## Test Conditions
DESIREE-FIRE Intermediate Scale Test 4 - Circuit Data Only
Test Date: | 2009-11-12
DCSim DAQ Start Time | 10:31
DCSim Time for Synchronization | 10:32
Heat Source Synchronization | 0:01 | hours:minutes:seconds
Heat Source DAQ Start Time | 10:31
Fire Time | 11:20
Offset | 0:49 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2940 | seconds
Heat Source Offset | 0:49 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2935 | seconds
Heat Source Stop Time | 13:12
Test Duration | 1:52 | hours:minutes:seconds
| 6720 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
Large Coil | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.90625 | 121.8338 | -61.2488 | 60.3333 | -0.21851 | 0.013016 | 0.071222 | 0.070478 | 0.13101 | -0.0021768 | -0.0052424 | -0.16144 | -0.0049924 | 0.060808 | 0.071886 | 0.00017731 | -0.0068209 | 60.2417 | 60.4248 | 0.13733 | -61.3541 | 60.2875 | -61.2305 | -61.1893 | -61.0611 | 0.15564 | -61.5189 | 60.2737 | 60.2646 | -61.1435 | -61.3266 | 0.01831 | 0.059509 | -0.045776 | 121.6736 | -0.10529 | -0.16479 | -0.091553 | 0.10529 | -0.07782 | -0.059509 | 0.18768 | -0.27008 | -0.19226 | -0.068665 | 121.5363 | 121.4905 | 61.3861 | -121.5225 | 121.5225 | 121.5134 | 61.4044 | -121.6599
0.78125 | 121.9116 | -61.1664 | 60.3561 | -0.0048827 | 0.011734 | 0.073785 | 0.06642 | 0.12717 | -0.0081582 | -0.0063104 | 0.15137 | -0.0092648 | 0.061449 | 0.070818 | -0.00089089 | -0.0059665 | 60.228 | 60.4568 | 0.064087 | -61.3449 | 60.2188 | -61.235 | -61.203 | -61.0153 | 0.11444 | -61.4685 | 60.1868 | 60.1913 | -61.1526 | -61.3403 | -0.068664 | -0.036621 | -0.13733 | 121.6232 | -0.17853 | -0.14191 | -0.12817 | 0.013733 | -0.17395 | -0.16937 | 0.15106 | -0.30212 | -0.12817 | -0.1648 | 121.3852 | 121.3943 | 61.2305 | -121.5591 | 121.3531 | 121.3577 | 61.2808 | -121.6965
2.5312 | 121.9208 | -61.2762 | 60.2692 | 0.16296 | 0.016861 | 0.068018 | 0.067274 | 0.1293 | -0.00089518 | -0.003106 | 0.13611 | -0.0045652 | 0.063158 | 0.072527 | 0.0018863 | -0.0091709 | 60.2097 | 60.3928 | -0.064087 | -61.3998 | 60.1547 | -61.2991 | -61.2808 | -61.0199 | 0.013733 | -61.5143 | 60.1456 | 60.1135 | -61.1984 | -61.3678 | -0.022888 | -0.004578 | -0.11444 | 121.669 | -0.1236 | -0.11902 | -0.059509 | 0.07782 | -0.091553 | -0.1236 | 0.25635 | -0.23804 | -0.14648 | -0.15564 | 121.431 | 121.4859 | 61.2122 | -121.55 | 121.4218 | 121.3898 | 61.29 | -121.637
4.2188 | 121.9208 | -61.171 | 60.3882 | 0.010376 | 0.011521 | 0.070367 | 0.066847 | 0.12952 | -0.0064492 | -0.007165 | 0.13611 | -0.0084104 | 0.062944 | 0.070605 | 0.00039091 | -0.0070345 | 60.2463 | 60.4568 | 0.064087 | -61.3266 | 60.2142 | -61.2442 | -61.1938 | -61.0153 | 0.11444 | -61.4639 | 60.2188 | 60.173 | -61.1435 | -61.2991 | -0.073243 | -0.022889 | -0.17395 | 121.6278 | -0.15564 | -0.13275 | -0.14191 | 0.027465 | -0.12817 | -0.16937 | 0.15564 | -0.29297 | -0.1648 | -0.21515 | 121.3852 | 121.4172 | 61.235 | -121.582 | 121.3898 | 121.344 | 61.2854 | -121.6873
5.9688 | 121.7697 | -61.3037 | 60.3195 | -0.050659 | 0.013016 | 0.069727 | 0.062147 | 0.1293 | 0.004659 | -0.003747 | -0.046997 | -0.0056332 | 0.062089 | 0.072741 | 0.0055179 | -0.0093845 | 60.2417 | 60.4111 | 0.013733 | -61.377 | 60.1822 | -61.2946 | -61.2488 | -61.0794 | 0.041199 | -61.5784 | 60.1868 | 60.1547 | -61.1984 | -61.3907 | 0.009155 | 0.054932 | -0.13733 | 121.7148 | -0.073242 | -0.12817 | -0.07782 | 0.10529 | -0.086975 | -0.13275 | 0.2243 | -0.27466 | -0.18768 | -0.16479 | 121.4859 | 121.5454 | 61.3174 | -121.5683 | 121.4905 | 121.4584 | 61.3449 | -121.7102
7.7188 | 121.8796 | -61.2167 | 60.3149 | 0.079041 | 0.012375 | 0.06994 | 0.06642 | 0.12888 | -0.004313 | -0.0043878 | 0.20477 | -0.0073422 | 0.060594 | 0.072954 | 0.0012455 | -0.0053257 | 60.2417 | 60.466 | 0.027466 | -61.3632 | 60.141 | -61.235 | -61.2259 | -61.0016 | 0.07782 | -61.4777 | 60.1868 | 60.1776 | -61.1114 | -61.3266 | -0.01831 | -0.009155 | -0.17395 | 121.6827 | -0.14648 | -0.13733 | -0.073242 | 0.10529 | -0.10986 | -0.12817 | 0.21515 | -0.26093 | -0.15106 | -0.13733 | 121.3577 | 121.4584 | 61.2442 | -121.5408 | 121.4035 | 121.3943 | 61.2946 | -121.6415
9.3906 | 121.9299 | -61.1526 | 60.3745 | -0.065918 | 0.01323 | 0.071436 | 0.067915 | 0.12888 | -0.0081582 | -0.0050286 | -0.0012209 | -0.0062742 | 0.061876 | 0.070605 | -0.0015317 | -0.0061801 | 60.3333 | 60.5255 | 0.16022 | -61.2717 | 60.2142 | -61.203 | -61.1755 | -60.9238 | 0.25177 | -61.3678 | 60.2554 | 60.2005 | -61.0977 | -61.2625 | -0.050354 | -0.022888 | -0.16022 | 121.6782 | -0.11902 | -0.09613 | -0.041199 | 0.054932 | -0.10986 | -0.11902 | 0.22888 | -0.21515 | -0.10529 | -0.17395 | 121.3669 | 121.4859 | 61.3129 | -121.55 | 121.4081 | 121.3531 | 61.4044 | -121.637
11.1406 | 121.8979 | -61.2808 | 60.2463 | 0.079041 | 0.01323 | 0.071649 | 0.064711 | 0.12738 | 0.0016684 | -0.003747 | 0.18188 | -0.0039244 | 0.061662 | 0.0721 | 0.0053043 | -0.010025 | 60.1959 | 60.3424 | -0.12817 | -61.441 | 60.1501 | -61.322 | -61.2762 | -61.0794 | -0.054932 | -61.5555 | 60.1547 | 60.1227 | -61.1984 | -61.3998 | -0.041198 | 0.004578 | -0.096131 | 121.6232 | -0.16022 | -0.16479 | -0.050354 | 0.082398 | -0.11902 | -0.091553 | 0.20142 | -0.27466 | -0.15564 | -0.1236 | 121.431 | 121.4767 | 61.1526 | -121.5225 | 121.4355 | 121.4035 | 61.2259 | -121.6461
12.8281 | 121.8842 | -61.235 | 60.3378 | 0.14771 | 0.013443 | 0.071222 | 0.066633 | 0.12845 | -0.0017496 | -0.003747 | 0.19714 | -0.0049924 | 0.060808 | 0.071673 | 0.0031681 | -0.0078891 | 60.2554 | 60.466 | -0.013733 | -61.3678 | 60.1135 | -61.2991 | -61.2534 | -60.997 | 0.041199 | -61.4822 | 60.141 | 60.1364 | -61.1618 | -61.3586 | -0.064087 | -0.018311 | -0.2243 | 121.701 | -0.13275 | -0.11444 | -0.082398 | 0.073242 | -0.1236 | -0.19684 | 0.23804 | -0.24719 | -0.1236 | -0.20142 | 121.3486 | 121.4905 | 61.2213 | -121.5912 | 121.376 | 121.3715 | 61.2762 | -121.6965
14.5625 | 121.8658 | -61.2076 | 60.347 | 0.10193 | 0.011948 | 0.072931 | 0.066633 | 0.12952 | -0.0051676 | -0.0018244 | 0.15137 | -0.0071286 | 0.058244 | 0.069536 | 0.0018863 | -0.0081027 | 60.2646 | 60.4797 | 0.036621 | -61.3541 | 60.1501 | -61.2488 | -61.203 | -61.0062 | 0.064087 | -61.4777 | 60.173 | 60.1685 | -61.1664 | -61.377 | -0.041198 | 0.004578 | -0.19684 | 121.6873 | -0.14648 | -0.15106 | -0.082398 | 0.041199 | -0.16937 | -0.17395 | 0.20142 | -0.27008 | -0.10071 | -0.17853 | 121.3577 | 121.4722 | 61.2442 | -121.55 | 121.3806 | 121.376 | 61.2717 | -121.7239
16.2969 | 121.8246 | -61.29 | 60.3012 | 0.056152 | 0.015152 | 0.071008 | 0.063002 | 0.1293 | 0.00060022 | -0.0046014 | 0.097962 | -0.005206 | 0.059526 | 0.070391 | 0.0035953 | -0.0072483 | 60.141 | 60.2875 | -0.11902 | -61.4731 | 60.1913 | -61.3312 | -61.3129 | -61.1481 | -0.11444 | -61.6562 | 60.1868 | 60.1227 | -61.2579 | -61.409 | -0.041199 | -0.022888 | -0.10986 | 121.5775 | -0.18311 | -0.16022 | -0.16022 | 0.032043 | -0.11902 | -0.11444 | 0.14191 | -0.36621 | -0.24719 | -0.17853 | 121.4813 | 121.431 | 61.171 | -121.6141 | 121.4767 | 121.4127 | 61.1755 | -121.7102
18.0625 | 121.8979 | -61.2167 | 60.3424 | 0.018005 | 0.011093 | 0.073999 | 0.066206 | 0.1308 | -0.0064492 | -0.0050286 | 0.11322 | -0.0067014 | 0.059953 | 0.068682 | 0.0018863 | -0.0059665 | 60.2371 | 60.4706 | 0.054932 | -61.3586 | 60.1959 | -61.2534 | -61.203 | -61.0107 | 0.086975 | -61.4777 | 60.2234 | 60.1547 | -61.1343 | -61.3403 | -0.036621 | 0.013733 | -0.14648 | 121.6873 | -0.14191 | -0.15564 | -0.10529 | 0.082398 | -0.1236 | -0.11902 | 0.20599 | -0.26093 | -0.13733 | -0.18768 | 121.4127 | 121.4539 | 61.2717 | -121.5454 | 121.4401 | 121.3715 | 61.3037 | -121.6827
19.7344 | 121.8384 | -61.2717 | 60.3058 | -0.14984 | 0.019211 | 0.070367 | 0.069197 | 0.1293 | 0.0012412 | -0.0033196 | -0.12329 | -0.0043516 | 0.060381 | 0.071673 | 0.00060451 | -0.0098117 | 60.2554 | 60.3928 | 0.082397 | -61.3586 | 60.2234 | -61.2854 | -61.2305 | -61.0519 | 0.11444 | -61.5234 | 60.2463 | 60.1685 | -61.1618 | -61.3632 | -0.013733 | 0.041198 | -0.082397 | 121.6644 | -0.086976 | -0.12817 | -0.050354 | 0.10986 | -0.091553 | -0.059509 | 0.21973 | -0.25177 | -0.16022 | -0.13733 | 121.4951 | 121.5271 | 61.3541 | -121.5363 | 121.5179 | 121.4401 | 61.3861 | -121.669
21.4688 | 121.8842 | -61.203 | 60.3699 | 0.010376 | 0.014939 | 0.071436 | 0.067488 | 0.12738 | -0.0051676 | -0.0041742 | 0.13611 | -0.0077696 | 0.062089 | 0.071245 | -0.0013181 | -0.0085299 | 60.2509 | 60.4614 | 0.045776 | -61.3449 | 60.1868 | -61.2396 | -61.203 | -61.0062 | 0.10529 | -61.4822 | 60.2051 | 60.2051 | -61.1389 | -61.3312 | -0.036621 | 0 | -0.1831 | 121.6644 | -0.14191 | -0.14191 | -0.11902 | 0.064087 | -0.12817 | -0.16479 | 0.19684 | -0.27924 | -0.15106 | -0.16479 | 121.3898 | 121.4539 | 61.2488 | -121.5729 | 121.4081 | 121.4081 | 61.3083 | -121.701
23.2344 | 121.7926 | -61.3266 | 60.3195 | 0.033264 | 0.015152 | 0.072076 | 0.064924 | 0.13165 | 0.0040182 | -0.0011834 | 0.029297 | -0.004138 | 0.062303 | 0.073168 | 0.0048769 | -0.0083163 | 60.173 | 60.3104 | -0.073242 | -61.4548 | 60.1776 | -61.3129 | -61.2854 | -61.1435 | -0.068665 | -61.6287 | 60.1776 | 60.1822 | -61.2396 | -61.3907 | 0.013733 | 0.041199 | -0.14191 | 121.637 | -0.12817 | -0.16937 | -0.14648 | 0.086975 | -0.064087 | -0.14191 | 0.18311 | -0.30212 | -0.23804 | -0.13733 | 121.5042 | 121.4996 | 61.2534 | -121.6049 | 121.5042 | 121.5088 | 61.2579 | -121.7102
24.9688 | 121.7926 | -61.3266 | 60.3012 | 0.071411 | 0.017289 | 0.072504 | 0.064283 | 0.12759 | 0.0020956 | -0.0035334 | 0.052185 | -0.0054196 | 0.061876 | 0.071673 | 0.0044497 | -0.0072483 | 60.1364 | 60.3241 | -0.10529 | -61.4502 | 60.1639 | -61.3037 | -61.2946 | -61.1435 | -0.073242 | -61.6653 | 60.1959 | 60.173 | -61.2442 | -61.4182 | 0.022888 | 0.032043 | -0.13733 | 121.6507 | -0.1236 | -0.15564 | -0.16479 | 0.082397 | -0.091553 | -0.10529 | 0.18311 | -0.33874 | -0.24719 | -0.12817 | 121.4905 | 121.463 | 61.2213 | -121.5958 | 121.5225 | 121.4996 | 61.2534 | -121.7194
26.7031 | 121.7834 | -61.3129 | 60.3149 | -0.096436 | 0.015793 | 0.070367 | 0.064924 | 0.12888 | -4.058e-05 | -0.002038 | -0.039368 | -0.0043516 | 0.06273 | 0.071245 | 0.0027407 | -0.0072483 | 60.2463 | 60.4385 | 0.064087 | -61.3678 | 60.1822 | -61.2808 | -61.2579 | -61.0565 | 0.10529 | -61.528 | 60.1822 | 60.1959 | -61.1893 | -61.3815 | 0.032043 | 0.054931 | -0.13275 | 121.7514 | -0.054932 | -0.10986 | -0.068664 | 0.1236 | -0.068665 | -0.13275 | 0.25635 | -0.21515 | -0.14648 | -0.11902 | 121.4951 | 121.5591 | 61.377 | -121.5729 | 121.4951 | 121.5088 | 61.4182 | -121.6965
28.4531 | 121.907 | -61.2717 | 60.2829 | 0.14771 | 0.012589 | 0.072076 | 0.065138 | 0.13016 | -0.0036722 | -0.003747 | 0.18951 | -0.005847 | 0.062303 | 0.069964 | 0.0035953 | -0.0044711 | 60.1868 | 60.3928 | -0.07782 | -61.409 | 60.1456 | -61.322 | -61.2534 | -61.0565 | 0 | -61.5189 | 60.1547 | 60.1044 | -61.2167 | -61.3724 | -0.050354 | 0.01831 | -0.13733 | 121.6644 | -0.13733 | -0.15564 | -0.09613 | 0.054931 | -0.10071 | -0.12817 | 0.21515 | -0.24719 | -0.14648 | -0.17853 | 121.4172 | 121.4584 | 61.1938 | -121.5363 | 121.4264 | 121.376 | 61.2717 | -121.6553
30.2031 | 121.8887 | -61.2396 | 60.347 | 0.0027468 | 0.012802 | 0.072076 | 0.067274 | 0.12952 | -0.007731 | -0.0035334 | 0.15137 | -0.006915 | 0.062089 | 0.069536 | -0.0013181 | -0.0078891 | 60.2371 | 60.4614 | 0.032043 | -61.3495 | 60.1685 | -61.2442 | -61.2167 | -61.0245 | 0.091553 | -61.4685 | 60.1868 | 60.1913 | -61.1435 | -61.3358 | -0.004578 | 0.022888 | -0.17853 | 121.7011 | -0.10986 | -0.13275 | -0.10986 | 0.09613 | -0.09613 | -0.16022 | 0.21515 | -0.22888 | -0.13275 | -0.15564 | 121.4081 | 121.4767 | 61.2717 | -121.5637 | 121.4264 | 121.431 | 61.3312 | -121.6827
31.8906 | 121.8521 | -61.2579 | 60.3378 | -0.1651 | 0.018997 | 0.071008 | 0.065565 | 0.12909 | -4.058e-05 | -0.0022516 | -0.092773 | -0.0054196 | 0.064226 | 0.071032 | 0.0012455 | -0.0095981 | 60.2509 | 60.4065 | 0.07782 | -61.3632 | 60.2142 | -61.2762 | -61.235 | -61.0657 | 0.1236 | -61.528 | 60.2325 | 60.2051 | -61.1847 | -61.3678 | -0.01831 | 0.022889 | -0.1236 | 121.6644 | -0.10528 | -0.12817 | -0.086976 | 0.073243 | -0.10986 | -0.10529 | 0.19226 | -0.27008 | -0.16022 | -0.13275 | 121.4722 | 121.5088 | 61.3358 | -121.5729 | 121.4905 | 121.463 | 61.3815 | -121.7056
33.6406 | 121.8979 | -61.2625 | 60.2921 | 0.10956 | 0.012589 | 0.06994 | 0.064497 | 0.12717 | -0.0030314 | -0.0050286 | 0.24292 | -0.0043516 | 0.059953 | 0.071459 | 0.0042361 | -0.0089573 | 60.26 | 60.4294 | -0.013733 | -61.377 | 60.1181 | -61.2854 | -61.2579 | -61.0382 | 0.032043 | -61.5051 | 60.1364 | 60.1089 | -61.1893 | -61.3632 | -0.022888 | 0.004577 | -0.17395 | 121.6919 | -0.11444 | -0.11902 | -0.032043 | 0.073242 | -0.10071 | -0.15564 | 0.2243 | -0.24262 | -0.14191 | -0.18311 | 121.3806 | 121.5225 | 61.2488 | -121.55 | 121.3989 | 121.3715 | 61.2946 | -121.6553
35.3281 | 121.907 | -61.1984 | 60.3607 | 0.0027468 | 0.01323 | 0.071649 | 0.066633 | 0.12973 | -0.0062356 | -0.0052424 | 0.15137 | -0.0060606 | 0.060594 | 0.071673 | -0.0019589 | -0.0074619 | 60.2417 | 60.4523 | 0.064087 | -61.3632 | 60.1959 | -61.2579 | -61.1984 | -61.0291 | 0.10529 | -61.4639 | 60.2142 | 60.1913 | -61.1343 | -61.3449 | -0.05951 | 0 | -0.16479 | 121.6507 | -0.16479 | -0.16479 | -0.11902 | 0.064087 | -0.14648 | -0.14648 | 0.16937 | -0.2655 | -0.11902 | -0.16937 | 121.3943 | 121.4401 | 61.2625 | -121.5591 | 121.4127 | 121.3898 | 61.3037 | -121.7056
37.0625 | 121.8887 | -61.203 | 60.3516 | 0.0027468 | 0.010666 | 0.071222 | 0.065351 | 0.12717 | -0.0062356 | -0.0056696 | 0.13611 | -0.0088376 | 0.059526 | 0.071886 | -3.629e-05 | -0.0083163 | 60.2554 | 60.4706 | 0.050354 | -61.3541 | 60.2097 | -61.2396 | -61.1984 | -61.0016 | 0.091553 | -61.4822 | 60.1959 | 60.2097 | -61.1618 | -61.3129 | -0.036621 | 0.004578 | -0.14191 | 121.6736 | -0.15106 | -0.15564 | -0.09613 | 0.041199 | -0.10986 | -0.15564 | 0.20142 | -0.27924 | -0.16937 | -0.14191 | 121.4127 | 121.4584 | 61.2534 | -121.55 | 121.3989 | 121.4127 | 61.2946 | -121.6644
38.8125 | 121.8475 | -61.2579 | 60.347 | -0.23376 | 0.013657 | 0.071008 | 0.066847 | 0.13144 | -0.00025418 | -0.004815 | -0.16907 | -0.0047788 | 0.061021 | 0.0721 | 0.0018863 | -0.0095981 | 60.2554 | 60.4202 | 0.09613 | -61.3541 | 60.2875 | -61.2396 | -61.203 | -61.0611 | 0.1236 | -61.5326 | 60.3149 | 60.2463 | -61.1526 | -61.3174 | 0.018311 | 0.054932 | -0.059509 | 121.6782 | -0.09613 | -0.15106 | -0.091553 | 0.10529 | -0.059509 | -0.032044 | 0.19684 | -0.27466 | -0.21515 | -0.10071 | 121.5454 | 121.5134 | 61.3541 | -121.55 | 121.5729 | 121.5042 | 61.3815 | -121.6644
40.5625 | 121.7834 | -61.2442 | 60.4019 | -0.25665 | 0.01558 | 0.070367 | 0.067915 | 0.12717 | -0.002604 | -0.004815 | -0.13855 | -0.0037106 | 0.061021 | 0.072314 | 0.0029543 | -0.0087435 | 60.3104 | 60.5255 | 0.20142 | -61.3037 | 60.2325 | -61.2259 | -61.1755 | -61.0245 | 0.20142 | -61.4639 | 60.2829 | 60.228 | -61.1572 | -61.3312 | 0.018311 | 0.068665 | -0.16937 | 121.7697 | -0.059509 | -0.12817 | -0.091553 | 0.086975 | -0.086975 | -0.11902 | 0.21973 | -0.21973 | -0.13275 | -0.17395 | 121.4767 | 121.5546 | 61.4456 | -121.5775 | 121.5271 | 121.4722 | 61.4456 | -121.7331
42.25 | 121.788 | -61.2991 | 60.2783 | -0.012512 | 0.014939 | 0.068658 | 0.064924 | 0.12824 | 0.001882 | -0.0024652 | -0.0088499 | -0.0067014 | 0.061662 | 0.0721 | 0.0053043 | -0.0083163 | 60.2097 | 60.3699 | -0.027466 | -61.409 | 60.2005 | -61.3266 | -61.2625 | -61.1389 | -0.045776 | -61.6241 | 60.1822 | 60.173 | -61.2488 | -61.3998 | -0.027466 | 0.036621 | -0.07782 | 121.669 | -0.10986 | -0.14648 | -0.068664 | 0.050354 | -0.10071 | -0.09613 | 0.16022 | -0.32501 | -0.22431 | -0.10529 | 121.4996 | 121.5088 | 61.2717 | -121.5408 | 121.4813 | 121.4722 | 61.2534 | -121.6782
44 | 121.907 | -61.1938 | 60.3836 | 0.0027468 | 0.012375 | 0.072076 | 0.065138 | 0.12994 | -0.0075174 | -0.0046014 | 0.12848 | -0.007556 | 0.059953 | 0.070605 | 0.0020999 | -0.0057529 | 60.228 | 60.4706 | 0.041199 | -61.3312 | 60.2097 | -61.2396 | -61.1938 | -61.0153 | 0.11444 | -61.4731 | 60.2325 | 60.1913 | -61.1343 | -61.3266 | -0.045776 | 0 | -0.17395 | 121.6644 | -0.13733 | -0.13733 | -0.15564 | 0.05951 | -0.13275 | -0.15106 | 0.17853 | -0.27923 | -0.14648 | -0.19226 | 121.4035 | 121.4218 | 61.235 | -121.5775 | 121.4264 | 121.3852 | 61.3083 | -121.7102
45.7344 | 121.9116 | -61.1755 | 60.3516 | 0.0027468 | 0.010453 | 0.072931 | 0.067274 | 0.12952 | -0.0055948 | -0.0058832 | 0.090332 | -0.0081968 | 0.060167 | 0.068468 | 0.0023135 | -0.0081027 | 60.2325 | 60.4568 | 0.064087 | -61.3449 | 60.2188 | -61.2442 | -61.2259 | -61.0107 | 0.11444 | -61.4639 | 60.2371 | 60.173 | -61.1389 | -61.3129 | -0.068665 | -0.050354 | -0.13275 | 121.6324 | -0.16937 | -0.11902 | -0.11902 | 0.036621 | -0.13733 | -0.11444 | 0.16479 | -0.28839 | -0.15106 | -0.17853 | 121.3943 | 121.4081 | 61.2396 | -121.5775 | 121.4127 | 121.3486 | 61.29 | -121.6644
47.4062 | 121.9162 | -61.1847 | 60.347 | -0.11932 | 0.013871 | 0.070581 | 0.067915 | 0.12717 | -0.004313 | -0.0033196 | -0.085144 | -0.0071286 | 0.061235 | 0.069964 | 0.00017731 | -0.0089573 | 60.3516 | 60.585 | 0.2243 | -61.2762 | 60.2142 | -61.2076 | -61.1526 | -60.91 | 0.28381 | -61.3724 | 60.2234 | 60.2005 | -61.0977 | -61.2854 | -0.022889 | 0.032043 | -0.13275 | 121.7697 | -0.091553 | -0.1236 | 0.004577 | 0.086975 | -0.10071 | -0.1236 | 0.27466 | -0.18768 | -0.086975 | -0.14648 | 121.3989 | 121.5363 | 61.409 | -121.4996 | 121.4081 | 121.3852 | 61.4685 | -121.6324
49.1406 | 121.8338 | -61.2625 | 60.3195 | -0.13458 | 0.018143 | 0.070367 | 0.067488 | 0.12909 | 0.0027364 | -0.0043878 | -0.13855 | -0.0039244 | 0.061449 | 0.073382 | 0.0033817 | -0.0091709 | 60.2737 | 60.4248 | 0.073242 | -61.3586 | 60.2234 | -61.2808 | -61.235 | -61.0336 | 0.13275 | -61.5234 | 60.2371 | 60.1868 | -61.1755 | -61.3632 | -0.018311 | 0.027466 | -0.09613 | 121.6873 | -0.096131 | -0.1236 | -0.045776 | 0.086975 | -0.10071 | -0.082397 | 0.22888 | -0.26093 | -0.16022 | -0.13275 | 121.4859 | 121.5363 | 61.3358 | -121.5546 | 121.4996 | 121.4493 | 61.3953 | -121.6827
50.8281 | 121.9162 | -61.1801 | 60.379 | -0.12695 | 0.014511 | 0.07229 | 0.067274 | 0.1308 | -0.0058084 | -0.0035334 | -0.031738 | -0.0067014 | 0.061876 | 0.068682 | -3.629e-05 | -0.0068209 | 60.3378 | 60.5942 | 0.21057 | -61.2625 | 60.1959 | -61.203 | -61.1435 | -60.8963 | 0.28839 | -61.3495 | 60.2325 | 60.2188 | -61.1252 | -61.2762 | -0.022888 | 0.036621 | -0.1831 | 121.7743 | -0.082397 | -0.11902 | -0.041198 | 0.054932 | -0.09613 | -0.14648 | 0.28381 | -0.16937 | -0.073242 | -0.16022 | 121.376 | 121.5179 | 61.3907 | -121.5225 | 121.4127 | 121.3989 | 61.4685 | -121.6553
52.5781 | 121.9345 | -61.1618 | 60.379 | -0.10406 | 0.010666 | 0.074426 | 0.063643 | 0.12738 | -0.006022 | -0.0060968 | -0.0088499 | -0.0073422 | 0.058031 | 0.069964 | 0.0012455 | -0.0089573 | 60.347 | 60.5804 | 0.19226 | -61.2579 | 60.2554 | -61.1984 | -61.1664 | -60.8963 | 0.25177 | -61.3678 | 60.228 | 60.1913 | -61.1069 | -61.2946 | -0.036621 | -0.004578 | -0.1236 | 121.7422 | -0.096131 | -0.091553 | -0.032043 | 0.054931 | -0.13275 | -0.15106 | 0.2655 | -0.20599 | -0.073242 | -0.18768 | 121.4172 | 121.5088 | 61.3541 | -121.5454 | 121.3898 | 121.3531 | 61.4136 | -121.6736
54.3281 | 121.843 | -61.2579 | 60.3378 | -0.20325 | 0.017289 | 0.072931 | 0.068129 | 0.13101 | 0.003591 | -0.0026788 | -0.15381 | -0.005206 | 0.062303 | 0.071032 | 0.0027407 | -0.0098117 | 60.26 | 60.4156 | 0.086975 | -61.3449 | 60.26 | -61.2808 | -61.2442 | -61.0611 | 0.11902 | -61.5326 | 60.2646 | 60.1959 | -61.1618 | -61.3724 | -0.022888 | 0.013733 | -0.07782 | 121.6736 | -0.086975 | -0.10071 | -0.07782 | 0.096131 | -0.11444 | -0.073243 | 0.19684 | -0.27466 | -0.16022 | -0.14191 | 121.5179 | 121.5179 | 61.3449 | -121.582 | 121.5225 | 121.4539 | 61.377 | -121.7102
56.0625 | 121.9254 | -61.2488 | 60.2554 | 0.079041 | 0.011948 | 0.070154 | 0.063856 | 0.12909 | 0.0025228 | -0.0069512 | 0.17426 | -0.0060606 | 0.062303 | 0.072314 | 0.0031681 | -0.0089573 | 60.1868 | 60.3333 | -0.1236 | -61.4365 | 60.1776 | -61.3083 | -61.2808 | -61.0931 | -0.091553 | -61.5875 | 60.1547 | 60.1501 | -61.203 | -61.4044 | -0.05951 | -0.032044 | -0.07782 | 121.582 | -0.18768 | -0.15564 | -0.068664 | 0.045776 | -0.15564 | -0.10071 | 0.15564 | -0.33875 | -0.18311 | -0.10529 | 121.4264 | 121.4355 | 61.1252 | -121.5363 | 121.4035 | 121.3989 | 61.1572 | -121.6599
57.8125 | 121.9162 | -61.171 | 60.3561 | 0.0027468 | 0.013871 | 0.072931 | 0.067274 | 0.12909 | -0.0062356 | -0.0028924 | 0.14374 | -0.0062742 | 0.063371 | 0.070391 | 0.00039091 | -0.0066073 | 60.2371 | 60.4523 | 0.059509 | -61.3449 | 60.2051 | -61.2579 | -61.203 | -61.0107 | 0.11444 | -61.4685 | 60.2097 | 60.1913 | -61.1435 | -61.3495 | -0.086976 | -0.032044 | -0.15106 | 121.6232 | -0.17395 | -0.14191 | -0.11902 | 0.027465 | -0.17853 | -0.14648 | 0.16022 | -0.29755 | -0.11902 | -0.1648 | 121.376 | 121.4081 | 61.2305 | -121.5591 | 121.3806 | 121.3623 | 61.2854 | -121.7056
59.5625 | 121.8063 | -61.2762 | 60.3195 | -0.096436 | 0.018784 | 0.069727 | 0.064283 | 0.1308 | 0.0033774 | -0.003106 | -0.077515 | -0.0047788 | 0.063798 | 0.071245 | 0.0053043 | -0.011094 | 60.2463 | 60.4385 | 0.064087 | -61.3678 | 60.2325 | -61.2991 | -61.2717 | -61.0428 | 0.10071 | -61.528 | 60.2097 | 60.1685 | -61.1847 | -61.3586 | -0.022888 | 0.004578 | -0.086975 | 121.7148 | -0.091553 | -0.096131 | -0.073242 | 0.091553 | -0.082398 | -0.10986 | 0.23346 | -0.25177 | -0.16937 | -0.15106 | 121.5088 | 121.5225 | 61.3403 | -121.5912 | 121.4859 | 121.4447 | 61.377 | -121.6782
61.2344 | 121.8979 | -61.2122 | 60.3561 | 0.033264 | 0.012802 | 0.071222 | 0.064711 | 0.1293 | -0.0073038 | -0.0041742 | 0.159 | -0.0047788 | 0.058672 | 0.070391 | -3.629e-05 | -0.0063937 | 60.2417 | 60.4614 | 0.041199 | -61.3586 | 60.1822 | -61.2717 | -61.2259 | -61.0199 | 0.07782 | -61.4639 | 60.1776 | 60.1593 | -61.1664 | -61.3083 | -0.059509 | -0.013733 | -0.17395 | 121.6736 | -0.14648 | -0.13275 | -0.11444 | 0.045776 | -0.096131 | -0.17853 | 0.19226 | -0.25177 | -0.15564 | -0.19684 | 121.3943 | 121.4539 | 61.2534 | -121.582 | 121.3898 | 121.3715 | 61.29 | -121.6644
62.9844 | 121.9208 | -61.1435 | 60.3699 | -0.10406 | 0.011307 | 0.073572 | 0.068342 | 0.12909 | -0.006022 | -0.0035334 | -0.039368 | -0.0064878 | 0.059312 | 0.070605 | 0.0025271 | -0.0098117 | 60.3378 | 60.5667 | 0.21057 | -61.2762 | 60.2463 | -61.2167 | -61.1664 | -60.9146 | 0.26093 | -61.3724 | 60.2463 | 60.2051 | -61.0931 | -61.3174 | -0.073242 | -0.022888 | -0.1236 | 121.7102 | -0.13275 | -0.10986 | -0.032043 | 0.050354 | -0.17395 | -0.1236 | 0.22888 | -0.22888 | -0.054931 | -0.16479 | 121.3898 | 121.4813 | 61.3541 | -121.5363 | 121.3898 | 121.3486 | 61.4044 | -121.6873
64.7344 | 121.7972 | -61.2213 | 60.4202 | -0.18799 | 0.01622 | 0.070581 | 0.067274 | 0.13101 | -0.0028178 | -0.0028924 | -0.13855 | -0.0060606 | 0.062944 | 0.069323 | -0.0011045 | -0.0070345 | 60.3424 | 60.5392 | 0.24261 | -61.2854 | 60.2371 | -61.1893 | -61.1664 | -60.965 | 0.27924 | -61.4365 | 60.2554 | 60.26 | -61.1435 | -61.2808 | 0.032043 | 0.054931 | -0.1831 | 121.7606 | -0.064087 | -0.11902 | -0.07782 | 0.077819 | -0.05951 | -0.16479 | 0.25635 | -0.21515 | -0.15564 | -0.16022 | 121.4584 | 121.5637 | 61.4639 | -121.5866 | 121.4767 | 121.4813 | 61.5005 | -121.701
66.4219 | 121.7834 | -61.322 | 60.3104 | -0.081177 | 0.014298 | 0.069299 | 0.06172 | 0.12738 | 0.0023092 | -0.0033196 | -0.069885 | -0.003497 | 0.062089 | 0.071459 | 0.0053043 | -0.0098117 | 60.2554 | 60.434 | 0.036621 | -61.377 | 60.2188 | -61.2946 | -61.2259 | -61.0565 | 0.064087 | -61.5601 | 60.228 | 60.1593 | -61.2122 | -61.3907 | 0.027465 | 0.09613 | -0.091553 | 121.756 | -0.054932 | -0.15106 | -0.054932 | 0.10986 | -0.068665 | -0.082398 | 0.2655 | -0.23804 | -0.16937 | -0.15106 | 121.5408 | 121.5775 | 61.3586 | -121.5363 | 121.55 | 121.4813 | 61.3861 | -121.7011
68.1719 | 121.8201 | -61.2808 | 60.3241 | -0.10406 | 0.014939 | 0.070581 | 0.064497 | 0.12973 | 0.0010276 | -0.0035334 | -0.085144 | -0.0045652 | 0.061662 | 0.071886 | 0.0059451 | -0.0078891 | 60.2463 | 60.4202 | 0.054932 | -61.3815 | 60.2097 | -61.2808 | -61.2488 | -61.0474 | 0.10986 | -61.5417 | 60.2142 | 60.1547 | -61.1984 | -61.3815 | 0 | 0.032044 | -0.11444 | 121.701 | -0.10071 | -0.13275 | -0.07782 | 0.082398 | -0.10071 | -0.10986 | 0.23346 | -0.26093 | -0.16022 | -0.16937 | 121.4905 | 121.5271 | 61.3358 | -121.5729 | 121.4951 | 121.4355 | 61.3907 | -121.7056
69.9219 | 121.9162 | -61.1755 | 60.3378 | 0.0027468 | 0.012589 | 0.073785 | 0.065565 | 0.13101 | -0.0064492 | -0.0035334 | 0.11322 | -0.0090512 | 0.062089 | 0.070391 | 0.00081811 | -0.0046847 | 60.2325 | 60.466 | 0.073242 | -61.3312 | 60.2051 | -61.2488 | -61.1984 | -61.0016 | 0.13275 | -61.4548 | 60.2234 | 60.1913 | -61.1618 | -61.322 | -0.073242 | -0.022888 | -0.13275 | 121.6415 | -0.15564 | -0.13275 | -0.10529 | 0.013733 | -0.14648 | -0.11444 | 0.17395 | -0.27924 | -0.13275 | -0.14648 | 121.3806 | 121.4081 | 61.2488 | -121.5363 | 121.3989 | 121.3669 | 61.3083 | -121.6599
71.5938 | 121.875 | -61.2122 | 60.3287 | 0.08667 | 0.012375 | 0.073572 | 0.064497 | 0.12888 | -0.0040994 | -0.0035334 | 0.18188 | -0.0043516 | 0.061876 | 0.070818 | 0.00017731 | -0.0068209 | 60.2554 | 60.466 | 0.013733 | -61.3724 | 60.1593 | -61.2717 | -61.2396 | -60.9924 | 0.07782 | -61.4685 | 60.1913 | 60.1639 | -61.1481 | -61.3403 | -0.059509 | -0.027466 | -0.16937 | 121.6782 | -0.16022 | -0.13275 | -0.073242 | 0.064087 | -0.12817 | -0.13733 | 0.21973 | -0.25635 | -0.12817 | -0.16479 | 121.3715 | 121.4676 | 61.2259 | -121.5683 | 121.4035 | 121.376 | 61.29 | -121.669
73.3438 | 121.9299 | -61.2808 | 60.2783 | 0.15533 | 0.012589 | 0.070367 | 0.064497 | 0.12781 | 0.0014548 | -0.0058832 | 0.18951 | -0.004138 | 0.061021 | 0.068468 | 0.0033817 | -0.0083163 | 60.1959 | 60.347 | -0.086975 | -61.4182 | 60.1639 | -61.3037 | -61.2854 | -61.0611 | -0.018311 | -61.5417 | 60.1547 | 60.1089 | -61.2259 | -61.4182 | -0.022888 | -0.004577 | -0.11444 | 121.6278 | -0.13733 | -0.13275 | -0.082397 | 0.054932 | -0.13733 | -0.1236 | 0.21973 | -0.26093 | -0.1236 | -0.16937 | 121.4447 | 121.4767 | 61.1938 | -121.5637 | 121.4355 | 121.3898 | 61.2625 | -121.6965
75.0938 | 121.8292 | -61.2762 | 60.3333 | -0.096436 | 0.017289 | 0.069299 | 0.067915 | 0.1308 | 0.00060022 | -0.0011834 | -0.077515 | -0.005206 | 0.064226 | 0.068896 | 0.0031681 | -0.0091709 | 60.2509 | 60.4202 | 0.068665 | -61.377 | 60.2005 | -61.2808 | -61.2625 | -61.0703 | 0.11902 | -61.5463 | 60.2005 | 60.173 | -61.1984 | -61.3586 | -0.004578 | 0.013733 | -0.13275 | 121.6965 | -0.10071 | -0.11444 | -0.082398 | 0.07782 | -0.082398 | -0.13275 | 0.20599 | -0.27008 | -0.18768 | -0.16022 | 121.4767 | 121.5271 | 61.3449 | -121.5958 | 121.4767 | 121.4493 | 61.3953 | -121.6919
76.7812 | 121.9025 | -61.2213 | 60.3012 | 0.14771 | 0.01558 | 0.070581 | 0.065779 | 0.12802 | -0.0023904 | -0.0035334 | 0.22766 | -0.004138 | 0.060594 | 0.070605 | 0.00017731 | -0.0066073 | 60.2417 | 60.466 | 0.018311 | -61.3632 | 60.1135 | -61.3174 | -61.2579 | -60.997 | 0.054932 | -61.4639 | 60.141 | 60.1318 | -61.1984 | -61.3953 | -0.096131 | -0.036622 | -0.18768 | 121.6873 | -0.14191 | -0.10528 | -0.059509 | 0.022888 | -0.17395 | -0.16022 | 0.2243 | -0.24262 | -0.068664 | -0.16937 | 121.3348 | 121.463 | 61.2396 | -121.5591 | 121.3623 | 121.3531 | 61.2762 | -121.6965
78.5312 | 121.9574 | -61.1572 | 60.3561 | -0.0354 | 0.012375 | 0.075067 | 0.069197 | 0.12781 | -0.0075174 | -0.005456 | 0.044556 | -0.0071286 | 0.061662 | 0.068041 | -3.629e-05 | -0.0066073 | 60.2829 | 60.5072 | 0.12817 | -61.3129 | 60.2188 | -61.2305 | -61.1893 | -60.9421 | 0.19684 | -61.3953 | 60.228 | 60.173 | -61.1435 | -61.2854 | -0.073242 | -0.032043 | -0.13733 | 121.6644 | -0.15564 | -0.1236 | -0.073242 | 0.013733 | -0.12817 | -0.12817 | 0.21515 | -0.23804 | -0.10986 | -0.18311 | 121.376 | 121.4401 | 61.2854 | -121.5454 | 121.3852 | 121.3303 | 61.3541 | -121.6415
80.2656 | 121.8979 | -61.2579 | 60.26 | 0.079041 | 0.012162 | 0.070581 | 0.065779 | 0.1293 | 0.00081382 | -0.0024652 | 0.11322 | -0.0054196 | 0.060167 | 0.071886 | 0.0057315 | -0.0074619 | 60.1822 | 60.3424 | -0.13275 | -61.4365 | 60.1959 | -61.3449 | -61.2854 | -61.1252 | -0.09613 | -61.6104 | 60.2005 | 60.1181 | -61.2396 | -61.4273 | -0.086975 | -0.027465 | -0.064087 | 121.6003 | -0.17853 | -0.15106 | -0.07782 | 0.018311 | -0.16937 | -0.05951 | 0.13275 | -0.35248 | -0.18311 | -0.14191 | 121.4539 | 121.4401 | 61.1252 | -121.5454 | 121.4584 | 121.376 | 61.1618 | -121.6873
81.9531 | 121.9528 | -61.1893 | 60.3653 | -0.058289 | 0.011521 | 0.072504 | 0.066847 | 0.12909 | -0.0062356 | -0.0035334 | 0.0064086 | -0.0067014 | 0.060808 | 0.067827 | 0.00060451 | -0.0068209 | 60.2921 | 60.5438 | 0.15564 | -61.2946 | 60.228 | -61.2305 | -61.1618 | -60.9146 | 0.2655 | -61.3724 | 60.2325 | 60.2188 | -61.084 | -61.3083 | -0.041199 | 0.027466 | -0.13733 | 121.7331 | -0.10529 | -0.13275 | -0.073242 | 0.10529 | -0.11902 | -0.13275 | 0.27466 | -0.1831 | -0.064086 | -0.14648 | 121.4172 | 121.4813 | 61.3449 | -121.5271 | 121.4218 | 121.4081 | 61.4548 | -121.6736
83.7031 | 121.7789 | -61.3083 | 60.3012 | -0.0354 | 0.019425 | 0.069727 | 0.067701 | 0.12994 | 0.0027364 | -0.0024652 | 0.014038 | -0.0039244 | 0.065294 | 0.071886 | 0.0033817 | -0.0083163 | 60.2188 | 60.3882 | -0.009155 | -61.409 | 60.1868 | -61.3037 | -61.3083 | -61.1206 | -0.027466 | -61.6104 | 60.2097 | 60.1456 | -61.2442 | -61.3953 | 0.004578 | 0 | -0.11444 | 121.6965 | -0.10071 | -0.10071 | -0.082397 | 0.064087 | -0.086975 | -0.091552 | 0.18768 | -0.30212 | -0.21515 | -0.15564 | 121.4951 | 121.5271 | 61.2991 | -121.6095 | 121.5179 | 121.4539 | 61.2808 | -121.6965
85.4375 | 121.8384 | -61.2488 | 60.3699 | -0.24902 | 0.01323 | 0.07464 | 0.065565 | 0.12824 | -0.0019632 | -0.003747 | -0.1767 | -0.0064878 | 0.062089 | 0.069109 | 0.0035953 | -0.0085299 | 60.2417 | 60.4385 | 0.1236 | -61.3678 | 60.2737 | -61.2488 | -61.2122 | -61.0611 | 0.15106 | -61.5372 | 60.2829 | 60.2646 | -61.1526 | -61.3358 | 0 | 0.036621 | -0.09613 | 121.6873 | -0.11902 | -0.15564 | -0.12817 | 0.09613 | -0.086975 | -0.086975 | 0.18768 | -0.28839 | -0.20142 | -0.10529 | 121.5225 | 121.4905 | 61.3724 | -121.582 | 121.5317 | 121.5134 | 61.3998 | -121.7056
87.125 | 121.8109 | -61.3083 | 60.3058 | 0.010376 | 0.012802 | 0.073572 | 0.063429 | 0.13037 | -0.00089518 | -0.0016108 | 0.044556 | -0.0045652 | 0.060381 | 0.072314 | 0.0053043 | -0.0072483 | 60.141 | 60.3378 | -0.086975 | -61.4594 | 60.1776 | -61.322 | -61.2946 | -61.1618 | -0.059509 | -61.6333 | 60.2051 | 60.1593 | -61.2396 | -61.4227 | -0.013732 | 0.013733 | -0.12817 | 121.6461 | -0.15106 | -0.16479 | -0.16479 | 0.068665 | -0.11444 | -0.10071 | 0.14649 | -0.32501 | -0.21057 | -0.14648 | 121.4859 | 121.4493 | 61.2213 | -121.6003 | 121.5134 | 121.4676 | 61.2488 | -121.7285
88.875 | 121.8887 | -61.2762 | 60.2692 | 0.094299 | 0.013443 | 0.07229 | 0.065351 | 0.13123 | -0.0034586 | -0.0011834 | 0.11322 | -0.0054196 | 0.061449 | 0.071886 | 0.0018863 | -0.0063937 | 60.1318 | 60.3287 | -0.14648 | -61.4456 | 60.1639 | -61.3632 | -61.2946 | -61.1252 | -0.086975 | -61.6013 | 60.1913 | 60.1364 | -61.2259 | -61.4136 | -0.086975 | -0.018311 | -0.10529 | 121.6049 | -0.16937 | -0.15106 | -0.13733 | 0.050354 | -0.13733 | -0.07782 | 0.15106 | -0.32501 | -0.18768 | -0.13275 | 121.4401 | 121.4081 | 61.1298 | -121.5637 | 121.4676 | 121.4127 | 61.1893 | -121.6827
90.625 | 121.8475 | -61.1847 | 60.4019 | -0.1651 | 0.014084 | 0.074854 | 0.069624 | 0.1293 | -0.0062356 | -0.0043878 | -0.039368 | -0.005847 | 0.063798 | 0.069964 | -0.0025999 | -0.0070345 | 60.3287 | 60.6033 | 0.26093 | -61.2579 | 60.2097 | -61.1893 | -61.1664 | -60.9558 | 0.29297 | -61.3861 | 60.2325 | 60.2142 | -61.1023 | -61.2808 | -0.004578 | 0.01831 | -0.19226 | 121.788 | -0.073243 | -0.091553 | -0.073243 | 0.082397 | -0.096131 | -0.16937 | 0.22888 | -0.20142 | -0.10529 | -0.18768 | 121.3943 | 121.5134 | 61.4456 | -121.5683 | 121.4172 | 121.3989 | 61.4777 | -121.6827
92.2969 | 121.9208 | -61.1984 | 60.3653 | -0.14221 | 0.013443 | 0.074213 | 0.06941 | 0.13059 | -0.0064492 | -0.0039606 | 0.044556 | -0.0047788 | 0.061449 | 0.070177 | -0.00024989 | -0.0081027 | 60.3378 | 60.5759 | 0.21057 | -61.2808 | 60.2188 | -61.2167 | -61.1572 | -60.9055 | 0.29755 | -61.3495 | 60.2234 | 60.2234 | -61.0794 | -61.2854 | -0.018311 | 0.041198 | -0.14648 | 121.7743 | -0.082398 | -0.1236 | -0.027465 | 0.11902 | -0.086975 | -0.14191 | 0.29297 | -0.15106 | -0.064087 | -0.14191 | 121.4172 | 121.5363 | 61.409 | -121.5225 | 121.4218 | 121.4218 | 61.496 | -121.6507
94.0312 | 121.8155 | -61.2854 | 60.3195 | -0.096436 | 0.017716 | 0.068658 | 0.064497 | 0.12994 | 0.003591 | -0.0028924 | -0.077515 | -0.003497 | 0.063371 | 0.073168 | 0.0038089 | -0.0089573 | 60.2646 | 60.4294 | 0.064087 | -61.377 | 60.228 | -61.3037 | -61.2808 | -61.0474 | 0.10071 | -61.5326 | 60.2188 | 60.173 | -61.1755 | -61.3678 | -0.018311 | 0.004577 | -0.091553 | 121.7148 | -0.091553 | -0.09613 | -0.054932 | 0.10986 | -0.082398 | -0.10071 | 0.23804 | -0.24719 | -0.16479 | -0.14648 | 121.5134 | 121.55 | 61.3495 | -121.6003 | 121.5042 | 121.4584 | 61.3861 | -121.6873
95.7188 | 121.9116 | -61.1801 | 60.3653 | -0.10406 | 0.014084 | 0.06994 | 0.066633 | 0.12952 | -0.0064492 | -0.0043878 | 0.014038 | -0.0067014 | 0.062944 | 0.070177 | 0.00081811 | -0.0078891 | 60.3241 | 60.5759 | 0.21515 | -61.2808 | 60.2234 | -61.1801 | -61.1618 | -60.9283 | 0.25177 | -61.3632 | 60.2371 | 60.1776 | -61.116 | -61.29 | 0 | 0.018311 | -0.14191 | 121.756 | -0.10071 | -0.11902 | -0.041198 | 0.064087 | -0.10986 | -0.12817 | 0.25177 | -0.1831 | -0.073242 | -0.18768 | 121.4035 | 121.5042 | 61.3953 | -121.5271 | 121.4172 | 121.3577 | 61.4319 | -121.6553
97.4531 | 121.9299 | -61.2534 | 60.2737 | 0.15533 | 0.015793 | 0.073358 | 0.062361 | 0.12888 | -0.001536 | -0.0022516 | 0.17426 | -0.0071286 | 0.05974 | 0.068682 | 0.0070133 | -0.0098117 | 60.2051 | 60.3928 | -0.082397 | -61.4136 | 60.141 | -61.3037 | -61.2625 | -61.0611 | 0.004578 | -61.5234 | 60.1547 | 60.1044 | -61.2167 | -61.3998 | -0.050354 | -0.009155 | -0.13275 | 121.6461 | -0.16022 | -0.15106 | -0.068665 | 0.036621 | -0.14648 | -0.11902 | 0.19226 | -0.27008 | -0.1236 | -0.16937 | 121.3943 | 121.4584 | 61.171 | -121.5363 | 121.4081 | 121.3577 | 61.2579 | -121.6736
99.2031 | 121.7834 | -61.2305 | 60.4111 | -0.24139 | 0.01622 | 0.070795 | 0.067915 | 0.13059 | -0.0019632 | -0.0033196 | -0.14618 | -0.0054196 | 0.062303 | 0.070818 | 0.0023135 | -0.0074619 | 60.26 | 60.466 | 0.15106 | -61.3358 | 60.2463 | -61.2259 | -61.1847 | -61.0336 | 0.1831 | -61.5005 | 60.3012 | 60.26 | -61.1481 | -61.3129 | 0.004578 | 0.045777 | -0.16479 | 121.6965 | -0.10529 | -0.15106 | -0.15106 | 0.082398 | -0.082397 | -0.10986 | 0.19684 | -0.27008 | -0.18768 | -0.15106 | 121.4767 | 121.4905 | 61.3815 | -121.5958 | 121.5317 | 121.4905 | 61.4136 | -121.7239
100.8906 | 121.8567 | -61.2488 | 60.3653 | -0.24139 | 0.015366 | 0.071649 | 0.066847 | 0.12866 | 0.00017302 | -0.0041742 | -0.15381 | -0.0079832 | 0.061876 | 0.0721 | 0.0044497 | -0.0083163 | 60.2417 | 60.4385 | 0.10529 | -61.3449 | 60.2646 | -61.2259 | -61.2213 | -61.0748 | 0.13275 | -61.5417 | 60.2875 | 60.2097 | -61.1664 | -61.3724 | 0.022888 | 0.027466 | -0.10071 | 121.6873 | -0.096131 | -0.1236 | -0.1236 | 0.082397 | -0.1236 | -0.077819 | 0.17395 | -0.29297 | -0.16937 | -0.15564 | 121.5134 | 121.4905 | 61.3541 | -121.5866 | 121.5363 | 121.4584 | 61.3815 | -121.7377
102.6406 | 121.8063 | -61.2442 | 60.379 | -0.15747 | 0.016861 | 0.071436 | 0.06941 | 0.12994 | -0.003245 | -0.0050286 | -0.077515 | -0.0062742 | 0.061449 | 0.069323 | -0.00067729 | -0.0095981 | 60.3149 | 60.5713 | 0.24719 | -61.2762 | 60.2188 | -61.1984 | -61.1664 | -60.9604 | 0.29297 | -61.3907 | 60.26 | 60.228 | -61.0977 | -61.3129 | 0.045777 | 0.07782 | -0.16022 | 121.8155 | -0.032043 | -0.10986 | -0.064087 | 0.14648 | -0.068664 | -0.11902 | 0.28381 | -0.14648 | -0.07782 | -0.15106 | 121.463 | 121.5591 | 61.4914 | -121.5454 | 121.5042 | 121.4722 | 61.5372 | -121.6919
104.3906 | 121.9254 | -61.2671 | 60.2509 | 0.15533 | 0.011948 | 0.069727 | 0.063856 | 0.1293 | 0.00038662 | -0.0041742 | 0.17426 | -0.0073422 | 0.061021 | 0.071886 | 0.0040225 | -0.0081027 | 60.1959 | 60.3836 | -0.07782 | -61.4273 | 60.1593 | -61.3312 | -61.2717 | -61.0519 | 0.009155 | -61.5189 | 60.1456 | 60.1593 | -61.203 | -61.3586 | -0.064087 | -0.004577 | -0.091552 | 121.6507 | -0.16022 | -0.15564 | -0.054931 | 0.064087 | -0.091553 | -0.10528 | 0.21515 | -0.25177 | -0.16022 | -0.091552 | 121.4264 | 121.463 | 61.1893 | -121.5225 | 121.4127 | 121.4264 | 61.2762 | -121.6095
106.0625 | 121.9391 | -61.1847 | 60.3653 | -0.0354 | 0.014939 | 0.073145 | 0.063429 | 0.12653 | -0.0070902 | -0.0046014 | 0.036926 | -0.0081968 | 0.060808 | 0.067827 | -3.629e-05 | -0.0095981 | 60.26 | 60.5072 | 0.10071 | -61.322 | 60.2142 | -61.2259 | -61.1755 | -60.9421 | 0.21515 | -61.377 | 60.2371 | 60.2142 | -61.116 | -61.2854 | -0.041199 | 0.009155 | -0.15106 | 121.6919 | -0.13733 | -0.14648 | -0.10529 | 0.068664 | -0.10071 | -0.12817 | 0.24261 | -0.19226 | -0.091553 | -0.15106 | 121.3989 | 121.4447 | 61.2854 | -121.5408 | 121.4218 | 121.3989 | 61.3998 | -121.6507
107.7969 | 121.8338 | -61.2579 | 60.3836 | -0.22614 | 0.015366 | 0.071863 | 0.066206 | 0.12888 | -4.058e-05 | -0.0060968 | -0.16907 | -0.0060606 | 0.063371 | 0.071245 | 0.0020999 | -0.0081027 | 60.2417 | 60.4065 | 0.09613 | -61.3403 | 60.26 | -61.2625 | -61.2076 | -61.0611 | 0.14191 | -61.5372 | 60.2966 | 60.2234 | -61.1618 | -61.3449 | -0.004577 | 0.050354 | -0.1236 | 121.6644 | -0.082397 | -0.13275 | -0.14191 | 0.096131 | -0.086975 | -0.086975 | 0.19684 | -0.27923 | -0.19226 | -0.16022 | 121.5179 | 121.4996 | 61.3541 | -121.5912 | 121.5546 | 121.4813 | 61.3998 | -121.7285
109.5625 | 121.8567 | -61.2579 | 60.3149 | -0.21088 | 0.014084 | 0.069513 | 0.065351 | 0.12717 | 0.0012412 | -0.0033196 | -0.13092 | -0.0043516 | 0.063158 | 0.073168 | 0.0027407 | -0.0083163 | 60.2509 | 60.4294 | 0.082397 | -61.3586 | 60.2463 | -61.3037 | -61.235 | -61.0657 | 0.12817 | -61.5417 | 60.2234 | 60.2097 | -61.1801 | -61.3678 | -0.045776 | 0.022889 | -0.068664 | 121.6873 | -0.10071 | -0.1236 | -0.064087 | 0.07782 | -0.10986 | -0.091552 | 0.19226 | -0.28381 | -0.17395 | -0.10528 | 121.5042 | 121.5088 | 61.3403 | -121.55 | 121.4813 | 121.4676 | 61.3861 | -121.6827
111.2344 | 121.8384 | -61.3037 | 60.2829 | 0.079041 | 0.015152 | 0.072076 | 0.063643 | 0.12952 | -0.00089518 | -0.0024652 | 0.13611 | -0.005847 | 0.061235 | 0.073809 | 0.0029543 | -0.0059665 | 60.141 | 60.3149 | -0.13275 | -61.4731 | 60.1639 | -61.3541 | -61.3129 | -61.1572 | -0.09613 | -61.6379 | 60.1868 | 60.1364 | -61.2442 | -61.4044 | -0.050354 | -0.009155 | -0.11902 | 121.6187 | -0.16937 | -0.16022 | -0.14191 | 0.059509 | -0.10071 | -0.09613 | 0.14648 | -0.33417 | -0.23346 | -0.14648 | 121.4676 | 121.4447 | 61.171 | -121.5958 | 121.4905 | 121.4401 | 61.2076 | -121.6873
112.9844 | 121.8384 | -61.2305 | 60.3882 | -0.24139 | 0.016434 | 0.073572 | 0.070692 | 0.12717 | -0.0034586 | -0.003747 | -0.16144 | -0.006915 | 0.062089 | 0.069964 | -0.00024989 | -0.0078891 | 60.228 | 60.4477 | 0.12817 | -61.3586 | 60.2737 | -61.235 | -61.1984 | -61.0794 | 0.15564 | -61.5143 | 60.2921 | 60.2509 | -61.1618 | -61.3312 | -0.004577 | 0.032044 | -0.11444 | 121.6782 | -0.12817 | -0.16022 | -0.16022 | 0.068665 | -0.10071 | -0.096131 | 0.15106 | -0.28381 | -0.18311 | -0.13733 | 121.5042 | 121.4584 | 61.3586 | -121.5866 | 121.5225 | 121.4813 | 61.3861 | -121.7194
114.7188 | 121.843 | -61.2625 | 60.3836 | -0.24139 | 0.017075 | 0.072504 | 0.066847 | 0.12909 | -0.0034586 | -0.0028924 | -0.15381 | -0.005206 | 0.06508 | 0.071886 | 0.0014591 | -0.010025 | 60.2234 | 60.4431 | 0.11444 | -61.3495 | 60.2875 | -61.2396 | -61.1984 | -61.0703 | 0.14191 | -61.528 | 60.2875 | 60.2417 | -61.1389 | -61.3449 | 0.022888 | 0.064087 | -0.09613 | 121.7056 | -0.086975 | -0.15106 | -0.16022 | 0.1236 | -0.082398 | -0.09613 | 0.19226 | -0.2655 | -0.18311 | -0.14191 | 121.55 | 121.4859 | 61.377 | -121.582 | 121.55 | 121.5042 | 61.4044 | -121.7285
116.4531 | 121.8201 | -61.2671 | 60.3241 | -0.081177 | 0.015793 | 0.071008 | 0.063643 | 0.13144 | 0.00017302 | -0.0022516 | -0.054626 | -0.0047788 | 0.064439 | 0.070818 | 0.0040225 | -0.0072483 | 60.2325 | 60.434 | 0.059509 | -61.3724 | 60.228 | -61.2762 | -61.2305 | -61.0565 | 0.1236 | -61.5234 | 60.2234 | 60.1685 | -61.1847 | -61.3861 | -0.009155 | 0.036621 | -0.096131 | 121.7011 | -0.10528 | -0.14191 | -0.091553 | 0.082398 | -0.11902 | -0.10071 | 0.21057 | -0.25635 | -0.13733 | -0.15564 | 121.4951 | 121.4996 | 61.3266 | -121.5546 | 121.4905 | 121.4355 | 61.3907 | -121.7102
118.2031 | 121.9208 | -61.2579 | 60.2737 | 0.13245 | 0.014298 | 0.069727 | 0.064283 | 0.12973 | -0.0045266 | -0.0009698 | 0.22766 | -0.003497 | 0.062089 | 0.069109 | 0.0055179 | -0.0044711 | 60.1593 | 60.3653 | -0.10071 | -61.4273 | 60.173 | -61.3266 | -61.29 | -61.0657 | -0.022888 | -61.5326 | 60.1456 | 60.1227 | -61.2122 | -61.3724 | -0.068664 | -0.032043 | -0.10071 | 121.6232 | -0.16937 | -0.13733 | -0.11444 | 0.045777 | -0.11444 | -0.12817 | 0.19226 | -0.27466 | -0.16022 | -0.15106 | 121.431 | 121.4172 | 61.1572 | -121.5637 | 121.4035 | 121.3806 | 61.235 | -121.6461
119.8906 | 121.7972 | -61.2122 | 60.4065 | -0.18799 | 0.01622 | 0.072504 | 0.068983 | 0.12888 | -0.006663 | -0.0024652 | -0.11566 | -0.006915 | 0.062089 | 0.072741 | 0.00039091 | -0.0068209 | 60.3104 | 60.553 | 0.2243 | -61.2762 | 60.2188 | -61.2167 | -61.171 | -60.997 | 0.24261 | -61.4365 | 60.26 | 60.2371 | -61.1206 | -61.3129 | -0.004578 | 0.041199 | -0.18768 | 121.7651 | -0.064087 | -0.10529 | -0.09613 | 0.091553 | -0.10071 | -0.14648 | 0.21515 | -0.2243 | -0.1236 | -0.16937 | 121.431 | 121.5225 | 61.4365 | -121.5775 | 121.4722 | 121.4493 | 61.4548 | -121.7194
121.6406 | 121.8796 | -61.2167 | 60.3561 | 0.040894 | 0.013657 | 0.071436 | 0.069197 | 0.12866 | -0.007731 | -0.0043878 | 0.16663 | -0.0060606 | 0.061876 | 0.070818 | 0.00039091 | -0.0066073 | 60.2325 | 60.4706 | 0.045776 | -61.3495 | 60.2005 | -61.2213 | -61.203 | -61.0199 | 0.09613 | -61.4639 | 60.2051 | 60.1868 | -61.1389 | -61.3358 | -0.004577 | 0.013733 | -0.15564 | 121.6873 | -0.13275 | -0.14648 | -0.1236 | 0.07782 | -0.11902 | -0.15106 | 0.19684 | -0.24719 | -0.12817 | -0.16937 | 121.4172 | 121.4493 | 61.2625 | -121.5591 | 121.4218 | 121.4035 | 61.3129 | -121.6919
123.3906 | 121.9025 | -61.203 | 60.3653 | 0.0027468 | 0.013871 | 0.073358 | 0.068769 | 0.12909 | -0.0047404 | -0.003747 | 0.12848 | -0.005206 | 0.061662 | 0.070818 | -0.00046349 | -0.0070345 | 60.2463 | 60.4614 | 0.050354 | -61.3495 | 60.2051 | -61.2442 | -61.1801 | -61.0291 | 0.10529 | -61.4685 | 60.2417 | 60.1822 | -61.1252 | -61.3312 | -0.041199 | 0.022888 | -0.16022 | 121.6644 | -0.14648 | -0.16937 | -0.11902 | 0.07782 | -0.12817 | -0.1236 | 0.17395 | -0.2655 | -0.13733 | -0.18311 | 121.4081 | 121.4493 | 61.2534 | -121.5454 | 121.4447 | 121.3852 | 61.3083 | -121.6965
125.0781 | 121.8796 | -61.2167 | 60.3424 | 0.094299 | 0.010666 | 0.072931 | 0.063856 | 0.12888 | -0.0040994 | -0.0063104 | 0.159 | -0.0060606 | 0.061662 | 0.06975 | 0.0020999 | -0.0081027 | 60.2554 | 60.4706 | 0.032043 | -61.3541 | 60.1593 | -61.2717 | -61.2076 | -61.0107 | 0.064087 | -61.4639 | 60.1913 | 60.1501 | -61.1343 | -61.3174 | -0.054931 | 0.009155 | -0.18311 | 121.6873 | -0.13733 | -0.14648 | -0.086975 | 0.082398 | -0.10071 | -0.15106 | 0.20599 | -0.24719 | -0.14648 | -0.19226 | 121.376 | 121.4722 | 61.2488 | -121.55 | 121.4081 | 121.3669 | 61.2808 | -121.6599
126.8125 | 121.8887 | -61.1847 | 60.4111 | -0.1651 | 0.013016 | 0.072717 | 0.06642 | 0.12802 | -0.0051676 | -0.0063104 | -0.10803 | -0.0073422 | 0.062303 | 0.071032 | -0.0013181 | -0.010239 | 60.3607 | 60.585 | 0.24719 | -61.2717 | 60.2554 | -61.2076 | -61.1481 | -60.9283 | 0.30212 | -61.3678 | 60.2554 | 60.2234 | -61.0977 | -61.2717 | -0.022889 | 0.036621 | -0.15564 | 121.7697 | -0.086975 | -0.1236 | -0.050354 | 0.086975 | -0.086975 | -0.15564 | 0.25635 | -0.18311 | -0.096131 | -0.18768 | 121.4401 | 121.5454 | 61.4319 | -121.5591 | 121.4401 | 121.4081 | 61.4868 | -121.6827
128.5625 | 121.8201 | -61.2808 | 60.3333 | -0.081177 | 0.013657 | 0.070367 | 0.064711 | 0.12866 | 0.0027364 | -0.0041742 | -0.10803 | -0.0043516 | 0.062944 | 0.073168 | 0.0055179 | -0.0095981 | 60.26 | 60.4385 | 0.054932 | -61.3678 | 60.2142 | -61.2854 | -61.2534 | -61.0428 | 0.09613 | -61.5234 | 60.228 | 60.1868 | -61.1984 | -61.3907 | -0.004577 | 0.027466 | -0.11902 | 121.7194 | -0.086975 | -0.11444 | -0.073242 | 0.082398 | -0.10986 | -0.10529 | 0.23804 | -0.24261 | -0.13275 | -0.14648 | 121.4951 | 121.5408 | 61.3358 | -121.5866 | 121.5088 | 121.4676 | 61.377 | -121.7239
130.3125 | 121.8887 | -61.2305 | 60.2921 | 0.14771 | 0.011948 | 0.069086 | 0.064924 | 0.12888 | -0.0040994 | -0.002038 | 0.22766 | -0.0094786 | 0.059953 | 0.068896 | 0.0044497 | -0.0072483 | 60.2371 | 60.466 | -0.013733 | -61.377 | 60.1089 | -61.2854 | -61.2534 | -61.0153 | 0.036621 | -61.4822 | 60.1501 | 60.1181 | -61.2167 | -61.3724 | -0.054931 | -0.022888 | -0.18311 | 121.6965 | -0.14648 | -0.1236 | -0.054931 | 0.013733 | -0.14191 | -0.14191 | 0.21515 | -0.25177 | -0.10986 | -0.17395 | 121.3394 | 121.4676 | 61.2167 | -121.5454 | 121.3806 | 121.3486 | 61.2671 | -121.6644
131.9844 | 121.875 | -61.1893 | 60.4156 | -0.18799 | 0.013657 | 0.072717 | 0.068342 | 0.12759 | -0.004313 | -0.008233 | -0.077515 | -0.0067014 | 0.062944 | 0.070391 | 0.00060451 | -0.0078891 | 60.3561 | 60.5942 | 0.25177 | -61.2534 | 60.2325 | -61.1938 | -61.1572 | -60.9329 | 0.30212 | -61.3907 | 60.2554 | 60.2371 | -61.0886 | -61.3083 | -0.004578 | 0.032043 | -0.18311 | 121.7834 | -0.064087 | -0.09613 | -0.059509 | 0.10071 | -0.11902 | -0.16022 | 0.25635 | -0.20142 | -0.082397 | -0.17853 | 121.4218 | 121.5454 | 61.441 | -121.5729 | 121.4447 | 121.4264 | 61.4914 | -121.7239
133.7188 | 121.8292 | -61.2396 | 60.3699 | -0.23376 | 0.018784 | 0.072076 | 0.070265 | 0.12845 | -0.0023904 | -0.0050286 | -0.20721 | -0.0043516 | 0.062089 | 0.069964 | 0.0014591 | -0.0085299 | 60.26 | 60.4431 | 0.12817 | -61.3449 | 60.2783 | -61.2396 | -61.1984 | -61.0611 | 0.14648 | -61.528 | 60.2966 | 60.2325 | -61.1664 | -61.3174 | 0 | 0.041199 | -0.091553 | 121.6827 | -0.10529 | -0.14648 | -0.10986 | 0.073242 | -0.07782 | -0.073242 | 0.17853 | -0.28839 | -0.21057 | -0.13733 | 121.5179 | 121.4996 | 61.3678 | -121.5683 | 121.5363 | 121.4722 | 61.3861 | -121.6873
135.3906 | 121.9345 | -61.2579 | 60.2692 | 0.11719 | 0.013871 | 0.071863 | 0.062574 | 0.12781 | -0.00089518 | -0.0033196 | 0.16663 | -0.0043516 | 0.062089 | 0.0721 | 0.0065859 | -0.0085299 | 60.1776 | 60.3561 | -0.11444 | -61.441 | 60.1776 | -61.3266 | -61.3083 | -61.0794 | -0.045776 | -61.5601 | 60.173 | 60.1135 | -61.2396 | -61.409 | -0.068664 | -0.050354 | -0.091553 | 121.6141 | -0.1831 | -0.13275 | -0.091553 | 0.018311 | -0.15106 | -0.09613 | 0.17853 | -0.30212 | -0.15106 | -0.15564 | 121.4355 | 121.4355 | 61.1435 | -121.5775 | 121.431 | 121.3715 | 61.2122 | -121.6782
137.1406 | 121.9208 | -61.2442 | 60.3149 | 0.13245 | 0.01622 | 0.069299 | 0.065565 | 0.13187 | -0.00068138 | -0.0035334 | 0.20477 | -0.0054196 | 0.061021 | 0.070391 | 0.0014591 | -0.0076755 | 60.2554 | 60.4568 | -0.013733 | -61.377 | 60.1089 | -61.3083 | -61.2625 | -61.0245 | 0.018311 | -61.4868 | 60.1227 | 60.0906 | -61.1801 | -61.3861 | -0.064087 | -0.01831 | -0.20599 | 121.7011 | -0.13275 | -0.11444 | -0.059509 | 0.064087 | -0.14191 | -0.19226 | 0.21973 | -0.24261 | -0.10071 | -0.2243 | 121.3531 | 121.4996 | 61.2305 | -121.5775 | 121.3669 | 121.3348 | 61.2625 | -121.701
138.8281 | 121.8155 | -61.2762 | 60.3882 | -0.13458 | 0.015793 | 0.072504 | 0.069624 | 0.12888 | -0.0021768 | -0.002038 | -0.15381 | -0.0062742 | 0.062089 | 0.070818 | 0.00017731 | -0.0078891 | 60.2554 | 60.4523 | 0.13733 | -61.3541 | 60.2417 | -61.2259 | -61.1984 | -61.0611 | 0.16479 | -61.5051 | 60.3012 | 60.2509 | -61.1526 | -61.3174 | 0.050354 | 0.07782 | -0.14649 | 121.7285 | -0.07782 | -0.15564 | -0.13275 | 0.1236 | -0.041199 | -0.086976 | 0.21515 | -0.22888 | -0.18768 | -0.13733 | 121.5179 | 121.5317 | 61.4136 | -121.5866 | 121.5775 | 121.5271 | 61.441 | -121.7056
140.5938 | 121.9254 | -61.1847 | 60.3607 | 0.018005 | 0.014511 | 0.071008 | 0.069197 | 0.12781 | -0.0070902 | -0.005456 | 0.13611 | -0.0060606 | 0.059953 | 0.071245 | 0.00060451 | -0.0078891 | 60.2509 | 60.4523 | 0.054932 | -61.3312 | 60.2142 | -61.235 | -61.203 | -61.0153 | 0.091553 | -61.4685 | 60.2142 | 60.2051 | -61.1343 | -61.322 | -0.050354 | -0.018311 | -0.14648 | 121.637 | -0.14648 | -0.12817 | -0.10986 | 0.050354 | -0.13733 | -0.14648 | 0.16937 | -0.28381 | -0.14648 | -0.15564 | 121.3989 | 121.4355 | 61.2396 | -121.5637 | 121.3989 | 121.3898 | 61.2762 | -121.6827
142.3281 | 121.8887 | -61.2488 | 60.347 | 0.094299 | 0.010453 | 0.07229 | 0.06407 | 0.12952 | -0.0051676 | -0.0046014 | 0.16663 | -0.0062742 | 0.060808 | 0.070391 | 0.0018863 | -0.0085299 | 60.2692 | 60.466 | 0.027466 | -61.3586 | 60.2005 | -61.2625 | -61.1984 | -60.997 | 0.064087 | -61.4777 | 60.1959 | 60.2005 | -61.1389 | -61.3632 | -0.013733 | 0.050354 | -0.14648 | 121.7148 | -0.10986 | -0.16022 | -0.07782 | 0.10986 | -0.11444 | -0.15106 | 0.25177 | -0.22888 | -0.11444 | -0.14648 | 121.4493 | 121.5179 | 61.2762 | -121.5454 | 121.4447 | 121.4493 | 61.3129 | -121.7102
144.0156 | 121.9208 | -61.1938 | 60.3928 | -0.11932 | 0.013871 | 0.07229 | 0.07176 | 0.13123 | -0.0034586 | -0.0050286 | -0.039368 | -0.007556 | 0.062089 | 0.069109 | -0.0011045 | -0.0081027 | 60.3516 | 60.585 | 0.2243 | -61.2671 | 60.2234 | -61.2122 | -61.1847 | -60.9009 | 0.27466 | -61.3541 | 60.2737 | 60.2142 | -61.0977 | -61.2625 | -0.01831 | 0.009156 | -0.16937 | 121.7789 | -0.073242 | -0.082398 | -0.041199 | 0.096131 | -0.068664 | -0.11902 | 0.29297 | -0.16022 | -0.091553 | -0.17853 | 121.4172 | 121.5454 | 61.4182 | -121.5775 | 121.4676 | 121.4081 | 61.4685 | -121.6553
145.7656 | 121.8933 | -61.2213 | 60.3287 | 0.018005 | 0.012802 | 0.071222 | 0.064924 | 0.12802 | -0.003245 | -0.0050286 | 0.097962 | -0.006915 | 0.061021 | 0.071245 | -0.00046349 | -0.0081027 | 60.2554 | 60.4614 | 0.045776 | -61.3541 | 60.1959 | -61.2579 | -61.2259 | -61.0199 | 0.086975 | -61.4822 | 60.2005 | 60.1913 | -61.1526 | -61.3266 | -0.036622 | -0.004578 | -0.13275 | 121.6827 | -0.13275 | -0.12817 | -0.073242 | 0.068664 | -0.10529 | -0.12817 | 0.20142 | -0.26093 | -0.15564 | -0.13733 | 121.4172 | 121.4767 | 61.2671 | -121.5546 | 121.4218 | 121.4127 | 61.3083 | -121.6553
147.4375 | 121.9345 | -61.1847 | 60.3195 | 0.0027468 | 0.01558 | 0.070581 | 0.065992 | 0.12695 | -0.004954 | -0.0056696 | 0.067444 | -0.0067014 | 0.061662 | 0.069536 | 0.0020999 | -0.0070345 | 60.2737 | 60.466 | 0.073242 | -61.3266 | 60.228 | -61.2305 | -61.2076 | -60.997 | 0.12817 | -61.4548 | 60.2234 | 60.2005 | -61.1389 | -61.29 | -0.045777 | -0.022889 | -0.091553 | 121.6507 | -0.14191 | -0.11902 | -0.045776 | 0.045776 | -0.10529 | -0.09613 | 0.18768 | -0.27008 | -0.1648 | -0.11902 | 121.4127 | 121.4584 | 61.2579 | -121.5271 | 121.4081 | 121.3852 | 61.3129 | -121.6095
149.1719 | 121.8704 | -61.2259 | 60.3287 | 0.13245 | 0.01323 | 0.070367 | 0.065351 | 0.1293 | -4.058e-05 | -0.0035334 | 0.13611 | -0.0067014 | 0.060594 | 0.071032 | 0.0018863 | -0.0083163 | 60.2921 | 60.4706 | 0.018311 | -61.3632 | 60.1364 | -61.2946 | -61.2167 | -60.9879 | 0.050354 | -61.4731 | 60.1639 | 60.1273 | -61.1801 | -61.3586 | -0.068665 | 0.009155 | -0.19226 | 121.6965 | -0.13733 | -0.14648 | -0.036621 | 0.045776 | -0.13275 | -0.16479 | 0.23804 | -0.24719 | -0.11444 | -0.20142 | 121.3623 | 121.5179 | 61.2442 | -121.5454 | 121.3898 | 121.3531 | 61.2762 | -121.6873
150.9375 | 121.7926 | -61.3266 | 60.3241 | -0.0354 | 0.01558 | 0.071436 | 0.064283 | 0.12866 | 0.006368 | -0.0016108 | -0.024109 | -0.005847 | 0.058672 | 0.072954 | 0.0061587 | -0.0093845 | 60.2325 | 60.3745 | -0.013733 | -61.4273 | 60.1959 | -61.322 | -61.29 | -61.1252 | -0.027466 | -61.6333 | 60.1776 | 60.1639 | -61.2305 | -61.4044 | 0.004578 | 0.036621 | -0.12817 | 121.7011 | -0.10071 | -0.13733 | -0.091553 | 0.09613 | -0.07782 | -0.14648 | 0.20142 | -0.3067 | -0.22888 | -0.16022 | 121.5225 | 121.5591 | 61.3129 | -121.6141 | 121.5042 | 121.4905 | 61.2991 | -121.7285
152.6875 | 121.8155 | -61.2854 | 60.3058 | -0.096436 | 0.016861 | 0.073358 | 0.068342 | 0.1293 | 0.0012412 | -0.003747 | -0.10803 | -0.0056332 | 0.063798 | 0.071459 | 0.0050907 | -0.0087435 | 60.2463 | 60.434 | 0.054932 | -61.3678 | 60.2051 | -61.2946 | -61.2762 | -61.0336 | 0.10071 | -61.5417 | 60.2097 | 60.2005 | -61.1984 | -61.3632 | -0.009156 | 0.009155 | -0.10071 | 121.7194 | -0.082398 | -0.091553 | -0.059509 | 0.086975 | -0.07782 | -0.09613 | 0.25177 | -0.25635 | -0.17853 | -0.10529 | 121.4905 | 121.5317 | 61.3403 | -121.582 | 121.4951 | 121.4859 | 61.3861 | -121.669
154.4219 | 121.7926 | -61.3037 | 60.3012 | -0.088806 | 0.018357 | 0.072504 | 0.065138 | 0.1293 | 0.00038662 | -0.0026788 | -0.069885 | -0.0022154 | 0.060381 | 0.070605 | 0.0048769 | -0.0074619 | 60.2509 | 60.4385 | 0.059509 | -61.3815 | 60.2005 | -61.2808 | -61.2717 | -61.0428 | 0.09613 | -61.5372 | 60.2142 | 60.1913 | -61.2122 | -61.3678 | 0.022888 | 0.032044 | -0.10071 | 121.7422 | -0.07782 | -0.10986 | -0.050354 | 0.091553 | -0.064087 | -0.086975 | 0.26093 | -0.23346 | -0.16937 | -0.10986 | 121.5042 | 121.5546 | 61.3632 | -121.5729 | 121.5179 | 121.4951 | 61.3998 | -121.669
156.125 | 121.9025 | -61.203 | 60.3607 | -0.0048827 | 0.012589 | 0.072717 | 0.066847 | 0.12717 | -0.0090128 | -0.0039606 | 0.10559 | -0.0062742 | 0.063585 | 0.072314 | -0.0013181 | -0.0055393 | 60.2417 | 60.4568 | 0.07782 | -61.3403 | 60.2234 | -61.235 | -61.1938 | -61.0107 | 0.1236 | -61.4548 | 60.1868 | 60.2142 | -61.1572 | -61.3266 | -0.032043 | 0.009155 | -0.13733 | 121.6599 | -0.13733 | -0.14648 | -0.11902 | 0.045776 | -0.1236 | -0.17395 | 0.19226 | -0.25177 | -0.12817 | -0.14648 | 121.4264 | 121.4447 | 61.2808 | -121.5546 | 121.3898 | 121.4172 | 61.3266 | -121.6873
157.8125 | 121.8796 | -61.2213 | 60.3241 | 0.14771 | 0.013871 | 0.070581 | 0.064711 | 0.1308 | -0.00025418 | -0.0022516 | 0.20477 | -0.0056332 | 0.061235 | 0.073595 | 0.0016727 | -0.0087435 | 60.2692 | 60.4431 | 0 | -61.3632 | 60.1456 | -61.3083 | -61.2488 | -60.9833 | 0.054932 | -61.4594 | 60.1547 | 60.141 | -61.1893 | -61.3632 | -0.086976 | -0.027466 | -0.17853 | 121.6644 | -0.14191 | -0.11444 | -0.054932 | 0.032043 | -0.14191 | -0.16937 | 0.23804 | -0.23804 | -0.096131 | -0.18311 | 121.3669 | 121.4905 | 61.2213 | -121.5729 | 121.376 | 121.3623 | 61.2762 | -121.6873
159.5469 | 121.8063 | -61.235 | 60.3836 | -0.21088 | 0.01558 | 0.071649 | 0.069624 | 0.12802 | -0.001536 | -0.0035334 | -0.14618 | -0.006915 | 0.064226 | 0.071886 | 0.00060451 | -0.0081027 | 60.2554 | 60.4385 | 0.13275 | -61.3632 | 60.2554 | -61.2213 | -61.2167 | -61.0382 | 0.19684 | -61.5051 | 60.3012 | 60.2875 | -61.1572 | -61.3266 | 0.013733 | 0.01831 | -0.12817 | 121.6736 | -0.12817 | -0.14648 | -0.12817 | 0.077819 | -0.091553 | -0.082398 | 0.19684 | -0.27008 | -0.17853 | -0.09613 | 121.4905 | 121.4905 | 61.3678 | -121.6003 | 121.5363 | 121.5225 | 61.4319 | -121.7102
161.3125 | 121.907 | -61.203 | 60.379 | 0.010376 | 0.014298 | 0.071649 | 0.067701 | 0.12781 | -0.006022 | -0.0039606 | 0.12085 | -0.0064878 | 0.061662 | 0.071459 | 0.00017731 | -0.0081027 | 60.2509 | 60.4477 | 0.059509 | -61.3495 | 60.2188 | -61.2488 | -61.1938 | -61.0245 | 0.10986 | -61.4731 | 60.2188 | 60.2051 | -61.1389 | -61.322 | -0.045776 | 0.009155 | -0.16022 | 121.6507 | -0.14648 | -0.15564 | -0.12817 | 0.064087 | -0.11902 | -0.16022 | 0.17853 | -0.27008 | -0.15106 | -0.17395 | 121.4218 | 121.4539 | 61.2625 | -121.5729 | 121.4218 | 121.4081 | 61.3129 | -121.701
163 | 121.7743 | -61.3174 | 60.2875 | -0.0354 | 0.01558 | 0.069513 | 0.064711 | 0.12781 | 0.003591 | -0.0022516 | -0.0088499 | -0.0060606 | 0.062089 | 0.072314 | 0.0048769 | -0.0083163 | 60.2417 | 60.3836 | 0.013733 | -61.4136 | 60.1913 | -61.2946 | -61.2717 | -61.1069 | 0 | -61.6013 | 60.1959 | 60.1685 | -61.235 | -61.4227 | 0.022888 | 0.045777 | -0.096131 | 121.7011 | -0.09613 | -0.14191 | -0.045777 | 0.082398 | -0.10528 | -0.091553 | 0.21057 | -0.28381 | -0.17853 | -0.11902 | 121.5088 | 121.5591 | 61.3312 | -121.5591 | 121.5134 | 121.4859 | 61.3174 | -121.7102
164.75 | 121.9528 | -61.1755 | 60.3836 | -0.058289 | 0.01323 | 0.072931 | 0.068129 | 0.13037 | -0.0075174 | -0.0050286 | 0.0064086 | -0.008624 | 0.062303 | 0.06975 | 0.0016727 | -0.0085299 | 60.2875 | 60.5164 | 0.12817 | -61.3083 | 60.2142 | -61.235 | -61.1801 | -60.9375 | 0.22888 | -61.3815 | 60.2234 | 60.2188 | -61.1343 | -61.3037 | -0.059509 | -0.004578 | -0.16937 | 121.6919 | -0.13275 | -0.12817 | -0.09613 | 0.041199 | -0.12817 | -0.16022 | 0.23804 | -0.20599 | -0.07782 | -0.16479 | 121.3898 | 121.463 | 61.3037 | -121.5637 | 121.3989 | 121.3943 | 61.4044 | -121.6873
166.4844 | 121.875 | -61.2305 | 60.3561 | 0.094299 | 0.012802 | 0.070795 | 0.064711 | 0.12781 | -0.0028178 | -0.0050286 | 0.2124 | -0.0060606 | 0.061021 | 0.070818 | 0.00039091 | -0.0076755 | 60.2692 | 60.466 | 0.027466 | -61.3724 | 60.1593 | -61.2808 | -61.235 | -60.997 | 0.068665 | -61.4914 | 60.2097 | 60.1501 | -61.1664 | -61.3541 | -0.050354 | -0.004577 | -0.19684 | 121.6965 | -0.14191 | -0.13733 | -0.086975 | 0.064087 | -0.1236 | -0.14648 | 0.23346 | -0.26093 | -0.13733 | -0.20599 | 121.3898 | 121.4996 | 61.2579 | -121.5912 | 121.4401 | 121.3806 | 61.2991 | -121.7102
168.2188 | 121.8933 | -61.235 | 60.3378 | 0.10956 | 0.013871 | 0.074213 | 0.063856 | 0.12866 | -0.002604 | -0.0022516 | 0.18951 | -0.0056332 | 0.058885 | 0.069109 | 0.0035953 | -0.0072483 | 60.2783 | 60.466 | 0.022888 | -61.3586 | 60.1273 | -61.2991 | -61.2488 | -60.9924 | 0.059509 | -61.4777 | 60.1685 | 60.141 | -61.1801 | -61.3632 | -0.064087 | -0.013733 | -0.21057 | 121.701 | -0.1236 | -0.10986 | -0.05951 | 0.054931 | -0.12817 | -0.16937 | 0.24261 | -0.24262 | -0.11444 | -0.19684 | 121.3623 | 121.5134 | 61.2579 | -121.5866 | 121.4035 | 121.376 | 61.2946 | -121.701
169.9062 | 121.7697 | -61.3174 | 60.3012 | -0.027771 | 0.016007 | 0.071008 | 0.065565 | 0.1293 | 0.0014548 | -0.0043878 | -0.024109 | -0.0049924 | 0.064653 | 0.072954 | 0.0067997 | -0.0083163 | 60.2097 | 60.3516 | -0.036621 | -61.4365 | 60.2051 | -61.3266 | -61.2946 | -61.1389 | -0.032043 | -61.6425 | 60.2005 | 60.141 | -61.2396 | -61.409 | -0.009155 | 0.022888 | -0.09613 | 121.669 | -0.11902 | -0.14191 | -0.091552 | 0.07782 | -0.091553 | -0.10071 | 0.17853 | -0.32501 | -0.23346 | -0.16022 | 121.5225 | 121.5271 | 61.2808 | -121.5958 | 121.5179 | 121.4584 | 61.2854 | -121.7102
171.6562 | 121.9208 | -61.2946 | 60.2417 | 0.11719 | 0.013871 | 0.071222 | 0.062361 | 0.12781 | -0.00068138 | -0.001397 | 0.16663 | -0.0073422 | 0.061021 | 0.070177 | 0.0048769 | -0.0081027 | 60.1776 | 60.3287 | -0.10986 | -61.441 | 60.1776 | -61.3312 | -61.2854 | -61.0657 | -0.041199 | -61.5692 | 60.1639 | 60.141 | -61.235 | -61.3907 | -0.036621 | 0.009156 | -0.064087 | 121.6232 | -0.14648 | -0.15564 | -0.064087 | 0.05951 | -0.09613 | -0.07782 | 0.22888 | -0.27466 | -0.17853 | -0.10071 | 121.4722 | 121.4722 | 61.1847 | -121.5271 | 121.4584 | 121.4355 | 61.2534 | -121.6324
173.4062 | 121.8796 | -61.2259 | 60.3516 | 0.094299 | 0.015152 | 0.070581 | 0.067488 | 0.13037 | -0.0055948 | -0.003106 | 0.18951 | -0.0071286 | 0.062944 | 0.069536 | 0.00017731 | -0.0072483 | 60.2371 | 60.466 | 0.027466 | -61.3678 | 60.1685 | -61.2579 | -61.2396 | -61.0153 | 0.073242 | -61.4685 | 60.1868 | 60.1639 | -61.1572 | -61.3541 | -0.032044 | -0.013733 | -0.18311 | 121.6919 | -0.14191 | -0.12817 | -0.11444 | 0.068664 | -0.12817 | -0.16479 | 0.21057 | -0.24262 | -0.11444 | -0.18768 | 121.3943 | 121.463 | 61.2534 | -121.5912 | 121.4127 | 121.3898 | 61.2991 | -121.7056
175.1562 | 121.8658 | -61.2122 | 60.4019 | -0.20325 | 0.012802 | 0.070795 | 0.070692 | 0.12888 | -0.0051676 | -0.0052424 | -0.069885 | -0.0077696 | 0.060808 | 0.071886 | 0.00039091 | -0.0095981 | 60.347 | 60.5942 | 0.25635 | -61.2717 | 60.2325 | -61.1938 | -61.1526 | -60.9421 | 0.29297 | -61.3953 | 60.2371 | 60.2234 | -61.1252 | -61.29 | 0.01831 | 0.059509 | -0.16937 | 121.8063 | -0.059509 | -0.11902 | -0.054932 | 0.086975 | -0.07782 | -0.16479 | 0.27008 | -0.18311 | -0.10529 | -0.17853 | 121.4447 | 121.5591 | 61.4685 | -121.5546 | 121.4493 | 121.4355 | 61.5051 | -121.6919
176.8281 | 121.9208 | -61.2442 | 60.3012 | 0.14008 | 0.011948 | 0.071436 | 0.064283 | 0.12738 | -0.0011088 | -0.0026788 | 0.17426 | -0.0067014 | 0.060808 | 0.0721 | 0.0029543 | -0.01088 | 60.2417 | 60.4614 | -0.022888 | -61.3632 | 60.1318 | -61.3129 | -61.235 | -61.0199 | 0.018311 | -61.5005 | 60.1501 | 60.0906 | -61.2259 | -61.3998 | -0.068664 | 0.009156 | -0.16937 | 121.7056 | -0.11902 | -0.12817 | -0.059509 | 0.018311 | -0.15564 | -0.15106 | 0.22431 | -0.25635 | -0.10071 | -0.21057 | 121.376 | 121.4859 | 61.2213 | -121.5363 | 121.3943 | 121.3348 | 61.2625 | -121.701
178.5625 | 121.9116 | -61.2671 | 60.2829 | 0.094299 | 0.013443 | 0.073999 | 0.063215 | 0.12888 | -0.00068138 | -0.001397 | 0.11322 | -0.0062742 | 0.060167 | 0.071032 | 0.0065859 | -0.0074619 | 60.1639 | 60.3516 | -0.1236 | -61.4456 | 60.1868 | -61.3174 | -61.3037 | -61.1069 | -0.073242 | -61.6058 | 60.2097 | 60.1227 | -61.203 | -61.4136 | -0.050354 | -0.036621 | -0.09613 | 121.6187 | -0.17853 | -0.14191 | -0.11902 | 0.064087 | -0.14648 | -0.073242 | 0.16022 | -0.33874 | -0.19226 | -0.16022 | 121.4539 | 121.431 | 61.1435 | -121.5866 | 121.4767 | 121.3898 | 61.1938 | -121.6965
180.2344 | 121.9162 | -61.1847 | 60.3745 | -0.14984 | 0.013657 | 0.072717 | 0.06941 | 0.12631 | -0.0070902 | -0.003106 | -0.046997 | -0.0079832 | 0.061235 | 0.068682 | -0.00089089 | -0.0089573 | 60.3561 | 60.6262 | 0.22888 | -61.2396 | 60.228 | -61.1847 | -61.1664 | -60.9146 | 0.32501 | -61.3541 | 60.2463 | 60.2051 | -61.1069 | -61.2854 | 0 | 0.01831 | -0.14648 | 121.8109 | -0.054932 | -0.073242 | -0.018311 | 0.077819 | -0.10071 | -0.12817 | 0.27008 | -0.16937 | -0.068665 | -0.16937 | 121.4127 | 121.5408 | 61.4136 | -121.5408 | 121.431 | 121.3898 | 61.5097 | -121.6599
181.9844 | 121.8384 | -61.2854 | 60.3653 | -0.19562 | 0.016007 | 0.071008 | 0.067488 | 0.12845 | -0.00025418 | -0.0052424 | -0.15381 | -0.004138 | 0.063585 | 0.072527 | 0.0014591 | -0.010453 | 60.2371 | 60.4156 | 0.091553 | -61.3632 | 60.2829 | -61.2717 | -61.2305 | -61.0565 | 0.14191 | -61.5372 | 60.2966 | 60.2509 | -61.1572 | -61.3586 | 0.013733 | 0.054931 | -0.082397 | 121.701 | -0.07782 | -0.13275 | -0.12817 | 0.12817 | -0.073243 | -0.068664 | 0.22888 | -0.25177 | -0.17853 | -0.11444 | 121.5683 | 121.5225 | 61.377 | -121.5958 | 121.582 | 121.5363 | 61.4273 | -121.7239
183.7188 | 121.9482 | -61.1893 | 60.3516 | -0.012512 | 0.012802 | 0.073358 | 0.062788 | 0.1308 | -0.0073038 | -0.0052424 | 0.067444 | -0.0043516 | 0.061235 | 0.068468 | -0.00024989 | -0.0063937 | 60.2783 | 60.4889 | 0.09613 | -61.3266 | 60.2051 | -61.2396 | -61.1893 | -60.965 | 0.19684 | -61.409 | 60.2325 | 60.2051 | -61.1252 | -61.2946 | -0.050354 | 0 | -0.14648 | 121.6782 | -0.13733 | -0.13733 | -0.073242 | 0.064087 | -0.10529 | -0.11902 | 0.2243 | -0.21973 | -0.11444 | -0.14648 | 121.3943 | 121.4676 | 61.2854 | -121.5408 | 121.4218 | 121.3943 | 61.3861 | -121.6461
185.4531 | 121.788 | -61.2305 | 60.4477 | -0.23376 | 0.016007 | 0.073572 | 0.068342 | 0.12845 | -0.0028178 | -0.0041742 | -0.12329 | -0.0049924 | 0.064012 | 0.071459 | 0.0012455 | -0.0089573 | 60.3058 | 60.5118 | 0.21057 | -61.3083 | 60.2509 | -61.2305 | -61.1984 | -61.0153 | 0.21057 | -61.4731 | 60.2737 | 60.2692 | -61.1389 | -61.3037 | 0 | 0.032044 | -0.19684 | 121.7422 | -0.07782 | -0.10986 | -0.14191 | 0.091553 | -0.073242 | -0.17395 | 0.21515 | -0.24261 | -0.16937 | -0.17853 | 121.4813 | 121.5363 | 61.441 | -121.6461 | 121.5042 | 121.4996 | 61.441 | -121.7514
187.1406 | 121.8796 | -61.2305 | 60.3195 | 0.094299 | 0.012375 | 0.074213 | 0.064711 | 0.12866 | -0.0028178 | -0.0026788 | 0.17426 | -0.0071286 | 0.060381 | 0.071673 | 0.0046633 | -0.0063937 | 60.2554 | 60.4889 | 0.027466 | -61.3632 | 60.1547 | -61.2946 | -61.2396 | -60.9924 | 0.059509 | -61.4777 | 60.1822 | 60.141 | -61.1893 | -61.3632 | -0.064087 | -0.009155 | -0.16479 | 121.7194 | -0.13275 | -0.1236 | -0.064087 | 0.041199 | -0.13275 | -0.13733 | 0.23804 | -0.24719 | -0.11444 | -0.17853 | 121.3852 | 121.4859 | 61.2579 | -121.5591 | 121.4127 | 121.3715 | 61.29 | -121.6827
188.8906 | 121.8887 | -61.2305 | 60.3287 | 0.10956 | 0.016007 | 0.071008 | 0.065565 | 0.12781 | -0.0013224 | -0.0033196 | 0.159 | -0.0077696 | 0.061662 | 0.071032 | 0.0016727 | -0.0076755 | 60.26 | 60.4935 | 0.022888 | -61.3632 | 60.1547 | -61.2808 | -61.2625 | -61.0016 | 0.064087 | -61.4731 | 60.1593 | 60.1273 | -61.1938 | -61.3632 | -0.050354 | -0.032043 | -0.17395 | 121.7239 | -0.13275 | -0.10071 | -0.068664 | 0.036621 | -0.13275 | -0.16937 | 0.22888 | -0.24261 | -0.10986 | -0.20142 | 121.3852 | 121.4905 | 61.2534 | -121.5912 | 121.3898 | 121.3577 | 61.2946 | -121.6919
190.5781 | 121.8109 | -61.2488 | 60.3973 | -0.21088 | 0.013871 | 0.073145 | 0.065992 | 0.13037 | -0.00046778 | -0.0052424 | -0.2301 | -0.0060606 | 0.063585 | 0.06975 | 0.00017731 | -0.0083163 | 60.2692 | 60.4431 | 0.12817 | -61.3632 | 60.2783 | -61.235 | -61.203 | -61.0382 | 0.17395 | -61.5097 | 60.3058 | 60.2875 | -61.1618 | -61.3266 | 0.013733 | 0.045776 | -0.11902 | 121.6919 | -0.11444 | -0.16022 | -0.12817 | 0.086975 | -0.07782 | -0.091553 | 0.21057 | -0.26093 | -0.18311 | -0.10986 | 121.5271 | 121.5179 | 61.377 | -121.6003 | 121.5546 | 121.5363 | 61.4227 | -121.7239
192.3281 | 121.8018 | -61.2259 | 60.4019 | -0.38635 | 0.014511 | 0.070795 | 0.067488 | 0.1293 | -0.0023904 | -0.0052424 | -0.14618 | -0.0062742 | 0.062303 | 0.071459 | 0.00017731 | -0.0072483 | 60.2646 | 60.4431 | 0.15106 | -61.3586 | 60.2921 | -61.235 | -61.2122 | -61.0291 | 0.17395 | -61.5051 | 60.3058 | 60.2737 | -61.1435 | -61.3083 | -0.009155 | 0.013733 | -0.10986 | 121.669 | -0.13275 | -0.14648 | -0.13733 | 0.082397 | -0.082398 | -0.096131 | 0.19684 | -0.27924 | -0.19684 | -0.12817 | 121.5179 | 121.4905 | 61.377 | -121.6141 | 121.5317 | 121.4996 | 61.3998 | -121.7102
194.0781 | 121.8979 | -61.2076 | 60.3653 | 0.018005 | 0.01323 | 0.073358 | 0.065779 | 0.13037 | -0.0062356 | -0.003106 | 0.11322 | -0.0062742 | 0.059953 | 0.071245 | 0.0018863 | -0.0087435 | 60.2554 | 60.4568 | 0.050354 | -61.3449 | 60.2188 | -61.2442 | -61.1938 | -61.0153 | 0.10071 | -61.4685 | 60.2188 | 60.2142 | -61.1526 | -61.3266 | -0.036621 | 0.013733 | -0.14648 | 121.6644 | -0.13733 | -0.15106 | -0.10986 | 0.054932 | -0.11902 | -0.14648 | 0.19226 | -0.26093 | -0.14191 | -0.15106 | 121.4264 | 121.463 | 61.2579 | -121.5591 | 121.4264 | 121.4218 | 61.3083 | -121.6919
195.8281 | 121.8063 | -61.2991 | 60.3287 | -0.012512 | 0.015366 | 0.071008 | 0.063856 | 0.12824 | 0.0061544 | -0.0035334 | 0.036926 | -0.0043516 | 0.060167 | 0.070818 | 0.0053043 | -0.0087435 | 60.1776 | 60.3012 | -0.07782 | -61.4319 | 60.1959 | -61.3358 | -61.2854 | -61.1526 | -0.059509 | -61.6379 | 60.228 | 60.173 | -61.235 | -61.4227 | -0.036621 | 0.013733 | -0.13275 | 121.6003 | -0.13275 | -0.14648 | -0.15106 | 0.064087 | -0.1236 | -0.10071 | 0.14648 | -0.33875 | -0.21515 | -0.15564 | 121.4951 | 121.4767 | 61.2213 | -121.6141 | 121.5271 | 121.4722 | 61.2396 | -121.7514
197.5625 | 121.875 | -61.2122 | 60.3195 | 0.079041 | 0.010453 | 0.072931 | 0.064711 | 0.13037 | -0.006022 | -0.003106 | 0.18951 | -0.007556 | 0.063158 | 0.070605 | 0.0040225 | -0.0061801 | 60.2463 | 60.4797 | 0.027466 | -61.377 | 60.141 | -61.2762 | -61.2442 | -60.9879 | 0.07782 | -61.4639 | 60.1868 | 60.1593 | -61.171 | -61.3495 | -0.064087 | -0.032044 | -0.17853 | 121.6919 | -0.16479 | -0.13275 | -0.073242 | 0.041199 | -0.13733 | -0.13275 | 0.2243 | -0.25177 | -0.11444 | -0.16022 | 121.3531 | 121.4584 | 61.2396 | -121.5637 | 121.3989 | 121.3715 | 61.29 | -121.669
199.2344 | 121.8292 | -61.2122 | 60.4065 | -0.19562 | 0.015366 | 0.072931 | 0.070265 | 0.12802 | -0.0038858 | -0.0058832 | -0.092773 | -0.0081968 | 0.061449 | 0.070605 | -0.00046349 | -0.0078891 | 60.3424 | 60.5621 | 0.24261 | -61.2808 | 60.2371 | -61.2167 | -61.1526 | -60.9421 | 0.29297 | -61.4044 | 60.2509 | 60.2097 | -61.1298 | -61.2854 | -0.004578 | 0.059509 | -0.16937 | 121.7743 | -0.068665 | -0.12817 | -0.064087 | 0.082397 | -0.073242 | -0.15564 | 0.27008 | -0.19226 | -0.11902 | -0.19684 | 121.4493 | 121.5546 | 61.4548 | -121.5591 | 121.463 | 121.4218 | 61.5051 | -121.6919
200.9844 | 121.8384 | -61.2625 | 60.3745 | -0.22614 | 0.015366 | 0.071863 | 0.066633 | 0.12994 | -0.0030314 | -0.0028924 | -0.19958 | -0.005206 | 0.06273 | 0.073809 | 0.0020999 | -0.0087435 | 60.2554 | 60.4248 | 0.11444 | -61.3541 | 60.2692 | -61.2442 | -61.2488 | -61.0474 | 0.15106 | -61.5234 | 60.3058 | 60.2692 | -61.1755 | -61.3403 | 0.01831 | 0.013733 | -0.10529 | 121.6873 | -0.091553 | -0.10529 | -0.11902 | 0.086975 | -0.07782 | -0.068665 | 0.21515 | -0.26093 | -0.18311 | -0.10529 | 121.5317 | 121.5179 | 61.377 | -121.6232 | 121.5683 | 121.5317 | 61.4136 | -121.7148
202.7344 | 121.843 | -61.2671 | 60.347 | -0.20325 | 0.017075 | 0.068445 | 0.067915 | 0.12802 | 0.0023092 | -0.0011834 | -0.13092 | -0.0028562 | 0.063798 | 0.073595 | 0.0027407 | -0.01088 | 60.26 | 60.4111 | 0.10529 | -61.3449 | 60.2646 | -61.2534 | -61.2259 | -61.0611 | 0.15564 | -61.5234 | 60.2737 | 60.2509 | -61.1801 | -61.3495 | 0.013733 | 0.041199 | -0.082398 | 121.6782 | -0.07782 | -0.11902 | -0.086975 | 0.086975 | -0.082397 | -0.073242 | 0.20599 | -0.25635 | -0.17395 | -0.096131 | 121.5317 | 121.5271 | 61.3724 | -121.5729 | 121.5408 | 121.5179 | 61.4227 | -121.6965
204.4219 | 121.9254 | -61.29 | 60.2509 | 0.11719 | 0.015152 | 0.071863 | 0.064711 | 0.13037 | -0.00025418 | -0.001397 | 0.20477 | -0.004138 | 0.062944 | 0.071459 | 0.0038089 | -0.0061801 | 60.1593 | 60.3607 | -0.10071 | -61.4456 | 60.1547 | -61.3449 | -61.29 | -61.0657 | -0.041199 | -61.5601 | 60.1776 | 60.1181 | -61.235 | -61.4044 | -0.054932 | 0 | -0.09613 | 121.6507 | -0.15564 | -0.15564 | -0.091552 | 0.054932 | -0.11444 | -0.073242 | 0.2243 | -0.27008 | -0.15564 | -0.13275 | 121.4447 | 121.4493 | 61.1893 | -121.5408 | 121.4676 | 121.4081 | 61.2488 | -121.6553
206.1875 | 121.8018 | -61.3037 | 60.3333 | -0.073547 | 0.014725 | 0.070795 | 0.065992 | 0.13059 | -4.058e-05 | -0.0011834 | -0.016479 | -0.005847 | 0.061662 | 0.071459 | 0.0027407 | -0.0070345 | 60.2371 | 60.434 | 0.027466 | -61.3907 | 60.2097 | -61.2946 | -61.2762 | -61.1023 | 0.018311 | -61.5829 | 60.2051 | 60.1685 | -61.2488 | -61.4365 | 0.009155 | 0.027466 | -0.1236 | 121.7377 | -0.086975 | -0.11444 | -0.09613 | 0.054932 | -0.13275 | -0.12817 | 0.20142 | -0.27924 | -0.14648 | -0.1648 | 121.5134 | 121.5408 | 61.3312 | -121.6095 | 121.5088 | 121.4722 | 61.322 | -121.7697
207.9375 | 121.8109 | -61.3037 | 60.3104 | 0.056152 | 0.016007 | 0.071436 | 0.065779 | 0.12952 | -4.058e-05 | -0.0001154 | 0.10559 | -0.0043516 | 0.062944 | 0.072527 | 0.0042361 | -0.0057529 | 60.1318 | 60.3287 | -0.10529 | -61.4594 | 60.1913 | -61.3312 | -61.3083 | -61.1755 | -0.07782 | -61.6379 | 60.1822 | 60.1364 | -61.2671 | -61.4456 | -0.027466 | -0.004578 | -0.11902 | 121.6324 | -0.15564 | -0.15106 | -0.17853 | 0.036621 | -0.14191 | -0.12817 | 0.12817 | -0.33417 | -0.19226 | -0.17395 | 121.4951 | 121.4355 | 61.1984 | -121.6187 | 121.4859 | 121.4401 | 61.2259 | -121.756
209.6719 | 121.8063 | -61.2305 | 60.4202 | -0.23376 | 0.013016 | 0.071863 | 0.068129 | 0.13037 | -0.006663 | -0.0028924 | -0.054626 | -0.0077696 | 0.061021 | 0.071032 | -0.0019589 | -0.0059665 | 60.2783 | 60.498 | 0.1831 | -61.3174 | 60.2692 | -61.1938 | -61.1938 | -61.0519 | 0.19684 | -61.4914 | 60.2646 | 60.2417 | -61.1664 | -61.322 | 0.036621 | 0.036621 | -0.15106 | 121.7285 | -0.086975 | -0.1236 | -0.14191 | 0.064087 | -0.091552 | -0.15564 | 0.17853 | -0.26093 | -0.16937 | -0.17853 | 121.4996 | 121.5088 | 61.4136 | -121.6141 | 121.4951 | 121.4722 | 61.4273 | -121.7422
211.3594 | 121.9345 | -61.2625 | 60.2646 | 0.14771 | 0.013443 | 0.074426 | 0.066206 | 0.12695 | -0.0013224 | -0.0026788 | 0.18951 | -0.0056332 | 0.05974 | 0.070605 | 0.0038089 | -0.0063937 | 60.1593 | 60.3653 | -0.10071 | -61.4273 | 60.1456 | -61.3174 | -61.2808 | -61.0565 | 0.004578 | -61.5326 | 60.1685 | 60.1227 | -61.2488 | -61.377 | -0.054932 | -0.018311 | -0.11902 | 121.6278 | -0.16479 | -0.14648 | -0.10529 | 0.013733 | -0.11444 | -0.09613 | 0.20599 | -0.27008 | -0.15564 | -0.14191 | 121.4081 | 121.4218 | 61.1618 | -121.5454 | 121.431 | 121.3852 | 61.2671 | -121.6415
213.125 | 121.8201 | -61.3129 | 60.2966 | 0.048523 | 0.017289 | 0.071008 | 0.064924 | 0.12824 | -0.00068138 | -0.0009698 | 0.044556 | -0.005206 | 0.061449 | 0.070605 | 0.0038089 | -0.0076755 | 60.1227 | 60.3195 | -0.10071 | -61.4502 | 60.1913 | -61.3403 | -61.3083 | -61.1893 | -0.10071 | -61.6791 | 60.1959 | 60.1913 | -61.2625 | -61.409 | -0.027466 | 0.004577 | -0.10529 | 121.6324 | -0.13733 | -0.14191 | -0.17395 | 0.050354 | -0.096131 | -0.10071 | 0.1236 | -0.36621 | -0.27008 | -0.10529 | 121.5042 | 121.4355 | 61.2122 | -121.6049 | 121.5088 | 121.5042 | 61.2122 | -121.7056
214.8125 | 121.8887 | -61.2396 | 60.3333 | 0.14771 | 0.013016 | 0.073145 | 0.066847 | 0.1293 | -0.0053812 | -0.0026788 | 0.22003 | -0.0045652 | 0.061021 | 0.069964 | 0.0014591 | -0.0048983 | 60.2554 | 60.4568 | 0.004578 | -61.3586 | 60.1273 | -61.2808 | -61.2442 | -61.0153 | 0.059509 | -61.4685 | 60.1776 | 60.1547 | -61.1847 | -61.3541 | -0.041199 | -0.004578 | -0.20599 | 121.6965 | -0.11902 | -0.11444 | -0.07782 | 0.054932 | -0.11444 | -0.15564 | 0.2243 | -0.22888 | -0.11444 | -0.17853 | 121.3669 | 121.4951 | 61.2442 | -121.5775 | 121.4172 | 121.3943 | 61.2991 | -121.6873
216.5625 | 121.8155 | -61.2991 | 60.3241 | 0.063782 | 0.014298 | 0.072717 | 0.064497 | 0.12952 | -0.0011088 | -0.0022516 | 0.13611 | -0.005847 | 0.062303 | 0.070818 | 0.0044497 | -0.0072483 | 60.1318 | 60.2921 | -0.12817 | -61.4914 | 60.1776 | -61.3266 | -61.3037 | -61.171 | -0.11444 | -61.6516 | 60.1868 | 60.1547 | -61.2579 | -61.441 | -0.027466 | -0.004578 | -0.14648 | 121.5912 | -0.19226 | -0.18768 | -0.19226 | 0.041198 | -0.14191 | -0.13733 | 0.12817 | -0.35248 | -0.21057 | -0.16937 | 121.4767 | 121.431 | 61.171 | -121.6278 | 121.4859 | 121.4539 | 61.1847 | -121.7651
218.25 | 121.8201 | -61.1847 | 60.3973 | -0.20325 | 0.016007 | 0.072504 | 0.069838 | 0.1293 | -0.0064492 | -0.0016108 | -0.039368 | -0.0090512 | 0.062089 | 0.068896 | -3.629e-05 | -0.0066073 | 60.3149 | 60.5759 | 0.24719 | -61.2854 | 60.2234 | -61.2122 | -61.1755 | -60.9741 | 0.29297 | -61.3998 | 60.2463 | 60.2051 | -61.1252 | -61.3083 | -0.027466 | 0.009155 | -0.17395 | 121.7606 | -0.10071 | -0.10986 | -0.082398 | 0.059509 | -0.1236 | -0.15106 | 0.21057 | -0.21515 | -0.091552 | -0.19226 | 121.4081 | 121.4996 | 61.4319 | -121.5729 | 121.431 | 121.3898 | 61.4777 | -121.7056
219.9844 | 121.8933 | -61.2213 | 60.3699 | 0.048523 | 0.012375 | 0.073358 | 0.067915 | 0.13123 | -0.0062356 | -0.0058832 | 0.15137 | -0.005206 | 0.060594 | 0.070177 | -0.00089089 | -0.0087435 | 60.2325 | 60.4614 | 0.045776 | -61.3541 | 60.1959 | -61.2671 | -61.2076 | -61.0291 | 0.073242 | -61.4777 | 60.2097 | 60.2051 | -61.1572 | -61.322 | -0.045777 | 0.013732 | -0.17395 | 121.6827 | -0.13275 | -0.14648 | -0.13733 | 0.064086 | -0.10071 | -0.16022 | 0.19226 | -0.25635 | -0.15564 | -0.16479 | 121.4172 | 121.4539 | 61.2671 | -121.5775 | 121.431 | 121.4264 | 61.2946 | -121.6919
221.7344 | 121.8979 | -61.1984 | 60.4202 | -0.17273 | 0.014084 | 0.074213 | 0.06941 | 0.13037 | -0.0045266 | -0.0056696 | -0.062256 | -0.0084104 | 0.061449 | 0.069964 | 0.0014591 | -0.0083163 | 60.3561 | 60.5896 | 0.23346 | -61.2579 | 60.2371 | -61.1893 | -61.1343 | -60.9329 | 0.30212 | -61.3815 | 60.2783 | 60.1913 | -61.1206 | -61.2854 | 0.009155 | 0.064087 | -0.1831 | 121.788 | -0.05951 | -0.1236 | -0.064087 | 0.07782 | -0.086975 | -0.14191 | 0.2655 | -0.18311 | -0.096131 | -0.22888 | 121.4355 | 121.5546 | 61.4319 | -121.5546 | 121.4767 | 121.3898 | 61.5005 | -121.7056
223.4844 | 121.7834 | -61.3266 | 60.3104 | -0.027771 | 0.01558 | 0.070154 | 0.063429 | 0.12802 | 0.0023092 | -0.0033196 | 0.014038 | -0.003497 | 0.061449 | 0.071886 | 0.0074405 | -0.0091709 | 60.2142 | 60.3561 | -0.027466 | -61.4319 | 60.1868 | -61.3174 | -61.2625 | -61.1481 | -0.050354 | -61.647 | 60.2142 | 60.173 | -61.2396 | -61.4273 | 0.009155 | 0.064087 | -0.1236 | 121.6827 | -0.10529 | -0.16937 | -0.096131 | 0.086975 | -0.10071 | -0.096131 | 0.17853 | -0.32043 | -0.21973 | -0.13733 | 121.5134 | 121.5408 | 61.2991 | -121.5729 | 121.5408 | 121.4996 | 61.2762 | -121.7377
225.2188 | 121.9345 | -61.2854 | 60.2737 | 0.16296 | 0.013443 | 0.071863 | 0.062147 | 0.12994 | -0.0019632 | -0.0039606 | 0.159 | -0.0037106 | 0.059526 | 0.069964 | 0.0031681 | -0.0081027 | 60.1868 | 60.3653 | -0.086975 | -61.4227 | 60.1501 | -61.3129 | -61.29 | -61.0657 | -0.013733 | -61.5417 | 60.1639 | 60.1227 | -61.2534 | -61.3632 | -0.027466 | -0.004578 | -0.1236 | 121.6507 | -0.13733 | -0.13275 | -0.086975 | 0.032043 | -0.07782 | -0.10986 | 0.21973 | -0.25635 | -0.17853 | -0.15106 | 121.4355 | 121.4722 | 61.1984 | -121.5637 | 121.4493 | 121.4081 | 61.2717 | -121.637
226.9062 | 121.9299 | -61.2625 | 60.2783 | 0.14771 | 0.016007 | 0.07229 | 0.063856 | 0.12845 | 0.00060022 | -0.0039606 | 0.17426 | -0.006915 | 0.060167 | 0.06975 | 0.0033817 | -0.0066073 | 60.1776 | 60.379 | -0.091553 | -61.4182 | 60.1501 | -61.3174 | -61.29 | -61.0565 | -0.032043 | -61.5463 | 60.141 | 60.1273 | -61.2076 | -61.3953 | -0.054932 | -0.027466 | -0.12817 | 121.6415 | -0.15564 | -0.12817 | -0.10071 | 0.054931 | -0.13275 | -0.13733 | 0.20599 | -0.28381 | -0.15106 | -0.15106 | 121.4127 | 121.4401 | 61.171 | -121.5683 | 121.4035 | 121.3898 | 61.2305 | -121.6736
228.6406 | 121.7926 | -61.2991 | 60.3424 | -0.081177 | 0.016434 | 0.072504 | 0.064711 | 0.12802 | -0.00068138 | -0.0033196 | -0.031738 | -0.0032834 | 0.062517 | 0.069323 | 0.0040225 | -0.0081027 | 60.2463 | 60.4385 | 0.050354 | -61.3907 | 60.1868 | -61.2991 | -61.2579 | -61.0794 | 0.045776 | -61.5692 | 60.2142 | 60.1776 | -61.2305 | -61.409 | 0 | 0.041198 | -0.15564 | 121.7377 | -0.091553 | -0.13275 | -0.09613 | 0.068664 | -0.10986 | -0.12817 | 0.21973 | -0.27008 | -0.16022 | -0.16479 | 121.4859 | 121.5454 | 61.3495 | -121.6003 | 121.5134 | 121.4767 | 61.3449 | -121.7514
230.3125 | 121.8521 | -61.2579 | 60.3287 | -0.11932 | 0.019852 | 0.072717 | 0.067915 | 0.13144 | 0.00017302 | -0.0022516 | -0.085144 | -0.0073422 | 0.06273 | 0.071886 | 0.0014591 | -0.0081027 | 60.2188 | 60.4385 | 0.07782 | -61.3678 | 60.228 | -61.2808 | -61.235 | -61.0794 | 0.10986 | -61.5372 | 60.2188 | 60.2188 | -61.203 | -61.3632 | -0.022888 | 0.022889 | -0.10071 | 121.6965 | -0.10986 | -0.13275 | -0.10986 | 0.054932 | -0.10528 | -0.10986 | 0.17853 | -0.27923 | -0.17395 | -0.10986 | 121.4859 | 121.4767 | 61.3358 | -121.5637 | 121.4767 | 121.4767 | 61.3678 | -121.6919
232.0625 | 121.8887 | -61.203 | 60.4111 | -0.1651 | 0.015152 | 0.071436 | 0.069197 | 0.12909 | -0.008372 | -0.0024652 | -0.046997 | -0.0090512 | 0.061662 | 0.068682 | 0.00039091 | -0.0074619 | 60.3195 | 60.585 | 0.27008 | -61.2762 | 60.26 | -61.2076 | -61.1618 | -60.9467 | 0.30212 | -61.3998 | 60.2417 | 60.2188 | -61.1206 | -61.3037 | -0.004578 | 0.041199 | -0.15106 | 121.788 | -0.073242 | -0.11444 | -0.091553 | 0.082398 | -0.10071 | -0.16937 | 0.25635 | -0.19684 | -0.09613 | -0.19226 | 121.463 | 121.5225 | 61.4731 | -121.5729 | 121.4447 | 121.4218 | 61.5051 | -121.7148
233.7969 | 121.9208 | -61.1847 | 60.3836 | -0.10406 | 0.016861 | 0.073145 | 0.067915 | 0.12781 | -0.006663 | -0.0041742 | -0.016479 | -0.0064878 | 0.061876 | 0.068255 | -0.00067729 | -0.0074619 | 60.3424 | 60.5942 | 0.21057 | -61.2854 | 60.2142 | -61.1938 | -61.1664 | -60.91 | 0.28381 | -61.3495 | 60.2325 | 60.2142 | -61.1023 | -61.29 | -0.009156 | 0.01831 | -0.16937 | 121.7789 | -0.10071 | -0.11902 | -0.041199 | 0.082397 | -0.10529 | -0.15106 | 0.27466 | -0.1648 | -0.059509 | -0.16937 | 121.3989 | 121.5271 | 61.3953 | -121.55 | 121.4172 | 121.3989 | 61.4685 | -121.6736
235.4688 | 121.8887 | -61.2259 | 60.347 | 0.079041 | 0.015793 | 0.073572 | 0.063215 | 0.12824 | -0.0040994 | -0.004815 | 0.22003 | -0.0060606 | 0.061876 | 0.0721 | -0.00024989 | -0.0074619 | 60.2646 | 60.4752 | 0.045776 | -61.3632 | 60.1639 | -61.2946 | -61.2488 | -61.0245 | 0.064087 | -61.4914 | 60.173 | 60.1501 | -61.1755 | -61.3495 | -0.068665 | -0.022888 | -0.18311 | 121.701 | -0.13733 | -0.11444 | -0.082398 | 0.050354 | -0.1236 | -0.17395 | 0.20142 | -0.2655 | -0.14191 | -0.19684 | 121.3898 | 121.4905 | 61.2717 | -121.5958 | 121.3989 | 121.376 | 61.29 | -121.6965
237.2188 | 121.8567 | -61.2534 | 60.3149 | -0.15747 | 0.019425 | 0.070581 | 0.064711 | 0.12824 | 0.0031638 | -0.0035334 | -0.1004 | -0.0047788 | 0.062944 | 0.071673 | 0.0029543 | -0.010025 | 60.2509 | 60.4248 | 0.091553 | -61.3586 | 60.2554 | -61.2991 | -61.2396 | -61.0565 | 0.10986 | -61.5509 | 60.228 | 60.2234 | -61.2076 | -61.3541 | -0.045776 | 0.013733 | -0.059509 | 121.6782 | -0.10529 | -0.11902 | -0.064087 | 0.045776 | -0.10071 | -0.086975 | 0.19684 | -0.29755 | -0.19684 | -0.091552 | 121.5088 | 121.5042 | 61.3449 | -121.5546 | 121.4813 | 121.4767 | 61.3632 | -121.669
238.8906 | 121.8842 | -61.2396 | 60.3333 | 0.15533 | 0.013657 | 0.073358 | 0.061506 | 0.12674 | -0.003245 | -0.0028924 | 0.19714 | -0.0064878 | 0.061235 | 0.069323 | 0.0027407 | -0.0091709 | 60.2234 | 60.4843 | 0.009155 | -61.3678 | 60.1273 | -61.2946 | -61.2625 | -61.0153 | 0.054932 | -61.4822 | 60.1456 | 60.1227 | -61.2076 | -61.377 | -0.054932 | -0.022888 | -0.20599 | 121.7239 | -0.12817 | -0.10529 | -0.10986 | 0.032043 | -0.13733 | -0.18768 | 0.2243 | -0.24262 | -0.10529 | -0.21057 | 121.3669 | 121.463 | 61.2488 | -121.5958 | 121.3852 | 121.3623 | 61.2946 | -121.7102
240.6406 | 121.8658 | -61.1984 | 60.4019 | -0.18036 | 0.012375 | 0.07464 | 0.065565 | 0.12909 | -0.006022 | -0.0052424 | -0.039368 | -0.0079832 | 0.061876 | 0.067827 | 0.0025271 | -0.0059665 | 60.3378 | 60.5988 | 0.25635 | -61.2717 | 60.2646 | -61.1984 | -61.1572 | -60.9421 | 0.28381 | -61.4044 | 60.2188 | 60.2005 | -61.1481 | -61.2946 | 0 | 0.041198 | -0.13733 | 121.7972 | -0.073242 | -0.11444 | -0.064087 | 0.050354 | -0.096131 | -0.18311 | 0.25635 | -0.20599 | -0.10986 | -0.20142 | 121.463 | 121.5363 | 61.4548 | -121.5591 | 121.4172 | 121.3989 | 61.4822 | -121.6965
242.375 | 121.9254 | -61.1755 | 60.3699 | -0.11169 | 0.013657 | 0.073999 | 0.068129 | 0.12802 | -0.0062356 | -0.006524 | -0.054626 | -0.0067014 | 0.061449 | 0.070177 | -0.00089089 | -0.0057529 | 60.3378 | 60.5804 | 0.20142 | -61.2717 | 60.2325 | -61.1847 | -61.1572 | -60.9146 | 0.28381 | -61.377 | 60.2509 | 60.2371 | -61.1069 | -61.2762 | -0.009155 | 0.01831 | -0.13733 | 121.756 | -0.09613 | -0.11444 | -0.032043 | 0.068664 | -0.10071 | -0.11902 | 0.26093 | -0.20142 | -0.10071 | -0.13275 | 121.4081 | 121.5134 | 61.377 | -121.5271 | 121.4264 | 121.4127 | 61.4594 | -121.6461
244.1094 | 121.9208 | -61.1801 | 60.379 | -0.13458 | 0.011948 | 0.072717 | 0.065779 | 0.12909 | -0.0055948 | -0.0060968 | -0.085144 | -0.008624 | 0.062089 | 0.072527 | -0.00089089 | -0.0091709 | 60.3745 | 60.5942 | 0.24261 | -61.2579 | 60.228 | -61.1938 | -61.1664 | -60.9192 | 0.29297 | -61.3632 | 60.2692 | 60.2234 | -61.0931 | -61.2762 | -0.013733 | 0.013733 | -0.15106 | 121.7743 | -0.07782 | -0.091553 | -0.004577 | 0.086975 | -0.09613 | -0.10986 | 0.26093 | -0.1831 | -0.086975 | -0.15564 | 121.4081 | 121.5546 | 61.4227 | -121.5454 | 121.4493 | 121.4035 | 61.4731 | -121.6553
245.7969 | 121.9391 | -61.2488 | 60.2875 | 0.11719 | 0.014725 | 0.070795 | 0.064497 | 0.12759 | -0.0013224 | -0.0024652 | 0.18188 | -0.0056332 | 0.062303 | 0.071245 | 0.0033817 | -0.0098117 | 60.2737 | 60.4385 | -0.018311 | -61.3586 | 60.1685 | -61.3083 | -61.2717 | -61.0107 | 0.032043 | -61.5189 | 60.1593 | 60.141 | -61.2305 | -61.3678 | -0.05951 | -0.022888 | -0.11902 | 121.6873 | -0.10986 | -0.086976 | -0.013733 | 0.01831 | -0.11902 | -0.12817 | 0.23804 | -0.27008 | -0.15106 | -0.14648 | 121.4172 | 121.5225 | 61.2305 | -121.5591 | 121.4081 | 121.3898 | 61.2808 | -121.6553
247.5469 | 121.8063 | -61.203 | 60.4294 | -0.21851 | 0.014939 | 0.073358 | 0.065992 | 0.12952 | -0.0034586 | -0.003747 | -0.14618 | -0.0077696 | 0.062517 | 0.070605 | 0.00039091 | -0.010453 | 60.3378 | 60.5576 | 0.21973 | -61.2808 | 60.2509 | -61.2259 | -61.171 | -60.9924 | 0.2243 | -61.4685 | 60.2966 | 60.2737 | -61.1298 | -61.3174 | -0.022888 | 0.032044 | -0.17853 | 121.7606 | -0.07782 | -0.10986 | -0.091552 | 0.073242 | -0.11444 | -0.13275 | 0.21057 | -0.2655 | -0.15106 | -0.15564 | 121.4539 | 121.5408 | 61.4227 | -121.6003 | 121.4996 | 121.4767 | 61.4273 | -121.7468
249.2812 | 121.8292 | -61.2396 | 60.3882 | -0.22614 | 0.017075 | 0.073785 | 0.065779 | 0.12952 | -0.001536 | -0.0041742 | -0.19958 | -0.0045652 | 0.062944 | 0.072314 | 0.0029543 | -0.0085299 | 60.2509 | 60.4431 | 0.11902 | -61.3586 | 60.2829 | -61.2396 | -61.235 | -61.0382 | 0.16937 | -61.5372 | 60.3333 | 60.26 | -61.1755 | -61.322 | 0 | 0.004578 | -0.10529 | 121.6827 | -0.11902 | -0.1236 | -0.13733 | 0.064087 | -0.082397 | -0.054932 | 0.20142 | -0.29755 | -0.21515 | -0.12817 | 121.5225 | 121.4905 | 61.3586 | -121.6232 | 121.5729 | 121.4996 | 61.409 | -121.7102
250.9688 | 121.843 | -61.2671 | 60.3561 | -0.24139 | 0.01622 | 0.072717 | 0.067488 | 0.12759 | -0.001536 | -0.0035334 | -0.16907 | -0.005847 | 0.063371 | 0.070391 | 0.0029543 | -0.0070345 | 60.2463 | 60.4614 | 0.1236 | -61.3541 | 60.3241 | -61.2213 | -61.2213 | -61.0382 | 0.16479 | -61.5417 | 60.3012 | 60.2509 | -61.1847 | -61.3449 | 0.045777 | 0.045777 | -0.032043 | 121.7285 | -0.086975 | -0.13275 | -0.10986 | 0.082398 | -0.07782 | -0.054932 | 0.22888 | -0.27466 | -0.19684 | -0.10529 | 121.5912 | 121.5134 | 61.3907 | -121.5775 | 121.5683 | 121.5179 | 61.4319 | -121.7011
252.7031 | 121.8979 | -61.235 | 60.3516 | 0.025635 | 0.012162 | 0.072931 | 0.065779 | 0.12738 | -0.0070902 | -0.0063104 | 0.12085 | -0.005847 | 0.061662 | 0.068896 | 0.00017731 | -0.0074619 | 60.2371 | 60.466 | 0.050354 | -61.3541 | 60.1868 | -61.2717 | -61.2076 | -61.0153 | 0.10529 | -61.4914 | 60.2234 | 60.1959 | -61.1389 | -61.3632 | -0.036621 | 0.027465 | -0.16479 | 121.701 | -0.11902 | -0.14648 | -0.11444 | 0.09613 | -0.12817 | -0.12817 | 0.21973 | -0.25635 | -0.12817 | -0.15564 | 121.4218 | 121.4722 | 61.2854 | -121.5591 | 121.4584 | 121.431 | 61.3403 | -121.7148
254.375 | 121.9574 | -61.1526 | 60.379 | -0.096436 | 0.013657 | 0.073785 | 0.065992 | 0.12909 | -0.0051676 | -0.0052424 | -0.0088499 | -0.0054196 | 0.060594 | 0.070605 | 0.00060451 | -0.010025 | 60.3378 | 60.585 | 0.20142 | -61.2717 | 60.26 | -61.2213 | -61.171 | -60.9192 | 0.27008 | -61.3724 | 60.2463 | 60.2325 | -61.1069 | -61.2946 | -0.068664 | -0.01831 | -0.11902 | 121.7377 | -0.11902 | -0.10071 | -0.041198 | 0.045776 | -0.14191 | -0.13275 | 0.23346 | -0.21973 | -0.077819 | -0.14648 | 121.4127 | 121.4905 | 61.3541 | -121.55 | 121.3989 | 121.3852 | 61.4227 | -121.6736
256.125 | 121.907 | -61.2625 | 60.2692 | 0.079041 | 0.011521 | 0.070795 | 0.065565 | 0.12994 | 0.0025228 | -0.0035334 | 0.159 | -0.003497 | 0.060381 | 0.072527 | 0.0044497 | -0.011948 | 60.1868 | 60.3241 | -0.12817 | -61.441 | 60.2097 | -61.3358 | -61.3083 | -61.0977 | -0.07782 | -61.6013 | 60.1959 | 60.1547 | -61.2305 | -61.3998 | -0.073242 | -0.045777 | -0.059509 | 121.5866 | -0.17853 | -0.13275 | -0.082397 | 0.032043 | -0.13733 | -0.073242 | 0.16479 | -0.33874 | -0.20142 | -0.11444 | 121.4722 | 121.4493 | 61.1343 | -121.5775 | 121.4584 | 121.4172 | 61.1847 | -121.669
257.7969 | 121.8292 | -61.2396 | 60.3882 | -0.21851 | 0.016648 | 0.073145 | 0.069838 | 0.12973 | 0.00017302 | -0.0035334 | -0.18433 | -0.005847 | 0.06273 | 0.070177 | 0.0020999 | -0.0083163 | 60.26 | 60.4477 | 0.12817 | -61.3586 | 60.2921 | -61.2305 | -61.2259 | -61.0565 | 0.16022 | -61.5051 | 60.2737 | 60.2737 | -61.1755 | -61.3266 | 0.009155 | 0.013733 | -0.096131 | 121.6873 | -0.11902 | -0.13275 | -0.12817 | 0.064087 | -0.086975 | -0.11444 | 0.1831 | -0.2655 | -0.17853 | -0.11444 | 121.5317 | 121.4996 | 61.3678 | -121.6141 | 121.5134 | 121.5134 | 61.3998 | -121.7148
259.5312 | 121.962 | -61.171 | 60.3882 | -0.0354 | 0.012589 | 0.071863 | 0.06706 | 0.12866 | -0.0055948 | -0.0058832 | 0.044556 | -0.006915 | 0.061662 | 0.070818 | -3.629e-05 | -0.0074619 | 60.2829 | 60.5072 | 0.11902 | -61.3129 | 60.2234 | -61.2122 | -61.1938 | -60.9467 | 0.21973 | -61.4136 | 60.2325 | 60.2417 | -61.1298 | -61.3174 | -0.041199 | -0.022889 | -0.1648 | 121.6782 | -0.14191 | -0.11902 | -0.10529 | 0.041198 | -0.14648 | -0.15564 | 0.2243 | -0.24261 | -0.09613 | -0.14649 | 121.3943 | 121.4539 | 61.29 | -121.582 | 121.4035 | 121.4127 | 61.3907 | -121.7056
261.2812 | 121.907 | -61.2717 | 60.2692 | 0.10956 | 0.013871 | 0.073145 | 0.061934 | 0.12695 | 0.00017302 | -0.0026788 | 0.097962 | -0.0060606 | 0.062517 | 0.071245 | 0.0057315 | -0.0093845 | 60.1822 | 60.3241 | -0.14191 | -61.4456 | 60.2005 | -61.3266 | -61.3037 | -61.1069 | -0.086975 | -61.615 | 60.2188 | 60.1685 | -61.2259 | -61.3998 | -0.054932 | -0.032044 | -0.068665 | 121.5958 | -0.17395 | -0.14191 | -0.086975 | 0.045776 | -0.12817 | -0.050354 | 0.16479 | -0.34332 | -0.21515 | -0.10071 | 121.4722 | 121.4539 | 61.1298 | -121.5729 | 121.4905 | 121.4401 | 61.1847 | -121.669
262.9688 | 121.9437 | -61.1572 | 60.3836 | -0.073547 | 0.013443 | 0.073785 | 0.068983 | 0.12695 | -0.0058084 | -0.0063104 | -0.0012209 | -0.0077696 | 0.061662 | 0.06975 | -0.0017453 | -0.0068209 | 60.3378 | 60.5621 | 0.1831 | -61.2808 | 60.2646 | -61.2122 | -61.1526 | -60.9192 | 0.26093 | -61.377 | 60.2554 | 60.2325 | -61.116 | -61.2808 | -0.054931 | 0.004578 | -0.11902 | 121.7194 | -0.1236 | -0.12817 | -0.045776 | 0.041199 | -0.1236 | -0.12817 | 0.23804 | -0.21973 | -0.09613 | -0.15106 | 121.4218 | 121.4951 | 61.3403 | -121.5363 | 121.4127 | 121.3898 | 61.4182 | -121.6644
264.7188 | 121.9299 | -61.171 | 60.3836 | -0.0048827 | 0.012802 | 0.072717 | 0.067274 | 0.13294 | -0.0038858 | -0.0069512 | 0.090332 | -0.0084104 | 0.060594 | 0.069109 | 0.00039091 | -0.0078891 | 60.2509 | 60.4614 | 0.054932 | -61.3403 | 60.2142 | -61.235 | -61.203 | -61.0062 | 0.11444 | -61.4731 | 60.2325 | 60.2005 | -61.1435 | -61.3541 | -0.064087 | -0.032044 | -0.16937 | 121.6324 | -0.16937 | -0.13733 | -0.13275 | 0.027465 | -0.18311 | -0.15106 | 0.16479 | -0.30212 | -0.11902 | -0.18311 | 121.3852 | 121.4218 | 61.2259 | -121.5866 | 121.4035 | 121.3715 | 61.2854 | -121.7377
266.4062 | 121.8979 | -61.2259 | 60.347 | 0.094299 | 0.012162 | 0.072504 | 0.066633 | 0.1293 | -0.0040994 | -0.0058832 | 0.18188 | -0.0060606 | 0.05974 | 0.071459 | 0.0025271 | -0.0081027 | 60.2646 | 60.4752 | 0.013733 | -61.377 | 60.173 | -61.2579 | -61.2488 | -61.0016 | 0.091553 | -61.4777 | 60.2097 | 60.1776 | -61.171 | -61.3495 | -0.032044 | -0.022888 | -0.17395 | 121.701 | -0.15106 | -0.12817 | -0.082398 | 0.054932 | -0.1236 | -0.13733 | 0.2243 | -0.25177 | -0.12817 | -0.16937 | 121.3989 | 121.4905 | 61.2396 | -121.5958 | 121.4355 | 121.4035 | 61.3174 | -121.6965
268.1562 | 121.843 | -61.2259 | 60.3973 | -0.21851 | 0.014939 | 0.073145 | 0.069197 | 0.12909 | -4.058e-05 | -0.0035334 | -0.21484 | -0.0056332 | 0.060167 | 0.071673 | 0.0016727 | -0.0081027 | 60.2509 | 60.4431 | 0.12817 | -61.3586 | 60.2875 | -61.2305 | -61.1893 | -61.0565 | 0.16479 | -61.5143 | 60.3195 | 60.26 | -61.1801 | -61.3358 | -0.004578 | 0.036621 | -0.10986 | 121.669 | -0.13275 | -0.16937 | -0.14649 | 0.045776 | -0.10986 | -0.07782 | 0.16937 | -0.28839 | -0.17853 | -0.13733 | 121.5134 | 121.4767 | 61.3541 | -121.5866 | 121.5454 | 121.4859 | 61.3907 | -121.7331
269.9062 | 121.8246 | -61.2122 | 60.3836 | -0.21851 | 0.013016 | 0.072717 | 0.068556 | 0.13016 | -0.0021768 | -0.0043878 | -0.20721 | -0.007556 | 0.060808 | 0.072527 | 0.0040225 | -0.0063937 | 60.2463 | 60.4568 | 0.13733 | -61.3678 | 60.2966 | -61.235 | -61.2122 | -61.0336 | 0.17853 | -61.5189 | 60.3378 | 60.26 | -61.171 | -61.3312 | -0.022888 | 0 | -0.086975 | 121.669 | -0.15564 | -0.15564 | -0.13733 | 0.041199 | -0.11902 | -0.045776 | 0.17853 | -0.3067 | -0.18768 | -0.1236 | 121.5088 | 121.4584 | 61.3495 | -121.5958 | 121.55 | 121.4722 | 61.3907 | -121.7148
271.5938 | 121.9254 | -61.2717 | 60.2921 | 0.14771 | 0.012162 | 0.071222 | 0.064283 | 0.12888 | -0.0013224 | -0.0011834 | 0.18188 | -0.0071286 | 0.058885 | 0.073382 | 0.0029543 | -0.0076755 | 60.2509 | 60.4706 | -0.022888 | -61.3678 | 60.1593 | -61.2854 | -61.2762 | -61.0291 | 0.036621 | -61.528 | 60.1685 | 60.1044 | -61.2076 | -61.3861 | -0.013733 | -0.004578 | -0.13275 | 121.7422 | -0.096131 | -0.091553 | -0.041199 | 0.064086 | -0.11444 | -0.1236 | 0.24261 | -0.25635 | -0.14191 | -0.18768 | 121.431 | 121.5225 | 61.2488 | -121.5683 | 121.4401 | 121.376 | 61.3083 | -121.6782
273.3281 | 121.8475 | -61.2625 | 60.3149 | -0.18036 | 0.017502 | 0.070795 | 0.064497 | 0.12866 | 0.0012412 | -0.002038 | -0.11566 | -0.005847 | 0.063371 | 0.071032 | 0.0025271 | -0.0059665 | 60.2325 | 60.4385 | 0.082397 | -61.3632 | 60.2554 | -61.2808 | -61.235 | -61.0565 | 0.13733 | -61.5326 | 60.2463 | 60.1913 | -61.2213 | -61.3907 | -0.018311 | 0.027466 | -0.059509 | 121.7011 | -0.10071 | -0.12817 | -0.082397 | 0.041199 | -0.12817 | -0.068664 | 0.20599 | -0.27008 | -0.14191 | -0.1236 | 121.5179 | 121.4951 | 61.3449 | -121.55 | 121.5088 | 121.4539 | 61.3998 | -121.7056
275.0781 | 121.8796 | -61.2305 | 60.3241 | 0.12482 | 0.014084 | 0.073572 | 0.063856 | 0.12631 | -0.004313 | -0.0022516 | 0.17426 | -0.005847 | 0.061449 | 0.069536 | 0.0018863 | -0.0063937 | 60.2463 | 60.4889 | 0.013733 | -61.3541 | 60.1364 | -61.2762 | -61.2534 | -61.0062 | 0.068665 | -61.4731 | 60.1776 | 60.1639 | -61.1847 | -61.3953 | -0.045776 | -0.022888 | -0.18768 | 121.7194 | -0.1236 | -0.10071 | -0.07782 | 0.045777 | -0.16479 | -0.14648 | 0.2243 | -0.24261 | -0.077819 | -0.16022 | 121.3669 | 121.4767 | 61.2442 | -121.5775 | 121.4081 | 121.3943 | 61.2991 | -121.7194
276.8125 | 121.8384 | -61.2534 | 60.347 | -0.19562 | 0.016648 | 0.072717 | 0.070265 | 0.12824 | 0.00038662 | -0.0046014 | -0.13855 | -0.0047788 | 0.061876 | 0.070818 | 0.0012455 | -0.0098117 | 60.2417 | 60.4294 | 0.086975 | -61.3495 | 60.2509 | -61.2671 | -61.2396 | -61.0703 | 0.14648 | -61.528 | 60.2966 | 60.2325 | -61.171 | -61.3403 | -0.013733 | 0.013733 | -0.096131 | 121.6827 | -0.09613 | -0.10986 | -0.10529 | 0.082398 | -0.086975 | -0.050354 | 0.18311 | -0.27466 | -0.18768 | -0.11444 | 121.5042 | 121.4951 | 61.3403 | -121.5866 | 121.55 | 121.4859 | 61.3998 | -121.6873
278.5625 | 121.8155 | -61.2213 | 60.4111 | -0.23376 | 0.014511 | 0.070795 | 0.069197 | 0.12845 | -0.0040994 | -0.0035334 | -0.18433 | -0.0056332 | 0.062944 | 0.071886 | -3.629e-05 | -0.0098117 | 60.2371 | 60.4431 | 0.13275 | -61.3586 | 60.2875 | -61.2442 | -61.2167 | -61.0428 | 0.17395 | -61.5189 | 60.3149 | 60.26 | -61.1801 | -61.322 | -0.022889 | 0.004577 | -0.1236 | 121.6644 | -0.13733 | -0.14191 | -0.17395 | 0.041198 | -0.10071 | -0.096131 | 0.17853 | -0.29755 | -0.19684 | -0.15106 | 121.5088 | 121.4584 | 61.3541 | -121.6278 | 121.5363 | 121.4813 | 61.3953 | -121.7331
280.2969 | 121.8338 | -61.2396 | 60.379 | -0.23376 | 0.018143 | 0.07229 | 0.069197 | 0.12909 | -0.0036722 | -0.0039606 | -0.16907 | -0.0062742 | 0.064439 | 0.072954 | -0.00067729 | -0.0091709 | 60.2371 | 60.4568 | 0.1236 | -61.3495 | 60.2875 | -61.2305 | -61.1938 | -61.0611 | 0.15106 | -61.5417 | 60.3104 | 60.26 | -61.1481 | -61.322 | 0.009155 | 0.045776 | -0.091552 | 121.6965 | -0.10986 | -0.15564 | -0.14191 | 0.091553 | -0.082397 | -0.068664 | 0.17853 | -0.30212 | -0.21973 | -0.11902 | 121.5271 | 121.4767 | 61.3632 | -121.5729 | 121.55 | 121.4996 | 61.3907 | -121.701
282.0469 | 121.8384 | -61.2579 | 60.3241 | -0.13458 | 0.016861 | 0.071863 | 0.066633 | 0.13037 | 0.00017302 | -0.001397 | -0.12329 | -0.0047788 | 0.064012 | 0.074023 | 0.0035953 | -0.010025 | 60.2417 | 60.434 | 0.086975 | -61.3678 | 60.2188 | -61.2854 | -61.2579 | -61.0519 | 0.13733 | -61.5372 | 60.2188 | 60.1959 | -61.2167 | -61.377 | -0.027465 | 0 | -0.10529 | 121.6919 | -0.10986 | -0.10986 | -0.082398 | 0.041199 | -0.11902 | -0.10529 | 0.20599 | -0.27923 | -0.16022 | -0.12817 | 121.4767 | 121.4996 | 61.3449 | -121.582 | 121.4767 | 121.4539 | 61.3953 | -121.7011
283.7344 | 121.9208 | -61.2625 | 60.3058 | 0.14008 | 0.012375 | 0.071222 | 0.061506 | 0.13229 | -0.0034586 | -0.004815 | 0.23529 | -0.0079832 | 0.061876 | 0.071032 | 0.0035953 | -0.0085299 | 60.228 | 60.4614 | -0.027466 | -61.3632 | 60.1227 | -61.2946 | -61.2488 | -61.0199 | 0.045776 | -61.4868 | 60.1501 | 60.1227 | -61.235 | -61.3907 | -0.032044 | 0.013733 | -0.1831 | 121.7239 | -0.10071 | -0.11444 | -0.07782 | 0.027466 | -0.12817 | -0.15564 | 0.24262 | -0.2243 | -0.09613 | -0.1831 | 121.3852 | 121.4905 | 61.235 | -121.5546 | 121.4127 | 121.3852 | 61.3083 | -121.6965
285.4844 | 121.875 | -61.2488 | 60.3378 | 0.10956 | 0.013016 | 0.070154 | 0.06642 | 0.12866 | -0.0051676 | -0.0028924 | 0.22003 | -0.0064878 | 0.061662 | 0.0721 | 0.0014591 | -0.0074619 | 60.2371 | 60.4752 | 0.022888 | -61.3541 | 60.1547 | -61.2717 | -61.2534 | -61.0062 | 0.064087 | -61.4914 | 60.1685 | 60.1364 | -61.1938 | -61.3724 | -0.022888 | -0.004578 | -0.18311 | 121.7239 | -0.10529 | -0.10071 | -0.10071 | 0.054931 | -0.1236 | -0.16937 | 0.24261 | -0.24262 | -0.11902 | -0.20142 | 121.4035 | 121.4859 | 61.2717 | -121.5912 | 121.4172 | 121.3852 | 61.3129 | -121.7102
287.1719 | 121.9437 | -61.2579 | 60.2646 | 0.14008 | 0.012802 | 0.070795 | 0.063429 | 0.1293 | -0.00046778 | -0.003747 | 0.159 | -0.0064878 | 0.058244 | 0.069964 | 0.0046633 | -0.0091709 | 60.2188 | 60.4477 | -0.027466 | -61.3815 | 60.1776 | -61.3037 | -61.2579 | -61.0382 | 0.027466 | -61.528 | 60.1822 | 60.1273 | -61.2213 | -61.3861 | -0.045776 | 0 | -0.086975 | 121.7056 | -0.1236 | -0.1236 | -0.045776 | 0.036622 | -0.12817 | -0.082397 | 0.21973 | -0.27008 | -0.14191 | -0.13733 | 121.4355 | 121.4767 | 61.2305 | -121.5225 | 121.4401 | 121.3852 | 61.2854 | -121.6507
288.9219 | 121.9482 | -61.1938 | 60.3836 | -0.012512 | 0.012589 | 0.071863 | 0.068556 | 0.12546 | -0.0070902 | -0.0041742 | 0.11322 | -0.005847 | 0.062517 | 0.070391 | -0.0019589 | -0.0085299 | 60.2371 | 60.4431 | 0.068665 | -61.3541 | 60.2188 | -61.2442 | -61.1984 | -61.0199 | 0.11444 | -61.4639 | 60.2417 | 60.2325 | -61.1481 | -61.3403 | -0.050354 | -0.004577 | -0.16479 | 121.637 | -0.16022 | -0.15564 | -0.14648 | 0.045777 | -0.14648 | -0.14191 | 0.17395 | -0.27008 | -0.1236 | -0.15106 | 121.4127 | 121.431 | 61.2625 | -121.582 | 121.4355 | 121.4264 | 61.3083 | -121.7239
290.6719 | 121.8155 | -61.2305 | 60.4202 | -0.19562 | 0.012162 | 0.071436 | 0.067488 | 0.12909 | -0.0019632 | -0.005456 | -0.14618 | -0.0064878 | 0.060594 | 0.070818 | -0.0011045 | -0.0081027 | 60.3333 | 60.5438 | 0.22888 | -61.29 | 60.26 | -61.2167 | -61.1801 | -60.997 | 0.23804 | -61.4685 | 60.2783 | 60.26 | -61.1298 | -61.3083 | 0.013733 | 0.050354 | -0.16022 | 121.7743 | -0.059509 | -0.10986 | -0.086975 | 0.10071 | -0.07782 | -0.14191 | 0.23346 | -0.23804 | -0.16022 | -0.16022 | 121.4905 | 121.5637 | 61.4594 | -121.6003 | 121.5088 | 121.4905 | 61.4685 | -121.7285
292.3594 | 121.9162 | -61.171 | 60.4019 | -0.15747 | 0.015152 | 0.070795 | 0.068342 | 0.13016 | -0.004313 | -0.0041742 | -0.069885 | -0.005847 | 0.06273 | 0.070177 | 0.0018863 | -0.0081027 | 60.3699 | 60.5942 | 0.24261 | -61.2534 | 60.2509 | -61.203 | -61.1572 | -60.9192 | 0.31128 | -61.3678 | 60.2646 | 60.2188 | -61.1252 | -61.2991 | -0.032044 | 0.013732 | -0.15106 | 121.7651 | -0.082398 | -0.09613 | -0.032044 | 0.045776 | -0.12817 | -0.13733 | 0.25177 | -0.19684 | -0.068665 | -0.18311 | 121.4218 | 121.5408 | 61.4136 | -121.5591 | 121.4355 | 121.3898 | 61.4822 | -121.701
294.1094 | 121.8704 | -61.2717 | 60.3516 | -0.20325 | 0.015793 | 0.071436 | 0.064283 | 0.13187 | -0.0011088 | -0.0050286 | -0.1767 | -0.0056332 | 0.060167 | 0.072954 | 0.0055179 | -0.0098117 | 60.2371 | 60.4248 | 0.086975 | -61.3678 | 60.2783 | -61.2762 | -61.2305 | -61.0748 | 0.14191 | -61.5372 | 60.3012 | 60.2554 | -61.1572 | -61.3541 | -0.004578 | 0.041198 | -0.073242 | 121.6965 | -0.096131 | -0.13733 | -0.11444 | 0.11444 | -0.082398 | -0.050354 | 0.19684 | -0.2655 | -0.18311 | -0.09613 | 121.55 | 121.5088 | 61.3586 | -121.582 | 121.5729 | 121.5271 | 61.4136 | -121.7056
295.7969 | 121.9574 | -61.1755 | 60.3653 | -0.0354 | 0.014939 | 0.071863 | 0.062361 | 0.12845 | -0.006022 | -0.0046014 | 0.044556 | -0.0081968 | 0.061876 | 0.0721 | 0.0012455 | -0.0085299 | 60.2509 | 60.5026 | 0.10529 | -61.3129 | 60.2142 | -61.2305 | -61.1847 | -60.9467 | 0.19684 | -61.3998 | 60.2463 | 60.2325 | -61.1298 | -61.3358 | -0.054932 | -0.009155 | -0.15106 | 121.6782 | -0.13733 | -0.12817 | -0.11444 | 0.045776 | -0.16022 | -0.11902 | 0.22888 | -0.2243 | -0.064087 | -0.13275 | 121.3898 | 121.4264 | 61.2808 | -121.55 | 121.4218 | 121.4081 | 61.3724 | -121.701
297.5312 | 121.9025 | -61.235 | 60.3378 | 0.12482 | 0.014084 | 0.071863 | 0.06407 | 0.12824 | -0.0017496 | -0.0024652 | 0.17426 | -0.0071286 | 0.061235 | 0.071673 | 0.0029543 | -0.01088 | 60.2554 | 60.4614 | 0.032043 | -61.3724 | 60.1501 | -61.3083 | -61.2488 | -60.997 | 0.054932 | -61.4822 | 60.1822 | 60.1547 | -61.1984 | -61.3815 | -0.073243 | -0.013733 | -0.18768 | 121.6965 | -0.13733 | -0.1236 | -0.082398 | 0.036621 | -0.14649 | -0.15564 | 0.23804 | -0.24719 | -0.10071 | -0.18311 | 121.3852 | 121.4905 | 61.2671 | -121.5866 | 121.4172 | 121.3898 | 61.29 | -121.7194
299.2812 | 121.8338 | -61.2854 | 60.3973 | -0.23376 | 0.016861 | 0.069513 | 0.066633 | 0.12717 | -0.00046778 | -0.003747 | -0.20721 | -0.005847 | 0.064012 | 0.0721 | 0.0025271 | -0.010239 | 60.2737 | 60.434 | 0.12817 | -61.3495 | 60.2921 | -61.2213 | -61.2122 | -61.0519 | 0.15106 | -61.5326 | 60.3149 | 60.2692 | -61.1893 | -61.3495 | 0.064087 | 0.073242 | -0.10529 | 121.7194 | -0.064087 | -0.13733 | -0.1236 | 0.09613 | -0.064087 | -0.082398 | 0.23346 | -0.24719 | -0.18311 | -0.12817 | 121.5775 | 121.5591 | 61.4136 | -121.6095 | 121.6003 | 121.5546 | 61.4365 | -121.7468
300.9688 | 121.9299 | -61.1618 | 60.379 | 0.071411 | 0.014725 | 0.075708 | 0.065351 | 0.12866 | -0.0064492 | -0.0060968 | -0.024109 | -0.0088376 | 0.061662 | 0.071459 | -0.00046349 | -0.0068209 | 60.3378 | 60.5576 | 0.20599 | -61.2808 | 60.2417 | -61.2167 | -61.1618 | -60.9192 | 0.2655 | -61.3724 | 60.2509 | 60.2097 | -61.1343 | -61.3129 | -0.054932 | 0 | -0.13733 | 121.7194 | -0.11902 | -0.11902 | -0.041198 | 0.027466 | -0.15106 | -0.12817 | 0.24261 | -0.21057 | -0.059509 | -0.16937 | 121.4035 | 121.4996 | 61.3678 | -121.5408 | 121.4127 | 121.3715 | 61.4273 | -121.6919
302.7188 | 121.8201 | -61.2946 | 60.3287 | 0.040894 | 0.014725 | 0.070795 | 0.062574 | 0.1293 | 0.0014548 | -0.0016108 | 0.029297 | -0.0056332 | 0.061662 | 0.069964 | 0.0053043 | -0.0098117 | 60.1501 | 60.3241 | -0.11444 | -61.4456 | 60.2188 | -61.3403 | -61.2991 | -61.1618 | -0.10986 | -61.6653 | 60.2097 | 60.1685 | -61.2442 | -61.4502 | -0.045776 | -0.004577 | -0.10986 | 121.6187 | -0.15106 | -0.14649 | -0.17853 | 0.050354 | -0.15564 | -0.11902 | 0.13275 | -0.37079 | -0.21515 | -0.16022 | 121.5134 | 121.4447 | 61.1801 | -121.6278 | 121.5042 | 121.463 | 61.1847 | -121.7789
304.4531 | 121.9162 | -61.235 | 60.3333 | 0.14771 | 0.014084 | 0.071649 | 0.064283 | 0.1293 | -0.0017496 | -0.0033196 | 0.22003 | -0.0079832 | 0.061876 | 0.071245 | 0.0018863 | -0.0078891 | 60.2325 | 60.466 | 0 | -61.3724 | 60.1273 | -61.2854 | -61.2488 | -61.0062 | 0.054932 | -61.496 | 60.1593 | 60.1181 | -61.2076 | -61.3815 | -0.050354 | -0.013733 | -0.20599 | 121.701 | -0.13733 | -0.1236 | -0.10071 | 0.027465 | -0.14649 | -0.17395 | 0.22888 | -0.26093 | -0.11444 | -0.21515 | 121.3623 | 121.4676 | 61.235 | -121.582 | 121.3943 | 121.3531 | 61.29 | -121.7148
306.2031 | 121.9208 | -61.2808 | 60.3149 | 0.08667 | 0.015366 | 0.072931 | 0.065351 | 0.12888 | -0.00068138 | -0.0026788 | 0.12085 | -0.004138 | 0.061021 | 0.071673 | 0.0055179 | -0.0078891 | 60.1776 | 60.347 | -0.13275 | -61.4639 | 60.2005 | -61.3358 | -61.3083 | -61.1069 | -0.091553 | -61.6287 | 60.2005 | 60.1547 | -61.2534 | -61.4319 | -0.054931 | -0.027466 | -0.11444 | 121.6278 | -0.18311 | -0.15564 | -0.13733 | 0.027466 | -0.15106 | -0.11444 | 0.17395 | -0.3479 | -0.19684 | -0.16022 | 121.4813 | 121.4584 | 61.1481 | -121.6232 | 121.4813 | 121.4355 | 61.1893 | -121.7468
307.9375 | 121.8613 | -61.2579 | 60.3378 | -0.18799 | 0.016434 | 0.07229 | 0.068342 | 0.12973 | -0.0030314 | -0.001397 | -0.15381 | -0.0043516 | 0.060594 | 0.071459 | 0.0033817 | -0.0074619 | 60.2509 | 60.4248 | 0.082397 | -61.3586 | 60.2737 | -61.2625 | -61.2259 | -61.0748 | 0.12817 | -61.5326 | 60.2463 | 60.2142 | -61.2167 | -61.3678 | -0.004577 | 0.032044 | -0.064087 | 121.6827 | -0.10071 | -0.13275 | -0.086976 | 0.041199 | -0.10986 | -0.091553 | 0.18311 | -0.27466 | -0.16479 | -0.1236 | 121.5317 | 121.5088 | 61.3403 | -121.5637 | 121.5042 | 121.4722 | 61.3861 | -121.7056
309.625 | 121.8109 | -61.3129 | 60.2875 | -0.027771 | 0.015152 | 0.070581 | 0.063002 | 0.12781 | -0.00089518 | -0.001397 | 0.075073 | -0.0049924 | 0.061876 | 0.073382 | 0.0050907 | -0.0070345 | 60.2097 | 60.379 | -0.022888 | -61.4319 | 60.1822 | -61.3174 | -61.2854 | -61.1572 | -0.022888 | -61.6333 | 60.1959 | 60.1776 | -61.2717 | -61.441 | -0.004578 | 0.027466 | -0.10529 | 121.6919 | -0.11902 | -0.14648 | -0.07782 | 0.041199 | -0.12817 | -0.091553 | 0.15564 | -0.32044 | -0.19226 | -0.10986 | 121.4951 | 121.5225 | 61.29 | -121.5729 | 121.5088 | 121.4905 | 61.29 | -121.7285
311.3594 | 121.8201 | -61.2534 | 60.379 | -0.18036 | 0.015793 | 0.069727 | 0.069838 | 0.1308 | -0.004313 | -0.0046014 | -0.16907 | -0.005847 | 0.064012 | 0.071459 | 0.00017731 | -0.0063937 | 60.2188 | 60.4385 | 0.11902 | -61.3541 | 60.26 | -61.2488 | -61.2167 | -61.0474 | 0.16937 | -61.5005 | 60.2966 | 60.2829 | -61.1664 | -61.3174 | 0.004578 | 0.036621 | -0.11902 | 121.6919 | -0.10071 | -0.13733 | -0.16022 | 0.086975 | -0.064087 | -0.082397 | 0.20599 | -0.24719 | -0.1831 | -0.09613 | 121.5134 | 121.4722 | 61.3724 | -121.5958 | 121.55 | 121.5363 | 61.4227 | -121.6965
313.1094 | 121.9437 | -61.1801 | 60.379 | 0.0027468 | 0.011734 | 0.072931 | 0.065351 | 0.12759 | -0.0073038 | -0.003106 | 0.12085 | -0.0077696 | 0.060594 | 0.068896 | -3.629e-05 | -0.0053257 | 60.2234 | 60.466 | 0.059509 | -61.3312 | 60.228 | -61.2305 | -61.2076 | -61.0245 | 0.1236 | -61.4639 | 60.228 | 60.2188 | -61.1618 | -61.3174 | -0.050354 | -0.027466 | -0.15106 | 121.6461 | -0.15106 | -0.1236 | -0.15564 | 0.018311 | -0.13733 | -0.15106 | 0.15564 | -0.28381 | -0.14648 | -0.16022 | 121.4081 | 121.4035 | 61.2396 | -121.5866 | 121.4081 | 121.3989 | 61.3037 | -121.6965
314.7812 | 121.8201 | -61.2991 | 60.3195 | 0.025635 | 0.016861 | 0.070795 | 0.062147 | 0.12802 | 0.00038662 | -0.003106 | 0.12085 | -0.0045652 | 0.062517 | 0.071459 | 0.0048769 | -0.0076755 | 60.1501 | 60.2783 | -0.13275 | -61.4731 | 60.2097 | -61.322 | -61.2946 | -61.1664 | -0.11444 | -61.6425 | 60.228 | 60.1593 | -61.2671 | -61.4319 | -0.022888 | 0.004577 | -0.10986 | 121.5775 | -0.17395 | -0.17853 | -0.16937 | 0.032043 | -0.13275 | -0.091553 | 0.13275 | -0.34332 | -0.21057 | -0.16022 | 121.5088 | 121.4493 | 61.1664 | -121.6141 | 121.5271 | 121.4584 | 61.1847 | -121.7514
316.5312 | 121.9666 | -61.1755 | 60.3882 | -0.058289 | 0.01323 | 0.072717 | 0.068129 | 0.1293 | -0.0085856 | -0.0050286 | 0.059815 | -0.0092648 | 0.062517 | 0.071673 | -0.0025999 | -0.0078891 | 60.2875 | 60.5164 | 0.14648 | -61.3266 | 60.2325 | -61.2259 | -61.1618 | -60.9421 | 0.22888 | -61.3953 | 60.26 | 60.228 | -61.1206 | -61.3129 | -0.050354 | 0.013733 | -0.15564 | 121.6919 | -0.15106 | -0.1648 | -0.10071 | 0.054932 | -0.13733 | -0.12817 | 0.23346 | -0.21973 | -0.082398 | -0.16022 | 121.4081 | 121.463 | 61.322 | -121.55 | 121.4355 | 121.4035 | 61.4044 | -121.7011
318.2969 | 121.9391 | -61.2534 | 60.2783 | 0.094299 | 0.013016 | 0.072931 | 0.063215 | 0.1293 | -0.0019632 | -0.0028924 | 0.18951 | -0.0056332 | 0.059526 | 0.071886 | 0.0053043 | -0.0098117 | 60.2509 | 60.4523 | -0.013733 | -61.3541 | 60.173 | -61.3129 | -61.2579 | -61.0428 | 0.027466 | -61.5005 | 60.1593 | 60.1227 | -61.2213 | -61.3998 | -0.059509 | -0.004578 | -0.10529 | 121.7056 | -0.10071 | -0.09613 | -0.027466 | 0.032044 | -0.14648 | -0.11902 | 0.21057 | -0.24719 | -0.10071 | -0.15564 | 121.4264 | 121.5042 | 61.2396 | -121.5363 | 121.4127 | 121.376 | 61.2808 | -121.6782
319.9844 | 121.8292 | -61.2122 | 60.4111 | -0.18036 | 0.016007 | 0.07229 | 0.069197 | 0.12845 | -0.004313 | -0.0041742 | -0.062256 | -0.0067014 | 0.064439 | 0.071245 | -3.629e-05 | -0.01088 | 60.3287 | 60.5667 | 0.26093 | -61.2717 | 60.2371 | -61.203 | -61.1664 | -60.9879 | 0.27008 | -61.4136 | 60.2737 | 60.2371 | -61.1023 | -61.3174 | 0.009155 | 0.045776 | -0.17395 | 121.7789 | -0.059509 | -0.10529 | -0.082398 | 0.10986 | -0.10529 | -0.13733 | 0.2243 | -0.20142 | -0.09613 | -0.17395 | 121.4493 | 121.5408 | 61.4731 | -121.5775 | 121.4859 | 121.4493 | 61.4822 | -121.7285
321.7344 | 121.9025 | -61.1847 | 60.4065 | -0.13458 | 0.013871 | 0.073785 | 0.065992 | 0.12717 | -0.0045266 | -0.0058832 | -0.077515 | -0.0067014 | 0.062517 | 0.070605 | 0.0010317 | -0.0076755 | 60.379 | 60.6125 | 0.23804 | -61.2625 | 60.2783 | -61.2076 | -61.1435 | -60.9238 | 0.31128 | -61.377 | 60.2692 | 60.2371 | -61.0977 | -61.3037 | -0.022889 | 0.041198 | -0.12817 | 121.7972 | -0.07782 | -0.11902 | -0.027466 | 0.086975 | -0.11902 | -0.13733 | 0.26093 | -0.19226 | -0.073242 | -0.16937 | 121.463 | 121.5637 | 61.4227 | -121.55 | 121.4539 | 121.4218 | 61.496 | -121.7102
323.5 | 121.9162 | -61.1847 | 60.3699 | -0.012512 | 0.012162 | 0.072931 | 0.065351 | 0.12717 | -0.0058084 | -0.0056696 | 0.11322 | -0.0081968 | 0.05974 | 0.070605 | 0.00039091 | -0.0074619 | 60.2509 | 60.4568 | 0.054932 | -61.3266 | 60.228 | -61.2488 | -61.2122 | -61.0199 | 0.086975 | -61.4914 | 60.2234 | 60.2005 | -61.1435 | -61.3449 | -0.064087 | -0.027466 | -0.14191 | 121.6415 | -0.14191 | -0.11444 | -0.11902 | 0.041198 | -0.16022 | -0.14648 | 0.16479 | -0.3067 | -0.14648 | -0.16937 | 121.4127 | 121.4355 | 61.2396 | -121.582 | 121.4081 | 121.3852 | 61.2717 | -121.7148
325.25 | 121.907 | -61.2762 | 60.2783 | 0.10193 | 0.014298 | 0.072504 | 0.063429 | 0.12888 | 0.0023092 | -0.001397 | 0.075073 | -0.0060606 | 0.060167 | 0.070177 | 0.0050907 | -0.0089573 | 60.1547 | 60.3241 | -0.13733 | -61.4639 | 60.2005 | -61.3266 | -61.3037 | -61.1069 | -0.09613 | -61.615 | 60.2325 | 60.1547 | -61.2488 | -61.4227 | -0.050354 | -0.027466 | -0.07782 | 121.6003 | -0.18768 | -0.16022 | -0.1236 | 0.027466 | -0.14648 | -0.045776 | 0.16937 | -0.33874 | -0.19226 | -0.1236 | 121.4767 | 121.431 | 61.1389 | -121.582 | 121.5088 | 121.431 | 61.1801 | -121.701
326.9375 | 121.8567 | -61.2442 | 60.3928 | -0.23376 | 0.016007 | 0.071863 | 0.066633 | 0.12973 | -0.0019632 | -0.0022516 | -0.19958 | -0.0054196 | 0.061662 | 0.068468 | 0.0031681 | -0.0070345 | 60.2463 | 60.4523 | 0.13733 | -61.3495 | 60.2966 | -61.2396 | -61.2396 | -61.0565 | 0.15564 | -61.5463 | 60.2966 | 60.2875 | -61.1481 | -61.3541 | 0.004578 | 0.004578 | -0.09613 | 121.6965 | -0.10529 | -0.10986 | -0.14648 | 0.096131 | -0.10986 | -0.09613 | 0.18768 | -0.30212 | -0.19226 | -0.10529 | 121.5408 | 121.4905 | 61.3815 | -121.6324 | 121.5408 | 121.5317 | 61.3998 | -121.7468
328.6875 | 121.843 | -61.3083 | 60.3287 | 0.033264 | 0.016007 | 0.072504 | 0.063856 | 0.12866 | -0.0017496 | -0.003106 | 0.082703 | -0.0045652 | 0.063798 | 0.071245 | 0.0048769 | -0.0093845 | 60.1318 | 60.2966 | -0.1236 | -61.4594 | 60.1913 | -61.3266 | -61.3174 | -61.1618 | -0.086975 | -61.6562 | 60.2188 | 60.1547 | -61.2762 | -61.441 | -0.01831 | -0.009155 | -0.13733 | 121.6049 | -0.15106 | -0.14191 | -0.19684 | 0.032044 | -0.13275 | -0.10986 | 0.14649 | -0.3479 | -0.21515 | -0.17395 | 121.4996 | 121.4401 | 61.1847 | -121.6461 | 121.5271 | 121.463 | 61.2213 | -121.7697
330.4375 | 121.9391 | -61.1847 | 60.4019 | -0.088806 | 0.010666 | 0.070581 | 0.069838 | 0.12866 | -0.0075174 | -0.003106 | -0.0012209 | -0.0064878 | 0.063371 | 0.070818 | -0.0017453 | -0.0059665 | 60.3241 | 60.585 | 0.20599 | -61.2808 | 60.2554 | -61.2076 | -61.1801 | -60.9055 | 0.27008 | -61.3724 | 60.2417 | 60.2142 | -61.1252 | -61.2991 | -0.022889 | 0.004577 | -0.14648 | 121.7697 | -0.096131 | -0.10071 | -0.07782 | 0.059509 | -0.11444 | -0.16022 | 0.27923 | -0.18768 | -0.073242 | -0.18768 | 121.4401 | 121.5088 | 61.3907 | -121.582 | 121.4264 | 121.3989 | 61.4548 | -121.701
332.1875 | 121.8292 | -61.2946 | 60.3104 | 0.048523 | 0.016648 | 0.071222 | 0.06407 | 0.12824 | 0.0023092 | -0.003106 | 0.067444 | -0.0043516 | 0.062089 | 0.075304 | 0.0042361 | -0.0089573 | 60.1547 | 60.2875 | -0.13275 | -61.4731 | 60.1959 | -61.3312 | -61.3037 | -61.1572 | -0.10071 | -61.6653 | 60.2188 | 60.1776 | -61.2579 | -61.4365 | -0.036621 | -0.009155 | -0.11444 | 121.582 | -0.17853 | -0.16937 | -0.15564 | 0.036621 | -0.14191 | -0.091553 | 0.13733 | -0.37079 | -0.22888 | -0.13275 | 121.4905 | 121.4493 | 61.1618 | -121.6141 | 121.5134 | 121.4722 | 61.1938 | -121.7468
333.875 | 121.8613 | -61.2396 | 60.3653 | -0.18799 | 0.015793 | 0.072717 | 0.070906 | 0.12866 | -0.0017496 | -0.0007562 | -0.14618 | -0.0049924 | 0.061662 | 0.073809 | 0.0016727 | -0.0098117 | 60.2371 | 60.4156 | 0.086975 | -61.3586 | 60.2737 | -61.2625 | -61.2579 | -61.0565 | 0.15564 | -61.5234 | 60.2829 | 60.26 | -61.1984 | -61.3586 | -0.022888 | -0.018311 | -0.091552 | 121.6553 | -0.11902 | -0.10071 | -0.12817 | 0.041199 | -0.11902 | -0.082397 | 0.1831 | -0.28381 | -0.16479 | -0.10529 | 121.5134 | 121.4767 | 61.3266 | -121.6232 | 121.5225 | 121.4996 | 61.3953 | -121.7239
335.6094 | 121.7972 | -61.3129 | 60.3241 | -0.058289 | 0.017289 | 0.071008 | 0.066633 | 0.13016 | 0.00060022 | -0.0016108 | 0.0064086 | -0.0045652 | 0.061449 | 0.07445 | 0.0033817 | -0.0083163 | 60.2188 | 60.4065 | 0.004578 | -61.4136 | 60.1868 | -61.3037 | -61.2717 | -61.116 | 0 | -61.6104 | 60.1776 | 60.1593 | -61.2579 | -61.4182 | 0.009155 | 0.041199 | -0.13733 | 121.7194 | -0.10071 | -0.14191 | -0.10529 | 0.054931 | -0.10529 | -0.14648 | 0.19684 | -0.29755 | -0.19226 | -0.1648 | 121.4996 | 121.5317 | 61.3174 | -121.5958 | 121.4905 | 121.4722 | 61.3129 | -121.7422
337.3594 | 121.8521 | -61.2396 | 60.4111 | -0.21851 | 0.016648 | 0.073145 | 0.068129 | 0.12824 | -0.0034586 | -0.0050286 | -0.16907 | -0.0071286 | 0.063798 | 0.071459 | 0.0012455 | -0.0091709 | 60.2188 | 60.4523 | 0.12817 | -61.3541 | 60.2966 | -61.2305 | -61.2076 | -61.0611 | 0.17395 | -61.528 | 60.3195 | 60.2921 | -61.1526 | -61.3358 | 0.009155 | 0.032043 | -0.11444 | 121.6919 | -0.11444 | -0.14648 | -0.19226 | 0.086975 | -0.09613 | -0.091553 | 0.17853 | -0.28839 | -0.19226 | -0.11902 | 121.5363 | 121.4584 | 61.3678 | -121.6187 | 121.5591 | 121.5317 | 61.4136 | -121.7468
339.1094 | 121.9162 | -61.2167 | 60.3653 | 0.0027468 | 0.016861 | 0.070154 | 0.067488 | 0.12482 | -0.0092264 | -0.003106 | 0.14374 | -0.0067014 | 0.062303 | 0.069323 | -0.00046349 | -0.0076755 | 60.2417 | 60.4614 | 0.050354 | -61.3358 | 60.2142 | -61.235 | -61.1984 | -61.0336 | 0.10071 | -61.4639 | 60.2371 | 60.2142 | -61.1847 | -61.3541 | -0.01831 | 0.018311 | -0.15106 | 121.6782 | -0.11902 | -0.13733 | -0.1236 | 0.032044 | -0.13733 | -0.12817 | 0.18311 | -0.24719 | -0.10986 | -0.15106 | 121.431 | 121.4584 | 61.2671 | -121.5637 | 121.4539 | 121.431 | 61.3174 | -121.7194
340.7969 | 121.9299 | -61.2808 | 60.2783 | 0.08667 | 0.013443 | 0.071222 | 0.064497 | 0.12653 | -0.0013224 | -0.0028924 | 0.159 | -0.0056332 | 0.060381 | 0.070391 | 0.0057315 | -0.0085299 | 60.1776 | 60.3424 | -0.1236 | -61.4639 | 60.2097 | -61.3403 | -61.3037 | -61.1023 | -0.064087 | -61.5875 | 60.1822 | 60.1593 | -61.235 | -61.4182 | -0.059509 | -0.022888 | -0.068664 | 121.6232 | -0.18311 | -0.16022 | -0.10071 | 0.045777 | -0.13733 | -0.09613 | 0.17853 | -0.3067 | -0.16937 | -0.11902 | 121.4905 | 121.4584 | 61.1572 | -121.582 | 121.463 | 121.4401 | 61.2167 | -121.6965
342.5469 | 121.7972 | -61.2259 | 60.4065 | -0.24902 | 0.017502 | 0.071436 | 0.068342 | 0.13144 | -0.0055948 | -0.0073786 | -0.085144 | -0.0043516 | 0.062089 | 0.070391 | 0.00060451 | -0.0087435 | 60.2966 | 60.466 | 0.17853 | -61.3312 | 60.2646 | -61.2442 | -61.2213 | -61.0428 | 0.20142 | -61.5051 | 60.2966 | 60.2646 | -61.1664 | -61.3312 | -0.018311 | 0.004578 | -0.14191 | 121.6919 | -0.10529 | -0.10986 | -0.10986 | 0.059509 | -0.10529 | -0.10986 | 0.1831 | -0.27924 | -0.17395 | -0.14191 | 121.4905 | 121.5225 | 61.4044 | -121.6278 | 121.5225 | 121.4905 | 61.4273 | -121.7377
344.2969 | 121.907 | -61.2076 | 60.3928 | -0.17273 | 0.01558 | 0.073145 | 0.067274 | 0.13208 | -0.0055948 | -0.0039606 | -0.069885 | -0.0067014 | 0.062517 | 0.06975 | -0.00067729 | -0.0087435 | 60.3607 | 60.5942 | 0.25177 | -61.2534 | 60.2509 | -61.203 | -61.171 | -60.9375 | 0.31128 | -61.3907 | 60.2737 | 60.2325 | -61.1343 | -61.3037 | 0.004578 | 0.036622 | -0.14191 | 121.8018 | -0.045776 | -0.082398 | -0.032043 | 0.073243 | -0.09613 | -0.11902 | 0.27008 | -0.18311 | -0.086975 | -0.16022 | 121.4584 | 121.5683 | 61.4594 | -121.5637 | 121.4813 | 121.4401 | 61.5189 | -121.6965
345.9844 | 121.8384 | -61.3312 | 60.3149 | 0.056152 | 0.017289 | 0.071436 | 0.063856 | 0.12631 | 0.0027364 | -0.002038 | 0.082703 | -0.006915 | 0.061662 | 0.072954 | 0.0046633 | -0.0085299 | 60.1547 | 60.2829 | -0.10986 | -61.4594 | 60.2051 | -61.3358 | -61.3174 | -61.1435 | -0.07782 | -61.6745 | 60.2005 | 60.1959 | -61.2671 | -61.4273 | -0.004577 | 0.013733 | -0.10986 | 121.6141 | -0.12817 | -0.14191 | -0.16022 | 0.064087 | -0.09613 | -0.11444 | 0.18768 | -0.34332 | -0.24719 | -0.11902 | 121.5363 | 121.4859 | 61.2213 | -121.6324 | 121.5317 | 121.5271 | 61.2534 | -121.7422
347.7344 | 121.8933 | -61.2396 | 60.3241 | 0.10956 | 0.013871 | 0.070795 | 0.064283 | 0.12909 | -0.0062356 | -0.0018244 | 0.19714 | -0.0077696 | 0.060381 | 0.073168 | 0.0014591 | -0.0087435 | 60.2554 | 60.4706 | 0.027466 | -61.3724 | 60.1822 | -61.2625 | -61.2305 | -61.0336 | 0.073242 | -61.4731 | 60.2188 | 60.2142 | -61.1618 | -61.3449 | -0.022888 | 0.009155 | -0.14191 | 121.7102 | -0.13275 | -0.14191 | -0.068665 | 0.07782 | -0.10529 | -0.10529 | 0.20599 | -0.23346 | -0.12817 | -0.10986 | 121.4218 | 121.4951 | 61.2671 | -121.5546 | 121.4584 | 121.4539 | 61.3129 | -121.669
349.4688 | 121.9528 | -61.1755 | 60.3607 | -0.11169 | 0.013871 | 0.071436 | 0.068129 | 0.12888 | -0.0064492 | -0.006524 | -0.0012209 | -0.0062742 | 0.063798 | 0.071459 | 0.00081811 | -0.0070345 | 60.3516 | 60.5621 | 0.20599 | -61.2762 | 60.2692 | -61.2167 | -61.171 | -60.9192 | 0.25635 | -61.3815 | 60.2325 | 60.2417 | -61.1206 | -61.2946 | -0.041199 | 0.004578 | -0.091553 | 121.7377 | -0.10071 | -0.10529 | -0.009156 | 0.054932 | -0.11902 | -0.12817 | 0.25635 | -0.20599 | -0.086975 | -0.11902 | 121.4447 | 121.5271 | 61.3815 | -121.5317 | 121.4081 | 121.4172 | 61.4319 | -121.6553
351.1562 | 121.8842 | -61.2442 | 60.3516 | 0.10956 | 0.014084 | 0.068445 | 0.063215 | 0.12759 | -0.0064492 | -0.003747 | 0.159 | -0.0062742 | 0.061876 | 0.071032 | 0.0016727 | -0.0072483 | 60.2737 | 60.466 | 0.032043 | -61.3678 | 60.173 | -61.2625 | -61.2442 | -61.0062 | 0.073242 | -61.496 | 60.2005 | 60.2051 | -61.1893 | -61.3449 | -0.01831 | 0 | -0.17853 | 121.7102 | -0.1236 | -0.1236 | -0.077819 | 0.054932 | -0.10071 | -0.15106 | 0.23804 | -0.25177 | -0.15106 | -0.14648 | 121.4172 | 121.5179 | 61.2762 | -121.5958 | 121.4447 | 121.4493 | 61.3174 | -121.6965
352.8438 | 121.907 | -61.2488 | 60.3333 | 0.16296 | 0.014725 | 0.072504 | 0.064283 | 0.12717 | -4.058e-05 | -0.0026788 | 0.18951 | -0.0071286 | 0.058885 | 0.071245 | 0.0055179 | -0.0085299 | 60.2737 | 60.466 | 0.004578 | -61.3815 | 60.1318 | -61.2946 | -61.2488 | -61.0153 | 0.050354 | -61.5051 | 60.1776 | 60.1456 | -61.1984 | -61.3861 | -0.045777 | 0 | -0.20142 | 121.7148 | -0.13275 | -0.13275 | -0.059509 | 0.050354 | -0.13733 | -0.15564 | 0.23346 | -0.25635 | -0.11902 | -0.18768 | 121.3806 | 121.5225 | 61.2534 | -121.582 | 121.4264 | 121.3943 | 61.2991 | -121.7194
354.5938 | 121.8246 | -61.3129 | 60.3195 | -0.11169 | 0.017075 | 0.072504 | 0.065565 | 0.12866 | 0.0020956 | -0.0011834 | -0.092773 | -0.0062742 | 0.061876 | 0.071459 | 0.0048769 | -0.011307 | 60.2554 | 60.4156 | 0.059509 | -61.3815 | 60.228 | -61.2991 | -61.2442 | -61.0474 | 0.09613 | -61.5463 | 60.2463 | 60.1913 | -61.2213 | -61.3953 | 0.013733 | 0.068664 | -0.091553 | 121.7285 | -0.068665 | -0.13733 | -0.064087 | 0.091553 | -0.082398 | -0.073242 | 0.2655 | -0.23346 | -0.15106 | -0.12817 | 121.5408 | 121.5683 | 61.3724 | -121.5637 | 121.5591 | 121.5042 | 61.409 | -121.7148
356.3125 | 121.9528 | -61.1755 | 60.3882 | -0.13458 | 0.015793 | 0.07229 | 0.06642 | 0.13016 | -0.0070902 | -0.0035334 | -0.0012209 | -0.0088376 | 0.062517 | 0.072314 | -0.0013181 | -0.0070345 | 60.3424 | 60.5667 | 0.20599 | -61.2762 | 60.2463 | -61.1893 | -61.1664 | -60.9192 | 0.2655 | -61.377 | 60.2509 | 60.2417 | -61.1298 | -61.29 | -0.013733 | 0.009155 | -0.14191 | 121.7422 | -0.10071 | -0.10986 | -0.045777 | 0.045776 | -0.11444 | -0.13733 | 0.25635 | -0.20142 | -0.086975 | -0.14649 | 121.4218 | 121.5179 | 61.3815 | -121.5546 | 121.4264 | 121.4172 | 61.441 | -121.6782
358 | 121.9299 | -61.203 | 60.3607 | -0.12695 | 0.01558 | 0.075281 | 0.066633 | 0.13144 | -0.0040994 | -0.002038 | -0.054626 | -0.0077696 | 0.060594 | 0.070818 | -0.00024989 | -0.0085299 | 60.3516 | 60.585 | 0.2243 | -61.29 | 60.2509 | -61.203 | -61.171 | -60.9146 | 0.28839 | -61.3724 | 60.2646 | 60.228 | -61.1114 | -61.2762 | 0 | 0.032044 | -0.10986 | 121.788 | -0.086975 | -0.11902 | -0.009156 | 0.091553 | -0.073242 | -0.096131 | 0.28839 | -0.16937 | -0.09613 | -0.13275 | 121.4539 | 121.5546 | 61.4273 | -121.5317 | 121.4676 | 121.431 | 61.4914 | -121.637
359.7344 | 121.9437 | -61.1801 | 60.3882 | -0.11169 | 0.013871 | 0.073572 | 0.064497 | 0.12866 | -0.0051676 | -0.0052424 | -0.016479 | -0.0073422 | 0.060808 | 0.068041 | -0.00046349 | -0.0081027 | 60.347 | 60.5438 | 0.18768 | -61.2808 | 60.2463 | -61.2167 | -61.1801 | -60.9192 | 0.26093 | -61.3907 | 60.228 | 60.2371 | -61.1252 | -61.2991 | -0.036621 | 0 | -0.14191 | 121.7239 | -0.10071 | -0.10071 | -0.041199 | 0.054932 | -0.11902 | -0.16022 | 0.26093 | -0.21057 | -0.091553 | -0.15106 | 121.4264 | 121.5271 | 61.3678 | -121.5683 | 121.4081 | 121.4172 | 61.441 | -121.6873
361.4062 | 121.9574 | -61.203 | 60.3607 | 0.018005 | 0.014298 | 0.072717 | 0.065992 | 0.12994 | -0.0034586 | -0.0024652 | 0.036926 | -0.0088376 | 0.062517 | 0.071245 | 0.0010317 | -0.0091709 | 60.2783 | 60.466 | 0.07782 | -61.3403 | 60.2325 | -61.2534 | -61.1938 | -60.9741 | 0.16479 | -61.4365 | 60.26 | 60.2234 | -61.1572 | -61.3083 | -0.050354 | 0.009155 | -0.12817 | 121.669 | -0.13733 | -0.14648 | -0.082398 | 0.045776 | -0.10529 | -0.10071 | 0.22888 | -0.23346 | -0.12817 | -0.13733 | 121.4355 | 121.4813 | 61.2808 | -121.5546 | 121.463 | 121.4264 | 61.3678 | -121.669
363.1719 | 121.8338 | -61.29 | 60.3104 | -0.096436 | 0.019211 | 0.06994 | 0.066206 | 0.1308 | 0.0031638 | -0.005456 | -0.10803 | -0.0047788 | 0.062089 | 0.071886 | 0.0040225 | -0.011521 | 60.26 | 60.4248 | 0.064087 | -61.3861 | 60.2097 | -61.3037 | -61.2625 | -61.0474 | 0.10529 | -61.5463 | 60.2371 | 60.2097 | -61.2305 | -61.3907 | -0.013733 | 0.027466 | -0.10071 | 121.7148 | -0.09613 | -0.1236 | -0.050354 | 0.059509 | -0.10071 | -0.073242 | 0.24262 | -0.25635 | -0.15564 | -0.10071 | 121.4996 | 121.55 | 61.3541 | -121.5729 | 121.5271 | 121.4996 | 61.3953 | -121.7011
364.9219 | 121.9254 | -61.171 | 60.3653 | 0.0027468 | 0.012375 | 0.071008 | 0.068556 | 0.12738 | -0.004313 | -0.0046014 | 0.10559 | -0.0062742 | 0.064439 | 0.069109 | 0.00039091 | -0.0074619 | 60.2554 | 60.4843 | 0.064087 | -61.3449 | 60.2051 | -61.2259 | -61.2259 | -61.0107 | 0.10986 | -61.4822 | 60.2463 | 60.1959 | -61.1984 | -61.3403 | -0.054932 | -0.054932 | -0.16022 | 121.6553 | -0.17395 | -0.11902 | -0.10986 | -0.027466 | -0.16937 | -0.11902 | 0.16022 | -0.31128 | -0.14191 | -0.16937 | 121.376 | 121.4264 | 61.235 | -121.5912 | 121.4172 | 121.3669 | 61.2808 | -121.7056
366.6094 | 121.9162 | -61.1893 | 60.3699 | -0.12695 | 0.017929 | 0.07229 | 0.065992 | 0.12717 | -0.006022 | -0.0046014 | -0.077515 | -0.007556 | 0.061021 | 0.072314 | 0.00017731 | -0.0085299 | 60.347 | 60.6171 | 0.24719 | -61.2534 | 60.2463 | -61.2076 | -61.1664 | -60.9192 | 0.3067 | -61.3724 | 60.26 | 60.2371 | -61.1069 | -61.2808 | -0.018311 | 0.022888 | -0.1236 | 121.8063 | -0.064087 | -0.086975 | -0.022888 | 0.082397 | -0.091553 | -0.10986 | 0.27008 | -0.1831 | -0.091552 | -0.13275 | 121.4355 | 121.5363 | 61.4365 | -121.5363 | 121.4493 | 121.4264 | 61.496 | -121.6507
368.375 | 121.8933 | -61.2396 | 60.3561 | 0.08667 | 0.017289 | 0.073145 | 0.065992 | 0.12952 | -0.0045266 | -0.0035334 | 0.17426 | -0.0062742 | 0.064867 | 0.071032 | 0.0038089 | -0.0074619 | 60.2692 | 60.4752 | 0.022888 | -61.3632 | 60.173 | -61.2854 | -61.2396 | -61.0016 | 0.064087 | -61.496 | 60.1913 | 60.1501 | -61.1984 | -61.3541 | -0.045776 | 0 | -0.18311 | 121.7148 | -0.1236 | -0.1236 | -0.086975 | 0.041199 | -0.11444 | -0.1648 | 0.23804 | -0.25635 | -0.14191 | -0.20599 | 121.4127 | 121.5088 | 61.2625 | -121.5958 | 121.431 | 121.3898 | 61.3037 | -121.7102
370.0625 | 121.9391 | -61.1664 | 60.3516 | -0.0048827 | 0.013443 | 0.075708 | 0.065351 | 0.12866 | -0.004313 | -0.0043878 | 0.059815 | -0.0060606 | 0.060808 | 0.069964 | 0.00060451 | -0.0057529 | 60.2646 | 60.4797 | 0.082397 | -61.3358 | 60.2509 | -61.2579 | -61.2076 | -60.9879 | 0.13733 | -61.4594 | 60.2417 | 60.2005 | -61.171 | -61.3403 | -0.091553 | -0.041199 | -0.10071 | 121.6461 | -0.16937 | -0.12817 | -0.086975 | -0.004577 | -0.17395 | -0.10986 | 0.17853 | -0.29297 | -0.11902 | -0.15106 | 121.4172 | 121.431 | 61.2488 | -121.5591 | 121.4081 | 121.3669 | 61.3037 | -121.6919
371.8125 | 121.8201 | -61.235 | 60.4477 | -0.21088 | 0.014939 | 0.073145 | 0.066206 | 0.12909 | -0.00068138 | -0.0035334 | -0.15381 | -0.0045652 | 0.062944 | 0.073168 | 0.00060451 | -0.0091709 | 60.3699 | 60.5484 | 0.21515 | -61.2808 | 60.2783 | -61.2213 | -61.171 | -60.997 | 0.23804 | -61.4777 | 60.3012 | 60.2509 | -61.1618 | -61.3495 | 0.013733 | 0.064087 | -0.16937 | 121.7834 | -0.045777 | -0.10986 | -0.07782 | 0.073242 | -0.11444 | -0.14648 | 0.23804 | -0.24262 | -0.12817 | -0.19684 | 121.5134 | 121.6049 | 61.4502 | -121.6187 | 121.5363 | 121.4859 | 61.4731 | -121.7972
373.5938 | 121.8796 | -61.2122 | 60.3745 | 0.08667 | 0.014725 | 0.071436 | 0.066847 | 0.12866 | -0.0034586 | -0.0028924 | 0.15137 | -0.004138 | 0.061021 | 0.070605 | 0.0014591 | -0.0085299 | 60.26 | 60.4523 | 0.027466 | -61.377 | 60.1822 | -61.29 | -61.2305 | -60.997 | 0.059509 | -61.4868 | 60.2051 | 60.173 | -61.1755 | -61.3266 | -0.07782 | -0.018311 | -0.19226 | 121.6644 | -0.16479 | -0.14648 | -0.11444 | 0.036621 | -0.11444 | -0.16937 | 0.21515 | -0.27466 | -0.16022 | -0.20142 | 121.3943 | 121.4722 | 61.2396 | -121.6049 | 121.4172 | 121.3852 | 61.2717 | -121.7011
375.3438 | 121.8613 | -61.2808 | 60.3241 | -0.096436 | 0.018143 | 0.072076 | 0.064283 | 0.13037 | 0.0044454 | -0.0022516 | -0.12329 | -0.0020018 | 0.061235 | 0.071245 | 0.0059451 | -0.0091709 | 60.2692 | 60.4431 | 0.064087 | -61.3678 | 60.2417 | -61.3312 | -61.2762 | -61.0474 | 0.10986 | -61.5417 | 60.2371 | 60.1868 | -61.2122 | -61.4044 | -0.050354 | 0.004578 | -0.082398 | 121.7239 | -0.086975 | -0.091553 | -0.054932 | 0.068665 | -0.1236 | -0.086975 | 0.23346 | -0.26093 | -0.13733 | -0.13733 | 121.5225 | 121.55 | 61.3449 | -121.6003 | 121.5179 | 121.4676 | 61.3907 | -121.7285
377.0156 | 121.8109 | -61.2854 | 60.3241 | -0.065918 | 0.014725 | 0.075067 | 0.064283 | 0.12952 | 0.00038662 | -0.0028924 | -0.069885 | -0.005206 | 0.059526 | 0.06975 | 0.0067997 | -0.0081027 | 60.2554 | 60.4477 | 0.045776 | -61.377 | 60.2188 | -61.29 | -61.2442 | -61.0519 | 0.10529 | -61.5463 | 60.2554 | 60.1822 | -61.2167 | -61.3861 | -0.004578 | 0.041198 | -0.10529 | 121.7331 | -0.091553 | -0.13275 | -0.068665 | 0.068664 | -0.10071 | -0.068665 | 0.23346 | -0.26093 | -0.16022 | -0.14191 | 121.5042 | 121.5408 | 61.3312 | -121.5683 | 121.5408 | 121.4676 | 61.3907 | -121.7102
378.7812 | 121.9345 | -61.1755 | 60.3607 | -0.073547 | 0.01558 | 0.074213 | 0.067915 | 0.1293 | -0.0081582 | -0.003747 | -0.0088499 | -0.0049924 | 0.05974 | 0.068468 | 0.0010317 | -0.0072483 | 60.3378 | 60.5713 | 0.20142 | -61.2762 | 60.2646 | -61.2076 | -61.1847 | -60.9238 | 0.26093 | -61.3724 | 60.2463 | 60.2142 | -61.1298 | -61.3449 | -0.032044 | -0.009155 | -0.096131 | 121.7468 | -0.10071 | -0.091553 | -0.022888 | 0.045776 | -0.16937 | -0.11444 | 0.25177 | -0.19684 | -0.027465 | -0.14648 | 121.4401 | 121.5134 | 61.377 | -121.5454 | 121.4218 | 121.3898 | 61.4365 | -121.7056
380.4688 | 121.7926 | -61.3266 | 60.3195 | -0.065918 | 0.016434 | 0.072076 | 0.064711 | 0.12824 | 0.0027364 | -0.0024652 | -0.016479 | -0.0043516 | 0.061449 | 0.071032 | 0.0055179 | -0.0095981 | 60.2371 | 60.4065 | 0 | -61.4136 | 60.2188 | -61.2991 | -61.2854 | -61.0931 | 0.013733 | -61.615 | 60.2371 | 60.1959 | -61.2305 | -61.4365 | 0.027466 | 0.041199 | -0.10071 | 121.7331 | -0.086975 | -0.12817 | -0.082397 | 0.09613 | -0.10986 | -0.082397 | 0.23346 | -0.28839 | -0.17853 | -0.1236 | 121.5454 | 121.5637 | 61.3266 | -121.6049 | 121.5637 | 121.5225 | 61.3403 | -121.756
382.2188 | 121.8979 | -61.2213 | 60.3607 | 0.056152 | 0.014725 | 0.072931 | 0.065351 | 0.12674 | -0.0070902 | -0.0039606 | 0.159 | -0.0060606 | 0.059099 | 0.068896 | 0.0014591 | -0.0066073 | 60.2417 | 60.5026 | 0.027466 | -61.3586 | 60.1913 | -61.2717 | -61.2305 | -61.0291 | 0.073242 | -61.4777 | 60.2005 | 60.1913 | -61.1893 | -61.3403 | -0.050354 | -0.009156 | -0.16937 | 121.7239 | -0.13733 | -0.12817 | -0.11902 | 0.032043 | -0.11902 | -0.16022 | 0.19226 | -0.25635 | -0.13733 | -0.16937 | 121.4127 | 121.463 | 61.2488 | -121.5912 | 121.4218 | 121.4127 | 61.2946 | -121.701
383.9688 | 121.9025 | -61.2167 | 60.3653 | 0.0027468 | 0.010453 | 0.072717 | 0.063429 | 0.12973 | -0.0079446 | -0.0046014 | 0.12848 | -0.006915 | 0.062303 | 0.069109 | 0.0025271 | -0.0074619 | 60.2371 | 60.4706 | 0.059509 | -61.3449 | 60.2234 | -61.2488 | -61.1984 | -61.0336 | 0.10529 | -61.4777 | 60.2463 | 60.2188 | -61.1801 | -61.3403 | -0.032043 | 0.018311 | -0.14191 | 121.6873 | -0.12817 | -0.14648 | -0.12817 | 0.036621 | -0.1236 | -0.11902 | 0.18311 | -0.26093 | -0.13733 | -0.14648 | 121.4401 | 121.4539 | 61.2762 | -121.5637 | 121.463 | 121.4355 | 61.322 | -121.7056
385.6406 | 121.8613 | -61.2488 | 60.347 | -0.12695 | 0.019852 | 0.070581 | 0.068129 | 0.1293 | 0.0014548 | -0.0035334 | -0.085144 | -0.0064878 | 0.062303 | 0.072954 | 0.0033817 | -0.0089573 | 60.2737 | 60.4248 | 0.082397 | -61.3678 | 60.2463 | -61.2991 | -61.2762 | -61.0611 | 0.10529 | -61.5417 | 60.2188 | 60.1913 | -61.203 | -61.4044 | -0.050354 | -0.027466 | -0.10071 | 121.6736 | -0.11902 | -0.091553 | -0.073242 | 0.045776 | -0.15564 | -0.12817 | 0.18768 | -0.29297 | -0.13733 | -0.15564 | 121.4951 | 121.5225 | 61.3312 | -121.6232 | 121.4676 | 121.4401 | 61.3541 | -121.7514
387.375 | 121.8018 | -61.322 | 60.3149 | 0.048523 | 0.018784 | 0.06994 | 0.066633 | 0.12909 | -4.058e-05 | -0.0009698 | 0.052185 | -0.0043516 | 0.062517 | 0.072314 | 0.0046633 | -0.0076755 | 60.1547 | 60.3241 | -0.082397 | -61.4594 | 60.1913 | -61.3541 | -61.2946 | -61.1526 | -0.054932 | -61.6379 | 60.2417 | 60.1913 | -61.2717 | -61.409 | -0.032044 | 0.027465 | -0.1236 | 121.6461 | -0.13733 | -0.16479 | -0.16022 | 0.050354 | -0.086976 | -0.073242 | 0.16937 | -0.31586 | -0.22888 | -0.1236 | 121.5134 | 121.4767 | 61.2396 | -121.6095 | 121.5637 | 121.5134 | 61.2671 | -121.7239
389.125 | 121.8338 | -61.2396 | 60.3836 | -0.23376 | 0.019211 | 0.072504 | 0.068342 | 0.12909 | -0.001536 | -0.0043878 | -0.1767 | -0.0062742 | 0.065294 | 0.071673 | -3.629e-05 | -0.0083163 | 60.26 | 60.4431 | 0.12817 | -61.3541 | 60.3104 | -61.2534 | -61.235 | -61.0794 | 0.15564 | -61.5051 | 60.3058 | 60.2966 | -61.1801 | -61.3358 | -0.013733 | 0.004578 | -0.073242 | 121.6827 | -0.11444 | -0.11902 | -0.1236 | 0.059509 | -0.09613 | -0.07782 | 0.16022 | -0.2655 | -0.16937 | -0.086975 | 121.55 | 121.4996 | 61.3678 | -121.6187 | 121.5454 | 121.5363 | 61.3953 | -121.7194
390.8594 | 121.8201 | -61.2946 | 60.3058 | 0.056152 | 0.01622 | 0.072076 | 0.061934 | 0.12973 | -0.001536 | -0.0009698 | 0.090332 | -0.0064878 | 0.061876 | 0.071459 | 0.0042361 | -0.0093845 | 60.1501 | 60.2875 | -0.1236 | -61.4731 | 60.1959 | -61.3312 | -61.2946 | -61.1755 | -0.091553 | -61.6379 | 60.2188 | 60.1685 | -61.2762 | -61.4548 | -0.036621 | 0 | -0.10986 | 121.582 | -0.17853 | -0.17853 | -0.15564 | 0.018311 | -0.16022 | -0.086975 | 0.11902 | -0.34332 | -0.1831 | -0.13733 | 121.4905 | 121.4447 | 61.171 | -121.6003 | 121.5134 | 121.463 | 61.203 | -121.7606
392.6094 | 121.9391 | -61.1893 | 60.347 | 0.0027468 | 0.015793 | 0.072931 | 0.068983 | 0.12738 | -0.010295 | -0.0056696 | 0.12085 | -0.0077696 | 0.06273 | 0.072741 | -0.0017453 | -0.0078891 | 60.2142 | 60.4614 | 0.082397 | -61.3449 | 60.2142 | -61.2625 | -61.2122 | -61.0291 | 0.1236 | -61.4502 | 60.2463 | 60.2142 | -61.1618 | -61.3312 | -0.073242 | -0.022888 | -0.13275 | 121.6507 | -0.15564 | -0.13275 | -0.13275 | 0.027466 | -0.14191 | -0.10071 | 0.16022 | -0.26093 | -0.11902 | -0.13275 | 121.4035 | 121.4035 | 61.2717 | -121.5591 | 121.4355 | 121.4035 | 61.3129 | -121.6782
394.2969 | 121.9025 | -61.235 | 60.347 | 0.10193 | 0.014084 | 0.072504 | 0.061506 | 0.12781 | -0.004313 | -0.0050286 | 0.22766 | -0.0062742 | 0.060808 | 0.072314 | 0.0042361 | -0.0066073 | 60.2554 | 60.4706 | 0.022888 | -61.3724 | 60.1501 | -61.2717 | -61.2579 | -61.0291 | 0.054932 | -61.4685 | 60.1959 | 60.1685 | -61.1984 | -61.377 | -0.036621 | -0.022889 | -0.19684 | 121.7056 | -0.13733 | -0.11444 | -0.091553 | 0.036621 | -0.14191 | -0.15106 | 0.20599 | -0.23346 | -0.091553 | -0.17853 | 121.3852 | 121.4905 | 61.2579 | -121.6049 | 121.431 | 121.4035 | 61.29 | -121.7239
395.9844 | 121.8109 | -61.3129 | 60.3333 | 0.079041 | 0.014939 | 0.069086 | 0.063856 | 0.12781 | 0.0014548 | -0.0028924 | 0.044556 | -0.0062742 | 0.061449 | 0.072741 | 0.0053043 | -0.0083163 | 60.1501 | 60.3012 | -0.086975 | -61.4594 | 60.2097 | -61.322 | -61.3037 | -61.1664 | -0.07782 | -61.6562 | 60.2371 | 60.1913 | -61.2762 | -61.4548 | -0.009155 | 0.009155 | -0.1236 | 121.6141 | -0.14648 | -0.15564 | -0.18311 | 0.036621 | -0.14191 | -0.09613 | 0.14648 | -0.34332 | -0.20142 | -0.14191 | 121.5225 | 121.463 | 61.2259 | -121.637 | 121.55 | 121.5042 | 61.235 | -121.788
397.7344 | 121.788 | -61.3129 | 60.3241 | -0.04303 | 0.01558 | 0.070367 | 0.066206 | 0.13037 | 0.001882 | -0.003106 | 0.0064086 | -0.0039244 | 0.060381 | 0.072741 | 0.0048769 | -0.0089573 | 60.2325 | 60.3973 | -0.009155 | -61.4227 | 60.2051 | -61.2991 | -61.2762 | -61.1389 | -0.009155 | -61.6379 | 60.1959 | 60.1868 | -61.2625 | -61.4319 | 0.013733 | 0.036621 | -0.11902 | 121.7102 | -0.10986 | -0.14648 | -0.091553 | 0.050354 | -0.11902 | -0.12817 | 0.17395 | -0.32501 | -0.20599 | -0.13733 | 121.5179 | 121.5454 | 61.3037 | -121.6003 | 121.5088 | 121.4996 | 61.3037 | -121.756
399.5 | 121.8475 | -61.2854 | 60.3516 | -0.24902 | 0.01622 | 0.072076 | 0.06941 | 0.1293 | -0.0030314 | -0.0052424 | -0.15381 | -0.005206 | 0.062517 | 0.071886 | 0.0023135 | -0.0070345 | 60.2234 | 60.434 | 0.1236 | -61.3632 | 60.3012 | -61.2579 | -61.2122 | -61.084 | 0.15564 | -61.5372 | 60.2921 | 60.2783 | -61.171 | -61.3586 | 0.027465 | 0.073242 | -0.050354 | 121.7194 | -0.07782 | -0.15106 | -0.12817 | 0.11444 | -0.073243 | -0.059509 | 0.20142 | -0.25177 | -0.17853 | -0.073242 | 121.5866 | 121.5088 | 61.409 | -121.5637 | 121.5775 | 121.5637 | 61.441 | -121.7102
401.1875 | 121.8338 | -61.3037 | 60.3195 | 0.018005 | 0.017075 | 0.07229 | 0.063002 | 0.12845 | -0.00046778 | -0.0011834 | 0.10559 | -0.0056332 | 0.061449 | 0.0721 | 0.0057315 | -0.0072483 | 60.1181 | 60.2829 | -0.13275 | -61.4731 | 60.1868 | -61.3358 | -61.3174 | -61.1801 | -0.09613 | -61.647 | 60.2097 | 60.1547 | -61.2946 | -61.441 | -0.032043 | -0.013733 | -0.13275 | 121.5866 | -0.16937 | -0.15564 | -0.20142 | 0.009155 | -0.13733 | -0.10986 | 0.1236 | -0.34332 | -0.20599 | -0.16479 | 121.4905 | 121.4218 | 61.171 | -121.637 | 121.5134 | 121.4584 | 61.2076 | -121.7606
402.9531 | 121.8704 | -61.2808 | 60.3104 | -0.18036 | 0.019638 | 0.07229 | 0.068556 | 0.12888 | -0.00068138 | -0.0016108 | -0.10803 | -0.0054196 | 0.063585 | 0.071673 | 0.0023135 | -0.0070345 | 60.2417 | 60.4156 | 0.086975 | -61.3586 | 60.2463 | -61.2854 | -61.2488 | -61.0748 | 0.13275 | -61.5189 | 60.2097 | 60.2554 | -61.2076 | -61.3907 | -0.004577 | 0.032044 | -0.064087 | 121.6965 | -0.07782 | -0.10986 | -0.068665 | 0.073242 | -0.10986 | -0.10071 | 0.20599 | -0.23804 | -0.12817 | -0.054932 | 121.5271 | 121.5225 | 61.3678 | -121.5591 | 121.4905 | 121.5363 | 61.4136 | -121.7011
404.7031 | 121.8613 | -61.2762 | 60.3653 | -0.18036 | 0.017075 | 0.07229 | 0.065779 | 0.12845 | -0.004313 | -0.0026788 | -0.12329 | -0.005206 | 0.065507 | 0.073168 | 0.0012455 | -0.0089573 | 60.2325 | 60.434 | 0.10529 | -61.3586 | 60.2829 | -61.2534 | -61.2076 | -61.0931 | 0.13733 | -61.5234 | 60.2737 | 60.2463 | -61.1801 | -61.377 | 0.022888 | 0.068664 | -0.082397 | 121.7102 | -0.082398 | -0.15106 | -0.13275 | 0.09613 | -0.10071 | -0.091552 | 0.18311 | -0.24719 | -0.14648 | -0.11902 | 121.5591 | 121.5088 | 61.3815 | -121.5729 | 121.55 | 121.5225 | 61.4136 | -121.7422
406.3906 | 121.7972 | -61.3129 | 60.3516 | -0.073547 | 0.017289 | 0.073358 | 0.06407 | 0.12994 | -0.00046778 | -0.0016108 | 0.014038 | -0.0049924 | 0.06273 | 0.073809 | 0.0033817 | -0.0063937 | 60.2097 | 60.4156 | 0.018311 | -61.3953 | 60.2188 | -61.29 | -61.2808 | -61.1206 | 0.036621 | -61.6013 | 60.2097 | 60.173 | -61.2625 | -61.4319 | 0.022888 | 0.032043 | -0.13275 | 121.7285 | -0.082398 | -0.11444 | -0.14191 | 0.050354 | -0.11902 | -0.14191 | 0.19226 | -0.28839 | -0.16937 | -0.17853 | 121.5317 | 121.5225 | 61.3312 | -121.6324 | 121.5225 | 121.4859 | 61.3495 | -121.7834
408.1562 | 121.8475 | -61.2808 | 60.3561 | -0.15747 | 0.016648 | 0.074426 | 0.067701 | 0.12824 | -0.0013224 | -0.0024652 | -0.14618 | -0.0045652 | 0.063158 | 0.071673 | 0.00060451 | -0.0081027 | 60.2188 | 60.4202 | 0.10071 | -61.3815 | 60.2783 | -61.2579 | -61.235 | -61.0794 | 0.12817 | -61.5417 | 60.2829 | 60.2463 | -61.1801 | -61.3861 | 0.022888 | 0.045777 | -0.07782 | 121.701 | -0.10071 | -0.14649 | -0.13733 | 0.10071 | -0.10529 | -0.073242 | 0.20142 | -0.26093 | -0.15564 | -0.10986 | 121.5591 | 121.4996 | 61.3815 | -121.5912 | 121.5637 | 121.5271 | 61.409 | -121.7422
410.125 | 121.8979 | -61.235 | 60.3607 | 0.056152 | 0.011948 | 0.073572 | 0.065992 | 0.12717 | -0.0079446 | -0.0039606 | 0.18951 | -0.0071286 | 0.061021 | 0.072527 | -0.0011045 | -0.0059665 | 60.228 | 60.4706 | 0.032043 | -61.3586 | 60.1913 | -61.2488 | -61.2442 | -61.0611 | 0.073242 | -61.4868 | 60.2051 | 60.1639 | -61.2076 | -61.3449 | -0.013733 | -0.009156 | -0.16937 | 121.7056 | -0.1236 | -0.11444 | -0.13275 | 0.027465 | -0.10986 | -0.15564 | 0.17395 | -0.25177 | -0.14191 | -0.19684 | 121.4264 | 121.463 | 61.2671 | -121.6049 | 121.4401 | 121.3989 | 61.3083 | -121.7056
413.9219 | 121.8567 | -61.1938 | 60.3928 | -0.18799 | 0.01088 | 0.070367 | 0.066633 | 0.12674 | -0.0070902 | -0.0033196 | -0.0088499 | -0.0067014 | 0.062303 | 0.069964 | 0.0020999 | -0.0091709 | 60.3333 | 60.5896 | 0.25177 | -61.2808 | 60.2646 | -61.2076 | -61.1664 | -60.965 | 0.28839 | -61.3998 | 60.2646 | 60.2463 | -61.1526 | -61.3174 | -0.013733 | 0.027466 | -0.12817 | 121.7834 | -0.086975 | -0.11444 | -0.059509 | 0.041199 | -0.1236 | -0.12817 | 0.22888 | -0.20599 | -0.082397 | -0.14648 | 121.4584 | 121.5271 | 61.4456 | -121.5591 | 121.4584 | 121.4401 | 61.4822 | -121.7102
417.2656 | 121.8979 | -61.2305 | 60.3516 | 0.14008 | 0.011734 | 0.06994 | 0.064711 | 0.13251 | -0.0028178 | -0.003747 | 0.20477 | -0.008624 | 0.061876 | 0.071886 | 0.0025271 | -0.0098117 | 60.26 | 60.4752 | 0.004578 | -61.3678 | 60.1456 | -61.3037 | -61.2488 | -61.0062 | 0.054932 | -61.4777 | 60.1868 | 60.1685 | -61.203 | -61.3586 | -0.073242 | -0.01831 | -0.20599 | 121.7056 | -0.13733 | -0.11902 | -0.091552 | 0.027466 | -0.12817 | -0.16479 | 0.2243 | -0.24719 | -0.11902 | -0.18311 | 121.376 | 121.4905 | 61.235 | -121.6003 | 121.4172 | 121.3989 | 61.2854 | -121.7102
422.9375 | 121.9299 | -61.1755 | 60.3973 | -0.13458 | 0.013871 | 0.072504 | 0.066633 | 0.12845 | -0.0064492 | -0.0060968 | -0.046997 | -0.0071286 | 0.060808 | 0.070818 | -0.0019589 | -0.0093845 | 60.3653 | 60.6033 | 0.24261 | -61.2625 | 60.2554 | -61.1984 | -61.171 | -60.9421 | 0.30212 | -61.3724 | 60.2783 | 60.26 | -61.1114 | -61.2854 | -0.022888 | 0.004578 | -0.14191 | 121.7789 | -0.086975 | -0.091553 | -0.032044 | 0.064087 | -0.10986 | -0.11902 | 0.23346 | -0.19684 | -0.086975 | -0.13733 | 121.431 | 121.5408 | 61.4182 | -121.5683 | 121.4539 | 121.4355 | 61.4777 | -121.6827
424.7031 | 121.8063 | -61.235 | 60.434 | -0.21088 | 0.015793 | 0.073785 | 0.068342 | 0.12909 | -0.0023904 | -0.0058832 | -0.14618 | -0.0054196 | 0.063371 | 0.071886 | -3.629e-05 | -0.010025 | 60.3333 | 60.5392 | 0.21973 | -61.29 | 60.2646 | -61.2122 | -61.1801 | -61.0153 | 0.22888 | -61.4594 | 60.2875 | 60.2646 | -61.1801 | -61.3266 | 0.022888 | 0.054931 | -0.16937 | 121.7743 | -0.054932 | -0.10986 | -0.10071 | 0.054931 | -0.091553 | -0.14648 | 0.21973 | -0.22431 | -0.13275 | -0.16937 | 121.4996 | 121.5683 | 61.4548 | -121.6141 | 121.5225 | 121.4996 | 61.4639 | -121.7606
426.4531 | 121.907 | -61.235 | 60.347 | 0.14771 | 0.011521 | 0.070154 | 0.063002 | 0.12909 | -0.0038858 | -0.0046014 | 0.19714 | -0.0054196 | 0.062303 | 0.070391 | 0.0057315 | -0.0078891 | 60.2371 | 60.4614 | 0.009155 | -61.3632 | 60.1593 | -61.2808 | -61.2625 | -61.0199 | 0.050354 | -61.4868 | 60.1776 | 60.1501 | -61.2167 | -61.377 | -0.045777 | -0.027466 | -0.18768 | 121.6965 | -0.12817 | -0.10071 | -0.10986 | 0.01831 | -0.14191 | -0.16937 | 0.21515 | -0.25177 | -0.10986 | -0.19684 | 121.3943 | 121.4722 | 61.2442 | -121.6095 | 121.4127 | 121.3852 | 61.2854 | -121.7239
428.2031 | 121.843 | -61.3129 | 60.347 | 0.063782 | 0.015366 | 0.069299 | 0.064497 | 0.12695 | 0.0038046 | -0.002038 | 0.090332 | -0.0045652 | 0.064012 | 0.072527 | 0.0050907 | -0.011521 | 60.1456 | 60.2921 | -0.13275 | -61.4731 | 60.228 | -61.3586 | -61.3037 | -61.1618 | -0.11444 | -61.6516 | 60.2051 | 60.1776 | -61.2717 | -61.4594 | -0.045777 | 0.009155 | -0.11902 | 121.6049 | -0.16022 | -0.16937 | -0.20142 | 0.041199 | -0.14648 | -0.14191 | 0.15106 | -0.33875 | -0.19226 | -0.16937 | 121.5408 | 121.4584 | 61.1801 | -121.6507 | 121.5179 | 121.4905 | 61.1984 | -121.8063
429.9375 | 121.9482 | -61.1984 | 60.3516 | -0.012512 | 0.013443 | 0.073999 | 0.065351 | 0.12973 | -0.0090128 | -0.0035334 | 0.10559 | -0.0062742 | 0.061021 | 0.069109 | 0.00081811 | -0.0070345 | 60.2417 | 60.4843 | 0.068665 | -61.3449 | 60.2234 | -61.235 | -61.2076 | -61.0153 | 0.13733 | -61.4639 | 60.2417 | 60.2005 | -61.1618 | -61.3358 | -0.036621 | -0.009156 | -0.12817 | 121.6827 | -0.14648 | -0.13733 | -0.10986 | 0.036621 | -0.13733 | -0.10986 | 0.1831 | -0.2655 | -0.12817 | -0.15106 | 121.4218 | 121.4401 | 61.2671 | -121.5591 | 121.4401 | 121.3989 | 61.3358 | -121.6873
431.6094 | 121.8338 | -61.2259 | 60.3973 | -0.17273 | 0.015793 | 0.073145 | 0.067488 | 0.12717 | -0.0036722 | -0.003747 | -0.077515 | -0.006915 | 0.062517 | 0.071459 | -0.00067729 | -0.0098117 | 60.3378 | 60.5484 | 0.25177 | -61.2762 | 60.2325 | -61.2213 | -61.1984 | -60.9604 | 0.28381 | -61.4182 | 60.2646 | 60.2554 | -61.1206 | -61.322 | 0.004578 | 0.027466 | -0.1648 | 121.7743 | -0.050354 | -0.07782 | -0.059509 | 0.10529 | -0.09613 | -0.13275 | 0.2655 | -0.19226 | -0.096131 | -0.14191 | 121.4584 | 121.5637 | 61.4777 | -121.5958 | 121.4905 | 121.4813 | 61.5097 | -121.7194
433.3594 | 121.9254 | -61.2762 | 60.2783 | 0.079041 | 0.014511 | 0.072076 | 0.063215 | 0.12845 | 0.0010276 | -0.0039606 | 0.090332 | -0.0043516 | 0.060808 | 0.0721 | 0.0035953 | -0.0091709 | 60.173 | 60.3424 | -0.11444 | -61.4594 | 60.2234 | -61.3449 | -61.3129 | -61.1023 | -0.073242 | -61.615 | 60.2188 | 60.1593 | -61.2717 | -61.4273 | -0.068665 | -0.036621 | -0.054931 | 121.6187 | -0.18311 | -0.14648 | -0.10529 | 0.004578 | -0.15106 | -0.059509 | 0.17395 | -0.33874 | -0.18768 | -0.11902 | 121.4996 | 121.4493 | 61.1618 | -121.5912 | 121.4951 | 121.4355 | 61.203 | -121.7056
435.0312 | 121.8521 | -61.2671 | 60.347 | -0.21851 | 0.01558 | 0.073358 | 0.067488 | 0.13101 | -0.0011088 | -0.003747 | -0.15381 | -0.0045652 | 0.063158 | 0.071673 | 0.0035953 | -0.0095981 | 60.2417 | 60.4294 | 0.09613 | -61.3586 | 60.2921 | -61.2534 | -61.2442 | -61.0748 | 0.15106 | -61.5509 | 60.2966 | 60.2829 | -61.2076 | -61.3541 | 0.013733 | 0.022888 | -0.054932 | 121.6965 | -0.091553 | -0.11444 | -0.10529 | 0.059509 | -0.086975 | -0.050354 | 0.19226 | -0.28381 | -0.19684 | -0.064087 | 121.5591 | 121.5088 | 61.3632 | -121.5912 | 121.5637 | 121.55 | 61.4182 | -121.701
436.7188 | 121.9528 | -61.2625 | 60.2692 | 0.11719 | 0.014511 | 0.072504 | 0.063429 | 0.12866 | -0.0023904 | -0.003747 | 0.19714 | -0.0062742 | 0.061662 | 0.070605 | 0.0050907 | -0.0085299 | 60.1547 | 60.3653 | -0.12817 | -61.4548 | 60.173 | -61.3495 | -61.29 | -61.0931 | -0.050354 | -61.5646 | 60.1776 | 60.1501 | -61.2625 | -61.4273 | -0.086975 | -0.027466 | -0.09613 | 121.6278 | -0.19226 | -0.1648 | -0.11444 | 0 | -0.16479 | -0.091553 | 0.16937 | -0.30212 | -0.13733 | -0.11902 | 121.4355 | 121.4172 | 61.1343 | -121.5591 | 121.4401 | 121.4127 | 61.2122 | -121.6965
438.4688 | 121.9025 | -61.2213 | 60.3516 | 0.048523 | 0.017502 | 0.073999 | 0.069197 | 0.12866 | -0.0064492 | -0.0050286 | 0.14374 | -0.0077696 | 0.063158 | 0.071245 | -0.00089089 | -0.0059665 | 60.2371 | 60.4614 | 0.036621 | -61.3632 | 60.2325 | -61.2442 | -61.2167 | -61.0245 | 0.10071 | -61.4777 | 60.2097 | 60.2234 | -61.171 | -61.3449 | -0.022889 | 0.004577 | -0.11902 | 121.6827 | -0.14191 | -0.14648 | -0.11444 | 0.050354 | -0.1236 | -0.14191 | 0.19684 | -0.25635 | -0.13275 | -0.12817 | 121.4539 | 121.4584 | 61.2579 | -121.5683 | 121.431 | 121.4447 | 61.322 | -121.6965
440.1719 | 121.9254 | -61.2534 | 60.3058 | 0.048523 | 0.01323 | 0.072717 | 0.062361 | 0.13059 | -4.058e-05 | -0.0041742 | 0.19714 | -0.0067014 | 0.059526 | 0.070391 | 0.0018863 | -0.0089573 | 60.2692 | 60.4523 | -0.027466 | -61.3678 | 60.1547 | -61.3083 | -61.2579 | -61.0336 | 0.022888 | -61.5189 | 60.1593 | 60.1273 | -61.2488 | -61.4044 | -0.054932 | -0.004578 | -0.15106 | 121.7056 | -0.11444 | -0.10986 | -0.036621 | 0.004578 | -0.15106 | -0.14648 | 0.21973 | -0.2655 | -0.11444 | -0.17853 | 121.4081 | 121.5225 | 61.2259 | -121.5637 | 121.4127 | 121.3806 | 61.2762 | -121.7102
441.9062 | 121.9482 | -61.2671 | 60.2829 | 0.14771 | 0.013657 | 0.072076 | 0.064711 | 0.12824 | -0.00089518 | -0.003106 | 0.19714 | -0.005847 | 0.061876 | 0.074023 | 0.0065859 | -0.0083163 | 60.1913 | 60.3561 | -0.10529 | -61.4365 | 60.1913 | -61.3495 | -61.3083 | -61.0703 | -0.022888 | -61.5509 | 60.1593 | 60.1364 | -61.2259 | -61.3998 | -0.082397 | -0.041199 | -0.091553 | 121.6232 | -0.16937 | -0.12817 | -0.091553 | 0.041199 | -0.13275 | -0.1236 | 0.19684 | -0.28381 | -0.15106 | -0.14648 | 121.4584 | 121.4584 | 61.1618 | -121.5912 | 121.4264 | 121.4035 | 61.2442 | -121.6827
443.5781 | 121.8796 | -61.2167 | 60.3973 | 0.08667 | 0.012162 | 0.071863 | 0.06642 | 0.1293 | -0.0053812 | -0.0063104 | 0.17426 | -0.0071286 | 0.059953 | 0.068255 | 0.00039091 | -0.0070345 | 60.228 | 60.4706 | 0.022888 | -61.3724 | 60.1547 | -61.2808 | -61.2396 | -61.0199 | 0.073242 | -61.4777 | 60.2325 | 60.1868 | -61.1755 | -61.377 | -0.064087 | -0.022888 | -0.24262 | 121.6873 | -0.15564 | -0.13275 | -0.16937 | 0.041199 | -0.16022 | -0.1648 | 0.19684 | -0.26093 | -0.10071 | -0.21057 | 121.3715 | 121.4447 | 61.2396 | -121.637 | 121.4493 | 121.4035 | 61.29 | -121.7743
445.3125 | 121.9116 | -61.1938 | 60.4019 | -0.1651 | 0.014298 | 0.07229 | 0.066206 | 0.12845 | -0.006022 | -0.0058832 | -0.1004 | -0.0073422 | 0.063371 | 0.071245 | -3.629e-05 | -0.0085299 | 60.3607 | 60.5804 | 0.25635 | -61.2671 | 60.2692 | -61.1893 | -61.203 | -60.9329 | 0.30212 | -61.3861 | 60.2921 | 60.2509 | -61.1206 | -61.29 | 0.004578 | -0.009155 | -0.13275 | 121.7743 | -0.073242 | -0.064087 | -0.041199 | 0.073243 | -0.09613 | -0.10986 | 0.26093 | -0.19226 | -0.09613 | -0.15106 | 121.463 | 121.5546 | 61.4502 | -121.6049 | 121.4859 | 121.4447 | 61.496 | -121.6919
446.9844 | 121.8292 | -61.2854 | 60.3104 | -0.096436 | 0.020066 | 0.071222 | 0.066847 | 0.13059 | 0.0031638 | -0.005456 | -0.092773 | -0.005847 | 0.064653 | 0.0721 | 0.0033817 | -0.012162 | 60.2737 | 60.4156 | 0.054932 | -61.377 | 60.2234 | -61.2991 | -61.2488 | -61.0611 | 0.091553 | -61.5509 | 60.2325 | 60.1913 | -61.2534 | -61.3815 | -0.013733 | 0.036621 | -0.086975 | 121.701 | -0.091553 | -0.12817 | -0.036621 | 0.032043 | -0.096131 | -0.07782 | 0.2243 | -0.2655 | -0.16937 | -0.11902 | 121.5088 | 121.5591 | 61.3403 | -121.5591 | 121.5179 | 121.4767 | 61.377 | -121.6919
448.7344 | 121.7972 | -61.3449 | 60.3012 | 0.0027468 | 0.016861 | 0.072931 | 0.058943 | 0.12888 | 0.0031638 | -0.002038 | 0.021668 | -0.004138 | 0.061876 | 0.071245 | 0.0063723 | -0.0095981 | 60.1685 | 60.3516 | -0.059509 | -61.4502 | 60.1868 | -61.3495 | -61.2808 | -61.1526 | -0.050354 | -61.6379 | 60.2188 | 60.1822 | -61.2762 | -61.4136 | -0.004577 | 0.064087 | -0.11444 | 121.6965 | -0.10529 | -0.16937 | -0.13275 | 0.068665 | -0.068664 | -0.082397 | 0.19226 | -0.29297 | -0.2243 | -0.11902 | 121.5317 | 121.5134 | 61.2854 | -121.582 | 121.5637 | 121.5271 | 61.2946 | -121.7148
450.5 | 121.8567 | -61.2534 | 60.347 | -0.18799 | 0.013871 | 0.074426 | 0.065565 | 0.12759 | -0.0021768 | -0.0028924 | -0.14618 | -0.0043516 | 0.059099 | 0.070818 | 0.0018863 | -0.0066073 | 60.2188 | 60.4294 | 0.082397 | -61.3586 | 60.2783 | -61.2762 | -61.2442 | -61.0657 | 0.15564 | -61.5417 | 60.2829 | 60.2371 | -61.1847 | -61.3724 | -0.022888 | 0.009155 | -0.068665 | 121.6827 | -0.10529 | -0.11444 | -0.12817 | 0.068665 | -0.11902 | -0.064087 | 0.18768 | -0.28839 | -0.16937 | -0.10986 | 121.5317 | 121.4722 | 61.3358 | -121.5912 | 121.5363 | 121.4905 | 61.409 | -121.7194
452.1719 | 121.9345 | -61.2946 | 60.26 | 0.094299 | 0.014725 | 0.072931 | 0.064497 | 0.12866 | -0.00025418 | -0.0024652 | 0.19714 | -0.006915 | 0.061021 | 0.072314 | 0.0027407 | -0.0087435 | 60.1547 | 60.347 | -0.11902 | -61.4502 | 60.1776 | -61.3312 | -61.3037 | -61.0794 | -0.036621 | -61.5646 | 60.1776 | 60.1273 | -61.2625 | -61.3998 | -0.036621 | -0.009155 | -0.082398 | 121.6415 | -0.15564 | -0.14648 | -0.10529 | 0.032044 | -0.10529 | -0.082398 | 0.21515 | -0.27008 | -0.16479 | -0.13275 | 121.4722 | 121.4493 | 61.1755 | -121.5637 | 121.4722 | 121.4218 | 61.2579 | -121.6599
453.9062 | 121.8018 | -61.3266 | 60.3058 | -0.012512 | 0.014298 | 0.071222 | 0.065565 | 0.12845 | 0.0020956 | -0.003106 | 0.029297 | -0.005847 | 0.063585 | 0.073382 | 0.0033817 | -0.0078891 | 60.173 | 60.3607 | -0.045776 | -61.4502 | 60.2188 | -61.3083 | -61.3083 | -61.1755 | -0.045776 | -61.6241 | 60.2188 | 60.1868 | -61.2534 | -61.4548 | 0.01831 | 0.01831 | -0.086975 | 121.6873 | -0.1236 | -0.14191 | -0.13275 | 0.073242 | -0.12817 | -0.086975 | 0.15106 | -0.29755 | -0.16937 | -0.11902 | 121.5454 | 121.4996 | 61.2808 | -121.6141 | 121.5454 | 121.5134 | 61.2808 | -121.7606
455.6562 | 121.9116 | -61.2213 | 60.3653 | -0.012512 | 0.011948 | 0.073145 | 0.065779 | 0.13059 | -0.00944 | -0.0058832 | 0.159 | -0.0064878 | 0.060167 | 0.06975 | -0.00046349 | -0.0085299 | 60.2097 | 60.4752 | 0.050354 | -61.3495 | 60.2325 | -61.2534 | -61.2076 | -61.0382 | 0.09613 | -61.4822 | 60.2234 | 60.1959 | -61.1618 | -61.3724 | -0.032044 | 0.013732 | -0.13275 | 121.6965 | -0.12817 | -0.14191 | -0.15564 | 0.059509 | -0.15106 | -0.14191 | 0.18311 | -0.26093 | -0.10986 | -0.16937 | 121.4539 | 121.431 | 61.2717 | -121.5729 | 121.4447 | 121.4172 | 61.3174 | -121.7377
457.4062 | 121.8613 | -61.2808 | 60.3516 | -0.088806 | 0.017929 | 0.071863 | 0.065992 | 0.1308 | -0.0019632 | -0.0028924 | -0.077515 | -0.0043516 | 0.063585 | 0.071032 | 0.0014591 | -0.0098117 | 60.26 | 60.4248 | 0.059509 | -61.3815 | 60.2142 | -61.2991 | -61.2717 | -61.0748 | 0.10071 | -61.5417 | 60.2234 | 60.1959 | -61.2213 | -61.3815 | -0.01831 | 0.009156 | -0.13733 | 121.7056 | -0.10071 | -0.10986 | -0.091552 | 0.05951 | -0.10071 | -0.12817 | 0.20599 | -0.26093 | -0.16022 | -0.15564 | 121.4951 | 121.5408 | 61.3403 | -121.6232 | 121.5042 | 121.4767 | 61.3815 | -121.7331
459.1562 | 121.9666 | -61.1801 | 60.3928 | -0.058289 | 0.014725 | 0.072504 | 0.067488 | 0.1293 | -0.0075174 | -0.004815 | 0.014038 | -0.0067014 | 0.061021 | 0.072954 | -0.0032407 | -0.0083163 | 60.2829 | 60.5072 | 0.14648 | -61.29 | 60.2509 | -61.2396 | -61.203 | -60.9558 | 0.23804 | -61.3815 | 60.2692 | 60.2646 | -61.1252 | -61.2946 | -0.059509 | -0.022888 | -0.14191 | 121.6873 | -0.10986 | -0.086975 | -0.10986 | 0.054932 | -0.11444 | -0.1236 | 0.2243 | -0.20142 | -0.086975 | -0.12817 | 121.431 | 121.463 | 61.3266 | -121.5958 | 121.4493 | 121.4447 | 61.4182 | -121.6873
460.8438 | 121.8201 | -61.3037 | 60.3287 | 0.056152 | 0.017075 | 0.072931 | 0.063643 | 0.13059 | 0.0012412 | -0.0043878 | 0.082703 | -0.0056332 | 0.062303 | 0.071673 | 0.0055179 | -0.0089573 | 60.1456 | 60.3149 | -0.10529 | -61.4548 | 60.2142 | -61.322 | -61.3083 | -61.1984 | -0.086975 | -61.6745 | 60.2097 | 60.1685 | -61.2671 | -61.4594 | -0.01831 | -0.004578 | -0.11444 | 121.6187 | -0.15106 | -0.14648 | -0.1831 | 0.036621 | -0.15564 | -0.11902 | 0.10529 | -0.37079 | -0.21515 | -0.16022 | 121.5179 | 121.4493 | 61.1984 | -121.637 | 121.5134 | 121.4722 | 61.2167 | -121.788
462.5938 | 121.9391 | -61.2671 | 60.2875 | 0.10956 | 0.015152 | 0.072076 | 0.060652 | 0.12845 | -0.00025418 | -0.0035334 | 0.19714 | -0.0049924 | 0.061021 | 0.070605 | 0.0063723 | -0.0083163 | 60.1776 | 60.3516 | -0.10071 | -61.4548 | 60.1639 | -61.3266 | -61.3174 | -61.0794 | -0.032043 | -61.5646 | 60.2051 | 60.1593 | -61.2305 | -61.409 | -0.059509 | -0.050354 | -0.1236 | 121.6187 | -0.18768 | -0.13733 | -0.10986 | 0.036621 | -0.14191 | -0.082398 | 0.18768 | -0.29755 | -0.15564 | -0.12817 | 121.431 | 121.4447 | 61.1664 | -121.6049 | 121.4722 | 121.4264 | 61.235 | -121.6965
464.2656 | 121.8567 | -61.203 | 60.4294 | -0.19562 | 0.014725 | 0.075067 | 0.066633 | 0.12824 | -0.0081582 | -0.0043878 | -0.0088499 | -0.007556 | 0.062303 | 0.069536 | -0.00024989 | -0.0068209 | 60.3287 | 60.5988 | 0.24261 | -61.2579 | 60.26 | -61.2122 | -61.1572 | -60.9604 | 0.29755 | -61.4136 | 60.2417 | 60.2646 | -61.1206 | -61.3129 | -0.009155 | 0.045776 | -0.16937 | 121.8018 | -0.054932 | -0.10071 | -0.10071 | 0.082398 | -0.10986 | -0.18768 | 0.24262 | -0.21057 | -0.10071 | -0.16479 | 121.463 | 121.5317 | 61.4456 | -121.5866 | 121.4447 | 121.4676 | 61.5005 | -121.7422
466.0156 | 121.8658 | -61.3083 | 60.2966 | 0.10956 | 0.014725 | 0.073785 | 0.064711 | 0.12952 | 0.00038662 | -0.002038 | 0.13611 | -0.004138 | 0.061021 | 0.071459 | 0.0053043 | -0.0091709 | 60.141 | 60.3012 | -0.15106 | -61.4868 | 60.1959 | -61.3266 | -61.3083 | -61.1481 | -0.09613 | -61.6287 | 60.228 | 60.173 | -61.2762 | -61.441 | -0.01831 | 0 | -0.10071 | 121.6095 | -0.17853 | -0.17853 | -0.15564 | 0.032044 | -0.13275 | -0.068665 | 0.16022 | -0.32043 | -0.18768 | -0.1236 | 121.5042 | 121.4493 | 61.1572 | -121.6049 | 121.5363 | 121.4813 | 61.2122 | -121.7377
467.7031 | 121.9437 | -61.1618 | 60.379 | -0.081177 | 0.012162 | 0.07464 | 0.064497 | 0.12824 | -0.0075174 | -0.0035334 | 0.021668 | -0.0071286 | 0.059953 | 0.071459 | -3.629e-05 | -0.0061801 | 60.3287 | 60.5438 | 0.1831 | -61.2625 | 60.26 | -61.203 | -61.1938 | -60.9421 | 0.26093 | -61.3815 | 60.26 | 60.2234 | -61.1343 | -61.322 | -0.041199 | -0.032044 | -0.11902 | 121.7056 | -0.10071 | -0.068664 | -0.050354 | 0.027466 | -0.16022 | -0.11902 | 0.21973 | -0.21973 | -0.05951 | -0.15564 | 121.4218 | 121.4905 | 61.3449 | -121.5729 | 121.4218 | 121.3852 | 61.4227 | -121.701
469.4531 | 121.9574 | -61.2762 | 60.2875 | 0.10956 | 0.017075 | 0.072076 | 0.064711 | 0.12994 | 0.00081382 | -0.0041742 | 0.20477 | -0.0067014 | 0.064012 | 0.072954 | 0.0033817 | -0.0087435 | 60.1913 | 60.3378 | -0.11444 | -61.441 | 60.2005 | -61.3495 | -61.322 | -61.1023 | -0.045776 | -61.5692 | 60.2051 | 60.1318 | -61.2671 | -61.3998 | -0.073242 | -0.045776 | -0.086976 | 121.6141 | -0.16479 | -0.11902 | -0.096131 | 0.009155 | -0.1236 | -0.082398 | 0.17395 | -0.29297 | -0.16937 | -0.15564 | 121.4767 | 121.4676 | 61.1618 | -121.6095 | 121.4813 | 121.4081 | 61.2305 | -121.6873
471.2031 | 121.907 | -61.2259 | 60.3561 | 0.13245 | 0.012802 | 0.073999 | 0.065779 | 0.12952 | -0.0036722 | -0.0043878 | 0.2124 | -0.007556 | 0.062303 | 0.0721 | 0.0027407 | -0.0087435 | 60.2509 | 60.4797 | 0.013733 | -61.377 | 60.1685 | -61.29 | -61.2259 | -61.0062 | 0.050354 | -61.4914 | 60.2005 | 60.1593 | -61.2259 | -61.3815 | -0.064087 | 0 | -0.18768 | 121.7056 | -0.15106 | -0.15106 | -0.10529 | 0 | -0.15564 | -0.15564 | 0.21973 | -0.2655 | -0.10986 | -0.19684 | 121.3943 | 121.4767 | 61.2396 | -121.582 | 121.4264 | 121.3852 | 61.2762 | -121.7377
472.9375 | 121.9345 | -61.2625 | 60.2966 | 0.10956 | 0.014298 | 0.074854 | 0.060865 | 0.12759 | -0.00089518 | -0.003747 | 0.22766 | -0.007556 | 0.061449 | 0.071886 | 0.0061587 | -0.0076755 | 60.2554 | 60.4568 | -0.018311 | -61.3632 | 60.1547 | -61.29 | -61.2808 | -61.0382 | 0.032043 | -61.5143 | 60.141 | 60.1181 | -61.2396 | -61.4044 | -0.027466 | -0.018311 | -0.14191 | 121.7194 | -0.10071 | -0.082397 | -0.041199 | 0.022888 | -0.14191 | -0.15564 | 0.2243 | -0.25177 | -0.10986 | -0.17853 | 121.4172 | 121.5179 | 61.2442 | -121.5775 | 121.4035 | 121.3806 | 61.2946 | -121.701
474.6719 | 121.9208 | -61.29 | 60.3104 | 0.10193 | 0.016434 | 0.073145 | 0.068342 | 0.12824 | -0.00046778 | -0.002038 | 0.11322 | -0.004138 | 0.061662 | 0.069536 | 0.0042361 | -0.0081027 | 60.1501 | 60.3287 | -0.12817 | -61.4548 | 60.1959 | -61.3312 | -61.2854 | -61.1343 | -0.086975 | -61.615 | 60.2142 | 60.1639 | -61.2671 | -61.4182 | -0.041199 | 0.004578 | -0.11444 | 121.6187 | -0.1648 | -0.16937 | -0.16022 | 0.022888 | -0.12817 | -0.096131 | 0.15564 | -0.32501 | -0.19684 | -0.14648 | 121.4859 | 121.4401 | 61.1618 | -121.5958 | 121.5042 | 121.4539 | 61.203 | -121.7285
476.3594 | 121.8567 | -61.2579 | 60.347 | -0.18036 | 0.017289 | 0.071222 | 0.066206 | 0.1308 | 0.0010276 | -0.003106 | -0.15381 | -0.0028562 | 0.063371 | 0.071459 | 0.0020999 | -0.010239 | 60.2371 | 60.4431 | 0.10071 | -61.3541 | 60.2783 | -61.2808 | -61.2488 | -61.0748 | 0.12817 | -61.5555 | 60.2692 | 60.2417 | -61.2076 | -61.3815 | -0.022888 | 0.009156 | -0.068665 | 121.7011 | -0.09613 | -0.10529 | -0.10986 | 0.050354 | -0.1236 | -0.07782 | 0.18311 | -0.29755 | -0.17395 | -0.10529 | 121.5363 | 121.4951 | 61.3586 | -121.5958 | 121.5271 | 121.4996 | 61.3861 | -121.7285
478.1094 | 121.8109 | -61.322 | 60.3287 | -0.081177 | 0.016434 | 0.070154 | 0.065565 | 0.12888 | 0.00017302 | -0.0033196 | -0.0012209 | -0.0045652 | 0.061876 | 0.070177 | 0.0027407 | -0.0078891 | 60.2463 | 60.4065 | 0.027466 | -61.3907 | 60.2097 | -61.3174 | -61.2625 | -61.1206 | 0.004578 | -61.5875 | 60.1959 | 60.2005 | -61.235 | -61.4136 | 0.004577 | 0.059509 | -0.11902 | 121.7285 | -0.068665 | -0.12817 | -0.082397 | 0.086975 | -0.091553 | -0.13275 | 0.20142 | -0.2655 | -0.17395 | -0.12817 | 121.5317 | 121.5683 | 61.3495 | -121.5912 | 121.5179 | 121.5225 | 61.3266 | -121.7422
479.8594 | 121.9528 | -61.1755 | 60.3928 | -0.088806 | 0.013657 | 0.075922 | 0.066847 | 0.12909 | -0.010722 | -0.0039606 | 0.014038 | -0.0084104 | 0.060808 | 0.069964 | -0.0017453 | -0.0072483 | 60.2875 | 60.5484 | 0.17853 | -61.2946 | 60.2463 | -61.2076 | -61.1938 | -60.9421 | 0.24719 | -61.3861 | 60.2554 | 60.2417 | -61.1572 | -61.3083 | -0.032044 | -0.018311 | -0.14648 | 121.7239 | -0.11902 | -0.10071 | -0.10529 | 0.01831 | -0.13275 | -0.13733 | 0.23346 | -0.21057 | -0.077819 | -0.15106 | 121.4218 | 121.463 | 61.3541 | -121.5866 | 121.431 | 121.4172 | 61.4227 | -121.7011
481.5469 | 121.9254 | -61.2579 | 60.2875 | 0.094299 | 0.01558 | 0.071863 | 0.064497 | 0.12845 | -0.00046778 | -0.002038 | 0.19714 | -0.0060606 | 0.061235 | 0.071245 | 0.0042361 | -0.0087435 | 60.173 | 60.3516 | -0.10986 | -61.4639 | 60.1822 | -61.3403 | -61.3129 | -61.1023 | -0.054932 | -61.5875 | 60.2051 | 60.1364 | -61.2625 | -61.409 | -0.082397 | -0.054931 | -0.10529 | 121.6095 | -0.20599 | -0.15106 | -0.11444 | -0.004577 | -0.15106 | -0.082398 | 0.15564 | -0.32959 | -0.17853 | -0.15106 | 121.4401 | 121.431 | 61.1481 | -121.6003 | 121.463 | 121.3943 | 61.203 | -121.6965
483.2969 | 121.8338 | -61.3083 | 60.3104 | 0.033264 | 0.018784 | 0.073785 | 0.063856 | 0.12824 | -4.058e-05 | -0.0039606 | 0.075073 | -0.0032834 | 0.062303 | 0.071886 | 0.0048769 | -0.0074619 | 60.1456 | 60.3149 | -0.10071 | -61.4639 | 60.2234 | -61.3495 | -61.29 | -61.1755 | -0.091553 | -61.647 | 60.1959 | 60.141 | -61.2854 | -61.4456 | -0.041198 | 0.018311 | -0.086975 | 121.6232 | -0.15564 | -0.17395 | -0.16479 | 0.022889 | -0.13733 | -0.11444 | 0.13275 | -0.33874 | -0.20142 | -0.16937 | 121.5317 | 121.4539 | 61.2076 | -121.6003 | 121.5042 | 121.4493 | 61.2167 | -121.756
485.0469 | 121.8613 | -61.2488 | 60.3836 | -0.23376 | 0.015152 | 0.076349 | 0.067915 | 0.13059 | -0.0040994 | -0.0028924 | -0.14618 | -0.0054196 | 0.063158 | 0.071673 | 0.0020999 | -0.0091709 | 60.2509 | 60.4523 | 0.11902 | -61.3495 | 60.3104 | -61.2625 | -61.2213 | -61.084 | 0.16022 | -61.528 | 60.3287 | 60.2463 | -61.171 | -61.3358 | -0.013733 | 0.027466 | -0.073242 | 121.7011 | -0.10071 | -0.12817 | -0.13275 | 0.07782 | -0.086975 | -0.054932 | 0.16479 | -0.27924 | -0.19226 | -0.13733 | 121.5591 | 121.4996 | 61.3678 | -121.6049 | 121.5775 | 121.4951 | 61.409 | -121.7194
486.7344 | 121.9437 | -61.1618 | 60.4019 | -0.11932 | 0.014511 | 0.073358 | 0.067701 | 0.12717 | -0.0098672 | -0.0028924 | 0.014038 | -0.0077696 | 0.063585 | 0.071673 | -0.0028135 | -0.010239 | 60.3333 | 60.5621 | 0.21057 | -61.2717 | 60.2737 | -61.1801 | -61.1847 | -60.9467 | 0.26093 | -61.3907 | 60.228 | 60.2325 | -61.116 | -61.3037 | -0.018311 | -0.022888 | -0.12817 | 121.7239 | -0.10986 | -0.086975 | -0.068665 | 0.045776 | -0.14191 | -0.17395 | 0.21515 | -0.22888 | -0.086975 | -0.16937 | 121.4355 | 121.4951 | 61.3724 | -121.5866 | 121.3898 | 121.3943 | 61.4227 | -121.7056
488.4844 | 121.8109 | -61.2396 | 60.434 | -0.18036 | 0.015793 | 0.073358 | 0.067701 | 0.12888 | -0.003245 | -0.004815 | -0.11566 | -0.0079832 | 0.064653 | 0.071459 | -0.00046349 | -0.0095981 | 60.3195 | 60.5576 | 0.21973 | -61.2762 | 60.26 | -61.2122 | -61.1755 | -60.9787 | 0.27466 | -61.4365 | 60.2921 | 60.2875 | -61.1526 | -61.3266 | 0.027466 | 0.064087 | -0.17395 | 121.7972 | -0.036621 | -0.10071 | -0.11444 | 0.086975 | -0.086975 | -0.14191 | 0.26093 | -0.19684 | -0.10986 | -0.14648 | 121.4996 | 121.5591 | 61.4594 | -121.6095 | 121.5317 | 121.5271 | 61.5143 | -121.7606
490.25 | 121.9345 | -61.1938 | 60.4202 | 0.0027468 | 0.016434 | 0.072931 | 0.06706 | 0.13016 | -0.0058084 | -0.0067376 | 0.13611 | -0.006915 | 0.061449 | 0.070605 | -0.0015317 | -0.0081027 | 60.2463 | 60.4614 | 0.059509 | -61.3449 | 60.2234 | -61.2534 | -61.2213 | -61.0291 | 0.11902 | -61.4822 | 60.2371 | 60.2234 | -61.1664 | -61.3449 | -0.059509 | -0.027465 | -0.19684 | 121.6553 | -0.15106 | -0.1236 | -0.17395 | 0.027466 | -0.15106 | -0.1831 | 0.1648 | -0.28839 | -0.13733 | -0.19684 | 121.4172 | 121.4401 | 61.2534 | -121.6415 | 121.431 | 121.4172 | 61.3129 | -121.7651
492 | 121.8613 | -61.2076 | 60.4248 | -0.19562 | 0.015366 | 0.073785 | 0.064497 | 0.12994 | -0.0034586 | -0.0046014 | -0.092773 | -0.0079832 | 0.060808 | 0.070605 | -0.00024989 | -0.011521 | 60.3516 | 60.5804 | 0.2655 | -61.2717 | 60.2463 | -61.2167 | -61.1526 | -60.9512 | 0.29297 | -61.4136 | 60.2554 | 60.2325 | -61.1618 | -61.2991 | -0.009155 | 0.054932 | -0.17853 | 121.788 | -0.064086 | -0.11902 | -0.073243 | 0.045777 | -0.091552 | -0.16937 | 0.25635 | -0.20599 | -0.11444 | -0.19226 | 121.4539 | 121.5591 | 61.4731 | -121.5775 | 121.463 | 121.4401 | 61.5005 | -121.7239
493.75 | 121.8384 | -61.2122 | 60.3973 | -0.18799 | 0.014939 | 0.074426 | 0.067274 | 0.13101 | -0.001536 | -0.0056696 | -0.085144 | -0.0079832 | 0.063371 | 0.072954 | 0.0014591 | -0.0087435 | 60.3424 | 60.5713 | 0.24261 | -61.2808 | 60.26 | -61.2076 | -61.1755 | -60.9512 | 0.29297 | -61.4182 | 60.2554 | 60.2097 | -61.1526 | -61.3174 | 0.004577 | 0.036621 | -0.13733 | 121.7834 | -0.068665 | -0.10529 | -0.054932 | 0.059509 | -0.10529 | -0.14191 | 0.26093 | -0.20599 | -0.10071 | -0.18768 | 121.4722 | 121.5546 | 61.4548 | -121.5729 | 121.4676 | 121.4218 | 61.5051 | -121.7148
495.5 | 121.8109 | -61.3449 | 60.3058 | 0.056152 | 0.020279 | 0.071436 | 0.064283 | 0.12845 | 0.0027364 | -0.003747 | 0.029297 | -0.0039244 | 0.061235 | 0.072741 | 0.0065859 | -0.011521 | 60.1639 | 60.3378 | -0.091553 | -61.4685 | 60.228 | -61.3495 | -61.3083 | -61.1481 | -0.050354 | -61.6425 | 60.2234 | 60.1868 | -61.2625 | -61.441 | -0.004577 | 0.036621 | -0.07782 | 121.6827 | -0.1236 | -0.16022 | -0.14191 | 0.082398 | -0.09613 | -0.082397 | 0.19684 | -0.29755 | -0.20142 | -0.11902 | 121.5729 | 121.5088 | 61.2534 | -121.6141 | 121.5683 | 121.5317 | 61.2946 | -121.7468
497.1875 | 121.8658 | -61.2671 | 60.347 | -0.18036 | 0.019425 | 0.073145 | 0.065138 | 0.12973 | 0.00038662 | -0.0026788 | -0.13092 | -0.005206 | 0.061449 | 0.072527 | 0.0055179 | -0.0083163 | 60.2463 | 60.434 | 0.082397 | -61.3541 | 60.2783 | -61.2808 | -61.2488 | -61.084 | 0.13275 | -61.5463 | 60.2646 | 60.2097 | -61.2213 | -61.3815 | -0.013733 | 0.018311 | -0.068665 | 121.7011 | -0.086975 | -0.10529 | -0.10071 | 0.045777 | -0.11444 | -0.082398 | 0.18311 | -0.27924 | -0.16479 | -0.13733 | 121.5454 | 121.5134 | 61.3495 | -121.5958 | 121.5317 | 121.4767 | 61.3998 | -121.7285
498.9219 | 121.8109 | -61.2213 | 60.3973 | -0.23376 | 0.017929 | 0.072931 | 0.068342 | 0.12866 | -0.004313 | -0.0041742 | -0.085144 | -0.007556 | 0.06273 | 0.072527 | -0.00089089 | -0.0076755 | 60.2234 | 60.498 | 0.17395 | -61.3358 | 60.2783 | -61.2305 | -61.2213 | -61.0382 | 0.19226 | -61.5051 | 60.2875 | 60.2966 | -61.1801 | -61.3495 | -0.009156 | 0 | -0.11902 | 121.7194 | -0.11444 | -0.11444 | -0.17395 | 0.041198 | -0.12817 | -0.10986 | 0.18311 | -0.28381 | -0.15564 | -0.10071 | 121.4996 | 121.4447 | 61.3953 | -121.6187 | 121.5088 | 121.5179 | 61.4136 | -121.7468
500.6719 | 121.9528 | -61.1847 | 60.3699 | -0.14221 | 0.014511 | 0.075708 | 0.065138 | 0.12695 | -0.0087992 | -0.0058832 | -0.0012209 | -0.0064878 | 0.060594 | 0.070605 | -3.629e-05 | -0.0072483 | 60.3333 | 60.585 | 0.20142 | -61.2808 | 60.2554 | -61.2076 | -61.203 | -60.9238 | 0.29297 | -61.377 | 60.2417 | 60.2463 | -61.1526 | -61.3083 | -0.022889 | -0.018311 | -0.11444 | 121.7697 | -0.096131 | -0.07782 | -0.036621 | 0.032043 | -0.1236 | -0.12817 | 0.26093 | -0.19226 | -0.068664 | -0.1236 | 121.4401 | 121.5179 | 61.3861 | -121.5729 | 121.4264 | 121.431 | 61.4777 | -121.6782
502.3594 | 121.8887 | -61.2396 | 60.3561 | 0.079041 | 0.01558 | 0.073999 | 0.06407 | 0.12888 | -0.004954 | -0.0026788 | 0.16663 | -0.0054196 | 0.060594 | 0.06975 | 0.0035953 | -0.0078891 | 60.2509 | 60.4797 | 0.036621 | -61.3724 | 60.1959 | -61.2671 | -61.2305 | -61.0245 | 0.091553 | -61.4868 | 60.2142 | 60.1913 | -61.1893 | -61.3586 | -0.027466 | 0.009155 | -0.16022 | 121.7194 | -0.13275 | -0.14191 | -0.10529 | 0.050354 | -0.11902 | -0.14191 | 0.21515 | -0.24719 | -0.12817 | -0.1648 | 121.4355 | 121.4905 | 61.2762 | -121.5866 | 121.4539 | 121.431 | 61.3312 | -121.7148
504.125 | 121.7926 | -61.3037 | 60.3333 | -0.081177 | 0.016434 | 0.071436 | 0.064283 | 0.12824 | 0.0016684 | -0.003106 | -0.062256 | -0.003497 | 0.06273 | 0.074023 | 0.0031681 | -0.010453 | 60.2692 | 60.4294 | 0.032043 | -61.3953 | 60.2325 | -61.29 | -61.2762 | -61.084 | 0.064087 | -61.5784 | 60.2509 | 60.1868 | -61.2488 | -61.4044 | 0.013733 | 0.027466 | -0.10071 | 121.7331 | -0.091553 | -0.11902 | -0.064087 | 0.054932 | -0.10071 | -0.082398 | 0.21973 | -0.27466 | -0.17395 | -0.14648 | 121.5363 | 121.5729 | 61.3358 | -121.6095 | 121.5546 | 121.4905 | 61.3678 | -121.7377
505.8125 | 121.9025 | -61.2259 | 60.3607 | 0.071411 | 0.013657 | 0.074426 | 0.065138 | 0.12824 | -0.0034586 | -0.0035334 | 0.18188 | -0.0081968 | 0.063371 | 0.070818 | 0.00039091 | -0.0068209 | 60.2509 | 60.4935 | 0.041199 | -61.3815 | 60.228 | -61.2579 | -61.2259 | -61.0245 | 0.091553 | -61.4914 | 60.2051 | 60.1868 | -61.1984 | -61.3678 | -0.032044 | 0 | -0.13275 | 121.7194 | -0.15564 | -0.15564 | -0.10986 | 0.027466 | -0.14191 | -0.15564 | 0.20142 | -0.2655 | -0.1236 | -0.17395 | 121.4539 | 121.4767 | 61.2671 | -121.5866 | 121.431 | 121.4127 | 61.3174 | -121.7285
507.5625 | 121.8109 | -61.3403 | 60.3287 | -0.020142 | 0.017929 | 0.071222 | 0.066206 | 0.12952 | 0.001882 | -0.0024652 | 0.044556 | -0.005206 | 0.062089 | 0.072314 | 0.0053043 | -0.010666 | 60.2005 | 60.3561 | -0.059509 | -61.441 | 60.2005 | -61.3174 | -61.3129 | -61.1526 | -0.050354 | -61.6516 | 60.2051 | 60.1639 | -61.2946 | -61.4365 | 0.022888 | 0.027466 | -0.12817 | 121.6965 | -0.10071 | -0.12817 | -0.12817 | 0.045776 | -0.09613 | -0.1236 | 0.18768 | -0.31128 | -0.21515 | -0.16479 | 121.5408 | 121.5408 | 61.2808 | -121.6415 | 121.5454 | 121.5042 | 61.29 | -121.7651
509.2344 | 121.962 | -61.1618 | 60.3882 | -0.088806 | 0.014511 | 0.07464 | 0.067915 | 0.12759 | -0.0081582 | -0.0052424 | -0.0012209 | -0.0073422 | 0.06273 | 0.071459 | -0.0013181 | -0.0074619 | 60.3058 | 60.5804 | 0.15564 | -61.2808 | 60.2417 | -61.2213 | -61.203 | -60.9467 | 0.25635 | -61.3724 | 60.2692 | 60.2463 | -61.1206 | -61.3266 | -0.059509 | -0.041199 | -0.14649 | 121.7422 | -0.11902 | -0.07782 | -0.082398 | 0.041199 | -0.1648 | -0.11902 | 0.21515 | -0.21057 | -0.045776 | -0.14191 | 121.4035 | 121.4676 | 61.3174 | -121.5912 | 121.431 | 121.4081 | 61.4182 | -121.7148
510.9844 | 121.8475 | -61.2579 | 60.3699 | -0.17273 | 0.014511 | 0.070795 | 0.070051 | 0.12973 | -0.001536 | -0.005456 | -0.16907 | -0.0039244 | 0.062303 | 0.072954 | 0.0025271 | -0.010453 | 60.2463 | 60.4111 | 0.091553 | -61.3632 | 60.2966 | -61.2808 | -61.2259 | -61.0703 | 0.15564 | -61.5372 | 60.3195 | 60.2371 | -61.1893 | -61.3724 | -0.022888 | 0.032044 | -0.073242 | 121.669 | -0.10528 | -0.13733 | -0.1236 | 0.068665 | -0.11444 | -0.050354 | 0.18768 | -0.27923 | -0.1648 | -0.13275 | 121.5546 | 121.5042 | 61.3495 | -121.5958 | 121.5775 | 121.4951 | 61.4136 | -121.7422
512.75 | 121.8155 | -61.2305 | 60.4111 | -0.23376 | 0.013016 | 0.072931 | 0.06706 | 0.12973 | -0.0045266 | -0.0050286 | -0.10803 | -0.0062742 | 0.063158 | 0.070605 | 0.0012455 | -0.0074619 | 60.2325 | 60.4889 | 0.15106 | -61.3495 | 60.2783 | -61.235 | -61.2442 | -61.0565 | 0.1831 | -61.5143 | 60.3058 | 60.2737 | -61.2076 | -61.322 | -0.004577 | -0.013733 | -0.13275 | 121.7194 | -0.11902 | -0.10529 | -0.17853 | 0.022888 | -0.091552 | -0.10529 | 0.17395 | -0.28381 | -0.19226 | -0.13733 | 121.5088 | 121.463 | 61.3815 | -121.6553 | 121.5363 | 121.5042 | 61.4136 | -121.7331
514.4375 | 121.8292 | -61.3174 | 60.3104 | -0.088806 | 0.015366 | 0.070795 | 0.064283 | 0.12973 | 0.0010276 | -0.0028924 | -0.077515 | -0.005206 | 0.063798 | 0.071245 | 0.0078677 | -0.0098117 | 60.2325 | 60.434 | 0.064087 | -61.3907 | 60.26 | -61.3083 | -61.2579 | -61.0703 | 0.10071 | -61.5555 | 60.2325 | 60.1776 | -61.235 | -61.409 | 0.009155 | 0.059509 | -0.050354 | 121.7514 | -0.073242 | -0.13275 | -0.07782 | 0.082398 | -0.091553 | -0.07782 | 0.24719 | -0.23804 | -0.14648 | -0.13275 | 121.5775 | 121.55 | 61.3815 | -121.5683 | 121.55 | 121.4951 | 61.4182 | -121.7194
516.1875 | 121.8658 | -61.3037 | 60.2737 | 0.094299 | 0.014939 | 0.071863 | 0.064497 | 0.12589 | -0.001536 | -0.0026788 | 0.12848 | -0.0028562 | 0.061235 | 0.072954 | 0.0042361 | -0.0081027 | 60.1318 | 60.3104 | -0.13733 | -61.4594 | 60.2051 | -61.3449 | -61.3266 | -61.1526 | -0.091553 | -61.6287 | 60.1822 | 60.1822 | -61.2762 | -61.4456 | -0.041199 | -0.022888 | -0.068665 | 121.6141 | -0.15564 | -0.13275 | -0.14191 | 0.027466 | -0.14191 | -0.091553 | 0.15106 | -0.32501 | -0.1831 | -0.091553 | 121.5088 | 121.4355 | 61.1664 | -121.6003 | 121.4859 | 121.4859 | 61.2122 | -121.7194
517.9375 | 121.9391 | -61.2579 | 60.2692 | 0.15533 | 0.013871 | 0.071222 | 0.063215 | 0.13144 | -0.003245 | -0.003106 | 0.20477 | -0.0067014 | 0.062089 | 0.0721 | 0.0042361 | -0.0081027 | 60.2234 | 60.4568 | -0.041199 | -61.3953 | 60.1593 | -61.322 | -61.2991 | -61.0519 | 0.022888 | -61.5051 | 60.1639 | 60.1364 | -61.2442 | -61.409 | -0.064086 | -0.041198 | -0.10986 | 121.7148 | -0.13733 | -0.096131 | -0.045776 | 0.013733 | -0.15106 | -0.10529 | 0.20599 | -0.24719 | -0.09613 | -0.13275 | 121.4172 | 121.4813 | 61.2167 | -121.5683 | 121.4218 | 121.3943 | 61.2808 | -121.6782
519.6875 | 121.8613 | -61.2808 | 60.3607 | -0.18036 | 0.018997 | 0.071436 | 0.069624 | 0.12952 | -4.058e-05 | -0.0043878 | -0.12329 | -0.0064878 | 0.063585 | 0.072741 | 0.0023135 | -0.011094 | 60.2371 | 60.4294 | 0.09613 | -61.3541 | 60.2875 | -61.2671 | -61.2305 | -61.0886 | 0.14191 | -61.5372 | 60.2737 | 60.2188 | -61.235 | -61.3953 | 0.013733 | 0.050354 | -0.073242 | 121.7102 | -0.073242 | -0.1236 | -0.1236 | 0.045777 | -0.11444 | -0.086975 | 0.19226 | -0.25635 | -0.14191 | -0.14191 | 121.5683 | 121.5179 | 61.377 | -121.5912 | 121.5546 | 121.4996 | 61.4227 | -121.756
521.375 | 121.9299 | -61.2213 | 60.379 | 0.010376 | 0.015793 | 0.072717 | 0.067915 | 0.13037 | -0.008372 | -0.0063104 | 0.159 | -0.0077696 | 0.06273 | 0.071459 | -0.00024989 | -0.0057529 | 60.2142 | 60.4843 | 0.059509 | -61.3586 | 60.228 | -61.2396 | -61.2305 | -61.0611 | 0.10529 | -61.4731 | 60.228 | 60.2371 | -61.1893 | -61.3815 | -0.018311 | -0.009156 | -0.15106 | 121.7056 | -0.13733 | -0.12817 | -0.16479 | 0.032043 | -0.16022 | -0.15106 | 0.16022 | -0.25177 | -0.091552 | -0.14191 | 121.4493 | 121.4355 | 61.2808 | -121.6095 | 121.4493 | 121.4584 | 61.3266 | -121.7606
523.125 | 121.8658 | -61.2762 | 60.347 | -0.14221 | 0.016861 | 0.070154 | 0.064711 | 0.12845 | 0.0012412 | -0.002038 | -0.069885 | -0.0060606 | 0.062517 | 0.075731 | 0.0023135 | -0.011521 | 60.2325 | 60.4248 | 0.064087 | -61.3678 | 60.2646 | -61.2946 | -61.2808 | -61.0703 | 0.11902 | -61.5417 | 60.2646 | 60.2234 | -61.2213 | -61.377 | -0.018311 | -0.004578 | -0.082398 | 121.7011 | -0.091553 | -0.086975 | -0.11444 | 0.054932 | -0.10071 | -0.082398 | 0.20599 | -0.2655 | -0.16479 | -0.1236 | 121.5408 | 121.5088 | 61.3403 | -121.6278 | 121.5408 | 121.4996 | 61.3953 | -121.7239
524.8125 | 121.9528 | -61.171 | 60.4065 | -0.17273 | 0.017502 | 0.073785 | 0.068983 | 0.1293 | -0.0073038 | -0.006524 | 0.014038 | -0.0084104 | 0.06273 | 0.070391 | -0.00024989 | -0.0051119 | 60.3058 | 60.5804 | 0.18768 | -61.2762 | 60.2509 | -61.2305 | -61.1938 | -60.9283 | 0.26093 | -61.377 | 60.2509 | 60.2142 | -61.1618 | -61.3174 | -0.05951 | -0.022889 | -0.15564 | 121.7514 | -0.10529 | -0.082397 | -0.10071 | 0.009155 | -0.14648 | -0.15564 | 0.24261 | -0.20599 | -0.059509 | -0.19226 | 121.4218 | 121.4767 | 61.3586 | -121.6003 | 121.4218 | 121.3852 | 61.4319 | -121.7239
526.5625 | 121.8018 | -61.2991 | 60.3195 | 0.056152 | 0.017289 | 0.072076 | 0.064497 | 0.13101 | 0.00081382 | -0.0016108 | 0.067444 | -0.004138 | 0.063371 | 0.06975 | 0.0055179 | -0.0087435 | 60.141 | 60.3333 | -0.10529 | -61.4685 | 60.2325 | -61.3403 | -61.2946 | -61.1801 | -0.09613 | -61.6837 | 60.2005 | 60.1776 | -61.2762 | -61.4639 | -0.041199 | 0.004577 | -0.086975 | 121.6324 | -0.16937 | -0.17395 | -0.17853 | 0.022888 | -0.1648 | -0.11902 | 0.11902 | -0.38452 | -0.21973 | -0.14191 | 121.5317 | 121.4401 | 61.1938 | -121.6141 | 121.4996 | 121.4767 | 61.203 | -121.7834
528.2969 | 121.9345 | -61.2717 | 60.26 | 0.14008 | 0.014939 | 0.075922 | 0.061934 | 0.12695 | -0.0023904 | -0.0016108 | 0.18188 | -0.005847 | 0.057817 | 0.06975 | 0.0029543 | -0.0066073 | 60.228 | 60.4294 | -0.032043 | -61.3907 | 60.1822 | -61.2991 | -61.29 | -61.0474 | 0.022888 | -61.5143 | 60.173 | 60.141 | -61.2579 | -61.4044 | -0.027466 | -0.018311 | -0.07782 | 121.701 | -0.11902 | -0.10071 | -0.032044 | 0.013732 | -0.13275 | -0.086975 | 0.2243 | -0.24262 | -0.10986 | -0.11902 | 121.4539 | 121.4996 | 61.2396 | -121.55 | 121.4447 | 121.4127 | 61.2946 | -121.6644
529.9688 | 121.8292 | -61.2305 | 60.4431 | -0.18036 | 0.017075 | 0.074213 | 0.067488 | 0.12845 | -0.006022 | -0.0043878 | -0.1004 | -0.006915 | 0.060594 | 0.069964 | -0.00024989 | -0.0083163 | 60.3058 | 60.5484 | 0.22888 | -61.29 | 60.2692 | -61.2122 | -61.203 | -61.0062 | 0.2655 | -61.441 | 60.2921 | 60.2829 | -61.1572 | -61.3266 | 0.018311 | 0.027466 | -0.17395 | 121.7789 | -0.059509 | -0.086975 | -0.13733 | 0.073242 | -0.09613 | -0.15106 | 0.2243 | -0.21057 | -0.11444 | -0.16022 | 121.4996 | 121.5363 | 61.4594 | -121.6461 | 121.5225 | 121.5134 | 61.496 | -121.7697
531.7188 | 121.8979 | -61.2259 | 60.3516 | 0.063782 | 0.011948 | 0.073999 | 0.06407 | 0.13016 | -0.0064492 | -0.004815 | 0.16663 | -0.006915 | 0.059312 | 0.070177 | 0.0014591 | -0.0081027 | 60.2554 | 60.4797 | 0.032043 | -61.3724 | 60.2142 | -61.2717 | -61.2167 | -61.0428 | 0.064087 | -61.496 | 60.2188 | 60.1776 | -61.1938 | -61.3632 | -0.045776 | 0.009155 | -0.13733 | 121.7056 | -0.14648 | -0.15564 | -0.09613 | 0.032043 | -0.13733 | -0.13275 | 0.1831 | -0.27008 | -0.13275 | -0.17395 | 121.4401 | 121.4813 | 61.2579 | -121.5683 | 121.4447 | 121.4035 | 61.29 | -121.7148
533.4531 | 121.9254 | -61.3037 | 60.2829 | 0.094299 | 0.015152 | 0.07229 | 0.06706 | 0.12802 | 0.0014548 | -0.006524 | 0.11322 | -0.004138 | 0.06273 | 0.072741 | 0.0035953 | -0.0087435 | 60.1822 | 60.3241 | -0.1236 | -61.4594 | 60.2142 | -61.3358 | -61.3037 | -61.1252 | -0.082397 | -61.6196 | 60.2188 | 60.1913 | -61.2396 | -61.4273 | -0.032043 | 0 | -0.068665 | 121.6278 | -0.15564 | -0.15564 | -0.10071 | 0.064087 | -0.1236 | -0.064087 | 0.17853 | -0.31586 | -0.19226 | -0.091553 | 121.5179 | 121.4859 | 61.1801 | -121.5866 | 121.5225 | 121.4951 | 61.2213 | -121.7102
535.2031 | 121.8658 | -61.2671 | 60.347 | -0.19562 | 0.017929 | 0.073145 | 0.068342 | 0.12824 | -0.001536 | -0.003106 | -0.13092 | -0.0056332 | 0.061662 | 0.069964 | 0.0044497 | -0.012162 | 60.2646 | 60.4294 | 0.091553 | -61.3449 | 60.2875 | -61.2762 | -61.2671 | -61.0794 | 0.11902 | -61.5417 | 60.2921 | 60.2509 | -61.2213 | -61.3724 | -0.009155 | 0 | -0.059509 | 121.6965 | -0.07782 | -0.07782 | -0.082398 | 0.045777 | -0.10528 | -0.054932 | 0.18768 | -0.27466 | -0.16937 | -0.096131 | 121.5546 | 121.5317 | 61.3586 | -121.6141 | 121.5591 | 121.5179 | 61.3861 | -121.7194
536.8906 | 121.9162 | -61.1847 | 60.3973 | -0.012512 | 0.015366 | 0.071436 | 0.069624 | 0.12567 | -0.0062356 | -0.0046014 | 0.14374 | -0.0073422 | 0.063798 | 0.073595 | -0.0013181 | -0.0076755 | 60.2417 | 60.466 | 0.059509 | -61.3403 | 60.228 | -61.2442 | -61.1984 | -61.0291 | 0.10529 | -61.4685 | 60.2325 | 60.2234 | -61.1526 | -61.3403 | -0.05951 | -0.013733 | -0.16937 | 121.6507 | -0.15564 | -0.14191 | -0.15564 | 0.032043 | -0.15564 | -0.1648 | 0.15564 | -0.28381 | -0.12817 | -0.17395 | 121.4127 | 121.4264 | 61.2442 | -121.5958 | 121.4172 | 121.4081 | 61.29 | -121.7377
538.6406 | 121.9437 | -61.1847 | 60.4156 | -0.12695 | 0.01622 | 0.071436 | 0.067701 | 0.12973 | -0.0068766 | -0.0043878 | -0.0012209 | -0.007556 | 0.063585 | 0.073168 | -0.0021725 | -0.0083163 | 60.3378 | 60.5759 | 0.21057 | -61.2808 | 60.2325 | -61.2122 | -61.1847 | -60.9055 | 0.28381 | -61.3495 | 60.2463 | 60.228 | -61.1389 | -61.2991 | -0.027466 | 0 | -0.18311 | 121.7606 | -0.096131 | -0.096131 | -0.077819 | 0.045776 | -0.11444 | -0.16937 | 0.27923 | -0.1648 | -0.050354 | -0.18768 | 121.4172 | 121.5225 | 61.3953 | -121.6003 | 121.431 | 121.4127 | 61.4685 | -121.7148
540.3906 | 121.8979 | -61.1938 | 60.4156 | -0.18036 | 0.017075 | 0.074426 | 0.06706 | 0.12781 | -0.0038858 | -0.0052424 | -0.092773 | -0.0081968 | 0.062303 | 0.069536 | 0.00081811 | -0.0095981 | 60.3653 | 60.5896 | 0.24261 | -61.2717 | 60.2737 | -61.2076 | -61.1755 | -60.9467 | 0.28839 | -61.4044 | 60.2646 | 60.26 | -61.1526 | -61.2946 | -0.013733 | 0.018311 | -0.14191 | 121.7834 | -0.077819 | -0.09613 | -0.050354 | 0.041199 | -0.10071 | -0.15106 | 0.24719 | -0.21057 | -0.10986 | -0.15564 | 121.4676 | 121.5591 | 61.4365 | -121.5912 | 121.4584 | 121.4539 | 61.4822 | -121.7102
542.0938 | 121.9528 | -61.1938 | 60.3928 | -0.14221 | 0.016434 | 0.074854 | 0.066847 | 0.12888 | -0.0036722 | -0.0046014 | 0.0064086 | -0.0088376 | 0.061449 | 0.0721 | 0.0018863 | -0.0091709 | 60.3424 | 60.585 | 0.20142 | -61.2946 | 60.2692 | -61.1984 | -61.171 | -60.91 | 0.27466 | -61.3678 | 60.2692 | 60.2142 | -61.1435 | -61.3174 | -0.004577 | 0.022889 | -0.1236 | 121.7789 | -0.10071 | -0.1236 | -0.050354 | 0.050354 | -0.1236 | -0.1236 | 0.28381 | -0.17395 | -0.050354 | -0.17853 | 121.463 | 121.5363 | 61.3953 | -121.5637 | 121.463 | 121.4081 | 61.4685 | -121.7102
543.8438 | 121.8201 | -61.2167 | 60.3928 | -0.22614 | 0.017075 | 0.072717 | 0.065565 | 0.12759 | 0.00081382 | -0.0060968 | -0.16907 | -0.0049924 | 0.064012 | 0.071673 | 0.0014591 | -0.01088 | 60.2875 | 60.4614 | 0.16022 | -61.3541 | 60.2875 | -61.2717 | -61.2076 | -61.0428 | 0.17853 | -61.5189 | 60.3241 | 60.2875 | -61.1847 | -61.3541 | -0.054931 | 0.009155 | -0.10529 | 121.6782 | -0.13733 | -0.14648 | -0.10529 | 0.032044 | -0.13733 | -0.068664 | 0.17395 | -0.30212 | -0.16479 | -0.10529 | 121.5042 | 121.5042 | 61.377 | -121.6003 | 121.5408 | 121.5042 | 61.3953 | -121.7468
545.5938 | 121.7926 | -61.3037 | 60.3012 | -0.065918 | 0.017929 | 0.07229 | 0.064283 | 0.12994 | 0.003591 | -0.004815 | -0.024109 | -0.0062742 | 0.061021 | 0.072314 | 0.0046633 | -0.0091709 | 60.2417 | 60.4111 | 0 | -61.4136 | 60.2463 | -61.3037 | -61.2717 | -61.1069 | -0.013733 | -61.615 | 60.2234 | 60.1593 | -61.2808 | -61.441 | 0 | 0.032044 | -0.054931 | 121.7148 | -0.10986 | -0.14191 | -0.059509 | 0.022888 | -0.13733 | -0.077819 | 0.19684 | -0.31128 | -0.17395 | -0.14191 | 121.55 | 121.5454 | 61.3037 | -121.5729 | 121.5271 | 121.463 | 61.29 | -121.7422
547.3438 | 121.8567 | -61.2854 | 60.3378 | -0.14984 | 0.017716 | 0.071222 | 0.067701 | 0.12866 | 0.001882 | -0.003747 | -0.13855 | -0.0062742 | 0.064867 | 0.074236 | 0.0050907 | -0.0070345 | 60.2463 | 60.4431 | 0.091553 | -61.3678 | 60.2692 | -61.2991 | -61.2579 | -61.0703 | 0.13275 | -61.5417 | 60.2554 | 60.2417 | -61.2122 | -61.409 | -0.013733 | 0.027465 | -0.068665 | 121.7285 | -0.082398 | -0.10986 | -0.091553 | 0.073242 | -0.1236 | -0.082398 | 0.21515 | -0.25635 | -0.13275 | -0.096131 | 121.5546 | 121.5317 | 61.377 | -121.5958 | 121.5408 | 121.5271 | 61.4182 | -121.7468
549.0938 | 121.9391 | -61.2579 | 60.26 | 0.14771 | 0.016861 | 0.071436 | 0.062361 | 0.12567 | -0.0011088 | -0.0011834 | 0.18951 | -0.0062742 | 0.061449 | 0.070391 | 0.0020999 | -0.0070345 | 60.1776 | 60.379 | -0.10071 | -61.4365 | 60.173 | -61.3266 | -61.3083 | -61.0657 | -0.004578 | -61.528 | 60.1913 | 60.141 | -61.2808 | -61.3998 | -0.068664 | -0.050354 | -0.086975 | 121.637 | -0.17853 | -0.12817 | -0.082398 | -0.022888 | -0.14191 | -0.068665 | 0.19226 | -0.27008 | -0.12817 | -0.11902 | 121.431 | 121.4355 | 61.1572 | -121.5683 | 121.4493 | 121.3989 | 61.2534 | -121.6599
550.7656 | 121.9437 | -61.1755 | 60.4111 | -0.14221 | 0.016648 | 0.071863 | 0.06706 | 0.12674 | -0.0075174 | -0.0035334 | 0.014038 | -0.0081968 | 0.062517 | 0.071459 | 0.00039091 | -0.0089573 | 60.3241 | 60.5896 | 0.20142 | -61.2717 | 60.2509 | -61.2122 | -61.1572 | -60.9329 | 0.29755 | -61.3541 | 60.2692 | 60.26 | -61.1343 | -61.3266 | -0.036621 | 0.01831 | -0.16022 | 121.7651 | -0.09613 | -0.11444 | -0.086975 | 0.041199 | -0.15106 | -0.14191 | 0.24262 | -0.17853 | -0.027466 | -0.15106 | 121.4264 | 121.4996 | 61.377 | -121.5683 | 121.4447 | 121.4355 | 61.4731 | -121.7377
552.5156 | 121.8521 | -61.29 | 60.3195 | -0.13458 | 0.015366 | 0.070581 | 0.064711 | 0.13123 | 0.0029502 | -0.0035334 | -0.092773 | -0.0067014 | 0.061235 | 0.072527 | 0.0038089 | -0.0089573 | 60.26 | 60.4385 | 0.082397 | -61.377 | 60.2463 | -61.2717 | -61.2762 | -61.0657 | 0.12817 | -61.5463 | 60.2509 | 60.2051 | -61.2259 | -61.4273 | 0.018311 | 0.013733 | -0.073242 | 121.7285 | -0.086975 | -0.10071 | -0.059509 | 0.064087 | -0.13733 | -0.068665 | 0.2243 | -0.25635 | -0.11902 | -0.11444 | 121.5363 | 121.55 | 61.3724 | -121.5958 | 121.5408 | 121.4951 | 61.4182 | -121.7468
554.2656 | 121.8109 | -61.322 | 60.3333 | -0.073547 | 0.014725 | 0.071863 | 0.062788 | 0.13037 | 0.0020956 | -0.0035334 | -0.0088499 | -0.0060606 | 0.059953 | 0.070818 | 0.0046633 | -0.0070345 | 60.2463 | 60.4248 | 0.018311 | -61.3953 | 60.2417 | -61.29 | -61.29 | -61.1069 | 0.036621 | -61.5875 | 60.2234 | 60.173 | -61.2717 | -61.4227 | 0.032043 | 0.032043 | -0.091553 | 121.7468 | -0.073243 | -0.10529 | -0.086975 | 0.050354 | -0.10071 | -0.10986 | 0.21515 | -0.2655 | -0.1648 | -0.16022 | 121.5637 | 121.5683 | 61.3403 | -121.6232 | 121.5454 | 121.4951 | 61.3586 | -121.756
555.9531 | 121.9437 | -61.2534 | 60.2737 | 0.10193 | 0.013871 | 0.073145 | 0.065992 | 0.12802 | -0.003245 | -0.0016108 | 0.20477 | -0.005847 | 0.062089 | 0.070177 | 0.0044497 | -0.0087435 | 60.1593 | 60.3607 | -0.1236 | -61.4456 | 60.2005 | -61.3449 | -61.322 | -61.0977 | -0.041199 | -61.5738 | 60.1822 | 60.1318 | -61.2625 | -61.409 | -0.091553 | -0.068664 | -0.073243 | 121.6141 | -0.19226 | -0.1236 | -0.11444 | -0.009155 | -0.15564 | -0.091553 | 0.15564 | -0.32043 | -0.16479 | -0.14191 | 121.4539 | 121.4127 | 61.1298 | -121.5958 | 121.4355 | 121.3852 | 61.2122 | -121.6827
557.7031 | 121.9116 | -61.2579 | 60.347 | 0.071411 | 0.011734 | 0.073999 | 0.065351 | 0.12567 | -0.006022 | -0.0035334 | 0.25055 | -0.0094786 | 0.06273 | 0.070605 | 0.0027407 | -0.0051119 | 60.2463 | 60.4935 | 0.027466 | -61.3815 | 60.173 | -61.2717 | -61.2717 | -61.0245 | 0.068665 | -61.4822 | 60.1685 | 60.173 | -61.1984 | -61.3586 | -0.013732 | -0.013732 | -0.17395 | 121.7514 | -0.1236 | -0.10986 | -0.10071 | 0.05951 | -0.10071 | -0.17853 | 0.23346 | -0.2243 | -0.1236 | -0.17395 | 121.431 | 121.5042 | 61.2854 | -121.6187 | 121.4264 | 121.431 | 61.3266 | -121.7056
559.3906 | 121.962 | -61.1664 | 60.3607 | -0.012512 | 0.01622 | 0.073358 | 0.070478 | 0.12824 | -0.0068766 | -0.0046014 | 0.097962 | -0.0081968 | 0.061449 | 0.071459 | -0.0017453 | -0.0089573 | 60.2417 | 60.466 | 0.082397 | -61.3403 | 60.2692 | -61.2396 | -61.2259 | -61.0245 | 0.14191 | -61.4502 | 60.2417 | 60.2463 | -61.1755 | -61.3541 | -0.073242 | -0.059509 | -0.091553 | 121.6324 | -0.17395 | -0.11444 | -0.11902 | -0.009155 | -0.18768 | -0.11902 | 0.14191 | -0.28381 | -0.09613 | -0.11444 | 121.4355 | 121.4081 | 61.2488 | -121.5866 | 121.4081 | 121.4127 | 61.3083 | -121.7148
561.1406 | 121.8796 | -61.2534 | 60.3561 | -0.15747 | 0.020279 | 0.071008 | 0.069197 | 0.13144 | 0.0023092 | -0.0058832 | -0.1767 | -0.0067014 | 0.063585 | 0.072741 | 0.0027407 | -0.012162 | 60.2509 | 60.4248 | 0.091553 | -61.3449 | 60.2875 | -61.2717 | -61.2167 | -61.0794 | 0.13733 | -61.5555 | 60.2875 | 60.2554 | -61.2122 | -61.377 | -0.01831 | 0.036621 | -0.068664 | 121.6782 | -0.091553 | -0.12817 | -0.10529 | 0.041199 | -0.1236 | -0.068664 | 0.17395 | -0.30212 | -0.17853 | -0.10071 | 121.5408 | 121.5042 | 61.3449 | -121.5729 | 121.5408 | 121.5088 | 61.3907 | -121.7331
562.875 | 121.8018 | -61.3083 | 60.3104 | -0.065918 | 0.018784 | 0.071863 | 0.063429 | 0.12824 | 0.001882 | -0.002038 | -0.031738 | -0.0054196 | 0.063585 | 0.072314 | 0.0048769 | -0.0087435 | 60.2554 | 60.4385 | 0.027466 | -61.3861 | 60.2463 | -61.2717 | -61.2671 | -61.1023 | 0.054932 | -61.5784 | 60.2097 | 60.228 | -61.2579 | -61.4044 | 0.036622 | 0.041199 | -0.064087 | 121.7468 | -0.077819 | -0.11902 | -0.054932 | 0.050354 | -0.09613 | -0.10071 | 0.20599 | -0.27008 | -0.17395 | -0.082398 | 121.5546 | 121.5637 | 61.3358 | -121.5775 | 121.5179 | 121.5363 | 61.3632 | -121.7148
564.625 | 121.8292 | -61.3174 | 60.3195 | 0.025635 | 0.015793 | 0.070367 | 0.063643 | 0.12952 | 0.00081382 | -0.0018244 | 0.10559 | -0.0064878 | 0.064653 | 0.071886 | 0.0020999 | -0.0081027 | 60.141 | 60.2921 | -0.1236 | -61.4639 | 60.2142 | -61.3541 | -61.3037 | -61.171 | -0.082397 | -61.6516 | 60.1868 | 60.1685 | -61.2854 | -61.4319 | -0.036621 | 0.013733 | -0.10529 | 121.6095 | -0.14648 | -0.16022 | -0.17853 | 0.032044 | -0.11444 | -0.13275 | 0.14648 | -0.33417 | -0.21973 | -0.15106 | 121.5317 | 121.4584 | 61.1938 | -121.6232 | 121.5042 | 121.4859 | 61.235 | -121.7514
566.375 | 121.9528 | -61.1893 | 60.3607 | 0.0027468 | 0.016434 | 0.073785 | 0.068769 | 0.1261 | -0.00944 | -0.007165 | 0.11322 | -0.0067014 | 0.064012 | 0.069323 | -0.0011045 | -0.0072483 | 60.2188 | 60.4935 | 0.073242 | -61.3358 | 60.2097 | -61.2671 | -61.2167 | -61.0291 | 0.13733 | -61.4456 | 60.2325 | 60.2142 | -61.1938 | -61.3449 | -0.07782 | -0.027466 | -0.15106 | 121.6827 | -0.14648 | -0.11902 | -0.14191 | -0.004578 | -0.15564 | -0.12817 | 0.16022 | -0.25635 | -0.10071 | -0.14648 | 121.3989 | 121.4081 | 61.2625 | -121.5775 | 121.4218 | 121.4035 | 61.3266 | -121.7056
568.0625 | 121.8292 | -61.3174 | 60.3287 | 0.040894 | 0.017929 | 0.071008 | 0.064924 | 0.12994 | 0.001882 | -0.003106 | 0.12848 | -0.0054196 | 0.064653 | 0.074236 | 0.0035953 | -0.0093845 | 60.1456 | 60.3012 | -0.11902 | -61.4777 | 60.2051 | -61.3541 | -61.3083 | -61.1618 | -0.09613 | -61.6425 | 60.2142 | 60.1822 | -61.2946 | -61.4502 | -0.036621 | 0.009155 | -0.1236 | 121.6187 | -0.16022 | -0.16937 | -0.1831 | 0.022888 | -0.13275 | -0.11444 | 0.15564 | -0.32501 | -0.19226 | -0.14648 | 121.5225 | 121.463 | 61.1984 | -121.637 | 121.5317 | 121.4996 | 61.2213 | -121.7789
569.75 | 121.8384 | -61.2442 | 60.4111 | -0.21088 | 0.015366 | 0.073145 | 0.06941 | 0.13037 | -0.0040994 | -0.0069512 | -0.16144 | -0.0062742 | 0.061876 | 0.071032 | -3.629e-05 | -0.0083163 | 60.2417 | 60.4385 | 0.12817 | -61.3632 | 60.3104 | -61.2534 | -61.235 | -61.084 | 0.16937 | -61.5189 | 60.3241 | 60.2921 | -61.1847 | -61.3083 | -0.009155 | 0.009156 | -0.10071 | 121.6827 | -0.11902 | -0.12817 | -0.16937 | 0.05951 | -0.064087 | -0.086975 | 0.16022 | -0.27466 | -0.21057 | -0.11902 | 121.5546 | 121.4859 | 61.3724 | -121.6461 | 121.5683 | 121.5363 | 61.4136 | -121.7194
571.5 | 121.8292 | -61.2991 | 60.2966 | 0.056152 | 0.016434 | 0.069513 | 0.063643 | 0.12973 | 0.0014548 | -0.003106 | 0.059815 | -0.005206 | 0.06273 | 0.073809 | 0.0029543 | -0.0074619 | 60.1501 | 60.3149 | -0.082397 | -61.4594 | 60.228 | -61.3266 | -61.3129 | -61.1893 | -0.082397 | -61.6608 | 60.2417 | 60.1959 | -61.2762 | -61.409 | -0.027466 | -0.013733 | -0.068665 | 121.6141 | -0.16022 | -0.14648 | -0.14648 | 0.022888 | -0.10986 | -0.054932 | 0.10986 | -0.36163 | -0.25177 | -0.10071 | 121.5271 | 121.4493 | 61.2167 | -121.6095 | 121.5408 | 121.4951 | 61.2167 | -121.7056
573.25 | 121.8567 | -61.3266 | 60.2783 | 0.071411 | 0.014298 | 0.072931 | 0.063429 | 0.12866 | -0.00089518 | -0.003747 | 0.17426 | -0.0043516 | 0.062517 | 0.073168 | 0.0046633 | -0.0076755 | 60.1273 | 60.3058 | -0.13733 | -61.4731 | 60.1959 | -61.3358 | -61.2946 | -61.1481 | -0.10529 | -61.6425 | 60.1959 | 60.1959 | -61.2946 | -61.4365 | -0.009155 | 0.032043 | -0.082397 | 121.6324 | -0.14648 | -0.17853 | -0.15106 | 0.032043 | -0.10986 | -0.082397 | 0.17853 | -0.31586 | -0.20599 | -0.082397 | 121.5225 | 121.4539 | 61.1893 | -121.5729 | 121.5225 | 121.5225 | 61.2213 | -121.7148
575 | 121.9391 | -61.171 | 60.3699 | -0.13458 | 0.014725 | 0.074213 | 0.06706 | 0.12866 | -0.0079446 | -0.0033196 | -0.0012209 | -0.0099058 | 0.061021 | 0.071459 | -3.629e-05 | -0.0068209 | 60.3287 | 60.5896 | 0.22888 | -61.2808 | 60.2325 | -61.2259 | -61.1801 | -60.9329 | 0.29755 | -61.3541 | 60.2509 | 60.2554 | -61.1664 | -61.3129 | -0.054932 | -0.009156 | -0.13733 | 121.7606 | -0.10986 | -0.10071 | -0.041199 | 0.004577 | -0.14191 | -0.11902 | 0.23804 | -0.18311 | -0.041199 | -0.11444 | 121.4035 | 121.4996 | 61.3998 | -121.55 | 121.4218 | 121.4264 | 61.4685 | -121.6827
576.75 | 121.8521 | -61.2534 | 60.3699 | -0.21088 | 0.016434 | 0.072076 | 0.067915 | 0.13037 | -0.00068138 | -0.0035334 | -0.16907 | -0.004138 | 0.064439 | 0.074236 | 0.00017731 | -0.0083163 | 60.2371 | 60.4385 | 0.10071 | -61.3449 | 60.3195 | -61.2488 | -61.2122 | -61.0931 | 0.14191 | -61.5326 | 60.2783 | 60.2554 | -61.2076 | -61.377 | 0.004578 | 0.041199 | -0.050354 | 121.6919 | -0.091553 | -0.13275 | -0.13275 | 0.045776 | -0.1236 | -0.091553 | 0.16022 | -0.27924 | -0.15564 | -0.11444 | 121.5729 | 121.4905 | 61.3541 | -121.582 | 121.5317 | 121.5088 | 61.3953 | -121.7468
578.4375 | 121.8933 | -61.2213 | 60.3653 | 0.040894 | 0.014939 | 0.073358 | 0.064711 | 0.12994 | -0.0062356 | -0.0073786 | 0.15137 | -0.0077696 | 0.063798 | 0.070177 | -0.00067729 | -0.0076755 | 60.2234 | 60.4797 | 0.050354 | -61.377 | 60.2325 | -61.2488 | -61.2396 | -61.0291 | 0.073242 | -61.4822 | 60.2325 | 60.2097 | -61.1893 | -61.3586 | -0.027466 | -0.018311 | -0.13275 | 121.701 | -0.15564 | -0.13733 | -0.14191 | 0.032043 | -0.13733 | -0.13275 | 0.19226 | -0.26093 | -0.1236 | -0.15564 | 121.4539 | 121.4447 | 61.2717 | -121.6049 | 121.4539 | 121.431 | 61.2946 | -121.7239
580.1875 | 121.8704 | -61.2625 | 60.3653 | -0.18799 | 0.018784 | 0.07229 | 0.06642 | 0.13101 | -4.058e-05 | -0.0039606 | -0.14618 | -0.0047788 | 0.064012 | 0.074023 | 0.0040225 | -0.010453 | 60.2554 | 60.4385 | 0.09613 | -61.3632 | 60.2921 | -61.2991 | -61.2442 | -61.0931 | 0.13275 | -61.5463 | 60.2737 | 60.228 | -61.2076 | -61.3998 | -0.036621 | 0.01831 | -0.073242 | 121.7011 | -0.10071 | -0.11902 | -0.10986 | 0.054931 | -0.13733 | -0.091552 | 0.16937 | -0.28381 | -0.14648 | -0.13733 | 121.5546 | 121.5179 | 61.3586 | -121.6095 | 121.5363 | 121.4905 | 61.3953 | -121.7651
581.9375 | 121.843 | -61.3174 | 60.3104 | 0.08667 | 0.014725 | 0.069086 | 0.06407 | 0.12781 | 0.00017302 | -0.0041742 | 0.11322 | -0.0043516 | 0.063158 | 0.074877 | 0.0029543 | -0.0095981 | 60.1364 | 60.2966 | -0.13275 | -61.4731 | 60.1822 | -61.3449 | -61.3037 | -61.1572 | -0.11444 | -61.6562 | 60.2234 | 60.2051 | -61.2762 | -61.4319 | -0.027466 | 0.013733 | -0.12817 | 121.6141 | -0.15564 | -0.16937 | -0.17395 | 0.041199 | -0.11444 | -0.086975 | 0.16022 | -0.33874 | -0.2243 | -0.10529 | 121.4996 | 121.4539 | 61.1847 | -121.6141 | 121.5408 | 121.5225 | 61.203 | -121.7422
583.6875 | 121.8658 | -61.2122 | 60.4065 | -0.18799 | 0.012162 | 0.073999 | 0.064924 | 0.13059 | -0.0064492 | -0.0056696 | -0.024109 | -0.0090512 | 0.061449 | 0.06975 | 0.00081811 | -0.0070345 | 60.3333 | 60.6033 | 0.25177 | -61.2762 | 60.2692 | -61.2076 | -61.171 | -60.9787 | 0.28381 | -61.4182 | 60.2692 | 60.2417 | -61.1618 | -61.3174 | 0.004577 | 0.041199 | -0.13733 | 121.8155 | -0.064087 | -0.10529 | -0.073242 | 0.050354 | -0.10529 | -0.13733 | 0.23346 | -0.20599 | -0.10071 | -0.1648 | 121.4813 | 121.5454 | 61.4639 | -121.5775 | 121.4813 | 121.4539 | 61.496 | -121.7239
585.3594 | 121.8292 | -61.2991 | 60.2921 | 0.056152 | 0.015366 | 0.069513 | 0.065565 | 0.12909 | -4.058e-05 | -0.0033196 | 0.11322 | -0.0030698 | 0.062517 | 0.071673 | 0.0050907 | -0.0081027 | 60.1501 | 60.2921 | -0.13733 | -61.4777 | 60.2188 | -61.3632 | -61.3358 | -61.1847 | -0.10529 | -61.6562 | 60.2051 | 60.1593 | -61.2808 | -61.4365 | -0.064087 | -0.036621 | -0.073242 | 121.5912 | -0.17853 | -0.14191 | -0.14191 | 0.01831 | -0.13733 | -0.086975 | 0.11444 | -0.35706 | -0.21973 | -0.13275 | 121.5179 | 121.4493 | 61.1618 | -121.6278 | 121.5042 | 121.4584 | 61.1938 | -121.7285
587.1094 | 121.9299 | -61.203 | 60.3745 | 0.018005 | 0.014298 | 0.074426 | 0.069197 | 0.12845 | -0.008372 | -0.0041742 | 0.15137 | -0.0084104 | 0.061662 | 0.067827 | -0.00089089 | -0.0085299 | 60.2188 | 60.4614 | 0.068665 | -61.3449 | 60.2371 | -61.2442 | -61.235 | -61.0336 | 0.11902 | -61.4685 | 60.2417 | 60.2051 | -61.1893 | -61.3449 | -0.041199 | -0.032043 | -0.13733 | 121.6644 | -0.14191 | -0.10986 | -0.15564 | 0.013733 | -0.14191 | -0.13275 | 0.16937 | -0.2655 | -0.1236 | -0.16937 | 121.4401 | 121.4218 | 61.2717 | -121.6095 | 121.4447 | 121.4081 | 61.322 | -121.7194
588.8438 | 121.9391 | -61.2717 | 60.2966 | 0.063782 | 0.016434 | 0.072504 | 0.063002 | 0.12994 | -0.00089518 | -0.0041742 | 0.22003 | -0.0037106 | 0.060808 | 0.072741 | 0.0055179 | -0.0081027 | 60.2417 | 60.4614 | -0.018311 | -61.377 | 60.1501 | -61.3174 | -61.2717 | -61.0519 | 0.013733 | -61.5143 | 60.1639 | 60.1456 | -61.2442 | -61.3861 | -0.045777 | 0 | -0.14648 | 121.7331 | -0.10529 | -0.10529 | -0.054932 | 0.027465 | -0.11444 | -0.13275 | 0.21973 | -0.24262 | -0.12817 | -0.15106 | 121.4218 | 121.5134 | 61.2534 | -121.5683 | 121.4355 | 121.4172 | 61.2854 | -121.6827
590.5781 | 121.962 | -61.1847 | 60.3745 | -0.012512 | 0.013016 | 0.073358 | 0.064924 | 0.12717 | -0.008372 | -0.0041742 | 0.11322 | -0.0073422 | 0.062089 | 0.071245 | 0.00017731 | -0.0066073 | 60.2417 | 60.466 | 0.086975 | -61.322 | 60.26 | -61.235 | -61.1893 | -61.0245 | 0.13733 | -61.4685 | 60.2554 | 60.2463 | -61.1755 | -61.3358 | -0.050354 | -0.004578 | -0.11444 | 121.6507 | -0.13733 | -0.13275 | -0.13275 | 0.009155 | -0.15106 | -0.11902 | 0.16022 | -0.28381 | -0.13275 | -0.12817 | 121.4447 | 121.4264 | 61.2717 | -121.5637 | 121.4401 | 121.431 | 61.322 | -121.7102
592.3281 | 121.9574 | -61.2579 | 60.2783 | 0.14008 | 0.013871 | 0.072076 | 0.064283 | 0.12631 | 0.00081382 | -0.0035334 | 0.18188 | -0.0054196 | 0.060808 | 0.070818 | 0.0044497 | -0.010239 | 60.2417 | 60.434 | -0.054932 | -61.4044 | 60.1593 | -61.3037 | -61.2534 | -61.0519 | 0.022888 | -61.5234 | 60.1868 | 60.1547 | -61.2534 | -61.409 | -0.045776 | 0.004578 | -0.11902 | 121.6919 | -0.14648 | -0.15106 | -0.036621 | 0.004578 | -0.15106 | -0.091552 | 0.20599 | -0.2655 | -0.11444 | -0.1236 | 121.4172 | 121.4996 | 61.203 | -121.5317 | 121.4447 | 121.4127 | 61.2808 | -121.6873
594 | 121.8384 | -61.2122 | 60.434 | -0.15747 | 0.016648 | 0.073358 | 0.07176 | 0.12759 | -0.0045266 | -0.0060968 | -0.1004 | -0.0084104 | 0.064012 | 0.071032 | 0.0014591 | -0.0091709 | 60.3149 | 60.5576 | 0.23346 | -61.29 | 60.2509 | -61.2396 | -61.1893 | -60.9924 | 0.29297 | -61.4365 | 60.2692 | 60.2737 | -61.1664 | -61.3174 | -0.027466 | 0.022888 | -0.18311 | 121.7697 | -0.07782 | -0.10071 | -0.11902 | 0.045776 | -0.10529 | -0.16479 | 0.21973 | -0.2243 | -0.11902 | -0.16022 | 121.463 | 121.5271 | 61.4456 | -121.6232 | 121.4813 | 121.4859 | 61.5051 | -121.7514
595.7344 | 121.8613 | -61.2671 | 60.3836 | -0.21851 | 0.018143 | 0.072931 | 0.069197 | 0.12802 | 0.00081382 | -0.0052424 | -0.14618 | -0.0064878 | 0.062944 | 0.072741 | 0.0029543 | -0.0098117 | 60.26 | 60.4065 | 0.10071 | -61.3586 | 60.2966 | -61.2854 | -61.2305 | -61.0931 | 0.13733 | -61.5555 | 60.3287 | 60.3058 | -61.2122 | -61.3724 | -0.01831 | 0.036621 | -0.086975 | 121.6736 | -0.091553 | -0.12817 | -0.1236 | 0.054932 | -0.10528 | -0.054932 | 0.17395 | -0.28839 | -0.18311 | -0.07782 | 121.5637 | 121.5271 | 61.3678 | -121.6141 | 121.5958 | 121.5729 | 61.4044 | -121.756
597.4219 | 121.8704 | -61.2671 | 60.3653 | -0.1651 | 0.01558 | 0.071436 | 0.065779 | 0.13165 | 0.00060022 | -0.003747 | -0.19196 | -0.0073422 | 0.061662 | 0.073382 | 0.0029543 | -0.010453 | 60.2554 | 60.4202 | 0.10529 | -61.3495 | 60.3012 | -61.2717 | -61.2488 | -61.0886 | 0.11444 | -61.5463 | 60.3104 | 60.26 | -61.2213 | -61.3953 | -0.004577 | 0.018311 | -0.064087 | 121.6873 | -0.082397 | -0.10071 | -0.10986 | 0.045777 | -0.12817 | -0.054931 | 0.17853 | -0.27924 | -0.15106 | -0.10529 | 121.5683 | 121.5225 | 61.3724 | -121.6141 | 121.5775 | 121.5271 | 61.3815 | -121.7606
599.1562 | 121.8018 | -61.3312 | 60.3149 | -0.058289 | 0.018784 | 0.070367 | 0.064924 | 0.12973 | 0.00038662 | -0.0039606 | 0.021668 | -0.0037106 | 0.063798 | 0.073595 | 0.0042361 | -0.0093845 | 60.2188 | 60.4156 | 0.009155 | -61.4044 | 60.228 | -61.2991 | -61.2717 | -61.1298 | -0.013733 | -61.6241 | 60.2325 | 60.1913 | -61.2671 | -61.4365 | 0.032044 | 0.05951 | -0.086975 | 121.7468 | -0.073242 | -0.13275 | -0.09613 | 0.064087 | -0.10529 | -0.082397 | 0.20142 | -0.29297 | -0.18768 | -0.1236 | 121.5591 | 121.55 | 61.3403 | -121.5866 | 121.5637 | 121.5225 | 61.3174 | -121.7514
600.9062 | 121.8842 | -61.2213 | 60.3516 | 0.10956 | 0.013443 | 0.071649 | 0.067488 | 0.12888 | -0.006022 | -0.0052424 | 0.20477 | -0.005206 | 0.061662 | 0.071886 | 0.00017731 | -0.0074619 | 60.228 | 60.4614 | 0.036621 | -61.3907 | 60.1685 | -61.2854 | -61.2534 | -61.0291 | 0.082397 | -61.4685 | 60.1822 | 60.2097 | -61.1893 | -61.3632 | -0.064087 | -0.032044 | -0.18311 | 121.6827 | -0.16937 | -0.13733 | -0.1236 | 0.032043 | -0.14191 | -0.16937 | 0.19226 | -0.24719 | -0.10529 | -0.14191 | 121.3898 | 121.4493 | 61.2579 | -121.6049 | 121.4035 | 121.431 | 61.3037 | -121.7148
602.5938 | 121.8796 | -61.2396 | 60.4111 | -0.21088 | 0.015366 | 0.073572 | 0.06706 | 0.1293 | -0.0036722 | -0.0039606 | -0.046997 | -0.0079832 | 0.062303 | 0.070177 | 0.00039091 | -0.0091709 | 60.3378 | 60.585 | 0.24261 | -61.2808 | 60.2646 | -61.1938 | -61.1847 | -60.965 | 0.28839 | -61.4136 | 60.2646 | 60.2417 | -61.1755 | -61.3358 | 0.045776 | 0.054932 | -0.14648 | 121.8246 | -0.041199 | -0.096131 | -0.073242 | 0.064087 | -0.09613 | -0.14648 | 0.27466 | -0.17395 | -0.07782 | -0.16937 | 121.5042 | 121.5775 | 61.4822 | -121.5958 | 121.5042 | 121.4813 | 61.528 | -121.7468
604.3281 | 121.9162 | -61.2076 | 60.379 | 0.0027468 | 0.012162 | 0.073785 | 0.065138 | 0.12717 | -0.0062356 | -0.0058832 | 0.12085 | -0.0090512 | 0.061235 | 0.071459 | -0.00067729 | -0.0076755 | 60.2417 | 60.4752 | 0.050354 | -61.3495 | 60.2188 | -61.2579 | -61.2167 | -61.0291 | 0.091553 | -61.4731 | 60.2325 | 60.2188 | -61.1938 | -61.3541 | -0.050354 | -0.009155 | -0.16022 | 121.6827 | -0.14191 | -0.13275 | -0.13733 | 0.013733 | -0.14648 | -0.14648 | 0.17853 | -0.2655 | -0.11902 | -0.16022 | 121.4264 | 121.4493 | 61.2579 | -121.5958 | 121.4401 | 121.4264 | 61.2991 | -121.7331
606 | 121.8201 | -61.2442 | 60.434 | -0.14221 | 0.018357 | 0.072931 | 0.068129 | 0.12994 | -0.003245 | -0.0067376 | -0.14618 | -0.005847 | 0.064867 | 0.071459 | 0.0018863 | -0.0083163 | 60.2646 | 60.4431 | 0.1236 | -61.3586 | 60.3058 | -61.2579 | -61.2213 | -61.0474 | 0.16937 | -61.5143 | 60.3287 | 60.2966 | -61.1984 | -61.3449 | -0.013733 | 0.022889 | -0.12817 | 121.6873 | -0.11444 | -0.13733 | -0.16937 | 0.045777 | -0.10071 | -0.10529 | 0.19684 | -0.27008 | -0.16937 | -0.13733 | 121.55 | 121.5088 | 61.3678 | -121.6553 | 121.5729 | 121.5408 | 61.4136 | -121.7789
607.75 | 121.9528 | -61.2579 | 60.2829 | 0.13245 | 0.015366 | 0.073358 | 0.062361 | 0.12909 | -0.00025418 | -0.0035334 | 0.075073 | -0.005847 | 0.06273 | 0.072527 | 0.0029543 | -0.0095981 | 60.1959 | 60.3836 | -0.050354 | -61.3998 | 60.1685 | -61.3083 | -61.2854 | -61.0428 | 0.027466 | -61.528 | 60.1868 | 60.1593 | -61.2534 | -61.4227 | -0.050354 | -0.027465 | -0.11444 | 121.6415 | -0.14191 | -0.11444 | -0.086975 | 0.004578 | -0.16479 | -0.09613 | 0.21515 | -0.27008 | -0.10529 | -0.1236 | 121.4264 | 121.4539 | 61.2076 | -121.5683 | 121.4447 | 121.4172 | 61.2854 | -121.7056
609.5 | 121.9299 | -61.2717 | 60.3012 | 0.14771 | 0.01558 | 0.06994 | 0.064924 | 0.12909 | -0.0021768 | -0.0016108 | 0.22003 | -0.0056332 | 0.063798 | 0.073595 | 0.0038089 | -0.0081027 | 60.2463 | 60.4568 | -0.018311 | -61.3724 | 60.1456 | -61.3312 | -61.2762 | -61.0382 | 0.036621 | -61.5143 | 60.173 | 60.1456 | -61.2579 | -61.4227 | -0.05951 | -0.004578 | -0.15564 | 121.7285 | -0.10071 | -0.09613 | -0.054931 | 0.013732 | -0.15106 | -0.12817 | 0.23346 | -0.24262 | -0.091553 | -0.15564 | 121.4172 | 121.5179 | 61.2534 | -121.5775 | 121.4447 | 121.4172 | 61.3083 | -121.7239
611.1875 | 121.8109 | -61.3266 | 60.3058 | -0.065918 | 0.018143 | 0.071436 | 0.06407 | 0.13059 | 0.0023092 | -0.0024652 | -0.0088499 | -0.0054196 | 0.062517 | 0.072527 | 0.0046633 | -0.010239 | 60.228 | 60.4065 | -0.004578 | -61.4227 | 60.2463 | -61.3129 | -61.29 | -61.1298 | 0.004578 | -61.615 | 60.228 | 60.2097 | -61.2579 | -61.4319 | 0.013733 | 0.036621 | -0.059509 | 121.7331 | -0.09613 | -0.13275 | -0.07782 | 0.068664 | -0.10529 | -0.07782 | 0.19684 | -0.28839 | -0.1831 | -0.09613 | 121.5729 | 121.5546 | 61.322 | -121.5958 | 121.5546 | 121.5363 | 61.3312 | -121.7377
612.9375 | 121.907 | -61.2259 | 60.3745 | 0.079041 | 0.015793 | 0.072076 | 0.066206 | 0.12952 | -0.0051676 | -0.0033196 | 0.23529 | -0.005847 | 0.061876 | 0.073382 | -0.00089089 | -0.0063937 | 60.2371 | 60.4889 | 0.022888 | -61.377 | 60.2051 | -61.2717 | -61.2396 | -61.0107 | 0.073242 | -61.4731 | 60.2234 | 60.1868 | -61.2167 | -61.3632 | -0.045776 | -0.013733 | -0.16937 | 121.7148 | -0.15106 | -0.13733 | -0.13733 | 0.009155 | -0.13733 | -0.15106 | 0.21515 | -0.24719 | -0.10986 | -0.18768 | 121.431 | 121.463 | 61.2488 | -121.6141 | 121.4493 | 121.4127 | 61.2991 | -121.7377
614.6875 | 121.875 | -61.2076 | 60.4065 | -0.17273 | 0.017929 | 0.071863 | 0.068983 | 0.12824 | -0.0038858 | -0.0039606 | -0.046997 | -0.0054196 | 0.061235 | 0.072314 | -3.629e-05 | -0.0095981 | 60.3516 | 60.5759 | 0.25635 | -61.2625 | 60.2371 | -61.1938 | -61.1847 | -60.9604 | 0.3067 | -61.4044 | 60.2692 | 60.2371 | -61.171 | -61.3358 | 0.013733 | 0.022889 | -0.16937 | 121.7834 | -0.054931 | -0.07782 | -0.054932 | 0.036622 | -0.12817 | -0.13733 | 0.24719 | -0.19684 | -0.068665 | -0.16937 | 121.4447 | 121.5591 | 61.4639 | -121.5912 | 121.4767 | 121.4447 | 61.5143 | -121.7422
616.375 | 121.8658 | -61.3129 | 60.2783 | 0.094299 | 0.01622 | 0.071649 | 0.061293 | 0.12866 | 0.00017302 | -0.0024652 | 0.13611 | -0.0026426 | 0.063371 | 0.069536 | 0.0053043 | -0.0095981 | 60.1364 | 60.3104 | -0.14191 | -61.4639 | 60.2188 | -61.3495 | -61.322 | -61.1435 | -0.10071 | -61.615 | 60.2325 | 60.1868 | -61.2854 | -61.4639 | -0.036621 | -0.009155 | -0.059509 | 121.6232 | -0.15106 | -0.14191 | -0.14191 | 0.027466 | -0.15106 | -0.045776 | 0.16937 | -0.30212 | -0.15106 | -0.091552 | 121.5317 | 121.4493 | 61.171 | -121.6003 | 121.5454 | 121.4996 | 61.2122 | -121.7422
618.125 | 121.9345 | -61.1755 | 60.3836 | -0.13458 | 0.017502 | 0.073785 | 0.068129 | 0.12952 | -0.0062356 | -0.0058832 | -0.039368 | -0.0084104 | 0.062303 | 0.070818 | 0.00039091 | -0.010025 | 60.3195 | 60.6171 | 0.23804 | -61.2671 | 60.2692 | -61.1938 | -61.1664 | -60.9421 | 0.29755 | -61.3861 | 60.2692 | 60.2554 | -61.1435 | -61.2946 | -0.018311 | 0.009155 | -0.11444 | 121.7926 | -0.091553 | -0.10071 | -0.064087 | 0.032043 | -0.11902 | -0.11444 | 0.23346 | -0.21057 | -0.091552 | -0.12817 | 121.4447 | 121.4951 | 61.4136 | -121.55 | 121.4447 | 121.431 | 61.4731 | -121.6782
619.8125 | 121.907 | -61.2213 | 60.3516 | 0.08667 | 0.011948 | 0.072504 | 0.064497 | 0.12909 | -0.003245 | -0.006524 | 0.159 | -0.0094786 | 0.060808 | 0.072954 | 0.0031681 | -0.0083163 | 60.2554 | 60.4614 | 0.013733 | -61.3724 | 60.173 | -61.2717 | -61.2305 | -61.0245 | 0.07782 | -61.4868 | 60.2417 | 60.2142 | -61.203 | -61.3632 | -0.050354 | -0.009156 | -0.17853 | 121.6827 | -0.15106 | -0.14191 | -0.09613 | 0.01831 | -0.14191 | -0.10986 | 0.19684 | -0.2655 | -0.1236 | -0.13733 | 121.3943 | 121.4767 | 61.235 | -121.582 | 121.463 | 121.4355 | 61.2991 | -121.7148
621.5625 | 121.8018 | -61.3449 | 60.3149 | 0.018005 | 0.016861 | 0.07229 | 0.060865 | 0.13059 | 0.0029502 | -0.003106 | 0.052185 | -0.0064878 | 0.059526 | 0.072954 | 0.0059451 | -0.010239 | 60.1593 | 60.3195 | -0.09613 | -61.441 | 60.2234 | -61.3358 | -61.322 | -61.1618 | -0.091553 | -61.6791 | 60.2051 | 60.1868 | -61.2991 | -61.4639 | 0.009156 | 0.022889 | -0.091552 | 121.6644 | -0.09613 | -0.11902 | -0.15564 | 0.045777 | -0.11902 | -0.10986 | 0.18311 | -0.33417 | -0.21515 | -0.12817 | 121.5683 | 121.5042 | 61.2488 | -121.637 | 121.55 | 121.5317 | 61.2534 | -121.7789
623.25 | 121.7972 | -61.3358 | 60.3149 | -0.0354 | 0.017716 | 0.074854 | 0.066633 | 0.12845 | 0.00038662 | -0.0022516 | 0.036926 | -0.0045652 | 0.061662 | 0.072954 | 0.0046633 | -0.0085299 | 60.1959 | 60.3745 | -0.027466 | -61.441 | 60.1959 | -61.322 | -61.3083 | -61.1664 | -0.032043 | -61.6425 | 60.2234 | 60.2051 | -61.2808 | -61.4685 | 0.013733 | 0.027465 | -0.11902 | 121.7102 | -0.10529 | -0.13275 | -0.11902 | 0.054931 | -0.13275 | -0.091552 | 0.16937 | -0.3067 | -0.17395 | -0.10986 | 121.5317 | 121.5317 | 61.3083 | -121.6232 | 121.5591 | 121.5408 | 61.3037 | -121.7834
624.9375 | 121.962 | -61.203 | 60.3836 | -0.0048827 | 0.014298 | 0.073999 | 0.065992 | 0.12952 | -0.0062356 | -0.0035334 | 0.12085 | -0.0079832 | 0.064012 | 0.071459 | -0.00089089 | -0.0061801 | 60.2234 | 60.4797 | 0.068665 | -61.3312 | 60.2417 | -61.2442 | -61.2305 | -61.0428 | 0.10986 | -61.4777 | 60.2417 | 60.2188 | -61.203 | -61.3541 | -0.041199 | -0.027466 | -0.14191 | 121.6827 | -0.12817 | -0.10071 | -0.16022 | 0 | -0.15106 | -0.14191 | 0.16022 | -0.27466 | -0.1236 | -0.16479 | 121.4447 | 121.4264 | 61.2717 | -121.6141 | 121.4447 | 121.4218 | 61.3129 | -121.7377
626.6875 | 121.9391 | -61.1893 | 60.3928 | 0.018005 | 0.016434 | 0.072717 | 0.068556 | 0.12845 | -0.0068766 | -0.005456 | 0.14374 | -0.0077696 | 0.063158 | 0.072527 | -3.629e-05 | -0.0081027 | 60.228 | 60.466 | 0.054932 | -61.3632 | 60.2234 | -61.2534 | -61.2076 | -61.0428 | 0.10071 | -61.4868 | 60.2417 | 60.2188 | -61.2076 | -61.3495 | -0.064087 | -0.018311 | -0.16937 | 121.6553 | -0.17395 | -0.15564 | -0.16479 | -0.018311 | -0.16022 | -0.15106 | 0.14648 | -0.29755 | -0.13733 | -0.17395 | 121.4127 | 121.4172 | 61.2442 | -121.6003 | 121.431 | 121.4081 | 61.29 | -121.7422
628.375 | 121.9208 | -61.2488 | 60.3241 | 0.14008 | 0.014939 | 0.072076 | 0.063215 | 0.12695 | -0.0019632 | -0.0043878 | 0.19714 | -0.0071286 | 0.05974 | 0.070391 | 0.0038089 | -0.0093845 | 60.2509 | 60.466 | -0.004578 | -61.377 | 60.141 | -61.3266 | -61.29 | -61.0153 | 0.041199 | -61.5005 | 60.173 | 60.1181 | -61.2442 | -61.4136 | -0.07782 | -0.041199 | -0.18311 | 121.7148 | -0.12817 | -0.086975 | -0.073243 | 0.004577 | -0.16479 | -0.15106 | 0.23346 | -0.25177 | -0.086975 | -0.20599 | 121.3898 | 121.4996 | 61.2442 | -121.6141 | 121.4218 | 121.3669 | 61.29 | -121.7377
630.125 | 121.9482 | -61.171 | 60.3836 | -0.14221 | 0.016434 | 0.07464 | 0.06706 | 0.12802 | -0.0053812 | -0.007165 | -0.0088499 | -0.0071286 | 0.06273 | 0.071032 | 0.0020999 | -0.0076755 | 60.3561 | 60.5759 | 0.2243 | -61.29 | 60.2509 | -61.2167 | -61.1893 | -60.9283 | 0.28839 | -61.3586 | 60.2509 | 60.2371 | -61.1572 | -61.3083 | -0.045777 | -0.018311 | -0.13275 | 121.7468 | -0.11902 | -0.10071 | -0.027466 | 0.013732 | -0.13733 | -0.13275 | 0.24261 | -0.18768 | -0.050354 | -0.14648 | 121.4218 | 121.5271 | 61.3953 | -121.5729 | 121.4218 | 121.4081 | 61.4594 | -121.6919
631.8125 | 121.8109 | -61.322 | 60.3378 | -0.050659 | 0.01558 | 0.06994 | 0.065565 | 0.13016 | 0.0048728 | -0.0018244 | -0.024109 | -0.005847 | 0.062303 | 0.071886 | 0.0055179 | -0.010666 | 60.2646 | 60.3973 | 0 | -61.4182 | 60.2463 | -61.3174 | -61.2946 | -61.1252 | -0.009155 | -61.6333 | 60.2325 | 60.1959 | -61.2808 | -61.4365 | 0.004577 | 0.027465 | -0.091553 | 121.7194 | -0.096131 | -0.1236 | -0.073243 | 0.041198 | -0.11444 | -0.10529 | 0.19684 | -0.31128 | -0.19684 | -0.14191 | 121.5683 | 121.5866 | 61.322 | -121.6324 | 121.5546 | 121.5179 | 61.3129 | -121.7743
633.5625 | 121.8155 | -61.3174 | 60.3378 | -0.065918 | 0.016434 | 0.073785 | 0.063643 | 0.13144 | 0.00038662 | -0.002038 | -0.039368 | -0.0047788 | 0.061449 | 0.072314 | 0.0057315 | -0.0068209 | 60.2509 | 60.4385 | 0.041199 | -61.3953 | 60.2188 | -61.3037 | -61.2808 | -61.0886 | 0.059509 | -61.5829 | 60.2417 | 60.2051 | -61.2717 | -61.4044 | 0.013733 | 0.036621 | -0.11902 | 121.756 | -0.07782 | -0.11444 | -0.086976 | 0.045777 | -0.086975 | -0.096131 | 0.22888 | -0.2655 | -0.17853 | -0.13275 | 121.5363 | 121.5683 | 61.3586 | -121.6187 | 121.5591 | 121.5225 | 61.377 | -121.7422
635.25 | 121.8933 | -61.235 | 60.3699 | 0.10193 | 0.015793 | 0.073572 | 0.066206 | 0.12909 | -0.0045266 | -0.0028924 | 0.18951 | -0.0092648 | 0.064012 | 0.071245 | 0.00039091 | -0.0087435 | 60.2371 | 60.4752 | 0.032043 | -61.3724 | 60.1913 | -61.2808 | -61.2442 | -61.0245 | 0.064087 | -61.4731 | 60.2097 | 60.1913 | -61.235 | -61.3678 | -0.045777 | -0.009156 | -0.17853 | 121.7102 | -0.13733 | -0.12817 | -0.13275 | 0 | -0.13275 | -0.16022 | 0.21057 | -0.23804 | -0.10529 | -0.17853 | 121.4264 | 121.4722 | 61.2671 | -121.6141 | 121.4447 | 121.4264 | 61.2991 | -121.7377
637 | 121.9116 | -61.2488 | 60.3104 | 0.11719 | 0.017502 | 0.070581 | 0.066633 | 0.12824 | -0.0036722 | -0.0011834 | 0.22766 | -0.005847 | 0.062303 | 0.072741 | 0.0031681 | -0.0081027 | 60.2417 | 60.4477 | -0.004578 | -61.3815 | 60.1685 | -61.3266 | -61.2762 | -61.0428 | 0.054932 | -61.5051 | 60.173 | 60.1181 | -61.2488 | -61.3907 | -0.07782 | -0.027466 | -0.14191 | 121.6965 | -0.13275 | -0.10529 | -0.068665 | 0 | -0.14191 | -0.13733 | 0.20599 | -0.25635 | -0.11444 | -0.19226 | 121.4172 | 121.4905 | 61.2442 | -121.5866 | 121.4218 | 121.3669 | 61.3037 | -121.7011
638.7656 | 121.875 | -61.2854 | 60.347 | -0.11932 | 0.016007 | 0.073572 | 0.066847 | 0.12845 | 0.00038662 | -0.0052424 | -0.1004 | -0.005847 | 0.061662 | 0.072741 | 0.0044497 | -0.0093845 | 60.2692 | 60.4385 | 0.073242 | -61.3724 | 60.2371 | -61.2762 | -61.2579 | -61.0794 | 0.11444 | -61.5372 | 60.2371 | 60.2188 | -61.2076 | -61.3907 | 0.009155 | 0.027465 | -0.10986 | 121.7239 | -0.086975 | -0.11444 | -0.07782 | 0.077819 | -0.10529 | -0.10986 | 0.20599 | -0.25177 | -0.14648 | -0.12817 | 121.5225 | 121.5546 | 61.3586 | -121.6049 | 121.5225 | 121.5042 | 61.3998 | -121.7377
640.4375 | 121.9345 | -61.2762 | 60.2783 | 0.10956 | 0.016648 | 0.074213 | 0.064711 | 0.12717 | 0.00038662 | -0.0011834 | 0.090332 | -0.006915 | 0.063158 | 0.071673 | 0.0053043 | -0.0083163 | 60.1593 | 60.3333 | -0.1236 | -61.4731 | 60.228 | -61.3266 | -61.3037 | -61.1343 | -0.068665 | -61.615 | 60.2509 | 60.1959 | -61.29 | -61.441 | -0.050354 | -0.027466 | -0.050354 | 121.6095 | -0.19684 | -0.16937 | -0.11902 | -0.013733 | -0.16479 | -0.027466 | 0.14191 | -0.33874 | -0.17395 | -0.082397 | 121.5042 | 121.4355 | 61.1526 | -121.582 | 121.5271 | 121.4722 | 61.2076 | -121.7194
642.1875 | 121.907 | -61.2213 | 60.3241 | 0.14771 | 0.014725 | 0.071222 | 0.062788 | 0.13016 | -0.0047404 | -0.0041742 | 0.22003 | -0.0062742 | 0.061449 | 0.070605 | 0.0020999 | -0.0074619 | 60.2371 | 60.4843 | 0 | -61.3724 | 60.1501 | -61.3083 | -61.2762 | -61.0291 | 0.086975 | -61.4914 | 60.1776 | 60.1593 | -61.235 | -61.3815 | -0.086976 | -0.054932 | -0.17395 | 121.7056 | -0.15106 | -0.09613 | -0.086975 | -0.013733 | -0.16022 | -0.14648 | 0.19226 | -0.27008 | -0.10986 | -0.1648 | 121.3715 | 121.4584 | 61.2213 | -121.6003 | 121.3989 | 121.3806 | 61.3083 | -121.7056
643.875 | 121.8796 | -61.2854 | 60.3836 | -0.24902 | 0.014511 | 0.072717 | 0.068769 | 0.12802 | -0.0034586 | -0.0033196 | -0.16144 | -0.0043516 | 0.061235 | 0.072314 | 0.0012455 | -0.0078891 | 60.2646 | 60.434 | 0.11444 | -61.3678 | 60.3058 | -61.2488 | -61.2259 | -61.084 | 0.15564 | -61.528 | 60.3149 | 60.3012 | -61.1938 | -61.3449 | 0.036621 | 0.059509 | -0.07782 | 121.7194 | -0.082398 | -0.14191 | -0.11902 | 0.091552 | -0.05951 | -0.068665 | 0.20142 | -0.24262 | -0.18311 | -0.082398 | 121.5912 | 121.55 | 61.3998 | -121.6095 | 121.6003 | 121.5866 | 61.441 | -121.7285
645.625 | 121.8338 | -61.2534 | 60.3973 | -0.21088 | 0.015366 | 0.074426 | 0.069197 | 0.13016 | -0.0036722 | -0.0043878 | -0.1767 | -0.0054196 | 0.062944 | 0.073382 | 0.0014591 | -0.0074619 | 60.2646 | 60.4477 | 0.14191 | -61.3724 | 60.2966 | -61.2442 | -61.2259 | -61.0657 | 0.19684 | -61.5189 | 60.3561 | 60.3058 | -61.1984 | -61.3449 | 0.009155 | 0.027466 | -0.10071 | 121.7011 | -0.11902 | -0.14648 | -0.13275 | 0.054932 | -0.091553 | -0.041199 | 0.18768 | -0.2655 | -0.17395 | -0.091553 | 121.55 | 121.5179 | 61.3953 | -121.6232 | 121.6095 | 121.5591 | 61.4502 | -121.7422
647.3125 | 121.8887 | -61.2122 | 60.4202 | -0.18036 | 0.017929 | 0.073785 | 0.064924 | 0.12973 | -0.0058084 | -0.0050286 | -0.046997 | -0.0090512 | 0.062944 | 0.069964 | -0.00046349 | -0.0093845 | 60.3195 | 60.5942 | 0.24719 | -61.2717 | 60.2646 | -61.2076 | -61.1618 | -60.9833 | 0.29297 | -61.3953 | 60.2463 | 60.2509 | -61.1389 | -61.3495 | 0.004577 | 0.050354 | -0.15564 | 121.8063 | -0.059509 | -0.10986 | -0.10071 | 0.073242 | -0.13733 | -0.17395 | 0.22888 | -0.18311 | -0.045777 | -0.16937 | 121.4767 | 121.5317 | 61.4594 | -121.582 | 121.4584 | 121.463 | 61.5051 | -121.7697
649.0625 | 121.7926 | -61.3266 | 60.3012 | -0.0354 | 0.019852 | 0.071008 | 0.06407 | 0.12674 | 0.0020956 | -0.0033196 | 0.029297 | -0.0039244 | 0.060381 | 0.073168 | 0.0057315 | -0.0098117 | 60.2005 | 60.3745 | -0.032043 | -61.441 | 60.1959 | -61.3129 | -61.3174 | -61.1572 | -0.027466 | -61.6562 | 60.2188 | 60.1639 | -61.2854 | -61.441 | 0.013733 | 0.009155 | -0.10529 | 121.7011 | -0.11444 | -0.1236 | -0.10071 | 0.041199 | -0.11444 | -0.082397 | 0.16937 | -0.32959 | -0.21515 | -0.13733 | 121.5225 | 121.5271 | 61.2946 | -121.6187 | 121.5454 | 121.4905 | 61.2991 | -121.7422
650.8125 | 121.8018 | -61.2991 | 60.3287 | -0.073547 | 0.016861 | 0.07229 | 0.063643 | 0.12802 | 0.0014548 | -0.0033196 | -0.031738 | -0.0060606 | 0.064439 | 0.071886 | 0.0023135 | -0.0078891 | 60.2325 | 60.4431 | 0.032043 | -61.3861 | 60.2325 | -61.2991 | -61.2625 | -61.0977 | 0.064087 | -61.5692 | 60.2234 | 60.1822 | -61.2488 | -61.3998 | 0 | 0.036621 | -0.09613 | 121.7422 | -0.086975 | -0.1236 | -0.09613 | 0.050354 | -0.10071 | -0.10529 | 0.20142 | -0.27008 | -0.16937 | -0.14648 | 121.5317 | 121.5317 | 61.3312 | -121.5912 | 121.5225 | 121.4813 | 61.3632 | -121.7285
652.5156 | 121.9025 | -61.2305 | 60.347 | 0.056152 | 0.01088 | 0.073572 | 0.067274 | 0.12824 | -0.0079446 | -0.0050286 | 0.15137 | -0.0092648 | 0.062089 | 0.071245 | 0.00017731 | -0.0063937 | 60.2325 | 60.4614 | 0.045776 | -61.3678 | 60.2142 | -61.2671 | -61.2396 | -61.0382 | 0.07782 | -61.4914 | 60.2463 | 60.2051 | -61.1938 | -61.3724 | -0.036621 | -0.009155 | -0.13275 | 121.6919 | -0.13733 | -0.12817 | -0.11444 | 0.036621 | -0.14191 | -0.10071 | 0.19226 | -0.26093 | -0.11902 | -0.14191 | 121.4447 | 121.463 | 61.2762 | -121.5866 | 121.4767 | 121.4355 | 61.3083 | -121.7194
654.25 | 121.962 | -61.1984 | 60.3973 | -0.10406 | 0.01622 | 0.074854 | 0.064711 | 0.12674 | -0.0087992 | -0.0052424 | 0.021668 | -0.008624 | 0.061662 | 0.070605 | -0.0013181 | -0.0081027 | 60.3058 | 60.5484 | 0.1831 | -61.2991 | 60.2783 | -61.2213 | -61.1938 | -60.9558 | 0.24261 | -61.3953 | 60.2692 | 60.2142 | -61.1526 | -61.3129 | -0.022888 | 0.004577 | -0.11902 | 121.7468 | -0.10071 | -0.10528 | -0.091553 | 0.045776 | -0.11444 | -0.12817 | 0.24261 | -0.19684 | -0.082398 | -0.18311 | 121.4767 | 121.5042 | 61.3815 | -121.5912 | 121.4676 | 121.4127 | 61.441 | -121.7102
655.9219 | 121.8567 | -61.2579 | 60.3424 | -0.22614 | 0.017929 | 0.074426 | 0.07176 | 0.12759 | -0.00046778 | -0.0035334 | -0.14618 | -0.004138 | 0.06508 | 0.070177 | 0.0014591 | -0.010453 | 60.2554 | 60.4156 | 0.10986 | -61.3632 | 60.3012 | -61.2808 | -61.2488 | -61.0886 | 0.13733 | -61.5372 | 60.3241 | 60.2829 | -61.1755 | -61.3403 | -0.022888 | 0.009156 | -0.041199 | 121.6736 | -0.10528 | -0.11444 | -0.086975 | 0.082398 | -0.082397 | -0.01831 | 0.16937 | -0.27923 | -0.19684 | -0.059509 | 121.5591 | 121.5134 | 61.3678 | -121.5912 | 121.582 | 121.5408 | 61.3953 | -121.6827
657.6562 | 121.7972 | -61.3174 | 60.3149 | -0.04303 | 0.018143 | 0.070154 | 0.065351 | 0.1293 | 0.0025228 | -0.0033196 | 0.036926 | -0.0043516 | 0.061021 | 0.073595 | 0.0035953 | -0.011094 | 60.2188 | 60.3745 | -0.013733 | -61.4182 | 60.2325 | -61.322 | -61.2991 | -61.1389 | -0.009155 | -61.6379 | 60.2509 | 60.2051 | -61.2671 | -61.4319 | -0.004577 | 0.018311 | -0.082397 | 121.6919 | -0.10071 | -0.11902 | -0.09613 | 0.050354 | -0.11444 | -0.064087 | 0.17853 | -0.32043 | -0.20599 | -0.10986 | 121.55 | 121.5363 | 61.3037 | -121.6141 | 121.5683 | 121.5225 | 61.3083 | -121.7468
659.3438 | 121.8933 | -61.2442 | 60.3745 | 0.071411 | 0.015152 | 0.069086 | 0.068342 | 0.12631 | -0.0062356 | -0.004815 | 0.18188 | -0.0084104 | 0.063158 | 0.073382 | -0.0021725 | -0.0074619 | 60.2463 | 60.4843 | 0.027466 | -61.377 | 60.2142 | -61.2534 | -61.2396 | -61.0245 | 0.068665 | -61.4868 | 60.2188 | 60.2005 | -61.1984 | -61.377 | -0.009155 | 0.004578 | -0.16022 | 121.7285 | -0.13275 | -0.13733 | -0.12817 | 0.045777 | -0.13275 | -0.15564 | 0.21973 | -0.24261 | -0.10986 | -0.17395 | 121.4584 | 121.4905 | 61.2717 | -121.6141 | 121.463 | 121.4447 | 61.3129 | -121.7514
661.0781 | 121.9162 | -61.2488 | 60.3745 | 0.12482 | 0.014511 | 0.074213 | 0.064283 | 0.12759 | -0.0064492 | -0.0056696 | 0.19714 | -0.0081968 | 0.061662 | 0.069964 | 0.0023135 | -0.0081027 | 60.2692 | 60.4935 | 0.013733 | -61.3815 | 60.1868 | -61.3083 | -61.2579 | -61.0199 | 0.059509 | -61.496 | 60.1959 | 60.1547 | -61.2259 | -61.3861 | -0.05951 | -0.009156 | -0.18768 | 121.7422 | -0.13275 | -0.1236 | -0.10529 | 0.022888 | -0.13733 | -0.17853 | 0.22888 | -0.24719 | -0.10986 | -0.21973 | 121.4355 | 121.5179 | 61.2625 | -121.6324 | 121.4447 | 121.4035 | 61.3083 | -121.7606
662.8438 | 121.8246 | -61.3358 | 60.3058 | -0.081177 | 0.014939 | 0.070581 | 0.066206 | 0.13037 | 0.00038662 | -0.0039606 | -0.069885 | -0.0030698 | 0.062517 | 0.073168 | 0.0044497 | -0.0093845 | 60.2692 | 60.4523 | 0.036621 | -61.377 | 60.2463 | -61.29 | -61.2854 | -61.0703 | 0.091553 | -61.5463 | 60.2509 | 60.2234 | -61.2259 | -61.3861 | 0.045776 | 0.050354 | -0.059509 | 121.788 | -0.041199 | -0.091553 | -0.036621 | 0.10986 | -0.050354 | -0.054932 | 0.2655 | -0.21057 | -0.16022 | -0.082397 | 121.582 | 121.6049 | 61.3724 | -121.5912 | 121.5866 | 121.5591 | 61.4273 | -121.6919
664.5156 | 121.962 | -61.2122 | 60.4019 | -0.020142 | 0.011521 | 0.074213 | 0.067488 | 0.12631 | -0.0085856 | -0.0046014 | 0.067444 | -0.0071286 | 0.062089 | 0.070391 | -3.629e-05 | -0.0078891 | 60.2417 | 60.5118 | 0.10529 | -61.3403 | 60.2371 | -61.2579 | -61.2122 | -60.997 | 0.18768 | -61.441 | 60.26 | 60.2646 | -61.1572 | -61.322 | -0.045777 | 0 | -0.16479 | 121.7239 | -0.12817 | -0.12817 | -0.16022 | 0.054931 | -0.10986 | -0.14191 | 0.21515 | -0.22888 | -0.11902 | -0.13733 | 121.4493 | 121.4539 | 61.3174 | -121.6141 | 121.4722 | 121.4767 | 61.3998 | -121.7239
666.25 | 121.8842 | -61.203 | 60.4019 | -0.19562 | 0.01857 | 0.073785 | 0.066847 | 0.12631 | -0.0051676 | -0.005456 | -0.062256 | -0.0079832 | 0.065507 | 0.069536 | -0.00046349 | -0.010666 | 60.347 | 60.5804 | 0.25635 | -61.2717 | 60.2829 | -61.2213 | -61.1664 | -60.9558 | 0.28839 | -61.4227 | 60.2737 | 60.2417 | -61.1664 | -61.3129 | -0.01831 | 0.036621 | -0.11902 | 121.7834 | -0.068664 | -0.10529 | -0.054932 | 0.036621 | -0.10986 | -0.12817 | 0.24719 | -0.21973 | -0.10986 | -0.16022 | 121.4859 | 121.55 | 61.4594 | -121.5683 | 121.4767 | 121.4447 | 61.4914 | -121.7148
667.9375 | 121.8384 | -61.235 | 60.3928 | -0.22614 | 0.016648 | 0.074854 | 0.067488 | 0.12824 | -0.003245 | -0.0039606 | -0.19958 | -0.006915 | 0.063585 | 0.070177 | 0.0025271 | -0.011094 | 60.2509 | 60.4431 | 0.1236 | -61.3632 | 60.3195 | -61.2396 | -61.2396 | -61.0611 | 0.18768 | -61.5097 | 60.3378 | 60.3012 | -61.1984 | -61.3632 | -0.004578 | -0.004578 | -0.073242 | 121.6782 | -0.12817 | -0.1236 | -0.14191 | 0.036621 | -0.12817 | -0.054931 | 0.17395 | -0.27466 | -0.14648 | -0.091553 | 121.5546 | 121.4859 | 61.3586 | -121.6324 | 121.5729 | 121.5363 | 61.4227 | -121.756
669.6719 | 121.8704 | -61.2625 | 60.3607 | -0.17273 | 0.01857 | 0.072931 | 0.06706 | 0.12674 | 0.00038662 | -0.0039606 | -0.1767 | -0.0060606 | 0.062944 | 0.073168 | 0.0027407 | -0.0081027 | 60.2463 | 60.4156 | 0.10071 | -61.3541 | 60.3058 | -61.2854 | -61.2625 | -61.0748 | 0.13275 | -61.5372 | 60.2921 | 60.2371 | -61.235 | -61.3861 | -0.022888 | 0 | -0.054932 | 121.6782 | -0.091553 | -0.091553 | -0.11444 | 0.027466 | -0.1236 | -0.068665 | 0.18768 | -0.27466 | -0.15106 | -0.1236 | 121.5683 | 121.5088 | 61.3632 | -121.6232 | 121.5546 | 121.4996 | 61.3953 | -121.7468
671.3438 | 121.9482 | -61.2671 | 60.2737 | 0.16296 | 0.014725 | 0.073358 | 0.06172 | 0.1293 | -0.0017496 | -0.0033196 | 0.19714 | -0.0060606 | 0.060594 | 0.071673 | 0.0044497 | -0.0070345 | 60.1776 | 60.3882 | -0.10529 | -61.4319 | 60.1776 | -61.3449 | -61.29 | -61.0703 | -0.009155 | -61.5417 | 60.1639 | 60.1547 | -61.2488 | -61.4227 | -0.07782 | -0.022888 | -0.096131 | 121.6553 | -0.16479 | -0.14191 | -0.096131 | 0.018311 | -0.15564 | -0.10986 | 0.19684 | -0.27466 | -0.11902 | -0.11902 | 121.4447 | 121.4447 | 61.1618 | -121.5637 | 121.431 | 121.4218 | 61.2579 | -121.6965
673.0938 | 121.9528 | -61.2717 | 60.26 | 0.094299 | 0.016648 | 0.072504 | 0.065138 | 0.12674 | 0.00038662 | -0.0024652 | 0.20477 | -0.0039244 | 0.062303 | 0.072741 | 0.0042361 | -0.0095981 | 60.173 | 60.3333 | -0.11444 | -61.4594 | 60.2234 | -61.3541 | -61.2991 | -61.1114 | -0.059509 | -61.6013 | 60.1913 | 60.1822 | -61.2579 | -61.4273 | -0.082398 | -0.027466 | -0.036621 | 121.6049 | -0.18768 | -0.16022 | -0.086975 | 0.013732 | -0.15564 | -0.068665 | 0.16022 | -0.32959 | -0.17395 | -0.07782 | 121.4951 | 121.4447 | 61.1572 | -121.5591 | 121.463 | 121.4539 | 61.2122 | -121.6873
674.7812 | 121.8521 | -61.2625 | 60.3333 | -0.11169 | 0.017075 | 0.071649 | 0.067701 | 0.12824 | 0.0014548 | -0.0022516 | -0.062256 | -0.0039244 | 0.062517 | 0.072954 | 0.0025271 | -0.0089573 | 60.2554 | 60.4385 | 0.073242 | -61.3724 | 60.2646 | -61.29 | -61.2579 | -61.0657 | 0.09613 | -61.5326 | 60.2509 | 60.2509 | -61.2442 | -61.4044 | -0.027466 | 0.004577 | -0.068665 | 121.7011 | -0.10986 | -0.11444 | -0.07782 | 0.01831 | -0.14191 | -0.082398 | 0.19684 | -0.27008 | -0.12817 | -0.082398 | 121.5271 | 121.5179 | 61.3358 | -121.5912 | 121.5134 | 121.5134 | 61.3586 | -121.7377
676.5312 | 121.9437 | -61.2808 | 60.2829 | 0.10956 | 0.015152 | 0.071863 | 0.064497 | 0.12845 | -0.0019632 | -0.0043878 | 0.18951 | -0.0045652 | 0.05974 | 0.072314 | 0.0023135 | -0.0085299 | 60.2325 | 60.3973 | -0.050354 | -61.3998 | 60.173 | -61.3129 | -61.3037 | -61.0474 | 0.032043 | -61.5189 | 60.2005 | 60.141 | -61.2488 | -61.409 | -0.032043 | -0.022888 | -0.10986 | 121.6782 | -0.11902 | -0.09613 | -0.050354 | 0.032044 | -0.12817 | -0.082398 | 0.23346 | -0.23804 | -0.10986 | -0.14191 | 121.4539 | 121.5134 | 61.2305 | -121.5866 | 121.4813 | 121.4218 | 61.3129 | -121.6919
678.2812 | 121.9437 | -61.2534 | 60.3058 | 0.11719 | 0.012162 | 0.072076 | 0.065779 | 0.13101 | -0.004954 | -0.003747 | 0.24292 | -0.006915 | 0.061235 | 0.070177 | 0.0023135 | -0.0085299 | 60.2509 | 60.466 | -0.013733 | -61.3861 | 60.1456 | -61.3083 | -61.2854 | -61.0428 | 0.032043 | -61.5189 | 60.1501 | 60.1593 | -61.235 | -61.4365 | -0.054932 | -0.032043 | -0.16022 | 121.7194 | -0.13275 | -0.10071 | -0.054932 | 0.018311 | -0.1831 | -0.15564 | 0.21057 | -0.2655 | -0.082398 | -0.14648 | 121.3989 | 121.5042 | 61.2396 | -121.5912 | 121.4035 | 121.4127 | 61.2854 | -121.7422
680.0312 | 121.8521 | -61.2213 | 60.4431 | -0.17273 | 0.016648 | 0.073572 | 0.072187 | 0.13016 | -0.0038858 | -0.0050286 | -0.0088499 | -0.0060606 | 0.063371 | 0.071245 | -0.0028135 | -0.0087435 | 60.3195 | 60.5576 | 0.26093 | -61.2854 | 60.2692 | -61.2076 | -61.1847 | -60.9741 | 0.28839 | -61.4227 | 60.2692 | 60.26 | -61.1893 | -61.3129 | 0.013732 | 0.036621 | -0.17395 | 121.7789 | -0.064087 | -0.10071 | -0.1236 | 0.032043 | -0.091553 | -0.17395 | 0.24719 | -0.20142 | -0.10986 | -0.1831 | 121.4905 | 121.5408 | 61.4822 | -121.6278 | 121.4905 | 121.4813 | 61.5097 | -121.756
681.7188 | 121.8155 | -61.3266 | 60.3195 | -0.088806 | 0.01857 | 0.071436 | 0.065565 | 0.12824 | 0.0020956 | -0.003747 | -0.062256 | -0.0062742 | 0.061449 | 0.072741 | 0.0061587 | -0.0095981 | 60.2875 | 60.4294 | 0.059509 | -61.3998 | 60.2509 | -61.2946 | -61.2534 | -61.0611 | 0.09613 | -61.5555 | 60.2325 | 60.2097 | -61.2442 | -61.4182 | 0.032043 | 0.073242 | -0.068665 | 121.756 | -0.073242 | -0.14648 | -0.032043 | 0.082397 | -0.091553 | -0.086975 | 0.2655 | -0.22888 | -0.13733 | -0.10986 | 121.5775 | 121.6141 | 61.3861 | -121.5729 | 121.5591 | 121.5363 | 61.4227 | -121.7377
683.4688 | 121.8338 | -61.3129 | 60.3012 | 0.26978 | 0.020493 | 0.075922 | 0.063856 | 0.1308 | 0.0020956 | -0.0024652 | 0.075073 | -0.0064878 | 0.059953 | 0.073168 | 0.0061587 | -0.010025 | 60.1501 | 60.3333 | -0.07782 | -61.4548 | 60.2188 | -61.322 | -61.3129 | -61.171 | -0.059509 | -61.6516 | 60.2371 | 60.2051 | -61.2625 | -61.4548 | -0.009155 | 0 | -0.082397 | 121.6461 | -0.14191 | -0.14191 | -0.15106 | 0.050354 | -0.14191 | -0.064086 | 0.14191 | -0.33875 | -0.19684 | -0.09613 | 121.5317 | 121.463 | 61.235 | -121.6141 | 121.55 | 121.5179 | 61.2534 | -121.756
685.2344 | 121.8246 | -61.2488 | 60.4202 | -0.22614 | 0.018143 | 0.071008 | 0.068129 | 0.12994 | -0.0038858 | -0.002038 | -0.12329 | -0.006915 | 0.064439 | 0.070605 | -0.00046349 | -0.0063937 | 60.2554 | 60.4614 | 0.15106 | -61.3449 | 60.2966 | -61.2259 | -61.235 | -61.0657 | 0.19684 | -61.5097 | 60.3195 | 60.2783 | -61.1938 | -61.3541 | 0.022888 | 0.013733 | -0.1236 | 121.7102 | -0.096131 | -0.10986 | -0.16479 | 0.054931 | -0.10529 | -0.10071 | 0.1831 | -0.26093 | -0.15564 | -0.14191 | 121.5454 | 121.5042 | 61.3998 | -121.6553 | 121.5683 | 121.5271 | 61.4456 | -121.7743
686.9844 | 121.9345 | -61.2854 | 60.3058 | 0.08667 | 0.018784 | 0.071863 | 0.06407 | 0.12952 | -0.0028178 | -0.0043878 | 0.14374 | -0.0081968 | 0.064226 | 0.073595 | 0.0040225 | -0.0083163 | 60.1685 | 60.3424 | -0.1236 | -61.4548 | 60.228 | -61.3403 | -61.322 | -61.1298 | -0.082397 | -61.6104 | 60.2097 | 60.1868 | -61.2717 | -61.4548 | -0.054932 | -0.036621 | -0.07782 | 121.6278 | -0.16937 | -0.13275 | -0.13733 | 0.013733 | -0.16937 | -0.09613 | 0.15564 | -0.32501 | -0.15564 | -0.11902 | 121.5134 | 121.4539 | 61.1618 | -121.6278 | 121.4951 | 121.4722 | 61.203 | -121.7606
688.6719 | 121.8246 | -61.3174 | 60.3241 | -0.088806 | 0.018784 | 0.071008 | 0.065351 | 0.13059 | 0.00017302 | -0.0009698 | -0.054626 | -0.005847 | 0.06273 | 0.070177 | 0.0053043 | -0.0091709 | 60.2509 | 60.4431 | 0.059509 | -61.3815 | 60.2554 | -61.3037 | -61.2717 | -61.0886 | 0.10071 | -61.5463 | 60.2417 | 60.2234 | -61.2625 | -61.4227 | 0.013733 | 0.045777 | -0.068665 | 121.7606 | -0.064087 | -0.10986 | -0.073243 | 0.054932 | -0.10528 | -0.082398 | 0.22888 | -0.22888 | -0.1236 | -0.10071 | 121.5729 | 121.5683 | 61.377 | -121.5958 | 121.5591 | 121.5408 | 61.4182 | -121.7468
690.4062 | 121.875 | -61.2717 | 60.3287 | -0.14221 | 0.019852 | 0.071436 | 0.068129 | 0.12824 | -0.00068138 | -0.0018244 | -0.069885 | -0.0071286 | 0.063158 | 0.072527 | 0.0010317 | -0.0095981 | 60.2371 | 60.4385 | 0.09613 | -61.377 | 60.2737 | -61.29 | -61.2671 | -61.0748 | 0.13275 | -61.528 | 60.2417 | 60.2417 | -61.2396 | -61.3998 | -0.018311 | 0.004577 | -0.054931 | 121.7102 | -0.10529 | -0.10986 | -0.091552 | 0.032043 | -0.12817 | -0.086975 | 0.19684 | -0.25635 | -0.12817 | -0.086975 | 121.5454 | 121.5088 | 61.3678 | -121.5958 | 121.5134 | 121.5134 | 61.4044 | -121.7285
692.1562 | 121.8567 | -61.3312 | 60.2966 | 0.08667 | 0.019425 | 0.075067 | 0.063215 | 0.12973 | -0.001536 | -0.0033196 | 0.13611 | -0.006915 | 0.061662 | 0.071886 | 0.0044497 | -0.0061801 | 60.1364 | 60.3012 | -0.12817 | -61.4685 | 60.2051 | -61.3129 | -61.3266 | -61.1847 | -0.10529 | -61.6333 | 60.2097 | 60.1959 | -61.3083 | -61.4594 | 0.018311 | 0.004578 | -0.091553 | 121.6324 | -0.13733 | -0.14191 | -0.16022 | 0.022888 | -0.12817 | -0.086975 | 0.14648 | -0.30212 | -0.17395 | -0.10071 | 121.5363 | 121.4676 | 61.203 | -121.6232 | 121.5408 | 121.5271 | 61.2259 | -121.756
693.8438 | 121.7972 | -61.3129 | 60.3195 | -0.050659 | 0.019211 | 0.068872 | 0.06941 | 0.12909 | -0.00046778 | -0.0046014 | 0.036926 | -0.0043516 | 0.064012 | 0.073382 | 0.0023135 | -0.0078891 | 60.2188 | 60.4065 | 0.004578 | -61.4044 | 60.2371 | -61.3174 | -61.2854 | -61.1481 | 0.009155 | -61.6013 | 60.2371 | 60.2188 | -61.2717 | -61.4365 | -0.004578 | 0.027466 | -0.082397 | 121.7194 | -0.091553 | -0.11902 | -0.10071 | 0.041199 | -0.1236 | -0.082397 | 0.16479 | -0.28839 | -0.16479 | -0.10071 | 121.55 | 121.5317 | 61.3174 | -121.6049 | 121.55 | 121.5317 | 61.322 | -121.756
695.5781 | 121.8109 | -61.2213 | 60.4202 | -0.25665 | 0.016648 | 0.073572 | 0.070265 | 0.12717 | -0.0053812 | -0.0035334 | -0.077515 | -0.007556 | 0.066148 | 0.072314 | -0.00089089 | -0.0068209 | 60.2875 | 60.5026 | 0.21057 | -61.3129 | 60.3012 | -61.2442 | -61.2122 | -61.0611 | 0.20142 | -61.5051 | 60.3241 | 60.3195 | -61.1938 | -61.3266 | -0.022889 | 0.009155 | -0.11902 | 121.7239 | -0.091553 | -0.10071 | -0.13275 | 0.027465 | -0.10529 | -0.09613 | 0.16022 | -0.28381 | -0.17853 | -0.10071 | 121.5225 | 121.5088 | 61.4319 | -121.6324 | 121.5454 | 121.5408 | 61.4227 | -121.7468
697.3125 | 121.875 | -61.203 | 60.4202 | -0.19562 | 0.017502 | 0.073145 | 0.068983 | 0.12909 | -0.0090128 | -0.0073786 | -0.062256 | -0.0077696 | 0.061449 | 0.071886 | 0.00017731 | -0.0063937 | 60.3333 | 60.5988 | 0.25635 | -61.2534 | 60.2692 | -61.1984 | -61.1664 | -60.9741 | 0.28839 | -61.4044 | 60.26 | 60.2692 | -61.171 | -61.3266 | 0.004578 | 0.036621 | -0.15106 | 121.8018 | -0.050354 | -0.086975 | -0.086975 | 0.032044 | -0.1236 | -0.16022 | 0.22888 | -0.20142 | -0.07782 | -0.15106 | 121.4722 | 121.5363 | 61.4594 | -121.5866 | 121.463 | 121.4722 | 61.4914 | -121.7468
699.0781 | 121.9574 | -61.1755 | 60.3973 | -0.027771 | 0.01857 | 0.07229 | 0.066206 | 0.13016 | -0.0070902 | -0.007165 | 0.052185 | -0.0071286 | 0.062089 | 0.073595 | -0.0019589 | -0.0074619 | 60.2646 | 60.4889 | 0.10986 | -61.3358 | 60.2463 | -61.2625 | -61.235 | -60.9787 | 0.21057 | -61.409 | 60.2692 | 60.2554 | -61.1389 | -61.3403 | -0.086975 | -0.059509 | -0.15106 | 121.6644 | -0.16022 | -0.10071 | -0.13275 | 0.036621 | -0.16479 | -0.12817 | 0.19684 | -0.23346 | -0.068665 | -0.14191 | 121.4218 | 121.4401 | 61.2854 | -121.6324 | 121.4447 | 121.431 | 61.3861 | -121.7377
700.7656 | 121.8063 | -61.3083 | 60.3287 | -0.065918 | 0.019852 | 0.072717 | 0.064924 | 0.12909 | 0.0016684 | -0.0041742 | -0.054626 | -0.003497 | 0.063371 | 0.075518 | 0.0040225 | -0.011307 | 60.2692 | 60.4202 | 0.036621 | -61.3998 | 60.2554 | -61.3129 | -61.3083 | -61.0794 | 0.054932 | -61.5738 | 60.2371 | 60.2188 | -61.2625 | -61.4136 | -0.004577 | 0 | -0.073242 | 121.7285 | -0.091552 | -0.091552 | -0.059509 | 0.045777 | -0.10528 | -0.091552 | 0.22888 | -0.2655 | -0.16022 | -0.10986 | 121.5637 | 121.5775 | 61.3449 | -121.637 | 121.5454 | 121.5271 | 61.3632 | -121.7422
702.5 | 121.9528 | -61.2717 | 60.2966 | 0.12482 | 0.014511 | 0.070367 | 0.060652 | 0.12738 | -0.002604 | -0.0001154 | 0.16663 | -0.006915 | 0.062944 | 0.072527 | 0.0040225 | -0.0093845 | 60.2234 | 60.4385 | -0.041199 | -61.3724 | 60.1685 | -61.3266 | -61.29 | -61.0428 | 0.013733 | -61.5189 | 60.1822 | 60.1456 | -61.2534 | -61.4182 | -0.054932 | -0.018311 | -0.12817 | 121.7102 | -0.10071 | -0.082397 | -0.073242 | 0.01831 | -0.14648 | -0.11444 | 0.22888 | -0.24719 | -0.10071 | -0.15106 | 121.4401 | 121.4951 | 61.2305 | -121.5866 | 121.4539 | 121.4172 | 61.2854 | -121.7148
704.25 | 121.9666 | -61.2991 | 60.2875 | 0.14008 | 0.014511 | 0.074213 | 0.063643 | 0.12802 | -0.0019632 | -0.003106 | 0.17426 | -0.0088376 | 0.060808 | 0.071245 | 0.0053043 | -0.0072483 | 60.1959 | 60.4065 | -0.082397 | -61.4227 | 60.1776 | -61.3312 | -61.3083 | -61.0794 | 0.004578 | -61.5189 | 60.1822 | 60.1593 | -61.2442 | -61.4136 | -0.032044 | -0.009156 | -0.10986 | 121.7056 | -0.1236 | -0.11444 | -0.091553 | 0.054931 | -0.11444 | -0.10529 | 0.21973 | -0.21973 | -0.10529 | -0.12817 | 121.4767 | 121.4951 | 61.2167 | -121.5958 | 121.4813 | 121.4584 | 61.3037 | -121.701
705.9219 | 121.8933 | -61.1664 | 60.4065 | -0.18036 | 0.014939 | 0.073572 | 0.067701 | 0.13144 | -0.0070902 | -0.003747 | -0.046997 | -0.005847 | 0.062089 | 0.071032 | -0.0019589 | -0.0068209 | 60.3607 | 60.6033 | 0.2655 | -61.2808 | 60.2463 | -61.235 | -61.1938 | -60.9787 | 0.29755 | -61.3998 | 60.26 | 60.2463 | -61.1755 | -61.3358 | -0.068664 | -0.027466 | -0.16022 | 121.7697 | -0.11444 | -0.086975 | -0.045776 | -0.009155 | -0.16937 | -0.14648 | 0.18768 | -0.23346 | -0.064087 | -0.16022 | 121.4127 | 121.5271 | 61.4319 | -121.6003 | 121.4264 | 121.4127 | 61.4639 | -121.7422
707.6719 | 121.962 | -61.1847 | 60.3882 | -0.027771 | 0.0089572 | 0.072931 | 0.065138 | 0.12845 | -0.0058084 | -0.0063104 | 0.090332 | -0.0090512 | 0.058672 | 0.074236 | 0.00060451 | -0.0072483 | 60.2646 | 60.4935 | 0.086975 | -61.3403 | 60.2554 | -61.2442 | -61.2213 | -60.9879 | 0.16479 | -61.4273 | 60.2646 | 60.2463 | -61.1664 | -61.3312 | -0.05951 | -0.036621 | -0.13275 | 121.6782 | -0.15564 | -0.11902 | -0.1236 | 0.01831 | -0.14648 | -0.1236 | 0.19684 | -0.24262 | -0.09613 | -0.14191 | 121.4401 | 121.4493 | 61.2717 | -121.6095 | 121.4493 | 121.431 | 61.3495 | -121.7194
709.4219 | 121.843 | -61.235 | 60.3973 | -0.21851 | 0.014725 | 0.07464 | 0.065992 | 0.12909 | 0.00038662 | -0.0067376 | -0.18433 | -0.005847 | 0.059099 | 0.072741 | 0.0029543 | -0.0087435 | 60.2737 | 60.4385 | 0.12817 | -61.3541 | 60.3241 | -61.2213 | -61.2259 | -61.0703 | 0.15564 | -61.528 | 60.3287 | 60.3149 | -61.1984 | -61.3495 | 0.013733 | 0.009155 | -0.073242 | 121.6736 | -0.11902 | -0.12817 | -0.1236 | 0.036621 | -0.11444 | -0.068665 | 0.16479 | -0.29297 | -0.17853 | -0.082398 | 121.5591 | 121.5088 | 61.3632 | -121.6232 | 121.5637 | 121.55 | 61.3907 | -121.7468
711.1719 | 121.8796 | -61.2625 | 60.347 | -0.18036 | 0.016648 | 0.073785 | 0.066206 | 0.12781 | -4.058e-05 | -0.0043878 | -0.10803 | -0.003497 | 0.061021 | 0.0721 | 0.0044497 | -0.011521 | 60.26 | 60.4385 | 0.082397 | -61.377 | 60.3012 | -61.2854 | -61.2762 | -61.0794 | 0.12817 | -61.5509 | 60.2463 | 60.2325 | -61.2259 | -61.3907 | -0.022888 | -0.013733 | -0.045777 | 121.7011 | -0.11444 | -0.10071 | -0.086975 | 0.036621 | -0.12817 | -0.10071 | 0.1831 | -0.28839 | -0.16022 | -0.11444 | 121.5637 | 121.5225 | 61.3449 | -121.6232 | 121.5088 | 121.4951 | 61.3907 | -121.7377
712.8594 | 121.8292 | -61.2396 | 60.4294 | -0.24139 | 0.016434 | 0.076349 | 0.066847 | 0.12802 | -0.004313 | -0.0050286 | -0.20721 | -0.0096922 | 0.064226 | 0.071245 | -0.00024989 | -0.0093845 | 60.2692 | 60.5072 | 0.1831 | -61.3312 | 60.2921 | -61.2167 | -61.2396 | -61.0565 | 0.18768 | -61.5189 | 60.3104 | 60.2783 | -61.2076 | -61.3449 | 0.022888 | 0 | -0.13733 | 121.7468 | -0.091553 | -0.091553 | -0.16022 | 0.032043 | -0.10529 | -0.11902 | 0.1831 | -0.27924 | -0.17395 | -0.15106 | 121.5317 | 121.5088 | 61.4227 | -121.669 | 121.55 | 121.5179 | 61.4273 | -121.7743
714.6094 | 121.9437 | -61.235 | 60.2966 | 0.29266 | 0.01622 | 0.072717 | 0.063643 | 0.12802 | -0.0034586 | -0.0022516 | 0.19714 | -0.0056332 | 0.061021 | 0.071459 | 0.0050907 | -0.0087435 | 60.2554 | 60.466 | -0.032043 | -61.3724 | 60.2005 | -61.3266 | -61.2946 | -61.0428 | 0.027466 | -61.5143 | 60.1822 | 60.1273 | -61.2717 | -61.4044 | -0.091553 | -0.05951 | -0.096131 | 121.701 | -0.13733 | -0.077819 | -0.041199 | -0.036621 | -0.16937 | -0.11444 | 0.19226 | -0.27924 | -0.10986 | -0.16937 | 121.4355 | 121.4905 | 61.203 | -121.5912 | 121.4172 | 121.3623 | 61.2625 | -121.701
716.3594 | 121.8246 | -61.2167 | 60.4156 | -0.20325 | 0.016434 | 0.073572 | 0.067488 | 0.12717 | -0.004313 | -0.0058832 | -0.13855 | -0.0067014 | 0.063158 | 0.072527 | -0.00067729 | -0.010666 | 60.3195 | 60.5484 | 0.24719 | -61.2717 | 60.2921 | -61.203 | -61.1938 | -61.0062 | 0.25635 | -61.4685 | 60.2921 | 60.2737 | -61.1755 | -61.3312 | 0.013733 | 0.022888 | -0.1236 | 121.7651 | -0.054931 | -0.077819 | -0.09613 | 0.041199 | -0.11444 | -0.1236 | 0.21057 | -0.25177 | -0.13733 | -0.14191 | 121.5088 | 121.5363 | 61.4639 | -121.6095 | 121.5088 | 121.4905 | 61.4731 | -121.7468
718.0938 | 121.8018 | -61.3358 | 60.3012 | -0.0354 | 0.020279 | 0.069727 | 0.065779 | 0.12674 | 0.0020956 | -0.0035334 | 0.021668 | -0.005847 | 0.062303 | 0.071886 | 0.0048769 | -0.010239 | 60.2188 | 60.3836 | -0.013733 | -61.4365 | 60.2188 | -61.3266 | -61.3037 | -61.1526 | -0.027466 | -61.6379 | 60.2051 | 60.1639 | -61.2579 | -61.441 | 0.009155 | 0.032043 | -0.082397 | 121.7194 | -0.10071 | -0.13275 | -0.082397 | 0.077819 | -0.10529 | -0.09613 | 0.18311 | -0.30212 | -0.19684 | -0.13733 | 121.5546 | 121.5546 | 61.322 | -121.6049 | 121.5408 | 121.4996 | 61.3083 | -121.7422
719.7812 | 121.8521 | -61.2167 | 60.434 | -0.20325 | 0.017289 | 0.075494 | 0.069197 | 0.12802 | -0.0058084 | -0.004815 | -0.069885 | -0.0071286 | 0.063585 | 0.068682 | -0.0013181 | -0.0076755 | 60.3195 | 60.5988 | 0.24719 | -61.29 | 60.26 | -61.2213 | -61.1847 | -60.9741 | 0.27924 | -61.4136 | 60.2783 | 60.2554 | -61.1755 | -61.322 | -0.004577 | 0.032044 | -0.17395 | 121.8155 | -0.073242 | -0.10529 | -0.11444 | 0.041199 | -0.10529 | -0.15564 | 0.24262 | -0.19684 | -0.091553 | -0.17853 | 121.4767 | 121.5363 | 61.4639 | -121.6187 | 121.4951 | 121.4722 | 61.496 | -121.756
721.5156 | 121.9025 | -61.2488 | 60.3653 | 0.10193 | 0.014939 | 0.074426 | 0.064924 | 0.12674 | -0.0070902 | -0.0050286 | 0.16663 | -0.0081968 | 0.061235 | 0.070391 | 0.0018863 | -0.0068209 | 60.2554 | 60.466 | 0.045776 | -61.3815 | 60.2142 | -61.2534 | -61.2534 | -61.0245 | 0.068665 | -61.5097 | 60.2371 | 60.2051 | -61.203 | -61.3861 | -0.004578 | -0.004578 | -0.15106 | 121.7148 | -0.13275 | -0.12817 | -0.10986 | 0.045776 | -0.13733 | -0.12817 | 0.2243 | -0.26093 | -0.1236 | -0.16022 | 121.463 | 121.5042 | 61.2946 | -121.6187 | 121.4859 | 121.4539 | 61.3174 | -121.7514
723.2656 | 121.8979 | -61.2167 | 60.3607 | 0.094299 | 0.013016 | 0.072076 | 0.063002 | 0.12738 | -0.004954 | -0.005456 | 0.17426 | -0.0067014 | 0.060167 | 0.073382 | 0.0023135 | -0.0093845 | 60.26 | 60.4797 | 0.032043 | -61.3724 | 60.2097 | -61.2717 | -61.235 | -61.0107 | 0.073242 | -61.5005 | 60.2417 | 60.2051 | -61.2076 | -61.3632 | -0.054931 | -0.01831 | -0.15106 | 121.6965 | -0.15564 | -0.13733 | -0.10071 | 0.009155 | -0.14648 | -0.11902 | 0.20599 | -0.28381 | -0.13733 | -0.15564 | 121.4264 | 121.4767 | 61.2488 | -121.5958 | 121.4584 | 121.4218 | 61.29 | -121.7239
724.9531 | 121.8155 | -61.3449 | 60.3149 | -0.050659 | 0.014939 | 0.071863 | 0.065992 | 0.13059 | 0.004659 | -0.0026788 | -0.024109 | -0.0056332 | 0.060808 | 0.073382 | 0.0055179 | -0.011094 | 60.26 | 60.4019 | 0.027466 | -61.409 | 60.2371 | -61.3312 | -61.3083 | -61.1298 | -0.009155 | -61.6104 | 60.2325 | 60.173 | -61.2579 | -61.4319 | 0.013733 | 0.036621 | -0.077819 | 121.7468 | -0.064087 | -0.10071 | -0.054931 | 0.086975 | -0.086975 | -0.082397 | 0.21515 | -0.2655 | -0.17853 | -0.14191 | 121.582 | 121.6049 | 61.3724 | -121.6232 | 121.5775 | 121.5179 | 61.3358 | -121.7468
726.7031 | 121.962 | -61.2717 | 60.2737 | 0.15533 | 0.013443 | 0.07229 | 0.062788 | 0.12952 | -0.0023904 | -0.0024652 | 0.34973 | -0.0071286 | 0.061662 | 0.072527 | 0.0038089 | -0.0081027 | 60.2142 | 60.4156 | -0.064087 | -61.409 | 60.1868 | -61.3129 | -61.2854 | -61.0336 | 0.027466 | -61.528 | 60.2051 | 60.1547 | -61.2717 | -61.4044 | -0.041199 | -0.013733 | -0.086975 | 121.6873 | -0.13733 | -0.1236 | -0.05951 | 0 | -0.13275 | -0.068665 | 0.23804 | -0.25635 | -0.1236 | -0.11902 | 121.4584 | 121.4859 | 61.2076 | -121.5591 | 121.4767 | 121.4264 | 61.2991 | -121.6782
728.4531 | 121.8338 | -61.3083 | 60.3104 | -0.073547 | 0.017929 | 0.069727 | 0.06706 | 0.12759 | 0.0027364 | -0.0011834 | -0.077515 | -0.0073422 | 0.061021 | 0.074877 | 0.0050907 | -0.0085299 | 60.2554 | 60.4294 | 0.059509 | -61.3907 | 60.2325 | -61.2991 | -61.2671 | -61.0611 | 0.10986 | -61.5601 | 60.26 | 60.1959 | -61.235 | -61.409 | 0.009156 | 0.041199 | -0.07782 | 121.7377 | -0.082397 | -0.1236 | -0.054932 | 0.073243 | -0.10071 | -0.050354 | 0.24719 | -0.25177 | -0.15106 | -0.11444 | 121.5408 | 121.5637 | 61.3678 | -121.5775 | 121.5683 | 121.5042 | 61.4182 | -121.7194
730.1562 | 121.8292 | -61.3174 | 60.3378 | -0.088806 | 0.01558 | 0.070367 | 0.067274 | 0.12717 | 0.0016684 | -0.000329 | -0.046997 | -0.0054196 | 0.06273 | 0.071673 | 0.0038089 | -0.0083163 | 60.2463 | 60.4385 | 0.064087 | -61.3953 | 60.228 | -61.2946 | -61.2671 | -61.0703 | 0.10529 | -61.5555 | 60.2325 | 60.2142 | -61.2534 | -61.4227 | 0.022888 | 0.050354 | -0.10986 | 121.756 | -0.07782 | -0.12817 | -0.091553 | 0.064087 | -0.10528 | -0.10529 | 0.24719 | -0.23804 | -0.13275 | -0.1236 | 121.5454 | 121.5637 | 61.3815 | -121.6049 | 121.55 | 121.5317 | 61.4227 | -121.7606
731.8906 | 121.843 | -61.3037 | 60.3058 | -0.096436 | 0.018143 | 0.073145 | 0.067701 | 0.12888 | -0.0023904 | -0.0018244 | -0.077515 | -0.0056332 | 0.06508 | 0.071245 | 0.0035953 | -0.0072483 | 60.2371 | 60.4385 | 0.059509 | -61.3907 | 60.2646 | -61.2991 | -61.3129 | -61.0611 | 0.13733 | -61.5555 | 60.2325 | 60.1959 | -61.2671 | -61.4136 | 0.004578 | -0.009155 | -0.041199 | 121.7422 | -0.086975 | -0.07782 | -0.068664 | 0.036621 | -0.10986 | -0.073242 | 0.24262 | -0.25177 | -0.14191 | -0.10986 | 121.5683 | 121.5408 | 61.3632 | -121.6187 | 121.5363 | 121.4996 | 61.441 | -121.7194
733.6406 | 121.9254 | -61.235 | 60.3424 | 0.15533 | 0.016861 | 0.070581 | 0.064711 | 0.1293 | -0.0064492 | -0.0046014 | 0.25055 | -0.0081968 | 0.061449 | 0.071459 | 0.0038089 | -0.0087435 | 60.2188 | 60.4843 | 0.004578 | -61.3953 | 60.1456 | -61.3174 | -61.2762 | -61.0336 | 0.064087 | -61.4914 | 60.1685 | 60.1639 | -61.2488 | -61.4044 | -0.082398 | -0.041199 | -0.19684 | 121.7194 | -0.16022 | -0.11902 | -0.1236 | -0.013733 | -0.16937 | -0.17395 | 0.20142 | -0.25635 | -0.086975 | -0.17853 | 121.3806 | 121.4539 | 61.2396 | -121.6187 | 121.4035 | 121.3989 | 61.2991 | -121.7468
735.3906 | 121.907 | -61.2305 | 60.379 | 0.094299 | 0.01558 | 0.073145 | 0.067274 | 0.12824 | -0.006022 | -0.003747 | 0.23529 | -0.0071286 | 0.059099 | 0.073382 | 0.0010317 | -0.0085299 | 60.2463 | 60.4843 | 0.013733 | -61.3861 | 60.1913 | -61.2808 | -61.2534 | -61.0245 | 0.082397 | -61.4731 | 60.228 | 60.2051 | -61.1938 | -61.3724 | -0.050354 | -0.022888 | -0.18768 | 121.7148 | -0.15564 | -0.13275 | -0.13275 | 0.036621 | -0.14191 | -0.15106 | 0.20599 | -0.24261 | -0.10071 | -0.17395 | 121.4218 | 121.4767 | 61.2442 | -121.6324 | 121.4584 | 121.4355 | 61.3129 | -121.7514
737.1406 | 121.875 | -61.2762 | 60.347 | -0.18036 | 0.019638 | 0.071863 | 0.065565 | 0.12888 | -4.058e-05 | -0.0039606 | -0.10803 | -0.0037106 | 0.060381 | 0.070605 | 0.0029543 | -0.0095981 | 60.2325 | 60.4202 | 0.07782 | -61.3678 | 60.2829 | -61.2762 | -61.2671 | -61.0794 | 0.12817 | -61.528 | 60.2646 | 60.2142 | -61.2396 | -61.3953 | 0 | 0.009155 | -0.064087 | 121.6965 | -0.091553 | -0.10071 | -0.11444 | 0.036621 | -0.11902 | -0.082398 | 0.19684 | -0.25177 | -0.13275 | -0.13275 | 121.5591 | 121.5088 | 61.3541 | -121.6141 | 121.5408 | 121.4905 | 61.4044 | -121.7422
738.8281 | 121.9345 | -61.2442 | 60.3012 | 0.14008 | 0.014511 | 0.071008 | 0.063856 | 0.12994 | -0.0047404 | -0.003747 | 0.25055 | -0.007556 | 0.061662 | 0.071673 | 0.0027407 | -0.010666 | 60.2463 | 60.4614 | -0.009155 | -61.3815 | 60.1547 | -61.3174 | -61.2854 | -61.0291 | 0.045776 | -61.5005 | 60.1639 | 60.1273 | -61.2625 | -61.4182 | -0.073242 | -0.041198 | -0.14648 | 121.7056 | -0.13733 | -0.096131 | -0.054931 | -0.01831 | -0.17395 | -0.13733 | 0.21515 | -0.25635 | -0.082397 | -0.17395 | 121.3989 | 121.4905 | 61.235 | -121.5866 | 121.4081 | 121.3715 | 61.29 | -121.7194
740.5625 | 121.9116 | -61.2305 | 60.3424 | 0.13245 | 0.012589 | 0.076349 | 0.06407 | 0.13187 | -0.0038858 | -0.0041742 | 0.23529 | -0.0071286 | 0.062089 | 0.071459 | 0.0044497 | -0.0083163 | 60.2509 | 60.4706 | 0.009155 | -61.3678 | 60.1593 | -61.29 | -61.2717 | -61.0291 | 0.054932 | -61.4822 | 60.1868 | 60.1639 | -61.2442 | -61.3861 | -0.059509 | -0.041198 | -0.18311 | 121.7011 | -0.13733 | -0.096131 | -0.091553 | -0.013733 | -0.15564 | -0.15564 | 0.20142 | -0.25177 | -0.096131 | -0.17853 | 121.3898 | 121.4813 | 61.2396 | -121.6141 | 121.4172 | 121.3943 | 61.2854 | -121.7285
742.2969 | 121.9299 | -61.29 | 60.2829 | 0.094299 | 0.021347 | 0.070367 | 0.064924 | 0.1293 | 0.001882 | -0.0026788 | 0.12848 | -0.0071286 | 0.064226 | 0.072954 | 0.0023135 | -0.010666 | 60.173 | 60.3378 | -0.11902 | -61.4639 | 60.2188 | -61.3358 | -61.322 | -61.1114 | -0.073242 | -61.6287 | 60.2142 | 60.1913 | -61.2671 | -61.441 | -0.045776 | -0.032043 | -0.064087 | 121.6278 | -0.17395 | -0.14191 | -0.10986 | 0.022888 | -0.15106 | -0.068665 | 0.17853 | -0.33875 | -0.18768 | -0.091553 | 121.5088 | 121.463 | 61.171 | -121.6049 | 121.5042 | 121.4813 | 61.2167 | -121.7239
743.9844 | 121.8658 | -61.29 | 60.347 | -0.10406 | 0.01558 | 0.072076 | 0.062788 | 0.12802 | 0.0010276 | -0.0028924 | -0.054626 | -0.006915 | 0.062089 | 0.071245 | 0.0040225 | -0.0091709 | 60.2417 | 60.4385 | 0.082397 | -61.3678 | 60.2646 | -61.3174 | -61.2762 | -61.0703 | 0.1236 | -61.5555 | 60.2509 | 60.2188 | -61.2534 | -61.409 | -0.027466 | 0.013733 | -0.082398 | 121.7285 | -0.07782 | -0.091553 | -0.10529 | 0.036621 | -0.11902 | -0.096131 | 0.21973 | -0.2655 | -0.14648 | -0.12817 | 121.5546 | 121.5317 | 61.3724 | -121.6232 | 121.5408 | 121.5088 | 61.4136 | -121.756
745.7344 | 121.8567 | -61.2167 | 60.4202 | -0.18036 | 0.016861 | 0.072076 | 0.068983 | 0.12759 | -0.007731 | -0.0050286 | -0.031738 | -0.0064878 | 0.061662 | 0.071673 | -0.00067729 | -0.0098117 | 60.3149 | 60.5576 | 0.24719 | -61.2762 | 60.2692 | -61.2167 | -61.203 | -60.9879 | 0.29755 | -61.409 | 60.2646 | 60.26 | -61.1572 | -61.3312 | 0 | 0.013733 | -0.15106 | 121.7743 | -0.059509 | -0.073242 | -0.10529 | 0.059509 | -0.11444 | -0.15564 | 0.22888 | -0.19226 | -0.07782 | -0.16022 | 121.4859 | 121.5317 | 61.4639 | -121.6232 | 121.4813 | 121.4767 | 61.5143 | -121.7514
747.4844 | 121.8475 | -61.2991 | 60.3333 | -0.10406 | 0.017289 | 0.071222 | 0.066633 | 0.12866 | 0.00017302 | -0.003106 | -0.069885 | -0.004138 | 0.062089 | 0.072527 | 0.0055179 | -0.010025 | 60.2646 | 60.4248 | 0.050354 | -61.3953 | 60.2417 | -61.3129 | -61.2671 | -61.0519 | 0.11444 | -61.5555 | 60.2554 | 60.2371 | -61.2259 | -61.4044 | -0.013733 | 0.032043 | -0.091553 | 121.7239 | -0.096131 | -0.12817 | -0.068665 | 0.073242 | -0.10529 | -0.07782 | 0.24719 | -0.25635 | -0.15106 | -0.09613 | 121.5408 | 121.5637 | 61.3495 | -121.6003 | 121.5546 | 121.5363 | 61.4136 | -121.7377
749.1719 | 121.8613 | -61.2671 | 60.347 | -0.15747 | 0.016861 | 0.072717 | 0.066847 | 0.12909 | -0.0011088 | -0.0039606 | -0.16907 | -0.0062742 | 0.06273 | 0.071673 | 0.0014591 | -0.010239 | 60.2417 | 60.4065 | 0.091553 | -61.377 | 60.2737 | -61.2762 | -61.2259 | -61.0794 | 0.14191 | -61.5417 | 60.2875 | 60.2692 | -61.2396 | -61.3953 | -0.009155 | 0.041199 | -0.073242 | 121.6736 | -0.10986 | -0.15106 | -0.10529 | 0.027466 | -0.12817 | -0.059509 | 0.18768 | -0.27466 | -0.14648 | -0.07782 | 121.5408 | 121.5088 | 61.3586 | -121.5729 | 121.5546 | 121.5363 | 61.409 | -121.7422
750.9219 | 121.8475 | -61.322 | 60.3241 | -0.088806 | 0.017289 | 0.074213 | 0.06407 | 0.12567 | -0.00068138 | -0.003106 | -0.062256 | -0.0060606 | 0.061021 | 0.074236 | 0.0035953 | -0.0087435 | 60.2509 | 60.4294 | 0.050354 | -61.3907 | 60.2325 | -61.2991 | -61.2671 | -61.0703 | 0.10071 | -61.5463 | 60.2325 | 60.2509 | -61.2625 | -61.4227 | 0.022888 | 0.054931 | -0.091553 | 121.7514 | -0.068665 | -0.1236 | -0.073243 | 0.059509 | -0.10071 | -0.091553 | 0.25177 | -0.22431 | -0.1236 | -0.073243 | 121.5546 | 121.5729 | 61.3724 | -121.5912 | 121.5546 | 121.5729 | 61.4227 | -121.7468
752.6719 | 121.9437 | -61.2762 | 60.2875 | 0.071411 | 0.014084 | 0.07229 | 0.065351 | 0.12866 | -0.0017496 | -0.0041742 | 0.22003 | -0.0039244 | 0.062517 | 0.073595 | 0.0025271 | -0.0095981 | 60.173 | 60.3424 | -0.11902 | -61.4594 | 60.2371 | -61.3449 | -61.2946 | -61.1343 | -0.064087 | -61.615 | 60.2005 | 60.2005 | -61.2762 | -61.4365 | -0.068665 | -0.018311 | -0.050354 | 121.6187 | -0.18311 | -0.16479 | -0.11444 | 0 | -0.16022 | -0.086976 | 0.14191 | -0.33874 | -0.17853 | -0.086976 | 121.5134 | 121.4493 | 61.1572 | -121.582 | 121.4767 | 121.4767 | 61.2122 | -121.7239
754.3594 | 121.8933 | -61.29 | 60.3516 | -0.15747 | 0.020279 | 0.073145 | 0.068769 | 0.12738 | -0.00025418 | -0.0024652 | -0.062256 | -0.006915 | 0.062944 | 0.073595 | 0.0018863 | -0.0068209 | 60.2463 | 60.4111 | 0.091553 | -61.3724 | 60.2692 | -61.3083 | -61.2854 | -61.084 | 0.13733 | -61.528 | 60.26 | 60.2509 | -61.2442 | -61.3861 | -0.018311 | 0.004578 | -0.082397 | 121.701 | -0.082397 | -0.086975 | -0.10529 | 0.045776 | -0.09613 | -0.091552 | 0.20599 | -0.23804 | -0.14191 | -0.10071 | 121.5591 | 121.5363 | 61.3815 | -121.637 | 121.55 | 121.5408 | 61.4273 | -121.7377
756.0938 | 121.9482 | -61.203 | 60.3882 | -0.12695 | 0.016007 | 0.073999 | 0.067701 | 0.12802 | -0.010295 | -0.0056696 | 0.052185 | -0.007556 | 0.061449 | 0.071245 | -0.0015317 | -0.0083163 | 60.347 | 60.5759 | 0.21057 | -61.2946 | 60.2509 | -61.2213 | -61.1984 | -60.9146 | 0.31128 | -61.3541 | 60.26 | 60.2829 | -61.1938 | -61.3083 | -0.01831 | 0.004578 | -0.13733 | 121.7789 | -0.091553 | -0.096131 | -0.041199 | 0.009155 | -0.10529 | -0.12817 | 0.28839 | -0.15106 | -0.045776 | -0.10529 | 121.4539 | 121.55 | 61.4136 | -121.5866 | 121.463 | 121.4859 | 61.5143 | -121.6965
757.8594 | 121.9666 | -61.2808 | 60.2783 | 0.12482 | 0.016861 | 0.074213 | 0.064711 | 0.12824 | -0.0023904 | -0.0046014 | 0.18188 | -0.0045652 | 0.063371 | 0.071673 | 0.0040225 | -0.0098117 | 60.1822 | 60.3195 | -0.1236 | -61.4548 | 60.228 | -61.3495 | -61.2946 | -61.1023 | -0.050354 | -61.5601 | 60.2051 | 60.1685 | -61.2854 | -61.4273 | -0.068664 | -0.013733 | -0.050354 | 121.6003 | -0.17395 | -0.16022 | -0.09613 | -0.004577 | -0.14648 | -0.073242 | 0.17853 | -0.27924 | -0.13275 | -0.10986 | 121.5088 | 121.463 | 61.1572 | -121.5729 | 121.4859 | 121.4493 | 61.2305 | -121.7056
759.5469 | 121.9574 | -61.2762 | 60.2783 | 0.14008 | 0.018997 | 0.072931 | 0.063002 | 0.12909 | -0.00068138 | -0.0039606 | 0.22003 | -0.0060606 | 0.061235 | 0.071245 | 0.0070133 | -0.0076755 | 60.1822 | 60.3561 | -0.11444 | -61.4502 | 60.1822 | -61.3266 | -61.2991 | -61.0748 | -0.022888 | -61.5509 | 60.1913 | 60.1364 | -61.2717 | -61.4227 | -0.050354 | -0.022888 | -0.09613 | 121.6324 | -0.17395 | -0.15106 | -0.09613 | 0.004578 | -0.14648 | -0.086975 | 0.20142 | -0.27466 | -0.12817 | -0.14191 | 121.4584 | 121.4584 | 61.1618 | -121.5775 | 121.4676 | 121.4127 | 61.2534 | -121.701
761.2812 | 121.9437 | -61.2946 | 60.2875 | 0.15533 | 0.016434 | 0.071649 | 0.063643 | 0.12824 | -0.001536 | -0.0018244 | 0.20477 | -0.0064878 | 0.061449 | 0.072954 | 0.0048769 | -0.0087435 | 60.1685 | 60.3882 | -0.09613 | -61.4502 | 60.1913 | -61.3174 | -61.3083 | -61.0657 | 0.013733 | -61.5372 | 60.1913 | 60.1639 | -61.2762 | -61.4365 | -0.022888 | -0.013733 | -0.096131 | 121.6827 | -0.15564 | -0.14191 | -0.11902 | 0.018311 | -0.14191 | -0.096131 | 0.22888 | -0.24261 | -0.10071 | -0.1236 | 121.4859 | 121.463 | 61.1984 | -121.5958 | 121.4859 | 121.4584 | 61.3083 | -121.7239
763.0469 | 121.9711 | -61.2122 | 60.3699 | 0.0027468 | 0.014084 | 0.07464 | 0.067274 | 0.12717 | -0.0079446 | -0.0069512 | 0.097962 | -0.0094786 | 0.061876 | 0.070818 | -0.0013181 | -0.0063937 | 60.2554 | 60.4797 | 0.091553 | -61.3449 | 60.2509 | -61.2442 | -61.2259 | -60.9924 | 0.17395 | -61.4319 | 60.2646 | 60.26 | -61.1664 | -61.3495 | -0.032044 | -0.013733 | -0.11902 | 121.6919 | -0.13275 | -0.11902 | -0.11444 | 0.045776 | -0.13733 | -0.10529 | 0.21973 | -0.21973 | -0.082398 | -0.10986 | 121.463 | 121.4676 | 61.3037 | -121.5958 | 121.4767 | 121.4722 | 61.3861 | -121.7194
764.7344 | 121.9299 | -61.1847 | 60.3882 | -0.11169 | 0.014511 | 0.075708 | 0.065992 | 0.12888 | -0.0068766 | -0.0056696 | 0.021668 | -0.0096922 | 0.062517 | 0.071673 | -0.0013181 | -0.0091709 | 60.347 | 60.5804 | 0.21057 | -61.2946 | 60.2463 | -61.203 | -61.203 | -60.9375 | 0.27924 | -61.3632 | 60.2463 | 60.2692 | -61.1526 | -61.3174 | -0.018311 | -0.018311 | -0.14191 | 121.7651 | -0.10986 | -0.091553 | -0.041199 | 0.032043 | -0.13275 | -0.14191 | 0.24719 | -0.17853 | -0.045776 | -0.11902 | 121.431 | 121.5317 | 61.3953 | -121.5912 | 121.431 | 121.4539 | 61.4639 | -121.7056
766.4688 | 121.9299 | -61.2076 | 60.3745 | -0.0048827 | 0.012802 | 0.072931 | 0.066847 | 0.12567 | -0.0047404 | -0.0052424 | 0.12085 | -0.0090512 | 0.060808 | 0.071032 | 0.0014591 | -0.0085299 | 60.2463 | 60.466 | 0.068665 | -61.3586 | 60.2554 | -61.2625 | -61.2259 | -61.0336 | 0.10529 | -61.4731 | 60.2737 | 60.228 | -61.2076 | -61.3815 | -0.054931 | -0.01831 | -0.11902 | 121.6736 | -0.15106 | -0.13275 | -0.12817 | 0 | -0.17395 | -0.10071 | 0.17395 | -0.2655 | -0.091552 | -0.14648 | 121.463 | 121.4539 | 61.2762 | -121.6003 | 121.4813 | 121.4355 | 61.3129 | -121.756
768.2031 | 121.907 | -61.203 | 60.4111 | -0.18036 | 0.015366 | 0.073572 | 0.070051 | 0.13059 | -0.0045266 | -0.0060968 | -0.10803 | -0.008624 | 0.062303 | 0.072954 | -3.629e-05 | -0.0093845 | 60.379 | 60.5942 | 0.25635 | -61.29 | 60.3012 | -61.1984 | -61.1847 | -60.9421 | 0.28839 | -61.409 | 60.2737 | 60.2829 | -61.1618 | -61.3174 | 0.004578 | 0.018311 | -0.10986 | 121.7972 | -0.086975 | -0.10529 | -0.032044 | 0.041199 | -0.11444 | -0.13733 | 0.26093 | -0.20599 | -0.091553 | -0.12817 | 121.5042 | 121.582 | 61.4594 | -121.5958 | 121.4767 | 121.4859 | 61.4914 | -121.7285
769.9531 | 121.9254 | -61.2488 | 60.3241 | 0.17059 | 0.01857 | 0.071649 | 0.064711 | 0.13059 | 0.00017302 | -0.0043878 | 0.20477 | -0.007556 | 0.061876 | 0.073595 | 0.0046633 | -0.0093845 | 60.2509 | 60.4477 | 0.013733 | -61.3632 | 60.1547 | -61.3358 | -61.2671 | -61.0199 | 0.059509 | -61.5097 | 60.173 | 60.1547 | -61.2579 | -61.4182 | -0.086975 | -0.018311 | -0.16937 | 121.6965 | -0.11444 | -0.09613 | -0.073243 | -0.009156 | -0.16937 | -0.15106 | 0.22888 | -0.26093 | -0.091553 | -0.16937 | 121.4035 | 121.4996 | 61.2625 | -121.5912 | 121.4218 | 121.4035 | 61.3083 | -121.7422
771.625 | 121.9666 | -61.2625 | 60.3012 | 0.14008 | 0.01558 | 0.071222 | 0.062147 | 0.12781 | -0.00046778 | -0.0046014 | 0.11322 | -0.005206 | 0.063371 | 0.072741 | 0.0046633 | -0.010666 | 60.2325 | 60.4248 | -0.045776 | -61.4044 | 60.1639 | -61.3266 | -61.2854 | -61.0382 | 0.009155 | -61.5326 | 60.1868 | 60.1501 | -61.2579 | -61.4044 | -0.064087 | -0.022888 | -0.13733 | 121.6873 | -0.14191 | -0.11902 | -0.068664 | 0.004577 | -0.14191 | -0.11444 | 0.2243 | -0.27008 | -0.12817 | -0.15106 | 121.4264 | 121.4951 | 61.2167 | -121.5866 | 121.4493 | 121.4127 | 61.2717 | -121.7056
773.375 | 121.9437 | -61.2762 | 60.3012 | 0.063782 | 0.015152 | 0.073785 | 0.064497 | 0.12759 | 0.00060022 | -0.0024652 | 0.159 | -0.0056332 | 0.060381 | 0.071886 | 0.0055179 | -0.0093845 | 60.2509 | 60.4614 | -0.018311 | -61.3907 | 60.173 | -61.3083 | -61.2946 | -61.0474 | 0.041199 | -61.5326 | 60.1776 | 60.1501 | -61.2579 | -61.4044 | -0.032044 | -0.018311 | -0.12817 | 121.7377 | -0.11444 | -0.09613 | -0.050354 | 0.01831 | -0.12817 | -0.1236 | 0.22888 | -0.25635 | -0.12817 | -0.15106 | 121.4493 | 121.5271 | 61.2579 | -121.5958 | 121.4539 | 121.4264 | 61.3174 | -121.7056
775.125 | 121.8887 | -61.2488 | 60.3516 | -0.18036 | 0.019425 | 0.072504 | 0.068983 | 0.12909 | 0.001882 | -0.003747 | -0.16907 | -0.0054196 | 0.063158 | 0.071673 | 0.0027407 | -0.011307 | 60.2463 | 60.4202 | 0.10986 | -61.3815 | 60.2829 | -61.2671 | -61.235 | -61.0611 | 0.15564 | -61.5372 | 60.3195 | 60.2692 | -61.2213 | -61.377 | -0.018311 | 0.013733 | -0.068664 | 121.669 | -0.13275 | -0.14649 | -0.10529 | 0.027466 | -0.12817 | -0.032043 | 0.18768 | -0.28839 | -0.16022 | -0.082397 | 121.5317 | 121.4951 | 61.3586 | -121.5866 | 121.5683 | 121.5179 | 61.4044 | -121.7285
776.8125 | 121.9162 | -61.2305 | 60.3378 | 0.11719 | 0.015152 | 0.07464 | 0.06642 | 0.1293 | -0.0038858 | -0.004815 | 0.18951 | -0.007556 | 0.060381 | 0.069964 | 0.0033817 | -0.0098117 | 60.2417 | 60.4935 | 0.013733 | -61.377 | 60.2005 | -61.2991 | -61.2579 | -61.0107 | 0.064087 | -61.4822 | 60.2097 | 60.1501 | -61.2488 | -61.3953 | -0.068664 | -0.027466 | -0.13733 | 121.7239 | -0.14648 | -0.11902 | -0.096131 | -0.01831 | -0.16479 | -0.12817 | 0.21973 | -0.25177 | -0.086975 | -0.18768 | 121.431 | 121.4722 | 61.2442 | -121.5958 | 121.4401 | 121.3806 | 61.2946 | -121.7331
778.5625 | 121.9162 | -61.2488 | 60.3699 | 0.025635 | 0.017075 | 0.073145 | 0.069197 | 0.12802 | -0.0053812 | -0.0069512 | 0.13611 | -0.0079832 | 0.065507 | 0.071459 | 0.0010317 | -0.0091709 | 60.2325 | 60.4752 | 0.045776 | -61.3678 | 60.2325 | -61.2762 | -61.2488 | -61.0199 | 0.10071 | -61.4822 | 60.2417 | 60.228 | -61.1893 | -61.3586 | -0.027466 | 0 | -0.13733 | 121.7239 | -0.11902 | -0.11902 | -0.13733 | 0.059509 | -0.10986 | -0.12817 | 0.22888 | -0.23346 | -0.1236 | -0.14191 | 121.4813 | 121.4813 | 61.2946 | -121.6187 | 121.4905 | 121.4767 | 61.3495 | -121.7285
780.3281 | 121.8475 | -61.2946 | 60.3241 | 0.063782 | 0.015366 | 0.07229 | 0.065351 | 0.12845 | 0.00060022 | -0.0052424 | 0.097962 | -0.003497 | 0.063371 | 0.072527 | 0.0048769 | -0.010453 | 60.141 | 60.2875 | -0.1236 | -61.4868 | 60.2417 | -61.3541 | -61.3358 | -61.1572 | -0.09613 | -61.6608 | 60.228 | 60.1776 | -61.3129 | -61.4548 | -0.059509 | -0.041198 | -0.082398 | 121.582 | -0.19226 | -0.15106 | -0.18311 | -0.01831 | -0.16022 | -0.096131 | 0.13733 | -0.36621 | -0.20599 | -0.14648 | 121.5363 | 121.4355 | 61.171 | -121.6599 | 121.5225 | 121.4722 | 61.1984 | -121.7789
782.0156 | 121.9208 | -61.2442 | 60.3333 | 0.094299 | 0.014939 | 0.074213 | 0.066206 | 0.12781 | -0.0036722 | -0.0028924 | 0.23529 | -0.006915 | 0.063158 | 0.070605 | 0.0016727 | -0.0083163 | 60.2463 | 60.5026 | 0.036621 | -61.3907 | 60.1959 | -61.2717 | -61.2534 | -61.0153 | 0.068665 | -61.4868 | 60.2005 | 60.1685 | -61.2213 | -61.3724 | -0.027465 | -0.009155 | -0.13733 | 121.7468 | -0.14648 | -0.13733 | -0.086975 | 0.022889 | -0.12817 | -0.13275 | 0.22888 | -0.24261 | -0.11444 | -0.1648 | 121.4401 | 121.4905 | 61.2808 | -121.5866 | 121.4447 | 121.4127 | 61.3129 | -121.7056
783.7656 | 121.9162 | -61.2488 | 60.3607 | 0.079041 | 0.014084 | 0.075922 | 0.065992 | 0.12888 | -0.0070902 | -0.0041742 | 0.17426 | -0.0088376 | 0.060808 | 0.068896 | 0.00081811 | -0.0053257 | 60.2463 | 60.4935 | 0.032043 | -61.3632 | 60.228 | -61.2671 | -61.2396 | -61.0245 | 0.073242 | -61.496 | 60.228 | 60.173 | -61.2213 | -61.3815 | -0.018311 | 0.009155 | -0.13275 | 121.7422 | -0.11444 | -0.1236 | -0.11444 | 0.027466 | -0.13275 | -0.13275 | 0.2243 | -0.24719 | -0.11444 | -0.18768 | 121.4767 | 121.4951 | 61.2808 | -121.6003 | 121.4767 | 121.4218 | 61.322 | -121.7422
785.5156 | 121.9482 | -61.1664 | 60.3973 | -0.096436 | 0.018143 | 0.073999 | 0.069197 | 0.13101 | -0.0051676 | -0.0039606 | -0.024109 | -0.0094786 | 0.061449 | 0.070391 | 0.00017731 | -0.011094 | 60.3378 | 60.5713 | 0.19684 | -61.2854 | 60.2921 | -61.2167 | -61.1893 | -60.9238 | 0.2655 | -61.4044 | 60.26 | 60.2188 | -61.1526 | -61.3174 | -0.050354 | -0.022888 | -0.10529 | 121.7377 | -0.11902 | -0.09613 | -0.059509 | 0.013733 | -0.15106 | -0.13733 | 0.24262 | -0.23804 | -0.086975 | -0.17853 | 121.4584 | 121.5042 | 61.3632 | -121.5866 | 121.4264 | 121.3852 | 61.4319 | -121.7148
787.2031 | 121.8246 | -61.2488 | 60.4202 | -0.22614 | 0.01622 | 0.071863 | 0.066847 | 0.1308 | -0.00046778 | -0.0052424 | -0.14618 | -0.0039244 | 0.063371 | 0.071886 | 0.0012455 | -0.010453 | 60.2829 | 60.4706 | 0.14648 | -61.3495 | 60.2966 | -61.2442 | -61.2305 | -61.0428 | 0.17395 | -61.5143 | 60.3058 | 60.2875 | -61.203 | -61.3358 | 0.004577 | 0.01831 | -0.1236 | 121.7194 | -0.10071 | -0.11902 | -0.13733 | 0.045776 | -0.086975 | -0.11444 | 0.20599 | -0.2655 | -0.17853 | -0.13275 | 121.5454 | 121.5317 | 61.3953 | -121.6507 | 121.5546 | 121.5363 | 61.4227 | -121.756
788.9688 | 121.8933 | -61.2534 | 60.347 | 0.094299 | 0.014511 | 0.073358 | 0.065779 | 0.12567 | -0.0019632 | -0.0035334 | 0.13611 | -0.0084104 | 0.05974 | 0.071459 | 0.00017731 | -0.0078891 | 60.2783 | 60.4752 | 0.036621 | -61.3724 | 60.2097 | -61.2717 | -61.2442 | -61.0153 | 0.082397 | -61.5051 | 60.2463 | 60.2234 | -61.1984 | -61.4136 | -0.01831 | 0.009155 | -0.13733 | 121.7285 | -0.11902 | -0.12817 | -0.068665 | 0.054932 | -0.16022 | -0.10071 | 0.23804 | -0.25177 | -0.091553 | -0.1236 | 121.463 | 121.5317 | 61.29 | -121.5912 | 121.4996 | 121.4767 | 61.3358 | -121.7606
790.7188 | 121.8933 | -61.2167 | 60.3561 | 0.10956 | 0.016861 | 0.07464 | 0.064497 | 0.12695 | -0.004954 | -0.0041742 | 0.14374 | -0.0088376 | 0.058672 | 0.070818 | 0.0018863 | -0.0085299 | 60.2646 | 60.4797 | 0.041199 | -61.377 | 60.228 | -61.2717 | -61.2396 | -61.0107 | 0.07782 | -61.4868 | 60.2371 | 60.1959 | -61.2122 | -61.3815 | -0.054931 | -0.022888 | -0.12817 | 121.6965 | -0.16022 | -0.13733 | -0.091553 | 0.004578 | -0.1648 | -0.11902 | 0.20599 | -0.27008 | -0.10528 | -0.16022 | 121.4447 | 121.4813 | 61.2579 | -121.5958 | 121.4539 | 121.4127 | 61.2946 | -121.7377
792.4062 | 121.9482 | -61.2808 | 60.2783 | 0.16296 | 0.017075 | 0.071436 | 0.06172 | 0.12866 | 0.00017302 | -0.0035334 | 0.22766 | -0.007556 | 0.059953 | 0.072741 | 0.0042361 | -0.012375 | 60.2371 | 60.4248 | -0.068665 | -61.4227 | 60.1822 | -61.3129 | -61.29 | -61.0336 | 0.022888 | -61.5189 | 60.2097 | 60.1593 | -61.2488 | -61.3998 | -0.032043 | -0.009155 | -0.09613 | 121.7056 | -0.14191 | -0.13275 | -0.041198 | 0.032044 | -0.11902 | -0.068664 | 0.24719 | -0.23804 | -0.11902 | -0.11902 | 121.463 | 121.5179 | 61.2122 | -121.5683 | 121.4905 | 121.4401 | 61.3037 | -121.6782
794.1562 | 121.8658 | -61.2167 | 60.4111 | -0.20325 | 0.01622 | 0.07464 | 0.067488 | 0.13016 | -0.0051676 | -0.003747 | -0.077515 | -0.0079832 | 0.060594 | 0.069536 | 0.0033817 | -0.0089573 | 60.3424 | 60.5988 | 0.26093 | -61.2808 | 60.2783 | -61.1938 | -61.1938 | -60.9512 | 0.31586 | -61.4136 | 60.2921 | 60.228 | -61.1893 | -61.3174 | 0.022888 | 0.022888 | -0.13275 | 121.8155 | -0.064087 | -0.086975 | -0.068665 | 0.027466 | -0.10071 | -0.11902 | 0.2655 | -0.19684 | -0.09613 | -0.18311 | 121.4951 | 121.5591 | 61.4777 | -121.6049 | 121.5088 | 121.4447 | 61.5326 | -121.7285
795.9062 | 121.8338 | -61.2259 | 60.4202 | -0.18799 | 0.020066 | 0.072076 | 0.070051 | 0.13123 | -0.0028178 | -0.0046014 | -0.16907 | -0.0084104 | 0.062944 | 0.071886 | 0.0020999 | -0.01088 | 60.3561 | 60.553 | 0.21515 | -61.2991 | 60.2783 | -61.2122 | -61.2167 | -61.0107 | 0.27008 | -61.4456 | 60.2966 | 60.2966 | -61.1847 | -61.3174 | 0.013733 | 0.009155 | -0.14191 | 121.7789 | -0.073242 | -0.082397 | -0.064087 | 0.041199 | -0.091553 | -0.1236 | 0.21515 | -0.21973 | -0.12817 | -0.1236 | 121.5042 | 121.582 | 61.441 | -121.637 | 121.5225 | 121.5225 | 61.496 | -121.7377
797.5938 | 121.8979 | -61.3129 | 60.2829 | 0.11719 | 0.017075 | 0.073785 | 0.062574 | 0.12824 | 0.0012412 | -0.0033196 | 0.075073 | -0.0039244 | 0.062517 | 0.071886 | 0.0070133 | -0.0085299 | 60.1685 | 60.3241 | -0.14648 | -61.4822 | 60.2463 | -61.3586 | -61.3312 | -61.116 | -0.082397 | -61.6333 | 60.2325 | 60.1868 | -61.2762 | -61.4502 | -0.045777 | -0.018311 | -0.036621 | 121.637 | -0.16937 | -0.15106 | -0.11444 | 0.036621 | -0.13733 | -0.050354 | 0.19684 | -0.32044 | -0.18311 | -0.09613 | 121.5591 | 121.4813 | 61.1664 | -121.6141 | 121.5454 | 121.4996 | 61.2305 | -121.7331
799.3438 | 121.8704 | -61.2167 | 60.4019 | -0.21088 | 0.016007 | 0.073145 | 0.065351 | 0.1293 | -0.0045266 | -0.0041742 | -0.085144 | -0.0071286 | 0.062517 | 0.069964 | 0.00081811 | -0.0087435 | 60.3149 | 60.5896 | 0.23346 | -61.2854 | 60.2509 | -61.2122 | -61.1801 | -60.9604 | 0.29297 | -61.409 | 60.2875 | 60.228 | -61.171 | -61.3312 | 0.004578 | 0.036621 | -0.15106 | 121.8063 | -0.068664 | -0.10529 | -0.086976 | 0.045777 | -0.11444 | -0.11444 | 0.25635 | -0.19226 | -0.07782 | -0.17395 | 121.4676 | 121.5317 | 61.4502 | -121.582 | 121.5042 | 121.4447 | 61.5097 | -121.7331
801.0781 | 121.8613 | -61.2442 | 60.3836 | -0.24902 | 0.020066 | 0.07464 | 0.06941 | 0.13037 | -0.003245 | -0.0050286 | -0.16907 | -0.0060606 | 0.061662 | 0.072527 | 0.00081811 | -0.0098117 | 60.2692 | 60.4385 | 0.1236 | -61.3632 | 60.3149 | -61.2717 | -61.2167 | -61.0657 | 0.15106 | -61.5372 | 60.3241 | 60.2692 | -61.2259 | -61.3724 | -0.027465 | 0.027466 | -0.068665 | 121.6827 | -0.11902 | -0.14648 | -0.11444 | 0.018311 | -0.12817 | -0.059509 | 0.17853 | -0.29297 | -0.1648 | -0.11444 | 121.5591 | 121.5134 | 61.3678 | -121.6003 | 121.5683 | 121.5134 | 61.3953 | -121.756
802.8125 | 121.8155 | -61.3403 | 60.3195 | -0.050659 | 0.020279 | 0.069513 | 0.065565 | 0.12909 | 0.0027364 | -0.002038 | 0.014038 | -0.0060606 | 0.062517 | 0.073168 | 0.0046633 | -0.0093845 | 60.2417 | 60.3836 | -0.013733 | -61.4319 | 60.2325 | -61.322 | -61.3037 | -61.1481 | -0.013733 | -61.6333 | 60.2371 | 60.1547 | -61.2808 | -61.4319 | 0.018311 | 0.036621 | -0.086975 | 121.7239 | -0.091553 | -0.12817 | -0.07782 | 0.059509 | -0.091553 | -0.082397 | 0.19226 | -0.29297 | -0.20142 | -0.16479 | 121.5729 | 121.582 | 61.3266 | -121.6232 | 121.5775 | 121.4951 | 61.3266 | -121.7514
804.5625 | 121.8155 | -61.3129 | 60.3424 | -0.0354 | 0.017075 | 0.070795 | 0.065138 | 0.12952 | 0.0010276 | -0.0018244 | 0.014038 | -0.003497 | 0.062944 | 0.074663 | 0.0053043 | -0.0081027 | 60.2234 | 60.4019 | -0.013733 | -61.4319 | 60.2371 | -61.3403 | -61.3037 | -61.1298 | -0.009155 | -61.6425 | 60.2417 | 60.1913 | -61.29 | -61.4594 | -0.027466 | 0.009155 | -0.10529 | 121.7148 | -0.11902 | -0.12817 | -0.11902 | 0.022888 | -0.14648 | -0.10071 | 0.1831 | -0.32959 | -0.18311 | -0.15106 | 121.55 | 121.5363 | 61.2991 | -121.6461 | 121.5546 | 121.5042 | 61.3037 | -121.8018
806.2344 | 121.962 | -61.2762 | 60.2966 | 0.14008 | 0.017502 | 0.071222 | 0.062361 | 0.12802 | -0.0040994 | -0.0018244 | 0.18951 | -0.005847 | 0.061662 | 0.071886 | 0.0050907 | -0.0091709 | 60.1868 | 60.3973 | -0.082397 | -61.4273 | 60.2051 | -61.3403 | -61.29 | -61.0519 | 0.004578 | -61.528 | 60.1959 | 60.1456 | -61.2671 | -61.4136 | -0.064087 | -0.013733 | -0.091553 | 121.6736 | -0.15106 | -0.13733 | -0.10986 | 0.009155 | -0.13733 | -0.10071 | 0.2243 | -0.25177 | -0.11444 | -0.15106 | 121.4813 | 121.463 | 61.1938 | -121.5866 | 121.4722 | 121.4218 | 61.2808 | -121.7102
807.9219 | 121.8613 | -61.2762 | 60.3424 | -0.12695 | 0.017289 | 0.074426 | 0.067274 | 0.13059 | -0.0013224 | -0.0018244 | -0.085144 | -0.0071286 | 0.063371 | 0.071673 | 0.0025271 | -0.0083163 | 60.2509 | 60.4568 | 0.068665 | -61.3861 | 60.2692 | -61.29 | -61.2671 | -61.0748 | 0.11902 | -61.5372 | 60.2554 | 60.2097 | -61.2534 | -61.4182 | -0.013733 | 0.009155 | -0.073242 | 121.7331 | -0.10986 | -0.11902 | -0.091553 | 0.022888 | -0.14191 | -0.086975 | 0.20142 | -0.26093 | -0.11902 | -0.13275 | 121.5454 | 121.5271 | 61.3449 | -121.6095 | 121.5317 | 121.4859 | 61.3953 | -121.7606
809.6719 | 121.843 | -61.2488 | 60.434 | -0.15747 | 0.014939 | 0.072076 | 0.068342 | 0.12738 | -0.006022 | -0.005456 | -0.077515 | -0.0062742 | 0.062944 | 0.073168 | 0.00017731 | -0.0081027 | 60.3012 | 60.5667 | 0.24261 | -61.2946 | 60.2692 | -61.2305 | -61.1984 | -61.0016 | 0.29297 | -61.4044 | 60.2875 | 60.2737 | -61.1664 | -61.3174 | 0.01831 | 0.050354 | -0.16479 | 121.8155 | -0.045777 | -0.096131 | -0.13275 | 0.082397 | -0.068665 | -0.14648 | 0.24719 | -0.15564 | -0.086975 | -0.16022 | 121.5179 | 121.55 | 61.4914 | -121.6324 | 121.5363 | 121.5225 | 61.5417 | -121.7514
811.3438 | 121.8384 | -61.235 | 60.4294 | -0.11169 | 0.019211 | 0.074213 | 0.069624 | 0.12973 | -0.0036722 | -0.0052424 | -0.14618 | -0.0049924 | 0.064653 | 0.075731 | -0.00046349 | -0.0085299 | 60.2417 | 60.4477 | 0.1236 | -61.3815 | 60.2966 | -61.2442 | -61.2305 | -61.0565 | 0.18768 | -61.5097 | 60.347 | 60.3195 | -61.1893 | -61.3495 | -0.009156 | 0.004577 | -0.13275 | 121.6827 | -0.14649 | -0.15106 | -0.18768 | 0.045776 | -0.11444 | -0.082397 | 0.17853 | -0.27466 | -0.16022 | -0.10986 | 121.5317 | 121.4767 | 61.3586 | -121.6599 | 121.582 | 121.5546 | 61.4227 | -121.7789
813.1094 | 121.9528 | -61.2808 | 60.26 | 0.08667 | 0.01857 | 0.071649 | 0.063856 | 0.12888 | -0.00046778 | -0.0041742 | 0.19714 | -0.005847 | 0.061235 | 0.071886 | 0.0055179 | -0.0095981 | 60.1868 | 60.3378 | -0.11444 | -61.4639 | 60.2234 | -61.3495 | -61.3129 | -61.116 | -0.045776 | -61.5646 | 60.2142 | 60.1639 | -61.2762 | -61.4548 | -0.068664 | -0.032043 | -0.036621 | 121.6187 | -0.18311 | -0.15106 | -0.073242 | 0.004578 | -0.17395 | -0.045777 | 0.16479 | -0.28381 | -0.10986 | -0.096131 | 121.5042 | 121.4676 | 61.1664 | -121.5729 | 121.4951 | 121.4447 | 61.235 | -121.7148
814.7969 | 121.9528 | -61.2625 | 60.2829 | 0.14008 | 0.017502 | 0.073572 | 0.06407 | 0.12824 | -0.004313 | -0.0018244 | 0.23529 | -0.0043516 | 0.05974 | 0.070177 | 0.0067997 | -0.0078891 | 60.2097 | 60.4065 | -0.07782 | -61.4182 | 60.1822 | -61.3083 | -61.3037 | -61.0474 | 0.032043 | -61.5143 | 60.2005 | 60.1776 | -61.2534 | -61.409 | -0.045777 | -0.041199 | -0.10071 | 121.669 | -0.15564 | -0.11444 | -0.073242 | 0.009155 | -0.14648 | -0.082398 | 0.21515 | -0.25177 | -0.10529 | -0.10529 | 121.4447 | 121.4722 | 61.1847 | -121.5866 | 121.463 | 121.4401 | 61.2946 | -121.6919
816.5312 | 121.9116 | -61.2808 | 60.2966 | 0.10956 | 0.017075 | 0.074213 | 0.062788 | 0.12845 | 0.00017302 | -0.003747 | 0.097962 | -0.0056332 | 0.059526 | 0.070605 | 0.0042361 | -0.0070345 | 60.1639 | 60.3104 | -0.14191 | -61.4822 | 60.2142 | -61.3541 | -61.3358 | -61.1526 | -0.091553 | -61.6241 | 60.2325 | 60.173 | -61.2671 | -61.4456 | -0.073242 | -0.054931 | -0.082398 | 121.5912 | -0.20142 | -0.14648 | -0.13275 | 0.013733 | -0.1648 | -0.064087 | 0.12817 | -0.34332 | -0.17853 | -0.1236 | 121.4951 | 121.4447 | 61.1389 | -121.6324 | 121.5134 | 121.4539 | 61.1893 | -121.7422
818.2656 | 121.9574 | -61.2808 | 60.2875 | 0.08667 | 0.016007 | 0.073785 | 0.064924 | 0.12973 | -0.0019632 | -0.004815 | 0.159 | -0.0060606 | 0.061235 | 0.071886 | 0.0044497 | -0.0081027 | 60.1776 | 60.3378 | -0.1236 | -61.4685 | 60.2737 | -61.3403 | -61.3403 | -61.1389 | -0.082397 | -61.6058 | 60.2234 | 60.1822 | -61.2854 | -61.4456 | -0.059509 | -0.059509 | -0.013733 | 121.6187 | -0.18768 | -0.12817 | -0.10986 | -0.004577 | -0.1648 | -0.064087 | 0.14191 | -0.32501 | -0.16022 | -0.10529 | 121.5546 | 121.4584 | 61.1572 | -121.6278 | 121.5042 | 121.463 | 61.1984 | -121.7331
820.0156 | 121.8704 | -61.3129 | 60.3104 | 0.079041 | 0.016434 | 0.072717 | 0.065138 | 0.12824 | -0.00046778 | -0.0028924 | 0.15137 | -0.0056332 | 0.05974 | 0.073382 | 0.0027407 | -0.010453 | 60.1227 | 60.2921 | -0.13275 | -61.4777 | 60.2188 | -61.3724 | -61.3449 | -61.1664 | -0.09613 | -61.6516 | 60.228 | 60.2051 | -61.3037 | -61.4639 | -0.059509 | -0.032044 | -0.091553 | 121.6049 | -0.16479 | -0.13275 | -0.18768 | 0.009155 | -0.15106 | -0.082398 | 0.14648 | -0.33875 | -0.18768 | -0.10529 | 121.5317 | 121.4355 | 61.1801 | -121.6553 | 121.5408 | 121.5179 | 61.2167 | -121.7743
821.75 | 121.8979 | -61.2991 | 60.2921 | 0.10193 | 0.016648 | 0.074426 | 0.06642 | 0.12952 | -0.001536 | -0.003747 | 0.14374 | -0.0032834 | 0.062089 | 0.073595 | 0.0031681 | -0.0078891 | 60.1364 | 60.2966 | -0.13733 | -61.4777 | 60.2142 | -61.3266 | -61.3083 | -61.1572 | -0.082397 | -61.6333 | 60.2325 | 60.2005 | -61.29 | -61.4365 | -0.027466 | -0.009156 | -0.07782 | 121.5958 | -0.17853 | -0.16937 | -0.15564 | 0.009155 | -0.13733 | -0.059509 | 0.14191 | -0.33417 | -0.19684 | -0.091553 | 121.5134 | 121.4355 | 61.1618 | -121.6003 | 121.5317 | 121.4996 | 61.2167 | -121.7285
823.4844 | 121.9345 | -61.2213 | 60.3745 | 0.063782 | 0.012162 | 0.072717 | 0.066633 | 0.13016 | -0.0073038 | -0.002038 | 0.18188 | -0.0088376 | 0.061662 | 0.070391 | -3.629e-05 | -0.0066073 | 60.2463 | 60.466 | 0.041199 | -61.3815 | 60.2371 | -61.2534 | -61.2167 | -61.0519 | 0.086975 | -61.4868 | 60.26 | 60.2325 | -61.2076 | -61.377 | -0.032044 | 0.004577 | -0.13733 | 121.6873 | -0.16022 | -0.1648 | -0.12817 | 0.013732 | -0.15564 | -0.11444 | 0.16937 | -0.2655 | -0.10986 | -0.14191 | 121.4584 | 121.4676 | 61.2625 | -121.5912 | 121.4813 | 121.4539 | 61.3083 | -121.7514
825.2344 | 121.8704 | -61.2625 | 60.3928 | -0.23376 | 0.017075 | 0.075281 | 0.066206 | 0.12994 | -0.0028178 | -0.0056696 | -0.14618 | -0.005206 | 0.065294 | 0.070818 | 0.0038089 | -0.0078891 | 60.2554 | 60.434 | 0.10529 | -61.3815 | 60.3287 | -61.2671 | -61.2488 | -61.0886 | 0.13733 | -61.5372 | 60.3287 | 60.2829 | -61.2259 | -61.3495 | -0.004578 | 0.013733 | -0.064087 | 121.6965 | -0.11902 | -0.13275 | -0.13733 | 0.036621 | -0.086975 | -0.064087 | 0.17395 | -0.27466 | -0.18768 | -0.10986 | 121.5912 | 121.5179 | 61.3678 | -121.6415 | 121.5912 | 121.5454 | 61.3998 | -121.7422
826.9219 | 121.9116 | -61.2442 | 60.347 | 0.14771 | 0.011948 | 0.074213 | 0.062788 | 0.13016 | -0.0036722 | -0.0033196 | 0.23529 | -0.010547 | 0.060808 | 0.070818 | 0.0050907 | -0.0076755 | 60.2417 | 60.4568 | -0.004578 | -61.3907 | 60.1547 | -61.2946 | -61.2808 | -61.0474 | 0.054932 | -61.4914 | 60.1913 | 60.1639 | -61.2488 | -61.409 | -0.050354 | -0.036621 | -0.19226 | 121.7011 | -0.14648 | -0.10986 | -0.10529 | -0.004577 | -0.16479 | -0.15564 | 0.19684 | -0.24719 | -0.082397 | -0.18311 | 121.3989 | 121.4859 | 61.2396 | -121.6278 | 121.4355 | 121.4081 | 61.2991 | -121.756
828.6562 | 121.8979 | -61.2167 | 60.3882 | 0.063782 | 0.012802 | 0.07464 | 0.065138 | 0.12567 | -0.006663 | -0.0058832 | 0.18188 | -0.0084104 | 0.061662 | 0.071459 | 0.00060451 | -0.0074619 | 60.2646 | 60.4889 | 0.022888 | -61.377 | 60.2417 | -61.2717 | -61.2488 | -61.0382 | 0.073242 | -61.4822 | 60.2371 | 60.1913 | -61.2259 | -61.3907 | -0.054931 | -0.032043 | -0.14649 | 121.7056 | -0.16022 | -0.12817 | -0.1236 | -0.009155 | -0.17395 | -0.15106 | 0.17853 | -0.2655 | -0.091553 | -0.19684 | 121.4584 | 121.4813 | 61.2396 | -121.637 | 121.4539 | 121.4081 | 61.29 | -121.7789
830.4062 | 121.9299 | -61.29 | 60.2875 | 0.079041 | 0.018784 | 0.070795 | 0.06407 | 0.12738 | -0.00025418 | -0.0052424 | 0.10559 | -0.0062742 | 0.062517 | 0.071886 | 0.0038089 | -0.010453 | 60.1685 | 60.3333 | -0.11444 | -61.4731 | 60.2463 | -61.3449 | -61.3174 | -61.1252 | -0.082397 | -61.6196 | 60.2371 | 60.1868 | -61.2625 | -61.4319 | -0.054932 | -0.027466 | -0.041199 | 121.6232 | -0.18311 | -0.15564 | -0.11902 | 0.027466 | -0.14191 | -0.050354 | 0.16479 | -0.32959 | -0.18768 | -0.10071 | 121.5363 | 121.4584 | 61.1755 | -121.6049 | 121.5271 | 121.4767 | 61.2076 | -121.7194
832.1562 | 121.962 | -61.2946 | 60.2875 | 0.15533 | 0.014298 | 0.071863 | 0.06642 | 0.12994 | -0.0013224 | -0.0033196 | 0.17426 | -0.0071286 | 0.059526 | 0.071459 | 0.0044497 | -0.0083163 | 60.1868 | 60.3836 | -0.086975 | -61.441 | 60.1868 | -61.3495 | -61.2946 | -61.0748 | -0.004578 | -61.5509 | 60.2005 | 60.1639 | -61.2762 | -61.4136 | -0.054931 | 0 | -0.10071 | 121.6782 | -0.14648 | -0.14648 | -0.10071 | 0.018311 | -0.11902 | -0.086976 | 0.21973 | -0.25635 | -0.13733 | -0.1236 | 121.4813 | 121.4813 | 61.2076 | -121.582 | 121.4951 | 121.4584 | 61.29 | -121.701
833.8438 | 121.8475 | -61.29 | 60.3333 | -0.10406 | 0.019852 | 0.072717 | 0.068983 | 0.12973 | 0.00081382 | -0.005456 | -0.069885 | -0.005206 | 0.064867 | 0.073382 | 0.0029543 | -0.010453 | 60.2463 | 60.4431 | 0.064087 | -61.3815 | 60.2417 | -61.3174 | -61.2671 | -61.0703 | 0.10986 | -61.5372 | 60.2554 | 60.2005 | -61.2534 | -61.409 | -0.027466 | 0.022888 | -0.091553 | 121.7331 | -0.091553 | -0.11444 | -0.086975 | 0.036621 | -0.11902 | -0.07782 | 0.21973 | -0.24719 | -0.12817 | -0.13275 | 121.5317 | 121.5363 | 61.3541 | -121.6003 | 121.5454 | 121.4905 | 61.3998 | -121.7422
835.5938 | 121.8292 | -61.2167 | 60.4385 | -0.19562 | 0.01622 | 0.073572 | 0.065992 | 0.12845 | -0.0062356 | -0.003747 | -0.13855 | -0.0081968 | 0.064012 | 0.071673 | 0.0020999 | -0.010025 | 60.2966 | 60.5759 | 0.23804 | -61.2991 | 60.2829 | -61.2442 | -61.1984 | -61.0245 | 0.24719 | -61.4639 | 60.2829 | 60.26 | -61.1938 | -61.3495 | -0.027466 | 0.018311 | -0.15564 | 121.7926 | -0.082397 | -0.10071 | -0.14191 | 0.022888 | -0.13275 | -0.15564 | 0.19226 | -0.24719 | -0.11444 | -0.17853 | 121.4996 | 121.5134 | 61.4548 | -121.637 | 121.4996 | 121.4767 | 61.4639 | -121.788
837.3281 | 121.8933 | -61.2625 | 60.3424 | -0.11932 | 0.023056 | 0.07229 | 0.06642 | 0.13144 | 0.0010276 | -0.0035334 | -0.1004 | -0.005206 | 0.064867 | 0.074023 | 0.0031681 | -0.010025 | 60.2463 | 60.434 | 0.07782 | -61.3815 | 60.2692 | -61.2808 | -61.2717 | -61.0886 | 0.10986 | -61.5372 | 60.2692 | 60.2325 | -61.235 | -61.4273 | -0.018311 | -0.009155 | -0.073242 | 121.6965 | -0.11902 | -0.10986 | -0.09613 | 0.027466 | -0.16479 | -0.073242 | 0.17395 | -0.27466 | -0.10986 | -0.10986 | 121.5317 | 121.5088 | 61.3403 | -121.6141 | 121.5317 | 121.4951 | 61.3724 | -121.7697
839.0781 | 121.907 | -61.2534 | 60.3424 | 0.12482 | 0.019211 | 0.072504 | 0.066847 | 0.12845 | -0.0055948 | -0.0035334 | 0.19714 | -0.007556 | 0.062089 | 0.072314 | -0.00046349 | -0.0078891 | 60.2417 | 60.4752 | 0.013733 | -61.3861 | 60.173 | -61.29 | -61.2762 | -61.0336 | 0.073242 | -61.4868 | 60.1868 | 60.1501 | -61.2579 | -61.377 | -0.036621 | -0.022888 | -0.16937 | 121.7285 | -0.13275 | -0.10986 | -0.10071 | -0.004578 | -0.1236 | -0.15564 | 0.21973 | -0.23346 | -0.10986 | -0.19226 | 121.4264 | 121.4951 | 61.2671 | -121.6187 | 121.4401 | 121.4035 | 61.3266 | -121.7194
840.7656 | 121.9116 | -61.2167 | 60.3607 | 0.018005 | 0.013871 | 0.07464 | 0.064924 | 0.12845 | -0.006663 | -0.0046014 | 0.12848 | -0.0077696 | 0.060594 | 0.070177 | 0.0020999 | -0.0066073 | 60.2371 | 60.4752 | 0.045776 | -61.3541 | 60.2646 | -61.2854 | -61.235 | -61.0245 | 0.09613 | -61.4777 | 60.2646 | 60.2142 | -61.2076 | -61.377 | -0.068664 | -0.01831 | -0.096131 | 121.6919 | -0.13733 | -0.11902 | -0.1236 | 0.009155 | -0.16022 | -0.096131 | 0.19226 | -0.26093 | -0.10071 | -0.14648 | 121.4813 | 121.4539 | 61.2625 | -121.5958 | 121.4813 | 121.431 | 61.3129 | -121.7377
842.5156 | 121.9437 | -61.1984 | 60.4065 | -0.12695 | 0.016861 | 0.074426 | 0.067701 | 0.12802 | -0.008372 | -0.0050286 | -0.1004 | -0.0073422 | 0.063798 | 0.070391 | 0.0012455 | -0.0091709 | 60.3561 | 60.6125 | 0.25177 | -61.2808 | 60.2692 | -61.2305 | -61.1847 | -60.9283 | 0.32044 | -61.3678 | 60.2921 | 60.2646 | -61.1435 | -61.322 | -0.032044 | 0.013733 | -0.13733 | 121.8109 | -0.082398 | -0.096131 | -0.050354 | 0.054931 | -0.1236 | -0.11444 | 0.27008 | -0.16937 | -0.045777 | -0.14191 | 121.4676 | 121.5546 | 61.4502 | -121.5912 | 121.4905 | 121.463 | 61.5189 | -121.7285
844.2656 | 121.8704 | -61.3174 | 60.3287 | 0.094299 | 0.018357 | 0.070795 | 0.063643 | 0.12567 | 0.0014548 | -0.0056696 | 0.097962 | -0.0030698 | 0.059312 | 0.073168 | 0.0048769 | -0.010453 | 60.1639 | 60.2921 | -0.1236 | -61.4685 | 60.2417 | -61.3678 | -61.322 | -61.1572 | -0.10071 | -61.6608 | 60.2325 | 60.1913 | -61.2991 | -61.4731 | -0.050354 | -0.004577 | -0.086975 | 121.6095 | -0.15106 | -0.14648 | -0.16479 | 0.018311 | -0.15564 | -0.09613 | 0.16022 | -0.34332 | -0.18768 | -0.13733 | 121.5591 | 121.4813 | 61.1938 | -121.6507 | 121.55 | 121.5088 | 61.2167 | -121.8018
845.9531 | 121.9803 | -61.1893 | 60.3745 | -0.027771 | 0.01622 | 0.073572 | 0.065779 | 0.12546 | -0.0064492 | -0.005456 | 0.075073 | -0.0099058 | 0.060381 | 0.072527 | -0.0017453 | -0.010239 | 60.2509 | 60.4889 | 0.091553 | -61.3541 | 60.2554 | -61.2854 | -61.2167 | -60.997 | 0.16937 | -61.4456 | 60.2829 | 60.2417 | -61.1938 | -61.322 | -0.09613 | -0.027466 | -0.11902 | 121.6782 | -0.16479 | -0.13733 | -0.1236 | -0.004578 | -0.13275 | -0.091553 | 0.19226 | -0.25635 | -0.1236 | -0.13275 | 121.4447 | 121.4401 | 61.2808 | -121.5912 | 121.4722 | 121.431 | 61.3586 | -121.6965
847.7031 | 121.8475 | -61.3037 | 60.3378 | 0.040894 | 0.019211 | 0.072931 | 0.067701 | 0.12994 | 0.0010276 | -0.0028924 | 0.067444 | -0.0062742 | 0.061662 | 0.072527 | 0.0038089 | -0.0098117 | 60.1639 | 60.3241 | -0.09613 | -61.4548 | 60.2463 | -61.3541 | -61.3037 | -61.1755 | -0.073242 | -61.6791 | 60.2371 | 60.2051 | -61.3037 | -61.4502 | -0.050354 | 0 | -0.091553 | 121.6278 | -0.15106 | -0.15106 | -0.17395 | 0 | -0.14648 | -0.10071 | 0.12817 | -0.37537 | -0.22888 | -0.13275 | 121.55 | 121.4676 | 61.2076 | -121.6415 | 121.5408 | 121.5088 | 61.2305 | -121.788
849.4531 | 121.8338 | -61.3312 | 60.3378 | -0.065918 | 0.017289 | 0.072717 | 0.065565 | 0.12802 | 0.00060022 | -0.0033196 | -0.016479 | -0.0064878 | 0.061876 | 0.072954 | 0.0046633 | -0.0085299 | 60.2371 | 60.4385 | 0.022888 | -61.409 | 60.228 | -61.3174 | -61.2991 | -61.1114 | 0.018311 | -61.6104 | 60.2234 | 60.1822 | -61.29 | -61.4456 | 0.013733 | 0.032044 | -0.10986 | 121.7697 | -0.07782 | -0.10986 | -0.10071 | 0.041199 | -0.11444 | -0.11444 | 0.21973 | -0.27924 | -0.16479 | -0.15564 | 121.5591 | 121.5683 | 61.3541 | -121.637 | 121.5546 | 121.5134 | 61.3495 | -121.7834
851.2188 | 121.8796 | -61.2534 | 60.3607 | -0.21088 | 0.017075 | 0.073785 | 0.067488 | 0.12888 | -0.0019632 | -0.0035334 | -0.14618 | -0.005206 | 0.062089 | 0.072527 | 0.0014591 | -0.0070345 | 60.2325 | 60.434 | 0.10986 | -61.3724 | 60.3012 | -61.2671 | -61.2396 | -61.084 | 0.15564 | -61.5417 | 60.2966 | 60.26 | -61.2259 | -61.3586 | -0.013733 | 0.013733 | -0.05951 | 121.6873 | -0.11902 | -0.13275 | -0.12817 | 0.027466 | -0.10529 | -0.064087 | 0.16937 | -0.28839 | -0.1831 | -0.10071 | 121.5546 | 121.4859 | 61.3632 | -121.6003 | 121.55 | 121.5134 | 61.409 | -121.7194
852.9688 | 121.9437 | -61.2488 | 60.2829 | 0.11719 | 0.015793 | 0.074213 | 0.062574 | 0.13208 | -0.0028178 | -0.0028924 | 0.23529 | -0.0079832 | 0.059953 | 0.0721 | 0.0040225 | -0.0074619 | 60.2463 | 60.4568 | -0.013733 | -61.3861 | 60.173 | -61.3083 | -61.29 | -61.0428 | 0.045776 | -61.5189 | 60.1913 | 60.1273 | -61.29 | -61.4182 | -0.05951 | -0.041199 | -0.10986 | 121.7056 | -0.13733 | -0.09613 | -0.036621 | -0.041199 | -0.16937 | -0.091553 | 0.20599 | -0.27008 | -0.10071 | -0.15564 | 121.4218 | 121.4951 | 61.235 | -121.5729 | 121.4401 | 121.376 | 61.2946 | -121.7011
854.6406 | 121.8704 | -61.2534 | 60.3699 | -0.23376 | 0.018784 | 0.074854 | 0.06941 | 0.12866 | -0.002604 | -0.004815 | -0.14618 | -0.0062742 | 0.064012 | 0.073809 | 0.00060451 | -0.01088 | 60.2417 | 60.4431 | 0.10529 | -61.3724 | 60.3195 | -61.29 | -61.2442 | -61.0748 | 0.14648 | -61.5326 | 60.3195 | 60.3012 | -61.2396 | -61.3632 | -0.036621 | 0.009155 | -0.050354 | 121.6965 | -0.11902 | -0.12817 | -0.12817 | 0.013733 | -0.10986 | -0.050354 | 0.17853 | -0.27924 | -0.16937 | -0.068665 | 121.5729 | 121.4951 | 61.3586 | -121.6141 | 121.5729 | 121.5546 | 61.3998 | -121.7331
856.3906 | 121.9299 | -61.2076 | 60.4202 | -0.1651 | 0.015793 | 0.075922 | 0.06941 | 0.12845 | -0.0085856 | -0.0043878 | -0.062256 | -0.006915 | 0.063585 | 0.072954 | -0.0011045 | -0.0091709 | 60.3378 | 60.6171 | 0.24719 | -61.2717 | 60.2783 | -61.2122 | -61.1984 | -60.9421 | 0.31586 | -61.3907 | 60.2737 | 60.2692 | -61.1481 | -61.3037 | -0.004577 | 0.009156 | -0.14191 | 121.8246 | -0.064086 | -0.073242 | -0.082397 | 0.05951 | -0.09613 | -0.14648 | 0.2655 | -0.18311 | -0.086975 | -0.15106 | 121.4859 | 121.5454 | 61.4548 | -121.6187 | 121.4813 | 121.4767 | 61.5234 | -121.7239
858.1406 | 121.8796 | -61.2671 | 60.3928 | -0.20325 | 0.018143 | 0.070581 | 0.068983 | 0.12824 | -4.058e-05 | -0.0046014 | -0.13855 | -0.005206 | 0.064439 | 0.074023 | 0.0025271 | -0.01088 | 60.2509 | 60.4202 | 0.09613 | -61.3724 | 60.3058 | -61.2717 | -61.2534 | -61.0748 | 0.16022 | -61.528 | 60.3195 | 60.3058 | -61.1984 | -61.3861 | -0.004577 | 0.013733 | -0.086975 | 121.6873 | -0.10528 | -0.11902 | -0.14191 | 0.068665 | -0.11902 | -0.073242 | 0.19226 | -0.26093 | -0.14191 | -0.086975 | 121.5729 | 121.5179 | 61.3632 | -121.6461 | 121.5866 | 121.5729 | 61.4273 | -121.7789
859.8281 | 121.962 | -61.1984 | 60.3882 | -0.020142 | 0.012375 | 0.074426 | 0.063429 | 0.12973 | -0.0081582 | -0.0043878 | 0.13611 | -0.0071286 | 0.061021 | 0.072527 | 0.0023135 | -0.0070345 | 60.2463 | 60.4752 | 0.064087 | -61.3541 | 60.2554 | -61.2442 | -61.2213 | -61.0428 | 0.11444 | -61.4731 | 60.2554 | 60.228 | -61.1984 | -61.377 | -0.045777 | -0.022888 | -0.13275 | 121.6736 | -0.15564 | -0.13275 | -0.14191 | 0 | -0.17853 | -0.13275 | 0.15564 | -0.27466 | -0.09613 | -0.16022 | 121.4539 | 121.4447 | 61.2625 | -121.6095 | 121.4539 | 121.4264 | 61.3129 | -121.7651
861.5781 | 121.8246 | -61.2213 | 60.4202 | -0.23376 | 0.017716 | 0.075281 | 0.070906 | 0.12952 | -0.0036722 | -0.0073786 | -0.12329 | -0.005847 | 0.064653 | 0.074023 | -0.0011045 | -0.0091709 | 60.2966 | 60.5118 | 0.19684 | -61.322 | 60.2783 | -61.2305 | -61.2076 | -61.0428 | 0.20142 | -61.4914 | 60.3287 | 60.3012 | -61.203 | -61.3541 | -0.009156 | 0.013732 | -0.14191 | 121.7331 | -0.10071 | -0.11444 | -0.1236 | 0.01831 | -0.13275 | -0.091553 | 0.17853 | -0.27008 | -0.13733 | -0.11902 | 121.4996 | 121.5179 | 61.4182 | -121.6278 | 121.55 | 121.5225 | 61.4227 | -121.7743
863.3125 | 121.9437 | -61.1755 | 60.3745 | -0.14984 | 0.020279 | 0.075494 | 0.066847 | 0.1308 | -0.0036722 | -0.0050286 | -0.031738 | -0.0079832 | 0.063585 | 0.070391 | 0.0014591 | -0.0091709 | 60.3378 | 60.585 | 0.21973 | -61.29 | 60.2646 | -61.2167 | -61.1984 | -60.9192 | 0.29755 | -61.3541 | 60.2875 | 60.2509 | -61.1526 | -61.3174 | -0.041199 | -0.022888 | -0.10986 | 121.7606 | -0.11444 | -0.091553 | -0.036621 | 0.022888 | -0.14191 | -0.086975 | 0.25635 | -0.17853 | -0.036621 | -0.1236 | 121.4401 | 121.5134 | 61.3953 | -121.5729 | 121.463 | 121.4264 | 61.4731 | -121.6919
865.0781 | 121.843 | -61.235 | 60.4019 | -0.23376 | 0.018784 | 0.075067 | 0.067701 | 0.1308 | -0.0011088 | -0.0067376 | -0.14618 | -0.004138 | 0.066148 | 0.071245 | 0.00017731 | -0.0087435 | 60.2509 | 60.498 | 0.15564 | -61.3495 | 60.3241 | -61.2717 | -61.2305 | -61.0474 | 0.19226 | -61.5097 | 60.3287 | 60.2737 | -61.1893 | -61.3541 | -0.036621 | 0.004577 | -0.07782 | 121.7331 | -0.11444 | -0.11902 | -0.15106 | 0.045776 | -0.11902 | -0.073243 | 0.18768 | -0.27466 | -0.15564 | -0.12817 | 121.5591 | 121.4859 | 61.3907 | -121.6324 | 121.5637 | 121.5088 | 61.4273 | -121.756
866.75 | 121.9574 | -61.203 | 60.3745 | -0.012512 | 0.012375 | 0.073358 | 0.064497 | 0.12738 | -0.0062356 | -0.0067376 | 0.097962 | -0.0077696 | 0.062089 | 0.072527 | 0.0020999 | -0.0091709 | 60.228 | 60.4843 | 0.064087 | -61.3632 | 60.2646 | -61.2579 | -61.235 | -61.0291 | 0.1236 | -61.4777 | 60.2783 | 60.2097 | -61.203 | -61.3586 | -0.054932 | -0.032043 | -0.10986 | 121.6873 | -0.16022 | -0.12817 | -0.14648 | 0 | -0.15564 | -0.096131 | 0.17395 | -0.27466 | -0.11902 | -0.16479 | 121.4676 | 121.431 | 61.2671 | -121.6095 | 121.4813 | 121.4127 | 61.3266 | -121.7331
868.5 | 121.875 | -61.2534 | 60.3745 | -0.1651 | 0.01857 | 0.074854 | 0.065138 | 0.12781 | 0.001882 | -0.003106 | -0.16144 | -0.005206 | 0.061235 | 0.072314 | 0.0050907 | -0.0098117 | 60.2463 | 60.4477 | 0.091553 | -61.3541 | 60.3241 | -61.29 | -61.2534 | -61.0794 | 0.13733 | -61.5372 | 60.2829 | 60.2417 | -61.235 | -61.3907 | -0.036621 | 0 | -0.050354 | 121.7011 | -0.10071 | -0.10071 | -0.12817 | 0.018311 | -0.13733 | -0.091553 | 0.17395 | -0.28381 | -0.14648 | -0.13275 | 121.5775 | 121.4996 | 61.3449 | -121.6278 | 121.5363 | 121.4951 | 61.3907 | -121.7651
870.2656 | 121.9574 | -61.1847 | 60.3745 | -0.012512 | 0.017075 | 0.073999 | 0.065565 | 0.12866 | -0.006022 | -0.004815 | 0.059815 | -0.007556 | 0.063585 | 0.070605 | 0.0014591 | -0.0076755 | 60.2554 | 60.5072 | 0.10529 | -61.3403 | 60.2509 | -61.2717 | -61.2305 | -60.9695 | 0.19226 | -61.4227 | 60.2737 | 60.2417 | -61.1893 | -61.3312 | -0.086975 | -0.045777 | -0.1236 | 121.6919 | -0.15564 | -0.10986 | -0.11902 | -0.004578 | -0.14648 | -0.10071 | 0.21515 | -0.23804 | -0.091552 | -0.13275 | 121.4355 | 121.4401 | 61.29 | -121.6049 | 121.4584 | 121.4264 | 61.377 | -121.7056
871.9531 | 121.8887 | -61.2854 | 60.347 | -0.18799 | 0.015793 | 0.071863 | 0.06642 | 0.12952 | 0.0033774 | -0.003747 | -0.15381 | -0.0043516 | 0.061021 | 0.072314 | 0.0050907 | -0.0095981 | 60.2509 | 60.434 | 0.07782 | -61.3861 | 60.3333 | -61.3037 | -61.2946 | -61.0748 | 0.13275 | -61.5555 | 60.2783 | 60.26 | -61.235 | -61.4044 | -0.018311 | -0.009156 | -0.013733 | 121.7194 | -0.10071 | -0.091552 | -0.096131 | 0.050354 | -0.11902 | -0.068665 | 0.21057 | -0.27008 | -0.15106 | -0.086975 | 121.6187 | 121.5363 | 61.3632 | -121.6415 | 121.5637 | 121.5454 | 61.4182 | -121.7514
873.7031 | 121.9711 | -61.2808 | 60.2875 | 0.11719 | 0.019211 | 0.072076 | 0.066206 | 0.12824 | -0.00068138 | -0.003106 | 0.20477 | -0.0047788 | 0.060594 | 0.075304 | 0.0029543 | -0.0083163 | 60.1822 | 60.3607 | -0.10071 | -61.4639 | 60.2097 | -61.3724 | -61.3266 | -61.084 | -0.022888 | -61.5601 | 60.2051 | 60.1593 | -61.2717 | -61.4319 | -0.091552 | -0.045776 | -0.07782 | 121.6415 | -0.18311 | -0.13733 | -0.10529 | 0.009156 | -0.15106 | -0.082398 | 0.19684 | -0.27924 | -0.12817 | -0.12817 | 121.4905 | 121.463 | 61.1801 | -121.6141 | 121.4859 | 121.4401 | 61.2579 | -121.7194
875.4531 | 121.8384 | -61.203 | 60.4294 | -0.24139 | 0.018357 | 0.072504 | 0.068983 | 0.12354 | -0.006663 | -0.0039606 | -0.13092 | -0.0054196 | 0.062517 | 0.071032 | 0.0010317 | -0.0091709 | 60.2921 | 60.5301 | 0.19684 | -61.3129 | 60.2921 | -61.2442 | -61.2122 | -61.0428 | 0.22888 | -61.4914 | 60.3058 | 60.2829 | -61.2167 | -61.3449 | -0.041199 | -0.009155 | -0.13733 | 121.7331 | -0.10986 | -0.10071 | -0.13733 | -0.013733 | -0.14191 | -0.1236 | 0.16022 | -0.28839 | -0.14648 | -0.14648 | 121.4951 | 121.4951 | 61.3998 | -121.6415 | 121.5088 | 121.4859 | 61.4319 | -121.7743
877.2031 | 121.9803 | -61.1847 | 60.3928 | -0.0354 | 0.013443 | 0.075708 | 0.064711 | 0.13037 | -0.0075174 | -0.005456 | 0.067444 | -0.0077696 | 0.060594 | 0.070391 | -3.629e-05 | -0.0081027 | 60.26 | 60.5164 | 0.11902 | -61.3403 | 60.2829 | -61.2534 | -61.2305 | -60.9741 | 0.21973 | -61.3998 | 60.26 | 60.2325 | -61.1801 | -61.3358 | -0.068665 | -0.045777 | -0.10986 | 121.701 | -0.15564 | -0.10986 | -0.13275 | 0.004577 | -0.15106 | -0.13275 | 0.21057 | -0.21515 | -0.064087 | -0.16022 | 121.4676 | 121.4447 | 61.3037 | -121.6232 | 121.4447 | 121.4172 | 61.4044 | -121.7285
878.9531 | 121.9345 | -61.2488 | 60.347 | 0.10193 | 0.01857 | 0.073145 | 0.066633 | 0.12802 | -0.0053812 | -0.003106 | 0.19714 | -0.0071286 | 0.061662 | 0.072314 | 0.0025271 | -0.0083163 | 60.26 | 60.4752 | 0.041199 | -61.3815 | 60.2005 | -61.2946 | -61.2671 | -61.0199 | 0.082397 | -61.4777 | 60.228 | 60.1913 | -61.2167 | -61.3861 | -0.045777 | -0.018311 | -0.14648 | 121.7239 | -0.13275 | -0.11444 | -0.086975 | 0.032043 | -0.13733 | -0.11902 | 0.22888 | -0.22888 | -0.091553 | -0.15564 | 121.4493 | 121.5088 | 61.29 | -121.6141 | 121.4767 | 121.4401 | 61.3312 | -121.7331
880.6406 | 121.8338 | -61.203 | 60.4248 | -0.19562 | 0.017502 | 0.072717 | 0.065565 | 0.12909 | -0.0034586 | -0.0063104 | -0.15381 | -0.0079832 | 0.059312 | 0.072741 | 0.0018863 | -0.01088 | 60.3516 | 60.5713 | 0.2243 | -61.3083 | 60.2737 | -61.2122 | -61.1847 | -60.9879 | 0.29755 | -61.441 | 60.3104 | 60.2829 | -61.1755 | -61.3358 | -0.009155 | 0.018311 | -0.15106 | 121.7743 | -0.10529 | -0.1236 | -0.073243 | 0.027466 | -0.13275 | -0.11444 | 0.21515 | -0.23804 | -0.10529 | -0.14191 | 121.4767 | 121.5546 | 61.4273 | -121.6095 | 121.5134 | 121.4859 | 61.5005 | -121.7606
882.375 | 121.8292 | -61.2625 | 60.4111 | -0.12695 | 0.017716 | 0.072076 | 0.06706 | 0.13123 | -0.0011088 | -0.006524 | -0.16907 | -0.0049924 | 0.062517 | 0.072954 | 0.0018863 | -0.010239 | 60.2554 | 60.466 | 0.13733 | -61.3678 | 60.3424 | -61.2671 | -61.2305 | -61.0519 | 0.1831 | -61.5189 | 60.3378 | 60.3058 | -61.2259 | -61.322 | -0.004578 | 0.032043 | -0.068665 | 121.7285 | -0.10529 | -0.13733 | -0.15564 | 0.036621 | -0.059509 | -0.073242 | 0.21057 | -0.25635 | -0.19684 | -0.10529 | 121.6049 | 121.5179 | 61.3998 | -121.6415 | 121.6003 | 121.5683 | 61.4456 | -121.7331
884.125 | 121.8338 | -61.2396 | 60.4294 | -0.1651 | 0.018143 | 0.073785 | 0.06941 | 0.12738 | -0.004313 | -0.0041742 | -0.1767 | -0.0096922 | 0.063371 | 0.072314 | -0.00046349 | -0.0083163 | 60.3287 | 60.5621 | 0.23346 | -61.2946 | 60.2737 | -61.2122 | -61.1801 | -60.9879 | 0.28381 | -61.4365 | 60.3104 | 60.2692 | -61.1801 | -61.3266 | 0.027466 | 0.059509 | -0.15564 | 121.8018 | -0.054932 | -0.11444 | -0.10071 | 0.059509 | -0.086975 | -0.11902 | 0.25177 | -0.19684 | -0.10986 | -0.16022 | 121.5134 | 121.5683 | 61.4731 | -121.6095 | 121.55 | 121.5088 | 61.5234 | -121.756
885.8125 | 121.8842 | -61.2808 | 60.3424 | -0.15747 | 0.01857 | 0.073785 | 0.066847 | 0.13358 | 0.0020956 | -0.0039606 | -0.11566 | -0.0062742 | 0.062944 | 0.074877 | 0.0038089 | -0.012589 | 60.2509 | 60.4431 | 0.07782 | -61.377 | 60.2737 | -61.3174 | -61.2991 | -61.0611 | 0.14191 | -61.5509 | 60.3104 | 60.2417 | -61.2534 | -61.3907 | -0.036621 | -0.01831 | -0.068664 | 121.7239 | -0.09613 | -0.07782 | -0.091553 | 0.027466 | -0.10986 | -0.032043 | 0.21973 | -0.27008 | -0.16022 | -0.10071 | 121.5546 | 121.5317 | 61.3586 | -121.6415 | 121.5912 | 121.5225 | 61.4227 | -121.7331
887.5469 | 121.8018 | -61.2991 | 60.3607 | -0.073547 | 0.018997 | 0.075067 | 0.065138 | 0.12781 | 0.00060022 | -0.003747 | -0.069885 | -0.0043516 | 0.063798 | 0.073168 | 0.0055179 | -0.0083163 | 60.2509 | 60.4523 | 0.045776 | -61.3998 | 60.2463 | -61.3174 | -61.2534 | -61.0657 | 0.091553 | -61.5646 | 60.2463 | 60.2005 | -61.2671 | -61.441 | -0.018311 | 0.045776 | -0.11444 | 121.7514 | -0.10071 | -0.14648 | -0.10986 | 0.032043 | -0.14191 | -0.11444 | 0.23346 | -0.2655 | -0.1236 | -0.16022 | 121.5454 | 121.55 | 61.3449 | -121.6141 | 121.5454 | 121.4996 | 61.3907 | -121.8018
889.2969 | 121.8979 | -61.235 | 60.3699 | 0.063782 | 0.01857 | 0.073785 | 0.067488 | 0.12994 | -0.0068766 | -0.003747 | 0.159 | -0.006915 | 0.063371 | 0.071459 | 0.00017731 | -0.0076755 | 60.228 | 60.4797 | 0.032043 | -61.377 | 60.2097 | -61.2717 | -61.2579 | -61.0428 | 0.082397 | -61.4914 | 60.2417 | 60.2188 | -61.2167 | -61.377 | -0.036621 | -0.022889 | -0.16022 | 121.7148 | -0.14191 | -0.11902 | -0.14191 | 0.01831 | -0.14191 | -0.12817 | 0.19226 | -0.25635 | -0.11444 | -0.15106 | 121.4447 | 121.463 | 61.2671 | -121.6278 | 121.4767 | 121.4539 | 61.3174 | -121.7468
890.9844 | 121.9711 | -61.1938 | 60.3973 | -0.012512 | 0.014511 | 0.075922 | 0.065138 | 0.12888 | -0.007731 | -0.0056696 | 0.082703 | -0.0073422 | 0.05974 | 0.070818 | 0.0012455 | -0.0074619 | 60.2509 | 60.4843 | 0.07782 | -61.3586 | 60.2737 | -61.2671 | -61.235 | -61.0245 | 0.16022 | -61.4456 | 60.2463 | 60.2234 | -61.2122 | -61.3586 | -0.073242 | -0.041198 | -0.1236 | 121.6782 | -0.16479 | -0.1236 | -0.14649 | -0.01831 | -0.16479 | -0.15106 | 0.16937 | -0.25177 | -0.086975 | -0.17395 | 121.4676 | 121.4447 | 61.2717 | -121.6324 | 121.4401 | 121.4172 | 61.3541 | -121.756
892.7188 | 121.9254 | -61.2167 | 60.3745 | 0.033264 | 0.013657 | 0.074854 | 0.06407 | 0.12631 | -0.004954 | -0.0063104 | 0.12848 | -0.005847 | 0.06273 | 0.06975 | 0.0025271 | -0.0074619 | 60.2463 | 60.4843 | 0.032043 | -61.3724 | 60.2417 | -61.2717 | -61.2305 | -61.0565 | 0.10071 | -61.4914 | 60.2325 | 60.1868 | -61.2305 | -61.3541 | -0.054931 | -0.013733 | -0.13275 | 121.701 | -0.15564 | -0.14191 | -0.12817 | -0.013733 | -0.13733 | -0.14191 | 0.16022 | -0.27466 | -0.13733 | -0.18768 | 121.4584 | 121.463 | 61.2488 | -121.6049 | 121.4493 | 121.4035 | 61.3174 | -121.7285
894.4688 | 121.8384 | -61.2534 | 60.3973 | -0.17273 | 0.019638 | 0.073358 | 0.068129 | 0.12802 | -0.002604 | -0.0052424 | -0.18433 | -0.0039244 | 0.060808 | 0.070391 | 0.0020999 | -0.010666 | 60.26 | 60.4614 | 0.12817 | -61.377 | 60.2921 | -61.2625 | -61.2259 | -61.0565 | 0.17395 | -61.528 | 60.3378 | 60.2966 | -61.2122 | -61.3632 | -0.009155 | 0.027466 | -0.10529 | 121.7148 | -0.1236 | -0.15106 | -0.13733 | 0.041199 | -0.10986 | -0.059509 | 0.19684 | -0.27466 | -0.1648 | -0.10071 | 121.5454 | 121.5134 | 61.3815 | -121.6232 | 121.5912 | 121.55 | 61.4273 | -121.7606
896.2344 | 121.8567 | -61.322 | 60.3012 | 0.071411 | 0.018997 | 0.07464 | 0.06172 | 0.13037 | 0.0027364 | -0.0039606 | 0.11322 | -0.0060606 | 0.060594 | 0.073382 | 0.0067997 | -0.0076755 | 60.141 | 60.3149 | -0.15106 | -61.4731 | 60.2097 | -61.3495 | -61.322 | -61.1526 | -0.09613 | -61.6562 | 60.2097 | 60.173 | -61.3083 | -61.4502 | -0.027466 | 0 | -0.091552 | 121.637 | -0.15106 | -0.15106 | -0.16022 | 0.013732 | -0.12817 | -0.091552 | 0.16937 | -0.33417 | -0.20599 | -0.12817 | 121.5317 | 121.463 | 61.171 | -121.6232 | 121.5317 | 121.4951 | 61.2259 | -121.7514
897.9062 | 121.843 | -61.2396 | 60.434 | -0.18799 | 0.016648 | 0.074213 | 0.067915 | 0.12909 | -0.0058084 | -0.005456 | -0.12329 | -0.0071286 | 0.063158 | 0.071673 | 0.0014591 | -0.0093845 | 60.3149 | 60.5621 | 0.2243 | -61.2854 | 60.2737 | -61.2442 | -61.1984 | -60.9833 | 0.28381 | -61.4319 | 60.2921 | 60.2554 | -61.1984 | -61.3174 | -0.004578 | 0.041199 | -0.16022 | 121.8018 | -0.045776 | -0.086975 | -0.11902 | 0.041199 | -0.07782 | -0.14191 | 0.25635 | -0.19226 | -0.11444 | -0.17853 | 121.5134 | 121.5546 | 61.4639 | -121.6324 | 121.5317 | 121.4951 | 61.5234 | -121.7514
899.6406 | 121.8613 | -61.2442 | 60.4248 | -0.21088 | 0.018997 | 0.074213 | 0.070265 | 0.1293 | -0.002604 | -0.0052424 | -0.1767 | -0.0062742 | 0.064012 | 0.075518 | 0.00060451 | -0.011521 | 60.26 | 60.4477 | 0.1236 | -61.3678 | 60.3333 | -61.2854 | -61.235 | -61.0657 | 0.18768 | -61.5189 | 60.3516 | 60.3104 | -61.2076 | -61.377 | -0.041198 | 0.009156 | -0.091553 | 121.6919 | -0.1236 | -0.13275 | -0.16479 | 0.036621 | -0.13275 | -0.073243 | 0.17853 | -0.27466 | -0.14191 | -0.11444 | 121.5775 | 121.5042 | 61.3678 | -121.6599 | 121.5958 | 121.5546 | 61.4319 | -121.8018
901.3906 | 121.8292 | -61.2442 | 60.4202 | -0.25665 | 0.018357 | 0.073358 | 0.066633 | 0.13059 | -0.0047404 | -0.003106 | -0.15381 | -0.0071286 | 0.061876 | 0.074023 | -0.00067729 | -0.0087435 | 60.3241 | 60.5438 | 0.21057 | -61.3083 | 60.2875 | -61.2488 | -61.1893 | -61.0336 | 0.21515 | -61.4914 | 60.3058 | 60.2966 | -61.1801 | -61.3449 | -0.004577 | 0.054932 | -0.13275 | 121.788 | -0.064087 | -0.11902 | -0.09613 | 0.064087 | -0.10071 | -0.11444 | 0.21057 | -0.24719 | -0.14648 | -0.1236 | 121.5317 | 121.5683 | 61.4548 | -121.6095 | 121.55 | 121.5408 | 61.4594 | -121.7651
903.0781 | 121.9116 | -61.235 | 60.3607 | 0.079041 | 0.018143 | 0.07464 | 0.065779 | 0.12909 | -0.004954 | -0.0028924 | 0.19714 | -0.0081968 | 0.061235 | 0.0721 | 0.00039091 | -0.0083163 | 60.2509 | 60.498 | 0.022888 | -61.3953 | 60.2051 | -61.2671 | -61.2717 | -61.0153 | 0.07782 | -61.4868 | 60.2005 | 60.1868 | -61.2442 | -61.3724 | -0.032044 | -0.036621 | -0.15564 | 121.7331 | -0.16022 | -0.1236 | -0.10986 | -0.009156 | -0.13733 | -0.16022 | 0.21973 | -0.25177 | -0.11444 | -0.17395 | 121.4401 | 121.4859 | 61.2579 | -121.6324 | 121.4355 | 121.4218 | 61.3129 | -121.7331
904.8281 | 121.8842 | -61.2717 | 60.3287 | -0.18799 | 0.020706 | 0.075281 | 0.065351 | 0.12802 | 0.0025228 | -0.0060968 | -0.16907 | -0.0071286 | 0.062944 | 0.073382 | 0.0046633 | -0.011734 | 60.26 | 60.4431 | 0.091553 | -61.3724 | 60.3287 | -61.2991 | -61.2808 | -61.0703 | 0.12817 | -61.5372 | 60.2921 | 60.2463 | -61.2671 | -61.377 | -0.027466 | -0.009156 | 0 | 121.7148 | -0.10071 | -0.091552 | -0.068664 | 0.004577 | -0.10529 | -0.036621 | 0.20142 | -0.2655 | -0.16022 | -0.082397 | 121.6003 | 121.5317 | 61.3632 | -121.6095 | 121.5637 | 121.5179 | 61.3998 | -121.7056
906.5781 | 121.8521 | -61.235 | 60.4248 | -0.19562 | 0.01558 | 0.073572 | 0.068769 | 0.12973 | -0.0062356 | -0.0046014 | -0.062256 | -0.006915 | 0.062944 | 0.073168 | 0.00039091 | -0.0078891 | 60.3424 | 60.5713 | 0.25635 | -61.2717 | 60.2829 | -61.2305 | -61.1938 | -60.9787 | 0.29755 | -61.4136 | 60.2783 | 60.2692 | -61.171 | -61.3403 | 0.004577 | 0.041198 | -0.14191 | 121.8063 | -0.036621 | -0.077819 | -0.082398 | 0.064087 | -0.10529 | -0.14648 | 0.25635 | -0.17853 | -0.073242 | -0.15564 | 121.5179 | 121.5775 | 61.4914 | -121.6187 | 121.5134 | 121.5042 | 61.5326 | -121.7651
908.3281 | 121.8567 | -61.3312 | 60.3149 | 0.063782 | 0.01558 | 0.072717 | 0.063429 | 0.1293 | 0.0014548 | -0.003747 | 0.10559 | -0.0047788 | 0.058244 | 0.072741 | 0.0050907 | -0.0087435 | 60.1593 | 60.3104 | -0.13275 | -61.4685 | 60.2188 | -61.3724 | -61.3586 | -61.1481 | -0.091553 | -61.6425 | 60.2097 | 60.1959 | -61.3174 | -61.441 | -0.041198 | -0.027466 | -0.09613 | 121.6415 | -0.13733 | -0.10986 | -0.15564 | 0.013733 | -0.10986 | -0.10528 | 0.18311 | -0.31128 | -0.20142 | -0.11902 | 121.55 | 121.4905 | 61.1984 | -121.6736 | 121.5408 | 121.5271 | 61.2396 | -121.756
910.0312 | 121.9299 | -61.1938 | 60.3928 | -0.14221 | 0.015152 | 0.075708 | 0.064924 | 0.12888 | -0.0064492 | -0.0024652 | -0.054626 | -0.0092648 | 0.06273 | 0.070391 | 0.0012455 | -0.0074619 | 60.3378 | 60.6125 | 0.23804 | -61.2808 | 60.2829 | -61.2122 | -61.1755 | -60.9375 | 0.29755 | -61.3678 | 60.3104 | 60.2371 | -61.1664 | -61.3083 | -0.01831 | 0.018311 | -0.10986 | 121.8063 | -0.086975 | -0.10529 | -0.054931 | 0.027466 | -0.11444 | -0.082397 | 0.25635 | -0.17395 | -0.059509 | -0.15564 | 121.4767 | 121.5317 | 61.4319 | -121.5683 | 121.5042 | 121.431 | 61.4914 | -121.7011
911.7812 | 121.8567 | -61.2946 | 60.3333 | 0.063782 | 0.018784 | 0.070581 | 0.06407 | 0.13059 | 0.003591 | -0.003106 | 0.12085 | -0.0037106 | 0.062944 | 0.074023 | 0.0050907 | -0.010239 | 60.1501 | 60.2966 | -0.1236 | -61.4914 | 60.2325 | -61.3632 | -61.322 | -61.1618 | -0.10071 | -61.6562 | 60.2188 | 60.2097 | -61.29 | -61.4639 | -0.068664 | -0.027465 | -0.10071 | 121.5912 | -0.19684 | -0.16937 | -0.18311 | 0.004578 | -0.16937 | -0.11444 | 0.13275 | -0.36163 | -0.19226 | -0.1236 | 121.5271 | 121.4447 | 61.171 | -121.6553 | 121.5134 | 121.5042 | 61.1938 | -121.7972
913.5156 | 121.9116 | -61.2396 | 60.3287 | 0.16296 | 0.015366 | 0.072504 | 0.065779 | 0.13144 | -0.0038858 | -0.0033196 | 0.2124 | -0.0049924 | 0.061449 | 0.0721 | 0.0014591 | -0.0070345 | 60.2463 | 60.4797 | 0.004578 | -61.3815 | 60.173 | -61.3129 | -61.29 | -61.0245 | 0.073242 | -61.4822 | 60.2051 | 60.173 | -61.2625 | -61.4182 | -0.073242 | -0.050354 | -0.15564 | 121.7194 | -0.14191 | -0.091553 | -0.082397 | -0.022888 | -0.17853 | -0.1236 | 0.21515 | -0.24262 | -0.064087 | -0.15564 | 121.4127 | 121.4859 | 61.2442 | -121.6187 | 121.4447 | 121.4127 | 61.3129 | -121.7468
915.25 | 121.9849 | -61.1618 | 60.379 | -0.050659 | 0.01558 | 0.075922 | 0.06642 | 0.13016 | -0.0073038 | -0.0039606 | 0.036926 | -0.006915 | 0.061449 | 0.071886 | -0.0011045 | -0.0093845 | 60.2783 | 60.5118 | 0.12817 | -61.322 | 60.2737 | -61.235 | -61.2076 | -60.9695 | 0.2243 | -61.3678 | 60.2646 | 60.2509 | -61.1847 | -61.3403 | -0.073242 | -0.045777 | -0.10528 | 121.6736 | -0.16022 | -0.11444 | -0.10071 | -0.022888 | -0.17853 | -0.11444 | 0.19226 | -0.20599 | -0.027466 | -0.12817 | 121.4355 | 121.4401 | 61.29 | -121.5866 | 121.4264 | 121.4127 | 61.3861 | -121.7194
916.9375 | 121.8384 | -61.2213 | 60.4294 | -0.18036 | 0.016007 | 0.071008 | 0.067488 | 0.13101 | -0.003245 | -0.0058832 | -0.077515 | -0.007556 | 0.064012 | 0.072527 | 0.0014591 | -0.0095981 | 60.3287 | 60.553 | 0.23346 | -61.3037 | 60.2737 | -61.2396 | -61.203 | -60.9695 | 0.28839 | -61.4136 | 60.3104 | 60.2737 | -61.171 | -61.3266 | -0.018311 | 0.01831 | -0.15564 | 121.7743 | -0.082398 | -0.10071 | -0.10071 | 0.050354 | -0.10529 | -0.11902 | 0.25177 | -0.19226 | -0.086975 | -0.15564 | 121.4951 | 121.55 | 61.4548 | -121.6324 | 121.5317 | 121.4951 | 61.5097 | -121.756
918.625 | 121.9482 | -61.2808 | 60.2829 | 0.071411 | 0.018997 | 0.075281 | 0.063429 | 0.12738 | 0.0016684 | -0.0046014 | 0.13611 | -0.0071286 | 0.06273 | 0.07445 | 0.0048769 | -0.0093845 | 60.1913 | 60.3424 | -0.11902 | -61.4594 | 60.2463 | -61.3632 | -61.3083 | -61.116 | -0.073242 | -61.615 | 60.2005 | 60.1547 | -61.322 | -61.4548 | -0.082397 | -0.027466 | -0.036621 | 121.6232 | -0.17853 | -0.15106 | -0.091553 | -0.041198 | -0.17395 | -0.082398 | 0.16479 | -0.33417 | -0.16022 | -0.12817 | 121.5271 | 121.4722 | 61.1618 | -121.5912 | 121.4813 | 121.4355 | 61.2076 | -121.7377
920.375 | 121.9666 | -61.2625 | 60.3104 | 0.14771 | 0.017502 | 0.071436 | 0.06407 | 0.12994 | -0.00089518 | -0.0050286 | 0.159 | -0.0049924 | 0.062944 | 0.072954 | 0.0035953 | -0.010453 | 60.2051 | 60.3928 | -0.086975 | -61.4273 | 60.1822 | -61.3358 | -61.3037 | -61.0703 | 0 | -61.5417 | 60.2005 | 60.173 | -61.2762 | -61.4182 | -0.073242 | -0.041199 | -0.12817 | 121.6553 | -0.16479 | -0.1236 | -0.10529 | -0.013733 | -0.15564 | -0.10986 | 0.19226 | -0.27924 | -0.1236 | -0.13733 | 121.4447 | 121.4676 | 61.1755 | -121.6141 | 121.463 | 121.4355 | 61.2625 | -121.7285
922.125 | 121.8796 | -61.2854 | 60.3836 | -0.14984 | 0.020493 | 0.072717 | 0.069624 | 0.12952 | 0.0014548 | -0.0005426 | -0.092773 | -0.003497 | 0.063371 | 0.075304 | 0.0050907 | -0.010239 | 60.2554 | 60.434 | 0.086975 | -61.377 | 60.2646 | -61.3037 | -61.2946 | -61.0657 | 0.13733 | -61.5417 | 60.2829 | 60.2234 | -61.2442 | -61.4136 | -0.018311 | -0.009156 | -0.11902 | 121.7194 | -0.091553 | -0.082397 | -0.12817 | 0.041198 | -0.12817 | -0.10071 | 0.21973 | -0.25635 | -0.12817 | -0.16022 | 121.55 | 121.5408 | 61.3724 | -121.6782 | 121.5683 | 121.5088 | 61.4227 | -121.7972
923.7969 | 121.9574 | -61.29 | 60.2921 | 0.14008 | 0.017929 | 0.073145 | 0.064283 | 0.12909 | -0.00089518 | -0.0024652 | 0.2124 | -0.0060606 | 0.061662 | 0.072954 | 0.0044497 | -0.0089573 | 60.1685 | 60.379 | -0.09613 | -61.4639 | 60.2005 | -61.3495 | -61.322 | -61.084 | -0.004578 | -61.5509 | 60.1959 | 60.173 | -61.29 | -61.4319 | -0.059509 | -0.032043 | -0.091553 | 121.669 | -0.17395 | -0.14191 | -0.1236 | 0 | -0.14191 | -0.09613 | 0.20599 | -0.26093 | -0.11902 | -0.11902 | 121.4905 | 121.4584 | 61.1938 | -121.6141 | 121.4859 | 121.463 | 61.2854 | -121.7239
925.5469 | 121.9299 | -61.1755 | 60.4202 | -0.14221 | 0.015793 | 0.073999 | 0.067274 | 0.13016 | -0.006663 | -0.0028924 | -0.039368 | -0.0094786 | 0.064226 | 0.071673 | -0.00067729 | -0.0087435 | 60.347 | 60.6125 | 0.24719 | -61.2946 | 60.2829 | -61.1938 | -61.1938 | -60.9421 | 0.31128 | -61.3678 | 60.2783 | 60.26 | -61.1572 | -61.3174 | -0.018311 | -0.018311 | -0.13733 | 121.788 | -0.11902 | -0.10071 | -0.073242 | 0.01831 | -0.14191 | -0.14191 | 0.23346 | -0.19226 | -0.050354 | -0.16022 | 121.4584 | 121.5225 | 61.4227 | -121.6141 | 121.4539 | 121.4355 | 61.4868 | -121.7377
927.2969 | 121.9345 | -61.235 | 60.3836 | 0.048523 | 0.015793 | 0.071649 | 0.065138 | 0.12866 | -0.004954 | -0.004815 | 0.14374 | -0.0084104 | 0.060808 | 0.071245 | -3.629e-05 | -0.0078891 | 60.2463 | 60.4706 | 0.045776 | -61.3678 | 60.2646 | -61.2579 | -61.2488 | -61.0382 | 0.086975 | -61.4822 | 60.2554 | 60.2325 | -61.2076 | -61.3632 | -0.022889 | -0.013733 | -0.11902 | 121.7056 | -0.13275 | -0.11902 | -0.13733 | 0.027465 | -0.12817 | -0.12817 | 0.19684 | -0.24719 | -0.11902 | -0.15106 | 121.4996 | 121.4813 | 61.2808 | -121.6324 | 121.4905 | 121.4676 | 61.322 | -121.7468
928.9844 | 121.8292 | -61.3358 | 60.3104 | -0.081177 | 0.015793 | 0.073358 | 0.063643 | 0.1308 | 0.0031638 | -0.0043878 | -0.054626 | -0.0047788 | 0.061449 | 0.073382 | 0.0055179 | -0.0091709 | 60.2554 | 60.4523 | 0.041199 | -61.4044 | 60.2371 | -61.3129 | -61.2946 | -61.0657 | 0.091553 | -61.5646 | 60.2692 | 60.2325 | -61.2579 | -61.4273 | 0.022888 | 0.041198 | -0.073242 | 121.788 | -0.068665 | -0.10986 | -0.054932 | 0.077819 | -0.091553 | -0.041199 | 0.27008 | -0.22888 | -0.13733 | -0.07782 | 121.5729 | 121.5912 | 61.377 | -121.6049 | 121.6049 | 121.5683 | 61.4273 | -121.7377
930.7344 | 121.9254 | -61.2122 | 60.3607 | 0.033264 | 0.013443 | 0.074854 | 0.065351 | 0.12909 | -0.0058084 | -0.0039606 | 0.14374 | -0.007556 | 0.062089 | 0.070818 | 0.00017731 | -0.0091709 | 60.228 | 60.4797 | 0.036621 | -61.3815 | 60.26 | -61.2808 | -61.2442 | -61.0336 | 0.091553 | -61.4822 | 60.2417 | 60.2234 | -61.2213 | -61.3678 | -0.068665 | -0.032044 | -0.10071 | 121.6919 | -0.16937 | -0.13733 | -0.13275 | -0.009155 | -0.15564 | -0.11902 | 0.17853 | -0.27008 | -0.11444 | -0.13733 | 121.4722 | 121.4401 | 61.2488 | -121.6049 | 121.4539 | 121.4355 | 61.3037 | -121.7285
932.4844 | 121.9711 | -61.1938 | 60.4019 | 0.0027468 | 0.013016 | 0.076776 | 0.062574 | 0.13059 | -0.0068766 | -0.004815 | 0.10559 | -0.006915 | 0.058244 | 0.070177 | 0.0029543 | -0.0072483 | 60.228 | 60.4889 | 0.059509 | -61.3586 | 60.2646 | -61.2534 | -61.2488 | -61.0428 | 0.10529 | -61.4868 | 60.2463 | 60.2142 | -61.2213 | -61.3998 | -0.059509 | -0.054931 | -0.13733 | 121.6827 | -0.16479 | -0.10986 | -0.17395 | -0.027465 | -0.20599 | -0.15564 | 0.15106 | -0.29297 | -0.086975 | -0.18768 | 121.4584 | 121.4218 | 61.2534 | -121.6507 | 121.4401 | 121.4081 | 61.2991 | -121.8018
934.1719 | 121.8155 | -61.3495 | 60.3195 | -0.027771 | 0.017289 | 0.072931 | 0.065138 | 0.12888 | 0.001882 | -0.0022516 | -0.031738 | -0.005206 | 0.06273 | 0.072527 | 0.0046633 | -0.010239 | 60.2142 | 60.3607 | -0.036621 | -61.441 | 60.2554 | -61.3358 | -61.3129 | -61.1618 | -0.022888 | -61.6425 | 60.2509 | 60.2051 | -61.3037 | -61.4456 | 0.013733 | 0.036621 | -0.064087 | 121.7102 | -0.091553 | -0.12817 | -0.10529 | 0.045776 | -0.096131 | -0.068665 | 0.18768 | -0.29297 | -0.19684 | -0.11444 | 121.6049 | 121.5637 | 61.3129 | -121.6324 | 121.6003 | 121.5546 | 61.3266 | -121.7651
935.875 | 121.8292 | -61.3083 | 60.3149 | 0.063782 | 0.021347 | 0.074854 | 0.069197 | 0.1293 | 0.0031638 | -0.0033196 | 0.044556 | -0.0081968 | 0.062517 | 0.071673 | 0.0044497 | -0.0091709 | 60.1547 | 60.3058 | -0.07782 | -61.4456 | 60.2463 | -61.3495 | -61.322 | -61.1755 | -0.086975 | -61.6745 | 60.2142 | 60.1868 | -61.3129 | -61.4594 | -0.041198 | -0.013732 | -0.068664 | 121.6141 | -0.13733 | -0.1236 | -0.16022 | -0.004577 | -0.15106 | -0.10071 | 0.13275 | -0.36621 | -0.21515 | -0.12817 | 121.5546 | 121.463 | 61.2305 | -121.637 | 121.5225 | 121.4951 | 61.2213 | -121.7743
937.6094 | 121.8658 | -61.2854 | 60.3424 | -0.14221 | 0.018784 | 0.073145 | 0.069197 | 0.1261 | 0.0012412 | -0.0005426 | -0.085144 | -0.0043516 | 0.06273 | 0.072314 | 0.0020999 | -0.011307 | 60.2554 | 60.4431 | 0.07782 | -61.3998 | 60.2875 | -61.3037 | -61.2579 | -61.0703 | 0.12817 | -61.5555 | 60.2692 | 60.2325 | -61.2534 | -61.409 | -0.018311 | 0.027465 | -0.054931 | 121.7285 | -0.11444 | -0.14191 | -0.086975 | 0.032043 | -0.1236 | -0.073242 | 0.21515 | -0.27008 | -0.14648 | -0.10986 | 121.5729 | 121.5408 | 61.3632 | -121.6003 | 121.5546 | 121.5179 | 61.4136 | -121.7514
939.3438 | 121.8521 | -61.2946 | 60.3378 | -0.11169 | 0.02092 | 0.073358 | 0.065565 | 0.13037 | 0.00038662 | -0.002038 | -0.069885 | -0.006915 | 0.062944 | 0.074023 | 0.0035953 | -0.0074619 | 60.2463 | 60.4477 | 0.073242 | -61.3907 | 60.2646 | -61.3129 | -61.2717 | -61.084 | 0.1236 | -61.5326 | 60.2554 | 60.2234 | -61.2579 | -61.3953 | -0.01831 | 0.022889 | -0.073243 | 121.7422 | -0.09613 | -0.11902 | -0.091553 | 0.036621 | -0.10071 | -0.082398 | 0.21057 | -0.23804 | -0.13733 | -0.11444 | 121.5591 | 121.5408 | 61.3678 | -121.6095 | 121.55 | 121.5179 | 61.4182 | -121.7331
941.1094 | 121.9299 | -61.2808 | 60.3424 | 0.14771 | 0.01622 | 0.073999 | 0.063856 | 0.12866 | -0.0053812 | -0.0041742 | 0.26581 | -0.0079832 | 0.062089 | 0.070818 | 0.0018863 | -0.0081027 | 60.2097 | 60.466 | 0 | -61.3815 | 60.1593 | -61.322 | -61.2854 | -61.0474 | 0.064087 | -61.4914 | 60.1959 | 60.141 | -61.2808 | -61.4044 | -0.041198 | -0.004577 | -0.18311 | 121.7468 | -0.10071 | -0.096131 | -0.13275 | 0 | -0.1236 | -0.14648 | 0.23346 | -0.21057 | -0.086975 | -0.20142 | 121.4401 | 121.4905 | 61.2808 | -121.6278 | 121.4767 | 121.4218 | 61.3449 | -121.7468
942.7969 | 121.9666 | -61.2122 | 60.3653 | -0.012512 | 0.017502 | 0.073785 | 0.070692 | 0.12845 | -0.0090128 | -0.0060968 | 0.097962 | -0.0077696 | 0.061235 | 0.072527 | -0.0025999 | -0.0081027 | 60.2463 | 60.4797 | 0.10071 | -61.3495 | 60.2783 | -61.2488 | -61.2534 | -61.0153 | 0.16022 | -61.4273 | 60.2921 | 60.2737 | -61.1984 | -61.322 | -0.036621 | -0.041199 | -0.086975 | 121.6919 | -0.13733 | -0.09613 | -0.11902 | 0.013733 | -0.10986 | -0.073242 | 0.19684 | -0.21515 | -0.10529 | -0.091552 | 121.4905 | 121.4584 | 61.3129 | -121.6187 | 121.5042 | 121.4859 | 61.3724 | -121.6873
944.5312 | 121.9711 | -61.1938 | 60.4156 | 0.010376 | 0.013657 | 0.074426 | 0.066633 | 0.12802 | -0.006663 | -0.0052424 | 0.12848 | -0.008624 | 0.061662 | 0.073382 | 0.0023135 | -0.0095981 | 60.228 | 60.4797 | 0.064087 | -61.3541 | 60.2646 | -61.2671 | -61.2579 | -61.0382 | 0.10986 | -61.4777 | 60.2737 | 60.2142 | -61.2076 | -61.3632 | -0.073242 | -0.064087 | -0.15106 | 121.6736 | -0.16022 | -0.09613 | -0.18768 | -0.013733 | -0.16937 | -0.14191 | 0.15564 | -0.28381 | -0.11444 | -0.20142 | 121.4584 | 121.4218 | 61.2579 | -121.6736 | 121.4676 | 121.4081 | 61.3037 | -121.7789
946.2344 | 121.9345 | -61.1984 | 60.4065 | -0.0048827 | 0.014084 | 0.074426 | 0.066206 | 0.12845 | -0.0028178 | -0.0043878 | 0.10559 | -0.0079832 | 0.062303 | 0.07445 | 0.0018863 | -0.011521 | 60.2554 | 60.4614 | 0.045776 | -61.3449 | 60.2692 | -61.2534 | -61.2305 | -61.0382 | 0.10071 | -61.4822 | 60.26 | 60.2417 | -61.203 | -61.3586 | -0.054932 | -0.032044 | -0.13733 | 121.6599 | -0.14648 | -0.11444 | -0.15106 | -0.004578 | -0.16022 | -0.14648 | 0.16022 | -0.28381 | -0.1236 | -0.1648 | 121.4676 | 121.4539 | 61.2442 | -121.637 | 121.4584 | 121.4401 | 61.2991 | -121.7651
947.9688 | 121.8567 | -61.2305 | 60.4156 | -0.17273 | 0.018997 | 0.072931 | 0.065351 | 0.13016 | -0.003245 | -0.0067376 | -0.077515 | -0.0079832 | 0.061235 | 0.071886 | 0.0010317 | -0.0091709 | 60.347 | 60.5621 | 0.23804 | -61.2946 | 60.3104 | -61.2442 | -61.2122 | -60.9787 | 0.28839 | -61.409 | 60.2966 | 60.2692 | -61.1755 | -61.3129 | -0.013733 | 0.018311 | -0.10529 | 121.7926 | -0.064087 | -0.082398 | -0.068664 | 0.054932 | -0.082397 | -0.11902 | 0.25177 | -0.17853 | -0.096131 | -0.14648 | 121.5408 | 121.5775 | 61.4685 | -121.6278 | 121.5271 | 121.4996 | 61.5189 | -121.7285
949.7188 | 121.8796 | -61.2717 | 60.3516 | -0.13458 | 0.017502 | 0.073145 | 0.065992 | 0.12866 | 0.00081382 | -0.0039606 | -0.092773 | -0.0047788 | 0.062303 | 0.072314 | 0.0027407 | -0.011521 | 60.2966 | 60.4385 | 0.086975 | -61.3678 | 60.2737 | -61.322 | -61.2625 | -61.0519 | 0.11902 | -61.5372 | 60.2737 | 60.2509 | -61.2579 | -61.409 | -0.050354 | 0.009155 | -0.077819 | 121.7102 | -0.096131 | -0.10529 | -0.054931 | 0.013732 | -0.13733 | -0.077819 | 0.21973 | -0.2655 | -0.12817 | -0.10071 | 121.5454 | 121.5683 | 61.3586 | -121.6141 | 121.5454 | 121.5225 | 61.3907 | -121.7606
951.4062 | 121.8979 | -61.1938 | 60.4202 | -0.18799 | 0.017716 | 0.075281 | 0.065992 | 0.12802 | -0.0045266 | -0.0043878 | -0.077515 | -0.0092648 | 0.062303 | 0.070391 | 0.0033817 | -0.0098117 | 60.3516 | 60.585 | 0.24719 | -61.2946 | 60.2783 | -61.2076 | -61.1984 | -60.9604 | 0.28381 | -61.4182 | 60.2737 | 60.26 | -61.1938 | -61.2946 | -0.013733 | -0.004577 | -0.14191 | 121.7789 | -0.10071 | -0.096131 | -0.068665 | 0 | -0.10071 | -0.14648 | 0.23346 | -0.2243 | -0.1236 | -0.16022 | 121.4722 | 121.5454 | 61.441 | -121.6187 | 121.4676 | 121.4539 | 61.4777 | -121.7148
953.1562 | 121.8887 | -61.3083 | 60.2966 | 0.10193 | 0.017929 | 0.074213 | 0.063856 | 0.12824 | 0.0012412 | -0.0033196 | 0.10559 | -0.0067014 | 0.058885 | 0.073382 | 0.0059451 | -0.0083163 | 60.1593 | 60.3195 | -0.13275 | -61.4777 | 60.228 | -61.377 | -61.3495 | -61.1481 | -0.073242 | -61.6287 | 60.2142 | 60.2142 | -61.2991 | -61.4502 | -0.068664 | -0.041198 | -0.068665 | 121.6278 | -0.16937 | -0.12817 | -0.13733 | 0.009156 | -0.14191 | -0.082398 | 0.16022 | -0.32043 | -0.17853 | -0.082398 | 121.5363 | 121.4676 | 61.1755 | -121.6461 | 121.5225 | 121.5225 | 61.235 | -121.7468
954.8438 | 121.8658 | -61.2305 | 60.4111 | -0.19562 | 0.017502 | 0.073572 | 0.069197 | 0.12781 | -0.0045266 | -0.003747 | -0.077515 | -0.0088376 | 0.062517 | 0.071673 | 0.00017731 | -0.010025 | 60.3378 | 60.5804 | 0.26093 | -61.2946 | 60.26 | -61.235 | -61.1938 | -60.9741 | 0.30212 | -61.3998 | 60.2692 | 60.2509 | -61.1893 | -61.322 | -0.004577 | 0.036621 | -0.15106 | 121.8109 | -0.064087 | -0.10071 | -0.073242 | 0.041199 | -0.091552 | -0.14191 | 0.25635 | -0.16937 | -0.07782 | -0.16022 | 121.4905 | 121.5683 | 61.4914 | -121.6049 | 121.4996 | 121.4813 | 61.5326 | -121.7331
956.5938 | 121.9482 | -61.1893 | 60.4202 | -0.11932 | 0.016648 | 0.073785 | 0.067274 | 0.12845 | -0.0079446 | -0.0046014 | -0.069885 | -0.008624 | 0.061662 | 0.071459 | -0.0011045 | -0.0091709 | 60.3561 | 60.6171 | 0.25177 | -61.2717 | 60.2921 | -61.2213 | -61.1893 | -60.9375 | 0.32044 | -61.3586 | 60.2921 | 60.2554 | -61.1618 | -61.3083 | -0.032043 | 0 | -0.12817 | 121.8063 | -0.082397 | -0.082397 | -0.064087 | 0.027466 | -0.11902 | -0.12817 | 0.25177 | -0.16937 | -0.050354 | -0.16479 | 121.4813 | 121.5454 | 61.441 | -121.6095 | 121.4813 | 121.4447 | 61.5097 | -121.7285
958.2812 | 121.8567 | -61.322 | 60.3424 | 0.033264 | 0.017075 | 0.071222 | 0.06407 | 0.13059 | 0.0029502 | -0.0041742 | 0.075073 | -0.0047788 | 0.063158 | 0.072741 | 0.0050907 | -0.010453 | 60.1501 | 60.2875 | -0.11902 | -61.4822 | 60.2325 | -61.3449 | -61.3129 | -61.171 | -0.10529 | -61.6608 | 60.2234 | 60.1868 | -61.322 | -61.4365 | -0.022889 | 0.009155 | -0.10986 | 121.6095 | -0.16022 | -0.16937 | -0.19226 | 0 | -0.11444 | -0.11902 | 0.15106 | -0.33875 | -0.22431 | -0.15564 | 121.5546 | 121.4722 | 61.203 | -121.6553 | 121.5454 | 121.5088 | 61.2167 | -121.7789
960.0312 | 121.9666 | -61.1893 | 60.379 | -0.15747 | 0.016434 | 0.075281 | 0.067274 | 0.12994 | -0.0064492 | -0.006524 | -0.039368 | -0.0079832 | 0.062089 | 0.069964 | 0.0027407 | -0.0093845 | 60.3378 | 60.585 | 0.21515 | -61.2946 | 60.2737 | -61.2213 | -61.1893 | -60.9329 | 0.29297 | -61.3678 | 60.2554 | 60.2783 | -61.1801 | -61.3037 | -0.032043 | 0 | -0.10528 | 121.7743 | -0.10529 | -0.10529 | -0.041198 | 0.009155 | -0.11444 | -0.1236 | 0.25635 | -0.17853 | -0.064087 | -0.10071 | 121.463 | 121.5271 | 61.4044 | -121.5683 | 121.4447 | 121.4676 | 61.4822 | -121.6827
961.7344 | 121.8521 | -61.3083 | 60.3424 | -0.096436 | 0.018997 | 0.073358 | 0.065351 | 0.12717 | 0.0023092 | -0.0033196 | -0.077515 | -0.0037106 | 0.062517 | 0.075945 | 0.0055179 | -0.0091709 | 60.2554 | 60.4248 | 0.064087 | -61.3907 | 60.2646 | -61.3174 | -61.2854 | -61.0474 | 0.11444 | -61.5463 | 60.2554 | 60.2417 | -61.2717 | -61.4136 | -0.009155 | 0.022889 | -0.07782 | 121.7331 | -0.082397 | -0.10529 | -0.086975 | 0.036622 | -0.10528 | -0.086975 | 0.26093 | -0.23804 | -0.13275 | -0.10071 | 121.5729 | 121.5637 | 61.3724 | -121.6278 | 121.5637 | 121.55 | 61.4227 | -121.756
963.4688 | 121.8613 | -61.3037 | 60.3516 | -0.081177 | 0.021134 | 0.073145 | 0.068342 | 0.1308 | -0.0013224 | -0.002038 | -0.069885 | -0.005847 | 0.063798 | 0.073595 | 0.0033817 | -0.010025 | 60.26 | 60.434 | 0.068665 | -61.377 | 60.2737 | -61.3083 | -61.2808 | -61.0611 | 0.12817 | -61.5463 | 60.2737 | 60.2325 | -61.2534 | -61.4319 | -0.004578 | 0.022888 | -0.077819 | 121.7377 | -0.073242 | -0.09613 | -0.091552 | 0.050354 | -0.12817 | -0.077819 | 0.24262 | -0.24262 | -0.11444 | -0.11902 | 121.5775 | 121.5637 | 61.3724 | -121.6324 | 121.5775 | 121.5363 | 61.4319 | -121.7834
965.2188 | 121.8521 | -61.2305 | 60.4477 | -0.18036 | 0.019638 | 0.071863 | 0.070478 | 0.13144 | -0.006663 | -0.005456 | -0.13092 | -0.0073422 | 0.06508 | 0.071886 | -0.00089089 | -0.0089573 | 60.3287 | 60.5713 | 0.23804 | -61.2762 | 60.2966 | -61.2213 | -61.2122 | -61.0062 | 0.27008 | -61.4594 | 60.3149 | 60.2829 | -61.1938 | -61.3266 | 0.009156 | 0.018311 | -0.15106 | 121.8018 | -0.045776 | -0.064087 | -0.11902 | 0.036621 | -0.09613 | -0.13275 | 0.2243 | -0.22888 | -0.13275 | -0.16479 | 121.5271 | 121.5591 | 61.4685 | -121.6599 | 121.5454 | 121.5134 | 61.5005 | -121.7743
966.9062 | 121.907 | -61.2259 | 60.3699 | 0.063782 | 0.014725 | 0.073572 | 0.068769 | 0.12824 | -0.0068766 | -0.0056696 | 0.16663 | -0.0071286 | 0.064439 | 0.074236 | 0.00081811 | -0.0070345 | 60.2417 | 60.4706 | 0.045776 | -61.3815 | 60.2188 | -61.2534 | -61.2167 | -61.0382 | 0.091553 | -61.4822 | 60.2463 | 60.2142 | -61.2213 | -61.3998 | -0.027466 | 0.009155 | -0.15106 | 121.6965 | -0.15564 | -0.1648 | -0.12817 | 0.004578 | -0.17395 | -0.1236 | 0.18768 | -0.25635 | -0.082398 | -0.15564 | 121.4447 | 121.4676 | 61.2717 | -121.5866 | 121.4722 | 121.4401 | 61.3174 | -121.7697
968.6562 | 121.9666 | -61.1938 | 60.4019 | -0.14221 | 0.016007 | 0.074854 | 0.070265 | 0.1293 | -0.0051676 | -0.0063104 | -0.0012209 | -0.007556 | 0.061235 | 0.072527 | -0.00046349 | -0.010666 | 60.3195 | 60.5988 | 0.21057 | -61.2946 | 60.2829 | -61.2213 | -61.1664 | -60.9192 | 0.30212 | -61.3541 | 60.2921 | 60.2234 | -61.1847 | -61.3312 | -0.027465 | 0.027466 | -0.11902 | 121.7926 | -0.10071 | -0.12817 | -0.082398 | 0.009156 | -0.13733 | -0.10986 | 0.27466 | -0.16022 | -0.022888 | -0.17853 | 121.4767 | 121.5134 | 61.4044 | -121.5683 | 121.4859 | 121.4172 | 61.496 | -121.7331
970.3438 | 121.8887 | -61.3037 | 60.2692 | 0.08667 | 0.015793 | 0.073358 | 0.062361 | 0.12546 | 0.00081382 | -0.002038 | 0.12085 | -0.0047788 | 0.063158 | 0.073809 | 0.0065859 | -0.0093845 | 60.1639 | 60.3149 | -0.13733 | -61.4822 | 60.2554 | -61.3678 | -61.3312 | -61.1481 | -0.07782 | -61.6379 | 60.2463 | 60.2097 | -61.3037 | -61.4731 | -0.064087 | -0.027466 | -0.013733 | 121.6187 | -0.17853 | -0.15106 | -0.10529 | 0 | -0.16937 | -0.022888 | 0.15564 | -0.33417 | -0.16479 | -0.059509 | 121.5591 | 121.4676 | 61.1664 | -121.6003 | 121.55 | 121.5134 | 61.2259 | -121.7422
972.0781 | 121.9116 | -61.2396 | 60.3699 | 0.079041 | 0.014939 | 0.074426 | 0.064711 | 0.12952 | -0.004954 | -0.005456 | 0.19714 | -0.0064878 | 0.062944 | 0.072314 | 0.0038089 | -0.0068209 | 60.2509 | 60.5026 | 0.032043 | -61.3632 | 60.1913 | -61.2854 | -61.2762 | -61.0336 | 0.068665 | -61.496 | 60.2097 | 60.1547 | -61.2488 | -61.409 | -0.045776 | -0.036621 | -0.17853 | 121.7422 | -0.1236 | -0.086975 | -0.11902 | -0.009155 | -0.16937 | -0.16022 | 0.20599 | -0.25635 | -0.086975 | -0.21515 | 121.431 | 121.4905 | 61.2717 | -121.6461 | 121.4493 | 121.3943 | 61.3083 | -121.7789
973.8125 | 121.9803 | -61.2076 | 60.3836 | -0.0354 | 0.014511 | 0.073999 | 0.064924 | 0.12845 | -0.0079446 | -0.0056696 | 0.075073 | -0.0067014 | 0.064226 | 0.070177 | 0.0018863 | -0.0085299 | 60.2417 | 60.5026 | 0.07782 | -61.3358 | 60.2829 | -61.2625 | -61.2625 | -61.0107 | 0.16022 | -61.4365 | 60.2646 | 60.2371 | -61.1938 | -61.3312 | -0.054931 | -0.054931 | -0.10071 | 121.7102 | -0.12817 | -0.073242 | -0.14191 | 0.013733 | -0.1236 | -0.11902 | 0.19684 | -0.22888 | -0.10529 | -0.14648 | 121.4905 | 121.4493 | 61.2854 | -121.6461 | 121.4722 | 121.4447 | 61.3678 | -121.7148
975.5625 | 121.8521 | -61.2442 | 60.4111 | -0.22614 | 0.01857 | 0.07229 | 0.068983 | 0.12952 | -0.00046778 | -0.0084466 | -0.085144 | -0.0062742 | 0.063371 | 0.0721 | 0.0010317 | -0.010239 | 60.3149 | 60.5026 | 0.17395 | -61.3541 | 60.3058 | -61.2488 | -61.2167 | -61.0519 | 0.17395 | -61.5234 | 60.3149 | 60.2966 | -61.2305 | -61.377 | -0.004577 | 0.027466 | -0.10529 | 121.7468 | -0.10986 | -0.13733 | -0.096131 | 0.013733 | -0.13275 | -0.096131 | 0.19226 | -0.27923 | -0.14648 | -0.11444 | 121.55 | 121.5591 | 61.4182 | -121.6278 | 121.5591 | 121.5408 | 61.4182 | -121.788
977.25 | 121.875 | -61.2076 | 60.4156 | -0.20325 | 0.017502 | 0.075067 | 0.068129 | 0.12909 | -0.0058084 | -0.0035334 | -0.062256 | -0.0071286 | 0.061876 | 0.071886 | 0.0018863 | -0.010025 | 60.3607 | 60.5759 | 0.24719 | -61.3037 | 60.2829 | -61.2213 | -61.1984 | -60.9741 | 0.29755 | -61.4182 | 60.3012 | 60.2692 | -61.171 | -61.3449 | -0.013732 | 0.009156 | -0.13275 | 121.7834 | -0.09613 | -0.10529 | -0.054931 | 0.036622 | -0.13733 | -0.11444 | 0.23346 | -0.21057 | -0.073242 | -0.14648 | 121.4905 | 121.5683 | 61.4548 | -121.6141 | 121.5088 | 121.4767 | 61.5051 | -121.7606
979 | 121.8246 | -61.3129 | 60.3424 | -0.065918 | 0.019638 | 0.071863 | 0.065779 | 0.12909 | 0.0031638 | -0.0028924 | -0.039368 | -0.0047788 | 0.063158 | 0.075518 | 0.0057315 | -0.010025 | 60.2646 | 60.4202 | 0.027466 | -61.4044 | 60.26 | -61.322 | -61.29 | -61.0977 | 0.032043 | -61.6196 | 60.2692 | 60.2188 | -61.2854 | -61.441 | -0.009155 | 0.022888 | -0.082397 | 121.7331 | -0.091553 | -0.11444 | -0.07782 | 0.027466 | -0.12817 | -0.073242 | 0.21515 | -0.3067 | -0.17853 | -0.1236 | 121.5729 | 121.5775 | 61.3403 | -121.6324 | 121.582 | 121.5317 | 61.3449 | -121.7834
980.75 | 121.9711 | -61.2808 | 60.2737 | 0.12482 | 0.017502 | 0.073572 | 0.062361 | 0.12973 | -0.003245 | -0.0024652 | 0.18951 | -0.0067014 | 0.059526 | 0.072314 | 0.0046633 | -0.0083163 | 60.2325 | 60.4568 | -0.041199 | -61.4182 | 60.2097 | -61.3449 | -61.2991 | -61.0382 | 0.013733 | -61.5189 | 60.2005 | 60.1501 | -61.2808 | -61.4136 | -0.064087 | -0.01831 | -0.064087 | 121.7377 | -0.13733 | -0.11902 | -0.041199 | 0 | -0.13275 | -0.073243 | 0.24262 | -0.23804 | -0.10529 | -0.1236 | 121.4905 | 121.5134 | 61.2396 | -121.5729 | 121.4813 | 121.431 | 61.2946 | -121.6873
982.4375 | 121.9391 | -61.2946 | 60.2966 | 0.094299 | 0.017929 | 0.073785 | 0.063429 | 0.12866 | 0.0010276 | -0.0039606 | 0.11322 | -0.0056332 | 0.061662 | 0.071673 | 0.0048769 | -0.0091709 | 60.1501 | 60.3653 | -0.13275 | -61.4685 | 60.2325 | -61.3632 | -61.3403 | -61.1252 | -0.073242 | -61.6196 | 60.2509 | 60.1913 | -61.2991 | -61.4594 | -0.068664 | -0.045776 | -0.064087 | 121.6599 | -0.17395 | -0.12817 | -0.14648 | -0.004577 | -0.16479 | -0.045777 | 0.16937 | -0.32501 | -0.16022 | -0.10529 | 121.5271 | 121.4447 | 61.1618 | -121.637 | 121.5454 | 121.4859 | 61.2213 | -121.756
984.1875 | 121.9482 | -61.2671 | 60.2875 | 0.10956 | 0.01622 | 0.073999 | 0.065138 | 0.12695 | -0.0021768 | -0.0039606 | 0.2124 | -0.0077696 | 0.060808 | 0.071673 | 0.0029543 | -0.0081027 | 60.2417 | 60.4752 | 0 | -61.3861 | 60.1685 | -61.3358 | -61.3037 | -61.0474 | 0.059509 | -61.496 | 60.1776 | 60.1364 | -61.2854 | -61.409 | -0.068664 | -0.036621 | -0.11902 | 121.7422 | -0.11902 | -0.082397 | -0.045777 | -0.01831 | -0.14191 | -0.10986 | 0.21973 | -0.22888 | -0.086975 | -0.15106 | 121.4355 | 121.5088 | 61.2671 | -121.5912 | 121.4447 | 121.4035 | 61.3266 | -121.6965
985.9375 | 121.8384 | -61.3312 | 60.3149 | -0.020142 | 0.019638 | 0.075494 | 0.066633 | 0.12717 | 0.0010276 | -0.003747 | 0.097962 | -0.0043516 | 0.064012 | 0.074236 | 0.0057315 | -0.0089573 | 60.173 | 60.3745 | -0.036621 | -61.4502 | 60.228 | -61.3358 | -61.3174 | -61.171 | -0.027466 | -61.6425 | 60.2371 | 60.2005 | -61.3129 | -61.4502 | -0.004577 | 0.013733 | -0.086975 | 121.7056 | -0.11902 | -0.13275 | -0.14191 | 0.018311 | -0.11902 | -0.077819 | 0.16022 | -0.31128 | -0.19226 | -0.11444 | 121.5591 | 121.5042 | 61.2946 | -121.6324 | 121.5683 | 121.5317 | 61.3037 | -121.7651
987.625 | 121.8384 | -61.2259 | 60.4065 | -0.21851 | 0.017929 | 0.073999 | 0.071333 | 0.1308 | -0.0064492 | -0.0026788 | -0.046997 | -0.005206 | 0.062303 | 0.07445 | -0.00089089 | -0.0076755 | 60.2737 | 60.498 | 0.17395 | -61.3358 | 60.3195 | -61.2671 | -61.2259 | -61.0611 | 0.19226 | -61.5143 | 60.3104 | 60.3012 | -61.2167 | -61.322 | -0.041199 | 0 | -0.086975 | 121.7239 | -0.10986 | -0.10986 | -0.13275 | 0.009155 | -0.09613 | -0.09613 | 0.16479 | -0.28839 | -0.19226 | -0.10529 | 121.5454 | 121.4996 | 61.3998 | -121.6324 | 121.5363 | 121.5271 | 61.4182 | -121.7285
989.375 | 121.8567 | -61.235 | 60.4385 | -0.1651 | 0.017502 | 0.073785 | 0.068129 | 0.12994 | -0.0047404 | -0.0063104 | -0.062256 | -0.006915 | 0.061021 | 0.0721 | 0.00060451 | -0.0093845 | 60.3104 | 60.553 | 0.23804 | -61.2854 | 60.2875 | -61.2442 | -61.203 | -60.9924 | 0.29297 | -61.409 | 60.2921 | 60.2829 | -61.1847 | -61.3174 | -0.009156 | 0.032043 | -0.15106 | 121.788 | -0.050354 | -0.082397 | -0.12817 | 0.050354 | -0.082398 | -0.14648 | 0.24261 | -0.17395 | -0.091553 | -0.15564 | 121.5225 | 121.5454 | 61.4731 | -121.6415 | 121.5271 | 121.5179 | 61.528 | -121.756
991.125 | 121.8292 | -61.235 | 60.434 | -0.23376 | 0.016648 | 0.074426 | 0.06642 | 0.13016 | -0.004313 | -0.0039606 | -0.14618 | -0.0062742 | 0.063585 | 0.072314 | 0.0014591 | -0.0083163 | 60.2921 | 60.4889 | 0.1831 | -61.3449 | 60.3012 | -61.2259 | -61.2122 | -61.0611 | 0.18768 | -61.5051 | 60.3516 | 60.3058 | -61.2396 | -61.3678 | 0.009155 | 0.022888 | -0.13275 | 121.7239 | -0.10986 | -0.13275 | -0.14191 | -0.004578 | -0.13275 | -0.082398 | 0.17395 | -0.27008 | -0.13733 | -0.12817 | 121.5363 | 121.5271 | 61.4182 | -121.6461 | 121.5866 | 121.5408 | 61.4227 | -121.8018
992.875 | 121.8521 | -61.3495 | 60.3104 | 0.063782 | 0.016648 | 0.072504 | 0.06407 | 0.12888 | 0.00081382 | -0.0041742 | 0.044556 | -0.0047788 | 0.061449 | 0.072741 | 0.0065859 | -0.010453 | 60.1547 | 60.3333 | -0.09613 | -61.4731 | 60.2463 | -61.3449 | -61.3266 | -61.1801 | -0.082397 | -61.6653 | 60.2554 | 60.1868 | -61.3174 | -61.4822 | 0.004577 | 0.022888 | -0.064087 | 121.6827 | -0.1236 | -0.14648 | -0.15564 | 0.032043 | -0.13275 | -0.054932 | 0.16937 | -0.31586 | -0.1831 | -0.1236 | 121.5958 | 121.5042 | 61.2534 | -121.637 | 121.6049 | 121.5363 | 61.2671 | -121.7926
994.625 | 121.8613 | -61.2762 | 60.4248 | -0.21851 | 0.017716 | 0.073358 | 0.067274 | 0.12781 | -0.0030314 | -0.0050286 | -0.18433 | -0.0071286 | 0.06508 | 0.070605 | 0.0012455 | -0.0087435 | 60.2509 | 60.4568 | 0.1236 | -61.377 | 60.3333 | -61.2762 | -61.2396 | -61.0794 | 0.1831 | -61.5189 | 60.3333 | 60.3058 | -61.1938 | -61.3678 | 0 | 0.036621 | -0.091553 | 121.7331 | -0.10071 | -0.13733 | -0.17395 | 0.082397 | -0.091553 | -0.091553 | 0.19684 | -0.24261 | -0.15106 | -0.11902 | 121.6095 | 121.5271 | 61.3998 | -121.6644 | 121.6095 | 121.582 | 61.4594 | -121.7926
996.3125 | 121.8521 | -61.322 | 60.3378 | -0.096436 | 0.018997 | 0.071222 | 0.062788 | 0.12824 | 0.00060022 | -0.0035334 | -0.062256 | -0.0073422 | 0.063371 | 0.07445 | 0.0042361 | -0.0083163 | 60.2509 | 60.4294 | 0.064087 | -61.3998 | 60.2829 | -61.3403 | -61.2854 | -61.0657 | 0.10986 | -61.5372 | 60.2554 | 60.2325 | -61.2717 | -61.4182 | -0.018311 | 0.036621 | -0.054932 | 121.7514 | -0.07782 | -0.11444 | -0.086976 | 0.050354 | -0.096131 | -0.082398 | 0.25635 | -0.21515 | -0.11902 | -0.10529 | 121.6049 | 121.5729 | 61.3861 | -121.6232 | 121.5775 | 121.5546 | 61.4319 | -121.756
998.0625 | 121.9574 | -61.2259 | 60.3928 | 0.010376 | 0.013657 | 0.075281 | 0.065565 | 0.12717 | -0.0087992 | -0.0060968 | 0.13611 | -0.008624 | 0.062303 | 0.069964 | 0.0018863 | -0.0063937 | 60.2234 | 60.4752 | 0.07782 | -61.3678 | 60.2554 | -61.2534 | -61.235 | -61.0428 | 0.11444 | -61.4777 | 60.2463 | 60.2234 | -61.1984 | -61.3724 | -0.027466 | -0.009155 | -0.13733 | 121.701 | -0.14191 | -0.13275 | -0.16937 | 0.027466 | -0.14648 | -0.14648 | 0.1831 | -0.25177 | -0.10529 | -0.16937 | 121.4813 | 121.4493 | 61.3037 | -121.6278 | 121.4722 | 121.4493 | 61.3403 | -121.7651
999.8125 | 121.8842 | -61.2946 | 60.3516 | -0.17273 | 0.016434 | 0.073785 | 0.068769 | 0.12973 | 0.00017302 | -0.0039606 | -0.16907 | -0.005847 | 0.061876 | 0.072954 | 0.0023135 | -0.0098117 | 60.2417 | 60.4294 | 0.091553 | -61.3678 | 60.3058 | -61.2579 | -61.2579 | -61.0748 | 0.15106 | -61.5509 | 60.3058 | 60.2875 | -61.2625 | -61.4182 | 0.036621 | 0.036621 | -0.045776 | 121.7239 | -0.073242 | -0.10986 | -0.10986 | 0.032044 | -0.1236 | -0.045776 | 0.21973 | -0.25635 | -0.13275 | -0.064086 | 121.6003 | 121.5363 | 61.3861 | -121.6095 | 121.6003 | 121.582 | 61.4456 | -121.7697
1001.5625 | 121.9345 | -61.2396 | 60.3882 | 0.010376 | 0.012162 | 0.076135 | 0.063429 | 0.12759 | -0.0075174 | -0.0046014 | 0.13611 | -0.010333 | 0.060594 | 0.069964 | 0.0027407 | -0.0070345 | 60.2371 | 60.4752 | 0.045776 | -61.3541 | 60.2325 | -61.2717 | -61.2534 | -61.0474 | 0.10986 | -61.4777 | 60.2509 | 60.2371 | -61.2259 | -61.3724 | -0.032043 | -0.013733 | -0.15564 | 121.7148 | -0.11444 | -0.10071 | -0.15106 | 0.013733 | -0.13275 | -0.13733 | 0.19226 | -0.23804 | -0.10529 | -0.15106 | 121.4722 | 121.4767 | 61.2854 | -121.6415 | 121.4905 | 121.4767 | 61.3495 | -121.7606
1003.25 | 121.9574 | -61.2579 | 60.2966 | 0.12482 | 0.017075 | 0.073358 | 0.066206 | 0.12653 | -0.001536 | -0.0039606 | 0.16663 | -0.0088376 | 0.060808 | 0.071032 | 0.0040225 | -0.0093845 | 60.2371 | 60.4248 | -0.059509 | -61.3861 | 60.2234 | -61.3266 | -61.2854 | -61.0565 | 0.027466 | -61.528 | 60.2051 | 60.1547 | -61.2717 | -61.4136 | -0.068664 | -0.027465 | -0.073242 | 121.6827 | -0.12817 | -0.10071 | -0.059509 | -0.013732 | -0.15564 | -0.091553 | 0.20142 | -0.27008 | -0.11444 | -0.14191 | 121.4813 | 121.4951 | 61.1984 | -121.582 | 121.463 | 121.4127 | 61.2854 | -121.7102
1005 | 121.9803 | -61.1801 | 60.4111 | -0.14984 | 0.015793 | 0.072717 | 0.067274 | 0.1308 | -0.0062356 | -0.0052424 | 0.029297 | -0.0084104 | 0.062303 | 0.071673 | 0.00060451 | -0.0087435 | 60.3424 | 60.585 | 0.21057 | -61.2762 | 60.2829 | -61.235 | -61.1755 | -60.9283 | 0.27924 | -61.3632 | 60.2921 | 60.2554 | -61.1801 | -61.29 | -0.054931 | 0.004578 | -0.12817 | 121.7651 | -0.09613 | -0.10071 | -0.068665 | 0 | -0.10986 | -0.11902 | 0.25177 | -0.1831 | -0.073242 | -0.15564 | 121.463 | 121.5225 | 61.3907 | -121.5866 | 121.4722 | 121.4355 | 61.4594 | -121.701
1006.7344 | 121.8658 | -61.203 | 60.4294 | -0.20325 | 0.016434 | 0.074426 | 0.068342 | 0.12845 | -0.006663 | -0.0043878 | -0.085144 | -0.0084104 | 0.063585 | 0.073809 | 0.0023135 | -0.011948 | 60.3516 | 60.5667 | 0.24719 | -61.2854 | 60.3195 | -61.2305 | -61.1755 | -60.9833 | 0.29297 | -61.4136 | 60.3012 | 60.2463 | -61.1664 | -61.3174 | -0.027466 | 0.027466 | -0.10986 | 121.7697 | -0.082397 | -0.10986 | -0.07782 | 0.036621 | -0.11444 | -0.12817 | 0.21973 | -0.21057 | -0.09613 | -0.1831 | 121.5225 | 121.5546 | 61.4502 | -121.6049 | 121.5042 | 121.4493 | 61.496 | -121.7468
1008.4844 | 121.9162 | -61.2122 | 60.4294 | -0.21088 | 0.016434 | 0.072717 | 0.067274 | 0.12674 | -0.0045266 | -0.0063104 | -0.085144 | -0.0079832 | 0.061235 | 0.071673 | 0.0027407 | -0.010453 | 60.3653 | 60.5988 | 0.25635 | -61.2762 | 60.2966 | -61.2076 | -61.2076 | -60.9695 | 0.30212 | -61.4044 | 60.2737 | 60.2875 | -61.1801 | -61.322 | 0.004577 | 0.004577 | -0.13275 | 121.8109 | -0.064087 | -0.068664 | -0.064087 | 0.032043 | -0.10986 | -0.15564 | 0.24262 | -0.19226 | -0.082398 | -0.14191 | 121.5088 | 121.5775 | 61.4685 | -121.637 | 121.4859 | 121.4996 | 61.5143 | -121.7514
1010.1562 | 121.9803 | -61.2717 | 60.2921 | 0.14771 | 0.014084 | 0.071863 | 0.059797 | 0.1293 | 0.00081382 | -0.0026788 | 0.15137 | -0.0067014 | 0.061021 | 0.073382 | 0.0046633 | -0.010239 | 60.2417 | 60.4431 | -0.036621 | -61.3953 | 60.2234 | -61.3449 | -61.2946 | -61.0428 | 0.027466 | -61.528 | 60.2097 | 60.1593 | -61.2717 | -61.4273 | -0.073243 | -0.022889 | -0.068664 | 121.7148 | -0.1236 | -0.10071 | -0.050354 | 0 | -0.15564 | -0.082397 | 0.22888 | -0.25635 | -0.10071 | -0.13275 | 121.4951 | 121.5134 | 61.235 | -121.5866 | 121.4813 | 121.431 | 61.2991 | -121.7194
1011.9062 | 121.9299 | -61.2442 | 60.3607 | 0.12482 | 0.013657 | 0.07229 | 0.064924 | 0.12824 | -0.004313 | -0.004815 | 0.16663 | -0.0084104 | 0.061449 | 0.074236 | 0.0020999 | -0.010666 | 60.2554 | 60.4843 | 0.018311 | -61.3724 | 60.1868 | -61.2854 | -61.2579 | -61.0062 | 0.07782 | -61.5051 | 60.1913 | 60.1776 | -61.2442 | -61.4273 | -0.041198 | -0.013733 | -0.17395 | 121.7285 | -0.12817 | -0.11444 | -0.10529 | 0 | -0.1831 | -0.16937 | 0.23804 | -0.26093 | -0.07782 | -0.18311 | 121.431 | 121.4996 | 61.2625 | -121.6187 | 121.4355 | 121.4218 | 61.322 | -121.788
1013.5781 | 121.9482 | -61.2122 | 60.4156 | 0.0027468 | 0.014725 | 0.075922 | 0.066847 | 0.12674 | -0.0055948 | -0.005456 | 0.13611 | -0.0064878 | 0.062089 | 0.070818 | 0.0027407 | -0.0098117 | 60.26 | 60.4752 | 0.064087 | -61.3541 | 60.2554 | -61.2534 | -61.2305 | -61.0291 | 0.10529 | -61.496 | 60.2875 | 60.228 | -61.2213 | -61.3541 | -0.041199 | -0.018311 | -0.16022 | 121.6873 | -0.14191 | -0.1236 | -0.15564 | -0.009155 | -0.14191 | -0.12817 | 0.18311 | -0.28381 | -0.14191 | -0.18768 | 121.4676 | 121.4722 | 61.2762 | -121.6461 | 121.4996 | 121.4401 | 61.3174 | -121.7697
1015.3125 | 122.0032 | -61.1938 | 60.4111 | -0.058289 | 0.01558 | 0.075281 | 0.065138 | 0.13016 | -0.0055948 | -0.0058832 | -0.031738 | -0.008624 | 0.061235 | 0.071673 | 0.00081811 | -0.010666 | 60.3104 | 60.5438 | 0.15106 | -61.3129 | 60.2966 | -61.2534 | -61.2167 | -60.9467 | 0.25177 | -61.4044 | 60.2737 | 60.26 | -61.171 | -61.3495 | -0.059509 | -0.022888 | -0.11444 | 121.7377 | -0.11902 | -0.09613 | -0.10071 | 0.022889 | -0.15564 | -0.13733 | 0.24719 | -0.21057 | -0.054932 | -0.15106 | 121.4905 | 121.5042 | 61.3449 | -121.6278 | 121.4676 | 121.4539 | 61.4456 | -121.7606
1017.0625 | 121.9482 | -61.2762 | 60.3104 | 0.11719 | 0.017716 | 0.072931 | 0.06172 | 0.12759 | -0.0011088 | -0.003747 | 0.18951 | -0.0071286 | 0.05974 | 0.071886 | 0.0067997 | -0.011307 | 60.2829 | 60.4523 | -0.013733 | -61.377 | 60.2051 | -61.3174 | -61.2946 | -61.0382 | 0.018311 | -61.5189 | 60.1959 | 60.141 | -61.2854 | -61.4182 | -0.041199 | -0.018311 | -0.10529 | 121.7285 | -0.10071 | -0.082397 | -0.027466 | -0.009155 | -0.14191 | -0.11444 | 0.23804 | -0.24261 | -0.10071 | -0.16937 | 121.4813 | 121.5591 | 61.2625 | -121.6049 | 121.4722 | 121.4172 | 61.2946 | -121.7285
1018.7344 | 121.8338 | -61.3449 | 60.3424 | -0.0048827 | 0.019211 | 0.070581 | 0.06407 | 0.12909 | 0.0027364 | -0.0024652 | 0.052185 | -0.005206 | 0.060808 | 0.074236 | 0.0055179 | -0.011521 | 60.1868 | 60.3333 | -0.068665 | -61.4639 | 60.2325 | -61.3541 | -61.3266 | -61.1526 | -0.045776 | -61.6562 | 60.2692 | 60.2188 | -61.3037 | -61.4456 | -0.009155 | 0.018311 | -0.10986 | 121.6782 | -0.11902 | -0.13733 | -0.15564 | 0.041199 | -0.10071 | -0.073242 | 0.19226 | -0.31128 | -0.21057 | -0.1236 | 121.5775 | 121.5317 | 61.2762 | -121.669 | 121.6141 | 121.5637 | 61.2991 | -121.788
1020.4844 | 121.9116 | -61.235 | 60.3745 | 0.063782 | 0.016007 | 0.071649 | 0.069197 | 0.12994 | -0.0073038 | -0.0041742 | 0.14374 | -0.0073422 | 0.062944 | 0.072954 | 0.00017731 | -0.0098117 | 60.2554 | 60.4752 | 0.050354 | -61.3678 | 60.2371 | -61.2762 | -61.2442 | -61.0199 | 0.073242 | -61.5097 | 60.2692 | 60.2371 | -61.235 | -61.3724 | -0.041199 | -0.009156 | -0.13733 | 121.7102 | -0.13275 | -0.1236 | -0.11902 | 0 | -0.13733 | -0.10529 | 0.21515 | -0.27466 | -0.13733 | -0.13733 | 121.4722 | 121.4905 | 61.2854 | -121.6187 | 121.5042 | 121.4722 | 61.3083 | -121.7468
1022.25 | 121.8887 | -61.3266 | 60.3104 | 0.094299 | 0.018357 | 0.071649 | 0.064497 | 0.12909 | 0.0014548 | -0.0024652 | 0.097962 | -0.0054196 | 0.063371 | 0.073809 | 0.0046633 | -0.011094 | 60.1822 | 60.3104 | -0.11444 | -61.4731 | 60.2371 | -61.3495 | -61.322 | -61.1389 | -0.09613 | -61.6562 | 60.2371 | 60.1913 | -61.3312 | -61.4594 | -0.022888 | 0.004578 | -0.073242 | 121.637 | -0.14648 | -0.15106 | -0.12817 | -0.004578 | -0.13275 | -0.073242 | 0.18768 | -0.32959 | -0.19684 | -0.11902 | 121.5637 | 121.5088 | 61.2122 | -121.6324 | 121.5637 | 121.5179 | 61.2305 | -121.7697
1023.9375 | 121.8842 | -61.2762 | 60.3516 | -0.17273 | 0.018997 | 0.073358 | 0.067488 | 0.12909 | -0.00068138 | -0.0035334 | -0.19196 | -0.0060606 | 0.063585 | 0.071673 | 0.0033817 | -0.011948 | 60.2417 | 60.4477 | 0.10986 | -61.3815 | 60.3241 | -61.2808 | -61.2579 | -61.0703 | 0.14191 | -61.5417 | 60.3195 | 60.2737 | -61.2762 | -61.3907 | -0.004578 | 0.01831 | -0.027465 | 121.7239 | -0.10529 | -0.1236 | -0.10986 | 0 | -0.11444 | -0.032043 | 0.20599 | -0.2655 | -0.15106 | -0.077819 | 121.6003 | 121.5179 | 61.3861 | -121.6095 | 121.5958 | 121.55 | 61.4182 | -121.7422
1025.6719 | 121.8613 | -61.322 | 60.3195 | 0.056152 | 0.021988 | 0.070795 | 0.068983 | 0.12824 | -4.058e-05 | -0.0026788 | 0.044556 | -0.0047788 | 0.064653 | 0.072741 | 0.0027407 | -0.010239 | 60.1547 | 60.3104 | -0.082397 | -61.4639 | 60.2417 | -61.3358 | -61.322 | -61.1847 | -0.073242 | -61.6928 | 60.2325 | 60.2005 | -61.3129 | -61.4685 | -0.013733 | 0 | -0.07782 | 121.6324 | -0.14191 | -0.14191 | -0.16479 | 0.009155 | -0.14648 | -0.086975 | 0.13733 | -0.37079 | -0.2243 | -0.11902 | 121.5637 | 121.4767 | 61.2396 | -121.6415 | 121.5546 | 121.5225 | 61.2488 | -121.788
1027.4219 | 121.8292 | -61.2213 | 60.4385 | -0.23376 | 0.018784 | 0.073999 | 0.068769 | 0.12994 | -0.0040994 | -0.0016108 | -0.12329 | -0.0056332 | 0.062944 | 0.072527 | -0.00046349 | -0.0089573 | 60.2554 | 60.4797 | 0.14648 | -61.3403 | 60.3149 | -61.2396 | -61.2396 | -61.0519 | 0.19226 | -61.5097 | 60.347 | 60.3012 | -61.2167 | -61.3449 | -0.018311 | -0.018311 | -0.1236 | 121.701 | -0.11902 | -0.10071 | -0.18311 | 0.004577 | -0.1236 | -0.091553 | 0.16937 | -0.28839 | -0.16479 | -0.13733 | 121.5363 | 121.4767 | 61.3678 | -121.6782 | 121.5683 | 121.5225 | 61.4136 | -121.7834
1029.1875 | 121.8796 | -61.2717 | 60.3516 | -0.17273 | 0.020706 | 0.073785 | 0.066847 | 0.12973 | -0.00089518 | -0.0050286 | -0.14618 | -0.0064878 | 0.06273 | 0.072954 | 0.0035953 | -0.0089573 | 60.2325 | 60.434 | 0.10986 | -61.3632 | 60.3241 | -61.2534 | -61.2625 | -61.0886 | 0.14191 | -61.5417 | 60.2966 | 60.2417 | -61.2488 | -61.4319 | 0.01831 | 0.009155 | -0.027465 | 121.7056 | -0.091553 | -0.10071 | -0.11902 | 0.022888 | -0.16022 | -0.054931 | 0.1831 | -0.27008 | -0.10986 | -0.10986 | 121.5958 | 121.5042 | 61.3815 | -121.6141 | 121.5683 | 121.5134 | 61.4136 | -121.7834
1030.875 | 121.8658 | -61.29 | 60.3653 | -0.11932 | 0.02092 | 0.072076 | 0.065351 | 0.13016 | -0.001536 | -0.0039606 | -0.054626 | -0.005847 | 0.063371 | 0.074236 | 0.0053043 | -0.0078891 | 60.2417 | 60.4523 | 0.073242 | -61.3815 | 60.2921 | -61.3174 | -61.2854 | -61.0611 | 0.1236 | -61.5509 | 60.2692 | 60.2188 | -61.2671 | -61.4548 | -0.027466 | 0.004578 | -0.073242 | 121.7422 | -0.091553 | -0.096131 | -0.1236 | 0.022888 | -0.1648 | -0.09613 | 0.22888 | -0.26093 | -0.09613 | -0.14648 | 121.582 | 121.5317 | 61.3632 | -121.6507 | 121.5591 | 121.5088 | 61.4136 | -121.8201
1032.6406 | 121.8842 | -61.2534 | 60.3745 | -0.21851 | 0.016861 | 0.07464 | 0.06642 | 0.12952 | -0.0011088 | -0.003106 | -0.12329 | -0.0071286 | 0.061876 | 0.074023 | 0.0012455 | -0.0081027 | 60.2142 | 60.4385 | 0.10986 | -61.3678 | 60.2921 | -61.2808 | -61.2488 | -61.0886 | 0.16937 | -61.5143 | 60.3424 | 60.2737 | -61.2488 | -61.377 | -0.027466 | 0.004578 | -0.082398 | 121.6919 | -0.11444 | -0.11902 | -0.16022 | 0.004578 | -0.1236 | -0.032044 | 0.16479 | -0.26093 | -0.13733 | -0.10071 | 121.5454 | 121.4676 | 61.3632 | -121.6232 | 121.5958 | 121.5271 | 61.4227 | -121.7514
1034.3281 | 121.907 | -61.2396 | 60.3424 | 0.08667 | 0.014298 | 0.073358 | 0.06706 | 0.12866 | -0.0058084 | -0.0050286 | 0.25055 | -0.0090512 | 0.061876 | 0.072314 | 0.0014591 | -0.0081027 | 60.2371 | 60.5118 | 0.032043 | -61.377 | 60.1959 | -61.2854 | -61.2534 | -61.0382 | 0.068665 | -61.4914 | 60.2097 | 60.1776 | -61.2396 | -61.409 | -0.045776 | -0.013733 | -0.14648 | 121.7514 | -0.13733 | -0.1236 | -0.10529 | 0 | -0.16937 | -0.13275 | 0.20142 | -0.25177 | -0.082397 | -0.16479 | 121.4355 | 121.4767 | 61.2717 | -121.5958 | 121.4493 | 121.4172 | 61.3083 | -121.7514
1036.0625 | 121.8384 | -61.2579 | 60.4156 | -0.17273 | 0.01857 | 0.076349 | 0.069624 | 0.12909 | -0.0028178 | -0.0067376 | -0.14618 | -0.0067014 | 0.064012 | 0.070818 | 0.0029543 | -0.0083163 | 60.2371 | 60.4706 | 0.14191 | -61.3586 | 60.3012 | -61.2579 | -61.2442 | -61.0657 | 0.1831 | -61.5097 | 60.3607 | 60.2966 | -61.2259 | -61.3632 | 0 | 0.013733 | -0.11444 | 121.7285 | -0.10071 | -0.11444 | -0.17853 | 0.032044 | -0.10528 | -0.054931 | 0.19226 | -0.25177 | -0.14648 | -0.11902 | 121.5591 | 121.4951 | 61.3998 | -121.6599 | 121.6187 | 121.5546 | 61.441 | -121.7789
1037.75 | 121.8796 | -61.2854 | 60.3745 | -0.25665 | 0.018784 | 0.074854 | 0.066206 | 0.12909 | -0.0030314 | -0.0043878 | -0.16144 | -0.0064878 | 0.065294 | 0.073382 | 0.0031681 | -0.0098117 | 60.228 | 60.4568 | 0.11902 | -61.3678 | 60.347 | -61.2579 | -61.2488 | -61.0748 | 0.15106 | -61.5417 | 60.347 | 60.2829 | -61.2625 | -61.3678 | 0.027465 | 0.036621 | -0.027466 | 121.7422 | -0.082398 | -0.11902 | -0.14648 | 0.022888 | -0.082398 | -0.027466 | 0.21057 | -0.25635 | -0.17395 | -0.091553 | 121.6324 | 121.5134 | 61.4044 | -121.6232 | 121.6324 | 121.5683 | 61.4365 | -121.7422
1039.4844 | 121.8338 | -61.3037 | 60.3104 | -0.081177 | 0.020493 | 0.073785 | 0.066633 | 0.13208 | 0.001882 | -0.003106 | -0.046997 | -0.0047788 | 0.061876 | 0.072954 | 0.0059451 | -0.010025 | 60.2509 | 60.4248 | 0.041199 | -61.3953 | 60.2646 | -61.3083 | -61.3037 | -61.0977 | 0.07782 | -61.5646 | 60.2371 | 60.2234 | -61.2625 | -61.409 | -0.004578 | 0 | -0.045777 | 121.7285 | -0.091553 | -0.091553 | -0.05951 | 0.041199 | -0.10529 | -0.073242 | 0.20599 | -0.26093 | -0.15564 | -0.086975 | 121.5683 | 121.5546 | 61.3449 | -121.6141 | 121.5408 | 121.5271 | 61.3815 | -121.7194
1041.2344 | 121.9482 | -61.2717 | 60.3012 | 0.15533 | 0.018357 | 0.074854 | 0.063856 | 0.12653 | -0.0047404 | -0.0026788 | 0.13611 | -0.0062742 | 0.061662 | 0.073595 | 0.0033817 | -0.0072483 | 60.1913 | 60.4111 | -0.054932 | -61.4182 | 60.2188 | -61.322 | -61.3129 | -61.0565 | 0.018311 | -61.5326 | 60.2234 | 60.1685 | -61.2854 | -61.4273 | -0.050354 | -0.041199 | -0.082397 | 121.6827 | -0.14648 | -0.10529 | -0.10986 | -0.013733 | -0.15564 | -0.077819 | 0.21515 | -0.26093 | -0.10529 | -0.13275 | 121.4905 | 121.463 | 61.2167 | -121.6141 | 121.4951 | 121.4401 | 61.29 | -121.7285
1042.9844 | 121.9574 | -61.1893 | 60.3973 | -0.14221 | 0.015793 | 0.073358 | 0.067701 | 0.12845 | -0.006663 | -0.005456 | -0.016479 | -0.0064878 | 0.063371 | 0.073809 | -0.00067729 | -0.0072483 | 60.3333 | 60.5988 | 0.23804 | -61.2762 | 60.2783 | -61.2259 | -61.2076 | -60.9421 | 0.29297 | -61.377 | 60.2875 | 60.2829 | -61.1618 | -61.3083 | -0.036621 | -0.018311 | -0.11902 | 121.788 | -0.086975 | -0.068664 | -0.064087 | 0.027466 | -0.11902 | -0.10986 | 0.24719 | -0.18768 | -0.068664 | -0.11444 | 121.4676 | 121.5225 | 61.4273 | -121.6049 | 121.4767 | 121.4722 | 61.4822 | -121.7056
1044.6719 | 121.9574 | -61.2442 | 60.3195 | 0.11719 | 0.016007 | 0.073999 | 0.064711 | 0.12888 | -0.0028178 | -0.004815 | 0.22003 | -0.0073422 | 0.060167 | 0.072314 | 0.0038089 | -0.010453 | 60.2463 | 60.4706 | -0.013733 | -61.3815 | 60.1959 | -61.3495 | -61.2671 | -61.0565 | 0.036621 | -61.5189 | 60.173 | 60.1547 | -61.29 | -61.4365 | -0.10529 | -0.022888 | -0.1236 | 121.7148 | -0.13733 | -0.11444 | -0.073242 | -0.045776 | -0.19226 | -0.14648 | 0.18768 | -0.27466 | -0.082398 | -0.16479 | 121.4401 | 121.4905 | 61.2305 | -121.5866 | 121.4172 | 121.3989 | 61.2808 | -121.756
1046.4062 | 121.9528 | -61.2534 | 60.3104 | 0.14771 | 0.017075 | 0.075281 | 0.063215 | 0.12994 | -0.0019632 | -0.0039606 | 0.159 | -0.0099058 | 0.060381 | 0.071459 | 0.0046633 | -0.0095981 | 60.2325 | 60.4614 | -0.032043 | -61.3998 | 60.2142 | -61.3403 | -61.3037 | -61.0382 | 0.036621 | -61.528 | 60.2005 | 60.1456 | -61.2762 | -61.4273 | -0.086975 | -0.050354 | -0.096131 | 121.7148 | -0.14648 | -0.09613 | -0.07782 | -0.022888 | -0.17395 | -0.10986 | 0.21515 | -0.27466 | -0.10071 | -0.16479 | 121.4676 | 121.4859 | 61.2213 | -121.6141 | 121.4539 | 121.3989 | 61.29 | -121.7377
1048.1562 | 121.9757 | -61.2122 | 60.3745 | 0.0027468 | 0.015366 | 0.078058 | 0.066206 | 0.12781 | -0.007731 | -0.0050286 | 0.12085 | -0.0079832 | 0.061021 | 0.070177 | 0.00060451 | -0.0072483 | 60.2188 | 60.4935 | 0.073242 | -61.3541 | 60.2554 | -61.2579 | -61.235 | -61.0245 | 0.13275 | -61.4731 | 60.2509 | 60.2325 | -61.2122 | -61.377 | -0.045777 | -0.022888 | -0.11902 | 121.7056 | -0.14191 | -0.11902 | -0.15564 | 0 | -0.16479 | -0.1236 | 0.18768 | -0.26093 | -0.09613 | -0.14191 | 121.4676 | 121.431 | 61.2854 | -121.6095 | 121.463 | 121.4447 | 61.3449 | -121.7514
1049.8281 | 121.843 | -61.322 | 60.347 | -0.10406 | 0.020066 | 0.073785 | 0.06642 | 0.1308 | 0.0014548 | -0.0026788 | -0.062256 | -0.0045652 | 0.06273 | 0.075091 | 0.0038089 | -0.011521 | 60.2692 | 60.4614 | 0.059509 | -61.3724 | 60.2692 | -61.322 | -61.2854 | -61.0519 | 0.082397 | -61.5738 | 60.2783 | 60.228 | -61.2762 | -61.409 | 0 | 0.036621 | -0.07782 | 121.7834 | -0.050354 | -0.086975 | -0.07782 | 0.045776 | -0.086976 | -0.068665 | 0.27008 | -0.25177 | -0.16479 | -0.11902 | 121.5912 | 121.5912 | 61.3815 | -121.6324 | 121.6003 | 121.55 | 61.4044 | -121.756
1051.5781 | 121.8567 | -61.3266 | 60.3424 | 0.048523 | 0.018357 | 0.075067 | 0.065992 | 0.13101 | 0.0023092 | -0.0018244 | 0.052185 | -0.0043516 | 0.060808 | 0.072741 | 0.0046633 | -0.0089573 | 60.1547 | 60.3241 | -0.086975 | -61.4548 | 60.2554 | -61.3449 | -61.3083 | -61.1938 | -0.09613 | -61.6745 | 60.2509 | 60.2005 | -61.3129 | -61.4365 | -0.018311 | 0.01831 | -0.086975 | 121.6507 | -0.12817 | -0.14648 | -0.18768 | 0.013733 | -0.10986 | -0.091553 | 0.13275 | -0.3479 | -0.23804 | -0.14191 | 121.582 | 121.4813 | 61.2396 | -121.6507 | 121.5775 | 121.5271 | 61.2305 | -121.7789
1053.3281 | 121.8933 | -61.2534 | 60.3561 | -0.18799 | 0.018143 | 0.072076 | 0.066847 | 0.12888 | -0.0017496 | -0.0033196 | -0.10803 | -0.0067014 | 0.062303 | 0.071459 | 0.0023135 | -0.0091709 | 60.2188 | 60.4431 | 0.082397 | -61.3724 | 60.2966 | -61.3083 | -61.2946 | -61.0886 | 0.13733 | -61.5417 | 60.2692 | 60.2509 | -61.2625 | -61.3907 | -0.054932 | -0.041199 | -0.059509 | 121.6965 | -0.11902 | -0.077819 | -0.13733 | -0.009155 | -0.13733 | -0.086975 | 0.16479 | -0.28839 | -0.15106 | -0.10529 | 121.55 | 121.4722 | 61.3358 | -121.6507 | 121.5225 | 121.5042 | 61.3907 | -121.7468
1055.0625 | 121.8384 | -61.2991 | 60.3424 | -0.088806 | 0.02092 | 0.073572 | 0.067701 | 0.12759 | -0.00068138 | -0.000329 | -0.046997 | -0.0062742 | 0.06508 | 0.071459 | 0.0048769 | -0.010666 | 60.2371 | 60.4614 | 0.064087 | -61.3861 | 60.2417 | -61.3129 | -61.2808 | -61.0703 | 0.082397 | -61.5601 | 60.2554 | 60.2371 | -61.2625 | -61.3998 | -0.013733 | 0.01831 | -0.10071 | 121.7606 | -0.086975 | -0.10529 | -0.10529 | 0.036621 | -0.10071 | -0.086975 | 0.22888 | -0.26093 | -0.16022 | -0.10529 | 121.5408 | 121.5363 | 61.3632 | -121.6232 | 121.5546 | 121.5363 | 61.3815 | -121.7422
1056.75 | 121.8933 | -61.29 | 60.3882 | -0.21851 | 0.018784 | 0.075067 | 0.070692 | 0.12994 | -0.0034586 | -0.0035334 | -0.13092 | -0.0064878 | 0.063585 | 0.073168 | -0.0015317 | -0.0078891 | 60.2371 | 60.4385 | 0.11902 | -61.3541 | 60.3195 | -61.2671 | -61.2625 | -61.0886 | 0.15106 | -61.5509 | 60.3333 | 60.3104 | -61.2396 | -61.3724 | 0.022888 | 0.027466 | -0.068665 | 121.7285 | -0.064087 | -0.091553 | -0.15106 | 0.050354 | -0.082397 | -0.054932 | 0.20142 | -0.26093 | -0.17853 | -0.07782 | 121.6095 | 121.5271 | 61.409 | -121.6507 | 121.6232 | 121.6003 | 61.441 | -121.7606
1058.4844 | 121.9803 | -61.2946 | 60.2692 | 0.14771 | 0.019211 | 0.073572 | 0.062574 | 0.12973 | -0.0040994 | -0.0024652 | 0.22766 | -0.0054196 | 0.063371 | 0.071886 | 0.0023135 | -0.01088 | 60.1776 | 60.3882 | -0.091553 | -61.4456 | 60.2097 | -61.3266 | -61.3174 | -61.0886 | -0.013733 | -61.5463 | 60.2005 | 60.1822 | -61.29 | -61.441 | -0.032043 | -0.022888 | -0.059509 | 121.6827 | -0.15106 | -0.12817 | -0.091553 | 0.004578 | -0.14648 | -0.068665 | 0.20599 | -0.25177 | -0.10529 | -0.086975 | 121.5042 | 121.4722 | 61.203 | -121.5866 | 121.4951 | 121.4767 | 61.2808 | -121.7102
1060.2344 | 121.8338 | -61.2534 | 60.4294 | -0.21088 | 0.017716 | 0.072931 | 0.069838 | 0.13059 | -0.006663 | -0.0050286 | -0.077515 | -0.0088376 | 0.062944 | 0.071673 | 0.0014591 | -0.0083163 | 60.2509 | 60.4843 | 0.16479 | -61.3495 | 60.3287 | -61.2534 | -61.2534 | -61.0703 | 0.19226 | -61.5189 | 60.3561 | 60.3058 | -61.2213 | -61.3541 | 0 | 0 | -0.10071 | 121.7377 | -0.09613 | -0.09613 | -0.17853 | 0.032044 | -0.10071 | -0.073242 | 0.18311 | -0.2655 | -0.16479 | -0.1236 | 121.582 | 121.5042 | 61.4182 | -121.6827 | 121.6095 | 121.5591 | 61.4456 | -121.7834
1061.9844 | 121.8384 | -61.3083 | 60.347 | 0.040894 | 0.017716 | 0.074213 | 0.065992 | 0.12759 | -0.00089518 | -0.0039606 | 0.075073 | -0.0054196 | 0.061235 | 0.074663 | 0.0050907 | -0.010239 | 60.1547 | 60.3333 | -0.082397 | -61.4731 | 60.2554 | -61.322 | -61.3129 | -61.1801 | -0.086975 | -61.702 | 60.2234 | 60.2051 | -61.3129 | -61.4777 | -0.013732 | -0.004577 | -0.091553 | 121.6415 | -0.16479 | -0.16022 | -0.19226 | -0.004577 | -0.16937 | -0.1236 | 0.12817 | -0.39368 | -0.2243 | -0.14191 | 121.5637 | 121.463 | 61.2259 | -121.6599 | 121.5317 | 121.5134 | 61.2213 | -121.8246
1063.7344 | 121.9757 | -61.1755 | 60.3882 | -0.20325 | 0.01558 | 0.075281 | 0.068129 | 0.12973 | -0.011149 | -0.0041742 | 0.021668 | -0.008624 | 0.062089 | 0.070605 | -0.00067729 | -0.0081027 | 60.3058 | 60.585 | 0.20142 | -61.2762 | 60.2646 | -61.2259 | -61.203 | -60.9558 | 0.25177 | -61.3861 | 60.2829 | 60.2783 | -61.1893 | -61.3403 | -0.050354 | -0.027466 | -0.1236 | 121.7606 | -0.10071 | -0.073242 | -0.082398 | -0.013733 | -0.16479 | -0.10529 | 0.21973 | -0.21057 | -0.045776 | -0.10986 | 121.4401 | 121.4813 | 61.377 | -121.5912 | 121.4584 | 121.4539 | 61.4273 | -121.7285
1065.4219 | 121.8933 | -61.2396 | 60.3882 | -0.21088 | 0.017075 | 0.073572 | 0.064924 | 0.1261 | -0.00089518 | -0.0050286 | -0.12329 | -0.0049924 | 0.060808 | 0.072741 | 0.0033817 | -0.010666 | 60.26 | 60.4294 | 0.10986 | -61.377 | 60.3333 | -61.2717 | -61.2717 | -61.084 | 0.14191 | -61.5555 | 60.3516 | 60.2646 | -61.203 | -61.3632 | -0.032043 | -0.032043 | -0.054932 | 121.669 | -0.13733 | -0.10529 | -0.12817 | 0.036621 | -0.1236 | -0.036622 | 0.15564 | -0.31586 | -0.19226 | -0.1236 | 121.5729 | 121.4996 | 61.3495 | -121.6599 | 121.5912 | 121.5042 | 61.3815 | -121.7514
1067.1719 | 121.9757 | -61.1938 | 60.3928 | 0.010376 | 0.015152 | 0.075281 | 0.063215 | 0.13101 | -0.008372 | -0.0043878 | 0.12085 | -0.011401 | 0.061449 | 0.070391 | 0.0033817 | -0.0081027 | 60.2325 | 60.4797 | 0.064087 | -61.3586 | 60.2692 | -61.2396 | -61.2259 | -61.0474 | 0.10986 | -61.4822 | 60.2692 | 60.2234 | -61.2076 | -61.3861 | -0.045776 | -0.032043 | -0.1236 | 121.6736 | -0.16479 | -0.13275 | -0.16022 | -0.013733 | -0.19226 | -0.1236 | 0.14649 | -0.28839 | -0.096131 | -0.16937 | 121.463 | 121.4264 | 61.2579 | -121.6187 | 121.463 | 121.4172 | 61.3037 | -121.7789
1068.8594 | 121.843 | -61.2167 | 60.434 | -0.18799 | 0.020706 | 0.076135 | 0.067915 | 0.12845 | -0.004313 | -0.0056696 | -0.13092 | -0.0094786 | 0.063371 | 0.071673 | 0.00039091 | -0.010666 | 60.3104 | 60.5804 | 0.23346 | -61.2854 | 60.2692 | -61.2534 | -61.2076 | -60.9833 | 0.27924 | -61.4319 | 60.3104 | 60.2646 | -61.1984 | -61.3266 | -0.036621 | 0.009155 | -0.16479 | 121.7972 | -0.068664 | -0.077819 | -0.1236 | 0.018311 | -0.10986 | -0.1236 | 0.23346 | -0.21515 | -0.10529 | -0.16937 | 121.4859 | 121.5271 | 61.4502 | -121.6415 | 121.5271 | 121.4813 | 61.496 | -121.7606
1070.6094 | 121.9299 | -61.2579 | 60.3058 | 0.14008 | 0.017289 | 0.07229 | 0.063643 | 0.13037 | -0.004954 | -0.0033196 | 0.2124 | -0.0088376 | 0.061449 | 0.070391 | 0.0038089 | -0.010239 | 60.2371 | 60.4706 | -0.009155 | -61.3907 | 60.1868 | -61.3129 | -61.2854 | -61.0291 | 0.022888 | -61.5005 | 60.1959 | 60.1456 | -61.2671 | -61.4227 | -0.054931 | -0.027465 | -0.11902 | 121.7285 | -0.13275 | -0.10529 | -0.068664 | -0.009155 | -0.16479 | -0.10986 | 0.22888 | -0.24261 | -0.07782 | -0.16022 | 121.4447 | 121.4951 | 61.2488 | -121.5912 | 121.4539 | 121.4035 | 61.2808 | -121.7285
1072.3594 | 121.9803 | -61.1755 | 60.4248 | -0.14221 | 0.01622 | 0.072504 | 0.067701 | 0.13123 | -0.0051676 | -0.0050286 | -0.024109 | -0.0079832 | 0.062089 | 0.069536 | 0.0010317 | -0.010025 | 60.3378 | 60.5896 | 0.2243 | -61.2808 | 60.2921 | -61.2305 | -61.203 | -60.9329 | 0.27008 | -61.3724 | 60.26 | 60.2325 | -61.1801 | -61.3037 | -0.054932 | -0.027466 | -0.13275 | 121.7651 | -0.10529 | -0.07782 | -0.086975 | -0.004578 | -0.12817 | -0.16479 | 0.24262 | -0.19684 | -0.068664 | -0.19226 | 121.4676 | 121.5134 | 61.3998 | -121.6278 | 121.4355 | 121.4081 | 61.4456 | -121.7285
1074.0469 | 121.9345 | -61.1618 | 60.4294 | -0.18799 | 0.017289 | 0.074854 | 0.06642 | 0.12994 | -0.0051676 | -0.0046014 | -0.11566 | -0.0081968 | 0.063585 | 0.071673 | 0.0014591 | -0.010025 | 60.3424 | 60.6216 | 0.25635 | -61.2717 | 60.2966 | -61.1984 | -61.1664 | -60.9283 | 0.29297 | -61.3953 | 60.3012 | 60.2783 | -61.1618 | -61.322 | -0.036621 | -0.004578 | -0.13275 | 121.7834 | -0.10986 | -0.10529 | -0.086975 | 0 | -0.16022 | -0.12817 | 0.23346 | -0.23346 | -0.073243 | -0.15106 | 121.4584 | 121.5042 | 61.4182 | -121.5958 | 121.463 | 121.4401 | 61.4548 | -121.7514
1075.8125 | 121.9299 | -61.2625 | 60.3104 | 0.11719 | 0.017075 | 0.071222 | 0.063429 | 0.13059 | 0.00060022 | -0.003106 | 0.082703 | -0.0067014 | 0.062089 | 0.075731 | 0.0035953 | -0.010025 | 60.1868 | 60.3607 | -0.11902 | -61.4639 | 60.2509 | -61.3495 | -61.3449 | -61.116 | -0.073242 | -61.6196 | 60.2463 | 60.173 | -61.2946 | -61.4227 | -0.086975 | -0.082398 | -0.05951 | 121.6232 | -0.20142 | -0.11902 | -0.1236 | -0.032044 | -0.16022 | -0.064087 | 0.14648 | -0.35706 | -0.19684 | -0.13733 | 121.5134 | 121.4493 | 61.1435 | -121.6553 | 121.5088 | 121.4355 | 61.1893 | -121.7331
1077.5469 | 121.962 | -61.2671 | 60.2921 | 0.10193 | 0.018357 | 0.074213 | 0.060865 | 0.12888 | 0.0010276 | -0.0033196 | 0.18951 | -0.006915 | 0.062089 | 0.072527 | 0.0035953 | -0.010025 | 60.1868 | 60.3561 | -0.10071 | -61.4731 | 60.2188 | -61.3403 | -61.3449 | -61.0931 | -0.036621 | -61.5921 | 60.2234 | 60.1822 | -61.2762 | -61.4502 | -0.073242 | -0.07782 | -0.073242 | 121.6232 | -0.20599 | -0.12817 | -0.10529 | -0.009155 | -0.1831 | -0.068664 | 0.17395 | -0.32501 | -0.14191 | -0.10986 | 121.4859 | 121.4539 | 61.1664 | -121.637 | 121.4905 | 121.4493 | 61.2305 | -121.7422
1079.2969 | 121.8567 | -61.322 | 60.3424 | 0.056152 | 0.018357 | 0.072076 | 0.065779 | 0.13016 | -0.00046778 | -0.0016108 | 0.044556 | -0.0047788 | 0.063371 | 0.074023 | 0.0061587 | -0.010666 | 60.1639 | 60.3378 | -0.086975 | -61.4685 | 60.2463 | -61.3403 | -61.3129 | -61.1801 | -0.091553 | -61.6837 | 60.2417 | 60.1868 | -61.3174 | -61.4731 | -0.018311 | 0.009155 | -0.09613 | 121.6599 | -0.14648 | -0.15564 | -0.17853 | 0.004577 | -0.15106 | -0.10071 | 0.14191 | -0.36163 | -0.21057 | -0.15564 | 121.5683 | 121.4859 | 61.235 | -121.6553 | 121.5637 | 121.5088 | 61.2305 | -121.8155
1080.9844 | 121.8842 | -61.2717 | 60.3516 | -0.13458 | 0.017716 | 0.072931 | 0.067274 | 0.12909 | -0.00046778 | -0.0026788 | -0.077515 | -0.0064878 | 0.064012 | 0.073382 | 0.0025271 | -0.010025 | 60.2463 | 60.4477 | 0.09613 | -61.3586 | 60.2783 | -61.2808 | -61.29 | -61.0794 | 0.11902 | -61.5463 | 60.2692 | 60.2325 | -61.2579 | -61.4136 | -0.009156 | -0.018311 | -0.073242 | 121.7194 | -0.086976 | -0.068665 | -0.10529 | 0.013732 | -0.14191 | -0.082397 | 0.19226 | -0.27466 | -0.13275 | -0.11902 | 121.55 | 121.5179 | 61.3678 | -121.6415 | 121.5408 | 121.5042 | 61.3907 | -121.7651
1082.7344 | 121.9254 | -61.2625 | 60.3699 | 0.094299 | 0.016434 | 0.074213 | 0.064283 | 0.12695 | -0.0064492 | -0.0033196 | 0.24292 | -0.0081968 | 0.06273 | 0.073595 | 0.0010317 | -0.0078891 | 60.2463 | 60.498 | 0.027466 | -61.3861 | 60.1913 | -61.2854 | -61.2625 | -61.0245 | 0.073242 | -61.496 | 60.2417 | 60.2142 | -61.2076 | -61.4044 | -0.022888 | 0 | -0.17853 | 121.7606 | -0.1236 | -0.1236 | -0.1236 | 0.054931 | -0.14191 | -0.12817 | 0.23804 | -0.23346 | -0.091553 | -0.15564 | 121.4539 | 121.5088 | 61.29 | -121.6324 | 121.5042 | 121.4767 | 61.3358 | -121.7743
1084.4688 | 121.9894 | -61.171 | 60.3973 | -0.088806 | 0.013657 | 0.072931 | 0.068769 | 0.12781 | -0.0062356 | -0.0060968 | -0.0012209 | -0.0092648 | 0.062944 | 0.071673 | -0.0028135 | -0.0085299 | 60.3058 | 60.5392 | 0.17853 | -61.3037 | 60.2829 | -61.2396 | -61.1801 | -60.9467 | 0.25635 | -61.3907 | 60.2783 | 60.2737 | -61.1572 | -61.3312 | -0.068665 | -0.009156 | -0.11444 | 121.7102 | -0.13275 | -0.1236 | -0.091553 | 0.013732 | -0.16022 | -0.11902 | 0.2243 | -0.21973 | -0.059509 | -0.1236 | 121.4539 | 121.4767 | 61.3495 | -121.5775 | 121.4493 | 121.4447 | 61.4273 | -121.7285
1086.2188 | 121.9666 | -61.2671 | 60.3012 | 0.14771 | 0.018143 | 0.071436 | 0.063856 | 0.1308 | -0.0011088 | -0.0028924 | 0.159 | -0.005847 | 0.059312 | 0.073382 | 0.0048769 | -0.0095981 | 60.2646 | 60.4248 | -0.032043 | -61.3953 | 60.2005 | -61.3266 | -61.2946 | -61.0474 | 0.027466 | -61.5326 | 60.2051 | 60.173 | -61.29 | -61.3953 | -0.059509 | -0.027466 | -0.10071 | 121.6919 | -0.12817 | -0.10071 | -0.036621 | -0.022888 | -0.12817 | -0.09613 | 0.21973 | -0.2655 | -0.13733 | -0.12817 | 121.4676 | 121.5317 | 61.235 | -121.5958 | 121.4722 | 121.4401 | 61.2946 | -121.6965
1087.9062 | 121.8292 | -61.322 | 60.347 | -0.073547 | 0.019638 | 0.074426 | 0.063643 | 0.1308 | 0.0016684 | -0.003747 | 0.021668 | -0.007556 | 0.060808 | 0.07445 | 0.0067997 | -0.012162 | 60.2509 | 60.4202 | 0.032043 | -61.4136 | 60.2737 | -61.3174 | -61.3037 | -61.1298 | 0.009155 | -61.6379 | 60.2371 | 60.2051 | -61.2854 | -61.4548 | 0.004577 | 0.01831 | -0.073242 | 121.7422 | -0.091553 | -0.10986 | -0.096131 | 0.036621 | -0.13275 | -0.10986 | 0.19226 | -0.31586 | -0.1831 | -0.14191 | 121.5958 | 121.5729 | 61.3541 | -121.6507 | 121.5591 | 121.5271 | 61.3312 | -121.8018
1089.6562 | 121.9666 | -61.29 | 60.3058 | 0.10193 | 0.018784 | 0.072717 | 0.064924 | 0.1308 | -0.0017496 | -0.0035334 | 0.2124 | -0.0062742 | 0.065507 | 0.072527 | 0.0027407 | -0.0083163 | 60.173 | 60.3653 | -0.10529 | -61.4594 | 60.2417 | -61.3312 | -61.3312 | -61.1069 | -0.045776 | -61.5875 | 60.2325 | 60.1639 | -61.2762 | -61.4456 | -0.041199 | -0.041199 | -0.064087 | 121.6553 | -0.16937 | -0.12817 | -0.13275 | 0.013733 | -0.15564 | -0.073242 | 0.1831 | -0.29755 | -0.14191 | -0.14191 | 121.5317 | 121.463 | 61.1847 | -121.637 | 121.5225 | 121.4539 | 61.2442 | -121.7514
1091.4219 | 121.8704 | -61.2991 | 60.3424 | 0.048523 | 0.017289 | 0.073145 | 0.065779 | 0.12845 | -0.00046778 | -0.003106 | 0.13611 | -0.0054196 | 0.062303 | 0.073168 | 0.0025271 | -0.0087435 | 60.141 | 60.3058 | -0.10529 | -61.4868 | 60.2325 | -61.322 | -61.3541 | -61.1664 | -0.10071 | -61.6562 | 60.2188 | 60.2097 | -61.3266 | -61.4639 | -0.022888 | -0.054932 | -0.10986 | 121.6049 | -0.18768 | -0.13275 | -0.20142 | -0.027466 | -0.1648 | -0.1236 | 0.13275 | -0.35706 | -0.19226 | -0.13275 | 121.5317 | 121.4401 | 61.1938 | -121.6965 | 121.5179 | 121.5088 | 61.1984 | -121.8063
1093.1875 | 121.8567 | -61.3129 | 60.3378 | -0.096436 | 0.017075 | 0.071863 | 0.067488 | 0.12994 | -0.0011088 | -0.0024652 | -0.069885 | -0.005206 | 0.063371 | 0.075091 | 0.0042361 | -0.0089573 | 60.2509 | 60.4385 | 0.073242 | -61.3998 | 60.2554 | -61.3083 | -61.2671 | -61.0565 | 0.10986 | -61.5463 | 60.2554 | 60.2234 | -61.2625 | -61.4182 | 0.004577 | 0.045776 | -0.082398 | 121.7514 | -0.086975 | -0.13275 | -0.086976 | 0.050354 | -0.10529 | -0.082398 | 0.25635 | -0.23346 | -0.12817 | -0.11444 | 121.5683 | 121.5637 | 61.3861 | -121.6049 | 121.5683 | 121.5363 | 61.4227 | -121.756
1094.875 | 121.9666 | -61.1801 | 60.4202 | 0.0027468 | 0.01622 | 0.072931 | 0.069197 | 0.12952 | -0.011149 | -0.0039606 | 0.13611 | -0.0077696 | 0.064226 | 0.07445 | -0.0023861 | -0.0078891 | 60.2188 | 60.4797 | 0.082397 | -61.3495 | 60.26 | -61.235 | -61.2259 | -61.0291 | 0.11902 | -61.4731 | 60.2554 | 60.2417 | -61.2122 | -61.3541 | -0.054931 | -0.045776 | -0.16022 | 121.6599 | -0.16937 | -0.1236 | -0.20142 | -0.032043 | -0.17395 | -0.16479 | 0.15106 | -0.29297 | -0.11902 | -0.17853 | 121.4401 | 121.3989 | 61.2625 | -121.6461 | 121.4355 | 121.4218 | 61.2991 | -121.7743
1096.625 | 121.9345 | -61.235 | 60.379 | 0.033264 | 0.017929 | 0.072717 | 0.06706 | 0.13208 | -0.006022 | -0.0073786 | 0.17426 | -0.0099058 | 0.063158 | 0.0721 | 0.00039091 | -0.0091709 | 60.2417 | 60.4843 | 0.054932 | -61.3678 | 60.2325 | -61.2625 | -61.2625 | -61.0382 | 0.091553 | -61.4822 | 60.2692 | 60.2188 | -61.235 | -61.377 | -0.027466 | -0.027466 | -0.14648 | 121.7194 | -0.13275 | -0.10529 | -0.13733 | 0 | -0.14191 | -0.10986 | 0.19684 | -0.24719 | -0.10529 | -0.16022 | 121.4676 | 121.4767 | 61.29 | -121.6415 | 121.5042 | 121.4539 | 61.3266 | -121.756
1098.3281 | 121.907 | -61.2213 | 60.3836 | 0.071411 | 0.013871 | 0.077203 | 0.065992 | 0.12695 | -0.007731 | -0.0067376 | 0.17426 | -0.0073422 | 0.063158 | 0.071886 | 0.00081811 | -0.0093845 | 60.2554 | 60.4706 | 0.041199 | -61.377 | 60.2234 | -61.2671 | -61.235 | -61.0245 | 0.082397 | -61.496 | 60.2509 | 60.2371 | -61.2167 | -61.3632 | -0.045777 | -0.013733 | -0.16022 | 121.6919 | -0.15564 | -0.14191 | -0.12817 | 0.004577 | -0.14191 | -0.13275 | 0.19684 | -0.27466 | -0.13275 | -0.14648 | 121.4447 | 121.4767 | 61.2625 | -121.6187 | 121.4722 | 121.4584 | 61.3037 | -121.7468
1100.0781 | 121.8567 | -61.322 | 60.3241 | 0.040894 | 0.019852 | 0.073572 | 0.064711 | 0.12952 | 0.00060022 | -0.0052424 | 0.059815 | -0.004138 | 0.063798 | 0.075304 | 0.0059451 | -0.012162 | 60.1868 | 60.3241 | -0.082397 | -61.4548 | 60.26 | -61.3403 | -61.3541 | -61.1755 | -0.09613 | -61.6699 | 60.2417 | 60.2325 | -61.3037 | -61.4273 | -0.018311 | -0.032044 | -0.064087 | 121.6461 | -0.13275 | -0.10071 | -0.13733 | 0.01831 | -0.10529 | -0.082398 | 0.14648 | -0.3479 | -0.24262 | -0.091553 | 121.582 | 121.5088 | 61.2396 | -121.6782 | 121.5637 | 121.5546 | 61.2259 | -121.7514
1101.8281 | 121.9391 | -61.2167 | 60.379 | 0.033264 | 0.015152 | 0.074426 | 0.065138 | 0.12717 | -0.0064492 | -0.0058832 | 0.12085 | -0.0092648 | 0.063798 | 0.070818 | 0.0029543 | -0.0081027 | 60.2417 | 60.4797 | 0.07782 | -61.3678 | 60.2463 | -61.2808 | -61.2213 | -61.0245 | 0.086975 | -61.496 | 60.2646 | 60.2509 | -61.2122 | -61.3541 | -0.064087 | -0.004577 | -0.13275 | 121.6965 | -0.15106 | -0.14648 | -0.13733 | 0.004578 | -0.13733 | -0.11444 | 0.19226 | -0.27924 | -0.14191 | -0.12817 | 121.463 | 121.4584 | 61.2946 | -121.6003 | 121.4813 | 121.4676 | 61.3037 | -121.7331
1103.5781 | 121.9711 | -61.2946 | 60.2829 | 0.15533 | 0.017716 | 0.073572 | 0.061934 | 0.12824 | -0.0011088 | -0.0050286 | 0.11322 | -0.0067014 | 0.060381 | 0.072954 | 0.0048769 | -0.010666 | 60.2325 | 60.4156 | -0.045776 | -61.4182 | 60.2097 | -61.3037 | -61.3266 | -61.0519 | 0.027466 | -61.528 | 60.2188 | 60.1776 | -61.2625 | -61.4044 | -0.009155 | -0.032043 | -0.073242 | 121.7102 | -0.1236 | -0.091553 | -0.050354 | 0.032044 | -0.10986 | -0.064087 | 0.24262 | -0.23346 | -0.1236 | -0.10529 | 121.5042 | 121.5271 | 61.2488 | -121.6095 | 121.5134 | 121.4722 | 61.322 | -121.6873
1105.3281 | 121.962 | -61.203 | 60.4065 | -0.15747 | 0.016007 | 0.075494 | 0.069624 | 0.12909 | -0.0081582 | -0.0067376 | 0.014038 | -0.0090512 | 0.062517 | 0.070391 | -0.00024989 | -0.0098117 | 60.3699 | 60.5942 | 0.2243 | -61.2808 | 60.2783 | -61.2167 | -61.1893 | -60.9055 | 0.29297 | -61.3724 | 60.2966 | 60.2646 | -61.1572 | -61.3312 | -0.013733 | 0.013733 | -0.12817 | 121.7972 | -0.07782 | -0.091553 | -0.036621 | 0.045776 | -0.12817 | -0.10986 | 0.29755 | -0.16937 | -0.041198 | -0.14191 | 121.4813 | 121.5729 | 61.4273 | -121.5958 | 121.4996 | 121.4676 | 61.496 | -121.7377
1107.0156 | 121.9437 | -61.2305 | 60.3516 | 0.025635 | 0.012162 | 0.074426 | 0.063856 | 0.12866 | -0.0051676 | -0.0060968 | 0.11322 | -0.0090512 | 0.062517 | 0.071886 | 0.0012455 | -0.0085299 | 60.2509 | 60.4706 | 0.050354 | -61.3678 | 60.2783 | -61.2717 | -61.235 | -61.0336 | 0.091553 | -61.4914 | 60.2783 | 60.2234 | -61.2259 | -61.3724 | -0.041198 | -0.004577 | -0.073242 | 121.7011 | -0.13733 | -0.13275 | -0.10071 | 0.004578 | -0.14191 | -0.073242 | 0.19684 | -0.26093 | -0.11902 | -0.12817 | 121.5088 | 121.4813 | 61.2808 | -121.5866 | 121.5088 | 121.4539 | 61.322 | -121.7239
1108.7656 | 122.0032 | -61.1664 | 60.4065 | -0.050659 | 0.017289 | 0.074854 | 0.063856 | 0.12866 | -0.0058084 | -0.0060968 | -0.0012209 | -0.0081968 | 0.061876 | 0.069964 | -0.00089089 | -0.0089573 | 60.2921 | 60.5347 | 0.13275 | -61.3129 | 60.2966 | -61.2488 | -61.1984 | -60.9421 | 0.23804 | -61.3907 | 60.3012 | 60.2554 | -61.1801 | -61.3403 | -0.082397 | -0.032043 | -0.10986 | 121.7011 | -0.14648 | -0.11444 | -0.11444 | -0.013733 | -0.17395 | -0.10529 | 0.2243 | -0.2243 | -0.050354 | -0.15106 | 121.463 | 121.4584 | 61.2991 | -121.6049 | 121.4676 | 121.4218 | 61.4044 | -121.7468
1110.5 | 121.9437 | -61.1847 | 60.4019 | -0.13458 | 0.017716 | 0.075281 | 0.066847 | 0.12695 | -0.003245 | -0.0063104 | -0.077515 | -0.0090512 | 0.063585 | 0.071245 | 0.00017731 | -0.010025 | 60.3699 | 60.6354 | 0.26093 | -61.2762 | 60.2875 | -61.203 | -61.2076 | -60.9192 | 0.32501 | -61.3861 | 60.2921 | 60.2783 | -61.1984 | -61.29 | -0.018311 | -0.022889 | -0.11444 | 121.8201 | -0.091553 | -0.068664 | -0.032044 | -0.013733 | -0.10529 | -0.10986 | 0.2655 | -0.20142 | -0.09613 | -0.1236 | 121.4722 | 121.5546 | 61.4456 | -121.6095 | 121.4767 | 121.463 | 61.5097 | -121.6919
1112.1875 | 121.9574 | -61.2762 | 60.2875 | 0.14008 | 0.015793 | 0.072504 | 0.064283 | 0.12909 | 0.0038046 | -0.0041742 | 0.15137 | -0.0047788 | 0.061021 | 0.073809 | 0.0063723 | -0.010453 | 60.228 | 60.3928 | -0.068665 | -61.4273 | 60.2142 | -61.3266 | -61.322 | -61.0382 | -0.009155 | -61.5463 | 60.2188 | 60.1547 | -61.2717 | -61.4227 | -0.050354 | -0.045776 | -0.073243 | 121.669 | -0.15106 | -0.10529 | -0.05951 | 0.004578 | -0.14648 | -0.068665 | 0.23804 | -0.27008 | -0.1236 | -0.13275 | 121.4905 | 121.5042 | 61.2076 | -121.6095 | 121.4951 | 121.431 | 61.2671 | -121.7102
1113.9531 | 121.8979 | -61.2717 | 60.3378 | -0.12695 | 0.019638 | 0.071436 | 0.066206 | 0.1293 | 0.0010276 | -0.0039606 | -0.092773 | -0.0043516 | 0.061021 | 0.074023 | 0.0035953 | -0.01088 | 60.2875 | 60.4523 | 0.10071 | -61.3815 | 60.2692 | -61.3129 | -61.2991 | -61.0565 | 0.11902 | -61.5646 | 60.2737 | 60.2463 | -61.2396 | -61.4136 | -0.041199 | -0.027466 | -0.068665 | 121.7239 | -0.10986 | -0.082398 | -0.050354 | 0.032043 | -0.14191 | -0.064087 | 0.21515 | -0.29297 | -0.15106 | -0.091553 | 121.5408 | 121.5591 | 61.3724 | -121.637 | 121.5454 | 121.5179 | 61.3907 | -121.7514
1115.7031 | 121.8384 | -61.3403 | 60.3333 | 0.025635 | 0.023697 | 0.072504 | 0.070265 | 0.13016 | 0.00060022 | -0.0035334 | 0.029297 | -0.0032834 | 0.064867 | 0.072954 | 0.0016727 | -0.0081027 | 60.1776 | 60.3195 | -0.068665 | -61.4548 | 60.2417 | -61.3449 | -61.3174 | -61.1755 | -0.07782 | -61.6791 | 60.2509 | 60.2234 | -61.2991 | -61.4594 | -0.004578 | 0.022888 | -0.091553 | 121.6599 | -0.11444 | -0.13733 | -0.15564 | 0.041199 | -0.11902 | -0.082398 | 0.16479 | -0.33875 | -0.21973 | -0.10986 | 121.582 | 121.5179 | 61.2717 | -121.6507 | 121.5912 | 121.5637 | 61.2625 | -121.7926
1117.3906 | 121.9528 | -61.1938 | 60.3882 | 0.0027468 | 0.017075 | 0.073145 | 0.070051 | 0.12802 | -0.0073038 | -0.003747 | 0.12085 | -0.0084104 | 0.062303 | 0.071673 | -0.0017453 | -0.0081027 | 60.2325 | 60.4889 | 0.082397 | -61.3541 | 60.2692 | -61.2396 | -61.235 | -61.0291 | 0.11902 | -61.4639 | 60.2554 | 60.2371 | -61.2259 | -61.377 | -0.045776 | -0.041198 | -0.11902 | 121.6827 | -0.16022 | -0.11902 | -0.15564 | -0.032043 | -0.1831 | -0.13275 | 0.1648 | -0.27008 | -0.086975 | -0.15106 | 121.463 | 121.4264 | 61.2762 | -121.6232 | 121.4493 | 121.431 | 61.3129 | -121.7651
1119.1719 | 121.8613 | -61.3129 | 60.3241 | 0.079041 | 0.016648 | 0.07464 | 0.06172 | 0.12888 | -0.00068138 | -0.0018244 | 0.11322 | -0.005847 | 0.061021 | 0.0721 | 0.0070133 | -0.01088 | 60.141 | 60.3333 | -0.11902 | -61.4822 | 60.2417 | -61.3495 | -61.3174 | -61.1572 | -0.086975 | -61.6562 | 60.2509 | 60.1685 | -61.3312 | -61.4731 | -0.036621 | -0.004578 | -0.082398 | 121.6461 | -0.16937 | -0.16479 | -0.18311 | -0.018311 | -0.16022 | -0.073243 | 0.15564 | -0.34332 | -0.18311 | -0.15564 | 121.5546 | 121.4539 | 61.1938 | -121.6415 | 121.5637 | 121.4813 | 61.2259 | -121.7972
1120.8594 | 121.843 | -61.3266 | 60.3378 | 0.056152 | 0.018357 | 0.073358 | 0.065992 | 0.12909 | 0.001882 | -0.0018244 | 0.044556 | -0.0054196 | 0.062944 | 0.074663 | 0.0044497 | -0.010025 | 60.1639 | 60.3149 | -0.07782 | -61.4777 | 60.2463 | -61.3586 | -61.3129 | -61.1801 | -0.086975 | -61.6791 | 60.2646 | 60.2005 | -61.322 | -61.4914 | -0.032044 | 0.013733 | -0.091553 | 121.6415 | -0.15106 | -0.16479 | -0.17395 | 0.004578 | -0.16479 | -0.073243 | 0.14648 | -0.35248 | -0.18768 | -0.13733 | 121.5729 | 121.4905 | 61.2488 | -121.6507 | 121.5912 | 121.5271 | 61.2396 | -121.8292
1122.5938 | 121.8338 | -61.3174 | 60.347 | -0.096436 | 0.020493 | 0.072076 | 0.065779 | 0.12994 | 0.00081382 | -0.005456 | -0.039368 | -0.003497 | 0.063158 | 0.070391 | 0.0059451 | -0.0066073 | 60.2463 | 60.466 | 0.073242 | -61.3953 | 60.2463 | -61.2991 | -61.2946 | -61.0657 | 0.086975 | -61.5509 | 60.2737 | 60.2188 | -61.2762 | -61.4273 | 0.018311 | 0.022888 | -0.10071 | 121.7834 | -0.07782 | -0.10071 | -0.10071 | 0.041199 | -0.10986 | -0.073242 | 0.25177 | -0.23346 | -0.1236 | -0.12817 | 121.5637 | 121.5637 | 61.3907 | -121.6415 | 121.5912 | 121.5363 | 61.4044 | -121.7743
1124.3438 | 121.9208 | -61.1847 | 60.3973 | -0.20325 | 0.016434 | 0.073358 | 0.068129 | 0.1293 | -0.0079446 | -0.0035334 | -0.062256 | -0.010119 | 0.063158 | 0.072527 | -0.0025999 | -0.0063937 | 60.3333 | 60.6308 | 0.27008 | -61.2717 | 60.2875 | -61.2259 | -61.1847 | -60.9421 | 0.33875 | -61.3724 | 60.2829 | 60.26 | -61.1618 | -61.2991 | -0.041199 | 0 | -0.10986 | 121.8155 | -0.086975 | -0.086975 | -0.064087 | 0.022888 | -0.11444 | -0.11444 | 0.24261 | -0.18768 | -0.073242 | -0.13733 | 121.4722 | 121.5179 | 61.4548 | -121.582 | 121.4676 | 121.4447 | 61.5234 | -121.6965
1126.0938 | 121.8613 | -61.3358 | 60.3012 | 0.08667 | 0.017502 | 0.074213 | 0.064283 | 0.12653 | 0.0016684 | -0.0035334 | 0.14374 | -0.0049924 | 0.063158 | 0.072954 | 0.0044497 | -0.0095981 | 60.1547 | 60.3287 | -0.11444 | -61.4731 | 60.2234 | -61.3449 | -61.3541 | -61.1572 | -0.086975 | -61.6425 | 60.2417 | 60.2142 | -61.3174 | -61.4548 | -0.009156 | -0.018311 | -0.077819 | 121.6644 | -0.13733 | -0.11902 | -0.14648 | 0.01831 | -0.11902 | -0.059509 | 0.17853 | -0.3067 | -0.18768 | -0.086975 | 121.5591 | 121.4905 | 61.2213 | -121.6553 | 121.5775 | 121.55 | 61.2488 | -121.756
1127.7812 | 121.8475 | -61.2167 | 60.4294 | -0.17273 | 0.017929 | 0.074854 | 0.068342 | 0.12994 | -0.0064492 | -0.0035334 | -0.13092 | -0.0084104 | 0.060808 | 0.071886 | 0.0016727 | -0.0083163 | 60.3149 | 60.5759 | 0.25177 | -61.2808 | 60.2875 | -61.2122 | -61.2076 | -61.0062 | 0.28381 | -61.4227 | 60.3333 | 60.2966 | -61.1893 | -61.3312 | 0.004578 | 0.009155 | -0.14191 | 121.7926 | -0.064087 | -0.073242 | -0.11444 | 0.027466 | -0.11444 | -0.09613 | 0.21057 | -0.20599 | -0.091552 | -0.13275 | 121.5042 | 121.5317 | 61.4685 | -121.637 | 121.55 | 121.5134 | 61.5005 | -121.7606
1129.5469 | 121.8201 | -61.3449 | 60.3378 | -0.012512 | 0.019852 | 0.069299 | 0.066206 | 0.13037 | 0.001882 | -0.0046014 | 0.082703 | -0.0047788 | 0.066362 | 0.074877 | 0.0046633 | -0.0098117 | 60.2005 | 60.3836 | -0.018311 | -61.4456 | 60.26 | -61.3312 | -61.3174 | -61.1526 | -0.036621 | -61.6333 | 60.26 | 60.2005 | -61.2991 | -61.4639 | 0.013733 | 0.027466 | -0.07782 | 121.7285 | -0.10071 | -0.12817 | -0.13733 | 0.045777 | -0.11902 | -0.07782 | 0.19226 | -0.28839 | -0.16937 | -0.13733 | 121.6049 | 121.5454 | 61.3266 | -121.6553 | 121.6049 | 121.5454 | 61.3083 | -121.8018
1131.2344 | 121.8658 | -61.2625 | 60.4248 | -0.21088 | 0.018784 | 0.074854 | 0.068983 | 0.13037 | -0.0047404 | -0.0035334 | -0.16144 | -0.0081968 | 0.064226 | 0.074877 | 0.0031681 | -0.0076755 | 60.2463 | 60.4706 | 0.14648 | -61.3586 | 60.3378 | -61.2625 | -61.2305 | -61.0474 | 0.19226 | -61.5097 | 60.3745 | 60.3378 | -61.2213 | -61.3403 | 0 | 0.032043 | -0.086975 | 121.7331 | -0.096131 | -0.12817 | -0.17853 | 0.041199 | -0.07782 | -0.050354 | 0.21515 | -0.24719 | -0.16937 | -0.086975 | 121.6003 | 121.5088 | 61.409 | -121.6553 | 121.637 | 121.6003 | 61.4548 | -121.7651
1133 | 121.8887 | -61.2579 | 60.3699 | -0.20325 | 0.016434 | 0.073358 | 0.064924 | 0.12888 | -0.0017496 | -0.0056696 | -0.13092 | -0.0064878 | 0.063158 | 0.071032 | 0.0033817 | -0.0091709 | 60.228 | 60.4431 | 0.10986 | -61.3678 | 60.3195 | -61.2808 | -61.2442 | -61.0931 | 0.17395 | -61.5326 | 60.347 | 60.2783 | -61.2442 | -61.3907 | -0.022888 | 0.013733 | -0.050354 | 121.7011 | -0.10986 | -0.1236 | -0.14191 | 0.013733 | -0.13275 | -0.022888 | 0.1648 | -0.27466 | -0.14191 | -0.091553 | 121.5775 | 121.4859 | 61.3678 | -121.6141 | 121.6049 | 121.5363 | 61.4319 | -121.7606
1134.75 | 121.8842 | -61.2854 | 60.3607 | -0.10406 | 0.020279 | 0.073572 | 0.065565 | 0.12888 | 0.0012412 | -0.0046014 | -0.069885 | -0.005206 | 0.066362 | 0.073595 | 0.0065859 | -0.0081027 | 60.2417 | 60.466 | 0.082397 | -61.3815 | 60.2966 | -61.3312 | -61.2808 | -61.084 | 0.11444 | -61.5417 | 60.26 | 60.2188 | -61.2671 | -61.4136 | -0.045777 | 0.004577 | -0.064087 | 121.7514 | -0.096131 | -0.10071 | -0.11902 | 0.01831 | -0.12817 | -0.10071 | 0.20142 | -0.25635 | -0.12817 | -0.14191 | 121.582 | 121.5271 | 61.3678 | -121.6415 | 121.5454 | 121.5042 | 61.3998 | -121.7743
1136.4531 | 121.8887 | -61.2762 | 60.4294 | -0.23376 | 0.018143 | 0.077631 | 0.068769 | 0.12973 | -0.0045266 | -0.0052424 | -0.16144 | -0.0045652 | 0.062303 | 0.071886 | 0.00017731 | -0.0085299 | 60.2509 | 60.4568 | 0.14191 | -61.3632 | 60.3333 | -61.2671 | -61.2442 | -61.0748 | 0.17395 | -61.5326 | 60.3424 | 60.3333 | -61.2122 | -61.3678 | 0.009155 | 0.032043 | -0.09613 | 121.7331 | -0.086975 | -0.11902 | -0.17853 | 0.064087 | -0.091553 | -0.086975 | 0.20142 | -0.25635 | -0.16479 | -0.09613 | 121.6095 | 121.5271 | 61.4182 | -121.6736 | 121.6187 | 121.6095 | 61.4502 | -121.7972
1138.2031 | 121.9299 | -61.2305 | 60.3241 | 0.12482 | 0.017075 | 0.075067 | 0.061934 | 0.12802 | -0.0058084 | -0.0022516 | 0.24292 | -0.0079832 | 0.061662 | 0.0721 | 0.0025271 | -0.0085299 | 60.2325 | 60.4797 | 0 | -61.3907 | 60.1913 | -61.3266 | -61.29 | -61.0336 | 0.041199 | -61.4914 | 60.1868 | 60.1868 | -61.2717 | -61.3998 | -0.09613 | -0.059509 | -0.13275 | 121.7102 | -0.16022 | -0.10071 | -0.091553 | -0.041198 | -0.16937 | -0.13733 | 0.19684 | -0.26093 | -0.091553 | -0.13733 | 121.4218 | 121.463 | 61.2305 | -121.6141 | 121.4172 | 121.4172 | 61.2717 | -121.7239
1139.8906 | 121.9254 | -61.2122 | 60.3516 | 0.10956 | 0.017716 | 0.073572 | 0.06407 | 0.13037 | -0.0073038 | -0.0026788 | 0.20477 | -0.0077696 | 0.061449 | 0.0721 | 0.0053043 | -0.0089573 | 60.2325 | 60.4889 | 0.022888 | -61.3678 | 60.1959 | -61.2946 | -61.2625 | -61.0199 | 0.086975 | -61.4731 | 60.2234 | 60.1868 | -61.2396 | -61.3998 | -0.082398 | -0.050354 | -0.15564 | 121.7011 | -0.15564 | -0.10529 | -0.11902 | -0.027466 | -0.18768 | -0.12817 | 0.19226 | -0.26093 | -0.073242 | -0.16479 | 121.4081 | 121.4447 | 61.235 | -121.6141 | 121.4355 | 121.3989 | 61.2991 | -121.7514
1141.6406 | 121.9711 | -61.2671 | 60.3012 | 0.14008 | 0.017289 | 0.071436 | 0.065351 | 0.13165 | -0.0023904 | -0.003747 | 0.16663 | -0.0088376 | 0.063371 | 0.071886 | 0.0050907 | -0.01088 | 60.2142 | 60.4248 | -0.032043 | -61.3953 | 60.2097 | -61.3312 | -61.2991 | -61.0565 | 0.022888 | -61.528 | 60.2051 | 60.141 | -61.2762 | -61.4182 | -0.064087 | -0.032043 | -0.091552 | 121.6919 | -0.12817 | -0.096131 | -0.086975 | -0.009155 | -0.15106 | -0.09613 | 0.21057 | -0.26093 | -0.10986 | -0.16022 | 121.4767 | 121.4813 | 61.235 | -121.6003 | 121.4722 | 121.4081 | 61.29 | -121.7194
1143.3906 | 121.9711 | -61.2534 | 60.2829 | 0.12482 | 0.019638 | 0.071436 | 0.070051 | 0.13037 | -0.0019632 | -0.0033196 | 0.20477 | -0.005847 | 0.063371 | 0.075304 | 0.0029543 | -0.010666 | 60.1913 | 60.379 | -0.07782 | -61.441 | 60.2509 | -61.3541 | -61.3037 | -61.0931 | -0.032043 | -61.5601 | 60.2142 | 60.2051 | -61.2808 | -61.4182 | -0.10071 | -0.050354 | -0.032044 | 121.6324 | -0.18768 | -0.13733 | -0.091553 | -0.027466 | -0.16479 | -0.068665 | 0.16022 | -0.3067 | -0.14191 | -0.07782 | 121.5042 | 121.4447 | 61.1755 | -121.5866 | 121.4676 | 121.4584 | 61.2213 | -121.7011
1145.1562 | 121.8933 | -61.3037 | 60.3745 | -0.17273 | 0.01622 | 0.075708 | 0.065138 | 0.12781 | -0.00068138 | -0.0022516 | -0.12329 | -0.007556 | 0.061021 | 0.073809 | 0.0050907 | -0.0081027 | 60.2646 | 60.466 | 0.10071 | -61.3724 | 60.3058 | -61.29 | -61.2762 | -61.0748 | 0.12817 | -61.5417 | 60.2875 | 60.2829 | -61.2396 | -61.4136 | 0.013733 | 0.027466 | -0.068665 | 121.7697 | -0.068664 | -0.09613 | -0.10986 | 0.064087 | -0.10986 | -0.086975 | 0.22888 | -0.23804 | -0.12817 | -0.091553 | 121.6095 | 121.5683 | 61.4044 | -121.6507 | 121.5912 | 121.5866 | 61.4319 | -121.788
1146.8438 | 121.8704 | -61.2076 | 60.4385 | -0.1651 | 0.019211 | 0.075494 | 0.068342 | 0.13229 | -0.006663 | -0.0056696 | -0.039368 | -0.0092648 | 0.064012 | 0.072314 | -0.0013181 | -0.0095981 | 60.3241 | 60.5804 | 0.25177 | -61.2762 | 60.2554 | -61.203 | -61.1618 | -60.9833 | 0.27466 | -61.4136 | 60.3012 | 60.2829 | -61.1893 | -61.3449 | 0.004578 | 0.045777 | -0.18311 | 121.788 | -0.068664 | -0.11444 | -0.11444 | 0.018311 | -0.13733 | -0.13733 | 0.22431 | -0.20599 | -0.068664 | -0.15564 | 121.463 | 121.5317 | 61.4594 | -121.6003 | 121.5088 | 121.4905 | 61.4822 | -121.7834
1148.5938 | 121.8475 | -61.3312 | 60.3241 | 0.040894 | 0.018143 | 0.071863 | 0.066206 | 0.12717 | 0.0016684 | -0.0028924 | 0.059815 | -0.005206 | 0.061876 | 0.074877 | 0.0044497 | -0.010239 | 60.173 | 60.3287 | -0.059509 | -61.4548 | 60.2188 | -61.3449 | -61.322 | -61.1664 | -0.050354 | -61.647 | 60.2646 | 60.2509 | -61.29 | -61.4639 | -0.013733 | 0.009156 | -0.10529 | 121.6599 | -0.1236 | -0.13275 | -0.15106 | 0.041199 | -0.13275 | -0.05951 | 0.16479 | -0.31586 | -0.18311 | -0.073243 | 121.55 | 121.5042 | 61.2717 | -121.6461 | 121.5958 | 121.582 | 61.2808 | -121.788
1150.3281 | 121.8842 | -61.2625 | 60.4019 | -0.22614 | 0.021561 | 0.075494 | 0.068769 | 0.12759 | -0.004954 | -0.0039606 | -0.13855 | -0.007556 | 0.063371 | 0.073382 | -0.00046349 | -0.0095981 | 60.2554 | 60.4385 | 0.13733 | -61.3586 | 60.3424 | -61.2671 | -61.2213 | -61.0703 | 0.15564 | -61.5417 | 60.3195 | 60.2921 | -61.2442 | -61.3815 | -0.004578 | 0.041199 | -0.05951 | 121.7011 | -0.096131 | -0.13733 | -0.14648 | 0.01831 | -0.11902 | -0.082398 | 0.19226 | -0.27924 | -0.16022 | -0.10986 | 121.6049 | 121.5179 | 61.3998 | -121.6232 | 121.582 | 121.5546 | 61.4182 | -121.7834
1152.0781 | 121.8475 | -61.2991 | 60.3378 | -0.088806 | 0.021775 | 0.074213 | 0.063215 | 0.12824 | -4.058e-05 | -0.0050286 | -0.039368 | -0.0043516 | 0.064226 | 0.074663 | 0.0044497 | -0.0093845 | 60.2509 | 60.4523 | 0.068665 | -61.3861 | 60.2829 | -61.3083 | -61.2534 | -61.0748 | 0.086975 | -61.5509 | 60.2783 | 60.2554 | -61.2854 | -61.409 | -0.009156 | 0.045776 | -0.054932 | 121.7514 | -0.086975 | -0.13275 | -0.086976 | 0.013733 | -0.10986 | -0.05951 | 0.2243 | -0.25177 | -0.14191 | -0.082398 | 121.582 | 121.55 | 61.3678 | -121.5912 | 121.5775 | 121.5546 | 61.3861 | -121.7468
1153.7656 | 121.9803 | -61.2671 | 60.2921 | 0.15533 | 0.017716 | 0.073999 | 0.065351 | 0.12802 | -0.0040994 | -0.0026788 | 0.20477 | -0.0079832 | 0.061449 | 0.072741 | 0.0044497 | -0.0091709 | 60.1822 | 60.4111 | -0.045776 | -61.4182 | 60.2188 | -61.3266 | -61.3129 | -61.0748 | 0.004578 | -61.5097 | 60.2051 | 60.1822 | -61.29 | -61.3998 | -0.059509 | -0.045776 | -0.073242 | 121.6782 | -0.15106 | -0.10529 | -0.10986 | -0.022888 | -0.13275 | -0.086975 | 0.19226 | -0.24261 | -0.10986 | -0.10986 | 121.4859 | 121.4493 | 61.2213 | -121.6049 | 121.4722 | 121.4493 | 61.2717 | -121.6919
1155.5156 | 121.9208 | -61.2213 | 60.3607 | 0.14008 | 0.018143 | 0.072931 | 0.065779 | 0.12802 | -0.0040994 | -0.0041742 | 0.23529 | -0.006915 | 0.064653 | 0.070391 | -0.00067729 | -0.0095981 | 60.2554 | 60.4752 | 0.045776 | -61.3632 | 60.228 | -61.3174 | -61.2671 | -61.0245 | 0.064087 | -61.4777 | 60.1776 | 60.2005 | -61.2305 | -61.409 | -0.096131 | -0.045777 | -0.13275 | 121.6965 | -0.14191 | -0.09613 | -0.10529 | -0.009156 | -0.18768 | -0.18311 | 0.19684 | -0.25635 | -0.068664 | -0.16022 | 121.4493 | 121.4767 | 61.2671 | -121.6278 | 121.3989 | 121.4218 | 61.2854 | -121.7697
1157.2656 | 121.8384 | -61.3083 | 60.3745 | -0.073547 | 0.020706 | 0.07229 | 0.06642 | 0.12909 | -0.00046778 | -0.003747 | -0.024109 | -0.004138 | 0.063158 | 0.071459 | 0.0061587 | -0.0093845 | 60.2509 | 60.4431 | 0.064087 | -61.409 | 60.2783 | -61.2946 | -61.29 | -61.0886 | 0.054932 | -61.5921 | 60.2509 | 60.2509 | -61.2762 | -61.441 | 0.013733 | 0.018311 | -0.096131 | 121.7514 | -0.10071 | -0.11902 | -0.1236 | 0.032044 | -0.13275 | -0.1236 | 0.21973 | -0.28381 | -0.15106 | -0.1236 | 121.5866 | 121.5591 | 61.3724 | -121.6644 | 121.5591 | 121.5591 | 61.3632 | -121.8155
1159.0156 | 121.907 | -61.1938 | 60.4385 | -0.18036 | 0.016007 | 0.074426 | 0.070051 | 0.12845 | -0.0079446 | -0.0039606 | -0.054626 | -0.0092648 | 0.062517 | 0.073382 | -0.0017453 | -0.0087435 | 60.347 | 60.6079 | 0.28381 | -61.2717 | 60.2966 | -61.2122 | -61.1618 | -60.9558 | 0.29755 | -61.3998 | 60.2921 | 60.2737 | -61.1847 | -61.3174 | -0.01831 | 0.032044 | -0.14191 | 121.8018 | -0.077819 | -0.10986 | -0.091553 | 0.009156 | -0.1236 | -0.14648 | 0.23804 | -0.20599 | -0.082397 | -0.16479 | 121.4905 | 121.5408 | 61.4777 | -121.6003 | 121.4859 | 121.4676 | 61.4914 | -121.756
1160.7031 | 121.9345 | -61.2122 | 60.3561 | 0.079041 | 0.017289 | 0.075708 | 0.061293 | 0.12888 | -0.0051676 | -0.0067376 | 0.22766 | -0.0062742 | 0.061876 | 0.073168 | 0.0027407 | -0.0081027 | 60.2554 | 60.4889 | 0.054932 | -61.3678 | 60.1959 | -61.2808 | -61.2442 | -61.0245 | 0.073242 | -61.4914 | 60.2371 | 60.2097 | -61.2122 | -61.3678 | -0.068665 | -0.032044 | -0.16022 | 121.7011 | -0.15564 | -0.1236 | -0.10071 | 0 | -0.15564 | -0.11902 | 0.18768 | -0.27924 | -0.1236 | -0.14648 | 121.4081 | 121.4676 | 61.2671 | -121.6003 | 121.4493 | 121.4218 | 61.2854 | -121.7239
1162.4375 | 121.9803 | -61.1847 | 60.4019 | -0.0354 | 0.015366 | 0.073999 | 0.069197 | 0.12781 | -0.006663 | -0.0056696 | 0.044556 | -0.0079832 | 0.062303 | 0.072954 | 0.0012455 | -0.0098117 | 60.2417 | 60.5072 | 0.15106 | -61.3358 | 60.2692 | -61.2442 | -61.2396 | -60.9558 | 0.20142 | -61.4044 | 60.3058 | 60.2829 | -61.1893 | -61.3083 | -0.05951 | -0.054932 | -0.13275 | 121.6919 | -0.15106 | -0.09613 | -0.16022 | -0.004578 | -0.1236 | -0.096131 | 0.22888 | -0.21973 | -0.09613 | -0.11902 | 121.4539 | 121.4264 | 61.3358 | -121.6415 | 121.4905 | 121.4676 | 61.3861 | -121.7102
1164.1875 | 121.8567 | -61.2122 | 60.4431 | -0.15747 | 0.018997 | 0.075708 | 0.067274 | 0.12824 | -0.004313 | -0.0067376 | -0.14618 | -0.0081968 | 0.062089 | 0.073809 | 0.00017731 | -0.011307 | 60.3378 | 60.5804 | 0.2655 | -61.29 | 60.3012 | -61.2167 | -61.2076 | -60.9787 | 0.29297 | -61.4365 | 60.3287 | 60.3195 | -61.1893 | -61.3449 | -0.004578 | 0.004577 | -0.14191 | 121.7926 | -0.07782 | -0.082397 | -0.10529 | 0.022888 | -0.13275 | -0.11444 | 0.23346 | -0.2243 | -0.091552 | -0.1236 | 121.5134 | 121.55 | 61.4777 | -121.6507 | 121.5408 | 121.5317 | 61.5051 | -121.788
1165.875 | 121.9757 | -61.2762 | 60.2921 | 0.10193 | 0.015152 | 0.07229 | 0.062788 | 0.12845 | 0.00081382 | -0.0043878 | 0.16663 | -0.0067014 | 0.060381 | 0.0721 | 0.0035953 | -0.010453 | 60.1822 | 60.3653 | -0.068665 | -61.4365 | 60.228 | -61.3541 | -61.3129 | -61.1023 | -0.050354 | -61.5875 | 60.2463 | 60.2051 | -61.2579 | -61.4227 | -0.07782 | -0.036621 | -0.064087 | 121.6415 | -0.16022 | -0.1236 | -0.10986 | 0.01831 | -0.14648 | -0.045776 | 0.17395 | -0.31128 | -0.1648 | -0.086975 | 121.5042 | 121.4584 | 61.2076 | -121.6049 | 121.5225 | 121.4813 | 61.2259 | -121.7148
1167.625 | 121.9666 | -61.2625 | 60.3287 | 0.071411 | 0.021347 | 0.072931 | 0.06941 | 0.13059 | -0.00068138 | -0.003747 | 0.16663 | -0.0071286 | 0.061876 | 0.074236 | 0.0029543 | -0.010453 | 60.2646 | 60.4614 | 0.036621 | -61.3815 | 60.2005 | -61.2991 | -61.3037 | -61.0336 | 0.032043 | -61.5051 | 60.2188 | 60.1776 | -61.2625 | -61.3998 | -0.036621 | -0.041199 | -0.12817 | 121.7239 | -0.11902 | -0.07782 | -0.064087 | 0 | -0.13733 | -0.10986 | 0.22888 | -0.24262 | -0.10529 | -0.15106 | 121.463 | 121.5271 | 61.2991 | -121.6324 | 121.4813 | 121.4401 | 61.2946 | -121.7285
1169.3906 | 121.8521 | -61.3129 | 60.3745 | 0.040894 | 0.020706 | 0.073572 | 0.061079 | 0.13016 | 0.0016684 | -0.0043878 | 0.097962 | -0.0039244 | 0.061662 | 0.076159 | 0.0050907 | -0.010239 | 60.1776 | 60.3378 | -0.054932 | -61.4685 | 60.2463 | -61.3495 | -61.3129 | -61.1481 | -0.07782 | -61.6653 | 60.2509 | 60.2234 | -61.3129 | -61.4365 | -0.036621 | 0 | -0.12817 | 121.6507 | -0.15564 | -0.15564 | -0.19684 | 0 | -0.1236 | -0.1236 | 0.16479 | -0.35248 | -0.22888 | -0.15106 | 121.5591 | 121.4905 | 61.2579 | -121.6873 | 121.5637 | 121.5363 | 61.235 | -121.8109
1171.1406 | 121.9025 | -61.2442 | 60.4019 | -0.17273 | 0.020493 | 0.074854 | 0.068983 | 0.12824 | -0.0021768 | -0.0022516 | -0.16907 | -0.0067014 | 0.065507 | 0.072741 | 0.0014591 | -0.010666 | 60.2371 | 60.4431 | 0.16479 | -61.3678 | 60.3333 | -61.2671 | -61.2671 | -61.0657 | 0.16022 | -61.5509 | 60.3378 | 60.3104 | -61.2259 | -61.3815 | -0.022888 | -0.022888 | -0.068665 | 121.6873 | -0.1236 | -0.10071 | -0.16479 | 0.018311 | -0.13733 | -0.064087 | 0.17853 | -0.3067 | -0.16937 | -0.091553 | 121.5775 | 121.4813 | 61.409 | -121.669 | 121.582 | 121.5546 | 61.4044 | -121.7834
1172.8281 | 121.8933 | -61.3129 | 60.3149 | 0.10193 | 0.016861 | 0.077631 | 0.064283 | 0.12845 | 0.00081382 | -0.002038 | 0.13611 | -0.0077696 | 0.063158 | 0.074023 | 0.0050907 | -0.0083163 | 60.1364 | 60.3241 | -0.059509 | -61.4685 | 60.2554 | -61.3678 | -61.3358 | -61.1389 | -0.086975 | -61.647 | 60.2463 | 60.2142 | -61.2991 | -61.4594 | -0.054932 | -0.022888 | -0.059509 | 121.637 | -0.15564 | -0.13275 | -0.17853 | 0.013733 | -0.14648 | -0.068664 | 0.17395 | -0.33417 | -0.18768 | -0.10071 | 121.5683 | 121.4493 | 61.2534 | -121.6507 | 121.5591 | 121.5271 | 61.2259 | -121.7743
1174.5781 | 121.9757 | -61.1435 | 60.4019 | -0.096436 | 0.017502 | 0.07464 | 0.07176 | 0.13016 | -0.008372 | -0.005456 | 0.044556 | -0.0084104 | 0.063158 | 0.071032 | -0.0017453 | -0.0063937 | 60.3149 | 60.585 | 0.28381 | -61.29 | 60.3058 | -61.1984 | -61.1938 | -60.9421 | 0.2655 | -61.3678 | 60.3104 | 60.2783 | -61.1893 | -61.322 | -0.054931 | -0.050354 | -0.096131 | 121.7285 | -0.14648 | -0.09613 | -0.086976 | -0.045776 | -0.17853 | -0.091553 | 0.20142 | -0.2243 | -0.045777 | -0.1236 | 121.4493 | 121.4584 | 61.4273 | -121.5958 | 121.4539 | 121.4218 | 61.409 | -121.7239
1176.2812 | 121.9254 | -61.2167 | 60.3653 | 0.018005 | 0.016434 | 0.076135 | 0.068129 | 0.12781 | -0.0075174 | -0.005456 | 0.15137 | -0.0077696 | 0.06273 | 0.073809 | -0.0025999 | -0.0098117 | 60.26 | 60.4752 | 0.13275 | -61.3678 | 60.2463 | -61.2534 | -61.2442 | -61.0245 | 0.11444 | -61.4822 | 60.2692 | 60.2509 | -61.2076 | -61.3449 | -0.036621 | -0.027466 | -0.11902 | 121.6919 | -0.15106 | -0.1236 | -0.10529 | 0.009155 | -0.12817 | -0.09613 | 0.19226 | -0.2655 | -0.13733 | -0.11444 | 121.463 | 121.4767 | 61.3495 | -121.6095 | 121.4859 | 121.4676 | 61.3312 | -121.7102
1178.0312 | 122.0123 | -61.1984 | 60.3928 | 0.0027468 | 0.01622 | 0.074426 | 0.06706 | 0.12952 | -0.0079446 | -0.003747 | 0.097962 | -0.0077696 | 0.062517 | 0.071459 | 0.0010317 | -0.012375 | 60.26 | 60.4797 | 0.20599 | -61.3312 | 60.2921 | -61.2442 | -61.235 | -61.0107 | 0.14191 | -61.4594 | 60.3104 | 60.2554 | -61.2076 | -61.3541 | -0.045777 | -0.036621 | -0.10071 | 121.6782 | -0.13275 | -0.096131 | -0.13275 | -0.009156 | -0.15564 | -0.082397 | 0.18768 | -0.26093 | -0.10529 | -0.13733 | 121.4905 | 121.4584 | 61.4044 | -121.6278 | 121.5088 | 121.4539 | 61.3403 | -121.7468
1179.7344 | 121.8338 | -61.2259 | 60.4431 | -0.25665 | 0.016007 | 0.072504 | 0.06642 | 0.1308 | -0.003245 | -0.0058832 | -0.14618 | -0.0067014 | 0.06273 | 0.072527 | 0.0023135 | -0.0095981 | 60.3149 | 60.5255 | 0.29755 | -61.3083 | 60.3241 | -61.2259 | -61.1893 | -61.0336 | 0.2243 | -61.4868 | 60.3516 | 60.3287 | -61.1938 | -61.3495 | 0 | 0.036621 | -0.11902 | 121.7514 | -0.082398 | -0.11902 | -0.12817 | 0.032043 | -0.1236 | -0.091553 | 0.19226 | -0.26093 | -0.13733 | -0.11444 | 121.55 | 121.5408 | 61.5234 | -121.6324 | 121.5775 | 121.5546 | 61.4502 | -121.7926
1181.4844 | 121.8704 | -61.2122 | 60.4568 | -0.21088 | 0.017289 | 0.074426 | 0.067915 | 0.13165 | -0.0045266 | -0.005456 | -0.062256 | -0.0067014 | 0.061449 | 0.072741 | 0.0012455 | -0.0091709 | 60.3699 | 60.585 | 0.3479 | -61.2808 | 60.3012 | -61.2305 | -61.1618 | -60.9512 | 0.30212 | -61.3998 | 60.3195 | 60.2829 | -61.1755 | -61.3449 | -0.018311 | 0.050354 | -0.15564 | 121.7972 | -0.068665 | -0.11902 | -0.086975 | 0.036621 | -0.13275 | -0.13733 | 0.26093 | -0.18768 | -0.054931 | -0.17395 | 121.5134 | 121.582 | 61.5601 | -121.6187 | 121.5317 | 121.4951 | 61.5143 | -121.8018
1183.1719 | 121.9757 | -61.1847 | 60.4202 | -0.0048827 | 0.015366 | 0.073785 | 0.064497 | 0.12824 | -0.0040994 | -0.0063104 | 0.090332 | -0.0077696 | 0.062089 | 0.071459 | 0.0029543 | -0.0081027 | 60.2646 | 60.498 | 0.15564 | -61.3403 | 60.2829 | -61.235 | -61.2213 | -61.0107 | 0.1236 | -61.4777 | 60.3058 | 60.2463 | -61.2122 | -61.377 | -0.050354 | -0.036621 | -0.13733 | 121.6827 | -0.15564 | -0.11902 | -0.15564 | -0.027466 | -0.19226 | -0.11444 | 0.17395 | -0.29297 | -0.10071 | -0.17395 | 121.4676 | 121.4493 | 61.3403 | -121.6415 | 121.4905 | 121.431 | 61.3083 | -121.7972
1184.9062 | 121.8796 | -61.2717 | 60.3882 | -0.13458 | 0.018997 | 0.073145 | 0.068129 | 0.12824 | 0.0023092 | -0.003747 | -0.10803 | -0.006915 | 0.061876 | 0.074663 | 0.0044497 | -0.013657 | 60.2875 | 60.4568 | 0.15564 | -61.3632 | 60.3195 | -61.2854 | -61.2671 | -61.0428 | 0.1236 | -61.5326 | 60.2921 | 60.2417 | -61.2396 | -61.4136 | -0.013733 | 0.004577 | -0.068665 | 121.7285 | -0.091553 | -0.09613 | -0.10071 | 0.032043 | -0.14191 | -0.096131 | 0.22888 | -0.26093 | -0.11902 | -0.14649 | 121.5912 | 121.5591 | 61.4273 | -121.6553 | 121.5637 | 121.5134 | 61.3953 | -121.8018
1186.6562 | 121.9299 | -61.2122 | 60.3653 | 0.11719 | 0.018357 | 0.072076 | 0.064283 | 0.12717 | -0.0051676 | -0.0043878 | 0.17426 | -0.0077696 | 0.063158 | 0.072741 | 0.0016727 | -0.0095981 | 60.2737 | 60.5209 | 0.10529 | -61.3586 | 60.2097 | -61.2808 | -61.2534 | -61.0107 | 0.07782 | -61.4868 | 60.2005 | 60.2051 | -61.2442 | -61.4182 | -0.068665 | -0.041199 | -0.15564 | 121.7331 | -0.14648 | -0.10529 | -0.091552 | -0.032044 | -0.20599 | -0.1648 | 0.20142 | -0.27466 | -0.068664 | -0.16022 | 121.4218 | 121.4859 | 61.3174 | -121.6187 | 121.4127 | 121.4172 | 61.29 | -121.7834
1188.3438 | 121.8246 | -61.322 | 60.3424 | -0.065918 | 0.01857 | 0.072717 | 0.062574 | 0.12888 | 0.0033774 | -0.003106 | -0.0012209 | -0.0045652 | 0.061021 | 0.074877 | 0.0050907 | -0.011307 | 60.2646 | 60.4385 | 0.07782 | -61.4044 | 60.2921 | -61.3083 | -61.2946 | -61.0977 | 0.004578 | -61.6287 | 60.2783 | 60.2325 | -61.2854 | -61.4227 | 0.013732 | 0.027465 | -0.050354 | 121.7606 | -0.082398 | -0.10986 | -0.07782 | 0.036621 | -0.10071 | -0.064087 | 0.2243 | -0.3067 | -0.20599 | -0.10986 | 121.6141 | 121.5866 | 61.3998 | -121.637 | 121.6003 | 121.5546 | 61.3266 | -121.7651
1190.0938 | 121.8933 | -61.2946 | 60.347 | 0.079041 | 0.017502 | 0.074213 | 0.064283 | 0.12909 | 0.00081382 | -0.0018244 | 0.10559 | -0.0045652 | 0.061662 | 0.07445 | 0.0031681 | -0.0089573 | 60.1639 | 60.3378 | -0.086975 | -61.4594 | 60.2737 | -61.3266 | -61.3174 | -61.1298 | -0.086975 | -61.6287 | 60.2737 | 60.2417 | -61.2991 | -61.4502 | -0.032043 | -0.022888 | -0.073242 | 121.6324 | -0.16479 | -0.14191 | -0.18311 | -0.004577 | -0.15564 | -0.073242 | 0.16479 | -0.33417 | -0.17853 | -0.10529 | 121.5683 | 121.4584 | 61.2076 | -121.6644 | 121.5683 | 121.5363 | 61.2076 | -121.7972
1191.7812 | 121.9757 | -61.1526 | 60.4202 | -0.14221 | 0.018143 | 0.072717 | 0.067488 | 0.13037 | -0.0070902 | -0.002038 | 0.0064086 | -0.0094786 | 0.06508 | 0.072954 | -0.0017453 | -0.0076755 | 60.3516 | 60.64 | 0.22888 | -61.2534 | 60.3149 | -61.2213 | -61.1938 | -60.9055 | 0.32501 | -61.3358 | 60.3241 | 60.2783 | -61.1755 | -61.3174 | -0.068664 | -0.041199 | -0.10529 | 121.7926 | -0.10071 | -0.059509 | -0.068665 | -0.022888 | -0.1648 | -0.09613 | 0.24719 | -0.18311 | -0.01831 | -0.14191 | 121.4676 | 121.5042 | 61.3815 | -121.6141 | 121.4767 | 121.431 | 61.4777 | -121.7377
1193.5312 | 121.843 | -61.2122 | 60.4706 | -0.21851 | 0.016007 | 0.074213 | 0.06642 | 0.12973 | -0.0034586 | -0.0060968 | -0.13092 | -0.006915 | 0.062517 | 0.073382 | 0.0031681 | -0.0091709 | 60.2921 | 60.5209 | 0.1236 | -61.3541 | 60.3745 | -61.2396 | -61.1984 | -61.0291 | 0.20142 | -61.4914 | 60.379 | 60.3378 | -61.1801 | -61.3403 | -0.027466 | 0.013733 | -0.09613 | 121.7331 | -0.14191 | -0.15564 | -0.17853 | 0.032043 | -0.12817 | -0.091553 | 0.18311 | -0.27924 | -0.15106 | -0.13275 | 121.5866 | 121.5042 | 61.3358 | -121.669 | 121.5912 | 121.55 | 61.4136 | -121.8109
1195.2188 | 121.8704 | -61.1938 | 60.4614 | -0.20325 | 0.020066 | 0.073999 | 0.069197 | 0.12994 | -0.0045266 | -0.0033196 | -0.18433 | -0.0054196 | 0.06508 | 0.07445 | 0.00081811 | -0.0087435 | 60.2829 | 60.4568 | 0.082397 | -61.3358 | 60.3653 | -61.2213 | -61.1938 | -61.0336 | 0.1831 | -61.5005 | 60.4019 | 60.3699 | -61.1755 | -61.3174 | -0.027465 | 0 | -0.096131 | 121.6507 | -0.14191 | -0.14191 | -0.17853 | 0.018311 | -0.1236 | -0.059509 | 0.16022 | -0.3067 | -0.1831 | -0.091553 | 121.5591 | 121.4767 | 61.2762 | -121.6553 | 121.5958 | 121.5637 | 61.377 | -121.7789
1196.9688 | 121.9208 | -61.203 | 60.3973 | 0.056152 | 0.014084 | 0.073358 | 0.063215 | 0.12973 | -0.0073038 | -0.0043878 | 0.13611 | -0.0081968 | 0.063371 | 0.071886 | -0.00046349 | -0.010025 | 60.2646 | 60.5118 | 0.009155 | -61.3403 | 60.2829 | -61.235 | -61.2167 | -60.9879 | 0.086975 | -61.4685 | 60.2737 | 60.26 | -61.1984 | -61.3541 | -0.032043 | -0.013733 | -0.11444 | 121.7148 | -0.13733 | -0.1236 | -0.13275 | 0.004578 | -0.15106 | -0.1236 | 0.21515 | -0.2655 | -0.11444 | -0.13733 | 121.4859 | 121.4676 | 61.2122 | -121.6141 | 121.4767 | 121.463 | 61.29 | -121.7514
1198.6562 | 121.8567 | -61.2717 | 60.3561 | 0.025635 | 0.016861 | 0.072931 | 0.063002 | 0.12909 | 0.0012412 | -0.0039606 | 0.075073 | -0.0047788 | 0.062303 | 0.073595 | 0.0076541 | -0.0098117 | 60.1776 | 60.3241 | -0.17395 | -61.4456 | 60.2692 | -61.3174 | -61.3037 | -61.1435 | -0.07782 | -61.6287 | 60.2737 | 60.2325 | -61.2717 | -61.4502 | -0.045777 | -0.032044 | -0.086975 | 121.5958 | -0.17395 | -0.14191 | -0.17853 | 0 | -0.17853 | -0.082397 | 0.12817 | -0.35706 | -0.17853 | -0.1236 | 121.5408 | 121.4493 | 61.0977 | -121.6599 | 121.5454 | 121.5042 | 61.1938 | -121.8063
1200.4062 | 121.8979 | -61.2579 | 60.3607 | -0.14984 | 0.018784 | 0.073785 | 0.068342 | 0.13037 | 0.00038662 | -0.0024652 | -0.11566 | -0.0071286 | 0.063158 | 0.074236 | 0.0035953 | -0.0085299 | 60.2875 | 60.4752 | 0.018311 | -61.3449 | 60.3241 | -61.2488 | -61.2625 | -61.0336 | 0.13733 | -61.5143 | 60.3104 | 60.2921 | -61.2076 | -61.3815 | 0.009156 | -0.004577 | -0.036621 | 121.7331 | -0.086975 | -0.082398 | -0.073242 | 0.050354 | -0.1236 | -0.050354 | 0.22431 | -0.25635 | -0.13275 | -0.068665 | 121.582 | 121.5454 | 61.2762 | -121.6232 | 121.5683 | 121.55 | 61.3953 | -121.7422
1202.1562 | 121.907 | -61.2991 | 60.3378 | 0.10956 | 0.017289 | 0.07229 | 0.063643 | 0.12994 | -4.058e-05 | -0.0035334 | 0.14374 | -0.004138 | 0.062944 | 0.074877 | 0.0038089 | -0.0095981 | 60.1822 | 60.3607 | -0.17853 | -61.441 | 60.2783 | -61.3174 | -61.3129 | -61.116 | -0.086975 | -61.6013 | 60.3104 | 60.2554 | -61.2717 | -61.4319 | -0.018311 | -0.013733 | -0.05951 | 121.6599 | -0.14191 | -0.12817 | -0.15564 | 0.027466 | -0.13275 | -0.027466 | 0.1831 | -0.30212 | -0.16937 | -0.082398 | 121.5775 | 121.4813 | 61.1206 | -121.6507 | 121.6095 | 121.5546 | 61.2122 | -121.7697
1203.9062 | 121.9254 | -61.1755 | 60.4065 | 0.040894 | 0.016007 | 0.075281 | 0.06941 | 0.12888 | -0.0085856 | -0.0067376 | 0.159 | -0.0088376 | 0.064012 | 0.071886 | 0.0020999 | -0.0093845 | 60.2692 | 60.5026 | 0.022888 | -61.3495 | 60.2829 | -61.2305 | -61.2213 | -61.0016 | 0.10986 | -61.441 | 60.2966 | 60.2875 | -61.1664 | -61.3358 | -0.054932 | -0.045776 | -0.1236 | 121.6782 | -0.17395 | -0.12817 | -0.13733 | 0.009155 | -0.16022 | -0.10986 | 0.17395 | -0.2655 | -0.10529 | -0.11902 | 121.4584 | 121.4447 | 61.1984 | -121.6278 | 121.4722 | 121.463 | 61.2854 | -121.7422
1205.6562 | 121.843 | -61.1893 | 60.4614 | -0.17273 | 0.018357 | 0.073358 | 0.071119 | 0.13059 | -0.004954 | -0.0050286 | -0.13092 | -0.0073422 | 0.064012 | 0.072954 | 0.00060451 | -0.010666 | 60.3745 | 60.5896 | 0.21057 | -61.2488 | 60.3561 | -61.1893 | -61.171 | -60.9467 | 0.29755 | -61.3861 | 60.3607 | 60.3561 | -61.1481 | -61.2991 | 0 | 0.018311 | -0.10529 | 121.7789 | -0.059509 | -0.07782 | -0.086975 | 0.041199 | -0.10986 | -0.10071 | 0.24262 | -0.19684 | -0.086975 | -0.10529 | 121.5454 | 121.5637 | 61.3998 | -121.6324 | 121.55 | 121.5454 | 61.4868 | -121.7606
1207.3906 | 121.8475 | -61.29 | 60.3882 | 0.048523 | 0.018357 | 0.072931 | 0.061079 | 0.12845 | 0.0014548 | -0.0026788 | 0.052185 | -0.0060606 | 0.062944 | 0.073168 | 0.0055179 | -0.010453 | 60.2005 | 60.3699 | -0.064087 | -61.4365 | 60.3058 | -61.2946 | -61.29 | -61.1343 | -0.064087 | -61.6333 | 60.3058 | 60.2417 | -61.2762 | -61.4136 | -0.004578 | 0 | -0.082398 | 121.6599 | -0.14648 | -0.14648 | -0.18768 | 0.013733 | -0.1236 | -0.082398 | 0.15564 | -0.34332 | -0.21973 | -0.14649 | 121.5958 | 121.4905 | 61.2259 | -121.6782 | 121.5958 | 121.5317 | 61.2259 | -121.8018
1209.0938 | 121.9849 | -61.1481 | 60.4477 | -0.073547 | 0.018997 | 0.074213 | 0.067915 | 0.12952 | -0.0079446 | -0.0056696 | 0.036926 | -0.0088376 | 0.062089 | 0.072527 | -0.0013181 | -0.0085299 | 60.3333 | 60.585 | 0.25177 | -61.2671 | 60.3195 | -61.2167 | -61.1664 | -60.9192 | 0.27466 | -61.3495 | 60.3195 | 60.2921 | -61.1526 | -61.2762 | -0.068665 | -0.018311 | -0.12817 | 121.7331 | -0.11902 | -0.10071 | -0.11444 | -0.004578 | -0.12817 | -0.12817 | 0.22888 | -0.20142 | -0.073242 | -0.15564 | 121.4676 | 121.4813 | 61.3998 | -121.6141 | 121.4676 | 121.4401 | 61.4227 | -121.7239
1210.8438 | 121.9299 | -61.2762 | 60.3424 | 0.10956 | 0.017502 | 0.073358 | 0.06407 | 0.12909 | -4.058e-05 | -0.0058832 | 0.097962 | -0.0049924 | 0.060808 | 0.071245 | 0.0040225 | -0.0081027 | 60.2005 | 60.379 | 0.027466 | -61.409 | 60.2966 | -61.3403 | -61.2854 | -61.1023 | -0.073242 | -61.5967 | 60.2875 | 60.2692 | -61.2808 | -61.3998 | -0.064087 | -0.009155 | -0.045776 | 121.6553 | -0.13275 | -0.1236 | -0.14191 | -0.004578 | -0.1236 | -0.054931 | 0.17395 | -0.32043 | -0.19684 | -0.073242 | 121.5729 | 121.4767 | 61.3037 | -121.6278 | 121.5637 | 121.5454 | 61.203 | -121.7422
1212.5938 | 121.9986 | -61.1572 | 60.4294 | -0.081177 | 0.016861 | 0.073358 | 0.06642 | 0.1261 | -0.0087992 | -0.0056696 | 0.021668 | -0.0077696 | 0.061021 | 0.073595 | -0.00046349 | -0.0070345 | 60.3561 | 60.6125 | 0.42114 | -61.2534 | 60.3378 | -61.203 | -61.1801 | -60.9146 | 0.27466 | -61.3724 | 60.3378 | 60.3287 | -61.116 | -61.2808 | -0.045776 | -0.022888 | -0.091552 | 121.7697 | -0.09613 | -0.073242 | -0.073242 | 0.041199 | -0.1236 | -0.091552 | 0.24262 | -0.21515 | -0.091552 | -0.10071 | 121.4951 | 121.5134 | 61.5784 | -121.6095 | 121.4951 | 121.4859 | 61.4319 | -121.7102
1214.3438 | 121.9482 | -61.2259 | 60.3653 | 0.063782 | 0.022629 | 0.073145 | 0.067274 | 0.12802 | -0.0030314 | -0.0058832 | 0.22003 | -0.0073422 | 0.06273 | 0.072527 | 0.0038089 | -0.01088 | 60.3195 | 60.4889 | 0.37537 | -61.3403 | 60.2463 | -61.2854 | -61.2579 | -61.0107 | 0.041199 | -61.4731 | 60.2371 | 60.2371 | -61.2579 | -61.3678 | -0.059509 | -0.032044 | -0.11902 | 121.7148 | -0.11444 | -0.082397 | -0.045776 | -0.032044 | -0.14191 | -0.12817 | 0.21515 | -0.24719 | -0.10529 | -0.12817 | 121.4722 | 121.5454 | 61.6013 | -121.6232 | 121.463 | 121.463 | 61.2671 | -121.7331
1216.0312 | 121.9757 | -61.2488 | 60.347 | 0.14008 | 0.015152 | 0.073572 | 0.063215 | 0.12845 | -4.058e-05 | -0.004815 | 0.18951 | -0.0073422 | 0.061021 | 0.074236 | 0.0057315 | -0.0091709 | 60.2509 | 60.4111 | 0.42114 | -61.3815 | 60.2417 | -61.2946 | -61.2808 | -61.0291 | 0.009155 | -61.5143 | 60.2554 | 60.2371 | -61.2579 | -61.377 | -0.045777 | -0.032044 | -0.10529 | 121.6599 | -0.13275 | -0.10071 | -0.096131 | -0.009156 | -0.12817 | -0.091553 | 0.21973 | -0.2655 | -0.13733 | -0.10986 | 121.4905 | 121.4996 | 61.6699 | -121.6278 | 121.5042 | 121.4859 | 61.2579 | -121.7239
1217.7812 | 121.875 | -61.1572 | 60.4935 | -0.18799 | 0.018784 | 0.073572 | 0.070265 | 0.12994 | -0.0053812 | -0.0069512 | -0.054626 | -0.0084104 | 0.061876 | 0.074023 | 0.0010317 | -0.010025 | 60.3699 | 60.6079 | 0.81482 | -61.2488 | 60.3104 | -61.1847 | -61.1572 | -60.9238 | 0.30212 | -61.3815 | 60.3333 | 60.3195 | -61.1526 | -61.3037 | -0.027465 | 0 | -0.1831 | 121.7651 | -0.091552 | -0.091552 | -0.1236 | 0.004578 | -0.14648 | -0.16022 | 0.23346 | -0.2243 | -0.07782 | -0.17395 | 121.4676 | 121.5271 | 61.972 | -121.6507 | 121.4905 | 121.4767 | 61.4594 | -121.7972
1219.4844 | 121.9757 | -61.1343 | 60.4202 | -0.11932 | 0.013016 | 0.077203 | 0.061506 | 0.1293 | -0.006663 | -0.0052424 | -0.0012209 | -0.0088376 | 0.061662 | 0.071032 | 0.0023135 | -0.0085299 | 60.3745 | 60.6445 | 0.83313 | -61.2488 | 60.3378 | -61.1755 | -61.1755 | -60.8871 | 0.31128 | -61.3312 | 60.3241 | 60.3333 | -61.1572 | -61.2717 | -0.041199 | -0.041199 | -0.082397 | 121.7789 | -0.11444 | -0.073242 | -0.045776 | -0.022889 | -0.13733 | -0.09613 | 0.24719 | -0.19684 | -0.05951 | -0.086975 | 121.4722 | 121.5088 | 61.9675 | -121.5958 | 121.4584 | 121.4676 | 61.4456 | -121.6919
1221.2344 | 121.8613 | -61.2122 | 60.4568 | -0.23376 | 0.017929 | 0.073999 | 0.068556 | 0.12866 | -0.00089518 | -0.0052424 | -0.19196 | -0.0062742 | 0.062517 | 0.075731 | 0.0033817 | -0.011948 | 60.3149 | 60.5026 | 0.74158 | -61.3266 | 60.3882 | -61.2167 | -61.1847 | -61.0199 | 0.16479 | -61.5051 | 60.4019 | 60.347 | -61.1938 | -61.3449 | -0.004578 | 0.027466 | -0.068664 | 121.7148 | -0.11444 | -0.14191 | -0.14191 | 0.01831 | -0.13275 | -0.054931 | 0.19226 | -0.29297 | -0.16022 | -0.10986 | 121.6003 | 121.5271 | 61.9537 | -121.6415 | 121.6141 | 121.5591 | 61.377 | -121.8018
1222.9844 | 121.9482 | -61.2625 | 60.3516 | 0.094299 | 0.017502 | 0.073785 | 0.062361 | 0.12674 | -0.00068138 | -0.002038 | 0.10559 | -0.0045652 | 0.062517 | 0.074236 | 0.0061587 | -0.011734 | 60.2417 | 60.3745 | 0.63171 | -61.4136 | 60.2966 | -61.3083 | -61.2946 | -61.084 | -0.059509 | -61.5875 | 60.2921 | 60.2463 | -61.2762 | -61.4136 | -0.045777 | -0.032044 | -0.054931 | 121.637 | -0.15106 | -0.11902 | -0.10986 | -0.013733 | -0.15106 | -0.059509 | 0.17853 | -0.32501 | -0.17395 | -0.10529 | 121.5591 | 121.5042 | 61.8942 | -121.6461 | 121.5546 | 121.5088 | 61.203 | -121.7651
1224.7344 | 121.8475 | -61.1893 | 60.466 | -0.24139 | 0.019638 | 0.07464 | 0.069624 | 0.12952 | -0.0040994 | -0.005456 | -0.16144 | -0.0064878 | 0.064439 | 0.072741 | 0.00081811 | -0.0076755 | 60.2875 | 60.5164 | 0.84686 | -61.3174 | 60.3699 | -61.2122 | -61.1938 | -61.0291 | 0.20599 | -61.4914 | 60.3836 | 60.3378 | -61.1801 | -61.322 | -0.022888 | -0.004578 | -0.09613 | 121.7056 | -0.12817 | -0.1236 | -0.17853 | 0.009155 | -0.13275 | -0.082397 | 0.16022 | -0.30212 | -0.16937 | -0.12817 | 121.5591 | 121.4767 | 62.0361 | -121.6599 | 121.5729 | 121.5271 | 61.3953 | -121.788
1226.5 | 121.8384 | -61.2122 | 60.4523 | -0.23376 | 0.018997 | 0.075922 | 0.067701 | 0.12866 | -0.0053812 | -0.0050286 | -0.32928 | -0.0037106 | 0.063371 | 0.071032 | 0.0029543 | -0.0072483 | 60.3104 | 60.5576 | 0.92468 | -61.2991 | 60.3424 | -61.2122 | -61.203 | -61.0245 | 0.21057 | -61.4868 | 60.3745 | 60.3149 | -61.1984 | -61.322 | 0 | 0.009155 | -0.10986 | 121.7697 | -0.086975 | -0.09613 | -0.14191 | 0.013733 | -0.10986 | -0.07782 | 0.18768 | -0.27466 | -0.16479 | -0.13733 | 121.5546 | 121.5225 | 62.1368 | -121.6553 | 121.5866 | 121.5271 | 61.4227 | -121.7743
1228.1875 | 121.9482 | -61.1481 | 60.4752 | -0.18036 | 0.016434 | 0.077844 | 0.063856 | 0.12589 | -0.0051676 | -0.0050286 | -0.1004 | -0.0079832 | 0.062517 | 0.069964 | 0.0010317 | -0.010666 | 60.3745 | 60.6537 | 1.0391 | -61.2534 | 60.3424 | -61.1572 | -61.1435 | -60.9238 | 0.33875 | -61.3495 | 60.3287 | 60.2829 | -61.1526 | -61.3083 | -0.009156 | 0.004577 | -0.13275 | 121.8018 | -0.10529 | -0.10986 | -0.10071 | -0.004578 | -0.16022 | -0.14648 | 0.2243 | -0.20142 | -0.041198 | -0.19226 | 121.4905 | 121.5225 | 62.1872 | -121.6187 | 121.4767 | 121.431 | 61.4868 | -121.7834
1229.9375 | 121.9345 | -61.2076 | 60.3882 | 0.08667 | 0.014298 | 0.07464 | 0.065565 | 0.12909 | -0.0038858 | -0.0041742 | 0.20477 | -0.0062742 | 0.063585 | 0.073809 | 0.0020999 | -0.011521 | 60.2921 | 60.5301 | 0.92926 | -61.3632 | 60.2463 | -61.2625 | -61.2259 | -60.9924 | 0.073242 | -61.4502 | 60.2692 | 60.2142 | -61.2305 | -61.3678 | -0.054931 | -0.01831 | -0.14191 | 121.7377 | -0.15564 | -0.13733 | -0.096131 | -0.022888 | -0.16022 | -0.11902 | 0.21515 | -0.24261 | -0.082397 | -0.17395 | 121.4539 | 121.4996 | 62.1368 | -121.6141 | 121.4767 | 121.4218 | 61.2808 | -121.756
1231.6719 | 121.9757 | -61.1481 | 60.4614 | -0.081177 | 0.0098118 | 0.073785 | 0.063429 | 0.12866 | -0.0064492 | -0.0067376 | -0.024109 | -0.0094786 | 0.060167 | 0.071032 | 0.0010317 | -0.0098117 | 60.347 | 60.6171 | 1.0895 | -61.2625 | 60.3561 | -61.171 | -61.1572 | -60.9192 | 0.27466 | -61.3586 | 60.3195 | 60.2783 | -61.1526 | -61.3083 | -0.022888 | -0.009156 | -0.10529 | 121.7651 | -0.11444 | -0.10529 | -0.11444 | -0.004578 | -0.16022 | -0.14191 | 0.22888 | -0.21057 | -0.050354 | -0.18311 | 121.5042 | 121.4951 | 62.2375 | -121.6187 | 121.4676 | 121.4264 | 61.4227 | -121.7697
1233.3438 | 121.843 | -61.1893 | 60.4843 | -0.22614 | 0.018997 | 0.073572 | 0.06706 | 0.13016 | -0.00089518 | -0.005456 | -0.18433 | -0.0071286 | 0.061662 | 0.072314 | -3.629e-05 | -0.01088 | 60.3561 | 60.5804 | 1.1902 | -61.2717 | 60.3561 | -61.2213 | -61.1893 | -60.997 | 0.25177 | -61.4548 | 60.3607 | 60.3058 | -61.1801 | -61.2946 | -0.032043 | 0 | -0.12817 | 121.7697 | -0.082397 | -0.082397 | -0.12817 | 0.009155 | -0.10529 | -0.1236 | 0.19226 | -0.2655 | -0.16022 | -0.17853 | 121.5454 | 121.5454 | 62.3795 | -121.6736 | 121.55 | 121.4951 | 61.441 | -121.7789
1235.0938 | 121.8567 | -61.2259 | 60.4614 | -0.22614 | 0.01857 | 0.07464 | 0.069838 | 0.12866 | -0.003245 | -0.0063104 | -0.1004 | -0.006915 | 0.064439 | 0.072314 | 0.0014591 | -0.010239 | 60.3149 | 60.5301 | 1.2268 | -61.3129 | 60.3699 | -61.2213 | -61.235 | -61.0291 | 0.19684 | -61.5005 | 60.379 | 60.3241 | -61.1847 | -61.3403 | 0.004578 | -0.009155 | -0.091553 | 121.756 | -0.086975 | -0.07782 | -0.14649 | 0.041199 | -0.11444 | -0.082398 | 0.19684 | -0.27466 | -0.16022 | -0.13733 | 121.5958 | 121.5408 | 62.4527 | -121.6965 | 121.6049 | 121.55 | 61.4227 | -121.8018
1236.7812 | 121.9025 | -61.2167 | 60.3653 | 0.10193 | 0.014725 | 0.073785 | 0.065138 | 0.12418 | -0.003245 | -0.0035334 | 0.159 | -0.0077696 | 0.064012 | 0.070818 | 0.0040225 | -0.0081027 | 60.2921 | 60.5255 | 1.1948 | -61.3586 | 60.2417 | -61.2579 | -61.203 | -60.997 | 0.068665 | -61.4822 | 60.228 | 60.1959 | -61.2213 | -61.3815 | -0.041199 | 0.013733 | -0.1236 | 121.7422 | -0.14191 | -0.15564 | -0.073242 | -0.004577 | -0.1648 | -0.13733 | 0.21973 | -0.2655 | -0.10071 | -0.16937 | 121.4584 | 121.5088 | 62.4115 | -121.5683 | 121.4447 | 121.4127 | 61.2854 | -121.7468
1238.5469 | 121.8567 | -61.2991 | 60.3333 | -0.11932 | 0.01857 | 0.072931 | 0.065779 | 0.12952 | 0.0016684 | -0.0046014 | -0.092773 | -0.0062742 | 0.062303 | 0.073382 | 0.0055179 | -0.011734 | 60.2829 | 60.4935 | 1.1673 | -61.3541 | 60.2966 | -61.3037 | -61.2671 | -61.0382 | 0.10071 | -61.5601 | 60.3012 | 60.2554 | -61.2305 | -61.3815 | -0.004578 | 0.032043 | -0.036621 | 121.7926 | -0.054932 | -0.086975 | -0.050354 | 0.068664 | -0.082398 | -0.032044 | 0.26093 | -0.26093 | -0.17853 | -0.07782 | 121.5958 | 121.582 | 62.4664 | -121.6003 | 121.6003 | 121.5546 | 61.3998 | -121.7148
1240.2344 | 121.9482 | -61.2396 | 60.3561 | 0.10956 | 0.016648 | 0.075281 | 0.063215 | 0.12845 | -0.0011088 | -0.0052424 | 0.2124 | -0.0067014 | 0.061021 | 0.073168 | 0.0038089 | -0.0085299 | 60.2692 | 60.4889 | 1.2039 | -61.3586 | 60.228 | -61.2991 | -61.2762 | -61.0062 | 0.045776 | -61.4777 | 60.228 | 60.2005 | -61.2625 | -61.4136 | -0.059509 | -0.036621 | -0.12817 | 121.7285 | -0.11902 | -0.082398 | -0.086975 | -0.022888 | -0.17395 | -0.12817 | 0.23346 | -0.23804 | -0.064087 | -0.15564 | 121.4676 | 121.5088 | 62.4435 | -121.6324 | 121.4676 | 121.4401 | 61.2854 | -121.7697
1241.9844 | 121.9711 | -61.1618 | 60.4202 | -0.11169 | 0.015793 | 0.077203 | 0.06941 | 0.12717 | -0.0062356 | -0.003106 | -0.024109 | -0.010547 | 0.064867 | 0.071032 | 0.00017731 | -0.0091709 | 60.3561 | 60.6171 | 1.4465 | -61.2625 | 60.3241 | -61.1938 | -61.1801 | -60.9375 | 0.27466 | -61.3724 | 60.2966 | 60.2509 | -61.1755 | -61.3174 | -0.032044 | -0.018311 | -0.09613 | 121.7789 | -0.10071 | -0.082397 | -0.064087 | -0.013733 | -0.15564 | -0.1236 | 0.2243 | -0.21057 | -0.054931 | -0.16937 | 121.4859 | 121.5179 | 62.6083 | -121.6003 | 121.4584 | 121.4127 | 61.4365 | -121.7377
1243.7344 | 121.8521 | -61.235 | 60.4797 | -0.19562 | 0.017502 | 0.076135 | 0.068129 | 0.13144 | -0.0017496 | -0.0039606 | -0.16144 | -0.0056332 | 0.061021 | 0.071245 | 0.0016727 | -0.0089573 | 60.347 | 60.5942 | 1.5335 | -61.2579 | 60.3241 | -61.1938 | -61.1755 | -60.9833 | 0.27924 | -61.4319 | 60.3607 | 60.3058 | -61.1755 | -61.3129 | 0.041198 | 0.059509 | -0.15564 | 121.8292 | -0.022889 | -0.082398 | -0.13275 | 0.059509 | -0.07782 | -0.11902 | 0.25177 | -0.19684 | -0.11902 | -0.17395 | 121.5591 | 121.582 | 62.7686 | -121.6553 | 121.5958 | 121.5408 | 61.5143 | -121.7926
1245.4219 | 121.8475 | -61.2808 | 60.3516 | -0.088806 | 0.019638 | 0.073785 | 0.061934 | 0.12759 | 0.0031638 | -0.0033196 | -0.1004 | -0.0064878 | 0.062944 | 0.070605 | 0.0061587 | -0.011521 | 60.2783 | 60.498 | 1.442 | -61.3586 | 60.2966 | -61.2991 | -61.2946 | -61.0428 | 0.12817 | -61.528 | 60.3058 | 60.2325 | -61.2625 | -61.4227 | -0.01831 | -0.013733 | -0.054931 | 121.7789 | -0.07782 | -0.064087 | -0.073242 | 0.018311 | -0.14191 | -0.045776 | 0.23804 | -0.24719 | -0.10529 | -0.11902 | 121.5775 | 121.5591 | 62.7228 | -121.6461 | 121.5866 | 121.5134 | 61.409 | -121.7743
1247.1719 | 121.8384 | -61.3083 | 60.3653 | -0.081177 | 0.019425 | 0.075067 | 0.064497 | 0.12909 | 0.0020956 | -0.000329 | -0.039368 | -0.005847 | 0.061235 | 0.074023 | 0.0057315 | -0.010239 | 60.2737 | 60.4752 | 1.4832 | -61.3678 | 60.2966 | -61.29 | -61.2534 | -61.0657 | 0.07782 | -61.5646 | 60.2829 | 60.2646 | -61.2671 | -61.4044 | 0.018311 | 0.054932 | -0.068664 | 121.7834 | -0.059509 | -0.11444 | -0.091552 | 0.041199 | -0.09613 | -0.082397 | 0.24262 | -0.25635 | -0.16022 | -0.10071 | 121.6049 | 121.582 | 62.7914 | -121.6187 | 121.5912 | 121.5729 | 61.3861 | -121.7697
1248.9219 | 121.9345 | -61.235 | 60.3699 | 0.071411 | 0.014511 | 0.075281 | 0.065138 | 0.12653 | -0.007731 | -0.0018244 | 0.20477 | -0.0088376 | 0.059526 | 0.070605 | 0.0018863 | -0.0066073 | 60.2371 | 60.5209 | 1.5839 | -61.3586 | 60.2325 | -61.2625 | -61.2396 | -61.0153 | 0.09613 | -61.4639 | 60.2509 | 60.2509 | -61.2305 | -61.377 | -0.027466 | -0.004578 | -0.13733 | 121.756 | -0.1236 | -0.11902 | -0.13275 | 0.004577 | -0.14191 | -0.11902 | 0.21973 | -0.22888 | -0.086975 | -0.11902 | 121.4676 | 121.4722 | 62.8189 | -121.6095 | 121.4859 | 121.4859 | 61.3312 | -121.7468
1250.6719 | 121.8155 | -61.3129 | 60.3561 | -0.058289 | 0.018784 | 0.074426 | 0.067274 | 0.12909 | 0.0031638 | -0.0039606 | -0.0088499 | -0.005847 | 0.061021 | 0.075518 | 0.0031681 | -0.010239 | 60.26 | 60.4431 | 1.5656 | -61.3815 | 60.2783 | -61.29 | -61.2717 | -61.116 | 0.041199 | -61.5967 | 60.2737 | 60.2325 | -61.2762 | -61.4456 | 0.022888 | 0.041199 | -0.07782 | 121.756 | -0.068665 | -0.10986 | -0.09613 | 0.036621 | -0.13275 | -0.082397 | 0.19684 | -0.28381 | -0.15106 | -0.1236 | 121.5912 | 121.5729 | 62.8784 | -121.6278 | 121.5866 | 121.5454 | 61.3541 | -121.8018
1252.3594 | 121.8887 | -61.2625 | 60.3928 | -0.1651 | 0.022629 | 0.073358 | 0.072187 | 0.12759 | -0.0017496 | -0.0028924 | -0.18433 | -0.0071286 | 0.067216 | 0.074236 | 0.0014591 | -0.0093845 | 60.228 | 60.4477 | 1.6342 | -61.3403 | 60.3424 | -61.2625 | -61.2488 | -61.0657 | 0.16022 | -61.5326 | 60.3287 | 60.2737 | -61.2305 | -61.3678 | 0 | 0.013733 | -0.050354 | 121.7102 | -0.07782 | -0.091553 | -0.16479 | 0.032043 | -0.10529 | -0.064087 | 0.19684 | -0.27008 | -0.16479 | -0.11902 | 121.6049 | 121.4905 | 62.8967 | -121.6415 | 121.5912 | 121.5363 | 61.4227 | -121.7606
1254.1094 | 121.8887 | -61.1893 | 60.4477 | -0.18036 | 0.016434 | 0.075708 | 0.067915 | 0.13059 | -0.0070902 | -0.0035334 | -0.016479 | -0.0079832 | 0.061662 | 0.073809 | 0.0012455 | -0.0076755 | 60.3378 | 60.6445 | 1.8631 | -61.2534 | 60.3058 | -61.2122 | -61.1755 | -60.9604 | 0.32501 | -61.4136 | 60.2875 | 60.2509 | -61.1847 | -61.3403 | -0.022888 | 0.013733 | -0.14191 | 121.8338 | -0.064087 | -0.07782 | -0.10986 | 0.004578 | -0.15106 | -0.16022 | 0.22888 | -0.2243 | -0.073242 | -0.19684 | 121.4951 | 121.5271 | 63.0524 | -121.6232 | 121.4767 | 121.4401 | 61.5143 | -121.788
1255.7969 | 121.8613 | -61.2213 | 60.4385 | -0.22614 | 0.019425 | 0.076563 | 0.068769 | 0.12994 | -0.002604 | -0.0035334 | -0.16144 | -0.007556 | 0.066148 | 0.072741 | 0.0018863 | -0.0095981 | 60.2463 | 60.4843 | 1.7899 | -61.3495 | 60.347 | -61.2625 | -61.203 | -61.0565 | 0.18768 | -61.5143 | 60.3699 | 60.3195 | -61.2488 | -61.3632 | -0.041199 | 0.01831 | -0.091553 | 121.7056 | -0.12817 | -0.14648 | -0.19226 | -0.027466 | -0.14191 | -0.068665 | 0.16479 | -0.29297 | -0.15106 | -0.11902 | 121.5683 | 121.4676 | 63.0112 | -121.6415 | 121.5912 | 121.5408 | 61.409 | -121.8018
1257.5469 | 121.9711 | -61.2579 | 60.2829 | 0.14008 | 0.016648 | 0.072931 | 0.064711 | 0.12845 | -0.00068138 | -0.0033196 | 0.13611 | -0.0084104 | 0.062517 | 0.070177 | 0.0044497 | -0.011307 | 60.2097 | 60.4614 | 1.7761 | -61.3861 | 60.2188 | -61.3358 | -61.2854 | -61.0382 | 0.036621 | -61.496 | 60.2234 | 60.1593 | -61.2671 | -61.4044 | -0.077819 | -0.027465 | -0.064087 | 121.7194 | -0.12817 | -0.10071 | -0.073242 | -0.009155 | -0.14648 | -0.059509 | 0.21973 | -0.23804 | -0.091553 | -0.1236 | 121.4767 | 121.4676 | 63.0341 | -121.5683 | 121.4813 | 121.4172 | 61.2946 | -121.6873
1259.2344 | 121.8796 | -61.2808 | 60.3607 | -0.10406 | 0.019425 | 0.073572 | 0.065779 | 0.13016 | -4.058e-05 | -0.0033196 | -0.062256 | -0.0043516 | 0.064226 | 0.07445 | 0.0023135 | -0.010666 | 60.2692 | 60.4614 | 1.8173 | -61.3586 | 60.2692 | -61.3083 | -61.3037 | -61.0748 | 0.12817 | -61.5555 | 60.2966 | 60.2509 | -61.2579 | -61.3907 | -0.027466 | -0.022888 | -0.091553 | 121.7422 | -0.07782 | -0.054932 | -0.091553 | 0.022888 | -0.10986 | -0.064087 | 0.20599 | -0.27466 | -0.16479 | -0.10986 | 121.55 | 121.55 | 63.0981 | -121.6644 | 121.5775 | 121.5317 | 61.409 | -121.7514
1260.9844 | 121.8933 | -61.2488 | 60.379 | -0.14984 | 0.020706 | 0.073358 | 0.068556 | 0.12802 | -0.0011088 | -0.0033196 | -0.085144 | -0.0049924 | 0.063158 | 0.074877 | 0.0029543 | -0.0091709 | 60.26 | 60.434 | 1.8951 | -61.3632 | 60.3058 | -61.2946 | -61.2854 | -61.0748 | 0.13733 | -61.5417 | 60.2875 | 60.2692 | -61.2488 | -61.3998 | -0.045777 | -0.036621 | -0.073242 | 121.6827 | -0.11444 | -0.07782 | -0.11902 | 0 | -0.15106 | -0.091552 | 0.17395 | -0.29297 | -0.14191 | -0.10986 | 121.5546 | 121.5088 | 63.1439 | -121.6644 | 121.5363 | 121.5179 | 61.3861 | -121.7789
1262.7344 | 121.9437 | -61.2534 | 60.3195 | 0.12482 | 0.017075 | 0.073145 | 0.063643 | 0.1293 | -0.006022 | -0.0009698 | 0.28107 | -0.0073422 | 0.059099 | 0.074023 | 0.00081811 | -0.0076755 | 60.2417 | 60.4568 | 2.2476 | -61.3861 | 60.1822 | -61.3083 | -61.3037 | -61.0611 | 0.059509 | -61.5051 | 60.1959 | 60.173 | -61.2854 | -61.3953 | -0.054932 | -0.050354 | -0.13733 | 121.7102 | -0.13275 | -0.082397 | -0.07782 | -0.032043 | -0.14191 | -0.1236 | 0.19226 | -0.25177 | -0.10986 | -0.14648 | 121.4355 | 121.4951 | 63.501 | -121.6232 | 121.4493 | 121.4264 | 61.3129 | -121.7148
1264.4219 | 121.8613 | -61.2579 | 60.4019 | -0.19562 | 0.015793 | 0.076776 | 0.068342 | 0.12824 | -0.004313 | -0.0058832 | -0.16144 | -0.0067014 | 0.062089 | 0.074236 | 0.0020999 | -0.0085299 | 60.2509 | 60.4523 | 2.3666 | -61.3678 | 60.3287 | -61.2671 | -61.2442 | -61.084 | 0.17853 | -61.5326 | 60.3516 | 60.3149 | -61.2167 | -61.3678 | -0.009155 | 0.013733 | -0.073243 | 121.7102 | -0.10986 | -0.1236 | -0.15106 | 0.041199 | -0.10986 | -0.050355 | 0.17395 | -0.27466 | -0.16479 | -0.086976 | 121.5866 | 121.5088 | 63.6246 | -121.6461 | 121.6095 | 121.5729 | 61.4365 | -121.7697
1266.1875 | 121.9574 | -61.2076 | 60.3882 | -0.11932 | 0.017929 | 0.075494 | 0.06706 | 0.1308 | -0.0081582 | -0.0052424 | 0.014038 | -0.0090512 | 0.063798 | 0.072314 | -0.0015317 | -0.0068209 | 60.347 | 60.5713 | 2.2339 | -61.29 | 60.2829 | -61.2213 | -61.2076 | -60.9421 | 0.29297 | -61.377 | 60.2875 | 60.2921 | -61.1755 | -61.3358 | -0.013732 | 0 | -0.10529 | 121.7789 | -0.082397 | -0.082397 | -0.041199 | 0.032044 | -0.12817 | -0.10071 | 0.2655 | -0.16937 | -0.041199 | -0.096131 | 121.4905 | 121.5546 | 63.4415 | -121.5958 | 121.4951 | 121.4996 | 61.5005 | -121.7239
1267.9375 | 121.9574 | -61.1984 | 60.4019 | -0.073547 | 0.018143 | 0.075494 | 0.068129 | 0.1293 | -0.0068766 | -0.006524 | -0.0088499 | -0.0088376 | 0.062517 | 0.073168 | -3.629e-05 | -0.010453 | 60.3058 | 60.5072 | 2.243 | -61.2946 | 60.2829 | -61.2396 | -61.2213 | -60.9604 | 0.24719 | -61.3953 | 60.2737 | 60.2692 | -61.1893 | -61.3312 | -0.041199 | -0.022888 | -0.11902 | 121.7056 | -0.096131 | -0.073243 | -0.096131 | 0.009155 | -0.13275 | -0.12817 | 0.23804 | -0.19684 | -0.064087 | -0.13275 | 121.4813 | 121.5042 | 63.4415 | -121.6232 | 121.4722 | 121.4676 | 61.4456 | -121.7331
1269.6875 | 121.8567 | -61.2534 | 60.4477 | -0.18036 | 0.018784 | 0.073785 | 0.067701 | 0.1293 | -0.0028178 | -0.0078058 | -0.14618 | -0.0084104 | 0.063158 | 0.071245 | 0.0023135 | -0.0091709 | 60.3149 | 60.5484 | 2.2339 | -61.3037 | 60.3149 | -61.2579 | -61.2259 | -61.0153 | 0.25635 | -61.4685 | 60.3287 | 60.2737 | -61.2488 | -61.3586 | -0.004578 | 0.027466 | -0.13275 | 121.8018 | -0.050354 | -0.07782 | -0.13275 | 0.004578 | -0.10529 | -0.11902 | 0.23804 | -0.21515 | -0.10986 | -0.17395 | 121.5683 | 121.5683 | 63.4872 | -121.6736 | 121.582 | 121.5271 | 61.5097 | -121.8063
1271.375 | 121.9025 | -61.2259 | 60.3516 | 0.048523 | 0.014084 | 0.074213 | 0.063215 | 0.12952 | -0.006663 | -0.0056696 | 0.12848 | -0.0084104 | 0.060381 | 0.071886 | 0.0038089 | -0.010239 | 60.228 | 60.4935 | 2.1835 | -61.3815 | 60.2509 | -61.2946 | -61.2762 | -61.0565 | 0.054932 | -61.5189 | 60.228 | 60.1868 | -61.2671 | -61.4227 | -0.068665 | -0.050354 | -0.10071 | 121.7194 | -0.15564 | -0.10529 | -0.1236 | -0.041199 | -0.19684 | -0.1236 | 0.16937 | -0.29297 | -0.096131 | -0.16479 | 121.4767 | 121.4539 | 63.4094 | -121.6278 | 121.4539 | 121.4127 | 61.2808 | -121.7743
1273.125 | 121.9391 | -61.2488 | 60.3745 | 0.040894 | 0.015152 | 0.075708 | 0.064283 | 0.12866 | -0.0038858 | -0.0073786 | 0.11322 | -0.0060606 | 0.060594 | 0.073382 | 0.0029543 | -0.010025 | 60.2142 | 60.4568 | 2.1927 | -61.3907 | 60.2325 | -61.2854 | -61.29 | -61.0657 | 0.091553 | -61.5189 | 60.2509 | 60.2142 | -61.2579 | -61.3861 | -0.036621 | -0.041199 | -0.14191 | 121.7056 | -0.14191 | -0.10071 | -0.16022 | -0.009156 | -0.13733 | -0.1236 | 0.1831 | -0.27008 | -0.13275 | -0.16022 | 121.4813 | 121.463 | 63.4415 | -121.6644 | 121.4996 | 121.463 | 61.3403 | -121.7606
1274.875 | 121.9116 | -61.2213 | 60.3836 | -0.18036 | 0.017929 | 0.075281 | 0.068983 | 0.13123 | -0.0034586 | -0.004815 | -0.10803 | -0.007556 | 0.062089 | 0.073168 | 0.0014591 | -0.0091709 | 60.347 | 60.5804 | 2.3346 | -61.3083 | 60.2692 | -61.2534 | -61.2167 | -60.9879 | 0.28839 | -61.4456 | 60.2692 | 60.26 | -61.203 | -61.3586 | -0.032044 | 0.004577 | -0.11444 | 121.8018 | -0.086976 | -0.091553 | -0.036621 | 0.01831 | -0.13733 | -0.11444 | 0.23346 | -0.22431 | -0.086975 | -0.1236 | 121.4905 | 121.5683 | 63.5559 | -121.6003 | 121.4905 | 121.4813 | 61.5097 | -121.7422
1276.5625 | 121.962 | -61.2213 | 60.3836 | -0.11932 | 0.017502 | 0.075708 | 0.06941 | 0.12952 | -0.004954 | -0.004815 | -0.1004 | -0.008624 | 0.063798 | 0.073168 | 0.0023135 | -0.011521 | 60.3333 | 60.585 | 2.3254 | -61.3174 | 60.26 | -61.2671 | -61.2167 | -60.9512 | 0.28381 | -61.4182 | 60.2692 | 60.2234 | -61.2122 | -61.3495 | -0.045777 | 0.004577 | -0.1236 | 121.8063 | -0.096131 | -0.10071 | -0.050354 | 0.009155 | -0.12817 | -0.11444 | 0.27008 | -0.19684 | -0.068665 | -0.16022 | 121.4813 | 121.5546 | 63.5468 | -121.6003 | 121.4905 | 121.4447 | 61.5051 | -121.7331
1278.2969 | 121.8979 | -61.29 | 60.3287 | -0.19562 | 0.019638 | 0.072504 | 0.068129 | 0.1308 | 0.0016684 | -0.0039606 | -0.19196 | -0.0064878 | 0.064012 | 0.072527 | 0.0048769 | -0.011307 | 60.2325 | 60.4065 | 2.1652 | -61.3998 | 60.3104 | -61.3266 | -61.3083 | -61.0977 | 0.12817 | -61.5829 | 60.2921 | 60.228 | -61.29 | -61.4273 | -0.036621 | -0.018311 | -0.01831 | 121.6965 | -0.10986 | -0.091552 | -0.09613 | 0 | -0.13733 | -0.036621 | 0.19226 | -0.29297 | -0.15564 | -0.10071 | 121.6003 | 121.5225 | 63.4552 | -121.637 | 121.582 | 121.5179 | 61.4182 | -121.756
1280.0469 | 121.907 | -61.3174 | 60.3241 | -0.18799 | 0.019211 | 0.07229 | 0.064711 | 0.12759 | 0.0031638 | -0.0026788 | -0.13092 | -0.0045652 | 0.061662 | 0.072741 | 0.0038089 | -0.012589 | 60.2188 | 60.4019 | 2.1332 | -61.409 | 60.2921 | -61.377 | -61.3129 | -61.0977 | 0.11444 | -61.5921 | 60.26 | 60.2142 | -61.2991 | -61.4502 | -0.059509 | 0.004578 | -0.032044 | 121.7194 | -0.091553 | -0.096131 | -0.10529 | 0.018311 | -0.13275 | -0.064087 | 0.21973 | -0.27466 | -0.14191 | -0.10986 | 121.6095 | 121.5363 | 63.4506 | -121.637 | 121.5775 | 121.5317 | 61.4319 | -121.7743
1281.7969 | 121.9803 | -61.2305 | 60.3333 | -0.058289 | 0.016434 | 0.075067 | 0.063215 | 0.12802 | -0.007731 | -0.0035334 | 0.052185 | -0.0099058 | 0.06273 | 0.073809 | 0.00039091 | -0.0093845 | 60.2142 | 60.466 | 2.2751 | -61.3678 | 60.2234 | -61.2946 | -61.2808 | -61.0016 | 0.17853 | -61.4685 | 60.2463 | 60.228 | -61.2442 | -61.3724 | -0.064087 | -0.050354 | -0.10986 | 121.6965 | -0.13733 | -0.086975 | -0.11902 | -0.013733 | -0.14191 | -0.086975 | 0.22888 | -0.23804 | -0.096131 | -0.10529 | 121.4539 | 121.4447 | 63.5056 | -121.6141 | 121.4767 | 121.4584 | 61.409 | -121.7056
1283.5625 | 121.8796 | -61.3678 | 60.2783 | 0.08667 | 0.020066 | 0.073358 | 0.064497 | 0.12781 | 0.0027364 | -0.003106 | 0.11322 | -0.005206 | 0.060808 | 0.074877 | 0.0046633 | -0.010666 | 60.1135 | 60.2646 | 2.0737 | -61.5097 | 60.2051 | -61.409 | -61.3998 | -61.1893 | -0.11902 | -61.7111 | 60.1868 | 60.1822 | -61.377 | -61.4914 | -0.041199 | -0.032043 | -0.073242 | 121.6324 | -0.14191 | -0.10986 | -0.16479 | -0.009155 | -0.1236 | -0.091552 | 0.17853 | -0.34332 | -0.21973 | -0.09613 | 121.5729 | 121.4813 | 63.4415 | -121.6782 | 121.5546 | 121.55 | 61.2488 | -121.7697
1285.25 | 121.9803 | -61.2946 | 60.2509 | 0.10193 | 0.018357 | 0.071863 | 0.065992 | 0.13059 | -0.0034586 | -0.003747 | 0.23529 | -0.0079832 | 0.062944 | 0.073595 | 0.0018863 | -0.0091709 | 60.2097 | 60.4019 | 2.2522 | -61.4044 | 60.1364 | -61.3678 | -61.3403 | -61.084 | 0.018311 | -61.5738 | 60.1456 | 60.1364 | -61.3266 | -61.4639 | -0.073242 | -0.045776 | -0.11444 | 121.6965 | -0.10986 | -0.064087 | -0.041198 | -0.032043 | -0.16937 | -0.10528 | 0.21057 | -0.27924 | -0.10986 | -0.11444 | 121.431 | 121.5042 | 63.5468 | -121.5912 | 121.4401 | 121.431 | 61.3129 | -121.7148
1287 | 121.8658 | -61.2946 | 60.3836 | -0.15747 | 0.017716 | 0.075067 | 0.067915 | 0.1293 | -0.0038858 | -0.0039606 | -0.062256 | -0.006915 | 0.061876 | 0.072741 | -0.00046349 | -0.0093845 | 60.3012 | 60.5255 | 2.3346 | -61.3312 | 60.2554 | -61.29 | -61.2717 | -61.0336 | 0.26093 | -61.4822 | 60.2234 | 60.2554 | -61.2579 | -61.409 | 0.004578 | 0.022889 | -0.12817 | 121.8201 | -0.036621 | -0.05951 | -0.082398 | 0.036621 | -0.11444 | -0.16022 | 0.26093 | -0.18768 | -0.073242 | -0.12817 | 121.55 | 121.5958 | 63.6292 | -121.6553 | 121.5179 | 121.55 | 61.5555 | -121.7926
1288.6719 | 121.9254 | -61.29 | 60.3149 | 0.048523 | 0.014084 | 0.075281 | 0.063429 | 0.13037 | -0.006663 | -0.0058832 | 0.12848 | -0.0073422 | 0.063158 | 0.070391 | 0.0012455 | -0.0076755 | 60.2005 | 60.4248 | 2.1744 | -61.3998 | 60.2142 | -61.3174 | -61.3083 | -61.0794 | 0.064087 | -61.5326 | 60.2234 | 60.1913 | -61.2991 | -61.4227 | -0.027466 | -0.018311 | -0.10071 | 121.7148 | -0.10986 | -0.091552 | -0.11444 | -0.009155 | -0.13275 | -0.091552 | 0.21057 | -0.24262 | -0.10986 | -0.1236 | 121.5042 | 121.4905 | 63.4644 | -121.6232 | 121.5134 | 121.4813 | 61.3541 | -121.7377
1290.4219 | 121.875 | -61.29 | 60.3653 | -0.21088 | 0.019211 | 0.077203 | 0.069197 | 0.12909 | -0.00068138 | -0.0067376 | -0.19196 | -0.0071286 | 0.061662 | 0.073809 | 0.0016727 | -0.010025 | 60.228 | 60.3973 | 2.1973 | -61.3953 | 60.2783 | -61.3083 | -61.3129 | -61.1252 | 0.13733 | -61.5967 | 60.3333 | 60.2417 | -61.2762 | -61.441 | -0.018311 | -0.022888 | -0.086975 | 121.6873 | -0.10529 | -0.082398 | -0.13733 | 0.013733 | -0.15106 | -0.032043 | 0.16479 | -0.3067 | -0.15564 | -0.1236 | 121.5683 | 121.5179 | 63.4872 | -121.6782 | 121.6232 | 121.5317 | 61.4273 | -121.8063
1292.1094 | 121.8887 | -61.2579 | 60.3607 | -0.21088 | 0.017289 | 0.076349 | 0.065779 | 0.1308 | -0.006663 | -0.006524 | -0.077515 | -0.0067014 | 0.06273 | 0.072314 | 0.0014591 | -0.0083163 | 60.2875 | 60.5576 | 2.2751 | -61.3312 | 60.2325 | -61.2854 | -61.2854 | -61.0245 | 0.25635 | -61.4639 | 60.2371 | 60.2142 | -61.2717 | -61.3907 | -0.027465 | -0.027465 | -0.12817 | 121.8155 | -0.073242 | -0.045777 | -0.073242 | -0.013732 | -0.13275 | -0.1236 | 0.23346 | -0.20599 | -0.073242 | -0.14648 | 121.4905 | 121.5454 | 63.533 | -121.6461 | 121.4951 | 121.4722 | 61.5143 | -121.7514
1293.8594 | 121.9803 | -61.2717 | 60.3195 | -0.088806 | 0.014511 | 0.077417 | 0.065138 | 0.12845 | -0.004313 | -0.003747 | -0.0012209 | -0.007556 | 0.061876 | 0.070818 | 0.0018863 | -0.0085299 | 60.2646 | 60.498 | 2.2842 | -61.3495 | 60.2371 | -61.2762 | -61.2671 | -60.9924 | 0.20142 | -61.4639 | 60.228 | 60.173 | -61.2259 | -61.4044 | -0.004578 | 0.004577 | -0.082397 | 121.7697 | -0.07782 | -0.082397 | -0.054932 | 0.045776 | -0.13275 | -0.091553 | 0.27923 | -0.19226 | -0.059509 | -0.14648 | 121.5088 | 121.5363 | 63.5559 | -121.5866 | 121.4996 | 121.4447 | 61.4731 | -121.7239
1295.6094 | 121.9894 | -61.2213 | 60.3561 | -0.11169 | 0.016861 | 0.075494 | 0.065779 | 0.12866 | -0.004954 | -0.004815 | -0.054626 | -0.0064878 | 0.061662 | 0.072741 | 0.0016727 | -0.010025 | 60.2783 | 60.5209 | 2.2842 | -61.3312 | 60.2554 | -61.2854 | -61.2579 | -61.0016 | 0.21973 | -61.4502 | 60.2234 | 60.2051 | -61.2579 | -61.3953 | -0.064087 | -0.036622 | -0.10071 | 121.7422 | -0.10986 | -0.073242 | -0.07782 | -0.036622 | -0.17395 | -0.13275 | 0.21973 | -0.22888 | -0.054931 | -0.15106 | 121.4767 | 121.4996 | 63.5056 | -121.6141 | 121.4447 | 121.4264 | 61.441 | -121.7514
1297.2812 | 121.8658 | -61.409 | 60.2463 | -0.073547 | 0.019211 | 0.071649 | 0.065138 | 0.1308 | 0.003591 | -0.0043878 | 0.029297 | -0.0043516 | 0.062944 | 0.07445 | 0.0067997 | -0.0085299 | 60.1227 | 60.2737 | 2.0508 | -61.5189 | 60.1868 | -61.4136 | -61.3998 | -61.2213 | -0.086975 | -61.7203 | 60.1959 | 60.1318 | -61.3724 | -61.5326 | -0.004577 | 0.009156 | -0.059509 | 121.6827 | -0.10986 | -0.11902 | -0.1236 | 0.036622 | -0.1236 | -0.050354 | 0.18768 | -0.31128 | -0.18768 | -0.11444 | 121.5958 | 121.5317 | 63.4598 | -121.6461 | 121.6049 | 121.5408 | 61.322 | -121.7789
1299.0469 | 121.9574 | -61.3449 | 60.2051 | 0.11719 | 0.021134 | 0.074213 | 0.064711 | 0.12952 | 0.00017302 | -0.0033196 | 0.18951 | -0.003497 | 0.061662 | 0.073382 | 0.0053043 | -0.0076755 | 60.1135 | 60.3058 | 2.0416 | -61.5005 | 60.1501 | -61.4319 | -61.3861 | -61.1389 | -0.068665 | -61.6333 | 60.1456 | 60.1227 | -61.3403 | -61.5097 | -0.086975 | -0.041198 | -0.054932 | 121.6507 | -0.15564 | -0.11444 | -0.091553 | 0.004578 | -0.16479 | -0.059509 | 0.20599 | -0.28839 | -0.1236 | -0.082397 | 121.4951 | 121.4584 | 63.3865 | -121.5912 | 121.4905 | 121.4676 | 61.2762 | -121.7148
1300.8125 | 121.8292 | -61.3953 | 60.2966 | -0.065918 | 0.017716 | 0.076776 | 0.065351 | 0.12994 | 0.0012412 | -0.002038 | -0.039368 | -0.0056332 | 0.060381 | 0.074663 | 0.0050907 | -0.0093845 | 60.1959 | 60.3561 | 2.0691 | -61.4594 | 60.1776 | -61.3861 | -61.3815 | -61.1526 | 0 | -61.6745 | 60.1913 | 60.1593 | -61.3541 | -61.5189 | 0.009156 | 0.013733 | -0.11902 | 121.7514 | -0.064087 | -0.07782 | -0.10071 | 0.041199 | -0.1236 | -0.10529 | 0.24262 | -0.27924 | -0.15564 | -0.13733 | 121.5729 | 121.5912 | 63.4644 | -121.6782 | 121.5866 | 121.5546 | 61.3953 | -121.8155
1302.5625 | 121.875 | -61.3541 | 60.2783 | -0.11932 | 0.021775 | 0.074426 | 0.066847 | 0.12802 | -0.00068138 | -0.003747 | -0.085144 | -0.006915 | 0.064012 | 0.073809 | 0.0050907 | -0.0098117 | 60.1776 | 60.3653 | 2.0233 | -61.4456 | 60.1822 | -61.3953 | -61.3586 | -61.1252 | 0.064087 | -61.6241 | 60.173 | 60.1501 | -61.3586 | -61.4822 | -0.041199 | -0.004578 | -0.09613 | 121.7194 | -0.091553 | -0.086975 | -0.10071 | -0.004578 | -0.12817 | -0.10529 | 0.22888 | -0.27008 | -0.14191 | -0.12817 | 121.5363 | 121.5317 | 63.3774 | -121.637 | 121.5271 | 121.5042 | 61.4182 | -121.7606
1304.25 | 121.9666 | -61.2625 | 60.3241 | -0.14221 | 0.017716 | 0.074213 | 0.070478 | 0.12994 | -0.0096536 | -0.0052424 | 0.0064086 | -0.0099058 | 0.062944 | 0.073382 | -0.0013181 | -0.0093845 | 60.2509 | 60.5347 | 2.179 | -61.3495 | 60.2097 | -61.2946 | -61.2808 | -61.0199 | 0.21515 | -61.4456 | 60.2005 | 60.173 | -61.2717 | -61.3907 | -0.032044 | -0.018311 | -0.11444 | 121.7972 | -0.086975 | -0.068664 | -0.073243 | -0.009155 | -0.12817 | -0.1236 | 0.24262 | -0.18311 | -0.054932 | -0.15106 | 121.4722 | 121.5134 | 63.4415 | -121.6049 | 121.463 | 121.4355 | 61.4777 | -121.7148
1306 | 121.9254 | -61.3632 | 60.2325 | 0.10956 | 0.017502 | 0.072504 | 0.063856 | 0.12824 | -0.00046778 | -0.0026788 | 0.097962 | -0.005206 | 0.063371 | 0.075518 | 0.0038089 | -0.0083163 | 60.0586 | 60.2554 | 1.8677 | -61.5234 | 60.1593 | -61.441 | -61.4319 | -61.235 | -0.14191 | -61.7157 | 60.173 | 60.1227 | -61.3998 | -61.5417 | -0.07782 | -0.068665 | -0.073242 | 121.6187 | -0.16022 | -0.091552 | -0.17395 | -0.036621 | -0.17853 | -0.059509 | 0.12817 | -0.35248 | -0.17395 | -0.10986 | 121.5225 | 121.4218 | 63.2309 | -121.6644 | 121.5363 | 121.4859 | 61.2213 | -121.7743
1307.75 | 121.9803 | -61.2717 | 60.3104 | 0.0027468 | 0.017929 | 0.075922 | 0.06706 | 0.12653 | -0.0058084 | -0.0050286 | 0.10559 | -0.0064878 | 0.063585 | 0.070391 | 0.00017731 | -0.0076755 | 60.1456 | 60.3928 | 2.0416 | -61.409 | 60.1913 | -61.3403 | -61.3312 | -61.0977 | 0.068665 | -61.5463 | 60.1822 | 60.1639 | -61.322 | -61.4319 | -0.068665 | -0.05951 | -0.11902 | 121.6644 | -0.13733 | -0.07782 | -0.16479 | -0.050354 | -0.16022 | -0.12817 | 0.17395 | -0.27466 | -0.11444 | -0.14648 | 121.463 | 121.4172 | 63.3133 | -121.6415 | 121.4539 | 121.4355 | 61.3403 | -121.7422
1309.5 | 121.9482 | -61.3861 | 60.2097 | 0.10956 | 0.017929 | 0.073572 | 0.063429 | 0.12866 | -4.058e-05 | -0.0056696 | 0.10559 | -0.003497 | 0.060594 | 0.074663 | 0.0053043 | -0.0093845 | 60.0861 | 60.2463 | 1.8631 | -61.5097 | 60.173 | -61.4273 | -61.4273 | -61.2213 | -0.13275 | -61.7249 | 60.1685 | 60.1273 | -61.3998 | -61.5555 | -0.041199 | -0.041199 | -0.036621 | 121.6324 | -0.1236 | -0.082398 | -0.1236 | -0.013733 | -0.16937 | -0.041199 | 0.16479 | -0.33875 | -0.16937 | -0.082398 | 121.5591 | 121.4722 | 63.2492 | -121.637 | 121.5546 | 121.5134 | 61.2534 | -121.7651
1311.1875 | 121.9711 | -61.3678 | 60.2509 | 0.14008 | 0.016861 | 0.077417 | 0.063643 | 0.1308 | -0.0030314 | -0.003106 | 0.2887 | -0.0064878 | 0.062303 | 0.072314 | 0.0053043 | -0.0091709 | 60.1456 | 60.3333 | 1.8814 | -61.4639 | 60.1318 | -61.4319 | -61.3998 | -61.1526 | -0.022888 | -61.6241 | 60.1135 | 60.0906 | -61.3678 | -61.4914 | -0.064087 | -0.032043 | -0.11902 | 121.7011 | -0.09613 | -0.064087 | -0.10528 | 0 | -0.1236 | -0.13733 | 0.21515 | -0.25635 | -0.13275 | -0.16022 | 121.4996 | 121.5134 | 63.2492 | -121.6507 | 121.4813 | 121.4584 | 61.3449 | -121.7422
1312.9375 | 121.9254 | -61.2808 | 60.3378 | -0.15747 | 0.017289 | 0.076563 | 0.069624 | 0.13144 | -0.0064492 | -0.005456 | -0.077515 | -0.007556 | 0.062303 | 0.072527 | -0.0019589 | -0.011094 | 60.2737 | 60.5164 | 2.0645 | -61.3266 | 60.1959 | -61.3083 | -61.2808 | -61.0382 | 0.25635 | -61.4868 | 60.2463 | 60.2325 | -61.2534 | -61.3953 | -0.027466 | 0 | -0.14191 | 121.7972 | -0.045776 | -0.045776 | -0.064087 | 0.027466 | -0.11444 | -0.091553 | 0.24262 | -0.20599 | -0.091552 | -0.10529 | 121.4767 | 121.5546 | 63.3453 | -121.6187 | 121.5271 | 121.5134 | 61.5372 | -121.7331
1314.625 | 121.907 | -61.3358 | 60.2829 | 0.08667 | 0.017289 | 0.075281 | 0.064497 | 0.13251 | -0.006663 | -0.0058832 | 0.14374 | -0.0090512 | 0.062944 | 0.074023 | 0.0010317 | -0.0085299 | 60.1822 | 60.4065 | 2.0462 | -61.4319 | 60.1456 | -61.3541 | -61.3495 | -61.1023 | 0.032043 | -61.5829 | 60.1639 | 60.1364 | -61.2946 | -61.4639 | -0.018311 | -0.013733 | -0.13733 | 121.7422 | -0.096131 | -0.082398 | -0.10071 | 0.041198 | -0.12817 | -0.11902 | 0.23346 | -0.24719 | -0.11902 | -0.14648 | 121.4813 | 121.5179 | 63.382 | -121.6324 | 121.4996 | 121.4722 | 61.3678 | -121.7468
1316.375 | 121.962 | -61.2854 | 60.3058 | -0.012512 | 0.014511 | 0.075067 | 0.064497 | 0.13037 | -0.0058084 | -0.0058832 | 0.090332 | -0.0088376 | 0.060167 | 0.073809 | 0.0040225 | -0.0087435 | 60.1593 | 60.3928 | 2.0508 | -61.3907 | 60.1776 | -61.3449 | -61.3174 | -61.1023 | 0.059509 | -61.5555 | 60.1776 | 60.1501 | -61.3266 | -61.4548 | -0.05951 | -0.032044 | -0.12817 | 121.6782 | -0.10529 | -0.073242 | -0.14648 | -0.041199 | -0.16937 | -0.12817 | 0.18311 | -0.27008 | -0.10071 | -0.15564 | 121.463 | 121.4447 | 63.3362 | -121.6232 | 121.463 | 121.4355 | 61.3449 | -121.7606
1318.125 | 121.9666 | -61.3495 | 60.228 | 0.10193 | 0.017716 | 0.072931 | 0.06642 | 0.12973 | -0.001536 | -0.0058832 | 0.19714 | -0.0056332 | 0.061235 | 0.072954 | 0.0033817 | -0.010453 | 60.173 | 60.379 | 2.0966 | -61.4456 | 60.1364 | -61.4182 | -61.3815 | -61.1114 | -0.018311 | -61.6058 | 60.1318 | 60.0861 | -61.3953 | -61.5097 | -0.068665 | -0.032044 | -0.091552 | 121.7285 | -0.096131 | -0.064087 | -0.054931 | -0.045777 | -0.16022 | -0.09613 | 0.23804 | -0.25635 | -0.09613 | -0.14191 | 121.4859 | 121.5225 | 63.446 | -121.6095 | 121.4813 | 121.4355 | 61.3312 | -121.7377
1319.8594 | 121.9803 | -61.2854 | 60.3012 | -0.1651 | 0.018143 | 0.074426 | 0.070051 | 0.13187 | -0.0075174 | -0.0067376 | -0.016479 | -0.007556 | 0.063158 | 0.072954 | 0.00060451 | -0.0091709 | 60.2554 | 60.5072 | 2.1652 | -61.3403 | 60.228 | -61.322 | -61.3083 | -60.997 | 0.20599 | -61.4914 | 60.1776 | 60.1593 | -61.2854 | -61.4136 | -0.036621 | -0.022889 | -0.073242 | 121.7926 | -0.054932 | -0.032043 | -0.045776 | 0 | -0.12817 | -0.1236 | 0.28839 | -0.20599 | -0.07782 | -0.14191 | 121.5134 | 121.5408 | 63.4506 | -121.6095 | 121.463 | 121.4447 | 61.4914 | -121.7148
1321.5469 | 121.8658 | -61.3083 | 60.3607 | -0.1651 | 0.019425 | 0.07464 | 0.069838 | 0.12909 | -0.0021768 | -0.0056696 | -0.16907 | -0.007556 | 0.064867 | 0.072527 | 0.0014591 | -0.011094 | 60.2463 | 60.4889 | 2.211 | -61.3403 | 60.2234 | -61.322 | -61.2854 | -61.0428 | 0.20599 | -61.5234 | 60.2325 | 60.1868 | -61.2762 | -61.4319 | -0.013732 | 0.022889 | -0.13733 | 121.7972 | -0.032043 | -0.054932 | -0.11444 | 0.032044 | -0.1236 | -0.12817 | 0.2655 | -0.21515 | -0.091552 | -0.17395 | 121.5317 | 121.5546 | 63.5193 | -121.6461 | 121.5408 | 121.4951 | 61.5143 | -121.7926
1323.2969 | 122.0078 | -61.2762 | 60.3058 | -0.058289 | 0.01622 | 0.075281 | 0.065351 | 0.13016 | -0.0045266 | -0.0046014 | 0.0064086 | -0.0092648 | 0.059953 | 0.071886 | 0.0040225 | -0.0091709 | 60.2005 | 60.4568 | 2.243 | -61.3495 | 60.2234 | -61.322 | -61.3037 | -61.0153 | 0.16022 | -61.496 | 60.2005 | 60.1822 | -61.2671 | -61.4136 | -0.045776 | -0.027466 | -0.082397 | 121.7331 | -0.073242 | -0.045776 | -0.10529 | 0.009155 | -0.13733 | -0.10529 | 0.26093 | -0.21973 | -0.082398 | -0.1236 | 121.4996 | 121.4767 | 63.5193 | -121.6095 | 121.4767 | 121.4584 | 61.4365 | -121.7194
1325.0312 | 121.8933 | -61.3586 | 60.2646 | -0.18036 | 0.022202 | 0.072717 | 0.065779 | 0.13187 | 0.0023092 | -0.0041742 | -0.15381 | -0.0073422 | 0.06273 | 0.072314 | 0.0059451 | -0.013016 | 60.1868 | 60.3607 | 2.1423 | -61.3953 | 60.2509 | -61.3541 | -61.3632 | -61.116 | 0.059509 | -61.6333 | 60.2188 | 60.1913 | -61.3266 | -61.4777 | 0.004578 | -0.004577 | -0.013733 | 121.7194 | -0.036621 | -0.032044 | -0.077819 | 0.032044 | -0.11902 | -0.045776 | 0.24262 | -0.27466 | -0.15564 | -0.073242 | 121.6095 | 121.5454 | 63.501 | -121.6278 | 121.5775 | 121.55 | 61.4182 | -121.7422
1326.7812 | 121.9528 | -61.2946 | 60.3149 | -0.11169 | 0.016861 | 0.074854 | 0.067274 | 0.12824 | -0.0064492 | -0.0041742 | -0.069885 | -0.0081968 | 0.060594 | 0.072741 | -0.0019589 | -0.0093845 | 60.2875 | 60.5484 | 2.2888 | -61.2991 | 60.2051 | -61.2991 | -61.3037 | -60.9833 | 0.21057 | -61.4822 | 60.1959 | 60.1822 | -61.2442 | -61.3953 | -0.004577 | -0.009155 | -0.10986 | 121.843 | -0.004577 | 0.004578 | -0.027465 | 0.050354 | -0.10071 | -0.11902 | 0.31128 | -0.18768 | -0.086975 | -0.13275 | 121.4996 | 121.582 | 63.5834 | -121.6187 | 121.4905 | 121.4767 | 61.5051 | -121.7102
1328.5469 | 121.8842 | -61.3861 | 60.2921 | -0.11169 | 0.021134 | 0.073358 | 0.062361 | 0.12674 | 0.0010276 | -0.002038 | -0.092773 | -0.003497 | 0.062517 | 0.075091 | 0.0078677 | -0.011521 | 60.1913 | 60.3882 | 2.2842 | -61.3998 | 60.1868 | -61.3998 | -61.3724 | -61.1069 | 0.045776 | -61.6333 | 60.2097 | 60.1776 | -61.3449 | -61.4914 | -0.013733 | 0.013733 | -0.10529 | 121.7743 | -0.013733 | -0.027466 | -0.10071 | 0.041198 | -0.10529 | -0.082397 | 0.27923 | -0.24719 | -0.14191 | -0.11444 | 121.5729 | 121.5775 | 63.6703 | -121.6644 | 121.5958 | 121.5637 | 61.4319 | -121.7834
1330.2344 | 121.9391 | -61.29 | 60.2783 | 0.094299 | 0.017502 | 0.075922 | 0.065138 | 0.12994 | -0.0045266 | -0.004815 | 0.22003 | -0.0094786 | 0.061235 | 0.071459 | 0.0033817 | -0.0081027 | 60.1776 | 60.4385 | 2.4536 | -61.3998 | 60.1364 | -61.3724 | -61.3541 | -61.0611 | -0.004578 | -61.5601 | 60.1593 | 60.1181 | -61.3358 | -61.4685 | -0.082397 | -0.064087 | -0.14191 | 121.7285 | -0.10986 | -0.045776 | -0.10071 | -0.045776 | -0.17853 | -0.11902 | 0.22888 | -0.27008 | -0.091553 | -0.16022 | 121.4264 | 121.4676 | 63.7436 | -121.6324 | 121.4493 | 121.4081 | 61.2854 | -121.7468
1331.9844 | 121.8338 | -61.3815 | 60.26 | -0.065918 | 0.017502 | 0.074213 | 0.065565 | 0.12759 | 0.001882 | -0.0022516 | -0.0012209 | -0.0060606 | 0.061449 | 0.073809 | 0.0076541 | -0.010666 | 60.1685 | 60.347 | 2.4719 | -61.4365 | 60.1868 | -61.3998 | -61.3953 | -61.1847 | -0.050354 | -61.7065 | 60.1913 | 60.1181 | -61.3861 | -61.5555 | -0.01831 | -0.013733 | -0.073242 | 121.7285 | -0.054931 | -0.041198 | -0.091553 | -0.004577 | -0.17395 | -0.068665 | 0.19684 | -0.32501 | -0.15106 | -0.14191 | 121.5683 | 121.55 | 63.8535 | -121.6553 | 121.5729 | 121.4996 | 61.3312 | -121.8155
1333.6719 | 121.875 | -61.3174 | 60.347 | -0.18036 | 0.019425 | 0.078271 | 0.071119 | 0.13251 | -0.006022 | -0.001397 | -0.092773 | -0.0090512 | 0.063585 | 0.071459 | -0.00067729 | -0.0089573 | 60.2371 | 60.5118 | 2.6321 | -61.3129 | 60.2142 | -61.3266 | -61.29 | -61.0336 | 0.23346 | -61.5051 | 60.2188 | 60.1913 | -61.2854 | -61.3998 | -0.009155 | 0.027466 | -0.13275 | 121.8292 | 0.004578 | -0.022888 | -0.10986 | 0.032044 | -0.082397 | -0.12817 | 0.28381 | -0.18768 | -0.10529 | -0.15564 | 121.5317 | 121.5546 | 63.9496 | -121.637 | 121.5363 | 121.5088 | 61.5509 | -121.7468
1335.4219 | 121.843 | -61.3129 | 60.3653 | -0.19562 | 0.018143 | 0.073785 | 0.068129 | 0.12759 | -0.0051676 | -0.0016108 | -0.16144 | -0.0079832 | 0.06273 | 0.074023 | -0.00067729 | -0.0098117 | 60.2463 | 60.5026 | 2.6001 | -61.29 | 60.2371 | -61.2991 | -61.2625 | -61.0519 | 0.22888 | -61.5326 | 60.2463 | 60.1959 | -61.2488 | -61.4319 | 0.013733 | 0.050354 | -0.12817 | 121.8155 | 0.022888 | -0.027466 | -0.11902 | 0.064087 | -0.11902 | -0.11902 | 0.26093 | -0.21973 | -0.10071 | -0.16937 | 121.55 | 121.5591 | 63.913 | -121.6278 | 121.5591 | 121.5088 | 61.5417 | -121.7972
1337.1875 | 121.9803 | -61.2305 | 60.3424 | -0.10406 | 0.018997 | 0.076776 | 0.068769 | 0.12994 | -0.0055948 | -0.0041742 | -0.024109 | -0.0079832 | 0.061876 | 0.075731 | 0.00017731 | -0.01088 | 60.2646 | 60.5072 | 2.6642 | -61.3037 | 60.2325 | -61.3174 | -61.2625 | -60.9879 | 0.28839 | -61.4777 | 60.2234 | 60.1959 | -61.2762 | -61.4227 | -0.086975 | -0.032043 | -0.10986 | 121.7377 | -0.073242 | -0.041199 | -0.07782 | -0.045776 | -0.19226 | -0.11902 | 0.24262 | -0.24719 | -0.054932 | -0.14648 | 121.463 | 121.4951 | 63.8947 | -121.6049 | 121.4539 | 121.4264 | 61.5189 | -121.7651
1338.9688 | 121.9803 | -61.3586 | 60.2417 | 0.10956 | 0.01857 | 0.074213 | 0.061934 | 0.1308 | 0.00038662 | -0.0022516 | 0.17426 | -0.0047788 | 0.059526 | 0.073809 | 0.0055179 | -0.010239 | 60.1685 | 60.3973 | 2.7466 | -61.4044 | 60.1227 | -61.3953 | -61.3861 | -61.0977 | 0.10986 | -61.615 | 60.1089 | 60.054 | -61.3861 | -61.5051 | -0.036621 | -0.027465 | -0.11902 | 121.756 | -0.045776 | -0.018311 | -0.073242 | -0.027465 | -0.14648 | -0.13275 | 0.26093 | -0.25635 | -0.10986 | -0.18768 | 121.4813 | 121.5271 | 64.1052 | -121.6278 | 121.4676 | 121.4127 | 61.4685 | -121.7468
1340.7188 | 121.9025 | -61.3678 | 60.2646 | -0.18036 | 0.020706 | 0.072504 | 0.068556 | 0.12866 | 0.0023092 | -0.0039606 | -0.14618 | -0.0037106 | 0.065507 | 0.074663 | 0.0031681 | -0.010453 | 60.1593 | 60.347 | 2.6917 | -61.4044 | 60.2325 | -61.3815 | -61.3861 | -61.1206 | 0.22888 | -61.6425 | 60.2188 | 60.1501 | -61.3358 | -61.5051 | -0.013733 | -0.01831 | -0.032043 | 121.7148 | -0.036621 | -0.018311 | -0.10529 | 0.032044 | -0.13733 | -0.045776 | 0.24719 | -0.27466 | -0.13733 | -0.11444 | 121.6003 | 121.5271 | 64.0594 | -121.6507 | 121.5866 | 121.5179 | 61.5967 | -121.7697
1342.4062 | 121.8658 | -61.4044 | 60.2692 | -0.081177 | 0.021775 | 0.073572 | 0.06706 | 0.13144 | 0.0016684 | -0.0028924 | -0.085144 | -0.0060606 | 0.061876 | 0.074663 | 0.0038089 | -0.0091709 | 60.1685 | 60.3607 | 2.6962 | -61.4136 | 60.173 | -61.4182 | -61.3953 | -61.1114 | 0.24261 | -61.6562 | 60.173 | 60.1501 | -61.3678 | -61.5326 | -0.013733 | 0.009155 | -0.09613 | 121.7651 | -0.009155 | -0.01831 | -0.10071 | 0.036621 | -0.12817 | -0.09613 | 0.29297 | -0.25177 | -0.1236 | -0.11902 | 121.5775 | 121.5729 | 64.1006 | -121.6644 | 121.5775 | 121.5546 | 61.647 | -121.8018
1344.1562 | 121.962 | -61.2946 | 60.3058 | -0.11932 | 0.01857 | 0.073572 | 0.070478 | 0.13123 | -0.0081582 | -0.0041742 | -0.031738 | -0.006915 | 0.062517 | 0.071459 | 0.00039091 | -0.0087435 | 60.2234 | 60.5118 | 3.0212 | -61.3129 | 60.1822 | -61.3266 | -61.3037 | -60.9924 | 0.48523 | -61.4685 | 60.2051 | 60.1639 | -61.2854 | -61.4136 | -0.032043 | -0.009155 | -0.1236 | 121.8063 | -0.01831 | -0.009155 | -0.082397 | 0.009156 | -0.11902 | -0.10071 | 0.30212 | -0.17395 | -0.054932 | -0.14191 | 121.4767 | 121.5179 | 64.3158 | -121.6095 | 121.4996 | 121.4584 | 61.7798 | -121.7194
1345.9062 | 121.8521 | -61.4227 | 60.2646 | 0.040894 | 0.021775 | 0.072717 | 0.06407 | 0.12994 | 0.0027364 | -0.002038 | 0.059815 | -0.0054196 | 0.064012 | 0.075518 | 0.0050907 | -0.010453 | 60.0632 | 60.2234 | 2.829 | -61.496 | 60.1593 | -61.4639 | -61.441 | -61.2442 | 0.17853 | -61.7844 | 60.1685 | 60.0906 | -61.4365 | -61.5875 | -0.041199 | -0.018311 | -0.10529 | 121.6461 | -0.073243 | -0.054932 | -0.20142 | -0.013733 | -0.1648 | -0.09613 | 0.17853 | -0.36163 | -0.19684 | -0.17395 | 121.582 | 121.4859 | 64.2517 | -121.7056 | 121.5912 | 121.5134 | 61.6013 | -121.8521
1347.6562 | 121.8292 | -61.4456 | 60.2188 | 0.0027468 | 0.020279 | 0.072717 | 0.063643 | 0.12866 | 0.00017302 | -0.0028924 | 0.067444 | -0.0047788 | 0.062089 | 0.074877 | 0.0067997 | -0.0089573 | 60.0586 | 60.2371 | 2.8976 | -61.5005 | 60.1227 | -61.4685 | -61.4456 | -61.2305 | 0.27008 | -61.7615 | 60.1685 | 60.1318 | -61.4182 | -61.5738 | -0.022888 | 0 | -0.09613 | 121.6827 | -0.054931 | -0.054931 | -0.16022 | 0.027466 | -0.12817 | -0.050354 | 0.21515 | -0.31586 | -0.18768 | -0.086975 | 121.5683 | 121.5042 | 64.3433 | -121.6644 | 121.6141 | 121.5775 | 61.7157 | -121.7926
1349.3438 | 121.9803 | -61.2991 | 60.3012 | -0.10406 | 0.017716 | 0.076776 | 0.069624 | 0.12759 | -0.0090128 | -0.005456 | 0.036926 | -0.0088376 | 0.062944 | 0.073595 | -0.00024989 | -0.0078891 | 60.2142 | 60.466 | 3.1311 | -61.3174 | 60.1776 | -61.322 | -61.3174 | -61.0153 | 0.6134 | -61.4914 | 60.1685 | 60.1776 | -61.2991 | -61.4594 | -0.022888 | -0.018311 | -0.1236 | 121.7651 | -0.018311 | 0 | -0.086975 | 0 | -0.16022 | -0.13275 | 0.28381 | -0.19226 | -0.032043 | -0.1236 | 121.4767 | 121.5134 | 64.4302 | -121.6187 | 121.4676 | 121.4767 | 61.9125 | -121.7606
1351.1094 | 121.9391 | -61.3586 | 60.2463 | 0.08667 | 0.017289 | 0.075494 | 0.067274 | 0.12824 | -0.0047404 | -0.0060968 | 0.2124 | -0.0077696 | 0.061662 | 0.072741 | 0.0016727 | -0.0085299 | 60.1273 | 60.3607 | 3.1174 | -61.4227 | 60.1044 | -61.3998 | -61.3815 | -61.1023 | 0.49439 | -61.615 | 60.1318 | 60.1364 | -61.3586 | -61.496 | -0.041198 | -0.022888 | -0.14191 | 121.7194 | -0.064086 | -0.041198 | -0.11902 | 0 | -0.13733 | -0.11444 | 0.25635 | -0.25635 | -0.11902 | -0.10986 | 121.463 | 121.4859 | 64.476 | -121.6278 | 121.4905 | 121.4951 | 61.853 | -121.7422
1352.8594 | 121.9666 | -61.3953 | 60.1501 | 0.19348 | 0.017502 | 0.076135 | 0.062361 | 0.13037 | -0.0013224 | -0.0033196 | 0.15137 | -0.0077696 | 0.062517 | 0.075091 | 0.0067997 | -0.0089573 | 60.0769 | 60.2829 | 3.0716 | -61.4594 | 60.0998 | -61.4685 | -61.4502 | -61.1435 | 0.48981 | -61.6516 | 60.0723 | 60.022 | -61.4319 | -61.5417 | -0.073242 | -0.054931 | -0.050354 | 121.6782 | -0.064087 | -0.009156 | -0.073242 | -0.036621 | -0.14648 | -0.077819 | 0.25177 | -0.25635 | -0.10986 | -0.12817 | 121.4951 | 121.4722 | 64.4669 | -121.6003 | 121.4676 | 121.4172 | 61.8851 | -121.6919
1354.6094 | 121.8475 | -61.4639 | 60.2188 | -0.0354 | 0.02092 | 0.07464 | 0.06706 | 0.12973 | 0.0012412 | -0.0041742 | 0.014038 | -0.0056332 | 0.061235 | 0.073809 | 0.0038089 | -0.010666 | 60.1089 | 60.2921 | 3.1311 | -61.4548 | 60.1318 | -61.4777 | -61.4502 | -61.2259 | 0.5127 | -61.7661 | 60.1227 | 60.0815 | -61.4365 | -61.6013 | -0.013733 | 0.013733 | -0.086975 | 121.756 | 0.009155 | -0.004578 | -0.10986 | 0.027466 | -0.13733 | -0.09613 | 0.23804 | -0.30212 | -0.1648 | -0.13733 | 121.5958 | 121.5729 | 64.595 | -121.669 | 121.5866 | 121.5454 | 61.9766 | -121.8201
1356.2969 | 121.8933 | -61.4273 | 60.2371 | -0.11169 | 0.018997 | 0.072076 | 0.071119 | 0.12866 | -4.058e-05 | -0.0033196 | -0.069885 | -0.0067014 | 0.062089 | 0.070391 | 0.0044497 | -0.010239 | 60.1044 | 60.3287 | 3.2135 | -61.4273 | 60.141 | -61.4594 | -61.4319 | -61.1664 | 0.64087 | -61.6882 | 60.1501 | 60.1044 | -61.4502 | -61.5509 | -0.032044 | -0.004578 | -0.096131 | 121.756 | 0 | 0.004578 | -0.13275 | -0.022888 | -0.1236 | -0.086976 | 0.26093 | -0.26093 | -0.13733 | -0.13275 | 121.5683 | 121.5317 | 64.6408 | -121.669 | 121.5775 | 121.5317 | 62.0682 | -121.788
1358.0469 | 121.9482 | -61.409 | 60.1822 | 0.14008 | 0.017289 | 0.076563 | 0.064497 | 0.12952 | -0.0040994 | -0.0033196 | 0.23529 | -0.0099058 | 0.063158 | 0.073809 | 0.0038089 | -0.010025 | 60.0998 | 60.3378 | 3.3188 | -61.4273 | 60.0403 | -61.4502 | -61.4182 | -61.1023 | 0.67291 | -61.6425 | 60.0632 | 60.0494 | -61.4182 | -61.5829 | -0.041198 | -0.009155 | -0.14191 | 121.7468 | -0.01831 | -0.009155 | -0.082398 | -0.009155 | -0.17395 | -0.11902 | 0.3067 | -0.23346 | -0.059509 | -0.13275 | 121.4493 | 121.5088 | 64.7278 | -121.6003 | 121.4722 | 121.4584 | 62.0819 | -121.7651
1359.7969 | 121.8521 | -61.4548 | 60.1959 | -0.081177 | 0.017929 | 0.075067 | 0.06706 | 0.12824 | 0.0020956 | -0.003747 | -0.031738 | -0.0045652 | 0.063798 | 0.075304 | 0.0033817 | -0.0095981 | 60.1227 | 60.3012 | 3.4515 | -61.4365 | 60.0998 | -61.4777 | -61.4227 | -61.1572 | 0.70038 | -61.702 | 60.1547 | 60.0952 | -61.4044 | -61.5509 | -0.022888 | 0.032044 | -0.096131 | 121.756 | 0.018311 | -0.013733 | -0.073242 | 0.050354 | -0.09613 | -0.041199 | 0.29755 | -0.24719 | -0.15106 | -0.10071 | 121.5546 | 121.5775 | 64.9063 | -121.6187 | 121.6095 | 121.55 | 62.1552 | -121.7468
1361.5625 | 121.8613 | -61.3815 | 60.2646 | -0.19562 | 0.017289 | 0.075281 | 0.067915 | 0.1293 | -0.0068766 | -0.0039606 | -0.046997 | -0.0073422 | 0.06273 | 0.073809 | 0.00039091 | -0.0078891 | 60.141 | 60.4202 | 3.5294 | -61.3312 | 60.1318 | -61.3907 | -61.3724 | -61.0703 | 0.93842 | -61.5875 | 60.1501 | 60.1044 | -61.3678 | -61.5097 | -0.009155 | 0.009156 | -0.13275 | 121.8018 | 0.050354 | 0.041198 | -0.1236 | 0.013733 | -0.12817 | -0.11444 | 0.31128 | -0.20599 | -0.077819 | -0.16022 | 121.5134 | 121.5225 | 64.9109 | -121.637 | 121.5317 | 121.4859 | 62.3199 | -121.7743
1363.25 | 121.9894 | -61.3861 | 60.2097 | -0.012512 | 0.014298 | 0.076563 | 0.06706 | 0.12994 | -0.0064492 | -0.004815 | 0.10559 | -0.007556 | 0.061876 | 0.070605 | 0.00017731 | -0.0074619 | 60.0677 | 60.3241 | 3.5522 | -61.4182 | 60.0998 | -61.4456 | -61.3953 | -61.1252 | 0.86517 | -61.6196 | 60.1089 | 60.0632 | -61.3998 | -61.5417 | -0.05951 | -0.009156 | -0.10986 | 121.7102 | -0.032044 | -0.022888 | -0.14191 | -0.013733 | -0.15564 | -0.10071 | 0.26093 | -0.23346 | -0.07782 | -0.14649 | 121.4859 | 121.4539 | 64.9384 | -121.6049 | 121.4951 | 121.4493 | 62.2513 | -121.7514
1364.9844 | 121.843 | -61.5051 | 60.1776 | -0.17273 | 0.02092 | 0.075494 | 0.069624 | 0.12973 | -0.004313 | -0.0039606 | -0.11566 | -0.0096922 | 0.062303 | 0.072314 | -0.0013181 | -0.011948 | 60.0769 | 60.2966 | 3.8406 | -61.4273 | 60.022 | -61.4868 | -61.4548 | -61.1664 | 0.97046 | -61.6837 | 60.0815 | 60.0311 | -61.4456 | -61.6104 | 0.018311 | 0.050354 | -0.15564 | 121.8018 | 0.07782 | 0.027466 | -0.10071 | 0.059509 | -0.10529 | -0.09613 | 0.33875 | -0.17853 | -0.073242 | -0.14648 | 121.5271 | 121.582 | 65.3458 | -121.6324 | 121.5866 | 121.5363 | 62.4756 | -121.788
1366.7344 | 121.8475 | -62.3062 | 59.3491 | 0.010376 | 0.020706 | 0.073572 | 0.065351 | 0.13037 | 0.0053 | -0.003747 | 0.044556 | -0.0064878 | 0.062303 | 0.074663 | 0.0059451 | -0.01088 | 59.1614 | 59.3124 | 3.6255 | -62.3428 | 59.2575 | -62.3657 | -62.3291 | -62.0956 | 0.58594 | -62.6633 | 59.2529 | 59.2392 | -62.3337 | -62.4893 | -0.05951 | -0.022889 | -0.091553 | 121.6187 | -0.036621 | -0.013732 | -0.18768 | -0.027466 | -0.18311 | -0.09613 | 0.21057 | -0.35706 | -0.17395 | -0.10986 | 121.5637 | 121.4676 | 65.9317 | -121.6782 | 121.5591 | 121.5454 | 62.8922 | -121.8384
1368.4844 | 121.9849 | -62.8784 | 58.7448 | -0.21088 | 0.017502 | 0.076776 | 0.068342 | 0.12845 | -0.004954 | -0.0041742 | -0.0012209 | -0.0088376 | 0.063158 | 0.071459 | -0.0015317 | -0.010239 | 58.6533 | 58.8959 | 3.9871 | -62.8281 | 58.6166 | -62.9242 | -62.883 | -62.5076 | 0.83771 | -63.0524 | 58.6121 | 58.6029 | -62.851 | -62.9974 | -0.045776 | -0.004578 | -0.12817 | 121.7743 | 0.050354 | 0.054932 | -0.091553 | 0.027466 | -0.11902 | -0.13275 | 0.37079 | -0.17395 | -0.054931 | -0.14191 | 121.4951 | 121.5317 | 66.8655 | -121.6278 | 121.4905 | 121.4813 | 63.7161 | -121.7422
1370.1719 | 121.9482 | -62.1689 | 59.4452 | 0.10956 | 0.018784 | 0.07699 | 0.062147 | 0.12888 | 0.001882 | -0.0050286 | 0.10559 | -0.0043516 | 0.060167 | 0.073168 | 0.0050907 | -0.011734 | 59.317 | 59.4589 | 3.923 | -62.2147 | 59.404 | -62.2513 | -62.2101 | -61.9263 | 0.62256 | -62.4893 | 59.3994 | 59.3628 | -62.1964 | -62.3383 | -0.082398 | -0.041199 | -0.041198 | 121.6278 | -0.045777 | -0.004578 | -0.12817 | -0.027466 | -0.16937 | -0.045776 | 0.24261 | -0.32044 | -0.15106 | -0.082397 | 121.5729 | 121.4859 | 66.0919 | -121.6553 | 121.5683 | 121.5317 | 62.7914 | -121.7834
1371.9219 | 121.8887 | -62.0041 | 59.6558 | -0.21851 | 0.019211 | 0.078485 | 0.069838 | 0.12909 | -0.00068138 | -0.0035334 | -0.14618 | -0.0071286 | 0.065935 | 0.073595 | 0.0042361 | -0.0085299 | 59.5093 | 59.7107 | 4.0604 | -61.9583 | 59.6054 | -62.0087 | -61.972 | -61.734 | 0.86517 | -62.2879 | 59.5825 | 59.5551 | -61.9858 | -62.1094 | -0.004578 | 0.032043 | -0.050354 | 121.7148 | 0.045776 | 0.013733 | -0.14649 | 0.01831 | -0.10529 | -0.073242 | 0.27008 | -0.28381 | -0.17853 | -0.10071 | 121.6095 | 121.5134 | 66.0645 | -121.6278 | 121.5866 | 121.5591 | 62.8693 | -121.7651
1373.6719 | 121.8979 | -62.0087 | 59.6649 | -0.14984 | 0.018143 | 0.074854 | 0.065779 | 0.12952 | -4.058e-05 | -0.0035334 | -0.11566 | -0.007556 | 0.06273 | 0.074023 | 0.0027407 | -0.011307 | 59.5367 | 59.729 | 4.2389 | -61.94 | 59.5642 | -62.0224 | -61.9858 | -61.6974 | 0.91095 | -62.2559 | 59.5871 | 59.5413 | -61.9675 | -62.1231 | -0.013733 | 0.022888 | -0.10071 | 121.7377 | 0.068665 | 0.045777 | -0.12817 | 0.041199 | -0.11444 | -0.07782 | 0.31128 | -0.24719 | -0.13275 | -0.1236 | 121.5729 | 121.5454 | 66.2476 | -121.6507 | 121.5958 | 121.55 | 62.9196 | -121.788
1375.3594 | 121.9711 | -62.0041 | 59.5688 | 0.26978 | 0.01857 | 0.075067 | 0.067488 | 0.12674 | -0.0028178 | -0.0028924 | 0.20477 | -0.008624 | 0.062517 | 0.071673 | 0.0012455 | -0.010666 | 59.5184 | 59.7519 | 4.4266 | -61.9446 | 59.4772 | -62.0407 | -62.0132 | -61.6791 | 0.8606 | -62.2467 | 59.4818 | 59.4452 | -61.9949 | -62.1552 | -0.036621 | -0.009156 | -0.091553 | 121.756 | 0.059509 | 0.068665 | -0.050354 | 0.009155 | -0.15106 | -0.086975 | 0.32501 | -0.24262 | -0.091553 | -0.1236 | 121.4813 | 121.5225 | 66.4307 | -121.582 | 121.4859 | 121.4493 | 62.8647 | -121.7239
1377.125 | 121.8979 | -62.1094 | 59.5322 | 0.063782 | 0.018357 | 0.073785 | 0.067488 | 0.1308 | 0.0012412 | -0.0016108 | 0.12848 | -0.006915 | 0.062517 | 0.074877 | 0.0053043 | -0.0091709 | 59.3445 | 59.5276 | 4.3854 | -62.1094 | 59.4498 | -62.1689 | -62.1368 | -61.8576 | 0.73242 | -62.4435 | 59.4406 | 59.4589 | -62.114 | -62.265 | -0.059509 | -0.027466 | -0.082398 | 121.637 | 0 | 0.027466 | -0.18768 | -0.004578 | -0.15564 | -0.091553 | 0.25177 | -0.33417 | -0.17853 | -0.073243 | 121.5591 | 121.4539 | 66.4948 | -121.669 | 121.55 | 121.5683 | 62.8418 | -121.7972
1378.8594 | 121.8475 | -62.2055 | 59.4589 | 0.0027468 | 0.022415 | 0.074426 | 0.067701 | 0.1293 | -0.0023904 | -0.0018244 | 0.082703 | -0.0049924 | 0.063798 | 0.07445 | 0.0044497 | -0.010239 | 59.3079 | 59.4772 | 4.4907 | -62.1506 | 59.3674 | -62.2055 | -62.1872 | -61.9308 | 0.80566 | -62.5259 | 59.3903 | 59.3628 | -62.1826 | -62.3154 | 0 | 0.01831 | -0.091552 | 121.6827 | 0.054931 | 0.036621 | -0.15106 | 0.022888 | -0.10986 | -0.068664 | 0.27466 | -0.32043 | -0.21057 | -0.09613 | 121.5729 | 121.5134 | 66.6962 | -121.6461 | 121.5958 | 121.5683 | 63.0112 | -121.7743
1380.625 | 121.9757 | -62.1506 | 59.4452 | -0.065918 | 0.016007 | 0.07699 | 0.069838 | 0.12845 | -0.0070902 | -0.004815 | 0.014038 | -0.010333 | 0.061876 | 0.071245 | -0.00046349 | -0.0074619 | 59.3308 | 59.5871 | 4.8203 | -62.1185 | 59.317 | -62.2192 | -62.2009 | -61.821 | 1.1124 | -62.384 | 59.317 | 59.2987 | -62.1918 | -62.3154 | -0.068664 | -0.050354 | -0.12817 | 121.7377 | 0.032044 | 0.082398 | -0.11444 | -0.041198 | -0.16479 | -0.12817 | 0.32959 | -0.23346 | -0.068664 | -0.14648 | 121.4676 | 121.4813 | 66.9708 | -121.6461 | 121.4676 | 121.4493 | 63.2629 | -121.7606
1382.3125 | 121.9391 | -62.2925 | 59.3124 | 0.10956 | 0.018997 | 0.076776 | 0.065565 | 0.12888 | -0.0053812 | -0.0043878 | 0.20477 | -0.0077696 | 0.061876 | 0.071032 | -0.00046349 | -0.0095981 | 59.1888 | 59.4223 | 4.7791 | -62.2559 | 59.166 | -62.352 | -62.2879 | -61.9766 | 0.98877 | -62.5351 | 59.1888 | 59.1751 | -62.2742 | -62.4435 | -0.05951 | 0.004577 | -0.14648 | 121.7148 | 0.036621 | 0.032044 | -0.1236 | 0.01831 | -0.15106 | -0.1236 | 0.31586 | -0.24262 | -0.091553 | -0.13733 | 121.4584 | 121.4813 | 67.0715 | -121.6003 | 121.4813 | 121.4676 | 63.2812 | -121.756
1384.0625 | 121.9666 | -62.4023 | 59.1934 | 0.15533 | 0.021775 | 0.076135 | 0.062574 | 0.13144 | 0.0010276 | -0.0052424 | 0.2124 | -0.005206 | 0.062944 | 0.071673 | 0.0029543 | -0.011094 | 59.1339 | 59.3353 | 4.7882 | -62.3383 | 59.0881 | -62.4664 | -62.4207 | -62.0636 | 0.99335 | -62.6358 | 59.0744 | 59.0057 | -62.439 | -62.5671 | -0.064087 | -0.01831 | -0.10529 | 121.7377 | 0.064087 | 0.082397 | -0.059509 | -0.036621 | -0.16479 | -0.11902 | 0.33874 | -0.23346 | -0.068664 | -0.18768 | 121.4905 | 121.5363 | 67.1906 | -121.6141 | 121.4767 | 121.4081 | 63.3957 | -121.7606
1385.8125 | 121.8475 | -62.5305 | 59.1751 | -0.17273 | 0.022202 | 0.074854 | 0.071547 | 0.12994 | -0.002604 | -0.003747 | -0.13092 | -0.0088376 | 0.064012 | 0.074236 | -0.0011045 | -0.012589 | 58.9874 | 59.2026 | 4.715 | -62.4435 | 59.0607 | -62.5351 | -62.4847 | -62.2101 | 1.0986 | -62.7869 | 59.0881 | 59.0607 | -62.4619 | -62.6129 | -0.004577 | 0.045777 | -0.11444 | 121.7331 | 0.086976 | 0.041199 | -0.18768 | 0.068665 | -0.082397 | -0.086975 | 0.32044 | -0.25635 | -0.17395 | -0.11444 | 121.5912 | 121.5179 | 67.2455 | -121.6599 | 121.6187 | 121.5912 | 63.6292 | -121.788
1387.4844 | 121.962 | -64.5035 | 57.0923 | 0.0027468 | 0.015366 | 0.079767 | 0.063429 | 0.12717 | -0.0040994 | -0.003747 | 0.10559 | -0.0081968 | 0.059312 | 0.0721 | 0.0016727 | -0.0095981 | 56.8176 | 57.0557 | 4.8569 | -64.5905 | 56.8268 | -64.682 | -64.6774 | -64.3158 | 0.78278 | -64.8972 | 56.8771 | 56.8359 | -64.6545 | -64.7919 | -0.17853 | -0.17395 | -0.2655 | 121.5591 | -0.086975 | 0.086975 | -0.27466 | -0.15106 | -0.28839 | -0.21515 | 0.18768 | -0.39368 | -0.10529 | -0.25635 | 121.3303 | 121.3211 | 69.3604 | -121.7697 | 121.3806 | 121.3394 | 65.2863 | -121.8842
1389.25 | 121.9574 | -62.677 | 58.905 | 0.0027468 | 0.017502 | 0.076563 | 0.06941 | 0.12952 | -0.0047404 | -0.003747 | 0.12848 | -0.0077696 | 0.064653 | 0.073382 | 0.00017731 | -0.01088 | 58.7585 | 58.992 | 4.8431 | -62.6404 | 58.7952 | -62.764 | -62.7502 | -62.4023 | 1.0712 | -62.9837 | 58.7997 | 58.7448 | -62.7228 | -62.8601 | -0.086975 | -0.073242 | -0.10986 | 121.669 | 0.036621 | 0.10986 | -0.14648 | -0.045776 | -0.1831 | -0.10529 | 0.27466 | -0.3067 | -0.1236 | -0.16022 | 121.4722 | 121.4355 | 67.5201 | -121.6553 | 121.4767 | 121.4218 | 63.7482 | -121.7651
1391 | 121.9666 | -62.6678 | 58.9417 | -0.14221 | 0.01857 | 0.075922 | 0.065779 | 0.12952 | -0.0028178 | -0.0063104 | -0.085144 | -0.0092648 | 0.062303 | 0.071459 | 0.0038089 | -0.0095981 | 58.8913 | 59.1385 | 5.127 | -62.5534 | 58.8181 | -62.7274 | -62.6999 | -62.2833 | 1.2909 | -62.8693 | 58.8135 | 58.7723 | -62.6633 | -62.796 | -0.059509 | -0.032043 | -0.1236 | 121.8063 | 0.11444 | 0.14648 | -0.050354 | 0.004578 | -0.12817 | -0.12817 | 0.38452 | -0.20142 | -0.073242 | -0.16937 | 121.4859 | 121.5591 | 67.7948 | -121.6415 | 121.4813 | 121.4401 | 63.9587 | -121.7377
1392.7031 | 121.8567 | -63.2172 | 58.4564 | -0.20325 | 0.021134 | 0.076349 | 0.070051 | 0.13165 | -4.058e-05 | -0.0028924 | -0.15381 | -0.006915 | 0.064012 | 0.073595 | 0.0014591 | -0.0098117 | 58.2825 | 58.5068 | 4.9805 | -63.1165 | 58.3786 | -63.2538 | -63.2217 | -62.883 | 1.0849 | -63.4918 | 58.3923 | 58.3328 | -63.1851 | -63.3316 | -0.036621 | -0.004578 | -0.07782 | 121.7239 | 0.10071 | 0.10529 | -0.17395 | 0.032043 | -0.11444 | -0.064087 | 0.33417 | -0.27466 | -0.16022 | -0.1236 | 121.5958 | 121.4996 | 68.1976 | -121.6782 | 121.6095 | 121.55 | 64.3021 | -121.788
1394.4531 | 121.994 | -63.1302 | 58.4518 | -0.0048827 | 0.01857 | 0.074213 | 0.066847 | 0.1293 | -0.0034586 | -0.0033196 | 0.067444 | -0.0073422 | 0.063371 | 0.073809 | 0.0012455 | -0.011094 | 58.3191 | 58.5846 | 4.8019 | -63.0707 | 58.3832 | -63.1989 | -63.1668 | -62.7869 | 1.1353 | -63.3591 | 58.3511 | 58.3008 | -63.1302 | -63.2858 | -0.068665 | -0.036621 | -0.068664 | 121.7148 | 0.059509 | 0.09613 | -0.13275 | 0 | -0.15564 | -0.10071 | 0.34332 | -0.22888 | -0.073242 | -0.15106 | 121.5134 | 121.4493 | 67.9321 | -121.6187 | 121.4813 | 121.431 | 64.2654 | -121.7377
1396.2031 | 121.875 | -63.3545 | 58.2458 | -0.096436 | 0.019852 | 0.075281 | 0.066633 | 0.12888 | 0.0048728 | -0.0009698 | -0.1004 | -0.0043516 | 0.060594 | 0.075304 | 0.0076541 | -0.012162 | 58.1863 | 58.3786 | 4.5685 | -63.2263 | 58.2275 | -63.4048 | -63.3499 | -62.9837 | 1.0666 | -63.6383 | 58.1863 | 58.1406 | -63.3453 | -63.501 | -0.050354 | 0.004577 | -0.018311 | 121.7331 | 0.12817 | 0.1236 | -0.05951 | 0.009155 | -0.14648 | -0.05951 | 0.37079 | -0.28381 | -0.13733 | -0.10529 | 121.582 | 121.5408 | 67.923 | -121.5958 | 121.5408 | 121.4951 | 64.4211 | -121.7468
1397.9688 | 121.843 | -65.5884 | 56.0669 | -0.23376 | 0.020279 | 0.077844 | 0.071547 | 0.13123 | -0.0013224 | -0.0052424 | -0.15381 | -0.0088376 | 0.061662 | 0.074663 | 0.0010317 | -0.0095981 | 55.632 | 55.8472 | 4.5868 | -65.6937 | 55.7144 | -65.8997 | -65.8859 | -65.7028 | 0.43945 | -66.3803 | 55.5176 | 55.4764 | -66.0416 | -66.1148 | -0.31128 | -0.29755 | -0.35248 | 121.4355 | -0.10529 | 0.19226 | -0.43488 | -0.45319 | -0.52643 | -0.54932 | -0.11444 | -0.79193 | -0.2655 | -0.59052 | 121.3028 | 121.2204 | 70.1752 | -121.9528 | 121.106 | 121.0648 | 66.0278 | -122.1817
1399.6562 | 121.8796 | -63.7848 | 57.8888 | -0.096436 | 0.023911 | 0.073999 | 0.070692 | 0.12909 | 0.0029502 | -0.0005426 | -0.085144 | -0.0026426 | 0.065935 | 0.075304 | 0.0027407 | -0.012803 | 57.7789 | 57.9575 | 4.3442 | -63.6429 | 57.7927 | -63.8031 | -63.7619 | -63.3957 | 0.96588 | -64.0503 | 57.7927 | 57.7423 | -63.7527 | -63.9359 | -0.018311 | 0.022888 | -0.09613 | 121.7422 | 0.14191 | 0.11902 | -0.10986 | 0.032043 | -0.15106 | -0.09613 | 0.3891 | -0.2655 | -0.11444 | -0.14648 | 121.5775 | 121.5637 | 68.129 | -121.6507 | 121.5775 | 121.5271 | 64.7507 | -121.8246
1401.4062 | 121.8613 | -63.8809 | 57.7744 | -0.25665 | 0.022202 | 0.074426 | 0.067701 | 0.13016 | -0.0034586 | -0.0022516 | -0.15381 | -0.0049924 | 0.063585 | 0.074023 | 0.0018863 | -0.0087435 | 57.6233 | 57.8659 | 4.2984 | -63.7619 | 57.6645 | -63.9175 | -63.8901 | -63.5468 | 1.0208 | -64.1647 | 57.6965 | 57.6736 | -63.8718 | -64.0182 | -0.036622 | -0.009156 | -0.10986 | 121.7468 | 0.11902 | 0.12817 | -0.15106 | 0.009155 | -0.13733 | -0.07782 | 0.33417 | -0.28381 | -0.14648 | -0.10071 | 121.5454 | 121.5042 | 68.1793 | -121.6644 | 121.5775 | 121.5546 | 64.9017 | -121.7926
1403.1094 | 121.9666 | -70.079 | 51.4664 | 0.11719 | 0.019211 | 0.078058 | 0.063429 | 0.1308 | -4.058e-05 | -0.0016108 | 0.17426 | -0.0077696 | 0.062089 | 0.072527 | 0.0033817 | -0.0091709 | 51.3886 | 51.6541 | 5.3513 | -69.96 | 51.3153 | -70.1935 | -70.1385 | -69.6808 | -0.34332 | -70.3217 | 51.3428 | 51.3199 | -70.1431 | -70.2896 | -0.11444 | -0.059509 | -0.15106 | 121.7331 | 0.11902 | 0.17853 | -0.07782 | -0.064086 | -0.21057 | -0.1236 | 0.39826 | -0.24261 | -0.032043 | -0.14648 | 121.3943 | 121.4676 | 75.4303 | -121.6049 | 121.4218 | 121.3989 | 69.7357 | -121.756
1404.8125 | 121.9849 | -64.2105 | 57.399 | 0.14008 | 0.023056 | 0.075708 | 0.065779 | 0.12695 | -0.00025418 | -0.0039606 | 0.17426 | -0.005847 | 0.061876 | 0.074236 | 0.0044497 | -0.010453 | 57.3441 | 57.5546 | 4.3121 | -64.0228 | 57.3303 | -64.2288 | -64.1876 | -63.7756 | 0.89722 | -64.4028 | 57.3166 | 57.2891 | -64.183 | -64.325 | -0.018311 | 0.022888 | -0.068665 | 121.7651 | 0.18768 | 0.16479 | -0.054932 | 0.027466 | -0.11444 | -0.082398 | 0.43487 | -0.19226 | -0.07782 | -0.10986 | 121.5408 | 121.5546 | 68.5226 | -121.5866 | 121.5271 | 121.4996 | 65.1077 | -121.7239
1406.5625 | 121.9208 | -71.2784 | 50.3036 | 0.063782 | 0.018997 | 0.07934 | 0.068342 | 0.13037 | -0.006022 | -0.003106 | 0.11322 | -0.0073422 | 0.064867 | 0.072741 | -3.629e-05 | -0.0087435 | 50.116 | 50.3586 | 5.8502 | -71.1777 | 50.1343 | -71.402 | -71.3242 | -70.8939 | -0.52643 | -71.5485 | 50.1801 | 50.1709 | -71.3287 | -71.4752 | -0.1236 | -0.045777 | -0.16937 | 121.637 | 0.10071 | 0.14648 | -0.18768 | -0.050354 | -0.19684 | -0.1236 | 0.38452 | -0.27008 | -0.073242 | -0.13275 | 121.4127 | 121.3943 | 77.1286 | -121.6278 | 121.4584 | 121.4493 | 70.752 | -121.7789
1408.3125 | 121.875 | -66.5039 | 55.2017 | -0.24139 | 0.021347 | 0.077417 | 0.070906 | 0.12973 | 0.0010276 | -0.0018244 | -0.1767 | -0.0062742 | 0.063158 | 0.073168 | 0.00039091 | -0.010453 | 55.4718 | 55.6366 | 4.39 | -65.9088 | 55.5222 | -66.069 | -66.069 | -65.7486 | 0.53101 | -66.3712 | 55.5084 | 55.4581 | -66.0873 | -66.2384 | 0.43488 | 0.43488 | 0.32044 | 122.1405 | 0.59509 | 0.16022 | 0.27008 | 0.41657 | 0.2655 | 0.3067 | 0.75531 | 0.13275 | -0.13275 | 0.25635 | 122.0261 | 121.9757 | 70.8939 | -121.2708 | 122.0123 | 121.962 | 67.0349 | -121.4401
1409.9844 | 121.9437 | -66.4627 | 55.1285 | 0.063782 | 0.020706 | 0.079126 | 0.06407 | 0.1293 | -0.004313 | -0.0028924 | 0.15137 | -0.010119 | 0.061662 | 0.073809 | 0.0020999 | -0.0083163 | 55.1239 | 55.394 | 4.4678 | -66.2018 | 55.1285 | -66.394 | -66.3391 | -65.9546 | 0.56763 | -66.5909 | 55.1605 | 55.1102 | -66.3574 | -66.5085 | 0.068665 | 0.1236 | 0 | 121.8567 | 0.26093 | 0.13733 | -0.004578 | 0.10529 | -0.045776 | 0.032043 | 0.50812 | -0.12817 | -0.082397 | -0.018311 | 121.5912 | 121.5866 | 70.9305 | -121.4676 | 121.6232 | 121.5729 | 67.0303 | -121.637
1411.7344 | 121.8842 | -66.5863 | 55.0735 | -0.24139 | 0.02092 | 0.077203 | 0.068983 | 0.12888 | 0.0012412 | -0.0026788 | -0.16907 | -0.0071286 | 0.061662 | 0.072954 | 0.0044497 | -0.011094 | 54.9728 | 55.1788 | 4.5044 | -66.3849 | 55.0552 | -66.5771 | -66.5497 | -66.1697 | 0.48523 | -66.8289 | 55.0323 | 54.9591 | -66.568 | -66.6824 | 0.009156 | 0.036621 | -0.01831 | 121.7651 | 0.20142 | 0.16479 | -0.10071 | 0.018311 | -0.09613 | -0.041198 | 0.41656 | -0.24261 | -0.14648 | -0.11444 | 121.6415 | 121.5591 | 71.0907 | -121.6232 | 121.6187 | 121.5454 | 67.0715 | -121.756
1413.4375 | 121.9391 | -67.6071 | 53.9795 | -0.18799 | 0.022415 | 0.080408 | 0.071119 | 0.12973 | -0.004954 | -0.0028924 | -0.062256 | -0.006915 | 0.063158 | 0.072954 | -0.00067729 | -0.0095981 | 55.6778 | 55.8563 | 4.509 | -65.8218 | 55.545 | -66.0416 | -66.0416 | -66.806 | -0.059509 | -67.4515 | 54.2679 | 54.2084 | -67.2501 | -67.4194 | 1.5656 | 1.5656 | 1.5656 | 123.4634 | 1.7853 | 0.21973 | 1.6983 | 0.35706 | 0.18768 | 0.28839 | 0.80109 | 0.15564 | -0.032043 | 0.22888 | 123.1522 | 123.2849 | 72.1161 | -120.0211 | 121.875 | 121.8155 | 67.5476 | -121.3989
1415.1875 | 121.8567 | -66.4124 | 55.2887 | -0.073547 | 0.021134 | 0.077844 | 0.067915 | 0.12994 | 0.003591 | 0.0003118 | -0.085144 | -0.0032834 | 0.062089 | 0.075304 | 0.0065859 | -0.011521 | 55.1971 | 55.3848 | 3.8177 | -66.1652 | 55.2109 | -66.3849 | -66.362 | -65.9409 | 0.46692 | -66.6138 | 55.2109 | 55.1697 | -66.3483 | -66.4902 | 0.027466 | 0.050354 | -0.07782 | 121.7972 | 0.24719 | 0.19684 | -0.091552 | 0.064087 | -0.077819 | -0.07782 | 0.4715 | -0.20142 | -0.1236 | -0.11902 | 121.6232 | 121.6095 | 70.2301 | -121.6507 | 121.6232 | 121.582 | 66.8793 | -121.7789
1416.9375 | 121.9482 | -66.5817 | 54.9911 | 0.14771 | 0.017716 | 0.081049 | 0.064283 | 0.1293 | -0.00068138 | -0.0005426 | 0.19714 | -0.0079832 | 0.059312 | 0.073382 | 0.0023135 | -0.0087435 | 54.9454 | 55.1605 | 4.5685 | -66.394 | 54.8813 | -66.6321 | -66.6 | -66.1514 | 0.41199 | -66.7969 | 54.9042 | 54.8584 | -66.6046 | -66.7557 | -0.050354 | -0.018311 | -0.10986 | 121.7422 | 0.18768 | 0.20599 | -0.045776 | -0.022888 | -0.17395 | -0.086975 | 0.4303 | -0.21515 | -0.041199 | -0.13275 | 121.463 | 121.5271 | 71.1502 | -121.5912 | 121.4859 | 121.4401 | 66.9937 | -121.7468
1418.6875 | 121.8613 | -66.6595 | 55.0049 | -0.24139 | 0.020279 | 0.079553 | 0.068129 | 0.12994 | -0.0013224 | -0.002038 | -0.13855 | -0.006915 | 0.060808 | 0.073168 | 0.0040225 | -0.0078891 | 54.8492 | 55.0827 | 3.2913 | -66.4398 | 54.9316 | -66.655 | -66.6367 | -66.243 | 0.45319 | -66.9113 | 54.9591 | 54.9179 | -66.6183 | -66.7786 | 0.004578 | 0.022888 | -0.073242 | 121.7422 | 0.21973 | 0.19684 | -0.15564 | 0.041199 | -0.11902 | -0.045777 | 0.41657 | -0.25177 | -0.13275 | -0.086975 | 121.5912 | 121.5088 | 69.9509 | -121.6415 | 121.6187 | 121.5775 | 67.1127 | -121.7834
1420.3906 | 121.8292 | -68.1839 | 53.4714 | -0.073547 | 0.021988 | 0.080621 | 0.069624 | 0.13336 | 0.0053 | -0.0009698 | -0.039368 | -0.0056332 | 0.064867 | 0.074236 | 0.0042361 | -0.010239 | 53.389 | 53.5583 | 4.6005 | -67.9459 | 53.4027 | -68.2114 | -68.1885 | -67.7582 | -0.16937 | -68.4357 | 53.3981 | 53.3707 | -68.1473 | -68.3075 | -0.027466 | -0.004578 | -0.068665 | 121.7422 | 0.23804 | 0.24262 | -0.082398 | 0.036621 | -0.1236 | -0.073243 | 0.42572 | -0.25177 | -0.12817 | -0.10071 | 121.5866 | 121.5729 | 72.7844 | -121.6599 | 121.582 | 121.5546 | 68.0145 | -121.7789
1422.1406 | 121.8384 | -68.1015 | 53.5629 | -0.22614 | 0.017289 | 0.083398 | 0.064924 | 0.13037 | -0.0036722 | -0.0011834 | -0.092773 | -0.0060606 | 0.059099 | 0.074663 | 0.0018863 | -0.0089573 | 53.3615 | 53.6224 | 4.422 | -67.8772 | 53.4668 | -68.129 | -68.1061 | -67.7216 | -0.17853 | -68.3807 | 53.4851 | 53.4302 | -68.1061 | -68.2571 | -0.027466 | -0.004578 | -0.09613 | 121.7239 | 0.2243 | 0.22888 | -0.20142 | -0.004578 | -0.15564 | -0.07782 | 0.37994 | -0.27924 | -0.1236 | -0.13275 | 121.5683 | 121.463 | 72.5235 | -121.669 | 121.5866 | 121.5317 | 67.923 | -121.8201
1423.8281 | 121.962 | -69.5297 | 52.0203 | 0.040894 | 0.019425 | 0.080621 | 0.064497 | 0.13336 | -0.00068138 | -0.0024652 | 0.17426 | -0.0067014 | 0.061021 | 0.073168 | 0.0059451 | -0.0089573 | 51.9791 | 52.1942 | 4.7653 | -69.3054 | 51.9562 | -69.6121 | -69.5755 | -69.0765 | -0.63629 | -69.7586 | 51.9058 | 51.9012 | -69.5709 | -69.7128 | -0.082398 | -0.045776 | -0.064087 | 121.7239 | 0.2243 | 0.27008 | -0.041199 | -0.041199 | -0.18311 | -0.11444 | 0.45319 | -0.22888 | -0.045776 | -0.11902 | 121.4859 | 121.5088 | 74.295 | -121.5958 | 121.4355 | 121.431 | 68.8934 | -121.7331
1425.5781 | 121.907 | -69.9188 | 51.7044 | -0.21088 | 0.024338 | 0.07998 | 0.073256 | 0.1293 | 0.0010276 | -0.0007562 | -0.15381 | -0.006915 | 0.063158 | 0.074877 | -0.0011045 | -0.0072483 | 51.5259 | 51.741 | 4.7333 | -69.6899 | 51.6495 | -69.9738 | -69.9554 | -69.5023 | -0.737 | -70.1843 | 51.6815 | 51.6357 | -69.9097 | -70.0653 | -0.054932 | -0.036621 | -0.054932 | 121.6599 | 0.22888 | 0.2655 | -0.17853 | 0.009155 | -0.14648 | -0.022888 | 0.41657 | -0.2655 | -0.11902 | -0.068665 | 121.5683 | 121.4447 | 74.6521 | -121.6599 | 121.6003 | 121.5546 | 69.1818 | -121.7697
1427.2656 | 121.8384 | -70.2209 | 51.4343 | 0.010376 | 0.024552 | 0.079767 | 0.067488 | 0.12952 | 0.0050864 | -0.001397 | 0.075073 | -0.0056332 | 0.063585 | 0.076159 | 0.0040225 | -0.0089573 | 51.2375 | 51.4023 | 4.953 | -70.0607 | 51.2924 | -70.3125 | -70.3033 | -69.7998 | -0.97046 | -70.5139 | 51.3748 | 51.3382 | -70.2347 | -70.3354 | -0.091553 | -0.082398 | -0.14191 | 121.6232 | 0.16022 | 0.24261 | -0.19684 | -0.013733 | -0.11444 | -0.059509 | 0.42114 | -0.29297 | -0.17853 | -0.09613 | 121.5134 | 121.4584 | 75.1739 | -121.7377 | 121.5958 | 121.5591 | 69.2505 | -121.7697
1429.0156 | 121.9254 | -70.5231 | 51.0635 | 0.063782 | 0.019425 | 0.085107 | 0.068556 | 0.12952 | -0.006663 | -0.0018244 | 0.17426 | -0.0071286 | 0.062944 | 0.073382 | -0.0015317 | -0.0074619 | 50.9399 | 51.1963 | 2.449 | -70.2621 | 50.9445 | -70.5826 | -70.5368 | -70.0699 | -1.0391 | -70.752 | 50.9674 | 50.9354 | -70.5231 | -70.6924 | -0.05951 | -0.013733 | -0.11902 | 121.7194 | 0.26093 | 0.27466 | -0.1236 | 0 | -0.16937 | -0.096131 | 0.45319 | -0.22888 | -0.059509 | -0.12817 | 121.4676 | 121.463 | 72.9721 | -121.6003 | 121.4905 | 121.4584 | 69.4839 | -121.756
1430.7031 | 121.9803 | -71.0678 | 50.5142 | -0.12695 | 0.019852 | 0.084894 | 0.06642 | 0.13165 | -0.004313 | -0.0028924 | 0.014038 | -0.0077696 | 0.061449 | 0.073382 | 0.00039091 | -0.011521 | 50.4547 | 50.7202 | 1.8997 | -70.752 | 50.441 | -71.1044 | -71.0724 | -70.5276 | -1.0986 | -71.2234 | 50.4227 | 50.4089 | -71.0678 | -71.1914 | -0.036621 | -0.004578 | -0.073242 | 121.788 | 0.31586 | 0.32044 | -0.059509 | 0 | -0.1236 | -0.091553 | 0.54016 | -0.15564 | -0.032044 | -0.10529 | 121.5088 | 121.5225 | 72.9675 | -121.5866 | 121.4905 | 121.4767 | 69.9692 | -121.7056
1432.4531 | 121.9482 | -72.5464 | 49.0448 | 0.14771 | 0.016648 | 0.083398 | 0.065351 | 0.13358 | -0.00025418 | -0.0009698 | 0.22766 | -0.0079832 | 0.062089 | 0.076372 | 0.0040225 | -0.010025 | 48.9258 | 49.1318 | 3.6667 | -72.4319 | 48.7747 | -72.8485 | -72.821 | -71.9788 | -2.0096 | -72.6837 | 48.9532 | 48.9441 | -72.4823 | -72.5967 | -0.30212 | -0.27466 | -0.27008 | 121.6782 | 0.11444 | 0.3891 | -0.11902 | 0.064087 | -0.050354 | -0.091553 | 0.56763 | -0.13733 | -0.086975 | -0.10071 | 121.3211 | 121.4722 | 76.2131 | -121.8658 | 121.4996 | 121.4905 | 70.5368 | -121.6415
1434.1875 | 121.8384 | -71.2234 | 50.4639 | -0.24139 | 0.019852 | 0.086389 | 0.071119 | 0.13593 | -0.00046778 | -0.0009698 | -0.15381 | -0.007556 | 0.063585 | 0.072314 | 0.0018863 | -0.010453 | 50.2853 | 50.5508 | 1.2955 | -70.8755 | 50.3311 | -71.228 | -71.2143 | -70.7611 | -1.8219 | -71.5073 | 50.3403 | 50.2808 | -71.2418 | -71.3654 | -0.004577 | 0.009156 | -0.13275 | 121.7743 | 0.3479 | 0.33874 | -0.17853 | -0.01831 | -0.14191 | -0.1236 | 0.46234 | -0.28381 | -0.14191 | -0.1831 | 121.5546 | 121.5088 | 72.5189 | -121.6782 | 121.5637 | 121.5042 | 69.4016 | -121.8292
1435.9375 | 121.8887 | -71.9421 | 49.7177 | -0.20325 | 0.02327 | 0.088098 | 0.068769 | 0.13699 | 0.0029502 | 0.0003118 | -0.14618 | -0.0054196 | 0.064867 | 0.073168 | 0.0014591 | -0.010239 | 49.5987 | 49.8688 | 1.2131 | -71.3974 | 49.7955 | -71.8506 | -71.8277 | -71.4478 | -2.3117 | -72.2992 | 49.6445 | 49.6033 | -71.933 | -72.1161 | 0.091553 | 0.11444 | 0.07782 | 121.8109 | 0.54474 | 0.4303 | -0.11902 | 0.009156 | -0.17395 | -0.073242 | 0.49438 | -0.35706 | -0.1831 | -0.11444 | 121.7377 | 121.5408 | 73.1552 | -121.5454 | 121.5866 | 121.5454 | 69.6304 | -121.8338
1437.7031 | 121.8613 | -71.4249 | 50.2121 | 0.025635 | 0.024765 | 0.08938 | 0.065992 | 0.13699 | 0.0044454 | 0.0009528 | 0.10559 | -0.0056332 | 0.062944 | 0.073595 | 0.0061587 | -0.0081027 | 50.1022 | 50.2625 | -1.0162 | -71.1273 | 50.1755 | -71.434 | -71.3745 | -70.8527 | -2.3254 | -71.6446 | 50.235 | 50.2304 | -71.3242 | -71.4569 | -0.009155 | 0.050354 | -0.036621 | 121.6873 | 0.29755 | 0.24719 | -0.10986 | 0.10071 | -0.032043 | 0.022888 | 0.5722 | -0.21973 | -0.18768 | 0.018311 | 121.6003 | 121.5271 | 70.4086 | -121.5866 | 121.6599 | 121.6553 | 69.0994 | -121.669
1439.3906 | 121.843 | -71.4523 | 50.2121 | -0.25665 | 0.022843 | 0.091516 | 0.073469 | 0.13892 | -0.0036722 | -0.000329 | -0.12329 | -0.008624 | 0.064226 | 0.0721 | -0.00024989 | -0.010025 | 50.0656 | 50.322 | -1.6479 | -71.0953 | 50.1022 | -71.489 | -71.4569 | -70.9579 | -2.3026 | -71.6858 | 50.1068 | 50.0885 | -71.4523 | -71.5897 | -0.036621 | -0.004577 | -0.10986 | 121.7743 | 0.35706 | 0.36163 | -0.14648 | 0 | -0.13733 | -0.10529 | 0.49438 | -0.23346 | -0.09613 | -0.1236 | 121.5546 | 121.5179 | 69.8044 | -121.669 | 121.5591 | 121.5408 | 69.1498 | -121.8018
1441.1406 | 121.8658 | -72.5784 | 49.0768 | 0.040894 | 0.021561 | 0.08938 | 0.065351 | 0.1355 | 0.0042318 | 0.0026618 | 0.067444 | -0.0049924 | 0.060594 | 0.075731 | 0.0061587 | -0.01088 | 48.848 | 49.0448 | -0.72327 | -72.2809 | 48.9716 | -72.6562 | -72.6059 | -72.1527 | -2.9434 | -72.9218 | 48.967 | 48.9441 | -72.5922 | -72.7386 | -0.07782 | -0.027466 | -0.10528 | 121.6232 | 0.29755 | 0.32501 | -0.22888 | -0.013733 | -0.16022 | -0.10986 | 0.42572 | -0.34332 | -0.18311 | -0.13275 | 121.55 | 121.4264 | 71.8552 | -121.6827 | 121.5454 | 121.5225 | 69.635 | -121.8155
1442.8438 | 121.9437 | -72.8165 | 48.7518 | 0.14008 | 0.022629 | 0.089166 | 0.070051 | 0.13614 | -0.00068138 | 0.0011664 | 0.25055 | -0.007556 | 0.064012 | 0.074236 | 0.00081811 | -0.0081027 | 48.5138 | 48.7839 | -2.3666 | -72.6151 | 48.4955 | -73.0316 | -72.9904 | -72.3679 | -3.0945 | -73.0362 | 48.555 | 48.5596 | -72.8622 | -72.9996 | -0.21515 | -0.17395 | -0.25635 | 121.6003 | 0.20142 | 0.37537 | -0.23804 | -0.045777 | -0.18311 | -0.19684 | 0.44861 | -0.21973 | -0.036621 | -0.19226 | 121.3119 | 121.3303 | 70.4498 | -121.7422 | 121.3715 | 121.376 | 69.722 | -121.7514
1444.6094 | 121.9757 | -72.7844 | 48.8113 | 0.15533 | 0.021988 | 0.092584 | 0.065992 | 0.1387 | 0.001882 | 9.8198e-05 | 0.2124 | -0.0064878 | 0.061876 | 0.074023 | 0.0040225 | -0.0093845 | 48.674 | 48.8937 | -5.04 | -72.4457 | 48.7335 | -72.8302 | -72.8119 | -72.1985 | -3.1998 | -73.0133 | 48.7335 | 48.6923 | -72.7844 | -72.9172 | -0.045776 | -0.027466 | -0.077819 | 121.6782 | 0.33875 | 0.36621 | -0.13733 | 0 | -0.13275 | -0.077819 | 0.58594 | -0.22888 | -0.096131 | -0.11902 | 121.5179 | 121.4584 | 67.7444 | -121.6232 | 121.5179 | 121.4767 | 69.5847 | -121.7285
1446.3594 | 121.8567 | -73.1003 | 48.5596 | -0.24902 | 0.023056 | 0.092798 | 0.071333 | 0.1355 | -0.0019632 | 0.00138 | -0.085144 | -0.0077696 | 0.064012 | 0.074236 | 0.0014591 | -0.0093845 | 48.2391 | 48.5001 | -4.7333 | -72.7982 | 48.3398 | -73.2239 | -73.1552 | -72.5327 | -3.186 | -73.3063 | 48.4909 | 48.4634 | -73.0911 | -73.2422 | -0.1236 | -0.054931 | -0.21973 | 121.6003 | 0.30212 | 0.35706 | -0.32043 | 0.009156 | -0.14191 | -0.068664 | 0.56763 | -0.20599 | -0.064087 | -0.09613 | 121.4401 | 121.3394 | 68.367 | -121.7148 | 121.5912 | 121.5637 | 69.9142 | -121.8018
1448.0469 | 121.9757 | -73.8007 | 47.7859 | 0.10193 | 0.020279 | 0.090662 | 0.068769 | 0.13464 | 0.0020956 | 0.0026618 | 0.18188 | -0.006915 | 0.061662 | 0.075091 | 0.0053043 | -0.0095981 | 47.6303 | 47.8455 | -4.4952 | -73.4573 | 47.7493 | -73.8831 | -73.8281 | -73.2468 | -3.7445 | -74.0753 | 47.7264 | 47.6944 | -73.8052 | -73.9655 | -0.082398 | -0.027466 | -0.036621 | 121.6461 | 0.34332 | 0.37079 | -0.15564 | -0.004578 | -0.16479 | -0.05951 | 0.55389 | -0.27466 | -0.10986 | -0.091553 | 121.55 | 121.431 | 69.3054 | -121.6141 | 121.5271 | 121.4951 | 70.0562 | -121.7514
1449.7812 | 121.9208 | -74.1531 | 47.4426 | 0.048523 | 0.017929 | 0.093652 | 0.065992 | 0.13443 | -0.0030314 | 0.0020208 | 0.16663 | -0.0096922 | 0.062517 | 0.071032 | 0.0012455 | -0.0089573 | 46.8704 | 47.1313 | -4.3259 | -74.263 | 46.8292 | -74.7437 | -74.6841 | -74.1669 | -4.2023 | -74.9817 | 46.7834 | 46.7239 | -74.7253 | -74.8764 | -0.59051 | -0.53101 | -0.6134 | 121.2845 | -0.10986 | 0.42114 | -0.57221 | -0.5722 | -0.72327 | -0.65918 | -0.013733 | -0.82855 | -0.10529 | -0.71869 | 120.9824 | 121.0236 | 69.8273 | -122.1268 | 120.9366 | 120.8771 | 69.9509 | -122.319
1451.5312 | 121.9757 | -74.8077 | 46.756 | -0.14221 | 0.021347 | 0.095789 | 0.07176 | 0.134 | -0.0038858 | 0.0003118 | 0.014038 | -0.0096922 | 0.060808 | 0.072741 | 0.00081811 | -0.0091709 | 46.6827 | 46.9803 | -5.1132 | -74.3546 | 46.7011 | -74.8627 | -74.8123 | -74.1486 | -4.0192 | -74.9725 | 46.6782 | 46.6324 | -74.794 | -74.9817 | -0.054932 | -0.004578 | -0.054931 | 121.788 | 0.45319 | 0.45776 | -0.073242 | 0.013733 | -0.17395 | -0.077819 | 0.65918 | -0.16479 | 0.009155 | -0.1236 | 121.5088 | 121.4905 | 69.6945 | -121.5683 | 121.4859 | 121.4401 | 70.7886 | -121.7377
1453.2344 | 121.8292 | -75.9567 | 45.694 | 0.0027468 | 0.024552 | 0.093011 | 0.063856 | 0.13657 | 0.0055136 | 0.004798 | 0.044556 | -0.0037106 | 0.062089 | 0.074236 | 0.0065859 | -0.011948 | 45.52 | 45.7306 | -4.7607 | -75.5173 | 45.6024 | -76.0025 | -75.9705 | -75.3845 | -4.8431 | -76.2405 | 45.6345 | 45.5887 | -75.9338 | -76.0986 | -0.045776 | -0.013733 | -0.091553 | 121.6873 | 0.43945 | 0.45319 | -0.17395 | 0.022888 | -0.14191 | -0.05951 | 0.5722 | -0.28381 | -0.14191 | -0.10529 | 121.5591 | 121.4767 | 71.196 | -121.6644 | 121.5912 | 121.5454 | 71.1136 | -121.7926
1454.9844 | 121.9437 | -76.0483 | 45.5521 | -0.14984 | 0.02327 | 0.093439 | 0.069838 | 0.13934 | -0.004954 | 0.0022346 | -0.077515 | -0.008624 | 0.064653 | 0.075091 | 0.00060451 | -0.0087435 | 45.4056 | 45.694 | -3.6484 | -75.5905 | 45.3918 | -76.1673 | -76.1261 | -75.4532 | -4.7516 | -76.2726 | 45.3598 | 45.3461 | -76.1215 | -76.2497 | -0.11902 | -0.07782 | -0.16022 | 121.7422 | 0.45776 | 0.53558 | -0.14648 | -0.073242 | -0.20142 | -0.19226 | 0.59509 | -0.2243 | -0.022888 | -0.20599 | 121.4401 | 121.4539 | 72.3999 | -121.6782 | 121.4081 | 121.3943 | 71.2967 | -121.8018
1456.7344 | 121.8613 | -76.712 | 44.8975 | -0.096436 | 0.024979 | 0.093439 | 0.06706 | 0.13678 | 0.0038046 | 0.0041572 | -0.077515 | -0.0047788 | 0.060808 | 0.074023 | 0.0059451 | -0.0093845 | 44.6915 | 44.9615 | -4.7562 | -76.2955 | 44.7235 | -76.8677 | -76.7944 | -76.3046 | -5.3741 | -77.1973 | 44.632 | 44.6136 | -76.8585 | -77.0279 | -0.15564 | -0.082398 | -0.17395 | 121.6736 | 0.41656 | 0.49896 | -0.20599 | -0.14648 | -0.31586 | -0.2655 | 0.40741 | -0.48523 | -0.16937 | -0.28381 | 121.4355 | 121.4035 | 71.9559 | -121.6919 | 121.344 | 121.3257 | 71.3379 | -121.9254
1458.4688 | 121.9711 | -77.1973 | 44.3802 | -0.027771 | 0.02092 | 0.094293 | 0.069838 | 0.13785 | -0.0023904 | 0.0003118 | 0.097962 | -0.008624 | 0.06273 | 0.072954 | -0.00024989 | -0.0076755 | 44.2154 | 44.4946 | -2.9526 | -76.6937 | 44.2795 | -77.2888 | -77.2202 | -76.5472 | -5.5115 | -77.3804 | 44.3115 | 44.2841 | -77.2018 | -77.3529 | -0.091552 | -0.022888 | -0.10071 | 121.6919 | 0.50354 | 0.52643 | -0.16479 | -0.004577 | -0.15564 | -0.068665 | 0.65002 | -0.1831 | -0.027466 | -0.09613 | 121.4767 | 121.4127 | 74.2447 | -121.6003 | 121.5088 | 121.4813 | 71.6858 | -121.7331
1460.1719 | 121.8887 | -76.4053 | 45.2454 | -0.15747 | 0.025406 | 0.094507 | 0.069197 | 0.13571 | 0.0044454 | 0.0056524 | -0.092773 | -0.0067014 | 0.065721 | 0.074236 | 0.0040225 | -0.01088 | 45.0897 | 45.3232 | -3.9047 | -75.8606 | 45.1538 | -76.4465 | -76.3962 | -75.7416 | -5.4428 | -76.6251 | 45.163 | 45.1309 | -76.4099 | -76.5472 | -0.041199 | 0.009155 | -0.091552 | 121.7285 | 0.54474 | 0.53558 | -0.15564 | -0.004578 | -0.14191 | -0.082397 | 0.66376 | -0.21973 | -0.07782 | -0.11444 | 121.5591 | 121.4951 | 72.5006 | -121.6415 | 121.5683 | 121.5363 | 70.9625 | -121.7926
1461.875 | 121.9254 | -78.4882 | 43.0573 | -0.21088 | 0.026261 | 0.095575 | 0.070906 | 0.134 | 0.0025228 | 0.0024482 | -0.10803 | -0.0062742 | 0.065721 | 0.07445 | 0.0023135 | -0.010453 | 43.8538 | 44.0872 | -1.8219 | -77.5406 | 43.8217 | -77.9022 | -77.774 | -76.8539 | -5.7999 | -77.774 | 43.9911 | 43.8538 | -77.6962 | -77.8061 | 0.58594 | 0.71411 | 0.76447 | 122.5754 | 0.94757 | 0.23346 | 0.79651 | 0.79193 | 0.68207 | 0.93384 | 1.6342 | 0.71411 | 0.032043 | 0.79651 | 122.3099 | 122.3419 | 76.6663 | -120.8313 | 122.4792 | 122.3419 | 72.6883 | -120.8633
1463.6406 | 121.8979 | -77.33 | 44.2841 | -0.17273 | 0.024552 | 0.095148 | 0.069838 | 0.13699 | 0.0044454 | 0.0037298 | -0.1004 | -0.0079832 | 0.062303 | 0.074023 | 0.0035953 | -0.0089573 | 44.1193 | 44.3848 | -2.7237 | -76.6663 | 44.2017 | -77.417 | -77.3621 | -76.6434 | -5.9784 | -77.5635 | 44.2383 | 44.1788 | -77.3026 | -77.504 | -0.086975 | -0.032044 | -0.082398 | 121.7148 | 0.66376 | 0.6958 | -0.1648 | 0.027466 | -0.17395 | -0.045777 | 0.68664 | -0.23346 | -0.05951 | -0.10529 | 121.5317 | 121.4493 | 74.6063 | -121.6461 | 121.5683 | 121.5088 | 71.3516 | -121.788
1465.3438 | 121.9849 | -77.9205 | 43.6203 | 0.10193 | 0.022415 | 0.098566 | 0.066633 | 0.13785 | 0.0012412 | 0.0060798 | 0.20477 | -0.0071286 | 0.062303 | 0.074663 | 0.0057315 | -0.0095981 | 43.4647 | 43.7347 | -2.6505 | -77.3895 | 43.602 | -77.9846 | -77.9663 | -77.2751 | -6.5277 | -78.2181 | 43.5699 | 43.5059 | -77.98 | -78.1036 | -0.064087 | -0.045777 | -0.01831 | 121.6553 | 0.53101 | 0.57678 | -0.15564 | -0.05951 | -0.18311 | -0.050354 | 0.64545 | -0.29755 | -0.11444 | -0.11444 | 121.5225 | 121.3852 | 75.2701 | -121.5866 | 121.4905 | 121.4264 | 71.3928 | -121.7239
1467.0781 | 121.8201 | -78.1082 | 43.5425 | -0.0354 | 0.025406 | 0.098779 | 0.067701 | 0.13849 | 0.0038046 | 0.0073614 | 0.029297 | -0.0039244 | 0.064653 | 0.072314 | 0.0076541 | -0.0093845 | 43.3456 | 43.6157 | -3.1769 | -77.4307 | 43.4326 | -78.1998 | -78.1174 | -77.4399 | -6.7062 | -78.3875 | 43.483 | 43.4006 | -78.1128 | -78.2822 | -0.091553 | -0.009156 | -0.10986 | 121.7239 | 0.67749 | 0.68665 | -0.19684 | -0.004578 | -0.17395 | -0.059509 | 0.66833 | -0.27924 | -0.10528 | -0.14191 | 121.5408 | 121.4539 | 74.9313 | -121.6599 | 121.5912 | 121.5088 | 71.402 | -121.8246
1468.7656 | 121.9025 | -78.273 | 43.3594 | -0.14984 | 0.021134 | 0.098566 | 0.068556 | 0.13806 | 0.0025228 | 0.0080024 | -0.077515 | -0.005847 | 0.062303 | 0.075731 | 0.0027407 | -0.0085299 | 43.19 | 43.4509 | -2.5726 | -77.5406 | 43.2861 | -78.3279 | -78.2776 | -77.5589 | -6.7429 | -78.4927 | 43.2724 | 43.2495 | -78.2547 | -78.4332 | -0.054932 | -0.004578 | -0.073242 | 121.7239 | 0.73242 | 0.737 | -0.16937 | 0.01831 | -0.16022 | -0.086975 | 0.71411 | -0.21973 | -0.059509 | -0.10986 | 121.5591 | 121.463 | 75.7004 | -121.637 | 121.5454 | 121.5225 | 71.5302 | -121.7926
1470.4844 | 121.8246 | -78.3829 | 43.2724 | -0.25665 | 0.022843 | 0.1007 | 0.072828 | 0.13721 | -0.0021768 | 0.0041572 | -0.11566 | -0.0062742 | 0.062944 | 0.07445 | -0.0015317 | -0.0087435 | 43.0527 | 43.3136 | -3.0212 | -77.6505 | 43.1625 | -78.4149 | -78.3691 | -77.6916 | -6.8665 | -78.6209 | 43.19 | 43.1534 | -78.4058 | -78.5385 | -0.032043 | 0.013733 | -0.10986 | 121.6965 | 0.73242 | 0.71869 | -0.21973 | -0.022888 | -0.15564 | -0.082398 | 0.69122 | -0.23804 | -0.082398 | -0.11902 | 121.5454 | 121.4355 | 75.3616 | -121.6415 | 121.5729 | 121.5363 | 71.5164 | -121.8109
1472.2031 | 121.843 | -77.124 | 44.5541 | -0.073547 | 0.022629 | 0.09942 | 0.066847 | 0.13892 | 0.0065818 | 0.008216 | -0.0012209 | -0.0067014 | 0.063585 | 0.075091 | 0.0057315 | -0.010666 | 44.1696 | 44.2429 | -3.0167 | -76.7303 | 44.0964 | -77.5681 | -77.5543 | -76.712 | -6.6422 | -77.8198 | 44.0552 | 44.0048 | -77.5269 | -77.6688 | -0.44403 | -0.4303 | -0.45776 | 121.3669 | 0.39368 | 0.82397 | -0.38452 | -0.40283 | -0.54474 | -0.49896 | 0.41199 | -0.6958 | -0.15106 | -0.54932 | 121.2204 | 121.2936 | 74.1074 | -122.1085 | 121.1792 | 121.1288 | 70.4819 | -122.2229
1473.9219 | 121.8384 | -77.9572 | 43.6844 | -0.21088 | 0.020066 | 0.10156 | 0.070692 | 0.13956 | -0.0036722 | 0.0037298 | -0.092773 | -0.0071286 | 0.062517 | 0.073595 | -0.00089089 | -0.0095981 | 43.5059 | 43.8171 | -2.4216 | -77.1744 | 43.5471 | -78.0075 | -77.9617 | -77.2202 | -6.7154 | -78.1631 | 43.5837 | 43.5791 | -77.9388 | -78.1036 | -0.050354 | -0.004578 | -0.13733 | 121.7743 | 0.78278 | 0.78735 | -0.17853 | 0.01831 | -0.14648 | -0.10071 | 0.737 | -0.20599 | -0.059509 | -0.10529 | 121.5042 | 121.463 | 75.5356 | -121.6461 | 121.5408 | 121.5363 | 71.2418 | -121.788
1475.6562 | 121.9528 | -78.1586 | 43.4052 | 0.13245 | 0.020493 | 0.1022 | 0.068129 | 0.13828 | 0.00081382 | 0.0045844 | 0.28107 | -0.0067014 | 0.061876 | 0.075091 | 0.0031681 | -0.0093845 | 43.3182 | 43.602 | -3.2272 | -77.3438 | 43.364 | -78.1631 | -78.1265 | -77.3621 | -6.9626 | -78.3691 | 43.3044 | 43.2816 | -78.1586 | -78.2867 | -0.004578 | 0.032043 | -0.041198 | 121.7606 | 0.81482 | 0.78278 | -0.086975 | 0 | -0.12817 | -0.10071 | 0.79651 | -0.21057 | -0.082398 | -0.1236 | 121.5225 | 121.4767 | 74.9313 | -121.5317 | 121.463 | 121.4401 | 71.196 | -121.6919
1477.3594 | 121.875 | -77.5452 | 44.1101 | -0.24139 | 0.023697 | 0.10412 | 0.071974 | 0.13849 | 0.0012412 | 0.0071478 | -0.13855 | -0.0079832 | 0.062517 | 0.074663 | 0.0012455 | -0.010239 | 43.5699 | 43.8354 | -0.89722 | -77.1194 | 43.721 | -77.9205 | -77.8702 | -77.1378 | -6.9168 | -78.1082 | 43.7119 | 43.721 | -77.8427 | -77.9938 | -0.37537 | -0.32501 | -0.3891 | 121.3806 | 0.42572 | 0.75073 | -0.54016 | -0.29755 | -0.44861 | -0.39825 | 0.40741 | -0.56305 | -0.11444 | -0.3891 | 121.2662 | 121.1151 | 76.6479 | -121.9803 | 121.257 | 121.2662 | 70.6284 | -122.1039
1479.0625 | 121.9757 | -77.124 | 44.4626 | -0.15747 | 0.023697 | 0.10348 | 0.071333 | 0.13849 | -0.0017496 | 0.005866 | 0.036926 | -0.007556 | 0.063798 | 0.073168 | -0.0019589 | -0.010453 | 44.2154 | 44.5496 | -3.6987 | -76.3367 | 44.2841 | -77.2247 | -77.1378 | -76.2863 | -6.665 | -77.243 | 44.3527 | 44.3298 | -77.1103 | -77.2797 | -0.10071 | -0.013733 | -0.17853 | 121.6736 | 0.78735 | 0.80109 | -0.24719 | 0.013732 | -0.15564 | -0.10986 | 0.83771 | -0.11902 | 0.036621 | -0.13275 | 121.4081 | 121.3394 | 73.4253 | -121.6003 | 121.4767 | 121.4539 | 70.459 | -121.7422
1480.8125 | 121.8246 | -76.3412 | 45.3461 | -0.18036 | 0.021561 | 0.10604 | 0.069624 | 0.1402 | 0.0010276 | 0.007575 | -0.10803 | -0.0092648 | 0.061449 | 0.074023 | 0.0038089 | -0.010239 | 45.2087 | 45.4971 | -3.0533 | -75.2472 | 45.2316 | -76.2909 | -76.2497 | -75.4669 | -6.3995 | -76.4465 | 45.2499 | 45.2408 | -76.2405 | -76.4145 | 0.050354 | 0.091553 | -0.11444 | 121.8384 | 1.0941 | 1.0025 | -0.13733 | 0.10071 | -0.073242 | -0.09613 | 0.87433 | -0.10529 | -0.032043 | -0.10529 | 121.5729 | 121.55 | 73.288 | -121.5958 | 121.5912 | 121.582 | 69.9417 | -121.7606
1482.5938 | 121.8796 | -76.8723 | 44.7281 | 0.071411 | 0.022202 | 0.10369 | 0.065351 | 0.14084 | 0.0065818 | 0.0080024 | 0.13611 | -0.0071286 | 0.063371 | 0.073809 | 0.0063723 | -0.0085299 | 44.664 | 44.9203 | -3.1036 | -75.9338 | 44.8242 | -76.7944 | -76.7441 | -75.9842 | -6.8024 | -77.0966 | 44.7968 | 44.751 | -76.8036 | -76.9684 | 0.077819 | 0.12817 | 0.096131 | 121.7926 | 0.93842 | 0.81024 | -0.064087 | 0.068664 | -0.096131 | 0.068665 | 0.88806 | -0.22431 | -0.12817 | 0.022889 | 121.6965 | 121.5363 | 73.7686 | -121.4722 | 121.669 | 121.6232 | 70.0699 | -121.6965
1484.2969 | 121.8933 | -76.918 | 44.6777 | -0.20325 | 0.024765 | 0.10754 | 0.070906 | 0.14404 | -0.00068138 | 0.0054388 | -0.039368 | -0.0084104 | 0.061876 | 0.073168 | 0.0018863 | -0.0081027 | 44.5862 | 44.902 | -1.4694 | -75.9384 | 44.5816 | -76.9318 | -76.8951 | -76.0391 | -6.6467 | -77.0691 | 44.6091 | 44.5724 | -76.8997 | -77.0416 | -0.013733 | 0.022888 | -0.09613 | 121.8201 | 0.97961 | 0.95673 | -0.091552 | 0.018311 | -0.1236 | -0.068664 | 0.87891 | -0.15106 | -0.027466 | -0.10529 | 121.4996 | 121.5042 | 75.4486 | -121.5729 | 121.5271 | 121.4905 | 70.2713 | -121.7194
1486.0469 | 121.8842 | -77.3209 | 44.2841 | -0.19562 | 0.021134 | 0.11117 | 0.069624 | 0.13956 | 0.010641 | 0.0080024 | -0.11566 | -0.0073422 | 0.062089 | 0.075304 | 0.0044497 | -0.010025 | 44.1742 | 44.4077 | -0.43945 | -75.705 | 44.3024 | -77.3209 | -77.2888 | -76.474 | -7.0587 | -77.5543 | 44.2474 | 44.2291 | -77.2842 | -77.4399 | 0 | 0.032044 | 0.01831 | 121.7285 | 1.6159 | 1.5839 | -0.10986 | 0.036621 | -0.11902 | -0.036621 | 0.84686 | -0.23346 | -0.11444 | -0.054932 | 121.6232 | 121.4951 | 76.8814 | -121.5729 | 121.5683 | 121.55 | 70.2621 | -121.7239
1487.7344 | 121.962 | -77.1103 | 44.4489 | -0.027771 | 0.019638 | 0.11202 | 0.069624 | 0.14468 | 0.0055136 | 0.007575 | 0.15137 | -0.0094786 | 0.061021 | 0.071459 | 0.0012455 | -0.0059665 | 44.458 | 44.7601 | -0.31586 | -75.2747 | 44.5221 | -77.0187 | -76.9455 | -76.0483 | -6.839 | -77.1011 | 44.5724 | 44.5633 | -76.9226 | -77.0966 | 0.091553 | 0.16479 | 0.073242 | 121.8704 | 1.8356 | 1.6708 | 0.009155 | 0.18768 | 0.013733 | 0.1236 | 1.062 | 0.009156 | -0.004577 | 0.11444 | 121.6324 | 121.5683 | 76.7944 | -121.3943 | 121.6827 | 121.6736 | 70.2713 | -121.5454
1489.4062 | 121.8567 | -77.2797 | 44.3481 | 0.056152 | 0.022843 | 0.11138 | 0.068129 | 0.14597 | 0.0091452 | 0.0073614 | 0.159 | -0.0037106 | 0.062944 | 0.073595 | 0.0080813 | -0.0085299 | 44.101 | 44.3161 | 1.0025 | -75.8926 | 44.2612 | -77.3712 | -77.3254 | -76.4511 | -7.1182 | -77.5864 | 44.2795 | 44.2383 | -77.2934 | -77.4582 | -0.091553 | -0.045776 | -0.086976 | 121.5958 | 1.387 | 1.4328 | -0.24719 | -0.013733 | -0.17853 | -0.068665 | 0.82855 | -0.3067 | -0.12817 | -0.10986 | 121.5408 | 121.3806 | 78.2822 | -121.6736 | 121.5591 | 121.5179 | 70.1614 | -121.8063
1491.0938 | 121.8796 | -77.0462 | 44.5908 | -0.17273 | 0.024979 | 0.11331 | 0.071547 | 0.14511 | 0.0093588 | 0.012061 | -0.085144 | -0.005206 | 0.06273 | 0.072954 | 0.0018863 | -0.0076755 | 44.4077 | 44.6411 | 3.7354 | -75.5402 | 44.5084 | -77.1057 | -77.0828 | -76.1398 | -6.839 | -77.2751 | 44.4946 | 44.4855 | -77.0142 | -77.1744 | -0.059509 | -0.036621 | -0.082397 | 121.6873 | 1.506 | 1.5427 | -0.1831 | 0.032044 | -0.12817 | -0.09613 | 0.90637 | -0.22888 | -0.10071 | -0.10528 | 121.5546 | 121.4539 | 80.7816 | -121.6736 | 121.5408 | 121.5317 | 70.2072 | -121.7651
1492.7656 | 121.843 | -76.918 | 44.7418 | -0.18036 | 0.023056 | 0.11672 | 0.075819 | 0.14618 | 0.0025228 | 0.009925 | -0.085144 | -0.011401 | 0.06508 | 0.076159 | -0.0013181 | -0.0098117 | 44.545 | 44.8425 | 0.5127 | -75.4669 | 44.5724 | -76.9684 | -76.8951 | -75.9705 | -6.7154 | -77.1103 | 44.5816 | 44.5908 | -76.9135 | -77.0599 | -0.050354 | 0.022888 | -0.16937 | 121.7606 | 1.4511 | 1.4282 | -0.19684 | 0.004578 | -0.14191 | -0.16022 | 0.94757 | -0.19226 | -0.050354 | -0.15106 | 121.4905 | 121.463 | 77.4307 | -121.637 | 121.4996 | 121.5088 | 70.2026 | -121.8018
1494.4531 | 121.962 | -75.4349 | 46.1792 | 0.12482 | 0.022415 | 0.11501 | 0.068129 | 0.14533 | 0.0078634 | 0.01142 | 0.22766 | -0.0071286 | 0.061235 | 0.075091 | 0.0057315 | -0.0081027 | 46.0373 | 46.312 | 3.9368 | -73.8922 | 46.0602 | -75.4715 | -75.4486 | -74.4415 | -6.0699 | -75.6134 | 46.0602 | 46.0327 | -75.4486 | -75.5814 | -0.036622 | -0.013733 | -0.11902 | 121.7468 | 1.5427 | 1.5564 | -0.14191 | -0.013733 | -0.14648 | -0.11902 | 0.99335 | -0.17853 | -0.032043 | -0.14648 | 121.4951 | 121.4722 | 79.3716 | -121.6278 | 121.4951 | 121.4676 | 69.3649 | -121.7606
1496.1406 | 121.875 | -72.8622 | 48.793 | -0.18036 | 0.025406 | 0.11053 | 0.078383 | 0.14618 | 0.01235 | 0.010139 | -0.14618 | -0.0071286 | 0.063798 | 0.075945 | 0.0033817 | -0.011094 | 48.5596 | 48.793 | 2.4307 | -70.8389 | 48.6832 | -72.9309 | -72.8714 | -71.9604 | -4.953 | -73.1461 | 48.6649 | 48.6328 | -72.8714 | -73.0362 | -0.068664 | -0.009155 | -0.10986 | 121.6553 | 2.0233 | 2.0325 | -0.23346 | -0.009155 | -0.17395 | -0.12817 | 0.9018 | -0.28381 | -0.10986 | -0.16022 | 121.5454 | 121.4218 | 75.293 | -121.6644 | 121.5271 | 121.4951 | 67.9092 | -121.8292
1497.8281 | 121.843 | -71.9238 | 49.7314 | -0.22614 | 0.022202 | 0.11138 | 0.077742 | 0.14383 | 0.0093588 | 0.013557 | -0.14618 | -0.005847 | 0.064012 | 0.073168 | 0.0033817 | -0.0087435 | 49.4522 | 49.7726 | 4.866 | -69.754 | 49.617 | -71.965 | -71.9193 | -71.022 | -4.5273 | -72.1848 | 49.6628 | 49.6124 | -71.9284 | -72.0749 | -0.041199 | 0.004578 | -0.11444 | 121.6965 | 2.1698 | 2.1652 | -0.27924 | -0.004578 | -0.15106 | -0.068664 | 0.90179 | -0.26093 | -0.10986 | -0.11902 | 121.5408 | 121.376 | 76.7899 | -121.6507 | 121.5866 | 121.5363 | 67.3965 | -121.8063
1499.5781 | 121.8155 | -71.3562 | 50.2625 | -0.088806 | 0.024124 | 0.10967 | 0.076246 | 0.14511 | 0.015981 | 0.012916 | -0.024109 | -0.0054196 | 0.063798 | 0.075091 | 0.0035953 | -0.0095981 | 50.1343 | 50.3723 | 4.9667 | -68.8705 | 50.2075 | -71.3791 | -71.3425 | -70.3949 | -4.3167 | -71.608 | 50.1755 | 50.1526 | -71.3425 | -71.521 | -0.022888 | 0.013733 | -0.054931 | 121.7285 | 2.4857 | 2.4719 | -0.12817 | 0.013733 | -0.16479 | -0.086975 | 0.9613 | -0.25177 | -0.086975 | -0.10986 | 121.5637 | 121.4905 | 76.3229 | -121.6049 | 121.5317 | 121.5088 | 67.0395 | -121.7834
1501.2656 | 121.8338 | -71.5988 | 50.0427 | -0.19562 | 0.024552 | 0.11309 | 0.082228 | 0.14597 | 0.008718 | 0.010566 | -0.077515 | -0.0090512 | 0.063798 | 0.073809 | -0.00024989 | -0.0076755 | 49.8413 | 50.1709 | 7.196 | -69.1772 | 49.8642 | -71.6583 | -71.608 | -70.6009 | -4.3991 | -71.7911 | 49.8962 | 49.8779 | -71.6217 | -71.7545 | -0.059509 | -0.009155 | -0.17853 | 121.7697 | 2.4216 | 2.4307 | -0.20142 | -0.022888 | -0.15564 | -0.14648 | 0.99792 | -0.19226 | -0.036621 | -0.16479 | 121.463 | 121.4401 | 78.7949 | -121.6507 | 121.4951 | 121.4767 | 67.1997 | -121.7972
1503.0156 | 121.9116 | -71.1823 | 50.3998 | 0.15533 | 0.021347 | 0.11309 | 0.077742 | 0.14682 | 0.013845 | 0.012916 | 0.23529 | -0.0045652 | 0.061449 | 0.073809 | 0.0018863 | -0.010453 | 50.2853 | 50.5692 | 7.1365 | -68.4814 | 50.2762 | -71.2006 | -71.1594 | -70.1111 | -4.3396 | -71.3562 | 50.2808 | 50.267 | -71.1731 | -71.3242 | -0.018311 | 0.022888 | -0.1236 | 121.7514 | 2.7008 | 2.6779 | -0.11444 | 0.009155 | -0.14191 | -0.11902 | 1.0712 | -0.17395 | -0.032043 | -0.13275 | 121.4584 | 121.4676 | 78.3188 | -121.5591 | 121.463 | 121.4493 | 66.8427 | -121.7239
1504.8281 | 121.8338 | -70.3308 | 51.3062 | -0.18799 | 0.020493 | 0.11523 | 0.080732 | 0.15195 | 0.012777 | 0.0084296 | -0.054626 | -0.007556 | 0.061662 | 0.072954 | 0.0016727 | -0.010239 | 51.2009 | 51.4847 | 6.514 | -67.4606 | 51.2192 | -70.3125 | -70.285 | -69.2139 | -3.9001 | -70.4773 | 51.1963 | 51.1917 | -70.3079 | -70.4361 | 0.018311 | 0.045777 | -0.086975 | 121.8155 | 2.8702 | 2.8244 | -0.10528 | 0.022889 | -0.10529 | -0.10986 | 1.1169 | -0.14648 | -0.041199 | -0.11444 | 121.55 | 121.5317 | 76.8448 | -121.5912 | 121.5271 | 121.5225 | 66.4307 | -121.7422
1506.5781 | 121.9208 | -69.1635 | 52.446 | 0.010376 | 0.021134 | 0.11352 | 0.077742 | 0.14703 | 0.011922 | 0.0069342 | 0.13611 | -0.0064878 | 0.062303 | 0.071673 | 0.0033817 | -0.0068209 | 52.3911 | 52.6016 | 6.0379 | -66.4398 | 52.3956 | -69.1315 | -69.1132 | -68.0237 | -3.511 | -69.3054 | 52.4277 | 52.3682 | -69.0948 | -69.2505 | 0.032043 | 0.050354 | -0.050354 | 121.7651 | 2.7237 | 2.6733 | -0.054932 | 0.068664 | -0.086975 | -0.018311 | 1.1398 | -0.14191 | -0.054932 | -0.07782 | 121.5591 | 121.5546 | 75.2014 | -121.5591 | 121.5912 | 121.5317 | 65.6525 | -121.6965
1508.3438 | 121.9162 | -69.6991 | 51.8921 | 0.010376 | 0.018784 | 0.11843 | 0.080305 | 0.15045 | 0.015981 | 0.011634 | 0.12085 | -0.0079832 | 0.062303 | 0.072527 | 0.0029543 | -0.0093845 | 51.7227 | 51.9745 | 6.4957 | -66.9434 | 51.7868 | -69.722 | -69.7174 | -68.6234 | -3.772 | -69.9326 | 51.7776 | 51.7685 | -69.6854 | -69.8685 | -0.022888 | -0.01831 | -0.10529 | 121.6736 | 2.7557 | 2.774 | -0.16937 | 0.013733 | -0.16937 | -0.11444 | 1.0757 | -0.23346 | -0.064087 | -0.1236 | 121.4859 | 121.4218 | 76.1948 | -121.6095 | 121.4767 | 121.4676 | 65.9271 | -121.7606
1510.0938 | 121.8979 | -69.9326 | 51.6541 | 0.10956 | 0.019425 | 0.11715 | 0.078169 | 0.15302 | 0.014913 | 0.0071478 | 0.17426 | -0.0088376 | 0.061449 | 0.074663 | 0.0031681 | -0.0081027 | 51.5305 | 51.7731 | 6.7886 | -67.1768 | 51.5533 | -69.9829 | -69.9097 | -68.7927 | -4.2435 | -70.1523 | 51.5625 | 51.5442 | -69.9371 | -70.0699 | -0.050354 | 0.022888 | -0.10071 | 121.7056 | 2.7557 | 2.7328 | -0.1236 | -0.004578 | -0.13733 | -0.091553 | 1.1398 | -0.21973 | -0.082398 | -0.10986 | 121.4859 | 121.463 | 76.7212 | -121.5637 | 121.4951 | 121.4767 | 65.6891 | -121.7239
1511.7812 | 121.843 | -68.6188 | 53.0273 | -0.088806 | 0.026688 | 0.11459 | 0.08885 | 0.15665 | 0.026876 | 0.0090704 | -0.077515 | -0.0043516 | 0.062089 | 0.075091 | 0.0053043 | -0.011307 | 52.8763 | 53.0731 | 7.0679 | -65.2451 | 52.9404 | -68.6508 | -68.5913 | -67.4561 | -3.6026 | -68.866 | 52.9129 | 52.9037 | -68.6142 | -68.7607 | -0.032044 | 0.027465 | -0.086975 | 121.6919 | 3.3737 | 3.3463 | -0.15106 | 0.004577 | -0.14191 | -0.11444 | 1.1627 | -0.24719 | -0.10529 | -0.1236 | 121.5591 | 121.4951 | 75.6866 | -121.6187 | 121.5317 | 121.5225 | 65.0162 | -121.788
1513.5312 | 121.8979 | -67.2546 | 54.3137 | 0.08667 | 0.019638 | 0.12292 | 0.086287 | 0.15707 | 0.021322 | 0.010779 | 0.2124 | -0.0062742 | 0.062089 | 0.074236 | 0.0018863 | -0.0098117 | 54.2175 | 54.4876 | 5.7404 | -63.4644 | 54.1809 | -67.2958 | -67.2409 | -66.0324 | -3.0762 | -67.4469 | 54.245 | 54.2084 | -67.2043 | -67.3782 | -0.041198 | 0.013733 | -0.13275 | 121.7422 | 3.7903 | 3.7766 | -0.096131 | 0.050354 | -0.1236 | -0.068665 | 1.2222 | -0.19226 | -0.068664 | -0.10529 | 121.4355 | 121.4722 | 72.995 | -121.5546 | 121.4996 | 121.463 | 64.1785 | -121.6919
1515.2812 | 122.0078 | -83.6792 | 37.8845 | -0.065918 | 0.022202 | 0.14791 | 0.098249 | 0.16733 | 0.02474 | 0.01612 | 0.044556 | -0.0073422 | 0.064012 | 0.073809 | -0.00067729 | -0.0091709 | 38.269 | 38.562 | -1.3321 | -78.6804 | 38.2782 | -83.2626 | -83.1894 | -81.7245 | -11.3159 | -83.3313 | 38.3148 | 38.2782 | -83.2077 | -83.3496 | 0.41656 | 0.48981 | 0.39368 | 122.2412 | 4.9988 | 4.509 | 0.38452 | 0.4715 | 0.32959 | 0.4303 | 1.9547 | 0.3479 | 0.01831 | 0.39368 | 121.9574 | 121.9482 | 82.3471 | -121.0739 | 121.994 | 121.9574 | 72.3633 | -121.2341
1516.9688 | 121.7743 | -82.0908 | 39.6103 | -0.24139 | 0.026902 | 0.72897 | 0.098036 | 0.75586 | 0.027517 | 0.014838 | -0.19958 | -0.005847 | 0.064012 | 0.075518 | 0.0033817 | -0.011734 | 38.4613 | 39.2349 | 7.2235 | -78.5339 | 38.8275 | -82.782 | -82.7774 | -77.742 | -10.6842 | -82.132 | 41.2811 | 40.7913 | -80.9647 | -80.7449 | -0.69122 | -0.68665 | -0.78278 | 121.3257 | 3.5568 | 4.2435 | -1.149 | 1.1261 | 1.3458 | 1.6708 | 4.3488 | -0.041199 | -1.387 | 1.181 | 120.9183 | 120.5521 | 89.3143 | -122.3877 | 123.3719 | 122.8821 | 71.4066 | -120.3552
1518.7188 | 121.8201 | -53.4531 | 68.0649 | 0.094299 | 0.022843 | 0.98083 | 0.096327 | 1.0231 | 0.025381 | 0.017615 | 0.30396 | -0.0077696 | 0.064226 | 0.074877 | 0.0038089 | -0.0089573 | 67.8955 | 67.9138 | 34.3781 | -48.8068 | 67.8223 | -53.3661 | -53.4164 | -52.153 | 3.4103 | -53.7003 | 68.0191 | 67.9733 | -53.3981 | -53.54 | 0.086975 | 0.036621 | -0.24261 | 121.3669 | 4.6463 | 4.6097 | -0.16937 | 0.054932 | -0.086975 | -0.045776 | 1.3 | -0.24719 | -0.16022 | -0.091552 | 121.2753 | 121.3486 | 87.8311 | -121.4813 | 121.4722 | 121.4264 | 56.8634 | -121.6049
1520.4688 | 121.6736 | -64.2517 | 57.1243 | -0.1651 | 0.026902 | 1.479 | 0.10209 | 1.5264 | 0.032003 | 0.018256 | -0.092773 | -0.0039244 | 0.062944 | 0.07445 | 0.0065859 | -0.011734 | 59.2529 | 59.3994 | 25.2274 | -56.9778 | 59.3033 | -62.1002 | -62.2238 | -60.4568 | -0.95215 | -61.7706 | 59.5505 | 59.5596 | -61.6653 | -61.7157 | 2.1515 | 2.0279 | 2.179 | 123.6511 | 7.2739 | 5.246 | 2.1286 | 2.5864 | 2.536 | 2.4261 | 3.7949 | 2.4811 | -0.054932 | 2.4353 | 123.555 | 123.5046 | 89.4791 | -119.3481 | 123.8022 | 123.8113 | 63.2996 | -118.84
1522.2188 | 121.4813 | -61.4685 | 60.3378 | -0.18036 | 0.02327 | 2.2779 | 0.10573 | 2.3224 | 0.031576 | 0.008216 | -0.039368 | -0.008624 | 0.061021 | 0.07445 | 0.0033817 | -0.010453 | 59.9213 | 60.3516 | 15.2893 | -57.4036 | 59.4269 | -61.9171 | -62.0682 | -61.1984 | -1.1032 | -62.5031 | 58.9233 | 58.873 | -62.4435 | -62.6266 | -0.44861 | -0.59967 | -0.91095 | 121.8201 | 4.0649 | 4.6646 | -0.41656 | -0.97504 | -1.1581 | -1.4145 | 0.27008 | -1.0345 | 0.1236 | -1.4648 | 120.8954 | 121.3898 | 76.7578 | -122.406 | 120.3918 | 120.3415 | 60.3653 | -122.9645
1523.9062 | 121.5546 | -60.7315 | 60.5118 | -0.22614 | 0.026688 | 3.5471 | 0.11833 | 3.6396 | 0.04482 | 0.0086432 | -0.12329 | -0.0064878 | 0.065721 | 0.073382 | 0.0038089 | -0.0089573 | 58.8821 | 60.2646 | 25.8133 | -53.8651 | 59.8068 | -60.8551 | -60.965 | -60.5621 | -0.80566 | -62.1094 | 59.436 | 59.3994 | -61.8027 | -61.9171 | -0.1236 | -0.23346 | -0.70496 | 120.9961 | 6.8665 | 7.0999 | -1.6296 | -1.0712 | -1.1856 | -1.0757 | 0.16937 | -1.3779 | -0.19226 | -1.1124 | 120.5383 | 119.6136 | 86.5448 | -121.4767 | 120.1675 | 120.1309 | 59.9258 | -122.4289
1525.6406 | 121.5591 | -65.0803 | 56.0349 | 0.033264 | 0.024552 | 3.6413 | 0.11406 | 3.7867 | 0.055715 | 0.0071478 | 0.097962 | -0.0054196 | 0.063585 | 0.076586 | 0.0057315 | -0.0070345 | 55.632 | 56.2683 | 26.0605 | -56.8726 | 56.1447 | -64.3799 | -64.2563 | -62.9242 | -1.8539 | -64.682 | 56.8085 | 56.7398 | -64.4806 | -64.6454 | 0.70038 | 0.82397 | 0.10986 | 121.3486 | 8.2077 | 7.3837 | -0.40283 | 0.59967 | 0.43487 | 0.77362 | 2.1561 | 0.39825 | -0.036621 | 0.70496 | 121.225 | 120.7123 | 91.1407 | -120.2911 | 121.8887 | 121.8201 | 63.2263 | -120.6802
1527.3281 | 121.5591 | -69.7952 | 51.3474 | 0.094299 | 0.025406 | 2.6704 | 0.11406 | 2.8724 | 0.048238 | 0.021888 | 0.31921 | -0.0054196 | 0.061449 | 0.074877 | 0.0063723 | -0.0083163 | 52.8763 | 53.3661 | 3.3279 | -59.5184 | 53.4439 | -66.9113 | -66.9617 | -66.2979 | -3.0304 | -67.5842 | 53.7598 | 53.5904 | -67.6849 | -67.9138 | 2.8839 | 2.8336 | 2.0966 | 123.1613 | 10.2768 | 7.4432 | 1.5289 | 2.1103 | 1.8814 | 2.4124 | 3.4973 | 2.211 | 0.32959 | 2.243 | 123.2391 | 122.6715 | 73.1232 | -118.309 | 123.555 | 123.3856 | 66.7648 | -119.2612
1529.0781 | 121.5363 | -62.1231 | 59.0286 | 0.14771 | 0.024552 | 3.8867 | 0.12303 | 3.8904 | 0.061269 | 0.007575 | 0.31158 | -0.005206 | 0.062089 | 0.075945 | 0.0046633 | -0.0083163 | 58.3191 | 58.5846 | 31.6772 | -52.3911 | 58.7723 | -61.6745 | -61.6287 | -60.8368 | -0.51727 | -62.2696 | 59.0652 | 59.0607 | -62.0728 | -62.2147 | 0.44861 | 0.49439 | -0.25635 | 120.7077 | 9.7321 | 9.2377 | -0.70953 | 0.050354 | -0.091553 | 0.036622 | 1.2863 | -0.14648 | -0.054931 | 0.032044 | 120.8954 | 120.4422 | 93.8004 | -120.6573 | 121.1884 | 121.1838 | 61.6058 | -121.2433
1530.8125 | 121.4035 | -60.1685 | 60.9695 | 0.13245 | 0.024765 | 3.7808 | 0.12538 | 3.8365 | 0.051656 | 0.069526 | 0.22766 | -0.0064878 | 0.062517 | 0.074023 | 0.0038089 | -0.0074619 | 61.0519 | 60.8643 | 5.9555 | -49.5667 | 61.1069 | -59.079 | -58.9279 | -57.3395 | 1.5472 | -59.7473 | 61.8164 | 61.6104 | -59.285 | -59.2392 | 1.0895 | 1.2405 | 0.13733 | 121.0327 | 10.6018 | 9.3613 | 0.082398 | 0.88348 | 0.92926 | 0.84686 | 2.829 | 0.42114 | -0.50812 | 0.64087 | 121.2753 | 121.2204 | 66.124 | -119.8975 | 121.9849 | 121.7789 | 61.7157 | -120.2087
1532.5 | 121.5317 | -0.56763 | 120.8908 | 0.018005 | 0.040573 | 0.063745 | 0.0023329 | 0.054109 | -0.0038858 | 0.007575 | 0.33447 | -0.0081968 | 0.061021 | 0.071245 | 0.0014591 | -0.0074619 | -0.064087 | -0.050354 | -0.050354 | -0.45319 | 0.004578 | -0.49896 | -0.59052 | 0.54932 | 30.1117 | -0.49896 | 120.726 | 120.7077 | -0.55389 | -0.59967 | 0.068665 | -0.022888 | -120.8862 | 0.51727 | 0.11444 | 0.13733 | -120.9549 | 0.013733 | -0.032043 | -0.1648 | 1.1169 | 0.068665 | 0.10071 | -0.18311 | 0.5722 | 0.50354 | 0.51727 | -121.4813 | 121.2936 | 121.2753 | 30.6793 | -121.4905
1534.25 | 121.6919 | -0.51727 | 121.0373 | 0.0027468 | 0.038437 | 0.063318 | 0.0051099 | 0.0524 | -0.0053812 | 0.007575 | 0.18188 | -0.0084104 | 0.06273 | 0.072314 | 0.0012455 | -0.0093845 | -0.041199 | -0.045776 | -0.036621 | -0.40741 | -0.004578 | -0.42114 | -0.57678 | 0.62714 | 29.7638 | -0.46234 | 120.9229 | 120.845 | -0.52643 | -0.54474 | 0.09613 | -0.059509 | -121.0419 | 0.4715 | 0.10986 | 0.16937 | -121.0785 | -0.009155 | -0.027466 | -0.11444 | 1.1444 | 0.054932 | 0.082398 | -0.19226 | 0.5127 | 0.47607 | 0.48065 | -121.6141 | 121.4401 | 121.3623 | 30.2811 | -121.582
1535.9375 | 121.6095 | -0.65002 | 121.019 | 0.056152 | 0.043778 | 0.060968 | -0.00087155 | 0.050477 | -0.00025418 | 0.009925 | 0.097962 | -0.0047788 | 0.063798 | 0.072954 | 0.0074405 | -0.011734 | -0.068665 | -0.16937 | -0.14191 | -0.54932 | 0.022888 | -0.52643 | -0.66834 | 0.53101 | 29.3701 | -0.66376 | 120.8908 | 120.8633 | -0.6546 | -0.66376 | 0.1236 | -0.018311 | -120.9961 | 0.48065 | 0.10071 | 0.11902 | -121.0876 | -0.004578 | -0.013733 | -0.12817 | 1.181 | -0.013733 | 0 | -0.15564 | 0.67291 | 0.58136 | 0.50812 | -121.6873 | 121.5408 | 121.5134 | 30.0201 | -121.6827
1537.625 | 121.637 | -0.6546 | 121.0236 | 0.040894 | 0.045487 | 0.058191 | 0.0034009 | 0.050904 | 0.0014548 | 0.013129 | 0.067444 | -0.006915 | 0.065935 | 0.074663 | 0.0048769 | -0.0083163 | -0.14191 | -0.20142 | -0.16022 | -0.55847 | -0.013733 | -0.55389 | -0.69122 | 0.56763 | 29.1504 | -0.67291 | 120.932 | 120.8542 | -0.65002 | -0.67749 | 0.10071 | -0.036621 | -121.0373 | 0.45319 | 0.09613 | 0.13275 | -121.1655 | 0.004578 | -0.022888 | -0.091553 | 1.2222 | -0.018311 | 0.004577 | -0.16937 | 0.64087 | 0.5127 | 0.49439 | -121.7148 | 121.5866 | 121.5088 | 29.805 | -121.7011
1539.3906 | 121.7697 | -0.65918 | 120.9549 | -0.0354 | 0.051041 | 0.053278 | 0.0059643 | 0.049409 | -0.0055948 | 0.02082 | 0.0064086 | -0.010333 | 0.06508 | 0.072954 | -0.0021725 | -0.0098117 | -0.2243 | -0.19226 | -0.17853 | -0.55389 | -0.17853 | -0.57678 | -0.71869 | 0.64545 | 29.3427 | -0.59052 | 120.8038 | 120.7489 | -0.69122 | -0.6958 | 0.082398 | -0.059509 | -121.1334 | 0.46692 | 0.10529 | 0.1648 | -121.1792 | -0.032043 | -0.036621 | -0.15106 | 1.3046 | 0.068665 | 0.10529 | -0.20599 | 0.48065 | 0.43488 | 0.48065 | -121.6736 | 121.463 | 121.4081 | 30.0018 | -121.6507
1541.1406 | 121.8292 | -5.7495 | 115.6952 | -0.065918 | 0.079666 | 0.024225 | 0.0089551 | 0.29508 | -0.0036722 | 0.085975 | -0.11566 | -0.0077696 | 0.064226 | 0.074236 | 0.00017731 | -0.011307 | -1.8951 | -1.8723 | -1.8677 | -5.5069 | -1.8951 | -5.7816 | -5.9006 | -4.3671 | 26.7975 | -5.7724 | 115.6448 | 115.5899 | -5.8273 | -5.8731 | -0.032043 | -0.15106 | -117.5903 | 3.8773 | 0.24261 | 0.39368 | -117.5903 | -0.07782 | -0.1236 | -0.050354 | 1.3824 | -0.022888 | 0.10071 | -0.10528 | 3.8544 | 3.8544 | 3.8818 | -121.5958 | 121.3943 | 121.3394 | 32.547 | -121.5683
1542.8438 | 121.8155 | -7.37 | 114.1708 | -0.012512 | 0.064072 | 0.032556 | 0.0098097 | 0.39249 | -0.00068138 | 0.12229 | -0.046997 | -0.006915 | 0.063158 | 0.072954 | 0.00081811 | -0.0070345 | -2.7649 | -2.7283 | -2.7145 | -5.8273 | -2.6779 | -7.1732 | -7.2968 | -5.8594 | 25.8133 | -7.3746 | 114.1434 | 114.0839 | -7.3242 | -7.3929 | 0.19684 | 0.073242 | -116.8488 | 4.6417 | 1.5427 | 1.4694 | -116.9357 | 0.045776 | -0.022888 | -0.027465 | 1.5106 | -0.004578 | 0.01831 | -0.086975 | 4.6921 | 4.6051 | 4.6555 | -121.4676 | 121.5134 | 121.4539 | 33.1833 | -121.5637
1544.6094 | 121.6782 | -1.3962 | 120.2499 | -0.081177 | 0.046555 | 0.057336 | 0.0068189 | 0.13358 | 0.0057272 | 0.063544 | -0.16907 | -0.005847 | 0.065935 | 0.073595 | 0.0063723 | -0.01323 | -0.75531 | -0.79651 | -0.79651 | -1.1261 | -0.72327 | -1.3412 | -1.506 | 0.054932 | 28.3081 | -1.442 | 120.0897 | 120.0302 | -1.4511 | -1.4923 | 0.054931 | -0.10986 | -120.9732 | 0.59967 | 0.27008 | 0.37994 | -121.0052 | -0.054932 | -0.096131 | -0.16022 | 1.4511 | -0.045777 | 0.050354 | -0.21973 | 0.67291 | 0.64087 | 0.59967 | -121.756 | 121.4859 | 121.4264 | 29.7043 | -121.7422
1546.3438 | 121.7422 | -1.7532 | 119.8654 | 0.08667 | 0.041428 | 0.059473 | 0.0036145 | 0.15323 | -0.0017496 | 0.064612 | 0.12848 | -0.0067014 | 0.064226 | 0.074023 | 0.0038089 | -0.0089573 | -0.93384 | -0.90637 | -0.89264 | -1.1902 | -0.94757 | -1.5976 | -1.7395 | -0.11902 | 28.3859 | -1.6663 | 119.7418 | 119.7052 | -1.7441 | -1.7624 | 0.15564 | 0.013733 | -120.813 | 0.84686 | 0.56305 | 0.54932 | -120.7993 | 0.009155 | -0.009155 | -0.1236 | 1.6342 | 0.086975 | 0.09613 | -0.16022 | 0.80566 | 0.8194 | 0.8606 | -121.6049 | 121.4951 | 121.4584 | 30.1392 | -121.6278
1548.0938 | 121.6141 | -8.812 | 113.8321 | 0.010376 | 0.056595 | 0.025079 | 0.0061781 | 1.0549 | 0.0033774 | 0.13532 | 0.029297 | -0.0054196 | 0.061021 | 0.074023 | 0.0061587 | -0.0091709 | -7.663 | -8.0017 | -8.139 | -8.725 | -7.5165 | -9.5078 | -9.6542 | -8.3908 | 24.5361 | -10.0159 | 111.4655 | 111.5067 | -9.8923 | -9.8831 | -0.6958 | -0.84228 | -121.3486 | 0.81024 | 0.086975 | 0.92926 | -121.4951 | -1.0803 | -1.0712 | -2.3666 | 0.42114 | -1.2039 | -0.13275 | -2.3254 | 1.2955 | 1.149 | 0.67291 | -123.4863 | 120.2774 | 120.3186 | 33.3481 | -123.7152
1549.7812 | 121.6599 | -12.0895 | 109.4421 | -0.020142 | 0.072403 | 0.02337 | 0.0087415 | 1.5832 | -0.0013224 | 0.028724 | -0.016479 | -0.0071286 | 0.064439 | 0.072741 | -3.629e-05 | -0.0083163 | -9.1965 | -9.0775 | -9.1003 | -9.2834 | -8.6105 | -10.2219 | -10.2768 | -9.2606 | 23.8678 | -10.7208 | 110.7193 | 110.6598 | -10.6934 | -10.849 | 1.8677 | 1.8127 | -118.0527 | 3.0121 | 2.8061 | 0.99335 | -118.6386 | 1.3962 | 1.2405 | 1.2772 | 2.829 | 1.3687 | 0.12817 | 1.2177 | 3.479 | 2.8931 | 2.9892 | -119.7189 | 122.8088 | 122.7493 | 35.9573 | -120.2911
1551.5156 | 121.6507 | -1.7258 | 119.7922 | 0.048523 | 0.043351 | 0.0599 | 0.0038281 | 0.30576 | -0.0021768 | 0.015266 | 0.082703 | -0.0064878 | 0.062944 | 0.073382 | 0.0042361 | -0.0095981 | -1.5472 | -1.5701 | -1.5106 | -1.6022 | -1.5701 | -1.712 | -1.8219 | -0.041199 | 28.1616 | -1.8036 | 119.5862 | 119.5038 | -1.7899 | -1.8402 | 0.013733 | -0.09613 | -121.3623 | 0.15564 | 0.1236 | 0.21973 | -121.3394 | -0.064087 | -0.11444 | -0.20599 | 1.6846 | -0.07782 | 0.036621 | -0.28839 | 0.15564 | 0.17853 | 0.21515 | -121.6141 | 121.312 | 121.2296 | 29.8874 | -121.6324
1553.2656 | 121.6049 | -0.5127 | 121.1288 | -0.24902 | 0.04805 | 0.058191 | 0.0044691 | 0.25107 | -0.00089518 | 0.012275 | -0.15381 | -0.0043516 | 0.06508 | 0.071459 | 0.0023135 | -0.010025 | -1.4328 | -0.75531 | -0.35248 | -0.35706 | -1.2955 | -1.2451 | -1.2497 | 1.3 | 28.7567 | -0.49896 | 121.0556 | 120.9732 | -0.40283 | -0.4303 | -0.73242 | -0.737 | -122.4243 | -0.24262 | 0.15564 | 0.89264 | -122.5616 | 0.10986 | 0.082397 | -0.073242 | 1.8127 | 0.013733 | -0.068664 | -0.15564 | -0.78278 | -0.92011 | 0.16022 | -122.3785 | 121.5683 | 121.4859 | 29.2694 | -121.5591
1554.9688 | 121.6232 | -0.48981 | 121.1655 | -0.065918 | 0.042496 | 0.06225 | 0.0012647 | 0.059876 | 0.003591 | 0.015266 | -0.13855 | -0.001788 | 0.065721 | 0.075945 | 0.0072269 | -0.011734 | -0.29297 | -0.33417 | -0.33875 | -0.35706 | -0.27924 | -0.38452 | -0.52643 | 1.4099 | 28.3813 | -0.46692 | 121.0648 | 121.0144 | -0.48065 | -0.5127 | 0.10529 | -0.036621 | -121.4447 | 0.15564 | 0.13275 | 0.16937 | -121.4584 | 0.009155 | -0.022888 | -0.10071 | 1.8997 | 0.022888 | 0.045776 | -0.15106 | 0.21057 | 0.19684 | 0.15106 | -121.6919 | 121.5546 | 121.5042 | 28.8712 | -121.6782
1556.7188 | 121.6461 | -0.62256 | 121.0236 | -0.0354 | 0.044632 | 0.061823 | 0.0016919 | 0.065431 | 0.00081382 | 0.015479 | -0.092773 | -0.0037106 | 0.065507 | 0.075091 | 0.0053043 | -0.0081027 | -0.43488 | -0.45776 | -0.45319 | -0.48523 | -0.3891 | -0.47607 | -0.62714 | 1.2909 | 27.9465 | -0.60883 | 120.9549 | 120.8862 | -0.60883 | -0.66834 | 0.14648 | -0.004577 | -121.4127 | 0.16479 | 0.13733 | 0.14191 | -121.4584 | 0.013733 | -0.045776 | -0.068665 | 1.9135 | 0.013733 | 0.059509 | -0.13733 | 0.23346 | 0.18768 | 0.16937 | -121.6507 | 121.5775 | 121.5088 | 28.569 | -121.6919
1558.4844 | 121.6599 | -0.64545 | 121.0739 | -0.21088 | 0.039933 | 0.063745 | 0.0040417 | 0.065431 | -0.0070902 | 0.01142 | -0.24536 | -0.0032834 | 0.064439 | 0.073382 | 0.00039091 | -0.0070345 | -0.45776 | -0.42572 | -0.43488 | -0.5127 | -0.4303 | -0.5127 | -0.66834 | 1.387 | 27.9968 | -0.57678 | 120.9274 | 120.8771 | -0.65918 | -0.67291 | 0.13275 | -0.022888 | -121.5042 | 0.21973 | 0.13275 | 0.15564 | -121.5317 | -0.013733 | -0.027466 | -0.14648 | 2.0325 | 0.068665 | 0.096131 | -0.19684 | 0.21515 | 0.18768 | 0.21057 | -121.7422 | 121.5729 | 121.5225 | 28.6423 | -121.7468
1560.25 | 121.6278 | -3.9688 | 117.7917 | -0.17273 | 0.048905 | 0.057123 | 0.0053235 | 0.33716 | -0.0040994 | 0.011634 | -0.031738 | -0.0060606 | 0.064439 | 0.074236 | 0.0035953 | -0.0078891 | -3.4058 | -3.3554 | -3.3508 | -3.4744 | -3.4378 | -3.6621 | -3.7445 | -1.8082 | 27.2415 | -3.804 | 117.6682 | 117.691 | -3.8269 | -3.8544 | 0.3067 | 0.2243 | -121.2296 | 0.6134 | 0.49439 | 0.27008 | -121.1975 | 0.14191 | 0.11444 | -0.1236 | 2.1606 | 0.1648 | 0.050354 | -0.10071 | 0.53101 | 0.56305 | 0.61798 | -121.5363 | 121.637 | 121.6599 | 31.2103 | -121.6461
1561.9531 | 121.6919 | -3.0029 | 118.5974 | -0.088806 | 0.048905 | 0.056696 | 0.0010511 | 0.2861 | 0.0033774 | 0.015906 | -0.16907 | -0.0028562 | 0.064653 | 0.074023 | 0.0065859 | -0.011521 | -2.6093 | -2.6276 | -2.6825 | -2.6917 | -2.6001 | -2.8381 | -2.9709 | -0.66376 | 27.6215 | -2.8793 | 118.6523 | 118.6066 | -2.8976 | -2.9526 | 0.1648 | 0.032044 | -121.1975 | 0.37537 | 0.31128 | 0.27924 | -121.2067 | 0.10529 | 0.050354 | 0.054932 | 2.3392 | 0.1236 | 0.073243 | 0.009155 | 0.40283 | 0.39368 | 0.32044 | -121.5683 | 121.6553 | 121.6095 | 30.6244 | -121.55
1563.7031 | 121.7056 | -5.4016 | 116.2125 | 0.08667 | 0.055527 | 0.051569 | 0.0012647 | 0.53818 | 0.0031638 | 0.015906 | -0.062256 | -0.0022154 | 0.069139 | 0.077013 | 0.0053043 | -0.0089573 | -5.1132 | -5.0674 | -4.985 | -5.1453 | -4.9255 | -5.2963 | -5.4016 | -3.0441 | 24.8154 | -5.603 | 116.1072 | 116.0843 | -5.4153 | -5.4474 | 0.10529 | 0 | -121.138 | 0.33417 | 0.25635 | 0.25635 | -121.3257 | -0.013733 | -0.045777 | -0.10528 | 2.3575 | -0.20142 | -0.15564 | -0.12817 | 0.47607 | 0.28839 | 0.41657 | -121.6141 | 121.5088 | 121.4859 | 30.217 | -121.6599
1565.4688 | 121.6827 | -1.6388 | 120.0348 | -0.04303 | 0.047196 | 0.057336 | 0.0012647 | 0.23312 | -0.0011088 | 0.013984 | -0.085144 | -0.0037106 | 0.06508 | 0.07445 | 0.0029543 | -0.0083163 | -2.3026 | -2.0645 | -2.1057 | -2.2751 | -2.1286 | -2.3346 | -2.4673 | -0.09613 | 27.0996 | -2.3392 | 119.1696 | 119.1925 | -2.3849 | -2.3987 | -0.6958 | -0.82855 | -122.1634 | -0.42572 | -0.63629 | 0.19226 | -122.3373 | -0.74616 | -0.75989 | -0.86517 | 1.5427 | -0.70038 | 0.05951 | -0.84229 | -0.48981 | -0.66376 | -0.46692 | -122.5021 | 120.8084 | 120.8313 | 28.7384 | -122.4335
1567.2188 | 121.6599 | -16.713 | 104.6539 | 0.094299 | 0.070694 | 0.02572 | 0.0061781 | 2.7761 | -0.00025418 | 0.026801 | 0.12085 | -0.0049924 | 0.065935 | 0.075945 | 0.0014591 | -0.0048983 | -14.6393 | -14.6027 | -14.6027 | -14.9643 | -9.0088 | -16.1499 | -16.2415 | -14.003 | 20.2377 | -16.8503 | 104.6127 | 104.567 | -16.7038 | -16.7725 | 0.56305 | 0.4715 | -113.6627 | 2.1103 | 1.7487 | 1.2772 | -119.2932 | 0.009156 | -0.059509 | -0.041199 | 2.71 | -0.13733 | -0.07782 | -0.086975 | 7.7042 | 2.0737 | 2.1103 | -120.8954 | 121.3257 | 121.2799 | 36.9507 | -121.4264
1568.9688 | 121.6873 | -3.2043 | 118.4052 | -0.24902 | 0.049759 | 0.059045 | 0.0048963 | 0.53177 | -0.00068138 | 0.01377 | -0.18433 | -0.004138 | 0.065507 | 0.076372 | 0.0018863 | -0.0095981 | -2.8839 | -2.8793 | -2.8885 | -2.9114 | -2.71 | -3.067 | -3.2043 | -0.65002 | 22.934 | -3.2272 | 118.3273 | 118.3044 | -3.2043 | -3.241 | 0.13733 | 0 | -121.1151 | 0.32501 | 0.29297 | 0.29297 | -121.2891 | 0 | -0.036621 | -0.077819 | 2.5543 | -0.022888 | 0.013733 | -0.10071 | 0.49439 | 0.32044 | 0.31586 | -121.6095 | 121.5317 | 121.5088 | 26.1383 | -121.6461
1570.6562 | 121.6278 | -5.7999 | 115.741 | -0.081177 | 0.054245 | 0.053705 | 0.0036145 | 0.95517 | 0.0040182 | 0.015266 | -0.10803 | -0.0011472 | 0.06743 | 0.07744 | 0.0048769 | -0.0098117 | -4.9072 | -4.921 | -4.9301 | -5.0354 | -4.7745 | -5.2505 | -5.3833 | -2.5543 | 22.3801 | -5.452 | 116.0706 | 116.0156 | -5.3833 | -5.484 | 0.54932 | 0.41656 | -120.5154 | 0.87891 | 0.76447 | 0.3479 | -120.6482 | 0.41656 | 0.31586 | 0.32959 | 3.2455 | 0.3479 | 0.032044 | 0.27466 | 1.0254 | 0.89264 | 0.86975 | -121.1243 | 121.8704 | 121.8155 | 28.1799 | -121.225
1572.4062 | 121.6507 | -9.1461 | 112.1933 | 0.063782 | 0.058304 | 0.046869 | 0.00041005 | 1.5685 | -0.003245 | 0.023383 | 0.16663 | -0.0060606 | 0.065935 | 0.076372 | 0.0029543 | -0.0074619 | -8.1436 | -8.1024 | -7.9559 | -8.0887 | -7.8506 | -8.4503 | -8.5556 | -5.5435 | 21.2631 | -8.4915 | 112.7838 | 112.587 | -8.67 | -8.8211 | 0.6958 | 0.59051 | -120.0439 | 1.0437 | 1.0574 | 0.46692 | -120.3369 | 0.47607 | 0.32501 | 0.59051 | 3.6026 | 0.6546 | 0.32959 | 0.39368 | 1.2955 | 1.0025 | 1.1902 | -120.7489 | 121.9299 | 121.7331 | 30.4092 | -121.0144
1574.1719 | 121.5775 | -1.6708 | 119.9295 | -0.096436 | 0.046555 | 0.058832 | 0.0023329 | 0.30618 | 0.0010276 | 0.015052 | -0.15381 | -0.0020018 | 0.066576 | 0.075304 | 0.0061587 | -0.01088 | -1.442 | -1.4511 | -1.4282 | -1.4511 | -1.3733 | -1.5289 | -1.6754 | 1.1948 | 23.5977 | -1.68 | 119.8013 | 119.751 | -1.6708 | -1.712 | 0.14191 | -0.004578 | -121.3028 | 0.21973 | 0.21973 | 0.2243 | -121.3715 | 0 | -0.041199 | -0.12817 | 2.8656 | -0.009156 | 0.032043 | -0.17853 | 0.29755 | 0.22888 | 0.24261 | -121.6049 | 121.4722 | 121.4218 | 25.2686 | -121.6415
1575.8594 | 121.6415 | -1.3367 | 120.2911 | 0.033264 | 0.044846 | 0.056696 | 0.0023329 | 0.19852 | -0.00046778 | 0.015052 | 0.021668 | -0.0030698 | 0.06743 | 0.075518 | 0.0055179 | -0.0091709 | -1.181 | -1.2131 | -1.1993 | -1.1673 | -1.0391 | -1.181 | -1.3229 | 1.5884 | 27.2278 | -1.2817 | 120.2637 | 120.2133 | -1.2817 | -1.3184 | 0.15564 | 0.013733 | -121.3303 | 0.1236 | 0.16937 | 0.15564 | -121.4722 | 0.054932 | 0.018311 | -0.027466 | 2.9251 | 0.054932 | 0.036621 | -0.07782 | 0.29755 | 0.15564 | 0.13733 | -121.6141 | 121.6003 | 121.55 | 28.5645 | -121.6095
1577.6094 | 121.7194 | -1.0712 | 120.6482 | 0.018005 | 0.048905 | 0.058618 | 0.0014783 | 0.26175 | 0.001882 | 0.015052 | -0.039368 | -7.8952e-05 | 0.066576 | 0.07744 | 0.0050907 | -0.0087435 | -1.6022 | -1.6479 | -1.593 | -1.5793 | -1.4923 | -1.6113 | -1.7166 | 1.5289 | 22.2794 | -1.442 | 120.1035 | 119.9982 | -1.4877 | -1.5289 | -0.54016 | -0.64545 | -122.1405 | -0.57678 | -0.50812 | 0.13733 | -122.2504 | -0.41657 | -0.45776 | -0.54474 | 2.6001 | -0.37079 | 0.086975 | -0.65002 | -0.42114 | -0.53101 | -0.52185 | -122.3648 | 121.1746 | 121.0693 | 23.3505 | -122.1771
1579.3594 | 121.701 | -9.7458 | 111.7355 | 0.063782 | 0.069199 | 0.039606 | 0.0044691 | 1.4608 | -0.0070902 | 0.021888 | 0.044556 | -0.0039244 | 0.068071 | 0.077227 | -0.00089089 | -0.0074619 | -9.375 | -9.1736 | -9.3979 | -9.3567 | -8.4869 | -9.5306 | -9.6268 | -6.4041 | 19.7983 | -9.5993 | 111.8134 | 111.7401 | -9.5581 | -9.6085 | 0.21515 | 0.11902 | -120.2225 | 0.57221 | 0.3891 | 0.27008 | -121.1105 | 0.18768 | 0.13733 | 0.077819 | 3.3417 | 0.14649 | 0.009155 | 0.004577 | 1.2589 | 0.37079 | 0.3479 | -121.3623 | 121.5591 | 121.4859 | 29.5441 | -121.344
1581.1094 | 121.5866 | -12.8448 | 108.4396 | 0.08667 | 0.081589 | 0.026147 | -0.0040759 | 2.1812 | 0.0010276 | 0.021461 | -0.0012209 | -0.0026426 | 0.065721 | 0.079363 | 0.0067997 | -0.0085299 | -11.9385 | -12.0071 | -12.0987 | -12.0621 | -8.9722 | -12.2498 | -12.3825 | -9.8923 | 17.1844 | -13.3804 | 108.1558 | 108.0231 | -13.2523 | -13.3255 | 0.59509 | 0.46234 | -117.4118 | 0.83771 | 0.78278 | 0.32043 | -120.3781 | -0.40741 | -0.48065 | -0.28381 | 2.9526 | -0.53558 | -0.054932 | -0.41656 | 3.8727 | 0.90637 | 0.74615 | -120.8221 | 121.0007 | 120.8679 | 30.0293 | -121.7651
1582.7969 | 121.5088 | -13.5132 | 107.9407 | 0.11719 | 0.076248 | 0.030634 | -0.0010851 | 2.6554 | -0.0019632 | 0.01612 | 0.12848 | -0.0037106 | 0.067003 | 0.077227 | 0.0038089 | -0.0059665 | -11.8011 | -11.6638 | -11.6455 | -11.7599 | -8.9905 | -12.0941 | -12.204 | -9.0042 | 17.1844 | -12.4512 | 108.7555 | 108.783 | -12.3459 | -12.41 | 1.4191 | 1.3092 | -116.9312 | 1.8494 | 1.7532 | 0.44403 | -119.7418 | 1.1673 | 1.1032 | 0.81482 | 4.509 | 1.062 | -0.041199 | 0.84229 | 4.5227 | 1.712 | 1.8677 | -120.1447 | 122.2687 | 122.2961 | 30.6976 | -120.3506
1584.5469 | 121.3211 | -20.1553 | 100.9094 | -0.027771 | 0.091629 | 0.004358 | 0.0087415 | 5.3015 | 0.0065818 | 0.01847 | 0.090332 | -0.0056332 | 0.066789 | 0.077868 | 0.0046633 | -0.0070345 | -17.9764 | -17.9352 | -17.8894 | -18.0817 | -9.0179 | -19.5648 | -19.6472 | -16.5207 | 14.6896 | -20.7047 | 100.5981 | 100.4791 | -20.4163 | -20.5444 | 0.59051 | 0.50812 | -109.9274 | 2.2202 | 2.0737 | 1.5656 | -118.8858 | -0.26093 | -0.3891 | -0.31128 | 3.6346 | -0.54932 | -0.16022 | -0.4303 | 11.1374 | 2.179 | 2.2659 | -120.5566 | 120.7535 | 120.6345 | 34.845 | -121.4539
1586.2969 | 121.1426 | -17.3264 | 103.6606 | 0.063782 | 0.080735 | 0.021875 | 0.0066053 | 5.5256 | 0.011068 | 0.022742 | 0.059815 | 0.00034825 | 0.068925 | 0.078722 | 0.0091495 | -0.0078891 | -16.2094 | -16.3742 | -16.3925 | -16.5298 | -9.0179 | -17.7063 | -17.8299 | -14.003 | 19.1483 | -18.0634 | 103.1616 | 103.1021 | -17.8391 | -17.9764 | -0.37994 | -0.50354 | -112.6785 | 0.95215 | 0.79651 | 1.3 | -119.87 | -0.5127 | -0.65002 | -0.49896 | 3.3234 | -0.737 | -0.086975 | -0.55847 | 8.3084 | 1.1169 | 0.93384 | -121.4905 | 120.488 | 120.4285 | 36.4746 | -121.637
1587.9844 | 121.5088 | -0.19684 | 121.2524 | 0.094299 | 0.041214 | 0.064813 | 0.0029737 | 0.057954 | -0.0064492 | 0.012488 | 0.18951 | -0.0049924 | 0.067216 | 0.072527 | 0.0029543 | -0.0091709 | -0.004578 | 0.022888 | 0.004578 | -0.050354 | -0.027466 | -0.073242 | -0.21515 | 3.3875 | 26.7883 | -0.064087 | 121.1105 | 121.1105 | -0.17395 | -0.18768 | 0.1236 | -0.018311 | -121.2799 | 0.21973 | 0.14648 | 0.16479 | -121.257 | 0.022888 | 0.009155 | -0.14191 | 3.5843 | 0.13275 | 0.1236 | -0.14191 | 0.16937 | 0.19226 | 0.20142 | -121.4676 | 121.3074 | 121.3074 | 26.9852 | -121.4401
1589.7344 | 121.5546 | -0.21515 | 121.3623 | -0.14221 | 0.043564 | 0.063104 | 0.0038281 | 0.061372 | 0.00017302 | 0.013343 | -0.12329 | -0.0026426 | 0.065935 | 0.075091 | 0.0065859 | -0.0087435 | -0.022888 | -0.041199 | -0.045776 | -0.054932 | 0.027466 | -0.10529 | -0.27008 | 3.447 | 24.6918 | -0.11902 | 121.2479 | 121.1838 | -0.19226 | -0.23804 | 0.10986 | -0.054932 | -121.3348 | 0.17395 | 0.16022 | 0.21515 | -121.3852 | 0.022888 | -0.022888 | -0.11444 | 3.6621 | 0.09613 | 0.11902 | -0.17853 | 0.24261 | 0.19226 | 0.16937 | -121.6324 | 121.463 | 121.3989 | 24.9069 | -121.6003
1591.4219 | 121.6141 | -0.20599 | 121.3898 | -0.20325 | 0.042069 | 0.065027 | 0.0068189 | 0.059876 | -0.0055948 | 0.012916 | -0.13092 | -0.0054196 | 0.070207 | 0.076159 | 0.0023135 | -0.0070345 | 0.009155 | 0.073242 | 0.068665 | -0.009155 | -0.022888 | -0.082397 | -0.23346 | 3.5797 | 29.9744 | -0.027466 | 121.2158 | 121.1563 | -0.19226 | -0.20599 | 0.1236 | -0.027465 | -121.4127 | 0.27924 | 0.19684 | 0.2243 | -121.3806 | 0.013733 | 0 | -0.17395 | 3.7857 | 0.17853 | 0.17853 | -0.23346 | 0.18311 | 0.21515 | 0.27466 | -121.6232 | 121.4218 | 121.3623 | 30.1804 | -121.5958
1593.1562 | 121.5958 | -0.22888 | 121.376 | 0.033264 | 0.04271 | 0.062036 | 0.0016919 | 0.055604 | 0.001882 | 0.013984 | 0.036926 | -7.8952e-05 | 0.071062 | 0.0768 | 0.0063723 | -0.0072483 | -0.054932 | -0.13275 | -0.10071 | -0.11444 | 0.041199 | -0.11444 | -0.25635 | 3.5706 | 30.9219 | -0.19684 | 121.312 | 121.257 | -0.21973 | -0.24719 | 0.11444 | -0.027466 | -121.3348 | 0.096131 | 0.11444 | 0.14191 | -121.431 | 0.009155 | -0.01831 | -0.064087 | 3.7994 | 0.032044 | 0.050354 | -0.11902 | 0.27008 | 0.17395 | 0.12817 | -121.6324 | 121.5408 | 121.4859 | 31.1508 | -121.6232
1594.9062 | 121.5866 | -0.24261 | 121.4172 | -0.04303 | 0.044632 | 0.061823 | 0.0019055 | 0.060945 | 0.001882 | 0.014625 | -0.046997 | 0.00077545 | 0.069994 | 0.07744 | 0.0065859 | -0.0083163 | -0.009155 | -0.027466 | -0.036621 | -0.073242 | 0.013733 | -0.11444 | -0.25177 | 3.7262 | 31.2378 | -0.18768 | 121.2936 | 121.2616 | -0.23346 | -0.25177 | 0.12817 | -0.009155 | -121.4035 | 0.21515 | 0.16937 | 0.17853 | -121.4264 | 0.009156 | -0.009155 | -0.1236 | 3.9688 | 0.054932 | 0.064087 | -0.15564 | 0.25635 | 0.23346 | 0.20599 | -121.669 | 121.5363 | 121.5042 | 31.4804 | -121.669
1596.6562 | 121.6553 | -0.23346 | 121.376 | 0.079041 | 0.044846 | 0.063959 | 0.0023329 | 0.062226 | -0.00025418 | 0.015693 | 0.067444 | -0.00071995 | 0.070634 | 0.077013 | 0.0078677 | -0.0066073 | -0.059509 | -0.10071 | -0.086975 | -0.082397 | 0.032043 | -0.13275 | -0.27924 | 3.8086 | 28.0792 | -0.21973 | 121.312 | 121.2936 | -0.2243 | -0.25635 | 0.10071 | -0.045777 | -121.344 | 0.13275 | 0.15106 | 0.19684 | -121.4355 | 0.009155 | -0.022889 | -0.064087 | 4.0421 | 0.013732 | 0.036621 | -0.082398 | 0.2655 | 0.17395 | 0.14648 | -121.6553 | 121.5454 | 121.5271 | 28.3127 | -121.6324
1598.4062 | 121.6278 | -0.25635 | 121.4218 | -0.21851 | 0.043991 | 0.063104 | 0.0098097 | 0.062654 | -0.0062356 | 0.011634 | -0.15381 | -0.001788 | 0.074266 | 0.077868 | 0.00060451 | -0.0072483 | -0.068665 | -0.018311 | -0.036621 | -0.082397 | 0.036621 | -0.13275 | -0.27924 | 3.9368 | 29.7363 | -0.18768 | 121.3074 | 121.2845 | -0.23804 | -0.25635 | 0.1236 | -0.022888 | -121.3852 | 0.23804 | 0.17395 | 0.19684 | -121.4905 | 0.018311 | 0 | -0.11444 | 4.1931 | 0.068665 | 0.068665 | -0.13733 | 0.29297 | 0.18768 | 0.21973 | -121.701 | 121.5637 | 121.5408 | 29.9927 | -121.6782
1600.1562 | 121.6736 | -0.2243 | 121.431 | -0.20325 | 0.044419 | 0.061182 | 0.0066053 | 0.061799 | -0.0030314 | 0.013343 | -0.23773 | -0.0028562 | 0.073839 | 0.075304 | 0.0014591 | -0.0078891 | -0.073242 | -0.068665 | -0.068665 | -0.091553 | 0.059509 | -0.15564 | -0.29297 | 4.0512 | 30.9082 | -0.20599 | 121.3348 | 121.2891 | -0.25177 | -0.2655 | 0.068664 | -0.068665 | -121.3715 | 0.15564 | 0.13275 | 0.20142 | -121.5042 | -0.027466 | -0.041199 | -0.09613 | 4.2755 | 0.01831 | 0.059509 | -0.14191 | 0.28381 | 0.15106 | 0.15564 | -121.7239 | 121.5591 | 121.5134 | 31.1325 | -121.6965
1601.8438 | 121.7789 | -0.21973 | 121.376 | 0.0027468 | 0.040146 | 0.062463 | 0.0031873 | 0.061158 | -0.0079446 | 0.010779 | 0.059815 | -0.0049924 | 0.073412 | 0.0768 | -0.00046349 | -0.0046847 | -0.045776 | -0.004578 | -0.004578 | -0.050354 | 0.009155 | -0.11444 | -0.25635 | 4.2526 | 33.4076 | -0.1236 | 121.2662 | 121.2708 | -0.2243 | -0.25177 | 0.10529 | -0.036621 | -121.3669 | 0.21515 | 0.16937 | 0.20599 | -121.4218 | -0.004577 | -0.032043 | -0.10986 | 4.4724 | 0.096131 | 0.12817 | -0.10529 | 0.22888 | 0.17395 | 0.21515 | -121.6324 | 121.4859 | 121.4905 | 33.6273 | -121.6278
1603.5938 | 121.6827 | -0.25635 | 121.4218 | -0.19562 | 0.040573 | 0.062677 | 0.0063917 | 0.063508 | -0.0028178 | 0.010566 | -0.20721 | -0.0026426 | 0.074907 | 0.078295 | 0.00039091 | -0.0072483 | 0.027466 | 0.050354 | 0.045776 | -0.009155 | 0.004578 | -0.13275 | -0.25635 | 4.3945 | 33.8287 | -0.09613 | 121.3165 | 121.2708 | -0.2243 | -0.24719 | 0.1236 | 0 | -121.4172 | 0.3067 | 0.24719 | 0.24719 | -121.3943 | 0.032044 | 0.009156 | -0.10529 | 4.6509 | 0.16022 | 0.15106 | -0.15106 | 0.26093 | 0.28381 | 0.30212 | -121.6782 | 121.5729 | 121.5271 | 34.0851 | -121.669
1605.3594 | 121.756 | -0.2243 | 121.4081 | -0.0048827 | 0.039505 | 0.065027 | 0.0025465 | 0.062654 | -0.006022 | 0.010139 | 0.044556 | -0.005206 | 0.073198 | 0.0768 | 0.0048769 | -0.0059665 | -0.013733 | 0 | 0.013733 | -0.045776 | 0.004578 | -0.1236 | -0.26093 | 4.5364 | 34.1263 | -0.2243 | 121.3074 | 121.2982 | -0.2243 | -0.23346 | 0.10071 | -0.036621 | -121.4035 | 0.2243 | 0.17853 | 0.21515 | -121.4218 | 0 | -0.009155 | -0.10071 | 4.7607 | 0 | 0.009155 | -0.10986 | 0.22888 | 0.21057 | 0.23804 | -121.669 | 121.5317 | 121.5225 | 34.3506 | -121.6415
1607.1094 | 121.6736 | -0.25177 | 121.4584 | -0.065918 | 0.044419 | 0.0599 | 0.0010511 | 0.065858 | 0.0025228 | 0.012275 | -0.11566 | -0.00071995 | 0.073625 | 0.079577 | 0.0074405 | -0.0095981 | 0.013733 | -0.018311 | -0.036621 | -0.045776 | 0.032043 | -0.12817 | -0.27008 | 4.6646 | 35.7651 | -0.22888 | 121.344 | 121.3211 | -0.2243 | -0.25635 | 0.1236 | -0.018311 | -121.4264 | 0.23346 | 0.20599 | 0.22431 | -121.4447 | 0.027466 | -0.004578 | -0.11444 | 4.9164 | 0.022888 | 0.027466 | -0.13733 | 0.28381 | 0.2655 | 0.21515 | -121.7285 | 121.5958 | 121.5729 | 36.0168 | -121.7148
1608.7969 | 121.6644 | -0.27008 | 121.463 | -0.21088 | 0.043564 | 0.060327 | 0.0051099 | 0.06479 | -0.0034586 | 0.012061 | -0.1767 | -0.00050635 | 0.076616 | 0.078509 | 0.0025271 | -0.0093845 | -0.059509 | -0.022888 | -0.032043 | -0.086975 | 0.032043 | -0.15564 | -0.31128 | 4.8203 | 37.4222 | -0.18768 | 121.3715 | 121.3394 | -0.25177 | -0.26093 | 0.11444 | -0.041198 | -121.431 | 0.24719 | 0.18311 | 0.2243 | -121.5225 | 0.018311 | 0.009156 | -0.091553 | 5.0903 | 0.082398 | 0.073242 | -0.1236 | 0.30212 | 0.21057 | 0.23804 | -121.7743 | 121.6415 | 121.6095 | 37.6923 | -121.7239
1610.5469 | 121.8109 | -0.21057 | 121.4035 | 0.094299 | 0.040573 | 0.063959 | -1.7146e-05 | 0.068849 | -0.0011088 | 0.01377 | 0.10559 | 0.0012026 | 0.075548 | 0.079577 | 0.0072269 | -0.0087435 | -0.032043 | -0.073242 | -0.054932 | -0.091553 | 0.032043 | -0.14648 | -0.29297 | 5.0034 | 38.9557 | -0.15106 | 121.3623 | 121.3348 | -0.23346 | -0.27008 | 0.064087 | -0.082398 | -121.3715 | 0.13733 | 0.11902 | 0.20142 | -121.4355 | -0.022888 | -0.05951 | -0.041198 | 5.2139 | 0.059509 | 0.11902 | -0.068664 | 0.24261 | 0.17853 | 0.15564 | -121.6965 | 121.5729 | 121.5454 | 39.1663 | -121.6736
1612.2969 | 121.8475 | -0.21973 | 121.4172 | -0.073547 | 0.042282 | 0.061823 | 0.0066053 | 0.065858 | -0.0068766 | 0.009925 | -0.085144 | -7.8952e-05 | 0.080675 | 0.07744 | 0.0018863 | -0.0070345 | 0.004578 | 0.013733 | 0.045776 | -0.022888 | 0.018311 | -0.14648 | -0.27466 | 5.2826 | 41.0202 | -0.050354 | 121.3257 | 121.2891 | -0.21973 | -0.24719 | 0.073243 | -0.054931 | -121.3989 | 0.23346 | 0.19684 | 0.25177 | -121.4127 | 0 | -0.027465 | -0.091552 | 5.5023 | 0.16937 | 0.19684 | -0.12817 | 0.23804 | 0.22431 | 0.2655 | -121.6919 | 121.5454 | 121.5088 | 41.2399 | -121.6644
1614.0469 | 121.7972 | -0.23804 | 121.4401 | 0.094299 | 0.041001 | 0.063318 | 0.0019055 | 0.06479 | 0.00060022 | 0.012702 | 0.044556 | 0.00013465 | 0.078752 | 0.081499 | 0.0074405 | -0.0098117 | -0.041199 | -0.10071 | -0.10071 | -0.09613 | 0.041199 | -0.15564 | -0.3067 | 5.365 | 39.6515 | -0.19684 | 121.3577 | 121.3257 | -0.25177 | -0.27924 | 0.082397 | -0.068665 | -121.3989 | 0.13733 | 0.14191 | 0.21057 | -121.4813 | -0.013733 | -0.041199 | -0.082398 | 5.603 | 0.041199 | 0.082398 | -0.11444 | 0.27924 | 0.19684 | 0.13733 | -121.7468 | 121.5958 | 121.5637 | 39.8895 | -121.7194
1615.7344 | 121.8063 | -0.24261 | 121.4127 | 0.11719 | 0.040787 | 0.060968 | 0.0014783 | 0.063508 | -0.00068138 | 0.01377 | 0.052185 | -0.00050635 | 0.078111 | 0.081499 | 0.0059451 | -0.0061801 | -0.032043 | -0.10986 | -0.09613 | -0.086975 | 0.032043 | -0.17853 | -0.31586 | 5.5481 | 39.9948 | -0.21515 | 121.3669 | 121.312 | -0.2655 | -0.28839 | 0.064087 | -0.073242 | -121.3806 | 0.13275 | 0.15564 | 0.22888 | -121.4447 | -0.022888 | -0.045776 | -0.045777 | 5.7907 | 0.027466 | 0.073242 | -0.10071 | 0.27466 | 0.21057 | 0.14649 | -121.7285 | 121.6095 | 121.5546 | 40.2374 | -121.7011
1617.4844 | 121.701 | -0.34332 | 121.3715 | -0.23376 | 0.042496 | 0.062036 | 0.0078871 | 0.066072 | -0.004954 | 0.016547 | -0.14618 | 0.00013465 | 0.080461 | 0.077654 | 0.0029543 | -0.0059665 | -0.045776 | -0.036621 | -0.018311 | -0.073242 | -0.009155 | -0.23346 | -0.35706 | 5.7404 | 40.8417 | -0.23804 | 121.2891 | 121.257 | -0.32501 | -0.33875 | 0.10986 | -0.013733 | -121.3806 | 0.3067 | 0.27008 | 0.28381 | -121.4172 | 0.018311 | 0.004578 | -0.082398 | 6.0837 | 0.10529 | 0.10071 | -0.11444 | 0.33417 | 0.29755 | 0.32501 | -121.7285 | 121.6324 | 121.6003 | 41.185 | -121.7102
1619.2344 | 121.8109 | -0.30212 | 121.3852 | -0.13458 | 0.039292 | 0.061182 | 0.0072461 | 0.06244 | -0.0073038 | 0.015693 | -0.13855 | -0.00029275 | 0.083665 | 0.078722 | 0.0027407 | -0.0083163 | 0.013733 | 0.073242 | 0.045776 | -0.036621 | -0.032043 | -0.19226 | -0.33417 | 5.9555 | 41.304 | -0.11444 | 121.2479 | 121.2341 | -0.29297 | -0.3067 | 0.10986 | -0.032043 | -121.4172 | 0.37537 | 0.2655 | 0.29755 | -121.3715 | 0.009155 | -0.004578 | -0.13733 | 6.2576 | 0.18768 | 0.19226 | -0.15106 | 0.27008 | 0.31586 | 0.3479 | -121.7194 | 121.55 | 121.5363 | 41.6061 | -121.6919
1620.9219 | 121.756 | -0.33417 | 121.4035 | -0.22614 | 0.0457 | 0.062463 | 0.0074597 | 0.064149 | -4.058e-05 | 0.014838 | -0.20721 | 0.00077545 | 0.086443 | 0.081286 | 0.0046633 | -0.0083163 | -0.09613 | -0.09613 | -0.09613 | -0.10529 | 0.022888 | -0.23346 | -0.37994 | 6.0745 | 39.7018 | -0.2655 | 121.3348 | 121.2479 | -0.31586 | -0.36163 | 0.10071 | -0.045777 | -121.3806 | 0.23804 | 0.22888 | 0.27466 | -121.4996 | 0.01831 | -0.027466 | -0.068664 | 6.4087 | 0.068664 | 0.09613 | -0.15564 | 0.35706 | 0.23804 | 0.23804 | -121.7834 | 121.669 | 121.582 | 40.036 | -121.7651
1622.6719 | 121.788 | -0.33875 | 121.3806 | -0.19562 | 0.039078 | 0.061609 | 0.0051099 | 0.067567 | -0.006663 | 0.01847 | -0.13855 | -0.0026426 | 0.085374 | 0.077227 | 0.0040225 | -0.0053257 | 0 | 0.050354 | 0.041199 | -0.036621 | -0.027466 | -0.2243 | -0.34332 | 6.3354 | 41.3635 | -0.10986 | 121.2662 | 121.2158 | -0.29755 | -0.32044 | 0.11444 | -0.004578 | -121.4081 | 0.3891 | 0.30212 | 0.3067 | -121.3806 | 0.041199 | 0.01831 | -0.11444 | 6.6742 | 0.22888 | 0.21057 | -0.1648 | 0.31128 | 0.33875 | 0.37994 | -121.7239 | 121.6049 | 121.5546 | 41.7023 | -121.7011
1624.4219 | 121.8246 | -0.33875 | 121.3486 | 0.010376 | 0.039505 | 0.0599 | 0.0046827 | 0.066926 | -0.0047404 | 0.017402 | 0.052185 | -0.0015744 | 0.087297 | 0.081499 | 0.0020999 | -0.0081027 | -0.050354 | -0.013733 | -0.027466 | -0.10529 | -0.027466 | -0.2243 | -0.36621 | 6.5048 | 42.5583 | -0.18768 | 121.2524 | 121.2067 | -0.32959 | -0.36163 | 0.11444 | -0.027466 | -121.376 | 0.32501 | 0.23346 | 0.26093 | -121.3989 | 0.009155 | -0.022888 | -0.096131 | 6.8436 | 0.15106 | 0.17395 | -0.14191 | 0.31128 | 0.28839 | 0.31128 | -121.7148 | 121.5912 | 121.5454 | 42.897 | -121.7102
1626.125 | 121.8292 | -0.33875 | 121.3577 | -0.12695 | 0.041214 | 0.060754 | 0.0087415 | 0.068849 | -0.0047404 | 0.018683 | -0.14618 | -0.002429 | 0.090715 | 0.081927 | 0.0038089 | -0.0070345 | 0.013733 | 0.068665 | 0.032043 | -0.054932 | -0.036621 | -0.23346 | -0.37994 | 6.9901 | 48.0835 | -0.11902 | 121.2433 | 121.1792 | -0.32959 | -0.3479 | 0.10529 | -0.041199 | -121.3943 | 0.40741 | 0.28381 | 0.32501 | -121.344 | 0.009155 | -0.009155 | -0.11444 | 7.3288 | 0.21973 | 0.22888 | -0.17853 | 0.30212 | 0.35248 | 0.37079 | -121.7377 | 121.582 | 121.5179 | 48.4222 | -121.7056
1627.8906 | 121.788 | -0.36163 | 121.3669 | -0.14221 | 0.044419 | 0.061182 | 0.0036145 | 0.066285 | 0.003591 | 0.021247 | -0.19196 | 0.00077545 | 0.091997 | 0.080218 | 0.0093631 | -0.0078891 | -0.068665 | -0.10071 | -0.10071 | -0.14191 | -0.004578 | -0.25635 | -0.40283 | 7.0312 | 49.2828 | -0.21973 | 121.2982 | 121.2204 | -0.37079 | -0.37994 | 0.10528 | -0.041199 | -121.3715 | 0.26092 | 0.21973 | 0.26093 | -121.4355 | -0.009156 | -0.018311 | -0.068664 | 7.3929 | 0.14191 | 0.16022 | -0.14648 | 0.35705 | 0.29297 | 0.26092 | -121.7697 | 121.6599 | 121.582 | 49.6445 | -121.7468
1629.6406 | 121.8063 | -0.3479 | 121.3669 | 0.08667 | 0.040146 | 0.0599 | 0.0031873 | 0.069917 | -0.0058084 | 0.021461 | 0.090332 | 0.00056185 | 0.093278 | 0.081072 | 0.0063723 | -0.0025485 | -0.068665 | -0.045776 | -0.045776 | -0.15106 | -0.082397 | -0.23346 | -0.36163 | 7.3334 | 51.9104 | -0.15106 | 121.2479 | 121.2524 | -0.32044 | -0.33417 | 0.11444 | -0.013733 | -121.4493 | 0.30212 | 0.19684 | 0.21057 | -121.4355 | 0.027465 | 0.013733 | -0.11902 | 7.6813 | 0.19684 | 0.1831 | -0.11444 | 0.2655 | 0.27924 | 0.30212 | -121.7285 | 121.5958 | 121.6003 | 52.2583 | -121.701
1631.3281 | 121.8567 | -0.32959 | 121.3669 | -0.10406 | 0.038864 | 0.061395 | 0.0061781 | 0.071412 | -0.0075174 | 0.022315 | -0.085144 | -0.0026426 | 0.097337 | 0.079577 | 0.0044497 | -0.0048983 | -0.082397 | -0.018311 | -0.027466 | -0.12817 | -0.086975 | -0.24261 | -0.36621 | 7.6355 | 52.9953 | -0.086975 | 121.2616 | 121.2204 | -0.32959 | -0.35706 | 0.086975 | -0.036621 | -121.4539 | 0.31128 | 0.20142 | 0.23804 | -121.4493 | 0 | -0.027466 | -0.10529 | 7.9651 | 0.24261 | 0.27008 | -0.14648 | 0.24261 | 0.24719 | 0.30212 | -121.7331 | 121.5912 | 121.55 | 53.3249 | -121.7239
1633.1094 | 121.8384 | -0.3479 | 121.3531 | 0.033264 | 0.042069 | 0.061609 | 0.0085279 | 0.072694 | -0.0021768 | 0.02381 | 0.067444 | 0.00056185 | 0.10503 | 0.082354 | 0.0040225 | -0.0046847 | -0.10529 | -0.086975 | -0.07782 | -0.17395 | -0.10529 | -0.25177 | -0.37079 | 7.7728 | 54.744 | -0.14648 | 121.257 | 121.2021 | -0.34332 | -0.36621 | 0.09613 | -0.022889 | -121.4584 | 0.26092 | 0.17395 | 0.19684 | -121.4584 | 0.004577 | -0.018311 | -0.09613 | 8.1207 | 0.20142 | 0.21973 | -0.15106 | 0.24261 | 0.24261 | 0.27008 | -121.7239 | 121.6049 | 121.55 | 55.0919 | -121.7194
1634.7969 | 121.8246 | -0.37537 | 121.3211 | 0.071411 | 0.038437 | 0.058832 | 0.0066053 | 0.079743 | -0.0045266 | 0.026801 | 0.067444 | -7.8952e-05 | 0.11571 | 0.083208 | 0.0061587 | -0.0031893 | -0.11444 | -0.07782 | -0.10071 | -0.21057 | -0.13275 | -0.27008 | -0.40741 | 8.3084 | 57.5592 | -0.17395 | 121.225 | 121.1609 | -0.37994 | -0.41199 | 0.10528 | -0.032044 | -121.4539 | 0.29755 | 0.16479 | 0.19684 | -121.4355 | -0.004578 | -0.036621 | -0.09613 | 8.6838 | 0.20142 | 0.23804 | -0.16022 | 0.24261 | 0.26092 | 0.27466 | -121.7285 | 121.6003 | 121.5363 | 57.9346 | -121.7331
1636.5469 | 121.8246 | -1.0345 | 120.694 | -0.18036 | 0.034165 | 0.055627 | 0.021345 | 0.15366 | -0.002604 | 0.061622 | -0.1767 | 0.0016298 | 0.23577 | 0.085131 | 0.010218 | -0.0029757 | -0.4715 | -0.42572 | -0.4303 | -0.6546 | -0.50812 | -0.89264 | -1.0254 | 8.1528 | 76.0986 | -0.70038 | 120.5612 | 120.5246 | -0.99792 | -1.0437 | 0.14191 | 0.009155 | -121.2021 | 0.60883 | 0.37994 | 0.37079 | -121.1655 | 0.036621 | -0.009155 | -0.13275 | 9.1873 | 0.33417 | 0.34332 | -0.16937 | 0.52643 | 0.56305 | 0.60425 | -121.7194 | 121.5958 | 121.5591 | 77.1332 | -121.7377
1638.2969 | 121.8796 | -0.32044 | 121.376 | 0.0027468 | 0.036301 | 0.060114 | 0.0040417 | 0.059663 | -0.0058084 | 0.022956 | 0.029297 | 0.0024844 | 0.094774 | 0.083636 | 0.0044497 | -0.00062592 | -0.10529 | -0.091553 | -0.068665 | -0.14191 | -0.07782 | -0.19226 | -0.34332 | 9.0958 | 93.0862 | -0.091553 | 121.3257 | 121.2662 | -0.29755 | -0.30212 | 0.12817 | -0.022888 | -121.4539 | 0.22888 | 0.17853 | 0.20142 | -121.4813 | 0.022889 | 0.018311 | -0.050354 | 9.4162 | 0.22888 | 0.21057 | -0.10986 | 0.24262 | 0.21515 | 0.25177 | -121.7194 | 121.6461 | 121.5866 | 93.4067 | -121.6782
1639.9844 | 121.8658 | -0.29297 | 121.3989 | 0.11719 | 0.039933 | 0.058832 | 0.0019055 | 0.059022 | 0.0016684 | 0.024451 | 0.12848 | 0.00013465 | 0.09221 | 0.083422 | 0.0087223 | -0.0051119 | -0.027466 | -0.045776 | -0.036621 | -0.11902 | -0.09613 | -0.17853 | -0.32959 | 9.4391 | 91.3879 | -0.091553 | 121.3211 | 121.2845 | -0.27924 | -0.28381 | 0.11444 | -0.036621 | -121.4951 | 0.24719 | 0.17395 | 0.21057 | -121.4264 | 0.013733 | 0.009156 | -0.07782 | 9.7321 | 0.20142 | 0.19226 | -0.11444 | 0.19684 | 0.2655 | 0.25635 | -121.7285 | 121.6141 | 121.5775 | 91.6809 | -121.6827
1641.75 | 121.8887 | -0.30212 | 121.3943 | 0.018005 | 0.036087 | 0.060754 | 0.0061781 | 0.058167 | -0.0068766 | 0.025519 | 0.0064086 | 0.00013465 | 0.092638 | 0.082995 | 0.0059451 | -0.00083952 | -0.10529 | -0.09613 | -0.10529 | -0.16937 | -0.091553 | -0.21973 | -0.34332 | 9.0591 | 93.544 | -0.086975 | 121.3257 | 121.2891 | -0.31128 | -0.31128 | 0.082397 | -0.041199 | -121.4859 | 0.20599 | 0.13275 | 0.17395 | -121.4996 | -0.009155 | -0.009155 | -0.068664 | 9.3613 | 0.21515 | 0.2243 | -0.10529 | 0.21057 | 0.19684 | 0.19684 | -121.7377 | 121.6278 | 121.5912 | 93.8461 | -121.7056
1643.4844 | 121.7697 | -0.36163 | 121.4493 | -0.23376 | 0.043564 | 0.059686 | 0.0098097 | 0.061372 | -0.0019632 | 0.025306 | -0.1767 | -7.8952e-05 | 0.097337 | 0.086199 | 0.0055179 | 0.00022848 | -0.086975 | -0.10986 | -0.10071 | -0.18768 | -0.073242 | -0.24261 | -0.37994 | 9.3063 | 90.0513 | -0.19226 | 121.3486 | 121.312 | -0.32959 | -0.36621 | 0.11902 | -0.018311 | -121.5225 | 0.25177 | 0.17395 | 0.19226 | -121.5363 | 0.032043 | -0.004578 | -0.10071 | 9.668 | 0.16937 | 0.17395 | -0.13733 | 0.28839 | 0.27466 | 0.26092 | -121.8292 | 121.7102 | 121.6736 | 90.4129 | -121.8155
1645.2344 | 121.8613 | -0.33875 | 121.3852 | 0.10193 | 0.04036 | 0.057764 | 0.0036145 | 0.058595 | 0.001882 | 0.027228 | 0.014038 | 0.0020572 | 0.10268 | 0.087694 | 0.011713 | 1.4884e-05 | -0.14191 | -0.20142 | -0.19226 | -0.23346 | -0.054932 | -0.25635 | -0.39825 | 10.0342 | 92.8757 | -0.45319 | 121.344 | 121.2845 | -0.32501 | -0.38452 | 0.082397 | -0.059509 | -121.4401 | 0.13733 | 0.10529 | 0.16479 | -121.5271 | 0.013733 | -0.045776 | -0.041199 | 10.3729 | -0.11444 | -0.068665 | -0.10071 | 0.28381 | 0.19684 | 0.14648 | -121.7834 | 121.6827 | 121.6232 | 93.2144 | -121.7697
1647.0312 | 121.7697 | -0.36163 | 121.4081 | -0.096436 | 0.038864 | 0.059045 | 0.0068189 | 0.062226 | 0.0038046 | 0.029365 | -0.16144 | 0.0037662 | 0.10503 | 0.083849 | 0.010645 | -0.00062592 | -0.10071 | -0.11444 | -0.1236 | -0.20599 | -0.082397 | -0.25635 | -0.40283 | 10.8856 | 94.5328 | -0.064087 | 121.2936 | 121.2341 | -0.35706 | -0.38452 | 0.10528 | -0.041199 | -121.4905 | 0.24719 | 0.15564 | 0.19684 | -121.5088 | 0.004577 | -0.022888 | -0.11444 | 11.2473 | 0.29755 | 0.32043 | -0.17395 | 0.27924 | 0.26092 | 0.23804 | -121.8109 | 121.6553 | 121.5958 | 94.8944 | -121.7926
1648.7188 | 121.8018 | -0.42572 | 121.376 | -0.21851 | 0.041428 | 0.060541 | 0.01045 | 0.059449 | -0.00046778 | 0.034278 | -0.19958 | 0.0024844 | 0.11229 | 0.085131 | 0.010218 | 0.0068509 | -0.20599 | -0.21515 | -0.21057 | -0.2655 | -0.11444 | -0.32501 | -0.4303 | 10.9314 | 92.1295 | -0.16022 | 121.3074 | 121.2158 | -0.42114 | -0.42114 | 0.10071 | -0.004578 | -121.4905 | 0.21057 | 0.16022 | 0.1648 | -121.582 | 0.004577 | 0.004577 | -0.068665 | 11.3571 | 0.2655 | 0.26093 | -0.16022 | 0.31128 | 0.21973 | 0.21515 | -121.8063 | 121.7331 | 121.6415 | 92.5552 | -121.7972
1650.4688 | 121.7834 | -0.4303 | 121.3806 | -0.21088 | 0.041428 | 0.060968 | 0.011518 | 0.059449 | -0.0053812 | 0.035132 | -0.19958 | 0.0020572 | 0.11528 | 0.084276 | 0.0057315 | 0.0068509 | -0.17395 | -0.12817 | -0.13275 | -0.21973 | -0.16937 | -0.28381 | -0.44403 | 9.8877 | 91.0126 | -0.13275 | 121.2662 | 121.2067 | -0.39825 | -0.43488 | 0.14649 | -0.013733 | -121.55 | 0.30212 | 0.21057 | 0.2243 | -121.5546 | 0.032044 | -0.004577 | -0.11444 | 10.318 | 0.29755 | 0.30212 | -0.17395 | 0.26093 | 0.25635 | 0.29755 | -121.8246 | 121.6965 | 121.637 | 91.4429 | -121.8155
1652.2188 | 121.8567 | -0.42114 | 121.3074 | 0.08667 | 0.039719 | 0.0599 | 0.0070325 | 0.057527 | -0.006022 | 0.035132 | 0.12085 | -0.00050635 | 0.11742 | 0.08684 | 0.0078677 | 0.0096281 | -0.16022 | -0.11902 | -0.11444 | -0.23804 | -0.16479 | -0.28381 | -0.41199 | 10.0204 | 92.1661 | -0.073242 | 121.2296 | 121.1792 | -0.37994 | -0.41657 | 0.13733 | 0.009156 | -121.4722 | 0.30212 | 0.18311 | 0.17395 | -121.4676 | 0.041199 | 0.004578 | -0.07782 | 10.4416 | 0.3479 | 0.34332 | -0.12817 | 0.25635 | 0.26093 | 0.3067 | -121.7194 | 121.6507 | 121.6003 | 92.5873 | -121.7239
1653.9062 | 121.8704 | -0.39825 | 121.3303 | 0.033264 | 0.037583 | 0.058832 | 0.0053235 | 0.057527 | -0.0051676 | 0.035132 | 0.067444 | 0.00098905 | 0.11699 | 0.08449 | 0.010431 | 0.010269 | -0.1831 | -0.16022 | -0.16479 | -0.2655 | -0.17853 | -0.29297 | -0.41657 | 10.405 | 89.0625 | -0.082397 | 121.2204 | 121.1884 | -0.39825 | -0.41199 | 0.10529 | -0.018311 | -121.5088 | 0.23804 | 0.13275 | 0.15106 | -121.5134 | 0 | -0.013733 | -0.10986 | 10.8032 | 0.31586 | 0.32959 | -0.14191 | 0.21973 | 0.21515 | 0.23346 | -121.7468 | 121.6187 | 121.5866 | 89.4608 | -121.7422
1655.6719 | 121.7834 | -0.48981 | 121.344 | -0.25665 | 0.040573 | 0.059686 | 0.0098097 | 0.059449 | -0.001536 | 0.038978 | -0.15381 | 0.0031252 | 0.12746 | 0.08449 | 0.010218 | 0.012191 | -0.21973 | -0.2243 | -0.21057 | -0.29755 | -0.19226 | -0.3479 | -0.48065 | 10.8856 | 90.3992 | -0.13733 | 121.2296 | 121.17 | -0.45319 | -0.47607 | 0.14191 | 0.009155 | -121.5363 | 0.2655 | 0.19226 | 0.18311 | -121.5637 | 0.036621 | 0.013733 | -0.11444 | 11.3754 | 0.35248 | 0.33874 | -0.17395 | 0.29755 | 0.27008 | 0.27924 | -121.8246 | 121.7194 | 121.6599 | 90.889 | -121.8201
1657.3594 | 121.8521 | -0.93384 | 120.7809 | 0.10193 | 0.034806 | 0.055627 | 0.010664 | 0.096406 | -0.0030314 | 0.075507 | 0.097962 | 0.0035524 | 0.18984 | 0.085345 | 0.012781 | -0.00083952 | -0.50354 | -0.49439 | -0.50354 | -0.68665 | -0.53558 | -0.81024 | -0.93842 | 11.9659 | 32.7896 | -0.58136 | 120.6802 | 120.6436 | -0.90179 | -0.93842 | 0.1236 | -0.004578 | -121.3165 | 0.43945 | 0.24719 | 0.25177 | -121.2845 | 0.032044 | -0.004578 | -0.10071 | 12.8998 | 0.35248 | 0.35706 | -0.13733 | 0.39825 | 0.4303 | 0.4303 | -121.7194 | 121.6141 | 121.5775 | 33.7234 | -121.7194
1659.1094 | 121.8201 | -2.1881 | 119.5404 | -0.20325 | 0.0098118 | 0.035974 | 0.064711 | 0.22223 | -0.00089518 | 0.045173 | -0.16907 | 0.00056185 | 0.33574 | 0.091967 | 0.01449 | 0.014968 | -0.74616 | -0.70953 | -0.68665 | -1.387 | -0.7782 | -2.0416 | -2.1744 | 13.266 | 100.2274 | -1.6251 | 119.426 | 119.3939 | -2.1652 | -2.1698 | 0.14648 | 0.013733 | -120.3186 | 1.4786 | 0.80109 | 0.78735 | -120.2866 | 0.022888 | 0.01831 | -0.11444 | 15.4541 | 0.56305 | 0.54474 | -0.14648 | 1.4099 | 1.442 | 1.5015 | -121.7148 | 121.6141 | 121.582 | 102.4155 | -121.7102
1660.8125 | 121.9116 | -2.2476 | 119.4489 | -0.21851 | -0.012405 | 0.047083 | 0.10145 | 0.39868 | 0.0012412 | 0.052222 | -0.016479 | 0.00034825 | 0.46434 | 0.089831 | 0.018122 | 0.0186 | -1.1353 | -0.98419 | -1.0895 | -2.2522 | -1.0483 | -3.154 | -3.2913 | 15.3488 | 113.118 | -2.6047 | 119.1971 | 119.1834 | -2.4536 | -2.3666 | -0.90637 | -1.0437 | -120.4971 | 1.2634 | -0.004577 | 1.0391 | -120.5841 | -0.20599 | -0.11902 | -0.25177 | 17.5964 | -0.35705 | -0.23804 | -0.2655 | 1.1993 | 1.1124 | 1.1581 | -122.7402 | 121.4447 | 121.431 | 115.3656 | -121.8155
1662.5625 | 121.8658 | -0.64087 | 121.1014 | 0.079041 | 0.031601 | 0.055627 | 0.016859 | 0.086366 | 0.0044454 | 0.019111 | 0.029297 | 0.0048342 | 0.14839 | 0.091112 | 0.016626 | 0.015396 | -0.19684 | -0.25177 | -0.24261 | -0.41657 | -0.1236 | -0.59052 | -0.72784 | 15.5319 | 119.8837 | -0.33417 | 121.0007 | 120.9641 | -0.66376 | -0.68207 | 0.050354 | -0.086975 | -121.225 | 0.3891 | 0.2243 | 0.31128 | -121.2982 | -0.022888 | -0.041199 | -0.10071 | 16.1728 | 0.3067 | 0.3479 | -0.13733 | 0.51727 | 0.44403 | 0.39825 | -121.8292 | 121.6415 | 121.6049 | 120.5246 | -121.7834
1664.25 | 121.8384 | -2.1286 | 119.6228 | -0.088806 | 0.013443 | 0.036401 | 0.058516 | 0.2186 | 0.0040182 | 0.035132 | -0.22247 | 0.0039798 | 0.30882 | 0.098376 | 0.017694 | 0.03099 | -0.59967 | -0.61798 | -0.63629 | -1.2863 | -0.59052 | -1.8814 | -1.9913 | 16.9235 | 117.2928 | -1.2497 | 119.8746 | 119.8105 | -1.7258 | -1.7395 | 0.24719 | 0.13733 | -120.2133 | 1.5106 | 0.84229 | 0.70496 | -120.2225 | 0.40283 | 0.3891 | 0.25177 | 19.0521 | 0.87891 | 0.48981 | 0.18768 | 1.5381 | 1.5289 | 1.4923 | -121.6141 | 122.0032 | 121.9391 | 119.4214 | -121.3623
1666.0156 | 121.6965 | -7.7728 | 113.887 | -0.027771 | -0.054275 | -0.019781 | 0.18306 | 0.77722 | 0.014272 | 0.24512 | -0.054626 | 0.0054752 | 1.1676 | 0.10799 | 0.02688 | 0.042312 | -3.479 | -3.5431 | -3.5019 | -5.6076 | -3.3966 | -7.5806 | -7.7133 | 12.9822 | 105.6152 | -7.2601 | 113.7497 | 113.6993 | -7.7087 | -7.7271 | 0.19226 | 0.059509 | -117.2836 | 4.2297 | 2.1652 | 2.1057 | -117.366 | 0.064087 | 0.045776 | -0.13733 | 20.755 | 0.5127 | 0.46692 | -0.18768 | 4.3762 | 4.2938 | 4.2709 | -121.6003 | 121.5225 | 121.4722 | 113.3881 | -121.6141
1667.7656 | 121.669 | -17.7658 | 103.7201 | -0.14221 | 0.078598 | 0.012048 | 0.021132 | 1.206 | 0.0010276 | 1.959 | -0.14618 | 0.0056888 | 3.3918 | 0.11931 | 0.040125 | 0.039962 | -15.1245 | -15.0009 | -15.0146 | -16.6077 | -9.0317 | -16.9601 | -17.0654 | 12.7899 | 99.5132 | -15.4587 | 104.3243 | 104.3106 | -16.7313 | -16.7725 | 0.80566 | 0.70038 | -112.7518 | 2.7649 | 1.1581 | 0.45776 | -118.8446 | 1.0345 | 0.99335 | 0.60425 | 30.5557 | 2.3071 | 1.3138 | 0.59051 | 8.7341 | 2.6413 | 2.7512 | -120.7855 | 122.0901 | 122.0764 | 117.2791 | -120.4926
1669.4531 | 120.845 | -75.737 | 44.7601 | -0.20325 | 0.22621 | -0.11442 | 0.0031873 | 5.1787 | 0.0027364 | 7.0381 | -0.085144 | 0.0050478 | 7.061 | 0.11696 | 0.023462 | 0.064315 | -71.7957 | -71.2967 | -71.1365 | -73.3521 | -9.0454 | -74.6521 | -74.469 | -36.8591 | 30.2628 | -75.3113 | 43.4372 | 43.2861 | -75.8469 | -75.9933 | 1.0849 | 1.268 | -53.8055 | 4.4403 | 2.3849 | 1.1169 | -116.5558 | -0.10986 | -0.25635 | -1.3229 | 38.8779 | 0.42572 | 0.68207 | -1.474 | 66.6916 | 3.9413 | 4.6005 | -119.2291 | 119.1742 | 119.0231 | 105.9998 | -120.7535
1671.2188 | 121.4447 | -116.185 | 4.9301 | -0.13458 | 0.042069 | 0.060327 | 0.0019055 | 0.027833 | -0.0058084 | 0.03855 | 0.021668 | 0.0033388 | 0.75572 | 0.14067 | 0.025171 | 0.090805 | 0.086975 | 0.15564 | 0.14648 | 0.082397 | 0.041199 | 0.059509 | -0.082397 | -70.6055 | 1.3824 | -116.1118 | 4.5639 | 4.5685 | -116.4459 | -116.6107 | 116.2445 | 116.1026 | -4.8889 | 116.3406 | 116.2674 | 0.16479 | -4.8431 | -0.26093 | -0.42572 | -0.36621 | 45.5795 | 0.073243 | 0.49896 | -0.36163 | 116.2262 | 116.272 | 116.3315 | -5.0125 | 120.7489 | 120.7535 | 117.5674 | -121.5408
1672.9375 | 120.8908 | -68.1564 | 52.5558 | -0.12695 | 0.042923 | 0.062891 | 0.0031873 | 0.0064707 | -0.0058084 | 0.062263 | -0.016479 | 0.036023 | 6.3441 | 6.0247 | 0.018976 | 0.039962 | -0.56305 | -0.54932 | -0.54474 | -0.60425 | -0.59052 | -0.60425 | -0.72784 | -22.3022 | 18.8599 | -62.5946 | 57.193 | 56.781 | -62.9974 | -63.5788 | 67.5522 | 67.4286 | -53.1464 | 67.6071 | 67.5522 | 0.1236 | -53.1189 | 5.159 | 4.5776 | 4.6371 | 45.8542 | 5.5618 | 0.98419 | 4.2252 | 67.5659 | 67.5934 | 67.6117 | -53.2837 | 125.3494 | 124.9374 | 87.0163 | -116.1346
1674.7031 | 120.9274 | -0.26093 | 120.9503 | -0.11169 | 0.046555 | 0.061395 | 0.0021191 | 0.031251 | 0.003591 | 0.036201 | -0.11566 | 0.039228 | 0.030901 | 0.065264 | 0.0016727 | 0.020736 | 0.054932 | 0.032043 | 0.027466 | 0.022888 | 0.09613 | 0.009155 | -0.11902 | 0.013733 | -0.041199 | -0.2243 | 0.032043 | 0 | -0.20599 | -0.28839 | 0.27008 | 0.14191 | -120.8542 | 0.29297 | 0.28381 | 0.14191 | -120.8954 | 0.054931 | -0.027466 | -120.9183 | 0.27466 | 0.036621 | 0.064087 | -120.9503 | 0.35706 | 0.31586 | 0.28839 | -121.0693 | 0.29297 | 0.26093 | 0.21973 | -121.2387
1676.3906 | 121.3486 | -0.1831 | 121.0236 | 0.14008 | 0.040146 | 0.060541 | 0.00019645 | 0.035096 | 0.00081382 | 0.035132 | 0.14374 | 0.044782 | 0.020433 | 0.065478 | 0.0025271 | 0.025436 | 0.032043 | 0.032043 | 0.041199 | -0.004578 | 0.059509 | 0.036621 | -0.086975 | 0.050354 | 0.041199 | -0.11444 | -0.041199 | -0.045776 | -0.11902 | -0.16022 | 0.21973 | 0.09613 | -120.9641 | 0.21515 | 0.17853 | 0.082397 | -120.9915 | 0.064086 | 0.022888 | -121.0648 | 0.23346 | 0.068664 | 0.045776 | -121.0693 | 0.24261 | 0.21515 | 0.2243 | -121.1105 | 0.14191 | 0.13733 | 0.2243 | -121.1838
1678.1406 | 121.2845 | -0.21515 | 121.1197 | -0.18799 | 0.041001 | 0.062891 | 0.0036145 | 0.035737 | -0.0058084 | 0.033851 | -0.1767 | 0.043927 | 0.022996 | 0.065905 | -0.0021725 | 0.024795 | 0.082397 | 0.11444 | 0.091553 | 0.054932 | 0.059509 | 0.054932 | -0.09613 | 0.004578 | 0.082397 | -0.11902 | -0.036621 | -0.068665 | -0.15106 | -0.20599 | 0.27008 | 0.11902 | -121.0602 | 0.32959 | 0.27008 | 0.15106 | -121.0373 | 0.064087 | 0.009155 | -121.1563 | 0.21973 | 0.09613 | 0.086975 | -121.1884 | 0.27466 | 0.29755 | 0.3067 | -121.2158 | 0.17853 | 0.14648 | 0.29755 | -121.3257
1679.8281 | 121.344 | -0.2243 | 121.1197 | -0.21088 | 0.044419 | 0.063532 | 0.0031873 | 0.033814 | -0.0047404 | 0.034278 | -0.10803 | 0.043714 | 0.022356 | 0.065905 | -0.00024989 | 0.024582 | 0.082397 | 0.12817 | 0.1236 | 0.068665 | 0.027466 | 0.050354 | -0.086975 | 0.009155 | 0.082397 | -0.11902 | -0.073242 | -0.09613 | -0.16479 | -0.20599 | 0.27466 | 0.13733 | -121.0922 | 0.35248 | 0.29297 | 0.15564 | -121.0373 | 0.059509 | 0.01831 | -121.1929 | 0.23346 | 0.10529 | 0.086975 | -121.2158 | 0.25177 | 0.3067 | 0.3479 | -121.2067 | 0.15106 | 0.12817 | 0.3067 | -121.3257
1681.5781 | 121.4035 | -0.24261 | 121.0968 | -0.20325 | 0.043137 | 0.060754 | 0.0027601 | 0.034242 | -0.004954 | 0.032783 | -0.12329 | 0.044354 | 0.020647 | 0.063982 | -0.0017453 | 0.024368 | 0.09613 | 0.13275 | 0.12817 | 0.064087 | 0.050354 | 0.054932 | -0.082397 | -0.004578 | 0.064087 | -0.13733 | -0.082397 | -0.10986 | -0.16937 | -0.2243 | 0.29755 | 0.16022 | -121.0464 | 0.37537 | 0.3067 | 0.14648 | -121.0007 | 0.073242 | 0.018311 | -121.1792 | 0.23804 | 0.10529 | 0.086975 | -121.2067 | 0.29297 | 0.33874 | 0.37079 | -121.1792 | 0.16022 | 0.13275 | 0.3067 | -121.3211
1683.3281 | 121.376 | -0.26093 | 121.1472 | 0.14008 | 0.045487 | 0.062677 | -0.0010851 | 0.034669 | 0.00081382 | 0.034919 | -0.031738 | 0.047772 | 0.019151 | 0.065905 | 0.0046633 | 0.0233 | 0.027466 | -0.036621 | -0.022888 | -0.022888 | 0.07782 | 0.022888 | -0.12817 | -0.13733 | -0.1236 | -0.28839 | -0.068665 | -0.068665 | -0.20142 | -0.28381 | 0.28381 | 0.13275 | -121.0693 | 0.2243 | 0.23804 | 0.10529 | -121.1197 | 0.059509 | -0.022888 | -121.2158 | 0.1236 | -0.027466 | -0.004578 | -121.2158 | 0.33875 | 0.28839 | 0.23804 | -121.2753 | 0.19226 | 0.19226 | 0.13733 | -121.431
1685.0938 | 121.4035 | -0.28381 | 121.138 | 0.048523 | 0.044846 | 0.062463 | -0.00023075 | 0.03296 | 0.0016684 | 0.035346 | -0.046997 | 0.050122 | 0.018297 | 0.064837 | 0.0020999 | 0.026291 | -0.004578 | -0.054932 | -0.027466 | -0.027466 | 0.07782 | 0.022888 | -0.1236 | -0.15564 | -0.13275 | -0.3067 | -0.07782 | -0.10529 | -0.2243 | -0.29755 | 0.3067 | 0.16022 | -121.0602 | 0.22888 | 0.25635 | 0.09613 | -121.1426 | 0.059509 | -0.013733 | -121.2158 | 0.12817 | -0.022889 | -0.009156 | -121.2433 | 0.36163 | 0.27923 | 0.25635 | -121.2616 | 0.20599 | 0.17853 | 0.15106 | -121.4355
1686.7969 | 121.4172 | -0.32044 | 121.1426 | -0.18799 | 0.042923 | 0.062891 | 0.0059643 | 0.032319 | -0.0062356 | 0.033423 | -0.22247 | 0.048413 | 0.018083 | 0.064623 | -0.0034543 | 0.025436 | 0.054932 | 0.10071 | 0.091553 | 0.036621 | 0.050354 | 0.027466 | -0.10529 | -0.10529 | 0.004578 | -0.21515 | -0.10529 | -0.13275 | -0.24719 | -0.29297 | 0.3479 | 0.21515 | -121.0922 | 0.42114 | 0.35706 | 0.14191 | -121.0876 | 0.073243 | 0.027466 | -121.2479 | 0.21515 | 0.10529 | 0.07782 | -121.2753 | 0.37079 | 0.37537 | 0.41199 | -121.2479 | 0.21515 | 0.18768 | 0.32501 | -121.4355
1688.5469 | 121.4355 | -0.31128 | 121.1472 | 0.0027468 | 0.046982 | 0.060968 | 0.00062385 | 0.032319 | -4.058e-05 | 0.036841 | -0.024109 | 0.051618 | 0.01552 | 0.066546 | 0.0027407 | 0.02565 | 0.013733 | -0.027466 | -0.018311 | -0.013733 | 0.086975 | 0.022888 | -0.13275 | -0.20142 | -0.11444 | -0.32959 | -0.12817 | -0.15106 | -0.27008 | -0.35706 | 0.33417 | 0.17853 | -121.0602 | 0.28381 | 0.29755 | 0.11902 | -121.1334 | 0.041198 | -0.045777 | -121.2753 | 0.10986 | -0.018311 | 0.027466 | -121.2982 | 0.39825 | 0.32501 | 0.29297 | -121.2799 | 0.1831 | 0.16022 | 0.19684 | -121.5042
1690.25 | 121.5637 | -0.2655 | 121.0831 | 0.11719 | 0.042496 | 0.060541 | 0.0023329 | 0.032105 | -0.0047404 | 0.036414 | 0.159 | 0.048841 | 0.01787 | 0.065264 | -0.00089089 | 0.027145 | 0.09613 | 0.10071 | 0.11444 | 0.068665 | 0.050354 | 0.050354 | -0.073242 | -0.073242 | 0.045776 | -0.1831 | -0.19226 | -0.19226 | -0.25177 | -0.31586 | 0.31586 | 0.19226 | -121.0327 | 0.36621 | 0.33417 | 0.14191 | -120.9869 | 0.013733 | -0.050354 | -121.2753 | 0.19226 | 0.082398 | 0.13275 | -121.2753 | 0.31586 | 0.36163 | 0.37994 | -121.1563 | 0.073242 | 0.073242 | 0.31128 | -121.3989
1692.0625 | 121.582 | -0.28839 | 121.138 | -0.12695 | 0.038651 | 0.06225 | 0.0038281 | 0.032319 | -0.006663 | 0.031501 | -0.069885 | 0.049695 | 0.01552 | 0.0627 | -0.0017453 | 0.025863 | 0.10529 | 0.14191 | 0.11902 | 0.064087 | 0.050354 | 0.050354 | -0.09613 | -0.068665 | 0.10529 | -0.17395 | -0.17853 | -0.19684 | -0.27466 | -0.33417 | 0.33875 | 0.19226 | -121.0876 | 0.4303 | 0.35248 | 0.16022 | -121.0327 | 0.013733 | -0.045776 | -121.3165 | 0.21973 | 0.11444 | 0.16022 | -121.3348 | 0.33875 | 0.39368 | 0.40741 | -121.2341 | 0.10986 | 0.091553 | 0.39368 | -121.4722
1693.7969 | 121.5363 | -0.32501 | 121.17 | -0.10406 | 0.047623 | 0.060327 | 0.0061781 | 0.032746 | 0.00060022 | 0.034492 | -0.1767 | 0.047986 | 0.021715 | 0.065691 | 0.00060451 | 0.024582 | 0.050354 | 0.022888 | 0.027466 | 0.036621 | 0.091553 | 0.013733 | -0.11902 | -0.13733 | 0 | -0.27924 | -0.15564 | -0.17395 | -0.27924 | -0.36163 | 0.33875 | 0.20599 | -121.0785 | 0.3479 | 0.36163 | 0.15564 | -121.1197 | 0.045776 | -0.036621 | -121.3257 | 0.18768 | 0.045776 | 0.082397 | -121.344 | 0.41657 | 0.37537 | 0.35248 | -121.2891 | 0.16937 | 0.15106 | 0.32501 | -121.5317
1695.5312 | 121.582 | -0.31586 | 121.1426 | 0.094299 | 0.040573 | 0.061823 | -1.7146e-05 | 0.03296 | -0.004313 | 0.032996 | 0.10559 | 0.046491 | 0.021287 | 0.065905 | -0.0019589 | 0.027999 | 0.064087 | 0.10529 | 0.10529 | 0.032043 | 0.027466 | 0.050354 | -0.10071 | -0.1236 | -0.009155 | -0.24261 | -0.19226 | -0.21057 | -0.27008 | -0.32044 | 0.36621 | 0.21515 | -121.1151 | 0.42114 | 0.3479 | 0.13275 | -121.0785 | 0.045776 | -0.004578 | -121.3348 | 0.19226 | 0.073242 | 0.07782 | -121.3531 | 0.34332 | 0.37994 | 0.42114 | -121.2433 | 0.1236 | 0.10529 | 0.3067 | -121.463
1697.2812 | 121.4996 | -0.37079 | 121.1746 | -0.073547 | 0.04506 | 0.060114 | 0.0023329 | 0.034669 | 0.0010276 | 0.035132 | -0.10803 | 0.05055 | 0.020433 | 0.065264 | 0.0029543 | 0.025863 | 0.041199 | 0.032043 | 0.022888 | 0.004578 | 0.082397 | 0.009155 | -0.1236 | -0.20142 | -0.11444 | -0.35248 | -0.18768 | -0.19684 | -0.32044 | -0.37079 | 0.37994 | 0.24719 | -121.0922 | 0.40283 | 0.37537 | 0.12817 | -121.1334 | 0.050354 | 0 | -121.3623 | 0.16937 | 0.018311 | 0.018311 | -121.3715 | 0.45319 | 0.41199 | 0.39368 | -121.2982 | 0.18311 | 0.17395 | 0.25635 | -121.5454
1698.9844 | 121.6553 | -0.32044 | 121.1334 | 0.08667 | 0.042282 | 0.061823 | 0.00019645 | 0.032746 | -0.0011088 | 0.032569 | 0.12085 | 0.049481 | 0.016801 | 0.065905 | 0.0027407 | 0.026504 | 0.018311 | -0.009155 | -0.009155 | -0.004578 | 0.07782 | 0.022888 | -0.1236 | -0.19684 | -0.14191 | -0.31586 | -0.1831 | -0.2243 | -0.32959 | -0.37537 | 0.34332 | 0.19684 | -121.0556 | 0.31128 | 0.31586 | 0.11902 | -121.1151 | -0.009155 | -0.054931 | -121.3165 | 0.1236 | 0.004578 | 0.059509 | -121.3577 | 0.39826 | 0.33875 | 0.31128 | -121.257 | 0.13733 | 0.096131 | 0.17853 | -121.5088
1700.7344 | 121.669 | -0.34332 | 121.1243 | 0.14771 | 0.041642 | 0.06225 | 0.00062385 | 0.033387 | -0.0045266 | 0.034705 | 0.097962 | 0.048627 | 0.016374 | 0.063555 | 0.0014591 | 0.026077 | 0.073242 | 0.082397 | 0.091553 | 0.059509 | 0.050354 | 0.045776 | -0.091553 | -0.13275 | -0.07782 | -0.2655 | -0.25177 | -0.25177 | -0.31586 | -0.36163 | 0.3891 | 0.25177 | -121.0739 | 0.42572 | 0.40283 | 0.15106 | -121.051 | 0.027466 | -0.01831 | -121.376 | 0.21057 | 0.07782 | 0.09613 | -121.376 | 0.39368 | 0.41656 | 0.43488 | -121.2158 | 0.091553 | 0.091553 | 0.2655 | -121.4859
1702.4531 | 121.637 | -0.37537 | 121.1655 | 0.10193 | 0.043564 | 0.059686 | 0.0010511 | 0.032319 | -0.001536 | 0.035346 | 0.052185 | 0.050122 | 0.017229 | 0.063982 | 0.0016727 | 0.026931 | -0.004578 | -0.032043 | -0.022888 | -0.022888 | 0.091553 | 0.013733 | -0.12817 | -0.24261 | -0.19684 | -0.3891 | -0.21973 | -0.23804 | -0.35706 | -0.42572 | 0.3891 | 0.24719 | -121.0739 | 0.34332 | 0.35248 | 0.10529 | -121.17 | 0.01831 | -0.050354 | -121.3852 | 0.13275 | -0.013733 | 0.036621 | -121.4035 | 0.46692 | 0.37079 | 0.35248 | -121.2936 | 0.15564 | 0.13733 | 0.17853 | -121.5912
1704.1875 | 121.6782 | -0.37994 | 121.138 | 0.094299 | 0.042069 | 0.065027 | 0.0031873 | 0.033814 | -0.0034586 | 0.035346 | 0.12848 | 0.047345 | 0.017442 | 0.061846 | 0.0012455 | 0.026077 | 0.082397 | 0.09613 | 0.09613 | 0.054932 | 0.041199 | 0.064087 | -0.091553 | -0.18768 | 0.073242 | -0.28839 | -0.27466 | -0.29297 | -0.32959 | -0.39825 | 0.44403 | 0.28839 | -121.0968 | 0.47607 | 0.43488 | 0.14649 | -121.0556 | 0.050354 | -0.01831 | -121.4127 | 0.19226 | 0.091553 | 0.10986 | -121.431 | 0.42114 | 0.46234 | 0.47607 | -121.2296 | 0.10529 | 0.086975 | 0.45319 | -121.5363
1705.9062 | 121.6324 | -0.43945 | 121.1105 | -0.18036 | 0.043564 | 0.060541 | 0.0029737 | 0.032746 | -0.0081582 | 0.032355 | -0.13855 | 0.046491 | 0.019792 | 0.062914 | -0.0017453 | 0.027786 | 0.07782 | 0.13733 | 0.13733 | 0.07782 | 0.050354 | 0.054932 | -0.086975 | -0.23346 | 0.11902 | -0.3067 | -0.31128 | -0.32501 | -0.37537 | -0.46234 | 0.49438 | 0.35248 | -121.0602 | 0.57678 | 0.51727 | 0.16479 | -121.0327 | 0.064087 | -0.022888 | -121.4218 | 0.20599 | 0.13275 | 0.15564 | -121.4355 | 0.48981 | 0.51727 | 0.57678 | -121.1975 | 0.12817 | 0.11444 | 0.55847 | -121.5729
1707.6562 | 121.6507 | -0.48523 | 121.0648 | -0.18036 | 0.042496 | 0.062463 | 0.0076733 | 0.033601 | -0.0064492 | 0.031928 | -0.16907 | 0.043927 | 0.018938 | 0.064837 | -0.0036679 | 0.025009 | 0.10529 | 0.10986 | 0.1236 | 0.064087 | 0.032043 | 0.032043 | -0.068665 | -0.27466 | 0.11444 | -0.36163 | -0.36621 | -0.36621 | -0.42114 | -0.48981 | 0.51727 | 0.41656 | -121.0327 | 0.59509 | 0.54932 | 0.13275 | -120.9595 | 0.064086 | -0.004578 | -121.431 | 0.21057 | 0.1236 | 0.12817 | -121.431 | 0.51727 | 0.59052 | 0.60883 | -121.1334 | 0.11902 | 0.11902 | 0.59967 | -121.5546
1709.375 | 121.6553 | -0.48065 | 121.0419 | 0.11719 | 0.044419 | 0.060327 | 0.0012647 | 0.033387 | 0.0014548 | 0.032996 | 0.029297 | 0.049909 | 0.020219 | 0.065264 | 0.0012455 | 0.023513 | 0.027466 | -0.050354 | -0.022888 | -0.004578 | 0.09613 | 0.013733 | -0.12817 | -0.38452 | -0.068665 | -0.50354 | -0.32501 | -0.36621 | -0.48065 | -0.51727 | 0.49439 | 0.35248 | -120.9457 | 0.4303 | 0.47607 | 0.1236 | -121.0144 | 0 | -0.036621 | -121.3669 | 0.096131 | -0.022888 | 0.013733 | -121.4081 | 0.57678 | 0.50812 | 0.45776 | -121.17 | 0.15564 | 0.11444 | 0.41199 | -121.5591
1711.1562 | 121.5912 | -0.52643 | 121.106 | -0.21851 | 0.040146 | 0.061609 | -1.7146e-05 | 0.033601 | -0.0062356 | 0.032355 | -0.21484 | 0.047345 | 0.017229 | 0.063982 | -0.0030271 | 0.025009 | 0.059509 | 0.086975 | 0.086975 | 0.036621 | 0.07782 | 0.036621 | -0.091553 | -0.32959 | 0.032043 | -0.44403 | -0.33417 | -0.35248 | -0.45319 | -0.52185 | 0.56305 | 0.43488 | -121.0281 | 0.6134 | 0.56305 | 0.12817 | -121.0464 | 0.073242 | 0.004577 | -121.4401 | 0.19684 | 0.082397 | 0.07782 | -121.4584 | 0.60425 | 0.58594 | 0.6134 | -121.1975 | 0.19226 | 0.17395 | 0.55847 | -121.6278
1712.9844 | 121.669 | -0.44403 | 121.106 | 0.071411 | 0.039292 | 0.065027 | -1.7146e-05 | 0.03061 | -0.0073038 | 0.032355 | 0.10559 | 0.047986 | 0.017442 | 0.062273 | -3.629e-05 | 0.029068 | 0.07782 | 0.07782 | 0.10071 | 0.032043 | 0.054932 | 0.054932 | -0.091553 | -0.27008 | 0.045776 | -0.37994 | -0.33417 | -0.35248 | -0.4303 | -0.48523 | 0.49896 | 0.35248 | -121.051 | 0.52185 | 0.47607 | 0.1236 | -121.0281 | 0.013733 | -0.041198 | -121.4401 | 0.17395 | 0.064087 | 0.10529 | -121.4584 | 0.49896 | 0.52185 | 0.54474 | -121.1975 | 0.10986 | 0.091553 | 0.48981 | -121.5912
1714.6875 | 121.6873 | -0.46234 | 121.0831 | 0.13245 | 0.041428 | 0.060754 | -0.00087155 | 0.031678 | -0.0021768 | 0.033851 | 0.10559 | 0.048627 | 0.015306 | 0.062914 | 0.0020999 | 0.024154 | 0.11902 | 0.10986 | 0.1236 | 0.054932 | 0.032043 | 0.059509 | -0.09613 | -0.24261 | 0.068665 | -0.36621 | -0.36163 | -0.37994 | -0.43488 | -0.4715 | 0.52185 | 0.36621 | -121.051 | 0.5722 | 0.51727 | 0.15106 | -120.9641 | 0.027466 | -0.009156 | -121.4447 | 0.21973 | 0.09613 | 0.10529 | -121.463 | 0.49438 | 0.58136 | 0.58594 | -121.1792 | 0.10071 | 0.082397 | 0.53101 | -121.5546
1716.4375 | 121.7377 | -0.45319 | 121.1288 | 0.11719 | 0.043564 | 0.060541 | 0.0023329 | 0.033387 | -0.00046778 | 0.034492 | 0.10559 | 0.0482 | 0.018724 | 0.067187 | -0.00024989 | 0.022873 | 0.045776 | -0.004578 | 0.027466 | 0.013733 | 0.086975 | 0.050354 | -0.10986 | -0.26093 | 0.018311 | -0.40283 | -0.32044 | -0.3479 | -0.42114 | -0.47607 | 0.50354 | 0.34332 | -121.0419 | 0.44861 | 0.46692 | 0.1236 | -121.0831 | 0.032043 | -0.022888 | -121.4493 | 0.19226 | 0.050354 | 0.073242 | -121.4767 | 0.54016 | 0.49896 | 0.48065 | -121.2387 | 0.13275 | 0.10529 | 0.4715 | -121.6049
1718.1875 | 121.6187 | -0.5127 | 121.17 | -0.0048827 | 0.043564 | 0.05755 | 0.0029737 | 0.031251 | 0.0012412 | 0.033423 | -0.0088499 | 0.047559 | 0.020647 | 0.064623 | 0.0048769 | 0.027359 | 0.032043 | -0.013733 | -0.009155 | -0.018311 | 0.073242 | 0.009155 | -0.11902 | -0.35706 | -0.050354 | -0.5127 | -0.3067 | -0.33417 | -0.44861 | -0.52643 | 0.52185 | 0.39368 | -121.0968 | 0.49896 | 0.49438 | 0.10071 | -121.138 | 0.064087 | -0.013733 | -121.4767 | 0.15564 | 0 | 0.013733 | -121.5042 | 0.58594 | 0.54474 | 0.50354 | -121.2891 | 0.20599 | 0.17853 | 0.46234 | -121.6965
1719.8906 | 121.637 | -0.49439 | 121.1334 | 0.048523 | 0.043991 | 0.060327 | 0.00083745 | 0.033174 | -0.00025418 | 0.033851 | 0.059815 | 0.047559 | 0.020006 | 0.063555 | 0.0027407 | 0.025009 | -0.018311 | -0.050354 | -0.018311 | -0.018311 | 0.068665 | 0.013733 | -0.1236 | -0.35706 | -0.068665 | -0.5127 | -0.33417 | -0.35706 | -0.46234 | -0.52185 | 0.50812 | 0.37079 | -121.0648 | 0.44403 | 0.47607 | 0.10528 | -121.1517 | 0.032044 | -0.027466 | -121.4676 | 0.13733 | -0.01831 | 0.009156 | -121.4905 | 0.56305 | 0.47607 | 0.47607 | -121.257 | 0.16022 | 0.13733 | 0.42572 | -121.6553
1721.6562 | 121.6232 | -0.49896 | 121.1472 | -0.081177 | 0.042923 | 0.0599 | 0.0023329 | 0.03531 | -0.0017496 | 0.034492 | -0.046997 | 0.046918 | 0.021074 | 0.067187 | 0.0023135 | 0.024154 | 0.032043 | 0.032043 | 0.018311 | 0.009155 | 0.064087 | 0.009155 | -0.13733 | -0.33417 | -0.009155 | -0.4715 | -0.32501 | -0.32501 | -0.43945 | -0.52185 | 0.50812 | 0.36163 | -121.0831 | 0.53101 | 0.50812 | 0.14648 | -121.1151 | 0.059509 | -0.022889 | -121.4722 | 0.1648 | 0.027465 | 0.050354 | -121.4722 | 0.56305 | 0.53101 | 0.51727 | -121.2845 | 0.17395 | 0.17395 | 0.48981 | -121.669
1723.3438 | 121.6415 | -0.50812 | 121.1792 | -0.21851 | 0.044419 | 0.06225 | 0.0076733 | 0.034883 | -0.0058084 | 0.034064 | -0.18433 | 0.044995 | 0.022569 | 0.063982 | -0.0030271 | 0.024154 | -0.009155 | 0.022888 | 0.027466 | -0.022888 | 0.064087 | 0.018311 | -0.12817 | -0.37537 | -0.009155 | -0.46234 | -0.32959 | -0.32501 | -0.4715 | -0.53101 | 0.52643 | 0.37994 | -121.1151 | 0.53101 | 0.48523 | 0.10529 | -121.1884 | 0.036621 | -0.022888 | -121.5088 | 0.13275 | 0.045777 | 0.068665 | -121.5042 | 0.5722 | 0.49896 | 0.53558 | -121.3074 | 0.17853 | 0.18311 | 0.49896 | -121.7102
1725.0938 | 121.6873 | -0.49439 | 121.1426 | -0.24139 | 0.041855 | 0.061395 | 0.0070325 | 0.030824 | -0.004313 | 0.032355 | -0.20721 | 0.049268 | 0.022783 | 0.065905 | -0.0028135 | 0.02565 | -0.013733 | -0.009155 | -0.009155 | -0.018311 | 0.09613 | 0.032043 | -0.14648 | -0.39368 | -0.032043 | -0.49439 | -0.32501 | -0.3479 | -0.4715 | -0.52185 | 0.52643 | 0.3479 | -121.0464 | 0.48523 | 0.47607 | 0.12817 | -121.1563 | 0.022888 | -0.027466 | -121.4676 | 0.10071 | 0 | 0.027466 | -121.4905 | 0.59052 | 0.48065 | 0.48523 | -121.2891 | 0.16937 | 0.14649 | 0.46234 | -121.6644
1726.8438 | 121.6827 | -0.4715 | 121.1746 | -0.11169 | 0.045914 | 0.060754 | 0.00041005 | 0.03296 | -4.058e-05 | 0.034278 | -0.13855 | 0.046063 | 0.021501 | 0.0627 | 0.0010317 | 0.023941 | 0.041199 | 0.045776 | 0.036621 | 0.013733 | 0.07782 | 0.036621 | -0.11902 | -0.29755 | 0.022888 | -0.42572 | -0.32044 | -0.35248 | -0.42114 | -0.51727 | 0.50812 | 0.35248 | -121.0968 | 0.51727 | 0.48523 | 0.13275 | -121.1334 | 0.050354 | -0.045776 | -121.4951 | 0.17395 | 0.045777 | 0.091553 | -121.5271 | 0.54932 | 0.5127 | 0.50812 | -121.2936 | 0.15106 | 0.11902 | 0.49439 | -121.6919
1728.5938 | 121.7148 | -0.50354 | 121.1609 | -0.17273 | 0.047837 | 0.061823 | 0.0057507 | 0.031678 | -0.00089518 | 0.033637 | -0.16907 | 0.047345 | 0.019365 | 0.064196 | 0.00081811 | 0.024795 | 0 | -0.009155 | 0.004578 | 0.009155 | 0.082397 | 0.009155 | -0.11902 | -0.35248 | 0.022888 | -0.47607 | -0.34332 | -0.35248 | -0.46234 | -0.53558 | 0.5127 | 0.38452 | -121.0785 | 0.49438 | 0.5127 | 0.12817 | -121.1609 | 0.041199 | -0.032043 | -121.5042 | 0.15106 | 0.027466 | 0.059509 | -121.5134 | 0.58594 | 0.50354 | 0.50812 | -121.2799 | 0.16022 | 0.15106 | 0.52643 | -121.6965
1730.2812 | 121.6644 | -0.52185 | 121.1655 | -0.012512 | 0.04271 | 0.060968 | 0.0014783 | 0.034455 | 0.0012412 | 0.033637 | 0.021668 | 0.050336 | 0.021715 | 0.062487 | 0.0014591 | 0.024795 | -0.018311 | -0.022888 | 0.004578 | 0 | 0.068665 | 0.022888 | -0.11444 | -0.40741 | -0.036621 | -0.54016 | -0.33875 | -0.36621 | -0.48981 | -0.54016 | 0.54474 | 0.40741 | -121.0968 | 0.49896 | 0.52185 | 0.11444 | -121.1838 | 0.032044 | -0.01831 | -121.5042 | 0.11444 | -0.01831 | 0 | -121.5317 | 0.59052 | 0.50354 | 0.52643 | -121.2799 | 0.18311 | 0.15564 | 0.48523 | -121.7056
1732.0312 | 121.7194 | -0.53558 | 121.1426 | -0.21088 | 0.042282 | 0.062891 | 0.0019055 | 0.036164 | -0.008372 | 0.033637 | -0.085144 | 0.045423 | 0.019151 | 0.062487 | -0.0015317 | 0.026931 | 0.054932 | 0.13275 | 0.13275 | 0.045776 | 0.050354 | 0.045776 | -0.07782 | -0.31586 | 0.11902 | -0.39368 | -0.37537 | -0.40741 | -0.45776 | -0.5127 | 0.58136 | 0.45776 | -121.0922 | 0.66833 | 0.58136 | 0.1236 | -121.0876 | 0.077819 | 0.022888 | -121.5179 | 0.21973 | 0.14191 | 0.11902 | -121.55 | 0.58594 | 0.59052 | 0.66833 | -121.2204 | 0.16022 | 0.12817 | 0.6546 | -121.6553
1733.7812 | 121.7697 | -0.52185 | 121.1472 | 0.071411 | 0.039719 | 0.061395 | 0.00062385 | 0.032105 | -0.0058084 | 0.031074 | 0.159 | 0.047345 | 0.019579 | 0.063769 | -0.0017453 | 0.026718 | 0.07782 | 0.086975 | 0.10529 | 0.059509 | 0.036621 | 0.064087 | -0.086975 | -0.28839 | 0.041199 | -0.40283 | -0.37079 | -0.39825 | -0.43945 | -0.48981 | 0.58594 | 0.43488 | -121.1105 | 0.60883 | 0.58136 | 0.14648 | -121.0693 | 0.082398 | 0.032044 | -121.5179 | 0.23346 | 0.11902 | 0.086975 | -121.5454 | 0.55847 | 0.59967 | 0.62714 | -121.2341 | 0.15106 | 0.1236 | 0.56305 | -121.637
1735.4688 | 121.701 | -0.50812 | 121.1975 | -0.081177 | 0.044205 | 0.06225 | 0.0046827 | 0.032105 | -0.00046778 | 0.034278 | -0.14618 | 0.049054 | 0.019792 | 0.065905 | 0.0020999 | 0.023727 | 0.073242 | 0.027466 | 0.041199 | 0.022888 | 0.10529 | 0.018311 | -0.1236 | -0.30212 | 0.032043 | -0.44861 | -0.3479 | -0.37079 | -0.44861 | -0.50812 | 0.52643 | 0.38452 | -121.0922 | 0.53558 | 0.53101 | 0.14648 | -121.1243 | 0.05951 | 0 | -121.5454 | 0.20599 | 0.05951 | 0.05951 | -121.5683 | 0.6134 | 0.58136 | 0.54932 | -121.3211 | 0.16022 | 0.13733 | 0.54016 | -121.7056
1737.2344 | 121.6827 | -0.50354 | 121.225 | -0.081177 | 0.042069 | 0.062036 | 0.0021191 | 0.033814 | 0.00081382 | 0.034278 | -0.11566 | 0.048413 | 0.018938 | 0.063982 | 0.0029543 | 0.023941 | 0.082397 | 0.045776 | 0.027466 | 0.022888 | 0.068665 | 0.032043 | -0.11902 | -0.31128 | 0.018311 | -0.45776 | -0.33417 | -0.3479 | -0.45319 | -0.52185 | 0.53558 | 0.38452 | -121.1563 | 0.54932 | 0.52643 | 0.14191 | -121.1426 | 0.050354 | -0.018311 | -121.5591 | 0.19226 | 0.045776 | 0.064087 | -121.5729 | 0.5722 | 0.58594 | 0.53101 | -121.344 | 0.16937 | 0.15564 | 0.52185 | -121.7468
1739 | 121.6919 | -0.51727 | 121.2387 | -0.21088 | 0.041428 | 0.061609 | 0.0021191 | 0.033814 | -0.0068766 | 0.03321 | -0.18433 | 0.046918 | 0.02086 | 0.061632 | -0.0015317 | 0.024154 | 0.045776 | 0.073242 | 0.091553 | 0.036621 | 0.045776 | 0.036621 | -0.10071 | -0.34332 | 0.032043 | -0.43488 | -0.33875 | -0.34332 | -0.45776 | -0.52185 | 0.55389 | 0.41656 | -121.1929 | 0.59052 | 0.55389 | 0.13733 | -121.1929 | 0.059509 | -0.004578 | -121.5775 | 0.17395 | 0.082398 | 0.086976 | -121.582 | 0.56305 | 0.56305 | 0.60883 | -121.3394 | 0.17853 | 0.17395 | 0.54932 | -121.7606
1740.75 | 121.6919 | -0.50812 | 121.2387 | -0.050659 | 0.043564 | 0.060327 | -0.0023669 | 0.034242 | -0.0013224 | 0.034705 | -0.046997 | 0.049054 | 0.019365 | 0.063555 | 0.0046633 | 0.025222 | 0.059509 | 0.009155 | 0.004578 | -0.009155 | 0.07782 | 0.022888 | -0.11444 | -0.34332 | -0.022888 | -0.48523 | -0.32501 | -0.32959 | -0.43945 | -0.52643 | 0.53101 | 0.39368 | -121.1609 | 0.51727 | 0.49896 | 0.10529 | -121.1792 | 0.068665 | -0.01831 | -121.5637 | 0.16479 | 0.022889 | 0.041199 | -121.5683 | 0.58594 | 0.56763 | 0.5127 | -121.3531 | 0.18311 | 0.17853 | 0.48523 | -121.7651
1742.4531 | 121.6873 | -0.50354 | 121.2479 | -0.04303 | 0.045273 | 0.061395 | 0.0012647 | 0.034669 | -0.00046778 | 0.034492 | -0.024109 | 0.048413 | 0.018083 | 0.064196 | 0.0038089 | 0.02565 | 0.064087 | 0.009155 | 0.013733 | 0.004578 | 0.07782 | 0.032043 | -0.1236 | -0.35248 | -0.032043 | -0.49439 | -0.32501 | -0.32501 | -0.45776 | -0.51727 | 0.53558 | 0.37994 | -121.17 | 0.5127 | 0.50812 | 0.12817 | -121.1838 | 0.045776 | -0.013733 | -121.5729 | 0.15106 | 0.009155 | 0.022888 | -121.5729 | 0.58136 | 0.56763 | 0.51727 | -121.3715 | 0.17853 | 0.17853 | 0.4715 | -121.7651
1744.2031 | 121.8018 | -0.46234 | 121.2067 | -0.1651 | 0.04271 | 0.064172 | 0.0038281 | 0.034883 | -0.0081582 | 0.030646 | -0.12329 | 0.046491 | 0.02086 | 0.059069 | -0.0034543 | 0.024368 | 0.082397 | 0.13275 | 0.12817 | 0.068665 | 0.041199 | 0.045776 | -0.082397 | -0.25635 | 0.13275 | -0.32959 | -0.35248 | -0.35248 | -0.41199 | -0.48065 | 0.50812 | 0.37994 | -121.1655 | 0.59509 | 0.53101 | 0.15106 | -121.1243 | 0.050354 | -0.018311 | -121.5591 | 0.20599 | 0.13275 | 0.15106 | -121.5591 | 0.50354 | 0.54474 | 0.59052 | -121.2891 | 0.10986 | 0.10986 | 0.59509 | -121.6873
1745.9531 | 121.8338 | -0.43488 | 121.2112 | -0.096436 | 0.040787 | 0.065027 | 0.0023329 | 0.03296 | -0.0085856 | 0.032569 | -0.054626 | 0.045209 | 0.020647 | 0.061846 | -0.0025999 | 0.025222 | 0.10071 | 0.1236 | 0.12817 | 0.054932 | 0.045776 | 0.041199 | -0.07782 | -0.2243 | 0.10986 | -0.32044 | -0.35706 | -0.37537 | -0.39825 | -0.47607 | 0.47607 | 0.35706 | -121.1655 | 0.55847 | 0.48981 | 0.13275 | -121.1105 | 0.036621 | -0.041199 | -121.5683 | 0.21057 | 0.11444 | 0.15564 | -121.5866 | 0.48065 | 0.53558 | 0.56305 | -121.2891 | 0.077819 | 0.059509 | 0.54474 | -121.6873
1747.7188 | 121.7285 | -0.48065 | 121.2479 | -0.088806 | 0.044205 | 0.06225 | 0.0016919 | 0.035096 | 0.0012412 | 0.032142 | -0.14618 | 0.047559 | 0.020006 | 0.062487 | -0.00089089 | 0.0233 | 0.073242 | 0.027466 | 0.041199 | 0.032043 | 0.082397 | 0.009155 | -0.10986 | -0.27924 | 0.018311 | -0.4303 | -0.32959 | -0.32501 | -0.4303 | -0.50354 | 0.48981 | 0.37079 | -121.1655 | 0.50812 | 0.5127 | 0.14191 | -121.1746 | 0.050354 | -0.022888 | -121.5775 | 0.20142 | 0.050354 | 0.073242 | -121.5729 | 0.56305 | 0.55389 | 0.52185 | -121.3577 | 0.15106 | 0.15564 | 0.49896 | -121.7514
1749.4688 | 121.8475 | -0.43945 | 121.2067 | 0.063782 | 0.040787 | 0.059686 | 0.00019645 | 0.032533 | -0.0021768 | 0.035346 | 0.13611 | 0.047132 | 0.019792 | 0.064196 | 0.00081811 | 0.026718 | 0.086975 | 0.09613 | 0.09613 | 0.07782 | 0.064087 | 0.050354 | -0.091553 | -0.22888 | 0.059509 | -0.3479 | -0.3479 | -0.37537 | -0.39825 | -0.45319 | 0.48981 | 0.3479 | -121.1426 | 0.53558 | 0.51727 | 0.16937 | -121.1197 | 0.041199 | -0.013733 | -121.5546 | 0.21057 | 0.091553 | 0.10529 | -121.582 | 0.50354 | 0.52643 | 0.53558 | -121.2982 | 0.091553 | 0.064087 | 0.49896 | -121.6599
1751.1562 | 121.8475 | -0.4303 | 121.2158 | 0.08667 | 0.042496 | 0.060754 | -1.7146e-05 | 0.031892 | -0.0021768 | 0.032142 | 0.11322 | 0.047986 | 0.019151 | 0.061846 | -0.00024989 | 0.027572 | 0.036621 | -0.018311 | -0.009155 | -0.009155 | 0.064087 | 0.022888 | -0.11444 | -0.28839 | -0.050354 | -0.44403 | -0.31586 | -0.29755 | -0.42572 | -0.4715 | 0.45319 | 0.31586 | -121.1517 | 0.41199 | 0.42114 | 0.10529 | -121.1792 | 0.004578 | -0.041199 | -121.5317 | 0.14191 | -0.013733 | 0.027466 | -121.5134 | 0.49439 | 0.46692 | 0.42114 | -121.3303 | 0.11444 | 0.13275 | 0.37994 | -121.6873
1752.9219 | 121.8704 | -0.41657 | 121.2158 | 0.14008 | 0.043351 | 0.062677 | 0.00062385 | 0.033814 | -0.0036722 | 0.034492 | 0.14374 | 0.047559 | 0.018724 | 0.062487 | 0.0012455 | 0.026718 | 0.041199 | 0.009155 | 0.018311 | 0.009155 | 0.073242 | 0.027466 | -0.11444 | -0.24719 | 0 | -0.3891 | -0.31128 | -0.32044 | -0.39825 | -0.45776 | 0.44403 | 0.30212 | -121.1426 | 0.42572 | 0.42572 | 0.1236 | -121.1746 | 0.018311 | -0.041199 | -121.5271 | 0.16937 | 0.027466 | 0.068665 | -121.5363 | 0.48981 | 0.45776 | 0.43488 | -121.3303 | 0.10529 | 0.09613 | 0.41657 | -121.6736
1754.6094 | 121.756 | -0.46234 | 121.2799 | 0.018005 | 0.042923 | 0.061609 | 0.0038281 | 0.033814 | 0.00038662 | 0.034705 | 0.029297 | 0.047986 | 0.020006 | 0.063555 | 0.0020999 | 0.025863 | 0.018311 | -0.068665 | -0.036621 | -0.018311 | 0.082397 | 0.004578 | -0.12817 | -0.36163 | -0.082397 | -0.49896 | -0.29297 | -0.28839 | -0.42114 | -0.46692 | 0.46692 | 0.33417 | -121.1975 | 0.39368 | 0.44403 | 0.10986 | -121.2616 | 0.041198 | -0.004578 | -121.5729 | 0.10071 | -0.036621 | -0.032043 | -121.5683 | 0.54474 | 0.48065 | 0.42572 | -121.4081 | 0.16937 | 0.17395 | 0.37994 | -121.7468
1756.3438 | 121.8246 | -0.41657 | 121.2662 | 0.040894 | 0.036942 | 0.062891 | 0.0012647 | 0.033601 | -0.0070902 | 0.031714 | 0.10559 | 0.045636 | 0.019579 | 0.060351 | -0.0030271 | 0.027999 | 0.064087 | 0.054932 | 0.064087 | 0.018311 | 0.041199 | 0.045776 | -0.086975 | -0.26093 | -0.004578 | -0.35706 | -0.32501 | -0.32501 | -0.3891 | -0.43945 | 0.46234 | 0.32959 | -121.225 | 0.4715 | 0.43488 | 0.10529 | -121.2021 | 0.027466 | -0.022888 | -121.5912 | 0.15564 | 0.059509 | 0.082397 | -121.5912 | 0.45776 | 0.48065 | 0.48065 | -121.3531 | 0.091553 | 0.091553 | 0.41199 | -121.7056
1758.125 | 121.8384 | -0.44403 | 121.3074 | -0.21088 | 0.043137 | 0.06225 | 0.0074597 | 0.031251 | -0.008372 | 0.030219 | -0.14618 | 0.045423 | 0.018938 | 0.061846 | -0.0030271 | 0.02565 | 0.10071 | 0.10529 | 0.14191 | 0.054932 | 0.059509 | 0.041199 | -0.07782 | -0.20599 | 0.091553 | -0.28381 | -0.31128 | -0.32501 | -0.37537 | -0.43488 | 0.48523 | 0.36621 | -121.2479 | 0.54932 | 0.49896 | 0.13275 | -121.2067 | 0.068665 | 0.009156 | -121.6187 | 0.23804 | 0.16022 | 0.15106 | -121.6324 | 0.50354 | 0.54474 | 0.58594 | -121.3852 | 0.13275 | 0.11902 | 0.53558 | -121.7422
1759.8281 | 121.8796 | -0.3891 | 121.2708 | -0.18036 | 0.041642 | 0.064386 | 0.0044691 | 0.030824 | -0.0075174 | 0.031501 | -0.069885 | 0.045636 | 0.018724 | 0.059283 | -0.0034543 | 0.025009 | 0.11444 | 0.10071 | 0.11902 | 0.064087 | 0.045776 | 0.050354 | -0.082397 | -0.15564 | 0.07782 | -0.27466 | -0.33875 | -0.32044 | -0.36163 | -0.41657 | 0.43945 | 0.3067 | -121.225 | 0.48981 | 0.45319 | 0.14648 | -121.1563 | 0.027466 | -0.027466 | -121.6095 | 0.23346 | 0.11444 | 0.14191 | -121.5912 | 0.43487 | 0.50354 | 0.50812 | -121.3531 | 0.050354 | 0.068664 | 0.46692 | -121.6873
1761.5625 | 121.8018 | -0.45776 | 121.312 | -0.19562 | 0.044205 | 0.06225 | 0.0044691 | 0.033174 | -0.0036722 | 0.031501 | -0.13855 | 0.042859 | 0.022569 | 0.059069 | -0.0013181 | 0.023513 | 0.10529 | 0.10986 | 0.11902 | 0.073242 | 0.045776 | 0.054932 | -0.073242 | -0.21515 | 0.07782 | -0.32501 | -0.32959 | -0.35248 | -0.37537 | -0.44861 | 0.5127 | 0.38452 | -121.2662 | 0.56763 | 0.53101 | 0.14648 | -121.2067 | 0.082398 | 0.009156 | -121.6415 | 0.24261 | 0.13275 | 0.1236 | -121.6644 | 0.50354 | 0.56305 | 0.57678 | -121.3852 | 0.12817 | 0.10529 | 0.53558 | -121.7606
1763.25 | 121.7651 | -0.48981 | 121.3669 | -0.24139 | 0.044205 | 0.062463 | 0.0061781 | 0.035096 | -0.0019632 | 0.030646 | -0.13855 | 0.0435 | 0.025987 | 0.06206 | -0.0011045 | 0.025009 | 0.045776 | 0.022888 | 0.041199 | 0.004578 | 0.082397 | 0.018311 | -0.1236 | -0.3067 | -0.045776 | -0.41657 | -0.28839 | -0.30212 | -0.40741 | -0.47607 | 0.50812 | 0.36621 | -121.2845 | 0.5127 | 0.49439 | 0.12817 | -121.3211 | 0.082397 | 0.013733 | -121.6553 | 0.18311 | 0.073242 | 0.059509 | -121.669 | 0.5722 | 0.53558 | 0.53101 | -121.4905 | 0.20142 | 0.18768 | 0.44403 | -121.843
1765 | 121.8887 | -0.38452 | 121.3211 | 0.10193 | 0.042923 | 0.063532 | -0.0023669 | 0.03531 | -0.00046778 | 0.034705 | 0.10559 | 0.04585 | 0.019365 | 0.060351 | 0.0029543 | 0.025222 | 0.11902 | 0.086975 | 0.086975 | 0.064087 | 0.054932 | 0.045776 | -0.10071 | -0.15564 | 0.036621 | -0.3067 | -0.30212 | -0.3067 | -0.35706 | -0.41199 | 0.4303 | 0.28381 | -121.2662 | 0.4715 | 0.44861 | 0.1648 | -121.2021 | 0.027465 | -0.027466 | -121.6232 | 0.22888 | 0.077819 | 0.10529 | -121.6278 | 0.43945 | 0.50354 | 0.4715 | -121.4218 | 0.082397 | 0.077819 | 0.42114 | -121.7331
1766.75 | 121.8796 | -0.3479 | 121.3669 | -0.14984 | 0.041428 | 0.060754 | 0.0046827 | 0.033601 | -0.0073038 | 0.031287 | -0.092773 | 0.042005 | 0.022356 | 0.058214 | -0.0017453 | 0.027572 | 0.11444 | 0.14648 | 0.13275 | 0.064087 | 0.059509 | 0.068665 | -0.09613 | -0.10071 | 0.054932 | -0.23804 | -0.25635 | -0.25635 | -0.31128 | -0.35248 | 0.41656 | 0.25177 | -121.3074 | 0.49438 | 0.41199 | 0.16022 | -121.2524 | 0.036621 | -0.004578 | -121.6232 | 0.24719 | 0.10986 | 0.11444 | -121.6232 | 0.40741 | 0.46234 | 0.48065 | -121.463 | 0.091552 | 0.091552 | 0.40283 | -121.7194
1768.4375 | 121.7697 | -0.39825 | 121.4172 | -0.25665 | 0.044205 | 0.063532 | 0.0068189 | 0.035096 | -0.0038858 | 0.032783 | -0.21484 | 0.044782 | 0.021501 | 0.059923 | -0.0019589 | 0.024582 | 0.054932 | 0.068665 | 0.036621 | 0.027466 | 0.07782 | 0.022888 | -0.10071 | -0.21057 | -0.07782 | -0.35248 | -0.21973 | -0.24719 | -0.32959 | -0.39368 | 0.42114 | 0.29755 | -121.3394 | 0.46692 | 0.42572 | 0.12817 | -121.3623 | 0.068664 | 0.004577 | -121.637 | 0.18768 | 0.045776 | 0.041199 | -121.6644 | 0.47607 | 0.45319 | 0.43488 | -121.5179 | 0.17853 | 0.15106 | 0.32043 | -121.8109
1770.1875 | 121.8201 | -0.36621 | 121.4401 | 0.079041 | 0.044419 | 0.061182 | -0.00087155 | 0.034455 | 0.0023092 | 0.03321 | 0.036926 | 0.047986 | 0.020647 | 0.063555 | 0.0042361 | 0.023727 | 0 | -0.036621 | -0.045776 | -0.027466 | 0.082397 | 0.027466 | -0.13275 | -0.20599 | -0.16022 | -0.38452 | -0.19226 | -0.20599 | -0.30212 | -0.37994 | 0.39368 | 0.23346 | -121.3577 | 0.32959 | 0.33875 | 0.10529 | -121.4401 | 0.064087 | -0.013733 | -121.6324 | 0.16022 | -0.01831 | -0.004577 | -121.6461 | 0.44861 | 0.36621 | 0.32044 | -121.5729 | 0.17395 | 0.16022 | 0.20599 | -121.8201
1771.9375 | 121.8475 | -0.32044 | 121.4035 | 0.08667 | 0.044846 | 0.065668 | 0.0031873 | 0.033174 | -0.0053812 | 0.03321 | 0.15137 | 0.046491 | 0.019792 | 0.059496 | -0.0011045 | 0.028427 | 0.073242 | 0.1236 | 0.11444 | 0.050354 | 0.036621 | 0.068665 | -0.082397 | -0.09613 | -0.036621 | -0.22888 | -0.2243 | -0.23804 | -0.29297 | -0.32501 | 0.3891 | 0.23804 | -121.3669 | 0.44403 | 0.37079 | 0.13275 | -121.3303 | 0.027466 | -0.004577 | -121.6278 | 0.22431 | 0.091553 | 0.09613 | -121.6415 | 0.35706 | 0.39368 | 0.43488 | -121.4859 | 0.096131 | 0.082398 | 0.28381 | -121.7285
1773.7031 | 121.8201 | -0.31586 | 121.4539 | 0.11719 | 0.043137 | 0.060327 | 0.00083745 | 0.029969 | 0.0027364 | 0.03321 | 0.052185 | 0.046491 | 0.023424 | 0.057574 | 0.0023135 | 0.02864 | 0.027466 | -0.041199 | -0.032043 | -0.018311 | 0.10529 | 0.009155 | -0.10986 | -0.17395 | -0.16937 | -0.33417 | -0.16022 | -0.17395 | -0.28381 | -0.3479 | 0.32501 | 0.20599 | -121.3486 | 0.27466 | 0.29755 | 0.091552 | -121.4264 | 0.032044 | -0.032043 | -121.6141 | 0.14191 | -0.01831 | 0.013733 | -121.6278 | 0.42114 | 0.34332 | 0.28381 | -121.5637 | 0.15564 | 0.14191 | 0.14648 | -121.8018
1775.4375 | 121.8155 | -0.29755 | 121.4996 | 0.040894 | 0.041428 | 0.060327 | 0.0038281 | 0.033387 | -0.00068138 | 0.035346 | 0.052185 | 0.045423 | 0.02321 | 0.05736 | 0.0014591 | 0.031417 | -0.022888 | -0.050354 | -0.022888 | -0.027466 | 0.086975 | 0.018311 | -0.10986 | -0.17395 | -0.18768 | -0.33417 | -0.14191 | -0.15564 | -0.27008 | -0.33875 | 0.31586 | 0.18768 | -121.4127 | 0.24719 | 0.27008 | 0.082397 | -121.5225 | 0.027465 | -0.041199 | -121.6415 | 0.1236 | -0.036621 | 0.004578 | -121.6553 | 0.38452 | 0.27466 | 0.27466 | -121.6095 | 0.15564 | 0.14191 | 0.10986 | -121.8384
1777.125 | 121.875 | -0.26093 | 121.4676 | 0.12482 | 0.040787 | 0.061609 | -0.00044435 | 0.031037 | -0.006663 | 0.034919 | 0.14374 | 0.041364 | 0.024492 | 0.052233 | -0.00067729 | 0.034408 | 0.091553 | 0.10986 | 0.11902 | 0.045776 | 0.032043 | 0.054932 | -0.07782 | -0.059509 | -0.018311 | -0.16937 | -0.17395 | -0.19226 | -0.22888 | -0.27466 | 0.31586 | 0.18311 | -121.4355 | 0.37079 | 0.3067 | 0.1236 | -121.376 | 0.032043 | -0.013733 | -121.6415 | 0.20142 | 0.091552 | 0.10529 | -121.6599 | 0.29297 | 0.35248 | 0.37994 | -121.5454 | 0.086975 | 0.068664 | 0.24261 | -121.7422
1778.875 | 121.8018 | -0.31586 | 121.5225 | -0.21851 | 0.043991 | 0.0646 | 0.0059643 | 0.032746 | -0.0038858 | 0.031714 | -0.15381 | 0.041364 | 0.027483 | 0.053728 | -0.0034543 | 0.031631 | 0.009155 | -0.004578 | -0.004578 | -0.018311 | 0.054932 | 0.018311 | -0.12817 | -0.16022 | -0.1236 | -0.29297 | -0.13733 | -0.16937 | -0.27466 | -0.31128 | 0.33417 | 0.18768 | -121.4676 | 0.31128 | 0.29755 | 0.10986 | -121.5134 | 0.041199 | 0.004578 | -121.6599 | 0.15564 | 0.022888 | 0.01831 | -121.6919 | 0.37079 | 0.32501 | 0.31128 | -121.6507 | 0.17853 | 0.14648 | 0.19226 | -121.8338
1780.6406 | 121.9208 | -0.26093 | 121.4767 | -0.14221 | 0.044632 | 0.06225 | 0.0046827 | 0.034455 | -0.006663 | 0.031501 | -0.12329 | 0.039655 | 0.027269 | 0.053301 | -0.0025999 | 0.031845 | 0.10071 | 0.15564 | 0.12817 | 0.07782 | 0.054932 | 0.068665 | -0.091553 | -0.050354 | 0.022888 | -0.14191 | -0.17395 | -0.17395 | -0.19684 | -0.24719 | 0.32959 | 0.16937 | -121.4218 | 0.41657 | 0.33875 | 0.16937 | -121.376 | 0.064087 | 0.013733 | -121.6507 | 0.21057 | 0.11902 | 0.10528 | -121.6507 | 0.31586 | 0.36163 | 0.3891 | -121.5683 | 0.086975 | 0.086975 | 0.28381 | -121.7239
1782.3906 | 121.8979 | -0.24719 | 121.4859 | 0.13245 | 0.042069 | 0.060114 | -1.7146e-05 | 0.032533 | -0.003245 | 0.034064 | 0.159 | 0.040082 | 0.021501 | 0.053728 | 0.0031681 | 0.03334 | 0.10986 | 0.10529 | 0.1236 | 0.073242 | 0.054932 | 0.059509 | -0.082397 | -0.032043 | -0.027466 | -0.14648 | -0.17853 | -0.17853 | -0.2243 | -0.27008 | 0.3067 | 0.16479 | -121.431 | 0.35248 | 0.32043 | 0.15564 | -121.376 | 0.022888 | -0.022889 | -121.6644 | 0.21515 | 0.10071 | 0.1236 | -121.6644 | 0.30212 | 0.35706 | 0.37079 | -121.5683 | 0.068664 | 0.068664 | 0.21973 | -121.756
1784.1406 | 121.8338 | -0.27466 | 121.5408 | -0.20325 | 0.043991 | 0.061609 | 0.0061781 | 0.033814 | -0.0051676 | 0.031074 | -0.13855 | 0.039868 | 0.028978 | 0.052233 | -0.0023861 | 0.03334 | 0.10071 | 0.11902 | 0.10986 | 0.068665 | 0.054932 | 0.059509 | -0.086975 | -0.059509 | 0 | -0.16022 | -0.16937 | -0.17395 | -0.20599 | -0.27466 | 0.33417 | 0.18768 | -121.4859 | 0.39368 | 0.34332 | 0.15564 | -121.4401 | 0.068664 | 0 | -121.7102 | 0.21515 | 0.11444 | 0.11444 | -121.7148 | 0.32959 | 0.37537 | 0.38452 | -121.6278 | 0.10529 | 0.10071 | 0.27466 | -121.8155
1785.8438 | 121.7926 | -0.29755 | 121.5271 | -0.22614 | 0.041642 | 0.063745 | 0.00041005 | 0.034242 | -0.004313 | 0.032783 | -0.20721 | 0.040082 | 0.026628 | 0.052019 | 0.00081811 | 0.034622 | 0.045776 | 0.068665 | 0.050354 | 0.022888 | 0.064087 | 0.036621 | -0.11444 | -0.14648 | -0.091553 | -0.25635 | -0.10986 | -0.14191 | -0.25177 | -0.30212 | 0.33417 | 0.1831 | -121.463 | 0.36621 | 0.32043 | 0.13733 | -121.4813 | 0.045776 | -0.004578 | -121.637 | 0.15106 | 0.041198 | 0.045776 | -121.669 | 0.36163 | 0.34332 | 0.3479 | -121.6415 | 0.18768 | 0.15564 | 0.20599 | -121.8292
1787.5938 | 121.9391 | -0.24719 | 121.5134 | -0.20325 | 0.041001 | 0.063104 | 0.0021191 | 0.033174 | -0.0058084 | 0.031501 | -0.10803 | 0.039441 | 0.025987 | 0.054156 | 0.0010317 | 0.034622 | 0.091553 | 0.10529 | 0.10986 | 0.068665 | 0.059509 | 0.041199 | -0.09613 | -0.004578 | 0.022888 | -0.11902 | -0.16022 | -0.16937 | -0.21515 | -0.24719 | 0.28839 | 0.15106 | -121.4539 | 0.35248 | 0.31586 | 0.16479 | -121.4218 | 0.032043 | 0 | -121.6736 | 0.24261 | 0.12817 | 0.12817 | -121.6827 | 0.3067 | 0.33874 | 0.35706 | -121.6095 | 0.086975 | 0.077819 | 0.27008 | -121.7606
1789.3438 | 121.9025 | -0.25177 | 121.5363 | -0.1651 | 0.042923 | 0.061609 | 0.0059643 | 0.036164 | -0.0045266 | 0.031074 | -0.16907 | 0.038159 | 0.028123 | 0.052233 | -0.0023861 | 0.033554 | 0.10071 | 0.13275 | 0.1236 | 0.064087 | 0.050354 | 0.045776 | -0.091553 | -0.018311 | 0.045776 | -0.13275 | -0.15106 | -0.17395 | -0.19684 | -0.24719 | 0.29755 | 0.16022 | -121.4859 | 0.38452 | 0.31586 | 0.15564 | -121.4355 | 0.054932 | 0.004578 | -121.6873 | 0.23346 | 0.11902 | 0.11444 | -121.7102 | 0.30212 | 0.35248 | 0.37537 | -121.6278 | 0.10071 | 0.07782 | 0.29755 | -121.7834
1791.125 | 121.8475 | -0.27008 | 121.5546 | -0.17273 | 0.043137 | 0.060968 | 0.0038281 | 0.03531 | -0.0036722 | 0.030646 | -0.16144 | 0.038159 | 0.029405 | 0.053301 | -0.00089089 | 0.032913 | 0.10529 | 0.11444 | 0.10986 | 0.054932 | 0.045776 | 0.050354 | -0.086975 | -0.036621 | 0.022888 | -0.16479 | -0.14648 | -0.15564 | -0.20599 | -0.25635 | 0.32044 | 0.18311 | -121.5088 | 0.38452 | 0.32501 | 0.14191 | -121.4493 | 0.064087 | 0.013733 | -121.701 | 0.23346 | 0.10529 | 0.091553 | -121.7102 | 0.31586 | 0.37537 | 0.37994 | -121.6415 | 0.1236 | 0.11444 | 0.29297 | -121.8109
1792.8281 | 121.843 | -0.27924 | 121.5179 | 0.056152 | 0.045487 | 0.060541 | -0.0015125 | 0.029542 | 0.0016684 | 0.034064 | -0.024109 | 0.040937 | 0.028337 | 0.055224 | 0.0053043 | 0.032058 | 0.009155 | -0.045776 | -0.036621 | -0.022888 | 0.091553 | 0.018311 | -0.1236 | -0.13275 | -0.15106 | -0.28381 | -0.10071 | -0.1236 | -0.23804 | -0.29297 | 0.29755 | 0.15564 | -121.4264 | 0.23346 | 0.25635 | 0.10071 | -121.5088 | 0.041199 | -0.013733 | -121.6187 | 0.14648 | -0.004577 | 0.009156 | -121.6415 | 0.37079 | 0.28839 | 0.24261 | -121.6415 | 0.17853 | 0.15564 | 0.12817 | -121.8109
1794.5938 | 121.8704 | -0.27466 | 121.5866 | -0.23376 | 0.043564 | 0.061182 | 0.0012647 | 0.034242 | -0.0023904 | 0.032783 | -0.24536 | 0.038373 | 0.028123 | 0.054796 | -0.00046349 | 0.031845 | -0.004578 | -0.004578 | -0.013733 | -0.022888 | 0.09613 | 0.004578 | -0.12817 | -0.14191 | -0.11902 | -0.26093 | -0.09613 | -0.10529 | -0.23346 | -0.29297 | 0.27924 | 0.14648 | -121.4905 | 0.27008 | 0.25177 | 0.10529 | -121.5912 | 0.041199 | -0.018311 | -121.6827 | 0.13275 | 0.013733 | 0.032044 | -121.6919 | 0.37079 | 0.27008 | 0.26093 | -121.7148 | 0.17853 | 0.16937 | 0.15564 | -121.8796
1796.3438 | 121.907 | -0.23346 | 121.5637 | -0.17273 | 0.043778 | 0.06225 | 0.0061781 | 0.034455 | -0.0058084 | 0.031501 | -0.16907 | 0.037305 | 0.02791 | 0.051806 | -0.0036679 | 0.031631 | 0.091553 | 0.15106 | 0.14191 | 0.07782 | 0.059509 | 0.064087 | -0.09613 | -0.032043 | 0.036621 | -0.1236 | -0.13275 | -0.16022 | -0.17853 | -0.24261 | 0.29755 | 0.13733 | -121.5042 | 0.38452 | 0.31128 | 0.17395 | -121.4722 | 0.054931 | -0.009156 | -121.6965 | 0.20142 | 0.10986 | 0.11902 | -121.7239 | 0.29297 | 0.32501 | 0.37537 | -121.6599 | 0.10071 | 0.073242 | 0.27008 | -121.8063
1798.0469 | 121.9254 | -0.2243 | 121.5363 | 0.071411 | 0.043137 | 0.058618 | 0.0012647 | 0.033387 | 0.0012412 | 0.033423 | 0.052185 | 0.040723 | 0.028123 | 0.056292 | 0.0023135 | 0.03334 | 0.027466 | -0.022888 | -0.022888 | -0.022888 | 0.086975 | 0.032043 | -0.11902 | -0.10071 | -0.11444 | -0.24261 | -0.10529 | -0.10986 | -0.19226 | -0.26093 | 0.25635 | 0.10529 | -121.4493 | 0.20142 | 0.20142 | 0.096131 | -121.5088 | 0.032043 | -0.036621 | -121.6415 | 0.1236 | -0.018311 | 0.01831 | -121.6461 | 0.31128 | 0.25177 | 0.20142 | -121.6553 | 0.11902 | 0.11444 | 0.10986 | -121.7972
1799.7969 | 121.8246 | -0.27924 | 121.5866 | -0.22614 | 0.043991 | 0.061182 | 0.0034009 | 0.034028 | -0.0021768 | 0.033423 | -0.15381 | 0.038373 | 0.030473 | 0.05501 | -0.00089089 | 0.033981 | -0.009155 | 0.036621 | 0.018311 | -0.004578 | 0.073242 | 0.009155 | -0.1236 | -0.13275 | -0.068665 | -0.23346 | -0.07782 | -0.091553 | -0.21515 | -0.28839 | 0.28839 | 0.15564 | -121.5134 | 0.31586 | 0.27466 | 0.11902 | -121.5958 | 0.064087 | -0.009155 | -121.6644 | 0.14648 | 0.045777 | 0.054932 | -121.6782 | 0.35248 | 0.27008 | 0.29755 | -121.7102 | 0.20142 | 0.18768 | 0.21057 | -121.875
1801.5469 | 121.9025 | -0.23804 | 121.5408 | 0.094299 | 0.039933 | 0.061182 | 0.0023329 | 0.032105 | -0.0038858 | 0.031928 | 0.11322 | 0.036237 | 0.02556 | 0.052447 | 0.00060451 | 0.034622 | 0.091553 | 0.10986 | 0.11444 | 0.054932 | 0.045776 | 0.068665 | -0.07782 | -0.013733 | 0.022888 | -0.14648 | -0.12817 | -0.16022 | -0.16937 | -0.23346 | 0.3067 | 0.16022 | -121.4951 | 0.3479 | 0.29297 | 0.13275 | -121.4493 | 0.068664 | 0.004578 | -121.669 | 0.2243 | 0.091553 | 0.086975 | -121.7011 | 0.28381 | 0.32959 | 0.35248 | -121.6187 | 0.10986 | 0.07782 | 0.26093 | -121.7743
1803.25 | 121.875 | -0.25177 | 121.5729 | -0.13458 | 0.045487 | 0.062036 | 0.0038281 | 0.033601 | -0.00046778 | 0.033851 | -0.1767 | 0.037519 | 0.028764 | 0.051378 | 0.0029543 | 0.032058 | 0.045776 | 0.036621 | 0.032043 | 0.022888 | 0.082397 | 0.018311 | -0.10529 | -0.082397 | -0.032043 | -0.20599 | -0.10071 | -0.11444 | -0.20142 | -0.26093 | 0.27008 | 0.14648 | -121.4905 | 0.28839 | 0.27466 | 0.12817 | -121.5271 | 0.050354 | -0.009155 | -121.6736 | 0.16937 | 0.045776 | 0.054931 | -121.6873 | 0.33417 | 0.29755 | 0.28381 | -121.6782 | 0.15106 | 0.13733 | 0.21973 | -121.8338
1805 | 121.8979 | -0.22888 | 121.5637 | 0.071411 | 0.041214 | 0.061609 | 0.0023329 | 0.034028 | -0.0064492 | 0.03321 | 0.12085 | 0.037519 | 0.029192 | 0.051165 | -0.0011045 | 0.036117 | 0.045776 | 0.082397 | 0.082397 | 0.027466 | 0.045776 | 0.050354 | -0.086975 | -0.045776 | -0.009155 | -0.15106 | -0.10986 | -0.13275 | -0.17395 | -0.24719 | 0.27924 | 0.14191 | -121.5179 | 0.31128 | 0.25635 | 0.11444 | -121.5179 | 0.054932 | -0.01831 | -121.6736 | 0.18311 | 0.07782 | 0.09613 | -121.6965 | 0.27466 | 0.27466 | 0.31128 | -121.6507 | 0.11902 | 0.096131 | 0.21973 | -121.8109
1806.75 | 121.8887 | -0.23804 | 121.6095 | -0.1651 | 0.0457 | 0.060968 | 0.0055371 | 0.032319 | -0.0013224 | 0.031714 | -0.25299 | 0.040082 | 0.029619 | 0.053728 | 0.00039091 | 0.032058 | 0.009155 | -0.004578 | -0.018311 | 0.004578 | 0.09613 | 0.022888 | -0.13275 | -0.12817 | -0.050354 | -0.21973 | -0.073242 | -0.10529 | -0.21515 | -0.24719 | 0.26093 | 0.10529 | -121.5134 | 0.23346 | 0.24261 | 0.13733 | -121.6003 | 0.022888 | -0.009155 | -121.6827 | 0.10986 | 0.01831 | 0.027465 | -121.7148 | 0.33417 | 0.24719 | 0.21973 | -121.7422 | 0.16479 | 0.13275 | 0.18768 | -121.8567
1808.4375 | 121.8887 | -0.23346 | 121.5958 | 0.10193 | 0.043351 | 0.061395 | -0.00044435 | 0.030183 | -0.00068138 | 0.032142 | 0.082703 | 0.039014 | 0.02791 | 0.051378 | 0.0023135 | 0.03569 | 0 | -0.027466 | -0.036621 | -0.013733 | 0.091553 | 0.018311 | -0.11444 | -0.10529 | -0.1236 | -0.25635 | -0.082397 | -0.091553 | -0.18768 | -0.27466 | 0.25177 | 0.11902 | -121.5042 | 0.20599 | 0.21973 | 0.10071 | -121.5958 | 0.045776 | -0.041199 | -121.6782 | 0.12817 | -0.022889 | 0.01831 | -121.6873 | 0.32501 | 0.23346 | 0.19684 | -121.7102 | 0.15106 | 0.14191 | 0.10986 | -121.8704
1810.1875 | 121.8384 | -0.24261 | 121.6232 | -0.065918 | 0.046982 | 0.0599 | 0.0021191 | 0.033387 | 0.001882 | 0.035773 | -0.062256 | 0.039014 | 0.029619 | 0.053728 | 0.0014591 | 0.032913 | 0.036621 | 0.027466 | 0.022888 | 0.018311 | 0.082397 | 0.018311 | -0.11444 | -0.09613 | -0.073242 | -0.24719 | -0.073242 | -0.086975 | -0.18768 | -0.26093 | 0.26093 | 0.12817 | -121.5408 | 0.27008 | 0.26093 | 0.13275 | -121.5866 | 0.054932 | -0.01831 | -121.6965 | 0.14649 | -0.004577 | 0.013733 | -121.7102 | 0.32501 | 0.27924 | 0.2655 | -121.7377 | 0.16937 | 0.15564 | 0.16937 | -121.8842
1811.875 | 121.8796 | -0.24261 | 121.6187 | -0.21851 | 0.042923 | 0.061609 | 0.0063917 | 0.035737 | -0.0036722 | 0.032355 | -0.18433 | 0.0388 | 0.032396 | 0.052233 | -0.0023861 | 0.034835 | -0.018311 | -0.009155 | -0.013733 | -0.004578 | 0.082397 | 0.027466 | -0.12817 | -0.12817 | -0.068665 | -0.2243 | -0.082397 | -0.091553 | -0.21057 | -0.25177 | 0.27008 | 0.11444 | -121.5363 | 0.23346 | 0.23804 | 0.1236 | -121.637 | 0.032044 | -0.009155 | -121.701 | 0.11444 | 0.018311 | 0.027466 | -121.7102 | 0.32501 | 0.2243 | 0.22888 | -121.7468 | 0.16022 | 0.15106 | 0.17395 | -121.8704
1813.5781 | 121.8338 | -0.23804 | 121.6324 | -0.065918 | 0.045273 | 0.061182 | 0.0019055 | 0.036164 | 0.00081382 | 0.034919 | -0.046997 | 0.039441 | 0.03026 | 0.052874 | -0.00024989 | 0.032486 | 0.045776 | 0.036621 | 0.018311 | 0.018311 | 0.059509 | 0.009155 | -0.11444 | -0.10071 | -0.059509 | -0.23346 | -0.091553 | -0.082397 | -0.19226 | -0.27466 | 0.24719 | 0.1236 | -121.5729 | 0.27466 | 0.25635 | 0.13275 | -121.5866 | 0.045776 | -0.036621 | -121.7239 | 0.13733 | 0.004578 | 0.041199 | -121.7148 | 0.29755 | 0.28381 | 0.25635 | -121.7468 | 0.14648 | 0.15564 | 0.17853 | -121.907
1815.3281 | 121.962 | -0.20599 | 121.5912 | 0.14771 | 0.04506 | 0.062463 | 0.0048963 | 0.032533 | -0.0040994 | 0.035132 | 0.159 | 0.036664 | 0.026414 | 0.047747 | 0.00060451 | 0.032913 | 0.050354 | 0.10071 | 0.091553 | 0.050354 | 0.041199 | 0.054932 | -0.059509 | 0.004578 | 0.032043 | -0.11902 | -0.11444 | -0.15106 | -0.16479 | -0.21973 | 0.26093 | 0.14649 | -121.55 | 0.3067 | 0.25635 | 0.10986 | -121.5408 | 0.041199 | -0.013733 | -121.7056 | 0.21057 | 0.086975 | 0.10071 | -121.7422 | 0.24719 | 0.25635 | 0.29755 | -121.6507 | 0.091553 | 0.054932 | 0.23804 | -121.8109
1817.0938 | 121.8658 | -0.23346 | 121.6232 | -0.096436 | 0.043991 | 0.061395 | 0.00062385 | 0.033601 | -0.001536 | 0.033851 | -0.092773 | 0.040296 | 0.028978 | 0.049029 | 0.0023135 | 0.033554 | 0.059509 | 0.045776 | 0.022888 | 0.009155 | 0.07782 | 0.013733 | -0.11444 | -0.07782 | -0.018311 | -0.19226 | -0.07782 | -0.09613 | -0.17395 | -0.25177 | 0.24719 | 0.11902 | -121.5454 | 0.27924 | 0.24261 | 0.1236 | -121.5637 | 0.059509 | -0.018311 | -121.7011 | 0.15564 | 0.041198 | 0.059509 | -121.7194 | 0.31128 | 0.29297 | 0.25635 | -121.7377 | 0.15564 | 0.13733 | 0.21515 | -121.875
1818.7969 | 121.9025 | -0.24261 | 121.637 | -0.20325 | 0.042496 | 0.061395 | 0.0063917 | 0.034883 | -0.010935 | 0.034064 | -0.10803 | 0.035382 | 0.027483 | 0.050951 | -0.0030271 | 0.035904 | 0.073242 | 0.13275 | 0.11902 | 0.068665 | 0.036621 | 0.045776 | -0.082397 | -0.041199 | 0.068665 | -0.10071 | -0.09613 | -0.11444 | -0.15106 | -0.2243 | 0.28839 | 0.16022 | -121.6003 | 0.37537 | 0.31128 | 0.15106 | -121.5637 | 0.091553 | 0.018311 | -121.7331 | 0.20142 | 0.14191 | 0.1236 | -121.7514 | 0.27924 | 0.31586 | 0.36163 | -121.7194 | 0.14649 | 0.12817 | 0.31128 | -121.8613
1820.5469 | 121.9116 | -0.2243 | 121.637 | -0.18036 | 0.047196 | 0.060327 | 0.0031873 | 0.034242 | 0.0012412 | 0.032996 | -0.1767 | 0.0388 | 0.031328 | 0.051806 | -0.00024989 | 0.031417 | 0.027466 | 0.018311 | 0.027466 | 0.022888 | 0.07782 | 0.013733 | -0.1236 | -0.07782 | -0.013733 | -0.17395 | -0.054932 | -0.07782 | -0.16937 | -0.25177 | 0.23804 | 0.10071 | -121.5591 | 0.24261 | 0.24719 | 0.14648 | -121.6095 | 0.054931 | -0.027466 | -121.6919 | 0.14648 | 0.050354 | 0.07782 | -121.7148 | 0.30212 | 0.25177 | 0.25177 | -121.7606 | 0.16937 | 0.14648 | 0.21057 | -121.8887
1822.2969 | 121.875 | -0.24261 | 121.6599 | -0.25665 | 0.046128 | 0.063104 | 0.0057507 | 0.037446 | -0.0075174 | 0.031928 | -0.20721 | 0.035596 | 0.030046 | 0.049883 | -0.0034543 | 0.033126 | 0.018311 | 0.07782 | 0.07782 | 0.036621 | 0.064087 | 0.032043 | -0.091553 | -0.09613 | -0.013733 | -0.17395 | -0.064087 | -0.09613 | -0.17853 | -0.23804 | 0.27466 | 0.15106 | -121.5958 | 0.32044 | 0.27924 | 0.12817 | -121.6415 | 0.064087 | 0.004578 | -121.7239 | 0.14649 | 0.068665 | 0.064087 | -121.756 | 0.3067 | 0.26093 | 0.32044 | -121.7514 | 0.17853 | 0.14649 | 0.22888 | -121.8979
1823.9844 | 121.962 | -0.19684 | 121.6324 | 0.13245 | 0.04036 | 0.058405 | -0.00065795 | 0.03531 | -0.0070902 | 0.03321 | 0.18951 | 0.036023 | 0.026628 | 0.049456 | -3.629e-05 | 0.032913 | 0.07782 | 0.11444 | 0.11444 | 0.073242 | 0.045776 | 0.068665 | -0.073242 | 0.018311 | 0.041199 | -0.086975 | -0.091553 | -0.11444 | -0.13275 | -0.21515 | 0.2655 | 0.1236 | -121.5866 | 0.31128 | 0.27008 | 0.14648 | -121.5546 | 0.064087 | -0.018311 | -121.7239 | 0.21515 | 0.10986 | 0.12817 | -121.7468 | 0.24261 | 0.27466 | 0.31128 | -121.7056 | 0.10529 | 0.082397 | 0.23804 | -121.8475
1825.7344 | 121.8979 | -0.21057 | 121.6599 | 0.079041 | 0.044846 | 0.059473 | 0.00019645 | 0.032533 | 0.00038662 | 0.032142 | 0.090332 | 0.038373 | 0.025774 | 0.053942 | 0.00081811 | 0.031631 | -0.013733 | -0.050354 | -0.032043 | -0.022888 | 0.10071 | 0.032043 | -0.11444 | -0.086975 | -0.086975 | -0.2243 | -0.068665 | -0.068665 | -0.1831 | -0.24261 | 0.24261 | 0.09613 | -121.5591 | 0.16022 | 0.18768 | 0.091553 | -121.6736 | 0.027466 | -0.032044 | -121.7285 | 0.1236 | -0.013733 | 0.018311 | -121.7285 | 0.31128 | 0.19684 | 0.17853 | -121.7743 | 0.14191 | 0.14191 | 0.1236 | -121.9025
1827.4844 | 121.9894 | -0.18768 | 121.6232 | -0.0048827 | 0.042496 | 0.061609 | 0.0046827 | 0.031465 | -0.0087992 | 0.031714 | 0.067444 | 0.037091 | 0.03026 | 0.049242 | -0.0023861 | 0.033981 | -0.004578 | 0.050354 | 0.059509 | 0.022888 | 0.068665 | 0.041199 | -0.10071 | -0.054932 | 0.018311 | -0.11902 | -0.086975 | -0.091553 | -0.15106 | -0.21973 | 0.22888 | 0.086975 | -121.5546 | 0.23804 | 0.21057 | 0.1236 | -121.6278 | 0.036621 | -0.032044 | -121.7102 | 0.13275 | 0.068664 | 0.10071 | -121.7148 | 0.25635 | 0.1831 | 0.24719 | -121.7239 | 0.10071 | 0.09613 | 0.20599 | -121.843
1829.25 | 121.8521 | -0.25635 | 121.6873 | -0.050659 | 0.045273 | 0.062036 | 0.00041005 | 0.03296 | -4.058e-05 | 0.033851 | -0.10803 | 0.039655 | 0.028123 | 0.052447 | 0.0050907 | 0.032486 | 0.041199 | 0.027466 | 0.004578 | 0.009155 | 0.073242 | 0.022888 | -0.11902 | -0.091553 | -0.07782 | -0.23346 | -0.059509 | -0.086975 | -0.16479 | -0.2243 | 0.27924 | 0.13733 | -121.6141 | 0.28381 | 0.2655 | 0.12817 | -121.6461 | 0.091553 | 0.032044 | -121.7468 | 0.1648 | 0.022889 | -0.009155 | -121.7743 | 0.32959 | 0.29755 | 0.26093 | -121.8063 | 0.19684 | 0.16937 | 0.17853 | -121.9116
1830.9375 | 121.9162 | -0.21973 | 121.6599 | -0.24902 | 0.043778 | 0.062036 | 0.0068189 | 0.033174 | -0.0040994 | 0.032142 | -0.2301 | 0.039868 | 0.029619 | 0.052874 | -0.00089089 | 0.029922 | -0.004578 | -0.018311 | -0.027466 | -0.013733 | 0.082397 | 0.013733 | -0.13275 | -0.11444 | -0.054932 | -0.20599 | -0.041199 | -0.064087 | -0.1831 | -0.23804 | 0.23346 | 0.086976 | -121.5775 | 0.20142 | 0.20599 | 0.11902 | -121.6644 | 0.036622 | -0.01831 | -121.7011 | 0.10529 | 0.013733 | 0.032043 | -121.7239 | 0.30212 | 0.21515 | 0.19226 | -121.7926 | 0.17853 | 0.15564 | 0.16479 | -121.8979
1832.6875 | 122.0169 | -0.17395 | 121.6324 | -0.020142 | 0.041642 | 0.061823 | 0.00019645 | 0.034028 | -0.0085856 | 0.031287 | 0.021668 | 0.035169 | 0.027055 | 0.050097 | -0.0038815 | 0.033767 | 0.018311 | 0.054932 | 0.07782 | 0.041199 | 0.054932 | 0.050354 | -0.09613 | -0.013733 | 0.036621 | -0.091553 | -0.07782 | -0.09613 | -0.13733 | -0.19684 | 0.2243 | 0.07782 | -121.5775 | 0.22888 | 0.21515 | 0.13733 | -121.6141 | 0.036621 | -0.022888 | -121.7102 | 0.16022 | 0.082397 | 0.10529 | -121.7285 | 0.22888 | 0.19226 | 0.25177 | -121.7285 | 0.09613 | 0.07782 | 0.21057 | -121.8292
1834.4375 | 121.994 | -0.16479 | 121.6415 | 0.08667 | 0.042496 | 0.060968 | 0.0010511 | 0.033387 | -0.0028178 | 0.031928 | 0.159 | 0.037091 | 0.028123 | 0.052019 | 0.0023135 | 0.030349 | 0.086975 | 0.11444 | 0.10071 | 0.073242 | 0.059509 | 0.050354 | -0.082397 | 0.036621 | 0.054932 | -0.091553 | -0.10986 | -0.11444 | -0.13733 | -0.18768 | 0.21515 | 0.082398 | -121.582 | 0.27924 | 0.23804 | 0.15564 | -121.5546 | 0.027466 | -0.022888 | -121.7514 | 0.20142 | 0.073242 | 0.09613 | -121.756 | 0.2243 | 0.25177 | 0.2655 | -121.7239 | 0.054932 | 0.050354 | 0.21973 | -121.8292
1836.1875 | 121.9528 | -0.20599 | 121.669 | -0.17273 | 0.043991 | 0.060754 | 0.0034009 | 0.033814 | -0.0055948 | 0.031928 | -0.13855 | 0.03581 | 0.028764 | 0.050951 | -0.0030271 | 0.032272 | 0.09613 | 0.14191 | 0.13275 | 0.068665 | 0.050354 | 0.064087 | -0.082397 | 0.022888 | 0.10071 | -0.086975 | -0.09613 | -0.10071 | -0.15106 | -0.20599 | 0.27008 | 0.1236 | -121.6187 | 0.3479 | 0.27466 | 0.15106 | -121.5729 | 0.054932 | 0 | -121.7651 | 0.22888 | 0.11902 | 0.11902 | -121.7697 | 0.25635 | 0.30212 | 0.33875 | -121.7514 | 0.10986 | 0.10529 | 0.3067 | -121.875
1837.875 | 121.8887 | -0.20599 | 121.6827 | -0.081177 | 0.044846 | 0.061182 | 0.0019055 | 0.032105 | 0.0025228 | 0.032569 | -0.13092 | 0.039228 | 0.030046 | 0.051378 | 0.0029543 | 0.031631 | 0.07782 | 0.050354 | 0.041199 | 0.013733 | 0.07782 | 0.013733 | -0.11444 | -0.022888 | -0.009155 | -0.1831 | -0.068665 | -0.059509 | -0.16022 | -0.23346 | 0.21973 | 0.091553 | -121.6049 | 0.25635 | 0.21973 | 0.12817 | -121.6049 | 0.045777 | -0.027465 | -121.7514 | 0.18311 | 0.022889 | 0.050354 | -121.7422 | 0.28381 | 0.28381 | 0.24719 | -121.7972 | 0.13733 | 0.14649 | 0.19684 | -121.9162
1839.625 | 122.0215 | -0.17395 | 121.637 | -0.096436 | 0.039292 | 0.052209 | 0.00083745 | 0.031678 | -0.008372 | 0.031928 | -0.069885 | 0.035169 | 0.027269 | 0.049456 | -0.00067729 | 0.032272 | 0.054932 | 0.11444 | 0.11444 | 0.054932 | 0.054932 | 0.032043 | -0.091553 | 0.027466 | 0.086975 | -0.054932 | -0.082397 | -0.082397 | -0.13733 | -0.18768 | 0.20599 | 0.082397 | -121.582 | 0.28839 | 0.22888 | 0.14649 | -121.582 | 0.036621 | -0.013733 | -121.7194 | 0.20142 | 0.11902 | 0.13275 | -121.7194 | 0.22888 | 0.22888 | 0.28839 | -121.7285 | 0.091553 | 0.091553 | 0.26092 | -121.8246
1841.3594 | 121.8796 | -0.21973 | 121.6919 | -0.073547 | 0.046341 | 0.060541 | 0.0031873 | 0.036164 | 0.0031638 | 0.033423 | -0.092773 | 0.039228 | 0.029619 | 0.052233 | 0.0031681 | 0.031631 | 0.068665 | 0.041199 | 0.027466 | 0.009155 | 0.054932 | 0.027466 | -0.10986 | -0.054932 | -0.041199 | -0.17853 | -0.050354 | -0.054932 | -0.16022 | -0.22888 | 0.24719 | 0.10986 | -121.637 | 0.26093 | 0.22888 | 0.11902 | -121.6232 | 0.05951 | -0.009155 | -121.7422 | 0.16479 | 0.041199 | 0.050354 | -121.7468 | 0.27466 | 0.28839 | 0.24719 | -121.8018 | 0.16937 | 0.16479 | 0.17853 | -121.9208
1843.0469 | 122.0352 | -0.17853 | 121.6599 | -0.0354 | 0.038651 | 0.062891 | 0.0023329 | 0.032533 | -0.0079446 | 0.031714 | -0.016479 | 0.03581 | 0.028123 | 0.049029 | -0.0023861 | 0.032058 | 0.036621 | 0.073242 | 0.068665 | 0.045776 | 0.059509 | 0.036621 | -0.09613 | 0.004578 | 0.054932 | -0.068665 | -0.073242 | -0.091553 | -0.14648 | -0.19684 | 0.21515 | 0.082398 | -121.6003 | 0.25177 | 0.2243 | 0.14191 | -121.6232 | 0.032044 | -0.01831 | -121.7331 | 0.18311 | 0.10986 | 0.12817 | -121.7514 | 0.23804 | 0.21515 | 0.24719 | -121.756 | 0.10529 | 0.086975 | 0.23346 | -121.8567
1844.75 | 122.0306 | -0.17853 | 121.6599 | -0.0354 | 0.04271 | 0.064386 | 0.0048963 | 0.031037 | -0.007731 | 0.033851 | -0.0088499 | 0.036664 | 0.029619 | 0.051592 | -0.0028135 | 0.031845 | 0.041199 | 0.064087 | 0.068665 | 0.032043 | 0.064087 | 0.032043 | -0.091553 | 0.004578 | 0.036621 | -0.10529 | -0.07782 | -0.09613 | -0.14648 | -0.19684 | 0.21057 | 0.086975 | -121.5958 | 0.24261 | 0.21057 | 0.1236 | -121.6187 | 0.032044 | -0.01831 | -121.7377 | 0.18311 | 0.073242 | 0.091552 | -121.756 | 0.24261 | 0.21973 | 0.24719 | -121.7514 | 0.10071 | 0.082398 | 0.21515 | -121.8567
1846.5 | 121.8933 | -0.21515 | 121.7285 | -0.23376 | 0.044632 | 0.061395 | 0.0042555 | 0.034455 | -0.001536 | 0.031501 | -0.19958 | 0.036664 | 0.031541 | 0.050951 | -0.0023861 | 0.030136 | 0.050354 | 0.045776 | 0.036621 | 0.009155 | 0.082397 | 0.032043 | -0.11444 | -0.059509 | -0.036621 | -0.17853 | -0.041199 | -0.041199 | -0.16022 | -0.2243 | 0.24719 | 0.10071 | -121.6461 | 0.26093 | 0.2243 | 0.1236 | -121.6782 | 0.054932 | -0.009155 | -121.7697 | 0.15564 | 0.036621 | 0.045776 | -121.7697 | 0.29755 | 0.2655 | 0.25177 | -121.843 | 0.17395 | 0.17395 | 0.17853 | -121.9528
1848.2812 | 122.0123 | -0.18768 | 121.6965 | -0.012512 | 0.041001 | 0.063745 | 0.0040417 | 0.03061 | -0.0051676 | 0.031714 | 0.036926 | 0.035596 | 0.031114 | 0.05031 | -0.0013181 | 0.031417 | 0.018311 | 0.054932 | 0.059509 | 0.022888 | 0.050354 | 0.054932 | -0.082397 | -0.009155 | 0.009155 | -0.10986 | -0.059509 | -0.082397 | -0.11902 | -0.20142 | 0.24261 | 0.10529 | -121.6461 | 0.24261 | 0.21057 | 0.10528 | -121.6782 | 0.068664 | -0.013733 | -121.756 | 0.17853 | 0.07782 | 0.091553 | -121.7789 | 0.23804 | 0.20599 | 0.24719 | -121.7789 | 0.12817 | 0.10529 | 0.19684 | -121.8979
1849.9688 | 121.9757 | -0.1831 | 121.6873 | 0.15533 | 0.040787 | 0.061823 | -0.0019397 | 0.034028 | -0.0019632 | 0.032996 | 0.11322 | 0.036023 | 0.027696 | 0.051378 | 0.0031681 | 0.032058 | 0.10986 | 0.10986 | 0.1236 | 0.054932 | 0.018311 | 0.064087 | -0.073242 | 0.073242 | 0.059509 | -0.091553 | -0.073242 | -0.10529 | -0.11902 | -0.1831 | 0.24719 | 0.10986 | -121.669 | 0.29297 | 0.23804 | 0.12817 | -121.5775 | 0.064086 | 0 | -121.7606 | 0.25635 | 0.091552 | 0.091552 | -121.7926 | 0.20142 | 0.29297 | 0.3067 | -121.7606 | 0.10986 | 0.077819 | 0.24261 | -121.8704
1851.7031 | 121.8933 | -0.21515 | 121.701 | -0.21088 | 0.044205 | 0.066309 | 0.0063917 | 0.03531 | -0.0028178 | 0.031928 | -0.21484 | 0.034741 | 0.030473 | 0.053515 | 0.0010317 | 0.030777 | 0.082397 | 0.09613 | 0.082397 | 0.054932 | 0.050354 | 0.027466 | -0.09613 | -0.027466 | 0.018311 | -0.16022 | -0.041199 | -0.045776 | -0.14191 | -0.22888 | 0.24261 | 0.11902 | -121.6507 | 0.31128 | 0.27008 | 0.15106 | -121.6187 | 0.073242 | -0.013733 | -121.7422 | 0.18768 | 0.054932 | 0.068665 | -121.7468 | 0.2655 | 0.29755 | 0.29755 | -121.7972 | 0.17395 | 0.16937 | 0.23346 | -121.9299
1853.4531 | 121.9437 | -0.19684 | 121.6827 | 0.071411 | 0.042923 | 0.060114 | 0.0012647 | 0.033814 | 0.0023092 | 0.032996 | 0.0064086 | 0.038373 | 0.025346 | 0.051165 | 0.0038089 | 0.029708 | 0.018311 | -0.027466 | -0.013733 | -0.027466 | 0.10071 | 0.013733 | -0.11902 | -0.064087 | -0.082397 | -0.23346 | -0.018311 | -0.059509 | -0.16022 | -0.2243 | 0.21057 | 0.077819 | -121.582 | 0.16937 | 0.16937 | 0.091553 | -121.6644 | 0.036621 | -0.027466 | -121.701 | 0.13275 | -0.036621 | -0.009155 | -121.7422 | 0.29755 | 0.21515 | 0.18311 | -121.8018 | 0.17853 | 0.13733 | 0.11444 | -121.907
1855.2188 | 121.9025 | -0.21515 | 121.7194 | -0.24139 | 0.045273 | 0.062891 | 0.0051099 | 0.032746 | -0.006663 | 0.031928 | -0.19196 | 0.038373 | 0.029405 | 0.050097 | -0.0013181 | 0.031417 | 0.059509 | 0.054932 | 0.064087 | 0.041199 | 0.068665 | 0.054932 | -0.11444 | -0.054932 | 0.009155 | -0.16479 | -0.036621 | -0.064087 | -0.15106 | -0.21057 | 0.27008 | 0.10071 | -121.6507 | 0.27008 | 0.25635 | 0.15564 | -121.6599 | 0.064087 | 0.004578 | -121.756 | 0.16022 | 0.050354 | 0.045776 | -121.7834 | 0.28381 | 0.27466 | 0.27924 | -121.8338 | 0.17853 | 0.15106 | 0.2243 | -121.9299
1856.9062 | 121.994 | -0.16937 | 121.6324 | -0.18799 | 0.04271 | 0.061182 | 0.0038281 | 0.033387 | -0.0070902 | 0.031928 | -0.092773 | 0.03645 | 0.027483 | 0.05266 | -0.0036679 | 0.032486 | 0.09613 | 0.13733 | 0.13275 | 0.059509 | 0.050354 | 0.07782 | -0.07782 | 0.059509 | 0.10529 | -0.050354 | -0.086975 | -0.10071 | -0.11902 | -0.20599 | 0.24719 | 0.091553 | -121.582 | 0.3067 | 0.22888 | 0.13733 | -121.5363 | 0.050354 | -0.036621 | -121.7194 | 0.22888 | 0.11902 | 0.15564 | -121.7331 | 0.21973 | 0.2655 | 0.30212 | -121.7102 | 0.082398 | 0.068665 | 0.27466 | -121.8384
1858.6562 | 121.962 | -0.19226 | 121.5958 | -0.15747 | 0.040573 | 0.062677 | 0.0023329 | 0.031678 | -0.0064492 | 0.032142 | -0.077515 | 0.037946 | 0.026414 | 0.052233 | -0.0021725 | 0.031631 | 0.10986 | 0.13275 | 0.12817 | 0.082397 | 0.059509 | 0.059509 | -0.082397 | 0.050354 | 0.09613 | -0.045776 | -0.068665 | -0.086975 | -0.14191 | -0.19226 | 0.25177 | 0.10986 | -121.5363 | 0.32501 | 0.27466 | 0.16479 | -121.4859 | 0.050354 | 0 | -121.6644 | 0.24261 | 0.14648 | 0.14648 | -121.6827 | 0.25177 | 0.30212 | 0.32044 | -121.6782 | 0.1236 | 0.10529 | 0.28839 | -121.788
1860.3906 | 121.8018 | -0.21057 | 121.6232 | -0.088806 | 0.045487 | 0.062036 | -0.00023075 | 0.032746 | 0.0040182 | 0.035132 | -0.12329 | 0.040082 | 0.025774 | 0.053728 | 0.0035953 | 0.030777 | 0.09613 | 0.041199 | 0.022888 | 0.018311 | 0.073242 | 0.036621 | -0.1236 | -0.036621 | -0.036621 | -0.21515 | -0.050354 | -0.050354 | -0.16479 | -0.2243 | 0.24719 | 0.086975 | -121.55 | 0.25177 | 0.22888 | 0.14191 | -121.5271 | 0.045776 | -0.013733 | -121.6736 | 0.17395 | -0.004578 | 0.009155 | -121.6736 | 0.28381 | 0.3067 | 0.23346 | -121.7468 | 0.16022 | 0.16022 | 0.17395 | -121.8475
1862.1562 | 121.8109 | -0.21057 | 121.6324 | -0.20325 | 0.043564 | 0.061182 | 0.0040417 | 0.032319 | -0.0055948 | 0.035132 | -0.15381 | 0.03581 | 0.029405 | 0.050951 | -0.0019589 | 0.033981 | 0.091553 | 0.13733 | 0.13275 | 0.073242 | 0.054932 | 0.041199 | -0.086975 | 0.036621 | 0.09613 | -0.07782 | -0.064087 | -0.086975 | -0.11902 | -0.19684 | 0.25177 | 0.1236 | -121.5775 | 0.3479 | 0.28381 | 0.16022 | -121.5408 | 0.091552 | 0.013733 | -121.6965 | 0.24719 | 0.13275 | 0.11902 | -121.7194 | 0.2655 | 0.30212 | 0.34332 | -121.7194 | 0.14648 | 0.1236 | 0.3067 | -121.8292
1863.8438 | 121.9162 | -0.17395 | 121.5637 | 0.13245 | 0.04036 | 0.0599 | -0.0012987 | 0.035737 | 0.00017302 | 0.033637 | 0.097962 | 0.036878 | 0.025987 | 0.052874 | 0.0042361 | 0.031417 | 0.07782 | 0.059509 | 0.054932 | 0.041199 | 0.059509 | 0.054932 | -0.068665 | 0.027466 | 0.041199 | -0.10529 | -0.054932 | -0.082397 | -0.13275 | -0.17853 | 0.22888 | 0.10528 | -121.5042 | 0.23346 | 0.21515 | 0.10986 | -121.4859 | 0.041199 | -0.004578 | -121.6187 | 0.20142 | 0.068664 | 0.073242 | -121.6461 | 0.23346 | 0.25177 | 0.22888 | -121.6324 | 0.11902 | 0.091553 | 0.21515 | -121.7422
1865.5938 | 121.8521 | -0.17853 | 121.5454 | 0.11719 | 0.04271 | 0.061395 | 0.0021191 | 0.034669 | -0.0040994 | 0.034492 | 0.12085 | 0.03645 | 0.027269 | 0.049883 | -0.00067729 | 0.03334 | 0.09613 | 0.14191 | 0.11902 | 0.064087 | 0.041199 | 0.064087 | -0.082397 | 0.045776 | 0.059509 | -0.068665 | -0.064087 | -0.082397 | -0.14191 | -0.18768 | 0.24261 | 0.096131 | -121.5042 | 0.32044 | 0.24261 | 0.14648 | -121.4493 | 0.036621 | -0.009155 | -121.6095 | 0.2243 | 0.10986 | 0.11902 | -121.6278 | 0.21973 | 0.27466 | 0.29755 | -121.6278 | 0.11444 | 0.096131 | 0.23804 | -121.7331
1867.3438 | 121.8338 | -0.19226 | 121.5683 | 0.10956 | 0.044205 | 0.061823 | 0.00083745 | 0.03296 | 0.0014548 | 0.033851 | 0.029297 | 0.040937 | 0.02556 | 0.05266 | 0.0027407 | 0.032699 | 0.032043 | -0.036621 | -0.032043 | -0.013733 | 0.091553 | 0.032043 | -0.11444 | -0.064087 | -0.086975 | -0.21973 | -0.041199 | -0.054932 | -0.1831 | -0.21973 | 0.2243 | 0.07782 | -121.4767 | 0.15564 | 0.17853 | 0.10071 | -121.5363 | 0.009156 | -0.027466 | -121.6095 | 0.12817 | -0.027466 | 0 | -121.6232 | 0.28381 | 0.2243 | 0.16022 | -121.6827 | 0.15106 | 0.13733 | 0.10529 | -121.788
1869.1094 | 121.8338 | -0.18768 | 121.5637 | 0.094299 | 0.041428 | 0.060754 | 0.0059643 | 0.033387 | -0.0058084 | 0.032783 | 0.097962 | 0.03645 | 0.029832 | 0.053087 | -0.0019589 | 0.034835 | 0.07782 | 0.082397 | 0.10986 | 0.032043 | 0.041199 | 0.054932 | -0.073242 | 0.018311 | 0.018311 | -0.09613 | -0.073242 | -0.064087 | -0.13733 | -0.17853 | 0.24261 | 0.11444 | -121.5225 | 0.27008 | 0.21973 | 0.10529 | -121.4859 | 0.050354 | 0.009155 | -121.637 | 0.20599 | 0.091553 | 0.082398 | -121.6278 | 0.22888 | 0.2655 | 0.29755 | -121.637 | 0.11444 | 0.1236 | 0.20599 | -121.7422
1870.7969 | 121.7651 | -0.21057 | 121.5317 | 0.063782 | 0.043351 | 0.062463 | 0.0010511 | 0.033174 | 0.001882 | 0.034705 | 0.044556 | 0.040296 | 0.029192 | 0.054583 | 0.0010317 | 0.031845 | 0.022888 | -0.050354 | -0.022888 | -0.013733 | 0.086975 | 0.036621 | -0.11444 | -0.068665 | -0.07782 | -0.21973 | -0.022888 | -0.064087 | -0.16022 | -0.22888 | 0.24719 | 0.09613 | -121.4447 | 0.16022 | 0.19684 | 0.10071 | -121.5088 | 0.050354 | -0.018311 | -121.5546 | 0.14191 | -0.009156 | 0.009155 | -121.5958 | 0.29755 | 0.23346 | 0.18768 | -121.6461 | 0.18768 | 0.14648 | 0.13275 | -121.7606
1872.5469 | 121.7606 | -0.20142 | 121.5408 | 0.040894 | 0.043564 | 0.060754 | 0.0027601 | 0.033174 | 0.0033774 | 0.035346 | 0.014038 | 0.041364 | 0.027696 | 0.053515 | 0.0033817 | 0.032058 | 0.004578 | -0.068665 | -0.032043 | -0.022888 | 0.091553 | 0.036621 | -0.11902 | -0.068665 | -0.086975 | -0.21973 | -0.027466 | -0.041199 | -0.15564 | -0.2243 | 0.23804 | 0.082397 | -121.4493 | 0.13275 | 0.17853 | 0.096131 | -121.5363 | 0.045776 | -0.022888 | -121.5683 | 0.13275 | -0.018311 | 0.004577 | -121.582 | 0.29297 | 0.20599 | 0.16937 | -121.6599 | 0.17395 | 0.16022 | 0.11444 | -121.7651
1874.2969 | 121.7926 | -0.2243 | 121.5317 | -0.24139 | 0.042496 | 0.060541 | 0.0023329 | 0.031892 | -0.00046778 | 0.032569 | -0.23773 | 0.038587 | 0.026842 | 0.053515 | -3.629e-05 | 0.032058 | 0.004578 | -0.027466 | -0.018311 | -0.004578 | 0.09613 | 0.022888 | -0.11444 | -0.09613 | -0.041199 | -0.19684 | -0.027466 | -0.036621 | -0.17853 | -0.2243 | 0.24719 | 0.10986 | -121.4355 | 0.19684 | 0.21973 | 0.10986 | -121.5271 | 0.045776 | 0 | -121.5591 | 0.12817 | 0.027466 | 0.027466 | -121.5683 | 0.32043 | 0.22888 | 0.20599 | -121.6461 | 0.19684 | 0.18768 | 0.18311 | -121.756
1876 | 121.7834 | -0.20599 | 121.5729 | -0.18799 | 0.044632 | 0.061823 | 0.0042555 | 0.031892 | -0.002604 | 0.032783 | -0.21484 | 0.037519 | 0.030687 | 0.05266 | 0.0018863 | 0.032058 | 0.018311 | -0.013733 | -0.009155 | 0.013733 | 0.07782 | 0.009155 | -0.10986 | -0.068665 | -0.032043 | -0.1831 | -0.032043 | -0.041199 | -0.14191 | -0.2243 | 0.21515 | 0.096131 | -121.4951 | 0.19226 | 0.21973 | 0.1236 | -121.5546 | 0.064087 | -0.01831 | -121.6049 | 0.13733 | 0.022889 | 0.041199 | -121.6141 | 0.28381 | 0.22431 | 0.19684 | -121.6827 | 0.17395 | 0.1648 | 0.17395 | -121.7972
1877.75 | 121.875 | -0.19226 | 121.5225 | 0.0027468 | 0.041642 | 0.0646 | 0.0046827 | 0.034669 | -0.010295 | 0.031928 | 0.067444 | 0.036237 | 0.02791 | 0.052233 | -0.0025999 | 0.033554 | 0.018311 | 0.054932 | 0.073242 | 0.022888 | 0.059509 | 0.068665 | -0.086975 | -0.022888 | 0.009155 | -0.10071 | -0.059509 | -0.068665 | -0.13733 | -0.19226 | 0.26093 | 0.10529 | -121.463 | 0.24719 | 0.21515 | 0.10986 | -121.5042 | 0.054932 | 0 | -121.582 | 0.16937 | 0.091553 | 0.091553 | -121.5912 | 0.25177 | 0.21057 | 0.2655 | -121.6095 | 0.13275 | 0.1236 | 0.20142 | -121.7148
1879.5156 | 121.7377 | -0.21057 | 121.5317 | -0.18799 | 0.044419 | 0.062891 | 0.0023329 | 0.033814 | -0.0047404 | 0.031928 | -0.22247 | 0.037946 | 0.028551 | 0.052447 | 0.00017731 | 0.033767 | 0 | 0.009155 | 0.004578 | -0.022888 | 0.091553 | 0.027466 | -0.11444 | -0.082397 | -0.036621 | -0.19684 | -0.027466 | -0.054932 | -0.16937 | -0.23804 | 0.23804 | 0.09613 | -121.4401 | 0.21973 | 0.18768 | 0.091553 | -121.5317 | 0.041198 | -0.027466 | -121.5591 | 0.12817 | 0.013733 | 0.041199 | -121.5866 | 0.30212 | 0.21057 | 0.21515 | -121.6461 | 0.18311 | 0.15564 | 0.17395 | -121.7697
1881.2656 | 121.8109 | -0.1831 | 121.5271 | 0.08667 | 0.03801 | 0.060968 | 0.0023329 | 0.03531 | -0.0064492 | 0.033423 | 0.097962 | 0.036023 | 0.028551 | 0.052233 | -0.0013181 | 0.033767 | 0.068665 | 0.082397 | 0.10529 | 0.041199 | 0.054932 | 0.050354 | -0.07782 | 0 | 0.018311 | -0.10986 | -0.068665 | -0.068665 | -0.1236 | -0.17853 | 0.23346 | 0.10528 | -121.4722 | 0.2655 | 0.2243 | 0.11902 | -121.4584 | 0.059509 | 0.004577 | -121.5958 | 0.1831 | 0.073242 | 0.068665 | -121.5958 | 0.23804 | 0.25177 | 0.28839 | -121.6049 | 0.11444 | 0.11444 | 0.20142 | -121.7056
1882.9531 | 121.843 | -0.19226 | 121.5042 | 0.0027468 | 0.038437 | 0.064172 | 0.0040417 | 0.03296 | -0.0064492 | 0.030006 | 0.059815 | 0.037732 | 0.026842 | 0.051592 | -0.0015317 | 0.033126 | 0.045776 | 0.054932 | 0.07782 | 0.027466 | 0.064087 | 0.064087 | -0.091553 | -0.013733 | 0.009155 | -0.091553 | -0.045776 | -0.073242 | -0.11902 | -0.19226 | 0.25635 | 0.10071 | -121.4401 | 0.24719 | 0.21973 | 0.11902 | -121.4584 | 0.073242 | 0 | -121.55 | 0.17853 | 0.10071 | 0.10071 | -121.5775 | 0.25635 | 0.23804 | 0.27008 | -121.5958 | 0.14648 | 0.11902 | 0.20142 | -121.6965
1884.7031 | 121.8109 | -0.18768 | 121.4676 | 0.040894 | 0.039292 | 0.063318 | 0.0010511 | 0.031892 | -0.0053812 | 0.031287 | 0.067444 | 0.036878 | 0.028123 | 0.050097 | -3.629e-05 | 0.031631 | 0.064087 | 0.068665 | 0.07782 | 0.027466 | 0.059509 | 0.054932 | -0.07782 | -0.009155 | 0.009155 | -0.10986 | -0.064087 | -0.07782 | -0.12817 | -0.18768 | 0.24261 | 0.10986 | -121.4081 | 0.25635 | 0.21515 | 0.10529 | -121.4035 | 0.059509 | 0 | -121.5317 | 0.17853 | 0.07782 | 0.07782 | -121.5454 | 0.24719 | 0.25177 | 0.2655 | -121.5454 | 0.1236 | 0.10986 | 0.19684 | -121.6553
1886.4531 | 121.7148 | -0.21515 | 121.5454 | -0.21851 | 0.045487 | 0.06225 | 0.0034009 | 0.035096 | -0.0023904 | 0.030433 | -0.21484 | 0.035382 | 0.027055 | 0.052874 | 0.00081811 | 0.031631 | 0.054932 | 0.013733 | 0.013733 | 0.009155 | 0.068665 | 0.013733 | -0.10071 | -0.064087 | -0.032043 | -0.19226 | -0.022888 | -0.041199 | -0.16479 | -0.21973 | 0.22888 | 0.11444 | -121.4767 | 0.22888 | 0.2243 | 0.10986 | -121.4905 | 0.050354 | -0.004578 | -121.5683 | 0.15106 | 0.022888 | 0.027466 | -121.5866 | 0.28381 | 0.27008 | 0.22888 | -121.6461 | 0.19226 | 0.17395 | 0.18311 | -121.7651
1888.2031 | 121.7148 | -0.23804 | 121.5134 | -0.24139 | 0.041855 | 0.062891 | 0.0055371 | 0.035737 | -0.002604 | 0.031287 | -0.2301 | 0.039441 | 0.028764 | 0.051165 | -3.629e-05 | 0.031204 | 0.073242 | 0.068665 | 0.07782 | 0.045776 | 0.07782 | 0.036621 | -0.10986 | -0.036621 | -0.004578 | -0.16479 | -0.027466 | -0.045776 | -0.16022 | -0.20599 | 0.27466 | 0.12817 | -121.4355 | 0.3067 | 0.28381 | 0.15564 | -121.4401 | 0.07782 | 0.032043 | -121.5408 | 0.20142 | 0.073242 | 0.041199 | -121.5591 | 0.31586 | 0.31128 | 0.31586 | -121.6232 | 0.21057 | 0.19226 | 0.23346 | -121.7194
1889.8906 | 121.7697 | -0.20142 | 121.4996 | -0.14984 | 0.046982 | 0.061395 | 0.0029737 | 0.032105 | 0.0014548 | 0.03321 | -0.23773 | 0.037091 | 0.033037 | 0.053301 | 0.00039091 | 0.03099 | 0.059509 | 0.036621 | 0.032043 | 0.032043 | 0.09613 | 0.027466 | -0.13275 | -0.009155 | 0.009155 | -0.17395 | -0.013733 | -0.045776 | -0.14648 | -0.21515 | 0.22888 | 0.068665 | -121.4035 | 0.23804 | 0.23346 | 0.16479 | -121.4401 | 0.054932 | -0.013733 | -121.5134 | 0.19226 | 0.027466 | 0.041199 | -121.5454 | 0.29755 | 0.26093 | 0.23346 | -121.6324 | 0.18768 | 0.15564 | 0.21057 | -121.7148
1891.6406 | 121.7194 | -0.20599 | 121.5225 | 0.071411 | 0.041855 | 0.062463 | -0.0017261 | 0.033387 | -4.058e-05 | 0.033423 | 0.067444 | 0.039655 | 0.028551 | 0.053301 | 0.0042361 | 0.033767 | -0.004578 | -0.027466 | -0.022888 | -0.013733 | 0.086975 | 0.032043 | -0.10071 | -0.073242 | -0.10071 | -0.2243 | -0.018311 | -0.036621 | -0.16479 | -0.23346 | 0.23804 | 0.10529 | -121.4355 | 0.17853 | 0.19226 | 0.086975 | -121.5271 | 0.041199 | -0.027465 | -121.5408 | 0.13275 | -0.01831 | 0.009155 | -121.5591 | 0.29297 | 0.20142 | 0.18311 | -121.6232 | 0.18768 | 0.16937 | 0.10529 | -121.756
1893.4062 | 121.8063 | -0.17853 | 121.4859 | 0.018005 | 0.04036 | 0.061609 | 0.0036145 | 0.032746 | -0.0073038 | 0.032142 | 0.067444 | 0.034741 | 0.03026 | 0.054369 | -0.0019589 | 0.033126 | 0.041199 | 0.059509 | 0.07782 | 0.041199 | 0.054932 | 0.054932 | -0.07782 | -0.022888 | 0.032043 | -0.11444 | -0.059509 | -0.073242 | -0.14648 | -0.16937 | 0.23346 | 0.10071 | -121.431 | 0.23804 | 0.21973 | 0.11902 | -121.4447 | 0.032044 | 0.009155 | -121.5454 | 0.15564 | 0.064087 | 0.054932 | -121.5591 | 0.23346 | 0.21973 | 0.25635 | -121.5637 | 0.11902 | 0.10529 | 0.21057 | -121.6553
1895.1562 | 121.8338 | -0.14648 | 121.4859 | -0.050659 | 0.042923 | 0.059259 | 0.0044691 | 0.033814 | -0.0058084 | 0.031714 | -0.039368 | 0.033246 | 0.030046 | 0.048388 | -0.0051633 | 0.028213 | 0.050354 | 0.07782 | 0.09613 | 0.045776 | 0.050354 | 0.054932 | -0.086975 | 0.054932 | 0.09613 | -0.036621 | -0.041199 | -0.059509 | -0.10071 | -0.15106 | 0.20142 | 0.059509 | -121.4355 | 0.2243 | 0.19226 | 0.13275 | -121.4355 | 0.045776 | -0.004578 | -121.5271 | 0.20142 | 0.10986 | 0.11444 | -121.5454 | 0.19684 | 0.19684 | 0.24261 | -121.5729 | 0.10529 | 0.086975 | 0.24261 | -121.637
1896.8438 | 121.843 | -0.16479 | 121.5454 | 0.10956 | 0.041428 | 0.061609 | 0.0031873 | 0.032105 | -0.0062356 | 0.030433 | 0.082703 | 0.034314 | 0.032396 | 0.04732 | 0.00017731 | 0.03099 | 0.07782 | 0.10529 | 0.086975 | 0.045776 | 0.041199 | 0.054932 | -0.07782 | 0.041199 | 0.032043 | -0.07782 | -0.022888 | -0.050354 | -0.10071 | -0.16937 | 0.21973 | 0.086975 | -121.5042 | 0.27008 | 0.21057 | 0.1236 | -121.4676 | 0.064087 | -0.004578 | -121.5683 | 0.20599 | 0.086975 | 0.091553 | -121.5958 | 0.20599 | 0.24261 | 0.25177 | -121.6232 | 0.14191 | 0.11444 | 0.19684 | -121.7148
1898.5938 | 121.8384 | -0.19226 | 121.6141 | -0.21851 | 0.046128 | 0.061395 | 0.0057507 | 0.034028 | -0.00068138 | 0.033423 | -0.24536 | 0.034101 | 0.033037 | 0.048601 | 0.0010317 | 0.028213 | 0.018311 | -0.027466 | -0.022888 | -0.013733 | 0.082397 | 0.013733 | -0.1236 | -0.050354 | -0.027466 | -0.17395 | 0.027466 | -0.004578 | -0.14648 | -0.19226 | 0.20599 | 0.068665 | -121.5317 | 0.16479 | 0.17853 | 0.10986 | -121.5958 | 0.045777 | 0 | -121.5866 | 0.14191 | 0.018311 | 0.018311 | -121.6187 | 0.27466 | 0.21057 | 0.16937 | -121.7377 | 0.21973 | 0.18768 | 0.16479 | -121.8063
1900.3594 | 121.875 | -0.16479 | 121.637 | -0.18799 | 0.043778 | 0.063745 | 0.0063917 | 0.032319 | -0.0055948 | 0.030646 | -0.13855 | 0.032605 | 0.033464 | 0.048601 | -0.0028135 | 0.029708 | 0.09613 | 0.13733 | 0.13275 | 0.064087 | 0.032043 | 0.045776 | -0.082397 | 0.059509 | 0.1236 | -0.036621 | -0.018311 | -0.059509 | -0.10071 | -0.13733 | 0.21057 | 0.082398 | -121.6049 | 0.30212 | 0.22888 | 0.14648 | -121.5408 | 0.064087 | 0.027466 | -121.6553 | 0.2243 | 0.12817 | 0.10071 | -121.6965 | 0.19684 | 0.26092 | 0.29755 | -121.7194 | 0.14648 | 0.10529 | 0.28839 | -121.7743
1902.1094 | 121.8796 | -0.18768 | 121.6507 | -0.14984 | 0.044846 | 0.062463 | 0.0034009 | 0.033387 | 0.0014548 | 0.032569 | -0.25299 | 0.032392 | 0.033037 | 0.047533 | 0.0029543 | 0.027786 | 0.036621 | -0.004578 | -0.009155 | 0 | 0.07782 | 0.022888 | -0.11444 | -0.022888 | 0.009155 | -0.14648 | 0.009155 | -0.022888 | -0.13275 | -0.1831 | 0.21057 | 0.073242 | -121.5729 | 0.1831 | 0.18768 | 0.11444 | -121.6141 | 0.054932 | 0.004578 | -121.6415 | 0.16479 | 0.041199 | 0.036621 | -121.6736 | 0.2655 | 0.2243 | 0.17853 | -121.7651 | 0.19684 | 0.16479 | 0.19684 | -121.8338
1903.7969 | 121.8246 | -0.17395 | 121.637 | -0.065918 | 0.04506 | 0.061182 | 0.0023329 | 0.033387 | 0.00060022 | 0.034492 | -0.069885 | 0.034741 | 0.03325 | 0.049456 | 0.0046633 | 0.030136 | 0.054932 | 0.041199 | 0.018311 | 0.018311 | 0.086975 | 0.022888 | -0.10529 | -0.022888 | -0.022888 | -0.17853 | 0.009155 | 0 | -0.11902 | -0.1831 | 0.19684 | 0.068664 | -121.55 | 0.21515 | 0.19226 | 0.1236 | -121.582 | 0.054931 | -0.009155 | -121.6278 | 0.15106 | -0.004578 | 0.004577 | -121.637 | 0.26092 | 0.22888 | 0.19226 | -121.7422 | 0.1831 | 0.17395 | 0.15106 | -121.8201
1905.5469 | 121.8887 | -0.18768 | 121.6827 | -0.22614 | 0.043564 | 0.061395 | 0.0057507 | 0.032105 | -0.0017496 | 0.033637 | -0.21484 | 0.034741 | 0.034105 | 0.046679 | -0.00046349 | 0.03099 | -0.009155 | -0.009155 | -0.018311 | -0.013733 | 0.086975 | -0.004578 | -0.13275 | -0.022888 | -0.013733 | -0.1831 | 0.022888 | 0.004578 | -0.14191 | -0.18768 | 0.1831 | 0.054932 | -121.5958 | 0.17853 | 0.17395 | 0.11902 | -121.6919 | 0.045776 | 0 | -121.6599 | 0.16479 | 0.004578 | 0.004578 | -121.6782 | 0.27466 | 0.17853 | 0.16937 | -121.8155 | 0.21057 | 0.19226 | 0.17395 | -121.8704
1907.2969 | 121.962 | -0.15564 | 121.6644 | 0.10956 | 0.042282 | 0.060541 | 0.00083745 | 0.035096 | -0.0038858 | 0.033423 | 0.18951 | 0.032605 | 0.033464 | 0.047533 | 0.0010317 | 0.031204 | 0.07782 | 0.12817 | 0.11444 | 0.068665 | 0.027466 | 0.068665 | -0.073242 | 0.082397 | 0.082397 | -0.041199 | -0.027466 | -0.045776 | -0.10071 | -0.16022 | 0.22431 | 0.082398 | -121.637 | 0.28381 | 0.22431 | 0.14191 | -121.5866 | 0.054932 | -0.004577 | -121.6919 | 0.23804 | 0.11444 | 0.11902 | -121.7102 | 0.18311 | 0.23346 | 0.27008 | -121.7377 | 0.12817 | 0.10986 | 0.23804 | -121.8246
1909 | 121.9849 | -0.15564 | 121.6415 | -0.11932 | 0.041855 | 0.064172 | 0.0027601 | 0.034028 | -0.0058084 | 0.031501 | -0.062256 | 0.031964 | 0.031969 | 0.048174 | 0.00017731 | 0.030777 | 0.09613 | 0.15564 | 0.1236 | 0.07782 | 0.036621 | 0.054932 | -0.082397 | 0.11902 | 0.13275 | -0.036621 | -0.004578 | -0.041199 | -0.091553 | -0.17395 | 0.21057 | 0.073243 | -121.6049 | 0.31128 | 0.23346 | 0.16022 | -121.5454 | 0.064087 | -0.01831 | -121.6461 | 0.27466 | 0.11902 | 0.13733 | -121.6827 | 0.19226 | 0.25177 | 0.27924 | -121.7239 | 0.15106 | 0.11444 | 0.28839 | -121.8155
1910.75 | 121.875 | -0.20142 | 121.6965 | 0.056152 | 0.045487 | 0.060754 | 0.0014783 | 0.031678 | 0.0023092 | 0.034278 | 0.036926 | 0.031537 | 0.038591 | 0.045824 | 0.0020999 | 0.031417 | -0.009155 | -0.054932 | -0.041199 | -0.018311 | 0.086975 | 0.022888 | -0.10986 | -0.022888 | -0.068665 | -0.20599 | 0.027466 | 0.018311 | -0.15106 | -0.21515 | 0.2243 | 0.091553 | -121.6095 | 0.14648 | 0.18311 | 0.091552 | -121.7056 | 0.050354 | -0.013733 | -121.669 | 0.17853 | -0.004578 | 0.009155 | -121.6782 | 0.28839 | 0.19226 | 0.16022 | -121.8063 | 0.22888 | 0.21973 | 0.13275 | -121.9116
1912.5 | 121.9482 | -0.16937 | 121.6873 | 0.10956 | 0.042282 | 0.061823 | 0.0025465 | 0.035523 | -0.0079446 | 0.032142 | 0.12848 | 0.030255 | 0.037523 | 0.047961 | -0.0032407 | 0.03334 | 0.045776 | 0.10529 | 0.086975 | 0.032043 | 0.036621 | 0.041199 | -0.082397 | 0.07782 | 0.045776 | -0.10071 | -0.004578 | -0.009155 | -0.13275 | -0.17853 | 0.21057 | 0.086976 | -121.6507 | 0.27466 | 0.20142 | 0.11444 | -121.6415 | 0.036622 | -0.009155 | -121.6919 | 0.24719 | 0.068665 | 0.07782 | -121.6965 | 0.20599 | 0.21515 | 0.25635 | -121.7697 | 0.16479 | 0.16022 | 0.21515 | -121.8658
1914.25 | 121.9849 | -0.16479 | 121.6965 | 0.010376 | 0.041855 | 0.063318 | 0.0023329 | 0.031465 | -0.0085856 | 0.03321 | 0.059815 | 0.028974 | 0.032823 | 0.044115 | -0.0038815 | 0.033126 | 0.032043 | 0.068665 | 0.068665 | 0.018311 | 0.041199 | 0.050354 | -0.091553 | 0.050354 | 0.032043 | -0.10071 | 0.009155 | -0.004578 | -0.10986 | -0.19226 | 0.21515 | 0.073242 | -121.6553 | 0.23346 | 0.18311 | 0.10986 | -121.6644 | 0.054932 | -0.027466 | -121.6873 | 0.21515 | 0.064087 | 0.091553 | -121.701 | 0.20599 | 0.19684 | 0.23346 | -121.788 | 0.17395 | 0.16022 | 0.19684 | -121.8887
1915.9375 | 121.9757 | -0.13733 | 121.6919 | 0.12482 | 0.041855 | 0.060541 | 0.0023329 | 0.031892 | -0.0038858 | 0.032783 | 0.12085 | 0.030042 | 0.034746 | 0.045183 | 0.00081811 | 0.030777 | 0.11444 | 0.10986 | 0.11444 | 0.059509 | 0.027466 | 0.064087 | -0.07782 | 0.10986 | 0.059509 | -0.059509 | -0.013733 | -0.022888 | -0.11444 | -0.16479 | 0.20142 | 0.059509 | -121.6644 | 0.24719 | 0.19684 | 0.13733 | -121.5775 | 0.022888 | -0.027466 | -121.7056 | 0.24719 | 0.07782 | 0.10529 | -121.7148 | 0.16479 | 0.25177 | 0.25177 | -121.7697 | 0.1236 | 0.11444 | 0.19684 | -121.8567
1917.6719 | 121.9025 | -0.20599 | 121.701 | 0.040894 | 0.047623 | 0.060327 | 0.0051099 | 0.033814 | 0.001882 | 0.03321 | 0.014038 | 0.032392 | 0.040941 | 0.046465 | 0.0010317 | 0.031417 | 0 | -0.045776 | -0.036621 | -0.032043 | 0.082397 | 0.013733 | -0.11444 | 0 | -0.07782 | -0.20599 | 0.041199 | 0.018311 | -0.13275 | -0.20599 | 0.21973 | 0.091553 | -121.6187 | 0.16022 | 0.17395 | 0.082398 | -121.701 | 0.073243 | 0 | -121.6599 | 0.20599 | 0 | 0 | -121.6827 | 0.28839 | 0.20599 | 0.16937 | -121.8155 | 0.24719 | 0.22431 | 0.12817 | -121.907
1919.4375 | 121.8842 | -0.18768 | 121.7422 | -0.088806 | 0.043351 | 0.061182 | 0.0023329 | 0.035737 | 0.0016684 | 0.034492 | -0.11566 | 0.030255 | 0.038591 | 0.04497 | 0.0023135 | 0.03099 | 0.068665 | 0.059509 | 0.032043 | 0.018311 | 0.091553 | 0.036621 | -0.1236 | 0.041199 | 0.009155 | -0.16022 | 0.022888 | 0.004578 | -0.16022 | -0.19684 | 0.2243 | 0.064087 | -121.6507 | 0.24719 | 0.20599 | 0.14191 | -121.6736 | 0.027466 | -0.009155 | -121.7194 | 0.22888 | 0.027466 | 0.036621 | -121.7377 | 0.27924 | 0.25635 | 0.21973 | -121.8658 | 0.21057 | 0.19226 | 0.19684 | -121.9391
1921.2031 | 121.9254 | -0.20142 | 121.7377 | -0.088806 | 0.043991 | 0.06225 | -0.00044435 | 0.032746 | -0.0019632 | 0.035773 | -0.13855 | 0.030683 | 0.036455 | 0.044115 | 0.0033817 | 0.031204 | 0.045776 | 0.054932 | 0.022888 | 0.022888 | 0.073242 | 0.027466 | -0.10986 | 0.059509 | 0.027466 | -0.14648 | 0.032043 | 0.004578 | -0.14191 | -0.21057 | 0.22888 | 0.091553 | -121.6644 | 0.25635 | 0.2243 | 0.13275 | -121.6919 | 0.059509 | -0.009155 | -121.7056 | 0.26093 | 0.054932 | 0.064087 | -121.7331 | 0.27466 | 0.24719 | 0.2243 | -121.8475 | 0.23346 | 0.20599 | 0.22888 | -121.9482
1922.9062 | 121.907 | -0.21057 | 121.7697 | -0.0048827 | 0.0457 | 0.058618 | 0.00062385 | 0.032105 | -0.00025418 | 0.035987 | 0.014038 | 0.030255 | 0.039018 | 0.044115 | 0.0018863 | 0.031631 | -0.004578 | -0.013733 | -0.022888 | -0.013733 | 0.073242 | 0.032043 | -0.1236 | -0.036621 | -0.050354 | -0.20142 | 0.022888 | 0 | -0.15564 | -0.21057 | 0.24261 | 0.086975 | -121.6965 | 0.19684 | 0.19684 | 0.10986 | -121.7743 | 0.054931 | 0 | -121.7468 | 0.17395 | 0.009155 | 0.009155 | -121.7697 | 0.28381 | 0.20599 | 0.18768 | -121.8933 | 0.23346 | 0.21057 | 0.16022 | -121.9803
1924.6719 | 122.0306 | -0.16479 | 121.7377 | -0.0048827 | 0.037155 | 0.063532 | 0.0031873 | 0.031251 | -0.011363 | 0.034492 | 0.059815 | 0.027478 | 0.034532 | 0.044756 | -0.0028135 | 0.035904 | 0 | 0.050354 | 0.054932 | 0.027466 | 0.045776 | 0.045776 | -0.10071 | 0.032043 | 0.050354 | -0.07782 | 0.009155 | -0.009155 | -0.11444 | -0.16479 | 0.21057 | 0.064087 | -121.6919 | 0.21515 | 0.19226 | 0.12817 | -121.7377 | 0.050354 | 0 | -121.7285 | 0.19684 | 0.086975 | 0.086975 | -121.7468 | 0.21057 | 0.16479 | 0.21973 | -121.8384 | 0.17395 | 0.15564 | 0.21515 | -121.9025
1926.4219 | 121.9391 | -0.17395 | 121.7514 | -0.12695 | 0.041642 | 0.060754 | 0.0019055 | 0.034883 | 0.0016684 | 0.033423 | -0.14618 | 0.03346 | 0.033464 | 0.043047 | 0.0033817 | 0.028427 | 0.054932 | 0.022888 | 0.027466 | 0.018311 | 0.073242 | 0.027466 | -0.10529 | 0.036621 | 0.041199 | -0.11444 | 0 | 0.009155 | -0.13733 | -0.18768 | 0.20142 | 0.068664 | -121.6782 | 0.19684 | 0.19226 | 0.1236 | -121.6965 | 0.036621 | -0.013733 | -121.7514 | 0.21057 | 0.059509 | 0.073242 | -121.7422 | 0.24719 | 0.22888 | 0.20142 | -121.8567 | 0.17395 | 0.1831 | 0.21515 | -121.9391
1928.1719 | 121.9345 | -0.19684 | 121.7743 | -0.18799 | 0.043564 | 0.063318 | 0.0059643 | 0.031678 | -0.0075174 | 0.034705 | -0.15381 | 0.027692 | 0.036241 | 0.045611 | -0.0021725 | 0.033554 | 0.064087 | 0.10071 | 0.10986 | 0.068665 | 0.032043 | 0.059509 | -0.09613 | 0.050354 | 0.10986 | -0.073242 | -0.004578 | -0.009155 | -0.10071 | -0.14648 | 0.25635 | 0.10071 | -121.7422 | 0.29755 | 0.2655 | 0.16479 | -121.7102 | 0.09613 | 0.050354 | -121.7789 | 0.24719 | 0.1236 | 0.073242 | -121.7834 | 0.22888 | 0.26093 | 0.3067 | -121.8704 | 0.19226 | 0.18768 | 0.3067 | -121.9208
1929.8594 | 121.9482 | -0.20142 | 121.7606 | -0.23376 | 0.0457 | 0.063532 | 0.0068189 | 0.03296 | -0.0034586 | 0.032355 | -0.22247 | 0.030042 | 0.036668 | 0.044543 | -0.0019589 | 0.03099 | 0 | -0.009155 | 0.004578 | -0.009155 | 0.082397 | -0.004578 | -0.11444 | -0.032043 | -0.004578 | -0.16937 | 0.045776 | 0.027466 | -0.14648 | -0.20142 | 0.19684 | 0.086975 | -121.6782 | 0.19226 | 0.19226 | 0.10529 | -121.7606 | 0.054932 | 0 | -121.7148 | 0.16937 | 0.032043 | 0.032043 | -121.7331 | 0.28381 | 0.20142 | 0.20599 | -121.875 | 0.24719 | 0.22888 | 0.19684 | -121.962
1931.5938 | 121.9757 | -0.16937 | 121.7422 | -0.14221 | 0.047196 | 0.061182 | 0.0042555 | 0.03296 | -0.00025418 | 0.033423 | -0.14618 | 0.031751 | 0.034105 | 0.044756 | 0.0010317 | 0.02864 | 0.059509 | 0.032043 | 0.032043 | 0.018311 | 0.091553 | 0.018311 | -0.10986 | 0.032043 | 0.036621 | -0.12817 | 0.018311 | 0.018311 | -0.13733 | -0.17853 | 0.18768 | 0.05951 | -121.6507 | 0.20142 | 0.18768 | 0.12817 | -121.6827 | 0.032044 | -0.009155 | -121.7239 | 0.20142 | 0.041199 | 0.050354 | -121.7239 | 0.26093 | 0.22888 | 0.20142 | -121.8521 | 0.18768 | 0.18768 | 0.20599 | -121.9208
1933.3438 | 121.9986 | -0.16022 | 121.7468 | 0.10956 | 0.042496 | 0.060541 | -0.00087155 | 0.032105 | -0.0011088 | 0.034064 | 0.052185 | 0.032605 | 0.036027 | 0.046465 | 0.0014591 | 0.033126 | -0.018311 | -0.036621 | -0.041199 | -0.018311 | 0.073242 | 0.018311 | -0.11902 | -0.004578 | -0.041199 | -0.18768 | 0.036621 | 0.018311 | -0.13275 | -0.18768 | 0.17853 | 0.041198 | -121.6736 | 0.1236 | 0.14191 | 0.10071 | -121.7651 | 0.027466 | -0.027466 | -121.7102 | 0.15564 | -0.027466 | 0 | -121.7285 | 0.23346 | 0.14191 | 0.11902 | -121.8658 | 0.19684 | 0.17853 | 0.11902 | -121.9345
1935.0938 | 121.9711 | -0.1831 | 121.7651 | 0.11719 | 0.04506 | 0.061823 | 0.0012647 | 0.033601 | -0.0017496 | 0.033423 | 0.090332 | 0.032392 | 0.032396 | 0.045824 | 0.0016727 | 0.032486 | -0.013733 | -0.032043 | -0.036621 | -0.032043 | 0.091553 | 0.022888 | -0.11444 | -0.013733 | -0.041199 | -0.1831 | 0.013733 | 0.013733 | -0.11902 | -0.20142 | 0.20599 | 0.068664 | -121.6736 | 0.15106 | 0.15106 | 0.082398 | -121.7789 | 0.064086 | -0.018311 | -121.7514 | 0.16937 | 0 | 0.018311 | -121.7514 | 0.27466 | 0.16937 | 0.14648 | -121.8796 | 0.19684 | 0.19684 | 0.14191 | -121.9666
1936.7812 | 122.0261 | -0.16022 | 121.7651 | 0.11719 | 0.04506 | 0.061823 | -1.7146e-05 | 0.035523 | -0.0023904 | 0.03321 | 0.067444 | 0.031751 | 0.034746 | 0.044115 | 0.0020999 | 0.033554 | 0 | -0.036621 | -0.032043 | -0.018311 | 0.082397 | 0.022888 | -0.11902 | -0.009155 | -0.045776 | -0.1831 | 0.022888 | 0.013733 | -0.1236 | -0.17853 | 0.1831 | 0.041198 | -121.6827 | 0.1236 | 0.14191 | 0.10071 | -121.7651 | 0.036621 | -0.018311 | -121.7422 | 0.15106 | -0.022888 | -0.004577 | -121.7514 | 0.24261 | 0.16022 | 0.12817 | -121.8842 | 0.1831 | 0.17395 | 0.11444 | -121.9437
1938.5312 | 121.9482 | -0.19226 | 121.7789 | -0.24139 | 0.043778 | 0.063532 | 0.0059643 | 0.032105 | -0.0058084 | 0.032569 | -0.19958 | 0.03111 | 0.03325 | 0.043047 | -0.0011045 | 0.033981 | -0.004578 | 0.013733 | 0.018311 | 0 | 0.073242 | 0.018311 | -0.11444 | -0.027466 | 0.004578 | -0.16479 | 0.045776 | 0.027466 | -0.15564 | -0.18768 | 0.21057 | 0.07782 | -121.7056 | 0.20599 | 0.19226 | 0.11444 | -121.7834 | 0.036621 | 0.004578 | -121.7331 | 0.16479 | 0.027466 | 0.022888 | -121.7514 | 0.2655 | 0.18768 | 0.21057 | -121.8933 | 0.23804 | 0.21973 | 0.19684 | -121.9666
1940.2969 | 121.9894 | -0.17395 | 121.7606 | -0.14221 | 0.043991 | 0.058618 | 0.0057507 | 0.031251 | -0.0023904 | 0.032569 | -0.15381 | 0.032819 | 0.038591 | 0.046038 | -0.0011045 | 0.030777 | 0.036621 | 0.027466 | 0.022888 | 0.027466 | 0.064087 | 0.004578 | -0.10986 | -0.004578 | 0.032043 | -0.15564 | 0.013733 | 0.013733 | -0.14648 | -0.21057 | 0.17853 | 0.064087 | -121.6965 | 0.20142 | 0.20142 | 0.13733 | -121.7239 | 0.027466 | -0.036621 | -121.7468 | 0.16937 | 0.01831 | 0.054931 | -121.7468 | 0.23804 | 0.21057 | 0.19684 | -121.8704 | 0.18768 | 0.18768 | 0.20599 | -121.9711
1941.9844 | 121.9894 | -0.19226 | 121.7651 | -0.21088 | 0.044846 | 0.062677 | 0.0036145 | 0.032105 | -0.001536 | 0.032783 | -0.18433 | 0.031964 | 0.03795 | 0.044756 | -0.0017453 | 0.03099 | -0.018311 | 0 | -0.022888 | -0.004578 | 0.082397 | 0.013733 | -0.11902 | -0.036621 | -0.013733 | -0.17395 | 0.027466 | 0 | -0.13733 | -0.21973 | 0.20599 | 0.073242 | -121.6827 | 0.19226 | 0.18768 | 0.11444 | -121.7834 | 0.054932 | -0.027466 | -121.7377 | 0.15564 | 0.018311 | 0.045777 | -121.7651 | 0.27466 | 0.17395 | 0.16937 | -121.8842 | 0.21973 | 0.19226 | 0.17853 | -121.9849
1943.7344 | 122.0306 | -0.17853 | 121.7743 | 0.094299 | 0.043351 | 0.063104 | 0.0010511 | 0.032746 | -0.002604 | 0.033851 | 0.097962 | 0.029828 | 0.035814 | 0.045611 | 0.00060451 | 0.032058 | 0 | -0.022888 | -0.013733 | -0.009155 | 0.07782 | 0.018311 | -0.11444 | -0.013733 | -0.045776 | -0.1831 | 0.027466 | -0.004578 | -0.14191 | -0.20599 | 0.19684 | 0.064087 | -121.6965 | 0.15564 | 0.16937 | 0.10529 | -121.7743 | 0.036621 | -0.027466 | -121.7468 | 0.16479 | -0.004577 | 0.022889 | -121.7789 | 0.25635 | 0.17853 | 0.16479 | -121.8887 | 0.20599 | 0.17395 | 0.13275 | -121.9803
1945.4844 | 122.0581 | -0.16937 | 121.7697 | -0.0048827 | 0.038437 | 0.0646 | -0.00044435 | 0.036592 | -0.0092264 | 0.030219 | 0.097962 | 0.030683 | 0.030473 | 0.043047 | -0.0015317 | 0.033767 | 0.022888 | 0.059509 | 0.064087 | 0.013733 | 0.064087 | 0.027466 | -0.091553 | 0.018311 | 0.032043 | -0.09613 | -0.004578 | -0.027466 | -0.11444 | -0.1831 | 0.19684 | 0.07782 | -121.7056 | 0.22888 | 0.18311 | 0.10529 | -121.7468 | 0.054932 | -0.013732 | -121.7743 | 0.18768 | 0.073243 | 0.086975 | -121.7972 | 0.23346 | 0.19226 | 0.23346 | -121.8613 | 0.16479 | 0.14191 | 0.20142 | -121.9528
1947.2344 | 122.049 | -0.16479 | 121.7331 | 0.15533 | 0.04036 | 0.059473 | -0.0010851 | 0.03296 | -0.0038858 | 0.030646 | 0.14374 | 0.029401 | 0.034318 | 0.04497 | 0.0016727 | 0.032058 | 0.09613 | 0.10071 | 0.10986 | 0.059509 | 0.045776 | 0.059509 | -0.064087 | 0.09613 | 0.07782 | -0.073242 | -0.013733 | -0.045776 | -0.11444 | -0.16022 | 0.2243 | 0.10071 | -121.6873 | 0.2655 | 0.2243 | 0.1236 | -121.637 | 0.050354 | 0.004578 | -121.7468 | 0.26092 | 0.091553 | 0.086975 | -121.7789 | 0.21057 | 0.26092 | 0.27466 | -121.7972 | 0.15106 | 0.11902 | 0.24261 | -121.8933
1948.9844 | 121.9894 | -0.17395 | 121.7743 | -0.18799 | 0.043351 | 0.065454 | 0.0021191 | 0.03296 | -0.0023904 | 0.032142 | -0.19958 | 0.03111 | 0.034532 | 0.046892 | 0.0010317 | 0.031417 | 0.027466 | -0.022888 | -0.013733 | 0 | 0.091553 | 0.018311 | -0.11902 | -0.050354 | 0 | -0.16937 | 0.022888 | 0.013733 | -0.13275 | -0.18768 | 0.19226 | 0.054931 | -121.6827 | 0.15106 | 0.17395 | 0.11902 | -121.7468 | 0.041199 | -0.013733 | -121.7514 | 0.1236 | 0.004577 | 0.01831 | -121.7606 | 0.2655 | 0.20142 | 0.16022 | -121.8933 | 0.19684 | 0.18768 | 0.17395 | -121.962
1950.6875 | 122.0398 | -0.17395 | 121.7834 | 0.12482 | 0.043778 | 0.060968 | -0.0012987 | 0.031465 | -4.058e-05 | 0.032569 | 0.090332 | 0.033887 | 0.03261 | 0.048174 | 0.0014591 | 0.03099 | 0.013733 | -0.045776 | -0.032043 | -0.027466 | 0.086975 | 0.022888 | -0.11902 | -0.022888 | -0.054932 | -0.19684 | 0.032043 | 0.009155 | -0.1236 | -0.20599 | 0.19684 | 0.054931 | -121.6965 | 0.12817 | 0.14648 | 0.091553 | -121.7697 | 0.050354 | -0.032044 | -121.7514 | 0.15106 | -0.022888 | 0.009156 | -121.7743 | 0.26092 | 0.18768 | 0.14191 | -121.9025 | 0.20599 | 0.1831 | 0.11902 | -121.9894
1952.4375 | 122.0169 | -0.16937 | 121.7834 | -0.18799 | 0.040787 | 0.060968 | 0.0053235 | 0.033387 | -0.00944 | 0.030646 | -0.10803 | 0.027265 | 0.038377 | 0.042406 | -0.0032407 | 0.032699 | 0.07782 | 0.11902 | 0.13275 | 0.064087 | 0.041199 | 0.054932 | -0.07782 | 0.073242 | 0.12817 | -0.050354 | 0.004578 | -0.045776 | -0.10986 | -0.16479 | 0.22431 | 0.091553 | -121.7422 | 0.28839 | 0.23346 | 0.14191 | -121.7056 | 0.05951 | 0.004578 | -121.7789 | 0.24261 | 0.11902 | 0.11444 | -121.8292 | 0.21057 | 0.24719 | 0.30212 | -121.8613 | 0.17395 | 0.1236 | 0.29755 | -121.9482
1954.1875 | 122.0123 | -0.16022 | 121.8063 | -0.18799 | 0.043137 | 0.06225 | 0.0029737 | 0.03296 | 0.0016684 | 0.034064 | -0.1767 | 0.032605 | 0.036241 | 0.046252 | 0.00017731 | 0.029281 | 0.018311 | 0.004578 | 0.013733 | 0.004578 | 0.086975 | 0.022888 | -0.11902 | 0.009155 | 0.013733 | -0.15106 | 0.018311 | -0.004578 | -0.14648 | -0.19226 | 0.1831 | 0.041198 | -121.7194 | 0.16479 | 0.16479 | 0.1236 | -121.788 | 0.013733 | -0.032044 | -121.788 | 0.16937 | 0.009155 | 0.041199 | -121.8109 | 0.24719 | 0.17853 | 0.17395 | -121.9254 | 0.17853 | 0.15564 | 0.17395 | -121.9986
1955.8906 | 122.0947 | -0.15106 | 121.7743 | 0.079041 | 0.04506 | 0.060114 | 0.0027601 | 0.032533 | -0.001536 | 0.033423 | 0.052185 | 0.030042 | 0.038377 | 0.046892 | -3.629e-05 | 0.032913 | 0 | -0.018311 | -0.004578 | -0.027466 | 0.07782 | 0.027466 | -0.11444 | 0.004578 | -0.027466 | -0.16937 | 0.032043 | 0.004578 | -0.12817 | -0.1831 | 0.17853 | 0.036621 | -121.6965 | 0.13275 | 0.1236 | 0.086975 | -121.7743 | 0.022888 | -0.032043 | -121.7422 | 0.15564 | -0.018311 | 0.013732 | -121.7697 | 0.22888 | 0.15106 | 0.14648 | -121.8887 | 0.18311 | 0.15564 | 0.1236 | -121.9574
1957.6406 | 122.0673 | -0.13733 | 121.7651 | 0.13245 | 0.0457 | 0.058618 | 0.0027601 | 0.033814 | -0.0055948 | 0.03321 | 0.18188 | 0.028333 | 0.035173 | 0.044329 | 0.00017731 | 0.03334 | 0.068665 | 0.11444 | 0.10529 | 0.064087 | 0.036621 | 0.059509 | -0.073242 | 0.11444 | 0.091553 | -0.045776 | -0.027466 | -0.027466 | -0.086975 | -0.16022 | 0.19684 | 0.064087 | -121.7285 | 0.25177 | 0.20142 | 0.13733 | -121.6965 | 0.050354 | -0.022888 | -121.7926 | 0.25177 | 0.091553 | 0.11444 | -121.7926 | 0.17395 | 0.20599 | 0.24262 | -121.8384 | 0.10986 | 0.10986 | 0.22888 | -121.9254
1959.4062 | 121.9666 | -0.18768 | 121.7972 | 0.033264 | 0.046128 | 0.059686 | 0.0019055 | 0.031465 | -0.0011088 | 0.032569 | -0.0012209 | 0.031964 | 0.035814 | 0.045611 | 0.0029543 | 0.030563 | -0.004578 | -0.050354 | -0.022888 | -0.018311 | 0.091553 | 0.027466 | -0.1236 | -0.054932 | -0.050354 | -0.2243 | 0.027466 | 0.032043 | -0.14648 | -0.21973 | 0.21515 | 0.064087 | -121.7056 | 0.13733 | 0.16937 | 0.10528 | -121.8018 | 0.041199 | -0.032044 | -121.7697 | 0.13275 | -0.036621 | -0.004577 | -121.7651 | 0.27924 | 0.1831 | 0.16479 | -121.9208 | 0.21515 | 0.21973 | 0.13733 | -122.0169
1961.1875 | 121.9574 | -0.17853 | 121.8201 | -0.088806 | 0.046341 | 0.063104 | 0.00019645 | 0.03296 | -0.0011088 | 0.034705 | -0.092773 | 0.031751 | 0.036027 | 0.044115 | 0.0018863 | 0.029922 | 0.073242 | 0.059509 | 0.027466 | 0.022888 | 0.07782 | 0.027466 | -0.10986 | 0.022888 | 0.027466 | -0.16479 | 0.027466 | 0.009155 | -0.12817 | -0.19684 | 0.20599 | 0.068665 | -121.7422 | 0.23804 | 0.20142 | 0.13275 | -121.7468 | 0.050354 | -0.01831 | -121.7926 | 0.20142 | 0.013733 | 0.032043 | -121.8109 | 0.25635 | 0.25177 | 0.20599 | -121.9299 | 0.20599 | 0.18768 | 0.20599 | -122.0169
1962.875 | 121.9849 | -0.18768 | 121.8063 | 0.040894 | 0.043351 | 0.059686 | 0.0012647 | 0.033387 | -0.0036722 | 0.032996 | 0.075073 | 0.033032 | 0.037736 | 0.047747 | 0.0023135 | 0.032486 | -0.018311 | -0.064087 | -0.032043 | -0.018311 | 0.086975 | 0.027466 | -0.1236 | -0.036621 | -0.036621 | -0.21057 | 0.027466 | 0.022888 | -0.14191 | -0.19684 | 0.21515 | 0.064087 | -121.7194 | 0.1236 | 0.16937 | 0.10528 | -121.8246 | 0.045776 | -0.009155 | -121.7789 | 0.15106 | -0.022888 | -0.013733 | -121.7834 | 0.27466 | 0.16937 | 0.15564 | -121.9299 | 0.21515 | 0.21057 | 0.15106 | -122.0032
1964.625 | 122.0856 | -0.13275 | 121.8018 | 0.12482 | 0.044632 | 0.062036 | 0.00083745 | 0.031037 | -0.0064492 | 0.03321 | 0.20477 | 0.030896 | 0.038377 | 0.043688 | 0.00039091 | 0.031417 | 0.086975 | 0.11444 | 0.09613 | 0.073242 | 0.041199 | 0.073242 | -0.07782 | 0.09613 | 0.091553 | -0.054932 | -0.022888 | -0.032043 | -0.082397 | -0.14191 | 0.20599 | 0.054931 | -121.7606 | 0.24719 | 0.20599 | 0.15106 | -121.7148 | 0.050354 | -0.009156 | -121.8246 | 0.22888 | 0.077819 | 0.086975 | -121.8338 | 0.17395 | 0.21973 | 0.22888 | -121.8796 | 0.10986 | 0.10071 | 0.2243 | -121.9437
1966.375 | 121.9803 | -0.16937 | 121.8246 | 0.010376 | 0.044846 | 0.060541 | -0.00023075 | 0.032533 | -0.002604 | 0.033851 | 0.014038 | 0.031751 | 0.0356 | 0.045824 | 0.0029543 | 0.031631 | 0.004578 | -0.004578 | 0 | -0.018311 | 0.073242 | 0.036621 | -0.11444 | -0.045776 | -0.032043 | -0.20599 | 0.045776 | 0.013733 | -0.13733 | -0.19226 | 0.20599 | 0.054932 | -121.7514 | 0.16479 | 0.15106 | 0.09613 | -121.8201 | 0.032044 | -0.022888 | -121.7789 | 0.1236 | -0.036621 | -0.013733 | -121.8109 | 0.24261 | 0.17395 | 0.16937 | -121.9391 | 0.21515 | 0.18311 | 0.13733 | -122.0169
1968.0625 | 121.9666 | -0.15564 | 121.8338 | -0.020142 | 0.043778 | 0.063104 | 0.0038281 | 0.031465 | -0.0017496 | 0.034919 | -0.0012209 | 0.032178 | 0.041368 | 0.046465 | 0.0020999 | 0.030777 | 0.013733 | 0 | 0.013733 | 0.032043 | 0.07782 | 0.018311 | -0.11902 | -0.027466 | -0.032043 | -0.21973 | 0.036621 | 0.004578 | -0.13275 | -0.18768 | 0.17395 | 0.036621 | -121.756 | 0.15564 | 0.18768 | 0.15106 | -121.8201 | 0.022889 | -0.032043 | -121.7972 | 0.12817 | -0.064087 | -0.032044 | -121.8292 | 0.23346 | 0.16937 | 0.16937 | -121.9528 | 0.19226 | 0.16022 | 0.1236 | -122.0215
1969.8125 | 122.113 | -0.15106 | 121.7972 | -0.14221 | 0.04271 | 0.063959 | 0.0042555 | 0.034242 | -0.00944 | 0.031928 | -0.069885 | 0.028119 | 0.036455 | 0.043688 | -0.0045225 | 0.03099 | 0.082397 | 0.13275 | 0.1236 | 0.068665 | 0.050354 | 0.059509 | -0.073242 | 0.10071 | 0.13733 | -0.036621 | -0.009155 | -0.022888 | -0.10071 | -0.16479 | 0.21057 | 0.07782 | -121.7468 | 0.28381 | 0.21973 | 0.14191 | -121.7148 | 0.050354 | -0.013733 | -121.8063 | 0.25177 | 0.11444 | 0.12817 | -121.8201 | 0.20142 | 0.23346 | 0.27466 | -121.8704 | 0.14191 | 0.12817 | 0.28839 | -121.962
1971.5625 | 122.0993 | -0.14191 | 121.8063 | 0.16296 | 0.041001 | 0.062036 | -0.0012987 | 0.033601 | -0.0019632 | 0.033851 | 0.22766 | 0.030255 | 0.037523 | 0.044115 | 0.00017731 | 0.027359 | 0.064087 | 0.045776 | 0.068665 | 0.036621 | 0.041199 | 0.054932 | -0.10071 | 0.091553 | 0.073242 | -0.086975 | -0.013733 | -0.009155 | -0.10529 | -0.14191 | 0.19684 | 0.041199 | -121.7651 | 0.18768 | 0.17853 | 0.13733 | -121.7422 | 0.036621 | 0 | -121.8201 | 0.23346 | 0.054932 | 0.054932 | -121.8155 | 0.18311 | 0.20599 | 0.21057 | -121.907 | 0.12817 | 0.13275 | 0.21515 | -121.9482
1973.3125 | 122.0993 | -0.14648 | 121.8109 | -0.11169 | 0.042923 | 0.059045 | 0.0027601 | 0.035737 | -0.007731 | 0.03321 | -0.10803 | 0.028333 | 0.036241 | 0.042193 | -0.0034543 | 0.029922 | 0.09613 | 0.14191 | 0.14191 | 0.086975 | 0.050354 | 0.064087 | -0.073242 | 0.086975 | 0.13733 | -0.027466 | -0.022888 | -0.018311 | -0.10071 | -0.15106 | 0.21057 | 0.073242 | -121.7606 | 0.28839 | 0.23346 | 0.16022 | -121.7148 | 0.045776 | -0.004578 | -121.8338 | 0.23346 | 0.11902 | 0.1236 | -121.8292 | 0.19684 | 0.24261 | 0.28839 | -121.8842 | 0.1236 | 0.12817 | 0.28381 | -121.962
1975.0156 | 122.0352 | -0.1831 | 121.8109 | -0.19562 | 0.043351 | 0.062463 | 0.0031873 | 0.031465 | -0.00089518 | 0.031074 | -0.19196 | 0.029187 | 0.037309 | 0.046679 | 0.00039091 | 0.027786 | 0.013733 | -0.032043 | -0.027466 | -0.018311 | 0.091553 | 0.018311 | -0.1236 | -0.013733 | 0 | -0.17395 | 0.054932 | 0.013733 | -0.12817 | -0.20599 | 0.20142 | 0.059509 | -121.7194 | 0.15106 | 0.16479 | 0.10528 | -121.7972 | 0.054931 | -0.022889 | -121.756 | 0.16937 | 0.009155 | 0.032044 | -121.7972 | 0.27466 | 0.19684 | 0.15564 | -121.9345 | 0.23804 | 0.19684 | 0.1831 | -122.0169
1976.7656 | 121.9711 | -0.19226 | 121.8246 | -0.058289 | 0.045914 | 0.062463 | -0.0012987 | 0.033601 | 0.0029502 | 0.032355 | -0.046997 | 0.030683 | 0.036455 | 0.048174 | 0.0010317 | 0.027359 | 0.059509 | 0.018311 | 0.013733 | 0.009155 | 0.068665 | 0.032043 | -0.11444 | 0.004578 | -0.013733 | -0.20142 | 0.018311 | 0.018311 | -0.13275 | -0.19226 | 0.2243 | 0.07782 | -121.756 | 0.21057 | 0.20142 | 0.1236 | -121.7651 | 0.05951 | 0 | -121.8063 | 0.19684 | -0.009155 | -0.009155 | -121.8063 | 0.26093 | 0.25177 | 0.20599 | -121.9391 | 0.21057 | 0.21057 | 0.17853 | -122.0169
1978.5312 | 122.1222 | -0.14648 | 121.7834 | 0.094299 | 0.044419 | 0.060754 | 0.00062385 | 0.032319 | -0.0038858 | 0.032569 | 0.159 | 0.029828 | 0.036455 | 0.046038 | 0.0042361 | 0.027999 | 0.09613 | 0.082397 | 0.11444 | 0.068665 | 0.036621 | 0.068665 | -0.068665 | 0.10071 | 0.091553 | -0.07782 | -0.004578 | -0.022888 | -0.09613 | -0.14191 | 0.21515 | 0.077819 | -121.7468 | 0.22888 | 0.21515 | 0.13733 | -121.6873 | 0.050354 | 0.004577 | -121.788 | 0.24719 | 0.068664 | 0.064087 | -121.8063 | 0.18311 | 0.24261 | 0.26093 | -121.8521 | 0.14191 | 0.1236 | 0.23804 | -121.9254
1980.2812 | 122.0718 | -0.16937 | 121.8063 | 0.11719 | 0.041001 | 0.063745 | 0.0012647 | 0.034028 | -0.0070902 | 0.032783 | 0.15137 | 0.028119 | 0.038164 | 0.045824 | -0.0021725 | 0.027572 | 0.09613 | 0.10071 | 0.1236 | 0.045776 | 0.018311 | 0.050354 | -0.068665 | 0.10529 | 0.09613 | -0.07782 | -0.009155 | -0.013733 | -0.086975 | -0.14648 | 0.21973 | 0.10071 | -121.788 | 0.27008 | 0.21515 | 0.11444 | -121.7102 | 0.082398 | 0.022889 | -121.8155 | 0.27466 | 0.091553 | 0.068664 | -121.8201 | 0.18768 | 0.2655 | 0.29297 | -121.875 | 0.16022 | 0.15564 | 0.2655 | -121.9528
1981.9688 | 122.1359 | -0.14191 | 121.8018 | -0.020142 | 0.040573 | 0.063104 | 0.0023329 | 0.032746 | -0.006663 | 0.03086 | 0.0064086 | 0.028333 | 0.0356 | 0.044329 | -0.0032407 | 0.028213 | 0.032043 | 0.054932 | 0.064087 | 0.022888 | 0.050354 | 0.050354 | -0.091553 | 0.091553 | 0.091553 | -0.059509 | 0.018311 | 0.009155 | -0.10071 | -0.16022 | 0.19226 | 0.050354 | -121.7514 | 0.19684 | 0.16479 | 0.11444 | -121.7697 | 0.041199 | -0.01831 | -121.7834 | 0.23346 | 0.082398 | 0.10071 | -121.7926 | 0.19226 | 0.17395 | 0.20599 | -121.8933 | 0.16022 | 0.15106 | 0.23346 | -121.962
1983.7188 | 121.994 | -0.19684 | 121.8567 | -0.065918 | 0.046555 | 0.0599 | 0.0010511 | 0.034669 | 0.00060022 | 0.032355 | -0.092773 | 0.029828 | 0.038164 | 0.046038 | 0.0016727 | 0.025436 | 0.082397 | 0.022888 | 0.022888 | 0.013733 | 0.073242 | 0.022888 | -0.11902 | 0.022888 | 0.009155 | -0.1831 | 0.022888 | 0.004578 | -0.12817 | -0.16937 | 0.21973 | 0.077819 | -121.7834 | 0.21973 | 0.21057 | 0.13275 | -121.7743 | 0.068664 | 0.027465 | -121.8338 | 0.21973 | 0.013733 | -0.013732 | -121.8521 | 0.27008 | 0.27924 | 0.21973 | -121.9757 | 0.21973 | 0.20142 | 0.20599 | -122.0261
1985.4688 | 122.1497 | -0.13733 | 121.8063 | 0.063782 | 0.041428 | 0.061395 | 0.0029737 | 0.031678 | -0.002604 | 0.03321 | 0.12085 | 0.029828 | 0.039018 | 0.045611 | 0.00060451 | 0.027572 | 0.09613 | 0.086975 | 0.091553 | 0.054932 | 0.054932 | 0.050354 | -0.082397 | 0.10986 | 0.09613 | -0.054932 | -0.013733 | -0.022888 | -0.10071 | -0.16022 | 0.18768 | 0.054932 | -121.7514 | 0.2243 | 0.19226 | 0.13733 | -121.7102 | 0.036621 | -0.022888 | -121.8201 | 0.24719 | 0.082397 | 0.10528 | -121.8292 | 0.19226 | 0.23346 | 0.22888 | -121.8887 | 0.1236 | 0.11444 | 0.23346 | -121.9666
1987.2188 | 121.9849 | -0.17853 | 121.875 | -0.04303 | 0.0457 | 0.059045 | 0.00041005 | 0.033174 | 0.00038662 | 0.035346 | -0.062256 | 0.033032 | 0.033464 | 0.046252 | 0.0040225 | 0.028427 | 0.059509 | 0.013733 | 0.013733 | 0 | 0.07782 | 0.018311 | -0.1236 | 0.004578 | -0.013733 | -0.19226 | 0.004578 | 0.004578 | -0.11902 | -0.19684 | 0.19684 | 0.054932 | -121.7972 | 0.19226 | 0.17853 | 0.1236 | -121.8155 | 0.059509 | -0.01831 | -121.8704 | 0.18311 | -0.013733 | 0.004577 | -121.8704 | 0.25635 | 0.23804 | 0.19226 | -121.9986 | 0.18311 | 0.18311 | 0.16479 | -122.0718
1988.9062 | 122.0169 | -0.16022 | 121.843 | -0.073547 | 0.045914 | 0.060754 | 0.0036145 | 0.034242 | -0.00025418 | 0.036628 | -0.12329 | 0.03111 | 0.036455 | 0.046038 | 0.00017731 | 0.027359 | 0.059509 | 0.050354 | 0.041199 | 0.022888 | 0.091553 | 0.041199 | -0.11444 | 0.032043 | 0.045776 | -0.14648 | -0.013733 | 0.009155 | -0.11902 | -0.17395 | 0.20142 | 0.045776 | -121.7514 | 0.21057 | 0.1831 | 0.13733 | -121.7834 | 0.041198 | -0.013733 | -121.8567 | 0.19226 | 0.013733 | 0.027466 | -121.8338 | 0.25177 | 0.21973 | 0.20142 | -121.9574 | 0.14648 | 0.16937 | 0.20599 | -122.0169
1990.6562 | 122.0398 | -0.16022 | 121.8475 | 0.079041 | 0.044419 | 0.060327 | 0.0016919 | 0.031678 | -0.0013224 | 0.034278 | 0.10559 | 0.030896 | 0.035814 | 0.047106 | 0.0012455 | 0.027786 | -0.022888 | -0.036621 | -0.036621 | -0.022888 | 0.064087 | 0.018311 | -0.11444 | -0.009155 | -0.059509 | -0.18768 | 0.036621 | 0.013733 | -0.1236 | -0.19684 | 0.17853 | 0.045776 | -121.7834 | 0.1236 | 0.13733 | 0.091553 | -121.8704 | 0.036621 | -0.036621 | -121.8109 | 0.15106 | -0.027466 | 0.009155 | -121.8338 | 0.2243 | 0.13733 | 0.1236 | -121.962 | 0.19684 | 0.17395 | 0.10071 | -122.0444
1992.3906 | 122.1085 | -0.13733 | 121.8292 | 0.13245 | 0.043351 | 0.059259 | 0.0023329 | 0.034028 | -0.006022 | 0.032355 | 0.18951 | 0.030683 | 0.034532 | 0.045183 | -0.0013181 | 0.028213 | 0.07782 | 0.10986 | 0.1236 | 0.07782 | 0.045776 | 0.073242 | -0.086975 | 0.10071 | 0.09613 | -0.041199 | -0.018311 | -0.054932 | -0.091553 | -0.14191 | 0.21057 | 0.050354 | -121.7834 | 0.24719 | 0.21515 | 0.16479 | -121.7514 | 0.045776 | -0.004578 | -121.8475 | 0.23804 | 0.09613 | 0.10071 | -121.8842 | 0.18311 | 0.21515 | 0.26093 | -121.9162 | 0.11902 | 0.082397 | 0.23346 | -121.9711
1994.0781 | 122.0169 | -0.17853 | 121.8796 | 0.010376 | 0.045273 | 0.059686 | 0.00083745 | 0.032105 | -0.0013224 | 0.034492 | -0.0012209 | 0.031964 | 0.0356 | 0.046679 | 0.0010317 | 0.030563 | 0.022888 | -0.013733 | -0.022888 | -0.013733 | 0.068665 | 0.022888 | -0.11444 | -0.041199 | -0.059509 | -0.19684 | 0.018311 | 0.009155 | -0.13733 | -0.19684 | 0.20142 | 0.064087 | -121.8109 | 0.16479 | 0.16479 | 0.10071 | -121.8567 | 0.041199 | -0.01831 | -121.8613 | 0.13733 | -0.01831 | 0 | -121.8704 | 0.24719 | 0.20142 | 0.15564 | -121.994 | 0.19684 | 0.18768 | 0.11902 | -122.0764
1995.7812 | 122.1542 | -0.11902 | 121.8384 | -0.04303 | 0.040787 | 0.062036 | 0.0031873 | 0.031465 | -0.012003 | 0.032783 | 0.0064086 | 0.031751 | 0.032823 | 0.043261 | -0.0047361 | 0.034195 | 0.022888 | 0.073242 | 0.091553 | 0.036621 | 0.059509 | 0.050354 | -0.086975 | 0.054932 | 0.09613 | -0.041199 | -0.013733 | -0.054932 | -0.07782 | -0.16022 | 0.16937 | 0.032044 | -121.7789 | 0.19226 | 0.15564 | 0.1236 | -121.8155 | 0.041199 | -0.041198 | -121.8521 | 0.17395 | 0.07782 | 0.11902 | -121.8933 | 0.17853 | 0.14191 | 0.21057 | -121.9254 | 0.10529 | 0.064087 | 0.21515 | -121.9986
1997.5156 | 122.0215 | -0.17853 | 121.8887 | -0.1651 | 0.044846 | 0.061823 | 0.0083143 | 0.033387 | -0.0055948 | 0.032355 | -0.1767 | 0.031751 | 0.036027 | 0.044756 | -0.0011045 | 0.030349 | 0.059509 | 0.10986 | 0.11444 | 0.059509 | 0.045776 | 0.045776 | -0.086975 | 0.045776 | 0.10529 | -0.059509 | -0.013733 | -0.013733 | -0.086975 | -0.15564 | 0.2243 | 0.091553 | -121.843 | 0.28839 | 0.23804 | 0.14648 | -121.8292 | 0.091553 | 0.022888 | -121.9025 | 0.2243 | 0.11902 | 0.096131 | -121.9025 | 0.2243 | 0.23804 | 0.29297 | -121.9757 | 0.16479 | 0.16479 | 0.28381 | -122.0444
1999.2656 | 122.1405 | -0.1236 | 121.8475 | 0.079041 | 0.043778 | 0.0599 | 0.0029737 | 0.031037 | -0.00046778 | 0.031928 | 0.067444 | 0.032819 | 0.0356 | 0.047961 | 0.0012455 | 0.031845 | 0.004578 | -0.009155 | -0.027466 | 0 | 0.07782 | 0.018311 | -0.11902 | 0.013733 | -0.036621 | -0.16937 | 0.022888 | -0.018311 | -0.13275 | -0.17395 | 0.14191 | 0.004577 | -121.7697 | 0.11444 | 0.1236 | 0.11902 | -121.843 | -0.009155 | -0.050354 | -121.8246 | 0.13733 | -0.045777 | 0.004577 | -121.8658 | 0.20142 | 0.12817 | 0.09613 | -121.9666 | 0.14648 | 0.10528 | 0.086975 | -122.0215
2000.9688 | 122.1451 | -0.13733 | 121.8384 | 0.063782 | 0.046128 | 0.063959 | 0.0012647 | 0.032746 | -0.0011088 | 0.031287 | 0.11322 | 0.034955 | 0.032823 | 0.046038 | 0.0016727 | 0.031417 | 0 | 0.004578 | -0.004578 | -0.027466 | 0.082397 | 0.009155 | -0.11444 | 0.013733 | -0.027466 | -0.14191 | -0.018311 | -0.013733 | -0.10529 | -0.15564 | 0.14648 | 0.022888 | -121.756 | 0.14191 | 0.10986 | 0.086975 | -121.8384 | 0.032043 | -0.018311 | -121.8567 | 0.15106 | -0.004578 | 0.013733 | -121.8521 | 0.21973 | 0.13733 | 0.13275 | -121.9528 | 0.11902 | 0.1236 | 0.10986 | -121.994
2002.7188 | 122.1588 | -0.13275 | 121.8338 | 0.0027468 | 0.043137 | 0.062463 | 0.0059643 | 0.031892 | -0.0079446 | 0.030219 | 0.036926 | 0.028333 | 0.034959 | 0.04262 | -0.0068723 | 0.031845 | 0 | 0.054932 | 0.068665 | 0.022888 | 0.054932 | 0.050354 | -0.09613 | 0.059509 | 0.059509 | -0.059509 | -0.018311 | -0.045776 | -0.09613 | -0.15106 | 0.18311 | 0.036621 | -121.7789 | 0.18768 | 0.15564 | 0.11902 | -121.8338 | 0.036621 | -0.018311 | -121.8521 | 0.19226 | 0.073242 | 0.091553 | -121.8796 | 0.18768 | 0.13275 | 0.20142 | -121.9299 | 0.11444 | 0.086975 | 0.19226 | -121.9849
2004.4844 | 122.1497 | -0.11902 | 121.8292 | 0.14771 | 0.041642 | 0.061182 | -0.00087155 | 0.032319 | -0.0011088 | 0.032783 | 0.14374 | 0.034741 | 0.032823 | 0.044543 | 0.0014591 | 0.029068 | 0.045776 | 0.036621 | 0.050354 | 0.032043 | 0.07782 | 0.050354 | -0.091553 | 0.073242 | 0.041199 | -0.073242 | -0.022888 | -0.054932 | -0.10071 | -0.15106 | 0.16937 | 0.027466 | -121.7514 | 0.15564 | 0.15106 | 0.1236 | -121.7834 | 0.018311 | -0.032043 | -121.8521 | 0.19226 | 0.045777 | 0.07782 | -121.8842 | 0.19684 | 0.16479 | 0.16937 | -121.9208 | 0.096131 | 0.064087 | 0.16022 | -121.9803
2006.25 | 122.1634 | -0.09613 | 121.8475 | -0.096436 | 0.043564 | 0.064386 | 0.0078871 | 0.035096 | -0.0073038 | 0.030006 | -0.054626 | 0.033246 | 0.032823 | 0.042193 | -0.0023861 | 0.033126 | 0.07782 | 0.11444 | 0.11902 | 0.054932 | 0.027466 | 0.050354 | -0.086975 | 0.11902 | 0.11444 | 0.004578 | -0.018311 | -0.032043 | -0.064087 | -0.12817 | 0.14648 | 0.009155 | -121.8201 | 0.21057 | 0.15106 | 0.14191 | -121.7697 | 0.032043 | -0.032044 | -121.8658 | 0.21515 | 0.10071 | 0.13275 | -121.8796 | 0.1236 | 0.17395 | 0.21515 | -121.9345 | 0.077819 | 0.064087 | 0.21057 | -121.9757
2007.9531 | 122.0215 | -0.15564 | 121.8887 | -0.096436 | 0.047623 | 0.060968 | 0.0012647 | 0.034242 | 0.0023092 | 0.032996 | -0.12329 | 0.034741 | 0.03261 | 0.044756 | 0.0023135 | 0.028213 | 0.07782 | 0.054932 | 0.041199 | 0.018311 | 0.073242 | 0.018311 | -0.10986 | 0.045776 | 0.009155 | -0.11902 | 0 | -0.022888 | -0.09613 | -0.15106 | 0.17395 | 0.045777 | -121.8155 | 0.21057 | 0.17395 | 0.12817 | -121.8109 | 0.05951 | 0.004578 | -121.8887 | 0.20142 | 0.036621 | 0.032043 | -121.9116 | 0.22888 | 0.23346 | 0.19684 | -121.9986 | 0.15564 | 0.13275 | 0.16479 | -122.0398
2009.6875 | 122.1497 | -0.12817 | 121.8384 | -0.012512 | 0.036728 | -0.033881 | -0.00087155 | 0.032533 | -0.0081582 | 0.031928 | 0.0064086 | 0.033246 | 0.03026 | 0.043688 | -3.629e-05 | 0.035476 | 0.027466 | 0.073242 | 0.073242 | 0.022888 | 0.045776 | 0.041199 | -0.09613 | 0.073242 | 0.073242 | -0.036621 | -0.013733 | -0.036621 | -0.073242 | -0.13275 | 0.16937 | 0.032044 | -121.7926 | 0.20142 | 0.15106 | 0.11902 | -121.8109 | 0.054932 | -0.004577 | -121.8521 | 0.20142 | 0.091553 | 0.09613 | -121.875 | 0.17395 | 0.15564 | 0.20142 | -121.9345 | 0.11444 | 0.091553 | 0.20142 | -121.9711
2011.4531 | 122.1405 | -0.10529 | 121.8658 | -0.0048827 | 0.042496 | 0.061823 | 0.0051099 | 0.030824 | -0.006663 | 0.03086 | 0.036926 | 0.033032 | 0.031114 | 0.044115 | -0.0040951 | 0.03099 | 0.027466 | 0.027466 | 0.064087 | 0.022888 | 0.059509 | 0.054932 | -0.09613 | 0.059509 | 0.041199 | -0.059509 | -0.041199 | -0.045776 | -0.082397 | -0.1236 | 0.16022 | 0.009156 | -121.8063 | 0.13275 | 0.12817 | 0.11902 | -121.8384 | 0.022889 | -0.01831 | -121.907 | 0.16479 | 0.045777 | 0.064087 | -121.9116 | 0.16479 | 0.13275 | 0.16937 | -121.962 | 0.064087 | 0.05951 | 0.14649 | -121.9894
2013.1406 | 122.0535 | -0.13733 | 121.8842 | -0.18799 | 0.043778 | 0.062891 | 0.0038281 | 0.030397 | -0.0040994 | 0.029578 | -0.13855 | 0.032178 | 0.030687 | 0.04497 | -0.0023861 | 0.030777 | 0.082397 | 0.11902 | 0.11902 | 0.054932 | 0.036621 | 0.050354 | -0.07782 | 0.086975 | 0.11902 | -0.045776 | -0.018311 | -0.032043 | -0.10071 | -0.14191 | 0.18768 | 0.059509 | -121.8475 | 0.25635 | 0.19226 | 0.13275 | -121.8018 | 0.036621 | -0.004578 | -121.9025 | 0.2243 | 0.091553 | 0.096131 | -121.9162 | 0.17395 | 0.21973 | 0.25635 | -121.962 | 0.11902 | 0.10529 | 0.25635 | -122.0261
2014.8906 | 122.049 | -0.14648 | 121.9208 | -0.1651 | 0.044419 | 0.060327 | 0.0059643 | 0.034883 | -0.003245 | 0.032996 | -0.19196 | 0.034101 | 0.035387 | 0.043902 | -0.0019589 | 0.029708 | 0.091553 | 0.10529 | 0.10071 | 0.068665 | 0.054932 | 0.054932 | -0.082397 | 0.059509 | 0.10529 | -0.068665 | -0.027466 | -0.027466 | -0.07782 | -0.14648 | 0.20142 | 0.064087 | -121.8658 | 0.25177 | 0.21515 | 0.15106 | -121.8292 | 0.068664 | 0 | -121.9482 | 0.20599 | 0.077819 | 0.077819 | -121.9482 | 0.20142 | 0.23804 | 0.24719 | -122.0032 | 0.11902 | 0.11902 | 0.25177 | -122.0673
2016.6406 | 122.1222 | -0.11902 | 121.8704 | 0.048523 | 0.042069 | 0.063532 | 0.00083745 | 0.031465 | -0.0051676 | 0.031714 | 0.036926 | 0.034741 | 0.030473 | 0.044115 | -0.00089089 | 0.029922 | 0.054932 | 0.064087 | 0.07782 | 0.018311 | 0.036621 | 0.054932 | -0.07782 | 0.059509 | 0.041199 | -0.068665 | -0.036621 | -0.054932 | -0.073242 | -0.1236 | 0.17395 | 0.041199 | -121.8338 | 0.18311 | 0.13733 | 0.096131 | -121.8155 | 0.045777 | -0.004577 | -121.907 | 0.17853 | 0.050354 | 0.054931 | -121.9254 | 0.15564 | 0.17395 | 0.19684 | -121.9482 | 0.082398 | 0.064087 | 0.16022 | -121.994
2018.3906 | 122.0947 | -0.14648 | 121.8933 | -0.18036 | 0.044632 | 0.059686 | 0.0016919 | 0.035951 | -0.00046778 | 0.034492 | -0.26062 | 0.035596 | 0.031541 | 0.04732 | 0.0010317 | 0.02864 | 0.027466 | -0.009155 | -0.022888 | 0 | 0.07782 | 0 | -0.1236 | 0.004578 | 0 | -0.14191 | 0.009155 | -0.004578 | -0.09613 | -0.14648 | 0.14648 | 0.022888 | -121.8155 | 0.13733 | 0.14648 | 0.1236 | -121.8658 | 0.050354 | 0 | -121.8842 | 0.15106 | 0.004577 | 0.004577 | -121.8979 | 0.2243 | 0.17395 | 0.1236 | -122.0169 | 0.15564 | 0.14191 | 0.14648 | -122.0398
2020.0781 | 122.1405 | -0.13733 | 121.8887 | 0.10956 | 0.046128 | 0.06225 | 0.00041005 | 0.031251 | 0.00081382 | 0.034919 | 0.036926 | 0.036237 | 0.030687 | 0.046679 | 0.0029543 | 0.027572 | 0.018311 | -0.018311 | -0.027466 | -0.013733 | 0.086975 | 0.009155 | -0.1236 | 0.022888 | -0.041199 | -0.14648 | 0.027466 | -0.018311 | -0.086975 | -0.15564 | 0.14648 | 0.013733 | -121.8018 | 0.11902 | 0.1236 | 0.10986 | -121.8704 | 0.050354 | -0.018311 | -121.8613 | 0.16022 | -0.009155 | 0.009156 | -121.907 | 0.2243 | 0.15564 | 0.10986 | -122.0123 | 0.16479 | 0.11902 | 0.09613 | -122.0444
2021.8281 | 122.1497 | -0.086975 | 121.8704 | 0.079041 | 0.043351 | 0.063532 | -0.0017261 | 0.031892 | 0.00038662 | 0.03321 | 0.059815 | 0.036664 | 0.029832 | 0.047961 | 0.0035953 | 0.030136 | 0.036621 | -0.018311 | -0.022888 | -0.013733 | 0.082397 | 0.018311 | -0.10986 | 0.013733 | -0.027466 | -0.14648 | -0.013733 | -0.009155 | -0.091553 | -0.15564 | 0.10529 | -0.022888 | -121.788 | 0.068664 | 0.073242 | 0.09613 | -121.8338 | -0.004578 | -0.068665 | -121.8842 | 0.10071 | -0.059509 | 0.009156 | -121.8796 | 0.16937 | 0.1236 | 0.064087 | -121.9803 | 0.073242 | 0.07782 | 0.059509 | -122.0261
2023.5781 | 122.0993 | -0.14191 | 121.9391 | -0.19562 | 0.045487 | 0.062036 | 0.0051099 | 0.032746 | -0.0011088 | 0.033851 | -0.16144 | 0.035169 | 0.033037 | 0.046252 | 0.00060451 | 0.029922 | 0.045776 | 0 | 0.018311 | 0.022888 | 0.082397 | 0.032043 | -0.1236 | 0.022888 | 0.036621 | -0.10529 | 0.004578 | -0.009155 | -0.091553 | -0.15564 | 0.17395 | 0.018311 | -121.8567 | 0.14191 | 0.16479 | 0.14648 | -121.8933 | 0.050354 | -0.013733 | -121.9345 | 0.16479 | 0.036621 | 0.050354 | -121.9482 | 0.2243 | 0.18768 | 0.16022 | -122.0627 | 0.14649 | 0.13275 | 0.17853 | -122.0947
2025.3281 | 122.1313 | -0.10986 | 121.8933 | -0.1651 | 0.044632 | 0.060968 | 0.0066053 | 0.034455 | -0.0070902 | 0.032569 | -0.12329 | 0.034955 | 0.033678 | 0.046679 | -0.0047361 | 0.029281 | 0.068665 | 0.13733 | 0.13733 | 0.068665 | 0.045776 | 0.036621 | -0.086975 | 0.091553 | 0.13275 | 0.004578 | -0.022888 | -0.036621 | -0.059509 | -0.11902 | 0.14648 | 0.022888 | -121.8475 | 0.24719 | 0.17853 | 0.15564 | -121.8246 | 0.050354 | -0.009156 | -121.9162 | 0.20142 | 0.11444 | 0.1236 | -121.9299 | 0.15564 | 0.17853 | 0.24719 | -121.9803 | 0.086975 | 0.073242 | 0.24261 | -122.0123
2027.0938 | 122.081 | -0.14648 | 121.9345 | -0.12695 | 0.046555 | 0.061182 | 0.0053235 | 0.03296 | -0.0011088 | 0.035346 | -0.11566 | 0.038159 | 0.032396 | 0.048388 | 0.00060451 | 0.025436 | 0.059509 | 0.036621 | 0.022888 | 0.032043 | 0.07782 | 0.027466 | -0.11444 | 0.045776 | 0.036621 | -0.10071 | 0.004578 | -0.013733 | -0.091553 | -0.14191 | 0.17395 | 0.032043 | -121.8567 | 0.18311 | 0.17853 | 0.14648 | -121.875 | 0.054931 | 0.004577 | -121.9299 | 0.19226 | 0.045776 | 0.041199 | -121.9482 | 0.2243 | 0.20599 | 0.16937 | -122.049 | 0.15106 | 0.13275 | 0.18311 | -122.0764
2028.7812 | 122.049 | -0.15106 | 121.9437 | -0.21088 | 0.044419 | 0.060541 | 0.0068189 | 0.033601 | -0.004954 | 0.03086 | -0.20721 | 0.033673 | 0.034318 | 0.046465 | -0.0013181 | 0.02864 | 0.054932 | 0.10529 | 0.086975 | 0.054932 | 0.050354 | 0.059509 | -0.10986 | 0.036621 | 0.059509 | -0.073242 | -0.004578 | -0.013733 | -0.091553 | -0.13275 | 0.21057 | 0.041199 | -121.8933 | 0.25635 | 0.20599 | 0.16479 | -121.8887 | 0.059509 | 0.018311 | -121.9482 | 0.18768 | 0.07782 | 0.059509 | -121.9574 | 0.20142 | 0.20599 | 0.23804 | -122.0535 | 0.14648 | 0.13733 | 0.21057 | -122.0764
2030.5312 | 122.1771 | -0.10986 | 121.9025 | 0.071411 | 0.04506 | 0.059259 | -0.0032213 | 0.030397 | 0.00038662 | 0.033851 | 0.052185 | 0.037519 | 0.030901 | 0.048815 | 0.0029543 | 0.028427 | 0.009155 | -0.013733 | -0.022888 | -0.018311 | 0.086975 | 0.036621 | -0.10071 | 0.018311 | -0.018311 | -0.13275 | 0.009155 | 0 | -0.091553 | -0.15564 | 0.14648 | 0.009155 | -121.8155 | 0.09613 | 0.091552 | 0.082397 | -121.8933 | 0.01831 | -0.045777 | -121.8933 | 0.12817 | -0.022888 | 0.022889 | -121.9025 | 0.19684 | 0.11902 | 0.086975 | -122.0032 | 0.11902 | 0.10986 | 0.091552 | -122.0581
2032.2812 | 122.0901 | -0.14648 | 121.9025 | -0.17273 | 0.043991 | 0.062891 | 0.0027601 | 0.031678 | -0.0013224 | 0.031714 | -0.1767 | 0.03645 | 0.031541 | 0.047533 | 0.00060451 | 0.030349 | 0.009155 | -0.009155 | -0.022888 | 0 | 0.082397 | 0.013733 | -0.12817 | -0.027466 | 0.018311 | -0.13733 | 0.022888 | -0.013733 | -0.091553 | -0.16479 | 0.16022 | 0.01831 | -121.8201 | 0.13733 | 0.14648 | 0.12817 | -121.8933 | 0.054931 | -0.018311 | -121.8796 | 0.11902 | 0.009155 | 0.027466 | -121.9162 | 0.22888 | 0.15564 | 0.1236 | -122.0306 | 0.16937 | 0.13275 | 0.16479 | -122.0673
2033.9844 | 122.1176 | -0.11902 | 121.9162 | -0.18036 | 0.044419 | 0.060114 | 0.0027601 | 0.033174 | -0.002604 | 0.034064 | -0.23773 | 0.031751 | 0.030687 | 0.046679 | -0.0011045 | 0.03099 | -0.004578 | -0.009155 | -0.009155 | 0.004578 | 0.059509 | 0.004578 | -0.10986 | 0 | 0.018311 | -0.11902 | 0.009155 | 0.013733 | -0.10071 | -0.16022 | 0.1236 | 0.009156 | -121.8567 | 0.10986 | 0.1236 | 0.11444 | -121.9208 | 0.018311 | -0.041198 | -121.907 | 0.11902 | 0 | 0.041198 | -121.9025 | 0.17853 | 0.11444 | 0.10986 | -122.0261 | 0.12817 | 0.13275 | 0.13733 | -122.0764
2035.75 | 122.0581 | -0.16022 | 121.9299 | -0.23376 | 0.039933 | 0.063532 | 0.0029737 | 0.037232 | -0.004954 | 0.032142 | -0.16907 | 0.034741 | 0.030473 | 0.046038 | -0.0015317 | 0.029281 | 0.045776 | 0.073242 | 0.059509 | 0.036621 | 0.059509 | 0.045776 | -0.10071 | 0.018311 | 0.054932 | -0.086975 | -0.004578 | -0.018311 | -0.09613 | -0.15564 | 0.20599 | 0.059509 | -121.8704 | 0.23346 | 0.19684 | 0.13733 | -121.8842 | 0.064087 | 0.004577 | -121.9345 | 0.17853 | 0.073242 | 0.068665 | -121.9482 | 0.21973 | 0.20599 | 0.21973 | -122.0306 | 0.15564 | 0.14191 | 0.21515 | -122.0856
2037.5 | 122.1222 | -0.12817 | 121.907 | 0.08667 | 0.039933 | 0.060754 | 0.0016919 | 0.032533 | -0.006663 | 0.031287 | 0.15137 | 0.032392 | 0.031114 | 0.047533 | -0.0015317 | 0.030563 | 0.082397 | 0.09613 | 0.11444 | 0.036621 | 0.045776 | 0.050354 | -0.064087 | 0.07782 | 0.073242 | -0.027466 | -0.009155 | -0.032043 | -0.073242 | -0.11444 | 0.17853 | 0.064087 | -121.8613 | 0.2243 | 0.1648 | 0.10071 | -121.8246 | 0.054932 | 0.013733 | -121.9162 | 0.20599 | 0.10071 | 0.086975 | -121.9391 | 0.17395 | 0.21057 | 0.24262 | -121.9711 | 0.11902 | 0.096131 | 0.20142 | -122.0215
2039.25 | 122.0306 | -0.15564 | 121.9437 | -0.0048827 | 0.046128 | 0.0599 | -0.00065795 | 0.031465 | 0.0010276 | 0.033851 | 0.021668 | 0.037305 | 0.030473 | 0.046465 | 0.0042361 | 0.028427 | 0.064087 | -0.004578 | -0.004578 | -0.009155 | 0.086975 | 0.027466 | -0.11444 | -0.018311 | -0.032043 | -0.16022 | 0.027466 | -0.004578 | -0.073242 | -0.15106 | 0.18311 | 0.041199 | -121.8567 | 0.15106 | 0.14649 | 0.10529 | -121.8796 | 0.082398 | 0.004578 | -121.9162 | 0.13733 | -0.004577 | -0.009155 | -121.9482 | 0.24261 | 0.21973 | 0.15106 | -122.0581 | 0.18311 | 0.15106 | 0.1236 | -122.0947
2040.9531 | 122.1863 | -0.11444 | 121.9254 | -0.096436 | 0.040573 | 0.060114 | 0.0051099 | 0.033174 | -0.008372 | 0.031287 | -0.069885 | 0.031323 | 0.032182 | 0.047961 | -0.0036679 | 0.029495 | 0.09613 | 0.1236 | 0.12817 | 0.068665 | 0.050354 | 0.050354 | -0.091553 | 0.1236 | 0.13275 | 0.018311 | -0.027466 | -0.032043 | -0.054932 | -0.10986 | 0.16479 | 0.022888 | -121.875 | 0.23804 | 0.18311 | 0.16022 | -121.8292 | 0.059509 | 0.004578 | -121.9528 | 0.23804 | 0.13275 | 0.12817 | -121.9574 | 0.16479 | 0.21057 | 0.24262 | -122.0169 | 0.086975 | 0.082398 | 0.24719 | -122.0352
2042.6875 | 122.0398 | -0.14648 | 121.9437 | -0.0354 | 0.043564 | 0.061823 | 0.0016919 | 0.035737 | 0.0031638 | 0.032996 | -0.085144 | 0.034741 | 0.030046 | 0.047961 | 0.0033817 | 0.026077 | 0.050354 | -0.009155 | -0.004578 | -0.004578 | 0.07782 | 0.032043 | -0.10529 | -0.027466 | -0.036621 | -0.16479 | 0.027466 | 0.004578 | -0.09613 | -0.16022 | 0.17853 | 0.041198 | -121.8658 | 0.13733 | 0.14191 | 0.10071 | -121.8933 | 0.050354 | -0.013733 | -121.9162 | 0.11902 | -0.018311 | -0.004578 | -121.9391 | 0.2243 | 0.19684 | 0.14191 | -122.049 | 0.17395 | 0.15106 | 0.10986 | -122.1039
2044.4375 | 122.1039 | -0.1236 | 121.9574 | -0.17273 | 0.046555 | 0.063745 | 0.0036145 | 0.03296 | 0.00081382 | 0.035346 | -0.23773 | 0.033246 | 0.03261 | 0.047533 | 0.00039091 | 0.027572 | 0.018311 | -0.009155 | -0.022888 | 0 | 0.091553 | 0.013733 | -0.14191 | 0 | 0.032043 | -0.10986 | 0.013733 | -0.013733 | -0.10529 | -0.14191 | 0.13733 | -0.018311 | -121.8658 | 0.11444 | 0.1236 | 0.14191 | -121.9391 | 0.01831 | -0.018311 | -121.9437 | 0.1236 | 0.013733 | 0.032044 | -121.9711 | 0.21515 | 0.14191 | 0.10071 | -122.0993 | 0.13733 | 0.10986 | 0.15564 | -122.0993
2046.1406 | 122.1542 | -0.1236 | 121.9299 | 0.079041 | 0.043137 | 0.06225 | 0.0034009 | 0.032105 | -0.0045266 | 0.032142 | 0.159 | 0.03346 | 0.034532 | 0.047747 | -0.00046349 | 0.030349 | 0.086975 | 0.10529 | 0.12817 | 0.050354 | 0.036621 | 0.059509 | -0.073242 | 0.09613 | 0.086975 | -0.018311 | -0.027466 | -0.022888 | -0.059509 | -0.1236 | 0.1831 | 0.050354 | -121.8933 | 0.22888 | 0.17395 | 0.1236 | -121.843 | 0.064087 | 0 | -121.9574 | 0.21973 | 0.10528 | 0.10528 | -121.9528 | 0.16022 | 0.21057 | 0.25177 | -122.0032 | 0.09613 | 0.10071 | 0.21057 | -122.0535
2047.8906 | 122.1497 | -0.11444 | 121.9299 | 0.15533 | 0.041855 | 0.060327 | 0.0019055 | 0.034455 | -0.0047404 | 0.032996 | 0.16663 | 0.034314 | 0.031541 | 0.04732 | -0.00089089 | 0.029708 | 0.10071 | 0.10986 | 0.11444 | 0.059509 | 0.041199 | 0.073242 | -0.091553 | 0.10986 | 0.091553 | -0.009155 | -0.050354 | -0.050354 | -0.064087 | -0.10986 | 0.18768 | 0.022888 | -121.8887 | 0.2243 | 0.17395 | 0.15106 | -121.8292 | 0.050354 | 0.004578 | -121.9803 | 0.2243 | 0.10529 | 0.10071 | -121.9803 | 0.15564 | 0.21515 | 0.22888 | -122.0215 | 0.064087 | 0.064087 | 0.20599 | -122.0398
2049.6406 | 122.1313 | -0.11444 | 121.9208 | 0.08667 | 0.042069 | 0.060968 | 0.0027601 | 0.030824 | -0.0053812 | 0.029792 | 0.097962 | 0.032392 | 0.031969 | 0.045183 | -0.0013181 | 0.027145 | 0.059509 | 0.091553 | 0.10071 | 0.032043 | 0.036621 | 0.073242 | -0.086975 | 0.07782 | 0.036621 | -0.054932 | -0.013733 | -0.036621 | -0.059509 | -0.11902 | 0.18768 | 0.027466 | -121.8842 | 0.20599 | 0.14648 | 0.11902 | -121.8613 | 0.054932 | -0.004578 | -121.9345 | 0.19226 | 0.059509 | 0.064087 | -121.9574 | 0.15106 | 0.17395 | 0.21515 | -122.0078 | 0.10071 | 0.07782 | 0.15106 | -122.0398
2051.3906 | 122.1451 | -0.10529 | 121.9345 | 0.056152 | 0.041428 | 0.06225 | 0.0023329 | 0.034242 | -0.004954 | 0.032996 | 0.090332 | 0.035382 | 0.030687 | 0.047533 | -0.00046349 | 0.026718 | 0.073242 | 0.073242 | 0.07782 | 0.022888 | 0.036621 | 0.041199 | -0.082397 | 0.059509 | 0.032043 | -0.050354 | -0.022888 | -0.022888 | -0.059509 | -0.1236 | 0.14649 | 0.022889 | -121.8979 | 0.17853 | 0.12817 | 0.10528 | -121.8613 | 0.045777 | -0.01831 | -121.9574 | 0.16479 | 0.054932 | 0.073242 | -121.9574 | 0.14191 | 0.17853 | 0.18311 | -122.0169 | 0.082398 | 0.082398 | 0.13733 | -122.0581
2053.1406 | 122.0627 | -0.14191 | 121.9345 | 0.056152 | 0.045487 | 0.062036 | 0.0034009 | 0.032533 | 0.0023092 | 0.034064 | -0.039368 | 0.036023 | 0.029192 | 0.047747 | 0.0048769 | 0.025863 | 0.032043 | -0.036621 | -0.013733 | -0.022888 | 0.073242 | 0.027466 | -0.11444 | -0.018311 | -0.064087 | -0.17853 | 0.027466 | 0.013733 | -0.086975 | -0.15564 | 0.16937 | 0.027466 | -121.8613 | 0.10529 | 0.11902 | 0.091553 | -121.9025 | 0.054932 | -0.013733 | -121.907 | 0.1236 | -0.036621 | -0.022888 | -121.9208 | 0.21515 | 0.17395 | 0.12817 | -122.049 | 0.16937 | 0.15564 | 0.07782 | -122.0901
2054.8281 | 122.2 | -0.082397 | 121.9116 | 0.14008 | 0.043778 | 0.060114 | 0.0016919 | 0.030397 | -0.0013224 | 0.033423 | 0.32684 | 0.03581 | 0.032182 | 0.047106 | 0.0014591 | 0.027145 | 0.082397 | 0.045776 | 0.054932 | 0.036621 | 0.050354 | 0.041199 | -0.091553 | 0.10071 | 0.068665 | -0.027466 | -0.027466 | -0.027466 | -0.054932 | -0.10986 | 0.1236 | -0.009156 | -121.8613 | 0.12817 | 0.11902 | 0.12817 | -121.8292 | 0.027465 | -0.027466 | -121.9391 | 0.18311 | 0.054931 | 0.082397 | -121.9391 | 0.13275 | 0.16479 | 0.13733 | -122.0032 | 0.054931 | 0.054931 | 0.15106 | -122.0215
2056.5781 | 122.0993 | -0.12817 | 121.9482 | -0.1651 | 0.043778 | 0.062036 | 0.0036145 | 0.032105 | -0.0053812 | 0.031714 | -0.12329 | 0.034528 | 0.033678 | 0.049029 | -0.0017453 | 0.027999 | 0.086975 | 0.11444 | 0.11444 | 0.073242 | 0.032043 | 0.045776 | -0.07782 | 0.07782 | 0.10986 | -0.022888 | -0.027466 | -0.036621 | -0.059509 | -0.12817 | 0.17395 | 0.050354 | -121.9162 | 0.24262 | 0.20142 | 0.15106 | -121.8613 | 0.068665 | 0 | -121.9757 | 0.20599 | 0.10529 | 0.10529 | -121.9849 | 0.16022 | 0.21515 | 0.24262 | -122.0261 | 0.10071 | 0.091553 | 0.23804 | -122.0764
2058.3281 | 122.168 | -0.10986 | 121.9391 | 0.018005 | 0.040573 | 0.060968 | -0.00044435 | 0.031251 | -0.007731 | 0.031287 | 0.052185 | 0.034314 | 0.029405 | 0.047747 | -0.0028135 | 0.027786 | 0.054932 | 0.059509 | 0.059509 | 0.027466 | 0.050354 | 0.041199 | -0.091553 | 0.059509 | 0.032043 | -0.054932 | -0.013733 | -0.022888 | -0.064087 | -0.10986 | 0.15106 | 0.01831 | -121.8887 | 0.16937 | 0.13733 | 0.11902 | -121.8842 | 0.045776 | 0 | -121.9528 | 0.16937 | 0.054931 | 0.054931 | -121.962 | 0.16022 | 0.16479 | 0.16937 | -122.0306 | 0.09613 | 0.086975 | 0.14191 | -122.049
2060.0781 | 122.1771 | -0.1236 | 121.9391 | -0.19562 | 0.043564 | 0.064386 | 0.0038281 | 0.031251 | -0.0034586 | 0.032142 | -0.16907 | 0.033673 | 0.032182 | 0.048815 | -0.00067729 | 0.027572 | 0.11444 | 0.1236 | 0.13275 | 0.059509 | 0.045776 | 0.068665 | -0.10071 | 0.10071 | 0.13733 | 0 | -0.013733 | -0.041199 | -0.064087 | -0.10071 | 0.19226 | 0.022888 | -121.8933 | 0.24719 | 0.1831 | 0.16022 | -121.8246 | 0.059509 | 0.022888 | -121.9528 | 0.2243 | 0.1236 | 0.10071 | -121.9803 | 0.16937 | 0.23804 | 0.25635 | -122.0398 | 0.10986 | 0.082397 | 0.26093 | -122.0398
2061.7656 | 122.0993 | -0.13733 | 121.9711 | -0.11932 | 0.046128 | 0.060541 | 0.0072461 | 0.030397 | 0.00060022 | 0.031928 | -0.16907 | 0.034101 | 0.033037 | 0.049883 | 0.0014591 | 0.024795 | 0.082397 | 0.041199 | 0.022888 | 0.022888 | 0.082397 | 0.013733 | -0.13733 | 0.054932 | 0.032043 | -0.10529 | 0 | 0 | -0.068665 | -0.12817 | 0.15106 | 0 | -121.8887 | 0.17853 | 0.16022 | 0.16022 | -121.8887 | 0.068664 | 0.009155 | -121.9711 | 0.19226 | 0.032043 | 0.022888 | -121.9711 | 0.21973 | 0.21973 | 0.16022 | -122.1085 | 0.13733 | 0.13733 | 0.16937 | -122.0993
2063.5156 | 122.081 | -0.13733 | 121.9757 | -0.081177 | 0.04805 | 0.061609 | 0.0038281 | 0.032105 | 0.001882 | 0.034064 | -0.10803 | 0.037305 | 0.034318 | 0.049669 | 0.0025271 | 0.025863 | 0.086975 | 0.050354 | 0.032043 | 0.018311 | 0.07782 | 0.013733 | -0.11902 | 0.054932 | 0.032043 | -0.09613 | 0.009155 | -0.009155 | -0.082397 | -0.16022 | 0.15106 | 0.01831 | -121.8979 | 0.18768 | 0.15564 | 0.13733 | -121.8887 | 0.054932 | -0.022888 | -121.9666 | 0.19226 | 0.041199 | 0.064087 | -121.9849 | 0.21515 | 0.2243 | 0.16937 | -122.0947 | 0.14648 | 0.12817 | 0.16937 | -122.1359
2065.2656 | 122.2 | -0.082397 | 121.9437 | 0.079041 | 0.043137 | 0.060114 | -0.00023075 | 0.034028 | -0.0013224 | 0.035132 | 0.090332 | 0.036237 | 0.030687 | 0.050524 | 0.0012455 | 0.030777 | 0.004578 | -0.018311 | -0.013733 | -0.018311 | 0.073242 | 0.036621 | -0.10986 | 0.032043 | -0.004578 | -0.1236 | 0.004578 | -0.013733 | -0.064087 | -0.1236 | 0.11902 | -0.027466 | -121.8704 | 0.064086 | 0.064086 | 0.091552 | -121.9391 | 0.01831 | -0.041199 | -121.9391 | 0.11444 | -0.041199 | 0 | -121.9574 | 0.15564 | 0.086975 | 0.068664 | -122.0535 | 0.086975 | 0.068664 | 0.077819 | -122.0673
2066.9531 | 122.1634 | -0.10071 | 121.9437 | 0.079041 | 0.039719 | 0.062463 | 0.0014783 | 0.034028 | -0.006663 | 0.034919 | 0.17426 | 0.034101 | 0.029832 | 0.044756 | -3.629e-05 | 0.03099 | 0.07782 | 0.1236 | 0.10529 | 0.054932 | 0.041199 | 0.045776 | -0.082397 | 0.10071 | 0.07782 | -0.027466 | -0.022888 | -0.027466 | -0.050354 | -0.11902 | 0.14648 | 0.018311 | -121.9025 | 0.2243 | 0.15564 | 0.13733 | -121.8658 | 0.050354 | -0.018311 | -121.9666 | 0.20142 | 0.073242 | 0.091553 | -121.9711 | 0.14191 | 0.17853 | 0.20599 | -122.0261 | 0.07782 | 0.073242 | 0.17853 | -122.0627
2068.7031 | 122.1313 | -0.11902 | 121.9391 | 0.10956 | 0.042923 | 0.062036 | 0.0010511 | 0.032319 | -0.0011088 | 0.035132 | 0.097962 | 0.035169 | 0.032182 | 0.049029 | 0.0020999 | 0.02864 | 0.018311 | -0.036621 | -0.041199 | -0.027466 | 0.086975 | 0.018311 | -0.11444 | 0 | -0.045776 | -0.14648 | 0.022888 | 0.018311 | -0.091553 | -0.15564 | 0.13733 | 0.004578 | -121.8521 | 0.082398 | 0.091553 | 0.086975 | -121.9208 | 0.027466 | -0.036621 | -121.9162 | 0.11902 | -0.027465 | 0.009156 | -121.9208 | 0.20599 | 0.13733 | 0.07782 | -122.0535 | 0.14191 | 0.13733 | 0.073243 | -122.0947
2070.3906 | 122.1176 | -0.13275 | 121.9666 | -0.13458 | 0.045273 | 0.059686 | 0.0038281 | 0.031678 | -0.0019632 | 0.034919 | -0.15381 | 0.035169 | 0.030901 | 0.048601 | 0.00039091 | 0.027572 | 0.064087 | 0.027466 | 0.018311 | 0 | 0.073242 | 0.027466 | -0.11444 | 0.050354 | 0.050354 | -0.09613 | 0.018311 | 0 | -0.086975 | -0.13275 | 0.16022 | 0.01831 | -121.8933 | 0.16022 | 0.13275 | 0.11444 | -121.9025 | 0.045776 | 0 | -121.9482 | 0.18311 | 0.036621 | 0.036621 | -121.9666 | 0.20599 | 0.19684 | 0.15106 | -122.081 | 0.15106 | 0.13275 | 0.18311 | -122.0993
2072.1406 | 122.081 | -0.14191 | 121.9849 | -0.15747 | 0.043137 | 0.066095 | 0.0078871 | 0.032319 | -0.0053812 | 0.032355 | -0.18433 | 0.033246 | 0.032396 | 0.048174 | -0.0040951 | 0.027786 | 0 | 0 | 0.022888 | -0.013733 | 0.064087 | 0.009155 | -0.10529 | -0.018311 | 0.018311 | -0.12817 | 0.027466 | 0.018311 | -0.10071 | -0.15106 | 0.15106 | 0.036621 | -121.9208 | 0.14191 | 0.12817 | 0.091553 | -121.9849 | 0.041199 | -0.009155 | -121.9574 | 0.1236 | 0.013733 | 0.022888 | -121.9666 | 0.20599 | 0.14191 | 0.16479 | -122.0901 | 0.16937 | 0.16022 | 0.16022 | -122.1359
2073.8281 | 122.0856 | -0.15564 | 121.9711 | -0.21851 | 0.046128 | 0.0646 | 0.0074597 | 0.029969 | -0.004313 | 0.032569 | -0.15381 | 0.034741 | 0.034532 | 0.049242 | -0.0015317 | 0.02864 | -0.009155 | 0.009155 | 0.013733 | -0.013733 | 0.068665 | 0.022888 | -0.11444 | 0 | 0.004578 | -0.1236 | 0.032043 | 0.009155 | -0.091553 | -0.14191 | 0.17853 | 0.041199 | -121.9025 | 0.16479 | 0.14191 | 0.10071 | -121.9803 | 0.064087 | 0.013733 | -121.9391 | 0.15564 | 0.032044 | 0.018311 | -121.962 | 0.22431 | 0.14649 | 0.16937 | -122.0856 | 0.18768 | 0.16479 | 0.16022 | -122.113
2075.5625 | 122.0718 | -0.11902 | 121.9803 | -0.065918 | 0.046555 | 0.060968 | 0.0019055 | 0.033174 | 0.0014548 | 0.032142 | -0.10803 | 0.033887 | 0.032823 | 0.048388 | 0.0027407 | 0.027145 | 0.073242 | 0.036621 | 0.032043 | 0.027466 | 0.073242 | 0.036621 | -0.10986 | 0.027466 | 0.032043 | -0.11444 | 0.004578 | 0.004578 | -0.082397 | -0.13733 | 0.15564 | 0.009156 | -121.907 | 0.15564 | 0.14649 | 0.13733 | -121.907 | 0.036622 | -0.01831 | -121.9757 | 0.14649 | 0.004578 | 0.022888 | -121.9757 | 0.19226 | 0.19226 | 0.15106 | -122.0901 | 0.1236 | 0.1236 | 0.15106 | -122.1176
2077.25 | 122.168 | -0.11444 | 121.9528 | 0.056152 | 0.040146 | 0.061609 | -0.0015125 | 0.031678 | -0.007731 | 0.031287 | 0.11322 | 0.031964 | 0.03026 | 0.047747 | -0.0011045 | 0.032272 | 0.041199 | 0.091553 | 0.073242 | 0.032043 | 0.036621 | 0.050354 | -0.091553 | 0.07782 | 0.068665 | -0.032043 | -0.027466 | -0.022888 | -0.050354 | -0.1236 | 0.16479 | 0.022888 | -121.9162 | 0.20599 | 0.14648 | 0.1236 | -121.9116 | 0.064087 | -0.009155 | -121.9803 | 0.19226 | 0.082398 | 0.091553 | -121.9757 | 0.15106 | 0.15564 | 0.18768 | -122.0444 | 0.086975 | 0.091553 | 0.18311 | -122.0764
2078.9375 | 122.0947 | -0.12817 | 121.9711 | -0.088806 | 0.043137 | 0.059686 | 0.00019645 | 0.03296 | -0.00089518 | 0.031287 | -0.10803 | 0.036878 | 0.029405 | 0.048388 | 0.0016727 | 0.026291 | 0.07782 | 0.045776 | 0.036621 | 0.027466 | 0.073242 | 0.027466 | -0.09613 | 0.036621 | 0.050354 | -0.10529 | 0.009155 | 0.018311 | -0.073242 | -0.13275 | 0.15564 | 0.032044 | -121.8979 | 0.17395 | 0.15564 | 0.1236 | -121.8933 | 0.054932 | -0.004577 | -121.962 | 0.1648 | 0.022888 | 0.027465 | -121.9528 | 0.20142 | 0.20599 | 0.1648 | -122.0673 | 0.13733 | 0.14649 | 0.17853 | -122.1039
2080.6875 | 122.2092 | -0.1236 | 121.9666 | -0.17273 | 0.043991 | 0.063104 | 0.0048963 | 0.035096 | -0.0092264 | 0.03086 | -0.15381 | 0.03111 | 0.034318 | 0.04732 | -0.0040951 | 0.03099 | 0.082397 | 0.14191 | 0.12817 | 0.07782 | 0.032043 | 0.041199 | -0.07782 | 0.10071 | 0.14648 | 0.009155 | -0.022888 | -0.032043 | -0.050354 | -0.11902 | 0.16479 | 0.045776 | -121.9345 | 0.2655 | 0.20142 | 0.15564 | -121.8842 | 0.073242 | 0.004577 | -121.9894 | 0.2243 | 0.13275 | 0.12817 | -121.9986 | 0.15564 | 0.20599 | 0.25177 | -122.0444 | 0.10071 | 0.091553 | 0.27008 | -122.0856
2082.3906 | 122.0718 | -0.14648 | 122.0032 | -0.04303 | 0.046128 | 0.059259 | 0.0023329 | 0.031465 | -4.058e-05 | 0.03321 | -0.046997 | 0.034101 | 0.033464 | 0.049669 | 0.0027407 | 0.027572 | 0.045776 | 0 | 0.009155 | 0.009155 | 0.064087 | 0.018311 | -0.12817 | 0.004578 | -0.018311 | -0.15106 | 0.018311 | 0.004578 | -0.086975 | -0.13275 | 0.16479 | 0.01831 | -121.9391 | 0.14648 | 0.15564 | 0.13733 | -121.9574 | 0.059509 | 0.013733 | -121.9849 | 0.15106 | -0.004578 | -0.018311 | -121.9986 | 0.21057 | 0.19226 | 0.15564 | -122.1313 | 0.16479 | 0.15106 | 0.12817 | -122.1359
2084.1406 | 122.1313 | -0.12817 | 121.9894 | -0.21851 | 0.039292 | 0.061395 | 0.0034009 | 0.033387 | -0.0087992 | 0.032569 | -0.11566 | 0.03346 | 0.032396 | 0.049029 | -0.0017453 | 0.029708 | 0.091553 | 0.11444 | 0.1236 | 0.059509 | 0.045776 | 0.050354 | -0.086975 | 0.082397 | 0.1236 | -0.004578 | -0.032043 | -0.018311 | -0.041199 | -0.10529 | 0.17853 | 0.041199 | -121.9437 | 0.24262 | 0.18768 | 0.14648 | -121.8979 | 0.086975 | 0.022888 | -122.0215 | 0.21057 | 0.1236 | 0.10071 | -122.0078 | 0.17395 | 0.21973 | 0.25177 | -122.0764 | 0.096131 | 0.10986 | 0.25177 | -122.0947
2085.8281 | 122.1451 | -0.14648 | 121.9482 | -0.17273 | 0.046768 | 0.060327 | 0.0044691 | 0.03296 | -0.0017496 | 0.032783 | -0.2301 | 0.034741 | 0.034105 | 0.048388 | -0.00067729 | 0.028213 | 0.013733 | -0.013733 | -0.013733 | -0.004578 | 0.073242 | 0.022888 | -0.1236 | 0.018311 | 0.041199 | -0.10986 | 0.027466 | 0.009155 | -0.073242 | -0.15106 | 0.16937 | 0.022888 | -121.875 | 0.13275 | 0.14191 | 0.11902 | -121.9345 | 0.073242 | -0.004578 | -121.9208 | 0.16479 | 0.036621 | 0.041199 | -121.9391 | 0.21973 | 0.16022 | 0.13275 | -122.0718 | 0.17395 | 0.15564 | 0.18768 | -122.0993
2087.5781 | 122.168 | -0.082397 | 121.9482 | 0.14008 | 0.04271 | 0.059259 | -0.0027941 | 0.036164 | -0.0019632 | 0.03321 | 0.13611 | 0.031537 | 0.030046 | 0.049669 | 0.00060451 | 0.02864 | 0.091553 | 0.11902 | 0.11902 | 0.059509 | 0.036621 | 0.059509 | -0.064087 | 0.10529 | 0.091553 | -0.004578 | -0.027466 | -0.032043 | -0.045776 | -0.10071 | 0.14191 | 0.01831 | -121.9116 | 0.20142 | 0.14191 | 0.1236 | -121.8567 | 0.036621 | -0.018311 | -121.9757 | 0.18768 | 0.077819 | 0.09613 | -121.9803 | 0.11902 | 0.17395 | 0.20142 | -122.0123 | 0.054931 | 0.050354 | 0.17395 | -122.0489
2089.2656 | 122.1863 | -0.10986 | 121.9757 | 0.079041 | 0.041855 | 0.060541 | -0.0010851 | 0.031251 | -0.0030314 | 0.032569 | 0.13611 | 0.033673 | 0.032182 | 0.047533 | -0.0015317 | 0.029922 | 0.091553 | 0.09613 | 0.10986 | 0.045776 | 0.045776 | 0.050354 | -0.068665 | 0.10529 | 0.09613 | -0.009155 | -0.009155 | -0.027466 | -0.050354 | -0.10986 | 0.16022 | 0.041198 | -121.9299 | 0.20599 | 0.15564 | 0.11444 | -121.8842 | 0.059509 | 0 | -121.9849 | 0.21515 | 0.10071 | 0.10071 | -122.0032 | 0.15564 | 0.20142 | 0.21973 | -122.0444 | 0.10071 | 0.082397 | 0.20599 | -122.0856
2091.0156 | 122.1451 | -0.11902 | 121.9803 | -0.14984 | 0.04506 | 0.060541 | 0.0059643 | 0.033174 | 0.00038662 | 0.032569 | -0.18433 | 0.035169 | 0.033464 | 0.048174 | 0.0014591 | 0.027359 | 0.059509 | 0.004578 | 0.027466 | 0.018311 | 0.086975 | 0.041199 | -0.12817 | 0.032043 | 0.045776 | -0.10529 | 0.013733 | 0 | -0.07782 | -0.13733 | 0.16022 | -0.009155 | -121.8933 | 0.1236 | 0.13733 | 0.14649 | -121.9208 | 0.041199 | -0.01831 | -121.9666 | 0.15106 | 0.013733 | 0.032043 | -121.9803 | 0.20599 | 0.17853 | 0.14649 | -122.1085 | 0.13275 | 0.11902 | 0.16479 | -122.1176
2092.7656 | 122.2321 | -0.082397 | 121.9803 | -0.096436 | 0.04271 | 0.063318 | 0.0059643 | 0.032533 | -0.0070902 | 0.031074 | -0.0012209 | 0.032392 | 0.032182 | 0.04732 | -0.0023861 | 0.02864 | 0.054932 | 0.10071 | 0.10986 | 0.054932 | 0.054932 | 0.032043 | -0.073242 | 0.10529 | 0.1236 | 0.013733 | -0.013733 | -0.036621 | -0.027466 | -0.11902 | 0.11444 | 0.009155 | -121.9254 | 0.18311 | 0.13733 | 0.12817 | -121.9254 | 0.054931 | -0.036622 | -121.994 | 0.18768 | 0.09613 | 0.13275 | -122.0169 | 0.13733 | 0.13733 | 0.19226 | -122.0535 | 0.068664 | 0.045776 | 0.20599 | -122.0993
2094.5312 | 122.1954 | -0.11444 | 121.9711 | 0.079041 | 0.043778 | 0.060968 | 0.0016919 | 0.031678 | -0.004954 | 0.031928 | 0.14374 | 0.033246 | 0.033464 | 0.047961 | 0.00017731 | 0.027786 | 0.091553 | 0.11902 | 0.10986 | 0.045776 | 0.045776 | 0.064087 | -0.073242 | 0.1236 | 0.07782 | -0.018311 | -0.018311 | -0.022888 | -0.059509 | -0.10986 | 0.17853 | 0.041199 | -121.9254 | 0.23346 | 0.16022 | 0.11902 | -121.8796 | 0.054932 | 0.004578 | -121.9894 | 0.23804 | 0.09613 | 0.091552 | -121.994 | 0.16022 | 0.20599 | 0.2243 | -122.0444 | 0.09613 | 0.091553 | 0.19226 | -122.081
2096.2812 | 122.1634 | -0.13733 | 121.9986 | -0.12695 | 0.046341 | 0.060327 | 0.0051099 | 0.031892 | 0.0010276 | 0.034064 | -0.18433 | 0.034101 | 0.034105 | 0.047747 | 0.0027407 | 0.025222 | 0.054932 | 0.032043 | 0.022888 | 0.013733 | 0.068665 | 0.013733 | -0.12817 | 0.050354 | 0.036621 | -0.091553 | 0.013733 | -0.004578 | -0.068665 | -0.11902 | 0.15106 | 0.009155 | -121.9299 | 0.16937 | 0.15106 | 0.14191 | -121.9437 | 0.068664 | 0.01831 | -121.9849 | 0.18768 | 0.045776 | 0.027466 | -122.0032 | 0.20599 | 0.19226 | 0.16022 | -122.1268 | 0.15106 | 0.13275 | 0.17395 | -122.1176
2097.9688 | 122.2092 | -0.10986 | 121.9803 | 0.10956 | 0.043778 | 0.061182 | -0.0012987 | 0.033814 | -0.00025418 | 0.032569 | 0.052185 | 0.036664 | 0.032182 | 0.050097 | 0.0018863 | 0.026077 | 0.009155 | 0 | -0.013733 | -0.013733 | 0.073242 | 0.041199 | -0.10986 | 0.027466 | -0.041199 | -0.1236 | 0.018311 | 0.022888 | -0.086975 | -0.13733 | 0.15106 | 0 | -121.907 | 0.10986 | 0.09613 | 0.09613 | -121.9711 | 0.022888 | -0.027466 | -121.962 | 0.13733 | -0.013733 | 0.013733 | -121.9574 | 0.18311 | 0.11902 | 0.09613 | -122.0901 | 0.12817 | 0.13275 | 0.068664 | -122.1176
2099.7188 | 122.1085 | -0.13733 | 122.0032 | -0.1651 | 0.043351 | 0.062891 | 0.0040417 | 0.031678 | -0.0062356 | 0.032996 | -0.16144 | 0.034101 | 0.033678 | 0.04732 | -0.0025999 | 0.028427 | 0.064087 | 0.12817 | 0.10986 | 0.054932 | 0.036621 | 0.045776 | -0.09613 | 0.064087 | 0.1236 | -0.027466 | -0.018311 | -0.036621 | -0.07782 | -0.13733 | 0.18311 | 0.041199 | -121.9666 | 0.2655 | 0.19226 | 0.15106 | -121.9391 | 0.059509 | 0 | -122.0215 | 0.20142 | 0.10986 | 0.10986 | -122.0398 | 0.17395 | 0.20142 | 0.24719 | -122.0993 | 0.11902 | 0.10071 | 0.26093 | -122.1405
2101.4062 | 122.1497 | -0.12817 | 121.9757 | -0.088806 | 0.047196 | 0.060754 | -0.00065795 | 0.034455 | 0.00060022 | 0.032783 | -0.13092 | 0.034314 | 0.031755 | 0.050097 | 0.0014591 | 0.027145 | 0.050354 | 0.059509 | 0.032043 | 0.027466 | 0.10529 | 0.022888 | -0.091553 | 0.045776 | 0.045776 | -0.091553 | 0.009155 | 0.004578 | -0.073242 | -0.13733 | 0.15106 | 0.036621 | -121.8704 | 0.18768 | 0.15564 | 0.11902 | -121.9254 | 0.054932 | -0.009155 | -121.9666 | 0.17395 | 0.036621 | 0.045776 | -121.9711 | 0.23346 | 0.17853 | 0.16022 | -122.0673 | 0.13733 | 0.13275 | 0.17395 | -122.113
2103.1719 | 122.1268 | -0.14648 | 121.9986 | -0.20325 | 0.04805 | 0.061182 | 0.0066053 | 0.03296 | -0.0055948 | 0.032142 | -0.21484 | 0.035382 | 0.033037 | 0.048174 | -0.0028135 | 0.028427 | -0.027466 | 0.004578 | 0.013733 | -0.013733 | 0.073242 | 0.009155 | -0.1236 | -0.004578 | -0.009155 | -0.1236 | 0.022888 | 0.027466 | -0.10529 | -0.14191 | 0.15564 | 0.022888 | -121.9254 | 0.15106 | 0.13275 | 0.10986 | -122.0261 | 0.041198 | 0.004577 | -121.9757 | 0.14191 | 0.022888 | 0.018311 | -121.9711 | 0.21973 | 0.11902 | 0.16022 | -122.1222 | 0.16937 | 0.17395 | 0.13733 | -122.1405
2104.8594 | 122.1634 | -0.09613 | 121.9849 | -0.18036 | 0.049332 | 0.060968 | 0.0063917 | 0.033814 | -0.00046778 | 0.034064 | -0.2301 | 0.035169 | 0.036241 | 0.046892 | -0.0023861 | 0.028854 | -0.022888 | 0.004578 | -0.004578 | 0.009155 | 0.086975 | 0.013733 | -0.1236 | 0 | 0.013733 | -0.1236 | 0.027466 | -0.009155 | -0.073242 | -0.14191 | 0.10986 | -0.027466 | -121.8979 | 0.10071 | 0.10528 | 0.13275 | -122.0078 | 0.022888 | -0.045777 | -121.9574 | 0.09613 | -0.027466 | 0.018311 | -121.994 | 0.1831 | 0.073242 | 0.091552 | -122.1085 | 0.1236 | 0.086975 | 0.10986 | -122.1268
2106.6094 | 122.2321 | -0.10071 | 121.9757 | -0.10406 | 0.040787 | 0.063532 | 0.0016919 | 0.034669 | -0.00944 | 0.032355 | -0.10803 | 0.031323 | 0.030901 | 0.047533 | -0.0011045 | 0.029281 | 0.073242 | 0.16022 | 0.13733 | 0.07782 | 0.054932 | 0.064087 | -0.082397 | 0.11444 | 0.15564 | 0.036621 | -0.022888 | -0.013733 | -0.032043 | -0.10071 | 0.1648 | 0.018311 | -121.9208 | 0.26093 | 0.17853 | 0.16022 | -121.9025 | 0.068665 | 0 | -121.9986 | 0.21515 | 0.13733 | 0.13733 | -121.9894 | 0.15564 | 0.17395 | 0.23804 | -122.0581 | 0.07782 | 0.086975 | 0.25635 | -122.0764
2108.3594 | 122.2275 | -0.07782 | 121.9482 | 0.094299 | 0.043778 | 0.061182 | 0.0016919 | 0.03296 | 0.00017302 | 0.033851 | 0.12848 | 0.034101 | 0.031969 | 0.046465 | 0.0010317 | 0.028854 | 0.004578 | -0.004578 | -0.013733 | -0.018311 | 0.07782 | 0.041199 | -0.10529 | 0.050354 | 0.004578 | -0.091553 | 0.004578 | -0.009155 | -0.073242 | -0.11444 | 0.11902 | -0.027466 | -121.8704 | 0.073242 | 0.059509 | 0.086975 | -121.9437 | 0.004578 | -0.036621 | -121.9437 | 0.12817 | -0.013733 | 0.022888 | -121.9574 | 0.15564 | 0.082398 | 0.064087 | -122.0535 | 0.082398 | 0.068665 | 0.082398 | -122.0627
2110.125 | 122.1359 | -0.12817 | 122.0306 | -0.088806 | 0.045273 | 0.061609 | 0.0031873 | 0.033387 | 0.00017302 | 0.033423 | -0.13855 | 0.033673 | 0.034318 | 0.048601 | 0.0018863 | 0.026718 | 0.064087 | 0.073242 | 0.041199 | 0.027466 | 0.068665 | 0.032043 | -0.10986 | 0.050354 | 0.041199 | -0.09613 | 0.027466 | -0.004578 | -0.059509 | -0.14191 | 0.16022 | 0.018311 | -121.962 | 0.20142 | 0.15564 | 0.13733 | -121.9666 | 0.068665 | -0.013733 | -122.0032 | 0.17853 | 0.032044 | 0.045777 | -122.0352 | 0.19684 | 0.19226 | 0.16937 | -122.1405 | 0.15564 | 0.1236 | 0.16937 | -122.1725
2111.8281 | 122.2412 | -0.082397 | 121.9849 | 0.08667 | 0.044205 | 0.058618 | 0.0019055 | 0.030824 | -0.0036722 | 0.03321 | 0.17426 | 0.036023 | 0.032823 | 0.048815 | -0.00024989 | 0.029495 | -0.018311 | -0.004578 | 0 | -0.013733 | 0.091553 | 0.032043 | -0.10529 | 0.045776 | 0.004578 | -0.073242 | 0.013733 | -0.022888 | -0.054932 | -0.13275 | 0.11444 | -0.022889 | -121.8933 | 0.077819 | 0.068664 | 0.091553 | -122.0032 | 0.027465 | -0.050354 | -121.9711 | 0.12817 | 0.009155 | 0.059509 | -122.0078 | 0.17395 | 0.064086 | 0.082397 | -122.0901 | 0.09613 | 0.059509 | 0.086975 | -122.1176
2113.5781 | 122.2366 | -0.091553 | 121.9894 | 0.010376 | 0.043778 | 0.060968 | 0.0070325 | 0.031465 | -0.007731 | 0.031074 | 0.067444 | 0.03111 | 0.033464 | 0.046679 | -0.0030271 | 0.029922 | -0.004578 | 0.054932 | 0.054932 | 0.027466 | 0.050354 | 0.041199 | -0.09613 | 0.059509 | 0.059509 | -0.032043 | 0.004578 | -0.027466 | -0.054932 | -0.10529 | 0.13275 | -0.004577 | -121.9391 | 0.14649 | 0.11902 | 0.1236 | -121.994 | 0.036621 | -0.013733 | -121.9849 | 0.15106 | 0.05951 | 0.073243 | -122.0169 | 0.14191 | 0.086975 | 0.14649 | -122.0856 | 0.096131 | 0.064087 | 0.15106 | -122.0947
2115.3438 | 122.1176 | -0.13733 | 121.9986 | 0.071411 | 0.044205 | 0.062891 | 0.0016919 | 0.031892 | 0.00060022 | 0.033423 | -0.0088499 | 0.034741 | 0.033037 | 0.046892 | 0.0023135 | 0.02864 | -0.004578 | -0.022888 | -0.036621 | -0.027466 | 0.073242 | 0.027466 | -0.091553 | -0.009155 | -0.041199 | -0.15564 | 0.041199 | 0.032043 | -0.086975 | -0.15106 | 0.16479 | 0.045776 | -121.9254 | 0.11444 | 0.10986 | 0.064087 | -122.0032 | 0.050354 | -0.013733 | -121.9574 | 0.12817 | -0.018311 | -0.004578 | -121.9666 | 0.21057 | 0.13275 | 0.10071 | -122.0901 | 0.17853 | 0.16937 | 0.09613 | -122.1497
2117.1094 | 122.1268 | -0.1236 | 122.049 | 0.040894 | 0.04506 | 0.061609 | -0.00044435 | 0.03061 | -0.00046778 | 0.034278 | -0.0012209 | 0.035382 | 0.030687 | 0.045824 | 0.0020999 | 0.029708 | -0.013733 | -0.045776 | -0.041199 | -0.027466 | 0.073242 | 0.013733 | -0.11444 | -0.018311 | -0.050354 | -0.16022 | 0.032043 | 0.009155 | -0.073242 | -0.13733 | 0.13733 | 0.009155 | -121.9757 | 0.07782 | 0.09613 | 0.086975 | -122.0627 | 0.050354 | -0.013733 | -122.0169 | 0.10528 | -0.036621 | -0.022888 | -122.0398 | 0.19684 | 0.10986 | 0.082397 | -122.1634 | 0.15564 | 0.13275 | 0.073242 | -122.1863
2118.7969 | 122.1817 | -0.12817 | 122.0123 | -0.13458 | 0.046768 | 0.061823 | 0.0044691 | 0.033174 | -0.0028178 | 0.032355 | -0.13855 | 0.034101 | 0.034105 | 0.046038 | -0.00067729 | 0.027359 | 0.036621 | 0.036621 | 0.027466 | 0.032043 | 0.068665 | 0.013733 | -0.10986 | 0.045776 | 0.045776 | -0.082397 | 0.013733 | -0.004578 | -0.07782 | -0.1236 | 0.14191 | 0.018311 | -121.9437 | 0.1648 | 0.16022 | 0.14191 | -121.9757 | 0.050354 | 0.004578 | -121.9986 | 0.17395 | 0.045777 | 0.041199 | -122.0169 | 0.19684 | 0.1648 | 0.15564 | -122.1222 | 0.14191 | 0.1236 | 0.17395 | -122.1359
2120.5469 | 122.2595 | -0.086975 | 121.9711 | 0.16296 | 0.044846 | 0.060327 | 0.0040417 | 0.034883 | -0.0036722 | 0.033637 | 0.15137 | 0.034314 | 0.03325 | 0.046892 | 0.00039091 | 0.029708 | 0.091553 | 0.09613 | 0.10529 | 0.059509 | 0.041199 | 0.054932 | -0.068665 | 0.11444 | 0.10529 | -0.009155 | -0.027466 | -0.032043 | -0.032043 | -0.07782 | 0.14191 | 0.01831 | -121.9299 | 0.1831 | 0.14648 | 0.12817 | -121.8796 | 0.054932 | 0.009155 | -121.9986 | 0.20142 | 0.07782 | 0.068665 | -122.0032 | 0.12817 | 0.17853 | 0.19226 | -122.0398 | 0.059509 | 0.054932 | 0.19226 | -122.049
2122.3125 | 122.1451 | -0.11902 | 122.0398 | -0.081177 | 0.04506 | 0.060327 | 0.0029737 | 0.032533 | -0.0017496 | 0.033637 | -0.085144 | 0.037732 | 0.032823 | 0.050097 | 0.0010317 | 0.026931 | 0.068665 | 0.022888 | 0.041199 | 0.009155 | 0.054932 | 0.009155 | -0.10529 | 0.045776 | 0.054932 | -0.086975 | 0.013733 | 0 | -0.068665 | -0.12817 | 0.12817 | 0.013733 | -121.9849 | 0.14191 | 0.12817 | 0.11444 | -121.9711 | 0.050354 | -0.009155 | -122.0261 | 0.16479 | 0.032044 | 0.041199 | -122.0398 | 0.17395 | 0.18768 | 0.16022 | -122.1451 | 0.13275 | 0.11902 | 0.17395 | -122.168
2124 | 122.2183 | -0.10986 | 121.994 | 0.033264 | 0.041001 | 0.062463 | 0.0014783 | 0.030397 | -0.0079446 | 0.031928 | 0.11322 | 0.031751 | 0.032396 | 0.04732 | -0.00089089 | 0.03099 | 0.027466 | 0.068665 | 0.064087 | 0.018311 | 0.041199 | 0.059509 | -0.073242 | 0.054932 | 0.059509 | -0.036621 | 0 | -0.018311 | -0.050354 | -0.10529 | 0.16937 | 0.036621 | -121.9528 | 0.17853 | 0.12817 | 0.091553 | -121.9666 | 0.059509 | 0.004577 | -121.994 | 0.16479 | 0.073242 | 0.068665 | -122.0123 | 0.15106 | 0.13733 | 0.17395 | -122.0673 | 0.10986 | 0.091552 | 0.16937 | -122.0993
2125.75 | 122.2366 | -0.07782 | 122.0078 | 0.17059 | 0.041428 | 0.060968 | -0.00023075 | 0.03296 | -0.0023904 | 0.031501 | 0.13611 | 0.032392 | 0.033464 | 0.04732 | 0.0010317 | 0.027572 | 0.086975 | 0.086975 | 0.09613 | 0.068665 | 0.050354 | 0.050354 | -0.07782 | 0.12817 | 0.10071 | -0.004578 | -0.027466 | -0.054932 | -0.036621 | -0.10071 | 0.12817 | 0 | -121.9574 | 0.16479 | 0.14649 | 0.14649 | -121.9208 | 0.041199 | -0.022888 | -122.0352 | 0.20599 | 0.073242 | 0.09613 | -122.0627 | 0.12817 | 0.16479 | 0.17395 | -122.0856 | 0.050354 | 0.022888 | 0.17853 | -122.1085
2127.5 | 122.168 | -0.14191 | 122.0398 | -0.10406 | 0.045914 | 0.061182 | 0.0044691 | 0.032319 | 0.0023092 | 0.031714 | -0.12329 | 0.032819 | 0.035173 | 0.047106 | 0.0018863 | 0.026931 | 0.050354 | 0.036621 | 0.022888 | 0.027466 | 0.064087 | 0.013733 | -0.09613 | 0.045776 | 0.045776 | -0.073242 | 0.009155 | 0 | -0.07782 | -0.13275 | 0.15564 | 0.045777 | -121.9757 | 0.17853 | 0.16937 | 0.1236 | -121.9894 | 0.064087 | 0.009156 | -122.0306 | 0.18768 | 0.068665 | 0.059509 | -122.0398 | 0.20599 | 0.19226 | 0.16479 | -122.1359 | 0.15106 | 0.14191 | 0.18768 | -122.1725
2129.25 | 122.2458 | -0.091553 | 122.0444 | -0.14984 | 0.041855 | 0.062677 | 0.0068189 | 0.032319 | -0.0079446 | 0.032142 | -0.046997 | 0.031964 | 0.031541 | 0.046679 | -0.0036679 | 0.029495 | 0.073242 | 0.14191 | 0.1236 | 0.064087 | 0.036621 | 0.064087 | -0.086975 | 0.13733 | 0.15564 | 0.050354 | -0.022888 | -0.022888 | -0.032043 | -0.10071 | 0.15564 | 0.004578 | -122.0078 | 0.23346 | 0.15564 | 0.15106 | -121.9711 | 0.05951 | -0.009155 | -122.0673 | 0.22888 | 0.14191 | 0.15106 | -122.0673 | 0.12817 | 0.16479 | 0.21515 | -122.1313 | 0.068665 | 0.068665 | 0.24719 | -122.1451
2130.9531 | 122.1451 | -0.13275 | 122.0398 | 0.033264 | 0.045914 | 0.060541 | -1.7146e-05 | 0.034455 | 0.0012412 | 0.034278 | -0.0088499 | 0.03346 | 0.032182 | 0.050524 | 0.0033817 | 0.026504 | -0.018311 | -0.045776 | -0.036621 | -0.022888 | 0.07782 | 0.022888 | -0.1236 | -0.013733 | -0.036621 | -0.15564 | 0.036621 | 0.009155 | -0.091553 | -0.12817 | 0.15564 | 0.009155 | -121.962 | 0.086975 | 0.10986 | 0.10071 | -122.0581 | 0.041198 | 0.004577 | -122.0032 | 0.11902 | -0.022889 | -0.027466 | -122.0306 | 0.21057 | 0.11444 | 0.09613 | -122.1634 | 0.16937 | 0.14191 | 0.09613 | -122.168
2132.7031 | 122.1222 | -0.13733 | 122.0444 | -0.20325 | 0.043351 | 0.061609 | 0.0053235 | 0.034669 | -0.006022 | 0.031714 | -0.20721 | 0.032392 | 0.032823 | 0.045611 | -0.0019589 | 0.029068 | 0.041199 | 0.10986 | 0.10071 | 0.050354 | 0.059509 | 0.036621 | -0.09613 | 0.036621 | 0.073242 | -0.050354 | 0.013733 | 0.004578 | -0.064087 | -0.13275 | 0.17395 | 0.041199 | -121.9849 | 0.24719 | 0.18768 | 0.14648 | -122.0032 | 0.073242 | 0.004578 | -122.0306 | 0.17395 | 0.086975 | 0.082397 | -122.0398 | 0.19684 | 0.17853 | 0.23804 | -122.1405 | 0.15106 | 0.14191 | 0.21057 | -122.1771
2134.4531 | 122.2824 | -0.086975 | 122.0123 | -0.012512 | 0.042069 | 0.064813 | 0.0023329 | 0.029328 | -0.0075174 | 0.029578 | -0.0088499 | 0.031751 | 0.032823 | 0.04732 | -0.0025999 | 0.029068 | 0.013733 | 0.064087 | 0.073242 | 0.041199 | 0.050354 | 0.045776 | -0.082397 | 0.068665 | 0.073242 | -0.004578 | 0 | -0.013733 | -0.050354 | -0.09613 | 0.13275 | 0.004578 | -121.962 | 0.15106 | 0.12817 | 0.1236 | -121.9986 | 0.036621 | -0.009155 | -122.0123 | 0.15564 | 0.082397 | 0.091552 | -122.0261 | 0.13733 | 0.10071 | 0.16022 | -122.0947 | 0.086975 | 0.073242 | 0.16022 | -122.1085
2136.2188 | 122.1451 | -0.1236 | 122.0261 | 0.056152 | 0.044846 | 0.059686 | -0.0012987 | 0.030183 | 0.0014548 | 0.033637 | -0.016479 | 0.036023 | 0.035173 | 0.05031 | 0.0016727 | 0.027572 | -0.009155 | -0.054932 | -0.045776 | -0.022888 | 0.068665 | 0.018311 | -0.10071 | -0.018311 | -0.054932 | -0.16479 | 0.027466 | 0.022888 | -0.086975 | -0.1236 | 0.14191 | 0.022888 | -121.9574 | 0.068664 | 0.10071 | 0.07782 | -122.0352 | 0.036621 | 0 | -121.9986 | 0.10528 | -0.041199 | -0.041199 | -122.0032 | 0.19226 | 0.11444 | 0.07782 | -122.1268 | 0.15106 | 0.14648 | 0.068664 | -122.1497
2137.9062 | 122.2733 | -0.091553 | 121.994 | -0.0354 | 0.042923 | 0.063959 | 0.0031873 | 0.02826 | -0.008372 | 0.030433 | -0.039368 | 0.029615 | 0.030473 | 0.046465 | -0.0015317 | 0.029495 | 0.050354 | 0.082397 | 0.086975 | 0.045776 | 0.050354 | 0.041199 | -0.086975 | 0.11902 | 0.10986 | 0.022888 | -0.018311 | -0.009155 | -0.045776 | -0.09613 | 0.13275 | 0.004578 | -121.9437 | 0.17395 | 0.13733 | 0.13275 | -121.9437 | 0.045777 | -0.004577 | -122.0123 | 0.21057 | 0.11444 | 0.11902 | -122.0032 | 0.14191 | 0.14191 | 0.17853 | -122.081 | 0.073242 | 0.082398 | 0.20142 | -122.0901
2139.6406 | 122.2412 | -0.10071 | 122.0123 | -0.15747 | 0.043564 | 0.061395 | 0.0068189 | 0.035096 | -0.0045266 | 0.031501 | -0.14618 | 0.032392 | 0.033464 | 0.04497 | -0.0019589 | 0.027999 | 0.091553 | 0.14191 | 0.1236 | 0.068665 | 0.041199 | 0.054932 | -0.09613 | 0.11902 | 0.14648 | 0.027466 | -0.009155 | -0.022888 | -0.036621 | -0.10986 | 0.15564 | 0.004578 | -121.9711 | 0.24262 | 0.16937 | 0.16479 | -121.9208 | 0.064087 | -0.009155 | -122.0215 | 0.21973 | 0.12817 | 0.13733 | -122.0352 | 0.14191 | 0.19226 | 0.2243 | -122.1085 | 0.091553 | 0.07782 | 0.24719 | -122.1222
2141.3906 | 122.1222 | -0.14191 | 122.0398 | -0.23376 | 0.044632 | 0.062463 | 0.0055371 | 0.035523 | -0.0030314 | 0.032996 | -0.22247 | 0.032605 | 0.035173 | 0.04732 | -0.00089089 | 0.026077 | 0.041199 | 0.059509 | 0.045776 | 0.018311 | 0.045776 | 0.036621 | -0.1236 | 0.027466 | 0.032043 | -0.10071 | 0.018311 | 0 | -0.086975 | -0.1236 | 0.17853 | 0.018311 | -121.994 | 0.20142 | 0.16022 | 0.14191 | -121.9986 | 0.054932 | 0.018311 | -122.0215 | 0.16937 | 0.041199 | 0.022888 | -122.0398 | 0.18768 | 0.18311 | 0.18768 | -122.1634 | 0.16022 | 0.14191 | 0.17395 | -122.1634
2143.1562 | 122.2549 | -0.086975 | 122.0169 | -0.11169 | 0.04036 | 0.06225 | 0.0019055 | 0.033174 | -0.0075174 | 0.031074 | -0.092773 | 0.030896 | 0.03261 | 0.04732 | -0.0025999 | 0.02864 | 0.082397 | 0.1236 | 0.11444 | 0.064087 | 0.050354 | 0.054932 | -0.059509 | 0.15106 | 0.13275 | 0.027466 | -0.004578 | -0.022888 | -0.036621 | -0.091553 | 0.14191 | 0.027466 | -121.9666 | 0.21057 | 0.15106 | 0.1236 | -121.9345 | 0.050354 | -0.004578 | -122.0215 | 0.23804 | 0.11444 | 0.11902 | -122.0398 | 0.13733 | 0.16937 | 0.20142 | -122.0764 | 0.082397 | 0.064087 | 0.21973 | -122.1085
2144.8438 | 122.2778 | -0.07782 | 122.0215 | 0.079041 | 0.044205 | 0.062463 | -0.0027941 | 0.031892 | 0.0020956 | 0.032996 | 0.097962 | 0.036023 | 0.03261 | 0.049242 | 0.0029543 | 0.026931 | 0.036621 | -0.013733 | -0.004578 | -0.004578 | 0.073242 | 0.022888 | -0.10986 | 0.082397 | 0.009155 | -0.068665 | 0.009155 | -0.009155 | -0.050354 | -0.10986 | 0.10071 | -0.032043 | -121.9482 | 0.064087 | 0.073242 | 0.10529 | -121.9849 | 0.027466 | -0.032043 | -122.0123 | 0.16022 | 0.009155 | 0.041198 | -122.0306 | 0.15106 | 0.11444 | 0.073242 | -122.1313 | 0.086975 | 0.068665 | 0.086975 | -122.1313
2146.6094 | 122.168 | -0.11902 | 122.0444 | -0.17273 | 0.04506 | 0.060327 | 0.0051099 | 0.031892 | -0.0053812 | 0.03321 | -0.16144 | 0.03346 | 0.034746 | 0.048388 | -0.0032407 | 0.029281 | 0.086975 | 0.1236 | 0.11444 | 0.07782 | 0.022888 | 0.059509 | -0.082397 | 0.09613 | 0.12817 | -0.027466 | 0.004578 | -0.013733 | -0.032043 | -0.10529 | 0.17853 | 0.036622 | -122.0215 | 0.24261 | 0.19684 | 0.16022 | -121.9574 | 0.086976 | 0.013733 | -122.0398 | 0.21515 | 0.091553 | 0.07782 | -122.0581 | 0.14191 | 0.20599 | 0.23346 | -122.1268 | 0.1236 | 0.10529 | 0.24719 | -122.1497
2148.375 | 122.2137 | -0.086975 | 122.0398 | -0.18799 | 0.042282 | 0.061823 | 0.0046827 | 0.031465 | -0.0036722 | 0.03086 | -0.15381 | 0.03346 | 0.034105 | 0.048815 | -0.0017453 | 0.028427 | 0.10529 | 0.13275 | 0.12817 | 0.068665 | 0.036621 | 0.050354 | -0.086975 | 0.12817 | 0.14648 | 0.013733 | -0.004578 | -0.027466 | -0.045776 | -0.09613 | 0.13733 | 0 | -122.0032 | 0.21973 | 0.15564 | 0.15564 | -121.9345 | 0.041199 | -0.009155 | -122.0444 | 0.21515 | 0.10071 | 0.10986 | -122.0673 | 0.1236 | 0.19226 | 0.21515 | -122.1268 | 0.082397 | 0.059509 | 0.23346 | -122.1359
2150.0625 | 122.2321 | -0.082397 | 121.9803 | 0.0027468 | 0.042923 | 0.062677 | 0.0027601 | 0.029756 | -0.004954 | 0.031928 | 0.029297 | 0.032605 | 0.03261 | 0.049669 | -0.0019589 | 0.027359 | 0.041199 | 0.050354 | 0.064087 | 0.022888 | 0.036621 | 0.032043 | -0.10071 | 0.064087 | 0.054932 | -0.050354 | 0.004578 | 0 | -0.032043 | -0.10071 | 0.11444 | -0.018311 | -121.9437 | 0.13275 | 0.10528 | 0.1236 | -121.9391 | 0.050354 | -0.018311 | -121.9757 | 0.14648 | 0.032043 | 0.050354 | -121.9803 | 0.11902 | 0.1236 | 0.14648 | -122.081 | 0.086975 | 0.082397 | 0.13733 | -122.081
2151.8125 | 122.2046 | -0.10529 | 122.0261 | 0.10956 | 0.043991 | 0.0599 | -0.00087155 | 0.034028 | 0.0040182 | 0.033851 | 0.029297 | 0.036023 | 0.03261 | 0.050097 | 0.0020999 | 0.02864 | 0.022888 | -0.027466 | -0.036621 | 0 | 0.07782 | 0.013733 | -0.11444 | 0.022888 | -0.036621 | -0.14648 | 0.032043 | -0.004578 | -0.050354 | -0.12817 | 0.11902 | -0.009155 | -121.9482 | 0.07782 | 0.10529 | 0.11444 | -122.0032 | 0.054932 | -0.022888 | -121.994 | 0.12817 | -0.041198 | -0.01831 | -122.0306 | 0.18311 | 0.12817 | 0.068665 | -122.1405 | 0.13733 | 0.10071 | 0.068665 | -122.1542
2153.5938 | 122.2229 | -0.10071 | 122.0306 | -0.18036 | 0.043564 | 0.059686 | 0.0055371 | 0.034455 | -0.006663 | 0.031501 | -0.16907 | 0.033246 | 0.03261 | 0.046679 | -0.00067729 | 0.026931 | 0.10529 | 0.14191 | 0.1236 | 0.064087 | 0.036621 | 0.068665 | -0.091553 | 0.11444 | 0.16022 | 0.009155 | -0.009155 | -0.032043 | -0.050354 | -0.11444 | 0.16937 | 0.009155 | -121.994 | 0.24262 | 0.1648 | 0.15564 | -121.9254 | 0.050354 | -0.013733 | -122.0398 | 0.21515 | 0.10986 | 0.1236 | -122.0627 | 0.13733 | 0.20599 | 0.2243 | -122.1222 | 0.091553 | 0.068665 | 0.26093 | -122.1451
2155.2656 | 122.2321 | -0.09613 | 122.0078 | 0.094299 | 0.041642 | 0.061395 | -0.00065795 | 0.030397 | -0.004954 | 0.032783 | 0.12085 | 0.033032 | 0.031969 | 0.04732 | 0.00039091 | 0.02864 | 0.09613 | 0.10529 | 0.10529 | 0.045776 | 0.045776 | 0.068665 | -0.073242 | 0.11444 | 0.082397 | -0.018311 | 0 | -0.036621 | -0.041199 | -0.09613 | 0.16479 | 0.022888 | -121.962 | 0.20142 | 0.14191 | 0.11902 | -121.9116 | 0.054931 | 0 | -122.0078 | 0.21057 | 0.077819 | 0.077819 | -122.0444 | 0.14191 | 0.19226 | 0.20142 | -122.081 | 0.09613 | 0.059509 | 0.17853 | -122.1039
2157.0156 | 122.1771 | -0.10986 | 122.0261 | -0.11932 | 0.046128 | 0.061395 | 0.0036145 | 0.032746 | 0.0020956 | 0.03321 | -0.19958 | 0.035596 | 0.033891 | 0.047961 | 0.0027407 | 0.027786 | 0.059509 | 0.045776 | 0.022888 | 0.041199 | 0.082397 | 0.036621 | -0.1236 | 0.068665 | 0.041199 | -0.082397 | 0.018311 | 0.018311 | -0.059509 | -0.13275 | 0.14648 | -0.013733 | -121.9437 | 0.15564 | 0.15106 | 0.16479 | -121.9666 | 0.050354 | -0.022888 | -122.0078 | 0.17853 | 0.027466 | 0.050354 | -122.0078 | 0.19226 | 0.16937 | 0.13275 | -122.1497 | 0.12817 | 0.12817 | 0.15106 | -122.1588
2158.7188 | 122.1542 | -0.14191 | 122.0718 | -0.1651 | 0.04506 | 0.060754 | 0.0031873 | 0.031465 | -0.0051676 | 0.032569 | -0.19958 | 0.033032 | 0.034746 | 0.04732 | -0.0028135 | 0.029068 | 0.073242 | 0.11902 | 0.09613 | 0.054932 | 0.041199 | 0.050354 | -0.09613 | 0.064087 | 0.091553 | -0.036621 | 0.004578 | -0.013733 | -0.050354 | -0.11444 | 0.19226 | 0.045777 | -122.0306 | 0.26093 | 0.19684 | 0.15106 | -121.9986 | 0.091553 | 0.027466 | -122.0673 | 0.20599 | 0.10529 | 0.07782 | -122.0856 | 0.18311 | 0.21515 | 0.23804 | -122.168 | 0.14649 | 0.12817 | 0.23346 | -122.1863
2160.4688 | 122.2321 | -0.082397 | 122.0352 | 0.094299 | 0.041001 | 0.063318 | -0.0019397 | 0.031892 | -0.0051676 | 0.031928 | 0.10559 | 0.032819 | 0.030687 | 0.04732 | 0.00081811 | 0.029068 | 0.09613 | 0.10071 | 0.086975 | 0.045776 | 0.032043 | 0.054932 | -0.086975 | 0.10071 | 0.073242 | -0.027466 | -0.013733 | -0.022888 | -0.027466 | -0.091553 | 0.13733 | -0.004578 | -122.0032 | 0.18311 | 0.12817 | 0.13275 | -121.9391 | 0.054931 | -0.009156 | -122.049 | 0.18311 | 0.054931 | 0.064087 | -122.0581 | 0.11444 | 0.17853 | 0.16937 | -122.1222 | 0.068664 | 0.059509 | 0.15564 | -122.1268
2162.2344 | 122.2458 | -0.091553 | 122.0306 | 0.15533 | 0.041855 | 0.059259 | -1.7146e-05 | 0.031465 | -0.0028178 | 0.032355 | 0.12085 | 0.031751 | 0.029619 | 0.047106 | 0.0012455 | 0.027786 | 0.10529 | 0.10071 | 0.1236 | 0.07782 | 0.018311 | 0.064087 | -0.073242 | 0.14191 | 0.11444 | 0.022888 | -0.032043 | -0.027466 | -0.036621 | -0.09613 | 0.15564 | 0.018311 | -122.0123 | 0.19226 | 0.16937 | 0.15106 | -121.9254 | 0.054932 | -0.004577 | -122.0627 | 0.23346 | 0.11444 | 0.11902 | -122.0581 | 0.10986 | 0.19684 | 0.21515 | -122.1039 | 0.05951 | 0.064087 | 0.20599 | -122.1268
2164 | 122.2824 | -0.07782 | 122.0398 | -0.020142 | 0.042923 | 0.060968 | 0.0029737 | 0.034028 | -0.0062356 | 0.031928 | -0.0088499 | 0.033032 | 0.033891 | 0.045824 | -0.0013181 | 0.027999 | 0.045776 | 0.045776 | 0.073242 | 0.013733 | 0.036621 | 0.050354 | -0.07782 | 0.07782 | 0.082397 | -0.022888 | 0 | -0.022888 | -0.022888 | -0.09613 | 0.12817 | 0 | -122.0032 | 0.1236 | 0.091553 | 0.091553 | -121.994 | 0.054932 | -0.01831 | -122.0398 | 0.15564 | 0.054932 | 0.073242 | -122.0627 | 0.11444 | 0.1236 | 0.15106 | -122.1176 | 0.07782 | 0.054932 | 0.16022 | -122.1359
2165.7031 | 122.2641 | -0.091553 | 122.0032 | -0.14221 | 0.039078 | 0.062891 | 0.0023329 | 0.030397 | -0.0038858 | 0.028297 | -0.15381 | 0.030683 | 0.031755 | 0.046038 | -0.0011045 | 0.027572 | 0.11902 | 0.13733 | 0.13275 | 0.073242 | 0.059509 | 0.064087 | -0.07782 | 0.13275 | 0.15106 | 0.032043 | -0.018311 | -0.027466 | -0.027466 | -0.091553 | 0.15564 | 0.013733 | -121.9437 | 0.22888 | 0.16479 | 0.15106 | -121.8842 | 0.064087 | 0 | -122.0215 | 0.2243 | 0.1236 | 0.1236 | -122.0306 | 0.15106 | 0.21057 | 0.2243 | -122.081 | 0.073242 | 0.064087 | 0.24261 | -122.0947
2167.4531 | 122.2916 | -0.068665 | 122.0078 | 0.12482 | 0.043991 | 0.060327 | 0.0021191 | 0.03296 | -4.058e-05 | 0.033423 | 0.12848 | 0.032178 | 0.036027 | 0.048601 | 0.0033817 | 0.024795 | 0.059509 | 0.018311 | 0.018311 | 0 | 0.07782 | 0.032043 | -0.10071 | 0.09613 | 0.041199 | -0.050354 | -0.004578 | -0.022888 | -0.045776 | -0.10986 | 0.10071 | -0.032043 | -121.9299 | 0.086976 | 0.068665 | 0.10071 | -121.9482 | 0.022889 | -0.041198 | -122.0123 | 0.16479 | 0.018311 | 0.059509 | -122.0306 | 0.14649 | 0.12817 | 0.086976 | -122.1085 | 0.064087 | 0.045777 | 0.10986 | -122.1176
2169.1406 | 122.1588 | -0.12817 | 122.0627 | 0.025635 | 0.044846 | 0.060114 | -0.0019397 | 0.034242 | 0.0014548 | 0.034064 | -0.039368 | 0.03581 | 0.032182 | 0.048174 | 0.0033817 | 0.027999 | 0.022888 | -0.041199 | -0.032043 | -0.013733 | 0.068665 | 0.018311 | -0.12817 | 0 | -0.032043 | -0.15564 | 0.041199 | -0.013733 | -0.054932 | -0.11902 | 0.14649 | 0 | -121.994 | 0.086975 | 0.11444 | 0.11444 | -122.0398 | 0.073242 | 0.009155 | -122.0215 | 0.12817 | -0.027466 | -0.036621 | -122.0764 | 0.19684 | 0.15106 | 0.096131 | -122.1909 | 0.16937 | 0.11444 | 0.096131 | -122.1817
2170.9062 | 122.2092 | -0.10529 | 122.081 | -0.18799 | 0.046982 | 0.060327 | 0.0048963 | 0.032105 | -0.0021768 | 0.035346 | -0.20721 | 0.032178 | 0.033464 | 0.047533 | -0.00024989 | 0.025863 | 0.013733 | 0.004578 | 0.013733 | 0.027466 | 0.064087 | 0.032043 | -0.11444 | 0.050354 | 0.054932 | -0.082397 | 0.032043 | 0.032043 | -0.064087 | -0.11902 | 0.13733 | -0.009155 | -122.0169 | 0.10986 | 0.13275 | 0.14191 | -122.0673 | 0.041199 | -0.013733 | -122.049 | 0.15564 | 0.022889 | 0.036622 | -122.049 | 0.16937 | 0.11902 | 0.11902 | -122.1954 | 0.13733 | 0.13733 | 0.16022 | -122.2
2172.6719 | 122.1405 | -0.1236 | 122.0764 | -0.073547 | 0.044419 | 0.059686 | 0.0036145 | 0.033174 | 0.0016684 | 0.033637 | -0.092773 | 0.033887 | 0.034318 | 0.050097 | 0.0018863 | 0.027999 | 0.059509 | 0.054932 | 0.032043 | 0.022888 | 0.059509 | 0.027466 | -0.10529 | 0.054932 | 0.050354 | -0.10071 | 0.036621 | 0 | -0.059509 | -0.13733 | 0.15106 | 0.01831 | -122.0169 | 0.17853 | 0.14648 | 0.12817 | -122.0169 | 0.064087 | -0.013733 | -122.0398 | 0.17853 | 0.022888 | 0.036621 | -122.0764 | 0.1831 | 0.1831 | 0.15564 | -122.1817 | 0.16022 | 0.1236 | 0.17395 | -122.2137
2174.3594 | 122.2092 | -0.091553 | 122.0581 | -0.15747 | 0.047837 | 0.060541 | 0.0053235 | 0.034455 | -0.00046778 | 0.033851 | -0.16907 | 0.034101 | 0.036027 | 0.049029 | -0.00046349 | 0.02864 | 0.013733 | 0.027466 | 0.018311 | 0.022888 | 0.068665 | 0.036621 | -0.11444 | 0.022888 | 0.064087 | -0.068665 | 0.027466 | 0.018311 | -0.064087 | -0.1236 | 0.12817 | -0.022888 | -121.9894 | 0.11902 | 0.11444 | 0.13733 | -122.0444 | 0.027466 | -0.032043 | -122.0306 | 0.11444 | 0.022888 | 0.054931 | -122.0398 | 0.16022 | 0.10529 | 0.10986 | -122.1725 | 0.11902 | 0.10986 | 0.15564 | -122.1817
2176.125 | 122.2778 | -0.064087 | 122.0261 | 0.08667 | 0.043351 | 0.063745 | 0.0012647 | 0.033174 | -0.001536 | 0.036841 | 0.16663 | 0.033673 | 0.031114 | 0.051165 | -0.00067729 | 0.027786 | 0.004578 | 0.013733 | -0.004578 | -0.013733 | 0.073242 | 0.022888 | -0.11902 | 0.064087 | 0.018311 | -0.064087 | 0.022888 | -0.009155 | -0.059509 | -0.11902 | 0.086975 | -0.054932 | -121.9528 | 0.07782 | 0.050354 | 0.10529 | -122.0215 | 0.004578 | -0.054932 | -122.0032 | 0.12817 | 0 | 0.054932 | -122.0352 | 0.13733 | 0.068665 | 0.059509 | -122.1451 | 0.086975 | 0.054932 | 0.082398 | -122.1451
2177.8906 | 122.168 | -0.12817 | 122.0581 | -0.081177 | 0.046128 | 0.058405 | 0.0031873 | 0.032746 | -0.0021768 | 0.032783 | -0.11566 | 0.034955 | 0.033678 | 0.047961 | -3.629e-05 | 0.027999 | 0.036621 | 0.064087 | 0.036621 | 0.018311 | 0.07782 | 0.022888 | -0.12817 | 0.073242 | 0.064087 | -0.07782 | 0.013733 | 0.013733 | -0.054932 | -0.11444 | 0.15106 | 0 | -121.9803 | 0.19226 | 0.14649 | 0.14649 | -122.0215 | 0.073242 | 0.013733 | -122.0444 | 0.20142 | 0.050354 | 0.036621 | -122.0444 | 0.20599 | 0.1648 | 0.1648 | -122.1863 | 0.14191 | 0.14191 | 0.19226 | -122.1725
2179.6406 | 122.2458 | -0.09613 | 122.0352 | 0.048523 | 0.041428 | 0.060327 | 0.00083745 | 0.032746 | -0.0073038 | 0.034492 | 0.11322 | 0.031323 | 0.03325 | 0.044756 | -0.0025999 | 0.030563 | 0.032043 | 0.082397 | 0.07782 | 0.013733 | 0.018311 | 0.07782 | -0.086975 | 0.073242 | 0.073242 | -0.022888 | -0.004578 | -0.004578 | -0.045776 | -0.11902 | 0.17395 | 0.009155 | -122.0169 | 0.17853 | 0.10986 | 0.10071 | -122.0032 | 0.050354 | -0.022889 | -122.0398 | 0.16937 | 0.073242 | 0.096131 | -122.0398 | 0.11444 | 0.12817 | 0.17395 | -122.1222 | 0.091552 | 0.091552 | 0.16937 | -122.1542
2181.3281 | 122.2549 | -0.07782 | 122.0444 | 0.11719 | 0.043351 | 0.0599 | 0.0014783 | 0.031037 | -0.0051676 | 0.031928 | 0.12848 | 0.030683 | 0.031541 | 0.047961 | -3.629e-05 | 0.027999 | 0.09613 | 0.10986 | 0.11444 | 0.054932 | 0.032043 | 0.059509 | -0.07782 | 0.12817 | 0.10529 | 0.009155 | -0.022888 | -0.027466 | -0.032043 | -0.091553 | 0.13733 | 0 | -122.0123 | 0.18768 | 0.13275 | 0.13275 | -121.9482 | 0.045777 | -0.013733 | -122.0673 | 0.20599 | 0.086975 | 0.10071 | -122.0718 | 0.10986 | 0.17395 | 0.19226 | -122.1222 | 0.054932 | 0.050354 | 0.18311 | -122.1359
2183.0938 | 122.2687 | -0.073242 | 122.0673 | -0.13458 | 0.043564 | 0.062677 | 0.0053235 | 0.031892 | -0.0073038 | 0.032142 | -0.10803 | 0.032178 | 0.033678 | 0.045183 | -0.0040951 | 0.029281 | 0.10071 | 0.16022 | 0.13275 | 0.082397 | 0.036621 | 0.064087 | -0.07782 | 0.1236 | 0.15564 | 0.041199 | 0.004578 | -0.032043 | -0.036621 | -0.086975 | 0.13733 | -0.004578 | -122.0306 | 0.23346 | 0.15564 | 0.16022 | -121.9666 | 0.036621 | -0.013733 | -122.0627 | 0.19684 | 0.11444 | 0.12817 | -122.0993 | 0.10986 | 0.17395 | 0.20599 | -122.1451 | 0.07782 | 0.041199 | 0.22888 | -122.1542
2184.8438 | 122.3007 | -0.068665 | 122.0123 | 0.15533 | 0.042069 | 0.058618 | 0.0012647 | 0.032105 | -0.0021768 | 0.033423 | 0.059815 | 0.031323 | 0.03261 | 0.048815 | 0.0042361 | 0.027359 | 0.09613 | 0.082397 | 0.07782 | 0.050354 | 0.059509 | 0.068665 | -0.091553 | 0.10529 | 0.09613 | -0.009155 | -0.004578 | -0.009155 | -0.036621 | -0.07782 | 0.13733 | -0.022888 | -121.9528 | 0.15106 | 0.11902 | 0.14191 | -121.9162 | 0.032044 | -0.009155 | -122.0169 | 0.17395 | 0.05951 | 0.068665 | -122.0215 | 0.12817 | 0.16479 | 0.14649 | -122.1039 | 0.064087 | 0.05951 | 0.16479 | -122.0901
2186.6094 | 122.2916 | -0.07782 | 122.0352 | -0.12695 | 0.043991 | 0.061395 | 0.0068189 | 0.031251 | -0.0079446 | 0.03086 | -0.085144 | 0.031537 | 0.0356 | 0.047106 | -0.0021725 | 0.028427 | 0.10529 | 0.13275 | 0.12817 | 0.064087 | 0.036621 | 0.050354 | -0.064087 | 0.13275 | 0.16937 | 0.027466 | -0.004578 | -0.032043 | -0.027466 | -0.10529 | 0.12817 | 0.013733 | -121.9986 | 0.21057 | 0.14191 | 0.12817 | -121.9299 | 0.050354 | -0.027466 | -122.0398 | 0.21057 | 0.10529 | 0.13275 | -122.0673 | 0.11444 | 0.18311 | 0.20599 | -122.0993 | 0.073242 | 0.045777 | 0.24719 | -122.1405
2188.2969 | 122.1588 | -0.1236 | 122.0535 | 0.056152 | 0.04506 | 0.060968 | 0.00062385 | 0.031678 | 0.0025228 | 0.032355 | 0.014038 | 0.035596 | 0.034746 | 0.048815 | 0.0055179 | 0.02565 | -0.004578 | -0.050354 | -0.041199 | -0.027466 | 0.07782 | 0.018311 | -0.11902 | 0.004578 | -0.041199 | -0.14648 | 0.054932 | 0.027466 | -0.064087 | -0.13275 | 0.14191 | 0.004577 | -121.9757 | 0.073242 | 0.09613 | 0.091553 | -122.0581 | 0.059509 | -0.009155 | -121.9986 | 0.12817 | -0.022888 | -0.013733 | -122.0261 | 0.20142 | 0.11902 | 0.082397 | -122.1725 | 0.17853 | 0.15106 | 0.082397 | -122.1863
2190.0469 | 122.168 | -0.13275 | 122.0947 | 0.040894 | 0.043137 | 0.059473 | 0.0021191 | 0.031678 | 0.00038662 | 0.03321 | -0.031738 | 0.034955 | 0.034959 | 0.048815 | 0.0025271 | 0.028427 | -0.004578 | -0.041199 | -0.041199 | -0.018311 | 0.07782 | 0.018311 | -0.11444 | -0.009155 | -0.045776 | -0.15564 | 0.041199 | 0.041199 | -0.054932 | -0.1236 | 0.15106 | 0.01831 | -122.0169 | 0.091552 | 0.11444 | 0.09613 | -122.0993 | 0.077819 | 0.009155 | -122.0535 | 0.1236 | -0.022889 | -0.032044 | -122.0535 | 0.21057 | 0.12817 | 0.091552 | -122.2092 | 0.17395 | 0.17395 | 0.086975 | -122.2183
2191.7344 | 122.1817 | -0.10986 | 122.081 | 0.033264 | 0.046555 | 0.060327 | 0.0034009 | 0.034883 | -4.058e-05 | 0.036201 | 0.044556 | 0.035169 | 0.034532 | 0.049456 | 0.0016727 | 0.02864 | -0.022888 | -0.07782 | -0.050354 | -0.036621 | 0.086975 | 0.018311 | -0.11902 | 0.013733 | -0.036621 | -0.13733 | 0.027466 | 0.009155 | -0.073242 | -0.11902 | 0.12817 | -0.009156 | -121.994 | 0.032043 | 0.073242 | 0.082398 | -122.1039 | 0.036621 | -0.009156 | -122.0535 | 0.1236 | -0.027466 | -0.01831 | -122.0718 | 0.19684 | 0.086975 | 0.059509 | -122.2 | 0.13733 | 0.11902 | 0.073242 | -122.2
2193.4844 | 122.2229 | -0.10071 | 122.081 | 0.08667 | 0.040787 | 0.063745 | 0.0016919 | 0.03296 | -0.0085856 | 0.032783 | 0.12848 | 0.032392 | 0.034105 | 0.04732 | -0.00089089 | 0.03099 | 0.027466 | 0.091553 | 0.091553 | 0.022888 | 0.022888 | 0.050354 | -0.07782 | 0.082397 | 0.07782 | -0.022888 | -0.004578 | -0.018311 | -0.013733 | -0.086975 | 0.15106 | 0.022888 | -122.0581 | 0.19226 | 0.1236 | 0.10071 | -122.0535 | 0.086975 | 0.013733 | -122.0856 | 0.18311 | 0.07782 | 0.064087 | -122.0993 | 0.1236 | 0.12817 | 0.19226 | -122.1588 | 0.09613 | 0.082397 | 0.17853 | -122.168
2195.2344 | 122.1725 | -0.1236 | 122.0993 | -0.23376 | 0.04506 | 0.063318 | 0.0085279 | 0.034028 | -0.0062356 | 0.03086 | -0.15381 | 0.033673 | 0.035387 | 0.046038 | -0.00067729 | 0.027786 | 0.013733 | 0.009155 | 0.027466 | 0.009155 | 0.073242 | 0.018311 | -0.13275 | 0.013733 | 0.018311 | -0.09613 | 0.032043 | 0.018311 | -0.07782 | -0.1236 | 0.14191 | -0.009155 | -122.0261 | 0.13275 | 0.13275 | 0.14191 | -122.0856 | 0.045776 | 0 | -122.0673 | 0.13733 | 0.027466 | 0.027466 | -122.081 | 0.19684 | 0.13733 | 0.15106 | -122.2321 | 0.15564 | 0.14191 | 0.14191 | -122.2229
2197 | 122.3053 | -0.082397 | 122.0398 | -0.027771 | 0.044846 | 0.062036 | 0.0044691 | 0.03296 | -0.0064492 | 0.030006 | 0.014038 | 0.027478 | 0.035173 | 0.048815 | -0.0051633 | 0.029068 | 0.013733 | 0.073242 | 0.064087 | 0.027466 | 0.050354 | 0.054932 | -0.07782 | 0.082397 | 0.10071 | 0.022888 | -0.004578 | -0.013733 | -0.050354 | -0.09613 | 0.13733 | 0.004577 | -121.9894 | 0.15564 | 0.10986 | 0.10529 | -122.0261 | 0.032043 | -0.013733 | -122.0444 | 0.16479 | 0.10528 | 0.11902 | -122.0535 | 0.13275 | 0.09613 | 0.14648 | -122.1176 | 0.077819 | 0.068664 | 0.18311 | -122.1359
2198.7031 | 122.2321 | -0.091553 | 122.0535 | -0.18036 | 0.0457 | 0.0599 | 0.0044691 | 0.031892 | -0.0013224 | 0.033851 | -0.25299 | 0.031323 | 0.033037 | 0.049883 | 0.0012455 | 0.024154 | 0.004578 | 0 | -0.013733 | 0.004578 | 0.086975 | 0.013733 | -0.11902 | 0.041199 | 0.045776 | -0.091553 | 0.032043 | 0.018311 | -0.059509 | -0.12817 | 0.10529 | -0.027466 | -121.9666 | 0.091553 | 0.096131 | 0.1236 | -122.049 | 0.032044 | -0.036621 | -122.0215 | 0.13275 | 0 | 0.036621 | -122.0352 | 0.17853 | 0.096131 | 0.07782 | -122.1725 | 0.1236 | 0.10986 | 0.13733 | -122.1817
2200.4688 | 122.287 | -0.054932 | 122.0306 | 0.071411 | 0.041642 | 0.060541 | -0.0010851 | 0.033387 | -0.003245 | 0.033423 | 0.13611 | 0.030255 | 0.033678 | 0.049242 | 0.0023135 | 0.029281 | 0.091553 | 0.11902 | 0.10071 | 0.068665 | 0.018311 | 0.064087 | -0.068665 | 0.14648 | 0.11444 | 0.018311 | -0.018311 | -0.018311 | -0.032043 | -0.082397 | 0.11902 | -0.013733 | -122.0123 | 0.17395 | 0.1236 | 0.13733 | -121.9391 | 0.022889 | -0.027465 | -122.049 | 0.20142 | 0.073243 | 0.10071 | -122.049 | 0.073243 | 0.14649 | 0.15564 | -122.0993 | 0.036621 | 0.036621 | 0.16937 | -122.113
2202.2188 | 122.3145 | -0.073242 | 122.0398 | -0.027771 | 0.039719 | 0.062463 | 0.0036145 | 0.031678 | -0.006022 | 0.031928 | 0.021668 | 0.031751 | 0.033678 | 0.049883 | -0.0017453 | 0.028213 | 0.027466 | 0.064087 | 0.068665 | 0.032043 | 0.045776 | 0.050354 | -0.073242 | 0.09613 | 0.10986 | 0.004578 | -0.004578 | -0.013733 | -0.027466 | -0.09613 | 0.1236 | 0 | -121.994 | 0.13733 | 0.10529 | 0.10529 | -122.0123 | 0.045776 | -0.022888 | -122.0444 | 0.16937 | 0.07782 | 0.10071 | -122.0535 | 0.11902 | 0.10071 | 0.14191 | -122.113 | 0.068664 | 0.059509 | 0.18311 | -122.1359
2203.9219 | 122.1909 | -0.13733 | 122.0673 | -0.22614 | 0.044419 | 0.060327 | 0.0063917 | 0.033174 | -0.0036722 | 0.032783 | -0.21484 | 0.032605 | 0.034105 | 0.049669 | -0.00024989 | 0.025863 | 0.004578 | 0.022888 | 0.027466 | 0 | 0.07782 | 0.022888 | -0.11902 | 0.022888 | 0.022888 | -0.10986 | 0.032043 | 0.018311 | -0.073242 | -0.11444 | 0.16022 | 0.01831 | -121.9894 | 0.16022 | 0.13733 | 0.11902 | -122.0627 | 0.064087 | 0.022888 | -122.0352 | 0.16022 | 0.027466 | 0.004578 | -122.049 | 0.21515 | 0.14191 | 0.16479 | -122.1863 | 0.16937 | 0.15564 | 0.16022 | -122.1817
2205.6719 | 122.1954 | -0.11902 | 122.0993 | -0.1651 | 0.039719 | 0.063959 | 0.0023329 | 0.033387 | -0.0036722 | 0.032355 | -0.14618 | 0.03346 | 0.031541 | 0.046038 | 0.00060451 | 0.028213 | 0.07782 | 0.11902 | 0.10986 | 0.054932 | 0.059509 | 0.059509 | -0.086975 | 0.091553 | 0.1236 | -0.009155 | 0.004578 | -0.018311 | -0.036621 | -0.09613 | 0.17853 | 0.032044 | -122.0398 | 0.23804 | 0.17395 | 0.14191 | -122.0215 | 0.082398 | 0.022889 | -122.0947 | 0.21057 | 0.10986 | 0.086975 | -122.1176 | 0.17853 | 0.19684 | 0.22888 | -122.1863 | 0.1236 | 0.10071 | 0.24261 | -122.1954
2207.3594 | 122.287 | -0.07782 | 122.0535 | -0.12695 | 0.041214 | 0.062891 | 0.0040417 | 0.032105 | -0.0058084 | 0.031714 | -0.11566 | 0.031751 | 0.033464 | 0.048388 | -0.0032407 | 0.027999 | 0.10529 | 0.15564 | 0.13275 | 0.082397 | 0.041199 | 0.059509 | -0.073242 | 0.13275 | 0.13275 | 0.036621 | 0.004578 | -0.027466 | -0.027466 | -0.082397 | 0.13733 | 0.004578 | -122.0123 | 0.23346 | 0.16022 | 0.15564 | -121.9482 | 0.050354 | -0.004577 | -122.049 | 0.21057 | 0.11444 | 0.11902 | -122.081 | 0.11902 | 0.18311 | 0.21057 | -122.1268 | 0.082398 | 0.050354 | 0.21057 | -122.1359
2209.1094 | 122.2275 | -0.11444 | 122.0718 | -0.20325 | 0.046341 | 0.059473 | 0.0034009 | 0.032746 | 0.0010276 | 0.031714 | -0.22247 | 0.032819 | 0.03261 | 0.048601 | 0.00017731 | 0.027572 | 0.032043 | -0.004578 | 0.009155 | 0.013733 | 0.073242 | 0.013733 | -0.12817 | 0.045776 | 0.045776 | -0.073242 | 0.018311 | 0.009155 | -0.07782 | -0.1236 | 0.12817 | -0.013733 | -121.9986 | 0.10986 | 0.12817 | 0.14191 | -122.0398 | 0.036621 | -0.009155 | -122.0535 | 0.16022 | 0.041199 | 0.050354 | -122.0627 | 0.18768 | 0.14648 | 0.1236 | -122.2 | 0.13275 | 0.1236 | 0.16022 | -122.1954
2210.7969 | 122.1725 | -0.10529 | 122.113 | -0.050659 | 0.045273 | 0.0599 | 0.0038281 | 0.033601 | 0.0016684 | 0.03556 | -0.046997 | 0.033673 | 0.035387 | 0.050097 | 0.0018863 | 0.027145 | 0.045776 | 0.022888 | 0.009155 | 0.009155 | 0.064087 | 0.018311 | -0.11444 | 0.041199 | 0.004578 | -0.13275 | 0.036621 | 0.009155 | -0.068665 | -0.13275 | 0.1236 | -0.009155 | -122.049 | 0.12817 | 0.11444 | 0.1236 | -122.0673 | 0.036621 | -0.027465 | -122.0764 | 0.14649 | -0.027465 | 0 | -122.1039 | 0.16937 | 0.15106 | 0.11444 | -122.2275 | 0.14191 | 0.11444 | 0.10986 | -122.2458
2212.5469 | 122.2824 | -0.068665 | 122.081 | -0.14984 | 0.046128 | 0.060754 | 0.0066053 | 0.032105 | -0.006022 | 0.031928 | -0.13092 | 0.03111 | 0.035814 | 0.049669 | -0.0047361 | 0.027572 | 0.07782 | 0.16479 | 0.11902 | 0.050354 | 0.036621 | 0.050354 | -0.07782 | 0.11444 | 0.16479 | 0.027466 | -0.004578 | -0.013733 | -0.032043 | -0.091553 | 0.11902 | -0.009155 | -122.0444 | 0.23346 | 0.11902 | 0.12817 | -122.0032 | 0.036622 | -0.022888 | -122.0856 | 0.18311 | 0.096131 | 0.11902 | -122.0947 | 0.10529 | 0.14649 | 0.18768 | -122.1588 | 0.064087 | 0.054932 | 0.23346 | -122.1725
2214.25 | 122.1817 | -0.11902 | 122.1039 | -0.088806 | 0.047196 | 0.059259 | 0.0031873 | 0.034883 | 0.001882 | 0.035987 | -0.092773 | 0.034528 | 0.034105 | 0.048174 | 0.0025271 | 0.027145 | 0.059509 | 0.050354 | 0.009155 | 0.022888 | 0.054932 | 0.032043 | -0.10529 | 0.050354 | 0.032043 | -0.091553 | 0.018311 | 0.013733 | -0.059509 | -0.13733 | 0.15106 | 0.013733 | -122.049 | 0.16937 | 0.14191 | 0.12817 | -122.0444 | 0.05951 | -0.01831 | -122.0856 | 0.16937 | 0.027466 | 0.045776 | -122.0901 | 0.17395 | 0.17853 | 0.12817 | -122.2092 | 0.13733 | 0.13275 | 0.15106 | -122.2412
2216 | 122.2961 | -0.059509 | 122.0261 | 0.16296 | 0.042923 | 0.061182 | 0.00062385 | 0.033814 | -0.0023904 | 0.032996 | 0.10559 | 0.032605 | 0.034105 | 0.050097 | 0.0010317 | 0.028213 | 0.036621 | 0.050354 | 0.050354 | 0.018311 | 0.059509 | 0.036621 | -0.09613 | 0.11444 | 0.09613 | -0.013733 | -0.004578 | -0.022888 | -0.022888 | -0.09613 | 0.09613 | -0.036621 | -121.9666 | 0.10986 | 0.07782 | 0.11444 | -121.9894 | 0.036621 | -0.036621 | -122.0306 | 0.17395 | 0.045776 | 0.082397 | -122.0489 | 0.11902 | 0.09613 | 0.10986 | -122.1222 | 0.054931 | 0.036621 | 0.15564 | -122.1222
2217.6875 | 122.2961 | -0.068665 | 122.0627 | 0.071411 | 0.04506 | 0.061182 | 0.0019055 | 0.033387 | -0.0011088 | 0.032783 | 0.13611 | 0.034101 | 0.033464 | 0.047961 | 0.0014591 | 0.028427 | 0.004578 | 0.004578 | -0.004578 | -0.013733 | 0.07782 | 0.036621 | -0.11444 | 0.054932 | 0.009155 | -0.086975 | 0.018311 | 0.022888 | -0.041199 | -0.10986 | 0.10529 | -0.045776 | -121.9849 | 0.073243 | 0.054932 | 0.10071 | -122.0581 | 0.027466 | -0.041198 | -122.0444 | 0.1236 | -0.01831 | 0.022888 | -122.0398 | 0.14649 | 0.073243 | 0.064087 | -122.1771 | 0.086976 | 0.091553 | 0.07782 | -122.1725
2219.4375 | 122.1817 | -0.11902 | 122.1268 | -0.065918 | 0.044632 | 0.060114 | -1.7146e-05 | 0.032105 | 0.001882 | 0.033423 | -0.062256 | 0.033887 | 0.031541 | 0.048815 | 0.0031681 | 0.027999 | 0.041199 | 0.032043 | 0.022888 | 0.018311 | 0.068665 | 0.036621 | -0.11902 | 0.036621 | 0.022888 | -0.09613 | 0.032043 | 0.013733 | -0.064087 | -0.13275 | 0.15564 | 0 | -122.0581 | 0.15106 | 0.13733 | 0.13733 | -122.0856 | 0.054932 | -0.013732 | -122.0947 | 0.15564 | 0.022889 | 0.036621 | -122.113 | 0.18768 | 0.16022 | 0.14191 | -122.2458 | 0.15106 | 0.13275 | 0.14191 | -122.2595
2221.2031 | 122.3465 | -0.059509 | 122.049 | -0.050659 | 0.043564 | 0.060968 | 0.0044691 | 0.032533 | -0.0098672 | 0.030219 | -0.0088499 | 0.031751 | 0.034318 | 0.046679 | -0.0049497 | 0.029068 | 0.013733 | 0.091553 | 0.10071 | 0.045776 | 0.041199 | 0.050354 | -0.091553 | 0.10986 | 0.13733 | 0.027466 | 0.009155 | -0.004578 | -0.022888 | -0.11444 | 0.10986 | -0.032044 | -122.0078 | 0.15106 | 0.10528 | 0.13733 | -122.0352 | 0.036621 | -0.054932 | -122.0398 | 0.16937 | 0.086975 | 0.14191 | -122.0535 | 0.10071 | 0.073242 | 0.16022 | -122.1405 | 0.068664 | 0.054931 | 0.19684 | -122.1634
2222.8906 | 122.3328 | -0.082397 | 122.0306 | -0.027771 | 0.041214 | 0.060754 | 0.0034009 | 0.031037 | -0.0073038 | 0.030646 | 0.029297 | 0.030042 | 0.033891 | 0.047533 | -0.0045225 | 0.030136 | 0.009155 | 0.059509 | 0.068665 | 0.027466 | 0.054932 | 0.027466 | -0.09613 | 0.082397 | 0.091553 | -0.009155 | -0.004578 | -0.032043 | -0.032043 | -0.086975 | 0.10986 | -0.013733 | -121.9757 | 0.14191 | 0.10986 | 0.1236 | -122.0215 | 0.050354 | -0.004578 | -122.0352 | 0.16479 | 0.073242 | 0.07782 | -122.0627 | 0.13733 | 0.091552 | 0.15106 | -122.1268 | 0.077819 | 0.050354 | 0.17395 | -122.1176
2224.6406 | 122.3053 | -0.068665 | 122.0215 | 0.08667 | 0.046341 | 0.061395 | -1.7146e-05 | 0.033814 | 0.0014548 | 0.031501 | 0.12848 | 0.032178 | 0.031755 | 0.049242 | 0.0010317 | 0.026077 | 0.027466 | -0.004578 | -0.004578 | -0.013733 | 0.068665 | 0.036621 | -0.09613 | 0.082397 | 0.027466 | -0.050354 | 0.027466 | 0.004578 | -0.036621 | -0.082397 | 0.10529 | -0.027465 | -121.9528 | 0.064087 | 0.054932 | 0.082397 | -121.994 | 0.032044 | -0.013732 | -121.994 | 0.15106 | 0.018311 | 0.032043 | -122.0169 | 0.13733 | 0.096131 | 0.064087 | -122.1176 | 0.096131 | 0.073243 | 0.096131 | -122.1039
2226.3281 | 122.1909 | -0.11902 | 122.0856 | 0.0027468 | 0.044846 | 0.061609 | 0.00083745 | 0.031037 | 0.00017302 | 0.03556 | -0.0088499 | 0.036023 | 0.03325 | 0.049456 | 0.0016727 | 0.029281 | 0.018311 | -0.018311 | -0.027466 | -0.022888 | 0.064087 | 0.027466 | -0.12817 | -0.004578 | -0.022888 | -0.15106 | 0.027466 | 0.018311 | -0.064087 | -0.13275 | 0.14649 | -0.009155 | -122.0215 | 0.10071 | 0.096131 | 0.10529 | -122.0673 | 0.054932 | -0.013732 | -122.0581 | 0.11444 | -0.032043 | -0.018311 | -122.0673 | 0.18311 | 0.13733 | 0.091553 | -122.2137 | 0.14649 | 0.13733 | 0.096131 | -122.2183
2228.0781 | 122.2412 | -0.10529 | 122.0856 | -0.17273 | 0.046982 | 0.062891 | 0.0029737 | 0.035737 | -0.0019632 | 0.034064 | -0.19196 | 0.034741 | 0.034532 | 0.047533 | -0.00067729 | 0.029281 | 0.022888 | 0 | -0.013733 | 0.004578 | 0.068665 | 0.032043 | -0.1236 | 0.036621 | 0.041199 | -0.073242 | 0.041199 | 0.036621 | -0.059509 | -0.1236 | 0.13733 | -0.01831 | -122.0169 | 0.10529 | 0.10986 | 0.12817 | -122.0627 | 0.045777 | -0.01831 | -122.0444 | 0.14191 | 0.032044 | 0.050354 | -122.049 | 0.17395 | 0.12817 | 0.091553 | -122.2092 | 0.14649 | 0.14191 | 0.14649 | -122.2092
2229.8281 | 122.1771 | -0.13275 | 122.0993 | -0.17273 | 0.044205 | 0.064386 | 0.0046827 | 0.034242 | -0.0068766 | 0.032142 | -0.19958 | 0.033032 | 0.034959 | 0.048174 | -0.0025999 | 0.027786 | 0.068665 | 0.10071 | 0.091553 | 0.050354 | 0.022888 | 0.041199 | -0.091553 | 0.054932 | 0.10529 | -0.027466 | 0.027466 | -0.004578 | -0.050354 | -0.10071 | 0.17395 | 0.041198 | -122.0764 | 0.23346 | 0.18311 | 0.14191 | -122.0306 | 0.082397 | 0.032043 | -122.0718 | 0.18768 | 0.10529 | 0.073242 | -122.1039 | 0.15564 | 0.20142 | 0.2243 | -122.1909 | 0.16022 | 0.12817 | 0.23804 | -122.2
2231.5625 | 122.287 | -0.086975 | 122.0673 | 0.10193 | 0.043351 | 0.061823 | 0.00041005 | 0.030824 | -0.00068138 | 0.032355 | 0.059815 | 0.036664 | 0.033037 | 0.049029 | 0.0016727 | 0.029708 | 0.013733 | -0.027466 | -0.027466 | -0.022888 | 0.064087 | 0.013733 | -0.1236 | 0.041199 | -0.018311 | -0.10529 | 0.032043 | 0.027466 | -0.059509 | -0.11444 | 0.10071 | -0.036621 | -122.0032 | 0.059509 | 0.064087 | 0.10071 | -122.0535 | 0.027466 | -0.027466 | -122.0352 | 0.12817 | -0.018311 | 0.009155 | -122.0398 | 0.15106 | 0.10071 | 0.059509 | -122.1909 | 0.11902 | 0.11444 | 0.068664 | -122.1817
2233.3125 | 122.1725 | -0.11444 | 122.0901 | -0.088806 | 0.04506 | 0.0599 | 0.0046827 | 0.032533 | 0.00060022 | 0.03321 | -0.1004 | 0.034528 | 0.033037 | 0.04732 | 0.0023135 | 0.026718 | 0.073242 | 0.036621 | 0.022888 | 0.018311 | 0.054932 | 0.027466 | -0.10986 | 0.050354 | 0.036621 | -0.082397 | 0.027466 | 0.018311 | -0.054932 | -0.11444 | 0.14191 | 0.004578 | -122.0352 | 0.15106 | 0.13275 | 0.12817 | -122.0169 | 0.059509 | 0 | -122.0627 | 0.16479 | 0.032044 | 0.032044 | -122.0718 | 0.16937 | 0.18768 | 0.13733 | -122.2 | 0.14191 | 0.13275 | 0.15106 | -122.2046
2235 | 122.168 | -0.11444 | 122.1176 | -0.027771 | 0.044419 | 0.0599 | 0.0025465 | 0.033601 | -0.00025418 | 0.03556 | 0.029297 | 0.034101 | 0.034746 | 0.048174 | 0.00081811 | 0.027572 | 0.027466 | 0.004578 | 0.004578 | 0 | 0.064087 | 0.022888 | -0.10986 | -0.009155 | 0.009155 | -0.12817 | 0.027466 | 0.022888 | -0.068665 | -0.1236 | 0.13733 | 0.004578 | -122.0535 | 0.11902 | 0.11444 | 0.10986 | -122.0901 | 0.045776 | -0.009155 | -122.0901 | 0.10529 | -0.013733 | -0.004578 | -122.0947 | 0.17853 | 0.14191 | 0.11902 | -122.2275 | 0.14191 | 0.13733 | 0.1236 | -122.2412
2236.7344 | 122.3419 | -0.07782 | 122.0581 | -0.0354 | 0.040787 | 0.061182 | 0.0051099 | 0.031251 | -0.0098672 | 0.030219 | 0.036926 | 0.031537 | 0.034318 | 0.049242 | -0.0043087 | 0.030136 | 0.009155 | 0.054932 | 0.073242 | 0.027466 | 0.045776 | 0.059509 | -0.09613 | 0.082397 | 0.10071 | 0.004578 | -0.009155 | 0 | -0.041199 | -0.091553 | 0.13733 | -0.01831 | -122.0123 | 0.13275 | 0.10529 | 0.1236 | -122.0489 | 0.036621 | -0.013733 | -122.0673 | 0.16022 | 0.082398 | 0.096131 | -122.0581 | 0.1236 | 0.086975 | 0.15106 | -122.1542 | 0.068665 | 0.07782 | 0.17853 | -122.1497
2238.4375 | 122.3053 | -0.064087 | 122.0535 | -0.15747 | 0.041428 | 0.062891 | 0.0051099 | 0.033174 | -0.0068766 | 0.029151 | -0.069885 | 0.030042 | 0.033464 | 0.04732 | -0.0038815 | 0.029068 | 0.064087 | 0.12817 | 0.13733 | 0.086975 | 0.045776 | 0.054932 | -0.082397 | 0.14648 | 0.14191 | 0.054932 | -0.009155 | -0.022888 | -0.032043 | -0.086975 | 0.11902 | -0.01831 | -122.0078 | 0.19226 | 0.15106 | 0.16937 | -121.9894 | 0.032044 | -0.022888 | -122.0627 | 0.21057 | 0.11902 | 0.14191 | -122.0764 | 0.10986 | 0.12817 | 0.20142 | -122.1359 | 0.054932 | 0.041199 | 0.20599 | -122.1405
2240.1875 | 122.2458 | -0.10986 | 122.1268 | -0.1651 | 0.04506 | 0.060327 | 0.0040417 | 0.032319 | 0.00060022 | 0.032783 | -0.22247 | 0.032605 | 0.033891 | 0.049242 | -3.629e-05 | 0.026077 | 0.004578 | -0.009155 | -0.013733 | 0.009155 | 0.068665 | 0.013733 | -0.11444 | 0.027466 | 0.059509 | -0.091553 | 0.018311 | 0.032043 | -0.059509 | -0.11444 | 0.1236 | -0.004578 | -122.0581 | 0.10071 | 0.11902 | 0.1236 | -122.1222 | 0.050354 | -0.004578 | -122.1085 | 0.13733 | 0.01831 | 0.022888 | -122.0947 | 0.17853 | 0.11444 | 0.09613 | -122.2412 | 0.12817 | 0.14191 | 0.16937 | -122.2412
2241.9375 | 122.1817 | -0.13733 | 122.1085 | -0.18036 | 0.046555 | 0.060968 | 0.0059643 | 0.03531 | -0.0051676 | 0.031287 | -0.20721 | 0.029615 | 0.033891 | 0.046892 | -0.0017453 | 0.027145 | 0.045776 | 0.11902 | 0.10529 | 0.064087 | 0.041199 | 0.045776 | -0.10986 | 0.068665 | 0.11444 | -0.027466 | 0.022888 | 0 | -0.032043 | -0.12817 | 0.18311 | 0.027466 | -122.0673 | 0.25635 | 0.20142 | 0.17395 | -122.0627 | 0.10529 | 0.009155 | -122.0856 | 0.20599 | 0.10986 | 0.10071 | -122.1085 | 0.17853 | 0.18311 | 0.24262 | -122.2183 | 0.16022 | 0.13733 | 0.25177 | -122.2366
2243.6406 | 122.1771 | -0.11444 | 122.1085 | -0.073547 | 0.046982 | 0.059045 | 0.0027601 | 0.032319 | 0.0016684 | 0.035987 | -0.1004 | 0.03346 | 0.034532 | 0.049669 | 0.0029543 | 0.026077 | 0.059509 | 0.036621 | 0.036621 | 0.004578 | 0.086975 | 0.018311 | -0.10529 | 0.041199 | 0.027466 | -0.10986 | 0.036621 | 0.022888 | -0.041199 | -0.11444 | 0.13275 | 0.009155 | -122.0215 | 0.15106 | 0.11902 | 0.10986 | -122.0489 | 0.073242 | 0 | -122.0718 | 0.15564 | 0.004578 | 0.004578 | -122.0856 | 0.20142 | 0.17395 | 0.15106 | -122.2137 | 0.15106 | 0.13733 | 0.14191 | -122.2229
2245.3906 | 122.3099 | -0.073242 | 122.0581 | 0.08667 | 0.043778 | 0.058405 | 0.00019645 | 0.032746 | -0.002604 | 0.034064 | 0.14374 | 0.033887 | 0.033037 | 0.048174 | 0.0031681 | 0.028213 | -0.009155 | 0.009155 | -0.009155 | -0.036621 | 0.073242 | 0.013733 | -0.10529 | 0.054932 | 0.018311 | -0.07782 | 0.013733 | -0.009155 | -0.022888 | -0.10529 | 0.086975 | -0.032044 | -121.9849 | 0.082397 | 0.036621 | 0.068665 | -122.0673 | 0.050354 | -0.032044 | -122.0444 | 0.12817 | -0.004578 | 0.027466 | -122.0673 | 0.14648 | 0.064087 | 0.064087 | -122.1634 | 0.086975 | 0.064087 | 0.091553 | -122.1634
2247.1406 | 122.2046 | -0.13275 | 122.1085 | -0.19562 | 0.046768 | 0.062891 | 0.0070325 | 0.034455 | -0.004313 | 0.032142 | -0.23773 | 0.030469 | 0.036668 | 0.048815 | -0.0032407 | 0.02864 | -0.027466 | 0 | -0.004578 | -0.022888 | 0.086975 | 0.009155 | -0.11902 | -0.004578 | 0.009155 | -0.10986 | 0.045776 | 0.027466 | -0.068665 | -0.12817 | 0.14191 | 0.013732 | -122.0215 | 0.13275 | 0.10986 | 0.096131 | -122.1359 | 0.064086 | 0.004577 | -122.0627 | 0.12817 | 0.022888 | 0.018311 | -122.081 | 0.21973 | 0.10529 | 0.12817 | -122.2275 | 0.17853 | 0.16022 | 0.14191 | -122.2366
2248.8281 | 122.319 | -0.07782 | 122.0581 | 0.063782 | 0.043778 | 0.059259 | 0.0021191 | 0.034242 | 0.00038662 | 0.034919 | 0.11322 | 0.031537 | 0.03261 | 0.048601 | 0.0014591 | 0.029495 | -0.004578 | -0.013733 | 0 | -0.013733 | 0.073242 | 0.013733 | -0.13275 | 0.050354 | 0 | -0.086975 | 0.009155 | 0.022888 | -0.050354 | -0.11902 | 0.091553 | -0.054931 | -121.9849 | 0.064087 | 0.064087 | 0.11902 | -122.0627 | 0.027466 | -0.041199 | -122.0489 | 0.12817 | -0.009155 | 0.032044 | -122.0352 | 0.15106 | 0.073242 | 0.07782 | -122.1909 | 0.086975 | 0.10071 | 0.07782 | -122.1771
2250.5781 | 122.2092 | -0.10071 | 122.1085 | 0.048523 | 0.043991 | 0.058832 | 0.0012647 | 0.033387 | 0.00017302 | 0.032142 | 0.014038 | 0.035169 | 0.031755 | 0.049456 | 0.00039091 | 0.027145 | -0.018311 | -0.041199 | -0.022888 | -0.013733 | 0.068665 | 0.032043 | -0.1236 | -0.022888 | -0.045776 | -0.14648 | 0.041199 | 0.027466 | -0.064087 | -0.1236 | 0.13275 | -0.022888 | -122.0398 | 0.059509 | 0.086975 | 0.10986 | -122.1268 | 0.036621 | -0.022888 | -122.0673 | 0.07782 | -0.045776 | -0.022888 | -122.081 | 0.16937 | 0.082397 | 0.07782 | -122.2321 | 0.14191 | 0.12817 | 0.054932 | -122.2321
2252.2656 | 122.1817 | -0.10986 | 122.1359 | -0.073547 | 0.043778 | 0.062036 | 0.0031873 | 0.032746 | 0.00081382 | 0.036201 | -0.031738 | 0.034741 | 0.035173 | 0.047961 | 0.00039091 | 0.028213 | 0.018311 | 0.027466 | 0.004578 | 0.013733 | 0.07782 | 0.027466 | -0.10529 | 0.018311 | 0.013733 | -0.11902 | 0.022888 | 0.032043 | -0.064087 | -0.1236 | 0.13733 | 0.004577 | -122.0581 | 0.13733 | 0.1236 | 0.11902 | -122.1176 | 0.045776 | -0.013733 | -122.113 | 0.12817 | -0.009156 | 0.004577 | -122.1039 | 0.18768 | 0.12817 | 0.11444 | -122.2412 | 0.13275 | 0.14191 | 0.1236 | -122.2595
2254.0312 | 122.1863 | -0.11444 | 122.0993 | -0.096436 | 0.044846 | 0.060327 | 0.0036145 | 0.030183 | 0.00038662 | 0.035132 | -0.092773 | 0.033887 | 0.033037 | 0.050097 | 0.00081811 | 0.027572 | 0.054932 | 0.050354 | 0.032043 | 0.027466 | 0.054932 | 0.032043 | -0.11444 | 0.045776 | 0.054932 | -0.082397 | 0.027466 | 0.013733 | -0.059509 | -0.10986 | 0.14648 | 0 | -122.0444 | 0.16479 | 0.14191 | 0.14191 | -122.0444 | 0.054932 | 0.004578 | -122.0718 | 0.16022 | 0.032044 | 0.027466 | -122.0856 | 0.16937 | 0.16937 | 0.14648 | -122.2137 | 0.14191 | 0.12817 | 0.16937 | -122.2092
2255.7812 | 122.287 | -0.091553 | 122.0581 | -0.18799 | 0.044419 | 0.060968 | 0.0029737 | 0.034028 | -0.0096536 | 0.029792 | -0.10803 | 0.030469 | 0.034105 | 0.046679 | -0.0019589 | 0.032272 | 0.059509 | 0.15106 | 0.13275 | 0.073242 | 0.036621 | 0.050354 | -0.082397 | 0.091553 | 0.16022 | 0.032043 | 0 | -0.018311 | -0.032043 | -0.07782 | 0.14191 | 0.009156 | -122.0215 | 0.24261 | 0.16479 | 0.15564 | -121.9986 | 0.05951 | 0.013733 | -122.0581 | 0.18311 | 0.1236 | 0.10986 | -122.0764 | 0.12817 | 0.15106 | 0.2243 | -122.1405 | 0.091553 | 0.073242 | 0.25177 | -122.1359
2257.4688 | 122.2595 | -0.086975 | 122.0764 | 0.10193 | 0.043137 | 0.058191 | 0.0021191 | 0.031037 | -0.0017496 | 0.032996 | 0.059815 | 0.036237 | 0.033037 | 0.046252 | 0.0033817 | 0.029922 | 0 | -0.036621 | -0.027466 | -0.013733 | 0.073242 | 0.022888 | -0.12817 | 0.013733 | -0.018311 | -0.10986 | 0.045776 | 0.018311 | -0.064087 | -0.11444 | 0.10986 | -0.041199 | -122.0032 | 0.050354 | 0.073242 | 0.11444 | -122.0764 | 0.022888 | -0.027466 | -122.0306 | 0.10071 | -0.022888 | 0.004578 | -122.0581 | 0.16022 | 0.086975 | 0.059509 | -122.2046 | 0.13275 | 0.10529 | 0.068664 | -122.1909
2259.2344 | 122.2458 | -0.1236 | 122.1222 | -0.18799 | 0.045487 | 0.061823 | 0.0042555 | 0.03531 | -0.002604 | 0.031074 | -0.22247 | 0.032819 | 0.034105 | 0.048815 | -0.00046349 | 0.027145 | 0.009155 | -0.018311 | -0.018311 | 0.004578 | 0.064087 | 0.018311 | -0.15564 | 0.004578 | 0.027466 | -0.091553 | 0.041199 | 0.018311 | -0.068665 | -0.10071 | 0.14191 | -0.032044 | -122.0581 | 0.10528 | 0.12817 | 0.16022 | -122.113 | 0.054931 | 0.022888 | -122.081 | 0.12817 | 0.032043 | 0.009155 | -122.1039 | 0.18768 | 0.13275 | 0.10528 | -122.2778 | 0.16479 | 0.14191 | 0.15106 | -122.2229
2260.9375 | 122.1817 | -0.1236 | 122.1176 | -0.04303 | 0.043991 | 0.060541 | 0.0019055 | 0.033174 | -0.0013224 | 0.033851 | -0.024109 | 0.034741 | 0.03325 | 0.049883 | 0.0023135 | 0.027145 | 0.036621 | 0.013733 | 0.009155 | 0.004578 | 0.045776 | 0.041199 | -0.11902 | 0.018311 | 0.013733 | -0.1236 | 0.027466 | 0.032043 | -0.041199 | -0.11902 | 0.16479 | 0.004577 | -122.0718 | 0.13733 | 0.12817 | 0.1236 | -122.081 | 0.082397 | 0.004577 | -122.0901 | 0.14191 | 0 | -0.004577 | -122.0856 | 0.16937 | 0.16022 | 0.13275 | -122.2366 | 0.15106 | 0.15564 | 0.13733 | -122.2366
2262.6875 | 122.2092 | -0.11444 | 122.1085 | -0.21088 | 0.044205 | 0.06225 | 0.0057507 | 0.032319 | -0.0070902 | 0.03086 | -0.19196 | 0.031964 | 0.036455 | 0.048388 | -0.0043087 | 0.02864 | -0.027466 | -0.004578 | -0.004578 | -0.022888 | 0.086975 | 0.013733 | -0.14191 | -0.009155 | 0.013733 | -0.09613 | 0.041199 | 0.022888 | -0.07782 | -0.14191 | 0.12817 | -0.027466 | -122.0215 | 0.10986 | 0.091553 | 0.11902 | -122.1359 | 0.036621 | -0.027466 | -122.0673 | 0.10529 | 0.018311 | 0.045777 | -122.0856 | 0.20142 | 0.086975 | 0.10986 | -122.2504 | 0.15564 | 0.13733 | 0.12817 | -122.2504
2264.4375 | 122.1954 | -0.10986 | 122.1222 | -0.073547 | 0.044846 | 0.059259 | 0.00062385 | 0.030397 | -0.00025418 | 0.030219 | -0.085144 | 0.034741 | 0.033891 | 0.048815 | 0.0031681 | 0.029281 | 0.068665 | 0.032043 | 0.032043 | 0.004578 | 0.07782 | 0.032043 | -0.10071 | 0.032043 | 0.032043 | -0.086975 | 0.036621 | 0.036621 | -0.045776 | -0.11902 | 0.14191 | 0.009155 | -122.0444 | 0.14191 | 0.11444 | 0.10529 | -122.0535 | 0.064087 | -0.009156 | -122.0856 | 0.14191 | 0.022888 | 0.032044 | -122.0856 | 0.18768 | 0.17853 | 0.14191 | -122.2229 | 0.14648 | 0.14648 | 0.14191 | -122.2412
2266.1406 | 122.3236 | -0.073242 | 122.0993 | 0.010376 | 0.042923 | 0.063959 | 0.0036145 | 0.032319 | -0.010295 | 0.03321 | 0.075073 | 0.030255 | 0.035387 | 0.046892 | -0.0045225 | 0.029495 | 0.004578 | 0.041199 | 0.064087 | 0.041199 | 0.041199 | 0.045776 | -0.09613 | 0.054932 | 0.073242 | -0.032043 | 0.013733 | -0.009155 | -0.036621 | -0.09613 | 0.11902 | -0.022888 | -122.0581 | 0.11444 | 0.11444 | 0.13733 | -122.0947 | 0.036621 | -0.022888 | -122.0856 | 0.12817 | 0.041199 | 0.064087 | -122.1085 | 0.11444 | 0.07782 | 0.13733 | -122.1954 | 0.086975 | 0.064087 | 0.14648 | -122.1954
2267.8906 | 122.2549 | -0.11444 | 122.1222 | -0.24139 | 0.044632 | 0.062036 | 0.0063917 | 0.031678 | -0.0021768 | 0.030433 | -0.21484 | 0.031537 | 0.036455 | 0.047961 | -0.0011045 | 0.028213 | -0.022888 | -0.004578 | -0.018311 | -0.018311 | 0.068665 | 0.013733 | -0.13733 | -0.013733 | 0.022888 | -0.11902 | 0.050354 | 0.036621 | -0.064087 | -0.1236 | 0.12817 | -0.022888 | -122.0535 | 0.10986 | 0.09613 | 0.11902 | -122.1451 | 0.050354 | -0.009155 | -122.0718 | 0.10071 | -0.004578 | 0.004577 | -122.0856 | 0.18311 | 0.091553 | 0.09613 | -122.2595 | 0.16479 | 0.15106 | 0.13733 | -122.2458
2269.6406 | 122.287 | -0.07782 | 122.0627 | 0.071411 | 0.043778 | 0.062036 | 0.0044691 | 0.032319 | -0.0062356 | 0.031714 | 0.10559 | 0.031964 | 0.034532 | 0.049029 | -0.0025999 | 0.029708 | 0.045776 | 0.073242 | 0.07782 | 0.018311 | 0.036621 | 0.073242 | -0.082397 | 0.073242 | 0.059509 | -0.013733 | 0.004578 | -0.027466 | -0.032043 | -0.082397 | 0.15106 | -0.004577 | -122.0261 | 0.15106 | 0.096131 | 0.10071 | -122.0169 | 0.045777 | -0.004577 | -122.0581 | 0.15106 | 0.064087 | 0.068664 | -122.0901 | 0.11444 | 0.1236 | 0.15564 | -122.1451 | 0.082398 | 0.050354 | 0.13733 | -122.1451
2271.3281 | 122.3007 | -0.082397 | 122.0856 | 0.018005 | 0.04036 | 0.063745 | 0.0010511 | 0.030183 | -0.0062356 | 0.030433 | 0.052185 | 0.032605 | 0.03261 | 0.047747 | -0.0021725 | 0.02864 | 0.036621 | 0.050354 | 0.059509 | 0.022888 | 0.050354 | 0.073242 | -0.091553 | 0.073242 | 0.054932 | -0.022888 | 0 | 0.018311 | -0.018311 | -0.091553 | 0.15564 | -0.009156 | -122.0352 | 0.13275 | 0.10528 | 0.11444 | -122.049 | 0.064086 | -0.009156 | -122.0856 | 0.15564 | 0.059509 | 0.068665 | -122.0673 | 0.13275 | 0.11902 | 0.14191 | -122.1771 | 0.082397 | 0.10071 | 0.13733 | -122.1771
2273.0781 | 122.2 | -0.12817 | 122.1176 | -0.25665 | 0.043564 | 0.063745 | 0.0046827 | 0.033174 | -0.0045266 | 0.028724 | -0.18433 | 0.030896 | 0.033678 | 0.050951 | -0.0015317 | 0.027999 | 0.045776 | 0.059509 | 0.050354 | 0.018311 | 0.064087 | 0.018311 | -0.10986 | 0.022888 | 0.045776 | -0.086975 | 0.027466 | 0.018311 | -0.073242 | -0.11902 | 0.14649 | 0.018311 | -122.0535 | 0.18768 | 0.14649 | 0.12817 | -122.0718 | 0.054932 | 0.009155 | -122.0901 | 0.15106 | 0.041199 | 0.032044 | -122.0993 | 0.19226 | 0.17395 | 0.17853 | -122.2275 | 0.15564 | 0.14649 | 0.17395 | -122.2366
2274.8438 | 122.2504 | -0.11444 | 122.1176 | -0.23376 | 0.044205 | 0.063104 | 0.0051099 | 0.032746 | -0.0034586 | 0.031714 | -0.25299 | 0.032819 | 0.034105 | 0.050097 | -0.00046349 | 0.027145 | -0.004578 | -0.022888 | -0.032043 | -0.022888 | 0.073242 | 0.004578 | -0.12817 | 0.004578 | -0.004578 | -0.1236 | 0.050354 | 0.022888 | -0.082397 | -0.11444 | 0.11902 | -0.013733 | -122.0444 | 0.091553 | 0.091553 | 0.10529 | -122.1222 | 0.032044 | 0 | -122.0673 | 0.11902 | -0.009155 | -0.009155 | -122.0947 | 0.18768 | 0.10986 | 0.082398 | -122.2458 | 0.16479 | 0.13733 | 0.10986 | -122.2321
2276.6094 | 122.2 | -0.13733 | 122.1405 | -0.25665 | 0.043351 | 0.064386 | 0.0040417 | 0.03296 | -0.0034586 | 0.031074 | -0.1767 | 0.034101 | 0.032823 | 0.051806 | 0.00060451 | 0.029281 | 0.018311 | 0.013733 | -0.004578 | -0.004578 | 0.059509 | 0.036621 | -0.10529 | 0.013733 | 0.009155 | -0.10071 | 0.036621 | 0.022888 | -0.068665 | -0.11902 | 0.17395 | 0.032043 | -122.081 | 0.15106 | 0.13275 | 0.10071 | -122.1222 | 0.068664 | 0.01831 | -122.1039 | 0.15106 | 0.036621 | 0.018311 | -122.1176 | 0.19684 | 0.15564 | 0.13275 | -122.2458 | 0.17395 | 0.16022 | 0.14648 | -122.2595
2278.375 | 122.2961 | -0.10071 | 122.081 | 0.14008 | 0.041428 | 0.063104 | 0.0025465 | 0.032533 | -0.0051676 | 0.032783 | 0.12085 | 0.032605 | 0.031114 | 0.050738 | -0.00089089 | 0.029281 | 0.07782 | 0.13275 | 0.11902 | 0.064087 | 0.032043 | 0.064087 | -0.064087 | 0.12817 | 0.10529 | 0.013733 | -0.036621 | -0.022888 | -0.018311 | -0.07782 | 0.1648 | 0.036621 | -122.049 | 0.23346 | 0.1648 | 0.12817 | -122.0032 | 0.082397 | 0.022888 | -122.1176 | 0.22888 | 0.11444 | 0.091553 | -122.1039 | 0.13275 | 0.17853 | 0.21973 | -122.1451 | 0.064087 | 0.07782 | 0.20599 | -122.1588
2280.1406 | 122.2778 | -0.086975 | 122.0718 | 0.12482 | 0.044205 | 0.060754 | 0.0038281 | 0.032533 | -0.0040994 | 0.031501 | 0.10559 | 0.030683 | 0.032182 | 0.048388 | -0.0021725 | 0.030349 | 0.091553 | 0.1236 | 0.11444 | 0.054932 | 0.032043 | 0.054932 | -0.07782 | 0.13275 | 0.10071 | 0 | 0.009155 | -0.018311 | -0.041199 | -0.082397 | 0.14191 | 0.009155 | -122.0398 | 0.21057 | 0.14191 | 0.13275 | -121.9803 | 0.045776 | 0.004578 | -122.0627 | 0.21973 | 0.086975 | 0.082397 | -122.0901 | 0.11902 | 0.17853 | 0.20142 | -122.1497 | 0.09613 | 0.068664 | 0.18768 | -122.1542
2281.8281 | 122.3328 | -0.073242 | 122.0901 | 0.14771 | 0.043564 | 0.062677 | 0.0012647 | 0.034242 | -0.00068138 | 0.035773 | 0.097962 | 0.03581 | 0.031328 | 0.050951 | 0.0035953 | 0.030349 | 0.086975 | 0.073242 | 0.073242 | 0.050354 | 0.045776 | 0.054932 | -0.10071 | 0.12817 | 0.091553 | -0.009155 | -0.018311 | -0.013733 | -0.022888 | -0.082397 | 0.12817 | -0.027466 | -122.0444 | 0.14648 | 0.1236 | 0.15106 | -122.0032 | 0.050354 | -0.009155 | -122.1085 | 0.20142 | 0.064087 | 0.073242 | -122.1039 | 0.11902 | 0.16022 | 0.14648 | -122.1909 | 0.054931 | 0.059509 | 0.16479 | -122.1725
2283.5781 | 122.3602 | -0.059509 | 122.0627 | -0.04303 | 0.041855 | 0.063104 | 0.0044691 | 0.029756 | -0.0064492 | 0.031714 | -0.0088499 | 0.033032 | 0.033891 | 0.050097 | -3.629e-05 | 0.028854 | 0.050354 | 0.07782 | 0.09613 | 0.036621 | 0.050354 | 0.041199 | -0.09613 | 0.10529 | 0.1236 | 0.009155 | 0.009155 | -0.018311 | -0.045776 | -0.10529 | 0.10071 | -0.036621 | -122.0123 | 0.13733 | 0.09613 | 0.13275 | -122.0123 | 0.013733 | -0.045777 | -122.0535 | 0.16479 | 0.068664 | 0.11444 | -122.081 | 0.10986 | 0.10986 | 0.15564 | -122.1588 | 0.068664 | 0.041198 | 0.1831 | -122.168
2285.3281 | 122.3419 | -0.07782 | 122.081 | 0.10193 | 0.043564 | 0.062036 | -0.00044435 | 0.034455 | -0.00068138 | 0.034492 | 0.11322 | 0.034101 | 0.029192 | 0.052233 | 0.0044497 | 0.028213 | 0.11902 | 0.10071 | 0.10071 | 0.073242 | 0.022888 | 0.073242 | -0.07782 | 0.13733 | 0.10071 | 0 | -0.004578 | -0.018311 | -0.022888 | -0.086975 | 0.15106 | 0 | -122.0581 | 0.17853 | 0.15106 | 0.15106 | -121.962 | 0.054932 | -0.009155 | -122.0856 | 0.21515 | 0.07782 | 0.086975 | -122.0993 | 0.10071 | 0.19684 | 0.17853 | -122.1588 | 0.073242 | 0.059509 | 0.17853 | -122.168
2287.0781 | 122.3419 | -0.10071 | 122.0856 | -0.0048827 | 0.039933 | 0.062891 | 0.0046827 | 0.033387 | -0.0055948 | 0.029365 | 0.036926 | 0.034101 | 0.030901 | 0.051806 | -0.0013181 | 0.030136 | 0.036621 | 0.045776 | 0.054932 | 0.036621 | 0.054932 | 0.036621 | -0.09613 | 0.082397 | 0.068665 | -0.022888 | -0.004578 | -0.009155 | -0.041199 | -0.086975 | 0.13733 | 0.004578 | -122.0306 | 0.14648 | 0.13733 | 0.13275 | -122.049 | 0.059509 | 0.013733 | -122.0901 | 0.18311 | 0.07782 | 0.064087 | -122.0947 | 0.15564 | 0.13733 | 0.15564 | -122.1817 | 0.09613 | 0.091553 | 0.16937 | -122.1725
2288.8438 | 122.2275 | -0.11444 | 122.113 | -0.081177 | 0.044419 | 0.06225 | 0.00041005 | 0.033387 | 0.0029502 | 0.032569 | -0.16144 | 0.033246 | 0.031541 | 0.050951 | 0.0014591 | 0.027999 | 0.09613 | 0.041199 | 0.022888 | 0.022888 | 0.064087 | 0.027466 | -0.10529 | 0.082397 | 0.054932 | -0.07782 | 0.032043 | 0.022888 | -0.050354 | -0.11902 | 0.14191 | 0.009155 | -122.049 | 0.15564 | 0.13733 | 0.12817 | -122.0169 | 0.064087 | -0.004578 | -122.081 | 0.19684 | 0.036621 | 0.041199 | -122.0901 | 0.17853 | 0.21057 | 0.13733 | -122.2183 | 0.14648 | 0.13733 | 0.16937 | -122.2321
2290.5312 | 122.2275 | -0.10986 | 122.1268 | -0.11169 | 0.043991 | 0.061823 | 0.0012647 | 0.032533 | 0.00017302 | 0.032355 | -0.14618 | 0.03581 | 0.028764 | 0.051378 | 0.0027407 | 0.028854 | 0.059509 | 0.050354 | 0.036621 | 0.018311 | 0.073242 | 0.022888 | -0.11444 | 0.07782 | 0.07782 | -0.068665 | 0.022888 | 0 | -0.041199 | -0.10529 | 0.13275 | -0.004578 | -122.0535 | 0.16022 | 0.12817 | 0.13275 | -122.0673 | 0.068664 | 0.004577 | -122.1039 | 0.18768 | 0.041198 | 0.036621 | -122.1268 | 0.18311 | 0.16937 | 0.14648 | -122.2412 | 0.13275 | 0.10986 | 0.18768 | -122.2321
2292.2812 | 122.319 | -0.064087 | 122.081 | -0.12695 | 0.041642 | 0.063318 | 0.0038281 | 0.03296 | -0.0096536 | 0.033423 | -0.069885 | 0.031323 | 0.029832 | 0.051165 | -0.0025999 | 0.033126 | 0.086975 | 0.13275 | 0.11444 | 0.068665 | 0.054932 | 0.050354 | -0.082397 | 0.14648 | 0.15106 | 0.036621 | -0.018311 | -0.004578 | -0.013733 | -0.064087 | 0.11444 | -0.01831 | -122.0261 | 0.19684 | 0.13275 | 0.15106 | -121.994 | 0.050354 | 0 | -122.0993 | 0.21057 | 0.10071 | 0.10071 | -122.0856 | 0.11902 | 0.15106 | 0.17853 | -122.1634 | 0.045776 | 0.059509 | 0.21515 | -122.1451
2294.0312 | 122.3145 | -0.086975 | 122.0901 | -0.1651 | 0.043351 | 0.062463 | 0.0040417 | 0.03296 | -0.0073038 | 0.03086 | -0.14618 | 0.032605 | 0.03261 | 0.051806 | -0.0023861 | 0.02864 | 0.10986 | 0.14648 | 0.11902 | 0.073242 | 0.032043 | 0.045776 | -0.068665 | 0.11444 | 0.16479 | 0.022888 | -0.009155 | -0.022888 | -0.022888 | -0.091553 | 0.13275 | 0.01831 | -122.0581 | 0.23346 | 0.16022 | 0.14191 | -121.9803 | 0.064087 | -0.004578 | -122.0993 | 0.20142 | 0.10986 | 0.11444 | -122.113 | 0.11902 | 0.19684 | 0.20599 | -122.1588 | 0.07782 | 0.064087 | 0.25177 | -122.1817
2295.7188 | 122.2229 | -0.12817 | 122.1085 | -0.24139 | 0.043991 | 0.062677 | 0.0029737 | 0.034455 | -0.0040994 | 0.03086 | -0.22247 | 0.032178 | 0.029832 | 0.051378 | -0.0021725 | 0.029922 | 0.07782 | 0.086975 | 0.059509 | 0.045776 | 0.041199 | 0.022888 | -0.11444 | 0.041199 | 0.059509 | -0.082397 | 0.018311 | 0.009155 | -0.068665 | -0.11444 | 0.15106 | 0.013733 | -122.0673 | 0.21515 | 0.17395 | 0.16022 | -122.0306 | 0.059509 | 0.013733 | -122.0901 | 0.16937 | 0.045777 | 0.032044 | -122.0993 | 0.16937 | 0.20599 | 0.18768 | -122.2229 | 0.14649 | 0.13733 | 0.18768 | -122.2229
2297.4688 | 122.2229 | -0.1236 | 122.1039 | 0.079041 | 0.044419 | 0.060114 | -0.0023669 | 0.033387 | 0.0025228 | 0.034705 | -0.031738 | 0.03581 | 0.030901 | 0.053087 | 0.0031681 | 0.027145 | 0.009155 | -0.036621 | -0.036621 | -0.022888 | 0.07782 | 0.018311 | -0.1236 | 0.004578 | -0.032043 | -0.15564 | 0.041199 | 0.009155 | -0.073242 | -0.14191 | 0.14191 | 0 | -122.0261 | 0.086975 | 0.10071 | 0.10071 | -122.0947 | 0.050354 | -0.018311 | -122.0627 | 0.12817 | -0.032044 | -0.013733 | -122.0947 | 0.20142 | 0.13275 | 0.086975 | -122.2275 | 0.16479 | 0.13275 | 0.091553 | -122.2458
2299.2344 | 122.2961 | -0.07782 | 122.1039 | 0.10956 | 0.043778 | 0.061823 | 0.00062385 | 0.033387 | -0.0036722 | 0.032142 | 0.12085 | 0.03346 | 0.030901 | 0.051806 | -3.629e-05 | 0.029281 | 0.09613 | 0.11902 | 0.11444 | 0.041199 | 0.045776 | 0.054932 | -0.082397 | 0.1236 | 0.10529 | 0.004578 | -0.013733 | -0.022888 | -0.018311 | -0.082397 | 0.13275 | -0.004577 | -122.0581 | 0.19684 | 0.11902 | 0.1236 | -122.0078 | 0.059509 | -0.004577 | -122.1176 | 0.20142 | 0.082398 | 0.086975 | -122.1268 | 0.1236 | 0.17395 | 0.19226 | -122.1863 | 0.064087 | 0.054932 | 0.18311 | -122.1863
2300.9375 | 122.3145 | -0.09613 | 122.081 | 0.10956 | 0.046555 | 0.063318 | 0.00019645 | 0.03296 | -0.0011088 | 0.035132 | 0.036926 | 0.035382 | 0.031755 | 0.052233 | 0.0020999 | 0.029281 | 0.022888 | -0.027466 | -0.036621 | -0.013733 | 0.082397 | 0.013733 | -0.10986 | 0.032043 | -0.018311 | -0.11444 | 0.036621 | 0.004578 | -0.073242 | -0.1236 | 0.10986 | -0.013733 | -121.9986 | 0.068664 | 0.082397 | 0.09613 | -122.0581 | 0.022888 | -0.027466 | -122.0444 | 0.12817 | -0.018311 | 0.009155 | -122.0764 | 0.17853 | 0.11902 | 0.059509 | -122.1909 | 0.13275 | 0.10071 | 0.077819 | -122.2046
2302.6875 | 122.2092 | -0.1236 | 122.1176 | -0.020142 | 0.04506 | 0.059045 | 0.0021191 | 0.029756 | 0.00060022 | 0.033637 | 0.014038 | 0.036878 | 0.031969 | 0.052019 | 0.0038089 | 0.027145 | 0.036621 | -0.004578 | 0 | -0.009155 | 0.068665 | 0.032043 | -0.10986 | 0.013733 | -0.009155 | -0.12817 | 0.032043 | 0.004578 | -0.041199 | -0.13275 | 0.15564 | 0.013733 | -122.049 | 0.11902 | 0.11444 | 0.10071 | -122.081 | 0.082397 | -0.009155 | -122.0856 | 0.13733 | -0.004578 | 0.004577 | -122.113 | 0.19226 | 0.16022 | 0.1236 | -122.2275 | 0.15564 | 0.12817 | 0.11444 | -122.2504
2304.4531 | 122.2092 | -0.13275 | 122.1268 | 0.08667 | 0.046768 | 0.061182 | 0.00041005 | 0.034455 | -0.0011088 | 0.035773 | -0.0012209 | 0.034528 | 0.030901 | 0.052874 | 0.0042361 | 0.030777 | -0.009155 | -0.013733 | -0.032043 | -0.018311 | 0.073242 | 0.018311 | -0.10071 | -0.013733 | -0.018311 | -0.15106 | 0.041199 | 0.032043 | -0.086975 | -0.12817 | 0.15106 | 0.032043 | -122.0535 | 0.11902 | 0.11444 | 0.082397 | -122.1359 | 0.045776 | 0.004577 | -122.0856 | 0.11902 | -0.018311 | -0.022888 | -122.0947 | 0.20599 | 0.1236 | 0.10071 | -122.2275 | 0.17395 | 0.16479 | 0.11444 | -122.2549
2306.2031 | 122.2275 | -0.1236 | 122.1313 | 0.048523 | 0.046982 | 0.062677 | 0.0016919 | 0.032319 | -0.0011088 | 0.034278 | 0.0064086 | 0.032605 | 0.032396 | 0.050097 | 0.0023135 | 0.030349 | -0.013733 | -0.045776 | -0.027466 | -0.032043 | 0.059509 | 0.009155 | -0.1236 | -0.022888 | -0.022888 | -0.14191 | 0.041199 | 0.018311 | -0.07782 | -0.1236 | 0.13275 | 0 | -122.0718 | 0.07782 | 0.091553 | 0.091553 | -122.1451 | 0.045776 | 0 | -122.0901 | 0.10071 | -0.018311 | -0.018311 | -122.113 | 0.1831 | 0.10986 | 0.09613 | -122.2549 | 0.16479 | 0.14191 | 0.10071 | -122.2549
2307.9531 | 122.2275 | -0.12817 | 122.1313 | -0.19562 | 0.04271 | 0.061609 | 0.0057507 | 0.033174 | -0.006022 | 0.03086 | -0.19196 | 0.03111 | 0.03261 | 0.052447 | -0.0013181 | 0.029922 | -0.027466 | 0.013733 | 0.009155 | -0.009155 | 0.064087 | 0.018311 | -0.12817 | 0 | 0.018311 | -0.082397 | 0.032043 | 0.018311 | -0.082397 | -0.13733 | 0.14649 | 0 | -122.0673 | 0.14191 | 0.11902 | 0.11902 | -122.1588 | 0.045777 | -0.009155 | -122.0993 | 0.12817 | 0.045777 | 0.054932 | -122.113 | 0.19226 | 0.10071 | 0.13733 | -122.2595 | 0.16022 | 0.14649 | 0.14649 | -122.2687
2309.6406 | 122.2504 | -0.091553 | 122.1268 | -0.19562 | 0.042496 | 0.062463 | 0.0051099 | 0.03296 | -0.008372 | 0.032355 | -0.1004 | 0.031537 | 0.033464 | 0.05031 | -0.0034543 | 0.032058 | 0.054932 | 0.13275 | 0.10529 | 0.059509 | 0.032043 | 0.050354 | -0.064087 | 0.10071 | 0.16022 | 0.013733 | -0.004578 | -0.018311 | -0.032043 | -0.091553 | 0.14191 | 0.027466 | -122.0947 | 0.2243 | 0.15106 | 0.1236 | -122.0718 | 0.05951 | 0 | -122.1313 | 0.19226 | 0.10529 | 0.10529 | -122.1451 | 0.1236 | 0.14649 | 0.19684 | -122.1909 | 0.086975 | 0.073242 | 0.25177 | -122.2183
2311.3906 | 122.3373 | -0.068665 | 122.0718 | 0.08667 | 0.043564 | 0.060968 | 0.0019055 | 0.03296 | -0.0028178 | 0.03321 | 0.097962 | 0.033032 | 0.034318 | 0.053942 | 0.0031681 | 0.029281 | -0.004578 | -0.022888 | -0.018311 | 0 | 0.073242 | 0.022888 | -0.09613 | 0.041199 | 0.004578 | -0.086975 | 0.018311 | 0.013733 | -0.059509 | -0.10986 | 0.091553 | -0.027465 | -121.9986 | 0.045777 | 0.068665 | 0.09613 | -122.0764 | 0.009156 | -0.041198 | -122.0535 | 0.10986 | -0.01831 | 0.022888 | -122.0581 | 0.14191 | 0.064087 | 0.050354 | -122.168 | 0.086976 | 0.082398 | 0.073243 | -122.1817
2313.1406 | 122.2595 | -0.09613 | 122.1313 | -0.19562 | 0.044205 | 0.060114 | 0.0027601 | 0.033601 | -0.0028178 | 0.031714 | -0.18433 | 0.03645 | 0.031114 | 0.049669 | 0.00039091 | 0.029708 | -0.018311 | -0.018311 | -0.022888 | 0 | 0.073242 | 0.004578 | -0.11444 | 0.013733 | 0.013733 | -0.09613 | 0.041199 | 0.013733 | -0.068665 | -0.11902 | 0.10071 | -0.018311 | -122.0581 | 0.077819 | 0.09613 | 0.11444 | -122.1497 | 0.027465 | -0.022889 | -122.0901 | 0.10986 | 0 | 0.022889 | -122.1176 | 0.16937 | 0.077819 | 0.073242 | -122.2458 | 0.13733 | 0.10986 | 0.10986 | -122.2504
2314.8438 | 122.2229 | -0.1236 | 122.1268 | -0.088806 | 0.045273 | 0.060114 | -0.0010851 | 0.03531 | -0.00068138 | 0.034278 | -0.092773 | 0.034314 | 0.030473 | 0.053087 | 0.0020999 | 0.029708 | 0.073242 | 0.054932 | 0.027466 | 0.036621 | 0.073242 | 0.027466 | -0.1236 | 0.059509 | 0.064087 | -0.073242 | 0.009155 | 0.004578 | -0.054932 | -0.11444 | 0.15106 | 0 | -122.0535 | 0.17853 | 0.16022 | 0.16022 | -122.0535 | 0.068664 | 0.009155 | -122.1176 | 0.1831 | 0.050354 | 0.041199 | -122.1222 | 0.19684 | 0.19684 | 0.15106 | -122.2504 | 0.13275 | 0.12817 | 0.18768 | -122.2412
2316.5938 | 122.3557 | -0.073242 | 122.0718 | -0.027771 | 0.041855 | 0.063318 | 0.0023329 | 0.031892 | -0.010508 | 0.031714 | 0.036926 | 0.031751 | 0.034105 | 0.050738 | -0.0051633 | 0.031845 | 0.013733 | 0.054932 | 0.07782 | 0.022888 | 0.041199 | 0.050354 | -0.086975 | 0.086975 | 0.10529 | 0.004578 | -0.009155 | -0.013733 | -0.032043 | -0.086975 | 0.1236 | -0.013733 | -122.0306 | 0.12817 | 0.09613 | 0.10986 | -122.0581 | 0.041199 | -0.013733 | -122.081 | 0.16022 | 0.07782 | 0.091553 | -122.0856 | 0.11444 | 0.086975 | 0.15106 | -122.1588 | 0.064087 | 0.059509 | 0.17853 | -122.1588
2318.3438 | 122.2275 | -0.14191 | 122.1313 | -0.1651 | 0.046768 | 0.062463 | 0.0038281 | 0.033814 | -0.0023904 | 0.031287 | -0.20721 | 0.031537 | 0.033891 | 0.053301 | -0.0017453 | 0.02864 | 0 | -0.018311 | 0 | -0.018311 | 0.073242 | 0.022888 | -0.1236 | -0.004578 | 0.022888 | -0.10986 | 0.041199 | 0.041199 | -0.068665 | -0.11902 | 0.16479 | 0.018311 | -122.0581 | 0.1236 | 0.1236 | 0.10528 | -122.1313 | 0.073242 | 0.022888 | -122.0901 | 0.13733 | 0.032044 | 0.009156 | -122.0901 | 0.21515 | 0.14191 | 0.14191 | -122.2549 | 0.18311 | 0.18311 | 0.16479 | -122.2504
2320.1094 | 122.2275 | -0.10529 | 122.1176 | 0.033264 | 0.047623 | 0.060327 | 0.0036145 | 0.031037 | 0.0010276 | 0.032569 | 0.052185 | 0.034528 | 0.034318 | 0.052874 | 0.0023135 | 0.030136 | -0.004578 | -0.059509 | -0.041199 | -0.013733 | 0.073242 | 0.027466 | -0.12817 | -0.004578 | -0.050354 | -0.14648 | 0.036621 | 0.018311 | -0.064087 | -0.13275 | 0.13275 | -0.022888 | -122.0444 | 0.045777 | 0.091553 | 0.11444 | -122.1222 | 0.041199 | -0.027465 | -122.081 | 0.10071 | -0.041198 | -0.013733 | -122.0993 | 0.17853 | 0.10071 | 0.064087 | -122.2458 | 0.14191 | 0.1236 | 0.054932 | -122.2504
2321.8125 | 122.2687 | -0.11444 | 122.1176 | -0.18036 | 0.044632 | 0.0599 | 0.00062385 | 0.032533 | -0.0019632 | 0.032569 | -0.1767 | 0.031964 | 0.032823 | 0.051378 | 0.00039091 | 0.027145 | 0.004578 | -0.004578 | -0.013733 | 0.013733 | 0.091553 | 0.022888 | -0.12817 | 0.041199 | 0.054932 | -0.068665 | 0.041199 | 0.009155 | -0.054932 | -0.13275 | 0.13733 | -0.013733 | -122.0261 | 0.10986 | 0.12817 | 0.14191 | -122.113 | 0.059509 | -0.01831 | -122.0764 | 0.15564 | 0.045776 | 0.064086 | -122.1085 | 0.20599 | 0.11902 | 0.10071 | -122.2458 | 0.15564 | 0.1236 | 0.16937 | -122.2504
2323.5625 | 122.2275 | -0.11902 | 122.1542 | -0.21851 | 0.044632 | 0.061182 | 0.0083143 | 0.031037 | -0.0073038 | 0.032783 | -0.15381 | 0.03111 | 0.034959 | 0.052233 | -0.0019589 | 0.029281 | 0.032043 | 0.086975 | 0.082397 | 0.041199 | 0.041199 | 0.032043 | -0.091553 | 0.054932 | 0.073242 | -0.054932 | 0.018311 | 0.009155 | -0.041199 | -0.11444 | 0.15106 | 0.027466 | -122.113 | 0.20599 | 0.16022 | 0.13275 | -122.1222 | 0.07782 | 0.004578 | -122.1359 | 0.17395 | 0.064087 | 0.059509 | -122.1451 | 0.16022 | 0.15106 | 0.20142 | -122.2458 | 0.13733 | 0.12817 | 0.19226 | -122.2687
2325.2656 | 122.3557 | -0.068665 | 122.0856 | 0.08667 | 0.043778 | 0.061395 | -0.0030077 | 0.030183 | -0.0021768 | 0.031074 | 0.14374 | 0.034528 | 0.032182 | 0.051592 | 0.0027407 | 0.029281 | 0.027466 | 0.004578 | 0.004578 | -0.009155 | 0.068665 | 0.032043 | -0.10529 | 0.064087 | 0.041199 | -0.054932 | 0.013733 | -0.004578 | -0.041199 | -0.09613 | 0.10071 | -0.036621 | -122.0169 | 0.073243 | 0.05951 | 0.096131 | -122.0581 | 0.027466 | -0.027465 | -122.0718 | 0.13275 | 0.013733 | 0.041198 | -122.0901 | 0.13733 | 0.096131 | 0.073243 | -122.1909 | 0.082398 | 0.064087 | 0.10986 | -122.1817
2327.0156 | 122.2733 | -0.1236 | 122.1405 | -0.19562 | 0.046341 | 0.061395 | 0.0048963 | 0.032319 | -0.0021768 | 0.031714 | -0.19196 | 0.03346 | 0.034105 | 0.053515 | -3.629e-05 | 0.027786 | 0 | -0.004578 | -0.013733 | 0.004578 | 0.07782 | 0.004578 | -0.13275 | 0.018311 | 0.032043 | -0.10529 | 0.041199 | 0.027466 | -0.073242 | -0.1236 | 0.12817 | -0.009155 | -122.0627 | 0.11902 | 0.12817 | 0.13733 | -122.1405 | 0.050354 | 0 | -122.0993 | 0.14191 | 0.01831 | 0.01831 | -122.113 | 0.20142 | 0.1236 | 0.10986 | -122.2733 | 0.16479 | 0.15106 | 0.15564 | -122.2641
2328.7812 | 122.2275 | -0.12817 | 122.1588 | -0.14221 | 0.047623 | 0.062677 | 0.0051099 | 0.032746 | -0.0036722 | 0.03086 | -0.19958 | 0.033246 | 0.035387 | 0.051806 | -0.0017453 | 0.027786 | -0.032043 | 0.022888 | -0.004578 | -0.009155 | 0.059509 | 0.018311 | -0.12817 | -0.004578 | 0.013733 | -0.091553 | 0.064087 | 0.036621 | -0.059509 | -0.13275 | 0.14649 | 0 | -122.0993 | 0.15106 | 0.11902 | 0.11902 | -122.1909 | 0.068665 | -0.004577 | -122.0947 | 0.1236 | 0.036621 | 0.041198 | -122.1222 | 0.18768 | 0.096131 | 0.1236 | -122.287 | 0.19226 | 0.1648 | 0.14191 | -122.2916
2330.5312 | 122.2641 | -0.1236 | 122.1451 | -0.18036 | 0.044205 | 0.062463 | 0.0040417 | 0.031892 | 0.00017302 | 0.032996 | -0.18433 | 0.033246 | 0.031969 | 0.052019 | -3.629e-05 | 0.029495 | -0.013733 | -0.018311 | -0.027466 | 0.004578 | 0.082397 | 0.032043 | -0.11902 | 0.013733 | 0.032043 | -0.10071 | 0.032043 | 0.022888 | -0.064087 | -0.11902 | 0.15564 | 0.004577 | -122.0627 | 0.10528 | 0.12817 | 0.1236 | -122.1588 | 0.059509 | 0.004577 | -122.113 | 0.13733 | 0.022888 | 0.018311 | -122.1222 | 0.20599 | 0.10986 | 0.09613 | -122.2641 | 0.15564 | 0.14648 | 0.15564 | -122.2641
2332.2812 | 122.3007 | -0.082397 | 122.1085 | 0.048523 | 0.041214 | 0.061823 | 0.0040417 | 0.031465 | -0.0087992 | 0.031287 | 0.097962 | 0.031537 | 0.0356 | 0.050738 | -0.00089089 | 0.031631 | 0.022888 | 0.091553 | 0.068665 | 0.018311 | 0.036621 | 0.064087 | -0.07782 | 0.082397 | 0.086975 | -0.022888 | 0.009155 | -0.009155 | -0.022888 | -0.09613 | 0.14648 | 0.004577 | -122.0718 | 0.17395 | 0.10071 | 0.096131 | -122.0856 | 0.059509 | -0.013733 | -122.0993 | 0.16479 | 0.059509 | 0.073242 | -122.1176 | 0.11902 | 0.10528 | 0.15106 | -122.1863 | 0.091552 | 0.073242 | 0.16937 | -122.2046
2333.9688 | 122.3053 | -0.064087 | 122.113 | 0.094299 | 0.039933 | 0.06225 | -0.0019397 | 0.033174 | -0.0068766 | 0.032783 | 0.12085 | 0.035382 | 0.028764 | 0.053515 | -0.00046349 | 0.028213 | 0.07782 | 0.13275 | 0.11444 | 0.050354 | 0.045776 | 0.050354 | -0.09613 | 0.12817 | 0.10071 | 0.022888 | 0 | -0.018311 | -0.013733 | -0.086975 | 0.11444 | -0.032043 | -122.0673 | 0.19684 | 0.11444 | 0.14648 | -122.0352 | 0.050354 | -0.022888 | -122.113 | 0.19226 | 0.086975 | 0.10986 | -122.1313 | 0.10986 | 0.14191 | 0.17853 | -122.2092 | 0.064087 | 0.045776 | 0.1648 | -122.2
2335.7344 | 122.2458 | -0.12817 | 122.1588 | -0.18036 | 0.041428 | 0.061823 | 0.0019055 | 0.033387 | -0.0055948 | 0.030646 | -0.1767 | 0.034528 | 0.033037 | 0.050524 | 0.00017731 | 0.028854 | 0.064087 | 0.10986 | 0.11444 | 0.064087 | 0.036621 | 0.050354 | -0.086975 | 0.086975 | 0.12817 | -0.013733 | 0.018311 | 0 | -0.041199 | -0.091553 | 0.17853 | 0.041199 | -122.1222 | 0.23804 | 0.19226 | 0.15106 | -122.0947 | 0.086975 | 0.036621 | -122.1405 | 0.21515 | 0.11444 | 0.07782 | -122.1588 | 0.1648 | 0.19226 | 0.24262 | -122.2458 | 0.14649 | 0.12817 | 0.25635 | -122.2504
2337.4844 | 122.2961 | -0.09613 | 122.1085 | 0.048523 | 0.043137 | 0.063745 | 0.0021191 | 0.032746 | -0.007731 | 0.031074 | 0.075073 | 0.031964 | 0.033464 | 0.049456 | -0.00089089 | 0.031204 | 0.045776 | 0.073242 | 0.07782 | 0.027466 | 0.050354 | 0.050354 | -0.07782 | 0.091553 | 0.07782 | -0.022888 | -0.013733 | -0.004578 | -0.022888 | -0.082397 | 0.14648 | 0.01831 | -122.0581 | 0.16937 | 0.1236 | 0.10529 | -122.0627 | 0.073242 | 0.013733 | -122.1222 | 0.18768 | 0.073242 | 0.059509 | -122.113 | 0.14648 | 0.14191 | 0.17395 | -122.1863 | 0.082397 | 0.091552 | 0.17395 | -122.1909
2339.2344 | 122.2412 | -0.1236 | 122.1405 | -0.088806 | 0.043351 | 0.061182 | -0.0019397 | 0.034242 | 0.0023092 | 0.033637 | -0.14618 | 0.033887 | 0.03026 | 0.051165 | 0.0053043 | 0.027999 | 0.086975 | 0.022888 | 0.022888 | 0.022888 | 0.082397 | 0.036621 | -0.09613 | 0.07782 | 0.036621 | -0.07782 | 0.009155 | 0.018311 | -0.059509 | -0.11902 | 0.16022 | 0.027466 | -122.0581 | 0.14648 | 0.14648 | 0.11902 | -122.0535 | 0.064087 | 0.004577 | -122.1313 | 0.20142 | 0.045776 | 0.041199 | -122.1222 | 0.20599 | 0.21057 | 0.14648 | -122.2366 | 0.13275 | 0.14191 | 0.16022 | -122.2595
2340.9375 | 122.2275 | -0.1236 | 122.1222 | -0.20325 | 0.046341 | 0.06225 | 0.0072461 | 0.032746 | -0.0045266 | 0.031287 | -0.19958 | 0.033887 | 0.036027 | 0.050097 | -0.00024989 | 0.029708 | -0.009155 | -0.009155 | 0 | -0.032043 | 0.073242 | 0.018311 | -0.1236 | 0.004578 | 0.018311 | -0.086975 | 0.045776 | 0.036621 | -0.064087 | -0.11902 | 0.14191 | 0 | -122.049 | 0.11444 | 0.091553 | 0.091553 | -122.1313 | 0.059509 | 0.004577 | -122.0764 | 0.12817 | 0.036621 | 0.032044 | -122.0856 | 0.19684 | 0.11444 | 0.1236 | -122.2458 | 0.16937 | 0.16022 | 0.14191 | -122.2412
2342.6875 | 122.2961 | -0.086975 | 122.1176 | 0.048523 | 0.038437 | 0.061609 | 0.00083745 | 0.030397 | -0.006663 | 0.031928 | 0.052185 | 0.030469 | 0.030901 | 0.050738 | -0.0017453 | 0.029708 | 0.054932 | 0.059509 | 0.073242 | 0.027466 | 0.045776 | 0.050354 | -0.09613 | 0.091553 | 0.068665 | -0.009155 | 0.027466 | -0.004578 | -0.027466 | -0.082397 | 0.13733 | -0.009155 | -122.0718 | 0.14648 | 0.11444 | 0.1236 | -122.0627 | 0.059509 | 0.004578 | -122.0901 | 0.17853 | 0.07782 | 0.073242 | -122.1222 | 0.13275 | 0.14191 | 0.16022 | -122.2137 | 0.11444 | 0.082397 | 0.15564 | -122.2
2344.4375 | 122.3465 | -0.068665 | 122.081 | 0.15533 | 0.046768 | 0.060968 | 0.0023329 | 0.030824 | 0.0020956 | 0.03321 | 0.12085 | 0.03581 | 0.034105 | 0.052233 | 0.0020999 | 0.02864 | 0.073242 | 0.022888 | 0.036621 | 0.018311 | 0.064087 | 0.050354 | -0.10071 | 0.10529 | 0.086975 | -0.027466 | 0 | 0 | -0.027466 | -0.086975 | 0.11902 | -0.032043 | -122.0169 | 0.091553 | 0.086976 | 0.11902 | -122.0078 | 0.041199 | -0.01831 | -122.081 | 0.17395 | 0.041199 | 0.059509 | -122.081 | 0.13275 | 0.14191 | 0.10529 | -122.1817 | 0.068665 | 0.068665 | 0.15564 | -122.168
2346.2188 | 122.2733 | -0.1236 | 122.1405 | -0.23376 | 0.044846 | 0.062463 | 0.0046827 | 0.034028 | -0.0028178 | 0.031501 | -0.2301 | 0.034528 | 0.031755 | 0.053515 | -3.629e-05 | 0.029495 | 0 | -0.018311 | -0.032043 | -0.027466 | 0.086975 | -0.004578 | -0.15106 | 0 | 0.009155 | -0.11444 | 0.050354 | 0.018311 | -0.073242 | -0.11902 | 0.11902 | -0.027466 | -122.0535 | 0.10528 | 0.09613 | 0.1236 | -122.1405 | 0.050354 | 0.004577 | -122.0901 | 0.1236 | 0.009155 | 0.004578 | -122.1222 | 0.21057 | 0.1236 | 0.091553 | -122.2916 | 0.17395 | 0.14191 | 0.13275 | -122.2595
2347.9062 | 122.2412 | -0.12817 | 122.113 | -0.21851 | 0.044846 | 0.061823 | 0.0061781 | 0.034242 | -0.0017496 | 0.031287 | -0.2301 | 0.031964 | 0.035814 | 0.053087 | -0.0015317 | 0.028427 | 0 | -0.013733 | -0.013733 | -0.018311 | 0.09613 | 0.027466 | -0.13733 | 0.004578 | 0.009155 | -0.10986 | 0.045776 | 0.041199 | -0.064087 | -0.13275 | 0.15564 | -0.009155 | -122.0169 | 0.11444 | 0.10986 | 0.11902 | -122.113 | 0.064087 | -0.004577 | -122.0673 | 0.13275 | 0.018311 | 0.022888 | -122.0718 | 0.2243 | 0.12817 | 0.11444 | -122.2504 | 0.17395 | 0.16937 | 0.13733 | -122.2458
2349.6406 | 122.3602 | -0.054932 | 122.1222 | 0.094299 | 0.042496 | 0.060541 | 0.0014783 | 0.030183 | -0.0028178 | 0.03321 | 0.12848 | 0.03111 | 0.033037 | 0.052447 | 0.0027407 | 0.028854 | 0.086975 | 0.086975 | 0.09613 | 0.068665 | 0.041199 | 0.064087 | -0.086975 | 0.11902 | 0.10986 | 0 | 0 | -0.032043 | -0.032043 | -0.091553 | 0.11902 | -0.032043 | -122.081 | 0.14191 | 0.1236 | 0.15564 | -122.0352 | 0.022889 | -0.036621 | -122.1222 | 0.17395 | 0.054932 | 0.091553 | -122.1542 | 0.096131 | 0.14191 | 0.15106 | -122.2092 | 0.054932 | 0.022889 | 0.16479 | -122.2137
2351.3906 | 122.2412 | -0.09613 | 122.1359 | 0.040894 | 0.046341 | 0.06225 | -0.00065795 | 0.030824 | -0.00068138 | 0.03321 | 0.014038 | 0.03581 | 0.03261 | 0.052874 | 0.0029543 | 0.030136 | -0.004578 | -0.045776 | -0.054932 | -0.022888 | 0.068665 | 0.027466 | -0.12817 | 0.009155 | -0.018311 | -0.13275 | 0.045776 | 0.027466 | -0.064087 | -0.10071 | 0.1236 | -0.032044 | -122.0673 | 0.050354 | 0.073242 | 0.10529 | -122.1405 | 0.032043 | -0.004578 | -122.0901 | 0.10528 | -0.036621 | -0.032043 | -122.1085 | 0.16479 | 0.091552 | 0.041198 | -122.2641 | 0.14191 | 0.1236 | 0.077819 | -122.2366
2353.1406 | 122.3648 | -0.068665 | 122.1176 | -0.13458 | 0.043564 | 0.064813 | 0.0036145 | 0.03061 | -0.0096536 | 0.031928 | -0.054626 | 0.031323 | 0.031755 | 0.049669 | -0.0030271 | 0.03099 | 0.10071 | 0.14191 | 0.11902 | 0.064087 | 0.027466 | 0.059509 | -0.086975 | 0.14648 | 0.15564 | 0.050354 | 0.004578 | -0.004578 | -0.036621 | -0.082397 | 0.12817 | -0.01831 | -122.0901 | 0.21057 | 0.13275 | 0.15106 | -122.0169 | 0.032044 | -0.013732 | -122.113 | 0.21515 | 0.11902 | 0.13275 | -122.1222 | 0.096131 | 0.16937 | 0.18768 | -122.2046 | 0.073243 | 0.064087 | 0.22431 | -122.2
2354.8438 | 122.2321 | -0.1236 | 122.1497 | -0.20325 | 0.044205 | 0.062036 | 0.0038281 | 0.032319 | -0.0034586 | 0.032569 | -0.20721 | 0.03346 | 0.033678 | 0.05266 | -0.0017453 | 0.029281 | 0.004578 | 0 | 0 | -0.027466 | 0.068665 | 0.027466 | -0.1236 | 0 | 0.041199 | -0.10071 | 0.045776 | 0.032043 | -0.082397 | -0.1236 | 0.15106 | 0 | -122.081 | 0.1236 | 0.09613 | 0.09613 | -122.1451 | 0.041199 | 0 | -122.1039 | 0.1236 | 0.022888 | 0.022888 | -122.1176 | 0.19226 | 0.12817 | 0.1236 | -122.2733 | 0.16937 | 0.15564 | 0.16479 | -122.2733
2356.5938 | 122.319 | -0.07782 | 122.1176 | 0.048523 | 0.039933 | 0.06225 | -0.00087155 | 0.032319 | -0.0068766 | 0.031074 | 0.067444 | 0.031537 | 0.031969 | 0.050738 | -0.00024989 | 0.028427 | 0.054932 | 0.064087 | 0.07782 | 0.018311 | 0.032043 | 0.064087 | -0.091553 | 0.073242 | 0.073242 | -0.013733 | 0.004578 | 0 | -0.036621 | -0.086975 | 0.14191 | -0.013733 | -122.0856 | 0.14191 | 0.096131 | 0.10986 | -122.0627 | 0.041199 | -0.009155 | -122.113 | 0.15106 | 0.064087 | 0.073242 | -122.1176 | 0.10986 | 0.13275 | 0.15564 | -122.2092 | 0.082398 | 0.07782 | 0.15106 | -122.2046
2358.3594 | 122.3236 | -0.082397 | 122.1039 | 0.018005 | 0.042496 | 0.060114 | 0.0044691 | 0.031892 | -0.0064492 | 0.031074 | 0.052185 | 0.03111 | 0.032182 | 0.049669 | -0.0015317 | 0.029922 | 0.050354 | 0.054932 | 0.073242 | 0.022888 | 0.036621 | 0.036621 | -0.091553 | 0.073242 | 0.07782 | -0.018311 | 0.018311 | 0 | -0.027466 | -0.07782 | 0.11902 | -0.009156 | -122.0673 | 0.13733 | 0.10528 | 0.11444 | -122.0535 | 0.054931 | 0.004577 | -122.0856 | 0.15564 | 0.064086 | 0.059509 | -122.1039 | 0.11902 | 0.13275 | 0.15564 | -122.1954 | 0.10071 | 0.082397 | 0.16022 | -122.1817
2360.125 | 122.3511 | -0.082397 | 122.1039 | 0.010376 | 0.044419 | 0.063104 | 0.0036145 | 0.03061 | -0.0055948 | 0.03321 | 0.014038 | 0.03111 | 0.030473 | 0.050097 | -0.00067729 | 0.029068 | 0.050354 | 0.036621 | 0.054932 | 0.022888 | 0.050354 | 0.036621 | -0.086975 | 0.082397 | 0.064087 | -0.018311 | 0 | 0 | -0.050354 | -0.09613 | 0.11902 | -0.004578 | -122.0535 | 0.11902 | 0.10528 | 0.10986 | -122.0535 | 0.032043 | -0.013733 | -122.1039 | 0.16479 | 0.064086 | 0.077819 | -122.1039 | 0.13275 | 0.13275 | 0.13733 | -122.1909 | 0.082397 | 0.082397 | 0.14648 | -122.2
2361.8125 | 122.3648 | -0.073242 | 122.1085 | -0.020142 | 0.042282 | 0.062891 | 0.0021191 | 0.032746 | -0.0051676 | 0.03086 | -0.039368 | 0.031537 | 0.031114 | 0.050951 | 0.00039091 | 0.029495 | 0.068665 | 0.054932 | 0.073242 | 0.041199 | 0.054932 | 0.045776 | -0.091553 | 0.10986 | 0.10071 | 0.013733 | -0.004578 | 0.004578 | -0.036621 | -0.068665 | 0.11902 | -0.018311 | -122.0535 | 0.12817 | 0.11444 | 0.13275 | -122.0398 | 0.036621 | 0.004577 | -122.113 | 0.18311 | 0.086975 | 0.082398 | -122.1039 | 0.12817 | 0.14191 | 0.14648 | -122.2 | 0.068664 | 0.07782 | 0.17395 | -122.1771
2363.5625 | 122.2824 | -0.091553 | 122.1634 | -0.17273 | 0.045273 | 0.061182 | 0.0021191 | 0.032533 | 0.0027364 | 0.031928 | -0.25299 | 0.034101 | 0.033464 | 0.050738 | -3.629e-05 | 0.025009 | 0.050354 | 0 | 0 | 0 | 0.086975 | 0.004578 | -0.12817 | 0.041199 | 0.032043 | -0.086975 | 0.022888 | 0.013733 | -0.045776 | -0.11444 | 0.096131 | -0.036621 | -122.0764 | 0.091553 | 0.091553 | 0.12817 | -122.113 | 0.045777 | -0.022888 | -122.1405 | 0.13275 | 0.004578 | 0.027466 | -122.1497 | 0.17853 | 0.14191 | 0.091553 | -122.2916 | 0.11444 | 0.10529 | 0.1236 | -122.2778
2365.3281 | 122.3602 | -0.07782 | 122.1176 | -0.088806 | 0.045487 | 0.062036 | 0.0044691 | 0.031465 | -0.0070902 | 0.030433 | -0.054626 | 0.029401 | 0.033464 | 0.052874 | -0.0028135 | 0.027999 | 0.073242 | 0.10529 | 0.10529 | 0.059509 | 0.045776 | 0.050354 | -0.091553 | 0.14191 | 0.13733 | 0.045776 | 0.004578 | -0.027466 | -0.018311 | -0.064087 | 0.12817 | -0.013733 | -122.0718 | 0.18311 | 0.13733 | 0.15106 | -122.0444 | 0.059509 | 0.013733 | -122.113 | 0.21973 | 0.1236 | 0.10986 | -122.1451 | 0.1236 | 0.15106 | 0.18311 | -122.2092 | 0.082398 | 0.050354 | 0.21515 | -122.1817
2367.0781 | 122.3694 | -0.064087 | 122.1039 | -0.088806 | 0.043137 | 0.06225 | 0.0031873 | 0.03296 | -0.0040994 | 0.031714 | -0.092773 | 0.030683 | 0.034959 | 0.050738 | -0.0015317 | 0.02864 | 0.091553 | 0.11444 | 0.11444 | 0.059509 | 0.041199 | 0.045776 | -0.073242 | 0.16022 | 0.15564 | 0.050354 | -0.009155 | -0.004578 | -0.022888 | -0.082397 | 0.10986 | -0.009155 | -122.0627 | 0.17853 | 0.1236 | 0.13275 | -122.0123 | 0.041199 | -0.01831 | -122.113 | 0.2243 | 0.11444 | 0.13275 | -122.1085 | 0.10529 | 0.15564 | 0.17853 | -122.1771 | 0.054932 | 0.059509 | 0.21973 | -122.1863
2368.7812 | 122.2961 | -0.086975 | 122.1039 | 0.094299 | 0.039719 | 0.062677 | -0.0030077 | 0.031465 | -0.0040994 | 0.030433 | 0.082703 | 0.030896 | 0.031328 | 0.053301 | 0.00017731 | 0.029068 | 0.082397 | 0.10071 | 0.091553 | 0.032043 | 0.022888 | 0.050354 | -0.09613 | 0.10529 | 0.068665 | -0.013733 | 0.013733 | -0.022888 | -0.022888 | -0.07782 | 0.13733 | -0.009155 | -122.081 | 0.18768 | 0.11902 | 0.12817 | -122.0215 | 0.064087 | 0.009155 | -122.0901 | 0.19226 | 0.073242 | 0.064087 | -122.1268 | 0.10986 | 0.16937 | 0.17853 | -122.2 | 0.10071 | 0.064087 | 0.15564 | -122.1817
2370.5312 | 122.3465 | -0.045776 | 122.1222 | 0.12482 | 0.044632 | 0.058405 | 0.0016919 | 0.031037 | 0.00081382 | 0.030646 | 0.044556 | 0.033887 | 0.032182 | 0.052233 | 0.0023135 | 0.026718 | 0.11444 | 0.045776 | 0.068665 | 0.068665 | 0.068665 | 0.054932 | -0.082397 | 0.13275 | 0.10529 | -0.009155 | -0.027466 | -0.022888 | -0.009155 | -0.068665 | 0.10071 | -0.036621 | -122.0535 | 0.091552 | 0.11444 | 0.15106 | -122.0078 | 0.036621 | -0.022889 | -122.1497 | 0.17853 | 0.036621 | 0.05951 | -122.1451 | 0.11444 | 0.16022 | 0.11444 | -122.2046 | 0.01831 | 0.022888 | 0.15106 | -122.1909
2372.2188 | 122.2641 | -0.091553 | 122.1268 | 0.079041 | 0.0457 | 0.060754 | 0.0016919 | 0.033387 | 0.00081382 | 0.032142 | 0.059815 | 0.035382 | 0.03325 | 0.05266 | 0.0018863 | 0.027359 | 0.018311 | -0.041199 | -0.036621 | -0.018311 | 0.082397 | 0.027466 | -0.10529 | 0.036621 | -0.018311 | -0.13275 | 0.036621 | 0.036621 | -0.064087 | -0.11444 | 0.11902 | -0.013733 | -122.0444 | 0.050354 | 0.073242 | 0.086975 | -122.1085 | 0.027466 | -0.022888 | -122.0901 | 0.12817 | -0.041198 | -0.01831 | -122.0901 | 0.17395 | 0.10986 | 0.054932 | -122.2321 | 0.12817 | 0.12817 | 0.073242 | -122.2412
2373.9688 | 122.2458 | -0.09613 | 122.168 | 0.040894 | 0.045487 | 0.0599 | -0.00044435 | 0.03296 | 0.0012412 | 0.033851 | 0.021668 | 0.033673 | 0.035173 | 0.053728 | 0.0025271 | 0.028427 | -0.004578 | -0.059509 | -0.041199 | -0.018311 | 0.073242 | 0.027466 | -0.13275 | 0.022888 | -0.022888 | -0.13733 | 0.041199 | 0.018311 | -0.054932 | -0.09613 | 0.1236 | -0.036621 | -122.0947 | 0.036621 | 0.077819 | 0.11444 | -122.1725 | 0.041198 | 0 | -122.1268 | 0.11902 | -0.041199 | -0.041199 | -122.1497 | 0.16937 | 0.091552 | 0.054931 | -122.3007 | 0.13733 | 0.11444 | 0.073242 | -122.2641
2375.7188 | 122.3465 | -0.059509 | 122.1222 | 0.048523 | 0.044419 | 0.062036 | 0.0016919 | 0.029969 | 0.00038662 | 0.034705 | 0.075073 | 0.032819 | 0.034105 | 0.054369 | 0.00060451 | 0.030349 | 0.009155 | -0.009155 | -0.022888 | -0.013733 | 0.091553 | 0.022888 | -0.13275 | 0.064087 | 0 | -0.07782 | 0.027466 | 0.004578 | -0.054932 | -0.10529 | 0.082397 | -0.073242 | -122.0306 | 0.050354 | 0.045776 | 0.11902 | -122.113 | 0.004577 | -0.045777 | -122.0947 | 0.1236 | -0.018311 | 0.027466 | -122.1176 | 0.15106 | 0.068664 | 0.036621 | -122.2549 | 0.086975 | 0.064087 | 0.059509 | -122.2275
2377.4688 | 122.2733 | -0.091553 | 122.1497 | -0.18036 | 0.046341 | 0.06225 | 0.0066053 | 0.034028 | -0.0030314 | 0.035132 | -0.1767 | 0.034314 | 0.034318 | 0.050097 | -0.00024989 | 0.028427 | -0.022888 | -0.004578 | -0.009155 | -0.013733 | 0.086975 | 0.018311 | -0.1236 | 0.022888 | 0.041199 | -0.091553 | 0.041199 | 0.009155 | -0.068665 | -0.11902 | 0.10986 | -0.032043 | -122.0627 | 0.086975 | 0.07782 | 0.10986 | -122.1725 | 0.022888 | -0.027466 | -122.1085 | 0.11444 | 0 | 0.027466 | -122.1405 | 0.17853 | 0.068665 | 0.082398 | -122.2733 | 0.13275 | 0.10071 | 0.13275 | -122.2687
2379.1562 | 122.3694 | -0.091553 | 122.0856 | -0.0354 | 0.042923 | 0.061182 | 0.0053235 | 0.032105 | -0.0087992 | 0.032355 | -0.0012209 | 0.031964 | 0.033891 | 0.053301 | -0.0047361 | 0.030563 | 0.009155 | 0.07782 | 0.073242 | 0.041199 | 0.059509 | 0.054932 | -0.082397 | 0.10529 | 0.1236 | 0.027466 | 0.009155 | 0 | -0.018311 | -0.10529 | 0.14649 | 0.009156 | -122.0261 | 0.16937 | 0.13275 | 0.1236 | -122.0764 | 0.073242 | -0.013733 | -122.0764 | 0.19684 | 0.11902 | 0.13275 | -122.0856 | 0.15106 | 0.10071 | 0.16479 | -122.168 | 0.10071 | 0.091553 | 0.21515 | -122.1909
2380.9219 | 122.3602 | -0.041199 | 122.1039 | 0.10956 | 0.044632 | 0.06225 | -0.0010851 | 0.031892 | -0.0017496 | 0.034492 | 0.13611 | 0.034101 | 0.03325 | 0.052019 | 0.0038089 | 0.02864 | 0.018311 | 0.009155 | 0.018311 | -0.004578 | 0.068665 | 0.022888 | -0.09613 | 0.086975 | 0.059509 | -0.036621 | 0.027466 | 0.009155 | -0.036621 | -0.07782 | 0.064087 | -0.054931 | -122.0352 | 0.050354 | 0.036621 | 0.091552 | -122.0856 | 0.004578 | -0.036621 | -122.0764 | 0.12817 | 0.004578 | 0.041199 | -122.0947 | 0.10986 | 0.05951 | 0.05951 | -122.2 | 0.068665 | 0.050354 | 0.10071 | -122.1817
2382.6094 | 122.3694 | -0.068665 | 122.0993 | 0.16296 | 0.043137 | 0.060968 | 0.00041005 | 0.034669 | -0.002604 | 0.033423 | 0.19714 | 0.034741 | 0.031755 | 0.052233 | 0.0012455 | 0.028213 | 0.082397 | 0.073242 | 0.091553 | 0.054932 | 0.050354 | 0.059509 | -0.07782 | 0.13733 | 0.10986 | 0 | -0.004578 | -0.013733 | 0 | -0.068665 | 0.12817 | -0.009155 | -122.049 | 0.14191 | 0.1236 | 0.13275 | -122.0169 | 0.068665 | 0 | -122.1039 | 0.20599 | 0.068665 | 0.068665 | -122.113 | 0.11902 | 0.15106 | 0.16022 | -122.1771 | 0.064087 | 0.054932 | 0.17853 | -122.168
2384.375 | 122.2733 | -0.10529 | 122.1634 | -0.17273 | 0.045273 | 0.062891 | 0.00041005 | 0.032105 | -0.0011088 | 0.034705 | -0.18433 | 0.033887 | 0.03325 | 0.050738 | 0.0020999 | 0.028427 | 0.009155 | 0.018311 | -0.018311 | 0.018311 | 0.064087 | 0.018311 | -0.13733 | 0.041199 | 0.068665 | -0.07782 | 0.027466 | 0.041199 | -0.050354 | -0.10071 | 0.1236 | -0.032043 | -122.0993 | 0.1236 | 0.1236 | 0.15564 | -122.1542 | 0.054932 | 0.004578 | -122.1359 | 0.14649 | 0.027466 | 0.022888 | -122.1222 | 0.16937 | 0.11444 | 0.086975 | -122.3007 | 0.13275 | 0.14649 | 0.17395 | -122.2641
2386.0938 | 122.3557 | -0.064087 | 122.1176 | 0.14008 | 0.044419 | 0.060968 | 0.0036145 | 0.030183 | -0.0023904 | 0.031928 | 0.27344 | 0.032392 | 0.033464 | 0.053728 | 0.0010317 | 0.027999 | 0.064087 | 0.068665 | 0.059509 | 0.032043 | 0.050354 | 0.054932 | -0.091553 | 0.1236 | 0.10529 | -0.004578 | -0.013733 | -0.013733 | -0.009155 | -0.082397 | 0.11902 | -0.027466 | -122.0673 | 0.13275 | 0.09613 | 0.1236 | -122.0535 | 0.054932 | -0.01831 | -122.1313 | 0.18768 | 0.059509 | 0.077819 | -122.1313 | 0.11444 | 0.12817 | 0.1236 | -122.2092 | 0.050354 | 0.050354 | 0.16937 | -122.2
2387.8438 | 122.2504 | -0.11902 | 122.1542 | -0.10406 | 0.046128 | 0.059473 | 0.0034009 | 0.031251 | -0.00046778 | 0.034492 | -0.085144 | 0.035596 | 0.035173 | 0.051592 | 0.0010317 | 0.029495 | 0.059509 | 0.054932 | 0.036621 | 0.027466 | 0.059509 | 0.045776 | -0.10986 | 0.073242 | 0.073242 | -0.073242 | 0.027466 | 0.018311 | -0.036621 | -0.10986 | 0.16479 | 0.009156 | -122.0947 | 0.17395 | 0.14649 | 0.13733 | -122.0947 | 0.082398 | 0.009156 | -122.1268 | 0.19226 | 0.045777 | 0.036621 | -122.1359 | 0.17853 | 0.17853 | 0.15564 | -122.2641 | 0.14649 | 0.13733 | 0.19226 | -122.2641
2389.5938 | 122.2458 | -0.12817 | 122.1542 | -0.21088 | 0.046341 | 0.061609 | 0.0066053 | 0.034242 | -0.0064492 | 0.030006 | -0.18433 | 0.032178 | 0.035173 | 0.051165 | -0.0034543 | 0.029281 | 0.032043 | 0.10986 | 0.082397 | 0.059509 | 0.050354 | 0.041199 | -0.10071 | 0.036621 | 0.091553 | -0.050354 | 0.018311 | 0.013733 | -0.045776 | -0.09613 | 0.16937 | 0.027466 | -122.1039 | 0.23804 | 0.18768 | 0.16022 | -122.1222 | 0.082398 | 0.032044 | -122.1359 | 0.1648 | 0.07782 | 0.045776 | -122.1405 | 0.17853 | 0.16022 | 0.21057 | -122.2549 | 0.14649 | 0.14191 | 0.21973 | -122.2504
2391.2812 | 122.2366 | -0.10071 | 122.1771 | 0.056152 | 0.045914 | 0.0599 | 0.0023329 | 0.033174 | -4.058e-05 | 0.032142 | 0.014038 | 0.034101 | 0.034105 | 0.053087 | 0.0033817 | 0.026504 | -0.009155 | -0.050354 | -0.054932 | -0.022888 | 0.07782 | 0.027466 | -0.13733 | -0.009155 | -0.036621 | -0.12817 | 0.059509 | 0.050354 | -0.059509 | -0.10071 | 0.12817 | -0.036621 | -122.0993 | 0.050354 | 0.07782 | 0.11444 | -122.1863 | 0.041199 | 0 | -122.1176 | 0.091553 | -0.027466 | -0.027466 | -122.1268 | 0.17853 | 0.091553 | 0.045776 | -122.3145 | 0.16022 | 0.15106 | 0.064087 | -122.2778
2393.0312 | 122.3648 | -0.059509 | 122.1039 | 0.0027468 | 0.043991 | 0.063104 | 0.0063917 | 0.032746 | -0.011363 | 0.031074 | 0.059815 | 0.029828 | 0.034318 | 0.050524 | -0.0053769 | 0.029495 | -0.009155 | 0.054932 | 0.064087 | 0.027466 | 0.059509 | 0.045776 | -0.082397 | 0.068665 | 0.073242 | 0 | 0.018311 | 0.004578 | -0.045776 | -0.07782 | 0.10528 | -0.022888 | -122.0444 | 0.11444 | 0.086975 | 0.10986 | -122.113 | 0.013733 | -0.018311 | -122.0856 | 0.12817 | 0.059509 | 0.07782 | -122.0993 | 0.11902 | 0.050354 | 0.1236 | -122.1863 | 0.07782 | 0.064087 | 0.13275 | -122.1817
2394.7812 | 122.2961 | -0.07782 | 122.1497 | 0.10956 | 0.046128 | 0.059045 | -1.7146e-05 | 0.032533 | 0.00060022 | 0.031714 | 0.067444 | 0.033673 | 0.03261 | 0.053087 | 0.0018863 | 0.026718 | 0.009155 | -0.045776 | -0.041199 | -0.013733 | 0.07782 | 0.027466 | -0.11902 | 0.027466 | -0.009155 | -0.10986 | 0.041199 | 0.036621 | -0.054932 | -0.09613 | 0.10529 | -0.041199 | -122.0718 | 0.032044 | 0.064087 | 0.10529 | -122.1405 | 0.022888 | -0.01831 | -122.1085 | 0.10529 | -0.032043 | -0.013733 | -122.113 | 0.15564 | 0.086975 | 0.036621 | -122.2687 | 0.11902 | 0.11444 | 0.068665 | -122.2458
2396.4688 | 122.3831 | -0.054932 | 122.1039 | -0.027771 | 0.041855 | 0.061823 | 0.0025465 | 0.032105 | -0.0090128 | 0.03086 | 0.0064086 | 0.030683 | 0.03261 | 0.049669 | -0.0011045 | 0.031417 | 0.032043 | 0.064087 | 0.059509 | 0.041199 | 0.050354 | 0.059509 | -0.09613 | 0.10529 | 0.11444 | 0.032043 | 0.018311 | 0.009155 | -0.018311 | -0.086975 | 0.11444 | -0.041198 | -122.0535 | 0.11902 | 0.096131 | 0.13733 | -122.0718 | 0.036621 | -0.032043 | -122.0856 | 0.16022 | 0.086975 | 0.11902 | -122.0947 | 0.10529 | 0.086975 | 0.11444 | -122.2 | 0.073243 | 0.064087 | 0.16937 | -122.1909
2398.2188 | 122.2504 | -0.1236 | 122.1588 | 0.033264 | 0.044419 | 0.059045 | 0.0016919 | 0.034455 | -0.00089518 | 0.033423 | -0.0012209 | 0.033673 | 0.035814 | 0.056292 | 0.0033817 | 0.027572 | -0.004578 | -0.036621 | -0.036621 | -0.027466 | 0.068665 | 0.018311 | -0.10986 | -0.004578 | -0.041199 | -0.14191 | 0.050354 | 0.036621 | -0.050354 | -0.11444 | 0.14191 | 0.013733 | -122.0901 | 0.086975 | 0.09613 | 0.082397 | -122.1634 | 0.073242 | 0.009155 | -122.1085 | 0.11902 | -0.018311 | -0.027466 | -122.1222 | 0.19226 | 0.11902 | 0.086975 | -122.2687 | 0.17395 | 0.16022 | 0.082397 | -122.2733
2399.9688 | 122.3831 | -0.059509 | 122.1222 | -0.020142 | 0.039933 | 0.064386 | 0.0027601 | 0.032105 | -0.00944 | 0.031074 | 0.029297 | 0.029401 | 0.031755 | 0.050524 | -0.0019589 | 0.029495 | 0.018311 | 0.054932 | 0.064087 | 0.036621 | 0.068665 | 0.050354 | -0.10071 | 0.091553 | 0.091553 | 0.009155 | 0.018311 | -0.004578 | -0.027466 | -0.082397 | 0.10986 | -0.041199 | -122.0535 | 0.11444 | 0.09613 | 0.13733 | -122.1039 | 0.032043 | -0.022888 | -122.1039 | 0.15106 | 0.068664 | 0.091552 | -122.1268 | 0.12817 | 0.07782 | 0.1236 | -122.2229 | 0.07782 | 0.054931 | 0.15106 | -122.2046
2401.7188 | 122.3282 | -0.068665 | 122.1497 | 0.16296 | 0.044205 | 0.059686 | -0.00044435 | 0.032319 | -0.0038858 | 0.029151 | 0.15137 | 0.033246 | 0.031541 | 0.052019 | 0.0023135 | 0.027999 | 0.11444 | 0.10071 | 0.10986 | 0.059509 | 0.041199 | 0.064087 | -0.073242 | 0.12817 | 0.13275 | 0.027466 | 0 | -0.027466 | -0.027466 | -0.054932 | 0.13275 | -0.004577 | -122.1085 | 0.16937 | 0.12817 | 0.13275 | -122.0352 | 0.041199 | 0.013733 | -122.1497 | 0.19684 | 0.096131 | 0.082398 | -122.1771 | 0.10986 | 0.18311 | 0.17853 | -122.2229 | 0.068665 | 0.041199 | 0.20142 | -122.2046
2403.4219 | 122.3465 | -0.068665 | 122.1268 | 0.079041 | 0.043137 | 0.063959 | 0.0016919 | 0.030824 | -0.004313 | 0.030646 | 0.090332 | 0.031751 | 0.032823 | 0.051378 | -0.0025999 | 0.029068 | 0.059509 | 0.059509 | 0.082397 | 0.018311 | 0.041199 | 0.059509 | -0.086975 | 0.11444 | 0.07782 | -0.022888 | 0.009155 | 0.004578 | -0.013733 | -0.10529 | 0.12817 | -0.01831 | -122.0856 | 0.12817 | 0.086976 | 0.10529 | -122.0673 | 0.054932 | -0.036621 | -122.1176 | 0.18311 | 0.045777 | 0.082398 | -122.1222 | 0.10986 | 0.12817 | 0.15106 | -122.2137 | 0.07782 | 0.073243 | 0.14649 | -122.2321
2405.1719 | 122.2733 | -0.09613 | 122.1405 | 0.079041 | 0.041855 | 0.060541 | 0.00062385 | 0.031251 | 0.001882 | 0.033423 | 0.059815 | 0.033673 | 0.031541 | 0.052019 | 0.0020999 | 0.026077 | 0.032043 | -0.068665 | -0.022888 | -0.032043 | 0.07782 | 0.032043 | -0.11902 | 0.041199 | -0.027466 | -0.12817 | 0.064087 | 0.036621 | -0.054932 | -0.11444 | 0.12817 | -0.022889 | -122.0627 | 0.027465 | 0.064087 | 0.086976 | -122.1085 | 0.041198 | -0.018311 | -122.0764 | 0.13733 | -0.032044 | -0.013733 | -122.1039 | 0.17395 | 0.12817 | 0.073242 | -122.2595 | 0.16022 | 0.13275 | 0.068664 | -122.2549
2406.875 | 122.3877 | -0.054932 | 122.1268 | -0.0354 | 0.042496 | 0.060327 | 0.0061781 | 0.032105 | -0.0062356 | 0.031074 | 0.0064086 | 0.031537 | 0.033891 | 0.052019 | -0.0021725 | 0.027145 | 0.027466 | 0.054932 | 0.064087 | 0.027466 | 0.050354 | 0.050354 | -0.09613 | 0.10071 | 0.10986 | 0.013733 | 0.004578 | -0.009155 | -0.009155 | -0.073242 | 0.10529 | -0.041198 | -122.0764 | 0.10986 | 0.082398 | 0.1236 | -122.0993 | 0.045777 | -0.01831 | -122.1222 | 0.15564 | 0.068665 | 0.086975 | -122.1359 | 0.10529 | 0.082398 | 0.11902 | -122.2229 | 0.05951 | 0.045777 | 0.16479 | -122.2
2408.625 | 122.3694 | -0.054932 | 122.1405 | 0.14008 | 0.044419 | 0.060968 | 0.0016919 | 0.033174 | 0.0020956 | 0.033637 | 0.10559 | 0.033887 | 0.03261 | 0.053301 | 0.0012455 | 0.025863 | 0.050354 | 0.036621 | 0.036621 | 0.018311 | 0.045776 | 0.050354 | -0.091553 | 0.13733 | 0.059509 | -0.004578 | 0 | -0.004578 | -0.032043 | -0.073242 | 0.10529 | -0.036621 | -122.0947 | 0.091553 | 0.073243 | 0.10986 | -122.0901 | 0.022889 | -0.01831 | -122.1405 | 0.19226 | 0.050354 | 0.068664 | -122.1451 | 0.10071 | 0.10529 | 0.091553 | -122.2321 | 0.054932 | 0.050354 | 0.11444 | -122.2137
2410.3125 | 122.2366 | -0.1236 | 122.1588 | -0.12695 | 0.045914 | 0.06225 | 0.0070325 | 0.031037 | -0.0036722 | 0.03321 | -0.21484 | 0.033246 | 0.035173 | 0.05266 | -0.0017453 | 0.026931 | 0 | 0.004578 | -0.009155 | -0.022888 | 0.086975 | 0.004578 | -0.12817 | 0.004578 | 0.041199 | -0.10529 | 0.041199 | 0.041199 | -0.054932 | -0.12817 | 0.12817 | -0.004578 | -122.0718 | 0.12817 | 0.10071 | 0.10529 | -122.1588 | 0.068664 | -0.004578 | -122.1176 | 0.12817 | 0.01831 | 0.022888 | -122.1176 | 0.21057 | 0.1236 | 0.11444 | -122.287 | 0.16479 | 0.16479 | 0.16479 | -122.287
2412.0156 | 122.3282 | -0.073242 | 122.1313 | 0.13245 | 0.044205 | 0.061182 | 0.0031873 | 0.032105 | -0.006022 | 0.032569 | 0.11322 | 0.030683 | 0.03325 | 0.052019 | 0.0029543 | 0.027786 | 0.10529 | 0.11902 | 0.12817 | 0.059509 | 0.041199 | 0.050354 | -0.059509 | 0.14648 | 0.11902 | 0.022888 | 0.004578 | -0.018311 | -0.036621 | -0.09613 | 0.1236 | 0.013733 | -122.0901 | 0.19226 | 0.13275 | 0.11902 | -122.0261 | 0.036621 | -0.022888 | -122.1268 | 0.21973 | 0.09613 | 0.11902 | -122.1497 | 0.11444 | 0.17853 | 0.20142 | -122.1909 | 0.07782 | 0.054931 | 0.19226 | -122.2275
2413.7812 | 122.2916 | -0.09613 | 122.1771 | -0.21088 | 0.047409 | 0.060114 | 0.0070325 | 0.033601 | -0.0011088 | 0.032142 | -0.20721 | 0.031751 | 0.036455 | 0.054369 | -0.00046349 | 0.026504 | -0.009155 | -0.004578 | -0.027466 | -0.004578 | 0.082397 | 0.022888 | -0.14648 | 0.022888 | 0.027466 | -0.10071 | 0.045776 | 0.032043 | -0.036621 | -0.11902 | 0.11902 | -0.050354 | -122.0947 | 0.091552 | 0.091552 | 0.14191 | -122.1863 | 0.059509 | -0.022889 | -122.1313 | 0.11902 | -0.004578 | 0.018311 | -122.1451 | 0.17853 | 0.086975 | 0.068664 | -122.3236 | 0.14191 | 0.12817 | 0.1236 | -122.2961
2415.5625 | 122.3648 | -0.059509 | 122.1542 | 0.16296 | 0.042496 | 0.06225 | 0.00019645 | 0.03061 | -0.0038858 | 0.031074 | 0.14374 | 0.032819 | 0.03325 | 0.052447 | 0.00060451 | 0.028854 | 0.09613 | 0.10529 | 0.07782 | 0.050354 | 0.027466 | 0.045776 | -0.082397 | 0.13733 | 0.12817 | 0.013733 | 0.009155 | -0.013733 | 0.004578 | -0.07782 | 0.10528 | -0.022888 | -122.1268 | 0.16479 | 0.10986 | 0.13275 | -122.0581 | 0.064087 | -0.018311 | -122.1451 | 0.19684 | 0.073242 | 0.091553 | -122.168 | 0.086975 | 0.15564 | 0.13733 | -122.2366 | 0.068664 | 0.045776 | 0.18768 | -122.2321
2417.25 | 122.3511 | -0.064087 | 122.1451 | 0.11719 | 0.045487 | 0.061609 | -0.0025805 | 0.031892 | -4.058e-05 | 0.033637 | 0.059815 | 0.03346 | 0.029619 | 0.051165 | 0.0018863 | 0.028427 | 0.013733 | -0.018311 | -0.041199 | -0.013733 | 0.07782 | 0.022888 | -0.11902 | 0.032043 | 0 | -0.10071 | 0.041199 | 0.032043 | -0.059509 | -0.10529 | 0.086975 | -0.054932 | -122.0673 | 0.045776 | 0.050354 | 0.10529 | -122.1313 | 0.004578 | -0.041199 | -122.1039 | 0.09613 | -0.036621 | 0.004578 | -122.113 | 0.14191 | 0.07782 | 0.022888 | -122.2641 | 0.10529 | 0.09613 | 0.064087 | -122.2504
2419 | 122.2504 | -0.091553 | 122.1588 | -0.081177 | 0.045273 | 0.060754 | 0.0010511 | 0.032105 | -0.00089518 | 0.03556 | -0.13855 | 0.032819 | 0.033037 | 0.050951 | 0.0014591 | 0.027145 | 0.073242 | 0.045776 | 0.027466 | 0.013733 | 0.068665 | 0.041199 | -0.11902 | 0.07782 | 0.073242 | -0.059509 | 0.050354 | 0.022888 | -0.050354 | -0.09613 | 0.13275 | -0.027466 | -122.0901 | 0.13733 | 0.10529 | 0.13275 | -122.0856 | 0.041199 | -0.004577 | -122.1085 | 0.16937 | 0.032044 | 0.036621 | -122.1359 | 0.16022 | 0.16479 | 0.11902 | -122.2778 | 0.14191 | 0.11444 | 0.16479 | -122.2549
2420.6875 | 122.3511 | -0.073242 | 122.1222 | 0.08667 | 0.045273 | 0.061182 | 0.0010511 | 0.034669 | -0.0017496 | 0.034064 | 0.090332 | 0.033032 | 0.034532 | 0.054796 | 0.0010317 | 0.028854 | 0.013733 | -0.041199 | -0.027466 | -0.013733 | 0.068665 | 0.032043 | -0.10986 | 0.036621 | 0.004578 | -0.082397 | 0.041199 | 0.036621 | -0.054932 | -0.09613 | 0.10529 | -0.036621 | -122.0535 | 0.032043 | 0.059509 | 0.09613 | -122.1085 | 0.01831 | -0.022888 | -122.081 | 0.10986 | -0.009155 | 0.013733 | -122.0856 | 0.14191 | 0.086975 | 0.045776 | -122.2321 | 0.11444 | 0.10986 | 0.07782 | -122.2183
2422.4219 | 122.287 | -0.086975 | 122.1863 | -0.18799 | 0.045487 | 0.061823 | 0.0061781 | 0.029328 | -0.0081582 | 0.03321 | -0.11566 | 0.031323 | 0.035173 | 0.051806 | -0.0043087 | 0.029068 | 0.064087 | 0.1236 | 0.10986 | 0.073242 | 0.036621 | 0.036621 | -0.086975 | 0.09613 | 0.16022 | 0.027466 | 0.004578 | -0.013733 | -0.022888 | -0.10529 | 0.1236 | 0 | -122.1497 | 0.21057 | 0.16022 | 0.16022 | -122.1222 | 0.064087 | -0.018311 | -122.1817 | 0.1831 | 0.11444 | 0.13275 | -122.2 | 0.1236 | 0.15106 | 0.19684 | -122.2733 | 0.091553 | 0.073242 | 0.24719 | -122.2916
2424.1719 | 122.3557 | -0.059509 | 122.1313 | 0.010376 | 0.038651 | 0.061609 | 0.0040417 | 0.03061 | -0.006022 | 0.031287 | 0.059815 | 0.029187 | 0.031328 | 0.050951 | -0.0015317 | 0.030136 | 0.009155 | 0.054932 | 0.054932 | 0.022888 | 0.068665 | 0.032043 | -0.086975 | 0.073242 | 0.073242 | -0.009155 | 0.018311 | 0.018311 | -0.036621 | -0.086975 | 0.091552 | -0.027466 | -122.0627 | 0.11444 | 0.082397 | 0.10986 | -122.1222 | 0.022888 | -0.027466 | -122.113 | 0.13275 | 0.050354 | 0.07782 | -122.113 | 0.12817 | 0.068664 | 0.11444 | -122.2183 | 0.07782 | 0.07782 | 0.13275 | -122.2183
2425.9375 | 122.2733 | -0.09613 | 122.1771 | -0.11932 | 0.045487 | 0.062036 | 0.0027601 | 0.033814 | 0.0016684 | 0.03086 | -0.15381 | 0.035169 | 0.034746 | 0.054369 | 0.0044497 | 0.027359 | 0.07782 | 0.022888 | 0.032043 | 0.022888 | 0.068665 | 0.027466 | -0.1236 | 0.091553 | 0.091553 | -0.059509 | 0.041199 | 0.032043 | -0.027466 | -0.10529 | 0.1236 | -0.027466 | -122.1085 | 0.11902 | 0.11902 | 0.14648 | -122.0993 | 0.068664 | -0.009156 | -122.1359 | 0.18768 | 0.036621 | 0.045777 | -122.1451 | 0.16479 | 0.17395 | 0.12817 | -122.3007 | 0.13733 | 0.12817 | 0.18768 | -122.2824
2427.6875 | 122.3923 | -0.082397 | 122.1085 | -0.027771 | 0.038864 | -0.034094 | -0.00065795 | 0.032105 | -0.0087992 | 0.032142 | 0.014038 | 0.031537 | 0.033037 | 0.050951 | -3.629e-05 | 0.030136 | 0.032043 | 0.068665 | 0.068665 | 0.027466 | 0.045776 | 0.036621 | -0.07782 | 0.086975 | 0.10986 | 0.013733 | 0.004578 | 0 | -0.027466 | -0.082397 | 0.11902 | 0.004577 | -122.0627 | 0.15106 | 0.10986 | 0.10529 | -122.0764 | 0.054931 | 0 | -122.1039 | 0.16937 | 0.09613 | 0.09613 | -122.1085 | 0.12817 | 0.11444 | 0.15106 | -122.1863 | 0.086975 | 0.082397 | 0.19226 | -122.1909
2429.375 | 122.3877 | -0.054932 | 122.1268 | 0.14771 | 0.042282 | 0.061182 | 0.0021191 | 0.032105 | -0.0017496 | 0.034278 | 0.090332 | 0.032819 | 0.031541 | 0.050524 | 0.0010317 | 0.027145 | 0.086975 | 0.068665 | 0.068665 | 0.036621 | 0.054932 | 0.064087 | -0.086975 | 0.1236 | 0.10986 | 0.004578 | 0.013733 | -0.009155 | -0.027466 | -0.064087 | 0.11902 | -0.032043 | -122.0718 | 0.1236 | 0.091553 | 0.1236 | -122.0398 | 0.027466 | -0.009155 | -122.113 | 0.17853 | 0.05951 | 0.068665 | -122.1359 | 0.10986 | 0.14191 | 0.1236 | -122.2137 | 0.068665 | 0.045777 | 0.16479 | -122.1909
2431.1406 | 122.3007 | -0.073242 | 122.1497 | -0.21088 | 0.043351 | 0.06225 | 0.0046827 | 0.033814 | -0.0070902 | 0.03086 | -0.14618 | 0.031537 | 0.033891 | 0.050951 | -0.0025999 | 0.025863 | 0.09613 | 0.13733 | 0.12817 | 0.064087 | 0.027466 | 0.041199 | -0.086975 | 0.11902 | 0.15564 | 0.032043 | 0.004578 | -0.013733 | -0.018311 | -0.10071 | 0.11444 | -0.013733 | -122.1222 | 0.21057 | 0.13733 | 0.15106 | -122.0535 | 0.054931 | -0.027466 | -122.1451 | 0.19226 | 0.10529 | 0.13275 | -122.1634 | 0.10071 | 0.16937 | 0.20142 | -122.2366 | 0.07782 | 0.059509 | 0.22888 | -122.2504
2432.875 | 122.2687 | -0.11444 | 122.1863 | 0.033264 | 0.046128 | 0.06225 | -0.00087155 | 0.031465 | 0.0033774 | 0.031074 | -0.0088499 | 0.034955 | 0.034105 | 0.053087 | 0.0025271 | 0.025436 | 0 | -0.054932 | -0.045776 | -0.036621 | 0.07782 | 0.018311 | -0.11444 | 0.022888 | -0.027466 | -0.11902 | 0.041199 | 0.009155 | -0.050354 | -0.10986 | 0.13275 | 0 | -122.1085 | 0.059509 | 0.07782 | 0.07782 | -122.1863 | 0.064087 | 0.004578 | -122.1451 | 0.13733 | -0.004578 | -0.009156 | -122.1771 | 0.19226 | 0.11444 | 0.068665 | -122.3007 | 0.15564 | 0.1236 | 0.086975 | -122.2961
2434.625 | 122.2595 | -0.10986 | 122.168 | 0.040894 | 0.048905 | 0.060327 | 0.0036145 | 0.03061 | 0.0027364 | 0.03556 | -0.024109 | 0.032605 | 0.033464 | 0.052874 | 0.0020999 | 0.027359 | 0 | -0.050354 | -0.032043 | -0.009155 | 0.068665 | 0.018311 | -0.11902 | 0 | -0.013733 | -0.14648 | 0.059509 | 0.050354 | -0.059509 | -0.1236 | 0.12817 | -0.009156 | -122.0993 | 0.059509 | 0.10071 | 0.10986 | -122.168 | 0.050354 | -0.013733 | -122.1085 | 0.10986 | -0.036621 | -0.022888 | -122.1176 | 0.17853 | 0.10986 | 0.07782 | -122.287 | 0.16937 | 0.16022 | 0.09613 | -122.2916
2436.375 | 122.2824 | -0.10529 | 122.1634 | 0.071411 | 0.046768 | 0.061609 | 0.00019645 | 0.034455 | -0.00046778 | 0.034064 | 0.075073 | 0.033032 | 0.034105 | 0.052019 | 0.00081811 | 0.026077 | 0.004578 | -0.050354 | -0.045776 | -0.018311 | 0.086975 | 0.027466 | -0.13275 | 0.013733 | -0.032043 | -0.10986 | 0.027466 | 0.036621 | -0.059509 | -0.10529 | 0.13275 | -0.027465 | -122.0764 | 0.054932 | 0.086975 | 0.11444 | -122.1588 | 0.045777 | 0 | -122.1359 | 0.11902 | -0.004577 | -0.004577 | -122.1268 | 0.19226 | 0.10986 | 0.05951 | -122.2961 | 0.13275 | 0.14191 | 0.073243 | -122.2687
2438.125 | 122.2595 | -0.10529 | 122.1634 | -0.088806 | 0.044419 | 0.062463 | 0.0038281 | 0.034883 | -4.058e-05 | 0.031501 | -0.10803 | 0.032178 | 0.035387 | 0.050524 | -0.00089089 | 0.028213 | 0.082397 | 0.041199 | 0.036621 | 0.022888 | 0.073242 | 0.064087 | -0.10529 | 0.064087 | 0.064087 | -0.064087 | 0.032043 | 0.027466 | -0.054932 | -0.10529 | 0.16937 | 0 | -122.0901 | 0.14649 | 0.12817 | 0.12817 | -122.081 | 0.050354 | 0 | -122.1313 | 0.16937 | 0.041199 | 0.041199 | -122.1359 | 0.17853 | 0.18768 | 0.14191 | -122.2687 | 0.13733 | 0.13275 | 0.16937 | -122.2687
2439.8125 | 122.3923 | -0.050354 | 122.1497 | 0.16296 | 0.042282 | 0.062036 | 0.0012647 | 0.033387 | -0.003245 | 0.034919 | 0.075073 | 0.030042 | 0.034746 | 0.054156 | -0.00089089 | 0.027999 | 0.068665 | 0.073242 | 0.07782 | 0.041199 | 0.045776 | 0.054932 | -0.09613 | 0.11902 | 0.09613 | 0.009155 | 0 | -0.022888 | -0.013733 | -0.073242 | 0.10529 | -0.045776 | -122.1039 | 0.1236 | 0.091553 | 0.13733 | -122.081 | 0.036621 | -0.022888 | -122.1497 | 0.16937 | 0.059509 | 0.082397 | -122.1725 | 0.09613 | 0.11902 | 0.12817 | -122.2458 | 0.050354 | 0.027466 | 0.14648 | -122.2229
2441.5781 | 122.3007 | -0.10071 | 122.2046 | -0.19562 | 0.043351 | 0.06225 | 0.0076733 | 0.034028 | -0.0062356 | 0.032569 | -0.1004 | 0.028974 | 0.035173 | 0.051165 | -0.0023861 | 0.029495 | 0.059509 | 0.13275 | 0.1236 | 0.064087 | 0.032043 | 0.045776 | -0.082397 | 0.11444 | 0.15564 | 0.041199 | -0.013733 | -0.013733 | -0.009155 | -0.073242 | 0.14648 | 0.018311 | -122.1725 | 0.23346 | 0.1648 | 0.14648 | -122.1451 | 0.091553 | 0.027466 | -122.2183 | 0.21515 | 0.14191 | 0.11444 | -122.2183 | 0.13275 | 0.16022 | 0.2243 | -122.287 | 0.086975 | 0.086975 | 0.25635 | -122.2778
2443.2656 | 122.406 | -0.068665 | 122.1313 | -0.065918 | 0.043137 | 0.060114 | 0.0036145 | 0.034242 | -0.00944 | 0.029151 | -0.085144 | 0.029828 | 0.035173 | 0.053087 | -0.0047361 | 0.029495 | 0.045776 | 0.091553 | 0.086975 | 0.045776 | 0.064087 | 0.045776 | -0.091553 | 0.13275 | 0.13275 | 0.036621 | 0.004578 | -0.009155 | -0.013733 | -0.07782 | 0.11444 | -0.022888 | -122.0673 | 0.16022 | 0.11444 | 0.13733 | -122.0856 | 0.054932 | -0.009155 | -122.1268 | 0.20142 | 0.10529 | 0.11444 | -122.1405 | 0.13275 | 0.11444 | 0.15564 | -122.2229 | 0.073243 | 0.05951 | 0.20142 | -122.2092
2445.0156 | 122.3007 | -0.082397 | 122.1817 | -0.11932 | 0.044846 | 0.062677 | 0.0010511 | 0.03296 | -0.00025418 | 0.034492 | -0.18433 | 0.033032 | 0.033037 | 0.054583 | 0.0018863 | 0.026077 | 0.059509 | 0.022888 | 0.018311 | 0.027466 | 0.073242 | 0.022888 | -0.10986 | 0.068665 | 0.073242 | -0.059509 | 0.041199 | 0.013733 | -0.041199 | -0.10529 | 0.10528 | -0.027466 | -122.1085 | 0.10528 | 0.10986 | 0.13733 | -122.1222 | 0.041198 | -0.022889 | -122.1405 | 0.15106 | 0.022888 | 0.045777 | -122.168 | 0.15564 | 0.14191 | 0.10071 | -122.2916 | 0.1236 | 0.09613 | 0.15564 | -122.287
2446.7812 | 122.3053 | -0.09613 | 122.1634 | 0.079041 | 0.045273 | 0.063318 | -0.0015125 | 0.030824 | 0.0010276 | 0.034919 | 0.082703 | 0.03346 | 0.034532 | 0.052233 | 0.0035953 | 0.027359 | 0.004578 | -0.041199 | -0.032043 | -0.027466 | 0.073242 | 0.022888 | -0.12817 | 0.022888 | -0.027466 | -0.10986 | 0.036621 | 0.022888 | -0.054932 | -0.10529 | 0.11902 | -0.032044 | -122.0901 | 0.054931 | 0.068664 | 0.10071 | -122.1588 | 0.041198 | -0.009156 | -122.1268 | 0.11902 | -0.013733 | -0.004577 | -122.1405 | 0.16937 | 0.10071 | 0.064087 | -122.2916 | 0.13275 | 0.11902 | 0.068664 | -122.2687
2448.4844 | 122.3419 | -0.086975 | 122.1725 | 0.094299 | 0.045273 | 0.062036 | 0.0019055 | 0.030397 | -0.0034586 | 0.033637 | 0.036926 | 0.032605 | 0.0356 | 0.053728 | 0.0012455 | 0.029281 | 0 | -0.027466 | -0.022888 | -0.018311 | 0.073242 | 0.022888 | -0.1236 | 0.027466 | -0.009155 | -0.10986 | 0.045776 | 0.018311 | -0.045776 | -0.11902 | 0.10986 | -0.036621 | -122.0993 | 0.059509 | 0.068664 | 0.10528 | -122.1725 | 0.041199 | -0.032044 | -122.1268 | 0.11444 | -0.022888 | 0.009156 | -122.1542 | 0.16022 | 0.086975 | 0.064087 | -122.2961 | 0.13275 | 0.10529 | 0.07782 | -122.2916
2450.2344 | 122.3236 | -0.082397 | 122.1451 | 0.079041 | 0.043351 | 0.061823 | 0.0036145 | 0.032746 | -0.0070902 | 0.032355 | 0.17426 | 0.031323 | 0.034105 | 0.050524 | -0.00024989 | 0.029495 | 0.07782 | 0.10529 | 0.10986 | 0.045776 | 0.027466 | 0.054932 | -0.073242 | 0.1236 | 0.10529 | 0.027466 | 0.022888 | 0.009155 | -0.036621 | -0.082397 | 0.13733 | 0.009155 | -122.1176 | 0.18768 | 0.12817 | 0.11902 | -122.0673 | 0.045776 | 0 | -122.1222 | 0.20599 | 0.10986 | 0.10986 | -122.1359 | 0.10986 | 0.16022 | 0.19226 | -122.2183 | 0.10528 | 0.091552 | 0.18768 | -122.2275
2451.9844 | 122.3053 | -0.091553 | 122.1771 | 0.08667 | 0.044846 | 0.058832 | 0.0016919 | 0.029969 | 0.0016684 | 0.031928 | 0.059815 | 0.033246 | 0.035814 | 0.056078 | 0.00017731 | 0.027359 | 0.004578 | -0.064087 | -0.022888 | -0.018311 | 0.059509 | 0.018311 | -0.13275 | 0.018311 | -0.027466 | -0.10986 | 0.041199 | 0.036621 | -0.050354 | -0.10071 | 0.10986 | -0.041198 | -122.1176 | 0.027466 | 0.073242 | 0.11444 | -122.1725 | 0.041199 | -0.009155 | -122.1359 | 0.10986 | -0.01831 | -0.009155 | -122.1405 | 0.15106 | 0.096131 | 0.068665 | -122.3099 | 0.13275 | 0.12817 | 0.064087 | -122.2778
2453.7344 | 122.4014 | -0.059509 | 122.1359 | -0.027771 | 0.043564 | 0.061823 | 0.0016919 | 0.034242 | -0.0081582 | 0.030646 | 0.021668 | 0.029828 | 0.034105 | 0.052874 | -0.0036679 | 0.028854 | 0.022888 | 0.050354 | 0.073242 | 0.032043 | 0.054932 | 0.050354 | -0.091553 | 0.086975 | 0.10986 | 0.022888 | 0.009155 | 0.004578 | -0.027466 | -0.091553 | 0.10986 | -0.032044 | -122.081 | 0.10986 | 0.091552 | 0.1236 | -122.113 | 0.032043 | -0.032044 | -122.1268 | 0.14648 | 0.082397 | 0.11444 | -122.1313 | 0.11444 | 0.082397 | 0.13275 | -122.2275 | 0.068664 | 0.064087 | 0.16937 | -122.2275
2455.4219 | 122.3557 | -0.07782 | 122.1359 | 0.12482 | 0.04271 | 0.06225 | -0.0012987 | 0.031678 | -0.0062356 | 0.031714 | 0.14374 | 0.033032 | 0.031969 | 0.053515 | 0.00081811 | 0.02565 | 0.10529 | 0.10071 | 0.10986 | 0.07782 | 0.036621 | 0.082397 | -0.082397 | 0.14191 | 0.1236 | 0.032043 | -0.004578 | 0.004578 | 0.009155 | -0.073242 | 0.16022 | -0.004577 | -122.0993 | 0.17853 | 0.15564 | 0.16022 | -122.0306 | 0.086975 | 0.004578 | -122.1405 | 0.21973 | 0.10986 | 0.10529 | -122.1313 | 0.11444 | 0.18311 | 0.18768 | -122.2183 | 0.073242 | 0.082398 | 0.20142 | -122.2092
2457.1875 | 122.2504 | -0.10071 | 122.1863 | 0.010376 | 0.048905 | 0.061395 | 0.0016919 | 0.033387 | 0.0023092 | 0.03086 | -0.024109 | 0.035382 | 0.035814 | 0.055437 | 0.0012455 | 0.024795 | 0.041199 | -0.045776 | -0.018311 | -0.018311 | 0.082397 | 0.022888 | -0.10529 | 0.018311 | -0.013733 | -0.1236 | 0.054932 | 0.041199 | -0.059509 | -0.11444 | 0.1236 | -0.004578 | -122.1039 | 0.054932 | 0.082397 | 0.086975 | -122.1451 | 0.041199 | -0.013733 | -122.1313 | 0.11902 | -0.022888 | -0.009155 | -122.1451 | 0.18311 | 0.14191 | 0.082397 | -122.2916 | 0.15564 | 0.14191 | 0.086975 | -122.3007
2458.9375 | 122.2778 | -0.10986 | 122.2046 | -0.24902 | 0.042496 | 0.062677 | 0.0066053 | 0.031892 | -0.007731 | 0.031928 | -0.1767 | 0.030896 | 0.036668 | 0.055437 | -0.0034543 | 0.027786 | 0.059509 | 0.068665 | 0.054932 | 0.036621 | 0.064087 | 0.027466 | -0.10071 | 0.032043 | 0.059509 | -0.064087 | 0.032043 | 0.041199 | -0.050354 | -0.09613 | 0.13733 | 0.009155 | -122.1405 | 0.17853 | 0.14648 | 0.13733 | -122.1451 | 0.059509 | 0.013733 | -122.1725 | 0.14191 | 0.045776 | 0.032043 | -122.1634 | 0.17395 | 0.16937 | 0.16479 | -122.3053 | 0.14191 | 0.15106 | 0.16937 | -122.3007
2460.7031 | 122.2504 | -0.1236 | 122.1542 | -0.24139 | 0.042923 | 0.061182 | 0.0057507 | 0.032746 | -0.0051676 | 0.031074 | -0.21484 | 0.031964 | 0.036027 | 0.053728 | -0.00089089 | 0.026077 | 0.004578 | 0.032043 | 0.009155 | 0.004578 | 0.059509 | 0.009155 | -0.10986 | 0.022888 | 0.050354 | -0.086975 | 0.041199 | 0.050354 | -0.068665 | -0.11902 | 0.13275 | 0.013733 | -122.0947 | 0.15564 | 0.12817 | 0.11444 | -122.1497 | 0.054931 | 0.004577 | -122.113 | 0.14648 | 0.036621 | 0.032044 | -122.1039 | 0.1831 | 0.12817 | 0.13275 | -122.2641 | 0.16479 | 0.17395 | 0.17395 | -122.2733
2462.4219 | 122.2687 | -0.10986 | 122.1863 | -0.21851 | 0.044205 | 0.061182 | 0.0038281 | 0.033814 | -0.0030314 | 0.028724 | -0.2301 | 0.032605 | 0.036241 | 0.049883 | -0.0021725 | 0.026291 | -0.013733 | -0.022888 | -0.013733 | -0.018311 | 0.082397 | 0.018311 | -0.13275 | 0.022888 | 0.027466 | -0.082397 | 0.045776 | 0.022888 | -0.059509 | -0.11444 | 0.12817 | -0.022888 | -122.1039 | 0.086975 | 0.091552 | 0.11444 | -122.2 | 0.050354 | -0.004578 | -122.1405 | 0.13275 | 0.027466 | 0.032044 | -122.1634 | 0.19226 | 0.09613 | 0.09613 | -122.319 | 0.15564 | 0.13275 | 0.13733 | -122.3007
2464.1719 | 122.406 | -0.054932 | 122.1863 | -0.050659 | 0.042069 | 0.063959 | 0.0012647 | 0.030824 | -0.0098672 | 0.03086 | -0.031738 | 0.031537 | 0.030901 | 0.053301 | -0.0025999 | 0.028854 | 0.054932 | 0.086975 | 0.09613 | 0.054932 | 0.041199 | 0.054932 | -0.086975 | 0.14648 | 0.13733 | 0.050354 | 0.004578 | 0.013733 | -0.022888 | -0.073242 | 0.10986 | -0.032043 | -122.1451 | 0.14191 | 0.10986 | 0.14191 | -122.1313 | 0.032044 | -0.01831 | -122.1817 | 0.20142 | 0.10529 | 0.1236 | -122.1725 | 0.096131 | 0.10986 | 0.15106 | -122.2733 | 0.05951 | 0.068665 | 0.19226 | -122.2595
2465.875 | 122.2458 | -0.10986 | 122.1771 | -0.050659 | 0.0457 | 0.060541 | 0.0016919 | 0.033601 | 0.0012412 | 0.03086 | -0.062256 | 0.033032 | 0.036241 | 0.053301 | 0.0042361 | 0.024154 | 0.07782 | 0.013733 | 0.009155 | 0.004578 | 0.07782 | 0.022888 | -0.13275 | 0.050354 | 0.032043 | -0.10986 | 0.050354 | 0.045776 | -0.054932 | -0.11444 | 0.13275 | -0.022888 | -122.0993 | 0.1236 | 0.11444 | 0.13733 | -122.0993 | 0.054931 | -0.004578 | -122.1268 | 0.16022 | 0 | 0.004578 | -122.1313 | 0.18768 | 0.18768 | 0.11902 | -122.3099 | 0.16022 | 0.15564 | 0.14191 | -122.2916
2467.6406 | 122.2824 | -0.086975 | 122.1909 | 0.063782 | 0.045273 | 0.059259 | 0.0012647 | 0.031465 | 0.0012412 | 0.032142 | 0.075073 | 0.032605 | 0.03325 | 0.053942 | 0.0029543 | 0.025436 | -0.009155 | -0.045776 | -0.045776 | -0.041199 | 0.073242 | 0.032043 | -0.12817 | 0.018311 | -0.027466 | -0.11444 | 0.054932 | 0.036621 | -0.054932 | -0.1236 | 0.11902 | -0.041199 | -122.1176 | 0.041199 | 0.045776 | 0.086975 | -122.2 | 0.032043 | -0.036621 | -122.1359 | 0.10529 | -0.027466 | 0.009155 | -122.1542 | 0.16022 | 0.07782 | 0.041199 | -122.319 | 0.14191 | 0.1236 | 0.059509 | -122.3145
2469.3281 | 122.2458 | -0.10529 | 122.1725 | -0.088806 | 0.045914 | 0.059045 | 0.0036145 | 0.029542 | -0.0017496 | 0.03321 | -0.1004 | 0.031964 | 0.034532 | 0.055437 | 0.0033817 | 0.023941 | 0.073242 | 0.045776 | 0.041199 | 0.013733 | 0.045776 | 0.022888 | -0.10529 | 0.064087 | 0.068665 | -0.073242 | 0.045776 | 0.027466 | -0.036621 | -0.10529 | 0.12817 | 0 | -122.1268 | 0.15106 | 0.11902 | 0.11902 | -122.0993 | 0.068665 | 0 | -122.1268 | 0.16937 | 0.032044 | 0.032044 | -122.1451 | 0.15106 | 0.17853 | 0.14649 | -122.2778 | 0.15106 | 0.13275 | 0.17395 | -122.2778
2471.0938 | 122.3419 | -0.059509 | 122.1405 | 0.079041 | 0.041855 | 0.061609 | 0.0044691 | 0.033601 | -0.0087992 | 0.031714 | 0.17426 | 0.029828 | 0.035387 | 0.056078 | -0.0032407 | 0.027145 | 0.073242 | 0.10071 | 0.086975 | 0.036621 | 0.022888 | 0.045776 | -0.086975 | 0.10986 | 0.10529 | 0.004578 | 0 | -0.004578 | -0.041199 | -0.082397 | 0.10528 | -0.027466 | -122.1176 | 0.16022 | 0.09613 | 0.1236 | -122.0673 | 0.01831 | -0.022888 | -122.1405 | 0.16937 | 0.064087 | 0.086975 | -122.1451 | 0.082397 | 0.13275 | 0.14648 | -122.2275 | 0.059509 | 0.054931 | 0.16479 | -122.2229
2472.8594 | 122.2916 | -0.11902 | 122.1863 | -0.18036 | 0.045914 | 0.061395 | 0.0061781 | 0.033814 | -0.0058084 | 0.030006 | -0.16144 | 0.030042 | 0.03795 | 0.053515 | -0.0051633 | 0.02864 | 0.073242 | 0.12817 | 0.10529 | 0.064087 | 0.036621 | 0.041199 | -0.10529 | 0.091553 | 0.13733 | 0.013733 | 0.027466 | -0.004578 | -0.022888 | -0.07782 | 0.16022 | 0.013733 | -122.1497 | 0.24719 | 0.18311 | 0.16937 | -122.113 | 0.096131 | 0.041199 | -122.1588 | 0.21057 | 0.13275 | 0.091553 | -122.1909 | 0.15564 | 0.19226 | 0.22431 | -122.2916 | 0.14649 | 0.11444 | 0.25635 | -122.2641
2474.5469 | 122.2824 | -0.11902 | 122.2046 | 0.048523 | 0.047196 | 0.060114 | 0.00041005 | 0.032105 | -0.0013224 | 0.031714 | 0.021668 | 0.030683 | 0.034532 | 0.055224 | 0.00017731 | 0.026291 | -0.022888 | -0.045776 | -0.064087 | -0.027466 | 0.086975 | 0.027466 | -0.11902 | 0.018311 | -0.027466 | -0.1236 | 0.045776 | 0.018311 | -0.045776 | -0.10529 | 0.14649 | 0 | -122.1176 | 0.073243 | 0.091553 | 0.091553 | -122.2275 | 0.073243 | 0.013733 | -122.1588 | 0.13733 | -0.004577 | -0.01831 | -122.1863 | 0.20599 | 0.096131 | 0.054932 | -122.3236 | 0.16479 | 0.13733 | 0.091553 | -122.3099
2476.2969 | 122.2916 | -0.091553 | 122.1725 | -0.20325 | 0.044632 | 0.062677 | 0.0053235 | 0.033814 | -0.006663 | 0.032996 | -0.11566 | 0.029828 | 0.036241 | 0.052874 | -0.0019589 | 0.026504 | 0.073242 | 0.14648 | 0.10986 | 0.073242 | 0.054932 | 0.059509 | -0.09613 | 0.10986 | 0.16479 | 0.027466 | 0.004578 | 0.013733 | -0.009155 | -0.086975 | 0.15106 | -0.004577 | -122.1176 | 0.23804 | 0.16479 | 0.16937 | -122.0993 | 0.082398 | 0.004578 | -122.168 | 0.20142 | 0.11902 | 0.11444 | -122.1588 | 0.14649 | 0.16479 | 0.20142 | -122.2687 | 0.096131 | 0.10529 | 0.25635 | -122.2595
2478.0625 | 122.2641 | -0.1236 | 122.1634 | -0.18799 | 0.043564 | 0.062036 | 0.0016919 | 0.034028 | -0.0047404 | 0.031714 | -0.22247 | 0.030469 | 0.0356 | 0.053728 | -0.0017453 | 0.025436 | 0.050354 | 0.1236 | 0.10986 | 0.054932 | 0.036621 | 0.050354 | -0.082397 | 0.07782 | 0.12817 | -0.013733 | 0.013733 | -0.004578 | -0.036621 | -0.091553 | 0.17395 | 0.041199 | -122.1268 | 0.24719 | 0.17853 | 0.13733 | -122.113 | 0.086975 | 0.032043 | -122.1497 | 0.20142 | 0.10986 | 0.07782 | -122.168 | 0.16022 | 0.17395 | 0.23346 | -122.2458 | 0.13733 | 0.11902 | 0.25177 | -122.2549
2479.8281 | 122.3511 | -0.07782 | 122.168 | -0.1651 | 0.042069 | 0.062463 | 0.0027601 | 0.031251 | -0.007731 | 0.02851 | -0.11566 | 0.030042 | 0.035814 | 0.053301 | -0.0023861 | 0.027145 | 0.07782 | 0.15106 | 0.11444 | 0.068665 | 0.036621 | 0.064087 | -0.082397 | 0.14648 | 0.19226 | 0.059509 | 0.004578 | 0.004578 | -0.009155 | -0.064087 | 0.14191 | -0.004577 | -122.1313 | 0.22888 | 0.14649 | 0.15106 | -122.0901 | 0.068665 | 0.013733 | -122.1634 | 0.2243 | 0.13733 | 0.1236 | -122.1634 | 0.11444 | 0.15564 | 0.19226 | -122.2504 | 0.082398 | 0.082398 | 0.27008 | -122.2321
2481.5938 | 123.8342 | -0.09613 | 122.1542 | -0.19562 | 0.044419 | 0.062036 | 0.0036145 | 0.029542 | -0.0051676 | 0.029151 | -0.13855 | 0.030042 | 0.03325 | 0.05266 | 0.00039091 | 0.026504 | 0.068665 | -0.059509 | 0.086975 | 0.50812 | 0.050354 | 0.054932 | -0.07782 | 1.2314 | 0.18768 | 0.2655 | 0.004578 | 0.013733 | -0.018311 | -0.07782 | 0.15106 | 0.01831 | -122.1039 | 0.036621 | 0.60425 | 0.58594 | -122.0856 | 0.077819 | 0.01831 | -122.1497 | 1.3275 | 0.36163 | 0.34332 | -122.1405 | 0.14648 | 0.16479 | 0.1831 | -122.2321 | 0.10071 | 0.10986 | 0.28381 | -122.2321
2483.2969 | 122.4976 | -0.091553 | 122.1634 | -0.19562 | 0.046555 | 0.059686 | 0.0042555 | 0.034028 | -0.00068138 | 0.031287 | -0.22247 | 0.031964 | 0.036241 | 0.055224 | 0.0012455 | 0.025436 | 0.032043 | 0.17395 | 0.59052 | 0.21057 | 0.086975 | 0 | -0.13733 | 0.10071 | 0.21515 | 0.009155 | 0.054932 | 0.027466 | -0.064087 | -0.1236 | 0.091553 | -0.045776 | -122.0764 | 0.2655 | 0.30212 | 0.3479 | -122.1313 | 0.027466 | -0.032043 | -122.1085 | 0.19226 | 0.10071 | 0.13275 | -122.1359 | 0.17853 | 0.1236 | 0.68207 | -122.3007 | 0.14649 | 0.11902 | 0.3067 | -122.287
2485.0469 | 122.5525 | -0.068665 | 122.1588 | 0.094299 | 0.041428 | 0.062463 | -0.00044435 | 0.029328 | -0.0068766 | 0.032142 | 0.097962 | 0.030042 | 0.032823 | 0.052233 | -0.00046349 | 0.026718 | 0.068665 | 0.18768 | 0.52643 | 0.26093 | 0.032043 | 0.045776 | -0.082397 | 0.28839 | 0.26093 | 0.050354 | 0.013733 | -0.004578 | -0.004578 | -0.082397 | 0.11444 | -0.013732 | -122.1268 | 0.25635 | 0.32959 | 0.34332 | -122.0901 | 0.064087 | -0.013732 | -122.1451 | 0.35706 | 0.11902 | 0.13275 | -122.1634 | 0.10071 | 0.13733 | 0.59509 | -122.2412 | 0.082398 | 0.064087 | 0.32959 | -122.2412
2486.8125 | 122.4792 | -0.054932 | 122.1542 | 0.16296 | 0.043137 | 0.061609 | 0.00019645 | 0.031465 | -0.0017496 | 0.031714 | 0.14374 | 0.032178 | 0.033037 | 0.054796 | 0.0031681 | 0.026504 | 0.1236 | 0.12817 | 0.54474 | 0.67291 | 0.045776 | 0.036621 | -0.082397 | 0.36163 | 0.5127 | 0.35248 | 0 | 0 | -0.013733 | -0.059509 | 0.091553 | -0.027465 | -122.1085 | 0.18311 | 0.72784 | 0.75531 | -122.0306 | 0.041199 | -0.004577 | -122.1542 | 0.41656 | 0.40741 | 0.41199 | -122.1542 | 0.10071 | 0.17853 | 0.59967 | -122.2366 | 0.054932 | 0.054932 | 0.56763 | -122.2137
2488.5 | 122.3557 | -0.09613 | 122.1863 | -0.20325 | 0.047196 | 0.060754 | 0.0053235 | 0.033387 | -0.0030314 | 0.031287 | -0.13855 | 0.030255 | 0.03261 | 0.053728 | -0.00024989 | 0.027145 | 0.082397 | 0.20142 | 0.29297 | 0.13733 | 0.027466 | 0.041199 | -0.07782 | 0.14648 | 0.23346 | 0.073242 | 0.009155 | -0.009155 | -0.022888 | -0.07782 | 0.13733 | 0.01831 | -122.1588 | 0.29755 | 0.23346 | 0.21515 | -122.1039 | 0.073242 | 0.01831 | -122.1771 | 0.24261 | 0.16937 | 0.15106 | -122.1954 | 0.1236 | 0.17853 | 0.3891 | -122.2641 | 0.10528 | 0.086975 | 0.32959 | -122.2641
2490.25 | 122.4014 | -0.068665 | 122.1634 | 0.094299 | 0.042923 | 0.0599 | 0.00062385 | 0.034242 | 0.00017302 | 0.034278 | 0.044556 | 0.032819 | 0.033678 | 0.055437 | 0.0020999 | 0.027359 | 0.027466 | 0.004578 | 0 | 0.004578 | 0.07782 | 0.032043 | -0.1236 | 0.059509 | 0.009155 | -0.064087 | 0.045776 | 0.018311 | -0.022888 | -0.10529 | 0.10071 | -0.054931 | -122.0856 | 0.073243 | 0.073243 | 0.12817 | -122.1359 | 0.045777 | -0.036621 | -122.1176 | 0.12817 | 0.004578 | 0.041199 | -122.1451 | 0.14649 | 0.096131 | 0.068665 | -122.287 | 0.11444 | 0.086976 | 0.07782 | -122.2687
2492.0156 | 122.3511 | -0.091553 | 122.1497 | 0.094299 | 0.042069 | 0.061182 | 0.0014783 | 0.033387 | -0.0073038 | 0.031928 | 0.12848 | 0.030255 | 0.032823 | 0.05031 | 0.0010317 | 0.026504 | 0.10529 | 0.09613 | 0.10986 | 0.073242 | 0.045776 | 0.064087 | -0.07782 | 0.13733 | 0.1236 | 0.004578 | 0.004578 | -0.018311 | -0.004578 | -0.086975 | 0.15564 | 0.013733 | -122.1039 | 0.18768 | 0.16479 | 0.15106 | -122.0444 | 0.086975 | 0.004578 | -122.1451 | 0.22888 | 0.096131 | 0.091553 | -122.168 | 0.13733 | 0.19684 | 0.20142 | -122.2275 | 0.096131 | 0.073242 | 0.21515 | -122.2366
2493.7031 | 122.374 | -0.07782 | 122.1634 | -0.1651 | 0.043991 | 0.06225 | 0.0059643 | 0.032746 | -0.0068766 | 0.031714 | -0.16144 | 0.031323 | 0.034318 | 0.051592 | -0.00089089 | 0.024368 | 0.11444 | 0.15106 | 0.14191 | 0.082397 | 0.064087 | 0.054932 | -0.086975 | 0.14648 | 0.17395 | 0.045776 | -0.009155 | -0.009155 | -0.027466 | -0.086975 | 0.13275 | -0.009155 | -122.0993 | 0.22888 | 0.16022 | 0.16937 | -122.049 | 0.050354 | -0.009155 | -122.1725 | 0.2243 | 0.1236 | 0.13275 | -122.1725 | 0.14191 | 0.19226 | 0.21973 | -122.2504 | 0.068665 | 0.068665 | 0.25177 | -122.2504
2495.4375 | 122.3923 | -0.09613 | 122.1954 | -0.24139 | 0.046555 | 0.062463 | 0.0072461 | 0.034028 | -0.0011088 | 0.031074 | -0.23773 | 0.03111 | 0.037523 | 0.054796 | 0.0025271 | 0.0233 | 0.018311 | 0.018311 | 0.17853 | 0.045776 | 0.068665 | 0.013733 | -0.13733 | 0.036621 | 0.068665 | -0.07782 | 0.059509 | 0.027466 | -0.086975 | -0.1236 | 0.10986 | -0.041199 | -122.1268 | 0.11444 | 0.14191 | 0.18311 | -122.1771 | 0.009155 | -0.027466 | -122.1359 | 0.13275 | 0.01831 | 0.045776 | -122.168 | 0.16479 | 0.11444 | 0.27466 | -122.3328 | 0.15564 | 0.1236 | 0.16479 | -122.319
2497.1875 | 122.3373 | -0.10529 | 122.2 | -0.25665 | 0.045914 | 0.063532 | 0.0038281 | 0.032533 | -0.0040994 | 0.029151 | -0.24536 | 0.030896 | 0.035173 | 0.053301 | -0.00089089 | 0.02565 | 0.004578 | 0.022888 | 0.13275 | 0.013733 | 0.082397 | 0.004578 | -0.11444 | 0.041199 | 0.064087 | -0.068665 | 0.050354 | 0.041199 | -0.059509 | -0.11902 | 0.10986 | -0.009155 | -122.1176 | 0.12817 | 0.11902 | 0.12817 | -122.1954 | 0.045777 | -0.013733 | -122.1497 | 0.14649 | 0.036621 | 0.050354 | -122.1588 | 0.18768 | 0.10986 | 0.23804 | -122.3145 | 0.15564 | 0.14649 | 0.16937 | -122.319
2498.9375 | 122.4518 | -0.050354 | 122.168 | 0.12482 | 0.044846 | 0.060541 | -0.00023075 | 0.032533 | -4.058e-05 | 0.034064 | 0.13611 | 0.032178 | 0.033464 | 0.05501 | 0.0038089 | 0.026077 | 0.032043 | 0.027466 | 0.13275 | 0.050354 | 0.054932 | 0.032043 | -0.11444 | 0.13275 | 0.10529 | 0.004578 | 0.022888 | 0.009155 | -0.041199 | -0.10071 | 0.082397 | -0.064087 | -122.113 | 0.07782 | 0.10071 | 0.16479 | -122.1359 | 0.009155 | -0.050354 | -122.1451 | 0.18311 | 0.054932 | 0.10529 | -122.1588 | 0.10529 | 0.082397 | 0.18311 | -122.2824 | 0.073242 | 0.059509 | 0.15564 | -122.2687
2500.6406 | 122.319 | -0.10071 | 122.2321 | -0.096436 | 0.046128 | 0.062036 | 0.0040417 | 0.032746 | 0.0020956 | 0.03321 | -0.10803 | 0.033246 | 0.033464 | 0.054583 | 0.0029543 | 0.026077 | 0.073242 | 0.073242 | 0.16022 | 0.059509 | 0.050354 | 0.027466 | -0.10529 | 0.082397 | 0.091553 | -0.050354 | 0.045776 | 0.032043 | -0.045776 | -0.10529 | 0.12817 | -0.004578 | -122.1817 | 0.17395 | 0.16022 | 0.16479 | -122.1588 | 0.054932 | -0.004578 | -122.1863 | 0.18311 | 0.050354 | 0.054932 | -122.2 | 0.15106 | 0.17395 | 0.26093 | -122.3373 | 0.14648 | 0.13275 | 0.19226 | -122.3373
2502.3906 | 122.3465 | -0.11444 | 122.1725 | 0.048523 | 0.048264 | 0.058618 | 0.0038281 | 0.03296 | -0.0019632 | 0.033423 | -0.0012209 | 0.031964 | 0.039873 | 0.054156 | 0.0023135 | 0.026718 | -0.004578 | -0.027466 | 0.10529 | 0.013733 | 0.064087 | 0.032043 | -0.10071 | 0.009155 | 0.004578 | -0.1236 | 0.054932 | 0.027466 | -0.041199 | -0.10529 | 0.14648 | 0.013733 | -122.1085 | 0.086975 | 0.12817 | 0.11444 | -122.1771 | 0.073242 | 0.009155 | -122.1176 | 0.1236 | -0.009155 | -0.01831 | -122.1451 | 0.17853 | 0.10986 | 0.21973 | -122.2733 | 0.16937 | 0.14191 | 0.11902 | -122.2778
2504.1406 | 122.4243 | -0.073242 | 122.1634 | 0.10193 | 0.042496 | 0.0599 | 0.0014783 | 0.031678 | -0.0023904 | 0.03321 | 0.075073 | 0.03346 | 0.034105 | 0.054369 | 0.0023135 | 0.027999 | -0.004578 | -0.004578 | 0.13275 | 0.013733 | 0.082397 | 0.018311 | -0.11902 | 0.054932 | 0.022888 | -0.086975 | 0.045776 | 0.032043 | -0.050354 | -0.10986 | 0.091553 | -0.045777 | -122.081 | 0.068664 | 0.086975 | 0.13275 | -122.168 | 0.022888 | -0.036621 | -122.1176 | 0.12817 | -0.013733 | 0.022888 | -122.1313 | 0.15564 | 0.068664 | 0.20599 | -122.2824 | 0.11902 | 0.10529 | 0.09613 | -122.2733
2505.8906 | 122.3373 | -0.091553 | 122.1451 | 0.079041 | 0.044846 | 0.059473 | 0.0014783 | 0.030397 | -0.00068138 | 0.033637 | 0.090332 | 0.03111 | 0.036668 | 0.055224 | -0.00024989 | 0.028213 | -0.027466 | -0.018311 | 0.10529 | 0.018311 | 0.086975 | 0.018311 | -0.13275 | 0.050354 | 0.009155 | -0.10071 | 0.059509 | 0.041199 | -0.068665 | -0.09613 | 0.10986 | -0.041198 | -122.0581 | 0.073242 | 0.10986 | 0.15106 | -122.1725 | 0.022888 | -0.004577 | -122.0856 | 0.14191 | -0.009155 | -0.004578 | -122.1039 | 0.17853 | 0.064087 | 0.19684 | -122.2778 | 0.15106 | 0.13275 | 0.10071 | -122.2412
2507.6406 | 122.4014 | -0.073242 | 122.1451 | 0.0027468 | 0.042496 | 0.063959 | 0.0046827 | 0.031892 | -0.0087992 | 0.030646 | 0.097962 | 0.02876 | 0.034746 | 0.054156 | -0.00067729 | 0.029068 | -0.004578 | 0.086975 | 0.1831 | 0.07782 | 0.050354 | 0.041199 | -0.07782 | 0.082397 | 0.11444 | 0.013733 | 0.018311 | 0.009155 | -0.027466 | -0.07782 | 0.11444 | -0.004578 | -122.0947 | 0.16022 | 0.15106 | 0.15564 | -122.1497 | 0.045776 | -0.004578 | -122.1268 | 0.15564 | 0.086975 | 0.091553 | -122.1359 | 0.1236 | 0.068664 | 0.25635 | -122.2229 | 0.091553 | 0.082397 | 0.18768 | -122.2229
2509.3906 | 122.4289 | -0.064087 | 122.1405 | 0.010376 | 0.042282 | 0.062891 | 0.0016919 | 0.031251 | -0.0064492 | 0.034064 | 0.067444 | 0.030255 | 0.034318 | 0.053728 | -0.0015317 | 0.025009 | 0.004578 | 0.054932 | 0.19684 | 0.059509 | 0.059509 | 0.054932 | -0.09613 | 0.09613 | 0.11444 | 0.018311 | 0.022888 | 0.013733 | -0.027466 | -0.09613 | 0.11902 | -0.032043 | -122.081 | 0.11902 | 0.1236 | 0.15564 | -122.1359 | 0.036621 | -0.032043 | -122.1176 | 0.16022 | 0.082398 | 0.11444 | -122.1268 | 0.1236 | 0.068665 | 0.26093 | -122.2366 | 0.086975 | 0.07782 | 0.17853 | -122.2366
2511.0938 | 122.4289 | -0.054932 | 122.1268 | 0.16296 | 0.043778 | 0.059045 | 0.00083745 | 0.029328 | 0.00038662 | 0.034278 | 0.12085 | 0.03111 | 0.034746 | 0.055224 | 0.0035953 | 0.023941 | 0.032043 | 0.032043 | 0.14191 | 0.064087 | 0.064087 | 0.041199 | -0.10071 | 0.13275 | 0.10986 | 0.022888 | 0.009155 | 0.009155 | -0.018311 | -0.082397 | 0.096131 | -0.045776 | -122.0627 | 0.086975 | 0.11902 | 0.1648 | -122.0947 | 0.036621 | -0.027465 | -122.1176 | 0.18768 | 0.07782 | 0.10528 | -122.1176 | 0.11902 | 0.086975 | 0.19684 | -122.2275 | 0.064087 | 0.064087 | 0.16479 | -122.2092
2512.8594 | 122.4289 | -0.059509 | 122.1542 | 0.063782 | 0.042069 | 0.060968 | 0.0012647 | 0.034028 | -0.0038858 | 0.03086 | 0.15137 | 0.030255 | 0.034746 | 0.053301 | 0.0031681 | 0.026077 | 0.09613 | 0.10986 | 0.20142 | 0.11902 | 0.050354 | 0.059509 | -0.073242 | 0.16022 | 0.16022 | 0.036621 | 0.018311 | -0.004578 | -0.009155 | -0.07782 | 0.11902 | -0.013733 | -122.1039 | 0.16937 | 0.17853 | 0.19226 | -122.0581 | 0.050354 | -0.018311 | -122.1359 | 0.21973 | 0.09613 | 0.11444 | -122.1588 | 0.10986 | 0.15564 | 0.26093 | -122.2275 | 0.07782 | 0.054931 | 0.21973 | -122.2321
2514.625 | 122.2778 | -0.10986 | 122.2092 | -0.065918 | 0.044632 | 0.063318 | 0.00041005 | 0.035523 | -0.00068138 | 0.03321 | -0.077515 | 0.031964 | 0.0356 | 0.054369 | 0.0033817 | 0.025863 | 0.050354 | 0.045776 | 0.082397 | 0.13733 | 0.064087 | 0.050354 | -0.10986 | 0.07782 | 0.073242 | -0.027466 | 0.050354 | 0.045776 | -0.054932 | -0.10986 | 0.16022 | 0 | -122.1451 | 0.15564 | 0.24719 | 0.24719 | -122.1588 | 0.054931 | 0 | -122.1588 | 0.18768 | 0.082397 | 0.082397 | -122.1634 | 0.17395 | 0.16022 | 0.19226 | -122.319 | 0.16022 | 0.15564 | 0.18311 | -122.319
2516.3125 | 122.287 | -0.10986 | 122.2046 | -0.13458 | 0.043778 | 0.062036 | 0.0066053 | 0.03296 | -0.004313 | 0.031714 | -0.22247 | 0.02876 | 0.035173 | 0.052233 | -0.00067729 | 0.026077 | 0 | 0.004578 | 0.13275 | 0.07782 | 0.073242 | 0.018311 | -0.11902 | 0.068665 | 0.10986 | 0.009155 | 0.050354 | 0.036621 | -0.054932 | -0.1236 | 0.12817 | -0.009156 | -122.1313 | 0.11444 | 0.18768 | 0.19684 | -122.2046 | 0.054931 | -0.013733 | -122.1542 | 0.17853 | 0.11902 | 0.13275 | -122.168 | 0.18311 | 0.10986 | 0.24261 | -122.3236 | 0.16022 | 0.14648 | 0.21973 | -122.3282
2518.0625 | 122.319 | -0.082397 | 122.1634 | -0.13458 | 0.048264 | 0.060541 | 0.0038281 | 0.03296 | 0.00060022 | 0.032355 | -0.16144 | 0.031323 | 0.036668 | 0.055437 | -0.0015317 | 0.027999 | 0.036621 | 0.045776 | 0.14648 | 0.14648 | 0.082397 | 0.009155 | -0.11444 | 0.10529 | 0.16937 | 0.073242 | 0.041199 | 0.022888 | -0.032043 | -0.091553 | 0.091552 | -0.032044 | -122.081 | 0.12817 | 0.22888 | 0.26093 | -122.1268 | 0.050354 | -0.009156 | -122.1222 | 0.18768 | 0.15564 | 0.16479 | -122.1405 | 0.16479 | 0.11902 | 0.22888 | -122.2778 | 0.1236 | 0.10528 | 0.25177 | -122.2549
2519.8125 | 122.3145 | -0.086975 | 122.1863 | -0.11932 | 0.047196 | 0.060327 | 0.0027601 | 0.031678 | -0.00068138 | 0.032142 | -0.13855 | 0.030255 | 0.034959 | 0.054796 | 0.00017731 | 0.026718 | 0.036621 | 0.041199 | 0.041199 | 0.027466 | 0.073242 | 0.022888 | -0.09613 | 0.073242 | 0.073242 | -0.064087 | 0.045776 | 0.027466 | -0.032043 | -0.10071 | 0.10986 | -0.009155 | -122.113 | 0.12817 | 0.11444 | 0.1236 | -122.1497 | 0.054932 | -0.013733 | -122.1405 | 0.16022 | 0.022888 | 0.036621 | -122.1588 | 0.16022 | 0.1236 | 0.12817 | -122.2824 | 0.13275 | 0.11444 | 0.16022 | -122.287
2521.5 | 122.3282 | -0.10529 | 122.1863 | -0.22614 | 0.046768 | 0.061609 | 0.0016919 | 0.031678 | -0.0023904 | 0.031928 | -0.1767 | 0.031751 | 0.037736 | 0.05266 | -0.00046349 | 0.027572 | -0.027466 | 0.004578 | -0.027466 | -0.022888 | 0.086975 | 0 | -0.13275 | 0.013733 | 0.027466 | -0.086975 | 0.068665 | 0.018311 | -0.068665 | -0.10986 | 0.10529 | -0.027465 | -122.0993 | 0.10986 | 0.082398 | 0.10986 | -122.2137 | 0.036621 | -0.004577 | -122.1176 | 0.11902 | 0.018311 | 0.022888 | -122.168 | 0.19226 | 0.07782 | 0.07782 | -122.319 | 0.17395 | 0.1236 | 0.13275 | -122.2961
2523.2656 | 122.3053 | -0.11902 | 122.1771 | -0.24902 | 0.045487 | 0.061182 | 0.0059643 | 0.028474 | -0.0021768 | 0.032569 | -0.19958 | 0.030683 | 0.037096 | 0.054583 | -0.0011045 | 0.026504 | -0.041199 | -0.004578 | -0.032043 | -0.009155 | 0.07782 | 0.018311 | -0.11902 | 0.018311 | 0.032043 | -0.091553 | 0.054932 | 0.036621 | -0.050354 | -0.11902 | 0.13733 | 0 | -122.0993 | 0.11444 | 0.10986 | 0.10986 | -122.2183 | 0.068665 | 0 | -122.1222 | 0.13733 | 0.027466 | 0.027466 | -122.1405 | 0.19684 | 0.07782 | 0.086976 | -122.2961 | 0.17395 | 0.15564 | 0.15106 | -122.2961
2525.0312 | 122.3785 | -0.07782 | 122.1542 | 0.033264 | 0.04271 | 0.061395 | 0.0029737 | 0.031678 | -0.0098672 | 0.032996 | 0.067444 | 0.028333 | 0.035173 | 0.054156 | -0.0021725 | 0.028213 | 0.009155 | 0.068665 | 0.064087 | 0.018311 | 0.054932 | 0.045776 | -0.07782 | 0.07782 | 0.086975 | -0.009155 | 0.018311 | 0.013733 | -0.018311 | -0.068665 | 0.1236 | 0 | -122.0993 | 0.14649 | 0.096131 | 0.096131 | -122.1451 | 0.059509 | 0.009155 | -122.1359 | 0.15564 | 0.068665 | 0.05951 | -122.1405 | 0.13275 | 0.086975 | 0.14191 | -122.2321 | 0.096131 | 0.091553 | 0.16479 | -122.2229
2526.7812 | 122.3831 | -0.082397 | 122.1542 | -0.0048827 | 0.039505 | 0.062677 | 0.0040417 | 0.032319 | -0.0090128 | 0.029792 | 0.075073 | 0.03111 | 0.034105 | 0.054796 | -0.0025999 | 0.024154 | 0.009155 | 0.059509 | 0.059509 | 0.032043 | 0.050354 | 0.059509 | -0.086975 | 0.07782 | 0.068665 | 0 | 0.013733 | -0.009155 | -0.018311 | -0.073242 | 0.14191 | -0.004578 | -122.1039 | 0.14191 | 0.11444 | 0.11902 | -122.1451 | 0.064086 | 0.009155 | -122.1405 | 0.16022 | 0.082397 | 0.073242 | -122.1634 | 0.13275 | 0.091552 | 0.14191 | -122.2412 | 0.09613 | 0.073242 | 0.15106 | -122.2275
2528.4844 | 122.3145 | -0.10529 | 122.1863 | -0.21088 | 0.04506 | 0.061609 | 0.0057507 | 0.032746 | -0.0017496 | 0.033423 | -0.19958 | 0.032392 | 0.035387 | 0.053728 | 0.00017731 | 0.022873 | -0.004578 | -0.013733 | -0.027466 | -0.032043 | 0.068665 | 0.032043 | -0.13733 | 0.018311 | 0.041199 | -0.09613 | 0.068665 | 0.050354 | -0.054932 | -0.10529 | 0.13733 | -0.032043 | -122.1176 | 0.091553 | 0.073243 | 0.10529 | -122.1909 | 0.050354 | 0 | -122.1176 | 0.1236 | 0.009156 | 0.009156 | -122.1359 | 0.17395 | 0.10071 | 0.07782 | -122.3236 | 0.17395 | 0.15564 | 0.14649 | -122.2916
2530.2344 | 122.3648 | -0.073242 | 122.1725 | 0.14008 | 0.042923 | 0.061609 | -0.0017261 | 0.035737 | -0.006022 | 0.032569 | 0.12848 | 0.030683 | 0.033678 | 0.051592 | 0.0012455 | 0.026504 | 0.091553 | 0.11902 | 0.1236 | 0.041199 | 0.022888 | 0.050354 | -0.07782 | 0.14191 | 0.13275 | 0.027466 | 0 | 0.009155 | -0.004578 | -0.07782 | 0.1236 | -0.004578 | -122.1497 | 0.19226 | 0.11444 | 0.11902 | -122.081 | 0.068664 | -0.004578 | -122.1725 | 0.21515 | 0.10071 | 0.10529 | -122.1634 | 0.09613 | 0.16479 | 0.19684 | -122.2504 | 0.073242 | 0.082397 | 0.20599 | -122.2504
2531.9844 | 122.3694 | -0.07782 | 122.1817 | 0.10193 | 0.042923 | 0.061609 | -0.00044435 | 0.032533 | -0.006663 | 0.030433 | 0.12848 | 0.030042 | 0.033678 | 0.051592 | 0.0010317 | 0.02565 | 0.09613 | 0.11444 | 0.10986 | 0.059509 | 0.036621 | 0.068665 | -0.068665 | 0.14191 | 0.10986 | 0.032043 | 0.009155 | 0.013733 | -0.027466 | -0.068665 | 0.14649 | 0.009155 | -122.1451 | 0.19226 | 0.13733 | 0.12817 | -122.0856 | 0.050354 | 0.009155 | -122.1725 | 0.21973 | 0.10986 | 0.10071 | -122.168 | 0.11444 | 0.17395 | 0.18768 | -122.2504 | 0.086975 | 0.091553 | 0.18768 | -122.2504
2533.6719 | 122.2733 | -0.10529 | 122.2229 | 0.0027468 | 0.051255 | 0.059473 | 0.0044691 | 0.030824 | 0.003591 | 0.036201 | -0.039368 | 0.034314 | 0.038164 | 0.05501 | 0.0029543 | 0.023086 | 0.013733 | -0.032043 | -0.022888 | -0.027466 | 0.086975 | 0.018311 | -0.11902 | 0 | -0.022888 | -0.1236 | 0.045776 | 0.068665 | -0.059509 | -0.09613 | 0.1236 | -0.013733 | -122.1359 | 0.073243 | 0.07782 | 0.091553 | -122.2092 | 0.045777 | 0.009156 | -122.1771 | 0.10529 | -0.01831 | -0.027466 | -122.1542 | 0.19226 | 0.11902 | 0.082398 | -122.3419 | 0.15106 | 0.17395 | 0.082398 | -122.319
2535.4219 | 122.3877 | -0.054932 | 122.1634 | 0.0027468 | 0.043991 | 0.060114 | 0.0042555 | 0.032105 | -0.0073038 | 0.030646 | 0.052185 | 0.028119 | 0.037096 | 0.052233 | -0.0040951 | 0.02565 | 0.022888 | 0.073242 | 0.068665 | 0.036621 | 0.059509 | 0.054932 | -0.07782 | 0.086975 | 0.068665 | -0.022888 | 0.009155 | 0.022888 | -0.036621 | -0.086975 | 0.10986 | -0.022888 | -122.1039 | 0.12817 | 0.091553 | 0.11444 | -122.1405 | 0.018311 | -0.032043 | -122.1542 | 0.14191 | 0.032044 | 0.064087 | -122.1405 | 0.11444 | 0.07782 | 0.1236 | -122.2412 | 0.064087 | 0.07782 | 0.1236 | -122.2504
2537.1875 | 122.3236 | -0.091553 | 122.2046 | 0.14771 | 0.044205 | 0.060327 | -1.7146e-05 | 0.031465 | -0.00089518 | 0.03556 | 0.082703 | 0.031323 | 0.036455 | 0.05501 | 0.0044497 | 0.025222 | 0.009155 | -0.045776 | -0.041199 | -0.022888 | 0.07782 | 0.013733 | -0.10986 | 0.022888 | -0.027466 | -0.09613 | 0.041199 | 0.050354 | -0.045776 | -0.09613 | 0.10529 | -0.01831 | -122.1268 | 0.045777 | 0.068665 | 0.086975 | -122.1954 | 0.045777 | -0.004577 | -122.1634 | 0.11444 | -0.004577 | 0 | -122.1542 | 0.16937 | 0.10071 | 0.050354 | -122.3145 | 0.13275 | 0.14191 | 0.064087 | -122.3007
2538.9531 | 122.319 | -0.10986 | 122.1954 | -0.1651 | 0.048264 | 0.061609 | 0.0051099 | 0.031465 | -0.00046778 | 0.031714 | -0.22247 | 0.033032 | 0.038591 | 0.053515 | 0.00017731 | 0.022445 | 0.022888 | -0.009155 | -0.013733 | 0.004578 | 0.073242 | 0.018311 | -0.12817 | 0.050354 | 0.054932 | -0.068665 | 0.054932 | 0.027466 | -0.064087 | -0.082397 | 0.12817 | -0.018311 | -122.1222 | 0.10071 | 0.11444 | 0.13275 | -122.1725 | 0.045776 | 0.027466 | -122.1405 | 0.16022 | 0.041198 | 0.013732 | -122.168 | 0.18311 | 0.13275 | 0.09613 | -122.3236 | 0.16479 | 0.13733 | 0.16479 | -122.2778
2540.7031 | 122.2961 | -0.10071 | 122.2 | -0.096436 | 0.047623 | 0.061395 | 0.0016919 | 0.032533 | -0.0011088 | 0.034705 | -0.12329 | 0.034741 | 0.034746 | 0.054583 | -3.629e-05 | 0.027359 | 0.045776 | 0.068665 | 0.022888 | 0.018311 | 0.059509 | 0.027466 | -0.10986 | 0.07782 | 0.086975 | -0.054932 | 0.032043 | 0.027466 | -0.041199 | -0.10071 | 0.12817 | -0.009155 | -122.1405 | 0.16937 | 0.11902 | 0.12817 | -122.1542 | 0.059509 | 0 | -122.168 | 0.17853 | 0.045776 | 0.045776 | -122.1725 | 0.16022 | 0.14648 | 0.1236 | -122.3099 | 0.13275 | 0.12817 | 0.18768 | -122.3007
2542.3906 | 122.3236 | -0.073242 | 122.1817 | 0.13245 | 0.043137 | 0.061395 | 0.0027601 | 0.03061 | -0.0017496 | 0.03321 | 0.097962 | 0.032819 | 0.036027 | 0.053515 | 0.0016727 | 0.025009 | -0.013733 | -0.036621 | -0.032043 | -0.013733 | 0.086975 | 0.004578 | -0.1236 | 0.032043 | -0.022888 | -0.091553 | 0.059509 | 0.032043 | -0.059509 | -0.11444 | 0.07782 | -0.050354 | -122.0947 | 0.036621 | 0.059509 | 0.10986 | -122.1954 | 0.013733 | -0.041199 | -122.1222 | 0.10529 | -0.018311 | 0.022888 | -122.1497 | 0.16022 | 0.059509 | 0.041199 | -122.3053 | 0.13275 | 0.10529 | 0.050354 | -122.2961
2544.1406 | 122.3602 | -0.068665 | 122.1634 | 0.14008 | 0.042282 | 0.062036 | 0.0012647 | 0.032533 | -0.007731 | 0.032569 | 0.159 | 0.030683 | 0.030687 | 0.052447 | 0.0014591 | 0.026931 | 0.07782 | 0.12817 | 0.10986 | 0.054932 | 0.022888 | 0.059509 | -0.07782 | 0.14191 | 0.1236 | 0.045776 | 0.009155 | -0.009155 | -0.018311 | -0.059509 | 0.12817 | -0.009155 | -122.1405 | 0.19684 | 0.1236 | 0.13275 | -122.0856 | 0.050354 | 0.009156 | -122.1542 | 0.21057 | 0.11444 | 0.10528 | -122.1725 | 0.091553 | 0.14649 | 0.17853 | -122.2412 | 0.07782 | 0.05951 | 0.19226 | -122.2229
2545.8906 | 122.2687 | -0.091553 | 122.2137 | -0.073547 | 0.047196 | 0.062036 | 0.0040417 | 0.031678 | -0.002604 | 0.031714 | -0.10803 | 0.034955 | 0.035814 | 0.05501 | 0.0018863 | 0.024582 | 0.073242 | 0.045776 | 0.027466 | 0.009155 | 0.041199 | 0.027466 | -0.10529 | 0.050354 | 0.050354 | -0.068665 | 0.045776 | 0.036621 | -0.041199 | -0.09613 | 0.11902 | -0.013733 | -122.1725 | 0.13733 | 0.10071 | 0.11444 | -122.1405 | 0.050354 | -0.004577 | -122.168 | 0.14191 | 0.022888 | 0.027465 | -122.1771 | 0.13275 | 0.16479 | 0.11902 | -122.319 | 0.13733 | 0.12817 | 0.14191 | -122.3099
2547.6406 | 122.3145 | -0.10529 | 122.168 | 0.10193 | 0.042923 | 0.060754 | 0.0014783 | 0.029328 | -0.00068138 | 0.034705 | 0.067444 | 0.032392 | 0.037096 | 0.052874 | 0.0012455 | 0.026077 | -0.022888 | -0.041199 | -0.036621 | -0.013733 | 0.073242 | 0.027466 | -0.1236 | 0.009155 | -0.027466 | -0.11444 | 0.064087 | 0.041199 | -0.050354 | -0.11444 | 0.13275 | -0.01831 | -122.0947 | 0.064087 | 0.091553 | 0.10986 | -122.1909 | 0.054932 | -0.009155 | -122.1039 | 0.11444 | -0.009155 | 0 | -122.1268 | 0.17853 | 0.082398 | 0.068665 | -122.2916 | 0.16937 | 0.14649 | 0.07782 | -122.2824
2549.3281 | 122.3602 | -0.082397 | 122.1405 | 0.08667 | 0.042069 | 0.060327 | 0.0010511 | 0.033601 | -0.0087992 | 0.03321 | 0.16663 | 0.030683 | 0.034532 | 0.052874 | -0.00067729 | 0.028427 | 0.064087 | 0.11444 | 0.09613 | 0.036621 | 0.036621 | 0.059509 | -0.086975 | 0.1236 | 0.10986 | 0.018311 | -0.004578 | -0.004578 | -0.032043 | -0.073242 | 0.14191 | -0.004578 | -122.1039 | 0.19684 | 0.11902 | 0.1236 | -122.0764 | 0.050354 | 0.009155 | -122.1451 | 0.20599 | 0.10071 | 0.091553 | -122.1451 | 0.11902 | 0.14648 | 0.17853 | -122.2275 | 0.077819 | 0.077819 | 0.19226 | -122.2137
2551.0938 | 122.3557 | -0.086975 | 122.168 | 0.10956 | 0.039719 | 0.060754 | 0.0036145 | 0.032533 | -0.0090128 | 0.031074 | 0.11322 | 0.030683 | 0.034318 | 0.053942 | -0.00046349 | 0.026291 | 0.068665 | 0.09613 | 0.091553 | 0.032043 | 0.045776 | 0.059509 | -0.086975 | 0.10071 | 0.082397 | -0.004578 | 0.022888 | 0.004578 | -0.018311 | -0.073242 | 0.14648 | 0 | -122.1222 | 0.1831 | 0.11902 | 0.11902 | -122.0993 | 0.068664 | 0.013733 | -122.1451 | 0.18768 | 0.082397 | 0.068664 | -122.1634 | 0.13275 | 0.15564 | 0.17853 | -122.2549 | 0.10986 | 0.091553 | 0.16937 | -122.2412
2552.7812 | 122.2961 | -0.10071 | 122.2137 | -0.21851 | 0.041642 | 0.063532 | 0.0063917 | 0.034455 | -0.0047404 | 0.031928 | -0.26062 | 0.030896 | 0.036027 | 0.054156 | -0.0023861 | 0.025009 | 0 | -0.013733 | -0.027466 | -0.027466 | 0.07782 | 0.027466 | -0.11444 | 0.004578 | 0.004578 | -0.09613 | 0.054932 | 0.054932 | -0.054932 | -0.11444 | 0.12817 | -0.013733 | -122.1359 | 0.086975 | 0.073242 | 0.086975 | -122.2137 | 0.045776 | -0.013733 | -122.1588 | 0.10529 | 0.004578 | 0.018311 | -122.1588 | 0.17853 | 0.10071 | 0.073242 | -122.3282 | 0.15564 | 0.15564 | 0.10529 | -122.3282
2554.5312 | 122.287 | -0.10071 | 122.1909 | -0.1651 | 0.044632 | 0.060541 | 0.0036145 | 0.033387 | -0.0055948 | 0.03321 | -0.14618 | 0.030042 | 0.036668 | 0.052233 | -0.0019589 | 0.024368 | 0.09613 | 0.091553 | 0.10986 | 0.068665 | 0.032043 | 0.054932 | -0.086975 | 0.10986 | 0.15106 | 0.018311 | 0.022888 | 0.018311 | -0.027466 | -0.082397 | 0.15564 | 0.013733 | -122.1588 | 0.19226 | 0.16937 | 0.15564 | -122.0947 | 0.073242 | 0.018311 | -122.168 | 0.21057 | 0.11902 | 0.10071 | -122.1725 | 0.13275 | 0.19684 | 0.21057 | -122.2778 | 0.1236 | 0.11902 | 0.25177 | -122.2733
2556.2812 | 122.4289 | -0.059509 | 122.1542 | -0.081177 | 0.043351 | 0.060541 | 0.0025465 | 0.033814 | -0.004954 | 0.028937 | -0.092773 | 0.029615 | 0.034532 | 0.052447 | -0.0025999 | 0.025222 | 0.082397 | 0.1236 | 0.10529 | 0.045776 | 0.054932 | 0.054932 | -0.091553 | 0.15106 | 0.16479 | 0.054932 | 0.009155 | 0.009155 | -0.013733 | -0.064087 | 0.11444 | -0.032044 | -122.0993 | 0.1831 | 0.10528 | 0.13733 | -122.0718 | 0.045776 | -0.004578 | -122.1451 | 0.21057 | 0.11444 | 0.11902 | -122.1451 | 0.11444 | 0.14191 | 0.16479 | -122.2458 | 0.068664 | 0.068664 | 0.2243 | -122.2183
2558.0312 | 122.3099 | -0.10071 | 122.1817 | -0.24139 | 0.048691 | 0.060968 | 0.0046827 | 0.031465 | -0.001536 | 0.029792 | -0.27588 | 0.030469 | 0.0356 | 0.053087 | -0.0013181 | 0.025009 | 0.009155 | -0.018311 | -0.009155 | -0.036621 | 0.10071 | -0.004578 | -0.1236 | 0.022888 | 0.018311 | -0.10071 | 0.059509 | 0.054932 | -0.054932 | -0.11444 | 0.09613 | -0.022888 | -122.081 | 0.082397 | 0.064087 | 0.086975 | -122.1725 | 0.045776 | -0.013733 | -122.1222 | 0.1236 | 0 | 0.013733 | -122.1268 | 0.20142 | 0.10986 | 0.091553 | -122.3053 | 0.16022 | 0.15564 | 0.11902 | -122.2961
2559.7188 | 122.3419 | -0.07782 | 122.1725 | 0.13245 | 0.045273 | 0.0599 | -0.00023075 | 0.032105 | 0.001882 | 0.034064 | 0.029297 | 0.029615 | 0.036027 | 0.054156 | 0.0029543 | 0.024795 | 0.018311 | -0.050354 | -0.041199 | -0.027466 | 0.082397 | 0.018311 | -0.11444 | 0.032043 | -0.027466 | -0.11902 | 0.045776 | 0.036621 | -0.059509 | -0.10986 | 0.096131 | -0.036621 | -122.0901 | 0.027466 | 0.050354 | 0.086975 | -122.1542 | 0.018311 | -0.032043 | -122.1268 | 0.10986 | -0.041199 | -0.009156 | -122.1359 | 0.16022 | 0.096131 | 0.036621 | -122.287 | 0.1236 | 0.11444 | 0.050354 | -122.2824
2561.4688 | 122.2961 | -0.09613 | 122.1954 | -0.18799 | 0.045914 | 0.059259 | 0.0066053 | 0.031251 | -0.006663 | 0.030219 | -0.13092 | 0.028974 | 0.036882 | 0.052233 | -0.0028135 | 0.026291 | 0.068665 | 0.13733 | 0.11444 | 0.073242 | 0.045776 | 0.032043 | -0.086975 | 0.11902 | 0.16479 | 0.018311 | 0.004578 | 0.009155 | -0.018311 | -0.09613 | 0.12817 | 0.009155 | -122.1497 | 0.23346 | 0.16937 | 0.16022 | -122.1268 | 0.077819 | 0 | -122.1909 | 0.21515 | 0.11444 | 0.11444 | -122.1863 | 0.14191 | 0.16479 | 0.21057 | -122.2824 | 0.10071 | 0.10528 | 0.26092 | -122.2916
2563.2344 | 122.3419 | -0.082397 | 122.1725 | 0.10956 | 0.045487 | 0.059045 | -1.7146e-05 | 0.032533 | 0.00038662 | 0.032996 | 0.036926 | 0.032178 | 0.034318 | 0.055865 | 0.00060451 | 0.026077 | -0.004578 | -0.027466 | -0.032043 | -0.022888 | 0.073242 | 0.027466 | -0.10986 | 0.041199 | -0.004578 | -0.11444 | 0.050354 | 0.032043 | -0.064087 | -0.11444 | 0.10986 | -0.027466 | -122.0993 | 0.054931 | 0.059509 | 0.086975 | -122.1771 | 0.01831 | -0.032044 | -122.1222 | 0.1236 | -0.032044 | 0 | -122.1405 | 0.15564 | 0.077819 | 0.050354 | -122.2824 | 0.13275 | 0.11444 | 0.077819 | -122.287
2564.9844 | 122.2687 | -0.09613 | 122.2229 | -0.065918 | 0.044419 | 0.061609 | 0.00041005 | 0.031678 | -0.00025418 | 0.033637 | -0.039368 | 0.032178 | 0.034746 | 0.053728 | 0.0035953 | 0.025009 | 0.036621 | 0.032043 | 0.009155 | 0.004578 | 0.07782 | 0.022888 | -0.11444 | 0.045776 | 0.027466 | -0.10986 | 0.022888 | 0.036621 | -0.032043 | -0.10986 | 0.11902 | -0.018311 | -122.1451 | 0.12817 | 0.10071 | 0.11902 | -122.1863 | 0.064087 | -0.013733 | -122.2 | 0.14191 | -0.013733 | 0 | -122.1863 | 0.17395 | 0.13275 | 0.10528 | -122.3373 | 0.11902 | 0.13275 | 0.1236 | -122.3328
2566.6719 | 122.319 | -0.082397 | 122.2137 | 0.079041 | 0.0457 | 0.062677 | 0.00083745 | 0.033387 | -0.0013224 | 0.033851 | 0.082703 | 0.032178 | 0.038164 | 0.05501 | 0.0020999 | 0.027572 | -0.004578 | -0.041199 | -0.041199 | -0.027466 | 0.10071 | 0.009155 | -0.1236 | 0.022888 | -0.032043 | -0.10529 | 0.054932 | 0.022888 | -0.050354 | -0.10071 | 0.091552 | -0.041199 | -122.113 | 0.041198 | 0.054931 | 0.09613 | -122.2183 | 0.032043 | -0.018311 | -122.1588 | 0.10528 | -0.022889 | -0.004578 | -122.1909 | 0.18311 | 0.077819 | 0.041198 | -122.3373 | 0.13733 | 0.10528 | 0.050354 | -122.3145
2568.4219 | 122.4289 | -0.073242 | 122.1588 | -0.012512 | 0.041855 | 0.064172 | 0.0021191 | 0.034028 | -0.010295 | 0.030006 | 0.044556 | 0.028333 | 0.036027 | 0.051806 | -0.0025999 | 0.027999 | -0.009155 | 0.064087 | 0.068665 | 0.022888 | 0.041199 | 0.032043 | -0.091553 | 0.082397 | 0.10071 | 0.022888 | 0.013733 | 0.018311 | -0.027466 | -0.064087 | 0.10529 | -0.018311 | -122.1176 | 0.13733 | 0.09613 | 0.11444 | -122.168 | 0.045776 | 0.009155 | -122.1451 | 0.15564 | 0.09613 | 0.086975 | -122.1405 | 0.11444 | 0.064087 | 0.14191 | -122.2504 | 0.086975 | 0.091553 | 0.17395 | -122.2229
2570.1719 | 122.3923 | -0.07782 | 122.1817 | -0.0048827 | 0.039078 | 0.062891 | 0.0031873 | 0.029328 | -0.0096536 | 0.031287 | 0.059815 | 0.029828 | 0.03325 | 0.053942 | -0.0019589 | 0.027145 | 0.036621 | 0.050354 | 0.068665 | 0.022888 | 0.036621 | 0.050354 | -0.091553 | 0.07782 | 0.073242 | 0 | 0.018311 | 0.004578 | -0.013733 | -0.073242 | 0.12817 | -0.013733 | -122.1451 | 0.12817 | 0.10071 | 0.11444 | -122.1451 | 0.064087 | 0.004578 | -122.1634 | 0.15564 | 0.07782 | 0.073242 | -122.1771 | 0.11444 | 0.11444 | 0.14649 | -122.2733 | 0.096131 | 0.082398 | 0.15106 | -122.2549
2571.8594 | 122.3831 | -0.064087 | 122.1909 | -0.17273 | 0.045487 | 0.062036 | 0.0051099 | 0.034455 | -0.0064492 | 0.028724 | -0.13092 | 0.028546 | 0.036668 | 0.053728 | -0.0023861 | 0.024154 | 0.09613 | 0.13275 | 0.13275 | 0.068665 | 0.041199 | 0.032043 | -0.091553 | 0.12817 | 0.1831 | 0.059509 | 0 | 0.018311 | -0.018311 | -0.091553 | 0.09613 | -0.027466 | -122.1497 | 0.19684 | 0.13275 | 0.16022 | -122.0947 | 0.045776 | -0.027466 | -122.1909 | 0.19226 | 0.1236 | 0.15106 | -122.1725 | 0.10529 | 0.16022 | 0.19684 | -122.2824 | 0.064087 | 0.082398 | 0.24719 | -122.2824
2573.625 | 122.2687 | -0.10529 | 122.2046 | 0.040894 | 0.044846 | 0.060968 | -1.7146e-05 | 0.030824 | 0.0025228 | 0.032569 | -0.024109 | 0.033032 | 0.034318 | 0.054583 | 0.0046633 | 0.0233 | 0.013733 | -0.059509 | -0.027466 | -0.004578 | 0.073242 | 0.027466 | -0.11902 | 0.004578 | -0.022888 | -0.13275 | 0.064087 | 0.054932 | -0.054932 | -0.10071 | 0.13275 | -0.013733 | -122.1313 | 0.045777 | 0.10071 | 0.11444 | -122.1909 | 0.050354 | 0.004578 | -122.1405 | 0.10986 | -0.027465 | -0.032043 | -122.1497 | 0.17853 | 0.11902 | 0.07782 | -122.3236 | 0.16937 | 0.16022 | 0.082398 | -122.3053
2575.3906 | 122.2641 | -0.10071 | 122.1909 | -0.081177 | 0.047409 | 0.062891 | -0.0017261 | 0.032105 | 0.00038662 | 0.032569 | -0.11566 | 0.031964 | 0.034105 | 0.052019 | 0.0040225 | 0.024154 | 0.082397 | 0.041199 | 0.022888 | 0.027466 | 0.064087 | 0.018311 | -0.13275 | 0.068665 | 0.054932 | -0.073242 | 0.041199 | 0.032043 | -0.032043 | -0.09613 | 0.11902 | -0.032043 | -122.1268 | 0.14191 | 0.12817 | 0.16022 | -122.1085 | 0.068665 | 0.004578 | -122.1497 | 0.16937 | 0.027466 | 0.022888 | -122.1588 | 0.1648 | 0.18311 | 0.1236 | -122.3236 | 0.14191 | 0.13275 | 0.15564 | -122.287
2577.1406 | 122.287 | -0.09613 | 122.1909 | -0.21088 | 0.045273 | 0.063745 | 0.0061781 | 0.031251 | -0.0079446 | 0.03321 | -0.20721 | 0.027478 | 0.035814 | 0.051165 | -0.0015317 | 0.027572 | 0.059509 | 0.10529 | 0.07782 | 0.054932 | 0.041199 | 0.041199 | -0.10071 | 0.050354 | 0.10071 | -0.013733 | 0.018311 | 0.027466 | -0.041199 | -0.11902 | 0.13733 | -0.004578 | -122.1497 | 0.20142 | 0.15106 | 0.15564 | -122.1313 | 0.054931 | -0.022889 | -122.1725 | 0.14648 | 0.082397 | 0.10529 | -122.1634 | 0.13733 | 0.15564 | 0.17395 | -122.2916 | 0.11444 | 0.1236 | 0.19684 | -122.3099
2578.8594 | 122.4197 | -0.068665 | 122.1954 | -0.13458 | 0.042282 | 0.063104 | 0.0019055 | 0.031892 | -0.0079446 | 0.031928 | -0.069885 | 0.028333 | 0.033678 | 0.055651 | -0.0038815 | 0.02864 | 0.10529 | 0.11902 | 0.11444 | 0.068665 | 0.045776 | 0.059509 | -0.091553 | 0.15106 | 0.17853 | 0.068665 | 0.022888 | 0.004578 | -0.004578 | -0.07782 | 0.12817 | -0.022888 | -122.1497 | 0.18768 | 0.13733 | 0.16022 | -122.0901 | 0.064087 | -0.009155 | -122.1725 | 0.21973 | 0.13733 | 0.14649 | -122.1909 | 0.11444 | 0.17395 | 0.18311 | -122.287 | 0.091553 | 0.073243 | 0.24719 | -122.2733
2580.625 | 122.2916 | -0.10529 | 122.2275 | 0.025635 | 0.045914 | 0.061395 | 0.0021191 | 0.031465 | 0.00081382 | 0.031287 | -0.0012209 | 0.030896 | 0.033678 | 0.051806 | 0.0040225 | 0.023941 | 0.004578 | -0.068665 | -0.050354 | -0.022888 | 0.07782 | 0.027466 | -0.10529 | 0.018311 | -0.022888 | -0.11902 | 0.045776 | 0.045776 | -0.041199 | -0.10529 | 0.13275 | 0 | -122.1497 | 0.036621 | 0.082398 | 0.082398 | -122.2229 | 0.064087 | 0 | -122.1817 | 0.1236 | -0.013733 | -0.013733 | -122.1817 | 0.18311 | 0.10986 | 0.054932 | -122.3328 | 0.15106 | 0.15106 | 0.082398 | -122.3328
2582.3125 | 122.287 | -0.091553 | 122.2137 | 0.040894 | 0.047409 | 0.063104 | 0.00062385 | 0.029542 | -0.00046778 | 0.033423 | 0.044556 | 0.032178 | 0.03795 | 0.051378 | 0.0033817 | 0.025436 | 0 | -0.050354 | -0.045776 | -0.027466 | 0.091553 | 0.032043 | -0.13733 | 0.004578 | -0.018311 | -0.13733 | 0.045776 | 0.041199 | -0.041199 | -0.10071 | 0.1236 | -0.045776 | -122.1222 | 0.041199 | 0.064087 | 0.10986 | -122.2137 | 0.050354 | -0.009155 | -122.168 | 0.096131 | -0.045776 | -0.036621 | -122.1725 | 0.18311 | 0.091553 | 0.045777 | -122.3511 | 0.13733 | 0.13275 | 0.073242 | -122.3145
2584.0781 | 122.2961 | -0.11444 | 122.2229 | -0.21851 | 0.047837 | 0.060754 | 0.0059643 | 0.031892 | -0.006022 | 0.032142 | -0.24536 | 0.029615 | 0.038377 | 0.052447 | -0.0011045 | 0.02565 | -0.009155 | -0.004578 | -0.018311 | -0.032043 | 0.073242 | -0.004578 | -0.13275 | 0.013733 | 0.032043 | -0.091553 | 0.082397 | 0.036621 | -0.073242 | -0.10986 | 0.10986 | -0.01831 | -122.1497 | 0.10986 | 0.082398 | 0.10071 | -122.2321 | 0.041199 | 0.004578 | -122.1405 | 0.12817 | 0.022888 | 0.01831 | -122.1863 | 0.18768 | 0.10529 | 0.09613 | -122.3557 | 0.19684 | 0.15106 | 0.14648 | -122.3328
2585.8281 | 122.3282 | -0.09613 | 122.1863 | 0.08667 | 0.046128 | 0.060541 | 0.0031873 | 0.031465 | -0.00089518 | 0.035346 | 0.082703 | 0.031537 | 0.037736 | 0.054369 | 0.0014591 | 0.025222 | -0.022888 | -0.059509 | -0.027466 | -0.009155 | 0.086975 | 0.022888 | -0.10529 | 0.032043 | -0.013733 | -0.11444 | 0.050354 | 0.036621 | -0.041199 | -0.09613 | 0.11902 | -0.009156 | -122.0993 | 0.036621 | 0.086975 | 0.096131 | -122.2092 | 0.054931 | 0 | -122.1359 | 0.12817 | -0.018311 | -0.018311 | -122.1497 | 0.1831 | 0.073242 | 0.068664 | -122.2916 | 0.14648 | 0.13275 | 0.082397 | -122.2824
2587.5156 | 122.3648 | -0.086975 | 122.1771 | 0.08667 | 0.047196 | 0.061182 | -1.7146e-05 | 0.03061 | 0.00017302 | 0.031714 | 0.075073 | 0.033673 | 0.033891 | 0.051592 | -3.629e-05 | 0.026504 | -0.018311 | -0.036621 | -0.032043 | -0.027466 | 0.068665 | 0.027466 | -0.12817 | 0.027466 | -0.009155 | -0.09613 | 0.050354 | 0.050354 | -0.045776 | -0.10071 | 0.11444 | -0.041199 | -122.1085 | 0.050354 | 0.059509 | 0.10071 | -122.1954 | 0.041199 | -0.013733 | -122.1268 | 0.11444 | -0.009155 | 0.004578 | -122.1268 | 0.15564 | 0.068664 | 0.054932 | -122.3053 | 0.13733 | 0.13733 | 0.07782 | -122.2778
2589.2656 | 122.3877 | -0.068665 | 122.1771 | 0.018005 | 0.040573 | 0.061182 | 0.0042555 | 0.029542 | -0.0096536 | 0.030433 | 0.090332 | 0.027906 | 0.036027 | 0.051806 | -0.0051633 | 0.027145 | 0.004578 | 0.045776 | 0.059509 | 0.032043 | 0.059509 | 0.045776 | -0.086975 | 0.073242 | 0.082397 | -0.018311 | 0.027466 | 0.004578 | -0.022888 | -0.073242 | 0.11444 | -0.01831 | -122.1176 | 0.11444 | 0.10071 | 0.11902 | -122.1725 | 0.045777 | -0.004577 | -122.1497 | 0.14191 | 0.050354 | 0.054931 | -122.1725 | 0.12817 | 0.073243 | 0.12817 | -122.2641 | 0.096131 | 0.073243 | 0.15106 | -122.2504
2591.0156 | 122.4289 | -0.054932 | 122.1634 | -0.020142 | 0.041214 | 0.063318 | 0.0036145 | 0.032746 | -0.0068766 | 0.02851 | 0.029297 | 0.027692 | 0.034532 | 0.052447 | -0.0030271 | 0.027572 | 0.018311 | 0.041199 | 0.064087 | 0.027466 | 0.050354 | 0.059509 | -0.086975 | 0.07782 | 0.10071 | 0.009155 | 0.032043 | -0.004578 | -0.009155 | -0.073242 | 0.11444 | -0.032043 | -122.113 | 0.096131 | 0.082398 | 0.11444 | -122.1451 | 0.045777 | -0.01831 | -122.1313 | 0.13275 | 0.064087 | 0.082397 | -122.168 | 0.10529 | 0.073243 | 0.11902 | -122.2504 | 0.086975 | 0.050354 | 0.15564 | -122.2366
2592.7031 | 122.3465 | -0.086975 | 122.1817 | -0.17273 | 0.04271 | 0.060114 | 0.0051099 | 0.031892 | -0.006663 | 0.030006 | -0.16144 | 0.029615 | 0.036027 | 0.052233 | -0.0017453 | 0.0233 | 0.10529 | 0.13733 | 0.12817 | 0.073242 | 0.022888 | 0.050354 | -0.10071 | 0.13275 | 0.16022 | 0.036621 | 0.004578 | -0.004578 | -0.009155 | -0.082397 | 0.13733 | -0.013733 | -122.1588 | 0.2243 | 0.16022 | 0.17395 | -122.0764 | 0.07782 | 0.004578 | -122.1771 | 0.21973 | 0.1236 | 0.11902 | -122.1863 | 0.10986 | 0.19226 | 0.21515 | -122.2824 | 0.091553 | 0.082397 | 0.24719 | -122.2641
2594.4688 | 122.3831 | -0.073242 | 122.1771 | 0.14008 | 0.042496 | 0.061395 | -1.7146e-05 | 0.031251 | -0.004313 | 0.029578 | 0.14374 | 0.029828 | 0.033891 | 0.051378 | 0.0018863 | 0.024154 | 0.10986 | 0.10071 | 0.1236 | 0.059509 | 0.050354 | 0.050354 | -0.059509 | 0.15106 | 0.1236 | 0.032043 | 0.009155 | -0.013733 | -0.013733 | -0.073242 | 0.1236 | 0.013733 | -122.1268 | 0.17395 | 0.13275 | 0.11902 | -122.0673 | 0.059509 | 0 | -122.168 | 0.2243 | 0.10529 | 0.10529 | -122.1909 | 0.1236 | 0.18311 | 0.19684 | -122.2366 | 0.082397 | 0.059509 | 0.19684 | -122.2504
2596.1562 | 122.4014 | -0.032043 | 122.1863 | 0.10193 | 0.044846 | 0.060754 | -1.7146e-05 | 0.031251 | -0.0011088 | 0.031287 | 0.12848 | 0.030042 | 0.034105 | 0.052447 | 0.0025271 | 0.024795 | 0.11902 | 0.09613 | 0.10529 | 0.07782 | 0.027466 | 0.059509 | -0.073242 | 0.15564 | 0.11902 | 0.032043 | 0 | 0.004578 | -0.018311 | -0.064087 | 0.091552 | -0.041199 | -122.1588 | 0.12817 | 0.10986 | 0.15106 | -122.0673 | 0.013732 | -0.032044 | -122.1863 | 0.18768 | 0.064086 | 0.09613 | -122.1817 | 0.059509 | 0.15106 | 0.13733 | -122.2595 | 0.032043 | 0.036621 | 0.15106 | -122.2504
2597.9062 | 122.2687 | -0.07782 | 122.2412 | -0.058289 | 0.048264 | 0.058832 | 0.0040417 | 0.032533 | 0.0016684 | 0.032996 | -0.085144 | 0.032819 | 0.03795 | 0.05266 | 0.0040225 | 0.024154 | 0.068665 | 0.022888 | 0.009155 | 0.004578 | 0.073242 | 0.036621 | -0.11902 | 0.064087 | 0.036621 | -0.086975 | 0.054932 | 0.027466 | -0.045776 | -0.10986 | 0.11444 | -0.041199 | -122.168 | 0.10071 | 0.082398 | 0.1236 | -122.1725 | 0.032044 | -0.032043 | -122.1863 | 0.14191 | -0.009155 | 0.022888 | -122.2137 | 0.15106 | 0.14649 | 0.086975 | -122.3602 | 0.13275 | 0.10529 | 0.11444 | -122.3511
2599.6562 | 122.4106 | -0.054932 | 122.168 | 0.14771 | 0.044419 | 0.063532 | -0.00065795 | 0.033601 | -0.0028178 | 0.032142 | 0.11322 | 0.030042 | 0.034105 | 0.053087 | 0.0025271 | 0.025009 | 0.059509 | 0.050354 | 0.036621 | 0.032043 | 0.041199 | 0.064087 | -0.091553 | 0.1236 | 0.091553 | 0.022888 | 0.018311 | 0 | -0.004578 | -0.082397 | 0.11902 | -0.036621 | -122.1268 | 0.10529 | 0.086975 | 0.1236 | -122.1085 | 0.050354 | -0.027465 | -122.1497 | 0.17853 | 0.07782 | 0.10528 | -122.168 | 0.096131 | 0.11444 | 0.091553 | -122.2595 | 0.073243 | 0.054932 | 0.14649 | -122.2504
2601.3438 | 122.2961 | -0.09613 | 122.2229 | 0.025635 | 0.044632 | 0.061395 | 0.00083745 | 0.03061 | -0.0019632 | 0.03321 | 0.014038 | 0.030255 | 0.034959 | 0.053515 | 0.0027407 | 0.027572 | 0.027466 | -0.054932 | -0.036621 | -0.041199 | 0.086975 | 0.009155 | -0.11902 | 0.013733 | -0.041199 | -0.11902 | 0.059509 | 0.032043 | -0.041199 | -0.10529 | 0.10528 | -0.022889 | -122.1359 | 0.041198 | 0.054931 | 0.07782 | -122.1954 | 0.054931 | -0.009156 | -122.1634 | 0.10986 | -0.022889 | -0.013733 | -122.1909 | 0.1831 | 0.1236 | 0.059509 | -122.3419 | 0.15564 | 0.12817 | 0.054931 | -122.3282
2603.1094 | 122.4106 | -0.059509 | 122.1817 | -0.012512 | 0.042923 | 0.061609 | 0.0046827 | 0.033814 | -0.0075174 | 0.029151 | 0.052185 | 0.027692 | 0.035173 | 0.053301 | -0.0023861 | 0.027572 | 0.027466 | 0.041199 | 0.045776 | 0.032043 | 0.054932 | 0.064087 | -0.10986 | 0.082397 | 0.091553 | -0.013733 | 0.018311 | 0.022888 | -0.036621 | -0.09613 | 0.1236 | -0.050354 | -122.1268 | 0.10071 | 0.091552 | 0.14191 | -122.1542 | 0.022888 | -0.036621 | -122.1634 | 0.14191 | 0.045776 | 0.082397 | -122.1588 | 0.11444 | 0.086975 | 0.10528 | -122.2916 | 0.07782 | 0.082397 | 0.15106 | -122.2778
2604.8125 | 122.2687 | -0.10529 | 122.2183 | -0.073547 | 0.045487 | 0.061395 | 0.00019645 | 0.032533 | 0.00081382 | 0.034705 | -0.10803 | 0.031751 | 0.035814 | 0.050738 | 0.0038089 | 0.025222 | 0.07782 | 0.032043 | 0.027466 | 0.018311 | 0.073242 | 0.027466 | -0.10986 | 0.073242 | 0.064087 | -0.064087 | 0.045776 | 0.022888 | -0.041199 | -0.11444 | 0.13275 | -0.004577 | -122.1451 | 0.13733 | 0.1236 | 0.12817 | -122.1405 | 0.064087 | -0.009155 | -122.1725 | 0.17853 | 0.041199 | 0.050354 | -122.1954 | 0.17853 | 0.18311 | 0.13275 | -122.3282 | 0.15106 | 0.12817 | 0.16937 | -122.3328
2606.5625 | 122.2778 | -0.091553 | 122.2046 | -0.081177 | 0.048264 | 0.060541 | 0.0042555 | 0.032746 | -0.0017496 | 0.034278 | -0.12329 | 0.030683 | 0.036882 | 0.053728 | 0.0012455 | 0.025222 | 0.064087 | 0.045776 | 0.041199 | 0.027466 | 0.073242 | 0.027466 | -0.1236 | 0.086975 | 0.073242 | -0.045776 | 0.041199 | 0.018311 | -0.027466 | -0.10071 | 0.11902 | -0.032043 | -122.1313 | 0.13733 | 0.11902 | 0.15106 | -122.1405 | 0.064087 | -0.009155 | -122.1634 | 0.17853 | 0.045777 | 0.054932 | -122.1863 | 0.16479 | 0.15564 | 0.13275 | -122.3282 | 0.13275 | 0.10986 | 0.16479 | -122.3053
2608.3281 | 122.2824 | -0.10071 | 122.2 | 0.033264 | 0.044419 | 0.060968 | 0.00083745 | 0.03061 | 0.00060022 | 0.03321 | -0.0012209 | 0.033246 | 0.036027 | 0.054369 | 0.0031681 | 0.026718 | -0.013733 | -0.054932 | -0.036621 | -0.027466 | 0.082397 | 0.004578 | -0.1236 | -0.009155 | -0.022888 | -0.13275 | 0.054932 | 0.018311 | -0.059509 | -0.10986 | 0.10529 | -0.022888 | -122.1176 | 0.045776 | 0.073242 | 0.09613 | -122.2137 | 0.041199 | -0.009155 | -122.1451 | 0.091553 | -0.032043 | -0.022888 | -122.1817 | 0.18311 | 0.086975 | 0.064087 | -122.3236 | 0.15564 | 0.11902 | 0.07782 | -122.3099
2610.0938 | 122.3923 | -0.064087 | 122.1771 | 0.13245 | 0.045914 | 0.060968 | 0.0034009 | 0.032105 | -0.0047404 | 0.035132 | 0.14374 | 0.02876 | 0.034959 | 0.05266 | -3.629e-05 | 0.026504 | 0.082397 | 0.082397 | 0.091553 | 0.064087 | 0.036621 | 0.068665 | -0.082397 | 0.12817 | 0.11444 | 0.018311 | 0.018311 | 0.013733 | -0.009155 | -0.073242 | 0.13275 | -0.01831 | -122.1405 | 0.14648 | 0.12817 | 0.14648 | -122.0947 | 0.054932 | -0.009155 | -122.1588 | 0.19226 | 0.082398 | 0.091553 | -122.1634 | 0.10071 | 0.14648 | 0.15564 | -122.2595 | 0.082398 | 0.07782 | 0.17853 | -122.2504
2611.875 | 122.2778 | -0.10529 | 122.2321 | 0.033264 | 0.047623 | 0.0599 | 0.0031873 | 0.031037 | -0.0017496 | 0.03321 | 0.021668 | 0.03111 | 0.03795 | 0.052874 | 0.0016727 | 0.026077 | -0.022888 | -0.054932 | -0.041199 | -0.032043 | 0.086975 | 0.009155 | -0.10986 | 0.009155 | -0.022888 | -0.11902 | 0.064087 | 0.041199 | -0.045776 | -0.10071 | 0.11444 | -0.004577 | -122.1451 | 0.050354 | 0.073243 | 0.07782 | -122.2549 | 0.05951 | 0.004578 | -122.168 | 0.11444 | -0.013733 | -0.018311 | -122.1909 | 0.19226 | 0.082398 | 0.064087 | -122.3419 | 0.16937 | 0.14649 | 0.082398 | -122.3328
2613.5625 | 122.3831 | -0.064087 | 122.1954 | 0.10193 | 0.043351 | 0.061182 | 0.0016919 | 0.029115 | -0.00068138 | 0.032355 | 0.075073 | 0.032605 | 0.036241 | 0.052019 | 0.0031681 | 0.025863 | -0.009155 | -0.032043 | -0.022888 | -0.004578 | 0.073242 | 0.032043 | -0.13275 | 0.036621 | -0.013733 | -0.09613 | 0.036621 | 0.036621 | -0.036621 | -0.10071 | 0.09613 | -0.068664 | -122.1222 | 0.032044 | 0.059509 | 0.12817 | -122.2046 | 0.027466 | -0.036621 | -122.1588 | 0.10071 | -0.032043 | 0.004578 | -122.1588 | 0.13733 | 0.054932 | 0.041199 | -122.3282 | 0.10071 | 0.10071 | 0.050354 | -122.2961
2615.3281 | 122.4106 | -0.059509 | 122.1771 | -0.15747 | 0.044205 | 0.061609 | 0.0070325 | 0.031465 | -0.0098672 | 0.028937 | -0.031738 | 0.027265 | 0.037523 | 0.052233 | -0.0062315 | 0.027359 | 0.073242 | 0.14648 | 0.13733 | 0.068665 | 0.022888 | 0.054932 | -0.086975 | 0.14648 | 0.1831 | 0.09613 | 0.022888 | -0.009155 | -0.009155 | -0.086975 | 0.11444 | -0.027466 | -122.1542 | 0.20599 | 0.12817 | 0.15564 | -122.1039 | 0.050354 | -0.027466 | -122.1542 | 0.20599 | 0.15564 | 0.1831 | -122.1863 | 0.082397 | 0.13275 | 0.19684 | -122.2641 | 0.082397 | 0.050354 | 0.24261 | -122.2641
2617.0938 | 122.3236 | -0.091553 | 122.2092 | -0.15747 | 0.046555 | 0.061182 | 0.0072461 | 0.031892 | -0.00089518 | 0.031501 | -0.21484 | 0.030255 | 0.039018 | 0.053942 | -0.0013181 | 0.024154 | 0.009155 | -0.013733 | -0.018311 | 0.013733 | 0.07782 | 0.004578 | -0.11902 | 0.027466 | 0.054932 | -0.068665 | 0.054932 | 0.050354 | -0.054932 | -0.10529 | 0.096131 | -0.027466 | -122.1313 | 0.07782 | 0.10529 | 0.13275 | -122.2 | 0.036621 | -0.013733 | -122.1542 | 0.11902 | 0.022888 | 0.036621 | -122.1588 | 0.16937 | 0.10071 | 0.073242 | -122.3282 | 0.14649 | 0.14191 | 0.14649 | -122.3145
2618.8594 | 122.3923 | -0.07782 | 122.1909 | 0.094299 | 0.0457 | 0.057336 | -0.00023075 | 0.029542 | -0.003245 | 0.03321 | 0.090332 | 0.03111 | 0.037309 | 0.053728 | 0.0014591 | 0.024154 | 0 | -0.022888 | -0.041199 | -0.027466 | 0.082397 | 0.022888 | -0.10986 | 0.041199 | 0.004578 | -0.068665 | 0.050354 | 0.032043 | -0.032043 | -0.09613 | 0.10071 | -0.032043 | -122.1085 | 0.054932 | 0.050354 | 0.082397 | -122.1909 | 0.045777 | -0.01831 | -122.1405 | 0.11902 | 0.009155 | 0.027465 | -122.1588 | 0.16022 | 0.07782 | 0.036621 | -122.3007 | 0.12817 | 0.10986 | 0.082398 | -122.287
2620.625 | 122.3969 | -0.073242 | 122.1634 | -0.12695 | 0.041642 | 0.062677 | 0.0034009 | 0.032746 | -0.010295 | 0.029151 | -0.077515 | 0.026197 | 0.035387 | 0.051378 | -0.0032407 | 0.026077 | 0.10071 | 0.16022 | 0.13733 | 0.091553 | 0.045776 | 0.045776 | -0.07782 | 0.13733 | 0.17853 | 0.059509 | -0.009155 | 0.009155 | -0.004578 | -0.082397 | 0.11902 | -0.004578 | -122.1176 | 0.23346 | 0.16479 | 0.16937 | -122.0627 | 0.068664 | -0.009155 | -122.1725 | 0.21057 | 0.13275 | 0.14191 | -122.1542 | 0.11902 | 0.17395 | 0.21057 | -122.2412 | 0.064087 | 0.082397 | 0.25177 | -122.2458
2622.3281 | 122.4014 | -0.073242 | 122.1863 | -0.0048827 | 0.045914 | 0.060327 | 0.0057507 | 0.03061 | -0.0068766 | 0.029792 | 0.059815 | 0.028974 | 0.038591 | 0.05266 | -0.0038815 | 0.024795 | 0.018311 | 0.036621 | 0.064087 | 0.027466 | 0.045776 | 0.045776 | -0.09613 | 0.07782 | 0.073242 | 0.004578 | 0.004578 | 0.013733 | -0.032043 | -0.10529 | 0.11902 | -0.022888 | -122.1405 | 0.10986 | 0.10071 | 0.1236 | -122.168 | 0.041199 | -0.032044 | -122.1817 | 0.15106 | 0.07782 | 0.10986 | -122.1725 | 0.11902 | 0.091553 | 0.13733 | -122.2824 | 0.07782 | 0.086975 | 0.14648 | -122.2916
2624.0938 | 122.3785 | -0.068665 | 122.1817 | 0.094299 | 0.041642 | 0.060114 | 0.0010511 | 0.03061 | -0.0038858 | 0.030433 | 0.13611 | 0.031323 | 0.036455 | 0.052874 | 0.00039091 | 0.023941 | 0.10986 | 0.10986 | 0.10071 | 0.050354 | 0.050354 | 0.059509 | -0.082397 | 0.14191 | 0.11902 | 0.022888 | 0.009155 | 0.004578 | 0 | -0.068665 | 0.12817 | -0.013732 | -122.1313 | 0.17853 | 0.11902 | 0.13275 | -122.0718 | 0.068665 | 0 | -122.1725 | 0.21057 | 0.091553 | 0.091553 | -122.1771 | 0.11902 | 0.17853 | 0.16937 | -122.2641 | 0.07782 | 0.073243 | 0.18768 | -122.2504
2625.7812 | 122.3785 | -0.086975 | 122.2046 | 0.033264 | 0.041214 | 0.061395 | 0.0012647 | 0.032746 | -0.0053812 | 0.02851 | 0.059815 | 0.028333 | 0.035814 | 0.05266 | 0.00060451 | 0.026504 | 0.050354 | 0.064087 | 0.059509 | 0.027466 | 0.036621 | 0.068665 | -0.082397 | 0.091553 | 0.082397 | -0.004578 | 0.022888 | 0.013733 | -0.013733 | -0.086975 | 0.15564 | 0.004578 | -122.168 | 0.15106 | 0.11444 | 0.10986 | -122.1542 | 0.073242 | 0 | -122.1817 | 0.17853 | 0.082397 | 0.082397 | -122.1909 | 0.1236 | 0.13733 | 0.14648 | -122.287 | 0.10986 | 0.10071 | 0.16937 | -122.2916
2627.5312 | 122.2916 | -0.11444 | 122.2275 | 0.0027468 | 0.043778 | 0.063959 | 0.0023329 | 0.033814 | 0.0023092 | 0.031714 | -0.031738 | 0.031751 | 0.035814 | 0.052447 | 0.0046633 | 0.0233 | 0.022888 | -0.022888 | -0.027466 | -0.022888 | 0.073242 | 0.022888 | -0.11902 | 0.027466 | -0.009155 | -0.1236 | 0.036621 | 0.022888 | -0.050354 | -0.10529 | 0.13733 | -0.004578 | -122.1542 | 0.091553 | 0.091553 | 0.096131 | -122.2046 | 0.064087 | 0.009155 | -122.1909 | 0.14191 | -0.009155 | -0.01831 | -122.2046 | 0.18768 | 0.13733 | 0.086975 | -122.3465 | 0.15106 | 0.13733 | 0.10529 | -122.3328
2629.2344 | 122.3099 | -0.086975 | 122.2275 | -0.18799 | 0.046341 | 0.062677 | 0.0021191 | 0.032105 | -0.006022 | 0.032996 | -0.13092 | 0.027265 | 0.036241 | 0.050097 | -0.00046349 | 0.026291 | 0.068665 | 0.11902 | 0.11902 | 0.068665 | 0.045776 | 0.059509 | -0.07782 | 0.10529 | 0.15106 | 0.018311 | 0.018311 | 0 | -0.009155 | -0.073242 | 0.14648 | 0.009155 | -122.1817 | 0.20599 | 0.15564 | 0.14649 | -122.1588 | 0.07782 | 0.013733 | -122.2092 | 0.19226 | 0.10529 | 0.091553 | -122.2275 | 0.13275 | 0.15564 | 0.20599 | -122.3053 | 0.10529 | 0.086975 | 0.23804 | -122.3007
2630.9844 | 122.3602 | -0.082397 | 122.2 | -0.18799 | 0.043137 | 0.063532 | 0.0048963 | 0.034242 | -0.0053812 | 0.031928 | -0.16907 | 0.027478 | 0.037096 | 0.054156 | -0.0011045 | 0.025222 | 0.10529 | 0.13733 | 0.13733 | 0.07782 | 0.050354 | 0.050354 | -0.07782 | 0.13733 | 0.16937 | 0.045776 | 0.013733 | 0.004578 | -0.013733 | -0.073242 | 0.13275 | 0.004577 | -122.1497 | 0.21973 | 0.16022 | 0.15564 | -122.0947 | 0.068664 | 0.009155 | -122.1863 | 0.21973 | 0.12817 | 0.11902 | -122.1954 | 0.13275 | 0.18768 | 0.21973 | -122.2778 | 0.09613 | 0.086975 | 0.25177 | -122.2733
2632.7344 | 122.3053 | -0.10529 | 122.2092 | -0.18036 | 0.0457 | 0.061182 | 0.0059643 | 0.032319 | -0.0030314 | 0.031501 | -0.15381 | 0.02876 | 0.037309 | 0.053515 | -0.0025999 | 0.023086 | 0.09613 | 0.11444 | 0.10986 | 0.064087 | 0.032043 | 0.059509 | -0.09613 | 0.10986 | 0.15106 | 0.027466 | 0.013733 | 0.009155 | -0.018311 | -0.073242 | 0.16479 | 0.009156 | -122.1771 | 0.21973 | 0.16937 | 0.16022 | -122.113 | 0.086975 | 0.032044 | -122.1954 | 0.21515 | 0.13275 | 0.10071 | -122.2 | 0.13733 | 0.20142 | 0.21515 | -122.3053 | 0.11902 | 0.11444 | 0.25635 | -122.2824
2634.4219 | 122.3648 | -0.064087 | 122.2 | 0.08667 | 0.041642 | 0.061395 | -0.00065795 | 0.031678 | -0.003245 | 0.030433 | 0.097962 | 0.026837 | 0.034318 | 0.053515 | -0.00046349 | 0.02565 | 0.091553 | 0.11444 | 0.11444 | 0.054932 | 0.041199 | 0.064087 | -0.082397 | 0.15564 | 0.1236 | 0.032043 | 0.009155 | 0 | -0.018311 | -0.073242 | 0.12817 | -0.01831 | -122.1588 | 0.17853 | 0.11902 | 0.13733 | -122.1085 | 0.045776 | -0.009155 | -122.1909 | 0.21973 | 0.09613 | 0.10529 | -122.2 | 0.10529 | 0.15564 | 0.17853 | -122.2824 | 0.073242 | 0.064087 | 0.18768 | -122.2733
2636.1719 | 122.3785 | -0.045776 | 122.1909 | 0.15533 | 0.043351 | 0.062463 | -0.0019397 | 0.031251 | -0.002604 | 0.031074 | 0.12848 | 0.026837 | 0.035387 | 0.05031 | 0.0016727 | 0.026504 | 0.10986 | 0.1236 | 0.10529 | 0.064087 | 0.045776 | 0.041199 | -0.07782 | 0.16479 | 0.14191 | 0.032043 | 0.004578 | -0.009155 | 0.004578 | -0.050354 | 0.086975 | -0.032044 | -122.1451 | 0.16937 | 0.10986 | 0.14191 | -122.081 | 0.050354 | -0.004578 | -122.1863 | 0.21057 | 0.077819 | 0.082397 | -122.2 | 0.091552 | 0.15564 | 0.15106 | -122.2687 | 0.050354 | 0.036621 | 0.18768 | -122.2412
2637.8594 | 122.374 | -0.07782 | 122.1909 | -0.17273 | 0.043351 | 0.063318 | 0.0042555 | 0.03296 | -0.0081582 | 0.031714 | -0.1767 | 0.027265 | 0.034532 | 0.05031 | -0.0023861 | 0.024368 | 0.10071 | 0.15106 | 0.11444 | 0.073242 | 0.050354 | 0.059509 | -0.10529 | 0.13275 | 0.1831 | 0.045776 | 0.018311 | 0.009155 | -0.013733 | -0.064087 | 0.13733 | -0.027466 | -122.1405 | 0.22888 | 0.15106 | 0.17853 | -122.0901 | 0.064087 | 0.013733 | -122.1725 | 0.21057 | 0.1236 | 0.10986 | -122.1817 | 0.12817 | 0.17853 | 0.19226 | -122.2961 | 0.096131 | 0.086975 | 0.26092 | -122.2549
2639.625 | 122.3923 | -0.050354 | 122.2046 | 0.15533 | 0.042923 | 0.06225 | -0.0027941 | 0.03296 | -0.0019632 | 0.032996 | 0.12848 | 0.027478 | 0.033891 | 0.050951 | 0.0018863 | 0.026291 | 0.10986 | 0.1236 | 0.1236 | 0.054932 | 0.032043 | 0.064087 | -0.091553 | 0.15564 | 0.12817 | 0.027466 | 0 | -0.018311 | -0.004578 | -0.07782 | 0.11444 | -0.041199 | -122.1725 | 0.17395 | 0.10529 | 0.14649 | -122.0947 | 0.045776 | -0.027466 | -122.2046 | 0.20599 | 0.07782 | 0.10529 | -122.2229 | 0.082397 | 0.16022 | 0.17395 | -122.2961 | 0.050354 | 0.032043 | 0.17853 | -122.2824
2641.375 | 122.2824 | -0.10529 | 122.2366 | -0.065918 | 0.047623 | 0.061823 | -1.7146e-05 | 0.033387 | 0.0033774 | 0.03321 | -0.12329 | 0.032178 | 0.036455 | 0.053942 | 0.0040225 | 0.025222 | 0.07782 | 0.032043 | 0.004578 | 0.018311 | 0.073242 | 0.027466 | -0.12817 | 0.073242 | 0.041199 | -0.091553 | 0.054932 | 0.041199 | -0.041199 | -0.10529 | 0.13275 | -0.022888 | -122.1634 | 0.13733 | 0.1236 | 0.14649 | -122.1588 | 0.064087 | 0 | -122.1817 | 0.17853 | 0.013733 | 0.013733 | -122.1954 | 0.17853 | 0.18311 | 0.10986 | -122.3648 | 0.16022 | 0.14649 | 0.14649 | -122.3419
2643.0781 | 122.4152 | -0.054932 | 122.1909 | 0.16296 | 0.043778 | 0.061823 | 0.0010511 | 0.033601 | -0.0021768 | 0.033851 | 0.10559 | 0.032178 | 0.034532 | 0.052019 | 0.00060451 | 0.025863 | 0.059509 | 0.027466 | 0.041199 | 0.027466 | 0.068665 | 0.050354 | -0.082397 | 0.14191 | 0.10529 | 0.013733 | 0.013733 | 0 | -0.018311 | -0.068665 | 0.10529 | -0.027465 | -122.1222 | 0.082398 | 0.082398 | 0.10986 | -122.1313 | 0.036621 | -0.013733 | -122.1771 | 0.19684 | 0.068665 | 0.082398 | -122.1909 | 0.1236 | 0.11444 | 0.096131 | -122.2733 | 0.068665 | 0.054932 | 0.16022 | -122.2595
2644.8438 | 122.3785 | -0.068665 | 122.2137 | 0.056152 | 0.04271 | 0.061823 | 0.0036145 | 0.031892 | -0.0068766 | 0.03086 | 0.082703 | 0.02876 | 0.036668 | 0.052233 | -0.0025999 | 0.027145 | 0.054932 | 0.059509 | 0.07782 | 0.036621 | 0.041199 | 0.054932 | -0.082397 | 0.10071 | 0.09613 | -0.009155 | 0 | 0 | -0.013733 | -0.073242 | 0.1236 | -0.013732 | -122.1725 | 0.12817 | 0.10529 | 0.11902 | -122.1588 | 0.054932 | -0.004577 | -122.2137 | 0.16937 | 0.05951 | 0.064087 | -122.2137 | 0.10986 | 0.1236 | 0.14649 | -122.2961 | 0.068665 | 0.068665 | 0.16479 | -122.287
2646.6094 | 122.3831 | -0.07782 | 122.1954 | 0.13245 | 0.041855 | 0.060968 | -0.00044435 | 0.032319 | -0.0047404 | 0.032142 | 0.11322 | 0.029187 | 0.033037 | 0.05266 | 0.0014591 | 0.025222 | 0.12817 | 0.091553 | 0.1236 | 0.054932 | 0.041199 | 0.068665 | -0.068665 | 0.14648 | 0.13733 | 0.022888 | 0.009155 | 0 | -0.009155 | -0.050354 | 0.14649 | 0.009155 | -122.1542 | 0.16937 | 0.13275 | 0.1236 | -122.0673 | 0.068665 | 0.027466 | -122.1863 | 0.2243 | 0.10071 | 0.073242 | -122.1954 | 0.11902 | 0.20599 | 0.20142 | -122.2641 | 0.086975 | 0.07782 | 0.21515 | -122.2458
2648.375 | 122.2778 | -0.10986 | 122.2412 | -0.027771 | 0.046128 | 0.059259 | -0.00065795 | 0.032105 | 0.0023092 | 0.033637 | -0.024109 | 0.034314 | 0.034746 | 0.050524 | 0.0053043 | 0.023727 | 0.045776 | -0.013733 | -0.009155 | -0.018311 | 0.068665 | 0.022888 | -0.12817 | 0.027466 | -0.009155 | -0.11902 | 0.045776 | 0.027466 | -0.045776 | -0.11444 | 0.13275 | -0.018311 | -122.1725 | 0.09613 | 0.091552 | 0.10986 | -122.1954 | 0.064087 | -0.004578 | -122.1954 | 0.13733 | -0.009156 | -0.004578 | -122.2137 | 0.17853 | 0.15564 | 0.10071 | -122.3694 | 0.15564 | 0.13733 | 0.10071 | -122.3557
2650.0781 | 122.3511 | -0.073242 | 122.2046 | 0.079041 | 0.046982 | 0.060327 | 0.0021191 | 0.031037 | -0.00046778 | 0.033423 | 0.075073 | 0.033032 | 0.036027 | 0.053301 | -0.00067729 | 0.025436 | 0.018311 | -0.050354 | -0.032043 | -0.018311 | 0.064087 | 0.013733 | -0.11902 | 0.032043 | -0.009155 | -0.10071 | 0.050354 | 0.027466 | -0.045776 | -0.10071 | 0.086975 | -0.045777 | -122.1405 | 0.022888 | 0.054931 | 0.10071 | -122.1863 | 0.027466 | -0.027466 | -122.1542 | 0.10529 | -0.027466 | 0 | -122.1771 | 0.13733 | 0.091553 | 0.041199 | -122.3236 | 0.1236 | 0.10071 | 0.064087 | -122.3053
2651.8281 | 122.406 | -0.050354 | 122.1588 | 0.14771 | 0.045914 | 0.059473 | 0.0025465 | 0.030397 | -0.0019632 | 0.032996 | 0.059815 | 0.028119 | 0.036027 | 0.052447 | 0.0027407 | 0.026077 | 0.064087 | 0.059509 | 0.064087 | 0.054932 | 0.064087 | 0.059509 | -0.09613 | 0.14191 | 0.11902 | 0.004578 | 0.009155 | -0.004578 | -0.018311 | -0.073242 | 0.10986 | -0.045776 | -122.0947 | 0.10986 | 0.10529 | 0.15106 | -122.0947 | 0.032043 | -0.022888 | -122.1497 | 0.19226 | 0.054932 | 0.07782 | -122.1634 | 0.11444 | 0.11444 | 0.11444 | -122.2549 | 0.059509 | 0.045776 | 0.16937 | -122.2321
2653.5781 | 122.2961 | -0.10071 | 122.2137 | -0.10406 | 0.047196 | 0.058832 | 0.0029737 | 0.031678 | 0.0014548 | 0.032996 | -0.12329 | 0.032605 | 0.036882 | 0.051592 | 0.0020999 | 0.024795 | 0.07782 | 0.054932 | 0.032043 | 0.022888 | 0.068665 | 0.036621 | -0.11902 | 0.073242 | 0.086975 | -0.050354 | 0.064087 | 0.027466 | -0.036621 | -0.073242 | 0.13733 | -0.018311 | -122.1451 | 0.15564 | 0.1236 | 0.14191 | -122.1359 | 0.064087 | 0.027466 | -122.1497 | 0.17395 | 0.050354 | 0.022888 | -122.1863 | 0.16937 | 0.17853 | 0.13275 | -122.3328 | 0.1648 | 0.12817 | 0.18768 | -122.287
2655.2656 | 122.374 | -0.073242 | 122.1954 | 0.13245 | 0.041001 | 0.061609 | 0.00083745 | 0.033174 | -0.0075174 | 0.033423 | 0.15137 | 0.028546 | 0.032182 | 0.053301 | 0.0014591 | 0.026931 | 0.086975 | 0.11444 | 0.10529 | 0.054932 | 0.036621 | 0.073242 | -0.07782 | 0.14648 | 0.11902 | 0.022888 | 0.018311 | 0 | -0.004578 | -0.07782 | 0.14648 | -0.004578 | -122.1588 | 0.18768 | 0.12817 | 0.13275 | -122.1085 | 0.068664 | -0.004578 | -122.1771 | 0.21973 | 0.09613 | 0.10071 | -122.1954 | 0.10986 | 0.16022 | 0.17853 | -122.2733 | 0.091553 | 0.073242 | 0.19226 | -122.2733
2657.0156 | 122.3282 | -0.086975 | 122.2137 | -0.21088 | 0.046768 | 0.064172 | 0.0038281 | 0.030183 | -0.006663 | 0.032355 | -0.12329 | 0.030042 | 0.038164 | 0.051378 | -0.0032407 | 0.024582 | 0.07782 | 0.11444 | 0.12817 | 0.054932 | 0.036621 | 0.059509 | -0.082397 | 0.10986 | 0.16022 | 0.032043 | 0.018311 | 0.004578 | -0.013733 | -0.086975 | 0.14648 | 0.004578 | -122.1771 | 0.20142 | 0.14191 | 0.13733 | -122.1359 | 0.073242 | 0 | -122.1954 | 0.19684 | 0.11902 | 0.11902 | -122.2092 | 0.1236 | 0.16479 | 0.21515 | -122.2961 | 0.10529 | 0.091553 | 0.24719 | -122.3007
2658.7031 | 122.3419 | -0.082397 | 122.1954 | -0.15747 | 0.049759 | 0.061395 | 0.0029737 | 0.030397 | -0.00046778 | 0.032142 | -0.18433 | 0.030042 | 0.037736 | 0.052874 | 0.00039091 | 0.024368 | 0.059509 | 0.013733 | 0.004578 | 0.036621 | 0.068665 | 0.022888 | -0.12817 | 0.068665 | 0.064087 | -0.045776 | 0.050354 | 0.018311 | -0.054932 | -0.11444 | 0.10528 | -0.045777 | -122.1268 | 0.09613 | 0.11902 | 0.1648 | -122.1359 | 0.027465 | -0.032044 | -122.1451 | 0.15106 | 0.036621 | 0.068665 | -122.1771 | 0.15106 | 0.14191 | 0.086975 | -122.3236 | 0.13275 | 0.10071 | 0.14648 | -122.3099
2660.4688 | 122.3969 | -0.050354 | 122.1863 | 0.079041 | 0.046768 | 0.062677 | 0.00062385 | 0.033601 | -0.0021768 | 0.030219 | 0.097962 | 0.030042 | 0.033464 | 0.051806 | 0.0010317 | 0.026077 | 0.009155 | -0.013733 | -0.018311 | -0.013733 | 0.086975 | 0.018311 | -0.11444 | 0.064087 | 0.018311 | -0.054932 | 0.064087 | 0.032043 | -0.022888 | -0.09613 | 0.068665 | -0.064087 | -122.0993 | 0.036621 | 0.036621 | 0.10071 | -122.1771 | 0.027466 | -0.045776 | -122.1222 | 0.11444 | -0.004578 | 0.041198 | -122.1542 | 0.13733 | 0.059509 | 0.032043 | -122.3007 | 0.11444 | 0.082397 | 0.068665 | -122.2824
2662.1562 | 122.4014 | -0.050354 | 122.2 | 0.071411 | 0.045273 | 0.060541 | 0.0019055 | 0.032319 | -0.0013224 | 0.035132 | 0.12085 | 0.030255 | 0.036668 | 0.052447 | 0.0023135 | 0.026931 | 0.004578 | -0.009155 | -0.018311 | -0.022888 | 0.082397 | 0.036621 | -0.11444 | 0.054932 | 0.032043 | -0.050354 | 0.041199 | 0.032043 | -0.041199 | -0.10529 | 0.086975 | -0.064087 | -122.1176 | 0.041199 | 0.027466 | 0.091553 | -122.1954 | 0.009155 | -0.054932 | -122.1588 | 0.10529 | 0 | 0.054932 | -122.168 | 0.13275 | 0.054932 | 0.032043 | -122.3145 | 0.091553 | 0.082397 | 0.082397 | -122.3053
2663.9219 | 122.3877 | -0.064087 | 122.2 | 0.10956 | 0.043778 | 0.061823 | 0.0012647 | 0.031037 | -0.00046778 | 0.03321 | 0.075073 | 0.030042 | 0.037523 | 0.049883 | 0.0016727 | 0.02565 | -0.009155 | -0.013733 | -0.041199 | -0.004578 | 0.073242 | 0.013733 | -0.12817 | 0.041199 | 0.009155 | -0.082397 | 0.045776 | 0.027466 | -0.050354 | -0.10071 | 0.07782 | -0.064087 | -122.1268 | 0.050354 | 0.059509 | 0.1236 | -122.2092 | 0.013733 | -0.036621 | -122.1542 | 0.10529 | -0.01831 | 0.018311 | -122.1725 | 0.13733 | 0.054932 | 0.022888 | -122.3282 | 0.10986 | 0.091553 | 0.073242 | -122.3007
2665.6719 | 122.374 | -0.073242 | 122.1863 | 0.040894 | 0.039292 | 0.064813 | 0.0021191 | 0.033814 | -0.0085856 | 0.031501 | 0.10559 | 0.024701 | 0.034105 | 0.052019 | -0.0015317 | 0.029068 | 0.022888 | 0.073242 | 0.064087 | 0.013733 | 0.045776 | 0.054932 | -0.10071 | 0.091553 | 0.07782 | -0.004578 | 0.027466 | 0 | -0.022888 | -0.07782 | 0.12817 | -0.027466 | -122.1405 | 0.14648 | 0.086975 | 0.11444 | -122.1634 | 0.050354 | -0.004578 | -122.1588 | 0.16479 | 0.068664 | 0.073242 | -122.1863 | 0.11902 | 0.09613 | 0.13733 | -122.287 | 0.10071 | 0.073242 | 0.15106 | -122.2641
2667.3594 | 122.3969 | -0.059509 | 122.1771 | 0.13245 | 0.043564 | 0.061609 | -0.00065795 | 0.031037 | -0.002604 | 0.031287 | 0.17426 | 0.027906 | 0.034105 | 0.05031 | 0.00081811 | 0.026718 | 0.10986 | 0.11444 | 0.10986 | 0.07782 | 0.041199 | 0.064087 | -0.082397 | 0.12817 | 0.12817 | 0.032043 | 0.004578 | 0 | -0.004578 | -0.064087 | 0.1236 | -0.022888 | -122.1359 | 0.17395 | 0.13733 | 0.16022 | -122.0673 | 0.054931 | -0.004578 | -122.1725 | 0.18768 | 0.091552 | 0.09613 | -122.1771 | 0.10071 | 0.16937 | 0.16937 | -122.2595 | 0.064087 | 0.059509 | 0.18768 | -122.2412
2669.1094 | 122.4335 | -0.064087 | 122.1954 | -0.088806 | 0.042923 | 0.062036 | 0.0070325 | 0.034455 | -0.0087992 | 0.030219 | -0.054626 | 0.026837 | 0.036668 | 0.052447 | -0.0036679 | 0.02565 | 0.091553 | 0.10529 | 0.10529 | 0.059509 | 0.045776 | 0.059509 | -0.091553 | 0.13733 | 0.15564 | 0.054932 | 0.004578 | 0.018311 | -0.009155 | -0.054932 | 0.1236 | -0.027466 | -122.1497 | 0.16937 | 0.1236 | 0.15106 | -122.1039 | 0.054932 | 0.009155 | -122.1909 | 0.20142 | 0.11902 | 0.10986 | -122.1771 | 0.10986 | 0.15564 | 0.16937 | -122.287 | 0.068665 | 0.082398 | 0.21973 | -122.2504
2670.8125 | 122.3785 | -0.07782 | 122.2046 | -0.18036 | 0.043991 | 0.061609 | 0.0051099 | 0.032319 | -0.006022 | 0.030219 | -0.15381 | 0.028119 | 0.037096 | 0.05266 | -0.0021725 | 0.023941 | 0.10071 | 0.13275 | 0.13275 | 0.073242 | 0.027466 | 0.054932 | -0.086975 | 0.14191 | 0.16937 | 0.050354 | 0.009155 | 0.013733 | -0.009155 | -0.068665 | 0.13275 | -0.009155 | -122.1771 | 0.21057 | 0.15106 | 0.16022 | -122.1039 | 0.068665 | 0.009155 | -122.1954 | 0.21973 | 0.12817 | 0.11902 | -122.1909 | 0.10529 | 0.17853 | 0.21057 | -122.2916 | 0.086975 | 0.091553 | 0.24719 | -122.2733
2672.5625 | 122.3007 | -0.11902 | 122.2046 | -0.13458 | 0.047196 | 0.060541 | 0.0048963 | 0.031465 | -0.0036722 | 0.031928 | -0.22247 | 0.027051 | 0.03795 | 0.053301 | -0.0011045 | 0.024582 | 0.018311 | -0.009155 | -0.013733 | -0.018311 | 0.073242 | 0.013733 | -0.1236 | 0.036621 | 0.027466 | -0.07782 | 0.041199 | 0.054932 | -0.045776 | -0.10071 | 0.13275 | -0.004577 | -122.1313 | 0.10986 | 0.10071 | 0.10528 | -122.1863 | 0.073243 | 0.018311 | -122.1634 | 0.15564 | 0.041199 | 0.022888 | -122.1497 | 0.19226 | 0.13733 | 0.10529 | -122.3282 | 0.16022 | 0.17395 | 0.14649 | -122.3053
2674.3125 | 122.3053 | -0.1236 | 122.2046 | -0.21851 | 0.046555 | 0.062677 | 0.0055371 | 0.031678 | -0.0023904 | 0.031928 | -0.25299 | 0.03111 | 0.036668 | 0.05501 | 0.00081811 | 0.024582 | 0.009155 | -0.027466 | -0.022888 | -0.027466 | 0.082397 | 0.004578 | -0.1236 | 0.027466 | 0.018311 | -0.10071 | 0.054932 | 0.045776 | -0.064087 | -0.10529 | 0.12817 | 0 | -122.1222 | 0.09613 | 0.09613 | 0.09613 | -122.1954 | 0.059509 | 0.01831 | -122.1497 | 0.15106 | 0.022888 | 0.004578 | -122.1588 | 0.20599 | 0.13275 | 0.10071 | -122.3282 | 0.17853 | 0.16937 | 0.14191 | -122.3099
2676.0625 | 122.4106 | -0.036621 | 122.2 | -0.11932 | 0.042282 | 0.063104 | 0.00062385 | 0.033174 | -0.006663 | 0.031287 | -0.077515 | 0.026837 | 0.036668 | 0.050524 | -0.00089089 | 0.025863 | 0.09613 | 0.10986 | 0.10986 | 0.068665 | 0.045776 | 0.050354 | -0.082397 | 0.16479 | 0.17853 | 0.073242 | 0.022888 | 0.004578 | -0.004578 | -0.068665 | 0.086975 | -0.045776 | -122.1542 | 0.14648 | 0.10529 | 0.15106 | -122.1039 | 0.032043 | -0.032044 | -122.1771 | 0.20142 | 0.10986 | 0.14191 | -122.1954 | 0.082397 | 0.13275 | 0.14648 | -122.2824 | 0.059509 | 0.041199 | 0.21515 | -122.2687
2677.8125 | 122.3053 | -0.10986 | 122.2321 | -0.15747 | 0.045487 | 0.062463 | 0.0040417 | 0.032746 | -0.0021768 | 0.031074 | -0.2301 | 0.029401 | 0.038377 | 0.050738 | 0.00039091 | 0.023086 | 0.004578 | 0 | -0.004578 | -0.018311 | 0.086975 | 0.036621 | -0.10986 | 0.018311 | 0.041199 | -0.082397 | 0.054932 | 0.041199 | -0.073242 | -0.10529 | 0.14648 | 0 | -122.1451 | 0.10986 | 0.091552 | 0.091552 | -122.2275 | 0.036621 | 0.004577 | -122.1771 | 0.12817 | 0.027466 | 0.022889 | -122.1909 | 0.19684 | 0.11444 | 0.10529 | -122.3419 | 0.16479 | 0.15106 | 0.15106 | -122.3373
2679.5781 | 122.2824 | -0.091553 | 122.2183 | -0.081177 | 0.047623 | 0.058191 | -0.00044435 | 0.030824 | 0.001882 | 0.032355 | -0.14618 | 0.031751 | 0.035387 | 0.053087 | 0.0033817 | 0.024154 | 0.086975 | 0.036621 | 0.022888 | 0.018311 | 0.07782 | 0.041199 | -0.10071 | 0.091553 | 0.059509 | -0.068665 | 0.045776 | 0.009155 | -0.027466 | -0.10529 | 0.13275 | -0.009155 | -122.1405 | 0.12817 | 0.10986 | 0.11902 | -122.1313 | 0.064087 | -0.013733 | -122.1725 | 0.18311 | 0.022888 | 0.036621 | -122.2092 | 0.16937 | 0.17853 | 0.11444 | -122.319 | 0.13733 | 0.10071 | 0.15106 | -122.3236
2681.2812 | 122.406 | -0.054932 | 122.1909 | 0.15533 | 0.043564 | 0.060327 | -0.0010851 | 0.032319 | -0.0023904 | 0.032355 | 0.13611 | 0.029828 | 0.036668 | 0.05031 | 0.0010317 | 0.02565 | 0.10529 | 0.09613 | 0.11902 | 0.073242 | 0.036621 | 0.073242 | -0.073242 | 0.15564 | 0.1236 | 0.041199 | 0 | -0.004578 | -0.013733 | -0.059509 | 0.12817 | -0.01831 | -122.1542 | 0.15106 | 0.12817 | 0.14648 | -122.0856 | 0.041199 | -0.004577 | -122.1909 | 0.21057 | 0.096131 | 0.10071 | -122.1954 | 0.091553 | 0.16022 | 0.17395 | -122.2641 | 0.054932 | 0.050354 | 0.17853 | -122.2504
2682.9844 | 122.3831 | -0.064087 | 122.1771 | 0.12482 | 0.042069 | 0.060541 | 0.00083745 | 0.033387 | -0.0040994 | 0.03321 | 0.11322 | 0.027906 | 0.036668 | 0.052874 | -0.0019589 | 0.026291 | 0.10071 | 0.12817 | 0.11902 | 0.054932 | 0.022888 | 0.050354 | -0.073242 | 0.14648 | 0.12817 | 0.041199 | 0.018311 | 0 | -0.009155 | -0.064087 | 0.11444 | -0.009155 | -122.1542 | 0.19226 | 0.11902 | 0.12817 | -122.0764 | 0.054932 | 0 | -122.1588 | 0.21057 | 0.10529 | 0.10529 | -122.1771 | 0.086975 | 0.1648 | 0.18311 | -122.2504 | 0.082398 | 0.064087 | 0.19226 | -122.2412
2684.7344 | 122.2916 | -0.10071 | 122.2366 | -0.027771 | 0.046555 | 0.059686 | 0.0021191 | 0.032746 | 0.0012412 | 0.034064 | -0.016479 | 0.032605 | 0.037736 | 0.051592 | 0.0035953 | 0.026504 | 0.018311 | -0.032043 | -0.027466 | 0 | 0.091553 | 0.018311 | -0.1236 | 0.018311 | -0.004578 | -0.12817 | 0.045776 | 0.041199 | -0.054932 | -0.11902 | 0.11902 | -0.022888 | -122.1451 | 0.068665 | 0.10071 | 0.1236 | -122.2183 | 0.045776 | -0.018311 | -122.1909 | 0.11902 | -0.027466 | -0.009155 | -122.1954 | 0.19226 | 0.11902 | 0.073242 | -122.3602 | 0.14648 | 0.14191 | 0.09613 | -122.3557
2686.4844 | 122.3785 | -0.068665 | 122.1863 | 0.13245 | 0.042496 | 0.061395 | -0.00065795 | 0.028474 | -0.004313 | 0.034064 | 0.14374 | 0.027051 | 0.034746 | 0.052019 | -0.0011045 | 0.025863 | 0.082397 | 0.11902 | 0.11444 | 0.059509 | 0.032043 | 0.068665 | -0.082397 | 0.15564 | 0.12817 | 0.032043 | 0.009155 | 0 | -0.009155 | -0.073242 | 0.13733 | -0.013732 | -122.1542 | 0.18768 | 0.12817 | 0.14191 | -122.1039 | 0.05951 | -0.004577 | -122.1771 | 0.22431 | 0.10071 | 0.10529 | -122.1863 | 0.10071 | 0.15106 | 0.18311 | -122.2687 | 0.07782 | 0.068665 | 0.19684 | -122.2595
2688.1719 | 122.4014 | -0.059509 | 122.2046 | -0.0048827 | 0.041642 | 0.061609 | 0.0027601 | 0.031892 | -0.0085856 | 0.030006 | 0.044556 | 0.028119 | 0.0356 | 0.049029 | -0.0011045 | 0.026077 | 0.018311 | 0.032043 | 0.064087 | 0.027466 | 0.059509 | 0.050354 | -0.086975 | 0.064087 | 0.07782 | 0.004578 | 0.041199 | 0.013733 | -0.022888 | -0.082397 | 0.10986 | -0.027466 | -122.1451 | 0.091552 | 0.086975 | 0.11444 | -122.1863 | 0.036621 | -0.022888 | -122.1634 | 0.1236 | 0.064087 | 0.086975 | -122.1909 | 0.11902 | 0.07782 | 0.1236 | -122.2916 | 0.10071 | 0.073242 | 0.13733 | -122.287
2689.9375 | 122.3877 | -0.054932 | 122.1954 | 0.11719 | 0.041642 | 0.061182 | 0.0016919 | 0.029328 | -0.002604 | 0.031287 | 0.12085 | 0.030255 | 0.036027 | 0.049883 | -3.629e-05 | 0.025222 | 0.10986 | 0.10529 | 0.10986 | 0.054932 | 0.050354 | 0.064087 | -0.068665 | 0.14191 | 0.13733 | 0.041199 | 0.004578 | -0.013733 | 0 | -0.059509 | 0.11902 | -0.013733 | -122.1451 | 0.16022 | 0.10986 | 0.1236 | -122.0856 | 0.054932 | -0.004577 | -122.1909 | 0.19684 | 0.096131 | 0.10071 | -122.2092 | 0.10529 | 0.16479 | 0.16479 | -122.2641 | 0.05951 | 0.041199 | 0.19226 | -122.2549
2691.6875 | 122.3236 | -0.091553 | 122.2092 | -0.10406 | 0.049332 | 0.059686 | 0.0070325 | 0.029328 | 0.00081382 | 0.031714 | -0.14618 | 0.030255 | 0.039232 | 0.052019 | 0.0033817 | 0.023513 | 0.082397 | 0.032043 | 0.032043 | 0.018311 | 0.086975 | 0.027466 | -0.11902 | 0.086975 | 0.073242 | -0.045776 | 0.041199 | 0.036621 | -0.036621 | -0.10529 | 0.11902 | -0.027466 | -122.1222 | 0.1236 | 0.10986 | 0.13733 | -122.1268 | 0.054932 | -0.013733 | -122.168 | 0.17853 | 0.045777 | 0.05951 | -122.1725 | 0.17853 | 0.17395 | 0.1236 | -122.3282 | 0.13275 | 0.12817 | 0.16479 | -122.3145
2693.375 | 122.3007 | -0.091553 | 122.2 | -0.073547 | 0.049973 | 0.0599 | 0.0066053 | 0.033387 | -4.058e-05 | 0.032996 | -0.14618 | 0.028974 | 0.039232 | 0.052233 | 0.0023135 | 0.023941 | 0.054932 | 0.041199 | 0.032043 | 0.022888 | 0.068665 | 0.032043 | -0.10986 | 0.091553 | 0.086975 | -0.050354 | 0.045776 | 0.009155 | -0.054932 | -0.086975 | 0.1236 | -0.01831 | -122.1313 | 0.13275 | 0.11444 | 0.13275 | -122.1451 | 0.036621 | 0.004578 | -122.1542 | 0.18311 | 0.041199 | 0.036621 | -122.1909 | 0.16022 | 0.14649 | 0.1236 | -122.3099 | 0.13733 | 0.10071 | 0.17853 | -122.287
2695.1406 | 122.287 | -0.11444 | 122.2412 | -0.19562 | 0.046555 | 0.062677 | 0.0063917 | 0.032533 | -0.0062356 | 0.032569 | -0.21484 | 0.028333 | 0.036241 | 0.052233 | -0.0034543 | 0.026931 | 0.059509 | 0.10071 | 0.073242 | 0.050354 | 0.050354 | 0.050354 | -0.10986 | 0.073242 | 0.11444 | -0.027466 | 0.050354 | 0.018311 | -0.036621 | -0.091553 | 0.16479 | 0.004578 | -122.1909 | 0.21515 | 0.16479 | 0.16022 | -122.1817 | 0.07782 | 0.022888 | -122.1909 | 0.18768 | 0.086975 | 0.064087 | -122.2229 | 0.16479 | 0.17395 | 0.18768 | -122.3511 | 0.16479 | 0.13275 | 0.22888 | -122.3328
2696.8281 | 122.3511 | -0.09613 | 122.2137 | -0.18799 | 0.04805 | 0.057977 | 0.0059643 | 0.031251 | 0.00060022 | 0.033423 | -0.18433 | 0.03111 | 0.03795 | 0.053301 | 0.00017731 | 0.023727 | 0.013733 | 0.009155 | 0.004578 | 0.004578 | 0.07782 | 0.027466 | -0.13275 | 0.041199 | 0.073242 | -0.050354 | 0.045776 | 0.022888 | -0.041199 | -0.09613 | 0.1236 | -0.036621 | -122.1359 | 0.10528 | 0.10071 | 0.13733 | -122.2 | 0.054931 | 0 | -122.168 | 0.13733 | 0.045776 | 0.045776 | -122.1909 | 0.17395 | 0.10986 | 0.10071 | -122.3465 | 0.14191 | 0.11902 | 0.16937 | -122.3099
2698.5781 | 122.3877 | -0.059509 | 122.2137 | -0.1651 | 0.045914 | 0.065027 | 0.0021191 | 0.030397 | -0.0085856 | 0.029792 | -0.14618 | 0.028119 | 0.036882 | 0.053087 | -0.0021725 | 0.024582 | 0.064087 | 0.13733 | 0.1236 | 0.073242 | 0.050354 | 0.054932 | -0.10071 | 0.1236 | 0.18768 | 0.054932 | 0.013733 | 0.009155 | -0.022888 | -0.086975 | 0.11444 | -0.041199 | -122.1634 | 0.19684 | 0.13275 | 0.17395 | -122.1497 | 0.036621 | -0.027466 | -122.2 | 0.1831 | 0.11444 | 0.14191 | -122.2046 | 0.10986 | 0.1236 | 0.1831 | -122.3145 | 0.073242 | 0.068664 | 0.24719 | -122.3007
2700.3281 | 122.3969 | -0.064087 | 122.2046 | 0.094299 | 0.044846 | 0.063959 | 0.0010511 | 0.033174 | -0.00025418 | 0.032783 | 0.036926 | 0.030896 | 0.036241 | 0.052874 | 0.0040225 | 0.025222 | 0.013733 | -0.018311 | -0.032043 | -0.009155 | 0.086975 | 0.004578 | -0.10529 | 0.045776 | 0.009155 | -0.073242 | 0.054932 | 0.045776 | -0.054932 | -0.091553 | 0.068665 | -0.041199 | -122.1176 | 0.045776 | 0.054932 | 0.096131 | -122.1909 | 0.009155 | -0.027466 | -122.1497 | 0.10986 | -0.009155 | 0.018311 | -122.1588 | 0.15106 | 0.07782 | 0.032044 | -122.3099 | 0.11902 | 0.10986 | 0.073242 | -122.2961
2702.0938 | 122.3831 | -0.068665 | 122.1909 | -0.19562 | 0.0457 | 0.06225 | 0.0051099 | 0.030824 | -0.0092264 | 0.029151 | -0.13855 | 0.025769 | 0.039018 | 0.05266 | -0.0023861 | 0.025009 | 0.07782 | 0.13733 | 0.11902 | 0.068665 | 0.036621 | 0.045776 | -0.068665 | 0.12817 | 0.17853 | 0.059509 | 0.013733 | 0.004578 | 0.004578 | -0.068665 | 0.11444 | 0 | -122.1542 | 0.20599 | 0.13733 | 0.13733 | -122.113 | 0.073243 | 0 | -122.1771 | 0.19684 | 0.12817 | 0.12817 | -122.1863 | 0.10529 | 0.14649 | 0.18768 | -122.2595 | 0.082398 | 0.073243 | 0.24719 | -122.2595
2703.8594 | 122.4289 | -0.068665 | 122.1817 | -0.012512 | 0.042923 | 0.061395 | 0.0034009 | 0.03296 | -0.0055948 | 0.03086 | 0.044556 | 0.028974 | 0.037736 | 0.049883 | -0.0011045 | 0.025222 | 0.013733 | 0.059509 | 0.064087 | 0.032043 | 0.059509 | 0.041199 | -0.082397 | 0.09613 | 0.091553 | 0.009155 | 0.032043 | 0.032043 | -0.004578 | -0.082397 | 0.10986 | -0.013732 | -122.1222 | 0.12817 | 0.10071 | 0.11444 | -122.168 | 0.064087 | -0.013732 | -122.1497 | 0.16479 | 0.07782 | 0.091552 | -122.1497 | 0.12817 | 0.082398 | 0.13275 | -122.2641 | 0.10071 | 0.10071 | 0.16022 | -122.2641
2705.625 | 122.4289 | -0.059509 | 122.1771 | -0.012512 | 0.043137 | 0.060541 | 0.0014783 | 0.032533 | -0.0055948 | 0.03086 | 0.052185 | 0.027692 | 0.035173 | 0.052233 | -3.629e-05 | 0.026077 | 0.022888 | 0.054932 | 0.059509 | 0.022888 | 0.045776 | 0.050354 | -0.09613 | 0.07782 | 0.07782 | 0 | 0.013733 | 0.004578 | -0.013733 | -0.07782 | 0.10986 | -0.036621 | -122.1313 | 0.11444 | 0.082397 | 0.11902 | -122.1542 | 0.045776 | -0.018311 | -122.1634 | 0.13733 | 0.059509 | 0.07782 | -122.1725 | 0.10528 | 0.082397 | 0.11902 | -122.2733 | 0.073242 | 0.064087 | 0.13733 | -122.2549
2707.375 | 122.3831 | -0.054932 | 122.2092 | 0.14008 | 0.043137 | 0.060541 | -0.0019397 | 0.031678 | -0.0028178 | 0.031287 | 0.14374 | 0.029187 | 0.033678 | 0.052233 | 0.0012455 | 0.023086 | 0.10986 | 0.1236 | 0.10529 | 0.082397 | 0.041199 | 0.059509 | -0.07782 | 0.16479 | 0.13733 | 0.041199 | 0.009155 | 0.009155 | -0.004578 | -0.050354 | 0.11444 | -0.022888 | -122.168 | 0.17853 | 0.13733 | 0.16022 | -122.0993 | 0.050354 | 0.004578 | -122.2 | 0.21973 | 0.096131 | 0.091553 | -122.2 | 0.096131 | 0.16479 | 0.16022 | -122.287 | 0.064087 | 0.064087 | 0.19226 | -122.2595
2709.125 | 122.319 | -0.086975 | 122.2321 | -0.088806 | 0.045914 | 0.061609 | -0.00044435 | 0.029756 | 0.00060022 | 0.033637 | -0.15381 | 0.031537 | 0.036668 | 0.053301 | 0.0023135 | 0.0233 | 0.073242 | 0.041199 | 0.022888 | 0.027466 | 0.07782 | 0.009155 | -0.11444 | 0.09613 | 0.07782 | -0.068665 | 0.022888 | 0.032043 | -0.036621 | -0.086975 | 0.09613 | -0.027466 | -122.1542 | 0.12817 | 0.11444 | 0.14191 | -122.1588 | 0.050354 | 0 | -122.2092 | 0.1831 | 0.01831 | 0.01831 | -122.2 | 0.16479 | 0.16022 | 0.10986 | -122.3465 | 0.10986 | 0.11902 | 0.16479 | -122.319
2710.8125 | 122.4014 | -0.050354 | 122.1909 | 0.14771 | 0.04271 | 0.061395 | -0.00023075 | 0.032105 | -0.0028178 | 0.033851 | 0.159 | 0.029401 | 0.035814 | 0.051378 | 0.0014591 | 0.02565 | 0.10986 | 0.10529 | 0.11444 | 0.059509 | 0.036621 | 0.068665 | -0.082397 | 0.15106 | 0.12817 | 0.041199 | 0.004578 | -0.009155 | -0.018311 | -0.054932 | 0.11902 | -0.032043 | -122.1542 | 0.15564 | 0.10986 | 0.14191 | -122.081 | 0.032043 | -0.004578 | -122.1863 | 0.20142 | 0.091553 | 0.096131 | -122.2 | 0.086975 | 0.16022 | 0.16479 | -122.2733 | 0.054932 | 0.041199 | 0.17853 | -122.2458
2712.5625 | 122.2916 | -0.09613 | 122.2183 | -0.065918 | 0.047196 | 0.061182 | 0.0036145 | 0.031678 | -0.00089518 | 0.031714 | -0.11566 | 0.030469 | 0.036668 | 0.052447 | 0.0035953 | 0.023727 | 0.059509 | 0.059509 | 0.041199 | 0.022888 | 0.068665 | 0.022888 | -0.10529 | 0.064087 | 0.068665 | -0.068665 | 0.041199 | 0.032043 | -0.059509 | -0.09613 | 0.11902 | -0.009156 | -122.1497 | 0.15564 | 0.11902 | 0.12817 | -122.1588 | 0.036621 | 0 | -122.1771 | 0.16022 | 0.027465 | 0.027465 | -122.1863 | 0.16479 | 0.15564 | 0.13733 | -122.3236 | 0.13733 | 0.12817 | 0.16479 | -122.3145
2714.3125 | 122.3969 | -0.050354 | 122.2183 | 0.10956 | 0.043778 | 0.063745 | 0.0014783 | 0.030397 | -0.0058084 | 0.034278 | 0.16663 | 0.02876 | 0.036027 | 0.049883 | 0.0012455 | 0.027572 | 0.10071 | 0.10529 | 0.09613 | 0.07782 | 0.054932 | 0.064087 | -0.073242 | 0.14648 | 0.13275 | 0.050354 | 0.009155 | -0.013733 | -0.018311 | -0.064087 | 0.11444 | -0.022888 | -122.1634 | 0.15564 | 0.12817 | 0.15106 | -122.1176 | 0.032043 | -0.013733 | -122.2092 | 0.19684 | 0.10071 | 0.11444 | -122.2321 | 0.10529 | 0.15106 | 0.14648 | -122.2916 | 0.059509 | 0.036621 | 0.18311 | -122.2824
2716 | 122.3145 | -0.082397 | 122.2275 | -0.11169 | 0.046128 | 0.060114 | 0.0023329 | 0.031892 | 0.00038662 | 0.035346 | -0.12329 | 0.03346 | 0.036882 | 0.051806 | 0.0023135 | 0.024368 | 0.068665 | 0.041199 | 0.027466 | 0.022888 | 0.07782 | 0.022888 | -0.10986 | 0.082397 | 0.07782 | -0.054932 | 0.045776 | 0.018311 | -0.041199 | -0.10529 | 0.10528 | -0.027466 | -122.1497 | 0.1236 | 0.10528 | 0.13275 | -122.1588 | 0.041198 | -0.022889 | -122.1817 | 0.16479 | 0.027465 | 0.050354 | -122.2092 | 0.16022 | 0.15106 | 0.10986 | -122.3373 | 0.12817 | 0.10071 | 0.16022 | -122.3328
2717.75 | 122.3694 | -0.082397 | 122.2 | 0.079041 | 0.04271 | 0.060754 | 0.0055371 | 0.031465 | -0.010081 | 0.030646 | 0.11322 | 0.029187 | 0.035173 | 0.051165 | -0.0013181 | 0.025863 | 0.050354 | 0.082397 | 0.07782 | 0.022888 | 0.032043 | 0.064087 | -0.082397 | 0.09613 | 0.082397 | -0.004578 | 0.022888 | 0 | -0.027466 | -0.073242 | 0.14648 | 0 | -122.168 | 0.16479 | 0.10528 | 0.10528 | -122.1497 | 0.054931 | 0.009155 | -122.1771 | 0.17853 | 0.077819 | 0.068664 | -122.2 | 0.11444 | 0.13275 | 0.16022 | -122.2824 | 0.10528 | 0.082397 | 0.16479 | -122.2733
2719.4531 | 122.3785 | -0.064087 | 122.1954 | 0.11719 | 0.043778 | 0.059686 | 0.0036145 | 0.032105 | -0.0055948 | 0.031074 | 0.15137 | 0.030683 | 0.036027 | 0.052019 | -3.629e-05 | 0.027999 | 0.09613 | 0.091553 | 0.10986 | 0.059509 | 0.041199 | 0.059509 | -0.091553 | 0.13275 | 0.11444 | 0.018311 | 0.022888 | -0.004578 | -0.032043 | -0.064087 | 0.1236 | -0.027466 | -122.1542 | 0.15564 | 0.1236 | 0.15106 | -122.0993 | 0.032044 | 0 | -122.1725 | 0.19684 | 0.082398 | 0.082398 | -122.2 | 0.10529 | 0.16022 | 0.17395 | -122.287 | 0.086975 | 0.059509 | 0.17853 | -122.2595
2721.2188 | 122.3328 | -0.10986 | 122.2412 | -0.22614 | 0.045914 | 0.060114 | 0.0055371 | 0.034028 | -0.0017496 | 0.030646 | -0.26825 | 0.029615 | 0.038377 | 0.052233 | -0.0025999 | 0.022873 | 0.013733 | -0.018311 | -0.018311 | -0.027466 | 0.09613 | 0.004578 | -0.14191 | 0.013733 | 0.013733 | -0.086975 | 0.054932 | 0.064087 | -0.054932 | -0.11444 | 0.11444 | -0.032044 | -122.1451 | 0.091552 | 0.082397 | 0.11444 | -122.2275 | 0.054931 | -0.004578 | -122.1863 | 0.1236 | 0.022888 | 0.027466 | -122.1771 | 0.20599 | 0.1236 | 0.091552 | -122.3831 | 0.16479 | 0.17395 | 0.1236 | -122.3557
2722.9688 | 122.4289 | -0.073242 | 122.2046 | -0.058289 | 0.044846 | 0.061182 | 0.0042555 | 0.034455 | -0.0073038 | 0.030006 | -0.10803 | 0.028546 | 0.034959 | 0.054156 | -0.0030271 | 0.026291 | 0.054932 | 0.09613 | 0.086975 | 0.050354 | 0.054932 | 0.050354 | -0.09613 | 0.14648 | 0.16022 | 0.059509 | 0.018311 | 0.018311 | -0.009155 | -0.059509 | 0.1236 | -0.022888 | -122.1497 | 0.16937 | 0.1236 | 0.14648 | -122.1497 | 0.064087 | 0.013733 | -122.1863 | 0.21973 | 0.13275 | 0.11902 | -122.1863 | 0.12817 | 0.12817 | 0.16022 | -122.3007 | 0.091553 | 0.091553 | 0.23346 | -122.2641
2724.7344 | 122.374 | -0.059509 | 122.1863 | 0.10193 | 0.043991 | 0.059473 | 0.00062385 | 0.031251 | -0.0036722 | 0.030433 | 0.12085 | 0.030042 | 0.035387 | 0.053087 | 0.0020999 | 0.024368 | 0.11444 | 0.10071 | 0.10071 | 0.050354 | 0.027466 | 0.064087 | -0.082397 | 0.14191 | 0.11444 | 0.032043 | 0.013733 | 0.004578 | -0.013733 | -0.068665 | 0.1236 | -0.022888 | -122.1588 | 0.16022 | 0.10986 | 0.13275 | -122.0718 | 0.045776 | -0.009156 | -122.1725 | 0.20142 | 0.091552 | 0.10071 | -122.1817 | 0.086975 | 0.17395 | 0.16022 | -122.2687 | 0.073242 | 0.064087 | 0.17395 | -122.2549
2726.4375 | 122.3373 | -0.10071 | 122.2412 | -0.23376 | 0.044205 | 0.063104 | 0.0070325 | 0.030824 | -0.0028178 | 0.032142 | -0.26062 | 0.029187 | 0.036882 | 0.05266 | -0.00089089 | 0.022445 | 0 | 0 | -0.022888 | -0.022888 | 0.091553 | 0.022888 | -0.13733 | 0.022888 | 0.036621 | -0.09613 | 0.073242 | 0.050354 | -0.059509 | -0.10529 | 0.1236 | -0.036621 | -122.1497 | 0.10071 | 0.07782 | 0.11444 | -122.2412 | 0.041199 | -0.004578 | -122.168 | 0.1236 | 0.004578 | 0.009156 | -122.1909 | 0.19226 | 0.10071 | 0.07782 | -122.3785 | 0.17395 | 0.15106 | 0.13733 | -122.3465
2728.1875 | 122.4701 | -0.068665 | 122.2092 | -0.058289 | 0.043564 | 0.062677 | 0.0036145 | 0.031251 | -0.006663 | 0.030646 | -0.069885 | 0.024274 | 0.034959 | 0.052447 | -0.0011045 | 0.024795 | 0.064087 | 0.082397 | 0.082397 | 0.050354 | 0.036621 | 0.054932 | -0.09613 | 0.13275 | 0.14191 | 0.054932 | 0.013733 | 0.022888 | -0.013733 | -0.09613 | 0.1236 | -0.027465 | -122.1725 | 0.15106 | 0.11902 | 0.14648 | -122.1451 | 0.054932 | -0.027465 | -122.1954 | 0.20142 | 0.1236 | 0.15106 | -122.1863 | 0.10529 | 0.13275 | 0.15106 | -122.3053 | 0.082398 | 0.091553 | 0.21057 | -122.3053
2729.9531 | 122.4518 | -0.073242 | 122.2229 | -0.027771 | 0.040787 | 0.060327 | 0.0036145 | 0.032319 | -0.0062356 | 0.028083 | -0.046997 | 0.027478 | 0.035814 | 0.054369 | -0.00046349 | 0.022873 | 0.036621 | 0.064087 | 0.07782 | 0.045776 | 0.045776 | 0.045776 | -0.091553 | 0.13275 | 0.13275 | 0.041199 | 0.032043 | 0.009155 | -0.013733 | -0.059509 | 0.11902 | -0.018311 | -122.1771 | 0.13733 | 0.11902 | 0.13733 | -122.1863 | 0.059509 | 0.013733 | -122.1909 | 0.20599 | 0.11444 | 0.10071 | -122.2137 | 0.11902 | 0.10986 | 0.15106 | -122.3145 | 0.10529 | 0.082397 | 0.20599 | -122.2824
2731.7188 | 122.3007 | -0.09613 | 122.2412 | -0.19562 | 0.046128 | 0.06225 | 0.0029737 | 0.03531 | -0.0030314 | 0.029578 | -0.23773 | 0.02876 | 0.036882 | 0.049669 | -3.629e-05 | 0.025009 | 0.082397 | 0.11444 | 0.082397 | 0.073242 | 0.041199 | 0.045776 | -0.10986 | 0.09613 | 0.11444 | -0.018311 | 0.036621 | 0.013733 | -0.009155 | -0.082397 | 0.14191 | -0.013733 | -122.2 | 0.21057 | 0.16937 | 0.18311 | -122.1588 | 0.086975 | 0.013733 | -122.2046 | 0.19226 | 0.077819 | 0.064086 | -122.2275 | 0.13733 | 0.17853 | 0.17853 | -122.3511 | 0.13275 | 0.10986 | 0.21057 | -122.3236
2733.4062 | 122.4197 | -0.068665 | 122.1817 | 0.010376 | 0.041214 | 0.060114 | 0.0023329 | 0.029969 | -0.0055948 | 0.031714 | -0.0012209 | 0.028974 | 0.034318 | 0.053087 | 0.00017731 | 0.027359 | 0.032043 | 0.041199 | 0.059509 | 0.022888 | 0.059509 | 0.041199 | -0.073242 | 0.09613 | 0.07782 | 0 | 0.027466 | 0.022888 | -0.018311 | -0.091553 | 0.10986 | -0.004577 | -122.1222 | 0.10986 | 0.091553 | 0.09613 | -122.1497 | 0.050354 | -0.022888 | -122.1542 | 0.16479 | 0.068665 | 0.091553 | -122.1588 | 0.12817 | 0.10071 | 0.12817 | -122.2549 | 0.096131 | 0.091553 | 0.14649 | -122.2733
2735.1562 | 122.3053 | -0.10986 | 122.2458 | -0.21088 | 0.047837 | 0.063745 | 0.0044691 | 0.03296 | -0.0011088 | 0.031074 | -0.21484 | 0.029401 | 0.036455 | 0.053728 | -0.0021725 | 0.023941 | 0.032043 | 0.009155 | 0.004578 | -0.027466 | 0.082397 | 0.004578 | -0.14648 | 0.041199 | 0.027466 | -0.07782 | 0.054932 | 0.041199 | -0.050354 | -0.10986 | 0.11444 | -0.036621 | -122.1634 | 0.11902 | 0.082397 | 0.11902 | -122.2137 | 0.059509 | 0 | -122.1909 | 0.15106 | 0.032043 | 0.032043 | -122.2046 | 0.19226 | 0.14191 | 0.11444 | -122.3923 | 0.16479 | 0.15106 | 0.13733 | -122.3557
2736.9062 | 122.3282 | -0.09613 | 122.2595 | -0.21851 | 0.045914 | 0.062463 | 0.0031873 | 0.03061 | -0.00046778 | 0.031928 | -0.26825 | 0.030469 | 0.035387 | 0.051806 | 0.0012455 | 0.025222 | 0.022888 | -0.004578 | -0.022888 | -0.018311 | 0.082397 | 0.009155 | -0.1236 | 0.045776 | 0.027466 | -0.091553 | 0.059509 | 0.059509 | -0.068665 | -0.11902 | 0.10528 | -0.027466 | -122.1771 | 0.091552 | 0.077819 | 0.10528 | -122.2366 | 0.027465 | -0.022889 | -122.2 | 0.14191 | 0.004577 | 0.027466 | -122.2 | 0.17853 | 0.11902 | 0.073242 | -122.3831 | 0.15564 | 0.15564 | 0.1236 | -122.3785
2738.6562 | 122.3465 | -0.10071 | 122.2183 | -0.22614 | 0.04805 | 0.059686 | 0.0046827 | 0.033174 | -4.058e-05 | 0.031074 | -0.23773 | 0.030255 | 0.039018 | 0.052019 | 0.0014591 | 0.025863 | 0.009155 | -0.004578 | -0.018311 | -0.018311 | 0.091553 | 0.022888 | -0.13733 | 0.032043 | 0.036621 | -0.09613 | 0.059509 | 0.045776 | -0.054932 | -0.10529 | 0.1236 | -0.036621 | -122.1268 | 0.09613 | 0.082397 | 0.11902 | -122.2092 | 0.045776 | -0.004578 | -122.1588 | 0.13275 | 0.004578 | 0.009156 | -122.1725 | 0.19226 | 0.10986 | 0.082397 | -122.3557 | 0.16022 | 0.14648 | 0.13733 | -122.3236
2740.3438 | 122.3602 | -0.086975 | 122.1863 | 0.10193 | 0.043991 | 0.058618 | -1.7146e-05 | 0.03061 | 0.00060022 | 0.032142 | 0.036926 | 0.030042 | 0.038164 | 0.054796 | 0.0020999 | 0.025009 | -0.004578 | -0.022888 | -0.022888 | -0.027466 | 0.082397 | 0.018311 | -0.13275 | 0.045776 | 0.004578 | -0.086975 | 0.064087 | 0.036621 | -0.059509 | -0.11902 | 0.10529 | -0.045776 | -122.1039 | 0.064087 | 0.059509 | 0.10529 | -122.1909 | 0.027466 | -0.032044 | -122.1222 | 0.13275 | 0 | 0.032044 | -122.1497 | 0.16937 | 0.082397 | 0.064087 | -122.319 | 0.15106 | 0.1236 | 0.091553 | -122.3053
2742.1094 | 122.4472 | -0.054932 | 122.1771 | 0.0027468 | 0.044205 | 0.063318 | 0.0034009 | 0.033174 | -0.0087992 | 0.031928 | -0.0012209 | 0.027906 | 0.036455 | 0.049883 | -0.00089089 | 0.025436 | 0.013733 | 0.073242 | 0.068665 | 0.036621 | 0.036621 | 0.054932 | -0.091553 | 0.10529 | 0.11444 | 0.027466 | 0.013733 | 0.009155 | -0.009155 | -0.073242 | 0.10986 | -0.036621 | -122.1405 | 0.12817 | 0.091553 | 0.12817 | -122.1634 | 0.045777 | -0.01831 | -122.1634 | 0.16022 | 0.082398 | 0.10071 | -122.168 | 0.091553 | 0.068665 | 0.1236 | -122.2687 | 0.068665 | 0.064087 | 0.16937 | -122.2504
2743.8594 | 122.3877 | -0.064087 | 122.2092 | 0.14008 | 0.043351 | 0.058405 | 0.0025465 | 0.031037 | -0.0023904 | 0.029578 | 0.17426 | 0.028119 | 0.034959 | 0.054369 | 0.0010317 | 0.023513 | 0.10529 | 0.11902 | 0.10986 | 0.068665 | 0.045776 | 0.073242 | -0.086975 | 0.15106 | 0.13275 | 0.041199 | 0.013733 | -0.013733 | -0.018311 | -0.059509 | 0.13733 | -0.022888 | -122.1634 | 0.18311 | 0.13275 | 0.15564 | -122.1039 | 0.045776 | 0.004578 | -122.1954 | 0.21515 | 0.10529 | 0.10071 | -122.2229 | 0.10986 | 0.16937 | 0.17395 | -122.2961 | 0.07782 | 0.050354 | 0.19684 | -122.2687
2745.625 | 122.3419 | -0.091553 | 122.2595 | -0.22614 | 0.046128 | 0.062891 | 0.0046827 | 0.031251 | -0.00068138 | 0.030646 | -0.24536 | 0.029615 | 0.035387 | 0.051592 | 0.00039091 | 0.024582 | 0 | -0.013733 | -0.045776 | -0.009155 | 0.086975 | -0.004578 | -0.13275 | 0.022888 | 0.027466 | -0.091553 | 0.059509 | 0.059509 | -0.059509 | -0.11444 | 0.086975 | -0.041198 | -122.1725 | 0.07782 | 0.082398 | 0.1236 | -122.2595 | 0.032044 | -0.022888 | -122.2 | 0.11444 | 0 | 0.022888 | -122.2 | 0.17853 | 0.091553 | 0.045777 | -122.3923 | 0.15106 | 0.15106 | 0.11902 | -122.374
2747.3125 | 122.319 | -0.10529 | 122.2595 | -0.096436 | 0.047196 | 0.060114 | 0.00041005 | 0.030183 | 0.00038662 | 0.032996 | -0.15381 | 0.032605 | 0.034746 | 0.052233 | 0.0025271 | 0.025863 | 0.064087 | 0.054932 | 0.027466 | 0.027466 | 0.073242 | 0.027466 | -0.14648 | 0.09613 | 0.09613 | -0.036621 | 0.032043 | 0.036621 | -0.036621 | -0.10529 | 0.13275 | -0.041198 | -122.1863 | 0.16022 | 0.13275 | 0.17395 | -122.1954 | 0.068665 | 0 | -122.2275 | 0.20142 | 0.068665 | 0.068665 | -122.2229 | 0.17853 | 0.16937 | 0.13275 | -122.406 | 0.13733 | 0.14191 | 0.20142 | -122.3648
2749.0781 | 122.3511 | -0.086975 | 122.2183 | -0.17273 | 0.045914 | 0.060327 | 0.0031873 | 0.034028 | -0.001536 | 0.034492 | -0.1767 | 0.028974 | 0.036882 | 0.051806 | 0.00060451 | 0.023513 | 0.013733 | 0.018311 | 0.004578 | 0.013733 | 0.064087 | 0.009155 | -0.1236 | 0.050354 | 0.07782 | -0.054932 | 0.045776 | 0.032043 | -0.045776 | -0.10986 | 0.09613 | -0.036621 | -122.1542 | 0.10529 | 0.10071 | 0.13733 | -122.2046 | 0.041199 | -0.022888 | -122.1725 | 0.13733 | 0.032043 | 0.054931 | -122.1863 | 0.15106 | 0.10071 | 0.091553 | -122.3419 | 0.13275 | 0.11902 | 0.16479 | -122.3282
2750.8438 | 122.438 | -0.045776 | 122.1909 | 0.063782 | 0.04506 | 0.060754 | 0.0014783 | 0.033601 | -0.0051676 | 0.032996 | 0.159 | 0.028974 | 0.036241 | 0.052447 | 0.00081811 | 0.026718 | 0.07782 | 0.10986 | 0.082397 | 0.064087 | 0.054932 | 0.07782 | -0.045776 | 0.14191 | 0.13733 | 0.022888 | 0.013733 | -0.009155 | -0.018311 | -0.064087 | 0.1236 | 0 | -122.1359 | 0.15564 | 0.10986 | 0.10986 | -122.113 | 0.027465 | -0.018311 | -122.1771 | 0.18768 | 0.068664 | 0.086975 | -122.2 | 0.10071 | 0.1236 | 0.12817 | -122.2366 | 0.059509 | 0.036621 | 0.18311 | -122.2549
2752.5312 | 122.3694 | -0.073242 | 122.2046 | 0.11719 | 0.042069 | 0.061609 | 0.0019055 | 0.028688 | -0.006022 | 0.034278 | 0.14374 | 0.030469 | 0.036882 | 0.052874 | -0.00046349 | 0.025009 | 0.064087 | 0.082397 | 0.082397 | 0.050354 | 0.036621 | 0.054932 | -0.086975 | 0.10071 | 0.09613 | 0.018311 | 0.022888 | 0.004578 | -0.009155 | -0.073242 | 0.12817 | -0.013733 | -122.168 | 0.15564 | 0.1236 | 0.13733 | -122.1405 | 0.064087 | 0 | -122.1817 | 0.17395 | 0.091553 | 0.091553 | -122.2 | 0.10986 | 0.13733 | 0.15564 | -122.2916 | 0.09613 | 0.07782 | 0.16937 | -122.2778
2754.2812 | 122.3145 | -0.09613 | 122.2275 | 0.079041 | 0.046128 | 0.061823 | 0.0023329 | 0.03531 | 0.0014548 | 0.031714 | -0.024109 | 0.029828 | 0.034318 | 0.052019 | 0.0044497 | 0.024795 | 0.004578 | -0.032043 | -0.018311 | -0.013733 | 0.073242 | 0.022888 | -0.11902 | -0.004578 | -0.022888 | -0.11902 | 0.068665 | 0.041199 | -0.059509 | -0.10071 | 0.11902 | -0.022889 | -122.1542 | 0.064087 | 0.082397 | 0.10529 | -122.2229 | 0.036621 | -0.004578 | -122.1588 | 0.091552 | -0.022889 | -0.018311 | -122.1863 | 0.16937 | 0.10071 | 0.077819 | -122.3465 | 0.16479 | 0.13733 | 0.073242 | -122.3282
2755.9844 | 122.3007 | -0.10071 | 122.2366 | -0.096436 | 0.046982 | 0.062036 | 0.0053235 | 0.030824 | 0.00017302 | 0.034705 | -0.11566 | 0.030896 | 0.038164 | 0.052233 | 0.0023135 | 0.023941 | 0.064087 | 0.054932 | 0.036621 | 0.022888 | 0.068665 | 0.022888 | -0.11444 | 0.064087 | 0.068665 | -0.064087 | 0.032043 | 0.027466 | -0.036621 | -0.082397 | 0.1236 | -0.013733 | -122.168 | 0.15564 | 0.1236 | 0.13733 | -122.1725 | 0.064087 | 0.018311 | -122.2046 | 0.1648 | 0.036621 | 0.01831 | -122.2092 | 0.16937 | 0.1648 | 0.13733 | -122.3511 | 0.13275 | 0.12817 | 0.16937 | -122.319
2757.7344 | 122.3099 | -0.1236 | 122.2 | -0.20325 | 0.046341 | 0.063318 | 0.0029737 | 0.031251 | -0.0073038 | 0.03086 | -0.19196 | 0.031964 | 0.035814 | 0.050738 | -0.0032407 | 0.023941 | 0.050354 | 0.086975 | 0.073242 | 0.050354 | 0.050354 | 0.041199 | -0.11444 | 0.054932 | 0.11444 | -0.013733 | 0.036621 | 0.027466 | -0.041199 | -0.082397 | 0.16479 | 0.009155 | -122.1497 | 0.21057 | 0.17395 | 0.16479 | -122.1497 | 0.082397 | 0.041199 | -122.1634 | 0.17853 | 0.10986 | 0.068664 | -122.1725 | 0.17395 | 0.17395 | 0.19684 | -122.3145 | 0.16022 | 0.15106 | 0.23804 | -122.2824
2759.4219 | 122.4197 | -0.059509 | 122.2092 | -0.096436 | 0.0457 | 0.061395 | 0.0044691 | 0.033387 | -0.0090128 | 0.029792 | -0.054626 | 0.028119 | 0.037096 | 0.050951 | -0.0032407 | 0.0233 | 0.068665 | 0.10529 | 0.09613 | 0.07782 | 0.032043 | 0.027466 | -0.091553 | 0.13733 | 0.17395 | 0.064087 | 0.018311 | 0 | -0.009155 | -0.07782 | 0.086975 | -0.032044 | -122.1771 | 0.16479 | 0.13733 | 0.16937 | -122.1405 | 0.050354 | -0.018311 | -122.1909 | 0.19684 | 0.1236 | 0.14191 | -122.2092 | 0.091552 | 0.12817 | 0.15564 | -122.3007 | 0.07782 | 0.059509 | 0.23346 | -122.287
2761.1875 | 122.3236 | -0.086975 | 122.2229 | -0.088806 | 0.047837 | 0.061182 | 0.00083745 | 0.029969 | 0.0016684 | 0.031714 | -0.15381 | 0.028974 | 0.036668 | 0.05266 | 0.0027407 | 0.0233 | 0.064087 | 0.045776 | 0.018311 | 0.022888 | 0.07782 | 0.022888 | -0.091553 | 0.086975 | 0.073242 | -0.032043 | 0.045776 | 0.027466 | -0.036621 | -0.10071 | 0.10986 | -0.004578 | -122.1451 | 0.13275 | 0.10986 | 0.11444 | -122.1588 | 0.050354 | -0.013733 | -122.1771 | 0.17395 | 0.054932 | 0.068665 | -122.1954 | 0.16479 | 0.15106 | 0.10529 | -122.3145 | 0.13275 | 0.11444 | 0.16022 | -122.3236
2762.9375 | 122.4243 | -0.054932 | 122.2092 | 0.094299 | 0.043778 | 0.061182 | -0.0012987 | 0.030824 | -0.0038858 | 0.033851 | 0.15137 | 0.027478 | 0.032823 | 0.052233 | 0.0029543 | 0.026077 | 0.091553 | 0.1236 | 0.10071 | 0.073242 | 0.032043 | 0.050354 | -0.091553 | 0.14191 | 0.12817 | 0.041199 | 0.009155 | -0.009155 | -0.004578 | -0.050354 | 0.10529 | -0.036621 | -122.1771 | 0.17853 | 0.12817 | 0.16479 | -122.1176 | 0.050354 | 0.004578 | -122.2 | 0.19684 | 0.096131 | 0.091553 | -122.2183 | 0.086975 | 0.14649 | 0.15564 | -122.3007 | 0.064087 | 0.045777 | 0.18311 | -122.2595
2764.6875 | 122.4289 | -0.054932 | 122.1909 | 0.11719 | 0.043137 | 0.063318 | 0.0023329 | 0.030183 | -0.003245 | 0.031928 | 0.021668 | 0.029187 | 0.032823 | 0.050524 | 0.0035953 | 0.024368 | 0.068665 | 0.091553 | 0.068665 | 0.041199 | 0.050354 | 0.059509 | -0.086975 | 0.13733 | 0.11902 | 0.027466 | 0.004578 | 0.004578 | -0.009155 | -0.059509 | 0.11444 | -0.032043 | -122.1405 | 0.14649 | 0.096131 | 0.12817 | -122.1222 | 0.045777 | -0.004577 | -122.1863 | 0.19226 | 0.082398 | 0.086975 | -122.1863 | 0.10529 | 0.1236 | 0.1236 | -122.2778 | 0.05951 | 0.05951 | 0.17395 | -122.2504
2766.375 | 122.438 | -0.064087 | 122.1954 | -0.0048827 | 0.043137 | 0.06524 | 0.0040417 | 0.030397 | -0.0087992 | 0.030646 | 0.044556 | 0.029615 | 0.035814 | 0.051165 | -0.0015317 | 0.026718 | 0.009155 | 0.050354 | 0.07782 | 0.032043 | 0.059509 | 0.045776 | -0.10529 | 0.073242 | 0.091553 | 0.022888 | 0.022888 | 0.018311 | -0.004578 | -0.073242 | 0.10986 | -0.041199 | -122.1359 | 0.11444 | 0.09613 | 0.13733 | -122.1863 | 0.059509 | -0.009155 | -122.1725 | 0.13733 | 0.086975 | 0.09613 | -122.1771 | 0.1236 | 0.073242 | 0.14191 | -122.3007 | 0.086975 | 0.082398 | 0.15564 | -122.2687
2768.125 | 122.406 | -0.059509 | 122.2046 | 0.0027468 | 0.044205 | 0.0599 | -0.00065795 | 0.029756 | -0.0058084 | 0.030646 | 0.059815 | 0.028546 | 0.033037 | 0.050524 | -0.00046349 | 0.023513 | 0.050354 | 0.036621 | 0.059509 | 0.013733 | 0.068665 | 0.059509 | -0.09613 | 0.068665 | 0.064087 | -0.009155 | 0.022888 | 0.022888 | -0.009155 | -0.086975 | 0.11902 | -0.036621 | -122.1359 | 0.09613 | 0.073242 | 0.10986 | -122.1542 | 0.050354 | -0.027466 | -122.1817 | 0.12817 | 0.050354 | 0.07782 | -122.1817 | 0.12817 | 0.10986 | 0.11902 | -122.3007 | 0.082397 | 0.082397 | 0.1236 | -122.2916
2769.8125 | 122.3511 | -0.091553 | 122.2504 | -0.22614 | 0.046555 | 0.062463 | 0.0021191 | 0.031037 | 0.00038662 | 0.030433 | -0.2301 | 0.030469 | 0.037523 | 0.053942 | 0.00039091 | 0.022445 | 0.004578 | -0.036621 | -0.018311 | -0.004578 | 0.091553 | 0.004578 | -0.12817 | 0.032043 | 0.022888 | -0.09613 | 0.073242 | 0.041199 | -0.050354 | -0.09613 | 0.096131 | -0.036621 | -122.1588 | 0.054932 | 0.086975 | 0.1236 | -122.2458 | 0.041199 | -0.004577 | -122.1771 | 0.1236 | -0.004577 | 0 | -122.2092 | 0.18311 | 0.096131 | 0.073242 | -122.3785 | 0.16479 | 0.13275 | 0.11444 | -122.3465
2771.5625 | 122.3694 | -0.068665 | 122.2137 | 0.094299 | 0.047409 | 0.061182 | 0.00019645 | 0.030824 | -0.0017496 | 0.034492 | 0.059815 | 0.030896 | 0.036027 | 0.054369 | 0.0033817 | 0.023727 | 0.013733 | -0.032043 | -0.041199 | -0.018311 | 0.086975 | 0 | -0.1236 | 0.050354 | -0.013733 | -0.10071 | 0.045776 | 0.041199 | -0.050354 | -0.10529 | 0.068665 | -0.054931 | -122.1268 | 0.036622 | 0.050354 | 0.10528 | -122.2 | 0.018311 | -0.036621 | -122.168 | 0.11902 | -0.032043 | 0.004578 | -122.1725 | 0.15564 | 0.082398 | 0.027466 | -122.3373 | 0.11444 | 0.10986 | 0.054932 | -122.319
2773.25 | 122.3785 | -0.073242 | 122.2092 | 0.12482 | 0.042496 | 0.060968 | -0.00023075 | 0.032105 | -0.0038858 | 0.031928 | 0.11322 | 0.030042 | 0.032396 | 0.053087 | 0.00060451 | 0.027359 | 0.10071 | 0.09613 | 0.11444 | 0.064087 | 0.036621 | 0.064087 | -0.07782 | 0.15564 | 0.12817 | 0.032043 | 0.027466 | 0 | -0.027466 | -0.073242 | 0.13733 | -0.004578 | -122.1725 | 0.16937 | 0.13733 | 0.14191 | -122.1085 | 0.045776 | 0 | -122.1817 | 0.22888 | 0.10529 | 0.10529 | -122.2092 | 0.10986 | 0.17395 | 0.18768 | -122.287 | 0.10071 | 0.073242 | 0.20142 | -122.2824
2775 | 122.406 | -0.064087 | 122.1863 | 0.14771 | 0.044846 | 0.058618 | 0.00019645 | 0.031892 | -0.003245 | 0.031287 | 0.18188 | 0.028333 | 0.034959 | 0.05031 | 0.0033817 | 0.025009 | 0.10986 | 0.091553 | 0.10529 | 0.07782 | 0.032043 | 0.059509 | -0.082397 | 0.15564 | 0.1236 | 0.032043 | 0.018311 | 0.004578 | -0.018311 | -0.059509 | 0.1236 | -0.01831 | -122.1542 | 0.15564 | 0.14191 | 0.16022 | -122.0764 | 0.045776 | 0.004578 | -122.168 | 0.21973 | 0.09613 | 0.091552 | -122.1817 | 0.09613 | 0.17395 | 0.16937 | -122.2687 | 0.082398 | 0.068665 | 0.18768 | -122.2458
2776.7656 | 122.4243 | -0.068665 | 122.1909 | -0.0048827 | 0.042496 | 0.061609 | 0.0046827 | 0.032746 | -0.007731 | 0.030219 | 0.059815 | 0.027906 | 0.037736 | 0.051592 | -0.0030271 | 0.026077 | 0.054932 | 0.036621 | 0.068665 | 0.022888 | 0.054932 | 0.045776 | -0.10986 | 0.073242 | 0.068665 | 0.004578 | 0.013733 | 0.009155 | -0.036621 | -0.10529 | 0.11444 | -0.041198 | -122.1359 | 0.10529 | 0.091553 | 0.13275 | -122.1359 | 0.032044 | -0.036621 | -122.1771 | 0.14191 | 0.073243 | 0.10986 | -122.1817 | 0.1236 | 0.1236 | 0.13733 | -122.3007 | 0.082398 | 0.07782 | 0.13733 | -122.2961
2778.4531 | 122.3785 | -0.054932 | 122.2046 | 0.079041 | 0.039933 | 0.062891 | 0.00041005 | 0.032319 | -0.0051676 | 0.027442 | 0.090332 | 0.027051 | 0.035387 | 0.050738 | 0.0010317 | 0.024795 | 0.086975 | 0.068665 | 0.068665 | 0.036621 | 0.022888 | 0.064087 | -0.07782 | 0.10986 | 0.082397 | -0.004578 | 0.018311 | 0.004578 | -0.013733 | -0.064087 | 0.11902 | -0.022888 | -122.1817 | 0.1236 | 0.091553 | 0.11444 | -122.1176 | 0.041199 | -0.009155 | -122.1863 | 0.16479 | 0.050354 | 0.059509 | -122.2 | 0.07782 | 0.14191 | 0.1236 | -122.2824 | 0.073243 | 0.05951 | 0.13733 | -122.2687
2780.2031 | 122.3877 | -0.068665 | 122.2092 | 0.033264 | 0.041214 | 0.06225 | 0.0016919 | 0.031465 | -0.006022 | 0.029792 | 0.059815 | 0.028333 | 0.032823 | 0.052019 | 0.00017731 | 0.025222 | 0.059509 | 0.050354 | 0.073242 | 0.041199 | 0.041199 | 0.07782 | -0.09613 | 0.10529 | 0.07782 | 0 | 0.013733 | 0.013733 | -0.027466 | -0.086975 | 0.14649 | -0.027465 | -122.168 | 0.11902 | 0.10986 | 0.13733 | -122.1497 | 0.041199 | -0.01831 | -122.1954 | 0.17395 | 0.068665 | 0.086975 | -122.1954 | 0.10986 | 0.12817 | 0.14191 | -122.3053 | 0.082398 | 0.082398 | 0.14649 | -122.2961
2781.9688 | 122.3602 | -0.086975 | 122.2137 | -0.20325 | 0.046982 | 0.05755 | 0.0021191 | 0.03296 | 0.00060022 | 0.031714 | -0.2301 | 0.028546 | 0.03795 | 0.052447 | 0.0025271 | 0.022018 | 0.045776 | -0.004578 | -0.004578 | 0.018311 | 0.086975 | 0.013733 | -0.1236 | 0.073242 | 0.064087 | -0.059509 | 0.059509 | 0.032043 | -0.045776 | -0.10529 | 0.10071 | -0.036621 | -122.1268 | 0.082397 | 0.10529 | 0.14191 | -122.168 | 0.041199 | -0.018311 | -122.1542 | 0.16022 | 0.027466 | 0.045777 | -122.1817 | 0.17395 | 0.13275 | 0.082397 | -122.3373 | 0.14648 | 0.11902 | 0.15106 | -122.319
2783.7344 | 122.4289 | -0.050354 | 122.2092 | 0.10193 | 0.041428 | 0.059473 | 0.0023329 | 0.030824 | 0.00038662 | 0.034705 | 0.13611 | 0.028119 | 0.035814 | 0.053301 | 0.0012455 | 0.025436 | 0.1236 | 0.09613 | 0.10529 | 0.07782 | 0.032043 | 0.050354 | -0.09613 | 0.16022 | 0.1236 | 0.027466 | -0.018311 | 0 | -0.004578 | -0.054932 | 0.10071 | -0.045776 | -122.1771 | 0.14648 | 0.12817 | 0.17395 | -122.0856 | 0.045776 | -0.004578 | -122.2275 | 0.21057 | 0.07782 | 0.082398 | -122.2092 | 0.082397 | 0.17395 | 0.15564 | -122.3053 | 0.032043 | 0.050354 | 0.17395 | -122.2641
2785.4219 | 122.3328 | -0.07782 | 122.2366 | 0.063782 | 0.0457 | 0.06225 | 0.00062385 | 0.029969 | -0.00025418 | 0.03321 | 0.097962 | 0.027478 | 0.035814 | 0.051592 | 0.0048769 | 0.023086 | 0.027466 | -0.041199 | -0.050354 | -0.018311 | 0.068665 | 0.022888 | -0.12817 | 0.045776 | -0.027466 | -0.10986 | 0.045776 | 0.041199 | -0.054932 | -0.11444 | 0.10071 | -0.050354 | -122.168 | 0.036621 | 0.059509 | 0.10986 | -122.2092 | 0.022888 | -0.036621 | -122.1909 | 0.1236 | -0.032043 | 0.004578 | -122.1954 | 0.14649 | 0.10529 | 0.027466 | -122.3648 | 0.1236 | 0.11902 | 0.050354 | -122.3511
2787.1875 | 122.3145 | -0.1236 | 122.2275 | -0.1651 | 0.047409 | 0.063104 | 0.0063917 | 0.033174 | -0.0045266 | 0.030433 | -0.22247 | 0.029401 | 0.038805 | 0.052233 | -0.0030271 | 0.023941 | 0.07782 | 0.10071 | 0.10071 | 0.068665 | 0.050354 | 0.041199 | -0.10986 | 0.09613 | 0.11444 | -0.018311 | 0.032043 | 0.009155 | -0.027466 | -0.082397 | 0.16479 | 0.013733 | -122.1771 | 0.2243 | 0.19226 | 0.17853 | -122.1497 | 0.09613 | 0.041199 | -122.1954 | 0.21973 | 0.10528 | 0.064086 | -122.2183 | 0.17395 | 0.20142 | 0.2243 | -122.3373 | 0.15564 | 0.13275 | 0.23804 | -122.3099
2788.875 | 122.3236 | -0.10071 | 122.2137 | -0.10406 | 0.048264 | 0.059045 | 0.0042555 | 0.031037 | -4.058e-05 | 0.034064 | -0.15381 | 0.028974 | 0.037096 | 0.053942 | 0.00017731 | 0.022873 | 0.041199 | 0.036621 | 0.032043 | 0.036621 | 0.073242 | 0.013733 | -0.11444 | 0.091553 | 0.091553 | -0.041199 | 0.059509 | 0.036621 | -0.054932 | -0.10529 | 0.11444 | -0.013733 | -122.1405 | 0.13733 | 0.13733 | 0.15106 | -122.1725 | 0.045776 | -0.004578 | -122.1542 | 0.19226 | 0.059509 | 0.064087 | -122.1771 | 0.17395 | 0.14191 | 0.13275 | -122.3282 | 0.16022 | 0.13733 | 0.19226 | -122.319
2790.625 | 122.3923 | -0.059509 | 122.2137 | 0.10193 | 0.046128 | 0.060541 | 0.0019055 | 0.031037 | -0.0013224 | 0.031287 | 0.036926 | 0.030042 | 0.035173 | 0.051806 | 0.0038089 | 0.02565 | -0.018311 | -0.018311 | -0.027466 | -0.009155 | 0.091553 | 0.009155 | -0.10529 | 0.045776 | 0.004578 | -0.091553 | 0.068665 | 0.041199 | -0.054932 | -0.10071 | 0.068664 | -0.045777 | -122.1222 | 0.041198 | 0.050354 | 0.096131 | -122.2321 | 0.004577 | -0.041199 | -122.1451 | 0.10528 | -0.032044 | 0.009155 | -122.1725 | 0.15106 | 0.041198 | 0.032043 | -122.319 | 0.12817 | 0.10071 | 0.064087 | -122.3145
2792.3125 | 122.4197 | -0.064087 | 122.2275 | -0.0048827 | 0.041001 | 0.061395 | 0.0019055 | 0.033174 | -0.010081 | 0.031287 | 0.052185 | 0.027692 | 0.036241 | 0.050738 | -0.0025999 | 0.027999 | 0 | 0.050354 | 0.064087 | 0.032043 | 0.059509 | 0.050354 | -0.091553 | 0.086975 | 0.086975 | 0.013733 | 0.045776 | 0.018311 | -0.013733 | -0.068665 | 0.11444 | -0.027466 | -122.168 | 0.11444 | 0.09613 | 0.1236 | -122.2275 | 0.050354 | -0.004578 | -122.1817 | 0.15106 | 0.07782 | 0.082398 | -122.2092 | 0.1236 | 0.064087 | 0.12817 | -122.319 | 0.10986 | 0.082398 | 0.15106 | -122.2961
2794.0625 | 122.3923 | -0.064087 | 122.2183 | -0.17273 | 0.043137 | 0.063104 | 0.0042555 | 0.033174 | -0.0053812 | 0.030219 | -0.14618 | 0.028119 | 0.037523 | 0.049883 | -0.0021725 | 0.025009 | 0.09613 | 0.14648 | 0.12817 | 0.07782 | 0.036621 | 0.054932 | -0.09613 | 0.14648 | 0.1831 | 0.064087 | 0.032043 | 0.009155 | -0.018311 | -0.054932 | 0.11902 | -0.032043 | -122.1817 | 0.21057 | 0.14191 | 0.17395 | -122.1222 | 0.045776 | 0.009155 | -122.1863 | 0.21057 | 0.12817 | 0.11902 | -122.2092 | 0.10071 | 0.16022 | 0.19226 | -122.3145 | 0.09613 | 0.073242 | 0.24719 | -122.2733
2795.8125 | 122.438 | -0.059509 | 122.1817 | -0.13458 | 0.041001 | 0.063532 | 0.0029737 | 0.032105 | -0.0064492 | 0.029578 | -0.10803 | 0.025983 | 0.035387 | 0.050951 | -0.0023861 | 0.024154 | 0.11444 | 0.15106 | 0.14648 | 0.07782 | 0.045776 | 0.064087 | -0.086975 | 0.14648 | 0.16937 | 0.050354 | 0.013733 | 0.009155 | -0.009155 | -0.054932 | 0.1236 | -0.027466 | -122.1359 | 0.21057 | 0.13733 | 0.16479 | -122.0673 | 0.050354 | 0.004577 | -122.168 | 0.20599 | 0.10986 | 0.10529 | -122.1725 | 0.10528 | 0.17395 | 0.20599 | -122.2687 | 0.073242 | 0.068664 | 0.22888 | -122.2366
2797.5 | 122.3373 | -0.09613 | 122.2229 | -0.18036 | 0.046555 | 0.060754 | 0.0059643 | 0.033174 | -0.0038858 | 0.030006 | -0.15381 | 0.02876 | 0.036027 | 0.051806 | -0.00089089 | 0.022873 | 0.07782 | 0.1236 | 0.10986 | 0.064087 | 0.045776 | 0.068665 | -0.091553 | 0.11902 | 0.13733 | 0.032043 | 0.004578 | 0.009155 | -0.027466 | -0.091553 | 0.16479 | 0.004577 | -122.1771 | 0.21973 | 0.16022 | 0.15564 | -122.1451 | 0.068664 | 0.004577 | -122.2183 | 0.21515 | 0.12817 | 0.1236 | -122.2137 | 0.14191 | 0.17395 | 0.20599 | -122.3145 | 0.10071 | 0.10528 | 0.23346 | -122.3145
2799.2656 | 122.3419 | -0.073242 | 122.2321 | 0.040894 | 0.046555 | 0.061182 | -1.7146e-05 | 0.031678 | 0.0025228 | 0.033423 | -0.0012209 | 0.030255 | 0.0356 | 0.053301 | 0.0031681 | 0.023941 | 0.018311 | -0.050354 | -0.050354 | -0.036621 | 0.09613 | 0.013733 | -0.12817 | 0.036621 | -0.013733 | -0.11444 | 0.041199 | 0.050354 | -0.041199 | -0.10986 | 0.086975 | -0.054932 | -122.1359 | 0.022888 | 0.036621 | 0.091553 | -122.2137 | 0.032043 | -0.036621 | -122.1909 | 0.10986 | -0.041199 | -0.004578 | -122.1817 | 0.16937 | 0.091553 | 0.022888 | -122.3602 | 0.11444 | 0.1236 | 0.059509 | -122.3419
2801.0312 | 122.3007 | -0.10986 | 122.2321 | -0.25665 | 0.046768 | 0.06225 | 0.0059643 | 0.032319 | -0.0047404 | 0.029151 | -0.10803 | 0.030042 | 0.038377 | 0.050097 | 0.00060451 | 0.024582 | 0.004578 | 0.054932 | 0.009155 | 0.009155 | 0.068665 | 0.013733 | -0.10986 | 0.041199 | 0.045776 | -0.059509 | 0.045776 | 0.022888 | -0.059509 | -0.10529 | 0.1236 | 0 | -122.1634 | 0.16479 | 0.11902 | 0.11902 | -122.2275 | 0.050354 | 0.004577 | -122.1863 | 0.15106 | 0.050354 | 0.045777 | -122.2092 | 0.17853 | 0.11444 | 0.11902 | -122.3419 | 0.15564 | 0.13275 | 0.15564 | -122.3373
2802.7812 | 122.3511 | -0.086975 | 122.2229 | -0.21088 | 0.045273 | 0.062463 | 0.0051099 | 0.033387 | -0.006663 | 0.029151 | -0.13855 | 0.028546 | 0.038377 | 0.051806 | -0.0021725 | 0.0233 | 0.082397 | 0.12817 | 0.11444 | 0.068665 | 0.050354 | 0.050354 | -0.091553 | 0.13733 | 0.16022 | 0.041199 | 0.018311 | 0.013733 | -0.009155 | -0.073242 | 0.13733 | -0.004578 | -122.1725 | 0.21515 | 0.15564 | 0.16022 | -122.1405 | 0.07782 | 0.013733 | -122.2046 | 0.2243 | 0.12817 | 0.11444 | -122.2092 | 0.13733 | 0.16937 | 0.20142 | -122.3145 | 0.10529 | 0.10071 | 0.24719 | -122.2961
2804.5312 | 122.3465 | -0.086975 | 122.2641 | -0.24139 | 0.047196 | 0.060968 | 0.0040417 | 0.032319 | 0.00081382 | 0.031714 | -0.2301 | 0.030042 | 0.038805 | 0.054156 | 0.00081811 | 0.024368 | -0.013733 | 0.009155 | -0.036621 | -0.004578 | 0.068665 | 0.009155 | -0.1236 | 0.032043 | 0.050354 | -0.082397 | 0.054932 | 0.041199 | -0.045776 | -0.11902 | 0.09613 | -0.036621 | -122.1954 | 0.09613 | 0.082397 | 0.11902 | -122.2778 | 0.041199 | -0.032044 | -122.2092 | 0.11902 | 0.004578 | 0.036622 | -122.2229 | 0.15564 | 0.073242 | 0.050354 | -122.3877 | 0.14191 | 0.12817 | 0.13733 | -122.3831
2806.2969 | 122.4152 | -0.054932 | 122.1954 | 0.094299 | 0.044205 | 0.061609 | 0.0021191 | 0.030397 | -0.0011088 | 0.032783 | 0.12085 | 0.030469 | 0.036241 | 0.053087 | 0.0029543 | 0.025222 | -0.009155 | 0.004578 | -0.009155 | -0.009155 | 0.059509 | 0.022888 | -0.12817 | 0.07782 | 0.032043 | -0.068665 | 0.036621 | 0.032043 | -0.032043 | -0.082397 | 0.07782 | -0.073242 | -122.1359 | 0.05951 | 0.045777 | 0.11902 | -122.2046 | 0.022889 | -0.027465 | -122.1588 | 0.13275 | -0.013733 | 0.013732 | -122.1634 | 0.11444 | 0.045777 | 0.045777 | -122.3236 | 0.091553 | 0.086975 | 0.086975 | -122.2778
2808 | 122.3831 | -0.041199 | 122.1863 | 0.10193 | 0.044205 | 0.060754 | 0.0019055 | 0.034242 | -0.0051676 | 0.034278 | 0.14374 | 0.029401 | 0.03795 | 0.051378 | 0.00039091 | 0.026291 | 0.073242 | 0.13733 | 0.10071 | 0.054932 | 0.027466 | 0.064087 | -0.086975 | 0.14648 | 0.10986 | 0.045776 | 0.018311 | -0.009155 | -0.013733 | -0.073242 | 0.10529 | -0.045776 | -122.1588 | 0.17853 | 0.096131 | 0.14191 | -122.113 | 0.027466 | -0.032043 | -122.168 | 0.18768 | 0.086975 | 0.11902 | -122.1954 | 0.068665 | 0.11444 | 0.14191 | -122.2733 | 0.05951 | 0.032044 | 0.15106 | -122.2595
2809.6875 | 122.3145 | -0.10071 | 122.2641 | -0.22614 | 0.044632 | 0.062463 | 0.00062385 | 0.032319 | -0.0058084 | 0.03086 | -0.1767 | 0.029615 | 0.034105 | 0.048601 | -0.00024989 | 0.026291 | 0.036621 | 0.068665 | 0.036621 | 0.022888 | 0.068665 | 0.022888 | -0.10529 | 0.050354 | 0.050354 | -0.073242 | 0.041199 | 0.041199 | -0.041199 | -0.10529 | 0.1236 | -0.004578 | -122.1954 | 0.16937 | 0.1236 | 0.12817 | -122.2275 | 0.059509 | -0.004578 | -122.2229 | 0.15106 | 0.027466 | 0.032044 | -122.2229 | 0.16937 | 0.13733 | 0.13733 | -122.3694 | 0.14191 | 0.14191 | 0.15106 | -122.3694
2811.4375 | 122.4701 | -0.054932 | 122.2183 | -0.058289 | 0.041855 | 0.064813 | 0.0046827 | 0.031465 | -0.0079446 | 0.029792 | -0.062256 | 0.028333 | 0.034532 | 0.050738 | -0.0019589 | 0.02565 | 0.036621 | 0.086975 | 0.09613 | 0.045776 | 0.041199 | 0.036621 | -0.082397 | 0.1236 | 0.13733 | 0.050354 | 0.018311 | 0.032043 | -0.004578 | -0.073242 | 0.091553 | -0.027465 | -122.1771 | 0.14191 | 0.10071 | 0.12817 | -122.1817 | 0.050354 | -0.01831 | -122.2 | 0.17853 | 0.10529 | 0.1236 | -122.1863 | 0.096131 | 0.091553 | 0.15106 | -122.3007 | 0.073243 | 0.086975 | 0.19226 | -122.2916
2813.1875 | 122.3145 | -0.09613 | 122.2321 | -0.22614 | 0.046341 | 0.060968 | 0.0048963 | 0.031892 | -0.001536 | 0.029365 | -0.19196 | 0.02876 | 0.035814 | 0.052447 | -0.0011045 | 0.026077 | -0.009155 | 0.027466 | 0.013733 | 0 | 0.073242 | 0.018311 | -0.11902 | 0.027466 | 0.036621 | -0.068665 | 0.059509 | 0.045776 | -0.064087 | -0.10986 | 0.11444 | -0.022889 | -122.1588 | 0.1236 | 0.09613 | 0.11902 | -122.2412 | 0.032043 | -0.013733 | -122.1725 | 0.1236 | 0.027465 | 0.041198 | -122.1863 | 0.16937 | 0.086975 | 0.10986 | -122.3511 | 0.15564 | 0.14191 | 0.13275 | -122.3419
2814.9375 | 122.3236 | -0.091553 | 122.2458 | -0.18799 | 0.039719 | 0.061182 | 0.0014783 | 0.034242 | -0.0036722 | 0.031714 | -0.16144 | 0.028119 | 0.0356 | 0.052233 | -0.00067729 | 0.026718 | 0.073242 | 0.14191 | 0.10529 | 0.064087 | 0.036621 | 0.054932 | -0.10529 | 0.11902 | 0.16022 | 0.022888 | 0.022888 | 0.009155 | -0.018311 | -0.07782 | 0.14649 | -0.013733 | -122.2092 | 0.23346 | 0.15564 | 0.16937 | -122.1725 | 0.073242 | 0.013733 | -122.2229 | 0.21057 | 0.11444 | 0.10071 | -122.2366 | 0.12817 | 0.16479 | 0.19684 | -122.3511 | 0.11444 | 0.10071 | 0.25177 | -122.3236
2816.6406 | 122.4197 | -0.054932 | 122.2046 | 0.071411 | 0.043778 | 0.061182 | 0.0012647 | 0.031465 | 0.00038662 | 0.03321 | 0.082703 | 0.030255 | 0.037523 | 0.052019 | 0.0018863 | 0.024582 | 0.091553 | 0.11444 | 0.07782 | 0.073242 | 0.045776 | 0.059509 | -0.09613 | 0.15106 | 0.13275 | 0.027466 | 0.004578 | -0.009155 | -0.009155 | -0.050354 | 0.11444 | -0.041198 | -122.1588 | 0.16937 | 0.12817 | 0.16937 | -122.113 | 0.045777 | 0.004578 | -122.2 | 0.20599 | 0.082398 | 0.07782 | -122.2137 | 0.10071 | 0.14649 | 0.13275 | -122.3007 | 0.05951 | 0.045777 | 0.18768 | -122.2549
2818.3906 | 122.3465 | -0.086975 | 122.2275 | 0.13245 | 0.04506 | 0.060541 | -1.7146e-05 | 0.033387 | -0.0011088 | 0.033637 | 0.059815 | 0.029828 | 0.035387 | 0.052019 | 0.0042361 | 0.026077 | 0 | -0.041199 | -0.036621 | -0.013733 | 0.086975 | 0.027466 | -0.12817 | 0.041199 | -0.009155 | -0.11444 | 0.050354 | 0.041199 | -0.032043 | -0.10986 | 0.11444 | -0.041199 | -122.1405 | 0.045776 | 0.073242 | 0.11444 | -122.2275 | 0.054932 | -0.022888 | -122.1771 | 0.12817 | -0.027466 | -0.004578 | -122.1863 | 0.17395 | 0.086975 | 0.050354 | -122.3557 | 0.13733 | 0.12817 | 0.07782 | -122.3373
2820.0938 | 122.4564 | -0.045776 | 122.2137 | -0.0048827 | 0.044846 | 0.061609 | 0.0066053 | 0.031678 | -0.0075174 | 0.030006 | 0.036926 | 0.027906 | 0.036882 | 0.050097 | -0.0034543 | 0.027572 | 0.009155 | 0.054932 | 0.054932 | 0.036621 | 0.054932 | 0.064087 | -0.10529 | 0.07782 | 0.091553 | 0.013733 | 0.032043 | 0.009155 | -0.018311 | -0.09613 | 0.10986 | -0.05951 | -122.1588 | 0.10071 | 0.082397 | 0.14191 | -122.2046 | 0.027465 | -0.050354 | -122.1817 | 0.1236 | 0.059509 | 0.10986 | -122.2046 | 0.10071 | 0.054931 | 0.10071 | -122.319 | 0.077819 | 0.054931 | 0.13733 | -122.3099
2821.8594 | 122.3007 | -0.09613 | 122.2321 | -0.04303 | 0.047837 | 0.059686 | 0.0027601 | 0.031251 | 0.003591 | 0.032142 | -0.062256 | 0.031751 | 0.036668 | 0.052233 | 0.0038089 | 0.023513 | 0.041199 | 0.041199 | 0 | 0.009155 | 0.07782 | 0.022888 | -0.12817 | 0.050354 | 0.018311 | -0.086975 | 0.036621 | 0.041199 | -0.054932 | -0.11902 | 0.11902 | -0.032044 | -122.1542 | 0.13733 | 0.10528 | 0.13733 | -122.1909 | 0.041198 | -0.022889 | -122.1954 | 0.14648 | 0.009155 | 0.032044 | -122.1909 | 0.17395 | 0.13733 | 0.09613 | -122.3602 | 0.13275 | 0.13733 | 0.11444 | -122.3511
2823.6094 | 122.438 | -0.050354 | 122.2137 | 0.094299 | 0.04805 | 0.060114 | 0.0066053 | 0.029969 | -0.0011088 | 0.034919 | 0.14374 | 0.028333 | 0.039445 | 0.05031 | -3.629e-05 | 0.025863 | 0 | -0.004578 | 0.004578 | 0 | 0.07782 | 0.018311 | -0.11444 | 0.09613 | 0.064087 | -0.018311 | 0.027466 | 0.022888 | -0.032043 | -0.086975 | 0.068665 | -0.064087 | -122.1359 | 0.045776 | 0.050354 | 0.11444 | -122.2137 | 0.018311 | -0.036621 | -122.1863 | 0.14648 | 0.032043 | 0.068664 | -122.1909 | 0.12817 | 0.050354 | 0.054932 | -122.3282 | 0.07782 | 0.073242 | 0.11444 | -122.3007
2825.3594 | 122.374 | -0.059509 | 122.2183 | 0.094299 | 0.043351 | 0.0599 | 0.0025465 | 0.029756 | -0.0073038 | 0.032996 | 0.11322 | 0.027265 | 0.0356 | 0.052233 | -0.00089089 | 0.027786 | 0.068665 | 0.11444 | 0.10071 | 0.036621 | 0.036621 | 0.064087 | -0.082397 | 0.11444 | 0.10529 | 0.013733 | 0.009155 | 0.009155 | 0 | -0.064087 | 0.1236 | -0.022888 | -122.1817 | 0.17395 | 0.09613 | 0.11902 | -122.1497 | 0.059509 | -0.004578 | -122.2092 | 0.17395 | 0.073242 | 0.07782 | -122.2092 | 0.09613 | 0.12817 | 0.16022 | -122.3007 | 0.068664 | 0.068664 | 0.16479 | -122.2824
2827.0625 | 122.3145 | -0.09613 | 122.2412 | -0.088806 | 0.045273 | 0.060114 | 0.0038281 | 0.031251 | 0.0016684 | 0.035346 | -0.13092 | 0.029615 | 0.037523 | 0.052019 | 0.0016727 | 0.0233 | 0.059509 | 0.059509 | 0.041199 | 0.027466 | 0.073242 | 0.022888 | -0.10529 | 0.073242 | 0.086975 | -0.059509 | 0.036621 | 0.022888 | -0.032043 | -0.09613 | 0.11902 | -0.009156 | -122.168 | 0.15564 | 0.1236 | 0.13275 | -122.1817 | 0.064087 | 0 | -122.2046 | 0.16937 | 0.036621 | 0.036621 | -122.2183 | 0.16937 | 0.15564 | 0.13733 | -122.3465 | 0.13275 | 0.11902 | 0.1831 | -122.3373
2828.8281 | 122.4335 | -0.036621 | 122.2321 | 0.071411 | 0.044205 | 0.060968 | 0.0025465 | 0.028901 | -0.002604 | 0.034278 | 0.11322 | 0.028119 | 0.037309 | 0.051806 | 0.0018863 | 0.025863 | 0.009155 | -0.009155 | -0.027466 | -0.013733 | 0.07782 | 0.018311 | -0.11444 | 0.068665 | 0.009155 | -0.059509 | 0.050354 | 0.045776 | -0.050354 | -0.091553 | 0.054932 | -0.07782 | -122.1542 | 0.027466 | 0.022888 | 0.10071 | -122.2229 | -0.013733 | -0.054932 | -122.1817 | 0.10529 | -0.022888 | 0.032044 | -122.1863 | 0.11444 | 0.045776 | 0.009155 | -122.3465 | 0.086975 | 0.082397 | 0.045776 | -122.3236
2830.5156 | 122.3969 | -0.068665 | 122.2229 | 0.10956 | 0.045273 | 0.062677 | 0.00083745 | 0.030824 | -0.0013224 | 0.032355 | 0.052185 | 0.029828 | 0.036455 | 0.05266 | 0.0018863 | 0.027359 | 0.009155 | -0.018311 | -0.032043 | -0.018311 | 0.082397 | 0.032043 | -0.13733 | 0.041199 | 0.009155 | -0.073242 | 0.041199 | 0.032043 | -0.036621 | -0.091553 | 0.10071 | -0.068664 | -122.1405 | 0.050354 | 0.050354 | 0.11902 | -122.2137 | 0.032044 | -0.022888 | -122.1817 | 0.10986 | -0.004577 | 0.018311 | -122.1909 | 0.15106 | 0.07782 | 0.036622 | -122.3602 | 0.10986 | 0.10071 | 0.07782 | -122.3145
2832.2812 | 122.4289 | -0.059509 | 122.2092 | -0.073547 | 0.041855 | 0.061609 | 0.0040417 | 0.030183 | -0.0098672 | 0.031714 | -0.054626 | 0.027051 | 0.035814 | 0.049883 | -0.0036679 | 0.027359 | 0.041199 | 0.09613 | 0.09613 | 0.068665 | 0.045776 | 0.045776 | -0.091553 | 0.15106 | 0.16479 | 0.068665 | 0.009155 | 0.009155 | -0.018311 | -0.068665 | 0.10528 | -0.032044 | -122.1634 | 0.15564 | 0.12817 | 0.16022 | -122.168 | 0.041198 | -0.009156 | -122.2 | 0.21057 | 0.12817 | 0.13733 | -122.2 | 0.10528 | 0.10071 | 0.15564 | -122.3007 | 0.068664 | 0.068664 | 0.2243 | -122.2778
2834.0469 | 122.4335 | -0.064087 | 122.2275 | -0.13458 | 0.044846 | 0.06524 | 0.0051099 | 0.033387 | -0.0079446 | 0.030433 | -0.062256 | 0.029401 | 0.035387 | 0.050738 | -0.0028135 | 0.024582 | 0.082397 | 0.13733 | 0.11444 | 0.07782 | 0.054932 | 0.041199 | -0.086975 | 0.15564 | 0.18768 | 0.073242 | 0.027466 | -0.009155 | -0.018311 | -0.050354 | 0.10529 | -0.022888 | -122.1725 | 0.20142 | 0.14191 | 0.16479 | -122.1451 | 0.045776 | 0.013733 | -122.2 | 0.21973 | 0.13733 | 0.1236 | -122.2366 | 0.11902 | 0.14648 | 0.17853 | -122.3145 | 0.091553 | 0.054932 | 0.25177 | -122.2778
2835.7969 | 122.438 | -0.045776 | 122.2137 | 0.079041 | 0.042923 | 0.060754 | 0.0010511 | 0.033814 | -0.0038858 | 0.032355 | 0.12085 | 0.029401 | 0.036241 | 0.052874 | 0.0010317 | 0.024795 | 0.10986 | 0.091553 | 0.10529 | 0.073242 | 0.050354 | 0.059509 | -0.07782 | 0.16022 | 0.11902 | 0.032043 | 0.009155 | -0.004578 | -0.009155 | -0.082397 | 0.10528 | -0.032044 | -122.1634 | 0.13733 | 0.11902 | 0.15106 | -122.1039 | 0.036621 | -0.036621 | -122.2046 | 0.20599 | 0.077819 | 0.11444 | -122.2183 | 0.09613 | 0.15564 | 0.15106 | -122.2916 | 0.054931 | 0.041198 | 0.16479 | -122.2961
2837.5469 | 122.3145 | -0.082397 | 122.2504 | 0.033264 | 0.046768 | 0.058618 | 0.0016919 | 0.033601 | 0.0012412 | 0.032355 | -0.0012209 | 0.030255 | 0.038377 | 0.053728 | 0.0018863 | 0.023513 | 0.004578 | -0.045776 | -0.045776 | -0.013733 | 0.086975 | 0.018311 | -0.11444 | 0 | -0.022888 | -0.13275 | 0.050354 | 0.045776 | -0.059509 | -0.09613 | 0.10071 | -0.032044 | -122.1634 | 0.036621 | 0.068664 | 0.10071 | -122.2458 | 0.022888 | -0.013733 | -122.2 | 0.082397 | -0.050354 | -0.036621 | -122.2046 | 0.16937 | 0.086975 | 0.036621 | -122.3648 | 0.13275 | 0.12817 | 0.059509 | -122.3465
2839.25 | 122.319 | -0.086975 | 122.2458 | -0.096436 | 0.045914 | 0.060968 | 0.0027601 | 0.032319 | -0.001536 | 0.033423 | -0.11566 | 0.03111 | 0.034318 | 0.053301 | 0.0038089 | 0.025009 | 0.068665 | 0.059509 | 0.013733 | 0.018311 | 0.068665 | 0.022888 | -0.1236 | 0.07782 | 0.082397 | -0.059509 | 0.054932 | 0.032043 | -0.041199 | -0.10071 | 0.10986 | -0.036621 | -122.1771 | 0.14648 | 0.10529 | 0.14191 | -122.1771 | 0.045776 | -0.013733 | -122.1909 | 0.16479 | 0.027466 | 0.041199 | -122.2137 | 0.15564 | 0.15564 | 0.10071 | -122.3694 | 0.14191 | 0.11902 | 0.16937 | -122.3465
2841 | 122.3145 | -0.10529 | 122.2504 | -0.26428 | 0.045273 | 0.062463 | 0.0070325 | 0.031892 | -0.0051676 | 0.032569 | -0.1767 | 0.026624 | 0.040727 | 0.053301 | -0.0040951 | 0.026718 | 0.036621 | 0.073242 | 0.059509 | 0.032043 | 0.059509 | 0.032043 | -0.11444 | 0.050354 | 0.054932 | -0.032043 | 0.064087 | 0.027466 | -0.045776 | -0.09613 | 0.13733 | -0.009155 | -122.1909 | 0.17853 | 0.13733 | 0.14648 | -122.2137 | 0.05951 | 0.009156 | -122.1863 | 0.15564 | 0.073243 | 0.064087 | -122.2229 | 0.16479 | 0.14191 | 0.16479 | -122.3648 | 0.16937 | 0.13275 | 0.16022 | -122.3465
2842.75 | 122.3328 | -0.09613 | 122.2549 | -0.24139 | 0.045914 | 0.060541 | 0.0048963 | 0.029542 | -0.004954 | 0.031287 | -0.21484 | 0.027478 | 0.038591 | 0.053515 | -0.0015317 | 0.023513 | 0.027466 | 0.091553 | 0.07782 | 0.059509 | 0.064087 | 0.032043 | -0.09613 | 0.045776 | 0.091553 | -0.032043 | 0.050354 | 0.027466 | -0.041199 | -0.10529 | 0.12817 | 0 | -122.1909 | 0.18768 | 0.15564 | 0.15564 | -122.2275 | 0.054931 | -0.009156 | -122.2046 | 0.14191 | 0.064087 | 0.073243 | -122.2275 | 0.16022 | 0.1236 | 0.17395 | -122.3511 | 0.14648 | 0.1236 | 0.18768 | -122.3602
2844.5 | 122.4564 | -0.054932 | 122.1863 | -0.020142 | 0.041855 | 0.060754 | 0.0044691 | 0.033174 | -0.006663 | 0.029792 | -0.016479 | 0.025769 | 0.038164 | 0.050951 | -0.0021725 | 0.025222 | 0.018311 | 0.091553 | 0.073242 | 0.036621 | 0.054932 | 0.041199 | -0.09613 | 0.10986 | 0.11902 | 0.032043 | 0.009155 | -0.013733 | -0.022888 | -0.064087 | 0.096131 | -0.041198 | -122.1313 | 0.14649 | 0.091553 | 0.13275 | -122.168 | 0.032044 | -0.009155 | -122.1771 | 0.16479 | 0.086975 | 0.09613 | -122.2 | 0.10986 | 0.073243 | 0.12817 | -122.2824 | 0.064087 | 0.041199 | 0.17395 | -122.2504
2846.1875 | 122.319 | -0.11902 | 122.2321 | -0.18036 | 0.046128 | 0.062036 | 0.0061781 | 0.03296 | -0.0023904 | 0.02851 | -0.24536 | 0.029187 | 0.037096 | 0.051806 | 0.0010317 | 0.024154 | 0.004578 | -0.004578 | -0.013733 | -0.022888 | 0.091553 | 0 | -0.13733 | 0.022888 | 0.027466 | -0.086975 | 0.068665 | 0.022888 | -0.068665 | -0.10986 | 0.11902 | -0.01831 | -122.1405 | 0.11444 | 0.096131 | 0.11444 | -122.2275 | 0.050354 | 0.009156 | -122.1634 | 0.14191 | 0.032044 | 0.022888 | -122.2092 | 0.21057 | 0.1236 | 0.10529 | -122.3694 | 0.18768 | 0.14191 | 0.14649 | -122.3419
2847.9375 | 122.3099 | -0.091553 | 122.2687 | -0.096436 | 0.047409 | 0.060754 | 0.0021191 | 0.033601 | 0.0020956 | 0.030006 | -0.14618 | 0.029615 | 0.036668 | 0.05266 | 0.0027407 | 0.021804 | 0.068665 | 0.045776 | 0.027466 | 0.036621 | 0.07782 | 0.022888 | -0.10986 | 0.073242 | 0.059509 | -0.059509 | 0.045776 | 0.027466 | -0.045776 | -0.091553 | 0.11444 | -0.01831 | -122.1909 | 0.13733 | 0.12817 | 0.14648 | -122.2 | 0.045777 | 0 | -122.2229 | 0.16479 | 0.032044 | 0.032044 | -122.2412 | 0.16937 | 0.16022 | 0.11902 | -122.3785 | 0.13733 | 0.11902 | 0.15106 | -122.3602
2849.6875 | 122.2916 | -0.10986 | 122.2275 | -0.050659 | 0.0504 | 0.057977 | 0.0040417 | 0.032319 | 0.0014548 | 0.033423 | -0.031738 | 0.033246 | 0.038805 | 0.053515 | 0.0027407 | 0.02565 | 0.041199 | 0.036621 | 0.009155 | 0.009155 | 0.082397 | 0.009155 | -0.10529 | 0.036621 | 0.022888 | -0.09613 | 0.041199 | 0.027466 | -0.036621 | -0.11902 | 0.11902 | 0.004577 | -122.1451 | 0.14648 | 0.11902 | 0.11444 | -122.1863 | 0.073242 | -0.009156 | -122.1863 | 0.14648 | 0.013733 | 0.022889 | -122.2 | 0.19226 | 0.15106 | 0.11902 | -122.3328 | 0.15106 | 0.13733 | 0.13275 | -122.3465
2851.3906 | 122.4472 | -0.068665 | 122.1909 | -0.0048827 | 0.046341 | 0.059045 | 0.0038281 | 0.031678 | -0.0096536 | 0.032783 | 0.052185 | 0.028546 | 0.036027 | 0.05266 | -0.0032407 | 0.025009 | -0.018311 | 0.068665 | 0.041199 | 0.036621 | 0.064087 | 0.041199 | -0.10529 | 0.086975 | 0.091553 | 0.018311 | 0.027466 | 0.004578 | -0.036621 | -0.091553 | 0.10986 | -0.036621 | -122.1268 | 0.13733 | 0.10529 | 0.14191 | -122.2092 | 0.032044 | -0.022888 | -122.1634 | 0.15564 | 0.086976 | 0.10986 | -122.1863 | 0.13275 | 0.050354 | 0.10986 | -122.2961 | 0.096131 | 0.073243 | 0.16022 | -122.2824
2853.1562 | 122.3511 | -0.10986 | 122.2458 | -0.22614 | 0.046128 | 0.061182 | 0.0023329 | 0.031037 | -0.004313 | 0.03086 | -0.21484 | 0.028546 | 0.039018 | 0.05266 | 0.0025271 | 0.023086 | -0.022888 | 0.018311 | -0.018311 | -0.009155 | 0.10071 | 0.009155 | -0.13733 | 0.022888 | 0.027466 | -0.086975 | 0.059509 | 0.041199 | -0.073242 | -0.10986 | 0.11902 | -0.027466 | -122.1451 | 0.12817 | 0.10071 | 0.12817 | -122.2687 | 0.036621 | 0 | -122.1863 | 0.13275 | 0.022888 | 0.022888 | -122.2046 | 0.21057 | 0.086975 | 0.091552 | -122.3831 | 0.16937 | 0.15106 | 0.13733 | -122.3557
2854.8594 | 122.3511 | -0.082397 | 122.2366 | -0.15747 | 0.045487 | 0.063959 | 0.0023329 | 0.032105 | -0.0017496 | 0.034064 | -0.16144 | 0.02876 | 0.033037 | 0.049029 | 0.0025271 | 0.025222 | 0.013733 | 0.050354 | 0.022888 | 0.022888 | 0.086975 | 0.022888 | -0.1236 | 0.064087 | 0.073242 | -0.050354 | 0.050354 | 0.022888 | -0.045776 | -0.091553 | 0.10528 | -0.041199 | -122.1497 | 0.13275 | 0.10528 | 0.14648 | -122.2229 | 0.036621 | -0.009156 | -122.1863 | 0.14648 | 0.032043 | 0.041199 | -122.2137 | 0.16937 | 0.09613 | 0.10528 | -122.3602 | 0.13275 | 0.10528 | 0.15564 | -122.3282
2856.625 | 122.3053 | -0.10529 | 122.2549 | -0.081177 | 0.046128 | 0.058405 | 0.0016919 | 0.033387 | -0.00025418 | 0.03321 | -0.069885 | 0.029615 | 0.037309 | 0.052874 | 0.0031681 | 0.026931 | 0.022888 | 0.045776 | 0.013733 | 0.013733 | 0.082397 | 0.036621 | -0.10986 | 0.054932 | 0.050354 | -0.059509 | 0.041199 | 0.045776 | -0.041199 | -0.10071 | 0.14191 | -0.004577 | -122.1725 | 0.15106 | 0.11902 | 0.1236 | -122.2321 | 0.064087 | 0.004578 | -122.2137 | 0.16022 | 0.045777 | 0.041199 | -122.2092 | 0.18768 | 0.12817 | 0.11902 | -122.3648 | 0.14649 | 0.15106 | 0.15564 | -122.3557
2858.375 | 122.3236 | -0.11444 | 122.2595 | -0.17273 | 0.045273 | 0.063745 | 0.0061781 | 0.032105 | -0.0092264 | 0.030219 | -0.13855 | 0.029187 | 0.036241 | 0.049456 | -0.0028135 | 0.026718 | 0.050354 | 0.14648 | 0.09613 | 0.07782 | 0.054932 | 0.059509 | -0.09613 | 0.10071 | 0.16937 | 0.027466 | 0.018311 | 0.018311 | -0.022888 | -0.086975 | 0.17395 | 0.018311 | -122.2046 | 0.26093 | 0.19226 | 0.17395 | -122.2092 | 0.091553 | 0.027466 | -122.2412 | 0.21515 | 0.14191 | 0.11444 | -122.2412 | 0.16937 | 0.16479 | 0.21057 | -122.3557 | 0.13275 | 0.13275 | 0.28381 | -122.3465
2860.0625 | 122.3511 | -0.091553 | 122.2412 | -0.12695 | 0.046768 | 0.060541 | 0.0051099 | 0.031892 | 0.0010276 | 0.035132 | -0.15381 | 0.028546 | 0.037309 | 0.053728 | 0.0010317 | 0.023941 | 0.032043 | 0.036621 | 0.018311 | 0.032043 | 0.082397 | 0.013733 | -0.12817 | 0.068665 | 0.091553 | -0.041199 | 0.050354 | 0.036621 | -0.022888 | -0.10071 | 0.10529 | -0.036621 | -122.1588 | 0.12817 | 0.1236 | 0.16022 | -122.2092 | 0.068665 | -0.009155 | -122.1909 | 0.16022 | 0.050354 | 0.059509 | -122.2046 | 0.17395 | 0.1236 | 0.10986 | -122.3694 | 0.14191 | 0.12817 | 0.18311 | -122.3419
2861.7656 | 122.4289 | -0.059509 | 122.2229 | -0.13458 | 0.044419 | 0.063959 | 0.0031873 | 0.031678 | -0.011363 | 0.031074 | -0.1004 | 0.027692 | 0.0356 | 0.051165 | -0.0030271 | 0.026504 | 0.07782 | 0.17853 | 0.1236 | 0.091553 | 0.054932 | 0.050354 | -0.09613 | 0.11444 | 0.17853 | 0.082397 | 0.013733 | -0.013733 | -0.013733 | -0.059509 | 0.10986 | -0.036621 | -122.168 | 0.23804 | 0.15106 | 0.18768 | -122.1451 | 0.045776 | 0 | -122.2092 | 0.17395 | 0.14191 | 0.14191 | -122.2366 | 0.11444 | 0.13733 | 0.1831 | -122.319 | 0.073242 | 0.045776 | 0.23804 | -122.2824
2863.5312 | 122.4426 | -0.045776 | 122.2092 | -0.0048827 | 0.04506 | 0.062036 | 0.0055371 | 0.03061 | -0.0068766 | 0.030646 | 0.052185 | 0.027265 | 0.036027 | 0.050951 | -0.0034543 | 0.024795 | 0.022888 | 0.045776 | 0.054932 | 0.018311 | 0.036621 | 0.045776 | -0.086975 | 0.073242 | 0.082397 | 0.018311 | 0.041199 | 0.004578 | -0.018311 | -0.082397 | 0.091552 | -0.041199 | -122.1725 | 0.091552 | 0.064087 | 0.10529 | -122.1863 | 0.027465 | -0.036621 | -122.168 | 0.11902 | 0.064087 | 0.10071 | -122.2046 | 0.082397 | 0.068664 | 0.10071 | -122.2961 | 0.086975 | 0.050354 | 0.12817 | -122.2916
2865.2969 | 122.438 | -0.054932 | 122.2 | 0.18585 | 0.045487 | 0.059686 | 0.0016919 | 0.032105 | -0.00025418 | 0.03086 | 0.082703 | 0.029828 | 0.034318 | 0.051378 | 0.0014591 | 0.025009 | 0.054932 | 0.045776 | 0.045776 | 0.036621 | 0.073242 | 0.054932 | -0.091553 | 0.12817 | 0.10529 | -0.009155 | 0.013733 | 0.013733 | -0.009155 | -0.064087 | 0.10986 | -0.036621 | -122.1268 | 0.10071 | 0.091553 | 0.12817 | -122.1451 | 0.045777 | -0.009155 | -122.1863 | 0.18311 | 0.045777 | 0.054932 | -122.1863 | 0.12817 | 0.10986 | 0.10071 | -122.2916 | 0.068665 | 0.068665 | 0.16022 | -122.2641
2867 | 122.3419 | -0.091553 | 122.2458 | -0.096436 | 0.046768 | 0.0599 | 0.00041005 | 0.029969 | 0.00060022 | 0.034064 | -0.13092 | 0.030896 | 0.034959 | 0.052233 | 0.0031681 | 0.024795 | 0.07782 | 0.054932 | 0.032043 | 0.022888 | 0.073242 | 0.022888 | -0.10529 | 0.082397 | 0.091553 | -0.041199 | 0.045776 | 0.045776 | -0.032043 | -0.091553 | 0.11444 | -0.013733 | -122.1725 | 0.14649 | 0.11444 | 0.12817 | -122.168 | 0.05951 | 0 | -122.2 | 0.17395 | 0.050354 | 0.050354 | -122.2 | 0.16479 | 0.16937 | 0.1236 | -122.3511 | 0.13733 | 0.13733 | 0.18311 | -122.3373
2868.75 | 122.4197 | -0.064087 | 122.2183 | -0.13458 | 0.043351 | 0.061182 | 0.0046827 | 0.029969 | -0.008372 | 0.031074 | -0.085144 | 0.028546 | 0.037523 | 0.051165 | -0.0045225 | 0.026077 | 0.091553 | 0.15564 | 0.13275 | 0.073242 | 0.036621 | 0.050354 | -0.091553 | 0.13733 | 0.1831 | 0.068665 | 0.009155 | 0.022888 | -0.004578 | -0.064087 | 0.11444 | -0.027466 | -122.1817 | 0.21973 | 0.13733 | 0.16479 | -122.1268 | 0.059509 | 0 | -122.2092 | 0.20142 | 0.13275 | 0.13275 | -122.1954 | 0.10071 | 0.15564 | 0.19684 | -122.3099 | 0.073242 | 0.086975 | 0.24719 | -122.2824
2870.4531 | 122.3236 | -0.10529 | 122.2275 | -0.18799 | 0.046555 | 0.060114 | 0.0044691 | 0.031892 | -0.0047404 | 0.030646 | -0.19958 | 0.027265 | 0.039445 | 0.052019 | -0.0030271 | 0.024368 | 0.068665 | 0.11444 | 0.10529 | 0.064087 | 0.054932 | 0.045776 | -0.086975 | 0.086975 | 0.14648 | 0.027466 | 0.022888 | 0.004578 | -0.036621 | -0.073242 | 0.15106 | 0.018311 | -122.1725 | 0.21973 | 0.16937 | 0.15106 | -122.1588 | 0.068665 | 0.032044 | -122.2046 | 0.19226 | 0.13275 | 0.10071 | -122.2229 | 0.16022 | 0.17395 | 0.21057 | -122.3145 | 0.12817 | 0.10986 | 0.25177 | -122.3007
2872.2188 | 122.3694 | -0.086975 | 122.2549 | -0.18799 | 0.043778 | 0.061609 | -0.00044435 | 0.031251 | -0.00068138 | 0.032355 | -0.23773 | 0.028974 | 0.036882 | 0.052447 | 0.0018863 | 0.024582 | 0.004578 | -0.009155 | -0.027466 | 0.004578 | 0.086975 | 0.009155 | -0.12817 | 0.036621 | 0.050354 | -0.073242 | 0.064087 | 0.027466 | -0.032043 | -0.10986 | 0.09613 | -0.041199 | -122.168 | 0.07782 | 0.091553 | 0.13275 | -122.2504 | 0.054932 | -0.022888 | -122.1909 | 0.1236 | 0.013733 | 0.036621 | -122.2275 | 0.17395 | 0.091553 | 0.059509 | -122.3831 | 0.15106 | 0.11444 | 0.13733 | -122.3648
2873.9219 | 122.319 | -0.11444 | 122.2412 | 0.040894 | 0.046555 | 0.061609 | 0.0046827 | 0.031892 | 0.0012412 | 0.034064 | -0.031738 | 0.030469 | 0.035814 | 0.053728 | 0.0023135 | 0.024795 | -0.018311 | -0.022888 | -0.036621 | -0.009155 | 0.068665 | 0.022888 | -0.1236 | 0.013733 | -0.013733 | -0.13733 | 0.059509 | 0.045776 | -0.045776 | -0.10071 | 0.13733 | -0.009155 | -122.1725 | 0.091553 | 0.10529 | 0.11444 | -122.2595 | 0.068665 | 0.013733 | -122.1817 | 0.12817 | -0.022888 | -0.036621 | -122.1954 | 0.18311 | 0.09613 | 0.07782 | -122.3648 | 0.17395 | 0.16022 | 0.10071 | -122.3419
2875.6719 | 122.3511 | -0.073242 | 122.2275 | -0.11932 | 0.049118 | 0.059045 | 0.0063917 | 0.031678 | -0.00068138 | 0.032996 | -0.11566 | 0.030042 | 0.039232 | 0.052447 | 0.00017731 | 0.025009 | 0.041199 | 0.041199 | 0.027466 | 0.022888 | 0.068665 | 0.018311 | -0.10071 | 0.086975 | 0.07782 | -0.054932 | 0.050354 | 0.027466 | -0.032043 | -0.091553 | 0.091553 | -0.027466 | -122.1588 | 0.11444 | 0.09613 | 0.1236 | -122.1863 | 0.041199 | -0.018311 | -122.1771 | 0.16022 | 0.01831 | 0.036621 | -122.2 | 0.14191 | 0.11444 | 0.10071 | -122.3282 | 0.1236 | 0.10071 | 0.15106 | -122.319
2877.3594 | 122.3557 | -0.091553 | 122.2092 | 0.079041 | 0.0457 | 0.057764 | 0.0014783 | 0.031465 | -0.0040994 | 0.03556 | 0.082703 | 0.030042 | 0.0356 | 0.052874 | 0.0020999 | 0.027572 | -0.032043 | -0.032043 | -0.036621 | -0.022888 | 0.091553 | 0.022888 | -0.1236 | 0.018311 | -0.009155 | -0.10986 | 0.050354 | 0.041199 | -0.045776 | -0.1236 | 0.11444 | -0.032043 | -122.1176 | 0.05951 | 0.068665 | 0.10071 | -122.2412 | 0.045777 | -0.032043 | -122.1588 | 0.10986 | -0.01831 | 0.013733 | -122.168 | 0.18311 | 0.05951 | 0.054932 | -122.3328 | 0.14191 | 0.13275 | 0.082398 | -122.3328
2879.1094 | 122.3877 | -0.073242 | 122.1909 | 0.094299 | 0.045487 | 0.059259 | 0.00062385 | 0.03296 | -0.0011088 | 0.033851 | 0.059815 | 0.029615 | 0.036882 | 0.051592 | 0.00017731 | 0.026291 | -0.022888 | -0.018311 | -0.036621 | -0.022888 | 0.09613 | 0.022888 | -0.10529 | 0.027466 | 0.009155 | -0.082397 | 0.041199 | 0.045776 | -0.045776 | -0.09613 | 0.09613 | -0.032044 | -122.0947 | 0.054931 | 0.050354 | 0.082398 | -122.2137 | 0.027466 | -0.022888 | -122.1497 | 0.10071 | -0.009155 | 0.013733 | -122.1451 | 0.16937 | 0.050354 | 0.036621 | -122.2961 | 0.11444 | 0.11902 | 0.082397 | -122.287
2880.875 | 122.3877 | -0.068665 | 122.2046 | 0.11719 | 0.043351 | 0.062036 | 0.0044691 | 0.02826 | -0.007731 | 0.032142 | 0.13611 | 0.027692 | 0.037736 | 0.052019 | -0.0015317 | 0.028213 | 0.045776 | 0.10071 | 0.068665 | 0.032043 | 0.027466 | 0.059509 | -0.07782 | 0.10529 | 0.10071 | 0.022888 | 0.018311 | 0 | 0.004578 | -0.064087 | 0.12817 | -0.009155 | -122.1771 | 0.16937 | 0.10071 | 0.10986 | -122.1588 | 0.073243 | 0.004578 | -122.1863 | 0.17395 | 0.091553 | 0.086975 | -122.2046 | 0.096131 | 0.11444 | 0.13733 | -122.2824 | 0.086976 | 0.068665 | 0.16937 | -122.2687
2882.5781 | 122.3145 | -0.09613 | 122.2504 | -0.012512 | 0.047623 | 0.058618 | 0.0027601 | 0.032533 | 0.00017302 | 0.032783 | 0.0064086 | 0.031751 | 0.036241 | 0.05266 | 0.0025271 | 0.025222 | 0.004578 | -0.032043 | -0.027466 | -0.032043 | 0.068665 | 0.013733 | -0.13733 | 0.009155 | 0 | -0.1236 | 0.064087 | 0.036621 | -0.041199 | -0.10071 | 0.10986 | -0.041199 | -122.1817 | 0.064087 | 0.064087 | 0.10529 | -122.2458 | 0.054931 | -0.004578 | -122.1863 | 0.10528 | -0.027466 | -0.022888 | -122.2137 | 0.16479 | 0.10071 | 0.068664 | -122.3877 | 0.16022 | 0.13275 | 0.09613 | -122.3511
2884.3281 | 122.3831 | -0.07782 | 122.2 | 0.094299 | 0.040573 | 0.062677 | 0.00019645 | 0.029542 | -0.006022 | 0.031501 | 0.12085 | 0.028333 | 0.036241 | 0.050951 | -0.0019589 | 0.028213 | 0.045776 | 0.07782 | 0.07782 | 0.027466 | 0.054932 | 0.032043 | -0.07782 | 0.10071 | 0.091553 | 0.004578 | 0.027466 | 0.018311 | -0.013733 | -0.073242 | 0.10986 | 0 | -122.1451 | 0.15564 | 0.10529 | 0.10529 | -122.1542 | 0.064087 | 0.004578 | -122.1725 | 0.17853 | 0.082398 | 0.07782 | -122.1817 | 0.13275 | 0.1236 | 0.15564 | -122.2778 | 0.10529 | 0.096131 | 0.16937 | -122.2733
2886.0781 | 122.4243 | -0.045776 | 122.2275 | 0.079041 | 0.045914 | 0.061182 | -1.7146e-05 | 0.032319 | -0.00089518 | 0.029792 | 0.12848 | 0.029401 | 0.037523 | 0.053728 | 0.0018863 | 0.025222 | 0 | -0.004578 | -0.027466 | -0.018311 | 0.086975 | 0.041199 | -0.11902 | 0.07782 | 0.013733 | -0.059509 | 0.036621 | 0.018311 | -0.027466 | -0.10529 | 0.086975 | -0.073243 | -122.1405 | 0.041198 | 0.027465 | 0.10071 | -122.2275 | 0.01831 | -0.05951 | -122.1909 | 0.1236 | -0.013733 | 0.045777 | -122.2092 | 0.13275 | 0.045776 | 0.01831 | -122.3465 | 0.082397 | 0.064087 | 0.059509 | -122.3328
2887.8438 | 122.3373 | -0.082397 | 122.2595 | -0.18799 | 0.04506 | 0.063532 | 0.0040417 | 0.029969 | -0.006022 | 0.030219 | -0.13855 | 0.027478 | 0.037309 | 0.049456 | -0.0013181 | 0.024368 | 0.073242 | 0.11902 | 0.11444 | 0.07782 | 0.050354 | 0.045776 | -0.082397 | 0.10529 | 0.15564 | 0.041199 | 0.013733 | -0.004578 | 0 | -0.07782 | 0.12817 | 0 | -122.2092 | 0.20142 | 0.16022 | 0.16022 | -122.1863 | 0.082397 | 0.004577 | -122.2458 | 0.18768 | 0.1236 | 0.11902 | -122.2641 | 0.13275 | 0.15564 | 0.19684 | -122.3419 | 0.09613 | 0.077819 | 0.23804 | -122.3373
2889.5312 | 122.3282 | -0.10986 | 122.2412 | -0.17273 | 0.047196 | 0.060541 | 0.0051099 | 0.031251 | -0.0053812 | 0.030646 | -0.13855 | 0.028119 | 0.034959 | 0.051165 | 0.00017731 | 0.023941 | 0.073242 | 0.11902 | 0.10986 | 0.073242 | 0.050354 | 0.032043 | -0.091553 | 0.10071 | 0.16022 | 0.018311 | 0.022888 | 0.013733 | -0.032043 | -0.082397 | 0.14191 | 0.01831 | -122.1909 | 0.22888 | 0.18311 | 0.16479 | -122.168 | 0.07782 | 0.027466 | -122.2183 | 0.21057 | 0.12817 | 0.10071 | -122.2275 | 0.16022 | 0.18311 | 0.21973 | -122.3328 | 0.13275 | 0.1236 | 0.27008 | -122.3236
2891.2812 | 122.4518 | -0.059509 | 122.2092 | 0.14008 | 0.047623 | 0.060754 | 0.0012647 | 0.03061 | -0.0051676 | 0.03086 | 0.067444 | 0.029187 | 0.036455 | 0.051806 | 0.0016727 | 0.025009 | 0.11902 | 0.050354 | 0.07782 | 0.059509 | 0.059509 | 0.045776 | -0.091553 | 0.14191 | 0.11444 | 0.013733 | 0 | -0.004578 | 0 | -0.073242 | 0.10528 | -0.032044 | -122.1497 | 0.10986 | 0.11902 | 0.15106 | -122.0901 | 0.059509 | -0.013733 | -122.2092 | 0.20142 | 0.073242 | 0.086975 | -122.2137 | 0.11902 | 0.17853 | 0.13733 | -122.3007 | 0.059509 | 0.054931 | 0.17395 | -122.2824
2893.0469 | 122.438 | -0.068665 | 122.2137 | -0.12695 | 0.043991 | 0.061395 | 0.0061781 | 0.031037 | -0.0079446 | 0.030006 | -0.085144 | 0.029187 | 0.039445 | 0.052874 | -0.0038815 | 0.023941 | 0.11902 | 0.14191 | 0.11444 | 0.068665 | 0.041199 | 0.059509 | -0.082397 | 0.16937 | 0.19684 | 0.064087 | 0.013733 | 0.018311 | -0.013733 | -0.064087 | 0.12817 | -0.013732 | -122.1725 | 0.21057 | 0.13733 | 0.15106 | -122.0947 | 0.054932 | 0.004578 | -122.2 | 0.23804 | 0.13275 | 0.12817 | -122.1954 | 0.10986 | 0.18768 | 0.18311 | -122.2961 | 0.082398 | 0.086976 | 0.2655 | -122.2778
2894.7344 | 122.3557 | -0.082397 | 122.2275 | 0.10193 | 0.04506 | 0.0599 | 0.0021191 | 0.031465 | 0.00081382 | 0.032142 | 0.052185 | 0.02876 | 0.036455 | 0.054156 | 0.0031681 | 0.024368 | 0.013733 | -0.036621 | -0.059509 | -0.027466 | 0.09613 | 0.004578 | -0.13275 | 0.036621 | -0.022888 | -0.10071 | 0.054932 | 0.032043 | -0.068665 | -0.11444 | 0.086975 | -0.050354 | -122.1313 | 0.045776 | 0.054931 | 0.10529 | -122.2137 | 0.013732 | -0.032044 | -122.1725 | 0.11902 | -0.018311 | 0.013733 | -122.1954 | 0.17853 | 0.09613 | 0.022888 | -122.3602 | 0.13733 | 0.11444 | 0.059509 | -122.3419
2896.4844 | 122.3282 | -0.10071 | 122.2549 | -0.0048827 | 0.049332 | 0.059259 | 0.0051099 | 0.029115 | 0.0016684 | 0.033637 | 0.0064086 | 0.030469 | 0.039018 | 0.050738 | 0.0027407 | 0.025222 | 0.009155 | -0.013733 | -0.022888 | -0.004578 | 0.07782 | 0.032043 | -0.13275 | 0.009155 | -0.004578 | -0.12817 | 0.045776 | 0.041199 | -0.050354 | -0.1236 | 0.13275 | -0.032043 | -122.1771 | 0.086975 | 0.09613 | 0.12817 | -122.2458 | 0.050354 | -0.022888 | -122.2092 | 0.10986 | -0.027466 | -0.004578 | -122.2137 | 0.17853 | 0.10986 | 0.07782 | -122.3877 | 0.14648 | 0.14191 | 0.09613 | -122.3785
2898.2344 | 122.4289 | -0.032043 | 122.1725 | 0.14008 | 0.045914 | 0.059473 | 0.0021191 | 0.031037 | -0.0017496 | 0.033851 | 0.13611 | 0.029187 | 0.035814 | 0.052233 | 0.0012455 | 0.026291 | 0.009155 | 0.036621 | 0.018311 | 0.009155 | 0.064087 | 0.045776 | -0.11444 | 0.10986 | 0.07782 | -0.004578 | 0.018311 | 0.032043 | -0.009155 | -0.07782 | 0.077819 | -0.082398 | -122.1085 | 0.068664 | 0.041198 | 0.1236 | -122.1634 | 0.022888 | -0.045777 | -122.1542 | 0.14191 | 0.027465 | 0.073242 | -122.1405 | 0.09613 | 0.041198 | 0.050354 | -122.287 | 0.050354 | 0.064086 | 0.10986 | -122.2504
2899.9219 | 122.3557 | -0.086975 | 122.2504 | -0.19562 | 0.043564 | 0.062677 | 0.0044691 | 0.03296 | -0.0085856 | 0.029792 | -0.12329 | 0.028333 | 0.034532 | 0.053087 | -0.0028135 | 0.02565 | 0.073242 | 0.14191 | 0.11444 | 0.064087 | 0.041199 | 0.045776 | -0.082397 | 0.11902 | 0.16479 | 0.050354 | 0.018311 | 0.009155 | -0.004578 | -0.086975 | 0.13275 | 0.004578 | -122.2092 | 0.22888 | 0.15106 | 0.14648 | -122.1771 | 0.082397 | 0 | -122.2321 | 0.20599 | 0.13733 | 0.13733 | -122.2412 | 0.12817 | 0.16022 | 0.20142 | -122.3328 | 0.10529 | 0.09613 | 0.25177 | -122.3373
2901.6719 | 122.3648 | -0.082397 | 122.2458 | -0.18036 | 0.050614 | 0.060968 | 0.0036145 | 0.03296 | -4.058e-05 | 0.030433 | -0.22247 | 0.030042 | 0.038164 | 0.052019 | 0.0010317 | 0.023513 | 0.013733 | 0 | -0.009155 | 0.009155 | 0.073242 | 0.004578 | -0.12817 | 0.041199 | 0.064087 | -0.064087 | 0.086975 | 0.054932 | -0.050354 | -0.11902 | 0.086975 | -0.045777 | -122.1725 | 0.082397 | 0.091552 | 0.13733 | -122.2321 | 0.032043 | -0.036622 | -122.1588 | 0.1236 | 0.01831 | 0.054932 | -122.1909 | 0.15564 | 0.09613 | 0.073242 | -122.374 | 0.16937 | 0.13733 | 0.14648 | -122.3648
2903.375 | 122.3877 | -0.059509 | 122.2458 | 0.10956 | 0.044632 | 0.063318 | -0.00023075 | 0.032533 | 0.0010276 | 0.033637 | 0.044556 | 0.033032 | 0.035173 | 0.053301 | 0.0027407 | 0.025222 | 0 | -0.027466 | -0.022888 | -0.018311 | 0.07782 | 0.018311 | -0.10986 | 0.036621 | 0.004578 | -0.10071 | 0.054932 | 0.041199 | -0.050354 | -0.10986 | 0.07782 | -0.050354 | -122.168 | 0.032043 | 0.041198 | 0.091552 | -122.2458 | 0.009155 | -0.050354 | -122.1909 | 0.09613 | -0.041199 | 0.009155 | -122.2046 | 0.13733 | 0.059509 | 0.036621 | -122.3557 | 0.11444 | 0.10071 | 0.064087 | -122.3557
2905.1406 | 122.319 | -0.091553 | 122.2321 | -0.096436 | 0.04805 | 0.061182 | 0.0046827 | 0.031892 | 0.0023092 | 0.033851 | -0.10803 | 0.029187 | 0.0356 | 0.050951 | 0.0035953 | 0.025009 | 0.068665 | 0.054932 | 0.036621 | 0.036621 | 0.064087 | 0.027466 | -0.11444 | 0.068665 | 0.07782 | -0.045776 | 0.036621 | 0.009155 | -0.045776 | -0.091553 | 0.11902 | -0.022888 | -122.168 | 0.14649 | 0.12817 | 0.15106 | -122.1634 | 0.045777 | 0 | -122.1954 | 0.16022 | 0.045777 | 0.045777 | -122.2229 | 0.15564 | 0.16022 | 0.12817 | -122.3465 | 0.12817 | 0.10071 | 0.16937 | -122.3236
2906.9062 | 122.3145 | -0.10986 | 122.2641 | -0.10406 | 0.0457 | 0.060754 | 0.0040417 | 0.031251 | -0.00025418 | 0.03321 | -0.11566 | 0.033032 | 0.036455 | 0.053301 | 0.0023135 | 0.024582 | 0.054932 | 0.054932 | 0.018311 | 0.022888 | 0.050354 | 0.022888 | -0.12817 | 0.082397 | 0.07782 | -0.059509 | 0.045776 | 0.036621 | -0.045776 | -0.10071 | 0.13275 | -0.018311 | -122.2137 | 0.16479 | 0.13275 | 0.15106 | -122.2092 | 0.064087 | 0.009155 | -122.2183 | 0.19226 | 0.050354 | 0.041199 | -122.2275 | 0.16022 | 0.16479 | 0.12817 | -122.3923 | 0.15564 | 0.14648 | 0.18768 | -122.3648
2908.6094 | 122.2961 | -0.10529 | 122.2641 | -0.22614 | 0.046555 | 0.061182 | 0.0076733 | 0.031678 | -0.0092264 | 0.031714 | -0.18433 | 0.027692 | 0.037736 | 0.052874 | -0.0036679 | 0.02565 | 0.027466 | 0.086975 | 0.07782 | 0.054932 | 0.045776 | 0.027466 | -0.11444 | 0.036621 | 0.09613 | -0.050354 | 0.045776 | 0.027466 | -0.045776 | -0.082397 | 0.13275 | -0.009155 | -122.2183 | 0.19226 | 0.16022 | 0.16937 | -122.2366 | 0.05951 | 0.022889 | -122.2183 | 0.14191 | 0.054932 | 0.032043 | -122.2366 | 0.15106 | 0.13275 | 0.18311 | -122.3785 | 0.15106 | 0.13275 | 0.20142 | -122.3465
2910.3594 | 122.3007 | -0.11444 | 122.2504 | -0.020142 | 0.047623 | 0.060114 | 0.0019055 | 0.033814 | -0.0011088 | 0.033423 | 0.021668 | 0.030683 | 0.037309 | 0.053301 | 0.0023135 | 0.023727 | 0.009155 | -0.018311 | -0.027466 | -0.013733 | 0.07782 | 0.013733 | -0.10986 | 0.004578 | 0.013733 | -0.11444 | 0.064087 | 0.045776 | -0.050354 | -0.10986 | 0.12817 | 0.004578 | -122.1725 | 0.09613 | 0.10071 | 0.09613 | -122.2412 | 0.064087 | 0.004578 | -122.1863 | 0.11902 | 0 | -0.004578 | -122.2046 | 0.19226 | 0.1236 | 0.086975 | -122.3602 | 0.17853 | 0.16022 | 0.12817 | -122.3602
2912.125 | 122.3419 | -0.09613 | 122.2733 | 0.056152 | 0.047623 | 0.060114 | 0.0014783 | 0.029115 | -0.00089518 | 0.032355 | 0.067444 | 0.031323 | 0.038164 | 0.053942 | 0.00081811 | 0.026077 | -0.013733 | -0.041199 | -0.036621 | -0.022888 | 0.086975 | 0.027466 | -0.1236 | 0.022888 | -0.032043 | -0.11902 | 0.054932 | 0.036621 | -0.050354 | -0.10986 | 0.1236 | -0.027466 | -122.1863 | 0.054931 | 0.073242 | 0.10071 | -122.287 | 0.045776 | -0.013733 | -122.2183 | 0.11902 | -0.022889 | -0.009156 | -122.2366 | 0.1831 | 0.082397 | 0.059509 | -122.3969 | 0.15106 | 0.13275 | 0.064087 | -122.3831
2913.8281 | 122.3511 | -0.10071 | 122.2641 | -0.24139 | 0.044419 | 0.06225 | 0.0042555 | 0.034028 | -0.0038858 | 0.031287 | -0.19958 | 0.029615 | 0.037736 | 0.054156 | -0.00067729 | 0.024795 | -0.027466 | -0.013733 | -0.027466 | -0.022888 | 0.07782 | 0.022888 | -0.13275 | 0.004578 | 0.022888 | -0.082397 | 0.054932 | 0.050354 | -0.036621 | -0.11902 | 0.1236 | -0.032043 | -122.1863 | 0.086975 | 0.07782 | 0.10986 | -122.2916 | 0.064087 | -0.018311 | -122.2092 | 0.10529 | 0.018311 | 0.036622 | -122.2137 | 0.17853 | 0.073242 | 0.073242 | -122.3969 | 0.15564 | 0.15106 | 0.1236 | -122.3831
2915.5781 | 122.4701 | -0.068665 | 122.2229 | -0.088806 | 0.042496 | 0.06225 | 0.0036145 | 0.032105 | -0.00944 | 0.030433 | -0.046997 | 0.025769 | 0.034959 | 0.049883 | -0.0030271 | 0.027786 | 0.059509 | 0.10071 | 0.10071 | 0.064087 | 0.054932 | 0.059509 | -0.10986 | 0.14648 | 0.17395 | 0.064087 | 0.013733 | 0.009155 | -0.004578 | -0.068665 | 0.12817 | -0.041198 | -122.168 | 0.16937 | 0.13275 | 0.17395 | -122.1634 | 0.064087 | 0 | -122.2092 | 0.21515 | 0.13275 | 0.13275 | -122.2137 | 0.1236 | 0.12817 | 0.16937 | -122.3328 | 0.082398 | 0.07782 | 0.24261 | -122.2916
2917.3281 | 122.3923 | -0.064087 | 122.2366 | 0.10956 | 0.043991 | 0.062677 | -0.00065795 | 0.03061 | -0.0062356 | 0.030006 | 0.12085 | 0.029187 | 0.034105 | 0.05266 | 0.0025271 | 0.026077 | 0.091553 | 0.10529 | 0.10071 | 0.064087 | 0.045776 | 0.064087 | -0.082397 | 0.13733 | 0.10071 | 0.032043 | 0.004578 | 0.004578 | -0.018311 | -0.07782 | 0.12817 | -0.01831 | -122.1909 | 0.16937 | 0.12817 | 0.14648 | -122.1451 | 0.045776 | -0.013733 | -122.2321 | 0.20142 | 0.09613 | 0.10986 | -122.2321 | 0.10986 | 0.15564 | 0.1648 | -122.319 | 0.068665 | 0.068665 | 0.1648 | -122.3145
2919.0938 | 122.4014 | -0.07782 | 122.2321 | 0.056152 | 0.04271 | 0.060968 | 0.0023329 | 0.031037 | -0.0062356 | 0.028083 | 0.10559 | 0.026624 | 0.036027 | 0.051165 | -0.0011045 | 0.02565 | 0.050354 | 0.073242 | 0.082397 | 0.022888 | 0.050354 | 0.068665 | -0.07782 | 0.082397 | 0.07782 | 0 | 0.018311 | 0.036621 | -0.022888 | -0.07782 | 0.14649 | 0 | -122.1817 | 0.15106 | 0.10071 | 0.10071 | -122.1817 | 0.054932 | 0 | -122.2137 | 0.16022 | 0.07782 | 0.07782 | -122.1954 | 0.12817 | 0.12817 | 0.16022 | -122.3099 | 0.096131 | 0.11444 | 0.15564 | -122.3099
2920.7969 | 122.3648 | -0.09613 | 122.2137 | -0.1651 | 0.048477 | 0.060327 | 0.0048963 | 0.032319 | 0.00017302 | 0.031714 | -0.25299 | 0.030683 | 0.038164 | 0.053301 | 0.0016727 | 0.022873 | 0.022888 | -0.013733 | -0.004578 | -0.004578 | 0.07782 | -0.004578 | -0.12817 | 0.036621 | 0.045776 | -0.064087 | 0.054932 | 0.041199 | -0.036621 | -0.10071 | 0.091552 | -0.032044 | -122.1359 | 0.082397 | 0.091552 | 0.1236 | -122.1909 | 0.059509 | -0.004578 | -122.1588 | 0.13275 | 0.032043 | 0.036621 | -122.1725 | 0.17395 | 0.11902 | 0.091552 | -122.3419 | 0.15106 | 0.13733 | 0.14191 | -122.3145
2922.5625 | 122.319 | -0.073242 | 122.2824 | -0.11169 | 0.047196 | 0.0599 | 0.0019055 | 0.029756 | 0.0012412 | 0.033637 | -0.11566 | 0.030469 | 0.035387 | 0.051806 | 0.0027407 | 0.023086 | 0.082397 | 0.050354 | 0.022888 | 0.032043 | 0.064087 | 0.009155 | -0.11444 | 0.068665 | 0.064087 | -0.073242 | 0.032043 | 0.032043 | -0.041199 | -0.086975 | 0.082397 | -0.041199 | -122.2183 | 0.1236 | 0.10529 | 0.14648 | -122.2 | 0.032043 | -0.013733 | -122.2504 | 0.14191 | 0 | 0.013733 | -122.2504 | 0.13733 | 0.15564 | 0.09613 | -122.3969 | 0.10529 | 0.10529 | 0.13733 | -122.3694
2924.2812 | 122.3557 | -0.082397 | 122.2275 | -0.11932 | 0.047196 | 0.062677 | 0.0025465 | 0.029756 | -0.00089518 | 0.032142 | -0.14618 | 0.029187 | 0.035387 | 0.053087 | 0.0020999 | 0.026504 | 0.045776 | 0.032043 | 0.013733 | 0.022888 | 0.07782 | 0.018311 | -0.12817 | 0.064087 | 0.07782 | -0.036621 | 0.045776 | 0.059509 | -0.036621 | -0.082397 | 0.10071 | -0.045777 | -122.1497 | 0.11444 | 0.10528 | 0.15106 | -122.1817 | 0.045776 | 0 | -122.1817 | 0.14648 | 0.045776 | 0.045776 | -122.168 | 0.16022 | 0.12817 | 0.09613 | -122.3557 | 0.12817 | 0.14191 | 0.16022 | -122.3099
2926.0312 | 122.4289 | -0.045776 | 122.2092 | -0.13458 | 0.042069 | 0.062891 | 0.0046827 | 0.032319 | -0.0087992 | 0.030646 | -0.10803 | 0.030042 | 0.035814 | 0.050524 | -0.0028135 | 0.027786 | 0.10529 | 0.15106 | 0.14648 | 0.086975 | 0.050354 | 0.050354 | -0.09613 | 0.1236 | 0.17395 | 0.064087 | 0.018311 | 0.018311 | -0.013733 | -0.064087 | 0.09613 | -0.050354 | -122.1588 | 0.19684 | 0.13275 | 0.1831 | -122.1039 | 0.032043 | -0.018311 | -122.1909 | 0.16937 | 0.10986 | 0.12817 | -122.1909 | 0.09613 | 0.15106 | 0.19226 | -122.3053 | 0.064087 | 0.064087 | 0.21973 | -122.2733
2927.7812 | 122.3007 | -0.10071 | 122.2641 | -0.073547 | 0.047196 | 0.060541 | 0.0027601 | 0.030824 | 0.0016684 | 0.033637 | -0.077515 | 0.03111 | 0.036668 | 0.054156 | 0.0029543 | 0.0233 | 0.073242 | 0.036621 | 0.027466 | 0.018311 | 0.073242 | 0.022888 | -0.10529 | 0.064087 | 0.036621 | -0.091553 | 0.073242 | 0.018311 | -0.045776 | -0.10071 | 0.1236 | -0.004578 | -122.1909 | 0.13733 | 0.11902 | 0.1236 | -122.1909 | 0.054932 | 0 | -122.1909 | 0.1648 | 0.009155 | 0.009155 | -122.2458 | 0.17395 | 0.17395 | 0.12817 | -122.3694 | 0.17395 | 0.11902 | 0.13733 | -122.3648
2929.5469 | 122.3328 | -0.11444 | 122.2458 | -0.18036 | 0.045487 | 0.061823 | 0.0057507 | 0.031892 | -0.0062356 | 0.031287 | -0.18433 | 0.030683 | 0.036668 | 0.052233 | -0.0032407 | 0.025863 | -0.004578 | 0 | 0.004578 | -0.004578 | 0.07782 | 0.013733 | -0.13733 | 0.018311 | 0.036621 | -0.082397 | 0.045776 | 0.050354 | -0.050354 | -0.09613 | 0.12817 | -0.022888 | -122.168 | 0.11444 | 0.10986 | 0.13275 | -122.2504 | 0.064087 | 0.018311 | -122.2 | 0.13275 | 0.032044 | 0.013733 | -122.1954 | 0.19226 | 0.10986 | 0.11902 | -122.3831 | 0.16022 | 0.16479 | 0.15106 | -122.3419
2931.2969 | 122.3145 | -0.068665 | 122.2595 | -0.10406 | 0.049332 | 0.059045 | 0.0010511 | 0.03061 | 0.00081382 | 0.034064 | -0.11566 | 0.028546 | 0.037523 | 0.054583 | 0.0023135 | 0.024154 | 0.050354 | 0.054932 | 0.032043 | 0.013733 | 0.073242 | 0.032043 | -0.11902 | 0.07782 | 0.082397 | -0.045776 | 0.027466 | 0.032043 | -0.041199 | -0.07782 | 0.10071 | -0.050354 | -122.1863 | 0.1236 | 0.082398 | 0.13275 | -122.2092 | 0.027466 | -0.009155 | -122.2321 | 0.14649 | 0.022889 | 0.032044 | -122.2275 | 0.14191 | 0.11902 | 0.10071 | -122.3785 | 0.096131 | 0.10071 | 0.15106 | -122.3373
2933.0469 | 122.3419 | -0.086975 | 122.2412 | 0.08667 | 0.047409 | 0.061182 | -0.00087155 | 0.034028 | -0.0030314 | 0.032996 | 0.090332 | 0.030042 | 0.034532 | 0.051378 | -0.00089089 | 0.026504 | -0.018311 | -0.050354 | -0.041199 | -0.013733 | 0.068665 | 0.027466 | -0.11444 | 0.032043 | -0.027466 | -0.10529 | 0.050354 | 0.041199 | -0.027466 | -0.10529 | 0.11444 | -0.027466 | -122.1725 | 0.036621 | 0.073242 | 0.10071 | -122.2595 | 0.059509 | -0.018311 | -122.1909 | 0.11902 | -0.018311 | 0 | -122.2 | 0.15564 | 0.068664 | 0.045776 | -122.3557 | 0.13733 | 0.12817 | 0.059509 | -122.3465
2934.7344 | 122.4518 | -0.032043 | 122.2183 | 0.063782 | 0.04271 | 0.061395 | -0.0010851 | 0.031251 | -0.0051676 | 0.034064 | 0.15137 | 0.029615 | 0.032396 | 0.050097 | -3.629e-05 | 0.027999 | 0.091553 | 0.10529 | 0.073242 | 0.064087 | 0.032043 | 0.045776 | -0.07782 | 0.11902 | 0.12817 | 0.027466 | 0.004578 | 0.018311 | -0.013733 | -0.064087 | 0.077819 | -0.045777 | -122.1863 | 0.13733 | 0.09613 | 0.14191 | -122.1268 | 0.01831 | -0.032044 | -122.2137 | 0.15106 | 0.059509 | 0.091553 | -122.2 | 0.064086 | 0.1236 | 0.10529 | -122.2961 | 0.036621 | 0.050354 | 0.16022 | -122.2824
2936.4844 | 122.4243 | -0.059509 | 122.2366 | 0.08667 | 0.047196 | 0.061395 | 0.0038281 | 0.032746 | -0.0013224 | 0.032142 | 0.082703 | 0.028546 | 0.037523 | 0.050738 | -3.629e-05 | 0.02565 | -0.013733 | -0.022888 | -0.027466 | -0.013733 | 0.07782 | 0.018311 | -0.11444 | 0.045776 | 0.004578 | -0.082397 | 0.045776 | 0.045776 | -0.036621 | -0.10529 | 0.07782 | -0.054932 | -122.1588 | 0.036621 | 0.045776 | 0.10071 | -122.2504 | 0.022888 | -0.045777 | -122.1909 | 0.10528 | -0.022888 | 0.022889 | -122.1909 | 0.13733 | 0.045776 | 0.032043 | -122.3511 | 0.10528 | 0.10528 | 0.064087 | -122.3419
2938.2344 | 122.4564 | -0.064087 | 122.2046 | -0.19562 | 0.042923 | 0.064386 | 0.0057507 | 0.031678 | -0.0092264 | 0.031287 | -0.031738 | 0.027906 | 0.039018 | 0.050097 | -0.0040951 | 0.025222 | 0.054932 | 0.1236 | 0.10986 | 0.068665 | 0.041199 | 0.045776 | -0.082397 | 0.13733 | 0.15564 | 0.073242 | 0.004578 | -0.009155 | -0.009155 | -0.064087 | 0.10986 | -0.01831 | -122.1634 | 0.18768 | 0.13275 | 0.15106 | -122.1497 | 0.054932 | 0 | -122.2 | 0.20142 | 0.13733 | 0.13733 | -122.2137 | 0.10529 | 0.11902 | 0.17395 | -122.287 | 0.068665 | 0.054932 | 0.21973 | -122.2687
2939.9375 | 122.3785 | -0.073242 | 122.2412 | -0.18036 | 0.048691 | 0.059686 | 0.0029737 | 0.032319 | -0.00068138 | 0.030219 | -0.1767 | 0.027906 | 0.0356 | 0.051378 | 0.0012455 | 0.024154 | 0.027466 | 0.004578 | 0.013733 | 0.022888 | 0.073242 | 0.013733 | -0.11444 | 0.041199 | 0.064087 | -0.054932 | 0.050354 | 0.027466 | -0.059509 | -0.091553 | 0.086975 | -0.041199 | -122.168 | 0.07782 | 0.09613 | 0.13733 | -122.2137 | 0.013733 | -0.018311 | -122.1909 | 0.11444 | 0.01831 | 0.036621 | -122.2137 | 0.14648 | 0.10071 | 0.086975 | -122.3557 | 0.1236 | 0.10071 | 0.13733 | -122.3328
2941.7031 | 122.3099 | -0.082397 | 122.2504 | -0.081177 | 0.049118 | 0.057977 | 0.0036145 | 0.029542 | 0.00060022 | 0.032569 | -0.077515 | 0.029828 | 0.03795 | 0.054796 | 0.0016727 | 0.023941 | 0.059509 | 0.032043 | 0.018311 | 0.032043 | 0.064087 | 0.022888 | -0.11902 | 0.059509 | 0.045776 | -0.082397 | 0.032043 | 0.054932 | -0.050354 | -0.09613 | 0.10528 | -0.036622 | -122.1863 | 0.11444 | 0.11444 | 0.15106 | -122.1909 | 0.032043 | -0.013733 | -122.2183 | 0.14191 | 0 | 0.013733 | -122.1954 | 0.14648 | 0.14191 | 0.10071 | -122.3694 | 0.11444 | 0.13733 | 0.12817 | -122.3465
2943.4062 | 122.4518 | -0.045776 | 122.2137 | -0.04303 | 0.044846 | 0.063318 | 0.0034009 | 0.033387 | -0.011576 | 0.031074 | -0.039368 | 0.027051 | 0.034105 | 0.049242 | -0.00089089 | 0.025436 | 0.064087 | 0.13275 | 0.10529 | 0.054932 | 0.054932 | 0.054932 | -0.082397 | 0.14191 | 0.15564 | 0.068665 | 0.009155 | 0.009155 | -0.036621 | -0.064087 | 0.10071 | -0.036621 | -122.1588 | 0.17853 | 0.10071 | 0.13733 | -122.1497 | 0.009155 | -0.018311 | -122.2046 | 0.18768 | 0.11444 | 0.13275 | -122.2046 | 0.10071 | 0.10986 | 0.15106 | -122.2961 | 0.054931 | 0.054931 | 0.20142 | -122.2778
2945.1562 | 122.438 | -0.050354 | 122.1954 | 0.08667 | 0.045273 | 0.062677 | 0.00041005 | 0.032105 | -0.0017496 | 0.034278 | 0.14374 | 0.031751 | 0.036027 | 0.053301 | 0.0012455 | 0.026291 | 0.013733 | -0.018311 | -0.013733 | -0.009155 | 0.07782 | 0.041199 | -0.10529 | 0.073242 | 0.032043 | -0.050354 | 0.045776 | 0.032043 | -0.022888 | -0.09613 | 0.091553 | -0.054932 | -122.1176 | 0.032043 | 0.041199 | 0.096131 | -122.1817 | 0.027466 | -0.045776 | -122.1497 | 0.1236 | 0 | 0.045776 | -122.1634 | 0.12817 | 0.064087 | 0.036621 | -122.3007 | 0.09613 | 0.082397 | 0.082397 | -122.2916
2946.9219 | 122.3602 | -0.10071 | 122.2183 | 0.094299 | 0.04506 | 0.061823 | 0.0010511 | 0.031037 | -0.00025418 | 0.029578 | 0.075073 | 0.030042 | 0.038805 | 0.052874 | 0.0010317 | 0.025436 | -0.009155 | -0.045776 | -0.036621 | 0.004578 | 0.10071 | 0.027466 | -0.11902 | 0.027466 | -0.022888 | -0.10071 | 0.064087 | 0.041199 | -0.054932 | -0.10986 | 0.12817 | -0.018311 | -122.1176 | 0.054932 | 0.10529 | 0.1236 | -122.2275 | 0.045776 | -0.009155 | -122.1542 | 0.12817 | 0 | 0.009155 | -122.1771 | 0.20142 | 0.091553 | 0.064087 | -122.3373 | 0.1648 | 0.14191 | 0.07782 | -122.3282
2948.6719 | 122.3053 | -0.091553 | 122.2595 | -0.088806 | 0.048905 | 0.061395 | 0.0051099 | 0.031251 | -0.00046778 | 0.032142 | -0.077515 | 0.032392 | 0.036241 | 0.051592 | 0.0027407 | 0.024582 | 0.064087 | 0.050354 | 0.022888 | 0.022888 | 0.068665 | 0.018311 | -0.11444 | 0.073242 | 0.050354 | -0.064087 | 0.036621 | 0.050354 | -0.054932 | -0.10071 | 0.10986 | -0.022888 | -122.1909 | 0.14191 | 0.11444 | 0.13733 | -122.1954 | 0.036621 | -0.009155 | -122.2229 | 0.16479 | 0.027466 | 0.036621 | -122.2092 | 0.16022 | 0.15564 | 0.11444 | -122.374 | 0.12817 | 0.14191 | 0.14191 | -122.3602
2950.3594 | 122.4152 | -0.073242 | 122.2229 | 0.15533 | 0.045914 | 0.062036 | 0.00041005 | 0.032746 | -0.0081582 | 0.034705 | 0.17426 | 0.027478 | 0.034746 | 0.05031 | 0.00081811 | 0.027572 | 0.054932 | 0.1236 | 0.091553 | 0.068665 | 0.022888 | 0.059509 | -0.073242 | 0.14648 | 0.13275 | 0.054932 | 0.004578 | -0.009155 | -0.018311 | -0.064087 | 0.13275 | 0 | -122.2 | 0.19684 | 0.14191 | 0.14191 | -122.168 | 0.054931 | 0.009155 | -122.2183 | 0.21973 | 0.12817 | 0.11902 | -122.2321 | 0.09613 | 0.12817 | 0.16479 | -122.2961 | 0.07782 | 0.064087 | 0.20599 | -122.287
2952.125 | 122.319 | -0.10529 | 122.2595 | -0.23376 | 0.044846 | 0.062891 | 0.0066053 | 0.031037 | -0.0058084 | 0.029792 | -0.10803 | 0.027692 | 0.037736 | 0.050738 | -0.0017453 | 0.026504 | -0.004578 | 0.045776 | 0.036621 | 0.018311 | 0.064087 | 0.013733 | -0.1236 | 0.036621 | 0.027466 | -0.073242 | 0.059509 | 0.050354 | -0.054932 | -0.11444 | 0.11902 | -0.01831 | -122.1954 | 0.15106 | 0.1236 | 0.14191 | -122.2641 | 0.050354 | -0.009155 | -122.2 | 0.14191 | 0.032044 | 0.041199 | -122.2092 | 0.16937 | 0.10071 | 0.14191 | -122.3831 | 0.16479 | 0.15564 | 0.13275 | -122.374
2953.9062 | 122.438 | -0.059509 | 122.2 | 0.010376 | 0.043564 | 0.061182 | 0.0051099 | 0.033601 | -0.008372 | 0.029578 | 0.067444 | 0.027478 | 0.037736 | 0.049456 | -0.0030271 | 0.02565 | 0.009155 | 0.064087 | 0.064087 | 0.036621 | 0.054932 | 0.045776 | -0.07782 | 0.068665 | 0.068665 | 0 | 0.018311 | 0.013733 | -0.027466 | -0.086975 | 0.10528 | -0.018311 | -122.1451 | 0.1236 | 0.09613 | 0.11444 | -122.1909 | 0.032043 | -0.027466 | -122.1817 | 0.12817 | 0.059509 | 0.086975 | -122.1863 | 0.11444 | 0.068664 | 0.1236 | -122.2778 | 0.07782 | 0.073242 | 0.12817 | -122.287
2955.6562 | 122.3282 | -0.10529 | 122.287 | 0.056152 | 0.0457 | 0.061182 | 0.0010511 | 0.029115 | 0.00017302 | 0.033637 | -0.0012209 | 0.030896 | 0.03795 | 0.051806 | 0.0040225 | 0.024795 | -0.009155 | -0.027466 | -0.045776 | -0.027466 | 0.086975 | 0.022888 | -0.10986 | -0.004578 | -0.027466 | -0.11902 | 0.073242 | 0.050354 | -0.045776 | -0.10529 | 0.12817 | -0.004577 | -122.2 | 0.07782 | 0.07782 | 0.082397 | -122.2961 | 0.05951 | 0 | -122.2137 | 0.10071 | -0.013733 | -0.013733 | -122.2366 | 0.19226 | 0.096131 | 0.05951 | -122.3969 | 0.17853 | 0.15564 | 0.07782 | -122.3923
2957.3438 | 122.4197 | -0.064087 | 122.2275 | 0.010376 | 0.039933 | 0.063959 | 0.0023329 | 0.03061 | -0.010081 | 0.031287 | 0.067444 | 0.026624 | 0.036668 | 0.050524 | -0.0017453 | 0.027145 | 0.036621 | 0.054932 | 0.059509 | 0.036621 | 0.045776 | 0.068665 | -0.09613 | 0.086975 | 0.086975 | 0.004578 | 0.032043 | 0.022888 | -0.036621 | -0.07782 | 0.13275 | -0.032043 | -122.1817 | 0.11902 | 0.10071 | 0.13275 | -122.1909 | 0.027466 | -0.013733 | -122.1954 | 0.15106 | 0.068665 | 0.082398 | -122.2046 | 0.10986 | 0.10071 | 0.1236 | -122.3236 | 0.09613 | 0.086975 | 0.15106 | -122.3053
2959.1094 | 122.4335 | -0.054932 | 122.2321 | -0.13458 | 0.04506 | 0.062036 | 0.0059643 | 0.029969 | -0.0085856 | 0.031287 | -0.13092 | 0.027692 | 0.0356 | 0.049456 | -0.00024989 | 0.027572 | 0.10529 | 0.16479 | 0.1236 | 0.082397 | 0.036621 | 0.041199 | -0.086975 | 0.13733 | 0.18768 | 0.054932 | 0.027466 | -0.004578 | -0.004578 | -0.064087 | 0.096131 | -0.032043 | -122.1954 | 0.21973 | 0.13733 | 0.16937 | -122.1268 | 0.050354 | -0.009155 | -122.2046 | 0.19226 | 0.10986 | 0.11902 | -122.2366 | 0.091553 | 0.16022 | 0.17853 | -122.319 | 0.082398 | 0.050354 | 0.24261 | -122.2961
2960.7969 | 122.374 | -0.10071 | 122.2504 | -0.15747 | 0.046555 | 0.059045 | 0.0061781 | 0.033387 | -0.001536 | 0.029151 | -0.26825 | 0.029401 | 0.037096 | 0.051806 | -0.00067729 | 0.024368 | 0.013733 | 0.004578 | -0.022888 | 0.004578 | 0.07782 | 0.004578 | -0.13733 | 0.032043 | 0.045776 | -0.09613 | 0.068665 | 0.041199 | -0.054932 | -0.10529 | 0.10529 | -0.036621 | -122.1725 | 0.10529 | 0.10529 | 0.14191 | -122.2366 | 0.045776 | -0.004578 | -122.1817 | 0.13275 | 0.004578 | 0.009156 | -122.2092 | 0.17853 | 0.11444 | 0.07782 | -122.3877 | 0.16937 | 0.14191 | 0.14648 | -122.3557
2962.5469 | 122.3831 | -0.07782 | 122.2229 | -0.19562 | 0.046555 | 0.060968 | 0.0087415 | 0.028901 | -0.0062356 | 0.031928 | -0.15381 | 0.028974 | 0.037309 | 0.052447 | -0.0017453 | 0.026077 | 0.086975 | 0.13275 | 0.1236 | 0.068665 | 0.050354 | 0.045776 | -0.10529 | 0.13275 | 0.16479 | 0.032043 | 0.013733 | 0.018311 | -0.027466 | -0.068665 | 0.1236 | -0.027466 | -122.1725 | 0.21057 | 0.14649 | 0.17395 | -122.1359 | 0.050354 | 0.009155 | -122.2092 | 0.21057 | 0.10986 | 0.10071 | -122.2046 | 0.12817 | 0.16479 | 0.20142 | -122.3282 | 0.091553 | 0.096131 | 0.24261 | -122.2916
2964.3125 | 122.3282 | -0.10071 | 122.2549 | -0.1651 | 0.044205 | 0.064386 | 0.0023329 | 0.031251 | -0.004313 | 0.030433 | -0.22247 | 0.027478 | 0.0356 | 0.050951 | -0.0011045 | 0.0233 | 0.068665 | 0.11444 | 0.091553 | 0.068665 | 0.036621 | 0.045776 | -0.10529 | 0.10071 | 0.12817 | 0.018311 | 0.036621 | 0.013733 | -0.036621 | -0.091553 | 0.14648 | -0.004578 | -122.2183 | 0.21515 | 0.16937 | 0.17395 | -122.1863 | 0.064087 | 0.009155 | -122.2183 | 0.20142 | 0.11902 | 0.10986 | -122.2412 | 0.13733 | 0.16937 | 0.19226 | -122.3602 | 0.13733 | 0.11444 | 0.22888 | -122.3465
2966 | 122.3648 | -0.086975 | 122.2549 | -0.19562 | 0.047623 | 0.06225 | 0.00083745 | 0.030824 | 0.00038662 | 0.03321 | -0.22247 | 0.028546 | 0.037309 | 0.052447 | 0.0044497 | 0.021377 | 0.027466 | 0.009155 | -0.009155 | 0.009155 | 0.07782 | 0.013733 | -0.11902 | 0.064087 | 0.054932 | -0.064087 | 0.059509 | 0.054932 | -0.045776 | -0.10529 | 0.10071 | -0.032044 | -122.1771 | 0.09613 | 0.09613 | 0.12817 | -122.2275 | 0.041199 | -0.018311 | -122.1954 | 0.15106 | 0.022888 | 0.041199 | -122.2 | 0.16479 | 0.11444 | 0.07782 | -122.374 | 0.14648 | 0.14191 | 0.14191 | -122.3602
2967.75 | 122.4243 | -0.064087 | 122.2687 | 0.018005 | 0.043564 | 0.06225 | 0.0027601 | 0.028688 | -0.0087992 | 0.031714 | 0.052185 | 0.025983 | 0.037309 | 0.049669 | -0.0015317 | 0.027145 | 0.027466 | 0.059509 | 0.050354 | 0.018311 | 0.050354 | 0.041199 | -0.082397 | 0.091553 | 0.091553 | 0 | 0.027466 | 0.027466 | -0.022888 | -0.086975 | 0.10529 | -0.01831 | -122.2183 | 0.1236 | 0.082398 | 0.10071 | -122.2412 | 0.041199 | -0.022888 | -122.2412 | 0.15564 | 0.064087 | 0.086975 | -122.2412 | 0.11444 | 0.091553 | 0.11444 | -122.3511 | 0.091553 | 0.091553 | 0.15564 | -122.3557
2969.4531 | 122.406 | -0.073242 | 122.1954 | 0.033264 | 0.043351 | 0.062463 | -0.00023075 | 0.032533 | -0.0062356 | 0.03086 | 0.059815 | 0.029615 | 0.036455 | 0.052447 | -0.00046349 | 0.023941 | 0.027466 | 0.07782 | 0.050354 | 0.018311 | 0.036621 | 0.036621 | -0.09613 | 0.10529 | 0.086975 | -0.009155 | 0.036621 | 0.018311 | -0.027466 | -0.09613 | 0.10986 | -0.022888 | -122.1588 | 0.15106 | 0.091553 | 0.11444 | -122.168 | 0.045776 | -0.022888 | -122.1588 | 0.17853 | 0.064087 | 0.086975 | -122.1771 | 0.10986 | 0.10071 | 0.1236 | -122.2916 | 0.10986 | 0.091553 | 0.16022 | -122.2916
2971.2031 | 122.3694 | -0.10071 | 122.2321 | -0.17273 | 0.047837 | 0.061395 | 0.0042555 | 0.033387 | 0.00017302 | 0.031714 | -0.2301 | 0.029828 | 0.036668 | 0.052233 | 0.0023135 | 0.022873 | 0.013733 | 0.009155 | -0.018311 | 0 | 0.082397 | 0.009155 | -0.13275 | 0.054932 | 0.054932 | -0.050354 | 0.059509 | 0.027466 | -0.032043 | -0.10529 | 0.10986 | -0.032043 | -122.1497 | 0.10986 | 0.10071 | 0.13275 | -122.2183 | 0.068665 | -0.004578 | -122.1725 | 0.15564 | 0.050354 | 0.054932 | -122.2046 | 0.18311 | 0.11444 | 0.082397 | -122.3648 | 0.16022 | 0.12817 | 0.15564 | -122.3373
2972.9688 | 122.4243 | -0.064087 | 122.2092 | 0.0027468 | 0.043137 | 0.060114 | 0.0019055 | 0.031892 | -0.0085856 | 0.031928 | 0.052185 | 0.027051 | 0.037736 | 0.052874 | -0.0053769 | 0.025009 | 0.013733 | 0.059509 | 0.059509 | 0.036621 | 0.059509 | 0.050354 | -0.11902 | 0.07782 | 0.082397 | 0.009155 | 0.022888 | -0.004578 | -0.009155 | -0.045776 | 0.11444 | -0.054932 | -122.1497 | 0.1236 | 0.10071 | 0.15564 | -122.1954 | 0.054932 | 0.018311 | -122.1863 | 0.14191 | 0.073242 | 0.054931 | -122.2137 | 0.1236 | 0.07782 | 0.1236 | -122.3282 | 0.086975 | 0.059509 | 0.14648 | -122.2549
2974.6562 | 122.3785 | -0.073242 | 122.2549 | -0.1651 | 0.048691 | 0.061395 | 0.0051099 | 0.033387 | 0.001882 | 0.030219 | -0.19196 | 0.03111 | 0.039232 | 0.053087 | 0.0012455 | 0.0233 | 0.041199 | 0.018311 | 0 | 0.027466 | 0.073242 | 0.013733 | -0.11902 | 0.068665 | 0.073242 | -0.073242 | 0.036621 | 0.022888 | -0.045776 | -0.10986 | 0.086975 | -0.045777 | -122.1817 | 0.091553 | 0.10071 | 0.14649 | -122.2137 | 0.027466 | -0.036621 | -122.2183 | 0.14191 | 0 | 0.036621 | -122.2321 | 0.14648 | 0.11444 | 0.073242 | -122.374 | 0.10986 | 0.09613 | 0.14648 | -122.3648
2976.4062 | 122.374 | -0.10071 | 122.2412 | -0.25665 | 0.048905 | 0.062036 | 0.0051099 | 0.031037 | -0.0030314 | 0.032355 | -0.21484 | 0.027478 | 0.037096 | 0.051806 | -0.00089089 | 0.026718 | -0.009155 | 0 | -0.027466 | -0.018311 | 0.07782 | 0.009155 | -0.12817 | 0.013733 | 0.027466 | -0.09613 | 0.073242 | 0.045776 | -0.059509 | -0.11902 | 0.10986 | -0.027466 | -122.1634 | 0.10071 | 0.082397 | 0.10986 | -122.2504 | 0.041199 | -0.018311 | -122.168 | 0.11444 | 0.004578 | 0.022889 | -122.1954 | 0.17853 | 0.091553 | 0.073242 | -122.3694 | 0.17395 | 0.14648 | 0.12817 | -122.3602
2978.0938 | 122.374 | -0.086975 | 122.2275 | 0.10193 | 0.046128 | 0.059686 | -1.7146e-05 | 0.030183 | 0.00081382 | 0.034278 | 0.090332 | 0.03111 | 0.034746 | 0.053087 | 0.0012455 | 0.026291 | -0.013733 | -0.013733 | -0.045776 | -0.013733 | 0.068665 | 0.022888 | -0.11902 | 0.045776 | -0.013733 | -0.10529 | 0.054932 | 0.036621 | -0.045776 | -0.10071 | 0.10986 | -0.032044 | -122.1588 | 0.073242 | 0.073242 | 0.10529 | -122.2412 | 0.041199 | -0.013733 | -122.1725 | 0.13275 | -0.018311 | -0.004578 | -122.1909 | 0.15564 | 0.073242 | 0.041199 | -122.3465 | 0.14191 | 0.1236 | 0.073242 | -122.3282
2979.8438 | 122.3511 | -0.10529 | 122.2275 | 0.079041 | 0.044419 | 0.059473 | 0.00019645 | 0.030397 | -0.00089518 | 0.031714 | 0.075073 | 0.031323 | 0.038164 | 0.050524 | 0.0012455 | 0.025222 | -0.022888 | -0.018311 | -0.045776 | -0.018311 | 0.07782 | 0.009155 | -0.1236 | 0.032043 | -0.004578 | -0.10071 | 0.045776 | 0.041199 | -0.045776 | -0.09613 | 0.11444 | -0.01831 | -122.1497 | 0.086975 | 0.086975 | 0.10528 | -122.2504 | 0.05951 | 0.009156 | -122.1817 | 0.13733 | 0.004578 | -0.004578 | -122.1863 | 0.18311 | 0.082398 | 0.05951 | -122.3511 | 0.15106 | 0.14649 | 0.10071 | -122.3236
2981.6094 | 122.438 | -0.050354 | 122.2046 | -0.14984 | 0.044632 | 0.063318 | 0.0055371 | 0.028901 | -0.0096536 | 0.032996 | -0.085144 | 0.027265 | 0.039018 | 0.052874 | -0.0043087 | 0.026077 | 0.064087 | 0.17395 | 0.1236 | 0.07782 | 0.059509 | 0.032043 | -0.082397 | 0.15106 | 0.17395 | 0.073242 | 0.018311 | -0.009155 | -0.018311 | -0.064087 | 0.082397 | -0.032043 | -122.1451 | 0.2243 | 0.12817 | 0.16022 | -122.1405 | 0.032043 | -0.013733 | -122.1863 | 0.20142 | 0.1236 | 0.13733 | -122.2137 | 0.10986 | 0.11444 | 0.17395 | -122.287 | 0.068665 | 0.041199 | 0.2243 | -122.2687
2983.3125 | 122.3373 | -0.091553 | 122.2504 | -0.17273 | 0.0457 | 0.060114 | 0.0046827 | 0.033601 | -0.006663 | 0.030219 | -0.1767 | 0.028119 | 0.036668 | 0.049669 | -0.0030271 | 0.02565 | 0.050354 | 0.10986 | 0.086975 | 0.059509 | 0.032043 | 0.050354 | -0.086975 | 0.10071 | 0.13733 | 0.013733 | 0.022888 | 0.013733 | -0.027466 | -0.091553 | 0.14191 | 0.004578 | -122.2183 | 0.20142 | 0.15106 | 0.14648 | -122.2 | 0.064087 | 0 | -122.2275 | 0.19226 | 0.10529 | 0.10529 | -122.2366 | 0.1236 | 0.14191 | 0.17853 | -122.3373 | 0.11444 | 0.10529 | 0.22888 | -122.3419
2985.0781 | 122.3236 | -0.10529 | 122.2641 | 0.056152 | 0.047623 | 0.059686 | -0.0021533 | 0.032746 | 0.0014548 | 0.033851 | -0.016479 | 0.028974 | 0.035173 | 0.053728 | 0.0044497 | 0.024154 | -0.009155 | -0.036621 | -0.059509 | -0.036621 | 0.082397 | 0.022888 | -0.1236 | 0 | -0.022888 | -0.12817 | 0.07782 | 0.050354 | -0.054932 | -0.10071 | 0.12817 | -0.01831 | -122.1817 | 0.068665 | 0.068665 | 0.086975 | -122.2733 | 0.050354 | 0.004578 | -122.1863 | 0.10529 | -0.022888 | -0.027466 | -122.2137 | 0.18768 | 0.096131 | 0.045777 | -122.3877 | 0.18311 | 0.15564 | 0.082398 | -122.3648
2986.7656 | 122.3328 | -0.10529 | 122.2687 | -0.18799 | 0.044419 | 0.061609 | 0.0044691 | 0.031892 | -0.0062356 | 0.030006 | -0.19958 | 0.028333 | 0.036668 | 0.051378 | -0.0021725 | 0.026931 | 0.068665 | 0.10529 | 0.07782 | 0.054932 | 0.064087 | 0.036621 | -0.07782 | 0.082397 | 0.11902 | -0.004578 | 0.036621 | 0.013733 | -0.032043 | -0.086975 | 0.14191 | 0.027466 | -122.2046 | 0.21057 | 0.16022 | 0.13275 | -122.2 | 0.073243 | 0.018311 | -122.2321 | 0.18768 | 0.10071 | 0.082397 | -122.2549 | 0.16937 | 0.17395 | 0.18311 | -122.3465 | 0.14191 | 0.11902 | 0.22431 | -122.3557
2988.5156 | 122.4106 | -0.073242 | 122.2412 | 0.033264 | 0.042282 | 0.061182 | 0.0034009 | 0.029756 | -0.006663 | 0.031287 | 0.052185 | 0.029615 | 0.034105 | 0.051165 | -0.00046349 | 0.026931 | 0.027466 | 0.068665 | 0.054932 | 0.027466 | 0.041199 | 0.054932 | -0.10071 | 0.07782 | 0.086975 | 0.009155 | 0.032043 | 0.013733 | 0 | -0.082397 | 0.12817 | -0.027466 | -122.2 | 0.14191 | 0.10071 | 0.12817 | -122.2137 | 0.073242 | -0.009155 | -122.2092 | 0.15106 | 0.082397 | 0.091552 | -122.2275 | 0.11444 | 0.10071 | 0.12817 | -122.3419 | 0.10529 | 0.086975 | 0.16022 | -122.3236
2990.2031 | 122.3602 | -0.068665 | 122.2504 | -0.11169 | 0.048905 | 0.060541 | 0.0044691 | 0.031678 | 0.00081382 | 0.033423 | -0.16907 | 0.030255 | 0.036455 | 0.053728 | 0.0010317 | 0.022873 | 0.045776 | 0.027466 | 0.009155 | 0.027466 | 0.086975 | 0.027466 | -0.11444 | 0.086975 | 0.082397 | -0.036621 | 0.064087 | 0.032043 | -0.050354 | -0.091553 | 0.096131 | -0.045776 | -122.1634 | 0.096131 | 0.096131 | 0.14191 | -122.2046 | 0.018311 | -0.022888 | -122.1863 | 0.15564 | 0.032044 | 0.054932 | -122.2183 | 0.15564 | 0.11444 | 0.07782 | -122.3648 | 0.13275 | 0.10071 | 0.15106 | -122.3419
2991.9688 | 122.406 | -0.050354 | 122.2275 | 0.11719 | 0.044205 | 0.060327 | 0.0014783 | 0.031465 | -0.006663 | 0.032142 | 0.10559 | 0.026837 | 0.036241 | 0.049029 | 0.0014591 | 0.027359 | 0.064087 | 0.13733 | 0.10529 | 0.054932 | 0.022888 | 0.068665 | -0.068665 | 0.13275 | 0.13275 | 0.036621 | 0.027466 | 0.013733 | -0.009155 | -0.064087 | 0.11902 | -0.018311 | -122.2046 | 0.18768 | 0.10529 | 0.1236 | -122.1634 | 0.041199 | -0.013733 | -122.2 | 0.18311 | 0.086975 | 0.10071 | -122.2137 | 0.073242 | 0.11444 | 0.15564 | -122.2961 | 0.07782 | 0.064087 | 0.18311 | -122.2916
2993.7344 | 122.4335 | -0.059509 | 122.2366 | 0.10956 | 0.043778 | 0.058832 | -1.7146e-05 | 0.031465 | -0.0038858 | 0.031714 | 0.13611 | 0.027906 | 0.034959 | 0.050951 | 0.0020999 | 0.025009 | 0.09613 | 0.11902 | 0.082397 | 0.064087 | 0.027466 | 0.059509 | -0.073242 | 0.14648 | 0.13733 | 0.036621 | 0 | -0.013733 | -0.022888 | -0.050354 | 0.11902 | -0.013733 | -122.2092 | 0.17853 | 0.1236 | 0.13733 | -122.1405 | 0.036621 | 0.009155 | -122.2366 | 0.20599 | 0.09613 | 0.086975 | -122.2504 | 0.086975 | 0.15564 | 0.14191 | -122.3099 | 0.059509 | 0.045776 | 0.19684 | -122.287
2995.4844 | 122.3145 | -0.10071 | 122.2778 | 0.048523 | 0.046341 | 0.062677 | 0.0010511 | 0.033387 | 0.00038662 | 0.033423 | -0.0088499 | 0.032178 | 0.036241 | 0.052233 | 0.0038089 | 0.026291 | 0.018311 | -0.027466 | -0.027466 | -0.013733 | 0.082397 | 0.022888 | -0.11902 | -0.013733 | -0.009155 | -0.12817 | 0.068665 | 0.050354 | -0.045776 | -0.086975 | 0.1236 | -0.018311 | -122.1954 | 0.073242 | 0.086975 | 0.10529 | -122.2595 | 0.054932 | 0.013733 | -122.2092 | 0.086975 | -0.027466 | -0.041199 | -122.2275 | 0.18311 | 0.11902 | 0.073242 | -122.3969 | 0.16937 | 0.15106 | 0.091553 | -122.3648
2997.1875 | 122.3602 | -0.086975 | 122.2549 | -0.24139 | 0.046768 | 0.060968 | 0.0040417 | 0.034242 | -0.0036722 | 0.032355 | -0.22247 | 0.030469 | 0.036882 | 0.051592 | -0.0019589 | 0.026077 | -0.018311 | -0.004578 | -0.032043 | -0.004578 | 0.07782 | -0.004578 | -0.13733 | 0.009155 | 0.027466 | -0.086975 | 0.045776 | 0.045776 | -0.032043 | -0.10529 | 0.082397 | -0.050354 | -122.1771 | 0.082397 | 0.082397 | 0.13275 | -122.2733 | 0.054932 | -0.018311 | -122.2092 | 0.09613 | 0 | 0.018311 | -122.2092 | 0.16479 | 0.068664 | 0.054932 | -122.3923 | 0.13275 | 0.13275 | 0.11444 | -122.3602
2998.9531 | 122.4197 | -0.064087 | 122.2549 | 0.025635 | 0.042282 | 0.06225 | 0.0016919 | 0.032746 | -0.010295 | 0.029578 | 0.067444 | 0.026624 | 0.034532 | 0.05266 | 0.0012455 | 0.027999 | 0.018311 | 0.073242 | 0.045776 | 0.022888 | 0.050354 | 0.054932 | -0.10986 | 0.07782 | 0.091553 | 0 | 0.036621 | 0.013733 | -0.013733 | -0.073242 | 0.11902 | -0.045776 | -122.2046 | 0.13733 | 0.086975 | 0.13275 | -122.2366 | 0.050354 | -0.009155 | -122.2183 | 0.14191 | 0.064087 | 0.073242 | -122.2412 | 0.11444 | 0.082398 | 0.10986 | -122.3648 | 0.10071 | 0.07782 | 0.15564 | -122.3282
3000.7188 | 122.4197 | -0.041199 | 122.2275 | 0.033264 | 0.043778 | 0.059259 | 0.0038281 | 0.03061 | -0.0051676 | 0.030006 | 0.052185 | 0.029187 | 0.034959 | 0.053087 | -0.0023861 | 0.025863 | 0.045776 | 0.054932 | 0.054932 | 0.036621 | 0.050354 | 0.045776 | -0.082397 | 0.086975 | 0.082397 | 0.009155 | 0.036621 | 0.009155 | -0.022888 | -0.07782 | 0.086975 | -0.041198 | -122.1771 | 0.096131 | 0.07782 | 0.11902 | -122.1817 | 0.018311 | -0.036621 | -122.1909 | 0.12817 | 0.050354 | 0.086975 | -122.2183 | 0.091553 | 0.086975 | 0.096131 | -122.3099 | 0.07782 | 0.050354 | 0.1236 | -122.3053
3002.4844 | 122.4609 | -0.054932 | 122.2 | -0.012512 | 0.042496 | 0.060541 | 0.0040417 | 0.031465 | -0.0064492 | 0.028937 | 0.036926 | 0.029187 | 0.038377 | 0.051165 | -0.00089089 | 0.024368 | 0.022888 | 0.036621 | 0.054932 | 0.036621 | 0.050354 | 0.054932 | -0.10529 | 0.082397 | 0.086975 | 0.004578 | 0.032043 | 0.004578 | -0.027466 | -0.082397 | 0.10986 | -0.050354 | -122.1497 | 0.091553 | 0.091553 | 0.14191 | -122.1771 | 0.027466 | -0.027465 | -122.168 | 0.13733 | 0.05951 | 0.086975 | -122.1954 | 0.10529 | 0.07782 | 0.10986 | -122.3053 | 0.086975 | 0.05951 | 0.14191 | -122.2824
3004.1875 | 122.4518 | -0.036621 | 122.2366 | -0.11169 | 0.045487 | 0.059686 | 0.0051099 | 0.030824 | -0.0075174 | 0.028937 | -0.10803 | 0.026837 | 0.0356 | 0.053728 | -0.0015317 | 0.024154 | 0.086975 | 0.1236 | 0.10529 | 0.068665 | 0.064087 | 0.041199 | -0.091553 | 0.15106 | 0.17395 | 0.068665 | 0.004578 | 0.018311 | -0.004578 | -0.045776 | 0.07782 | -0.054932 | -122.1725 | 0.16022 | 0.10529 | 0.16022 | -122.1497 | 0.032043 | -0.009155 | -122.2321 | 0.18768 | 0.10529 | 0.11444 | -122.2183 | 0.10071 | 0.1236 | 0.14191 | -122.3282 | 0.041199 | 0.054932 | 0.21057 | -122.2824
3005.9375 | 122.4472 | -0.054932 | 122.2412 | 0.010376 | 0.042496 | 0.061182 | 0.00019645 | 0.029542 | -0.0068766 | 0.030433 | 0.0064086 | 0.027051 | 0.033678 | 0.05031 | 0.00039091 | 0.025009 | 0.045776 | 0.059509 | 0.045776 | 0.032043 | 0.050354 | 0.036621 | -0.091553 | 0.10529 | 0.086975 | -0.009155 | 0.032043 | 0.018311 | -0.018311 | -0.07782 | 0.091553 | -0.036621 | -122.1909 | 0.11444 | 0.086975 | 0.1236 | -122.1954 | 0.036621 | -0.022888 | -122.2092 | 0.16022 | 0.045777 | 0.068665 | -122.2229 | 0.10529 | 0.10071 | 0.10071 | -122.3328 | 0.086975 | 0.073243 | 0.14191 | -122.319
3007.6875 | 122.3785 | -0.054932 | 122.2366 | 0.14008 | 0.042923 | 0.060754 | 0.00083745 | 0.030183 | -0.0028178 | 0.031928 | 0.090332 | 0.027051 | 0.036241 | 0.051378 | 0.0033817 | 0.025009 | 0.11444 | 0.1236 | 0.11444 | 0.064087 | 0.045776 | 0.068665 | -0.073242 | 0.15564 | 0.12817 | 0.045776 | 0.027466 | 0 | -0.013733 | -0.068665 | 0.1236 | -0.01831 | -122.1909 | 0.17853 | 0.11902 | 0.13733 | -122.1222 | 0.041199 | -0.013733 | -122.2092 | 0.21057 | 0.10071 | 0.11444 | -122.2366 | 0.10071 | 0.16937 | 0.16937 | -122.3099 | 0.082398 | 0.054932 | 0.18311 | -122.3053
3009.4531 | 122.3145 | -0.10529 | 122.2687 | -0.21851 | 0.045914 | 0.062891 | 0.0055371 | 0.034242 | -0.002604 | 0.02851 | -0.18433 | 0.028119 | 0.036241 | 0.050524 | -0.00046349 | 0.025222 | 0.027466 | 0.022888 | 0.004578 | 0.009155 | 0.07782 | 0.032043 | -0.1236 | 0.045776 | 0.032043 | -0.064087 | 0.045776 | 0.045776 | -0.059509 | -0.1236 | 0.13733 | -0.01831 | -122.1909 | 0.12817 | 0.11444 | 0.13275 | -122.2412 | 0.045777 | -0.01831 | -122.2229 | 0.15106 | 0.041199 | 0.059509 | -122.2229 | 0.18311 | 0.13275 | 0.10986 | -122.3923 | 0.15106 | 0.15106 | 0.13733 | -122.3923
3011.1562 | 122.3328 | -0.10071 | 122.2595 | 0.018005 | 0.04506 | 0.059686 | 0.00019645 | 0.031465 | 0.0023092 | 0.034919 | -0.016479 | 0.029401 | 0.037523 | 0.052019 | 0.0040225 | 0.022232 | -0.013733 | -0.041199 | -0.050354 | -0.022888 | 0.082397 | 0.009155 | -0.14191 | 0.027466 | -0.027466 | -0.11444 | 0.050354 | 0.036621 | -0.045776 | -0.10529 | 0.10986 | -0.041199 | -122.1771 | 0.059509 | 0.07782 | 0.11902 | -122.2733 | 0.054932 | -0.004578 | -122.2092 | 0.12817 | -0.013733 | -0.009155 | -122.2229 | 0.18311 | 0.086975 | 0.050354 | -122.4014 | 0.15106 | 0.13733 | 0.073242 | -122.3648
3012.9062 | 122.3694 | -0.07782 | 122.2321 | -0.18799 | 0.047623 | 0.057977 | 0.0036145 | 0.033601 | 0.0012412 | 0.035346 | -0.19958 | 0.029828 | 0.039232 | 0.050738 | 0.0012455 | 0.024795 | 0.027466 | 0.027466 | -0.009155 | 0.022888 | 0.09613 | 0.018311 | -0.12817 | 0.059509 | 0.086975 | -0.059509 | 0.045776 | 0.041199 | -0.041199 | -0.091553 | 0.096131 | -0.050354 | -122.1359 | 0.10529 | 0.10071 | 0.15106 | -122.2046 | 0.036621 | -0.013733 | -122.1863 | 0.13733 | 0.018311 | 0.032044 | -122.1909 | 0.17395 | 0.10529 | 0.068665 | -122.3602 | 0.1236 | 0.11902 | 0.16479 | -122.3236
3014.6719 | 122.4792 | -0.050354 | 122.2321 | -0.065918 | 0.042923 | 0.062891 | 0.0046827 | 0.029328 | -0.00944 | 0.03086 | -0.062256 | 0.028333 | 0.035814 | 0.050524 | -0.0017453 | 0.025863 | 0.036621 | 0.13275 | 0.091553 | 0.059509 | 0.050354 | 0.050354 | -0.11444 | 0.14191 | 0.16479 | 0.064087 | 0.027466 | -0.004578 | -0.004578 | -0.045776 | 0.10071 | -0.064087 | -122.1817 | 0.18311 | 0.10986 | 0.17395 | -122.1954 | 0.045776 | 0.004578 | -122.2046 | 0.19226 | 0.11444 | 0.10986 | -122.2366 | 0.10071 | 0.086975 | 0.14191 | -122.3465 | 0.07782 | 0.045776 | 0.21515 | -122.2778
3016.4219 | 122.406 | -0.064087 | 122.2549 | 0.14771 | 0.046982 | 0.060114 | 0.0027601 | 0.032746 | -0.0019632 | 0.032569 | 0.15137 | 0.027478 | 0.037523 | 0.051592 | 0.0014591 | 0.026077 | 0.10986 | 0.11902 | 0.11902 | 0.064087 | 0.032043 | 0.07782 | -0.086975 | 0.14648 | 0.13275 | 0.041199 | 0.004578 | -0.009155 | -0.013733 | -0.073242 | 0.14191 | -0.022888 | -122.2229 | 0.18311 | 0.12817 | 0.15106 | -122.1451 | 0.050354 | -0.009155 | -122.2504 | 0.21057 | 0.10529 | 0.11444 | -122.2641 | 0.09613 | 0.17395 | 0.18311 | -122.3419 | 0.068665 | 0.054932 | 0.19684 | -122.3282
3018.125 | 122.4747 | -0.045776 | 122.2458 | -0.050659 | 0.043137 | 0.061395 | 0.0016919 | 0.031251 | -0.0075174 | 0.03086 | -0.046997 | 0.02876 | 0.033464 | 0.050738 | -0.00089089 | 0.025222 | 0.054932 | 0.086975 | 0.082397 | 0.050354 | 0.059509 | 0.050354 | -0.09613 | 0.13733 | 0.13733 | 0.054932 | 0.032043 | 0.004578 | -0.009155 | -0.064087 | 0.09613 | -0.050354 | -122.1863 | 0.13275 | 0.09613 | 0.14648 | -122.1909 | 0.036621 | -0.018311 | -122.2137 | 0.18311 | 0.10071 | 0.11902 | -122.2412 | 0.10528 | 0.10071 | 0.12817 | -122.3419 | 0.077819 | 0.050354 | 0.18311 | -122.3099
3019.8906 | 122.3694 | -0.086975 | 122.2504 | -0.17273 | 0.048264 | 0.059045 | 0.0059643 | 0.034242 | -4.058e-05 | 0.030646 | -0.24536 | 0.030683 | 0.038377 | 0.054156 | 0.0010317 | 0.021591 | 0.032043 | 0 | -0.013733 | 0.018311 | 0.073242 | 0.022888 | -0.1236 | 0.064087 | 0.050354 | -0.054932 | 0.064087 | 0.050354 | -0.050354 | -0.082397 | 0.10986 | -0.036621 | -122.1771 | 0.086975 | 0.10529 | 0.14191 | -122.2183 | 0.036621 | 0.004578 | -122.1863 | 0.15106 | 0.032043 | 0.027465 | -122.2 | 0.16022 | 0.11902 | 0.073242 | -122.374 | 0.15106 | 0.13733 | 0.13733 | -122.3328
3021.6406 | 122.3648 | -0.086975 | 122.2458 | -0.14984 | 0.047837 | 0.060327 | 0.0019055 | 0.03061 | -0.00025418 | 0.031501 | -0.16907 | 0.029828 | 0.037523 | 0.05266 | 0.00039091 | 0.022232 | 0.036621 | 0.050354 | 0.022888 | 0.022888 | 0.082397 | 0.013733 | -0.12817 | 0.086975 | 0.07782 | -0.059509 | 0.054932 | 0.032043 | -0.041199 | -0.086975 | 0.10071 | -0.041199 | -122.1634 | 0.13733 | 0.10986 | 0.15106 | -122.2092 | 0.045776 | 0 | -122.1909 | 0.17395 | 0.027466 | 0.027466 | -122.2137 | 0.16937 | 0.1236 | 0.10986 | -122.374 | 0.14191 | 0.11902 | 0.16479 | -122.3328
3023.3281 | 122.319 | -0.11444 | 122.2549 | 0.056152 | 0.046982 | 0.060327 | 0.00062385 | 0.031892 | -0.00046778 | 0.033637 | -0.0088499 | 0.03111 | 0.036455 | 0.051378 | 0.0042361 | 0.024795 | -0.013733 | -0.009155 | -0.045776 | -0.022888 | 0.07782 | 0.027466 | -0.13733 | 0.004578 | 0 | -0.10071 | 0.050354 | 0.036621 | -0.054932 | -0.10529 | 0.14191 | -0.022888 | -122.1771 | 0.10529 | 0.091553 | 0.11444 | -122.2687 | 0.059509 | 0.009155 | -122.2046 | 0.11902 | 0.013733 | 0.004578 | -122.2183 | 0.19226 | 0.10071 | 0.068665 | -122.3923 | 0.16479 | 0.15106 | 0.11444 | -122.3602
3025.1094 | 122.3465 | -0.091553 | 122.2412 | -0.21851 | 0.046341 | 0.062463 | 0.0027601 | 0.029115 | -0.0040994 | 0.031501 | -0.24536 | 0.028119 | 0.036241 | 0.050738 | -0.0011045 | 0.026077 | -0.036621 | 0.018311 | -0.013733 | -0.018311 | 0.082397 | 0.022888 | -0.14191 | 0.009155 | 0.041199 | -0.073242 | 0.064087 | 0.041199 | -0.054932 | -0.10986 | 0.11444 | -0.050354 | -122.1588 | 0.10986 | 0.073242 | 0.1236 | -122.2778 | 0.036621 | -0.01831 | -122.1771 | 0.10071 | 0.018311 | 0.036621 | -122.2 | 0.17395 | 0.054932 | 0.07782 | -122.3831 | 0.15564 | 0.13275 | 0.13275 | -122.3511
3026.875 | 122.3373 | -0.1236 | 122.2366 | -0.24139 | 0.045914 | 0.059686 | 0.0055371 | 0.032105 | -0.0064492 | 0.032569 | -0.19196 | 0.027906 | 0.03795 | 0.05266 | -0.0023861 | 0.02565 | 0.013733 | 0.082397 | 0.054932 | 0.027466 | 0.059509 | 0.032043 | -0.10986 | 0.045776 | 0.073242 | -0.045776 | 0.068665 | 0.027466 | -0.041199 | -0.09613 | 0.15564 | 0.013733 | -122.1771 | 0.20599 | 0.15106 | 0.13733 | -122.2229 | 0.082397 | 0.027466 | -122.168 | 0.16937 | 0.07782 | 0.050354 | -122.2092 | 0.1831 | 0.13733 | 0.17853 | -122.3465 | 0.19226 | 0.15106 | 0.19684 | -122.3328
3028.6406 | 122.4289 | -0.064087 | 122.2092 | 0.079041 | 0.045914 | 0.0646 | -0.00023075 | 0.03296 | -0.00046778 | 0.032355 | 0.082703 | 0.030469 | 0.034746 | 0.053301 | 0.0018863 | 0.026504 | 0.004578 | 0.004578 | -0.032043 | -0.018311 | 0.068665 | 0.022888 | -0.10986 | 0.064087 | 0.022888 | -0.068665 | 0.050354 | 0.036621 | -0.036621 | -0.086975 | 0.086975 | -0.045776 | -122.1405 | 0.068665 | 0.045776 | 0.091552 | -122.2046 | 0.027466 | -0.022888 | -122.1588 | 0.12817 | -0.004578 | 0.01831 | -122.1725 | 0.13275 | 0.068665 | 0.032044 | -122.319 | 0.11444 | 0.10071 | 0.086975 | -122.2961
3030.3281 | 122.4197 | -0.082397 | 122.2275 | 0.010376 | 0.041855 | 0.060968 | -0.0010851 | 0.029115 | -0.0070902 | 0.032142 | 0.075073 | 0.027906 | 0.034105 | 0.051592 | -0.0019589 | 0.027999 | 0.022888 | 0.059509 | 0.045776 | 0.022888 | 0.054932 | 0.054932 | -0.086975 | 0.082397 | 0.091553 | 0.009155 | 0.013733 | 0.018311 | -0.004578 | -0.073242 | 0.13733 | -0.004578 | -122.1725 | 0.14191 | 0.10528 | 0.10986 | -122.2046 | 0.077819 | 0.009155 | -122.2137 | 0.16479 | 0.091552 | 0.082397 | -122.2092 | 0.13733 | 0.10528 | 0.12817 | -122.3145 | 0.09613 | 0.10071 | 0.17395 | -122.3007
3032.0938 | 122.3373 | -0.10529 | 122.2504 | -0.19562 | 0.045914 | 0.062677 | 0.0070325 | 0.03296 | -0.004954 | 0.030433 | -0.16144 | 0.029187 | 0.037736 | 0.051806 | -0.0025999 | 0.024795 | 0.082397 | 0.10986 | 0.10071 | 0.068665 | 0.036621 | 0.050354 | -0.091553 | 0.10986 | 0.14648 | 0.036621 | 0.027466 | 0.009155 | -0.022888 | -0.086975 | 0.15564 | 0.013733 | -122.2137 | 0.21515 | 0.17395 | 0.16022 | -122.168 | 0.082398 | 0.018311 | -122.2229 | 0.21515 | 0.14191 | 0.1236 | -122.2412 | 0.14191 | 0.18768 | 0.20599 | -122.3419 | 0.13275 | 0.11444 | 0.25177 | -122.3373
3033.7812 | 122.3099 | -0.082397 | 122.2321 | -0.012512 | 0.046768 | 0.057336 | -0.0023669 | 0.034028 | 0.00060022 | 0.031928 | -0.016479 | 0.030683 | 0.036241 | 0.052019 | 0.0018863 | 0.023086 | 0.032043 | -0.027466 | -0.022888 | 0 | 0.073242 | 0.004578 | -0.11902 | 0.009155 | -0.013733 | -0.10986 | 0.045776 | 0.059509 | -0.036621 | -0.11444 | 0.086975 | -0.036622 | -122.1588 | 0.054931 | 0.082397 | 0.11902 | -122.2 | 0.045776 | -0.032044 | -122.1863 | 0.091552 | -0.027466 | 0.004578 | -122.1725 | 0.15564 | 0.11444 | 0.059509 | -122.3511 | 0.12817 | 0.14191 | 0.068664 | -122.3465
3035.5469 | 122.3373 | -0.10529 | 122.2595 | -0.18799 | 0.044846 | 0.059686 | 0.0074597 | 0.034028 | -0.007731 | 0.031928 | -0.19196 | 0.026197 | 0.037096 | 0.052019 | -0.0032407 | 0.025009 | 0.059509 | 0.10986 | 0.091553 | 0.073242 | 0.045776 | 0.045776 | -0.09613 | 0.086975 | 0.15106 | 0.013733 | 0.018311 | 0.027466 | -0.022888 | -0.07782 | 0.15106 | 0.009156 | -122.2137 | 0.21515 | 0.17853 | 0.16937 | -122.2 | 0.082398 | 0.027466 | -122.2412 | 0.19226 | 0.11902 | 0.091553 | -122.2321 | 0.15106 | 0.16479 | 0.19684 | -122.3557 | 0.1236 | 0.13275 | 0.25635 | -122.3373
3037.2969 | 122.4106 | -0.050354 | 122.2275 | 0.14008 | 0.046128 | 0.0599 | 0.0016919 | 0.031037 | -0.0040994 | 0.031928 | 0.12848 | 0.026624 | 0.036027 | 0.050738 | -3.629e-05 | 0.023513 | 0.10986 | 0.10529 | 0.11902 | 0.059509 | 0.032043 | 0.050354 | -0.07782 | 0.15564 | 0.11902 | 0.041199 | -0.004578 | 0.009155 | -0.013733 | -0.064087 | 0.10071 | -0.027466 | -122.1954 | 0.15564 | 0.10986 | 0.13733 | -122.1176 | 0.036621 | -0.013733 | -122.2321 | 0.20599 | 0.091553 | 0.10529 | -122.2183 | 0.082397 | 0.16022 | 0.16937 | -122.3053 | 0.045776 | 0.059509 | 0.16937 | -122.2916
3039.0625 | 122.406 | -0.054932 | 122.2183 | 0.08667 | 0.046341 | 0.061182 | 0.0034009 | 0.03296 | -0.006663 | 0.03086 | 0.13611 | 0.027692 | 0.033678 | 0.052233 | -0.0011045 | 0.025436 | 0.07782 | 0.09613 | 0.10071 | 0.050354 | 0.054932 | 0.045776 | -0.082397 | 0.12817 | 0.09613 | 0.004578 | 0.018311 | 0 | -0.027466 | -0.073242 | 0.10071 | -0.027465 | -122.1634 | 0.15106 | 0.10529 | 0.13275 | -122.1405 | 0.027466 | -0.01831 | -122.2 | 0.18311 | 0.05951 | 0.07782 | -122.2183 | 0.10986 | 0.13275 | 0.15564 | -122.3007 | 0.073243 | 0.054932 | 0.15106 | -122.2916
3040.7656 | 122.3099 | -0.10986 | 122.2504 | -0.096436 | 0.048691 | 0.059686 | 0.0021191 | 0.031251 | 0.0025228 | 0.031714 | -0.14618 | 0.030042 | 0.037523 | 0.05266 | 0.0033817 | 0.0233 | 0.082397 | 0.045776 | 0.018311 | 0.009155 | 0.064087 | 0.022888 | -0.10986 | 0.086975 | 0.064087 | -0.059509 | 0.064087 | 0.036621 | -0.032043 | -0.10071 | 0.13275 | 0 | -122.1863 | 0.15564 | 0.11902 | 0.11902 | -122.168 | 0.07782 | 0.009155 | -122.1863 | 0.19684 | 0.050354 | 0.041199 | -122.2137 | 0.17395 | 0.19226 | 0.12817 | -122.3602 | 0.17395 | 0.14648 | 0.17395 | -122.3511
3042.5156 | 122.4289 | -0.064087 | 122.2183 | 0.079041 | 0.045273 | 0.060327 | 0.00062385 | 0.031037 | -0.001536 | 0.032996 | 0.12085 | 0.029615 | 0.034318 | 0.054369 | 0.0020999 | 0.026504 | 0.013733 | -0.022888 | -0.022888 | -0.009155 | 0.082397 | 0.032043 | -0.1236 | 0.073242 | 0.027466 | -0.064087 | 0.036621 | 0.009155 | -0.032043 | -0.086975 | 0.09613 | -0.059509 | -122.1359 | 0.041199 | 0.054932 | 0.11444 | -122.2046 | 0.032044 | -0.022888 | -122.1817 | 0.13733 | 0 | 0.022888 | -122.2092 | 0.14648 | 0.07782 | 0.041199 | -122.3419 | 0.10071 | 0.073242 | 0.091553 | -122.3053
3044.2031 | 122.3145 | -0.091553 | 122.2733 | -0.21088 | 0.045273 | 0.062891 | 0.0042555 | 0.032533 | -0.004954 | 0.030006 | -0.1004 | 0.026624 | 0.036455 | 0.047961 | -0.0015317 | 0.026291 | 0.013733 | 0.036621 | 0.009155 | 0.004578 | 0.064087 | 0.027466 | -0.13733 | 0.045776 | 0.045776 | -0.068665 | 0.054932 | 0.045776 | -0.045776 | -0.10529 | 0.11902 | -0.045776 | -122.2092 | 0.12817 | 0.096131 | 0.14191 | -122.2595 | 0.045777 | -0.013733 | -122.2183 | 0.13733 | 0.022888 | 0.036621 | -122.2275 | 0.15564 | 0.10529 | 0.10071 | -122.4106 | 0.14649 | 0.13733 | 0.13733 | -122.3785
3045.9688 | 122.3328 | -0.091553 | 122.2824 | 0.040894 | 0.047196 | 0.063318 | 0.0014783 | 0.033814 | -0.0017496 | 0.031501 | 0.021668 | 0.029828 | 0.034959 | 0.051806 | 0.0031681 | 0.026291 | -0.027466 | -0.041199 | -0.054932 | -0.027466 | 0.09613 | 0.027466 | -0.1236 | 0.022888 | -0.004578 | -0.10529 | 0.054932 | 0.050354 | -0.050354 | -0.11902 | 0.11902 | -0.032043 | -122.1863 | 0.050354 | 0.064087 | 0.09613 | -122.3099 | 0.041199 | -0.027466 | -122.2275 | 0.11444 | -0.013733 | 0.013733 | -122.2321 | 0.18768 | 0.064087 | 0.036621 | -122.406 | 0.14649 | 0.14191 | 0.086975 | -122.4014
3047.6562 | 122.3373 | -0.10529 | 122.2733 | -0.081177 | 0.045914 | 0.062036 | 0.0036145 | 0.030824 | 0.00038662 | 0.034278 | -0.1004 | 0.029615 | 0.037736 | 0.05031 | 0.0027407 | 0.026291 | 0.059509 | 0.073242 | 0.041199 | 0.013733 | 0.073242 | 0.009155 | -0.13275 | 0.082397 | 0.068665 | -0.054932 | 0.041199 | 0.036621 | -0.054932 | -0.091553 | 0.11444 | -0.027465 | -122.2 | 0.17853 | 0.11902 | 0.14648 | -122.2137 | 0.050354 | 0.013733 | -122.2321 | 0.18768 | 0.050354 | 0.036621 | -122.2366 | 0.17853 | 0.16479 | 0.14649 | -122.406 | 0.14649 | 0.14191 | 0.17395 | -122.3648
3049.4062 | 122.3145 | -0.10986 | 122.2412 | -0.065918 | 0.047409 | 0.060114 | 0.0042555 | 0.03061 | -0.0011088 | 0.034705 | -0.069885 | 0.031537 | 0.038377 | 0.052874 | 0.00039091 | 0.02565 | 0.045776 | 0.041199 | 0.013733 | 0.018311 | 0.073242 | 0.018311 | -0.13733 | 0.059509 | 0.036621 | -0.082397 | 0.045776 | 0.036621 | -0.050354 | -0.11444 | 0.12817 | -0.027466 | -122.168 | 0.15106 | 0.12817 | 0.15564 | -122.1954 | 0.059509 | -0.004578 | -122.1954 | 0.16937 | 0.027466 | 0.032044 | -122.2046 | 0.18311 | 0.15564 | 0.1236 | -122.3785 | 0.15564 | 0.14648 | 0.14648 | -122.3557
3051.1719 | 122.3099 | -0.086975 | 122.2778 | -0.0048827 | 0.046982 | 0.061823 | 0.0014783 | 0.031465 | -0.0019632 | 0.035132 | 0.021668 | 0.029401 | 0.035387 | 0.051592 | 0.0027407 | 0.026504 | -0.018311 | -0.009155 | -0.036621 | -0.032043 | 0.073242 | 0.018311 | -0.12817 | 0.009155 | 0.009155 | -0.10529 | 0.054932 | 0.045776 | -0.045776 | -0.11444 | 0.10529 | -0.041199 | -122.2046 | 0.07782 | 0.054932 | 0.096131 | -122.2961 | 0.041199 | -0.027466 | -122.2229 | 0.09613 | -0.018311 | 0.009155 | -122.2321 | 0.16022 | 0.068664 | 0.050354 | -122.406 | 0.14191 | 0.13275 | 0.09613 | -122.3923
3052.9219 | 122.3145 | -0.091553 | 122.2641 | -0.23376 | 0.046128 | 0.061395 | 0.0072461 | 0.032533 | -0.0075174 | 0.032142 | -0.16907 | 0.02641 | 0.038805 | 0.050738 | -0.0049497 | 0.027145 | 0 | 0.07782 | 0.045776 | 0.036621 | 0.050354 | 0.022888 | -0.11444 | 0.018311 | 0.082397 | -0.054932 | 0.059509 | 0.018311 | -0.050354 | -0.10071 | 0.11444 | -0.022888 | -122.2137 | 0.16937 | 0.12817 | 0.15106 | -122.2641 | 0.041199 | -0.009155 | -122.2046 | 0.10986 | 0.036621 | 0.045776 | -122.2458 | 0.14191 | 0.091553 | 0.13733 | -122.3785 | 0.15106 | 0.10986 | 0.17395 | -122.3648
3054.6875 | 122.3694 | -0.091553 | 122.2733 | -0.18799 | 0.04805 | 0.061823 | 0.0042555 | 0.034242 | -0.0070902 | 0.031074 | -0.092773 | 0.027692 | 0.036241 | 0.050097 | -0.0030271 | 0.026077 | 0.054932 | 0.13733 | 0.10529 | 0.07782 | 0.050354 | 0.050354 | -0.073242 | 0.10529 | 0.16479 | 0.045776 | 0.018311 | 0.013733 | -0.009155 | -0.073242 | 0.14191 | 0.018311 | -122.2229 | 0.22888 | 0.16937 | 0.15106 | -122.2183 | 0.082398 | 0.018311 | -122.2549 | 0.19684 | 0.13733 | 0.11902 | -122.2595 | 0.14191 | 0.14649 | 0.19684 | -122.3465 | 0.10986 | 0.10529 | 0.25635 | -122.3465
3056.375 | 122.3694 | -0.086975 | 122.2504 | -0.14984 | 0.047837 | 0.060754 | 0.0053235 | 0.030824 | -0.00068138 | 0.032355 | -0.18433 | 0.029828 | 0.037096 | 0.050951 | 0.0014591 | 0.023727 | 0.027466 | 0.027466 | 0 | 0.022888 | 0.073242 | 0 | -0.14648 | 0.073242 | 0.068665 | -0.045776 | 0.041199 | 0.032043 | -0.036621 | -0.086975 | 0.086975 | -0.059509 | -122.1771 | 0.11444 | 0.10986 | 0.16937 | -122.2229 | 0.050354 | 0 | -122.2092 | 0.16022 | 0.041199 | 0.041199 | -122.2183 | 0.16022 | 0.11444 | 0.086975 | -122.3969 | 0.12817 | 0.11902 | 0.15564 | -122.3373
3058.125 | 122.3373 | -0.12817 | 122.2778 | -0.23376 | 0.044419 | 0.058191 | 0.0042555 | 0.033174 | -0.0081582 | 0.029578 | -0.19196 | 0.026197 | 0.035814 | 0.052447 | -0.0019589 | 0.026931 | 0.027466 | 0.10071 | 0.059509 | 0.054932 | 0.050354 | 0.041199 | -0.10529 | 0.059509 | 0.091553 | -0.036621 | 0.041199 | 0.013733 | -0.054932 | -0.10071 | 0.16937 | 0.022888 | -122.2275 | 0.22888 | 0.18311 | 0.16022 | -122.2504 | 0.073242 | 0.027466 | -122.2366 | 0.18768 | 0.091553 | 0.064087 | -122.2641 | 0.17853 | 0.15564 | 0.18768 | -122.3831 | 0.16937 | 0.14191 | 0.21973 | -122.3785
3059.8281 | 122.4655 | -0.027466 | 122.2321 | 0.13245 | 0.044846 | 0.059686 | 0.00062385 | 0.032746 | -0.0028178 | 0.031714 | 0.10559 | 0.028119 | 0.034318 | 0.051592 | 0.0023135 | 0.024368 | 0.082397 | 0.091553 | 0.07782 | 0.064087 | 0.045776 | 0.045776 | -0.07782 | 0.12817 | 0.11902 | 0.022888 | 0.022888 | 0.004578 | -0.013733 | -0.064087 | 0.073242 | -0.050354 | -122.1863 | 0.11902 | 0.091553 | 0.14191 | -122.1497 | 0.013733 | -0.036621 | -122.2092 | 0.15564 | 0.050354 | 0.086975 | -122.2275 | 0.073242 | 0.10986 | 0.10529 | -122.3099 | 0.050354 | 0.032044 | 0.14649 | -122.2961
3061.5781 | 122.4426 | -0.050354 | 122.2137 | -0.14221 | 0.04271 | 0.061182 | 0.0053235 | 0.03296 | -0.0073038 | 0.030433 | -0.054626 | 0.027692 | 0.035387 | 0.051592 | -0.0017453 | 0.023941 | 0.086975 | 0.13275 | 0.11444 | 0.064087 | 0.045776 | 0.073242 | -0.082397 | 0.16022 | 0.19226 | 0.09613 | 0.027466 | 0.004578 | -0.004578 | -0.073242 | 0.1236 | -0.032043 | -122.168 | 0.18311 | 0.11444 | 0.14648 | -122.1268 | 0.045776 | -0.022888 | -122.1863 | 0.21057 | 0.14648 | 0.16937 | -122.2092 | 0.09613 | 0.13733 | 0.16479 | -122.2961 | 0.07782 | 0.054932 | 0.24261 | -122.287
3063.3438 | 122.3053 | -0.09613 | 122.2641 | 0.010376 | 0.047837 | 0.059686 | -0.00044435 | 0.030183 | 0.0025228 | 0.031501 | -0.016479 | 0.028974 | 0.036241 | 0.052233 | 0.0040225 | 0.023941 | 0.018311 | 0 | -0.027466 | -0.018311 | 0.09613 | 0.013733 | -0.1236 | 0.027466 | -0.009155 | -0.10986 | 0.054932 | 0.054932 | -0.068665 | -0.10071 | 0.10986 | -0.027466 | -122.168 | 0.09613 | 0.077819 | 0.10528 | -122.2458 | 0.027465 | -0.004578 | -122.2092 | 0.1236 | -0.013733 | -0.009155 | -122.2092 | 0.19226 | 0.11444 | 0.068664 | -122.3877 | 0.15106 | 0.15106 | 0.086975 | -122.3648
3065.0469 | 122.4426 | -0.059509 | 122.2412 | -0.13458 | 0.043564 | 0.061609 | 0.0048963 | 0.031892 | -0.008372 | 0.028937 | -0.11566 | 0.025983 | 0.0356 | 0.050524 | -0.0021725 | 0.02565 | 0.082397 | 0.17853 | 0.13733 | 0.07782 | 0.041199 | 0.050354 | -0.073242 | 0.13275 | 0.17395 | 0.068665 | 0.022888 | 0 | 0 | -0.07782 | 0.10986 | -0.013733 | -122.2 | 0.23804 | 0.13733 | 0.15106 | -122.1588 | 0.059509 | -0.018311 | -122.2183 | 0.19226 | 0.12817 | 0.14649 | -122.2412 | 0.10071 | 0.14191 | 0.19684 | -122.3145 | 0.082397 | 0.059509 | 0.23346 | -122.319
3066.7969 | 122.374 | -0.07782 | 122.2321 | -0.23376 | 0.043137 | 0.06225 | 0.0072461 | 0.032746 | -0.0073038 | 0.032355 | -0.11566 | 0.029828 | 0.0356 | 0.052019 | -0.0023861 | 0.023513 | 0.073242 | 0.13275 | 0.11902 | 0.073242 | 0.050354 | 0.050354 | -0.073242 | 0.1236 | 0.16022 | 0.041199 | 0.018311 | 0.013733 | -0.004578 | -0.068665 | 0.12817 | 0.004578 | -122.1817 | 0.21057 | 0.15106 | 0.14648 | -122.1588 | 0.073242 | 0.009155 | -122.2137 | 0.20142 | 0.11902 | 0.10986 | -122.2183 | 0.12817 | 0.15106 | 0.19684 | -122.3053 | 0.096131 | 0.091553 | 0.23804 | -122.3007
3068.5625 | 122.3099 | -0.09613 | 122.3007 | -0.081177 | 0.047409 | 0.058405 | 0.00062385 | 0.032105 | 0.0010276 | 0.03321 | -0.085144 | 0.030896 | 0.037523 | 0.052447 | 0.0018863 | 0.022659 | 0.064087 | 0.045776 | 0 | 0.009155 | 0.073242 | 0.027466 | -0.13275 | 0.054932 | 0.027466 | -0.082397 | 0.050354 | 0.041199 | -0.041199 | -0.09613 | 0.1236 | -0.036621 | -122.2275 | 0.14191 | 0.10528 | 0.14191 | -122.2366 | 0.054931 | 0 | -122.2504 | 0.15106 | 0.013733 | 0.013733 | -122.2595 | 0.16937 | 0.16022 | 0.09613 | -122.4335 | 0.14648 | 0.13733 | 0.1236 | -122.3969
3070.3281 | 122.3511 | -0.10986 | 122.2641 | -0.18799 | 0.047409 | 0.062036 | 0.0040417 | 0.030397 | -0.004954 | 0.030006 | -0.26062 | 0.027265 | 0.038805 | 0.051165 | -0.0019589 | 0.025009 | -0.022888 | -0.004578 | -0.032043 | -0.027466 | 0.082397 | 0.004578 | -0.13733 | 0.018311 | 0.018311 | -0.086975 | 0.073242 | 0.041199 | -0.054932 | -0.10071 | 0.11444 | -0.027466 | -122.1817 | 0.10529 | 0.082397 | 0.10986 | -122.287 | 0.054931 | 0.009155 | -122.1909 | 0.12817 | 0.022888 | 0.013733 | -122.2229 | 0.19226 | 0.086975 | 0.07782 | -122.4014 | 0.18311 | 0.15106 | 0.12817 | -122.3648
3072.0156 | 122.4289 | -0.050354 | 122.2092 | 0.14771 | 0.043991 | 0.059686 | 0.0025465 | 0.033387 | -0.0040994 | 0.032355 | 0.16663 | 0.028333 | 0.036241 | 0.050951 | -0.00089089 | 0.025009 | 0.086975 | 0.11902 | 0.10529 | 0.082397 | 0.022888 | 0.068665 | -0.073242 | 0.14191 | 0.11902 | 0.036621 | 0.004578 | -0.004578 | -0.018311 | -0.064087 | 0.11902 | -0.022888 | -122.1863 | 0.16937 | 0.13275 | 0.15564 | -122.1222 | 0.032043 | -0.013733 | -122.2046 | 0.19226 | 0.086975 | 0.10071 | -122.2137 | 0.073242 | 0.13733 | 0.15564 | -122.2824 | 0.054932 | 0.045776 | 0.16937 | -122.2733
3073.7656 | 122.3923 | -0.050354 | 122.2366 | 0.13245 | 0.042923 | 0.0599 | 0.00041005 | 0.031892 | -0.004313 | 0.03086 | 0.12848 | 0.028119 | 0.037309 | 0.051806 | 0.00039091 | 0.023727 | 0.082397 | 0.13733 | 0.11444 | 0.036621 | 0.041199 | 0.073242 | -0.082397 | 0.14648 | 0.11902 | 0.027466 | 0.022888 | -0.004578 | -0.022888 | -0.068665 | 0.1236 | -0.032043 | -122.1954 | 0.18768 | 0.086975 | 0.11902 | -122.1542 | 0.027466 | -0.018311 | -122.2137 | 0.19684 | 0.07782 | 0.096131 | -122.2412 | 0.091553 | 0.13275 | 0.16479 | -122.319 | 0.073242 | 0.045776 | 0.16937 | -122.3053
3075.5312 | 122.3648 | -0.082397 | 122.2916 | -0.11932 | 0.048264 | 0.062036 | 0.00083745 | 0.031892 | 0.00038662 | 0.03086 | -0.13855 | 0.030042 | 0.034105 | 0.050951 | 0.0010317 | 0.023086 | 0.059509 | 0.036621 | 0.004578 | 0.027466 | 0.068665 | 0.032043 | -0.1236 | 0.091553 | 0.064087 | -0.059509 | 0.054932 | 0.032043 | -0.041199 | -0.10071 | 0.11444 | -0.041199 | -122.2229 | 0.11902 | 0.10986 | 0.15106 | -122.2321 | 0.041198 | -0.018311 | -122.2366 | 0.17395 | 0.022888 | 0.041199 | -122.2595 | 0.15106 | 0.14191 | 0.086975 | -122.4152 | 0.13733 | 0.11444 | 0.14648 | -122.3923
3077.2188 | 122.2916 | -0.10529 | 122.2641 | -0.04303 | 0.046555 | 0.062036 | 0.0023329 | 0.032319 | -0.00046778 | 0.032142 | 0.036926 | 0.029828 | 0.037309 | 0.05031 | 0.0035953 | 0.025009 | 0.027466 | 0.009155 | -0.004578 | 0 | 0.07782 | 0.041199 | -0.11444 | 0.027466 | -0.009155 | -0.10529 | 0.059509 | 0.036621 | -0.045776 | -0.1236 | 0.14649 | -0.009155 | -122.1863 | 0.11444 | 0.10529 | 0.11444 | -122.2366 | 0.05951 | -0.01831 | -122.2046 | 0.13275 | 0 | 0.01831 | -122.2275 | 0.18311 | 0.13275 | 0.10071 | -122.3785 | 0.16479 | 0.14191 | 0.096131 | -122.3877
3078.9844 | 122.3282 | -0.086975 | 122.2961 | -0.088806 | 0.0457 | 0.060327 | 0.0048963 | 0.031251 | 0.0016684 | 0.032569 | -0.092773 | 0.030896 | 0.036668 | 0.051378 | 0.0018863 | 0.024154 | 0.054932 | 0.064087 | 0.013733 | 0.032043 | 0.073242 | 0.027466 | -0.10529 | 0.07782 | 0.068665 | -0.064087 | 0.059509 | 0.027466 | -0.036621 | -0.09613 | 0.11444 | -0.018311 | -122.2229 | 0.15106 | 0.11902 | 0.13733 | -122.2412 | 0.050354 | -0.009155 | -122.2366 | 0.16479 | 0.022888 | 0.032043 | -122.2687 | 0.16022 | 0.14191 | 0.10071 | -122.4014 | 0.14648 | 0.11444 | 0.15564 | -122.3923
3080.75 | 122.4289 | -0.059509 | 122.2275 | 0.010376 | 0.04271 | 0.060114 | 0.0038281 | 0.031465 | -0.0096536 | 0.030006 | 0.075073 | 0.028546 | 0.034959 | 0.052019 | -0.0019589 | 0.027786 | 0 | 0.059509 | 0.064087 | 0.022888 | 0.054932 | 0.032043 | -0.09613 | 0.064087 | 0.091553 | 0.004578 | 0.018311 | 0.018311 | -0.027466 | -0.068665 | 0.091552 | -0.036621 | -122.1725 | 0.11902 | 0.082397 | 0.11902 | -122.2275 | 0.032043 | -0.009156 | -122.2092 | 0.1236 | 0.064087 | 0.073243 | -122.2092 | 0.11444 | 0.059509 | 0.1236 | -122.3236 | 0.07782 | 0.07782 | 0.15106 | -122.2961
3082.4375 | 122.3328 | -0.10529 | 122.2504 | -0.31769 | 0.048905 | 0.060541 | 0.0063917 | 0.029328 | -0.0062356 | 0.029151 | -0.19196 | 0.030042 | 0.036882 | 0.050951 | -0.0036679 | 0.02565 | -0.009155 | 0.013733 | -0.004578 | -0.027466 | 0.082397 | 0.018311 | -0.11444 | 0.027466 | 0.036621 | -0.07782 | 0.064087 | 0.059509 | -0.050354 | -0.09613 | 0.1236 | -0.009155 | -122.168 | 0.11902 | 0.07782 | 0.086975 | -122.2595 | 0.054932 | 0.009156 | -122.1863 | 0.13275 | 0.027466 | 0.01831 | -122.1909 | 0.18768 | 0.096131 | 0.10071 | -122.3648 | 0.16937 | 0.16479 | 0.14191 | -122.3465
3084.1875 | 122.4335 | -0.07782 | 122.2412 | -0.17273 | 0.0457 | 0.060968 | 0.0059643 | 0.030824 | -0.0073038 | 0.029151 | -0.15381 | 0.025342 | 0.034959 | 0.051378 | -0.0025999 | 0.025436 | 0.086975 | 0.15106 | 0.11902 | 0.068665 | 0.050354 | 0.064087 | -0.09613 | 0.13275 | 0.1831 | 0.045776 | 0.004578 | 0.022888 | -0.004578 | -0.068665 | 0.14191 | -0.01831 | -122.1909 | 0.22888 | 0.14649 | 0.16479 | -122.1542 | 0.073242 | 0.009155 | -122.2366 | 0.21057 | 0.1236 | 0.11444 | -122.2183 | 0.12817 | 0.16479 | 0.19684 | -122.3373 | 0.082398 | 0.10071 | 0.26092 | -122.3099
3085.8906 | 122.4472 | -0.036621 | 122.2137 | 0.071411 | 0.045487 | 0.059473 | -0.0019397 | 0.03296 | -0.002604 | 0.031928 | 0.11322 | 0.029187 | 0.036027 | 0.051378 | 0.0029543 | 0.02565 | 0.10529 | 0.086975 | 0.082397 | 0.064087 | 0.07782 | 0.059509 | -0.10986 | 0.15106 | 0.11444 | 0.032043 | 0.009155 | -0.009155 | -0.004578 | -0.07782 | 0.09613 | -0.073242 | -122.1359 | 0.1236 | 0.10071 | 0.17395 | -122.1085 | 0.032043 | -0.041199 | -122.2046 | 0.18768 | 0.068664 | 0.10986 | -122.2229 | 0.11444 | 0.14191 | 0.11902 | -122.3236 | 0.045776 | 0.027466 | 0.15106 | -122.2916
3087.6562 | 122.4289 | -0.064087 | 122.2504 | 0.025635 | 0.040573 | 0.062891 | 0.00083745 | 0.031465 | -0.0075174 | 0.026801 | 0.059815 | 0.027265 | 0.034318 | 0.050951 | -0.00067729 | 0.026291 | 0.032043 | 0.082397 | 0.054932 | 0.013733 | 0.059509 | 0.041199 | -0.10529 | 0.091553 | 0.082397 | 0 | 0.018311 | 0.009155 | -0.018311 | -0.068665 | 0.10529 | -0.041199 | -122.1909 | 0.14648 | 0.07782 | 0.11902 | -122.2183 | 0.045776 | -0.004578 | -122.2321 | 0.15564 | 0.064087 | 0.068665 | -122.2412 | 0.1236 | 0.09613 | 0.11902 | -122.3557 | 0.082398 | 0.073242 | 0.14648 | -122.319
3089.3594 | 122.4335 | -0.041199 | 122.2321 | 0.010376 | 0.043778 | 0.061609 | 0.0042555 | 0.03061 | -0.0087992 | 0.031501 | 0.029297 | 0.027692 | 0.035814 | 0.05031 | -0.0013181 | 0.025222 | 0.027466 | 0.032043 | 0.064087 | 0.022888 | 0.045776 | 0.045776 | -0.086975 | 0.07782 | 0.09613 | -0.004578 | 0.032043 | 0.045776 | -0.036621 | -0.068665 | 0.086975 | -0.045776 | -122.1863 | 0.073242 | 0.064087 | 0.10986 | -122.2046 | 0.004578 | -0.027466 | -122.2 | 0.11902 | 0.036621 | 0.064087 | -122.1863 | 0.086975 | 0.068665 | 0.10529 | -122.319 | 0.073242 | 0.086975 | 0.13733 | -122.3007
3091.125 | 122.4838 | -0.050354 | 122.2229 | -0.050659 | 0.045273 | 0.06225 | 0.0051099 | 0.029969 | -0.0051676 | 0.029578 | -0.039368 | 0.027265 | 0.039018 | 0.051378 | -0.0017453 | 0.024154 | 0.041199 | 0.059509 | 0.073242 | 0.036621 | 0.059509 | 0.041199 | -0.091553 | 0.14648 | 0.12817 | 0.041199 | 0.022888 | 0 | -0.013733 | -0.073242 | 0.091553 | -0.041199 | -122.1634 | 0.10986 | 0.086975 | 0.12817 | -122.1817 | 0.036621 | -0.022888 | -122.2 | 0.19684 | 0.091553 | 0.11444 | -122.2229 | 0.10986 | 0.091553 | 0.1236 | -122.3145 | 0.073242 | 0.050354 | 0.17853 | -122.2961
3092.8906 | 122.4335 | -0.064087 | 122.2412 | 0.0027468 | 0.041428 | 0.060114 | 0.0023329 | 0.03296 | -0.0051676 | 0.029792 | 0.044556 | 0.026624 | 0.034105 | 0.051592 | -0.0030271 | 0.024582 | 0.050354 | 0.050354 | 0.059509 | 0.041199 | 0.064087 | 0.041199 | -0.10529 | 0.10071 | 0.07782 | -0.013733 | 0.027466 | 0.022888 | -0.009155 | -0.07782 | 0.10529 | -0.041199 | -122.1771 | 0.11444 | 0.10529 | 0.14649 | -122.1909 | 0.054932 | -0.013733 | -122.2137 | 0.1648 | 0.050354 | 0.064087 | -122.2183 | 0.12817 | 0.11444 | 0.1236 | -122.3465 | 0.091553 | 0.086975 | 0.14191 | -122.319
3094.6875 | 122.4106 | -0.059509 | 122.2366 | 0.14771 | 0.04506 | 0.059045 | 0.00041005 | 0.031892 | -0.0030314 | 0.032142 | 0.12848 | 0.029187 | 0.036668 | 0.051806 | 0.0027407 | 0.023727 | 0.13733 | 0.15106 | 0.12817 | 0.11444 | 0.018311 | 0.054932 | -0.086975 | 0.17853 | 0.1236 | 0.041199 | 0.009155 | -0.013733 | -0.018311 | -0.082397 | 0.11444 | -0.027466 | -122.2183 | 0.21057 | 0.17395 | 0.20142 | -122.0993 | 0.041198 | -0.022888 | -122.2275 | 0.23804 | 0.10071 | 0.1236 | -122.2504 | 0.07782 | 0.19684 | 0.18768 | -122.3236 | 0.068664 | 0.045776 | 0.1831 | -122.319
3096.3906 | 122.3419 | -0.09613 | 122.2366 | 0.063782 | 0.046555 | 0.059686 | -0.0042895 | 0.032105 | 0.0014548 | 0.032355 | -0.024109 | 0.02876 | 0.036027 | 0.050524 | 0.0048769 | 0.021804 | 0.009155 | -0.041199 | -0.050354 | -0.018311 | 0.091553 | 0.032043 | -0.14648 | 0.050354 | -0.009155 | -0.1236 | 0.07782 | 0.032043 | -0.059509 | -0.10986 | 0.12817 | -0.050354 | -122.1451 | 0.054931 | 0.077819 | 0.12817 | -122.2275 | 0.036621 | -0.013733 | -122.1588 | 0.14648 | -0.027466 | -0.013733 | -122.2046 | 0.18768 | 0.10528 | 0.045776 | -122.3831 | 0.17395 | 0.12817 | 0.086975 | -122.3465
3098.1562 | 122.4655 | -0.064087 | 122.2229 | -0.027771 | 0.0457 | 0.061823 | 0.0012647 | 0.031251 | -0.0064492 | 0.030646 | 0.0064086 | 0.026837 | 0.036668 | 0.050097 | -3.629e-05 | 0.023727 | 0.022888 | 0.068665 | 0.064087 | 0.045776 | 0.045776 | 0.041199 | -0.10529 | 0.11902 | 0.11444 | 0.027466 | 0.022888 | 0.018311 | -0.027466 | -0.086975 | 0.10529 | -0.041199 | -122.1771 | 0.13275 | 0.10986 | 0.15106 | -122.2 | 0.036621 | -0.022888 | -122.2 | 0.18311 | 0.091553 | 0.11444 | -122.2046 | 0.10986 | 0.086975 | 0.12817 | -122.3282 | 0.086975 | 0.082398 | 0.17853 | -122.3099
3099.8438 | 122.374 | -0.10071 | 122.2549 | -0.24902 | 0.048477 | 0.060968 | 0.0053235 | 0.033174 | -0.0034586 | 0.030219 | -0.25299 | 0.030683 | 0.038591 | 0.052874 | -0.0013181 | 0.023941 | 0 | -0.018311 | -0.027466 | -0.009155 | 0.09613 | 0.009155 | -0.11902 | 0.036621 | 0.027466 | -0.082397 | 0.054932 | 0.036621 | -0.041199 | -0.10986 | 0.10986 | -0.018311 | -122.1588 | 0.082397 | 0.091553 | 0.10986 | -122.2549 | 0.059509 | -0.009155 | -122.2 | 0.13733 | 0.018311 | 0.027466 | -122.2183 | 0.19684 | 0.10071 | 0.073242 | -122.374 | 0.15564 | 0.13733 | 0.12817 | -122.3648
3101.625 | 122.4289 | -0.059509 | 122.2137 | 0.11719 | 0.043351 | 0.059259 | -0.00023075 | 0.032105 | -0.0011088 | 0.030006 | 0.15137 | 0.029401 | 0.036241 | 0.053087 | 0.0018863 | 0.025863 | 0.10986 | 0.10986 | 0.086975 | 0.07782 | 0.054932 | 0.059509 | -0.064087 | 0.15564 | 0.13275 | 0.032043 | 0.004578 | -0.013733 | -0.004578 | -0.045776 | 0.11902 | -0.004578 | -122.1588 | 0.16937 | 0.13733 | 0.14191 | -122.1039 | 0.054931 | 0.013733 | -122.2092 | 0.21515 | 0.091552 | 0.077819 | -122.2275 | 0.11444 | 0.16937 | 0.14648 | -122.2778 | 0.064087 | 0.045776 | 0.19226 | -122.2595
3103.3125 | 122.4472 | -0.054932 | 122.2366 | -0.14221 | 0.044205 | 0.062891 | 0.0081007 | 0.033174 | -0.0068766 | 0.03086 | -0.1004 | 0.028546 | 0.0356 | 0.052447 | -0.0021725 | 0.026931 | 0.10529 | 0.15564 | 0.12817 | 0.086975 | 0.059509 | 0.068665 | -0.091553 | 0.15106 | 0.16479 | 0.059509 | 0.022888 | 0.009155 | -0.013733 | -0.068665 | 0.1236 | -0.036621 | -122.1771 | 0.21057 | 0.14191 | 0.17853 | -122.1313 | 0.041199 | -0.013733 | -122.2137 | 0.20599 | 0.11444 | 0.12817 | -122.2275 | 0.11444 | 0.16022 | 0.18311 | -122.3282 | 0.07782 | 0.064087 | 0.21973 | -122.3053
3105.0625 | 122.3557 | -0.091553 | 122.2504 | -0.13458 | 0.049973 | 0.059259 | 0.0053235 | 0.03296 | 0.0016684 | 0.028937 | -0.18433 | 0.031323 | 0.038805 | 0.052233 | 0.0018863 | 0.022445 | 0.054932 | 0.027466 | 0.013733 | 0.036621 | 0.073242 | 0.004578 | -0.13275 | 0.086975 | 0.07782 | -0.050354 | 0.068665 | 0.036621 | -0.041199 | -0.10071 | 0.096131 | -0.041198 | -122.1771 | 0.11902 | 0.12817 | 0.16937 | -122.1954 | 0.050354 | -0.009155 | -122.1817 | 0.17853 | 0.041199 | 0.050354 | -122.2137 | 0.16479 | 0.14649 | 0.10529 | -122.3831 | 0.16022 | 0.12817 | 0.16937 | -122.3511
3106.7656 | 122.3648 | -0.091553 | 122.2412 | -0.22614 | 0.045273 | 0.059686 | 0.0016919 | 0.030397 | -0.00089518 | 0.031928 | -0.18433 | 0.02876 | 0.037736 | 0.051806 | -0.00067729 | 0.023727 | 0 | -0.013733 | -0.022888 | -0.018311 | 0.091553 | 0.009155 | -0.12817 | 0.027466 | 0.041199 | -0.086975 | 0.045776 | 0.036621 | -0.068665 | -0.10986 | 0.10071 | -0.036621 | -122.1497 | 0.07782 | 0.073242 | 0.10986 | -122.2412 | 0.022888 | -0.01831 | -122.1954 | 0.11902 | 0.004578 | 0.022888 | -122.2046 | 0.18311 | 0.091553 | 0.068665 | -122.3694 | 0.13733 | 0.12817 | 0.13275 | -122.3511
3108.5156 | 122.3282 | -0.10071 | 122.2595 | -0.23376 | 0.043778 | 0.062036 | 0.0061781 | 0.032105 | -0.0045266 | 0.03086 | -0.1767 | 0.027692 | 0.036882 | 0.052447 | -0.00024989 | 0.024368 | 0.054932 | 0.091553 | 0.073242 | 0.050354 | 0.064087 | 0.027466 | -0.11902 | 0.07782 | 0.09613 | -0.022888 | 0.027466 | 0.022888 | -0.050354 | -0.10071 | 0.12817 | -0.018311 | -122.1954 | 0.19226 | 0.15106 | 0.16937 | -122.2046 | 0.050354 | 0 | -122.2321 | 0.17853 | 0.07782 | 0.07782 | -122.2366 | 0.1648 | 0.15564 | 0.17395 | -122.3785 | 0.12817 | 0.1236 | 0.19684 | -122.3602
3110.2812 | 122.3465 | -0.10529 | 122.2412 | 0.018005 | 0.046555 | 0.060541 | 0.0029737 | 0.033814 | 0.0012412 | 0.031287 | 0.082703 | 0.029401 | 0.037096 | 0.054583 | 0.0025271 | 0.023941 | -0.027466 | -0.050354 | -0.054932 | -0.013733 | 0.091553 | 0.022888 | -0.1236 | 0.036621 | -0.009155 | -0.10071 | 0.041199 | 0.045776 | -0.050354 | -0.09613 | 0.12817 | -0.01831 | -122.1497 | 0.054932 | 0.091553 | 0.10986 | -122.2687 | 0.054932 | 0.009156 | -122.2 | 0.14191 | 0.004578 | -0.004578 | -122.1954 | 0.19684 | 0.07782 | 0.050354 | -122.3648 | 0.14649 | 0.15106 | 0.096131 | -122.3373
3112.0469 | 122.3923 | -0.086975 | 122.2687 | -0.18036 | 0.0457 | 0.06225 | 0.0029737 | 0.032105 | -0.0098672 | 0.030219 | -0.13092 | 0.028974 | 0.037096 | 0.049242 | -0.0023861 | 0.026291 | 0.07782 | 0.14648 | 0.11902 | 0.068665 | 0.036621 | 0.045776 | -0.07782 | 0.13733 | 0.17853 | 0.050354 | 0.004578 | 0.022888 | -0.013733 | -0.050354 | 0.13275 | 0.009155 | -122.2321 | 0.23346 | 0.15564 | 0.14649 | -122.1909 | 0.073242 | 0.036621 | -122.2641 | 0.2243 | 0.13733 | 0.10071 | -122.2458 | 0.1236 | 0.16479 | 0.20599 | -122.3465 | 0.091553 | 0.10986 | 0.2655 | -122.319
3113.75 | 122.4243 | -0.054932 | 122.2412 | -0.1651 | 0.044419 | 0.061609 | 0.0048963 | 0.030824 | -0.0073038 | 0.028724 | -0.13855 | 0.02876 | 0.037523 | 0.050951 | -0.0019589 | 0.026291 | 0.07782 | 0.14648 | 0.12817 | 0.073242 | 0.054932 | 0.041199 | -0.082397 | 0.13733 | 0.17853 | 0.064087 | 0.013733 | -0.004578 | -0.004578 | -0.059509 | 0.096131 | -0.027465 | -122.1863 | 0.20142 | 0.12817 | 0.15564 | -122.1634 | 0.050354 | -0.004577 | -122.2275 | 0.19226 | 0.11902 | 0.1236 | -122.2458 | 0.10986 | 0.13275 | 0.18311 | -122.3236 | 0.068665 | 0.050354 | 0.23346 | -122.3007
3115.5156 | 122.3785 | -0.10529 | 122.2595 | -0.17273 | 0.04805 | 0.060754 | 0.0027601 | 0.031678 | 0.0010276 | 0.031501 | -0.25299 | 0.031537 | 0.036668 | 0.053301 | 0.0010317 | 0.021164 | 0.022888 | -0.009155 | -0.013733 | 0.009155 | 0.073242 | 0.009155 | -0.13275 | 0.068665 | 0.073242 | -0.054932 | 0.054932 | 0.050354 | -0.064087 | -0.082397 | 0.11444 | -0.027465 | -122.1863 | 0.096131 | 0.11444 | 0.14191 | -122.2366 | 0.041199 | 0.022889 | -122.2046 | 0.17395 | 0.050354 | 0.027465 | -122.2092 | 0.17853 | 0.12817 | 0.091553 | -122.3923 | 0.16022 | 0.15564 | 0.17853 | -122.3419
3117.2656 | 122.4609 | -0.068665 | 122.2092 | -0.088806 | 0.044419 | 0.0599 | 0.0029737 | 0.03061 | -0.0087992 | 0.030006 | -0.054626 | 0.026837 | 0.035387 | 0.054156 | -0.0032407 | 0.026504 | 0.068665 | 0.1236 | 0.091553 | 0.054932 | 0.064087 | 0.050354 | -0.09613 | 0.15564 | 0.14648 | 0.073242 | 0.027466 | 0.018311 | 0.004578 | -0.059509 | 0.11902 | -0.027465 | -122.1451 | 0.19226 | 0.1236 | 0.15106 | -122.1405 | 0.073243 | 0.009156 | -122.1817 | 0.22431 | 0.14191 | 0.13275 | -122.1909 | 0.13275 | 0.13733 | 0.16022 | -122.3053 | 0.096131 | 0.086976 | 0.21515 | -122.2687
3119.0156 | 122.4243 | -0.045776 | 122.2321 | -0.11169 | 0.04506 | 0.063318 | 0.0027601 | 0.031251 | -0.0073038 | 0.030433 | -0.13855 | 0.029187 | 0.03795 | 0.052874 | -0.00089089 | 0.023727 | 0.10986 | 0.16479 | 0.13733 | 0.07782 | 0.036621 | 0.036621 | -0.064087 | 0.15106 | 0.17853 | 0.050354 | 0.022888 | -0.018311 | -0.009155 | -0.07782 | 0.082397 | -0.018311 | -122.1954 | 0.21057 | 0.1236 | 0.14191 | -122.1222 | 0.036621 | -0.032044 | -122.2092 | 0.19684 | 0.09613 | 0.12817 | -122.2504 | 0.082397 | 0.15564 | 0.18311 | -122.2961 | 0.068664 | 0.027465 | 0.2243 | -122.3099
3120.7812 | 122.4106 | -0.059509 | 122.2321 | 0.14771 | 0.043778 | 0.058832 | -1.7146e-05 | 0.031251 | -0.0034586 | 0.031287 | 0.12848 | 0.028119 | 0.035387 | 0.052019 | 0.0033817 | 0.023727 | 0.09613 | 0.11902 | 0.11444 | 0.064087 | 0.036621 | 0.050354 | -0.073242 | 0.17395 | 0.14191 | 0.027466 | 0.009155 | 0.009155 | -0.009155 | -0.064087 | 0.10986 | -0.013733 | -122.1954 | 0.17853 | 0.1236 | 0.13733 | -122.1359 | 0.050354 | -0.004578 | -122.2229 | 0.23346 | 0.086975 | 0.091553 | -122.2229 | 0.09613 | 0.15564 | 0.17395 | -122.3053 | 0.068664 | 0.068664 | 0.20142 | -122.2961
3122.4688 | 122.3831 | -0.09613 | 122.2595 | -0.23376 | 0.048691 | 0.061609 | 0.0038281 | 0.031251 | -0.0011088 | 0.032355 | -0.19958 | 0.029187 | 0.039018 | 0.052447 | -0.00046349 | 0.021591 | 0.013733 | -0.018311 | -0.022888 | -0.013733 | 0.10529 | 0.004578 | -0.13275 | 0.036621 | 0.050354 | -0.07782 | 0.064087 | 0.032043 | -0.054932 | -0.09613 | 0.10071 | -0.036621 | -122.1542 | 0.077819 | 0.082397 | 0.11902 | -122.2458 | 0.041198 | 0 | -122.1954 | 0.13275 | 0.01831 | 0.01831 | -122.2275 | 0.20142 | 0.10986 | 0.073242 | -122.3923 | 0.16022 | 0.12817 | 0.14648 | -122.3557
3124.2344 | 122.2916 | -0.10071 | 122.2733 | -0.04303 | 0.047196 | 0.0599 | 0.00041005 | 0.030824 | 0.0010276 | 0.032569 | -0.046997 | 0.03111 | 0.035387 | 0.053942 | 0.0040225 | 0.024154 | 0.050354 | 0.022888 | -0.022888 | 0.022888 | 0.073242 | 0.041199 | -0.11902 | 0.054932 | 0.022888 | -0.10071 | 0.050354 | 0.041199 | -0.036621 | -0.10071 | 0.14191 | -0.018311 | -122.2 | 0.1236 | 0.1236 | 0.14191 | -122.2229 | 0.064087 | 0 | -122.2229 | 0.15564 | 0 | 0 | -122.2321 | 0.17395 | 0.15106 | 0.07782 | -122.3923 | 0.15106 | 0.14191 | 0.1236 | -122.374
3126 | 122.4701 | -0.032043 | 122.2137 | 0.14008 | 0.04805 | 0.060754 | 0.0021191 | 0.031678 | -0.0034586 | 0.033423 | 0.13611 | 0.029828 | 0.039232 | 0.052233 | 0.0014591 | 0.026291 | 0.022888 | 0.013733 | 0.009155 | 0.009155 | 0.068665 | 0.032043 | -0.10986 | 0.1236 | 0.086975 | -0.009155 | 0.027466 | 0.018311 | -0.018311 | -0.10071 | 0.064086 | -0.07782 | -122.1451 | 0.045776 | 0.041198 | 0.11902 | -122.1909 | 0.013732 | -0.068665 | -122.1863 | 0.15564 | 0.022888 | 0.091553 | -122.1954 | 0.10071 | 0.054931 | 0.041198 | -122.3236 | 0.059509 | 0.050354 | 0.11902 | -122.3145
3127.7031 | 122.4243 | -0.059509 | 122.2549 | 0.094299 | 0.041428 | 0.064386 | 0.0016919 | 0.02826 | -0.0070902 | 0.030646 | 0.14374 | 0.027692 | 0.036241 | 0.051378 | 0.00081811 | 0.026504 | 0.059509 | 0.11444 | 0.086975 | 0.054932 | 0.041199 | 0.050354 | -0.082397 | 0.11902 | 0.10529 | 0.004578 | 0.013733 | 0.009155 | -0.036621 | -0.059509 | 0.10986 | -0.022888 | -122.2137 | 0.17395 | 0.11444 | 0.13733 | -122.1954 | 0.022888 | 0 | -122.2412 | 0.17853 | 0.064087 | 0.064087 | -122.2458 | 0.10071 | 0.11902 | 0.14648 | -122.3373 | 0.073242 | 0.068664 | 0.16479 | -122.3145
3129.4531 | 122.4106 | -0.064087 | 122.2321 | 0.079041 | 0.043351 | 0.062891 | 0.0031873 | 0.030397 | -0.0055948 | 0.03086 | 0.15137 | 0.028333 | 0.035814 | 0.049883 | 0.0014591 | 0.025863 | 0.082397 | 0.1236 | 0.09613 | 0.036621 | 0.059509 | 0.050354 | -0.073242 | 0.13275 | 0.10986 | 0.022888 | 0.018311 | -0.004578 | -0.009155 | -0.091553 | 0.11444 | -0.009155 | -122.1725 | 0.18768 | 0.10071 | 0.10986 | -122.1497 | 0.054932 | -0.027466 | -122.2137 | 0.19684 | 0.086975 | 0.11444 | -122.2366 | 0.1236 | 0.14648 | 0.16022 | -122.3053 | 0.082398 | 0.059509 | 0.17395 | -122.3236
3131.2188 | 122.3282 | -0.10986 | 122.2549 | -0.24902 | 0.044846 | 0.063959 | 0.0059643 | 0.033814 | -0.0051676 | 0.030006 | -0.19958 | 0.027265 | 0.036882 | 0.052019 | -0.0013181 | 0.024368 | 0.041199 | 0.064087 | 0.027466 | 0.032043 | 0.064087 | 0.032043 | -0.10071 | 0.041199 | 0.045776 | -0.045776 | 0.041199 | 0.027466 | -0.050354 | -0.091553 | 0.14191 | 0.009155 | -122.1909 | 0.17395 | 0.14191 | 0.13275 | -122.2137 | 0.059509 | 0.01831 | -122.2137 | 0.15106 | 0.064087 | 0.045777 | -122.2275 | 0.17395 | 0.15106 | 0.13733 | -122.3557 | 0.15106 | 0.13733 | 0.15564 | -122.3465
3132.9844 | 122.319 | -0.09613 | 122.2595 | -0.26428 | 0.046768 | 0.060968 | 0.0072461 | 0.031037 | -0.002604 | 0.031287 | -0.19196 | 0.029401 | 0.038805 | 0.054369 | -0.0019589 | 0.024154 | 0.022888 | 0.064087 | 0.041199 | 0.027466 | 0.059509 | 0.018311 | -0.12817 | 0.036621 | 0.054932 | -0.041199 | 0.059509 | 0.045776 | -0.059509 | -0.09613 | 0.11444 | -0.032044 | -122.2 | 0.16022 | 0.1236 | 0.15564 | -122.2366 | 0.036621 | 0 | -122.2 | 0.13275 | 0.054931 | 0.054931 | -122.2137 | 0.15564 | 0.11902 | 0.13733 | -122.3877 | 0.15564 | 0.14191 | 0.15106 | -122.3557
3134.75 | 122.4335 | -0.07782 | 122.2321 | 0.010376 | 0.04271 | 0.06225 | 0.0027601 | 0.031892 | -0.0070902 | 0.030433 | 0.029297 | 0.027906 | 0.035173 | 0.052019 | -0.0032407 | 0.024582 | 0.032043 | 0.064087 | 0.050354 | 0.027466 | 0.050354 | 0.045776 | -0.09613 | 0.10529 | 0.091553 | 0.004578 | 0.032043 | 0.022888 | -0.004578 | -0.07782 | 0.1236 | -0.01831 | -122.1817 | 0.14191 | 0.10529 | 0.1236 | -122.2 | 0.073242 | 0 | -122.2 | 0.18311 | 0.082398 | 0.082398 | -122.2092 | 0.12817 | 0.10986 | 0.12817 | -122.3282 | 0.10986 | 0.10071 | 0.16937 | -122.3099
3136.5156 | 122.3236 | -0.10071 | 122.2733 | -0.027771 | 0.047623 | 0.059473 | 0.0021191 | 0.030397 | 0.0027364 | 0.03086 | -0.069885 | 0.029401 | 0.035173 | 0.052447 | 0.0059451 | 0.023727 | 0.059509 | 0.018311 | -0.004578 | 0.018311 | 0.086975 | 0.018311 | -0.11902 | 0.041199 | 0.018311 | -0.09613 | 0.059509 | 0.050354 | -0.041199 | -0.10986 | 0.11902 | -0.018311 | -122.1863 | 0.11902 | 0.11902 | 0.13733 | -122.2137 | 0.059509 | -0.009155 | -122.2137 | 0.14191 | 0.004578 | 0.013733 | -122.2229 | 0.18768 | 0.16022 | 0.09613 | -122.3923 | 0.16022 | 0.15106 | 0.11902 | -122.3831
3138.2031 | 122.4564 | -0.036621 | 122.2092 | 0.14008 | 0.047623 | 0.060114 | 0.0016919 | 0.030824 | -0.0019632 | 0.032783 | 0.075073 | 0.028119 | 0.035173 | 0.05266 | 0.0029543 | 0.025436 | 0.045776 | 0.068665 | 0.045776 | 0.027466 | 0.064087 | 0.041199 | -0.10071 | 0.13733 | 0.10071 | 0.018311 | 0.004578 | 0 | -0.022888 | -0.068665 | 0.07782 | -0.064087 | -122.1451 | 0.10529 | 0.064087 | 0.12817 | -122.1634 | 0.013733 | -0.032044 | -122.2046 | 0.17395 | 0.054932 | 0.086976 | -122.2092 | 0.10071 | 0.082397 | 0.082397 | -122.3099 | 0.041199 | 0.036621 | 0.13733 | -122.2778
3139.9531 | 122.3557 | -0.073242 | 122.2504 | -0.11169 | 0.048264 | 0.060541 | 0.0014783 | 0.030824 | 0.0010276 | 0.031287 | -0.13855 | 0.02876 | 0.0356 | 0.053942 | 0.0023135 | 0.021591 | 0.045776 | 0.041199 | 0.013733 | 0.018311 | 0.07782 | 0.013733 | -0.10529 | 0.086975 | 0.07782 | -0.045776 | 0.032043 | 0.041199 | -0.032043 | -0.10529 | 0.086975 | -0.032044 | -122.1725 | 0.11444 | 0.091553 | 0.1236 | -122.2046 | 0.041199 | -0.032044 | -122.2183 | 0.16022 | 0.027466 | 0.05951 | -122.2092 | 0.15106 | 0.11902 | 0.086975 | -122.3557 | 0.10529 | 0.11444 | 0.15106 | -122.3557
3141.7188 | 122.493 | -0.045776 | 122.2137 | -0.04303 | 0.043137 | 0.063318 | 0.0029737 | 0.033174 | -0.0096536 | 0.029792 | -0.031738 | 0.027478 | 0.03795 | 0.050738 | -0.0032407 | 0.027359 | 0.009155 | 0.09613 | 0.082397 | 0.036621 | 0.054932 | 0.041199 | -0.11444 | 0.10986 | 0.13733 | 0.045776 | 0.022888 | 0 | -0.027466 | -0.064087 | 0.086975 | -0.068665 | -122.1588 | 0.14191 | 0.082397 | 0.15106 | -122.2046 | 0.01831 | -0.018311 | -122.1909 | 0.15564 | 0.091552 | 0.10986 | -122.2137 | 0.10071 | 0.054931 | 0.12817 | -122.3282 | 0.068664 | 0.045776 | 0.18311 | -122.2778
3143.4062 | 122.3694 | -0.09613 | 122.2458 | -0.21851 | 0.047409 | 0.063104 | 0.0068189 | 0.029969 | -0.0038858 | 0.031074 | -0.24536 | 0.02876 | 0.03795 | 0.054156 | -0.0013181 | 0.0233 | -0.004578 | 0 | -0.009155 | -0.009155 | 0.086975 | 0.022888 | -0.11902 | 0.022888 | 0.032043 | -0.09613 | 0.050354 | 0.045776 | -0.054932 | -0.09613 | 0.11902 | -0.022889 | -122.1588 | 0.09613 | 0.086975 | 0.10986 | -122.2504 | 0.041198 | 0 | -122.1954 | 0.11902 | 0 | 0 | -122.2 | 0.1831 | 0.091552 | 0.086975 | -122.3648 | 0.14648 | 0.14191 | 0.12817 | -122.3419
3145.1562 | 122.3282 | -0.10986 | 122.2595 | -0.23376 | 0.047623 | 0.06225 | 0.0025465 | 0.032746 | -0.0030314 | 0.032569 | -0.24536 | 0.029615 | 0.040086 | 0.05501 | -0.0017453 | 0.0233 | -0.022888 | 0.018311 | -0.009155 | -0.004578 | 0.086975 | 0.027466 | -0.12817 | 0.032043 | 0.022888 | -0.07782 | 0.068665 | 0.045776 | -0.082397 | -0.09613 | 0.13733 | -0.018311 | -122.1725 | 0.12817 | 0.10529 | 0.1236 | -122.2824 | 0.027466 | 0.013733 | -122.1909 | 0.14191 | 0.032043 | 0.01831 | -122.2137 | 0.19684 | 0.086975 | 0.10071 | -122.3877 | 0.17853 | 0.15564 | 0.13275 | -122.3557
3146.9062 | 122.3877 | -0.064087 | 122.2458 | -0.19562 | 0.044205 | 0.061823 | 0.0027601 | 0.03061 | -0.0058084 | 0.03086 | -0.15381 | 0.027692 | 0.033464 | 0.05266 | -0.00046349 | 0.024795 | 0.086975 | 0.14191 | 0.10986 | 0.073242 | 0.036621 | 0.041199 | -0.082397 | 0.11902 | 0.19684 | 0.041199 | 0.009155 | 0.009155 | -0.036621 | -0.073242 | 0.10529 | -0.01831 | -122.2092 | 0.20599 | 0.13733 | 0.15564 | -122.1588 | 0.027466 | -0.009155 | -122.2366 | 0.18311 | 0.10529 | 0.11444 | -122.2366 | 0.10071 | 0.15106 | 0.17395 | -122.3282 | 0.073242 | 0.073242 | 0.26093 | -122.319
3148.6094 | 122.4014 | -0.073242 | 122.2275 | 0.056152 | 0.041428 | 0.063104 | -0.00023075 | 0.032319 | -0.0064492 | 0.032142 | 0.097962 | 0.026197 | 0.034318 | 0.053087 | 0.00039091 | 0.022873 | 0.041199 | 0.07782 | 0.064087 | 0.027466 | 0.064087 | 0.059509 | -0.082397 | 0.10071 | 0.091553 | 0.004578 | 0.018311 | 0 | -0.027466 | -0.082397 | 0.13275 | -0.009155 | -122.1634 | 0.15106 | 0.10071 | 0.10986 | -122.1863 | 0.045776 | -0.009155 | -122.2092 | 0.17395 | 0.07782 | 0.086975 | -122.2275 | 0.13733 | 0.11444 | 0.13733 | -122.3099 | 0.091553 | 0.073242 | 0.16479 | -122.3099
3150.375 | 122.4152 | -0.064087 | 122.2366 | 0.040894 | 0.044419 | 0.060754 | 0.0029737 | 0.031465 | -0.004954 | 0.030646 | 0.082703 | 0.025983 | 0.039232 | 0.052233 | -0.0013181 | 0.023941 | 0.032043 | 0.073242 | 0.073242 | 0.032043 | 0.068665 | 0.054932 | -0.086975 | 0.09613 | 0.091553 | -0.009155 | 0.036621 | 0.004578 | -0.018311 | -0.082397 | 0.11902 | -0.022888 | -122.168 | 0.13733 | 0.09613 | 0.11902 | -122.2046 | 0.045776 | -0.01831 | -122.2 | 0.16022 | 0.054932 | 0.073242 | -122.2321 | 0.13275 | 0.09613 | 0.13733 | -122.3236 | 0.10071 | 0.068665 | 0.15564 | -122.319
3152.1562 | 122.4152 | -0.054932 | 122.2321 | 0.17059 | 0.045487 | 0.060327 | 0.0029737 | 0.031465 | -0.0013224 | 0.029792 | 0.13611 | 0.02876 | 0.03795 | 0.056292 | -3.629e-05 | 0.024154 | 0.10071 | 0.11902 | 0.10529 | 0.082397 | 0.032043 | 0.054932 | -0.082397 | 0.15564 | 0.13733 | 0.032043 | 0.004578 | 0.009155 | -0.013733 | -0.064087 | 0.10986 | -0.027465 | -122.2 | 0.17395 | 0.13733 | 0.16479 | -122.1313 | 0.041199 | -0.009155 | -122.2275 | 0.21057 | 0.086975 | 0.09613 | -122.2229 | 0.086975 | 0.15564 | 0.16022 | -122.3145 | 0.05951 | 0.064087 | 0.19226 | -122.2961
3153.8438 | 122.4518 | -0.050354 | 122.2321 | -0.14221 | 0.04506 | 0.062677 | 0.0021191 | 0.031678 | -0.0064492 | 0.028937 | -0.085144 | 0.027265 | 0.034959 | 0.051592 | -0.0011045 | 0.024154 | 0.10986 | 0.15106 | 0.10071 | 0.068665 | 0.032043 | 0.045776 | -0.086975 | 0.17395 | 0.17395 | 0.068665 | 0.004578 | 0 | -0.009155 | -0.064087 | 0.09613 | -0.036621 | -122.2 | 0.20142 | 0.11902 | 0.15564 | -122.1222 | 0.041199 | -0.013733 | -122.2275 | 0.2243 | 0.11902 | 0.13275 | -122.2321 | 0.082397 | 0.16022 | 0.15106 | -122.319 | 0.054932 | 0.050354 | 0.2243 | -122.2961
3155.5938 | 122.3373 | -0.082397 | 122.2549 | -0.18036 | 0.046768 | 0.060541 | 0.0053235 | 0.030824 | -0.0045266 | 0.028937 | -0.18433 | 0.027906 | 0.037736 | 0.05031 | -0.0015317 | 0.023513 | 0.091553 | 0.1236 | 0.10529 | 0.064087 | 0.041199 | 0.036621 | -0.086975 | 0.12817 | 0.15564 | 0.018311 | 0.022888 | 0.013733 | -0.027466 | -0.068665 | 0.11902 | -0.004578 | -122.2137 | 0.20599 | 0.14648 | 0.15106 | -122.1634 | 0.054931 | 0.013732 | -122.2321 | 0.21057 | 0.10071 | 0.086976 | -122.2412 | 0.1236 | 0.17395 | 0.18768 | -122.3419 | 0.10528 | 0.09613 | 0.23804 | -122.3236
3157.3594 | 122.3099 | -0.10529 | 122.2641 | -0.020142 | 0.044632 | 0.058832 | -0.00065795 | 0.031465 | 0.004659 | 0.032783 | -0.10803 | 0.03111 | 0.035173 | 0.052019 | 0.0059451 | 0.023513 | 0.059509 | 0.022888 | -0.004578 | 0.004578 | 0.09613 | 0.009155 | -0.11902 | 0.041199 | 0.013733 | -0.10529 | 0.064087 | 0.050354 | -0.036621 | -0.10529 | 0.11444 | -0.013733 | -122.168 | 0.12817 | 0.10986 | 0.1236 | -122.2046 | 0.068665 | 0 | -122.2 | 0.14649 | 0 | 0 | -122.2137 | 0.20142 | 0.16479 | 0.10071 | -122.3831 | 0.16937 | 0.15564 | 0.11902 | -122.3694
3159.0625 | 122.4289 | -0.054932 | 122.2458 | 0.14771 | 0.043778 | 0.060541 | -1.7146e-05 | 0.029115 | -0.0047404 | 0.036201 | 0.14374 | 0.02876 | 0.035814 | 0.050097 | 0.0018863 | 0.024154 | 0.10071 | 0.13733 | 0.10986 | 0.073242 | 0.036621 | 0.050354 | -0.082397 | 0.16479 | 0.14648 | 0.036621 | 0.009155 | -0.009155 | 0 | -0.068665 | 0.10529 | -0.027465 | -122.2092 | 0.19226 | 0.12817 | 0.15564 | -122.1451 | 0.054932 | -0.013733 | -122.2366 | 0.21973 | 0.091553 | 0.10529 | -122.2549 | 0.091553 | 0.15564 | 0.16479 | -122.3282 | 0.064087 | 0.045777 | 0.20142 | -122.3145
3160.8281 | 122.3145 | -0.09613 | 122.2778 | -0.058289 | 0.047409 | 0.060541 | 0.0034009 | 0.032533 | 0.0020956 | 0.032569 | -0.092773 | 0.032178 | 0.034105 | 0.051165 | 0.0040225 | 0.024368 | 0.059509 | 0.045776 | 0.013733 | 0.018311 | 0.07782 | 0.027466 | -0.1236 | 0.064087 | 0.036621 | -0.082397 | 0.050354 | 0.027466 | -0.050354 | -0.09613 | 0.1236 | -0.027466 | -122.2 | 0.14191 | 0.11444 | 0.14191 | -122.2183 | 0.045776 | 0 | -122.2275 | 0.16022 | 0.013733 | 0.013733 | -122.2504 | 0.17395 | 0.15564 | 0.10986 | -122.4014 | 0.14648 | 0.1236 | 0.13275 | -122.374
3162.5938 | 122.3328 | -0.10529 | 122.2778 | -0.13458 | 0.048477 | 0.06225 | 0.0078871 | 0.031678 | -0.0030314 | 0.030219 | -0.22247 | 0.027906 | 0.038377 | 0.050738 | -0.0021725 | 0.026718 | -0.013733 | 0.013733 | -0.013733 | -0.013733 | 0.07782 | 0.004578 | -0.13733 | 0.027466 | 0.032043 | -0.07782 | 0.064087 | 0.036621 | -0.054932 | -0.10986 | 0.10986 | -0.032043 | -122.2 | 0.11902 | 0.091553 | 0.1236 | -122.2916 | 0.050354 | -0.004577 | -122.2137 | 0.13275 | 0.027466 | 0.032043 | -122.2412 | 0.18311 | 0.091553 | 0.091553 | -122.4152 | 0.16937 | 0.14191 | 0.13733 | -122.3877
3164.3594 | 122.3236 | -0.10529 | 122.2412 | -0.058289 | 0.046341 | 0.059259 | 0.0029737 | 0.032319 | -0.00068138 | 0.033851 | -0.069885 | 0.030042 | 0.03795 | 0.053728 | 0.0023135 | 0.023941 | 0.032043 | 0.045776 | 0.013733 | 0.027466 | 0.07782 | 0.027466 | -0.11444 | 0.059509 | 0.041199 | -0.07782 | 0.041199 | 0.045776 | -0.050354 | -0.10071 | 0.13275 | -0.009155 | -122.1634 | 0.15106 | 0.13275 | 0.14191 | -122.2092 | 0.054932 | 0.004578 | -122.2 | 0.16479 | 0.027466 | 0.022888 | -122.1954 | 0.18311 | 0.13733 | 0.11902 | -122.3557 | 0.14649 | 0.15106 | 0.14649 | -122.3419
3166.1094 | 122.3373 | -0.10986 | 122.2549 | -0.21088 | 0.047196 | 0.062036 | 0.0070325 | 0.033174 | -0.0058084 | 0.031928 | -0.1767 | 0.028119 | 0.038805 | 0.051165 | -0.0030271 | 0.024582 | 0.032043 | 0.12817 | 0.091553 | 0.073242 | 0.059509 | 0.032043 | -0.10529 | 0.10071 | 0.15106 | 0.004578 | 0.027466 | 0.022888 | -0.027466 | -0.091553 | 0.14191 | 0.004577 | -122.1954 | 0.23804 | 0.18311 | 0.17853 | -122.2229 | 0.082397 | 0.01831 | -122.2275 | 0.21057 | 0.11444 | 0.096131 | -122.2321 | 0.16937 | 0.14191 | 0.20142 | -122.3602 | 0.13733 | 0.13275 | 0.26093 | -122.3465
3167.8125 | 122.4152 | -0.054932 | 122.2321 | 0.13245 | 0.044419 | 0.060327 | 0.0025465 | 0.031678 | -0.006022 | 0.032355 | 0.12085 | 0.027692 | 0.036882 | 0.052447 | 0.0014591 | 0.026291 | 0.07782 | 0.13733 | 0.10529 | 0.054932 | 0.054932 | 0.064087 | -0.091553 | 0.13733 | 0.13275 | 0.036621 | 0.009155 | -0.013733 | -0.013733 | -0.086975 | 0.11902 | -0.036621 | -122.1771 | 0.19226 | 0.10986 | 0.14649 | -122.1542 | 0.041199 | -0.032043 | -122.2229 | 0.19226 | 0.091553 | 0.1236 | -122.2458 | 0.10986 | 0.13275 | 0.16022 | -122.3236 | 0.064087 | 0.041199 | 0.18768 | -122.319
3169.5781 | 122.4152 | -0.082397 | 122.2366 | 0.10193 | 0.042282 | 0.060754 | 0.0016919 | 0.029969 | -0.006022 | 0.030646 | 0.10559 | 0.028974 | 0.036241 | 0.05266 | -0.00024989 | 0.025436 | 0.045776 | 0.086975 | 0.068665 | 0.036621 | 0.045776 | 0.054932 | -0.073242 | 0.10529 | 0.082397 | 0.004578 | 0.022888 | 0.013733 | -0.009155 | -0.07782 | 0.13733 | 0.009155 | -122.1909 | 0.16937 | 0.11902 | 0.10986 | -122.1909 | 0.073242 | 0.004577 | -122.2137 | 0.18768 | 0.086975 | 0.082398 | -122.2229 | 0.12817 | 0.12817 | 0.15106 | -122.3099 | 0.10528 | 0.09613 | 0.16479 | -122.3145
3171.3438 | 122.374 | -0.068665 | 122.2458 | -0.12695 | 0.052964 | 0.060754 | 0.0081007 | 0.029115 | 0.001882 | 0.031287 | -0.19196 | 0.028333 | 0.039018 | 0.055437 | 0.00081811 | 0.021164 | 0.045776 | 0.032043 | 0.022888 | 0.032043 | 0.082397 | 0.013733 | -0.1236 | 0.086975 | 0.064087 | -0.050354 | 0.050354 | 0.036621 | -0.022888 | -0.10071 | 0.082398 | -0.054931 | -122.1634 | 0.10071 | 0.10071 | 0.15564 | -122.2 | 0.045777 | -0.032043 | -122.1954 | 0.15564 | 0.018311 | 0.050354 | -122.2092 | 0.15106 | 0.11444 | 0.091553 | -122.3694 | 0.11902 | 0.10529 | 0.13275 | -122.3465
3173.1094 | 122.4197 | -0.050354 | 122.2183 | 0.10956 | 0.046982 | 0.060327 | -0.0019397 | 0.030824 | -0.0013224 | 0.03086 | 0.052185 | 0.030896 | 0.034532 | 0.052233 | 0.0029543 | 0.026077 | -0.013733 | -0.004578 | -0.050354 | -0.018311 | 0.082397 | 0.027466 | -0.11902 | 0.041199 | 0.009155 | -0.07782 | 0.050354 | 0.036621 | -0.045776 | -0.10071 | 0.07782 | -0.068665 | -122.1359 | 0.045776 | 0.032043 | 0.10071 | -122.2321 | 0.004578 | -0.050354 | -122.168 | 0.091553 | -0.027466 | 0.022888 | -122.1817 | 0.13275 | 0.036621 | 0 | -122.3373 | 0.10071 | 0.086975 | 0.059509 | -122.319
3174.7969 | 122.4609 | -0.054932 | 122.2412 | -0.020142 | 0.043137 | 0.060327 | 0.0023329 | 0.03061 | -0.0087992 | 0.031501 | 0.052185 | 0.030255 | 0.036241 | 0.051378 | -0.0028135 | 0.02565 | -0.004578 | 0.064087 | 0.054932 | 0.032043 | 0.064087 | 0.059509 | -0.10071 | 0.091553 | 0.09613 | 0.013733 | 0.027466 | 0.004578 | -0.013733 | -0.073242 | 0.11444 | -0.045776 | -122.1771 | 0.11902 | 0.086975 | 0.13275 | -122.2458 | 0.041199 | -0.01831 | -122.2137 | 0.14649 | 0.068665 | 0.086975 | -122.2366 | 0.11902 | 0.050354 | 0.10986 | -122.3419 | 0.082398 | 0.05951 | 0.15106 | -122.3145
3176.5625 | 122.3602 | -0.09613 | 122.2595 | -0.20325 | 0.04506 | 0.060968 | 0.0040417 | 0.029542 | -0.0064492 | 0.02851 | -0.11566 | 0.027265 | 0.036027 | 0.051806 | -0.0023861 | 0.024368 | 0.082397 | 0.13733 | 0.10529 | 0.059509 | 0.050354 | 0.041199 | -0.10071 | 0.11902 | 0.15564 | 0.032043 | 0.004578 | 0.009155 | -0.013733 | -0.073242 | 0.13733 | -0.004578 | -122.2092 | 0.23346 | 0.15564 | 0.16022 | -122.1771 | 0.082397 | 0.022888 | -122.2549 | 0.21515 | 0.12817 | 0.10529 | -122.2504 | 0.14648 | 0.17853 | 0.20142 | -122.3602 | 0.10071 | 0.10528 | 0.25177 | -122.3328
3178.2656 | 122.3419 | -0.10529 | 122.2687 | -0.020142 | 0.046768 | 0.059045 | -0.00044435 | 0.030824 | 0.0020956 | 0.030646 | -0.0088499 | 0.030042 | 0.037096 | 0.054583 | 0.0044497 | 0.0233 | -0.004578 | -0.041199 | -0.059509 | -0.027466 | 0.07782 | 0.009155 | -0.10986 | 0.004578 | -0.009155 | -0.1236 | 0.068665 | 0.027466 | -0.050354 | -0.10529 | 0.11444 | -0.004577 | -122.1909 | 0.064087 | 0.07782 | 0.082397 | -122.2733 | 0.054932 | 0 | -122.2 | 0.10986 | -0.01831 | -0.01831 | -122.2412 | 0.18311 | 0.10071 | 0.045777 | -122.3785 | 0.17395 | 0.13275 | 0.096131 | -122.374
3180.0312 | 122.4976 | -0.091553 | 122.2321 | -0.23376 | 0.045914 | 0.061823 | 0.0063917 | 0.029542 | -0.00089518 | 0.030006 | -0.20721 | 0.028333 | 0.037309 | 0.054156 | -0.0015317 | 0.0233 | 0 | 0.07782 | -0.013733 | 0.15106 | 0.091553 | 0.004578 | -0.12817 | 0.032043 | 0.07782 | -0.041199 | 0.054932 | 0.032043 | -0.054932 | -0.11902 | 0.096131 | -0.036621 | -122.1405 | 0.16937 | 0.24261 | 0.27924 | -122.2321 | 0.036621 | -0.027466 | -122.1771 | 0.1236 | 0.050354 | 0.07782 | -122.2 | 0.18311 | 0.091553 | 0.07782 | -122.3602 | 0.14649 | 0.1236 | 0.16937 | -122.3511
3181.7969 | 122.4518 | -0.10986 | 122.2687 | 0.033264 | 0.047196 | 0.060968 | 0.0010511 | 0.033814 | -4.058e-05 | 0.035132 | -0.016479 | 0.031751 | 0.037523 | 0.05266 | 0.0027407 | 0.026718 | 0.013733 | 0.041199 | -0.032043 | 0.11444 | 0.07782 | 0.027466 | -0.12817 | 0.004578 | 0.004578 | -0.09613 | 0.059509 | 0.045776 | -0.032043 | -0.10529 | 0.13733 | -0.018311 | -122.1909 | 0.15106 | 0.2243 | 0.24262 | -122.2549 | 0.07782 | 0.004577 | -122.2092 | 0.11444 | 0.013733 | 0.009156 | -122.2229 | 0.18768 | 0.1236 | 0.07782 | -122.3969 | 0.16937 | 0.15564 | 0.11444 | -122.374
3183.5 | 122.374 | -0.09613 | 122.2641 | -0.22614 | 0.048691 | 0.06225 | 0.0044691 | 0.032533 | -0.0040994 | 0.030646 | -0.19958 | 0.029187 | 0.037096 | 0.050097 | -0.0021725 | 0.023941 | -0.022888 | -0.004578 | -0.027466 | -0.018311 | 0.10071 | 0.004578 | -0.12817 | 0.022888 | 0.032043 | -0.082397 | 0.059509 | 0.059509 | -0.054932 | -0.091553 | 0.10071 | -0.032044 | -122.1634 | 0.091552 | 0.077819 | 0.10986 | -122.287 | 0.041198 | 0.004577 | -122.2046 | 0.11902 | 0.013733 | 0.009156 | -122.2046 | 0.19684 | 0.073242 | 0.068664 | -122.3923 | 0.15564 | 0.15564 | 0.12817 | -122.3557
3185.2656 | 122.3419 | -0.091553 | 122.2687 | -0.088806 | 0.0457 | 0.059473 | -0.0017261 | 0.03061 | -0.0011088 | 0.031501 | -0.13092 | 0.030255 | 0.036455 | 0.054156 | 0.00060451 | 0.025863 | 0.032043 | 0.045776 | 0.041199 | 0.032043 | 0.059509 | 0.018311 | -0.11444 | 0.07782 | 0.082397 | -0.045776 | 0.027466 | 0.027466 | -0.027466 | -0.091553 | 0.10986 | -0.022888 | -122.2092 | 0.13733 | 0.1236 | 0.14648 | -122.2366 | 0.064087 | 0 | -122.2412 | 0.16937 | 0.045777 | 0.045777 | -122.2412 | 0.15106 | 0.1236 | 0.13275 | -122.3831 | 0.11902 | 0.11902 | 0.17395 | -122.3602
3186.9688 | 122.3785 | -0.10071 | 122.2824 | -0.18036 | 0.045914 | 0.062463 | 0.0057507 | 0.032533 | -0.0017496 | 0.032142 | -0.19196 | 0.029615 | 0.036882 | 0.052233 | 0.0016727 | 0.02565 | -0.022888 | -0.009155 | -0.032043 | 0.013733 | 0.082397 | 0.009155 | -0.13733 | 0.018311 | 0.068665 | -0.054932 | 0.041199 | 0.064087 | -0.050354 | -0.10071 | 0.10986 | -0.036621 | -122.2 | 0.091553 | 0.11444 | 0.15106 | -122.3053 | 0.050354 | 0 | -122.2412 | 0.11902 | 0.045776 | 0.045776 | -122.2183 | 0.18311 | 0.07782 | 0.068665 | -122.4197 | 0.14191 | 0.1648 | 0.16937 | -122.3831
3188.7188 | 122.3236 | -0.09613 | 122.2824 | -0.050659 | 0.048477 | 0.0599 | 0.0014783 | 0.031892 | 0.00017302 | 0.034492 | -0.031738 | 0.030042 | 0.037736 | 0.050951 | 0.0016727 | 0.023513 | 0.027466 | 0.041199 | 0.004578 | 0.018311 | 0.07782 | 0.022888 | -0.13275 | 0.032043 | 0.032043 | -0.091553 | 0.041199 | 0.045776 | -0.041199 | -0.086975 | 0.11902 | -0.036621 | -122.2046 | 0.13733 | 0.11444 | 0.15106 | -122.2549 | 0.054931 | 0.009155 | -122.2412 | 0.12817 | 0.004577 | -0.004578 | -122.2366 | 0.17395 | 0.1236 | 0.10071 | -122.4152 | 0.13733 | 0.14191 | 0.12817 | -122.3694
3190.4688 | 122.4243 | -0.045776 | 122.2366 | 0.14771 | 0.04506 | 0.060327 | 0.0019055 | 0.031892 | -0.0070902 | 0.033851 | 0.17426 | 0.029828 | 0.035387 | 0.053087 | 0.00039091 | 0.026931 | 0.073242 | 0.1236 | 0.09613 | 0.082397 | 0.027466 | 0.036621 | -0.086975 | 0.14648 | 0.13733 | 0.054932 | 0.009155 | -0.013733 | -0.009155 | -0.068665 | 0.082397 | -0.041199 | -122.2092 | 0.16937 | 0.12817 | 0.16937 | -122.1634 | 0.036621 | -0.022889 | -122.2275 | 0.19226 | 0.10071 | 0.1236 | -122.2504 | 0.073242 | 0.11902 | 0.14191 | -122.3236 | 0.054931 | 0.032043 | 0.18311 | -122.3053
3192.1875 | 122.3511 | -0.11902 | 122.2778 | -0.21088 | 0.043137 | 0.062891 | 0.00083745 | 0.031037 | -0.0055948 | 0.031928 | -0.21484 | 0.029401 | 0.037736 | 0.049669 | -0.0017453 | 0.025863 | -0.018311 | -0.022888 | -0.022888 | -0.018311 | 0.07782 | 0.018311 | -0.11444 | 0.009155 | 0.032043 | -0.086975 | 0.059509 | 0.054932 | -0.068665 | -0.091553 | 0.13733 | 0.004578 | -122.2 | 0.096131 | 0.10071 | 0.09613 | -122.2961 | 0.050354 | 0.027466 | -122.2183 | 0.12817 | 0.032044 | 0.004578 | -122.2229 | 0.19684 | 0.10071 | 0.096131 | -122.3923 | 0.17853 | 0.17395 | 0.15106 | -122.3694
3193.9531 | 122.4792 | -0.059509 | 122.2412 | -0.081177 | 0.043564 | 0.063318 | 0.0057507 | 0.02826 | -0.0096536 | 0.030646 | -0.024109 | 0.024701 | 0.037736 | 0.053087 | -0.0058041 | 0.024582 | 0.059509 | 0.027466 | 0.07782 | 0.036621 | 0.032043 | 0.045776 | -0.10071 | 0.14191 | 0.17853 | 0.073242 | 0.027466 | 0.018311 | -0.022888 | -0.064087 | 0.10528 | -0.041199 | -122.2092 | 0.086975 | 0.09613 | 0.13733 | -122.1817 | 0.036621 | -0.004578 | -122.2137 | 0.20142 | 0.13275 | 0.13733 | -122.2229 | 0.091552 | 0.11902 | 0.13733 | -122.3419 | 0.086975 | 0.07782 | 0.23804 | -122.3053
3195.7031 | 122.493 | -0.045776 | 122.2366 | -0.065918 | 0.042069 | 0.061395 | 0.0040417 | 0.029756 | -0.007731 | 0.031928 | -0.016479 | 0.029828 | 0.032396 | 0.051806 | -0.0030271 | 0.023941 | 0.059509 | 0.073242 | 0.073242 | 0.050354 | 0.064087 | 0.036621 | -0.086975 | 0.11444 | 0.13733 | 0.054932 | 0.036621 | 0.013733 | -0.018311 | -0.073242 | 0.082397 | -0.041199 | -122.1725 | 0.11902 | 0.09613 | 0.13733 | -122.1771 | 0.027465 | -0.027466 | -122.2 | 0.16022 | 0.10071 | 0.12817 | -122.2229 | 0.10986 | 0.10528 | 0.11902 | -122.3236 | 0.082397 | 0.059509 | 0.18311 | -122.3099
3197.4688 | 122.3419 | -0.10986 | 122.2778 | -0.24902 | 0.044632 | 0.061182 | 0.0016919 | 0.031251 | -0.0036722 | 0.029365 | -0.20721 | 0.026197 | 0.034532 | 0.050738 | 0.00017731 | 0.023727 | 0.068665 | 0.07782 | 0.068665 | 0.050354 | 0.064087 | 0.041199 | -0.12817 | 0.054932 | 0.068665 | -0.036621 | 0.068665 | 0.041199 | -0.022888 | -0.09613 | 0.15106 | -0.018311 | -122.2137 | 0.18768 | 0.16022 | 0.17853 | -122.2092 | 0.086975 | 0.013733 | -122.2092 | 0.16479 | 0.073242 | 0.059509 | -122.2366 | 0.17395 | 0.17853 | 0.17853 | -122.406 | 0.17853 | 0.15106 | 0.17853 | -122.374
3199.2344 | 122.3694 | -0.086975 | 122.2549 | -0.21851 | 0.045914 | 0.060541 | 0.0046827 | 0.030397 | 0.00038662 | 0.031287 | -0.21484 | 0.028333 | 0.037736 | 0.053087 | -3.629e-05 | 0.022445 | 0.004578 | -0.018311 | -0.027466 | 0.004578 | 0.10071 | 0.027466 | -0.13275 | 0.036621 | 0.041199 | -0.086975 | 0.054932 | 0.032043 | -0.054932 | -0.10071 | 0.11444 | -0.045776 | -122.1542 | 0.068664 | 0.091553 | 0.13733 | -122.2504 | 0.032043 | -0.013733 | -122.2 | 0.1236 | 0 | 0.013733 | -122.2229 | 0.18768 | 0.091553 | 0.059509 | -122.3877 | 0.14191 | 0.11902 | 0.12817 | -122.3557
3200.9375 | 122.3145 | -0.09613 | 122.2916 | -0.081177 | 0.044632 | 0.060968 | 0.00062385 | 0.030824 | 0.0010276 | 0.031714 | -0.092773 | 0.030683 | 0.039232 | 0.05266 | 0.0031681 | 0.023513 | 0.064087 | 0.059509 | 0.013733 | 0.018311 | 0.059509 | 0.013733 | -0.11444 | 0.068665 | 0.045776 | -0.07782 | 0.054932 | 0.045776 | -0.045776 | -0.10986 | 0.10986 | -0.018311 | -122.2321 | 0.15564 | 0.11444 | 0.13275 | -122.2275 | 0.050354 | -0.013733 | -122.2366 | 0.16479 | 0.01831 | 0.032043 | -122.2458 | 0.15564 | 0.16022 | 0.10986 | -122.406 | 0.15106 | 0.14191 | 0.14191 | -122.4014
3202.6406 | 122.3831 | -0.091553 | 122.2595 | -0.17273 | 0.047196 | 0.060114 | 0.0048963 | 0.033387 | -0.0011088 | 0.034278 | -0.2301 | 0.030042 | 0.036882 | 0.053087 | -0.00046349 | 0.022873 | -0.013733 | -0.004578 | -0.018311 | -0.004578 | 0.073242 | 0.018311 | -0.12817 | 0.036621 | 0.059509 | -0.07782 | 0.064087 | 0.045776 | -0.045776 | -0.10986 | 0.10986 | -0.036621 | -122.1863 | 0.086975 | 0.086975 | 0.1236 | -122.2733 | 0.045777 | -0.01831 | -122.1954 | 0.12817 | 0.013733 | 0.032043 | -122.2137 | 0.16479 | 0.07782 | 0.073242 | -122.3877 | 0.15564 | 0.13733 | 0.15106 | -122.3694
3204.3906 | 122.3465 | -0.10529 | 122.2412 | 0.056152 | 0.047623 | 0.059473 | 0.0010511 | 0.029969 | 0.00017302 | 0.032783 | -0.024109 | 0.030683 | 0.038164 | 0.053301 | 0.0016727 | 0.025222 | -0.018311 | -0.036621 | -0.022888 | -0.018311 | 0.09613 | 0.032043 | -0.1236 | -0.004578 | -0.009155 | -0.11902 | 0.059509 | 0.027466 | -0.064087 | -0.11444 | 0.13733 | -0.01831 | -122.1451 | 0.068665 | 0.086975 | 0.10528 | -122.2595 | 0.041199 | -0.009155 | -122.1817 | 0.10071 | -0.013733 | -0.004578 | -122.2137 | 0.20142 | 0.086975 | 0.082398 | -122.3648 | 0.16479 | 0.13275 | 0.096131 | -122.3557
3206.1562 | 122.3465 | -0.10529 | 122.2687 | 0.040894 | 0.047409 | 0.060968 | 0.0025465 | 0.031465 | -0.0028178 | 0.032783 | 0.0064086 | 0.02876 | 0.03795 | 0.054369 | 0.00081811 | 0.023727 | -0.036621 | -0.036621 | -0.036621 | -0.022888 | 0.086975 | 0.022888 | -0.11902 | 0 | 0.009155 | -0.11902 | 0.054932 | 0.041199 | -0.041199 | -0.11444 | 0.12817 | -0.013733 | -122.1817 | 0.068665 | 0.082398 | 0.096131 | -122.3053 | 0.064087 | -0.009155 | -122.2137 | 0.10529 | -0.013733 | -0.004578 | -122.2275 | 0.19226 | 0.068665 | 0.068665 | -122.3877 | 0.16022 | 0.14649 | 0.11444 | -122.3831
3207.8594 | 122.4701 | -0.068665 | 122.2366 | -0.13458 | 0.044846 | 0.061182 | 0.0053235 | 0.027619 | -0.012003 | 0.031714 | -0.046997 | 0.027265 | 0.037309 | 0.051378 | -0.0036679 | 0.025436 | 0.07782 | 0.15564 | 0.11444 | 0.07782 | 0.054932 | 0.045776 | -0.09613 | 0.15564 | 0.20142 | 0.064087 | 0.009155 | 0.009155 | -0.013733 | -0.073242 | 0.11444 | -0.027465 | -122.1817 | 0.22431 | 0.14649 | 0.17395 | -122.1588 | 0.054932 | -0.004577 | -122.2275 | 0.22431 | 0.13275 | 0.13733 | -122.2275 | 0.1236 | 0.14649 | 0.18311 | -122.3328 | 0.07782 | 0.07782 | 0.27008 | -122.3099
3209.625 | 122.4747 | -0.068665 | 122.2137 | -0.020142 | 0.045914 | 0.062463 | 0.0038281 | 0.031251 | -0.010081 | 0.030219 | 0.029297 | 0.027265 | 0.036882 | 0.051165 | -0.0017453 | 0.023086 | 0.018311 | 0.068665 | 0.082397 | 0.045776 | 0.054932 | 0.018311 | -0.10071 | 0.11444 | 0.1236 | 0.022888 | 0.027466 | 0.004578 | -0.022888 | -0.07782 | 0.086976 | -0.032043 | -122.1588 | 0.13733 | 0.11444 | 0.14648 | -122.1954 | 0.045777 | -0.009155 | -122.1863 | 0.18311 | 0.091553 | 0.10071 | -122.2092 | 0.1236 | 0.086976 | 0.15106 | -122.3145 | 0.096131 | 0.073243 | 0.19226 | -122.2916
3211.3906 | 122.4518 | -0.054932 | 122.2229 | 0.094299 | 0.044419 | 0.060541 | -0.00044435 | 0.032319 | 0.00060022 | 0.030433 | 0.13611 | 0.02876 | 0.036882 | 0.054156 | 0.0018863 | 0.024582 | 0.032043 | -0.013733 | -0.004578 | -0.013733 | 0.07782 | 0.022888 | -0.11444 | 0.07782 | 0.041199 | -0.045776 | 0.036621 | 0.018311 | -0.032043 | -0.086975 | 0.07782 | -0.059509 | -122.1451 | 0.041199 | 0.041199 | 0.10071 | -122.1909 | 0.022889 | -0.032043 | -122.1863 | 0.13275 | 0.009156 | 0.041199 | -122.2046 | 0.13275 | 0.086975 | 0.050354 | -122.3373 | 0.091553 | 0.073243 | 0.096131 | -122.3099
3213.0938 | 122.3236 | -0.09613 | 122.2321 | -0.22614 | 0.046555 | 0.062891 | 0.0063917 | 0.031465 | -0.0047404 | 0.031714 | -0.19196 | 0.026837 | 0.036027 | 0.054369 | -0.00089089 | 0.023941 | 0.050354 | 0.10529 | 0.068665 | 0.054932 | 0.068665 | 0.022888 | -0.11902 | 0.054932 | 0.086975 | -0.050354 | 0.032043 | 0.050354 | -0.032043 | -0.086975 | 0.11902 | -0.022889 | -122.1634 | 0.20142 | 0.15106 | 0.17395 | -122.1817 | 0.064087 | 0.009155 | -122.2 | 0.15106 | 0.045776 | 0.036621 | -122.1817 | 0.16479 | 0.14648 | 0.16479 | -122.3511 | 0.12817 | 0.14648 | 0.1831 | -122.319
3214.8594 | 122.3511 | -0.10529 | 122.2733 | -0.15747 | 0.046555 | 0.06225 | 0.0034009 | 0.029756 | -0.0047404 | 0.029578 | -0.21484 | 0.030469 | 0.037096 | 0.05266 | -0.0011045 | 0.022018 | -0.018311 | 0.013733 | -0.004578 | -0.032043 | 0.091553 | 0.004578 | -0.13733 | 0.022888 | 0.045776 | -0.073242 | 0.068665 | 0.059509 | -0.059509 | -0.10529 | 0.10986 | -0.032043 | -122.1817 | 0.11902 | 0.073243 | 0.10529 | -122.2916 | 0.045777 | 0 | -122.2046 | 0.12817 | 0.032044 | 0.032044 | -122.2137 | 0.19684 | 0.086975 | 0.10071 | -122.4106 | 0.17395 | 0.16479 | 0.15106 | -122.3785
3216.6406 | 122.3282 | -0.10986 | 122.2641 | -0.24902 | 0.044419 | 0.062036 | 0.0029737 | 0.029969 | -0.0038858 | 0.032142 | -0.19958 | 0.025983 | 0.038164 | 0.051378 | 0.00081811 | 0.023086 | 0.041199 | 0.09613 | 0.059509 | 0.036621 | 0.054932 | 0.045776 | -0.09613 | 0.050354 | 0.059509 | -0.054932 | 0.059509 | 0.036621 | -0.032043 | -0.10986 | 0.15564 | 0.013733 | -122.2092 | 0.20599 | 0.14648 | 0.13275 | -122.2229 | 0.07782 | 0 | -122.2046 | 0.16022 | 0.054931 | 0.054931 | -122.2275 | 0.16479 | 0.15106 | 0.16937 | -122.3602 | 0.16937 | 0.14648 | 0.16937 | -122.374
3218.4062 | 122.3282 | -0.10986 | 122.2778 | 0.0027468 | 0.047409 | 0.059045 | 0.0012647 | 0.032533 | -0.00068138 | 0.033423 | -0.0088499 | 0.028119 | 0.035814 | 0.051592 | 0.0035953 | 0.023727 | 0 | -0.013733 | -0.018311 | 0 | 0.082397 | 0.018311 | -0.13275 | 0.022888 | -0.004578 | -0.11902 | 0.054932 | 0.027466 | -0.045776 | -0.09613 | 0.12817 | -0.022888 | -122.1954 | 0.09613 | 0.10986 | 0.13275 | -122.2778 | 0.064087 | 0.013733 | -122.2229 | 0.13275 | -0.009156 | -0.022889 | -122.2504 | 0.19226 | 0.10986 | 0.091552 | -122.4106 | 0.16479 | 0.13733 | 0.10529 | -122.374
3220.1562 | 122.3328 | -0.082397 | 122.2733 | 0.033264 | 0.048477 | 0.063318 | 0.0025465 | 0.032105 | 0.00038662 | 0.03321 | -0.016479 | 0.029828 | 0.037736 | 0.051378 | 0.0042361 | 0.023727 | -0.032043 | -0.027466 | -0.036621 | -0.013733 | 0.09613 | -0.004578 | -0.13275 | 0 | -0.027466 | -0.11902 | 0.059509 | 0.036621 | -0.054932 | -0.10071 | 0.077819 | -0.050354 | -122.1771 | 0.054931 | 0.068664 | 0.11902 | -122.3053 | 0.027465 | -0.018311 | -122.2137 | 0.082397 | -0.036622 | -0.018311 | -122.2366 | 0.17853 | 0.050354 | 0.045776 | -122.406 | 0.14191 | 0.11902 | 0.054931 | -122.374
3221.8594 | 122.3602 | -0.091553 | 122.2595 | -0.24902 | 0.046768 | 0.060541 | 0.0025465 | 0.031251 | -0.0047404 | 0.033637 | -0.1767 | 0.029615 | 0.036668 | 0.052019 | 0.00081811 | 0.023727 | -0.018311 | -0.013733 | -0.022888 | 0 | 0.07782 | 0.013733 | -0.14191 | 0.032043 | 0.036621 | -0.082397 | 0.045776 | 0.045776 | -0.054932 | -0.09613 | 0.10529 | -0.050354 | -122.1817 | 0.07782 | 0.091553 | 0.14191 | -122.2778 | 0.036621 | -0.004577 | -122.2137 | 0.1236 | 0.009156 | 0.013733 | -122.2137 | 0.16937 | 0.073242 | 0.068665 | -122.4014 | 0.13733 | 0.13733 | 0.12817 | -122.3557
3223.625 | 122.3419 | -0.10529 | 122.2961 | -0.18036 | 0.044419 | 0.062036 | 0.0036145 | 0.031037 | -0.004954 | 0.030006 | -0.20721 | 0.030683 | 0.035814 | 0.053728 | -0.0032407 | 0.02565 | -0.022888 | 0.013733 | -0.004578 | -0.018311 | 0.073242 | 0 | -0.12817 | 0.022888 | 0.036621 | -0.07782 | 0.059509 | 0.032043 | -0.050354 | -0.10071 | 0.10529 | -0.022888 | -122.2229 | 0.11902 | 0.086975 | 0.10986 | -122.319 | 0.054932 | 0.004578 | -122.2366 | 0.12817 | 0.027466 | 0.022888 | -122.2641 | 0.17853 | 0.082398 | 0.10071 | -122.4243 | 0.16479 | 0.13733 | 0.14191 | -122.3969
3225.3281 | 122.4197 | -0.064087 | 122.2504 | 0.08667 | 0.046768 | 0.063318 | 0.0012647 | 0.031037 | -0.003245 | 0.032142 | 0.059815 | 0.029187 | 0.036241 | 0.051806 | 0.0033817 | 0.023513 | -0.013733 | -0.022888 | -0.045776 | -0.027466 | 0.073242 | 0.022888 | -0.13275 | 0.027466 | -0.004578 | -0.091553 | 0.064087 | 0.032043 | -0.036621 | -0.10071 | 0.086975 | -0.068664 | -122.1771 | 0.041199 | 0.036621 | 0.10529 | -122.2641 | 0.027466 | -0.036621 | -122.1863 | 0.091553 | -0.027466 | 0.009155 | -122.2183 | 0.13733 | 0.050354 | 0.018311 | -122.3831 | 0.12817 | 0.09613 | 0.059509 | -122.3511
3227.0938 | 122.4609 | -0.050354 | 122.2412 | -0.0048827 | 0.042282 | 0.060327 | 0.0044691 | 0.029115 | -0.0075174 | 0.030006 | 0.059815 | 0.027692 | 0.035814 | 0.052447 | -0.0040951 | 0.023941 | -0.009155 | 0.054932 | 0.045776 | 0.018311 | 0.059509 | 0.054932 | -0.09613 | 0.086975 | 0.10529 | 0.009155 | 0.022888 | 0.018311 | -0.018311 | -0.091553 | 0.10529 | -0.045776 | -122.1817 | 0.10529 | 0.068665 | 0.11444 | -122.2504 | 0.032043 | -0.041199 | -122.2183 | 0.13733 | 0.059509 | 0.10071 | -122.2229 | 0.10986 | 0.041199 | 0.09613 | -122.3373 | 0.073242 | 0.068665 | 0.15564 | -122.3328
3228.7812 | 122.3145 | -0.10529 | 122.2778 | -0.0354 | 0.048264 | 0.059259 | 0.0038281 | 0.030824 | -4.058e-05 | 0.03086 | -0.039368 | 0.028974 | 0.036668 | 0.053087 | 0.0035953 | 0.023727 | 0.041199 | 0.018311 | 0 | 0.004578 | 0.07782 | 0.022888 | -0.10986 | 0.041199 | 0.018311 | -0.091553 | 0.045776 | 0.036621 | -0.064087 | -0.1236 | 0.12817 | -0.004577 | -122.2 | 0.1236 | 0.10986 | 0.11444 | -122.2366 | 0.041199 | -0.01831 | -122.2321 | 0.14649 | 0.013733 | 0.032043 | -122.2412 | 0.18311 | 0.14649 | 0.10529 | -122.3877 | 0.15106 | 0.14191 | 0.1236 | -122.4014
3230.5312 | 122.3282 | -0.10071 | 122.2778 | -0.081177 | 0.046341 | 0.058405 | 0.0031873 | 0.031251 | -0.00025418 | 0.031928 | -0.1004 | 0.02876 | 0.037736 | 0.05266 | 0.0023135 | 0.024368 | 0.054932 | 0.045776 | 0.013733 | 0.018311 | 0.086975 | 0.018311 | -0.10071 | 0.064087 | 0.068665 | -0.068665 | 0.041199 | 0.018311 | -0.045776 | -0.10071 | 0.11902 | 0 | -122.1909 | 0.14648 | 0.11902 | 0.11902 | -122.2229 | 0.054932 | 0 | -122.2366 | 0.1648 | 0.032043 | 0.032043 | -122.2595 | 0.18768 | 0.15564 | 0.11444 | -122.3785 | 0.14191 | 0.11902 | 0.16937 | -122.3785
3232.2812 | 122.3557 | -0.091553 | 122.2412 | 0.08667 | 0.046555 | 0.060114 | 0.0016919 | 0.029756 | 0.00038662 | 0.03321 | 0.082703 | 0.028333 | 0.036455 | 0.053515 | 0.0014591 | 0.023941 | -0.013733 | -0.045776 | -0.050354 | -0.013733 | 0.07782 | 0.027466 | -0.13275 | 0.032043 | -0.022888 | -0.10071 | 0.064087 | 0.041199 | -0.032043 | -0.10071 | 0.11902 | -0.041198 | -122.1634 | 0.045777 | 0.07782 | 0.11902 | -122.2549 | 0.05951 | -0.009155 | -122.1771 | 0.1236 | -0.009155 | 0 | -122.2 | 0.16937 | 0.07782 | 0.041199 | -122.374 | 0.15564 | 0.13275 | 0.068665 | -122.3419
3234.0469 | 122.3282 | -0.11444 | 122.2641 | -0.23376 | 0.046555 | 0.06225 | 0.0031873 | 0.030824 | -0.0090128 | 0.031714 | -0.16144 | 0.029828 | 0.039018 | 0.050951 | -0.0023861 | 0.026291 | -0.018311 | 0.032043 | 0.013733 | -0.004578 | 0.07782 | 0.009155 | -0.13275 | 0.022888 | 0.032043 | -0.082397 | 0.059509 | 0.036621 | -0.064087 | -0.11444 | 0.1236 | -0.01831 | -122.1863 | 0.14648 | 0.10986 | 0.12817 | -122.2824 | 0.050354 | 0 | -122.2046 | 0.13733 | 0.032044 | 0.032044 | -122.2275 | 0.19226 | 0.09613 | 0.12817 | -122.3969 | 0.17395 | 0.15106 | 0.14648 | -122.3785
3235.7344 | 122.4518 | -0.07782 | 122.2275 | -0.012512 | 0.041428 | 0.062891 | 0.0016919 | 0.030183 | -0.0085856 | 0.031074 | 0.082703 | 0.025128 | 0.038377 | 0.049669 | -0.0011045 | 0.026077 | 0 | 0.064087 | 0.050354 | 0.041199 | 0.054932 | 0.041199 | -0.086975 | 0.068665 | 0.07782 | 0.009155 | 0.009155 | 0.032043 | -0.013733 | -0.07782 | 0.11902 | -0.009155 | -122.1725 | 0.14191 | 0.11902 | 0.12817 | -122.2275 | 0.064087 | 0 | -122.2183 | 0.14649 | 0.086975 | 0.086975 | -122.1954 | 0.13275 | 0.07782 | 0.12817 | -122.3145 | 0.086975 | 0.10986 | 0.15564 | -122.3053
3237.5 | 122.3282 | -0.10529 | 122.2733 | -0.25665 | 0.0457 | 0.063104 | 0.0048963 | 0.029756 | -0.0036722 | 0.027869 | -0.14618 | 0.029828 | 0.035173 | 0.052233 | -0.0013181 | 0.0233 | 0.018311 | 0.041199 | 0.009155 | 0.022888 | 0.059509 | 0.018311 | -0.10986 | 0.018311 | 0.050354 | -0.059509 | 0.059509 | 0.032043 | -0.036621 | -0.10071 | 0.1236 | -0.004577 | -122.2137 | 0.14649 | 0.12817 | 0.13275 | -122.2549 | 0.068665 | 0.004578 | -122.2137 | 0.1236 | 0.045777 | 0.041199 | -122.2412 | 0.16479 | 0.1236 | 0.11444 | -122.3831 | 0.16479 | 0.13733 | 0.15564 | -122.374
3239.2656 | 122.3923 | -0.082397 | 122.2595 | -0.19562 | 0.0457 | 0.06225 | 0.0057507 | 0.029969 | -0.0064492 | 0.02851 | -0.12329 | 0.028119 | 0.036027 | 0.053728 | -0.0025999 | 0.023727 | 0.086975 | 0.13733 | 0.11444 | 0.059509 | 0.041199 | 0.050354 | -0.09613 | 0.13275 | 0.17853 | 0.036621 | 0.018311 | 0.022888 | -0.032043 | -0.064087 | 0.13275 | -0.013733 | -122.2183 | 0.21973 | 0.14191 | 0.15564 | -122.1725 | 0.050354 | 0.01831 | -122.2412 | 0.21515 | 0.11902 | 0.10071 | -122.2366 | 0.1236 | 0.16937 | 0.19684 | -122.3557 | 0.10071 | 0.10528 | 0.26092 | -122.3236
3241.0312 | 122.4838 | -0.050354 | 122.2275 | -0.020142 | 0.044632 | 0.061182 | 0.0070325 | 0.028901 | -0.0079446 | 0.029792 | -0.016479 | 0.027051 | 0.037096 | 0.05266 | -0.0045225 | 0.022873 | 0.041199 | 0.054932 | 0.068665 | 0.059509 | 0.036621 | 0.036621 | -0.10986 | 0.10529 | 0.11444 | 0.036621 | 0.032043 | 0.022888 | -0.013733 | -0.073242 | 0.086975 | -0.059509 | -122.1909 | 0.10529 | 0.10986 | 0.16937 | -122.1863 | 0.036621 | -0.022888 | -122.1954 | 0.15564 | 0.086975 | 0.10986 | -122.2046 | 0.086975 | 0.091553 | 0.11902 | -122.3373 | 0.082397 | 0.073242 | 0.16479 | -122.3007
3242.7969 | 122.4701 | -0.032043 | 122.2458 | 0.13245 | 0.045914 | 0.058832 | -0.0034351 | 0.032319 | 0.00081382 | 0.031501 | 0.075073 | 0.02876 | 0.033464 | 0.05266 | 0.0018863 | 0.021591 | 0.10529 | 0.091553 | 0.073242 | 0.068665 | 0.059509 | 0.059509 | -0.10071 | 0.15106 | 0.10986 | 0.032043 | 0.027466 | 0.009155 | -0.032043 | -0.059509 | 0.091552 | -0.068665 | -122.1863 | 0.1236 | 0.10071 | 0.16937 | -122.1405 | 0 | -0.027466 | -122.2183 | 0.18311 | 0.064086 | 0.091552 | -122.2366 | 0.091552 | 0.13733 | 0.10529 | -122.3465 | 0.059509 | 0.041198 | 0.14191 | -122.3053
3244.5 | 122.3923 | -0.073242 | 122.2549 | -0.18036 | 0.045487 | 0.063318 | 0.0014783 | 0.028901 | -0.0053812 | 0.029792 | -0.14618 | 0.02641 | 0.034746 | 0.050524 | 0.0010317 | 0.023727 | 0.10986 | 0.1236 | 0.1236 | 0.068665 | 0.050354 | 0.041199 | -0.09613 | 0.14191 | 0.16937 | 0.027466 | 0.022888 | 0 | -0.013733 | -0.064087 | 0.11444 | -0.022888 | -122.2046 | 0.19684 | 0.14191 | 0.16479 | -122.1451 | 0.059509 | 0.009155 | -122.2321 | 0.21515 | 0.10071 | 0.091553 | -122.2549 | 0.1236 | 0.18311 | 0.19684 | -122.3511 | 0.09613 | 0.073242 | 0.24261 | -122.319
3246.2656 | 122.3419 | -0.09613 | 122.2824 | -0.23376 | 0.0457 | 0.0599 | 0.0055371 | 0.03296 | -0.0021768 | 0.030646 | -0.19958 | 0.029401 | 0.036882 | 0.054583 | -0.00067729 | 0.022445 | 0.041199 | 0 | 0 | -0.009155 | 0.073242 | 0.013733 | -0.12817 | 0.036621 | 0.045776 | -0.086975 | 0.068665 | 0.054932 | -0.059509 | -0.10529 | 0.10986 | -0.032044 | -122.2092 | 0.09613 | 0.086975 | 0.11902 | -122.2412 | 0.036621 | -0.009156 | -122.2137 | 0.13275 | 0.009155 | 0.018311 | -122.2275 | 0.16937 | 0.13733 | 0.09613 | -122.4106 | 0.16479 | 0.15106 | 0.14191 | -122.3877
3248.0312 | 122.3282 | -0.07782 | 122.2778 | 0.040894 | 0.047837 | 0.059473 | 0.0014783 | 0.031892 | 0.0014548 | 0.031928 | -0.046997 | 0.030683 | 0.034105 | 0.054156 | 0.0053043 | 0.023727 | 0.004578 | -0.054932 | -0.050354 | -0.022888 | 0.086975 | 0.013733 | -0.1236 | 0.004578 | -0.018311 | -0.11902 | 0.059509 | 0.045776 | -0.045776 | -0.10986 | 0.091553 | -0.045776 | -122.1909 | 0.022888 | 0.054932 | 0.10071 | -122.2733 | 0.032044 | -0.032043 | -122.2183 | 0.082398 | -0.041199 | -0.009156 | -122.2321 | 0.16479 | 0.082398 | 0.027466 | -122.4014 | 0.13733 | 0.1236 | 0.059509 | -122.3877
3249.7344 | 122.3785 | -0.086975 | 122.2504 | -0.21851 | 0.044846 | 0.060754 | 0.0036145 | 0.031037 | -0.0023904 | 0.032355 | -0.19958 | 0.027692 | 0.03795 | 0.052874 | 0.00017731 | 0.021804 | 0.004578 | -0.018311 | -0.013733 | 0.004578 | 0.07782 | -0.009155 | -0.13275 | 0.032043 | 0.054932 | -0.068665 | 0.059509 | 0.050354 | -0.050354 | -0.11902 | 0.07782 | -0.045776 | -122.1725 | 0.068664 | 0.091553 | 0.13733 | -122.2458 | 0.036621 | -0.032044 | -122.1909 | 0.11902 | 0.01831 | 0.050354 | -122.2 | 0.16479 | 0.091553 | 0.073242 | -122.3831 | 0.14648 | 0.13733 | 0.14191 | -122.3694
3251.4844 | 122.4152 | -0.086975 | 122.2549 | -0.18036 | 0.043351 | 0.060114 | 0.0048963 | 0.03061 | -0.0075174 | 0.029792 | -0.14618 | 0.02641 | 0.036027 | 0.053728 | -0.0013181 | 0.026077 | 0.082397 | 0.15106 | 0.1236 | 0.068665 | 0.045776 | 0.064087 | -0.082397 | 0.12817 | 0.16479 | 0.045776 | 0.009155 | 0.013733 | -0.013733 | -0.082397 | 0.15106 | 0.004578 | -122.2092 | 0.23804 | 0.15564 | 0.15106 | -122.1725 | 0.073242 | 0.004578 | -122.2458 | 0.21515 | 0.13275 | 0.12817 | -122.2412 | 0.13275 | 0.16937 | 0.21057 | -122.3373 | 0.09613 | 0.10071 | 0.25177 | -122.3373
3253.2344 | 122.3602 | -0.091553 | 122.2412 | -0.24902 | 0.047623 | 0.062036 | 0.0068189 | 0.032533 | -0.0030314 | 0.029578 | -0.25299 | 0.028333 | 0.036455 | 0.053728 | -0.0011045 | 0.022659 | -0.009155 | -0.004578 | -0.022888 | -0.018311 | 0.091553 | 0.022888 | -0.1236 | 0.027466 | 0.032043 | -0.09613 | 0.068665 | 0.036621 | -0.054932 | -0.10986 | 0.11444 | -0.032043 | -122.1497 | 0.086975 | 0.073242 | 0.10528 | -122.2504 | 0.036621 | -0.01831 | -122.1725 | 0.11902 | -0.004577 | 0.013733 | -122.2046 | 0.18311 | 0.082398 | 0.068665 | -122.3648 | 0.16022 | 0.12817 | 0.1236 | -122.3511
3255 | 122.3465 | -0.10986 | 122.2824 | 0.040894 | 0.046341 | 0.060968 | -1.7146e-05 | 0.031251 | 0.00038662 | 0.032355 | -0.016479 | 0.032605 | 0.0356 | 0.053301 | 0.0025271 | 0.0233 | -0.009155 | -0.041199 | -0.045776 | -0.018311 | 0.068665 | 0.004578 | -0.1236 | 0.013733 | -0.018311 | -0.10986 | 0.050354 | 0.041199 | -0.032043 | -0.11444 | 0.11444 | -0.013733 | -122.2137 | 0.068664 | 0.091552 | 0.10528 | -122.2916 | 0.07782 | -0.004578 | -122.2321 | 0.1236 | 0 | 0.004578 | -122.2412 | 0.17853 | 0.10071 | 0.064087 | -122.406 | 0.16022 | 0.15106 | 0.091552 | -122.3969
3256.7031 | 122.3419 | -0.10071 | 122.2733 | -0.24139 | 0.045487 | 0.061609 | 0.0055371 | 0.029542 | -0.0051676 | 0.030433 | -0.16144 | 0.027478 | 0.039659 | 0.053087 | -0.0019589 | 0.025863 | 0 | 0.027466 | 0.013733 | 0 | 0.073242 | 0.018311 | -0.14648 | 0.022888 | 0.059509 | -0.068665 | 0.068665 | 0.054932 | -0.068665 | -0.10529 | 0.11902 | -0.045776 | -122.2 | 0.12817 | 0.10071 | 0.14648 | -122.2733 | 0.032043 | -0.004578 | -122.2046 | 0.1236 | 0.032043 | 0.036621 | -122.2183 | 0.17395 | 0.10071 | 0.11444 | -122.4197 | 0.16937 | 0.15564 | 0.16022 | -122.3785
3258.4688 | 122.4152 | -0.068665 | 122.2549 | 0.10956 | 0.042923 | 0.062036 | 0.0023329 | 0.029542 | -0.0085856 | 0.030006 | 0.11322 | 0.027906 | 0.038591 | 0.053301 | -0.0017453 | 0.026931 | 0.068665 | 0.091553 | 0.059509 | 0.036621 | 0.045776 | 0.045776 | -0.09613 | 0.10986 | 0.09613 | 0.018311 | 0.036621 | 0.018311 | -0.004578 | -0.073242 | 0.11444 | -0.027465 | -122.2092 | 0.16022 | 0.10529 | 0.13275 | -122.1863 | 0.064087 | -0.004577 | -122.2183 | 0.17853 | 0.086976 | 0.091553 | -122.2366 | 0.11444 | 0.13733 | 0.12817 | -122.3511 | 0.10529 | 0.086976 | 0.16479 | -122.3282
3260.1719 | 122.3511 | -0.09613 | 122.2687 | 0.025635 | 0.046128 | 0.057764 | 0.0023329 | 0.031678 | 0.00060022 | 0.032996 | 0.036926 | 0.032178 | 0.037096 | 0.054369 | 0.0048769 | 0.023086 | 0 | -0.082397 | -0.050354 | -0.013733 | 0.086975 | 0.022888 | -0.12817 | 0.036621 | -0.013733 | -0.10986 | 0.059509 | 0.050354 | -0.045776 | -0.10529 | 0.11902 | -0.032044 | -122.1817 | 0.013733 | 0.082397 | 0.11444 | -122.2687 | 0.050354 | -0.009156 | -122.2092 | 0.13275 | -0.013733 | -0.004577 | -122.2183 | 0.1831 | 0.09613 | 0.045776 | -122.3969 | 0.15564 | 0.14648 | 0.082397 | -122.374
3261.9375 | 122.4472 | -0.045776 | 122.2229 | 0.11719 | 0.043137 | 0.061609 | 0.0023329 | 0.030824 | -0.004313 | 0.030006 | 0.097962 | 0.027478 | 0.037096 | 0.05266 | 0.0025271 | 0.023513 | 0.086975 | 0.07782 | 0.082397 | 0.054932 | 0.064087 | 0.059509 | -0.082397 | 0.14191 | 0.14191 | 0.032043 | 0.027466 | 0.009155 | 0 | -0.054932 | 0.10528 | -0.036621 | -122.1588 | 0.1236 | 0.10071 | 0.13733 | -122.1359 | 0.045776 | -0.009156 | -122.1954 | 0.18768 | 0.077819 | 0.086975 | -122.2137 | 0.10986 | 0.13275 | 0.12817 | -122.3053 | 0.073242 | 0.054931 | 0.18768 | -122.2778
3263.7031 | 122.3373 | -0.086975 | 122.2504 | -0.096436 | 0.049546 | 0.060541 | 0.0048963 | 0.032319 | -0.0019632 | 0.034278 | -0.10803 | 0.029187 | 0.036668 | 0.053301 | -3.629e-05 | 0.023513 | 0.07782 | 0.050354 | 0.036621 | 0.022888 | 0.082397 | 0.027466 | -0.13275 | 0.082397 | 0.086975 | -0.054932 | 0.041199 | 0.045776 | -0.032043 | -0.10529 | 0.11444 | -0.045776 | -122.168 | 0.13733 | 0.10986 | 0.15564 | -122.1725 | 0.054932 | -0.018311 | -122.2092 | 0.16937 | 0.032043 | 0.050354 | -122.2046 | 0.16937 | 0.16479 | 0.1236 | -122.3831 | 0.12817 | 0.13275 | 0.17395 | -122.3557
3265.3906 | 122.4701 | -0.064087 | 122.2412 | 0.10956 | 0.046341 | 0.063104 | -0.0012987 | 0.032319 | -0.001536 | 0.031714 | 0.15137 | 0.028546 | 0.034746 | 0.052447 | 0.0014591 | 0.026077 | 0.013733 | 0.009155 | -0.004578 | -0.009155 | 0.073242 | 0.027466 | -0.11902 | 0.09613 | 0.059509 | -0.027466 | 0.027466 | 0.013733 | -0.032043 | -0.07782 | 0.091553 | -0.054932 | -122.168 | 0.073242 | 0.054932 | 0.10986 | -122.2275 | 0.032044 | -0.013733 | -122.2137 | 0.16022 | 0.036621 | 0.050354 | -122.2275 | 0.13733 | 0.07782 | 0.059509 | -122.3602 | 0.091553 | 0.07782 | 0.1236 | -122.319
3267.1562 | 122.3465 | -0.10529 | 122.287 | -0.21088 | 0.0457 | 0.060327 | 0.0072461 | 0.031037 | -0.006663 | 0.032142 | -0.20721 | 0.027265 | 0.037096 | 0.054796 | -0.0028135 | 0.025009 | -0.032043 | -0.004578 | -0.004578 | -0.022888 | 0.068665 | 0.004578 | -0.12817 | 0.022888 | 0.027466 | -0.07782 | 0.059509 | 0.054932 | -0.073242 | -0.11444 | 0.10986 | -0.022888 | -122.2183 | 0.10071 | 0.082398 | 0.10529 | -122.319 | 0.032044 | -0.009155 | -122.2275 | 0.12817 | 0.027466 | 0.036621 | -122.2321 | 0.17395 | 0.073243 | 0.10071 | -122.4152 | 0.16479 | 0.16022 | 0.13275 | -122.4014
3268.9219 | 122.4609 | -0.059509 | 122.2275 | 0.08667 | 0.046555 | 0.062036 | 0.0014783 | 0.028901 | -0.002604 | 0.031714 | 0.12848 | 0.027265 | 0.032396 | 0.050738 | 0.0020999 | 0.023086 | 0.018311 | -0.013733 | -0.009155 | 0 | 0.073242 | 0.027466 | -0.1236 | 0.082397 | 0.050354 | -0.050354 | 0.032043 | 0.027466 | -0.050354 | -0.082397 | 0.086975 | -0.064087 | -122.1542 | 0.045776 | 0.059509 | 0.1236 | -122.2092 | 0.009155 | -0.022888 | -122.1954 | 0.14191 | 0.009155 | 0.032043 | -122.2 | 0.13275 | 0.07782 | 0.050354 | -122.3511 | 0.091552 | 0.086975 | 0.10986 | -122.3099
3270.6719 | 122.4335 | -0.054932 | 122.2229 | 0.14008 | 0.043778 | 0.0599 | 0.00041005 | 0.031465 | -0.0051676 | 0.032783 | 0.13611 | 0.025983 | 0.0356 | 0.051592 | 0.0025271 | 0.026504 | 0.073242 | 0.12817 | 0.11444 | 0.059509 | 0.027466 | 0.045776 | -0.09613 | 0.13733 | 0.12817 | 0.036621 | 0.018311 | 0 | -0.009155 | -0.073242 | 0.10071 | -0.041198 | -122.1954 | 0.18311 | 0.11444 | 0.15564 | -122.1497 | 0.045777 | -0.01831 | -122.2046 | 0.19226 | 0.091553 | 0.10986 | -122.2229 | 0.082398 | 0.12817 | 0.16937 | -122.319 | 0.073243 | 0.054932 | 0.18311 | -122.2961
3272.375 | 122.3557 | -0.091553 | 122.2778 | -0.22614 | 0.047837 | 0.060541 | 0.0078871 | 0.031251 | -0.004954 | 0.028937 | -0.15381 | 0.026197 | 0.038377 | 0.051378 | -0.0043087 | 0.023513 | 0 | 0.036621 | 0.009155 | 0.009155 | 0.091553 | 0.027466 | -0.11902 | 0.013733 | 0.041199 | -0.07782 | 0.064087 | 0.059509 | -0.036621 | -0.11444 | 0.11902 | -0.027466 | -122.1863 | 0.12817 | 0.10071 | 0.12817 | -122.2778 | 0.054932 | -0.022888 | -122.2137 | 0.10529 | 0.013733 | 0.036621 | -122.2183 | 0.18311 | 0.091553 | 0.10071 | -122.3969 | 0.15564 | 0.15106 | 0.13275 | -122.3923
3274.1406 | 122.4472 | -0.045776 | 122.2366 | 0.08667 | 0.046982 | 0.060114 | 0.0029737 | 0.032533 | -0.00046778 | 0.032996 | 0.075073 | 0.026197 | 0.037736 | 0.054796 | 0.0016727 | 0.023086 | 0.022888 | -0.027466 | -0.018311 | -0.022888 | 0.09613 | 0.022888 | -0.1236 | 0.054932 | -0.009155 | -0.073242 | 0.041199 | 0.041199 | -0.045776 | -0.10529 | 0.068664 | -0.07782 | -122.1405 | 0.01831 | 0.022888 | 0.10071 | -122.2137 | 0 | -0.05951 | -122.1954 | 0.10071 | -0.027466 | 0.032044 | -122.1954 | 0.14191 | 0.068664 | 0.027465 | -122.3602 | 0.086975 | 0.086975 | 0.036621 | -122.3419
3275.875 | 122.3373 | -0.10986 | 122.2641 | -0.19562 | 0.046768 | 0.060968 | 0.0070325 | 0.031678 | -0.0073038 | 0.030006 | -0.19958 | 0.027478 | 0.037736 | 0.052874 | -0.00067729 | 0.023727 | 0.064087 | 0.09613 | 0.064087 | 0.07782 | 0.036621 | 0.032043 | -0.10071 | 0.07782 | 0.11902 | -0.018311 | 0.041199 | 0.027466 | -0.036621 | -0.10986 | 0.14191 | 0.009155 | -122.2275 | 0.20599 | 0.18768 | 0.17853 | -122.2 | 0.073242 | 0 | -122.2229 | 0.18768 | 0.091552 | 0.091552 | -122.2366 | 0.14648 | 0.17395 | 0.17395 | -122.3648 | 0.15106 | 0.13733 | 0.22888 | -122.374
3277.6406 | 122.319 | -0.086975 | 122.2504 | -0.058289 | 0.047623 | 0.059473 | 0.00019645 | 0.032105 | 0.00060022 | 0.032569 | -0.039368 | 0.029401 | 0.03795 | 0.053301 | 0.0027407 | 0.0233 | 0.054932 | 0.013733 | 0 | 0.013733 | 0.091553 | 0.013733 | -0.1236 | 0.045776 | 0.004578 | -0.09613 | 0.045776 | 0.032043 | -0.045776 | -0.091553 | 0.10071 | -0.036621 | -122.1588 | 0.10071 | 0.10071 | 0.13733 | -122.1954 | 0.041199 | -0.004578 | -122.2046 | 0.13275 | -0.009155 | -0.004577 | -122.2183 | 0.17853 | 0.14191 | 0.086975 | -122.374 | 0.13275 | 0.11902 | 0.091553 | -122.3419
3279.4219 | 122.4884 | -0.050354 | 122.2 | -0.081177 | 0.046341 | 0.063104 | 0.0029737 | 0.028047 | -0.0081582 | 0.032142 | -0.0012209 | 0.024274 | 0.039232 | 0.05266 | -0.0047361 | 0.025436 | 0.050354 | 0.10071 | 0.07782 | 0.059509 | 0.050354 | 0.032043 | -0.068665 | 0.1236 | 0.16022 | 0.059509 | 0.018311 | 0.018311 | -0.009155 | -0.059509 | 0.082397 | -0.018311 | -122.1497 | 0.15106 | 0.10986 | 0.12817 | -122.1497 | 0.041199 | -0.009155 | -122.1817 | 0.17395 | 0.10986 | 0.11902 | -122.1817 | 0.10071 | 0.10071 | 0.12817 | -122.2687 | 0.068665 | 0.068665 | 0.21057 | -122.2595
3281.125 | 122.3648 | -0.09613 | 122.2321 | -0.21088 | 0.044846 | 0.060754 | 0.0040417 | 0.031678 | -0.001536 | 0.029578 | -0.21484 | 0.030469 | 0.037736 | 0.05501 | 0.0016727 | 0.022018 | 0 | -0.027466 | -0.032043 | -0.009155 | 0.091553 | 0.004578 | -0.12817 | 0.018311 | 0.050354 | -0.086975 | 0.068665 | 0.054932 | -0.041199 | -0.091553 | 0.10071 | -0.032044 | -122.1405 | 0.068664 | 0.086975 | 0.11902 | -122.2321 | 0.054931 | 0.004577 | -122.1634 | 0.11444 | 0.009155 | 0.004578 | -122.1771 | 0.18768 | 0.09613 | 0.064087 | -122.3602 | 0.16479 | 0.15106 | 0.14648 | -122.3236
3282.875 | 122.3511 | -0.09613 | 122.2595 | -0.18036 | 0.044632 | 0.0599 | 0.0061781 | 0.032105 | -0.0055948 | 0.03086 | -0.12329 | 0.029615 | 0.038591 | 0.052233 | -0.0017453 | 0.022232 | 0.068665 | 0.12817 | 0.1236 | 0.07782 | 0.045776 | 0.036621 | -0.091553 | 0.11902 | 0.16479 | 0.032043 | 0.009155 | 0.027466 | -0.032043 | -0.068665 | 0.13275 | 0.004577 | -122.2137 | 0.2243 | 0.17395 | 0.16937 | -122.1909 | 0.064087 | 0.027465 | -122.2504 | 0.21515 | 0.12817 | 0.10071 | -122.2321 | 0.14191 | 0.16479 | 0.21973 | -122.3511 | 0.10528 | 0.1236 | 0.26092 | -122.3282
3284.6406 | 122.4838 | -0.032043 | 122.2183 | -0.020142 | 0.044205 | 0.061609 | 0.0023329 | 0.03296 | -0.0073038 | 0.029578 | 0.0064086 | 0.025128 | 0.035387 | 0.051165 | -0.0015317 | 0.024795 | 0.027466 | 0.07782 | 0.059509 | 0.041199 | 0.050354 | 0.045776 | -0.09613 | 0.10986 | 0.13733 | 0.027466 | 0.041199 | 0.009155 | -0.009155 | -0.064087 | 0.077819 | -0.064087 | -122.168 | 0.10986 | 0.073242 | 0.13733 | -122.1909 | 0.022888 | -0.032044 | -122.1771 | 0.14191 | 0.059509 | 0.091553 | -122.2092 | 0.082397 | 0.059509 | 0.091552 | -122.3145 | 0.073242 | 0.041198 | 0.16937 | -122.2824
3286.3906 | 122.438 | -0.036621 | 122.2137 | 0.10956 | 0.043564 | 0.061609 | -0.00065795 | 0.031251 | -0.0011088 | 0.031928 | 0.16663 | 0.02876 | 0.034959 | 0.050524 | 0.0038089 | 0.021804 | 0.11902 | 0.091553 | 0.09613 | 0.068665 | 0.064087 | 0.068665 | -0.086975 | 0.14191 | 0.13275 | 0.027466 | 0.009155 | 0.009155 | -0.013733 | -0.054932 | 0.10529 | -0.050354 | -122.1497 | 0.12817 | 0.10529 | 0.15564 | -122.0947 | 0.022888 | -0.018311 | -122.2046 | 0.17853 | 0.064087 | 0.082398 | -122.2046 | 0.10071 | 0.15564 | 0.13275 | -122.3007 | 0.045776 | 0.045776 | 0.16937 | -122.2687
3288.0781 | 122.3648 | -0.09613 | 122.2778 | -0.13458 | 0.046128 | 0.061182 | 0.0025465 | 0.031251 | 0.00060022 | 0.034278 | -0.1767 | 0.027692 | 0.036027 | 0.050951 | 0.0033817 | 0.022873 | 0.064087 | 0.041199 | 0.027466 | 0.027466 | 0.091553 | 0.027466 | -0.13275 | 0.09613 | 0.07782 | -0.054932 | 0.045776 | 0.045776 | -0.036621 | -0.09613 | 0.1236 | -0.036621 | -122.1863 | 0.13733 | 0.1236 | 0.16022 | -122.2137 | 0.059509 | 0 | -122.2321 | 0.19226 | 0.041198 | 0.041198 | -122.2321 | 0.18768 | 0.16022 | 0.1236 | -122.4106 | 0.14191 | 0.14191 | 0.17395 | -122.374
3289.8438 | 122.4426 | -0.054932 | 122.2321 | 0.14771 | 0.046768 | 0.062036 | -0.0012987 | 0.030183 | -0.003245 | 0.032355 | 0.16663 | 0.029401 | 0.037523 | 0.050951 | 0.0023135 | 0.024368 | 0.10986 | 0.11444 | 0.10986 | 0.068665 | 0.032043 | 0.036621 | -0.07782 | 0.14191 | 0.12817 | 0.022888 | 0.009155 | 0.004578 | 0.013733 | -0.054932 | 0.091553 | -0.022888 | -122.2 | 0.16937 | 0.1236 | 0.14649 | -122.1222 | 0.068665 | 0 | -122.2229 | 0.19684 | 0.07782 | 0.07782 | -122.2275 | 0.086975 | 0.16479 | 0.16479 | -122.3099 | 0.064087 | 0.05951 | 0.18311 | -122.287
3291.6094 | 122.3602 | -0.07782 | 122.2824 | -0.21088 | 0.047196 | 0.061823 | 0.0081007 | 0.031678 | -0.0058084 | 0.03086 | -0.13855 | 0.027692 | 0.036027 | 0.050951 | -0.0015317 | 0.02565 | 0.09613 | 0.10986 | 0.11902 | 0.068665 | 0.045776 | 0.050354 | -0.10071 | 0.11444 | 0.15106 | 0.022888 | 0.013733 | 0.022888 | -0.018311 | -0.086975 | 0.12817 | -0.022888 | -122.2366 | 0.18768 | 0.14649 | 0.16937 | -122.1863 | 0.059509 | -0.009155 | -122.2687 | 0.19226 | 0.10071 | 0.10986 | -122.2595 | 0.1236 | 0.17395 | 0.19684 | -122.3831 | 0.091553 | 0.10071 | 0.22888 | -122.3694
3293.375 | 122.3511 | -0.068665 | 122.2549 | 0.033264 | 0.047409 | 0.0599 | 0.0010511 | 0.03061 | 0.00081382 | 0.031287 | 0.044556 | 0.028333 | 0.03795 | 0.052447 | 0.0018863 | 0.023727 | -0.022888 | -0.050354 | -0.059509 | -0.018311 | 0.09613 | 0.018311 | -0.1236 | 0.032043 | -0.018311 | -0.1236 | 0.059509 | 0.036621 | -0.050354 | -0.10071 | 0.086976 | -0.054931 | -122.1588 | 0.018311 | 0.050354 | 0.10528 | -122.2778 | 0.018311 | -0.032043 | -122.1954 | 0.10071 | -0.054931 | -0.022888 | -122.2183 | 0.16479 | 0.045777 | 0.009156 | -122.3785 | 0.12817 | 0.10529 | 0.050354 | -122.3557
3295.0781 | 122.4426 | -0.032043 | 122.2412 | 0.10956 | 0.044632 | 0.060541 | 0.0010511 | 0.03061 | -0.0055948 | 0.032569 | 0.15137 | 0.029401 | 0.035814 | 0.050951 | 0.0020999 | 0.023086 | 0.10529 | 0.10071 | 0.09613 | 0.082397 | 0.032043 | 0.050354 | -0.09613 | 0.15564 | 0.14191 | 0.036621 | 0.018311 | -0.004578 | -0.009155 | -0.059509 | 0.082397 | -0.064087 | -122.2092 | 0.13275 | 0.11444 | 0.17853 | -122.1359 | 0.022888 | -0.027466 | -122.2229 | 0.18768 | 0.068664 | 0.09613 | -122.2458 | 0.064086 | 0.13733 | 0.12817 | -122.3373 | 0.050354 | 0.027465 | 0.17395 | -122.3007
3296.8594 | 122.3236 | -0.10529 | 122.2504 | -0.058289 | 0.045914 | 0.060327 | 0.0021191 | 0.033387 | 0.00081382 | 0.032569 | -0.062256 | 0.029828 | 0.036668 | 0.053087 | 0.0018863 | 0.0233 | 0.050354 | 0.009155 | -0.004578 | 0.018311 | 0.064087 | 0.032043 | -0.10986 | 0.041199 | 0.041199 | -0.09613 | 0.068665 | 0.032043 | -0.054932 | -0.10529 | 0.13733 | -0.004577 | -122.1863 | 0.11444 | 0.1236 | 0.12817 | -122.2 | 0.050354 | 0 | -122.1817 | 0.14649 | 0.009156 | 0.009156 | -122.2183 | 0.16937 | 0.15564 | 0.10071 | -122.3602 | 0.17395 | 0.13733 | 0.14649 | -122.3557
3298.5625 | 122.4518 | -0.050354 | 122.2183 | -0.11932 | 0.044419 | 0.062036 | 0.0055371 | 0.030183 | -0.0092264 | 0.031501 | -0.1004 | 0.027478 | 0.036668 | 0.051165 | -0.0030271 | 0.025222 | 0.068665 | 0.12817 | 0.11444 | 0.073242 | 0.045776 | 0.059509 | -0.09613 | 0.14648 | 0.16479 | 0.082397 | 0.027466 | 0.013733 | -0.018311 | -0.07782 | 0.10986 | -0.045776 | -122.1725 | 0.17853 | 0.1236 | 0.16937 | -122.1497 | 0.032043 | -0.027466 | -122.1909 | 0.19684 | 0.13275 | 0.16022 | -122.2046 | 0.09613 | 0.11902 | 0.16479 | -122.3145 | 0.07782 | 0.064087 | 0.21515 | -122.2961
3300.3281 | 122.4197 | -0.064087 | 122.2366 | 0.10956 | 0.046128 | 0.059473 | -0.00044435 | 0.03061 | -0.00025418 | 0.031074 | 0.029297 | 0.029828 | 0.036027 | 0.050951 | 0.0025271 | 0.024368 | 0.004578 | -0.036621 | -0.036621 | -0.009155 | 0.086975 | 0.018311 | -0.12817 | 0.050354 | -0.004578 | -0.10071 | 0.068665 | 0.050354 | -0.045776 | -0.10071 | 0.082398 | -0.064087 | -122.1497 | 0.027466 | 0.054932 | 0.11902 | -122.2321 | 0.018311 | -0.036621 | -122.168 | 0.11444 | -0.036621 | 0 | -122.1863 | 0.15106 | 0.068665 | 0.027466 | -122.3648 | 0.13275 | 0.11444 | 0.059509 | -122.3373
3302.1094 | 122.4014 | -0.07782 | 122.2504 | 0.16296 | 0.045273 | 0.060114 | 0.0012647 | 0.029969 | -0.0040994 | 0.032142 | 0.14374 | 0.027692 | 0.034959 | 0.048601 | -0.0015317 | 0.024368 | 0.082397 | 0.11902 | 0.10071 | 0.068665 | 0.045776 | 0.054932 | -0.09613 | 0.15564 | 0.14191 | 0.036621 | -0.004578 | -0.009155 | -0.013733 | -0.064087 | 0.13275 | -0.01831 | -122.2046 | 0.19684 | 0.14649 | 0.16479 | -122.168 | 0.064087 | 0.013733 | -122.2549 | 0.23346 | 0.11444 | 0.10071 | -122.2595 | 0.1236 | 0.16022 | 0.17853 | -122.3465 | 0.073242 | 0.068665 | 0.21973 | -122.3145
3303.8125 | 122.3785 | -0.091553 | 122.287 | -0.24902 | 0.047409 | 0.059686 | 0.0040417 | 0.033387 | -0.0019632 | 0.031501 | -0.19958 | 0.029401 | 0.035173 | 0.055651 | -0.00024989 | 0.025436 | 0 | -0.022888 | -0.032043 | 0 | 0.082397 | 0.009155 | -0.12817 | 0.018311 | 0.041199 | -0.091553 | 0.068665 | 0.050354 | -0.050354 | -0.11444 | 0.10071 | -0.036621 | -122.2046 | 0.068665 | 0.091553 | 0.12817 | -122.287 | 0.041199 | -0.022888 | -122.2183 | 0.10986 | 0 | 0.022888 | -122.2366 | 0.17395 | 0.091553 | 0.05951 | -122.4152 | 0.16022 | 0.14191 | 0.13275 | -122.4014
3305.5625 | 122.4655 | -0.050354 | 122.2321 | -0.14221 | 0.043564 | 0.062677 | 0.0036145 | 0.03296 | -0.0079446 | 0.029578 | -0.069885 | 0.02876 | 0.037309 | 0.053301 | -0.0043087 | 0.023513 | 0.073242 | 0.11444 | 0.10529 | 0.054932 | 0.050354 | 0.045776 | -0.073242 | 0.16022 | 0.16937 | 0.068665 | 0.009155 | 0.013733 | -0.018311 | -0.059509 | 0.09613 | -0.022888 | -122.1817 | 0.16479 | 0.10529 | 0.12817 | -122.1588 | 0.032043 | -0.009155 | -122.2229 | 0.21057 | 0.11902 | 0.12817 | -122.2183 | 0.10071 | 0.1236 | 0.15564 | -122.3053 | 0.059509 | 0.064087 | 0.21973 | -122.2916
3307.3125 | 122.3877 | -0.073242 | 122.2504 | 0.094299 | 0.049332 | 0.060968 | -0.00044435 | 0.032533 | 0.0010276 | 0.03086 | 0.082703 | 0.029828 | 0.035387 | 0.049883 | 0.0014591 | 0.022659 | 0.004578 | -0.045776 | -0.041199 | -0.032043 | 0.086975 | 0.009155 | -0.11902 | 0.032043 | -0.009155 | -0.10529 | 0.032043 | 0.045776 | -0.045776 | -0.10986 | 0.082397 | -0.045777 | -122.1634 | 0.027466 | 0.041199 | 0.086976 | -122.2458 | 0.027466 | -0.036621 | -122.2183 | 0.10529 | -0.032044 | 0.004577 | -122.2046 | 0.16022 | 0.07782 | 0.032043 | -122.3694 | 0.10529 | 0.11902 | 0.064087 | -122.3602
3309.0781 | 122.3419 | -0.09613 | 122.2687 | -0.26428 | 0.046768 | 0.062891 | 0.0061781 | 0.032746 | -0.0040994 | 0.029151 | -0.15381 | 0.029615 | 0.034959 | 0.051165 | -0.00089089 | 0.0233 | 0.022888 | 0.041199 | 0.027466 | 0.013733 | 0.064087 | 0.004578 | -0.1236 | 0.036621 | 0.045776 | -0.07782 | 0.054932 | 0.032043 | -0.059509 | -0.13275 | 0.10071 | -0.027466 | -122.2046 | 0.13733 | 0.10986 | 0.13733 | -122.2458 | 0.036621 | -0.036621 | -122.2137 | 0.13275 | 0.01831 | 0.054931 | -122.2366 | 0.16022 | 0.11902 | 0.1236 | -122.3923 | 0.15106 | 0.12817 | 0.14191 | -122.4014
3310.7812 | 122.406 | -0.059509 | 122.2458 | 0.079041 | 0.045273 | 0.061609 | 0.0057507 | 0.031465 | -0.006663 | 0.030433 | 0.090332 | 0.027265 | 0.039232 | 0.052019 | -0.0013181 | 0.024368 | 0.050354 | 0.07782 | 0.07782 | 0.027466 | 0.054932 | 0.050354 | -0.086975 | 0.10529 | 0.091553 | 0.004578 | 0.027466 | 0.009155 | -0.022888 | -0.068665 | 0.10986 | -0.027466 | -122.1909 | 0.13733 | 0.086975 | 0.11444 | -122.1954 | 0.036621 | -0.009156 | -122.2183 | 0.16479 | 0.064087 | 0.073243 | -122.2366 | 0.11444 | 0.10986 | 0.13733 | -122.3328 | 0.086975 | 0.068664 | 0.15106 | -122.3145
3312.5312 | 122.4243 | -0.059509 | 122.2458 | 0.11719 | 0.041642 | 0.060541 | -0.0019397 | 0.029542 | -0.0023904 | 0.031501 | 0.090332 | 0.027906 | 0.036027 | 0.052019 | 0.0012455 | 0.023513 | 0.091553 | 0.11444 | 0.11444 | 0.064087 | 0.036621 | 0.064087 | -0.068665 | 0.15106 | 0.12817 | 0.036621 | 0.009155 | -0.004578 | -0.013733 | -0.064087 | 0.1236 | -0.009156 | -122.2092 | 0.17395 | 0.1236 | 0.13275 | -122.1542 | 0.045776 | -0.004578 | -122.2366 | 0.21057 | 0.09613 | 0.10071 | -122.2504 | 0.09613 | 0.15106 | 0.17395 | -122.3145 | 0.068664 | 0.054931 | 0.18768 | -122.3099
3314.2812 | 122.406 | -0.064087 | 122.2412 | 0.12482 | 0.042496 | 0.062677 | 0.0036145 | 0.032319 | -0.0019632 | 0.030219 | 0.10559 | 0.025342 | 0.035173 | 0.050738 | 0.0038089 | 0.02565 | 0.082397 | 0.11902 | 0.10529 | 0.064087 | 0.045776 | 0.064087 | -0.082397 | 0.15564 | 0.13275 | 0.027466 | 0.018311 | 0.013733 | -0.013733 | -0.064087 | 0.12817 | -0.01831 | -122.1954 | 0.18311 | 0.12817 | 0.14648 | -122.1588 | 0.050354 | 0 | -122.2229 | 0.21973 | 0.091553 | 0.091553 | -122.2275 | 0.10986 | 0.14648 | 0.16937 | -122.3236 | 0.082398 | 0.07782 | 0.19684 | -122.3053
3316.0312 | 122.4518 | -0.041199 | 122.2595 | 0.10193 | 0.046555 | 0.059686 | 0.00083745 | 0.029969 | -0.00046778 | 0.032355 | 0.11322 | 0.029615 | 0.036882 | 0.052447 | 0.0031681 | 0.022232 | 0 | 0.009155 | -0.018311 | 0 | 0.082397 | 0.013733 | -0.10986 | 0.086975 | 0.054932 | -0.032043 | 0.045776 | 0.032043 | -0.036621 | -0.09613 | 0.054932 | -0.068664 | -122.1771 | 0.050354 | 0.041199 | 0.10986 | -122.2595 | 0.004578 | -0.054931 | -122.2137 | 0.12817 | 0.009156 | 0.064087 | -122.2275 | 0.1236 | 0.041199 | 0.022888 | -122.3694 | 0.086975 | 0.073242 | 0.096131 | -122.3557
3317.7812 | 122.4243 | -0.082397 | 122.2229 | 0.018005 | 0.039719 | 0.059259 | 0.0025465 | 0.029115 | -0.0073038 | 0.031714 | 0.067444 | 0.025342 | 0.034105 | 0.050951 | -0.0015317 | 0.025222 | 0.045776 | 0.050354 | 0.059509 | 0.032043 | 0.054932 | 0.041199 | -0.11444 | 0.086975 | 0.082397 | 0.009155 | 0.036621 | 0.013733 | -0.013733 | -0.068665 | 0.1236 | -0.032044 | -122.168 | 0.13275 | 0.11444 | 0.14648 | -122.1771 | 0.068664 | 0.013732 | -122.1863 | 0.16937 | 0.091552 | 0.07782 | -122.2092 | 0.13733 | 0.12817 | 0.14191 | -122.3373 | 0.11902 | 0.09613 | 0.16479 | -122.2916
3319.4844 | 122.4152 | -0.082397 | 122.2137 | 0.15533 | 0.045487 | 0.061395 | 0.00062385 | 0.031037 | -0.0038858 | 0.032783 | 0.13611 | 0.02641 | 0.036455 | 0.051165 | 0.0012455 | 0.023086 | 0.091553 | 0.1236 | 0.1236 | 0.073242 | 0.036621 | 0.059509 | -0.082397 | 0.16479 | 0.13275 | 0.032043 | 0.018311 | -0.004578 | -0.018311 | -0.064087 | 0.14191 | 0 | -122.1771 | 0.20599 | 0.15564 | 0.15564 | -122.1222 | 0.064086 | 0.01831 | -122.1954 | 0.24719 | 0.11444 | 0.09613 | -122.2183 | 0.11902 | 0.17395 | 0.20599 | -122.2961 | 0.10071 | 0.077819 | 0.21515 | -122.2778
3321.2344 | 122.406 | -0.064087 | 122.2092 | 0.094299 | 0.044846 | 0.060968 | 0.0057507 | 0.031465 | -0.0045266 | 0.032783 | 0.13611 | 0.02641 | 0.036241 | 0.053301 | -3.629e-05 | 0.023727 | 0.086975 | 0.10986 | 0.10529 | 0.045776 | 0.045776 | 0.050354 | -0.091553 | 0.1236 | 0.091553 | -0.004578 | 0.013733 | 0.004578 | -0.018311 | -0.064087 | 0.11444 | -0.027466 | -122.1634 | 0.17395 | 0.10986 | 0.13733 | -122.1222 | 0.045776 | 0 | -122.1954 | 0.18768 | 0.059509 | 0.059509 | -122.2046 | 0.10986 | 0.15106 | 0.16937 | -122.3007 | 0.07782 | 0.068665 | 0.15564 | -122.2733
3322.9219 | 122.3923 | -0.082397 | 122.2366 | -0.21851 | 0.046982 | 0.0599 | 0.0072461 | 0.033174 | 0.00081382 | 0.030219 | -0.23773 | 0.028119 | 0.038377 | 0.050951 | 0.00060451 | 0.021377 | 0.022888 | 0 | -0.027466 | 0.009155 | 0.091553 | 0.004578 | -0.1236 | 0.022888 | 0.045776 | -0.10071 | 0.059509 | 0.045776 | -0.032043 | -0.10986 | 0.086975 | -0.041199 | -122.1451 | 0.082397 | 0.091552 | 0.13275 | -122.2137 | 0.050354 | -0.027466 | -122.1771 | 0.10528 | -0.018311 | 0.009155 | -122.1909 | 0.17395 | 0.10528 | 0.054931 | -122.3602 | 0.14191 | 0.12817 | 0.12817 | -122.3465
3324.6875 | 122.3419 | -0.091553 | 122.2778 | -0.25665 | 0.047409 | 0.060327 | 0.0031873 | 0.029115 | -0.0011088 | 0.03086 | -0.25299 | 0.025769 | 0.0356 | 0.052447 | -0.00067729 | 0.023941 | 0.013733 | 0.022888 | 0.004578 | 0 | 0.07782 | 0 | -0.1236 | 0.045776 | 0.045776 | -0.073242 | 0.059509 | 0.054932 | -0.059509 | -0.10071 | 0.091553 | -0.032043 | -122.2 | 0.11444 | 0.091553 | 0.1236 | -122.2641 | 0.032044 | -0.009155 | -122.2183 | 0.13733 | 0.018311 | 0.027466 | -122.2229 | 0.16937 | 0.10529 | 0.096131 | -122.4014 | 0.15106 | 0.14649 | 0.13733 | -122.3785
3326.4375 | 122.3282 | -0.10529 | 122.2778 | -0.22614 | 0.049546 | 0.060327 | 0.0068189 | 0.032746 | -0.002604 | 0.030219 | -0.19196 | 0.028546 | 0.038805 | 0.051592 | -0.00024989 | 0.021591 | -0.004578 | 0.022888 | -0.004578 | -0.013733 | 0.073242 | 0.022888 | -0.13733 | 0.045776 | 0.059509 | -0.082397 | 0.068665 | 0.041199 | -0.059509 | -0.10986 | 0.12817 | -0.032043 | -122.2046 | 0.12817 | 0.091553 | 0.1236 | -122.2824 | 0.045777 | -0.004577 | -122.2092 | 0.15106 | 0.022889 | 0.027466 | -122.2366 | 0.17853 | 0.10071 | 0.10071 | -122.4152 | 0.17395 | 0.14649 | 0.16479 | -122.3877
3328.125 | 122.3602 | -0.10529 | 122.2595 | 0.033264 | 0.046982 | 0.059473 | 0.0025465 | 0.031678 | 0.0016684 | 0.03556 | -0.0012209 | 0.029615 | 0.036241 | 0.052447 | 0.0020999 | 0.024795 | -0.009155 | -0.041199 | -0.050354 | -0.032043 | 0.091553 | 0 | -0.11444 | 0.032043 | -0.009155 | -0.10529 | 0.073242 | 0.036621 | -0.045776 | -0.091553 | 0.10529 | -0.009155 | -122.168 | 0.064087 | 0.073243 | 0.082398 | -122.2687 | 0.05951 | 0.013733 | -122.1863 | 0.13733 | 0 | -0.013733 | -122.2229 | 0.19684 | 0.096131 | 0.054932 | -122.374 | 0.17853 | 0.14191 | 0.096131 | -122.3511
3329.9062 | 122.4472 | -0.054932 | 122.2321 | -0.14221 | 0.043991 | 0.060754 | 0.0023329 | 0.031037 | -0.0079446 | 0.029365 | -0.11566 | 0.025342 | 0.036241 | 0.050524 | -0.0034543 | 0.025009 | 0.07782 | 0.17853 | 0.1236 | 0.073242 | 0.059509 | 0.059509 | -0.086975 | 0.15564 | 0.1831 | 0.050354 | 0.022888 | 0.013733 | -0.013733 | -0.091553 | 0.11444 | -0.032043 | -122.1725 | 0.23346 | 0.12817 | 0.16022 | -122.1542 | 0.041199 | -0.036621 | -122.2092 | 0.21057 | 0.10529 | 0.14191 | -122.2183 | 0.11444 | 0.13275 | 0.17853 | -122.319 | 0.07782 | 0.068665 | 0.23804 | -122.3236
3331.6562 | 122.3465 | -0.10529 | 122.2961 | -0.23376 | 0.046341 | 0.060114 | 0.0023329 | 0.030824 | -0.0045266 | 0.031287 | -0.2301 | 0.027906 | 0.037309 | 0.050524 | -0.00024989 | 0.024795 | -0.018311 | 0.013733 | -0.018311 | -0.018311 | 0.091553 | 0.018311 | -0.10529 | 0.036621 | 0.036621 | -0.086975 | 0.059509 | 0.054932 | -0.064087 | -0.10071 | 0.1236 | 0 | -122.2046 | 0.11902 | 0.086975 | 0.086975 | -122.3145 | 0.041199 | 0.004578 | -122.2366 | 0.14191 | 0.018311 | 0.013733 | -122.2412 | 0.19684 | 0.086975 | 0.086975 | -122.4014 | 0.16479 | 0.16022 | 0.14191 | -122.3969
3333.4062 | 122.4564 | -0.054932 | 122.2183 | -0.0048827 | 0.043778 | 0.06225 | 0.0038281 | 0.028047 | -0.006022 | 0.031074 | 0.014038 | 0.025769 | 0.038164 | 0.052233 | -0.0015317 | 0.025009 | 0 | 0.073242 | 0.045776 | 0.027466 | 0.064087 | 0.041199 | -0.09613 | 0.09613 | 0.091553 | 0.013733 | 0.032043 | 0.013733 | -0.032043 | -0.082397 | 0.096131 | -0.041198 | -122.1542 | 0.12817 | 0.082398 | 0.1236 | -122.2183 | 0.022889 | -0.027465 | -122.1863 | 0.15106 | 0.068665 | 0.09613 | -122.2046 | 0.11902 | 0.054932 | 0.10071 | -122.3145 | 0.086975 | 0.068665 | 0.14649 | -122.3007
3335.1719 | 122.4609 | -0.054932 | 122.2275 | -0.12695 | 0.045487 | 0.063532 | 0.0019055 | 0.030824 | -0.0073038 | 0.029578 | -0.077515 | 0.02641 | 0.036241 | 0.050097 | -0.00089089 | 0.0233 | 0.07782 | 0.15564 | 0.11444 | 0.064087 | 0.059509 | 0.050354 | -0.082397 | 0.17853 | 0.17853 | 0.082397 | 0.004578 | 0 | -0.032043 | -0.068665 | 0.10529 | -0.027465 | -122.168 | 0.21057 | 0.11902 | 0.14648 | -122.1497 | 0.022889 | -0.013733 | -122.2229 | 0.23346 | 0.13733 | 0.15106 | -122.2275 | 0.11444 | 0.13275 | 0.16937 | -122.3099 | 0.05951 | 0.054932 | 0.23346 | -122.2961
3336.875 | 122.4426 | -0.045776 | 122.2183 | 0.094299 | 0.04506 | 0.058405 | 0.0021191 | 0.031251 | -0.0013224 | 0.030219 | 0.14374 | 0.027906 | 0.037523 | 0.052019 | 0.00081811 | 0.022018 | 0.09613 | 0.12817 | 0.086975 | 0.082397 | 0.036621 | 0.059509 | -0.086975 | 0.16022 | 0.13275 | 0.022888 | 0.018311 | 0 | -0.009155 | -0.059509 | 0.10528 | -0.041199 | -122.1817 | 0.17395 | 0.12817 | 0.16937 | -122.1222 | 0.036621 | -0.013733 | -122.2 | 0.20599 | 0.068664 | 0.082397 | -122.2183 | 0.082397 | 0.14191 | 0.13275 | -122.3053 | 0.064087 | 0.045776 | 0.17853 | -122.2778
3338.6406 | 122.4243 | -0.059509 | 122.2595 | 0.08667 | 0.043351 | 0.063318 | 0.0036145 | 0.033387 | -0.004954 | 0.030006 | 0.090332 | 0.025983 | 0.037736 | 0.05266 | -0.0011045 | 0.023513 | 0.041199 | 0.10529 | 0.082397 | 0.032043 | 0.045776 | 0.050354 | -0.086975 | 0.11444 | 0.10986 | -0.004578 | 0.018311 | 0.018311 | -0.022888 | -0.064087 | 0.10986 | -0.027466 | -122.2137 | 0.16479 | 0.091552 | 0.11902 | -122.2183 | 0.036621 | -0.004578 | -122.2412 | 0.17395 | 0.054931 | 0.059509 | -122.2412 | 0.10528 | 0.10071 | 0.14191 | -122.3465 | 0.07782 | 0.07782 | 0.16937 | -122.3236
3340.4062 | 122.438 | -0.059509 | 122.2321 | 0.018005 | 0.043991 | 0.060968 | 0.0040417 | 0.031678 | -0.0070902 | 0.028083 | 0.029297 | 0.025556 | 0.037309 | 0.050951 | -0.00067729 | 0.022873 | 0.018311 | 0.068665 | 0.045776 | 0.032043 | 0.059509 | 0.050354 | -0.086975 | 0.086975 | 0.07782 | -0.009155 | 0.018311 | -0.009155 | -0.018311 | -0.082397 | 0.10986 | -0.027466 | -122.1725 | 0.12817 | 0.091552 | 0.11902 | -122.2137 | 0.041198 | -0.022888 | -122.2137 | 0.14648 | 0.050354 | 0.073242 | -122.2412 | 0.11902 | 0.07782 | 0.10528 | -122.319 | 0.07782 | 0.050354 | 0.13733 | -122.3145
3342.1875 | 122.4426 | -0.041199 | 122.2183 | 0.071411 | 0.043137 | 0.062463 | 0.00041005 | 0.031678 | -0.00025418 | 0.031928 | 0.11322 | 0.028546 | 0.036241 | 0.052019 | 0.0042361 | 0.0233 | 0.09613 | 0.11444 | 0.082397 | 0.07782 | 0.045776 | 0.059509 | -0.073242 | 0.16937 | 0.11444 | 0.022888 | 0.013733 | -0.004578 | -0.009155 | -0.059509 | 0.10071 | -0.032043 | -122.1725 | 0.15564 | 0.11902 | 0.15106 | -122.1222 | 0.032044 | -0.01831 | -122.2046 | 0.21057 | 0.064087 | 0.082397 | -122.2229 | 0.086975 | 0.13733 | 0.1236 | -122.2916 | 0.054932 | 0.036621 | 0.15564 | -122.2778
3343.9531 | 122.4792 | -0.050354 | 122.2183 | -0.073547 | 0.044419 | 0.059473 | 0.0031873 | 0.031678 | -0.0075174 | 0.031074 | -0.077515 | 0.026837 | 0.035173 | 0.049029 | 0.00039091 | 0.024368 | 0.059509 | 0.10529 | 0.086975 | 0.045776 | 0.054932 | 0.050354 | -0.10529 | 0.15564 | 0.16479 | 0.054932 | 0.045776 | 0.004578 | -0.018311 | -0.068665 | 0.10071 | -0.054932 | -122.1634 | 0.15564 | 0.09613 | 0.15106 | -122.1588 | 0.032043 | -0.018311 | -122.1725 | 0.20599 | 0.10529 | 0.1236 | -122.2137 | 0.10529 | 0.10986 | 0.13733 | -122.3236 | 0.09613 | 0.054932 | 0.21515 | -122.287
3345.6406 | 122.4472 | -0.054932 | 122.2366 | -0.14221 | 0.044632 | 0.060968 | 0.0053235 | 0.031678 | -0.0053812 | 0.029151 | -0.13092 | 0.027906 | 0.034532 | 0.052019 | -0.0023861 | 0.0233 | 0.11902 | 0.17395 | 0.13275 | 0.073242 | 0.041199 | 0.050354 | -0.091553 | 0.16022 | 0.1831 | 0.059509 | 0.022888 | 0.009155 | -0.009155 | -0.059509 | 0.10529 | -0.036621 | -122.1954 | 0.22888 | 0.12817 | 0.16479 | -122.1176 | 0.045777 | -0.004577 | -122.2137 | 0.21515 | 0.11444 | 0.11902 | -122.2275 | 0.096131 | 0.17395 | 0.18768 | -122.3282 | 0.07782 | 0.064087 | 0.23804 | -122.2961
3347.3281 | 122.4701 | -0.054932 | 122.2183 | -0.081177 | 0.043991 | 0.059686 | 0.0038281 | 0.031251 | -0.0058084 | 0.030646 | -0.092773 | 0.025556 | 0.038805 | 0.051806 | -0.00089089 | 0.022873 | 0.09613 | 0.13733 | 0.10529 | 0.073242 | 0.054932 | 0.050354 | -0.086975 | 0.19226 | 0.17853 | 0.073242 | 0.013733 | -0.004578 | -0.009155 | -0.064087 | 0.10529 | -0.032043 | -122.1634 | 0.19226 | 0.12817 | 0.16022 | -122.1222 | 0.045777 | -0.009155 | -122.2046 | 0.24719 | 0.12817 | 0.13733 | -122.2229 | 0.10986 | 0.15106 | 0.16022 | -122.3053 | 0.068665 | 0.050354 | 0.23346 | -122.2824
3349.0938 | 122.3602 | -0.086975 | 122.2504 | 0.071411 | 0.046982 | 0.059045 | -0.00044435 | 0.029969 | 0.0038046 | 0.031714 | 0.044556 | 0.03111 | 0.036455 | 0.054583 | 0.0033817 | 0.026077 | 0.018311 | -0.041199 | -0.045776 | -0.018311 | 0.091553 | 0.013733 | -0.11902 | 0.059509 | -0.027466 | -0.11902 | 0.050354 | 0.041199 | -0.050354 | -0.086975 | 0.10071 | -0.032044 | -122.1588 | 0.045776 | 0.068664 | 0.10071 | -122.2321 | 0.036621 | 0 | -122.2 | 0.14648 | -0.032044 | -0.032044 | -122.2092 | 0.17853 | 0.10529 | 0.041199 | -122.3694 | 0.13733 | 0.12817 | 0.059509 | -122.3373
3350.7812 | 122.4152 | -0.068665 | 122.2321 | 0.040894 | 0.04271 | 0.060754 | -1.7146e-05 | 0.032533 | -0.0068766 | 0.031501 | 0.044556 | 0.027692 | 0.034318 | 0.051592 | 0.00060451 | 0.026718 | 0.041199 | 0.073242 | 0.050354 | 0.022888 | 0.045776 | 0.054932 | -0.09613 | 0.1236 | 0.10071 | -0.018311 | 0.032043 | 0.018311 | -0.018311 | -0.068665 | 0.1236 | -0.027465 | -122.1863 | 0.14191 | 0.091553 | 0.11902 | -122.1909 | 0.050354 | 0 | -122.2 | 0.19226 | 0.050354 | 0.050354 | -122.2137 | 0.11444 | 0.10986 | 0.11902 | -122.3282 | 0.10071 | 0.086976 | 0.16937 | -122.3007
3352.5469 | 122.3877 | -0.082397 | 122.2549 | -0.15747 | 0.047196 | 0.060114 | 0.0057507 | 0.031678 | 0.00038662 | 0.03321 | -0.20721 | 0.027692 | 0.036027 | 0.053728 | 0.0031681 | 0.021377 | 0.068665 | 0.018311 | 0.009155 | 0.018311 | 0.086975 | 0.018311 | -0.12817 | 0.07782 | 0.064087 | -0.054932 | 0.050354 | 0.045776 | -0.041199 | -0.086975 | 0.10071 | -0.045777 | -122.168 | 0.10071 | 0.10071 | 0.14649 | -122.1863 | 0.041198 | -0.004578 | -122.2046 | 0.16022 | 0.027465 | 0.032043 | -122.2092 | 0.16937 | 0.15106 | 0.091552 | -122.3831 | 0.13275 | 0.12817 | 0.14648 | -122.3419
3354.3125 | 122.438 | -0.064087 | 122.2275 | -0.14221 | 0.04506 | 0.063104 | 0.0044691 | 0.029115 | -0.008372 | 0.032142 | -0.1004 | 0.025983 | 0.037309 | 0.05031 | -0.0013181 | 0.024795 | 0.09613 | 0.16022 | 0.11444 | 0.07782 | 0.032043 | 0.059509 | -0.091553 | 0.16479 | 0.19684 | 0.059509 | 0.009155 | -0.004578 | -0.022888 | -0.07782 | 0.1236 | -0.027466 | -122.1954 | 0.2243 | 0.14191 | 0.16937 | -122.1313 | 0.041199 | -0.013733 | -122.2183 | 0.22888 | 0.1236 | 0.13733 | -122.2321 | 0.09613 | 0.16022 | 0.17853 | -122.319 | 0.073242 | 0.059509 | 0.26093 | -122.3053
3356.0781 | 122.3831 | -0.082397 | 122.2549 | -0.18036 | 0.050186 | 0.059686 | 0.0040417 | 0.031465 | 0.00017302 | 0.032142 | -0.1767 | 0.028546 | 0.036241 | 0.051592 | 0.0010317 | 0.023727 | 0.041199 | 0.004578 | -0.009155 | 0.027466 | 0.086975 | 0.004578 | -0.13275 | 0.073242 | 0.091553 | -0.059509 | 0.064087 | 0.018311 | -0.036621 | -0.10529 | 0.086975 | -0.050354 | -122.168 | 0.086975 | 0.10986 | 0.16022 | -122.2137 | 0.045776 | -0.022889 | -122.1909 | 0.15564 | 0.022888 | 0.045777 | -122.2366 | 0.16937 | 0.1236 | 0.073242 | -122.3877 | 0.14648 | 0.10071 | 0.17395 | -122.3602
3357.7656 | 122.4243 | -0.050354 | 122.2504 | 0.14008 | 0.044419 | 0.059045 | 0.0027601 | 0.029328 | -0.003245 | 0.031714 | 0.16663 | 0.027051 | 0.036241 | 0.051806 | 0.00081811 | 0.025863 | 0.09613 | 0.13275 | 0.10071 | 0.073242 | 0.045776 | 0.054932 | -0.073242 | 0.16937 | 0.14648 | 0.032043 | -0.004578 | -0.009155 | -0.009155 | -0.07782 | 0.10529 | -0.022888 | -122.2046 | 0.18311 | 0.1236 | 0.14648 | -122.1542 | 0.041199 | -0.027466 | -122.2549 | 0.21973 | 0.082397 | 0.10986 | -122.2595 | 0.09613 | 0.14648 | 0.15106 | -122.3236 | 0.045776 | 0.041199 | 0.19684 | -122.3282
3359.5312 | 122.406 | -0.059509 | 122.2046 | 0.10956 | 0.045914 | 0.060114 | 0.0051099 | 0.031037 | -0.0064492 | 0.031714 | 0.10559 | 0.025769 | 0.03795 | 0.052233 | 0.0014591 | 0.026291 | 0.050354 | 0.10071 | 0.086975 | 0.041199 | 0.050354 | 0.054932 | -0.10071 | 0.11444 | 0.10529 | 0.004578 | 0.027466 | 0.009155 | -0.032043 | -0.064087 | 0.11444 | -0.041199 | -122.1542 | 0.16022 | 0.10071 | 0.14191 | -122.1542 | 0.027466 | -0.004578 | -122.1771 | 0.17395 | 0.064087 | 0.068665 | -122.1954 | 0.10986 | 0.10986 | 0.14648 | -122.3053 | 0.086975 | 0.068664 | 0.16479 | -122.2687
3361.2969 | 122.4701 | -0.045776 | 122.2366 | 0.14008 | 0.046341 | 0.060754 | 0.0016919 | 0.031678 | -0.0019632 | 0.034064 | 0.13611 | 0.028119 | 0.036241 | 0.052233 | 0.0040225 | 0.022873 | 0.07782 | 0.059509 | 0.064087 | 0.054932 | 0.064087 | 0.041199 | -0.10071 | 0.14191 | 0.11444 | 0.013733 | 0.009155 | 0.027466 | -0.018311 | -0.064087 | 0.086975 | -0.054932 | -122.1725 | 0.10528 | 0.10071 | 0.15564 | -122.1588 | 0.027465 | -0.018311 | -122.2275 | 0.18768 | 0.059509 | 0.07782 | -122.2092 | 0.10986 | 0.1236 | 0.10986 | -122.3373 | 0.054931 | 0.073242 | 0.16022 | -122.3007
3362.9844 | 122.4106 | -0.082397 | 122.2504 | 0.071411 | 0.04271 | 0.058618 | -0.00065795 | 0.032533 | -0.0070902 | 0.030006 | 0.15137 | 0.027051 | 0.034959 | 0.05266 | 0.0010317 | 0.024154 | 0.091553 | 0.11902 | 0.10071 | 0.045776 | 0.018311 | 0.054932 | -0.09613 | 0.14648 | 0.11444 | 0.027466 | 0.013733 | 0.009155 | -0.018311 | -0.073242 | 0.13733 | -0.013733 | -122.2321 | 0.20142 | 0.12817 | 0.14191 | -122.1588 | 0.064086 | 0.009155 | -122.2366 | 0.22888 | 0.10986 | 0.10071 | -122.2412 | 0.10071 | 0.17395 | 0.18311 | -122.3465 | 0.09613 | 0.091552 | 0.19684 | -122.3236
3364.75 | 122.319 | -0.10529 | 122.2504 | -0.0354 | 0.048264 | 0.060541 | 0.0038281 | 0.030183 | 0.0010276 | 0.033851 | -0.046997 | 0.029187 | 0.035814 | 0.053728 | 0.0044497 | 0.025436 | 0.050354 | 0.018311 | 0.004578 | 0.018311 | 0.073242 | 0.027466 | -0.1236 | 0.059509 | 0.027466 | -0.10529 | 0.041199 | 0.022888 | -0.045776 | -0.10986 | 0.13275 | -0.01831 | -122.1771 | 0.1236 | 0.1236 | 0.14191 | -122.2 | 0.05951 | -0.004577 | -122.2092 | 0.16479 | 0 | 0.004577 | -122.2275 | 0.17853 | 0.15564 | 0.10986 | -122.374 | 0.14649 | 0.12817 | 0.13275 | -122.3602
3366.5 | 122.3465 | -0.10071 | 122.2778 | 0.033264 | 0.046768 | 0.059045 | 0.00041005 | 0.032105 | -4.058e-05 | 0.035346 | 0.021668 | 0.028333 | 0.038377 | 0.050951 | 0.0044497 | 0.024795 | -0.022888 | -0.059509 | -0.045776 | -0.004578 | 0.10071 | 0.009155 | -0.13275 | 0.027466 | 0.009155 | -0.10071 | 0.068665 | 0.036621 | -0.041199 | -0.091553 | 0.10986 | -0.032043 | -122.1771 | 0.041199 | 0.09613 | 0.12817 | -122.3007 | 0.059509 | 0.009155 | -122.2092 | 0.12817 | 0 | -0.009155 | -122.2412 | 0.20142 | 0.07782 | 0.054932 | -122.4106 | 0.16937 | 0.13733 | 0.10986 | -122.3694
3368.2656 | 122.4014 | -0.073242 | 122.2366 | 0.10193 | 0.046982 | 0.060968 | 0.0019055 | 0.031037 | -0.00046778 | 0.032569 | 0.090332 | 0.032178 | 0.036027 | 0.05266 | 0.0025271 | 0.026291 | -0.022888 | -0.022888 | -0.050354 | -0.004578 | 0.07782 | 0.018311 | -0.1236 | 0.041199 | -0.004578 | -0.10529 | 0.059509 | 0.054932 | -0.054932 | -0.10071 | 0.091553 | -0.050354 | -122.1588 | 0.050354 | 0.068664 | 0.11902 | -122.2595 | 0.01831 | -0.027466 | -122.1771 | 0.11444 | -0.032044 | -0.004578 | -122.1817 | 0.15106 | 0.050354 | 0.022888 | -122.3602 | 0.13275 | 0.12817 | 0.068664 | -122.3373
3369.9688 | 122.4747 | -0.059509 | 122.2549 | -0.12695 | 0.044846 | 0.061609 | 0.0059643 | 0.029542 | -0.010508 | 0.031714 | -0.062256 | 0.026624 | 0.038805 | 0.050951 | -0.0047361 | 0.027145 | 0.07782 | 0.13275 | 0.12817 | 0.086975 | 0.045776 | 0.045776 | -0.10986 | 0.16022 | 0.20142 | 0.082397 | 0.018311 | 0.027466 | -0.013733 | -0.073242 | 0.10528 | -0.050354 | -122.2092 | 0.19226 | 0.14648 | 0.19684 | -122.1771 | 0.045776 | -0.013733 | -122.2366 | 0.21973 | 0.14191 | 0.15564 | -122.2275 | 0.10528 | 0.13733 | 0.18768 | -122.3648 | 0.07782 | 0.086975 | 0.26093 | -122.3282
3371.7344 | 122.3877 | -0.082397 | 122.2687 | -0.15747 | 0.047196 | 0.059686 | 0.0042555 | 0.031678 | -0.0013224 | 0.031714 | -0.18433 | 0.028546 | 0.037096 | 0.05501 | 0.00060451 | 0.023941 | 0.027466 | 0.027466 | 0.032043 | 0.032043 | 0.10071 | 0.018311 | -0.15564 | 0.07782 | 0.082397 | -0.054932 | 0.064087 | 0.027466 | -0.036621 | -0.09613 | 0.10071 | -0.073243 | -122.168 | 0.10986 | 0.11444 | 0.18768 | -122.2412 | 0.045776 | -0.013733 | -122.2046 | 0.16022 | 0.027465 | 0.041198 | -122.2412 | 0.18311 | 0.10986 | 0.11444 | -122.4243 | 0.14648 | 0.10986 | 0.16479 | -122.3648
3373.4844 | 122.4564 | -0.059509 | 122.2321 | 0.018005 | 0.045273 | 0.061395 | 0.0074597 | 0.029115 | -0.0090128 | 0.029792 | 0.059815 | 0.025556 | 0.038377 | 0.050097 | -0.0017453 | 0.026077 | -0.009155 | 0.054932 | 0.068665 | 0.032043 | 0.059509 | 0.054932 | -0.10529 | 0.082397 | 0.10529 | 0.013733 | 0.032043 | 0.018311 | -0.036621 | -0.086975 | 0.11444 | -0.045777 | -122.1725 | 0.11444 | 0.091552 | 0.13733 | -122.2412 | 0.022888 | -0.027466 | -122.2 | 0.14191 | 0.073242 | 0.10071 | -122.2137 | 0.11902 | 0.050354 | 0.12817 | -122.3373 | 0.091552 | 0.07782 | 0.16479 | -122.319
3375.2656 | 122.406 | -0.054932 | 122.2412 | 0.08667 | 0.042923 | 0.060968 | 0.0029737 | 0.031037 | -0.0038858 | 0.03321 | 0.12848 | 0.028119 | 0.036027 | 0.052447 | 0.00017731 | 0.024795 | 0.068665 | 0.09613 | 0.10529 | 0.041199 | 0.045776 | 0.045776 | -0.091553 | 0.12817 | 0.10529 | 0.022888 | 0.018311 | 0.013733 | -0.013733 | -0.054932 | 0.10071 | -0.036621 | -122.1954 | 0.15106 | 0.096131 | 0.13275 | -122.1725 | 0.041199 | 0 | -122.2229 | 0.18311 | 0.07782 | 0.07782 | -122.2275 | 0.10071 | 0.1236 | 0.16022 | -122.3328 | 0.073243 | 0.068665 | 0.16022 | -122.2961
3376.9688 | 122.374 | -0.07782 | 122.2229 | -0.13458 | 0.050186 | 0.056268 | 0.0029737 | 0.031678 | -4.058e-05 | 0.032142 | -0.16144 | 0.028119 | 0.037523 | 0.054156 | 0.0033817 | 0.0233 | 0.064087 | 0.032043 | 0.009155 | 0.027466 | 0.082397 | 0.018311 | -0.1236 | 0.07782 | 0.07782 | -0.059509 | 0.050354 | 0.036621 | -0.041199 | -0.091553 | 0.096131 | -0.045776 | -122.1405 | 0.10986 | 0.10529 | 0.15106 | -122.1588 | 0.036621 | -0.013733 | -122.1725 | 0.15564 | 0.018311 | 0.032044 | -122.1863 | 0.16022 | 0.14191 | 0.086975 | -122.3465 | 0.12817 | 0.11444 | 0.15564 | -122.3145
3378.7188 | 122.406 | -0.082397 | 122.2412 | -0.18036 | 0.046128 | 0.060541 | 0.0070325 | 0.031465 | -0.007731 | 0.030219 | -0.15381 | 0.026837 | 0.036882 | 0.050951 | -0.0025999 | 0.026504 | 0.082397 | 0.14191 | 0.11444 | 0.073242 | 0.059509 | 0.041199 | -0.10071 | 0.12817 | 0.16022 | 0.050354 | 0.022888 | 0.004578 | -0.013733 | -0.045776 | 0.1236 | -0.018311 | -122.1817 | 0.2243 | 0.15564 | 0.17395 | -122.1588 | 0.068664 | 0.036621 | -122.2183 | 0.21057 | 0.13275 | 0.09613 | -122.2366 | 0.14191 | 0.16479 | 0.19684 | -122.3419 | 0.10528 | 0.086975 | 0.24261 | -122.287
3380.4844 | 122.374 | -0.082397 | 122.2687 | -0.14221 | 0.050186 | 0.060327 | 0.0027601 | 0.03296 | 0.0014548 | 0.032355 | -0.15381 | 0.029187 | 0.038805 | 0.054369 | 0.0027407 | 0.024368 | 0.059509 | 0.036621 | 0.018311 | 0.027466 | 0.082397 | 0.027466 | -0.11444 | 0.091553 | 0.07782 | -0.059509 | 0.041199 | 0.036621 | -0.045776 | -0.091553 | 0.10986 | -0.032044 | -122.1863 | 0.11902 | 0.10986 | 0.14191 | -122.2092 | 0.036621 | -0.009156 | -122.2275 | 0.17395 | 0.022888 | 0.032044 | -122.2321 | 0.16479 | 0.14191 | 0.10071 | -122.3831 | 0.1236 | 0.11902 | 0.16022 | -122.3602
3382.25 | 122.4106 | -0.082397 | 122.2275 | 0.040894 | 0.046982 | 0.060541 | 0.0023329 | 0.029542 | -0.0068766 | 0.031501 | 0.097962 | 0.026197 | 0.038591 | 0.051592 | -0.0015317 | 0.026718 | 0.022888 | 0.091553 | 0.07782 | 0.036621 | 0.050354 | 0.050354 | -0.068665 | 0.10071 | 0.091553 | 0.004578 | 0.027466 | 0.004578 | -0.013733 | -0.082397 | 0.13275 | 0.013732 | -122.1771 | 0.17395 | 0.11902 | 0.10529 | -122.2046 | 0.068664 | 0 | -122.2 | 0.18311 | 0.086975 | 0.086975 | -122.2229 | 0.13275 | 0.10528 | 0.16022 | -122.2961 | 0.10986 | 0.086975 | 0.17395 | -122.3099
3384.0156 | 122.3328 | -0.11444 | 122.2733 | -0.020142 | 0.04805 | 0.0599 | -0.00087155 | 0.031678 | 0.00060022 | 0.030219 | -0.031738 | 0.029187 | 0.036455 | 0.049883 | 0.0044497 | 0.025009 | 0.018311 | -0.050354 | -0.022888 | -0.009155 | 0.086975 | 0.013733 | -0.1236 | 0.013733 | 0.018311 | -0.10529 | 0.045776 | 0.045776 | -0.041199 | -0.11444 | 0.12817 | -0.009155 | -122.1863 | 0.064087 | 0.10529 | 0.11444 | -122.2549 | 0.073242 | 0 | -122.2275 | 0.12817 | 0.009155 | 0.009155 | -122.2275 | 0.20142 | 0.13275 | 0.091553 | -122.3969 | 0.16022 | 0.16022 | 0.13275 | -122.3877
3385.7188 | 122.3602 | -0.09613 | 122.2549 | -0.096436 | 0.050186 | 0.061182 | 0.0036145 | 0.029756 | -0.0013224 | 0.032996 | -0.13092 | 0.030683 | 0.039018 | 0.054369 | 0.0012455 | 0.024154 | 0.054932 | 0.041199 | 0.022888 | 0.013733 | 0.07782 | 0.027466 | -0.11444 | 0.07782 | 0.086975 | -0.041199 | 0.054932 | 0.036621 | -0.032043 | -0.10986 | 0.1236 | -0.018311 | -122.1771 | 0.13733 | 0.10986 | 0.12817 | -122.2 | 0.064087 | -0.013733 | -122.2 | 0.17395 | 0.054931 | 0.068664 | -122.2183 | 0.17395 | 0.15106 | 0.11902 | -122.3694 | 0.15106 | 0.13275 | 0.1831 | -122.3648
3387.4688 | 122.4106 | -0.064087 | 122.2321 | 0.08667 | 0.04271 | 0.059686 | 0.0019055 | 0.029756 | -0.0062356 | 0.029365 | 0.15137 | 0.029187 | 0.036027 | 0.052874 | 0.00060451 | 0.028427 | 0.059509 | 0.10529 | 0.10529 | 0.050354 | 0.041199 | 0.041199 | -0.073242 | 0.10529 | 0.10529 | 0.036621 | 0.036621 | 0.013733 | -0.022888 | -0.07782 | 0.10529 | -0.009155 | -122.1909 | 0.16937 | 0.11444 | 0.1236 | -122.1725 | 0.041199 | -0.013733 | -122.1954 | 0.16937 | 0.10071 | 0.11444 | -122.2183 | 0.10529 | 0.1236 | 0.16937 | -122.3053 | 0.10071 | 0.07782 | 0.16937 | -122.3099
3389.2344 | 122.4243 | -0.059509 | 122.2458 | 0.16296 | 0.044846 | 0.060541 | 0.00083745 | 0.030183 | -0.0047404 | 0.031501 | 0.15137 | 0.02876 | 0.034746 | 0.051592 | 0.0018863 | 0.025863 | 0.086975 | 0.11444 | 0.10529 | 0.073242 | 0.045776 | 0.064087 | -0.07782 | 0.16937 | 0.12817 | 0.041199 | 0.009155 | 0.013733 | -0.032043 | -0.073242 | 0.1236 | -0.018311 | -122.2 | 0.17395 | 0.13275 | 0.15106 | -122.1588 | 0.027466 | -0.013733 | -122.2366 | 0.22888 | 0.10071 | 0.11444 | -122.2321 | 0.10528 | 0.14648 | 0.16479 | -122.3236 | 0.068664 | 0.073242 | 0.18768 | -122.319
3391 | 122.4243 | -0.054932 | 122.2229 | 0.079041 | 0.04506 | 0.059686 | 0.0023329 | 0.030397 | -0.006022 | 0.031074 | 0.13611 | 0.025556 | 0.036882 | 0.05031 | 0.0014591 | 0.026077 | 0.086975 | 0.1236 | 0.10071 | 0.041199 | 0.041199 | 0.059509 | -0.091553 | 0.12817 | 0.10986 | 0.022888 | 0.009155 | 0.004578 | -0.027466 | -0.068665 | 0.11444 | -0.036621 | -122.1817 | 0.17853 | 0.096131 | 0.13275 | -122.1359 | 0.027466 | -0.013733 | -122.2137 | 0.18311 | 0.07782 | 0.091553 | -122.2183 | 0.096131 | 0.14191 | 0.15564 | -122.3145 | 0.064087 | 0.05951 | 0.16479 | -122.2916
3392.7031 | 122.4838 | -0.059509 | 122.2229 | -0.0354 | 0.045914 | 0.062891 | 0.0044691 | 0.029542 | -0.0068766 | 0.029365 | -0.0088499 | 0.02641 | 0.03795 | 0.051378 | -0.0011045 | 0.025009 | 0.027466 | 0.064087 | 0.082397 | 0.041199 | 0.050354 | 0.041199 | -0.091553 | 0.10986 | 0.1236 | 0.027466 | 0.018311 | 0 | -0.009155 | -0.068665 | 0.10071 | -0.032044 | -122.1725 | 0.1236 | 0.10071 | 0.13275 | -122.1954 | 0.050354 | -0.009156 | -122.2046 | 0.16937 | 0.086975 | 0.096131 | -122.2229 | 0.10986 | 0.086975 | 0.14191 | -122.3145 | 0.07782 | 0.059509 | 0.1831 | -122.2916
3394.4688 | 122.3694 | -0.11444 | 122.2595 | -0.22614 | 0.047623 | 0.060327 | 0.0068189 | 0.033387 | -0.0023904 | 0.027869 | -0.25299 | 0.028974 | 0.038591 | 0.051592 | -0.00067729 | 0.024368 | -0.004578 | -0.013733 | -0.022888 | -0.027466 | 0.10071 | 0.009155 | -0.12817 | 0.013733 | 0.036621 | -0.091553 | 0.068665 | 0.054932 | -0.059509 | -0.10986 | 0.1236 | -0.013733 | -122.1588 | 0.10071 | 0.086975 | 0.10071 | -122.2641 | 0.054932 | 0.004578 | -122.1909 | 0.12817 | 0.022888 | 0.01831 | -122.2046 | 0.21515 | 0.10986 | 0.091553 | -122.3877 | 0.18311 | 0.16937 | 0.15106 | -122.3694
3396.1562 | 122.4106 | -0.082397 | 122.2504 | 0.10956 | 0.042069 | 0.061395 | -0.0015125 | 0.030183 | -0.0040994 | 0.030433 | 0.11322 | 0.026624 | 0.037096 | 0.051592 | 0.0016727 | 0.026077 | 0.086975 | 0.12817 | 0.11444 | 0.064087 | 0.032043 | 0.050354 | -0.082397 | 0.14648 | 0.1236 | 0.041199 | 0.009155 | -0.004578 | -0.027466 | -0.07782 | 0.13275 | 0 | -122.2183 | 0.21057 | 0.14648 | 0.14648 | -122.1634 | 0.054931 | 0.004577 | -122.2412 | 0.22888 | 0.1236 | 0.11902 | -122.2549 | 0.11444 | 0.16937 | 0.19684 | -122.3328 | 0.091552 | 0.077819 | 0.20599 | -122.3282
3397.9062 | 122.4197 | -0.064087 | 122.2458 | 0.094299 | 0.040146 | 0.062463 | 0.0025465 | 0.031037 | -0.003245 | 0.029792 | 0.075073 | 0.025342 | 0.034959 | 0.051378 | -0.00067729 | 0.024582 | 0.082397 | 0.10071 | 0.086975 | 0.041199 | 0.041199 | 0.050354 | -0.07782 | 0.1236 | 0.09613 | 0.013733 | 0.013733 | 0.032043 | -0.032043 | -0.068665 | 0.11444 | -0.013733 | -122.2046 | 0.1648 | 0.10529 | 0.11902 | -122.1634 | 0.032044 | -0.004578 | -122.2321 | 0.18768 | 0.07782 | 0.082398 | -122.2137 | 0.10529 | 0.14648 | 0.15106 | -122.3236 | 0.07782 | 0.09613 | 0.16022 | -122.3145
3399.6094 | 122.4426 | -0.036621 | 122.2458 | 0.079041 | 0.045487 | 0.0599 | 0.0023329 | 0.029969 | 0.0020956 | 0.031928 | 0.036926 | 0.028333 | 0.037096 | 0.050951 | 0.0025271 | 0.024154 | 0.022888 | -0.013733 | -0.013733 | -0.018311 | 0.09613 | 0.022888 | -0.13733 | 0.068665 | 0.004578 | -0.064087 | 0.036621 | 0.027466 | -0.041199 | -0.091553 | 0.059509 | -0.10071 | -122.1497 | 0.022888 | 0.01831 | 0.11902 | -122.2229 | -0.004578 | -0.054932 | -122.2092 | 0.10529 | -0.027466 | 0.027466 | -122.2183 | 0.13275 | 0.059509 | 0.022888 | -122.3831 | 0.073242 | 0.064087 | 0.041199 | -122.3373
3401.3594 | 122.4518 | -0.064087 | 122.2183 | 0.071411 | 0.046768 | 0.060968 | 0.0034009 | 0.035096 | -0.0013224 | 0.031501 | 0.15137 | 0.027265 | 0.039445 | 0.05031 | 0.0027407 | 0.024154 | 0.10529 | 0.11902 | 0.09613 | 0.068665 | 0.054932 | 0.050354 | -0.082397 | 0.15564 | 0.13275 | 0.027466 | 0.027466 | -0.009155 | -0.009155 | -0.064087 | 0.11444 | -0.01831 | -122.1634 | 0.18311 | 0.13275 | 0.15106 | -122.113 | 0.054932 | 0 | -122.1909 | 0.21973 | 0.091553 | 0.091553 | -122.2275 | 0.11902 | 0.16937 | 0.16022 | -122.3007 | 0.091553 | 0.054932 | 0.19684 | -122.2824
3403.1094 | 122.4655 | -0.050354 | 122.2321 | 0.094299 | 0.047837 | 0.060754 | 0.00062385 | 0.029756 | -0.0023904 | 0.031501 | 0.082703 | 0.027692 | 0.036882 | 0.05031 | 0.0044497 | 0.026504 | 0.018311 | -0.009155 | -0.013733 | 0 | 0.086975 | 0.018311 | -0.1236 | 0.086975 | 0.018311 | -0.064087 | 0.041199 | 0.022888 | -0.045776 | -0.086975 | 0.068665 | -0.073242 | -122.1451 | 0.041199 | 0.050354 | 0.1236 | -122.2137 | 0.004578 | -0.036621 | -122.1909 | 0.13733 | -0.013733 | 0.022888 | -122.2092 | 0.13733 | 0.068665 | 0.036621 | -122.3557 | 0.091553 | 0.073242 | 0.068665 | -122.319
3404.875 | 122.3877 | -0.091553 | 122.2641 | -0.21088 | 0.046341 | 0.062036 | 0.0057507 | 0.030824 | -0.0017496 | 0.031714 | -0.20721 | 0.028119 | 0.03795 | 0.052233 | -0.00046349 | 0.026077 | -0.009155 | -0.004578 | -0.009155 | -0.009155 | 0.07782 | 0.009155 | -0.13733 | 0.036621 | 0.041199 | -0.07782 | 0.059509 | 0.036621 | -0.068665 | -0.10986 | 0.10071 | -0.045776 | -122.1863 | 0.086975 | 0.082398 | 0.12817 | -122.2733 | 0.022888 | -0.01831 | -122.2046 | 0.12817 | 0.013733 | 0.032043 | -122.2275 | 0.16937 | 0.082398 | 0.082398 | -122.4014 | 0.15106 | 0.12817 | 0.13275 | -122.374
3406.6562 | 122.4335 | -0.064087 | 122.2641 | 0.08667 | 0.04506 | 0.062036 | 0.0027601 | 0.031678 | -0.0087992 | 0.032996 | 0.14374 | 0.02641 | 0.036455 | 0.048174 | -0.00089089 | 0.026931 | 0.045776 | 0.13275 | 0.10071 | 0.045776 | 0.041199 | 0.064087 | -0.091553 | 0.10986 | 0.11444 | 0.013733 | 0.027466 | 0.018311 | 0 | -0.064087 | 0.12817 | -0.027466 | -122.2229 | 0.19684 | 0.10986 | 0.13733 | -122.2183 | 0.064087 | 0 | -122.2366 | 0.17395 | 0.07782 | 0.07782 | -122.2458 | 0.10529 | 0.10986 | 0.1648 | -122.3557 | 0.091553 | 0.082398 | 0.17853 | -122.3282
3408.3438 | 122.3969 | -0.059509 | 122.2549 | 0.079041 | 0.041428 | 0.060968 | 0.0038281 | 0.029115 | -0.0073038 | 0.031928 | 0.090332 | 0.02876 | 0.034959 | 0.05031 | 0.00017731 | 0.026931 | 0.041199 | 0.086975 | 0.064087 | 0.036621 | 0.050354 | 0.059509 | -0.086975 | 0.11444 | 0.091553 | -0.009155 | 0.027466 | 0.009155 | -0.027466 | -0.086975 | 0.11902 | -0.027466 | -122.2046 | 0.14648 | 0.09613 | 0.1236 | -122.2137 | 0.032043 | -0.027466 | -122.2275 | 0.17395 | 0.050354 | 0.07782 | -122.2458 | 0.10986 | 0.10071 | 0.1236 | -122.3419 | 0.086975 | 0.068664 | 0.15106 | -122.3419
3410.1094 | 122.3511 | -0.10071 | 122.2961 | -0.18036 | 0.046128 | 0.061182 | 0.0061781 | 0.031251 | -0.004954 | 0.031074 | -0.23773 | 0.025769 | 0.038164 | 0.049456 | -0.0028135 | 0.025009 | 0.07782 | 0.10071 | 0.09613 | 0.054932 | 0.059509 | 0.050354 | -0.082397 | 0.09613 | 0.13275 | 0 | 0.027466 | 0.022888 | -0.013733 | -0.068665 | 0.15106 | 0.018311 | -122.2366 | 0.20142 | 0.15564 | 0.13733 | -122.2183 | 0.086975 | 0.032043 | -122.2687 | 0.19684 | 0.10071 | 0.068665 | -122.2733 | 0.16022 | 0.17853 | 0.19684 | -122.3785 | 0.12817 | 0.1236 | 0.23346 | -122.3648
3411.8125 | 122.3145 | -0.10071 | 122.2641 | -0.04303 | 0.047837 | 0.058405 | 0.0019055 | 0.028688 | 0.0020956 | 0.03086 | 0.036926 | 0.027051 | 0.040514 | 0.054156 | 0.0042361 | 0.022445 | 0.059509 | 0.022888 | 0.009155 | 0.004578 | 0.073242 | 0.018311 | -0.13275 | 0.054932 | 0.018311 | -0.10071 | 0.045776 | 0.036621 | -0.041199 | -0.10071 | 0.11902 | -0.032043 | -122.1909 | 0.1236 | 0.10529 | 0.13733 | -122.2046 | 0.059509 | 0 | -122.2183 | 0.15564 | 0 | 0 | -122.2275 | 0.17395 | 0.16022 | 0.10986 | -122.3969 | 0.14648 | 0.13733 | 0.11902 | -122.3648
3413.5781 | 122.3373 | -0.10986 | 122.2412 | -0.27191 | 0.048905 | 0.059045 | 0.0061781 | 0.029969 | -0.0038858 | 0.030433 | -0.19196 | 0.027478 | 0.036455 | 0.051806 | -0.0017453 | 0.026931 | 0.036621 | 0.064087 | 0.045776 | 0.036621 | 0.064087 | 0.013733 | -0.12817 | 0.032043 | 0.068665 | -0.064087 | 0.050354 | 0.050354 | -0.059509 | -0.10071 | 0.1236 | -0.018311 | -122.1771 | 0.17395 | 0.14648 | 0.1648 | -122.2046 | 0.050354 | 0.009155 | -122.1909 | 0.14191 | 0.045776 | 0.036621 | -122.1909 | 0.17395 | 0.14648 | 0.15564 | -122.3694 | 0.16022 | 0.16022 | 0.17853 | -122.3419
3415.3438 | 122.3373 | -0.10071 | 122.2778 | -0.24902 | 0.04506 | 0.062677 | 0.0034009 | 0.032533 | -0.004313 | 0.033637 | -0.13855 | 0.028333 | 0.034959 | 0.050738 | 0.00039091 | 0.024795 | 0.022888 | 0.041199 | 0.018311 | 0.022888 | 0.073242 | 0.013733 | -0.11902 | 0.041199 | 0.045776 | -0.073242 | 0.045776 | 0.032043 | -0.036621 | -0.09613 | 0.11444 | -0.018311 | -122.2046 | 0.14191 | 0.1236 | 0.14191 | -122.2549 | 0.064087 | 0.004578 | -122.2321 | 0.14191 | 0.027466 | 0.022888 | -122.2458 | 0.17395 | 0.1236 | 0.11902 | -122.3969 | 0.14648 | 0.13275 | 0.14648 | -122.374
3417.1094 | 122.374 | -0.091553 | 122.2778 | -0.14984 | 0.046555 | 0.059686 | -1.7146e-05 | 0.029328 | 0.00081382 | 0.032355 | -0.16907 | 0.028974 | 0.035387 | 0.050738 | 0.0020999 | 0.023941 | 0.064087 | 0.032043 | -0.004578 | 0.032043 | 0.082397 | 0.036621 | -0.13275 | 0.07782 | 0.082397 | -0.027466 | 0.050354 | 0.032043 | -0.050354 | -0.091553 | 0.12817 | -0.041198 | -122.1954 | 0.1236 | 0.1236 | 0.16479 | -122.2137 | 0.041199 | 0 | -122.2275 | 0.16937 | 0.064087 | 0.064087 | -122.2458 | 0.17395 | 0.15564 | 0.086975 | -122.4106 | 0.14191 | 0.1236 | 0.17395 | -122.3694
3418.8125 | 122.4564 | -0.050354 | 122.2366 | 0.13245 | 0.0457 | 0.059045 | -0.0032213 | 0.031251 | -0.0028178 | 0.032142 | 0.082703 | 0.027265 | 0.036027 | 0.050097 | 0.0042361 | 0.027999 | 0.07782 | 0.073242 | 0.059509 | 0.059509 | 0.045776 | 0.059509 | -0.082397 | 0.13275 | 0.11902 | 0.041199 | 0.009155 | 0.004578 | -0.013733 | -0.073242 | 0.10986 | -0.032043 | -122.1909 | 0.1236 | 0.10986 | 0.14191 | -122.1588 | 0.036621 | -0.022888 | -122.2275 | 0.18311 | 0.091553 | 0.11444 | -122.2321 | 0.09613 | 0.12817 | 0.10986 | -122.319 | 0.059509 | 0.054932 | 0.16937 | -122.3099
3420.5781 | 122.3694 | -0.10529 | 122.287 | -0.18799 | 0.045914 | 0.061609 | 0.0068189 | 0.030824 | -0.008372 | 0.030646 | -0.13092 | 0.027906 | 0.036027 | 0.051165 | -0.0021725 | 0.026504 | 0.07782 | 0.10529 | 0.10529 | 0.073242 | 0.045776 | 0.054932 | -0.09613 | 0.10986 | 0.16022 | 0.027466 | 0.018311 | 0 | -0.018311 | -0.091553 | 0.16022 | 0.009156 | -122.2412 | 0.21057 | 0.17853 | 0.16937 | -122.2092 | 0.086975 | 0.013733 | -122.2687 | 0.21515 | 0.13275 | 0.11902 | -122.287 | 0.15106 | 0.18311 | 0.21057 | -122.3831 | 0.1236 | 0.10529 | 0.2655 | -122.3785
3422.3281 | 122.319 | -0.091553 | 122.2824 | -0.073547 | 0.045914 | 0.060541 | -1.7146e-05 | 0.030824 | 0.00038662 | 0.032783 | -0.085144 | 0.029187 | 0.036668 | 0.050524 | 0.0029543 | 0.023513 | 0.059509 | 0.045776 | 0.004578 | 0.013733 | 0.082397 | 0.032043 | -0.09613 | 0.054932 | 0.054932 | -0.082397 | 0.054932 | 0.036621 | -0.050354 | -0.10071 | 0.1236 | -0.004577 | -122.2 | 0.13733 | 0.10529 | 0.10986 | -122.2229 | 0.041199 | -0.009155 | -122.2275 | 0.14649 | 0.009156 | 0.018311 | -122.2458 | 0.17395 | 0.15106 | 0.096131 | -122.3785 | 0.14649 | 0.12817 | 0.14649 | -122.3831
3424.0938 | 122.3373 | -0.10529 | 122.2595 | -0.19562 | 0.046128 | 0.061609 | 0.0051099 | 0.028901 | -0.006663 | 0.030433 | -0.22247 | 0.028119 | 0.035387 | 0.05266 | -0.0025999 | 0.023727 | 0.041199 | 0.10529 | 0.082397 | 0.050354 | 0.036621 | 0.036621 | -0.11902 | 0.059509 | 0.10986 | -0.013733 | 0.036621 | 0.027466 | -0.050354 | -0.11444 | 0.14191 | -0.013733 | -122.2229 | 0.21057 | 0.15564 | 0.16937 | -122.2183 | 0.054932 | -0.009155 | -122.2229 | 0.16479 | 0.091553 | 0.10071 | -122.2321 | 0.14191 | 0.14649 | 0.18768 | -122.3785 | 0.14191 | 0.13275 | 0.21515 | -122.374
3425.8594 | 122.4426 | -0.059509 | 122.2275 | 0.11719 | 0.045273 | 0.060968 | -0.00044435 | 0.029542 | -0.0030314 | 0.030646 | 0.159 | 0.027478 | 0.03795 | 0.049883 | 0.0031681 | 0.024154 | 0.091553 | 0.10529 | 0.10529 | 0.082397 | 0.036621 | 0.050354 | -0.059509 | 0.13733 | 0.14191 | 0.045776 | -0.009155 | 0.009155 | -0.013733 | -0.073242 | 0.10986 | 0 | -122.1909 | 0.16479 | 0.14191 | 0.14191 | -122.1359 | 0.045776 | -0.013733 | -122.2366 | 0.19684 | 0.10528 | 0.11902 | -122.2183 | 0.09613 | 0.15106 | 0.16479 | -122.287 | 0.050354 | 0.068664 | 0.20142 | -122.3007
3427.625 | 122.3419 | -0.10986 | 122.2824 | -0.19562 | 0.046128 | 0.060327 | 0.0055371 | 0.032533 | -0.004954 | 0.030433 | -0.19958 | 0.028119 | 0.037736 | 0.052019 | -0.0015317 | 0.025436 | 0.068665 | 0.10986 | 0.082397 | 0.064087 | 0.045776 | 0.036621 | -0.10071 | 0.091553 | 0.13733 | -0.004578 | 0.027466 | 0.032043 | -0.032043 | -0.091553 | 0.14648 | 0.009155 | -122.2366 | 0.21973 | 0.17395 | 0.1648 | -122.2137 | 0.07782 | 0.01831 | -122.2549 | 0.20142 | 0.10529 | 0.086975 | -122.2504 | 0.15564 | 0.17853 | 0.19226 | -122.3831 | 0.13733 | 0.14191 | 0.24719 | -122.374
3429.3281 | 122.3602 | -0.073242 | 122.2824 | -0.081177 | 0.048691 | 0.058618 | -0.00023075 | 0.031251 | 0.0027364 | 0.034278 | -0.13855 | 0.027692 | 0.035814 | 0.051378 | 0.0025271 | 0.023513 | 0.059509 | 0.059509 | 0.027466 | 0.045776 | 0.07782 | 0.027466 | -0.11444 | 0.07782 | 0.07782 | -0.059509 | 0.045776 | 0.032043 | -0.036621 | -0.091553 | 0.10071 | -0.041199 | -122.2046 | 0.13275 | 0.11902 | 0.16022 | -122.2229 | 0.036621 | -0.018311 | -122.2366 | 0.15106 | 0.013733 | 0.032044 | -122.2504 | 0.15106 | 0.13275 | 0.10071 | -122.3969 | 0.11902 | 0.10529 | 0.15106 | -122.374
3431.1094 | 122.4609 | -0.068665 | 122.2229 | -0.096436 | 0.045914 | 0.060114 | 0.0053235 | 0.030824 | -0.00944 | 0.031287 | -0.054626 | 0.02406 | 0.038805 | 0.051592 | -0.0025999 | 0.025436 | 0.059509 | 0.1236 | 0.10529 | 0.064087 | 0.059509 | 0.054932 | -0.091553 | 0.15106 | 0.17853 | 0.073242 | 0.022888 | 0.009155 | -0.013733 | -0.064087 | 0.1236 | -0.022888 | -122.1634 | 0.19226 | 0.13275 | 0.15564 | -122.1634 | 0.054932 | 0.004578 | -122.2 | 0.21973 | 0.14191 | 0.13733 | -122.2137 | 0.12817 | 0.12817 | 0.17395 | -122.3145 | 0.091553 | 0.07782 | 0.24719 | -122.287
3432.8125 | 122.3877 | -0.073242 | 122.2778 | -0.18799 | 0.045914 | 0.059473 | 0.0027601 | 0.031037 | 0.00060022 | 0.032355 | -0.19958 | 0.029828 | 0.037523 | 0.053301 | 0.0018863 | 0.023513 | 0.036621 | 0.022888 | -0.009155 | 0.022888 | 0.073242 | 0.009155 | -0.12817 | 0.068665 | 0.073242 | -0.050354 | 0.068665 | 0.032043 | -0.054932 | -0.10986 | 0.082397 | -0.054932 | -122.2046 | 0.09613 | 0.09613 | 0.15106 | -122.2412 | 0.01831 | -0.036621 | -122.2092 | 0.14191 | 0.022888 | 0.059509 | -122.2458 | 0.14648 | 0.10986 | 0.064087 | -122.406 | 0.14191 | 0.10529 | 0.14648 | -122.3877
3434.5781 | 122.3419 | -0.10071 | 122.2641 | 0.033264 | 0.046128 | 0.057764 | 0.0010511 | 0.031465 | 0.0023092 | 0.03321 | 0.036926 | 0.028974 | 0.036455 | 0.053515 | 0.0018863 | 0.024154 | -0.013733 | -0.068665 | -0.054932 | -0.036621 | 0.10071 | 0 | -0.1236 | 0.022888 | -0.009155 | -0.10529 | 0.054932 | 0.045776 | -0.045776 | -0.09613 | 0.10071 | -0.022888 | -122.1634 | 0.032043 | 0.064087 | 0.086975 | -122.2778 | 0.054932 | 0.004578 | -122.2092 | 0.1236 | -0.004578 | -0.009156 | -122.2183 | 0.20142 | 0.086975 | 0.045776 | -122.3877 | 0.15564 | 0.14648 | 0.091553 | -122.3602
3436.3281 | 122.4472 | -0.073242 | 122.2366 | 0.040894 | 0.044205 | 0.06225 | 0.0031873 | 0.031251 | -0.0098672 | 0.030219 | 0.075073 | 0.025983 | 0.034959 | 0.049456 | -0.0019589 | 0.028427 | 0.018311 | 0.064087 | 0.050354 | 0.032043 | 0.054932 | 0.041199 | -0.09613 | 0.07782 | 0.091553 | 0.004578 | 0.032043 | 0.022888 | -0.027466 | -0.082397 | 0.11444 | -0.022888 | -122.1817 | 0.13733 | 0.10529 | 0.12817 | -122.2183 | 0.045776 | -0.009155 | -122.2046 | 0.15106 | 0.07782 | 0.086975 | -122.2137 | 0.12817 | 0.091553 | 0.1236 | -122.3328 | 0.10529 | 0.09613 | 0.16479 | -122.319
3438.0781 | 122.4472 | -0.054932 | 122.2412 | 0.063782 | 0.0457 | 0.060754 | -1.7146e-05 | 0.029328 | -4.058e-05 | 0.032996 | 0.052185 | 0.029187 | 0.036668 | 0.050097 | 0.0031681 | 0.027572 | 0 | -0.018311 | -0.018311 | -0.018311 | 0.091553 | 0.018311 | -0.10986 | 0.064087 | -0.004578 | -0.068665 | 0.059509 | 0.032043 | -0.032043 | -0.09613 | 0.073243 | -0.054931 | -122.1497 | 0.036621 | 0.036621 | 0.091552 | -122.2412 | 0.022889 | -0.041198 | -122.1817 | 0.11902 | -0.013733 | 0.027465 | -122.2092 | 0.14649 | 0.054932 | 0.036621 | -122.3511 | 0.11444 | 0.086975 | 0.050354 | -122.3373
3439.8438 | 122.4152 | -0.064087 | 122.2549 | 0.056152 | 0.044846 | 0.059686 | 0.0057507 | 0.029756 | -0.0081582 | 0.031928 | 0.11322 | 0.028333 | 0.037309 | 0.052447 | -0.0017453 | 0.026077 | 0.036621 | 0.07782 | 0.073242 | 0.032043 | 0.045776 | 0.050354 | -0.086975 | 0.09613 | 0.082397 | 0 | 0.009155 | 0.009155 | -0.018311 | -0.064087 | 0.11444 | -0.022888 | -122.2092 | 0.14191 | 0.09613 | 0.11902 | -122.2183 | 0.045776 | 0 | -122.2458 | 0.16022 | 0.064087 | 0.064087 | -122.2458 | 0.10986 | 0.10071 | 0.13733 | -122.3419 | 0.073242 | 0.073242 | 0.14648 | -122.319
3441.6094 | 122.4564 | -0.041199 | 122.2275 | 0.14008 | 0.044846 | 0.062463 | 0.0012647 | 0.03061 | -0.0028178 | 0.030433 | 0.15137 | 0.025128 | 0.036882 | 0.048174 | 0.0023135 | 0.025863 | 0.10071 | 0.11444 | 0.086975 | 0.059509 | 0.050354 | 0.050354 | -0.09613 | 0.14648 | 0.13733 | 0.032043 | 0.022888 | -0.009155 | 0 | -0.068665 | 0.091553 | -0.054931 | -122.1771 | 0.15564 | 0.10071 | 0.15564 | -122.1268 | 0.041199 | -0.027466 | -122.2046 | 0.18768 | 0.073242 | 0.10071 | -122.2366 | 0.091553 | 0.14191 | 0.12817 | -122.3236 | 0.064087 | 0.032044 | 0.17853 | -122.2961
3443.3594 | 122.4701 | -0.064087 | 122.2458 | 0.16296 | 0.04506 | 0.062891 | -1.7146e-05 | 0.032319 | -0.0030314 | 0.03321 | 0.082703 | 0.02876 | 0.036455 | 0.053728 | 0.0035953 | 0.02565 | 0.068665 | 0.059509 | 0.059509 | 0.045776 | 0.068665 | 0.064087 | -0.10529 | 0.13275 | 0.12817 | 0.018311 | 0.032043 | 0.018311 | 0.004578 | -0.050354 | 0.12817 | -0.041199 | -122.1771 | 0.1236 | 0.10986 | 0.15106 | -122.1771 | 0.068665 | 0.013733 | -122.2137 | 0.19684 | 0.082398 | 0.068665 | -122.2275 | 0.13275 | 0.13275 | 0.1236 | -122.3511 | 0.09613 | 0.082398 | 0.19226 | -122.2961
3445.1094 | 122.4152 | -0.07782 | 122.2412 | 0.094299 | 0.042282 | 0.060327 | 0.0019055 | 0.032319 | -0.0064492 | 0.029365 | 0.11322 | 0.02641 | 0.036668 | 0.049883 | -0.0011045 | 0.027145 | 0.082397 | 0.086975 | 0.07782 | 0.036621 | 0.045776 | 0.045776 | -0.10071 | 0.11902 | 0.091553 | 0.018311 | 0.022888 | 0.022888 | -0.018311 | -0.073242 | 0.1236 | -0.022888 | -122.1954 | 0.16479 | 0.11444 | 0.13733 | -122.1588 | 0.059509 | 0.004578 | -122.2183 | 0.19684 | 0.096131 | 0.091553 | -122.2183 | 0.1236 | 0.16022 | 0.15564 | -122.3419 | 0.10071 | 0.10071 | 0.16937 | -122.3145
3446.8125 | 122.4655 | -0.064087 | 122.2595 | 0.0027468 | 0.044419 | 0.060327 | 0.0021191 | 0.029115 | -0.0073038 | 0.029151 | 0.036926 | 0.026624 | 0.036668 | 0.049669 | -0.0028135 | 0.025009 | 0.013733 | 0.050354 | 0.050354 | 0.041199 | 0.054932 | 0.036621 | -0.10071 | 0.073242 | 0.086975 | 0 | 0.045776 | 0.022888 | -0.022888 | -0.10071 | 0.10071 | -0.036621 | -122.2046 | 0.11444 | 0.10529 | 0.14191 | -122.2458 | 0.041199 | -0.036621 | -122.2137 | 0.13733 | 0.064087 | 0.10071 | -122.2366 | 0.11902 | 0.07782 | 0.11444 | -122.3602 | 0.10986 | 0.086975 | 0.15106 | -122.3602
3448.5625 | 122.4609 | -0.054932 | 122.2366 | -0.0048827 | 0.044846 | 0.061823 | 0.0044691 | 0.028047 | -0.0064492 | 0.02851 | 0.036926 | 0.025769 | 0.036668 | 0.051378 | -0.00089089 | 0.026291 | 0.032043 | 0.036621 | 0.045776 | 0.018311 | 0.059509 | 0.036621 | -0.09613 | 0.10986 | 0.091553 | 0.022888 | 0.018311 | 0.013733 | -0.022888 | -0.082397 | 0.091553 | -0.041198 | -122.1771 | 0.091553 | 0.073243 | 0.11444 | -122.2046 | 0.032044 | -0.027465 | -122.2183 | 0.16479 | 0.07782 | 0.10528 | -122.2229 | 0.11444 | 0.086975 | 0.10071 | -122.3328 | 0.073243 | 0.068665 | 0.14649 | -122.319
3450.3281 | 122.4106 | -0.07782 | 122.2366 | 0.018005 | 0.046128 | 0.061395 | 0.0031873 | 0.030824 | -0.0047404 | 0.030433 | 0.067444 | 0.028333 | 0.037096 | 0.052233 | -0.0015317 | 0.026718 | 0.064087 | 0.064087 | 0.082397 | 0.018311 | 0.041199 | 0.036621 | -0.082397 | 0.11444 | 0.09613 | 0.009155 | 0.009155 | 0.018311 | -0.036621 | -0.09613 | 0.11444 | -0.004577 | -122.1954 | 0.14191 | 0.096131 | 0.10071 | -122.1725 | 0.041199 | -0.01831 | -122.2275 | 0.19226 | 0.086975 | 0.10528 | -122.2183 | 0.11902 | 0.14191 | 0.16022 | -122.319 | 0.086975 | 0.096131 | 0.17395 | -122.3328
3452.0312 | 122.4197 | -0.07782 | 122.2366 | 0.08667 | 0.040573 | 0.060327 | 0.00083745 | 0.030183 | -0.0034586 | 0.029365 | 0.075073 | 0.027478 | 0.035173 | 0.051592 | 0.0016727 | 0.025863 | 0.10071 | 0.09613 | 0.091553 | 0.054932 | 0.054932 | 0.045776 | -0.091553 | 0.12817 | 0.091553 | -0.004578 | 0.022888 | -0.004578 | -0.018311 | -0.073242 | 0.1236 | -0.013733 | -122.1817 | 0.17395 | 0.13275 | 0.14649 | -122.1359 | 0.059509 | 0.004578 | -122.2137 | 0.20599 | 0.073242 | 0.068664 | -122.2412 | 0.13275 | 0.17853 | 0.16937 | -122.3282 | 0.10071 | 0.073242 | 0.16937 | -122.3099
3453.7812 | 122.4655 | -0.054932 | 122.2504 | -0.11932 | 0.045273 | 0.058618 | 0.0046827 | 0.029542 | -0.0058084 | 0.030219 | -0.13092 | 0.026197 | 0.03795 | 0.051165 | -0.0019589 | 0.023941 | 0.1236 | 0.14648 | 0.13275 | 0.073242 | 0.045776 | 0.041199 | -0.082397 | 0.16937 | 0.18768 | 0.064087 | 0.027466 | 0.004578 | -0.018311 | -0.073242 | 0.096131 | -0.027465 | -122.2046 | 0.20142 | 0.12817 | 0.15564 | -122.1268 | 0.036621 | -0.01831 | -122.2229 | 0.22431 | 0.11902 | 0.13733 | -122.2458 | 0.10071 | 0.17853 | 0.18768 | -122.3328 | 0.082398 | 0.05951 | 0.24261 | -122.3236
3455.5469 | 122.4747 | -0.050354 | 122.2092 | -0.027771 | 0.040787 | 0.060327 | -0.00023075 | 0.030824 | -0.0038858 | 0.028937 | -0.031738 | 0.027478 | 0.035173 | 0.051806 | 0.00039091 | 0.025222 | 0.059509 | 0.054932 | 0.054932 | 0.041199 | 0.045776 | 0.041199 | -0.10529 | 0.11902 | 0.11902 | 0.013733 | 0.036621 | 0.013733 | -0.009155 | -0.059509 | 0.091553 | -0.054932 | -122.1634 | 0.10529 | 0.091553 | 0.14649 | -122.1497 | 0.041199 | -0.009155 | -122.1725 | 0.16937 | 0.064087 | 0.073242 | -122.1954 | 0.09613 | 0.10986 | 0.10529 | -122.3145 | 0.086975 | 0.064087 | 0.16937 | -122.2687
3457.3125 | 122.4747 | -0.036621 | 122.2504 | -0.10406 | 0.043778 | 0.059473 | 0.0040417 | 0.028901 | -0.0040994 | 0.027869 | -0.12329 | 0.024915 | 0.035173 | 0.050524 | -0.00024989 | 0.025222 | 0.091553 | 0.10986 | 0.10986 | 0.064087 | 0.064087 | 0.045776 | -0.09613 | 0.17395 | 0.18768 | 0.059509 | 0.022888 | 0.013733 | -0.018311 | -0.068665 | 0.082397 | -0.059509 | -122.1863 | 0.14648 | 0.10071 | 0.16022 | -122.1588 | 0.01831 | -0.032044 | -122.2275 | 0.21057 | 0.09613 | 0.12817 | -122.2366 | 0.10071 | 0.12817 | 0.14648 | -122.3465 | 0.059509 | 0.050354 | 0.2243 | -122.319
3459.0156 | 122.3877 | -0.10071 | 122.2412 | -0.19562 | 0.046768 | 0.060968 | 0.0023329 | 0.030824 | 0.00017302 | 0.030219 | -0.26062 | 0.030683 | 0.037309 | 0.052019 | 0.0027407 | 0.021164 | 0.045776 | 0.009155 | -0.004578 | 0.013733 | 0.082397 | 0.004578 | -0.14648 | 0.07782 | 0.059509 | -0.059509 | 0.054932 | 0.041199 | -0.050354 | -0.10986 | 0.10529 | -0.045776 | -122.1588 | 0.10986 | 0.11444 | 0.16022 | -122.1954 | 0.050354 | -0.009155 | -122.1863 | 0.17853 | 0.041199 | 0.050354 | -122.2 | 0.18311 | 0.14648 | 0.09613 | -122.3877 | 0.15564 | 0.14191 | 0.16022 | -122.3511
3460.7969 | 122.4564 | -0.045776 | 122.2504 | -0.14984 | 0.0457 | 0.059686 | 0.0046827 | 0.029542 | -0.0058084 | 0.031287 | -0.092773 | 0.026197 | 0.036882 | 0.050524 | -0.00089089 | 0.026718 | 0.10071 | 0.16022 | 0.11902 | 0.068665 | 0.050354 | 0.027466 | -0.10529 | 0.17853 | 0.19684 | 0.068665 | 0.018311 | 0.004578 | -0.022888 | -0.041199 | 0.073242 | -0.05951 | -122.2 | 0.20599 | 0.11444 | 0.17395 | -122.1497 | 0.022888 | 0.004577 | -122.2321 | 0.2243 | 0.11444 | 0.10986 | -122.2458 | 0.09613 | 0.14648 | 0.16479 | -122.3557 | 0.064087 | 0.050354 | 0.24261 | -122.2916
3462.5625 | 122.374 | -0.086975 | 122.2549 | 0.08667 | 0.04805 | 0.061609 | 0.00019645 | 0.029969 | 0.0014548 | 0.03321 | 0.036926 | 0.029401 | 0.035814 | 0.049029 | 0.0038089 | 0.025222 | 0.004578 | -0.013733 | -0.036621 | -0.004578 | 0.082397 | 0.022888 | -0.11902 | 0.059509 | -0.004578 | -0.09613 | 0.068665 | 0.050354 | -0.045776 | -0.082397 | 0.10986 | -0.032044 | -122.1725 | 0.073242 | 0.082397 | 0.11444 | -122.2504 | 0.041199 | 0.004578 | -122.1863 | 0.14648 | -0.009155 | -0.013733 | -122.2046 | 0.16937 | 0.091553 | 0.050354 | -122.374 | 0.15564 | 0.13733 | 0.082397 | -122.3373
3464.3125 | 122.3419 | -0.086975 | 122.2778 | 0.033264 | 0.051468 | 0.061823 | 0.0055371 | 0.029969 | 0.0023092 | 0.03321 | 0.014038 | 0.028974 | 0.039232 | 0.05031 | 0.0016727 | 0.025436 | -0.013733 | -0.045776 | -0.036621 | -0.032043 | 0.086975 | 0.032043 | -0.1236 | 0.041199 | 0.004578 | -0.11444 | 0.050354 | 0.050354 | -0.050354 | -0.10529 | 0.11902 | -0.036621 | -122.1909 | 0.041199 | 0.054932 | 0.091553 | -122.2916 | 0.036621 | -0.018311 | -122.2275 | 0.12817 | -0.027466 | -0.009155 | -122.2275 | 0.17395 | 0.073242 | 0.050354 | -122.4014 | 0.13733 | 0.13733 | 0.091553 | -122.3831
3466 | 122.493 | -0.059509 | 122.2321 | -0.050659 | 0.043137 | 0.063532 | 0.0048963 | 0.02826 | -0.0085856 | 0.032142 | -0.031738 | 0.025983 | 0.036668 | 0.051165 | -0.00089089 | 0.026718 | 0.022888 | 0.10986 | 0.086975 | 0.054932 | 0.045776 | 0.032043 | -0.091553 | 0.12817 | 0.14648 | 0.050354 | 0.027466 | 0.004578 | -0.032043 | -0.086975 | 0.091552 | -0.032044 | -122.1863 | 0.16937 | 0.11444 | 0.14649 | -122.2092 | 0.027466 | -0.027466 | -122.2046 | 0.18768 | 0.10986 | 0.13733 | -122.2275 | 0.10528 | 0.082397 | 0.14648 | -122.3236 | 0.086975 | 0.064087 | 0.20599 | -122.319
3467.75 | 122.4106 | -0.064087 | 122.2504 | 0.079041 | 0.043137 | 0.060541 | 0.0014783 | 0.031892 | -0.0053812 | 0.03086 | 0.11322 | 0.025769 | 0.034746 | 0.049029 | 0.0010317 | 0.027359 | 0.064087 | 0.12817 | 0.086975 | 0.036621 | 0.045776 | 0.050354 | -0.07782 | 0.14648 | 0.10529 | 0.018311 | 0.022888 | 0.009155 | -0.018311 | -0.064087 | 0.11444 | -0.013733 | -122.2046 | 0.19226 | 0.10071 | 0.11444 | -122.1863 | 0.045776 | 0 | -122.2275 | 0.21057 | 0.082398 | 0.082398 | -122.2412 | 0.10986 | 0.12817 | 0.15106 | -122.3282 | 0.086975 | 0.073242 | 0.16937 | -122.3145
3469.5156 | 122.3785 | -0.082397 | 122.2366 | -0.18799 | 0.04805 | 0.060968 | 0.0048963 | 0.029328 | -0.00089518 | 0.031928 | -0.20721 | 0.031323 | 0.037523 | 0.051165 | 0.0016727 | 0.023086 | -0.004578 | -0.009155 | -0.013733 | 0.022888 | 0.10071 | -0.004578 | -0.12817 | 0.041199 | 0.059509 | -0.07782 | 0.059509 | 0.041199 | -0.059509 | -0.09613 | 0.077819 | -0.045777 | -122.1359 | 0.073242 | 0.10528 | 0.15106 | -122.2412 | 0.022888 | -0.013733 | -122.1771 | 0.1236 | 0.004577 | 0.01831 | -122.1954 | 0.18311 | 0.077819 | 0.068664 | -122.3648 | 0.14191 | 0.1236 | 0.14191 | -122.3328
3471.2344 | 122.4609 | -0.054932 | 122.2366 | -0.14984 | 0.045487 | 0.063532 | 0.0040417 | 0.03061 | -0.0058084 | 0.028724 | -0.10803 | 0.025769 | 0.036027 | 0.049456 | -0.0023861 | 0.02565 | 0.10071 | 0.15564 | 0.13275 | 0.068665 | 0.041199 | 0.064087 | -0.09613 | 0.15564 | 0.1831 | 0.068665 | 0.013733 | 0.004578 | -0.013733 | -0.054932 | 0.11902 | -0.041198 | -122.1954 | 0.21057 | 0.1236 | 0.16479 | -122.1359 | 0.041199 | 0 | -122.2229 | 0.21057 | 0.1236 | 0.1236 | -122.2321 | 0.096131 | 0.15564 | 0.18768 | -122.3328 | 0.068665 | 0.05951 | 0.23804 | -122.2916
3472.9844 | 122.4426 | -0.073242 | 122.2412 | 0.010376 | 0.043778 | 0.062036 | -1.7146e-05 | 0.029542 | -0.00944 | 0.031501 | 0.036926 | 0.02876 | 0.033891 | 0.049669 | -0.00067729 | 0.026718 | 0.041199 | 0.073242 | 0.054932 | 0.045776 | 0.059509 | 0.050354 | -0.082397 | 0.10986 | 0.10529 | 0.004578 | 0.027466 | 0.013733 | -0.022888 | -0.082397 | 0.1236 | -0.009155 | -122.1817 | 0.14648 | 0.11902 | 0.12817 | -122.2 | 0.050354 | -0.009155 | -122.2137 | 0.18311 | 0.07782 | 0.086975 | -122.2275 | 0.13275 | 0.11444 | 0.12817 | -122.3236 | 0.10071 | 0.086975 | 0.17853 | -122.3236
3474.7344 | 122.4152 | -0.068665 | 122.2549 | 0.033264 | 0.041428 | 0.062036 | 0.00041005 | 0.029969 | -0.003245 | 0.029151 | 0.052185 | 0.026837 | 0.035387 | 0.049242 | 0.00039091 | 0.027145 | 0.041199 | 0.091553 | 0.068665 | 0.022888 | 0.050354 | 0.054932 | -0.086975 | 0.10986 | 0.09613 | 0.004578 | 0.032043 | 0.022888 | -0.018311 | -0.073242 | 0.1236 | -0.01831 | -122.2046 | 0.16022 | 0.091553 | 0.10986 | -122.2137 | 0.050354 | -0.004577 | -122.2229 | 0.17853 | 0.073243 | 0.07782 | -122.2321 | 0.11902 | 0.10986 | 0.13733 | -122.3419 | 0.10071 | 0.091553 | 0.16479 | -122.3282
3476.5 | 122.3602 | -0.10986 | 122.2824 | -0.18036 | 0.04506 | 0.060754 | 0.0055371 | 0.031037 | -0.001536 | 0.031074 | -0.24536 | 0.024488 | 0.03795 | 0.052447 | -0.0011045 | 0.023727 | 0 | 0.018311 | -0.013733 | -0.013733 | 0.091553 | 0.018311 | -0.1236 | 0.027466 | 0.045776 | -0.091553 | 0.073242 | 0.045776 | -0.064087 | -0.10986 | 0.12817 | -0.013733 | -122.1909 | 0.12817 | 0.09613 | 0.10986 | -122.2824 | 0.045776 | 0 | -122.2092 | 0.13733 | 0.01831 | 0.01831 | -122.2366 | 0.20142 | 0.10986 | 0.09613 | -122.406 | 0.18311 | 0.15564 | 0.15564 | -122.3923
3478.2031 | 122.3282 | -0.091553 | 122.2687 | -0.096436 | 0.049332 | 0.060754 | 0.00083745 | 0.030397 | 0.0023092 | 0.033637 | -0.15381 | 0.027692 | 0.034959 | 0.051806 | 0.0040225 | 0.022873 | 0.086975 | 0.073242 | 0.027466 | 0.032043 | 0.07782 | 0.022888 | -0.11444 | 0.086975 | 0.086975 | -0.059509 | 0.059509 | 0.027466 | -0.032043 | -0.082397 | 0.11444 | -0.022888 | -122.1909 | 0.16479 | 0.1236 | 0.14648 | -122.1817 | 0.05951 | 0.009156 | -122.2092 | 0.17853 | 0.032044 | 0.022888 | -122.2412 | 0.16937 | 0.17853 | 0.11902 | -122.3831 | 0.15106 | 0.11902 | 0.17853 | -122.3511
3479.9844 | 122.4106 | -0.086975 | 122.2733 | -0.21088 | 0.047409 | 0.0646 | 0.0019055 | 0.031037 | -0.0055948 | 0.032569 | -0.15381 | 0.025342 | 0.036455 | 0.048174 | -0.0015317 | 0.025222 | 0.064087 | 0.15564 | 0.11902 | 0.068665 | 0.059509 | 0.036621 | -0.10071 | 0.14648 | 0.1831 | 0.054932 | 0.004578 | 0.004578 | -0.022888 | -0.059509 | 0.1236 | -0.013733 | -122.2137 | 0.24261 | 0.15564 | 0.16937 | -122.2092 | 0.064087 | 0.027466 | -122.2687 | 0.23346 | 0.14191 | 0.11444 | -122.2687 | 0.14648 | 0.15106 | 0.20599 | -122.374 | 0.091553 | 0.091553 | 0.27008 | -122.3328
3481.6875 | 122.4335 | -0.068665 | 122.2366 | 0.0027468 | 0.039933 | 0.062677 | -0.00065795 | 0.029542 | -0.004313 | 0.030646 | 0.052185 | 0.027478 | 0.034532 | 0.048174 | 0.0012455 | 0.027359 | 0.022888 | 0.064087 | 0.059509 | 0.018311 | 0.059509 | 0.059509 | -0.086975 | 0.091553 | 0.086975 | 0.013733 | 0.027466 | 0.018311 | -0.018311 | -0.073242 | 0.12817 | -0.01831 | -122.1771 | 0.13275 | 0.086976 | 0.10529 | -122.2137 | 0.050354 | -0.004577 | -122.2092 | 0.16022 | 0.082398 | 0.086975 | -122.2183 | 0.12817 | 0.091553 | 0.12817 | -122.3236 | 0.096131 | 0.086976 | 0.15564 | -122.3099
3483.4375 | 122.319 | -0.09613 | 122.2961 | -0.050659 | 0.047409 | 0.060114 | 0.0019055 | 0.031465 | 0.0029502 | 0.032142 | -0.077515 | 0.030255 | 0.034959 | 0.052019 | 0.0059451 | 0.022873 | 0.032043 | 0.041199 | -0.013733 | 0.013733 | 0.086975 | 0.027466 | -0.13275 | 0.064087 | 0.022888 | -0.086975 | 0.045776 | 0.027466 | -0.054932 | -0.11902 | 0.1236 | -0.036621 | -122.2092 | 0.13733 | 0.10986 | 0.14648 | -122.2641 | 0.041198 | -0.022889 | -122.2504 | 0.16022 | 0.009155 | 0.032044 | -122.2687 | 0.1831 | 0.12817 | 0.082397 | -122.4289 | 0.14191 | 0.1236 | 0.11902 | -122.4152
3485.2031 | 122.4609 | -0.032043 | 122.2321 | 0.12482 | 0.0457 | 0.060114 | 0.0023329 | 0.031892 | -0.00025418 | 0.032355 | 0.082703 | 0.029401 | 0.036027 | 0.051378 | 0.0023135 | 0.024795 | 0.054932 | 0.10529 | 0.073242 | 0.059509 | 0.064087 | 0.050354 | -0.07782 | 0.15106 | 0.13275 | 0.027466 | 0.022888 | 0 | -0.004578 | -0.068665 | 0.082397 | -0.045777 | -122.168 | 0.13733 | 0.091552 | 0.13733 | -122.1771 | 0.027465 | -0.036622 | -122.2092 | 0.18311 | 0.059509 | 0.096131 | -122.2321 | 0.09613 | 0.086975 | 0.10529 | -122.3099 | 0.054931 | 0.032043 | 0.16479 | -122.3007
3486.9688 | 122.3877 | -0.086975 | 122.2504 | -0.13458 | 0.047196 | 0.060754 | 0.0036145 | 0.030397 | -0.00046778 | 0.031501 | -0.13092 | 0.028119 | 0.035387 | 0.05031 | 0.0025271 | 0.026291 | 0.036621 | 0.064087 | 0.027466 | 0.041199 | 0.068665 | 0.009155 | -0.14648 | 0.082397 | 0.073242 | -0.064087 | 0.059509 | 0.032043 | -0.059509 | -0.086975 | 0.09613 | -0.059509 | -122.1817 | 0.15106 | 0.12817 | 0.18768 | -122.2137 | 0.027466 | 0 | -122.1909 | 0.16937 | 0.022888 | 0.022888 | -122.2183 | 0.15564 | 0.1236 | 0.11444 | -122.3969 | 0.14648 | 0.11902 | 0.16022 | -122.3373
3488.6719 | 122.4747 | -0.059509 | 122.2229 | -0.0048827 | 0.042282 | 0.062677 | 0.0044691 | 0.028474 | -0.0098672 | 0.030646 | 0.052185 | 0.024915 | 0.036668 | 0.047961 | -0.0013181 | 0.030349 | -0.009155 | 0.073242 | 0.064087 | 0.032043 | 0.073242 | 0.045776 | -0.10071 | 0.07782 | 0.091553 | 0.013733 | 0.032043 | 0.022888 | -0.022888 | -0.07782 | 0.10528 | -0.041199 | -122.1497 | 0.13275 | 0.091552 | 0.13275 | -122.2321 | 0.036621 | -0.018311 | -122.1909 | 0.13733 | 0.073242 | 0.091553 | -122.2 | 0.13275 | 0.050354 | 0.1236 | -122.3236 | 0.091552 | 0.082397 | 0.15106 | -122.3007
3490.4219 | 122.4976 | -0.045776 | 122.2549 | -0.04303 | 0.044419 | 0.062891 | 0.0055371 | 0.03061 | -0.0081582 | 0.029365 | -0.046997 | 0.028546 | 0.036455 | 0.049242 | -0.0058041 | 0.026718 | 0.036621 | 0.091553 | 0.07782 | 0.059509 | 0.054932 | 0.036621 | -0.091553 | 0.11902 | 0.14648 | 0.073242 | 0.027466 | 0 | -0.018311 | -0.068665 | 0.082397 | -0.045777 | -122.2 | 0.13733 | 0.10528 | 0.15106 | -122.2183 | 0.027465 | -0.022889 | -122.2275 | 0.16479 | 0.11902 | 0.14191 | -122.2549 | 0.10071 | 0.082397 | 0.1236 | -122.3465 | 0.073242 | 0.045776 | 0.19226 | -122.3236
3492.1875 | 122.4106 | -0.064087 | 122.2504 | 0.071411 | 0.044205 | 0.060541 | -0.00087155 | 0.029328 | -0.003245 | 0.030219 | 0.14374 | 0.027051 | 0.036241 | 0.051806 | 0.0012455 | 0.023941 | 0.10529 | 0.1236 | 0.10529 | 0.050354 | 0.036621 | 0.064087 | -0.091553 | 0.13275 | 0.11902 | 0.027466 | 0.013733 | 0.009155 | -0.013733 | -0.064087 | 0.12817 | -0.027466 | -122.2137 | 0.18768 | 0.11444 | 0.14191 | -122.1451 | 0.050354 | 0 | -122.2366 | 0.19684 | 0.091553 | 0.091553 | -122.2412 | 0.10071 | 0.16937 | 0.16937 | -122.3419 | 0.07782 | 0.073242 | 0.18311 | -122.3145
3493.9375 | 122.4472 | -0.064087 | 122.2321 | 0.12482 | 0.044205 | 0.060327 | 0.0023329 | 0.029542 | -0.0019632 | 0.032142 | 0.13611 | 0.026837 | 0.035814 | 0.048815 | 0.0016727 | 0.024154 | 0.10529 | 0.11902 | 0.09613 | 0.068665 | 0.045776 | 0.054932 | -0.09613 | 0.16479 | 0.13733 | 0.036621 | 0.009155 | -0.009155 | -0.004578 | -0.059509 | 0.11902 | -0.032043 | -122.1863 | 0.18311 | 0.13275 | 0.16479 | -122.1268 | 0.059509 | 0.004578 | -122.2229 | 0.22888 | 0.10071 | 0.09613 | -122.2412 | 0.10986 | 0.16937 | 0.16022 | -122.3282 | 0.073242 | 0.054932 | 0.20142 | -122.2916
3495.6875 | 122.4152 | -0.045776 | 122.2458 | 0.12482 | 0.043778 | 0.063745 | 0.0010511 | 0.029756 | -0.004313 | 0.031928 | 0.12848 | 0.025342 | 0.035173 | 0.049883 | 0.0029543 | 0.026077 | 0.09613 | 0.13733 | 0.10529 | 0.068665 | 0.045776 | 0.054932 | -0.07782 | 0.15564 | 0.11902 | 0.045776 | 0.018311 | -0.009155 | -0.004578 | -0.068665 | 0.10071 | -0.032044 | -122.2 | 0.18311 | 0.11444 | 0.14649 | -122.1497 | 0.041198 | -0.022889 | -122.2275 | 0.20142 | 0.091552 | 0.11444 | -122.2549 | 0.091552 | 0.14191 | 0.15106 | -122.3236 | 0.064087 | 0.036621 | 0.16479 | -122.3145
3497.4531 | 122.4609 | -0.050354 | 122.2366 | -0.13458 | 0.042496 | 0.060327 | 0.0055371 | 0.033814 | -0.006663 | 0.030646 | -0.10803 | 0.025983 | 0.034746 | 0.050738 | -0.00024989 | 0.024795 | 0.10986 | 0.15564 | 0.11902 | 0.07782 | 0.064087 | 0.041199 | -0.068665 | 0.16937 | 0.19684 | 0.082397 | 0.018311 | 0.013733 | -0.027466 | -0.059509 | 0.091553 | -0.018311 | -122.1725 | 0.20599 | 0.12817 | 0.14649 | -122.1268 | 0.022888 | -0.009155 | -122.2183 | 0.21973 | 0.13275 | 0.14191 | -122.2229 | 0.11444 | 0.16022 | 0.16937 | -122.3053 | 0.068665 | 0.064087 | 0.24719 | -122.2961
3499.1562 | 122.3969 | -0.091553 | 122.2595 | -0.19562 | 0.046555 | 0.059686 | 0.0012647 | 0.029756 | 0.001882 | 0.031287 | -0.22247 | 0.027478 | 0.037523 | 0.053515 | 0.0016727 | 0.023513 | 0.027466 | 0.009155 | -0.013733 | 0.018311 | 0.082397 | 0.009155 | -0.13275 | 0.068665 | 0.073242 | -0.045776 | 0.059509 | 0.050354 | -0.050354 | -0.10529 | 0.10071 | -0.041198 | -122.1771 | 0.10071 | 0.10986 | 0.15106 | -122.2321 | 0.041199 | -0.013733 | -122.2 | 0.16022 | 0.045777 | 0.05951 | -122.2092 | 0.17395 | 0.11902 | 0.07782 | -122.3923 | 0.15106 | 0.14191 | 0.16479 | -122.3648
3500.9219 | 122.3877 | -0.086975 | 122.2595 | 0.10956 | 0.047409 | 0.063318 | -0.00065795 | 0.030824 | 0.0025228 | 0.032355 | 0.059815 | 0.02641 | 0.036027 | 0.051378 | 0.0046633 | 0.026718 | -0.009155 | -0.022888 | -0.027466 | -0.004578 | 0.082397 | 0.022888 | -0.13733 | 0.054932 | -0.013733 | -0.10071 | 0.050354 | 0.041199 | -0.054932 | -0.10071 | 0.10986 | -0.050354 | -122.1771 | 0.064087 | 0.082397 | 0.13275 | -122.2687 | 0.032043 | -0.013733 | -122.2092 | 0.14191 | -0.013733 | 0 | -122.2183 | 0.16937 | 0.07782 | 0.059509 | -122.3969 | 0.13733 | 0.12817 | 0.073242 | -122.3602
3502.6875 | 122.4701 | -0.050354 | 122.2458 | -0.012512 | 0.042282 | 0.062677 | 0.0029737 | 0.03061 | -0.0087992 | 0.031287 | 0.029297 | 0.025128 | 0.037309 | 0.050951 | -0.0021725 | 0.027145 | 0.027466 | 0.073242 | 0.059509 | 0.045776 | 0.064087 | 0.027466 | -0.10071 | 0.10071 | 0.10071 | 0.032043 | 0.013733 | 0.018311 | -0.004578 | -0.082397 | 0.07782 | -0.050354 | -122.1817 | 0.1236 | 0.09613 | 0.14648 | -122.2183 | 0.045776 | -0.032043 | -122.2321 | 0.15106 | 0.082397 | 0.11444 | -122.2275 | 0.11444 | 0.07782 | 0.10986 | -122.3465 | 0.064087 | 0.068665 | 0.15106 | -122.3282
3504.3906 | 122.3328 | -0.086975 | 122.2733 | -0.081177 | 0.048477 | 0.0599 | 0.0051099 | 0.031037 | 0.00060022 | 0.03086 | -0.13855 | 0.029828 | 0.038377 | 0.052233 | 0.0029543 | 0.023513 | 0.091553 | 0.054932 | 0.032043 | 0.032043 | 0.07782 | 0.032043 | -0.1236 | 0.10071 | 0.064087 | -0.059509 | 0.041199 | 0.041199 | -0.027466 | -0.091553 | 0.11902 | -0.036621 | -122.1954 | 0.14191 | 0.11902 | 0.15564 | -122.1817 | 0.059509 | -0.004578 | -122.2321 | 0.18768 | 0.027466 | 0.032044 | -122.2321 | 0.16479 | 0.17853 | 0.11902 | -122.3969 | 0.12817 | 0.12817 | 0.15106 | -122.3648
3506.1406 | 122.3602 | -0.09613 | 122.2961 | -0.20325 | 0.047623 | 0.0599 | 0.0027601 | 0.032319 | -0.0062356 | 0.031501 | -0.12329 | 0.029187 | 0.037096 | 0.049883 | -0.00067729 | 0.026931 | 0.082397 | 0.13275 | 0.11902 | 0.07782 | 0.041199 | 0.045776 | -0.10529 | 0.10986 | 0.17853 | 0.032043 | 0.027466 | 0.018311 | -0.013733 | -0.073242 | 0.14191 | -0.009156 | -122.2549 | 0.22888 | 0.17395 | 0.18311 | -122.2137 | 0.082397 | 0.022888 | -122.2687 | 0.20599 | 0.12817 | 0.10529 | -122.2778 | 0.13733 | 0.17853 | 0.21515 | -122.4014 | 0.1236 | 0.11444 | 0.27466 | -122.3694
3507.9062 | 122.374 | -0.07782 | 122.2687 | -0.12695 | 0.046341 | 0.058832 | 0.0031873 | 0.031892 | 0.00038662 | 0.032569 | -0.15381 | 0.029187 | 0.037096 | 0.052874 | 0.00060451 | 0.022873 | 0.068665 | 0.022888 | 0.018311 | 0.013733 | 0.091553 | 0.013733 | -0.13275 | 0.082397 | 0.10529 | -0.045776 | 0.045776 | 0.032043 | -0.041199 | -0.086975 | 0.091553 | -0.054931 | -122.1771 | 0.10071 | 0.091553 | 0.14648 | -122.2 | 0.036621 | -0.009155 | -122.2229 | 0.16022 | 0.032044 | 0.041199 | -122.2366 | 0.16937 | 0.14649 | 0.096131 | -122.4014 | 0.1236 | 0.10986 | 0.18311 | -122.3557
3509.6562 | 122.4518 | -0.073242 | 122.2504 | -0.14984 | 0.043778 | 0.062036 | 0.0066053 | 0.028901 | -0.0085856 | 0.03086 | -0.13855 | 0.024701 | 0.038377 | 0.048601 | -3.629e-05 | 0.026077 | 0.09613 | 0.14648 | 0.11444 | 0.07782 | 0.050354 | 0.054932 | -0.10529 | 0.14648 | 0.20142 | 0.059509 | 0.009155 | 0.013733 | -0.018311 | -0.068665 | 0.12817 | -0.032044 | -122.2 | 0.21973 | 0.15106 | 0.18311 | -122.1542 | 0.054931 | 0.004577 | -122.2412 | 0.21973 | 0.13275 | 0.12817 | -122.2366 | 0.1236 | 0.16937 | 0.18768 | -122.3557 | 0.082397 | 0.086975 | 0.27466 | -122.319
3511.3438 | 122.4564 | -0.041199 | 122.2458 | 0.071411 | 0.047623 | 0.060968 | -1.7146e-05 | 0.031678 | 0.0010276 | 0.030006 | 0.075073 | 0.029828 | 0.036668 | 0.049883 | 0.0027407 | 0.023513 | 0.018311 | -0.009155 | -0.022888 | 0.004578 | 0.10071 | 0.013733 | -0.12817 | 0.073242 | 0.013733 | -0.050354 | 0.036621 | 0.032043 | -0.054932 | -0.091553 | 0.054932 | -0.086975 | -122.1451 | 0.032044 | 0.045777 | 0.13275 | -122.2275 | -0.013733 | -0.050354 | -122.2092 | 0.11444 | -0.009155 | 0.041199 | -122.2137 | 0.14191 | 0.05951 | 0.018311 | -122.374 | 0.07782 | 0.073242 | 0.054932 | -122.3373
3513.1094 | 122.3648 | -0.091553 | 122.2733 | -0.10406 | 0.049118 | 0.060327 | 0.0046827 | 0.032319 | 0.0014548 | 0.032569 | -0.13092 | 0.029401 | 0.037736 | 0.050951 | 0.0031681 | 0.025222 | 0.059509 | 0.059509 | 0.013733 | 0.032043 | 0.082397 | 0.032043 | -0.11902 | 0.091553 | 0.10071 | -0.045776 | 0.036621 | 0.036621 | -0.018311 | -0.09613 | 0.1236 | -0.027466 | -122.1909 | 0.15106 | 0.1236 | 0.15106 | -122.2137 | 0.073242 | -0.004577 | -122.2366 | 0.18311 | 0.045777 | 0.050354 | -122.2366 | 0.17395 | 0.15106 | 0.10529 | -122.3923 | 0.12817 | 0.12817 | 0.19226 | -122.3694
3514.8125 | 122.3831 | -0.10071 | 122.2778 | -0.23376 | 0.049973 | 0.062463 | 0.0055371 | 0.033601 | -0.0055948 | 0.030646 | -0.2301 | 0.027692 | 0.037523 | 0.051378 | -0.00046349 | 0.025222 | -0.050354 | -0.004578 | -0.013733 | -0.013733 | 0.091553 | 0.009155 | -0.14191 | 0.013733 | 0.045776 | -0.07782 | 0.059509 | 0.050354 | -0.054932 | -0.10529 | 0.10986 | -0.041199 | -122.1863 | 0.09613 | 0.086975 | 0.12817 | -122.3282 | 0.045776 | -0.004578 | -122.2183 | 0.11444 | 0.022888 | 0.027466 | -122.2275 | 0.19226 | 0.050354 | 0.086975 | -122.4197 | 0.16022 | 0.15106 | 0.14648 | -122.3831
3516.5781 | 122.4106 | -0.073242 | 122.2321 | 0.08667 | 0.044632 | 0.059045 | 0.0025465 | 0.032746 | -0.006022 | 0.030219 | 0.17426 | 0.023847 | 0.038377 | 0.049029 | -0.0021725 | 0.026718 | 0.059509 | 0.1236 | 0.10986 | 0.054932 | 0.041199 | 0.059509 | -0.068665 | 0.14648 | 0.1236 | 0.027466 | 0.027466 | 0.009155 | -0.032043 | -0.050354 | 0.13275 | 0.004577 | -122.1909 | 0.19684 | 0.12817 | 0.1236 | -122.1725 | 0.041199 | 0.022888 | -122.2046 | 0.21973 | 0.10071 | 0.07782 | -122.2229 | 0.11444 | 0.13275 | 0.18311 | -122.3007 | 0.10071 | 0.082397 | 0.19684 | -122.2824
3518.3438 | 122.4884 | -0.064087 | 122.2366 | -0.073547 | 0.045273 | 0.060327 | 0.0063917 | 0.030397 | -0.0092264 | 0.03086 | -0.062256 | 0.025983 | 0.037523 | 0.050524 | -0.0049497 | 0.027145 | 0.045776 | 0.10529 | 0.10071 | 0.041199 | 0.059509 | 0.032043 | -0.086975 | 0.14191 | 0.16937 | 0.068665 | 0.032043 | 0.013733 | 0 | -0.082397 | 0.09613 | -0.022888 | -122.1771 | 0.16937 | 0.10529 | 0.12817 | -122.1909 | 0.064087 | -0.01831 | -122.2046 | 0.20599 | 0.13275 | 0.15106 | -122.2229 | 0.1236 | 0.10986 | 0.1648 | -122.3236 | 0.09613 | 0.07782 | 0.23346 | -122.319
3520.0625 | 122.3877 | -0.082397 | 122.2778 | -0.22614 | 0.045273 | 0.061395 | 0.0038281 | 0.03061 | -0.004954 | 0.029578 | -0.13855 | 0.028333 | 0.036455 | 0.050524 | -0.00046349 | 0.023941 | 0.086975 | 0.12817 | 0.10529 | 0.07782 | 0.068665 | 0.041199 | -0.073242 | 0.14191 | 0.1831 | 0.045776 | 0 | 0.013733 | -0.004578 | -0.073242 | 0.1236 | 0.009155 | -122.2092 | 0.21057 | 0.16022 | 0.15106 | -122.1909 | 0.077819 | 0.009155 | -122.2778 | 0.2243 | 0.12817 | 0.11902 | -122.2641 | 0.15106 | 0.16937 | 0.18768 | -122.3511 | 0.082397 | 0.09613 | 0.2655 | -122.3511
3521.8438 | 122.4609 | -0.050354 | 122.2366 | 0.094299 | 0.046341 | 0.059686 | 0.0016919 | 0.031465 | 0.00038662 | 0.031287 | 0.10559 | 0.030255 | 0.0356 | 0.05266 | 0.0025271 | 0.024154 | 0.027466 | 0 | -0.022888 | -0.013733 | 0.10071 | 0.013733 | -0.11902 | 0.082397 | 0.027466 | -0.054932 | 0.050354 | 0.013733 | -0.032043 | -0.07782 | 0.064087 | -0.068665 | -122.1359 | 0.050354 | 0.036621 | 0.10529 | -122.2092 | 0.018311 | -0.027466 | -122.1863 | 0.13275 | -0.004578 | 0.022888 | -122.2229 | 0.15106 | 0.07782 | 0.027466 | -122.3557 | 0.10071 | 0.064087 | 0.07782 | -122.3145
3523.6094 | 122.438 | -0.050354 | 122.2412 | 0.14008 | 0.046128 | 0.059473 | -0.00065795 | 0.031251 | -0.0062356 | 0.031714 | 0.14374 | 0.02641 | 0.036241 | 0.049029 | 0.0018863 | 0.023513 | 0.086975 | 0.10986 | 0.11902 | 0.059509 | 0.050354 | 0.054932 | -0.064087 | 0.14191 | 0.13733 | 0.045776 | 0.013733 | 0 | -0.013733 | -0.07782 | 0.10529 | -0.013733 | -122.1909 | 0.16022 | 0.10986 | 0.1236 | -122.1542 | 0.036621 | -0.027466 | -122.2275 | 0.19226 | 0.09613 | 0.1236 | -122.2412 | 0.10071 | 0.13733 | 0.16937 | -122.3053 | 0.064087 | 0.050354 | 0.18768 | -122.319
3525.375 | 122.3328 | -0.10071 | 122.2778 | 0.0027468 | 0.046982 | 0.057977 | 0.0010511 | 0.033387 | 0.0020956 | 0.031501 | -0.0088499 | 0.030896 | 0.03795 | 0.053087 | 0.0038089 | 0.023727 | 0.018311 | -0.013733 | -0.027466 | 0.004578 | 0.09613 | 0.032043 | -0.13275 | 0.013733 | 0.009155 | -0.11444 | 0.064087 | 0.036621 | -0.050354 | -0.10529 | 0.13275 | -0.032043 | -122.1817 | 0.086975 | 0.10529 | 0.13733 | -122.2595 | 0.050354 | -0.004578 | -122.2137 | 0.11444 | -0.013733 | -0.009155 | -122.2412 | 0.19684 | 0.11902 | 0.073242 | -122.4106 | 0.1648 | 0.13733 | 0.10986 | -122.3831
3527.0938 | 122.525 | -0.054932 | 122.2549 | -0.0048827 | 0.042496 | 0.06225 | 0.0034009 | 0.029969 | -0.011576 | 0.030646 | 0.059815 | 0.027692 | 0.037523 | 0.048815 | -0.0015317 | 0.024795 | 0.013733 | 0.045776 | 0.064087 | 0.022888 | 0.054932 | 0.041199 | -0.09613 | 0.082397 | 0.10071 | 0.013733 | 0.041199 | 0.027466 | -0.036621 | -0.073242 | 0.096131 | -0.041198 | -122.2 | 0.10071 | 0.07782 | 0.11902 | -122.2412 | 0.018311 | -0.01831 | -122.2137 | 0.13733 | 0.068665 | 0.086975 | -122.2275 | 0.10986 | 0.068665 | 0.11902 | -122.3511 | 0.096131 | 0.082398 | 0.15564 | -122.3282
3528.8594 | 122.4472 | -0.050354 | 122.2183 | 0.079041 | 0.046555 | 0.056482 | 0.0023329 | 0.029756 | -0.0036722 | 0.030219 | 0.13611 | 0.027692 | 0.035814 | 0.049669 | 0.0035953 | 0.02565 | 0.10071 | 0.11444 | 0.09613 | 0.086975 | 0.032043 | 0.041199 | -0.091553 | 0.15106 | 0.13275 | 0.027466 | 0.013733 | 0.009155 | -0.004578 | -0.054932 | 0.091553 | -0.041199 | -122.1863 | 0.16479 | 0.13733 | 0.17853 | -122.1176 | 0.045776 | -0.004578 | -122.2046 | 0.20142 | 0.07782 | 0.082398 | -122.2092 | 0.082397 | 0.15106 | 0.14648 | -122.3099 | 0.064087 | 0.059509 | 0.18311 | -122.2733
3530.625 | 122.4701 | -0.036621 | 122.2366 | -0.0048827 | 0.041214 | 0.062677 | 0.0034009 | 0.03061 | -0.006663 | 0.030433 | 0.036926 | 0.02641 | 0.033891 | 0.050097 | -0.00089089 | 0.026504 | 0.013733 | 0.054932 | 0.064087 | 0.041199 | 0.059509 | 0.054932 | -0.082397 | 0.09613 | 0.09613 | 0.009155 | 0.045776 | 0.018311 | -0.027466 | -0.086975 | 0.091553 | -0.045776 | -122.1771 | 0.091553 | 0.07782 | 0.1236 | -122.2229 | 0.009155 | -0.050354 | -122.1909 | 0.13275 | 0.045776 | 0.09613 | -122.2183 | 0.09613 | 0.050354 | 0.10071 | -122.319 | 0.082397 | 0.054932 | 0.13275 | -122.3236
3532.3281 | 122.3465 | -0.10529 | 122.2687 | -0.50079 | 0.045487 | 0.061823 | 0.0076733 | 0.030824 | -0.0023904 | 0.031074 | -0.23773 | 0.029828 | 0.038591 | 0.049883 | -0.0013181 | 0.025863 | 0.004578 | -0.004578 | -0.004578 | -0.022888 | 0.082397 | -0.004578 | -0.12817 | 0.027466 | 0.041199 | -0.07782 | 0.073242 | 0.068665 | -0.059509 | -0.10071 | 0.10071 | -0.022888 | -122.1863 | 0.10071 | 0.082398 | 0.10529 | -122.2641 | 0.045777 | 0.004578 | -122.1954 | 0.13275 | 0.027466 | 0.022888 | -122.2 | 0.18768 | 0.10986 | 0.10071 | -122.3969 | 0.17853 | 0.17395 | 0.14649 | -122.3694
3534.1406 | 122.4655 | -0.068665 | 122.2549 | -0.0048827 | 0.043778 | 0.064172 | 0.0021191 | 0.031892 | -0.0062356 | 0.030006 | 0.036926 | 0.025128 | 0.032823 | 0.048601 | 0.00017731 | 0.02565 | 0.036621 | 0.054932 | 0.050354 | 0.013733 | 0.059509 | 0.032043 | -0.086975 | 0.082397 | 0.07782 | 0.013733 | 0.018311 | 0.022888 | -0.022888 | -0.064087 | 0.10071 | -0.01831 | -122.1954 | 0.1236 | 0.082398 | 0.10071 | -122.2183 | 0.045777 | 0.004578 | -122.2366 | 0.15106 | 0.082398 | 0.07782 | -122.2321 | 0.12817 | 0.10529 | 0.11902 | -122.3419 | 0.086976 | 0.091553 | 0.14649 | -122.319
3535.8438 | 122.3373 | -0.09613 | 122.2549 | -0.096436 | 0.048477 | 0.062463 | 0.0036145 | 0.031251 | 0.00060022 | 0.03321 | -0.15381 | 0.029187 | 0.037523 | 0.05266 | 0.0035953 | 0.024154 | 0.10071 | 0.050354 | 0.032043 | 0.018311 | 0.073242 | 0.022888 | -0.11902 | 0.09613 | 0.086975 | -0.059509 | 0.059509 | 0.050354 | -0.050354 | -0.086975 | 0.11902 | -0.022889 | -122.1817 | 0.14648 | 0.11444 | 0.13733 | -122.1542 | 0.045776 | 0.009155 | -122.1954 | 0.19226 | 0.036621 | 0.027466 | -122.2046 | 0.16937 | 0.19684 | 0.12817 | -122.374 | 0.15564 | 0.14648 | 0.1831 | -122.3419
3537.5781 | 122.4335 | -0.064087 | 122.2275 | 0.018005 | 0.044419 | 0.060754 | 0.0072461 | 0.029756 | -0.0073038 | 0.029578 | 0.059815 | 0.024915 | 0.037736 | 0.051378 | -0.0025999 | 0.027359 | 0.022888 | 0.073242 | 0.059509 | 0.009155 | 0.064087 | 0.064087 | -0.10986 | 0.086975 | 0.09613 | 0.009155 | 0.041199 | 0.009155 | -0.009155 | -0.068665 | 0.12817 | -0.045776 | -122.1634 | 0.13733 | 0.073242 | 0.11902 | -122.2046 | 0.054932 | -0.004578 | -122.1863 | 0.15106 | 0.073242 | 0.07782 | -122.2183 | 0.12817 | 0.086975 | 0.1236 | -122.3373 | 0.10529 | 0.073242 | 0.16022 | -122.2961
3539.3594 | 122.4747 | -0.041199 | 122.2549 | 0.14008 | 0.046128 | 0.060968 | 0.00041005 | 0.031465 | -0.0013224 | 0.032355 | 0.13611 | 0.028546 | 0.035173 | 0.048815 | 0.0027407 | 0.025222 | 0.027466 | 0.027466 | 0.018311 | 0.004578 | 0.064087 | 0.032043 | -0.10529 | 0.11902 | 0.091553 | -0.013733 | 0.013733 | -0.009155 | -0.013733 | -0.059509 | 0.073242 | -0.064087 | -122.1909 | 0.068665 | 0.045777 | 0.10986 | -122.2275 | 0.027466 | -0.01831 | -122.2412 | 0.16022 | 0.027466 | 0.045776 | -122.2641 | 0.10529 | 0.068665 | 0.05951 | -122.3602 | 0.054932 | 0.032044 | 0.13275 | -122.3145
3541.0781 | 122.3511 | -0.11444 | 122.2641 | 0.0027468 | 0.048691 | 0.059473 | -0.00087155 | 0.029115 | 0.003591 | 0.031928 | -0.024109 | 0.028974 | 0.036027 | 0.050738 | 0.0040225 | 0.024582 | -0.004578 | 0.013733 | -0.018311 | 0 | 0.086975 | 0.013733 | -0.13733 | 0.041199 | 0.022888 | -0.11444 | 0.022888 | 0.036621 | -0.036621 | -0.10529 | 0.12817 | -0.022888 | -122.1771 | 0.12817 | 0.11444 | 0.13733 | -122.2687 | 0.07782 | 0.009155 | -122.2412 | 0.15564 | 0 | -0.009155 | -122.2275 | 0.20142 | 0.10986 | 0.09613 | -122.4014 | 0.13733 | 0.15106 | 0.13733 | -122.3694
3542.8594 | 122.3969 | -0.064087 | 122.2229 | 0.11719 | 0.046555 | 0.060754 | 0.00041005 | 0.03061 | 0.00081382 | 0.033637 | 0.082703 | 0.029401 | 0.036455 | 0.05031 | 0.0020999 | 0.026077 | -0.027466 | -0.009155 | -0.036621 | -0.022888 | 0.09613 | 0.022888 | -0.1236 | 0.041199 | 0 | -0.091553 | 0.059509 | 0.041199 | -0.054932 | -0.10529 | 0.086975 | -0.059509 | -122.1268 | 0.054932 | 0.041199 | 0.10071 | -122.2504 | 0.009155 | -0.041199 | -122.1634 | 0.10529 | -0.027466 | 0.013733 | -122.1817 | 0.16022 | 0.036621 | 0.027466 | -122.3465 | 0.1236 | 0.10529 | 0.064087 | -122.3282
3544.6406 | 122.4838 | -0.064087 | 122.2458 | -0.0354 | 0.044846 | 0.061182 | 0.0027601 | 0.02826 | -0.010081 | 0.031074 | -0.0088499 | 0.026197 | 0.034959 | 0.049029 | -0.0032407 | 0.029495 | 0.009155 | 0.068665 | 0.064087 | 0.050354 | 0.059509 | 0.050354 | -0.086975 | 0.11444 | 0.14648 | 0.045776 | 0.022888 | 0.013733 | -0.022888 | -0.068665 | 0.11444 | -0.022888 | -122.1863 | 0.13275 | 0.11444 | 0.13733 | -122.2366 | 0.041199 | -0.004578 | -122.2229 | 0.17853 | 0.10986 | 0.11444 | -122.2321 | 0.1236 | 0.073242 | 0.12817 | -122.3328 | 0.086975 | 0.07782 | 0.21057 | -122.3145
3546.3281 | 122.493 | -0.054932 | 122.2366 | -0.027771 | 0.044846 | 0.060968 | 0.0051099 | 0.028901 | -0.0073038 | 0.030006 | 0.0064086 | 0.027051 | 0.036027 | 0.049456 | -0.0034543 | 0.028427 | 0.027466 | 0.059509 | 0.068665 | 0.041199 | 0.050354 | 0.050354 | -0.09613 | 0.11902 | 0.11902 | 0.032043 | 0.032043 | 0.004578 | -0.009155 | -0.073242 | 0.10529 | -0.041198 | -122.1863 | 0.11444 | 0.096131 | 0.13733 | -122.2092 | 0.045777 | -0.01831 | -122.2046 | 0.17395 | 0.086975 | 0.10529 | -122.2321 | 0.10529 | 0.082398 | 0.1236 | -122.3328 | 0.086975 | 0.05951 | 0.17395 | -122.3099
3548.0938 | 122.3373 | -0.091553 | 122.2824 | -0.22614 | 0.047837 | 0.060754 | 0.0046827 | 0.031892 | -0.0038858 | 0.030006 | -0.19958 | 0.02876 | 0.034318 | 0.051378 | -3.629e-05 | 0.025222 | 0.032043 | 0.004578 | 0 | -0.009155 | 0.086975 | 0.027466 | -0.11902 | 0.050354 | 0.050354 | -0.064087 | 0.068665 | 0.064087 | -0.054932 | -0.11902 | 0.11902 | -0.027466 | -122.1954 | 0.096131 | 0.082398 | 0.10986 | -122.2504 | 0.036621 | -0.027466 | -122.2137 | 0.14191 | 0.027466 | 0.054932 | -122.2183 | 0.17853 | 0.1236 | 0.091553 | -122.4014 | 0.16022 | 0.15564 | 0.14191 | -122.4014
3549.8438 | 122.3923 | -0.11444 | 122.2824 | -0.22614 | 0.047409 | 0.06225 | 0.0048963 | 0.033387 | -0.0019632 | 0.030646 | -0.2301 | 0.031323 | 0.037523 | 0.050524 | -0.00089089 | 0.022659 | -0.004578 | -0.013733 | -0.045776 | 0.004578 | 0.09613 | 0.013733 | -0.12817 | 0.018311 | 0.027466 | -0.086975 | 0.073242 | 0.059509 | -0.068665 | -0.10529 | 0.12817 | -0.013733 | -122.1863 | 0.10071 | 0.11902 | 0.13275 | -122.287 | 0.045776 | 0.009155 | -122.2092 | 0.13275 | 0.027466 | 0.018311 | -122.2229 | 0.21057 | 0.10986 | 0.068665 | -122.4106 | 0.18768 | 0.17395 | 0.14191 | -122.3877
3551.5938 | 122.3648 | -0.10986 | 122.2641 | -0.23376 | 0.046982 | 0.061395 | 0.0048963 | 0.031678 | -0.0040994 | 0.031501 | -0.19196 | 0.025983 | 0.03795 | 0.050524 | -0.0011045 | 0.024582 | 0.013733 | 0.022888 | -0.004578 | -0.009155 | 0.091553 | 0.004578 | -0.13275 | 0.032043 | 0.045776 | -0.068665 | 0.059509 | 0.054932 | -0.050354 | -0.11902 | 0.11444 | -0.022888 | -122.1725 | 0.13275 | 0.10071 | 0.1236 | -122.2504 | 0.059509 | -0.009156 | -122.2046 | 0.14191 | 0.041198 | 0.050354 | -122.2092 | 0.20142 | 0.1236 | 0.10529 | -122.3969 | 0.16937 | 0.16479 | 0.15564 | -122.3831
3553.2812 | 122.4701 | -0.050354 | 122.2458 | 0.13245 | 0.046341 | 0.058832 | -1.7146e-05 | 0.031037 | -0.001536 | 0.030433 | 0.11322 | 0.029828 | 0.034532 | 0.05031 | 0.0042361 | 0.02565 | 0.032043 | 0.036621 | 0.022888 | 0.022888 | 0.091553 | 0.041199 | -0.086975 | 0.12817 | 0.09613 | 0.004578 | 0.022888 | 0.013733 | 0.004578 | -0.064087 | 0.091553 | -0.036621 | -122.1542 | 0.086975 | 0.073242 | 0.10986 | -122.2137 | 0.054932 | -0.013733 | -122.2229 | 0.17853 | 0.054932 | 0.068665 | -122.2321 | 0.14191 | 0.082397 | 0.073242 | -122.3328 | 0.073242 | 0.064087 | 0.14648 | -122.3099
3555.0469 | 122.4335 | -0.059509 | 122.2412 | 0.08667 | 0.044419 | 0.063745 | 0.0016919 | 0.029969 | -0.0051676 | 0.032355 | 0.159 | 0.025556 | 0.03795 | 0.048815 | 0.0018863 | 0.028213 | 0.07782 | 0.10986 | 0.09613 | 0.054932 | 0.054932 | 0.041199 | -0.086975 | 0.15106 | 0.1236 | 0.032043 | 0.041199 | -0.018311 | -0.032043 | -0.07782 | 0.10071 | -0.027466 | -122.1863 | 0.16937 | 0.11444 | 0.14191 | -122.1634 | 0.027466 | -0.018311 | -122.2 | 0.21057 | 0.091552 | 0.10986 | -122.2595 | 0.11444 | 0.13733 | 0.15564 | -122.3282 | 0.10071 | 0.041198 | 0.1831 | -122.319
3556.75 | 122.3923 | -0.09613 | 122.2504 | -0.14221 | 0.047837 | 0.059045 | 0.0040417 | 0.031037 | 0.0010276 | 0.03086 | -0.19958 | 0.028333 | 0.035814 | 0.052874 | 0.00060451 | 0.023727 | 0.050354 | 0.022888 | 0.018311 | 0.018311 | 0.068665 | 0.013733 | -0.13275 | 0.068665 | 0.059509 | -0.054932 | 0.036621 | 0.041199 | -0.032043 | -0.10071 | 0.10986 | -0.036621 | -122.1817 | 0.11902 | 0.11444 | 0.15106 | -122.2 | 0.064087 | -0.004578 | -122.2137 | 0.16479 | 0.041198 | 0.045776 | -122.2092 | 0.16479 | 0.14648 | 0.11444 | -122.3831 | 0.13275 | 0.13733 | 0.15564 | -122.3511
3558.5156 | 122.4701 | -0.050354 | 122.2321 | 0.13245 | 0.046128 | 0.060327 | 0.00062385 | 0.032105 | -0.002604 | 0.031928 | 0.12848 | 0.029401 | 0.035814 | 0.052874 | 0.0042361 | 0.02565 | 0.036621 | 0.036621 | 0.013733 | 0 | 0.086975 | 0.036621 | -0.10529 | 0.10986 | 0.082397 | -0.009155 | 0.018311 | 0.018311 | -0.013733 | -0.07782 | 0.086975 | -0.054932 | -122.1451 | 0.086975 | 0.050354 | 0.10529 | -122.1954 | 0.036621 | -0.027466 | -122.2137 | 0.16022 | 0.041199 | 0.068665 | -122.2137 | 0.13733 | 0.086975 | 0.064087 | -122.3373 | 0.068665 | 0.068665 | 0.13275 | -122.3099
3560.2656 | 122.4289 | -0.07782 | 122.2321 | 0.10956 | 0.046768 | 0.061823 | -1.7146e-05 | 0.029542 | -0.0017496 | 0.031928 | 0.052185 | 0.029401 | 0.036882 | 0.051806 | 0.0012455 | 0.026931 | -0.027466 | -0.004578 | -0.041199 | -0.009155 | 0.09613 | 0.009155 | -0.10986 | 0.054932 | 0.004578 | -0.082397 | 0.064087 | 0.032043 | -0.045776 | -0.09613 | 0.086975 | -0.032043 | -122.1359 | 0.073242 | 0.068665 | 0.10071 | -122.2595 | 0.032044 | -0.01831 | -122.168 | 0.13275 | -0.004577 | 0.013733 | -122.2 | 0.17395 | 0.050354 | 0.036621 | -122.3419 | 0.14191 | 0.10986 | 0.082398 | -122.3282
3562.0156 | 122.4152 | -0.07782 | 122.2412 | 0.094299 | 0.040573 | 0.060541 | 0.0034009 | 0.028688 | -0.006022 | 0.031714 | 0.13611 | 0.025769 | 0.036882 | 0.050951 | -3.629e-05 | 0.026291 | 0.07782 | 0.11902 | 0.10529 | 0.054932 | 0.054932 | 0.041199 | -0.07782 | 0.12817 | 0.1236 | 0.032043 | 0.022888 | 0.018311 | -0.004578 | -0.068665 | 0.11902 | 0 | -122.1863 | 0.19684 | 0.13275 | 0.13275 | -122.1634 | 0.073242 | 0.009155 | -122.2183 | 0.20599 | 0.10986 | 0.10071 | -122.2229 | 0.13275 | 0.15564 | 0.18311 | -122.319 | 0.10071 | 0.096131 | 0.20142 | -122.3099
3563.7812 | 122.3373 | -0.11902 | 122.2778 | -0.22614 | 0.04506 | 0.062677 | 0.0063917 | 0.028474 | -0.0038858 | 0.031714 | -0.15381 | 0.025983 | 0.038591 | 0.053515 | -0.00089089 | 0.023086 | 0.018311 | 0.032043 | 0.009155 | 0.009155 | 0.064087 | 0.036621 | -0.11902 | 0.022888 | 0.045776 | -0.059509 | 0.07782 | 0.041199 | -0.059509 | -0.10529 | 0.15564 | 0 | -122.2137 | 0.15106 | 0.12817 | 0.12817 | -122.2595 | 0.05951 | 0.013733 | -122.2 | 0.14191 | 0.05951 | 0.045777 | -122.2366 | 0.18311 | 0.13733 | 0.12817 | -122.3969 | 0.19684 | 0.16022 | 0.16479 | -122.3831
3565.4844 | 122.3877 | -0.086975 | 122.2549 | -0.1651 | 0.0457 | 0.060968 | -0.00065795 | 0.029328 | -0.0011088 | 0.032142 | -0.2301 | 0.029401 | 0.036668 | 0.051165 | 0.0025271 | 0.025222 | 0.009155 | 0 | -0.022888 | 0.013733 | 0.086975 | 0.013733 | -0.13275 | 0.045776 | 0.07782 | -0.068665 | 0.050354 | 0.041199 | -0.045776 | -0.10529 | 0.10071 | -0.045776 | -122.168 | 0.086975 | 0.10071 | 0.14648 | -122.2458 | 0.041199 | -0.018311 | -122.2046 | 0.13275 | 0.01831 | 0.036621 | -122.2137 | 0.17395 | 0.09613 | 0.064087 | -122.3877 | 0.13733 | 0.12817 | 0.16479 | -122.3602
3567.25 | 122.4335 | -0.054932 | 122.2183 | 0.10956 | 0.043351 | 0.059473 | 0.0010511 | 0.029542 | -0.0028178 | 0.031074 | 0.17426 | 0.028333 | 0.036668 | 0.050738 | 0.00081811 | 0.024582 | 0.07782 | 0.11902 | 0.11444 | 0.068665 | 0.045776 | 0.050354 | -0.09613 | 0.14648 | 0.14191 | 0.045776 | 0 | -0.009155 | -0.032043 | -0.073242 | 0.10529 | -0.041198 | -122.1725 | 0.17395 | 0.1236 | 0.16479 | -122.1405 | 0.022889 | -0.01831 | -122.2183 | 0.20142 | 0.10071 | 0.11902 | -122.2275 | 0.10071 | 0.13275 | 0.16937 | -122.3145 | 0.054932 | 0.045777 | 0.19684 | -122.2916
3569 | 122.4426 | -0.050354 | 122.2595 | -0.13458 | 0.043778 | 0.062677 | 0.0053235 | 0.030397 | -0.0079446 | 0.027442 | -0.10803 | 0.026837 | 0.03795 | 0.051378 | -0.0030271 | 0.025009 | 0.10986 | 0.15106 | 0.14191 | 0.086975 | 0.059509 | 0.054932 | -0.09613 | 0.13275 | 0.17853 | 0.059509 | 0.022888 | -0.004578 | -0.013733 | -0.07782 | 0.10529 | -0.045776 | -122.2 | 0.20142 | 0.13733 | 0.1831 | -122.1497 | 0.036621 | -0.027466 | -122.2366 | 0.18311 | 0.10986 | 0.13733 | -122.2641 | 0.10986 | 0.16022 | 0.19226 | -122.3557 | 0.073242 | 0.045776 | 0.22888 | -122.3373
3570.7031 | 122.3328 | -0.091553 | 122.2595 | -0.04303 | 0.047409 | 0.060968 | -0.00023075 | 0.03061 | 0.0025228 | 0.03086 | 0.059815 | 0.027906 | 0.037309 | 0.049883 | 0.0061587 | 0.022659 | 0.032043 | 0.018311 | -0.018311 | 0.004578 | 0.086975 | 0.041199 | -0.10529 | 0.054932 | 0.018311 | -0.086975 | 0.059509 | 0.041199 | -0.045776 | -0.10529 | 0.13275 | -0.013733 | -122.1725 | 0.10986 | 0.096131 | 0.10986 | -122.2275 | 0.045777 | -0.013733 | -122.2 | 0.14649 | 0.004578 | 0.018311 | -122.2183 | 0.17853 | 0.1236 | 0.073242 | -122.3648 | 0.15106 | 0.13275 | 0.10986 | -122.3648
3572.4688 | 122.4609 | -0.059509 | 122.2458 | 0.079041 | 0.044419 | 0.060968 | 0.0031873 | 0.029969 | -0.00089518 | 0.031074 | 0.075073 | 0.028546 | 0.037736 | 0.051378 | 0.00060451 | 0.027786 | 0 | 0.004578 | -0.018311 | -0.018311 | 0.09613 | 0.032043 | -0.1236 | 0.050354 | 0.013733 | -0.07782 | 0.073242 | 0.013733 | -0.059509 | -0.10071 | 0.091552 | -0.064087 | -122.1497 | 0.064087 | 0.041198 | 0.10528 | -122.2458 | 0 | -0.041199 | -122.1725 | 0.10986 | -0.018311 | 0.022888 | -122.2321 | 0.15564 | 0.059509 | 0.041198 | -122.3694 | 0.13275 | 0.073242 | 0.073242 | -122.3465
3574.1719 | 122.4701 | -0.041199 | 122.2458 | 0.14771 | 0.043137 | 0.060754 | 0.0016919 | 0.029969 | -0.0030314 | 0.032142 | 0.090332 | 0.030255 | 0.0356 | 0.050097 | 0.0016727 | 0.027359 | 0.032043 | 0.064087 | 0.064087 | 0.036621 | 0.073242 | 0.050354 | -0.086975 | 0.12817 | 0.10986 | 0.009155 | 0.027466 | 0.027466 | -0.018311 | -0.064087 | 0.091553 | -0.045776 | -122.1725 | 0.10529 | 0.07782 | 0.1236 | -122.2137 | 0.022888 | -0.022888 | -122.2183 | 0.16937 | 0.050354 | 0.073242 | -122.2183 | 0.11444 | 0.073242 | 0.10529 | -122.3328 | 0.068665 | 0.068665 | 0.15106 | -122.3099
3575.9375 | 122.4701 | -0.036621 | 122.2778 | -0.14221 | 0.041855 | 0.063104 | 0.0038281 | 0.028901 | -0.0079446 | 0.028937 | -0.1004 | 0.025556 | 0.036882 | 0.049669 | -0.0023861 | 0.027145 | 0.086975 | 0.15106 | 0.1236 | 0.068665 | 0.041199 | 0.050354 | -0.086975 | 0.13275 | 0.18768 | 0.054932 | 0.041199 | 0.013733 | -0.013733 | -0.064087 | 0.086975 | -0.050354 | -122.2366 | 0.18768 | 0.10529 | 0.15564 | -122.1909 | 0.022888 | -0.027466 | -122.2366 | 0.16937 | 0.091553 | 0.11902 | -122.2641 | 0.07782 | 0.1236 | 0.16022 | -122.3648 | 0.07782 | 0.050354 | 0.2243 | -122.3419
3577.625 | 122.3328 | -0.091553 | 122.287 | -0.088806 | 0.048264 | 0.060114 | 0.0027601 | 0.030824 | 0.0016684 | 0.030646 | -0.1004 | 0.030255 | 0.038805 | 0.052019 | 0.00081811 | 0.022873 | 0.082397 | 0.064087 | 0.032043 | 0.022888 | 0.082397 | 0.045776 | -0.1236 | 0.082397 | 0.068665 | -0.064087 | 0.054932 | 0.050354 | -0.027466 | -0.10529 | 0.13733 | -0.032043 | -122.2046 | 0.15564 | 0.11444 | 0.14648 | -122.2046 | 0.064087 | -0.013733 | -122.2321 | 0.17395 | 0.027466 | 0.041199 | -122.2366 | 0.17395 | 0.17395 | 0.1236 | -122.4106 | 0.14649 | 0.14191 | 0.16022 | -122.3923
3579.375 | 122.3602 | -0.086975 | 122.2458 | 0.033264 | 0.046768 | 0.060541 | 0.00019645 | 0.032533 | -0.00025418 | 0.030433 | 0.059815 | 0.02876 | 0.037096 | 0.05031 | 0.0035953 | 0.0233 | -0.032043 | -0.045776 | -0.050354 | -0.032043 | 0.086975 | 0 | -0.12817 | 0.018311 | -0.004578 | -0.10986 | 0.059509 | 0.036621 | -0.041199 | -0.11444 | 0.086975 | -0.041199 | -122.1588 | 0.041199 | 0.054932 | 0.096131 | -122.2778 | 0.045776 | -0.027466 | -122.1863 | 0.10529 | -0.022888 | 0.004578 | -122.2092 | 0.17395 | 0.054932 | 0.036621 | -122.374 | 0.14648 | 0.1236 | 0.082397 | -122.3602
3581.1406 | 122.4289 | -0.068665 | 122.2549 | 0.048523 | 0.04506 | 0.059473 | 0.0059643 | 0.03061 | -0.0092264 | 0.031501 | 0.075073 | 0.025556 | 0.037309 | 0.050738 | -0.0025999 | 0.029708 | 0.027466 | 0.073242 | 0.068665 | 0.018311 | 0.064087 | 0.054932 | -0.091553 | 0.09613 | 0.086975 | -0.004578 | 0.027466 | 0.013733 | -0.032043 | -0.064087 | 0.1236 | -0.022888 | -122.1909 | 0.14191 | 0.086976 | 0.10986 | -122.2275 | 0.036622 | 0.004578 | -122.2275 | 0.16479 | 0.064087 | 0.059509 | -122.2412 | 0.13275 | 0.096131 | 0.13733 | -122.3465 | 0.096131 | 0.082398 | 0.15564 | -122.319
3582.8594 | 122.3557 | -0.10071 | 122.2824 | -0.21088 | 0.04506 | 0.061609 | 0.0053235 | 0.032533 | -0.0062356 | 0.032569 | -0.11566 | 0.025128 | 0.038377 | 0.050097 | -0.0047361 | 0.026504 | 0.073242 | 0.1236 | 0.11902 | 0.059509 | 0.059509 | 0.036621 | -0.10071 | 0.1236 | 0.16479 | 0.032043 | 0.036621 | 0.022888 | -0.009155 | -0.07782 | 0.13733 | 0 | -122.2229 | 0.2243 | 0.16022 | 0.16022 | -122.2092 | 0.091553 | 0.022888 | -122.2458 | 0.2243 | 0.13275 | 0.10986 | -122.2595 | 0.16022 | 0.17395 | 0.21973 | -122.3831 | 0.13733 | 0.1236 | 0.2655 | -122.3602
3584.6406 | 122.4472 | -0.050354 | 122.2275 | 0.11719 | 0.0457 | 0.058618 | 0.00062385 | 0.031465 | -0.003245 | 0.030646 | 0.159 | 0.028546 | 0.035814 | 0.05031 | 0.0029543 | 0.025863 | 0.10071 | 0.11444 | 0.10529 | 0.082397 | 0.045776 | 0.045776 | -0.068665 | 0.14648 | 0.14648 | 0.027466 | 0.022888 | 0.004578 | -0.036621 | -0.064087 | 0.09613 | -0.018311 | -122.1817 | 0.16479 | 0.13275 | 0.15106 | -122.1268 | 0.013733 | -0.013733 | -122.2046 | 0.19684 | 0.07782 | 0.091553 | -122.2229 | 0.09613 | 0.15106 | 0.15564 | -122.2961 | 0.073242 | 0.054932 | 0.19684 | -122.2916
3586.3906 | 122.3465 | -0.09613 | 122.2778 | 0.16296 | 0.048905 | 0.057336 | -1.7146e-05 | 0.031678 | 0.0016684 | 0.032996 | -0.024109 | 0.030255 | 0.034318 | 0.050951 | 0.0029543 | 0.024582 | 0.009155 | -0.027466 | -0.032043 | -0.018311 | 0.10529 | 0.027466 | -0.12817 | 0.013733 | -0.004578 | -0.1236 | 0.073242 | 0.050354 | -0.064087 | -0.10529 | 0.1236 | -0.032044 | -122.1725 | 0.068664 | 0.077819 | 0.10986 | -122.2687 | 0.032043 | -0.009156 | -122.2046 | 0.10986 | -0.027466 | -0.01831 | -122.2275 | 0.20142 | 0.10528 | 0.064087 | -122.406 | 0.16937 | 0.14648 | 0.091552 | -122.3831
3588.1562 | 122.4884 | -0.064087 | 122.2321 | -0.020142 | 0.045273 | 0.0599 | 0.0061781 | 0.025483 | -0.0068766 | 0.031074 | 0.0064086 | 0.028119 | 0.036668 | 0.048815 | -0.0036679 | 0.027359 | 0.022888 | 0.064087 | 0.068665 | 0.045776 | 0.064087 | 0.032043 | -0.11444 | 0.11902 | 0.1236 | 0.041199 | 0.036621 | 0.022888 | -0.022888 | -0.073242 | 0.09613 | -0.050354 | -122.168 | 0.12817 | 0.10986 | 0.16022 | -122.2092 | 0.041199 | -0.009155 | -122.1954 | 0.18311 | 0.10529 | 0.11444 | -122.2092 | 0.12817 | 0.086975 | 0.13275 | -122.3465 | 0.10071 | 0.086975 | 0.18768 | -122.3053
3589.8594 | 122.3328 | -0.10071 | 122.2733 | -0.020142 | 0.048905 | 0.0599 | 0.0038281 | 0.030824 | 0.0023092 | 0.031501 | 0.014038 | 0.030469 | 0.037096 | 0.05266 | 0.0025271 | 0.024154 | 0.036621 | -0.009155 | -0.022888 | 0.004578 | 0.07782 | 0.013733 | -0.11444 | 0.009155 | 0.022888 | -0.10529 | 0.059509 | 0.045776 | -0.059509 | -0.086975 | 0.11444 | -0.013733 | -122.1954 | 0.091553 | 0.10529 | 0.11902 | -122.2366 | 0.041199 | 0.013733 | -122.2137 | 0.10986 | -0.004578 | -0.018311 | -122.2275 | 0.17853 | 0.13733 | 0.07782 | -122.3877 | 0.16022 | 0.14648 | 0.1236 | -122.3602
3591.6094 | 122.3877 | -0.068665 | 122.2641 | -0.21851 | 0.044846 | 0.061182 | 0.0046827 | 0.03061 | -0.0011088 | 0.031287 | -0.19196 | 0.028546 | 0.036668 | 0.051592 | -0.0011045 | 0.026077 | -0.013733 | -0.009155 | -0.018311 | 0.009155 | 0.10071 | -0.009155 | -0.13733 | 0.027466 | 0.045776 | -0.082397 | 0.059509 | 0.041199 | -0.054932 | -0.09613 | 0.05951 | -0.068664 | -122.1634 | 0.05951 | 0.07782 | 0.14648 | -122.2778 | 0.013733 | -0.027465 | -122.2046 | 0.096131 | -0.013732 | 0.013733 | -122.2229 | 0.16937 | 0.054932 | 0.050354 | -122.4014 | 0.12817 | 0.10986 | 0.11444 | -122.3602
3593.375 | 122.3831 | -0.082397 | 122.2595 | -0.18799 | 0.047409 | 0.059686 | 0.00083745 | 0.029328 | -0.00025418 | 0.031501 | -0.19196 | 0.029615 | 0.037736 | 0.049883 | -0.00046349 | 0.026077 | -0.004578 | 0.013733 | -0.013733 | 0 | 0.086975 | 0.013733 | -0.13733 | 0.059509 | 0.086975 | -0.059509 | 0.054932 | 0.041199 | -0.054932 | -0.10071 | 0.09613 | -0.054932 | -122.1725 | 0.09613 | 0.082397 | 0.13733 | -122.2641 | 0.027465 | -0.018311 | -122.2046 | 0.14191 | 0.022888 | 0.041199 | -122.2183 | 0.16937 | 0.077819 | 0.068664 | -122.3969 | 0.13733 | 0.1236 | 0.16937 | -122.3602
3595.1406 | 122.4243 | -0.054932 | 122.2321 | 0.033264 | 0.044632 | 0.061609 | 0.0027601 | 0.029542 | -0.010935 | 0.031501 | 0.090332 | 0.027478 | 0.036027 | 0.048388 | -0.0055905 | 0.026504 | 0.018311 | 0.068665 | 0.059509 | 0.027466 | 0.041199 | 0.050354 | -0.09613 | 0.091553 | 0.10071 | 0.009155 | 0.027466 | 0.036621 | -0.004578 | -0.068665 | 0.10529 | -0.041198 | -122.1909 | 0.1236 | 0.082398 | 0.1236 | -122.2137 | 0.050354 | -0.013733 | -122.2046 | 0.14649 | 0.064087 | 0.07782 | -122.1954 | 0.096131 | 0.073243 | 0.11444 | -122.3282 | 0.082398 | 0.091553 | 0.15564 | -122.3007
3596.9062 | 122.3373 | -0.10529 | 122.2733 | -0.18036 | 0.0457 | 0.060327 | 0.0061781 | 0.031465 | -0.0068766 | 0.029365 | -0.19196 | 0.026837 | 0.0356 | 0.052019 | -0.0019589 | 0.026504 | 0.059509 | 0.11902 | 0.07782 | 0.050354 | 0.054932 | 0.032043 | -0.091553 | 0.068665 | 0.1236 | -0.013733 | 0.027466 | 0.036621 | -0.027466 | -0.091553 | 0.13733 | 0.013733 | -122.2183 | 0.22431 | 0.15564 | 0.14191 | -122.2137 | 0.07782 | 0.013733 | -122.2458 | 0.17395 | 0.091553 | 0.07782 | -122.2366 | 0.16022 | 0.16479 | 0.18311 | -122.3648 | 0.13275 | 0.14191 | 0.22888 | -122.3648
3598.6094 | 122.4976 | -0.054932 | 122.2458 | -0.050659 | 0.044419 | 0.060541 | 0.0044691 | 0.031037 | -0.0079446 | 0.029365 | -0.054626 | 0.025769 | 0.036241 | 0.048174 | -0.00024989 | 0.027786 | 0.041199 | 0.091553 | 0.082397 | 0.050354 | 0.054932 | 0.045776 | -0.10071 | 0.13275 | 0.15564 | 0.073242 | 0.022888 | 0.018311 | -0.013733 | -0.068665 | 0.10071 | -0.045776 | -122.1909 | 0.14649 | 0.10529 | 0.15106 | -122.2046 | 0.041199 | -0.013733 | -122.2229 | 0.18768 | 0.12817 | 0.14191 | -122.2275 | 0.10986 | 0.096131 | 0.13733 | -122.3465 | 0.07782 | 0.073243 | 0.21057 | -122.3145
3600.3594 | 122.3511 | -0.07782 | 122.2778 | -0.20325 | 0.043564 | 0.061182 | 0.0025465 | 0.032319 | -0.0051676 | 0.028083 | -0.14618 | 0.027265 | 0.03795 | 0.048174 | -0.00067729 | 0.025436 | 0.086975 | 0.13275 | 0.11444 | 0.064087 | 0.045776 | 0.054932 | -0.09613 | 0.11902 | 0.16937 | 0.041199 | 0.022888 | 0.009155 | 0.018311 | -0.086975 | 0.13275 | -0.01831 | -122.2321 | 0.21057 | 0.14191 | 0.16022 | -122.1909 | 0.096131 | -0.009155 | -122.2549 | 0.19684 | 0.11902 | 0.12817 | -122.2687 | 0.1236 | 0.16479 | 0.19226 | -122.374 | 0.10071 | 0.086975 | 0.24719 | -122.3648
3602.125 | 122.3877 | -0.09613 | 122.287 | -0.14984 | 0.046128 | 0.059473 | 0.00041005 | 0.031251 | 0.0029502 | 0.034492 | -0.18433 | 0.029187 | 0.035814 | 0.051165 | 0.0020999 | 0.022659 | 0.054932 | 0.059509 | 0.018311 | 0.032043 | 0.086975 | 0.018311 | -0.10529 | 0.07782 | 0.086975 | -0.041199 | 0.054932 | 0.032043 | -0.027466 | -0.10071 | 0.11444 | -0.009156 | -122.2 | 0.15564 | 0.12817 | 0.13733 | -122.2321 | 0.068664 | -0.004578 | -122.2321 | 0.17395 | 0.054931 | 0.059509 | -122.2549 | 0.1831 | 0.15106 | 0.11444 | -122.3923 | 0.15106 | 0.12817 | 0.1831 | -122.3877
3603.8906 | 122.4976 | -0.064087 | 122.2366 | -0.065918 | 0.043991 | 0.060968 | 0.0034009 | 0.032533 | -0.0079446 | 0.029151 | -0.039368 | 0.027265 | 0.035814 | 0.050951 | -0.0021725 | 0.028213 | 0.036621 | 0.086975 | 0.091553 | 0.041199 | 0.064087 | 0.041199 | -0.086975 | 0.15106 | 0.15564 | 0.064087 | 0.041199 | 0.004578 | -0.027466 | -0.086975 | 0.10529 | -0.022888 | -122.1725 | 0.15106 | 0.10529 | 0.12817 | -122.2 | 0.036621 | -0.022888 | -122.1954 | 0.21515 | 0.12817 | 0.15106 | -122.2321 | 0.12817 | 0.10071 | 0.15564 | -122.3236 | 0.10529 | 0.068665 | 0.21973 | -122.3236
3605.6406 | 122.4792 | -0.059509 | 122.2595 | 0.010376 | 0.044205 | 0.061609 | 0.0034009 | 0.03061 | -0.0053812 | 0.028724 | 0.029297 | 0.025128 | 0.034105 | 0.049029 | 0.00017731 | 0.026718 | 0.022888 | 0.050354 | 0.059509 | 0.032043 | 0.059509 | 0.045776 | -0.10071 | 0.082397 | 0.10529 | 0.004578 | 0.022888 | 0.013733 | -0.018311 | -0.086975 | 0.10528 | -0.041199 | -122.2 | 0.10986 | 0.091552 | 0.13275 | -122.2366 | 0.041198 | -0.027466 | -122.2366 | 0.14191 | 0.064087 | 0.091553 | -122.2458 | 0.11902 | 0.082397 | 0.11902 | -122.3602 | 0.082397 | 0.073242 | 0.16479 | -122.3465
3607.4062 | 122.3465 | -0.10986 | 122.287 | -0.17273 | 0.0457 | 0.060754 | 0.0038281 | 0.030397 | -0.0028178 | 0.030219 | -0.18433 | 0.025769 | 0.036455 | 0.048601 | -0.00024989 | 0.024368 | 0.073242 | 0.1236 | 0.11444 | 0.064087 | 0.050354 | 0.050354 | -0.091553 | 0.10071 | 0.14191 | 0.009155 | 0.032043 | 0 | -0.041199 | -0.064087 | 0.16022 | 0.01831 | -122.2366 | 0.23346 | 0.17395 | 0.15564 | -122.2137 | 0.068664 | 0.045776 | -122.2549 | 0.21057 | 0.11902 | 0.073242 | -122.287 | 0.16022 | 0.18311 | 0.2243 | -122.3785 | 0.14191 | 0.10986 | 0.25177 | -122.3511
3609.1094 | 122.4335 | -0.050354 | 122.2412 | -0.17273 | 0.045273 | 0.063318 | 0.0055371 | 0.029756 | -0.004313 | 0.030646 | -0.1767 | 0.027478 | 0.035173 | 0.050097 | -0.0021725 | 0.024795 | 0.10071 | 0.14648 | 0.1236 | 0.064087 | 0.054932 | 0.036621 | -0.086975 | 0.15564 | 0.19684 | 0.054932 | 0.009155 | 0.004578 | 0.004578 | -0.059509 | 0.086975 | -0.036621 | -122.1863 | 0.19684 | 0.11444 | 0.15106 | -122.1405 | 0.054932 | -0.009155 | -122.2321 | 0.20599 | 0.10529 | 0.11444 | -122.2366 | 0.10529 | 0.15106 | 0.17395 | -122.3282 | 0.059509 | 0.054932 | 0.24719 | -122.3007
3610.8594 | 122.4792 | -0.050354 | 122.2549 | -0.11932 | 0.042496 | 0.060327 | 0.0036145 | 0.029542 | -0.0051676 | 0.031714 | -0.092773 | 0.026197 | 0.036241 | 0.051165 | -0.0038815 | 0.024795 | 0.09613 | 0.13275 | 0.10986 | 0.073242 | 0.073242 | 0.022888 | -0.10071 | 0.16937 | 0.16937 | 0.064087 | 0.022888 | 0.018311 | -0.013733 | -0.059509 | 0.073242 | -0.050354 | -122.1817 | 0.18311 | 0.1236 | 0.17395 | -122.1588 | 0.036621 | -0.009155 | -122.2321 | 0.21973 | 0.11444 | 0.1236 | -122.2366 | 0.1236 | 0.14648 | 0.16022 | -122.3557 | 0.073242 | 0.068665 | 0.21973 | -122.3145
3612.6094 | 122.3923 | -0.11444 | 122.2504 | -0.24902 | 0.047409 | 0.061395 | 0.0048963 | 0.029542 | 0.0010276 | 0.030433 | -0.28351 | 0.030042 | 0.037736 | 0.050951 | -0.0015317 | 0.021164 | 0.018311 | -0.004578 | -0.032043 | -0.013733 | 0.10071 | 0.004578 | -0.13275 | 0.022888 | 0.022888 | -0.09613 | 0.059509 | 0.045776 | -0.054932 | -0.10071 | 0.11902 | -0.01831 | -122.1497 | 0.10986 | 0.10071 | 0.11902 | -122.2321 | 0.059509 | 0.013733 | -122.1909 | 0.13733 | 0.018311 | 0.004578 | -122.2046 | 0.21515 | 0.13275 | 0.082398 | -122.3831 | 0.17395 | 0.16022 | 0.13733 | -122.3511
3614.3125 | 122.4701 | -0.045776 | 122.2412 | 0.14008 | 0.044419 | 0.061395 | -0.0010851 | 0.032533 | 0.00081382 | 0.032569 | 0.097962 | 0.027478 | 0.0356 | 0.049242 | 0.0038089 | 0.024154 | 0.036621 | 0.027466 | 0.022888 | 0.004578 | 0.059509 | 0.027466 | -0.10529 | 0.12817 | 0.07782 | -0.022888 | 0.036621 | 0.022888 | -0.041199 | -0.073242 | 0.073242 | -0.05951 | -122.1817 | 0.073242 | 0.050354 | 0.10986 | -122.2046 | 0.004577 | -0.027466 | -122.2046 | 0.17395 | 0.022888 | 0.050354 | -122.2183 | 0.10528 | 0.082397 | 0.068664 | -122.3465 | 0.082397 | 0.068664 | 0.1236 | -122.3145
3616.0781 | 122.3877 | -0.086975 | 122.2687 | -0.14984 | 0.045487 | 0.060541 | 0.0025465 | 0.031037 | -0.0011088 | 0.033423 | -0.16144 | 0.028333 | 0.036455 | 0.049242 | 0.0027407 | 0.024582 | 0.045776 | 0.059509 | 0.013733 | 0.022888 | 0.09613 | 0.018311 | -0.11444 | 0.082397 | 0.09613 | -0.041199 | 0.050354 | 0.041199 | -0.032043 | -0.09613 | 0.10529 | -0.027466 | -122.1725 | 0.14648 | 0.10986 | 0.13733 | -122.2229 | 0.054932 | -0.009155 | -122.2183 | 0.16937 | 0.045776 | 0.054931 | -122.2275 | 0.1831 | 0.13275 | 0.10071 | -122.3831 | 0.13733 | 0.12817 | 0.1831 | -122.3648
3617.8281 | 122.3969 | -0.068665 | 122.2458 | -0.19562 | 0.049118 | 0.060327 | 0.0055371 | 0.031892 | -4.058e-05 | 0.032142 | -0.1767 | 0.028119 | 0.03795 | 0.049669 | 0.00060451 | 0.02565 | 0.041199 | 0.018311 | 0.004578 | 0.018311 | 0.082397 | 0.022888 | -0.13733 | 0.07782 | 0.068665 | -0.054932 | 0.050354 | 0.064087 | -0.050354 | -0.10529 | 0.091553 | -0.068664 | -122.1634 | 0.086976 | 0.086976 | 0.15564 | -122.2046 | 0.018311 | -0.036621 | -122.1954 | 0.14649 | 0.013733 | 0.050354 | -122.1817 | 0.15106 | 0.10986 | 0.073243 | -122.3831 | 0.11902 | 0.13275 | 0.13733 | -122.3511
3619.5938 | 122.4609 | -0.041199 | 122.2412 | 0.15533 | 0.047409 | 0.060968 | 0.00083745 | 0.02826 | -0.0034586 | 0.032996 | 0.044556 | 0.030683 | 0.034318 | 0.05031 | 0.0025271 | 0.027786 | 0.054932 | 0.091553 | 0.068665 | 0.054932 | 0.064087 | 0.059509 | -0.10529 | 0.14191 | 0.12817 | 0.032043 | 0.018311 | 0.018311 | -0.009155 | -0.073242 | 0.10071 | -0.064087 | -122.1771 | 0.13275 | 0.096131 | 0.16022 | -122.1863 | 0.032044 | -0.032043 | -122.2229 | 0.18311 | 0.073242 | 0.10529 | -122.2229 | 0.10529 | 0.096131 | 0.10986 | -122.3465 | 0.05951 | 0.05951 | 0.16937 | -122.3145
3621.3594 | 122.4335 | -0.059509 | 122.2412 | 0.14771 | 0.043778 | 0.059686 | 0.0019055 | 0.031037 | -0.0055948 | 0.032142 | 0.15137 | 0.026624 | 0.036455 | 0.048388 | 0.0018863 | 0.026504 | 0.09613 | 0.1236 | 0.10071 | 0.054932 | 0.032043 | 0.041199 | -0.082397 | 0.16022 | 0.16022 | 0.050354 | 0.022888 | 0.009155 | -0.013733 | -0.068665 | 0.10071 | -0.022888 | -122.2092 | 0.1831 | 0.11444 | 0.13733 | -122.1451 | 0.045776 | -0.009156 | -122.2183 | 0.21973 | 0.10986 | 0.11902 | -122.2321 | 0.091552 | 0.15564 | 0.16022 | -122.3236 | 0.082397 | 0.068664 | 0.21973 | -122.3099
3623.125 | 122.3511 | -0.086975 | 122.2916 | -0.096436 | 0.047409 | 0.058191 | 0.0029737 | 0.031465 | -0.00089518 | 0.033423 | -0.12329 | 0.030042 | 0.036241 | 0.049883 | 0.0023135 | 0.025436 | 0.068665 | 0.045776 | 0.032043 | 0.022888 | 0.073242 | 0.022888 | -0.1236 | 0.091553 | 0.07782 | -0.054932 | 0.064087 | 0.041199 | -0.022888 | -0.10071 | 0.10986 | -0.036621 | -122.2183 | 0.13275 | 0.10986 | 0.14648 | -122.2229 | 0.064087 | -0.013733 | -122.2275 | 0.17853 | 0.032043 | 0.045776 | -122.2504 | 0.16022 | 0.15564 | 0.11902 | -122.4152 | 0.15106 | 0.12817 | 0.16479 | -122.3923
3624.8281 | 122.4197 | -0.050354 | 122.2641 | 0.040894 | 0.042282 | 0.059259 | 0.0019055 | 0.029328 | -0.0075174 | 0.029365 | 0.11322 | 0.026624 | 0.037523 | 0.049456 | -0.0017453 | 0.027572 | 0.045776 | 0.07782 | 0.073242 | 0.022888 | 0.054932 | 0.041199 | -0.091553 | 0.10071 | 0.10071 | 0.009155 | 0.027466 | 0.013733 | -0.022888 | -0.086975 | 0.091553 | -0.041199 | -122.2092 | 0.12817 | 0.073242 | 0.11444 | -122.2183 | 0.027466 | -0.036621 | -122.2366 | 0.15106 | 0.059509 | 0.09613 | -122.2504 | 0.10529 | 0.09613 | 0.1236 | -122.3557 | 0.07782 | 0.064087 | 0.15106 | -122.3511
3626.5781 | 122.4701 | -0.041199 | 122.2458 | -0.19562 | 0.042496 | 0.061609 | 0.0027601 | 0.028047 | -0.0092264 | 0.029365 | -0.085144 | 0.026624 | 0.036027 | 0.049883 | -0.0013181 | 0.024795 | 0.068665 | 0.12817 | 0.11902 | 0.054932 | 0.050354 | 0.045776 | -0.10071 | 0.16022 | 0.16937 | 0.07782 | 0.013733 | 0.009155 | -0.009155 | -0.068665 | 0.086975 | -0.059509 | -122.1954 | 0.16937 | 0.096131 | 0.15564 | -122.1771 | 0.032044 | -0.027466 | -122.2321 | 0.20142 | 0.11902 | 0.14649 | -122.2366 | 0.091553 | 0.10986 | 0.16022 | -122.3465 | 0.054932 | 0.050354 | 0.21057 | -122.3145
3628.3281 | 122.4655 | -0.064087 | 122.2458 | -0.0048827 | 0.043351 | 0.062036 | 0.00062385 | 0.032319 | -0.0053812 | 0.026801 | 0.021668 | 0.027906 | 0.035173 | 0.05031 | -0.0011045 | 0.026291 | 0.022888 | 0.059509 | 0.054932 | 0.027466 | 0.064087 | 0.041199 | -0.07782 | 0.07782 | 0.082397 | 0.009155 | 0.018311 | 0.018311 | -0.013733 | -0.09613 | 0.10529 | -0.013733 | -122.1817 | 0.1236 | 0.091553 | 0.10529 | -122.2229 | 0.050354 | -0.032043 | -122.2275 | 0.14191 | 0.073242 | 0.10528 | -122.2275 | 0.12817 | 0.086975 | 0.11902 | -122.3236 | 0.082398 | 0.082398 | 0.14648 | -122.3419
3630.0938 | 122.3465 | -0.091553 | 122.2641 | 0.079041 | 0.045914 | 0.058191 | 0.0019055 | 0.03061 | 0.00060022 | 0.031501 | -0.039368 | 0.030469 | 0.038164 | 0.051378 | 0.0038089 | 0.024582 | 0.022888 | -0.050354 | -0.036621 | -0.004578 | 0.082397 | 0.032043 | -0.11902 | 0.009155 | -0.013733 | -0.10986 | 0.064087 | 0.059509 | -0.050354 | -0.11444 | 0.1236 | -0.027466 | -122.1817 | 0.041199 | 0.086975 | 0.11444 | -122.2412 | 0.041199 | -0.022888 | -122.2 | 0.10071 | -0.01831 | 0.004578 | -122.2046 | 0.17395 | 0.11444 | 0.054932 | -122.3831 | 0.15564 | 0.15106 | 0.07782 | -122.3785
3631.7969 | 122.3969 | -0.10529 | 122.2687 | -0.18036 | 0.049759 | 0.0599 | 0.0048963 | 0.03061 | -0.0011088 | 0.034064 | -0.22247 | 0.027478 | 0.036241 | 0.048388 | 0.0010317 | 0.02565 | 0.009155 | 0.009155 | -0.009155 | 0 | 0.073242 | 0.032043 | -0.1236 | 0.036621 | 0.064087 | -0.059509 | 0.073242 | 0.059509 | -0.073242 | -0.09613 | 0.13733 | -0.01831 | -122.1954 | 0.11444 | 0.10529 | 0.1236 | -122.2595 | 0.032044 | 0.009156 | -122.1954 | 0.14191 | 0.045777 | 0.036621 | -122.2092 | 0.17853 | 0.11444 | 0.096131 | -122.3923 | 0.17853 | 0.16479 | 0.16937 | -122.3648
3633.5625 | 122.3831 | -0.073242 | 122.2824 | -0.19562 | 0.0457 | 0.060327 | 0.0021191 | 0.030824 | -0.00089518 | 0.031501 | -0.18433 | 0.029401 | 0.037736 | 0.050951 | 0.0020999 | 0.025863 | 0.009155 | -0.004578 | -0.018311 | 0.018311 | 0.10071 | 0.018311 | -0.1236 | 0.054932 | 0.07782 | -0.050354 | 0.045776 | 0.036621 | -0.045776 | -0.10071 | 0.091553 | -0.050354 | -122.1817 | 0.068664 | 0.091553 | 0.14191 | -122.2733 | 0.027466 | -0.027466 | -122.2366 | 0.12817 | 0.022888 | 0.050354 | -122.2458 | 0.17395 | 0.082397 | 0.054931 | -122.406 | 0.11902 | 0.10986 | 0.15106 | -122.3831
3635.3281 | 122.3694 | -0.10071 | 122.3007 | -0.30243 | 0.045273 | 0.060327 | 0.0051099 | 0.030824 | -0.0045266 | 0.030006 | -0.19196 | 0.027478 | 0.037523 | 0.050097 | -0.0025999 | 0.029495 | -0.022888 | 0.022888 | 0 | -0.009155 | 0.086975 | -0.009155 | -0.13733 | 0.022888 | 0.045776 | -0.068665 | 0.050354 | 0.059509 | -0.068665 | -0.10986 | 0.091553 | -0.036621 | -122.2137 | 0.1236 | 0.091553 | 0.12817 | -122.3236 | 0.032043 | -0.009155 | -122.2504 | 0.1236 | 0.032043 | 0.041198 | -122.2412 | 0.18768 | 0.07782 | 0.10071 | -122.438 | 0.15106 | 0.16022 | 0.14648 | -122.4106
3637.0781 | 122.4655 | -0.068665 | 122.2137 | -0.096436 | 0.043137 | 0.062677 | 0.0046827 | 0.028688 | -0.0092264 | 0.030219 | -0.069885 | 0.02641 | 0.036882 | 0.050738 | -0.0015317 | 0.028854 | 0.091553 | 0.13275 | 0.1236 | 0.073242 | 0.068665 | 0.050354 | -0.09613 | 0.15564 | 0.17853 | 0.073242 | 0.027466 | 0.004578 | 0 | -0.050354 | 0.11902 | -0.027465 | -122.1451 | 0.20142 | 0.14191 | 0.16937 | -122.1222 | 0.068665 | 0.018311 | -122.1863 | 0.22431 | 0.14191 | 0.1236 | -122.2092 | 0.13733 | 0.16022 | 0.19226 | -122.3099 | 0.096131 | 0.073243 | 0.24719 | -122.2641
3638.8281 | 122.4518 | -0.050354 | 122.2687 | -0.14221 | 0.045487 | 0.062036 | 0.0016919 | 0.031037 | -0.0040994 | 0.029151 | -0.13855 | 0.024274 | 0.034746 | 0.048815 | -0.0028135 | 0.025863 | 0.086975 | 0.15106 | 0.11444 | 0.07782 | 0.045776 | 0.045776 | -0.10071 | 0.13275 | 0.19226 | 0.068665 | 0.027466 | -0.009155 | -0.004578 | -0.068665 | 0.09613 | -0.050354 | -122.2229 | 0.20142 | 0.12817 | 0.17853 | -122.1817 | 0.045776 | -0.018311 | -122.2412 | 0.18311 | 0.11902 | 0.13733 | -122.2778 | 0.09613 | 0.13733 | 0.16479 | -122.3694 | 0.07782 | 0.041199 | 0.24261 | -122.3373
3640.5938 | 122.4335 | -0.054932 | 122.2412 | 0.16296 | 0.043991 | 0.060327 | -0.0019397 | 0.033387 | -0.0058084 | 0.030646 | 0.14374 | 0.027478 | 0.034318 | 0.049883 | 0.0040225 | 0.02565 | 0.10071 | 0.13275 | 0.10071 | 0.064087 | 0.032043 | 0.059509 | -0.064087 | 0.15564 | 0.13733 | 0.036621 | 0.018311 | -0.009155 | -0.032043 | -0.054932 | 0.11444 | -0.009155 | -122.2092 | 0.18768 | 0.11902 | 0.12817 | -122.1405 | 0.022889 | 0 | -122.2229 | 0.21057 | 0.091553 | 0.091553 | -122.2504 | 0.086975 | 0.15564 | 0.15564 | -122.3053 | 0.073243 | 0.045777 | 0.19226 | -122.2961
3642.2812 | 122.3557 | -0.082397 | 122.2916 | -0.14984 | 0.046555 | 0.061609 | 0.0066053 | 0.031251 | -0.0030314 | 0.029792 | -0.20721 | 0.029401 | 0.036027 | 0.05031 | -0.00046349 | 0.025436 | 0.004578 | 0.013733 | 0.004578 | -0.009155 | 0.07782 | 0.013733 | -0.14648 | 0.018311 | 0.045776 | -0.073242 | 0.054932 | 0.054932 | -0.041199 | -0.10986 | 0.09613 | -0.064087 | -122.2137 | 0.09613 | 0.073242 | 0.13733 | -122.287 | 0.041198 | -0.027466 | -122.2366 | 0.10071 | 0.009155 | 0.036621 | -122.2366 | 0.16022 | 0.086975 | 0.086975 | -122.438 | 0.13733 | 0.13733 | 0.12817 | -122.4014
3644.0469 | 122.3831 | -0.07782 | 122.2824 | 0.08667 | 0.048477 | 0.0599 | 0.0016919 | 0.030824 | 0.00081382 | 0.03321 | 0.044556 | 0.02876 | 0.037309 | 0.05031 | 0.0038089 | 0.024368 | 0.009155 | -0.054932 | -0.041199 | -0.013733 | 0.10071 | 0.009155 | -0.13275 | 0.041199 | -0.018311 | -0.11444 | 0.064087 | 0.036621 | -0.073242 | -0.091553 | 0.086975 | -0.054931 | -122.1817 | 0.022888 | 0.064087 | 0.11902 | -122.2733 | 0.004578 | -0.013733 | -122.2183 | 0.11902 | -0.036621 | -0.022888 | -122.2458 | 0.17853 | 0.086975 | 0.036621 | -122.4152 | 0.14191 | 0.11444 | 0.059509 | -122.374
3645.8125 | 122.4747 | -0.022888 | 122.2595 | 0.14771 | 0.046341 | 0.058405 | 0.0014783 | 0.031037 | -0.002604 | 0.03321 | 0.11322 | 0.028974 | 0.035814 | 0.048601 | 0.0025271 | 0.028854 | 0.068665 | 0.073242 | 0.064087 | 0.059509 | 0.064087 | 0.045776 | -0.10986 | 0.14648 | 0.11902 | 0.009155 | 0.009155 | 0.009155 | -0.018311 | -0.059509 | 0.068664 | -0.086975 | -122.1954 | 0.09613 | 0.082397 | 0.16937 | -122.1909 | 0.004577 | -0.036621 | -122.2504 | 0.16937 | 0.032043 | 0.068664 | -122.2504 | 0.086975 | 0.091553 | 0.086975 | -122.3694 | 0.032043 | 0.032043 | 0.14191 | -122.319
3647.5156 | 122.4289 | -0.045776 | 122.2641 | 0.12482 | 0.043778 | 0.060114 | 0.0016919 | 0.029115 | -0.006663 | 0.032569 | 0.11322 | 0.025769 | 0.034318 | 0.049242 | 0.00081811 | 0.026931 | 0.091553 | 0.13733 | 0.09613 | 0.059509 | 0.041199 | 0.054932 | -0.091553 | 0.15564 | 0.13733 | 0.032043 | 0.027466 | 0.013733 | -0.018311 | -0.082397 | 0.10071 | -0.045777 | -122.2229 | 0.18311 | 0.10528 | 0.15106 | -122.1725 | 0.027465 | -0.036621 | -122.2366 | 0.20142 | 0.077819 | 0.11444 | -122.2504 | 0.086975 | 0.13733 | 0.14191 | -122.3557 | 0.073242 | 0.059509 | 0.18311 | -122.3465
3649.2812 | 122.4518 | -0.050354 | 122.2321 | 0.12482 | 0.045487 | 0.058191 | 0.0040417 | 0.029328 | -0.00089518 | 0.031074 | 0.159 | 0.027692 | 0.037736 | 0.04732 | 0.00060451 | 0.026718 | 0.10986 | 0.11444 | 0.10071 | 0.068665 | 0.036621 | 0.045776 | -0.073242 | 0.16479 | 0.14648 | 0.041199 | 0.022888 | 0.022888 | -0.022888 | -0.073242 | 0.09613 | -0.022888 | -122.1954 | 0.16479 | 0.11902 | 0.14191 | -122.1222 | 0.027466 | -0.022888 | -122.2092 | 0.21515 | 0.091553 | 0.11444 | -122.2092 | 0.086975 | 0.16022 | 0.15106 | -122.3053 | 0.073242 | 0.073242 | 0.19684 | -122.3053
3651.0469 | 122.4518 | -0.059509 | 122.2504 | 0.08667 | 0.0457 | 0.061823 | -0.00065795 | 0.03061 | 0.00017302 | 0.032142 | 0.052185 | 0.029828 | 0.03795 | 0.049456 | 0.0025271 | 0.026504 | 0.009155 | -0.018311 | -0.027466 | -0.004578 | 0.082397 | 0.018311 | -0.11444 | 0.068665 | 0.018311 | -0.091553 | 0.064087 | 0.032043 | -0.054932 | -0.091553 | 0.07782 | -0.054932 | -122.168 | 0.041198 | 0.054931 | 0.10986 | -122.2412 | 0.004577 | -0.032044 | -122.1863 | 0.12817 | -0.032044 | 0 | -122.2183 | 0.14191 | 0.068664 | 0.032043 | -122.3648 | 0.1236 | 0.091552 | 0.07782 | -122.3419
3652.8125 | 122.4884 | -0.045776 | 122.2458 | -0.0354 | 0.042282 | 0.060327 | 0.0042555 | 0.032319 | -0.0085856 | 0.029792 | -0.024109 | 0.025769 | 0.034746 | 0.04732 | -0.00024989 | 0.028854 | 0.022888 | 0.082397 | 0.064087 | 0.041199 | 0.073242 | 0.054932 | -0.10529 | 0.12817 | 0.14191 | 0.032043 | 0.022888 | 0.013733 | -0.022888 | -0.07782 | 0.10071 | -0.05951 | -122.1725 | 0.12817 | 0.086975 | 0.14649 | -122.2229 | 0.022888 | -0.032044 | -122.2229 | 0.17395 | 0.077819 | 0.10986 | -122.2321 | 0.11902 | 0.068664 | 0.10986 | -122.3511 | 0.068664 | 0.059509 | 0.18768 | -122.3236
3654.5781 | 122.3511 | -0.09613 | 122.2824 | -0.081177 | 0.046341 | 0.060541 | 0.00062385 | 0.028688 | 0.0020956 | 0.031928 | -0.092773 | 0.030469 | 0.036241 | 0.051165 | 0.0035953 | 0.026504 | 0.050354 | 0.050354 | 0.018311 | 0.022888 | 0.091553 | 0.018311 | -0.10986 | 0.07782 | 0.041199 | -0.082397 | 0.054932 | 0.036621 | -0.045776 | -0.09613 | 0.11444 | -0.013733 | -122.1909 | 0.14648 | 0.11902 | 0.13275 | -122.2321 | 0.050354 | 0 | -122.2275 | 0.17395 | 0.013733 | 0.013733 | -122.2458 | 0.18768 | 0.14648 | 0.11444 | -122.3923 | 0.15106 | 0.13275 | 0.13733 | -122.3785
3656.2812 | 122.4289 | -0.059509 | 122.2687 | 0.063782 | 0.047409 | 0.06225 | 0.0025465 | 0.03296 | -0.006663 | 0.029151 | 0.159 | 0.02641 | 0.038377 | 0.04732 | 0.00017731 | 0.028213 | 0.082397 | 0.11902 | 0.11902 | 0.045776 | 0.045776 | 0.050354 | -0.091553 | 0.13275 | 0.11902 | 0.013733 | 0.009155 | 0.022888 | -0.027466 | -0.059509 | 0.10986 | -0.032044 | -122.2229 | 0.17853 | 0.10528 | 0.13733 | -122.1863 | 0.032043 | 0 | -122.2595 | 0.19226 | 0.073242 | 0.073242 | -122.2458 | 0.10528 | 0.14191 | 0.17853 | -122.3602 | 0.068664 | 0.082397 | 0.17853 | -122.3282
3658.0469 | 122.5067 | -0.059509 | 122.2412 | -0.065918 | 0.04271 | 0.063104 | 0.0040417 | 0.028047 | -0.0087992 | 0.029151 | -0.077515 | 0.025769 | 0.035387 | 0.049883 | -0.0025999 | 0.026291 | 0.059509 | 0.086975 | 0.091553 | 0.073242 | 0.064087 | 0.045776 | -0.09613 | 0.15106 | 0.15564 | 0.064087 | 0.022888 | 0.013733 | -0.013733 | -0.041199 | 0.10528 | -0.036621 | -122.1771 | 0.14648 | 0.13275 | 0.16937 | -122.1817 | 0.045776 | 0.01831 | -122.2183 | 0.21057 | 0.1236 | 0.10529 | -122.2275 | 0.1236 | 0.11902 | 0.15106 | -122.3373 | 0.082397 | 0.073242 | 0.21515 | -122.2824
3659.75 | 122.4472 | -0.045776 | 122.2412 | 0.010376 | 0.043137 | 0.061609 | 0.0038281 | 0.029756 | -0.006022 | 0.02616 | 0.044556 | 0.026624 | 0.036455 | 0.047961 | -0.00024989 | 0.026077 | 0.027466 | 0.064087 | 0.064087 | 0.032043 | 0.054932 | 0.054932 | -0.11902 | 0.091553 | 0.082397 | -0.004578 | 0.036621 | 0.018311 | -0.027466 | -0.068665 | 0.10071 | -0.073243 | -122.1863 | 0.10986 | 0.077819 | 0.15106 | -122.2137 | 0.01831 | -0.022889 | -122.2046 | 0.13733 | 0.041198 | 0.064087 | -122.2229 | 0.10071 | 0.073242 | 0.10986 | -122.3602 | 0.082397 | 0.064087 | 0.12817 | -122.3099
3661.5156 | 122.4609 | -0.041199 | 122.2275 | 0.10193 | 0.042923 | 0.061609 | 0.00041005 | 0.029542 | -0.0011088 | 0.031714 | 0.12085 | 0.027906 | 0.033891 | 0.046679 | 0.0038089 | 0.027359 | 0.10986 | 0.10071 | 0.073242 | 0.073242 | 0.054932 | 0.064087 | -0.10071 | 0.15564 | 0.1236 | 0.022888 | 0.013733 | -0.013733 | -0.009155 | -0.064087 | 0.10529 | -0.059509 | -122.1725 | 0.14191 | 0.11444 | 0.17395 | -122.1176 | 0.032044 | -0.022888 | -122.2137 | 0.19684 | 0.064087 | 0.086975 | -122.2412 | 0.096131 | 0.15106 | 0.11444 | -122.3282 | 0.054932 | 0.027466 | 0.16479 | -122.2916
3663.2812 | 122.3557 | -0.10529 | 122.2916 | -0.23376 | 0.047409 | 0.061182 | 0.0063917 | 0.027619 | -0.004954 | 0.028083 | -0.18433 | 0.028333 | 0.036882 | 0.049883 | -0.00067729 | 0.027145 | 0.009155 | 0.045776 | 0.013733 | 0 | 0.082397 | 0.009155 | -0.13733 | 0.036621 | 0.036621 | -0.068665 | 0.07782 | 0.041199 | -0.045776 | -0.10529 | 0.11444 | -0.032043 | -122.2092 | 0.15106 | 0.10529 | 0.13733 | -122.2824 | 0.05951 | 0 | -122.2137 | 0.14191 | 0.036621 | 0.036621 | -122.2504 | 0.18768 | 0.11444 | 0.11902 | -122.4289 | 0.18311 | 0.14649 | 0.14191 | -122.3969
3665.0469 | 122.3831 | -0.07782 | 122.2549 | 0.079041 | 0.046128 | 0.060541 | 0.0012647 | 0.029115 | 0.00081382 | 0.031287 | 0.036926 | 0.026837 | 0.036241 | 0.049883 | 0.0048769 | 0.026291 | -0.004578 | -0.022888 | -0.036621 | -0.013733 | 0.086975 | 0.018311 | -0.14648 | 0.054932 | -0.009155 | -0.10986 | 0.050354 | 0.050354 | -0.036621 | -0.10071 | 0.096131 | -0.068664 | -122.168 | 0.054932 | 0.064087 | 0.13275 | -122.2595 | 0.041199 | -0.022888 | -122.2046 | 0.13275 | -0.032043 | -0.009155 | -122.2046 | 0.16479 | 0.073242 | 0.041199 | -122.4014 | 0.12817 | 0.12817 | 0.068665 | -122.3557
3666.8125 | 122.3648 | -0.11444 | 122.2916 | -0.19562 | 0.04805 | 0.063532 | 0.0061781 | 0.029756 | -0.004954 | 0.030219 | -0.25299 | 0.030042 | 0.037523 | 0.051592 | -0.00067729 | 0.027145 | -0.027466 | 0.022888 | -0.018311 | -0.013733 | 0.086975 | 0 | -0.13275 | 0.022888 | 0.045776 | -0.073242 | 0.073242 | 0.050354 | -0.064087 | -0.10986 | 0.11444 | -0.01831 | -122.2046 | 0.13733 | 0.10071 | 0.11902 | -122.319 | 0.050354 | 0.004578 | -122.2183 | 0.13733 | 0.041199 | 0.036621 | -122.2412 | 0.20142 | 0.086975 | 0.09613 | -122.4243 | 0.18768 | 0.16479 | 0.16022 | -122.4014
3668.5156 | 122.4747 | -0.054932 | 122.2321 | -0.012512 | 0.039933 | 0.064172 | 0.00083745 | 0.030397 | -0.0085856 | 0.030646 | 0.021668 | 0.025342 | 0.034532 | 0.048388 | -3.629e-05 | 0.03099 | 0.009155 | 0.07782 | 0.050354 | 0.036621 | 0.068665 | 0.041199 | -0.10529 | 0.10071 | 0.10071 | 0.009155 | 0.027466 | 0.032043 | -0.027466 | -0.059509 | 0.096131 | -0.050354 | -122.1634 | 0.13275 | 0.091553 | 0.14191 | -122.2229 | 0.027466 | -0.004577 | -122.2046 | 0.15564 | 0.064087 | 0.068664 | -122.2 | 0.1236 | 0.064087 | 0.10529 | -122.3373 | 0.082398 | 0.086975 | 0.15564 | -122.2916
3670.2812 | 122.3969 | -0.10071 | 122.2733 | -0.12695 | 0.04805 | 0.058191 | 0.0070325 | 0.031892 | -0.00089518 | 0.030433 | -0.20721 | 0.029828 | 0.038805 | 0.053301 | 0.0012455 | 0.026291 | 0.059509 | 0.013733 | 0.013733 | 0.027466 | 0.10071 | 0.009155 | -0.11902 | 0.07782 | 0.07782 | -0.050354 | 0.059509 | 0.032043 | -0.036621 | -0.10986 | 0.10986 | -0.018311 | -122.1725 | 0.11444 | 0.12817 | 0.14649 | -122.2137 | 0.064087 | -0.009155 | -122.2137 | 0.17853 | 0.050354 | 0.059509 | -122.2412 | 0.20142 | 0.16022 | 0.11444 | -122.3923 | 0.16022 | 0.13275 | 0.17853 | -122.3831
3672.0312 | 122.4014 | -0.086975 | 122.2687 | -0.20325 | 0.049759 | 0.062036 | 0.0055371 | 0.031678 | -0.001536 | 0.030646 | -0.1767 | 0.030683 | 0.037523 | 0.050524 | 0.0012455 | 0.026931 | 0.041199 | 0.013733 | 0.004578 | 0.032043 | 0.09613 | 0.018311 | -0.13733 | 0.07782 | 0.07782 | -0.059509 | 0.045776 | 0.050354 | -0.041199 | -0.091553 | 0.10529 | -0.050354 | -122.1725 | 0.10071 | 0.11902 | 0.16937 | -122.2275 | 0.045776 | -0.004578 | -122.2229 | 0.16479 | 0.027466 | 0.032044 | -122.2183 | 0.1831 | 0.12817 | 0.091553 | -122.406 | 0.13275 | 0.13733 | 0.16479 | -122.3602
3673.7969 | 122.3923 | -0.068665 | 122.2687 | 0.094299 | 0.046982 | 0.060114 | 0.0019055 | 0.029115 | -4.058e-05 | 0.032142 | 0.082703 | 0.030255 | 0.036668 | 0.051806 | -0.00067729 | 0.026504 | 0.013733 | -0.027466 | -0.036621 | -0.004578 | 0.09613 | 0.009155 | -0.1236 | 0.036621 | -0.004578 | -0.10986 | 0.073242 | 0.041199 | -0.045776 | -0.09613 | 0.07782 | -0.054931 | -122.1725 | 0.041199 | 0.064087 | 0.11902 | -122.2549 | 0.022889 | -0.027465 | -122.1954 | 0.10529 | -0.041198 | -0.013733 | -122.2275 | 0.16479 | 0.082398 | 0.032044 | -122.3923 | 0.14191 | 0.10986 | 0.064087 | -122.3648
3675.5625 | 122.4289 | -0.050354 | 122.2412 | 0.12482 | 0.048477 | 0.060968 | 0.0036145 | 0.031037 | -0.0073038 | 0.031074 | 0.13611 | 0.025556 | 0.035814 | 0.049456 | -0.00067729 | 0.029068 | 0.086975 | 0.10986 | 0.10986 | 0.059509 | 0.027466 | 0.064087 | -0.082397 | 0.15106 | 0.14191 | 0.045776 | 0.004578 | 0.009155 | -0.004578 | -0.059509 | 0.11444 | -0.032043 | -122.2137 | 0.16022 | 0.10986 | 0.14191 | -122.1542 | 0.045776 | -0.009155 | -122.2366 | 0.20142 | 0.09613 | 0.10528 | -122.2321 | 0.07782 | 0.13733 | 0.16022 | -122.3236 | 0.054932 | 0.059509 | 0.19226 | -122.3007
3677.3281 | 122.4838 | -0.054932 | 122.2321 | -0.020142 | 0.043991 | 0.061182 | 0.0044691 | 0.02826 | -0.0096536 | 0.029151 | 0.052185 | 0.026197 | 0.036668 | 0.048388 | -0.0015317 | 0.029922 | 0.018311 | 0.064087 | 0.050354 | 0.036621 | 0.050354 | 0.054932 | -0.10071 | 0.09613 | 0.11444 | 0.027466 | 0.027466 | 0.027466 | -0.041199 | -0.068665 | 0.10986 | -0.045776 | -122.1817 | 0.11902 | 0.091553 | 0.13733 | -122.2137 | 0.013733 | -0.013733 | -122.2046 | 0.15106 | 0.082398 | 0.096131 | -122.2046 | 0.10529 | 0.073243 | 0.10529 | -122.3328 | 0.082398 | 0.082398 | 0.16937 | -122.3007
3679.0312 | 122.4747 | -0.050354 | 122.2458 | 0.094299 | 0.047409 | 0.059259 | 0.0019055 | 0.030183 | -0.0011088 | 0.031074 | 0.13611 | 0.029187 | 0.035173 | 0.052019 | 0.0029543 | 0.024795 | 0.036621 | 0.004578 | -0.009155 | 0 | 0.10529 | 0.027466 | -0.1236 | 0.086975 | 0.054932 | -0.036621 | 0.036621 | 0.022888 | -0.027466 | -0.086975 | 0.07782 | -0.073242 | -122.1405 | 0.054932 | 0.050354 | 0.1236 | -122.2092 | 0.022888 | -0.036621 | -122.2092 | 0.13733 | 0.013733 | 0.050354 | -122.2229 | 0.15564 | 0.086975 | 0.041199 | -122.3694 | 0.086975 | 0.073242 | 0.10529 | -122.3328
3680.7969 | 122.4014 | -0.082397 | 122.2916 | 0.10193 | 0.04805 | 0.059259 | 0.00041005 | 0.029756 | -0.0017496 | 0.032142 | 0.059815 | 0.029615 | 0.036455 | 0.047747 | 0.0038089 | 0.026718 | 0.009155 | -0.022888 | -0.032043 | -0.022888 | 0.086975 | 0.022888 | -0.11444 | 0.036621 | 0.009155 | -0.082397 | 0.050354 | 0.032043 | -0.045776 | -0.11444 | 0.10528 | -0.032044 | -122.2046 | 0.059509 | 0.059509 | 0.091553 | -122.2824 | 0.036621 | -0.032044 | -122.2412 | 0.11902 | 0 | 0.032044 | -122.2595 | 0.16937 | 0.091552 | 0.050354 | -122.406 | 0.13275 | 0.11444 | 0.091552 | -122.406
3682.5 | 122.4792 | -0.045776 | 122.2229 | -0.012512 | 0.044205 | 0.061609 | 0.0059643 | 0.032533 | -0.0090128 | 0.029365 | 0.052185 | 0.026837 | 0.036668 | 0.047961 | -0.0023861 | 0.028854 | 0.009155 | 0.054932 | 0.068665 | 0.032043 | 0.059509 | 0.041199 | -0.09613 | 0.091553 | 0.11444 | 0.013733 | 0.045776 | 0.032043 | -0.009155 | -0.09613 | 0.086975 | -0.050354 | -122.1634 | 0.10071 | 0.077819 | 0.12817 | -122.2137 | 0.036621 | -0.050354 | -122.1771 | 0.13733 | 0.059509 | 0.10986 | -122.1909 | 0.10528 | 0.054931 | 0.11444 | -122.319 | 0.091552 | 0.077819 | 0.16022 | -122.319
3684.2656 | 122.3648 | -0.091553 | 122.2824 | -0.081177 | 0.047409 | 0.060114 | 0.0019055 | 0.030183 | 0.0010276 | 0.030646 | -0.13855 | 0.030469 | 0.035814 | 0.049242 | 0.0033817 | 0.025863 | 0.086975 | 0.027466 | 0.032043 | 0.022888 | 0.073242 | 0.022888 | -0.10986 | 0.10529 | 0.073242 | -0.064087 | 0.059509 | 0.045776 | -0.036621 | -0.082397 | 0.11444 | -0.01831 | -122.2092 | 0.11902 | 0.11444 | 0.13275 | -122.1954 | 0.054932 | 0.009156 | -122.2229 | 0.19684 | 0.027466 | 0.01831 | -122.2366 | 0.16479 | 0.17853 | 0.1236 | -122.3923 | 0.15106 | 0.13733 | 0.16479 | -122.3648
3686.0156 | 122.374 | -0.09613 | 122.2824 | -0.11169 | 0.049546 | 0.059473 | 0.0046827 | 0.03296 | 0.0012412 | 0.032142 | -0.12329 | 0.029401 | 0.037523 | 0.051378 | 0.0025271 | 0.026077 | 0.054932 | 0.045776 | 0.027466 | 0.032043 | 0.086975 | 0.032043 | -0.13275 | 0.091553 | 0.091553 | -0.054932 | 0.041199 | 0.041199 | -0.045776 | -0.10529 | 0.12817 | -0.036621 | -122.1954 | 0.14191 | 0.12817 | 0.16479 | -122.2275 | 0.050354 | -0.009156 | -122.2412 | 0.18768 | 0.041198 | 0.050354 | -122.2412 | 0.1831 | 0.15106 | 0.1236 | -122.4152 | 0.13733 | 0.13733 | 0.18768 | -122.3877
3687.7656 | 122.3282 | -0.091553 | 122.2733 | -0.096436 | 0.049546 | 0.058191 | 0.0010511 | 0.029115 | 0.001882 | 0.031074 | -0.12329 | 0.029828 | 0.036668 | 0.050738 | 0.0018863 | 0.027145 | 0.068665 | 0.054932 | 0.022888 | 0.027466 | 0.082397 | 0.032043 | -0.11444 | 0.07782 | 0.07782 | -0.059509 | 0.036621 | 0.041199 | -0.032043 | -0.10071 | 0.1236 | -0.022888 | -122.1909 | 0.14649 | 0.11902 | 0.14191 | -122.2046 | 0.05951 | -0.009155 | -122.2366 | 0.16937 | 0.032044 | 0.041199 | -122.2321 | 0.17395 | 0.16022 | 0.11444 | -122.3877 | 0.12817 | 0.13275 | 0.16937 | -122.374
3689.4688 | 122.4884 | -0.050354 | 122.2229 | -0.027771 | 0.043778 | 0.06225 | 0.0038281 | 0.031678 | -0.010935 | 0.029578 | 0.029297 | 0.027051 | 0.038805 | 0.047747 | -0.0021725 | 0.029281 | 0.004578 | 0.059509 | 0.073242 | 0.032043 | 0.045776 | 0.050354 | -0.10529 | 0.11902 | 0.11902 | 0.036621 | 0.027466 | 0.013733 | -0.027466 | -0.07782 | 0.10071 | -0.054932 | -122.1771 | 0.10986 | 0.082397 | 0.13733 | -122.2183 | 0.022888 | -0.027466 | -122.1954 | 0.16937 | 0.086975 | 0.11444 | -122.2092 | 0.09613 | 0.054932 | 0.1236 | -122.3282 | 0.07782 | 0.064087 | 0.16937 | -122.3007
3691.2344 | 122.4701 | -0.032043 | 122.2412 | -0.1651 | 0.044632 | 0.060114 | 0.0066053 | 0.032105 | -0.0098672 | 0.03086 | -0.039368 | 0.027692 | 0.038377 | 0.049029 | -0.0032407 | 0.027145 | 0.082397 | 0.12817 | 0.10986 | 0.064087 | 0.045776 | 0.050354 | -0.07782 | 0.16937 | 0.17853 | 0.09613 | 0.027466 | 0.009155 | -0.004578 | -0.073242 | 0.082397 | -0.045777 | -122.1954 | 0.16022 | 0.09613 | 0.14191 | -122.1588 | 0.027465 | -0.041199 | -122.2137 | 0.20142 | 0.12817 | 0.16937 | -122.2321 | 0.077819 | 0.11444 | 0.14191 | -122.319 | 0.059509 | 0.041198 | 0.21057 | -122.3145
3693 | 122.4197 | -0.068665 | 122.2687 | -0.15747 | 0.049118 | 0.0599 | 0.0025465 | 0.027833 | -0.006663 | 0.030646 | -0.16907 | 0.027051 | 0.034532 | 0.048601 | -0.0023861 | 0.024795 | 0.09613 | 0.13275 | 0.11902 | 0.073242 | 0.054932 | 0.059509 | -0.09613 | 0.14648 | 0.17853 | 0.064087 | 0.013733 | 0.013733 | -0.009155 | -0.068665 | 0.12817 | -0.027465 | -122.2137 | 0.20142 | 0.14191 | 0.16937 | -122.1725 | 0.05951 | 0 | -122.2549 | 0.21515 | 0.13275 | 0.13275 | -122.2549 | 0.1236 | 0.16479 | 0.18768 | -122.3648 | 0.082398 | 0.082398 | 0.24719 | -122.3373
3694.7812 | 122.3831 | -0.082397 | 122.2733 | 0.063782 | 0.047623 | 0.060541 | -0.00023075 | 0.027406 | 0.0016684 | 0.029151 | 0.0064086 | 0.029615 | 0.03795 | 0.050738 | 0.0042361 | 0.025436 | 0.013733 | -0.045776 | -0.045776 | -0.009155 | 0.07782 | 0.013733 | -0.11444 | 0.041199 | -0.009155 | -0.11902 | 0.068665 | 0.036621 | -0.041199 | -0.1236 | 0.09613 | -0.032044 | -122.1954 | 0.036621 | 0.073242 | 0.10529 | -122.2595 | 0.041198 | -0.041199 | -122.2046 | 0.1236 | -0.036622 | 0.004577 | -122.2366 | 0.16022 | 0.09613 | 0.036621 | -122.3877 | 0.15106 | 0.11902 | 0.073242 | -122.3969
3696.5625 | 122.4701 | -0.041199 | 122.2458 | -0.081177 | 0.042923 | 0.062463 | 0.0016919 | 0.028688 | -0.0096536 | 0.03086 | -0.069885 | 0.025556 | 0.036668 | 0.047747 | -0.0013181 | 0.027572 | 0.073242 | 0.10071 | 0.09613 | 0.045776 | 0.054932 | 0.050354 | -0.091553 | 0.15106 | 0.16479 | 0.068665 | 0.027466 | 0.018311 | -0.004578 | -0.054932 | 0.091553 | -0.050354 | -122.1909 | 0.14191 | 0.086975 | 0.13733 | -122.1725 | 0.036621 | -0.013733 | -122.2183 | 0.19226 | 0.10986 | 0.1236 | -122.2275 | 0.096131 | 0.11444 | 0.13733 | -122.3373 | 0.068665 | 0.05951 | 0.20599 | -122.3007
3698.25 | 122.3373 | -0.10529 | 122.2687 | -0.058289 | 0.048264 | 0.057977 | 0.0016919 | 0.031251 | 0.0031638 | 0.028724 | -0.11566 | 0.02876 | 0.035814 | 0.050097 | 0.0012455 | 0.025436 | 0.082397 | 0.041199 | 0.009155 | 0.022888 | 0.07782 | 0.032043 | -0.1236 | 0.073242 | 0.059509 | -0.064087 | 0.064087 | 0.045776 | -0.045776 | -0.082397 | 0.13733 | -0.01831 | -122.1909 | 0.14649 | 0.12817 | 0.14648 | -122.1863 | 0.05951 | 0.022889 | -122.2046 | 0.17853 | 0.041199 | 0.01831 | -122.2229 | 0.18311 | 0.18768 | 0.11444 | -122.3923 | 0.16937 | 0.15106 | 0.16479 | -122.3511
3699.9375 | 122.4838 | -0.018311 | 122.2321 | -0.027771 | 0.044419 | 0.061609 | 0.0014783 | 0.032105 | -0.0092264 | 0.03086 | -0.0088499 | 0.026837 | 0.034959 | 0.047106 | -0.0013181 | 0.028213 | 0.018311 | 0.082397 | 0.068665 | 0.036621 | 0.054932 | 0.045776 | -0.091553 | 0.10986 | 0.10986 | 0.022888 | 0.032043 | 0.022888 | 0 | -0.073242 | 0.064087 | -0.073242 | -122.1771 | 0.10071 | 0.054932 | 0.12817 | -122.2137 | 0.018311 | -0.054931 | -122.2 | 0.12817 | 0.041199 | 0.09613 | -122.2092 | 0.073243 | 0.036622 | 0.086976 | -122.3236 | 0.050354 | 0.041199 | 0.12817 | -122.3053
3701.7188 | 122.4609 | -0.059509 | 122.2504 | -0.020142 | 0.042923 | 0.063959 | 0.0053235 | 0.02826 | -0.0053812 | 0.029151 | 0.021668 | 0.026837 | 0.036668 | 0.050524 | -0.0015317 | 0.027145 | 0.041199 | 0.041199 | 0.054932 | 0.032043 | 0.054932 | 0.045776 | -0.10071 | 0.09613 | 0.09613 | 0.018311 | 0.041199 | 0.022888 | -0.018311 | -0.064087 | 0.10528 | -0.041199 | -122.1954 | 0.10071 | 0.091552 | 0.13275 | -122.2092 | 0.041198 | -0.004578 | -122.2092 | 0.15564 | 0.07782 | 0.082398 | -122.2275 | 0.11444 | 0.10071 | 0.11444 | -122.3511 | 0.10071 | 0.082397 | 0.15564 | -122.3145
3703.4844 | 122.4792 | -0.059509 | 122.2504 | 0.14771 | 0.046128 | 0.057977 | 0.0038281 | 0.033387 | -0.0011088 | 0.03086 | 0.11322 | 0.029187 | 0.0356 | 0.050097 | 0.00039091 | 0.025863 | 0.10529 | 0.07782 | 0.068665 | 0.068665 | 0.059509 | 0.054932 | -0.10071 | 0.14648 | 0.10071 | 0.013733 | 0.018311 | -0.004578 | -0.013733 | -0.045776 | 0.11444 | -0.041199 | -122.1909 | 0.13733 | 0.12817 | 0.16937 | -122.1451 | 0.045776 | 0.013733 | -122.2321 | 0.20599 | 0.073242 | 0.059509 | -122.2549 | 0.11902 | 0.16479 | 0.12817 | -122.3511 | 0.07782 | 0.054931 | 0.16022 | -122.2961
3705.25 | 122.4792 | -0.032043 | 122.2504 | 0.071411 | 0.043351 | 0.058618 | 0.0014783 | 0.031251 | -0.0019632 | 0.030006 | 0.090332 | 0.027906 | 0.034959 | 0.049029 | 0.0023135 | 0.027145 | 0.091553 | 0.10529 | 0.073242 | 0.068665 | 0.059509 | 0.050354 | -0.09613 | 0.16479 | 0.13275 | 0.009155 | 0.018311 | 0.009155 | -0.009155 | -0.068665 | 0.082397 | -0.064087 | -122.1909 | 0.13733 | 0.10071 | 0.16479 | -122.1588 | 0.022888 | -0.036622 | -122.2321 | 0.19684 | 0.041198 | 0.07782 | -122.2412 | 0.091552 | 0.1236 | 0.10529 | -122.3465 | 0.050354 | 0.041198 | 0.16479 | -122.319
3706.9531 | 122.4747 | -0.045776 | 122.2412 | -0.096436 | 0.044632 | 0.062891 | 0.0027601 | 0.031678 | -0.0062356 | 0.029792 | -0.077515 | 0.025983 | 0.036027 | 0.048601 | -0.0017453 | 0.029708 | 0.10071 | 0.13733 | 0.09613 | 0.068665 | 0.059509 | 0.041199 | -0.091553 | 0.15106 | 0.16022 | 0.054932 | 0.027466 | 0.004578 | -0.018311 | -0.064087 | 0.086975 | -0.045777 | -122.1817 | 0.18311 | 0.11444 | 0.16022 | -122.1405 | 0.027465 | -0.018311 | -122.2137 | 0.19684 | 0.10071 | 0.11902 | -122.2366 | 0.10528 | 0.14648 | 0.14191 | -122.3328 | 0.073242 | 0.050354 | 0.20599 | -122.3053
3708.7188 | 122.3511 | -0.10071 | 122.2824 | -0.23376 | 0.045487 | 0.060327 | 0.0034009 | 0.030824 | -0.001536 | 0.030219 | -0.26062 | 0.02876 | 0.034959 | 0.049456 | -0.00067729 | 0.025863 | 0.027466 | 0.018311 | 0.013733 | 0.009155 | 0.07782 | 0.018311 | -0.1236 | 0.032043 | 0.050354 | -0.068665 | 0.054932 | 0.050354 | -0.059509 | -0.11902 | 0.11902 | -0.022888 | -122.2046 | 0.11902 | 0.10986 | 0.13275 | -122.2549 | 0.041199 | -0.018311 | -122.2275 | 0.13275 | 0.032043 | 0.050354 | -122.2321 | 0.17853 | 0.12817 | 0.11444 | -122.406 | 0.15564 | 0.15106 | 0.15106 | -122.4014
3710.4844 | 122.3328 | -0.10071 | 122.287 | -0.096436 | 0.047196 | 0.062036 | 0.0023329 | 0.03061 | 0.0023092 | 0.031074 | -0.14618 | 0.030042 | 0.036882 | 0.049242 | 0.0025271 | 0.025009 | 0.09613 | 0.050354 | 0.018311 | 0.036621 | 0.07782 | 0.022888 | -0.1236 | 0.091553 | 0.068665 | -0.059509 | 0.050354 | 0.036621 | -0.036621 | -0.09613 | 0.1236 | -0.022888 | -122.2092 | 0.15106 | 0.13733 | 0.16022 | -122.1909 | 0.064087 | 0.004578 | -122.2366 | 0.19226 | 0.041199 | 0.036621 | -122.2504 | 0.17853 | 0.19684 | 0.11902 | -122.4106 | 0.15106 | 0.13733 | 0.16937 | -122.3831
3712.25 | 122.3923 | -0.07782 | 122.2687 | -0.20325 | 0.045487 | 0.060541 | 0.0038281 | 0.031037 | -0.006663 | 0.031928 | -0.13855 | 0.024274 | 0.035814 | 0.046892 | -0.00067729 | 0.028854 | 0.073242 | 0.15564 | 0.11444 | 0.082397 | 0.032043 | 0.045776 | -0.10529 | 0.12817 | 0.17395 | 0.027466 | 0.018311 | 0.018311 | -0.018311 | -0.082397 | 0.1236 | -0.027466 | -122.2366 | 0.23346 | 0.16022 | 0.18768 | -122.1954 | 0.059509 | -0.004577 | -122.2504 | 0.20599 | 0.10529 | 0.10986 | -122.2504 | 0.10986 | 0.15106 | 0.19226 | -122.374 | 0.096131 | 0.096131 | 0.25177 | -122.3511
3713.9531 | 122.4655 | -0.064087 | 122.2321 | 0.08667 | 0.048477 | 0.0599 | -1.7146e-05 | 0.031465 | -0.00025418 | 0.03086 | 0.067444 | 0.028974 | 0.036455 | 0.049242 | 0.0014591 | 0.025436 | 0.009155 | -0.009155 | -0.032043 | -0.013733 | 0.09613 | 0.027466 | -0.1236 | 0.064087 | 0.027466 | -0.068665 | 0.054932 | 0.050354 | -0.045776 | -0.09613 | 0.091553 | -0.059509 | -122.1359 | 0.054932 | 0.050354 | 0.10986 | -122.2229 | 0.018311 | -0.032043 | -122.1771 | 0.12817 | -0.004578 | 0.027465 | -122.1817 | 0.16022 | 0.073242 | 0.032044 | -122.3557 | 0.11902 | 0.11444 | 0.091553 | -122.3282
3715.7188 | 122.4655 | -0.045776 | 122.2321 | -0.088806 | 0.045487 | 0.062036 | 0.0055371 | 0.030183 | -0.0090128 | 0.028724 | -0.077515 | 0.026197 | 0.035387 | 0.047106 | -0.0015317 | 0.030349 | 0.07782 | 0.14648 | 0.1236 | 0.068665 | 0.054932 | 0.045776 | -0.10071 | 0.16479 | 0.18768 | 0.068665 | 0.013733 | 0.004578 | -0.004578 | -0.059509 | 0.091552 | -0.054932 | -122.1771 | 0.19226 | 0.11444 | 0.16937 | -122.1542 | 0.041198 | -0.013733 | -122.2183 | 0.21057 | 0.11444 | 0.12817 | -122.2275 | 0.10071 | 0.1236 | 0.16937 | -122.3328 | 0.059509 | 0.050354 | 0.23346 | -122.2916
3717.4219 | 122.3419 | -0.11902 | 122.287 | -0.21851 | 0.044846 | 0.062036 | 0.0063917 | 0.028688 | -0.0040994 | 0.027869 | -0.12329 | 0.027051 | 0.039232 | 0.048601 | -0.0015317 | 0.025009 | 0.027466 | 0.022888 | 0.013733 | 0.004578 | 0.073242 | 0.013733 | -0.11902 | 0.041199 | 0.041199 | -0.073242 | 0.064087 | 0.054932 | -0.041199 | -0.10986 | 0.13275 | 0 | -122.2137 | 0.14191 | 0.1236 | 0.1236 | -122.2595 | 0.07782 | 0.009156 | -122.2229 | 0.16022 | 0.045777 | 0.036621 | -122.2321 | 0.19226 | 0.14649 | 0.13275 | -122.406 | 0.18311 | 0.17395 | 0.16022 | -122.3969
3719.1875 | 122.4976 | -0.036621 | 122.2275 | -0.04303 | 0.043351 | 0.0599 | 0.0059643 | 0.031037 | -0.0070902 | 0.027869 | -0.046997 | 0.027478 | 0.033464 | 0.049669 | -0.0019589 | 0.027786 | 0.054932 | 0.068665 | 0.086975 | 0.054932 | 0.054932 | 0.054932 | -0.086975 | 0.13275 | 0.13275 | 0.045776 | 0.027466 | 0.022888 | -0.004578 | -0.068665 | 0.091553 | -0.050354 | -122.1725 | 0.10529 | 0.091553 | 0.14191 | -122.1725 | 0.032043 | -0.032044 | -122.2 | 0.16937 | 0.082397 | 0.11444 | -122.2046 | 0.091553 | 0.091553 | 0.1236 | -122.3145 | 0.064087 | 0.059509 | 0.16937 | -122.2961
3720.9531 | 122.4243 | -0.064087 | 122.2366 | 0.08667 | 0.04271 | 0.06225 | 0.0036145 | 0.028474 | -0.0036722 | 0.029365 | 0.11322 | 0.027692 | 0.036668 | 0.049029 | 0.00017731 | 0.027359 | 0.091553 | 0.10529 | 0.091553 | 0.054932 | 0.050354 | 0.050354 | -0.082397 | 0.13275 | 0.11444 | 0 | 0.032043 | 0.022888 | -0.013733 | -0.07782 | 0.11444 | -0.01831 | -122.1863 | 0.16937 | 0.11902 | 0.13733 | -122.1451 | 0.050354 | -0.013733 | -122.2046 | 0.19684 | 0.064087 | 0.07782 | -122.2137 | 0.11444 | 0.15564 | 0.15564 | -122.319 | 0.09613 | 0.086975 | 0.17853 | -122.3145
3722.6562 | 122.3877 | -0.068665 | 122.2687 | -0.19562 | 0.046555 | 0.061823 | 0.0025465 | 0.029328 | -0.0011088 | 0.031287 | -0.25299 | 0.027478 | 0.037309 | 0.048388 | 0.0029543 | 0.024582 | 0.018311 | -0.004578 | -0.013733 | 0 | 0.10071 | 0.018311 | -0.13733 | 0.041199 | 0.050354 | -0.091553 | 0.073242 | 0.050354 | -0.032043 | -0.11444 | 0.086976 | -0.068664 | -122.168 | 0.064087 | 0.068665 | 0.13733 | -122.2504 | 0.036622 | -0.045776 | -122.1954 | 0.10986 | -0.022888 | 0.022888 | -122.2183 | 0.16937 | 0.086976 | 0.054932 | -122.406 | 0.14191 | 0.11902 | 0.11902 | -122.3831
3724.4219 | 122.3877 | -0.082397 | 122.2504 | -0.18799 | 0.047409 | 0.0599 | 0.0010511 | 0.032105 | -0.00046778 | 0.030433 | -0.23773 | 0.028119 | 0.037096 | 0.049029 | 0.0020999 | 0.026504 | 0.022888 | 0.009155 | -0.018311 | 0.013733 | 0.086975 | 0.027466 | -0.14191 | 0.07782 | 0.073242 | -0.059509 | 0.054932 | 0.045776 | -0.050354 | -0.10071 | 0.10986 | -0.05951 | -122.1634 | 0.091552 | 0.09613 | 0.15564 | -122.2275 | 0.032043 | -0.018311 | -122.1954 | 0.16022 | 0.022888 | 0.041199 | -122.2046 | 0.16937 | 0.10528 | 0.064086 | -122.3923 | 0.13733 | 0.12817 | 0.15564 | -122.3511
3726.125 | 122.3465 | -0.10529 | 122.2778 | -0.15747 | 0.048905 | 0.061609 | 0.0051099 | 0.030824 | -0.004954 | 0.029578 | -0.21484 | 0.028333 | 0.036455 | 0.048815 | -0.0013181 | 0.027145 | -0.013733 | 0.009155 | 0 | -0.013733 | 0.091553 | 0.022888 | -0.13733 | 0.027466 | 0.050354 | -0.091553 | 0.064087 | 0.032043 | -0.050354 | -0.11444 | 0.12817 | -0.032043 | -122.1863 | 0.11444 | 0.091553 | 0.1236 | -122.2916 | 0.054932 | -0.009155 | -122.2137 | 0.13275 | 0.013733 | 0.022888 | -122.2458 | 0.19684 | 0.091553 | 0.10529 | -122.4152 | 0.16937 | 0.13733 | 0.15564 | -122.3923
3727.8906 | 122.406 | -0.091553 | 122.2778 | -0.19562 | 0.046128 | 0.061609 | 0.0027601 | 0.031251 | -0.00089518 | 0.032142 | -0.22247 | 0.027906 | 0.034959 | 0.048388 | -0.0017453 | 0.027572 | -0.009155 | 0 | -0.004578 | 0.009155 | 0.09613 | 0.018311 | -0.13275 | 0.022888 | 0.054932 | -0.07782 | 0.068665 | 0.045776 | -0.054932 | -0.09613 | 0.10986 | -0.041198 | -122.1817 | 0.091553 | 0.10071 | 0.14191 | -122.287 | 0.036621 | -0.004577 | -122.2092 | 0.11444 | 0.013733 | 0.01831 | -122.2321 | 0.18768 | 0.082398 | 0.086975 | -122.4106 | 0.16022 | 0.13733 | 0.14649 | -122.374
3729.6406 | 122.3419 | -0.10529 | 122.287 | -0.21851 | 0.048905 | 0.061609 | 0.0066053 | 0.031892 | -0.0053812 | 0.029578 | -0.19196 | 0.027906 | 0.037096 | 0.051378 | -0.0013181 | 0.027786 | -0.004578 | 0.027466 | 0.004578 | 0 | 0.09613 | 0.013733 | -0.12817 | 0.036621 | 0.059509 | -0.073242 | 0.064087 | 0.054932 | -0.050354 | -0.11444 | 0.11902 | -0.022888 | -122.1909 | 0.13275 | 0.10529 | 0.12817 | -122.2916 | 0.054932 | -0.009155 | -122.2229 | 0.14191 | 0.032044 | 0.041199 | -122.2321 | 0.20142 | 0.10071 | 0.10986 | -122.4152 | 0.16937 | 0.16022 | 0.16479 | -122.4014
3731.4062 | 122.3282 | -0.10529 | 122.287 | -0.065918 | 0.046341 | 0.059259 | 0.0025465 | 0.030824 | 0.00038662 | 0.031287 | -0.069885 | 0.028333 | 0.036668 | 0.049029 | 0.0046633 | 0.024368 | 0.064087 | 0.036621 | 0.009155 | 0.018311 | 0.086975 | 0.018311 | -0.13275 | 0.045776 | 0.054932 | -0.082397 | 0.059509 | 0.045776 | -0.036621 | -0.11902 | 0.1236 | -0.027465 | -122.2 | 0.14191 | 0.1236 | 0.15106 | -122.2229 | 0.068665 | -0.013733 | -122.2275 | 0.15106 | 0.022889 | 0.036622 | -122.2412 | 0.19226 | 0.16937 | 0.11444 | -122.4197 | 0.16479 | 0.15106 | 0.16022 | -122.406
3733.1094 | 122.4838 | -0.059509 | 122.2412 | -0.0354 | 0.044419 | 0.062463 | 0.0059643 | 0.030824 | -0.0090128 | 0.031501 | 0.029297 | 0.026624 | 0.03795 | 0.047106 | -0.0028135 | 0.030136 | 0.009155 | 0.064087 | 0.059509 | 0.045776 | 0.073242 | 0.041199 | -0.082397 | 0.091553 | 0.11902 | 0.041199 | 0.036621 | 0.009155 | -0.027466 | -0.064087 | 0.10071 | -0.022888 | -122.168 | 0.1236 | 0.10528 | 0.12817 | -122.2321 | 0.032043 | -0.004578 | -122.2046 | 0.15106 | 0.10071 | 0.10529 | -122.2321 | 0.13275 | 0.068664 | 0.11902 | -122.3236 | 0.09613 | 0.068664 | 0.17853 | -122.3053
3734.8906 | 122.3785 | -0.086975 | 122.2504 | 0.079041 | 0.047837 | 0.059473 | 0.00062385 | 0.030824 | 0.00081382 | 0.031714 | 0.075073 | 0.029187 | 0.034959 | 0.051165 | 0.0023135 | 0.02565 | 0.004578 | -0.036621 | -0.050354 | -0.018311 | 0.10071 | 0.004578 | -0.12817 | 0.045776 | -0.009155 | -0.10071 | 0.068665 | 0.045776 | -0.050354 | -0.11444 | 0.091553 | -0.041199 | -122.1497 | 0.050354 | 0.068664 | 0.10986 | -122.2458 | 0.036621 | -0.027466 | -122.1817 | 0.13275 | -0.013733 | 0.013733 | -122.2046 | 0.18768 | 0.091553 | 0.036621 | -122.3785 | 0.15564 | 0.13275 | 0.07782 | -122.3648
3736.6562 | 122.493 | -0.050354 | 122.2458 | -0.088806 | 0.044205 | 0.061395 | 0.0034009 | 0.027619 | -0.0090128 | 0.029365 | -0.077515 | 0.025769 | 0.035173 | 0.047533 | -0.0015317 | 0.027359 | 0.059509 | 0.13275 | 0.10071 | 0.068665 | 0.059509 | 0.054932 | -0.086975 | 0.1236 | 0.16937 | 0.073242 | 0.004578 | 0.004578 | -0.022888 | -0.082397 | 0.10529 | -0.036621 | -122.1863 | 0.18311 | 0.11902 | 0.15564 | -122.1863 | 0.027466 | -0.032043 | -122.2412 | 0.17395 | 0.1236 | 0.15564 | -122.2412 | 0.10986 | 0.10986 | 0.15106 | -122.3328 | 0.054932 | 0.054932 | 0.21973 | -122.3282
3738.4062 | 122.4472 | -0.050354 | 122.2412 | -0.13458 | 0.046555 | 0.059473 | 0.0042555 | 0.028474 | -0.006663 | 0.03086 | -0.12329 | 0.027051 | 0.037736 | 0.048815 | -0.0047361 | 0.025863 | 0.11902 | 0.16479 | 0.1236 | 0.082397 | 0.059509 | 0.032043 | -0.10071 | 0.14648 | 0.18768 | 0.054932 | 0.013733 | 0.009155 | -0.009155 | -0.064087 | 0.082397 | -0.050354 | -122.1817 | 0.21515 | 0.13275 | 0.18311 | -122.1222 | 0.041199 | -0.013733 | -122.2275 | 0.19684 | 0.10529 | 0.11902 | -122.2321 | 0.10986 | 0.16937 | 0.17395 | -122.3419 | 0.064087 | 0.059509 | 0.23804 | -122.3053
3740.1719 | 122.4335 | -0.059509 | 122.2321 | 0.10956 | 0.046982 | 0.057977 | -0.00023075 | 0.031892 | 0.00081382 | 0.031074 | 0.052185 | 0.029401 | 0.035173 | 0.05031 | 0.0029543 | 0.026718 | 0.032043 | -0.027466 | -0.022888 | -0.013733 | 0.10071 | 0.022888 | -0.13733 | 0.050354 | 0.009155 | -0.091553 | 0.068665 | 0.041199 | -0.041199 | -0.091553 | 0.082397 | -0.07782 | -122.1313 | 0.032043 | 0.045776 | 0.1236 | -122.2 | 0.01831 | -0.032044 | -122.1634 | 0.10986 | -0.032044 | 0 | -122.1909 | 0.16022 | 0.091552 | 0.036621 | -122.3694 | 0.12817 | 0.10071 | 0.068664 | -122.3236
3741.875 | 122.319 | -0.10071 | 122.287 | -0.04303 | 0.048477 | 0.0599 | 0.0021191 | 0.031678 | 0.00017302 | 0.031287 | -0.054626 | 0.028546 | 0.034746 | 0.048815 | 0.0040225 | 0.028213 | 0.041199 | 0.018311 | 0.004578 | 0 | 0.091553 | 0.009155 | -0.11444 | 0.041199 | 0.013733 | -0.10071 | 0.068665 | 0.059509 | -0.054932 | -0.10529 | 0.10986 | -0.013733 | -122.1954 | 0.11902 | 0.10071 | 0.11444 | -122.2458 | 0.045776 | -0.004578 | -122.2183 | 0.14191 | 0 | 0.004578 | -122.2275 | 0.19226 | 0.14191 | 0.10529 | -122.4014 | 0.16937 | 0.16022 | 0.11444 | -122.3923
3743.6406 | 122.374 | -0.10529 | 122.2778 | -0.23376 | 0.049546 | 0.060968 | 0.0072461 | 0.031678 | -0.0036722 | 0.031287 | -0.2301 | 0.026837 | 0.036882 | 0.049669 | -3.629e-05 | 0.027999 | -0.018311 | 0 | -0.018311 | -0.018311 | 0.082397 | 0.004578 | -0.13733 | 0.013733 | 0.022888 | -0.086975 | 0.073242 | 0.064087 | -0.045776 | -0.09613 | 0.10986 | -0.032043 | -122.1954 | 0.10529 | 0.086975 | 0.11902 | -122.2961 | 0.05951 | 0.009156 | -122.2046 | 0.11902 | 0.018311 | 0.009155 | -122.2137 | 0.18768 | 0.086975 | 0.086975 | -122.4152 | 0.17853 | 0.16937 | 0.12817 | -122.374
3745.3438 | 122.4289 | -0.054932 | 122.2458 | 0.11719 | 0.044205 | 0.060754 | 0.0014783 | 0.031251 | -0.0064492 | 0.030433 | 0.14374 | 0.027478 | 0.037309 | 0.048174 | 0.00039091 | 0.027786 | 0.064087 | 0.13733 | 0.1236 | 0.059509 | 0.054932 | 0.064087 | -0.091553 | 0.13275 | 0.14648 | 0.041199 | 0.018311 | 0.009155 | -0.027466 | -0.068665 | 0.11902 | -0.036621 | -122.1909 | 0.19226 | 0.11444 | 0.15106 | -122.1817 | 0.027466 | -0.013733 | -122.2275 | 0.18768 | 0.096131 | 0.10986 | -122.2366 | 0.10986 | 0.11902 | 0.17853 | -122.3373 | 0.073243 | 0.064087 | 0.20142 | -122.3145
3747.1094 | 122.438 | -0.068665 | 122.2549 | 0.010376 | 0.0457 | 0.063104 | 0.0025465 | 0.031037 | -0.0064492 | 0.028297 | 0.067444 | 0.026197 | 0.037309 | 0.047106 | -0.0032407 | 0.029922 | 0.027466 | 0.068665 | 0.054932 | 0.041199 | 0.064087 | 0.054932 | -0.09613 | 0.086975 | 0.091553 | -0.004578 | 0.041199 | 0.009155 | -0.013733 | -0.07782 | 0.1236 | -0.027465 | -122.1909 | 0.13733 | 0.10986 | 0.13733 | -122.2275 | 0.054932 | -0.009155 | -122.2137 | 0.15564 | 0.064087 | 0.073242 | -122.2458 | 0.13275 | 0.096131 | 0.1236 | -122.3511 | 0.10986 | 0.07782 | 0.16022 | -122.3328
3748.875 | 122.3877 | -0.064087 | 122.2687 | -0.19562 | 0.04805 | 0.060327 | 0.0040417 | 0.02826 | -0.00025418 | 0.030433 | -0.20721 | 0.028333 | 0.037096 | 0.048601 | 0.0012455 | 0.026291 | 0.004578 | 0.004578 | -0.032043 | 0 | 0.086975 | 0.013733 | -0.13275 | 0.032043 | 0.036621 | -0.073242 | 0.050354 | 0.036621 | -0.054932 | -0.10986 | 0.07782 | -0.068664 | -122.1817 | 0.068665 | 0.064087 | 0.13275 | -122.2641 | 0.009155 | -0.045776 | -122.2183 | 0.09613 | -0.009155 | 0.036621 | -122.2321 | 0.15106 | 0.068665 | 0.032044 | -122.4014 | 0.11444 | 0.10071 | 0.10071 | -122.3785
3750.6406 | 122.3602 | -0.09613 | 122.2916 | 0.040894 | 0.048264 | 0.060541 | 0.00083745 | 0.030824 | 0.0010276 | 0.032996 | 0.021668 | 0.03111 | 0.036882 | 0.05031 | 0.0033817 | 0.027999 | -0.022888 | -0.027466 | -0.054932 | 0 | 0.07782 | 0 | -0.13275 | 0.032043 | -0.004578 | -0.11444 | 0.068665 | 0.064087 | -0.073242 | -0.11902 | 0.09613 | -0.036621 | -122.2137 | 0.068664 | 0.09613 | 0.13275 | -122.3145 | 0.022888 | -0.022889 | -122.2229 | 0.12817 | -0.018311 | 0.004578 | -122.2275 | 0.17395 | 0.073242 | 0.041198 | -122.4243 | 0.16479 | 0.16022 | 0.091552 | -122.4106
3752.3281 | 122.3419 | -0.11444 | 122.3053 | 0.36896 | 0.04805 | 0.06225 | 0.0012647 | 0.029969 | -0.00025418 | 0.032142 | 0.0064086 | 0.027478 | 0.037309 | 0.049029 | 0.0059451 | 0.02864 | -0.018311 | 0 | -0.041199 | -0.004578 | 0.07782 | 0.018311 | -0.11902 | -0.004578 | -0.004578 | -0.10529 | 0.054932 | 0.036621 | -0.054932 | -0.11444 | 0.13275 | -0.004578 | -122.2275 | 0.11444 | 0.10986 | 0.11444 | -122.3236 | 0.059509 | 0 | -122.2504 | 0.10986 | 0.009155 | 0.009155 | -122.2687 | 0.19226 | 0.09613 | 0.073242 | -122.4243 | 0.16937 | 0.15106 | 0.10986 | -122.4197
3754.0938 | 122.4747 | -0.045776 | 122.2137 | -0.10406 | 0.045487 | 0.06225 | 0.0066053 | 0.033387 | -0.012644 | 0.031928 | -0.046997 | 0.026837 | 0.03795 | 0.047533 | -0.0043087 | 0.028854 | 0.050354 | 0.11902 | 0.10529 | 0.064087 | 0.059509 | 0.054932 | -0.09613 | 0.14648 | 0.17853 | 0.068665 | 0.018311 | 0.013733 | -0.022888 | -0.059509 | 0.10071 | -0.050354 | -122.1542 | 0.16479 | 0.10986 | 0.16022 | -122.1634 | 0.022888 | -0.013733 | -122.1954 | 0.19226 | 0.11444 | 0.12817 | -122.2 | 0.10528 | 0.09613 | 0.15106 | -122.3099 | 0.064087 | 0.059509 | 0.2243 | -122.2733
3755.7969 | 122.4197 | -0.059509 | 122.2687 | 0.079041 | 0.042282 | 0.061609 | 0.00041005 | 0.031251 | -0.0058084 | 0.029365 | 0.16663 | 0.02876 | 0.032823 | 0.050524 | 0.0020999 | 0.029281 | 0.07782 | 0.11444 | 0.10071 | 0.041199 | 0.045776 | 0.068665 | -0.091553 | 0.12817 | 0.12817 | 0.013733 | 0.032043 | 0.027466 | -0.022888 | -0.082397 | 0.12817 | -0.032044 | -122.2229 | 0.17395 | 0.10071 | 0.13275 | -122.1909 | 0.036621 | -0.022888 | -122.2366 | 0.18768 | 0.073242 | 0.09613 | -122.2412 | 0.10528 | 0.13733 | 0.16022 | -122.3602 | 0.091552 | 0.086975 | 0.18768 | -122.3511
3757.5469 | 122.4106 | -0.064087 | 122.2321 | 0.063782 | 0.043351 | 0.061823 | 0.0023329 | 0.031892 | -0.0075174 | 0.029151 | 0.097962 | 0.027478 | 0.035814 | 0.046252 | -0.00046349 | 0.029068 | 0.059509 | 0.082397 | 0.050354 | 0.032043 | 0.059509 | 0.059509 | -0.086975 | 0.10071 | 0.086975 | 0.004578 | 0.032043 | 0.013733 | 0 | -0.086975 | 0.1236 | -0.022888 | -122.1725 | 0.14648 | 0.09613 | 0.11902 | -122.1725 | 0.064087 | -0.022888 | -122.2 | 0.1648 | 0.068665 | 0.091553 | -122.2183 | 0.1236 | 0.1236 | 0.11444 | -122.319 | 0.09613 | 0.07782 | 0.15106 | -122.319
3759.3125 | 122.3602 | -0.091553 | 122.287 | 0.056152 | 0.049546 | 0.061609 | 0.0014783 | 0.03061 | 0.0027364 | 0.030006 | 0.044556 | 0.028546 | 0.034959 | 0.048174 | 0.0035953 | 0.02565 | -0.009155 | -0.045776 | -0.041199 | -0.013733 | 0.086975 | 0.032043 | -0.13733 | 0.022888 | -0.032043 | -0.09613 | 0.050354 | 0.068665 | -0.045776 | -0.09613 | 0.1236 | -0.045776 | -122.2 | 0.045777 | 0.07782 | 0.1236 | -122.2961 | 0.045777 | -0.004577 | -122.2366 | 0.11444 | -0.004577 | 0 | -122.2183 | 0.17853 | 0.082398 | 0.050354 | -122.4243 | 0.14191 | 0.16022 | 0.05951 | -122.3831
3761.0781 | 122.4335 | -0.045776 | 122.2595 | 0.033264 | 0.043351 | 0.060754 | 0.0029737 | 0.02826 | -0.007731 | 0.029151 | 0.052185 | 0.025128 | 0.036027 | 0.046465 | -0.0030271 | 0.027572 | 0.036621 | 0.068665 | 0.064087 | 0.036621 | 0.059509 | 0.050354 | -0.082397 | 0.10529 | 0.07782 | 0.004578 | 0.027466 | 0.009155 | -0.027466 | -0.07782 | 0.09613 | -0.036621 | -122.2 | 0.11444 | 0.082397 | 0.11902 | -122.2229 | 0.01831 | -0.032044 | -122.2321 | 0.15106 | 0.050354 | 0.082398 | -122.2504 | 0.10528 | 0.082397 | 0.10986 | -122.3419 | 0.073242 | 0.054931 | 0.1236 | -122.3373
3762.7969 | 122.4289 | -0.041199 | 122.2412 | 0.048523 | 0.044846 | 0.058191 | 0.0038281 | 0.031465 | -0.0055948 | 0.030433 | 0.044556 | 0.025128 | 0.035814 | 0.048601 | -3.629e-05 | 0.029281 | 0.045776 | 0.073242 | 0.064087 | 0.036621 | 0.059509 | 0.054932 | -0.11444 | 0.091553 | 0.10071 | 0.009155 | 0.036621 | 0.004578 | -0.018311 | -0.086975 | 0.096131 | -0.073242 | -122.1817 | 0.11444 | 0.07782 | 0.15106 | -122.1954 | 0.022888 | -0.045776 | -122.2046 | 0.13275 | 0.050354 | 0.09613 | -122.2366 | 0.10071 | 0.086975 | 0.10529 | -122.3557 | 0.07782 | 0.045777 | 0.14191 | -122.3282
3764.5625 | 122.4243 | -0.059509 | 122.2733 | 0.094299 | 0.048264 | 0.06225 | 0.0025465 | 0.027833 | -0.0051676 | 0.031074 | 0.12085 | 0.026624 | 0.038377 | 0.047533 | 0.00039091 | 0.027145 | 0.07782 | 0.10071 | 0.09613 | 0.059509 | 0.027466 | 0.050354 | -0.086975 | 0.13275 | 0.10071 | 0.004578 | 0.032043 | 0.018311 | -0.009155 | -0.068665 | 0.10986 | -0.027466 | -122.2458 | 0.16022 | 0.11902 | 0.14648 | -122.1954 | 0.050354 | -0.009156 | -122.2412 | 0.19226 | 0.064087 | 0.073243 | -122.2549 | 0.086975 | 0.13733 | 0.15564 | -122.3602 | 0.091552 | 0.07782 | 0.16022 | -122.3419
3766.3125 | 122.4701 | -0.032043 | 122.2595 | 0.094299 | 0.045914 | 0.060754 | 0.0016919 | 0.034455 | -0.00089518 | 0.032783 | 0.052185 | 0.028333 | 0.036027 | 0.047747 | 0.0042361 | 0.025222 | 0.045776 | 0.009155 | -0.018311 | -0.013733 | 0.086975 | 0.022888 | -0.12817 | 0.073242 | 0.013733 | -0.07782 | 0.054932 | 0.036621 | -0.045776 | -0.10529 | 0.054931 | -0.096131 | -122.1725 | 0.041198 | 0.01831 | 0.11444 | -122.2137 | -0.013733 | -0.073243 | -122.2046 | 0.10529 | -0.045777 | 0.027466 | -122.2229 | 0.11902 | 0.077819 | 0.013732 | -122.3877 | 0.086975 | 0.068664 | 0.045776 | -122.3648
3768.0781 | 122.438 | -0.050354 | 122.2504 | 0.14008 | 0.045273 | 0.060968 | 0.0010511 | 0.029328 | -0.0036722 | 0.03321 | 0.11322 | 0.027478 | 0.035814 | 0.047533 | 0.0010317 | 0.027572 | 0.091553 | 0.13733 | 0.1236 | 0.064087 | 0.032043 | 0.054932 | -0.059509 | 0.16937 | 0.14648 | 0.036621 | 0.022888 | -0.009155 | -0.004578 | -0.068665 | 0.10529 | -0.009155 | -122.2183 | 0.18768 | 0.11444 | 0.1236 | -122.1588 | 0.045776 | -0.018311 | -122.2275 | 0.21973 | 0.086975 | 0.10529 | -122.2595 | 0.082397 | 0.14191 | 0.17395 | -122.3099 | 0.073242 | 0.041199 | 0.19684 | -122.319
3769.8438 | 122.4152 | -0.073242 | 122.2458 | 0.08667 | 0.047196 | 0.059259 | 0.0040417 | 0.028474 | -0.006663 | 0.029792 | 0.11322 | 0.025983 | 0.036027 | 0.047747 | -0.0013181 | 0.027999 | 0.068665 | 0.091553 | 0.082397 | 0.036621 | 0.050354 | 0.041199 | -0.073242 | 0.1236 | 0.07782 | 0.004578 | 0.018311 | 0.036621 | -0.018311 | -0.082397 | 0.11444 | 0 | -122.1954 | 0.16479 | 0.10986 | 0.10986 | -122.1771 | 0.054931 | -0.009155 | -122.2275 | 0.19684 | 0.07782 | 0.086975 | -122.2092 | 0.1236 | 0.14191 | 0.15564 | -122.319 | 0.091553 | 0.10986 | 0.15106 | -122.3282
3771.5469 | 122.3923 | -0.086975 | 122.2595 | 0.10193 | 0.047196 | 0.060541 | 0.00083745 | 0.028474 | -0.0011088 | 0.03086 | 0.059815 | 0.029615 | 0.035814 | 0.050097 | 0.0053043 | 0.027572 | -0.004578 | -0.013733 | -0.054932 | -0.013733 | 0.086975 | 0.009155 | -0.11902 | 0.064087 | -0.009155 | -0.09613 | 0.068665 | 0.032043 | -0.045776 | -0.10071 | 0.09613 | -0.032044 | -122.1725 | 0.073242 | 0.073242 | 0.10529 | -122.2641 | 0.041199 | -0.013733 | -122.1909 | 0.15106 | -0.009155 | 0.004578 | -122.2275 | 0.17395 | 0.082397 | 0.032043 | -122.3785 | 0.15564 | 0.11902 | 0.07782 | -122.3602
3773.2969 | 122.3419 | -0.10529 | 122.2916 | -0.081177 | 0.048264 | 0.060541 | 0.0038281 | 0.030824 | 0.00017302 | 0.033423 | -0.092773 | 0.028974 | 0.037523 | 0.048388 | 0.0031681 | 0.024582 | 0.073242 | 0.036621 | 0.009155 | 0.013733 | 0.073242 | 0.022888 | -0.11902 | 0.068665 | 0.050354 | -0.082397 | 0.050354 | 0.050354 | -0.045776 | -0.09613 | 0.12817 | -0.013733 | -122.2183 | 0.14191 | 0.11902 | 0.13275 | -122.2183 | 0.05951 | 0.009156 | -122.2412 | 0.17395 | 0.022889 | 0.013733 | -122.2412 | 0.17853 | 0.17853 | 0.11444 | -122.4106 | 0.15564 | 0.15564 | 0.15564 | -122.3877
3775.0469 | 122.4289 | -0.068665 | 122.2321 | 0.040894 | 0.044205 | 0.060541 | 0.0048963 | 0.029542 | -0.0081582 | 0.030433 | 0.067444 | 0.027478 | 0.036241 | 0.048815 | -0.0034543 | 0.029281 | 0.027466 | 0.073242 | 0.064087 | 0.022888 | 0.045776 | 0.032043 | -0.09613 | 0.091553 | 0.091553 | 0 | 0.018311 | 0.027466 | -0.018311 | -0.07782 | 0.10071 | -0.027465 | -122.1863 | 0.14191 | 0.091553 | 0.11902 | -122.2046 | 0.050354 | -0.009155 | -122.2137 | 0.16022 | 0.068665 | 0.07782 | -122.2046 | 0.11444 | 0.096131 | 0.13275 | -122.3282 | 0.086976 | 0.096131 | 0.16022 | -122.3099
3776.75 | 122.4518 | -0.050354 | 122.2641 | 0.12482 | 0.044846 | 0.058191 | 0.00083745 | 0.030824 | -0.0038858 | 0.030219 | 0.17426 | 0.025769 | 0.035387 | 0.048174 | 0.0040225 | 0.026718 | 0.091553 | 0.1236 | 0.10071 | 0.07782 | 0.045776 | 0.050354 | -0.086975 | 0.16022 | 0.13733 | 0.036621 | 0.022888 | 0.009155 | -0.013733 | -0.054932 | 0.10071 | -0.036621 | -122.2183 | 0.17395 | 0.12817 | 0.16479 | -122.1725 | 0.036621 | -0.004578 | -122.2412 | 0.21057 | 0.086975 | 0.091553 | -122.2549 | 0.09613 | 0.14191 | 0.15106 | -122.3511 | 0.073242 | 0.059509 | 0.18768 | -122.319
3778.5 | 122.3923 | -0.09613 | 122.2778 | -0.23376 | 0.048905 | 0.061395 | 0.0046827 | 0.031465 | -0.0017496 | 0.029578 | -0.21484 | 0.026624 | 0.034959 | 0.048601 | 0.00017731 | 0.026504 | -0.009155 | -0.004578 | -0.036621 | -0.009155 | 0.09613 | 0 | -0.12817 | 0.018311 | 0.045776 | -0.086975 | 0.068665 | 0.045776 | -0.045776 | -0.082397 | 0.09613 | -0.032044 | -122.1817 | 0.091552 | 0.086975 | 0.11902 | -122.287 | 0.050354 | 0.013733 | -122.2092 | 0.11444 | 0.009155 | -0.004578 | -122.2321 | 0.19226 | 0.086975 | 0.059509 | -122.406 | 0.16479 | 0.14191 | 0.14191 | -122.3602
3780.2656 | 122.4106 | -0.082397 | 122.3007 | -0.15747 | 0.047196 | 0.059473 | 0.0061781 | 0.031251 | -0.00025418 | 0.030433 | -0.1767 | 0.02876 | 0.038805 | 0.049242 | 0.0018863 | 0.025009 | 0.032043 | 0.032043 | 0.009155 | 0.027466 | 0.068665 | 0.022888 | -0.13275 | 0.059509 | 0.086975 | -0.064087 | 0.059509 | 0.054932 | -0.041199 | -0.091553 | 0.10528 | -0.050354 | -122.2321 | 0.11444 | 0.10986 | 0.16022 | -122.2687 | 0.041198 | -0.009156 | -122.2412 | 0.14191 | 0.01831 | 0.027466 | -122.2458 | 0.15106 | 0.11444 | 0.091552 | -122.4335 | 0.14191 | 0.13733 | 0.16937 | -122.3923
3781.9844 | 122.3785 | -0.10529 | 122.287 | -0.24139 | 0.046982 | 0.061823 | 0.0059643 | 0.028688 | -0.0028178 | 0.03086 | -0.2301 | 0.028974 | 0.035387 | 0.049242 | -0.00067729 | 0.028854 | 0 | -0.004578 | -0.018311 | -0.013733 | 0.10071 | 0.004578 | -0.14648 | 0.009155 | 0.036621 | -0.091553 | 0.091553 | 0.041199 | -0.054932 | -0.10071 | 0.10986 | -0.041198 | -122.1863 | 0.10071 | 0.091553 | 0.13275 | -122.287 | 0.050354 | 0.004578 | -122.1954 | 0.11444 | 0.013733 | 0.009155 | -122.2458 | 0.20599 | 0.10529 | 0.086975 | -122.4335 | 0.19684 | 0.14649 | 0.14191 | -122.3877
3783.75 | 122.3282 | -0.091553 | 122.3053 | -0.088806 | 0.049332 | 0.058191 | 0.0031873 | 0.029328 | -0.00025418 | 0.032783 | -0.1004 | 0.030469 | 0.036027 | 0.049029 | 0.0029543 | 0.027359 | 0.068665 | 0.032043 | 0.027466 | 0.041199 | 0.07782 | 0.013733 | -0.11444 | 0.068665 | 0.054932 | -0.068665 | 0.064087 | 0.041199 | -0.050354 | -0.086975 | 0.10529 | -0.022888 | -122.2275 | 0.1236 | 0.13275 | 0.15564 | -122.2366 | 0.041199 | 0.004578 | -122.2412 | 0.16022 | 0.022888 | 0.01831 | -122.2641 | 0.16937 | 0.16022 | 0.11902 | -122.4197 | 0.15564 | 0.13275 | 0.14649 | -122.3923
3785.5312 | 122.4655 | -0.054932 | 122.2641 | -0.027771 | 0.04036 | -0.034308 | 0.0027601 | 0.027619 | -0.011149 | 0.030219 | 0.021668 | 0.027692 | 0.033678 | 0.047533 | -0.0015317 | 0.029708 | 0.009155 | 0.082397 | 0.068665 | 0.050354 | 0.07782 | 0.050354 | -0.09613 | 0.10529 | 0.13275 | 0.036621 | 0.022888 | 0.013733 | -0.018311 | -0.073242 | 0.10529 | -0.041198 | -122.1863 | 0.13733 | 0.10529 | 0.14648 | -122.2549 | 0.036621 | -0.01831 | -122.2412 | 0.16022 | 0.091553 | 0.10986 | -122.2504 | 0.13275 | 0.064087 | 0.1236 | -122.3602 | 0.07782 | 0.068665 | 0.18768 | -122.3373
3787.2812 | 122.4701 | -0.045776 | 122.2733 | 0.08667 | 0.043991 | 0.060114 | 0.0010511 | 0.030397 | -0.0051676 | 0.028724 | 0.159 | 0.027265 | 0.035387 | 0.047106 | 0.0010317 | 0.027145 | 0.09613 | 0.10071 | 0.091553 | 0.054932 | 0.059509 | 0.045776 | -0.07782 | 0.13733 | 0.14191 | 0.032043 | 0.009155 | 0.013733 | -0.009155 | -0.059509 | 0.091552 | -0.032044 | -122.2137 | 0.14648 | 0.10071 | 0.13275 | -122.1771 | 0.036621 | -0.013733 | -122.2641 | 0.18311 | 0.077819 | 0.091552 | -122.2595 | 0.10528 | 0.14191 | 0.13733 | -122.3511 | 0.054931 | 0.059509 | 0.18768 | -122.3328
3788.9844 | 122.4014 | -0.068665 | 122.2549 | -0.18036 | 0.046555 | 0.059259 | 0.0057507 | 0.029542 | -0.00089518 | 0.029151 | -0.19196 | 0.028546 | 0.035814 | 0.049242 | 0.0014591 | 0.024154 | 0.032043 | 0.032043 | 0 | 0.027466 | 0.091553 | 0.018311 | -0.12817 | 0.07782 | 0.073242 | -0.059509 | 0.045776 | 0.032043 | -0.022888 | -0.09613 | 0.086976 | -0.059509 | -122.1634 | 0.10071 | 0.096131 | 0.15564 | -122.2229 | 0.045777 | -0.027465 | -122.2092 | 0.14649 | 0.009156 | 0.036621 | -122.2229 | 0.16022 | 0.10071 | 0.068665 | -122.3831 | 0.11444 | 0.10071 | 0.14191 | -122.3511
3790.75 | 122.3511 | -0.10071 | 122.2916 | 0.025635 | 0.047623 | 0.058618 | 0.0025465 | 0.03061 | 0.00038662 | 0.030006 | 0.014038 | 0.030255 | 0.036455 | 0.051165 | 0.0016727 | 0.027359 | 0.027466 | -0.036621 | -0.032043 | 0 | 0.073242 | 0.027466 | -0.11902 | 0.018311 | 0 | -0.11444 | 0.050354 | 0.045776 | -0.068665 | -0.1236 | 0.12817 | -0.018311 | -122.2183 | 0.064087 | 0.10071 | 0.11902 | -122.2641 | 0.032043 | -0.022888 | -122.2412 | 0.11902 | -0.013733 | 0.009155 | -122.2458 | 0.17395 | 0.12817 | 0.068665 | -122.4106 | 0.15106 | 0.14648 | 0.10071 | -122.4152
3792.4531 | 122.3511 | -0.086975 | 122.2961 | -0.24902 | 0.046982 | 0.061182 | 0.0098097 | 0.031037 | -0.007731 | 0.028724 | -0.18433 | 0.028333 | 0.038377 | 0.05031 | -0.0028135 | 0.027786 | 0.041199 | 0.07782 | 0.045776 | 0.050354 | 0.073242 | 0.018311 | -0.10071 | 0.050354 | 0.09613 | -0.036621 | 0.054932 | 0.036621 | -0.045776 | -0.091553 | 0.10529 | -0.013733 | -122.2229 | 0.16479 | 0.13733 | 0.15106 | -122.2549 | 0.041199 | -0.004578 | -122.2412 | 0.13733 | 0.050354 | 0.054932 | -122.2595 | 0.16022 | 0.12817 | 0.13275 | -122.3969 | 0.14191 | 0.1236 | 0.1831 | -122.3877
3794.2031 | 122.3419 | -0.10529 | 122.2778 | -0.23376 | 0.048905 | 0.059686 | 0.0044691 | 0.029328 | -0.0058084 | 0.030433 | -0.13855 | 0.028333 | 0.038164 | 0.047533 | -0.0023861 | 0.029281 | 0.022888 | 0.027466 | 0.022888 | 0.013733 | 0.082397 | 0.004578 | -0.12817 | 0.027466 | 0.050354 | -0.068665 | 0.059509 | 0.041199 | -0.059509 | -0.10986 | 0.10986 | -0.022888 | -122.1954 | 0.13275 | 0.11902 | 0.14191 | -122.2549 | 0.045777 | -0.004577 | -122.2183 | 0.13275 | 0.036621 | 0.041198 | -122.2366 | 0.18768 | 0.12817 | 0.12817 | -122.406 | 0.16479 | 0.14649 | 0.15564 | -122.3877
3795.9531 | 122.3373 | -0.091553 | 122.3007 | 0.37659 | 0.049118 | 0.058191 | 0.00062385 | 0.031251 | 0.00060022 | 0.030646 | -0.016479 | 0.028974 | 0.036455 | 0.049883 | 0.0040225 | 0.027359 | 0.009155 | -0.045776 | -0.036621 | -0.009155 | 0.10986 | 0.013733 | -0.1236 | -0.009155 | 0.013733 | -0.12817 | 0.059509 | 0.041199 | -0.050354 | -0.091553 | 0.10529 | -0.032043 | -122.1909 | 0.045777 | 0.082398 | 0.11444 | -122.2916 | 0.041199 | 0 | -122.2412 | 0.082398 | -0.036621 | -0.036621 | -122.2595 | 0.20142 | 0.10071 | 0.054932 | -122.4243 | 0.15106 | 0.13275 | 0.10529 | -122.3923
3797.7031 | 122.3511 | -0.10986 | 122.2778 | 0.056152 | 0.047196 | 0.059473 | 0.0014783 | 0.028901 | -0.00089518 | 0.034278 | 0.021668 | 0.029615 | 0.038591 | 0.049883 | 0.0020999 | 0.028213 | -0.032043 | -0.036621 | -0.050354 | -0.013733 | 0.09613 | -0.004578 | -0.1236 | 0.032043 | 0.004578 | -0.10071 | 0.050354 | 0.050354 | -0.064087 | -0.1236 | 0.10529 | -0.013733 | -122.1817 | 0.073242 | 0.09613 | 0.10986 | -122.3099 | 0.045776 | -0.013733 | -122.2275 | 0.14191 | 0.009155 | 0.022888 | -122.2275 | 0.20599 | 0.07782 | 0.059509 | -122.4014 | 0.16022 | 0.16022 | 0.11444 | -122.4014
3799.3906 | 122.4152 | -0.059509 | 122.2458 | 0.10956 | 0.041642 | 0.060754 | 0.00062385 | 0.032319 | -0.0098672 | 0.029151 | 0.12848 | 0.02641 | 0.033891 | 0.046252 | 0.00039091 | 0.031417 | 0.059509 | 0.091553 | 0.064087 | 0.032043 | 0.050354 | 0.064087 | -0.086975 | 0.11902 | 0.10529 | 0.018311 | 0.004578 | 0.022888 | -0.013733 | -0.068665 | 0.1236 | -0.027466 | -122.1954 | 0.15106 | 0.091552 | 0.11902 | -122.1863 | 0.045776 | -0.009156 | -122.2412 | 0.17853 | 0.07782 | 0.086976 | -122.2229 | 0.10986 | 0.11902 | 0.1236 | -122.3328 | 0.064087 | 0.082397 | 0.16479 | -122.3145
3801.1562 | 122.3557 | -0.11902 | 122.287 | -0.25665 | 0.043778 | 0.060754 | 0.0036145 | 0.034669 | -0.004313 | 0.029151 | -0.32166 | 0.02876 | 0.036882 | 0.048815 | -0.00024989 | 0.029495 | 0.041199 | 0.041199 | 0.018311 | 0.022888 | 0.073242 | 0.027466 | -0.1236 | 0.022888 | 0.045776 | -0.068665 | 0.059509 | 0.054932 | -0.054932 | -0.091553 | 0.14649 | -0.004577 | -122.2137 | 0.16022 | 0.14191 | 0.14648 | -122.2458 | 0.064087 | 0.027466 | -122.2275 | 0.14191 | 0.050354 | 0.022888 | -122.2321 | 0.19226 | 0.16022 | 0.13733 | -122.4106 | 0.17853 | 0.17395 | 0.16479 | -122.3785
3802.9219 | 122.3694 | -0.082397 | 122.287 | -0.10406 | 0.050827 | 0.059045 | 0.0040417 | 0.030824 | 0.00081382 | 0.03086 | -0.14618 | 0.030469 | 0.034959 | 0.050524 | 0.0012455 | 0.023727 | 0.064087 | 0.050354 | 0.013733 | 0.032043 | 0.082397 | 0.013733 | -0.11444 | 0.07782 | 0.10071 | -0.050354 | 0.050354 | 0.041199 | -0.041199 | -0.09613 | 0.09613 | -0.032044 | -122.2046 | 0.13275 | 0.11444 | 0.14648 | -122.2229 | 0.041198 | -0.013733 | -122.2366 | 0.16022 | 0.032043 | 0.045776 | -122.2458 | 0.16479 | 0.14648 | 0.09613 | -122.4014 | 0.13275 | 0.1236 | 0.18311 | -122.3831
3804.6875 | 122.4197 | -0.068665 | 122.2321 | 0.11719 | 0.0457 | 0.058618 | 0.0029737 | 0.028688 | -0.004954 | 0.030646 | 0.12848 | 0.025128 | 0.037523 | 0.047961 | -0.0015317 | 0.030563 | 0.091553 | 0.10529 | 0.10529 | 0.059509 | 0.041199 | 0.036621 | -0.091553 | 0.13733 | 0.11902 | 0.045776 | 0 | 0.018311 | -0.013733 | -0.068665 | 0.10529 | -0.022888 | -122.1909 | 0.17395 | 0.12817 | 0.15106 | -122.1405 | 0.054932 | 0 | -122.2321 | 0.20599 | 0.11444 | 0.11444 | -122.2137 | 0.10986 | 0.16022 | 0.17395 | -122.3236 | 0.068665 | 0.086976 | 0.18768 | -122.3007
3806.4531 | 122.4701 | -0.045776 | 122.2275 | 0.063782 | 0.047623 | 0.062036 | -0.00023075 | 0.033814 | -0.0028178 | 0.03086 | 0.097962 | 0.026837 | 0.036882 | 0.048388 | 0.0018863 | 0.026504 | 0.086975 | 0.091553 | 0.082397 | 0.073242 | 0.054932 | 0.059509 | -0.082397 | 0.14648 | 0.13733 | 0.022888 | 0.013733 | -0.004578 | -0.018311 | -0.068665 | 0.10528 | -0.036621 | -122.1725 | 0.13733 | 0.11902 | 0.15564 | -122.1405 | 0.027465 | -0.022889 | -122.2137 | 0.19226 | 0.068664 | 0.091553 | -122.2321 | 0.10071 | 0.13275 | 0.12817 | -122.3099 | 0.059509 | 0.041198 | 0.18311 | -122.2961
3808.2188 | 122.438 | -0.068665 | 122.2549 | 0.08667 | 0.043991 | 0.060754 | 0.0019055 | 0.031037 | -0.0036722 | 0.029151 | 0.15137 | 0.027051 | 0.035814 | 0.048174 | -0.00024989 | 0.027786 | 0.07782 | 0.13275 | 0.11444 | 0.054932 | 0.032043 | 0.050354 | -0.064087 | 0.14191 | 0.11444 | 0.032043 | 0.018311 | 0.004578 | -0.027466 | -0.064087 | 0.11902 | 0.004578 | -122.2229 | 0.20142 | 0.1236 | 0.11902 | -122.1771 | 0.041199 | 0.004578 | -122.2366 | 0.21057 | 0.10071 | 0.09613 | -122.2504 | 0.10071 | 0.14649 | 0.18311 | -122.319 | 0.086976 | 0.073243 | 0.18311 | -122.319
3809.9219 | 122.3602 | -0.086975 | 122.3053 | -0.18799 | 0.043991 | 0.0599 | 0.0036145 | 0.029542 | -0.004313 | 0.030219 | -0.23773 | 0.027051 | 0.037523 | 0.048388 | 0.00081811 | 0.027145 | 0 | 0.004578 | -0.032043 | -0.022888 | 0.10529 | 0.022888 | -0.13733 | 0.022888 | 0.032043 | -0.086975 | 0.07782 | 0.064087 | -0.059509 | -0.10986 | 0.10986 | -0.050354 | -122.2 | 0.091553 | 0.064087 | 0.11444 | -122.3053 | 0.027466 | -0.022888 | -122.2275 | 0.10986 | 0 | 0.022888 | -122.2412 | 0.19226 | 0.086975 | 0.054932 | -122.4426 | 0.16479 | 0.15106 | 0.11902 | -122.4152
3811.6875 | 122.4289 | -0.059509 | 122.2229 | 0.010376 | 0.040787 | 0.060754 | -0.00044435 | 0.029969 | -0.007731 | 0.029578 | 0.059815 | 0.02641 | 0.036241 | 0.049456 | -0.00024989 | 0.029281 | 0.041199 | 0.045776 | 0.059509 | 0.036621 | 0.054932 | 0.041199 | -0.10529 | 0.10071 | 0.086975 | 0.004578 | 0.036621 | 0.027466 | -0.022888 | -0.059509 | 0.10071 | -0.045777 | -122.168 | 0.10528 | 0.09613 | 0.14191 | -122.1817 | 0.036621 | 0 | -122.1863 | 0.16022 | 0.064087 | 0.064087 | -122.1954 | 0.11444 | 0.10071 | 0.11902 | -122.3282 | 0.09613 | 0.086975 | 0.14648 | -122.2824
3813.4531 | 122.4701 | -0.059509 | 122.2321 | 0.010376 | 0.046341 | 0.061395 | 0.0061781 | 0.029542 | -0.006022 | 0.028937 | 0.036926 | 0.025342 | 0.036455 | 0.047533 | -0.0015317 | 0.028213 | 0.027466 | 0.045776 | 0.054932 | 0.032043 | 0.054932 | 0.059509 | -0.10529 | 0.082397 | 0.082397 | -0.004578 | 0.027466 | 0.022888 | -0.013733 | -0.091553 | 0.11902 | -0.045777 | -122.1771 | 0.10528 | 0.091552 | 0.13733 | -122.2046 | 0.045776 | -0.032044 | -122.2046 | 0.14191 | 0.054931 | 0.086975 | -122.2092 | 0.11444 | 0.086975 | 0.11444 | -122.3373 | 0.086975 | 0.082397 | 0.14191 | -122.3236
3815.1562 | 122.3648 | -0.073242 | 122.2961 | -0.096436 | 0.046768 | 0.060754 | -0.0015125 | 0.031678 | 0.0016684 | 0.030006 | -0.16907 | 0.029401 | 0.035173 | 0.05031 | 0.0057315 | 0.026077 | 0.07782 | 0.036621 | 0.013733 | 0.018311 | 0.086975 | 0.022888 | -0.13275 | 0.091553 | 0.082397 | -0.045776 | 0.054932 | 0.041199 | -0.050354 | -0.10986 | 0.09613 | -0.059509 | -122.2092 | 0.10986 | 0.091553 | 0.15106 | -122.2183 | 0.022888 | -0.036621 | -122.2412 | 0.16479 | 0.027466 | 0.064087 | -122.2549 | 0.16022 | 0.15106 | 0.086975 | -122.4289 | 0.12817 | 0.11444 | 0.15564 | -122.406
3816.9219 | 122.4838 | -0.064087 | 122.2321 | -0.073547 | 0.043351 | 0.063318 | 0.0025465 | 0.028688 | -0.0092264 | 0.031287 | -0.11566 | 0.025769 | 0.034959 | 0.046679 | -0.0017453 | 0.029281 | 0.054932 | 0.10529 | 0.091553 | 0.059509 | 0.054932 | 0.059509 | -0.10071 | 0.14648 | 0.16022 | 0.054932 | 0.018311 | 0.004578 | -0.009155 | -0.054932 | 0.1236 | -0.036621 | -122.1771 | 0.16937 | 0.1236 | 0.16022 | -122.1771 | 0.054932 | 0.009155 | -122.2137 | 0.21057 | 0.11902 | 0.10986 | -122.2275 | 0.11902 | 0.11902 | 0.15564 | -122.3328 | 0.082398 | 0.068665 | 0.2243 | -122.287
3818.6875 | 122.3648 | -0.091553 | 122.287 | -0.21088 | 0.049759 | 0.060968 | 0.0036145 | 0.030397 | -0.0036722 | 0.030006 | -0.24536 | 0.029615 | 0.038805 | 0.049242 | -0.0017453 | 0.027359 | 0.013733 | -0.009155 | -0.027466 | -0.027466 | 0.11444 | 0.004578 | -0.11902 | 0.032043 | 0.032043 | -0.091553 | 0.073242 | 0.054932 | -0.050354 | -0.10986 | 0.096131 | -0.027466 | -122.1725 | 0.082398 | 0.064087 | 0.091553 | -122.2733 | 0.041199 | -0.01831 | -122.2137 | 0.1236 | 0 | 0.01831 | -122.2321 | 0.20599 | 0.10529 | 0.064087 | -122.406 | 0.16479 | 0.14649 | 0.1236 | -122.3969
3820.3906 | 122.3511 | -0.10071 | 122.2916 | 0.025635 | 0.04805 | 0.059473 | -1.7146e-05 | 0.029115 | 0.0010276 | 0.031501 | -0.024109 | 0.030255 | 0.036882 | 0.048815 | 0.0044497 | 0.026504 | -0.013733 | -0.032043 | -0.050354 | -0.004578 | 0.086975 | 0.009155 | -0.12817 | 0.027466 | -0.027466 | -0.10529 | 0.064087 | 0.045776 | -0.050354 | -0.10986 | 0.10986 | -0.027466 | -122.2046 | 0.068665 | 0.09613 | 0.1236 | -122.3053 | 0.050354 | -0.009155 | -122.2275 | 0.12817 | -0.004578 | 0.004577 | -122.2458 | 0.18768 | 0.086975 | 0.050354 | -122.4197 | 0.1648 | 0.14648 | 0.073242 | -122.4014
3822.1719 | 122.3328 | -0.082397 | 122.2733 | -0.18036 | 0.04805 | 0.061823 | 0.0036145 | 0.031678 | -0.0045266 | 0.031714 | -0.22247 | 0.025769 | 0.037523 | 0.04732 | 0.00017731 | 0.030136 | 0.064087 | 0.1236 | 0.10071 | 0.054932 | 0.068665 | 0.041199 | -0.09613 | 0.09613 | 0.13275 | 0 | 0.032043 | 0.032043 | -0.032043 | -0.091553 | 0.1236 | -0.013733 | -122.2046 | 0.20599 | 0.13733 | 0.15106 | -122.2092 | 0.050354 | -0.009156 | -122.2412 | 0.17853 | 0.082397 | 0.091553 | -122.2412 | 0.15106 | 0.14648 | 0.18311 | -122.3694 | 0.11444 | 0.11444 | 0.21515 | -122.3648
3823.9375 | 122.3923 | -0.091553 | 122.2641 | -0.24902 | 0.046128 | 0.059045 | 0.0044691 | 0.029969 | -0.0017496 | 0.029792 | -0.22247 | 0.026837 | 0.035814 | 0.047747 | 0.0012455 | 0.025863 | -0.004578 | -0.004578 | -0.022888 | 0 | 0.10071 | 0.013733 | -0.12817 | 0.032043 | 0.050354 | -0.086975 | 0.059509 | 0.064087 | -0.041199 | -0.11444 | 0.10529 | -0.036621 | -122.1634 | 0.086975 | 0.091553 | 0.12817 | -122.2687 | 0.050354 | -0.022888 | -122.2046 | 0.1236 | 0.004578 | 0.027466 | -122.2 | 0.19226 | 0.086975 | 0.068665 | -122.3923 | 0.15106 | 0.15564 | 0.14191 | -122.3785
3825.7031 | 122.3557 | -0.10529 | 122.2687 | -0.18799 | 0.046982 | 0.061182 | 0.0057507 | 0.031251 | -0.0047404 | 0.028083 | -0.20721 | 0.02641 | 0.037523 | 0.047747 | -0.0021725 | 0.028213 | 0.054932 | 0.10071 | 0.086975 | 0.073242 | 0.068665 | 0.032043 | -0.1236 | 0.073242 | 0.10986 | -0.022888 | 0.045776 | 0.036621 | -0.032043 | -0.091553 | 0.13733 | -0.01831 | -122.2 | 0.20599 | 0.17853 | 0.19684 | -122.2137 | 0.073243 | 0.013733 | -122.2229 | 0.17853 | 0.082398 | 0.068665 | -122.2321 | 0.17395 | 0.16022 | 0.19226 | -122.3923 | 0.15106 | 0.14191 | 0.21515 | -122.3602
3827.4219 | 122.4106 | -0.07782 | 122.2916 | -0.20325 | 0.043991 | 0.060754 | 0.0055371 | 0.031892 | -0.0087992 | 0.031714 | -0.14618 | 0.024915 | 0.038377 | 0.048815 | -0.0025999 | 0.029281 | 0.07782 | 0.13275 | 0.1236 | 0.073242 | 0.050354 | 0.068665 | -0.091553 | 0.14191 | 0.16479 | 0.041199 | 0.013733 | 0.004578 | -0.013733 | -0.064087 | 0.14649 | -0.013733 | -122.2412 | 0.21057 | 0.15106 | 0.16479 | -122.2137 | 0.064087 | 0.013733 | -122.2778 | 0.21973 | 0.11902 | 0.10529 | -122.287 | 0.12817 | 0.15564 | 0.20142 | -122.3831 | 0.091553 | 0.082398 | 0.24261 | -122.3557
3829.1875 | 122.3831 | -0.086975 | 122.2778 | -0.18799 | 0.047409 | 0.058618 | 0.0012647 | 0.032746 | 0.0014548 | 0.029578 | -0.20721 | 0.028974 | 0.034318 | 0.050524 | 0.0012455 | 0.026718 | 0.036621 | 0.022888 | 0 | 0.036621 | 0.10071 | 0.013733 | -0.13733 | 0.073242 | 0.059509 | -0.064087 | 0.064087 | 0.059509 | -0.050354 | -0.10071 | 0.10071 | -0.050354 | -122.1771 | 0.10986 | 0.1236 | 0.17395 | -122.2412 | 0.036621 | -0.013733 | -122.2137 | 0.16022 | 0.022888 | 0.036621 | -122.2183 | 0.18768 | 0.1236 | 0.086975 | -122.4152 | 0.15106 | 0.14648 | 0.14648 | -122.3785
3830.9531 | 122.3969 | -0.082397 | 122.2733 | -0.20325 | 0.04506 | 0.060541 | -0.00023075 | 0.031037 | -0.0011088 | 0.031074 | -0.19958 | 0.029401 | 0.037096 | 0.050524 | 0.0029543 | 0.027359 | 0.027466 | 0.013733 | -0.004578 | 0.027466 | 0.091553 | 0.018311 | -0.15106 | 0.064087 | 0.082397 | -0.050354 | 0.059509 | 0.054932 | -0.050354 | -0.09613 | 0.10071 | -0.068665 | -122.1817 | 0.09613 | 0.10986 | 0.17853 | -122.2458 | 0.032043 | -0.013733 | -122.2137 | 0.14648 | 0.032043 | 0.045776 | -122.2183 | 0.17395 | 0.10986 | 0.077819 | -122.4243 | 0.14191 | 0.13733 | 0.16479 | -122.3694
3832.7344 | 122.4197 | -0.059509 | 122.2549 | 0.10193 | 0.044846 | 0.0599 | 0.0010511 | 0.03061 | -0.006022 | 0.030219 | 0.159 | 0.026624 | 0.036882 | 0.047106 | 0.00017731 | 0.027999 | 0.064087 | 0.10071 | 0.086975 | 0.059509 | 0.041199 | 0.050354 | -0.091553 | 0.11444 | 0.09613 | 0.018311 | 0.009155 | 0 | -0.027466 | -0.086975 | 0.10986 | -0.032044 | -122.2137 | 0.16022 | 0.11902 | 0.15106 | -122.1909 | 0.032043 | -0.027466 | -122.2458 | 0.17395 | 0.07782 | 0.10529 | -122.2549 | 0.10071 | 0.1236 | 0.14648 | -122.3465 | 0.068664 | 0.059509 | 0.15564 | -122.3419
3834.5 | 122.3511 | -0.10071 | 122.2733 | -0.18036 | 0.044632 | 0.061823 | 0.0025465 | 0.029115 | -0.0068766 | 0.028297 | -0.16144 | 0.026837 | 0.037096 | 0.046465 | 0.00039091 | 0.027999 | 0.068665 | 0.11444 | 0.091553 | 0.068665 | 0.054932 | 0.036621 | -0.086975 | 0.10071 | 0.14191 | 0.027466 | 0.027466 | 0.032043 | -0.050354 | -0.082397 | 0.13733 | 0.013733 | -122.2183 | 0.21515 | 0.16937 | 0.15564 | -122.2046 | 0.050354 | 0.018311 | -122.2458 | 0.20142 | 0.12817 | 0.10986 | -122.2412 | 0.15564 | 0.16937 | 0.19226 | -122.3602 | 0.12817 | 0.13275 | 0.24262 | -122.3557
3836.2656 | 122.3328 | -0.082397 | 122.2641 | -0.096436 | 0.050827 | 0.060968 | 0.0038281 | 0.029969 | 0.00017302 | 0.03086 | -0.12329 | 0.029401 | 0.033464 | 0.049669 | 0.0029543 | 0.02565 | 0.082397 | 0.054932 | 0.022888 | 0.036621 | 0.09613 | 0.027466 | -0.1236 | 0.082397 | 0.091553 | -0.054932 | 0.054932 | 0.032043 | -0.032043 | -0.082397 | 0.10986 | -0.041199 | -122.168 | 0.13733 | 0.11902 | 0.16022 | -122.1817 | 0.050354 | 0 | -122.2092 | 0.16479 | 0.027465 | 0.027465 | -122.2321 | 0.17853 | 0.16479 | 0.10528 | -122.3877 | 0.13733 | 0.11444 | 0.17395 | -122.3465
3838.0312 | 122.5021 | -0.054932 | 122.2595 | -0.050659 | 0.043778 | 0.060327 | 0.0046827 | 0.031037 | -0.011149 | 0.031287 | -0.031738 | 0.026837 | 0.03795 | 0.047961 | -0.0032407 | 0.029068 | 0.045776 | 0.086975 | 0.082397 | 0.050354 | 0.068665 | 0.045776 | -0.086975 | 0.13275 | 0.16022 | 0.059509 | 0.022888 | 0.013733 | -0.013733 | -0.091553 | 0.10071 | -0.032043 | -122.1909 | 0.14191 | 0.10529 | 0.13733 | -122.2137 | 0.041199 | -0.036621 | -122.2366 | 0.18768 | 0.11444 | 0.15106 | -122.2458 | 0.1236 | 0.10071 | 0.13733 | -122.3465 | 0.07782 | 0.068665 | 0.21515 | -122.3511
3839.7344 | 122.4747 | -0.045776 | 122.2412 | 0.15533 | 0.048691 | 0.057336 | -0.0010851 | 0.029969 | -0.001536 | 0.030219 | 0.12085 | 0.027265 | 0.036241 | 0.048815 | 0.0033817 | 0.024795 | 0.059509 | 0.036621 | 0.022888 | 0.027466 | 0.082397 | 0.041199 | -0.082397 | 0.11902 | 0.091553 | 0 | 0.027466 | 0.004578 | -0.009155 | -0.073242 | 0.086975 | -0.036621 | -122.1588 | 0.082397 | 0.073242 | 0.10986 | -122.1817 | 0.036621 | -0.027466 | -122.2137 | 0.16479 | 0.045776 | 0.073242 | -122.2366 | 0.12817 | 0.10528 | 0.068664 | -122.3236 | 0.073242 | 0.050354 | 0.13733 | -122.3145
3841.4844 | 122.4243 | -0.068665 | 122.2458 | 0.071411 | 0.04036 | 0.06225 | 0.0012647 | 0.029328 | -0.0079446 | 0.02851 | 0.11322 | 0.025769 | 0.034532 | 0.049669 | 0.0031681 | 0.030777 | 0.041199 | 0.086975 | 0.068665 | 0.027466 | 0.041199 | 0.045776 | -0.073242 | 0.10986 | 0.091553 | 0.004578 | 0.036621 | 0.022888 | -0.022888 | -0.068665 | 0.11444 | -0.004577 | -122.2046 | 0.15564 | 0.096131 | 0.10071 | -122.2046 | 0.045777 | 0 | -122.2092 | 0.17853 | 0.073243 | 0.073243 | -122.2229 | 0.10986 | 0.10986 | 0.13733 | -122.319 | 0.10529 | 0.091553 | 0.16022 | -122.3145
3843.25 | 122.4335 | -0.064087 | 122.2275 | 0.14771 | 0.047623 | 0.060114 | 0.0016919 | 0.030397 | -0.0021768 | 0.032996 | 0.159 | 0.027265 | 0.036241 | 0.049029 | 0.0031681 | 0.030777 | 0.09613 | 0.12817 | 0.10986 | 0.082397 | 0.059509 | 0.059509 | -0.09613 | 0.16022 | 0.14191 | 0.041199 | 0.009155 | -0.018311 | -0.004578 | -0.068665 | 0.1236 | -0.032043 | -122.168 | 0.19226 | 0.14648 | 0.17853 | -122.1313 | 0.059509 | -0.004578 | -122.2183 | 0.2243 | 0.10529 | 0.10986 | -122.2458 | 0.1236 | 0.16022 | 0.17395 | -122.3236 | 0.073242 | 0.045776 | 0.20599 | -122.2961
3845.0156 | 122.3923 | -0.07782 | 122.2687 | -0.23376 | 0.048477 | 0.061182 | 0.0053235 | 0.03061 | -0.00068138 | 0.030219 | -0.22247 | 0.02876 | 0.03795 | 0.05031 | 0.00081811 | 0.02565 | 0.013733 | -0.004578 | -0.013733 | -0.018311 | 0.10071 | 0.018311 | -0.15106 | 0.041199 | 0.041199 | -0.091553 | 0.050354 | 0.032043 | -0.054932 | -0.10071 | 0.096131 | -0.073242 | -122.168 | 0.073242 | 0.059509 | 0.13275 | -122.2549 | 0.022888 | -0.022888 | -122.2183 | 0.11902 | -0.013733 | 0.009155 | -122.2366 | 0.17853 | 0.091553 | 0.064087 | -122.4197 | 0.12817 | 0.10986 | 0.11902 | -122.3694
3846.7188 | 122.3877 | -0.091553 | 122.2824 | -0.18036 | 0.044846 | 0.062463 | 0.0023329 | 0.03061 | -0.00089518 | 0.031287 | -0.21484 | 0.028119 | 0.039018 | 0.049242 | -3.629e-05 | 0.026291 | 0 | 0.004578 | -0.032043 | 0.009155 | 0.091553 | 0.013733 | -0.13275 | 0.041199 | 0.054932 | -0.07782 | 0.054932 | 0.041199 | -0.059509 | -0.11444 | 0.10529 | -0.041198 | -122.1909 | 0.096131 | 0.10071 | 0.14191 | -122.2824 | 0.032044 | -0.022888 | -122.2275 | 0.13275 | 0.013733 | 0.036621 | -122.2412 | 0.18311 | 0.091553 | 0.05951 | -122.4152 | 0.14649 | 0.13275 | 0.14649 | -122.3969
3848.4844 | 122.4472 | -0.059509 | 122.2778 | 0.010376 | 0.044205 | 0.059686 | 0.0072461 | 0.029542 | -0.0090128 | 0.032142 | 0.075073 | 0.027478 | 0.035387 | 0.048388 | -0.0013181 | 0.029281 | 0.027466 | 0.050354 | 0.054932 | 0.032043 | 0.064087 | 0.045776 | -0.10986 | 0.07782 | 0.07782 | 0 | 0.032043 | 0.032043 | -0.027466 | -0.07782 | 0.10528 | -0.050354 | -122.2137 | 0.10986 | 0.091552 | 0.14191 | -122.2504 | 0.032043 | -0.018311 | -122.2458 | 0.13733 | 0.059509 | 0.07782 | -122.2458 | 0.1236 | 0.086975 | 0.11444 | -122.3877 | 0.091552 | 0.091552 | 0.13733 | -122.3557
3850.1719 | 122.3602 | -0.10071 | 122.2916 | -0.25665 | 0.049332 | 0.058832 | 0.0044691 | 0.029328 | -0.0045266 | 0.027228 | -0.19196 | 0.027478 | 0.036668 | 0.05031 | -0.00089089 | 0.027786 | 0.059509 | 0.050354 | 0.041199 | 0.036621 | 0.064087 | 0.013733 | -0.13275 | 0.045776 | 0.07782 | -0.064087 | 0.050354 | 0.032043 | -0.050354 | -0.10529 | 0.11444 | -0.032043 | -122.2275 | 0.15106 | 0.13733 | 0.16937 | -122.2321 | 0.050354 | -0.004578 | -122.2412 | 0.14648 | 0.036621 | 0.041199 | -122.2595 | 0.1648 | 0.16022 | 0.14191 | -122.4243 | 0.15106 | 0.13275 | 0.17853 | -122.3969
3851.9375 | 122.3923 | -0.091553 | 122.2916 | -0.17273 | 0.045914 | 0.060327 | 0.00083745 | 0.03061 | -0.00046778 | 0.031714 | -0.26062 | 0.028333 | 0.036241 | 0.047533 | 0.0010317 | 0.025009 | 0.022888 | 0.009155 | -0.009155 | 0.013733 | 0.10071 | 0.018311 | -0.14191 | 0.041199 | 0.064087 | -0.064087 | 0.064087 | 0.045776 | -0.059509 | -0.09613 | 0.10986 | -0.050354 | -122.1909 | 0.10071 | 0.10529 | 0.15564 | -122.2687 | 0.032044 | -0.004577 | -122.2275 | 0.13275 | 0.027466 | 0.032043 | -122.2458 | 0.19226 | 0.11444 | 0.082398 | -122.4335 | 0.15564 | 0.13733 | 0.15564 | -122.3877
3853.7031 | 122.438 | -0.068665 | 122.2824 | 0.094299 | 0.04805 | 0.05755 | 0.0014783 | 0.029969 | -0.006022 | 0.030646 | 0.13611 | 0.026837 | 0.035173 | 0.049029 | -0.0019589 | 0.029708 | 0.09613 | 0.11444 | 0.10529 | 0.064087 | 0.036621 | 0.059509 | -0.086975 | 0.14648 | 0.11444 | 0.027466 | 0.032043 | -0.004578 | -0.004578 | -0.045776 | 0.12817 | -0.01831 | -122.2458 | 0.18311 | 0.13275 | 0.15106 | -122.1863 | 0.064087 | 0.022889 | -122.2504 | 0.21515 | 0.096131 | 0.073242 | -122.287 | 0.10529 | 0.16479 | 0.17395 | -122.3694 | 0.10071 | 0.064087 | 0.18311 | -122.3282
3855.4531 | 122.3923 | -0.09613 | 122.2687 | -0.19562 | 0.049118 | 0.060327 | 0.0061781 | 0.032746 | -0.0073038 | 0.030006 | -0.13855 | 0.024915 | 0.036241 | 0.051806 | -0.0011045 | 0.028427 | 0.10529 | 0.1236 | 0.1236 | 0.054932 | 0.045776 | 0.041199 | -0.09613 | 0.13275 | 0.17395 | 0.045776 | 0.013733 | 0.027466 | 0.004578 | -0.054932 | 0.13733 | 0 | -122.2229 | 0.21973 | 0.15106 | 0.15106 | -122.1634 | 0.10071 | 0.041198 | -122.2549 | 0.22888 | 0.14191 | 0.10071 | -122.2412 | 0.14191 | 0.20142 | 0.21973 | -122.3648 | 0.10986 | 0.1236 | 0.27008 | -122.3236
3857.1719 | 122.3831 | -0.086975 | 122.2824 | -0.15747 | 0.048691 | 0.057977 | 0.0031873 | 0.030397 | -0.00025418 | 0.02851 | -0.23773 | 0.029401 | 0.036027 | 0.052019 | -0.00067729 | 0.025436 | 0.013733 | -0.013733 | -0.018311 | 0.013733 | 0.091553 | 0.013733 | -0.15106 | 0.022888 | 0.050354 | -0.07782 | 0.068665 | 0.041199 | -0.041199 | -0.091553 | 0.10071 | -0.064087 | -122.1909 | 0.073242 | 0.10071 | 0.16479 | -122.2687 | 0.045776 | -0.004578 | -122.2137 | 0.10986 | 0.009155 | 0.013733 | -122.2412 | 0.17853 | 0.10071 | 0.068664 | -122.4335 | 0.15564 | 0.12817 | 0.13733 | -122.374
3858.9375 | 122.4289 | -0.064087 | 122.2366 | 0.063782 | 0.043991 | 0.061182 | -1.7146e-05 | 0.031037 | -0.0079446 | 0.028937 | 0.067444 | 0.027265 | 0.034532 | 0.049456 | -0.0017453 | 0.02864 | 0.050354 | 0.07782 | 0.064087 | 0.032043 | 0.036621 | 0.045776 | -0.09613 | 0.10986 | 0.086975 | 0 | 0.032043 | 0.027466 | -0.022888 | -0.07782 | 0.10986 | -0.032043 | -122.2 | 0.14191 | 0.09613 | 0.12817 | -122.1863 | 0.041199 | -0.013733 | -122.2046 | 0.17395 | 0.064087 | 0.07782 | -122.2092 | 0.10071 | 0.11444 | 0.12817 | -122.3328 | 0.09613 | 0.091553 | 0.15106 | -122.3145
3860.6875 | 122.4518 | -0.054932 | 122.2549 | 0.010376 | 0.042496 | 0.063318 | 0.00083745 | 0.029756 | -0.0051676 | 0.030646 | 0.029297 | 0.027478 | 0.035814 | 0.047747 | -0.0019589 | 0.027786 | 0.032043 | 0.059509 | 0.050354 | 0.027466 | 0.054932 | 0.050354 | -0.10071 | 0.082397 | 0.082397 | 0.004578 | 0.027466 | 0.013733 | -0.022888 | -0.07782 | 0.10529 | -0.045776 | -122.2 | 0.11444 | 0.082398 | 0.12817 | -122.2229 | 0.032044 | -0.022888 | -122.2275 | 0.13733 | 0.05951 | 0.082398 | -122.2412 | 0.10986 | 0.086975 | 0.10529 | -122.3557 | 0.082398 | 0.068665 | 0.13733 | -122.3328
3862.3906 | 122.3511 | -0.11444 | 122.2778 | -0.22614 | 0.050827 | 0.058832 | 0.0057507 | 0.030183 | -0.0045266 | 0.029792 | -0.23773 | 0.027051 | 0.03795 | 0.048601 | 0.00017731 | 0.027786 | 0.073242 | 0.082397 | 0.064087 | 0.050354 | 0.064087 | 0.045776 | -0.10529 | 0.064087 | 0.073242 | -0.050354 | 0.059509 | 0.054932 | -0.036621 | -0.086975 | 0.16022 | 0.009155 | -122.2137 | 0.19684 | 0.16479 | 0.15564 | -122.2046 | 0.07782 | 0.027466 | -122.2183 | 0.17853 | 0.064087 | 0.036621 | -122.2229 | 0.17853 | 0.18768 | 0.17853 | -122.3831 | 0.17395 | 0.16937 | 0.18768 | -122.3648
3864.1562 | 122.319 | -0.11902 | 122.2641 | -0.012512 | 0.049759 | 0.058618 | 0.0034009 | 0.029328 | 0.0040182 | 0.031074 | -0.039368 | 0.027906 | 0.036241 | 0.05031 | 0.0042361 | 0.026077 | 0.041199 | -0.004578 | -0.018311 | -0.009155 | 0.091553 | 0.018311 | -0.15106 | 0.050354 | 0.009155 | -0.11902 | 0.059509 | 0.045776 | -0.068665 | -0.091553 | 0.13733 | -0.032043 | -122.1725 | 0.11444 | 0.10986 | 0.14191 | -122.2229 | 0.050354 | 0.027466 | -122.2046 | 0.16937 | 0 | -0.027466 | -122.2183 | 0.21057 | 0.16022 | 0.10071 | -122.4152 | 0.17853 | 0.16479 | 0.12817 | -122.3557
3865.8594 | 122.4197 | -0.068665 | 122.2549 | 0.010376 | 0.043137 | 0.062036 | 0.0016919 | 0.029542 | -0.0062356 | 0.030433 | 0.067444 | 0.026624 | 0.037096 | 0.04732 | -0.0011045 | 0.028854 | 0.032043 | 0.07782 | 0.073242 | 0.032043 | 0.050354 | 0.032043 | -0.091553 | 0.10529 | 0.082397 | 0.004578 | 0.022888 | 0.004578 | -0.018311 | -0.091553 | 0.10071 | -0.022888 | -122.2046 | 0.14649 | 0.10071 | 0.1236 | -122.2229 | 0.050354 | -0.022888 | -122.2321 | 0.17395 | 0.073243 | 0.096131 | -122.2504 | 0.11902 | 0.10071 | 0.14191 | -122.3465 | 0.091553 | 0.073243 | 0.15106 | -122.3465
3867.6406 | 122.4518 | -0.064087 | 122.2412 | 0.063782 | 0.049118 | 0.059473 | 0.0012647 | 0.029756 | -0.00025418 | 0.029365 | 0.044556 | 0.027906 | 0.0356 | 0.049456 | 0.0040225 | 0.027999 | 0.013733 | -0.013733 | -0.022888 | -0.004578 | 0.09613 | 0.022888 | -0.1236 | 0.059509 | 0.013733 | -0.07782 | 0.059509 | 0.022888 | -0.059509 | -0.09613 | 0.086975 | -0.059509 | -122.1451 | 0.050354 | 0.059509 | 0.11902 | -122.2275 | 0.004578 | -0.032043 | -122.1817 | 0.1236 | -0.013733 | 0.01831 | -122.2183 | 0.16022 | 0.07782 | 0.041199 | -122.3648 | 0.1236 | 0.086975 | 0.07782 | -122.3373
3869.4219 | 122.3465 | -0.10529 | 122.2687 | -0.0048827 | 0.049118 | 0.059473 | 0.00083745 | 0.031465 | 0.0012412 | 0.031074 | -0.016479 | 0.030042 | 0.035173 | 0.048388 | 0.0046633 | 0.029068 | 0.032043 | -0.009155 | -0.027466 | -0.013733 | 0.07782 | 0.009155 | -0.13275 | 0.009155 | 0 | -0.11444 | 0.068665 | 0.045776 | -0.068665 | -0.10071 | 0.11444 | -0.027465 | -122.1909 | 0.096131 | 0.091553 | 0.11902 | -122.2366 | 0.036621 | 0.004578 | -122.2 | 0.11444 | -0.009155 | -0.013733 | -122.2229 | 0.18311 | 0.13733 | 0.07782 | -122.4014 | 0.17395 | 0.15106 | 0.10529 | -122.3694
3871.1875 | 122.4289 | -0.082397 | 122.2687 | 0.094299 | 0.048264 | 0.060754 | 0.0034009 | 0.030824 | 0.00017302 | 0.031501 | 0.044556 | 0.027692 | 0.036882 | 0.050097 | -3.629e-05 | 0.027999 | -0.009155 | -0.027466 | -0.032043 | -0.022888 | 0.091553 | 0.009155 | -0.13733 | 0.041199 | 0.009155 | -0.082397 | 0.059509 | 0.059509 | -0.054932 | -0.10071 | 0.091552 | -0.054932 | -122.1771 | 0.054931 | 0.059509 | 0.11444 | -122.2778 | 0.027465 | -0.018311 | -122.2092 | 0.1236 | 0 | 0.018311 | -122.2092 | 0.17395 | 0.073242 | 0.050354 | -122.406 | 0.14191 | 0.14191 | 0.091552 | -122.3694
3872.8906 | 122.3419 | -0.09613 | 122.2778 | -0.088806 | 0.046982 | 0.062036 | 0.0038281 | 0.028688 | -0.0023904 | 0.03086 | -0.10803 | 0.027478 | 0.036027 | 0.049029 | 0.0012455 | 0.026931 | 0.068665 | 0.068665 | 0.022888 | 0.036621 | 0.082397 | 0.036621 | -0.11902 | 0.064087 | 0.073242 | -0.050354 | 0.054932 | 0.050354 | -0.045776 | -0.10071 | 0.13275 | -0.022889 | -122.1954 | 0.16479 | 0.13275 | 0.15564 | -122.2092 | 0.050354 | -0.004578 | -122.2229 | 0.16022 | 0.045776 | 0.050354 | -122.2275 | 0.17853 | 0.16479 | 0.11902 | -122.3969 | 0.15106 | 0.14648 | 0.16937 | -122.3785
3874.6406 | 122.3511 | -0.086975 | 122.2824 | -0.012512 | 0.047623 | 0.060754 | -1.7146e-05 | 0.030183 | -0.0011088 | 0.034278 | 0.0064086 | 0.030042 | 0.037096 | 0.048388 | 0.0033817 | 0.030136 | -0.009155 | -0.027466 | -0.036621 | -0.013733 | 0.091553 | 0.022888 | -0.12817 | -0.009155 | 0 | -0.11902 | 0.041199 | 0.054932 | -0.064087 | -0.11444 | 0.10986 | -0.041199 | -122.1909 | 0.059509 | 0.073242 | 0.11444 | -122.2916 | 0.022888 | -0.027466 | -122.2412 | 0.07782 | -0.032044 | -0.004578 | -122.2275 | 0.17853 | 0.07782 | 0.050354 | -122.4106 | 0.12817 | 0.14191 | 0.086975 | -122.3969
3876.3281 | 122.4152 | -0.059509 | 122.2321 | 0.025635 | 0.043564 | 0.06225 | 0.0038281 | 0.030397 | -0.008372 | 0.029151 | 0.12085 | 0.025983 | 0.035387 | 0.04732 | -0.0015317 | 0.032486 | 0.009155 | 0.086975 | 0.073242 | 0.032043 | 0.059509 | 0.036621 | -0.10986 | 0.086975 | 0.091553 | 0.013733 | 0.022888 | 0.022888 | -0.027466 | -0.086975 | 0.09613 | -0.050354 | -122.1725 | 0.14648 | 0.091552 | 0.14191 | -122.2229 | 0.032043 | -0.027466 | -122.2092 | 0.14648 | 0.073242 | 0.10071 | -122.2092 | 0.11902 | 0.068664 | 0.13275 | -122.3419 | 0.082397 | 0.082397 | 0.15106 | -122.319
3878.0938 | 122.4564 | -0.07782 | 122.2458 | 0.10956 | 0.046341 | 0.059045 | 0.0036145 | 0.028047 | -0.0023904 | 0.031501 | 0.052185 | 0.030042 | 0.036668 | 0.050097 | 0.0016727 | 0.027999 | 0 | -0.022888 | -0.032043 | -0.009155 | 0.086975 | 0.009155 | -0.12817 | 0.050354 | 0.009155 | -0.082397 | 0.059509 | 0.032043 | -0.045776 | -0.09613 | 0.086975 | -0.050354 | -122.1588 | 0.054932 | 0.068665 | 0.11902 | -122.2458 | 0.032044 | -0.01831 | -122.1863 | 0.12817 | -0.004577 | 0.013733 | -122.2137 | 0.16479 | 0.07782 | 0.045777 | -122.374 | 0.13733 | 0.10986 | 0.086975 | -122.3419
3879.8438 | 122.4701 | -0.045776 | 122.2366 | 0.16296 | 0.043991 | 0.061609 | 0.0014783 | 0.028901 | -0.0036722 | 0.031287 | 0.39551 | 0.028974 | 0.036241 | 0.049883 | 0.0012455 | 0.026931 | 0.054932 | 0.059509 | 0.064087 | 0.050354 | 0.068665 | 0.045776 | -0.10071 | 0.12817 | 0.1236 | 0.036621 | 0.045776 | 0.009155 | -0.004578 | -0.041199 | 0.091552 | -0.054932 | -122.168 | 0.10528 | 0.09613 | 0.15106 | -122.1817 | 0.041198 | 0.004577 | -122.1909 | 0.17395 | 0.082397 | 0.07782 | -122.2275 | 0.11444 | 0.10071 | 0.10986 | -122.3373 | 0.091552 | 0.054931 | 0.16937 | -122.2778
3881.5938 | 122.4655 | -0.059509 | 122.2366 | 0.056152 | 0.0457 | 0.061182 | -0.00023075 | 0.030824 | -0.004313 | 0.033423 | 0.12848 | 0.027051 | 0.034532 | 0.047106 | 0.0027407 | 0.029495 | 0.068665 | 0.10986 | 0.07782 | 0.091553 | 0.059509 | 0.036621 | -0.086975 | 0.13275 | 0.13733 | 0.036621 | 0.018311 | 0.009155 | -0.022888 | -0.059509 | 0.09613 | -0.027466 | -122.1771 | 0.16937 | 0.15106 | 0.17853 | -122.168 | 0.036621 | 0 | -122.2183 | 0.19226 | 0.09613 | 0.09613 | -122.2275 | 0.11902 | 0.12817 | 0.13733 | -122.3236 | 0.07782 | 0.068664 | 0.19684 | -122.2961
3883.2969 | 122.4197 | -0.041199 | 122.2229 | 0.13245 | 0.04506 | 0.060114 | 0.0012647 | 0.027833 | -0.0047404 | 0.030433 | 0.14374 | 0.025556 | 0.034959 | 0.046038 | 0.0020999 | 0.030349 | 0.073242 | 0.1236 | 0.10986 | 0.073242 | 0.054932 | 0.073242 | -0.073242 | 0.14191 | 0.1236 | 0.050354 | 0.022888 | 0 | -0.018311 | -0.07782 | 0.11444 | -0.032043 | -122.168 | 0.16479 | 0.11444 | 0.14648 | -122.1497 | 0.022888 | -0.036621 | -122.2 | 0.18311 | 0.091553 | 0.12817 | -122.2229 | 0.096131 | 0.11444 | 0.15106 | -122.2961 | 0.064087 | 0.041199 | 0.16479 | -122.3007
3885.0469 | 122.3648 | -0.091553 | 122.2733 | -0.21088 | 0.045273 | 0.060541 | 0.0087415 | 0.030183 | -0.008372 | 0.031074 | -0.13092 | 0.026837 | 0.0356 | 0.047106 | -0.0051633 | 0.026718 | 0.086975 | 0.11902 | 0.10529 | 0.07782 | 0.050354 | 0.036621 | -0.10986 | 0.11444 | 0.16022 | 0.036621 | 0.018311 | 0.032043 | -0.022888 | -0.07782 | 0.12817 | -0.01831 | -122.2229 | 0.21057 | 0.16937 | 0.18768 | -122.1863 | 0.068665 | 0.013733 | -122.2549 | 0.20599 | 0.12817 | 0.11444 | -122.2412 | 0.14191 | 0.17853 | 0.19684 | -122.3831 | 0.10986 | 0.1236 | 0.25177 | -122.3511
3886.8125 | 122.3282 | -0.10071 | 122.2778 | -0.065918 | 0.048477 | 0.059045 | 0.0021191 | 0.029969 | 0.0014548 | 0.030646 | -0.092773 | 0.029615 | 0.039232 | 0.051165 | 0.0031681 | 0.026077 | 0.086975 | 0.036621 | 0.009155 | 0.022888 | 0.073242 | 0.018311 | -0.10986 | 0.07782 | 0.045776 | -0.07782 | 0.050354 | 0.027466 | -0.022888 | -0.10529 | 0.11902 | -0.009155 | -122.2046 | 0.13733 | 0.1236 | 0.13275 | -122.1909 | 0.07782 | -0.004578 | -122.2275 | 0.17853 | 0.022888 | 0.027466 | -122.2504 | 0.17395 | 0.18768 | 0.10986 | -122.3877 | 0.15106 | 0.12817 | 0.14648 | -122.3831
3888.5781 | 122.3465 | -0.11444 | 122.2504 | -0.18799 | 0.046982 | 0.062036 | 0.0076733 | 0.02826 | -0.0068766 | 0.02851 | -0.19958 | 0.026624 | 0.038164 | 0.050097 | -0.0051633 | 0.027786 | 0.082397 | 0.10529 | 0.10071 | 0.073242 | 0.050354 | 0.050354 | -0.09613 | 0.10071 | 0.14648 | 0.018311 | 0.041199 | 0.027466 | -0.041199 | -0.091553 | 0.16479 | 0.018311 | -122.2 | 0.21973 | 0.18768 | 0.16937 | -122.168 | 0.073242 | 0.022888 | -122.2092 | 0.21515 | 0.13275 | 0.10986 | -122.2229 | 0.16479 | 0.19684 | 0.21515 | -122.3465 | 0.15564 | 0.14191 | 0.26093 | -122.3419
3890.3438 | 122.4747 | -0.032043 | 122.2137 | 0.13245 | 0.045914 | 0.0599 | -1.7146e-05 | 0.030824 | -0.003245 | 0.031501 | 0.097962 | 0.026837 | 0.0356 | 0.048388 | 0.0018863 | 0.027786 | 0.068665 | 0.10071 | 0.086975 | 0.045776 | 0.068665 | 0.045776 | -0.086975 | 0.14648 | 0.13275 | 0.036621 | 0 | 0.004578 | -0.013733 | -0.064087 | 0.077819 | -0.054932 | -122.1451 | 0.13275 | 0.077819 | 0.13275 | -122.1451 | 0.01831 | -0.032044 | -122.2137 | 0.17853 | 0.068664 | 0.10071 | -122.2092 | 0.10071 | 0.10071 | 0.11902 | -122.3007 | 0.032043 | 0.036621 | 0.16479 | -122.2778
3892.0469 | 122.4518 | -0.068665 | 122.2229 | 0.079041 | 0.047623 | 0.058618 | 0.00041005 | 0.02826 | -0.0023904 | 0.031714 | 0.067444 | 0.029828 | 0.034959 | 0.049883 | 0.00081811 | 0.027359 | 0.036621 | -0.018311 | -0.032043 | -0.013733 | 0.09613 | -0.009155 | -0.14191 | 0.068665 | 0.013733 | -0.064087 | 0.059509 | 0.036621 | -0.036621 | -0.09613 | 0.05951 | -0.073242 | -122.1268 | 0.050354 | 0.054932 | 0.12817 | -122.1863 | 0.032044 | -0.027465 | -122.1634 | 0.13733 | 0.004578 | 0.032043 | -122.1863 | 0.16479 | 0.10529 | 0.036622 | -122.3648 | 0.12817 | 0.10529 | 0.082398 | -122.319
3893.75 | 122.438 | -0.068665 | 122.2366 | 0.17059 | 0.045914 | 0.059686 | 0.0034009 | 0.028688 | -0.0047404 | 0.03321 | 0.159 | 0.025769 | 0.038377 | 0.049242 | 0.00017731 | 0.027359 | 0.10529 | 0.10529 | 0.11444 | 0.064087 | 0.054932 | 0.054932 | -0.07782 | 0.15106 | 0.13275 | 0.036621 | 0.022888 | 0.022888 | 0.004578 | -0.073242 | 0.1236 | -0.009155 | -122.1817 | 0.17395 | 0.13275 | 0.14191 | -122.1313 | 0.073243 | -0.004577 | -122.2137 | 0.21973 | 0.10529 | 0.10986 | -122.2137 | 0.1236 | 0.17395 | 0.18311 | -122.3145 | 0.091553 | 0.091553 | 0.20142 | -122.3099
3895.5 | 122.3511 | -0.086975 | 122.2549 | 0.033264 | 0.047196 | 0.060968 | 0.00062385 | 0.029328 | -0.00089518 | 0.031074 | 0.029297 | 0.028119 | 0.038377 | 0.049029 | 0.0038089 | 0.027786 | -0.004578 | -0.059509 | -0.045776 | -0.022888 | 0.10071 | 0.013733 | -0.15106 | 0.022888 | -0.022888 | -0.11444 | 0.054932 | 0.041199 | -0.050354 | -0.10529 | 0.10071 | -0.064087 | -122.1542 | 0.027466 | 0.064087 | 0.12817 | -122.2595 | 0.036621 | -0.018311 | -122.2 | 0.10986 | -0.027466 | -0.009155 | -122.2137 | 0.18768 | 0.082397 | 0.041199 | -122.406 | 0.14191 | 0.12817 | 0.064087 | -122.3602
3897.25 | 122.3694 | -0.086975 | 122.2504 | 0.063782 | 0.046555 | 0.060968 | 0.0027601 | 0.029542 | -0.00068138 | 0.030646 | 0.052185 | 0.02876 | 0.036882 | 0.049883 | 0.0038089 | 0.027786 | -0.018311 | -0.032043 | -0.045776 | -0.013733 | 0.086975 | 0.022888 | -0.13733 | 0.036621 | -0.022888 | -0.10529 | 0.064087 | 0.036621 | -0.054932 | -0.10529 | 0.10986 | -0.050354 | -122.1634 | 0.054932 | 0.073242 | 0.1236 | -122.2687 | 0.032043 | -0.018311 | -122.1863 | 0.1236 | -0.018311 | 0 | -122.2137 | 0.17395 | 0.068664 | 0.041199 | -122.3877 | 0.15106 | 0.1236 | 0.064087 | -122.3557
3899.0156 | 122.3969 | -0.082397 | 122.2641 | -0.20325 | 0.046982 | 0.062677 | 0.0044691 | 0.030397 | -0.0045266 | 0.031928 | -0.19196 | 0.028546 | 0.036882 | 0.050097 | -0.00024989 | 0.027999 | -0.009155 | -0.013733 | -0.018311 | 0 | 0.082397 | 0.013733 | -0.13275 | 0.027466 | 0.041199 | -0.086975 | 0.068665 | 0.050354 | -0.059509 | -0.091553 | 0.09613 | -0.050354 | -122.1817 | 0.068664 | 0.082397 | 0.13275 | -122.2733 | 0.022888 | -0.009156 | -122.1954 | 0.10986 | -0.004578 | 0.004578 | -122.2137 | 0.16479 | 0.073242 | 0.064086 | -122.3969 | 0.15106 | 0.13275 | 0.1236 | -122.3557
3900.7656 | 122.3831 | -0.086975 | 122.2549 | -0.18036 | 0.048905 | 0.058405 | 0.0059643 | 0.032319 | -0.00068138 | 0.027869 | -0.21484 | 0.029828 | 0.040941 | 0.050097 | -0.0015317 | 0.027145 | -0.004578 | -0.018311 | -0.013733 | 0.004578 | 0.10071 | 0.022888 | -0.13275 | 0.027466 | 0.050354 | -0.07782 | 0.054932 | 0.050354 | -0.045776 | -0.1236 | 0.10986 | -0.045776 | -122.1542 | 0.068664 | 0.091553 | 0.13733 | -122.2595 | 0.041199 | -0.036621 | -122.2 | 0.11444 | 0.009155 | 0.045776 | -122.2046 | 0.18768 | 0.082397 | 0.073242 | -122.3877 | 0.14191 | 0.13733 | 0.13733 | -122.3785
3902.5312 | 122.4197 | -0.050354 | 122.2733 | 0.048523 | 0.043778 | 0.060114 | 0.0042555 | 0.030824 | -0.0079446 | 0.027656 | 0.11322 | 0.026624 | 0.037736 | 0.047747 | -0.0032407 | 0.03099 | 0.018311 | 0.054932 | 0.064087 | 0.036621 | 0.050354 | 0.045776 | -0.09613 | 0.10071 | 0.091553 | 0.018311 | 0.036621 | 0.018311 | -0.022888 | -0.073242 | 0.09613 | -0.045776 | -122.2229 | 0.10529 | 0.086975 | 0.13275 | -122.2549 | 0.027466 | -0.022888 | -122.2366 | 0.15106 | 0.068665 | 0.091553 | -122.2549 | 0.10071 | 0.068665 | 0.11444 | -122.3694 | 0.086975 | 0.068665 | 0.14191 | -122.3465
3904.2344 | 122.4655 | -0.041199 | 122.2549 | 0.063782 | 0.046768 | 0.057123 | 0.00062385 | 0.029969 | 0.00017302 | 0.029792 | 0.082703 | 0.028546 | 0.035387 | 0.051378 | 0.0023135 | 0.028213 | 0.004578 | -0.022888 | -0.032043 | -0.018311 | 0.10529 | 0.009155 | -0.13733 | 0.064087 | 0.013733 | -0.064087 | 0.059509 | 0.050354 | -0.045776 | -0.086975 | 0.050354 | -0.09613 | -122.1497 | 0.018311 | 0.022888 | 0.11902 | -122.2504 | -0.004577 | -0.045776 | -122.1954 | 0.10529 | -0.022888 | 0.022888 | -122.2046 | 0.14649 | 0.045777 | 0.009156 | -122.3923 | 0.10071 | 0.091553 | 0.054932 | -122.3419
3906 | 122.438 | -0.064087 | 122.2504 | 0.010376 | 0.0457 | 0.061182 | 0.0025465 | 0.031037 | -0.010935 | 0.030006 | 0.052185 | 0.02876 | 0.035814 | 0.048388 | -0.0021725 | 0.030136 | 0.027466 | 0.064087 | 0.045776 | 0.036621 | 0.064087 | 0.032043 | -0.086975 | 0.082397 | 0.086975 | 0.009155 | 0.027466 | 0.018311 | -0.022888 | -0.07782 | 0.09613 | -0.022888 | -122.1863 | 0.12817 | 0.10071 | 0.1236 | -122.2229 | 0.041199 | -0.013733 | -122.2229 | 0.14648 | 0.073242 | 0.086975 | -122.2321 | 0.12817 | 0.091553 | 0.10986 | -122.3373 | 0.091553 | 0.082398 | 0.15106 | -122.3282
3907.7656 | 122.3511 | -0.10986 | 122.3007 | 0.079041 | 0.0504 | 0.060754 | 0.00019645 | 0.030824 | 0.0020956 | 0.030219 | -0.024109 | 0.028119 | 0.037736 | 0.04732 | 0.0027407 | 0.027145 | 0.004578 | -0.036621 | -0.036621 | -0.004578 | 0.086975 | 0.022888 | -0.13275 | 0.004578 | -0.018311 | -0.12817 | 0.07782 | 0.064087 | -0.064087 | -0.10071 | 0.13275 | -0.022888 | -122.2137 | 0.073242 | 0.10529 | 0.12817 | -122.2961 | 0.045776 | 0.009155 | -122.2229 | 0.11444 | -0.018311 | -0.027466 | -122.2366 | 0.19684 | 0.11444 | 0.073242 | -122.4335 | 0.18768 | 0.17395 | 0.091552 | -122.4014
3909.4688 | 122.4289 | -0.050354 | 122.2641 | 0.079041 | 0.043991 | 0.060968 | 0.0016919 | 0.030824 | -0.0064492 | 0.029578 | 0.15137 | 0.02641 | 0.036882 | 0.046892 | 0.0012455 | 0.031204 | 0.064087 | 0.1236 | 0.10529 | 0.059509 | 0.059509 | 0.059509 | -0.082397 | 0.14648 | 0.11902 | 0.027466 | 0 | 0.018311 | -0.022888 | -0.073242 | 0.10986 | -0.032043 | -122.2046 | 0.17395 | 0.10986 | 0.14191 | -122.2 | 0.027466 | -0.022888 | -122.2641 | 0.19684 | 0.07782 | 0.10071 | -122.2458 | 0.10986 | 0.11444 | 0.15564 | -122.3465 | 0.050354 | 0.068665 | 0.16937 | -122.3373
3911.2188 | 122.4197 | -0.068665 | 122.2504 | 0.10193 | 0.043778 | 0.060114 | 0.0014783 | 0.027833 | -0.006663 | 0.02851 | 0.13611 | 0.027692 | 0.036882 | 0.046465 | -0.0023861 | 0.028854 | 0.064087 | 0.10529 | 0.082397 | 0.041199 | 0.045776 | 0.050354 | -0.091553 | 0.10986 | 0.082397 | 0.004578 | 0.027466 | 0.018311 | -0.041199 | -0.086975 | 0.11902 | -0.022888 | -122.2046 | 0.17395 | 0.10986 | 0.13275 | -122.1863 | 0.027466 | -0.01831 | -122.2229 | 0.17853 | 0.073243 | 0.091553 | -122.2321 | 0.11444 | 0.13275 | 0.15106 | -122.3419 | 0.096131 | 0.086976 | 0.15106 | -122.3373
3912.9219 | 122.4701 | -0.041199 | 122.2412 | 0.12482 | 0.046555 | 0.058405 | 0.00062385 | 0.028474 | -0.003245 | 0.029578 | 0.059815 | 0.027906 | 0.035814 | 0.047961 | -3.629e-05 | 0.027145 | 0.07782 | 0.10071 | 0.064087 | 0.050354 | 0.073242 | 0.045776 | -0.10071 | 0.15564 | 0.10071 | 0.009155 | 0.018311 | 0.013733 | -0.022888 | -0.059509 | 0.086975 | -0.059509 | -122.168 | 0.14191 | 0.091553 | 0.15106 | -122.1634 | 0.018311 | -0.01831 | -122.2229 | 0.19684 | 0.050354 | 0.068664 | -122.2275 | 0.11444 | 0.11902 | 0.10529 | -122.3419 | 0.05951 | 0.054932 | 0.14191 | -122.3007
3914.6875 | 122.3511 | -0.10529 | 122.2961 | -0.26428 | 0.047837 | 0.057764 | 0.0034009 | 0.03296 | -0.0034586 | 0.030006 | -0.22247 | 0.02641 | 0.037096 | 0.048815 | -0.0025999 | 0.026931 | 0.050354 | 0.068665 | 0.054932 | 0.041199 | 0.064087 | 0.022888 | -0.11444 | 0.064087 | 0.068665 | -0.059509 | 0.050354 | 0.041199 | -0.045776 | -0.10071 | 0.12817 | -0.009155 | -122.2321 | 0.17395 | 0.14649 | 0.15564 | -122.2458 | 0.05951 | 0.004578 | -122.2458 | 0.16937 | 0.045777 | 0.041199 | -122.2549 | 0.16937 | 0.15564 | 0.16022 | -122.4106 | 0.15564 | 0.14649 | 0.17395 | -122.3969
3916.3906 | 122.4426 | -0.073242 | 122.2458 | 0.033264 | 0.041855 | 0.0599 | 0.0014783 | 0.028901 | -0.0058084 | 0.028724 | 0.067444 | 0.025983 | 0.035387 | 0.047961 | 0.0020999 | 0.029495 | 0.050354 | 0.091553 | 0.059509 | 0.032043 | 0.045776 | 0.045776 | -0.09613 | 0.10986 | 0.082397 | -0.013733 | 0.032043 | 0.018311 | -0.032043 | -0.064087 | 0.11902 | -0.022888 | -122.2 | 0.16479 | 0.10529 | 0.12817 | -122.1954 | 0.041199 | 0.009155 | -122.2137 | 0.18311 | 0.059509 | 0.050354 | -122.2275 | 0.11902 | 0.1236 | 0.13275 | -122.3419 | 0.10529 | 0.091553 | 0.15564 | -122.3099
3918.1562 | 122.3694 | -0.09613 | 122.2595 | -0.14984 | 0.046555 | 0.059259 | 0.00062385 | 0.029756 | -0.0036722 | 0.030006 | -0.23773 | 0.027051 | 0.036455 | 0.046038 | -0.00024989 | 0.028427 | -0.009155 | 0.009155 | -0.004578 | -0.013733 | 0.091553 | 0.009155 | -0.14648 | 0.027466 | 0.054932 | -0.086975 | 0.059509 | 0.032043 | -0.054932 | -0.10529 | 0.10528 | -0.050354 | -122.168 | 0.10528 | 0.082397 | 0.13275 | -122.2687 | 0.041198 | -0.009156 | -122.2 | 0.1236 | 0.009155 | 0.018311 | -122.2275 | 0.18768 | 0.086975 | 0.091552 | -122.406 | 0.15564 | 0.12817 | 0.15106 | -122.3648
3919.9062 | 122.4197 | -0.073242 | 122.2458 | -0.18036 | 0.046341 | 0.062891 | 0.0036145 | 0.029328 | -0.0055948 | 0.028724 | -0.1767 | 0.025128 | 0.034105 | 0.046679 | 0.00017731 | 0.029068 | 0.07782 | 0.15564 | 0.11902 | 0.082397 | 0.041199 | 0.027466 | -0.10071 | 0.13275 | 0.17395 | 0.036621 | 0.022888 | 0.022888 | -0.018311 | -0.07782 | 0.10071 | -0.027466 | -122.2046 | 0.22888 | 0.15564 | 0.18311 | -122.168 | 0.054931 | -0.004578 | -122.2229 | 0.20599 | 0.10986 | 0.11444 | -122.2229 | 0.11444 | 0.15106 | 0.19226 | -122.3465 | 0.09613 | 0.09613 | 0.24719 | -122.3236
3921.6719 | 122.4472 | -0.054932 | 122.2366 | 0.10956 | 0.0457 | 0.057977 | 0.0014783 | 0.029542 | -0.0023904 | 0.03086 | 0.13611 | 0.027051 | 0.034532 | 0.04732 | 0.0010317 | 0.027786 | 0.11444 | 0.11902 | 0.10986 | 0.07782 | 0.045776 | 0.068665 | -0.082397 | 0.16937 | 0.13733 | 0.041199 | 0.022888 | -0.013733 | -0.013733 | -0.050354 | 0.1236 | -0.027465 | -122.1909 | 0.17395 | 0.13275 | 0.16022 | -122.1222 | 0.041199 | 0.004578 | -122.2137 | 0.22431 | 0.096131 | 0.091553 | -122.2504 | 0.10071 | 0.16937 | 0.16479 | -122.319 | 0.07782 | 0.041199 | 0.19226 | -122.287
3923.375 | 122.3785 | -0.10071 | 122.2687 | -0.22614 | 0.0457 | 0.060968 | 0.0057507 | 0.029756 | -0.00068138 | 0.031074 | -0.25299 | 0.029828 | 0.035387 | 0.050738 | -0.00046349 | 0.02864 | 0 | -0.018311 | -0.041199 | -0.004578 | 0.11444 | 0 | -0.15106 | 0.018311 | 0.032043 | -0.091553 | 0.07782 | 0.045776 | -0.068665 | -0.11444 | 0.10071 | -0.050354 | -122.1542 | 0.082397 | 0.09613 | 0.14648 | -122.2687 | 0.032043 | -0.013733 | -122.1909 | 0.11902 | 0.009155 | 0.022888 | -122.2229 | 0.21515 | 0.10071 | 0.059509 | -122.4197 | 0.17853 | 0.14648 | 0.13275 | -122.3831
3925.1406 | 122.3465 | -0.09613 | 122.2778 | 0.063782 | 0.049118 | 0.058618 | 0.0014783 | 0.02826 | 0.0012412 | 0.030433 | -0.024109 | 0.028546 | 0.037096 | 0.049883 | 0.0038089 | 0.027145 | 0 | -0.018311 | -0.036621 | -0.004578 | 0.091553 | 0.013733 | -0.12817 | 0.013733 | -0.004578 | -0.13733 | 0.054932 | 0.054932 | -0.054932 | -0.10071 | 0.10986 | -0.032044 | -122.1863 | 0.077819 | 0.091552 | 0.1236 | -122.2778 | 0.041198 | -0.004578 | -122.2229 | 0.10986 | -0.041199 | -0.036621 | -122.2229 | 0.18768 | 0.09613 | 0.059509 | -122.406 | 0.15106 | 0.15106 | 0.091552 | -122.3785
3926.875 | 122.4792 | -0.050354 | 122.2412 | 0.08667 | 0.0457 | 0.058618 | 0.0031873 | 0.031251 | -0.0021768 | 0.031074 | 0.12085 | 0.027478 | 0.036027 | 0.049242 | 0.0033817 | 0.031417 | 0.013733 | -0.009155 | -0.009155 | -0.004578 | 0.086975 | 0.022888 | -0.1236 | 0.091553 | 0.045776 | -0.045776 | 0.050354 | 0.041199 | -0.032043 | -0.082397 | 0.073242 | -0.073242 | -122.1542 | 0.041199 | 0.045776 | 0.11902 | -122.2275 | 0.018311 | -0.032043 | -122.1909 | 0.14191 | 0.004578 | 0.036621 | -122.2 | 0.13733 | 0.064087 | 0.041199 | -122.3648 | 0.10071 | 0.091553 | 0.09613 | -122.3236
3928.625 | 122.4747 | -0.041199 | 122.2549 | 0.16296 | 0.046768 | 0.059686 | 0.0012647 | 0.029115 | -0.001536 | 0.031074 | 0.4184 | 0.028546 | 0.035173 | 0.047533 | 0.0012455 | 0.029922 | 0.059509 | 0.064087 | 0.059509 | 0.054932 | 0.054932 | 0.041199 | -0.082397 | 0.13275 | 0.11902 | 0.041199 | 0.009155 | 0.022888 | -0.018311 | -0.068665 | 0.082398 | -0.041198 | -122.2 | 0.10529 | 0.096131 | 0.13733 | -122.1954 | 0.022888 | -0.027466 | -122.2458 | 0.17395 | 0.082398 | 0.10986 | -122.2321 | 0.096131 | 0.10071 | 0.10071 | -122.3373 | 0.050354 | 0.064087 | 0.16022 | -122.3236
3930.3906 | 122.4655 | -0.041199 | 122.2549 | -0.088806 | 0.04036 | 0.060754 | 0.0012647 | 0.030397 | -0.011149 | 0.02851 | -0.039368 | 0.024488 | 0.034105 | 0.046679 | -0.0015317 | 0.029708 | 0.064087 | 0.11444 | 0.10071 | 0.073242 | 0.059509 | 0.041199 | -0.09613 | 0.13733 | 0.16479 | 0.073242 | 0.022888 | 0.013733 | -0.018311 | -0.073242 | 0.082398 | -0.054931 | -122.1954 | 0.15564 | 0.11444 | 0.16937 | -122.1909 | 0.022888 | -0.032043 | -122.2321 | 0.17853 | 0.11444 | 0.14648 | -122.2412 | 0.10071 | 0.10529 | 0.14191 | -122.3511 | 0.064087 | 0.054932 | 0.20599 | -122.3282
3932.1562 | 122.4152 | -0.059509 | 122.2549 | -0.18036 | 0.0457 | 0.060754 | 0.0053235 | 0.028474 | -0.0073038 | 0.028937 | -0.16144 | 0.027478 | 0.036668 | 0.046679 | -0.0036679 | 0.029495 | 0.10071 | 0.13275 | 0.11444 | 0.082397 | 0.054932 | 0.041199 | -0.10071 | 0.13275 | 0.16479 | 0.045776 | 0.036621 | 0.022888 | -0.004578 | -0.07782 | 0.10071 | -0.041199 | -122.2 | 0.19226 | 0.14191 | 0.18311 | -122.1542 | 0.054931 | -0.018311 | -122.2183 | 0.19226 | 0.10528 | 0.1236 | -122.2321 | 0.11444 | 0.16022 | 0.17395 | -122.3557 | 0.09613 | 0.082397 | 0.2243 | -122.3328
3933.8594 | 122.5067 | -0.041199 | 122.2641 | -0.073547 | 0.043564 | 0.062036 | 0.00041005 | 0.029542 | -0.0068766 | 0.028937 | -0.077515 | 0.027051 | 0.036668 | 0.046252 | -0.0021725 | 0.029281 | 0.059509 | 0.091553 | 0.082397 | 0.059509 | 0.09613 | 0.041199 | -0.082397 | 0.13733 | 0.14648 | 0.045776 | 0.022888 | 0.018311 | -0.018311 | -0.064087 | 0.082398 | -0.041198 | -122.168 | 0.13275 | 0.10071 | 0.14191 | -122.2046 | 0.022888 | -0.022888 | -122.2412 | 0.17853 | 0.086975 | 0.10986 | -122.2458 | 0.13733 | 0.10071 | 0.1236 | -122.3465 | 0.064087 | 0.05951 | 0.18768 | -122.3282
3935.6094 | 122.3557 | -0.10529 | 122.2824 | -0.088806 | 0.047623 | 0.059259 | 0.0046827 | 0.027192 | 0.0020956 | 0.030646 | -0.15381 | 0.028119 | 0.037309 | 0.05031 | 0.0040225 | 0.025222 | 0.082397 | 0.050354 | 0.022888 | 0.022888 | 0.086975 | 0.041199 | -0.13275 | 0.09613 | 0.07782 | -0.054932 | 0.064087 | 0.045776 | -0.041199 | -0.09613 | 0.14649 | -0.027465 | -122.1954 | 0.15564 | 0.12817 | 0.15564 | -122.2 | 0.064087 | 0.009156 | -122.2183 | 0.20142 | 0.050354 | 0.041198 | -122.2366 | 0.19226 | 0.18768 | 0.12817 | -122.4152 | 0.16937 | 0.15106 | 0.18311 | -122.3785
3937.375 | 122.4701 | -0.036621 | 122.2321 | 0.10193 | 0.044846 | 0.058405 | 0.0027601 | 0.029115 | -0.0030314 | 0.031074 | 0.090332 | 0.026197 | 0.036241 | 0.048174 | 0.0010317 | 0.029922 | 0.082397 | 0.10986 | 0.082397 | 0.064087 | 0.054932 | 0.045776 | -0.07782 | 0.13733 | 0.11902 | 0.022888 | 0.013733 | -0.004578 | -0.018311 | -0.068665 | 0.082397 | -0.041199 | -122.1771 | 0.14648 | 0.10071 | 0.14191 | -122.1497 | 0.01831 | -0.032044 | -122.2183 | 0.17395 | 0.059509 | 0.091553 | -122.2366 | 0.091553 | 0.11902 | 0.11902 | -122.3099 | 0.050354 | 0.032043 | 0.15564 | -122.3007
3939.1562 | 122.4792 | -0.050354 | 122.2366 | 0.13245 | 0.047623 | 0.060541 | 0.0021191 | 0.027406 | -0.003245 | 0.032142 | 0.10559 | 0.027692 | 0.035173 | 0.047961 | 0.0046633 | 0.027572 | 0.073242 | 0.10529 | 0.082397 | 0.054932 | 0.064087 | 0.059509 | -0.09613 | 0.14648 | 0.12817 | 0.018311 | 0.018311 | 0 | 0 | -0.073242 | 0.10986 | -0.045776 | -122.1725 | 0.15564 | 0.10529 | 0.15106 | -122.1634 | 0.050354 | -0.022888 | -122.2183 | 0.19684 | 0.068665 | 0.091553 | -122.2366 | 0.11444 | 0.1236 | 0.13275 | -122.3328 | 0.068665 | 0.050354 | 0.17853 | -122.3099
3940.8594 | 122.3969 | -0.082397 | 122.2824 | -0.18036 | 0.050827 | 0.059259 | 0.0053235 | 0.028901 | -0.0034586 | 0.030006 | -0.20721 | 0.027478 | 0.036455 | 0.047747 | -0.0013181 | 0.028854 | 0.013733 | -0.013733 | -0.018311 | 0 | 0.073242 | 0.013733 | -0.14648 | 0.027466 | 0.050354 | -0.091553 | 0.07782 | 0.041199 | -0.041199 | -0.10529 | 0.09613 | -0.064087 | -122.2092 | 0.068664 | 0.082397 | 0.14648 | -122.2687 | 0.041198 | -0.022889 | -122.2046 | 0.10986 | -0.009156 | 0.013733 | -122.2412 | 0.15564 | 0.09613 | 0.064086 | -122.4289 | 0.16022 | 0.1236 | 0.13275 | -122.3877
3942.625 | 122.4701 | -0.045776 | 122.2412 | 0.11719 | 0.044419 | 0.060327 | 0.0014783 | 0.028901 | -0.0013224 | 0.030646 | 0.082703 | 0.024915 | 0.034318 | 0.047747 | 0.0016727 | 0.029495 | 0.10071 | 0.091553 | 0.082397 | 0.059509 | 0.045776 | 0.045776 | -0.086975 | 0.14191 | 0.14648 | 0.018311 | 0.018311 | 0.009155 | 0 | -0.064087 | 0.091552 | -0.041199 | -122.1954 | 0.13733 | 0.10528 | 0.14648 | -122.1405 | 0.045776 | -0.018311 | -122.2229 | 0.18768 | 0.064087 | 0.082398 | -122.2321 | 0.091552 | 0.14648 | 0.12817 | -122.3282 | 0.064087 | 0.054931 | 0.19226 | -122.3053
3944.3438 | 122.438 | -0.068665 | 122.2504 | 0.071411 | 0.044419 | 0.060968 | 0.0012647 | 0.030183 | -0.0062356 | 0.031928 | 0.15137 | 0.027906 | 0.0356 | 0.048815 | 0.0012455 | 0.030136 | 0.068665 | 0.13275 | 0.10071 | 0.050354 | 0.027466 | 0.045776 | -0.086975 | 0.14191 | 0.11902 | 0.032043 | 0.009155 | 0.004578 | -0.027466 | -0.068665 | 0.11444 | -0.01831 | -122.2229 | 0.20142 | 0.11902 | 0.13733 | -122.1817 | 0.041199 | 0 | -122.2412 | 0.21057 | 0.10071 | 0.10071 | -122.2458 | 0.096131 | 0.13733 | 0.16937 | -122.3373 | 0.07782 | 0.073243 | 0.18768 | -122.319
3946.1094 | 122.4426 | -0.054932 | 122.2137 | 0.10956 | 0.044632 | 0.059259 | 0.00019645 | 0.02826 | -0.0011088 | 0.031928 | 0.159 | 0.026197 | 0.034532 | 0.047961 | 0.0010317 | 0.027999 | 0.086975 | 0.10986 | 0.086975 | 0.082397 | 0.050354 | 0.059509 | -0.082397 | 0.15564 | 0.12817 | 0.032043 | 0.013733 | -0.013733 | -0.018311 | -0.064087 | 0.11444 | -0.027465 | -122.1634 | 0.16479 | 0.13733 | 0.16479 | -122.1268 | 0.036621 | -0.009155 | -122.2 | 0.21057 | 0.086975 | 0.09613 | -122.2275 | 0.10529 | 0.14191 | 0.14191 | -122.2961 | 0.068665 | 0.041199 | 0.18311 | -122.2778
3947.8594 | 122.4609 | -0.036621 | 122.2092 | 0.12482 | 0.046128 | 0.058832 | 0.0012647 | 0.031892 | -0.002604 | 0.031928 | 0.082703 | 0.025556 | 0.0356 | 0.046465 | 0.0018863 | 0.027999 | 0.07782 | 0.064087 | 0.073242 | 0.054932 | 0.068665 | 0.059509 | -0.09613 | 0.14648 | 0.12817 | 0.018311 | 0.022888 | 0.009155 | 0 | -0.059509 | 0.09613 | -0.059509 | -122.1405 | 0.10071 | 0.091553 | 0.15106 | -122.1313 | 0.036621 | -0.022888 | -122.1863 | 0.18311 | 0.054932 | 0.07782 | -122.2 | 0.10529 | 0.11444 | 0.10986 | -122.3053 | 0.059509 | 0.045776 | 0.1648 | -122.2687
3949.6406 | 122.4701 | -0.045776 | 122.2321 | -0.0048827 | 0.045914 | 0.063532 | 0.0038281 | 0.027406 | -0.0075174 | 0.028083 | 0.036926 | 0.024915 | 0.036882 | 0.044756 | -0.0011045 | 0.03099 | 0.009155 | 0.059509 | 0.073242 | 0.032043 | 0.064087 | 0.045776 | -0.10529 | 0.10071 | 0.09613 | 0.018311 | 0.022888 | 0.018311 | 0 | -0.082397 | 0.091552 | -0.05951 | -122.168 | 0.10528 | 0.077819 | 0.13733 | -122.2229 | 0.045776 | -0.036621 | -122.2092 | 0.14648 | 0.064087 | 0.10071 | -122.2137 | 0.10986 | 0.054931 | 0.11902 | -122.3373 | 0.068664 | 0.064087 | 0.14191 | -122.3145
3951.3438 | 122.3557 | -0.09613 | 122.2824 | -0.088806 | 0.048905 | 0.058191 | 0.0048963 | 0.029969 | 0.0023092 | 0.02851 | -0.13855 | 0.028974 | 0.035387 | 0.048815 | 0.0020999 | 0.026504 | 0.082397 | 0.050354 | 0.032043 | 0.041199 | 0.082397 | 0.027466 | -0.12817 | 0.10071 | 0.068665 | -0.050354 | 0.036621 | 0.032043 | -0.045776 | -0.086975 | 0.1236 | -0.032044 | -122.2 | 0.14648 | 0.13733 | 0.16937 | -122.2 | 0.050354 | 0.009155 | -122.2458 | 0.19684 | 0.045776 | 0.036621 | -122.2504 | 0.17853 | 0.17853 | 0.12817 | -122.4106 | 0.13275 | 0.12817 | 0.16479 | -122.3694
3953.1094 | 122.438 | -0.032043 | 122.2366 | 0.071411 | 0.047623 | 0.061823 | -0.00044435 | 0.028901 | -0.0013224 | 0.030433 | 0.059815 | 0.027051 | 0.036882 | 0.048388 | 0.0033817 | 0.027572 | 0 | 0 | -0.036621 | -0.018311 | 0.10071 | 0.018311 | -0.1236 | 0.050354 | 0.004578 | -0.068665 | 0.045776 | 0.027466 | -0.041199 | -0.086975 | 0.050354 | -0.091553 | -122.1359 | 0.032043 | 0.013732 | 0.10528 | -122.2366 | -0.009156 | -0.054932 | -122.1909 | 0.082397 | -0.036622 | 0.01831 | -122.2092 | 0.13275 | 0.032043 | -0.004578 | -122.3602 | 0.077819 | 0.059509 | 0.036621 | -122.3236
3954.8125 | 122.3831 | -0.091553 | 122.2458 | 0.079041 | 0.048905 | 0.061182 | 0.0010511 | 0.029115 | -0.0013224 | 0.029578 | 0.090332 | 0.027051 | 0.036455 | 0.048174 | 0.0035953 | 0.030136 | -0.004578 | -0.018311 | -0.032043 | -0.018311 | 0.082397 | 0.004578 | -0.11444 | 0.036621 | -0.018311 | -0.086975 | 0.068665 | 0.059509 | -0.050354 | -0.09613 | 0.096131 | -0.022888 | -122.1634 | 0.073242 | 0.073242 | 0.09613 | -122.2504 | 0.041199 | -0.004577 | -122.1771 | 0.12817 | 0.004578 | 0.009155 | -122.1863 | 0.17395 | 0.086975 | 0.05951 | -122.3602 | 0.16022 | 0.15106 | 0.073242 | -122.3419
3956.5156 | 122.3373 | -0.11444 | 122.2733 | -0.22614 | 0.046768 | 0.057977 | 0.0074597 | 0.03061 | -0.004954 | 0.031074 | -0.13855 | 0.027265 | 0.039018 | 0.047747 | -0.00046349 | 0.031417 | -0.022888 | 0.022888 | 0.013733 | 0.009155 | 0.07782 | 0.009155 | -0.14191 | 0.022888 | 0.045776 | -0.073242 | 0.059509 | 0.050354 | -0.07782 | -0.10529 | 0.1236 | -0.027466 | -122.1954 | 0.13733 | 0.1236 | 0.15106 | -122.2961 | 0.036621 | 0.009155 | -122.2137 | 0.13733 | 0.041199 | 0.032044 | -122.2229 | 0.19226 | 0.091553 | 0.12817 | -122.4152 | 0.17395 | 0.16479 | 0.16022 | -122.3785
3958.2812 | 122.4243 | -0.068665 | 122.2733 | 0.025635 | 0.04271 | 0.060114 | 0.0051099 | 0.032105 | -0.0090128 | 0.031074 | 0.090332 | 0.027051 | 0.035173 | 0.046038 | -0.0036679 | 0.029922 | 0.041199 | 0.073242 | 0.068665 | 0.018311 | 0.036621 | 0.036621 | -0.091553 | 0.086975 | 0.091553 | 0.004578 | 0.018311 | 0.022888 | -0.027466 | -0.07782 | 0.10529 | -0.022888 | -122.2366 | 0.14191 | 0.086976 | 0.10986 | -122.2321 | 0.041199 | -0.009155 | -122.2549 | 0.15564 | 0.073243 | 0.082398 | -122.2504 | 0.10529 | 0.10986 | 0.13733 | -122.3648 | 0.086976 | 0.091553 | 0.16022 | -122.3511
3959.9844 | 122.3511 | -0.082397 | 122.2824 | -0.088806 | 0.04805 | 0.056909 | 0.0014783 | 0.031678 | 0.0020956 | 0.031714 | -0.13855 | 0.029828 | 0.036241 | 0.050738 | 0.0023135 | 0.027572 | 0.07782 | 0.045776 | 0.027466 | 0.018311 | 0.09613 | 0.027466 | -0.091553 | 0.10071 | 0.082397 | -0.054932 | 0.050354 | 0.050354 | -0.059509 | -0.086975 | 0.10986 | -0.009156 | -122.1863 | 0.12817 | 0.10071 | 0.10986 | -122.2046 | 0.022888 | -0.004578 | -122.2321 | 0.18311 | 0.027465 | 0.032043 | -122.2321 | 0.17853 | 0.16022 | 0.10986 | -122.374 | 0.13275 | 0.13275 | 0.16479 | -122.3694
3961.75 | 122.406 | -0.068665 | 122.287 | 0.10956 | 0.046982 | 0.0599 | 0.0014783 | 0.027833 | -0.0011088 | 0.033423 | 0.082703 | 0.028546 | 0.038591 | 0.048815 | 0.0029543 | 0.029708 | 0.013733 | -0.045776 | -0.045776 | -0.004578 | 0.082397 | 0.027466 | -0.12817 | 0.036621 | 0 | -0.09613 | 0.059509 | 0.050354 | -0.041199 | -0.086975 | 0.096131 | -0.059509 | -122.2046 | 0.022889 | 0.064087 | 0.1236 | -122.2733 | 0.027466 | -0.01831 | -122.2275 | 0.10529 | -0.027465 | -0.009155 | -122.2366 | 0.15106 | 0.082398 | 0.022889 | -122.4152 | 0.12817 | 0.11902 | 0.068665 | -122.374
3963.5156 | 122.3282 | -0.09613 | 122.2824 | -0.18799 | 0.047623 | 0.059045 | 0.0055371 | 0.031892 | -0.0062356 | 0.031714 | -0.19958 | 0.026624 | 0.036455 | 0.046252 | -0.0025999 | 0.030563 | 0.054932 | 0.11902 | 0.10986 | 0.068665 | 0.064087 | 0.041199 | -0.09613 | 0.09613 | 0.15106 | 0 | 0.050354 | 0.018311 | -0.032043 | -0.09613 | 0.13733 | 0 | -122.2183 | 0.21515 | 0.16479 | 0.16479 | -122.2275 | 0.064087 | 0 | -122.2321 | 0.19226 | 0.09613 | 0.09613 | -122.2641 | 0.16022 | 0.15106 | 0.20599 | -122.3785 | 0.14648 | 0.11444 | 0.24719 | -122.3785
3965.2812 | 122.3557 | -0.082397 | 122.2595 | 0.033264 | 0.04805 | 0.061395 | -0.0015125 | 0.028474 | -0.00046778 | 0.030006 | -0.0088499 | 0.029828 | 0.036241 | 0.048601 | 0.0040225 | 0.028213 | -0.009155 | -0.022888 | -0.045776 | -0.013733 | 0.10071 | 0.004578 | -0.13733 | 0 | -0.013733 | -0.1236 | 0.059509 | 0.041199 | -0.059509 | -0.10529 | 0.086975 | -0.054932 | -122.1588 | 0.059509 | 0.068664 | 0.1236 | -122.2687 | 0.022888 | -0.022889 | -122.2 | 0.082397 | -0.041199 | -0.01831 | -122.2183 | 0.18311 | 0.073242 | 0.036621 | -122.3969 | 0.14191 | 0.1236 | 0.068664 | -122.3648
3966.9844 | 122.3511 | -0.10071 | 122.2733 | 0.033264 | 0.047409 | 0.058618 | 0.0010511 | 0.027192 | -0.0013224 | 0.032142 | 0.036926 | 0.030896 | 0.039018 | 0.049029 | 0.0027407 | 0.030349 | -0.013733 | -0.045776 | -0.050354 | -0.018311 | 0.082397 | 0 | -0.13275 | 0.013733 | 0 | -0.10986 | 0.068665 | 0.032043 | -0.054932 | -0.10986 | 0.10071 | -0.032043 | -122.1909 | 0.054932 | 0.082397 | 0.11444 | -122.287 | 0.045776 | -0.009155 | -122.2046 | 0.11444 | -0.009155 | 0 | -122.2412 | 0.18311 | 0.086975 | 0.050354 | -122.406 | 0.16937 | 0.13275 | 0.10071 | -122.3831
3968.75 | 122.3511 | -0.09613 | 122.2733 | -0.18036 | 0.047409 | 0.061823 | 0.0029737 | 0.03061 | -0.0064492 | 0.031714 | -0.20721 | 0.025128 | 0.037309 | 0.046465 | -0.00089089 | 0.031631 | 0.045776 | 0.1236 | 0.09613 | 0.064087 | 0.07782 | 0.036621 | -0.10071 | 0.082397 | 0.12817 | -0.004578 | 0.027466 | 0.032043 | -0.045776 | -0.10071 | 0.13275 | -0.004578 | -122.1954 | 0.21973 | 0.16022 | 0.1648 | -122.2275 | 0.050354 | -0.004578 | -122.2458 | 0.17853 | 0.091552 | 0.09613 | -122.2412 | 0.17395 | 0.14191 | 0.19226 | -122.374 | 0.1236 | 0.12817 | 0.2243 | -122.374
3970.5156 | 122.3785 | -0.07782 | 122.2687 | 0.094299 | 0.045487 | 0.061823 | -0.0010851 | 0.034242 | -0.0023904 | 0.030219 | 0.082703 | 0.028546 | 0.034746 | 0.047961 | 0.0035953 | 0.028854 | -0.009155 | -0.022888 | -0.045776 | -0.032043 | 0.086975 | 0 | -0.1236 | 0.036621 | 0 | -0.09613 | 0.064087 | 0.059509 | -0.050354 | -0.11444 | 0.07782 | -0.045776 | -122.1817 | 0.054932 | 0.045777 | 0.091553 | -122.2778 | 0.027466 | -0.036621 | -122.2046 | 0.11444 | -0.01831 | 0.018311 | -122.2092 | 0.16479 | 0.068665 | 0.032044 | -122.3923 | 0.14191 | 0.13733 | 0.07782 | -122.3831
3972.2812 | 122.3877 | -0.09613 | 122.319 | -0.23376 | 0.047409 | 0.061609 | 0.0046827 | 0.031678 | -0.004954 | 0.029578 | -0.25299 | 0.025342 | 0.036027 | 0.046679 | 0.00081811 | 0.02864 | -0.032043 | -0.009155 | -0.018311 | -0.018311 | 0.10071 | 0.018311 | -0.14648 | 0.018311 | 0.027466 | -0.073242 | 0.064087 | 0.045776 | -0.050354 | -0.11902 | 0.11444 | -0.050354 | -122.2183 | 0.086975 | 0.077819 | 0.12817 | -122.3511 | 0.045776 | -0.022889 | -122.2549 | 0.11444 | 0.022888 | 0.045777 | -122.2733 | 0.19684 | 0.064087 | 0.077819 | -122.4655 | 0.16022 | 0.14191 | 0.1236 | -122.438
3973.9844 | 122.3969 | -0.09613 | 122.2961 | -0.19562 | 0.046768 | 0.061182 | 0.0034009 | 0.030824 | -0.0021768 | 0.030219 | -0.19958 | 0.029615 | 0.038164 | 0.049029 | 0.0010317 | 0.029068 | -0.013733 | -0.004578 | -0.027466 | 0 | 0.10529 | 0.004578 | -0.14191 | 0.018311 | 0.068665 | -0.07782 | 0.073242 | 0.045776 | -0.050354 | -0.086975 | 0.10071 | -0.045777 | -122.1909 | 0.091552 | 0.09613 | 0.14191 | -122.3099 | 0.045776 | 0.009155 | -122.2229 | 0.11444 | 0.01831 | 0.009155 | -122.2504 | 0.20142 | 0.082397 | 0.068664 | -122.4381 | 0.16937 | 0.14191 | 0.16479 | -122.3831
3975.7344 | 122.4014 | -0.086975 | 122.2916 | -0.14984 | 0.048477 | 0.060541 | 0.0036145 | 0.029115 | -0.002604 | 0.032783 | -0.16144 | 0.028333 | 0.039445 | 0.048815 | 0.00039091 | 0.027572 | 0.032043 | 0.027466 | 0.018311 | 0.027466 | 0.10986 | 0.013733 | -0.12817 | 0.073242 | 0.086975 | -0.041199 | 0.064087 | 0.059509 | -0.036621 | -0.07782 | 0.10071 | -0.041199 | -122.1817 | 0.11444 | 0.11444 | 0.15564 | -122.2595 | 0.050354 | 0.009155 | -122.2275 | 0.16022 | 0.045776 | 0.036621 | -122.2321 | 0.19684 | 0.11902 | 0.10529 | -122.4197 | 0.15106 | 0.14648 | 0.17395 | -122.3694
3977.4844 | 122.3282 | -0.09613 | 122.2595 | 0.048523 | 0.049118 | 0.059686 | -0.0010851 | 0.028901 | -0.0013224 | 0.032569 | -0.0012209 | 0.030683 | 0.036882 | 0.047533 | 0.0023135 | 0.027999 | -0.032043 | -0.041199 | -0.032043 | -0.004578 | 0.09613 | 0.027466 | -0.14191 | -0.004578 | -0.027466 | -0.13275 | 0.073242 | 0.059509 | -0.068665 | -0.10529 | 0.1236 | -0.045777 | -122.1634 | 0.054931 | 0.091552 | 0.13733 | -122.2916 | 0.027465 | -0.009156 | -122.1863 | 0.091552 | -0.036621 | -0.027465 | -122.2 | 0.19226 | 0.064087 | 0.064087 | -122.4014 | 0.16937 | 0.15564 | 0.068664 | -122.3648
3979.25 | 122.319 | -0.086975 | 122.2916 | -0.027771 | 0.049118 | 0.060754 | 0.0021191 | 0.03061 | -0.00025418 | 0.033423 | 0.0064086 | 0.026624 | 0.038164 | 0.049669 | 0.0031681 | 0.029281 | 0.018311 | 0.018311 | -0.022888 | 0.004578 | 0.07782 | 0.018311 | -0.12817 | 0.013733 | 0.004578 | -0.10071 | 0.054932 | 0.068665 | -0.036621 | -0.09613 | 0.10529 | -0.041199 | -122.2137 | 0.10529 | 0.091553 | 0.13275 | -122.2733 | 0.050354 | -0.009155 | -122.2366 | 0.10071 | -0.013733 | -0.004578 | -122.2229 | 0.16479 | 0.10529 | 0.064087 | -122.4197 | 0.14191 | 0.15564 | 0.091553 | -122.3877
3980.9531 | 122.4655 | -0.054932 | 122.2641 | -0.012512 | 0.046768 | 0.059259 | 0.0070325 | 0.031678 | -0.0098672 | 0.029578 | 0.097962 | 0.025983 | 0.034959 | 0.04732 | -0.0043087 | 0.030777 | 0.009155 | 0.059509 | 0.045776 | 0.032043 | 0.073242 | 0.045776 | -0.10529 | 0.068665 | 0.086975 | 0.013733 | 0.032043 | 0.036621 | -0.032043 | -0.086975 | 0.10071 | -0.050354 | -122.1909 | 0.11444 | 0.086975 | 0.13733 | -122.2549 | 0.022889 | -0.032043 | -122.2321 | 0.1236 | 0.068665 | 0.10071 | -122.2275 | 0.12817 | 0.064087 | 0.10071 | -122.3694 | 0.086975 | 0.091553 | 0.14191 | -122.3511
3982.7188 | 122.4289 | -0.045776 | 122.2733 | 0.063782 | 0.047196 | 0.059045 | 0.0025465 | 0.032105 | -0.006022 | 0.028937 | 0.18951 | 0.025983 | 0.036882 | 0.049242 | -0.0019589 | 0.028854 | 0.086975 | 0.09613 | 0.10529 | 0.059509 | 0.041199 | 0.054932 | -0.082397 | 0.11902 | 0.11902 | 0.032043 | 0.027466 | 0.013733 | -0.022888 | -0.068665 | 0.10071 | -0.036621 | -122.2321 | 0.14191 | 0.10528 | 0.14191 | -122.1863 | 0.022888 | -0.022889 | -122.2458 | 0.16479 | 0.077819 | 0.10071 | -122.2595 | 0.086975 | 0.13275 | 0.15106 | -122.3557 | 0.073242 | 0.059509 | 0.16479 | -122.3419
3984.5 | 122.3419 | -0.091553 | 122.3007 | -0.10406 | 0.046768 | 0.059259 | 0.0012647 | 0.031037 | 0.0010276 | 0.030433 | -0.10803 | 0.028974 | 0.035814 | 0.04732 | 0.0042361 | 0.027572 | 0.091553 | 0.041199 | 0.013733 | 0.032043 | 0.086975 | 0.032043 | -0.11902 | 0.068665 | 0.059509 | -0.054932 | 0.054932 | 0.036621 | -0.050354 | -0.10529 | 0.1236 | -0.027466 | -122.2137 | 0.13275 | 0.1236 | 0.15106 | -122.2092 | 0.041199 | -0.013733 | -122.2458 | 0.16022 | 0.036621 | 0.050354 | -122.2641 | 0.17853 | 0.18311 | 0.10529 | -122.4197 | 0.14649 | 0.12817 | 0.15106 | -122.406
3986.2031 | 122.4976 | -0.050354 | 122.2641 | -0.058289 | 0.043778 | 0.063104 | 0.0021191 | 0.031678 | -0.0092264 | 0.028297 | -0.024109 | 0.025769 | 0.035173 | 0.047961 | -0.0023861 | 0.029708 | 0.022888 | 0.091553 | 0.082397 | 0.045776 | 0.064087 | 0.064087 | -0.09613 | 0.11444 | 0.14648 | 0.045776 | 0.027466 | 0.027466 | -0.036621 | -0.091553 | 0.11444 | -0.045776 | -122.2 | 0.14191 | 0.09613 | 0.14191 | -122.2412 | 0.013733 | -0.041199 | -122.2366 | 0.16479 | 0.09613 | 0.13733 | -122.2366 | 0.11444 | 0.073242 | 0.13275 | -122.3602 | 0.07782 | 0.07782 | 0.19684 | -122.3557
3987.9688 | 122.3602 | -0.082397 | 122.2824 | -0.096436 | 0.049332 | 0.059045 | 0.0027601 | 0.03061 | 0.001882 | 0.029365 | -0.14618 | 0.027906 | 0.037736 | 0.050524 | 0.00081811 | 0.026718 | 0.064087 | 0.045776 | 0.004578 | 0.022888 | 0.082397 | 0.022888 | -0.1236 | 0.082397 | 0.091553 | -0.041199 | 0.064087 | 0.036621 | -0.027466 | -0.07782 | 0.10528 | -0.041199 | -122.2 | 0.12817 | 0.10528 | 0.14648 | -122.2183 | 0.054931 | 0.004577 | -122.2183 | 0.16479 | 0.041198 | 0.036621 | -122.2458 | 0.16479 | 0.14648 | 0.086975 | -122.406 | 0.14648 | 0.11902 | 0.17395 | -122.3602
3989.6562 | 122.4655 | -0.059509 | 122.2778 | -0.12695 | 0.046982 | 0.061823 | 0.0044691 | 0.031678 | -0.0098672 | 0.028724 | -0.10803 | 0.025342 | 0.033891 | 0.049242 | -0.0034543 | 0.030777 | 0.10071 | 0.15106 | 0.1236 | 0.07782 | 0.064087 | 0.059509 | -0.10986 | 0.13275 | 0.1831 | 0.050354 | 0.032043 | 0.004578 | -0.004578 | -0.073242 | 0.11902 | -0.050354 | -122.2137 | 0.21057 | 0.13733 | 0.18768 | -122.1771 | 0.054931 | -0.013733 | -122.2458 | 0.19226 | 0.10986 | 0.1236 | -122.2733 | 0.1236 | 0.16022 | 0.1831 | -122.3877 | 0.091552 | 0.064087 | 0.24261 | -122.3511
3991.4062 | 122.4747 | -0.064087 | 122.2504 | -0.012512 | 0.041855 | 0.062463 | 0.0012647 | 0.029756 | -0.0070902 | 0.028083 | 0.029297 | 0.027051 | 0.035814 | 0.047106 | -0.0011045 | 0.030136 | 0.032043 | 0.041199 | 0.045776 | 0.036621 | 0.068665 | 0.041199 | -0.10529 | 0.09613 | 0.09613 | 0.013733 | 0.050354 | 0.022888 | -0.018311 | -0.073242 | 0.10529 | -0.041199 | -122.1817 | 0.10529 | 0.10071 | 0.14191 | -122.2183 | 0.045776 | -0.009155 | -122.2 | 0.16022 | 0.07782 | 0.086975 | -122.2275 | 0.13275 | 0.09613 | 0.10986 | -122.3557 | 0.11444 | 0.086975 | 0.16022 | -122.3236
3993.1094 | 122.4701 | -0.045776 | 122.2412 | 0.14008 | 0.046341 | 0.060541 | 0.0021191 | 0.031037 | 0.00038662 | 0.029365 | 0.10559 | 0.028333 | 0.035814 | 0.048174 | 0.0031681 | 0.026718 | 0.050354 | 0.004578 | 0.018311 | 0 | 0.09613 | 0.018311 | -0.1236 | 0.11444 | 0.059509 | -0.009155 | 0.027466 | 0.022888 | -0.032043 | -0.082397 | 0.064087 | -0.07782 | -122.1451 | 0.050354 | 0.045776 | 0.1236 | -122.1909 | 0.013733 | -0.036621 | -122.2137 | 0.16022 | 0.036621 | 0.073242 | -122.2183 | 0.14191 | 0.09613 | 0.064087 | -122.3648 | 0.073242 | 0.068664 | 0.10528 | -122.3236
3994.8281 | 122.3419 | -0.086975 | 122.2687 | 0.0027468 | 0.045914 | 0.058832 | 0.0014783 | 0.027192 | 0.0012412 | 0.031501 | -0.016479 | 0.027906 | 0.036241 | 0.046892 | 0.0040225 | 0.029281 | 0.013733 | 0.004578 | -0.027466 | -0.009155 | 0.086975 | 0.009155 | -0.12817 | 0.013733 | -0.004578 | -0.1236 | 0.059509 | 0.050354 | -0.050354 | -0.10071 | 0.09613 | -0.041199 | -122.1817 | 0.091553 | 0.07782 | 0.11902 | -122.2549 | 0.036621 | -0.013733 | -122.2092 | 0.10071 | -0.036621 | -0.022888 | -122.2183 | 0.17395 | 0.10071 | 0.059509 | -122.3969 | 0.14648 | 0.13733 | 0.082397 | -122.3694
3996.5938 | 122.3419 | -0.09613 | 122.2733 | 0.018005 | 0.04805 | 0.057977 | 0.0023329 | 0.028688 | -4.058e-05 | 0.032569 | -0.016479 | 0.028546 | 0.035814 | 0.04732 | 0.0038089 | 0.027572 | -0.009155 | -0.013733 | -0.045776 | -0.009155 | 0.086975 | 0.018311 | -0.12817 | 0.009155 | -0.004578 | -0.10986 | 0.059509 | 0.045776 | -0.059509 | -0.10986 | 0.11444 | -0.032044 | -122.1863 | 0.082397 | 0.086975 | 0.11902 | -122.2824 | 0.036621 | -0.013733 | -122.2137 | 0.10528 | -0.013733 | 0 | -122.2275 | 0.1831 | 0.086975 | 0.050354 | -122.4014 | 0.15564 | 0.14191 | 0.091552 | -122.3831
3998.3438 | 122.374 | -0.086975 | 122.2733 | -0.096436 | 0.049118 | 0.058618 | 0.0048963 | 0.031037 | -0.0013224 | 0.032569 | -0.11566 | 0.027692 | 0.038377 | 0.04732 | -0.00067729 | 0.030349 | 0.054932 | 0.064087 | 0.027466 | 0.041199 | 0.091553 | 0.027466 | -0.11444 | 0.086975 | 0.082397 | -0.050354 | 0.041199 | 0.022888 | -0.041199 | -0.10986 | 0.11444 | -0.027466 | -122.1817 | 0.15106 | 0.12817 | 0.15564 | -122.2183 | 0.045776 | -0.022888 | -122.2321 | 0.17395 | 0.036621 | 0.059509 | -122.2504 | 0.17853 | 0.14191 | 0.11444 | -122.3877 | 0.12817 | 0.10986 | 0.16937 | -122.3831
4000.0469 | 122.3373 | -0.10071 | 122.2961 | -0.073547 | 0.049973 | 0.059686 | 0.0040417 | 0.028901 | -0.00046778 | 0.032355 | -0.069885 | 0.030042 | 0.038377 | 0.049669 | -0.00024989 | 0.029708 | 0.036621 | 0.036621 | 0.027466 | 0.013733 | 0.082397 | 0.018311 | -0.13275 | 0.050354 | 0.041199 | -0.082397 | 0.07782 | 0.045776 | -0.045776 | -0.091553 | 0.11902 | -0.032043 | -122.2137 | 0.13733 | 0.11444 | 0.14648 | -122.2595 | 0.054932 | 0.009155 | -122.2183 | 0.15106 | 0.018311 | 0.009156 | -122.2504 | 0.18311 | 0.13733 | 0.12817 | -122.4289 | 0.17853 | 0.14648 | 0.14191 | -122.3877
4001.75 | 122.4335 | -0.059509 | 122.2458 | 0.08667 | 0.048477 | 0.060754 | 0.0044691 | 0.029328 | -0.008372 | 0.030646 | 0.19714 | 0.027051 | 0.035173 | 0.046252 | -0.0028135 | 0.031417 | 0.050354 | 0.11444 | 0.10529 | 0.050354 | 0.054932 | 0.036621 | -0.10071 | 0.1236 | 0.09613 | 0.022888 | 0.027466 | 0.009155 | -0.013733 | -0.054932 | 0.09613 | -0.041199 | -122.1909 | 0.17395 | 0.10986 | 0.15106 | -122.1954 | 0.045776 | 0.004577 | -122.2183 | 0.1831 | 0.082397 | 0.07782 | -122.2366 | 0.11444 | 0.10986 | 0.16479 | -122.3465 | 0.086975 | 0.068664 | 0.15564 | -122.3007
4003.4531 | 122.3831 | -0.09613 | 122.2595 | -0.20325 | 0.045487 | 0.059473 | 0.0072461 | 0.028047 | -0.0075174 | 0.029792 | -0.11566 | 0.026624 | 0.035387 | 0.046679 | -0.0040951 | 0.029068 | 0.068665 | 0.14648 | 0.10071 | 0.050354 | 0.059509 | 0.027466 | -0.10071 | 0.10529 | 0.16479 | 0.027466 | 0.022888 | 0.027466 | -0.013733 | -0.059509 | 0.1236 | -0.004578 | -122.2 | 0.24261 | 0.14648 | 0.15106 | -122.1909 | 0.082397 | 0.036621 | -122.2366 | 0.20142 | 0.1236 | 0.086975 | -122.2321 | 0.15564 | 0.16479 | 0.19684 | -122.3602 | 0.11902 | 0.1236 | 0.26092 | -122.319
4005.2188 | 122.3785 | -0.086975 | 122.2641 | -0.24139 | 0.046982 | 0.063532 | 0.0019055 | 0.030397 | -0.0045266 | 0.028297 | -0.24536 | 0.027265 | 0.037736 | 0.048388 | 0.00017731 | 0.028213 | -0.009155 | -0.009155 | -0.009155 | -0.027466 | 0.09613 | -0.009155 | -0.13733 | 0.009155 | 0.022888 | -0.09613 | 0.082397 | 0.068665 | -0.059509 | -0.10071 | 0.07782 | -0.050354 | -122.168 | 0.07782 | 0.059509 | 0.10986 | -122.2733 | 0.027466 | -0.013733 | -122.1817 | 0.09613 | -0.009155 | 0.004578 | -122.1954 | 0.1831 | 0.07782 | 0.07782 | -122.4014 | 0.16937 | 0.15564 | 0.10986 | -122.3648
4006.9844 | 122.4197 | -0.073242 | 122.2412 | 0.071411 | 0.043564 | 0.06225 | 0.00041005 | 0.028688 | -0.0075174 | 0.028724 | 0.10559 | 0.027478 | 0.035387 | 0.046679 | -0.00067729 | 0.030349 | 0.054932 | 0.091553 | 0.07782 | 0.036621 | 0.050354 | 0.054932 | -0.082397 | 0.11902 | 0.10071 | 0.013733 | 0.036621 | 0.018311 | -0.004578 | -0.054932 | 0.12817 | -0.009155 | -122.1909 | 0.16479 | 0.10986 | 0.11902 | -122.1863 | 0.068664 | 0.01831 | -122.2046 | 0.19226 | 0.086975 | 0.068665 | -122.2229 | 0.1236 | 0.12817 | 0.15106 | -122.3236 | 0.10986 | 0.091553 | 0.17395 | -122.2961
4008.7344 | 122.4335 | -0.054932 | 122.2504 | 0.010376 | 0.041214 | 0.062036 | 0.0014783 | 0.027406 | -0.0073038 | 0.029792 | 0.044556 | 0.025342 | 0.033464 | 0.046679 | -0.0011045 | 0.030349 | 0.036621 | 0.068665 | 0.068665 | 0.022888 | 0.064087 | 0.022888 | -0.091553 | 0.073242 | 0.086975 | 0.004578 | 0.041199 | 0.018311 | -0.032043 | -0.068665 | 0.07782 | -0.036621 | -122.1863 | 0.1236 | 0.07782 | 0.11444 | -122.2137 | 0.022889 | -0.013733 | -122.2092 | 0.12817 | 0.05951 | 0.073243 | -122.2321 | 0.11902 | 0.091553 | 0.1236 | -122.3419 | 0.096131 | 0.073243 | 0.14191 | -122.319
4011.7656 | 122.438 | -0.064087 | 122.2549 | -0.0048827 | 0.046982 | 0.061395 | 0.0066053 | 0.029969 | -0.007731 | 0.027015 | 0.029297 | 0.027478 | 0.036241 | 0.048174 | -0.0015317 | 0.028854 | 0.036621 | 0.050354 | 0.054932 | 0.027466 | 0.059509 | 0.050354 | -0.09613 | 0.086975 | 0.082397 | 0 | 0.036621 | 0.013733 | -0.013733 | -0.073242 | 0.11444 | -0.032043 | -122.1954 | 0.11444 | 0.091553 | 0.1236 | -122.2183 | 0.050354 | -0.009155 | -122.2183 | 0.15106 | 0.064087 | 0.073242 | -122.2412 | 0.1236 | 0.10071 | 0.11902 | -122.3511 | 0.10071 | 0.07782 | 0.14648 | -122.3282
4014.4531 | 122.3785 | -0.086975 | 122.2595 | 0.08667 | 0.046555 | 0.060327 | -0.00065795 | 0.029328 | 0.0014548 | 0.029151 | 0.044556 | 0.028119 | 0.0356 | 0.048388 | 0.0040225 | 0.025436 | 0.013733 | -0.032043 | -0.041199 | -0.009155 | 0.10529 | 0.013733 | -0.11902 | 0.036621 | -0.022888 | -0.11444 | 0.059509 | 0.045776 | -0.041199 | -0.09613 | 0.10071 | -0.032044 | -122.1542 | 0.054932 | 0.07782 | 0.10986 | -122.2458 | 0.045776 | -0.009155 | -122.2 | 0.1236 | -0.027466 | -0.018311 | -122.2137 | 0.19226 | 0.10071 | 0.045776 | -122.3785 | 0.14648 | 0.13275 | 0.064087 | -122.3557
4018.125 | 122.3602 | -0.086975 | 122.287 | -0.21088 | 0.043991 | 0.062677 | 0.0025465 | 0.029969 | -0.0030314 | 0.027442 | -0.26062 | 0.028119 | 0.036027 | 0.04732 | -3.629e-05 | 0.029708 | 0.004578 | 0.013733 | -0.022888 | -0.018311 | 0.086975 | 0 | -0.13275 | 0.027466 | 0.036621 | -0.09613 | 0.07782 | 0.073242 | -0.059509 | -0.10986 | 0.086975 | -0.045776 | -122.2 | 0.10071 | 0.068664 | 0.11444 | -122.2824 | 0.027466 | -0.022888 | -122.2092 | 0.11444 | -0.009155 | 0.013733 | -122.2137 | 0.17395 | 0.091553 | 0.064087 | -122.4197 | 0.16479 | 0.16022 | 0.1236 | -122.3969
4023.4375 | 122.3419 | -0.086975 | 122.2595 | -0.088806 | 0.048691 | 0.061182 | 0.0029737 | 0.026551 | 0.00081382 | 0.030219 | -0.10803 | 0.029401 | 0.037096 | 0.047747 | 0.0046633 | 0.026931 | 0.073242 | 0.050354 | 0.022888 | 0.032043 | 0.07782 | 0.032043 | -0.11902 | 0.068665 | 0.054932 | -0.068665 | 0.050354 | 0.041199 | -0.045776 | -0.10071 | 0.11902 | -0.032044 | -122.1817 | 0.13733 | 0.11902 | 0.15106 | -122.1863 | 0.041199 | -0.013733 | -122.2092 | 0.15564 | 0.01831 | 0.032043 | -122.2183 | 0.16479 | 0.16022 | 0.10986 | -122.3785 | 0.13733 | 0.12817 | 0.14191 | -122.3602
4025.2188 | 122.4472 | -0.068665 | 122.2366 | -0.14221 | 0.0457 | 0.060541 | 0.0068189 | 0.028688 | -0.011149 | 0.028937 | -0.11566 | 0.027265 | 0.036882 | 0.047961 | -0.0049497 | 0.029922 | 0.09613 | 0.15564 | 0.11902 | 0.082397 | 0.050354 | 0.045776 | -0.10529 | 0.15106 | 0.17853 | 0.064087 | 0.018311 | 0.018311 | -0.009155 | -0.07782 | 0.11444 | -0.036621 | -122.1863 | 0.22431 | 0.15106 | 0.18768 | -122.1405 | 0.05951 | -0.009155 | -122.2183 | 0.21973 | 0.13275 | 0.14191 | -122.2183 | 0.11902 | 0.16479 | 0.18768 | -122.3419 | 0.086976 | 0.086976 | 0.24719 | -122.3145
4026.9219 | 122.438 | -0.054932 | 122.2733 | 0.079041 | 0.042923 | 0.060327 | 0.0014783 | 0.029756 | -0.0070902 | 0.029151 | 0.10559 | 0.025128 | 0.0356 | 0.046252 | 0.00017731 | 0.02864 | 0.036621 | 0.091553 | 0.068665 | 0.036621 | 0.050354 | 0.041199 | -0.091553 | 0.091553 | 0.09613 | 0.013733 | 0.045776 | 0.013733 | -0.022888 | -0.073242 | 0.096131 | -0.036621 | -122.2229 | 0.14649 | 0.091553 | 0.12817 | -122.2366 | 0.032044 | -0.01831 | -122.2275 | 0.14649 | 0.068665 | 0.086975 | -122.2595 | 0.10529 | 0.091553 | 0.1236 | -122.3648 | 0.10071 | 0.068665 | 0.15106 | -122.3465
4028.6719 | 122.4106 | -0.07782 | 122.2778 | -0.1651 | 0.047837 | 0.060754 | 0.0038281 | 0.031465 | -0.0055948 | 0.028724 | -0.15381 | 0.025556 | 0.034532 | 0.04497 | -0.00089089 | 0.028213 | 0.086975 | 0.14648 | 0.11902 | 0.086975 | 0.064087 | 0.041199 | -0.10071 | 0.14191 | 0.17853 | 0.07782 | 0.022888 | 0.009155 | -0.018311 | -0.082397 | 0.11902 | -0.022888 | -122.2137 | 0.2243 | 0.16479 | 0.18768 | -122.1909 | 0.059509 | -0.004577 | -122.2549 | 0.21973 | 0.15564 | 0.16022 | -122.2687 | 0.14191 | 0.16479 | 0.19684 | -122.3785 | 0.10071 | 0.086975 | 0.25635 | -122.3602
4030.4375 | 122.3785 | -0.068665 | 122.2778 | -0.096436 | 0.046982 | 0.060968 | 0.0012647 | 0.028688 | 0.0031638 | 0.032569 | -0.18433 | 0.028119 | 0.032823 | 0.047106 | 0.0033817 | 0.02864 | 0.073242 | 0.045776 | 0.013733 | 0.022888 | 0.10071 | 0.036621 | -0.13733 | 0.086975 | 0.07782 | -0.045776 | 0.045776 | 0.018311 | -0.054932 | -0.091553 | 0.10529 | -0.068664 | -122.1771 | 0.11444 | 0.091553 | 0.16022 | -122.2046 | 0.013733 | -0.022888 | -122.2321 | 0.15564 | 0.022889 | 0.045777 | -122.2595 | 0.16937 | 0.14191 | 0.082398 | -122.4152 | 0.11444 | 0.086976 | 0.14649 | -122.3694
4032.2188 | 122.3511 | -0.086975 | 122.2778 | -0.14221 | 0.047409 | 0.060754 | 0.0072461 | 0.029115 | -0.0047404 | 0.02851 | -0.27588 | 0.028119 | 0.036241 | 0.048388 | -0.00067729 | 0.029281 | 0.009155 | 0.013733 | -0.022888 | -0.009155 | 0.082397 | 0.004578 | -0.12817 | 0.022888 | 0.045776 | -0.082397 | 0.073242 | 0.064087 | -0.068665 | -0.10071 | 0.091553 | -0.041199 | -122.1954 | 0.10071 | 0.07782 | 0.11902 | -122.2687 | 0.01831 | -0.013733 | -122.2046 | 0.10986 | 0.004578 | 0.018311 | -122.2137 | 0.16937 | 0.09613 | 0.064087 | -122.406 | 0.16022 | 0.15106 | 0.13275 | -122.3785
4033.9219 | 122.4701 | -0.054932 | 122.2549 | -0.11169 | 0.045487 | 0.060327 | 0.0046827 | 0.027619 | -0.0068766 | 0.030433 | -0.077515 | 0.023633 | 0.035814 | 0.047533 | -0.0021725 | 0.029922 | 0.10071 | 0.13733 | 0.11444 | 0.073242 | 0.054932 | 0.036621 | -0.09613 | 0.16937 | 0.1831 | 0.073242 | 0.018311 | 0.009155 | -0.004578 | -0.064087 | 0.091553 | -0.041198 | -122.2 | 0.19226 | 0.12817 | 0.16937 | -122.1542 | 0.050354 | -0.009155 | -122.2366 | 0.22431 | 0.12817 | 0.13733 | -122.2458 | 0.10986 | 0.15564 | 0.16937 | -122.3511 | 0.073243 | 0.064087 | 0.23804 | -122.319
4035.6094 | 122.3923 | -0.07782 | 122.2641 | 0.10193 | 0.049118 | 0.057977 | 0.0021191 | 0.02527 | 0.0029502 | 0.03086 | 0.059815 | 0.030255 | 0.038377 | 0.049242 | 0.0031681 | 0.025863 | 0.027466 | -0.032043 | -0.036621 | -0.013733 | 0.09613 | 0.013733 | -0.14191 | 0.064087 | -0.009155 | -0.10071 | 0.068665 | 0.064087 | -0.041199 | -0.10529 | 0.091553 | -0.064087 | -122.168 | 0.045777 | 0.064087 | 0.12817 | -122.2366 | 0.036621 | -0.027466 | -122.1954 | 0.14191 | -0.022888 | 0.004578 | -122.2 | 0.17395 | 0.10529 | 0.041199 | -122.406 | 0.14649 | 0.14191 | 0.068665 | -122.3694
4037.375 | 122.3969 | -0.073242 | 122.2733 | -0.15747 | 0.051895 | 0.059045 | 0.0046827 | 0.031465 | -4.058e-05 | 0.032355 | -0.18433 | 0.02876 | 0.037096 | 0.046038 | 0.0012455 | 0.027145 | 0.054932 | 0.032043 | 0.018311 | 0.032043 | 0.11444 | 0.018311 | -0.12817 | 0.07782 | 0.082397 | -0.059509 | 0.054932 | 0.059509 | -0.054932 | -0.10529 | 0.091553 | -0.054932 | -122.1588 | 0.10529 | 0.10529 | 0.16022 | -122.2183 | 0.01831 | -0.032044 | -122.2183 | 0.15106 | 0.013733 | 0.045777 | -122.2137 | 0.18768 | 0.12817 | 0.091553 | -122.4014 | 0.12817 | 0.13275 | 0.15564 | -122.3785
4039.1562 | 122.438 | -0.045776 | 122.2549 | 0.079041 | 0.047196 | 0.059259 | -0.00023075 | 0.031251 | -0.0023904 | 0.032355 | 0.067444 | 0.026837 | 0.034318 | 0.049669 | 0.0046633 | 0.031204 | 0 | -0.018311 | -0.027466 | -0.009155 | 0.09613 | 0.009155 | -0.11902 | 0.050354 | 0.018311 | -0.068665 | 0.082397 | 0.041199 | -0.045776 | -0.10986 | 0.054931 | -0.073243 | -122.1588 | 0.027465 | 0.036621 | 0.10986 | -122.2549 | 0 | -0.064087 | -122.1725 | 0.09613 | -0.022889 | 0.041198 | -122.2137 | 0.14191 | 0.045776 | 0.01831 | -122.374 | 0.12817 | 0.086975 | 0.064087 | -122.3648
4040.875 | 122.3694 | -0.10529 | 122.2824 | 0.063782 | 0.048264 | 0.059686 | 0.0012647 | 0.029115 | -0.0034586 | 0.032142 | 0.12085 | 0.028546 | 0.035814 | 0.048388 | 0.0016727 | 0.029495 | -0.004578 | -0.032043 | -0.036621 | -0.013733 | 0.091553 | 0.022888 | -0.13275 | 0.045776 | 0 | -0.09613 | 0.045776 | 0.041199 | -0.041199 | -0.10071 | 0.12817 | -0.027465 | -122.1909 | 0.073243 | 0.091553 | 0.11902 | -122.287 | 0.064087 | 0.004578 | -122.2366 | 0.15106 | 0.009156 | 0.004578 | -122.2412 | 0.19684 | 0.10071 | 0.068665 | -122.4152 | 0.15106 | 0.14649 | 0.10529 | -122.3831
4042.6406 | 122.3465 | -0.10071 | 122.2824 | 0.033264 | 0.047196 | 0.060114 | 0.0014783 | 0.030397 | -0.00089518 | 0.032355 | 0.029297 | 0.028974 | 0.037309 | 0.047747 | 0.0040225 | 0.029922 | -0.004578 | -0.013733 | -0.022888 | -0.027466 | 0.086975 | 0.009155 | -0.13733 | 0.013733 | 0.004578 | -0.11902 | 0.068665 | 0.059509 | -0.050354 | -0.10529 | 0.10986 | -0.036621 | -122.1954 | 0.086975 | 0.073242 | 0.10986 | -122.287 | 0.050354 | -0.004578 | -122.2137 | 0.11444 | -0.018311 | -0.013733 | -122.2229 | 0.18768 | 0.09613 | 0.07782 | -122.4197 | 0.16937 | 0.16022 | 0.10529 | -122.3877
4044.3438 | 122.4655 | -0.045776 | 122.2687 | -0.14984 | 0.044419 | 0.062463 | 0.0061781 | 0.031465 | -0.010508 | 0.030219 | -0.031738 | 0.025128 | 0.034959 | 0.046252 | -0.0036679 | 0.030136 | 0.073242 | 0.12817 | 0.11444 | 0.07782 | 0.050354 | 0.032043 | -0.091553 | 0.16479 | 0.17853 | 0.068665 | 0.013733 | 0.009155 | -0.018311 | -0.082397 | 0.077819 | -0.045777 | -122.2183 | 0.17395 | 0.1236 | 0.16937 | -122.1954 | 0.027465 | -0.036621 | -122.2549 | 0.21057 | 0.11444 | 0.15106 | -122.2595 | 0.09613 | 0.11902 | 0.16022 | -122.3602 | 0.059509 | 0.054931 | 0.2243 | -122.3511
4046.1094 | 122.4335 | -0.068665 | 122.2641 | -0.18799 | 0.046341 | 0.061182 | 0.0063917 | 0.028688 | -0.0070902 | 0.030006 | -0.13092 | 0.025128 | 0.036027 | 0.046679 | -0.0030271 | 0.028213 | 0.091553 | 0.14648 | 0.11902 | 0.082397 | 0.045776 | 0.045776 | -0.10529 | 0.13275 | 0.18768 | 0.054932 | 0.041199 | 0.027466 | -0.013733 | -0.054932 | 0.11444 | -0.036621 | -122.2183 | 0.21515 | 0.15106 | 0.18768 | -122.1725 | 0.054932 | 0.013733 | -122.2229 | 0.20142 | 0.1236 | 0.10986 | -122.2366 | 0.11444 | 0.16022 | 0.18768 | -122.3694 | 0.10986 | 0.096131 | 0.25635 | -122.319
4047.7969 | 122.3969 | -0.07782 | 122.2549 | 0.094299 | 0.047623 | 0.059686 | 0.0025465 | 0.031465 | -0.00068138 | 0.028937 | 0.044556 | 0.029401 | 0.036241 | 0.048601 | 0.0038089 | 0.027145 | 0.009155 | -0.041199 | -0.050354 | -0.013733 | 0.091553 | 0.032043 | -0.13733 | 0.036621 | -0.004578 | -0.09613 | 0.041199 | 0.059509 | -0.054932 | -0.11902 | 0.10986 | -0.059509 | -122.1634 | 0.036621 | 0.064087 | 0.1236 | -122.2458 | 0.022888 | -0.041199 | -122.2137 | 0.11444 | -0.01831 | 0.022889 | -122.1954 | 0.16937 | 0.086975 | 0.027466 | -122.3923 | 0.11902 | 0.13733 | 0.073242 | -122.374
4049.5625 | 122.3282 | -0.091553 | 122.2961 | -0.21851 | 0.047196 | 0.062891 | 0.0078871 | 0.029969 | -0.0047404 | 0.029792 | -0.19196 | 0.02641 | 0.036882 | 0.047747 | -0.00024989 | 0.028427 | 0.050354 | 0.10071 | 0.064087 | 0.050354 | 0.059509 | 0.018311 | -0.1236 | 0.045776 | 0.09613 | -0.032043 | 0.041199 | 0.036621 | -0.050354 | -0.09613 | 0.10986 | -0.032043 | -122.2366 | 0.19226 | 0.14191 | 0.17395 | -122.2458 | 0.041199 | -0.004577 | -122.2549 | 0.13733 | 0.05951 | 0.064087 | -122.2595 | 0.15106 | 0.14191 | 0.15564 | -122.4197 | 0.13275 | 0.12817 | 0.18768 | -122.3923
4051.3281 | 122.3602 | -0.10071 | 122.2778 | 0.063782 | 0.046982 | 0.057336 | 0.0021191 | 0.029756 | 0.0014548 | 0.031287 | -0.0088499 | 0.026197 | 0.035814 | 0.046465 | 0.0031681 | 0.028213 | 0.004578 | -0.018311 | -0.032043 | -0.018311 | 0.091553 | 0.013733 | -0.13275 | 0.022888 | -0.009155 | -0.11444 | 0.054932 | 0.054932 | -0.068665 | -0.11902 | 0.11444 | -0.032043 | -122.1863 | 0.082397 | 0.082397 | 0.11444 | -122.2733 | 0.032043 | -0.018311 | -122.2229 | 0.1236 | -0.013733 | 0.004578 | -122.2229 | 0.19226 | 0.10529 | 0.068665 | -122.4106 | 0.15564 | 0.15564 | 0.091553 | -122.3969
4053.0938 | 122.4609 | -0.054932 | 122.2824 | -0.14984 | 0.045914 | 0.063104 | 0.0055371 | 0.032533 | -0.0096536 | 0.030006 | -0.092773 | 0.025128 | 0.035814 | 0.046892 | -0.0017453 | 0.029495 | 0.086975 | 0.17395 | 0.13275 | 0.07782 | 0.045776 | 0.045776 | -0.09613 | 0.13733 | 0.17395 | 0.073242 | 0.032043 | -0.004578 | -0.036621 | -0.086975 | 0.10071 | -0.041198 | -122.2366 | 0.22888 | 0.13275 | 0.17395 | -122.1954 | 0.018311 | -0.032043 | -122.2504 | 0.19226 | 0.12817 | 0.16022 | -122.287 | 0.10071 | 0.14191 | 0.18768 | -122.3785 | 0.086975 | 0.050354 | 0.22888 | -122.3694
4054.7812 | 122.3511 | -0.082397 | 122.2778 | 0.040894 | 0.046982 | 0.060968 | -0.00044435 | 0.029115 | -4.058e-05 | 0.031074 | 0.0064086 | 0.030042 | 0.035814 | 0.047533 | 0.0063723 | 0.029068 | -0.022888 | -0.050354 | -0.050354 | -0.018311 | 0.11444 | 0.013733 | -0.11902 | 0.018311 | -0.009155 | -0.11902 | 0.068665 | 0.050354 | -0.045776 | -0.11444 | 0.09613 | -0.036622 | -122.1634 | 0.032043 | 0.064086 | 0.10071 | -122.3007 | 0.036621 | -0.032044 | -122.2092 | 0.10071 | -0.036622 | -0.004578 | -122.2275 | 0.19684 | 0.059509 | 0.032043 | -122.3969 | 0.15106 | 0.13275 | 0.073242 | -122.3923
4056.5625 | 122.4197 | -0.064087 | 122.2595 | 0.033264 | 0.045273 | 0.060114 | 0.0029737 | 0.026979 | -0.008372 | 0.032142 | 0.11322 | 0.026197 | 0.036027 | 0.045824 | -0.00067729 | 0.031417 | 0.036621 | 0.073242 | 0.059509 | 0.027466 | 0.064087 | 0.068665 | -0.091553 | 0.091553 | 0.10986 | 0.013733 | 0.032043 | 0.032043 | -0.013733 | -0.064087 | 0.13275 | -0.027466 | -122.1954 | 0.13733 | 0.091553 | 0.11902 | -122.2229 | 0.050354 | 0 | -122.2275 | 0.15564 | 0.07782 | 0.07782 | -122.2275 | 0.12817 | 0.10071 | 0.1236 | -122.3511 | 0.09613 | 0.09613 | 0.17395 | -122.3236
4058.3281 | 122.4792 | -0.045776 | 122.2321 | 0.10956 | 0.0457 | 0.060754 | 0.0010511 | 0.029969 | -0.0013224 | 0.029365 | 0.17426 | 0.027478 | 0.035814 | 0.047533 | 0.0035953 | 0.027999 | 0.064087 | 0.07782 | 0.059509 | 0.036621 | 0.073242 | 0.045776 | -0.11902 | 0.13275 | 0.11444 | 0.022888 | 0.018311 | -0.004578 | -0.004578 | -0.068665 | 0.091552 | -0.073243 | -122.1588 | 0.1236 | 0.082397 | 0.15564 | -122.168 | 0.041198 | -0.022889 | -122.2137 | 0.17853 | 0.068664 | 0.091553 | -122.2366 | 0.11902 | 0.10986 | 0.10528 | -122.3511 | 0.064087 | 0.041198 | 0.16022 | -122.3007
4060.0938 | 122.3557 | -0.086975 | 122.319 | -0.12695 | 0.046555 | 0.062463 | 0.0059643 | 0.02826 | -0.0053812 | 0.029578 | -0.19958 | 0.025769 | 0.037736 | 0.04732 | -0.00089089 | 0.027359 | -0.013733 | 0.009155 | -0.013733 | -0.009155 | 0.10071 | 0.018311 | -0.15106 | 0.022888 | 0.041199 | -0.082397 | 0.068665 | 0.041199 | -0.064087 | -0.12817 | 0.10529 | -0.064087 | -122.2183 | 0.09613 | 0.07782 | 0.14191 | -122.3328 | 0.022888 | -0.041199 | -122.2504 | 0.10986 | 0.004578 | 0.045777 | -122.2778 | 0.18768 | 0.073242 | 0.073242 | -122.4701 | 0.15564 | 0.12817 | 0.12817 | -122.4472
4061.7969 | 122.4884 | -0.07782 | 122.2504 | -0.04303 | 0.0457 | 0.059686 | 0.0034009 | 0.026551 | -0.0075174 | 0.030646 | -0.031738 | 0.025128 | 0.034318 | 0.046892 | -0.0049497 | 0.028427 | 0.032043 | 0.086975 | 0.082397 | 0.045776 | 0.054932 | 0.027466 | -0.09613 | 0.11444 | 0.13733 | 0.064087 | 0.018311 | 0.004578 | -0.018311 | -0.073242 | 0.10529 | -0.01831 | -122.1954 | 0.16479 | 0.1236 | 0.14191 | -122.2183 | 0.059509 | 0.004578 | -122.2321 | 0.19226 | 0.14191 | 0.13733 | -122.2458 | 0.13275 | 0.10986 | 0.16022 | -122.3465 | 0.096131 | 0.082398 | 0.21515 | -122.3236
4063.5938 | 122.4106 | -0.068665 | 122.2504 | 0.079041 | 0.042069 | 0.058191 | 0.0014783 | 0.02591 | -0.004313 | 0.030006 | 0.090332 | 0.027265 | 0.036027 | 0.049029 | 0.00039091 | 0.030136 | 0.091553 | 0.091553 | 0.09613 | 0.036621 | 0.054932 | 0.050354 | -0.082397 | 0.11902 | 0.10071 | 0.009155 | 0.050354 | 0.022888 | -0.013733 | -0.068665 | 0.11902 | -0.013732 | -122.1954 | 0.16022 | 0.10529 | 0.11902 | -122.1588 | 0.054932 | 0 | -122.2 | 0.18768 | 0.07782 | 0.07782 | -122.2275 | 0.1236 | 0.16022 | 0.16479 | -122.3328 | 0.11902 | 0.091553 | 0.16937 | -122.319
4065.3906 | 122.4014 | -0.041199 | 122.2549 | 0.14008 | 0.04506 | 0.059259 | 0.0014783 | 0.030183 | -0.001536 | 0.028297 | 0.10559 | 0.024701 | 0.034959 | 0.045397 | 0.0035953 | 0.028854 | 0.09613 | 0.12817 | 0.10529 | 0.059509 | 0.045776 | 0.054932 | -0.086975 | 0.16022 | 0.11902 | 0.041199 | 0.027466 | 0 | -0.027466 | -0.059509 | 0.096131 | -0.045776 | -122.2092 | 0.16937 | 0.10071 | 0.14648 | -122.1588 | 0.013733 | -0.01831 | -122.2275 | 0.20142 | 0.082398 | 0.10071 | -122.2549 | 0.086975 | 0.13733 | 0.14649 | -122.3419 | 0.068665 | 0.041199 | 0.16022 | -122.3145
4067.1406 | 122.3602 | -0.10529 | 122.2961 | -0.22614 | 0.049332 | 0.060114 | 0.0059643 | 0.02826 | -0.003245 | 0.029365 | -0.27588 | 0.02876 | 0.038164 | 0.047747 | -0.0017453 | 0.029068 | 0.013733 | -0.013733 | -0.027466 | -0.009155 | 0.09613 | 0 | -0.14648 | 0.027466 | 0.022888 | -0.082397 | 0.073242 | 0.054932 | -0.050354 | -0.10071 | 0.10529 | -0.041198 | -122.2 | 0.091553 | 0.096131 | 0.13733 | -122.2824 | 0.054932 | 0.004578 | -122.2229 | 0.13275 | 0.022889 | 0.018311 | -122.2412 | 0.20142 | 0.11902 | 0.07782 | -122.4426 | 0.17853 | 0.16022 | 0.12817 | -122.3969
4068.8438 | 122.4243 | -0.050354 | 122.2549 | 0.063782 | 0.046341 | 0.060754 | 0.0014783 | 0.029542 | -0.0036722 | 0.032142 | 0.159 | 0.024701 | 0.034318 | 0.04732 | 0.0010317 | 0.030136 | 0.073242 | 0.11902 | 0.10071 | 0.050354 | 0.054932 | 0.054932 | -0.091553 | 0.14648 | 0.10529 | 0.022888 | 0.018311 | 0.013733 | -0.018311 | -0.064087 | 0.10529 | -0.041199 | -122.2 | 0.16937 | 0.10071 | 0.14191 | -122.1817 | 0.032043 | -0.013733 | -122.2366 | 0.19684 | 0.073242 | 0.086975 | -122.2412 | 0.10529 | 0.1236 | 0.15106 | -122.3465 | 0.068665 | 0.064087 | 0.15564 | -122.319
4070.6094 | 122.4701 | -0.054932 | 122.2549 | -0.11932 | 0.044632 | 0.060327 | 0.0055371 | 0.031037 | -0.004954 | 0.029365 | -0.1004 | 0.022992 | 0.035173 | 0.04732 | -0.0030271 | 0.029708 | 0.091553 | 0.15106 | 0.11902 | 0.064087 | 0.068665 | 0.032043 | -0.10071 | 0.17395 | 0.16937 | 0.073242 | 0.009155 | 0.018311 | -0.004578 | -0.054932 | 0.086975 | -0.045776 | -122.1863 | 0.20599 | 0.11902 | 0.1648 | -122.1634 | 0.050354 | 0 | -122.2458 | 0.22888 | 0.12817 | 0.12817 | -122.2366 | 0.1236 | 0.14649 | 0.17395 | -122.3557 | 0.064087 | 0.073243 | 0.22431 | -122.3099
4072.375 | 122.3969 | -0.073242 | 122.2687 | -0.18036 | 0.04506 | 0.060754 | 0.0029737 | 0.032533 | 0.0012412 | 0.030219 | -0.26825 | 0.028119 | 0.034532 | 0.048815 | 0.0020999 | 0.02565 | 0.027466 | 0.013733 | -0.018311 | -0.004578 | 0.091553 | -0.004578 | -0.1236 | 0.064087 | 0.064087 | -0.068665 | 0.059509 | 0.050354 | -0.064087 | -0.091553 | 0.068664 | -0.050354 | -122.1771 | 0.086975 | 0.068664 | 0.11902 | -122.2412 | 0.009155 | -0.018311 | -122.2092 | 0.13733 | 0.004577 | 0.022888 | -122.2183 | 0.16479 | 0.10071 | 0.054931 | -122.3923 | 0.13275 | 0.1236 | 0.13733 | -122.3602
4074.1562 | 122.3648 | -0.082397 | 122.2549 | -0.11932 | 0.048477 | 0.060754 | 0.00019645 | 0.029542 | 0.0012412 | 0.030006 | -0.16907 | 0.029187 | 0.034746 | 0.048388 | 0.0029543 | 0.027572 | 0.064087 | 0.064087 | 0.013733 | 0.022888 | 0.091553 | 0.013733 | -0.13275 | 0.086975 | 0.082397 | -0.050354 | 0.050354 | 0.032043 | -0.068665 | -0.086975 | 0.09613 | -0.050354 | -122.1634 | 0.14648 | 0.10528 | 0.15564 | -122.1909 | 0.013732 | -0.004578 | -122.2046 | 0.16937 | 0.032043 | 0.036621 | -122.2229 | 0.17395 | 0.14648 | 0.09613 | -122.3877 | 0.13275 | 0.11444 | 0.16479 | -122.3419
4075.8594 | 122.493 | -0.064087 | 122.2412 | -0.020142 | 0.045273 | 0.06225 | -0.0010851 | 0.026338 | -0.010295 | 0.02851 | 0.021668 | 0.023419 | 0.037096 | 0.045824 | -0.00024989 | 0.030563 | 0.009155 | 0.07782 | 0.064087 | 0.032043 | 0.07782 | 0.027466 | -0.12817 | 0.10986 | 0.10529 | 0.018311 | 0.036621 | 0.036621 | -0.027466 | -0.068665 | 0.091553 | -0.064087 | -122.1634 | 0.14191 | 0.09613 | 0.16022 | -122.2321 | 0.036621 | -0.004578 | -122.2046 | 0.17395 | 0.082398 | 0.086976 | -122.2046 | 0.14191 | 0.073242 | 0.12817 | -122.3694 | 0.10071 | 0.10071 | 0.16937 | -122.3099
4077.625 | 122.3557 | -0.09613 | 122.2778 | -0.096436 | 0.048905 | 0.062036 | 0.0012647 | 0.029115 | -0.00046778 | 0.030433 | -0.13855 | 0.028546 | 0.034746 | 0.047747 | 0.0027407 | 0.028854 | 0.068665 | 0.068665 | 0.036621 | 0.036621 | 0.073242 | 0.022888 | -0.14191 | 0.091553 | 0.086975 | -0.045776 | 0.054932 | 0.045776 | -0.045776 | -0.091553 | 0.11902 | -0.045777 | -122.2046 | 0.16479 | 0.13275 | 0.17853 | -122.2092 | 0.050354 | 0.004577 | -122.2229 | 0.18768 | 0.050354 | 0.045777 | -122.2321 | 0.16937 | 0.16479 | 0.13275 | -122.4197 | 0.15106 | 0.14191 | 0.1831 | -122.3694
4079.3906 | 122.3465 | -0.10529 | 122.2595 | -0.26428 | 0.048691 | 0.060114 | 0.0098097 | 0.029969 | -0.0053812 | 0.031501 | -0.1767 | 0.02641 | 0.038377 | 0.045611 | -0.00089089 | 0.032272 | 0.032043 | 0.07782 | 0.059509 | 0.045776 | 0.068665 | 0.032043 | -0.10529 | 0.041199 | 0.086975 | -0.054932 | 0.050354 | 0.041199 | -0.036621 | -0.10529 | 0.13733 | 0 | -122.1909 | 0.18311 | 0.15106 | 0.15106 | -122.2275 | 0.068665 | 0 | -122.2092 | 0.14649 | 0.050354 | 0.050354 | -122.2183 | 0.17395 | 0.13733 | 0.16479 | -122.3648 | 0.15564 | 0.14649 | 0.19226 | -122.3648
4081.2031 | 122.4747 | -0.045776 | 122.2275 | 0.14771 | 0.045914 | 0.060968 | -0.0025805 | 0.030824 | -0.0030314 | 0.032783 | 0.097962 | 0.028546 | 0.033464 | 0.049242 | 0.0020999 | 0.029708 | 0.064087 | 0.09613 | 0.059509 | 0.041199 | 0.050354 | 0.050354 | -0.09613 | 0.12817 | 0.13275 | 0.022888 | 0.036621 | 0.009155 | -0.018311 | -0.059509 | 0.09613 | -0.050354 | -122.1771 | 0.14191 | 0.086975 | 0.13733 | -122.1634 | 0.027465 | -0.013733 | -122.1909 | 0.17395 | 0.068664 | 0.082397 | -122.2183 | 0.09613 | 0.10986 | 0.10528 | -122.3236 | 0.082397 | 0.054931 | 0.17853 | -122.287
4082.9844 | 122.3282 | -0.091553 | 122.2916 | -0.065918 | 0.046982 | 0.057977 | 0.00083745 | 0.028047 | 0.0014548 | 0.030646 | -0.062256 | 0.02876 | 0.035387 | 0.050951 | 0.0018863 | 0.026291 | 0.050354 | 0.032043 | 0.009155 | 0.027466 | 0.086975 | 0.018311 | -0.13275 | 0.054932 | 0.050354 | -0.09613 | 0.045776 | 0.050354 | -0.045776 | -0.09613 | 0.10986 | -0.041198 | -122.2046 | 0.1236 | 0.11902 | 0.16022 | -122.2412 | 0.045777 | -0.004577 | -122.2458 | 0.14649 | -0.004577 | 0 | -122.2412 | 0.17853 | 0.14191 | 0.10071 | -122.4243 | 0.13733 | 0.14191 | 0.14191 | -122.3877
4084.7031 | 122.4289 | -0.054932 | 122.2733 | 0.094299 | 0.046128 | 0.058832 | 0.0027601 | 0.027833 | -0.0062356 | 0.031501 | 0.15137 | 0.028546 | 0.036241 | 0.048174 | -0.0023861 | 0.031631 | 0.059509 | 0.1236 | 0.10071 | 0.068665 | 0.050354 | 0.050354 | -0.082397 | 0.12817 | 0.10529 | 0.022888 | 0.013733 | 0.009155 | -0.027466 | -0.064087 | 0.10529 | -0.027465 | -122.2229 | 0.17853 | 0.1236 | 0.15106 | -122.2137 | 0.027466 | -0.009155 | -122.2595 | 0.18311 | 0.07782 | 0.086975 | -122.2641 | 0.10529 | 0.11444 | 0.15564 | -122.3557 | 0.068665 | 0.064087 | 0.16022 | -122.3373
4086.4219 | 122.3923 | -0.11902 | 122.2733 | -0.19562 | 0.046341 | 0.059686 | 0.0040417 | 0.029542 | -0.0021768 | 0.030006 | -0.20721 | 0.028974 | 0.038164 | 0.051165 | -0.00089089 | 0.027786 | 0.004578 | -0.018311 | -0.032043 | 0 | 0.09613 | 0.013733 | -0.13733 | 0.027466 | 0.050354 | -0.07782 | 0.07782 | 0.054932 | -0.050354 | -0.091553 | 0.13275 | -0.01831 | -122.1771 | 0.10071 | 0.11902 | 0.13733 | -122.2687 | 0.068665 | 0.027466 | -122.1954 | 0.14649 | 0.041199 | 0.013733 | -122.2183 | 0.21515 | 0.1236 | 0.086976 | -122.4106 | 0.19684 | 0.17395 | 0.16937 | -122.3648
4088.1719 | 122.4747 | -0.054932 | 122.1954 | 0.14008 | 0.045273 | 0.060754 | 0.00083745 | 0.028901 | -0.002604 | 0.032355 | 0.13611 | 0.027265 | 0.0356 | 0.049883 | 0.00081811 | 0.028854 | 0.032043 | 0.018311 | 0.027466 | 0.013733 | 0.082397 | 0.045776 | -0.086975 | 0.13275 | 0.09613 | 0 | 0.013733 | 0.018311 | -0.013733 | -0.068665 | 0.10071 | -0.032043 | -122.113 | 0.073243 | 0.068665 | 0.10071 | -122.1634 | 0.041199 | -0.013733 | -122.1817 | 0.18768 | 0.054932 | 0.068665 | -122.1771 | 0.13733 | 0.086975 | 0.082398 | -122.2824 | 0.068665 | 0.073243 | 0.15106 | -122.2641
4089.875 | 122.438 | -0.07782 | 122.2412 | 0.010376 | 0.044205 | 0.062677 | 0.0023329 | 0.029115 | -0.010081 | 0.030006 | 0.075073 | 0.025556 | 0.034959 | 0.045183 | -0.0011045 | 0.031204 | 0.032043 | 0.073242 | 0.064087 | 0.022888 | 0.059509 | 0.050354 | -0.09613 | 0.091553 | 0.09613 | 0.013733 | 0.032043 | 0.032043 | -0.022888 | -0.086975 | 0.12817 | -0.01831 | -122.1817 | 0.15106 | 0.10071 | 0.11902 | -122.2092 | 0.054932 | -0.009155 | -122.2092 | 0.16937 | 0.091553 | 0.10071 | -122.2092 | 0.13733 | 0.10986 | 0.14191 | -122.3373 | 0.10986 | 0.10986 | 0.17395 | -122.3282
4091.625 | 122.3877 | -0.082397 | 122.2824 | -0.20325 | 0.045487 | 0.063318 | 0.0046827 | 0.028474 | -0.0051676 | 0.028937 | -0.13092 | 0.026624 | 0.037309 | 0.046038 | -0.00024989 | 0.028427 | 0.082397 | 0.12817 | 0.10986 | 0.07782 | 0.054932 | 0.041199 | -0.09613 | 0.11444 | 0.16479 | 0.018311 | 0.045776 | 0.018311 | -0.004578 | -0.086975 | 0.1236 | -0.013733 | -122.2275 | 0.21057 | 0.16022 | 0.17395 | -122.2 | 0.077819 | -0.004578 | -122.2366 | 0.19684 | 0.10071 | 0.10529 | -122.2641 | 0.13733 | 0.16479 | 0.19226 | -122.3785 | 0.12817 | 0.10071 | 0.24719 | -122.3694
4093.3281 | 122.3877 | -0.10071 | 122.2687 | 0.079041 | 0.047409 | 0.061823 | 0.00062385 | 0.030824 | -4.058e-05 | 0.03086 | 0.067444 | 0.02641 | 0.033678 | 0.049456 | 0.00039091 | 0.027999 | 0.009155 | -0.041199 | -0.045776 | -0.009155 | 0.11444 | 0.004578 | -0.14191 | 0.032043 | -0.018311 | -0.10529 | 0.091553 | 0.036621 | -0.059509 | -0.10986 | 0.10529 | -0.041199 | -122.1542 | 0.059509 | 0.091553 | 0.13275 | -122.2595 | 0.041199 | -0.009155 | -122.1771 | 0.13275 | -0.004578 | 0.004577 | -122.2321 | 0.21515 | 0.10986 | 0.054932 | -122.4106 | 0.19226 | 0.13733 | 0.082397 | -122.3785
4095.0312 | 122.4426 | -0.059509 | 122.2916 | -0.15747 | 0.047837 | 0.06225 | 0.0066053 | 0.028474 | -0.008372 | 0.030006 | -0.16907 | 0.02641 | 0.03795 | 0.048174 | -0.00024989 | 0.029281 | 0.10986 | 0.14191 | 0.11444 | 0.073242 | 0.068665 | 0.022888 | -0.073242 | 0.1236 | 0.19226 | 0.064087 | 0.018311 | 0.009155 | -0.022888 | -0.082397 | 0.082397 | -0.013733 | -122.2229 | 0.20142 | 0.13275 | 0.14648 | -122.1817 | 0.036621 | -0.022888 | -122.2733 | 0.1831 | 0.1236 | 0.14648 | -122.2824 | 0.12817 | 0.16937 | 0.17395 | -122.3648 | 0.07782 | 0.068664 | 0.25177 | -122.374
4096.7188 | 122.3602 | -0.10529 | 122.2733 | 0.071411 | 0.049332 | 0.059045 | 0.0034009 | 0.026551 | 0.00081382 | 0.029578 | 0.029297 | 0.02641 | 0.036027 | 0.049669 | 0.0035953 | 0.027359 | 0.009155 | -0.032043 | -0.032043 | -0.018311 | 0.09613 | 0 | -0.12817 | 0.022888 | -0.009155 | -0.10071 | 0.082397 | 0.050354 | -0.050354 | -0.10529 | 0.10529 | -0.022888 | -122.1771 | 0.073243 | 0.086975 | 0.10986 | -122.2641 | 0.054932 | 0 | -122.1909 | 0.12817 | 0.004578 | 0.004578 | -122.2229 | 0.20142 | 0.11444 | 0.073243 | -122.4014 | 0.18768 | 0.15564 | 0.096131 | -122.3785
4098.4219 | 122.4838 | -0.068665 | 122.2504 | -0.050659 | 0.04506 | 0.061182 | 0.0076733 | 0.031678 | -0.0079446 | 0.02851 | -0.039368 | 0.025128 | 0.036241 | 0.048601 | -0.0036679 | 0.029708 | 0.036621 | 0.07782 | 0.10071 | 0.064087 | 0.07782 | 0.050354 | -0.10071 | 0.11902 | 0.14191 | 0.050354 | 0.022888 | 0.013733 | -0.013733 | -0.068665 | 0.11902 | -0.032043 | -122.1725 | 0.14649 | 0.13275 | 0.1648 | -122.2137 | 0.054932 | 0 | -122.2275 | 0.18768 | 0.11902 | 0.11902 | -122.2366 | 0.14649 | 0.10529 | 0.16937 | -122.3511 | 0.091553 | 0.082398 | 0.21057 | -122.319
4100.125 | 122.374 | -0.086975 | 122.287 | -0.18799 | 0.046128 | 0.058405 | 0.0051099 | 0.031465 | 0.0014548 | 0.029578 | -0.23773 | 0.02876 | 0.0356 | 0.049456 | 0.0031681 | 0.027572 | 0.022888 | -0.013733 | -0.022888 | 0.018311 | 0.082397 | 0.004578 | -0.13733 | 0.073242 | 0.054932 | -0.064087 | 0.054932 | 0.059509 | -0.045776 | -0.10529 | 0.091553 | -0.050354 | -122.2046 | 0.073242 | 0.10529 | 0.15564 | -122.2641 | 0.041199 | -0.018311 | -122.2321 | 0.16022 | 0.022888 | 0.041199 | -122.2275 | 0.16937 | 0.10986 | 0.064087 | -122.4243 | 0.14191 | 0.14648 | 0.14191 | -122.3923
4101.8281 | 122.4838 | -0.050354 | 122.2504 | -0.12695 | 0.0457 | 0.062463 | 0.0012647 | 0.029756 | -0.007731 | 0.029365 | -0.069885 | 0.023633 | 0.037736 | 0.047961 | -0.0013181 | 0.028854 | 0.091553 | 0.15564 | 0.10529 | 0.07782 | 0.059509 | 0.050354 | -0.11444 | 0.16937 | 0.17395 | 0.07782 | 0.018311 | 0.018311 | -0.022888 | -0.064087 | 0.10071 | -0.064087 | -122.1909 | 0.20599 | 0.12817 | 0.19226 | -122.1588 | 0.027466 | -0.013733 | -122.2321 | 0.21973 | 0.12817 | 0.14191 | -122.2321 | 0.10986 | 0.14191 | 0.15564 | -122.3648 | 0.068665 | 0.068665 | 0.2243 | -122.3145
4103.5781 | 122.4518 | -0.050354 | 122.2458 | 0.12482 | 0.0457 | 0.059045 | 0.00019645 | 0.031037 | -0.0036722 | 0.032142 | 0.14374 | 0.026837 | 0.0356 | 0.04732 | 0.0035953 | 0.026931 | 0.10986 | 0.086975 | 0.091553 | 0.073242 | 0.054932 | 0.045776 | -0.073242 | 0.15564 | 0.11444 | 0.036621 | 0.009155 | -0.009155 | 0.004578 | -0.068665 | 0.09613 | -0.022888 | -122.1909 | 0.13733 | 0.1236 | 0.14648 | -122.1359 | 0.054932 | -0.018311 | -122.2366 | 0.20599 | 0.086975 | 0.10529 | -122.2549 | 0.10529 | 0.16022 | 0.14191 | -122.319 | 0.059509 | 0.041199 | 0.16479 | -122.3145
4105.2812 | 122.3648 | -0.09613 | 122.2733 | -0.21088 | 0.047623 | 0.06225 | 0.0055371 | 0.029969 | -0.003245 | 0.031074 | -0.28351 | 0.028333 | 0.036455 | 0.047961 | -0.00046349 | 0.026931 | -0.004578 | -0.018311 | -0.018311 | -0.004578 | 0.091553 | 0.013733 | -0.12817 | 0.018311 | 0.022888 | -0.082397 | 0.082397 | 0.068665 | -0.059509 | -0.10529 | 0.10986 | -0.032044 | -122.1817 | 0.077819 | 0.091552 | 0.1236 | -122.2778 | 0.036621 | -0.009156 | -122.1909 | 0.11444 | 0.013733 | 0.022889 | -122.2046 | 0.18768 | 0.091552 | 0.077819 | -122.4014 | 0.17853 | 0.16479 | 0.11902 | -122.3785
4106.9844 | 122.4609 | -0.045776 | 122.2549 | -0.17273 | 0.046341 | 0.060968 | 0.0063917 | 0.027192 | -0.007731 | 0.028297 | -0.14618 | 0.024701 | 0.036027 | 0.047533 | -0.0015317 | 0.030136 | 0.10529 | 0.15106 | 0.11444 | 0.068665 | 0.064087 | 0.041199 | -0.086975 | 0.15564 | 0.19684 | 0.068665 | 0.022888 | 0.013733 | -0.022888 | -0.073242 | 0.086975 | -0.041199 | -122.1909 | 0.19684 | 0.11444 | 0.15564 | -122.1497 | 0.022888 | -0.027466 | -122.2321 | 0.20142 | 0.11444 | 0.14191 | -122.2412 | 0.10986 | 0.15106 | 0.16022 | -122.3419 | 0.068664 | 0.059509 | 0.24261 | -122.3282
4108.6875 | 122.3511 | -0.09613 | 122.2687 | 0.079041 | 0.049118 | 0.060754 | -0.0017261 | 0.028901 | 0.0027364 | 0.029365 | -0.016479 | 0.027906 | 0.035173 | 0.049242 | 0.0042361 | 0.027572 | 0.013733 | -0.027466 | -0.045776 | -0.018311 | 0.10986 | 0.018311 | -0.1236 | 0.022888 | 0.009155 | -0.11902 | 0.068665 | 0.068665 | -0.050354 | -0.10529 | 0.11444 | -0.027466 | -122.1588 | 0.068664 | 0.077819 | 0.10528 | -122.2549 | 0.045776 | -0.009156 | -122.2 | 0.11902 | -0.022889 | -0.013733 | -122.2 | 0.20599 | 0.10986 | 0.050354 | -122.3923 | 0.16479 | 0.16479 | 0.10528 | -122.374
4110.375 | 122.4564 | -0.054932 | 122.2458 | -0.11932 | 0.0457 | 0.061182 | 0.0059643 | 0.031892 | -0.007731 | 0.030646 | -0.062256 | 0.02406 | 0.038591 | 0.048174 | -0.0036679 | 0.029495 | 0.086975 | 0.16937 | 0.12817 | 0.07782 | 0.064087 | 0.045776 | -0.10529 | 0.17853 | 0.19226 | 0.091553 | 0.018311 | 0.013733 | -0.004578 | -0.082397 | 0.10071 | -0.050354 | -122.1817 | 0.22431 | 0.13275 | 0.18311 | -122.1588 | 0.050354 | -0.027465 | -122.2275 | 0.23346 | 0.14649 | 0.17395 | -122.2321 | 0.11902 | 0.14191 | 0.18311 | -122.3511 | 0.073243 | 0.068665 | 0.24719 | -122.3282
4112.0781 | 122.4014 | -0.10986 | 122.287 | -0.17273 | 0.048905 | 0.062677 | 0.0046827 | 0.031037 | -0.0013224 | 0.029578 | -0.2301 | 0.028974 | 0.036241 | 0.049456 | 0.0012455 | 0.025863 | 0.018311 | 0.009155 | -0.022888 | 0.009155 | 0.10529 | 0.004578 | -0.12817 | 0.050354 | 0.064087 | -0.054932 | 0.073242 | 0.050354 | -0.064087 | -0.10986 | 0.11444 | -0.018311 | -122.1817 | 0.11902 | 0.11902 | 0.13733 | -122.2687 | 0.045776 | 0 | -122.2137 | 0.16022 | 0.054931 | 0.054931 | -122.2366 | 0.21515 | 0.12817 | 0.086975 | -122.4152 | 0.18311 | 0.16022 | 0.17395 | -122.3969
4113.7812 | 122.4655 | -0.045776 | 122.2183 | 0.15533 | 0.047196 | 0.060541 | -0.0017261 | 0.028901 | -0.0030314 | 0.030006 | 0.13611 | 0.024701 | 0.034746 | 0.047747 | 0.0046633 | 0.029281 | 0.022888 | 0.041199 | 0.032043 | 0.013733 | 0.082397 | 0.022888 | -0.10986 | 0.12817 | 0.09613 | 0.009155 | 0.013733 | 0.022888 | -0.013733 | -0.07782 | 0.068664 | -0.064087 | -122.1359 | 0.086975 | 0.059509 | 0.1236 | -122.1954 | 0.032043 | -0.032044 | -122.2046 | 0.17395 | 0.054931 | 0.086975 | -122.1954 | 0.12817 | 0.068664 | 0.077819 | -122.3282 | 0.059509 | 0.068664 | 0.14191 | -122.2961
4115.5312 | 122.4152 | -0.068665 | 122.2412 | 0.094299 | 0.045914 | 0.060754 | 0.0019055 | 0.02826 | -0.0013224 | 0.032569 | 0.059815 | 0.029615 | 0.035173 | 0.049242 | 0.0016727 | 0.028854 | -0.009155 | -0.032043 | -0.045776 | -0.009155 | 0.10529 | 0.009155 | -0.11444 | 0.041199 | 0 | -0.082397 | 0.050354 | 0.068665 | -0.045776 | -0.11444 | 0.07782 | -0.045776 | -122.1359 | 0.036622 | 0.05951 | 0.10529 | -122.2504 | 0.022889 | -0.045776 | -122.1909 | 0.10986 | -0.013732 | 0.032044 | -122.1725 | 0.17395 | 0.05951 | 0.022889 | -122.3557 | 0.11902 | 0.13733 | 0.068665 | -122.3557
4117.2344 | 122.4747 | -0.054932 | 122.2641 | -0.088806 | 0.045914 | 0.061609 | 0.0083143 | 0.030183 | -0.0079446 | 0.031928 | -0.069885 | 0.025128 | 0.036027 | 0.046038 | -0.0034543 | 0.030777 | 0.07782 | 0.13733 | 0.10529 | 0.068665 | 0.059509 | 0.041199 | -0.11444 | 0.15106 | 0.16479 | 0.07782 | 0.022888 | -0.004578 | -0.036621 | -0.064087 | 0.096131 | -0.059509 | -122.2046 | 0.19226 | 0.1236 | 0.18311 | -122.1863 | 0.018311 | -0.009155 | -122.2412 | 0.20599 | 0.13275 | 0.14191 | -122.2687 | 0.11444 | 0.13275 | 0.16022 | -122.3785 | 0.07782 | 0.050354 | 0.21973 | -122.3282
4118.9375 | 122.3419 | -0.10529 | 122.2641 | -0.027771 | 0.046341 | 0.060541 | 0.0014783 | 0.029756 | 0.0010276 | 0.031287 | -0.0012209 | 0.027906 | 0.037096 | 0.045611 | 0.0042361 | 0.029495 | 0.009155 | -0.027466 | -0.032043 | -0.009155 | 0.07782 | 0.022888 | -0.12817 | 0.004578 | -0.009155 | -0.13275 | 0.045776 | 0.045776 | -0.050354 | -0.10986 | 0.12817 | -0.022888 | -122.1863 | 0.07782 | 0.096131 | 0.11902 | -122.2549 | 0.054932 | -0.004577 | -122.2183 | 0.10986 | -0.027465 | -0.022888 | -122.2183 | 0.18311 | 0.11444 | 0.073243 | -122.3923 | 0.15106 | 0.15106 | 0.096131 | -122.374
4120.6406 | 122.4426 | -0.054932 | 122.2229 | 0.13245 | 0.044419 | 0.060754 | 0.0014783 | 0.030183 | -0.0055948 | 0.031287 | 0.18188 | 0.027051 | 0.0356 | 0.047106 | 0.0035953 | 0.029708 | 0.091553 | 0.1236 | 0.10071 | 0.082397 | 0.036621 | 0.059509 | -0.086975 | 0.15564 | 0.13733 | 0.041199 | 0.009155 | 0.009155 | -0.041199 | -0.073242 | 0.11444 | -0.032043 | -122.1863 | 0.17853 | 0.13733 | 0.16937 | -122.1313 | 0.013733 | -0.01831 | -122.2137 | 0.21057 | 0.096131 | 0.11444 | -122.2137 | 0.091553 | 0.14649 | 0.15564 | -122.3099 | 0.064087 | 0.064087 | 0.19226 | -122.2961
4122.3281 | 122.3923 | -0.086975 | 122.2824 | -0.19562 | 0.050827 | 0.0599 | 0.0061781 | 0.032746 | -0.00089518 | 0.031714 | -0.2301 | 0.028119 | 0.037096 | 0.048388 | -0.00024989 | 0.027786 | -0.004578 | -0.009155 | -0.032043 | 0.009155 | 0.10071 | 0.004578 | -0.14191 | 0.022888 | 0.059509 | -0.07782 | 0.086975 | 0.059509 | -0.050354 | -0.10529 | 0.091553 | -0.054932 | -122.1817 | 0.07782 | 0.09613 | 0.15106 | -122.287 | 0.036621 | -0.018311 | -122.1954 | 0.10986 | 0.009155 | 0.027466 | -122.2229 | 0.18768 | 0.082397 | 0.054932 | -122.4243 | 0.17395 | 0.14648 | 0.14648 | -122.3877
4124.0312 | 122.4609 | -0.050354 | 122.2412 | 0.10956 | 0.047623 | 0.061609 | -0.0025805 | 0.03061 | -0.0047404 | 0.031074 | 0.097962 | 0.025342 | 0.035387 | 0.048174 | 0.0029543 | 0.027999 | 0.082397 | 0.082397 | 0.073242 | 0.073242 | 0.050354 | 0.041199 | -0.07782 | 0.14648 | 0.12817 | 0.041199 | 0.013733 | 0.009155 | -0.009155 | -0.064087 | 0.091553 | -0.027466 | -122.1909 | 0.13275 | 0.1236 | 0.15106 | -122.1588 | 0.041199 | -0.013733 | -122.2275 | 0.19684 | 0.091553 | 0.10529 | -122.2321 | 0.10071 | 0.13275 | 0.1236 | -122.319 | 0.064087 | 0.059509 | 0.17853 | -122.3053
4125.75 | 122.4747 | -0.050354 | 122.2275 | 0.063782 | 0.047196 | 0.061395 | 0.0019055 | 0.03061 | -0.0030314 | 0.031287 | 0.15137 | 0.028119 | 0.034318 | 0.049883 | 0.0018863 | 0.029068 | 0.018311 | 0 | 0 | 0.009155 | 0.091553 | -0.004578 | -0.11902 | 0.07782 | 0.022888 | -0.045776 | 0.050354 | 0.013733 | -0.036621 | -0.10529 | 0.045776 | -0.068665 | -122.1359 | 0.050354 | 0.059509 | 0.12817 | -122.2092 | 0.013733 | -0.054932 | -122.1771 | 0.12817 | 0.004578 | 0.05951 | -122.2137 | 0.14191 | 0.068665 | 0.050354 | -122.3465 | 0.10071 | 0.064087 | 0.073242 | -122.3328
4127.4375 | 122.3969 | -0.064087 | 122.2549 | 0.08667 | 0.043778 | 0.061823 | 0.0023329 | 0.029756 | -0.0064492 | 0.027869 | 0.11322 | 0.02406 | 0.036027 | 0.048174 | -0.00046349 | 0.030349 | 0.041199 | 0.10071 | 0.082397 | 0.050354 | 0.050354 | 0.050354 | -0.09613 | 0.10529 | 0.09613 | 0.009155 | 0.022888 | -0.004578 | -0.036621 | -0.082397 | 0.11444 | -0.032043 | -122.2046 | 0.1648 | 0.11444 | 0.14648 | -122.2137 | 0.027466 | -0.01831 | -122.2321 | 0.16937 | 0.073242 | 0.091552 | -122.2595 | 0.11444 | 0.10529 | 0.14648 | -122.3511 | 0.086975 | 0.059509 | 0.16022 | -122.3373
4129.1406 | 122.4197 | -0.068665 | 122.2412 | 0.071411 | 0.043991 | 0.061182 | 0.0023329 | 0.029756 | -0.0079446 | 0.030219 | 0.159 | 0.027265 | 0.034532 | 0.046038 | -3.629e-05 | 0.028854 | 0.07782 | 0.11902 | 0.091553 | 0.059509 | 0.041199 | 0.050354 | -0.068665 | 0.1236 | 0.10529 | 0.009155 | 0.036621 | 0.018311 | -0.009155 | -0.068665 | 0.11902 | 0 | -122.2 | 0.18768 | 0.12817 | 0.12817 | -122.1634 | 0.05951 | 0 | -122.2046 | 0.19226 | 0.07782 | 0.07782 | -122.2229 | 0.10986 | 0.14649 | 0.16022 | -122.3099 | 0.10529 | 0.086976 | 0.17395 | -122.3099
4130.8281 | 122.374 | -0.11444 | 122.2733 | -0.24902 | 0.047196 | 0.061609 | 0.0081007 | 0.030397 | -0.0034586 | 0.02851 | -0.24536 | 0.026624 | 0.038805 | 0.049029 | -0.00089089 | 0.026718 | 0.018311 | -0.009155 | -0.041199 | -0.022888 | 0.10986 | 0 | -0.14191 | 0.009155 | 0.032043 | -0.07782 | 0.068665 | 0.050354 | -0.059509 | -0.10529 | 0.11444 | -0.027466 | -122.1634 | 0.10529 | 0.091553 | 0.11902 | -122.2549 | 0.054932 | 0.009155 | -122.2046 | 0.1236 | 0.036621 | 0.027466 | -122.2229 | 0.2243 | 0.13275 | 0.073242 | -122.4152 | 0.18311 | 0.16479 | 0.14648 | -122.3785
4132.5312 | 122.3923 | -0.07782 | 122.2504 | 0.10956 | 0.048477 | 0.060968 | 0.0023329 | 0.028474 | 0.0012412 | 0.033423 | 0.044556 | 0.027478 | 0.036241 | 0.048601 | 0.0044497 | 0.031845 | 0.004578 | -0.018311 | -0.027466 | -0.013733 | 0.10529 | 0 | -0.1236 | 0.041199 | -0.009155 | -0.086975 | 0.073242 | 0.050354 | -0.054932 | -0.10986 | 0.07782 | -0.045776 | -122.1451 | 0.059509 | 0.064087 | 0.10986 | -122.2458 | 0.022888 | -0.032043 | -122.1771 | 0.11902 | -0.009155 | 0.022888 | -122.2 | 0.18311 | 0.082398 | 0.050354 | -122.374 | 0.15106 | 0.12817 | 0.068665 | -122.3602
4134.25 | 122.3923 | -0.09613 | 122.2733 | -0.22614 | 0.047623 | 0.060327 | 0.0083143 | 0.029542 | -0.0021768 | 0.031287 | -0.19196 | 0.028333 | 0.035814 | 0.049029 | 0.00081811 | 0.027359 | 0 | -0.009155 | -0.022888 | 0 | 0.10529 | 0.004578 | -0.12817 | 0.013733 | 0.027466 | -0.07782 | 0.064087 | 0.045776 | -0.059509 | -0.10529 | 0.10071 | -0.032044 | -122.168 | 0.086975 | 0.09613 | 0.12817 | -122.2733 | 0.036621 | -0.009156 | -122.2092 | 0.10986 | 0.01831 | 0.027466 | -122.2275 | 0.20142 | 0.09613 | 0.073242 | -122.4014 | 0.16022 | 0.14191 | 0.1236 | -122.3785
4135.9375 | 122.4518 | -0.045776 | 122.2275 | 0.0027468 | 0.042069 | 0.0599 | 0.0014783 | 0.029542 | -0.008372 | 0.031501 | 0.052185 | 0.025342 | 0.033464 | 0.046465 | 0.00039091 | 0.030349 | 0.013733 | 0.050354 | 0.054932 | 0.018311 | 0.064087 | 0.050354 | -0.09613 | 0.086975 | 0.086975 | 0 | 0.036621 | 0.018311 | -0.032043 | -0.082397 | 0.09613 | -0.050354 | -122.1634 | 0.09613 | 0.064087 | 0.11444 | -122.2137 | 0.013733 | -0.036621 | -122.1909 | 0.13275 | 0.045776 | 0.082397 | -122.2092 | 0.10986 | 0.059509 | 0.10071 | -122.3236 | 0.082397 | 0.064087 | 0.13275 | -122.3099
4137.6406 | 122.4609 | -0.07782 | 122.2504 | -0.15747 | 0.0457 | 0.060541 | 0.0038281 | 0.031251 | -0.0062356 | 0.028083 | -0.16144 | 0.024701 | 0.035387 | 0.049029 | -0.0030271 | 0.030136 | 0.09613 | 0.15106 | 0.1236 | 0.091553 | 0.041199 | 0.050354 | -0.086975 | 0.14648 | 0.17853 | 0.054932 | 0.018311 | 0 | -0.027466 | -0.07782 | 0.12817 | -0.009155 | -122.2092 | 0.22888 | 0.16937 | 0.17853 | -122.1542 | 0.050354 | 0 | -122.2321 | 0.2243 | 0.13275 | 0.13275 | -122.2504 | 0.11902 | 0.17395 | 0.20142 | -122.3373 | 0.096131 | 0.07782 | 0.25635 | -122.3282
4139.3438 | 122.3328 | -0.10529 | 122.2824 | -0.081177 | 0.04805 | 0.060754 | -1.7146e-05 | 0.03061 | 0.0040182 | 0.02851 | -0.1004 | 0.02641 | 0.034532 | 0.048815 | 0.0050907 | 0.026077 | 0.064087 | 0.054932 | 0.009155 | 0.032043 | 0.082397 | 0.027466 | -0.10986 | 0.050354 | 0.032043 | -0.082397 | 0.073242 | 0.041199 | -0.068665 | -0.10986 | 0.13275 | -0.004577 | -122.2 | 0.16022 | 0.13733 | 0.14191 | -122.2183 | 0.036621 | -0.004577 | -122.2092 | 0.15564 | 0.022889 | 0.027466 | -122.2412 | 0.18768 | 0.16937 | 0.11444 | -122.3923 | 0.17853 | 0.14649 | 0.13733 | -122.3923
4141.1094 | 122.4335 | -0.045776 | 122.2504 | 0.10193 | 0.046128 | 0.060327 | -0.0015125 | 0.029969 | -0.0030314 | 0.031287 | 0.14374 | 0.026624 | 0.034105 | 0.046038 | 0.0023135 | 0.028427 | 0.09613 | 0.1236 | 0.09613 | 0.064087 | 0.045776 | 0.059509 | -0.091553 | 0.16479 | 0.14648 | 0.054932 | 0.004578 | 0.009155 | -0.018311 | -0.068665 | 0.10528 | -0.045777 | -122.2046 | 0.16937 | 0.10986 | 0.15564 | -122.1542 | 0.027465 | -0.022889 | -122.2458 | 0.21057 | 0.10071 | 0.1236 | -122.2412 | 0.091552 | 0.14191 | 0.14191 | -122.3419 | 0.050354 | 0.054931 | 0.19226 | -122.319
4142.7969 | 122.3648 | -0.091553 | 122.2961 | -0.21851 | 0.046982 | 0.061395 | 0.0081007 | 0.029969 | -0.0023904 | 0.029365 | -0.24536 | 0.025983 | 0.03795 | 0.050738 | -0.0011045 | 0.029068 | -0.018311 | -0.004578 | -0.022888 | -0.027466 | 0.091553 | 0.009155 | -0.15106 | 0.013733 | 0.022888 | -0.073242 | 0.059509 | 0.041199 | -0.064087 | -0.10986 | 0.10071 | -0.059509 | -122.2046 | 0.086975 | 0.064087 | 0.1236 | -122.3145 | 0.027466 | -0.01831 | -122.2366 | 0.10529 | 0.018311 | 0.036621 | -122.2549 | 0.18311 | 0.073242 | 0.068665 | -122.4472 | 0.15106 | 0.13275 | 0.11444 | -122.406
4144.4844 | 122.4655 | -0.054932 | 122.2458 | 0.15533 | 0.047409 | 0.06225 | 0.00019645 | 0.03061 | -0.0030314 | 0.030219 | 0.12848 | 0.027478 | 0.033464 | 0.049883 | 0.0012455 | 0.029281 | 0.036621 | 0.054932 | 0.022888 | 0.018311 | 0.091553 | 0.032043 | -0.10071 | 0.1236 | 0.091553 | 0.004578 | 0.022888 | 0 | -0.018311 | -0.059509 | 0.086975 | -0.045776 | -122.1542 | 0.10986 | 0.073243 | 0.11902 | -122.2092 | 0.036621 | -0.004577 | -122.2229 | 0.17853 | 0.05951 | 0.064087 | -122.2458 | 0.14649 | 0.091553 | 0.07782 | -122.3465 | 0.07782 | 0.054932 | 0.14649 | -122.3053
4146.1875 | 122.4701 | -0.054932 | 122.2366 | -0.45502 | 0.047196 | 0.063104 | 0.0055371 | 0.028474 | -0.010722 | 0.027656 | -0.054626 | 0.024488 | 0.037096 | 0.044329 | -0.0034543 | 0.03099 | 0.082397 | 0.13733 | 0.10529 | 0.073242 | 0.054932 | 0.050354 | -0.09613 | 0.15106 | 0.16479 | 0.082397 | 0.018311 | 0 | -0.013733 | -0.068665 | 0.10529 | -0.041198 | -122.1817 | 0.19226 | 0.12817 | 0.16937 | -122.1542 | 0.041199 | -0.013733 | -122.2183 | 0.20599 | 0.13733 | 0.15106 | -122.2366 | 0.10986 | 0.13733 | 0.16022 | -122.3328 | 0.073243 | 0.054932 | 0.21973 | -122.3053
4147.8906 | 122.3969 | -0.086975 | 122.2778 | -0.18036 | 0.048905 | 0.061395 | 0.0044691 | 0.030824 | -0.0019632 | 0.028297 | -0.22247 | 0.026624 | 0.037096 | 0.048815 | -0.00067729 | 0.026291 | 0.013733 | -0.018311 | -0.022888 | 0.009155 | 0.10529 | 0.009155 | -0.13275 | 0.027466 | 0.041199 | -0.086975 | 0.054932 | 0.064087 | -0.036621 | -0.11902 | 0.09613 | -0.045776 | -122.1725 | 0.068664 | 0.09613 | 0.14191 | -122.2641 | 0.050354 | -0.032044 | -122.2229 | 0.11444 | 0 | 0.032044 | -122.2137 | 0.19226 | 0.10071 | 0.064087 | -122.4106 | 0.14191 | 0.15106 | 0.12817 | -122.3969
4149.6094 | 122.3557 | -0.086975 | 122.2733 | -0.081177 | 0.046982 | 0.061182 | 0.0014783 | 0.031892 | -4.058e-05 | 0.031501 | -0.13855 | 0.027265 | 0.034105 | 0.048815 | 0.0020999 | 0.027999 | 0.073242 | 0.059509 | 0.018311 | 0.036621 | 0.091553 | 0.009155 | -0.1236 | 0.09613 | 0.086975 | -0.041199 | 0.045776 | 0.041199 | -0.054932 | -0.10529 | 0.09613 | -0.036621 | -122.1817 | 0.14648 | 0.1236 | 0.16022 | -122.2 | 0.032043 | -0.018311 | -122.2275 | 0.1831 | 0.045776 | 0.064087 | -122.2321 | 0.17853 | 0.16022 | 0.10529 | -122.3969 | 0.13275 | 0.12817 | 0.17395 | -122.3785
4151.3125 | 122.4609 | -0.041199 | 122.2412 | 0.094299 | 0.047196 | 0.062463 | 0.0016919 | 0.031251 | -0.0036722 | 0.031287 | 0.12085 | 0.027478 | 0.036027 | 0.047106 | 0.0029543 | 0.030349 | 0.013733 | 0.009155 | -0.009155 | -0.018311 | 0.10071 | 0.009155 | -0.11444 | 0.059509 | 0.045776 | -0.041199 | 0.050354 | 0.050354 | -0.045776 | -0.086975 | 0.050354 | -0.073242 | -122.1405 | 0.050354 | 0.022888 | 0.09613 | -122.2275 | -0.004577 | -0.045776 | -122.1909 | 0.10071 | 0 | 0.045776 | -122.1909 | 0.14191 | 0.054932 | 0.032044 | -122.3557 | 0.091553 | 0.091553 | 0.086975 | -122.3282
4153.0781 | 122.4976 | -0.036621 | 122.2412 | -0.065918 | 0.043564 | 0.063318 | 0.0012647 | 0.029542 | -0.0079446 | 0.029792 | -0.024109 | 0.024915 | 0.033891 | 0.047106 | -0.0017453 | 0.030777 | 0.041199 | 0.10986 | 0.086975 | 0.064087 | 0.059509 | 0.050354 | -0.082397 | 0.13275 | 0.16022 | 0.054932 | 0.041199 | 0.009155 | -0.009155 | -0.073242 | 0.086975 | -0.045776 | -122.1817 | 0.14648 | 0.10071 | 0.14648 | -122.2 | 0.027466 | -0.036621 | -122.2 | 0.16937 | 0.091553 | 0.12817 | -122.2321 | 0.09613 | 0.07782 | 0.1236 | -122.3236 | 0.07782 | 0.045776 | 0.19684 | -122.3145
4154.7812 | 122.3785 | -0.09613 | 122.2733 | -0.11169 | 0.050186 | 0.05755 | 0.0036145 | 0.031892 | 0.0014548 | 0.03086 | -0.14618 | 0.028546 | 0.036882 | 0.047961 | 0.0040225 | 0.027572 | 0.050354 | 0.045776 | 0.013733 | 0.036621 | 0.091553 | 0.018311 | -0.13275 | 0.07782 | 0.082397 | -0.050354 | 0.054932 | 0.041199 | -0.032043 | -0.091553 | 0.11444 | -0.036621 | -122.1817 | 0.14191 | 0.13275 | 0.16937 | -122.2229 | 0.064087 | 0.004577 | -122.2183 | 0.17395 | 0.045776 | 0.041199 | -122.2321 | 0.18768 | 0.14648 | 0.10986 | -122.406 | 0.15106 | 0.13733 | 0.17853 | -122.3648
4156.5312 | 122.3877 | -0.086975 | 122.3007 | -0.13458 | 0.047837 | 0.058618 | 0.0023329 | 0.031892 | -0.00068138 | 0.032569 | -0.15381 | 0.027478 | 0.039018 | 0.047747 | 0.0012455 | 0.028427 | 0.041199 | 0.045776 | 0.004578 | 0.027466 | 0.10071 | 0.009155 | -0.13275 | 0.082397 | 0.07782 | -0.068665 | 0.064087 | 0.045776 | -0.041199 | -0.10529 | 0.09613 | -0.045776 | -122.2 | 0.13275 | 0.11444 | 0.16022 | -122.2595 | 0.045776 | -0.018311 | -122.2366 | 0.16937 | 0.01831 | 0.036621 | -122.2549 | 0.18768 | 0.12817 | 0.091553 | -122.4335 | 0.15106 | 0.13275 | 0.16479 | -122.406
4158.2344 | 122.4106 | -0.059509 | 122.2412 | 0.10193 | 0.045914 | 0.060968 | 0.0051099 | 0.027406 | -0.00944 | 0.032142 | 0.13611 | 0.024701 | 0.037309 | 0.046038 | -0.0023861 | 0.030777 | 0.059509 | 0.10986 | 0.086975 | 0.050354 | 0.064087 | 0.045776 | -0.09613 | 0.10986 | 0.10071 | 0.018311 | 0.018311 | 0.009155 | -0.032043 | -0.07782 | 0.10528 | -0.036621 | -122.1771 | 0.16937 | 0.10986 | 0.14648 | -122.1817 | 0.027466 | -0.018311 | -122.2229 | 0.16937 | 0.07782 | 0.096131 | -122.2321 | 0.1236 | 0.11902 | 0.14648 | -122.3373 | 0.07782 | 0.068664 | 0.16022 | -122.319
4159.9375 | 122.374 | -0.086975 | 122.2687 | -0.18799 | 0.04805 | 0.0599 | 0.0042555 | 0.031892 | -0.0075174 | 0.029151 | -0.10803 | 0.026837 | 0.036882 | 0.048815 | -0.0028135 | 0.02864 | 0.082397 | 0.1236 | 0.11444 | 0.07782 | 0.050354 | 0.032043 | -0.10529 | 0.11444 | 0.16022 | 0.036621 | 0.022888 | -0.004578 | -0.027466 | -0.073242 | 0.11902 | -0.018311 | -122.2183 | 0.21057 | 0.16479 | 0.18311 | -122.1863 | 0.059509 | 0.013733 | -122.2458 | 0.20142 | 0.1236 | 0.10986 | -122.2733 | 0.13733 | 0.16937 | 0.20142 | -122.374 | 0.10986 | 0.082397 | 0.24719 | -122.3419
4161.625 | 122.4747 | -0.068665 | 122.2641 | -0.0048827 | 0.0457 | 0.060968 | 0.0034009 | 0.03061 | -0.0092264 | 0.030219 | 0.021668 | 0.027051 | 0.033678 | 0.048815 | -0.0017453 | 0.029281 | 0.050354 | 0.073242 | 0.054932 | 0.045776 | 0.054932 | 0.036621 | -0.11444 | 0.10071 | 0.10986 | 0.032043 | 0.032043 | 0.018311 | -0.027466 | -0.068665 | 0.10529 | -0.045776 | -122.2092 | 0.14191 | 0.11444 | 0.16022 | -122.2137 | 0.041199 | 0 | -122.2321 | 0.16937 | 0.10071 | 0.10071 | -122.2458 | 0.1236 | 0.11902 | 0.1236 | -122.3785 | 0.10071 | 0.086976 | 0.17853 | -122.3328
4163.3438 | 122.3465 | -0.11444 | 122.3007 | -0.24902 | 0.048905 | 0.058405 | 0.0053235 | 0.029969 | -0.0040994 | 0.027015 | -0.24536 | 0.028333 | 0.036668 | 0.050097 | 0.00039091 | 0.029495 | 0.036621 | 0.004578 | -0.004578 | 0 | 0.086975 | 0 | -0.10529 | 0.045776 | 0.041199 | -0.068665 | 0.068665 | 0.059509 | -0.045776 | -0.11902 | 0.11444 | 0.009155 | -122.2137 | 0.11902 | 0.11444 | 0.10529 | -122.2641 | 0.068665 | -0.004578 | -122.2321 | 0.16022 | 0.045776 | 0.050354 | -122.2412 | 0.20142 | 0.15106 | 0.10986 | -122.406 | 0.18311 | 0.17395 | 0.15564 | -122.4197
4165.0469 | 122.3831 | -0.073242 | 122.2916 | -0.20325 | 0.049759 | 0.058191 | 0.0072461 | 0.029115 | 0.00017302 | 0.029151 | -0.22247 | 0.028974 | 0.037736 | 0.049242 | -0.00046349 | 0.027999 | 0.013733 | -0.009155 | -0.027466 | -0.009155 | 0.09613 | -0.004578 | -0.13733 | 0.036621 | 0.045776 | -0.07782 | 0.054932 | 0.041199 | -0.050354 | -0.11902 | 0.068664 | -0.064087 | -122.1954 | 0.064087 | 0.064087 | 0.12817 | -122.2778 | 0.022888 | -0.045777 | -122.2366 | 0.10986 | -0.004578 | 0.041199 | -122.2504 | 0.16937 | 0.086975 | 0.045776 | -122.4289 | 0.12817 | 0.11444 | 0.11902 | -122.4106
4166.75 | 122.3511 | -0.10071 | 122.2916 | -0.18036 | 0.048691 | 0.060754 | 0.0038281 | 0.031037 | -0.0028178 | 0.030646 | -0.2301 | 0.027692 | 0.037523 | 0.049242 | -0.0015317 | 0.030349 | 0.004578 | 0.009155 | -0.009155 | -0.018311 | 0.10986 | 0.018311 | -0.14648 | 0.041199 | 0.059509 | -0.068665 | 0.082397 | 0.068665 | -0.064087 | -0.091553 | 0.11902 | -0.045776 | -122.1817 | 0.10986 | 0.082397 | 0.12817 | -122.287 | 0.036621 | 0.009155 | -122.2092 | 0.14191 | 0.032043 | 0.022888 | -122.2229 | 0.21057 | 0.10529 | 0.091553 | -122.438 | 0.18311 | 0.16937 | 0.16022 | -122.3831
4168.4375 | 122.4609 | -0.032043 | 122.2504 | 0.071411 | 0.045273 | 0.061823 | -0.0010851 | 0.031251 | -0.0034586 | 0.030219 | 0.12085 | 0.027265 | 0.034959 | 0.049029 | 0.0048769 | 0.029495 | 0.082397 | 0.10986 | 0.082397 | 0.07782 | 0.054932 | 0.036621 | -0.10529 | 0.16022 | 0.12817 | 0.027466 | 0.009155 | 0.013733 | -0.009155 | -0.054932 | 0.068664 | -0.073243 | -122.1954 | 0.14191 | 0.10986 | 0.18311 | -122.168 | 0.022888 | -0.022889 | -122.2412 | 0.19226 | 0.059509 | 0.082398 | -122.2366 | 0.086975 | 0.11444 | 0.11444 | -122.3557 | 0.041198 | 0.045776 | 0.16022 | -122.3053
4170.1406 | 122.4655 | -0.054932 | 122.2366 | -0.14221 | 0.045273 | 0.062036 | 0.0040417 | 0.026765 | -0.0073038 | 0.029151 | -0.11566 | 0.025342 | 0.038377 | 0.046252 | -3.629e-05 | 0.029495 | 0.086975 | 0.16937 | 0.13275 | 0.082397 | 0.054932 | 0.050354 | -0.11444 | 0.14648 | 0.1831 | 0.064087 | 0.013733 | 0.009155 | -0.032043 | -0.07782 | 0.10529 | -0.059509 | -122.1817 | 0.22431 | 0.13733 | 0.19684 | -122.1497 | 0.022889 | -0.022888 | -122.2229 | 0.20142 | 0.11902 | 0.14191 | -122.2275 | 0.10986 | 0.14191 | 0.18768 | -122.3511 | 0.068665 | 0.064087 | 0.23804 | -122.3145
4171.8438 | 122.3328 | -0.09613 | 122.2824 | -0.065918 | 0.046982 | 0.058832 | 0.0021191 | 0.029328 | 0.0027364 | 0.030646 | -0.12329 | 0.029828 | 0.036027 | 0.049456 | 0.0046633 | 0.027145 | 0.082397 | 0.059509 | 0.018311 | 0.022888 | 0.07782 | 0.027466 | -0.11902 | 0.073242 | 0.045776 | -0.07782 | 0.064087 | 0.064087 | -0.041199 | -0.10986 | 0.1236 | -0.022889 | -122.2046 | 0.15564 | 0.11902 | 0.14191 | -122.2 | 0.054931 | -0.013733 | -122.2183 | 0.16937 | 0.01831 | 0.032043 | -122.2183 | 0.17395 | 0.17853 | 0.11444 | -122.4014 | 0.16022 | 0.16022 | 0.14191 | -122.3923
4173.5938 | 122.3602 | -0.10529 | 122.2778 | -0.17273 | 0.048905 | 0.059259 | 0.0083143 | 0.028474 | -0.0058084 | 0.030006 | -0.15381 | 0.025983 | 0.037523 | 0.046892 | -0.0025999 | 0.030349 | 0.059509 | 0.13733 | 0.10529 | 0.064087 | 0.064087 | 0.041199 | -0.11444 | 0.09613 | 0.15106 | 0.013733 | 0.032043 | 0.018311 | -0.018311 | -0.064087 | 0.14649 | -0.009155 | -122.2137 | 0.24262 | 0.16937 | 0.17853 | -122.2183 | 0.086975 | 0.041199 | -122.2458 | 0.20142 | 0.11902 | 0.07782 | -122.2595 | 0.16937 | 0.16479 | 0.21057 | -122.3923 | 0.13733 | 0.1236 | 0.25635 | -122.3419
4175.2969 | 122.3557 | -0.082397 | 122.287 | -0.10406 | 0.046555 | 0.059686 | 0.00062385 | 0.028688 | 0.00060022 | 0.030433 | -0.16144 | 0.028974 | 0.032823 | 0.049669 | 0.0040225 | 0.027572 | 0.045776 | 0.07782 | 0.018311 | 0.032043 | 0.091553 | 0 | -0.12817 | 0.10071 | 0.082397 | -0.050354 | 0.064087 | 0.032043 | -0.045776 | -0.10071 | 0.082397 | -0.045777 | -122.1954 | 0.16022 | 0.11444 | 0.16022 | -122.2412 | 0.036621 | -0.018311 | -122.2229 | 0.18311 | 0.032043 | 0.050354 | -122.2549 | 0.17395 | 0.12817 | 0.10071 | -122.4152 | 0.14648 | 0.11444 | 0.16479 | -122.3877
4177.0625 | 122.3831 | -0.10071 | 122.2641 | -0.18036 | 0.049118 | 0.0599 | 0.0019055 | 0.02826 | -0.0034586 | 0.031287 | -0.21484 | 0.027478 | 0.036668 | 0.048174 | 0.00081811 | 0.029068 | -0.004578 | 0.009155 | -0.013733 | -0.004578 | 0.086975 | 0.004578 | -0.14191 | 0.027466 | 0.054932 | -0.064087 | 0.054932 | 0.045776 | -0.064087 | -0.10529 | 0.10529 | -0.041199 | -122.1771 | 0.10986 | 0.09613 | 0.13733 | -122.2687 | 0.036621 | -0.004578 | -122.2092 | 0.12817 | 0.036621 | 0.041199 | -122.2183 | 0.18768 | 0.09613 | 0.086975 | -122.406 | 0.15564 | 0.14648 | 0.15564 | -122.3694
4178.7656 | 122.4197 | -0.068665 | 122.2595 | 0.08667 | 0.047837 | 0.061182 | 0.0034009 | 0.029328 | -0.0017496 | 0.032142 | 0.075073 | 0.02876 | 0.0356 | 0.04732 | 0.0025271 | 0.030777 | -0.018311 | -0.004578 | -0.036621 | -0.027466 | 0.091553 | 0.022888 | -0.13275 | 0.041199 | -0.004578 | -0.086975 | 0.054932 | 0.041199 | -0.050354 | -0.09613 | 0.091553 | -0.064086 | -122.168 | 0.064087 | 0.041199 | 0.10529 | -122.2778 | 0.018311 | -0.027465 | -122.2046 | 0.10986 | -0.01831 | 0.009155 | -122.2183 | 0.16022 | 0.050354 | 0.032044 | -122.3923 | 0.1236 | 0.10986 | 0.064087 | -122.3557
4180.4688 | 122.438 | -0.064087 | 122.2687 | -0.17273 | 0.047409 | 0.060754 | 0.0044691 | 0.02826 | -0.00944 | 0.031287 | -0.11566 | 0.023847 | 0.036882 | 0.048174 | -0.0040951 | 0.027999 | 0.068665 | 0.15564 | 0.1236 | 0.073242 | 0.064087 | 0.018311 | -0.10529 | 0.12817 | 0.18768 | 0.054932 | 0.013733 | 0 | 0.004578 | -0.064087 | 0.082398 | -0.041199 | -122.2046 | 0.21973 | 0.13733 | 0.17853 | -122.2 | 0.068665 | 0 | -122.2549 | 0.19226 | 0.11902 | 0.11902 | -122.2687 | 0.12817 | 0.13275 | 0.18768 | -122.374 | 0.07782 | 0.064087 | 0.25177 | -122.3328
4182.1875 | 122.4518 | -0.036621 | 122.2504 | 0.10956 | 0.044205 | 0.060541 | -0.00044435 | 0.028047 | -0.0030314 | 0.031714 | 0.159 | 0.026624 | 0.034318 | 0.050738 | 0.0029543 | 0.028213 | 0.086975 | 0.11444 | 0.091553 | 0.073242 | 0.041199 | 0.054932 | -0.09613 | 0.15106 | 0.13733 | 0.050354 | 0.004578 | 0.018311 | -0.027466 | -0.059509 | 0.091553 | -0.059509 | -122.2092 | 0.15106 | 0.10986 | 0.16937 | -122.1634 | 0.009155 | -0.022888 | -122.2458 | 0.18768 | 0.086975 | 0.10986 | -122.2321 | 0.07782 | 0.1236 | 0.12817 | -122.3465 | 0.041199 | 0.054932 | 0.17395 | -122.3099
4183.8906 | 122.3419 | -0.10529 | 122.3007 | -0.17273 | 0.046555 | 0.060541 | 0.0066053 | 0.030824 | -0.0028178 | 0.029578 | -0.19958 | 0.027265 | 0.039018 | 0.050097 | -0.0021725 | 0.029708 | -0.013733 | 0 | -0.009155 | -0.018311 | 0.10529 | 0.013733 | -0.14191 | 0.018311 | 0.032043 | -0.07782 | 0.064087 | 0.068665 | -0.064087 | -0.10529 | 0.11902 | -0.036621 | -122.1954 | 0.10529 | 0.086975 | 0.1236 | -122.3145 | 0.041199 | 0 | -122.2366 | 0.1236 | 0.027466 | 0.027466 | -122.2321 | 0.21057 | 0.091553 | 0.096131 | -122.4426 | 0.16937 | 0.17395 | 0.13733 | -122.406
4185.625 | 122.4335 | -0.059509 | 122.2504 | -0.18036 | 0.046341 | 0.061182 | 0.0044691 | 0.029328 | -0.0070902 | 0.028724 | -0.16907 | 0.026197 | 0.035814 | 0.050951 | -0.0019589 | 0.030136 | 0.091553 | 0.15106 | 0.11902 | 0.064087 | 0.059509 | 0.036621 | -0.10071 | 0.13275 | 0.17853 | 0.073242 | 0.018311 | 0.013733 | -0.009155 | -0.059509 | 0.09613 | -0.041199 | -122.1909 | 0.21057 | 0.1236 | 0.1648 | -122.1588 | 0.050354 | 0 | -122.2321 | 0.19226 | 0.13275 | 0.13275 | -122.2366 | 0.11902 | 0.15106 | 0.17853 | -122.3511 | 0.07782 | 0.073242 | 0.23804 | -122.3099
4187.3281 | 122.3282 | -0.10071 | 122.2824 | -0.012512 | 0.048691 | 0.0599 | 0.00062385 | 0.029756 | 0.00060022 | 0.030433 | -0.024109 | 0.025769 | 0.035387 | 0.047961 | 0.0050907 | 0.027359 | 0.027466 | 0.022888 | -0.013733 | -0.009155 | 0.091553 | -0.009155 | -0.13275 | 0.022888 | -0.004578 | -0.11444 | 0.068665 | 0.041199 | -0.050354 | -0.10071 | 0.091553 | -0.032043 | -122.1909 | 0.1236 | 0.091553 | 0.1236 | -122.2549 | 0.050354 | 0 | -122.2137 | 0.1236 | -0.013733 | -0.013733 | -122.2412 | 0.19226 | 0.12817 | 0.086975 | -122.4152 | 0.16937 | 0.14191 | 0.09613 | -122.3831
4189.0781 | 122.4564 | -0.050354 | 122.2046 | 0.14771 | 0.047837 | 0.060114 | -0.0012987 | 0.030183 | -0.0028178 | 0.031714 | 0.12085 | 0.027906 | 0.034318 | 0.046252 | 0.0033817 | 0.031417 | 0.027466 | 0.050354 | 0.041199 | 0.009155 | 0.064087 | 0.032043 | -0.11444 | 0.12817 | 0.10529 | 0.018311 | 0.022888 | 0.022888 | -0.004578 | -0.07782 | 0.082397 | -0.064087 | -122.1405 | 0.10071 | 0.059509 | 0.1236 | -122.1771 | 0.045776 | -0.027466 | -122.1817 | 0.17853 | 0.068665 | 0.096131 | -122.1817 | 0.11444 | 0.07782 | 0.091553 | -122.319 | 0.073242 | 0.073242 | 0.15564 | -122.2824
4190.7969 | 122.4152 | -0.064087 | 122.2549 | -0.19562 | 0.046555 | 0.061395 | 0.0074597 | 0.029328 | -0.007731 | 0.029792 | -0.13855 | 0.025342 | 0.037096 | 0.048174 | -0.0030271 | 0.031204 | 0.082397 | 0.14191 | 0.11444 | 0.07782 | 0.036621 | 0.054932 | -0.082397 | 0.12817 | 0.17395 | 0.041199 | 0.013733 | 0.022888 | -0.004578 | -0.07782 | 0.11902 | -0.01831 | -122.2183 | 0.20599 | 0.14191 | 0.16022 | -122.1725 | 0.059509 | -0.013733 | -122.2412 | 0.19226 | 0.10529 | 0.11902 | -122.2321 | 0.10071 | 0.14648 | 0.17853 | -122.3373 | 0.07782 | 0.086975 | 0.23804 | -122.3328
4192.5469 | 122.4609 | -0.045776 | 122.2229 | 0.13245 | 0.046341 | 0.062036 | 0.0021191 | 0.031037 | -0.0013224 | 0.028937 | 0.036926 | 0.026624 | 0.035814 | 0.048388 | 0.0020999 | 0.028213 | 0.050354 | 0.064087 | 0.054932 | 0.032043 | 0.068665 | 0.041199 | -0.10529 | 0.1236 | 0.10071 | 0.013733 | 0.036621 | 0.018311 | -0.004578 | -0.073242 | 0.086975 | -0.05951 | -122.1542 | 0.10986 | 0.077819 | 0.13733 | -122.1725 | 0.041198 | -0.027466 | -122.1863 | 0.16937 | 0.059509 | 0.086975 | -122.2046 | 0.11444 | 0.09613 | 0.10071 | -122.3282 | 0.082397 | 0.064087 | 0.14648 | -122.2961
4194.25 | 122.3511 | -0.11444 | 122.287 | -0.23376 | 0.047623 | 0.059473 | 0.0046827 | 0.029115 | -0.0047404 | 0.029151 | -0.18433 | 0.025769 | 0.039445 | 0.047747 | -0.0011045 | 0.029068 | 0.004578 | 0.032043 | 0.013733 | -0.009155 | 0.073242 | 0.018311 | -0.14191 | 0.032043 | 0.045776 | -0.068665 | 0.068665 | 0.059509 | -0.064087 | -0.10986 | 0.13275 | -0.027466 | -122.2137 | 0.14648 | 0.10529 | 0.13275 | -122.2824 | 0.050354 | 0.004578 | -122.2183 | 0.14648 | 0.045776 | 0.041198 | -122.2275 | 0.18768 | 0.11902 | 0.12817 | -122.4289 | 0.18311 | 0.17395 | 0.16022 | -122.3969
4195.9375 | 122.4335 | -0.050354 | 122.2549 | 0.13245 | 0.047196 | 0.06225 | -0.0019397 | 0.029756 | -0.0045266 | 0.03086 | 0.12848 | 0.025769 | 0.035387 | 0.047961 | 0.0038089 | 0.030136 | 0.082397 | 0.12817 | 0.10529 | 0.068665 | 0.032043 | 0.054932 | -0.091553 | 0.16022 | 0.12817 | 0.041199 | 0.018311 | 0.009155 | -0.027466 | -0.064087 | 0.10529 | -0.041199 | -122.2229 | 0.17853 | 0.11902 | 0.16022 | -122.1725 | 0.022888 | -0.013733 | -122.2366 | 0.21057 | 0.091553 | 0.10529 | -122.2458 | 0.082397 | 0.13275 | 0.15564 | -122.3465 | 0.068665 | 0.059509 | 0.17853 | -122.319
4197.6562 | 122.374 | -0.082397 | 122.2549 | -0.11169 | 0.045914 | 0.058618 | 0.0038281 | 0.028474 | -0.00046778 | 0.029792 | -0.13092 | 0.028546 | 0.034532 | 0.048388 | 0.0035953 | 0.028854 | 0.059509 | 0.050354 | 0.004578 | 0.027466 | 0.091553 | 0.018311 | -0.14648 | 0.082397 | 0.082397 | -0.045776 | 0.059509 | 0.054932 | -0.032043 | -0.09613 | 0.10071 | -0.064087 | -122.1634 | 0.13275 | 0.10986 | 0.17395 | -122.1954 | 0.050354 | -0.013733 | -122.1954 | 0.16479 | 0.036621 | 0.050354 | -122.2 | 0.17395 | 0.14191 | 0.086975 | -122.4014 | 0.14191 | 0.13733 | 0.16479 | -122.3511
4199.3594 | 122.4747 | -0.054932 | 122.2275 | -0.13458 | 0.044205 | 0.061609 | 0.0057507 | 0.028901 | -0.0092264 | 0.030219 | -0.069885 | 0.024915 | 0.035814 | 0.049242 | -0.0015317 | 0.030136 | 0.07782 | 0.15106 | 0.10986 | 0.073242 | 0.068665 | 0.036621 | -0.09613 | 0.15106 | 0.16937 | 0.073242 | 0.032043 | 0.009155 | -0.013733 | -0.082397 | 0.091553 | -0.041198 | -122.1588 | 0.20599 | 0.12817 | 0.16937 | -122.1497 | 0.041199 | -0.027465 | -122.1954 | 0.20599 | 0.12817 | 0.15564 | -122.2183 | 0.1236 | 0.13275 | 0.16479 | -122.3236 | 0.086975 | 0.064087 | 0.22431 | -122.3099
4201.0781 | 122.4243 | -0.050354 | 122.2412 | 0.14008 | 0.046982 | 0.059045 | -0.00065795 | 0.029542 | -0.0040994 | 0.029792 | 0.159 | 0.025342 | 0.035814 | 0.048174 | 0.0018863 | 0.029922 | 0.09613 | 0.13275 | 0.10529 | 0.068665 | 0.045776 | 0.064087 | -0.086975 | 0.15564 | 0.12817 | 0.027466 | 0.013733 | -0.009155 | -0.022888 | -0.07782 | 0.11444 | -0.036621 | -122.1954 | 0.18311 | 0.11902 | 0.15564 | -122.1451 | 0.027466 | -0.027466 | -122.2275 | 0.20599 | 0.07782 | 0.10529 | -122.2504 | 0.09613 | 0.14648 | 0.15564 | -122.3282 | 0.064087 | 0.041199 | 0.17853 | -122.319
4202.7812 | 122.3969 | -0.091553 | 122.2549 | -0.24139 | 0.048477 | 0.060114 | 0.0059643 | 0.029115 | -0.0019632 | 0.030006 | -0.22247 | 0.027051 | 0.037523 | 0.051592 | -0.0011045 | 0.028213 | 0.009155 | -0.004578 | -0.032043 | -0.013733 | 0.10529 | 0.009155 | -0.15106 | 0.027466 | 0.027466 | -0.09613 | 0.059509 | 0.045776 | -0.059509 | -0.11902 | 0.10071 | -0.059509 | -122.1497 | 0.086975 | 0.07782 | 0.13733 | -122.2458 | 0.032044 | -0.027466 | -122.1954 | 0.11902 | -0.004577 | 0.022889 | -122.2092 | 0.19684 | 0.10071 | 0.05951 | -122.406 | 0.15106 | 0.13733 | 0.11902 | -122.374
4204.4688 | 122.4243 | -0.059509 | 122.2641 | 0.094299 | 0.044632 | 0.06225 | 0.0027601 | 0.030824 | -0.0058084 | 0.029151 | 0.10559 | 0.026624 | 0.034532 | 0.047106 | 0.0012455 | 0.029922 | 0.059509 | 0.10529 | 0.07782 | 0.027466 | 0.050354 | 0.045776 | -0.10071 | 0.09613 | 0.10071 | 0 | 0.032043 | 0.018311 | -0.018311 | -0.064087 | 0.10528 | -0.041199 | -122.2137 | 0.16479 | 0.086975 | 0.12817 | -122.2046 | 0.041198 | -0.004578 | -122.2321 | 0.15564 | 0.059509 | 0.064087 | -122.2458 | 0.10986 | 0.11902 | 0.13733 | -122.3648 | 0.091552 | 0.07782 | 0.16022 | -122.3282
4206.1875 | 122.3465 | -0.10986 | 122.2961 | -0.15747 | 0.046555 | 0.060327 | 0.0048963 | 0.030824 | -0.003245 | 0.029151 | -0.22247 | 0.027478 | 0.03795 | 0.048815 | 0.00017731 | 0.02864 | 0.009155 | 0.004578 | -0.022888 | -0.022888 | 0.09613 | 0.004578 | -0.1236 | 0.018311 | 0.041199 | -0.073242 | 0.068665 | 0.059509 | -0.059509 | -0.10071 | 0.11444 | -0.013733 | -122.2 | 0.11444 | 0.086975 | 0.10071 | -122.287 | 0.050354 | 0.009155 | -122.2275 | 0.12817 | 0.036621 | 0.027466 | -122.2366 | 0.20599 | 0.11902 | 0.086975 | -122.4197 | 0.17853 | 0.16937 | 0.15106 | -122.3969
4207.8906 | 122.4518 | -0.050354 | 122.2229 | 0.094299 | 0.047623 | 0.060754 | -0.0010851 | 0.028688 | -0.0036722 | 0.030006 | 0.12848 | 0.027478 | 0.034746 | 0.048174 | 0.0010317 | 0.029708 | 0.10986 | 0.12817 | 0.10071 | 0.07782 | 0.045776 | 0.050354 | -0.10071 | 0.14648 | 0.13275 | 0.036621 | 0.009155 | 0.013733 | -0.018311 | -0.073242 | 0.10071 | -0.050354 | -122.1771 | 0.17853 | 0.12817 | 0.17853 | -122.113 | 0.032043 | -0.022888 | -122.2137 | 0.19684 | 0.086975 | 0.10986 | -122.2092 | 0.09613 | 0.16022 | 0.15106 | -122.3236 | 0.059509 | 0.064087 | 0.18311 | -122.2961
4209.6406 | 122.3465 | -0.10529 | 122.3053 | -0.23376 | 0.046341 | 0.0599 | 0.0070325 | 0.028474 | -0.0038858 | 0.029578 | -0.19958 | 0.02641 | 0.036668 | 0.048815 | -0.0021725 | 0.029281 | 0.009155 | 0.018311 | 0.004578 | 0 | 0.082397 | 0.009155 | -0.15564 | 0.027466 | 0.045776 | -0.07782 | 0.073242 | 0.054932 | -0.059509 | -0.10986 | 0.11444 | -0.050354 | -122.2229 | 0.1236 | 0.10529 | 0.15564 | -122.2961 | 0.045777 | -0.004577 | -122.2321 | 0.13275 | 0.027466 | 0.032043 | -122.2504 | 0.18768 | 0.11444 | 0.10986 | -122.4609 | 0.17853 | 0.16022 | 0.15106 | -122.4152
4211.3438 | 122.3373 | -0.091553 | 122.2595 | -0.10406 | 0.04805 | 0.059259 | 0.00083745 | 0.029328 | 0.0014548 | 0.032569 | -0.13092 | 0.027692 | 0.035814 | 0.051378 | 0.0046633 | 0.027999 | 0.07782 | 0.068665 | 0.013733 | 0.032043 | 0.082397 | 0.009155 | -0.11902 | 0.07782 | 0.064087 | -0.064087 | 0.068665 | 0.036621 | -0.059509 | -0.086975 | 0.10071 | -0.027466 | -122.1771 | 0.16022 | 0.1236 | 0.15106 | -122.1817 | 0.032044 | 0.004578 | -122.1909 | 0.16937 | 0.027466 | 0.022888 | -122.2229 | 0.17395 | 0.16937 | 0.10529 | -122.3785 | 0.16022 | 0.12817 | 0.15564 | -122.3465
4213.0469 | 122.3419 | -0.086975 | 122.3053 | -0.18799 | 0.047196 | 0.059473 | 0.0076733 | 0.028474 | -0.0087992 | 0.029151 | -0.15381 | 0.025128 | 0.03795 | 0.049029 | -0.0030271 | 0.030777 | 0.064087 | 0.13275 | 0.11444 | 0.073242 | 0.045776 | 0.050354 | -0.082397 | 0.11902 | 0.16022 | 0.032043 | 0.050354 | 0.013733 | -0.013733 | -0.082397 | 0.13733 | 0.004578 | -122.2595 | 0.21973 | 0.16022 | 0.15564 | -122.2412 | 0.073242 | 0.004578 | -122.2549 | 0.20599 | 0.11902 | 0.11444 | -122.2916 | 0.13275 | 0.15106 | 0.20142 | -122.3877 | 0.13733 | 0.10071 | 0.24719 | -122.3877
4214.7344 | 122.4335 | -0.054932 | 122.2412 | 0.14008 | 0.046341 | 0.062677 | -0.0010851 | 0.030397 | -0.0047404 | 0.030433 | 0.14374 | 0.026197 | 0.034105 | 0.04732 | 0.0044497 | 0.029922 | 0.073242 | 0.13275 | 0.10529 | 0.073242 | 0.041199 | 0.050354 | -0.082397 | 0.14648 | 0.14191 | 0.050354 | 0.013733 | 0.004578 | 0 | -0.07782 | 0.10529 | -0.027465 | -122.2 | 0.18768 | 0.12817 | 0.15564 | -122.168 | 0.054932 | -0.022888 | -122.2275 | 0.20142 | 0.10529 | 0.12817 | -122.2366 | 0.096131 | 0.12817 | 0.16022 | -122.3236 | 0.068665 | 0.05951 | 0.19684 | -122.319
4216.4375 | 122.3465 | -0.09613 | 122.2778 | -0.21851 | 0.0457 | 0.058832 | 0.0040417 | 0.029542 | -0.0068766 | 0.028937 | -0.23773 | 0.025342 | 0.036027 | 0.049029 | -3.629e-05 | 0.027786 | 0.064087 | 0.10986 | 0.068665 | 0.050354 | 0.064087 | 0.036621 | -0.10529 | 0.068665 | 0.10071 | -0.032043 | 0.041199 | 0.032043 | -0.036621 | -0.10529 | 0.13275 | -0.009156 | -122.2137 | 0.20599 | 0.14648 | 0.15564 | -122.2137 | 0.059509 | -0.009156 | -122.2366 | 0.16479 | 0.064087 | 0.073243 | -122.2458 | 0.16022 | 0.16022 | 0.16479 | -122.3831 | 0.13733 | 0.12817 | 0.19684 | -122.3831
4218.1406 | 122.4243 | -0.050354 | 122.2412 | 0.12482 | 0.043991 | 0.060968 | 0.00019645 | 0.029328 | -0.0038858 | 0.030433 | 0.11322 | 0.027692 | 0.037523 | 0.048174 | 0.00039091 | 0.029495 | 0.09613 | 0.1236 | 0.10529 | 0.064087 | 0.045776 | 0.050354 | -0.07782 | 0.16022 | 0.1236 | 0.036621 | 0.018311 | 0.009155 | -0.009155 | -0.068665 | 0.10071 | -0.027466 | -122.1954 | 0.17395 | 0.11444 | 0.14191 | -122.1451 | 0.041199 | -0.018311 | -122.2229 | 0.21057 | 0.086975 | 0.10529 | -122.2321 | 0.09613 | 0.14648 | 0.15564 | -122.319 | 0.068665 | 0.059509 | 0.17395 | -122.3099
4219.8281 | 122.3602 | -0.10986 | 122.287 | -0.088806 | 0.051255 | 0.058191 | 0.0021191 | 0.031678 | 0.0023092 | 0.032996 | -0.16144 | 0.027051 | 0.03795 | 0.050951 | 0.0033817 | 0.028427 | 0.086975 | 0.032043 | 0.018311 | 0.032043 | 0.091553 | 0.022888 | -0.12817 | 0.091553 | 0.07782 | -0.050354 | 0.045776 | 0.041199 | -0.045776 | -0.10071 | 0.13275 | -0.018311 | -122.1954 | 0.14191 | 0.14191 | 0.16022 | -122.2 | 0.064087 | 0.009155 | -122.2412 | 0.20142 | 0.059509 | 0.050354 | -122.2458 | 0.20142 | 0.19684 | 0.12817 | -122.4152 | 0.15564 | 0.15106 | 0.18768 | -122.3877
4221.5781 | 122.3465 | -0.10071 | 122.2641 | -0.24902 | 0.04805 | 0.059686 | 0.0053235 | 0.029969 | -0.0038858 | 0.028724 | -0.10803 | 0.02641 | 0.036241 | 0.047533 | -0.0015317 | 0.030136 | 0.004578 | 0.022888 | 0.004578 | 0.013733 | 0.091553 | 0.013733 | -0.11444 | 0.032043 | 0.036621 | -0.064087 | 0.054932 | 0.054932 | -0.054932 | -0.1236 | 0.11444 | -0.013733 | -122.1725 | 0.1236 | 0.11444 | 0.12817 | -122.2595 | 0.045776 | -0.022888 | -122.2092 | 0.13275 | 0.036621 | 0.059509 | -122.2092 | 0.19226 | 0.10529 | 0.10529 | -122.3785 | 0.15564 | 0.15564 | 0.13733 | -122.3877
4223.2812 | 122.3602 | -0.082397 | 122.2595 | 0.11719 | 0.046982 | 0.0599 | -0.0012987 | 0.027833 | -0.0011088 | 0.032142 | 0.059815 | 0.025769 | 0.035387 | 0.049242 | 0.0031681 | 0.032058 | -0.013733 | -0.022888 | -0.041199 | -0.022888 | 0.10529 | 0 | -0.13733 | 0.041199 | -0.009155 | -0.10071 | 0.050354 | 0.036621 | -0.050354 | -0.09613 | 0.082397 | -0.054932 | -122.1542 | 0.059509 | 0.059509 | 0.11444 | -122.2733 | 0.032043 | -0.013733 | -122.2092 | 0.1236 | -0.018311 | -0.004578 | -122.2229 | 0.18768 | 0.068664 | 0.041198 | -122.3969 | 0.13275 | 0.11902 | 0.073242 | -122.3557
4224.9844 | 122.4518 | -0.059509 | 122.2687 | -0.12695 | 0.046982 | 0.060541 | 0.0068189 | 0.029969 | -0.010081 | 0.028724 | -0.085144 | 0.025983 | 0.037309 | 0.047747 | -0.0028135 | 0.031204 | 0.082397 | 0.16479 | 0.11902 | 0.07782 | 0.059509 | 0.041199 | -0.086975 | 0.15564 | 0.20142 | 0.07782 | 0.018311 | 0.004578 | -0.018311 | -0.068665 | 0.10071 | -0.027466 | -122.2092 | 0.2243 | 0.13733 | 0.16479 | -122.1863 | 0.041198 | -0.009156 | -122.2504 | 0.21515 | 0.13733 | 0.14649 | -122.2641 | 0.11902 | 0.14191 | 0.17853 | -122.3557 | 0.07782 | 0.064087 | 0.26093 | -122.3373
4226.6875 | 122.4152 | -0.050354 | 122.2733 | 0.08667 | 0.042496 | 0.061609 | -0.00087155 | 0.028047 | -0.0055948 | 0.029792 | 0.12848 | 0.025556 | 0.034959 | 0.049242 | 0.00081811 | 0.029495 | 0.068665 | 0.1236 | 0.086975 | 0.050354 | 0.054932 | 0.045776 | -0.10071 | 0.12817 | 0.09613 | 0.018311 | 0.013733 | 0.004578 | -0.036621 | -0.068665 | 0.09613 | -0.050354 | -122.2183 | 0.17395 | 0.10071 | 0.15106 | -122.2046 | 0.013733 | -0.018311 | -122.2595 | 0.17853 | 0.068665 | 0.086976 | -122.2687 | 0.10529 | 0.11902 | 0.13733 | -122.374 | 0.064087 | 0.054932 | 0.14648 | -122.3419
4228.3906 | 122.3831 | -0.082397 | 122.2412 | -0.18036 | 0.048905 | 0.057764 | 0.00062385 | 0.029115 | 0.001882 | 0.032996 | -0.21484 | 0.029187 | 0.037096 | 0.049669 | 0.0020999 | 0.030349 | 0.027466 | 0.009155 | -0.009155 | 0.022888 | 0.086975 | 0.004578 | -0.14191 | 0.054932 | 0.068665 | -0.054932 | 0.050354 | 0.059509 | -0.045776 | -0.09613 | 0.086975 | -0.05951 | -122.1542 | 0.091552 | 0.10528 | 0.16479 | -122.2137 | 0.036621 | -0.013733 | -122.1909 | 0.13733 | 0.027465 | 0.041198 | -122.1817 | 0.16937 | 0.10986 | 0.073242 | -122.3831 | 0.13275 | 0.14191 | 0.15106 | -122.3373
4230.0938 | 122.4197 | -0.059509 | 122.2321 | 0.040894 | 0.043991 | 0.062463 | 0.00019645 | 0.028474 | -0.0090128 | 0.029578 | 0.044556 | 0.026624 | 0.035387 | 0.047106 | -0.0015317 | 0.033126 | 0.022888 | 0.07782 | 0.054932 | 0.013733 | 0.068665 | 0.027466 | -0.10071 | 0.086975 | 0.091553 | 0.004578 | 0.032043 | 0.022888 | -0.013733 | -0.086975 | 0.086975 | -0.041199 | -122.1634 | 0.13733 | 0.073242 | 0.11444 | -122.2092 | 0.045776 | -0.027466 | -122.2 | 0.14648 | 0.064087 | 0.091553 | -122.2092 | 0.12817 | 0.082397 | 0.11444 | -122.3328 | 0.091552 | 0.082397 | 0.15106 | -122.319
4231.7969 | 122.3282 | -0.09613 | 122.2916 | -0.088806 | 0.048905 | 0.059473 | 0.00019645 | 0.029328 | -0.00068138 | 0.031287 | -0.11566 | 0.02876 | 0.036241 | 0.052447 | 0.0025271 | 0.027145 | 0.07782 | 0.036621 | 0.013733 | 0.032043 | 0.07782 | 0.013733 | -0.1236 | 0.086975 | 0.054932 | -0.064087 | 0.050354 | 0.041199 | -0.050354 | -0.091553 | 0.10986 | -0.027466 | -122.2137 | 0.13275 | 0.12817 | 0.15564 | -122.2137 | 0.045776 | 0.004577 | -122.2412 | 0.1831 | 0.032043 | 0.027466 | -122.2504 | 0.17395 | 0.17395 | 0.10986 | -122.4152 | 0.14648 | 0.13733 | 0.15106 | -122.3831
4233.5 | 122.4564 | -0.041199 | 122.2275 | 0.063782 | 0.045487 | 0.059473 | 0.0010511 | 0.029542 | -0.00025418 | 0.03086 | 0.12085 | 0.026837 | 0.037523 | 0.047961 | 0.0035953 | 0.029281 | 0.09613 | 0.10529 | 0.082397 | 0.068665 | 0.068665 | 0.045776 | -0.10071 | 0.14191 | 0.1236 | 0.027466 | 0.013733 | 0 | 0.004578 | -0.068665 | 0.086975 | -0.059509 | -122.1588 | 0.14649 | 0.10986 | 0.16937 | -122.1313 | 0.045777 | -0.027466 | -122.2137 | 0.18311 | 0.068665 | 0.096131 | -122.2275 | 0.10986 | 0.13733 | 0.1236 | -122.3282 | 0.054932 | 0.041199 | 0.16479 | -122.2961
4235.2188 | 122.4289 | -0.036621 | 122.2137 | 0.14008 | 0.045914 | 0.061182 | 0.0036145 | 0.028047 | -0.0045266 | 0.031714 | 0.16663 | 0.026837 | 0.036882 | 0.046892 | 0.0025271 | 0.030349 | 0.09613 | 0.1236 | 0.10529 | 0.073242 | 0.059509 | 0.036621 | -0.086975 | 0.14191 | 0.14191 | 0.032043 | 0.013733 | 0 | -0.018311 | -0.050354 | 0.073242 | -0.050354 | -122.1542 | 0.16022 | 0.10986 | 0.16022 | -122.1176 | 0.01831 | -0.013733 | -122.2 | 0.17853 | 0.068664 | 0.082397 | -122.2137 | 0.09613 | 0.13275 | 0.14191 | -122.3007 | 0.050354 | 0.036621 | 0.17853 | -122.2641
4236.9219 | 122.3419 | -0.12817 | 122.2778 | -0.23376 | 0.046982 | 0.061395 | 0.0081007 | 0.029328 | -0.001536 | 0.026801 | -0.1004 | 0.027478 | 0.039659 | 0.051806 | -0.0032407 | 0.031417 | 0.009155 | 0.022888 | -0.004578 | 0.004578 | 0.091553 | 0.009155 | -0.15106 | 0.027466 | 0.045776 | -0.068665 | 0.050354 | 0.045776 | -0.059509 | -0.10071 | 0.13733 | -0.022888 | -122.1863 | 0.15106 | 0.13275 | 0.15564 | -122.2687 | 0.068665 | 0.027466 | -122.2275 | 0.15564 | 0.059509 | 0.032043 | -122.2321 | 0.21973 | 0.13733 | 0.1236 | -122.4289 | 0.17853 | 0.17395 | 0.17395 | -122.3785
4238.625 | 122.4426 | -0.045776 | 122.2183 | 0.11719 | 0.045487 | 0.0599 | -0.00087155 | 0.030183 | -0.0019632 | 0.031287 | 0.14374 | 0.02641 | 0.033891 | 0.049669 | 0.0033817 | 0.030777 | 0.091553 | 0.10529 | 0.09613 | 0.068665 | 0.050354 | 0.045776 | -0.086975 | 0.14648 | 0.12817 | 0.041199 | 0.018311 | -0.009155 | -0.018311 | -0.068665 | 0.091552 | -0.041199 | -122.168 | 0.15106 | 0.11444 | 0.15564 | -122.1268 | 0.027465 | -0.022889 | -122.2 | 0.19226 | 0.086975 | 0.10986 | -122.2275 | 0.09613 | 0.13733 | 0.14191 | -122.3053 | 0.064087 | 0.036621 | 0.17395 | -122.287
4240.3438 | 122.3419 | -0.11444 | 122.2778 | -0.1651 | 0.046555 | 0.061823 | 0.0068189 | 0.031037 | -0.0053812 | 0.029578 | -0.23773 | 0.027051 | 0.035814 | 0.049883 | -0.0030271 | 0.030349 | 0.068665 | 0.10529 | 0.10071 | 0.064087 | 0.064087 | 0.041199 | -0.10529 | 0.068665 | 0.12817 | 0 | 0.050354 | 0.032043 | -0.050354 | -0.10529 | 0.15564 | 0.009155 | -122.2137 | 0.21973 | 0.17853 | 0.16937 | -122.2092 | 0.064087 | 0.009155 | -122.2275 | 0.18311 | 0.11444 | 0.10529 | -122.2458 | 0.17853 | 0.18311 | 0.21515 | -122.3831 | 0.16479 | 0.14648 | 0.24262 | -122.3831
4242.0469 | 122.3831 | -0.10529 | 122.2778 | -0.18799 | 0.049118 | 0.061182 | 0.0044691 | 0.028474 | -0.0019632 | 0.029792 | -0.2301 | 0.02876 | 0.038591 | 0.051806 | -0.00024989 | 0.02864 | 0.022888 | -0.009155 | -0.027466 | 0.004578 | 0.11902 | -0.004578 | -0.14648 | 0.022888 | 0.050354 | -0.073242 | 0.045776 | 0.050354 | -0.073242 | -0.10529 | 0.10071 | -0.041198 | -122.1588 | 0.096131 | 0.10986 | 0.15106 | -122.2549 | 0.032044 | 0 | -122.2321 | 0.12817 | 0.032044 | 0.032044 | -122.2275 | 0.22431 | 0.12817 | 0.07782 | -122.4243 | 0.15106 | 0.15564 | 0.15564 | -122.3831
4243.7656 | 122.3923 | -0.082397 | 122.2641 | -0.20325 | 0.048691 | 0.062677 | 0.0046827 | 0.030397 | -0.0070902 | 0.030219 | -0.14618 | 0.024915 | 0.035173 | 0.048601 | -0.0017453 | 0.030136 | 0.073242 | 0.15106 | 0.11902 | 0.07782 | 0.064087 | 0.022888 | -0.09613 | 0.1236 | 0.16479 | 0.032043 | 0.018311 | 0.009155 | -0.027466 | -0.07782 | 0.10528 | -0.013733 | -122.2 | 0.23346 | 0.16022 | 0.17395 | -122.1909 | 0.054931 | 0.004577 | -122.2458 | 0.20599 | 0.11444 | 0.10986 | -122.2549 | 0.14648 | 0.15564 | 0.20142 | -122.3602 | 0.10071 | 0.091552 | 0.24719 | -122.3419
4245.4531 | 122.3557 | -0.10986 | 122.2916 | 0.033264 | 0.047409 | 0.059045 | 0.00083745 | 0.029756 | -0.0011088 | 0.03086 | -0.0088499 | 0.029615 | 0.036241 | 0.049669 | 0.0033817 | 0.028213 | -0.013733 | -0.045776 | -0.054932 | -0.009155 | 0.10529 | 0.009155 | -0.14191 | 0.022888 | -0.009155 | -0.10529 | 0.082397 | 0.045776 | -0.064087 | -0.11902 | 0.11902 | -0.032044 | -122.1863 | 0.064087 | 0.10071 | 0.13275 | -122.3053 | 0.045776 | -0.009156 | -122.2092 | 0.13275 | 0.004577 | 0.013733 | -122.2458 | 0.21515 | 0.09613 | 0.054931 | -122.4335 | 0.19226 | 0.15564 | 0.10071 | -122.4106
4247.1562 | 122.374 | -0.086975 | 122.2733 | -0.20325 | 0.048264 | 0.058832 | 0.0044691 | 0.030824 | -0.0075174 | 0.027869 | -0.13855 | 0.024915 | 0.036027 | 0.049669 | -0.00067729 | 0.03099 | 0.082397 | 0.13733 | 0.10986 | 0.073242 | 0.050354 | 0.041199 | -0.082397 | 0.11902 | 0.16479 | 0.036621 | 0.027466 | 0.018311 | -0.018311 | -0.082397 | 0.12817 | 0.004578 | -122.2229 | 0.2243 | 0.16022 | 0.15564 | -122.1909 | 0.068664 | 0.004578 | -122.2458 | 0.20599 | 0.1236 | 0.11902 | -122.2549 | 0.13733 | 0.16937 | 0.19684 | -122.3557 | 0.11444 | 0.10529 | 0.25177 | -122.3557
4248.875 | 122.4243 | -0.068665 | 122.2504 | 0.040894 | 0.045273 | 0.060754 | 0.0036145 | 0.029756 | -0.0073038 | 0.027869 | 0.067444 | 0.024701 | 0.03325 | 0.047533 | -0.00089089 | 0.029495 | 0.036621 | 0.086975 | 0.050354 | 0.036621 | 0.045776 | 0.041199 | -0.09613 | 0.09613 | 0.09613 | 0.013733 | 0.027466 | 0.036621 | -0.018311 | -0.068665 | 0.10986 | -0.027465 | -122.2046 | 0.15564 | 0.10529 | 0.13275 | -122.2137 | 0.050354 | 0 | -122.2229 | 0.16479 | 0.082398 | 0.082398 | -122.2137 | 0.11444 | 0.10529 | 0.11902 | -122.3465 | 0.096131 | 0.10529 | 0.16479 | -122.319
4250.625 | 122.4747 | -0.059509 | 122.1909 | -0.058289 | 0.043564 | 0.060754 | 0.0042555 | 0.030397 | -0.0055948 | 0.029365 | -0.046997 | 0.023847 | 0.034746 | 0.048601 | -0.0011045 | 0.030563 | 0.045776 | 0.082397 | 0.068665 | 0.036621 | 0.073242 | 0.032043 | -0.11444 | 0.12817 | 0.13733 | 0.050354 | 0.041199 | 0.018311 | -0.022888 | -0.064087 | 0.091552 | -0.054932 | -122.1176 | 0.14191 | 0.09613 | 0.15106 | -122.1451 | 0.036621 | -0.004578 | -122.1497 | 0.18768 | 0.10986 | 0.11444 | -122.1725 | 0.13275 | 0.10528 | 0.12817 | -122.3053 | 0.10071 | 0.07782 | 0.19684 | -122.2549
4252.3281 | 122.3694 | -0.086975 | 122.2641 | -0.24139 | 0.048477 | 0.060541 | 0.0038281 | 0.032319 | 0.00081382 | 0.028297 | -0.26825 | 0.030469 | 0.034746 | 0.050738 | 0.00060451 | 0.027999 | 0.009155 | -0.018311 | -0.036621 | -0.013733 | 0.09613 | -0.009155 | -0.12817 | 0.022888 | 0.022888 | -0.073242 | 0.064087 | 0.082397 | -0.054932 | -0.086975 | 0.07782 | -0.041199 | -122.168 | 0.068664 | 0.073242 | 0.11444 | -122.2549 | 0.032043 | 0 | -122.2 | 0.10986 | 0.013733 | 0.013733 | -122.1817 | 0.1831 | 0.09613 | 0.050354 | -122.3923 | 0.15106 | 0.16937 | 0.10986 | -122.3511
4254.0312 | 122.4152 | -0.059509 | 122.2412 | 0.040894 | 0.041855 | 0.059686 | -0.00023075 | 0.027833 | -0.0058084 | 0.029578 | 0.059815 | 0.024915 | 0.0356 | 0.048174 | 0.0018863 | 0.030349 | 0.045776 | 0.082397 | 0.064087 | 0.022888 | 0.064087 | 0.036621 | -0.10529 | 0.091553 | 0.082397 | 0.009155 | 0.045776 | 0.009155 | -0.041199 | -0.086975 | 0.09613 | -0.045777 | -122.1771 | 0.14191 | 0.082397 | 0.12817 | -122.1954 | 0.01831 | -0.027466 | -122.1954 | 0.15106 | 0.068664 | 0.09613 | -122.2321 | 0.1236 | 0.10528 | 0.1236 | -122.3465 | 0.10528 | 0.068664 | 0.14191 | -122.3282
4255.7188 | 122.3282 | -0.11902 | 122.2961 | 0.0027468 | 0.0504 | 0.057764 | 0.0031873 | 0.030824 | 0.0020956 | 0.030219 | -0.046997 | 0.028333 | 0.0356 | 0.051806 | 0.0044497 | 0.026931 | 0.045776 | -0.022888 | -0.027466 | -0.004578 | 0.086975 | 0 | -0.13275 | 0.022888 | -0.009155 | -0.11902 | 0.059509 | 0.050354 | -0.064087 | -0.10071 | 0.11902 | -0.013732 | -122.2092 | 0.096131 | 0.11444 | 0.12817 | -122.2504 | 0.054932 | 0.018311 | -122.2366 | 0.14191 | 0 | -0.018311 | -122.2458 | 0.20599 | 0.16479 | 0.091553 | -122.4289 | 0.17853 | 0.16937 | 0.10986 | -122.3969
4257.4531 | 122.3557 | -0.10529 | 122.2504 | -0.21851 | 0.047623 | 0.063532 | 0.0044691 | 0.028474 | -0.0070902 | 0.028083 | -0.24536 | 0.025128 | 0.038591 | 0.049669 | 0.0010317 | 0.030349 | -0.018311 | 0.013733 | -0.018311 | -0.022888 | 0.091553 | 0 | -0.13733 | 0.018311 | 0.027466 | -0.07782 | 0.07782 | 0.073242 | -0.073242 | -0.11444 | 0.10529 | -0.032043 | -122.1588 | 0.11902 | 0.082398 | 0.11444 | -122.2687 | 0.032044 | -0.009155 | -122.1725 | 0.1236 | 0.027466 | 0.036621 | -122.1771 | 0.19684 | 0.086975 | 0.086975 | -122.3877 | 0.18311 | 0.17853 | 0.13275 | -122.3648
4259.1406 | 122.4152 | -0.073242 | 122.2458 | 0.040894 | 0.042069 | 0.061823 | 0.0042555 | 0.027833 | -0.006663 | 0.029578 | 0.075073 | 0.024488 | 0.034532 | 0.049883 | -0.00089089 | 0.033126 | 0.027466 | 0.07782 | 0.059509 | 0.036621 | 0.059509 | 0.045776 | -0.091553 | 0.10529 | 0.09613 | -0.004578 | 0.022888 | 0.013733 | -0.004578 | -0.07782 | 0.11902 | -0.018311 | -122.1863 | 0.15106 | 0.10986 | 0.12817 | -122.2183 | 0.068664 | -0.004578 | -122.2229 | 0.17853 | 0.068664 | 0.073242 | -122.2321 | 0.13275 | 0.10071 | 0.13275 | -122.3373 | 0.09613 | 0.086975 | 0.16937 | -122.3236
4260.8594 | 122.4106 | -0.064087 | 122.2458 | 0.079041 | 0.041428 | 0.060327 | 0.0016919 | 0.030397 | -0.0064492 | 0.029792 | 0.13611 | 0.02406 | 0.035387 | 0.047961 | 0.0020999 | 0.031417 | 0.054932 | 0.12817 | 0.09613 | 0.045776 | 0.050354 | 0.041199 | -0.091553 | 0.13275 | 0.10986 | 0.018311 | 0.041199 | 0.027466 | 0 | -0.064087 | 0.10529 | -0.027466 | -122.1954 | 0.19226 | 0.10986 | 0.13733 | -122.1909 | 0.064087 | 0 | -122.2046 | 0.19684 | 0.082398 | 0.082398 | -122.2183 | 0.11444 | 0.11902 | 0.16022 | -122.3373 | 0.10529 | 0.091553 | 0.17395 | -122.3099
4262.6094 | 122.4655 | -0.041199 | 122.2321 | 0.0027468 | 0.043564 | 0.059686 | 0.0034009 | 0.026551 | -0.0053812 | 0.029578 | 0.014038 | 0.02641 | 0.035387 | 0.048815 | -0.0028135 | 0.032272 | 0.032043 | 0.059509 | 0.059509 | 0.036621 | 0.068665 | 0.022888 | -0.10986 | 0.09613 | 0.086975 | 0.022888 | 0.032043 | 0.036621 | -0.027466 | -0.082397 | 0.064087 | -0.068664 | -122.1634 | 0.10071 | 0.07782 | 0.14648 | -122.2 | 0.013733 | -0.041198 | -122.2 | 0.13733 | 0.064087 | 0.10528 | -122.1954 | 0.10986 | 0.073242 | 0.10071 | -122.3419 | 0.073242 | 0.07782 | 0.12817 | -122.3145
4264.2969 | 122.374 | -0.10071 | 122.2687 | -0.21851 | 0.052964 | 0.06225 | 0.0087415 | 0.031037 | -0.00046778 | 0.026801 | -0.2301 | 0.028119 | 0.035814 | 0.051806 | 0.0020999 | 0.02864 | 0.027466 | -0.022888 | -0.036621 | -0.004578 | 0.10529 | -0.004578 | -0.14191 | 0.032043 | 0.027466 | -0.091553 | 0.082397 | 0.041199 | -0.050354 | -0.11444 | 0.09613 | -0.041199 | -122.1634 | 0.07782 | 0.09613 | 0.13733 | -122.2412 | 0.050354 | -0.013733 | -122.1863 | 0.13275 | 0.009155 | 0.022888 | -122.2275 | 0.20599 | 0.12817 | 0.064087 | -122.4106 | 0.18311 | 0.14191 | 0.12817 | -122.3831
4266 | 122.4609 | -0.050354 | 122.2229 | 0.11719 | 0.046341 | 0.0599 | 0.0014783 | 0.028047 | -0.00089518 | 0.03321 | 0.090332 | 0.028119 | 0.034318 | 0.050738 | 0.0031681 | 0.031845 | 0.11444 | 0.10529 | 0.082397 | 0.064087 | 0.073242 | 0.068665 | -0.082397 | 0.14648 | 0.1236 | 0.027466 | 0 | 0.004578 | -0.032043 | -0.073242 | 0.11902 | -0.032043 | -122.1497 | 0.15564 | 0.11444 | 0.14648 | -122.1085 | 0.018311 | -0.022888 | -122.2229 | 0.19684 | 0.07782 | 0.10071 | -122.2183 | 0.1236 | 0.16479 | 0.13275 | -122.3053 | 0.050354 | 0.054932 | 0.17395 | -122.2961
4267.7031 | 122.3877 | -0.10071 | 122.2687 | -0.24139 | 0.04805 | 0.061182 | 0.0068189 | 0.031678 | -0.00068138 | 0.030433 | -0.22247 | 0.02876 | 0.038805 | 0.051165 | 0.00060451 | 0.030136 | 0.009155 | -0.013733 | -0.022888 | -0.018311 | 0.07782 | 0.004578 | -0.15106 | 0.022888 | 0.032043 | -0.07782 | 0.082397 | 0.054932 | -0.050354 | -0.11444 | 0.10529 | -0.050354 | -122.1909 | 0.086975 | 0.082397 | 0.13275 | -122.2595 | 0.050354 | -0.013733 | -122.1863 | 0.1236 | 0.022888 | 0.036621 | -122.2137 | 0.17853 | 0.10986 | 0.07782 | -122.4197 | 0.18311 | 0.15564 | 0.13275 | -122.3831
4269.3906 | 122.4472 | -0.059509 | 122.2504 | 0.12482 | 0.047409 | 0.060114 | 0.00041005 | 0.032105 | -0.0051676 | 0.028937 | 0.18951 | 0.025128 | 0.034532 | 0.047747 | 0.0018863 | 0.031417 | 0.10529 | 0.11444 | 0.10071 | 0.068665 | 0.054932 | 0.036621 | -0.068665 | 0.16937 | 0.14191 | 0.032043 | 0.032043 | 0.009155 | -0.018311 | -0.068665 | 0.09613 | -0.009156 | -122.1954 | 0.17395 | 0.12817 | 0.13733 | -122.1451 | 0.041198 | -0.009156 | -122.2183 | 0.22888 | 0.091552 | 0.10071 | -122.2412 | 0.11444 | 0.16479 | 0.16022 | -122.319 | 0.091552 | 0.068664 | 0.20142 | -122.319
4271.0938 | 122.3831 | -0.082397 | 122.2504 | -0.18799 | 0.047409 | 0.060327 | 0.0034009 | 0.028688 | 0.00017302 | 0.030219 | -0.19196 | 0.027692 | 0.034746 | 0.048174 | 0.0027407 | 0.028427 | 0.027466 | 0.022888 | -0.018311 | 0.009155 | 0.10071 | 0.018311 | -0.1236 | 0.073242 | 0.068665 | -0.054932 | 0.064087 | 0.022888 | -0.059509 | -0.11444 | 0.10071 | -0.041199 | -122.1497 | 0.10528 | 0.091552 | 0.13275 | -122.2229 | 0.022888 | -0.032044 | -122.1863 | 0.15564 | 0.027465 | 0.059509 | -122.2275 | 0.18311 | 0.10986 | 0.064086 | -122.374 | 0.14648 | 0.10528 | 0.15106 | -122.3648
4272.7969 | 122.4747 | -0.054932 | 122.2137 | -0.04303 | 0.046341 | 0.060754 | 0.0034009 | 0.028474 | -0.00944 | 0.029578 | -0.024109 | 0.024488 | 0.036241 | 0.049883 | -0.0017453 | 0.031845 | 0.036621 | 0.091553 | 0.073242 | 0.059509 | 0.068665 | 0.032043 | -0.11902 | 0.1236 | 0.16022 | 0.050354 | 0.018311 | 0.018311 | -0.027466 | -0.073242 | 0.086975 | -0.064087 | -122.1451 | 0.14649 | 0.11444 | 0.17853 | -122.1771 | 0.027466 | -0.01831 | -122.1954 | 0.17853 | 0.10529 | 0.1236 | -122.1954 | 0.1236 | 0.091553 | 0.12817 | -122.3328 | 0.073243 | 0.073243 | 0.21515 | -122.287
4274.5312 | 122.3923 | -0.086975 | 122.2778 | -0.17273 | 0.049973 | 0.060114 | 0.0046827 | 0.031037 | -4.058e-05 | 0.030433 | -0.2301 | 0.028333 | 0.037736 | 0.051378 | 0.0016727 | 0.029281 | 0.018311 | -0.009155 | -0.027466 | 0.018311 | 0.091553 | -0.004578 | -0.1236 | 0.068665 | 0.064087 | -0.050354 | 0.054932 | 0.036621 | -0.054932 | -0.10986 | 0.082397 | -0.036621 | -122.1863 | 0.07782 | 0.10529 | 0.14191 | -122.2595 | 0.032043 | -0.022888 | -122.2229 | 0.15564 | 0.036621 | 0.059509 | -122.2412 | 0.17853 | 0.10529 | 0.059509 | -122.4014 | 0.14191 | 0.1236 | 0.15106 | -122.3877
4276.2344 | 122.4106 | -0.07782 | 122.2229 | 0.08667 | 0.046982 | 0.060327 | 0.0025465 | 0.030397 | -0.006663 | 0.031501 | 0.12848 | 0.024915 | 0.037309 | 0.049669 | 0.0010317 | 0.030136 | 0.07782 | 0.11902 | 0.11444 | 0.064087 | 0.022888 | 0.045776 | -0.086975 | 0.15106 | 0.1236 | 0.045776 | 0.018311 | 0.009155 | -0.013733 | -0.064087 | 0.1236 | -0.009155 | -122.2 | 0.19684 | 0.14191 | 0.15106 | -122.1451 | 0.064087 | 0.013733 | -122.2046 | 0.22888 | 0.1236 | 0.10986 | -122.2137 | 0.10071 | 0.15564 | 0.19226 | -122.3099 | 0.096131 | 0.086975 | 0.20142 | -122.287
4277.9531 | 122.4518 | -0.064087 | 122.2458 | -0.13458 | 0.047196 | 0.061395 | 0.0034009 | 0.031251 | -0.0064492 | 0.029365 | -0.13092 | 0.025128 | 0.038377 | 0.049456 | -0.0015317 | 0.03099 | 0.09613 | 0.16479 | 0.14191 | 0.086975 | 0.050354 | 0.041199 | -0.10071 | 0.14648 | 0.19226 | 0.059509 | 0.027466 | 0 | -0.018311 | -0.068665 | 0.10529 | -0.036621 | -122.1954 | 0.22888 | 0.15106 | 0.18768 | -122.1497 | 0.045776 | -0.004578 | -122.2183 | 0.21057 | 0.1236 | 0.12817 | -122.2458 | 0.11444 | 0.16022 | 0.20599 | -122.3465 | 0.091553 | 0.064087 | 0.25635 | -122.3145
4279.6719 | 122.4564 | -0.054932 | 122.2504 | -0.11169 | 0.0457 | 0.058618 | 0.0046827 | 0.030183 | -0.006663 | 0.028724 | -0.085144 | 0.025128 | 0.039018 | 0.048815 | -0.0023861 | 0.032913 | 0.091553 | 0.13275 | 0.10071 | 0.073242 | 0.059509 | 0.059509 | -0.086975 | 0.15106 | 0.15564 | 0.07782 | 0.027466 | 0.004578 | -0.032043 | -0.059509 | 0.11444 | -0.032043 | -122.1909 | 0.18768 | 0.12817 | 0.16022 | -122.1588 | 0.022889 | -0.004577 | -122.2229 | 0.20599 | 0.13275 | 0.13733 | -122.2458 | 0.11444 | 0.14649 | 0.15564 | -122.3373 | 0.082398 | 0.05951 | 0.21057 | -122.3099
4281.3594 | 122.3694 | -0.091553 | 122.2778 | -0.21851 | 0.047837 | 0.061609 | 0.0051099 | 0.029756 | -0.0053812 | 0.028083 | -0.14618 | 0.027051 | 0.035173 | 0.05031 | -0.0011045 | 0.030349 | 0.10071 | 0.13275 | 0.09613 | 0.064087 | 0.054932 | 0.045776 | -0.086975 | 0.14191 | 0.16937 | 0.041199 | 0.022888 | 0.018311 | -0.004578 | -0.082397 | 0.13733 | 0.004578 | -122.2229 | 0.2243 | 0.15564 | 0.15106 | -122.1771 | 0.086975 | 0.009156 | -122.2549 | 0.23346 | 0.13275 | 0.1236 | -122.2595 | 0.14649 | 0.19226 | 0.18768 | -122.3648 | 0.11444 | 0.10986 | 0.26093 | -122.3602
4283.0781 | 122.3785 | -0.064087 | 122.2641 | -0.11932 | 0.047837 | 0.058191 | -0.0023669 | 0.030183 | 0.0020956 | 0.030433 | -0.1767 | 0.027265 | 0.034746 | 0.052233 | 0.0042361 | 0.026931 | 0.082397 | 0.050354 | 0.018311 | 0.013733 | 0.082397 | -0.004578 | -0.15564 | 0.082397 | 0.073242 | -0.059509 | 0.059509 | 0.018311 | -0.032043 | -0.091553 | 0.059509 | -0.091553 | -122.1817 | 0.11444 | 0.07782 | 0.16937 | -122.1817 | 0.032044 | -0.027466 | -122.2046 | 0.14648 | 0.004578 | 0.032044 | -122.2458 | 0.14648 | 0.14648 | 0.082398 | -122.4197 | 0.1236 | 0.082398 | 0.13733 | -122.3557
4284.7812 | 122.3557 | -0.10529 | 122.2641 | -0.18036 | 0.049118 | 0.061609 | 0.0025465 | 0.029756 | -0.0045266 | 0.030006 | -0.13855 | 0.022992 | 0.037309 | 0.048174 | -0.0030271 | 0.031631 | 0.082397 | 0.14191 | 0.10986 | 0.068665 | 0.050354 | 0.036621 | -0.10071 | 0.11444 | 0.15564 | 0.027466 | 0.036621 | 0.013733 | -0.022888 | -0.073242 | 0.14191 | 0.004578 | -122.2137 | 0.24719 | 0.17395 | 0.16937 | -122.1817 | 0.082398 | 0.032044 | -122.2275 | 0.21973 | 0.13275 | 0.10071 | -122.2504 | 0.15564 | 0.18768 | 0.21515 | -122.3648 | 0.14191 | 0.11902 | 0.26093 | -122.3373
4286.4688 | 122.4564 | -0.068665 | 122.2366 | 0.08667 | 0.048477 | 0.059045 | -0.00023075 | 0.026338 | -0.00068138 | 0.030433 | 0.082703 | 0.028974 | 0.035387 | 0.049883 | 0.0048769 | 0.029922 | 0.018311 | 0.009155 | -0.004578 | -0.009155 | 0.11444 | 0.013733 | -0.13733 | 0.091553 | 0.054932 | -0.027466 | 0.050354 | 0.045776 | -0.027466 | -0.082397 | 0.082398 | -0.068664 | -122.1222 | 0.07782 | 0.05951 | 0.12817 | -122.2183 | 0.041199 | -0.013732 | -122.1863 | 0.16022 | 0.041199 | 0.054931 | -122.1909 | 0.18311 | 0.086976 | 0.064087 | -122.374 | 0.11902 | 0.11444 | 0.1236 | -122.319
4288.1719 | 122.3419 | -0.10529 | 122.287 | -0.24139 | 0.048691 | 0.060541 | 0.0038281 | 0.028901 | -0.0028178 | 0.030219 | -0.14618 | 0.027692 | 0.035814 | 0.050097 | -0.0015317 | 0.030349 | 0.018311 | 0.022888 | 0.009155 | 0.013733 | 0.091553 | 0.004578 | -0.12817 | 0.032043 | 0.045776 | -0.064087 | 0.07782 | 0.050354 | -0.054932 | -0.10071 | 0.10986 | -0.022888 | -122.1954 | 0.12817 | 0.11902 | 0.14191 | -122.2687 | 0.050354 | 0.004578 | -122.2092 | 0.13733 | 0.041199 | 0.036621 | -122.2366 | 0.19684 | 0.1236 | 0.11444 | -122.4152 | 0.18311 | 0.15564 | 0.15106 | -122.3877
4289.8906 | 122.4976 | -0.054932 | 122.2412 | -0.050659 | 0.04506 | 0.061395 | 0.0014783 | 0.027833 | -0.0070902 | 0.029365 | -0.039368 | 0.025128 | 0.035387 | 0.047533 | -3.629e-05 | 0.032699 | 0.041199 | 0.10071 | 0.082397 | 0.050354 | 0.068665 | 0.036621 | -0.10529 | 0.13275 | 0.17853 | 0.050354 | 0.027466 | 0.022888 | -0.022888 | -0.059509 | 0.091553 | -0.050354 | -122.1725 | 0.15564 | 0.10529 | 0.15564 | -122.2 | 0.032044 | -0.004577 | -122.2137 | 0.18768 | 0.10529 | 0.10986 | -122.2183 | 0.1236 | 0.096131 | 0.13733 | -122.3465 | 0.082398 | 0.07782 | 0.23346 | -122.3007
4291.6406 | 122.3923 | -0.09613 | 122.2595 | -0.19562 | 0.048477 | 0.0599 | 0.0014783 | 0.029756 | 0.00081382 | 0.030646 | -0.20721 | 0.027692 | 0.036241 | 0.050738 | 0.0027407 | 0.029068 | 0.036621 | 0.032043 | -0.009155 | 0.018311 | 0.09613 | 0.009155 | -0.11902 | 0.054932 | 0.07782 | -0.054932 | 0.064087 | 0.045776 | -0.045776 | -0.10529 | 0.10528 | -0.022889 | -122.1634 | 0.12817 | 0.11444 | 0.13733 | -122.2229 | 0.050354 | -0.009156 | -122.1954 | 0.15106 | 0.041198 | 0.050354 | -122.2137 | 0.19226 | 0.13275 | 0.086975 | -122.3785 | 0.16022 | 0.14191 | 0.17395 | -122.3648
4293.3438 | 122.4609 | -0.045776 | 122.2412 | -0.14984 | 0.04506 | 0.061395 | 0.0040417 | 0.029115 | -0.0090128 | 0.031714 | -0.10803 | 0.022351 | 0.036882 | 0.049456 | -0.0034543 | 0.031845 | 0.07782 | 0.15564 | 0.12817 | 0.082397 | 0.059509 | 0.050354 | -0.10986 | 0.15106 | 0.17853 | 0.07782 | 0.036621 | 0.004578 | -0.018311 | -0.07782 | 0.09613 | -0.064087 | -122.1817 | 0.20142 | 0.12817 | 0.19226 | -122.1634 | 0.027465 | -0.032044 | -122.2046 | 0.19684 | 0.1236 | 0.15564 | -122.2366 | 0.10528 | 0.1236 | 0.17395 | -122.3511 | 0.082397 | 0.050354 | 0.2243 | -122.319
4295.0469 | 122.3282 | -0.10529 | 122.2687 | -0.14984 | 0.047623 | 0.061182 | 0.0023329 | 0.030824 | -0.0019632 | 0.028724 | -0.22247 | 0.028119 | 0.0356 | 0.049456 | 0.0020999 | 0.032699 | -0.004578 | 0.013733 | -0.009155 | -0.018311 | 0.10529 | 0.013733 | -0.14648 | 0.018311 | 0.059509 | -0.073242 | 0.073242 | 0.050354 | -0.064087 | -0.10529 | 0.11902 | -0.041198 | -122.1634 | 0.11902 | 0.086975 | 0.12817 | -122.2733 | 0.041199 | 0 | -122.1954 | 0.1236 | 0.032044 | 0.032044 | -122.2183 | 0.21057 | 0.10071 | 0.096131 | -122.4152 | 0.17853 | 0.15564 | 0.16479 | -122.374
4296.7344 | 122.4197 | -0.07782 | 122.2366 | 0.056152 | 0.043137 | 0.063532 | 0.00019645 | 0.031037 | -0.0073038 | 0.029151 | 0.067444 | 0.026197 | 0.035387 | 0.049669 | -0.00024989 | 0.033126 | 0.054932 | 0.09613 | 0.054932 | 0.036621 | 0.054932 | 0.027466 | -0.10071 | 0.10986 | 0.086975 | 0.009155 | 0.022888 | 0.018311 | -0.022888 | -0.064087 | 0.10529 | -0.022888 | -122.1817 | 0.17395 | 0.11444 | 0.13733 | -122.1817 | 0.054932 | 0.013733 | -122.2137 | 0.18768 | 0.086975 | 0.073242 | -122.2183 | 0.13275 | 0.13275 | 0.13275 | -122.3373 | 0.10071 | 0.096131 | 0.16479 | -122.3007
4298.4375 | 122.3877 | -0.086975 | 122.2595 | -0.18036 | 0.047196 | 0.060114 | 0.0027601 | 0.028047 | 0.00017302 | 0.030646 | -0.2301 | 0.028333 | 0.0356 | 0.052019 | 0.0029543 | 0.029708 | 0.022888 | 0.013733 | -0.018311 | 0.018311 | 0.09613 | 0.004578 | -0.14648 | 0.068665 | 0.064087 | -0.059509 | 0.050354 | 0.064087 | -0.032043 | -0.10529 | 0.091553 | -0.059509 | -122.1634 | 0.10071 | 0.10529 | 0.16479 | -122.2366 | 0.054932 | -0.018311 | -122.2092 | 0.15564 | 0.027466 | 0.045777 | -122.1954 | 0.1831 | 0.10986 | 0.068664 | -122.406 | 0.13733 | 0.15106 | 0.15106 | -122.3648
4300.1875 | 122.3328 | -0.11444 | 122.2687 | -0.22614 | 0.046768 | 0.060114 | 0.0046827 | 0.029969 | -0.004954 | 0.030433 | -0.13092 | 0.02641 | 0.03795 | 0.050524 | -0.0015317 | 0.032699 | 0.013733 | 0.050354 | 0.013733 | 0 | 0.091553 | 0.004578 | -0.13733 | 0.018311 | 0.050354 | -0.068665 | 0.073242 | 0.064087 | -0.059509 | -0.10529 | 0.11902 | -0.022888 | -122.1771 | 0.16479 | 0.11444 | 0.13733 | -122.2549 | 0.054932 | 0.009155 | -122.1954 | 0.13275 | 0.045776 | 0.036621 | -122.2046 | 0.20599 | 0.12817 | 0.12817 | -122.406 | 0.18768 | 0.17853 | 0.16479 | -122.374
4301.8906 | 122.4747 | -0.059509 | 122.2229 | -0.020142 | 0.042282 | 0.062463 | -0.00065795 | 0.030397 | -0.00944 | 0.030219 | 0.036926 | 0.026624 | 0.033678 | 0.049242 | -3.629e-05 | 0.033554 | 0.004578 | 0.073242 | 0.059509 | 0.032043 | 0.064087 | 0.027466 | -0.091553 | 0.086975 | 0.086975 | 0.004578 | 0.045776 | 0.009155 | -0.036621 | -0.068665 | 0.086975 | -0.032044 | -122.1588 | 0.13275 | 0.091552 | 0.1236 | -122.2183 | 0.022888 | -0.009156 | -122.1771 | 0.14648 | 0.064087 | 0.073243 | -122.2137 | 0.1236 | 0.064087 | 0.11902 | -122.3145 | 0.10528 | 0.068664 | 0.14648 | -122.2916
4303.6406 | 122.3969 | -0.10071 | 122.2504 | -0.20325 | 0.0457 | 0.059045 | 0.0014783 | 0.031892 | 0.0014548 | 0.029792 | -0.20721 | 0.028333 | 0.035814 | 0.05266 | 0.0016727 | 0.031631 | 0.036621 | 0.013733 | -0.004578 | -0.004578 | 0.11444 | 0 | -0.14648 | 0.059509 | 0.068665 | -0.059509 | 0.064087 | 0.050354 | -0.059509 | -0.10529 | 0.10071 | -0.045776 | -122.1359 | 0.11444 | 0.09613 | 0.14191 | -122.2137 | 0.041199 | -0.004578 | -122.1863 | 0.16022 | 0.041199 | 0.045777 | -122.2 | 0.21515 | 0.13733 | 0.09613 | -122.3969 | 0.1648 | 0.15106 | 0.16937 | -122.3557
4305.375 | 122.3511 | -0.10071 | 122.2778 | -0.19562 | 0.048264 | 0.058405 | 0.0038281 | 0.026979 | -0.004313 | 0.029578 | -0.24536 | 0.026837 | 0.037736 | 0.051378 | -0.0011045 | 0.030136 | -0.009155 | -0.013733 | -0.018311 | -0.009155 | 0.09613 | 0 | -0.13733 | 0.018311 | 0.036621 | -0.086975 | 0.073242 | 0.059509 | -0.073242 | -0.10529 | 0.10071 | -0.036621 | -122.1817 | 0.086975 | 0.091553 | 0.12817 | -122.287 | 0.027466 | -0.004578 | -122.2046 | 0.11902 | 0.013733 | 0.018311 | -122.2183 | 0.19684 | 0.091553 | 0.082397 | -122.4152 | 0.17395 | 0.16022 | 0.13733 | -122.3831
4307.0781 | 122.4335 | -0.082397 | 122.2275 | 0.063782 | 0.047837 | 0.061395 | -0.0023669 | 0.028474 | -0.0017496 | 0.030433 | 0.052185 | 0.027478 | 0.035387 | 0.052233 | 0.0020999 | 0.031631 | 0.009155 | -0.009155 | -0.036621 | -0.013733 | 0.10529 | 0.013733 | -0.13275 | 0.054932 | 0.018311 | -0.068665 | 0.054932 | 0.041199 | -0.045776 | -0.11444 | 0.09613 | -0.050354 | -122.1222 | 0.073242 | 0.068664 | 0.11902 | -122.2183 | 0.036621 | -0.032044 | -122.1725 | 0.13733 | 0.013732 | 0.045776 | -122.1863 | 0.18768 | 0.091552 | 0.045776 | -122.3602 | 0.13733 | 0.1236 | 0.10071 | -122.3419
4308.8125 | 122.3877 | -0.073242 | 122.2961 | -0.24139 | 0.047196 | 0.059686 | 0.0063917 | 0.029328 | -0.00068138 | 0.028937 | -0.20721 | 0.028333 | 0.03795 | 0.053087 | -3.629e-05 | 0.032272 | 0.004578 | 0.004578 | -0.036621 | -0.004578 | 0.091553 | 0 | -0.12817 | 0.004578 | 0.045776 | -0.09613 | 0.054932 | 0.059509 | -0.054932 | -0.11444 | 0.073242 | -0.054932 | -122.2046 | 0.07782 | 0.068664 | 0.1236 | -122.2916 | 0.01831 | -0.041199 | -122.2412 | 0.07782 | -0.022888 | 0.018311 | -122.2366 | 0.16479 | 0.07782 | 0.036621 | -122.4243 | 0.12817 | 0.13275 | 0.11902 | -122.4106
4310.6094 | 122.3511 | -0.086975 | 122.2733 | 0.025635 | 0.048905 | 0.060968 | 0.0012647 | 0.027619 | 0.0012412 | 0.032569 | 0.036926 | 0.02876 | 0.036027 | 0.050097 | 0.0048769 | 0.033126 | -0.018311 | -0.036621 | -0.059509 | -0.022888 | 0.082397 | 0.009155 | -0.13733 | 0.022888 | -0.027466 | -0.10071 | 0.059509 | 0.050354 | -0.050354 | -0.086975 | 0.09613 | -0.050354 | -122.1909 | 0.050354 | 0.064087 | 0.11444 | -122.2916 | 0.036621 | 0 | -122.2137 | 0.10986 | -0.013733 | -0.013733 | -122.2229 | 0.16937 | 0.068664 | 0.027466 | -122.4106 | 0.14648 | 0.13733 | 0.059509 | -122.3602
4312.3906 | 122.3282 | -0.082397 | 122.287 | -0.081177 | 0.047623 | 0.060114 | 0.0031873 | 0.032533 | -0.00046778 | 0.031501 | -0.1004 | 0.027906 | 0.037523 | 0.052019 | 0.0040225 | 0.032272 | 0.059509 | 0.064087 | 0.018311 | 0.036621 | 0.082397 | -0.004578 | -0.14191 | 0.064087 | 0.07782 | -0.054932 | 0.045776 | 0.050354 | -0.050354 | -0.10986 | 0.077819 | -0.05951 | -122.2046 | 0.14648 | 0.11902 | 0.17853 | -122.2275 | 0.032043 | -0.027466 | -122.2412 | 0.14648 | 0.027465 | 0.054931 | -122.2366 | 0.16479 | 0.14191 | 0.10071 | -122.4289 | 0.12817 | 0.13275 | 0.16022 | -122.3969
4314.125 | 122.3557 | -0.10986 | 122.2824 | -0.17273 | 0.045914 | 0.061395 | 0.0063917 | 0.032319 | -0.0070902 | 0.030646 | -0.1767 | 0.027478 | 0.037309 | 0.051592 | -0.0013181 | 0.032058 | -0.045776 | 0.027466 | 0 | -0.018311 | 0.09613 | 0.009155 | -0.14191 | 0.004578 | 0.054932 | -0.064087 | 0.064087 | 0.050354 | -0.068665 | -0.12817 | 0.11902 | -0.032044 | -122.1863 | 0.13733 | 0.091552 | 0.1236 | -122.3282 | 0.041198 | -0.018311 | -122.2183 | 0.11444 | 0.045776 | 0.064087 | -122.2321 | 0.20599 | 0.064087 | 0.10986 | -122.4243 | 0.17395 | 0.16022 | 0.16479 | -122.4106
4315.8906 | 122.438 | -0.059509 | 122.2366 | -0.18036 | 0.046555 | 0.062036 | 0.0040417 | 0.032105 | -0.0087992 | 0.030646 | -0.13092 | 0.023633 | 0.036241 | 0.053515 | -0.0015317 | 0.034408 | 0.064087 | 0.15564 | 0.11902 | 0.064087 | 0.064087 | 0.059509 | -0.091553 | 0.11902 | 0.17853 | 0.073242 | 0.009155 | 0.009155 | -0.027466 | -0.059509 | 0.11902 | -0.032044 | -122.1725 | 0.21515 | 0.1236 | 0.15564 | -122.1725 | 0.032043 | 0 | -122.2275 | 0.17853 | 0.13275 | 0.13275 | -122.2275 | 0.1236 | 0.1236 | 0.17853 | -122.3282 | 0.068664 | 0.068664 | 0.23804 | -122.2961
4317.6562 | 122.3602 | -0.10071 | 122.2824 | -0.23376 | 0.047409 | 0.060968 | 0.0068189 | 0.028047 | -0.0036722 | 0.029151 | -0.2301 | 0.027051 | 0.038377 | 0.052874 | -0.0025999 | 0.030777 | -0.027466 | -0.004578 | -0.022888 | -0.018311 | 0.09613 | 0 | -0.15564 | 0.018311 | 0.018311 | -0.068665 | 0.068665 | 0.068665 | -0.073242 | -0.10986 | 0.10071 | -0.054932 | -122.1863 | 0.09613 | 0.082397 | 0.13733 | -122.3099 | 0.027466 | -0.009155 | -122.2137 | 0.11902 | 0.032043 | 0.041198 | -122.2137 | 0.19684 | 0.073242 | 0.07782 | -122.4381 | 0.16937 | 0.16937 | 0.11902 | -122.3923
4319.3594 | 122.4884 | -0.045776 | 122.2366 | -0.027771 | 0.042496 | 0.061182 | 0.0036145 | 0.029969 | -0.0079446 | 0.028297 | -0.0012209 | 0.025983 | 0.033464 | 0.052447 | -0.00046349 | 0.032699 | 0.036621 | 0.07782 | 0.068665 | 0.050354 | 0.059509 | 0.041199 | -0.10071 | 0.11902 | 0.1236 | 0.054932 | 0.036621 | 0.022888 | -0.013733 | -0.068665 | 0.086975 | -0.054932 | -122.1771 | 0.1236 | 0.09613 | 0.15106 | -122.2 | 0.032043 | -0.022889 | -122.2 | 0.16479 | 0.10071 | 0.1236 | -122.2137 | 0.10528 | 0.082397 | 0.11444 | -122.3373 | 0.082397 | 0.068664 | 0.16937 | -122.3053
4321.125 | 122.4289 | -0.073242 | 122.2549 | 0.033264 | 0.042282 | 0.06225 | 0.00062385 | 0.032105 | -0.0064492 | 0.029151 | 0.067444 | 0.023847 | 0.035814 | 0.048174 | -0.0013181 | 0.032058 | 0.032043 | 0.064087 | 0.050354 | 0.041199 | 0.064087 | 0.036621 | -0.10071 | 0.086975 | 0.073242 | 0 | 0.036621 | 0 | -0.041199 | -0.064087 | 0.10986 | -0.027466 | -122.1909 | 0.13733 | 0.11444 | 0.14191 | -122.2229 | 0.032043 | 0.009155 | -122.2183 | 0.16022 | 0.073242 | 0.064087 | -122.2549 | 0.13733 | 0.10529 | 0.1236 | -122.3557 | 0.10986 | 0.073242 | 0.14648 | -122.319
4322.8125 | 122.3648 | -0.10071 | 122.2687 | -0.24139 | 0.049759 | 0.060754 | 0.0061781 | 0.031678 | -0.0021768 | 0.02851 | -0.26825 | 0.026624 | 0.037736 | 0.051592 | -0.00024989 | 0.029922 | 0 | -0.004578 | -0.036621 | -0.009155 | 0.09613 | 0.009155 | -0.15106 | 0.027466 | 0.032043 | -0.086975 | 0.068665 | 0.064087 | -0.064087 | -0.1236 | 0.10986 | -0.050354 | -122.1725 | 0.09613 | 0.091553 | 0.14191 | -122.2687 | 0.036621 | -0.022888 | -122.2 | 0.12817 | 0.013733 | 0.036621 | -122.2046 | 0.19684 | 0.10071 | 0.064087 | -122.4197 | 0.16937 | 0.1648 | 0.13275 | -122.3923
4324.5781 | 122.3511 | -0.082397 | 122.2778 | -0.088806 | 0.047409 | 0.057977 | 0.0036145 | 0.029115 | 0.001882 | 0.030006 | -0.16144 | 0.027906 | 0.036882 | 0.053942 | 0.0046633 | 0.028854 | 0.082397 | 0.050354 | 0.027466 | 0.027466 | 0.086975 | 0.013733 | -0.1236 | 0.07782 | 0.07782 | -0.045776 | 0.059509 | 0.041199 | -0.032043 | -0.09613 | 0.09613 | -0.041199 | -122.1909 | 0.13275 | 0.10986 | 0.15106 | -122.1954 | 0.050354 | -0.013733 | -122.2183 | 0.16022 | 0.036621 | 0.050354 | -122.2366 | 0.16937 | 0.16479 | 0.10986 | -122.4014 | 0.14191 | 0.1236 | 0.16022 | -122.374
4326.3438 | 122.4106 | -0.091553 | 122.2641 | 0.025635 | 0.04271 | 0.0599 | 0.00041005 | 0.028901 | -0.0068766 | 0.027869 | 0.075073 | 0.024701 | 0.034746 | 0.04732 | 0.00081811 | 0.034622 | 0.036621 | 0.09613 | 0.064087 | 0.022888 | 0.054932 | 0.032043 | -0.11444 | 0.10071 | 0.09613 | 0.027466 | 0.027466 | 0.032043 | -0.018311 | -0.091553 | 0.1236 | -0.022888 | -122.2092 | 0.18768 | 0.11444 | 0.13733 | -122.2275 | 0.073242 | 0 | -122.2366 | 0.19226 | 0.11902 | 0.11902 | -122.2321 | 0.14649 | 0.12817 | 0.15564 | -122.3785 | 0.11902 | 0.1236 | 0.18768 | -122.3557
4328.1094 | 122.3328 | -0.10071 | 122.2641 | -0.096436 | 0.047837 | 0.060327 | 0.00083745 | 0.029969 | 0.0016684 | 0.03086 | -0.12329 | 0.029187 | 0.034959 | 0.050951 | 0.0025271 | 0.030777 | 0.082397 | 0.068665 | 0.009155 | 0.018311 | 0.082397 | 0.013733 | -0.12817 | 0.068665 | 0.064087 | -0.059509 | 0.054932 | 0.050354 | -0.045776 | -0.086975 | 0.11444 | -0.027466 | -122.1817 | 0.16937 | 0.11902 | 0.14649 | -122.1817 | 0.054932 | 0.013733 | -122.2092 | 0.16937 | 0.041199 | 0.027466 | -122.2137 | 0.18311 | 0.18311 | 0.10986 | -122.3923 | 0.15564 | 0.15106 | 0.1648 | -122.3511
4329.8125 | 122.3282 | -0.10986 | 122.2687 | -0.25665 | 0.049332 | 0.060754 | 0.0053235 | 0.030824 | -0.0051676 | 0.028297 | -0.20721 | 0.027051 | 0.037096 | 0.050951 | -0.0028135 | 0.032058 | 0.036621 | 0.082397 | 0.054932 | 0.027466 | 0.082397 | 0.018311 | -0.10986 | 0.041199 | 0.059509 | -0.036621 | 0.054932 | 0.054932 | -0.054932 | -0.091553 | 0.12817 | 0 | -122.1863 | 0.19226 | 0.13733 | 0.13733 | -122.2321 | 0.054931 | 0.01831 | -122.2137 | 0.15106 | 0.073242 | 0.054932 | -122.2137 | 0.19226 | 0.14648 | 0.16479 | -122.3785 | 0.16479 | 0.16479 | 0.16937 | -122.3602
4331.5781 | 122.4197 | -0.054932 | 122.2687 | 0.094299 | 0.044205 | 0.06225 | -0.0027941 | 0.031892 | -0.0062356 | 0.031287 | 0.13611 | 0.025342 | 0.035387 | 0.052447 | 0.00039091 | 0.033981 | 0.086975 | 0.12817 | 0.10986 | 0.050354 | 0.041199 | 0.064087 | -0.09613 | 0.15106 | 0.11444 | 0.032043 | 0.018311 | 0.013733 | -0.027466 | -0.07782 | 0.11902 | -0.041198 | -122.2275 | 0.18311 | 0.10529 | 0.14648 | -122.1817 | 0.027466 | -0.022888 | -122.2504 | 0.20599 | 0.086975 | 0.10986 | -122.2549 | 0.096131 | 0.14191 | 0.16479 | -122.3648 | 0.073243 | 0.068665 | 0.16937 | -122.3465
4333.3281 | 122.4197 | -0.064087 | 122.2549 | -0.18036 | 0.045487 | 0.062036 | 0.0053235 | 0.029115 | -0.0075174 | 0.028083 | -0.1767 | 0.024915 | 0.036668 | 0.050951 | 0.00017731 | 0.031845 | 0.10071 | 0.14648 | 0.13275 | 0.073242 | 0.054932 | 0.045776 | -0.086975 | 0.13275 | 0.18768 | 0.041199 | 0.004578 | 0.009155 | -0.018311 | -0.07782 | 0.10986 | -0.022888 | -122.2 | 0.21057 | 0.13733 | 0.16022 | -122.1542 | 0.045776 | -0.013733 | -122.2504 | 0.19684 | 0.10529 | 0.11902 | -122.2458 | 0.11902 | 0.1648 | 0.19684 | -122.3419 | 0.068665 | 0.073242 | 0.25177 | -122.3328
4335.0938 | 122.3373 | -0.10071 | 122.2778 | -0.027771 | 0.051468 | 0.060114 | -0.00044435 | 0.031465 | 0.0014548 | 0.03086 | -0.039368 | 0.030896 | 0.038164 | 0.052233 | 0.0031681 | 0.031417 | 0.027466 | -0.009155 | -0.022888 | 0 | 0.091553 | 0.018311 | -0.14191 | 0.018311 | -0.004578 | -0.13275 | 0.045776 | 0.032043 | -0.064087 | -0.10529 | 0.11902 | -0.041199 | -122.1863 | 0.091553 | 0.10071 | 0.14191 | -122.2504 | 0.036621 | -0.004578 | -122.2321 | 0.11902 | -0.032043 | -0.027465 | -122.2458 | 0.19226 | 0.12817 | 0.07782 | -122.4197 | 0.14648 | 0.13275 | 0.09613 | -122.3831
4336.8125 | 122.4426 | -0.064087 | 122.2412 | 0.0027468 | 0.043778 | 0.061823 | 0.0029737 | 0.029969 | -0.0070902 | 0.030006 | 0.052185 | 0.024915 | 0.036882 | 0.048815 | -0.00024989 | 0.03334 | 0.013733 | 0.07782 | 0.059509 | 0.027466 | 0.059509 | 0.036621 | -0.11444 | 0.082397 | 0.086975 | 0.004578 | 0.041199 | 0.022888 | -0.022888 | -0.082397 | 0.10071 | -0.050354 | -122.1817 | 0.14191 | 0.091553 | 0.14191 | -122.2275 | 0.041199 | -0.01831 | -122.2 | 0.14648 | 0.068665 | 0.086975 | -122.2183 | 0.1236 | 0.07782 | 0.1236 | -122.3557 | 0.10529 | 0.086975 | 0.15106 | -122.3236
4338.5625 | 122.4564 | -0.059509 | 122.2412 | -0.14221 | 0.04506 | 0.060754 | 0.0089551 | 0.028474 | -0.0058084 | 0.028937 | -0.14618 | 0.025128 | 0.036882 | 0.049029 | -0.0019589 | 0.032058 | 0.10529 | 0.14648 | 0.12817 | 0.07782 | 0.050354 | 0.036621 | -0.09613 | 0.11902 | 0.1831 | 0.064087 | 0.022888 | 0.009155 | -0.013733 | -0.045776 | 0.09613 | -0.036621 | -122.1909 | 0.20599 | 0.13733 | 0.17395 | -122.1359 | 0.045776 | 0.013733 | -122.2183 | 0.17853 | 0.1236 | 0.10986 | -122.2321 | 0.10986 | 0.16479 | 0.18768 | -122.3373 | 0.082397 | 0.068664 | 0.24261 | -122.287
4340.3281 | 122.3785 | -0.10071 | 122.2733 | -0.18036 | 0.047409 | 0.059686 | 0.0016919 | 0.031251 | -4.058e-05 | 0.031074 | -0.26825 | 0.02641 | 0.037096 | 0.053942 | 0.00060451 | 0.027145 | 0.022888 | -0.009155 | -0.027466 | -0.009155 | 0.10986 | 0 | -0.13733 | 0.036621 | 0.054932 | -0.07782 | 0.050354 | 0.036621 | -0.050354 | -0.10529 | 0.10071 | -0.036621 | -122.1634 | 0.091553 | 0.091553 | 0.12817 | -122.2504 | 0.050354 | -0.004578 | -122.2229 | 0.13733 | 0.022888 | 0.027466 | -122.2366 | 0.21057 | 0.1236 | 0.073242 | -122.4106 | 0.15106 | 0.13733 | 0.15564 | -122.3785
4342.0938 | 122.4564 | -0.045776 | 122.2321 | -0.11932 | 0.045914 | 0.06225 | 0.0029737 | 0.029756 | -0.0085856 | 0.030006 | -0.1004 | 0.02406 | 0.036241 | 0.05031 | -0.0036679 | 0.032272 | 0.091553 | 0.15106 | 0.10986 | 0.073242 | 0.086975 | 0.041199 | -0.09613 | 0.16937 | 0.17395 | 0.064087 | 0.022888 | -0.004578 | -0.013733 | -0.082397 | 0.086975 | -0.050354 | -122.1451 | 0.19684 | 0.11902 | 0.16937 | -122.1405 | 0.032043 | -0.036621 | -122.2092 | 0.21515 | 0.10986 | 0.14648 | -122.2366 | 0.13275 | 0.13733 | 0.15564 | -122.3282 | 0.068664 | 0.041198 | 0.21973 | -122.3145
4343.7969 | 122.4701 | -0.054932 | 122.2321 | -0.096436 | 0.046555 | 0.063318 | 0.0044691 | 0.027833 | -0.0073038 | 0.027015 | -0.10803 | 0.023633 | 0.035173 | 0.051806 | -0.0021725 | 0.030136 | 0.082397 | 0.11902 | 0.091553 | 0.054932 | 0.073242 | 0.036621 | -0.10529 | 0.14648 | 0.16479 | 0.059509 | 0.032043 | 0.018311 | -0.018311 | -0.082397 | 0.091553 | -0.050354 | -122.1588 | 0.17395 | 0.10986 | 0.16022 | -122.1497 | 0.036621 | -0.027465 | -122.2 | 0.20142 | 0.11444 | 0.14191 | -122.2137 | 0.12817 | 0.13733 | 0.14649 | -122.3373 | 0.086975 | 0.073243 | 0.21973 | -122.3145
4345.5625 | 122.3236 | -0.10986 | 122.2916 | -0.088806 | 0.048477 | 0.057764 | 0.0014783 | 0.032319 | 0.0040182 | 0.028724 | -0.13855 | 0.029401 | 0.036455 | 0.053301 | 0.0055179 | 0.026718 | 0.091553 | 0.068665 | 0.022888 | 0.032043 | 0.086975 | 0.032043 | -0.11902 | 0.086975 | 0.054932 | -0.068665 | 0.045776 | 0.022888 | -0.054932 | -0.10529 | 0.14191 | -0.009156 | -122.2046 | 0.17853 | 0.14191 | 0.15106 | -122.2 | 0.054931 | 0.004577 | -122.2458 | 0.19684 | 0.041198 | 0.036621 | -122.2687 | 0.19684 | 0.20142 | 0.13275 | -122.4106 | 0.15564 | 0.13275 | 0.16479 | -122.3969
4347.3281 | 122.3328 | -0.091553 | 122.2687 | -0.012512 | 0.050186 | 0.059045 | 0.00062385 | 0.031037 | 0.0020956 | 0.030219 | -0.016479 | 0.027478 | 0.036882 | 0.049456 | 0.0067997 | 0.032058 | 0.027466 | 0.018311 | -0.004578 | -0.009155 | 0.082397 | 0.018311 | -0.14191 | 0.032043 | 0 | -0.10986 | 0.045776 | 0.054932 | -0.045776 | -0.11444 | 0.10986 | -0.050354 | -122.1863 | 0.10986 | 0.082398 | 0.13275 | -122.2412 | 0.045777 | -0.022888 | -122.2229 | 0.1236 | -0.01831 | 0.004578 | -122.2137 | 0.17395 | 0.11902 | 0.086975 | -122.4106 | 0.13733 | 0.14649 | 0.091553 | -122.3831
4349.0312 | 122.3877 | -0.10529 | 122.2824 | -0.19562 | 0.048905 | 0.060114 | 0.0051099 | 0.031678 | -0.0040994 | 0.031928 | -0.22247 | 0.026837 | 0.036668 | 0.051378 | -0.00046349 | 0.031845 | 0.004578 | 0.009155 | -0.022888 | 0.004578 | 0.09613 | 0 | -0.12817 | 0.041199 | 0.068665 | -0.073242 | 0.050354 | 0.027466 | -0.054932 | -0.11902 | 0.10529 | -0.022888 | -122.1863 | 0.11444 | 0.10986 | 0.13275 | -122.2778 | 0.050354 | -0.013733 | -122.2321 | 0.14649 | 0.032044 | 0.045777 | -122.2549 | 0.20142 | 0.10986 | 0.082398 | -122.4106 | 0.15564 | 0.13275 | 0.17395 | -122.4014
4350.7969 | 122.3557 | -0.082397 | 122.2549 | 0.040894 | 0.048477 | 0.059045 | 0.0021191 | 0.029328 | -0.00089518 | 0.031074 | 0.052185 | 0.027692 | 0.035387 | 0.053301 | 0.0012455 | 0.031845 | -0.013733 | -0.059509 | -0.07782 | -0.027466 | 0.091553 | 0.022888 | -0.12817 | 0.032043 | -0.022888 | -0.10529 | 0.059509 | 0.054932 | -0.054932 | -0.10986 | 0.10528 | -0.045777 | -122.1634 | 0.022888 | 0.054931 | 0.10071 | -122.2687 | 0.027465 | -0.027466 | -122.1954 | 0.11444 | -0.022889 | 0.004577 | -122.2 | 0.17395 | 0.068664 | 0.004577 | -122.3831 | 0.14191 | 0.13733 | 0.059509 | -122.3648
4352.5781 | 122.3373 | -0.10529 | 122.2733 | -0.18799 | 0.048264 | 0.060541 | 0.0078871 | 0.030824 | -0.006022 | 0.03086 | -0.20721 | 0.027478 | 0.036027 | 0.054369 | -0.0023861 | 0.033767 | -0.009155 | 0 | -0.022888 | -0.018311 | 0.10071 | 0.018311 | -0.15564 | 0.009155 | 0.041199 | -0.068665 | 0.059509 | 0.064087 | -0.064087 | -0.11444 | 0.1236 | -0.050354 | -122.1725 | 0.10529 | 0.086975 | 0.13733 | -122.2824 | 0.041199 | -0.009155 | -122.2137 | 0.11444 | 0.036621 | 0.045776 | -122.2092 | 0.20599 | 0.096131 | 0.082398 | -122.4289 | 0.16479 | 0.16937 | 0.14649 | -122.3877
4354.2812 | 122.4518 | -0.045776 | 122.2 | 0.12482 | 0.048264 | 0.059473 | 0.0014783 | 0.029969 | -0.0034586 | 0.032569 | 0.097962 | 0.026837 | 0.034746 | 0.050951 | 0.0035953 | 0.031631 | 0.082397 | 0.082397 | 0.082397 | 0.059509 | 0.050354 | 0.041199 | -0.091553 | 0.13733 | 0.11902 | 0.027466 | 0.013733 | 0.022888 | -0.027466 | -0.073242 | 0.086975 | -0.045777 | -122.1497 | 0.12817 | 0.10528 | 0.15106 | -122.1176 | 0.01831 | -0.027466 | -122.1863 | 0.18311 | 0.073242 | 0.10071 | -122.1771 | 0.09613 | 0.12817 | 0.12817 | -122.2916 | 0.059509 | 0.068664 | 0.16479 | -122.2733
4356.0469 | 122.3465 | -0.09613 | 122.2412 | -0.20325 | 0.048264 | 0.062463 | 0.0031873 | 0.03061 | -0.0070902 | 0.027656 | -0.1004 | 0.025342 | 0.034959 | 0.050951 | -0.00089089 | 0.032913 | 0.07782 | 0.13275 | 0.10986 | 0.068665 | 0.073242 | 0.059509 | -0.09613 | 0.10529 | 0.17853 | 0.050354 | 0.022888 | 0.018311 | -0.009155 | -0.091553 | 0.15564 | 0 | -122.168 | 0.22888 | 0.16479 | 0.16479 | -122.1634 | 0.086975 | 0.004577 | -122.2183 | 0.20142 | 0.14648 | 0.14191 | -122.2229 | 0.16937 | 0.17395 | 0.20599 | -122.3373 | 0.11902 | 0.11444 | 0.27466 | -122.3328
4357.8125 | 122.374 | -0.086975 | 122.2504 | -0.12695 | 0.049759 | 0.058191 | -0.0019397 | 0.030397 | 0.0016684 | 0.029578 | -0.16144 | 0.030042 | 0.036455 | 0.052874 | 0.0040225 | 0.028854 | 0.059509 | 0.041199 | 0.013733 | 0.018311 | 0.09613 | 0.009155 | -0.11902 | 0.064087 | 0.073242 | -0.050354 | 0.073242 | 0.054932 | -0.041199 | -0.09613 | 0.09613 | -0.032044 | -122.1542 | 0.12817 | 0.10529 | 0.13733 | -122.1909 | 0.045776 | -0.009155 | -122.1771 | 0.15106 | 0.036621 | 0.045776 | -122.1954 | 0.1831 | 0.14648 | 0.10071 | -122.3694 | 0.16022 | 0.14191 | 0.16022 | -122.3465
4359.5781 | 122.4152 | -0.064087 | 122.2549 | 0.10193 | 0.044846 | 0.063104 | 0.0012647 | 0.028688 | -0.0087992 | 0.02851 | 0.13611 | 0.027265 | 0.036027 | 0.049669 | -0.00046349 | 0.033981 | 0.059509 | 0.091553 | 0.07782 | 0.032043 | 0.045776 | 0.032043 | -0.10529 | 0.10071 | 0.10071 | -0.018311 | 0.018311 | 0.004578 | -0.022888 | -0.091553 | 0.09613 | -0.041199 | -122.2092 | 0.15564 | 0.09613 | 0.13733 | -122.1954 | 0.041199 | -0.027466 | -122.2366 | 0.1648 | 0.045776 | 0.073242 | -122.2504 | 0.10986 | 0.1236 | 0.14191 | -122.3602 | 0.082398 | 0.068665 | 0.1648 | -122.3465
4361.3438 | 122.3831 | -0.10529 | 122.2504 | 0.079041 | 0.048905 | 0.061182 | 0.0021191 | 0.029115 | 0.00017302 | 0.031287 | 0.059815 | 0.027265 | 0.034318 | 0.052447 | 0.0027407 | 0.031845 | 0.013733 | -0.045776 | -0.027466 | -0.004578 | 0.10529 | -0.004578 | -0.13733 | 0.018311 | -0.018311 | -0.11444 | 0.059509 | 0.059509 | -0.068665 | -0.11902 | 0.10071 | -0.032043 | -122.1451 | 0.05951 | 0.10071 | 0.13275 | -122.2366 | 0.036621 | -0.013733 | -122.1909 | 0.1236 | -0.009155 | 0.004578 | -122.1909 | 0.21057 | 0.11902 | 0.07782 | -122.3877 | 0.16479 | 0.16479 | 0.086975 | -122.3694
4363.125 | 122.4426 | -0.041199 | 122.2549 | -0.15747 | 0.046128 | 0.060754 | 0.0070325 | 0.030824 | -0.0081582 | 0.030219 | -0.12329 | 0.02406 | 0.035814 | 0.048815 | -0.0034543 | 0.033981 | 0.09613 | 0.14191 | 0.11444 | 0.082397 | 0.050354 | 0.041199 | -0.091553 | 0.12817 | 0.19684 | 0.082397 | 0.018311 | 0.018311 | -0.009155 | -0.054932 | 0.082398 | -0.050354 | -122.2046 | 0.18311 | 0.1236 | 0.17395 | -122.1588 | 0.032044 | -0.013733 | -122.2366 | 0.16937 | 0.1236 | 0.13733 | -122.2366 | 0.091553 | 0.13733 | 0.15564 | -122.3465 | 0.05951 | 0.05951 | 0.23804 | -122.3099
4364.8281 | 122.4655 | -0.054932 | 122.2183 | -0.073547 | 0.04506 | 0.060968 | 0.0023329 | 0.027192 | -0.00944 | 0.027228 | -0.031738 | 0.023847 | 0.036241 | 0.052019 | -0.0019589 | 0.033126 | 0.059509 | 0.10529 | 0.086975 | 0.059509 | 0.073242 | 0.045776 | -0.10529 | 0.14648 | 0.16479 | 0.054932 | 0.022888 | 0.022888 | -0.022888 | -0.068665 | 0.10071 | -0.050354 | -122.1451 | 0.16022 | 0.11444 | 0.16479 | -122.1588 | 0.032044 | -0.013733 | -122.1954 | 0.20142 | 0.10986 | 0.1236 | -122.1954 | 0.12817 | 0.11444 | 0.14191 | -122.3236 | 0.07782 | 0.07782 | 0.21973 | -122.287
4366.5938 | 122.4564 | -0.054932 | 122.2321 | -0.020142 | 0.043351 | 0.062677 | 0.00019645 | 0.029115 | -0.0075174 | 0.026374 | 0.029297 | 0.023419 | 0.033678 | 0.048174 | -0.0017453 | 0.033554 | 0.022888 | 0.068665 | 0.064087 | 0.032043 | 0.064087 | 0.022888 | -0.11444 | 0.086975 | 0.09613 | 0.013733 | 0.032043 | 0.022888 | -0.032043 | -0.086975 | 0.07782 | -0.059509 | -122.168 | 0.1236 | 0.086975 | 0.14648 | -122.2092 | 0.022889 | -0.032043 | -122.2 | 0.14191 | 0.068665 | 0.10071 | -122.2092 | 0.11902 | 0.07782 | 0.11902 | -122.3465 | 0.086975 | 0.07782 | 0.15106 | -122.319
4368.3438 | 122.3557 | -0.10529 | 122.2549 | -0.21088 | 0.046982 | 0.058618 | 0.0016919 | 0.029542 | -0.003245 | 0.028297 | -0.27588 | 0.027692 | 0.036027 | 0.051165 | -3.629e-05 | 0.030563 | 0.004578 | 0 | -0.022888 | -0.018311 | 0.09613 | 0.004578 | -0.14191 | 0.018311 | 0.032043 | -0.086975 | 0.068665 | 0.059509 | -0.050354 | -0.1236 | 0.10986 | -0.036621 | -122.1588 | 0.10529 | 0.086975 | 0.1236 | -122.2504 | 0.054932 | -0.01831 | -122.1863 | 0.1236 | 0.018311 | 0.036621 | -122.1954 | 0.20142 | 0.10986 | 0.082398 | -122.3969 | 0.17395 | 0.16479 | 0.13733 | -122.3785
4370.0469 | 122.4655 | -0.059509 | 122.2092 | 0.15533 | 0.045487 | 0.06225 | -0.00044435 | 0.027833 | -0.00089518 | 0.028083 | 0.13611 | 0.026197 | 0.034105 | 0.050738 | 0.0018863 | 0.029281 | 0.086975 | 0.082397 | 0.064087 | 0.045776 | 0.059509 | 0.041199 | -0.086975 | 0.14191 | 0.10986 | 0.022888 | 0.004578 | 0.009155 | -0.009155 | -0.086975 | 0.10071 | -0.027466 | -122.1497 | 0.14191 | 0.10528 | 0.13275 | -122.1222 | 0.050354 | -0.027466 | -122.2046 | 0.20142 | 0.082397 | 0.10986 | -122.2 | 0.11902 | 0.14648 | 0.1236 | -122.2961 | 0.064087 | 0.068664 | 0.16937 | -122.2961
4371.8281 | 122.3419 | -0.07782 | 122.2595 | -0.081177 | 0.048905 | 0.057764 | 0.0021191 | 0.031037 | 0.00060022 | 0.029365 | -0.15381 | 0.029187 | 0.036882 | 0.051592 | 0.0016727 | 0.030777 | 0.068665 | 0.059509 | 0.013733 | 0.027466 | 0.086975 | 0 | -0.1236 | 0.10529 | 0.082397 | -0.054932 | 0.045776 | 0.032043 | -0.064087 | -0.10529 | 0.07782 | -0.045776 | -122.1725 | 0.13733 | 0.10529 | 0.15106 | -122.1909 | 0.013733 | -0.027466 | -122.2137 | 0.18311 | 0.022888 | 0.050354 | -122.2275 | 0.16479 | 0.14649 | 0.091553 | -122.3831 | 0.1236 | 0.10986 | 0.16022 | -122.3648
4373.5938 | 122.4838 | -0.050354 | 122.2595 | -0.065918 | 0.044632 | 0.06225 | 0.0038281 | 0.028901 | -0.010508 | 0.028937 | -0.14618 | 0.024488 | 0.034746 | 0.049456 | -0.0011045 | 0.034622 | 0.050354 | 0.11444 | 0.086975 | 0.068665 | 0.064087 | 0.054932 | -0.10071 | 0.15106 | 0.16937 | 0.054932 | 0.027466 | 0.018311 | -0.022888 | -0.064087 | 0.10529 | -0.050354 | -122.1954 | 0.16479 | 0.11902 | 0.16937 | -122.2092 | 0.027466 | -0.013733 | -122.2321 | 0.20142 | 0.10529 | 0.11902 | -122.2412 | 0.11444 | 0.10071 | 0.13733 | -122.3602 | 0.07782 | 0.068665 | 0.21973 | -122.3236
4375.3438 | 122.3465 | -0.10529 | 122.2687 | -0.17273 | 0.046982 | 0.060327 | 0.0072461 | 0.029969 | -0.0023904 | 0.028937 | -0.19958 | 0.026624 | 0.038805 | 0.050738 | -0.0017453 | 0.031204 | 0.073242 | 0.11444 | 0.09613 | 0.059509 | 0.068665 | 0.045776 | -0.11902 | 0.091553 | 0.1236 | 0.004578 | 0.032043 | 0.036621 | -0.032043 | -0.091553 | 0.15106 | -0.013733 | -122.2 | 0.21973 | 0.16479 | 0.17853 | -122.1954 | 0.073243 | 0.013733 | -122.2366 | 0.19684 | 0.10986 | 0.096131 | -122.2321 | 0.17395 | 0.17853 | 0.20142 | -122.3877 | 0.13733 | 0.14191 | 0.22888 | -122.3602
4377.0469 | 122.4518 | -0.054932 | 122.2641 | -0.13458 | 0.046341 | 0.059473 | 0.0072461 | 0.031465 | -0.0045266 | 0.027015 | -0.13855 | 0.025556 | 0.035387 | 0.051806 | -0.0021725 | 0.032486 | 0.10529 | 0.17853 | 0.14191 | 0.07782 | 0.059509 | 0.045776 | -0.09613 | 0.15106 | 0.18768 | 0.054932 | 0.032043 | 0.018311 | -0.013733 | -0.068665 | 0.10071 | -0.041198 | -122.2046 | 0.23346 | 0.13275 | 0.17395 | -122.1588 | 0.041199 | -0.013733 | -122.2321 | 0.20599 | 0.10986 | 0.1236 | -122.2458 | 0.11444 | 0.16022 | 0.19684 | -122.3602 | 0.086975 | 0.073243 | 0.24261 | -122.3328
4378.8125 | 122.3236 | -0.09613 | 122.2458 | -0.058289 | 0.049759 | 0.059259 | -0.0017261 | 0.028688 | 0.0033774 | 0.030433 | -0.077515 | 0.02876 | 0.035173 | 0.051592 | 0.0055179 | 0.030349 | 0.064087 | 0.041199 | -0.004578 | 0.009155 | 0.07782 | 0.027466 | -0.12817 | 0.036621 | 0.022888 | -0.091553 | 0.068665 | 0.041199 | -0.059509 | -0.10529 | 0.1236 | -0.032044 | -122.168 | 0.13733 | 0.10528 | 0.13733 | -122.1817 | 0.036621 | -0.009156 | -122.1771 | 0.13275 | 0.004577 | 0.013733 | -122.2046 | 0.17395 | 0.16022 | 0.091552 | -122.374 | 0.16479 | 0.13733 | 0.11902 | -122.3511
4380.5156 | 122.374 | -0.10071 | 122.2549 | -0.11932 | 0.049118 | 0.059045 | 0.0044691 | 0.032533 | 0.0010276 | 0.032569 | -0.13092 | 0.027478 | 0.037096 | 0.05266 | 0.0029543 | 0.032272 | 0.045776 | 0.054932 | 0.022888 | 0.027466 | 0.10986 | 0.009155 | -0.11444 | 0.091553 | 0.064087 | -0.064087 | 0.059509 | 0.032043 | -0.050354 | -0.10529 | 0.10986 | -0.013733 | -122.1451 | 0.15564 | 0.12817 | 0.14191 | -122.2092 | 0.050354 | -0.004578 | -122.1954 | 0.19226 | 0.036621 | 0.041199 | -122.2229 | 0.21057 | 0.14648 | 0.1236 | -122.3694 | 0.16022 | 0.13275 | 0.1648 | -122.3602
4382.2812 | 122.4106 | -0.054932 | 122.2412 | 0.094299 | 0.045914 | 0.060541 | -0.0012987 | 0.029115 | -0.0053812 | 0.030219 | 0.13611 | 0.027692 | 0.035814 | 0.051592 | 0.0018863 | 0.033554 | 0.068665 | 0.13733 | 0.10529 | 0.054932 | 0.064087 | 0.036621 | -0.09613 | 0.12817 | 0.11444 | 0.027466 | 0.018311 | 0.009155 | -0.032043 | -0.064087 | 0.091553 | -0.041198 | -122.1771 | 0.19226 | 0.10986 | 0.15106 | -122.1725 | 0.022889 | -0.009155 | -122.2229 | 0.18311 | 0.082398 | 0.091553 | -122.2321 | 0.11902 | 0.1236 | 0.16022 | -122.3373 | 0.073243 | 0.064087 | 0.16937 | -122.3053
4383.9844 | 122.3419 | -0.10529 | 122.2641 | 0.040894 | 0.048691 | 0.058832 | 0.0021191 | 0.02826 | 0.00017302 | 0.029792 | 0.0064086 | 0.029828 | 0.036241 | 0.053942 | 0.0016727 | 0.032486 | -0.009155 | -0.045776 | -0.041199 | -0.013733 | 0.11444 | 0.013733 | -0.13733 | 0 | -0.027466 | -0.12817 | 0.064087 | 0.045776 | -0.054932 | -0.10529 | 0.11902 | -0.032043 | -122.1497 | 0.05951 | 0.091553 | 0.1236 | -122.2733 | 0.050354 | 0 | -122.2 | 0.10529 | -0.022888 | -0.022888 | -122.2183 | 0.21973 | 0.096131 | 0.064087 | -122.4014 | 0.16937 | 0.15106 | 0.07782 | -122.3694
4385.75 | 122.406 | -0.068665 | 122.2275 | 0.14771 | 0.048264 | 0.060968 | 0.0036145 | 0.030183 | -0.0075174 | 0.03086 | 0.17426 | 0.025342 | 0.036241 | 0.053301 | 0.0016727 | 0.034195 | 0.086975 | 0.11444 | 0.1236 | 0.059509 | 0.045776 | 0.032043 | -0.091553 | 0.15106 | 0.14191 | 0.032043 | 0.018311 | 0.013733 | -0.018311 | -0.059509 | 0.10071 | -0.022888 | -122.1817 | 0.18311 | 0.12817 | 0.15106 | -122.1405 | 0.050354 | 0.009156 | -122.2092 | 0.21973 | 0.10071 | 0.091552 | -122.2137 | 0.11444 | 0.15564 | 0.19226 | -122.319 | 0.086976 | 0.082398 | 0.21057 | -122.287
4387.5469 | 122.4655 | -0.050354 | 122.2458 | 0.17822 | 0.046768 | 0.058832 | 0.00083745 | 0.028474 | -0.0021768 | 0.031287 | 0.12848 | 0.027478 | 0.033464 | 0.053728 | 0.0042361 | 0.031845 | 0.041199 | 0.032043 | 0.022888 | 0.009155 | 0.082397 | 0.018311 | -0.10071 | 0.11902 | 0.09613 | 0.013733 | 0.036621 | 0.013733 | -0.027466 | -0.07782 | 0.068665 | -0.050354 | -122.1634 | 0.082397 | 0.059509 | 0.10986 | -122.2046 | 0.022888 | -0.027466 | -122.2092 | 0.16937 | 0.064087 | 0.091553 | -122.2321 | 0.13275 | 0.091553 | 0.073242 | -122.3465 | 0.086975 | 0.064087 | 0.14648 | -122.3236
4389.25 | 122.3511 | -0.11902 | 122.2641 | -0.18036 | 0.047837 | 0.059473 | 0.0051099 | 0.029542 | -0.0055948 | 0.030433 | -0.21484 | 0.027265 | 0.036668 | 0.051165 | -0.0030271 | 0.032058 | 0.004578 | 0 | -0.013733 | -0.009155 | 0.10071 | 0.004578 | -0.14191 | 0.041199 | 0.032043 | -0.064087 | 0.07782 | 0.073242 | -0.073242 | -0.11444 | 0.1236 | -0.022888 | -122.1634 | 0.11902 | 0.10986 | 0.13275 | -122.2595 | 0.045777 | 0.004578 | -122.1863 | 0.16022 | 0.054932 | 0.050354 | -122.1909 | 0.21973 | 0.1236 | 0.10529 | -122.406 | 0.19684 | 0.19226 | 0.15106 | -122.3785
4391 | 122.374 | -0.064087 | 122.2687 | -0.14221 | 0.049118 | 0.059045 | 0.0040417 | 0.027833 | 0.00081382 | 0.031714 | -0.16144 | 0.026837 | 0.034105 | 0.053942 | 0.0027407 | 0.030563 | 0.059509 | 0.027466 | 0.013733 | 0.036621 | 0.10986 | 0.018311 | -0.12817 | 0.073242 | 0.07782 | -0.036621 | 0.054932 | 0.068665 | -0.027466 | -0.10071 | 0.082398 | -0.064087 | -122.1588 | 0.091553 | 0.10071 | 0.1648 | -122.2092 | 0.036621 | -0.036621 | -122.2137 | 0.13733 | 0.027466 | 0.064087 | -122.2 | 0.17395 | 0.1236 | 0.07782 | -122.3969 | 0.11902 | 0.13275 | 0.14191 | -122.3694
4392.7656 | 122.3785 | -0.091553 | 122.2641 | 0.079041 | 0.049332 | 0.059045 | -0.00065795 | 0.032105 | -0.001536 | 0.030433 | 0.075073 | 0.028119 | 0.036668 | 0.052019 | 0.0044497 | 0.034835 | -0.013733 | -0.036621 | -0.045776 | -0.022888 | 0.091553 | 0.009155 | -0.15106 | 0.022888 | -0.009155 | -0.10071 | 0.059509 | 0.064087 | -0.050354 | -0.10071 | 0.10071 | -0.059509 | -122.1725 | 0.054932 | 0.068665 | 0.12817 | -122.2778 | 0.041199 | -0.009155 | -122.2046 | 0.11444 | -0.009155 | 0 | -122.2 | 0.18311 | 0.07782 | 0.045777 | -122.4152 | 0.15106 | 0.15564 | 0.082398 | -122.3648
4394.4688 | 122.374 | -0.082397 | 122.2687 | -0.19562 | 0.0504 | 0.059045 | 0.0057507 | 0.029969 | -0.0036722 | 0.030219 | -0.18433 | 0.029828 | 0.039018 | 0.053728 | 0.00039091 | 0.032272 | 0 | -0.013733 | -0.018311 | 0.009155 | 0.10529 | 0.009155 | -0.14191 | 0.018311 | 0.050354 | -0.082397 | 0.059509 | 0.050354 | -0.068665 | -0.11444 | 0.091552 | -0.05951 | -122.1634 | 0.068664 | 0.091552 | 0.15106 | -122.2687 | 0.013732 | -0.032044 | -122.2092 | 0.10071 | 0 | 0.032044 | -122.2183 | 0.18768 | 0.082397 | 0.064086 | -122.4106 | 0.14191 | 0.13275 | 0.13275 | -122.3831
4396.2188 | 122.3785 | -0.068665 | 122.2687 | -0.18799 | 0.048264 | 0.059045 | 0.0063917 | 0.031251 | -0.0017496 | 0.030433 | -0.19958 | 0.029401 | 0.038377 | 0.054156 | 0.00060451 | 0.032486 | -0.004578 | -0.013733 | -0.036621 | 0.004578 | 0.10071 | 0.036621 | -0.12817 | 0.027466 | 0.059509 | -0.07782 | 0.064087 | 0.059509 | -0.054932 | -0.10071 | 0.10529 | -0.059509 | -122.168 | 0.054932 | 0.073243 | 0.13275 | -122.2733 | 0.013733 | -0.032043 | -122.2046 | 0.096131 | -0.009155 | 0.022888 | -122.2092 | 0.16937 | 0.064087 | 0.032044 | -122.3969 | 0.13275 | 0.12817 | 0.12817 | -122.3694
4397.9844 | 122.4609 | -0.054932 | 122.2366 | 0.17059 | 0.047623 | 0.057336 | -0.00044435 | 0.028688 | -0.0045266 | 0.03086 | 0.090332 | 0.027478 | 0.035814 | 0.051378 | 0.0033817 | 0.03334 | 0.050354 | 0.07782 | 0.045776 | 0.041199 | 0.068665 | 0.032043 | -0.11902 | 0.11902 | 0.1236 | 0.018311 | 0.009155 | 0.004578 | -0.027466 | -0.059509 | 0.086975 | -0.064087 | -122.168 | 0.13275 | 0.096131 | 0.16022 | -122.1863 | 0.027466 | -0.004577 | -122.2275 | 0.17395 | 0.073243 | 0.07782 | -122.2321 | 0.1236 | 0.10529 | 0.10071 | -122.3557 | 0.064087 | 0.05951 | 0.17853 | -122.2961
4399.75 | 122.4609 | -0.041199 | 122.2321 | -0.081177 | 0.044632 | 0.062891 | 0.0040417 | 0.031678 | -0.011149 | 0.02851 | -0.054626 | 0.023847 | 0.035814 | 0.051165 | -0.0013181 | 0.035904 | 0.045776 | 0.11902 | 0.09613 | 0.068665 | 0.059509 | 0.045776 | -0.10071 | 0.13275 | 0.17395 | 0.068665 | 0.013733 | 0.004578 | -0.013733 | -0.073242 | 0.086975 | -0.059509 | -122.1725 | 0.16022 | 0.10986 | 0.16937 | -122.1863 | 0.027466 | -0.032043 | -122.2183 | 0.17395 | 0.10986 | 0.14191 | -122.2275 | 0.10071 | 0.086975 | 0.13733 | -122.3328 | 0.054932 | 0.045777 | 0.21515 | -122.3053
4401.5156 | 122.4518 | -0.068665 | 122.2321 | 0.10956 | 0.046555 | 0.058191 | 0.0025465 | 0.026551 | -0.0028178 | 0.029365 | 0.18188 | 0.025769 | 0.034746 | 0.054369 | 0.0029543 | 0.032272 | 0.09613 | 0.11444 | 0.086975 | 0.068665 | 0.059509 | 0.041199 | -0.086975 | 0.15106 | 0.12817 | 0.045776 | 0.013733 | 0 | -0.027466 | -0.059509 | 0.10986 | -0.01831 | -122.1725 | 0.18311 | 0.13733 | 0.15564 | -122.1359 | 0.041199 | 0.009156 | -122.2183 | 0.21973 | 0.11444 | 0.10528 | -122.2321 | 0.12817 | 0.16479 | 0.15564 | -122.319 | 0.082398 | 0.068665 | 0.19684 | -122.2916
4403.2031 | 122.3923 | -0.086975 | 122.2641 | -0.18799 | 0.048264 | 0.061609 | 0.0061781 | 0.031251 | -0.00046778 | 0.03086 | -0.19958 | 0.027265 | 0.037736 | 0.053087 | 0.0010317 | 0.030777 | 0.027466 | 0 | -0.032043 | 0.027466 | 0.10529 | 0.027466 | -0.14191 | 0.054932 | 0.073242 | -0.050354 | 0.050354 | 0.059509 | -0.045776 | -0.11444 | 0.11444 | -0.054932 | -122.1588 | 0.086975 | 0.11444 | 0.16937 | -122.2366 | 0.041199 | -0.027466 | -122.2137 | 0.14191 | 0.036621 | 0.064087 | -122.2046 | 0.19226 | 0.11444 | 0.054932 | -122.406 | 0.13733 | 0.14648 | 0.16022 | -122.3785
4404.9688 | 122.4609 | -0.059509 | 122.2183 | 0.10956 | 0.046982 | 0.060754 | 0.00041005 | 0.030183 | -0.0019632 | 0.032142 | 0.15137 | 0.027692 | 0.036668 | 0.05501 | 0.00039091 | 0.033126 | 0.022888 | -0.009155 | 0 | 0.004578 | 0.09613 | 0.013733 | -0.11902 | 0.086975 | 0.064087 | -0.032043 | 0.027466 | 0.022888 | -0.045776 | -0.086975 | 0.073242 | -0.05951 | -122.1222 | 0.050354 | 0.064087 | 0.1236 | -122.1954 | 0.013733 | -0.027466 | -122.1909 | 0.14648 | 0.027466 | 0.054932 | -122.1954 | 0.15564 | 0.082397 | 0.059509 | -122.3373 | 0.086975 | 0.082397 | 0.1236 | -122.3053
4406.6875 | 122.4792 | -0.050354 | 122.2183 | -0.050659 | 0.045487 | 0.061182 | 0.0057507 | 0.027833 | -0.010081 | 0.028297 | -0.0012209 | 0.026837 | 0.037309 | 0.053515 | -0.0030271 | 0.031204 | 0.050354 | 0.082397 | 0.073242 | 0.045776 | 0.059509 | 0.036621 | -0.09613 | 0.13275 | 0.13275 | 0.036621 | 0.027466 | 0.027466 | -0.032043 | -0.068665 | 0.086975 | -0.045776 | -122.1588 | 0.13275 | 0.09613 | 0.14191 | -122.168 | 0.018311 | -0.018311 | -122.1909 | 0.18311 | 0.086975 | 0.10529 | -122.1909 | 0.10986 | 0.10071 | 0.1236 | -122.3145 | 0.07782 | 0.07782 | 0.18311 | -122.287
4408.4375 | 122.3511 | -0.086975 | 122.2595 | -0.20325 | 0.047837 | 0.059045 | 0.0070325 | 0.030183 | -0.0040994 | 0.028297 | -0.24536 | 0.028546 | 0.037096 | 0.053515 | -3.629e-05 | 0.031845 | 0.022888 | -0.009155 | -0.013733 | -0.009155 | 0.10529 | 0.018311 | -0.13275 | 0.022888 | 0.022888 | -0.073242 | 0.082397 | 0.064087 | -0.054932 | -0.082397 | 0.10529 | -0.045776 | -122.1542 | 0.07782 | 0.07782 | 0.1236 | -122.2366 | 0.032043 | 0.004578 | -122.1771 | 0.10986 | 0.013733 | 0.009155 | -122.1954 | 0.19226 | 0.10986 | 0.073242 | -122.3923 | 0.16937 | 0.15106 | 0.10986 | -122.3419
4410.1406 | 122.3465 | -0.10529 | 122.2412 | 0.040894 | 0.049332 | 0.058405 | -0.0015125 | 0.027619 | -0.0017496 | 0.031074 | 0.021668 | 0.029401 | 0.036668 | 0.053728 | 0.0050907 | 0.034622 | 0 | -0.054932 | -0.064087 | -0.022888 | 0.10071 | 0.009155 | -0.13733 | 0.032043 | -0.027466 | -0.11902 | 0.068665 | 0.054932 | -0.068665 | -0.10529 | 0.11444 | -0.032043 | -122.1405 | 0.050354 | 0.082398 | 0.11444 | -122.2412 | 0.036621 | 0 | -122.1725 | 0.13733 | -0.013733 | -0.013733 | -122.1863 | 0.20599 | 0.10529 | 0.041199 | -122.3785 | 0.17395 | 0.16022 | 0.07782 | -122.3465
4411.9062 | 122.3602 | -0.064087 | 122.2733 | -0.20325 | 0.047623 | 0.058405 | 0.0048963 | 0.027619 | -0.00944 | 0.028083 | -0.13092 | 0.025128 | 0.036882 | 0.051165 | -0.0021725 | 0.03569 | 0.082397 | 0.13733 | 0.13733 | 0.091553 | 0.082397 | 0.054932 | -0.082397 | 0.13275 | 0.1831 | 0.041199 | 0.022888 | 0.032043 | -0.018311 | -0.050354 | 0.11902 | -0.01831 | -122.1909 | 0.20142 | 0.15564 | 0.17395 | -122.1909 | 0.045776 | 0.013733 | -122.2504 | 0.19684 | 0.10529 | 0.091553 | -122.2412 | 0.14648 | 0.14648 | 0.20142 | -122.3557 | 0.086975 | 0.09613 | 0.24719 | -122.3236
4413.6562 | 122.3557 | -0.073242 | 122.2733 | -0.12695 | 0.051895 | 0.0599 | 0.0040417 | 0.031251 | -0.00025418 | 0.029792 | -0.16907 | 0.02876 | 0.035814 | 0.055651 | 0.0012455 | 0.030563 | 0.086975 | 0.059509 | 0.027466 | 0.036621 | 0.11902 | 0.027466 | -0.11444 | 0.09613 | 0.086975 | -0.036621 | 0.050354 | 0.054932 | -0.041199 | -0.10071 | 0.10071 | -0.041199 | -122.1542 | 0.13275 | 0.10986 | 0.15106 | -122.1863 | 0.032043 | -0.027466 | -122.2229 | 0.16937 | 0.036621 | 0.064087 | -122.2183 | 0.19226 | 0.16022 | 0.10071 | -122.3877 | 0.1236 | 0.12817 | 0.16022 | -122.374
4415.3594 | 122.3282 | -0.073242 | 122.3236 | -0.22614 | 0.049332 | 0.061395 | 0.0059643 | 0.030397 | -0.0064492 | 0.030219 | -0.23773 | 0.024274 | 0.039873 | 0.053942 | -0.0021725 | 0.033981 | 0.018311 | 0.009155 | 0.004578 | 0 | 0.11444 | 0.013733 | -0.12817 | 0.036621 | 0.054932 | -0.064087 | 0.086975 | 0.073242 | -0.045776 | -0.09613 | 0.086975 | -0.054932 | -122.2092 | 0.082397 | 0.073242 | 0.12817 | -122.3053 | 0.027466 | -0.022888 | -122.2366 | 0.10986 | 0.009155 | 0.032043 | -122.2504 | 0.18768 | 0.091553 | 0.07782 | -122.4518 | 0.16022 | 0.14648 | 0.12817 | -122.4197
4417.125 | 122.4701 | -0.07782 | 122.2137 | 0.094299 | 0.048264 | 0.058618 | -0.0010851 | 0.028901 | -0.00046778 | 0.032569 | 0.12848 | 0.026837 | 0.036241 | 0.054583 | 0.0023135 | 0.032699 | 0.013733 | -0.018311 | -0.036621 | 0 | 0.073242 | -0.018311 | -0.15564 | 0.07782 | 0.027466 | -0.054932 | 0.013733 | 0.009155 | -0.045776 | -0.12817 | 0.059509 | -0.07782 | -122.1405 | 0.059509 | 0.07782 | 0.15564 | -122.2 | 0.032044 | -0.050354 | -122.2 | 0.15564 | 0.022888 | 0.073242 | -122.2046 | 0.15106 | 0.091553 | 0.041199 | -122.3694 | 0.091553 | 0.086975 | 0.10529 | -122.3419
4418.8906 | 122.3145 | -0.11444 | 122.2778 | -0.073547 | 0.050614 | 0.056909 | 0.0016919 | 0.028688 | -0.00068138 | 0.032569 | -0.046997 | 0.029401 | 0.035814 | 0.055651 | 0.0018863 | 0.032913 | 0.068665 | 0.045776 | -0.004578 | 0.004578 | 0.091553 | 0.018311 | -0.1236 | 0.050354 | 0.041199 | -0.082397 | 0.045776 | 0.064087 | -0.054932 | -0.10071 | 0.13275 | -0.009155 | -122.1863 | 0.16022 | 0.11902 | 0.12817 | -122.2092 | 0.059509 | 0.013733 | -122.2321 | 0.16479 | 0.032044 | 0.018311 | -122.2137 | 0.20599 | 0.18311 | 0.10986 | -122.4014 | 0.16022 | 0.17853 | 0.15564 | -122.3785
4420.5938 | 122.4655 | -0.027466 | 122.2778 | -0.12695 | 0.046982 | 0.058832 | 0.0059643 | 0.028901 | -0.0079446 | 0.030219 | -0.10803 | 0.025342 | 0.036027 | 0.053515 | -0.0038815 | 0.034195 | 0.091553 | 0.16479 | 0.12817 | 0.091553 | 0.068665 | 0.045776 | -0.10071 | 0.15106 | 0.19684 | 0.086975 | 0.050354 | 0.009155 | -0.013733 | -0.064087 | 0.073242 | -0.073242 | -122.2092 | 0.19226 | 0.11902 | 0.19226 | -122.1863 | 0.013733 | -0.036621 | -122.2275 | 0.17853 | 0.11444 | 0.15106 | -122.2687 | 0.096131 | 0.11902 | 0.15564 | -122.3785 | 0.07782 | 0.036621 | 0.2243 | -122.3419
4422.375 | 122.406 | -0.09613 | 122.2183 | 0.10956 | 0.047409 | 0.057764 | -0.00087155 | 0.029115 | 0.00017302 | 0.031501 | 0.067444 | 0.028119 | 0.035814 | 0.053087 | 0.0029543 | 0.034408 | -0.009155 | -0.050354 | -0.064087 | -0.018311 | 0.10529 | -0.009155 | -0.14191 | 0.027466 | -0.009155 | -0.10071 | 0.045776 | 0.045776 | -0.064087 | -0.10986 | 0.086975 | -0.045777 | -122.113 | 0.045776 | 0.077819 | 0.1236 | -122.2275 | 0.032043 | -0.013733 | -122.1725 | 0.1236 | -0.004578 | 0.009155 | -122.1725 | 0.20142 | 0.086975 | 0.032043 | -122.3602 | 0.14191 | 0.14191 | 0.086975 | -122.3282
4424.1562 | 122.4243 | -0.059509 | 122.2778 | -0.17273 | 0.045273 | 0.060968 | 0.0031873 | 0.028901 | -0.0075174 | 0.030646 | -0.11566 | 0.025983 | 0.034532 | 0.05266 | -0.0015317 | 0.035476 | 0.086975 | 0.14648 | 0.13275 | 0.09613 | 0.059509 | 0.059509 | -0.10986 | 0.13275 | 0.19226 | 0.054932 | 0.013733 | 0.032043 | -0.022888 | -0.059509 | 0.11902 | -0.050354 | -122.2183 | 0.20599 | 0.15564 | 0.20599 | -122.1909 | 0.036621 | 0 | -122.2641 | 0.19226 | 0.11444 | 0.11444 | -122.2458 | 0.11902 | 0.14648 | 0.19226 | -122.3877 | 0.073242 | 0.091552 | 0.25177 | -122.3373
4425.8438 | 122.4564 | -0.054932 | 122.2321 | 0.056152 | 0.049973 | 0.059045 | 0.00019645 | 0.029328 | -0.00068138 | 0.030433 | 0.12085 | 0.027265 | 0.037736 | 0.053942 | 0.0027407 | 0.032699 | 0.013733 | -0.018311 | -0.045776 | -0.013733 | 0.07782 | -0.004578 | -0.13275 | 0.054932 | 0.013733 | -0.086975 | 0.036621 | 0.036621 | -0.064087 | -0.09613 | 0.050354 | -0.077819 | -122.1542 | 0.036621 | 0.041199 | 0.11902 | -122.2183 | -0.009155 | -0.041198 | -122.1954 | 0.10986 | -0.032043 | 0.009155 | -122.1954 | 0.13275 | 0.068665 | 0.009156 | -122.3648 | 0.091553 | 0.091553 | 0.068665 | -122.3282
4427.6094 | 122.3282 | -0.10071 | 122.2412 | 0.048523 | 0.049546 | 0.060541 | 0.0019055 | 0.030824 | -0.00025418 | 0.028297 | -0.0088499 | 0.028974 | 0.036241 | 0.05266 | 0.0035953 | 0.033554 | 0.018311 | -0.041199 | -0.041199 | -0.018311 | 0.09613 | 0.013733 | -0.12817 | 0.013733 | -0.022888 | -0.11902 | 0.068665 | 0.059509 | -0.041199 | -0.1236 | 0.11444 | -0.027466 | -122.1451 | 0.059509 | 0.082397 | 0.10986 | -122.2229 | 0.059509 | -0.022888 | -122.1725 | 0.11444 | -0.018311 | 0.004577 | -122.1817 | 0.19684 | 0.11902 | 0.059509 | -122.3694 | 0.16937 | 0.16022 | 0.07782 | -122.3648
4429.3125 | 122.4838 | -0.064087 | 122.2595 | -0.073547 | 0.046128 | 0.059259 | 0.0048963 | 0.027619 | -0.0090128 | 0.02851 | -0.039368 | 0.025983 | 0.040727 | 0.052447 | -0.0055905 | 0.035263 | 0.054932 | 0.07782 | 0.09613 | 0.059509 | 0.064087 | 0.050354 | -0.10986 | 0.13275 | 0.14648 | 0.054932 | 0.027466 | 0.013733 | -0.018311 | -0.09613 | 0.11444 | -0.045776 | -122.1954 | 0.14191 | 0.1236 | 0.16937 | -122.2046 | 0.045776 | -0.032043 | -122.2321 | 0.19684 | 0.11902 | 0.15106 | -122.2458 | 0.12817 | 0.11902 | 0.16022 | -122.3694 | 0.091553 | 0.07782 | 0.21057 | -122.3557
4431.0781 | 122.3694 | -0.091553 | 122.2321 | 0.056152 | 0.050186 | 0.061395 | -0.0012987 | 0.029756 | -0.0017496 | 0.027869 | 0.082703 | 0.028333 | 0.036455 | 0.054583 | 0.0035953 | 0.033981 | 0.013733 | -0.050354 | -0.045776 | -0.013733 | 0.086975 | 0.009155 | -0.13733 | 0.018311 | -0.027466 | -0.10071 | 0.07782 | 0.045776 | -0.054932 | -0.10986 | 0.10071 | -0.045776 | -122.1451 | 0.041199 | 0.07782 | 0.1236 | -122.2183 | 0.036621 | -0.01831 | -122.1542 | 0.10986 | -0.009155 | 0.009155 | -122.1863 | 0.17853 | 0.10529 | 0.045777 | -122.3694 | 0.16937 | 0.13733 | 0.064087 | -122.3419
4432.7812 | 122.3236 | -0.10071 | 122.2549 | -0.020142 | 0.049118 | 0.057764 | 0.00083745 | 0.028688 | -0.00046778 | 0.031714 | -0.0012209 | 0.029615 | 0.037309 | 0.054156 | 0.0038089 | 0.033767 | 0.036621 | -0.009155 | -0.022888 | -0.009155 | 0.091553 | -0.009155 | -0.1236 | 0.013733 | 0.009155 | -0.11902 | 0.07782 | 0.050354 | -0.068665 | -0.11902 | 0.091553 | -0.022888 | -122.1634 | 0.091553 | 0.091553 | 0.11444 | -122.2183 | 0.032043 | -0.018311 | -122.1771 | 0.11444 | -0.018311 | 0 | -122.2046 | 0.19226 | 0.13733 | 0.07782 | -122.3785 | 0.17853 | 0.15106 | 0.10986 | -122.374
4434.5312 | 122.4335 | -0.050354 | 122.2321 | 0.010376 | 0.04506 | 0.059259 | 0.0021191 | 0.031465 | -0.0096536 | 0.027442 | 0.067444 | 0.02406 | 0.034746 | 0.053301 | -0.0034543 | 0.036117 | 0.013733 | 0.054932 | 0.041199 | 0.027466 | 0.07782 | 0.041199 | -0.09613 | 0.064087 | 0.07782 | 0.004578 | 0.027466 | 0.036621 | -0.036621 | -0.07782 | 0.091553 | -0.045776 | -122.1542 | 0.10529 | 0.07782 | 0.1236 | -122.2183 | 0.013733 | -0.027466 | -122.2046 | 0.11444 | 0.054932 | 0.082398 | -122.1954 | 0.12817 | 0.064087 | 0.091553 | -122.3282 | 0.07782 | 0.086975 | 0.12817 | -122.3099
4436.2969 | 122.4335 | -0.073242 | 122.2137 | -0.0048827 | 0.046982 | 0.062036 | 0.0044691 | 0.02591 | -0.0085856 | 0.030006 | 0.052185 | 0.023419 | 0.038377 | 0.051806 | -0.0023861 | 0.036544 | 0.013733 | 0.064087 | 0.068665 | 0.041199 | 0.064087 | 0.045776 | -0.10529 | 0.068665 | 0.07782 | -0.009155 | 0.013733 | 0.022888 | -0.027466 | -0.07782 | 0.11902 | -0.032044 | -122.1497 | 0.13733 | 0.11444 | 0.14649 | -122.2 | 0.045776 | -0.004578 | -122.2 | 0.14191 | 0.064087 | 0.068665 | -122.1909 | 0.13733 | 0.086975 | 0.14191 | -122.319 | 0.086975 | 0.09613 | 0.15106 | -122.2916
4438.0625 | 122.4243 | -0.091553 | 122.2321 | 0.10956 | 0.048264 | 0.060114 | 0.00083745 | 0.031251 | -0.00068138 | 0.030646 | 0.029297 | 0.028546 | 0.037309 | 0.056078 | 0.0025271 | 0.033767 | 0.022888 | -0.036621 | -0.041199 | -0.009155 | 0.1236 | 0.009155 | -0.13275 | 0.054932 | -0.009155 | -0.10529 | 0.059509 | 0.036621 | -0.045776 | -0.11902 | 0.10071 | -0.041198 | -122.1085 | 0.054932 | 0.082398 | 0.1236 | -122.2092 | 0.045777 | -0.027466 | -122.1725 | 0.14649 | -0.013733 | 0.013733 | -122.1954 | 0.21515 | 0.11444 | 0.050354 | -122.3648 | 0.15106 | 0.12817 | 0.082398 | -122.3511
4439.8125 | 122.4335 | -0.068665 | 122.2183 | 0.10193 | 0.046341 | 0.059686 | 0.00041005 | 0.031678 | -0.002604 | 0.029578 | 0.13611 | 0.02641 | 0.0356 | 0.053942 | 0.0018863 | 0.035263 | 0.018311 | 0.004578 | -0.004578 | 0 | 0.086975 | 0.022888 | -0.12817 | 0.09613 | 0.050354 | -0.022888 | 0.050354 | 0.036621 | -0.036621 | -0.082397 | 0.091553 | -0.059509 | -122.1313 | 0.073243 | 0.068665 | 0.12817 | -122.2 | 0.032044 | -0.013732 | -122.168 | 0.16479 | 0.045777 | 0.059509 | -122.1817 | 0.15564 | 0.086976 | 0.064087 | -122.3465 | 0.11902 | 0.10529 | 0.11902 | -122.3007
4441.5156 | 122.4289 | -0.07782 | 122.2458 | 0.08667 | 0.044205 | 0.060968 | 0.0019055 | 0.029328 | -0.007731 | 0.030646 | 0.17426 | 0.025769 | 0.037096 | 0.051806 | 0.00039091 | 0.036117 | 0.064087 | 0.11444 | 0.086975 | 0.059509 | 0.041199 | 0.050354 | -0.091553 | 0.11902 | 0.10071 | 0.022888 | 0.032043 | 0.013733 | -0.013733 | -0.073242 | 0.12817 | -0.013733 | -122.2046 | 0.19226 | 0.13733 | 0.15106 | -122.1817 | 0.064087 | 0.004578 | -122.2137 | 0.19684 | 0.10071 | 0.09613 | -122.2321 | 0.11902 | 0.14191 | 0.16479 | -122.3373 | 0.10986 | 0.091553 | 0.17853 | -122.319
4443.2812 | 122.4197 | -0.054932 | 122.2733 | -0.18036 | 0.047623 | 0.0599 | 0.0074597 | 0.031678 | -0.0068766 | 0.029578 | -0.14618 | 0.024274 | 0.037736 | 0.053087 | -0.0023861 | 0.034835 | 0.10529 | 0.13733 | 0.12817 | 0.068665 | 0.073242 | 0.041199 | -0.11902 | 0.14191 | 0.1831 | 0.045776 | 0.027466 | 0.018311 | -0.013733 | -0.082397 | 0.096131 | -0.064087 | -122.2 | 0.19226 | 0.1236 | 0.18768 | -122.168 | 0.041199 | -0.027465 | -122.2458 | 0.19684 | 0.10071 | 0.12817 | -122.2549 | 0.12817 | 0.16022 | 0.18311 | -122.3923 | 0.082398 | 0.073243 | 0.23804 | -122.3557
4444.9844 | 122.4838 | -0.041199 | 122.2275 | -0.0048827 | 0.045273 | 0.060968 | 0.0023329 | 0.029756 | -0.0079446 | 0.028083 | -0.0088499 | 0.023847 | 0.036027 | 0.054796 | -0.0025999 | 0.034835 | 0.032043 | 0.068665 | 0.064087 | 0.027466 | 0.068665 | 0.041199 | -0.10529 | 0.09613 | 0.10986 | 0.009155 | 0.041199 | 0.022888 | -0.041199 | -0.091553 | 0.082398 | -0.064087 | -122.1588 | 0.10986 | 0.068665 | 0.13275 | -122.1954 | 0 | -0.050354 | -122.1863 | 0.13733 | 0.050354 | 0.10071 | -122.2046 | 0.10986 | 0.073242 | 0.10529 | -122.3328 | 0.082398 | 0.064087 | 0.15106 | -122.319
4446.75 | 122.4609 | -0.054932 | 122.1954 | 0.15533 | 0.046341 | 0.057977 | 0.0019055 | 0.02826 | 0.00017302 | 0.027015 | 0.11322 | 0.026837 | 0.034318 | 0.055865 | 0.0042361 | 0.033554 | 0.068665 | 0.018311 | 0.018311 | 0.004578 | 0.086975 | 0.041199 | -0.10529 | 0.11444 | 0.068665 | -0.013733 | 0.032043 | 0.013733 | -0.027466 | -0.073242 | 0.096131 | -0.050354 | -122.1085 | 0.073243 | 0.05951 | 0.10986 | -122.1268 | 0.027466 | -0.01831 | -122.1634 | 0.16937 | 0.041199 | 0.059509 | -122.1817 | 0.14191 | 0.1236 | 0.073243 | -122.3007 | 0.086975 | 0.068665 | 0.1236 | -122.2687
4448.4531 | 122.4014 | -0.07782 | 122.2549 | 0.094299 | 0.043351 | 0.060968 | 0.0027601 | 0.027192 | -0.0062356 | 0.027228 | 0.090332 | 0.025769 | 0.035173 | 0.053515 | 0.0014591 | 0.036117 | 0.068665 | 0.10529 | 0.086975 | 0.041199 | 0.059509 | 0.041199 | -0.082397 | 0.10986 | 0.09613 | -0.013733 | 0.027466 | 0.022888 | -0.018311 | -0.086975 | 0.11902 | -0.004577 | -122.1954 | 0.18311 | 0.11902 | 0.1236 | -122.1863 | 0.059509 | -0.009155 | -122.2275 | 0.18768 | 0.064087 | 0.073242 | -122.2321 | 0.13733 | 0.14649 | 0.16479 | -122.3373 | 0.10529 | 0.10071 | 0.17395 | -122.3419
4450.2031 | 122.3602 | -0.082397 | 122.2595 | -0.23376 | 0.049759 | 0.061182 | 0.0061781 | 0.028688 | -0.003245 | 0.029578 | -0.26825 | 0.027265 | 0.039873 | 0.054583 | -0.00067729 | 0.035263 | 0.004578 | -0.004578 | -0.018311 | -0.013733 | 0.11444 | -0.004578 | -0.16022 | 0.018311 | 0.018311 | -0.10071 | 0.073242 | 0.050354 | -0.050354 | -0.10986 | 0.077819 | -0.07782 | -122.1451 | 0.077819 | 0.068664 | 0.14648 | -122.2549 | 0.032043 | -0.027466 | -122.1863 | 0.10071 | -0.018311 | 0.009155 | -122.2092 | 0.19684 | 0.086975 | 0.064086 | -122.4197 | 0.15564 | 0.13275 | 0.10071 | -122.3694
4451.9844 | 122.3648 | -0.07782 | 122.2595 | -0.11169 | 0.047409 | 0.061182 | 0.0023329 | 0.029969 | -4.058e-05 | 0.031501 | -0.15381 | 0.027906 | 0.035814 | 0.05501 | 0.0042361 | 0.034622 | 0.064087 | 0.050354 | 0.018311 | 0.022888 | 0.082397 | 0.022888 | -0.13733 | 0.10071 | 0.073242 | -0.068665 | 0.050354 | 0.041199 | -0.059509 | -0.10986 | 0.10071 | -0.059509 | -122.1771 | 0.12817 | 0.10071 | 0.16022 | -122.1954 | 0.018311 | -0.032043 | -122.2092 | 0.17853 | 0.009155 | 0.041198 | -122.2183 | 0.16022 | 0.14191 | 0.096131 | -122.3969 | 0.12817 | 0.11902 | 0.15106 | -122.3694
4453.7031 | 122.3511 | -0.073242 | 122.2504 | 0.079041 | 0.049973 | 0.059045 | 0.0036145 | 0.028901 | 0.00017302 | 0.031501 | 0.067444 | 0.027906 | 0.037309 | 0.055651 | 0.0016727 | 0.035049 | 0.004578 | -0.041199 | -0.041199 | -0.009155 | 0.11444 | 0 | -0.14648 | 0.036621 | -0.018311 | -0.10986 | 0.064087 | 0.050354 | -0.059509 | -0.11444 | 0.073242 | -0.073242 | -122.1359 | 0.032043 | 0.064087 | 0.13733 | -122.2458 | 0.013733 | -0.041199 | -122.1863 | 0.10986 | -0.036621 | 0.004578 | -122.2 | 0.18768 | 0.07782 | 0.032043 | -122.3969 | 0.13733 | 0.1236 | 0.054931 | -122.3648
4455.4688 | 122.4106 | -0.064087 | 122.2275 | 0.063782 | 0.044846 | 0.06225 | 0.0023329 | 0.029969 | -0.010508 | 0.030219 | 0.097962 | 0.02406 | 0.0356 | 0.054583 | -0.0021725 | 0.03569 | 0.036621 | 0.07782 | 0.064087 | 0.027466 | 0.059509 | 0.054932 | -0.09613 | 0.11444 | 0.09613 | 0.004578 | 0.027466 | 0.018311 | -0.032043 | -0.073242 | 0.11902 | -0.032043 | -122.168 | 0.14191 | 0.091553 | 0.1236 | -122.1909 | 0.032044 | -0.009155 | -122.2 | 0.17853 | 0.068665 | 0.07782 | -122.2092 | 0.1236 | 0.10071 | 0.12817 | -122.3236 | 0.091553 | 0.082398 | 0.16022 | -122.3007
4457.1719 | 122.3648 | -0.07782 | 122.2412 | -0.13458 | 0.046341 | 0.059473 | 0.0027601 | 0.031465 | -0.00046778 | 0.031501 | -0.16144 | 0.026197 | 0.035814 | 0.056719 | 0.0018863 | 0.034195 | 0.054932 | 0.050354 | 0 | 0.036621 | 0.10071 | 0.009155 | -0.15106 | 0.073242 | 0.082397 | -0.045776 | 0.050354 | 0.027466 | -0.041199 | -0.10986 | 0.086975 | -0.073242 | -122.1405 | 0.12817 | 0.11444 | 0.18768 | -122.1863 | 0.036621 | -0.032043 | -122.1909 | 0.15106 | 0.032044 | 0.064087 | -122.2137 | 0.17853 | 0.13275 | 0.07782 | -122.3923 | 0.12817 | 0.10529 | 0.16022 | -122.3511
4458.9375 | 122.3282 | -0.10986 | 122.2595 | -0.25665 | 0.047623 | 0.060968 | 0.0072461 | 0.030183 | -0.0051676 | 0.029578 | -0.21484 | 0.025128 | 0.037309 | 0.054796 | -0.0025999 | 0.034195 | -0.013733 | 0.018311 | 0.004578 | -0.004578 | 0.082397 | 0.013733 | -0.11902 | 0.036621 | 0.050354 | -0.082397 | 0.068665 | 0.059509 | -0.068665 | -0.10529 | 0.1236 | -0.009156 | -122.1771 | 0.12817 | 0.10529 | 0.11444 | -122.2733 | 0.041198 | 0.004577 | -122.1909 | 0.14648 | 0.027466 | 0.022889 | -122.2 | 0.19226 | 0.09613 | 0.11444 | -122.3785 | 0.17853 | 0.16937 | 0.16022 | -122.3648
4460.7031 | 122.3602 | -0.059509 | 122.2687 | -0.1651 | 0.04805 | 0.059045 | 0.0029737 | 0.029542 | -0.00025418 | 0.030006 | -0.2301 | 0.02406 | 0.036241 | 0.055865 | 0.0029543 | 0.034622 | -0.009155 | 0.009155 | -0.018311 | 0.009155 | 0.10529 | -0.004578 | -0.14191 | 0.041199 | 0.059509 | -0.054932 | 0.054932 | 0.041199 | -0.064087 | -0.10986 | 0.054931 | -0.082398 | -122.1634 | 0.068664 | 0.068664 | 0.15106 | -122.2778 | -0.004578 | -0.050354 | -122.2137 | 0.10071 | 0.004577 | 0.054931 | -122.2275 | 0.16479 | 0.050354 | 0.041198 | -122.4106 | 0.11444 | 0.10071 | 0.11902 | -122.3785
4462.4062 | 122.3511 | -0.091553 | 122.2549 | -0.23376 | 0.047409 | 0.062036 | 0.0036145 | 0.028474 | -0.0038858 | 0.02851 | -0.22247 | 0.025769 | 0.035387 | 0.056719 | 0.00017731 | 0.036758 | -0.032043 | 0.009155 | -0.013733 | -0.004578 | 0.10529 | -0.009155 | -0.14648 | 0.009155 | 0.032043 | -0.086975 | 0.082397 | 0.054932 | -0.073242 | -0.11444 | 0.082398 | -0.054931 | -122.1497 | 0.10071 | 0.086975 | 0.14191 | -122.287 | 0.018311 | -0.022888 | -122.1725 | 0.10071 | 0.004578 | 0.027466 | -122.2 | 0.19684 | 0.05951 | 0.07782 | -122.4014 | 0.17395 | 0.14649 | 0.1236 | -122.3694
4464.1719 | 122.319 | -0.10529 | 122.2641 | -0.19562 | 0.0457 | 0.060327 | 0.0044691 | 0.031251 | -0.0062356 | 0.029578 | -0.16907 | 0.025556 | 0.036455 | 0.053728 | -0.00089089 | 0.036972 | 0.054932 | 0.12817 | 0.09613 | 0.054932 | 0.059509 | 0.050354 | -0.091553 | 0.09613 | 0.15106 | 0 | 0.054932 | 0.022888 | -0.045776 | -0.091553 | 0.15564 | 0.013733 | -122.2046 | 0.23346 | 0.16022 | 0.14649 | -122.2092 | 0.05951 | 0.013733 | -122.2092 | 0.20142 | 0.10529 | 0.091553 | -122.2412 | 0.16479 | 0.16022 | 0.20142 | -122.3557 | 0.16022 | 0.12817 | 0.25635 | -122.3557
4465.8906 | 122.438 | -0.09613 | 122.2137 | 0.063782 | 0.049759 | 0.059686 | 0.00019645 | 0.031678 | -0.00046778 | 0.029792 | 0.067444 | 0.02876 | 0.036241 | 0.057146 | 0.0023135 | 0.035049 | 0.004578 | -0.013733 | -0.022888 | -0.018311 | 0.10071 | 0.018311 | -0.14191 | 0.045776 | 0.018311 | -0.068665 | 0.050354 | 0.036621 | -0.036621 | -0.10529 | 0.11444 | -0.045777 | -122.113 | 0.082397 | 0.077819 | 0.1236 | -122.2092 | 0.059509 | -0.009156 | -122.1634 | 0.14191 | 0.027465 | 0.036621 | -122.1771 | 0.19684 | 0.10071 | 0.073242 | -122.3557 | 0.14648 | 0.13275 | 0.11444 | -122.319
4467.6562 | 122.374 | -0.086975 | 122.2412 | -0.19562 | 0.049332 | 0.060327 | 0.0040417 | 0.031037 | -4.058e-05 | 0.030433 | -0.16144 | 0.027906 | 0.036882 | 0.056719 | 0.0010317 | 0.036758 | 0.013733 | 0.018311 | -0.009155 | 0.022888 | 0.091553 | 0.004578 | -0.13733 | 0.059509 | 0.082397 | -0.054932 | 0.059509 | 0.045776 | -0.036621 | -0.10071 | 0.091553 | -0.050354 | -122.1497 | 0.10529 | 0.10986 | 0.16022 | -122.2275 | 0.050354 | -0.013733 | -122.1817 | 0.14648 | 0.032043 | 0.045776 | -122.1954 | 0.17853 | 0.10071 | 0.07782 | -122.3785 | 0.14648 | 0.13275 | 0.16937 | -122.3419
4469.4219 | 122.3236 | -0.082397 | 122.2549 | -0.10406 | 0.049546 | 0.060541 | -0.0017261 | 0.03061 | -0.0013224 | 0.031287 | -0.11566 | 0.028119 | 0.034746 | 0.056505 | 0.0029543 | 0.036758 | 0.050354 | 0.054932 | 0.018311 | 0.032043 | 0.091553 | 0.013733 | -0.14191 | 0.082397 | 0.10071 | -0.068665 | 0.041199 | 0.032043 | -0.059509 | -0.11444 | 0.09613 | -0.05951 | -122.1634 | 0.13733 | 0.11444 | 0.17395 | -122.2046 | 0.022888 | -0.032044 | -122.2137 | 0.16479 | 0.013732 | 0.045776 | -122.2229 | 0.17395 | 0.13275 | 0.10071 | -122.3969 | 0.1236 | 0.11444 | 0.18311 | -122.3694
4471.1875 | 122.3557 | -0.091553 | 122.2687 | -0.20325 | 0.047623 | 0.060968 | 0.0048963 | 0.029328 | -0.007731 | 0.03086 | -0.1004 | 0.025983 | 0.035173 | 0.056505 | -0.0045225 | 0.038467 | 0.064087 | 0.1236 | 0.10986 | 0.07782 | 0.054932 | 0.041199 | -0.1236 | 0.11444 | 0.18768 | 0.032043 | 0.018311 | 0.013733 | -0.013733 | -0.086975 | 0.13275 | -0.032043 | -122.2137 | 0.21515 | 0.16937 | 0.20142 | -122.2046 | 0.07782 | 0.004578 | -122.2504 | 0.20599 | 0.1236 | 0.11902 | -122.2549 | 0.14649 | 0.15564 | 0.20142 | -122.3923 | 0.10986 | 0.10529 | 0.27924 | -122.3557
4472.8906 | 122.3557 | -0.086975 | 122.2458 | -0.21088 | 0.049546 | 0.058191 | 0.0040417 | 0.028688 | -0.0019632 | 0.02851 | -0.16144 | 0.027906 | 0.036027 | 0.056292 | 0.00060451 | 0.034408 | 0 | 0.018311 | -0.004578 | 0.022888 | 0.10529 | 0.009155 | -0.13733 | 0.041199 | 0.073242 | -0.054932 | 0.07782 | 0.059509 | -0.059509 | -0.11444 | 0.09613 | -0.050354 | -122.1405 | 0.10529 | 0.10986 | 0.16022 | -122.2458 | 0.027466 | -0.027466 | -122.168 | 0.12817 | 0.032043 | 0.059509 | -122.1863 | 0.19226 | 0.086975 | 0.082397 | -122.3831 | 0.16479 | 0.14648 | 0.16022 | -122.3602
4474.6562 | 122.3419 | -0.082397 | 122.2366 | 0.063782 | 0.048264 | 0.060968 | 0.0021191 | 0.033601 | -0.00068138 | 0.030433 | -0.0012209 | 0.028974 | 0.034105 | 0.056719 | 0.0038089 | 0.036544 | -0.013733 | -0.050354 | -0.036621 | -0.022888 | 0.10529 | 0.004578 | -0.15106 | -0.004578 | -0.018311 | -0.14191 | 0.064087 | 0.064087 | -0.059509 | -0.1236 | 0.086975 | -0.068665 | -122.1313 | 0.032043 | 0.059509 | 0.12817 | -122.2504 | 0.022888 | -0.041199 | -122.1725 | 0.077819 | -0.05951 | -0.018311 | -122.1725 | 0.18768 | 0.068664 | 0.045776 | -122.3877 | 0.14648 | 0.14648 | 0.064086 | -122.3602
4476.4219 | 122.4701 | -0.064087 | 122.2321 | -0.073547 | 0.044419 | 0.062036 | 0.0012647 | 0.029328 | -0.0096536 | 0.030006 | -0.092773 | 0.025342 | 0.036455 | 0.058001 | -0.0040951 | 0.039749 | 0.036621 | 0.10529 | 0.082397 | 0.07782 | 0.07782 | 0.032043 | -0.10986 | 0.12817 | 0.16937 | 0.059509 | 0.018311 | 0.018311 | -0.032043 | -0.091553 | 0.09613 | -0.045776 | -122.1542 | 0.16937 | 0.14191 | 0.18768 | -122.1954 | 0.032044 | -0.027466 | -122.2137 | 0.19226 | 0.1236 | 0.15106 | -122.2137 | 0.14191 | 0.10071 | 0.14648 | -122.3419 | 0.082398 | 0.082398 | 0.23346 | -122.3236
4478.125 | 122.4197 | -0.073242 | 122.2412 | 0.040894 | 0.042923 | 0.060754 | 0.0042555 | 0.027619 | -0.0079446 | 0.029578 | 0.082703 | 0.027051 | 0.037523 | 0.056933 | -0.0019589 | 0.039108 | 0.041199 | 0.045776 | 0.059509 | 0.018311 | 0.059509 | 0.041199 | -0.11902 | 0.082397 | 0.082397 | -0.009155 | 0.032043 | 0.032043 | -0.032043 | -0.07782 | 0.11444 | -0.045777 | -122.1817 | 0.11902 | 0.091553 | 0.13733 | -122.2 | 0.041199 | -0.004578 | -122.2092 | 0.15564 | 0.064087 | 0.068665 | -122.2092 | 0.13275 | 0.11444 | 0.13275 | -122.3602 | 0.10529 | 0.10529 | 0.15564 | -122.319
4479.8906 | 122.4014 | -0.068665 | 122.2366 | -0.21088 | 0.045914 | 0.060541 | 0.0025465 | 0.02826 | -0.0073038 | 0.029578 | -0.14618 | 0.025342 | 0.037096 | 0.05501 | -0.0011045 | 0.037185 | 0.086975 | 0.14191 | 0.10986 | 0.07782 | 0.041199 | 0.032043 | -0.086975 | 0.1236 | 0.16937 | 0.036621 | 0.018311 | 0.009155 | -0.041199 | -0.091553 | 0.10071 | -0.01831 | -122.1954 | 0.21057 | 0.14649 | 0.16479 | -122.1497 | 0.027466 | -0.022888 | -122.2183 | 0.19226 | 0.10529 | 0.12817 | -122.2275 | 0.10986 | 0.15564 | 0.17853 | -122.3236 | 0.086976 | 0.07782 | 0.23804 | -122.3282
4481.5938 | 122.3969 | -0.050354 | 122.2321 | 0.10193 | 0.047837 | 0.059259 | -0.00065795 | 0.027192 | -0.003245 | 0.027869 | 0.12085 | 0.025983 | 0.036668 | 0.058001 | 0.0014591 | 0.035476 | 0.091553 | 0.1236 | 0.10529 | 0.064087 | 0.059509 | 0.041199 | -0.086975 | 0.15564 | 0.11444 | 0.018311 | 0.018311 | 0.004578 | -0.027466 | -0.082397 | 0.091553 | -0.036621 | -122.1725 | 0.17395 | 0.11444 | 0.15106 | -122.1405 | 0.022888 | -0.032043 | -122.2137 | 0.20599 | 0.068665 | 0.10071 | -122.2275 | 0.10986 | 0.14191 | 0.15564 | -122.319 | 0.068665 | 0.054932 | 0.16479 | -122.3145
4483.375 | 122.4014 | -0.059509 | 122.2229 | -0.19562 | 0.046555 | 0.060114 | 0.0034009 | 0.029756 | -0.0055948 | 0.027869 | -0.15381 | 0.026624 | 0.037736 | 0.056078 | 0.00017731 | 0.036758 | 0.10071 | 0.13733 | 0.11444 | 0.07782 | 0.073242 | 0.045776 | -0.11902 | 0.1236 | 0.17395 | 0.045776 | 0.032043 | 0.022888 | -0.027466 | -0.064087 | 0.10528 | -0.05951 | -122.1497 | 0.19684 | 0.13733 | 0.19684 | -122.1222 | 0.032043 | -0.004578 | -122.1909 | 0.1831 | 0.10528 | 0.10986 | -122.2 | 0.13275 | 0.16022 | 0.17395 | -122.3419 | 0.091552 | 0.082397 | 0.23346 | -122.287
4485.0625 | 122.406 | -0.064087 | 122.2046 | 0.14771 | 0.045487 | 0.057977 | -0.0038623 | 0.02826 | -0.0017496 | 0.028937 | 0.13611 | 0.025983 | 0.034532 | 0.053301 | 0.0031681 | 0.03804 | 0.11444 | 0.12817 | 0.10529 | 0.068665 | 0.041199 | 0.059509 | -0.10529 | 0.16022 | 0.13275 | 0.018311 | 0.018311 | -0.004578 | -0.036621 | -0.091553 | 0.1236 | -0.041199 | -122.1634 | 0.19226 | 0.13275 | 0.17395 | -122.0901 | 0.027466 | -0.027466 | -122.1863 | 0.2243 | 0.082398 | 0.10986 | -122.2092 | 0.10529 | 0.17853 | 0.16937 | -122.3099 | 0.082398 | 0.059509 | 0.19684 | -122.2961
4486.8281 | 122.3648 | -0.091553 | 122.2412 | -0.19562 | 0.047623 | 0.062463 | 0.0059643 | 0.032533 | -0.0045266 | 0.027869 | -0.16144 | 0.025769 | 0.035387 | 0.055224 | 0.00017731 | 0.036544 | 0.086975 | 0.13275 | 0.11444 | 0.082397 | 0.059509 | 0.022888 | -0.091553 | 0.11902 | 0.16479 | 0.027466 | 0.027466 | 0.009155 | -0.018311 | -0.07782 | 0.11444 | 0 | -122.1817 | 0.2243 | 0.17395 | 0.17395 | -122.1542 | 0.073242 | 0.013733 | -122.2137 | 0.21057 | 0.11902 | 0.10529 | -122.2321 | 0.15106 | 0.17853 | 0.20599 | -122.3328 | 0.11902 | 0.10071 | 0.25635 | -122.319
4488.6094 | 122.3923 | -0.07782 | 122.2412 | 0.11719 | 0.046128 | 0.056268 | -1.7146e-05 | 0.030397 | -0.00068138 | 0.031501 | 0.036926 | 0.028546 | 0.034532 | 0.059923 | 0.0027407 | 0.035904 | 0.032043 | -0.045776 | -0.054932 | -0.009155 | 0.09613 | 0.013733 | -0.13275 | 0.050354 | -0.018311 | -0.10529 | 0.059509 | 0.059509 | -0.045776 | -0.11902 | 0.091553 | -0.054931 | -122.1451 | 0.032044 | 0.068665 | 0.1236 | -122.2092 | 0.032044 | -0.041199 | -122.1817 | 0.12817 | -0.027466 | 0.013733 | -122.1817 | 0.17395 | 0.10986 | 0.022888 | -122.374 | 0.13733 | 0.13733 | 0.059509 | -122.3602
4490.3125 | 122.4609 | -0.054932 | 122.2 | -0.0048827 | 0.047196 | 0.060541 | 0.0048963 | 0.029542 | -0.0075174 | 0.029151 | 0.021668 | 0.023419 | 0.038164 | 0.056505 | -0.0021725 | 0.038467 | 0.018311 | 0.068665 | 0.050354 | 0.027466 | 0.059509 | 0.036621 | -0.09613 | 0.09613 | 0.09613 | 0.013733 | 0.027466 | 0.036621 | -0.036621 | -0.091553 | 0.091553 | -0.041198 | -122.1405 | 0.1236 | 0.082398 | 0.1236 | -122.1817 | 0.018311 | -0.036621 | -122.1725 | 0.15106 | 0.068665 | 0.10529 | -122.1634 | 0.11444 | 0.073243 | 0.10529 | -122.2961 | 0.082398 | 0.091553 | 0.15106 | -122.2916
4492.0938 | 122.4014 | -0.073242 | 122.2275 | 0.071411 | 0.046341 | 0.060968 | 0.0027601 | 0.03061 | -0.006022 | 0.027869 | 0.10559 | 0.024488 | 0.034746 | 0.056292 | 0.0031681 | 0.039535 | 0.068665 | 0.12817 | 0.082397 | 0.045776 | 0.059509 | 0.032043 | -0.09613 | 0.1236 | 0.091553 | 0 | 0.027466 | 0.013733 | -0.022888 | -0.068665 | 0.10529 | -0.022888 | -122.168 | 0.20142 | 0.11902 | 0.14191 | -122.1588 | 0.050354 | 0.004577 | -122.2 | 0.19684 | 0.073242 | 0.068665 | -122.2137 | 0.13275 | 0.14191 | 0.15564 | -122.3236 | 0.10071 | 0.086975 | 0.16479 | -122.2961
4493.875 | 122.4335 | -0.036621 | 122.2137 | 0.13245 | 0.046982 | 0.059686 | 0.0021191 | 0.029328 | 0.00038662 | 0.031074 | 0.12085 | 0.025556 | 0.034318 | 0.058001 | 0.0020999 | 0.037613 | 0.041199 | 0.018311 | 0.013733 | 0.004578 | 0.091553 | 0.018311 | -0.11444 | 0.1236 | 0.086975 | -0.009155 | 0.050354 | 0.022888 | -0.018311 | -0.064087 | 0.054932 | -0.07782 | -122.1222 | 0.054932 | 0.041199 | 0.11902 | -122.1725 | 0.01831 | -0.027466 | -122.1634 | 0.16022 | 0.027466 | 0.054932 | -122.1909 | 0.12817 | 0.07782 | 0.050354 | -122.3282 | 0.086975 | 0.059509 | 0.1236 | -122.2778
4495.5781 | 122.4472 | -0.059509 | 122.2046 | -0.088806 | 0.046982 | 0.062036 | 0.0061781 | 0.028901 | -0.0070902 | 0.028297 | -0.077515 | 0.023847 | 0.036668 | 0.056933 | -0.0023861 | 0.037399 | 0.068665 | 0.12817 | 0.10071 | 0.073242 | 0.073242 | 0.045776 | -0.09613 | 0.16479 | 0.16022 | 0.068665 | 0.013733 | 0.027466 | -0.018311 | -0.086975 | 0.10528 | -0.036621 | -122.1313 | 0.18768 | 0.13275 | 0.16937 | -122.1359 | 0.041198 | -0.027466 | -122.1909 | 0.2243 | 0.12817 | 0.15564 | -122.1771 | 0.13275 | 0.12817 | 0.16022 | -122.3007 | 0.073242 | 0.086975 | 0.21973 | -122.2916
4497.3438 | 122.319 | -0.10529 | 122.2687 | -0.19562 | 0.045914 | 0.059686 | 0.0057507 | 0.029969 | -0.0062356 | 0.028724 | -0.23773 | 0.027478 | 0.0356 | 0.056933 | -3.629e-05 | 0.038467 | 0.07782 | 0.11902 | 0.073242 | 0.054932 | 0.082397 | 0.022888 | -0.09613 | 0.086975 | 0.10529 | -0.032043 | 0.050354 | 0.041199 | -0.032043 | -0.09613 | 0.12817 | 0.009156 | -122.1863 | 0.22431 | 0.16022 | 0.15106 | -122.1909 | 0.073243 | 0.009156 | -122.2183 | 0.19226 | 0.073243 | 0.064087 | -122.2275 | 0.18768 | 0.18311 | 0.17853 | -122.3648 | 0.15564 | 0.14649 | 0.21057 | -122.3648
4499.125 | 122.3419 | -0.09613 | 122.2504 | -0.10406 | 0.050186 | 0.059045 | 0.0023329 | 0.028688 | 0.0010276 | 0.031501 | -0.18433 | 0.029187 | 0.036241 | 0.058642 | 0.0035953 | 0.037826 | 0.07782 | 0.045776 | 0.018311 | 0.027466 | 0.073242 | 0.004578 | -0.11902 | 0.091553 | 0.086975 | -0.059509 | 0.036621 | 0.041199 | -0.041199 | -0.10071 | 0.10071 | -0.022889 | -122.1771 | 0.14191 | 0.1236 | 0.14649 | -122.1725 | 0.054931 | -0.004578 | -122.2137 | 0.18768 | 0.036621 | 0.041199 | -122.2092 | 0.16937 | 0.17395 | 0.11444 | -122.3694 | 0.13275 | 0.13733 | 0.1831 | -122.3511
4500.8281 | 122.4518 | -0.054932 | 122.2229 | -0.050659 | 0.046555 | 0.060968 | 0.0055371 | 0.029542 | -0.006663 | 0.028937 | -0.054626 | 0.024488 | 0.036241 | 0.057146 | -0.0021725 | 0.040603 | 0.022888 | 0.10071 | 0.082397 | 0.059509 | 0.082397 | 0.036621 | -0.12817 | 0.1236 | 0.15106 | 0.050354 | 0.022888 | 0.018311 | -0.013733 | -0.091553 | 0.091553 | -0.073242 | -122.1405 | 0.15564 | 0.11444 | 0.18768 | -122.2 | 0.041199 | -0.036621 | -122.2 | 0.17853 | 0.10529 | 0.14191 | -122.2046 | 0.13733 | 0.07782 | 0.13733 | -122.3511 | 0.07782 | 0.073243 | 0.20599 | -122.3145
4502.5938 | 122.3511 | -0.11444 | 122.2641 | -0.24902 | 0.048905 | 0.059259 | 0.0057507 | 0.027833 | -0.0040994 | 0.02851 | -0.23773 | 0.027692 | 0.037096 | 0.059496 | -0.0015317 | 0.038467 | 0.009155 | -0.004578 | -0.032043 | -0.027466 | 0.1236 | -0.004578 | -0.15106 | 0.018311 | 0.027466 | -0.091553 | 0.07782 | 0.054932 | -0.068665 | -0.11902 | 0.10986 | -0.036621 | -122.1405 | 0.10986 | 0.086975 | 0.1236 | -122.2549 | 0.045776 | -0.004578 | -122.1863 | 0.13275 | 0.022888 | 0.027466 | -122.2092 | 0.23804 | 0.1236 | 0.082398 | -122.4152 | 0.19226 | 0.16937 | 0.14191 | -122.3831
4504.3438 | 122.319 | -0.10071 | 122.2321 | 0.048523 | 0.046982 | 0.060541 | -0.00023075 | 0.02826 | 0.0025228 | 0.029792 | -0.0012209 | 0.027265 | 0.032396 | 0.059283 | 0.0038089 | 0.03804 | 0 | -0.041199 | -0.041199 | -0.018311 | 0.086975 | 0.009155 | -0.14191 | 0.009155 | -0.018311 | -0.13275 | 0.068665 | 0.059509 | -0.045776 | -0.10986 | 0.10986 | -0.041199 | -122.1451 | 0.059509 | 0.082397 | 0.1236 | -122.2321 | 0.054932 | -0.009155 | -122.1634 | 0.10986 | -0.032043 | -0.022888 | -122.1725 | 0.18768 | 0.10071 | 0.059509 | -122.374 | 0.16937 | 0.16022 | 0.082397 | -122.3419
4506.1094 | 122.3236 | -0.10071 | 122.2366 | 0.040894 | 0.049332 | 0.058618 | -0.00087155 | 0.029756 | -0.0013224 | 0.031074 | -0.0088499 | 0.027906 | 0.034318 | 0.06206 | 0.0063723 | 0.04103 | -0.009155 | -0.045776 | -0.054932 | -0.022888 | 0.09613 | 0.013733 | -0.15106 | 0.009155 | -0.013733 | -0.13275 | 0.064087 | 0.054932 | -0.07782 | -0.10529 | 0.11444 | -0.050354 | -122.1405 | 0.054932 | 0.07782 | 0.12817 | -122.2458 | 0.022888 | -0.004578 | -122.1725 | 0.10986 | -0.032043 | -0.027465 | -122.1817 | 0.19684 | 0.091553 | 0.045776 | -122.3877 | 0.1648 | 0.15564 | 0.086975 | -122.3419
4507.875 | 122.3328 | -0.10529 | 122.2321 | 0.018005 | 0.049332 | 0.058832 | 0.0029737 | 0.030824 | -0.0011088 | 0.032569 | 0.014038 | 0.027692 | 0.035173 | 0.060137 | 0.0027407 | 0.041458 | -0.022888 | -0.054932 | -0.045776 | -0.018311 | 0.09613 | 0.013733 | -0.15564 | 0 | 0.004578 | -0.091553 | 0.054932 | 0.068665 | -0.050354 | -0.11902 | 0.11902 | -0.050354 | -122.1359 | 0.050354 | 0.086975 | 0.13733 | -122.2549 | 0.054932 | -0.013733 | -122.1771 | 0.10529 | 0.013733 | 0.027466 | -122.1634 | 0.20142 | 0.082398 | 0.05951 | -122.3877 | 0.16022 | 0.17395 | 0.10986 | -122.3511
4509.6406 | 122.3557 | -0.09613 | 122.2321 | -0.13458 | 0.052109 | 0.060541 | 0.0027601 | 0.031892 | -0.002604 | 0.029365 | -0.12329 | 0.027478 | 0.033464 | 0.062273 | 0.00039091 | 0.04039 | 0.045776 | 0.041199 | 0.013733 | 0.041199 | 0.086975 | 0.009155 | -0.15564 | 0.07782 | 0.091553 | -0.054932 | 0.064087 | 0.036621 | -0.054932 | -0.09613 | 0.10528 | -0.05951 | -122.1451 | 0.13733 | 0.13733 | 0.19684 | -122.1863 | 0.041198 | 0 | -122.168 | 0.17395 | 0.041198 | 0.041198 | -122.1954 | 0.1831 | 0.14191 | 0.10986 | -122.3877 | 0.16022 | 0.13275 | 0.18768 | -122.3282
4511.4062 | 122.4426 | -0.064087 | 122.2183 | -0.0354 | 0.042923 | 0.061823 | 0.0010511 | 0.027406 | -0.012003 | 0.031074 | 0.036926 | 0.022779 | 0.037096 | 0.060778 | -0.0034543 | 0.041458 | 0.004578 | 0.064087 | 0.07782 | 0.041199 | 0.050354 | 0.032043 | -0.10986 | 0.10071 | 0.10986 | 0.032043 | 0.041199 | 0.036621 | -0.032043 | -0.082397 | 0.09613 | -0.045776 | -122.168 | 0.12817 | 0.10529 | 0.15106 | -122.2137 | 0.032044 | -0.01831 | -122.1771 | 0.1648 | 0.09613 | 0.11444 | -122.1817 | 0.11444 | 0.068665 | 0.14191 | -122.3282 | 0.10529 | 0.10071 | 0.17395 | -122.3007
4513.1719 | 122.3007 | -0.10986 | 122.2275 | 0.0027468 | 0.047409 | 0.060114 | -0.0012987 | 0.025483 | -0.0013224 | 0.031287 | 0.021668 | 0.026837 | 0.036668 | 0.066973 | 0.0053043 | 0.047226 | 0.027466 | -0.004578 | -0.036621 | 0.009155 | 0.091553 | 0.018311 | -0.13275 | 0 | 0.004578 | -0.10529 | 0.073242 | 0.050354 | -0.064087 | -0.13275 | 0.12817 | -0.022888 | -122.1359 | 0.10529 | 0.11902 | 0.14191 | -122.2 | 0.045776 | -0.022888 | -122.1542 | 0.10986 | 0.004577 | 0.027465 | -122.1771 | 0.20142 | 0.13733 | 0.073242 | -122.3602 | 0.18311 | 0.16022 | 0.11444 | -122.3602
4514.875 | 122.1222 | -0.39825 | 121.7514 | -0.20325 | 0.048477 | 0.058405 | 0.0040417 | 0.030397 | -0.0087992 | 0.027656 | -0.092773 | 0.025128 | 0.035173 | 0.60039 | 0.00060451 | 0.57829 | 0.022888 | 0.059509 | 0.041199 | 0.018311 | 0.004578 | 0 | -0.15106 | -0.004578 | 0.064087 | -0.091553 | -0.09613 | -0.10529 | -0.27008 | -0.33417 | 0.39825 | 0.24719 | -121.7468 | 0.45776 | 0.41657 | 0.16937 | -121.7285 | 0.12817 | 0.064087 | -121.8475 | 0.39368 | 0.3067 | 0.24261 | -121.8567 | 0.40283 | 0.42114 | 0.43945 | -121.9025 | 0.30212 | 0.29297 | 0.46234 | -122.0856
4516.6406 | 122.1542 | -0.07782 | 122.0444 | -0.17273 | 0.049973 | 0.060327 | 0.0042555 | 0.031037 | -0.0019632 | 0.029365 | -0.22247 | 0.017011 | 0.035387 | 0.053942 | 0.0012455 | 0.032699 | -0.013733 | -0.018311 | -0.018311 | -0.004578 | 0.11444 | -0.004578 | -0.14648 | 0.018311 | 0.050354 | -0.082397 | 0.064087 | 0.073242 | -0.064087 | -0.10529 | 0.073242 | -0.068664 | -121.9299 | 0.059509 | 0.073242 | 0.14191 | -122.0581 | 0.013733 | -0.027466 | -121.9803 | 0.096131 | -0.004577 | 0.022889 | -121.9711 | 0.19226 | 0.064087 | 0.059509 | -122.1909 | 0.14191 | 0.15106 | 0.12817 | -122.1497
4518.4062 | 122.2916 | -0.054932 | 122.0398 | -0.012512 | 0.043778 | 0.062891 | 0.00041005 | 0.027619 | -0.0098672 | 0.031074 | 0.036926 | 0.015088 | 0.034532 | 0.055865 | 0.0010317 | 0.036117 | -0.004578 | 0.054932 | 0.054932 | 0.036621 | 0.064087 | 0.041199 | -0.11444 | 0.09613 | 0.10071 | 0.018311 | 0.027466 | 0.018311 | -0.032043 | -0.082397 | 0.096131 | -0.059509 | -121.9757 | 0.10986 | 0.091553 | 0.15106 | -122.0444 | 0.022889 | -0.027465 | -122.0123 | 0.15106 | 0.073243 | 0.10071 | -122.0215 | 0.11902 | 0.050354 | 0.10986 | -122.1542 | 0.082398 | 0.073243 | 0.15564 | -122.1222
4520.0938 | 122.2046 | -0.086975 | 122.1085 | 0.040894 | 0.047196 | 0.057977 | 0.0023329 | 0.030397 | -4.058e-05 | 0.032783 | 0.090332 | 0.015515 | 0.033464 | 0.056719 | 0.0035953 | 0.03334 | -0.004578 | -0.054932 | -0.059509 | 0 | 0.082397 | 0.018311 | -0.13275 | 0.022888 | -0.022888 | -0.11444 | 0.082397 | 0.045776 | -0.050354 | -0.10986 | 0.10529 | -0.045776 | -122.0261 | 0.032043 | 0.086975 | 0.13275 | -122.113 | 0.036621 | -0.022888 | -122.0261 | 0.10986 | -0.027466 | -0.004578 | -122.0627 | 0.16937 | 0.082397 | 0.027466 | -122.2412 | 0.16937 | 0.13275 | 0.064087 | -122.2183
4521.8594 | 122.3282 | -0.050354 | 122.0901 | -0.096436 | 0.043564 | 0.060327 | 0.0044691 | 0.028474 | -0.0087992 | 0.027015 | -0.085144 | 0.012097 | 0.031755 | 0.056292 | -0.0017453 | 0.034622 | 0.082397 | 0.14648 | 0.11444 | 0.082397 | 0.073242 | 0.045776 | -0.086975 | 0.15106 | 0.1831 | 0.064087 | 0.013733 | 0.013733 | -0.013733 | -0.059509 | 0.09613 | -0.036621 | -122.0169 | 0.19684 | 0.13275 | 0.16937 | -122.0078 | 0.036621 | -0.009155 | -122.0764 | 0.20142 | 0.11444 | 0.1236 | -122.0764 | 0.1236 | 0.13275 | 0.16479 | -122.1771 | 0.064087 | 0.064087 | 0.23346 | -122.1497
4523.625 | 122.3602 | -0.036621 | 122.1039 | -0.012512 | 0.044632 | 0.060754 | 0.0023329 | 0.03061 | -0.0073038 | 0.027228 | 0.0064086 | 0.013166 | 0.031328 | 0.053728 | -3.629e-05 | 0.03569 | 0.036621 | 0.064087 | 0.059509 | 0.054932 | 0.073242 | 0.027466 | -0.10986 | 0.11444 | 0.11444 | 0.027466 | 0.045776 | 0.036621 | -0.022888 | -0.086975 | 0.064087 | -0.073242 | -122.0306 | 0.10071 | 0.091553 | 0.16479 | -122.0673 | 0.013733 | -0.050354 | -122.0581 | 0.15106 | 0.064087 | 0.11444 | -122.0673 | 0.10986 | 0.073242 | 0.09613 | -122.2137 | 0.082397 | 0.073242 | 0.15106 | -122.1909
4525.3125 | 122.2092 | -0.10529 | 122.1634 | 0.08667 | 0.049759 | 0.058832 | 0.00062385 | 0.030824 | 0.00081382 | 0.028724 | -0.024109 | 0.017438 | 0.032823 | 0.055437 | 0.0031681 | 0.034195 | 0.032043 | -0.036621 | -0.027466 | -0.004578 | 0.09613 | 0.013733 | -0.1236 | 0.013733 | -0.009155 | -0.11902 | 0.041199 | 0.068665 | -0.036621 | -0.10529 | 0.11902 | -0.01831 | -122.0673 | 0.068665 | 0.10071 | 0.11902 | -122.1313 | 0.068665 | 0 | -122.1222 | 0.11902 | -0.013733 | -0.013733 | -122.0947 | 0.20142 | 0.13733 | 0.07782 | -122.287 | 0.14649 | 0.17395 | 0.096131 | -122.2687
4527.0781 | 122.2504 | -0.082397 | 122.1497 | -0.13458 | 0.051041 | 0.059686 | 0.0036145 | 0.028047 | -0.0017496 | 0.031501 | -0.15381 | 0.015088 | 0.035814 | 0.056292 | 0.0033817 | 0.033554 | 0.054932 | 0.050354 | 0.013733 | 0.041199 | 0.091553 | 0.004578 | -0.12817 | 0.082397 | 0.082397 | -0.041199 | 0.054932 | 0.050354 | -0.027466 | -0.10986 | 0.086975 | -0.045777 | -122.0581 | 0.13275 | 0.1236 | 0.16937 | -122.0947 | 0.054931 | -0.027466 | -122.0947 | 0.16479 | 0.041198 | 0.068664 | -122.0993 | 0.17395 | 0.13733 | 0.09613 | -122.2778 | 0.13733 | 0.13275 | 0.16479 | -122.2595
4528.8438 | 122.2504 | -0.068665 | 122.1817 | -0.17273 | 0.046768 | 0.059045 | 0.0038281 | 0.027619 | -0.0085856 | 0.028724 | -0.13855 | 0.012311 | 0.034105 | 0.054583 | -0.00024989 | 0.036758 | 0.07782 | 0.13275 | 0.10529 | 0.07782 | 0.045776 | 0.036621 | -0.09613 | 0.09613 | 0.15106 | 0.018311 | 0.032043 | 0.013733 | -0.027466 | -0.082397 | 0.10529 | -0.027465 | -122.1359 | 0.20142 | 0.14649 | 0.17395 | -122.1039 | 0.041199 | -0.013732 | -122.1497 | 0.16479 | 0.086976 | 0.10071 | -122.168 | 0.11444 | 0.14649 | 0.17395 | -122.2778 | 0.10071 | 0.082398 | 0.21973 | -122.2641
4530.5938 | 122.2687 | -0.082397 | 122.1771 | -0.11169 | 0.05275 | 0.058191 | 0.0027601 | 0.027406 | 0.0010276 | 0.032569 | -0.14618 | 0.015515 | 0.034532 | 0.057787 | 0.0020999 | 0.032058 | 0.054932 | 0.059509 | 0.018311 | 0.027466 | 0.091553 | 0.027466 | -0.14191 | 0.082397 | 0.086975 | -0.050354 | 0.059509 | 0.041199 | -0.050354 | -0.09613 | 0.10986 | -0.05951 | -122.0856 | 0.14191 | 0.10986 | 0.16937 | -122.1222 | 0.032043 | -0.013733 | -122.1176 | 0.16479 | 0.032043 | 0.045776 | -122.1359 | 0.17395 | 0.13733 | 0.10071 | -122.319 | 0.14191 | 0.1236 | 0.16937 | -122.2733
4532.2969 | 122.3557 | -0.07782 | 122.1497 | -0.0048827 | 0.043991 | 0.059473 | 0.0029737 | 0.027192 | -0.008372 | 0.027015 | 0.067444 | 0.012525 | 0.034105 | 0.054583 | -0.0038815 | 0.035476 | 0.004578 | 0.07782 | 0.059509 | 0.036621 | 0.082397 | 0.027466 | -0.10529 | 0.07782 | 0.07782 | -0.004578 | 0.045776 | 0.022888 | -0.022888 | -0.091553 | 0.10529 | -0.027466 | -122.0673 | 0.15564 | 0.11444 | 0.14191 | -122.1451 | 0.054932 | -0.013733 | -122.1039 | 0.15564 | 0.073242 | 0.086975 | -122.1268 | 0.16022 | 0.082398 | 0.13733 | -122.2549 | 0.1236 | 0.10071 | 0.15564 | -122.2412
4534.0156 | 122.3511 | -0.054932 | 122.1725 | -0.11932 | 0.046768 | 0.060754 | 0.0046827 | 0.03061 | -0.007731 | 0.028724 | -0.16907 | 0.014661 | 0.037096 | 0.05501 | -0.0021725 | 0.035263 | 0.09613 | 0.14191 | 0.10986 | 0.07782 | 0.064087 | 0.045776 | -0.10071 | 0.13275 | 0.17853 | 0.054932 | 0.027466 | 0.004578 | -0.013733 | -0.07782 | 0.10071 | -0.045776 | -122.1085 | 0.19684 | 0.13275 | 0.17853 | -122.0764 | 0.041199 | -0.022888 | -122.1451 | 0.18768 | 0.10986 | 0.13275 | -122.168 | 0.11902 | 0.15106 | 0.16479 | -122.2733 | 0.082398 | 0.05951 | 0.23346 | -122.2504
4535.7969 | 122.3145 | -0.064087 | 122.1451 | 0.10193 | 0.048905 | 0.060114 | 0.0025465 | 0.026765 | 0.00017302 | 0.029792 | 0.036926 | 0.017865 | 0.033678 | 0.05736 | 0.0038089 | 0.033767 | 0.022888 | -0.032043 | -0.041199 | -0.022888 | 0.10529 | 0.009155 | -0.12817 | 0.041199 | 0.004578 | -0.09613 | 0.050354 | 0.050354 | -0.050354 | -0.09613 | 0.073242 | -0.064087 | -122.0398 | 0.032044 | 0.041199 | 0.10529 | -122.1222 | 0.013733 | -0.032043 | -122.0947 | 0.10529 | -0.032043 | 0 | -122.0947 | 0.16937 | 0.086975 | 0.022888 | -122.2733 | 0.11444 | 0.11444 | 0.068665 | -122.2412
4537.5625 | 122.3373 | -0.064087 | 122.2 | 0.079041 | 0.046768 | 0.060754 | 0.0031873 | 0.028047 | -0.0070902 | 0.03086 | 0.12848 | 0.015515 | 0.03325 | 0.055437 | -0.00067729 | 0.037826 | 0.07782 | 0.10071 | 0.10071 | 0.050354 | 0.045776 | 0.041199 | -0.09613 | 0.1236 | 0.10529 | 0.004578 | 0.027466 | 0.009155 | -0.022888 | -0.082397 | 0.10529 | -0.032043 | -122.1542 | 0.1648 | 0.11444 | 0.14648 | -122.1222 | 0.041199 | -0.01831 | -122.1725 | 0.18768 | 0.068665 | 0.086975 | -122.1909 | 0.10986 | 0.14191 | 0.1648 | -122.2961 | 0.091553 | 0.073242 | 0.16937 | -122.2824
4539.2812 | 122.3602 | -0.059509 | 122.1634 | 0.040894 | 0.046768 | 0.059686 | 0.0063917 | 0.029115 | -0.0075174 | 0.029365 | 0.052185 | 0.014661 | 0.034532 | 0.055224 | -0.0017453 | 0.036758 | 0.036621 | 0.064087 | 0.073242 | 0.027466 | 0.059509 | 0.027466 | -0.10529 | 0.091553 | 0.086975 | 0 | 0.027466 | 0.027466 | -0.036621 | -0.068665 | 0.086975 | -0.045777 | -122.1039 | 0.1236 | 0.086975 | 0.13275 | -122.1268 | 0.022888 | -0.009156 | -122.1359 | 0.15106 | 0.059509 | 0.068665 | -122.1359 | 0.11902 | 0.09613 | 0.13275 | -122.2687 | 0.086975 | 0.086975 | 0.14648 | -122.2321
4541.0625 | 122.3877 | -0.050354 | 122.1451 | 0.063782 | 0.047623 | 0.059686 | 0.0012647 | 0.029115 | 0.0010276 | 0.030006 | 0.090332 | 0.016584 | 0.032396 | 0.056078 | 0.0031681 | 0.035263 | 0.022888 | -0.009155 | -0.036621 | -0.013733 | 0.10529 | 0.009155 | -0.13275 | 0.07782 | 0.013733 | -0.059509 | 0.054932 | 0.045776 | -0.032043 | -0.09613 | 0.059509 | -0.082397 | -122.0398 | 0.041199 | 0.036621 | 0.11902 | -122.1222 | 0.018311 | -0.045776 | -122.0901 | 0.12817 | -0.009155 | 0.036621 | -122.0993 | 0.15564 | 0.073242 | 0.013733 | -122.2778 | 0.10529 | 0.09613 | 0.064087 | -122.2412
4542.7812 | 122.3511 | -0.064087 | 122.168 | 0.094299 | 0.046982 | 0.059259 | 0.0031873 | 0.028047 | -0.0036722 | 0.029151 | 0.14374 | 0.013806 | 0.035387 | 0.056505 | -0.00046349 | 0.03569 | 0.10529 | 0.10529 | 0.091553 | 0.059509 | 0.059509 | 0.027466 | -0.10071 | 0.14191 | 0.11444 | 0.013733 | 0.022888 | 0.013733 | -0.036621 | -0.10071 | 0.091553 | -0.036621 | -122.1085 | 0.16937 | 0.1236 | 0.16022 | -122.0627 | 0.027466 | -0.036621 | -122.1451 | 0.20599 | 0.07782 | 0.11444 | -122.1542 | 0.1236 | 0.16937 | 0.15564 | -122.2687 | 0.086975 | 0.07782 | 0.17853 | -122.2687
4544.5625 | 122.2824 | -0.082397 | 122.2137 | -0.10406 | 0.046768 | 0.059045 | 0.00062385 | 0.029328 | 0.00017302 | 0.029578 | -0.13855 | 0.015729 | 0.033464 | 0.057787 | 0.0040225 | 0.034622 | 0.091553 | 0.027466 | 0.013733 | 0.018311 | 0.086975 | 0.013733 | -0.12817 | 0.091553 | 0.086975 | -0.059509 | 0.059509 | 0.059509 | -0.050354 | -0.09613 | 0.09613 | -0.045777 | -122.1268 | 0.10986 | 0.10071 | 0.14649 | -122.1222 | 0.032043 | -0.013733 | -122.1542 | 0.17395 | 0.022888 | 0.036621 | -122.1542 | 0.16937 | 0.17395 | 0.09613 | -122.3419 | 0.14191 | 0.14191 | 0.16937 | -122.3099
4546.3125 | 122.2916 | -0.10071 | 122.2183 | -0.24139 | 0.049118 | 0.058618 | 0.0059643 | 0.029969 | -0.0038858 | 0.028937 | -0.2301 | 0.016584 | 0.036668 | 0.057574 | -0.00024989 | 0.034408 | 0.018311 | -0.013733 | -0.041199 | -0.027466 | 0.091553 | 0 | -0.14191 | 0.027466 | 0.027466 | -0.09613 | 0.091553 | 0.068665 | -0.073242 | -0.10529 | 0.10071 | -0.041199 | -122.1268 | 0.086975 | 0.073242 | 0.11444 | -122.2 | 0.027466 | -0.004578 | -122.1268 | 0.12817 | 0.004578 | 0.009156 | -122.1497 | 0.19226 | 0.11902 | 0.059509 | -122.3602 | 0.19226 | 0.16937 | 0.12817 | -122.3236
4548.0781 | 122.406 | -0.054932 | 122.1863 | -0.081177 | 0.044846 | 0.060327 | 0.0044691 | 0.029328 | -0.0073038 | 0.028297 | -0.077515 | 0.012525 | 0.03325 | 0.053301 | -0.0019589 | 0.037613 | 0.068665 | 0.11444 | 0.11444 | 0.054932 | 0.064087 | 0.041199 | -0.082397 | 0.16937 | 0.16937 | 0.059509 | 0.018311 | 0.018311 | -0.013733 | -0.07782 | 0.096131 | -0.027465 | -122.1222 | 0.16937 | 0.10986 | 0.13733 | -122.1176 | 0.041199 | -0.022888 | -122.168 | 0.22431 | 0.11444 | 0.13733 | -122.168 | 0.11902 | 0.1236 | 0.16937 | -122.2687 | 0.073243 | 0.073243 | 0.22431 | -122.2641
4549.8438 | 122.3969 | -0.045776 | 122.1542 | 0.12482 | 0.04805 | 0.0599 | -0.0025805 | 0.028688 | -0.0021768 | 0.031287 | 0.13611 | 0.015088 | 0.034532 | 0.056292 | 0.0033817 | 0.036117 | 0.032043 | -0.009155 | -0.004578 | 0.009155 | 0.09613 | 0.032043 | -0.13733 | 0.10071 | 0.068665 | -0.013733 | 0.032043 | 0.032043 | -0.018311 | -0.10071 | 0.077819 | -0.091553 | -122.0581 | 0.036621 | 0.054931 | 0.14648 | -122.1222 | 0.027465 | -0.054932 | -122.1222 | 0.14648 | 0.032043 | 0.086975 | -122.1222 | 0.14191 | 0.077819 | 0.041198 | -122.2916 | 0.077819 | 0.077819 | 0.11444 | -122.2549
4551.5469 | 122.2824 | -0.10071 | 122.2 | -0.19562 | 0.048477 | 0.061823 | 0.0048963 | 0.031037 | -0.004954 | 0.030006 | -0.21484 | 0.012952 | 0.035387 | 0.057146 | -0.0015317 | 0.038894 | 0.064087 | 0.10071 | 0.07782 | 0.068665 | 0.082397 | 0.032043 | -0.10071 | 0.086975 | 0.11902 | -0.027466 | 0.059509 | 0.036621 | -0.050354 | -0.10071 | 0.13275 | 0 | -122.1176 | 0.20142 | 0.16937 | 0.16937 | -122.1359 | 0.050354 | 0 | -122.1405 | 0.18768 | 0.073242 | 0.073242 | -122.1634 | 0.18311 | 0.1648 | 0.17853 | -122.3007 | 0.16022 | 0.13733 | 0.21973 | -122.3007
4553.2969 | 122.3007 | -0.073242 | 122.2275 | -0.11169 | 0.050186 | 0.0599 | 0.0055371 | 0.029969 | -0.00046778 | 0.030219 | -0.16907 | 0.016584 | 0.036241 | 0.057146 | 0.0029543 | 0.034622 | 0.07782 | 0.041199 | 0.022888 | 0.032043 | 0.09613 | 0.004578 | -0.13275 | 0.073242 | 0.07782 | -0.064087 | 0.059509 | 0.041199 | -0.064087 | -0.10529 | 0.07782 | -0.059509 | -122.1313 | 0.11444 | 0.10529 | 0.16479 | -122.1497 | 0.009155 | -0.032044 | -122.168 | 0.14648 | 0.009155 | 0.041199 | -122.1863 | 0.16937 | 0.15106 | 0.09613 | -122.3602 | 0.13275 | 0.11444 | 0.15106 | -122.3328
4555 | 122.3145 | -0.073242 | 122.2046 | -0.14221 | 0.04805 | 0.058191 | 0.0012647 | 0.029756 | -0.00089518 | 0.030433 | -0.15381 | 0.017652 | 0.0356 | 0.059069 | 0.0014591 | 0.03334 | 0.073242 | 0.032043 | 0.004578 | 0.041199 | 0.10071 | 0.018311 | -0.14648 | 0.07782 | 0.073242 | -0.050354 | 0.054932 | 0.045776 | -0.050354 | -0.10529 | 0.091553 | -0.073242 | -122.1039 | 0.10529 | 0.11444 | 0.18768 | -122.1313 | 0.022888 | -0.032044 | -122.1497 | 0.15106 | 0.022888 | 0.054932 | -122.1588 | 0.17395 | 0.14648 | 0.07782 | -122.3511 | 0.12817 | 0.11902 | 0.14648 | -122.3099
4556.7656 | 122.3511 | -0.07782 | 122.2 | 0.10193 | 0.045273 | 0.060327 | 0.0016919 | 0.029542 | -0.008372 | 0.028724 | 0.12085 | 0.01167 | 0.035173 | 0.056078 | -0.0021725 | 0.039749 | 0.050354 | 0.10529 | 0.054932 | 0.027466 | 0.059509 | 0.041199 | -0.10986 | 0.10986 | 0.07782 | 0.009155 | 0.027466 | 0.018311 | -0.036621 | -0.07782 | 0.11902 | -0.032043 | -122.1405 | 0.18311 | 0.10529 | 0.13733 | -122.1497 | 0.041199 | 0 | -122.1725 | 0.18768 | 0.086975 | 0.086975 | -122.1817 | 0.13733 | 0.12817 | 0.13275 | -122.3099 | 0.10529 | 0.096131 | 0.15564 | -122.2778
4558.5469 | 122.3969 | -0.050354 | 122.1817 | -0.15747 | 0.046341 | 0.063745 | 0.0025465 | 0.028047 | -0.0079446 | 0.029151 | -0.062256 | 0.01402 | 0.032396 | 0.057574 | -0.0011045 | 0.036758 | 0.091553 | 0.14191 | 0.12817 | 0.054932 | 0.073242 | 0.036621 | -0.09613 | 0.16022 | 0.19226 | 0.086975 | 0.022888 | 0.004578 | -0.022888 | -0.064087 | 0.086975 | -0.045776 | -122.1085 | 0.19226 | 0.10529 | 0.15106 | -122.0901 | 0.027466 | -0.013733 | -122.1588 | 0.21057 | 0.13733 | 0.15106 | -122.1771 | 0.1236 | 0.14191 | 0.17853 | -122.2778 | 0.073242 | 0.054932 | 0.24261 | -122.2458
4560.3125 | 122.2733 | -0.10986 | 122.2137 | -0.088806 | 0.048691 | 0.060754 | 0.00019645 | 0.029542 | 0.0016684 | 0.030433 | -0.10803 | 0.016156 | 0.034105 | 0.058001 | 0.0046633 | 0.034622 | 0.073242 | 0.064087 | -0.004578 | 0.036621 | 0.091553 | 0.004578 | -0.13275 | 0.059509 | 0.045776 | -0.086975 | 0.050354 | 0.041199 | -0.064087 | -0.11444 | 0.11444 | -0.022888 | -122.1222 | 0.17395 | 0.14648 | 0.16937 | -122.1405 | 0.045776 | -0.004578 | -122.1634 | 0.16937 | 0.022888 | 0.027466 | -122.1725 | 0.20142 | 0.18311 | 0.10529 | -122.3465 | 0.16022 | 0.15106 | 0.15564 | -122.3282
4562.0156 | 122.2595 | -0.10071 | 122.2137 | -0.04303 | 0.047837 | 0.059045 | 0.0021191 | 0.029969 | 0.00038662 | 0.030006 | -0.024109 | 0.015943 | 0.036882 | 0.055651 | 0.0031681 | 0.035263 | 0.022888 | 0.013733 | -0.018311 | 0.004578 | 0.10071 | 0.009155 | -0.13733 | 0.009155 | 0.009155 | -0.10529 | 0.054932 | 0.041199 | -0.07782 | -0.10986 | 0.10986 | -0.036621 | -122.113 | 0.11444 | 0.10529 | 0.14191 | -122.1909 | 0.022888 | -0.009155 | -122.1588 | 0.10986 | -0.004578 | 0.004577 | -122.1725 | 0.20142 | 0.1236 | 0.082397 | -122.3511 | 0.15564 | 0.14191 | 0.10986 | -122.3236
4563.7188 | 122.3282 | -0.07782 | 122.1771 | 0.079041 | 0.048477 | 0.060114 | 0.0031873 | 0.028688 | -0.0023904 | 0.032355 | 0.090332 | 0.015302 | 0.034318 | 0.057146 | 0.0027407 | 0.036117 | -0.022888 | -0.027466 | -0.036621 | -0.018311 | 0.10529 | 0.009155 | -0.14191 | 0.036621 | -0.018311 | -0.10986 | 0.045776 | 0.050354 | -0.050354 | -0.09613 | 0.086975 | -0.064087 | -122.0718 | 0.050354 | 0.059509 | 0.1236 | -122.2 | 0.027466 | -0.01831 | -122.1313 | 0.11444 | -0.032043 | -0.013733 | -122.1268 | 0.18311 | 0.054932 | 0.041199 | -122.319 | 0.1236 | 0.12817 | 0.059509 | -122.2733
4565.4844 | 122.3328 | -0.10529 | 122.2183 | -0.20325 | 0.051468 | 0.059045 | 0.0076733 | 0.028901 | -0.0034586 | 0.030219 | -0.1767 | 0.016156 | 0.036455 | 0.057787 | -0.0011045 | 0.036331 | 0.013733 | 0.022888 | -0.009155 | 0.032043 | 0.086975 | 0.004578 | -0.13275 | 0.045776 | 0.07782 | -0.045776 | 0.054932 | 0.054932 | -0.064087 | -0.11444 | 0.10986 | -0.027465 | -122.1313 | 0.12817 | 0.13733 | 0.16479 | -122.2046 | 0.041199 | -0.009155 | -122.1634 | 0.15106 | 0.05951 | 0.068665 | -122.1634 | 0.19226 | 0.11902 | 0.096131 | -122.3511 | 0.16022 | 0.16022 | 0.18311 | -122.3328
4567.1719 | 122.374 | -0.068665 | 122.2092 | 0.094299 | 0.044846 | 0.059686 | 0.00041005 | 0.028901 | -0.008372 | 0.027442 | 0.13611 | 0.013806 | 0.033678 | 0.055651 | -0.0023861 | 0.038253 | 0.059509 | 0.091553 | 0.07782 | 0.050354 | 0.050354 | 0.036621 | -0.091553 | 0.091553 | 0.10529 | 0.027466 | 0.013733 | 0.027466 | -0.027466 | -0.091553 | 0.10529 | -0.022888 | -122.1588 | 0.16022 | 0.11902 | 0.14191 | -122.1497 | 0.041199 | -0.022888 | -122.1954 | 0.16022 | 0.096131 | 0.11902 | -122.1817 | 0.11902 | 0.12817 | 0.14649 | -122.3007 | 0.082398 | 0.096131 | 0.17395 | -122.3007
4568.9375 | 122.4106 | -0.032043 | 122.1863 | -0.12695 | 0.045273 | 0.06225 | 0.0044691 | 0.027406 | -0.0075174 | 0.029578 | -0.062256 | 0.014875 | 0.035173 | 0.055651 | -0.0034543 | 0.03804 | 0.073242 | 0.11902 | 0.10071 | 0.073242 | 0.054932 | 0.036621 | -0.09613 | 0.14191 | 0.16937 | 0.068665 | 0.032043 | 0 | -0.022888 | -0.086975 | 0.068664 | -0.064087 | -122.1313 | 0.15106 | 0.10529 | 0.16937 | -122.113 | 0.009155 | -0.054932 | -122.1542 | 0.17395 | 0.10071 | 0.15564 | -122.1863 | 0.086975 | 0.10529 | 0.13275 | -122.2824 | 0.064086 | 0.032043 | 0.20142 | -122.2733
4570.7188 | 122.3648 | -0.059509 | 122.1725 | 0.14008 | 0.0457 | 0.06225 | 0.0010511 | 0.030183 | -0.0051676 | 0.027869 | 0.12848 | 0.012525 | 0.032823 | 0.054583 | 0.0012455 | 0.036972 | 0.091553 | 0.11444 | 0.10986 | 0.07782 | 0.054932 | 0.036621 | -0.073242 | 0.14191 | 0.13275 | 0.045776 | 0.036621 | -0.013733 | -0.022888 | -0.073242 | 0.09613 | -0.013733 | -122.1176 | 0.17395 | 0.13733 | 0.15106 | -122.081 | 0.036621 | -0.013733 | -122.1359 | 0.20142 | 0.10528 | 0.11902 | -122.1863 | 0.11444 | 0.15106 | 0.16937 | -122.2458 | 0.09613 | 0.045776 | 0.19226 | -122.2458
4572.4219 | 122.2824 | -0.11902 | 122.2183 | 0.010376 | 0.048905 | 0.056909 | 0.0014783 | 0.029328 | 0.00038662 | 0.029365 | -0.0012209 | 0.01637 | 0.034105 | 0.057787 | 0.0048769 | 0.036117 | 0.027466 | -0.013733 | -0.041199 | -0.009155 | 0.10071 | 0.013733 | -0.14191 | 0.022888 | -0.009155 | -0.12817 | 0.064087 | 0.054932 | -0.054932 | -0.11444 | 0.13275 | -0.022888 | -122.1176 | 0.10529 | 0.10986 | 0.13275 | -122.1909 | 0.064087 | 0.004578 | -122.1542 | 0.14191 | -0.009155 | -0.013733 | -122.1634 | 0.21973 | 0.14649 | 0.07782 | -122.3602 | 0.18311 | 0.17395 | 0.10986 | -122.3328
4574.2031 | 122.3694 | -0.068665 | 122.1817 | 0.071411 | 0.048905 | 0.062677 | 0.00083745 | 0.028901 | -0.0075174 | 0.026801 | 0.159 | 0.013166 | 0.034318 | 0.056505 | 0.0010317 | 0.037399 | 0.082397 | 0.10071 | 0.082397 | 0.059509 | 0.064087 | 0.059509 | -0.10529 | 0.11444 | 0.10071 | 0.018311 | 0.027466 | 0.009155 | -0.013733 | -0.09613 | 0.12817 | -0.036621 | -122.1176 | 0.16937 | 0.12817 | 0.16479 | -122.0993 | 0.054932 | -0.027465 | -122.1542 | 0.18311 | 0.086976 | 0.11444 | -122.1725 | 0.13275 | 0.15106 | 0.15106 | -122.287 | 0.096131 | 0.07782 | 0.16937 | -122.2778
4575.9688 | 122.3648 | -0.073242 | 122.1954 | 0.094299 | 0.045487 | 0.062677 | 0.0027601 | 0.028688 | -0.0070902 | 0.030433 | 0.12848 | 0.011884 | 0.03325 | 0.054583 | 0.00060451 | 0.037399 | 0.07782 | 0.13275 | 0.086975 | 0.059509 | 0.041199 | 0.045776 | -0.086975 | 0.15564 | 0.10986 | 0.027466 | 0.027466 | 0.018311 | -0.041199 | -0.073242 | 0.11902 | -0.013733 | -122.1542 | 0.20599 | 0.13275 | 0.14648 | -122.1176 | 0.032043 | 0 | -122.168 | 0.22888 | 0.10071 | 0.10071 | -122.1771 | 0.11444 | 0.15106 | 0.16022 | -122.2824 | 0.10071 | 0.091553 | 0.18311 | -122.2687
4577.7344 | 122.4426 | -0.07782 | 122.1634 | -0.027771 | 0.044632 | 0.060968 | 0.0031873 | 0.029756 | -0.0087992 | 0.027442 | -0.046997 | 0.012738 | 0.034959 | 0.055651 | -0.0015317 | 0.037613 | 0.041199 | 0.07782 | 0.068665 | 0.045776 | 0.073242 | 0.032043 | -0.10986 | 0.11902 | 0.13733 | 0.050354 | 0.041199 | 0.004578 | -0.018311 | -0.068665 | 0.10986 | -0.032043 | -122.0901 | 0.15564 | 0.1236 | 0.15564 | -122.1222 | 0.059509 | 0.009155 | -122.1222 | 0.19684 | 0.12817 | 0.11902 | -122.1588 | 0.15106 | 0.11902 | 0.14649 | -122.2733 | 0.11902 | 0.082398 | 0.21515 | -122.2321
4579.4531 | 122.3923 | -0.045776 | 122.1817 | 0.0027468 | 0.046768 | 0.060327 | 0.0042555 | 0.02826 | -0.0055948 | 0.026374 | 0.036926 | 0.014875 | 0.0356 | 0.056933 | -3.629e-05 | 0.033981 | 0.036621 | 0.045776 | 0.054932 | 0.041199 | 0.059509 | 0.032043 | -0.09613 | 0.082397 | 0.073242 | -0.009155 | 0.036621 | 0.027466 | -0.032043 | -0.07782 | 0.077819 | -0.050354 | -122.1222 | 0.091552 | 0.086975 | 0.13733 | -122.1451 | 0.013733 | -0.032044 | -122.1451 | 0.12817 | 0.036621 | 0.068665 | -122.1542 | 0.10528 | 0.082397 | 0.10071 | -122.2778 | 0.082397 | 0.073242 | 0.11902 | -122.2595
4581.2188 | 122.319 | -0.07782 | 122.2137 | -0.14984 | 0.047409 | 0.058191 | 0.0019055 | 0.028047 | -0.0013224 | 0.030646 | -0.19958 | 0.015729 | 0.034532 | 0.059283 | 0.0042361 | 0.033126 | 0.07782 | 0.032043 | 0.013733 | 0.036621 | 0.09613 | 0 | -0.13733 | 0.07782 | 0.07782 | -0.064087 | 0.059509 | 0.041199 | -0.032043 | -0.10071 | 0.07782 | -0.059509 | -122.1176 | 0.10986 | 0.11444 | 0.17395 | -122.1359 | 0.045777 | -0.022888 | -122.1542 | 0.15564 | 0.013733 | 0.036621 | -122.1725 | 0.17395 | 0.15564 | 0.091553 | -122.3511 | 0.13733 | 0.11902 | 0.15564 | -122.3145
4582.9688 | 122.2961 | -0.10529 | 122.1771 | 0.063782 | 0.047837 | 0.058618 | -1.7146e-05 | 0.02826 | 0.0012412 | 0.02851 | 0.059815 | 0.016584 | 0.035173 | 0.059923 | 0.0044497 | 0.036331 | 0.009155 | -0.054932 | -0.050354 | -0.018311 | 0.10529 | 0.013733 | -0.13733 | 0.027466 | -0.041199 | -0.13733 | 0.041199 | 0.036621 | -0.091553 | -0.12817 | 0.11902 | -0.032043 | -122.0718 | 0.050354 | 0.086975 | 0.11902 | -122.168 | 0.013733 | -0.022888 | -122.1359 | 0.13275 | -0.032043 | -0.009155 | -122.1405 | 0.21057 | 0.11444 | 0.054932 | -122.3145 | 0.14649 | 0.14191 | 0.064087 | -122.3053
4584.7344 | 122.4152 | 0.42572 | 122.7081 | -0.1651 | 0.048477 | 0.061823 | 0.0023329 | 0.029756 | -0.0013224 | 0.030219 | -0.21484 | 0.013593 | 0.0356 | 0.057574 | 0.0027407 | 0.037185 | 0.54016 | 0.53558 | 0.51727 | 0.53101 | 0.63629 | 0.53558 | 0.3891 | 0.5722 | 0.58136 | 0.44403 | 0.58594 | 0.56763 | 0.44861 | 0.3891 | 0.10986 | -0.036621 | -122.0718 | 0.10986 | 0.10529 | 0.14191 | -122.168 | 0.022888 | -0.036621 | -122.1222 | 0.14648 | 0.018311 | 0.054932 | -122.1405 | 0.21057 | 0.11444 | 0.091553 | -122.319 | 0.16022 | 0.14191 | 0.15564 | -122.319
4586.4375 | 122.4243 | -0.054932 | 122.1588 | -0.027771 | 0.046768 | 0.060754 | 0.0053235 | 0.027833 | -0.008372 | 0.029792 | 0.029297 | 0.012097 | 0.036455 | 0.058642 | -0.0043087 | 0.037399 | 0.004578 | 0.050354 | 0.050354 | 0.032043 | 0.068665 | 0.027466 | -0.10529 | 0.1236 | 0.13275 | 0.036621 | 0.027466 | 0.018311 | -0.036621 | -0.091553 | 0.082398 | -0.050354 | -122.0901 | 0.10529 | 0.086975 | 0.13733 | -122.1542 | 0.018311 | -0.036621 | -122.1313 | 0.17853 | 0.091553 | 0.12817 | -122.1405 | 0.1236 | 0.05951 | 0.10529 | -122.2641 | 0.082398 | 0.073243 | 0.18768 | -122.2504
4588.2031 | 122.4335 | 0.50812 | 122.8363 | -0.027771 | 0.044632 | 0.061609 | 0.0025465 | 0.028474 | -0.007731 | 0.027015 | -0.0012209 | 0.013806 | 0.034318 | 0.058001 | -0.0032407 | 0.038681 | -0.23804 | -0.16479 | -0.16937 | -0.17853 | -0.20599 | -0.21057 | -0.35248 | 0.041199 | 0.050354 | -0.036621 | -0.07782 | -0.082397 | -0.09613 | -0.16022 | -0.71869 | -0.8606 | -123.0423 | -0.67291 | -0.68665 | 0.17395 | -123.0743 | -0.60425 | -0.66833 | -122.9141 | -0.46692 | -0.54474 | 0.1236 | -122.9187 | -0.71411 | -0.74615 | -0.67749 | -123.1888 | -0.58594 | -0.59051 | -0.45776 | -122.9965
4589.9844 | 122.2549 | 0.4303 | 122.7814 | -0.21851 | 0.048264 | 0.062463 | 0.0040417 | 0.02826 | -0.002604 | 0.027869 | -0.20721 | 0.01402 | 0.03325 | 0.057574 | 0.00017731 | 0.036331 | 0.41199 | 0.41657 | 0.37079 | 0.39368 | 0.33875 | 0.28381 | 0.14191 | 0.45776 | 0.48065 | 0.37079 | 0.54016 | 0.48981 | 0.40741 | 0.35248 | -0.14649 | -0.28839 | -122.4426 | -0.013733 | -0.036621 | 0.25177 | -122.3694 | -0.022888 | -0.07782 | -122.2412 | 0.027466 | -0.059509 | 0.018311 | -122.2916 | -0.091553 | -0.018311 | -0.059509 | -122.6395 | 0.10986 | 0.059509 | 0.050354 | -122.4289
4591.75 | 122.4014 | -0.45319 | 121.8063 | 0.13245 | 0.044632 | 0.057977 | -0.00065795 | 0.02826 | -0.0036722 | 0.030006 | 0.17426 | 0.015515 | 0.033678 | 0.059283 | 0.0040225 | 0.036544 | -0.26093 | -0.26093 | -0.25635 | -0.29297 | -0.32044 | -0.31128 | -0.45776 | -0.21515 | -0.24719 | -0.33417 | -0.36163 | -0.35248 | -0.37537 | -0.4303 | 0.14191 | -0.004578 | -122.1268 | 0.19226 | 0.16022 | 0.1648 | -122.0673 | 0.07782 | 0.022888 | -122.168 | 0.23804 | 0.11902 | 0.096131 | -122.1588 | 0.13275 | 0.19226 | 0.19684 | -122.2641 | 0.091553 | 0.10071 | 0.20599 | -122.2366
4593.4531 | 122.287 | 0.46234 | 122.8088 | -0.25665 | 0.048905 | 0.060327 | 0.0066053 | 0.03061 | -0.0034586 | 0.028724 | -0.1004 | 0.013166 | 0.0356 | 0.059069 | -0.00024989 | 0.036544 | 0.49896 | 0.48981 | 0.4715 | 0.49439 | 0.59052 | 0.48981 | 0.33875 | 0.52643 | 0.54474 | 0.41657 | 0.54016 | 0.54016 | 0.42572 | 0.35706 | 0.027466 | -0.1236 | -122.2183 | 0.027466 | 0.032044 | 0.15564 | -122.3099 | -0.036621 | -0.10529 | -122.2687 | 0.064087 | -0.045776 | 0.059509 | -122.2687 | 0.12817 | 0.036621 | 0.009156 | -122.4701 | 0.07782 | 0.07782 | 0.082398 | -122.4518
4595.2188 | 122.2549 | 0.63629 | 122.9645 | -0.21088 | 0.049973 | 0.060327 | 0.0023329 | 0.029969 | -0.0040994 | 0.029151 | -0.13092 | 0.015729 | 0.032823 | 0.057787 | 0.0020999 | 0.038681 | 0.63629 | 0.68207 | 0.6546 | 0.65918 | 0.76446 | 0.70496 | 0.53558 | 0.69122 | 0.73242 | 0.60883 | 0.74616 | 0.72327 | 0.59509 | 0.54474 | 0.068664 | -0.10071 | -122.2 | 0.045776 | 0.022888 | 0.1236 | -122.3282 | -0.041199 | -0.091553 | -122.2183 | 0.054931 | -0.027466 | 0.064087 | -122.2412 | 0.12817 | 0 | 0.01831 | -122.4289 | 0.10986 | 0.086975 | 0.09613 | -122.4197
4596.9219 | 122.3648 | -0.59967 | 121.7148 | 0.08667 | 0.0457 | 0.060754 | 0.0023329 | 0.028901 | -0.0062356 | 0.028297 | 0.082703 | 0.014875 | 0.036241 | 0.054369 | -0.0017453 | 0.037399 | -0.69122 | -0.62256 | -0.62256 | -0.67749 | -0.67749 | -0.65918 | -0.81482 | -0.55389 | -0.58594 | -0.69122 | -0.64545 | -0.66376 | -0.71411 | -0.76446 | -0.05951 | -0.21515 | -122.3923 | -0.022889 | -0.07782 | 0.13733 | -122.406 | -0.11444 | -0.16479 | -122.3602 | 0.045776 | -0.091553 | 0.073242 | -122.3785 | -0.07782 | -0.091553 | -0.022889 | -122.5296 | -0.045777 | -0.064087 | 0.013733 | -122.4792
4598.6875 | 122.3007 | -0.10529 | 122.1909 | 0.033264 | 0.048905 | 0.059259 | 0.00062385 | 0.029328 | 0.0025228 | 0.029578 | 0.0064086 | 0.016156 | 0.034532 | 0.057574 | 0.0029543 | 0.035904 | -0.027466 | -0.073242 | -0.082397 | -0.036621 | 0.10529 | 0.013733 | -0.14648 | 0.036621 | -0.027466 | -0.14191 | 0.064087 | 0.036621 | -0.068665 | -0.12817 | 0.11902 | -0.041198 | -122.0856 | 0.032044 | 0.068665 | 0.10986 | -122.2183 | 0.036621 | -0.022888 | -122.1268 | 0.14191 | -0.036621 | -0.013733 | -122.1542 | 0.21057 | 0.07782 | 0.022889 | -122.3373 | 0.16937 | 0.14191 | 0.07782 | -122.319
4600.3906 | 122.4243 | -0.64545 | 121.5958 | 0.11719 | 0.04506 | 0.060754 | -0.0010851 | 0.028901 | -0.0028178 | 0.030006 | 0.12085 | 0.015088 | 0.03261 | 0.056505 | 0.0025271 | 0.039108 | -0.16479 | -0.13733 | -0.17395 | -0.19684 | -0.19226 | -0.2243 | -0.34332 | -0.45319 | -0.4715 | -0.5722 | -0.55389 | -0.56305 | -0.64087 | -0.70953 | 0.42114 | 0.30212 | -121.788 | 0.50812 | 0.44861 | 0.14648 | -121.7606 | 0.004578 | -0.064087 | -122.1497 | 0.19226 | 0.073242 | 0.13733 | -122.1588 | 0.45319 | 0.48065 | 0.4715 | -121.9391 | 0.091553 | 0.082398 | 0.17395 | -122.3053
4602.1562 | 122.4335 | -0.35706 | 121.8475 | 0.15533 | 0.047409 | 0.060327 | 0.0027601 | 0.030824 | -0.0017496 | 0.030646 | 0.052185 | 0.01637 | 0.032182 | 0.060992 | 0.0042361 | 0.035049 | -0.23804 | -0.29755 | -0.27008 | -0.24261 | -0.22888 | -0.25635 | -0.42572 | -0.17853 | -0.19226 | -0.3067 | -0.27924 | -0.27466 | -0.31586 | -0.37537 | 0.10071 | -0.068664 | -122.0764 | 0.05951 | 0.11444 | 0.1831 | -122.0856 | 0.041199 | -0.01831 | -122.1268 | 0.17853 | 0.050354 | 0.068664 | -122.1222 | 0.12817 | 0.11902 | 0.086975 | -122.2733 | 0.07782 | 0.082398 | 0.16479 | -122.2229
4603.8594 | 122.3785 | -0.054932 | 122.1817 | 0.094299 | 0.048477 | 0.060327 | 0.00062385 | 0.030183 | -0.0019632 | 0.031928 | 0.067444 | 0.015515 | 0.034746 | 0.05971 | 0.0029543 | 0.038894 | 0.013733 | -0.022888 | -0.022888 | -0.022888 | 0.086975 | 0.004578 | -0.11444 | 0.059509 | 0.009155 | -0.082397 | 0.050354 | 0.045776 | -0.050354 | -0.11444 | 0.05951 | -0.059509 | -122.0947 | 0.032044 | 0.032044 | 0.091553 | -122.168 | 0.004578 | -0.059509 | -122.1313 | 0.11444 | -0.027465 | 0.032044 | -122.1359 | 0.14191 | 0.068665 | 0.032044 | -122.2961 | 0.10529 | 0.10071 | 0.064087 | -122.2961
4605.625 | 122.3145 | -0.091553 | 122.2229 | -0.14984 | 0.046982 | 0.060327 | 0.0031873 | 0.030397 | -0.0011088 | 0.029792 | -0.13855 | 0.015515 | 0.033891 | 0.05971 | 0.0025271 | 0.037185 | 0.059509 | 0.036621 | 0.018311 | 0.041199 | 0.091553 | 0.018311 | -0.12817 | 0.07782 | 0.086975 | -0.054932 | 0.054932 | 0.050354 | -0.045776 | -0.091553 | 0.10986 | -0.036621 | -122.1313 | 0.12817 | 0.13275 | 0.16937 | -122.1634 | 0.045777 | 0 | -122.168 | 0.16937 | 0.036621 | 0.036621 | -122.1725 | 0.18311 | 0.15106 | 0.10986 | -122.3511 | 0.14649 | 0.14191 | 0.17853 | -122.3145
4607.3281 | 122.319 | -0.10071 | 122.2458 | -0.25665 | 0.048905 | 0.060754 | 0.0074597 | 0.027833 | -0.0045266 | 0.030646 | -0.23773 | 0.014661 | 0.034959 | 0.059923 | -0.00024989 | 0.039108 | -0.004578 | 0 | -0.013733 | -0.009155 | 0.10986 | 0.004578 | -0.13733 | 0.022888 | 0.032043 | -0.086975 | 0.073242 | 0.064087 | -0.068665 | -0.1236 | 0.10529 | -0.036621 | -122.1359 | 0.10071 | 0.091553 | 0.12817 | -122.2504 | 0.032043 | -0.022888 | -122.1725 | 0.1236 | 0.013733 | 0.036621 | -122.1817 | 0.21057 | 0.09613 | 0.086975 | -122.3831 | 0.17395 | 0.1648 | 0.13275 | -122.3694
4609.0938 | 122.3969 | -0.073242 | 122.2046 | -0.012512 | 0.043351 | 0.059045 | 0.0016919 | 0.029115 | -0.0079446 | 0.028724 | 0.067444 | 0.012952 | 0.035173 | 0.058428 | -0.00089089 | 0.04103 | 0.004578 | 0.064087 | 0.054932 | 0.036621 | 0.064087 | 0.041199 | -0.10529 | 0.073242 | 0.09613 | -0.004578 | 0.022888 | 0.013733 | -0.013733 | -0.09613 | 0.11444 | -0.032044 | -122.1405 | 0.13733 | 0.10986 | 0.14191 | -122.2 | 0.059509 | -0.022888 | -122.1817 | 0.14648 | 0.068664 | 0.091552 | -122.1909 | 0.13733 | 0.07782 | 0.12817 | -122.3099 | 0.09613 | 0.086975 | 0.16937 | -122.3007
4610.7969 | 122.3099 | -0.09613 | 122.2366 | -0.24902 | 0.049546 | 0.061609 | 0.0059643 | 0.028047 | -0.001536 | 0.027869 | -0.2301 | 0.01637 | 0.035387 | 0.059283 | 0.00039091 | 0.036972 | 0.004578 | -0.009155 | -0.036621 | -0.004578 | 0.10986 | 0.009155 | -0.15106 | 0.004578 | 0.036621 | -0.082397 | 0.07782 | 0.064087 | -0.073242 | -0.11902 | 0.10528 | -0.054932 | -122.1268 | 0.086975 | 0.091552 | 0.14648 | -122.2321 | 0.022888 | -0.022889 | -122.1588 | 0.10071 | 0.013733 | 0.036622 | -122.1725 | 0.20599 | 0.10071 | 0.059509 | -122.3877 | 0.17395 | 0.16022 | 0.13275 | -122.3557
4612.5625 | 122.287 | -0.10071 | 122.2046 | -0.058289 | 0.048477 | 0.0599 | -0.0010851 | 0.029328 | 0.001882 | 0.029151 | -0.085144 | 0.01637 | 0.034746 | 0.061846 | 0.0057315 | 0.037826 | 0.054932 | 0.041199 | 0.004578 | 0.022888 | 0.10529 | 0.018311 | -0.14648 | 0.054932 | 0.045776 | -0.082397 | 0.041199 | 0.059509 | -0.041199 | -0.12817 | 0.11902 | -0.045776 | -122.0993 | 0.14191 | 0.1236 | 0.16937 | -122.1497 | 0.059509 | -0.027466 | -122.1634 | 0.15564 | 0.018311 | 0.045777 | -122.1451 | 0.20599 | 0.15564 | 0.10529 | -122.3511 | 0.14191 | 0.16022 | 0.14648 | -122.3328
4614.3281 | 122.2824 | -0.10071 | 122.2046 | -0.088806 | 0.048905 | 0.061395 | -0.00044435 | 0.03296 | 0.00038662 | 0.029151 | -0.13092 | 0.015088 | 0.033037 | 0.060564 | 0.0040225 | 0.03804 | 0.068665 | 0.050354 | 0.022888 | 0.027466 | 0.09613 | 0.004578 | -0.12817 | 0.07782 | 0.086975 | -0.045776 | 0.041199 | 0.045776 | -0.041199 | -0.10529 | 0.10529 | -0.027466 | -122.1085 | 0.15106 | 0.12817 | 0.15564 | -122.1359 | 0.059509 | -0.004578 | -122.1634 | 0.17853 | 0.054932 | 0.05951 | -122.1588 | 0.19684 | 0.16937 | 0.1236 | -122.3328 | 0.14191 | 0.14648 | 0.18768 | -122.3099
4616.0469 | 122.2687 | -0.10986 | 122.2137 | -0.020142 | 0.050827 | 0.058832 | 0.0012647 | 0.029969 | -0.0017496 | 0.031928 | 0.036926 | 0.018506 | 0.034105 | 0.060351 | 0.0025271 | 0.039962 | 0.036621 | 0 | -0.004578 | -0.004578 | 0.086975 | 0.013733 | -0.12817 | 0.027466 | 0 | -0.10529 | 0.064087 | 0.059509 | -0.064087 | -0.11444 | 0.1236 | -0.018311 | -122.1268 | 0.10986 | 0.10529 | 0.1236 | -122.1771 | 0.045776 | -0.004578 | -122.1497 | 0.13733 | 0.004577 | 0.009155 | -122.1542 | 0.19684 | 0.14648 | 0.10529 | -122.3419 | 0.17395 | 0.16937 | 0.10986 | -122.3282
4617.75 | 122.3419 | -0.082397 | 122.2183 | -0.13458 | 0.049118 | 0.059045 | 0.0055371 | 0.03061 | -0.001536 | 0.03086 | -0.14618 | 0.01637 | 0.035387 | 0.061205 | -0.0013181 | 0.037826 | 0.027466 | 0.032043 | 0.018311 | 0.036621 | 0.10529 | 0 | -0.15106 | 0.059509 | 0.10071 | -0.045776 | 0.073242 | 0.045776 | -0.050354 | -0.09613 | 0.082397 | -0.068665 | -122.113 | 0.11444 | 0.11902 | 0.18768 | -122.1909 | 0.032043 | -0.013733 | -122.1451 | 0.14191 | 0.036621 | 0.050354 | -122.1725 | 0.18768 | 0.10986 | 0.10071 | -122.3694 | 0.15564 | 0.12817 | 0.18311 | -122.3145
4619.5 | 122.3099 | -0.086975 | 122.2137 | -0.10406 | 0.050186 | 0.059045 | 0.0046827 | 0.026551 | -0.0013224 | 0.030433 | -0.10803 | 0.01637 | 0.036241 | 0.06206 | -3.629e-05 | 0.039108 | 0.059509 | 0.050354 | 0.027466 | 0.036621 | 0.082397 | 0.022888 | -0.13275 | 0.082397 | 0.09613 | -0.045776 | 0.064087 | 0.045776 | -0.036621 | -0.082397 | 0.10986 | -0.045776 | -122.1313 | 0.13733 | 0.1236 | 0.16937 | -122.1542 | 0.050354 | 0.004578 | -122.1497 | 0.16937 | 0.041199 | 0.036621 | -122.168 | 0.16937 | 0.14648 | 0.11444 | -122.3465 | 0.15106 | 0.13275 | 0.1831 | -122.2961
4621.2656 | 122.3373 | -0.082397 | 122.2275 | -0.21088 | 0.050827 | 0.059259 | 0.0034009 | 0.03296 | -0.003245 | 0.030006 | -0.14618 | 0.016156 | 0.037096 | 0.060992 | 0.0012455 | 0.039535 | 0.013733 | -0.004578 | 0.004578 | 0.018311 | 0.09613 | 0.013733 | -0.1236 | 0.045776 | 0.082397 | -0.036621 | 0.064087 | 0.059509 | -0.041199 | -0.086975 | 0.09613 | -0.041199 | -122.1313 | 0.077819 | 0.10071 | 0.14191 | -122.2137 | 0.041198 | -0.004578 | -122.1634 | 0.12817 | 0.045776 | 0.050354 | -122.168 | 0.17853 | 0.09613 | 0.086975 | -122.3511 | 0.14648 | 0.14191 | 0.16479 | -122.3145
4622.9688 | 122.3557 | -0.068665 | 122.2412 | -0.20325 | 0.046768 | 0.062677 | 0.0048963 | 0.028688 | -0.010081 | 0.027228 | -0.1004 | 0.012738 | 0.035173 | 0.058428 | -0.0023861 | 0.041885 | 0.059509 | 0.13275 | 0.1236 | 0.068665 | 0.064087 | 0.036621 | -0.10529 | 0.12817 | 0.16937 | 0.054932 | 0.036621 | 0.018311 | -0.004578 | -0.07782 | 0.10529 | -0.036621 | -122.1771 | 0.20142 | 0.13733 | 0.17395 | -122.1817 | 0.064087 | -0.009155 | -122.2046 | 0.19684 | 0.1236 | 0.13275 | -122.2229 | 0.13275 | 0.12817 | 0.19226 | -122.3465 | 0.10529 | 0.086976 | 0.23804 | -122.319
4624.7344 | 122.3007 | -0.1236 | 122.2183 | 0.033264 | 0.046555 | 0.059473 | 0.00083745 | 0.02826 | -0.00089518 | 0.030219 | 0.067444 | 0.018292 | 0.037309 | 0.062487 | 0.0033817 | 0.038681 | -0.022888 | -0.059509 | -0.064087 | -0.027466 | 0.11444 | 0 | -0.15106 | 0.013733 | -0.018311 | -0.10986 | 0.073242 | 0.050354 | -0.073242 | -0.11444 | 0.1236 | -0.027466 | -122.1039 | 0.064087 | 0.09613 | 0.1236 | -122.2412 | 0.050354 | 0.009155 | -122.1451 | 0.13733 | 0.013733 | 0.004578 | -122.168 | 0.23804 | 0.10071 | 0.059509 | -122.3694 | 0.19684 | 0.17395 | 0.10528 | -122.3328
4626.4375 | 122.3923 | -0.059509 | 122.1588 | 0.39185 | 0.047623 | 0.062463 | 0.00041005 | 0.029115 | -0.0040994 | 0.029365 | 0.13611 | 0.013593 | 0.030901 | 0.058428 | 0.0023135 | 0.040603 | 0.07782 | 0.09613 | 0.07782 | 0.064087 | 0.036621 | 0.054932 | -0.091553 | 0.13275 | 0.1236 | 0.032043 | 0.004578 | 0.004578 | -0.018311 | -0.07782 | 0.11444 | -0.032044 | -122.1222 | 0.15564 | 0.1236 | 0.15564 | -122.081 | 0.041198 | -0.018311 | -122.1542 | 0.19226 | 0.091552 | 0.10986 | -122.1542 | 0.09613 | 0.13733 | 0.13733 | -122.2504 | 0.064087 | 0.064087 | 0.1831 | -122.2366
4628.2031 | 122.3785 | -0.064087 | 122.1817 | 0.018005 | 0.04805 | 0.060114 | 0.0010511 | 0.027406 | -0.0081582 | 0.028724 | 0.082703 | 0.013806 | 0.033037 | 0.057146 | -0.0011045 | 0.041671 | 0.027466 | 0.050354 | 0.045776 | 0.027466 | 0.064087 | 0.050354 | -0.11444 | 0.073242 | 0.07782 | 0.004578 | 0.041199 | 0.027466 | -0.027466 | -0.082397 | 0.11444 | -0.050354 | -122.1176 | 0.11444 | 0.091553 | 0.14191 | -122.1542 | 0.036621 | -0.01831 | -122.1405 | 0.13733 | 0.068665 | 0.086975 | -122.1542 | 0.12817 | 0.091553 | 0.10986 | -122.2961 | 0.10529 | 0.091553 | 0.14191 | -122.2641
4629.9219 | 122.3969 | -0.041199 | 122.1909 | 0.018005 | 0.0457 | 0.060541 | 0.0029737 | 0.029756 | -0.0064492 | 0.027228 | 0.075073 | 0.012311 | 0.034532 | 0.058642 | -0.0021725 | 0.038681 | 0.036621 | 0.045776 | 0.054932 | 0.027466 | 0.059509 | 0.027466 | -0.086975 | 0.082397 | 0.073242 | -0.004578 | 0.041199 | 0.041199 | -0.022888 | -0.073242 | 0.068665 | -0.045776 | -122.1313 | 0.086975 | 0.068665 | 0.11444 | -122.1542 | 0.018311 | -0.032043 | -122.1497 | 0.1236 | 0.036621 | 0.068664 | -122.1497 | 0.10071 | 0.07782 | 0.096131 | -122.2778 | 0.082398 | 0.082398 | 0.11444 | -122.2641
4631.6875 | 122.3419 | -0.082397 | 122.2046 | 0.10193 | 0.052536 | 0.059045 | 0.0036145 | 0.029969 | 0.00060022 | 0.031501 | 0.044556 | 0.01637 | 0.034959 | 0.0627 | 0.0010317 | 0.036972 | 0.027466 | -0.059509 | -0.054932 | -0.036621 | 0.086975 | -0.013733 | -0.14191 | 0.050354 | -0.018311 | -0.10986 | 0.054932 | 0.045776 | -0.050354 | -0.13275 | 0.068664 | -0.05951 | -122.1176 | 0.022888 | 0.045776 | 0.10529 | -122.1771 | 0.032043 | -0.050354 | -122.1497 | 0.13275 | -0.027466 | 0.022888 | -122.1588 | 0.16937 | 0.10986 | 0.027465 | -122.3465 | 0.13733 | 0.12817 | 0.064086 | -122.3373
4633.4375 | 122.3602 | -0.091553 | 122.2137 | 0.10956 | 0.049118 | 0.059473 | -0.0015125 | 0.029115 | -4.058e-05 | 0.02851 | 0.036926 | 0.013806 | 0.033464 | 0.063341 | 0.0031681 | 0.039749 | -0.004578 | -0.045776 | -0.045776 | -0.013733 | 0.10986 | -0.009155 | -0.14191 | 0.032043 | -0.013733 | -0.09613 | 0.059509 | 0.050354 | -0.059509 | -0.11902 | 0.082398 | -0.050354 | -122.1039 | 0.045777 | 0.07782 | 0.12817 | -122.2183 | 0.032044 | -0.027466 | -122.1542 | 0.1236 | -0.004577 | 0.022889 | -122.1634 | 0.20142 | 0.086975 | 0.045777 | -122.3557 | 0.15106 | 0.14191 | 0.07782 | -122.3328
4635.2031 | 122.319 | -0.15564 | 122.1405 | 0.025635 | 0.050186 | 0.059686 | 0.00019645 | 0.032746 | -0.002604 | 0.030433 | 0.021668 | 0.017224 | 0.034532 | 0.060137 | 0.0044497 | 0.041458 | -0.032043 | -0.054932 | -0.07782 | -0.032043 | 0.09613 | -0.004578 | -0.16022 | 0 | -0.059509 | -0.13275 | 0.050354 | 0.050354 | -0.10071 | -0.14191 | 0.15106 | -0.004577 | -122.0444 | 0.10071 | 0.1236 | 0.12817 | -122.1725 | 0.054932 | 0.013733 | -122.0901 | 0.15564 | 0.022889 | 0.009156 | -122.0901 | 0.25177 | 0.1236 | 0.07782 | -122.3007 | 0.20599 | 0.20599 | 0.096131 | -122.2824
4636.9062 | 122.374 | -0.52643 | 121.7468 | 0.025635 | 0.044419 | 0.061823 | 0.0016919 | 0.029756 | -0.0096536 | 0.028937 | 0.075073 | 0.012525 | 0.035814 | 0.059283 | -0.0017453 | 0.044021 | -0.49439 | -0.48065 | -0.48065 | -0.50354 | -0.46692 | -0.49896 | -0.65002 | -0.4303 | -0.44861 | -0.52185 | -0.50812 | -0.49439 | -0.53558 | -0.6134 | 0.027466 | -0.1236 | -122.2137 | 0.045776 | 0.022888 | 0.14648 | -122.2412 | -0.009155 | -0.086975 | -122.2549 | 0.09613 | 0.004577 | 0.091552 | -122.2412 | 0.059509 | 0.032043 | 0.045776 | -122.3969 | 0.01831 | 0.032043 | 0.07782 | -122.3602
4638.6719 | 122.2412 | -0.29755 | 121.9894 | -0.0354 | 0.047409 | 0.058618 | 0.0016919 | 0.029542 | 0.0016684 | 0.030006 | -0.046997 | 0.017438 | 0.036027 | 0.063555 | 0.0025271 | 0.039535 | 0.23346 | 0.14648 | 0.14191 | 0.14191 | 0.33417 | 0.21057 | 0.050354 | 0.054932 | 0.041199 | -0.09613 | 0.12817 | 0.07782 | -0.032043 | -0.10071 | 0.50812 | 0.3479 | -121.6553 | 0.44403 | 0.43945 | 0.091553 | -121.756 | 0.2655 | 0.19684 | -121.8613 | 0.35248 | 0.20142 | 0.004578 | -121.9116 | 0.63171 | 0.531 | 0.43945 | -121.9391 | 0.42572 | 0.37537 | 0.33874 | -122.0901
4640.375 | 122.3923 | -0.78735 | 121.4813 | 0.13245 | 0.049973 | 0.060114 | 0.0048963 | 0.030183 | -0.004954 | 0.030433 | 0.159 | 0.01402 | 0.034959 | 0.061419 | -0.0023861 | 0.04103 | -0.64545 | -0.63629 | -0.63629 | -0.68207 | -0.67291 | -0.70038 | -0.85602 | -0.60425 | -0.60425 | -0.72327 | -0.70953 | -0.72327 | -0.75989 | -0.8194 | 0.086976 | -0.068664 | -122.1542 | 0.15106 | 0.10529 | 0.17395 | -122.1268 | 0.027466 | -0.032043 | -122.1909 | 0.18311 | 0.064087 | 0.09613 | -122.2046 | 0.11444 | 0.14191 | 0.15106 | -122.3373 | 0.07782 | 0.064087 | 0.18311 | -122.3007
4642.1406 | 122.4152 | 0.16937 | 122.4564 | -0.050659 | 0.0457 | 0.059686 | 0.0042555 | 0.029969 | -0.0085856 | 0.028724 | -0.0012209 | 0.012738 | 0.032823 | 0.058428 | -0.0032407 | 0.042953 | -0.31128 | -0.26093 | -0.25177 | -0.3067 | -0.25635 | -0.29755 | -0.45319 | -0.17853 | -0.16022 | -0.25177 | -0.27466 | -0.28839 | -0.32501 | -0.38452 | -0.46692 | -0.62256 | -122.7127 | -0.4303 | -0.47607 | 0.14648 | -122.7676 | -0.49439 | -0.55389 | -122.731 | -0.3479 | -0.42114 | 0.13275 | -122.7448 | -0.42572 | -0.48065 | -0.42114 | -122.9095 | -0.44403 | -0.45776 | -0.32959 | -122.8409
4643.8438 | 122.3007 | -0.84686 | 121.4447 | 0.048523 | 0.047196 | 0.057764 | 0.0027601 | 0.029756 | 0.0010276 | 0.030219 | 0.036926 | 0.018079 | 0.033891 | 0.063341 | 0.0023135 | 0.041671 | -0.56763 | -0.65918 | -0.6546 | -0.63629 | -0.46692 | -0.57678 | -0.73242 | -0.71411 | -0.7782 | -0.88348 | -0.64545 | -0.67291 | -0.79193 | -0.86975 | 0.27008 | 0.11444 | -121.9116 | 0.18768 | 0.21057 | 0.09613 | -122.0123 | 0.054932 | -0.022888 | -122.0901 | 0.13275 | -0.036621 | -0.013733 | -122.1176 | 0.37994 | 0.27924 | 0.19226 | -122.1771 | 0.20142 | 0.17395 | 0.068665 | -122.3145
4645.6094 | 122.2641 | -0.52643 | 121.7056 | -0.0048827 | 0.050186 | 0.056055 | 0.0014783 | 0.026124 | -0.00046778 | 0.031287 | -0.0088499 | 0.014661 | 0.036241 | 0.062914 | 0.0025271 | 0.041244 | 0.1236 | 0.050354 | 0.032043 | 0.054932 | 0.1831 | 0.09613 | -0.059509 | -0.027466 | -0.054932 | -0.21515 | 0.041199 | 0.004578 | -0.12817 | -0.19684 | 0.62256 | 0.46692 | -121.5225 | 0.57678 | 0.58136 | 0.11444 | -121.582 | 0.39825 | 0.32959 | -121.6644 | 0.49896 | 0.31128 | -0.018311 | -121.701 | 0.70953 | 0.65002 | 0.55847 | -121.7651 | 0.56763 | 0.53101 | 0.4715 | -121.9025
4647.375 | 122.3694 | -0.6958 | 121.5454 | 0.11719 | 0.045487 | 0.060327 | 0.0014783 | 0.030183 | -0.0090128 | 0.031287 | 0.12848 | 0.013379 | 0.032396 | 0.061205 | 0.0016727 | 0.042099 | -0.72327 | -0.68665 | -0.6958 | -0.72327 | -0.72784 | -0.74616 | -0.88348 | -0.64545 | -0.65002 | -0.73242 | -0.74158 | -0.75531 | -0.80566 | -0.84686 | -0.050354 | -0.18768 | -122.2733 | 0.009155 | -0.027466 | 0.16022 | -122.2687 | -0.10986 | -0.15106 | -122.287 | 0.050354 | -0.036621 | 0.11444 | -122.3007 | -0.032043 | -0.027466 | 0 | -122.4289 | -0.045776 | -0.059509 | 0.045777 | -122.3923
4649.125 | 122.2641 | -0.082397 | 122.2366 | -0.18036 | 0.046982 | 0.0599 | 0.0040417 | 0.02826 | -0.006663 | 0.029792 | -0.2301 | 0.013166 | 0.032396 | 0.06206 | -0.0017453 | 0.042526 | 0.091553 | 0.11444 | 0.10986 | 0.082397 | 0.07782 | 0.1831 | 0.054932 | 0.1236 | 0.1831 | 0.041199 | 0.064087 | 0.059509 | -0.041199 | -0.09613 | 0.2655 | 0.13733 | -122.1588 | 0.19684 | 0.16479 | 0.027465 | -122.1451 | 0.041198 | -0.013733 | -122.1725 | 0.20599 | 0.1236 | 0.13733 | -122.1771 | 0.16022 | 0.17395 | 0.19226 | -122.1817 | 0.14648 | 0.14191 | 0.2655 | -122.3328
4650.8438 | 122.319 | 0.3479 | 122.6303 | -0.23376 | 0.048691 | 0.061395 | 0.0051099 | 0.029756 | -0.00089518 | 0.026801 | -0.25299 | 0.017652 | 0.036455 | 0.060351 | 0.0014591 | 0.041885 | 0.54474 | 0.52643 | 0.51727 | 0.54016 | 0.69122 | 0.59052 | 0.44403 | 0.57678 | 0.56763 | 0.46234 | 0.61798 | 0.59052 | 0.46234 | 0.41199 | 0.24262 | 0.096131 | -121.9391 | 0.17853 | 0.19226 | 0.09613 | -122.0856 | 0.11444 | 0.064087 | -122.0123 | 0.22888 | 0.11444 | 0.050354 | -122.0398 | 0.34332 | 0.19684 | 0.16937 | -122.1863 | 0.27008 | 0.24262 | 0.21973 | -122.2183
4652.6094 | 122.406 | -0.49896 | 121.6873 | 0.10956 | 0.046555 | 0.059473 | 0.0014783 | 0.032105 | -0.003245 | 0.02851 | 0.15137 | 0.012097 | 0.032396 | 0.061632 | 0.0018863 | 0.042953 | -0.35248 | -0.36621 | -0.37537 | -0.39368 | -0.41199 | -0.41657 | -0.54932 | -0.36163 | -0.39368 | -0.4715 | -0.49439 | -0.48523 | -0.52185 | -0.56305 | 0.082397 | -0.050354 | -122.0993 | 0.13275 | 0.10529 | 0.15564 | -122.0398 | -0.022889 | -0.064087 | -122.1817 | 0.13733 | 0.027465 | 0.091552 | -122.1725 | 0.086975 | 0.14648 | 0.1236 | -122.2366 | 0.004577 | 0.013733 | 0.10529 | -122.2504
4654.3594 | 122.4152 | -0.064087 | 122.1359 | 0.0027468 | 0.043991 | 0.061823 | 0.0016919 | 0.026124 | -0.0098672 | 0.026374 | 0.014038 | 0.013806 | 0.0356 | 0.062487 | -0.00089089 | 0.042526 | -0.32501 | -0.27008 | -0.25177 | -0.26093 | -0.25177 | -0.27924 | -0.40741 | -0.16937 | -0.16937 | -0.26093 | -0.24719 | -0.24719 | -0.3067 | -0.34332 | -0.21515 | -0.34332 | -122.3877 | -0.20599 | -0.19684 | 0.14648 | -122.4609 | -0.24261 | -0.27924 | -122.3831 | -0.10529 | -0.19684 | 0.082398 | -122.3831 | -0.18768 | -0.26093 | -0.18768 | -122.5433 | -0.1831 | -0.1831 | -0.10529 | -122.4792
4656.0625 | 122.3145 | 0.091553 | 122.3648 | -0.20325 | 0.047623 | 0.060754 | 0.0046827 | 0.029969 | -0.0047404 | 0.026374 | -0.13092 | 0.013806 | 0.034532 | 0.061632 | -0.0021725 | 0.042953 | 0.19684 | 0.21973 | 0.21515 | 0.15106 | 0.15106 | 0.13733 | -0.022888 | 0.23804 | 0.28381 | 0.14648 | 0.1236 | 0.13733 | 0.086975 | 0.036621 | 0.045776 | -0.11444 | -122.2137 | 0.12817 | 0.059509 | 0.17395 | -122.168 | -0.004578 | -0.054932 | -122.2412 | 0.14648 | 0.054931 | 0.10986 | -122.2275 | 0.059509 | 0.10529 | 0.1236 | -122.3877 | 0.032043 | 0.045776 | 0.19226 | -122.3282
4657.8281 | 122.3465 | 0.33417 | 122.5983 | -0.18799 | 0.04805 | 0.061395 | -0.00065795 | 0.030824 | 0.0012412 | 0.029792 | -0.2301 | 0.017224 | 0.031114 | 0.064837 | 0.0044497 | 0.039322 | 0.67291 | 0.63629 | 0.6134 | 0.62256 | 0.73242 | 0.63171 | 0.48981 | 0.65002 | 0.65002 | 0.53558 | 0.67291 | 0.63629 | 0.54474 | 0.52185 | 0.29755 | 0.15564 | -121.8658 | 0.30212 | 0.28839 | 0.13275 | -121.9254 | 0.21057 | 0.18768 | -121.9254 | 0.31586 | 0.20142 | 0.013732 | -121.962 | 0.39826 | 0.33875 | 0.27924 | -122.1085 | 0.33875 | 0.30212 | 0.31586 | -122.0764
4659.5938 | 122.4152 | -0.25177 | 122.0398 | -0.012512 | 0.04271 | 0.060541 | 0.0014783 | 0.028688 | -0.0081582 | 0.028297 | 0.052185 | 0.012097 | 0.034105 | 0.061419 | -0.00067729 | 0.044021 | -0.16937 | -0.14191 | -0.12817 | -0.16022 | -0.09613 | -0.14191 | -0.27466 | -0.10529 | -0.11444 | -0.20599 | -0.17395 | -0.16479 | -0.23346 | -0.29755 | 0.10986 | -0.022888 | -122.1359 | 0.10986 | 0.091553 | 0.11444 | -122.2092 | 0.018311 | -0.045776 | -122.2137 | 0.14648 | 0.045776 | 0.091552 | -122.2046 | 0.15564 | 0.082397 | 0.1236 | -122.3145 | 0.07782 | 0.086975 | 0.13733 | -122.3373
4661.2969 | 122.3511 | 0.018311 | 122.2733 | -0.21088 | 0.04805 | 0.061182 | 0.0059643 | 0.02826 | -0.0055948 | 0.028937 | -0.16907 | 0.013593 | 0.035387 | 0.061419 | -0.0034543 | 0.042099 | 0.1831 | 0.25177 | 0.22888 | 0.21057 | 0.15564 | 0.13733 | -0.004578 | 0.25635 | 0.2655 | 0.15564 | 0.14191 | 0.14191 | 0.10071 | 0.027466 | 0.11902 | -0.022889 | -122.1176 | 0.23346 | 0.19226 | 0.21515 | -122.0901 | 0.082397 | 0.009155 | -122.1313 | 0.23804 | 0.13733 | 0.12817 | -122.1313 | 0.13733 | 0.16479 | 0.21057 | -122.2778 | 0.1236 | 0.1236 | 0.24719 | -122.2458
4663 | 122.4976 | 0.032043 | 122.2504 | -0.050659 | 0.044205 | 0.062036 | 0.0021191 | 0.028474 | -0.0081582 | 0.030006 | -0.046997 | 0.014447 | 0.033464 | 0.060564 | -0.0011045 | 0.041671 | -0.1236 | -0.082397 | -0.07782 | -0.12817 | -0.073242 | -0.11444 | -0.22888 | 0 | 0.009155 | -0.10529 | -0.10529 | -0.14191 | -0.16937 | -0.21057 | -0.14648 | -0.26093 | -122.3236 | -0.11444 | -0.16022 | 0.10071 | -122.374 | -0.20142 | -0.24261 | -122.3557 | -0.032043 | -0.13733 | 0.10529 | -122.3923 | -0.10529 | -0.15564 | -0.10986 | -122.4792 | -0.13733 | -0.17395 | -0.022888 | -122.4609
4664.7656 | 122.3282 | 0.63629 | 122.937 | -0.19562 | 0.050186 | 0.0599 | 0.0025465 | 0.028047 | 0.0020956 | 0.029365 | -0.24536 | 0.014875 | 0.035173 | 0.066332 | 0.0014591 | 0.042526 | 0.92468 | 0.91553 | 0.84686 | 0.8606 | 1.0117 | 0.89722 | 0.737 | 0.90179 | 0.88348 | 0.76446 | 0.91095 | 0.89264 | 0.77362 | 0.73242 | 0.26093 | 0.10071 | -121.9254 | 0.27924 | 0.2243 | 0.1236 | -122.0123 | 0.13733 | 0.09613 | -122.0261 | 0.2655 | 0.12817 | 0.032043 | -122.0444 | 0.37537 | 0.28839 | 0.21057 | -122.2 | 0.27466 | 0.25635 | 0.24719 | -122.2046
4666.5469 | 122.2549 | -0.51727 | 121.7422 | -0.10406 | 0.047837 | 0.059045 | -0.0010851 | 0.030183 | -4.058e-05 | 0.031714 | -0.092773 | 0.016584 | 0.033891 | 0.070391 | 0.0055179 | 0.044021 | 0.60883 | 0.57678 | 0.54016 | 0.54932 | 0.6134 | 0.54932 | 0.40283 | 0.55389 | 0.53101 | 0.37994 | 0.53558 | 0.53558 | 0.42114 | 0.37079 | 1.0666 | 0.9201 | -121.1288 | 1.0941 | 1.0666 | 0.14648 | -121.1334 | 0.93842 | 0.88806 | -121.2067 | 1.0712 | 0.89722 | 0.009155 | -121.2067 | 1.1307 | 1.1261 | 1.0574 | -121.3394 | 1.0529 | 1.0529 | 1.0483 | -121.3715
4668.3125 | 122.3145 | 0.7782 | 123.1338 | -0.17273 | 0.048264 | 0.059045 | 0.0074597 | 0.029328 | -0.0062356 | 0.029365 | -0.21484 | 0.013379 | 0.034959 | 0.063128 | -0.0019589 | 0.038681 | 0.94299 | 0.99335 | 0.97961 | 0.9613 | 0.9613 | 0.92468 | 0.76446 | 1.0757 | 1.0941 | 0.90179 | 0.96588 | 0.95215 | 0.86975 | 0.8194 | 0.14649 | -0.013733 | -122.1725 | 0.21515 | 0.18311 | 0.19684 | -122.1909 | 0.091553 | 0.041199 | -122.168 | 0.29755 | 0.1236 | 0.082397 | -122.1817 | 0.18311 | 0.1648 | 0.20142 | -122.3694 | 0.18768 | 0.17395 | 0.31586 | -122.3145
4670.0156 | 122.287 | -0.13733 | 122.1725 | -0.1651 | 0.045914 | 0.060754 | 0.0027601 | 0.030183 | -0.004313 | 0.028297 | -0.19196 | 0.01402 | 0.03261 | 0.064623 | 0.00017731 | 0.045517 | 0.036621 | 0.10071 | 0.073242 | 0.041199 | 0.036621 | 0 | -0.13275 | 0.07782 | 0.10529 | -0.036621 | -0.004578 | -0.009155 | -0.068665 | -0.13275 | 0.13733 | 0.004578 | -122.1359 | 0.23804 | 0.17853 | 0.17395 | -122.1359 | 0.068664 | 0.004578 | -122.1771 | 0.21515 | 0.10071 | 0.09613 | -122.1817 | 0.17395 | 0.17395 | 0.21057 | -122.3053 | 0.13275 | 0.12817 | 0.24262 | -122.3053
4671.7812 | 122.3831 | -0.082397 | 122.1222 | 0.12482 | 0.046341 | 0.059259 | -0.00044435 | 0.029115 | -0.0021768 | 0.028724 | 0.18188 | 0.015302 | 0.034105 | 0.066332 | 0.00081811 | 0.044235 | 0.082397 | 0.07782 | 0.064087 | 0.045776 | 0.022888 | 0.018311 | -0.13275 | 0.1236 | 0.10071 | -0.009155 | -0.013733 | -0.032043 | -0.064087 | -0.10071 | 0.10071 | -0.050354 | -122.0993 | 0.16022 | 0.12817 | 0.17853 | -122.0398 | 0.01831 | -0.018311 | -122.1359 | 0.20599 | 0.073242 | 0.091553 | -122.1542 | 0.10528 | 0.16479 | 0.14648 | -122.2549 | 0.068664 | 0.050354 | 0.18311 | -122.2229
4673.5469 | 122.2595 | -0.13275 | 122.1909 | -0.24139 | 0.048264 | 0.058191 | 0.0061781 | 0.029115 | -0.0038858 | 0.030006 | -0.21484 | 0.015515 | 0.035173 | 0.064623 | -0.0017453 | 0.044021 | -0.018311 | -0.027466 | -0.036621 | -0.027466 | 0.050354 | -0.032043 | -0.15564 | 0.004578 | 0.004578 | -0.10986 | 0.050354 | 0.027466 | -0.09613 | -0.15106 | 0.10071 | -0.022889 | -122.1405 | 0.10529 | 0.10529 | 0.12817 | -122.2092 | 0.036621 | -0.018311 | -122.1405 | 0.13733 | 0.022888 | 0.041199 | -122.1634 | 0.18311 | 0.11444 | 0.09613 | -122.3465 | 0.18311 | 0.16022 | 0.13733 | -122.3419
4675.25 | 122.4243 | -0.086975 | 122.113 | -0.027771 | 0.0457 | 0.060754 | 0.0023329 | 0.029969 | -0.0090128 | 0.027656 | -0.0088499 | 0.012311 | 0.034959 | 0.064623 | -0.0017453 | 0.046371 | -0.013733 | 0.032043 | 0.032043 | 0.004578 | 0.059509 | -0.009155 | -0.14648 | 0.082397 | 0.086975 | 0 | 0.004578 | -0.027466 | -0.054932 | -0.1236 | 0.07782 | -0.059509 | -122.0535 | 0.11902 | 0.091553 | 0.15106 | -122.1268 | 0.032043 | -0.036621 | -122.1085 | 0.16937 | 0.086975 | 0.1236 | -122.1405 | 0.14648 | 0.073242 | 0.11902 | -122.2595 | 0.091553 | 0.059509 | 0.17395 | -122.2366
4676.9688 | 122.3373 | -0.091553 | 122.1497 | 0.10956 | 0.045273 | 0.061182 | 0.0012647 | 0.028047 | -0.0045266 | 0.030219 | 0.097962 | 0.01402 | 0.034959 | 0.065691 | 0.0012455 | 0.046798 | 0.036621 | 0.073242 | 0.036621 | -0.009155 | 0.018311 | 0.009155 | -0.10529 | 0.082397 | 0.045776 | -0.041199 | -0.004578 | -0.022888 | -0.064087 | -0.12817 | 0.10071 | -0.013733 | -122.1313 | 0.16479 | 0.082398 | 0.096131 | -122.113 | 0.027466 | -0.036621 | -122.1542 | 0.17395 | 0.050354 | 0.086975 | -122.1725 | 0.10986 | 0.12817 | 0.12817 | -122.2549 | 0.086975 | 0.068665 | 0.13733 | -122.2778
4678.7344 | 122.3419 | -0.091553 | 122.1405 | 0.079041 | 0.045487 | 0.060327 | 0.00019645 | 0.029328 | -0.0064492 | 0.029151 | 0.067444 | 0.014447 | 0.0356 | 0.065478 | 0.0014591 | 0.047653 | 0.013733 | 0.073242 | 0.045776 | 0 | 0.018311 | 0.022888 | -0.14191 | 0.09613 | 0.050354 | -0.041199 | 0.004578 | -0.009155 | -0.054932 | -0.10529 | 0.11444 | -0.050354 | -122.1222 | 0.16479 | 0.091553 | 0.14191 | -122.1268 | 0.036621 | -0.013733 | -122.1359 | 0.18768 | 0.050354 | 0.064087 | -122.1497 | 0.10986 | 0.10529 | 0.13733 | -122.2824 | 0.096131 | 0.082398 | 0.14191 | -122.2458
4680.5 | 122.3145 | -0.10529 | 122.1634 | -0.18036 | 0.048691 | 0.060114 | -0.00065795 | 0.029969 | 0.001882 | 0.029151 | -0.25299 | 0.015515 | 0.034959 | 0.065691 | 0.0040225 | 0.044235 | -0.009155 | -0.036621 | -0.050354 | -0.018311 | 0.073242 | -0.018311 | -0.1831 | 0.022888 | 0.027466 | -0.10529 | 0.032043 | 0.013733 | -0.10071 | -0.14191 | 0.086975 | -0.077819 | -122.0901 | 0.068665 | 0.086975 | 0.16479 | -122.1725 | 0.004578 | -0.036621 | -122.1313 | 0.12817 | 0 | 0.036621 | -122.1497 | 0.17853 | 0.096131 | 0.054932 | -122.3465 | 0.13733 | 0.11902 | 0.13275 | -122.3053
4682.2812 | 122.3969 | -0.073242 | 122.1313 | 0.094299 | 0.049118 | 0.058618 | -0.00044435 | 0.02826 | -4.058e-05 | 0.029792 | 0.11322 | 0.017224 | 0.033891 | 0.066332 | 0.0029543 | 0.044876 | 0.013733 | -0.013733 | -0.027466 | -0.027466 | 0.059509 | -0.027466 | -0.15106 | 0.064087 | 0.027466 | -0.059509 | 0.009155 | -0.013733 | -0.07782 | -0.11444 | 0.045776 | -0.07782 | -122.0718 | 0.059509 | 0.045776 | 0.1236 | -122.1176 | -0.004578 | -0.041199 | -122.1222 | 0.13733 | 0.013733 | 0.054932 | -122.1451 | 0.13275 | 0.086975 | 0.045776 | -122.2824 | 0.082397 | 0.059509 | 0.10071 | -122.2458
4684.0469 | 122.406 | -0.091553 | 122.1359 | 0.13245 | 0.04506 | 0.059473 | 0.0010511 | 0.029328 | -0.0023904 | 0.027442 | 0.044556 | 0.01637 | 0.034105 | 0.066546 | 0.0033817 | 0.044021 | 0.022888 | 0.036621 | 0.022888 | -0.004578 | 0.054932 | -0.004578 | -0.14648 | 0.10986 | 0.091553 | -0.013733 | 0.004578 | 0 | -0.064087 | -0.10986 | 0.086975 | -0.054931 | -122.081 | 0.12817 | 0.086975 | 0.14191 | -122.113 | 0.027466 | -0.01831 | -122.1313 | 0.20142 | 0.07782 | 0.09613 | -122.1359 | 0.14649 | 0.11444 | 0.11444 | -122.2824 | 0.096131 | 0.091553 | 0.18311 | -122.2458
4685.7656 | 122.3465 | -0.09613 | 122.1405 | 0.11719 | 0.045487 | 0.0599 | 0.00041005 | 0.02826 | -0.0045266 | 0.029578 | 0.12848 | 0.015302 | 0.033037 | 0.065264 | 0.0035953 | 0.049362 | 0.059509 | 0.091553 | 0.073242 | 0.036621 | 0.036621 | 0.022888 | -0.12817 | 0.11902 | 0.10529 | 0 | -0.018311 | -0.018311 | -0.064087 | -0.10529 | 0.11902 | -0.032044 | -122.1039 | 0.18768 | 0.13275 | 0.1648 | -122.081 | 0.032043 | -0.009156 | -122.1588 | 0.21515 | 0.09613 | 0.10529 | -122.1588 | 0.13275 | 0.15564 | 0.16937 | -122.2687 | 0.077819 | 0.077819 | 0.20142 | -122.2458
4687.5469 | 122.3465 | -0.11902 | 122.1359 | 0.079041 | 0.046341 | 0.06225 | 0.0044691 | 0.026338 | -0.0055948 | 0.027869 | 0.11322 | 0.01402 | 0.032396 | 0.064837 | 0.0010317 | 0.04808 | 0.050354 | 0.086975 | 0.059509 | 0.018311 | 0.013733 | 0.018311 | -0.15106 | 0.082397 | 0.086975 | -0.004578 | -0.004578 | -0.018311 | -0.059509 | -0.10529 | 0.13733 | -0.032043 | -122.1222 | 0.20599 | 0.13733 | 0.16937 | -122.0856 | 0.05951 | 0.013733 | -122.1405 | 0.20142 | 0.11444 | 0.10071 | -122.1542 | 0.13275 | 0.16937 | 0.17853 | -122.287 | 0.11444 | 0.10071 | 0.20599 | -122.2412
4689.3125 | 122.2504 | -0.1236 | 122.1451 | -0.096436 | 0.0504 | 0.058405 | 0.00083745 | 0.028688 | 0.0014548 | 0.029792 | -0.13855 | 0.017438 | 0.035387 | 0.069536 | 0.0020999 | 0.044662 | 0.054932 | 0.022888 | -0.013733 | -0.009155 | 0.050354 | -0.027466 | -0.16479 | 0.045776 | 0.032043 | -0.09613 | 0.022888 | 0.022888 | -0.082397 | -0.14648 | 0.09613 | -0.041199 | -122.0947 | 0.14648 | 0.11444 | 0.15564 | -122.0901 | 0.041199 | -0.022888 | -122.1222 | 0.16937 | 0.027466 | 0.050354 | -122.1222 | 0.17395 | 0.17853 | 0.10986 | -122.3099 | 0.14648 | 0.14648 | 0.15564 | -122.2916
4691.0156 | 122.3099 | -0.12817 | 122.1588 | -0.21088 | 0.050186 | 0.059686 | 0.0040417 | 0.02826 | -0.001536 | 0.029578 | -0.18433 | 0.014661 | 0.037309 | 0.070177 | 0.0018863 | 0.046798 | -0.009155 | -0.018311 | -0.032043 | -0.013733 | 0.059509 | -0.022888 | -0.17853 | 0.013733 | 0.032043 | -0.082397 | 0.032043 | 0.013733 | -0.082397 | -0.15106 | 0.10529 | -0.050354 | -122.0993 | 0.10986 | 0.11444 | 0.16479 | -122.168 | 0.045777 | -0.022888 | -122.1268 | 0.14191 | 0.045777 | 0.068665 | -122.1451 | 0.18768 | 0.11902 | 0.096131 | -122.3373 | 0.16022 | 0.14191 | 0.16022 | -122.3099
4692.7812 | 122.3648 | -0.10986 | 122.1313 | -0.0048827 | 0.046555 | 0.060327 | 0.0059643 | 0.029542 | -0.00944 | 0.027015 | 0.067444 | 0.012952 | 0.036882 | 0.06975 | -0.0028135 | 0.050644 | -0.027466 | 0.013733 | 0.022888 | 0.013733 | 0.050354 | 0 | -0.14191 | 0.045776 | 0.054932 | -0.022888 | 0 | -0.022888 | -0.050354 | -0.12817 | 0.10986 | -0.032044 | -122.081 | 0.1236 | 0.1236 | 0.15564 | -122.1588 | 0.059509 | -0.018311 | -122.1313 | 0.15564 | 0.086975 | 0.10529 | -122.1542 | 0.16022 | 0.082397 | 0.13275 | -122.2733 | 0.10986 | 0.086975 | 0.16479 | -122.2595
4694.5469 | 122.2366 | -0.14191 | 122.1497 | -0.04303 | 0.050614 | 0.057123 | 0.0021191 | 0.031465 | 0.001882 | 0.030006 | -0.031738 | 0.01402 | 0.033464 | 0.070391 | 0.0033817 | 0.048721 | 0.009155 | -0.004578 | -0.032043 | -0.022888 | 0.054932 | -0.022888 | -0.16479 | 0.004578 | -0.009155 | -0.15106 | 0.032043 | 0.013733 | -0.086975 | -0.15106 | 0.11902 | -0.022888 | -122.0947 | 0.13733 | 0.11902 | 0.14191 | -122.1405 | 0.054932 | -0.009155 | -122.1176 | 0.14649 | -0.009155 | 0 | -122.1359 | 0.19684 | 0.15106 | 0.10986 | -122.3145 | 0.17395 | 0.15564 | 0.13275 | -122.3007
4696.3125 | 122.3007 | -0.1236 | 122.1451 | -0.21088 | 0.048905 | 0.059259 | 0.0042555 | 0.03061 | -0.002604 | 0.03086 | -0.16907 | 0.014447 | 0.037736 | 0.068468 | 0.00081811 | 0.04808 | -0.050354 | -0.041199 | -0.059509 | -0.027466 | 0.086975 | -0.032043 | -0.16937 | -0.004578 | 0.004578 | -0.11444 | 0.041199 | 0.022888 | -0.11444 | -0.13733 | 0.091553 | -0.045777 | -122.0581 | 0.082397 | 0.09613 | 0.14191 | -122.1954 | 0.009155 | -0.013733 | -122.1039 | 0.11902 | 0.009155 | 0.022888 | -122.1222 | 0.21057 | 0.073242 | 0.064087 | -122.3145 | 0.16479 | 0.14648 | 0.12817 | -122.2824
4698.0781 | 122.2641 | -0.14191 | 122.1588 | -0.1651 | 0.050614 | 0.062891 | 0.0063917 | 0.031678 | -0.0030314 | 0.030433 | -0.21484 | 0.013379 | 0.038377 | 0.072741 | -0.0021725 | 0.050644 | -0.064087 | -0.013733 | -0.041199 | -0.041199 | 0.059509 | -0.027466 | -0.16937 | -0.013733 | 0.004578 | -0.11444 | 0.027466 | 0.022888 | -0.09613 | -0.16937 | 0.11444 | -0.027466 | -122.0993 | 0.12817 | 0.10071 | 0.12817 | -122.2229 | 0.045777 | -0.027466 | -122.1313 | 0.12817 | 0.027466 | 0.054932 | -122.1359 | 0.20142 | 0.07782 | 0.10071 | -122.3282 | 0.16937 | 0.16479 | 0.14649 | -122.3282
4699.7812 | 122.3465 | -0.10071 | 122.113 | -0.1651 | 0.046982 | 0.060968 | 0.0010511 | 0.029328 | -0.0075174 | 0.030219 | -0.14618 | 0.01402 | 0.033037 | 0.068896 | 0.00060451 | 0.051071 | 0.032043 | 0.13275 | 0.09613 | 0.041199 | 0.027466 | 0.004578 | -0.13275 | 0.091553 | 0.14648 | 0.022888 | 0 | -0.022888 | -0.059509 | -0.10529 | 0.10529 | -0.032043 | -122.0856 | 0.23346 | 0.14191 | 0.17395 | -122.081 | 0.041199 | -0.004578 | -122.113 | 0.19226 | 0.1236 | 0.12817 | -122.1359 | 0.12817 | 0.13275 | 0.19684 | -122.2458 | 0.10071 | 0.07782 | 0.24719 | -122.2183
4701.5469 | 122.374 | -0.091553 | 122.1085 | 0.063782 | 0.047409 | 0.059045 | 0.0019055 | 0.030183 | -0.0019632 | 0.029578 | 0.11322 | 0.015943 | 0.035387 | 0.071459 | 0.0040225 | 0.049148 | -0.027466 | -0.032043 | -0.054932 | -0.032043 | 0.086975 | -0.018311 | -0.17853 | 0.041199 | 0 | -0.082397 | 0.004578 | -0.004578 | -0.07782 | -0.13733 | 0.073242 | -0.086975 | -122.0215 | 0.05951 | 0.05951 | 0.14648 | -122.1359 | 0.013733 | -0.045776 | -122.1039 | 0.13275 | 0.009156 | 0.054932 | -122.113 | 0.17853 | 0.064087 | 0.036621 | -122.287 | 0.096131 | 0.086975 | 0.091553 | -122.2458
4703.3125 | 122.2458 | -0.14191 | 122.1817 | -0.088806 | 0.048477 | 0.059473 | 0.00019645 | 0.026765 | 0.0012412 | 0.030646 | -0.1004 | 0.017011 | 0.033891 | 0.069536 | 0.0046633 | 0.048294 | 0.041199 | 0.018311 | -0.013733 | 0 | 0.054932 | -0.013733 | -0.15564 | 0.045776 | 0.036621 | -0.09613 | 0.027466 | 0.032043 | -0.086975 | -0.14191 | 0.12817 | -0.013733 | -122.1268 | 0.16022 | 0.14191 | 0.15564 | -122.1405 | 0.054932 | 0 | -122.1542 | 0.18768 | 0.045777 | 0.045777 | -122.1497 | 0.19684 | 0.18311 | 0.12817 | -122.3373 | 0.16937 | 0.17395 | 0.17853 | -122.3236
4705.0781 | 122.3053 | -0.11444 | 122.1451 | -0.14221 | 0.052109 | 0.060327 | 0.0034009 | 0.029115 | -0.0045266 | 0.028937 | -0.15381 | 0.015515 | 0.034746 | 0.073382 | 0.0038089 | 0.049789 | 0.004578 | -0.004578 | -0.027466 | 0 | 0.073242 | -0.018311 | -0.17853 | 0.032043 | 0.050354 | -0.07782 | 0.018311 | 0.022888 | -0.091553 | -0.15106 | 0.09613 | -0.064087 | -122.0718 | 0.10986 | 0.11444 | 0.17853 | -122.1405 | 0.022888 | -0.036621 | -122.1268 | 0.14648 | 0.036621 | 0.073242 | -122.1222 | 0.18768 | 0.11902 | 0.086975 | -122.3236 | 0.13275 | 0.13733 | 0.16479 | -122.2961
4706.7812 | 122.3511 | -0.086975 | 122.1268 | 0.13245 | 0.044419 | 0.056055 | 0.0025465 | 0.030397 | -0.0073038 | 0.030646 | 0.19714 | 0.013806 | 0.031114 | 0.072741 | 0.0020999 | 0.051712 | 0.050354 | 0.086975 | 0.068665 | 0.045776 | 0.018311 | 0.009155 | -0.14191 | 0.10986 | 0.10986 | 0.009155 | -0.022888 | -0.027466 | -0.073242 | -0.10529 | 0.09613 | -0.054932 | -122.1085 | 0.17395 | 0.13275 | 0.18768 | -122.0764 | 0.013733 | -0.018311 | -122.1497 | 0.19684 | 0.09613 | 0.11444 | -122.1542 | 0.10529 | 0.13733 | 0.15564 | -122.2687 | 0.064087 | 0.059509 | 0.19684 | -122.2321
4708.5469 | 122.3145 | -0.11444 | 122.113 | 0.10193 | 0.050614 | 0.060327 | 0.0038281 | 0.028474 | -0.00089518 | 0.030646 | 0.075073 | 0.016797 | 0.036668 | 0.076159 | 0.0038089 | 0.050857 | -0.022888 | -0.068665 | -0.082397 | -0.050354 | 0.068665 | -0.045776 | -0.17395 | 0 | -0.041199 | -0.1236 | 0.022888 | 0.022888 | -0.10529 | -0.14191 | 0.068665 | -0.059509 | -122.0444 | 0.045776 | 0.064087 | 0.1236 | -122.1359 | 0.009155 | -0.027466 | -122.0901 | 0.11444 | -0.009155 | 0.018311 | -122.0901 | 0.18311 | 0.091553 | 0.032044 | -122.287 | 0.13733 | 0.13733 | 0.073242 | -122.2549
4710.25 | 122.287 | -0.13275 | 122.1497 | -0.25665 | 0.049973 | 0.061182 | 0.0044691 | 0.029969 | -0.0038858 | 0.02851 | -0.21484 | 0.013379 | 0.0356 | 0.075304 | -0.00046349 | 0.052139 | -0.045776 | -0.036621 | -0.073242 | -0.036621 | 0.054932 | -0.027466 | -0.18768 | -0.032043 | 0 | -0.11902 | 0.041199 | 0.009155 | -0.10986 | -0.15106 | 0.10529 | -0.054932 | -122.0947 | 0.09613 | 0.09613 | 0.15106 | -122.1954 | 0.022888 | -0.018311 | -122.1085 | 0.10071 | 0.013732 | 0.032043 | -122.1405 | 0.18768 | 0.086975 | 0.059509 | -122.3373 | 0.17395 | 0.14191 | 0.13275 | -122.3007
4712.0312 | 122.3694 | -0.086975 | 122.1176 | 0.063782 | 0.04805 | 0.060754 | 0.0014783 | 0.028901 | -0.0047404 | 0.031928 | 0.13611 | 0.014661 | 0.034105 | 0.072741 | -0.00024989 | 0.052566 | 0.045776 | 0.086975 | 0.050354 | 0.032043 | 0.027466 | 0.013733 | -0.1236 | 0.10529 | 0.082397 | 0 | 0.004578 | -0.009155 | -0.045776 | -0.09613 | 0.10071 | -0.036621 | -122.0901 | 0.17395 | 0.11902 | 0.15564 | -122.0718 | 0.041199 | -0.009155 | -122.113 | 0.19226 | 0.086975 | 0.09613 | -122.1268 | 0.11444 | 0.13275 | 0.13733 | -122.2412 | 0.091553 | 0.07782 | 0.16937 | -122.2137
4713.7812 | 122.3785 | -0.11444 | 122.1039 | -0.0048827 | 0.043351 | 0.062036 | 0.0031873 | 0.02826 | -0.0081582 | 0.028724 | 0.029297 | 0.012097 | 0.033464 | 0.073168 | -0.00067729 | 0.054916 | -0.018311 | 0.036621 | 0.022888 | -0.004578 | 0.032043 | -0.004578 | -0.14648 | 0.059509 | 0.07782 | -0.009155 | -0.009155 | -0.022888 | -0.068665 | -0.12817 | 0.10986 | -0.032043 | -122.0718 | 0.15106 | 0.10986 | 0.14191 | -122.1222 | 0.045776 | -0.013733 | -122.113 | 0.17395 | 0.10529 | 0.11902 | -122.1268 | 0.14648 | 0.09613 | 0.13733 | -122.2504 | 0.10529 | 0.091553 | 0.19226 | -122.2321
4715.5469 | 122.2549 | -0.13275 | 122.1359 | -0.45502 | 0.045273 | 0.059045 | 0.0046827 | 0.028474 | -0.0038858 | 0.028297 | -0.21484 | 0.01637 | 0.034318 | 0.075731 | 0.00039091 | 0.053207 | -0.027466 | -0.041199 | -0.050354 | -0.054932 | 0.059509 | -0.045776 | -0.17853 | -0.013733 | 0.004578 | -0.1236 | 0.032043 | 0.032043 | -0.10071 | -0.14191 | 0.086975 | -0.045777 | -122.0764 | 0.091552 | 0.077819 | 0.1236 | -122.1634 | 0.032043 | -0.009156 | -122.1039 | 0.11902 | 0.009155 | 0.018311 | -122.1039 | 0.19226 | 0.10529 | 0.082397 | -122.3145 | 0.16479 | 0.16479 | 0.13733 | -122.2778
4717.3438 | 122.3328 | -0.1236 | 122.1176 | 0.056152 | 0.04506 | 0.059686 | 0.0046827 | 0.029115 | -0.0053812 | 0.026374 | 0.11322 | 0.012738 | 0.034318 | 0.074877 | 0.00039091 | 0.053634 | 0.009155 | 0.045776 | 0.032043 | 0.009155 | 0.027466 | 0.013733 | -0.13733 | 0.068665 | 0.054932 | -0.032043 | -0.013733 | -0.013733 | -0.059509 | -0.13733 | 0.13733 | -0.013733 | -122.0901 | 0.16937 | 0.13275 | 0.14648 | -122.1085 | 0.064087 | -0.013733 | -122.1313 | 0.19226 | 0.091553 | 0.10529 | -122.1313 | 0.15106 | 0.13275 | 0.15564 | -122.2549 | 0.10986 | 0.10986 | 0.17853 | -122.2549
4719.1094 | 122.2961 | -0.12817 | 122.113 | -0.18036 | 0.051468 | 0.059259 | 0.0023329 | 0.031465 | -0.002604 | 0.030006 | -0.21484 | 0.014875 | 0.03261 | 0.07445 | 0.0025271 | 0.053421 | -0.009155 | -0.032043 | -0.045776 | -0.022888 | 0.07782 | -0.018311 | -0.16022 | 0.018311 | 0.027466 | -0.086975 | 0.036621 | 0.013733 | -0.10071 | -0.14648 | 0.10986 | -0.032043 | -122.0352 | 0.096131 | 0.10529 | 0.13733 | -122.1222 | 0.027466 | -0.01831 | -122.0764 | 0.14649 | 0.041199 | 0.059509 | -122.0993 | 0.20599 | 0.11902 | 0.082398 | -122.2733 | 0.1648 | 0.14191 | 0.15564 | -122.2595
4720.8125 | 122.2366 | -0.14648 | 122.1451 | -0.26428 | 0.045273 | 0.059473 | 0.0053235 | 0.030824 | -0.0064492 | 0.029151 | -0.19958 | 0.012525 | 0.036241 | 0.075091 | -0.0015317 | 0.056198 | 0.027466 | 0.041199 | 0.013733 | 0.013733 | 0.054932 | -0.018311 | -0.15564 | 0.018311 | 0.018311 | -0.068665 | 0.018311 | 0.027466 | -0.10071 | -0.14648 | 0.12817 | -0.009156 | -122.0901 | 0.18768 | 0.16022 | 0.16937 | -122.1176 | 0.045776 | 0 | -122.1268 | 0.16479 | 0.077819 | 0.077819 | -122.1176 | 0.20142 | 0.17395 | 0.16022 | -122.3007 | 0.16479 | 0.17395 | 0.16479 | -122.2916
4722.6094 | 122.3648 | -0.10529 | 122.1176 | -0.0048827 | 0.046341 | 0.060541 | 0.0046827 | 0.029115 | -0.0070902 | 0.028724 | 0.036926 | 0.012097 | 0.03325 | 0.077654 | -0.0021725 | 0.056411 | -0.009155 | 0.018311 | 0.027466 | 0.009155 | 0.050354 | 0.004578 | -0.14648 | 0.059509 | 0.054932 | -0.022888 | -0.009155 | -0.018311 | -0.07782 | -0.11444 | 0.10986 | -0.041198 | -122.0673 | 0.1236 | 0.11444 | 0.15564 | -122.1268 | 0.027466 | -0.009155 | -122.1268 | 0.16479 | 0.082398 | 0.091553 | -122.1359 | 0.15564 | 0.096131 | 0.13275 | -122.2641 | 0.096131 | 0.086975 | 0.16022 | -122.2321
4724.3125 | 122.3785 | -0.10071 | 122.0901 | -0.0048827 | 0.04506 | 0.061609 | 0.0040417 | 0.026551 | -0.0064492 | 0.028083 | 0.014038 | 0.012525 | 0.031969 | 0.076372 | 0.00060451 | 0.055984 | -0.013733 | 0.013733 | 0.013733 | -0.004578 | 0.054932 | -0.018311 | -0.14648 | 0.059509 | 0.073242 | -0.022888 | 0.013733 | -0.009155 | -0.073242 | -0.12817 | 0.082397 | -0.045776 | -122.0352 | 0.11444 | 0.09613 | 0.14191 | -122.1039 | 0.027466 | -0.027466 | -122.0764 | 0.16022 | 0.07782 | 0.10529 | -122.0993 | 0.15564 | 0.086975 | 0.11444 | -122.2366 | 0.11444 | 0.091553 | 0.17395 | -122.2183
4726.0781 | 122.2916 | -0.12817 | 122.113 | -0.18799 | 0.050186 | 0.060327 | 0.0031873 | 0.029542 | 0.0029502 | 0.028724 | -0.26062 | 0.014234 | 0.032823 | 0.079149 | 0.0031681 | 0.053207 | 0 | -0.013733 | -0.050354 | -0.022888 | 0.086975 | -0.036621 | -0.18768 | 0.013733 | 0.013733 | -0.10071 | 0.022888 | 0.013733 | -0.09613 | -0.14191 | 0.091553 | -0.059509 | -122.0261 | 0.11444 | 0.10529 | 0.16479 | -122.113 | 0.032044 | -0.013733 | -122.0901 | 0.14191 | 0.027466 | 0.041199 | -122.0993 | 0.21515 | 0.12817 | 0.07782 | -122.3007 | 0.15106 | 0.14191 | 0.14191 | -122.2549
4727.8594 | 122.2412 | -0.15106 | 122.1542 | -0.27191 | 0.050186 | 0.062677 | 0.0066053 | 0.028901 | -0.0034586 | 0.030006 | -0.10803 | 0.015302 | 0.035814 | 0.07979 | -0.00067729 | 0.055343 | -0.013733 | 0.018311 | -0.027466 | -0.018311 | 0.050354 | -0.018311 | -0.16937 | -0.013733 | 0 | -0.11444 | 0.050354 | 0.013733 | -0.10529 | -0.15564 | 0.13275 | -0.018311 | -122.1039 | 0.16937 | 0.13275 | 0.15106 | -122.168 | 0.045776 | -0.004578 | -122.1039 | 0.13733 | 0.036621 | 0.041199 | -122.1405 | 0.20142 | 0.13733 | 0.1236 | -122.3236 | 0.20142 | 0.16479 | 0.15106 | -122.3099
4729.6406 | 122.3236 | -0.10071 | 122.049 | 0.14008 | 0.046341 | 0.060754 | 0.00019645 | 0.029115 | -0.0021768 | 0.03086 | 0.15137 | 0.013593 | 0.032823 | 0.07744 | 0.0042361 | 0.05812 | 0.073242 | 0.086975 | 0.073242 | 0.041199 | 0.013733 | 0.004578 | -0.13275 | 0.13275 | 0.10986 | 0 | -0.036621 | -0.050354 | -0.054932 | -0.10071 | 0.10529 | -0.032043 | -122.0352 | 0.18768 | 0.14191 | 0.17395 | -121.9757 | 0.045776 | 0 | -122.0856 | 0.23346 | 0.10071 | 0.10071 | -122.0993 | 0.11444 | 0.17395 | 0.17395 | -122.1817 | 0.064087 | 0.050354 | 0.21057 | -122.1497
4731.4062 | 122.3053 | -0.1236 | 122.0856 | 0.10193 | 0.049118 | 0.059686 | 0.00019645 | 0.028688 | -4.058e-05 | 0.031501 | 0.029297 | 0.018079 | 0.033037 | 0.081072 | 0.0057315 | 0.057052 | -0.018311 | -0.054932 | -0.07782 | -0.054932 | 0.082397 | -0.022888 | -0.17395 | 0.013733 | -0.036621 | -0.1236 | 0.027466 | 0.018311 | -0.09613 | -0.14191 | 0.10071 | -0.050354 | -122.0032 | 0.068664 | 0.068664 | 0.11902 | -122.1039 | 0.027466 | -0.018311 | -122.0581 | 0.13733 | 0 | 0.018311 | -122.0673 | 0.20599 | 0.10528 | 0.045776 | -122.2595 | 0.15106 | 0.14191 | 0.086975 | -122.2275
4733.1094 | 122.3099 | -0.10071 | 122.113 | 0.079041 | 0.043137 | 0.062677 | -0.00023075 | 0.027192 | -0.0073038 | 0.028297 | 0.11322 | 0.013166 | 0.035387 | 0.078936 | 0.00017731 | 0.062393 | 0.022888 | 0.059509 | 0.036621 | 0 | 0.013733 | 0 | -0.12817 | 0.050354 | 0.059509 | -0.041199 | -0.009155 | -0.018311 | -0.07782 | -0.1236 | 0.10071 | -0.027466 | -122.0993 | 0.16022 | 0.10071 | 0.12817 | -122.0901 | 0.022888 | -0.022888 | -122.1222 | 0.15106 | 0.059509 | 0.082397 | -122.1313 | 0.11444 | 0.1236 | 0.13733 | -122.2412 | 0.091553 | 0.082397 | 0.16022 | -122.2366
4734.8125 | 122.3007 | -0.11444 | 122.0764 | 0.11719 | 0.046128 | 0.061182 | 0.00019645 | 0.029115 | -0.0058084 | 0.027656 | 0.097962 | 0.013379 | 0.031969 | 0.078936 | 0.0014591 | 0.059616 | 0.068665 | 0.082397 | 0.068665 | 0.032043 | 0.027466 | 0.013733 | -0.10986 | 0.10986 | 0.091553 | -0.013733 | -0.022888 | -0.032043 | -0.068665 | -0.10986 | 0.12817 | 0.004578 | -122.0489 | 0.19684 | 0.14648 | 0.14191 | -122.0078 | 0.045776 | 0.004578 | -122.0993 | 0.2243 | 0.10071 | 0.09613 | -122.1085 | 0.14191 | 0.18311 | 0.18311 | -122.1863 | 0.091553 | 0.082398 | 0.20599 | -122.1863
4736.5625 | 122.2824 | -0.1236 | 122.113 | -0.19562 | 0.046555 | 0.062463 | 0.0078871 | 0.030183 | -0.0073038 | 0.029151 | -0.16144 | 0.012525 | 0.034318 | 0.080645 | 0.00017731 | 0.060043 | 0.064087 | 0.091553 | 0.07782 | 0.050354 | 0.018311 | 0.009155 | -0.12817 | 0.086975 | 0.13275 | -0.018311 | -0.013733 | -0.018311 | -0.059509 | -0.11902 | 0.13275 | -0.004578 | -122.0947 | 0.21515 | 0.17395 | 0.17853 | -122.049 | 0.064087 | 0.004577 | -122.1268 | 0.21057 | 0.10528 | 0.10071 | -122.1313 | 0.14191 | 0.18768 | 0.20142 | -122.2412 | 0.10986 | 0.10528 | 0.25635 | -122.2321
4738.3281 | 122.3648 | -0.09613 | 122.0673 | -0.096436 | 0.047837 | 0.06225 | 0.0034009 | 0.027619 | -0.004313 | 0.025947 | -0.092773 | 0.012952 | 0.032823 | 0.080858 | -0.00046349 | 0.060257 | 0.050354 | 0.10071 | 0.073242 | 0.045776 | 0.022888 | 0.018311 | -0.13733 | 0.1236 | 0.13733 | 0.013733 | -0.018311 | -0.045776 | -0.068665 | -0.10071 | 0.11444 | -0.041199 | -122.0444 | 0.19684 | 0.14191 | 0.18311 | -122.0169 | 0.027465 | -0.004578 | -122.0856 | 0.21973 | 0.10986 | 0.11444 | -122.113 | 0.11902 | 0.14648 | 0.16937 | -122.2046 | 0.077819 | 0.050354 | 0.23346 | -122.168
4740.0312 | 122.3648 | -0.10986 | 122.0856 | -0.10406 | 0.044205 | 0.058832 | 0.0048963 | 0.028047 | -0.0073038 | 0.026801 | -0.1004 | 0.01402 | 0.03325 | 0.078722 | -0.0011045 | 0.059188 | 0.068665 | 0.09613 | 0.07782 | 0.027466 | 0.032043 | 0.018311 | -0.15106 | 0.13733 | 0.15564 | 0.036621 | -0.009155 | -0.018311 | -0.068665 | -0.11444 | 0.12817 | -0.041199 | -122.0535 | 0.20599 | 0.13733 | 0.17853 | -122.0169 | 0.041198 | -0.004578 | -122.0947 | 0.24719 | 0.14648 | 0.15106 | -122.1039 | 0.14191 | 0.17853 | 0.18768 | -122.2366 | 0.10071 | 0.091552 | 0.2655 | -122.2
4741.7812 | 122.2641 | -0.14191 | 122.113 | -0.25665 | 0.04805 | 0.059686 | 0.0044691 | 0.02826 | -0.0013224 | 0.027228 | -0.27588 | 0.015302 | 0.0356 | 0.083208 | 0.00060451 | 0.059829 | -0.022888 | -0.050354 | -0.059509 | -0.041199 | 0.068665 | -0.036621 | -0.17395 | -0.018311 | -0.009155 | -0.14648 | 0.032043 | 0.018311 | -0.10529 | -0.16022 | 0.10529 | -0.032043 | -122.0444 | 0.091553 | 0.10071 | 0.13275 | -122.1359 | 0.036621 | -0.01831 | -122.081 | 0.1236 | -0.004577 | 0.013733 | -122.0947 | 0.21057 | 0.11902 | 0.082398 | -122.287 | 0.17395 | 0.16022 | 0.13275 | -122.2733
4743.4844 | 122.2549 | -0.13275 | 122.1313 | -0.21851 | 0.051682 | 0.059259 | 0.0048963 | 0.031251 | -0.0013224 | 0.028297 | -0.24536 | 0.017652 | 0.036027 | 0.083849 | 0.0010317 | 0.061111 | -0.027466 | -0.032043 | -0.073242 | -0.041199 | 0.082397 | -0.059509 | -0.1831 | 0.004578 | 0 | -0.1236 | 0.022888 | 0.022888 | -0.12817 | -0.16937 | 0.073242 | -0.050354 | -122.049 | 0.10071 | 0.091552 | 0.14191 | -122.1588 | 0.004577 | -0.036622 | -122.1085 | 0.13733 | 0.009155 | 0.045777 | -122.1085 | 0.21515 | 0.10529 | 0.059509 | -122.3145 | 0.15564 | 0.15564 | 0.13275 | -122.3007
4745.25 | 122.2229 | -0.15106 | 122.081 | 0.040894 | 0.049973 | 0.060541 | -0.0015125 | 0.029115 | 0.001882 | 0.029365 | 0.014038 | 0.017438 | 0.033678 | 0.083849 | 0.0038089 | 0.062179 | -0.050354 | -0.054932 | -0.091553 | -0.050354 | 0.059509 | -0.027466 | -0.16479 | 0 | -0.054932 | -0.15106 | 0.018311 | 0.022888 | -0.09613 | -0.13275 | 0.1236 | -0.013733 | -122.0215 | 0.09613 | 0.10071 | 0.11444 | -122.1313 | 0.054932 | 0.018311 | -122.0627 | 0.15106 | 0 | -0.018311 | -122.0581 | 0.21057 | 0.10071 | 0.059509 | -122.2458 | 0.16937 | 0.17395 | 0.09613 | -122.2137
4747.0156 | 122.319 | -0.09613 | 122.0535 | 0.11719 | 0.046128 | 0.058405 | -1.7146e-05 | 0.028047 | -0.0053812 | 0.031287 | 0.16663 | 0.015729 | 0.030046 | 0.082995 | 0.0044497 | 0.063461 | 0.059509 | 0.07782 | 0.059509 | 0.054932 | 0.018311 | 0.018311 | -0.12817 | 0.11902 | 0.10071 | 0.004578 | -0.027466 | -0.027466 | -0.07782 | -0.1236 | 0.11444 | -0.032044 | -122.0352 | 0.17395 | 0.15106 | 0.18311 | -121.994 | 0.01831 | -0.027466 | -122.081 | 0.21515 | 0.10071 | 0.12817 | -122.081 | 0.11444 | 0.15564 | 0.15564 | -122.1817 | 0.068664 | 0.068664 | 0.19684 | -122.1771
4748.7969 | 122.2595 | -0.14191 | 122.0993 | -0.1651 | 0.048691 | 0.06225 | 0.00041005 | 0.030824 | -0.002604 | 0.029151 | -0.1767 | 0.014447 | 0.033464 | 0.086199 | 0.0031681 | 0.06282 | 0.013733 | -0.009155 | -0.018311 | 0 | 0.068665 | -0.027466 | -0.1831 | 0.032043 | 0.059509 | -0.09613 | 0.027466 | 0.018311 | -0.09613 | -0.15564 | 0.11444 | -0.041198 | -122.0306 | 0.13275 | 0.14191 | 0.1831 | -122.0856 | 0.045777 | -0.013733 | -122.0718 | 0.17395 | 0.045777 | 0.05951 | -122.081 | 0.21057 | 0.15564 | 0.1236 | -122.2824 | 0.16937 | 0.16022 | 0.20142 | -122.2549
4750.5 | 122.2275 | -0.15564 | 122.1359 | -0.21088 | 0.048905 | 0.0599 | 0.0085279 | 0.029328 | -0.0051676 | 0.029365 | -0.24536 | 0.014661 | 0.034105 | 0.085345 | -0.0028135 | 0.063461 | -0.050354 | -0.036621 | -0.059509 | -0.059509 | 0.082397 | -0.036621 | -0.17853 | -0.009155 | 0.004578 | -0.11444 | 0.036621 | 0.022888 | -0.10986 | -0.16022 | 0.11902 | -0.022888 | -122.0535 | 0.11902 | 0.096131 | 0.11902 | -122.1863 | 0.045777 | -0.004577 | -122.0993 | 0.14649 | 0.041199 | 0.045776 | -122.113 | 0.23804 | 0.10529 | 0.096131 | -122.3145 | 0.19226 | 0.17853 | 0.16022 | -122.2961
4752.2656 | 122.2961 | -0.1236 | 122.0856 | 0.079041 | 0.047623 | 0.059473 | 0.0061781 | 0.029328 | -0.0070902 | 0.03086 | 0.097962 | 0.013593 | 0.034532 | 0.084917 | -0.0023861 | 0.06517 | 0.022888 | 0.041199 | 0.036621 | 0.009155 | 0.013733 | -0.004578 | -0.1236 | 0.054932 | 0.054932 | -0.041199 | -0.004578 | -0.027466 | -0.068665 | -0.11902 | 0.11902 | 0 | -122.0718 | 0.16479 | 0.13275 | 0.13275 | -122.0627 | 0.054931 | 0.004577 | -122.0901 | 0.17853 | 0.082397 | 0.07782 | -122.113 | 0.13733 | 0.14648 | 0.16022 | -122.2092 | 0.11902 | 0.09613 | 0.17853 | -122.2046
4754.0312 | 122.2961 | -0.11902 | 122.0947 | -0.18036 | 0.049973 | 0.061609 | 0.0027601 | 0.027406 | -0.0053812 | 0.027442 | -0.14618 | 0.011029 | 0.033891 | 0.084276 | 0.00039091 | 0.064743 | 0.050354 | 0.11444 | 0.086975 | 0.050354 | 0.041199 | 0.013733 | -0.13275 | 0.09613 | 0.14191 | 0.009155 | -0.018311 | -0.018311 | -0.068665 | -0.1236 | 0.13275 | -0.013732 | -122.0535 | 0.23346 | 0.16937 | 0.18311 | -122.0444 | 0.050354 | -0.004577 | -122.113 | 0.21515 | 0.12817 | 0.13275 | -122.113 | 0.16022 | 0.16937 | 0.20599 | -122.2275 | 0.10071 | 0.10071 | 0.26093 | -122.2183
4755.7344 | 122.2916 | -0.10986 | 122.0535 | 0.10193 | 0.044205 | 0.060327 | -1.7146e-05 | 0.028474 | -0.002604 | 0.029578 | 0.10559 | 0.013379 | 0.034532 | 0.084063 | 0.00039091 | 0.06752 | 0.050354 | 0.10071 | 0.054932 | 0.013733 | 0.032043 | 0.027466 | -0.13733 | 0.10529 | 0.082397 | 0 | -0.009155 | -0.022888 | -0.045776 | -0.12817 | 0.13733 | -0.027466 | -122.0215 | 0.21057 | 0.1236 | 0.15106 | -122.0032 | 0.064087 | -0.018311 | -122.0627 | 0.21515 | 0.10986 | 0.12817 | -122.0764 | 0.14191 | 0.16022 | 0.16479 | -122.1909 | 0.10071 | 0.086975 | 0.19226 | -122.1817
4757.5 | 122.2137 | -0.14191 | 122.0856 | -0.18036 | 0.046768 | 0.061823 | 0.0025465 | 0.029756 | -0.004954 | 0.028297 | -0.19196 | 0.015729 | 0.034105 | 0.08684 | 0.0027407 | 0.066665 | 0.050354 | 0.086975 | 0.073242 | 0.032043 | 0.041199 | -0.004578 | -0.13275 | 0.054932 | 0.09613 | -0.032043 | -0.004578 | 0 | -0.082397 | -0.13275 | 0.13733 | 0.009156 | -122.0444 | 0.22888 | 0.17395 | 0.16479 | -122.0352 | 0.05951 | 0.009156 | -122.0901 | 0.19684 | 0.10986 | 0.10071 | -122.0856 | 0.18311 | 0.19226 | 0.21515 | -122.2183 | 0.13733 | 0.14191 | 0.23804 | -122.2183
4759.25 | 122.2229 | -0.14648 | 122.0764 | -0.24902 | 0.048905 | 0.062036 | 0.0048963 | 0.031251 | -0.0011088 | 0.029578 | -0.26825 | 0.015088 | 0.036668 | 0.090471 | 0.0010317 | 0.066024 | -0.027466 | -0.041199 | -0.068665 | -0.050354 | 0.068665 | -0.041199 | -0.1831 | -0.022888 | -0.018311 | -0.12817 | 0.041199 | 0.004578 | -0.11444 | -0.16937 | 0.10529 | -0.036621 | -122.0078 | 0.10529 | 0.09613 | 0.13275 | -122.1039 | 0.032043 | -0.022889 | -122.0352 | 0.1236 | 0.01831 | 0.041199 | -122.0718 | 0.21515 | 0.11902 | 0.077819 | -122.2595 | 0.18768 | 0.15106 | 0.12817 | -122.2458
4761.0156 | 122.3099 | -0.13275 | 122.0306 | -0.0048827 | 0.044419 | 0.060968 | 0.0029737 | 0.029328 | -0.0058084 | 0.028297 | 0.021668 | 0.012311 | 0.034105 | 0.091326 | -0.00046349 | 0.071579 | -0.009155 | 0.032043 | 0.027466 | -0.004578 | 0.050354 | 0.004578 | -0.15564 | 0.050354 | 0.054932 | -0.041199 | -0.009155 | -0.018311 | -0.086975 | -0.13733 | 0.13733 | -0.022889 | -121.9803 | 0.16479 | 0.12817 | 0.15106 | -122.0398 | 0.045776 | -0.004578 | -122.0398 | 0.18311 | 0.091552 | 0.09613 | -122.049 | 0.18311 | 0.1236 | 0.16022 | -122.1863 | 0.1236 | 0.11444 | 0.18768 | -122.168
4762.7969 | 122.1909 | -0.15106 | 122.0581 | 0.040894 | 0.049546 | 0.059259 | 0.0019055 | 0.029969 | 0.0016684 | 0.02851 | -0.031738 | 0.017438 | 0.03261 | 0.09154 | 0.0040225 | 0.067947 | -0.027466 | -0.07782 | -0.082397 | -0.054932 | 0.073242 | -0.032043 | -0.17395 | -0.018311 | -0.054932 | -0.14648 | 0.032043 | 0.004578 | -0.10071 | -0.16022 | 0.11902 | -0.022888 | -121.9849 | 0.073242 | 0.09613 | 0.11902 | -122.0856 | 0.050354 | -0.009155 | -122.0261 | 0.13275 | 0.004578 | 0.013733 | -122.0535 | 0.2243 | 0.1236 | 0.068665 | -122.2321 | 0.18311 | 0.15564 | 0.09613 | -122.2183
4764.5625 | 122.2916 | -0.1236 | 122.0352 | -0.1651 | 0.046128 | 0.060968 | 0.0040417 | 0.029328 | -0.0075174 | 0.027869 | -0.16144 | 0.014661 | 0.035173 | 0.090899 | -0.0015317 | 0.071365 | 0.050354 | 0.13275 | 0.068665 | 0.045776 | 0.027466 | 0.013733 | -0.14648 | 0.09613 | 0.14648 | 0.027466 | -0.013733 | -0.027466 | -0.054932 | -0.13275 | 0.13733 | -0.022888 | -122.0078 | 0.25635 | 0.16937 | 0.19226 | -121.9849 | 0.068664 | -0.009155 | -122.049 | 0.21973 | 0.15106 | 0.16022 | -122.0627 | 0.15106 | 0.17395 | 0.19226 | -122.1817 | 0.10986 | 0.09613 | 0.27008 | -122.168
4766.2656 | 117.9977 | -0.10986 | 117.8375 | 0.10193 | 0.046768 | 0.060968 | -0.00044435 | 0.027619 | -0.00068138 | 0.031287 | 0.036926 | 0.018506 | 0.034532 | 0.11653 | 0.0046633 | 0.094436 | -0.032043 | -0.050354 | -0.07782 | -0.045776 | 0.073242 | -0.032043 | -0.16022 | 0.022888 | -0.036621 | -0.14191 | 0.027466 | 0.013733 | -0.11444 | -0.16022 | 0.07782 | -0.050354 | -117.7643 | 0.059509 | 0.064087 | 0.11444 | -117.8696 | -0.004578 | -0.050354 | -117.8101 | 0.13275 | -0.032044 | 0.01831 | -117.8238 | 0.18311 | 0.07782 | 0.032043 | -117.9977 | 0.13733 | 0.1236 | 0.073242 | -117.9977
4768.0312 | 122.1313 | -0.15564 | 122.049 | -0.020142 | 0.0504 | 0.060327 | 0.0010511 | 0.028688 | -0.0011088 | 0.031714 | -0.046997 | 0.017224 | 0.033678 | 0.091326 | 0.0042361 | 0.070724 | -0.013733 | -0.032043 | -0.054932 | -0.041199 | 0.054932 | -0.018311 | -0.16937 | -0.004578 | -0.018311 | -0.14648 | 0.018311 | 0.009155 | -0.091553 | -0.16479 | 0.13733 | -0.013733 | -121.994 | 0.1236 | 0.11444 | 0.12817 | -122.0627 | 0.064087 | -0.009155 | -122.0306 | 0.15106 | 0.009156 | 0.018311 | -122.0398 | 0.21057 | 0.14191 | 0.10071 | -122.2183 | 0.17395 | 0.16479 | 0.13733 | -122.2137
4769.8125 | 122.1725 | -0.16022 | 122.0673 | 0.040894 | 0.049546 | 0.059473 | 0.0016919 | 0.028901 | -0.0013224 | 0.030006 | 0.014038 | 0.018292 | 0.034318 | 0.093249 | 0.0042361 | 0.06987 | -0.054932 | -0.050354 | -0.068665 | -0.045776 | 0.068665 | -0.032043 | -0.16022 | -0.032043 | -0.064087 | -0.16479 | 0.027466 | 0.041199 | -0.10986 | -0.16022 | 0.12817 | 0 | -121.9986 | 0.10986 | 0.11444 | 0.11444 | -122.1222 | 0.050354 | 0 | -122.0398 | 0.12817 | -0.004578 | -0.004578 | -122.0261 | 0.22888 | 0.10528 | 0.091552 | -122.2275 | 0.18768 | 0.20142 | 0.09613 | -122.2275
4771.5156 | 122.2137 | -0.13275 | 122.0718 | -0.21088 | 0.047623 | 0.062677 | 0.0072461 | 0.029969 | -0.0079446 | 0.031287 | -0.12329 | 0.013593 | 0.032823 | 0.093249 | -0.0011045 | 0.074356 | 0.027466 | 0.1236 | 0.091553 | 0.050354 | 0.022888 | 0.004578 | -0.14191 | 0.086975 | 0.13275 | 0.013733 | -0.032043 | -0.009155 | -0.064087 | -0.13275 | 0.13733 | -0.009156 | -122.049 | 0.25635 | 0.18311 | 0.19226 | -122.0444 | 0.068664 | 0 | -122.1039 | 0.21973 | 0.14648 | 0.14648 | -122.081 | 0.15564 | 0.16022 | 0.2243 | -122.2137 | 0.10071 | 0.1236 | 0.2655 | -122.2046
4773.2812 | 122.2504 | -0.11902 | 122.0306 | 0.15533 | 0.0457 | 0.060327 | 0.0036145 | 0.029969 | -0.0019632 | 0.029365 | 0.15137 | 0.014661 | 0.033037 | 0.093889 | 0.00060451 | 0.073288 | 0.068665 | 0.082397 | 0.082397 | 0.032043 | 0.009155 | 0.022888 | -0.11444 | 0.11444 | 0.10529 | 0.013733 | -0.013733 | -0.032043 | -0.07782 | -0.1236 | 0.14191 | 0.004578 | -122.0215 | 0.20142 | 0.15106 | 0.14648 | -121.962 | 0.041199 | -0.004577 | -122.0444 | 0.23346 | 0.13275 | 0.13733 | -122.0627 | 0.12817 | 0.18768 | 0.20142 | -122.1451 | 0.10529 | 0.086976 | 0.22431 | -122.1542
4775.0625 | 122.1405 | -0.14191 | 122.0306 | -0.096436 | 0.048477 | 0.060114 | 0.00019645 | 0.029969 | 0.0016684 | 0.029792 | -0.10803 | 0.016797 | 0.033464 | 0.097521 | 0.0046633 | 0.070724 | 0.050354 | 0.018311 | -0.018311 | -0.004578 | 0.07782 | -0.027466 | -0.15564 | 0.018311 | 0.032043 | -0.091553 | -0.004578 | 0.018311 | -0.10071 | -0.14648 | 0.11444 | -0.013733 | -121.9528 | 0.16022 | 0.13733 | 0.15106 | -121.9803 | 0.041199 | -0.004577 | -122.0352 | 0.16022 | 0.050354 | 0.054931 | -122.0123 | 0.21973 | 0.19226 | 0.1236 | -122.1863 | 0.13733 | 0.16022 | 0.17395 | -122.1771
4776.7656 | 122.1634 | -0.13733 | 122.0261 | -0.23376 | 0.0504 | 0.060754 | 0.0063917 | 0.028901 | -0.0064492 | 0.028083 | -0.2301 | 0.013593 | 0.034105 | 0.097094 | -0.0013181 | 0.075424 | -0.050354 | -0.045776 | -0.068665 | -0.045776 | 0.068665 | -0.022888 | -0.17853 | -0.032043 | -0.004578 | -0.1236 | 0.027466 | 0.032043 | -0.10529 | -0.16022 | 0.11444 | -0.041199 | -121.9574 | 0.091553 | 0.091553 | 0.13275 | -122.0764 | 0.032043 | -0.022888 | -121.9986 | 0.10529 | 0.013733 | 0.036621 | -121.994 | 0.20599 | 0.086975 | 0.068664 | -122.2046 | 0.16479 | 0.16937 | 0.13275 | -122.1863
4778.5312 | 122.1771 | -0.1236 | 121.9345 | 0.0027468 | 0.048264 | 0.059045 | 0.0048963 | 0.031678 | -0.0090128 | 0.028937 | 0.052185 | 0.010175 | 0.034959 | 0.097521 | -0.0013181 | 0.076492 | -0.027466 | 0.036621 | 0.045776 | 0 | 0.041199 | 0.009155 | -0.14191 | 0.041199 | 0.054932 | -0.036621 | 0.004578 | -0.022888 | -0.09613 | -0.13275 | 0.13275 | -0.018311 | -121.8933 | 0.16022 | 0.1236 | 0.14191 | -121.962 | 0.027466 | -0.009155 | -121.9299 | 0.16479 | 0.086975 | 0.09613 | -121.9574 | 0.16479 | 0.09613 | 0.16937 | -122.0764 | 0.12817 | 0.10071 | 0.17853 | -122.0673
4780.2344 | 122.2458 | -0.10986 | 121.9528 | 0.10193 | 0.051041 | 0.0599 | 0.0025465 | 0.029542 | -0.0021768 | 0.028724 | 0.14374 | 0.016584 | 0.033891 | 0.099444 | 0.0050907 | 0.076919 | 0.004578 | -0.032043 | -0.036621 | -0.032043 | 0.059509 | -0.027466 | -0.15564 | 0.064087 | 0.009155 | -0.082397 | 0.018311 | 0 | -0.073242 | -0.14191 | 0.082397 | -0.045777 | -121.8933 | 0.07782 | 0.07782 | 0.1236 | -121.9482 | 0.036621 | -0.032044 | -121.9345 | 0.17395 | 0.027466 | 0.05951 | -121.9528 | 0.16937 | 0.11444 | 0.073242 | -122.1085 | 0.12817 | 0.10986 | 0.11902 | -122.0947
4782 | 122.1222 | -0.15564 | 121.994 | -0.27954 | 0.047623 | 0.062036 | 0.0040417 | 0.030183 | -0.0053812 | 0.027228 | -0.18433 | 0.012738 | 0.034532 | 0.094958 | -0.0011045 | 0.077774 | 0 | 0.027466 | -0.004578 | 0 | 0.064087 | -0.004578 | -0.16022 | -0.004578 | 0.018311 | -0.091553 | 0.032043 | 0.018311 | -0.09613 | -0.15564 | 0.15106 | -0.004577 | -121.9299 | 0.18311 | 0.15564 | 0.16022 | -121.994 | 0.05951 | 0 | -121.962 | 0.15106 | 0.064087 | 0.064087 | -121.9757 | 0.21973 | 0.15564 | 0.15106 | -122.1542 | 0.18768 | 0.17395 | 0.17395 | -122.1497
4783.7656 | 122.113 | -0.14191 | 121.9391 | -0.17273 | 0.050827 | 0.058618 | 0.0040417 | 0.03061 | -0.00046778 | 0.029365 | -0.23773 | 0.013593 | 0.034318 | 0.1003 | 0.0016727 | 0.075637 | -0.027466 | -0.032043 | -0.041199 | -0.032043 | 0.050354 | -0.013733 | -0.17395 | -0.013733 | 0.022888 | -0.10529 | 0.027466 | 0.018311 | -0.10529 | -0.15106 | 0.12817 | -0.032043 | -121.8887 | 0.10986 | 0.10986 | 0.14191 | -121.9666 | 0.036621 | -0.009155 | -121.9116 | 0.12817 | 0.036621 | 0.045776 | -121.9208 | 0.19226 | 0.11444 | 0.10071 | -122.113 | 0.16937 | 0.16022 | 0.16479 | -122.0901
4785.4531 | 122.1222 | -0.11444 | 121.8704 | 0.14008 | 0.046341 | 0.060327 | -0.0025805 | 0.02826 | -0.006022 | 0.029365 | 0.16663 | 0.014661 | 0.031541 | 0.099657 | 0.0025271 | 0.080124 | 0.045776 | 0.10071 | 0.064087 | 0.045776 | 0.022888 | 0.027466 | -0.1236 | 0.10986 | 0.091553 | 0.013733 | -0.032043 | -0.041199 | -0.068665 | -0.1236 | 0.14191 | -0.009155 | -121.8475 | 0.21515 | 0.16022 | 0.16937 | -121.8246 | 0.045776 | -0.009155 | -121.9025 | 0.2243 | 0.12817 | 0.13733 | -121.9116 | 0.13733 | 0.16022 | 0.17853 | -121.994 | 0.082398 | 0.073242 | 0.20599 | -121.994
4787.2188 | 121.9391 | -0.1236 | 121.788 | -0.10406 | 0.052109 | 0.060754 | 0.0036145 | 0.031037 | 0.00060022 | 0.030006 | -0.15381 | 0.014661 | 0.034959 | 0.10265 | 0.0018863 | 0.078415 | 0.027466 | 0.018311 | -0.013733 | 0 | 0.045776 | -0.018311 | -0.1831 | 0.050354 | 0.036621 | -0.091553 | 0.027466 | 0 | -0.09613 | -0.15564 | 0.10528 | -0.059509 | -121.7422 | 0.14191 | 0.1236 | 0.1831 | -121.7606 | 0.027466 | -0.032044 | -121.7606 | 0.17395 | 0.032043 | 0.064087 | -121.788 | 0.16937 | 0.15106 | 0.10986 | -121.9711 | 0.15106 | 0.1236 | 0.16022 | -121.9437
4788.9219 | 121.9254 | -0.086975 | 121.7377 | 0.12482 | 0.046768 | 0.058832 | 0.00062385 | 0.031892 | -0.0073038 | 0.029151 | 0.18188 | 0.014234 | 0.031755 | 0.099871 | 0.0040225 | 0.081405 | 0.059509 | 0.07782 | 0.059509 | 0.050354 | 0.022888 | 0.027466 | -0.14191 | 0.10071 | 0.086975 | -0.009155 | -0.022888 | -0.032043 | -0.073242 | -0.10986 | 0.11444 | -0.054932 | -121.7148 | 0.16479 | 0.13733 | 0.19226 | -121.6782 | 0.013733 | -0.022888 | -121.7606 | 0.18768 | 0.07782 | 0.10071 | -121.7697 | 0.10986 | 0.14648 | 0.14648 | -121.8796 | 0.064087 | 0.054932 | 0.17395 | -121.8475
4790.6875 | 121.8384 | -0.091553 | 121.55 | -0.14221 | 0.047837 | 0.058832 | 0.0087415 | 0.028688 | -0.010722 | 0.027656 | -0.085144 | 0.012525 | 0.036455 | 0.09923 | -0.0040951 | 0.080124 | 0.050354 | 0.12817 | 0.082397 | 0.045776 | 0.054932 | 0.004578 | -0.14648 | 0.091553 | 0.15106 | 0.013733 | 0 | -0.018311 | -0.059509 | -0.1236 | 0.096131 | -0.054931 | -121.4951 | 0.21973 | 0.13733 | 0.19226 | -121.4996 | 0.032044 | -0.032043 | -121.55 | 0.18311 | 0.10529 | 0.13733 | -121.5683 | 0.14649 | 0.14191 | 0.17395 | -121.6965 | 0.091553 | 0.073242 | 0.24261 | -121.6736
4792.4062 | 121.7102 | -0.13733 | 121.4676 | 0.071411 | 0.050827 | 0.058405 | 0.0012647 | 0.028474 | 0.0014548 | 0.029792 | 0.059815 | 0.015729 | 0.034959 | 0.10073 | 0.0055179 | 0.078628 | -0.036621 | -0.059509 | -0.073242 | -0.022888 | 0.07782 | -0.022888 | -0.16479 | 0.004578 | -0.054932 | -0.14648 | 0.041199 | -0.004578 | -0.10986 | -0.16937 | 0.11444 | -0.027466 | -121.3898 | 0.07782 | 0.11444 | 0.14191 | -121.5042 | 0.027466 | -0.032044 | -121.4264 | 0.14191 | -0.009155 | 0.022889 | -121.4722 | 0.21515 | 0.10071 | 0.064087 | -121.6324 | 0.17853 | 0.13275 | 0.082397 | -121.637
4794.1719 | 121.8613 | -0.14648 | 121.6736 | -0.21088 | 0.050186 | 0.060968 | 0.0038281 | 0.028901 | -0.0021768 | 0.030646 | -0.22247 | 0.015515 | 0.0356 | 0.10158 | 0.0020999 | 0.07991 | -0.045776 | -0.032043 | -0.054932 | -0.036621 | 0.07782 | -0.027466 | -0.17395 | -0.022888 | 0.013733 | -0.1236 | 0.022888 | 0.022888 | -0.13275 | -0.15106 | 0.11902 | -0.027466 | -121.5958 | 0.11444 | 0.10986 | 0.13733 | -121.7194 | 0.013733 | -0.004578 | -121.6507 | 0.1236 | 0.022888 | 0.027466 | -121.6507 | 0.2243 | 0.10071 | 0.091552 | -121.8475 | 0.16937 | 0.16937 | 0.16022 | -121.8246
4795.9375 | 121.9162 | -0.082397 | 121.7102 | 0.018005 | 0.041855 | 0.059473 | 0.00062385 | 0.02826 | -0.0085856 | 0.028297 | 0.052185 | 0.012097 | 0.033037 | 0.051378 | -0.00067729 | 0.034408 | -0.013733 | 0.064087 | 0.036621 | 0.018311 | 0.045776 | 0.032043 | -0.1236 | 0.073242 | 0.054932 | -0.027466 | 0.013733 | 0 | -0.054932 | -0.11444 | 0.11444 | -0.041199 | -121.6644 | 0.14648 | 0.10071 | 0.14191 | -121.7239 | 0.027465 | -0.032044 | -121.6965 | 0.15564 | 0.054931 | 0.086975 | -121.7102 | 0.12817 | 0.068664 | 0.11902 | -121.8338 | 0.09613 | 0.082397 | 0.13733 | -121.8246
4797.6406 | 121.962 | -0.11902 | 121.8109 | -0.24902 | 0.046768 | 0.059686 | 0.0046827 | 0.030397 | -0.0030314 | 0.028724 | -0.20721 | 0.017652 | 0.034105 | 0.053515 | 0.00060451 | 0.030349 | -0.027466 | -0.036621 | -0.059509 | -0.027466 | 0.082397 | -0.041199 | -0.17395 | -0.022888 | 0.013733 | -0.11444 | 0.050354 | 0.036621 | -0.10071 | -0.12817 | 0.07782 | -0.054931 | -121.7285 | 0.082398 | 0.091553 | 0.14648 | -121.8384 | 0.018311 | -0.009155 | -121.7606 | 0.096131 | 0.004578 | 0.013733 | -121.7743 | 0.20142 | 0.091553 | 0.05951 | -121.9849 | 0.16937 | 0.15564 | 0.13275 | -121.9391
4799.4219 | 122.081 | -0.073242 | 121.8246 | 0.12482 | 0.046341 | 0.060968 | 0.00041005 | 0.027192 | -0.004313 | 0.03086 | 0.11322 | 0.014234 | 0.03261 | 0.05031 | 0.0020999 | 0.031417 | 0.036621 | 0.082397 | 0.045776 | 0.027466 | 0.050354 | 0.013733 | -0.13275 | 0.10986 | 0.091553 | 0 | 0.004578 | -0.022888 | -0.036621 | -0.10529 | 0.086975 | -0.059509 | -121.7743 | 0.15564 | 0.10071 | 0.16022 | -121.788 | 0.036621 | -0.032044 | -121.8201 | 0.18311 | 0.073242 | 0.10529 | -121.8475 | 0.1236 | 0.10986 | 0.11902 | -121.9574 | 0.07782 | 0.050354 | 0.16479 | -121.9299
4801.1719 | 122.0581 | -0.07782 | 121.8338 | 0.10193 | 0.048477 | 0.060968 | -1.7146e-05 | 0.029115 | -0.0028178 | 0.029792 | 0.16663 | 0.012525 | 0.03261 | 0.051592 | 0.0014591 | 0.031845 | 0.054932 | 0.10071 | 0.082397 | 0.050354 | 0.018311 | 0.009155 | -0.10986 | 0.11902 | 0.10986 | 0.009155 | -0.022888 | -0.013733 | -0.036621 | -0.09613 | 0.086975 | -0.032043 | -121.8155 | 0.17853 | 0.12817 | 0.16022 | -121.7789 | 0.041199 | -0.01831 | -121.8567 | 0.19684 | 0.086975 | 0.10528 | -121.8475 | 0.096131 | 0.13275 | 0.16022 | -121.9437 | 0.054932 | 0.064087 | 0.18768 | -121.9299
4802.9375 | 122.113 | -0.082397 | 121.8704 | -0.012512 | 0.046555 | 0.062463 | 0.0031873 | 0.029969 | -0.0070902 | 0.029151 | 0.059815 | 0.012311 | 0.036455 | 0.05031 | -0.0015317 | 0.031417 | -0.018311 | 0.050354 | 0.022888 | 0.018311 | 0.054932 | 0.004578 | -0.14648 | 0.045776 | 0.059509 | -0.009155 | 0.022888 | 0.009155 | -0.054932 | -0.10529 | 0.086975 | -0.064087 | -121.8155 | 0.13275 | 0.10071 | 0.16479 | -121.8887 | 0.027465 | -0.022889 | -121.8475 | 0.12817 | 0.073242 | 0.096131 | -121.8613 | 0.13733 | 0.064086 | 0.10528 | -122.0169 | 0.10528 | 0.091552 | 0.14191 | -121.9757
4804.7031 | 122.1176 | -0.07782 | 121.8933 | 0.08667 | 0.046982 | 0.062463 | 0.00041005 | 0.027406 | -0.0017496 | 0.031074 | 0.044556 | 0.015515 | 0.033891 | 0.052447 | 0.0033817 | 0.031845 | 0 | -0.045776 | -0.041199 | -0.041199 | 0.086975 | -0.009155 | -0.16479 | 0.045776 | -0.013733 | -0.10529 | 0.032043 | 0.022888 | -0.07782 | -0.11902 | 0.068665 | -0.086975 | -121.8063 | 0.032044 | 0.036621 | 0.1236 | -121.8933 | 0 | -0.041199 | -121.8613 | 0.1236 | -0.027466 | 0.013733 | -121.8704 | 0.16479 | 0.07782 | 0.036621 | -122.0581 | 0.10986 | 0.10071 | 0.064087 | -122.0123
4806.4062 | 122.0261 | -0.10071 | 121.9208 | -0.10406 | 0.049546 | 0.058618 | 0.0010511 | 0.026979 | -0.0011088 | 0.031714 | -0.13855 | 0.015729 | 0.033037 | 0.053087 | 0.0048769 | 0.029281 | 0.059509 | 0.032043 | -0.013733 | -0.018311 | 0.091553 | -0.018311 | -0.16479 | 0.059509 | 0.059509 | -0.091553 | 0.027466 | 0.018311 | -0.068665 | -0.11902 | 0.082397 | -0.064087 | -121.8292 | 0.13275 | 0.082397 | 0.14648 | -121.8613 | 0.032043 | -0.018311 | -121.8933 | 0.16022 | 0.009155 | 0.027466 | -121.9025 | 0.19226 | 0.16022 | 0.086975 | -122.0856 | 0.12817 | 0.11902 | 0.16022 | -122.0398
4808.1875 | 122.0123 | -0.1236 | 121.9391 | -0.24139 | 0.04805 | 0.060541 | 0.0070325 | 0.027833 | -0.0058084 | 0.029151 | -0.19196 | 0.011884 | 0.036455 | 0.053515 | -0.0019589 | 0.032486 | 0.004578 | 0.041199 | 0.004578 | 0.013733 | 0.068665 | -0.013733 | -0.16022 | -0.004578 | 0.054932 | -0.091553 | 0.036621 | 0.041199 | -0.07782 | -0.14191 | 0.10986 | -0.036621 | -121.8704 | 0.16479 | 0.13733 | 0.17395 | -121.9345 | 0.045776 | -0.018311 | -121.9025 | 0.11902 | 0.032043 | 0.050354 | -121.8979 | 0.19226 | 0.12817 | 0.12817 | -122.0993 | 0.16022 | 0.16479 | 0.17853 | -122.081
4809.9062 | 122.0764 | -0.10071 | 121.9299 | -0.18799 | 0.046341 | 0.057336 | 0.0029737 | 0.02826 | -0.001536 | 0.030219 | -0.23773 | 0.01402 | 0.034746 | 0.053301 | 0.0010317 | 0.028854 | -0.032043 | -0.018311 | -0.054932 | -0.013733 | 0.086975 | -0.045776 | -0.16022 | 0 | 0.022888 | -0.10071 | 0.054932 | 0.009155 | -0.09613 | -0.12817 | 0.054932 | -0.059509 | -121.843 | 0.082397 | 0.086975 | 0.14648 | -121.962 | 0.004578 | -0.027466 | -121.875 | 0.10071 | 0 | 0.027466 | -121.9208 | 0.18768 | 0.068665 | 0.045776 | -122.0901 | 0.15564 | 0.10986 | 0.1236 | -122.0581
4811.6719 | 122.1222 | -0.082397 | 121.9299 | 0.094299 | 0.043351 | 0.060327 | 0.0014783 | 0.027406 | -0.0081582 | 0.031074 | 0.12085 | 0.011029 | 0.031328 | 0.054156 | -0.00046349 | 0.032913 | 0.054932 | 0.082397 | 0.054932 | 0.018311 | 0.027466 | 0.027466 | -0.13733 | 0.082397 | 0.073242 | -0.018311 | -0.004578 | -0.004578 | -0.068665 | -0.10071 | 0.10986 | -0.054932 | -121.9025 | 0.16479 | 0.10071 | 0.15564 | -121.875 | 0.013732 | -0.018311 | -121.9345 | 0.16479 | 0.064086 | 0.082397 | -121.9345 | 0.10986 | 0.13733 | 0.13733 | -122.0673 | 0.077819 | 0.077819 | 0.15564 | -122.0306
4813.375 | 122.0535 | -0.1236 | 121.9666 | -0.26428 | 0.049118 | 0.061609 | 0.0057507 | 0.028901 | -0.006022 | 0.027228 | -0.19958 | 0.013806 | 0.034959 | 0.051165 | -0.0017453 | 0.031417 | 0.032043 | 0.050354 | 0.018311 | 0.009155 | 0.054932 | -0.027466 | -0.14191 | 0.027466 | 0.050354 | -0.07782 | 0.032043 | 0.032043 | -0.07782 | -0.11902 | 0.09613 | -0.018311 | -121.9116 | 0.17395 | 0.13275 | 0.15106 | -121.9345 | 0.045776 | 0.004577 | -121.9345 | 0.15106 | 0.045776 | 0.041199 | -121.9345 | 0.17853 | 0.15564 | 0.14191 | -122.1085 | 0.15564 | 0.15564 | 0.17395 | -122.0856
4815.1406 | 122.2 | -0.082397 | 121.9208 | -0.096436 | 0.044846 | 0.0599 | 0.0034009 | 0.029115 | -0.0064492 | 0.027228 | -0.092773 | 0.011243 | 0.036241 | 0.052019 | -0.0011045 | 0.032058 | 0.059509 | 0.09613 | 0.073242 | 0.036621 | 0.045776 | 0.018311 | -0.13733 | 0.14191 | 0.14648 | 0.045776 | 0.004578 | -0.013733 | -0.050354 | -0.11444 | 0.10071 | -0.054932 | -121.875 | 0.17853 | 0.11902 | 0.17395 | -121.8613 | 0.032043 | -0.032044 | -121.9162 | 0.2243 | 0.12817 | 0.16022 | -121.9345 | 0.12817 | 0.14191 | 0.15564 | -122.0581 | 0.086975 | 0.068664 | 0.22888 | -122.0352
4816.9062 | 122.081 | -0.10986 | 122.0032 | -0.1651 | 0.04805 | 0.058405 | 0.0023329 | 0.028474 | -0.004313 | 0.028937 | -0.22247 | 0.01402 | 0.034105 | 0.053087 | 0.00017731 | 0.032272 | 0.050354 | 0.091553 | 0.068665 | 0.050354 | 0.059509 | 0.018311 | -0.15106 | 0.07782 | 0.11444 | -0.018311 | 0.022888 | 0 | -0.059509 | -0.11444 | 0.12817 | -0.041199 | -121.9437 | 0.20142 | 0.16022 | 0.20142 | -121.9528 | 0.050354 | -0.004578 | -121.9803 | 0.18768 | 0.091552 | 0.09613 | -122.0032 | 0.16937 | 0.16022 | 0.17853 | -122.1542 | 0.13275 | 0.10986 | 0.2243 | -122.1176
4818.6875 | 122.0856 | -0.10986 | 121.9849 | -0.24139 | 0.048477 | 0.060754 | 0.0034009 | 0.028688 | -0.0047404 | 0.029578 | -0.27588 | 0.014661 | 0.034532 | 0.052447 | 0.00017731 | 0.030777 | -0.022888 | -0.022888 | -0.050354 | -0.041199 | 0.07782 | -0.027466 | -0.17395 | -0.004578 | 0.013733 | -0.11444 | 0.050354 | 0.054932 | -0.091553 | -0.14191 | 0.082397 | -0.064087 | -121.907 | 0.086975 | 0.068664 | 0.13275 | -122.0078 | 0.01831 | -0.032044 | -121.9345 | 0.10529 | -0.004578 | 0.027466 | -121.9299 | 0.18768 | 0.086975 | 0.059509 | -122.1588 | 0.16022 | 0.16479 | 0.1236 | -122.1268
4820.4688 | 122.2183 | -0.07782 | 121.9482 | -0.027771 | 0.047409 | 0.060114 | 0.0057507 | 0.031251 | -0.0075174 | 0.02616 | -0.031738 | 0.01167 | 0.032823 | 0.053942 | -0.0023861 | 0.03569 | 0.009155 | 0.054932 | 0.045776 | 0.027466 | 0.054932 | 0.004578 | -0.13275 | 0.086975 | 0.11444 | 0.009155 | 0.018311 | -0.013733 | -0.059509 | -0.10529 | 0.082398 | -0.054931 | -121.8933 | 0.13275 | 0.10529 | 0.16022 | -121.9391 | 0.018311 | -0.027466 | -121.9299 | 0.16479 | 0.086975 | 0.11444 | -121.962 | 0.13275 | 0.086975 | 0.1236 | -122.081 | 0.096131 | 0.064087 | 0.19226 | -122.0535
4822.1875 | 122.1039 | -0.1236 | 121.9757 | 0.071411 | 0.047623 | 0.05755 | -0.0010851 | 0.03061 | 0.0020956 | 0.029792 | 0.044556 | 0.015729 | 0.032182 | 0.056719 | 0.0044497 | 0.031204 | -0.004578 | -0.054932 | -0.059509 | -0.027466 | 0.086975 | -0.009155 | -0.15106 | 0.018311 | -0.045776 | -0.13275 | 0.054932 | 0.027466 | -0.064087 | -0.11902 | 0.11444 | -0.027466 | -121.8887 | 0.068664 | 0.09613 | 0.1236 | -121.9803 | 0.059509 | 0.004577 | -121.9208 | 0.14191 | -0.009155 | -0.013732 | -121.9482 | 0.21057 | 0.11902 | 0.064087 | -122.1268 | 0.17853 | 0.15106 | 0.07782 | -122.0947
4823.9688 | 122.2092 | -0.07782 | 121.9437 | -0.12695 | 0.045914 | 0.059473 | 0.0038281 | 0.028688 | -0.0068766 | 0.02851 | -0.069885 | 0.012097 | 0.03261 | 0.051592 | -0.0021725 | 0.032272 | 0.073242 | 0.13733 | 0.11444 | 0.054932 | 0.050354 | 0.022888 | -0.13275 | 0.16022 | 0.16937 | 0.041199 | -0.013733 | -0.013733 | -0.059509 | -0.11902 | 0.10071 | -0.054931 | -121.8933 | 0.21515 | 0.13275 | 0.18768 | -121.8704 | 0.018311 | -0.041199 | -121.9574 | 0.23804 | 0.11902 | 0.16022 | -121.9574 | 0.12817 | 0.15106 | 0.19226 | -122.0764 | 0.064087 | 0.064087 | 0.24719 | -122.0627
4825.6719 | 122.1588 | -0.07782 | 121.962 | 0.10956 | 0.044846 | 0.061609 | 0.00041005 | 0.029756 | -0.0036722 | 0.028724 | 0.11322 | 0.01402 | 0.033678 | 0.052447 | 0.0040225 | 0.032272 | 0.07782 | 0.10529 | 0.082397 | 0.036621 | 0.027466 | 0.032043 | -0.10986 | 0.12817 | 0.086975 | 0.004578 | 0.022888 | -0.009155 | -0.045776 | -0.10071 | 0.10986 | -0.032043 | -121.9345 | 0.18311 | 0.11444 | 0.14648 | -121.8842 | 0.032044 | -0.022888 | -121.9391 | 0.20599 | 0.082398 | 0.10529 | -121.9711 | 0.10529 | 0.15564 | 0.16022 | -122.0718 | 0.10071 | 0.068665 | 0.16479 | -122.0627
4827.4375 | 122.1176 | -0.11444 | 121.9849 | -0.20325 | 0.046341 | 0.061609 | 0.0031873 | 0.028901 | -0.0045266 | 0.027015 | -0.14618 | 0.014875 | 0.034105 | 0.051165 | -0.00046349 | 0.033767 | 0.050354 | 0.11444 | 0.091553 | 0.045776 | 0.054932 | 0.027466 | -0.13275 | 0.10529 | 0.12817 | 0 | 0.013733 | -0.009155 | -0.059509 | -0.10986 | 0.14191 | -0.01831 | -121.9299 | 0.22888 | 0.16022 | 0.17853 | -121.9345 | 0.054932 | 0.004578 | -121.9711 | 0.21973 | 0.11444 | 0.10986 | -121.994 | 0.16937 | 0.16479 | 0.20599 | -122.1176 | 0.12817 | 0.10529 | 0.24262 | -122.0947
4829.2188 | 122.2412 | -0.07782 | 121.9757 | -0.065918 | 0.045487 | 0.061182 | 0.0040417 | 0.030397 | -0.0051676 | 0.027869 | -0.062256 | 0.012097 | 0.03325 | 0.052874 | -0.0019589 | 0.031631 | 0.050354 | 0.073242 | 0.054932 | 0.027466 | 0.036621 | 0.013733 | -0.14648 | 0.11902 | 0.13733 | 0.027466 | 0.022888 | -0.004578 | -0.036621 | -0.091553 | 0.091553 | -0.068664 | -121.9391 | 0.15106 | 0.10529 | 0.17395 | -121.9254 | 0.041199 | -0.013733 | -121.9528 | 0.19684 | 0.10529 | 0.11902 | -121.9803 | 0.11444 | 0.12817 | 0.13275 | -122.1222 | 0.10071 | 0.073242 | 0.21515 | -122.0673
4830.9844 | 122.1359 | -0.10071 | 121.994 | 0.10193 | 0.049332 | 0.060114 | -0.0012987 | 0.029328 | 0.0042318 | 0.029151 | 0.036926 | 0.015088 | 0.033464 | 0.05501 | 0.0048769 | 0.031417 | -0.009155 | -0.050354 | -0.064087 | -0.032043 | 0.064087 | -0.013733 | -0.16479 | 0.041199 | -0.036621 | -0.12817 | 0.045776 | 0.032043 | -0.07782 | -0.1236 | 0.086975 | -0.064087 | -121.9299 | 0.050354 | 0.068665 | 0.13275 | -122.0032 | 0.022888 | -0.022888 | -121.9482 | 0.14191 | -0.027466 | -0.004578 | -121.962 | 0.1648 | 0.091553 | 0.036621 | -122.1588 | 0.14648 | 0.13275 | 0.064087 | -122.1176
4832.6875 | 122.1359 | -0.10071 | 122.0032 | -0.13458 | 0.04805 | 0.059259 | -0.00023075 | 0.030397 | 0.0012412 | 0.030433 | -0.1767 | 0.018292 | 0.034105 | 0.051806 | 0.0018863 | 0.030777 | 0.041199 | 0.027466 | 0.004578 | 0.013733 | 0.082397 | -0.022888 | -0.15106 | 0.059509 | 0.054932 | -0.068665 | 0.022888 | 0.027466 | -0.059509 | -0.13275 | 0.07782 | -0.050354 | -121.9208 | 0.12817 | 0.11444 | 0.16479 | -121.962 | 0.041199 | -0.032043 | -121.9803 | 0.16022 | 0.032043 | 0.064086 | -121.9757 | 0.18311 | 0.14191 | 0.10529 | -122.1542 | 0.1236 | 0.12817 | 0.15564 | -122.1359
4834.4688 | 122.1542 | -0.09613 | 121.9894 | 0.10956 | 0.049332 | 0.060541 | 0.0016919 | 0.029115 | 0.0010276 | 0.031501 | 0.052185 | 0.01637 | 0.033037 | 0.053301 | 0.0050907 | 0.032058 | 0 | -0.059509 | -0.068665 | -0.045776 | 0.10071 | -0.018311 | -0.15106 | 0.018311 | -0.032043 | -0.13275 | 0.036621 | 0.022888 | -0.073242 | -0.14191 | 0.077819 | -0.054932 | -121.8887 | 0.036621 | 0.050354 | 0.10529 | -121.9894 | 0.022888 | -0.045777 | -121.9528 | 0.11444 | -0.036621 | 0.009156 | -121.9666 | 0.19684 | 0.09613 | 0.027465 | -122.1405 | 0.13275 | 0.11902 | 0.064087 | -122.1313
4836.1562 | 122.1085 | -0.13275 | 122.049 | -0.22614 | 0.047196 | 0.059473 | 0.0044691 | 0.028474 | -0.0028178 | 0.028083 | -0.22247 | 0.016156 | 0.036455 | 0.052447 | 0.00039091 | 0.03334 | -0.027466 | -0.027466 | -0.041199 | -0.032043 | 0.086975 | -0.041199 | -0.16937 | -0.004578 | 0.013733 | -0.10529 | 0.032043 | 0.068665 | -0.10529 | -0.13733 | 0.091552 | -0.036622 | -121.962 | 0.10529 | 0.10071 | 0.13733 | -122.0764 | 0.027465 | -0.004578 | -122.0169 | 0.12817 | 0.027465 | 0.032043 | -121.9803 | 0.21973 | 0.10529 | 0.091552 | -122.2183 | 0.16479 | 0.20142 | 0.14648 | -122.1863
4837.9219 | 122.1085 | -0.11444 | 122.0215 | -0.10406 | 0.048477 | 0.059045 | 0.00019645 | 0.031892 | -0.00089518 | 0.031714 | -0.1004 | 0.017224 | 0.035173 | 0.054156 | 0.0014591 | 0.030777 | 0.032043 | 0.022888 | 0.009155 | 0.004578 | 0.064087 | -0.004578 | -0.16022 | 0.064087 | 0.059509 | -0.07782 | 0.032043 | 0.027466 | -0.068665 | -0.13275 | 0.10986 | -0.045776 | -121.9574 | 0.13733 | 0.11902 | 0.16479 | -121.9894 | 0.045776 | -0.01831 | -121.9894 | 0.17853 | 0.036621 | 0.054931 | -121.994 | 0.17853 | 0.14648 | 0.1236 | -122.1817 | 0.14648 | 0.14191 | 0.17395 | -122.1542
4839.6875 | 122.1085 | -0.12817 | 122.0398 | -0.18799 | 0.046128 | 0.0599 | 0.0046827 | 0.030397 | -0.0073038 | 0.028297 | -0.19958 | 0.012525 | 0.034105 | 0.051378 | -0.0025999 | 0.033767 | 0.013733 | 0.091553 | 0.073242 | 0.041199 | 0.045776 | -0.004578 | -0.1236 | 0.045776 | 0.10071 | -0.027466 | 0.032043 | 0.004578 | -0.082397 | -0.1236 | 0.1236 | 0.004578 | -121.994 | 0.21973 | 0.16937 | 0.16479 | -122.0261 | 0.045777 | 0.004578 | -122.0078 | 0.17395 | 0.10071 | 0.09613 | -122.0352 | 0.17395 | 0.14191 | 0.20142 | -122.1634 | 0.16022 | 0.13275 | 0.22888 | -122.1634
4841.3906 | 122.1359 | -0.09613 | 122.0123 | 0.079041 | 0.049546 | 0.060541 | -1.7146e-05 | 0.025483 | -0.001536 | 0.029578 | 0.067444 | 0.018292 | 0.033678 | 0.05266 | 0.0031681 | 0.031631 | -0.022888 | -0.045776 | -0.059509 | -0.045776 | 0.091553 | -0.027466 | -0.14648 | 0.004578 | -0.027466 | -0.11902 | 0.041199 | 0.022888 | -0.073242 | -0.14191 | 0.068664 | -0.050354 | -121.9208 | 0.050354 | 0.050354 | 0.10071 | -122.0352 | 0.022888 | -0.045777 | -121.9711 | 0.10071 | -0.022889 | 0.022888 | -121.9894 | 0.18768 | 0.073242 | 0.036621 | -122.1588 | 0.13733 | 0.11902 | 0.068664 | -122.1542
4843.1562 | 122.2 | -0.09613 | 121.9711 | 0.033264 | 0.044205 | 0.058618 | -0.00044435 | 0.028047 | -0.0079446 | 0.02616 | 0.067444 | 0.012311 | 0.032823 | 0.052019 | -3.629e-05 | 0.034195 | 0.009155 | 0.045776 | 0.041199 | 0.009155 | 0.045776 | 0.009155 | -0.1236 | 0.07782 | 0.073242 | -0.018311 | 0.013733 | 0.004578 | -0.054932 | -0.10529 | 0.10528 | -0.027466 | -121.9254 | 0.14191 | 0.10528 | 0.13275 | -121.962 | 0.041198 | -0.009156 | -121.9574 | 0.17395 | 0.077819 | 0.086975 | -121.9666 | 0.14191 | 0.10528 | 0.13733 | -122.0947 | 0.10986 | 0.10071 | 0.16937 | -122.0764
4844.8594 | 122.1725 | -0.086975 | 122.0078 | -0.19562 | 0.047196 | 0.061609 | 0.0046827 | 0.027406 | -0.0075174 | 0.027228 | -0.14618 | 0.013593 | 0.034105 | 0.051806 | -0.0040951 | 0.034195 | 0.045776 | 0.11902 | 0.09613 | 0.059509 | 0.032043 | 0.018311 | -0.12817 | 0.10986 | 0.16479 | 0.018311 | -0.009155 | -0.027466 | -0.041199 | -0.10071 | 0.10529 | -0.041199 | -121.9757 | 0.20599 | 0.14648 | 0.18768 | -121.962 | 0.045776 | -0.013733 | -122.0169 | 0.19684 | 0.10529 | 0.11902 | -122.0352 | 0.11902 | 0.13275 | 0.1831 | -122.1359 | 0.07782 | 0.059509 | 0.25177 | -122.1085
4846.625 | 122.2412 | -0.064087 | 121.9803 | 0.094299 | 0.048264 | 0.060114 | -0.0010851 | 0.029542 | -0.00025418 | 0.027869 | 0.12085 | 0.015302 | 0.032182 | 0.054583 | 0.0031681 | 0.02864 | 0.018311 | -0.036621 | -0.041199 | -0.027466 | 0.073242 | -0.009155 | -0.15106 | 0.059509 | 0.027466 | -0.059509 | 0.041199 | 0.018311 | -0.07782 | -0.10071 | 0.054932 | -0.086975 | -121.907 | 0.027466 | 0.036621 | 0.1236 | -121.962 | -0.013733 | -0.036621 | -121.9391 | 0.1236 | 0.004578 | 0.041199 | -121.962 | 0.13733 | 0.082398 | 0.022888 | -122.1313 | 0.10529 | 0.082398 | 0.091553 | -122.081
4848.3906 | 122.2458 | -0.07782 | 122.0078 | -0.096436 | 0.046555 | 0.061182 | 0.0031873 | 0.029328 | -0.0096536 | 0.027869 | -0.077515 | 0.012952 | 0.03261 | 0.049242 | -0.0013181 | 0.035049 | 0.050354 | 0.09613 | 0.082397 | 0.045776 | 0.041199 | 0.013733 | -0.13275 | 0.12817 | 0.15106 | 0.036621 | 0.004578 | 0 | -0.004578 | -0.10986 | 0.091553 | -0.054931 | -121.9666 | 0.17395 | 0.1236 | 0.17853 | -121.9574 | 0.073242 | -0.032043 | -122.0032 | 0.20599 | 0.11444 | 0.14648 | -122.0078 | 0.11902 | 0.12817 | 0.16022 | -122.1405 | 0.082398 | 0.07782 | 0.22888 | -122.1176
4850.1562 | 122.1588 | -0.09613 | 122.0444 | -0.17273 | 0.049118 | 0.059686 | 0.00083745 | 0.029328 | -0.001536 | 0.029792 | -0.25299 | 0.01637 | 0.033891 | 0.054369 | 0.0018863 | 0.029708 | -0.009155 | -0.032043 | -0.032043 | -0.013733 | 0.082397 | -0.027466 | -0.16479 | 0.022888 | 0.018311 | -0.091553 | 0.059509 | 0.018311 | -0.059509 | -0.1236 | 0.068664 | -0.068665 | -121.962 | 0.064087 | 0.082397 | 0.15106 | -122.0535 | 0.036621 | -0.027466 | -121.9849 | 0.11902 | 0.004577 | 0.032043 | -122.0261 | 0.17853 | 0.086975 | 0.064087 | -122.2092 | 0.15564 | 0.11444 | 0.11444 | -122.168
4851.8594 | 122.1634 | -0.1236 | 122.0398 | -0.24139 | 0.049118 | 0.063318 | 0.0034009 | 0.030824 | -0.0040994 | 0.027869 | -0.25299 | 0.01402 | 0.035387 | 0.051378 | -0.00046349 | 0.032699 | -0.032043 | -0.022888 | -0.045776 | -0.036621 | 0.091553 | -0.036621 | -0.15564 | -0.013733 | -0.004578 | -0.1236 | 0.059509 | 0.022888 | -0.09613 | -0.13275 | 0.086975 | -0.032044 | -121.9482 | 0.10071 | 0.086975 | 0.11902 | -122.0718 | 0.027466 | -0.009155 | -121.9803 | 0.10986 | 0 | 0.009155 | -122.0169 | 0.21515 | 0.091553 | 0.07782 | -122.1954 | 0.1831 | 0.14648 | 0.11902 | -122.1725
4853.625 | 122.1497 | -0.10071 | 122.0215 | 0.040894 | 0.049546 | 0.059259 | -0.00087155 | 0.029756 | 0.00017302 | 0.028724 | 0.029297 | 0.016156 | 0.03325 | 0.054156 | 0.0042361 | 0.033767 | -0.050354 | -0.068665 | -0.07782 | -0.041199 | 0.091553 | -0.009155 | -0.16022 | 0.018311 | -0.041199 | -0.1236 | 0.045776 | 0.045776 | -0.073242 | -0.14191 | 0.091553 | -0.059509 | -121.9299 | 0.032043 | 0.059509 | 0.11902 | -122.0718 | 0.027466 | -0.041199 | -121.9757 | 0.11902 | -0.022888 | 0.018311 | -121.9757 | 0.19226 | 0.050354 | 0.022888 | -122.1817 | 0.14648 | 0.14648 | 0.059509 | -122.1634
4855.3438 | 122.2092 | -0.07782 | 122.0306 | 0.14771 | 0.047837 | 0.060541 | -1.7146e-05 | 0.026765 | -0.0064492 | 0.029151 | 0.17426 | 0.011884 | 0.03261 | 0.052874 | 0.0014591 | 0.033126 | 0.073242 | 0.10071 | 0.091553 | 0.050354 | 0.032043 | 0.022888 | -0.11902 | 0.13275 | 0.11444 | 0.032043 | 0.013733 | -0.009155 | -0.036621 | -0.082397 | 0.10071 | -0.041199 | -121.9986 | 0.17853 | 0.12817 | 0.16937 | -121.9574 | 0.041199 | -0.004577 | -122.0169 | 0.21057 | 0.10986 | 0.11444 | -122.0398 | 0.10986 | 0.15106 | 0.16937 | -122.1497 | 0.091553 | 0.068665 | 0.19226 | -122.113
4857.125 | 122.1268 | -0.1236 | 122.0215 | -0.11169 | 0.047837 | 0.059259 | 0.00083745 | 0.03061 | -0.0013224 | 0.030219 | -0.14618 | 0.016797 | 0.036668 | 0.056719 | 0.0023135 | 0.033554 | 0.045776 | 0.032043 | 0 | 0.009155 | 0.059509 | 0 | -0.14648 | 0.064087 | 0.059509 | -0.082397 | 0.041199 | 0.022888 | -0.073242 | -0.11902 | 0.1236 | -0.022888 | -121.962 | 0.15564 | 0.13275 | 0.15564 | -121.9757 | 0.050354 | 0.004577 | -121.9803 | 0.18768 | 0.041199 | 0.036622 | -121.9986 | 0.1831 | 0.16937 | 0.1236 | -122.168 | 0.16479 | 0.14648 | 0.1831 | -122.1405
4858.8281 | 122.1222 | -0.11902 | 122.0444 | -0.081177 | 0.054032 | 0.060754 | 0.0070325 | 0.030824 | 0.0012412 | 0.030219 | -0.062256 | 0.015943 | 0.035173 | 0.054369 | 0.0010317 | 0.031631 | 0.032043 | -0.004578 | -0.018311 | 0.009155 | 0.059509 | -0.004578 | -0.15106 | 0.041199 | 0.018311 | -0.11444 | 0.041199 | 0.045776 | -0.091553 | -0.14191 | 0.11444 | -0.032043 | -121.9849 | 0.11444 | 0.12817 | 0.16022 | -122.0123 | 0.027466 | -0.022888 | -122.0032 | 0.16022 | 0.004578 | 0.027466 | -121.9986 | 0.17853 | 0.15106 | 0.10071 | -122.1954 | 0.16022 | 0.16479 | 0.13733 | -122.1863
4860.5938 | 122.1085 | -0.10986 | 122.0627 | -0.065918 | 0.04805 | 0.057336 | 0.0027601 | 0.028474 | -0.002604 | 0.032142 | -0.046997 | 0.01402 | 0.032823 | 0.052874 | 0.0033817 | 0.032486 | 0.022888 | 0.013733 | -0.018311 | 0.004578 | 0.064087 | -0.013733 | -0.16022 | 0.027466 | 0.013733 | -0.09613 | 0.045776 | 0.018311 | -0.091553 | -0.12817 | 0.09613 | -0.050354 | -121.9986 | 0.1236 | 0.11444 | 0.16479 | -122.0398 | 0.01831 | -0.018311 | -122.0169 | 0.13733 | 0.013733 | 0.032044 | -122.0444 | 0.17395 | 0.13275 | 0.091552 | -122.2229 | 0.15564 | 0.12817 | 0.1236 | -122.1909
4862.3594 | 122.2458 | -0.073242 | 121.9894 | 0.079041 | 0.047196 | 0.060541 | 0.0021191 | 0.030183 | -0.0053812 | 0.031714 | 0.13611 | 0.01402 | 0.036027 | 0.054583 | 0.0018863 | 0.034408 | 0.045776 | 0.086975 | 0.054932 | 0.054932 | 0.050354 | 0.022888 | -0.11902 | 0.1236 | 0.10529 | 0.013733 | -0.009155 | -0.022888 | -0.032043 | -0.09613 | 0.09613 | -0.045777 | -121.9391 | 0.16022 | 0.12817 | 0.17395 | -121.9437 | 0.041199 | -0.022888 | -121.9986 | 0.19684 | 0.086975 | 0.10986 | -122.0123 | 0.1236 | 0.11902 | 0.12817 | -122.1085 | 0.064087 | 0.050354 | 0.17853 | -122.0856
4864.0781 | 122.2366 | -0.091553 | 122.0261 | 0.033264 | 0.045914 | 0.062036 | 0.0038281 | 0.027833 | -0.0098672 | 0.026801 | 0.090332 | 0.014447 | 0.036455 | 0.053728 | -0.0025999 | 0.03569 | -0.004578 | 0.041199 | 0.032043 | 0.032043 | 0.059509 | 0.018311 | -0.14191 | 0.054932 | 0.064087 | -0.009155 | 0.009155 | 0.009155 | -0.054932 | -0.10071 | 0.10986 | -0.050354 | -121.9666 | 0.13275 | 0.1236 | 0.17395 | -122.0306 | 0.036621 | -0.009155 | -122.0169 | 0.14649 | 0.082398 | 0.091553 | -122.0169 | 0.15106 | 0.086975 | 0.1236 | -122.168 | 0.10071 | 0.10071 | 0.15564 | -122.1268
4865.8438 | 122.1497 | -0.10071 | 122.0764 | 0.040894 | 0.047409 | 0.059045 | -0.00065795 | 0.028474 | 0.00060022 | 0.028937 | 0.052185 | 0.019788 | 0.033891 | 0.054156 | 0.0029543 | 0.030777 | -0.027466 | -0.082397 | -0.064087 | -0.050354 | 0.073242 | -0.032043 | -0.15564 | -0.013733 | -0.032043 | -0.11902 | 0.059509 | 0.022888 | -0.073242 | -0.13275 | 0.068665 | -0.054932 | -122.0032 | 0.018311 | 0.050354 | 0.10529 | -122.1039 | 0.027466 | -0.032043 | -122.0169 | 0.086975 | -0.018311 | 0.013732 | -122.0535 | 0.17395 | 0.073242 | 0.036621 | -122.2321 | 0.16022 | 0.1236 | 0.068665 | -122.2092
4867.6094 | 122.2458 | -0.068665 | 122.0444 | 0.010376 | 0.048264 | 0.059045 | 0.0046827 | 0.027192 | -0.010508 | 0.027228 | 0.082703 | 0.011884 | 0.035173 | 0.051592 | -0.0021725 | 0.035049 | -0.009155 | 0.032043 | 0.036621 | 0.004578 | 0.041199 | 0.022888 | -0.12817 | 0.050354 | 0.059509 | -0.018311 | 0.018311 | 0.013733 | -0.059509 | -0.10071 | 0.091553 | -0.059509 | -122.0032 | 0.10071 | 0.073243 | 0.13275 | -122.0535 | 0.009156 | -0.032043 | -122.0261 | 0.11902 | 0.050354 | 0.082397 | -122.0306 | 0.10986 | 0.05951 | 0.10529 | -122.1725 | 0.086976 | 0.082398 | 0.12817 | -122.1451
4869.3281 | 122.2275 | -0.068665 | 122.0032 | 0.12482 | 0.046768 | 0.062463 | -0.0017261 | 0.029756 | -0.0019632 | 0.029151 | 0.18951 | 0.01167 | 0.03325 | 0.049242 | 0.0023135 | 0.032272 | 0.082397 | 0.091553 | 0.059509 | 0.059509 | 0.041199 | 0.018311 | -0.11444 | 0.1236 | 0.10529 | 0.013733 | -0.009155 | -0.022888 | -0.059509 | -0.091553 | 0.086976 | -0.045776 | -121.962 | 0.16022 | 0.12817 | 0.17395 | -121.9208 | 0.009156 | -0.022888 | -122.0123 | 0.19226 | 0.082398 | 0.10529 | -122.0261 | 0.10986 | 0.15106 | 0.12817 | -122.1176 | 0.05951 | 0.045777 | 0.17395 | -122.0947
4871.0938 | 122.1817 | -0.10071 | 122.0764 | -0.12695 | 0.04805 | 0.061182 | 0.0046827 | 0.029756 | 0.00081382 | 0.02851 | -0.12329 | 0.016156 | 0.0356 | 0.05501 | 0.0020999 | 0.029708 | 0.050354 | 0.009155 | 0.004578 | 0.009155 | 0.07782 | -0.013733 | -0.15106 | 0.064087 | 0.050354 | -0.073242 | 0.027466 | 0.013733 | -0.082397 | -0.10986 | 0.086975 | -0.050354 | -121.9986 | 0.10986 | 0.10986 | 0.16022 | -122.0261 | 0.018311 | -0.009155 | -122.0489 | 0.1648 | 0.027466 | 0.036621 | -122.0627 | 0.17853 | 0.15106 | 0.10529 | -122.2275 | 0.12817 | 0.11444 | 0.15106 | -122.1863
4872.7969 | 122.1725 | -0.11444 | 122.049 | -0.19562 | 0.051468 | 0.0599 | 0.0061781 | 0.026979 | -0.0047404 | 0.028724 | -0.22247 | 0.016156 | 0.03795 | 0.053942 | -3.629e-05 | 0.032058 | -0.013733 | -0.045776 | -0.032043 | -0.018311 | 0.10529 | 0.009155 | -0.16937 | 0.004578 | 0.032043 | -0.10986 | 0.022888 | 0.050354 | -0.082397 | -0.12817 | 0.1236 | -0.054932 | -121.9437 | 0.068665 | 0.09613 | 0.15106 | -122.0627 | 0.032044 | -0.013733 | -122.0261 | 0.11902 | 0.004578 | 0.018311 | -121.9986 | 0.21973 | 0.10071 | 0.082398 | -122.2183 | 0.13733 | 0.16479 | 0.14648 | -122.1771
4874.5781 | 122.2641 | -0.091553 | 122.0078 | -0.0048827 | 0.042496 | 0.061609 | 0.00062385 | 0.029542 | -0.0079446 | 0.028083 | 0.059815 | 0.013379 | 0.031328 | 0.052447 | 0.0012455 | 0.032913 | -0.018311 | 0.041199 | 0.036621 | 0.022888 | 0.050354 | 0.004578 | -0.1236 | 0.054932 | 0.073242 | 0 | 0.032043 | 0.013733 | -0.064087 | -0.10529 | 0.096131 | -0.032043 | -121.9574 | 0.13275 | 0.11444 | 0.14648 | -122.0261 | 0.027466 | -0.013733 | -121.9757 | 0.14649 | 0.091553 | 0.10529 | -121.994 | 0.14191 | 0.073242 | 0.12817 | -122.1313 | 0.1236 | 0.10529 | 0.16479 | -122.113
4876.3438 | 122.2275 | -0.082397 | 121.9986 | 0.13245 | 0.045914 | 0.059045 | 0.00019645 | 0.029115 | -0.0045266 | 0.030006 | 0.16663 | 0.014661 | 0.034105 | 0.051378 | 0.0027407 | 0.033554 | 0.068665 | 0.091553 | 0.082397 | 0.050354 | 0.022888 | 0.041199 | -0.10529 | 0.11444 | 0.11902 | 0.009155 | -0.004578 | -0.013733 | -0.054932 | -0.082397 | 0.1236 | -0.022889 | -121.9757 | 0.17395 | 0.13275 | 0.15564 | -121.9299 | 0.027465 | 0 | -122.0032 | 0.19684 | 0.091552 | 0.091552 | -122.0123 | 0.10528 | 0.15106 | 0.16479 | -122.1039 | 0.077819 | 0.068664 | 0.20142 | -122.081
4878.1094 | 122.2229 | -0.09613 | 122.049 | -0.18799 | 0.045914 | 0.061395 | 0.0055371 | 0.027619 | -0.0070902 | 0.026374 | -0.16144 | 0.013166 | 0.032823 | 0.05031 | -0.00089089 | 0.034835 | 0.059509 | 0.11444 | 0.11444 | 0.054932 | 0.041199 | 0 | -0.12817 | 0.091553 | 0.14191 | 0.032043 | 0 | -0.018311 | -0.050354 | -0.082397 | 0.09613 | -0.032044 | -122.0078 | 0.21057 | 0.15106 | 0.18311 | -121.9894 | 0.045776 | 0.013733 | -122.049 | 0.18768 | 0.12817 | 0.11444 | -122.0673 | 0.13733 | 0.15564 | 0.21057 | -122.1771 | 0.09613 | 0.077819 | 0.23804 | -122.1313
4879.8125 | 122.2229 | -0.10986 | 122.0306 | -0.19562 | 0.047409 | 0.06225 | 0.0066053 | 0.029328 | -0.0062356 | 0.025947 | -0.14618 | 0.012525 | 0.032396 | 0.051378 | -3.629e-05 | 0.032913 | 0.064087 | 0.1236 | 0.091553 | 0.073242 | 0.032043 | 0.018311 | -0.12817 | 0.10529 | 0.13733 | 0.013733 | -0.004578 | -0.004578 | -0.045776 | -0.10071 | 0.12817 | -0.018311 | -121.9986 | 0.23346 | 0.18311 | 0.20142 | -121.9666 | 0.064087 | 0.009155 | -122.0352 | 0.21515 | 0.1236 | 0.11444 | -122.0352 | 0.14191 | 0.17395 | 0.20142 | -122.1588 | 0.10529 | 0.10529 | 0.24719 | -122.1313
4881.5781 | 122.1863 | -0.091553 | 122.0535 | -0.17273 | 0.050186 | 0.060114 | 0.0044691 | 0.029969 | 0.0031638 | 0.027442 | -0.26062 | 0.015943 | 0.037309 | 0.053087 | 0.0016727 | 0.030563 | 0.013733 | -0.022888 | -0.027466 | -0.022888 | 0.07782 | -0.018311 | -0.16937 | 0.036621 | 0.027466 | -0.07782 | 0.022888 | 0.018311 | -0.073242 | -0.1236 | 0.073242 | -0.07782 | -121.9757 | 0.068665 | 0.068665 | 0.14649 | -122.0398 | 0.018311 | -0.032043 | -122.0306 | 0.12817 | 0.013733 | 0.045776 | -122.0352 | 0.16937 | 0.10529 | 0.064087 | -122.2229 | 0.11444 | 0.10986 | 0.11902 | -122.1771
4883.3281 | 122.2458 | -0.09613 | 122.0261 | 0.10193 | 0.049759 | 0.060541 | -0.00087155 | 0.02826 | 0.00017302 | 0.031074 | 0.052185 | 0.015515 | 0.03261 | 0.054369 | 0.0038089 | 0.03334 | 0.004578 | -0.041199 | -0.059509 | -0.032043 | 0.07782 | -0.009155 | -0.16479 | 0.022888 | -0.018311 | -0.10986 | 0.041199 | 0.036621 | -0.086975 | -0.14191 | 0.086975 | -0.068665 | -121.9482 | 0.054931 | 0.064087 | 0.13275 | -122.0215 | 0.009155 | -0.045777 | -121.9849 | 0.11902 | -0.013733 | 0.032044 | -121.9894 | 0.17395 | 0.10071 | 0.036621 | -122.1909 | 0.13733 | 0.13275 | 0.077819 | -122.168
4885.0469 | 122.2275 | -0.068665 | 122.0352 | 0.071411 | 0.044632 | 0.059686 | 0.00019645 | 0.027192 | -0.0075174 | 0.031287 | 0.12085 | 0.011884 | 0.031541 | 0.052874 | -0.0015317 | 0.034622 | 0.064087 | 0.09613 | 0.082397 | 0.032043 | 0.018311 | 0.013733 | -0.10986 | 0.12817 | 0.086975 | 0 | 0 | -0.009155 | -0.036621 | -0.10529 | 0.082398 | -0.041198 | -122.0169 | 0.16479 | 0.10071 | 0.14191 | -121.9711 | 0.032044 | -0.036621 | -122.0352 | 0.19684 | 0.068665 | 0.10529 | -122.0444 | 0.086976 | 0.13275 | 0.15106 | -122.1451 | 0.068665 | 0.05951 | 0.15564 | -122.1405
4886.8125 | 122.2 | -0.11902 | 122.0764 | -0.19562 | 0.051682 | 0.057977 | 0.0063917 | 0.030183 | -0.001536 | 0.029792 | -0.21484 | 0.018292 | 0.036455 | 0.053515 | 0.0014591 | 0.03099 | 0.013733 | -0.027466 | -0.041199 | 0 | 0.073242 | 0 | -0.16022 | 0.032043 | 0.059509 | -0.082397 | 0.032043 | 0.018311 | -0.073242 | -0.12817 | 0.11902 | -0.041198 | -122.0032 | 0.091553 | 0.11902 | 0.16022 | -122.0627 | 0.045777 | -0.009155 | -122.0444 | 0.15106 | 0.036622 | 0.045777 | -122.0581 | 0.19226 | 0.13275 | 0.07782 | -122.2366 | 0.15106 | 0.13733 | 0.17853 | -122.2046
4888.5781 | 122.1542 | -0.11444 | 122.0718 | -0.17273 | 0.048905 | 0.060114 | 0.0051099 | 0.027833 | -0.0047404 | 0.027442 | -0.21484 | 0.01402 | 0.03795 | 0.054156 | -3.629e-05 | 0.034195 | -0.032043 | -0.027466 | -0.032043 | -0.036621 | 0.07782 | -0.041199 | -0.17395 | -0.004578 | 0.018311 | -0.09613 | 0.054932 | 0.032043 | -0.086975 | -0.14648 | 0.073242 | -0.059509 | -121.994 | 0.086975 | 0.07782 | 0.13733 | -122.1039 | 0.027466 | -0.032043 | -122.0169 | 0.10986 | 0.018311 | 0.050354 | -122.0398 | 0.19226 | 0.082398 | 0.082398 | -122.2458 | 0.16937 | 0.14648 | 0.13275 | -122.2183
4890.2812 | 122.168 | -0.12817 | 122.0535 | -0.19562 | 0.048477 | 0.06225 | 0.0025465 | 0.03061 | -0.006022 | 0.029365 | -0.2301 | 0.014875 | 0.032396 | 0.053728 | 0.0023135 | 0.032699 | -0.032043 | -0.009155 | -0.041199 | -0.050354 | 0.07782 | -0.032043 | -0.17395 | -0.013733 | 0.013733 | -0.10071 | 0.054932 | 0.045776 | -0.10071 | -0.14648 | 0.096131 | -0.045776 | -121.9757 | 0.11902 | 0.07782 | 0.1236 | -122.0856 | 0.027466 | -0.01831 | -121.9986 | 0.11444 | 0.027466 | 0.045776 | -122.0078 | 0.20599 | 0.096131 | 0.086975 | -122.2275 | 0.18311 | 0.17395 | 0.14191 | -122.2
4892.0469 | 122.2641 | -0.064087 | 122.0169 | 0.14008 | 0.046768 | 0.059045 | -0.0010851 | 0.029328 | -0.002604 | 0.028937 | 0.067444 | 0.017011 | 0.03325 | 0.05501 | 0.0035953 | 0.033554 | 0.050354 | 0.073242 | 0.041199 | 0.041199 | 0.050354 | 0.018311 | -0.1236 | 0.11444 | 0.091553 | 0.009155 | 0.018311 | -0.013733 | -0.054932 | -0.07782 | 0.082398 | -0.059509 | -121.9666 | 0.13733 | 0.10529 | 0.16479 | -121.9666 | 0.009155 | -0.013733 | -121.9986 | 0.17853 | 0.073242 | 0.086975 | -122.0306 | 0.11444 | 0.11444 | 0.10529 | -122.1405 | 0.082398 | 0.050354 | 0.15564 | -122.0947
4893.75 | 122.1588 | -0.1236 | 122.0718 | -0.41687 | 0.046768 | 0.060114 | 0.0040417 | 0.028901 | -0.0036722 | 0.029151 | -0.20721 | 0.015088 | 0.035387 | 0.054583 | -0.0021725 | 0.034408 | -0.032043 | -0.013733 | -0.022888 | -0.027466 | 0.09613 | -0.004578 | -0.1831 | 0.018311 | 0.013733 | -0.09613 | 0.045776 | 0.027466 | -0.086975 | -0.14191 | 0.11902 | -0.059509 | -121.9757 | 0.10986 | 0.09613 | 0.15564 | -122.1039 | 0.036621 | -0.018311 | -122.0261 | 0.14191 | 0.027466 | 0.045777 | -122.0444 | 0.21973 | 0.091553 | 0.10071 | -122.2549 | 0.16937 | 0.15106 | 0.13733 | -122.2137
4895.5312 | 122.1497 | -0.13275 | 122.0673 | -0.25665 | 0.047196 | 0.060541 | 0.0042555 | 0.030397 | -0.0051676 | 0.028937 | -0.20721 | 0.01637 | 0.033464 | 0.054583 | 0.0012455 | 0.033767 | 0.027466 | 0.054932 | 0.027466 | 0.022888 | 0.064087 | -0.009155 | -0.15106 | 0.018311 | 0.041199 | -0.064087 | 0.045776 | 0.022888 | -0.082397 | -0.14191 | 0.1236 | -0.018311 | -122.0032 | 0.18768 | 0.15564 | 0.17395 | -122.0398 | 0.050354 | -0.009156 | -122.0215 | 0.15106 | 0.068664 | 0.07782 | -122.0444 | 0.19684 | 0.16022 | 0.16022 | -122.2183 | 0.17853 | 0.15564 | 0.17395 | -122.2092
4897.2969 | 122.1542 | -0.11444 | 122.0581 | -0.24902 | 0.047837 | 0.061823 | 0.0061781 | 0.028688 | -0.0053812 | 0.029578 | -0.19958 | 0.015302 | 0.033464 | 0.053942 | -0.0011045 | 0.032272 | 0.027466 | 0.041199 | 0.018311 | 0.013733 | 0.064087 | 0 | -0.15106 | 0.013733 | 0.041199 | -0.086975 | 0.027466 | 0.036621 | -0.073242 | -0.14648 | 0.11444 | -0.036621 | -121.994 | 0.15564 | 0.12817 | 0.16479 | -122.0306 | 0.041199 | -0.032043 | -122.0306 | 0.12817 | 0.027466 | 0.059509 | -122.0215 | 0.17853 | 0.14191 | 0.13275 | -122.2092 | 0.14191 | 0.15106 | 0.15564 | -122.2046
4899.0625 | 122.1588 | -0.13733 | 122.0856 | 0.048523 | 0.049546 | 0.059259 | 0.00083745 | 0.028901 | 0.0014548 | 0.031074 | -0.024109 | 0.016156 | 0.03325 | 0.054369 | 0.0025271 | 0.030136 | 0.004578 | -0.073242 | -0.059509 | -0.032043 | 0.059509 | -0.013733 | -0.15106 | -0.013733 | -0.027466 | -0.14648 | 0.054932 | 0.036621 | -0.07782 | -0.13733 | 0.1236 | -0.013733 | -122.0261 | 0.064087 | 0.10529 | 0.11902 | -122.081 | 0.059509 | 0 | -122.0306 | 0.1236 | -0.009155 | -0.009155 | -122.049 | 0.19684 | 0.14191 | 0.07782 | -122.2366 | 0.19226 | 0.17395 | 0.10986 | -122.2229
4900.8281 | 122.1771 | -0.11444 | 122.0535 | -0.23376 | 0.050827 | 0.062463 | 0.0087415 | 0.029115 | -0.004313 | 0.029792 | -0.26062 | 0.01402 | 0.036027 | 0.053301 | -0.00067729 | 0.031631 | -0.032043 | -0.032043 | -0.036621 | -0.027466 | 0.091553 | -0.022888 | -0.19226 | -0.013733 | 0.004578 | -0.10986 | 0.041199 | 0.036621 | -0.091553 | -0.13275 | 0.091553 | -0.07782 | -121.962 | 0.082398 | 0.086975 | 0.16479 | -122.0856 | 0.022888 | -0.01831 | -122.0123 | 0.10071 | 0.004578 | 0.022888 | -122.0169 | 0.20599 | 0.082398 | 0.07782 | -122.2458 | 0.15564 | 0.15106 | 0.11902 | -122.1863
4902.5938 | 122.2412 | -0.073242 | 122.049 | 0.056152 | 0.044846 | 0.058618 | 0.0031873 | 0.029969 | -0.006022 | 0.029578 | 0.159 | 0.014875 | 0.033891 | 0.052874 | 0.00017731 | 0.034408 | 0.059509 | 0.10986 | 0.09613 | 0.041199 | 0.032043 | 0.013733 | -0.1236 | 0.1236 | 0.10071 | 0 | 0.009155 | 0 | -0.041199 | -0.086975 | 0.086975 | -0.050354 | -122.0169 | 0.18311 | 0.11444 | 0.16479 | -121.9894 | 0.032043 | -0.013733 | -122.0398 | 0.19684 | 0.073242 | 0.086975 | -122.049 | 0.10529 | 0.13275 | 0.16937 | -122.1725 | 0.082397 | 0.073242 | 0.17395 | -122.1359
4904.3125 | 122.2412 | -0.064087 | 122.0215 | 0.079041 | 0.045487 | 0.059686 | 0.0034009 | 0.029756 | -0.0064492 | 0.027656 | 0.12848 | 0.010816 | 0.032823 | 0.052447 | 0.00060451 | 0.031417 | 0.045776 | 0.10071 | 0.068665 | 0.032043 | 0.041199 | 0.013733 | -0.13275 | 0.091553 | 0.082397 | -0.018311 | 0.013733 | 0.004578 | -0.050354 | -0.10071 | 0.07782 | -0.068664 | -121.9803 | 0.1648 | 0.09613 | 0.16479 | -121.9757 | 0.013733 | -0.036621 | -122.0078 | 0.15564 | 0.045776 | 0.082397 | -122.0169 | 0.10529 | 0.10986 | 0.13275 | -122.1542 | 0.07782 | 0.068665 | 0.14648 | -122.1222
4906.0781 | 122.287 | -0.064087 | 122.0398 | 0.12482 | 0.046555 | 0.059686 | 0.00041005 | 0.029969 | -0.0036722 | 0.030646 | 0.12085 | 0.016156 | 0.031755 | 0.053515 | 0.0033817 | 0.033767 | 0.027466 | -0.004578 | 0.004578 | 0 | 0.068665 | -0.013733 | -0.14648 | 0.10529 | 0.073242 | -0.032043 | 0.036621 | 0.013733 | -0.059509 | -0.091553 | 0.050354 | -0.082397 | -121.9711 | 0.059509 | 0.064087 | 0.14648 | -122.0123 | 0.004578 | -0.027466 | -122.0032 | 0.16937 | 0.032044 | 0.05951 | -122.0261 | 0.13275 | 0.091553 | 0.068665 | -122.1863 | 0.10071 | 0.07782 | 0.13733 | -122.1313
4907.8438 | 122.1634 | -0.13275 | 122.081 | -0.14984 | 0.047623 | 0.059473 | 0.0057507 | 0.026338 | -0.0023904 | 0.029365 | -0.19958 | 0.016156 | 0.033464 | 0.05266 | -0.00067729 | 0.034408 | -0.013733 | -0.004578 | -0.027466 | -0.032043 | 0.086975 | -0.009155 | -0.15106 | -0.004578 | 0.013733 | -0.091553 | 0.054932 | 0.032043 | -0.086975 | -0.14648 | 0.1236 | -0.018311 | -121.994 | 0.12817 | 0.10071 | 0.11902 | -122.0947 | 0.045776 | -0.013733 | -122.0261 | 0.12817 | 0.041198 | 0.054931 | -122.049 | 0.21973 | 0.11902 | 0.10529 | -122.2321 | 0.18768 | 0.16479 | 0.14648 | -122.2275
4909.625 | 122.2366 | -0.086975 | 122.0261 | 0.079041 | 0.046555 | 0.059259 | 0.0044691 | 0.028474 | -0.0053812 | 0.026801 | 0.082703 | 0.010816 | 0.035173 | 0.05501 | -0.0017453 | 0.032913 | 0.036621 | 0.073242 | 0.050354 | 0.009155 | 0.050354 | 0.018311 | -0.12817 | 0.091553 | 0.091553 | -0.032043 | 0.013733 | 0.009155 | -0.054932 | -0.10986 | 0.10529 | -0.041199 | -121.9757 | 0.16022 | 0.09613 | 0.13733 | -121.9894 | 0.032043 | -0.022888 | -122.0123 | 0.17853 | 0.054932 | 0.07782 | -122.0169 | 0.13733 | 0.1236 | 0.13733 | -122.1542 | 0.10071 | 0.09613 | 0.17853 | -122.1359
4911.3438 | 122.2549 | -0.068665 | 122.0123 | 0.14008 | 0.046555 | 0.061609 | 0.00019645 | 0.026551 | -0.0047404 | 0.031714 | 0.12848 | 0.012097 | 0.033891 | 0.052019 | 0.0020999 | 0.034408 | 0.068665 | 0.091553 | 0.091553 | 0.050354 | 0.054932 | 0.032043 | -0.11902 | 0.14191 | 0.10529 | 0.013733 | -0.004578 | -0.022888 | -0.032043 | -0.086975 | 0.10071 | -0.050354 | -121.9574 | 0.16022 | 0.11902 | 0.16937 | -121.9437 | 0.036622 | -0.01831 | -122.0169 | 0.21057 | 0.082398 | 0.10071 | -122.0352 | 0.1236 | 0.13733 | 0.16022 | -122.1313 | 0.064087 | 0.045777 | 0.17395 | -122.0993
4913.1094 | 122.1634 | -0.11444 | 122.0673 | 0.033264 | 0.050186 | 0.058832 | 0.00062385 | 0.027406 | 0.0020956 | 0.030646 | -0.016479 | 0.018079 | 0.036241 | 0.053515 | 0.0044497 | 0.031417 | -0.032043 | -0.064087 | -0.07782 | -0.027466 | 0.082397 | -0.027466 | -0.14648 | 0.004578 | -0.054932 | -0.1236 | 0.050354 | 0.036621 | -0.086975 | -0.11444 | 0.086975 | -0.032043 | -121.9849 | 0.050354 | 0.086975 | 0.11902 | -122.0993 | 0.027466 | 0 | -122.0169 | 0.11902 | -0.009155 | -0.009155 | -122.0306 | 0.19684 | 0.082398 | 0.036621 | -122.2137 | 0.16479 | 0.15106 | 0.059509 | -122.1817
4914.875 | 122.1817 | -0.10071 | 122.049 | 0.025635 | 0.048905 | 0.060541 | 0.0012647 | 0.027192 | -0.002604 | 0.028297 | 0.029297 | 0.015515 | 0.034105 | 0.053942 | 0.0046633 | 0.034195 | -0.036621 | -0.07782 | -0.07782 | -0.041199 | 0.082397 | 0 | -0.14648 | 0.009155 | -0.041199 | -0.14191 | 0.041199 | 0.041199 | -0.086975 | -0.11902 | 0.10071 | -0.045776 | -121.9666 | 0.022888 | 0.059509 | 0.10529 | -122.0856 | 0.013733 | -0.018311 | -122.0078 | 0.10986 | -0.041199 | -0.022888 | -122.0078 | 0.18311 | 0.064087 | 0.022888 | -122.1954 | 0.14191 | 0.14191 | 0.059509 | -122.168
4916.6562 | 122.2 | -0.11902 | 122.0856 | -0.15747 | 0.050827 | 0.056696 | 0.0053235 | 0.028901 | -0.0028178 | 0.030433 | -0.16907 | 0.015729 | 0.036027 | 0.054796 | 0.0031681 | 0.032913 | 0.018311 | 0.004578 | -0.013733 | 0.013733 | 0.068665 | -0.018311 | -0.16022 | 0.045776 | 0.068665 | -0.068665 | 0.036621 | 0.022888 | -0.064087 | -0.11902 | 0.10071 | -0.041198 | -122.0169 | 0.1236 | 0.13275 | 0.17395 | -122.0673 | 0.054932 | 0 | -122.049 | 0.16479 | 0.050354 | 0.050354 | -122.0627 | 0.18768 | 0.13733 | 0.10529 | -122.2458 | 0.15564 | 0.14191 | 0.18768 | -122.2046
4918.3594 | 122.2366 | -0.09613 | 122.0352 | 0.079041 | 0.047837 | 0.060114 | 0.0038281 | 0.03061 | -0.0079446 | 0.029151 | 0.13611 | 0.011029 | 0.036241 | 0.053515 | -0.0030271 | 0.03569 | 0.022888 | 0.10071 | 0.059509 | 0.022888 | 0.032043 | 0.027466 | -0.11902 | 0.082397 | 0.068665 | -0.013733 | 0.004578 | -0.004578 | -0.050354 | -0.10986 | 0.1236 | -0.022889 | -122.0032 | 0.19684 | 0.11902 | 0.14191 | -122.0123 | 0.045776 | -0.013733 | -122.0306 | 0.17853 | 0.082397 | 0.09613 | -122.0398 | 0.12817 | 0.11902 | 0.15564 | -122.1542 | 0.10071 | 0.091552 | 0.16479 | -122.1451
4920.125 | 122.1405 | -0.12817 | 122.0673 | -0.0354 | 0.049759 | 0.057336 | 0.0042555 | 0.027619 | 0.0014548 | 0.030433 | -0.039368 | 0.017652 | 0.034746 | 0.056505 | 0.0029543 | 0.031204 | 0.022888 | -0.004578 | -0.022888 | -0.018311 | 0.07782 | -0.013733 | -0.15106 | 0 | -0.009155 | -0.11444 | 0.041199 | 0.013733 | -0.091553 | -0.13275 | 0.11444 | -0.022888 | -121.9894 | 0.1236 | 0.10986 | 0.13275 | -122.0444 | 0.036621 | -0.004577 | -122.0261 | 0.12817 | 0.013733 | 0.01831 | -122.0535 | 0.20599 | 0.15106 | 0.10529 | -122.2183 | 0.16937 | 0.14191 | 0.11902 | -122.2
4921.8281 | 122.2321 | -0.073242 | 122.0444 | 0.071411 | 0.04271 | 0.059686 | 0.0031873 | 0.031037 | -0.0070902 | 0.027869 | 0.12085 | 0.014234 | 0.032823 | 0.054156 | -0.0015317 | 0.033767 | 0.032043 | 0.082397 | 0.054932 | 0.022888 | 0.036621 | 0.027466 | -0.11444 | 0.09613 | 0.07782 | -0.018311 | 0.004578 | 0 | -0.045776 | -0.09613 | 0.10071 | -0.041199 | -122.0078 | 0.15564 | 0.09613 | 0.13733 | -122.0123 | 0.027466 | -0.022888 | -122.0398 | 0.16937 | 0.054931 | 0.077819 | -122.0444 | 0.10986 | 0.10529 | 0.12817 | -122.1588 | 0.07782 | 0.073242 | 0.15106 | -122.1405
4923.5938 | 122.168 | -0.10529 | 122.0764 | -0.088806 | 0.051041 | 0.059473 | 0.0031873 | 0.028901 | -4.058e-05 | 0.028937 | -0.13855 | 0.016584 | 0.035173 | 0.054583 | 0.0027407 | 0.031845 | 0.059509 | 0.018311 | 0.004578 | 0.004578 | 0.07782 | -0.004578 | -0.14648 | 0.064087 | 0.068665 | -0.082397 | 0.041199 | 0.022888 | -0.064087 | -0.1236 | 0.10071 | -0.041198 | -121.9986 | 0.1236 | 0.10986 | 0.15106 | -122.0169 | 0.041199 | -0.01831 | -122.0352 | 0.16937 | 0.022889 | 0.041199 | -122.0535 | 0.18311 | 0.16479 | 0.10986 | -122.2229 | 0.14649 | 0.12817 | 0.17395 | -122.2
4925.3594 | 122.168 | -0.10529 | 122.0947 | -0.21851 | 0.049332 | 0.061395 | 0.0061781 | 0.02826 | -0.004954 | 0.029578 | -0.2301 | 0.014447 | 0.036668 | 0.056292 | 0.00017731 | 0.034835 | -0.036621 | -0.045776 | -0.041199 | -0.036621 | 0.086975 | -0.032043 | -0.16937 | -0.004578 | 0.009155 | -0.10529 | 0.050354 | 0.041199 | -0.09613 | -0.12817 | 0.073243 | -0.064087 | -122.0078 | 0.05951 | 0.068665 | 0.13275 | -122.1313 | 0.009156 | -0.022888 | -122.0444 | 0.10071 | 0 | 0.022888 | -122.0535 | 0.19226 | 0.068665 | 0.064087 | -122.2641 | 0.15564 | 0.14649 | 0.11444 | -122.2229
4927.0625 | 122.2641 | -0.07782 | 122.049 | -0.13458 | 0.0457 | 0.060968 | 0.0051099 | 0.029542 | -0.007731 | 0.02851 | -0.16144 | 0.012311 | 0.035387 | 0.054369 | -0.0036679 | 0.030777 | 0.086975 | 0.13733 | 0.10529 | 0.068665 | 0.059509 | 0.018311 | -0.13275 | 0.11444 | 0.15564 | 0.050354 | 0 | 0 | -0.045776 | -0.09613 | 0.096131 | -0.054931 | -121.9894 | 0.21515 | 0.14649 | 0.20142 | -121.962 | 0.032044 | -0.01831 | -122.049 | 0.19226 | 0.12817 | 0.14648 | -122.049 | 0.13733 | 0.16479 | 0.18311 | -122.1817 | 0.07782 | 0.07782 | 0.23346 | -122.1451
4928.8281 | 122.1542 | -0.12817 | 122.0947 | 0.025635 | 0.0504 | 0.059259 | 0.0021191 | 0.028688 | 0.0027364 | 0.031074 | -0.024109 | 0.015943 | 0.035387 | 0.053942 | 0.0053043 | 0.031631 | -0.022888 | -0.068665 | -0.054932 | -0.036621 | 0.07782 | -0.004578 | -0.15106 | -0.004578 | -0.027466 | -0.14191 | 0.054932 | 0.032043 | -0.07782 | -0.13733 | 0.1236 | -0.022888 | -122.0169 | 0.059509 | 0.091553 | 0.11444 | -122.1176 | 0.050354 | -0.009155 | -122.0398 | 0.1236 | -0.013733 | -0.004578 | -122.0627 | 0.20599 | 0.10529 | 0.073242 | -122.2458 | 0.18311 | 0.16022 | 0.10071 | -122.2321
4930.6094 | 122.2 | -0.13275 | 122.0901 | -0.22614 | 0.048477 | 0.062677 | 0.0038281 | 0.029328 | -0.0051676 | 0.028724 | -0.26062 | 0.012952 | 0.036027 | 0.054156 | 0.00017731 | 0.033981 | -0.045776 | -0.045776 | -0.054932 | -0.027466 | 0.064087 | -0.022888 | -0.15564 | -0.004578 | 0.009155 | -0.09613 | 0.073242 | 0.045776 | -0.086975 | -0.13275 | 0.10986 | -0.022889 | -122.0261 | 0.086975 | 0.10529 | 0.12817 | -122.1359 | 0.045776 | 0 | -122.0169 | 0.12817 | 0.036621 | 0.036621 | -122.0444 | 0.19684 | 0.086975 | 0.077819 | -122.2458 | 0.20599 | 0.17853 | 0.14191 | -122.2229
4932.375 | 122.2275 | -0.082397 | 122.0398 | 0.094299 | 0.044632 | 0.058832 | 0.0025465 | 0.029542 | -0.0068766 | 0.028083 | 0.11322 | 0.013806 | 0.033464 | 0.052233 | -0.00089089 | 0.036331 | 0.013733 | 0.068665 | 0.054932 | 0.009155 | 0.041199 | 0.009155 | -0.1236 | 0.086975 | 0.068665 | -0.022888 | 0.004578 | -0.004578 | -0.050354 | -0.10071 | 0.091552 | -0.041199 | -121.9986 | 0.15106 | 0.091552 | 0.13275 | -122.0261 | 0.032043 | -0.018311 | -122.0352 | 0.16937 | 0.059509 | 0.07782 | -122.0444 | 0.1236 | 0.09613 | 0.13733 | -122.1634 | 0.086975 | 0.077819 | 0.15106 | -122.1405
4934.0781 | 122.2412 | -0.07782 | 122.0581 | 0.14771 | 0.045487 | 0.059686 | -0.0015125 | 0.027192 | -0.0053812 | 0.026588 | 0.13611 | 0.011029 | 0.034105 | 0.053728 | 0.0029543 | 0.034408 | 0.082397 | 0.10071 | 0.091553 | 0.045776 | 0.041199 | 0.013733 | -0.1236 | 0.1236 | 0.11902 | 0.004578 | -0.009155 | -0.009155 | -0.032043 | -0.086975 | 0.091553 | -0.045776 | -122.0169 | 0.17853 | 0.1236 | 0.16937 | -121.9757 | 0.045777 | -0.009155 | -122.0673 | 0.20142 | 0.082398 | 0.091553 | -122.0673 | 0.11902 | 0.16022 | 0.16937 | -122.1817 | 0.068665 | 0.068665 | 0.19684 | -122.1451
4935.8438 | 122.2549 | -0.086975 | 122.0535 | 0.14008 | 0.046555 | 0.05755 | 0.0019055 | 0.02826 | -0.0030314 | 0.028083 | 0.12848 | 0.012525 | 0.034318 | 0.052874 | 0.0018863 | 0.032486 | 0.073242 | 0.091553 | 0.059509 | 0.041199 | 0.045776 | 0.022888 | -0.11902 | 0.14648 | 0.11444 | 0.018311 | 0.009155 | 0.004578 | -0.041199 | -0.10529 | 0.10986 | -0.032044 | -122.0078 | 0.17853 | 0.12817 | 0.16022 | -121.9803 | 0.045776 | -0.018311 | -122.0444 | 0.23346 | 0.10529 | 0.1236 | -122.049 | 0.13275 | 0.16022 | 0.14648 | -122.1725 | 0.09613 | 0.091553 | 0.20142 | -122.1588
4937.5469 | 122.2137 | -0.10071 | 122.0764 | -0.20325 | 0.046341 | 0.059045 | 0.0031873 | 0.030824 | -0.0030314 | 0.02851 | -0.2301 | 0.016156 | 0.034105 | 0.054796 | 0.0018863 | 0.032699 | -0.009155 | -0.036621 | -0.064087 | -0.018311 | 0.07782 | -0.027466 | -0.15564 | 0.009155 | 0.027466 | -0.10071 | 0.032043 | 0.032043 | -0.091553 | -0.13733 | 0.073242 | -0.054932 | -121.9986 | 0.064087 | 0.082397 | 0.13733 | -122.0856 | 0.009155 | -0.036621 | -122.0444 | 0.10986 | 0 | 0.036621 | -122.0444 | 0.17853 | 0.091553 | 0.036621 | -122.2321 | 0.13275 | 0.13275 | 0.12817 | -122.2137
4939.3281 | 122.2687 | -0.091553 | 122.0398 | 0.025635 | 0.046982 | 0.061395 | 0.0021191 | 0.028688 | -0.0092264 | 0.028724 | 0.021668 | 0.01167 | 0.03261 | 0.054796 | -3.629e-05 | 0.034835 | 0.027466 | 0.022888 | 0.032043 | 0.004578 | 0.068665 | 0.004578 | -0.14191 | 0.050354 | 0.059509 | -0.018311 | 0.013733 | -0.004578 | -0.045776 | -0.11902 | 0.096131 | -0.050354 | -121.9711 | 0.11444 | 0.096131 | 0.14649 | -122.0123 | 0.045777 | -0.027466 | -122.0261 | 0.14191 | 0.073242 | 0.10071 | -122.0444 | 0.16022 | 0.11902 | 0.1236 | -122.1817 | 0.10529 | 0.086975 | 0.15106 | -122.1588
4941.0312 | 122.2824 | -0.082397 | 122.0352 | -0.020142 | 0.043564 | 0.060754 | -0.00065795 | 0.026338 | -0.0068766 | 0.027656 | -0.0088499 | 0.01402 | 0.033037 | 0.053515 | -0.00024989 | 0.036758 | 0.032043 | 0.036621 | 0.032043 | 0.018311 | 0.050354 | 0 | -0.11902 | 0.07782 | 0.086975 | -0.004578 | 0.009155 | -0.004578 | -0.064087 | -0.09613 | 0.082397 | -0.036622 | -121.9849 | 0.11902 | 0.10071 | 0.13733 | -122.0032 | 0.01831 | -0.013733 | -122.0261 | 0.16022 | 0.077819 | 0.091552 | -122.0398 | 0.13275 | 0.11444 | 0.11444 | -122.1542 | 0.091552 | 0.077819 | 0.16937 | -122.1313
4942.7344 | 122.2504 | -0.068665 | 122.0123 | 0.14008 | 0.047196 | 0.06225 | -1.7146e-05 | 0.029542 | -0.0019632 | 0.029792 | 0.12848 | 0.012525 | 0.031541 | 0.054156 | 0.0020999 | 0.033767 | 0.09613 | 0.082397 | 0.086975 | 0.054932 | 0.036621 | 0.032043 | -0.11444 | 0.14648 | 0.10986 | 0 | -0.022888 | -0.018311 | -0.036621 | -0.10071 | 0.10071 | -0.045776 | -121.9757 | 0.15106 | 0.1236 | 0.16937 | -121.9162 | 0.032044 | -0.032043 | -122.0352 | 0.21515 | 0.068665 | 0.10071 | -122.0306 | 0.10529 | 0.16479 | 0.15564 | -122.1268 | 0.045777 | 0.050354 | 0.17853 | -122.113
4944.5 | 122.1954 | -0.10986 | 122.0673 | -0.23376 | 0.048905 | 0.059045 | 0.0048963 | 0.03061 | -0.0034586 | 0.027656 | -0.25299 | 0.015515 | 0.035814 | 0.055437 | 0.0020999 | 0.034835 | -0.009155 | -0.041199 | -0.045776 | -0.027466 | 0.10071 | -0.027466 | -0.16937 | 0.009155 | 0.009155 | -0.11444 | 0.041199 | 0.036621 | -0.10529 | -0.12817 | 0.082397 | -0.05951 | -121.9666 | 0.068664 | 0.082397 | 0.14191 | -122.0764 | 0.004577 | -0.018311 | -122.0261 | 0.11902 | -0.004578 | 0.013733 | -122.0306 | 0.21057 | 0.10071 | 0.064087 | -122.2366 | 0.15106 | 0.14648 | 0.11902 | -122.1954
4946.2188 | 122.2046 | -0.10986 | 122.049 | -0.12695 | 0.050614 | 0.060327 | 0.0021191 | 0.031465 | -0.00025418 | 0.030219 | -0.1767 | 0.013593 | 0.034318 | 0.053515 | 0.0038089 | 0.031631 | 0.041199 | 0.032043 | -0.009155 | 0 | 0.073242 | -0.009155 | -0.15106 | 0.050354 | 0.054932 | -0.073242 | 0.032043 | 0.022888 | -0.07782 | -0.13275 | 0.10071 | -0.041199 | -121.9757 | 0.14191 | 0.10986 | 0.15106 | -122.0078 | 0.032043 | -0.022888 | -122.0169 | 0.16022 | 0.036621 | 0.059509 | -122.0261 | 0.18311 | 0.15106 | 0.10071 | -122.2 | 0.14191 | 0.13275 | 0.16479 | -122.1817
4947.9844 | 122.2687 | -0.091553 | 122.0169 | -0.0048827 | 0.044205 | 0.060754 | 0.0012647 | 0.028688 | -0.007731 | 0.027442 | 0.044556 | 0.010388 | 0.032396 | 0.053087 | -3.629e-05 | 0.035476 | -0.022888 | 0.032043 | 0.032043 | 0.013733 | 0.054932 | 0.004578 | -0.14191 | 0.045776 | 0.064087 | -0.013733 | 0.013733 | 0.009155 | -0.045776 | -0.11902 | 0.096131 | -0.050354 | -121.962 | 0.1236 | 0.10529 | 0.15564 | -122.0398 | 0.045777 | -0.027466 | -122.0032 | 0.13733 | 0.07782 | 0.10529 | -122.0078 | 0.14649 | 0.068665 | 0.1236 | -122.1588 | 0.10529 | 0.10071 | 0.15564 | -122.1359
4949.75 | 122.1725 | -0.11444 | 122.081 | -0.20325 | 0.047196 | 0.058405 | 0.0061781 | 0.026551 | -0.0030314 | 0.028937 | -0.23773 | 0.017224 | 0.033891 | 0.057787 | -0.0015317 | 0.03334 | -0.022888 | -0.036621 | -0.036621 | -0.045776 | 0.086975 | -0.045776 | -0.16937 | 0 | 0.018311 | -0.10529 | 0.045776 | 0.045776 | -0.091553 | -0.11902 | 0.068665 | -0.054932 | -121.994 | 0.07782 | 0.068665 | 0.1236 | -122.1039 | 0.022888 | -0.004578 | -122.0352 | 0.11444 | 0.009155 | 0.013733 | -122.0352 | 0.20142 | 0.091553 | 0.07782 | -122.2504 | 0.16022 | 0.16022 | 0.13275 | -122.2
4951.4531 | 122.1588 | -0.1236 | 122.0718 | -0.22614 | 0.046982 | 0.060114 | 0.0031873 | 0.030824 | -0.004313 | 0.02851 | -0.22247 | 0.01402 | 0.033678 | 0.053301 | -0.00024989 | 0.034835 | 0.041199 | 0.07782 | 0.050354 | 0.032043 | 0.054932 | 0 | -0.15564 | 0.041199 | 0.073242 | -0.068665 | 0.036621 | 0.018311 | -0.064087 | -0.1236 | 0.1236 | -0.032044 | -122.0169 | 0.20142 | 0.15564 | 0.18768 | -122.0306 | 0.059509 | 0 | -122.0352 | 0.16479 | 0.054931 | 0.054931 | -122.0535 | 0.17853 | 0.16479 | 0.17395 | -122.2275 | 0.16022 | 0.14191 | 0.19684 | -122.1954
4953.2031 | 122.2046 | -0.10071 | 122.0581 | -0.21088 | 0.050186 | 0.060114 | 0.0055371 | 0.028047 | 0.0012412 | 0.029792 | -0.21484 | 0.015515 | 0.036241 | 0.057146 | -0.00089089 | 0.032272 | -0.022888 | -0.045776 | -0.045776 | -0.018311 | 0.082397 | -0.009155 | -0.15564 | 0 | 0.013733 | -0.1236 | 0.045776 | 0.041199 | -0.073242 | -0.13733 | 0.091553 | -0.054932 | -121.9757 | 0.054932 | 0.082397 | 0.13733 | -122.081 | 0.027466 | -0.036621 | -122.0123 | 0.10071 | -0.022888 | 0.013733 | -122.0169 | 0.18311 | 0.07782 | 0.054932 | -122.2137 | 0.14648 | 0.14191 | 0.11444 | -122.1954
4954.9062 | 122.1588 | -0.1236 | 122.0856 | -0.21851 | 0.049118 | 0.0599 | 0.0074597 | 0.031251 | -0.0058084 | 0.030219 | -0.2301 | 0.014234 | 0.034746 | 0.053301 | -3.629e-05 | 0.034408 | 0.050354 | 0.068665 | 0.045776 | 0.032043 | 0.064087 | 0 | -0.14648 | 0.041199 | 0.082397 | -0.054932 | 0.022888 | 0.018311 | -0.068665 | -0.11902 | 0.1236 | -0.022888 | -122.0215 | 0.19226 | 0.15564 | 0.17853 | -122.0352 | 0.054931 | 0.004577 | -122.0627 | 0.16479 | 0.068664 | 0.064087 | -122.0673 | 0.18768 | 0.17395 | 0.16937 | -122.2321 | 0.14648 | 0.14191 | 0.20599 | -122.2046
4956.6719 | 122.1588 | -0.10986 | 122.0718 | -0.096436 | 0.051895 | 0.058191 | 0.0019055 | 0.029115 | 0.00017302 | 0.030646 | -0.16144 | 0.017438 | 0.033891 | 0.058642 | 0.0046633 | 0.034195 | 0.045776 | 0.041199 | 0.004578 | 0.004578 | 0.091553 | -0.009155 | -0.17395 | 0.07782 | 0.064087 | -0.082397 | 0.036621 | 0.027466 | -0.073242 | -0.12817 | 0.10071 | -0.064087 | -121.9803 | 0.15106 | 0.11444 | 0.17853 | -122.0261 | 0.036621 | -0.018311 | -122.0352 | 0.18768 | 0.027466 | 0.045777 | -122.0444 | 0.20142 | 0.15564 | 0.11444 | -122.2458 | 0.14648 | 0.13733 | 0.17395 | -122.2
4958.4375 | 122.1954 | -0.1236 | 122.0581 | -0.22614 | 0.050186 | 0.0599 | 0.0057507 | 0.031251 | -0.0038858 | 0.028937 | -0.2301 | 0.014661 | 0.036668 | 0.054369 | 0.00017731 | 0.032486 | -0.045776 | -0.013733 | -0.045776 | -0.027466 | 0.086975 | -0.018311 | -0.19226 | 0.004578 | 0.009155 | -0.11444 | 0.050354 | 0.045776 | -0.09613 | -0.12817 | 0.10528 | -0.068665 | -121.9711 | 0.10986 | 0.09613 | 0.16479 | -122.1039 | 0.027466 | -0.004578 | -122.0078 | 0.12817 | 0.009155 | 0.013733 | -122.0123 | 0.21057 | 0.07782 | 0.07782 | -122.2504 | 0.17395 | 0.16937 | 0.13275 | -122.1863
4960.2031 | 122.2321 | -0.086975 | 122.0352 | -0.18799 | 0.047623 | 0.060114 | 0.0036145 | 0.029756 | -0.0098672 | 0.028297 | -0.14618 | 0.012097 | 0.034746 | 0.053301 | -0.0021725 | 0.033981 | 0.041199 | 0.12817 | 0.086975 | 0.068665 | 0.045776 | 0.022888 | -0.11902 | 0.11444 | 0.16937 | 0.027466 | -0.004578 | -0.009155 | -0.032043 | -0.091553 | 0.10986 | -0.032044 | -121.9894 | 0.21515 | 0.15564 | 0.18768 | -121.994 | 0.054932 | -0.004578 | -122.0398 | 0.20142 | 0.11444 | 0.11902 | -122.0444 | 0.13275 | 0.12817 | 0.17395 | -122.1542 | 0.082397 | 0.07782 | 0.25635 | -122.1268
4961.9062 | 122.2046 | -0.10986 | 122.049 | -0.19562 | 0.050614 | 0.059473 | 0.0048963 | 0.02527 | -0.00046778 | 0.028083 | -0.2301 | 0.016156 | 0.0356 | 0.055865 | 0.0018863 | 0.033554 | -0.027466 | 0 | -0.036621 | -0.004578 | 0.082397 | -0.013733 | -0.16479 | 0.013733 | 0.045776 | -0.091553 | 0.064087 | 0.018311 | -0.073242 | -0.14191 | 0.09613 | -0.054932 | -121.9666 | 0.10986 | 0.10529 | 0.16022 | -122.0764 | 0.036621 | -0.032044 | -121.9849 | 0.1236 | 0.01831 | 0.050354 | -122.0306 | 0.19226 | 0.082397 | 0.073242 | -122.2137 | 0.17395 | 0.12817 | 0.15564 | -122.1909
4963.6719 | 122.2046 | -0.10529 | 122.0673 | -0.20325 | 0.051895 | 0.059686 | 0.0029737 | 0.028474 | -0.00089518 | 0.030219 | -0.21484 | 0.013806 | 0.033891 | 0.054796 | 0.0031681 | 0.035049 | -0.022888 | -0.013733 | -0.041199 | 0.004578 | 0.07782 | -0.018311 | -0.1831 | 0.032043 | 0.045776 | -0.073242 | 0.036621 | 0.032043 | -0.082397 | -0.1236 | 0.086975 | -0.077819 | -121.9894 | 0.091553 | 0.10986 | 0.18768 | -122.0901 | 0.022889 | -0.01831 | -122.0306 | 0.13733 | 0.032044 | 0.050354 | -122.0352 | 0.18311 | 0.082398 | 0.064087 | -122.2504 | 0.14191 | 0.13733 | 0.15106 | -122.1909
4965.3594 | 122.2504 | -0.091553 | 122.0261 | 0.08667 | 0.044419 | 0.063318 | -0.00023075 | 0.028474 | -0.0064492 | 0.029151 | 0.11322 | 0.013593 | 0.032396 | 0.054583 | -3.629e-05 | 0.036331 | 0.009155 | 0.091553 | 0.059509 | 0.018311 | 0.036621 | 0.022888 | -0.11444 | 0.09613 | 0.064087 | -0.009155 | 0.018311 | -0.009155 | -0.050354 | -0.10986 | 0.11444 | -0.022888 | -121.9894 | 0.18311 | 0.10986 | 0.13275 | -122.0169 | 0.041199 | -0.01831 | -122.0078 | 0.18768 | 0.082398 | 0.10071 | -122.0352 | 0.12817 | 0.10071 | 0.15106 | -122.1405 | 0.10986 | 0.082398 | 0.15564 | -122.1359
4967.1406 | 122.2 | -0.11444 | 122.0352 | -0.22614 | 0.051468 | 0.061609 | 0.0081007 | 0.029115 | -0.0011088 | 0.028937 | -0.20721 | 0.018079 | 0.035387 | 0.056292 | 0.0012455 | 0.035049 | -0.027466 | -0.032043 | -0.064087 | -0.027466 | 0.091553 | -0.027466 | -0.17395 | -0.009155 | 0.013733 | -0.11444 | 0.041199 | 0.032043 | -0.082397 | -0.14191 | 0.086975 | -0.059509 | -121.9437 | 0.082398 | 0.086975 | 0.14648 | -122.0627 | 0.032044 | -0.027466 | -121.994 | 0.10529 | 0 | 0.027466 | -122.0032 | 0.20599 | 0.086975 | 0.050354 | -122.2092 | 0.15564 | 0.14648 | 0.12817 | -122.1771
4968.9062 | 122.2687 | -0.068665 | 122.0123 | 0.10193 | 0.044632 | 0.060541 | 0.00019645 | 0.028688 | -0.00089518 | 0.030219 | 0.13611 | 0.015515 | 0.03261 | 0.057146 | 0.0038089 | 0.035904 | -0.018311 | -0.018311 | -0.022888 | -0.022888 | 0.091553 | 0.009155 | -0.14648 | 0.07782 | 0.032043 | -0.050354 | 0.022888 | 0.013733 | -0.059509 | -0.11902 | 0.07782 | -0.077819 | -121.9208 | 0.050354 | 0.045777 | 0.1236 | -122.0306 | 0.009156 | -0.050354 | -121.9894 | 0.14649 | 0.018311 | 0.068665 | -121.9986 | 0.16022 | 0.050354 | 0.045777 | -122.1588 | 0.091553 | 0.082398 | 0.10071 | -122.1313
4970.6094 | 122.2778 | -0.068665 | 122.0215 | 0.094299 | 0.048691 | 0.0599 | 0.00083745 | 0.027406 | -0.0030314 | 0.030219 | 0.159 | 0.017011 | 0.031114 | 0.055651 | 0.0046633 | 0.035904 | -0.013733 | 0.004578 | -0.032043 | -0.027466 | 0.068665 | -0.004578 | -0.16022 | 0.068665 | 0.036621 | -0.064087 | 0.018311 | 0.027466 | -0.032043 | -0.10529 | 0.064087 | -0.091552 | -121.9528 | 0.073243 | 0.041199 | 0.13275 | -122.0352 | 0.036622 | -0.036621 | -122.0032 | 0.13733 | 0.004578 | 0.041199 | -121.994 | 0.13733 | 0.054932 | 0.036622 | -122.1817 | 0.086976 | 0.096131 | 0.10529 | -122.1268
4972.375 | 122.2961 | -0.073242 | 122.0032 | -0.058289 | 0.046555 | 0.060114 | 0.0057507 | 0.025697 | -0.010508 | 0.028724 | 0.0064086 | 0.012525 | 0.035173 | 0.055224 | -0.0017453 | 0.037185 | -0.004578 | 0.073242 | 0.064087 | 0.032043 | 0.045776 | 0.027466 | -0.12817 | 0.09613 | 0.11444 | 0.022888 | 0.009155 | -0.004578 | -0.041199 | -0.09613 | 0.10071 | -0.054932 | -121.9574 | 0.14648 | 0.10529 | 0.16022 | -122.0078 | 0.032043 | -0.022888 | -121.994 | 0.16937 | 0.09613 | 0.11902 | -122.0078 | 0.11902 | 0.068664 | 0.13733 | -122.1313 | 0.082397 | 0.068664 | 0.18768 | -122.0993
4974.1406 | 122.1313 | -0.11444 | 122.0215 | 0.071411 | 0.047837 | 0.060754 | 0.00083745 | 0.029328 | 0.0014548 | 0.02851 | 0.082703 | 0.015943 | 0.035173 | 0.056505 | 0.0027407 | 0.032272 | -0.022888 | -0.050354 | -0.054932 | -0.032043 | 0.082397 | -0.009155 | -0.15106 | 0.009155 | -0.036621 | -0.11902 | 0.050354 | 0.036621 | -0.07782 | -0.15106 | 0.10529 | -0.036621 | -121.9391 | 0.064087 | 0.082398 | 0.11902 | -122.0444 | 0.036621 | -0.036621 | -121.9711 | 0.1236 | -0.004578 | 0.032043 | -121.9849 | 0.19684 | 0.091553 | 0.059509 | -122.1725 | 0.16479 | 0.15106 | 0.07782 | -122.1725
4975.9062 | 122.2549 | -0.064087 | 122.0032 | 0.10193 | 0.047409 | 0.059686 | 0.0042555 | 0.029115 | -0.0023904 | 0.031928 | 0.090332 | 0.016584 | 0.031755 | 0.054156 | 0.0044497 | 0.032272 | 0.068665 | 0.059509 | 0.050354 | 0.059509 | 0.059509 | 0.041199 | -0.1236 | 0.13275 | 0.11444 | -0.013733 | -0.009155 | 0 | -0.036621 | -0.09613 | 0.10529 | -0.059509 | -121.9437 | 0.1236 | 0.1236 | 0.1831 | -121.9345 | 0.027466 | -0.032043 | -122.0123 | 0.19684 | 0.050354 | 0.082397 | -122.0032 | 0.1236 | 0.13275 | 0.11444 | -122.1268 | 0.054932 | 0.064087 | 0.17853 | -122.0993
4977.6875 | 122.1771 | -0.091553 | 122.0444 | -0.13458 | 0.053604 | 0.058618 | 0.0053235 | 0.028901 | -0.0011088 | 0.030006 | -0.12329 | 0.015943 | 0.037309 | 0.055865 | -0.0013181 | 0.032058 | 0.036621 | 0.022888 | 0 | 0.009155 | 0.082397 | -0.004578 | -0.17395 | 0.054932 | 0.068665 | -0.068665 | 0.027466 | 0.022888 | -0.059509 | -0.11902 | 0.086975 | -0.082397 | -121.962 | 0.11444 | 0.10071 | 0.1831 | -122.0078 | 0.032044 | -0.027466 | -122.0169 | 0.14649 | 0.022888 | 0.050354 | -122.0215 | 0.17395 | 0.12817 | 0.091553 | -122.2183 | 0.11902 | 0.11444 | 0.16022 | -122.1634
4979.4531 | 122.2504 | -0.068665 | 122.0078 | 0.14008 | 0.046768 | 0.059473 | 0.0021191 | 0.027619 | -0.0038858 | 0.030433 | 0.19714 | 0.013806 | 0.03325 | 0.053728 | 0.0018863 | 0.03334 | 0.064087 | 0.09613 | 0.082397 | 0.050354 | 0.036621 | 0.027466 | -0.12817 | 0.12817 | 0.11444 | 0.022888 | 0.013733 | -0.009155 | -0.059509 | -0.09613 | 0.096131 | -0.059509 | -121.9711 | 0.16479 | 0.11902 | 0.17853 | -121.9437 | 0.009156 | -0.027465 | -121.994 | 0.19684 | 0.091553 | 0.11902 | -122.0169 | 0.10529 | 0.13275 | 0.15106 | -122.1359 | 0.082398 | 0.05951 | 0.18311 | -122.1039
4981.1562 | 122.1451 | -0.11444 | 122.0856 | -0.012512 | 0.051041 | 0.057336 | 0.0027601 | 0.02591 | 0.00081382 | 0.030646 | 0.044556 | 0.015729 | 0.034318 | 0.053728 | 0.0057315 | 0.032272 | 0 | -0.004578 | -0.032043 | -0.009155 | 0.082397 | 0.004578 | -0.14191 | 0.018311 | 0 | -0.1236 | 0.036621 | 0.050354 | -0.086975 | -0.12817 | 0.11902 | -0.027466 | -122.0032 | 0.10986 | 0.10529 | 0.13275 | -122.0856 | 0.027466 | -0.013733 | -122.049 | 0.13275 | -0.009155 | 0.004578 | -122.0352 | 0.19684 | 0.11444 | 0.082398 | -122.2275 | 0.15106 | 0.16479 | 0.11444 | -122.2137
4982.8594 | 122.2229 | -0.086975 | 122.0581 | 0.10193 | 0.049759 | 0.061395 | -0.00087155 | 0.029115 | -0.0013224 | 0.031074 | 0.067444 | 0.015943 | 0.031541 | 0.054156 | 0.0035953 | 0.034622 | -0.018311 | -0.054932 | -0.064087 | -0.036621 | 0.073242 | -0.018311 | -0.15106 | 0.013733 | -0.018311 | -0.11444 | 0.054932 | 0.041199 | -0.082397 | -0.13275 | 0.068664 | -0.064087 | -121.9849 | 0.032043 | 0.050354 | 0.11444 | -122.0764 | 0.004578 | -0.045776 | -122.0032 | 0.10071 | -0.027466 | 0.01831 | -122.0169 | 0.16022 | 0.068664 | 0.022888 | -122.2092 | 0.14191 | 0.12817 | 0.068664 | -122.1909
4984.625 | 122.1771 | -0.1236 | 122.0535 | 0.048523 | 0.049759 | 0.061182 | 0.0014783 | 0.027619 | -0.0021768 | 0.032355 | 0.067444 | 0.015302 | 0.034746 | 0.056078 | 0.0038089 | 0.032913 | -0.036621 | -0.059509 | -0.064087 | -0.036621 | 0.091553 | -0.004578 | -0.17395 | -0.009155 | -0.027466 | -0.1236 | 0.054932 | 0.041199 | -0.064087 | -0.1236 | 0.11902 | -0.050354 | -121.962 | 0.064087 | 0.086975 | 0.13733 | -122.0901 | 0.059509 | 0 | -121.9986 | 0.11444 | 0 | 0 | -122.0123 | 0.21515 | 0.086975 | 0.059509 | -122.2275 | 0.17853 | 0.16479 | 0.09613 | -122.1771
4986.3125 | 122.287 | -0.068665 | 122.0444 | -0.13458 | 0.04805 | 0.061609 | 0.0066053 | 0.025483 | -0.010722 | 0.028083 | -0.069885 | 0.012097 | 0.036027 | 0.053728 | -0.0038815 | 0.03569 | 0.059509 | 0.14191 | 0.10986 | 0.054932 | 0.041199 | 0 | -0.11444 | 0.10529 | 0.16479 | 0.032043 | 0.018311 | -0.009155 | -0.059509 | -0.09613 | 0.068665 | -0.045776 | -122.0032 | 0.21057 | 0.1236 | 0.16937 | -121.9849 | 0.009156 | -0.027465 | -122.0261 | 0.17395 | 0.10071 | 0.12817 | -122.0535 | 0.10986 | 0.12817 | 0.17853 | -122.1588 | 0.086976 | 0.05951 | 0.23346 | -122.1405
4988.0938 | 122.1634 | -0.11444 | 122.1313 | -0.24902 | 0.04805 | 0.060968 | 0.0076733 | 0.028474 | -0.0073038 | 0.028937 | -0.11566 | 0.012952 | 0.037096 | 0.055224 | -0.0013181 | 0.032913 | -0.009155 | 0.032043 | 0.004578 | 0.018311 | 0.082397 | 0 | -0.13733 | 0.009155 | 0.022888 | -0.09613 | 0.054932 | 0.036621 | -0.054932 | -0.1236 | 0.11444 | -0.022888 | -122.049 | 0.14648 | 0.13275 | 0.15564 | -122.1405 | 0.059509 | -0.009155 | -122.0764 | 0.1236 | 0.018311 | 0.027466 | -122.0947 | 0.19684 | 0.10529 | 0.11902 | -122.2687 | 0.16937 | 0.15106 | 0.13733 | -122.2549
4989.8594 | 122.1725 | -0.10986 | 122.0856 | -0.088806 | 0.049332 | 0.05755 | 0.0031873 | 0.026551 | 0.00081382 | 0.029578 | -0.077515 | 0.016156 | 0.038377 | 0.054796 | 0.0020999 | 0.031845 | 0.018311 | 0.018311 | -0.018311 | -0.013733 | 0.068665 | -0.004578 | -0.17395 | 0.036621 | 0.009155 | -0.11444 | 0.032043 | 0.027466 | -0.073242 | -0.12817 | 0.10529 | -0.064087 | -122.0169 | 0.12817 | 0.09613 | 0.16022 | -122.0673 | 0.036621 | -0.018311 | -122.0535 | 0.14648 | -0.004578 | 0.013733 | -122.0581 | 0.17853 | 0.12817 | 0.091552 | -122.2595 | 0.14191 | 0.13733 | 0.11902 | -122.2137
4991.5469 | 122.1954 | -0.10986 | 122.0901 | 0.071411 | 0.05275 | 0.055627 | 0.0072461 | 0.029969 | -0.0013224 | 0.029365 | 0.052185 | 0.015302 | 0.039018 | 0.054369 | 0.0012455 | 0.032913 | -0.032043 | -0.050354 | -0.050354 | -0.018311 | 0.082397 | -0.004578 | -0.15564 | 0.018311 | -0.032043 | -0.10986 | 0.054932 | 0.022888 | -0.059509 | -0.1236 | 0.10529 | -0.045777 | -122.0078 | 0.059509 | 0.091552 | 0.13733 | -122.1222 | 0.050354 | -0.013733 | -122.0352 | 0.12817 | 0 | 0.013733 | -122.0673 | 0.19226 | 0.07782 | 0.059509 | -122.2458 | 0.16479 | 0.13275 | 0.07782 | -122.2137
4993.3125 | 122.3236 | -0.086975 | 122.0535 | -0.058289 | 0.044419 | 0.061823 | 0.0038281 | 0.030397 | -0.010295 | 0.029151 | -0.0088499 | 0.010602 | 0.03325 | 0.052874 | -0.0028135 | 0.036331 | -0.018311 | 0.073242 | 0.054932 | 0.041199 | 0.050354 | 0.013733 | -0.12817 | 0.091553 | 0.1236 | 0.022888 | 0.004578 | 0.018311 | -0.041199 | -0.10529 | 0.10071 | -0.041199 | -122.0032 | 0.16022 | 0.12817 | 0.16937 | -122.0718 | 0.045776 | -0.018311 | -122.049 | 0.17853 | 0.10986 | 0.12817 | -122.0352 | 0.13733 | 0.068664 | 0.14191 | -122.1817 | 0.091553 | 0.10529 | 0.21057 | -122.1588
4995.0781 | 122.2687 | -0.073242 | 122.0398 | 0.12482 | 0.045487 | 0.061823 | -0.0038623 | 0.030183 | -0.0036722 | 0.028724 | 0.17426 | 0.012525 | 0.031755 | 0.053301 | 0.0040225 | 0.033126 | 0.059509 | 0.09613 | 0.082397 | 0.050354 | 0.050354 | 0.018311 | -0.11444 | 0.13733 | 0.10529 | 0.022888 | 0.009155 | 0 | -0.041199 | -0.07782 | 0.091553 | -0.041199 | -121.9894 | 0.16937 | 0.1236 | 0.16479 | -121.9803 | 0.032043 | -0.004578 | -122.0306 | 0.21057 | 0.09613 | 0.10071 | -122.0398 | 0.1236 | 0.13275 | 0.15564 | -122.1542 | 0.082397 | 0.073242 | 0.17853 | -122.1176
4996.8438 | 122.319 | -0.059509 | 122.049 | 0.15533 | 0.047196 | 0.060541 | 0.0014783 | 0.030397 | -0.0028178 | 0.028724 | 0.159 | 0.011243 | 0.031541 | 0.05266 | 0.0029543 | 0.034195 | 0.036621 | 0.064087 | 0.050354 | 0.032043 | 0.050354 | 0.013733 | -0.13275 | 0.11902 | 0.09613 | -0.004578 | 0 | -0.009155 | -0.041199 | -0.09613 | 0.073242 | -0.073242 | -121.9986 | 0.1236 | 0.091552 | 0.16479 | -122.0123 | 0.01831 | -0.036621 | -122.049 | 0.17853 | 0.054931 | 0.091552 | -122.0581 | 0.10986 | 0.09613 | 0.10986 | -122.1817 | 0.059509 | 0.050354 | 0.15564 | -122.1451
4998.6094 | 122.168 | -0.12817 | 122.1039 | -0.058289 | 0.051041 | 0.058405 | 0.0010511 | 0.029115 | 0.00060022 | 0.030646 | -0.069885 | 0.015515 | 0.03325 | 0.055865 | 0.0044497 | 0.03334 | 0.041199 | 0.027466 | -0.009155 | 0.004578 | 0.073242 | -0.004578 | -0.16479 | 0.027466 | 0.018311 | -0.09613 | 0.059509 | 0.022888 | -0.073242 | -0.13275 | 0.1236 | -0.036621 | -122.0306 | 0.15564 | 0.13275 | 0.16937 | -122.0627 | 0.054932 | -0.004577 | -122.0444 | 0.15564 | 0.032044 | 0.036621 | -122.081 | 0.20142 | 0.16937 | 0.11902 | -122.2687 | 0.18768 | 0.15106 | 0.14649 | -122.2366
5000.3125 | 122.2916 | -0.086975 | 122.0856 | -0.12695 | 0.0457 | 0.059473 | 0.0055371 | 0.027192 | -0.008372 | 0.027869 | -0.13092 | 0.012738 | 0.035387 | 0.053301 | -0.0038815 | 0.032272 | 0.054932 | 0.14648 | 0.11444 | 0.082397 | 0.050354 | 0.013733 | -0.12817 | 0.11444 | 0.16479 | 0.045776 | 0.004578 | 0 | -0.050354 | -0.09613 | 0.10071 | -0.041199 | -122.0352 | 0.23346 | 0.16937 | 0.21057 | -122.0306 | 0.036621 | -0.009155 | -122.081 | 0.20142 | 0.13275 | 0.14191 | -122.0856 | 0.13733 | 0.14191 | 0.20142 | -122.2137 | 0.091553 | 0.086975 | 0.25177 | -122.1817
5002.0938 | 122.2549 | -0.091553 | 122.0764 | 0.063782 | 0.043351 | 0.059686 | -1.7146e-05 | 0.029115 | -0.0075174 | 0.028937 | 0.097962 | 0.013806 | 0.031541 | 0.054583 | -0.00024989 | 0.034835 | 0.018311 | 0.059509 | 0.050354 | 0.022888 | 0.054932 | 0.022888 | -0.1236 | 0.082397 | 0.068665 | -0.013733 | 0.013733 | 0.004578 | -0.045776 | -0.10529 | 0.11444 | -0.032043 | -122.0215 | 0.15106 | 0.11444 | 0.14648 | -122.0581 | 0.045777 | -0.013733 | -122.0627 | 0.17395 | 0.07782 | 0.091553 | -122.0718 | 0.14649 | 0.10986 | 0.14191 | -122.2 | 0.10529 | 0.096131 | 0.16022 | -122.1817
5003.8594 | 122.2412 | -0.10986 | 122.1085 | -0.17273 | 0.049118 | 0.059045 | 0.0027601 | 0.030183 | -0.00025418 | 0.030006 | -0.19958 | 0.01402 | 0.033678 | 0.055865 | 0.0040225 | 0.032272 | 0.018311 | 0 | -0.009155 | 0.013733 | 0.073242 | -0.018311 | -0.15564 | 0.041199 | 0.045776 | -0.068665 | 0.054932 | 0.032043 | -0.064087 | -0.10986 | 0.091552 | -0.045777 | -122.0352 | 0.10986 | 0.1236 | 0.16937 | -122.0901 | 0.045776 | 0 | -122.0535 | 0.15106 | 0.041198 | 0.041198 | -122.0764 | 0.18311 | 0.12817 | 0.10071 | -122.2641 | 0.16479 | 0.14191 | 0.15564 | -122.2183
5005.5625 | 122.1771 | -0.1236 | 122.113 | -0.20325 | 0.048264 | 0.06225 | 0.0055371 | 0.028688 | -0.0051676 | 0.027869 | -0.20721 | 0.014447 | 0.036455 | 0.054583 | -0.0019589 | 0.035904 | 0.036621 | 0.086975 | 0.068665 | 0.041199 | 0.054932 | 0.009155 | -0.11444 | 0.054932 | 0.09613 | -0.022888 | 0.018311 | 0.027466 | -0.064087 | -0.11902 | 0.13275 | 0.009155 | -122.0581 | 0.21057 | 0.16479 | 0.15564 | -122.0764 | 0.059509 | 0.004577 | -122.0947 | 0.17853 | 0.10071 | 0.096131 | -122.0856 | 0.17853 | 0.16022 | 0.19226 | -122.2275 | 0.14191 | 0.15106 | 0.21973 | -122.2321
5007.3438 | 122.3236 | -0.064087 | 122.0627 | -0.081177 | 0.04271 | 0.062677 | 0.0036145 | 0.028688 | -0.0096536 | 0.02616 | -0.1004 | 0.013166 | 0.031969 | 0.054583 | -0.0021725 | 0.03569 | 0.054932 | 0.09613 | 0.082397 | 0.054932 | 0.064087 | 0.018311 | -0.1236 | 0.13275 | 0.15564 | 0.036621 | 0 | -0.009155 | -0.036621 | -0.10071 | 0.082398 | -0.059509 | -121.9986 | 0.16022 | 0.11902 | 0.17853 | -122.0078 | 0.027466 | -0.036621 | -122.0627 | 0.19684 | 0.10071 | 0.13733 | -122.0718 | 0.12817 | 0.11902 | 0.14648 | -122.1863 | 0.064087 | 0.054932 | 0.21973 | -122.1634
5009.0469 | 122.3236 | -0.07782 | 122.0673 | -0.020142 | 0.044632 | 0.059473 | 0.0019055 | 0.026979 | -0.0070902 | 0.028297 | 0.021668 | 0.012952 | 0.031328 | 0.05266 | -0.00067729 | 0.035904 | 0 | 0.032043 | 0.032043 | 0.009155 | 0.050354 | 0.013733 | -0.13733 | 0.07782 | 0.068665 | -0.004578 | 0.013733 | 0.004578 | -0.045776 | -0.10529 | 0.091553 | -0.059509 | -122.0169 | 0.10986 | 0.086975 | 0.14648 | -122.0673 | 0.032044 | -0.027466 | -122.0535 | 0.15564 | 0.073242 | 0.10071 | -122.0627 | 0.12817 | 0.07782 | 0.10986 | -122.2046 | 0.091553 | 0.082398 | 0.14649 | -122.1725
5010.75 | 122.2137 | -0.10529 | 122.0718 | 0.08667 | 0.046555 | 0.062036 | 0.0027601 | 0.029542 | 0.0016684 | 0.029578 | 0.052185 | 0.017652 | 0.031541 | 0.05501 | 0.0048769 | 0.033554 | -0.004578 | -0.045776 | -0.07782 | -0.041199 | 0.10071 | -0.009155 | -0.16022 | 0.027466 | -0.036621 | -0.1236 | 0.041199 | 0.041199 | -0.073242 | -0.10529 | 0.096131 | -0.054931 | -121.9711 | 0.05951 | 0.064087 | 0.11902 | -122.0764 | 0.032044 | 0 | -122.0306 | 0.13275 | -0.01831 | -0.01831 | -122.0306 | 0.20599 | 0.10071 | 0.027466 | -122.2321 | 0.14649 | 0.14649 | 0.068665 | -122.1771
5012.5312 | 122.1909 | -0.11444 | 122.0627 | -0.088806 | 0.049973 | 0.061823 | 0.0034009 | 0.028901 | 0.00038662 | 0.030219 | -0.16144 | 0.014875 | 0.034959 | 0.053301 | 0.0055179 | 0.032486 | 0.041199 | 0.054932 | -0.004578 | 0.004578 | 0.073242 | -0.004578 | -0.15564 | 0.073242 | 0.064087 | -0.09613 | 0.036621 | 0.018311 | -0.068665 | -0.1236 | 0.10986 | -0.041199 | -121.9894 | 0.16937 | 0.11902 | 0.16022 | -122.0215 | 0.045776 | -0.009155 | -122.0261 | 0.18768 | 0.018311 | 0.027466 | -122.0444 | 0.18768 | 0.15564 | 0.10986 | -122.2183 | 0.15106 | 0.13275 | 0.17853 | -122.1863
5014.2969 | 122.2137 | -0.10071 | 122.0993 | -0.19562 | 0.048477 | 0.059045 | 0.0044691 | 0.026979 | -0.0075174 | 0.029151 | -0.13855 | 0.015302 | 0.032182 | 0.053728 | -0.0021725 | 0.036758 | 0.059509 | 0.10529 | 0.09613 | 0.064087 | 0.059509 | 0.004578 | -0.10529 | 0.10529 | 0.14191 | 0.022888 | 0.018311 | 0.004578 | -0.036621 | -0.086975 | 0.10529 | -0.004578 | -122.0398 | 0.20599 | 0.1648 | 0.16937 | -122.0398 | 0.064087 | 0.013733 | -122.081 | 0.20599 | 0.1236 | 0.10986 | -122.0947 | 0.16022 | 0.16022 | 0.19684 | -122.2046 | 0.11902 | 0.10529 | 0.24262 | -122.1863
5016.0625 | 122.2687 | -0.073242 | 122.0581 | 0.094299 | 0.044632 | 0.060114 | -0.00065795 | 0.027192 | -0.0045266 | 0.027869 | 0.15137 | 0.014661 | 0.03325 | 0.054369 | 0.0016727 | 0.034622 | 0.073242 | 0.09613 | 0.068665 | 0.032043 | 0.050354 | 0.022888 | -0.10986 | 0.11444 | 0.086975 | 0.009155 | 0 | 0.004578 | -0.041199 | -0.10071 | 0.09613 | -0.036621 | -122.0078 | 0.16937 | 0.10529 | 0.14191 | -121.9849 | 0.032043 | -0.027466 | -122.0581 | 0.18768 | 0.082397 | 0.10986 | -122.0535 | 0.1236 | 0.14648 | 0.14191 | -122.168 | 0.073242 | 0.07782 | 0.16022 | -122.1588
5017.8281 | 122.3007 | -0.068665 | 122.0627 | 0.10956 | 0.047837 | 0.060754 | -1.7146e-05 | 0.029542 | -0.002604 | 0.030219 | 0.159 | 0.012738 | 0.034746 | 0.054583 | 0.0029543 | 0.034622 | 0.09613 | 0.09613 | 0.082397 | 0.064087 | 0.041199 | 0.018311 | -0.10071 | 0.13733 | 0.10071 | 0.022888 | -0.009155 | -0.009155 | -0.059509 | -0.07782 | 0.086976 | -0.032043 | -122.0215 | 0.16479 | 0.13275 | 0.1648 | -121.9666 | 0.009156 | -0.009155 | -122.0718 | 0.20599 | 0.091553 | 0.10071 | -122.0718 | 0.10986 | 0.16479 | 0.15106 | -122.1634 | 0.05951 | 0.05951 | 0.16937 | -122.1405
5019.5938 | 122.2 | -0.1236 | 122.113 | -0.22614 | 0.049332 | 0.059045 | 0.0046827 | 0.028688 | -0.001536 | 0.027869 | -0.18433 | 0.01402 | 0.035173 | 0.054583 | -0.0011045 | 0.033554 | 0 | -0.013733 | -0.013733 | -0.009155 | 0.082397 | -0.018311 | -0.16937 | 0.004578 | 0.022888 | -0.10529 | 0.041199 | 0.050354 | -0.086975 | -0.1236 | 0.10528 | -0.045777 | -122.0306 | 0.10986 | 0.11444 | 0.16022 | -122.113 | 0.036621 | 0 | -122.0718 | 0.12817 | 0.01831 | 0.01831 | -122.0627 | 0.20599 | 0.1236 | 0.10986 | -122.2824 | 0.16479 | 0.17395 | 0.14648 | -122.2366
5021.2969 | 122.3236 | -0.082397 | 122.0947 | 0.010376 | 0.047409 | 0.060754 | 0.0031873 | 0.027833 | -0.007731 | 0.02851 | 0.029297 | 0.013166 | 0.034532 | 0.055865 | -0.00067729 | 0.035904 | 0 | 0.032043 | 0.032043 | 0.009155 | 0.050354 | 0.009155 | -0.13275 | 0.07782 | 0.064087 | -0.009155 | 0.018311 | 0.004578 | -0.050354 | -0.10529 | 0.091552 | -0.050354 | -122.0444 | 0.11444 | 0.091552 | 0.14191 | -122.0947 | 0.032043 | -0.022889 | -122.0764 | 0.16022 | 0.073242 | 0.096131 | -122.0901 | 0.13275 | 0.082397 | 0.11444 | -122.2275 | 0.10071 | 0.086975 | 0.14648 | -122.2
5023.0625 | 122.3053 | -0.07782 | 122.0444 | -0.0354 | 0.045273 | 0.061395 | 0.0027601 | 0.027192 | -0.0053812 | 0.027442 | 0.029297 | 0.012738 | 0.031114 | 0.053728 | -0.0017453 | 0.033767 | 0.009155 | 0.032043 | 0.045776 | 0.018311 | 0.059509 | 0.013733 | -0.14191 | 0.07782 | 0.07782 | -0.032043 | 0.018311 | 0.013733 | -0.045776 | -0.10986 | 0.091553 | -0.064087 | -121.9849 | 0.10986 | 0.096131 | 0.16022 | -122.0352 | 0.032044 | -0.032043 | -122.0261 | 0.15564 | 0.045777 | 0.07782 | -122.0306 | 0.13733 | 0.086975 | 0.1236 | -122.1863 | 0.096131 | 0.091553 | 0.15564 | -122.1542
5024.8438 | 122.3053 | -0.068665 | 122.0764 | 0.010376 | 0.047196 | 0.0599 | 0.0061781 | 0.026124 | -0.0058084 | 0.027869 | -0.0012209 | 0.013593 | 0.036455 | 0.05501 | -0.00046349 | 0.03569 | 0.009155 | 0.036621 | 0.036621 | 0.013733 | 0.064087 | 0.013733 | -0.13733 | 0.064087 | 0.059509 | -0.027466 | 0.041199 | -0.004578 | -0.041199 | -0.10986 | 0.082398 | -0.068664 | -122.0123 | 0.10529 | 0.082398 | 0.15106 | -122.0673 | 0.027466 | -0.041198 | -122.0352 | 0.13275 | 0.041199 | 0.082397 | -122.081 | 0.13275 | 0.07782 | 0.10529 | -122.2137 | 0.10986 | 0.064087 | 0.12817 | -122.1863
5026.5469 | 122.3282 | -0.082397 | 122.0764 | -0.020142 | 0.043991 | 0.062036 | 0.0021191 | 0.026124 | -0.0047404 | 0.027869 | 0.0064086 | 0.015302 | 0.033891 | 0.053515 | 0.00017731 | 0.034195 | 0.018311 | 0.041199 | 0.036621 | 0.018311 | 0.054932 | 0.013733 | -0.1236 | 0.091553 | 0.082397 | -0.004578 | 0.013733 | 0.004578 | -0.064087 | -0.10071 | 0.09613 | -0.041199 | -122.0215 | 0.1236 | 0.10071 | 0.14191 | -122.0581 | 0.01831 | -0.018311 | -122.0627 | 0.17395 | 0.077819 | 0.09613 | -122.0718 | 0.13733 | 0.10071 | 0.11902 | -122.2 | 0.09613 | 0.086975 | 0.16479 | -122.1771
5028.3125 | 122.3282 | -0.073242 | 122.0856 | -0.058289 | 0.046341 | 0.061182 | 0.0044691 | 0.029115 | -0.003245 | 0.026588 | -0.046997 | 0.012738 | 0.033464 | 0.054796 | -0.00024989 | 0.03334 | 0.064087 | 0.073242 | 0.064087 | 0.050354 | 0.045776 | 0.022888 | -0.12817 | 0.14648 | 0.12817 | 0.036621 | 0 | -0.013733 | -0.041199 | -0.11444 | 0.09613 | -0.054932 | -122.0398 | 0.14648 | 0.1236 | 0.17853 | -122.0215 | 0.032043 | -0.041199 | -122.0856 | 0.21973 | 0.10986 | 0.15106 | -122.0993 | 0.11902 | 0.13733 | 0.13733 | -122.2137 | 0.073242 | 0.059509 | 0.20142 | -122.2
5030.0781 | 122.2778 | -0.082397 | 122.0352 | 0.12482 | 0.045273 | 0.058618 | -0.0021533 | 0.027192 | -0.00068138 | 0.028937 | 0.12848 | 0.01402 | 0.030046 | 0.053515 | 0.0031681 | 0.031845 | 0.10071 | 0.11444 | 0.068665 | 0.041199 | 0.041199 | 0.018311 | -0.11444 | 0.15106 | 0.10986 | -0.004578 | 0 | -0.022888 | -0.032043 | -0.09613 | 0.10071 | -0.032044 | -121.994 | 0.19684 | 0.1236 | 0.15564 | -121.9345 | 0.050354 | -0.013733 | -122.0352 | 0.23346 | 0.077819 | 0.091552 | -122.0581 | 0.1236 | 0.18311 | 0.15106 | -122.1497 | 0.082397 | 0.059509 | 0.19226 | -122.1313
5031.7812 | 122.3328 | -0.082397 | 122.0764 | -0.027771 | 0.046128 | 0.062463 | 0.0014783 | 0.028047 | -0.0073038 | 0.028083 | -0.039368 | 0.011029 | 0.031969 | 0.054583 | -0.00046349 | 0.03569 | 0.036621 | 0.050354 | 0.036621 | 0.018311 | 0.045776 | -0.004578 | -0.14191 | 0.10071 | 0.091553 | 0 | 0.013733 | 0 | -0.054932 | -0.10071 | 0.077819 | -0.05951 | -122.0306 | 0.13275 | 0.10071 | 0.16022 | -122.0398 | 0.027465 | -0.018311 | -122.0627 | 0.18311 | 0.082397 | 0.10071 | -122.0764 | 0.12817 | 0.11902 | 0.11902 | -122.2183 | 0.09613 | 0.082397 | 0.17395 | -122.1771
5033.5469 | 122.3145 | -0.07782 | 122.0764 | 0.071411 | 0.046341 | 0.059686 | 0.00019645 | 0.03061 | -0.00025418 | 0.032783 | 0.075073 | 0.01637 | 0.031969 | 0.05266 | 0.0038089 | 0.035904 | 0.10986 | 0.073242 | 0.050354 | 0.068665 | 0.036621 | 0.009155 | -0.12817 | 0.15564 | 0.10986 | 0.009155 | -0.004578 | -0.009155 | -0.045776 | -0.086975 | 0.086975 | -0.050354 | -122.0398 | 0.15106 | 0.14649 | 0.19684 | -121.9666 | 0.032044 | -0.009155 | -122.081 | 0.23346 | 0.086975 | 0.09613 | -122.0856 | 0.11444 | 0.18768 | 0.12817 | -122.2046 | 0.073242 | 0.068665 | 0.18768 | -122.1634
5035.2969 | 122.319 | -0.07782 | 122.0764 | -0.0048827 | 0.045487 | 0.061182 | 0.0021191 | 0.027406 | -0.0073038 | 0.030433 | 0.029297 | 0.012311 | 0.03261 | 0.053087 | -3.629e-05 | 0.036544 | 0.022888 | 0.045776 | 0.041199 | 0.018311 | 0.050354 | 0.022888 | -0.13733 | 0.064087 | 0.082397 | -0.022888 | 0.022888 | -0.004578 | -0.050354 | -0.11444 | 0.10071 | -0.059509 | -122.0261 | 0.1236 | 0.096131 | 0.15564 | -122.0535 | 0.027466 | -0.036621 | -122.0535 | 0.14191 | 0.054932 | 0.091553 | -122.081 | 0.12817 | 0.10071 | 0.11902 | -122.2137 | 0.10071 | 0.073242 | 0.16022 | -122.1909
5037.0781 | 122.3282 | -0.082397 | 122.0718 | -0.0048827 | 0.047623 | 0.060327 | 0.0063917 | 0.028688 | -0.0058084 | 0.029151 | -0.0012209 | 0.013593 | 0.03325 | 0.054156 | -0.00046349 | 0.036331 | 0.022888 | 0.036621 | 0.036621 | 0.013733 | 0.059509 | 0.018311 | -0.11902 | 0.09613 | 0.082397 | 0 | 0.018311 | 0.004578 | -0.045776 | -0.10986 | 0.10071 | -0.036622 | -122.0123 | 0.11902 | 0.09613 | 0.13275 | -122.049 | 0.036621 | -0.027466 | -122.0535 | 0.17853 | 0.082397 | 0.10986 | -122.0673 | 0.14191 | 0.10528 | 0.11902 | -122.1909 | 0.10071 | 0.086975 | 0.16479 | -122.1817
5038.7969 | 122.1909 | -0.1236 | 122.0901 | -0.23376 | 0.046128 | 0.059686 | 0.0070325 | 0.029542 | -0.0028178 | 0.02851 | -0.39795 | 0.015302 | 0.034532 | 0.055651 | -0.00046349 | 0.034408 | 0.018311 | 0.027466 | -0.009155 | -0.004578 | 0.082397 | -0.009155 | -0.16022 | 0.041199 | 0.027466 | -0.091553 | 0.036621 | 0.022888 | -0.086975 | -0.13275 | 0.11444 | -0.036621 | -122.0078 | 0.15106 | 0.11902 | 0.15564 | -122.0718 | 0.036621 | -0.009155 | -122.0535 | 0.16479 | 0.032043 | 0.041198 | -122.0673 | 0.20599 | 0.14191 | 0.11444 | -122.2504 | 0.16022 | 0.14648 | 0.15106 | -122.2229
5040.5625 | 122.3236 | -0.064087 | 122.081 | 0.10193 | 0.046768 | 0.059259 | -0.00065795 | 0.026979 | -0.0011088 | 0.030646 | 0.10559 | 0.013593 | 0.032396 | 0.055224 | 0.0044497 | 0.033981 | 0.032043 | 0.018311 | -0.022888 | -0.009155 | 0.082397 | 0 | -0.13733 | 0.10529 | 0.041199 | -0.054932 | 0.036621 | 0.004578 | -0.050354 | -0.10986 | 0.064087 | -0.073242 | -121.9986 | 0.082398 | 0.054932 | 0.12817 | -122.049 | 0.013733 | -0.045776 | -122.0444 | 0.16937 | 0.009155 | 0.054931 | -122.0764 | 0.14648 | 0.09613 | 0.041199 | -122.2183 | 0.10071 | 0.068665 | 0.10529 | -122.1909
5042.3281 | 122.2046 | -0.13275 | 122.1039 | -0.1651 | 0.0457 | 0.061395 | 0.00083745 | 0.026979 | -0.0034586 | 0.027015 | -0.23773 | 0.015302 | 0.03325 | 0.053728 | 0.0027407 | 0.036331 | -0.018311 | 0 | -0.027466 | -0.032043 | 0.10529 | -0.022888 | -0.18768 | 0.027466 | 0.027466 | -0.10986 | 0.054932 | 0.027466 | -0.091553 | -0.14191 | 0.10986 | -0.054932 | -121.9986 | 0.13275 | 0.10071 | 0.15564 | -122.1222 | 0.041198 | -0.009156 | -122.049 | 0.16022 | 0.022888 | 0.032044 | -122.0764 | 0.23804 | 0.11444 | 0.10529 | -122.2916 | 0.18768 | 0.16022 | 0.16022 | -122.2458
5044.1094 | 122.2778 | -0.054932 | 122.0901 | 0.14771 | 0.04805 | 0.062677 | 0.0010511 | 0.027406 | -0.0040994 | 0.030433 | 0.13611 | 0.013166 | 0.034532 | 0.056078 | 0.0018863 | 0.035476 | 0.082397 | 0.09613 | 0.09613 | 0.045776 | 0.059509 | 0.022888 | -0.11444 | 0.14191 | 0.13275 | 0.013733 | 0.009155 | -0.022888 | -0.027466 | -0.09613 | 0.07782 | -0.059509 | -122.0306 | 0.15106 | 0.10071 | 0.16022 | -122.0078 | 0.027466 | -0.041198 | -122.081 | 0.19684 | 0.068665 | 0.10986 | -122.113 | 0.11444 | 0.13733 | 0.15106 | -122.2046 | 0.064087 | 0.032044 | 0.18768 | -122.1863
5045.8125 | 122.3145 | -0.059509 | 122.0581 | 0.13245 | 0.046128 | 0.062891 | 0.0019055 | 0.030183 | -0.0021768 | 0.030646 | 0.12085 | 0.016584 | 0.034105 | 0.057146 | 0.0012455 | 0.034622 | 0.091553 | 0.091553 | 0.064087 | 0.064087 | 0.064087 | 0.045776 | -0.12817 | 0.13733 | 0.10986 | 0.009155 | 0.009155 | 0.004578 | -0.032043 | -0.082397 | 0.10528 | -0.068665 | -121.994 | 0.15106 | 0.1236 | 0.19226 | -121.9666 | 0.027466 | -0.022888 | -122.0489 | 0.19684 | 0.068664 | 0.091552 | -122.0535 | 0.1236 | 0.15106 | 0.1236 | -122.1863 | 0.068664 | 0.064087 | 0.16937 | -122.1405
5047.5781 | 122.2778 | -0.082397 | 122.0856 | 0.11719 | 0.046555 | 0.057977 | 0.0025465 | 0.029328 | -0.0055948 | 0.027869 | 0.10559 | 0.013593 | 0.03325 | 0.057146 | -0.00067729 | 0.03569 | 0.073242 | 0.11444 | 0.10071 | 0.036621 | 0.054932 | 0.027466 | -0.11444 | 0.14191 | 0.10986 | 0.027466 | 0.013733 | -0.022888 | -0.050354 | -0.091553 | 0.10986 | -0.032044 | -122.0306 | 0.19684 | 0.11902 | 0.15106 | -122.0123 | 0.032043 | -0.009156 | -122.0718 | 0.2243 | 0.10986 | 0.11902 | -122.1085 | 0.13733 | 0.15564 | 0.18311 | -122.2 | 0.09613 | 0.059509 | 0.19226 | -122.1771
5049.2812 | 122.2733 | -0.086975 | 122.0764 | 0.11719 | 0.043564 | 0.060541 | -0.00044435 | 0.027192 | -0.0038858 | 0.028083 | 0.097962 | 0.012738 | 0.030901 | 0.053301 | 0.0010317 | 0.036117 | 0.091553 | 0.10071 | 0.082397 | 0.045776 | 0.036621 | 0.036621 | -0.12817 | 0.1236 | 0.10986 | 0.022888 | 0.018311 | -0.009155 | -0.036621 | -0.09613 | 0.1236 | -0.041199 | -122.0398 | 0.18768 | 0.13275 | 0.17395 | -121.9849 | 0.050354 | -0.009155 | -122.0581 | 0.21057 | 0.10986 | 0.11902 | -122.0856 | 0.1236 | 0.17853 | 0.16937 | -122.2046 | 0.10529 | 0.07782 | 0.19684 | -122.1725
5051.0469 | 122.2229 | -0.1236 | 122.113 | -0.18036 | 0.046982 | 0.062891 | 0.0078871 | 0.028047 | -0.004954 | 0.028083 | -0.15381 | 0.011884 | 0.034318 | 0.053301 | -3.629e-05 | 0.033554 | 0.068665 | 0.10529 | 0.10071 | 0.059509 | 0.054932 | 0.027466 | -0.13275 | 0.11444 | 0.14191 | 0 | 0.009155 | 0 | -0.041199 | -0.09613 | 0.15106 | -0.009155 | -122.0581 | 0.22888 | 0.1831 | 0.19226 | -122.0444 | 0.082397 | 0.027466 | -122.1039 | 0.23804 | 0.1236 | 0.09613 | -122.113 | 0.17853 | 0.19226 | 0.2243 | -122.2458 | 0.13275 | 0.1236 | 0.2655 | -122.2092
5052.8281 | 122.2412 | -0.11444 | 122.1085 | -0.1651 | 0.049973 | 0.060541 | 0.00083745 | 0.032105 | 0.00017302 | 0.031287 | -0.22247 | 0.017224 | 0.033891 | 0.058214 | 0.0018863 | 0.032486 | 0.041199 | 0.013733 | -0.027466 | -0.004578 | 0.091553 | -0.009155 | -0.16022 | 0.050354 | 0.073242 | -0.068665 | 0.050354 | 0.027466 | -0.068665 | -0.12817 | 0.10529 | -0.045776 | -122.0169 | 0.12817 | 0.10986 | 0.15564 | -122.0673 | 0.045776 | -0.013733 | -122.0581 | 0.16479 | 0.045776 | 0.059509 | -122.081 | 0.20599 | 0.15564 | 0.086975 | -122.2687 | 0.16479 | 0.14191 | 0.18768 | -122.2366
5054.6094 | 122.2458 | -0.11902 | 122.1085 | -0.25665 | 0.048477 | 0.057764 | 0.0057507 | 0.027619 | -0.003245 | 0.029365 | -0.23773 | 0.015515 | 0.034959 | 0.056292 | -0.0011045 | 0.034195 | -0.022888 | 0 | -0.050354 | -0.032043 | 0.10071 | -0.036621 | -0.17853 | 0.009155 | 0.022888 | -0.10986 | 0.064087 | 0.041199 | -0.086975 | -0.13733 | 0.082398 | -0.059509 | -122.0078 | 0.11902 | 0.086976 | 0.14648 | -122.1313 | 0.032044 | -0.01831 | -122.0444 | 0.12817 | 0.009156 | 0.027466 | -122.0673 | 0.21973 | 0.096131 | 0.068665 | -122.287 | 0.18311 | 0.16022 | 0.14191 | -122.2458
5056.3125 | 122.3007 | -0.054932 | 122.0581 | -0.0048827 | 0.043991 | 0.061182 | 0.00019645 | 0.027406 | -0.0079446 | 0.02851 | 0.044556 | 0.011457 | 0.034105 | 0.056505 | -0.0013181 | 0.034622 | -0.004578 | 0.041199 | 0.036621 | 0.018311 | 0.059509 | 0.013733 | -0.14191 | 0.064087 | 0.07782 | -0.022888 | 0.013733 | -0.004578 | -0.064087 | -0.10986 | 0.068665 | -0.086975 | -121.9986 | 0.096131 | 0.073243 | 0.16022 | -122.0627 | -0.009155 | -0.054931 | -122.0444 | 0.11902 | 0.032044 | 0.086975 | -122.0627 | 0.11444 | 0.050354 | 0.091553 | -122.2 | 0.068665 | 0.050354 | 0.13275 | -122.168
5058.0781 | 122.2824 | -0.068665 | 122.0627 | 0.079041 | 0.043778 | 0.058832 | -0.0017261 | 0.02591 | -0.0036722 | 0.028297 | 0.12085 | 0.014447 | 0.031969 | 0.055865 | 0.0012455 | 0.036972 | 0.07782 | 0.10529 | 0.082397 | 0.045776 | 0.054932 | 0.022888 | -0.1236 | 0.11444 | 0.10986 | 0.018311 | 0.018311 | 0.004578 | -0.054932 | -0.091553 | 0.091553 | -0.054931 | -122.0078 | 0.17395 | 0.11444 | 0.16937 | -121.9849 | 0.013733 | -0.022888 | -122.0444 | 0.18311 | 0.086976 | 0.10986 | -122.0581 | 0.1236 | 0.14649 | 0.15106 | -122.1863 | 0.086976 | 0.073243 | 0.17853 | -122.1542
5059.8438 | 122.1863 | -0.1236 | 122.0947 | -0.26428 | 0.048905 | 0.060968 | 0.0066053 | 0.029328 | -0.0045266 | 0.028937 | -0.2301 | 0.013379 | 0.035173 | 0.05501 | 0.00081811 | 0.035476 | 0.022888 | 0.068665 | 0.041199 | 0.027466 | 0.045776 | -0.004578 | -0.15564 | 0.041199 | 0.059509 | -0.068665 | 0.036621 | 0.032043 | -0.041199 | -0.1236 | 0.11902 | -0.032044 | -122.049 | 0.19226 | 0.15106 | 0.18311 | -122.0718 | 0.082397 | 0 | -122.0581 | 0.16479 | 0.054931 | 0.054931 | -122.0627 | 0.16937 | 0.14648 | 0.16479 | -122.2504 | 0.16022 | 0.15564 | 0.1831 | -122.2183
5061.6094 | 122.3053 | -0.073242 | 122.0856 | 0.063782 | 0.04805 | 0.061182 | -0.0010851 | 0.028047 | 0.00038662 | 0.029792 | 0.067444 | 0.014447 | 0.031114 | 0.057146 | 0.0042361 | 0.035263 | 0.009155 | -0.013733 | -0.045776 | -0.032043 | 0.086975 | -0.018311 | -0.15106 | 0.050354 | 0.009155 | -0.082397 | 0.032043 | 0.027466 | -0.064087 | -0.12817 | 0.054931 | -0.07782 | -121.9986 | 0.059509 | 0.041199 | 0.11902 | -122.0764 | 0.009155 | -0.054932 | -122.0535 | 0.1236 | -0.009155 | 0.045777 | -122.0581 | 0.16022 | 0.082397 | 0.027466 | -122.2366 | 0.10529 | 0.10071 | 0.082397 | -122.2137
5063.375 | 122.3328 | -0.073242 | 122.0856 | 0.11719 | 0.046128 | 0.060754 | 0.00062385 | 0.026979 | -0.001536 | 0.03086 | 0.0064086 | 0.016797 | 0.031969 | 0.056078 | 0.0038089 | 0.03804 | 0.064087 | 0.07782 | 0.054932 | 0.036621 | 0.050354 | 0.018311 | -0.13275 | 0.12817 | 0.10071 | -0.004578 | 0.027466 | 0.004578 | -0.036621 | -0.091553 | 0.091553 | -0.059509 | -122.0352 | 0.15106 | 0.10986 | 0.16937 | -122.0215 | 0.036621 | -0.018311 | -122.0581 | 0.20142 | 0.068664 | 0.086975 | -122.081 | 0.1236 | 0.13733 | 0.12817 | -122.2183 | 0.10071 | 0.07782 | 0.17395 | -122.1771
5065.0781 | 122.2229 | -0.1236 | 122.0947 | -0.0048827 | 0.049118 | 0.0599 | -0.00023075 | 0.028901 | -0.00068138 | 0.030219 | 0.036926 | 0.017865 | 0.034318 | 0.055437 | 0.0042361 | 0.033767 | -0.018311 | -0.068665 | -0.073242 | -0.045776 | 0.07782 | -0.013733 | -0.16479 | 0.009155 | -0.036621 | -0.12817 | 0.050354 | 0.054932 | -0.07782 | -0.13275 | 0.10986 | -0.041199 | -122.0169 | 0.054931 | 0.07782 | 0.11902 | -122.113 | 0.045776 | -0.009155 | -122.0444 | 0.13275 | -0.004578 | 0.004577 | -122.0398 | 0.20142 | 0.10528 | 0.050354 | -122.2595 | 0.17395 | 0.17853 | 0.086975 | -122.2275
5066.8281 | 122.3099 | -0.054932 | 122.081 | -0.11932 | 0.045487 | 0.061609 | 0.0055371 | 0.025697 | -0.010081 | 0.030006 | -0.054626 | 0.013379 | 0.033678 | 0.056078 | -0.0034543 | 0.037185 | 0.059509 | 0.11444 | 0.10529 | 0.064087 | 0.054932 | 0.022888 | -0.11902 | 0.13733 | 0.16022 | 0.054932 | 0.009155 | -0.018311 | -0.045776 | -0.11444 | 0.07782 | -0.064087 | -122.0261 | 0.16937 | 0.11902 | 0.18311 | -122.0215 | 0.009156 | -0.059509 | -122.0718 | 0.19226 | 0.10986 | 0.16937 | -122.0993 | 0.10986 | 0.11444 | 0.16022 | -122.2 | 0.064087 | 0.036621 | 0.21515 | -122.1954
5068.6094 | 122.3145 | -0.068665 | 122.0993 | -0.14221 | 0.048905 | 0.059473 | 0.0048963 | 0.029756 | -0.0064492 | 0.024238 | -0.077515 | 0.013593 | 0.032823 | 0.054156 | -0.0043087 | 0.035263 | 0.07782 | 0.1236 | 0.10071 | 0.068665 | 0.041199 | 0.009155 | -0.10986 | 0.14191 | 0.16937 | 0.054932 | 0.004578 | -0.004578 | -0.032043 | -0.082397 | 0.07782 | -0.041198 | -122.0581 | 0.19226 | 0.13733 | 0.17853 | -122.0215 | 0.036622 | -0.013732 | -122.0947 | 0.21057 | 0.1236 | 0.13733 | -122.1039 | 0.10986 | 0.14649 | 0.16937 | -122.2092 | 0.073243 | 0.064087 | 0.23804 | -122.1817
5070.3125 | 122.3007 | -0.068665 | 122.081 | 0.094299 | 0.048691 | 0.060968 | 0.0021191 | 0.029115 | -0.00089518 | 0.028937 | 0.11322 | 0.015729 | 0.035387 | 0.056933 | 0.0044497 | 0.033767 | 0.018311 | -0.027466 | -0.036621 | -0.018311 | 0.091553 | -0.013733 | -0.16022 | 0.054932 | 0.027466 | -0.073242 | 0.027466 | 0.009155 | -0.059509 | -0.11444 | 0.054932 | -0.091552 | -121.9894 | 0.041199 | 0.050354 | 0.14191 | -122.0627 | 0.009156 | -0.045776 | -122.0535 | 0.1236 | -0.004577 | 0.041199 | -122.0718 | 0.16022 | 0.086976 | 0.032044 | -122.2412 | 0.096131 | 0.07782 | 0.096131 | -122.1954
5072.0938 | 122.2641 | -0.086975 | 122.113 | 0.11719 | 0.048264 | 0.0599 | 0.00041005 | 0.031892 | -0.0011088 | 0.031928 | 0.036926 | 0.016584 | 0.034318 | 0.056719 | 0.0025271 | 0.036972 | 0.004578 | -0.045776 | -0.068665 | -0.022888 | 0.086975 | -0.032043 | -0.13275 | 0.018311 | -0.022888 | -0.10529 | 0.064087 | 0.036621 | -0.082397 | -0.13275 | 0.054932 | -0.045776 | -122.0261 | 0.041199 | 0.064087 | 0.10986 | -122.1085 | 0.004578 | -0.045776 | -122.049 | 0.10529 | -0.018311 | 0.027465 | -122.0764 | 0.17395 | 0.091553 | 0.01831 | -122.2458 | 0.15106 | 0.1236 | 0.064087 | -122.2458
5073.7969 | 122.2778 | -0.086975 | 122.0901 | 0.063782 | 0.044632 | 0.060114 | -0.0015125 | 0.025483 | -0.0092264 | 0.027228 | 0.15137 | 0.013379 | 0.031328 | 0.055651 | -0.00024989 | 0.037826 | 0.07782 | 0.082397 | 0.07782 | 0.045776 | 0.050354 | 0.045776 | -0.11902 | 0.11444 | 0.091553 | 0.004578 | 0.027466 | 0.004578 | -0.054932 | -0.091553 | 0.13275 | -0.032044 | -122.0398 | 0.16937 | 0.13275 | 0.16479 | -122.0123 | 0.032043 | -0.004578 | -122.0627 | 0.20142 | 0.091553 | 0.096131 | -122.0856 | 0.13733 | 0.16479 | 0.16479 | -122.2092 | 0.11444 | 0.091553 | 0.17853 | -122.1817
5075.5469 | 122.3099 | -0.082397 | 122.0581 | 0.0027468 | 0.044419 | 0.062677 | 0.0046827 | 0.026124 | -0.0064492 | 0.027228 | 0.052185 | 0.012311 | 0.034959 | 0.054369 | 0.00060451 | 0.037613 | 0.013733 | 0.032043 | 0.036621 | 0.027466 | 0.050354 | 0.009155 | -0.1236 | 0.073242 | 0.059509 | -0.013733 | 0.022888 | 0.004578 | -0.050354 | -0.10071 | 0.091552 | -0.041199 | -122.0078 | 0.11444 | 0.10986 | 0.15106 | -122.0444 | 0.032043 | -0.018311 | -122.0352 | 0.15564 | 0.068664 | 0.086975 | -122.0535 | 0.13275 | 0.09613 | 0.11902 | -122.1817 | 0.10528 | 0.086975 | 0.14191 | -122.1588
5077.3125 | 122.2092 | -0.11902 | 122.1222 | -0.20325 | 0.047196 | 0.060327 | 0.0042555 | 0.029115 | -0.003245 | 0.029578 | -0.24536 | 0.014234 | 0.032823 | 0.056505 | -0.0015317 | 0.034835 | 0.004578 | -0.027466 | -0.045776 | -0.032043 | 0.086975 | -0.032043 | -0.1831 | 0 | 0.018311 | -0.11902 | 0.068665 | 0.045776 | -0.09613 | -0.12817 | 0.086976 | -0.064086 | -122.0352 | 0.091553 | 0.086976 | 0.15106 | -122.1176 | 0.022889 | -0.009155 | -122.0535 | 0.11902 | 0 | 0.009155 | -122.0764 | 0.20599 | 0.1236 | 0.073243 | -122.3053 | 0.18768 | 0.16479 | 0.13733 | -122.2504
5079.0312 | 122.2046 | -0.10986 | 122.1313 | -0.19562 | 0.049118 | 0.0599 | 0.0057507 | 0.029328 | -0.004313 | 0.028724 | -0.24536 | 0.013593 | 0.035173 | 0.056505 | -0.00024989 | 0.034408 | -0.004578 | -0.032043 | -0.027466 | -0.036621 | 0.086975 | -0.018311 | -0.17395 | 0.022888 | 0.013733 | -0.10986 | 0.064087 | 0.045776 | -0.10071 | -0.13733 | 0.091552 | -0.064087 | -122.0444 | 0.07782 | 0.073242 | 0.13733 | -122.1359 | 0.009155 | -0.027466 | -122.0673 | 0.13275 | 0 | 0.027466 | -122.0856 | 0.19684 | 0.10529 | 0.082397 | -122.3053 | 0.17395 | 0.15564 | 0.1236 | -122.2687
5080.7969 | 122.3236 | -0.064087 | 122.0627 | 0.11719 | 0.049332 | 0.061182 | -0.00044435 | 0.028474 | -0.001536 | 0.029365 | 0.31921 | 0.014875 | 0.030046 | 0.055865 | 0.0048769 | 0.035476 | 0.054932 | 0.045776 | 0.032043 | 0.018311 | 0.064087 | 0.018311 | -0.12817 | 0.14191 | 0.10071 | -0.013733 | 0.022888 | -0.009155 | -0.036621 | -0.11444 | 0.082398 | -0.064087 | -121.9986 | 0.10986 | 0.082398 | 0.14649 | -122.0078 | 0.027466 | -0.050354 | -122.0398 | 0.20599 | 0.050354 | 0.10071 | -122.0718 | 0.12817 | 0.11902 | 0.09613 | -122.1909 | 0.086975 | 0.054932 | 0.1648 | -122.1771
5082.5625 | 122.2137 | -0.10986 | 122.0901 | 0.048523 | 0.0504 | 0.060968 | -1.7146e-05 | 0.027619 | 0.00060022 | 0.031287 | 0.052185 | 0.017224 | 0.03325 | 0.058642 | 0.0042361 | 0.036331 | 0 | -0.064087 | -0.068665 | -0.022888 | 0.086975 | -0.013733 | -0.15106 | 0.013733 | -0.027466 | -0.11902 | 0.064087 | 0.041199 | -0.07782 | -0.12817 | 0.09613 | -0.041199 | -122.0032 | 0.045776 | 0.086975 | 0.12817 | -122.0901 | 0.032043 | -0.018311 | -122.0261 | 0.1236 | -0.009156 | 0.009155 | -122.0489 | 0.19684 | 0.10986 | 0.041198 | -122.2412 | 0.17395 | 0.15106 | 0.082397 | -122.2183
5084.3281 | 122.3328 | -0.082397 | 122.0581 | -0.0048827 | 0.043778 | 0.060754 | 0.0010511 | 0.02591 | -0.0079446 | 0.028083 | 0.052185 | 0.012952 | 0.030901 | 0.05501 | 0.00039091 | 0.038467 | 0 | 0.036621 | 0.036621 | 0.022888 | 0.068665 | 0.004578 | -0.14191 | 0.064087 | 0.064087 | 0.013733 | 0.022888 | 0.013733 | -0.045776 | -0.10986 | 0.086975 | -0.05951 | -121.9894 | 0.11902 | 0.10528 | 0.16479 | -122.0581 | 0.036621 | -0.027466 | -122.0352 | 0.14648 | 0.09613 | 0.1236 | -122.0444 | 0.15106 | 0.082397 | 0.11902 | -122.2 | 0.10528 | 0.09613 | 0.14648 | -122.168
5086.0312 | 122.1954 | -0.1236 | 122.0764 | 0.010376 | 0.050186 | 0.063318 | 0.0012647 | 0.031037 | 0.0027364 | 0.030646 | -0.016479 | 0.01637 | 0.030687 | 0.056505 | 0.0038089 | 0.035049 | 0.018311 | -0.036621 | -0.054932 | -0.022888 | 0.07782 | -0.018311 | -0.14648 | 0 | -0.036621 | -0.1236 | 0.064087 | 0.041199 | -0.082397 | -0.14648 | 0.10528 | -0.022888 | -121.9986 | 0.086975 | 0.10071 | 0.1236 | -122.0581 | 0.041199 | -0.022888 | -122.0123 | 0.1236 | 0 | 0.022888 | -122.0352 | 0.20142 | 0.14191 | 0.068664 | -122.2229 | 0.18768 | 0.16479 | 0.086975 | -122.2229
5087.7969 | 122.3099 | -0.086975 | 122.0947 | 0.0027468 | 0.046555 | 0.060968 | 0.0021191 | 0.028474 | -0.0096536 | 0.028083 | 0.067444 | 0.015302 | 0.034746 | 0.055865 | -0.0021725 | 0.036972 | 0.018311 | 0.022888 | 0.036621 | 0.022888 | 0.045776 | 0.004578 | -0.13733 | 0.045776 | 0.064087 | 0 | 0.027466 | 0.004578 | -0.059509 | -0.10071 | 0.091553 | -0.050354 | -122.049 | 0.10986 | 0.10986 | 0.16022 | -122.0764 | 0.027466 | -0.013733 | -122.0673 | 0.13275 | 0.086975 | 0.10071 | -122.0901 | 0.13275 | 0.10529 | 0.1236 | -122.2321 | 0.11444 | 0.091553 | 0.15106 | -122.1954
5089.5781 | 122.3236 | -0.068665 | 122.0718 | -0.10406 | 0.046341 | 0.063318 | 0.0042555 | 0.028688 | -0.007731 | 0.02851 | -0.1004 | 0.010388 | 0.03325 | 0.055651 | -0.0023861 | 0.036544 | 0.068665 | 0.091553 | 0.086975 | 0.054932 | 0.032043 | 0.027466 | -0.13733 | 0.14191 | 0.14648 | 0.045776 | 0.018311 | -0.018311 | -0.045776 | -0.086975 | 0.096131 | -0.068664 | -122.0398 | 0.16022 | 0.1236 | 0.19226 | -122.0032 | 0.022889 | -0.01831 | -122.0535 | 0.21057 | 0.11444 | 0.13275 | -122.0901 | 0.10071 | 0.13733 | 0.15564 | -122.2092 | 0.086976 | 0.050354 | 0.21515 | -122.1588
5091.3438 | 122.2595 | -0.10071 | 122.1176 | 0.10956 | 0.048691 | 0.061395 | 0.0019055 | 0.029328 | 0.0012412 | 0.030433 | 0.059815 | 0.014875 | 0.033678 | 0.058001 | 0.0042361 | 0.034195 | 0.013733 | -0.059509 | -0.068665 | -0.018311 | 0.086975 | -0.009155 | -0.15106 | 0.027466 | -0.018311 | -0.11444 | 0.045776 | 0.022888 | -0.086975 | -0.11444 | 0.091553 | -0.050354 | -122.0306 | 0.041199 | 0.082397 | 0.13275 | -122.1039 | 0.013733 | -0.013733 | -122.0718 | 0.12817 | -0.013733 | 0 | -122.0947 | 0.18768 | 0.11444 | 0.032043 | -122.2687 | 0.14648 | 0.1236 | 0.082397 | -122.2321
5093.0469 | 122.2 | -0.10986 | 122.1268 | -0.088806 | 0.049118 | 0.058618 | -0.0015125 | 0.02826 | 0.00038662 | 0.029792 | -0.14618 | 0.015302 | 0.034105 | 0.060137 | 0.0040225 | 0.034408 | 0.068665 | 0.045776 | 0.004578 | 0.013733 | 0.082397 | 0.009155 | -0.13733 | 0.068665 | 0.059509 | -0.09613 | 0.045776 | 0.013733 | -0.064087 | -0.1236 | 0.11902 | -0.027466 | -122.0444 | 0.15564 | 0.1236 | 0.15106 | -122.0581 | 0.045776 | -0.013733 | -122.081 | 0.17853 | 0.013733 | 0.027466 | -122.113 | 0.19226 | 0.17853 | 0.11444 | -122.2641 | 0.15564 | 0.1236 | 0.16937 | -122.2504
5094.8281 | 122.2275 | -0.10529 | 122.113 | -0.23376 | 0.049546 | 0.061182 | 0.0061781 | 0.029969 | -0.0045266 | 0.028297 | -0.2301 | 0.015515 | 0.034105 | 0.059496 | -0.00024989 | 0.037613 | -0.004578 | -0.022888 | -0.045776 | -0.013733 | 0.091553 | -0.018311 | -0.15564 | 0.004578 | 0.018311 | -0.10529 | 0.054932 | 0.041199 | -0.073242 | -0.14191 | 0.086975 | -0.050354 | -122.0215 | 0.082398 | 0.091553 | 0.14191 | -122.1176 | 0.032044 | -0.036621 | -122.0581 | 0.10986 | 0 | 0.036621 | -122.0718 | 0.19684 | 0.10071 | 0.05951 | -122.2687 | 0.16022 | 0.14649 | 0.1236 | -122.2549
5096.6094 | 122.2092 | -0.13275 | 122.1085 | -0.18036 | 0.047196 | 0.059259 | 0.0057507 | 0.027833 | -0.006663 | 0.028937 | -0.13092 | 0.012952 | 0.0356 | 0.05736 | -0.0030271 | 0.035263 | 0.068665 | 0.10986 | 0.091553 | 0.059509 | 0.050354 | 0.004578 | -0.10529 | 0.10071 | 0.14191 | 0.009155 | 0.009155 | 0.009155 | -0.054932 | -0.10071 | 0.13733 | 0.027465 | -122.0581 | 0.24261 | 0.19226 | 0.16479 | -122.0398 | 0.077819 | 0.032043 | -122.0993 | 0.23346 | 0.14191 | 0.10986 | -122.0993 | 0.18311 | 0.20142 | 0.2243 | -122.2137 | 0.14191 | 0.14191 | 0.27466 | -122.2092
5098.375 | 122.3053 | -0.068665 | 122.0718 | 0.048523 | 0.049332 | 0.058618 | -0.0012987 | 0.027833 | -0.0038858 | 0.029151 | 0.12085 | 0.015088 | 0.030687 | 0.055865 | 0.0042361 | 0.037185 | 0.082397 | 0.07782 | 0.068665 | 0.059509 | 0.036621 | 0.018311 | -0.12817 | 0.13733 | 0.10529 | 0.004578 | 0 | -0.004578 | -0.041199 | -0.10071 | 0.086976 | -0.059509 | -122.0352 | 0.14649 | 0.12817 | 0.18768 | -121.9894 | 0.027466 | -0.032043 | -122.0718 | 0.20599 | 0.073243 | 0.10529 | -122.0764 | 0.10529 | 0.15106 | 0.13733 | -122.2 | 0.068665 | 0.064087 | 0.17395 | -122.1725
5100.0781 | 122.2778 | -0.091553 | 122.0856 | 0.063782 | 0.044419 | 0.059473 | 0.0023329 | 0.027406 | -0.0068766 | 0.028937 | 0.15137 | 0.014447 | 0.031969 | 0.058642 | -0.00046349 | 0.037399 | 0.068665 | 0.07782 | 0.07782 | 0.041199 | 0.041199 | 0.009155 | -0.1236 | 0.11444 | 0.082397 | 0 | 0.009155 | 0.004578 | -0.050354 | -0.09613 | 0.10071 | -0.032043 | -122.0444 | 0.16937 | 0.13275 | 0.16479 | -122.0169 | 0.041199 | -0.004577 | -122.0764 | 0.20599 | 0.091553 | 0.09613 | -122.081 | 0.13275 | 0.16022 | 0.16937 | -122.2092 | 0.10071 | 0.096131 | 0.17395 | -122.1817
5101.8438 | 122.2183 | -0.10529 | 122.1176 | -0.23376 | 0.049118 | 0.060541 | 0.0027601 | 0.031678 | -0.0023904 | 0.027228 | -0.24536 | 0.013379 | 0.036241 | 0.059496 | 0.0010317 | 0.035904 | -0.013733 | -0.018311 | -0.045776 | -0.032043 | 0.10071 | -0.022888 | -0.15106 | 0 | 0.022888 | -0.10529 | 0.068665 | 0.045776 | -0.10071 | -0.14191 | 0.082398 | -0.045776 | -122.0169 | 0.086975 | 0.073243 | 0.11902 | -122.1313 | 0.004578 | -0.036621 | -122.049 | 0.10529 | 0 | 0.036621 | -122.0718 | 0.20599 | 0.091553 | 0.05951 | -122.2687 | 0.17395 | 0.15106 | 0.12817 | -122.2595
5103.625 | 122.2733 | -0.09613 | 122.0627 | 0.071411 | 0.046341 | 0.059473 | 0.0014783 | 0.028047 | -0.0070902 | 0.02851 | 0.082703 | 0.013379 | 0.032396 | 0.056719 | 0.00017731 | 0.038253 | 0.050354 | 0.073242 | 0.064087 | 0.018311 | 0.041199 | 0.018311 | -0.11902 | 0.07782 | 0.082397 | -0.018311 | 0.004578 | -0.013733 | -0.054932 | -0.10071 | 0.11444 | -0.022889 | -122.0215 | 0.16937 | 0.11444 | 0.13733 | -122.0123 | 0.041198 | -0.004578 | -122.0581 | 0.17395 | 0.077819 | 0.082397 | -122.0764 | 0.13733 | 0.14648 | 0.16022 | -122.1817 | 0.10071 | 0.082397 | 0.17853 | -122.1634
5105.3281 | 122.2366 | -0.10071 | 122.0856 | 0.08667 | 0.04805 | 0.061609 | -0.00087155 | 0.025697 | 0.0010276 | 0.026374 | 0.044556 | 0.015515 | 0.030473 | 0.058001 | 0.0040225 | 0.036117 | 0.004578 | -0.054932 | -0.073242 | -0.027466 | 0.091553 | -0.013733 | -0.16937 | 0.027466 | -0.022888 | -0.11444 | 0.059509 | 0.045776 | -0.07782 | -0.11444 | 0.086975 | -0.068665 | -121.994 | 0.045776 | 0.073242 | 0.14191 | -122.081 | 0.022888 | -0.013733 | -122.0261 | 0.12817 | -0.013733 | 0 | -122.0398 | 0.19226 | 0.10529 | 0.027466 | -122.2549 | 0.16022 | 0.14648 | 0.07782 | -122.2
5107.0938 | 122.1634 | -0.1236 | 122.113 | -0.073547 | 0.050614 | 0.055841 | 0.0061781 | 0.02826 | 0.00081382 | 0.031501 | -0.085144 | 0.012738 | 0.036241 | 0.058001 | 0.0027407 | 0.035904 | 0.036621 | 0.009155 | 0 | 0.004578 | 0.086975 | 0.009155 | -0.14191 | 0.032043 | 0.018311 | -0.10529 | 0.036621 | 0.027466 | -0.082397 | -0.12817 | 0.13275 | -0.018311 | -122.0261 | 0.13275 | 0.12817 | 0.14649 | -122.0764 | 0.041199 | -0.004578 | -122.0764 | 0.15564 | 0.01831 | 0.022888 | -122.0856 | 0.21057 | 0.16022 | 0.1236 | -122.2549 | 0.16022 | 0.15106 | 0.14191 | -122.2412
5108.8594 | 122.2961 | -0.064087 | 122.0535 | -0.15747 | 0.046341 | 0.060968 | 0.0040417 | 0.027406 | -0.007731 | 0.029578 | -0.16144 | 0.011457 | 0.036668 | 0.055224 | -0.0045225 | 0.037613 | 0.059509 | 0.14191 | 0.10071 | 0.054932 | 0.050354 | 0.009155 | -0.1236 | 0.13733 | 0.16937 | 0.036621 | 0.027466 | 0.013733 | -0.041199 | -0.09613 | 0.073242 | -0.059509 | -122.0032 | 0.20599 | 0.11902 | 0.17853 | -121.994 | 0.022888 | -0.032043 | -122.0261 | 0.20142 | 0.10071 | 0.13275 | -122.0398 | 0.11444 | 0.1236 | 0.1648 | -122.1771 | 0.091553 | 0.07782 | 0.23346 | -122.1497
5110.6406 | 122.2687 | -0.086975 | 122.0581 | 0.048523 | 0.048905 | 0.058832 | 0.0044691 | 0.029328 | -0.0058084 | 0.029578 | 0.059815 | 0.012738 | 0.032823 | 0.055865 | -0.00046349 | 0.03804 | 0.027466 | 0.059509 | 0.054932 | 0.032043 | 0.054932 | 0.009155 | -0.12817 | 0.086975 | 0.073242 | -0.009155 | 0.013733 | 0 | -0.054932 | -0.10529 | 0.09613 | -0.041199 | -122.0032 | 0.14648 | 0.11902 | 0.16022 | -122.0306 | 0.032043 | -0.018311 | -122.0444 | 0.17395 | 0.07782 | 0.096131 | -122.0581 | 0.14191 | 0.11444 | 0.14191 | -122.1863 | 0.10071 | 0.086975 | 0.16022 | -122.1634
5112.4062 | 122.2412 | -0.10071 | 122.081 | -0.18036 | 0.0504 | 0.058618 | 0.0034009 | 0.029756 | -0.00025418 | 0.028937 | -0.24536 | 0.015302 | 0.034532 | 0.059496 | 0.0033817 | 0.034622 | 0.004578 | -0.009155 | -0.027466 | 0.004578 | 0.082397 | -0.022888 | -0.16479 | 0.032043 | 0.041199 | -0.086975 | 0.050354 | 0.032043 | -0.10071 | -0.13275 | 0.07782 | -0.064087 | -121.9986 | 0.091553 | 0.10529 | 0.16937 | -122.0764 | 0 | -0.032043 | -122.0306 | 0.13275 | 0.013733 | 0.045776 | -122.049 | 0.18311 | 0.10529 | 0.073242 | -122.2458 | 0.15106 | 0.13275 | 0.14191 | -122.2137
5114.1094 | 122.2687 | -0.086975 | 122.0673 | 0.13245 | 0.047409 | 0.056909 | 0.0023329 | 0.02826 | -0.004313 | 0.031287 | 0.11322 | 0.012952 | 0.033891 | 0.059069 | 0.00081811 | 0.03804 | 0.073242 | 0.11902 | 0.091553 | 0.059509 | 0.041199 | 0.032043 | -0.10529 | 0.13275 | 0.11444 | 0.009155 | -0.013733 | -0.018311 | -0.050354 | -0.086975 | 0.11902 | -0.018311 | -122.0261 | 0.20599 | 0.14648 | 0.16479 | -121.994 | 0.036621 | 0 | -122.081 | 0.21973 | 0.09613 | 0.09613 | -122.0856 | 0.12817 | 0.16022 | 0.17853 | -122.1725 | 0.073242 | 0.068664 | 0.20142 | -122.1542
5115.875 | 122.2046 | -0.11444 | 122.0947 | 0.033264 | 0.049546 | 0.059686 | 0.0023329 | 0.029328 | 0.00060022 | 0.030006 | 0.029297 | 0.015515 | 0.034532 | 0.061632 | 0.0053043 | 0.036972 | -0.041199 | -0.073242 | -0.082397 | -0.045776 | 0.10529 | -0.018311 | -0.14648 | 0.009155 | -0.027466 | -0.13275 | 0.054932 | 0.045776 | -0.068665 | -0.1236 | 0.09613 | -0.032043 | -121.9894 | 0.041199 | 0.068665 | 0.10071 | -122.1359 | 0.045776 | -0.009155 | -122.0398 | 0.1236 | -0.01831 | -0.009155 | -122.049 | 0.21973 | 0.073242 | 0.032044 | -122.2412 | 0.16937 | 0.16022 | 0.086975 | -122.2183
5117.6406 | 122.2046 | -0.11902 | 122.1039 | 0.025635 | 0.050186 | 0.060541 | 0.0019055 | 0.029542 | -0.001536 | 0.03086 | 0.044556 | 0.016156 | 0.030901 | 0.055651 | 0.0040225 | 0.038681 | -0.045776 | -0.068665 | -0.086975 | -0.032043 | 0.086975 | -0.018311 | -0.15106 | 0.004578 | -0.032043 | -0.1236 | 0.050354 | 0.054932 | -0.059509 | -0.1236 | 0.10071 | -0.032043 | -122.0169 | 0.050354 | 0.086976 | 0.11902 | -122.1497 | 0.05951 | -0.004577 | -122.0535 | 0.1236 | -0.004577 | 0 | -122.049 | 0.20599 | 0.073243 | 0.032044 | -122.2549 | 0.16937 | 0.17395 | 0.086976 | -122.2275
5119.3594 | 122.3053 | -0.073242 | 122.0627 | -0.0048827 | 0.046768 | 0.059686 | 0.0025465 | 0.026124 | -0.006663 | 0.028083 | 0.059815 | 0.014234 | 0.0356 | 0.056505 | -0.0013181 | 0.039962 | 0.004578 | 0.054932 | 0.045776 | 0.022888 | 0.050354 | 0.027466 | -0.13733 | 0.059509 | 0.07782 | -0.009155 | 0.018311 | 0 | -0.045776 | -0.082397 | 0.10071 | -0.064087 | -122.0123 | 0.12817 | 0.09613 | 0.16022 | -122.0581 | 0.027466 | -0.009155 | -122.0444 | 0.13275 | 0.064087 | 0.073242 | -122.0627 | 0.1236 | 0.07782 | 0.11902 | -122.2 | 0.091553 | 0.073242 | 0.15106 | -122.1451
5121.125 | 122.2733 | -0.091553 | 122.0581 | 0.13245 | 0.047196 | 0.060968 | -0.00065795 | 0.028047 | -0.0053812 | 0.030646 | 0.17426 | 0.01637 | 0.032823 | 0.055224 | 0.00081811 | 0.038467 | 0.082397 | 0.09613 | 0.082397 | 0.059509 | 0.041199 | 0.050354 | -0.10986 | 0.13275 | 0.11902 | 0.018311 | 0.009155 | -0.004578 | -0.036621 | -0.07782 | 0.14191 | -0.01831 | -122.0169 | 0.18768 | 0.15106 | 0.16937 | -121.9757 | 0.054932 | 0.013733 | -122.0489 | 0.2243 | 0.10986 | 0.096131 | -122.0627 | 0.13275 | 0.17395 | 0.17395 | -122.168 | 0.10071 | 0.086975 | 0.21057 | -122.1359
5122.8281 | 122.3145 | -0.082397 | 122.0444 | 0.17059 | 0.0504 | 0.058832 | 0.0014783 | 0.029969 | -0.0019632 | 0.031714 | 0.12848 | 0.01402 | 0.032823 | 0.057574 | 0.0042361 | 0.036758 | 0.036621 | 0.009155 | 0.013733 | 0.009155 | 0.073242 | 0.022888 | -0.13275 | 0.10071 | 0.073242 | -0.022888 | 0.009155 | 0.009155 | -0.036621 | -0.082397 | 0.10528 | -0.050354 | -121.9711 | 0.091552 | 0.091552 | 0.14191 | -122.0078 | 0.045776 | 0 | -122.0352 | 0.18311 | 0.059509 | 0.059509 | -122.0352 | 0.15564 | 0.11902 | 0.09613 | -122.1771 | 0.091552 | 0.091552 | 0.15564 | -122.1268
5124.5938 | 122.2092 | -0.11902 | 122.0856 | 0.048523 | 0.051255 | 0.057336 | 0.0021191 | 0.026338 | 0.00060022 | 0.031287 | 0.082703 | 0.016797 | 0.034318 | 0.058855 | 0.0033817 | 0.037185 | -0.018311 | -0.07782 | -0.073242 | -0.032043 | 0.10529 | 0.009155 | -0.15106 | 0.032043 | -0.041199 | -0.1236 | 0.050354 | 0.045776 | -0.064087 | -0.13733 | 0.12817 | -0.032043 | -121.9803 | 0.041199 | 0.086976 | 0.11902 | -122.1039 | 0.054932 | -0.01831 | -122.0352 | 0.15106 | -0.004577 | 0.013733 | -122.0398 | 0.22431 | 0.10071 | 0.045777 | -122.2366 | 0.16937 | 0.16479 | 0.07782 | -122.2229
5126.3594 | 122.1725 | -0.12817 | 122.1176 | -0.21851 | 0.046768 | 0.062036 | 0.0059643 | 0.028901 | -0.0068766 | 0.029365 | -0.22247 | 0.013806 | 0.033678 | 0.05501 | 0.00039091 | 0.038894 | 0.045776 | 0.073242 | 0.050354 | 0.041199 | 0.073242 | 0 | -0.14191 | 0.032043 | 0.073242 | -0.054932 | 0.036621 | 0.022888 | -0.086975 | -0.12817 | 0.12817 | -0.013733 | -122.0444 | 0.20142 | 0.16937 | 0.18311 | -122.0718 | 0.041199 | 0 | -122.081 | 0.16022 | 0.073242 | 0.073242 | -122.0947 | 0.20142 | 0.17395 | 0.17853 | -122.2595 | 0.1648 | 0.15106 | 0.20142 | -122.2458
5128.0625 | 122.2916 | -0.068665 | 122.0673 | -0.0048827 | 0.043351 | 0.060968 | 0.0027601 | 0.028474 | -0.0087992 | 0.028724 | 0.067444 | 0.012097 | 0.032182 | 0.057146 | -0.00089089 | 0.039535 | 0.004578 | 0.032043 | 0.027466 | 0.027466 | 0.068665 | 0.018311 | -0.11444 | 0.041199 | 0.054932 | -0.018311 | 0.013733 | -0.004578 | -0.036621 | -0.11902 | 0.086976 | -0.045776 | -121.9986 | 0.10071 | 0.096131 | 0.14191 | -122.0627 | 0.032044 | -0.050354 | -122.0535 | 0.10986 | 0.050354 | 0.10071 | -122.0718 | 0.13733 | 0.073243 | 0.096131 | -122.1817 | 0.082398 | 0.064087 | 0.1236 | -122.1863
5129.7812 | 122.168 | -0.11444 | 122.0856 | 0.010376 | 0.049546 | 0.057764 | 0.0012647 | 0.028688 | -0.0011088 | 0.031501 | -0.024109 | 0.012952 | 0.034746 | 0.058855 | 0.0053043 | 0.036972 | 0.009155 | -0.050354 | -0.041199 | -0.027466 | 0.091553 | 0 | -0.15564 | -0.004578 | -0.041199 | -0.15106 | 0.064087 | 0.036621 | -0.068665 | -0.13733 | 0.11444 | -0.041199 | -121.994 | 0.064087 | 0.086975 | 0.12817 | -122.0764 | 0.045776 | -0.022888 | -122.0215 | 0.10986 | -0.036621 | -0.013733 | -122.049 | 0.20599 | 0.1236 | 0.073242 | -122.2412 | 0.17853 | 0.15106 | 0.073242 | -122.2229
5131.5469 | 122.1817 | -0.10986 | 122.0901 | 0.071411 | 0.051041 | 0.058191 | 0.00062385 | 0.027619 | 0.0012412 | 0.029578 | -0.0012209 | 0.014875 | 0.033678 | 0.058001 | 0.0040225 | 0.037826 | 0.004578 | -0.059509 | -0.054932 | -0.027466 | 0.09613 | -0.018311 | -0.16937 | -0.013733 | -0.032043 | -0.14648 | 0.068665 | 0.022888 | -0.068665 | -0.12817 | 0.091552 | -0.05951 | -121.994 | 0.050354 | 0.082397 | 0.14191 | -122.0856 | 0.041198 | -0.018311 | -122.0215 | 0.09613 | -0.036621 | -0.01831 | -122.0673 | 0.20599 | 0.11444 | 0.054931 | -122.2595 | 0.17853 | 0.13275 | 0.07782 | -122.2183
5133.3281 | 122.1863 | -0.1236 | 122.113 | -0.28717 | 0.049546 | 0.059473 | 0.0074597 | 0.030824 | -0.0064492 | 0.030433 | -0.16144 | 0.010388 | 0.034746 | 0.060137 | -0.0028135 | 0.040176 | -0.022888 | 0.032043 | -0.004578 | 0.004578 | 0.082397 | -0.009155 | -0.15106 | 0.027466 | 0.032043 | -0.07782 | 0.050354 | 0.027466 | -0.07782 | -0.13733 | 0.11444 | -0.027466 | -122.0306 | 0.15564 | 0.12817 | 0.15564 | -122.1359 | 0.045776 | -0.013733 | -122.0627 | 0.15106 | 0.045776 | 0.059509 | -122.0856 | 0.20599 | 0.10071 | 0.11902 | -122.2641 | 0.17395 | 0.15106 | 0.15564 | -122.2504
5135.1094 | 122.3053 | -0.082397 | 122.081 | -0.12695 | 0.045273 | 0.060327 | 0.0085279 | 0.02826 | -0.0096536 | 0.029365 | -0.092773 | 0.012311 | 0.034318 | 0.057574 | -0.0051633 | 0.036972 | 0.086975 | 0.13275 | 0.10986 | 0.073242 | 0.041199 | 0.018311 | -0.12817 | 0.12817 | 0.15106 | 0.036621 | 0.018311 | -0.009155 | -0.041199 | -0.10529 | 0.10071 | -0.045777 | -122.0398 | 0.21515 | 0.15564 | 0.20142 | -121.994 | 0.041198 | -0.022889 | -122.0627 | 0.21057 | 0.11902 | 0.14191 | -122.0901 | 0.1236 | 0.16937 | 0.19226 | -122.2092 | 0.10071 | 0.073242 | 0.23346 | -122.1863
5136.8281 | 122.287 | -0.064087 | 122.0627 | -0.14984 | 0.046128 | 0.060754 | 0.0040417 | 0.026124 | -0.00944 | 0.026801 | -0.12329 | 0.011243 | 0.03325 | 0.058642 | -0.0021725 | 0.037826 | 0.07782 | 0.14648 | 0.10986 | 0.064087 | 0.059509 | 0.027466 | -0.10986 | 0.13733 | 0.15564 | 0.032043 | 0.027466 | -0.004578 | -0.041199 | -0.082397 | 0.091553 | -0.045776 | -122.0032 | 0.21057 | 0.12817 | 0.17395 | -121.9849 | 0.022888 | -0.01831 | -122.0352 | 0.20142 | 0.09613 | 0.11444 | -122.0673 | 0.1236 | 0.14191 | 0.17395 | -122.1725 | 0.091553 | 0.059509 | 0.21973 | -122.1451
5138.5938 | 122.3007 | -0.050354 | 122.0627 | 0.056152 | 0.047837 | 0.058405 | -0.00044435 | 0.030183 | 0.00017302 | 0.030006 | 0.090332 | 0.017652 | 0.033891 | 0.057574 | 0.0053043 | 0.037826 | 0.004578 | -0.022888 | -0.032043 | -0.009155 | 0.09613 | -0.004578 | -0.15106 | 0.054932 | 0.009155 | -0.082397 | 0.027466 | 0.027466 | -0.073242 | -0.11444 | 0.045776 | -0.10071 | -121.9666 | 0.027466 | 0.041199 | 0.14191 | -122.0581 | -0.022888 | -0.064087 | -122.0352 | 0.10529 | -0.032043 | 0.032044 | -122.0352 | 0.14648 | 0.054932 | 0.018311 | -122.2137 | 0.07782 | 0.07782 | 0.059509 | -122.1771
5140.3594 | 122.2824 | -0.086975 | 122.0581 | -0.0048827 | 0.045273 | 0.060114 | 0.0034009 | 0.027192 | -0.0070902 | 0.027869 | 0.059815 | 0.012525 | 0.031969 | 0.058642 | -0.00024989 | 0.039108 | 0.013733 | 0.041199 | 0.045776 | 0.027466 | 0.073242 | 0.027466 | -0.13733 | 0.073242 | 0.064087 | -0.018311 | 0.045776 | 0.004578 | -0.050354 | -0.10986 | 0.11444 | -0.050354 | -121.9849 | 0.12817 | 0.11444 | 0.16479 | -122.0444 | 0.036621 | -0.022888 | -122.0123 | 0.16022 | 0.068664 | 0.091552 | -122.0535 | 0.16022 | 0.10071 | 0.13275 | -122.1954 | 0.13275 | 0.091553 | 0.15106 | -122.168
5142.0625 | 122.2824 | -0.073242 | 122.0673 | -0.14984 | 0.047196 | 0.059259 | 0.0036145 | 0.029756 | -0.0058084 | 0.027656 | -0.15381 | 0.013379 | 0.031755 | 0.057574 | 0.00017731 | 0.038467 | 0.086975 | 0.1236 | 0.10071 | 0.045776 | 0.059509 | 0.022888 | -0.11902 | 0.13275 | 0.16022 | 0.045776 | 0.004578 | 0 | -0.018311 | -0.082397 | 0.09613 | -0.045777 | -122.0078 | 0.19684 | 0.11902 | 0.16479 | -121.9803 | 0.054931 | -0.009155 | -122.0627 | 0.20599 | 0.11902 | 0.12817 | -122.0673 | 0.13275 | 0.16022 | 0.17395 | -122.1863 | 0.07782 | 0.073242 | 0.23346 | -122.1497
5143.8281 | 122.168 | -0.11444 | 122.1039 | -0.088806 | 0.051682 | 0.060754 | 0.00041005 | 0.026979 | 0.0042318 | 0.029792 | -0.14618 | 0.014234 | 0.033891 | 0.059923 | 0.0046633 | 0.036758 | 0.07782 | 0.041199 | 0 | 0.018311 | 0.10529 | -0.004578 | -0.15106 | 0.068665 | 0.054932 | -0.086975 | 0.041199 | 0.032043 | -0.064087 | -0.13275 | 0.10986 | -0.036621 | -121.9986 | 0.15564 | 0.13275 | 0.16937 | -122.0261 | 0.050354 | -0.01831 | -122.0627 | 0.18311 | 0.027466 | 0.045776 | -122.0718 | 0.21973 | 0.19226 | 0.11444 | -122.2549 | 0.15564 | 0.14648 | 0.16937 | -122.2366
5145.6094 | 122.2092 | -0.12817 | 122.1268 | -0.20325 | 0.048905 | 0.061395 | 0.0081007 | 0.028901 | -0.0034586 | 0.029792 | -0.25299 | 0.015515 | 0.034959 | 0.061846 | -0.0011045 | 0.036758 | -0.022888 | -0.004578 | -0.045776 | -0.022888 | 0.10071 | -0.018311 | -0.16022 | 0.004578 | 0.013733 | -0.10071 | 0.059509 | 0.045776 | -0.07782 | -0.12817 | 0.10986 | -0.032043 | -122.0261 | 0.1236 | 0.10529 | 0.13733 | -122.1497 | 0.050354 | 0 | -122.0673 | 0.13275 | 0.027466 | 0.027466 | -122.081 | 0.22888 | 0.10529 | 0.082398 | -122.287 | 0.18768 | 0.17395 | 0.14191 | -122.2549
5147.3281 | 122.2733 | -0.091553 | 122.0718 | -0.1651 | 0.046982 | 0.061182 | 0.0063917 | 0.029542 | -0.0062356 | 0.029151 | -0.1767 | 0.015943 | 0.034105 | 0.058214 | -0.0013181 | 0.038467 | 0.064087 | 0.13733 | 0.09613 | 0.050354 | 0.045776 | 0.022888 | -0.10986 | 0.1236 | 0.16937 | 0.036621 | 0.013733 | 0 | -0.064087 | -0.09613 | 0.11444 | -0.01831 | -122.0261 | 0.22888 | 0.14191 | 0.16022 | -122.0078 | 0.027466 | -0.004577 | -122.0581 | 0.21515 | 0.12817 | 0.13275 | -122.0718 | 0.13733 | 0.15564 | 0.18768 | -122.1817 | 0.10529 | 0.091553 | 0.26093 | -122.168
5149.0938 | 122.2458 | -0.082397 | 122.0764 | 0.10193 | 0.04271 | 0.060327 | -0.00044435 | 0.026338 | -0.0055948 | 0.027442 | 0.082703 | 0.013806 | 0.031969 | 0.060992 | -0.0011045 | 0.040176 | 0.045776 | 0.091553 | 0.041199 | 0.022888 | 0.054932 | 0.036621 | -0.13275 | 0.09613 | 0.07782 | -0.009155 | 0 | -0.009155 | -0.036621 | -0.091553 | 0.11902 | -0.050354 | -122.0215 | 0.17395 | 0.10528 | 0.15564 | -122.0306 | 0.045776 | -0.009156 | -122.0764 | 0.17853 | 0.073242 | 0.082398 | -122.0856 | 0.13733 | 0.12817 | 0.1236 | -122.2092 | 0.082397 | 0.073242 | 0.16022 | -122.168
5150.8594 | 122.2183 | -0.10529 | 122.1039 | -0.21851 | 0.047623 | 0.061395 | 0.0042555 | 0.028688 | -0.002604 | 0.029151 | -0.23773 | 0.01637 | 0.031969 | 0.059283 | 0.0020999 | 0.03804 | -0.009155 | -0.032043 | -0.050354 | -0.018311 | 0.10986 | -0.018311 | -0.16022 | 0.022888 | 0.027466 | -0.10986 | 0.050354 | 0.041199 | -0.082397 | -0.13733 | 0.086975 | -0.054931 | -121.994 | 0.073243 | 0.086975 | 0.14191 | -122.113 | 0.022889 | -0.032043 | -122.0535 | 0.12817 | -0.004577 | 0.027466 | -122.0627 | 0.21515 | 0.096131 | 0.054932 | -122.2641 | 0.15564 | 0.14649 | 0.13275 | -122.2412
5152.6406 | 122.2504 | -0.086975 | 122.0627 | 0.10193 | 0.044419 | 0.060754 | 0.00019645 | 0.027619 | -0.0070902 | 0.029578 | 0.097962 | 0.014447 | 0.03325 | 0.058855 | 0.00017731 | 0.038894 | 0.054932 | 0.10071 | 0.064087 | 0.018311 | 0.036621 | 0.022888 | -0.1236 | 0.091553 | 0.086975 | -0.009155 | 0.013733 | -0.009155 | -0.054932 | -0.086975 | 0.10986 | -0.036621 | -122.0261 | 0.18768 | 0.10529 | 0.14191 | -122.0078 | 0.032043 | 0 | -122.049 | 0.17853 | 0.07782 | 0.07782 | -122.0718 | 0.1236 | 0.14191 | 0.15106 | -122.1863 | 0.10071 | 0.07782 | 0.17395 | -122.1497
5154.4219 | 122.3053 | -0.07782 | 122.0581 | -0.081177 | 0.047196 | 0.060541 | 0.0040417 | 0.028688 | -0.0073038 | 0.027228 | -0.092773 | 0.013166 | 0.032823 | 0.05971 | -0.0021725 | 0.03804 | 0.054932 | 0.10529 | 0.073242 | 0.045776 | 0.059509 | 0.027466 | -0.11444 | 0.12817 | 0.15564 | 0.041199 | 0.022888 | 0.013733 | -0.032043 | -0.091553 | 0.10529 | -0.036621 | -121.9986 | 0.18311 | 0.1236 | 0.16022 | -122.0032 | 0.045777 | -0.013733 | -122.0352 | 0.20599 | 0.11902 | 0.13275 | -122.0444 | 0.13733 | 0.13275 | 0.15106 | -122.1725 | 0.10071 | 0.091553 | 0.23346 | -122.1497
5156.125 | 122.2641 | -0.073242 | 122.0673 | 0.033264 | 0.044846 | 0.060754 | 0.0012647 | 0.026124 | -0.004313 | 0.027656 | 0.036926 | 0.013379 | 0.031755 | 0.057787 | 0.00060451 | 0.038467 | 0.050354 | 0.041199 | 0.050354 | 0.022888 | 0.059509 | 0.032043 | -0.12817 | 0.082397 | 0.064087 | -0.018311 | 0.027466 | 0.018311 | -0.050354 | -0.086975 | 0.10529 | -0.054932 | -122.0078 | 0.11444 | 0.09613 | 0.15106 | -122.0169 | 0.022888 | -0.013733 | -122.0398 | 0.15564 | 0.054931 | 0.068664 | -122.049 | 0.13275 | 0.1236 | 0.1236 | -122.1954 | 0.10071 | 0.091553 | 0.13733 | -122.1542
5157.8906 | 122.1588 | -0.12817 | 122.1085 | -0.073547 | 0.049546 | 0.059045 | 0.0025465 | 0.026338 | 0.0027364 | 0.029365 | -0.11566 | 0.016797 | 0.033891 | 0.059069 | 0.0038089 | 0.035904 | 0.064087 | 0.022888 | -0.013733 | 0.004578 | 0.082397 | 0.004578 | -0.15106 | 0.054932 | 0.013733 | -0.11444 | 0.045776 | 0.036621 | -0.059509 | -0.11444 | 0.13275 | -0.022888 | -122.0261 | 0.15106 | 0.13275 | 0.15564 | -122.0444 | 0.068665 | 0.013733 | -122.0627 | 0.18311 | 0.013733 | 0 | -122.0718 | 0.21057 | 0.19226 | 0.11444 | -122.2595 | 0.17395 | 0.1648 | 0.14191 | -122.2229
5159.6562 | 122.2824 | -0.064087 | 122.0398 | 0.11719 | 0.043351 | 0.059259 | -0.0021533 | 0.029756 | -0.0030314 | 0.03086 | 0.11322 | 0.014234 | 0.034959 | 0.060564 | 0.0018863 | 0.04103 | 0.07782 | 0.10071 | 0.082397 | 0.064087 | 0.059509 | 0.022888 | -0.1236 | 0.15564 | 0.11444 | 0.022888 | -0.004578 | 0.013733 | -0.032043 | -0.086975 | 0.086975 | -0.059509 | -121.9803 | 0.1648 | 0.12817 | 0.18768 | -121.962 | 0.032044 | -0.022888 | -122.0444 | 0.21973 | 0.086975 | 0.10986 | -122.0261 | 0.1236 | 0.14191 | 0.14648 | -122.1634 | 0.059509 | 0.07782 | 0.17853 | -122.1268
5161.4219 | 122.3053 | -0.054932 | 122.0398 | -0.058289 | 0.044419 | 0.060114 | 0.0023329 | 0.028688 | -0.0090128 | 0.027656 | -0.046997 | 0.012097 | 0.033037 | 0.059496 | 0.0010317 | 0.038681 | 0.045776 | 0.073242 | 0.054932 | 0.032043 | 0.073242 | 0.022888 | -0.1236 | 0.10986 | 0.14191 | 0.032043 | 0.027466 | 0.004578 | -0.045776 | -0.09613 | 0.07782 | -0.068664 | -121.9666 | 0.12817 | 0.086975 | 0.15564 | -121.994 | 0.009156 | -0.041198 | -122.0123 | 0.16479 | 0.086975 | 0.12817 | -122.0352 | 0.12817 | 0.10071 | 0.10986 | -122.1634 | 0.082398 | 0.05951 | 0.19684 | -122.1359
5163.125 | 122.2366 | -0.086975 | 122.0627 | 0.071411 | 0.044632 | 0.062036 | -1.7146e-05 | 0.029969 | -0.0070902 | 0.027869 | 0.036926 | 0.01402 | 0.030473 | 0.058642 | 0.0016727 | 0.042739 | 0.054932 | 0.068665 | 0.059509 | 0.009155 | 0.041199 | 0.022888 | -0.1236 | 0.09613 | 0.07782 | -0.013733 | 0 | -0.009155 | -0.041199 | -0.10986 | 0.10986 | -0.036621 | -122.0215 | 0.15564 | 0.09613 | 0.13275 | -122.0078 | 0.045776 | -0.022888 | -122.0627 | 0.1831 | 0.073242 | 0.09613 | -122.0718 | 0.12817 | 0.14191 | 0.14648 | -122.1863 | 0.086975 | 0.07782 | 0.16479 | -122.1725
5164.8906 | 122.2595 | -0.064087 | 122.0535 | 0.033264 | 0.045914 | 0.060541 | 0.0021191 | 0.030824 | -0.007731 | 0.027656 | 0.059815 | 0.013166 | 0.032182 | 0.059496 | -0.0013181 | 0.039535 | 0.041199 | 0.054932 | 0.045776 | 0.018311 | 0.068665 | 0.027466 | -0.12817 | 0.086975 | 0.07782 | -0.018311 | 0.018311 | 0.018311 | -0.054932 | -0.09613 | 0.091553 | -0.064087 | -121.9849 | 0.11902 | 0.082398 | 0.14649 | -122.0123 | 0.009155 | -0.032043 | -122.0352 | 0.15106 | 0.045776 | 0.077819 | -122.0352 | 0.13275 | 0.10529 | 0.10986 | -122.1817 | 0.082398 | 0.082398 | 0.14191 | -122.1497
5166.6562 | 122.3007 | -0.073242 | 122.0535 | 0.048523 | 0.045487 | 0.0599 | -0.00087155 | 0.031678 | -0.0017496 | 0.030219 | 0.097962 | 0.014661 | 0.030687 | 0.060992 | 0.0048769 | 0.038894 | 0.09613 | 0.086975 | 0.064087 | 0.073242 | 0.068665 | 0.022888 | -0.11444 | 0.15564 | 0.11444 | 0.018311 | 0.013733 | -0.013733 | -0.032043 | -0.09613 | 0.09613 | -0.041199 | -121.9849 | 0.16022 | 0.14648 | 0.18768 | -121.9574 | 0.041199 | -0.022888 | -122.0398 | 0.22888 | 0.091553 | 0.11444 | -122.0673 | 0.14191 | 0.16937 | 0.13733 | -122.168 | 0.086975 | 0.059509 | 0.18768 | -122.1497
5168.4219 | 122.2961 | -0.07782 | 122.0444 | -0.04303 | 0.047409 | 0.058618 | 0.0044691 | 0.026124 | -0.0075174 | 0.027228 | -0.031738 | 0.012952 | 0.035173 | 0.059496 | -0.0021725 | 0.038894 | 0.045776 | 0.064087 | 0.068665 | 0.027466 | 0.059509 | 0.004578 | -0.12817 | 0.10986 | 0.13275 | 0.018311 | 0.018311 | 0.022888 | -0.036621 | -0.10071 | 0.082398 | -0.050354 | -121.9849 | 0.14191 | 0.10529 | 0.15564 | -121.9986 | 0.041199 | -0.022888 | -122.0261 | 0.18768 | 0.096131 | 0.11902 | -122.0215 | 0.13733 | 0.1236 | 0.14649 | -122.1725 | 0.096131 | 0.10071 | 0.21057 | -122.1451
5170.1406 | 122.1863 | -0.10986 | 122.0718 | -0.21088 | 0.049759 | 0.0599 | 0.0040417 | 0.031037 | -0.0021768 | 0.031501 | -0.26062 | 0.013593 | 0.036241 | 0.060137 | -0.0015317 | 0.037185 | 0.009155 | -0.009155 | -0.036621 | -0.036621 | 0.10529 | -0.009155 | -0.15106 | 0.027466 | 0.018311 | -0.10529 | 0.054932 | 0.036621 | -0.09613 | -0.14648 | 0.10071 | -0.041199 | -121.9666 | 0.10071 | 0.073242 | 0.11444 | -122.0627 | 0.013733 | -0.036621 | -122.0169 | 0.13733 | 0.004577 | 0.041198 | -122.0352 | 0.21515 | 0.11902 | 0.073242 | -122.2229 | 0.16479 | 0.14648 | 0.12817 | -122.2183
5171.9219 | 122.2687 | -0.064087 | 122.0627 | 0.0027468 | 0.047837 | 0.062036 | 0.0038281 | 0.029115 | -0.0062356 | 0.030219 | 0.036926 | 0.013166 | 0.033464 | 0.058001 | -0.00089089 | 0.040817 | 0.027466 | 0.054932 | 0.045776 | 0.013733 | 0.068665 | 0.018311 | -0.091553 | 0.068665 | 0.073242 | -0.009155 | 0.032043 | 0.009155 | -0.050354 | -0.091553 | 0.082398 | -0.027466 | -121.994 | 0.11902 | 0.07782 | 0.10529 | -122.0352 | 0.013733 | -0.027466 | -122.0306 | 0.13275 | 0.054932 | 0.082398 | -122.0535 | 0.13275 | 0.091553 | 0.10986 | -122.1542 | 0.09613 | 0.073242 | 0.13733 | -122.1542
5173.6875 | 122.2504 | -0.059509 | 122.0535 | 0.094299 | 0.043778 | 0.057977 | 0.00041005 | 0.026551 | -0.0017496 | 0.027228 | 0.10559 | 0.013593 | 0.032396 | 0.061205 | 0.0027407 | 0.038894 | 0.091553 | 0.10986 | 0.086975 | 0.050354 | 0.073242 | 0.041199 | -0.10071 | 0.15106 | 0.10986 | 0.032043 | 0.018311 | -0.009155 | -0.041199 | -0.07782 | 0.10071 | -0.041199 | -121.9803 | 0.16937 | 0.10986 | 0.15106 | -121.962 | 0.01831 | -0.018311 | -122.0352 | 0.21057 | 0.091552 | 0.10986 | -122.0627 | 0.13275 | 0.15106 | 0.14648 | -122.1542 | 0.07782 | 0.050354 | 0.16937 | -122.1313
5175.4531 | 122.1451 | -0.10529 | 122.081 | 0.094299 | 0.050827 | 0.056909 | -0.00087155 | 0.029542 | 0.0027364 | 0.031501 | -0.046997 | 0.017224 | 0.034959 | 0.060992 | 0.0053043 | 0.035476 | 0.036621 | -0.022888 | -0.022888 | -0.018311 | 0.09613 | -0.004578 | -0.14191 | -0.004578 | -0.013733 | -0.12817 | 0.064087 | 0.050354 | -0.064087 | -0.1236 | 0.10071 | -0.036621 | -121.9849 | 0.082398 | 0.086975 | 0.1236 | -122.0444 | 0.041199 | -0.01831 | -122.0169 | 0.10071 | -0.022888 | -0.004578 | -122.0306 | 0.20142 | 0.14191 | 0.082398 | -122.2229 | 0.16937 | 0.15564 | 0.091553 | -122.2046
5177.1562 | 122.2275 | -0.07782 | 122.0627 | 0.079041 | 0.046982 | 0.059473 | -0.0025805 | 0.028474 | -0.0062356 | 0.030006 | 0.11322 | 0.014447 | 0.031114 | 0.058855 | 0.0025271 | 0.040603 | 0.082397 | 0.11902 | 0.086975 | 0.041199 | 0.064087 | 0.036621 | -0.10529 | 0.13275 | 0.11444 | 0.018311 | 0.022888 | 0.009155 | -0.050354 | -0.091553 | 0.11444 | -0.027466 | -121.9986 | 0.19684 | 0.11902 | 0.14649 | -121.9803 | 0.027466 | -0.013733 | -122.0398 | 0.21057 | 0.096131 | 0.10986 | -122.0535 | 0.14191 | 0.16022 | 0.16479 | -122.168 | 0.10071 | 0.086975 | 0.19226 | -122.1542
5178.9219 | 122.1817 | -0.09613 | 122.0535 | -0.19562 | 0.049332 | 0.060114 | 0.0059643 | 0.030397 | -0.006022 | 0.026801 | -0.15381 | 0.012952 | 0.035814 | 0.056292 | -0.00089089 | 0.038681 | 0.086975 | 0.14191 | 0.11902 | 0.073242 | 0.059509 | 0.032043 | -0.11444 | 0.1236 | 0.14648 | 0.018311 | 0.013733 | 0.013733 | -0.050354 | -0.09613 | 0.12817 | -0.018311 | -121.994 | 0.23804 | 0.16937 | 0.18768 | -121.9666 | 0.045776 | 0 | -122.0398 | 0.21973 | 0.11444 | 0.11444 | -122.0398 | 0.15564 | 0.1831 | 0.21515 | -122.168 | 0.10986 | 0.10986 | 0.24261 | -122.1497
5180.7031 | 122.2458 | -0.064087 | 122.0581 | -0.012512 | 0.047196 | 0.059686 | 0.0044691 | 0.029115 | -0.0079446 | 0.031287 | 0.036926 | 0.012311 | 0.033037 | 0.060564 | 0.0010317 | 0.038681 | 0.022888 | 0.050354 | 0.054932 | 0.013733 | 0.064087 | 0.036621 | -0.1236 | 0.07782 | 0.068665 | -0.013733 | 0.045776 | 0.013733 | -0.045776 | -0.10986 | 0.10071 | -0.059509 | -121.994 | 0.11444 | 0.07782 | 0.13733 | -122.0352 | 0.018311 | -0.045776 | -122.0123 | 0.14191 | 0.050354 | 0.09613 | -122.0444 | 0.12817 | 0.086975 | 0.11902 | -122.1817 | 0.10986 | 0.07782 | 0.13275 | -122.168
5182.4219 | 122.2961 | -0.064087 | 122.0261 | -0.065918 | 0.046341 | 0.060754 | 0.0074597 | 0.027619 | -0.007731 | 0.026801 | -0.069885 | 0.014661 | 0.033678 | 0.059496 | -0.0015317 | 0.037613 | 0.041199 | 0.10986 | 0.073242 | 0.059509 | 0.073242 | 0.032043 | -0.11444 | 0.14191 | 0.14191 | 0.050354 | 0.050354 | 0.013733 | -0.027466 | -0.09613 | 0.09613 | -0.050354 | -121.9528 | 0.17395 | 0.1236 | 0.17395 | -121.9849 | 0.036621 | -0.032043 | -121.9757 | 0.20599 | 0.11444 | 0.14648 | -122.0123 | 0.13733 | 0.10529 | 0.13733 | -122.1405 | 0.11444 | 0.07782 | 0.20599 | -122.1222
5184.1875 | 122.1725 | -0.09613 | 122.0627 | -0.10406 | 0.051468 | 0.060114 | 0.0034009 | 0.029756 | 0.0010276 | 0.029365 | -0.19196 | 0.014875 | 0.034318 | 0.061205 | 0.0031681 | 0.036117 | 0.054932 | 0.059509 | 0.009155 | 0.036621 | 0.10529 | 0.004578 | -0.14191 | 0.10986 | 0.082397 | -0.064087 | 0.045776 | 0.036621 | -0.064087 | -0.10986 | 0.10071 | -0.045777 | -121.9574 | 0.15564 | 0.13275 | 0.17853 | -122.0078 | 0.032043 | -0.013733 | -122.0169 | 0.20599 | 0.032043 | 0.045776 | -122.0261 | 0.20142 | 0.15106 | 0.10528 | -122.2046 | 0.14191 | 0.13275 | 0.17853 | -122.1725
5185.9531 | 122.1451 | -0.13733 | 122.0444 | -0.18799 | 0.048477 | 0.060968 | 0.0014783 | 0.026551 | -0.0055948 | 0.027656 | -0.23773 | 0.013593 | 0.033464 | 0.058642 | -0.00046349 | 0.039962 | 0.059509 | 0.11902 | 0.07782 | 0.054932 | 0.059509 | 0.004578 | -0.10529 | 0.086975 | 0.1236 | -0.013733 | 0.045776 | 0.032043 | -0.064087 | -0.09613 | 0.14191 | 0.032043 | -121.9849 | 0.25635 | 0.19226 | 0.16022 | -121.9849 | 0.073242 | 0.041199 | -121.9986 | 0.2243 | 0.1236 | 0.082397 | -122.0123 | 0.19684 | 0.19684 | 0.21515 | -122.1497 | 0.18311 | 0.16937 | 0.26093 | -122.1405
5187.7188 | 122.1542 | -0.09613 | 122.0306 | 0.071411 | 0.048477 | 0.058618 | 0.0012647 | 0.028474 | 0.0027364 | 0.031074 | 0.029297 | 0.015302 | 0.034105 | 0.061419 | 0.0031681 | 0.039535 | -0.013733 | -0.032043 | -0.050354 | -0.022888 | 0.10986 | 0 | -0.14191 | 0.032043 | -0.032043 | -0.11902 | 0.07782 | 0.032043 | -0.082397 | -0.11902 | 0.09613 | -0.045777 | -121.9208 | 0.064087 | 0.073242 | 0.11902 | -122.0444 | 0.013733 | -0.022889 | -121.9528 | 0.12817 | -0.022889 | 0 | -121.9986 | 0.20599 | 0.082397 | 0.045776 | -122.1725 | 0.17395 | 0.12817 | 0.064087 | -122.1497
5189.4219 | 122.1222 | -0.13275 | 122.0535 | -0.24902 | 0.048905 | 0.059473 | 0.0046827 | 0.027833 | -0.0047404 | 0.029792 | -0.18433 | 0.014234 | 0.033891 | 0.060778 | -0.0034543 | 0.039962 | 0.027466 | 0.09613 | 0.036621 | 0.041199 | 0.068665 | 0.018311 | -0.12817 | 0.041199 | 0.073242 | -0.050354 | 0.064087 | 0.032043 | -0.064087 | -0.1236 | 0.15106 | 0.004577 | -121.9849 | 0.22888 | 0.17395 | 0.16937 | -122.0261 | 0.068664 | 0.009155 | -121.9894 | 0.17395 | 0.082397 | 0.073242 | -122.0215 | 0.20142 | 0.16022 | 0.16937 | -122.1817 | 0.19684 | 0.16479 | 0.20599 | -122.1771
5191.2031 | 122.2366 | -0.054932 | 122.0169 | -0.0048827 | 0.045487 | 0.060541 | 0.0046827 | 0.028047 | -0.010295 | 0.02851 | 0.044556 | 0.014447 | 0.034105 | 0.060137 | -3.629e-05 | 0.040817 | 0.004578 | 0.064087 | 0.050354 | 0.022888 | 0.068665 | 0.018311 | -0.11444 | 0.091553 | 0.086975 | 0.009155 | 0.032043 | 0.018311 | -0.045776 | -0.091553 | 0.073243 | -0.059509 | -121.9482 | 0.11902 | 0.07782 | 0.13733 | -122.0123 | 0.009156 | -0.036621 | -121.9849 | 0.14649 | 0.064087 | 0.10071 | -121.9986 | 0.1236 | 0.05951 | 0.10529 | -122.1313 | 0.086975 | 0.073243 | 0.14191 | -122.1085
5192.9688 | 122.1313 | -0.1236 | 122.0444 | 0.048523 | 0.04805 | 0.05755 | -0.00087155 | 0.02826 | 0.0010276 | 0.030433 | -0.054626 | 0.016797 | 0.035387 | 0.061419 | 0.0048769 | 0.036758 | 0.009155 | -0.018311 | -0.054932 | -0.004578 | 0.086975 | 0.013733 | -0.14648 | 0.027466 | -0.018311 | -0.12817 | 0.082397 | 0.041199 | -0.07782 | -0.11902 | 0.13733 | -0.022888 | -121.9574 | 0.10528 | 0.11902 | 0.14191 | -122.0352 | 0.045776 | 0.004577 | -121.962 | 0.15106 | -0.004578 | -0.009155 | -122.0032 | 0.21057 | 0.13275 | 0.068664 | -122.1909 | 0.20599 | 0.16479 | 0.10528 | -122.1634
5194.7344 | 122.2641 | -0.068665 | 122.0078 | -0.0354 | 0.046128 | 0.060327 | 0.0019055 | 0.02591 | -0.0073038 | 0.030433 | 0.014038 | 0.013166 | 0.032182 | 0.056933 | -0.0021725 | 0.042312 | -0.004578 | 0.073242 | 0.036621 | 0.041199 | 0.07782 | 0.022888 | -0.13275 | 0.09613 | 0.11444 | 0.032043 | 0.032043 | 0 | -0.036621 | -0.086975 | 0.091553 | -0.064086 | -121.9299 | 0.14191 | 0.10986 | 0.17395 | -122.0123 | 0.032044 | -0.01831 | -121.9757 | 0.16479 | 0.10071 | 0.11902 | -122.0078 | 0.14649 | 0.064087 | 0.10529 | -122.1405 | 0.10071 | 0.068665 | 0.18311 | -122.0947
5196.4531 | 122.1405 | -0.10986 | 122.0535 | -0.20325 | 0.049118 | 0.059045 | 0.0055371 | 0.030824 | -0.0034586 | 0.029151 | -0.23773 | 0.015088 | 0.032823 | 0.05971 | -0.00024989 | 0.039322 | 0.041199 | 0.10529 | 0.068665 | 0.054932 | 0.073242 | 0.009155 | -0.13733 | 0.07782 | 0.10986 | -0.018311 | 0.041199 | 0.027466 | -0.045776 | -0.10986 | 0.11902 | -0.027466 | -121.9803 | 0.21515 | 0.16479 | 0.19226 | -122.0123 | 0.064087 | 0 | -122.0123 | 0.18768 | 0.091552 | 0.091552 | -122.0261 | 0.18311 | 0.15106 | 0.17853 | -122.1909 | 0.15106 | 0.13733 | 0.21973 | -122.1634
5198.2188 | 122.1909 | -0.082397 | 122.0215 | 0.025635 | 0.044205 | 0.060968 | 0.0014783 | 0.026124 | -0.007731 | 0.02851 | 0.067444 | 0.015515 | 0.032823 | 0.060137 | 0.00017731 | 0.039535 | 0.032043 | 0.082397 | 0.045776 | 0.045776 | 0.07782 | 0.050354 | -0.11444 | 0.086975 | 0.086975 | -0.004578 | 0.050354 | -0.004578 | -0.036621 | -0.091553 | 0.13275 | -0.032044 | -121.9437 | 0.16479 | 0.12817 | 0.16022 | -121.9894 | 0.045776 | -0.009156 | -121.9711 | 0.16937 | 0.077819 | 0.086975 | -122.0261 | 0.16022 | 0.11444 | 0.12817 | -122.1359 | 0.13275 | 0.077819 | 0.16937 | -122.113
5199.9844 | 122.2504 | -0.045776 | 122.0306 | -0.096436 | 0.041214 | -0.034094 | -0.00044435 | 0.028688 | -0.0090128 | 0.02616 | -0.10803 | 0.012311 | 0.03026 | 0.058642 | 0.0014591 | 0.040176 | 0.073242 | 0.12817 | 0.09613 | 0.068665 | 0.050354 | 0.032043 | -0.11902 | 0.15106 | 0.15564 | 0.064087 | 0.032043 | 0.004578 | -0.022888 | -0.082397 | 0.077819 | -0.073243 | -121.9803 | 0.17395 | 0.11444 | 0.18768 | -121.9574 | 0.022888 | -0.036621 | -121.9986 | 0.19684 | 0.10986 | 0.14648 | -122.0261 | 0.09613 | 0.11902 | 0.14191 | -122.1497 | 0.077819 | 0.050354 | 0.20142 | -122.113
5201.7031 | 122.2504 | -0.064087 | 121.9986 | -0.14221 | 0.043564 | 0.061823 | 0.0025465 | 0.026765 | -0.0064492 | 0.027015 | -0.092773 | 0.011029 | 0.031755 | 0.057787 | -0.00024989 | 0.039962 | 0.1236 | 0.14191 | 0.10986 | 0.07782 | 0.07782 | 0.022888 | -0.1236 | 0.16937 | 0.16937 | 0.07782 | 0.036621 | 0.018311 | -0.027466 | -0.073242 | 0.086975 | -0.059509 | -121.9208 | 0.20599 | 0.14191 | 0.20142 | -121.875 | 0.036621 | -0.009155 | -121.962 | 0.23346 | 0.14191 | 0.15106 | -121.9803 | 0.14191 | 0.18768 | 0.17395 | -122.1222 | 0.10071 | 0.082398 | 0.23346 | -122.0718
5203.4688 | 122.1451 | -0.10529 | 122.0627 | 0.079041 | 0.049332 | 0.056696 | 0.0027601 | 0.027833 | 0.0016684 | 0.030006 | 0.0064086 | 0.014447 | 0.033037 | 0.063555 | 0.0040225 | 0.036544 | 0.027466 | -0.050354 | -0.041199 | -0.009155 | 0.10071 | 0.009155 | -0.14648 | 0.041199 | -0.032043 | -0.11444 | 0.064087 | 0.036621 | -0.073242 | -0.10529 | 0.11444 | -0.041198 | -121.962 | 0.054932 | 0.096131 | 0.13733 | -122.0352 | 0.032044 | 0 | -121.9986 | 0.14649 | -0.009155 | -0.009155 | -122.0261 | 0.20599 | 0.13275 | 0.064087 | -122.2092 | 0.16937 | 0.14191 | 0.073243 | -122.168
5205.1719 | 122.2183 | -0.068665 | 122.0215 | 0.10193 | 0.048477 | 0.059259 | 0.0023329 | 0.029542 | 0.00038662 | 0.031287 | 0.059815 | 0.015302 | 0.03325 | 0.061632 | 0.0040225 | 0.037613 | 0.041199 | -0.022888 | -0.032043 | -0.022888 | 0.10529 | -0.004578 | -0.14648 | 0.064087 | 0.004578 | -0.07782 | 0.041199 | 0.036621 | -0.045776 | -0.10986 | 0.064087 | -0.077819 | -121.9162 | 0.045777 | 0.045777 | 0.1236 | -121.9803 | 0.022889 | -0.041198 | -121.9803 | 0.13275 | -0.009155 | 0.032043 | -121.9849 | 0.17395 | 0.10986 | 0.036622 | -122.168 | 0.10986 | 0.10529 | 0.073243 | -122.1313
5206.9375 | 122.2504 | -0.045776 | 121.9986 | 0.079041 | 0.046128 | 0.059045 | 0.00062385 | 0.027406 | 0.00081382 | 0.030646 | 0.13611 | 0.015943 | 0.034532 | 0.061205 | 0.0025271 | 0.038681 | 0.027466 | -0.013733 | -0.018311 | -0.013733 | 0.091553 | 0.004578 | -0.13733 | 0.07782 | 0.036621 | -0.059509 | 0.041199 | 0.032043 | -0.045776 | -0.11444 | 0.050354 | -0.091553 | -121.907 | 0.032043 | 0.032043 | 0.1236 | -121.9711 | 0 | -0.068665 | -121.9574 | 0.1236 | -0.013733 | 0.054932 | -121.9666 | 0.13733 | 0.073242 | 0.027465 | -122.1359 | 0.086975 | 0.077819 | 0.082397 | -122.113
5208.7031 | 122.2412 | -0.064087 | 122.0261 | -0.14221 | 0.046128 | 0.058832 | 0.0059643 | 0.027192 | -0.008372 | 0.028724 | -0.077515 | 0.012311 | 0.033464 | 0.059496 | -0.0030271 | 0.039749 | 0.073242 | 0.14648 | 0.11444 | 0.068665 | 0.059509 | 0.032043 | -0.1236 | 0.15564 | 0.16937 | 0.07782 | 0.032043 | 0.018311 | -0.022888 | -0.07782 | 0.09613 | -0.059509 | -121.9666 | 0.21057 | 0.13275 | 0.19226 | -121.9528 | 0.041199 | -0.013733 | -121.994 | 0.21973 | 0.14191 | 0.15564 | -122.0078 | 0.1236 | 0.13733 | 0.17853 | -122.1497 | 0.09613 | 0.082398 | 0.23346 | -122.1039
5210.5781 | 122.2 | -0.073242 | 121.9711 | 0.14771 | 0.049118 | 0.058405 | 0.0016919 | 0.03061 | -0.004313 | 0.029578 | 0.15137 | 0.013379 | 0.033464 | 0.063128 | 0.0033817 | 0.039108 | 0.086975 | 0.11902 | 0.10529 | 0.068665 | 0.045776 | 0.045776 | -0.10071 | 0.16022 | 0.13733 | 0.032043 | 0.009155 | 0.004578 | -0.036621 | -0.091553 | 0.11902 | -0.027466 | -121.9254 | 0.19226 | 0.14191 | 0.16937 | -121.8842 | 0.036621 | -0.018311 | -121.962 | 0.23346 | 0.10529 | 0.1236 | -121.9666 | 0.11902 | 0.16022 | 0.17853 | -122.0718 | 0.082397 | 0.07782 | 0.21057 | -122.0627
5212.375 | 122.0993 | -0.11902 | 122.0169 | -0.19562 | 0.050614 | 0.056055 | 0.0051099 | 0.026979 | -0.0047404 | 0.029578 | -0.2301 | 0.012738 | 0.036882 | 0.05971 | -0.00046349 | 0.040603 | 0.050354 | 0.11444 | 0.07782 | 0.059509 | 0.082397 | 0.018311 | -0.13275 | 0.07782 | 0.10071 | -0.032043 | 0.041199 | 0.032043 | -0.045776 | -0.10529 | 0.13733 | -0.013732 | -121.9345 | 0.23346 | 0.17853 | 0.19226 | -121.9666 | 0.073243 | 0.013733 | -121.9757 | 0.19684 | 0.086976 | 0.073243 | -121.9849 | 0.20142 | 0.16937 | 0.19684 | -122.1497 | 0.16022 | 0.15106 | 0.21973 | -122.1222
5214.0938 | 122.0947 | -0.11444 | 122.0306 | -0.23376 | 0.046982 | 0.062036 | 0.0019055 | 0.026765 | -0.0058084 | 0.02851 | -0.25299 | 0.013806 | 0.033464 | 0.060351 | 0.0020999 | 0.039108 | 0.050354 | 0.09613 | 0.050354 | 0.050354 | 0.068665 | -0.004578 | -0.13733 | 0.054932 | 0.07782 | -0.064087 | 0.045776 | 0.032043 | -0.045776 | -0.11902 | 0.10986 | -0.022888 | -121.962 | 0.21057 | 0.16479 | 0.18768 | -121.9803 | 0.068665 | -0.004578 | -121.9849 | 0.16937 | 0.050354 | 0.054932 | -121.9986 | 0.18311 | 0.16479 | 0.16479 | -122.168 | 0.16022 | 0.14648 | 0.19226 | -122.1497
5215.7969 | 122.1405 | -0.07782 | 122.0169 | -0.21088 | 0.051255 | 0.056696 | 0.0038281 | 0.027619 | 0.00038662 | 0.028724 | -0.22247 | 0.014661 | 0.032823 | 0.0627 | 0.0044497 | 0.041458 | 0.036621 | 0.027466 | 0 | 0.027466 | 0.09613 | -0.013733 | -0.14648 | 0.064087 | 0.064087 | -0.054932 | 0.068665 | 0.032043 | -0.068665 | -0.11902 | 0.064087 | -0.068664 | -121.9208 | 0.10529 | 0.10529 | 0.17395 | -121.9803 | 0.009155 | -0.041199 | -121.9482 | 0.14191 | 0.022888 | 0.064087 | -121.9849 | 0.17395 | 0.11444 | 0.07782 | -122.1634 | 0.14649 | 0.10986 | 0.14191 | -122.1359
5217.5312 | 122.1863 | -0.059509 | 121.9711 | -0.0048827 | 0.04805 | 0.060114 | 0.0031873 | 0.025697 | -0.0073038 | 0.028297 | 0.029297 | 0.012097 | 0.034105 | 0.063341 | -0.0017453 | 0.044021 | 0.013733 | 0.059509 | 0.050354 | 0.032043 | 0.07782 | 0.041199 | -0.11902 | 0.091553 | 0.09613 | -0.009155 | 0.032043 | 0.022888 | -0.059509 | -0.09613 | 0.10071 | -0.05951 | -121.8933 | 0.11902 | 0.091552 | 0.15106 | -121.9574 | 0 | -0.036621 | -121.9391 | 0.15106 | 0.050354 | 0.086975 | -121.9482 | 0.13733 | 0.073242 | 0.10986 | -122.0901 | 0.091552 | 0.082397 | 0.15564 | -122.0673
5219.3594 | 122.2275 | -0.073242 | 121.9574 | 0.056152 | 0.048691 | 0.060968 | -0.0015125 | 0.026765 | -0.0011088 | 0.03086 | 0.11322 | 0.014875 | 0.03261 | 0.063341 | 0.0055179 | 0.040603 | 0.009155 | 0.009155 | -0.027466 | -0.013733 | 0.11902 | 0.004578 | -0.1236 | 0.086975 | 0.036621 | -0.036621 | 0.050354 | 0.027466 | -0.054932 | -0.10071 | 0.07782 | -0.050354 | -121.8384 | 0.082397 | 0.059509 | 0.10986 | -121.9482 | 0.01831 | -0.027466 | -121.907 | 0.16022 | 0.036621 | 0.064087 | -121.9299 | 0.19226 | 0.082397 | 0.045776 | -122.081 | 0.1236 | 0.10071 | 0.10986 | -122.0581
5221.1094 | 122.1451 | -0.064087 | 121.994 | -0.21088 | 0.047623 | 0.062463 | 0.0070325 | 0.028474 | -0.0070902 | 0.028297 | -0.12329 | 0.014661 | 0.032823 | 0.063555 | -0.00067729 | 0.041885 | 0.07782 | 0.14648 | 0.11444 | 0.082397 | 0.041199 | 0.032043 | -0.11444 | 0.1236 | 0.16937 | 0.036621 | -0.004578 | 0.009155 | -0.027466 | -0.086975 | 0.09613 | -0.050354 | -121.9528 | 0.21057 | 0.14648 | 0.19684 | -121.9162 | 0.036621 | -0.022888 | -121.9986 | 0.18768 | 0.10071 | 0.1236 | -121.9849 | 0.10529 | 0.14191 | 0.17853 | -122.1085 | 0.059509 | 0.073242 | 0.23346 | -122.081
5222.875 | 122.0947 | -0.10529 | 122.0123 | -0.10406 | 0.048264 | 0.057764 | 0.0014783 | 0.026979 | 0.00060022 | 0.029578 | -0.14618 | 0.016584 | 0.033891 | 0.065264 | 0.0053043 | 0.042312 | 0.059509 | 0.045776 | 0.018311 | 0.032043 | 0.091553 | -0.004578 | -0.15106 | 0.086975 | 0.086975 | -0.059509 | 0.054932 | 0.036621 | -0.041199 | -0.1236 | 0.10071 | -0.045776 | -121.9208 | 0.15106 | 0.13733 | 0.18311 | -121.9528 | 0.064087 | -0.01831 | -121.9574 | 0.19226 | 0.045777 | 0.064087 | -121.9757 | 0.19684 | 0.16479 | 0.1236 | -122.1634 | 0.16022 | 0.14191 | 0.19226 | -122.1359
5224.7031 | 122.1634 | -0.091553 | 121.9574 | 0.079041 | 0.044419 | 0.059686 | -0.00065795 | 0.028047 | -0.0053812 | 0.029365 | 0.16663 | 0.01402 | 0.031755 | 0.063555 | 0.0025271 | 0.047653 | 0.068665 | 0.10529 | 0.082397 | 0.045776 | 0.059509 | 0.054932 | -0.11444 | 0.11902 | 0.10529 | 0.009155 | 0.032043 | 0.032043 | -0.041199 | -0.07782 | 0.14649 | -0.022888 | -121.8979 | 0.19684 | 0.13733 | 0.16022 | -121.8887 | 0.050354 | 0.013733 | -121.9254 | 0.21057 | 0.10071 | 0.086975 | -121.9254 | 0.15106 | 0.16022 | 0.17395 | -122.0718 | 0.1236 | 0.1236 | 0.19684 | -122.0352
5226.5 | 122.0764 | -0.11444 | 121.9711 | -0.1651 | 0.046341 | 0.059473 | 0.0029737 | 0.029328 | -0.0062356 | 0.02851 | -0.26062 | 0.015088 | 0.031755 | 0.063128 | 0.0023135 | 0.044448 | 0 | 0 | -0.018311 | -0.018311 | 0.091553 | -0.013733 | -0.16479 | 0.022888 | 0.036621 | -0.10529 | 0.064087 | 0.068665 | -0.07782 | -0.1236 | 0.10071 | -0.050354 | -121.8796 | 0.11444 | 0.09613 | 0.14648 | -121.9711 | 0.036621 | -0.009155 | -121.907 | 0.13733 | 0.009155 | 0.01831 | -121.9025 | 0.20599 | 0.11444 | 0.09613 | -122.1359 | 0.17853 | 0.18311 | 0.15106 | -122.0947
5228.2969 | 121.0098 | -0.064087 | 120.7901 | 0.10956 | 0.04506 | 0.060754 | 0.0031873 | 0.028047 | -0.006663 | 0.029151 | 0.097962 | 0.012952 | 0.031328 | 0.069109 | 0.0010317 | 0.052993 | 0.064087 | 0.086975 | 0.068665 | 0.027466 | 0.064087 | 0.041199 | -0.09613 | 0.10071 | 0.086975 | -0.022888 | 0.018311 | 0.018311 | -0.027466 | -0.086975 | 0.10529 | -0.032043 | -120.726 | 0.15106 | 0.091553 | 0.1236 | -120.726 | 0.036621 | -0.022888 | -120.7718 | 0.1648 | 0.041199 | 0.064087 | -120.7718 | 0.12817 | 0.12817 | 0.13275 | -120.8862 | 0.082398 | 0.082398 | 0.15106 | -120.8771
5230.0156 | 121.8475 | -0.073242 | 121.6461 | 0.12482 | 0.046128 | 0.060327 | 0.0010511 | 0.029328 | -0.0034586 | 0.027015 | 0.14374 | 0.013593 | 0.030687 | 0.063555 | 0.0018863 | 0.041671 | 0.09613 | 0.11444 | 0.10529 | 0.068665 | 0.050354 | 0.059509 | -0.10986 | 0.14648 | 0.13275 | 0.041199 | 0.013733 | 0.009155 | -0.022888 | -0.07782 | 0.13275 | -0.036621 | -121.5958 | 0.18768 | 0.14191 | 0.17853 | -121.55 | 0.050354 | -0.004578 | -121.6324 | 0.21973 | 0.11444 | 0.11902 | -121.637 | 0.1236 | 0.16937 | 0.17853 | -121.756 | 0.086975 | 0.082397 | 0.20599 | -121.7239
5231.8125 | 121.9482 | -0.07782 | 121.7194 | 0.12482 | 0.049118 | 0.057123 | 0.0025465 | 0.026338 | -0.0036722 | 0.028724 | 0.12848 | 0.013166 | 0.032823 | 0.074236 | 0.0023135 | 0.05513 | 0.11444 | 0.086975 | 0.10986 | 0.073242 | 0.054932 | 0.050354 | -0.10071 | 0.16479 | 0.1236 | 0.036621 | 0.013733 | 0.009155 | -0.032043 | -0.073242 | 0.12817 | -0.022888 | -121.6644 | 0.16479 | 0.15106 | 0.17395 | -121.6049 | 0.045777 | 0.004578 | -121.7056 | 0.24261 | 0.11444 | 0.10986 | -121.7102 | 0.13275 | 0.19226 | 0.18768 | -121.8201 | 0.091553 | 0.086975 | 0.20142 | -121.7926
5233.6094 | 121.9254 | -0.11444 | 121.6095 | -0.012512 | 0.046982 | 0.061395 | 0.0042555 | 0.028901 | -0.0085856 | 0.02851 | 0.021668 | 0.012952 | 0.03325 | 0.13426 | -0.0025999 | 0.10448 | 0.041199 | 0.045776 | 0.041199 | 0.036621 | 0.068665 | 0.018311 | -0.1236 | 0.086975 | 0.09613 | 0.004578 | 0.022888 | 0.013733 | -0.059509 | -0.10986 | 0.13275 | -0.009155 | -121.5408 | 0.16022 | 0.15106 | 0.16022 | -121.5683 | 0.054932 | 0.004578 | -121.5866 | 0.20142 | 0.11902 | 0.11444 | -121.5958 | 0.18311 | 0.15564 | 0.15564 | -121.7331 | 0.13733 | 0.12817 | 0.21057 | -121.7194
5235.375 | 121.8475 | -0.13275 | 121.6599 | -0.11932 | 0.048691 | 0.058618 | 0.0016919 | 0.028901 | 0.001882 | 0.026374 | -0.40558 | 0.014234 | 0.029832 | 0.14644 | 0.0038089 | 0.11601 | 0.027466 | -0.041199 | -0.045776 | -0.009155 | 0.10071 | -0.022888 | -0.17395 | 0.013733 | 0.018311 | -0.09613 | 0.059509 | 0.041199 | -0.10071 | -0.14191 | 0.10986 | -0.041199 | -121.5591 | 0.091552 | 0.1236 | 0.16479 | -121.6324 | 0.032043 | -0.009156 | -121.6003 | 0.14648 | 0.036621 | 0.045777 | -121.6187 | 0.23346 | 0.16022 | 0.086975 | -121.8338 | 0.19226 | 0.17395 | 0.15106 | -121.8018
5237.125 | 121.8246 | -0.10986 | 121.7194 | -0.25665 | 0.049546 | 0.058832 | 0.0076733 | 0.030397 | -0.0040994 | 0.028724 | -0.21484 | 0.015729 | 0.033037 | 0.082781 | -0.00067729 | 0.058761 | 0.036621 | 0.041199 | 0.032043 | 0.032043 | 0.082397 | 0.004578 | -0.13275 | 0.041199 | 0.041199 | -0.073242 | 0.050354 | 0.045776 | -0.07782 | -0.12817 | 0.11444 | -0.022888 | -121.637 | 0.15106 | 0.14191 | 0.16479 | -121.6827 | 0.032043 | -0.018311 | -121.669 | 0.15106 | 0.036621 | 0.054932 | -121.6736 | 0.19226 | 0.14648 | 0.14191 | -121.8521 | 0.16022 | 0.15564 | 0.15106 | -121.8475
5238.9688 | 121.962 | -0.086975 | 121.6965 | 0.14771 | 0.045914 | 0.059045 | 0.00019645 | 0.029115 | -0.0030314 | 0.030219 | 0.12085 | 0.01637 | 0.032182 | 0.082995 | 0.0029543 | 0.067093 | 0.10986 | 0.10071 | 0.082397 | 0.082397 | 0.064087 | 0.041199 | -0.10986 | 0.15564 | 0.1236 | 0.022888 | 0.018311 | 0 | -0.027466 | -0.086975 | 0.12817 | -0.022888 | -121.6324 | 0.18768 | 0.16937 | 0.19226 | -121.5866 | 0.059509 | 0 | -121.6782 | 0.24261 | 0.10986 | 0.10986 | -121.6965 | 0.15106 | 0.19684 | 0.16937 | -121.8063 | 0.10529 | 0.086975 | 0.21057 | -121.7834
5240.7031 | 121.8201 | -0.31586 | 121.5317 | -0.26428 | 0.050827 | 0.060754 | 0.0066053 | 0.028901 | -0.002604 | 0.030219 | -0.26062 | 0.017652 | 0.031755 | 0.38762 | 0.0046633 | 0.36723 | -0.032043 | -0.045776 | -0.068665 | -0.050354 | 0.07782 | -0.032043 | -0.16937 | -0.068665 | -0.045776 | -0.15564 | -0.013733 | -0.027466 | -0.23804 | -0.27466 | 0.28381 | 0.14648 | -121.4539 | 0.27008 | 0.2655 | 0.11902 | -121.5637 | 0.07782 | 0.041199 | -121.5454 | 0.24719 | 0.16022 | 0.11902 | -121.5591 | 0.39368 | 0.28381 | 0.24719 | -121.701 | 0.30212 | 0.28839 | 0.27008 | -121.8063
5242.4219 | 117.0181 | -0.1236 | 116.7114 | -0.13458 | 0.048264 | 0.059686 | 0.0046827 | 0.026979 | -0.006663 | 0.027442 | -0.1004 | 0.0046206 | 0.040941 | 0.13234 | -3.629e-05 | 0.22282 | 0.082397 | 0.14191 | 0.11902 | 0.050354 | 0.064087 | 0.018311 | -0.1236 | 0.1236 | 0.16937 | 0.082397 | -0.018311 | -0.013733 | -0.09613 | -0.15564 | 0.14191 | 0 | -116.6473 | 0.2655 | 0.17395 | 0.17395 | -116.629 | 0.027466 | -0.032044 | -116.7297 | 0.24719 | 0.20599 | 0.23804 | -116.7252 | 0.18768 | 0.20599 | 0.24261 | -116.835 | 0.10528 | 0.10986 | 0.29297 | -116.8671
5244.1719 | 121.5591 | -0.07782 | 121.3577 | -0.020142 | 0.04506 | 0.0599 | -0.0010851 | 0.028901 | -0.0038858 | 0.029792 | 0.082703 | 0.012738 | 0.031755 | 0.075518 | 0.0023135 | 0.054061 | 0.086975 | 0.1236 | 0.09613 | 0.068665 | 0.054932 | 0.045776 | -0.10529 | 0.15106 | 0.1236 | 0.022888 | 0.027466 | -0.004578 | -0.032043 | -0.07782 | 0.1236 | -0.027466 | -121.3028 | 0.20142 | 0.14649 | 0.17395 | -121.2708 | 0.045777 | 0 | -121.3303 | 0.22888 | 0.10071 | 0.10071 | -121.3623 | 0.13275 | 0.16479 | 0.17395 | -121.463 | 0.10529 | 0.073242 | 0.20142 | -121.4355
5245.9062 | 121.6873 | -0.068665 | 121.463 | -0.096436 | 0.043351 | 0.062891 | 0.0016919 | 0.027192 | -0.0079446 | 0.029151 | -0.11566 | 0.010816 | 0.031114 | 0.071886 | 0.00017731 | 0.051284 | 0.07782 | 0.10529 | 0.091553 | 0.064087 | 0.086975 | 0.027466 | -0.10986 | 0.14648 | 0.17395 | 0.050354 | 0.032043 | 0.018311 | -0.027466 | -0.07782 | 0.096131 | -0.041198 | -121.376 | 0.17395 | 0.13275 | 0.17395 | -121.3852 | 0.041199 | -0.009155 | -121.431 | 0.21515 | 0.11902 | 0.12817 | -121.4447 | 0.15564 | 0.14649 | 0.16022 | -121.5729 | 0.10071 | 0.086976 | 0.24261 | -121.5408
5247.625 | 121.6141 | -0.10986 | 121.5637 | -0.25665 | 0.048691 | 0.0599 | 0.0063917 | 0.029328 | -0.0017496 | 0.02851 | -0.25299 | 0.016797 | 0.033891 | 0.068041 | 0.0014591 | 0.045089 | 0.004578 | -0.018311 | -0.041199 | -0.018311 | 0.11444 | -0.018311 | -0.15106 | 0.041199 | 0.018311 | -0.11444 | 0.07782 | 0.045776 | -0.082397 | -0.14191 | 0.091552 | -0.041199 | -121.4493 | 0.091552 | 0.091552 | 0.13275 | -121.5591 | 0.027466 | -0.032044 | -121.4859 | 0.15106 | -0.004578 | 0.027466 | -121.5179 | 0.2243 | 0.11444 | 0.068664 | -121.7148 | 0.18768 | 0.15564 | 0.12817 | -121.7056
5249.3594 | 121.7239 | -0.064087 | 121.5271 | 0.094299 | 0.046982 | 0.055414 | 0.0010511 | 0.028688 | -0.00089518 | 0.029792 | 0.10559 | 0.014661 | 0.032823 | 0.070391 | 0.0033817 | 0.047012 | 0.009155 | 0 | -0.004578 | 0 | 0.09613 | 0.004578 | -0.13275 | 0.10071 | 0.045776 | -0.041199 | 0.054932 | 0.022888 | -0.045776 | -0.09613 | 0.068665 | -0.068664 | -121.431 | 0.064087 | 0.064087 | 0.13275 | -121.5179 | 0.018311 | -0.032043 | -121.4722 | 0.1648 | 0.022888 | 0.054931 | -121.5042 | 0.16022 | 0.073242 | 0.059509 | -121.6599 | 0.11902 | 0.086975 | 0.10986 | -121.6232
5251.1562 | 121.7239 | -0.059509 | 121.6141 | 0.025635 | 0.043351 | 0.0599 | 0.0019055 | 0.028688 | -0.0087992 | 0.027869 | 0.052185 | 0.01167 | 0.031328 | 0.053728 | 0.0010317 | 0.03334 | 0.036621 | 0.082397 | 0.054932 | 0.032043 | 0.059509 | 0.036621 | -0.10986 | 0.10071 | 0.086975 | -0.009155 | 0.032043 | 0.009155 | -0.022888 | -0.091553 | 0.09613 | -0.050354 | -121.5546 | 0.14191 | 0.091552 | 0.14191 | -121.5775 | 0.036621 | -0.032044 | -121.582 | 0.16022 | 0.050354 | 0.082398 | -121.6049 | 0.11902 | 0.09613 | 0.11444 | -121.7239 | 0.091552 | 0.068664 | 0.14648 | -121.7056
5252.8594 | 121.7651 | -0.054932 | 121.637 | -0.10406 | 0.053818 | 0.057977 | 0.0048963 | 0.031251 | 0.0012412 | 0.029578 | -0.19196 | 0.015088 | 0.035173 | 0.054369 | 0.0018863 | 0.029708 | 0.027466 | 0.045776 | 0.004578 | 0.032043 | 0.11444 | -0.004578 | -0.14648 | 0.073242 | 0.086975 | -0.068665 | 0.073242 | 0.027466 | -0.050354 | -0.10071 | 0.050354 | -0.091552 | -121.5225 | 0.10071 | 0.086975 | 0.17853 | -121.6095 | 0.004578 | -0.045776 | -121.5637 | 0.12817 | -0.013733 | 0.032043 | -121.6095 | 0.16937 | 0.082398 | 0.05951 | -121.7834 | 0.12817 | 0.082398 | 0.14191 | -121.7377
5254.5625 | 121.7743 | -0.064087 | 121.6187 | 0.071411 | 0.048691 | 0.059259 | 0.0023329 | 0.031037 | -0.0055948 | 0.030433 | 0.090332 | 0.012525 | 0.033464 | 0.053301 | -0.00024989 | 0.035476 | 0.073242 | 0.13733 | 0.10529 | 0.068665 | 0.054932 | 0.027466 | -0.091553 | 0.14648 | 0.13275 | 0.041199 | 0.018311 | -0.004578 | -0.013733 | -0.10529 | 0.091553 | -0.027466 | -121.5637 | 0.20142 | 0.13275 | 0.16022 | -121.5454 | 0.050354 | -0.041199 | -121.6003 | 0.21057 | 0.10529 | 0.14649 | -121.6232 | 0.11902 | 0.13733 | 0.16937 | -121.7102 | 0.082398 | 0.059509 | 0.19684 | -121.7239
5256.3281 | 121.7606 | -0.068665 | 121.5729 | 0.13245 | 0.0457 | 0.056909 | 0.0025465 | 0.029328 | -0.002604 | 0.030219 | 0.12848 | 0.012738 | 0.03261 | 0.052019 | 0.0012455 | 0.030563 | 0.091553 | 0.1236 | 0.10986 | 0.07782 | 0.064087 | 0.050354 | -0.091553 | 0.16022 | 0.13733 | 0.041199 | 0.022888 | 0.009155 | -0.036621 | -0.073242 | 0.11902 | -0.022888 | -121.5088 | 0.19226 | 0.14649 | 0.16937 | -121.4813 | 0.032044 | -0.004577 | -121.55 | 0.22888 | 0.10986 | 0.11444 | -121.5637 | 0.13275 | 0.16022 | 0.17853 | -121.6644 | 0.091553 | 0.07782 | 0.20599 | -121.6461
5258.1094 | 121.7789 | -0.10986 | 121.6461 | -0.12695 | 0.049118 | 0.059686 | 0.0055371 | 0.029328 | 0.0014548 | 0.030646 | -0.16144 | 0.018292 | 0.03325 | 0.089617 | 0.0042361 | 0.064315 | 0.059509 | 0.050354 | 0.022888 | 0.027466 | 0.10071 | 0 | -0.14191 | 0.086975 | 0.064087 | -0.059509 | 0.059509 | 0.032043 | -0.068665 | -0.11444 | 0.10986 | -0.032044 | -121.5454 | 0.16022 | 0.13733 | 0.16937 | -121.5866 | 0.041198 | -0.004578 | -121.5866 | 0.19684 | 0.050354 | 0.054932 | -121.6141 | 0.21057 | 0.16937 | 0.13275 | -121.788 | 0.16937 | 0.14191 | 0.17395 | -121.7606
5259.875 | 121.8018 | -0.09613 | 121.6461 | -0.1651 | 0.049118 | 0.059045 | 0.0034009 | 0.027619 | -0.0023904 | 0.030646 | -0.18433 | 0.017011 | 0.033037 | 0.07744 | 0.0029543 | 0.055343 | 0.022888 | 0.041199 | -0.009155 | 0.009155 | 0.10529 | -0.009155 | -0.15564 | 0.073242 | 0.064087 | -0.059509 | 0.050354 | 0.041199 | -0.068665 | -0.1236 | 0.086975 | -0.05951 | -121.5408 | 0.13733 | 0.10528 | 0.16479 | -121.6232 | 0.027465 | -0.027466 | -121.5958 | 0.16937 | 0.036621 | 0.064087 | -121.6049 | 0.20142 | 0.11902 | 0.086975 | -121.8018 | 0.14648 | 0.13733 | 0.16022 | -121.7697
5261.6562 | 121.756 | -0.11902 | 121.6278 | -0.20325 | 0.046982 | 0.059473 | 0.0034009 | 0.026765 | -0.0096536 | 0.029151 | -0.13855 | 0.015943 | 0.032823 | 0.096026 | -0.0013181 | 0.07991 | 0.050354 | 0.15106 | 0.11444 | 0.073242 | 0.050354 | 0.022888 | -0.11444 | 0.10529 | 0.16022 | 0.036621 | 0.022888 | 0.004578 | -0.054932 | -0.082397 | 0.14191 | 0.004578 | -121.5775 | 0.27008 | 0.19226 | 0.18768 | -121.5775 | 0.064087 | 0.036622 | -121.6049 | 0.22431 | 0.15564 | 0.11902 | -121.6232 | 0.16937 | 0.16937 | 0.23346 | -121.7422 | 0.14191 | 0.1236 | 0.27924 | -121.7102
5263.4062 | 121.7056 | -0.12817 | 121.6324 | -0.058289 | 0.050614 | 0.059686 | 0.0027601 | 0.029328 | -0.00025418 | 0.02851 | -0.054626 | 0.015515 | 0.03325 | 0.092608 | 0.0050907 | 0.068801 | 0.032043 | 0.027466 | -0.004578 | 0.018311 | 0.09613 | -0.004578 | -0.14191 | 0.027466 | 0.018311 | -0.10071 | 0.064087 | 0.013733 | -0.07782 | -0.12817 | 0.1236 | -0.013733 | -121.5363 | 0.15564 | 0.14649 | 0.16022 | -121.6003 | 0.050354 | 0 | -121.5683 | 0.15564 | 0.027466 | 0.027466 | -121.6187 | 0.2243 | 0.16022 | 0.1236 | -121.7743 | 0.19226 | 0.14191 | 0.14649 | -121.7606
5265.1719 | 121.7285 | -0.56763 | 121.0464 | -0.18799 | 0.046555 | 0.060327 | 0.0057507 | 0.028474 | -0.0087992 | 0.030006 | -0.12329 | 0.017224 | 0.028764 | 0.92018 | 0.0010317 | 0.89958 | -0.004578 | 0.073242 | 0.045776 | -0.009155 | -0.013733 | -0.036621 | -0.19226 | -0.073242 | -0.009155 | -0.13733 | -0.16022 | -0.17395 | -0.40741 | -0.47607 | 0.53101 | 0.37537 | -121.0602 | 0.64087 | 0.55847 | 0.18311 | -121.051 | 0.16022 | 0.091553 | -121.2067 | 0.49438 | 0.4303 | 0.33874 | -121.2204 | 0.55389 | 0.56305 | 0.6134 | -121.2387 | 0.40741 | 0.39368 | 0.55847 | -121.5225
5266.9219 | 121.7331 | -0.18768 | 121.5042 | -0.081177 | 0.054459 | 0.058832 | 0.0055371 | 0.028047 | -0.00025418 | 0.030006 | -0.10803 | 0.016584 | 0.035173 | 0.27611 | 0.0053043 | 0.2491 | 0.045776 | 0.032043 | 0.004578 | 0.018311 | 0.10071 | -0.009155 | -0.15106 | 0.054932 | 0.050354 | -0.022888 | 0.022888 | -0.004578 | -0.13275 | -0.20142 | 0.17853 | 0.036621 | -121.4035 | 0.21973 | 0.20599 | 0.16937 | -121.4584 | 0.054932 | -0.013733 | -121.4813 | 0.24261 | 0.16479 | 0.17853 | -121.5088 | 0.28839 | 0.23346 | 0.19226 | -121.6553 | 0.21057 | 0.1831 | 0.23804 | -121.7056
5268.625 | 121.3028 | -0.10529 | 121.2067 | -0.11932 | 0.051255 | 0.057336 | 0.0025465 | 0.028688 | -0.0021768 | 0.030006 | -0.13092 | 0.014661 | 0.034746 | 0.087267 | 0.0018863 | 0.066452 | 0.050354 | 0.041199 | 0 | 0.032043 | 0.10071 | -0.013733 | -0.14191 | 0.073242 | 0.086975 | -0.059509 | 0.054932 | 0.045776 | -0.073242 | -0.12817 | 0.091553 | -0.036621 | -121.106 | 0.14649 | 0.13733 | 0.17395 | -121.1563 | 0.032044 | -0.022888 | -121.1517 | 0.17853 | 0.045777 | 0.068665 | -121.1609 | 0.20599 | 0.15564 | 0.10529 | -121.3486 | 0.16022 | 0.15106 | 0.19226 | -121.3348
5270.375 | 121.4859 | -0.068665 | 121.2936 | 0.16296 | 0.046555 | 0.061823 | 0.0014783 | 0.027833 | -0.0079446 | 0.031074 | 0.17426 | 0.013379 | 0.030901 | 0.060778 | 0.0020999 | 0.041244 | 0.07782 | 0.1236 | 0.10529 | 0.073242 | 0.064087 | 0.050354 | -0.11444 | 0.13733 | 0.13275 | 0.041199 | 0.027466 | 0.009155 | -0.027466 | -0.086975 | 0.11902 | -0.045776 | -121.2296 | 0.19226 | 0.14191 | 0.18768 | -121.2158 | 0.041199 | -0.01831 | -121.2662 | 0.20599 | 0.10986 | 0.12817 | -121.2845 | 0.13275 | 0.14649 | 0.17395 | -121.4081 | 0.096131 | 0.07782 | 0.20142 | -121.3806
5272.1562 | 121.582 | -0.054932 | 121.3669 | 0.10956 | 0.048264 | 0.056909 | 0.0025465 | 0.029328 | -0.0038858 | 0.029151 | 0.36499 | 0.014447 | 0.034532 | 0.064623 | 0.0020999 | 0.047012 | 0.054932 | 0.054932 | 0.041199 | 0.045776 | 0.073242 | 0.022888 | -0.1236 | 0.12817 | 0.10529 | 0.013733 | 0.013733 | 0.013733 | -0.022888 | -0.082397 | 0.07782 | -0.068664 | -121.2936 | 0.10986 | 0.10071 | 0.16937 | -121.312 | 0.032044 | -0.027465 | -121.3531 | 0.18311 | 0.068665 | 0.09613 | -121.3531 | 0.12817 | 0.10986 | 0.096131 | -121.4905 | 0.068665 | 0.068665 | 0.16022 | -121.4493
5273.8594 | 121.5317 | -0.082397 | 121.4584 | -0.17273 | 0.049332 | 0.062036 | 0.0038281 | 0.02591 | -0.0034586 | 0.029151 | -0.18433 | 0.017011 | 0.033037 | 0.059923 | 0.00081811 | 0.036758 | 0.009155 | -0.004578 | -0.018311 | 0.009155 | 0.11444 | 0 | -0.13733 | 0.054932 | 0.064087 | -0.059509 | 0.064087 | 0.050354 | -0.073242 | -0.10986 | 0.082397 | -0.054932 | -121.344 | 0.077819 | 0.091552 | 0.14648 | -121.4493 | 0.009155 | -0.027466 | -121.3943 | 0.13733 | 0.022888 | 0.050354 | -121.4081 | 0.19684 | 0.091552 | 0.064086 | -121.5958 | 0.14648 | 0.13275 | 0.14648 | -121.5683
5275.625 | 120.9915 | -0.068665 | 120.7993 | 0.08667 | 0.04506 | 0.059686 | 0.0012647 | 0.027406 | -0.0092264 | 0.028297 | 0.16663 | 0.014875 | 0.031328 | 0.085558 | 0.0029543 | 0.067093 | 0.059509 | 0.11902 | 0.09613 | 0.045776 | 0.068665 | 0.045776 | -0.10986 | 0.10986 | 0.10071 | 0.013733 | 0.004578 | 0.013733 | -0.050354 | -0.11444 | 0.11444 | -0.041198 | -120.7306 | 0.18768 | 0.11444 | 0.15564 | -120.7397 | 0.018311 | -0.045776 | -120.7947 | 0.17853 | 0.082398 | 0.12817 | -120.7855 | 0.13733 | 0.12817 | 0.16479 | -120.9091 | 0.073243 | 0.082398 | 0.16937 | -120.9137
5277.3906 | 121.1334 | -0.15564 | 120.9229 | 0.048523 | 0.049546 | 0.057977 | -0.00044435 | 0.03061 | 0.00060022 | 0.028724 | 0.014038 | 0.016156 | 0.033037 | 0.17613 | 0.0029543 | 0.1534 | -0.027466 | -0.064087 | -0.073242 | -0.032043 | 0.10529 | -0.009155 | -0.16479 | -0.004578 | -0.045776 | -0.14191 | 0.036621 | 0.009155 | -0.1236 | -0.16479 | 0.14649 | -0.009155 | -120.8176 | 0.091553 | 0.1236 | 0.13275 | -120.9503 | 0.032044 | -0.009155 | -120.8862 | 0.15106 | 0.013733 | 0.022888 | -120.9137 | 0.26093 | 0.12817 | 0.082398 | -121.0876 | 0.19226 | 0.16479 | 0.10986 | -121.0876
5279.0938 | 121.1975 | -0.2655 | 120.8359 | 0.071411 | 0.050186 | 0.058832 | 0.0014783 | 0.025483 | -0.0011088 | 0.030646 | 0.067444 | 0.019361 | 0.030473 | 0.40108 | 0.0050907 | 0.38112 | -0.041199 | -0.054932 | -0.073242 | -0.045776 | 0.07782 | -0.018311 | -0.16937 | -0.013733 | -0.086975 | -0.18768 | -0.009155 | -0.009155 | -0.20142 | -0.27466 | 0.24719 | 0.09613 | -120.7581 | 0.21057 | 0.21973 | 0.1236 | -120.8771 | 0.064087 | -0.009155 | -120.845 | 0.25177 | 0.07782 | 0.086975 | -120.845 | 0.34332 | 0.2243 | 0.19226 | -121.0052 | 0.25635 | 0.25635 | 0.17853 | -121.1105
5280.7812 | 121.2387 | -0.36163 | 120.7535 | 0.010376 | 0.044205 | 0.06225 | 0.0029737 | 0.026551 | -0.0087992 | 0.027228 | 0.082703 | 0.017438 | 0.028123 | 0.54079 | 0.0029543 | 0.52019 | -0.009155 | 0.004578 | 0.004578 | -0.013733 | 0.018311 | 0.013733 | -0.14648 | -0.027466 | -0.013733 | -0.10071 | -0.068665 | -0.082397 | -0.25177 | -0.30212 | 0.37537 | 0.21515 | -120.7352 | 0.36621 | 0.3479 | 0.13275 | -120.7626 | 0.10986 | 0.059509 | -120.8221 | 0.33417 | 0.26092 | 0.20142 | -120.8359 | 0.37994 | 0.35248 | 0.36621 | -120.9 | 0.29297 | 0.27924 | 0.3479 | -121.0556
5282.5469 | 121.1792 | -0.37537 | 120.7901 | -0.14221 | 0.047623 | 0.057336 | 0.0025465 | 0.029542 | -0.0011088 | 0.027656 | -0.14618 | 0.018506 | 0.030901 | 0.52349 | 0.0053043 | 0.50075 | 0.018311 | -0.027466 | -0.032043 | -0.022888 | 0.054932 | -0.041199 | -0.19226 | -0.050354 | -0.045776 | -0.16937 | -0.022888 | -0.054932 | -0.26093 | -0.33875 | 0.33417 | 0.1831 | -120.7352 | 0.3479 | 0.35248 | 0.16937 | -120.7718 | 0.11444 | 0.036621 | -120.813 | 0.32501 | 0.20599 | 0.16937 | -120.845 | 0.4303 | 0.39368 | 0.34332 | -120.9824 | 0.35248 | 0.32043 | 0.32959 | -121.1288
5284.3125 | 117.7002 | -0.17853 | 117.4805 | -0.14221 | 0.050186 | 0.058618 | 0.00019645 | 0.027192 | -0.00068138 | 0.030646 | -0.16907 | 0.015729 | 0.034532 | 0.29448 | 0.0057315 | 0.27687 | 0.022888 | 0.009155 | -0.018311 | 0.013733 | 0.09613 | 0 | -0.16022 | 0.022888 | 0.027466 | -0.10071 | 0.009155 | 0.004578 | -0.16937 | -0.21973 | 0.17853 | 0.018311 | -117.3843 | 0.18768 | 0.19226 | 0.17395 | -117.4576 | 0.009155 | -0.041199 | -117.4713 | 0.20142 | 0.07782 | 0.11902 | -117.4759 | 0.27466 | 0.20142 | 0.16022 | -117.6407 | 0.18768 | 0.18311 | 0.20599 | -117.7002
5286.0781 | 120.9686 | -0.10529 | 120.7718 | 0.13245 | 0.046341 | 0.059473 | 0.00019645 | 0.02826 | -0.006663 | 0.029578 | 0.159 | 0.014661 | 0.030901 | 0.13854 | 0.0027407 | 0.12712 | 0.064087 | 0.10529 | 0.086975 | 0.064087 | 0.068665 | 0.041199 | -0.10986 | 0.11902 | 0.10071 | 0.022888 | 0.009155 | -0.013733 | -0.07782 | -0.11902 | 0.14649 | -0.004577 | -120.7031 | 0.21057 | 0.16937 | 0.17395 | -120.7077 | 0.027466 | -0.013733 | -120.7626 | 0.22431 | 0.12817 | 0.14191 | -120.7855 | 0.17395 | 0.16937 | 0.19226 | -120.8817 | 0.11444 | 0.091553 | 0.20599 | -120.8908
5287.7812 | 121.2158 | -0.31128 | 120.5795 | 0.23163 | 0.046768 | 0.060754 | 0.0016919 | 0.03061 | -0.0051676 | 0.029792 | 0.0064086 | 0.015302 | 0.029192 | 0.5566 | 0.0050907 | 0.53172 | 0.050354 | 0.064087 | 0.073242 | 0.018311 | 0.009155 | 0.022888 | -0.12817 | 0.027466 | 0.013733 | -0.059509 | -0.082397 | -0.10529 | -0.26093 | -0.29755 | 0.33417 | 0.1831 | -120.5704 | 0.37537 | 0.32959 | 0.14649 | -120.5292 | 0.050354 | 0.013733 | -120.6619 | 0.33874 | 0.25177 | 0.23804 | -120.6848 | 0.32043 | 0.36163 | 0.38452 | -120.7077 | 0.22888 | 0.20599 | 0.32501 | -120.8771
5289.5312 | 121.1746 | -0.20599 | 120.7489 | 0.14008 | 0.047409 | 0.059259 | 0.0023329 | 0.028474 | -0.0030314 | 0.029792 | 0.021668 | 0.017865 | 0.031541 | 0.32546 | 0.0053043 | 0.30336 | 0.045776 | 0.059509 | 0.041199 | 0.032043 | 0.059509 | 0.022888 | -0.13275 | 0.073242 | 0.045776 | -0.045776 | -0.036621 | -0.059509 | -0.13733 | -0.21515 | 0.22888 | 0.073243 | -120.6894 | 0.2655 | 0.23804 | 0.16479 | -120.7031 | 0.068665 | -0.009155 | -120.7855 | 0.27924 | 0.16022 | 0.16937 | -120.8084 | 0.2655 | 0.25177 | 0.24719 | -120.8817 | 0.16937 | 0.14649 | 0.25177 | -120.9641
5291.2812 | 121.1014 | -0.21057 | 120.8359 | -0.21088 | 0.048477 | 0.058832 | 0.0081007 | 0.025697 | -0.007731 | 0.02851 | -0.13092 | 0.015515 | 0.033678 | 0.25582 | 0.00039091 | 0.23457 | 0.068665 | 0.11444 | 0.09613 | 0.064087 | 0.045776 | 0.022888 | -0.13733 | 0.082397 | 0.1236 | -0.013733 | -0.009155 | -0.027466 | -0.1236 | -0.17853 | 0.23346 | 0.073242 | -120.7901 | 0.32501 | 0.27466 | 0.20142 | -120.7672 | 0.086975 | 0.032043 | -120.845 | 0.29297 | 0.19684 | 0.16479 | -120.8633 | 0.25635 | 0.27924 | 0.3067 | -120.9732 | 0.20142 | 0.18311 | 0.33417 | -121.0144
5292.9844 | 121.1517 | -0.20142 | 120.9 | -0.20325 | 0.047623 | 0.061182 | 0.0053235 | 0.027833 | -0.0079446 | 0.028724 | -0.13855 | 0.012952 | 0.034959 | 0.25987 | -0.0013181 | 0.24162 | 0.073242 | 0.1236 | 0.086975 | 0.054932 | 0.041199 | 0.022888 | -0.13275 | 0.086975 | 0.11902 | -0.009155 | -0.022888 | -0.022888 | -0.10529 | -0.17395 | 0.2243 | 0.068665 | -120.8588 | 0.32501 | 0.25635 | 0.18768 | -120.8267 | 0.09613 | 0.027466 | -120.9229 | 0.28839 | 0.19226 | 0.16479 | -120.9229 | 0.24262 | 0.27466 | 0.28839 | -121.0327 | 0.17853 | 0.17853 | 0.32044 | -121.0739
5294.7344 | 121.2387 | -0.1831 | 120.8771 | -0.21088 | 0.047623 | 0.056055 | 0.0059643 | 0.028047 | -0.007731 | 0.028083 | -0.1004 | 0.015729 | 0.03261 | 0.28188 | -0.0013181 | 0.25786 | 0.086975 | 0.11902 | 0.09613 | 0.045776 | 0.064087 | 0.009155 | -0.12817 | 0.10986 | 0.13275 | 0.013733 | -0.018311 | -0.041199 | -0.1236 | -0.17853 | 0.19226 | 0.054931 | -120.813 | 0.30212 | 0.22888 | 0.17395 | -120.7901 | 0.059509 | 0.004577 | -120.8954 | 0.29297 | 0.19684 | 0.19226 | -120.9183 | 0.24719 | 0.27008 | 0.27924 | -121.0052 | 0.16479 | 0.14191 | 0.31586 | -121.0556
5296.5 | 121.1472 | -0.21057 | 120.9412 | -0.11169 | 0.048477 | 0.056909 | -0.0025805 | 0.029969 | 0.00081382 | 0.027869 | -0.10803 | 0.017224 | 0.030687 | 0.26991 | 0.0078677 | 0.23778 | 0.054932 | 0.004578 | -0.032043 | -0.009155 | 0.09613 | -0.013733 | -0.16022 | -0.027466 | -0.050354 | -0.14648 | 0.013733 | 0.022888 | -0.15564 | -0.21973 | 0.19684 | 0.050354 | -120.845 | 0.21515 | 0.20142 | 0.15106 | -120.8862 | 0.054931 | -0.009156 | -120.9274 | 0.18311 | 0.064087 | 0.073243 | -120.9183 | 0.3067 | 0.2655 | 0.17853 | -121.1014 | 0.2243 | 0.23346 | 0.16022 | -121.1609
5298.2188 | 121.1426 | -0.42114 | 120.7077 | 0.033264 | 0.051468 | 0.061395 | -0.0017261 | 0.029328 | 0.0016684 | 0.031287 | 0.014038 | 0.020001 | 0.029192 | 0.60958 | 0.0067997 | 0.58363 | -0.054932 | -0.10986 | -0.10529 | -0.082397 | 0.068665 | -0.036621 | -0.18768 | -0.07782 | -0.13733 | -0.23346 | -0.041199 | -0.059509 | -0.31128 | -0.35248 | 0.38452 | 0.23346 | -120.639 | 0.31128 | 0.33875 | 0.10529 | -120.7626 | 0.10986 | 0.068665 | -120.7489 | 0.34332 | 0.18768 | 0.11902 | -120.7672 | 0.48981 | 0.36621 | 0.31586 | -120.8954 | 0.37994 | 0.36163 | 0.28381 | -121.0602
5299.9844 | 121.1975 | -0.48981 | 120.5246 | 0.056152 | 0.047409 | 0.061182 | 0.00062385 | 0.02826 | -0.00089518 | 0.029365 | 0.097962 | 0.022138 | 0.029405 | 0.80675 | 0.0072269 | 0.78017 | -0.036621 | -0.091553 | -0.09613 | -0.064087 | 0.036621 | -0.073242 | -0.21515 | -0.082397 | -0.13733 | -0.2243 | -0.10071 | -0.11444 | -0.36621 | -0.41657 | 0.41656 | 0.27466 | -120.488 | 0.39825 | 0.42572 | 0.15106 | -120.5612 | 0.1236 | 0.073242 | -120.6253 | 0.40741 | 0.2655 | 0.19226 | -120.639 | 0.52643 | 0.45319 | 0.39368 | -120.7397 | 0.3891 | 0.37537 | 0.35248 | -120.9412
5301.75 | 121.0968 | -0.46234 | 120.6299 | -0.19562 | 0.04805 | 0.058191 | 0.0042555 | 0.02826 | -0.008372 | 0.029792 | -0.10803 | 0.018933 | 0.029619 | 0.66277 | 0.0042361 | 0.64174 | 0.032043 | 0.068665 | 0.050354 | 0.018311 | 0.022888 | -0.022888 | -0.16937 | -0.018311 | 0.036621 | -0.10071 | -0.09613 | -0.10529 | -0.28381 | -0.3479 | 0.43945 | 0.29297 | -120.607 | 0.53101 | 0.48065 | 0.18768 | -120.5978 | 0.17853 | 0.11444 | -120.726 | 0.44403 | 0.36163 | 0.24719 | -120.7352 | 0.48523 | 0.49438 | 0.5127 | -120.7993 | 0.36621 | 0.35706 | 0.49896 | -120.9778
5303.4531 | 121.1472 | -0.59967 | 120.3598 | 0.08667 | 0.049332 | 0.058405 | 0.00019645 | 0.026765 | -0.00025418 | 0.030006 | 0.097962 | 0.020856 | 0.028337 | 1.0246 | 0.011286 | 1.0043 | -0.059509 | -0.091553 | -0.082397 | -0.086975 | 0.013733 | -0.064087 | -0.2243 | -0.11902 | -0.16479 | -0.24261 | -0.16022 | -0.16937 | -0.4715 | -0.51727 | 0.53558 | 0.37537 | -120.3461 | 0.50812 | 0.5127 | 0.13733 | -120.4193 | 0.12817 | 0.082397 | -120.52 | 0.48065 | 0.35706 | 0.27466 | -120.5292 | 0.6134 | 0.54016 | 0.51727 | -120.5841 | 0.43945 | 0.4303 | 0.43488 | -120.8771
5305.2188 | 120.9457 | -1.1581 | 119.6732 | 0.056152 | 0.044632 | 0.059473 | 0.0048963 | 0.027406 | -0.0075174 | 0.028083 | 0.090332 | 0.019788 | 0.021074 | 1.927 | 0.0093631 | 1.9013 | -0.12817 | -0.10071 | -0.091553 | -0.1236 | -0.10529 | -0.13733 | -0.2655 | -0.28839 | -0.3067 | -0.40741 | -0.3479 | -0.35248 | -0.8606 | -0.92468 | 1.0208 | 0.89264 | -119.7784 | 1.0574 | 1.0345 | 0.14191 | -119.8013 | 0.29755 | 0.23346 | -120.0211 | 0.86975 | 0.75073 | 0.51727 | -120.0256 | 1.0529 | 1.03 | 1.0666 | -119.9387 | 0.81024 | 0.80566 | 0.85144 | -120.5978
5306.9375 | 120.7901 | -120.0302 | 0.36163 | 0.12482 | 0.046555 | 0.05755 | 0.0021191 | 0.026551 | -0.0021768 | 0.029151 | 0.11322 | 0.014234 | 0.025133 | 0.034716 | 0.0050907 | 0.015823 | 0.09613 | 0.086975 | 0.073242 | 0.059509 | 0.086975 | 0.050354 | -0.10529 | 0.15106 | 0.13733 | 0.018311 | 0.009155 | 0.018311 | -0.032043 | -0.064087 | 120.0806 | 119.9249 | -0.27466 | 120.1172 | 120.0897 | 0.16479 | -0.2655 | 119.9982 | 119.9661 | -0.35248 | 120.1813 | 120.0485 | 0.082398 | -0.34332 | 120.1172 | 120.1263 | 120.1035 | -0.46692 | 120.0394 | 120.0485 | 120.1675 | -0.42572
5308.7031 | 120.8908 | -120.3094 | 0.40741 | 0.033264 | 0.047196 | 0.058618 | 0.0036145 | 0.032746 | -4.058e-05 | 0.029365 | 0.090332 | 0.016584 | 0.025133 | 0.038347 | 0.0046633 | 0.016464 | 0.004578 | -0.050354 | -0.041199 | -0.013733 | 0.10986 | 0.004578 | -0.11902 | 0.045776 | 0 | -0.10529 | 0.07782 | 0.050354 | -0.045776 | -0.10071 | 120.314 | 120.1904 | -0.29755 | 120.2591 | 120.2957 | 0.10529 | -0.40283 | 120.2637 | 120.2087 | -0.32959 | 120.3552 | 120.2042 | -0.004578 | -0.35706 | 120.4193 | 120.314 | 120.2682 | -0.52643 | 120.3873 | 120.3598 | 120.3094 | -0.50812
5310.4688 | 120.8038 | -120.1492 | 0.4303 | 0.14771 | 0.048264 | 0.059473 | 0.0042555 | 0.028688 | -0.002604 | 0.030219 | 0.12848 | 0.015302 | 0.025346 | 0.037493 | 0.00081811 | 0.017318 | 0.091553 | 0.064087 | 0.07782 | 0.068665 | 0.073242 | 0.036621 | -0.091553 | 0.14191 | 0.12817 | 0.032043 | 0.036621 | 0.027466 | -0.013733 | -0.073242 | 120.1859 | 120.0577 | -0.35706 | 120.2133 | 120.2179 | 0.16022 | -0.33875 | 120.1355 | 120.076 | -0.39368 | 120.2911 | 120.1813 | 0.10529 | -0.40283 | 120.2225 | 120.2408 | 120.2271 | -0.52185 | 120.1859 | 120.1767 | 120.2774 | -0.50354
5312.2344 | 120.9503 | -120.2499 | 0.4715 | -0.020142 | 0.049118 | 0.059473 | 0.0063917 | 0.02527 | -0.008372 | 0.030219 | 0.097962 | 0.011457 | 0.024705 | 0.034289 | -0.00067729 | 0.020523 | 0.041199 | 0.050354 | 0.045776 | 0.036621 | 0.082397 | 0.036621 | -0.09613 | 0.091553 | 0.091553 | 0.009155 | 0.054932 | 0.045776 | -0.032043 | -0.09613 | 120.2866 | 120.1538 | -0.3891 | 120.3003 | 120.2866 | 0.13275 | -0.4303 | 120.2179 | 120.1538 | -0.41657 | 120.3415 | 120.2591 | 0.10528 | -0.42572 | 120.3323 | 120.2911 | 120.2957 | -0.56763 | 120.3049 | 120.2957 | 120.3415 | -0.56763
5313.9375 | 121.0007 | -120.2591 | 0.50354 | 0.12482 | 0.048264 | 0.057336 | 0.0012647 | 0.025483 | -0.001536 | 0.028937 | 0.18951 | 0.013593 | 0.023851 | 0.034075 | 0.0044497 | 0.018173 | 0.10986 | 0.10529 | 0.10071 | 0.082397 | 0.059509 | 0.068665 | -0.086975 | 0.16479 | 0.14191 | 0.032043 | 0.018311 | 0.027466 | -0.013733 | -0.054932 | 120.3278 | 120.1721 | -0.44403 | 120.3644 | 120.3415 | 0.16937 | -0.39368 | 120.2454 | 120.2042 | -0.48523 | 120.4239 | 120.2911 | 0.086975 | -0.47607 | 120.3186 | 120.369 | 120.3598 | -0.59052 | 120.2774 | 120.2866 | 120.401 | -0.55847
5315.6875 | 121.1105 | -120.3094 | 0.50812 | 0.13245 | 0.04805 | 0.058618 | 0.0012647 | 0.028688 | -0.002604 | 0.027656 | 0.097962 | 0.01402 | 0.022142 | 0.03557 | 0.0042361 | 0.015182 | 0.091553 | 0.068665 | 0.050354 | 0.064087 | 0.082397 | 0.045776 | -0.11902 | 0.14191 | 0.10986 | 0.018311 | 0.018311 | 0.027466 | -0.018311 | -0.07782 | 120.3552 | 120.1904 | -0.42572 | 120.3781 | 120.3735 | 0.18311 | -0.41656 | 120.2911 | 120.2316 | -0.48981 | 120.4514 | 120.3278 | 0.096131 | -0.48065 | 120.3918 | 120.401 | 120.3598 | -0.62714 | 120.3278 | 120.3369 | 120.4193 | -0.58594
5317.4375 | 121.1105 | -120.3461 | 0.49439 | 0.14008 | 0.045914 | 0.055414 | 0.00041005 | 0.027192 | -0.0045266 | 0.030006 | 0.25055 | 0.012952 | 0.023424 | 0.036211 | 0.0016727 | 0.017105 | 0.11444 | 0.11444 | 0.11444 | 0.082397 | 0.073242 | 0.045776 | -0.082397 | 0.14648 | 0.15106 | 0.027466 | 0.032043 | 0.009155 | -0.018311 | -0.059509 | 120.3918 | 120.2637 | -0.42114 | 120.4605 | 120.4285 | 0.16479 | -0.37994 | 120.3278 | 120.2866 | -0.46234 | 120.4926 | 120.3735 | 0.086975 | -0.48523 | 120.4193 | 120.4605 | 120.4605 | -0.57678 | 120.3781 | 120.3552 | 120.4971 | -0.55389
5319.1562 | 121.0876 | -120.3827 | 0.52643 | -0.18799 | 0.046982 | 0.06225 | 0.0072461 | 0.027192 | -0.008372 | 0.02851 | -0.077515 | 0.010816 | 0.025133 | 0.034502 | -0.00067729 | 0.017746 | 0.10529 | 0.14648 | 0.12817 | 0.07782 | 0.068665 | 0.032043 | -0.09613 | 0.17395 | 0.16937 | 0.07782 | 0.041199 | 0.013733 | -0.022888 | -0.064087 | 120.4147 | 120.2866 | -0.45776 | 120.5292 | 120.4605 | 0.17395 | -0.42114 | 120.3598 | 120.3186 | -0.48523 | 120.5566 | 120.4605 | 0.14191 | -0.5127 | 120.4514 | 120.488 | 120.5109 | -0.62256 | 120.4239 | 120.3964 | 120.5521 | -0.59052
5320.8594 | 120.6253 | -3.2364 | 117.3248 | 0.10193 | 0.04506 | 0.059259 | -0.00065795 | 0.02826 | -0.0036722 | 0.027869 | 0.082703 | 0.012525 | 0.022142 | 0.033648 | 0.0050907 | 0.017959 | 0.091553 | 0.1236 | 0.091553 | 0.050354 | 0.059509 | 0.041199 | -0.11444 | 0.15106 | 0.11444 | 0.018311 | 0.045776 | 0.027466 | -0.032043 | -0.064087 | 3.2776 | 3.1219 | -117.2653 | 3.36 | 3.2867 | 0.16479 | -117.2333 | 3.2043 | 3.1723 | -117.2791 | 3.3875 | 3.2547 | 0.082398 | -117.2974 | 3.2959 | 3.3279 | 3.3279 | -117.4393 | 3.2822 | 3.2639 | 3.3508 | -117.3889
5322.625 | 120.7352 | -104.9927 | 15.2435 | -0.11932 | 0.043564 | 0.061182 | 0.0034009 | 0.026551 | -0.0070902 | 0.02616 | -0.10803 | 0.011884 | 0.022356 | 0.035143 | 0.00017731 | 0.017318 | 0.086975 | 0.13733 | 0.10071 | 0.068665 | 0.09613 | 0.032043 | -0.09613 | 0.16479 | 0.16937 | 0.073242 | 0.045776 | 0.018311 | -0.009155 | -0.07782 | 105.0247 | 104.8965 | -15.1474 | 105.13 | 105.0613 | 0.16479 | -15.1566 | 104.9835 | 104.9149 | -15.1978 | 105.1575 | 105.0659 | 0.15106 | -15.2252 | 105.0888 | 105.0797 | 105.0934 | -15.3397 | 105.0385 | 105.011 | 105.162 | -15.3213
5324.3906 | 120.9045 | -105.2948 | 15.1932 | 0.048523 | 0.042923 | 0.062463 | -0.00023075 | 0.027833 | -0.0053812 | 0.029151 | 0.075073 | 0.011243 | 0.022142 | 0.034929 | 0.0050907 | 0.019027 | 0.068665 | 0.086975 | 0.068665 | 0.036621 | 0.073242 | 0.045776 | -0.091553 | 0.1236 | 0.09613 | 0 | 0.045776 | 0.018311 | -0.032043 | -0.07782 | 105.3406 | 105.2032 | -15.1199 | 105.3818 | 105.3314 | 0.12817 | -15.1245 | 105.2628 | 105.217 | -15.1474 | 105.4184 | 105.2948 | 0.07782 | -15.1749 | 105.368 | 105.3635 | 105.3635 | -15.2847 | 105.3406 | 105.3131 | 105.3909 | -15.271
5326.1562 | 116.4551 | -80.4382 | 35.1379 | -0.17273 | 0.047623 | 0.060327 | 0.0085279 | 0.029756 | -0.0045266 | 0.028937 | -0.19196 | 0.014234 | 0.023424 | 0.034929 | -0.00046349 | 0.015823 | 0.1236 | 0.13733 | 0.11902 | 0.091553 | 0.073242 | 0.032043 | -0.10529 | 0.15106 | 0.18768 | 0.045776 | 0.032043 | 0.018311 | -0.022888 | -0.050354 | 80.4703 | 80.3329 | -35.0647 | 80.5756 | 80.5298 | 0.19684 | -35.0143 | 80.4153 | 80.3879 | -35.1059 | 80.5893 | 80.484 | 0.09613 | -35.1196 | 80.5115 | 80.5618 | 80.5573 | -35.2432 | 80.4703 | 80.4565 | 80.6259 | -35.1883
5327.8594 | 120.726 | -105.2124 | 15.0101 | -0.17273 | 0.047623 | 0.061182 | 0.0027601 | 0.027619 | -0.006022 | 0.02616 | -0.10803 | 0.011243 | 0.023851 | 0.035784 | -0.00046349 | 0.016037 | 0.10529 | 0.12817 | 0.1236 | 0.073242 | 0.068665 | 0.027466 | -0.1236 | 0.17853 | 0.16479 | 0.082397 | 0.045776 | 0.022888 | -0.013733 | -0.064087 | 105.2399 | 105.0888 | -14.9414 | 105.3406 | 105.2856 | 0.19684 | -14.9048 | 105.1987 | 105.1483 | -14.9643 | 105.3909 | 105.2948 | 0.14648 | -14.9872 | 105.2811 | 105.3177 | 105.336 | -15.1337 | 105.2582 | 105.2353 | 105.3772 | -15.0742
5329.6094 | 120.7489 | -105.3772 | 15.1245 | -0.18036 | 0.047837 | 0.060327 | 0.0031873 | 0.026124 | -0.003245 | 0.027869 | -0.18433 | 0.013593 | 0.026201 | 0.036852 | 0.00039091 | 0.015396 | 0.10986 | 0.11444 | 0.10071 | 0.082397 | 0.09613 | 0.041199 | -0.13733 | 0.12817 | 0.17395 | 0.022888 | 0.054932 | 0.018311 | -0.018311 | -0.07782 | 105.4184 | 105.2399 | -15.0284 | 105.4916 | 105.4596 | 0.21973 | -15.0146 | 105.3589 | 105.2994 | -15.0696 | 105.5054 | 105.4001 | 0.10071 | -15.1062 | 105.4733 | 105.4871 | 105.4779 | -15.2618 | 105.4321 | 105.3955 | 105.5511 | -15.2023
5331.3125 | 120.8359 | -105.9631 | 14.6622 | -0.088806 | 0.050186 | 0.060541 | -0.00065795 | 0.031037 | 0.0029502 | 0.028937 | -0.19196 | 0.013379 | 0.02086 | 0.036638 | 0.0057315 | 0.014114 | 0.10071 | 0.086975 | 0.022888 | 0.050354 | 0.10071 | 0.009155 | -0.1236 | 0.10071 | 0.082397 | -0.050354 | 0.091553 | 0.041199 | -0.036621 | -0.10071 | 105.9723 | 105.8395 | -14.5615 | 106.0501 | 106.0135 | 0.17395 | -14.5615 | 105.9265 | 105.8624 | -14.5706 | 106.0638 | 105.9128 | 0.050354 | -14.621 | 106.0638 | 106.0638 | 105.986 | -14.7858 | 106.0547 | 106.0043 | 106.0455 | -14.7629
5333.0938 | 120.9091 | -105.661 | 15.0146 | -0.11932 | 0.050186 | 0.058405 | 0.0036145 | 0.026979 | 0.0016684 | 0.031501 | -0.1767 | 0.014661 | 0.025133 | 0.03792 | 0.0044497 | 0.016464 | 0.068665 | 0.064087 | 0.027466 | 0.032043 | 0.10071 | 0.013733 | -0.15564 | 0.09613 | 0.086975 | -0.045776 | 0.068665 | 0.050354 | -0.059509 | -0.09613 | 105.6747 | 105.5054 | -14.9139 | 105.7251 | 105.6931 | 0.18768 | -14.946 | 105.6015 | 105.5649 | -14.946 | 105.7571 | 105.6152 | 0.050354 | -14.9643 | 105.7617 | 105.7297 | 105.6885 | -15.1703 | 105.7297 | 105.7114 | 105.748 | -15.1108
5334.7969 | 120.9961 | -105.1209 | 15.6006 | -0.1651 | 0.048691 | 0.061609 | 0.0048963 | 0.028688 | -0.010081 | 0.029365 | -0.16144 | 0.011457 | 0.02321 | 0.03557 | 0.0012455 | 0.019455 | 0.091553 | 0.17853 | 0.13275 | 0.082397 | 0.07782 | 0.050354 | -0.10986 | 0.14191 | 0.18768 | 0.064087 | 0.018311 | 0.032043 | -0.009155 | -0.07782 | 105.1712 | 105.011 | -15.5228 | 105.2994 | 105.2032 | 0.19226 | -15.509 | 105.1117 | 105.043 | -15.5823 | 105.2628 | 105.1849 | 0.14191 | -15.5685 | 105.1987 | 105.2124 | 105.2536 | -15.7104 | 105.1392 | 105.1529 | 105.3085 | -15.6784
5336.5469 | 120.5658 | -105.5054 | 14.6805 | -0.18799 | 0.049118 | 0.056696 | 0.0074597 | 0.027833 | -0.0055948 | 0.028724 | -0.14618 | 0.014875 | 0.024919 | 0.034716 | 0.00060451 | 0.015396 | 0.10529 | 0.14191 | 0.10529 | 0.082397 | 0.073242 | 0.032043 | -0.10071 | 0.12817 | 0.16022 | 0.045776 | 0.032043 | 0.027466 | -0.022888 | -0.068665 | 105.5374 | 105.4047 | -14.6072 | 105.6473 | 105.5878 | 0.18311 | -14.5752 | 105.4825 | 105.4367 | -14.6484 | 105.6335 | 105.5511 | 0.11444 | -14.653 | 105.5786 | 105.6107 | 105.6107 | -14.7812 | 105.5374 | 105.5328 | 105.6656 | -14.7491
5338.3125 | 120.9229 | -106.0272 | 14.534 | 0.10956 | 0.048691 | 0.059045 | 0.0023329 | 0.026765 | -0.001536 | 0.030006 | 0.052185 | 0.016156 | 0.024705 | 0.038134 | 0.0038089 | 0.017318 | 0.013733 | -0.027466 | -0.027466 | 0 | 0.11902 | 0.009155 | -0.14191 | 0.054932 | 0.004578 | -0.086975 | 0.07782 | 0.082397 | -0.054932 | -0.11444 | 106.0364 | 105.8853 | -14.415 | 105.9998 | 106.0272 | 0.14191 | -14.5203 | 105.9723 | 105.9128 | -14.4562 | 106.0822 | 105.9402 | 0.027466 | -14.4516 | 106.1462 | 106.041 | 105.9998 | -14.6759 | 106.105 | 106.1096 | 106.0318 | -14.6484
5340.0312 | 120.9457 | -106.2653 | 14.4424 | 0.0027468 | 0.047196 | 0.058191 | 0.0014783 | 0.027833 | 0.0010276 | 0.032996 | -0.0088499 | 0.016797 | 0.024705 | 0.038561 | 0.0057315 | 0.0186 | 0.009155 | -0.018311 | -0.041199 | -0.009155 | 0.10986 | 0.009155 | -0.16479 | 0.022888 | 0 | -0.10986 | 0.082397 | 0.045776 | -0.050354 | -0.11902 | 106.2744 | 106.1005 | -14.3326 | 106.2469 | 106.2561 | 0.15564 | -14.4333 | 106.2149 | 106.1462 | -14.36 | 106.2881 | 106.1554 | 0.009156 | -14.3967 | 106.3751 | 106.2744 | 106.2241 | -14.6072 | 106.3477 | 106.311 | 106.2653 | -14.5615
5341.7969 | 120.9641 | -106.1874 | 14.6027 | 0.0027468 | 0.047623 | 0.059045 | 0.00062385 | 0.03061 | -4.058e-05 | 0.029792 | 0.0064086 | 0.015943 | 0.024065 | 0.038775 | 0.0061587 | 0.017746 | 0.013733 | 0 | -0.036621 | -0.009155 | 0.11444 | 0 | -0.14648 | 0.022888 | 0.004578 | -0.11444 | 0.082397 | 0.064087 | -0.045776 | -0.10529 | 106.1874 | 106.041 | -14.4882 | 106.1874 | 106.1783 | 0.13733 | -14.5889 | 106.1417 | 106.0822 | -14.5203 | 106.2103 | 106.073 | -0.009155 | -14.5386 | 106.3019 | 106.2012 | 106.1508 | -14.7491 | 106.2698 | 106.2515 | 106.192 | -14.7079
5343.5625 | 120.9961 | -106.2241 | 14.6484 | -0.24139 | 0.049973 | 0.060541 | 0.0031873 | 0.028047 | -0.007731 | 0.029578 | -0.12329 | 0.01167 | 0.023851 | 0.033861 | 0.0025271 | 0.020095 | 0.009155 | 0.064087 | 0.022888 | 0.027466 | 0.086975 | 0.009155 | -0.12817 | 0.032043 | 0.054932 | -0.064087 | 0.082397 | 0.059509 | -0.050354 | -0.09613 | 106.2332 | 106.0959 | -14.5615 | 106.2881 | 106.2515 | 0.15564 | -14.6393 | 106.1737 | 106.1279 | -14.566 | 106.2561 | 106.16 | 0.032043 | -14.5889 | 106.311 | 106.2332 | 106.2469 | -14.7766 | 106.3065 | 106.2836 | 106.279 | -14.7446
5345.3281 | 120.3827 | -5.1956 | 115.7547 | 0.025635 | 0.049546 | 0.057977 | -0.00023075 | 0.028474 | -0.0017496 | 0.029792 | -0.024109 | 0.014447 | 0.024492 | 0.03792 | 0.0067997 | 0.0186 | -0.013733 | -0.032043 | -0.054932 | -0.013733 | 0.10071 | 0.013733 | -0.15106 | 0 | -0.004578 | -0.11902 | 0.068665 | 0.054932 | -0.073242 | -0.10529 | 5.2094 | 5.0446 | -115.654 | 5.1636 | 5.1819 | 0.13733 | -115.7684 | 5.1224 | 5.0903 | -115.686 | 5.1956 | 5.0766 | -0.013733 | -115.6998 | 5.2963 | 5.1819 | 5.1407 | -115.9058 | 5.2643 | 5.2505 | 5.191 | -115.86
5347.0312 | 120.4788 | -4.8203 | 116.1438 | -0.13458 | 0.052109 | 0.05755 | 0.0057507 | 0.026551 | -0.0011088 | 0.028297 | -0.16144 | 0.015088 | 0.028764 | 0.036425 | 0.0016727 | 0.0186 | 0.027466 | 0.041199 | 0.004578 | 0.041199 | 0.086975 | 0.009155 | -0.13275 | 0.064087 | 0.086975 | -0.045776 | 0.07782 | 0.050354 | -0.045776 | -0.10071 | 4.8294 | 4.6875 | -116.0568 | 4.8614 | 4.8614 | 0.17395 | -116.1163 | 4.7745 | 4.7195 | -116.066 | 4.8843 | 4.7745 | 0.054932 | -116.0934 | 4.9072 | 4.8477 | 4.8248 | -116.2766 | 4.8981 | 4.8706 | 4.9072 | -116.2445
5348.7969 | 120.9641 | -4.5547 | 116.4825 | -0.19562 | 0.046982 | 0.057977 | 0.0044691 | 0.029328 | -0.0064492 | 0.025947 | -0.20721 | 0.012311 | 0.023424 | 0.036852 | -0.00046349 | 0.017959 | 0.036621 | 0.10986 | 0.07782 | 0.064087 | 0.07782 | 0.027466 | -0.13733 | 0.054932 | 0.13275 | -0.004578 | 0.036621 | 0.054932 | -0.045776 | -0.09613 | 4.5822 | 4.4174 | -116.4047 | 4.6646 | 4.6188 | 0.20142 | -116.4459 | 4.509 | 4.4586 | -116.4459 | 4.6097 | 4.5502 | 0.091552 | -116.4276 | 4.6326 | 4.5914 | 4.6326 | -116.6199 | 4.5914 | 4.6097 | 4.6875 | -116.5787
5350.4844 | 120.3003 | -2.7786 | 118.2083 | -0.081177 | 0.048477 | 0.060754 | 0.00083745 | 0.027406 | -0.00068138 | 0.028724 | -0.092773 | 0.017011 | 0.026628 | 0.034929 | 0.0040225 | 0.015823 | 0.045776 | 0.050354 | 0.004578 | 0.036621 | 0.09613 | 0 | -0.12817 | 0.068665 | 0.054932 | -0.059509 | 0.07782 | 0.045776 | -0.050354 | -0.10071 | 2.7786 | 2.6505 | -118.1122 | 2.829 | 2.8152 | 0.1648 | -118.1625 | 2.7283 | 2.6779 | -118.1305 | 2.8473 | 2.7191 | 0.041199 | -118.1625 | 2.8748 | 2.8244 | 2.7832 | -118.3365 | 2.8564 | 2.8244 | 2.8336 | -118.309
5352.2344 | 121.0098 | -2.7008 | 118.3182 | -0.10406 | 0.050614 | 0.056909 | 0.0025465 | 0.026765 | -0.0038858 | 0.028937 | -0.14618 | 0.016584 | 0.026628 | 0.037279 | 0.0033817 | 0.016464 | 0.045776 | 0.050354 | 0.027466 | 0.027466 | 0.10071 | -0.022888 | -0.1236 | 0.082397 | 0.086975 | -0.045776 | 0.068665 | 0.045776 | -0.045776 | -0.10529 | 2.6779 | 2.5772 | -118.2175 | 2.7512 | 2.7283 | 0.15106 | -118.2724 | 2.655 | 2.5955 | -118.2495 | 2.7832 | 2.655 | 0.05951 | -118.2724 | 2.8015 | 2.7466 | 2.7283 | -118.4418 | 2.7695 | 2.7466 | 2.7878 | -118.4235
5354 | 120.607 | -71.5073 | 47.7448 | 0.13245 | 0.047196 | 0.05755 | 0.0040417 | 0.026765 | -0.0062356 | 0.030006 | 0.19714 | 0.014447 | 0.022569 | 0.036211 | 0.0012455 | 0.021164 | 0.091553 | 0.11902 | 0.10071 | 0.07782 | 0.059509 | 0.045776 | -0.11444 | 0.13275 | 0.13275 | 0.050354 | 0.022888 | 0.036621 | -0.022888 | -0.073242 | 71.553 | 71.3928 | -47.6852 | 71.6263 | 71.5851 | 0.19226 | -47.6532 | 71.4844 | 71.434 | -47.7219 | 71.64 | 71.5576 | 0.1236 | -47.7081 | 71.5668 | 71.5988 | 71.608 | -47.8592 | 71.5302 | 71.5439 | 71.64 | -47.818
5355.7031 | 120.8588 | -7.1228 | 113.5712 | -0.081177 | 0.046128 | 0.056482 | 0.0040417 | 0.026551 | -0.010508 | 0.027015 | -0.016479 | 0.011884 | 0.025133 | 0.034716 | -0.0013181 | 0.0186 | 0.036621 | 0.11902 | 0.09613 | 0.068665 | 0.064087 | 0.041199 | -0.11902 | 0.14648 | 0.15106 | 0.059509 | 0.032043 | 0.022888 | -0.018311 | -0.086975 | 7.164 | 7.0038 | -113.5071 | 7.2418 | 7.1915 | 0.18768 | -113.5345 | 7.1045 | 7.0358 | -113.5391 | 7.2693 | 7.1823 | 0.14648 | -113.5483 | 7.1869 | 7.1594 | 7.2189 | -113.6902 | 7.1548 | 7.1457 | 7.2739 | -113.6581
5357.4688 | 120.8862 | -6.546 | 114.2395 | 0.10193 | 0.046128 | 0.0599 | 0.00062385 | 0.030183 | -0.0053812 | 0.027442 | 0.14374 | 0.012311 | 0.022996 | 0.035143 | 0.0035953 | 0.017959 | 0.07782 | 0.1236 | 0.10529 | 0.064087 | 0.064087 | 0.054932 | -0.10529 | 0.13275 | 0.11902 | 0.045776 | 0.032043 | 0.022888 | -0.027466 | -0.082397 | 6.601 | 6.4407 | -114.1754 | 6.6696 | 6.6101 | 0.16937 | -114.1617 | 6.5186 | 6.4636 | -114.2075 | 6.6788 | 6.5918 | 0.12817 | -114.2166 | 6.6101 | 6.6238 | 6.6513 | -114.3448 | 6.5781 | 6.5689 | 6.665 | -114.3219
5359.2344 | 120.8862 | -5.7175 | 115.21 | -0.24139 | 0.048477 | 0.059686 | 0.0063917 | 0.03061 | -0.0034586 | 0.02616 | -0.19958 | 0.012952 | 0.025346 | 0.03557 | 0.0025271 | 0.016464 | 0.032043 | 0.045776 | 0.022888 | 0.018311 | 0.086975 | 0.018311 | -0.13275 | 0.032043 | 0.041199 | -0.054932 | 0.07782 | 0.059509 | -0.068665 | -0.11444 | 5.7358 | 5.5847 | -115.123 | 5.7632 | 5.7358 | 0.15106 | -115.1779 | 5.6488 | 5.603 | -115.1321 | 5.7495 | 5.6625 | 0.059509 | -115.1505 | 5.8044 | 5.7495 | 5.7404 | -115.3427 | 5.7953 | 5.777 | 5.7587 | -115.3244
5360.9375 | 121.0236 | -4.7653 | 116.1163 | 0.14008 | 0.049332 | 0.059473 | 0.0034009 | 0.028688 | -0.0036722 | 0.027656 | 0.13611 | 0.012097 | 0.023424 | 0.034929 | 0.0018863 | 0.017318 | 0.10071 | 0.10071 | 0.10529 | 0.07782 | 0.059509 | 0.050354 | -0.091553 | 0.13733 | 0.14191 | 0.045776 | 0.013733 | 0.013733 | -0.022888 | -0.059509 | 4.8157 | 4.6738 | -116.0568 | 4.866 | 4.8431 | 0.16937 | -116.0156 | 4.7424 | 4.7058 | -116.1026 | 4.9026 | 4.8111 | 0.10528 | -116.1026 | 4.8248 | 4.866 | 4.8706 | -116.2079 | 4.7791 | 4.7791 | 4.9072 | -116.1758
5362.7031 | 121.0098 | -4.7333 | 116.2628 | 0.063782 | 0.049546 | 0.058618 | -0.0010851 | 0.027192 | -0.0011088 | 0.027228 | 0.036926 | 0.013593 | 0.024919 | 0.037493 | 0.0046633 | 0.017746 | -0.004578 | -0.036621 | -0.041199 | -0.013733 | 0.10529 | 0.022888 | -0.13733 | 0.041199 | -0.022888 | -0.10071 | 0.073242 | 0.054932 | -0.073242 | -0.11902 | 4.7562 | 4.5959 | -116.1575 | 4.6967 | 4.7195 | 0.1236 | -116.2674 | 4.66 | 4.6143 | -116.1896 | 4.7745 | 4.6326 | 0.018311 | -116.2079 | 4.8386 | 4.7287 | 4.6921 | -116.4001 | 4.8065 | 4.7882 | 4.7104 | -116.3818
5364.4688 | 121.0602 | -4.6829 | 116.2949 | -0.18799 | 0.051468 | 0.060968 | 0.0014783 | 0.027406 | -0.00025418 | 0.030006 | -0.21484 | 0.012952 | 0.024278 | 0.033861 | 0.0035953 | 0.015609 | 0.004578 | 0.009155 | -0.013733 | 0.018311 | 0.10529 | -0.004578 | -0.15564 | 0.059509 | 0.068665 | -0.050354 | 0.07782 | 0.032043 | -0.064087 | -0.09613 | 4.6783 | 4.5273 | -116.1896 | 4.6921 | 4.7012 | 0.17395 | -116.2903 | 4.6188 | 4.5868 | -116.217 | 4.7424 | 4.6326 | 0.045776 | -116.2628 | 4.7882 | 4.6875 | 4.6692 | -116.4505 | 4.7607 | 4.715 | 4.7516 | -116.391
5366.2344 | 121.0739 | -4.715 | 116.3177 | 0.079041 | 0.049332 | 0.058405 | 0.0031873 | 0.02826 | -0.00089518 | 0.03086 | 0.067444 | 0.016156 | 0.024278 | 0.036425 | 0.0053043 | 0.020309 | -0.018311 | -0.022888 | -0.036621 | -0.009155 | 0.1236 | 0.013733 | -0.15106 | 0.022888 | -0.018311 | -0.11444 | 0.068665 | 0.059509 | -0.050354 | -0.10529 | 4.7287 | 4.5639 | -116.1942 | 4.6921 | 4.7058 | 0.14191 | -116.3361 | 4.6646 | 4.6097 | -116.2491 | 4.7379 | 4.6005 | -0.009155 | -116.2582 | 4.8386 | 4.6967 | 4.6783 | -116.4688 | 4.7836 | 4.7745 | 4.6967 | -116.423
5367.9375 | 121.0693 | -4.4632 | 116.6428 | -0.24902 | 0.049759 | 0.061182 | 0.0081007 | 0.027619 | -0.0055948 | 0.027015 | -0.18433 | 0.01402 | 0.024705 | 0.033007 | 0.00060451 | 0.02095 | -0.036621 | 0.036621 | -0.013733 | -0.004578 | 0.10529 | 0.013733 | -0.15106 | 0.027466 | 0.054932 | -0.073242 | 0.091553 | 0.059509 | -0.068665 | -0.13275 | 4.4769 | 4.3121 | -116.5375 | 4.4998 | 4.4586 | 0.14648 | -116.6794 | 4.3945 | 4.3304 | -116.5512 | 4.4907 | 4.39 | 0.059509 | -116.5833 | 4.5685 | 4.4266 | 4.4495 | -116.7938 | 4.5547 | 4.5227 | 4.5181 | -116.7755
5369.7031 | 121.1884 | -4.3488 | 116.6611 | 0.14771 | 0.046555 | 0.057977 | 0.0025465 | 0.029115 | -0.0064492 | 0.031501 | 0.159 | 0.012952 | 0.021928 | 0.038347 | 0.0031681 | 0.017959 | 0.082397 | 0.11444 | 0.10071 | 0.082397 | 0.068665 | 0.050354 | -0.09613 | 0.14648 | 0.13733 | 0.032043 | 0.027466 | 0.022888 | -0.036621 | -0.059509 | 4.3991 | 4.2526 | -116.5924 | 4.4632 | 4.4312 | 0.17853 | -116.5787 | 4.3121 | 4.2892 | -116.6336 | 4.4952 | 4.3808 | 0.091552 | -116.6382 | 4.4174 | 4.4312 | 4.4495 | -116.7572 | 4.3762 | 4.3716 | 4.4861 | -116.7206
5371.4062 | 121.2204 | -4.4861 | 116.5924 | 0.056152 | 0.046128 | 0.060541 | 0.0053235 | 0.027192 | -0.0087992 | 0.028297 | 0.097962 | 0.014447 | 0.025774 | 0.035998 | -0.0013181 | 0.019241 | 0.027466 | 0.050354 | 0.059509 | 0.032043 | 0.082397 | 0.041199 | -0.10986 | 0.091553 | 0.086975 | 0.009155 | 0.041199 | 0.032043 | -0.032043 | -0.073242 | 4.5273 | 4.3762 | -116.51 | 4.5364 | 4.5181 | 0.14191 | -116.5649 | 4.454 | 4.4128 | -116.5512 | 4.5776 | 4.4952 | 0.082397 | -116.5604 | 4.5685 | 4.5136 | 4.5456 | -116.7023 | 4.5273 | 4.5181 | 4.5731 | -116.6656
5373.1719 | 121.1746 | -4.5502 | 116.6382 | -0.11169 | 0.051468 | 0.058832 | 0.0034009 | 0.027192 | 0.00017302 | 0.027869 | -0.14618 | 0.015943 | 0.025133 | 0.034289 | 0.0061587 | 0.015182 | 0.086975 | 0.041199 | 0.009155 | 0.027466 | 0.10986 | 0.013733 | -0.15106 | 0.082397 | 0.082397 | -0.045776 | 0.054932 | 0.045776 | -0.059509 | -0.10071 | 4.5639 | 4.3991 | -116.5283 | 4.5914 | 4.5776 | 0.17853 | -116.5512 | 4.4907 | 4.4495 | -116.5833 | 4.6326 | 4.5044 | 0.054932 | -116.5924 | 4.66 | 4.6371 | 4.5593 | -116.7892 | 4.6051 | 4.5959 | 4.6326 | -116.7389
5374.875 | 121.1334 | -4.4449 | 116.6885 | 0.040894 | 0.048691 | 0.057764 | 0.00083745 | 0.029115 | 0.0014548 | 0.030006 | -0.016479 | 0.01402 | 0.026201 | 0.037493 | 0.0035953 | 0.016677 | 0 | -0.036621 | -0.041199 | -0.013733 | 0.11902 | 0.013733 | -0.13275 | 0.013733 | -0.022888 | -0.1236 | 0.082397 | 0.082397 | -0.064087 | -0.10071 | 4.4586 | 4.3121 | -116.5695 | 4.4083 | 4.4312 | 0.11902 | -116.6885 | 4.3808 | 4.3442 | -116.6061 | 4.4586 | 4.3213 | -0.022888 | -116.6061 | 4.5639 | 4.4449 | 4.4037 | -116.8213 | 4.5273 | 4.5273 | 4.422 | -116.7892
5376.6406 | 121.1792 | -3.8635 | 117.3157 | -0.04303 | 0.049332 | 0.056268 | 0.0053235 | 0.030183 | -0.001536 | 0.027442 | -0.024109 | 0.017438 | 0.026201 | 0.038561 | 0.0053043 | 0.017532 | 0.041199 | -0.004578 | -0.013733 | 0.018311 | 0.10986 | 0.004578 | -0.13733 | 0.027466 | 0.022888 | -0.10071 | 0.054932 | 0.064087 | -0.054932 | -0.10529 | 3.8681 | 3.7262 | -117.2058 | 3.8589 | 3.8818 | 0.15564 | -117.2745 | 3.8086 | 3.7582 | -117.2607 | 3.891 | 3.7628 | 0.004578 | -117.2516 | 3.9734 | 3.9047 | 3.8498 | -117.453 | 3.9185 | 3.9276 | 3.8864 | -117.421
5378.3906 | 120.4285 | -82.1915 | 38.1546 | -0.24139 | 0.048264 | 0.063532 | 0.0025465 | 0.026338 | -0.0064492 | 0.027869 | -0.16907 | 0.013379 | 0.021715 | 0.034716 | -3.629e-05 | 0.020095 | 0 | 0.022888 | 0.013733 | 0.004578 | 0.10529 | 0.009155 | -0.16022 | 0.018311 | 0.036621 | -0.068665 | 0.091553 | 0.041199 | -0.059509 | -0.10529 | 82.2006 | 82.0312 | -38.0493 | 82.2144 | 82.196 | 0.16479 | -38.1546 | 82.132 | 82.0862 | -38.063 | 82.2098 | 82.1228 | 0.036621 | -38.1134 | 82.2968 | 82.1915 | 82.2052 | -38.3148 | 82.283 | 82.2327 | 82.2281 | -38.2599
5380.1719 | 120.2316 | -10.7208 | 109.7992 | -0.073547 | 0.049546 | 0.059473 | 0.0014783 | 0.029756 | -0.00089518 | 0.030219 | -0.092773 | 0.014447 | 0.023637 | 0.035784 | 0.0038089 | 0.017959 | 0.054932 | 0.045776 | 0.004578 | 0.027466 | 0.09613 | 0.027466 | -0.11444 | 0.068665 | 0.064087 | -0.064087 | 0.059509 | 0.050354 | -0.041199 | -0.10529 | 10.7483 | 10.6064 | -109.7031 | 10.7666 | 10.7483 | 0.14191 | -109.7443 | 10.6796 | 10.6155 | -109.7397 | 10.7895 | 10.6567 | 0.041199 | -109.7488 | 10.817 | 10.7758 | 10.7254 | -109.9136 | 10.7803 | 10.7712 | 10.7849 | -109.9045
5381.8594 | 120.9732 | -111.0214 | 9.4254 | -0.1651 | 0.046555 | 0.06225 | 0.0019055 | 0.025483 | -0.0098672 | 0.028297 | -0.031738 | 0.01402 | 0.024065 | 0.034075 | 0.00017731 | 0.020309 | 0.054932 | 0.16937 | 0.1236 | 0.068665 | 0.07782 | 0.050354 | -0.09613 | 0.15106 | 0.18768 | 0.091553 | 0.022888 | 0.013733 | -0.018311 | -0.064087 | 111.0718 | 110.9253 | -9.3475 | 111.1908 | 111.0901 | 0.16479 | -9.3704 | 111.0031 | 110.9573 | -9.4025 | 111.1725 | 111.113 | 0.15564 | -9.4116 | 111.0992 | 111.0764 | 111.145 | -9.5215 | 111.0443 | 111.0352 | 111.2091 | -9.4894
5383.6094 | 121.0144 | -119.1605 | 1.4923 | 0.08667 | 0.045914 | 0.057764 | 0.0014783 | 0.027619 | -0.007731 | 0.02851 | 0.13611 | 0.013166 | 0.024065 | 0.035998 | 0.0031681 | 0.017746 | 0.036621 | 0.10986 | 0.073242 | 0.050354 | 0.073242 | 0.041199 | -0.10071 | 0.11902 | 0.10071 | 0 | 0.018311 | 0.032043 | -0.032043 | -0.10071 | 119.2017 | 119.0598 | -1.4191 | 119.2703 | 119.2108 | 0.15106 | -1.4557 | 119.1284 | 119.0598 | -1.474 | 119.2795 | 119.1605 | 0.10071 | -1.4603 | 119.2337 | 119.1971 | 119.2337 | -1.593 | 119.1788 | 119.1925 | 119.2612 | -1.593
5385.375 | 121.1014 | -119.696 | 0.99792 | 0.14771 | 0.048264 | 0.060754 | 0.0040417 | 0.02826 | -0.002604 | 0.02851 | 0.067444 | 0.013379 | 0.023637 | 0.03557 | 0.0035953 | 0.0139 | 0.073242 | 0.059509 | 0.059509 | 0.041199 | 0.082397 | 0.036621 | -0.10986 | 0.1236 | 0.11444 | 0.032043 | 0.041199 | 0.022888 | -0.018311 | -0.050354 | 119.7327 | 119.5862 | -0.91553 | 119.7556 | 119.7372 | 0.15106 | -0.92468 | 119.6777 | 119.6457 | -0.95673 | 119.8196 | 119.7281 | 0.082397 | -0.97504 | 119.7784 | 119.7693 | 119.7556 | -1.1078 | 119.7372 | 119.7189 | 119.8105 | -1.0483
5387.125 | 120.9961 | -0.40741 | 120.5566 | 0.025635 | 0.044205 | 0.061395 | 0.0044691 | 0.026338 | -0.0073038 | 0.027656 | 0.082703 | 0.012311 | 0.025346 | 0.035357 | -0.0011045 | 0.016677 | 0.036621 | 0.064087 | 0.064087 | 0.041199 | 0.064087 | 0.032043 | -0.11444 | 0.091553 | 0.07782 | 0.009155 | 0.050354 | 0.041199 | -0.036621 | -0.082397 | 0.43945 | 0.29297 | -120.4926 | 0.4715 | 0.44861 | 0.15564 | -120.52 | 0.37079 | 0.32501 | -120.5063 | 0.49896 | 0.41657 | 0.091552 | -120.5154 | 0.4715 | 0.44403 | 0.4715 | -120.6711 | 0.45776 | 0.44861 | 0.48523 | -120.639
5388.8281 | 121.0556 | -0.3891 | 120.575 | 0.056152 | 0.044846 | 0.058405 | 0.0016919 | 0.029328 | -0.0062356 | 0.026374 | 0.12848 | 0.011029 | 0.022569 | 0.036852 | 0.0020999 | 0.017746 | 0.07782 | 0.11444 | 0.082397 | 0.059509 | 0.045776 | 0.050354 | -0.10986 | 0.13275 | 0.09613 | 0.032043 | 0.027466 | 0.027466 | -0.018311 | -0.086975 | 0.43945 | 0.27924 | -120.5292 | 0.50354 | 0.44861 | 0.16937 | -120.4971 | 0.37079 | 0.30212 | -120.5475 | 0.52185 | 0.42114 | 0.11902 | -120.5475 | 0.43487 | 0.46692 | 0.4715 | -120.6848 | 0.41656 | 0.41656 | 0.48523 | -120.6619
5390.5781 | 121.1151 | -0.38452 | 120.6436 | -0.14221 | 0.046341 | 0.061395 | 0.0070325 | 0.028688 | -0.0081582 | 0.026374 | -0.16144 | 0.011029 | 0.024705 | 0.033648 | 0.00039091 | 0.016037 | 0.11902 | 0.16479 | 0.10986 | 0.091553 | 0.082397 | 0.022888 | -0.11902 | 0.14648 | 0.16937 | 0.059509 | 0.022888 | 0.027466 | -0.009155 | -0.082397 | 0.40741 | 0.2655 | -120.5612 | 0.54932 | 0.47607 | 0.21057 | -120.5246 | 0.37537 | 0.30212 | -120.6207 | 0.531 | 0.44403 | 0.14191 | -120.6161 | 0.46692 | 0.50354 | 0.49438 | -120.7626 | 0.40741 | 0.41199 | 0.55389 | -120.726
5392.3281 | 121.1426 | -0.38452 | 120.6619 | 0.0027468 | 0.043137 | 0.060754 | -0.00044435 | 0.028047 | -0.0068766 | 0.026588 | 0.029297 | 0.010175 | 0.022783 | 0.033861 | 0.0012455 | 0.017959 | 0.050354 | 0.068665 | 0.050354 | 0.036621 | 0.073242 | 0.027466 | -0.10529 | 0.10529 | 0.068665 | -0.009155 | 0.041199 | 0.018311 | -0.041199 | -0.082397 | 0.41199 | 0.27924 | -120.5887 | 0.45319 | 0.42114 | 0.14191 | -120.6116 | 0.34332 | 0.30212 | -120.6207 | 0.48981 | 0.37537 | 0.073242 | -120.6436 | 0.45776 | 0.43488 | 0.43488 | -120.7672 | 0.42572 | 0.40283 | 0.45319 | -120.7443
5394.0312 | 121.0922 | -0.4303 | 120.7169 | -0.18036 | 0.047623 | 0.061182 | 0.0042555 | 0.027833 | -0.0045266 | 0.028937 | -0.18433 | 0.011884 | 0.024705 | 0.033648 | 0.00081811 | 0.014755 | 0.10529 | 0.10986 | 0.10529 | 0.068665 | 0.07782 | 0.032043 | -0.11902 | 0.11902 | 0.15564 | 0.009155 | 0.054932 | 0.032043 | -0.013733 | -0.086975 | 0.46234 | 0.31128 | -120.639 | 0.54016 | 0.49896 | 0.18768 | -120.6116 | 0.41657 | 0.34332 | -120.6619 | 0.54932 | 0.43945 | 0.09613 | -120.6848 | 0.50812 | 0.53558 | 0.53558 | -120.8359 | 0.48523 | 0.46234 | 0.58594 | -120.8038
5395.7812 | 121.2067 | -0.36621 | 120.7031 | -0.17273 | 0.046982 | 0.059686 | 0.0021191 | 0.027833 | -0.004954 | 0.029365 | -0.1767 | 0.0097476 | 0.02556 | 0.034502 | 0.00060451 | 0.019668 | 0.10529 | 0.15106 | 0.1236 | 0.064087 | 0.068665 | 0.050354 | -0.1236 | 0.14191 | 0.17853 | 0.059509 | 0.013733 | 0.013733 | -0.032043 | -0.086975 | 0.41657 | 0.24262 | -120.6345 | 0.51727 | 0.4303 | 0.18768 | -120.5978 | 0.33417 | 0.27924 | -120.6894 | 0.50812 | 0.42572 | 0.14648 | -120.6894 | 0.43488 | 0.4715 | 0.48981 | -120.8267 | 0.37994 | 0.37994 | 0.54474 | -120.7901
5397.5312 | 121.1563 | -0.41657 | 120.7535 | -0.19562 | 0.049332 | 0.061182 | 0.0034009 | 0.028688 | -0.0045266 | 0.030219 | -0.16907 | 0.013806 | 0.023851 | 0.035784 | 0.00060451 | 0.017318 | 0.091553 | 0.13733 | 0.10986 | 0.068665 | 0.073242 | 0.045776 | -0.11902 | 0.11902 | 0.15564 | 0.022888 | 0.045776 | 0.032043 | -0.032043 | -0.068665 | 0.46234 | 0.29755 | -120.6802 | 0.55389 | 0.48523 | 0.18768 | -120.6619 | 0.38452 | 0.3479 | -120.7077 | 0.53558 | 0.43945 | 0.091553 | -120.7214 | 0.48981 | 0.50812 | 0.52643 | -120.8725 | 0.46234 | 0.44861 | 0.57221 | -120.8221
5399.2969 | 120.3506 | -0.37079 | 119.8334 | 0.10193 | 0.050186 | 0.056055 | 0.0010511 | 0.028047 | 0.00081382 | 0.026801 | 0.014038 | 0.015302 | 0.025346 | 0.036425 | 0.0063723 | 0.016891 | 0.022888 | -0.013733 | -0.018311 | -0.022888 | 0.1236 | 0.018311 | -0.13733 | 0.073242 | 0.004578 | -0.086975 | 0.073242 | 0.045776 | -0.059509 | -0.09613 | 0.3891 | 0.23346 | -119.7098 | 0.35706 | 0.3479 | 0.11444 | -119.8105 | 0.31128 | 0.27466 | -119.7601 | 0.44403 | 0.28381 | 0.009155 | -119.7876 | 0.49438 | 0.39368 | 0.35248 | -119.9707 | 0.44403 | 0.41656 | 0.37537 | -119.9295
5401 | 120.6802 | -0.38452 | 120.2637 | -0.1651 | 0.051682 | 0.059473 | 0.0053235 | 0.027406 | 0.0014548 | 0.031074 | -0.26825 | 0.015943 | 0.023424 | 0.035143 | 0.0033817 | 0.014755 | 0.018311 | 0.013733 | -0.018311 | 0.018311 | 0.10986 | -0.013733 | -0.14648 | 0.054932 | 0.064087 | -0.073242 | 0.059509 | 0.045776 | -0.059509 | -0.09613 | 0.37079 | 0.23804 | -120.1538 | 0.39825 | 0.40283 | 0.16479 | -120.2454 | 0.32501 | 0.28839 | -120.2042 | 0.43945 | 0.31128 | 0.022888 | -120.2179 | 0.49438 | 0.40283 | 0.36621 | -120.4102 | 0.44403 | 0.4303 | 0.44861 | -120.3598
5402.7656 | 120.7993 | -0.40283 | 120.3781 | -0.20325 | 0.051895 | 0.057977 | 0.0051099 | 0.028047 | 0.00017302 | 0.028297 | -0.20721 | 0.014661 | 0.023851 | 0.036852 | 0.0033817 | 0.016677 | 0.022888 | 0.013733 | -0.013733 | 0.022888 | 0.11444 | -0.018311 | -0.15106 | 0.054932 | 0.064087 | -0.054932 | 0.07782 | 0.068665 | -0.054932 | -0.10986 | 0.38452 | 0.25177 | -120.2637 | 0.41657 | 0.42572 | 0.17395 | -120.3552 | 0.3479 | 0.29297 | -120.3003 | 0.45776 | 0.3479 | 0.054931 | -120.3094 | 0.51727 | 0.42572 | 0.3891 | -120.5292 | 0.48065 | 0.4715 | 0.46692 | -120.488
5404.5312 | 120.8725 | -0.39825 | 120.4559 | -0.21088 | 0.04805 | 0.060114 | 0.0051099 | 0.029542 | -0.0070902 | 0.027869 | -0.11566 | 0.010816 | 0.025133 | 0.034502 | -0.0011045 | 0.018386 | 0.082397 | 0.14648 | 0.11902 | 0.068665 | 0.059509 | 0.050354 | -0.10986 | 0.12817 | 0.17395 | 0.050354 | 0.018311 | 0.022888 | -0.027466 | -0.073242 | 0.44861 | 0.28839 | -120.3964 | 0.54474 | 0.46692 | 0.17853 | -120.3735 | 0.37079 | 0.32501 | -120.4376 | 0.52643 | 0.44861 | 0.1236 | -120.433 | 0.45776 | 0.48065 | 0.51727 | -120.5658 | 0.41657 | 0.42114 | 0.5722 | -120.5292
5406.2969 | 120.8633 | -0.41657 | 120.5246 | -0.050659 | 0.051255 | 0.060327 | 0.0012647 | 0.030397 | 0.0012412 | 0.028937 | -0.054626 | 0.014875 | 0.023637 | 0.036638 | 0.0059451 | 0.017746 | 0.050354 | 0.041199 | -0.013733 | 0.022888 | 0.09613 | 0.018311 | -0.14191 | 0.050354 | 0.013733 | -0.09613 | 0.068665 | 0.045776 | -0.050354 | -0.11444 | 0.43488 | 0.27466 | -120.4285 | 0.45776 | 0.43945 | 0.16479 | -120.4742 | 0.36621 | 0.30212 | -120.4559 | 0.46692 | 0.32044 | 0.018311 | -120.4788 | 0.5127 | 0.46692 | 0.40283 | -120.6665 | 0.48523 | 0.46234 | 0.4303 | -120.639
5408.0469 | 120.9778 | -0.37994 | 120.5658 | -0.1651 | 0.051255 | 0.057764 | 0.0040417 | 0.027619 | -0.00025418 | 0.029151 | -0.1767 | 0.014234 | 0.023851 | 0.035998 | 0.0033817 | 0.017105 | 0.022888 | 0.059509 | 0.009155 | 0.036621 | 0.10071 | -0.004578 | -0.15564 | 0.068665 | 0.073242 | -0.041199 | 0.059509 | 0.041199 | -0.059509 | -0.10986 | 0.37537 | 0.2243 | -120.4651 | 0.43945 | 0.41657 | 0.19226 | -120.5429 | 0.32044 | 0.27008 | -120.5063 | 0.44861 | 0.33875 | 0.068664 | -120.5246 | 0.48065 | 0.40283 | 0.3891 | -120.7214 | 0.43945 | 0.42114 | 0.45319 | -120.6757
5409.75 | 121.0876 | -0.36163 | 120.6116 | -0.17273 | 0.048477 | 0.059473 | 0.0048963 | 0.028901 | -0.0087992 | 0.027656 | -0.13855 | 0.011029 | 0.026414 | 0.033221 | -0.00046349 | 0.017746 | 0.064087 | 0.16937 | 0.10529 | 0.086975 | 0.082397 | 0.045776 | -0.1236 | 0.11902 | 0.19684 | 0.059509 | 0.032043 | 0.018311 | -0.018311 | -0.068665 | 0.40741 | 0.23804 | -120.5292 | 0.53101 | 0.44861 | 0.21057 | -120.5475 | 0.34332 | 0.29297 | -120.5795 | 0.48065 | 0.42114 | 0.12817 | -120.5933 | 0.44403 | 0.42572 | 0.46692 | -120.7352 | 0.39368 | 0.37994 | 0.55847 | -120.6802
5411.5156 | 121.1288 | -0.3891 | 120.6436 | 0.11719 | 0.047196 | 0.060754 | -0.00087155 | 0.028047 | -0.0058084 | 0.029578 | 0.12085 | 0.014875 | 0.02556 | 0.036211 | 0.0010317 | 0.019027 | 0.086975 | 0.13733 | 0.091553 | 0.068665 | 0.059509 | 0.041199 | -0.091553 | 0.14191 | 0.12817 | 0.050354 | 0.032043 | 0.018311 | -0.027466 | -0.07782 | 0.4303 | 0.29755 | -120.5841 | 0.52643 | 0.45776 | 0.16022 | -120.5566 | 0.36163 | 0.31128 | -120.6116 | 0.53101 | 0.43945 | 0.12817 | -120.6253 | 0.44861 | 0.47607 | 0.48065 | -120.7352 | 0.42114 | 0.40741 | 0.51727 | -120.7214
5413.2812 | 121.2204 | -0.35706 | 120.6573 | -0.0354 | 0.046555 | 0.059686 | 0.0059643 | 0.02591 | -0.010081 | 0.027656 | -0.016479 | 0.010816 | 0.024278 | 0.034289 | -0.0023861 | 0.017532 | 0.041199 | 0.059509 | 0.059509 | 0.059509 | 0.091553 | 0.022888 | -0.10529 | 0.10529 | 0.13275 | 0.041199 | 0.054932 | 0.018311 | -0.022888 | -0.073242 | 0.37994 | 0.25177 | -120.5658 | 0.41656 | 0.41656 | 0.16479 | -120.6161 | 0.33417 | 0.28381 | -120.6024 | 0.46234 | 0.39825 | 0.11444 | -120.639 | 0.44861 | 0.39825 | 0.41656 | -120.7626 | 0.41199 | 0.37537 | 0.48981 | -120.7306
5415 | 121.1334 | -0.40741 | 120.7443 | -0.24139 | 0.047623 | 0.060114 | 0.0021191 | 0.028901 | -0.0030314 | 0.029578 | -0.24536 | 0.013593 | 0.026201 | 0.036211 | 0.0025271 | 0.016677 | 0.004578 | -0.013733 | -0.041199 | -0.009155 | 0.09613 | -0.013733 | -0.15106 | 0.032043 | 0.022888 | -0.07782 | 0.068665 | 0.050354 | -0.059509 | -0.10529 | 0.39368 | 0.25635 | -120.6482 | 0.39368 | 0.39825 | 0.14191 | -120.7397 | 0.3479 | 0.30212 | -120.6757 | 0.43945 | 0.32959 | 0.027466 | -120.694 | 0.50354 | 0.41199 | 0.36621 | -120.8954 | 0.47608 | 0.45776 | 0.4303 | -120.8496
5416.75 | 121.1746 | -0.39825 | 120.7123 | -0.22614 | 0.051041 | 0.058832 | 0.0053235 | 0.02826 | -0.002604 | 0.028297 | -0.20721 | 0.014875 | 0.024492 | 0.040911 | 0.0023135 | 0.018386 | 0.018311 | -0.009155 | -0.032043 | 0 | 0.12817 | -0.004578 | -0.16937 | 0.032043 | 0.032043 | -0.082397 | 0.086975 | 0.064087 | -0.045776 | -0.10071 | 0.39368 | 0.22888 | -120.5841 | 0.3891 | 0.39825 | 0.16937 | -120.694 | 0.35248 | 0.29755 | -120.6253 | 0.4303 | 0.31586 | 0.018311 | -120.6482 | 0.52643 | 0.41657 | 0.36621 | -120.8817 | 0.48523 | 0.46234 | 0.4303 | -120.813
5418.5 | 121.2341 | -0.39825 | 120.7535 | 0.10956 | 0.049546 | 0.060968 | -0.00044435 | 0.027833 | -0.0011088 | 0.030646 | 0.036926 | 0.013166 | 0.022356 | 0.035784 | 0.0042361 | 0.016677 | 0.009155 | -0.013733 | -0.045776 | -0.009155 | 0.1236 | 0.009155 | -0.1236 | 0.059509 | 0 | -0.07782 | 0.07782 | 0.045776 | -0.059509 | -0.10986 | 0.40741 | 0.27466 | -120.6299 | 0.38452 | 0.3891 | 0.11444 | -120.7443 | 0.33875 | 0.28839 | -120.6757 | 0.45776 | 0.32043 | 0.032043 | -120.7077 | 0.52185 | 0.40741 | 0.35248 | -120.8771 | 0.47607 | 0.44403 | 0.39825 | -120.8633
5420.2812 | 121.2708 | -0.37079 | 120.7352 | 0.10956 | 0.048905 | 0.057977 | -0.00023075 | 0.029328 | -0.0051676 | 0.031074 | 0.16663 | 0.013593 | 0.022356 | 0.036211 | 0.0029543 | 0.016677 | 0.10071 | 0.1236 | 0.11444 | 0.073242 | 0.068665 | 0.027466 | -0.11444 | 0.16022 | 0.14191 | 0.032043 | 0.018311 | 0.004578 | -0.013733 | -0.059509 | 0.39825 | 0.25635 | -120.6665 | 0.49438 | 0.44403 | 0.18768 | -120.6345 | 0.35706 | 0.31128 | -120.7169 | 0.53101 | 0.40283 | 0.091552 | -120.7306 | 0.43945 | 0.4715 | 0.48523 | -120.8496 | 0.3891 | 0.37537 | 0.5127 | -120.7947
5422.0469 | 121.225 | -0.40283 | 120.7947 | -0.18799 | 0.048905 | 0.0599 | 0.0063917 | 0.026338 | -0.0062356 | 0.02851 | -0.11566 | 0.012311 | 0.025133 | 0.034289 | -0.0028135 | 0.0186 | 0.07782 | 0.14191 | 0.10529 | 0.086975 | 0.059509 | 0.027466 | -0.10529 | 0.11444 | 0.16022 | 0.045776 | 0.032043 | 0.022888 | -0.018311 | -0.068665 | 0.4303 | 0.29755 | -120.7352 | 0.54474 | 0.48981 | 0.19226 | -120.7169 | 0.38452 | 0.33417 | -120.7626 | 0.51727 | 0.44861 | 0.11444 | -120.7718 | 0.46234 | 0.48065 | 0.50812 | -120.9 | 0.43488 | 0.42572 | 0.56305 | -120.8633
5423.75 | 121.312 | -0.3891 | 120.7764 | 0.08667 | 0.048905 | 0.05755 | 0.0010511 | 0.028901 | -0.00025418 | 0.027869 | 0.044556 | 0.013806 | 0.022996 | 0.03792 | 0.0031681 | 0.017318 | 0.013733 | -0.036621 | -0.041199 | -0.009155 | 0.10529 | 0.013733 | -0.15564 | 0.054932 | -0.004578 | -0.082397 | 0.068665 | 0.054932 | -0.045776 | -0.11444 | 0.40283 | 0.23346 | -120.6711 | 0.35248 | 0.37994 | 0.14649 | -120.7626 | 0.34332 | 0.27466 | -120.7077 | 0.44403 | 0.3067 | 0.032044 | -120.7214 | 0.49438 | 0.40283 | 0.3479 | -120.932 | 0.45776 | 0.44403 | 0.38452 | -120.8908
5425.5156 | 121.3531 | -0.37079 | 120.7855 | 0.079041 | 0.047196 | 0.059045 | 0.00019645 | 0.029756 | -0.0047404 | 0.029365 | 0.12848 | 0.012311 | 0.024065 | 0.034289 | 0.0044497 | 0.017746 | 0.07782 | 0.10986 | 0.086975 | 0.073242 | 0.073242 | 0.045776 | -0.11444 | 0.13275 | 0.1236 | 0.041199 | 0.013733 | 0.018311 | -0.036621 | -0.073242 | 0.41656 | 0.25635 | -120.7123 | 0.48065 | 0.44403 | 0.18768 | -120.7077 | 0.33417 | 0.29755 | -120.7718 | 0.50354 | 0.41199 | 0.11444 | -120.7672 | 0.44403 | 0.44861 | 0.45776 | -120.9 | 0.38452 | 0.3891 | 0.49438 | -120.8588
5427.2812 | 121.2479 | -0.4303 | 120.8405 | -0.18036 | 0.048905 | 0.058832 | 0.0053235 | 0.028901 | -0.0040994 | 0.029151 | -0.20721 | 0.012311 | 0.024919 | 0.035357 | -0.0011045 | 0.018173 | 0.068665 | 0.10986 | 0.07782 | 0.073242 | 0.07782 | 0.041199 | -0.10986 | 0.086975 | 0.11902 | -0.009155 | 0.050354 | 0.045776 | -0.032043 | -0.10529 | 0.4715 | 0.32044 | -120.7626 | 0.54016 | 0.50354 | 0.18311 | -120.7718 | 0.39826 | 0.32501 | -120.7901 | 0.51727 | 0.42114 | 0.096131 | -120.7947 | 0.50812 | 0.49896 | 0.50812 | -120.9503 | 0.48065 | 0.47607 | 0.54932 | -120.9457
5429.0312 | 121.3028 | -0.42114 | 120.8633 | -0.21088 | 0.049759 | 0.059686 | 0.0055371 | 0.028901 | -0.0011088 | 0.026374 | -0.22247 | 0.01402 | 0.026842 | 0.037279 | 0.0038089 | 0.015396 | 0 | -0.004578 | -0.027466 | 0.009155 | 0.1236 | -0.004578 | -0.14191 | 0.018311 | 0.050354 | -0.091553 | 0.064087 | 0.045776 | -0.064087 | -0.10529 | 0.41656 | 0.27924 | -120.7397 | 0.41656 | 0.4303 | 0.15106 | -120.8633 | 0.35706 | 0.31586 | -120.7993 | 0.43945 | 0.32959 | 0.013733 | -120.8176 | 0.54474 | 0.42114 | 0.39368 | -121.0052 | 0.48523 | 0.46692 | 0.4715 | -120.9686
5430.7344 | 121.3348 | -0.4303 | 120.8817 | -0.26428 | 0.051255 | 0.059045 | 0.0063917 | 0.024415 | -0.0013224 | 0.026801 | -0.23773 | 0.013806 | 0.026842 | 0.03792 | -0.00089089 | 0.017318 | -0.018311 | -0.022888 | -0.032043 | -0.018311 | 0.10986 | -0.013733 | -0.15564 | 0.027466 | 0.032043 | -0.073242 | 0.068665 | 0.068665 | -0.045776 | -0.11444 | 0.41657 | 0.27466 | -120.7718 | 0.40741 | 0.41199 | 0.13733 | -120.9 | 0.38452 | 0.31586 | -120.813 | 0.45776 | 0.35706 | 0.041199 | -120.813 | 0.54016 | 0.41199 | 0.39826 | -121.0373 | 0.49896 | 0.49896 | 0.46234 | -120.9961
5432.4844 | 121.344 | -0.42572 | 120.8908 | -0.21088 | 0.053391 | 0.057336 | 0.0057507 | 0.02826 | -0.0019632 | 0.029365 | -0.19196 | 0.017224 | 0.026201 | 0.036211 | 0.0012455 | 0.01625 | 0.004578 | -0.018311 | -0.027466 | 0 | 0.10986 | 0 | -0.15106 | 0.018311 | 0.054932 | -0.086975 | 0.073242 | 0.059509 | -0.059509 | -0.11444 | 0.42572 | 0.27466 | -120.7809 | 0.40741 | 0.42572 | 0.15106 | -120.8862 | 0.36621 | 0.31128 | -120.8176 | 0.44403 | 0.33874 | 0.027466 | -120.8313 | 0.53558 | 0.4303 | 0.39825 | -121.0419 | 0.49896 | 0.48523 | 0.48065 | -121.0052
5434.1875 | 121.4035 | -0.39825 | 120.8862 | 0.10193 | 0.046768 | 0.060541 | -0.0010851 | 0.024842 | -0.0079446 | 0.027442 | 0.12085 | 0.013166 | 0.022996 | 0.03557 | 0.0014591 | 0.017746 | 0.07782 | 0.1236 | 0.11444 | 0.073242 | 0.041199 | 0.041199 | -0.082397 | 0.12817 | 0.11444 | 0.036621 | 0.032043 | 0.009155 | -0.032043 | -0.07782 | 0.43945 | 0.31586 | -120.845 | 0.52185 | 0.4715 | 0.15564 | -120.8084 | 0.36621 | 0.32043 | -120.8542 | 0.52643 | 0.43488 | 0.11444 | -120.8771 | 0.43945 | 0.47607 | 0.5127 | -120.9686 | 0.4303 | 0.40741 | 0.5127 | -120.9641
5435.9531 | 121.4035 | -0.44403 | 120.8633 | 0.079041 | 0.050614 | 0.061182 | -0.00023075 | 0.026338 | 0.00038662 | 0.029578 | 0.059815 | 0.012952 | 0.024492 | 0.037493 | 0.0063723 | 0.017318 | -0.004578 | -0.032043 | -0.027466 | -0.013733 | 0.10071 | 0.004578 | -0.14191 | 0.041199 | -0.013733 | -0.082397 | 0.068665 | 0.064087 | -0.050354 | -0.10529 | 0.44861 | 0.30212 | -120.7626 | 0.41199 | 0.4303 | 0.12817 | -120.8679 | 0.39368 | 0.33875 | -120.7947 | 0.48523 | 0.36163 | 0.022889 | -120.7993 | 0.54474 | 0.43945 | 0.41657 | -121.0052 | 0.5127 | 0.50812 | 0.4303 | -120.9686
5437.7188 | 121.3852 | -0.44403 | 120.9366 | -0.21088 | 0.046128 | 0.061609 | 0.0034009 | 0.028474 | -0.0079446 | 0.027869 | -0.13092 | 0.013166 | 0.022996 | 0.034075 | -0.00067729 | 0.020095 | 0.059509 | 0.1236 | 0.10986 | 0.068665 | 0.059509 | 0.036621 | -0.10986 | 0.11444 | 0.17853 | 0.041199 | 0.027466 | 0.004578 | -0.041199 | -0.07782 | 0.48065 | 0.33417 | -120.8771 | 0.56763 | 0.5127 | 0.17853 | -120.8771 | 0.40283 | 0.36621 | -120.9091 | 0.55847 | 0.48523 | 0.11902 | -120.932 | 0.50354 | 0.50354 | 0.55389 | -121.0464 | 0.4715 | 0.44861 | 0.62256 | -121.0144
5439.4062 | 121.4172 | -0.43945 | 120.9412 | -0.13458 | 0.051468 | 0.056482 | 0.0031873 | 0.027833 | 0.0010276 | 0.028724 | -0.16144 | 0.016156 | 0.025133 | 0.03792 | 0.0048769 | 0.01625 | 0.064087 | 0.027466 | 0.004578 | 0.045776 | 0.11444 | -0.009155 | -0.15564 | 0.073242 | 0.068665 | -0.032043 | 0.064087 | 0.059509 | -0.045776 | -0.1236 | 0.4303 | 0.28381 | -120.8267 | 0.46692 | 0.48523 | 0.20142 | -120.8771 | 0.39368 | 0.31586 | -120.8771 | 0.5127 | 0.40741 | 0.091553 | -120.8817 | 0.55389 | 0.50354 | 0.44403 | -121.0968 | 0.50354 | 0.49896 | 0.50812 | -121.0648
5441.1719 | 121.4539 | -0.41199 | 120.9457 | 0.10956 | 0.046982 | 0.060327 | 0.0012647 | 0.02527 | -0.006022 | 0.02851 | 0.15137 | 0.012097 | 0.025133 | 0.037707 | 0.0010317 | 0.016677 | 0.086975 | 0.13733 | 0.11902 | 0.068665 | 0.064087 | 0.054932 | -0.09613 | 0.15106 | 0.13275 | 0.045776 | 0.027466 | 0.018311 | -0.032043 | -0.064087 | 0.46692 | 0.31586 | -120.8817 | 0.54932 | 0.48065 | 0.16479 | -120.8588 | 0.37994 | 0.3479 | -120.9183 | 0.56305 | 0.45776 | 0.10986 | -120.9274 | 0.47607 | 0.49896 | 0.53101 | -121.0419 | 0.43945 | 0.4303 | 0.54474 | -121.0098
5442.9375 | 121.3989 | -0.44861 | 120.9686 | 0.048523 | 0.050186 | 0.057764 | 0.0021191 | 0.027192 | -4.058e-05 | 0.029151 | -0.0012209 | 0.014234 | 0.025133 | 0.036852 | 0.0035953 | 0.017105 | 0.004578 | -0.045776 | -0.032043 | -0.018311 | 0.10071 | 0.022888 | -0.13733 | 0.013733 | -0.018311 | -0.12817 | 0.068665 | 0.07782 | -0.059509 | -0.11444 | 0.4715 | 0.31128 | -120.8679 | 0.40283 | 0.4303 | 0.11902 | -120.9641 | 0.3891 | 0.33417 | -120.9 | 0.46234 | 0.32043 | -0.013733 | -120.8908 | 0.54932 | 0.45319 | 0.41657 | -121.106 | 0.51727 | 0.52643 | 0.4303 | -121.0831
5444.7188 | 121.4264 | -0.45776 | 120.9732 | 0.040894 | 0.050186 | 0.056909 | 0.0019055 | 0.029328 | -0.0013224 | 0.030433 | 0.044556 | 0.013379 | 0.024919 | 0.038134 | 0.0046633 | 0.016891 | 0.004578 | -0.054932 | -0.050354 | -0.013733 | 0.10986 | -0.009155 | -0.14648 | 0.032043 | 0 | -0.10071 | 0.064087 | 0.054932 | -0.059509 | -0.10529 | 0.44861 | 0.31128 | -120.8633 | 0.40283 | 0.44403 | 0.13275 | -120.9686 | 0.39826 | 0.35248 | -120.9091 | 0.48981 | 0.35706 | 0.004578 | -120.9183 | 0.56763 | 0.46234 | 0.40741 | -121.1197 | 0.52185 | 0.5127 | 0.45776 | -121.0785
5446.4844 | 121.5546 | -0.40283 | 120.9549 | 0.12482 | 0.048477 | 0.057764 | 0.0012647 | 0.028047 | -0.0019632 | 0.031074 | 0.16663 | 0.013593 | 0.022569 | 0.037493 | 0.0031681 | 0.019455 | 0.018311 | 0 | 0.009155 | 0.009155 | 0.09613 | 0.009155 | -0.11902 | 0.10529 | 0.073242 | -0.013733 | 0.059509 | 0.041199 | -0.036621 | -0.091553 | 0.41199 | 0.28381 | -120.8588 | 0.40283 | 0.41199 | 0.12817 | -120.9366 | 0.36621 | 0.31128 | -120.8954 | 0.50812 | 0.3891 | 0.07782 | -120.9137 | 0.49896 | 0.42114 | 0.41199 | -121.0739 | 0.46234 | 0.44403 | 0.47607 | -121.0464
5448.1875 | 120.5429 | -119.2291 | 0.86517 | 0.063782 | 0.048264 | 0.057764 | 0.0027601 | 0.027619 | -0.0023904 | 0.029151 | 0.15137 | 0.01402 | 0.023851 | 0.038988 | 0.0031681 | 0.016677 | 0.009155 | -0.009155 | -0.018311 | -0.009155 | 0.09613 | -0.009155 | -0.12817 | 0.07782 | 0.027466 | -0.059509 | 0.073242 | 0.045776 | -0.041199 | -0.068665 | 119.22 | 119.101 | -0.76904 | 119.22 | 119.22 | 0.11902 | -0.85602 | 119.1879 | 119.1605 | -0.79193 | 119.3069 | 119.1696 | 0.009156 | -0.8194 | 119.3253 | 119.2383 | 119.2108 | -0.99335 | 119.3024 | 119.2749 | 119.2566 | -0.93384
5449.8906 | 121.0876 | -120.1447 | 0.72784 | 0.018005 | 0.051041 | 0.059686 | 0.0012647 | 0.027406 | -0.0038858 | 0.030006 | 0.12848 | 0.015729 | 0.02556 | 0.037707 | 0.0040225 | 0.017959 | -0.027466 | -0.050354 | -0.054932 | -0.027466 | 0.10071 | 0.004578 | -0.13733 | 0.013733 | -0.009155 | -0.10986 | 0.082397 | 0.041199 | -0.064087 | -0.11902 | 120.1492 | 120.0073 | -0.62714 | 120.0943 | 120.1172 | 0.10986 | -0.75531 | 120.0806 | 120.0256 | -0.64545 | 120.1584 | 120.0348 | 0.009156 | -0.68665 | 120.2454 | 120.1172 | 120.0897 | -0.86517 | 120.2271 | 120.1859 | 120.1355 | -0.84686
5451.6406 | 121.1792 | -120.369 | 0.6546 | -0.18799 | 0.046555 | 0.060114 | 0.0046827 | 0.026338 | -0.0073038 | 0.029792 | -0.10803 | 0.010388 | 0.024919 | 0.037707 | -0.0015317 | 0.017746 | 0.059509 | 0.10529 | 0.10529 | 0.068665 | 0.073242 | 0.027466 | -0.10986 | 0.082397 | 0.15106 | 0.022888 | 0.045776 | 0.041199 | -0.027466 | -0.082397 | 120.3964 | 120.2591 | -0.58136 | 120.4742 | 120.4376 | 0.17853 | -0.59509 | 120.3415 | 120.2866 | -0.60883 | 120.4514 | 120.3918 | 0.10528 | -0.6134 | 120.4422 | 120.4285 | 120.4742 | -0.76447 | 120.4147 | 120.4102 | 120.52 | -0.737
5453.4062 | 121.3577 | -120.4102 | 0.6134 | 0.048523 | 0.046768 | 0.059259 | 0.0014783 | 0.024842 | -0.0028178 | 0.030219 | 0.16663 | 0.013379 | 0.024705 | 0.035784 | 0.0042361 | 0.019668 | 0.09613 | 0.10986 | 0.082397 | 0.07782 | 0.07782 | 0.064087 | -0.09613 | 0.14648 | 0.14191 | 0.032043 | 0.032043 | 0.004578 | -0.009155 | -0.054932 | 120.4742 | 120.314 | -0.53558 | 120.52 | 120.488 | 0.17395 | -0.51727 | 120.401 | 120.3552 | -0.58136 | 120.5566 | 120.4422 | 0.086975 | -0.60883 | 120.488 | 120.5063 | 120.4926 | -0.70953 | 120.4422 | 120.4147 | 120.5521 | -0.66834
5455.1875 | 121.3806 | -120.1218 | 0.9613 | -0.012512 | 0.043778 | 0.0599 | 0.0027601 | 0.027406 | -0.010295 | 0.027015 | 0.097962 | 0.012952 | 0.025133 | 0.03557 | 0.0010317 | 0.020309 | 0.027466 | 0.059509 | 0.073242 | 0.027466 | 0.082397 | 0.032043 | -0.10071 | 0.07782 | 0.082397 | 0.013733 | 0.036621 | 0.045776 | -0.022888 | -0.073242 | 120.1538 | 120.0211 | -0.87891 | 120.1813 | 120.1492 | 0.12817 | -0.93384 | 120.0989 | 120.0485 | -0.92468 | 120.1996 | 120.1355 | 0.086975 | -0.91553 | 120.2042 | 120.1492 | 120.195 | -1.062 | 120.1584 | 120.1675 | 120.2042 | -1.0345
5456.8906 | 121.2982 | -120.1035 | 1.0574 | 0.033264 | 0.049118 | 0.059045 | -0.0010851 | 0.026551 | -0.00025418 | 0.029578 | 0.029297 | 0.015088 | 0.024705 | 0.037279 | 0.0038089 | 0.016677 | 0.009155 | -0.054932 | -0.050354 | -0.004578 | 0.1236 | 0.004578 | -0.1236 | 0.027466 | -0.009155 | -0.10986 | 0.073242 | 0.073242 | -0.064087 | -0.10986 | 120.108 | 119.9799 | -0.93384 | 120.0485 | 120.0989 | 0.11902 | -1.0483 | 120.0394 | 119.9936 | -0.98419 | 120.1309 | 119.9936 | 0 | -0.98419 | 120.2271 | 120.1126 | 120.0531 | -1.181 | 120.1767 | 120.1767 | 120.0943 | -1.1673
5458.6406 | 121.4447 | -120.4834 | 0.66834 | 0.063782 | 0.047196 | 0.059259 | 0.0021191 | 0.027619 | -0.0028178 | 0.029151 | 0.13611 | 0.01402 | 0.023424 | 0.037066 | 0.0055179 | 0.016677 | 0.018311 | 0.004578 | -0.013733 | 0.004578 | 0.09613 | 0.013733 | -0.13275 | 0.086975 | 0.036621 | -0.045776 | 0.064087 | 0.041199 | -0.036621 | -0.09613 | 120.4971 | 120.3506 | -0.57221 | 120.488 | 120.488 | 0.13733 | -0.65002 | 120.4468 | 120.3873 | -0.60425 | 120.5704 | 120.4376 | 0.050354 | -0.62714 | 120.5795 | 120.5017 | 120.4697 | -0.80109 | 120.5475 | 120.5246 | 120.52 | -0.76446
5460.3438 | 121.3852 | -120.5658 | 0.69122 | -0.21088 | 0.049118 | 0.060114 | 0.0044691 | 0.026124 | -0.0075174 | 0.027656 | -0.085144 | 0.010602 | 0.022142 | 0.033221 | -0.0011045 | 0.017746 | 0.073242 | 0.13275 | 0.1236 | 0.086975 | 0.082397 | 0.027466 | -0.11444 | 0.12817 | 0.16479 | 0.036621 | 0.041199 | 0.041199 | -0.013733 | -0.082397 | 120.5933 | 120.4514 | -0.60883 | 120.6985 | 120.6528 | 0.20142 | -0.61798 | 120.5521 | 120.4834 | -0.65002 | 120.694 | 120.6024 | 0.11902 | -0.65002 | 120.6482 | 120.639 | 120.6894 | -0.80566 | 120.607 | 120.607 | 120.7306 | -0.77362
5462.125 | 121.4676 | -120.5429 | 0.66376 | 0.0027468 | 0.045914 | 0.060754 | 0.0016919 | 0.027833 | -0.0092264 | 0.026588 | 0.052185 | 0.011884 | 0.02556 | 0.034716 | 0.0020999 | 0.019027 | 0.027466 | 0.054932 | 0.054932 | 0.050354 | 0.09613 | 0.036621 | -0.11902 | 0.07782 | 0.068665 | 0.013733 | 0.045776 | 0.041199 | -0.022888 | -0.10071 | 120.5795 | 120.4239 | -0.56763 | 120.5978 | 120.5933 | 0.16937 | -0.63629 | 120.52 | 120.4422 | -0.61798 | 120.6207 | 120.5566 | 0.11444 | -0.62256 | 120.639 | 120.5704 | 120.5978 | -0.78278 | 120.5887 | 120.5841 | 120.6116 | -0.76447
5463.8281 | 121.4081 | -120.5338 | 0.737 | -0.088806 | 0.049546 | 0.0552 | 0.0042555 | 0.029328 | 0.0020956 | 0.029365 | -0.14618 | 0.015515 | 0.025987 | 0.039202 | 0.0046633 | 0.015182 | 0.10529 | 0.050354 | 0.022888 | 0.041199 | 0.10529 | 0 | -0.14648 | 0.10529 | 0.064087 | -0.050354 | 0.082397 | 0.050354 | -0.041199 | -0.091553 | 120.5338 | 120.3873 | -0.63171 | 120.5841 | 120.575 | 0.18768 | -0.63171 | 120.4926 | 120.4422 | -0.6546 | 120.639 | 120.4834 | 0.041199 | -0.68665 | 120.639 | 120.639 | 120.5566 | -0.88348 | 120.6161 | 120.5841 | 120.5978 | -0.82855
5465.5938 | 121.5271 | -120.6116 | 0.61798 | 0.13245 | 0.047623 | 0.058405 | 0.0029737 | 0.028688 | -0.0045266 | 0.029578 | 0.10559 | 0.013806 | 0.024065 | 0.038561 | 0.0046633 | 0.018814 | 0.09613 | 0.086975 | 0.082397 | 0.064087 | 0.082397 | 0.045776 | -0.10529 | 0.14648 | 0.12817 | 0.032043 | 0.041199 | 0.013733 | -0.018311 | -0.050354 | 120.6573 | 120.5063 | -0.53558 | 120.6985 | 120.6757 | 0.16937 | -0.52185 | 120.5933 | 120.5612 | -0.57678 | 120.7581 | 120.6436 | 0.082397 | -0.60425 | 120.694 | 120.7077 | 120.694 | -0.72327 | 120.6528 | 120.6253 | 120.7397 | -0.66834
5467.2969 | 121.4722 | -120.6345 | 0.65002 | -0.19562 | 0.048264 | 0.057977 | 0.0040417 | 0.027619 | -0.0079446 | 0.027869 | -0.12329 | 0.012952 | 0.023851 | 0.033861 | -0.00067729 | 0.017532 | 0.086975 | 0.1236 | 0.11902 | 0.082397 | 0.068665 | 0.036621 | -0.091553 | 0.1236 | 0.17395 | 0.032043 | 0.032043 | 0.027466 | -0.022888 | -0.082397 | 120.6711 | 120.5429 | -0.58136 | 120.7581 | 120.7169 | 0.17395 | -0.56305 | 120.6116 | 120.5521 | -0.61798 | 120.7581 | 120.6665 | 0.11444 | -0.62256 | 120.7031 | 120.7214 | 120.7535 | -0.74158 | 120.6665 | 120.6619 | 120.8084 | -0.73242
5469.0625 | 120.9915 | -102.8915 | 17.5964 | 0.14771 | 0.046341 | 0.060327 | -0.0017261 | 0.031037 | -0.0030314 | 0.028724 | 0.19714 | 0.013379 | 0.022783 | 0.035784 | 0.0048769 | 0.016037 | 0.10529 | 0.11902 | 0.10071 | 0.082397 | 0.073242 | 0.045776 | -0.10071 | 0.17395 | 0.14191 | 0.036621 | 0.041199 | 0.013733 | -0.009155 | -0.073242 | 102.9373 | 102.7908 | -17.5232 | 103.0106 | 102.9739 | 0.18311 | -17.4912 | 102.8824 | 102.8183 | -17.5552 | 103.0655 | 102.9282 | 0.10986 | -17.5827 | 102.9648 | 102.9968 | 102.9922 | -17.6971 | 102.9327 | 102.9053 | 103.0334 | -17.6697
5470.8281 | 121.2891 | -105.1987 | 15.7516 | -0.11932 | 0.048691 | 0.057123 | -1.7146e-05 | 0.029328 | -0.0017496 | 0.029578 | -0.14618 | 0.014234 | 0.022996 | 0.036638 | 0.0050907 | 0.01625 | 0.07782 | 0.045776 | 0.032043 | 0.041199 | 0.1236 | 0.004578 | -0.15106 | 0.10529 | 0.07782 | -0.050354 | 0.073242 | 0.054932 | -0.045776 | -0.09613 | 105.2032 | 105.0476 | -15.6281 | 105.2444 | 105.2399 | 0.19226 | -15.6738 | 105.1529 | 105.1025 | -15.6784 | 105.304 | 105.1483 | 0.045776 | -15.6967 | 105.3223 | 105.2765 | 105.2307 | -15.9027 | 105.2719 | 105.2536 | 105.2765 | -15.8478
5472.5938 | 121.3943 | -104.6906 | 16.3239 | 0.048523 | 0.043778 | 0.058618 | 0.0027601 | 0.024201 | -0.0090128 | 0.028937 | 0.082703 | 0.011029 | 0.024278 | 0.036211 | 0.0014591 | 0.019668 | 0.045776 | 0.064087 | 0.059509 | 0.027466 | 0.091553 | 0.036621 | -0.09613 | 0.09613 | 0.091553 | 0 | 0.041199 | 0.022888 | -0.022888 | -0.091553 | 104.7272 | 104.5944 | -16.2323 | 104.7546 | 104.718 | 0.1236 | -16.2781 | 104.6677 | 104.599 | -16.2827 | 104.7867 | 104.6906 | 0.091553 | -16.301 | 104.7821 | 104.7363 | 104.7501 | -16.42 | 104.7318 | 104.7134 | 104.7821 | -16.4154
5474.3594 | 121.4813 | -104.1275 | 16.9373 | 0.0027468 | 0.046768 | 0.061823 | 0.0055371 | 0.026551 | -0.0092264 | 0.025519 | 0.029297 | 0.012311 | 0.025346 | 0.035143 | -0.0013181 | 0.018814 | 0.027466 | 0.050354 | 0.059509 | 0.036621 | 0.091553 | 0.054932 | -0.10986 | 0.10071 | 0.09613 | 0.004578 | 0.050354 | 0.041199 | -0.018311 | -0.086975 | 104.1824 | 104.0176 | -16.8457 | 104.1779 | 104.1641 | 0.14648 | -16.9098 | 104.1092 | 104.0405 | -16.8869 | 104.2282 | 104.1321 | 0.091553 | -16.8961 | 104.2191 | 104.155 | 104.187 | -17.0471 | 104.1779 | 104.1687 | 104.2236 | -17.0242
5476.125 | 121.4035 | -104.6173 | 16.571 | -0.21088 | 0.047409 | 0.058832 | 0.0036145 | 0.026551 | -0.0038858 | 0.027656 | -0.26062 | 0.013166 | 0.024919 | 0.035357 | 0.0014591 | 0.016464 | 0.018311 | 0.009155 | -0.013733 | -0.018311 | 0.11902 | -0.004578 | -0.16479 | 0.018311 | 0.036621 | -0.07782 | 0.073242 | 0.073242 | -0.068665 | -0.09613 | 104.6127 | 104.4525 | -16.452 | 104.6265 | 104.599 | 0.14648 | -16.5527 | 104.5486 | 104.5212 | -16.4978 | 104.6356 | 104.5395 | 0.01831 | -16.4978 | 104.7363 | 104.6356 | 104.6036 | -16.7358 | 104.6906 | 104.6906 | 104.6539 | -16.6672
5477.8438 | 121.5225 | -105.0659 | 16.0629 | -0.14221 | 0.047196 | 0.063532 | 0.00083745 | 0.029328 | -0.0075174 | 0.027015 | -0.13855 | 0.011243 | 0.024065 | 0.03557 | 0.00017731 | 0.0186 | 0.1236 | 0.18768 | 0.14191 | 0.086975 | 0.07782 | 0.045776 | -0.10071 | 0.15106 | 0.18768 | 0.050354 | 0.027466 | 0.004578 | -0.032043 | -0.064087 | 105.1117 | 104.9652 | -15.9851 | 105.2536 | 105.1529 | 0.18768 | -15.9393 | 105.0339 | 105.0018 | -16.0355 | 105.217 | 105.1163 | 0.11444 | -16.0583 | 105.1437 | 105.1895 | 105.2078 | -16.1636 | 105.0934 | 105.0705 | 105.2536 | -16.127
5479.6094 | 121.5637 | -105.5923 | 15.6006 | -0.0048827 | 0.046768 | 0.056696 | 0.0051099 | 0.028688 | -0.0045266 | 0.027656 | 0.021668 | 0.011029 | 0.025346 | 0.034929 | 0.0014591 | 0.017746 | 0.027466 | 0.054932 | 0.059509 | 0.032043 | 0.086975 | 0.022888 | -0.11444 | 0.11444 | 0.09613 | 0.018311 | 0.036621 | 0.045776 | 0.004578 | -0.086975 | 105.6152 | 105.4779 | -15.5136 | 105.6473 | 105.6244 | 0.14648 | -15.5731 | 105.5969 | 105.5054 | -15.564 | 105.7068 | 105.6107 | 0.10529 | -15.5548 | 105.6793 | 105.6198 | 105.6519 | -15.715 | 105.629 | 105.6381 | 105.6885 | -15.6876
5481.375 | 121.463 | -104.9561 | 16.3055 | -0.15747 | 0.048477 | 0.059473 | 0.0046827 | 0.028901 | -0.003245 | 0.026588 | -0.15381 | 0.012738 | 0.024705 | 0.035357 | 0.0016727 | 0.016464 | 0.091553 | 0.1236 | 0.10986 | 0.07782 | 0.086975 | 0.050354 | -0.10071 | 0.13275 | 0.14648 | 0.032043 | 0.036621 | 0.041199 | -0.032043 | -0.068665 | 105.0064 | 104.8553 | -16.2186 | 105.0797 | 105.0339 | 0.17853 | -16.214 | 104.924 | 104.8874 | -16.2689 | 105.0888 | 104.9881 | 0.10071 | -16.2643 | 105.043 | 105.0476 | 105.0659 | -16.4062 | 104.9927 | 104.9973 | 105.1025 | -16.3742
5483.1562 | 121.582 | -104.1 | 17.1249 | -0.15747 | 0.047837 | 0.061182 | 0.0025465 | 0.028688 | -0.006663 | 0.025306 | -0.1004 | 0.011457 | 0.024278 | 0.035784 | -0.00024989 | 0.016037 | 0.11902 | 0.15564 | 0.12817 | 0.086975 | 0.082397 | 0.041199 | -0.091553 | 0.16937 | 0.17395 | 0.059509 | 0.036621 | 0.013733 | -0.022888 | -0.091553 | 104.1412 | 104.0085 | -17.0425 | 104.2557 | 104.187 | 0.17853 | -17.0059 | 104.0771 | 104.0085 | -17.0883 | 104.2694 | 104.1595 | 0.15106 | -17.1112 | 104.1824 | 104.2191 | 104.2282 | -17.2165 | 104.1367 | 104.1138 | 104.274 | -17.2165
5484.8594 | 121.55 | -102.626 | 18.5852 | 0.16296 | 0.045914 | 0.059045 | -0.0025805 | 0.028688 | -0.0019632 | 0.027015 | 0.13611 | 0.011243 | 0.023424 | 0.035998 | 0.0053043 | 0.019027 | 0.1236 | 0.13275 | 0.10071 | 0.082397 | 0.068665 | 0.054932 | -0.082397 | 0.18768 | 0.13275 | 0.036621 | 0.032043 | 0.036621 | -0.022888 | -0.091553 | 102.681 | 102.5436 | -18.5165 | 102.7588 | 102.7084 | 0.16479 | -18.4616 | 102.6031 | 102.5345 | -18.5532 | 102.8137 | 102.6627 | 0.12817 | -18.5486 | 102.6947 | 102.7496 | 102.7267 | -18.6676 | 102.6581 | 102.6627 | 102.7588 | -18.6768
5486.625 | 121.2021 | -16.9327 | 104.5166 | -0.19562 | 0.049546 | 0.059686 | 0.0036145 | 0.028901 | -0.0045266 | 0.028937 | -0.16907 | 0.01402 | 0.025346 | 0.034502 | 0.0038089 | 0.016464 | 0.09613 | 0.12817 | 0.10529 | 0.082397 | 0.082397 | 0.032043 | -0.10986 | 0.13275 | 0.15564 | 0.018311 | 0.050354 | 0.041199 | -0.018311 | -0.086975 | 16.9647 | 16.8228 | -104.4342 | 17.0609 | 17.0151 | 0.19226 | -104.4205 | 16.9144 | 16.8457 | -104.4662 | 17.0654 | 16.951 | 0.10529 | -104.4754 | 17.0151 | 17.0288 | 17.038 | -104.6265 | 16.983 | 16.9739 | 17.0883 | -104.6036
5488.3906 | 120.9183 | -10.6064 | 110.8383 | -0.11169 | 0.048264 | 0.05755 | 0.00041005 | 0.027833 | 0.0029502 | 0.031287 | -0.20721 | 0.01402 | 0.022783 | 0.037279 | 0.0057315 | 0.0139 | 0.082397 | 0.050354 | 0.004578 | 0.032043 | 0.11444 | 0.018311 | -0.13733 | 0.11902 | 0.07782 | -0.059509 | 0.073242 | 0.050354 | -0.041199 | -0.086975 | 10.6247 | 10.4691 | -110.7239 | 10.6567 | 10.6384 | 0.16937 | -110.7559 | 10.5652 | 10.5194 | -110.7651 | 10.7254 | 10.5469 | 0.027466 | -110.788 | 10.7208 | 10.6888 | 10.611 | -110.9756 | 10.6796 | 10.6567 | 10.6842 | -110.9253
5490.1562 | 121.3394 | -9.4849 | 111.9278 | -0.11932 | 0.050186 | 0.058618 | 0.0023329 | 0.026765 | 0.00081382 | 0.030006 | -0.19196 | 0.012525 | 0.023424 | 0.035143 | 0.0042361 | 0.016464 | 0.064087 | 0.059509 | 0.022888 | 0.022888 | 0.10529 | 0.009155 | -0.15106 | 0.086975 | 0.07782 | -0.050354 | 0.068665 | 0.041199 | -0.036621 | -0.10071 | 9.494 | 9.3338 | -111.8225 | 9.5444 | 9.5078 | 0.17395 | -111.8637 | 9.4482 | 9.3842 | -111.8591 | 9.5718 | 9.4345 | 0.050354 | -111.8866 | 9.5901 | 9.549 | 9.5078 | -112.0789 | 9.5535 | 9.5261 | 9.5627 | -112.0285
5491.8594 | 121.4996 | -9.0775 | 112.3718 | -0.15747 | 0.050186 | 0.05755 | 0.0048963 | 0.029328 | 0.00081382 | 0.031714 | -0.16144 | 0.015088 | 0.026201 | 0.037707 | 0.0046633 | 0.017318 | 0.041199 | 0.059509 | 0.022888 | 0.041199 | 0.09613 | -0.004578 | -0.15106 | 0.07782 | 0.086975 | -0.041199 | 0.050354 | 0.068665 | -0.036621 | -0.10986 | 9.0729 | 8.9264 | -112.2757 | 9.137 | 9.1187 | 0.19226 | -112.3306 | 9.0408 | 8.9676 | -112.3215 | 9.1553 | 9.0363 | 0.068664 | -112.3032 | 9.1736 | 9.1187 | 9.1003 | -112.5229 | 9.1278 | 9.1461 | 9.1644 | -112.4817
5493.6094 | 121.4722 | -8.7891 | 112.6785 | -0.27954 | 0.047196 | 0.059473 | 0.0053235 | 0.026979 | -0.0085856 | 0.027869 | -0.19196 | 0.014661 | 0.023424 | 0.034289 | 0.0018863 | 0.019882 | 0.032043 | 0.082397 | 0.050354 | 0.050354 | 0.07782 | 0 | -0.11902 | 0.041199 | 0.091553 | -0.054932 | 0.059509 | 0.050354 | -0.050354 | -0.10986 | 8.7891 | 8.67 | -112.6007 | 8.8715 | 8.8394 | 0.16937 | -112.6465 | 8.7387 | 8.6792 | -112.619 | 8.8303 | 8.7341 | 0.054931 | -112.6282 | 8.8669 | 8.8211 | 8.8394 | -112.7975 | 8.8486 | 8.8394 | 8.8806 | -112.7884
5495.3906 | 121.5958 | -9.4711 | 111.9598 | 0.13245 | 0.050186 | 0.057123 | 0.00062385 | 0.025697 | -0.0028178 | 0.028724 | 0.097962 | 0.01402 | 0.023851 | 0.035998 | 0.0027407 | 0.0186 | 0.082397 | 0.086975 | 0.073242 | 0.068665 | 0.073242 | 0.050354 | -0.09613 | 0.13733 | 0.14191 | 0.036621 | 0.018311 | 0.027466 | -0.013733 | -0.073242 | 9.5215 | 9.375 | -111.8866 | 9.5581 | 9.5398 | 0.16479 | -111.8774 | 9.4574 | 9.3979 | -111.9415 | 9.6085 | 9.5078 | 0.10986 | -111.9324 | 9.5444 | 9.5535 | 9.5444 | -112.056 | 9.4894 | 9.4986 | 9.613 | -112.0331
5497.0938 | 121.5912 | -8.8028 | 112.619 | 0.079041 | 0.050614 | 0.060968 | 0.0016919 | 0.031037 | -0.001536 | 0.028724 | 0.036926 | 0.01637 | 0.022356 | 0.036425 | 0.0035953 | 0.018386 | 0.013733 | -0.004578 | -0.022888 | 0.004578 | 0.10529 | 0.013733 | -0.13275 | 0.050354 | 0 | -0.07782 | 0.07782 | 0.027466 | -0.041199 | -0.10071 | 8.8165 | 8.67 | -112.5137 | 8.7982 | 8.8074 | 0.13733 | -112.6053 | 8.7616 | 8.7021 | -112.5412 | 8.8531 | 8.725 | 0.022888 | -112.5916 | 8.9081 | 8.8165 | 8.7799 | -112.7518 | 8.8806 | 8.8303 | 8.8028 | -112.7197
5498.8594 | 121.582 | -8.67 | 112.793 | 0.10956 | 0.046982 | 0.059259 | 0.0027601 | 0.027192 | -0.0064492 | 0.030006 | 0.12085 | 0.013166 | 0.025133 | 0.034716 | 0.00017731 | 0.019241 | 0.082397 | 0.11902 | 0.10529 | 0.068665 | 0.059509 | 0.036621 | -0.10986 | 0.14191 | 0.13275 | 0.045776 | 0.027466 | 0.013733 | -0.027466 | -0.073242 | 8.7067 | 8.5602 | -112.7335 | 8.7891 | 8.7387 | 0.17853 | -112.7106 | 8.6426 | 8.5968 | -112.7655 | 8.812 | 8.7158 | 0.11902 | -112.7792 | 8.7296 | 8.7524 | 8.7753 | -112.9028 | 8.6975 | 8.6838 | 8.8028 | -112.8662
5500.625 | 121.6507 | -8.4274 | 113.0127 | 0.12482 | 0.052323 | 0.059259 | 0.0029737 | 0.029969 | -0.0017496 | 0.030646 | 0.15137 | 0.01402 | 0.025987 | 0.038775 | 0.0027407 | 0.01625 | 0.027466 | 0.022888 | 0.004578 | 0.013733 | 0.09613 | 0.041199 | -0.11444 | 0.11444 | 0.086975 | 0 | 0.036621 | 0.045776 | -0.032043 | -0.073242 | 8.4686 | 8.313 | -112.9166 | 8.4503 | 8.4412 | 0.12817 | -112.9852 | 8.3954 | 8.3542 | -112.9761 | 8.5419 | 8.4274 | 0.073242 | -112.9669 | 8.5236 | 8.4549 | 8.432 | -113.1271 | 8.4641 | 8.4732 | 8.5144 | -113.0859
5502.3906 | 121.6324 | -8.4503 | 112.999 | 0.14008 | 0.046768 | 0.058832 | 0.0036145 | 0.028047 | -0.0045266 | 0.030646 | 0.12848 | 0.014875 | 0.023851 | 0.036211 | 0.0023135 | 0.017318 | 0.086975 | 0.11444 | 0.10071 | 0.07782 | 0.07782 | 0.027466 | -0.073242 | 0.14648 | 0.13733 | 0.045776 | 0.032043 | 0.022888 | -0.022888 | -0.064087 | 8.4778 | 8.3771 | -112.9211 | 8.5648 | 8.5281 | 0.15106 | -112.912 | 8.4274 | 8.3862 | -112.9669 | 8.5968 | 8.4961 | 0.10986 | -112.9761 | 8.5281 | 8.5373 | 8.551 | -113.0722 | 8.4824 | 8.4732 | 8.5876 | -113.063
5504.1562 | 121.582 | -8.1894 | 113.3469 | -0.22614 | 0.049332 | 0.059045 | 0.0063917 | 0.029115 | -0.0040994 | 0.029792 | -0.25299 | 0.014875 | 0.027055 | 0.035357 | -0.0017453 | 0.016891 | 0.004578 | 0 | -0.022888 | -0.009155 | 0.09613 | -0.009155 | -0.16022 | 0.027466 | 0.022888 | -0.10071 | 0.082397 | 0.073242 | -0.073242 | -0.11902 | 8.1802 | 8.0292 | -113.2507 | 8.1894 | 8.1802 | 0.15106 | -113.3423 | 8.1161 | 8.0704 | -113.2645 | 8.2169 | 8.0887 | 0.018311 | -113.2736 | 8.2855 | 8.194 | 8.1665 | -113.5071 | 8.2718 | 8.2626 | 8.2123 | -113.4659
5505.8594 | 121.7056 | -8.1345 | 113.3194 | -0.0048827 | 0.047196 | 0.059686 | 0.0029737 | 0.026979 | -0.0079446 | 0.027656 | 0.021668 | 0.013593 | 0.023851 | 0.034289 | 0.00039091 | 0.0186 | 0.013733 | 0.050354 | 0.064087 | 0.027466 | 0.086975 | 0.027466 | -0.13275 | 0.10986 | 0.091553 | 0.018311 | 0.059509 | 0.041199 | -0.036621 | -0.073242 | 8.1619 | 8.0017 | -113.2324 | 8.1848 | 8.1619 | 0.16022 | -113.3057 | 8.0978 | 8.0612 | -113.2599 | 8.2443 | 8.1528 | 0.091553 | -113.2782 | 8.2214 | 8.1482 | 8.1985 | -113.4521 | 8.194 | 8.1757 | 8.226 | -113.3926
5507.625 | 121.5958 | -7.9376 | 113.5849 | 0.040894 | 0.050614 | 0.057336 | -0.00023075 | 0.030824 | 0.0023092 | 0.029365 | -0.031738 | 0.014234 | 0.024065 | 0.036638 | 0.0059451 | 0.014541 | 0.013733 | -0.045776 | -0.050354 | -0.009155 | 0.10529 | 0.013733 | -0.15106 | 0.004578 | -0.013733 | -0.1236 | 0.064087 | 0.050354 | -0.050354 | -0.11444 | 7.9514 | 7.7866 | -113.4796 | 7.8918 | 7.9285 | 0.14191 | -113.5712 | 7.8873 | 7.8232 | -113.5208 | 7.9422 | 7.814 | -0.009155 | -113.5345 | 8.0429 | 7.9514 | 7.8873 | -113.736 | 8.0017 | 7.988 | 7.9239 | -113.6993
5509.3281 | 121.6095 | -7.8049 | 113.7497 | -0.19562 | 0.049546 | 0.058832 | 0.0066053 | 0.026765 | -0.0070902 | 0.029365 | -0.13092 | 0.012525 | 0.024065 | 0.037279 | 0.00060451 | 0.017105 | 0.082397 | 0.11444 | 0.10529 | 0.068665 | 0.054932 | 0.032043 | -0.10529 | 0.1236 | 0.17853 | 0.041199 | 0.041199 | 0.027466 | -0.022888 | -0.073242 | 7.8369 | 7.6996 | -113.6948 | 7.9193 | 7.8735 | 0.17395 | -113.6673 | 7.782 | 7.7316 | -113.7085 | 7.9285 | 7.8461 | 0.11444 | -113.7222 | 7.8598 | 7.8873 | 7.9102 | -113.855 | 7.8461 | 7.8323 | 7.9834 | -113.8229
5511.1094 | 121.6003 | -7.7408 | 113.8687 | -0.18036 | 0.0504 | 0.062036 | 0.0029737 | 0.028047 | -0.0055948 | 0.028083 | -0.20721 | 0.010602 | 0.024492 | 0.033861 | 0.0016727 | 0.015396 | 0.068665 | 0.11902 | 0.091553 | 0.059509 | 0.07782 | 0.032043 | -0.11444 | 0.09613 | 0.13733 | 0.004578 | 0.054932 | 0.032043 | -0.036621 | -0.091553 | 7.7728 | 7.6263 | -113.7909 | 7.8598 | 7.8003 | 0.17395 | -113.8 | 7.7042 | 7.6492 | -113.8138 | 7.8369 | 7.7454 | 0.096131 | -113.8367 | 7.8186 | 7.8094 | 7.8323 | -113.9832 | 7.7957 | 7.7728 | 7.8781 | -113.9603
5512.8125 | 121.7514 | -7.6859 | 113.7955 | -0.012512 | 0.044419 | 0.062891 | 0.0029737 | 0.026551 | -0.0064492 | 0.026374 | -0.016479 | 0.010388 | 0.023637 | 0.035784 | -0.00024989 | 0.017532 | 0.027466 | 0.073242 | 0.050354 | 0.041199 | 0.09613 | 0.032043 | -0.11902 | 0.10071 | 0.11902 | 0.036621 | 0.045776 | 0.013733 | -0.032043 | -0.086975 | 7.7179 | 7.5668 | -113.6993 | 7.7591 | 7.7271 | 0.16022 | -113.768 | 7.6538 | 7.5989 | -113.7497 | 7.7866 | 7.7225 | 0.1236 | -113.7817 | 7.782 | 7.7133 | 7.7362 | -113.9145 | 7.7316 | 7.6996 | 7.8049 | -113.8824
5514.5781 | 121.6324 | -7.5943 | 114.0335 | -0.18799 | 0.050827 | 0.058191 | 0.0063917 | 0.027406 | -0.0038858 | 0.025947 | -0.26062 | 0.012525 | 0.023851 | 0.03557 | 0.00060451 | 0.014755 | 0.073242 | 0.10986 | 0.07782 | 0.068665 | 0.07782 | 0.018311 | -0.1236 | 0.086975 | 0.10986 | 0 | 0.054932 | 0.045776 | -0.041199 | -0.09613 | 7.6126 | 7.4707 | -113.9557 | 7.7042 | 7.663 | 0.19226 | -113.9603 | 7.5531 | 7.4982 | -113.9786 | 7.6813 | 7.5943 | 0.09613 | -113.9877 | 7.6721 | 7.6675 | 7.6721 | -114.1571 | 7.6492 | 7.6401 | 7.7042 | -114.1296
5516.3438 | 121.637 | -7.4799 | 114.1113 | -0.096436 | 0.050186 | 0.0599 | 0.0019055 | 0.027833 | 0.0027364 | 0.027869 | -0.15381 | 0.014661 | 0.025987 | 0.036425 | 0.0033817 | 0.0139 | 0.091553 | 0.073242 | 0.022888 | 0.027466 | 0.1236 | 0.004578 | -0.13733 | 0.09613 | 0.073242 | -0.082397 | 0.073242 | 0.045776 | -0.050354 | -0.10986 | 7.4844 | 7.3425 | -113.9877 | 7.5531 | 7.5073 | 0.16479 | -114.0198 | 7.4295 | 7.37 | -114.0381 | 7.576 | 7.3975 | 0.027466 | -114.0656 | 7.6035 | 7.5714 | 7.5027 | -114.2487 | 7.5531 | 7.5256 | 7.5531 | -114.2212
5518.1094 | 121.6965 | -7.4158 | 114.1251 | -0.21851 | 0.04805 | 0.060327 | 0.0027601 | 0.027619 | -0.0064492 | 0.028724 | -0.14618 | 0.01167 | 0.024278 | 0.035784 | -3.629e-05 | 0.017959 | 0.086975 | 0.15564 | 0.12817 | 0.086975 | 0.050354 | 0.045776 | -0.091553 | 0.13733 | 0.16022 | 0.045776 | 0.041199 | 0.022888 | -0.032043 | -0.073242 | 7.4615 | 7.3242 | -114.0747 | 7.5714 | 7.5027 | 0.17853 | -114.0381 | 7.3837 | 7.3425 | -114.0839 | 7.5531 | 7.4615 | 0.11902 | -114.1022 | 7.4661 | 7.5027 | 7.5439 | -114.2166 | 7.457 | 7.4387 | 7.576 | -114.1983
5519.875 | 121.6919 | -7.3975 | 114.2075 | -0.20325 | 0.050186 | 0.061823 | 0.0031873 | 0.027833 | -0.0055948 | 0.026801 | -0.12329 | 0.010602 | 0.024919 | 0.034289 | 0.0014591 | 0.015396 | 0.082397 | 0.15106 | 0.11902 | 0.073242 | 0.091553 | 0.032043 | -0.09613 | 0.13733 | 0.16479 | 0.050354 | 0.022888 | 0.018311 | -0.018311 | -0.086975 | 7.4295 | 7.3013 | -114.1159 | 7.5485 | 7.4707 | 0.16937 | -114.1251 | 7.3792 | 7.3105 | -114.1846 | 7.5348 | 7.4478 | 0.13733 | -114.1891 | 7.489 | 7.4799 | 7.5165 | -114.3036 | 7.4203 | 7.4158 | 7.5623 | -114.2944
5521.6562 | 121.0968 | -5.0446 | 115.9241 | 0.14771 | 0.048905 | 0.05755 | 0.0014783 | 0.029115 | -0.0062356 | 0.028724 | 0.12085 | 0.01402 | 0.023851 | 0.032366 | 0.0040225 | 0.017105 | 0.10071 | 0.10986 | 0.11444 | 0.082397 | 0.054932 | 0.045776 | -0.10071 | 0.15564 | 0.15106 | 0.036621 | 0.004578 | -0.004578 | -0.004578 | -0.064087 | 5.0903 | 4.9438 | -115.8691 | 5.1544 | 5.127 | 0.18311 | -115.8234 | 5.04 | 4.9805 | -115.9195 | 5.2002 | 5.0812 | 0.10071 | -115.9286 | 5.0995 | 5.1453 | 5.159 | -116.0248 | 5.0491 | 5.04 | 5.1956 | -115.9882
5523.4219 | 121.3486 | -3.772 | 117.4118 | 0.12482 | 0.049759 | 0.057977 | 0.0027601 | 0.027619 | -0.0017496 | 0.028297 | 0.13611 | 0.013593 | 0.024278 | 0.035998 | 0.0031681 | 0.017105 | 0.11444 | 0.10986 | 0.09613 | 0.073242 | 0.073242 | 0.045776 | -0.09613 | 0.15106 | 0.1236 | 0.045776 | 0.050354 | 0.018311 | -0.022888 | -0.059509 | 3.8177 | 3.6758 | -117.3386 | 3.8818 | 3.8452 | 0.16937 | -117.2974 | 3.7491 | 3.7125 | -117.3615 | 3.923 | 3.8177 | 0.10528 | -117.3935 | 3.8452 | 3.8864 | 3.8681 | -117.5079 | 3.8223 | 3.7903 | 3.8956 | -117.4713
5525.1875 | 121.3577 | -3.7537 | 117.5858 | -0.11932 | 0.051895 | 0.057977 | 0.0025465 | 0.027619 | 0.00038662 | 0.028724 | -0.18433 | 0.016584 | 0.02321 | 0.035784 | 0.0035953 | 0.017532 | 0.064087 | 0.045776 | 0.009155 | 0.027466 | 0.10529 | 0.004578 | -0.14191 | 0.09613 | 0.073242 | -0.045776 | 0.064087 | 0.059509 | -0.032043 | -0.10986 | 3.7582 | 3.6118 | -117.4805 | 3.7994 | 3.7811 | 0.16937 | -117.5217 | 3.7216 | 3.6438 | -117.5217 | 3.8498 | 3.7079 | 0.064087 | -117.5262 | 3.8589 | 3.8177 | 3.7628 | -117.7277 | 3.8177 | 3.8132 | 3.8269 | -117.6956
5526.9531 | 121.4584 | -4.2709 | 117.0731 | 0.071411 | 0.048477 | 0.0599 | 0.0014783 | 0.028047 | -0.004954 | 0.030433 | 0.15137 | 0.013166 | 0.021928 | 0.037066 | -0.00089089 | 0.019455 | 0.082397 | 0.11444 | 0.091553 | 0.064087 | 0.064087 | 0.041199 | -0.10986 | 0.14191 | 0.11444 | 0.018311 | 0.036621 | 0.022888 | -0.036621 | -0.07782 | 4.3121 | 4.1611 | -117.009 | 4.3854 | 4.335 | 0.17395 | -116.9907 | 4.2343 | 4.1931 | -117.0364 | 4.4128 | 4.2892 | 0.096131 | -117.0502 | 4.335 | 4.3533 | 4.3625 | -117.1829 | 4.3076 | 4.2938 | 4.3854 | -117.1509
5528.6562 | 121.4035 | -4.0237 | 117.4393 | -0.088806 | 0.048477 | 0.058405 | 0.0038281 | 0.028688 | 0.00017302 | 0.028937 | -0.11566 | 0.015943 | 0.022356 | 0.037279 | 0.0038089 | 0.015609 | 0.082397 | 0.041199 | 0.027466 | 0.041199 | 0.10986 | 0.022888 | -0.14648 | 0.073242 | 0.059509 | -0.064087 | 0.059509 | 0.050354 | -0.041199 | -0.11444 | 4.0466 | 3.8773 | -117.3294 | 4.0649 | 4.0649 | 0.18768 | -117.3569 | 3.9825 | 3.9093 | -117.3798 | 4.097 | 3.9597 | 0.050354 | -117.3889 | 4.1336 | 4.1061 | 4.0512 | -117.5858 | 4.0833 | 4.0741 | 4.0833 | -117.5537
5530.4062 | 121.5454 | -3.7949 | 117.5949 | 0.094299 | 0.049759 | 0.057336 | 0.00062385 | 0.026338 | -0.0013224 | 0.030219 | 0.036926 | 0.01402 | 0.024278 | 0.036638 | 0.0057315 | 0.018173 | 0.013733 | -0.013733 | -0.036621 | -0.004578 | 0.11902 | 0.013733 | -0.12817 | 0.045776 | 0 | -0.068665 | 0.041199 | 0.041199 | -0.054932 | -0.09613 | 3.8086 | 3.6667 | -117.4759 | 3.7811 | 3.7903 | 0.1236 | -117.5812 | 3.7399 | 3.6987 | -117.5537 | 3.8406 | 3.7262 | 0.027465 | -117.5537 | 3.9139 | 3.8086 | 3.7582 | -117.7231 | 3.8361 | 3.8361 | 3.7949 | -117.691
5532.1719 | 121.6278 | -3.392 | 118.0161 | -0.073547 | 0.047837 | 0.060541 | 0.0046827 | 0.026551 | -0.0092264 | 0.027442 | -0.062256 | 0.010388 | 0.023637 | 0.035784 | -0.00067729 | 0.019455 | 0.045776 | 0.09613 | 0.082397 | 0.041199 | 0.073242 | 0.041199 | -0.13275 | 0.13275 | 0.16937 | 0.064087 | 0.041199 | 0.018311 | -0.041199 | -0.068665 | 3.4332 | 3.2593 | -117.9428 | 3.4882 | 3.4332 | 0.17395 | -117.9703 | 3.3508 | 3.3234 | -117.9749 | 3.5248 | 3.4561 | 0.13275 | -117.9977 | 3.4653 | 3.4378 | 3.4744 | -118.1488 | 3.4332 | 3.4103 | 3.5614 | -118.0847
5533.9375 | 121.5454 | -3.3829 | 118.1213 | -0.23376 | 0.052323 | 0.0599 | 0.0068189 | 0.026551 | -0.0011088 | 0.025733 | -0.22247 | 0.014234 | 0.026628 | 0.036425 | 0.0016727 | 0.016037 | 0 | -0.009155 | -0.036621 | 0.009155 | 0.10986 | -0.013733 | -0.16022 | 0.036621 | 0.027466 | -0.07782 | 0.073242 | 0.07782 | -0.059509 | -0.11444 | 3.3691 | 3.2227 | -118.0115 | 3.3737 | 3.392 | 0.16937 | -118.1213 | 3.3234 | 3.2684 | -118.0481 | 3.4195 | 3.3051 | 0.036621 | -118.0435 | 3.4927 | 3.3829 | 3.3463 | -118.2816 | 3.4561 | 3.4607 | 3.4103 | -118.2358
5535.6875 | 121.5088 | -3.2913 | 118.2678 | -0.096436 | 0.053604 | 0.056909 | 0.0070325 | 0.026124 | -0.00025418 | 0.030433 | -0.12329 | 0.015302 | 0.027269 | 0.036638 | 0.0014591 | 0.016037 | 0.073242 | 0.045776 | 0.022888 | 0.022888 | 0.11444 | 0.013733 | -0.13733 | 0.068665 | 0.064087 | -0.064087 | 0.068665 | 0.036621 | -0.045776 | -0.11444 | 3.3051 | 3.154 | -118.1534 | 3.3371 | 3.3142 | 0.16022 | -118.1946 | 3.2455 | 3.1769 | -118.1992 | 3.36 | 3.2272 | 0.050354 | -118.2312 | 3.4058 | 3.3646 | 3.3142 | -118.4052 | 3.36 | 3.3279 | 3.3554 | -118.3823
5537.3906 | 121.637 | -3.2364 | 118.277 | -0.17273 | 0.049332 | 0.059473 | 0.0046827 | 0.028688 | -0.006663 | 0.026588 | -0.13092 | 0.010602 | 0.02556 | 0.038347 | -0.0023861 | 0.017959 | 0.073242 | 0.14191 | 0.11902 | 0.07782 | 0.073242 | 0.041199 | -0.11902 | 0.13275 | 0.18768 | 0.07782 | 0.032043 | 0.018311 | -0.018311 | -0.073242 | 3.2776 | 3.1174 | -118.2037 | 3.3783 | 3.3142 | 0.19684 | -118.2037 | 3.2181 | 3.1631 | -118.2449 | 3.3691 | 3.3142 | 0.15106 | -118.2587 | 3.3096 | 3.3096 | 3.3554 | -118.396 | 3.2684 | 3.2547 | 3.4241 | -118.3502
5539.1562 | 121.5637 | -3.1952 | 118.3502 | 0.063782 | 0.051041 | 0.058618 | -0.0012987 | 0.025056 | -0.0017496 | 0.030006 | -0.031738 | 0.015302 | 0.022569 | 0.037707 | 0.0067997 | 0.016891 | 0 | -0.045776 | -0.045776 | -0.018311 | 0.1236 | -0.009155 | -0.14191 | 0 | -0.009155 | -0.1236 | 0.073242 | 0.073242 | -0.054932 | -0.12817 | 3.186 | 3.0533 | -118.2266 | 3.1494 | 3.1769 | 0.1236 | -118.3502 | 3.1403 | 3.067 | -118.277 | 3.1952 | 3.0716 | 0.004578 | -118.277 | 3.3188 | 3.1952 | 3.1494 | -118.4921 | 3.2684 | 3.2684 | 3.186 | -118.4784
5540.8594 | 121.7239 | -3.1448 | 118.3456 | -0.058289 | 0.048477 | 0.059686 | 0.0070325 | 0.02826 | -0.010935 | 0.030006 | -0.024109 | 0.01167 | 0.024705 | 0.036425 | -0.0028135 | 0.019027 | 0.050354 | 0.10986 | 0.10071 | 0.068665 | 0.068665 | 0.036621 | -0.10529 | 0.13275 | 0.17395 | 0.050354 | 0.041199 | 0.032043 | -0.027466 | -0.086975 | 3.1815 | 3.0396 | -118.277 | 3.2547 | 3.2135 | 0.17395 | -118.2953 | 3.1174 | 3.0579 | -118.3044 | 3.2776 | 3.1952 | 0.13733 | -118.3136 | 3.2135 | 3.1952 | 3.2455 | -118.4509 | 3.186 | 3.1769 | 3.3188 | -118.4326
5542.6562 | 121.6599 | -3.3646 | 118.19 | 0.11719 | 0.052323 | 0.060114 | 0.00083745 | 0.026338 | -0.0017496 | 0.028724 | 0.059815 | 0.014234 | 0.021928 | 0.03792 | 0.0063723 | 0.017318 | 0.009155 | -0.032043 | -0.054932 | -0.018311 | 0.11902 | 0.004578 | -0.14191 | 0.041199 | -0.004578 | -0.09613 | 0.045776 | 0.064087 | -0.041199 | -0.10986 | 3.3691 | 3.2227 | -118.071 | 3.3325 | 3.3463 | 0.1236 | -118.1808 | 3.3234 | 3.2547 | -118.1442 | 3.4058 | 3.2684 | 0.013733 | -118.1259 | 3.4836 | 3.3737 | 3.3096 | -118.3319 | 3.4103 | 3.4287 | 3.36 | -118.2999
5544.3594 | 121.6232 | -3.4012 | 118.2083 | -0.27954 | 0.047196 | 0.059259 | 0.0061781 | 0.029328 | -0.006663 | 0.027228 | -0.22247 | 0.012311 | 0.025346 | 0.034502 | 0.00081811 | 0.017959 | 0.032043 | 0.082397 | 0.050354 | 0.041199 | 0.09613 | 0.009155 | -0.13275 | 0.050354 | 0.059509 | -0.059509 | 0.073242 | 0.073242 | -0.054932 | -0.11444 | 3.4103 | 3.2684 | -118.1122 | 3.4836 | 3.4424 | 0.17395 | -118.1763 | 3.3463 | 3.2867 | -118.1351 | 3.4515 | 3.3417 | 0.054932 | -118.1351 | 3.4973 | 3.4332 | 3.4515 | -118.3411 | 3.4744 | 3.4744 | 3.4607 | -118.3228
5546.125 | 121.6415 | -3.392 | 118.2404 | -0.11169 | 0.052536 | 0.058618 | 0.0038281 | 0.027192 | 0.00060022 | 0.030006 | -0.13855 | 0.014661 | 0.025987 | 0.03792 | 0.0040225 | 0.016037 | 0.050354 | 0.041199 | 0.027466 | 0.032043 | 0.10529 | 0.009155 | -0.13733 | 0.073242 | 0.091553 | -0.054932 | 0.064087 | 0.045776 | -0.054932 | -0.10071 | 3.4012 | 3.2547 | -118.1351 | 3.4332 | 3.4241 | 0.16937 | -118.19 | 3.3371 | 3.2913 | -118.1763 | 3.4653 | 3.3371 | 0.045776 | -118.1946 | 3.4973 | 3.4424 | 3.4195 | -118.3777 | 3.4561 | 3.4378 | 3.4836 | -118.3411
5547.8906 | 121.6919 | -3.392 | 118.2312 | -0.19562 | 0.050827 | 0.058618 | 0.0025465 | 0.029756 | -0.0019632 | 0.029792 | -0.21484 | 0.015302 | 0.025774 | 0.035143 | 0.0053043 | 0.017746 | -0.004578 | 0.018311 | -0.032043 | 0.018311 | 0.10986 | -0.004578 | -0.15564 | 0.054932 | 0.064087 | -0.068665 | 0.068665 | 0.054932 | -0.059509 | -0.09613 | 3.3875 | 3.2364 | -118.1213 | 3.4103 | 3.4103 | 0.17395 | -118.2358 | 3.3325 | 3.2959 | -118.1625 | 3.447 | 3.3234 | 0.027465 | -118.1763 | 3.5019 | 3.3875 | 3.36 | -118.3868 | 3.4607 | 3.447 | 3.4561 | -118.3273
5549.6406 | 121.6507 | -3.3966 | 118.2541 | -0.10406 | 0.051682 | 0.059473 | 0.0014783 | 0.029115 | -0.0017496 | 0.030219 | -0.13092 | 0.013379 | 0.025987 | 0.037066 | 0.0048769 | 0.016677 | 0.054932 | 0.073242 | 0.022888 | 0.018311 | 0.10986 | 0.009155 | -0.15106 | 0.086975 | 0.07782 | -0.041199 | 0.050354 | 0.050354 | -0.050354 | -0.10986 | 3.4058 | 3.2455 | -118.1442 | 3.4698 | 3.4149 | 0.16937 | -118.1992 | 3.3463 | 3.2867 | -118.2037 | 3.4836 | 3.3554 | 0.068664 | -118.2037 | 3.5065 | 3.4515 | 3.4195 | -118.4052 | 3.447 | 3.447 | 3.4744 | -118.364
5551.4062 | 121.7926 | -3.3325 | 118.2587 | 0.071411 | 0.047623 | 0.059259 | 0.0016919 | 0.029756 | -0.004313 | 0.029151 | 0.159 | 0.014234 | 0.02556 | 0.035143 | 0.0014591 | 0.019668 | 0.068665 | 0.10529 | 0.082397 | 0.068665 | 0.059509 | 0.036621 | -0.09613 | 0.13733 | 0.11902 | 0.032043 | 0.032043 | 0.032043 | -0.013733 | -0.073242 | 3.3691 | 3.2364 | -118.1992 | 3.4378 | 3.4012 | 0.16479 | -118.19 | 3.3188 | 3.2593 | -118.2266 | 3.4698 | 3.3646 | 0.10529 | -118.2266 | 3.392 | 3.4012 | 3.4149 | -118.3548 | 3.3646 | 3.3646 | 3.4515 | -118.3319
5553.1875 | 121.6827 | -3.3737 | 118.2953 | 0.040894 | 0.048264 | 0.059686 | -0.0015125 | 0.026979 | -0.0019632 | 0.031074 | 0.052185 | 0.014447 | 0.026201 | 0.036638 | 0.0046633 | 0.021377 | -0.022888 | -0.059509 | -0.050354 | -0.018311 | 0.10986 | -0.004578 | -0.13733 | 0.022888 | -0.013733 | -0.10071 | 0.073242 | 0.064087 | -0.068665 | -0.11444 | 3.3691 | 3.2364 | -118.1854 | 3.3142 | 3.3554 | 0.11902 | -118.3182 | 3.3051 | 3.2593 | -118.222 | 3.3966 | 3.273 | 0.013733 | -118.2312 | 3.4836 | 3.3508 | 3.3234 | -118.4326 | 3.447 | 3.4378 | 3.36 | -118.4097
5554.9531 | 121.7834 | -3.2135 | 118.364 | -0.13458 | 0.044632 | 0.061395 | 0.0057507 | 0.028474 | -0.012003 | 0.025733 | -0.085144 | 0.0091066 | 0.023851 | 0.033007 | -0.00067729 | 0.018814 | 0.082397 | 0.17395 | 0.14648 | 0.086975 | 0.064087 | 0.032043 | -0.10529 | 0.13275 | 0.1831 | 0.064087 | 0.041199 | 0.027466 | -0.036621 | -0.059509 | 3.2455 | 3.1082 | -118.2999 | 3.3875 | 3.3005 | 0.19226 | -118.2816 | 3.1769 | 3.154 | -118.3228 | 3.3463 | 3.2776 | 0.1236 | -118.3365 | 3.2776 | 3.2959 | 3.36 | -118.4692 | 3.2547 | 3.241 | 3.3966 | -118.4235
5556.6562 | 121.6827 | -3.2547 | 118.4189 | -0.18799 | 0.049332 | 0.060541 | 0.0042555 | 0.027619 | -0.006663 | 0.028724 | -0.19958 | 0.011457 | 0.023851 | 0.035143 | 0.0016727 | 0.018814 | 0.059509 | 0.11444 | 0.091553 | 0.068665 | 0.073242 | 0.045776 | -0.11902 | 0.059509 | 0.11444 | -0.004578 | 0.045776 | 0.045776 | -0.041199 | -0.10529 | 3.3005 | 3.1357 | -118.3456 | 3.3691 | 3.3234 | 0.18768 | -118.3594 | 3.2135 | 3.1494 | -118.3731 | 3.3142 | 3.2501 | 0.10071 | -118.3731 | 3.3279 | 3.3142 | 3.3463 | -118.5379 | 3.3005 | 3.3005 | 3.3691 | -118.5242
5558.4062 | 121.6599 | -3.1998 | 118.5059 | -0.050659 | 0.049546 | 0.058618 | 0.00062385 | 0.028047 | 0.00081382 | 0.029365 | -0.054626 | 0.014875 | 0.021715 | 0.035357 | 0.0072269 | 0.016677 | 0.045776 | 0.009155 | -0.004578 | -0.004578 | 0.10529 | 0.013733 | -0.13275 | 0.036621 | 0.013733 | -0.10529 | 0.064087 | 0.064087 | -0.050354 | -0.10071 | 3.2135 | 3.067 | -118.4006 | 3.2089 | 3.1952 | 0.12817 | -118.4601 | 3.1494 | 3.0991 | -118.4418 | 3.2364 | 3.0945 | -0.004578 | -118.4418 | 3.3051 | 3.2455 | 3.1952 | -118.6386 | 3.2639 | 3.2639 | 3.2135 | -118.6066
5560.1719 | 121.7422 | -3.1631 | 118.515 | -0.21851 | 0.051041 | 0.0599 | 0.0019055 | 0.02826 | -0.0028178 | 0.025733 | -0.19958 | 0.01402 | 0.026201 | 0.03557 | 0.0023135 | 0.017318 | -0.027466 | -0.009155 | -0.009155 | -0.004578 | 0.11902 | 0 | -0.15564 | 0.013733 | 0.027466 | -0.082397 | 0.059509 | 0.064087 | -0.068665 | -0.11902 | 3.1631 | 3.0075 | -118.396 | 3.154 | 3.1586 | 0.15106 | -118.5425 | 3.0945 | 3.0441 | -118.4555 | 3.1769 | 3.0808 | 0.036622 | -118.4509 | 3.2822 | 3.1357 | 3.154 | -118.6707 | 3.2227 | 3.2272 | 3.1906 | -118.634
5561.875 | 121.7194 | -3.1998 | 118.5287 | -0.18799 | 0.048264 | 0.0599 | 0.0025465 | 0.026124 | -0.00944 | 0.027656 | -0.13092 | 0.010175 | 0.027269 | 0.033221 | -3.629e-05 | 0.019882 | 0.054932 | 0.13733 | 0.10071 | 0.082397 | 0.073242 | 0.027466 | -0.10986 | 0.10986 | 0.14648 | 0.009155 | 0.045776 | 0.036621 | -0.036621 | -0.086975 | 3.2272 | 3.0899 | -118.4555 | 3.3371 | 3.2822 | 0.19226 | -118.4738 | 3.1631 | 3.1128 | -118.483 | 3.3096 | 3.2089 | 0.09613 | -118.4921 | 3.273 | 3.2547 | 3.3005 | -118.6386 | 3.2455 | 3.2364 | 3.3463 | -118.6157
5563.625 | 121.7056 | -3.1311 | 118.5791 | -0.19562 | 0.049332 | 0.058191 | 0.0051099 | 0.028901 | -0.0055948 | 0.026801 | -0.2301 | 0.013379 | 0.025987 | 0.035998 | -0.00024989 | 0.016464 | 0.064087 | 0.10986 | 0.073242 | 0.064087 | 0.086975 | 0.036621 | -0.10986 | 0.073242 | 0.11444 | -0.009155 | 0.054932 | 0.041199 | -0.045776 | -0.10986 | 3.1677 | 3.0212 | -118.4921 | 3.241 | 3.1952 | 0.17395 | -118.515 | 3.0853 | 3.0212 | -118.5242 | 3.2043 | 3.1219 | 0.10071 | -118.5379 | 3.2181 | 3.1952 | 3.2043 | -118.689 | 3.186 | 3.1723 | 3.2455 | -118.689
5565.3438 | 121.8155 | -3.0991 | 118.5699 | 0.10193 | 0.048691 | 0.058405 | 0.00083745 | 0.026551 | -0.0011088 | 0.028724 | 0.036926 | 0.015515 | 0.023637 | 0.038347 | 0.0050907 | 0.01625 | 0.013733 | -0.027466 | -0.054932 | -0.009155 | 0.12817 | -0.004578 | -0.14191 | 0.041199 | 0 | -0.082397 | 0.082397 | 0.054932 | -0.059509 | -0.11444 | 3.0945 | 2.9572 | -118.4418 | 3.0716 | 3.0899 | 0.13275 | -118.5562 | 3.0396 | 2.9846 | -118.4875 | 3.1403 | 3.0167 | 0.032044 | -118.515 | 3.2272 | 3.1128 | 3.0441 | -118.7119 | 3.1815 | 3.154 | 3.0991 | -118.6844
5567.1094 | 121.756 | -3.1128 | 118.6066 | -0.20325 | 0.048905 | 0.060541 | 0.0048963 | 0.027619 | -0.007731 | 0.029792 | -0.14618 | 0.0086794 | 0.024705 | 0.033648 | 0.0010317 | 0.018814 | 0.073242 | 0.13733 | 0.10986 | 0.068665 | 0.073242 | 0.022888 | -0.10071 | 0.10529 | 0.15106 | 0.027466 | 0.032043 | 0.022888 | -0.018311 | -0.091553 | 3.1357 | 3.0121 | -118.5333 | 3.2501 | 3.1815 | 0.16937 | -118.5333 | 3.0945 | 3.0212 | -118.5745 | 3.2181 | 3.1403 | 0.11902 | -118.5837 | 3.186 | 3.186 | 3.2227 | -118.7073 | 3.1448 | 3.1357 | 3.2639 | -118.6981
5568.8594 | 121.7743 | -3.0991 | 118.6203 | -0.24902 | 0.050614 | 0.058618 | 0.0061781 | 0.028688 | -0.0021768 | 0.028083 | -0.26825 | 0.014447 | 0.025346 | 0.037279 | -0.0013181 | 0.016677 | -0.004578 | -0.009155 | -0.022888 | -0.009155 | 0.1236 | -0.009155 | -0.14648 | 0.013733 | 0.013733 | -0.091553 | 0.07782 | 0.068665 | -0.068665 | -0.09613 | 3.0899 | 2.9526 | -118.4967 | 3.0899 | 3.0899 | 0.13733 | -118.6249 | 3.0304 | 3.0029 | -118.5425 | 3.1128 | 3.0075 | 0.004577 | -118.5516 | 3.2227 | 3.0945 | 3.0762 | -118.7668 | 3.1769 | 3.1677 | 3.1128 | -118.7164
5570.625 | 121.788 | -3.1219 | 118.5928 | 0.071411 | 0.049546 | 0.058618 | -0.00023075 | 0.027192 | -0.00046778 | 0.029792 | 0.052185 | 0.015088 | 0.022142 | 0.036638 | 0.0055179 | 0.0186 | 0.004578 | -0.041199 | -0.050354 | -0.013733 | 0.11902 | 0.013733 | -0.14191 | 0.041199 | -0.013733 | -0.10986 | 0.064087 | 0.064087 | -0.041199 | -0.10986 | 3.1357 | 2.98 | -118.4738 | 3.0807 | 3.1082 | 0.12817 | -118.5883 | 3.0807 | 3.0121 | -118.5287 | 3.1631 | 3.0121 | 0 | -118.5287 | 3.241 | 3.1265 | 3.0716 | -118.7347 | 3.186 | 3.186 | 3.1082 | -118.7027
5572.3281 | 121.8842 | -3.1952 | 118.4738 | -0.14221 | 0.048264 | 0.061395 | 0.0027601 | 0.027833 | -0.011149 | 0.027656 | -0.069885 | 0.010602 | 0.023424 | 0.035357 | -0.0017453 | 0.018173 | 0.068665 | 0.15106 | 0.10986 | 0.073242 | 0.082397 | 0.041199 | -0.11902 | 0.16022 | 0.16937 | 0.086975 | 0.036621 | 0.013733 | -0.027466 | -0.073242 | 3.2364 | 3.0762 | -118.3914 | 3.3463 | 3.2684 | 0.19226 | -118.4052 | 3.1677 | 3.1219 | -118.4372 | 3.3554 | 3.2822 | 0.16022 | -118.4601 | 3.2776 | 3.2639 | 3.3051 | -118.5928 | 3.2318 | 3.2089 | 3.3646 | -118.5471
5574.1094 | 121.8246 | -3.2272 | 118.4921 | 0.08667 | 0.047623 | 0.0599 | 0.00019645 | 0.029542 | 0.0012412 | 0.029365 | 0.059815 | 0.013593 | 0.024278 | 0.037066 | 0.0044497 | 0.018173 | 0.004578 | -0.036621 | -0.054932 | -0.009155 | 0.10986 | 0.013733 | -0.16022 | 0.022888 | -0.013733 | -0.10071 | 0.086975 | 0.059509 | -0.068665 | -0.10986 | 3.241 | 3.067 | -118.3823 | 3.1906 | 3.2181 | 0.15106 | -118.4875 | 3.1586 | 3.1174 | -118.4052 | 3.2501 | 3.1265 | 0.009155 | -118.4326 | 3.3371 | 3.2318 | 3.1723 | -118.6523 | 3.3142 | 3.2867 | 3.2135 | -118.602
5575.8125 | 121.7697 | -3.2318 | 118.5471 | -0.24902 | 0.051468 | 0.057123 | 0.0053235 | 0.028901 | -0.0073038 | 0.027228 | -0.1767 | 0.010602 | 0.02321 | 0.035998 | -3.629e-05 | 0.018814 | 0 | 0.036621 | 0 | 0.013733 | 0.10529 | 0 | -0.13733 | 0.027466 | 0.041199 | -0.073242 | 0.059509 | 0.059509 | -0.068665 | -0.10071 | 3.2318 | 3.0945 | -118.4418 | 3.2684 | 3.2455 | 0.15106 | -118.5471 | 3.1631 | 3.1311 | -118.4875 | 3.2593 | 3.1586 | 0.027466 | -118.4875 | 3.3371 | 3.2318 | 3.2318 | -118.6844 | 3.2913 | 3.2913 | 3.273 | -118.6478
5577.5781 | 121.8567 | -3.1815 | 118.4921 | 0.13245 | 0.049546 | 0.056268 | 0.0034009 | 0.027192 | -0.0073038 | 0.029578 | 0.15137 | 0.013593 | 0.025133 | 0.035143 | 0.00039091 | 0.019241 | 0.082397 | 0.1236 | 0.11444 | 0.064087 | 0.054932 | 0.045776 | -0.10071 | 0.15106 | 0.12817 | 0.041199 | 0.036621 | 0 | -0.041199 | -0.059509 | 3.2272 | 3.0808 | -118.4372 | 3.3051 | 3.2455 | 0.1648 | -118.4097 | 3.1403 | 3.1219 | -118.4555 | 3.3325 | 3.2227 | 0.10071 | -118.4921 | 3.2364 | 3.2639 | 3.2959 | -118.5928 | 3.2181 | 3.1815 | 3.3096 | -118.5516
5579.2812 | 121.8246 | -3.2043 | 118.5242 | -0.12695 | 0.050614 | 0.057336 | 0.0042555 | 0.029542 | 0.00017302 | 0.028297 | -0.13855 | 0.014661 | 0.023637 | 0.037279 | 0.0040225 | 0.016891 | 0.054932 | 0.036621 | 0 | 0.045776 | 0.10986 | -0.009155 | -0.13275 | 0.086975 | 0.07782 | -0.050354 | 0.064087 | 0.045776 | -0.045776 | -0.10986 | 3.1952 | 3.0716 | -118.4143 | 3.241 | 3.2501 | 0.17853 | -118.4692 | 3.1586 | 3.0945 | -118.4601 | 3.2913 | 3.154 | 0.059509 | -118.4784 | 3.3142 | 3.2593 | 3.2043 | -118.6569 | 3.2684 | 3.2501 | 3.2822 | -118.634
5581.0312 | 121.8979 | -3.1815 | 118.5379 | 0.10956 | 0.049332 | 0.059686 | 0.0010511 | 0.027192 | -0.00046778 | 0.029365 | 0.067444 | 0.014875 | 0.024492 | 0.035998 | 0.0048769 | 0.017318 | 0.013733 | -0.009155 | -0.050354 | -0.022888 | 0.11902 | -0.013733 | -0.13275 | 0.064087 | 0.009155 | -0.068665 | 0.073242 | 0.059509 | -0.036621 | -0.082397 | 3.1677 | 3.0487 | -118.4189 | 3.1723 | 3.1586 | 0.10986 | -118.5242 | 3.1448 | 3.0991 | -118.4647 | 3.2455 | 3.1128 | 0.013732 | -118.4784 | 3.3005 | 3.1952 | 3.1311 | -118.6707 | 3.2547 | 3.241 | 3.1906 | -118.6203
5582.7969 | 121.843 | -3.2135 | 118.5471 | -0.15747 | 0.051255 | 0.05755 | 0.0063917 | 0.029756 | -0.00068138 | 0.029792 | -0.15381 | 0.015302 | 0.024278 | 0.038347 | 0.0012455 | 0.016891 | 0.064087 | 0.027466 | 0 | 0.036621 | 0.1236 | 0.027466 | -0.14191 | 0.068665 | 0.064087 | -0.054932 | 0.059509 | 0.050354 | -0.041199 | -0.10529 | 3.241 | 3.0716 | -118.4235 | 3.241 | 3.2501 | 0.17853 | -118.483 | 3.1723 | 3.1082 | -118.4875 | 3.2822 | 3.1586 | 0.050354 | -118.4967 | 3.3371 | 3.2776 | 3.2135 | -118.689 | 3.273 | 3.2639 | 3.2776 | -118.6523
5584.5625 | 121.8933 | -3.1952 | 118.5699 | 0.033264 | 0.049759 | 0.058618 | 0.0057507 | 0.02591 | -0.0096536 | 0.027656 | 0.097962 | 0.011029 | 0.022996 | 0.035784 | -0.0019589 | 0.018173 | 0.009155 | 0.059509 | 0.068665 | 0.045776 | 0.059509 | 0.036621 | -0.1236 | 0.07782 | 0.068665 | -0.004578 | 0.041199 | 0.027466 | -0.027466 | -0.082397 | 3.2318 | 3.0716 | -118.5104 | 3.2547 | 3.241 | 0.16937 | -118.5608 | 3.1677 | 3.1128 | -118.5287 | 3.273 | 3.1906 | 0.077819 | -118.5425 | 3.2547 | 3.2043 | 3.2639 | -118.6935 | 3.2364 | 3.2227 | 3.2639 | -118.6523
5586.2656 | 121.8018 | -3.1952 | 118.5928 | 0.056152 | 0.048691 | 0.057977 | 0.0014783 | 0.028474 | 0.00038662 | 0.030646 | 0.021668 | 0.016156 | 0.022783 | 0.038775 | 0.0035953 | 0.018386 | 0.013733 | -0.045776 | -0.045776 | -0.013733 | 0.10986 | 0.018311 | -0.13733 | 0.032043 | -0.013733 | -0.10529 | 0.082397 | 0.068665 | -0.059509 | -0.10529 | 3.2135 | 3.0579 | -118.483 | 3.1494 | 3.1815 | 0.1236 | -118.5791 | 3.1357 | 3.0899 | -118.5104 | 3.2272 | 3.0899 | 0 | -118.5242 | 3.3051 | 3.2089 | 3.1494 | -118.7302 | 3.2776 | 3.2639 | 3.1815 | -118.6981
5588.0312 | 121.8521 | -3.2135 | 118.5837 | -0.20325 | 0.04805 | 0.060541 | 0.0044691 | 0.029115 | -0.0098672 | 0.028297 | -0.12329 | 0.0080386 | 0.026414 | 0.034716 | -0.0011045 | 0.018814 | 0.059509 | 0.13733 | 0.10986 | 0.073242 | 0.082397 | 0.041199 | -0.11444 | 0.1236 | 0.17853 | 0.050354 | 0.018311 | 0.013733 | -0.027466 | -0.07782 | 3.2547 | 3.0991 | -118.5013 | 3.3508 | 3.2867 | 0.18768 | -118.5242 | 3.186 | 3.1357 | -118.5654 | 3.3371 | 3.2639 | 0.12817 | -118.5699 | 3.2959 | 3.273 | 3.3234 | -118.6981 | 3.2318 | 3.2272 | 3.392 | -118.6615
5589.7969 | 121.9437 | -3.1906 | 118.5379 | 0.14771 | 0.04805 | 0.057123 | 0.00019645 | 0.028901 | -0.003245 | 0.028297 | 0.075073 | 0.013593 | 0.024705 | 0.034716 | 0.0027407 | 0.014968 | 0.068665 | 0.041199 | 0.041199 | 0.054932 | 0.082397 | 0.032043 | -0.1236 | 0.12817 | 0.10986 | 0.018311 | 0.027466 | 0.027466 | -0.022888 | -0.086975 | 3.2227 | 3.067 | -118.4555 | 3.2318 | 3.2455 | 0.17853 | -118.4692 | 3.1677 | 3.1036 | -118.5104 | 3.3188 | 3.2089 | 0.10529 | -118.5104 | 3.273 | 3.2593 | 3.2318 | -118.6615 | 3.2181 | 3.2181 | 3.3005 | -118.6249
5591.5 | 121.9208 | -3.2227 | 118.5425 | 0.010376 | 0.049118 | 0.060541 | 0.0029737 | 0.025483 | -0.0087992 | 0.027656 | 0.059815 | 0.013166 | 0.025987 | 0.035998 | -0.00024989 | 0.019455 | 0.032043 | 0.054932 | 0.059509 | 0.036621 | 0.086975 | 0.036621 | -0.1236 | 0.073242 | 0.082397 | 0.004578 | 0.032043 | 0.022888 | -0.032043 | -0.068665 | 3.2593 | 3.0991 | -118.4555 | 3.2776 | 3.2593 | 0.16022 | -118.5104 | 3.1906 | 3.154 | -118.5104 | 3.2959 | 3.2272 | 0.073243 | -118.5196 | 3.3096 | 3.2547 | 3.2822 | -118.6661 | 3.2547 | 3.2455 | 3.3051 | -118.6111
5593.2656 | 121.8567 | -3.273 | 118.5333 | 0.056152 | 0.050186 | 0.0599 | -0.0017261 | 0.02826 | 0.0016684 | 0.027015 | 0.044556 | 0.014234 | 0.021715 | 0.038347 | 0.0059451 | 0.015823 | 0.022888 | -0.032043 | -0.045776 | -0.004578 | 0.11444 | -0.009155 | -0.15106 | 0.041199 | -0.032043 | -0.10986 | 0.073242 | 0.064087 | -0.050354 | -0.11444 | 3.2639 | 3.1219 | -118.4189 | 3.241 | 3.2684 | 0.14648 | -118.5104 | 3.2227 | 3.1586 | -118.4601 | 3.3142 | 3.1631 | 0.004578 | -118.4692 | 3.3875 | 3.2959 | 3.2272 | -118.6844 | 3.3463 | 3.3371 | 3.241 | -118.6478
5595.0312 | 121.9666 | -3.2684 | 118.4875 | -0.18799 | 0.045487 | 0.059473 | 0.0057507 | 0.026124 | -0.0092264 | 0.028297 | -0.062256 | 0.011243 | 0.024278 | 0.033648 | -0.00024989 | 0.018386 | 0.054932 | 0.1236 | 0.10071 | 0.07782 | 0.068665 | 0.032043 | -0.11902 | 0.15564 | 0.16937 | 0.064087 | 0.022888 | 0.009155 | -0.027466 | -0.068665 | 3.3005 | 3.1494 | -118.4189 | 3.392 | 3.3463 | 0.19684 | -118.4326 | 3.241 | 3.1998 | -118.4647 | 3.4241 | 3.3325 | 0.13275 | -118.4784 | 3.3371 | 3.3234 | 3.3691 | -118.6066 | 3.2913 | 3.2776 | 3.4378 | -118.5562
5596.7812 | 121.8887 | -3.3875 | 118.4555 | -0.26428 | 0.051041 | 0.0599 | 0.0040417 | 0.027619 | -0.0013224 | 0.026374 | -0.2301 | 0.014875 | 0.025133 | 0.038561 | 0.0018863 | 0.014968 | 0.013733 | -0.022888 | -0.032043 | -0.009155 | 0.11444 | -0.013733 | -0.16479 | 0.022888 | 0.027466 | -0.10529 | 0.086975 | 0.054932 | -0.068665 | -0.12817 | 3.3737 | 3.2227 | -118.3411 | 3.3646 | 3.3783 | 0.15564 | -118.4418 | 3.3188 | 3.2593 | -118.3685 | 3.4103 | 3.2822 | 0.022888 | -118.4006 | 3.5019 | 3.4012 | 3.3554 | -118.6203 | 3.4744 | 3.4424 | 3.4149 | -118.5837
5598.5469 | 121.8796 | -3.392 | 118.4555 | -0.21088 | 0.050827 | 0.057977 | 0.0044691 | 0.025056 | -0.004313 | 0.027442 | -0.26062 | 0.014234 | 0.024705 | 0.036638 | 0.00081811 | 0.015823 | -0.004578 | -0.013733 | -0.032043 | -0.004578 | 0.11902 | 0.004578 | -0.15106 | 0.027466 | 0.027466 | -0.091553 | 0.10529 | 0.07782 | -0.068665 | -0.1236 | 3.3966 | 3.241 | -118.3365 | 3.3783 | 3.3875 | 0.14648 | -118.4601 | 3.3234 | 3.2684 | -118.3502 | 3.4195 | 3.3005 | 0.032043 | -118.3777 | 3.511 | 3.3875 | 3.36 | -118.6066 | 3.4973 | 3.4698 | 3.4195 | -118.5791
5600.3125 | 121.843 | -3.4058 | 118.4555 | -0.073547 | 0.050186 | 0.058832 | -0.0015125 | 0.027619 | 0.0023092 | 0.029792 | -0.085144 | 0.012525 | 0.025346 | 0.03557 | 0.0057315 | 0.016677 | 0.068665 | 0.041199 | 0 | 0.027466 | 0.10071 | 0.004578 | -0.13733 | 0.064087 | 0.032043 | -0.086975 | 0.050354 | 0.059509 | -0.045776 | -0.11444 | 3.4103 | 3.2684 | -118.3548 | 3.447 | 3.4332 | 0.16479 | -118.3868 | 3.36 | 3.2913 | -118.4052 | 3.4698 | 3.3188 | 0.027466 | -118.396 | 3.5065 | 3.4744 | 3.4058 | -118.5928 | 3.4561 | 3.4653 | 3.4378 | -118.5699
5602.0156 | 121.8567 | -3.3829 | 118.483 | -0.18799 | 0.047837 | 0.062036 | 0.0027601 | 0.029969 | -0.0073038 | 0.029151 | -0.14618 | 0.013166 | 0.024919 | 0.03557 | 0.00039091 | 0.019668 | 0.045776 | 0.12817 | 0.11444 | 0.064087 | 0.064087 | 0.032043 | -0.11444 | 0.09613 | 0.16479 | 0.022888 | 0.036621 | 0.036621 | -0.045776 | -0.10529 | 3.4149 | 3.2684 | -118.4189 | 3.511 | 3.447 | 0.17853 | -118.4372 | 3.3371 | 3.2776 | -118.4464 | 3.479 | 3.4058 | 0.12817 | -118.4464 | 3.447 | 3.4287 | 3.4973 | -118.5974 | 3.4195 | 3.4195 | 3.5477 | -118.5883
5603.7812 | 121.9437 | -3.3188 | 118.4509 | 0.10193 | 0.049546 | 0.058832 | 0.0014783 | 0.025056 | -0.00025418 | 0.030219 | 0.044556 | 0.014234 | 0.021928 | 0.036638 | 0.0057315 | 0.017746 | 0.004578 | -0.013733 | -0.041199 | -0.009155 | 0.11444 | 0 | -0.15564 | 0.041199 | -0.009155 | -0.11444 | 0.07782 | 0.059509 | -0.050354 | -0.1236 | 3.3188 | 3.1631 | -118.3365 | 3.3051 | 3.3096 | 0.14649 | -118.4464 | 3.2684 | 3.1952 | -118.3731 | 3.36 | 3.2043 | 0.009155 | -118.3914 | 3.4332 | 3.3234 | 3.2776 | -118.6066 | 3.3966 | 3.3783 | 3.3096 | -118.5745
5605.4844 | 121.9986 | -3.3096 | 118.5013 | 0.010376 | 0.045914 | 0.058832 | 0.0048963 | 0.028047 | -0.0092264 | 0.025092 | 0.052185 | 0.013166 | 0.025133 | 0.03557 | -0.0028135 | 0.019882 | 0.009155 | 0.073242 | 0.059509 | 0.045776 | 0.073242 | 0.022888 | -0.1236 | 0.082397 | 0.10071 | 0.022888 | 0.032043 | 0.032043 | -0.032043 | -0.086975 | 3.3325 | 3.186 | -118.428 | 3.3829 | 3.3554 | 0.16937 | -118.4921 | 3.2776 | 3.2227 | -118.4692 | 3.392 | 3.3325 | 0.10986 | -118.4692 | 3.3829 | 3.3188 | 3.3691 | -118.6249 | 3.3417 | 3.3417 | 3.4103 | -118.5883
5607.25 | 121.9208 | -3.3234 | 118.5196 | -0.20325 | 0.046768 | 0.060754 | 0.0063917 | 0.029328 | -0.0053812 | 0.025519 | -0.13092 | 0.010816 | 0.024278 | 0.035998 | 0.00039091 | 0.01625 | 0.10071 | 0.1236 | 0.10986 | 0.10071 | 0.064087 | 0.050354 | -0.1236 | 0.12817 | 0.16937 | 0.036621 | 0.032043 | 0.013733 | -0.032043 | -0.073242 | 3.3737 | 3.1998 | -118.4555 | 3.447 | 3.4241 | 0.2243 | -118.4189 | 3.2913 | 3.2501 | -118.4875 | 3.4515 | 3.36 | 0.10986 | -118.5059 | 3.3875 | 3.4241 | 3.4332 | -118.6432 | 3.3554 | 3.3371 | 3.4927 | -118.5928
5609.0156 | 122.0032 | -3.3051 | 118.5104 | -0.13458 | 0.048477 | 0.060754 | 0.0010511 | 0.028688 | -0.007731 | 0.024238 | -0.12329 | 0.015088 | 0.025774 | 0.034502 | -0.00046349 | 0.016037 | 0.10529 | 0.15106 | 0.10529 | 0.050354 | 0.064087 | 0.045776 | -0.10986 | 0.16022 | 0.18768 | 0.068665 | 0.027466 | 0.022888 | -0.018311 | -0.073242 | 3.3508 | 3.1952 | -118.4463 | 3.4561 | 3.3554 | 0.16022 | -118.4052 | 3.2867 | 3.2318 | -118.483 | 3.4653 | 3.3737 | 0.14191 | -118.4875 | 3.3691 | 3.4103 | 3.4103 | -118.6203 | 3.3325 | 3.3279 | 3.4927 | -118.5837
5610.7188 | 122.0215 | -3.3005 | 118.5196 | 0.14008 | 0.048691 | 0.0599 | 0.00041005 | 0.027406 | -0.00089518 | 0.029365 | 0.15137 | 0.012952 | 0.022356 | 0.036211 | 0.0055179 | 0.015396 | 0.086975 | 0.10529 | 0.059509 | 0.054932 | 0.09613 | 0.036621 | -0.12817 | 0.14648 | 0.10986 | 0.022888 | 0.054932 | 0.013733 | -0.027466 | -0.064087 | 3.3371 | 3.1723 | -118.4235 | 3.4058 | 3.3554 | 0.18311 | -118.4326 | 3.273 | 3.2364 | -118.4647 | 3.447 | 3.3234 | 0.086975 | -118.5059 | 3.3966 | 3.3875 | 3.36 | -118.6478 | 3.3554 | 3.3142 | 3.4103 | -118.5837
5612.4844 | 121.9757 | -3.3508 | 118.4647 | 0.14771 | 0.048477 | 0.058618 | 0.00062385 | 0.02591 | -0.0040994 | 0.028297 | 0.13611 | 0.01402 | 0.021715 | 0.035357 | 0.0053043 | 0.018173 | 0.09613 | 0.14648 | 0.10986 | 0.064087 | 0.064087 | 0.054932 | -0.10071 | 0.16022 | 0.1236 | 0.036621 | 0.032043 | 0.018311 | -0.009155 | -0.07782 | 3.4058 | 3.2501 | -118.4006 | 3.4973 | 3.4149 | 0.1648 | -118.3685 | 3.3417 | 3.273 | -118.4326 | 3.511 | 3.3875 | 0.11444 | -118.4464 | 3.4149 | 3.447 | 3.4607 | -118.5654 | 3.3829 | 3.3691 | 3.4744 | -118.5425
5614.1875 | 121.962 | -3.4378 | 118.3823 | 0.14771 | 0.049118 | 0.060327 | -0.0010851 | 0.028047 | -0.002604 | 0.030219 | 0.13611 | 0.011457 | 0.022142 | 0.03557 | 0.0053043 | 0.017959 | 0.11444 | 0.1236 | 0.10071 | 0.086975 | 0.059509 | 0.050354 | -0.11444 | 0.15106 | 0.13275 | 0.036621 | 0.022888 | 0.009155 | -0.041199 | -0.068665 | 3.4882 | 3.3234 | -118.3228 | 3.5614 | 3.5248 | 0.20142 | -118.2678 | 3.3966 | 3.3691 | -118.3594 | 3.5889 | 3.4744 | 0.10529 | -118.3731 | 3.4973 | 3.5522 | 3.5385 | -118.4967 | 3.4607 | 3.447 | 3.5706 | -118.4509
5615.9531 | 121.9849 | -3.4195 | 118.4189 | -0.18036 | 0.04805 | 0.062036 | 0.0066053 | 0.027619 | -0.0068766 | 0.026374 | -0.15381 | 0.011457 | 0.023424 | 0.036425 | -0.00089089 | 0.016891 | 0.09613 | 0.15564 | 0.1236 | 0.064087 | 0.07782 | 0.050354 | -0.10071 | 0.14191 | 0.18768 | 0.041199 | 0.045776 | 0.018311 | -0.018311 | -0.068665 | 3.4698 | 3.3188 | -118.3411 | 3.5751 | 3.4836 | 0.1648 | -118.3228 | 3.4012 | 3.3508 | -118.3731 | 3.5614 | 3.4607 | 0.10986 | -118.4006 | 3.4973 | 3.5156 | 3.5431 | -118.5196 | 3.4653 | 3.4378 | 3.6072 | -118.4875
5617.6719 | 122.0581 | -3.479 | 118.3319 | -0.0354 | 0.046341 | 0.061395 | 0.0034009 | 0.028688 | -0.0075174 | 0.025519 | -0.046997 | 0.011243 | 0.024492 | 0.035784 | -0.00024989 | 0.016677 | 0.050354 | 0.059509 | 0.059509 | 0.045776 | 0.07782 | 0.041199 | -0.11902 | 0.13733 | 0.13275 | 0.036621 | 0.045776 | 0.032043 | -0.027466 | -0.082397 | 3.5202 | 3.36 | -118.2541 | 3.5385 | 3.5248 | 0.16479 | -118.2816 | 3.4515 | 3.3966 | -118.2861 | 3.6163 | 3.5156 | 0.11902 | -118.2999 | 3.5568 | 3.5294 | 3.5385 | -118.4509 | 3.5248 | 3.511 | 3.6118 | -118.4143
5619.4375 | 122.0535 | -3.479 | 118.3685 | -0.065918 | 0.046982 | 0.059473 | 0.0055371 | 0.028901 | -0.004313 | 0.026374 | -0.069885 | 0.011884 | 0.023424 | 0.035784 | -0.0021725 | 0.016464 | 0.07782 | 0.091553 | 0.07782 | 0.059509 | 0.082397 | 0.045776 | -0.12817 | 0.15564 | 0.14191 | 0.054932 | 0.050354 | 0.013733 | -0.013733 | -0.091553 | 3.5248 | 3.3508 | -118.2861 | 3.5706 | 3.5385 | 0.18768 | -118.2907 | 3.4653 | 3.3875 | -118.3182 | 3.6346 | 3.5339 | 0.14649 | -118.3548 | 3.5614 | 3.5568 | 3.5568 | -118.4967 | 3.5294 | 3.4927 | 3.6209 | -118.4601
5621.1406 | 121.9437 | -3.4973 | 118.3914 | 0.056152 | 0.047623 | 0.058618 | -0.00044435 | 0.02826 | 0.0016684 | 0.03086 | -0.0012209 | 0.016584 | 0.025133 | 0.035784 | 0.0072269 | 0.015396 | 0.027466 | -0.022888 | -0.032043 | -0.018311 | 0.13275 | -0.009155 | -0.15564 | 0.050354 | -0.022888 | -0.10986 | 0.073242 | 0.059509 | -0.068665 | -0.11444 | 3.4882 | 3.3417 | -118.2587 | 3.4744 | 3.479 | 0.13733 | -118.364 | 3.4286 | 3.3829 | -118.3182 | 3.5477 | 3.3875 | 0.004578 | -118.3319 | 3.6301 | 3.5248 | 3.4653 | -118.5471 | 3.5706 | 3.5568 | 3.4744 | -118.5059
5622.9062 | 121.9116 | -3.511 | 118.4235 | -0.073547 | 0.051041 | 0.058832 | -0.0012987 | 0.027833 | 0.0020956 | 0.028937 | -0.092773 | 0.012525 | 0.025987 | 0.036638 | 0.0063723 | 0.017532 | 0.059509 | 0.045776 | 0.009155 | 0.018311 | 0.1236 | 0 | -0.13275 | 0.068665 | 0.045776 | -0.09613 | 0.073242 | 0.045776 | -0.045776 | -0.10529 | 3.511 | 3.3783 | -118.2999 | 3.5568 | 3.5294 | 0.15106 | -118.364 | 3.4653 | 3.4058 | -118.3502 | 3.5797 | 3.4149 | 0.009156 | -118.3777 | 3.6346 | 3.5706 | 3.5202 | -118.5562 | 3.5843 | 3.5568 | 3.5568 | -118.5287
5624.6719 | 121.9025 | -3.4744 | 118.428 | -0.0354 | 0.050614 | 0.056055 | 0.0042555 | 0.026765 | 0.00038662 | 0.030646 | -0.062256 | 0.013593 | 0.025133 | 0.037707 | 0.0048769 | 0.017105 | 0.041199 | 0.022888 | -0.009155 | 0.004578 | 0.10986 | -0.004578 | -0.14648 | 0.032043 | 0.027466 | -0.10986 | 0.059509 | 0.059509 | -0.054932 | -0.10071 | 3.4698 | 3.3279 | -118.3182 | 3.4973 | 3.479 | 0.15106 | -118.3868 | 3.4195 | 3.3737 | -118.3685 | 3.5065 | 3.3646 | -0.009155 | -118.3685 | 3.5843 | 3.5156 | 3.4653 | -118.5745 | 3.5339 | 3.5339 | 3.5019 | -118.5287
5626.4375 | 122.0764 | -3.4195 | 118.4235 | -0.065918 | 0.04506 | 0.060327 | 0.0063917 | 0.027192 | -0.010081 | 0.02616 | -0.039368 | 0.011884 | 0.027269 | 0.036638 | -0.0021725 | 0.019241 | 0.027466 | 0.10529 | 0.082397 | 0.054932 | 0.082397 | 0.027466 | -0.11444 | 0.13733 | 0.16022 | 0.059509 | 0.054932 | 0.013733 | -0.036621 | -0.086975 | 3.447 | 3.3051 | -118.3411 | 3.5248 | 3.4744 | 0.16937 | -118.396 | 3.3829 | 3.3325 | -118.3685 | 3.5568 | 3.479 | 0.14648 | -118.4097 | 3.5019 | 3.447 | 3.5019 | -118.5379 | 3.4744 | 3.4332 | 3.5797 | -118.5104
5628.1562 | 121.907 | -3.4744 | 118.4601 | 0.056152 | 0.052323 | 0.057336 | -1.7146e-05 | 0.027192 | -0.00025418 | 0.029151 | -0.016479 | 0.014875 | 0.022783 | 0.037066 | 0.0063723 | 0.015823 | 0.018311 | -0.022888 | -0.054932 | -0.004578 | 0.10529 | 0.004578 | -0.15564 | 0.013733 | -0.004578 | -0.12817 | 0.068665 | 0.064087 | -0.064087 | -0.10071 | 3.479 | 3.3188 | -118.3548 | 3.4515 | 3.4698 | 0.15106 | -118.4418 | 3.4103 | 3.3737 | -118.3914 | 3.4882 | 3.3463 | -0.027466 | -118.396 | 3.5797 | 3.4927 | 3.4195 | -118.6157 | 3.5431 | 3.5385 | 3.4698 | -118.5608
5629.9219 | 122.0627 | -3.4195 | 118.4372 | -0.027771 | 0.048691 | 0.060968 | 0.0031873 | 0.028474 | -0.008372 | 0.028083 | 0.036926 | 0.008893 | 0.02556 | 0.034716 | -0.0017453 | 0.018173 | 0 | 0.068665 | 0.045776 | 0.032043 | 0.091553 | 0.009155 | -0.11444 | 0.086975 | 0.11444 | 0.022888 | 0.045776 | 0.022888 | -0.027466 | -0.082397 | 3.4286 | 3.3051 | -118.3456 | 3.4882 | 3.4515 | 0.14648 | -118.4372 | 3.392 | 3.3371 | -118.3914 | 3.5065 | 3.4424 | 0.10528 | -118.4143 | 3.511 | 3.4195 | 3.4653 | -118.5516 | 3.4653 | 3.4424 | 3.5339 | -118.5196
5631.625 | 121.9894 | -3.4378 | 118.4647 | -0.14221 | 0.051468 | 0.058191 | 0.0031873 | 0.027833 | -4.058e-05 | 0.029792 | -0.16144 | 0.014447 | 0.024278 | 0.038347 | 0.0057315 | 0.0139 | 0.045776 | 0.050354 | -0.004578 | 0.036621 | 0.09613 | 0.009155 | -0.14648 | 0.068665 | 0.073242 | -0.059509 | 0.059509 | 0.054932 | -0.041199 | -0.11902 | 3.447 | 3.2913 | -118.3685 | 3.4882 | 3.4744 | 0.18311 | -118.4189 | 3.3966 | 3.3188 | -118.4052 | 3.5065 | 3.3783 | 0.05951 | -118.4097 | 3.5339 | 3.4836 | 3.4332 | -118.6111 | 3.4973 | 3.4927 | 3.511 | -118.5837
5633.3906 | 122.0261 | -3.4149 | 118.4235 | 0.14771 | 0.046768 | 0.059259 | 0.0016919 | 0.027192 | -0.0053812 | 0.027869 | 0.17426 | 0.010388 | 0.022996 | 0.036852 | 0.0044497 | 0.017532 | 0.10071 | 0.10529 | 0.10529 | 0.073242 | 0.050354 | 0.041199 | -0.10986 | 0.16022 | 0.12817 | 0.041199 | 0.022888 | 0.022888 | -0.022888 | -0.082397 | 3.4561 | 3.3051 | -118.3731 | 3.5202 | 3.4882 | 0.18311 | -118.3228 | 3.392 | 3.3325 | -118.4006 | 3.5751 | 3.4561 | 0.1236 | -118.4006 | 3.4653 | 3.5156 | 3.5202 | -118.5333 | 3.4378 | 3.4378 | 3.5431 | -118.5059
5635.1562 | 122.0764 | -3.392 | 118.4326 | 0.048523 | 0.048477 | 0.060327 | 0.0027601 | 0.028047 | -0.0017496 | 0.026588 | 0.15137 | 0.014875 | 0.023851 | 0.040056 | 0.0025271 | 0.01625 | 0.027466 | -0.013733 | -0.022888 | -0.009155 | 0.10071 | 0.013733 | -0.14191 | 0.082397 | 0.036621 | -0.050354 | 0.054932 | 0.050354 | -0.036621 | -0.10071 | 3.4058 | 3.2501 | -118.3319 | 3.3783 | 3.3829 | 0.13275 | -118.4052 | 3.3554 | 3.2913 | -118.3777 | 3.4744 | 3.3417 | 0.050354 | -118.3823 | 3.4927 | 3.4195 | 3.3691 | -118.5745 | 3.447 | 3.4424 | 3.4286 | -118.5333
5636.8594 | 121.9986 | -3.4653 | 118.4601 | -0.21851 | 0.047409 | 0.059259 | 0.0046827 | 0.030824 | -0.007731 | 0.02851 | -0.13855 | 0.012525 | 0.024065 | 0.035143 | -0.00067729 | 0.019455 | 0.09613 | 0.13733 | 0.11444 | 0.073242 | 0.07782 | 0.018311 | -0.10986 | 0.13275 | 0.16479 | 0.041199 | 0.018311 | 0.013733 | -0.045776 | -0.091553 | 3.4836 | 3.3554 | -118.3823 | 3.6026 | 3.5385 | 0.18311 | -118.364 | 3.4195 | 3.3737 | -118.4418 | 3.598 | 3.5065 | 0.13275 | -118.4463 | 3.5431 | 3.5614 | 3.5797 | -118.5699 | 3.4836 | 3.479 | 3.6301 | -118.5516
5638.6406 | 121.9986 | -3.4515 | 118.4509 | -0.19562 | 0.048691 | 0.060754 | 0.0053235 | 0.030397 | -0.0058084 | 0.028297 | -0.12329 | 0.010388 | 0.023851 | 0.035784 | -0.0015317 | 0.015609 | 0.068665 | 0.11902 | 0.10986 | 0.082397 | 0.068665 | 0.018311 | -0.1236 | 0.11902 | 0.16022 | 0.045776 | 0.036621 | 0.009155 | -0.036621 | -0.07782 | 3.4698 | 3.3279 | -118.3823 | 3.5706 | 3.5339 | 0.20599 | -118.3823 | 3.4149 | 3.3737 | -118.4143 | 3.5706 | 3.4973 | 0.1236 | -118.4418 | 3.5202 | 3.5202 | 3.5614 | -118.5745 | 3.4882 | 3.4607 | 3.6118 | -118.5287
5640.4219 | 122.0535 | -3.4607 | 118.428 | 0.063782 | 0.046768 | 0.056696 | 0.0023329 | 0.026765 | -0.0036722 | 0.029578 | 0.12848 | 0.012097 | 0.025774 | 0.036425 | 0.0020999 | 0.017105 | 0.10071 | 0.10986 | 0.09613 | 0.050354 | 0.064087 | 0.032043 | -0.10071 | 0.13733 | 0.10986 | 0.018311 | 0.045776 | 0.018311 | -0.032043 | -0.07782 | 3.4927 | 3.36 | -118.364 | 3.5706 | 3.511 | 0.15106 | -118.3273 | 3.4287 | 3.3829 | -118.3823 | 3.598 | 3.479 | 0.096131 | -118.4097 | 3.5248 | 3.5614 | 3.5568 | -118.5287 | 3.5065 | 3.479 | 3.5706 | -118.5059
5642.1875 | 122.0901 | -3.4378 | 118.4555 | -0.14221 | 0.046341 | 0.059473 | 0.0068189 | 0.027406 | -0.008372 | 0.026801 | -0.1004 | 0.011457 | 0.02321 | 0.036211 | -0.0015317 | 0.016891 | 0.10071 | 0.12817 | 0.12817 | 0.082397 | 0.086975 | 0.050354 | -0.12817 | 0.16022 | 0.1831 | 0.07782 | 0.013733 | 0.027466 | -0.032043 | -0.07782 | 3.4882 | 3.3096 | -118.3685 | 3.566 | 3.5202 | 0.21057 | -118.3548 | 3.4058 | 3.36 | -118.4418 | 3.598 | 3.5156 | 0.15564 | -118.428 | 3.5248 | 3.5385 | 3.566 | -118.5837 | 3.4515 | 3.4653 | 3.6209 | -118.5333
5643.9062 | 122.0444 | -3.4424 | 118.4692 | 0.071411 | 0.046341 | 0.057977 | 0.00083745 | 0.025483 | -0.003245 | 0.027228 | 0.13611 | 0.01167 | 0.022783 | 0.034929 | 0.0025271 | 0.017318 | 0.082397 | 0.11902 | 0.086975 | 0.059509 | 0.050354 | 0.032043 | -0.12817 | 0.12817 | 0.10071 | 0.004578 | 0.045776 | 0.013733 | -0.050354 | -0.07782 | 3.4744 | 3.3142 | -118.4189 | 3.5614 | 3.5019 | 0.18768 | -118.3868 | 3.392 | 3.3646 | -118.4235 | 3.5706 | 3.447 | 0.082398 | -118.4555 | 3.4927 | 3.5248 | 3.5294 | -118.5974 | 3.4882 | 3.4561 | 3.5431 | -118.5471
5645.6719 | 121.9757 | -3.4653 | 118.5059 | -0.18799 | 0.046982 | 0.057977 | 0.0055371 | 0.029756 | -0.0053812 | 0.027656 | -0.23773 | 0.010388 | 0.024492 | 0.034929 | 0.0010317 | 0.015823 | 0.073242 | 0.12817 | 0.07782 | 0.073242 | 0.073242 | 0.036621 | -0.13275 | 0.086975 | 0.11444 | -0.009155 | 0.045776 | 0.027466 | -0.059509 | -0.10986 | 3.5019 | 3.3325 | -118.4326 | 3.5934 | 3.5385 | 0.20599 | -118.4326 | 3.4058 | 3.3554 | -118.4601 | 3.5522 | 3.4561 | 0.10071 | -118.4784 | 3.5385 | 3.5385 | 3.5431 | -118.6386 | 3.511 | 3.4927 | 3.5797 | -118.6157
5647.4375 | 121.994 | -3.4561 | 118.483 | -0.11169 | 0.050614 | 0.060541 | 0.00041005 | 0.029542 | 0.0023092 | 0.027442 | -0.19958 | 0.015729 | 0.023637 | 0.036425 | 0.0044497 | 0.014755 | 0.064087 | 0.054932 | 0.018311 | 0.036621 | 0.11902 | 0.018311 | -0.14191 | 0.11444 | 0.07782 | -0.045776 | 0.07782 | 0.059509 | -0.054932 | -0.09613 | 3.4744 | 3.3142 | -118.364 | 3.511 | 3.4927 | 0.17853 | -118.4189 | 3.4012 | 3.36 | -118.4052 | 3.5706 | 3.4103 | 0.050354 | -118.4235 | 3.5751 | 3.5202 | 3.4744 | -118.6249 | 3.5339 | 3.5156 | 3.5339 | -118.5791
5649.1406 | 122.1039 | -3.4241 | 118.4555 | 0.10193 | 0.051895 | 0.058832 | 0.00083745 | 0.029969 | -0.0019632 | 0.029792 | 0.11322 | 0.014875 | 0.024065 | 0.038347 | 0.0059451 | 0.019455 | 0.027466 | 0.018311 | -0.013733 | 0.018311 | 0.11902 | 0 | -0.14191 | 0.10529 | 0.059509 | -0.022888 | 0.050354 | 0.027466 | -0.059509 | -0.07782 | 3.4241 | 3.2822 | -118.3365 | 3.4424 | 3.4424 | 0.16022 | -118.428 | 3.3646 | 3.3463 | -118.4052 | 3.5294 | 3.4012 | 0.054932 | -118.428 | 3.5431 | 3.4515 | 3.4103 | -118.5974 | 3.4744 | 3.4515 | 3.4836 | -118.5333
5650.9062 | 122.0627 | -3.4149 | 118.4692 | 0.071411 | 0.048477 | 0.059686 | 0.0025465 | 0.024842 | -0.0062356 | 0.028083 | 0.15137 | 0.013379 | 0.023424 | 0.035998 | 0.0010317 | 0.019455 | 0.086975 | 0.10986 | 0.11444 | 0.050354 | 0.068665 | 0.059509 | -0.09613 | 0.14191 | 0.10986 | 0.027466 | 0.045776 | 0.041199 | -0.032043 | -0.073242 | 3.4744 | 3.3188 | -118.4006 | 3.5248 | 3.4653 | 0.14648 | -118.3823 | 3.3829 | 3.3417 | -118.4235 | 3.5568 | 3.4424 | 0.10071 | -118.428 | 3.4836 | 3.5019 | 3.5294 | -118.5654 | 3.4607 | 3.4561 | 3.5248 | -118.5425
5652.6094 | 121.9849 | -3.5065 | 118.5013 | 0.033264 | 0.048691 | 0.060327 | -0.00044435 | 0.028047 | 0.0029502 | 0.030219 | -0.054626 | 0.014234 | 0.021074 | 0.036852 | 0.0042361 | 0.015823 | 0.013733 | -0.041199 | -0.050354 | -0.009155 | 0.10071 | -0.004578 | -0.14648 | 0.018311 | -0.013733 | -0.12817 | 0.086975 | 0.059509 | -0.045776 | -0.11444 | 3.5019 | 3.36 | -118.4006 | 3.4653 | 3.4973 | 0.13733 | -118.4875 | 3.4607 | 3.392 | -118.4143 | 3.5248 | 3.3783 | -0.013733 | -118.4418 | 3.6072 | 3.5202 | 3.4561 | -118.6478 | 3.5934 | 3.566 | 3.4927 | -118.6157
5654.375 | 122.0901 | -3.4241 | 118.5287 | 0.018005 | 0.045273 | 0.059259 | 0.0029737 | 0.02826 | -0.0092264 | 0.028937 | 0.082703 | 0.011884 | 0.024705 | 0.035784 | -0.00089089 | 0.018173 | 0.036621 | 0.064087 | 0.059509 | 0.027466 | 0.07782 | 0.045776 | -0.10986 | 0.10529 | 0.091553 | 0.009155 | 0.045776 | 0.041199 | -0.032043 | -0.10071 | 3.4698 | 3.3142 | -118.4509 | 3.4882 | 3.4515 | 0.13733 | -118.4921 | 3.392 | 3.3234 | -118.483 | 3.5294 | 3.4332 | 0.10986 | -118.4875 | 3.5019 | 3.4607 | 3.4836 | -118.6386 | 3.4698 | 3.4653 | 3.5156 | -118.6295
5656.125 | 122.0718 | -3.4149 | 118.5013 | 0.15533 | 0.048691 | 0.059259 | 0.0021191 | 0.028901 | -0.004313 | 0.027656 | 0.15137 | 0.0091066 | 0.023851 | 0.036211 | 0.0025271 | 0.018814 | 0.10071 | 0.1236 | 0.10529 | 0.064087 | 0.07782 | 0.027466 | -0.10986 | 0.15106 | 0.12817 | 0.041199 | 0.027466 | 0.004578 | -0.018311 | -0.068665 | 3.4424 | 3.3051 | -118.4235 | 3.5385 | 3.479 | 0.17395 | -118.4006 | 3.3966 | 3.3463 | -118.4738 | 3.566 | 3.4561 | 0.10986 | -118.4967 | 3.4927 | 3.5156 | 3.5202 | -118.6111 | 3.4424 | 3.4195 | 3.5431 | -118.5699
5657.8906 | 122.113 | -3.3875 | 118.5287 | -0.14984 | 0.048905 | 0.059686 | 0.0048963 | 0.026338 | -0.007731 | 0.026588 | -0.13092 | 0.008893 | 0.024919 | 0.033434 | -3.629e-05 | 0.014968 | 0.10071 | 0.16479 | 0.13733 | 0.086975 | 0.10529 | 0.050354 | -0.11902 | 0.13733 | 0.16479 | 0.064087 | 0.032043 | 0.022888 | -0.027466 | -0.068665 | 3.4378 | 3.2684 | -118.4235 | 3.5522 | 3.4744 | 0.20599 | -118.428 | 3.36 | 3.3188 | -118.4967 | 3.5248 | 3.4515 | 0.13275 | -118.5059 | 3.4927 | 3.4882 | 3.5248 | -118.6478 | 3.4195 | 3.4103 | 3.5522 | -118.5974
5659.6562 | 121.9986 | -3.392 | 118.5883 | -0.04303 | 0.049973 | 0.05755 | 0.0027601 | 0.028901 | 0.001882 | 0.030006 | -0.054626 | 0.015729 | 0.026201 | 0.035143 | 0.0080813 | 0.014968 | 0.054932 | 0.032043 | -0.013733 | 0.013733 | 0.1236 | 0.013733 | -0.14648 | 0.045776 | 0.009155 | -0.10071 | 0.064087 | 0.054932 | -0.068665 | -0.11902 | 3.4058 | 3.2455 | -118.4647 | 3.4241 | 3.4058 | 0.16022 | -118.5333 | 3.3234 | 3.273 | -118.5242 | 3.4378 | 3.2913 | 0.018311 | -118.5333 | 3.5156 | 3.447 | 3.3783 | -118.7347 | 3.4561 | 3.447 | 3.4012 | -118.7073
5661.3594 | 122.049 | -3.3875 | 118.5791 | -0.1651 | 0.047196 | 0.059473 | 0.0059643 | 0.02591 | -0.0055948 | 0.028724 | -0.13855 | 0.012738 | 0.025774 | 0.034716 | -0.00067729 | 0.018814 | 0.082397 | 0.15106 | 0.12817 | 0.068665 | 0.054932 | 0.032043 | -0.1236 | 0.1236 | 0.16937 | 0.050354 | 0.027466 | 0.027466 | -0.036621 | -0.07782 | 3.4195 | 3.2639 | -118.5242 | 3.5385 | 3.4561 | 0.19226 | -118.4967 | 3.3508 | 3.3096 | -118.5516 | 3.511 | 3.4378 | 0.12817 | -118.5516 | 3.4424 | 3.4698 | 3.5156 | -118.7027 | 3.4149 | 3.4149 | 3.5568 | -118.6569
5663.1406 | 122.1268 | -3.3325 | 118.5699 | 0.14771 | 0.047409 | 0.058832 | 0.00041005 | 0.02826 | -4.058e-05 | 0.03086 | 0.10559 | 0.013593 | 0.024278 | 0.036211 | 0.0046633 | 0.017959 | 0.068665 | 0.059509 | 0.050354 | 0.054932 | 0.091553 | 0.032043 | -0.11902 | 0.12817 | 0.11444 | 0.022888 | 0.032043 | 0.013733 | -0.018311 | -0.073242 | 3.3646 | 3.2135 | -118.4784 | 3.392 | 3.3875 | 0.17395 | -118.5013 | 3.3142 | 3.2593 | -118.5379 | 3.4607 | 3.3554 | 0.09613 | -118.5562 | 3.4241 | 3.4012 | 3.3829 | -118.689 | 3.3646 | 3.3463 | 3.447 | -118.6432
5664.9219 | 122.1634 | -3.3096 | 118.6111 | -0.027771 | 0.048477 | 0.061395 | 0.0061781 | 0.027833 | -0.0085856 | 0.026801 | -0.024109 | 0.010816 | 0.023637 | 0.03557 | -0.0028135 | 0.019027 | 0.027466 | 0.082397 | 0.082397 | 0.050354 | 0.086975 | 0.022888 | -0.11902 | 0.11902 | 0.13275 | 0.027466 | 0.045776 | 0.022888 | -0.032043 | -0.091553 | 3.3325 | 3.1906 | -118.5242 | 3.392 | 3.36 | 0.16937 | -118.5837 | 3.2776 | 3.2181 | -118.5654 | 3.4287 | 3.3371 | 0.11902 | -118.5883 | 3.3966 | 3.3371 | 3.392 | -118.7302 | 3.3554 | 3.3325 | 3.4424 | -118.7027
5666.6406 | 122.1588 | -3.3051 | 118.6386 | 0.14008 | 0.049973 | 0.05755 | 0.0012647 | 0.028047 | -0.00089518 | 0.028297 | 0.16663 | 0.013379 | 0.02556 | 0.036425 | 0.0053043 | 0.014541 | 0.036621 | 0.027466 | 0.018311 | 0.013733 | 0.10071 | 0.032043 | -0.12817 | 0.13733 | 0.091553 | 0 | 0.041199 | 0.018311 | -0.022888 | -0.064087 | 3.3371 | 3.1769 | -118.5379 | 3.3325 | 3.3188 | 0.14191 | -118.602 | 3.2822 | 3.241 | -118.5974 | 3.4424 | 3.3051 | 0.064087 | -118.6203 | 3.4058 | 3.3417 | 3.3234 | -118.7668 | 3.3463 | 3.3234 | 3.3966 | -118.7027
5668.4062 | 122.1359 | -3.2913 | 118.6478 | 0.025635 | 0.046982 | 0.0599 | 0.0031873 | 0.024629 | -0.0085856 | 0.025947 | 0.052185 | 0.011029 | 0.022996 | 0.034502 | 0.0014591 | 0.02095 | 0.032043 | 0.073242 | 0.050354 | 0.027466 | 0.064087 | 0.022888 | -0.1236 | 0.07782 | 0.07782 | -0.004578 | 0.032043 | 0.013733 | -0.041199 | -0.09613 | 3.3142 | 3.1677 | -118.5837 | 3.3646 | 3.3188 | 0.15106 | -118.6157 | 3.2501 | 3.1952 | -118.6157 | 3.3691 | 3.2867 | 0.091552 | -118.634 | 3.3554 | 3.3234 | 3.3417 | -118.7714 | 3.3234 | 3.3051 | 3.3691 | -118.7439
5670.1719 | 122.0261 | -3.4103 | 118.6249 | -0.24902 | 0.047623 | 0.061182 | 0.0072461 | 0.028688 | -0.0030314 | 0.02616 | -0.21484 | 0.01402 | 0.026628 | 0.034929 | -0.00046349 | 0.015823 | 0.073242 | 0.09613 | 0.073242 | 0.064087 | 0.068665 | 0.022888 | -0.1236 | 0.07782 | 0.086975 | -0.036621 | 0.059509 | 0.050354 | -0.059509 | -0.09613 | 3.4332 | 3.2867 | -118.5562 | 3.5065 | 3.4744 | 0.18768 | -118.5516 | 3.3508 | 3.3142 | -118.5654 | 3.4882 | 3.3737 | 0.059509 | -118.5745 | 3.479 | 3.4836 | 3.4836 | -118.7485 | 3.4698 | 3.4607 | 3.4973 | -118.721
5671.9219 | 122.0444 | -3.3463 | 118.6935 | -0.18036 | 0.042923 | 0.062036 | 0.00041005 | 0.026765 | -0.0055948 | 0.027442 | -0.19196 | 0.012097 | 0.020006 | 0.036211 | 0.00081811 | 0.018173 | 0.09613 | 0.13733 | 0.091553 | 0.082397 | 0.07782 | 0.018311 | -0.10986 | 0.10071 | 0.15106 | 0.013733 | 0.036621 | 0.032043 | -0.027466 | -0.07782 | 3.3646 | 3.2364 | -118.6157 | 3.4836 | 3.4286 | 0.19226 | -118.5974 | 3.3188 | 3.2684 | -118.6569 | 3.447 | 3.36 | 0.091553 | -118.6615 | 3.4241 | 3.4424 | 3.4378 | -118.8034 | 3.3829 | 3.3783 | 3.4973 | -118.7714
5673.625 | 122.081 | -3.3279 | 118.6386 | 0.071411 | 0.051895 | 0.058191 | 0.0016919 | 0.026338 | 0.00060022 | 0.027869 | 0.036926 | 0.015302 | 0.024492 | 0.036425 | 0.0042361 | 0.016677 | 0.018311 | -0.036621 | -0.045776 | -0.018311 | 0.13275 | -0.018311 | -0.13733 | 0.050354 | -0.009155 | -0.10529 | 0.086975 | 0.064087 | -0.064087 | -0.082397 | 3.3096 | 3.1906 | -118.5059 | 3.2913 | 3.3096 | 0.11902 | -118.6203 | 3.2639 | 3.2455 | -118.5516 | 3.3783 | 3.2227 | -0.022889 | -118.5745 | 3.4607 | 3.3463 | 3.2822 | -118.7759 | 3.4149 | 3.392 | 3.3188 | -118.721
5675.3906 | 122.1588 | -3.3188 | 118.6478 | -0.13458 | 0.047623 | 0.0599 | 0.0023329 | 0.029115 | -0.007731 | 0.028297 | -0.1004 | 0.011884 | 0.021501 | 0.035357 | -0.0011045 | 0.018386 | 0.10986 | 0.14648 | 0.10986 | 0.07782 | 0.054932 | 0.050354 | -0.10529 | 0.15106 | 0.18768 | 0.068665 | 0.032043 | 0.013733 | -0.013733 | -0.086975 | 3.3691 | 3.2135 | -118.5928 | 3.4653 | 3.3966 | 0.18311 | -118.5379 | 3.3051 | 3.2318 | -118.6157 | 3.4698 | 3.3875 | 0.15564 | -118.634 | 3.3737 | 3.4286 | 3.4286 | -118.7531 | 3.3508 | 3.3325 | 3.5065 | -118.7347
5677.1406 | 122.0444 | -3.2135 | 118.8217 | -0.17273 | 0.049332 | 0.058832 | 0.0061781 | 0.026338 | -0.0011088 | 0.027656 | -0.16907 | 0.012738 | 0.023424 | 0.036211 | 0.00081811 | 0.015823 | 0.091553 | 0.11444 | 0.10071 | 0.07782 | 0.064087 | 0.018311 | -0.11444 | 0.10986 | 0.15106 | 0.018311 | 0.045776 | 0.032043 | -0.036621 | -0.082397 | 3.2318 | 3.0991 | -118.7576 | 3.3279 | 3.2913 | 0.19226 | -118.7302 | 3.1769 | 3.1311 | -118.7759 | 3.3234 | 3.2318 | 0.10071 | -118.7897 | 3.2776 | 3.3051 | 3.3142 | -118.9362 | 3.2593 | 3.2455 | 3.3646 | -118.9041
5678.9062 | 122.1634 | -3.1677 | 118.7805 | 0.11719 | 0.048691 | 0.057977 | 0.0019055 | 0.028047 | -0.0028178 | 0.029365 | 0.090332 | 0.014234 | 0.023851 | 0.037279 | 0.0044497 | 0.015823 | 0.054932 | 0.018311 | 0.009155 | 0 | 0.11444 | 0.018311 | -0.13275 | 0.11444 | 0.07782 | -0.018311 | 0.050354 | 0.032043 | -0.013733 | -0.09613 | 3.186 | 3.035 | -118.6661 | 3.186 | 3.1677 | 0.13275 | -118.7256 | 3.154 | 3.0716 | -118.7302 | 3.2822 | 3.1494 | 0.077819 | -118.7485 | 3.2822 | 3.2227 | 3.1769 | -118.9133 | 3.2181 | 3.1998 | 3.2455 | -118.8766
5680.6719 | 122.081 | -3.2227 | 118.8034 | -0.18799 | 0.050827 | 0.059259 | 0.0044691 | 0.029115 | -0.001536 | 0.027015 | -0.21484 | 0.013593 | 0.023851 | 0.035998 | 0.0029543 | 0.015823 | 0.013733 | 0 | -0.018311 | 0.013733 | 0.11444 | 0 | -0.16022 | 0.041199 | 0.050354 | -0.073242 | 0.091553 | 0.064087 | -0.068665 | -0.10529 | 3.2227 | 3.0624 | -118.689 | 3.2227 | 3.2364 | 0.17395 | -118.7897 | 3.154 | 3.1174 | -118.7119 | 3.2639 | 3.1494 | 0.032044 | -118.7393 | 3.3371 | 3.2364 | 3.2043 | -118.9636 | 3.3142 | 3.2867 | 3.273 | -118.9087
5682.4375 | 122.1176 | -3.2043 | 118.7988 | 0.10193 | 0.049332 | 0.058618 | -0.0017261 | 0.028901 | 0.00060022 | 0.029151 | 0.044556 | 0.013593 | 0.026628 | 0.038347 | 0.0038089 | 0.016464 | 0.013733 | -0.032043 | -0.045776 | -0.009155 | 0.12817 | 0.004578 | -0.14648 | 0.050354 | -0.009155 | -0.091553 | 0.07782 | 0.050354 | -0.045776 | -0.12817 | 3.2089 | 3.0579 | -118.6707 | 3.1723 | 3.1952 | 0.13733 | -118.7851 | 3.1586 | 3.0762 | -118.721 | 3.2547 | 3.1128 | 0.036621 | -118.7485 | 3.3325 | 3.2181 | 3.1586 | -118.9453 | 3.2822 | 3.2547 | 3.1952 | -118.927
5684.1562 | 122.0947 | -3.2318 | 118.8171 | -0.20325 | 0.047409 | 0.061609 | 0.0063917 | 0.026979 | -0.008372 | 0.027442 | -0.12329 | 0.011884 | 0.024705 | 0.035357 | -0.0015317 | 0.017318 | 0.064087 | 0.15106 | 0.11444 | 0.082397 | 0.073242 | 0.022888 | -0.11444 | 0.11902 | 0.17853 | 0.050354 | 0.013733 | 0.018311 | -0.032043 | -0.064087 | 3.2547 | 3.1174 | -118.7439 | 3.3829 | 3.3142 | 0.19684 | -118.7531 | 3.1998 | 3.1677 | -118.8034 | 3.3508 | 3.2822 | 0.11444 | -118.7988 | 3.3051 | 3.2959 | 3.3463 | -118.9316 | 3.2455 | 3.2501 | 3.4103 | -118.8812
5685.9062 | 122.0993 | -3.2181 | 118.8263 | -0.12695 | 0.052109 | 0.056268 | 0.0055371 | 0.031037 | 0.00038662 | 0.02851 | -0.14618 | 0.015088 | 0.024492 | 0.038347 | 0.0050907 | 0.016677 | 0.059509 | 0.050354 | 0.009155 | 0.027466 | 0.09613 | 0.032043 | -0.15564 | 0.086975 | 0.082397 | -0.050354 | 0.064087 | 0.054932 | -0.032043 | -0.11444 | 3.2501 | 3.0624 | -118.7302 | 3.2684 | 3.2455 | 0.18311 | -118.7668 | 3.186 | 3.1036 | -118.7622 | 3.3051 | 3.1677 | 0.064087 | -118.7714 | 3.3142 | 3.2776 | 3.2272 | -118.9819 | 3.2822 | 3.273 | 3.3005 | -118.9407
5687.6719 | 122.1451 | -3.1906 | 118.8217 | 0.094299 | 0.043351 | 0.060327 | -0.0010851 | 0.026551 | -0.0075174 | 0.02851 | 0.10559 | 0.013379 | 0.021715 | 0.035998 | 0.00060451 | 0.02095 | 0.054932 | 0.11902 | 0.068665 | 0.036621 | 0.068665 | 0.041199 | -0.10986 | 0.1236 | 0.086975 | 0 | 0.027466 | 0.022888 | -0.027466 | -0.086975 | 3.2318 | 3.0808 | -118.7531 | 3.3096 | 3.2272 | 0.14648 | -118.7668 | 3.1631 | 3.1036 | -118.7942 | 3.3142 | 3.1906 | 0.086975 | -118.7988 | 3.2593 | 3.2455 | 3.2593 | -118.9316 | 3.2181 | 3.2135 | 3.2776 | -118.9087
5689.375 | 122.1222 | -3.1815 | 118.8309 | 0.10956 | 0.0504 | 0.060114 | 0.0019055 | 0.026124 | 0.00060022 | 0.029578 | 0.044556 | 0.015088 | 0.022783 | 0.037066 | 0.0070133 | 0.016464 | 0.004578 | -0.036621 | -0.045776 | -0.004578 | 0.12817 | 0 | -0.15564 | 0.041199 | -0.013733 | -0.082397 | 0.07782 | 0.059509 | -0.045776 | -0.10986 | 3.1815 | 3.0258 | -118.7027 | 3.1448 | 3.1769 | 0.15106 | -118.8263 | 3.1357 | 3.0716 | -118.7531 | 3.2227 | 3.0991 | 0.027466 | -118.7714 | 3.3096 | 3.186 | 3.1357 | -118.9865 | 3.2593 | 3.241 | 3.1677 | -118.9407
5691.1406 | 122.1222 | -3.3005 | 118.7759 | -0.15747 | 0.0504 | 0.058405 | 0.0044691 | 0.026551 | -0.0021768 | 0.030006 | -0.16907 | 0.015088 | 0.025774 | 0.034929 | 0.0063723 | 0.016464 | 0.050354 | 0.022888 | 0.004578 | 0.013733 | 0.10529 | -0.009155 | -0.13733 | 0.073242 | 0.07782 | -0.059509 | 0.07782 | 0.064087 | -0.041199 | -0.11444 | 3.2913 | 3.1631 | -118.6707 | 3.3234 | 3.3142 | 0.15106 | -118.7256 | 3.2593 | 3.186 | -118.6981 | 3.3737 | 3.241 | 0.054932 | -118.7119 | 3.4058 | 3.3508 | 3.3051 | -118.9133 | 3.3783 | 3.3646 | 3.3783 | -118.8904
5692.8438 | 122.081 | -3.2867 | 118.7897 | -0.14984 | 0.050614 | 0.059473 | 0.0061781 | 0.027833 | -0.004313 | 0.026588 | -0.18433 | 0.014234 | 0.026628 | 0.037279 | -0.0011045 | 0.019455 | -0.009155 | 0.022888 | -0.004578 | -0.004578 | 0.11902 | -0.004578 | -0.16022 | 0.013733 | 0.041199 | -0.064087 | 0.086975 | 0.073242 | -0.054932 | -0.1236 | 3.2822 | 3.1265 | -118.6707 | 3.3096 | 3.2822 | 0.15564 | -118.7988 | 3.2318 | 3.1631 | -118.7027 | 3.3005 | 3.2227 | 0.059509 | -118.7164 | 3.4058 | 3.2776 | 3.2822 | -118.9499 | 3.3737 | 3.36 | 3.3279 | -118.9133
5694.6094 | 122.1542 | -3.2272 | 118.7988 | 0.033264 | 0.04805 | 0.060754 | 0.0048963 | 0.027619 | -0.0081582 | 0.028297 | 0.075073 | 0.012525 | 0.026414 | 0.034716 | 0.00060451 | 0.017959 | 0.022888 | 0.073242 | 0.059509 | 0.027466 | 0.054932 | 0.045776 | -0.11444 | 0.086975 | 0.082397 | 0.009155 | 0.045776 | 0.022888 | -0.032043 | -0.07782 | 3.273 | 3.1128 | -118.7439 | 3.3005 | 3.2547 | 0.14191 | -118.7759 | 3.1952 | 3.1494 | -118.7531 | 3.3142 | 3.2364 | 0.086975 | -118.7759 | 3.2822 | 3.2501 | 3.2867 | -118.9133 | 3.273 | 3.2501 | 3.3096 | -118.8766
5696.375 | 122.1588 | -3.2181 | 118.8263 | 0.08667 | 0.049118 | 0.058618 | 0.0059643 | 0.026765 | -0.0038858 | 0.028297 | 0.10559 | 0.012525 | 0.025774 | 0.035998 | 0.00081811 | 0.017532 | 0.09613 | 0.1236 | 0.10071 | 0.064087 | 0.054932 | 0.041199 | -0.10986 | 0.16022 | 0.1236 | 0.041199 | 0.036621 | 0.036621 | -0.018311 | -0.073242 | 3.2593 | 3.1082 | -118.7714 | 3.3417 | 3.2822 | 0.17395 | -118.7302 | 3.1998 | 3.1448 | -118.7897 | 3.3783 | 3.2593 | 0.11444 | -118.7897 | 3.273 | 3.3142 | 3.3188 | -118.9362 | 3.2547 | 3.2547 | 3.3417 | -118.8995
5698.1562 | 122.2229 | -3.1906 | 118.8126 | 0.14771 | 0.047837 | 0.057336 | 0.0051099 | 0.026551 | -0.0023904 | 0.02851 | 0.052185 | 0.013166 | 0.024065 | 0.036852 | 0.0023135 | 0.015182 | 0.086975 | 0.059509 | 0.054932 | 0.045776 | 0.082397 | 0.036621 | -0.12817 | 0.12817 | 0.11444 | 0.032043 | 0.041199 | 0.004578 | -0.013733 | -0.07782 | 3.2272 | 3.0624 | -118.7302 | 3.2501 | 3.2364 | 0.17395 | -118.7256 | 3.1769 | 3.1128 | -118.7714 | 3.3188 | 3.2227 | 0.10986 | -118.808 | 3.273 | 3.2776 | 3.2455 | -118.9407 | 3.2318 | 3.1952 | 3.3051 | -118.8904
5699.875 | 122.1085 | -3.2364 | 118.8538 | 0.025635 | 0.049759 | 0.057336 | 0.00041005 | 0.028688 | 0.00038662 | 0.029151 | 0.036926 | 0.015515 | 0.022569 | 0.039416 | 0.0040225 | 0.018173 | -0.004578 | -0.045776 | -0.059509 | -0.013733 | 0.11902 | -0.009155 | -0.14191 | 0.036621 | -0.018311 | -0.10986 | 0.068665 | 0.059509 | -0.054932 | -0.1236 | 3.2272 | 3.0945 | -118.7347 | 3.1906 | 3.2227 | 0.12817 | -118.8583 | 3.1815 | 3.1128 | -118.7851 | 3.273 | 3.1265 | 0.013733 | -118.7943 | 3.3554 | 3.2318 | 3.1769 | -118.9957 | 3.3051 | 3.2959 | 3.2181 | -118.9774
5701.6406 | 122.2275 | -3.1128 | 118.9041 | -0.0354 | 0.046128 | 0.057764 | 0.0019055 | 0.024842 | -0.0096536 | 0.027656 | 0.044556 | 0.01167 | 0.024065 | 0.034502 | -0.00089089 | 0.020523 | 0 | 0.054932 | 0.064087 | 0.036621 | 0.091553 | 0.022888 | -0.10986 | 0.11444 | 0.09613 | 0.041199 | 0.045776 | 0.045776 | -0.050354 | -0.091553 | 3.1357 | 3.0029 | -118.8126 | 3.1677 | 3.1494 | 0.14648 | -118.9041 | 3.0624 | 3.0212 | -118.8583 | 3.2272 | 3.154 | 0.13275 | -118.8583 | 3.2043 | 3.1128 | 3.1769 | -119.014 | 3.1586 | 3.1586 | 3.2089 | -118.9957
5703.4062 | 122.1405 | -3.1815 | 118.8721 | -0.17273 | 0.048477 | 0.061182 | -1.7146e-05 | 0.024629 | -0.0013224 | 0.027869 | -0.19958 | 0.01402 | 0.024278 | 0.037066 | 0.0033817 | 0.015823 | 0.027466 | 0.027466 | 0.004578 | 0.027466 | 0.11444 | 0.004578 | -0.16479 | 0.064087 | 0.059509 | -0.059509 | 0.07782 | 0.068665 | -0.059509 | -0.10986 | 3.186 | 3.0167 | -118.7576 | 3.2089 | 3.2089 | 0.19226 | -118.8446 | 3.1219 | 3.0716 | -118.7942 | 3.2455 | 3.1219 | 0.050354 | -118.8034 | 3.2959 | 3.2089 | 3.186 | -119.0369 | 3.2593 | 3.2501 | 3.241 | -118.9819
5705.1094 | 122.081 | -3.1586 | 118.9453 | -0.088806 | 0.051895 | 0.057977 | 0.0048963 | 0.028474 | 0.00081382 | 0.032569 | -0.11566 | 0.015302 | 0.025987 | 0.037279 | 0.0027407 | 0.016464 | 0.09613 | 0.045776 | 0.041199 | 0.041199 | 0.091553 | 0.009155 | -0.15106 | 0.073242 | 0.068665 | -0.054932 | 0.064087 | 0.050354 | -0.054932 | -0.10529 | 3.1677 | 3.0075 | -118.8538 | 3.2043 | 3.1998 | 0.19226 | -118.8492 | 3.1036 | 3.0533 | -118.8812 | 3.2318 | 3.1036 | 0.050354 | -118.895 | 3.2501 | 3.2547 | 3.1998 | -119.0964 | 3.2227 | 3.2089 | 3.2272 | -119.0506
5706.875 | 122.1497 | -3.1586 | 118.9133 | 0.10956 | 0.04805 | 0.0599 | 0.00062385 | 0.028474 | 0.00081382 | 0.028937 | 0.082703 | 0.014234 | 0.02556 | 0.038134 | 0.0038089 | 0.018173 | 0.004578 | -0.032043 | -0.050354 | -0.022888 | 0.1236 | 0 | -0.14648 | 0.032043 | 0 | -0.091553 | 0.064087 | 0.068665 | -0.068665 | -0.11444 | 3.1586 | 3.0121 | -118.7897 | 3.1265 | 3.1357 | 0.1236 | -118.9087 | 3.0899 | 3.0441 | -118.8492 | 3.1906 | 3.067 | 0.022888 | -118.8446 | 3.2822 | 3.1631 | 3.1082 | -119.0598 | 3.2227 | 3.2272 | 3.1586 | -119.0277
5708.5781 | 122.0993 | -3.1677 | 118.927 | -0.25665 | 0.052536 | 0.059259 | 0.0095959 | 0.02826 | -0.0070902 | 0.026374 | -0.26825 | 0.012097 | 0.024705 | 0.035784 | -0.0011045 | 0.0186 | 0.004578 | 0.045776 | 0.009155 | 0.018311 | 0.11444 | 0.009155 | -0.13733 | 0.032043 | 0.050354 | -0.073242 | 0.064087 | 0.054932 | -0.064087 | -0.10529 | 3.1769 | 3.0304 | -118.8126 | 3.2135 | 3.186 | 0.15564 | -118.9224 | 3.1036 | 3.0624 | -118.8629 | 3.1998 | 3.0945 | 0.032044 | -118.8721 | 3.2822 | 3.1723 | 3.1769 | -119.0643 | 3.2318 | 3.2227 | 3.2181 | -119.0323
5710.3438 | 122.1039 | -3.1586 | 118.9362 | -0.020142 | 0.049759 | 0.057336 | -0.00023075 | 0.026551 | -0.0011088 | 0.028083 | -0.0088499 | 0.014234 | 0.025133 | 0.039416 | 0.0053043 | 0.019027 | 0 | -0.045776 | -0.032043 | -0.009155 | 0.09613 | 0.004578 | -0.15106 | -0.004578 | -0.004578 | -0.11902 | 0.086975 | 0.068665 | -0.082397 | -0.12817 | 3.1631 | 3.0075 | -118.84 | 3.1128 | 3.1494 | 0.14191 | -118.9362 | 3.0762 | 3.0304 | -118.8492 | 3.154 | 3.0395 | 0.009155 | -118.8675 | 3.2547 | 3.1586 | 3.1265 | -119.0872 | 3.2455 | 3.2272 | 3.154 | -119.0643
5712.0469 | 122.1542 | -3.1769 | 118.9041 | -0.19562 | 0.047623 | 0.062463 | 0.0061781 | 0.028688 | -0.0092264 | 0.027869 | -0.10803 | 0.01167 | 0.025346 | 0.034075 | -0.0011045 | 0.018814 | 0.068665 | 0.14191 | 0.12817 | 0.086975 | 0.068665 | 0.027466 | -0.13275 | 0.1236 | 0.17395 | 0.041199 | 0.022888 | 0.013733 | -0.018311 | -0.07782 | 3.2043 | 3.0441 | -118.8354 | 3.3188 | 3.2639 | 0.21973 | -118.8354 | 3.1586 | 3.0991 | -118.8812 | 3.3005 | 3.2181 | 0.11902 | -118.8904 | 3.2455 | 3.2455 | 3.3051 | -119.0369 | 3.1998 | 3.1906 | 3.3508 | -118.9819
5713.7969 | 122.1085 | -3.2043 | 118.8995 | -0.096436 | 0.050827 | 0.057764 | 0.0048963 | 0.027406 | -0.0021768 | 0.028297 | -0.13855 | 0.015088 | 0.026201 | 0.039416 | 0.0031681 | 0.014755 | 0.059509 | 0.045776 | 0.022888 | 0.041199 | 0.10529 | 0.009155 | -0.14648 | 0.091553 | 0.07782 | -0.054932 | 0.068665 | 0.050354 | -0.054932 | -0.09613 | 3.2135 | 3.0579 | -118.7942 | 3.2501 | 3.2455 | 0.18768 | -118.84 | 3.1494 | 3.1082 | -118.8309 | 3.2959 | 3.1494 | 0.041198 | -118.8492 | 3.3096 | 3.2639 | 3.2272 | -119.046 | 3.273 | 3.2547 | 3.2822 | -118.9957
5715.5781 | 122.1588 | -3.2364 | 118.84 | -0.19562 | 0.0504 | 0.059259 | 0.00019645 | 0.026765 | -0.0021768 | 0.026801 | -0.19196 | 0.014234 | 0.024278 | 0.035784 | 0.0038089 | 0.017318 | 0.013733 | 0.013733 | -0.022888 | 0.032043 | 0.10529 | 0.004578 | -0.15106 | 0.050354 | 0.068665 | -0.054932 | 0.059509 | 0.050354 | -0.068665 | -0.09613 | 3.241 | 3.0853 | -118.7347 | 3.2501 | 3.2684 | 0.18311 | -118.8263 | 3.1677 | 3.1403 | -118.7805 | 3.2867 | 3.1815 | 0.041198 | -118.7897 | 3.3417 | 3.2501 | 3.2135 | -118.9911 | 3.2959 | 3.2867 | 3.3051 | -118.9362
5717.2812 | 122.2229 | -3.2089 | 118.8217 | 0.056152 | 0.04805 | 0.060541 | 0.0016919 | 0.026765 | -0.004954 | 0.030219 | 0.13611 | 0.01402 | 0.02556 | 0.035784 | 0.0050907 | 0.0186 | 0.009155 | -0.013733 | -0.032043 | -0.009155 | 0.10986 | 0.004578 | -0.15564 | 0.064087 | 0.009155 | -0.032043 | 0.064087 | 0.054932 | -0.050354 | -0.09613 | 3.2135 | 3.0533 | -118.7119 | 3.1952 | 3.1998 | 0.14649 | -118.8126 | 3.1586 | 3.1128 | -118.7576 | 3.273 | 3.1769 | 0.064087 | -118.7668 | 3.3188 | 3.2181 | 3.1769 | -118.9774 | 3.273 | 3.2639 | 3.2181 | -118.9178
5719.0469 | 122.2458 | -3.2181 | 118.8263 | -0.012512 | 0.044419 | 0.059686 | 0.0034009 | 0.030183 | -0.011363 | 0.027442 | 0.052185 | 0.011884 | 0.022569 | 0.03557 | -0.0021725 | 0.019455 | 0.013733 | 0.050354 | 0.059509 | 0.036621 | 0.086975 | 0.022888 | -0.11902 | 0.086975 | 0.091553 | 0.032043 | 0.041199 | 0.045776 | -0.027466 | -0.091553 | 3.241 | 3.0991 | -118.7393 | 3.2684 | 3.2547 | 0.15564 | -118.8126 | 3.1906 | 3.1265 | -118.7851 | 3.3051 | 3.2501 | 0.1236 | -118.7805 | 3.3051 | 3.2318 | 3.2776 | -118.9453 | 3.2593 | 3.2639 | 3.3096 | -118.9178
5720.75 | 122.2321 | -3.2135 | 118.84 | -0.1651 | 0.049118 | 0.058191 | 0.0074597 | 0.026979 | -0.0098672 | 0.027656 | -0.13855 | 0.011029 | 0.026201 | 0.034502 | -0.0011045 | 0.016037 | 0.086975 | 0.14648 | 0.1236 | 0.086975 | 0.068665 | 0.027466 | -0.10529 | 0.13733 | 0.1831 | 0.064087 | 0.032043 | 0.036621 | -0.027466 | -0.068665 | 3.241 | 3.1082 | -118.7714 | 3.36 | 3.3005 | 0.19226 | -118.7531 | 3.186 | 3.1448 | -118.808 | 3.3508 | 3.2776 | 0.13275 | -118.8034 | 3.2822 | 3.3005 | 3.3371 | -118.9453 | 3.2455 | 3.2501 | 3.3966 | -118.9087
5722.5156 | 121.3577 | -39.6149 | 80.8685 | 0.08667 | 0.049759 | 0.060541 | 0.00062385 | 0.027619 | -0.0023904 | 0.029151 | 0.10559 | 0.014875 | 0.024705 | 0.036425 | 0.0050907 | 0.017532 | 0.032043 | -0.009155 | -0.022888 | 0.004578 | 0.10986 | 0 | -0.13275 | 0.068665 | 0.004578 | -0.059509 | 0.050354 | 0.045776 | -0.050354 | -0.10071 | 39.6149 | 39.4821 | -80.7587 | 39.6057 | 39.6194 | 0.13733 | -80.8365 | 39.5645 | 39.5142 | -80.8182 | 39.6835 | 39.5554 | 0.041199 | -80.8228 | 39.7247 | 39.6469 | 39.592 | -81.0013 | 39.6652 | 39.6606 | 39.6194 | -80.9692
5724.2188 | 120.7123 | -11.6592 | 109.7397 | -0.21088 | 0.052964 | 0.058618 | 0.0053235 | 0.028047 | -0.00025418 | 0.029151 | -0.1767 | 0.013593 | 0.026414 | 0.036211 | 0.0010317 | 0.016037 | -0.004578 | 0.004578 | -0.027466 | 0.004578 | 0.13733 | -0.004578 | -0.14648 | 0.027466 | 0.041199 | -0.086975 | 0.082397 | 0.059509 | -0.032043 | -0.11902 | 11.6547 | 11.5128 | -109.6024 | 11.6638 | 11.6638 | 0.15106 | -109.7443 | 11.6272 | 11.5402 | -109.6573 | 11.6867 | 11.5723 | 0.032044 | -109.6802 | 11.7966 | 11.6547 | 11.6318 | -109.8862 | 11.7416 | 11.7188 | 11.7004 | -109.8587
5725.9844 | 121.6049 | -10.3317 | 111.1633 | -0.1651 | 0.049759 | 0.058832 | 0.0066053 | 0.027192 | -0.0085856 | 0.027015 | -0.092773 | 0.010388 | 0.024705 | 0.036852 | -3.629e-05 | 0.015609 | 0.068665 | 0.13275 | 0.10986 | 0.086975 | 0.068665 | 0.027466 | -0.11902 | 0.10529 | 0.15106 | 0.032043 | 0.036621 | 0.036621 | -0.013733 | -0.073242 | 10.3592 | 10.2127 | -111.0947 | 10.4645 | 10.4187 | 0.20599 | -111.0947 | 10.318 | 10.2585 | -111.1267 | 10.437 | 10.3638 | 0.10529 | -111.1267 | 10.4004 | 10.4004 | 10.4416 | -111.2823 | 10.3683 | 10.3683 | 10.4828 | -111.2366
5727.6875 | 121.6049 | -9.819 | 111.6074 | 0.018005 | 0.043778 | 0.061182 | 0.00041005 | 0.026551 | -0.0062356 | 0.026374 | 0.075073 | 0.012952 | 0.021928 | 0.036638 | 0.0025271 | 0.017746 | 0.041199 | 0.082397 | 0.059509 | 0.041199 | 0.073242 | 0.036621 | -0.10071 | 0.10986 | 0.082397 | -0.004578 | 0.054932 | 0.045776 | -0.009155 | -0.082397 | 9.8557 | 9.7183 | -111.5341 | 9.9014 | 9.8602 | 0.14191 | -111.5662 | 9.8099 | 9.7366 | -111.5524 | 9.9289 | 9.8145 | 0.077819 | -111.5616 | 9.8923 | 9.8602 | 9.8785 | -111.7081 | 9.874 | 9.8648 | 9.9014 | -111.6898
5729.4531 | 121.7377 | -11.0046 | 110.5453 | -0.0048827 | 0.044632 | 0.062463 | 0.00041005 | 0.026338 | -0.0075174 | 0.028083 | 0.036926 | 0.011457 | 0.022142 | 0.035784 | 0.0020999 | 0.019027 | 0.018311 | 0.07782 | 0.050354 | 0.045776 | 0.082397 | 0.036621 | -0.1236 | 0.073242 | 0.086975 | 0.013733 | 0.045776 | 0.027466 | -0.032043 | -0.073242 | 11.0413 | 10.881 | -110.463 | 11.0825 | 11.0504 | 0.16937 | -110.527 | 10.9726 | 10.9314 | -110.4996 | 11.0779 | 11.0184 | 0.086975 | -110.5179 | 11.087 | 11.0229 | 11.055 | -110.6689 | 11.0504 | 11.0321 | 11.0916 | -110.6186
5731.1562 | 121.0922 | -19.6152 | 102.475 | -0.012512 | 0.048477 | 0.058191 | -0.00044435 | 0.03061 | -0.00025418 | 0.028297 | -0.10803 | 0.014875 | 0.025987 | 0.036852 | 0.0059451 | 0.017959 | 0.064087 | 0.032043 | -0.004578 | 0 | 0.10986 | 0 | -0.13275 | 0.054932 | 0.013733 | -0.09613 | 0.082397 | 0.045776 | -0.050354 | -0.10529 | 19.6152 | 19.4824 | -102.3651 | 19.6472 | 19.6152 | 0.13275 | -102.4109 | 19.5648 | 19.5099 | -102.3926 | 19.6701 | 19.519 | 0.009156 | -102.4292 | 19.725 | 19.6793 | 19.6106 | -102.6077 | 19.6976 | 19.6609 | 19.6289 | -102.5803
5732.9219 | 121.3989 | -14.2914 | 107.4371 | -0.11169 | 0.048691 | 0.060754 | 0.0066053 | 0.026551 | -0.006022 | 0.030219 | -0.2301 | 0.012952 | 0.023851 | 0.034502 | -0.0025999 | 0.017959 | 0.082397 | 0.10986 | 0.09613 | 0.068665 | 0.073242 | 0.027466 | -0.10071 | 0.086975 | 0.12817 | 0.004578 | 0.045776 | 0.036621 | -0.045776 | -0.07782 | 14.3188 | 14.1907 | -107.3639 | 14.4012 | 14.36 | 0.16937 | -107.3547 | 14.2456 | 14.2136 | -107.3914 | 14.3784 | 14.296 | 0.082398 | -107.4005 | 14.3646 | 14.3738 | 14.3875 | -107.5378 | 14.3372 | 14.328 | 14.4196 | -107.515
5734.6406 | 121.8246 | -10.3226 | 111.3007 | -0.050659 | 0.047196 | 0.058618 | 0.0031873 | 0.027833 | -0.0079446 | 0.026588 | -0.031738 | 0.011457 | 0.024065 | 0.034289 | 0.00017731 | 0.017532 | 0.045776 | 0.082397 | 0.07782 | 0.045776 | 0.07782 | 0.022888 | -0.1236 | 0.11444 | 0.11444 | 0.032043 | 0.041199 | 0.027466 | -0.032043 | -0.082397 | 10.3455 | 10.199 | -111.2228 | 10.405 | 10.3683 | 0.16937 | -111.2549 | 10.2905 | 10.2402 | -111.2595 | 10.437 | 10.3546 | 0.11444 | -111.2732 | 10.4004 | 10.3683 | 10.4004 | -111.4243 | 10.3638 | 10.35 | 10.437 | -111.3831
5736.4062 | 121.669 | -10.5698 | 111.1084 | -0.088806 | 0.050827 | 0.05755 | -0.00065795 | 0.029756 | 0.00081382 | 0.025947 | -0.15381 | 0.013593 | 0.022996 | 0.037279 | 0.0044497 | 0.014328 | 0.10071 | 0.054932 | 0.018311 | 0.027466 | 0.091553 | 0.013733 | -0.13275 | 0.073242 | 0.068665 | -0.050354 | 0.073242 | 0.054932 | -0.054932 | -0.09613 | 10.5835 | 10.437 | -111.0168 | 10.6247 | 10.5972 | 0.16022 | -111.0077 | 10.5148 | 10.4736 | -111.0352 | 10.643 | 10.5194 | 0.045776 | -111.0535 | 10.6613 | 10.6705 | 10.5881 | -111.2411 | 10.643 | 10.6247 | 10.6384 | -111.2045
5738.1719 | 121.843 | -25.6531 | 95.9244 | -0.0048827 | 0.047837 | 0.061609 | 0.0044691 | 0.027406 | -0.0079446 | 0.025092 | 0.059815 | 0.011457 | 0.02556 | 0.034289 | 0.0010317 | 0.018173 | 0.027466 | 0.054932 | 0.064087 | 0.027466 | 0.07782 | 0.027466 | -0.10986 | 0.07782 | 0.091553 | 0 | 0.027466 | 0.027466 | -0.013733 | -0.091553 | 25.6805 | 25.5432 | -95.8466 | 25.708 | 25.6805 | 0.13733 | -95.8969 | 25.6393 | 25.5615 | -95.8969 | 25.7309 | 25.6531 | 0.091553 | -95.8969 | 25.7309 | 25.6805 | 25.7172 | -96.0342 | 25.6805 | 25.6805 | 25.7446 | -96.0159
5739.9375 | 121.7972 | -26.0422 | 95.549 | 0.094299 | 0.049332 | 0.058405 | -0.00044435 | 0.027192 | -0.0011088 | 0.027869 | 0.067444 | 0.016156 | 0.022783 | 0.037066 | 0.0050907 | 0.0139 | 0.064087 | 0.07782 | 0.041199 | 0.041199 | 0.07782 | 0.032043 | -0.10529 | 0.13275 | 0.1236 | 0.013733 | 0.027466 | 0.004578 | -0.013733 | -0.086975 | 26.0742 | 25.9369 | -95.4712 | 26.12 | 26.0834 | 0.14649 | -95.4849 | 26.0284 | 25.9552 | -95.5215 | 26.1749 | 26.0559 | 0.10071 | -95.5444 | 26.12 | 26.1063 | 26.0834 | -95.6543 | 26.0696 | 26.0468 | 26.1658 | -95.636
5741.7031 | 121.8613 | -17.7017 | 103.9856 | -0.020142 | 0.046982 | 0.061823 | 0.0016919 | 0.026979 | -0.0090128 | 0.026801 | 0.0064086 | 0.011243 | 0.02321 | 0.034929 | 0.0012455 | 0.021164 | 0.009155 | 0.07782 | 0.068665 | 0.036621 | 0.07782 | 0.013733 | -0.13733 | 0.09613 | 0.09613 | 0.027466 | 0.032043 | 0.027466 | -0.022888 | -0.086975 | 17.7155 | 17.5644 | -103.9078 | 17.7795 | 17.7383 | 0.17395 | -103.9764 | 17.6788 | 17.6147 | -103.9536 | 17.7979 | 17.7292 | 0.11444 | -103.9581 | 17.7795 | 17.7109 | 17.7704 | -104.1229 | 17.7338 | 17.7292 | 17.7979 | -104.0726
5743.4062 | 121.17 | -13.9389 | 107.7942 | -0.11932 | 0.050614 | 0.055627 | 0.0046827 | 0.02826 | 0.00081382 | 0.027228 | -0.16907 | 0.015088 | 0.023424 | 0.036852 | 0.0050907 | 0.013473 | 0.086975 | 0.050354 | 0.018311 | 0.032043 | 0.10986 | 0.018311 | -0.13275 | 0.09613 | 0.086975 | -0.045776 | 0.064087 | 0.068665 | -0.036621 | -0.11444 | 13.9572 | 13.8062 | -107.6843 | 13.9893 | 13.9709 | 0.16479 | -107.7072 | 13.9023 | 13.8245 | -107.7301 | 14.035 | 13.8931 | 0.068665 | -107.7255 | 14.0488 | 14.0259 | 13.9572 | -107.9269 | 14.003 | 14.0076 | 14.0259 | -107.9086
5745.2188 | 121.7148 | -14.2181 | 107.5424 | 0.040894 | 0.049332 | 0.058618 | 0.0021191 | 0.026551 | 0.001882 | 0.028297 | -0.046997 | 0.014234 | 0.025987 | 0.03792 | 0.0042361 | 0.017105 | 0.004578 | -0.041199 | -0.054932 | 0 | 0.11444 | 0 | -0.17853 | 0.013733 | -0.022888 | -0.13275 | 0.073242 | 0.064087 | -0.050354 | -0.10529 | 14.2181 | 14.0396 | -107.428 | 14.1769 | 14.2181 | 0.17853 | -107.5378 | 14.1678 | 14.1129 | -107.4692 | 14.2319 | 14.0854 | -0.027465 | -107.4783 | 14.3326 | 14.2227 | 14.1632 | -107.7209 | 14.2914 | 14.2822 | 14.1953 | -107.6477
5746.9375 | 121.9391 | -17.6514 | 103.8437 | 0.10193 | 0.048691 | 0.060327 | 0.00083745 | 0.026338 | -0.0028178 | 0.028297 | 0.14374 | 0.012311 | 0.024492 | 0.03557 | 0.0046633 | 0.017318 | 0.045776 | 0.032043 | 0.013733 | 0.013733 | 0.10986 | 0.009155 | -0.1236 | 0.10986 | 0.068665 | 0 | 0.050354 | 0.036621 | -0.022888 | -0.064087 | 17.6605 | 17.5278 | -103.7338 | 17.6834 | 17.6651 | 0.13733 | -103.7979 | 17.6285 | 17.5873 | -103.7933 | 17.7612 | 17.6514 | 0.064087 | -103.8071 | 17.7612 | 17.6971 | 17.6651 | -103.9673 | 17.7017 | 17.688 | 17.72 | -103.9078
5748.7031 | 121.9482 | -23.5886 | 98.0621 | -0.065918 | 0.048477 | 0.059045 | 0.0048963 | 0.028047 | -0.0092264 | 0.028297 | -0.024109 | 0.012097 | 0.026842 | 0.034716 | -0.00046349 | 0.018814 | 0.022888 | 0.10529 | 0.07782 | 0.050354 | 0.082397 | 0.027466 | -0.11902 | 0.1236 | 0.13275 | 0.054932 | 0.045776 | 0.036621 | -0.041199 | -0.07782 | 23.616 | 23.4695 | -97.9797 | 23.6938 | 23.6389 | 0.16937 | -98.0392 | 23.5474 | 23.5107 | -98.0164 | 23.7122 | 23.6435 | 0.13275 | -98.0255 | 23.671 | 23.6114 | 23.6664 | -98.1812 | 23.6343 | 23.6252 | 23.7213 | -98.14
5750.4375 | 121.9025 | -31.1234 | 90.5319 | 0.08667 | 0.046341 | 0.058405 | 0.0063917 | 0.028688 | -0.0047404 | 0.026588 | 0.12848 | 0.012738 | 0.024065 | 0.036638 | 0.0010317 | 0.019882 | 0.082397 | 0.11444 | 0.10529 | 0.054932 | 0.073242 | 0.022888 | -0.10986 | 0.1236 | 0.09613 | 0.009155 | 0.045776 | 0.018311 | -0.027466 | -0.082397 | 31.1462 | 31.0135 | -90.4587 | 31.2378 | 31.1783 | 0.16479 | -90.4495 | 31.0959 | 31.041 | -90.4861 | 31.2469 | 31.1325 | 0.091552 | -90.5136 | 31.1966 | 31.2057 | 31.2286 | -90.6418 | 31.1691 | 31.1417 | 31.2195 | -90.6143
5752.2031 | 121.9025 | -28.0289 | 93.6356 | 0.033264 | 0.044632 | 0.060754 | 0.0016919 | 0.027619 | -0.006022 | 0.025306 | 0.067444 | 0.011243 | 0.02556 | 0.033007 | 0.0018863 | 0.019027 | 0.036621 | 0.073242 | 0.059509 | 0.036621 | 0.07782 | 0.032043 | -0.091553 | 0.086975 | 0.082397 | 0.009155 | 0.027466 | 0.018311 | -0.032043 | -0.086975 | 28.0609 | 27.9373 | -93.5577 | 28.1021 | 28.0655 | 0.12817 | -93.5989 | 27.9968 | 27.9419 | -93.6081 | 28.1158 | 28.038 | 0.09613 | -93.6172 | 28.1067 | 28.0655 | 28.0884 | -93.7271 | 28.0563 | 28.0472 | 28.1113 | -93.7225
5753.9688 | 121.9391 | -28.2669 | 93.4708 | -0.14984 | 0.047837 | 0.059473 | 0.0042555 | 0.026551 | -0.006663 | 0.026588 | -0.1004 | 0.011457 | 0.024492 | 0.034289 | -0.0019589 | 0.01625 | 0.091553 | 0.13733 | 0.11444 | 0.073242 | 0.082397 | 0.032043 | -0.11444 | 0.16022 | 0.15106 | 0.068665 | 0.018311 | 0.018311 | -0.018311 | -0.059509 | 28.299 | 28.1525 | -93.3884 | 28.4042 | 28.3401 | 0.18768 | -93.3792 | 28.2486 | 28.2074 | -93.4525 | 28.4271 | 28.3356 | 0.12817 | -93.4525 | 28.3493 | 28.3585 | 28.3813 | -93.5852 | 28.2852 | 28.2852 | 28.418 | -93.5303
5755.75 | 121.312 | -43.7119 | 84.6542 | 0.15533 | 0.048264 | 0.05755 | 0.0014783 | 0.02591 | 0.001882 | 0.027015 | 0.12085 | 0.015088 | 0.020006 | 0.037493 | 0.0038089 | 0.014328 | 0.064087 | 0.022888 | 0.004578 | 0.027466 | 0.10071 | 0.022888 | -0.11902 | 0.13275 | 0.091553 | -0.009155 | 0.050354 | 0.036621 | -0.032043 | -0.07782 | 43.7347 | 43.5928 | -84.5535 | 43.7347 | 43.7393 | 0.14649 | -84.5901 | 43.6798 | 43.634 | -84.6039 | 43.8446 | 43.7027 | 0.068665 | -84.6176 | 43.8126 | 43.7759 | 43.7164 | -84.7733 | 43.7622 | 43.7485 | 43.8034 | -84.7321
5757.5156 | 122.0856 | -118.364 | 3.2272 | 0.13245 | 0.049332 | 0.059259 | 0.0012647 | 0.026338 | -0.0040994 | 0.028724 | 0.13611 | 0.014447 | 0.023637 | 0.035998 | 0.0031681 | 0.016037 | 0.11444 | 0.1236 | 0.11444 | 0.068665 | 0.07782 | 0.050354 | -0.091553 | 0.15564 | 0.14648 | 0.050354 | 0.027466 | 0.022888 | -0.018311 | -0.073242 | 118.4143 | 118.2724 | -3.1494 | 118.4875 | 118.4326 | 0.16022 | -3.1128 | 118.3456 | 118.2907 | -3.1998 | 118.5196 | 118.4143 | 0.1236 | -3.2043 | 118.4418 | 118.4784 | 118.4784 | -3.3188 | 118.3914 | 118.3868 | 118.5104 | -3.3005
5759.2812 | 122.1497 | -119.6915 | 1.9913 | -0.050659 | 0.047409 | 0.057336 | 0.0029737 | 0.024201 | -0.0051676 | 0.027228 | -0.077515 | 0.011243 | 0.02321 | 0.035143 | 0.00060451 | 0.016891 | 0.073242 | 0.10529 | 0.064087 | 0.064087 | 0.082397 | 0.036621 | -0.11444 | 0.15106 | 0.16022 | 0.068665 | 0.036621 | 0.027466 | -0.032043 | -0.073242 | 119.7281 | 119.577 | -1.9089 | 119.7968 | 119.7556 | 0.17853 | -1.918 | 119.6594 | 119.6182 | -1.9547 | 119.8425 | 119.7601 | 0.14191 | -1.9638 | 119.7739 | 119.7647 | 119.7556 | -2.1057 | 119.7281 | 119.7189 | 119.8517 | -2.0645
5760.9844 | 122.0627 | -118.0298 | 3.6758 | -0.25665 | 0.048477 | 0.059045 | 0.0046827 | 0.02591 | -0.0036722 | 0.029792 | -0.22247 | 0.014447 | 0.022783 | 0.038347 | 0.00017731 | 0.016464 | 0.036621 | 0.032043 | 0.022888 | 0.013733 | 0.10529 | 0 | -0.15564 | 0.045776 | 0.045776 | -0.082397 | 0.082397 | 0.064087 | -0.064087 | -0.1236 | 118.0298 | 117.8741 | -3.5706 | 118.0618 | 118.0435 | 0.16937 | -3.6392 | 117.9657 | 117.9062 | -3.5934 | 118.0756 | 117.9474 | 0.041199 | -3.6118 | 118.1351 | 118.0664 | 118.0527 | -3.8315 | 118.1122 | 118.0939 | 118.0756 | -3.7994
5762.75 | 122.1451 | -118.428 | 3.2547 | 0.079041 | 0.050614 | 0.057977 | 0.00019645 | 0.029969 | 0.00038662 | 0.028937 | 0.12085 | 0.013379 | 0.02321 | 0.037066 | 0.0040225 | 0.018386 | 0.11444 | 0.10529 | 0.09613 | 0.091553 | 0.064087 | 0.041199 | -0.10986 | 0.16937 | 0.13275 | 0.036621 | 0.041199 | 0.027466 | -0.009155 | -0.068665 | 118.4692 | 118.3182 | -3.1906 | 118.5333 | 118.5196 | 0.20142 | -3.1403 | 118.4189 | 118.3594 | -3.2135 | 118.5974 | 118.4647 | 0.10529 | -3.2272 | 118.4921 | 118.5425 | 118.5242 | -3.3646 | 118.4692 | 118.4555 | 118.5608 | -3.3234
5764.5156 | 122.0123 | -118.7027 | 3.1357 | -0.22614 | 0.047837 | 0.0599 | 0.0044691 | 0.026551 | -0.0062356 | 0.027869 | -0.19958 | 0.013593 | 0.022142 | 0.035143 | 0.0012455 | 0.016891 | 0.073242 | 0.091553 | 0.064087 | 0.068665 | 0.10071 | 0.009155 | -0.11902 | 0.068665 | 0.10529 | -0.022888 | 0.07782 | 0.041199 | -0.050354 | -0.10529 | 118.7119 | 118.5837 | -3.035 | 118.7943 | 118.7714 | 0.18768 | -3.0624 | 118.6523 | 118.5974 | -3.0579 | 118.7714 | 118.6798 | 0.082398 | -3.0945 | 118.8034 | 118.7759 | 118.7668 | -3.2547 | 118.7805 | 118.7439 | 118.808 | -3.241
5766.2812 | 122.168 | -120.6299 | 1.0986 | -0.020142 | 0.045914 | 0.061182 | -1.7146e-05 | 0.02826 | -0.0079446 | 0.027228 | 0.036926 | 0.011243 | 0.024278 | 0.034929 | 0.00081811 | 0.019027 | 0.041199 | 0.073242 | 0.059509 | 0.036621 | 0.086975 | 0.032043 | -0.10529 | 0.091553 | 0.082397 | 0.004578 | 0.045776 | 0.036621 | -0.032043 | -0.073242 | 120.6619 | 120.5246 | -1.0117 | 120.7031 | 120.6665 | 0.14191 | -1.0574 | 120.5978 | 120.5566 | -1.0529 | 120.7214 | 120.6345 | 0.07782 | -1.062 | 120.7169 | 120.6711 | 120.6894 | -1.2039 | 120.6757 | 120.6665 | 120.7123 | -1.1719
5767.9844 | 122.0627 | -120.6985 | 1.1444 | -0.10406 | 0.049118 | 0.057977 | 0.0027601 | 0.024415 | 0.001882 | 0.028937 | -0.16144 | 0.016156 | 0.023637 | 0.036425 | 0.0059451 | 0.015396 | 0.091553 | 0.050354 | 0.027466 | 0.036621 | 0.11902 | 0.009155 | -0.12817 | 0.09613 | 0.07782 | -0.050354 | 0.068665 | 0.041199 | -0.045776 | -0.086975 | 120.7077 | 120.5704 | -1.0254 | 120.7489 | 120.7352 | 0.1648 | -1.0529 | 120.6528 | 120.6116 | -1.0757 | 120.7947 | 120.6482 | 0.036621 | -1.1032 | 120.8176 | 120.7901 | 120.726 | -1.2726 | 120.7672 | 120.7397 | 120.7764 | -1.2314
5769.75 | 122.0261 | -120.7077 | 1.181 | -0.15747 | 0.051682 | 0.058405 | -0.0017261 | 0.027619 | 0.00081382 | 0.028297 | -0.0012209 | 0.015515 | 0.023851 | 0.036425 | 0.0048769 | 0.017105 | 0.032043 | -0.009155 | -0.036621 | -0.009155 | 0.12817 | 0.004578 | -0.13733 | 0.022888 | 0 | -0.11902 | 0.073242 | 0.073242 | -0.054932 | -0.10529 | 120.7123 | 120.5704 | -1.0529 | 120.6985 | 120.6985 | 0.12817 | -1.149 | 120.6528 | 120.6024 | -1.1078 | 120.7306 | 120.5887 | -0.013733 | -1.1078 | 120.8359 | 120.7397 | 120.6711 | -1.3184 | 120.7809 | 120.7809 | 120.7077 | -1.2863
5771.5156 | 122.1085 | -120.7077 | 1.149 | -0.15747 | 0.049332 | 0.058405 | 0.0068189 | 0.027192 | -0.0085856 | 0.028937 | -0.15381 | 0.013166 | 0.023851 | 0.035143 | -0.0025999 | 0.018173 | 0.10986 | 0.14648 | 0.11444 | 0.091553 | 0.073242 | 0.050354 | -0.10986 | 0.13275 | 0.20142 | 0.068665 | 0.045776 | 0.027466 | -0.027466 | -0.082397 | 120.7581 | 120.5978 | -1.0757 | 120.8542 | 120.7993 | 0.20142 | -1.0391 | 120.6802 | 120.6253 | -1.1032 | 120.8405 | 120.7764 | 0.15106 | -1.1215 | 120.7809 | 120.8176 | 120.8221 | -1.2589 | 120.7535 | 120.7352 | 120.9091 | -1.2314
5773.2188 | 122.0993 | -120.5795 | 1.1673 | -0.073547 | 0.047409 | 0.0599 | 0.0023329 | 0.025483 | -0.00944 | 0.026588 | -0.039368 | 0.011243 | 0.023637 | 0.036638 | -0.00089089 | 0.017318 | 0.059509 | 0.11444 | 0.10071 | 0.054932 | 0.091553 | 0.027466 | -0.11444 | 0.16479 | 0.17395 | 0.082397 | 0.032043 | 0.036621 | -0.022888 | -0.073242 | 120.607 | 120.4651 | -1.0757 | 120.694 | 120.6345 | 0.16937 | -1.1078 | 120.5566 | 120.5063 | -1.1353 | 120.7443 | 120.6619 | 0.15564 | -1.1307 | 120.6711 | 120.639 | 120.6802 | -1.2817 | 120.6116 | 120.6161 | 120.7535 | -1.2405
5774.9844 | 122.0352 | -120.3964 | 1.4923 | -0.10406 | 0.049759 | 0.060968 | -1.7146e-05 | 0.028047 | 0.0012412 | 0.027015 | -0.15381 | 0.013593 | 0.023851 | 0.038347 | 0.0040225 | 0.012832 | 0.082397 | 0.050354 | 0.027466 | 0.018311 | 0.12817 | 0 | -0.14648 | 0.086975 | 0.091553 | -0.045776 | 0.059509 | 0.054932 | -0.054932 | -0.10986 | 120.3964 | 120.2499 | -1.3641 | 120.4468 | 120.4147 | 0.16479 | -1.4099 | 120.3415 | 120.2866 | -1.4328 | 120.4834 | 120.3506 | 0.064087 | -1.4374 | 120.5246 | 120.4788 | 120.4239 | -1.6388 | 120.4559 | 120.4514 | 120.488 | -1.6022
5776.75 | 122.1359 | -120.2637 | 1.5884 | -0.13458 | 0.047409 | 0.059473 | 0.0044691 | 0.025483 | -0.0085856 | 0.027656 | -0.077515 | 0.010816 | 0.023637 | 0.034716 | -0.00067729 | 0.018173 | 0.09613 | 0.13275 | 0.13275 | 0.082397 | 0.07782 | 0.045776 | -0.10986 | 0.15106 | 0.17853 | 0.082397 | 0.032043 | 0.027466 | -0.013733 | -0.059509 | 120.3094 | 120.1538 | -1.5106 | 120.3964 | 120.3461 | 0.19226 | -1.4923 | 120.2499 | 120.2042 | -1.5564 | 120.4147 | 120.3461 | 0.14191 | -1.561 | 120.3415 | 120.3598 | 120.3964 | -1.6983 | 120.2957 | 120.2911 | 120.4422 | -1.6479
5778.5156 | 121.9986 | -120.1721 | 1.7441 | -0.0354 | 0.0504 | 0.058832 | 0.00041005 | 0.026979 | 0.0016684 | 0.029578 | -0.054626 | 0.013806 | 0.021074 | 0.038134 | 0.0072269 | 0.01625 | 0.041199 | 0.022888 | -0.013733 | 0.013733 | 0.12817 | 0.013733 | -0.13733 | 0.036621 | 0.013733 | -0.11902 | 0.073242 | 0.054932 | -0.050354 | -0.10071 | 120.1859 | 120.0348 | -1.6159 | 120.195 | 120.1859 | 0.15106 | -1.7029 | 120.1218 | 120.0714 | -1.6708 | 120.2087 | 120.0531 | -0.018311 | -1.6891 | 120.3003 | 120.2133 | 120.1584 | -1.8814 | 120.2454 | 120.2271 | 120.1859 | -1.8448
5780.2812 | 122.049 | -120.1263 | 1.7853 | -0.24902 | 0.045914 | 0.060114 | 0.0023329 | 0.028474 | -0.0040994 | 0.02616 | -0.25299 | 0.013166 | 0.02321 | 0.03557 | 0.0014591 | 0.017746 | -0.013733 | 0.032043 | -0.027466 | -0.009155 | 0.1236 | -0.022888 | -0.14648 | 0.018311 | 0.041199 | -0.07782 | 0.086975 | 0.054932 | -0.068665 | -0.10986 | 120.1035 | 119.9799 | -1.6617 | 120.1584 | 120.1172 | 0.13733 | -1.799 | 120.0577 | 120.0165 | -1.6983 | 120.1447 | 120.0485 | 0.032043 | -1.7303 | 120.2499 | 120.1126 | 120.0989 | -1.9318 | 120.2133 | 120.1813 | 120.1675 | -1.8951
5781.9844 | 122.2412 | -117.0593 | 4.6097 | 0.071411 | 0.049759 | 0.059045 | 0.00019645 | 0.026765 | -0.0019632 | 0.028724 | 0.12085 | 0.013593 | 0.02321 | 0.035998 | 0.0042361 | 0.017746 | 0.022888 | 0.018311 | -0.004578 | 0 | 0.10986 | -0.004578 | -0.13275 | 0.07782 | 0.045776 | -0.032043 | 0.068665 | 0.027466 | -0.045776 | -0.086975 | 117.0547 | 116.9266 | -4.4998 | 117.0776 | 117.0593 | 0.13275 | -4.5868 | 117.0135 | 116.9724 | -4.541 | 117.1371 | 117.0273 | 0.054932 | -4.5822 | 117.1692 | 117.0822 | 117.0547 | -4.7424 | 117.128 | 117.0868 | 117.1051 | -4.6967
5783.75 | 122.1725 | -116.6382 | 5.1407 | 0.079041 | 0.045487 | 0.061609 | 0.0012647 | 0.024629 | -0.006022 | 0.028083 | 0.15137 | 0.011243 | 0.021501 | 0.035143 | 0.0014591 | 0.0186 | 0.07782 | 0.13733 | 0.10071 | 0.050354 | 0.07782 | 0.059509 | -0.11902 | 0.13275 | 0.13275 | 0.045776 | 0.027466 | 0.018311 | -0.036621 | -0.064087 | 116.6977 | 116.5192 | -5.0629 | 116.7755 | 116.6885 | 0.16937 | -5.0629 | 116.6016 | 116.5741 | -5.1132 | 116.7709 | 116.684 | 0.10986 | -5.1224 | 116.716 | 116.716 | 116.7389 | -5.2597 | 116.6656 | 116.6565 | 116.7709 | -5.2048
5785.5156 | 122.1542 | -119.0323 | 2.8152 | -0.1651 | 0.048691 | 0.057336 | 0.0038281 | 0.029756 | -0.0017496 | 0.02851 | -0.14618 | 0.016584 | 0.025133 | 0.038347 | 0.0038089 | 0.016464 | 0.054932 | 0.032043 | 0.004578 | 0.041199 | 0.10986 | 0.009155 | -0.13275 | 0.068665 | 0.073242 | -0.036621 | 0.082397 | 0.054932 | -0.027466 | -0.10986 | 119.0414 | 118.8995 | -2.7054 | 119.0643 | 119.0735 | 0.17395 | -2.7603 | 119.0048 | 118.9224 | -2.7329 | 119.101 | 118.9957 | 0.073242 | -2.7603 | 119.1422 | 119.0872 | 119.0369 | -2.948 | 119.1147 | 119.0872 | 119.1055 | -2.9251
5787.2812 | 122.1497 | -119.7464 | 2.1286 | 0.079041 | 0.045273 | 0.057764 | 0.0042555 | 0.027833 | -0.0068766 | 0.02616 | 0.10559 | 0.011884 | 0.025133 | 0.037279 | 0.0014591 | 0.019455 | 0.082397 | 0.11444 | 0.09613 | 0.050354 | 0.064087 | 0.032043 | -0.10071 | 0.10529 | 0.11444 | 0.036621 | 0.050354 | 0.032043 | -0.022888 | -0.068665 | 119.7784 | 119.6457 | -2.0645 | 119.8608 | 119.7968 | 0.15106 | -2.0462 | 119.7235 | 119.6777 | -2.0782 | 119.8517 | 119.783 | 0.10529 | -2.0966 | 119.8105 | 119.8288 | 119.8425 | -2.2293 | 119.7968 | 119.7784 | 119.8608 | -2.1973
5789 | 122.1222 | -119.7876 | 2.1286 | -0.18799 | 0.049546 | 0.057977 | 0.0055371 | 0.027192 | -0.0019632 | 0.027656 | -0.24536 | 0.01402 | 0.025774 | 0.036425 | 0.0038089 | 0.014541 | 0.018311 | 0.004578 | -0.009155 | 0.027466 | 0.11902 | -0.009155 | -0.15106 | 0.045776 | 0.068665 | -0.059509 | 0.07782 | 0.068665 | -0.064087 | -0.10071 | 119.7784 | 119.6365 | -2.0096 | 119.7922 | 119.8151 | 0.17853 | -2.1103 | 119.7235 | 119.6869 | -2.0508 | 119.8334 | 119.7281 | 0.041199 | -2.0599 | 119.9066 | 119.8059 | 119.7784 | -2.2797 | 119.8654 | 119.8563 | 119.8563 | -2.2293
5790.7656 | 122.2687 | -119.2108 | 2.6093 | 0.018005 | 0.043137 | 0.058832 | 0.0031873 | 0.027406 | -0.008372 | 0.027869 | 0.11322 | 0.013166 | 0.022569 | 0.037066 | 0.0016727 | 0.019241 | 0.050354 | 0.082397 | 0.068665 | 0.036621 | 0.068665 | 0.036621 | -0.10986 | 0.10529 | 0.09613 | 0.013733 | 0.059509 | 0.041199 | -0.032043 | -0.086975 | 119.2474 | 119.101 | -2.5406 | 119.2932 | 119.2474 | 0.14648 | -2.5589 | 119.1788 | 119.1238 | -2.5497 | 119.3161 | 119.2245 | 0.10071 | -2.5681 | 119.2795 | 119.2612 | 119.2795 | -2.7191 | 119.2703 | 119.252 | 119.3069 | -2.6962
5792.5312 | 122.2458 | -119.3893 | 2.4307 | 0.13245 | 0.047623 | 0.056696 | 0.0010511 | 0.026124 | -0.0021768 | 0.029151 | 0.0064086 | 0.012311 | 0.022142 | 0.035357 | 0.0046633 | 0.017746 | 0.091553 | 0.086975 | 0.07782 | 0.045776 | 0.086975 | 0.036621 | -0.10986 | 0.13733 | 0.11444 | 0.036621 | 0.022888 | 0.036621 | -0.018311 | -0.064087 | 119.426 | 119.2795 | -2.3438 | 119.4763 | 119.4351 | 0.15564 | -2.3392 | 119.371 | 119.3253 | -2.4078 | 119.5267 | 119.426 | 0.10071 | -2.3941 | 119.4763 | 119.4809 | 119.4672 | -2.5406 | 119.4122 | 119.426 | 119.5038 | -2.4948
5794.2344 | 122.1588 | -119.5129 | 2.3849 | -0.14984 | 0.051041 | 0.058618 | 0.0048963 | 0.031037 | 0.00081382 | 0.027869 | -0.19196 | 0.014875 | 0.024065 | 0.036425 | 0.0020999 | 0.015823 | 0.050354 | 0.004578 | 0 | 0.036621 | 0.1236 | 0 | -0.15564 | 0.068665 | 0.07782 | -0.041199 | 0.091553 | 0.045776 | -0.050354 | -0.09613 | 119.5129 | 119.3573 | -2.2614 | 119.5175 | 119.5496 | 0.19226 | -2.3346 | 119.4626 | 119.4168 | -2.2934 | 119.5816 | 119.4717 | 0.054931 | -2.3392 | 119.6365 | 119.5633 | 119.5129 | -2.5406 | 119.6045 | 119.5587 | 119.5908 | -2.4811
5796 | 122.0947 | -119.9387 | 2.0142 | -0.25665 | 0.049759 | 0.059473 | 0.0051099 | 0.029328 | -0.0064492 | 0.026801 | -0.11566 | 0.011884 | 0.025133 | 0.035998 | 0.00039091 | 0.017532 | 0.027466 | 0.064087 | 0.032043 | 0.027466 | 0.09613 | 0.009155 | -0.14191 | 0.032043 | 0.054932 | -0.059509 | 0.07782 | 0.054932 | -0.045776 | -0.09613 | 119.9478 | 119.7968 | -1.918 | 120.0027 | 119.9661 | 0.16937 | -1.9867 | 119.8929 | 119.8425 | -1.9363 | 119.9707 | 119.8792 | 0.036621 | -1.9592 | 120.0348 | 119.9661 | 119.9707 | -2.1561 | 120.0165 | 119.9936 | 119.9936 | -2.1103
5797.7031 | 122.0947 | -120.5154 | 1.4648 | -0.25665 | 0.050186 | 0.059473 | 0.0034009 | 0.028901 | -0.0038858 | 0.026588 | -0.20721 | 0.013379 | 0.023637 | 0.035143 | 0.0010317 | 0.020309 | 0.036621 | 0.082397 | 0.041199 | 0.041199 | 0.086975 | -0.004578 | -0.13275 | 0.036621 | 0.064087 | -0.064087 | 0.068665 | 0.054932 | -0.045776 | -0.09613 | 120.5109 | 120.3827 | -1.3779 | 120.5978 | 120.5566 | 0.17395 | -1.4282 | 120.4697 | 120.4193 | -1.3962 | 120.5521 | 120.4514 | 0.032043 | -1.4099 | 120.6024 | 120.5521 | 120.5566 | -1.5976 | 120.5841 | 120.5704 | 120.5795 | -1.561
5799.4531 | 122.1817 | -117.3981 | 4.5181 | -0.14221 | 0.047623 | 0.061182 | 0.0063917 | 0.029115 | -0.008372 | 0.026374 | -0.1004 | 0.01167 | 0.02556 | 0.035143 | -0.0011045 | 0.016037 | 0.10071 | 0.16937 | 0.12817 | 0.086975 | 0.082397 | 0.041199 | -0.09613 | 0.13733 | 0.17395 | 0.07782 | 0.050354 | 0.018311 | -0.004578 | -0.068665 | 117.4393 | 117.3019 | -4.4357 | 117.5674 | 117.485 | 0.1831 | -4.4174 | 117.3935 | 117.3294 | -4.4678 | 117.5354 | 117.4759 | 0.14649 | -4.4998 | 117.4805 | 117.4988 | 117.5262 | -4.6143 | 117.4484 | 117.4164 | 117.572 | -4.5868
5801.1562 | 122.1954 | -120.5887 | 1.2909 | -0.14984 | 0.051682 | 0.059473 | 0.0036145 | 0.027833 | 0.00038662 | 0.028297 | -0.21484 | 0.012952 | 0.026201 | 0.03557 | 0.0055179 | 0.014755 | 0.050354 | 0.036621 | 0.009155 | 0.041199 | 0.1236 | -0.013733 | -0.14191 | 0.068665 | 0.073242 | -0.041199 | 0.045776 | 0.059509 | -0.050354 | -0.10986 | 120.575 | 120.4468 | -1.1673 | 120.6253 | 120.6299 | 0.18311 | -1.2405 | 120.5383 | 120.4788 | -1.2451 | 120.6573 | 120.5475 | 0.068664 | -1.2314 | 120.7123 | 120.639 | 120.5978 | -1.4328 | 120.6345 | 120.6482 | 120.6619 | -1.4008
5802.9219 | 122.1451 | -120.8221 | 1.1261 | -0.23376 | 0.052109 | 0.059686 | 0.0063917 | 0.028688 | -0.0036722 | 0.027228 | -0.16144 | 0.012738 | 0.027055 | 0.037493 | 0.00017731 | 0.018173 | 0.018311 | 0.022888 | 0.013733 | 0.013733 | 0.1236 | 0.009155 | -0.13733 | 0.027466 | 0.050354 | -0.059509 | 0.082397 | 0.064087 | -0.059509 | -0.13733 | 120.8313 | 120.6848 | -1.0025 | 120.845 | 120.8359 | 0.15106 | -1.1078 | 120.7626 | 120.6848 | -1.0437 | 120.8496 | 120.7626 | 0.07782 | -1.062 | 120.9457 | 120.8405 | 120.8359 | -1.2634 | 120.9045 | 120.8862 | 120.8725 | -1.2634
5804.6875 | 122.1725 | -120.9091 | 1.0712 | -0.18799 | 0.049973 | 0.060327 | 0.0042555 | 0.027833 | -0.001536 | 0.029578 | -0.20721 | 0.013166 | 0.026842 | 0.035998 | 0.0035953 | 0.017532 | -0.018311 | 0 | -0.027466 | 0 | 0.13733 | 0 | -0.16479 | 0.032043 | 0.050354 | -0.073242 | 0.091553 | 0.050354 | -0.054932 | -0.10986 | 120.9091 | 120.7443 | -0.93384 | 120.9091 | 120.9091 | 0.16479 | -1.0895 | 120.8542 | 120.7993 | -0.97961 | 120.9412 | 120.8359 | 0.036621 | -1.0208 | 121.0464 | 120.8908 | 120.8817 | -1.236 | 121.0007 | 120.9595 | 120.9595 | -1.181
5806.3906 | 122.0901 | -120.0531 | 1.9455 | 0.13245 | 0.052109 | 0.057123 | 0.00062385 | 0.027619 | -0.0011088 | 0.028297 | -0.0012209 | 0.01402 | 0.026201 | 0.035998 | 0.0046633 | 0.015396 | -0.009155 | 0.009155 | -0.027466 | 0.009155 | 0.11902 | 0.009155 | -0.13275 | 0.022888 | 0.009155 | -0.10071 | 0.07782 | 0.050354 | -0.064087 | -0.10071 | 120.0623 | 119.9203 | -1.8265 | 120.0623 | 120.0623 | 0.14191 | -1.9547 | 119.989 | 119.9524 | -1.8677 | 120.076 | 119.9524 | 0 | -1.8951 | 120.1721 | 120.0439 | 120.0256 | -2.0782 | 120.1309 | 120.1035 | 120.0623 | -2.0462
5808.1719 | 122.1863 | -118.895 | 3.1952 | 0.056152 | 0.047196 | 0.061823 | 0.0023329 | 0.025056 | -0.0085856 | 0.02616 | 0.12085 | 0.010816 | 0.02321 | 0.03557 | 0.00039091 | 0.018386 | 0.009155 | 0.086975 | 0.059509 | 0.032043 | 0.064087 | 0.036621 | -0.11444 | 0.091553 | 0.091553 | 0.004578 | 0.036621 | 0.022888 | -0.022888 | -0.091553 | 118.9316 | 118.7805 | -3.1311 | 118.9819 | 118.927 | 0.14648 | -3.186 | 118.8721 | 118.8034 | -3.1586 | 118.9865 | 118.8995 | 0.096131 | -3.1723 | 118.959 | 118.9041 | 118.9545 | -3.3096 | 118.9316 | 118.9178 | 118.9865 | -3.2867
5809.875 | 122.2549 | -120.8817 | 1.03 | -0.020142 | 0.040573 | 0.060114 | 0.0029737 | 0.02826 | -0.0081582 | 0.026374 | 0.014038 | 0.010602 | 0.022142 | 0.036425 | -0.0013181 | 0.018814 | 0.022888 | 0.07782 | 0.073242 | 0.045776 | 0.082397 | 0.036621 | -0.11902 | 0.10071 | 0.12817 | 0.050354 | 0.032043 | 0.045776 | -0.032043 | -0.07782 | 120.9183 | 120.7626 | -0.94757 | 120.9595 | 120.9274 | 0.16479 | -1.0071 | 120.8496 | 120.8038 | -0.99792 | 120.9824 | 120.932 | 0.12817 | -0.98419 | 120.9641 | 120.9045 | 120.9549 | -1.149 | 120.9137 | 120.9274 | 121.0098 | -1.1078
5811.6406 | 122.1039 | -120.9045 | 1.0849 | 0.040894 | 0.050186 | 0.057977 | -0.00023075 | 0.027192 | 0.0016684 | 0.028083 | -0.031738 | 0.015302 | 0.023424 | 0.037493 | 0.0055179 | 0.014968 | 0.013733 | -0.036621 | -0.054932 | -0.009155 | 0.11902 | -0.004578 | -0.13275 | 0.009155 | -0.009155 | -0.13275 | 0.091553 | 0.054932 | -0.050354 | -0.11444 | 120.9 | 120.7718 | -0.96588 | 120.8679 | 120.8954 | 0.1236 | -1.0712 | 120.8542 | 120.7901 | -0.99335 | 120.9137 | 120.7718 | -0.01831 | -1.03 | 121.0236 | 120.9183 | 120.8496 | -1.2177 | 120.9961 | 120.9595 | 120.8954 | -1.1993
5813.3281 | 122.1542 | -120.8221 | 1.1627 | -0.27191 | 0.050614 | 0.05755 | 0.0068189 | 0.026338 | -0.0045266 | 0.026801 | -0.1004 | 0.01402 | 0.026201 | 0.036211 | -0.00024989 | 0.016891 | 0.013733 | 0.036621 | 0.018311 | 0.013733 | 0.10529 | 0.009155 | -0.15564 | 0.036621 | 0.045776 | -0.059509 | 0.07782 | 0.059509 | -0.073242 | -0.11902 | 120.8313 | 120.6665 | -1.0574 | 120.8588 | 120.8359 | 0.16937 | -1.149 | 120.7489 | 120.7031 | -1.0849 | 120.8588 | 120.7626 | 0.05951 | -1.1032 | 120.9274 | 120.8359 | 120.8405 | -1.3184 | 120.9 | 120.8817 | 120.8679 | -1.2817
5815.1094 | 122.1542 | -120.8267 | 1.1581 | 0.033264 | 0.048905 | 0.059045 | 0.0021191 | 0.028047 | 0.00060022 | 0.03086 | 0.021668 | 0.015943 | 0.025987 | 0.038561 | 0.0059451 | 0.016677 | 0 | -0.036621 | -0.054932 | 0 | 0.11902 | -0.013733 | -0.13733 | 0.027466 | 0.004578 | -0.10529 | 0.064087 | 0.064087 | -0.054932 | -0.086975 | 120.813 | 120.6894 | -1.0391 | 120.7901 | 120.8267 | 0.13733 | -1.1581 | 120.7718 | 120.7397 | -1.0941 | 120.8542 | 120.7214 | -0.018311 | -1.0941 | 120.9457 | 120.8267 | 120.7718 | -1.2955 | 120.8908 | 120.8908 | 120.8313 | -1.2451
5816.8281 | 122.1268 | -120.8588 | 1.1307 | 0.048523 | 0.048264 | 0.058832 | 0.0025465 | 0.028474 | 0.0010276 | 0.031287 | -0.0088499 | 0.016156 | 0.024065 | 0.039843 | 0.0040225 | 0.018173 | 0 | -0.022888 | -0.027466 | 0 | 0.11444 | 0.009155 | -0.15106 | 0 | 0 | -0.11444 | 0.082397 | 0.07782 | -0.068665 | -0.10071 | 120.8679 | 120.7077 | -1.0162 | 120.8359 | 120.8588 | 0.15106 | -1.1307 | 120.7901 | 120.7581 | -1.0483 | 120.8588 | 120.7443 | -0.013733 | -1.0529 | 120.9732 | 120.8588 | 120.8313 | -1.2817 | 120.9412 | 120.9366 | 120.8588 | -1.2314
5818.5938 | 122.1451 | -120.9366 | 1.0529 | 0.025635 | 0.050614 | 0.059045 | 0.0023329 | 0.029115 | -0.0023904 | 0.030219 | 0.075073 | 0.014661 | 0.024919 | 0.035784 | 0.0048769 | 0.018814 | -0.013733 | -0.036621 | -0.050354 | -0.027466 | 0.11444 | 0.004578 | -0.14191 | 0.009155 | -0.013733 | -0.09613 | 0.064087 | 0.073242 | -0.054932 | -0.10071 | 120.9412 | 120.7947 | -0.93841 | 120.9 | 120.9091 | 0.11444 | -1.0666 | 120.8817 | 120.8359 | -0.98877 | 120.9457 | 120.8405 | 0.004578 | -0.97961 | 121.051 | 120.9229 | 120.8862 | -1.1948 | 121.0007 | 121.0098 | 120.9229 | -1.1536
5820.2969 | 122.1725 | -120.9366 | 1.0666 | -0.14221 | 0.051255 | 0.05755 | 0.0048963 | 0.029756 | -0.0028178 | 0.030219 | -0.12329 | 0.011884 | 0.027269 | 0.034289 | 0.0012455 | 0.0186 | 0.045776 | 0.068665 | 0.013733 | 0.041199 | 0.11444 | -0.009155 | -0.13733 | 0.082397 | 0.073242 | -0.041199 | 0.064087 | 0.045776 | -0.045776 | -0.10071 | 120.9274 | 120.7993 | -0.95215 | 121.0052 | 120.9778 | 0.17853 | -1.0208 | 120.8908 | 120.8359 | -1.0025 | 121.019 | 120.8954 | 0.059509 | -1.0208 | 121.051 | 120.9824 | 120.9503 | -1.2039 | 121.0007 | 120.9824 | 121.0098 | -1.1673
5822.0625 | 122.2549 | -120.9274 | 1.0208 | -0.13458 | 0.045914 | 0.060114 | 0.0016919 | 0.027192 | -0.010295 | 0.027656 | -0.031738 | 0.012097 | 0.026201 | 0.033434 | -0.00089089 | 0.018814 | 0.073242 | 0.17395 | 0.1236 | 0.091553 | 0.07782 | 0.045776 | -0.086975 | 0.15106 | 0.19226 | 0.082397 | 0.041199 | 0.027466 | -0.041199 | -0.068665 | 120.9732 | 120.8405 | -0.94299 | 121.1014 | 121.019 | 0.17853 | -0.94757 | 120.8862 | 120.8588 | -0.97961 | 121.0785 | 121.0098 | 0.15106 | -0.99335 | 121.0052 | 121.0007 | 121.051 | -1.1078 | 120.9686 | 120.9549 | 121.1197 | -1.0895
5823.75 | 122.2504 | -120.8496 | 1.0712 | 0.14008 | 0.049973 | 0.059686 | 0.0036145 | 0.027619 | -0.002604 | 0.026801 | 0.18188 | 0.013379 | 0.025133 | 0.035357 | 0.0038089 | 0.01625 | 0.041199 | 0.013733 | 0.009155 | 0.018311 | 0.11902 | 0.022888 | -0.11902 | 0.10986 | 0.07782 | 0 | 0.036621 | 0.036621 | -0.027466 | -0.091553 | 120.8725 | 120.7306 | -0.95215 | 120.8633 | 120.8679 | 0.13733 | -1.03 | 120.8221 | 120.7581 | -1.0345 | 120.9595 | 120.8496 | 0.091553 | -1.0345 | 120.9686 | 120.8908 | 120.8588 | -1.1902 | 120.8862 | 120.8862 | 120.9274 | -1.1627
5825.5156 | 122.168 | -120.9 | 1.1124 | -0.17273 | 0.051041 | 0.058191 | 0.0051099 | 0.02826 | -0.0019632 | 0.029151 | -0.19196 | 0.016156 | 0.025774 | 0.037066 | 0.0012455 | 0.017959 | 0.004578 | 0 | -0.004578 | 0.022888 | 0.10986 | 0 | -0.15564 | 0.041199 | 0.050354 | -0.054932 | 0.068665 | 0.054932 | -0.068665 | -0.09613 | 120.9 | 120.7443 | -1.0025 | 120.9 | 120.9229 | 0.17853 | -1.1078 | 120.8313 | 120.8038 | -1.0437 | 120.9412 | 120.845 | 0.041198 | -1.0574 | 121.0098 | 120.9045 | 120.8954 | -1.268 | 120.9686 | 120.9549 | 120.9503 | -1.2085
5827.2812 | 122.1817 | -120.8862 | 1.1078 | -0.24139 | 0.049332 | 0.059473 | 0.0044691 | 0.027619 | -0.0036722 | 0.028297 | -0.19196 | 0.012525 | 0.027055 | 0.038347 | -0.00067729 | 0.017105 | -0.013733 | -0.009155 | -0.041199 | 0.009155 | 0.11902 | -0.004578 | -0.15564 | 0.013733 | 0.018311 | -0.07782 | 0.10071 | 0.07782 | -0.041199 | -0.10529 | 120.8817 | 120.7306 | -0.98877 | 120.8771 | 120.8954 | 0.16479 | -1.1215 | 120.845 | 120.7809 | -1.0071 | 120.9 | 120.8084 | 0.027466 | -1.03 | 121.0052 | 120.8725 | 120.845 | -1.2634 | 120.9869 | 120.9641 | 120.9045 | -1.2131
5829.0469 | 122.1909 | -120.9137 | 1.1078 | -0.20325 | 0.049332 | 0.057977 | 0.0048963 | 0.029969 | -0.00068138 | 0.026801 | -0.16144 | 0.015515 | 0.02556 | 0.036211 | 0.0027407 | 0.015823 | 0.032043 | 0.018311 | 0 | 0.045776 | 0.11444 | 0.004578 | -0.15564 | 0.064087 | 0.082397 | -0.045776 | 0.068665 | 0.064087 | -0.068665 | -0.10986 | 120.9183 | 120.7581 | -0.99335 | 120.932 | 120.9595 | 0.20142 | -1.0757 | 120.845 | 120.8038 | -1.0391 | 120.9778 | 120.8679 | 0.064087 | -1.0437 | 121.0281 | 120.9457 | 120.9137 | -1.2634 | 120.9824 | 120.9778 | 120.9961 | -1.2177
5830.75 | 122.1451 | -120.9229 | 1.1398 | -0.18799 | 0.049973 | 0.059686 | 0.0055371 | 0.027406 | -0.0092264 | 0.028083 | -0.092773 | 0.012097 | 0.026201 | 0.035998 | -0.0017453 | 0.018386 | 0.059509 | 0.13733 | 0.10986 | 0.086975 | 0.064087 | 0.022888 | -0.1236 | 0.10986 | 0.17853 | 0.036621 | 0.050354 | 0.041199 | -0.027466 | -0.091553 | 120.9457 | 120.7993 | -1.0757 | 121.0602 | 121.0098 | 0.21057 | -1.0803 | 120.8954 | 120.8313 | -1.0895 | 121.0327 | 120.9595 | 0.12817 | -1.0986 | 120.9869 | 120.9824 | 121.0327 | -1.2634 | 120.9732 | 120.9641 | 121.1014 | -1.2314
5832.5312 | 122.2733 | -120.8954 | 1.062 | -0.012512 | 0.048477 | 0.0599 | 0.0059643 | 0.029328 | -0.0096536 | 0.025947 | 0.075073 | 0.0084658 | 0.026628 | 0.034502 | -0.0019589 | 0.019027 | 0.009155 | 0.068665 | 0.054932 | 0.041199 | 0.09613 | 0.036621 | -0.13275 | 0.082397 | 0.07782 | 0.009155 | 0.054932 | 0.027466 | -0.036621 | -0.082397 | 120.932 | 120.7626 | -0.96588 | 120.9641 | 120.9366 | 0.17395 | -1.0529 | 120.8588 | 120.813 | -1.0071 | 120.9778 | 120.9045 | 0.091552 | -1.0345 | 120.9915 | 120.9045 | 120.9503 | -1.1948 | 120.9503 | 120.9229 | 120.9732 | -1.1444
5834.2969 | 122.1863 | -120.9457 | 1.1032 | -0.27191 | 0.05275 | 0.059473 | 0.0034009 | 0.028474 | -0.0013224 | 0.026588 | -0.22247 | 0.012525 | 0.026414 | 0.036852 | 0.00060451 | 0.015182 | -0.009155 | 0 | -0.027466 | 0.004578 | 0.11902 | 0.009155 | -0.14648 | 0.009155 | 0.032043 | -0.082397 | 0.082397 | 0.068665 | -0.064087 | -0.09613 | 120.9549 | 120.7993 | -0.98419 | 120.9457 | 120.9503 | 0.15106 | -1.1124 | 120.8817 | 120.8496 | -1.0208 | 120.9549 | 120.8633 | 0.013733 | -1.0345 | 121.0648 | 120.9366 | 120.9183 | -1.2497 | 121.0281 | 121.0144 | 120.9778 | -1.1993
5836.0625 | 122.2321 | -120.9183 | 1.0391 | 0.10193 | 0.047623 | 0.060114 | 0.0014783 | 0.028688 | -0.0047404 | 0.029151 | 0.11322 | 0.011457 | 0.024919 | 0.034929 | 0.0025271 | 0.017746 | 0.059509 | 0.11444 | 0.091553 | 0.059509 | 0.064087 | 0.027466 | -0.10071 | 0.1236 | 0.10071 | 0.022888 | 0.045776 | 0.032043 | -0.027466 | -0.068665 | 120.9457 | 120.8176 | -0.97504 | 121.0327 | 120.9778 | 0.16022 | -0.97961 | 120.8908 | 120.8496 | -0.99335 | 121.0419 | 120.9412 | 0.091553 | -1.0071 | 120.9824 | 120.9778 | 121.0098 | -1.1398 | 120.9641 | 120.9503 | 121.019 | -1.1078
5837.8438 | 122.2778 | -120.9412 | 1.0483 | -0.13458 | 0.046768 | 0.061182 | 0.0029737 | 0.026765 | -0.0068766 | 0.026588 | -0.077515 | 0.012311 | 0.020647 | 0.033434 | 0.00081811 | 0.018814 | 0.10071 | 0.14648 | 0.10071 | 0.086975 | 0.073242 | 0.036621 | -0.10529 | 0.16937 | 0.17395 | 0.086975 | 0.027466 | 0.032043 | -0.004578 | -0.064087 | 120.9778 | 120.8359 | -0.97504 | 121.0876 | 121.0281 | 0.19226 | -0.94757 | 120.9366 | 120.8771 | -1.0208 | 121.1105 | 121.0281 | 0.15106 | -1.0162 | 121.0144 | 121.0419 | 121.0419 | -1.1536 | 120.9686 | 120.9732 | 121.1151 | -1.1124
5839.6094 | 122.1909 | -120.9641 | 1.0574 | 0.071411 | 0.050186 | 0.060541 | 0.0014783 | 0.027406 | 0.00017302 | 0.029365 | 0.036926 | 0.015515 | 0.021287 | 0.037279 | 0.0072269 | 0.015609 | 0.018311 | -0.036621 | -0.054932 | 0.004578 | 0.10529 | 0.009155 | -0.13275 | 0.036621 | -0.022888 | -0.086975 | 0.086975 | 0.073242 | -0.041199 | -0.10529 | 120.9732 | 120.8313 | -0.95215 | 120.9274 | 120.9686 | 0.13733 | -1.0391 | 120.9229 | 120.8588 | -0.97046 | 121.0007 | 120.8771 | 0.018311 | -0.98419 | 121.0693 | 120.9824 | 120.9091 | -1.1902 | 121.051 | 121.0373 | 120.9412 | -1.1627
5841.3125 | 122.1863 | -120.9824 | 1.0666 | -0.24902 | 0.049973 | 0.059259 | 0.0055371 | 0.02826 | -0.0030314 | 0.028724 | -0.26062 | 0.01402 | 0.022996 | 0.03557 | 0.0018863 | 0.015823 | 0.009155 | -0.009155 | -0.027466 | 0.004578 | 0.1236 | -0.004578 | -0.14191 | 0.018311 | 0.027466 | -0.091553 | 0.086975 | 0.07782 | -0.050354 | -0.11444 | 120.9778 | 120.8405 | -0.94299 | 120.9732 | 120.9869 | 0.14649 | -1.0574 | 120.932 | 120.8679 | -0.97961 | 121.0007 | 120.8908 | 0.022888 | -0.98877 | 121.106 | 120.9915 | 120.9549 | -1.2085 | 121.0693 | 121.0602 | 121.0098 | -1.181
5843.1094 | 122.2733 | -120.9412 | 1.0483 | -0.1651 | 0.046982 | 0.058618 | 0.0055371 | 0.028901 | -0.0096536 | 0.025519 | -0.13855 | 0.0091066 | 0.022996 | 0.035143 | -0.0017453 | 0.019027 | 0.086975 | 0.14648 | 0.11902 | 0.073242 | 0.082397 | 0.032043 | -0.1236 | 0.14191 | 0.19684 | 0.07782 | 0.032043 | 0.018311 | -0.022888 | -0.07782 | 120.9732 | 120.8176 | -0.96588 | 121.0876 | 121.0144 | 0.19684 | -0.9613 | 120.9183 | 120.8633 | -1.0162 | 121.0831 | 121.019 | 0.15564 | -1.03 | 121.0236 | 121.0281 | 121.0602 | -1.1719 | 120.9732 | 120.9595 | 121.138 | -1.1261
5844.875 | 122.2916 | -120.9641 | 1.0345 | -0.096436 | 0.047196 | 0.060754 | 0.0034009 | 0.027833 | -0.0087992 | 0.026374 | -0.1004 | 0.0097476 | 0.023424 | 0.035784 | 0.00039091 | 0.01625 | 0.086975 | 0.13733 | 0.09613 | 0.064087 | 0.086975 | 0.036621 | -0.082397 | 0.16479 | 0.16022 | 0.086975 | 0.036621 | 0.022888 | -0.041199 | -0.082397 | 121.0007 | 120.8817 | -0.94757 | 121.1014 | 121.0281 | 0.14648 | -0.94757 | 120.9229 | 120.8817 | -0.99792 | 121.1288 | 121.051 | 0.16937 | -1.0117 | 121.051 | 121.051 | 121.0602 | -1.1169 | 121.0007 | 120.9869 | 121.1243 | -1.1169
5846.6562 | 122.168 | -120.9915 | 1.0849 | -0.073547 | 0.05275 | 0.05755 | 0.0014783 | 0.02527 | 0.0012412 | 0.029792 | -0.11566 | 0.015088 | 0.021287 | 0.037493 | 0.0061587 | 0.016037 | 0.07782 | 0.059509 | 0 | 0.032043 | 0.11902 | 0.018311 | -0.15564 | 0.07782 | 0.045776 | -0.068665 | 0.064087 | 0.068665 | -0.045776 | -0.10986 | 121.0098 | 120.8359 | -0.96588 | 121.051 | 121.0236 | 0.18768 | -1.0071 | 120.9457 | 120.8817 | -1.0208 | 121.0693 | 120.9229 | 0.041198 | -1.0162 | 121.1105 | 121.0693 | 120.9915 | -1.2405 | 121.0556 | 121.0602 | 121.0373 | -1.1948
5848.3594 | 122.2275 | -120.9824 | 1.0803 | -0.20325 | 0.051682 | 0.059259 | 0.0025465 | 0.02591 | -0.00089518 | 0.027869 | -0.21484 | 0.014661 | 0.024065 | 0.03557 | 0.0023135 | 0.017959 | 0.022888 | 0.018311 | -0.013733 | 0.013733 | 0.10986 | -0.004578 | -0.14648 | 0.059509 | 0.068665 | -0.064087 | 0.082397 | 0.073242 | -0.064087 | -0.10071 | 120.9778 | 120.8359 | -0.97046 | 121.0007 | 120.9961 | 0.16022 | -1.0574 | 120.9183 | 120.8817 | -0.99792 | 121.0419 | 120.9183 | 0.036621 | -1.0071 | 121.0922 | 121.0052 | 120.9686 | -1.2268 | 121.0648 | 121.0556 | 121.051 | -1.181
5850.0625 | 122.1817 | -121.0098 | 1.0895 | -0.18036 | 0.0504 | 0.059259 | 0.0057507 | 0.029115 | -0.008372 | 0.027228 | -0.18433 | 0.010388 | 0.02556 | 0.034929 | -0.00024989 | 0.018173 | 0.050354 | 0.13733 | 0.09613 | 0.091553 | 0.068665 | 0.032043 | -0.11444 | 0.10986 | 0.13275 | 0.018311 | 0.036621 | 0.050354 | -0.022888 | -0.10071 | 121.0419 | 120.8954 | -1.0208 | 121.1472 | 121.1014 | 0.20599 | -1.0391 | 120.9869 | 120.9091 | -1.0529 | 121.1197 | 121.0281 | 0.11902 | -1.0391 | 121.0785 | 121.0602 | 121.106 | -1.2039 | 121.0464 | 121.0602 | 121.1426 | -1.1902
5851.7812 | 122.2321 | -120.9641 | 1.0986 | -0.20325 | 0.051255 | 0.057977 | 0.0040417 | 0.029328 | 0.00060022 | 0.029365 | -0.19958 | 0.014875 | 0.02791 | 0.038775 | 0.0025271 | 0.015182 | 0.009155 | 0.027466 | 0.009155 | 0.018311 | 0.10986 | 0 | -0.14191 | 0.059509 | 0.068665 | -0.059509 | 0.064087 | 0.064087 | -0.045776 | -0.10529 | 120.9641 | 120.8221 | -0.98877 | 120.9915 | 120.9824 | 0.16022 | -1.0895 | 120.9183 | 120.8588 | -1.0345 | 121.0236 | 120.9045 | 0.045777 | -1.0345 | 121.0739 | 120.9732 | 120.9732 | -1.2405 | 121.0281 | 121.0281 | 121.0327 | -1.2039
5853.5312 | 122.3145 | -120.9137 | 1.0941 | 0.14771 | 0.048905 | 0.057764 | 0.00019645 | 0.027406 | -0.0040994 | 0.03086 | 0.082703 | 0.011884 | 0.022996 | 0.038775 | 0.0046633 | 0.019241 | 0.054932 | 0.091553 | 0.045776 | 0.054932 | 0.10071 | 0.027466 | -0.12817 | 0.12817 | 0.10986 | 0.022888 | 0.027466 | 0.009155 | -0.022888 | -0.086975 | 120.9412 | 120.7855 | -0.99335 | 121.0052 | 120.9686 | 0.18311 | -1.0391 | 120.8908 | 120.8267 | -1.0666 | 121.0419 | 120.9366 | 0.10986 | -1.0849 | 121.0144 | 120.9686 | 120.9595 | -1.2222 | 120.9412 | 120.9229 | 121.0236 | -1.181
5855.2344 | 122.1725 | -120.9778 | 1.1398 | -0.24139 | 0.048264 | 0.060114 | 0.0057507 | 0.029542 | -0.0062356 | 0.027442 | -0.18433 | 0.01402 | 0.02556 | 0.037066 | 0.00060451 | 0.017105 | 0.050354 | 0.10529 | 0.073242 | 0.059509 | 0.091553 | 0.027466 | -0.13733 | 0.045776 | 0.086975 | -0.032043 | 0.064087 | 0.045776 | -0.050354 | -0.082397 | 121.0052 | 120.8405 | -1.0483 | 121.0831 | 121.0373 | 0.19684 | -1.0895 | 120.9274 | 120.8954 | -1.0757 | 121.0236 | 120.9457 | 0.050354 | -1.0941 | 121.0693 | 121.0281 | 121.051 | -1.2772 | 121.0419 | 121.0236 | 121.0648 | -1.2222
5856.9375 | 122.2504 | -120.932 | 1.1215 | -0.20325 | 0.051468 | 0.058618 | 0.0051099 | 0.026551 | -0.0073038 | 0.025519 | -0.11566 | 0.011457 | 0.023637 | 0.034929 | -0.00046349 | 0.015609 | 0.086975 | 0.15106 | 0.11444 | 0.082397 | 0.086975 | 0.036621 | -0.10986 | 0.12817 | 0.17395 | 0.041199 | 0.041199 | 0.045776 | -0.013733 | -0.07782 | 120.9686 | 120.8221 | -1.0345 | 121.0831 | 121.0144 | 0.19226 | -1.0345 | 120.9183 | 120.8542 | -1.0803 | 121.0602 | 120.9732 | 0.11902 | -1.0757 | 121.019 | 121.019 | 121.0464 | -1.2314 | 120.9732 | 120.9778 | 121.106 | -1.1993
5858.6719 | 122.3145 | -120.8908 | 1.1078 | 0.20874 | 0.045487 | 0.060327 | -0.00087155 | 0.028474 | -0.0028178 | 0.029365 | 0.13611 | 0.012097 | 0.021715 | 0.034502 | 0.0065859 | 0.016677 | 0.10529 | 0.1236 | 0.086975 | 0.086975 | 0.073242 | 0.041199 | -0.09613 | 0.15106 | 0.11444 | 0.045776 | 0.032043 | 0.027466 | -0.032043 | -0.07782 | 120.932 | 120.7947 | -1.0345 | 121.0144 | 120.9778 | 0.1831 | -1.0025 | 120.8588 | 120.813 | -1.0757 | 121.0419 | 120.9366 | 0.1236 | -1.0803 | 120.9641 | 120.9961 | 120.9778 | -1.2039 | 120.9229 | 120.9183 | 121.0052 | -1.1856
5860.3594 | 122.2504 | -120.9137 | 1.1536 | -0.17273 | 0.049759 | 0.057336 | 0.0036145 | 0.027406 | 0.00017302 | 0.029151 | -0.20721 | 0.015515 | 0.025774 | 0.03792 | 0.0046633 | 0.016677 | 0.050354 | 0.036621 | 0.004578 | 0.032043 | 0.10986 | 0.004578 | -0.13275 | 0.07782 | 0.086975 | -0.041199 | 0.086975 | 0.064087 | -0.054932 | -0.082397 | 120.9183 | 120.7809 | -1.0437 | 120.9503 | 120.9457 | 0.16479 | -1.1032 | 120.8588 | 120.8313 | -1.0666 | 120.9915 | 120.8725 | 0.041198 | -1.0895 | 121.0236 | 120.9641 | 120.9183 | -1.2863 | 121.0007 | 120.9778 | 121.0007 | -1.236
5862.0781 | 122.2275 | -120.9091 | 1.1993 | -0.22614 | 0.04805 | 0.060327 | 0.0036145 | 0.026338 | -0.0045266 | 0.028937 | -0.2301 | 0.012525 | 0.02321 | 0.035143 | 0.0020999 | 0.017105 | -0.022888 | 0.013733 | -0.013733 | -0.009155 | 0.11902 | -0.013733 | -0.15564 | 0.022888 | 0.027466 | -0.07782 | 0.091553 | 0.073242 | -0.054932 | -0.11902 | 120.8954 | 120.7535 | -1.0803 | 120.9229 | 120.9 | 0.14649 | -1.2222 | 120.8542 | 120.7901 | -1.1078 | 120.932 | 120.8313 | 0.041199 | -1.1261 | 121.0281 | 120.8862 | 120.8954 | -1.355 | 121.0007 | 120.9824 | 120.9366 | -1.3184
5863.7812 | 122.2733 | -120.7855 | 1.2314 | 0.14008 | 0.0457 | 0.057336 | 0.0010511 | 0.027406 | -0.0040994 | 0.029365 | 0.14374 | 0.011457 | 0.023637 | 0.034075 | 0.0025271 | 0.018814 | 0.091553 | 0.13275 | 0.10071 | 0.068665 | 0.054932 | 0.050354 | -0.09613 | 0.14191 | 0.14648 | 0.054932 | 0.036621 | 0.018311 | -0.013733 | -0.068665 | 120.8359 | 120.6894 | -1.1765 | 120.9183 | 120.8542 | 0.16479 | -1.1398 | 120.7718 | 120.7169 | -1.1948 | 120.9274 | 120.8405 | 0.1236 | -1.2131 | 120.8405 | 120.8771 | 120.8862 | -1.3275 | 120.8221 | 120.8038 | 120.932 | -1.3
5865.5938 | 122.3099 | -120.7489 | 1.2543 | 0.10956 | 0.047837 | 0.05755 | 0.0014783 | 0.026551 | -0.0034586 | 0.029151 | 0.18188 | 0.013166 | 0.022569 | 0.036211 | 0.0033817 | 0.016677 | 0.09613 | 0.11902 | 0.10071 | 0.07782 | 0.07782 | 0.050354 | -0.10071 | 0.14648 | 0.13275 | 0.054932 | 0.045776 | 0.022888 | -0.018311 | -0.07782 | 120.7993 | 120.6482 | -1.1765 | 120.8679 | 120.8267 | 0.17853 | -1.1581 | 120.7306 | 120.6711 | -1.2085 | 120.8954 | 120.8038 | 0.13275 | -1.2314 | 120.8267 | 120.845 | 120.8496 | -1.355 | 120.7947 | 120.7718 | 120.8817 | -1.3321
5867.2969 | 122.2321 | -120.7764 | 1.3458 | -0.23376 | 0.050614 | 0.059686 | 0.0051099 | 0.026124 | -0.0021768 | 0.027015 | -0.26062 | 0.015515 | 0.026201 | 0.036211 | 0.0014591 | 0.01625 | 0 | 0.004578 | -0.018311 | 0 | 0.14191 | -0.013733 | -0.15564 | 0.022888 | 0.032043 | -0.086975 | 0.09613 | 0.068665 | -0.054932 | -0.10071 | 120.7626 | 120.6207 | -1.2039 | 120.7809 | 120.7764 | 0.15564 | -1.3458 | 120.7214 | 120.6757 | -1.2497 | 120.7993 | 120.6894 | 0.013733 | -1.2772 | 120.9183 | 120.7764 | 120.7581 | -1.5015 | 120.8725 | 120.845 | 120.8084 | -1.4465
5869 | 122.3419 | -120.7031 | 1.3321 | -0.0354 | 0.048691 | 0.058191 | 0.0072461 | 0.025056 | -0.0085856 | 0.02851 | -0.0012209 | 0.011029 | 0.026201 | 0.035998 | -0.00046349 | 0.017105 | 0.027466 | 0.059509 | 0.068665 | 0.045776 | 0.086975 | 0.036621 | -0.12817 | 0.11444 | 0.1236 | 0.041199 | 0.050354 | 0.032043 | -0.036621 | -0.073242 | 120.7397 | 120.575 | -1.2451 | 120.7626 | 120.7489 | 0.17395 | -1.3046 | 120.6665 | 120.6299 | -1.2817 | 120.8176 | 120.7443 | 0.11444 | -1.3 | 120.7901 | 120.7306 | 120.7718 | -1.4603 | 120.7535 | 120.7352 | 120.8267 | -1.4053
5870.7031 | 122.3328 | -120.6619 | 1.355 | 0.094299 | 0.051468 | 0.0599 | 0.00083745 | 0.027192 | 0.00081382 | 0.028937 | 0.12085 | 0.015729 | 0.022142 | 0.037066 | 0.0061587 | 0.0139 | 0.036621 | 0.022888 | -0.004578 | 0 | 0.12817 | 0.022888 | -0.14191 | 0.10529 | 0.068665 | -0.013733 | 0.050354 | 0.045776 | -0.045776 | -0.082397 | 120.6848 | 120.52 | -1.2268 | 120.6848 | 120.6619 | 0.14191 | -1.3184 | 120.6161 | 120.5795 | -1.3046 | 120.7672 | 120.6482 | 0.068664 | -1.3092 | 120.7901 | 120.6985 | 120.6573 | -1.4969 | 120.7123 | 120.7077 | 120.7306 | -1.4374
5872.3906 | 122.2687 | -120.6802 | 1.4191 | -0.21851 | 0.0504 | 0.058405 | 0.0055371 | 0.024201 | -0.0034586 | 0.026588 | -0.19196 | 0.014234 | 0.025774 | 0.036425 | 0.0031681 | 0.016464 | 0.013733 | -0.018311 | -0.027466 | 0.004578 | 0.11902 | 0 | -0.14648 | 0.041199 | 0.032043 | -0.068665 | 0.091553 | 0.086975 | -0.050354 | -0.10529 | 120.6802 | 120.5338 | -1.3 | 120.6619 | 120.6848 | 0.15106 | -1.4053 | 120.6299 | 120.575 | -1.3275 | 120.7214 | 120.6116 | 0.036621 | -1.3321 | 120.7993 | 120.694 | 120.6528 | -1.5656 | 120.7718 | 120.7672 | 120.7123 | -1.5244
5874.1406 | 122.2229 | -120.7581 | 1.355 | 0.048523 | 0.051041 | 0.058618 | 0.0014783 | 0.02591 | -0.0011088 | 0.027442 | 0.0064086 | 0.016156 | 0.023424 | 0.038134 | 0.0031681 | 0.017105 | 0.013733 | -0.022888 | -0.027466 | -0.009155 | 0.1236 | 0.004578 | -0.15106 | 0 | 0 | -0.1236 | 0.091553 | 0.068665 | -0.064087 | -0.11444 | 120.7626 | 120.607 | -1.2314 | 120.7352 | 120.7489 | 0.14191 | -1.3412 | 120.694 | 120.6436 | -1.2634 | 120.7581 | 120.6345 | -0.009155 | -1.2863 | 120.8817 | 120.7718 | 120.7306 | -1.506 | 120.8496 | 120.8267 | 120.7581 | -1.4694
5875.8594 | 122.3328 | -120.7718 | 1.2863 | -0.14221 | 0.046555 | 0.061609 | 0.0057507 | 0.02826 | -0.0085856 | 0.028083 | -0.092773 | 0.011029 | 0.026628 | 0.033007 | -0.0011045 | 0.017532 | 0.082397 | 0.17395 | 0.13275 | 0.082397 | 0.086975 | 0.045776 | -0.11902 | 0.12817 | 0.17853 | 0.073242 | 0.032043 | 0.032043 | -0.032043 | -0.082397 | 120.8176 | 120.6528 | -1.1993 | 120.9457 | 120.8542 | 0.20142 | -1.2039 | 120.7397 | 120.6894 | -1.2543 | 120.9 | 120.845 | 0.15564 | -1.2543 | 120.8588 | 120.8542 | 120.9045 | -1.4053 | 120.8038 | 120.8038 | 120.9503 | -1.3687
5877.625 | 122.3099 | -120.7672 | 1.3 | 0.11719 | 0.046128 | 0.056909 | 0.0019055 | 0.024629 | -0.0045266 | 0.030219 | 0.13611 | 0.011029 | 0.024492 | 0.036638 | 0.00081811 | 0.017532 | 0.10986 | 0.1236 | 0.11444 | 0.068665 | 0.073242 | 0.050354 | -0.11444 | 0.16937 | 0.13275 | 0.041199 | 0.041199 | 0.013733 | -0.032043 | -0.07782 | 120.8176 | 120.6528 | -1.2268 | 120.8908 | 120.8359 | 0.18311 | -1.1902 | 120.7352 | 120.6894 | -1.2589 | 120.9366 | 120.8084 | 0.11902 | -1.2863 | 120.8405 | 120.8771 | 120.8817 | -1.4145 | 120.8084 | 120.7809 | 120.9 | -1.3779
5879.3438 | 122.2641 | -120.8221 | 1.2772 | -0.13458 | 0.052536 | 0.057123 | 0.0019055 | 0.027619 | 0.00038662 | 0.027869 | -0.16144 | 0.012952 | 0.022783 | 0.03792 | 0.0033817 | 0.013687 | 0.068665 | 0.041199 | 0.018311 | 0.036621 | 0.10071 | 0.022888 | -0.13733 | 0.086975 | 0.064087 | -0.059509 | 0.073242 | 0.073242 | -0.050354 | -0.10071 | 120.845 | 120.6848 | -1.1765 | 120.8633 | 120.8588 | 0.17395 | -1.2085 | 120.7718 | 120.7214 | -1.2039 | 120.9091 | 120.7626 | 0.041199 | -1.2039 | 120.9229 | 120.8908 | 120.8405 | -1.4145 | 120.8954 | 120.8954 | 120.8862 | -1.3779
5881.0781 | 122.319 | -120.7947 | 1.268 | 0.010376 | 0.046555 | 0.060754 | 0.0038281 | 0.026338 | -0.0079446 | 0.027228 | 0.059815 | 0.011884 | 0.022569 | 0.033648 | -0.00089089 | 0.019455 | 0.027466 | 0.068665 | 0.054932 | 0.032043 | 0.086975 | 0.041199 | -0.11444 | 0.07782 | 0.082397 | 0.004578 | 0.045776 | 0.022888 | -0.036621 | -0.07782 | 120.8359 | 120.6802 | -1.181 | 120.8633 | 120.8267 | 0.14648 | -1.2405 | 120.7581 | 120.7169 | -1.2222 | 120.8725 | 120.7993 | 0.082398 | -1.2451 | 120.8817 | 120.8221 | 120.8496 | -1.3824 | 120.8405 | 120.8176 | 120.8771 | -1.3458
5882.7969 | 122.2321 | -120.8588 | 1.2955 | -0.10406 | 0.051682 | 0.058832 | 0.0016919 | 0.029115 | 0.00060022 | 0.027015 | -0.13855 | 0.015729 | 0.02321 | 0.037493 | 0.0053043 | 0.014968 | 0.091553 | 0.050354 | 0.009155 | 0.036621 | 0.10529 | 0.004578 | -0.13733 | 0.09613 | 0.073242 | -0.045776 | 0.073242 | 0.054932 | -0.059509 | -0.091553 | 120.8633 | 120.7214 | -1.1902 | 120.9091 | 120.8954 | 0.17395 | -1.2039 | 120.7993 | 120.7672 | -1.2222 | 120.9549 | 120.813 | 0.045777 | -1.2405 | 120.9641 | 120.9503 | 120.8679 | -1.4328 | 120.932 | 120.9137 | 120.932 | -1.387
5884.5 | 122.3557 | -120.7993 | 1.2497 | -0.13458 | 0.050186 | 0.059473 | 0.0042555 | 0.02826 | -0.010508 | 0.029578 | -0.092773 | 0.011029 | 0.024065 | 0.03557 | -0.0028135 | 0.015396 | 0.10071 | 0.16022 | 0.1236 | 0.082397 | 0.073242 | 0.045776 | -0.10986 | 0.16022 | 0.19226 | 0.059509 | 0.022888 | 0.032043 | -0.022888 | -0.07782 | 120.845 | 120.6894 | -1.1765 | 120.9595 | 120.8817 | 0.19226 | -1.149 | 120.7764 | 120.7214 | -1.2268 | 120.9595 | 120.8588 | 0.13733 | -1.2177 | 120.8725 | 120.9 | 120.9229 | -1.3596 | 120.8221 | 120.8313 | 120.9915 | -1.3275
5886.25 | 122.2824 | -120.8496 | 1.2863 | -0.23376 | 0.050614 | 0.058405 | 0.0044691 | 0.027192 | -0.0019632 | 0.027869 | -0.20721 | 0.016156 | 0.024065 | 0.039202 | 0.0053043 | 0.014114 | 0.004578 | -0.004578 | -0.027466 | 0 | 0.13275 | 0.004578 | -0.16022 | 0.022888 | 0.022888 | -0.068665 | 0.082397 | 0.068665 | -0.050354 | -0.10986 | 120.8542 | 120.6894 | -1.1536 | 120.845 | 120.8496 | 0.16022 | -1.2817 | 120.7993 | 120.7397 | -1.2039 | 120.8725 | 120.7809 | 0.041198 | -1.2177 | 120.9824 | 120.8542 | 120.8221 | -1.4465 | 120.932 | 120.9183 | 120.8725 | -1.3962
5887.9844 | 122.2549 | -120.8405 | 1.2817 | -0.18799 | 0.0504 | 0.061609 | 0.0063917 | 0.029115 | -0.0064492 | 0.027015 | -0.16907 | 0.0091066 | 0.024705 | 0.037279 | 0.0018863 | 0.018386 | 0.07782 | 0.13733 | 0.09613 | 0.082397 | 0.086975 | 0.045776 | -0.11902 | 0.10986 | 0.15564 | 0.022888 | 0.050354 | 0.022888 | -0.041199 | -0.073242 | 120.8862 | 120.7214 | -1.1948 | 120.9778 | 120.9229 | 0.20142 | -1.2039 | 120.7993 | 120.7672 | -1.2314 | 120.9503 | 120.8633 | 0.09613 | -1.2589 | 120.9274 | 120.9183 | 120.9366 | -1.4008 | 120.8908 | 120.8633 | 120.9961 | -1.355
5889.7344 | 122.319 | -120.8633 | 1.2405 | 0.079041 | 0.046128 | 0.060541 | -0.00023075 | 0.030183 | -0.0055948 | 0.027869 | 0.10559 | 0.01167 | 0.022142 | 0.034075 | 0.0042361 | 0.018173 | 0.09613 | 0.11902 | 0.10071 | 0.064087 | 0.082397 | 0.036621 | -0.11444 | 0.13733 | 0.10529 | 0.013733 | 0.041199 | 0.027466 | -0.022888 | -0.082397 | 120.9 | 120.7489 | -1.1581 | 120.9824 | 120.9274 | 0.17853 | -1.1444 | 120.8405 | 120.7809 | -1.1993 | 121.0007 | 120.8771 | 0.09613 | -1.2131 | 120.9457 | 120.9595 | 120.9641 | -1.355 | 120.9045 | 120.8908 | 120.9686 | -1.3229
5891.4219 | 122.2458 | -120.8725 | 1.2589 | -0.12695 | 0.0504 | 0.059045 | 0.0091687 | 0.026979 | -0.0038858 | 0.025733 | -0.2301 | 0.014447 | 0.02556 | 0.037493 | 0.00017731 | 0.015396 | 0.004578 | 0.013733 | -0.009155 | -0.009155 | 0.11902 | -0.009155 | -0.13733 | 0.027466 | 0.036621 | -0.068665 | 0.082397 | 0.068665 | -0.068665 | -0.10071 | 120.8633 | 120.7352 | -1.1398 | 120.8862 | 120.8633 | 0.12817 | -1.2543 | 120.8038 | 120.7718 | -1.1765 | 120.9 | 120.8038 | 0.032043 | -1.1902 | 120.9915 | 120.8771 | 120.8633 | -1.3962 | 120.9549 | 120.9412 | 120.9091 | -1.3596
5893.125 | 122.3419 | -120.9045 | 1.2039 | 0.040894 | 0.044846 | 0.058832 | 0.0019055 | 0.026765 | -0.0055948 | 0.027442 | 0.052185 | 0.011457 | 0.022569 | 0.032366 | 0.00017731 | 0.018386 | 0.050354 | 0.082397 | 0.064087 | 0.032043 | 0.064087 | 0.027466 | -0.1236 | 0.10071 | 0.07782 | 0.004578 | 0.036621 | 0.032043 | -0.032043 | -0.073242 | 120.932 | 120.7809 | -1.1398 | 120.9869 | 120.9366 | 0.15564 | -1.1536 | 120.8725 | 120.8313 | -1.1673 | 121.0052 | 120.9091 | 0.07782 | -1.1719 | 120.9686 | 120.9549 | 120.9686 | -1.3275 | 120.9412 | 120.9366 | 120.9824 | -1.2772
5894.8281 | 122.2412 | -120.7672 | 1.3824 | -0.0354 | 0.050614 | 0.056482 | 0.0014783 | 0.027192 | 0.0023092 | 0.027869 | -0.054626 | 0.015943 | 0.022996 | 0.036852 | 0.0059451 | 0.016464 | 0.054932 | 0.004578 | -0.013733 | 0.009155 | 0.11444 | 0 | -0.12817 | 0.032043 | 0 | -0.11902 | 0.073242 | 0.054932 | -0.054932 | -0.11444 | 120.7672 | 120.639 | -1.268 | 120.7718 | 120.7764 | 0.13733 | -1.3275 | 120.7123 | 120.6528 | -1.3092 | 120.7993 | 120.6482 | -0.004578 | -1.3275 | 120.8817 | 120.8221 | 120.7535 | -1.5106 | 120.8405 | 120.8221 | 120.7672 | -1.4969
5896.5938 | 122.3969 | -120.6802 | 1.3733 | 0.14008 | 0.047837 | 0.060114 | 0.0021191 | 0.027619 | -0.0023904 | 0.028724 | 0.10559 | 0.014234 | 0.021928 | 0.033861 | 0.0031681 | 0.0186 | 0.027466 | 0.036621 | 0.036621 | 0.022888 | 0.10071 | 0.032043 | -0.12817 | 0.12817 | 0.09613 | 0.009155 | 0.050354 | 0.045776 | -0.018311 | -0.073242 | 120.7123 | 120.5521 | -1.2726 | 120.7169 | 120.7031 | 0.15106 | -1.3458 | 120.6619 | 120.607 | -1.3229 | 120.8084 | 120.6894 | 0.082397 | -1.3275 | 120.7809 | 120.7077 | 120.7169 | -1.5015 | 120.7306 | 120.726 | 120.7764 | -1.4465
5898.3125 | 122.3007 | -119.5999 | 2.536 | -0.1651 | 0.050614 | 0.056909 | 0.0070325 | 0.029115 | -0.0034586 | 0.028937 | -0.21484 | 0.012311 | 0.023851 | 0.035998 | 0.0025271 | 0.015182 | 0.013733 | -0.004578 | -0.022888 | 0.004578 | 0.13733 | 0.004578 | -0.14191 | 0.032043 | 0.073242 | -0.054932 | 0.07782 | 0.068665 | -0.064087 | -0.11444 | 119.6045 | 119.458 | -2.3987 | 119.5953 | 119.6045 | 0.14649 | -2.5223 | 119.5358 | 119.4855 | -2.4582 | 119.632 | 119.545 | 0.059509 | -2.4673 | 119.7372 | 119.6136 | 119.577 | -2.6779 | 119.6777 | 119.6686 | 119.6732 | -2.6505
5900.0469 | 122.3877 | -120.7947 | 1.2772 | 0.063782 | 0.050827 | 0.060754 | 0.00019645 | 0.026765 | -0.003245 | 0.027656 | 0.12085 | 0.014875 | 0.02321 | 0.037066 | 0.0033817 | 0.018386 | 0.032043 | 0.013733 | -0.018311 | 0 | 0.10529 | -0.004578 | -0.14648 | 0.073242 | 0.036621 | -0.036621 | 0.073242 | 0.059509 | -0.036621 | -0.082397 | 120.7901 | 120.6482 | -1.1719 | 120.8084 | 120.7947 | 0.14648 | -1.2451 | 120.7581 | 120.7123 | -1.2039 | 120.8679 | 120.7581 | 0.045776 | -1.2177 | 120.9 | 120.8267 | 120.7764 | -1.4236 | 120.8679 | 120.8542 | 120.8313 | -1.3596
5901.7812 | 122.4014 | -120.7855 | 1.3229 | -0.14984 | 0.048691 | 0.059473 | 0.0055371 | 0.027833 | -0.010295 | 0.027015 | -0.062256 | 0.01167 | 0.026628 | 0.033861 | -0.0019589 | 0.017746 | 0.091553 | 0.16022 | 0.11902 | 0.082397 | 0.064087 | 0.022888 | -0.1236 | 0.16479 | 0.1831 | 0.091553 | 0.036621 | 0.018311 | -0.027466 | -0.064087 | 120.8084 | 120.6619 | -1.2589 | 120.9457 | 120.8679 | 0.20599 | -1.2314 | 120.7581 | 120.7214 | -1.2863 | 120.9503 | 120.8771 | 0.15564 | -1.3046 | 120.8496 | 120.8771 | 120.9045 | -1.4465 | 120.8221 | 120.8038 | 120.9686 | -1.387
5903.5156 | 122.2687 | -120.8038 | 1.355 | -0.25665 | 0.048264 | 0.060114 | 0.0042555 | 0.028474 | -0.0053812 | 0.025733 | -0.19196 | 0.012952 | 0.02556 | 0.038347 | -0.00067729 | 0.017105 | 0.045776 | 0.054932 | 0.041199 | 0.045776 | 0.086975 | 0.004578 | -0.1236 | 0.059509 | 0.059509 | -0.050354 | 0.082397 | 0.045776 | -0.041199 | -0.10986 | 120.8084 | 120.6802 | -1.268 | 120.8588 | 120.8496 | 0.16937 | -1.3092 | 120.7626 | 120.694 | -1.2726 | 120.8633 | 120.7535 | 0.059509 | -1.3092 | 120.8908 | 120.8496 | 120.845 | -1.4786 | 120.8862 | 120.8496 | 120.8633 | -1.4648
5905.25 | 122.2733 | -120.8221 | 1.3687 | -0.38635 | 0.048905 | 0.058832 | 0.0051099 | 0.027833 | -0.003245 | 0.024879 | -0.22247 | 0.013166 | 0.024919 | 0.03557 | -0.0011045 | 0.016677 | 0.009155 | 0.022888 | -0.013733 | -0.013733 | 0.11902 | 0 | -0.15106 | 0.009155 | 0.045776 | -0.073242 | 0.073242 | 0.073242 | -0.059509 | -0.12817 | 120.8221 | 120.6711 | -1.2497 | 120.845 | 120.8084 | 0.13733 | -1.3596 | 120.7626 | 120.694 | -1.2955 | 120.8313 | 120.7489 | 0.054932 | -1.2955 | 120.9412 | 120.8313 | 120.8084 | -1.5198 | 120.8954 | 120.8954 | 120.8679 | -1.4969
5906.9844 | 122.374 | -120.7489 | 1.3641 | -0.14221 | 0.048691 | 0.0599 | 0.0036145 | 0.02527 | -0.0075174 | 0.026588 | -0.1767 | 0.012097 | 0.023637 | 0.036211 | -0.00067729 | 0.018173 | 0.10529 | 0.15564 | 0.11444 | 0.068665 | 0.086975 | 0.036621 | -0.082397 | 0.14648 | 0.18768 | 0.068665 | 0.032043 | 0.022888 | -0.013733 | -0.073242 | 120.7855 | 120.6665 | -1.2772 | 120.9045 | 120.8176 | 0.15106 | -1.2589 | 120.7352 | 120.6757 | -1.3321 | 120.8954 | 120.8176 | 0.14191 | -1.3412 | 120.8359 | 120.8542 | 120.8633 | -1.4465 | 120.7809 | 120.7718 | 120.9366 | -1.4374
5908.7188 | 122.3419 | -120.7489 | 1.3824 | -0.27191 | 0.049759 | 0.058832 | 0.0029737 | 0.026551 | -0.0017496 | 0.026374 | -0.25299 | 0.014661 | 0.024919 | 0.037279 | 0.0023135 | 0.015182 | 0.013733 | 0 | -0.032043 | 0 | 0.11444 | -0.018311 | -0.16479 | 0.041199 | 0.027466 | -0.091553 | 0.082397 | 0.068665 | -0.064087 | -0.10529 | 120.7306 | 120.5841 | -1.268 | 120.7489 | 120.7489 | 0.16479 | -1.3687 | 120.6848 | 120.6436 | -1.3 | 120.7901 | 120.6573 | 0.013733 | -1.3138 | 120.8633 | 120.7626 | 120.7169 | -1.5472 | 120.8313 | 120.8176 | 120.7764 | -1.4877
5910.4688 | 122.287 | -120.7489 | 1.4191 | -0.19562 | 0.048264 | 0.061395 | 0.00083745 | 0.026551 | -0.0045266 | 0.030006 | -0.20721 | 0.011884 | 0.024278 | 0.033861 | 0.0016727 | 0.015182 | 0.082397 | 0.13275 | 0.082397 | 0.068665 | 0.091553 | 0.036621 | -0.11444 | 0.10986 | 0.15564 | 0.013733 | 0.059509 | 0.045776 | -0.027466 | -0.086975 | 120.7855 | 120.6345 | -1.3275 | 120.8817 | 120.8176 | 0.18311 | -1.3367 | 120.7214 | 120.6619 | -1.3596 | 120.8588 | 120.7626 | 0.10071 | -1.3733 | 120.8405 | 120.8313 | 120.8313 | -1.5335 | 120.8084 | 120.7947 | 120.9045 | -1.506
5912.1875 | 122.3969 | -120.6848 | 1.4328 | 0.12482 | 0.048264 | 0.057977 | -0.0027941 | 0.026551 | 0.00017302 | 0.028297 | 0.052185 | 0.013379 | 0.021928 | 0.033648 | 0.0040225 | 0.017746 | 0.07782 | 0.068665 | 0.059509 | 0.045776 | 0.086975 | 0.041199 | -0.10986 | 0.13733 | 0.13733 | 0.022888 | 0.050354 | 0.027466 | -0.022888 | -0.064087 | 120.726 | 120.575 | -1.3458 | 120.7535 | 120.7306 | 0.15564 | -1.355 | 120.6619 | 120.6207 | -1.3824 | 120.8221 | 120.7077 | 0.086975 | -1.4053 | 120.7718 | 120.7626 | 120.7443 | -1.5427 | 120.7352 | 120.7123 | 120.8221 | -1.4969
5913.9062 | 122.2824 | -120.7123 | 1.4694 | -0.30243 | 0.051895 | 0.057336 | 0.0059643 | 0.025483 | -0.0051676 | 0.028083 | -0.19958 | 0.010388 | 0.027055 | 0.034716 | 0.00039091 | 0.016464 | 0 | 0.022888 | -0.004578 | -0.009155 | 0.12817 | 0 | -0.14648 | 0.018311 | 0.036621 | -0.059509 | 0.091553 | 0.050354 | -0.086975 | -0.10529 | 120.7123 | 120.5658 | -1.3412 | 120.7352 | 120.7031 | 0.13733 | -1.4694 | 120.6253 | 120.607 | -1.3779 | 120.7306 | 120.6528 | 0.045777 | -1.4191 | 120.8405 | 120.7123 | 120.7077 | -1.6159 | 120.8038 | 120.7626 | 120.7489 | -1.5747
5915.6406 | 122.3007 | -120.6802 | 1.4877 | -0.18799 | 0.049118 | 0.056696 | 0.0057507 | 0.028901 | -0.0051676 | 0.027228 | -0.14618 | 0.011884 | 0.025774 | 0.034716 | 0.00039091 | 0.015609 | 0.068665 | 0.12817 | 0.10071 | 0.082397 | 0.073242 | 0.036621 | -0.11444 | 0.10986 | 0.15564 | 0.018311 | 0.036621 | 0.036621 | -0.009155 | -0.082397 | 120.7169 | 120.5658 | -1.4145 | 120.8084 | 120.7626 | 0.19684 | -1.4191 | 120.6711 | 120.5978 | -1.4511 | 120.7901 | 120.6985 | 0.10071 | -1.4511 | 120.7535 | 120.7489 | 120.7809 | -1.6022 | 120.7169 | 120.7169 | 120.8359 | -1.5701
5917.375 | 122.3969 | -120.6116 | 1.474 | 0.15533 | 0.048264 | 0.060754 | -0.0010851 | 0.026765 | -0.0023904 | 0.030006 | 0.067444 | 0.013166 | 0.021501 | 0.034716 | 0.0048769 | 0.019668 | 0.082397 | 0.068665 | 0.082397 | 0.073242 | 0.082397 | 0.022888 | -0.1236 | 0.14648 | 0.13275 | 0.036621 | 0.045776 | 0.004578 | -0.027466 | -0.064087 | 120.6345 | 120.488 | -1.3916 | 120.6802 | 120.6848 | 0.19684 | -1.3916 | 120.5841 | 120.5475 | -1.4282 | 120.7581 | 120.6482 | 0.10071 | -1.4694 | 120.694 | 120.694 | 120.694 | -1.5976 | 120.6573 | 120.6161 | 120.7443 | -1.5381
5919.1094 | 122.4472 | -120.607 | 1.4969 | -0.058289 | 0.048477 | 0.060327 | 0.0051099 | 0.027406 | -0.0090128 | 0.027869 | -0.031738 | 0.012738 | 0.023424 | 0.034716 | -0.00089089 | 0.018386 | 0.045776 | 0.10071 | 0.073242 | 0.045776 | 0.10071 | 0.022888 | -0.11444 | 0.14191 | 0.13275 | 0.064087 | 0.059509 | 0.041199 | -0.027466 | -0.073242 | 120.6299 | 120.4926 | -1.3962 | 120.7077 | 120.6528 | 0.16022 | -1.4511 | 120.5795 | 120.5338 | -1.4374 | 120.7489 | 120.6711 | 0.13733 | -1.4557 | 120.7077 | 120.6528 | 120.6802 | -1.6113 | 120.6665 | 120.6482 | 120.7397 | -1.5701
5920.8438 | 122.4289 | -120.5795 | 1.5106 | 0.08667 | 0.046128 | 0.058405 | 0.0027601 | 0.029115 | -0.00025418 | 0.027228 | 0.12848 | 0.013379 | 0.023851 | 0.036211 | 0.0044497 | 0.015823 | 0.032043 | 0.009155 | -0.013733 | 0.013733 | 0.11902 | 0.022888 | -0.13275 | 0.10986 | 0.045776 | -0.045776 | 0.064087 | 0.064087 | -0.022888 | -0.086975 | 120.6024 | 120.4468 | -1.3916 | 120.5887 | 120.5933 | 0.14648 | -1.4786 | 120.5566 | 120.4926 | -1.4465 | 120.6894 | 120.5338 | 0.041199 | -1.4465 | 120.6985 | 120.6116 | 120.5658 | -1.6434 | 120.6436 | 120.6436 | 120.6253 | -1.5976
5922.625 | 122.4106 | -120.5612 | 1.561 | 0.094299 | 0.050186 | 0.061182 | -0.00044435 | 0.026979 | -0.00025418 | 0.028297 | 0.059815 | 0.014447 | 0.021715 | 0.035998 | 0.0033817 | 0.017105 | 0.018311 | 0 | -0.022888 | -0.004578 | 0.1236 | 0.004578 | -0.13275 | 0.073242 | 0.013733 | -0.064087 | 0.073242 | 0.050354 | -0.054932 | -0.09613 | 120.5658 | 120.4285 | -1.4374 | 120.5612 | 120.5566 | 0.12817 | -1.5427 | 120.5063 | 120.4651 | -1.4877 | 120.6345 | 120.4971 | 0.032043 | -1.5106 | 120.6848 | 120.5795 | 120.5383 | -1.6937 | 120.6345 | 120.6116 | 120.575 | -1.6571
5924.3438 | 122.4152 | -120.575 | 1.5289 | 0.14008 | 0.047409 | 0.057764 | 0.0031873 | 0.029756 | -0.002604 | 0.030433 | 0.10559 | 0.012311 | 0.023424 | 0.036638 | 0.0027407 | 0.019027 | 0.091553 | 0.10529 | 0.073242 | 0.073242 | 0.09613 | 0.036621 | -0.10071 | 0.15564 | 0.1236 | 0.036621 | 0.032043 | 0.022888 | -0.009155 | -0.054932 | 120.6116 | 120.4742 | -1.4328 | 120.6802 | 120.6482 | 0.17395 | -1.4374 | 120.5658 | 120.52 | -1.4969 | 120.7306 | 120.6116 | 0.091553 | -1.506 | 120.6711 | 120.6665 | 120.6482 | -1.6296 | 120.607 | 120.5978 | 120.6985 | -1.5839
5926.0781 | 122.2961 | -120.5246 | 1.6663 | -0.24139 | 0.048264 | 0.059473 | 0.0057507 | 0.026979 | -0.003245 | 0.028937 | -0.20721 | 0.011457 | 0.027269 | 0.035998 | -0.0017453 | 0.017959 | -0.009155 | 0.027466 | -0.013733 | -0.013733 | 0.11444 | 0 | -0.13733 | 0.027466 | 0.054932 | -0.07782 | 0.082397 | 0.086975 | -0.064087 | -0.10986 | 120.5246 | 120.3873 | -1.5518 | 120.5521 | 120.5109 | 0.1236 | -1.6754 | 120.4605 | 120.4147 | -1.5839 | 120.5521 | 120.4468 | 0.032043 | -1.5793 | 120.639 | 120.5154 | 120.5109 | -1.8036 | 120.607 | 120.6116 | 120.5795 | -1.7761
5927.7812 | 122.3969 | -120.0714 | 2.0691 | 0.094299 | 0.043991 | 0.0599 | 0.00083745 | 0.026338 | -0.0075174 | 0.027228 | 0.097962 | 0.01167 | 0.024705 | 0.035357 | 0.0025271 | 0.017318 | 0.054932 | 0.11444 | 0.07782 | 0.054932 | 0.082397 | 0.041199 | -0.086975 | 0.10071 | 0.086975 | 0.022888 | 0.045776 | 0.022888 | -0.013733 | -0.07782 | 120.1126 | 119.9844 | -1.9867 | 120.1859 | 120.1263 | 0.14191 | -2.0142 | 120.0577 | 119.9936 | -2.0233 | 120.1721 | 120.0943 | 0.10071 | -2.0462 | 120.1538 | 120.1263 | 120.1492 | -2.1561 | 120.1172 | 120.0943 | 120.1584 | -2.1469
5929.5 | 122.438 | -120.1813 | 1.9089 | 0.14771 | 0.049973 | 0.059473 | -1.7146e-05 | 0.02826 | -0.0011088 | 0.031501 | 0.12848 | 0.01402 | 0.022996 | 0.034929 | 0.0031681 | 0.01625 | 0.054932 | 0.027466 | 0.027466 | 0.013733 | 0.1236 | 0.018311 | -0.10986 | 0.12817 | 0.09613 | 0.004578 | 0.032043 | 0.027466 | -0.022888 | -0.073242 | 120.1996 | 120.0714 | -1.7853 | 120.2087 | 120.195 | 0.1236 | -1.8539 | 120.1584 | 120.108 | -1.8768 | 120.3094 | 120.1859 | 0.07782 | -1.8814 | 120.3049 | 120.2362 | 120.2087 | -2.0187 | 120.2133 | 120.2087 | 120.2774 | -1.9821
5931.2031 | 122.3373 | -120.0439 | 2.1332 | -0.24902 | 0.049546 | 0.0599 | 0.0055371 | 0.027192 | -0.0040994 | 0.025733 | -0.2301 | 0.014234 | 0.025133 | 0.035784 | 0.00039091 | 0.01625 | -0.009155 | -0.004578 | -0.036621 | -0.004578 | 0.11902 | -0.013733 | -0.15564 | 0.022888 | 0.013733 | -0.091553 | 0.091553 | 0.07782 | -0.041199 | -0.11444 | 120.0302 | 119.8883 | -2.0142 | 120.0394 | 120.0394 | 0.15106 | -2.1423 | 120.0027 | 119.9295 | -2.0416 | 120.0668 | 119.9524 | 0.022888 | -2.0554 | 120.163 | 120.0348 | 120.0073 | -2.2888 | 120.1355 | 120.1218 | 120.0577 | -2.2476
5932.9375 | 122.4426 | -120.2591 | 1.886 | -0.14221 | 0.048264 | 0.059686 | 0.0046827 | 0.026338 | -0.0068766 | 0.026588 | -0.069885 | 0.011457 | 0.025133 | 0.034929 | -0.0019589 | 0.014328 | 0.10071 | 0.16937 | 0.13733 | 0.086975 | 0.082397 | 0.036621 | -0.10986 | 0.16937 | 0.19684 | 0.086975 | 0.050354 | 0.022888 | -0.018311 | -0.068665 | 120.2957 | 120.1492 | -1.8036 | 120.4285 | 120.3461 | 0.19684 | -1.7853 | 120.2408 | 120.1904 | -1.8356 | 120.4285 | 120.3461 | 0.15564 | -1.8631 | 120.3415 | 120.3598 | 120.3964 | -1.9958 | 120.3094 | 120.282 | 120.4559 | -1.9547
5934.6875 | 122.3602 | -120.3598 | 1.8356 | -0.14984 | 0.048264 | 0.056482 | 0.0031873 | 0.028901 | -0.00025418 | 0.027228 | -0.18433 | 0.016797 | 0.02321 | 0.038134 | 0.0050907 | 0.015182 | 0.07782 | 0.045776 | 0.022888 | 0.041199 | 0.1236 | 0.004578 | -0.13275 | 0.07782 | 0.073242 | -0.036621 | 0.091553 | 0.041199 | -0.054932 | -0.086975 | 120.3644 | 120.2271 | -1.712 | 120.4056 | 120.401 | 0.17395 | -1.7578 | 120.3049 | 120.2728 | -1.7441 | 120.4376 | 120.3232 | 0.050354 | -1.7944 | 120.4834 | 120.4376 | 120.3827 | -1.9684 | 120.4514 | 120.401 | 120.433 | -1.9226
5936.4219 | 122.3282 | -120.108 | 2.0828 | -0.081177 | 0.049546 | 0.057764 | -0.00065795 | 0.028688 | 0.00060022 | 0.031074 | -0.1004 | 0.01637 | 0.022569 | 0.036638 | 0.0055179 | 0.014328 | 0.068665 | 0.050354 | 0.022888 | 0.027466 | 0.10986 | 0.027466 | -0.1236 | 0.059509 | 0.073242 | -0.068665 | 0.064087 | 0.073242 | -0.032043 | -0.10986 | 120.1355 | 119.9844 | -1.973 | 120.1584 | 120.1355 | 0.15106 | -2.0142 | 120.076 | 119.9982 | -2.0187 | 120.1675 | 120.0394 | 0.041198 | -2.0096 | 120.2179 | 120.1767 | 120.1309 | -2.2064 | 120.1721 | 120.1813 | 120.1813 | -2.1927
5938.1406 | 122.3419 | -120.0989 | 2.092 | -0.12695 | 0.052109 | 0.057123 | 0.0021191 | 0.025483 | -0.0023904 | 0.030646 | -0.12329 | 0.012952 | 0.025774 | 0.036211 | 0.0035953 | 0.016037 | 0.059509 | 0.041199 | 0.027466 | 0.032043 | 0.12817 | 0.009155 | -0.14648 | 0.091553 | 0.086975 | -0.041199 | 0.068665 | 0.050354 | -0.050354 | -0.086975 | 120.108 | 119.9524 | -1.9638 | 120.1401 | 120.1309 | 0.17853 | -2.0325 | 120.0485 | 120.0119 | -2.0233 | 120.1904 | 120.0577 | 0.045776 | -2.0416 | 120.2271 | 120.1584 | 120.1263 | -2.2385 | 120.1675 | 120.1492 | 120.1859 | -2.179
5939.8906 | 122.2733 | -119.4855 | 2.6917 | -0.04303 | 0.051895 | 0.05755 | 0.0023329 | 0.027833 | -0.00046778 | 0.02851 | 0.036926 | 0.014234 | 0.024705 | 0.037279 | 0.0044497 | 0.0186 | 0.013733 | 0.027466 | -0.018311 | 0.013733 | 0.11444 | 0.004578 | -0.13733 | 0.018311 | 0.018311 | -0.10071 | 0.068665 | 0.059509 | -0.068665 | -0.11444 | 119.4901 | 119.3481 | -2.5772 | 119.5129 | 119.4992 | 0.15106 | -2.6779 | 119.4168 | 119.371 | -2.623 | 119.5038 | 119.3848 | 0.013733 | -2.6321 | 119.5999 | 119.4992 | 119.4672 | -2.829 | 119.5541 | 119.545 | 119.5038 | -2.8061
5941.6406 | 122.3969 | -118.2266 | 3.8864 | 0.14008 | 0.049118 | 0.057977 | 0.0016919 | 0.02591 | -0.0079446 | 0.028937 | 0.17426 | 0.012311 | 0.022996 | 0.034929 | 0.0027407 | 0.017105 | 0.086975 | 0.13275 | 0.11902 | 0.073242 | 0.064087 | 0.041199 | -0.09613 | 0.12817 | 0.13733 | 0.050354 | 0.022888 | 0.004578 | -0.036621 | -0.068665 | 118.2678 | 118.1305 | -3.8223 | 118.3594 | 118.2999 | 0.16937 | -3.7994 | 118.19 | 118.158 | -3.8635 | 118.3548 | 118.277 | 0.11902 | -3.8818 | 118.2907 | 118.3136 | 118.3456 | -3.9825 | 118.2495 | 118.2312 | 118.364 | -3.9551
5943.3594 | 122.3511 | -119.5633 | 2.6184 | -0.23376 | 0.049546 | 0.060541 | 0.0068189 | 0.028688 | -0.00089518 | 0.027015 | -0.19196 | 0.014447 | 0.025133 | 0.038134 | 0.00081811 | 0.016037 | -0.009155 | -0.004578 | -0.027466 | 0.018311 | 0.10986 | -0.009155 | -0.16479 | 0.022888 | 0.050354 | -0.059509 | 0.091553 | 0.07782 | -0.036621 | -0.091553 | 119.5541 | 119.3985 | -2.5085 | 119.5587 | 119.5816 | 0.18311 | -2.6276 | 119.5267 | 119.4717 | -2.5269 | 119.5862 | 119.5038 | 0.032044 | -2.5406 | 119.6732 | 119.5541 | 119.5358 | -2.7832 | 119.6548 | 119.6411 | 119.6136 | -2.71
5945.0625 | 122.4106 | -120.5154 | 1.6571 | 0.010376 | 0.045914 | 0.059686 | 0.0010511 | 0.026124 | -0.0075174 | 0.025947 | 0.090332 | 0.012097 | 0.021928 | 0.033434 | -0.00089089 | 0.019668 | 0.027466 | 0.082397 | 0.068665 | 0.036621 | 0.068665 | 0.041199 | -0.10529 | 0.10071 | 0.091553 | 0.022888 | 0.050354 | 0.032043 | 0 | -0.086975 | 120.5566 | 120.4102 | -1.5884 | 120.5978 | 120.5521 | 0.14191 | -1.6296 | 120.5154 | 120.4285 | -1.6067 | 120.6161 | 120.5383 | 0.10986 | -1.6251 | 120.5841 | 120.5429 | 120.5841 | -1.7624 | 120.5658 | 120.5475 | 120.607 | -1.7441
5946.7812 | 122.3465 | -120.3278 | 1.8356 | 0.033264 | 0.052536 | 0.05755 | 0.00019645 | 0.028474 | -0.0013224 | 0.027228 | 0.067444 | 0.015943 | 0.022569 | 0.036211 | 0.0059451 | 0.015182 | 0 | -0.059509 | -0.050354 | -0.018311 | 0.1236 | 0.004578 | -0.15106 | 0.013733 | -0.032043 | -0.09613 | 0.073242 | 0.059509 | -0.050354 | -0.10986 | 120.3323 | 120.1767 | -1.712 | 120.2682 | 120.3094 | 0.13275 | -1.8356 | 120.2774 | 120.2179 | -1.7624 | 120.3415 | 120.2316 | 0.013733 | -1.7761 | 120.4514 | 120.3278 | 120.2774 | -1.9867 | 120.401 | 120.3873 | 120.2957 | -1.9455
5948.5781 | 122.4197 | -120.6253 | 1.5381 | 0.018005 | 0.047409 | 0.060968 | 0.0034009 | 0.025483 | -0.0098672 | 0.025733 | 0.067444 | 0.011243 | 0.022142 | 0.034929 | -0.00024989 | 0.017532 | 0.041199 | 0.059509 | 0.054932 | 0.036621 | 0.073242 | 0.045776 | -0.09613 | 0.10071 | 0.086975 | 0.013733 | 0.045776 | 0.032043 | -0.018311 | -0.091553 | 120.6711 | 120.5292 | -1.4648 | 120.6848 | 120.6619 | 0.13275 | -1.4969 | 120.607 | 120.5338 | -1.4923 | 120.726 | 120.639 | 0.10529 | -1.506 | 120.6985 | 120.6665 | 120.6802 | -1.6342 | 120.6711 | 120.6573 | 120.7123 | -1.6296
5950.2969 | 122.4426 | -120.5887 | 1.5518 | 0.056152 | 0.049546 | 0.058832 | -1.7146e-05 | 0.027833 | 0.00017302 | 0.028937 | 0.10559 | 0.015943 | 0.022569 | 0.036638 | 0.0067997 | 0.017532 | 0.032043 | -0.004578 | -0.022888 | -0.004578 | 0.11444 | 0 | -0.15564 | 0.073242 | 0.032043 | -0.054932 | 0.07782 | 0.059509 | -0.041199 | -0.086975 | 120.5887 | 120.433 | -1.4374 | 120.5841 | 120.5841 | 0.15106 | -1.5198 | 120.5475 | 120.5017 | -1.474 | 120.6619 | 120.5338 | 0.032043 | -1.4923 | 120.7031 | 120.6207 | 120.5658 | -1.7075 | 120.6665 | 120.6482 | 120.6207 | -1.6388
5952.0781 | 122.4701 | -120.4605 | 1.6479 | 0.10956 | 0.051041 | 0.059473 | 0.00019645 | 0.026979 | -0.004313 | 0.028083 | 0.10559 | 0.012311 | 0.025346 | 0.035357 | 0.0031681 | 0.017532 | 0.091553 | 0.10986 | 0.091553 | 0.073242 | 0.082397 | 0.036621 | -0.09613 | 0.14648 | 0.12817 | 0.050354 | 0.050354 | 0.018311 | -0.027466 | -0.068665 | 120.4971 | 120.3644 | -1.5656 | 120.5704 | 120.5338 | 0.16937 | -1.5564 | 120.433 | 120.3918 | -1.5976 | 120.607 | 120.5109 | 0.11902 | -1.6296 | 120.5429 | 120.5521 | 120.5521 | -1.7441 | 120.5109 | 120.4788 | 120.5887 | -1.7166
5953.7812 | 122.3419 | -120.5154 | 1.7075 | -0.17273 | 0.0504 | 0.059686 | 0.0066053 | 0.026551 | -0.0038858 | 0.026801 | -0.22247 | 0.014661 | 0.024278 | 0.035357 | 0.00081811 | 0.017746 | -0.009155 | 0.009155 | -0.004578 | -0.018311 | 0.12817 | -0.009155 | -0.13733 | 0.018311 | 0.036621 | -0.064087 | 0.086975 | 0.068665 | -0.059509 | -0.11902 | 120.5063 | 120.3781 | -1.5793 | 120.5246 | 120.4971 | 0.11902 | -1.7166 | 120.4559 | 120.3964 | -1.6205 | 120.5338 | 120.4514 | 0.054932 | -1.6388 | 120.6436 | 120.5063 | 120.5109 | -1.8448 | 120.6024 | 120.5841 | 120.5521 | -1.8265
5955.5156 | 122.3602 | -120.4559 | 1.7578 | 0.063782 | 0.048905 | 0.061182 | -0.00065795 | 0.025697 | -0.00089518 | 0.027228 | 0.067444 | 0.012311 | 0.024705 | 0.034289 | 0.0078677 | 0.017318 | 0.018311 | -0.050354 | -0.041199 | 0 | 0.11444 | 0.004578 | -0.14191 | 0.032043 | -0.013733 | -0.10529 | 0.07782 | 0.07782 | -0.073242 | -0.10986 | 120.4605 | 120.314 | -1.6434 | 120.4056 | 120.4559 | 0.14191 | -1.7395 | 120.3827 | 120.3461 | -1.68 | 120.488 | 120.3506 | 0.004577 | -1.68 | 120.5704 | 120.4742 | 120.4147 | -1.8997 | 120.5338 | 120.5338 | 120.4422 | -1.8677
5957.2188 | 122.374 | -120.4239 | 1.799 | -0.25665 | 0.049332 | 0.060327 | 0.0051099 | 0.028901 | -0.0040994 | 0.028083 | -0.23773 | 0.015088 | 0.025133 | 0.039416 | 0.0025271 | 0.017318 | -0.009155 | -0.013733 | -0.022888 | 0.009155 | 0.11902 | -0.004578 | -0.14191 | 0.022888 | 0.032043 | -0.07782 | 0.086975 | 0.086975 | -0.059509 | -0.12817 | 120.4193 | 120.282 | -1.68 | 120.4102 | 120.433 | 0.15106 | -1.8082 | 120.3644 | 120.2957 | -1.712 | 120.4468 | 120.3461 | 0.050354 | -1.712 | 120.5429 | 120.4147 | 120.401 | -1.9409 | 120.5109 | 120.5109 | 120.4559 | -1.9272
5958.9219 | 122.4655 | -120.314 | 1.886 | -0.15747 | 0.046982 | 0.06225 | 0.0059643 | 0.027619 | -0.008372 | 0.028297 | -0.11566 | 0.012097 | 0.023637 | 0.034716 | -0.0013181 | 0.016464 | 0.09613 | 0.16937 | 0.1236 | 0.091553 | 0.082397 | 0.027466 | -0.11902 | 0.14191 | 0.19226 | 0.073242 | 0.045776 | 0.032043 | -0.027466 | -0.082397 | 120.3415 | 120.195 | -1.8036 | 120.4834 | 120.4056 | 0.21057 | -1.7899 | 120.2866 | 120.2316 | -1.8402 | 120.4559 | 120.3873 | 0.15564 | -1.8539 | 120.3964 | 120.4102 | 120.4376 | -2.005 | 120.3598 | 120.3461 | 120.5063 | -1.9684
5960.6406 | 122.3511 | -119.8654 | 2.3987 | -0.20325 | 0.052536 | 0.060114 | 0.0081007 | 0.024415 | -0.003245 | 0.026374 | -0.28351 | 0.01167 | 0.02556 | 0.037707 | 0.0012455 | 0.016891 | -0.004578 | 0.013733 | -0.009155 | -0.018311 | 0.11444 | -0.004578 | -0.15106 | 0.036621 | 0.041199 | -0.073242 | 0.082397 | 0.068665 | -0.054932 | -0.10986 | 119.8608 | 119.7144 | -2.2842 | 119.8791 | 119.8471 | 0.13275 | -2.4033 | 119.8105 | 119.7556 | -2.3163 | 119.902 | 119.7922 | 0.036621 | -2.33 | 119.9799 | 119.8608 | 119.8563 | -2.5497 | 119.9478 | 119.9341 | 119.9066 | -2.5085
5962.3438 | 122.4564 | -120.0943 | 2.0645 | 0.08667 | 0.050186 | 0.05755 | -0.0025805 | 0.026124 | -0.0011088 | 0.027228 | 0.067444 | 0.013379 | 0.024278 | 0.036638 | 0.0057315 | 0.0186 | 0.009155 | 0.013733 | -0.032043 | 0 | 0.13733 | 0 | -0.13733 | 0.064087 | 0.004578 | -0.054932 | 0.064087 | 0.045776 | -0.050354 | -0.11444 | 120.0943 | 119.957 | -1.9272 | 120.108 | 120.0943 | 0.13733 | -2.0554 | 120.0439 | 119.9799 | -2.0004 | 120.1584 | 120.0394 | 0.059509 | -2.0187 | 120.2316 | 120.1035 | 120.0623 | -2.2018 | 120.1584 | 120.1401 | 120.0989 | -2.179
5964.0469 | 122.3969 | -119.5267 | 2.6962 | -0.19562 | 0.052109 | 0.057764 | 0.0057507 | 0.026979 | -0.0045266 | 0.027442 | -0.21484 | 0.013166 | 0.024705 | 0.035143 | 0.0014591 | 0.014328 | 0.009155 | 0 | -0.022888 | 0.013733 | 0.11444 | 0.009155 | -0.15106 | 0.018311 | 0.054932 | -0.068665 | 0.086975 | 0.073242 | -0.059509 | -0.11444 | 119.5358 | 119.3756 | -2.5818 | 119.5267 | 119.5404 | 0.16479 | -2.6871 | 119.4672 | 119.4122 | -2.6093 | 119.545 | 119.458 | 0.045776 | -2.623 | 119.6411 | 119.5358 | 119.5038 | -2.8473 | 119.6136 | 119.5999 | 119.5816 | -2.8107
5965.75 | 122.4838 | -119.0643 | 3.0716 | -0.11169 | 0.047196 | 0.059473 | 0.0036145 | 0.025483 | -0.0098672 | 0.027015 | -0.062256 | 0.011457 | 0.024492 | 0.036425 | -0.0023861 | 0.017105 | 0.054932 | 0.12817 | 0.10071 | 0.073242 | 0.091553 | 0.032043 | -0.10986 | 0.14648 | 0.16479 | 0.064087 | 0.054932 | 0.022888 | -0.032043 | -0.050354 | 119.0964 | 118.9545 | -2.98 | 119.1925 | 119.1376 | 0.18311 | -3.0167 | 119.0323 | 119.014 | -3.0167 | 119.2108 | 119.1284 | 0.11444 | -3.0487 | 119.1559 | 119.1193 | 119.165 | -3.1815 | 119.1193 | 119.0872 | 119.2291 | -3.1219
5967.5469 | 122.4335 | -119.0598 | 3.1265 | 0.08667 | 0.049546 | 0.059686 | -0.00087155 | 0.024415 | -0.0021768 | 0.028297 | 0.029297 | 0.014875 | 0.022356 | 0.038561 | 0.0061587 | 0.014114 | 0.022888 | -0.018311 | -0.027466 | 0.013733 | 0.11902 | 0.004578 | -0.14191 | 0.045776 | -0.004578 | -0.07782 | 0.073242 | 0.045776 | -0.059509 | -0.10529 | 119.0643 | 118.9178 | -3.0075 | 119.0414 | 119.0735 | 0.15564 | -3.1036 | 119.0002 | 118.9545 | -3.0533 | 119.1055 | 118.9819 | 0.027466 | -3.0808 | 119.1788 | 119.0826 | 119.0323 | -3.2684 | 119.133 | 119.1055 | 119.0552 | -3.2318
5969.2812 | 122.4472 | -118.1213 | 4.01 | 0.11719 | 0.049973 | 0.058618 | 0.0038281 | 0.027619 | -0.0058084 | 0.02851 | 0.19714 | 0.014234 | 0.023424 | 0.036211 | 0.00081811 | 0.019882 | 0.11902 | 0.11902 | 0.10529 | 0.07782 | 0.068665 | 0.032043 | -0.091553 | 0.14191 | 0.14191 | 0.045776 | 0.036621 | 0.009155 | -0.027466 | -0.064087 | 118.1534 | 118.0298 | -3.9413 | 118.2404 | 118.1992 | 0.16937 | -3.891 | 118.0939 | 118.0573 | -3.9734 | 118.2632 | 118.1671 | 0.10986 | -4.0009 | 118.19 | 118.2404 | 118.2266 | -4.1016 | 118.158 | 118.1305 | 118.2632 | -4.0741
5970.9844 | 122.3694 | -120.2179 | 2.0096 | -0.23376 | 0.049546 | 0.059686 | 0.0053235 | 0.029115 | -0.001536 | 0.025947 | -0.24536 | 0.015515 | 0.024492 | 0.037493 | -3.629e-05 | 0.01625 | 0.013733 | -0.004578 | -0.022888 | -0.009155 | 0.1236 | 0 | -0.15106 | 0.018311 | 0.018311 | -0.086975 | 0.091553 | 0.086975 | -0.050354 | -0.11444 | 120.2179 | 120.0668 | -1.886 | 120.2133 | 120.2087 | 0.14191 | -1.9959 | 120.1675 | 120.1035 | -1.918 | 120.2362 | 120.1309 | 0.027466 | -1.9226 | 120.3415 | 120.2316 | 120.195 | -2.1606 | 120.3094 | 120.3049 | 120.2362 | -2.124
5972.7188 | 122.4838 | -120.1355 | 2.0142 | -0.027771 | 0.047196 | 0.05755 | 0.0053235 | 0.026338 | -0.010295 | 0.029578 | 0.029297 | 0.012738 | 0.025346 | 0.034502 | -0.0036679 | 0.019241 | 0.018311 | 0.054932 | 0.050354 | 0.032043 | 0.10986 | 0.032043 | -0.12817 | 0.091553 | 0.10986 | 0.032043 | 0.041199 | 0.041199 | -0.032043 | -0.07782 | 120.1675 | 120.0073 | -1.9043 | 120.1904 | 120.1675 | 0.16022 | -1.9958 | 120.1035 | 120.0577 | -1.973 | 120.2271 | 120.1675 | 0.10986 | -1.973 | 120.2454 | 120.1538 | 120.1859 | -2.1423 | 120.1767 | 120.1767 | 120.2454 | -2.092
5974.4219 | 122.3923 | -119.6732 | 2.5131 | -0.11932 | 0.051041 | 0.060114 | -1.7146e-05 | 0.026338 | -0.00025418 | 0.030219 | -0.16144 | 0.015515 | 0.024919 | 0.037066 | 0.0059451 | 0.013473 | 0.07782 | 0.045776 | 0.022888 | 0.041199 | 0.13275 | 0.004578 | -0.14648 | 0.09613 | 0.082397 | -0.041199 | 0.07782 | 0.059509 | -0.041199 | -0.091553 | 119.6777 | 119.5267 | -2.3804 | 119.7189 | 119.7144 | 0.18768 | -2.4353 | 119.632 | 119.5816 | -2.4353 | 119.7693 | 119.632 | 0.050354 | -2.4536 | 119.8059 | 119.751 | 119.696 | -2.6596 | 119.751 | 119.7327 | 119.7556 | -2.6047
5976.125 | 122.3694 | -119.1238 | 3.1174 | -0.22614 | 0.049973 | 0.060327 | 0.0046827 | 0.02826 | -0.006663 | 0.027228 | -0.22247 | 0.012525 | 0.026414 | 0.036852 | 0.00039091 | 0.015823 | -0.004578 | 0.022888 | 0 | -0.004578 | 0.12817 | -0.018311 | -0.15564 | 0.022888 | 0.050354 | -0.082397 | 0.091553 | 0.068665 | -0.07782 | -0.12817 | 119.1055 | 118.9682 | -2.9892 | 119.1467 | 119.1193 | 0.15106 | -3.1219 | 119.046 | 118.9957 | -3.0258 | 119.1467 | 119.0414 | 0.045777 | -3.0487 | 119.252 | 119.1193 | 119.1238 | -3.273 | 119.2154 | 119.1925 | 119.1742 | -3.2455
5977.8594 | 122.3648 | -119.9295 | 2.2888 | -0.21088 | 0.047837 | 0.059473 | 0.0042555 | 0.029542 | -0.0051676 | 0.025947 | -0.22247 | 0.01167 | 0.025987 | 0.037066 | 0.0010317 | 0.016037 | 0 | 0.013733 | 0.009155 | 0 | 0.10986 | -0.009155 | -0.14648 | 0.022888 | 0.054932 | -0.068665 | 0.10529 | 0.068665 | -0.068665 | -0.11902 | 119.9203 | 119.783 | -2.179 | 119.9432 | 119.9295 | 0.14648 | -2.2888 | 119.8608 | 119.8105 | -2.1835 | 119.9524 | 119.8608 | 0.050354 | -2.2202 | 120.0394 | 119.9295 | 119.9387 | -2.4353 | 120.0348 | 119.9982 | 119.9844 | -2.4078
5979.5625 | 122.3648 | -119.4763 | 2.7603 | 0.025635 | 0.0504 | 0.060968 | -0.0010851 | 0.026338 | 0.00060022 | 0.031287 | -0.016479 | 0.014875 | 0.024705 | 0.037066 | 0.0070133 | 0.016464 | 0.004578 | -0.027466 | -0.050354 | 0.004578 | 0.1236 | 0.013733 | -0.13733 | 0.013733 | -0.022888 | -0.086975 | 0.082397 | 0.064087 | -0.041199 | -0.11902 | 119.4901 | 119.339 | -2.6367 | 119.4489 | 119.4809 | 0.14191 | -2.7557 | 119.4351 | 119.3573 | -2.6779 | 119.4901 | 119.3893 | 0.032044 | -2.6962 | 119.5999 | 119.4809 | 119.426 | -2.8976 | 119.5587 | 119.5404 | 119.4534 | -2.8793
5981.2812 | 122.3602 | -119.1284 | 3.1265 | -0.20325 | 0.051468 | 0.058405 | 0.0078871 | 0.02826 | -0.0068766 | 0.027015 | -0.19958 | 0.011457 | 0.024705 | 0.03557 | -0.0015317 | 0.0186 | 0.059509 | 0.1236 | 0.07782 | 0.068665 | 0.091553 | 0.018311 | -0.1236 | 0.068665 | 0.11902 | -0.004578 | 0.064087 | 0.045776 | -0.045776 | -0.10071 | 119.1467 | 119.0048 | -3.035 | 119.252 | 119.1971 | 0.19226 | -3.067 | 119.0826 | 119.0277 | -3.0624 | 119.1971 | 119.1238 | 0.09613 | -3.0808 | 119.22 | 119.1879 | 119.2062 | -3.2501 | 119.1925 | 119.1742 | 119.2474 | -3.2272
5982.9844 | 122.4701 | -119.3069 | 2.8336 | 0.094299 | 0.048905 | 0.057764 | -1.7146e-05 | 0.023774 | -0.0017496 | 0.028724 | 0.14374 | 0.013166 | 0.021928 | 0.036852 | 0.0048769 | 0.015823 | 0.022888 | 0.018311 | 0 | 0.013733 | 0.10529 | 0.013733 | -0.1236 | 0.10071 | 0.054932 | -0.032043 | 0.054932 | 0.045776 | -0.027466 | -0.086975 | 119.3207 | 119.1833 | -2.7283 | 119.3253 | 119.3207 | 0.13733 | -2.8107 | 119.2795 | 119.22 | -2.7786 | 119.4077 | 119.2749 | 0.054932 | -2.7878 | 119.4122 | 119.3298 | 119.3069 | -2.9572 | 119.3619 | 119.3527 | 119.3619 | -2.9205
5984.7188 | 122.4838 | -119.2703 | 2.9022 | 0.10193 | 0.050614 | 0.058832 | 0.00019645 | 0.026338 | -0.004313 | 0.030433 | 0.13611 | 0.014234 | 0.021501 | 0.034929 | 0.0050907 | 0.017105 | 0.091553 | 0.11902 | 0.091553 | 0.073242 | 0.064087 | 0.059509 | -0.09613 | 0.14648 | 0.12817 | 0.045776 | 0.036621 | 0.032043 | -0.022888 | -0.07782 | 119.3298 | 119.1742 | -2.8381 | 119.3893 | 119.3436 | 0.16937 | -2.8107 | 119.2474 | 119.1925 | -2.8656 | 119.4168 | 119.3161 | 0.1236 | -2.8702 | 119.3344 | 119.3619 | 119.3619 | -2.9984 | 119.3069 | 119.3024 | 119.3985 | -2.98
5986.4219 | 122.4014 | -119.5175 | 2.7191 | -0.21851 | 0.048477 | 0.058191 | 0.0053235 | 0.028047 | -0.0028178 | 0.029578 | -0.1767 | 0.013806 | 0.025346 | 0.037707 | 0.0012455 | 0.016037 | 0.018311 | -0.013733 | -0.027466 | 0.004578 | 0.12817 | -0.004578 | -0.15564 | 0.022888 | 0.022888 | -0.082397 | 0.07782 | 0.064087 | -0.054932 | -0.11902 | 119.5129 | 119.3619 | -2.5909 | 119.5038 | 119.5221 | 0.16022 | -2.7008 | 119.4626 | 119.3985 | -2.6413 | 119.5404 | 119.4351 | 0.036622 | -2.655 | 119.6457 | 119.5358 | 119.4901 | -2.8748 | 119.5953 | 119.5816 | 119.5404 | -2.8381
5988.1562 | 122.5113 | -119.6091 | 2.5772 | -0.0354 | 0.045273 | 0.06225 | 0.0029737 | 0.026124 | -0.011149 | 0.025733 | -0.016479 | 0.011029 | 0.023424 | 0.035143 | -0.00067729 | 0.019241 | 0.054932 | 0.073242 | 0.091553 | 0.064087 | 0.09613 | 0.027466 | -0.11444 | 0.11902 | 0.13733 | 0.050354 | 0.041199 | 0.041199 | -0.032043 | -0.07782 | 119.6365 | 119.4946 | -2.4811 | 119.6823 | 119.6732 | 0.17853 | -2.5223 | 119.577 | 119.5312 | -2.536 | 119.7281 | 119.6594 | 0.12817 | -2.536 | 119.7052 | 119.664 | 119.7006 | -2.6916 | 119.6503 | 119.6503 | 119.7464 | -2.655
5989.8594 | 122.374 | -117.4393 | 4.7333 | -0.096436 | 0.048905 | 0.058832 | 0.0023329 | 0.027833 | 0.00038662 | 0.027656 | -0.16144 | 0.015302 | 0.023851 | 0.037493 | 0.0044497 | 0.015396 | 0.10071 | 0.045776 | 0.013733 | 0.041199 | 0.10071 | 0.013733 | -0.15106 | 0.091553 | 0.082397 | -0.041199 | 0.07782 | 0.059509 | -0.050354 | -0.10071 | 117.453 | 117.2882 | -4.6326 | 117.485 | 117.4805 | 0.19226 | -4.6326 | 117.3889 | 117.3386 | -4.6555 | 117.5308 | 117.3981 | 0.059509 | -4.6738 | 117.54 | 117.54 | 117.453 | -4.8843 | 117.5171 | 117.4988 | 117.5217 | -4.834
5991.6094 | 122.438 | -119.3802 | 2.7695 | 0.10956 | 0.047837 | 0.057123 | 0.0023329 | 0.024415 | -0.0047404 | 0.028297 | 0.159 | 0.012525 | 0.022783 | 0.035357 | 0.0040225 | 0.01625 | 0.09613 | 0.10986 | 0.086975 | 0.086975 | 0.082397 | 0.022888 | -0.10986 | 0.13733 | 0.12817 | 0.036621 | 0.041199 | 0.032043 | -0.041199 | -0.059509 | 119.4031 | 119.2703 | -2.6871 | 119.4901 | 119.4672 | 0.19684 | -2.6733 | 119.339 | 119.3207 | -2.7283 | 119.5175 | 119.4168 | 0.09613 | -2.7374 | 119.4626 | 119.4763 | 119.4672 | -2.8793 | 119.4214 | 119.4122 | 119.5084 | -2.829
5993.2969 | 122.4152 | -119.5541 | 2.6871 | -0.18036 | 0.050186 | 0.059686 | 0.0063917 | 0.026765 | -4.058e-05 | 0.028083 | -0.2301 | 0.01402 | 0.02556 | 0.035784 | 0.0016727 | 0.01625 | 0.022888 | -0.009155 | -0.018311 | 0.018311 | 0.09613 | -0.009155 | -0.15564 | 0.045776 | 0.054932 | -0.064087 | 0.068665 | 0.086975 | -0.064087 | -0.11902 | 119.545 | 119.3985 | -2.5909 | 119.545 | 119.5724 | 0.17395 | -2.6642 | 119.4901 | 119.4351 | -2.6184 | 119.5999 | 119.4901 | 0.054932 | -2.6001 | 119.6503 | 119.577 | 119.5358 | -2.8427 | 119.6228 | 119.6411 | 119.6091 | -2.8061
5995.0312 | 122.3557 | -119.5908 | 2.6779 | -0.0354 | 0.053604 | 0.060327 | -0.00044435 | 0.02591 | -4.058e-05 | 0.028083 | 0.059815 | 0.015088 | 0.02321 | 0.035357 | 0.0055179 | 0.016677 | 0.041199 | 0.004578 | -0.013733 | 0.009155 | 0.10986 | 0.009155 | -0.14648 | 0.018311 | 0.013733 | -0.082397 | 0.07782 | 0.059509 | -0.059509 | -0.11444 | 119.5999 | 119.4443 | -2.5681 | 119.5953 | 119.5999 | 0.15564 | -2.6367 | 119.5312 | 119.4763 | -2.6001 | 119.6091 | 119.5084 | 0.032044 | -2.6184 | 119.7006 | 119.632 | 119.577 | -2.8244 | 119.6686 | 119.6503 | 119.6045 | -2.7924
5996.7812 | 122.3831 | -119.2841 | 2.98 | -0.10406 | 0.0504 | 0.059473 | 0.0027601 | 0.028047 | -0.0017496 | 0.029792 | -0.069885 | 0.01402 | 0.025774 | 0.038775 | 0.0046633 | 0.017959 | 0.073242 | 0.041199 | 0.013733 | 0.027466 | 0.10529 | 0.027466 | -0.11902 | 0.064087 | 0.064087 | -0.059509 | 0.07782 | 0.059509 | -0.054932 | -0.09613 | 119.3115 | 119.165 | -2.8748 | 119.3253 | 119.3115 | 0.14649 | -2.9068 | 119.2291 | 119.1879 | -2.9022 | 119.3481 | 119.2245 | 0.036621 | -2.9205 | 119.3893 | 119.3573 | 119.2978 | -3.0991 | 119.3619 | 119.3436 | 119.3481 | -3.0762
5998.4844 | 122.406 | -119.5633 | 2.6642 | -0.21851 | 0.047409 | 0.059473 | 0.0068189 | 0.027619 | -0.011149 | 0.026801 | -0.092773 | 0.011457 | 0.025774 | 0.035784 | -0.0021725 | 0.019455 | 0.073242 | 0.14648 | 0.11902 | 0.091553 | 0.07782 | 0.045776 | -0.11902 | 0.11444 | 0.1831 | 0.027466 | 0.045776 | 0.041199 | -0.018311 | -0.082397 | 119.6091 | 119.4443 | -2.5864 | 119.7098 | 119.6548 | 0.21057 | -2.5909 | 119.545 | 119.4809 | -2.6184 | 119.6777 | 119.5908 | 0.10986 | -2.623 | 119.6411 | 119.6365 | 119.6823 | -2.7832 | 119.6091 | 119.6045 | 119.7464 | -2.7466
6000.1875 | 122.4792 | -119.8196 | 2.3483 | 0.11719 | 0.048691 | 0.056909 | 0.00019645 | 0.026338 | -0.0047404 | 0.02851 | 0.20477 | 0.013806 | 0.023851 | 0.035784 | 0.0038089 | 0.016037 | 0.10529 | 0.10986 | 0.091553 | 0.082397 | 0.064087 | 0.045776 | -0.09613 | 0.13275 | 0.13733 | 0.032043 | 0.032043 | 0.018311 | -0.027466 | -0.064087 | 119.8654 | 119.7235 | -2.2842 | 119.9295 | 119.902 | 0.17853 | -2.243 | 119.7922 | 119.7556 | -2.3163 | 119.9524 | 119.8517 | 0.09613 | -2.33 | 119.8837 | 119.9249 | 119.9112 | -2.4445 | 119.8517 | 119.838 | 119.957 | -2.4124
6001.8906 | 122.4152 | -120.0119 | 2.2705 | -0.23376 | 0.049118 | 0.060541 | 0.0038281 | 0.028688 | -0.0045266 | 0.025947 | -0.24536 | 0.012952 | 0.027696 | 0.036638 | 0.00039091 | 0.018814 | -0.009155 | 0.009155 | -0.018311 | -0.004578 | 0.1236 | 0 | -0.15564 | 0 | 0.032043 | -0.082397 | 0.10071 | 0.050354 | -0.050354 | -0.10529 | 120.0119 | 119.8563 | -2.1469 | 120.0211 | 120.0073 | 0.15106 | -2.2797 | 119.9615 | 119.9066 | -2.1698 | 120.0119 | 119.9295 | 0.022889 | -2.2202 | 120.1355 | 120.0027 | 119.9936 | -2.4261 | 120.1126 | 120.0623 | 120.0439 | -2.3758
6003.6406 | 122.3877 | -119.8563 | 2.4307 | -0.20325 | 0.050186 | 0.061395 | 0.0070325 | 0.029328 | -0.0058084 | 0.026374 | -0.22247 | 0.012311 | 0.02556 | 0.034929 | -0.0011045 | 0.017318 | 0.086975 | 0.11902 | 0.091553 | 0.068665 | 0.09613 | 0.022888 | -0.10529 | 0.091553 | 0.14648 | 0.009155 | 0.064087 | 0.036621 | -0.041199 | -0.09613 | 119.8791 | 119.751 | -2.3346 | 119.9753 | 119.9249 | 0.17395 | -2.3438 | 119.8151 | 119.7601 | -2.3666 | 119.9478 | 119.8654 | 0.10528 | -2.3941 | 119.9524 | 119.9432 | 119.9478 | -2.536 | 119.9203 | 119.8929 | 120.0027 | -2.5269
6005.3438 | 122.4655 | -119.4122 | 2.7969 | 0.025635 | 0.046128 | 0.060754 | 0.0027601 | 0.026338 | -0.0055948 | 0.026801 | 0.052185 | 0.01167 | 0.022142 | 0.033221 | 0.00039091 | 0.017318 | 0.027466 | 0.07782 | 0.059509 | 0.045776 | 0.086975 | 0.050354 | -0.12817 | 0.086975 | 0.07782 | 0.022888 | 0.045776 | 0.027466 | -0.032043 | -0.086975 | 119.4626 | 119.2841 | -2.71 | 119.4901 | 119.458 | 0.17395 | -2.7695 | 119.3802 | 119.3253 | -2.7512 | 119.4992 | 119.4351 | 0.10986 | -2.7695 | 119.4992 | 119.4397 | 119.4717 | -2.9251 | 119.458 | 119.4397 | 119.4901 | -2.8839
6007.0469 | 122.4335 | -119.5496 | 2.7237 | 0.056152 | 0.0504 | 0.05755 | -0.0021533 | 0.027192 | 0.0010276 | 0.026588 | 0.044556 | 0.012311 | 0.024065 | 0.037066 | 0.0063723 | 0.014755 | 0.018311 | -0.045776 | -0.032043 | -0.004578 | 0.10986 | 0 | -0.14191 | 0.022888 | -0.022888 | -0.10071 | 0.091553 | 0.054932 | -0.059509 | -0.11444 | 119.5496 | 119.4077 | -2.6138 | 119.5038 | 119.545 | 0.13733 | -2.7054 | 119.4901 | 119.4351 | -2.6321 | 119.5724 | 119.4489 | 0.013733 | -2.6688 | 119.6594 | 119.5679 | 119.5175 | -2.8656 | 119.6411 | 119.6045 | 119.5267 | -2.8381
6008.75 | 122.438 | -119.7418 | 2.449 | -0.15747 | 0.051682 | 0.056696 | 0.0044691 | 0.026124 | -0.00068138 | 0.027442 | -0.19196 | 0.014661 | 0.025774 | 0.036638 | 0.00060451 | 0.014328 | 0.054932 | 0.027466 | 0.004578 | 0.041199 | 0.11444 | -0.004578 | -0.15106 | 0.073242 | 0.073242 | -0.054932 | 0.064087 | 0.050354 | -0.059509 | -0.11444 | 119.7372 | 119.5908 | -2.3346 | 119.7693 | 119.783 | 0.19226 | -2.3941 | 119.6823 | 119.6274 | -2.3849 | 119.8151 | 119.6869 | 0.059509 | -2.3987 | 119.8563 | 119.7968 | 119.7464 | -2.6001 | 119.8059 | 119.7922 | 119.8151 | -2.5635
6010.4844 | 122.4243 | -119.8334 | 2.3941 | -0.18799 | 0.051041 | 0.060114 | 0.0057507 | 0.026551 | -0.0036722 | 0.029578 | -0.22247 | 0.013379 | 0.024705 | 0.033434 | 0.00081811 | 0.017318 | 0 | 0.009155 | -0.004578 | 0.018311 | 0.12817 | 0.009155 | -0.14648 | 0.045776 | 0.059509 | -0.064087 | 0.068665 | 0.068665 | -0.054932 | -0.091553 | 119.8425 | 119.6869 | -2.2659 | 119.8425 | 119.8517 | 0.16479 | -2.3941 | 119.7784 | 119.7418 | -2.3254 | 119.8792 | 119.7693 | 0.027466 | -2.3254 | 119.9615 | 119.8334 | 119.8288 | -2.5406 | 119.902 | 119.902 | 119.8929 | -2.4857
6012.1875 | 122.5204 | -120.0302 | 2.1835 | -0.0048827 | 0.046982 | 0.060114 | 0.0029737 | 0.029756 | -0.010295 | 0.025947 | 0.059815 | 0.010602 | 0.024919 | 0.034929 | -0.00067729 | 0.019027 | -0.004578 | 0.054932 | 0.068665 | 0.041199 | 0.091553 | 0.041199 | -0.11444 | 0.086975 | 0.09613 | 0.045776 | 0.045776 | 0.036621 | -0.032043 | -0.10529 | 120.0714 | 119.9158 | -2.092 | 120.0851 | 120.0714 | 0.15564 | -2.1881 | 119.9982 | 119.9249 | -2.1378 | 120.1172 | 120.076 | 0.15106 | -2.1469 | 120.1218 | 120.0256 | 120.0989 | -2.298 | 120.076 | 120.0668 | 120.1263 | -2.2888
6013.8906 | 122.4152 | -119.9799 | 2.3071 | 0.018005 | 0.051255 | 0.057764 | -0.0012987 | 0.026338 | 0.00081382 | 0.028083 | 0.052185 | 0.015943 | 0.023851 | 0.038561 | 0.0053043 | 0.015396 | 0.009155 | -0.036621 | -0.054932 | -0.009155 | 0.10986 | 0.004578 | -0.13733 | 0.027466 | -0.009155 | -0.09613 | 0.091553 | 0.073242 | -0.059509 | -0.13275 | 119.9844 | 119.8425 | -2.1973 | 119.9432 | 119.9707 | 0.12817 | -2.298 | 119.9203 | 119.8471 | -2.2156 | 120.0073 | 119.8837 | 0.036621 | -2.2339 | 120.0897 | 119.989 | 119.9249 | -2.4445 | 120.0714 | 120.0531 | 119.9707 | -2.4399
6015.6406 | 122.438 | -119.8059 | 2.3895 | 0.08667 | 0.04805 | 0.058405 | 0.0027601 | 0.027192 | -0.008372 | 0.025519 | 0.16663 | 0.011457 | 0.024705 | 0.033648 | -0.00024989 | 0.019455 | 0.068665 | 0.11902 | 0.10986 | 0.07782 | 0.073242 | 0.041199 | -0.10986 | 0.11444 | 0.10529 | 0.022888 | 0.050354 | 0.022888 | -0.022888 | -0.086975 | 119.8471 | 119.696 | -2.3163 | 119.9249 | 119.8837 | 0.18768 | -2.3209 | 119.783 | 119.7189 | -2.3392 | 119.9203 | 119.8288 | 0.10986 | -2.3666 | 119.8791 | 119.8746 | 119.9158 | -2.4994 | 119.8563 | 119.8288 | 119.9112 | -2.4765
6017.3438 | 122.438 | -119.9432 | 2.3346 | -0.24139 | 0.047837 | 0.058832 | 0.0051099 | 0.026338 | -0.002604 | 0.026801 | -0.2301 | 0.014661 | 0.024705 | 0.037493 | 0.0020999 | 0.016037 | 0.009155 | -0.004578 | -0.032043 | 0.004578 | 0.13733 | -0.013733 | -0.14648 | 0.018311 | 0.032043 | -0.10071 | 0.086975 | 0.073242 | -0.050354 | -0.10986 | 119.9295 | 119.7968 | -2.1973 | 119.9387 | 119.9478 | 0.15106 | -2.3254 | 119.8929 | 119.8334 | -2.2476 | 119.9615 | 119.8425 | 0.009155 | -2.2614 | 120.0806 | 119.9524 | 119.9112 | -2.4811 | 120.0302 | 120.0165 | 119.9753 | -2.4445
6019.0781 | 122.5571 | -119.9112 | 2.3026 | -0.058289 | 0.047837 | 0.059045 | 0.0070325 | 0.029115 | -0.0096536 | 0.025306 | -0.016479 | 0.013166 | 0.024492 | 0.037279 | -0.0036679 | 0.020309 | 0.041199 | 0.09613 | 0.086975 | 0.050354 | 0.09613 | 0.032043 | -0.10986 | 0.13275 | 0.15106 | 0.054932 | 0.032043 | 0.018311 | -0.022888 | -0.091553 | 119.9432 | 119.8013 | -2.2064 | 120.0073 | 119.9615 | 0.16022 | -2.2614 | 119.8883 | 119.8196 | -2.2705 | 120.0439 | 119.9661 | 0.14649 | -2.2842 | 120.0073 | 119.9524 | 119.9982 | -2.4124 | 119.9432 | 119.9295 | 120.0623 | -2.3941
6020.7812 | 122.525 | -119.8791 | 2.3712 | -0.020142 | 0.046982 | 0.0599 | 0.0012647 | 0.028474 | -0.0062356 | 0.027228 | 0.021668 | 0.011243 | 0.023424 | 0.034502 | 0.0025271 | 0.019027 | 0.018311 | 0.068665 | 0.050354 | 0.036621 | 0.091553 | 0.022888 | -0.10529 | 0.09613 | 0.11444 | 0.041199 | 0.050354 | 0.032043 | -0.036621 | -0.091553 | 119.902 | 119.7739 | -2.2797 | 119.9478 | 119.9158 | 0.14191 | -2.3529 | 119.8425 | 119.7876 | -2.3209 | 119.9753 | 119.9203 | 0.13275 | -2.3392 | 119.9707 | 119.8975 | 119.9295 | -2.4765 | 119.9295 | 119.9112 | 119.9936 | -2.4628
6022.4844 | 122.406 | -119.8151 | 2.4857 | 0.033264 | 0.050827 | 0.059259 | -0.00087155 | 0.026338 | 0.0010276 | 0.027869 | -0.046997 | 0.016156 | 0.02321 | 0.037493 | 0.0063723 | 0.015396 | 0.022888 | -0.018311 | -0.036621 | 0.004578 | 0.10071 | 0.018311 | -0.13733 | 0.018311 | -0.009155 | -0.12817 | 0.073242 | 0.073242 | -0.054932 | -0.1236 | 119.8334 | 119.6777 | -2.3849 | 119.7968 | 119.8196 | 0.14191 | -2.4628 | 119.7601 | 119.6915 | -2.4124 | 119.8334 | 119.6869 | -0.004578 | -2.4124 | 119.9158 | 119.838 | 119.7784 | -2.623 | 119.8883 | 119.8883 | 119.8059 | -2.6093
6024.2188 | 122.4472 | -120.1401 | 2.1103 | 0.094299 | 0.048905 | 0.057764 | 0.0021191 | 0.02527 | -0.00068138 | 0.026801 | 0.082703 | 0.013806 | 0.023424 | 0.037066 | 0.0070133 | 0.016677 | 0.022888 | -0.027466 | -0.041199 | -0.009155 | 0.11444 | 0.009155 | -0.13733 | 0.036621 | -0.009155 | -0.091553 | 0.064087 | 0.068665 | -0.059509 | -0.11902 | 120.1492 | 120.0027 | -1.9959 | 120.1126 | 120.1309 | 0.12817 | -2.0874 | 120.0806 | 120.0211 | -2.0462 | 120.1767 | 120.0485 | 0.027466 | -2.0416 | 120.2545 | 120.163 | 120.0989 | -2.2476 | 120.2042 | 120.2087 | 120.1309 | -2.2293
6025.9219 | 122.5067 | -119.9295 | 2.2751 | 0.10193 | 0.052109 | 0.056055 | 0.0051099 | 0.025697 | -0.001536 | 0.028724 | 0.18951 | 0.013593 | 0.024705 | 0.034716 | 0.0027407 | 0.016677 | 0.10071 | 0.1236 | 0.10071 | 0.07782 | 0.07782 | 0.045776 | -0.10986 | 0.16022 | 0.13733 | 0.054932 | 0.036621 | 0.027466 | -0.022888 | -0.068665 | 119.9753 | 119.8196 | -2.1973 | 120.0531 | 120.0073 | 0.18768 | -2.1744 | 119.9066 | 119.8608 | -2.2385 | 120.0897 | 119.9844 | 0.1236 | -2.2476 | 120.0073 | 120.0302 | 120.0302 | -2.3849 | 119.9661 | 119.957 | 120.0668 | -2.3438
6027.625 | 122.5159 | -119.7784 | 2.449 | -0.15747 | 0.048477 | 0.058618 | 0.0053235 | 0.027406 | -0.0055948 | 0.025733 | -0.13855 | 0.010388 | 0.023851 | 0.038561 | -0.0025999 | 0.015182 | 0.11444 | 0.13733 | 0.12817 | 0.091553 | 0.086975 | 0.013733 | -0.10071 | 0.15106 | 0.18768 | 0.068665 | 0.036621 | 0.036621 | -0.009155 | -0.07782 | 119.7922 | 119.6777 | -2.3621 | 119.9158 | 119.87 | 0.19226 | -2.3346 | 119.7693 | 119.7006 | -2.4124 | 119.9295 | 119.8471 | 0.14649 | -2.4124 | 119.8654 | 119.8929 | 119.9066 | -2.5497 | 119.8151 | 119.8151 | 119.9661 | -2.5269
6029.3438 | 122.3969 | -119.6548 | 2.6505 | -0.27191 | 0.049759 | 0.058191 | 0.0048963 | 0.028047 | -0.0038858 | 0.027656 | -0.21484 | 0.012097 | 0.023637 | 0.03557 | 0.0010317 | 0.016891 | 0.045776 | 0.064087 | 0.036621 | 0.041199 | 0.10986 | 0 | -0.15106 | 0.036621 | 0.059509 | -0.064087 | 0.068665 | 0.064087 | -0.059509 | -0.10986 | 119.6548 | 119.5038 | -2.5406 | 119.7189 | 119.696 | 0.19226 | -2.6047 | 119.5953 | 119.545 | -2.5818 | 119.6915 | 119.5908 | 0.045776 | -2.5864 | 119.7647 | 119.7006 | 119.6915 | -2.8015 | 119.7235 | 119.7189 | 119.7144 | -2.7603
6031.0781 | 122.4335 | -119.5633 | 2.7191 | -0.25665 | 0.045487 | 0.06225 | 0.0016919 | 0.026765 | -0.0034586 | 0.027869 | -0.25299 | 0.012525 | 0.024492 | 0.036211 | -3.629e-05 | 0.015609 | 0.013733 | 0.013733 | -0.027466 | -0.013733 | 0.13733 | -0.013733 | -0.16022 | 0.018311 | 0.027466 | -0.07782 | 0.082397 | 0.068665 | -0.054932 | -0.11444 | 119.5496 | 119.4031 | -2.5818 | 119.577 | 119.5496 | 0.14648 | -2.7054 | 119.5084 | 119.4489 | -2.6367 | 119.5816 | 119.4855 | 0.036621 | -2.6505 | 119.7006 | 119.577 | 119.5358 | -2.8793 | 119.6457 | 119.632 | 119.5908 | -2.8336
6032.7969 | 122.3831 | -119.4168 | 2.8931 | -0.25665 | 0.050827 | 0.060754 | 0.0046827 | 0.026338 | -0.0058084 | 0.026801 | -0.39032 | 0.012525 | 0.025133 | 0.036638 | 0.0018863 | 0.017318 | 0.036621 | 0.050354 | 0.018311 | 0.018311 | 0.11444 | 0.004578 | -0.14191 | 0.032043 | 0.054932 | -0.064087 | 0.082397 | 0.068665 | -0.059509 | -0.10529 | 119.4214 | 119.2749 | -2.7786 | 119.4672 | 119.4351 | 0.16022 | -2.8564 | 119.3573 | 119.3115 | -2.8107 | 119.4489 | 119.3527 | 0.041199 | -2.8244 | 119.5312 | 119.4534 | 119.4351 | -3.035 | 119.4992 | 119.4855 | 119.4717 | -2.9984
6034.5625 | 122.4197 | -120.3781 | 1.9135 | -0.25665 | 0.050614 | 0.058405 | 0.0055371 | 0.026124 | -0.0053812 | 0.024879 | -0.13092 | 0.01167 | 0.026201 | 0.037066 | -0.00024989 | 0.017105 | 0.018311 | 0.059509 | 0.022888 | 0.027466 | 0.10986 | 0.009155 | -0.13733 | 0.036621 | 0.064087 | -0.041199 | 0.086975 | 0.073242 | -0.059509 | -0.12817 | 120.3873 | 120.2408 | -1.8036 | 120.4376 | 120.4056 | 0.16479 | -1.8951 | 120.3186 | 120.2499 | -1.8265 | 120.4147 | 120.3369 | 0.086975 | -1.8402 | 120.488 | 120.3964 | 120.401 | -2.0508 | 120.4651 | 120.4514 | 120.4422 | -2.0416
6036.2656 | 122.493 | -120.2408 | 2.0142 | 0.033264 | 0.046341 | 0.060327 | 0.00041005 | 0.025483 | -0.0073038 | 0.027015 | 0.059815 | 0.012952 | 0.02321 | 0.037493 | 0.0033817 | 0.017959 | 0.041199 | 0.082397 | 0.073242 | 0.036621 | 0.091553 | 0.027466 | -0.11444 | 0.10529 | 0.10071 | 0.018311 | 0.032043 | 0.027466 | -0.018311 | -0.082397 | 120.2683 | 120.1263 | -1.9226 | 120.3232 | 120.2774 | 0.15106 | -1.973 | 120.2225 | 120.1584 | -1.9821 | 120.3461 | 120.2591 | 0.10071 | -1.9867 | 120.3323 | 120.282 | 120.314 | -2.1286 | 120.2728 | 120.2683 | 120.3415 | -2.0966
6037.9688 | 122.4518 | -120.2591 | 2.0325 | -0.11932 | 0.048905 | 0.058832 | 0.0023329 | 0.027406 | 0.00017302 | 0.025733 | -0.16907 | 0.015943 | 0.023637 | 0.037279 | 0.0046633 | 0.015396 | 0.068665 | 0.045776 | 0.027466 | 0.041199 | 0.12817 | 0.004578 | -0.13275 | 0.073242 | 0.07782 | -0.045776 | 0.064087 | 0.059509 | -0.036621 | -0.10071 | 120.2637 | 120.1263 | -1.9043 | 120.3049 | 120.3003 | 0.17395 | -1.9638 | 120.2225 | 120.1584 | -1.9684 | 120.3323 | 120.2133 | 0.054932 | -1.973 | 120.3873 | 120.3278 | 120.2866 | -2.1652 | 120.3232 | 120.3186 | 120.3369 | -2.1332
6039.7031 | 122.4335 | -120.2728 | 2.0325 | -0.081177 | 0.050827 | 0.058191 | 0.0029737 | 0.03061 | -0.0011088 | 0.027869 | -0.15381 | 0.012525 | 0.025133 | 0.039843 | 0.0027407 | 0.015609 | 0.07782 | 0.068665 | 0.018311 | 0.050354 | 0.10529 | 0.004578 | -0.15106 | 0.10529 | 0.10071 | -0.045776 | 0.073242 | 0.054932 | -0.054932 | -0.09613 | 120.2774 | 120.1218 | -1.9272 | 120.3415 | 120.3232 | 0.20142 | -1.9547 | 120.2179 | 120.1767 | -1.9592 | 120.3781 | 120.2271 | 0.050354 | -1.9775 | 120.3781 | 120.3506 | 120.2911 | -2.1835 | 120.3461 | 120.3278 | 120.3735 | -2.1286
6041.4062 | 122.4976 | -120.108 | 2.1378 | 0.063782 | 0.047196 | 0.059686 | 0.0023329 | 0.026551 | -0.0079446 | 0.02851 | 0.14374 | 0.013166 | 0.024492 | 0.036211 | 0.0027407 | 0.020736 | 0.068665 | 0.11902 | 0.082397 | 0.050354 | 0.064087 | 0.036621 | -0.10529 | 0.11444 | 0.10986 | 0.018311 | 0.045776 | 0.022888 | -0.013733 | -0.068665 | 120.1447 | 120.0027 | -2.0737 | 120.2271 | 120.1584 | 0.15564 | -2.0691 | 120.0943 | 120.0394 | -2.092 | 120.2225 | 120.1263 | 0.086976 | -2.1149 | 120.1721 | 120.1767 | 120.1904 | -2.243 | 120.1538 | 120.1309 | 120.2179 | -2.2064
6043.1406 | 122.438 | -120.108 | 2.179 | 0.033264 | 0.049118 | 0.059045 | -0.0019397 | 0.026124 | 0.0023092 | 0.029365 | 0.036926 | 0.015515 | 0.024278 | 0.039416 | 0.0053043 | 0.01625 | -0.013733 | -0.045776 | -0.054932 | -0.027466 | 0.11902 | 0.009155 | -0.16022 | 0.018311 | -0.009155 | -0.091553 | 0.082397 | 0.059509 | -0.045776 | -0.10529 | 120.1172 | 119.9478 | -2.0599 | 120.0623 | 120.0806 | 0.13275 | -2.1927 | 120.0623 | 120.0027 | -2.0966 | 120.1263 | 120.0165 | 0.013733 | -2.1194 | 120.2271 | 120.0943 | 120.0531 | -2.3392 | 120.1904 | 120.1675 | 120.0989 | -2.2842
6044.8438 | 122.4609 | -119.9707 | 2.3254 | -0.14221 | 0.049118 | 0.059686 | 0.0014783 | 0.026979 | -0.0011088 | 0.031074 | -0.16907 | 0.013806 | 0.026201 | 0.036638 | 0.0040225 | 0.014968 | 0.059509 | 0.050354 | 0.004578 | 0.036621 | 0.11902 | 0.022888 | -0.14648 | 0.082397 | 0.086975 | -0.036621 | 0.064087 | 0.064087 | -0.059509 | -0.10986 | 119.9936 | 119.8242 | -2.2064 | 120.0211 | 120.0073 | 0.18311 | -2.2659 | 119.9112 | 119.8608 | -2.2614 | 120.0531 | 119.9341 | 0.073242 | -2.2614 | 120.0897 | 120.0302 | 119.9753 | -2.4719 | 120.0348 | 120.0348 | 120.0577 | -2.4353
6046.5469 | 122.5571 | -119.9158 | 2.33 | -0.10406 | 0.047623 | 0.060327 | 0.0044691 | 0.02591 | -0.011576 | 0.028297 | -0.077515 | 0.010816 | 0.026628 | 0.035357 | -0.0015317 | 0.016677 | 0.073242 | 0.16022 | 0.12817 | 0.073242 | 0.091553 | 0.027466 | -0.10986 | 0.15106 | 0.17395 | 0.091553 | 0.032043 | 0.041199 | -0.022888 | -0.064087 | 119.9432 | 119.8059 | -2.2385 | 120.076 | 119.989 | 0.18311 | -2.2568 | 119.8929 | 119.8517 | -2.298 | 120.0668 | 120.0073 | 0.15564 | -2.2888 | 120.0073 | 119.989 | 120.0439 | -2.4399 | 119.9478 | 119.957 | 120.0897 | -2.3941
6048.2656 | 122.5662 | -119.7601 | 2.4902 | -0.012512 | 0.044632 | 0.060754 | 0.0023329 | 0.026338 | -0.0087992 | 0.027442 | 0.052185 | 0.012738 | 0.022996 | 0.033434 | 0.0018863 | 0.017318 | 0.022888 | 0.059509 | 0.064087 | 0.045776 | 0.10529 | 0.027466 | -0.10529 | 0.073242 | 0.091553 | 0.018311 | 0.050354 | 0.027466 | -0.036621 | -0.073242 | 119.7876 | 119.6548 | -2.3849 | 119.8196 | 119.8059 | 0.15106 | -2.4673 | 119.7235 | 119.6869 | -2.4399 | 119.8334 | 119.7784 | 0.091553 | -2.4628 | 119.8654 | 119.783 | 119.8242 | -2.5955 | 119.8105 | 119.7876 | 119.8517 | -2.5635
6049.9688 | 122.4243 | -120.2225 | 2.0828 | 0.010376 | 0.050827 | 0.055841 | -0.0019397 | 0.026338 | 0.0012412 | 0.028083 | 0.0064086 | 0.013379 | 0.022569 | 0.038775 | 0.0048769 | 0.015823 | 0.022888 | -0.018311 | -0.032043 | 0.004578 | 0.1236 | -0.004578 | -0.14648 | 0.009155 | 0.009155 | -0.11902 | 0.07782 | 0.054932 | -0.064087 | -0.10986 | 120.2179 | 120.076 | -1.9592 | 120.2042 | 120.2271 | 0.15106 | -2.0599 | 120.1584 | 120.1126 | -2.005 | 120.2316 | 120.1035 | -0.009156 | -2.0279 | 120.3461 | 120.2454 | 120.1904 | -2.2293 | 120.3003 | 120.2774 | 120.2316 | -2.1927
6051.6719 | 122.4518 | -120.076 | 2.2339 | -0.27191 | 0.049759 | 0.05755 | 0.0036145 | 0.028047 | -0.0021768 | 0.027015 | -0.2301 | 0.013593 | 0.025346 | 0.037707 | -3.629e-05 | 0.016677 | 0.004578 | 0 | -0.027466 | -0.013733 | 0.12817 | -0.018311 | -0.16022 | 0.013733 | 0.032043 | -0.068665 | 0.091553 | 0.073242 | -0.082397 | -0.10986 | 120.0577 | 119.9158 | -2.1057 | 120.076 | 120.0623 | 0.14648 | -2.2293 | 119.9936 | 119.9661 | -2.1423 | 120.0897 | 120.0073 | 0.041198 | -2.1606 | 120.2042 | 120.0806 | 120.0485 | -2.3941 | 120.1675 | 120.1492 | 120.108 | -2.3438
6053.3906 | 122.4472 | -119.8837 | 2.3849 | 0.048523 | 0.050186 | 0.058618 | -0.00065795 | 0.024842 | -0.0023904 | 0.027442 | 0.090332 | 0.013806 | 0.02321 | 0.037707 | 0.0031681 | 0.018814 | -0.013733 | -0.027466 | -0.045776 | -0.013733 | 0.11902 | 0.018311 | -0.15106 | 0.027466 | -0.022888 | -0.10071 | 0.068665 | 0.073242 | -0.059509 | -0.10986 | 119.902 | 119.7327 | -2.2659 | 119.8563 | 119.87 | 0.13733 | -2.3987 | 119.8242 | 119.7739 | -2.3163 | 119.9112 | 119.783 | 0.009155 | -2.3117 | 120.0027 | 119.87 | 119.838 | -2.536 | 119.9524 | 119.957 | 119.8608 | -2.4948
6055.0938 | 122.4289 | -119.9387 | 2.3804 | -0.14221 | 0.049332 | 0.059473 | 0.0038281 | 0.027833 | -0.0045266 | 0.028937 | -0.19196 | 0.013379 | 0.025346 | 0.038134 | 0.0010317 | 0.017532 | -0.009155 | 0.022888 | -0.022888 | 0.009155 | 0.11444 | -0.004578 | -0.13733 | 0.022888 | 0.036621 | -0.059509 | 0.10071 | 0.086975 | -0.073242 | -0.11444 | 119.9341 | 119.8013 | -2.2659 | 119.9615 | 119.9478 | 0.14648 | -2.3895 | 119.8654 | 119.8242 | -2.2797 | 119.9615 | 119.8792 | 0.054932 | -2.2934 | 120.0531 | 119.9295 | 119.9158 | -2.5177 | 120.0394 | 120.0256 | 119.9753 | -2.4948
6056.8125 | 122.5754 | -119.6045 | 2.6276 | -0.04303 | 0.047409 | 0.060541 | 0.0066053 | 0.028047 | -0.007731 | 0.029578 | -0.016479 | 0.01167 | 0.023851 | 0.036852 | -0.0028135 | 0.0186 | 0.018311 | 0.082397 | 0.07782 | 0.036621 | 0.091553 | 0.032043 | -0.1236 | 0.10986 | 0.14191 | 0.050354 | 0.059509 | 0.013733 | -0.022888 | -0.068665 | 119.6365 | 119.4809 | -2.536 | 119.6869 | 119.6411 | 0.16022 | -2.6093 | 119.5816 | 119.5358 | -2.5681 | 119.7144 | 119.6548 | 0.11902 | -2.6138 | 119.696 | 119.6228 | 119.6823 | -2.7512 | 119.664 | 119.6182 | 119.7464 | -2.6962
6058.5781 | 122.4197 | -119.5862 | 2.7649 | -0.21088 | 0.049118 | 0.05755 | 0.0036145 | 0.03061 | -0.0070902 | 0.027442 | -0.2301 | 0.011029 | 0.022996 | 0.036852 | 0.00060451 | 0.017746 | 0.059509 | 0.1236 | 0.073242 | 0.073242 | 0.086975 | 0.022888 | -0.11902 | 0.082397 | 0.11902 | -0.013733 | 0.054932 | 0.059509 | -0.032043 | -0.09613 | 119.6091 | 119.4672 | -2.6779 | 119.7098 | 119.6594 | 0.19226 | -2.7054 | 119.5541 | 119.4901 | -2.71 | 119.6686 | 119.5724 | 0.082397 | -2.7054 | 119.6732 | 119.6457 | 119.6594 | -2.8839 | 119.6411 | 119.6457 | 119.7052 | -2.861
6060.2812 | 122.493 | -119.3069 | 2.9388 | 0.071411 | 0.044846 | 0.058405 | -0.0015125 | 0.025056 | -0.0064492 | 0.027656 | 0.075073 | 0.010816 | 0.024278 | 0.034929 | 0.0029543 | 0.0186 | 0.07782 | 0.10529 | 0.073242 | 0.050354 | 0.086975 | 0.027466 | -0.09613 | 0.13275 | 0.091553 | 0.013733 | 0.027466 | 0.036621 | -0.018311 | -0.09613 | 119.3344 | 119.2108 | -2.8519 | 119.4122 | 119.3573 | 0.14648 | -2.861 | 119.2886 | 119.2108 | -2.9114 | 119.4397 | 119.3207 | 0.10986 | -2.9022 | 119.3939 | 119.3848 | 119.3802 | -3.035 | 119.3344 | 119.3436 | 119.3985 | -3.035
6062 | 122.5067 | -119.8105 | 2.449 | 0.08667 | 0.043991 | 0.058618 | 0.00041005 | 0.025483 | -0.0068766 | 0.025947 | 0.12085 | 0.012097 | 0.022142 | 0.033434 | 0.0027407 | 0.017746 | 0.091553 | 0.10071 | 0.082397 | 0.041199 | 0.07782 | 0.045776 | -0.11902 | 0.11444 | 0.11444 | 0.018311 | 0.050354 | 0.032043 | -0.022888 | -0.073242 | 119.8563 | 119.6915 | -2.3712 | 119.9112 | 119.8517 | 0.16022 | -2.3575 | 119.7876 | 119.7372 | -2.3987 | 119.9249 | 119.8288 | 0.091553 | -2.417 | 119.8883 | 119.902 | 119.8929 | -2.5681 | 119.8608 | 119.8425 | 119.9249 | -2.5223
6063.6875 | 122.4243 | -119.6915 | 2.623 | -0.088806 | 0.052536 | 0.057123 | 0.0061781 | 0.027192 | 0.003591 | 0.027656 | -0.11566 | 0.015943 | 0.024492 | 0.037066 | 0.0040225 | 0.014114 | 0.09613 | 0.036621 | 0.022888 | 0.027466 | 0.11444 | 0.013733 | -0.13275 | 0.073242 | 0.050354 | -0.068665 | 0.082397 | 0.064087 | -0.041199 | -0.086975 | 119.7052 | 119.5587 | -2.5085 | 119.7281 | 119.7189 | 0.16022 | -2.5269 | 119.6503 | 119.6045 | -2.5406 | 119.7647 | 119.6228 | 0.01831 | -2.5589 | 119.8059 | 119.7876 | 119.7144 | -2.7557 | 119.7739 | 119.7556 | 119.7418 | -2.71
6065.3906 | 122.5204 | -119.8196 | 2.4719 | 0.079041 | 0.048477 | 0.05755 | -0.0012987 | 0.029969 | -0.0038858 | 0.030219 | 0.12085 | 0.012525 | 0.025133 | 0.036425 | 0.0025271 | 0.017746 | 0.09613 | 0.13733 | 0.10529 | 0.059509 | 0.064087 | 0.041199 | -0.10986 | 0.14648 | 0.1236 | 0.041199 | 0.045776 | 0.032043 | -0.032043 | -0.086975 | 119.8608 | 119.7098 | -2.4078 | 119.957 | 119.8792 | 0.16937 | -2.3758 | 119.7876 | 119.7327 | -2.4261 | 119.9661 | 119.8608 | 0.12817 | -2.4399 | 119.8837 | 119.9158 | 119.9249 | -2.5818 | 119.8654 | 119.8517 | 119.9432 | -2.5589
6067.0938 | 122.4472 | -119.5038 | 2.7969 | 0.018005 | 0.050186 | 0.060754 | -1.7146e-05 | 0.026124 | 0.00060022 | 0.028724 | 0.0064086 | 0.01402 | 0.023424 | 0.036852 | 0.0044497 | 0.016464 | 0.004578 | -0.036621 | -0.059509 | -0.013733 | 0.13275 | 0.009155 | -0.14648 | 0.032043 | -0.009155 | -0.10986 | 0.086975 | 0.064087 | -0.045776 | -0.10529 | 119.5129 | 119.3573 | -2.6642 | 119.4672 | 119.4901 | 0.13275 | -2.7924 | 119.458 | 119.3985 | -2.71 | 119.5358 | 119.3939 | -0.004577 | -2.7328 | 119.6365 | 119.5084 | 119.4443 | -2.9434 | 119.5908 | 119.5679 | 119.4946 | -2.9022
6068.7969 | 122.4518 | -119.8563 | 2.4399 | -0.15747 | 0.051041 | 0.059473 | 0.0031873 | 0.030183 | -0.008372 | 0.028937 | -0.1767 | 0.010388 | 0.024278 | 0.035143 | 0.00060451 | 0.017532 | 0.091553 | 0.11902 | 0.07782 | 0.082397 | 0.073242 | 0.022888 | -0.10529 | 0.09613 | 0.14191 | 0.032043 | 0.064087 | 0.045776 | -0.036621 | -0.086975 | 119.8791 | 119.751 | -2.3666 | 119.9753 | 119.9387 | 0.18768 | -2.3483 | 119.8196 | 119.7693 | -2.3758 | 119.9524 | 119.8883 | 0.11902 | -2.3941 | 119.9295 | 119.9478 | 119.9341 | -2.5452 | 119.9203 | 119.902 | 119.9982 | -2.5269
6070.5625 | 122.5113 | -119.4672 | 2.8152 | -0.18799 | 0.049759 | 0.057336 | 0.0061781 | 0.026551 | -0.0073038 | 0.02616 | -0.16144 | 0.010602 | 0.024492 | 0.034289 | -0.0028135 | 0.016891 | 0.082397 | 0.15564 | 0.13733 | 0.07782 | 0.09613 | 0.027466 | -0.10071 | 0.14191 | 0.19226 | 0.059509 | 0.036621 | 0.032043 | -0.018311 | -0.091553 | 119.4946 | 119.3665 | -2.7191 | 119.6228 | 119.545 | 0.17853 | -2.7329 | 119.4489 | 119.3756 | -2.7786 | 119.6091 | 119.5267 | 0.15106 | -2.7832 | 119.5633 | 119.5496 | 119.6045 | -2.916 | 119.5038 | 119.4992 | 119.6594 | -2.9068
6072.2656 | 122.5159 | -119.9936 | 2.2659 | 0.13245 | 0.046982 | 0.057336 | -0.0025805 | 0.027192 | -0.0038858 | 0.025519 | 0.10559 | 0.012738 | 0.021287 | 0.033007 | 0.0018863 | 0.014328 | 0.10529 | 0.14191 | 0.10986 | 0.064087 | 0.068665 | 0.036621 | -0.10529 | 0.16479 | 0.14191 | 0.041199 | 0.022888 | 0.036621 | -0.022888 | -0.068665 | 120.0302 | 119.8883 | -2.1973 | 120.1355 | 120.0577 | 0.16937 | -2.1606 | 119.9707 | 119.9249 | -2.243 | 120.1584 | 120.0348 | 0.10986 | -2.2293 | 120.0623 | 120.0989 | 120.1035 | -2.3712 | 120.0165 | 120.0302 | 120.1355 | -2.3346
6073.9688 | 122.5204 | -119.7739 | 2.5131 | 0.11719 | 0.049332 | 0.060114 | 0.00041005 | 0.02826 | 0.00038662 | 0.028724 | 0.021668 | 0.013166 | 0.022996 | 0.038988 | 0.0053043 | 0.014968 | 0.041199 | -0.018311 | -0.032043 | -0.018311 | 0.12817 | 0 | -0.15564 | 0.054932 | 0.004578 | -0.082397 | 0.068665 | 0.068665 | -0.041199 | -0.10986 | 119.7739 | 119.6182 | -2.3849 | 119.7556 | 119.7556 | 0.13733 | -2.4719 | 119.7327 | 119.664 | -2.4445 | 119.8288 | 119.6915 | 0.027466 | -2.4445 | 119.902 | 119.8151 | 119.7418 | -2.6688 | 119.8425 | 119.8425 | 119.7784 | -2.623
6075.6719 | 122.493 | -119.6045 | 2.7191 | -0.20325 | 0.052964 | 0.059473 | 0.0063917 | 0.027833 | -0.0021768 | 0.029578 | -0.19958 | 0.013379 | 0.025774 | 0.037707 | 0.00081811 | 0.01625 | 0.013733 | -0.009155 | -0.027466 | -0.009155 | 0.11902 | -0.004578 | -0.17395 | 0.032043 | 0.036621 | -0.068665 | 0.09613 | 0.064087 | -0.050354 | -0.13275 | 119.5999 | 119.4305 | -2.6001 | 119.5953 | 119.5953 | 0.16479 | -2.7054 | 119.5541 | 119.4717 | -2.623 | 119.6365 | 119.5358 | 0.064086 | -2.655 | 119.7235 | 119.6182 | 119.577 | -2.8931 | 119.7006 | 119.6686 | 119.6411 | -2.8519
6077.3906 | 122.493 | -119.4855 | 2.8152 | -0.14984 | 0.051895 | 0.055841 | 0.0036145 | 0.026124 | -0.0023904 | 0.027228 | -0.19196 | 0.017224 | 0.024492 | 0.04027 | 0.0025271 | 0.016037 | 0.054932 | 0.041199 | -0.004578 | 0.027466 | 0.11444 | 0.004578 | -0.13733 | 0.082397 | 0.086975 | -0.032043 | 0.082397 | 0.073242 | -0.054932 | -0.10071 | 119.4901 | 119.3481 | -2.7008 | 119.5267 | 119.5129 | 0.16479 | -2.7603 | 119.4305 | 119.3848 | -2.7329 | 119.5679 | 119.4534 | 0.068665 | -2.742 | 119.5999 | 119.5404 | 119.4809 | -2.9526 | 119.5679 | 119.5587 | 119.5724 | -2.916
6079.1094 | 122.4243 | -119.8425 | 2.4948 | -0.04303 | 0.051682 | 0.059259 | 0.0019055 | 0.029542 | -0.00025418 | 0.030433 | -0.039368 | 0.017224 | 0.023637 | 0.038561 | 0.0053043 | 0.017105 | 0.050354 | 0.041199 | -0.022888 | 0.009155 | 0.10986 | 0.004578 | -0.13275 | 0.045776 | 0.027466 | -0.091553 | 0.073242 | 0.068665 | -0.045776 | -0.091553 | 119.8471 | 119.7098 | -2.3849 | 119.8837 | 119.8517 | 0.14191 | -2.4445 | 119.7968 | 119.751 | -2.4216 | 119.8883 | 119.751 | 0 | -2.4261 | 119.9524 | 119.8929 | 119.8196 | -2.6276 | 119.9158 | 119.9112 | 119.87 | -2.5864
6080.8125 | 122.438 | -120.369 | 1.9958 | -0.25665 | 0.047837 | 0.060327 | 0.0076733 | 0.027619 | -0.0079446 | 0.027656 | -0.18433 | 0.012952 | 0.024919 | 0.036425 | -0.00089089 | 0.019882 | 0.027466 | 0.091553 | 0.050354 | 0.054932 | 0.10986 | 0.009155 | -0.14191 | 0.045776 | 0.07782 | -0.036621 | 0.068665 | 0.059509 | -0.050354 | -0.11902 | 120.3781 | 120.2271 | -1.886 | 120.4605 | 120.4239 | 0.19684 | -1.9684 | 120.3186 | 120.2499 | -1.9272 | 120.4147 | 120.3323 | 0.082398 | -1.9363 | 120.4788 | 120.3964 | 120.4193 | -2.1378 | 120.4376 | 120.4285 | 120.4468 | -2.1149
6082.5156 | 122.5525 | -119.751 | 2.5223 | -0.012512 | 0.044846 | 0.056696 | 0.0042555 | 0.027619 | -0.0087992 | 0.028297 | 0.067444 | 0.011243 | 0.021715 | 0.036638 | 0.0010317 | 0.020736 | 0.004578 | 0.064087 | 0.050354 | 0.045776 | 0.09613 | 0.027466 | -0.10529 | 0.073242 | 0.10071 | 0.013733 | 0.045776 | 0.050354 | -0.041199 | -0.086975 | 119.7784 | 119.6457 | -2.4261 | 119.8151 | 119.7968 | 0.15106 | -2.5177 | 119.7098 | 119.664 | -2.4765 | 119.8242 | 119.7647 | 0.10071 | -2.4719 | 119.8471 | 119.7556 | 119.8013 | -2.6276 | 119.7968 | 119.8013 | 119.8517 | -2.6093
6084.2188 | 122.4472 | -119.8563 | 2.4948 | -0.24139 | 0.049973 | 0.0599 | 0.0048963 | 0.025697 | -0.0038858 | 0.024451 | -0.077515 | 0.013806 | 0.026414 | 0.035357 | 0.0014591 | 0.016464 | 0.032043 | 0.041199 | 0.009155 | 0.027466 | 0.11444 | 0 | -0.13275 | 0.027466 | 0.050354 | -0.054932 | 0.082397 | 0.059509 | -0.07782 | -0.10071 | 119.8563 | 119.7235 | -2.3804 | 119.8975 | 119.8837 | 0.16022 | -2.4628 | 119.7784 | 119.7556 | -2.4124 | 119.8837 | 119.8013 | 0.045776 | -2.4353 | 119.9707 | 119.8883 | 119.8654 | -2.6276 | 119.9387 | 119.9158 | 119.9066 | -2.5955
6085.9375 | 122.4655 | -119.8471 | 2.4994 | -0.096436 | 0.049118 | 0.056268 | -0.0010851 | 0.025697 | 0.00017302 | 0.027228 | -0.13855 | 0.016156 | 0.023851 | 0.038347 | 0.0055179 | 0.016037 | 0.091553 | 0.073242 | 0.018311 | 0.036621 | 0.1236 | 0.004578 | -0.13275 | 0.091553 | 0.073242 | -0.059509 | 0.068665 | 0.045776 | -0.045776 | -0.091553 | 119.8517 | 119.7144 | -2.3758 | 119.9203 | 119.8837 | 0.16937 | -2.4078 | 119.8013 | 119.7556 | -2.4307 | 119.9387 | 119.7876 | 0.032044 | -2.4536 | 119.9707 | 119.9387 | 119.8654 | -2.6321 | 119.9158 | 119.8929 | 119.9203 | -2.5909
6087.6562 | 122.5662 | -119.6869 | 2.536 | 0.056152 | 0.0504 | 0.060114 | 0.00083745 | 0.027619 | -0.0028178 | 0.027656 | 0.15137 | 0.013593 | 0.019792 | 0.035357 | 0.0038089 | 0.018386 | 0.10071 | 0.10071 | 0.10071 | 0.082397 | 0.07782 | 0.054932 | -0.10529 | 0.15564 | 0.13733 | 0.050354 | 0.022888 | 0.004578 | -0.022888 | -0.050354 | 119.7418 | 119.5816 | -2.4582 | 119.7876 | 119.7693 | 0.18768 | -2.4353 | 119.664 | 119.6365 | -2.5131 | 119.8425 | 119.7372 | 0.10071 | -2.5314 | 119.7647 | 119.7876 | 119.7876 | -2.6413 | 119.7098 | 119.6915 | 119.8242 | -2.5864
6089.3594 | 122.5708 | -119.6732 | 2.5955 | -0.14221 | 0.047837 | 0.061609 | 0.0076733 | 0.025697 | -0.0073038 | 0.025306 | -0.12329 | 0.011243 | 0.025346 | 0.034929 | -0.0019589 | 0.015609 | 0.07782 | 0.16022 | 0.11444 | 0.091553 | 0.07782 | 0.027466 | -0.10529 | 0.14191 | 0.18768 | 0.07782 | 0.032043 | 0.018311 | -0.022888 | -0.07782 | 119.7006 | 119.5679 | -2.5177 | 119.8334 | 119.7647 | 0.19684 | -2.5177 | 119.6503 | 119.5953 | -2.5635 | 119.8151 | 119.751 | 0.15564 | -2.5772 | 119.751 | 119.751 | 119.7876 | -2.7008 | 119.7052 | 119.6915 | 119.8608 | -2.6733
6091.0625 | 122.5616 | -119.3985 | 2.8427 | 0.14008 | 0.047623 | 0.057336 | -0.0017261 | 0.027192 | -0.0038858 | 0.02616 | 0.159 | 0.012952 | 0.022783 | 0.034716 | 0.0033817 | 0.016891 | 0.11902 | 0.1236 | 0.091553 | 0.07782 | 0.073242 | 0.045776 | -0.086975 | 0.13733 | 0.14191 | 0.054932 | 0.027466 | 0.004578 | 0 | -0.068665 | 119.4443 | 119.3115 | -2.7695 | 119.5221 | 119.4763 | 0.16479 | -2.7237 | 119.3985 | 119.3298 | -2.8152 | 119.5358 | 119.4534 | 0.1236 | -2.8381 | 119.4717 | 119.5175 | 119.4901 | -2.9297 | 119.426 | 119.4031 | 119.5404 | -2.9114
6092.7656 | 122.5067 | -119.8013 | 2.4948 | -0.18799 | 0.046555 | 0.058832 | 0.00083745 | 0.026551 | -0.0023904 | 0.027656 | -0.23773 | 0.014661 | 0.021928 | 0.037066 | 0.0046633 | 0.015609 | 0.036621 | 0.009155 | -0.013733 | 0.013733 | 0.12817 | 0.009155 | -0.14191 | 0.054932 | 0.068665 | -0.054932 | 0.091553 | 0.068665 | -0.041199 | -0.10986 | 119.8105 | 119.6594 | -2.3666 | 119.8105 | 119.8151 | 0.15564 | -2.4582 | 119.7601 | 119.6915 | -2.4033 | 119.8563 | 119.7464 | 0.054931 | -2.4261 | 119.9295 | 119.838 | 119.7876 | -2.6367 | 119.8929 | 119.87 | 119.87 | -2.6047
6094.4844 | 122.4564 | -119.7922 | 2.5589 | -0.11169 | 0.0504 | 0.060327 | 0.0029737 | 0.029542 | -0.0011088 | 0.028724 | -0.12329 | 0.013379 | 0.025133 | 0.037066 | 0.0048769 | 0.014328 | 0.086975 | 0.064087 | 0.027466 | 0.036621 | 0.11902 | 0.018311 | -0.13275 | 0.07782 | 0.073242 | -0.054932 | 0.059509 | 0.064087 | -0.054932 | -0.11444 | 119.8105 | 119.6594 | -2.4399 | 119.8563 | 119.8288 | 0.16937 | -2.4719 | 119.7372 | 119.6777 | -2.4994 | 119.87 | 119.7372 | 0.059509 | -2.4948 | 119.9112 | 119.8791 | 119.8196 | -2.6916 | 119.8517 | 119.8563 | 119.8654 | -2.6733
6096.1875 | 121.8338 | -118.9362 | 2.1286 | -0.1651 | 0.047837 | 0.060754 | 0.0051099 | 0.02826 | -0.010722 | 0.028297 | -0.13092 | 0.011029 | 0.025133 | 0.034929 | -0.0021725 | 0.020095 | 0.09613 | 0.18768 | 0.12817 | 0.082397 | 0.086975 | 0.036621 | -0.10529 | 0.13275 | 0.1831 | 0.064087 | 0.050354 | 0.022888 | -0.013733 | -0.082397 | 118.9728 | 118.8309 | -2.0416 | 119.1238 | 119.0186 | 0.18768 | -2.0325 | 118.9224 | 118.8538 | -2.0782 | 119.0689 | 119.0002 | 0.14648 | -2.1057 | 119.0231 | 119.0323 | 119.0643 | -2.2339 | 118.9865 | 118.959 | 119.1193 | -2.211
6097.8906 | 122.0901 | -108.9157 | 12.8677 | -0.18799 | 0.050827 | 0.057764 | 0.0066053 | 0.027192 | -0.0055948 | 0.026801 | -0.19958 | 0.011029 | 0.024919 | 0.033861 | -0.0011045 | 0.017105 | 0.068665 | 0.12817 | 0.09613 | 0.082397 | 0.068665 | 0.022888 | -0.10529 | 0.091553 | 0.13733 | 0.009155 | 0.050354 | 0.045776 | -0.050354 | -0.10071 | 108.9386 | 108.8104 | -12.7991 | 109.0439 | 108.9981 | 0.18768 | -12.7991 | 108.8654 | 108.815 | -12.8174 | 109.0073 | 108.9249 | 0.10986 | -12.822 | 108.9844 | 108.9844 | 109.0118 | -12.973 | 108.9661 | 108.9615 | 109.053 | -12.9684
6099.6406 | 122.3145 | -120.4788 | 1.3779 | 0.094299 | 0.049546 | 0.056268 | 0.0025465 | 0.027406 | -0.0030314 | 0.027869 | 0.13611 | 0.012525 | 0.024278 | 0.03557 | 0.0048769 | 0.016037 | 0.11902 | 0.11444 | 0.10071 | 0.064087 | 0.07782 | 0.050354 | -0.09613 | 0.16479 | 0.12817 | 0.041199 | 0.045776 | 0.022888 | -0.018311 | -0.068665 | 120.5292 | 120.3827 | -1.3 | 120.5933 | 120.5429 | 0.16022 | -1.2589 | 120.4605 | 120.4102 | -1.3321 | 120.6436 | 120.52 | 0.10986 | -1.355 | 120.5566 | 120.5978 | 120.5795 | -1.474 | 120.5246 | 120.5017 | 120.607 | -1.4465
6101.3438 | 122.2183 | -120.5612 | 1.4374 | -0.096436 | 0.053818 | 0.059686 | 0.0036145 | 0.029115 | 0.00081382 | 0.027442 | -0.12329 | 0.016797 | 0.023637 | 0.036211 | 0.0050907 | 0.013687 | 0.086975 | 0.064087 | 0.032043 | 0.036621 | 0.10071 | 0.022888 | -0.13733 | 0.073242 | 0.073242 | -0.054932 | 0.059509 | 0.068665 | -0.050354 | -0.086975 | 120.5841 | 120.4239 | -1.3367 | 120.6253 | 120.5978 | 0.17395 | -1.3504 | 120.5109 | 120.4742 | -1.3779 | 120.6345 | 120.5063 | 0.032043 | -1.3687 | 120.6619 | 120.6482 | 120.5933 | -1.5747 | 120.6207 | 120.6299 | 120.6345 | -1.5244
6103.0625 | 122.2458 | -120.6345 | 1.442 | -0.17273 | 0.049332 | 0.058191 | 0.0051099 | 0.029542 | -0.0055948 | 0.02851 | -0.16144 | 0.013166 | 0.021928 | 0.034289 | 0.00039091 | 0.0186 | 0.082397 | 0.11902 | 0.10986 | 0.091553 | 0.068665 | 0.050354 | -0.10986 | 0.09613 | 0.14648 | 0.018311 | 0.050354 | 0.041199 | -0.036621 | -0.086975 | 120.6848 | 120.5246 | -1.3733 | 120.7535 | 120.726 | 0.20142 | -1.3596 | 120.5978 | 120.5475 | -1.3916 | 120.7306 | 120.6528 | 0.10529 | -1.4008 | 120.7031 | 120.7169 | 120.7443 | -1.5518 | 120.6848 | 120.6757 | 120.7809 | -1.5289
6104.7656 | 122.3694 | -120.6024 | 1.442 | 0.010376 | 0.0457 | 0.0599 | 0.0023329 | 0.026551 | -0.0085856 | 0.027442 | 0.052185 | 0.011884 | 0.022783 | 0.034716 | 0.0012455 | 0.017746 | 0.018311 | 0.068665 | 0.050354 | 0.032043 | 0.09613 | 0.054932 | -0.1236 | 0.086975 | 0.09613 | 0.036621 | 0.050354 | 0.036621 | -0.022888 | -0.07782 | 120.6573 | 120.4788 | -1.3458 | 120.6711 | 120.6345 | 0.15564 | -1.4236 | 120.5795 | 120.5246 | -1.3916 | 120.6894 | 120.639 | 0.11444 | -1.4053 | 120.6985 | 120.6207 | 120.6528 | -1.5656 | 120.6528 | 120.639 | 120.6985 | -1.5198
6106.5 | 122.2916 | -118.5791 | 3.5202 | -0.23376 | 0.049546 | 0.0599 | -0.00023075 | 0.027833 | -0.0028178 | 0.027442 | -0.20721 | 0.013593 | 0.022996 | 0.035998 | 0.0042361 | 0.017105 | 0.004578 | 0 | -0.018311 | 0.009155 | 0.1236 | 0.013733 | -0.13733 | 0.022888 | 0.036621 | -0.068665 | 0.086975 | 0.068665 | -0.07782 | -0.1236 | 118.5928 | 118.4418 | -3.3966 | 118.5791 | 118.5883 | 0.14648 | -3.5156 | 118.5013 | 118.4555 | -3.4332 | 118.602 | 118.5104 | 0.054931 | -3.4515 | 118.7027 | 118.5837 | 118.5608 | -3.6575 | 118.6661 | 118.6478 | 118.6157 | -3.6438
6108.2031 | 122.3602 | -94.3588 | 27.5116 | 0.0027468 | 0.046555 | 0.060541 | 0.0010511 | 0.025697 | -0.007731 | 0.026588 | 0.052185 | 0.012097 | 0.021928 | 0.033221 | 0.0012455 | 0.018173 | 0.022888 | 0.073242 | 0.050354 | 0.041199 | 0.10071 | 0.032043 | -0.11444 | 0.091553 | 0.073242 | 0.027466 | 0.045776 | 0.027466 | -0.027466 | -0.082397 | 94.3909 | 94.2444 | -27.4109 | 94.4321 | 94.4 | 0.15564 | -27.4887 | 94.3314 | 94.2764 | -27.4658 | 94.4504 | 94.3863 | 0.10986 | -27.4841 | 94.4595 | 94.3817 | 94.4092 | -27.626 | 94.4046 | 94.3863 | 94.4321 | -27.594
6109.9219 | 122.3419 | -120.6253 | 1.4923 | -0.25665 | 0.049546 | 0.059686 | 0.0051099 | 0.023988 | -0.0058084 | 0.028937 | -0.20721 | 0.013166 | 0.024278 | 0.035998 | 0.00039091 | 0.015396 | 0.073242 | 0.09613 | 0.050354 | 0.041199 | 0.10529 | 0.022888 | -0.13275 | 0.059509 | 0.082397 | -0.045776 | 0.082397 | 0.045776 | -0.045776 | -0.10529 | 120.6482 | 120.4926 | -1.387 | 120.7214 | 120.6665 | 0.17395 | -1.4191 | 120.5795 | 120.52 | -1.4099 | 120.6848 | 120.5795 | 0.05951 | -1.4465 | 120.7306 | 120.6985 | 120.6757 | -1.6251 | 120.7077 | 120.6711 | 120.7077 | -1.5976
6111.6406 | 122.3511 | -113.7634 | 8.2535 | 0.12482 | 0.050614 | 0.057764 | 0.00041005 | 0.026979 | 0.00038662 | 0.027442 | 0.059815 | 0.014447 | 0.024492 | 0.037493 | 0.0057315 | 0.015609 | 0.013733 | -0.027466 | -0.050354 | -0.013733 | 0.13733 | -0.009155 | -0.16022 | 0.032043 | -0.032043 | -0.09613 | 0.10071 | 0.064087 | -0.045776 | -0.12817 | 113.7543 | 113.6032 | -8.1162 | 113.736 | 113.7497 | 0.14648 | -8.2397 | 113.7177 | 113.6353 | -8.1528 | 113.7955 | 113.6673 | 0.032044 | -8.1894 | 113.9008 | 113.7772 | 113.7131 | -8.4137 | 113.8641 | 113.8275 | 113.7314 | -8.3817
6113.3438 | 122.3465 | -120.6207 | 1.5198 | -0.24139 | 0.051468 | 0.057764 | 0.0053235 | 0.026338 | -0.0058084 | 0.028297 | -0.26825 | 0.012738 | 0.027269 | 0.036211 | 0.0010317 | 0.019668 | 0 | -0.004578 | -0.018311 | -0.013733 | 0.11444 | -0.004578 | -0.15106 | 0.027466 | 0.027466 | -0.082397 | 0.086975 | 0.07782 | -0.073242 | -0.11902 | 120.6162 | 120.4697 | -1.4053 | 120.6162 | 120.607 | 0.13733 | -1.5198 | 120.5475 | 120.5017 | -1.4328 | 120.6482 | 120.5383 | 0.036622 | -1.442 | 120.7352 | 120.6207 | 120.6024 | -1.6708 | 120.7077 | 120.6985 | 120.6482 | -1.6388
6115.0469 | 122.438 | -120.5933 | 1.5198 | -0.13458 | 0.049759 | 0.057977 | 0.0038281 | 0.028047 | -0.0081582 | 0.02851 | -0.1004 | 0.011243 | 0.023851 | 0.036211 | -0.0036679 | 0.017532 | 0.091553 | 0.16937 | 0.11902 | 0.10071 | 0.073242 | 0.036621 | -0.11444 | 0.15564 | 0.19226 | 0.064087 | 0.027466 | 0.018311 | -0.009155 | -0.091553 | 120.6299 | 120.4788 | -1.4465 | 120.7626 | 120.694 | 0.21515 | -1.4282 | 120.5841 | 120.5017 | -1.4923 | 120.7489 | 120.6573 | 0.15564 | -1.5015 | 120.6665 | 120.6848 | 120.7123 | -1.6342 | 120.6207 | 120.6116 | 120.7855 | -1.6113
6116.75 | 122.3877 | -120.5704 | 1.5564 | 0.033264 | 0.04506 | 0.060754 | 0.0029737 | 0.028901 | -0.0062356 | 0.027015 | 0.059815 | 0.012311 | 0.022996 | 0.03557 | 0.0014591 | 0.017105 | 0.027466 | 0.07782 | 0.064087 | 0.036621 | 0.091553 | 0.027466 | -0.10986 | 0.10071 | 0.091553 | 0.009155 | 0.041199 | 0.036621 | -0.041199 | -0.082397 | 120.5978 | 120.4605 | -1.4648 | 120.6482 | 120.607 | 0.14648 | -1.5289 | 120.5292 | 120.488 | -1.5152 | 120.6711 | 120.5795 | 0.091552 | -1.5198 | 120.6619 | 120.5978 | 120.6345 | -1.6663 | 120.6116 | 120.607 | 120.6619 | -1.6388
6118.4688 | 122.406 | -120.5475 | 1.5381 | 0.071411 | 0.048477 | 0.057336 | 0.00019645 | 0.028047 | -4.058e-05 | 0.027869 | 0.036926 | 0.014234 | 0.023851 | 0.037066 | 0.0042361 | 0.01625 | 0.032043 | -0.009155 | -0.027466 | 0.004578 | 0.12817 | -0.009155 | -0.15106 | 0.07782 | 0.013733 | -0.059509 | 0.068665 | 0.068665 | -0.045776 | -0.082397 | 120.5383 | 120.3964 | -1.4099 | 120.5383 | 120.5521 | 0.15564 | -1.506 | 120.5017 | 120.4651 | -1.4694 | 120.6253 | 120.488 | 0.022888 | -1.4694 | 120.6757 | 120.5795 | 120.52 | -1.6891 | 120.6161 | 120.6161 | 120.5612 | -1.6205
6120.1719 | 122.3236 | -120.5933 | 1.5793 | -0.24139 | 0.0504 | 0.060114 | 0.0042555 | 0.027833 | -0.0045266 | 0.025947 | -0.23773 | 0.013379 | 0.02556 | 0.037279 | 0.0018863 | 0.014328 | 0.004578 | 0.009155 | -0.022888 | -0.013733 | 0.13733 | 0 | -0.12817 | 0.022888 | 0.036621 | -0.07782 | 0.10986 | 0.073242 | -0.059509 | -0.11444 | 120.5933 | 120.4651 | -1.442 | 120.6024 | 120.5795 | 0.11444 | -1.5747 | 120.5338 | 120.4788 | -1.4694 | 120.6161 | 120.5154 | 0.036621 | -1.506 | 120.7306 | 120.5978 | 120.5704 | -1.7075 | 120.7031 | 120.6665 | 120.6299 | -1.6937
6121.8906 | 122.438 | -120.5475 | 1.5656 | 0.14771 | 0.050186 | 0.059259 | 0.0012647 | 0.027406 | 0.00017302 | 0.029792 | 0.11322 | 0.013806 | 0.020647 | 0.035784 | 0.0033817 | 0.016464 | 0.050354 | 0.032043 | 0.018311 | 0.018311 | 0.11902 | 0.022888 | -0.1236 | 0.12817 | 0.091553 | 0 | 0.045776 | 0.027466 | -0.022888 | -0.064087 | 120.5704 | 120.4239 | -1.4465 | 120.5795 | 120.5658 | 0.14191 | -1.5152 | 120.5246 | 120.4834 | -1.5198 | 120.6757 | 120.5475 | 0.064087 | -1.5381 | 120.6665 | 120.5978 | 120.5658 | -1.6891 | 120.5933 | 120.575 | 120.639 | -1.6296
6123.6406 | 122.3877 | -120.2682 | 1.8951 | 0.10956 | 0.046128 | 0.0599 | -0.00087155 | 0.028688 | -0.008372 | 0.028724 | 0.14374 | 0.011029 | 0.023851 | 0.033861 | 0.0040225 | 0.020309 | 0.086975 | 0.12817 | 0.10986 | 0.059509 | 0.082397 | 0.050354 | -0.10071 | 0.14648 | 0.1236 | 0.041199 | 0.036621 | 0.018311 | -0.036621 | -0.07782 | 120.3186 | 120.1675 | -1.8127 | 120.3964 | 120.3278 | 0.16022 | -1.8082 | 120.2316 | 120.1904 | -1.8585 | 120.4147 | 120.3094 | 0.11902 | -1.8768 | 120.3506 | 120.3552 | 120.3781 | -1.9959 | 120.3049 | 120.2866 | 120.3918 | -1.973
6125.3281 | 122.3053 | -120.2911 | 1.9226 | -0.058289 | 0.051041 | 0.058405 | 0.0023329 | 0.028688 | 0.0016684 | 0.026801 | -0.062256 | 0.012952 | 0.022783 | 0.037279 | 0.0053043 | 0.016037 | 0.068665 | 0.027466 | 0.004578 | 0.018311 | 0.1236 | 0.009155 | -0.14648 | 0.050354 | 0.027466 | -0.091553 | 0.086975 | 0.073242 | -0.032043 | -0.09613 | 120.3003 | 120.1447 | -1.799 | 120.3186 | 120.3094 | 0.16479 | -1.8539 | 120.2591 | 120.195 | -1.8356 | 120.3415 | 120.1996 | 0.004577 | -1.8494 | 120.4147 | 120.3598 | 120.2957 | -2.0691 | 120.3781 | 120.3644 | 120.3186 | -2.0187
6127.0312 | 122.4197 | -120.2728 | 1.8768 | -0.14984 | 0.048477 | 0.061182 | 0.0074597 | 0.029542 | -0.0085856 | 0.026801 | -0.1004 | 0.013593 | 0.025987 | 0.035784 | -0.00024989 | 0.017746 | 0.091553 | 0.15106 | 0.1236 | 0.086975 | 0.082397 | 0.041199 | -0.11902 | 0.14648 | 0.18768 | 0.059509 | 0.027466 | 0.027466 | -0.027466 | -0.068665 | 120.314 | 120.1538 | -1.7944 | 120.4239 | 120.3598 | 0.20599 | -1.7853 | 120.2454 | 120.2042 | -1.8494 | 120.4193 | 120.3323 | 0.12817 | -1.8494 | 120.3552 | 120.3644 | 120.3964 | -1.9958 | 120.3003 | 120.3003 | 120.4605 | -1.9455
6128.75 | 122.3053 | -120.3003 | 1.9089 | 0.018005 | 0.050614 | 0.057336 | 0.0016919 | 0.029756 | 0.0040182 | 0.027869 | -0.031738 | 0.015302 | 0.023851 | 0.038988 | 0.0053043 | 0.014755 | 0.041199 | -0.018311 | -0.041199 | -0.009155 | 0.1236 | 0.022888 | -0.14191 | 0.027466 | 0.004578 | -0.11444 | 0.07782 | 0.086975 | -0.059509 | -0.10986 | 120.3232 | 120.1584 | -1.7853 | 120.282 | 120.2911 | 0.13275 | -1.8677 | 120.2408 | 120.1904 | -1.8311 | 120.3278 | 120.1859 | -0.004578 | -1.8219 | 120.4239 | 120.3415 | 120.2591 | -2.0508 | 120.3781 | 120.3873 | 120.3049 | -2.0187
6130.4531 | 122.4609 | -120.4559 | 1.6891 | -0.13458 | 0.047623 | 0.061182 | 0.0061781 | 0.023347 | -0.007731 | 0.027869 | -0.062256 | 0.010388 | 0.023851 | 0.036211 | -0.0036679 | 0.017959 | 0.091553 | 0.14191 | 0.12817 | 0.073242 | 0.09613 | 0.032043 | -0.11902 | 0.15564 | 0.17395 | 0.086975 | 0.050354 | 0.036621 | -0.013733 | -0.064087 | 120.488 | 120.3369 | -1.593 | 120.5978 | 120.5292 | 0.19226 | -1.5976 | 120.4422 | 120.3918 | -1.6388 | 120.6116 | 120.5429 | 0.15106 | -1.6525 | 120.5521 | 120.5475 | 120.5841 | -1.8082 | 120.5063 | 120.4926 | 120.6299 | -1.7532
6132.1562 | 122.2824 | -120.4147 | 1.7807 | 0.040894 | 0.049332 | 0.057123 | 0.0016919 | 0.02591 | 0.0029502 | 0.028937 | -0.031738 | 0.01637 | 0.022996 | 0.037707 | 0.0057315 | 0.016891 | 0.018311 | -0.036621 | -0.041199 | 0.009155 | 0.11902 | 0.013733 | -0.16022 | 0.022888 | -0.009155 | -0.13733 | 0.086975 | 0.050354 | -0.064087 | -0.11902 | 120.4285 | 120.2545 | -1.6617 | 120.3781 | 120.4239 | 0.16937 | -1.7624 | 120.3506 | 120.2957 | -1.6937 | 120.4376 | 120.2774 | -0.01831 | -1.7303 | 120.5338 | 120.433 | 120.3735 | -1.9409 | 120.5017 | 120.4651 | 120.4056 | -1.8997
6133.8906 | 122.3236 | -120.282 | 1.9363 | 0.025635 | 0.049332 | 0.058191 | -0.00044435 | 0.026765 | 0.00038662 | 0.027869 | 0.036926 | 0.016156 | 0.022996 | 0.037707 | 0.0044497 | 0.015396 | 0.018311 | -0.045776 | -0.050354 | -0.013733 | 0.11444 | 0.027466 | -0.14648 | 0.022888 | 0 | -0.086975 | 0.07782 | 0.059509 | -0.050354 | -0.091553 | 120.3094 | 120.1355 | -1.8219 | 120.2362 | 120.2682 | 0.13275 | -1.918 | 120.2316 | 120.1904 | -1.8585 | 120.3049 | 120.195 | 0.004578 | -1.8768 | 120.3964 | 120.3003 | 120.2316 | -2.0828 | 120.3598 | 120.3415 | 120.282 | -2.0279
6135.6406 | 122.3785 | -120.4971 | 1.6937 | -0.24902 | 0.047623 | 0.060754 | 0.0012647 | 0.026979 | -0.0028178 | 0.02851 | -0.19196 | 0.014234 | 0.024278 | 0.037493 | 0.0016727 | 0.016891 | -0.009155 | -0.009155 | -0.036621 | 0.018311 | 0.13275 | 0.009155 | -0.15564 | 0.027466 | 0.041199 | -0.068665 | 0.091553 | 0.073242 | -0.068665 | -0.1236 | 120.5063 | 120.3415 | -1.561 | 120.488 | 120.5154 | 0.17395 | -1.7029 | 120.4285 | 120.3735 | -1.6022 | 120.5246 | 120.4285 | 0.054931 | -1.6205 | 120.6299 | 120.488 | 120.4605 | -1.8494 | 120.5887 | 120.5704 | 120.5383 | -1.8173
6137.3906 | 122.3785 | -120.5017 | 1.7029 | -0.27191 | 0.049332 | 0.060754 | 0.0057507 | 0.027192 | -0.006663 | 0.027015 | -0.21484 | 0.013379 | 0.025774 | 0.037066 | 0.0016727 | 0.018173 | -0.022888 | 0.004578 | -0.018311 | -0.004578 | 0.14191 | -0.004578 | -0.15564 | 0.013733 | 0.045776 | -0.068665 | 0.09613 | 0.059509 | -0.064087 | -0.10986 | 120.4971 | 120.3461 | -1.561 | 120.5063 | 120.4971 | 0.15106 | -1.7258 | 120.4376 | 120.3918 | -1.6068 | 120.5154 | 120.433 | 0.041198 | -1.6434 | 120.6436 | 120.4788 | 120.4834 | -1.8585 | 120.5978 | 120.5612 | 120.5475 | -1.8127
6139.0938 | 122.3877 | -98.2086 | 23.9227 | 0.018005 | 0.046128 | 0.061609 | 0.0023329 | 0.026551 | -0.00944 | 0.02616 | -0.0088499 | 0.0086794 | 0.025346 | 0.034075 | 0.00039091 | 0.018173 | -0.004578 | 0.068665 | 0.059509 | 0.041199 | 0.10071 | 0.045776 | -0.09613 | 0.082397 | 0.10986 | 0.036621 | 0.036621 | 0.022888 | -0.032043 | -0.091553 | 98.2544 | 98.1125 | -23.822 | 98.2773 | 98.2498 | 0.13733 | -23.9273 | 98.1766 | 98.1171 | -23.8861 | 98.291 | 98.2452 | 0.12817 | -23.8998 | 98.3093 | 98.204 | 98.2681 | -24.0189 | 98.2452 | 98.2315 | 98.3185 | -24.0143
6140.7969 | 122.3877 | -120.5704 | 1.6022 | 0.071411 | 0.0504 | 0.057123 | -0.0010851 | 0.026765 | 0.00017302 | 0.027442 | -0.016479 | 0.014875 | 0.025133 | 0.037066 | 0.0053043 | 0.016037 | 0 | -0.027466 | -0.036621 | 0 | 0.11902 | 0.009155 | -0.15106 | 0.013733 | 0 | -0.11902 | 0.091553 | 0.059509 | -0.050354 | -0.10071 | 120.5795 | 120.4193 | -1.4832 | 120.5429 | 120.5704 | 0.15106 | -1.6022 | 120.52 | 120.4697 | -1.5106 | 120.5841 | 120.4514 | -0.018311 | -1.5427 | 120.6894 | 120.5704 | 120.5338 | -1.7532 | 120.6619 | 120.6299 | 120.5704 | -1.7029
6142.5625 | 122.5113 | -120.5658 | 1.5701 | 0.056152 | 0.051041 | 0.060968 | 0.00062385 | 0.027833 | -0.001536 | 0.02851 | 0.12085 | 0.014661 | 0.02321 | 0.036852 | 0.0035953 | 0.0186 | 0.036621 | -0.004578 | -0.022888 | -0.027466 | 0.11902 | -0.009155 | -0.15564 | 0.068665 | 0.027466 | -0.045776 | 0.068665 | 0.059509 | -0.050354 | -0.09613 | 120.5566 | 120.4102 | -1.4511 | 120.5612 | 120.5383 | 0.12817 | -1.5335 | 120.5154 | 120.4697 | -1.5015 | 120.6345 | 120.52 | 0.050354 | -1.5106 | 120.6848 | 120.6024 | 120.5429 | -1.7258 | 120.6345 | 120.6253 | 120.5933 | -1.6663
6144.2656 | 122.4335 | -120.6162 | 1.5884 | -0.19562 | 0.054459 | 0.058405 | 0.0046827 | 0.028474 | -0.0045266 | 0.02616 | -0.20721 | 0.014234 | 0.024492 | 0.038775 | -0.0017453 | 0.017105 | 0.004578 | 0.009155 | -0.004578 | 0.018311 | 0.10529 | 0.004578 | -0.14648 | 0.027466 | 0.064087 | -0.059509 | 0.086975 | 0.068665 | -0.045776 | -0.10071 | 120.6207 | 120.4697 | -1.4832 | 120.6253 | 120.6345 | 0.16479 | -1.5839 | 120.5704 | 120.5154 | -1.5015 | 120.6436 | 120.5566 | 0.041199 | -1.5198 | 120.7214 | 120.6207 | 120.6116 | -1.7349 | 120.7031 | 120.6848 | 120.6802 | -1.6891
6145.9844 | 122.4747 | -120.6024 | 1.5656 | 0.15533 | 0.047196 | 0.056696 | -0.0019397 | 0.026551 | -0.004954 | 0.028083 | 0.2124 | 0.012097 | 0.021928 | 0.035998 | 0.0040225 | 0.0186 | 0.10529 | 0.12817 | 0.09613 | 0.07782 | 0.091553 | 0.054932 | -0.091553 | 0.14648 | 0.13275 | 0.050354 | 0.036621 | 0.036621 | -0.027466 | -0.054932 | 120.6573 | 120.5109 | -1.474 | 120.7306 | 120.6802 | 0.16937 | -1.4603 | 120.575 | 120.5475 | -1.5289 | 120.7489 | 120.6528 | 0.10529 | -1.5289 | 120.694 | 120.7077 | 120.6985 | -1.6571 | 120.639 | 120.639 | 120.7352 | -1.6205
6147.6875 | 121.7834 | -107.7026 | 13.9664 | -0.050659 | 0.052109 | 0.057336 | 0.0057507 | 0.026765 | -0.0021768 | 0.029151 | 0.029297 | 0.014661 | 0.025987 | 0.039629 | 0.0010317 | 0.017532 | 0.036621 | 0.013733 | -0.013733 | 0.018311 | 0.1236 | 0.013733 | -0.13275 | 0.036621 | 0.013733 | -0.082397 | 0.07782 | 0.07782 | -0.059509 | -0.11444 | 107.7164 | 107.5699 | -13.8428 | 107.7164 | 107.7209 | 0.15106 | -13.9297 | 107.6431 | 107.5882 | -13.8885 | 107.7393 | 107.6202 | 0.032044 | -13.8885 | 107.8262 | 107.7393 | 107.6889 | -14.0991 | 107.7805 | 107.7805 | 107.7164 | -14.0808
6149.375 | 122.0261 | -65.5151 | 56.1584 | -0.21088 | 0.048264 | 0.0599 | 0.0051099 | 0.028688 | -0.010081 | 0.025947 | -0.14618 | 0.010602 | 0.023637 | 0.036211 | 0.00039091 | 0.018173 | 0.073242 | 0.14648 | 0.12817 | 0.073242 | 0.07782 | 0.018311 | -0.11444 | 0.11902 | 0.17395 | 0.032043 | 0.036621 | 0.022888 | -0.027466 | -0.054932 | 65.5334 | 65.4007 | -56.0806 | 65.6616 | 65.5884 | 0.18768 | -56.0852 | 65.4877 | 65.4602 | -56.1218 | 65.6342 | 65.5472 | 0.086975 | -56.1356 | 65.593 | 65.5884 | 65.6433 | -56.2729 | 65.5518 | 65.538 | 65.6891 | -56.2134
6151.0938 | 121.7606 | -12.0712 | 109.8953 | 0.018005 | 0.049118 | 0.057977 | 0.00041005 | 0.026338 | -0.0013224 | 0.027442 | 0.052185 | 0.015729 | 0.02086 | 0.036425 | 0.0063723 | 0.016037 | -0.013733 | -0.041199 | -0.045776 | -0.009155 | 0.11902 | 0.009155 | -0.14191 | 0.032043 | -0.009155 | -0.091553 | 0.091553 | 0.068665 | -0.059509 | -0.11902 | 12.0804 | 11.9293 | -109.7763 | 12.03 | 12.0621 | 0.13275 | -109.9091 | 12.0117 | 11.9522 | -109.8038 | 12.1033 | 11.9797 | 0.027466 | -109.8267 | 12.1902 | 12.0575 | 12.0255 | -110.0372 | 12.1628 | 12.1399 | 12.0621 | -110.0143
6152.8125 | 122.1039 | -10.112 | 111.113 | -0.11169 | 0.0457 | 0.059473 | 0.0012647 | 0.023347 | -0.0098672 | 0.025306 | -0.069885 | 0.0099612 | 0.022142 | 0.036425 | -0.00046349 | 0.017959 | 0.050354 | 0.13275 | 0.086975 | 0.07782 | 0.091553 | 0.032043 | -0.10986 | 0.14191 | 0.16022 | 0.068665 | 0.041199 | 0.027466 | -0.018311 | -0.073242 | 10.144 | 10.0021 | -111.0214 | 10.2448 | 10.1898 | 0.18768 | -111.0626 | 10.0937 | 10.0388 | -111.0718 | 10.2539 | 10.1807 | 0.14191 | -111.0855 | 10.2036 | 10.1624 | 10.199 | -111.2228 | 10.1532 | 10.1395 | 10.2722 | -111.1862
6154.5 | 108.0002 | -12.1902 | 95.6268 | 0.10956 | 0.049973 | 0.059259 | 0.00083745 | 0.026765 | -0.0011088 | 0.028297 | 0.052185 | 0.014234 | 0.023851 | 0.034929 | 0.0059451 | 0.017959 | 0.022888 | -0.036621 | -0.045776 | -0.013733 | 0.11444 | 0.004578 | -0.13733 | 0.032043 | -0.009155 | -0.086975 | 0.082397 | 0.059509 | -0.064087 | -0.10071 | 12.1948 | 12.0529 | -95.5124 | 12.1536 | 12.1765 | 0.1236 | -95.6039 | 12.1262 | 12.0895 | -95.5444 | 12.2223 | 12.1033 | 0.013733 | -95.5673 | 12.3047 | 12.2131 | 12.1445 | -95.7642 | 12.2726 | 12.2498 | 12.1811 | -95.7275
6156.2031 | 91.2827 | -13.2202 | 80.8228 | -0.21851 | 0.047837 | 0.062036 | 0.0019055 | 0.026124 | -0.0070902 | 0.023597 | -0.20721 | 0.011243 | 0.02086 | 0.036211 | 0.0027407 | 0.018386 | -0.004578 | 0.013733 | 0 | -0.009155 | 0.10529 | 0.004578 | -0.14191 | 0.022888 | 0.036621 | -0.073242 | 0.082397 | 0.059509 | -0.068665 | -0.1236 | 13.2248 | 13.0783 | -80.7175 | 13.2339 | 13.2111 | 0.13275 | -80.8273 | 13.1516 | 13.0966 | -80.7404 | 13.2431 | 13.147 | 0.050354 | -80.7632 | 13.3255 | 13.2156 | 13.2202 | -80.9647 | 13.3026 | 13.2797 | 13.2568 | -80.9464
6157.9062 | 121.7468 | -12.1857 | 109.584 | 0.048523 | 0.045914 | 0.058405 | 0.0027601 | 0.024629 | -0.0051676 | 0.027015 | 0.12848 | 0.013593 | 0.02086 | 0.034502 | 0.0029543 | 0.017105 | 0.10071 | 0.11902 | 0.10529 | 0.064087 | 0.064087 | 0.032043 | -0.10986 | 0.15106 | 0.1236 | 0.041199 | 0.054932 | 0.032043 | -0.041199 | -0.082397 | 12.2177 | 12.0758 | -109.52 | 12.3047 | 12.2498 | 0.17395 | -109.4833 | 12.1445 | 12.1033 | -109.5291 | 12.3367 | 12.2269 | 0.1236 | -109.552 | 12.2498 | 12.2864 | 12.291 | -109.6939 | 12.2406 | 12.2177 | 12.3093 | -109.6664
6159.6094 | 122.3373 | -107.1671 | 14.653 | -0.18799 | 0.04805 | 0.059045 | 0.0076733 | 0.028474 | -0.0053812 | 0.025733 | -0.13092 | 0.011884 | 0.024919 | 0.034929 | -0.00067729 | 0.015609 | 0.10986 | 0.13275 | 0.12817 | 0.086975 | 0.086975 | 0.022888 | -0.10986 | 0.13733 | 0.17395 | 0.050354 | 0.050354 | 0.027466 | -0.036621 | -0.073242 | 107.1899 | 107.0572 | -14.566 | 107.2998 | 107.254 | 0.19684 | -14.5432 | 107.1304 | 107.0938 | -14.6027 | 107.3044 | 107.2174 | 0.1236 | -14.6255 | 107.254 | 107.2769 | 107.2952 | -14.7629 | 107.2174 | 107.1945 | 107.341 | -14.7263
6161.3281 | 122.3373 | -113.0447 | 8.8852 | -0.17273 | 0.05275 | 0.057336 | 0.0042555 | 0.029756 | -0.0011088 | 0.029578 | -0.1767 | 0.013806 | 0.026628 | 0.03792 | 0.0033817 | 0.014328 | 0.068665 | 0.018311 | 0.004578 | 0.041199 | 0.12817 | 0.004578 | -0.14191 | 0.07782 | 0.068665 | -0.045776 | 0.091553 | 0.059509 | -0.054932 | -0.10529 | 113.0493 | 112.9028 | -8.757 | 113.0631 | 113.0859 | 0.18311 | -8.8165 | 112.9898 | 112.9395 | -8.7936 | 113.1226 | 112.999 | 0.05951 | -8.8257 | 113.1729 | 113.1134 | 113.0493 | -9.0271 | 113.1363 | 113.1042 | 113.1134 | -8.9905
6163.0312 | 122.3557 | -105.954 | 15.889 | -0.081177 | 0.046768 | 0.059045 | 0.0051099 | 0.027406 | -0.0081582 | 0.025519 | -0.054626 | 0.011029 | 0.020433 | 0.034929 | -0.00046349 | 0.017532 | 0.059509 | 0.10071 | 0.11444 | 0.064087 | 0.10071 | 0.027466 | -0.10986 | 0.14191 | 0.15106 | 0.064087 | 0.027466 | 0.032043 | -0.022888 | -0.064087 | 105.9814 | 105.8441 | -15.7883 | 106.0547 | 106.0181 | 0.17395 | -15.8295 | 105.9311 | 105.8899 | -15.8615 | 106.0959 | 106.0181 | 0.12817 | -15.8569 | 106.0547 | 106.0135 | 106.0684 | -15.9988 | 105.9814 | 105.986 | 106.105 | -15.9531
6164.7656 | 122.2824 | -121.0556 | 0.94757 | 0.040894 | 0.051468 | 0.059259 | -0.0012987 | 0.026765 | 0.0010276 | 0.029578 | 0.029297 | 0.015088 | 0.023851 | 0.034075 | 0.0072269 | 0.016037 | 0.027466 | -0.032043 | -0.041199 | 0 | 0.11444 | 0.013733 | -0.15564 | 0.036621 | -0.018311 | -0.10071 | 0.064087 | 0.068665 | -0.054932 | -0.12817 | 121.0693 | 120.9 | -0.83313 | 121.0236 | 121.0556 | 0.15564 | -0.92011 | 121.0007 | 120.9274 | -0.88348 | 121.0922 | 120.9549 | 0.027466 | -0.87891 | 121.17 | 121.0831 | 121.0144 | -1.1032 | 121.1197 | 121.1243 | 121.0373 | -1.0757
6166.5312 | 122.2504 | -115.8966 | 6.0974 | 0.040894 | 0.046768 | 0.057977 | 0.0034009 | 0.026765 | -0.0058084 | 0.027869 | 0.159 | 0.012311 | 0.022356 | 0.037707 | 0.00017731 | 0.018814 | 0.091553 | 0.13275 | 0.10529 | 0.059509 | 0.064087 | 0.036621 | -0.10986 | 0.15106 | 0.11902 | 0.027466 | 0.032043 | 0.027466 | -0.045776 | -0.082397 | 115.9332 | 115.7867 | -6.0333 | 116.0294 | 115.9561 | 0.16937 | -6.0059 | 115.8508 | 115.8142 | -6.0654 | 116.0477 | 115.9241 | 0.10986 | -6.0699 | 115.9607 | 115.9882 | 116.0019 | -6.2073 | 115.9286 | 115.9241 | 116.0156 | -6.1798
6168.2344 | 122.1954 | -112.4634 | 9.4894 | -0.18036 | 0.049546 | 0.055841 | 0.0027601 | 0.030183 | -0.00068138 | 0.028083 | -0.19196 | 0.014875 | 0.027269 | 0.035143 | 0.0040225 | 0.015609 | 0.050354 | 0.018311 | -0.013733 | 0.027466 | 0.10529 | -0.004578 | -0.13275 | 0.059509 | 0.068665 | -0.054932 | 0.073242 | 0.054932 | -0.068665 | -0.10986 | 112.4588 | 112.3306 | -9.3842 | 112.4817 | 112.4908 | 0.16022 | -9.4391 | 112.3947 | 112.3535 | -9.4162 | 112.5229 | 112.4084 | 0.054931 | -9.4345 | 112.5687 | 112.5137 | 112.4496 | -9.6222 | 112.5366 | 112.5183 | 112.532 | -9.5993
6169.9375 | 122.3419 | -121.1243 | 0.88348 | -0.13458 | 0.044632 | 0.062036 | 0.0044691 | 0.026551 | -0.0090128 | 0.025947 | -0.085144 | 0.011457 | 0.024278 | 0.035143 | -0.00067729 | 0.017532 | 0.10071 | 0.16937 | 0.13275 | 0.091553 | 0.07782 | 0.032043 | -0.10529 | 0.15106 | 0.17853 | 0.064087 | 0.036621 | 0.009155 | -0.032043 | -0.073242 | 121.1563 | 121.019 | -0.80566 | 121.2936 | 121.2158 | 0.19684 | -0.78278 | 121.0922 | 121.051 | -0.84686 | 121.2753 | 121.1884 | 0.13733 | -0.87433 | 121.2021 | 121.225 | 121.257 | -0.98877 | 121.1609 | 121.1334 | 121.3028 | -0.95673
6171.6562 | 122.2183 | -121.1838 | 0.90637 | -0.25665 | 0.049973 | 0.058405 | 0.0083143 | 0.028047 | -0.003245 | 0.027228 | -0.22247 | 0.011457 | 0.025346 | 0.037493 | 0.00039091 | 0.017746 | 0.045776 | 0.082397 | 0.050354 | 0.050354 | 0.09613 | -0.018311 | -0.14648 | 0.041199 | 0.07782 | -0.054932 | 0.073242 | 0.064087 | -0.027466 | -0.11444 | 121.1655 | 121.0373 | -0.81024 | 121.2662 | 121.2341 | 0.19684 | -0.8606 | 121.1563 | 121.0693 | -0.83313 | 121.225 | 121.1288 | 0.059509 | -0.84228 | 121.2799 | 121.2296 | 121.2341 | -1.0529 | 121.257 | 121.2479 | 121.2616 | -1.0208
6173.3438 | 122.3236 | -121.1792 | 0.85602 | 0.14771 | 0.046128 | 0.058191 | -0.0025805 | 0.026551 | -0.004954 | 0.029365 | 0.15137 | 0.010816 | 0.023424 | 0.034502 | 0.0061587 | 0.017105 | 0.09613 | 0.13275 | 0.10529 | 0.073242 | 0.073242 | 0.032043 | -0.086975 | 0.15564 | 0.14191 | 0.041199 | 0.032043 | 0.027466 | -0.032043 | -0.068665 | 121.2112 | 121.0922 | -0.78278 | 121.3119 | 121.2524 | 0.16022 | -0.75989 | 121.1472 | 121.1105 | -0.82397 | 121.3348 | 121.2204 | 0.10986 | -0.82855 | 121.2524 | 121.2753 | 121.2845 | -0.94299 | 121.2112 | 121.2067 | 121.3211 | -0.92468
6175.0625 | 122.3236 | -121.1929 | 0.8606 | 0.14771 | 0.04805 | 0.0599 | -0.0010851 | 0.027406 | -0.004313 | 0.028297 | 0.13611 | 0.013593 | 0.024065 | 0.034716 | 0.0020999 | 0.016677 | 0.10071 | 0.14191 | 0.10986 | 0.064087 | 0.07782 | 0.050354 | -0.12817 | 0.15564 | 0.13275 | 0.036621 | 0.032043 | 0.032043 | -0.036621 | -0.064087 | 121.2433 | 121.0648 | -0.78278 | 121.3348 | 121.257 | 0.19226 | -0.75989 | 121.1563 | 121.1288 | -0.82855 | 121.3486 | 121.2296 | 0.10071 | -0.82855 | 121.2708 | 121.2936 | 121.3028 | -0.98877 | 121.225 | 121.225 | 121.3257 | -0.92468
6176.7656 | 122.3053 | -121.1884 | 0.86975 | 0.094299 | 0.049546 | 0.057336 | 0.0012647 | 0.02591 | -0.0013224 | 0.028724 | 0.052185 | 0.015088 | 0.024278 | 0.038347 | 0.0029543 | 0.013687 | 0.018311 | -0.022888 | -0.041199 | -0.018311 | 0.1236 | 0 | -0.15564 | 0.054932 | -0.009155 | -0.082397 | 0.086975 | 0.073242 | -0.041199 | -0.11444 | 121.1884 | 121.0327 | -0.74616 | 121.1655 | 121.17 | 0.13733 | -0.85144 | 121.1472 | 121.0739 | -0.78278 | 121.2433 | 121.106 | 0.032044 | -0.79651 | 121.312 | 121.2067 | 121.1472 | -1.0254 | 121.2753 | 121.2616 | 121.1792 | -0.98419
6178.4688 | 122.2549 | -121.1975 | 0.91095 | -0.22614 | 0.047623 | 0.060541 | 0.0055371 | 0.028901 | -0.004313 | 0.027228 | -0.16144 | 0.014447 | 0.023637 | 0.035357 | -3.629e-05 | 0.017746 | 0.027466 | 0.041199 | 0.004578 | 0.009155 | 0.11444 | -0.004578 | -0.16022 | 0.027466 | 0.045776 | -0.064087 | 0.086975 | 0.07782 | -0.073242 | -0.10986 | 121.1929 | 121.0373 | -0.79651 | 121.2387 | 121.2067 | 0.16937 | -0.88348 | 121.1243 | 121.0876 | -0.82398 | 121.225 | 121.1334 | 0.045776 | -0.83313 | 121.312 | 121.225 | 121.2021 | -1.0712 | 121.2845 | 121.2753 | 121.2433 | -1.0208
6180.1719 | 122.3602 | -121.1975 | 0.89264 | -0.012512 | 0.0457 | 0.058618 | 0.0014783 | 0.023988 | -0.0090128 | 0.027869 | 0.082703 | 0.012525 | 0.023851 | 0.035143 | 0.0014591 | 0.018173 | 0.041199 | 0.068665 | 0.059509 | 0.041199 | 0.09613 | 0.036621 | -0.11902 | 0.07782 | 0.086975 | 0.018311 | 0.054932 | 0.032043 | -0.032043 | -0.086975 | 121.2341 | 121.0785 | -0.79651 | 121.2662 | 121.2387 | 0.16022 | -0.85144 | 121.1655 | 121.1105 | -0.83771 | 121.2753 | 121.2158 | 0.10529 | -0.8606 | 121.2936 | 121.2387 | 121.257 | -1.0117 | 121.2524 | 121.2296 | 121.2845 | -0.97961
6181.8906 | 122.3785 | -121.1746 | 0.86975 | -0.0048827 | 0.047837 | 0.060541 | 0.0023329 | 0.026124 | -0.006022 | 0.02616 | 0.029297 | 0.011884 | 0.022996 | 0.034929 | -0.00089089 | 0.019027 | 0.036621 | 0.059509 | 0.059509 | 0.050354 | 0.10529 | 0.027466 | -0.10986 | 0.10071 | 0.10071 | 0.018311 | 0.059509 | 0.041199 | -0.018311 | -0.07782 | 121.2021 | 121.0648 | -0.76447 | 121.2341 | 121.225 | 0.16022 | -0.83313 | 121.1563 | 121.0968 | -0.81024 | 121.2753 | 121.1929 | 0.096131 | -0.82855 | 121.2799 | 121.2112 | 121.2341 | -0.97961 | 121.2341 | 121.2158 | 121.2753 | -0.94757
6183.6406 | 122.3328 | -121.2067 | 0.86975 | 0.10193 | 0.052109 | 0.058191 | 0.00062385 | 0.028901 | 0.00060022 | 0.026588 | 0.014038 | 0.016797 | 0.02086 | 0.03557 | 0.0065859 | 0.016037 | 0.036621 | -0.022888 | -0.050354 | -0.009155 | 0.12817 | 0.004578 | -0.13275 | 0.054932 | 0 | -0.09613 | 0.091553 | 0.064087 | -0.059509 | -0.10986 | 121.2112 | 121.0739 | -0.74158 | 121.1838 | 121.1975 | 0.1236 | -0.83313 | 121.1472 | 121.0968 | -0.7782 | 121.2616 | 121.1105 | 0.013733 | -0.80566 | 121.3348 | 121.2433 | 121.1563 | -1.0025 | 121.2982 | 121.2708 | 121.2067 | -0.97961
6185.3906 | 122.2961 | -121.2479 | 0.87891 | -0.14221 | 0.048264 | 0.058191 | 0.0038281 | 0.02826 | 0.0016684 | 0.02616 | -0.16144 | 0.014447 | 0.026842 | 0.036638 | 0.0031681 | 0.013473 | 0.07782 | 0.050354 | 0.018311 | 0.036621 | 0.11444 | 0.018311 | -0.15106 | 0.091553 | 0.086975 | -0.041199 | 0.068665 | 0.054932 | -0.036621 | -0.09613 | 121.2662 | 121.0968 | -0.76446 | 121.2982 | 121.2845 | 0.18768 | -0.80109 | 121.2112 | 121.1517 | -0.81024 | 121.3394 | 121.2067 | 0.054931 | -0.82397 | 121.3623 | 121.3257 | 121.2662 | -1.03 | 121.3165 | 121.3028 | 121.3348 | -0.97504
6187.0938 | 122.3785 | -121.225 | 0.86975 | -0.14221 | 0.047837 | 0.059259 | 0.0076733 | 0.026338 | -0.008372 | 0.026801 | -0.077515 | 0.010388 | 0.023424 | 0.036425 | -3.629e-05 | 0.019241 | 0.10529 | 0.15564 | 0.14191 | 0.082397 | 0.10529 | 0.041199 | -0.10071 | 0.15564 | 0.18768 | 0.086975 | 0.045776 | 0.018311 | -0.032043 | -0.073242 | 121.2662 | 121.1243 | -0.76447 | 121.3806 | 121.3074 | 0.18311 | -0.76447 | 121.1929 | 121.1517 | -0.82398 | 121.3806 | 121.312 | 0.16022 | -0.85144 | 121.3303 | 121.3303 | 121.3669 | -0.97046 | 121.2708 | 121.2433 | 121.4127 | -0.94299
6188.7969 | 122.3785 | -121.225 | 0.86517 | 0.094299 | 0.050827 | 0.057764 | 0.00083745 | 0.025483 | -0.00046778 | 0.028297 | 0.097962 | 0.012952 | 0.022356 | 0.03557 | 0.0059451 | 0.016891 | 0.041199 | 0 | -0.009155 | -0.004578 | 0.11444 | 0.018311 | -0.13733 | 0.082397 | 0.064087 | -0.027466 | 0.082397 | 0.050354 | -0.018311 | -0.086975 | 121.2433 | 121.0876 | -0.75073 | 121.225 | 121.2204 | 0.13275 | -0.82397 | 121.2067 | 121.138 | -0.78278 | 121.3074 | 121.1975 | 0.059509 | -0.81482 | 121.3394 | 121.2662 | 121.2158 | -1.0025 | 121.3074 | 121.2753 | 121.2891 | -0.95215
6190.5625 | 122.3419 | -121.2341 | 0.87891 | 0.063782 | 0.047196 | 0.060114 | 0.0031873 | 0.027192 | -0.0062356 | 0.028937 | 0.14374 | 0.011884 | 0.023851 | 0.035143 | -0.0011045 | 0.019668 | 0.091553 | 0.11902 | 0.10071 | 0.059509 | 0.086975 | 0.045776 | -0.10529 | 0.12817 | 0.10529 | 0.032043 | 0.045776 | 0.022888 | -0.022888 | -0.086975 | 121.2799 | 121.1288 | -0.79193 | 121.3531 | 121.2936 | 0.16479 | -0.78735 | 121.2112 | 121.1472 | -0.83313 | 121.3623 | 121.2662 | 0.11902 | -0.85602 | 121.3211 | 121.3257 | 121.3348 | -0.98419 | 121.2799 | 121.257 | 121.3394 | -0.96588
6192.2656 | 122.2504 | -121.2479 | 0.89722 | -0.058289 | 0.049759 | 0.059045 | 0.0029737 | 0.028047 | 0.0014548 | 0.030433 | -0.077515 | 0.015729 | 0.02556 | 0.036638 | 0.0070133 | 0.013259 | 0.07782 | 0.050354 | 0.013733 | 0.009155 | 0.10071 | 0.018311 | -0.1236 | 0.059509 | 0.036621 | -0.082397 | 0.07782 | 0.064087 | -0.059509 | -0.10529 | 121.2662 | 121.1243 | -0.79651 | 121.2982 | 121.257 | 0.13275 | -0.8194 | 121.1884 | 121.1426 | -0.8194 | 121.3074 | 121.1655 | 0.022889 | -0.83313 | 121.3486 | 121.3257 | 121.2616 | -1.0208 | 121.3257 | 121.312 | 121.2845 | -1.0025
6193.9844 | 122.3785 | -121.2204 | 0.85602 | 0.079041 | 0.049759 | 0.056055 | 0.0023329 | 0.027619 | -0.0036722 | 0.029365 | 0.097962 | 0.012952 | 0.023851 | 0.03792 | 0.0033817 | 0.015182 | 0.027466 | -0.009155 | -0.032043 | 0 | 0.1236 | -0.004578 | -0.14648 | 0.082397 | 0.022888 | -0.068665 | 0.073242 | 0.064087 | -0.050354 | -0.10986 | 121.2158 | 121.0739 | -0.73242 | 121.2112 | 121.2204 | 0.14648 | -0.82855 | 121.17 | 121.1105 | -0.78278 | 121.3028 | 121.1517 | 0.041198 | -0.79193 | 121.344 | 121.2479 | 121.1884 | -1.0025 | 121.2936 | 121.2845 | 121.2433 | -0.96588
6195.6875 | 122.319 | -121.2662 | 0.88806 | -0.17273 | 0.052323 | 0.057977 | 0.0072461 | 0.028901 | -0.0023904 | 0.02851 | -0.23773 | 0.011029 | 0.027055 | 0.034716 | 0.0018863 | 0.015396 | -0.009155 | 0.004578 | -0.018311 | 0.018311 | 0.11444 | 0.009155 | -0.15106 | 0.036621 | 0.054932 | -0.059509 | 0.07782 | 0.059509 | -0.041199 | -0.12817 | 121.2753 | 121.1151 | -0.77362 | 121.2708 | 121.2845 | 0.16937 | -0.89722 | 121.225 | 121.138 | -0.81024 | 121.3028 | 121.2067 | 0.068665 | -0.82855 | 121.3806 | 121.257 | 121.2479 | -1.0391 | 121.344 | 121.3257 | 121.3211 | -1.0162
6197.4219 | 122.3969 | -121.2662 | 0.8606 | 0.063782 | 0.049332 | 0.055627 | 0.0059643 | 0.02527 | -0.0092264 | 0.02851 | -0.046997 | 0.01167 | 0.023637 | 0.035143 | -0.0011045 | 0.017532 | 0.059509 | 0.13275 | 0.11444 | 0.082397 | 0.10986 | 0.036621 | -0.10071 | 0.16479 | 0.1831 | 0.091553 | 0.032043 | 0.027466 | -0.022888 | -0.068665 | 121.3028 | 121.1655 | -0.75073 | 121.3989 | 121.3486 | 0.18311 | -0.80109 | 121.2433 | 121.1975 | -0.82855 | 121.431 | 121.3577 | 0.16022 | -0.83313 | 121.376 | 121.3257 | 121.3806 | -0.9613 | 121.2982 | 121.2936 | 121.4493 | -0.92926
6199.1406 | 122.2824 | -121.2067 | 0.94757 | -0.11169 | 0.049973 | 0.058191 | 0.00041005 | 0.029328 | -0.0017496 | 0.029578 | -0.13092 | 0.017011 | 0.021074 | 0.038988 | 0.0061587 | 0.014968 | 0.086975 | 0.059509 | 0.018311 | 0.045776 | 0.11902 | 0.022888 | -0.14191 | 0.09613 | 0.091553 | -0.050354 | 0.082397 | 0.045776 | -0.045776 | -0.091553 | 121.2296 | 121.0648 | -0.82855 | 121.2662 | 121.2524 | 0.18768 | -0.8606 | 121.1609 | 121.1151 | -0.86517 | 121.3028 | 121.1563 | 0.041199 | -0.9018 | 121.3257 | 121.2936 | 121.225 | -1.0895 | 121.2891 | 121.2524 | 121.2982 | -1.0391
6200.8438 | 122.2778 | -121.2708 | 0.92926 | -0.22614 | 0.051255 | 0.058191 | 0.0053235 | 0.026979 | -0.0028178 | 0.029151 | -0.20721 | 0.014661 | 0.024919 | 0.036852 | 0.0014591 | 0.018173 | -0.009155 | 0.009155 | 0.004578 | -0.009155 | 0.11444 | 0 | -0.14648 | 0.013733 | 0.059509 | -0.068665 | 0.086975 | 0.07782 | -0.07782 | -0.11444 | 121.2708 | 121.1243 | -0.81482 | 121.2799 | 121.2616 | 0.13733 | -0.93841 | 121.1929 | 121.1563 | -0.84228 | 121.2845 | 121.2021 | 0.045776 | -0.85144 | 121.3852 | 121.2616 | 121.2753 | -1.0757 | 121.3577 | 121.3486 | 121.3303 | -1.0437
6202.5469 | 122.2916 | -121.2708 | 0.9201 | -0.26428 | 0.048691 | 0.059259 | 0.0063917 | 0.029756 | -0.0053812 | 0.025092 | -0.19958 | 0.012097 | 0.025346 | 0.037066 | 0.00039091 | 0.015396 | 0.022888 | 0.10071 | 0.036621 | 0.050354 | 0.10529 | 0.018311 | -0.14648 | 0.059509 | 0.07782 | -0.045776 | 0.068665 | 0.064087 | -0.036621 | -0.10071 | 121.2891 | 121.1243 | -0.81482 | 121.3715 | 121.3211 | 0.19684 | -0.89722 | 121.2341 | 121.17 | -0.85144 | 121.3303 | 121.225 | 0.054932 | -0.85602 | 121.376 | 121.2936 | 121.3074 | -1.0666 | 121.3394 | 121.3348 | 121.3486 | -1.0208
6204.2812 | 122.2504 | -121.2662 | 0.9201 | -0.04303 | 0.05275 | 0.057977 | -0.0025805 | 0.026551 | -4.058e-05 | 0.027442 | -0.0088499 | 0.014447 | 0.024492 | 0.039629 | 0.0057315 | 0.017532 | 0.050354 | 0.018311 | -0.013733 | 0.018311 | 0.1236 | 0.009155 | -0.15564 | 0.022888 | 0.013733 | -0.09613 | 0.073242 | 0.064087 | -0.064087 | -0.10986 | 121.2753 | 121.1105 | -0.79651 | 121.2845 | 121.2845 | 0.17395 | -0.86975 | 121.2021 | 121.1563 | -0.84686 | 121.2891 | 121.17 | 0.013733 | -0.85602 | 121.3898 | 121.3165 | 121.2524 | -1.0757 | 121.3394 | 121.3303 | 121.2799 | -1.03
6206.0156 | 122.2961 | -121.2524 | 0.92926 | -0.23376 | 0.051255 | 0.062677 | 0.0042555 | 0.027406 | -0.006663 | 0.027656 | -0.16907 | 0.013806 | 0.025987 | 0.036211 | 0.00039091 | 0.016891 | -0.036621 | 0.045776 | 0.004578 | 0 | 0.11444 | 0.004578 | -0.15106 | 0.018311 | 0.068665 | -0.050354 | 0.082397 | 0.068665 | -0.059509 | -0.11444 | 121.257 | 121.1014 | -0.81482 | 121.2982 | 121.2524 | 0.15106 | -0.96588 | 121.1929 | 121.138 | -0.84686 | 121.2708 | 121.2021 | 0.064087 | -0.86059 | 121.3669 | 121.2158 | 121.257 | -1.0803 | 121.3348 | 121.3211 | 121.3211 | -1.0437
6207.7188 | 122.4014 | -121.225 | 0.89264 | -0.0048827 | 0.04805 | 0.061182 | 0.0021191 | 0.024415 | -0.010722 | 0.025092 | -0.0012209 | 0.013166 | 0.023424 | 0.036211 | -0.0025999 | 0.018386 | 0.022888 | 0.073242 | 0.068665 | 0.045776 | 0.07782 | 0.013733 | -0.12817 | 0.10071 | 0.1236 | 0.045776 | 0.041199 | 0.050354 | -0.036621 | -0.07782 | 121.2387 | 121.0968 | -0.81482 | 121.2982 | 121.2708 | 0.17395 | -0.86975 | 121.1884 | 121.1472 | -0.85144 | 121.3257 | 121.2708 | 0.1236 | -0.84228 | 121.3028 | 121.2479 | 121.2936 | -1.0208 | 121.2662 | 121.2753 | 121.3486 | -0.97046
6209.4219 | 122.2824 | -121.2708 | 0.93842 | -0.073547 | 0.050827 | 0.054346 | 0.0012647 | 0.028688 | 0.00060022 | 0.027656 | -0.12329 | 0.015088 | 0.023851 | 0.038775 | 0.0055179 | 0.016891 | 0.091553 | 0.041199 | 0.004578 | 0.032043 | 0.10071 | 0.009155 | -0.14191 | 0.082397 | 0.059509 | -0.050354 | 0.07782 | 0.068665 | -0.050354 | -0.091553 | 121.2799 | 121.1288 | -0.83771 | 121.312 | 121.3028 | 0.17395 | -0.84686 | 121.2204 | 121.1792 | -0.8606 | 121.3531 | 121.2204 | 0.041199 | -0.86975 | 121.3715 | 121.3623 | 121.2753 | -1.0803 | 121.3486 | 121.3394 | 121.3303 | -1.03
6211.1562 | 122.3923 | -121.2662 | 0.87891 | 0.17059 | 0.047409 | 0.056055 | 0.0023329 | 0.023561 | -0.004313 | 0.027869 | 0.15137 | 0.015088 | 0.024705 | 0.036852 | 0.0020999 | 0.018173 | 0.10986 | 0.12817 | 0.1236 | 0.073242 | 0.09613 | 0.054932 | -0.10986 | 0.15106 | 0.14191 | 0.054932 | 0.036621 | 0.018311 | -0.013733 | -0.068665 | 121.3211 | 121.1563 | -0.78278 | 121.3943 | 121.3394 | 0.18311 | -0.76904 | 121.2524 | 121.1975 | -0.84228 | 121.4172 | 121.3211 | 0.1236 | -0.86059 | 121.3623 | 121.376 | 121.3898 | -0.98877 | 121.3028 | 121.2845 | 121.4081 | -0.94757
6212.8594 | 122.3465 | -121.2753 | 0.90179 | -0.21088 | 0.04805 | 0.0599 | 0.0051099 | 0.027619 | -0.0045266 | 0.027228 | -0.19958 | 0.015088 | 0.024919 | 0.036852 | 0.0023135 | 0.015609 | 0.009155 | -0.009155 | -0.041199 | -0.004578 | 0.12817 | 0 | -0.16937 | 0.027466 | 0.050354 | -0.068665 | 0.10529 | 0.073242 | -0.059509 | -0.11444 | 121.2753 | 121.106 | -0.77362 | 121.2662 | 121.2708 | 0.16479 | -0.89264 | 121.2158 | 121.1609 | -0.79651 | 121.3028 | 121.2067 | 0.045776 | -0.82855 | 121.4035 | 121.2845 | 121.2341 | -1.0712 | 121.3806 | 121.3486 | 121.3257 | -1.0162
6214.6094 | 122.3099 | -121.2753 | 0.89722 | -0.088806 | 0.051895 | 0.058618 | 0.0036145 | 0.026765 | -0.0017496 | 0.029365 | -0.11566 | 0.013806 | 0.022569 | 0.03792 | 0.0063723 | 0.017959 | 0.07782 | 0.054932 | 0.009155 | 0.041199 | 0.10986 | -0.004578 | -0.14191 | 0.073242 | 0.068665 | -0.068665 | 0.07782 | 0.059509 | -0.041199 | -0.09613 | 121.2708 | 121.1334 | -0.78735 | 121.3303 | 121.3165 | 0.18311 | -0.8194 | 121.2341 | 121.1792 | -0.8194 | 121.3486 | 121.2067 | 0.027465 | -0.83771 | 121.3852 | 121.3531 | 121.2845 | -1.0391 | 121.3531 | 121.3348 | 121.344 | -0.99335
6216.3125 | 122.3969 | -121.225 | 0.90179 | 0.040894 | 0.043778 | 0.058618 | 0.0012647 | 0.025483 | -0.0096536 | 0.025947 | 0.082703 | 0.0093204 | 0.021287 | 0.034929 | 0.0014591 | 0.021804 | 0.022888 | 0.10071 | 0.068665 | 0.041199 | 0.09613 | 0.032043 | -0.10529 | 0.082397 | 0.091553 | 0.018311 | 0.064087 | 0.022888 | -0.045776 | -0.082397 | 121.257 | 121.1197 | -0.80566 | 121.3257 | 121.2662 | 0.14649 | -0.87891 | 121.1792 | 121.1426 | -0.83771 | 121.3074 | 121.2433 | 0.10071 | -0.87891 | 121.3211 | 121.2479 | 121.2936 | -1.0071 | 121.2891 | 121.2479 | 121.3165 | -0.98419
6218.0469 | 122.3236 | -121.2753 | 0.91095 | 0.018005 | 0.049546 | 0.058618 | 0.0025465 | 0.027833 | 0.00060022 | 0.028724 | 0.029297 | 0.013593 | 0.024278 | 0.037066 | 0.0040225 | 0.016464 | -0.009155 | -0.050354 | -0.054932 | -0.022888 | 0.11902 | 0.009155 | -0.14191 | 0.032043 | -0.018311 | -0.11444 | 0.07782 | 0.064087 | -0.054932 | -0.11444 | 121.2845 | 121.1334 | -0.79193 | 121.225 | 121.2524 | 0.11902 | -0.92011 | 121.2204 | 121.1609 | -0.83313 | 121.3074 | 121.1609 | 0 | -0.84686 | 121.3943 | 121.2662 | 121.2204 | -1.0529 | 121.3531 | 121.3394 | 121.257 | -1.0254
6219.7656 | 122.2961 | -121.2891 | 0.9201 | -0.058289 | 0.049973 | 0.057764 | 0.00019645 | 0.026551 | -0.0013224 | 0.027015 | -0.031738 | 0.016156 | 0.023851 | 0.037707 | 0.0035953 | 0.01625 | 0.054932 | 0.032043 | 0 | 0.027466 | 0.10986 | 0.013733 | -0.16022 | 0.036621 | 0.018311 | -0.091553 | 0.086975 | 0.054932 | -0.041199 | -0.10529 | 121.3028 | 121.1288 | -0.81024 | 121.3211 | 121.3165 | 0.18768 | -0.86517 | 121.2479 | 121.1838 | -0.83313 | 121.3257 | 121.1975 | 0.013733 | -0.86517 | 121.3989 | 121.344 | 121.2891 | -1.0803 | 121.376 | 121.344 | 121.3074 | -1.0254
6221.4688 | 122.3923 | -121.257 | 0.90179 | 0.094299 | 0.044419 | 0.059686 | 0.0012647 | 0.026338 | -0.0075174 | 0.02616 | 0.17426 | 0.011029 | 0.024065 | 0.034075 | 0.00017731 | 0.018386 | 0.064087 | 0.12817 | 0.10529 | 0.059509 | 0.07782 | 0.050354 | -0.09613 | 0.1236 | 0.11902 | 0.041199 | 0.045776 | 0.032043 | -0.018311 | -0.082397 | 121.3074 | 121.1609 | -0.82397 | 121.3852 | 121.3165 | 0.15564 | -0.83771 | 121.2387 | 121.1746 | -0.85602 | 121.3806 | 121.2982 | 0.1236 | -0.86975 | 121.3348 | 121.3211 | 121.3623 | -0.99792 | 121.3028 | 121.2891 | 121.376 | -0.98419
6223.1719 | 122.319 | -121.2936 | 0.94757 | -0.24139 | 0.049973 | 0.058191 | 0.0066053 | 0.028047 | -0.004954 | 0.024238 | -0.24536 | 0.012525 | 0.027055 | 0.036852 | -0.0023861 | 0.015182 | 0.018311 | 0.022888 | 0 | 0.013733 | 0.11902 | 0.009155 | -0.14648 | 0.027466 | 0.032043 | -0.07782 | 0.086975 | 0.086975 | -0.045776 | -0.1236 | 121.3028 | 121.1472 | -0.82855 | 121.3165 | 121.3074 | 0.16022 | -0.92926 | 121.2479 | 121.17 | -0.8606 | 121.3211 | 121.2158 | 0.045776 | -0.8606 | 121.4127 | 121.312 | 121.2936 | -1.0941 | 121.3806 | 121.3806 | 121.3257 | -1.0712
6224.9062 | 122.4243 | -121.2662 | 0.89264 | 0.0027468 | 0.049332 | 0.060541 | 0.0046827 | 0.025483 | -0.008372 | 0.025733 | 0.044556 | 0.009534 | 0.027055 | 0.033007 | 0.00081811 | 0.019027 | 0.013733 | 0.064087 | 0.059509 | 0.036621 | 0.09613 | 0.013733 | -0.11444 | 0.073242 | 0.07782 | 0.018311 | 0.064087 | 0.032043 | -0.027466 | -0.10071 | 121.2799 | 121.1517 | -0.79651 | 121.3303 | 121.3028 | 0.15106 | -0.87891 | 121.2387 | 121.1655 | -0.82855 | 121.3394 | 121.2845 | 0.11902 | -0.8606 | 121.3623 | 121.2799 | 121.3257 | -1.0071 | 121.3303 | 121.2982 | 121.344 | -0.99335
6226.6094 | 122.3465 | -121.3211 | 0.89722 | 0.063782 | 0.049332 | 0.0599 | 0.00019645 | 0.029969 | 0.00017302 | 0.026801 | 0.052185 | 0.013593 | 0.022783 | 0.037493 | 0.0059451 | 0.015823 | 0 | -0.027466 | -0.036621 | 0 | 0.12817 | -0.013733 | -0.13733 | 0.032043 | -0.009155 | -0.11444 | 0.091553 | 0.07782 | -0.041199 | -0.11444 | 121.3074 | 121.1838 | -0.76904 | 121.2936 | 121.3211 | 0.13733 | -0.89722 | 121.2799 | 121.2067 | -0.80566 | 121.3531 | 121.2067 | 0 | -0.8194 | 121.4493 | 121.3211 | 121.2845 | -1.0345 | 121.4127 | 121.3989 | 121.312 | -1.0117
6228.2969 | 122.3648 | -121.2799 | 0.90179 | -0.20325 | 0.049759 | 0.059045 | 0.0083143 | 0.025056 | -0.0062356 | 0.02616 | -0.13855 | 0.012525 | 0.025774 | 0.034075 | 0.00060451 | 0.017746 | 0.091553 | 0.14648 | 0.11902 | 0.082397 | 0.091553 | 0.018311 | -0.10986 | 0.1236 | 0.16022 | 0.050354 | 0.045776 | 0.032043 | -0.032043 | -0.064087 | 121.2982 | 121.17 | -0.81024 | 121.4264 | 121.3623 | 0.19226 | -0.81024 | 121.2479 | 121.2158 | -0.85602 | 121.4035 | 121.3303 | 0.11444 | -0.86975 | 121.3715 | 121.3715 | 121.3989 | -1.0117 | 121.3257 | 121.3119 | 121.4401 | -0.96588
6230.0156 | 122.319 | -121.3074 | 0.90179 | -0.081177 | 0.050827 | 0.053491 | 0.00041005 | 0.026338 | 0.00017302 | 0.028937 | -0.12329 | 0.01402 | 0.024278 | 0.03792 | 0.0035953 | 0.014541 | 0.07782 | 0.068665 | 0.027466 | 0.027466 | 0.1236 | 0.004578 | -0.13275 | 0.059509 | 0.054932 | -0.064087 | 0.07782 | 0.07782 | -0.041199 | -0.091553 | 121.312 | 121.1746 | -0.7782 | 121.376 | 121.3348 | 0.16022 | -0.82397 | 121.2662 | 121.2158 | -0.82397 | 121.3669 | 121.2433 | 0.027466 | -0.82397 | 121.431 | 121.3852 | 121.3348 | -1.0345 | 121.3852 | 121.3852 | 121.3623 | -0.99335
6231.7188 | 122.3648 | -121.3028 | 0.90179 | -0.21851 | 0.051255 | 0.059686 | 0.0070325 | 0.029328 | -0.0073038 | 0.028297 | -0.26062 | 0.013166 | 0.025774 | 0.035357 | 0.0012455 | 0.018386 | -0.018311 | 0 | -0.009155 | 0 | 0.1236 | -0.013733 | -0.13733 | 0.013733 | 0.036621 | -0.082397 | 0.086975 | 0.086975 | -0.086975 | -0.10986 | 121.2891 | 121.1655 | -0.7782 | 121.3028 | 121.3028 | 0.13733 | -0.9201 | 121.2158 | 121.1929 | -0.81482 | 121.3165 | 121.2204 | 0.027466 | -0.81482 | 121.4264 | 121.2845 | 121.2936 | -1.0391 | 121.3898 | 121.3898 | 121.3394 | -1.0117
6233.4062 | 122.4426 | -121.2616 | 0.87433 | 0.16296 | 0.0504 | 0.058405 | -0.00023075 | 0.028474 | -0.0023904 | 0.028937 | 0.12848 | 0.015515 | 0.020647 | 0.035143 | 0.0055179 | 0.0186 | 0.032043 | 0.041199 | 0.018311 | 0.027466 | 0.11444 | 0.013733 | -0.11444 | 0.10986 | 0.10986 | 0.013733 | 0.045776 | 0.036621 | -0.027466 | -0.091553 | 121.2753 | 121.1472 | -0.75989 | 121.3028 | 121.2891 | 0.14191 | -0.84229 | 121.2341 | 121.17 | -0.82855 | 121.3715 | 121.2753 | 0.10529 | -0.83771 | 121.376 | 121.2936 | 121.2799 | -0.98877 | 121.3074 | 121.2982 | 121.3715 | -0.96588
6235.1406 | 122.3785 | -121.312 | 0.90179 | -0.17273 | 0.048905 | 0.056482 | 0.0044691 | 0.02826 | -0.0019632 | 0.027656 | -0.19958 | 0.01402 | 0.02556 | 0.034502 | 0.0031681 | 0.016037 | 0.004578 | 0.009155 | -0.004578 | 0.018311 | 0.12817 | 0 | -0.14648 | 0.050354 | 0.073242 | -0.050354 | 0.086975 | 0.064087 | -0.064087 | -0.10986 | 121.312 | 121.1655 | -0.77362 | 121.3211 | 121.3303 | 0.16479 | -0.89722 | 121.2479 | 121.2021 | -0.81482 | 121.3623 | 121.2616 | 0.059509 | -0.83771 | 121.4401 | 121.3165 | 121.3074 | -1.0483 | 121.3989 | 121.376 | 121.3852 | -1.0117
6236.8438 | 122.438 | -121.2616 | 0.88348 | -0.18036 | 0.046341 | 0.0599 | 0.0053235 | 0.028047 | -0.00944 | 0.025519 | -0.13092 | 0.011884 | 0.026201 | 0.037066 | -0.0013181 | 0.017532 | 0.073242 | 0.16022 | 0.1236 | 0.091553 | 0.07782 | 0.032043 | -0.11444 | 0.14191 | 0.19226 | 0.054932 | 0.036621 | 0.032043 | -0.022888 | -0.082397 | 121.2936 | 121.1472 | -0.80566 | 121.4218 | 121.3531 | 0.20599 | -0.81024 | 121.2387 | 121.1792 | -0.84686 | 121.4035 | 121.3165 | 0.13733 | -0.85144 | 121.3394 | 121.3348 | 121.3852 | -0.99793 | 121.2982 | 121.2936 | 121.4539 | -0.96588
6238.6094 | 122.4426 | -121.2708 | 0.88806 | -0.15747 | 0.049118 | 0.059259 | 0.0057507 | 0.025483 | -0.0090128 | 0.027442 | -0.13855 | 0.01167 | 0.026414 | 0.036425 | 0.00039091 | 0.017532 | 0.091553 | 0.16022 | 0.10986 | 0.082397 | 0.091553 | 0.022888 | -0.10986 | 0.11902 | 0.19226 | 0.073242 | 0.045776 | 0.027466 | -0.022888 | -0.054932 | 121.2936 | 121.1609 | -0.79651 | 121.431 | 121.3531 | 0.19226 | -0.79651 | 121.2479 | 121.2158 | -0.84229 | 121.3898 | 121.344 | 0.12817 | -0.8606 | 121.3623 | 121.3623 | 121.3806 | -0.99793 | 121.3165 | 121.2982 | 121.463 | -0.94299
6240.2969 | 122.4152 | -121.312 | 0.90179 | -0.17273 | 0.048905 | 0.058191 | 0.0044691 | 0.028688 | -0.0062356 | 0.026588 | -0.16144 | 0.012097 | 0.024492 | 0.033434 | -0.00067729 | 0.015609 | 0.10986 | 0.14648 | 0.12817 | 0.07782 | 0.07782 | 0.022888 | -0.10986 | 0.13733 | 0.16937 | 0.050354 | 0.054932 | 0.027466 | -0.018311 | -0.068665 | 121.3348 | 121.2021 | -0.82397 | 121.4584 | 121.3898 | 0.18768 | -0.79193 | 121.2936 | 121.2433 | -0.84686 | 121.4493 | 121.3623 | 0.11902 | -0.87433 | 121.3898 | 121.4218 | 121.4401 | -1.0117 | 121.3669 | 121.3394 | 121.4813 | -0.97046
6242.0625 | 122.406 | -121.3257 | 0.87433 | 0.08667 | 0.049332 | 0.056909 | 0.00019645 | 0.02591 | 0.001882 | 0.027015 | 0.052185 | 0.01402 | 0.025346 | 0.037707 | 0.0048769 | 0.016677 | 0.022888 | -0.027466 | -0.045776 | -0.013733 | 0.13275 | 0.009155 | -0.15564 | 0.045776 | -0.022888 | -0.086975 | 0.07782 | 0.064087 | -0.054932 | -0.10071 | 121.3348 | 121.17 | -0.74158 | 121.2982 | 121.312 | 0.14191 | -0.85144 | 121.2708 | 121.225 | -0.79651 | 121.3715 | 121.2387 | 0.013733 | -0.81024 | 121.4584 | 121.3486 | 121.2799 | -1.03 | 121.4035 | 121.3898 | 121.3028 | -0.97504
6243.7656 | 122.3648 | -121.3623 | 0.89722 | -0.26428 | 0.048691 | 0.058832 | 0.0042555 | 0.024415 | -0.004313 | 0.026801 | -0.19958 | 0.012097 | 0.027269 | 0.035357 | 0.00039091 | 0.017532 | 0.050354 | 0.07782 | 0.045776 | 0.050354 | 0.086975 | 0.027466 | -0.13733 | 0.054932 | 0.068665 | -0.050354 | 0.068665 | 0.059509 | -0.059509 | -0.11444 | 121.3898 | 121.225 | -0.81024 | 121.4401 | 121.4127 | 0.18768 | -0.84686 | 121.3028 | 121.2479 | -0.82855 | 121.4172 | 121.312 | 0.064087 | -0.83771 | 121.4493 | 121.4127 | 121.4081 | -1.0345 | 121.431 | 121.4218 | 121.431 | -1.0117
6245.5 | 122.3328 | -121.3394 | 0.90179 | -0.0354 | 0.0504 | 0.058832 | 0.0025465 | 0.028688 | 0.0012412 | 0.029792 | -0.13092 | 0.01402 | 0.024919 | 0.036852 | 0.0057315 | 0.015823 | 0.050354 | 0.032043 | 0 | 0.027466 | 0.10529 | 0.009155 | -0.1236 | 0.027466 | 0.009155 | -0.10071 | 0.082397 | 0.059509 | -0.064087 | -0.10529 | 121.3486 | 121.2158 | -0.79651 | 121.3715 | 121.3669 | 0.15106 | -0.85144 | 121.2753 | 121.2341 | -0.8194 | 121.3669 | 121.2387 | 0.004578 | -0.84228 | 121.4447 | 121.3898 | 121.3394 | -1.0254 | 121.4218 | 121.3989 | 121.3486 | -1.0071
6247.2188 | 122.4792 | -121.3348 | 0.85602 | -0.020142 | 0.044205 | 0.058832 | 0.0036145 | 0.024201 | -0.00944 | 0.025733 | 0.029297 | 0.01167 | 0.024705 | 0.034929 | -0.00089089 | 0.0186 | 0.004578 | 0.073242 | 0.050354 | 0.036621 | 0.09613 | 0.022888 | -0.11444 | 0.10986 | 0.10986 | 0.027466 | 0.054932 | 0.036621 | -0.027466 | -0.082397 | 121.3577 | 121.2204 | -0.75989 | 121.4081 | 121.3715 | 0.15106 | -0.85144 | 121.3074 | 121.2524 | -0.80109 | 121.4447 | 121.3623 | 0.10986 | -0.8194 | 121.431 | 121.3394 | 121.3852 | -0.97046 | 121.3898 | 121.3715 | 121.4447 | -0.93841
6248.9219 | 122.3923 | -121.3165 | 0.87891 | -0.11169 | 0.05275 | 0.057764 | 0.0027601 | 0.027192 | 0.0010276 | 0.027442 | -0.14618 | 0.013806 | 0.024065 | 0.037493 | 0.0029543 | 0.014541 | 0.068665 | 0.050354 | 0.018311 | 0.036621 | 0.11902 | 0.004578 | -0.13733 | 0.086975 | 0.082397 | -0.050354 | 0.086975 | 0.064087 | -0.045776 | -0.10071 | 121.3211 | 121.1792 | -0.75989 | 121.3669 | 121.3531 | 0.17395 | -0.81024 | 121.2708 | 121.2158 | -0.79193 | 121.4035 | 121.2662 | 0.050354 | -0.81482 | 121.4355 | 121.3852 | 121.3348 | -1.0162 | 121.4035 | 121.3806 | 121.3989 | -0.97961
6250.6562 | 122.406 | -121.3531 | 0.89722 | -0.25665 | 0.049973 | 0.057336 | 0.0078871 | 0.028474 | -0.0038858 | 0.027015 | -0.2301 | 0.013806 | 0.024065 | 0.036638 | 0.0012455 | 0.016677 | 0 | -0.009155 | -0.027466 | -0.004578 | 0.13275 | -0.018311 | -0.16937 | 0.018311 | 0.036621 | -0.091553 | 0.086975 | 0.082397 | -0.054932 | -0.11902 | 121.3348 | 121.1838 | -0.76447 | 121.344 | 121.3486 | 0.16479 | -0.89722 | 121.2982 | 121.2341 | -0.81024 | 121.3715 | 121.2616 | 0.027466 | -0.81482 | 121.4859 | 121.3531 | 121.3257 | -1.0666 | 121.4401 | 121.4355 | 121.3898 | -1.0162
6252.3438 | 122.4472 | -121.312 | 0.86975 | 0.16296 | 0.048691 | 0.058618 | -0.0023669 | 0.027192 | -0.004954 | 0.029578 | 0.159 | 0.011457 | 0.022783 | 0.033221 | 0.0038089 | 0.019241 | 0.091553 | 0.1236 | 0.10986 | 0.07782 | 0.068665 | 0.045776 | -0.10529 | 0.15564 | 0.15106 | 0.045776 | 0.036621 | 0.022888 | -0.013733 | -0.054932 | 121.3577 | 121.2067 | -0.80109 | 121.4355 | 121.3898 | 0.18311 | -0.7782 | 121.2982 | 121.257 | -0.83313 | 121.4676 | 121.3577 | 0.10071 | -0.84686 | 121.3806 | 121.4035 | 121.4218 | -0.97504 | 121.3486 | 121.3348 | 121.463 | -0.92468
6254.0469 | 122.3648 | -121.3531 | 0.89722 | 0.048523 | 0.049759 | 0.056482 | 0.0010511 | 0.027192 | 0.00038662 | 0.028937 | 0.021668 | 0.015302 | 0.024492 | 0.036425 | 0.0057315 | 0.016891 | 0.004578 | -0.059509 | -0.041199 | -0.004578 | 0.10071 | -0.004578 | -0.16022 | 0.018311 | -0.027466 | -0.10529 | 0.07782 | 0.054932 | -0.059509 | -0.13733 | 121.3486 | 121.1929 | -0.79651 | 121.2936 | 121.3486 | 0.15564 | -0.89264 | 121.2936 | 121.2158 | -0.8194 | 121.3715 | 121.2479 | 0.032043 | -0.84229 | 121.4539 | 121.3577 | 121.3119 | -1.0574 | 121.431 | 121.4081 | 121.3257 | -1.0345
6255.7656 | 122.4792 | -121.3165 | 0.86975 | 0.079041 | 0.048264 | 0.058618 | 0.0016919 | 0.025483 | -0.0036722 | 0.028937 | 0.12848 | 0.015302 | 0.02321 | 0.039202 | 0.0046633 | 0.017532 | 0.018311 | -0.013733 | -0.032043 | -0.004578 | 0.11902 | 0.013733 | -0.14191 | 0.064087 | 0.022888 | -0.050354 | 0.068665 | 0.059509 | -0.036621 | -0.09613 | 121.3303 | 121.1746 | -0.75073 | 121.3028 | 121.312 | 0.13733 | -0.85144 | 121.2799 | 121.2204 | -0.80109 | 121.3806 | 121.2662 | 0.045776 | -0.81024 | 121.4355 | 121.3348 | 121.2845 | -1.0117 | 121.3852 | 121.376 | 121.3394 | -0.96588
6257.4688 | 122.3831 | -121.344 | 0.8606 | -0.14221 | 0.05275 | 0.057123 | 0.0078871 | 0.028688 | -0.00046778 | 0.026588 | -0.13092 | 0.013166 | 0.026842 | 0.036852 | 0.0010317 | 0.014968 | 0.054932 | 0.041199 | 0.032043 | 0.027466 | 0.10986 | 0.004578 | -0.1236 | 0.07782 | 0.10071 | -0.036621 | 0.073242 | 0.068665 | -0.064087 | -0.10529 | 121.3486 | 121.2204 | -0.75073 | 121.3852 | 121.3715 | 0.15106 | -0.80566 | 121.2799 | 121.2387 | -0.78735 | 121.4218 | 121.3074 | 0.068665 | -0.79193 | 121.4539 | 121.3989 | 121.376 | -0.98419 | 121.4172 | 121.4127 | 121.4447 | -0.96588
6259.1719 | 122.493 | -121.3303 | 0.86975 | -0.14984 | 0.046768 | 0.05755 | 0.0063917 | 0.026765 | -0.00944 | 0.025947 | -0.077515 | 0.010388 | 0.025987 | 0.034502 | -0.0030271 | 0.016677 | 0.073242 | 0.15564 | 0.1236 | 0.082397 | 0.07782 | 0.041199 | -0.1236 | 0.13275 | 0.18768 | 0.064087 | 0.045776 | 0.018311 | -0.036621 | -0.064087 | 121.3715 | 121.2067 | -0.79193 | 121.4859 | 121.4127 | 0.20599 | -0.79651 | 121.2936 | 121.2662 | -0.82398 | 121.463 | 121.3943 | 0.12817 | -0.85144 | 121.4081 | 121.4035 | 121.4539 | -0.99335 | 121.376 | 121.3486 | 121.5179 | -0.93384
6260.8906 | 122.5159 | -121.3303 | 0.8606 | -0.1651 | 0.049546 | 0.059473 | 0.0027601 | 0.027406 | -0.0090128 | 0.025306 | -0.069885 | 0.0097476 | 0.024705 | 0.035998 | 0.00039091 | 0.015823 | 0.082397 | 0.15564 | 0.10529 | 0.07782 | 0.091553 | 0.041199 | -0.1236 | 0.16479 | 0.20142 | 0.068665 | 0.054932 | 0.036621 | -0.027466 | -0.07782 | 121.3715 | 121.2067 | -0.76904 | 121.4859 | 121.4081 | 0.20142 | -0.7782 | 121.3028 | 121.2524 | -0.80566 | 121.4951 | 121.3989 | 0.14649 | -0.82398 | 121.4218 | 121.4127 | 121.4355 | -0.98419 | 121.3852 | 121.3669 | 121.5317 | -0.93842
6262.5781 | 122.5113 | -121.3165 | 0.8606 | 0.15533 | 0.049118 | 0.059686 | -0.00087155 | 0.023133 | -0.0011088 | 0.028083 | 0.059815 | 0.012952 | 0.020006 | 0.035998 | 0.0042361 | 0.015182 | 0.086975 | 0.064087 | 0.050354 | 0.059509 | 0.09613 | 0.041199 | -0.11444 | 0.15106 | 0.11902 | 0.018311 | 0.054932 | 0.041199 | -0.032043 | -0.064087 | 121.3577 | 121.2021 | -0.76447 | 121.3806 | 121.376 | 0.17395 | -0.77362 | 121.2845 | 121.2524 | -0.80566 | 121.4676 | 121.3348 | 0.082398 | -0.8194 | 121.4127 | 121.4035 | 121.3669 | -0.97504 | 121.3715 | 121.3577 | 121.4355 | -0.92468
6264.2812 | 122.4106 | -121.376 | 0.87891 | -0.22614 | 0.050614 | 0.058191 | 0.0055371 | 0.027833 | -0.0038858 | 0.025306 | -0.23773 | 0.013379 | 0.026414 | 0.033861 | 0.0012455 | 0.018386 | -0.004578 | 0.004578 | -0.032043 | -0.013733 | 0.14648 | -0.013733 | -0.17853 | 0.022888 | 0.027466 | -0.082397 | 0.07782 | 0.068665 | -0.064087 | -0.10986 | 121.3623 | 121.1975 | -0.73242 | 121.3806 | 121.3623 | 0.16479 | -0.88348 | 121.312 | 121.2662 | -0.80109 | 121.3989 | 121.2936 | 0.027466 | -0.81024 | 121.5225 | 121.3715 | 121.344 | -1.0574 | 121.4539 | 121.4447 | 121.4035 | -0.98877
6266.0156 | 122.5067 | -121.3669 | 0.84686 | -0.11169 | 0.0457 | 0.061823 | 0.0031873 | 0.02527 | -0.007731 | 0.025092 | -0.085144 | 0.012097 | 0.02321 | 0.034716 | -0.0013181 | 0.01625 | 0.073242 | 0.14191 | 0.10986 | 0.07782 | 0.086975 | 0.036621 | -0.10986 | 0.15564 | 0.17853 | 0.07782 | 0.041199 | 0.045776 | -0.022888 | -0.07782 | 121.4035 | 121.257 | -0.75989 | 121.5088 | 121.4447 | 0.18768 | -0.77362 | 121.344 | 121.2891 | -0.80566 | 121.5225 | 121.4447 | 0.15564 | -0.80109 | 121.4539 | 121.4401 | 121.4767 | -0.95673 | 121.4081 | 121.4127 | 121.5454 | -0.92468
6267.7188 | 122.4655 | -121.3669 | 0.85602 | 0.12482 | 0.046128 | 0.059686 | -0.00044435 | 0.028901 | -0.0038858 | 0.025733 | 0.10559 | 0.011243 | 0.022569 | 0.035143 | 0.0033817 | 0.017532 | 0.11902 | 0.13275 | 0.10071 | 0.059509 | 0.068665 | 0.054932 | -0.09613 | 0.14191 | 0.1236 | 0.054932 | 0.050354 | 0.022888 | 0 | -0.068665 | 121.4218 | 121.2708 | -0.78735 | 121.4996 | 121.4264 | 0.15564 | -0.737 | 121.3669 | 121.2982 | -0.80566 | 121.5088 | 121.4218 | 0.1236 | -0.83313 | 121.4355 | 121.4859 | 121.4676 | -0.95215 | 121.4172 | 121.3898 | 121.4905 | -0.92468
6269.4219 | 122.5021 | -121.3486 | 0.83313 | 0.08667 | 0.051041 | 0.057336 | -0.00087155 | 0.025483 | 0.00017302 | 0.027442 | 0.044556 | 0.014875 | 0.022356 | 0.036425 | 0.0070133 | 0.016037 | 0.032043 | -0.009155 | -0.032043 | -0.004578 | 0.12817 | 0 | -0.16479 | 0.064087 | 0.009155 | -0.07782 | 0.07782 | 0.068665 | -0.050354 | -0.091553 | 121.3486 | 121.1838 | -0.70496 | 121.3394 | 121.344 | 0.16022 | -0.80109 | 121.2982 | 121.257 | -0.75531 | 121.4127 | 121.2708 | 0.013733 | -0.76447 | 121.4767 | 121.3806 | 121.3165 | -0.99793 | 121.4264 | 121.4172 | 121.3577 | -0.92468
6271.1406 | 122.4289 | -121.3531 | 0.87433 | -0.21088 | 0.050614 | 0.059686 | 0.0081007 | 0.029542 | -0.0021768 | 0.026801 | -0.19196 | 0.013806 | 0.02556 | 0.038775 | 0.0012455 | 0.015396 | 0.013733 | -0.013733 | -0.027466 | 0.009155 | 0.15564 | 0 | -0.16937 | 0.018311 | 0.036621 | -0.082397 | 0.086975 | 0.068665 | -0.045776 | -0.11902 | 121.3531 | 121.1838 | -0.71869 | 121.3394 | 121.3623 | 0.17853 | -0.8606 | 121.3074 | 121.2341 | -0.78735 | 121.3715 | 121.2708 | 0.036622 | -0.80566 | 121.5088 | 121.3669 | 121.3257 | -1.0437 | 121.4401 | 121.4218 | 121.3898 | -0.99335
6272.8438 | 122.4747 | -121.3531 | 0.85602 | 0.025635 | 0.046982 | 0.057336 | 0.0048963 | 0.026979 | -0.006663 | 0.025733 | 0.029297 | 0.013166 | 0.023424 | 0.034929 | 0.00017731 | 0.017105 | 0.018311 | 0.064087 | 0.064087 | 0.032043 | 0.091553 | 0.018311 | -0.10529 | 0.073242 | 0.09613 | 0.009155 | 0.045776 | 0.041199 | -0.045776 | -0.10071 | 121.3715 | 121.2479 | -0.76446 | 121.4172 | 121.3852 | 0.13733 | -0.83771 | 121.3074 | 121.2524 | -0.81024 | 121.4264 | 121.3623 | 0.10986 | -0.81482 | 121.4447 | 121.3715 | 121.4172 | -0.9613 | 121.3989 | 121.3943 | 121.4493 | -0.95673
6274.5469 | 122.5021 | -121.3348 | 0.86517 | 0.056152 | 0.050614 | 0.056909 | -0.0010851 | 0.026338 | -0.0019632 | 0.027228 | 0.12085 | 0.011884 | 0.019151 | 0.037279 | 0.0070133 | 0.015609 | 0.050354 | -0.004578 | -0.018311 | -0.004578 | 0.11444 | 0.013733 | -0.1236 | 0.091553 | 0.041199 | -0.050354 | 0.059509 | 0.045776 | -0.032043 | -0.086975 | 121.3486 | 121.2112 | -0.75073 | 121.3303 | 121.3303 | 0.11902 | -0.81482 | 121.3028 | 121.2479 | -0.80566 | 121.4264 | 121.2845 | 0.036621 | -0.8194 | 121.4493 | 121.3852 | 121.3165 | -0.98877 | 121.3943 | 121.3806 | 121.376 | -0.95215
6276.2812 | 122.5159 | -121.3486 | 0.85602 | 0.14771 | 0.047837 | 0.05755 | 0.00019645 | 0.026979 | -0.0017496 | 0.029151 | 0.12085 | 0.013593 | 0.021501 | 0.035998 | 0.0046633 | 0.01625 | 0.059509 | 0.041199 | 0.022888 | 0.009155 | 0.11444 | 0.022888 | -0.10986 | 0.12817 | 0.11444 | 0.004578 | 0.045776 | 0.054932 | -0.027466 | -0.086975 | 121.3715 | 121.2387 | -0.74158 | 121.3898 | 121.3577 | 0.11902 | -0.79651 | 121.3211 | 121.2616 | -0.81024 | 121.4767 | 121.3531 | 0.091553 | -0.80109 | 121.463 | 121.4081 | 121.3715 | -0.96588 | 121.3943 | 121.4035 | 121.463 | -0.94299
6277.9844 | 122.3511 | -121.3898 | 0.89264 | -0.027771 | 0.0504 | 0.056482 | 0.0029737 | 0.02826 | 0.0010276 | 0.029578 | -0.031738 | 0.016156 | 0.025987 | 0.037493 | 0.0038089 | 0.014328 | 0.064087 | 0.022888 | -0.013733 | 0.022888 | 0.1236 | 0.004578 | -0.14191 | 0.045776 | 0.013733 | -0.10529 | 0.086975 | 0.073242 | -0.045776 | -0.10071 | 121.3943 | 121.2479 | -0.76904 | 121.4127 | 121.4127 | 0.16479 | -0.82855 | 121.344 | 121.2891 | -0.80566 | 121.4355 | 121.2845 | -0.004578 | -0.8194 | 121.5134 | 121.4539 | 121.376 | -1.0345 | 121.4767 | 121.463 | 121.4035 | -0.99335
6279.7031 | 122.5342 | -121.3715 | 0.83771 | -0.020142 | 0.039292 | 0.059473 | 0.0023329 | 0.027406 | -0.010508 | 0.025519 | -0.024109 | 0.011457 | 0.021715 | 0.034929 | 0.00017731 | 0.019027 | 0.022888 | 0.10986 | 0.082397 | 0.045776 | 0.09613 | 0.022888 | -0.10986 | 0.1236 | 0.12817 | 0.059509 | 0.054932 | 0.045776 | -0.022888 | -0.07782 | 121.3943 | 121.2616 | -0.74158 | 121.4813 | 121.4172 | 0.15564 | -0.81482 | 121.3486 | 121.2936 | -0.78278 | 121.4951 | 121.431 | 0.13733 | -0.79193 | 121.4676 | 121.3943 | 121.4539 | -0.94757 | 121.4264 | 121.4172 | 121.4996 | -0.91553
6281.4062 | 122.4335 | -121.4035 | 0.89264 | -0.27191 | 0.049332 | 0.058405 | 0.0012647 | 0.027833 | -0.002604 | 0.024879 | -0.21484 | 0.015088 | 0.021928 | 0.03557 | 0.0023135 | 0.016037 | 0.018311 | -0.013733 | -0.022888 | 0 | 0.13275 | 0.004578 | -0.16479 | 0.022888 | 0.018311 | -0.082397 | 0.10529 | 0.064087 | -0.050354 | -0.10986 | 121.4081 | 121.2387 | -0.75989 | 121.3898 | 121.4035 | 0.16479 | -0.87433 | 121.3531 | 121.2936 | -0.78735 | 121.4264 | 121.3211 | 0.027466 | -0.82855 | 121.5363 | 121.4218 | 121.3806 | -1.0574 | 121.5088 | 121.4676 | 121.4218 | -1.0025
6283.1406 | 122.5113 | -121.3531 | 0.84228 | -0.012512 | 0.044205 | 0.059473 | 0.0048963 | 0.02591 | -0.010295 | 0.024024 | 0.029297 | 0.010388 | 0.024065 | 0.035784 | 0.00060451 | 0.016677 | 0.027466 | 0.050354 | 0.068665 | 0.045776 | 0.082397 | 0.027466 | -0.11902 | 0.091553 | 0.10071 | 0.032043 | 0.045776 | 0.022888 | -0.036621 | -0.086975 | 121.3806 | 121.2341 | -0.75989 | 121.4035 | 121.3989 | 0.16479 | -0.81482 | 121.3165 | 121.2662 | -0.79651 | 121.4447 | 121.3852 | 0.11902 | -0.8194 | 121.4355 | 121.3806 | 121.4218 | -0.9613 | 121.3989 | 121.376 | 121.4539 | -0.92926
6284.8438 | 122.3694 | -121.3898 | 0.87891 | -0.012512 | 0.051041 | 0.057977 | 0.0014783 | 0.026338 | 0.0010276 | 0.028297 | -0.062256 | 0.015515 | 0.022783 | 0.035784 | 0.0065859 | 0.016677 | 0.082397 | 0.009155 | 0.004578 | 0.009155 | 0.12817 | 0.013733 | -0.15106 | 0.050354 | 0.018311 | -0.086975 | 0.059509 | 0.07782 | -0.050354 | -0.10071 | 121.4035 | 121.2387 | -0.75073 | 121.3989 | 121.3989 | 0.16022 | -0.79651 | 121.3394 | 121.2891 | -0.8194 | 121.4401 | 121.3028 | 0.013733 | -0.80109 | 121.5179 | 121.4722 | 121.3943 | -1.03 | 121.4493 | 121.4676 | 121.4081 | -0.97961
6286.5625 | 122.4747 | -121.3577 | 0.86517 | 0.063782 | 0.0457 | 0.058832 | 0.0010511 | 0.026551 | -0.008372 | 0.025092 | 0.10559 | 0.0091066 | 0.023851 | 0.033007 | 0.0016727 | 0.020309 | 0.050354 | 0.10071 | 0.073242 | 0.036621 | 0.068665 | 0.045776 | -0.10986 | 0.11444 | 0.09613 | 0.018311 | 0.022888 | 0.027466 | -0.004578 | -0.082397 | 121.4035 | 121.2479 | -0.79651 | 121.4584 | 121.3943 | 0.14648 | -0.81482 | 121.3531 | 121.2753 | -0.84228 | 121.4722 | 121.376 | 0.10071 | -0.83771 | 121.4264 | 121.4081 | 121.431 | -0.97504 | 121.3806 | 121.3852 | 121.4539 | -0.94757
6288.2656 | 122.4518 | -121.3943 | 0.8194 | -0.19562 | 0.047837 | 0.061395 | 0.0023329 | 0.02826 | -0.006663 | 0.024451 | -0.16144 | 0.011884 | 0.024065 | 0.034289 | 0.0025271 | 0.014968 | 0.10986 | 0.14648 | 0.11902 | 0.068665 | 0.086975 | 0.022888 | -0.10529 | 0.13733 | 0.17395 | 0.050354 | 0.050354 | 0.027466 | -0.022888 | -0.073242 | 121.4172 | 121.2891 | -0.73242 | 121.5408 | 121.463 | 0.17395 | -0.70953 | 121.3715 | 121.3211 | -0.76904 | 121.5317 | 121.4447 | 0.1236 | -0.79193 | 121.4813 | 121.5042 | 121.5134 | -0.92468 | 121.4447 | 121.4218 | 121.5683 | -0.89264
6289.9688 | 122.4655 | -121.4035 | 0.85144 | 0.08667 | 0.047623 | 0.059473 | 0.0010511 | 0.025483 | -0.007731 | 0.027228 | 0.097962 | 0.012525 | 0.025133 | 0.034289 | -0.00046349 | 0.017532 | 0.10986 | 0.10986 | 0.082397 | 0.045776 | 0.086975 | 0.050354 | -0.11444 | 0.11902 | 0.09613 | 0.018311 | 0.045776 | 0.041199 | -0.022888 | -0.086975 | 121.4539 | 121.2891 | -0.76446 | 121.5134 | 121.4493 | 0.16022 | -0.74158 | 121.3806 | 121.3165 | -0.80566 | 121.5225 | 121.4218 | 0.10529 | -0.81024 | 121.4905 | 121.5134 | 121.4859 | -0.96588 | 121.4493 | 121.4447 | 121.4996 | -0.93841
6291.6875 | 122.493 | -121.4218 | 0.82855 | 0.08667 | 0.051041 | 0.05755 | 0.00083745 | 0.029115 | 0.00081382 | 0.028297 | 0.0064086 | 0.014234 | 0.023637 | 0.036211 | 0.0040225 | 0.015396 | 0.050354 | -0.027466 | -0.018311 | 0 | 0.12817 | 0.004578 | -0.13733 | 0.073242 | 0 | -0.086975 | 0.086975 | 0.050354 | -0.050354 | -0.10071 | 121.4264 | 121.2845 | -0.70038 | 121.3943 | 121.4218 | 0.13733 | -0.7782 | 121.3715 | 121.3211 | -0.74158 | 121.4951 | 121.3348 | 0.013733 | -0.7782 | 121.55 | 121.4722 | 121.4035 | -0.96588 | 121.5088 | 121.4722 | 121.4218 | -0.92926
6293.3906 | 122.5204 | -121.3943 | 0.82398 | -0.15747 | 0.046982 | 0.060327 | 0.0066053 | 0.027619 | -0.0064492 | 0.027656 | -0.12329 | 0.0084658 | 0.022783 | 0.034502 | -3.629e-05 | 0.015823 | 0.10071 | 0.16022 | 0.13275 | 0.07782 | 0.09613 | 0.027466 | -0.11444 | 0.15106 | 0.19684 | 0.059509 | 0.050354 | 0.022888 | -0.018311 | -0.064087 | 121.4218 | 121.2799 | -0.72785 | 121.5546 | 121.4722 | 0.19226 | -0.72327 | 121.376 | 121.3303 | -0.77362 | 121.5454 | 121.4539 | 0.1236 | -0.80109 | 121.4905 | 121.4951 | 121.5271 | -0.93842 | 121.4447 | 121.4172 | 121.5912 | -0.88806
6295.1406 | 122.4426 | -121.4355 | 0.84686 | -0.14221 | 0.053177 | 0.0552 | 0.0031873 | 0.026765 | 0.001882 | 0.027869 | -0.1767 | 0.011243 | 0.02556 | 0.038988 | 0.0057315 | 0.014755 | 0.07782 | 0.064087 | 0.018311 | 0.036621 | 0.10986 | 0.022888 | -0.14191 | 0.10071 | 0.091553 | -0.036621 | 0.073242 | 0.045776 | -0.050354 | -0.091553 | 121.4584 | 121.2936 | -0.737 | 121.4996 | 121.4722 | 0.17853 | -0.76904 | 121.3852 | 121.344 | -0.77362 | 121.5363 | 121.3989 | 0.054932 | -0.80109 | 121.5454 | 121.5134 | 121.4539 | -0.98877 | 121.5088 | 121.4813 | 121.5271 | -0.93842
6296.8438 | 122.4243 | -121.4401 | 0.83771 | -0.20325 | 0.047623 | 0.056909 | 0.0061781 | 0.024842 | -0.006022 | 0.026801 | -0.12329 | 0.011457 | 0.025133 | 0.034289 | -0.0013181 | 0.016891 | 0.073242 | 0.13733 | 0.10529 | 0.07782 | 0.059509 | 0.013733 | -0.13733 | 0.1236 | 0.16022 | 0.032043 | 0.050354 | 0.032043 | -0.022888 | -0.059509 | 121.4539 | 121.3028 | -0.7782 | 121.5775 | 121.5179 | 0.21515 | -0.76447 | 121.4172 | 121.3806 | -0.78735 | 121.5637 | 121.4722 | 0.091552 | -0.80566 | 121.4996 | 121.5134 | 121.5454 | -0.97504 | 121.4905 | 121.4722 | 121.6003 | -0.89722
6298.5625 | 122.5204 | -121.3989 | 0.82398 | 0.14008 | 0.049759 | 0.058618 | -0.00065795 | 0.028901 | -0.0023904 | 0.026801 | 0.17426 | 0.012311 | 0.024278 | 0.03557 | 0.0050907 | 0.017318 | 0.09613 | 0.13275 | 0.10529 | 0.091553 | 0.068665 | 0.050354 | -0.10986 | 0.15564 | 0.12817 | 0.054932 | 0.032043 | 0.027466 | -0.041199 | -0.068665 | 121.4493 | 121.2891 | -0.75531 | 121.5317 | 121.4905 | 0.20142 | -0.72785 | 121.3577 | 121.3303 | -0.79193 | 121.5546 | 121.4539 | 0.1236 | -0.79651 | 121.4676 | 121.4951 | 121.5042 | -0.93384 | 121.431 | 121.4264 | 121.5271 | -0.89264
6300.2656 | 122.4518 | -121.4447 | 0.85602 | -0.21851 | 0.047623 | 0.059473 | 0.0025465 | 0.026338 | -0.0036722 | 0.026588 | -0.19958 | 0.015088 | 0.024492 | 0.035143 | 0.0020999 | 0.016037 | 0 | 0.013733 | -0.027466 | 0.004578 | 0.12817 | 0.004578 | -0.15564 | 0.027466 | 0.054932 | -0.07782 | 0.086975 | 0.064087 | -0.073242 | -0.11902 | 121.4493 | 121.2891 | -0.72784 | 121.4584 | 121.4493 | 0.16022 | -0.85602 | 121.3715 | 121.3257 | -0.76904 | 121.4722 | 121.3669 | 0.041199 | -0.79193 | 121.5729 | 121.4447 | 121.4172 | -1.0117 | 121.5317 | 121.5088 | 121.4996 | -0.97504
6302 | 122.493 | -121.4401 | 0.83771 | 0.079041 | 0.046341 | 0.05755 | 0.0012647 | 0.023347 | -0.0062356 | 0.028083 | 0.13611 | 0.011884 | 0.022569 | 0.033434 | 0.0025271 | 0.0186 | 0.073242 | 0.14191 | 0.10071 | 0.059509 | 0.073242 | 0.054932 | -0.082397 | 0.14648 | 0.1236 | 0.050354 | 0.045776 | 0.027466 | -0.027466 | -0.073242 | 121.4951 | 121.3577 | -0.76447 | 121.582 | 121.4996 | 0.14191 | -0.76447 | 121.4127 | 121.3669 | -0.79193 | 121.5866 | 121.4905 | 0.1236 | -0.81024 | 121.5134 | 121.5134 | 121.5408 | -0.9201 | 121.4859 | 121.4676 | 121.5637 | -0.91095
6303.7344 | 122.4152 | -121.4813 | 0.88348 | -0.096436 | 0.050614 | 0.058832 | 0.0034009 | 0.025483 | -0.0045266 | 0.026801 | -0.22247 | 0.011243 | 0.026414 | 0.035357 | 0.0025271 | 0.017318 | 0 | 0.027466 | 0 | 0.013733 | 0.13275 | -0.018311 | -0.15564 | 0.027466 | 0.041199 | -0.091553 | 0.073242 | 0.073242 | -0.064087 | -0.11444 | 121.463 | 121.3257 | -0.75073 | 121.5088 | 121.4951 | 0.16937 | -0.88348 | 121.4172 | 121.3669 | -0.81024 | 121.5088 | 121.3898 | 0.022888 | -0.81024 | 121.6141 | 121.4813 | 121.4813 | -1.0391 | 121.5546 | 121.5546 | 121.5225 | -0.99793
6305.4375 | 122.4609 | -121.4493 | 0.8194 | 0.11719 | 0.051895 | 0.059473 | 0.00083745 | 0.02826 | 0.0014548 | 0.027869 | 0.059815 | 0.013593 | 0.022356 | 0.035998 | 0.0061587 | 0.017746 | 0.009155 | -0.013733 | -0.036621 | 0.009155 | 0.11902 | -0.004578 | -0.14648 | 0.041199 | 0 | -0.07782 | 0.091553 | 0.064087 | -0.059509 | -0.11444 | 121.4447 | 121.3028 | -0.70038 | 121.4355 | 121.4584 | 0.15564 | -0.81024 | 121.3898 | 121.3348 | -0.72784 | 121.4905 | 121.3715 | 0.036621 | -0.75531 | 121.5683 | 121.4584 | 121.4127 | -0.96588 | 121.5408 | 121.5134 | 121.4493 | -0.93384
6307.1406 | 122.4518 | -121.4447 | 0.82398 | -0.14984 | 0.049546 | 0.055627 | 0.0044691 | 0.025056 | -0.0017496 | 0.030006 | -0.14618 | 0.013806 | 0.025346 | 0.03557 | 0.0020999 | 0.017318 | 0.068665 | 0.068665 | 0.022888 | 0.041199 | 0.11902 | 0.004578 | -0.14191 | 0.068665 | 0.091553 | -0.054932 | 0.064087 | 0.054932 | -0.054932 | -0.10986 | 121.4493 | 121.3028 | -0.70496 | 121.5134 | 121.4859 | 0.18311 | -0.75531 | 121.3898 | 121.3348 | -0.75989 | 121.5134 | 121.3898 | 0.054931 | -0.76904 | 121.5637 | 121.5134 | 121.4676 | -0.96588 | 121.5088 | 121.4996 | 121.5363 | -0.93384
6308.8594 | 122.4197 | -121.4722 | 0.82855 | 0.048523 | 0.050827 | 0.058618 | 0.0014783 | 0.028688 | -0.0019632 | 0.029151 | 0.014038 | 0.014661 | 0.023424 | 0.033648 | 0.0029543 | 0.019668 | 0.004578 | -0.022888 | -0.041199 | -0.013733 | 0.15106 | -0.009155 | -0.16022 | 0 | -0.013733 | -0.11902 | 0.09613 | 0.068665 | -0.054932 | -0.09613 | 121.463 | 121.312 | -0.67749 | 121.4493 | 121.4584 | 0.14648 | -0.82397 | 121.4172 | 121.376 | -0.73242 | 121.4722 | 121.3531 | -0.022889 | -0.75989 | 121.6232 | 121.4767 | 121.431 | -0.98877 | 121.5683 | 121.5408 | 121.4584 | -0.92468
6310.6094 | 122.4289 | -121.4676 | 0.85144 | -0.19562 | 0.049332 | 0.060327 | 0.0046827 | 0.026979 | -0.0081582 | 0.025092 | -0.10803 | 0.012952 | 0.024492 | 0.036211 | -0.0028135 | 0.0186 | 0.059509 | 0.13733 | 0.11902 | 0.07782 | 0.068665 | 0.036621 | -0.11444 | 0.11444 | 0.17395 | 0.041199 | 0.050354 | 0.027466 | -0.041199 | -0.082397 | 121.5042 | 121.3531 | -0.78277 | 121.6049 | 121.5454 | 0.19226 | -0.79193 | 121.4264 | 121.3852 | -0.80109 | 121.582 | 121.5088 | 0.1236 | -0.82397 | 121.5363 | 121.5271 | 121.5866 | -0.96588 | 121.5179 | 121.4951 | 121.6415 | -0.93384
6312.2969 | 122.5296 | -121.4355 | 0.82398 | 0.15533 | 0.049332 | 0.060541 | -0.0019397 | 0.025056 | -0.0036722 | 0.028724 | 0.14374 | 0.012952 | 0.021501 | 0.03557 | 0.0038089 | 0.017959 | 0.10529 | 0.091553 | 0.082397 | 0.082397 | 0.086975 | 0.022888 | -0.09613 | 0.13733 | 0.14191 | 0.036621 | 0.036621 | 0.018311 | -0.027466 | -0.068665 | 121.4584 | 121.3394 | -0.737 | 121.5271 | 121.5179 | 0.17853 | -0.71869 | 121.4081 | 121.3669 | -0.78735 | 121.5729 | 121.4722 | 0.10529 | -0.80566 | 121.5225 | 121.5408 | 121.5179 | -0.9201 | 121.4722 | 121.4539 | 121.5775 | -0.89264
6314 | 122.5662 | -121.4218 | 0.80109 | -0.027771 | 0.043991 | 0.059259 | 0.0023329 | 0.02527 | -0.0098672 | 0.027442 | 0.059815 | 0.011884 | 0.024065 | 0.032366 | -0.00067729 | 0.017318 | 0.027466 | 0.064087 | 0.059509 | 0.041199 | 0.091553 | 0.036621 | -0.11902 | 0.086975 | 0.09613 | 0.018311 | 0.059509 | 0.045776 | -0.041199 | -0.082397 | 121.4584 | 121.3028 | -0.70953 | 121.4859 | 121.463 | 0.16022 | -0.77362 | 121.3806 | 121.3394 | -0.74158 | 121.5088 | 121.4401 | 0.10071 | -0.75531 | 121.5134 | 121.4493 | 121.4813 | -0.9201 | 121.4813 | 121.4676 | 121.5179 | -0.88348
6315.7031 | 122.4335 | -121.4722 | 0.81482 | -0.11169 | 0.054886 | 0.056909 | 0.0076733 | 0.027406 | 0.0027364 | 0.026588 | -0.13855 | 0.015302 | 0.026628 | 0.038775 | 0.0038089 | 0.014328 | 0.082397 | 0.054932 | 0.018311 | 0.045776 | 0.10986 | 0.009155 | -0.11902 | 0.09613 | 0.086975 | -0.059509 | 0.073242 | 0.050354 | -0.032043 | -0.10071 | 121.4813 | 121.3531 | -0.70496 | 121.5271 | 121.5179 | 0.16479 | -0.73242 | 121.4401 | 121.3715 | -0.74158 | 121.5683 | 121.4127 | 0.041199 | -0.76446 | 121.582 | 121.5546 | 121.4905 | -0.93384 | 121.5454 | 121.5225 | 121.5591 | -0.91553
6317.4062 | 122.3969 | -121.4493 | 0.84228 | -0.050659 | 0.052536 | 0.057977 | 0.00083745 | 0.024629 | -0.00068138 | 0.027228 | -0.046997 | 0.011884 | 0.024065 | 0.035784 | 0.0063723 | 0.015182 | 0.054932 | 0.045776 | 0.009155 | 0.013733 | 0.11444 | 0.009155 | -0.13733 | 0.032043 | 0.027466 | -0.086975 | 0.082397 | 0.064087 | -0.054932 | -0.11444 | 121.4584 | 121.312 | -0.72784 | 121.4951 | 121.463 | 0.15106 | -0.78735 | 121.3943 | 121.3348 | -0.75989 | 121.4813 | 121.3623 | 0.027466 | -0.7782 | 121.5637 | 121.5042 | 121.4584 | -0.97961 | 121.5317 | 121.5134 | 121.4767 | -0.95673
6319.125 | 122.5525 | -121.4539 | 0.82398 | -0.14984 | 0.047837 | 0.058405 | 0.0046827 | 0.026979 | -0.010508 | 0.030006 | -0.046997 | 0.010602 | 0.023851 | 0.036211 | -0.00089089 | 0.0186 | 0.059509 | 0.16479 | 0.11444 | 0.086975 | 0.086975 | 0.009155 | -0.11444 | 0.17395 | 0.1831 | 0.10071 | 0.036621 | 0.032043 | -0.027466 | -0.07782 | 121.463 | 121.3394 | -0.737 | 121.6187 | 121.5408 | 0.20142 | -0.76447 | 121.4264 | 121.376 | -0.78735 | 121.6278 | 121.5546 | 0.17853 | -0.79193 | 121.5408 | 121.5134 | 121.5683 | -0.93842 | 121.4905 | 121.4859 | 121.637 | -0.9018
6320.8281 | 122.5433 | -121.4172 | 0.78278 | 0.16296 | 0.049332 | 0.061823 | 0.0012647 | 0.026338 | -0.0038858 | 0.029578 | 0.18188 | 0.012525 | 0.023637 | 0.034502 | 0.0046633 | 0.017105 | 0.073242 | 0.091553 | 0.073242 | 0.064087 | 0.09613 | 0.018311 | -0.10071 | 0.14191 | 0.11902 | 0.027466 | 0.041199 | 0.018311 | -0.032043 | -0.064087 | 121.4355 | 121.3165 | -0.68665 | 121.5088 | 121.4813 | 0.1648 | -0.70953 | 121.3852 | 121.3531 | -0.74158 | 121.5591 | 121.4447 | 0.091553 | -0.76447 | 121.5134 | 121.4905 | 121.4905 | -0.88348 | 121.4584 | 121.4355 | 121.5363 | -0.84686
6322.5469 | 122.4564 | -121.4905 | 0.8194 | -0.15747 | 0.051895 | 0.05755 | 0.0040417 | 0.027619 | -0.00089518 | 0.030433 | -0.15381 | 0.015943 | 0.023424 | 0.034716 | 0.0027407 | 0.012619 | 0.059509 | 0.032043 | 0.018311 | 0.036621 | 0.10071 | 0.009155 | -0.15564 | 0.07782 | 0.07782 | -0.045776 | 0.07782 | 0.059509 | -0.059509 | -0.10071 | 121.4996 | 121.3348 | -0.71869 | 121.5225 | 121.5271 | 0.19226 | -0.75989 | 121.431 | 121.3898 | -0.74158 | 121.5683 | 121.4447 | 0.054932 | -0.75989 | 121.5912 | 121.55 | 121.5088 | -0.97504 | 121.5683 | 121.55 | 121.5683 | -0.92011
6324.25 | 122.5662 | -121.4584 | 0.81024 | -0.0354 | 0.049332 | 0.060327 | 0.0053235 | 0.025056 | -0.011363 | 0.026374 | -0.0088499 | 0.010816 | 0.024705 | 0.034075 | -0.0030271 | 0.016464 | 0.022888 | 0.10071 | 0.068665 | 0.068665 | 0.086975 | 0.032043 | -0.09613 | 0.1236 | 0.14648 | 0.054932 | 0.054932 | 0.050354 | -0.032043 | -0.068665 | 121.4905 | 121.3623 | -0.72327 | 121.5591 | 121.5271 | 0.16479 | -0.78735 | 121.4264 | 121.3898 | -0.75531 | 121.582 | 121.5134 | 0.1236 | -0.75989 | 121.5454 | 121.4813 | 121.5271 | -0.90637 | 121.5134 | 121.5088 | 121.6049 | -0.87891
6325.9531 | 122.5342 | -121.4676 | 0.78278 | 0.12482 | 0.048691 | 0.059686 | 0.0021191 | 0.028901 | -0.0023904 | 0.027015 | 0.18951 | 0.012952 | 0.022142 | 0.035998 | 0.0029543 | 0.017532 | 0.11444 | 0.1236 | 0.10071 | 0.082397 | 0.068665 | 0.036621 | -0.10071 | 0.15106 | 0.13733 | 0.045776 | 0.032043 | 0.041199 | -0.009155 | -0.073242 | 121.5042 | 121.3669 | -0.71411 | 121.5912 | 121.55 | 0.18311 | -0.66834 | 121.4584 | 121.3943 | -0.75073 | 121.6187 | 121.5134 | 0.11902 | -0.74158 | 121.5363 | 121.582 | 121.5683 | -0.88348 | 121.4996 | 121.5088 | 121.6049 | -0.85602
6327.6562 | 122.58 | -121.4355 | 0.80109 | -0.058289 | 0.0457 | 0.060968 | 0.0044691 | 0.025056 | -0.0085856 | 0.024665 | -0.062256 | 0.01167 | 0.024919 | 0.034502 | -0.00024989 | 0.017746 | 0.045776 | 0.10529 | 0.091553 | 0.059509 | 0.086975 | 0.036621 | -0.12817 | 0.13275 | 0.14191 | 0.068665 | 0.027466 | 0.022888 | -0.032043 | -0.082397 | 121.4722 | 121.3074 | -0.71411 | 121.5408 | 121.4951 | 0.18768 | -0.75531 | 121.4035 | 121.3531 | -0.77362 | 121.5683 | 121.5042 | 0.15106 | -0.7782 | 121.5225 | 121.4813 | 121.5271 | -0.92926 | 121.463 | 121.4584 | 121.5775 | -0.88348
6329.3906 | 122.5662 | -121.463 | 0.80109 | -0.012512 | 0.046128 | 0.060327 | 0.0023329 | 0.025483 | -0.006663 | 0.025947 | -0.016479 | 0.01167 | 0.02321 | 0.033221 | 0.00081811 | 0.0186 | 0.032043 | 0.064087 | 0.068665 | 0.045776 | 0.086975 | 0.050354 | -0.13275 | 0.10986 | 0.10529 | 0.045776 | 0.036621 | 0.032043 | -0.022888 | -0.07782 | 121.5134 | 121.3303 | -0.71411 | 121.5271 | 121.5088 | 0.17853 | -0.76904 | 121.4401 | 121.3852 | -0.76446 | 121.5729 | 121.5088 | 0.1236 | -0.76904 | 121.55 | 121.4951 | 121.5317 | -0.93384 | 121.4996 | 121.4951 | 121.5683 | -0.87891
6331.0938 | 122.5067 | -121.4584 | 0.81482 | 0.079041 | 0.045914 | 0.060541 | 0.0027601 | 0.024842 | -0.0036722 | 0.025306 | 0.082703 | 0.011029 | 0.021074 | 0.034502 | 0.00081811 | 0.017318 | 0.09613 | 0.11444 | 0.086975 | 0.059509 | 0.064087 | 0.045776 | -0.11902 | 0.12817 | 0.09613 | 0.009155 | 0.045776 | 0.036621 | -0.022888 | -0.086975 | 121.5042 | 121.3394 | -0.75073 | 121.5729 | 121.5179 | 0.17853 | -0.71869 | 121.4355 | 121.3715 | -0.76904 | 121.5866 | 121.4676 | 0.09613 | -0.7782 | 121.5225 | 121.5546 | 121.5454 | -0.93384 | 121.5042 | 121.4951 | 121.5546 | -0.90179
6332.7969 | 122.4243 | -121.4859 | 0.83771 | -0.020142 | 0.049973 | 0.057977 | -0.0017261 | 0.02591 | 0.004659 | 0.028724 | -0.024109 | 0.013806 | 0.022142 | 0.036425 | 0.0053043 | 0.013473 | 0.064087 | 0.009155 | 0.009155 | 0.004578 | 0.11902 | 0.027466 | -0.15106 | 0.032043 | -0.009155 | -0.11902 | 0.082397 | 0.07782 | -0.059509 | -0.11444 | 121.5134 | 121.3348 | -0.71869 | 121.4951 | 121.4905 | 0.15564 | -0.77362 | 121.4264 | 121.3715 | -0.75531 | 121.5179 | 121.3669 | -0.004578 | -0.75989 | 121.6049 | 121.55 | 121.4951 | -0.98877 | 121.5683 | 121.5637 | 121.4767 | -0.95215
6334.5156 | 122.5571 | -121.4493 | 0.80109 | 0.14008 | 0.049759 | 0.056055 | 0.0010511 | 0.028047 | -0.0017496 | 0.030219 | 0.090332 | 0.013806 | 0.025987 | 0.035998 | 0.0035953 | 0.017105 | 0.086975 | 0.10986 | 0.082397 | 0.054932 | 0.09613 | 0.036621 | -0.11444 | 0.14191 | 0.12817 | 0.027466 | 0.041199 | 0.041199 | -0.027466 | -0.07782 | 121.4859 | 121.3348 | -0.70496 | 121.5591 | 121.5042 | 0.16937 | -0.71411 | 121.4218 | 121.3715 | -0.75989 | 121.5912 | 121.4767 | 0.10529 | -0.75989 | 121.5454 | 121.5363 | 121.5317 | -0.91553 | 121.4905 | 121.4905 | 121.5775 | -0.87891
6336.2188 | 122.4289 | -121.4813 | 0.81024 | 0.033264 | 0.052109 | 0.057336 | 0.0036145 | 0.027619 | -0.0019632 | 0.028937 | -0.0088499 | 0.013806 | 0.024705 | 0.037493 | 0.0038089 | 0.016677 | 0.022888 | -0.022888 | -0.041199 | 0.004578 | 0.11444 | 0 | -0.14648 | 0 | -0.013733 | -0.1236 | 0.091553 | 0.07782 | -0.064087 | -0.11444 | 121.4813 | 121.3348 | -0.6958 | 121.4584 | 121.4859 | 0.15106 | -0.78735 | 121.4172 | 121.3669 | -0.71869 | 121.4813 | 121.3577 | -0.009155 | -0.73242 | 121.5958 | 121.5042 | 121.4401 | -0.95673 | 121.5729 | 121.5591 | 121.4676 | -0.92468
6337.9375 | 122.3969 | -121.4996 | 0.82855 | -0.0354 | 0.051041 | 0.05755 | 0.0027601 | 0.029328 | 0.00017302 | 0.030219 | -0.054626 | 0.013806 | 0.024278 | 0.037066 | 0.0027407 | 0.016677 | 0.032043 | 0.027466 | 0.004578 | 0.013733 | 0.11444 | 0.004578 | -0.15564 | 0.041199 | 0.032043 | -0.10071 | 0.086975 | 0.059509 | -0.036621 | -0.11444 | 121.5042 | 121.344 | -0.71411 | 121.5271 | 121.5134 | 0.16937 | -0.79651 | 121.463 | 121.3852 | -0.74158 | 121.5408 | 121.3989 | 0.013733 | -0.76904 | 121.6141 | 121.5317 | 121.5042 | -0.98419 | 121.5866 | 121.5591 | 121.5317 | -0.94299
6339.6562 | 122.5388 | -121.4767 | 0.7782 | 0.071411 | 0.049118 | 0.059473 | 0.0025465 | 0.028474 | -0.0023904 | 0.027869 | 0.097962 | 0.012952 | 0.022142 | 0.034929 | 0.0042361 | 0.016891 | 0.013733 | 0.009155 | -0.036621 | 0 | 0.13275 | 0.004578 | -0.13275 | 0.050354 | 0.036621 | -0.064087 | 0.07782 | 0.068665 | -0.027466 | -0.09613 | 121.4813 | 121.344 | -0.64545 | 121.4859 | 121.4767 | 0.13275 | -0.76446 | 121.4493 | 121.3806 | -0.70038 | 121.5271 | 121.4127 | 0.032043 | -0.70953 | 121.6095 | 121.4905 | 121.4401 | -0.91095 | 121.5546 | 121.5454 | 121.5134 | -0.87433
6341.3594 | 122.4747 | -121.5179 | 0.80566 | -0.11169 | 0.050827 | 0.056696 | 0.0036145 | 0.027833 | 0.00017302 | 0.029365 | -0.11566 | 0.014661 | 0.022783 | 0.03792 | 0.0033817 | 0.017318 | 0.054932 | 0.059509 | 0.027466 | 0.036621 | 0.11444 | -0.009155 | -0.15106 | 0.091553 | 0.09613 | -0.036621 | 0.086975 | 0.054932 | -0.050354 | -0.10986 | 121.5088 | 121.3669 | -0.69122 | 121.5775 | 121.5546 | 0.18768 | -0.75073 | 121.4676 | 121.4081 | -0.71869 | 121.6095 | 121.4813 | 0.073242 | -0.75073 | 121.6324 | 121.5729 | 121.5454 | -0.95673 | 121.6049 | 121.5729 | 121.6141 | -0.91553
6343.0625 | 122.5845 | -121.4722 | 0.80109 | -0.088806 | 0.047837 | 0.058405 | 0.0063917 | 0.025056 | -0.010935 | 0.027869 | -0.062256 | 0.009534 | 0.02556 | 0.033861 | -0.0043087 | 0.016891 | 0.059509 | 0.1236 | 0.091553 | 0.07782 | 0.082397 | 0.027466 | -0.10071 | 0.13733 | 0.17395 | 0.068665 | 0.059509 | 0.032043 | -0.027466 | -0.086975 | 121.4996 | 121.3715 | -0.71869 | 121.5958 | 121.55 | 0.17853 | -0.74158 | 121.4447 | 121.3852 | -0.74158 | 121.6095 | 121.5408 | 0.15564 | -0.76904 | 121.5546 | 121.5317 | 121.5637 | -0.90179 | 121.5317 | 121.5042 | 121.6461 | -0.88806
6344.7656 | 122.5296 | -121.4722 | 0.78278 | 0.13245 | 0.049759 | 0.058405 | -0.0015125 | 0.025697 | -0.0064492 | 0.02851 | 0.16663 | 0.010175 | 0.021074 | 0.037066 | 0.0029543 | 0.0186 | 0.086975 | 0.10986 | 0.10986 | 0.073242 | 0.064087 | 0.041199 | -0.10071 | 0.16022 | 0.14191 | 0.064087 | 0.054932 | 0.045776 | -0.032043 | -0.082397 | 121.5134 | 121.3715 | -0.71869 | 121.582 | 121.5454 | 0.17395 | -0.6958 | 121.4401 | 121.3898 | -0.72784 | 121.6324 | 121.5363 | 0.14648 | -0.737 | 121.5363 | 121.5591 | 121.582 | -0.88348 | 121.5271 | 121.5179 | 121.6141 | -0.86517
6346.5 | 122.5708 | -121.4767 | 0.80566 | -0.073547 | 0.046341 | 0.060754 | 0.0023329 | 0.029542 | -0.0092264 | 0.024024 | -0.046997 | 0.011029 | 0.021928 | 0.033861 | 0.00081811 | 0.019027 | 0.054932 | 0.10071 | 0.09613 | 0.064087 | 0.10529 | 0.013733 | -0.10529 | 0.16022 | 0.16022 | 0.073242 | 0.045776 | 0.032043 | -0.018311 | -0.091553 | 121.4905 | 121.3715 | -0.70038 | 121.5775 | 121.5408 | 0.16937 | -0.75073 | 121.4584 | 121.3852 | -0.75989 | 121.637 | 121.55 | 0.16479 | -0.77362 | 121.582 | 121.5317 | 121.5729 | -0.91095 | 121.5225 | 121.5088 | 121.637 | -0.89722
6348.2188 | 122.4655 | -121.5042 | 0.8194 | -0.12695 | 0.049759 | 0.060327 | 0.00041005 | 0.027406 | 0.00038662 | 0.025519 | -0.15381 | 0.015302 | 0.021501 | 0.037493 | 0.0061587 | 0.014968 | 0.09613 | 0.054932 | 0.009155 | 0.036621 | 0.13275 | 0.009155 | -0.14191 | 0.082397 | 0.086975 | -0.041199 | 0.068665 | 0.064087 | -0.045776 | -0.086975 | 121.5134 | 121.3623 | -0.68665 | 121.5591 | 121.5408 | 0.17853 | -0.72327 | 121.4584 | 121.4172 | -0.75073 | 121.5866 | 121.463 | 0.045776 | -0.75531 | 121.637 | 121.6003 | 121.5134 | -0.9613 | 121.5729 | 121.5683 | 121.5912 | -0.90637
6349.9219 | 122.5662 | -121.4722 | 0.80109 | -0.14221 | 0.046341 | 0.062036 | 0.0063917 | 0.026124 | -0.0079446 | 0.025519 | -0.077515 | 0.012097 | 0.024919 | 0.035143 | -0.00067729 | 0.017318 | 0.11444 | 0.15564 | 0.13733 | 0.09613 | 0.082397 | 0.032043 | -0.10529 | 0.15106 | 0.17395 | 0.064087 | 0.036621 | 0.027466 | -0.027466 | -0.068665 | 121.5042 | 121.3669 | -0.71869 | 121.6278 | 121.5683 | 0.20142 | -0.68664 | 121.4447 | 121.4035 | -0.76446 | 121.6232 | 121.5363 | 0.13275 | -0.77362 | 121.5546 | 121.5866 | 121.6095 | -0.90637 | 121.5088 | 121.4996 | 121.6461 | -0.86975
6351.6406 | 122.4884 | -121.5088 | 0.82398 | -0.15747 | 0.052536 | 0.057336 | 0.0044691 | 0.02527 | -0.002604 | 0.026801 | -0.26062 | 0.013379 | 0.025346 | 0.038134 | 0.0020999 | 0.0139 | 0.032043 | -0.009155 | -0.009155 | 0.009155 | 0.13275 | 0.018311 | -0.15106 | 0.041199 | 0.064087 | -0.073242 | 0.082397 | 0.045776 | -0.064087 | -0.09613 | 121.5271 | 121.3577 | -0.69122 | 121.4996 | 121.5179 | 0.16022 | -0.79193 | 121.4447 | 121.4127 | -0.74158 | 121.55 | 121.4355 | 0.022888 | -0.7782 | 121.6415 | 121.5408 | 121.4996 | -0.97504 | 121.5912 | 121.5546 | 121.5729 | -0.9201
6353.3438 | 122.5662 | -121.4767 | 0.81482 | -0.14984 | 0.049973 | 0.060541 | 0.0070325 | 0.024201 | -0.0068766 | 0.025733 | -0.092773 | 0.011457 | 0.024492 | 0.034929 | -0.0019589 | 0.015823 | 0.10529 | 0.18768 | 0.15564 | 0.09613 | 0.09613 | 0.041199 | -0.12817 | 0.14648 | 0.19226 | 0.073242 | 0.059509 | 0.027466 | -0.013733 | -0.086975 | 121.5179 | 121.3486 | -0.71869 | 121.6644 | 121.5729 | 0.2243 | -0.70953 | 121.463 | 121.3898 | -0.75531 | 121.6232 | 121.55 | 0.16022 | -0.78735 | 121.5729 | 121.582 | 121.6324 | -0.94299 | 121.5363 | 121.5042 | 121.669 | -0.90179
6355.0469 | 122.5433 | -121.4584 | 0.79651 | 0.17059 | 0.047837 | 0.056482 | -0.00087155 | 0.027833 | -0.0023904 | 0.029578 | 0.13611 | 0.012311 | 0.021928 | 0.035784 | 0.0029543 | 0.01625 | 0.10986 | 0.13275 | 0.082397 | 0.073242 | 0.091553 | 0.041199 | -0.10986 | 0.14191 | 0.13275 | 0.041199 | 0.041199 | 0.027466 | 0 | -0.064087 | 121.4996 | 121.3486 | -0.70496 | 121.5912 | 121.5317 | 0.18311 | -0.68665 | 121.4584 | 121.3943 | -0.75531 | 121.6003 | 121.4996 | 0.10529 | -0.76904 | 121.55 | 121.5683 | 121.5408 | -0.90637 | 121.4996 | 121.4859 | 121.5912 | -0.8606
6356.7812 | 122.4518 | -121.5408 | 0.8194 | -0.18036 | 0.051255 | 0.061182 | 0.0048963 | 0.026551 | -0.0051676 | 0.027228 | -0.19196 | 0.012738 | 0.022356 | 0.034929 | -3.629e-05 | 0.016037 | 0.082397 | 0.13733 | 0.10529 | 0.073242 | 0.07782 | 0.027466 | -0.1236 | 0.09613 | 0.14648 | 0.013733 | 0.073242 | 0.054932 | -0.032043 | -0.086975 | 121.5683 | 121.4172 | -0.74158 | 121.6782 | 121.6141 | 0.19684 | -0.737 | 121.5088 | 121.4539 | -0.74616 | 121.637 | 121.5546 | 0.10071 | -0.76447 | 121.6187 | 121.6232 | 121.6461 | -0.94299 | 121.6141 | 121.5958 | 121.6873 | -0.90637
6358.5312 | 122.58 | -121.4722 | 0.77362 | 0.14008 | 0.048905 | 0.057764 | -0.0012987 | 0.026551 | 0.00060022 | 0.027228 | 0.12085 | 0.013593 | 0.021501 | 0.034289 | 0.0050907 | 0.016037 | 0.054932 | 0.059509 | 0.032043 | 0.027466 | 0.09613 | 0.032043 | -0.13733 | 0.14648 | 0.09613 | 0.018311 | 0.045776 | 0.036621 | -0.013733 | -0.068665 | 121.5042 | 121.3348 | -0.67749 | 121.5317 | 121.4996 | 0.16479 | -0.71869 | 121.4584 | 121.4035 | -0.72784 | 121.6187 | 121.4905 | 0.086976 | -0.737 | 121.5683 | 121.5271 | 121.5042 | -0.91095 | 121.5179 | 121.5088 | 121.5683 | -0.84229
6360.2344 | 122.4564 | -121.5317 | 0.81482 | -0.088806 | 0.049759 | 0.058405 | 0.0012647 | 0.026979 | -0.00025418 | 0.027869 | -0.14618 | 0.01402 | 0.024278 | 0.036425 | 0.0042361 | 0.016037 | 0.086975 | 0.068665 | 0.022888 | 0.032043 | 0.11902 | 0.009155 | -0.13733 | 0.073242 | 0.073242 | -0.045776 | 0.073242 | 0.041199 | -0.068665 | -0.10986 | 121.5408 | 121.3943 | -0.6958 | 121.6003 | 121.5637 | 0.16937 | -0.72784 | 121.463 | 121.4218 | -0.74158 | 121.6049 | 121.4859 | 0.064087 | -0.77362 | 121.6507 | 121.6187 | 121.5546 | -0.95215 | 121.6049 | 121.5729 | 121.6049 | -0.92468
6361.9531 | 122.5845 | -121.4859 | 0.80109 | -0.14984 | 0.046768 | 0.059259 | 0.0029737 | 0.024842 | -0.0085856 | 0.027442 | -0.069885 | 0.011457 | 0.023637 | 0.035357 | -0.0011045 | 0.018173 | 0.09613 | 0.17395 | 0.12817 | 0.086975 | 0.091553 | 0.027466 | -0.1236 | 0.15564 | 0.19684 | 0.09613 | 0.050354 | 0.027466 | -0.018311 | -0.073242 | 121.5134 | 121.3623 | -0.70953 | 121.6599 | 121.5729 | 0.21057 | -0.70496 | 121.4676 | 121.4127 | -0.75073 | 121.6415 | 121.582 | 0.16937 | -0.77362 | 121.5775 | 121.582 | 121.6141 | -0.92468 | 121.5363 | 121.5134 | 121.6827 | -0.87433
6363.6719 | 122.5067 | -121.5271 | 0.82398 | -0.19562 | 0.052964 | 0.059686 | 0.0078871 | 0.026765 | -0.002604 | 0.027228 | -0.20721 | 0.01167 | 0.026414 | 0.035784 | 0.00017731 | 0.013687 | 0.009155 | 0 | -0.018311 | 0.013733 | 0.12817 | 0.004578 | -0.16022 | 0.027466 | 0.050354 | -0.082397 | 0.09613 | 0.068665 | -0.059509 | -0.12817 | 121.5317 | 121.3669 | -0.6958 | 121.5271 | 121.5408 | 0.17395 | -0.81482 | 121.4676 | 121.3989 | -0.72785 | 121.5546 | 121.4447 | 0.045777 | -0.75531 | 121.6553 | 121.5363 | 121.5088 | -0.98419 | 121.6232 | 121.5958 | 121.5775 | -0.95215
6365.375 | 122.5433 | -121.5179 | 0.78735 | 0.040894 | 0.045914 | 0.058618 | -0.0023669 | 0.031465 | -0.00944 | 0.02616 | 0.067444 | 0.009534 | 0.023851 | 0.033648 | 0.0012455 | 0.016891 | 0.036621 | 0.07782 | 0.068665 | 0.045776 | 0.09613 | 0.027466 | -0.1236 | 0.086975 | 0.082397 | 0.009155 | 0.041199 | 0.045776 | -0.041199 | -0.07782 | 121.5454 | 121.3943 | -0.69122 | 121.5958 | 121.5637 | 0.16937 | -0.75073 | 121.4767 | 121.4401 | -0.74616 | 121.6049 | 121.5271 | 0.086975 | -0.74158 | 121.6141 | 121.5546 | 121.5866 | -0.91095 | 121.5591 | 121.5637 | 121.6003 | -0.86517
6367.1094 | 122.5021 | -121.5225 | 0.80566 | -0.21851 | 0.050186 | 0.057977 | 0.0046827 | 0.026765 | -0.001536 | 0.026588 | -0.21484 | 0.014234 | 0.025346 | 0.036211 | 0.0018863 | 0.016464 | 0.004578 | 0 | -0.022888 | 0.009155 | 0.11444 | 0.004578 | -0.15564 | 0.036621 | 0.050354 | -0.082397 | 0.086975 | 0.064087 | -0.059509 | -0.10071 | 121.5271 | 121.3669 | -0.69122 | 121.5225 | 121.5317 | 0.16479 | -0.80109 | 121.463 | 121.4218 | -0.71869 | 121.5591 | 121.4401 | 0.018311 | -0.74158 | 121.637 | 121.5271 | 121.4996 | -0.9613 | 121.6095 | 121.5866 | 121.5729 | -0.90637
6368.8125 | 122.4884 | -121.5317 | 0.81482 | -0.19562 | 0.048691 | 0.059259 | 0.0021191 | 0.026124 | -0.006663 | 0.029151 | -0.12329 | 0.010602 | 0.022783 | 0.035143 | 0.0010317 | 0.015182 | 0.064087 | 0.13733 | 0.11444 | 0.073242 | 0.09613 | 0.050354 | -0.10529 | 0.1236 | 0.16479 | 0.054932 | 0.041199 | 0.027466 | -0.041199 | -0.086975 | 121.582 | 121.4264 | -0.71869 | 121.669 | 121.6049 | 0.17853 | -0.75073 | 121.4905 | 121.4447 | -0.77362 | 121.6553 | 121.5866 | 0.14191 | -0.78735 | 121.6278 | 121.5958 | 121.6461 | -0.9201 | 121.5729 | 121.5591 | 121.6965 | -0.90179
6370.5625 | 122.4884 | -121.5408 | 0.82398 | -0.22614 | 0.052964 | 0.060541 | 0.0048963 | 0.026979 | -0.0028178 | 0.026588 | -0.25299 | 0.015302 | 0.025346 | 0.037279 | -3.629e-05 | 0.014541 | -0.009155 | 0.018311 | -0.013733 | 0 | 0.12817 | -0.009155 | -0.14648 | 0.022888 | 0.041199 | -0.073242 | 0.10071 | 0.07782 | -0.073242 | -0.11444 | 121.5317 | 121.3943 | -0.6958 | 121.5591 | 121.5408 | 0.14648 | -0.83313 | 121.4676 | 121.4264 | -0.72327 | 121.5637 | 121.4676 | 0.041199 | -0.74616 | 121.669 | 121.5317 | 121.5271 | -0.97046 | 121.6415 | 121.6187 | 121.582 | -0.93842
6372.2656 | 122.493 | -121.5454 | 0.81024 | -0.21088 | 0.051041 | 0.056482 | 0.0046827 | 0.027406 | -0.0023904 | 0.024665 | -0.19958 | 0.015302 | 0.025133 | 0.037493 | 0.0014591 | 0.015609 | 0.009155 | 0.004578 | -0.022888 | 0.022888 | 0.1236 | -0.009155 | -0.16022 | 0.032043 | 0.045776 | -0.068665 | 0.086975 | 0.068665 | -0.054932 | -0.11444 | 121.5363 | 121.3852 | -0.68665 | 121.55 | 121.5683 | 0.1831 | -0.80109 | 121.4905 | 121.431 | -0.72327 | 121.5775 | 121.4767 | 0.045776 | -0.74158 | 121.669 | 121.5546 | 121.5225 | -0.97046 | 121.6324 | 121.6141 | 121.5912 | -0.92468
6373.9688 | 122.6028 | -121.4996 | 0.76446 | -0.04303 | 0.046982 | 0.059259 | 0.0023329 | 0.026979 | -0.0087992 | 0.026374 | 0.014038 | 0.011457 | 0.022142 | 0.035357 | -0.00046349 | 0.017746 | 0.009155 | 0.091553 | 0.064087 | 0.045776 | 0.10986 | 0.032043 | -0.11902 | 0.11444 | 0.11902 | 0.045776 | 0.050354 | 0.032043 | -0.041199 | -0.073242 | 121.5317 | 121.3806 | -0.6546 | 121.5912 | 121.5454 | 0.16479 | -0.75531 | 121.4584 | 121.4264 | -0.71411 | 121.6141 | 121.5454 | 0.11902 | -0.73242 | 121.6095 | 121.5088 | 121.5637 | -0.88348 | 121.55 | 121.5317 | 121.6187 | -0.83771
6375.6719 | 122.5891 | -121.4859 | 0.78735 | 0.10193 | 0.050827 | 0.059045 | -1.7146e-05 | 0.024629 | 0.0012412 | 0.029792 | 0.11322 | 0.014875 | 0.021928 | 0.037493 | 0.0046633 | 0.015396 | 0.041199 | 0.009155 | -0.004578 | -0.004578 | 0.13733 | -0.009155 | -0.13733 | 0.086975 | 0.054932 | -0.027466 | 0.073242 | 0.041199 | -0.041199 | -0.091553 | 121.4767 | 121.3486 | -0.65002 | 121.4951 | 121.4813 | 0.13275 | -0.74616 | 121.4447 | 121.3943 | -0.71411 | 121.5729 | 121.4584 | 0.064087 | -0.74616 | 121.6232 | 121.5271 | 121.4813 | -0.92468 | 121.5591 | 121.5271 | 121.5408 | -0.87891
6377.375 | 122.58 | -121.5042 | 0.78735 | -0.14984 | 0.04805 | 0.060968 | 0.0059643 | 0.026338 | -0.0070902 | 0.027015 | -0.13855 | 0.011884 | 0.023851 | 0.036638 | -0.00024989 | 0.017105 | 0.086975 | 0.17395 | 0.11444 | 0.064087 | 0.09613 | 0.041199 | -0.1236 | 0.14648 | 0.18768 | 0.068665 | 0.054932 | 0.018311 | -0.018311 | -0.073242 | 121.5454 | 121.3806 | -0.69122 | 121.6782 | 121.5683 | 0.18768 | -0.70038 | 121.4859 | 121.431 | -0.73242 | 121.6507 | 121.5729 | 0.14191 | -0.76904 | 121.6003 | 121.5912 | 121.6187 | -0.91095 | 121.5591 | 121.5225 | 121.6919 | -0.8606
6379.125 | 122.493 | -121.5408 | 0.80109 | -0.20325 | 0.048905 | 0.060327 | 0.0051099 | 0.027192 | -0.0062356 | 0.027656 | -0.12329 | 0.011457 | 0.022996 | 0.033648 | 0.00081811 | 0.017532 | 0.09613 | 0.15564 | 0.10986 | 0.086975 | 0.082397 | 0.036621 | -0.10071 | 0.12817 | 0.16479 | 0.054932 | 0.045776 | 0.036621 | -0.022888 | -0.082397 | 121.5775 | 121.4401 | -0.71869 | 121.6965 | 121.6278 | 0.18768 | -0.70496 | 121.5179 | 121.4584 | -0.75531 | 121.669 | 121.5958 | 0.13733 | -0.76446 | 121.6232 | 121.637 | 121.6507 | -0.90179 | 121.5866 | 121.5775 | 121.7056 | -0.88348
6380.8281 | 122.5983 | -121.5042 | 0.7782 | -0.012512 | 0.04805 | 0.060968 | -0.00023075 | 0.025483 | -0.006663 | 0.025733 | 0.021668 | 0.01167 | 0.021501 | 0.035784 | 0.00060451 | 0.016677 | 0.013733 | 0.064087 | 0.050354 | 0.032043 | 0.10071 | 0.022888 | -0.11444 | 0.10529 | 0.09613 | 0.018311 | 0.050354 | 0.036621 | -0.050354 | -0.068665 | 121.5271 | 121.3898 | -0.67749 | 121.5683 | 121.5363 | 0.14648 | -0.76446 | 121.4539 | 121.4355 | -0.72784 | 121.6095 | 121.5225 | 0.086976 | -0.74158 | 121.6049 | 121.5179 | 121.5546 | -0.89264 | 121.5546 | 121.5408 | 121.6003 | -0.84686
6382.5938 | 122.5754 | -121.5454 | 0.79193 | -0.14984 | 0.047196 | 0.057123 | 0.0063917 | 0.027406 | -0.006022 | 0.025306 | -0.15381 | 0.01167 | 0.024919 | 0.036638 | 0.00081811 | 0.018173 | 0.10529 | 0.15106 | 0.1236 | 0.068665 | 0.082397 | 0.022888 | -0.10986 | 0.16479 | 0.1831 | 0.059509 | 0.050354 | 0.022888 | -0.013733 | -0.068665 | 121.5683 | 121.4355 | -0.70953 | 121.6965 | 121.6141 | 0.17853 | -0.68665 | 121.5317 | 121.4767 | -0.74158 | 121.7102 | 121.6049 | 0.12817 | -0.76904 | 121.6278 | 121.6507 | 121.669 | -0.90179 | 121.5958 | 121.5683 | 121.7285 | -0.8606
6384.3438 | 122.5479 | -121.5363 | 0.78278 | 0.025635 | 0.046555 | 0.059686 | 0.0014783 | 0.028688 | -0.0075174 | 0.024024 | 0.014038 | 0.013593 | 0.022142 | 0.035998 | 0.00060451 | 0.017105 | 0.059509 | 0.07782 | 0.050354 | 0.045776 | 0.09613 | 0.018311 | -0.10986 | 0.10071 | 0.10071 | 0.013733 | 0.054932 | 0.032043 | -0.022888 | -0.086975 | 121.5546 | 121.4264 | -0.68665 | 121.6141 | 121.582 | 0.15564 | -0.72327 | 121.5134 | 121.4493 | -0.72784 | 121.637 | 121.55 | 0.10071 | -0.75073 | 121.6324 | 121.5958 | 121.5866 | -0.89264 | 121.5912 | 121.5683 | 121.637 | -0.86975
6386.0469 | 122.5845 | -121.4996 | 0.76904 | 0.025635 | 0.048477 | 0.057977 | -1.7146e-05 | 0.02591 | -0.00025418 | 0.029578 | 0.097962 | 0.015515 | 0.022142 | 0.035784 | 0.0057315 | 0.016037 | 0.1236 | 0.10071 | 0.082397 | 0.073242 | 0.09613 | 0.041199 | -0.09613 | 0.16022 | 0.13733 | 0.036621 | 0.054932 | 0.032043 | -0.018311 | -0.073242 | 121.5408 | 121.4035 | -0.67291 | 121.6003 | 121.5729 | 0.16937 | -0.64545 | 121.4813 | 121.4264 | -0.71411 | 121.6599 | 121.5363 | 0.10986 | -0.737 | 121.5958 | 121.6232 | 121.582 | -0.86517 | 121.5546 | 121.5317 | 121.637 | -0.84229
6387.7344 | 122.5845 | -121.5363 | 0.78278 | -0.13458 | 0.046341 | 0.060541 | 0.0034009 | 0.02591 | -0.006022 | 0.026588 | -0.16907 | 0.011884 | 0.022996 | 0.034716 | 0.00081811 | 0.018173 | 0.11902 | 0.18768 | 0.12817 | 0.09613 | 0.091553 | 0.045776 | -0.10986 | 0.14648 | 0.17395 | 0.073242 | 0.036621 | 0.018311 | -0.022888 | -0.064087 | 121.582 | 121.4264 | -0.69122 | 121.7239 | 121.6324 | 0.20599 | -0.66376 | 121.5134 | 121.4722 | -0.74616 | 121.6827 | 121.6095 | 0.13733 | -0.76447 | 121.6278 | 121.6553 | 121.6644 | -0.89264 | 121.5729 | 121.5546 | 121.7102 | -0.84686
6389.4531 | 122.58 | -121.5179 | 0.76904 | 0.048523 | 0.050186 | 0.058832 | -0.0012987 | 0.028047 | 0.0012412 | 0.026588 | 0.052185 | 0.013379 | 0.022569 | 0.03792 | 0.0057315 | 0.0139 | 0.050354 | 0 | -0.009155 | -0.004578 | 0.13275 | -0.004578 | -0.15106 | 0.091553 | 0.022888 | -0.045776 | 0.07782 | 0.054932 | -0.050354 | -0.10071 | 121.5134 | 121.3669 | -0.63629 | 121.5179 | 121.5134 | 0.14648 | -0.71869 | 121.4676 | 121.4172 | -0.69122 | 121.6095 | 121.4722 | 0.054932 | -0.71411 | 121.6507 | 121.5683 | 121.5088 | -0.92011 | 121.5958 | 121.5729 | 121.5408 | -0.86975
6391.1719 | 122.5204 | -121.5454 | 0.78735 | -0.14984 | 0.050827 | 0.0599 | 0.0042555 | 0.027192 | 0.00081382 | 0.029578 | -0.18433 | 0.015302 | 0.025987 | 0.038134 | 0.0050907 | 0.014114 | 0.073242 | 0.041199 | 0.018311 | 0.041199 | 0.12817 | 0.013733 | -0.13733 | 0.086975 | 0.09613 | -0.041199 | 0.073242 | 0.068665 | -0.054932 | -0.09613 | 121.5591 | 121.4081 | -0.65918 | 121.5866 | 121.5866 | 0.17853 | -0.71411 | 121.4905 | 121.4493 | -0.71411 | 121.6324 | 121.5042 | 0.054931 | -0.71869 | 121.6736 | 121.6187 | 121.5637 | -0.92468 | 121.6187 | 121.6141 | 121.6415 | -0.88348
6392.875 | 122.5983 | -121.4905 | 0.7782 | -0.073547 | 0.048477 | 0.059259 | 0.0046827 | 0.028901 | -0.008372 | 0.027656 | -0.10803 | 0.010175 | 0.024278 | 0.036852 | -0.0013181 | 0.017532 | 0.059509 | 0.1236 | 0.09613 | 0.059509 | 0.10071 | 0.018311 | -0.10071 | 0.15106 | 0.16937 | 0.082397 | 0.050354 | 0.018311 | -0.018311 | -0.082397 | 121.5088 | 121.3898 | -0.67749 | 121.6141 | 121.55 | 0.16022 | -0.71869 | 121.4722 | 121.4081 | -0.72784 | 121.6415 | 121.5729 | 0.16479 | -0.75989 | 121.5912 | 121.55 | 121.5866 | -0.87891 | 121.5408 | 121.5088 | 121.6599 | -0.86059
6394.5938 | 122.5571 | -121.5225 | 0.79651 | 0.079041 | 0.050186 | 0.058191 | 0.0042555 | 0.028688 | -0.004954 | 0.028937 | 0.11322 | 0.010816 | 0.024919 | 0.036211 | 0.0023135 | 0.016037 | 0.091553 | 0.11902 | 0.11902 | 0.068665 | 0.068665 | 0.045776 | -0.10529 | 0.15106 | 0.1236 | 0.036621 | 0.036621 | 0.036621 | -0.041199 | -0.064087 | 121.5683 | 121.4172 | -0.72784 | 121.6415 | 121.5912 | 0.17395 | -0.70496 | 121.4813 | 121.4584 | -0.75989 | 121.6736 | 121.5591 | 0.10071 | -0.75989 | 121.5912 | 121.6141 | 121.6415 | -0.9018 | 121.5591 | 121.5591 | 121.6461 | -0.8606
6396.2969 | 122.5983 | -121.5042 | 0.7782 | 0.056152 | 0.047409 | 0.060968 | -0.0012987 | 0.024415 | -0.0017496 | 0.028083 | 0.097962 | 0.014447 | 0.022569 | 0.034502 | 0.0055179 | 0.014968 | 0.032043 | 0.013733 | -0.013733 | -0.009155 | 0.12817 | 0 | -0.13733 | 0.09613 | 0.050354 | -0.027466 | 0.068665 | 0.054932 | -0.036621 | -0.07782 | 121.5042 | 121.3669 | -0.65002 | 121.5179 | 121.4951 | 0.12817 | -0.74615 | 121.4676 | 121.4264 | -0.70953 | 121.6003 | 121.4767 | 0.050354 | -0.72327 | 121.6324 | 121.5363 | 121.4905 | -0.91553 | 121.5729 | 121.5591 | 121.5546 | -0.85602
6398.0156 | 122.5983 | -121.5225 | 0.78735 | -0.088806 | 0.048477 | 0.058191 | 0.0027601 | 0.026765 | -0.0068766 | 0.026801 | -0.092773 | 0.010388 | 0.024705 | 0.034502 | 0.0010317 | 0.015823 | 0.073242 | 0.13733 | 0.10071 | 0.073242 | 0.091553 | 0.022888 | -0.10529 | 0.16479 | 0.17395 | 0.068665 | 0.036621 | 0.027466 | -0.045776 | -0.086975 | 121.5454 | 121.4172 | -0.6958 | 121.6599 | 121.5958 | 0.17853 | -0.71411 | 121.4767 | 121.4355 | -0.75073 | 121.6873 | 121.5912 | 0.15564 | -0.75989 | 121.6141 | 121.5958 | 121.6232 | -0.89264 | 121.5591 | 121.55 | 121.6965 | -0.87433
6399.7188 | 122.5479 | -121.5271 | 0.7782 | 0.08667 | 0.046341 | 0.058405 | -1.7146e-05 | 0.024629 | -0.0038858 | 0.026588 | 0.10559 | 0.010816 | 0.021928 | 0.034716 | 0.0035953 | 0.016037 | 0.10529 | 0.14191 | 0.10071 | 0.073242 | 0.07782 | 0.045776 | -0.10529 | 0.15106 | 0.10986 | 0.045776 | 0.045776 | 0.041199 | -0.041199 | -0.086975 | 121.5729 | 121.4218 | -0.70038 | 121.669 | 121.6003 | 0.17853 | -0.67291 | 121.4859 | 121.4401 | -0.73242 | 121.6782 | 121.5729 | 0.13275 | -0.737 | 121.6049 | 121.6324 | 121.6278 | -0.88348 | 121.5729 | 121.5683 | 121.637 | -0.86517
6401.4375 | 122.6166 | -121.5225 | 0.77362 | -0.050659 | 0.047409 | 0.060541 | 0.0034009 | 0.027833 | -0.0079446 | 0.024238 | -0.062256 | 0.011029 | 0.022996 | 0.035143 | 0.00060451 | 0.017746 | 0.054932 | 0.10529 | 0.091553 | 0.050354 | 0.091553 | 0.027466 | -0.11902 | 0.14191 | 0.15106 | 0.054932 | 0.059509 | 0.045776 | -0.027466 | -0.07782 | 121.55 | 121.4035 | -0.68207 | 121.6278 | 121.5729 | 0.16937 | -0.71869 | 121.4951 | 121.4447 | -0.71411 | 121.6644 | 121.5775 | 0.13275 | -0.72784 | 121.6141 | 121.5775 | 121.6141 | -0.89264 | 121.582 | 121.5683 | 121.6736 | -0.85144
6403.1406 | 122.5708 | -121.5179 | 0.78278 | 0.08667 | 0.050614 | 0.058405 | 0.0012647 | 0.024415 | 0.00060022 | 0.028724 | 0.0064086 | 0.01402 | 0.021501 | 0.035357 | 0.0061587 | 0.014968 | 0.022888 | -0.009155 | -0.022888 | 0.004578 | 0.1236 | 0.013733 | -0.12817 | 0.068665 | -0.009155 | -0.086975 | 0.086975 | 0.059509 | -0.045776 | -0.07782 | 121.5317 | 121.3898 | -0.65918 | 121.5088 | 121.5225 | 0.13275 | -0.75989 | 121.4722 | 121.4401 | -0.6958 | 121.5866 | 121.431 | -0.009155 | -0.72327 | 121.6415 | 121.5408 | 121.4951 | -0.91095 | 121.6049 | 121.5775 | 121.5088 | -0.8606
6404.8438 | 122.5571 | -121.5363 | 0.79193 | 0.10193 | 0.04506 | 0.056696 | 0.0027601 | 0.02527 | -0.0045266 | 0.028083 | 0.090332 | 0.012738 | 0.022569 | 0.036211 | 0.0020999 | 0.017959 | 0.082397 | 0.11902 | 0.091553 | 0.054932 | 0.073242 | 0.032043 | -0.10986 | 0.12817 | 0.10071 | 0.027466 | 0.041199 | 0.032043 | -0.027466 | -0.07782 | 121.5683 | 121.4264 | -0.71869 | 121.6553 | 121.5912 | 0.16479 | -0.70953 | 121.5088 | 121.4584 | -0.75073 | 121.6644 | 121.5637 | 0.10529 | -0.75989 | 121.6095 | 121.6187 | 121.6278 | -0.90179 | 121.5775 | 121.5683 | 121.637 | -0.86975
6406.6094 | 122.5479 | -121.5363 | 0.80109 | 0.094299 | 0.047837 | 0.057764 | 0.0029737 | 0.024629 | -0.0055948 | 0.027869 | 0.082703 | 0.01167 | 0.022996 | 0.034075 | 0.00060451 | 0.015823 | 0.10529 | 0.091553 | 0.082397 | 0.054932 | 0.068665 | 0.050354 | -0.10529 | 0.12817 | 0.10529 | 0.018311 | 0.050354 | 0.032043 | -0.013733 | -0.082397 | 121.5866 | 121.431 | -0.73242 | 121.6278 | 121.5912 | 0.16022 | -0.6958 | 121.5225 | 121.4539 | -0.75073 | 121.6644 | 121.5546 | 0.10071 | -0.76904 | 121.6049 | 121.6415 | 121.6187 | -0.90637 | 121.5866 | 121.5683 | 121.6415 | -0.88348
6408.3594 | 122.525 | -121.5591 | 0.80109 | -0.19562 | 0.050827 | 0.059686 | 0.0029737 | 0.029756 | 0.00017302 | 0.029365 | -0.23773 | 0.013593 | 0.025133 | 0.036852 | 0.0063723 | 0.0139 | 0.054932 | 0.018311 | 0 | 0.022888 | 0.11902 | 0.009155 | -0.15564 | 0.059509 | 0.073242 | -0.050354 | 0.073242 | 0.059509 | -0.054932 | -0.10071 | 121.5683 | 121.4035 | -0.68207 | 121.5775 | 121.582 | 0.17853 | -0.74615 | 121.5042 | 121.4584 | -0.72784 | 121.6187 | 121.5088 | 0.050354 | -0.74158 | 121.6782 | 121.6141 | 121.5591 | -0.95673 | 121.6324 | 121.6187 | 121.6324 | -0.90179
6410.0625 | 122.5662 | -121.5683 | 0.78735 | 0.094299 | 0.046341 | 0.0599 | 0.0012647 | 0.029969 | -0.0040994 | 0.027869 | 0.11322 | 0.012525 | 0.024278 | 0.035357 | 0.0027407 | 0.017746 | 0.091553 | 0.13733 | 0.091553 | 0.064087 | 0.086975 | 0.045776 | -0.11444 | 0.14191 | 0.1236 | 0.032043 | 0.045776 | 0.027466 | -0.036621 | -0.073242 | 121.6141 | 121.4539 | -0.70038 | 121.7056 | 121.6324 | 0.17853 | -0.6958 | 121.5317 | 121.4951 | -0.74158 | 121.7102 | 121.6003 | 0.10529 | -0.75989 | 121.6553 | 121.6599 | 121.6599 | -0.9018 | 121.6141 | 121.5958 | 121.6919 | -0.8606
6411.7656 | 122.5342 | -121.5454 | 0.79651 | 0.08667 | 0.049973 | 0.057123 | 0.0010511 | 0.026124 | -0.00025418 | 0.027869 | 0.036926 | 0.01402 | 0.023637 | 0.038561 | 0.0053043 | 0.015182 | 0.027466 | -0.022888 | -0.036621 | -0.013733 | 0.12817 | 0 | -0.14648 | 0.032043 | 0 | -0.07782 | 0.10071 | 0.041199 | -0.050354 | -0.10529 | 121.5454 | 121.3989 | -0.66834 | 121.5225 | 121.5317 | 0.13275 | -0.76904 | 121.4951 | 121.4401 | -0.6958 | 121.5775 | 121.4676 | 0.027466 | -0.75531 | 121.6736 | 121.5729 | 121.5088 | -0.94299 | 121.6461 | 121.5866 | 121.5454 | -0.9018
6413.4688 | 122.5754 | -121.5179 | 0.78278 | 0.13245 | 0.049546 | 0.058191 | 0.00041005 | 0.023988 | -0.0053812 | 0.030433 | 0.18188 | 0.01167 | 0.023637 | 0.034075 | 0.0038089 | 0.018386 | 0.10986 | 0.1236 | 0.10529 | 0.086975 | 0.068665 | 0.045776 | -0.11444 | 0.15106 | 0.12817 | 0.032043 | 0.041199 | 0.022888 | -0.036621 | -0.054932 | 121.5637 | 121.4035 | -0.71411 | 121.6415 | 121.6049 | 0.20142 | -0.67291 | 121.4813 | 121.463 | -0.74158 | 121.669 | 121.55 | 0.086975 | -0.75989 | 121.5866 | 121.6278 | 121.6232 | -0.89722 | 121.5591 | 121.5408 | 121.6461 | -0.83771
6415.1719 | 122.4976 | -121.5591 | 0.8194 | 0.033264 | 0.051041 | 0.059686 | 0.00062385 | 0.026979 | 0.00060022 | 0.027228 | 0.014038 | 0.014447 | 0.021074 | 0.038134 | 0.0046633 | 0.017318 | 0.022888 | -0.045776 | -0.045776 | -0.018311 | 0.14648 | 0.004578 | -0.14191 | 0.032043 | 0 | -0.09613 | 0.07782 | 0.064087 | -0.041199 | -0.10986 | 121.5637 | 121.4172 | -0.67291 | 121.5134 | 121.5408 | 0.1236 | -0.79651 | 121.5179 | 121.4493 | -0.74158 | 121.5912 | 121.463 | 0.013733 | -0.75531 | 121.7056 | 121.582 | 121.5134 | -0.9613 | 121.637 | 121.6232 | 121.5591 | -0.92926
6416.875 | 122.5204 | -121.5775 | 0.81024 | -0.24139 | 0.049546 | 0.059259 | 0.0078871 | 0.026338 | -0.0028178 | 0.027656 | -0.22247 | 0.013379 | 0.025346 | 0.036425 | 0.00060451 | 0.014968 | 0.004578 | -0.009155 | -0.013733 | 0 | 0.13733 | 0 | -0.16937 | 0.018311 | 0.036621 | -0.091553 | 0.07782 | 0.082397 | -0.045776 | -0.1236 | 121.5775 | 121.4081 | -0.67291 | 121.5683 | 121.5775 | 0.16937 | -0.80566 | 121.5317 | 121.4539 | -0.73242 | 121.5958 | 121.4859 | 0.032043 | -0.72785 | 121.7148 | 121.582 | 121.5637 | -0.97962 | 121.6553 | 121.6599 | 121.6141 | -0.93384
6418.5938 | 122.6166 | -121.5225 | 0.78735 | -0.0048827 | 0.046768 | 0.058618 | 0.0053235 | 0.026124 | -0.011363 | 0.025733 | -0.0012209 | 0.01167 | 0.022996 | 0.033648 | -0.0030271 | 0.017532 | 0.009155 | 0.10071 | 0.068665 | 0.045776 | 0.086975 | 0.013733 | -0.11902 | 0.1236 | 0.13275 | 0.054932 | 0.050354 | 0.041199 | -0.027466 | -0.073242 | 121.5363 | 121.4035 | -0.70038 | 121.6232 | 121.5683 | 0.16479 | -0.7782 | 121.4951 | 121.4493 | -0.737 | 121.6461 | 121.5775 | 0.12817 | -0.74616 | 121.6095 | 121.5317 | 121.5912 | -0.90637 | 121.5729 | 121.5637 | 121.6553 | -0.8606
6420.2969 | 122.6166 | -121.5179 | 0.76904 | 0.14771 | 0.048264 | 0.057123 | 0.00041005 | 0.026124 | -0.002604 | 0.02851 | 0.12085 | 0.012311 | 0.021501 | 0.036425 | 0.0048769 | 0.016891 | 0.059509 | 0.022888 | 0.032043 | 0.022888 | 0.10071 | 0.018311 | -0.13275 | 0.1236 | 0.10529 | 0.032043 | 0.050354 | 0.041199 | -0.036621 | -0.082397 | 121.5363 | 121.3852 | -0.66834 | 121.5408 | 121.5408 | 0.15564 | -0.70953 | 121.4813 | 121.4355 | -0.71869 | 121.6415 | 121.55 | 0.11444 | -0.72784 | 121.6187 | 121.5775 | 121.55 | -0.90179 | 121.5683 | 121.5591 | 121.6232 | -0.85144
6422 | 122.5342 | -121.5591 | 0.80566 | -0.24139 | 0.048905 | 0.059473 | 0.0042555 | 0.027192 | -0.0023904 | 0.026588 | -0.19958 | 0.013379 | 0.024278 | 0.036852 | 0.0014591 | 0.016037 | 0 | 0 | -0.018311 | 0.004578 | 0.12817 | -0.009155 | -0.16937 | 0.022888 | 0.054932 | -0.082397 | 0.091553 | 0.068665 | -0.059509 | -0.11444 | 121.55 | 121.3898 | -0.67749 | 121.5591 | 121.5637 | 0.17395 | -0.80566 | 121.4996 | 121.4447 | -0.71411 | 121.582 | 121.4767 | 0.032044 | -0.737 | 121.6873 | 121.5591 | 121.5408 | -0.97504 | 121.6507 | 121.6278 | 121.6141 | -0.92011
6423.7031 | 122.6212 | -121.5454 | 0.76446 | -0.14984 | 0.045914 | 0.059686 | 0.0031873 | 0.02527 | -0.0075174 | 0.025306 | -0.10803 | 0.012097 | 0.02321 | 0.034716 | -0.0019589 | 0.0186 | 0.09613 | 0.16937 | 0.1236 | 0.10071 | 0.086975 | 0.045776 | -0.086975 | 0.13733 | 0.17395 | 0.068665 | 0.045776 | 0.009155 | -0.027466 | -0.059509 | 121.5912 | 121.4584 | -0.67749 | 121.7148 | 121.6461 | 0.18768 | -0.66833 | 121.5179 | 121.4859 | -0.71869 | 121.6827 | 121.6141 | 0.12817 | -0.75531 | 121.6324 | 121.6415 | 121.669 | -0.85144 | 121.5912 | 121.5546 | 121.7194 | -0.82397
6425.4062 | 122.493 | -121.55 | 0.82855 | -0.073547 | 0.050827 | 0.060327 | -0.00087155 | 0.026124 | 0.0012412 | 0.026588 | -0.092773 | 0.014875 | 0.022783 | 0.035998 | 0.0055179 | 0.015396 | 0.082397 | 0.045776 | -0.009155 | 0.022888 | 0.10986 | 0.013733 | -0.13733 | 0.073242 | 0.045776 | -0.082397 | 0.064087 | 0.068665 | -0.054932 | -0.10071 | 121.5637 | 121.4127 | -0.71869 | 121.5958 | 121.5729 | 0.16022 | -0.74615 | 121.4951 | 121.4493 | -0.76446 | 121.6232 | 121.4676 | 0.018311 | -0.75989 | 121.6599 | 121.6324 | 121.5408 | -0.96588 | 121.6141 | 121.6187 | 121.5958 | -0.92926
6427.1094 | 122.5388 | -121.5363 | 0.82398 | -0.21851 | 0.053391 | 0.059045 | 0.0038281 | 0.027406 | -0.0038858 | 0.027228 | -0.19958 | 0.013166 | 0.026414 | 0.035998 | 0.0012455 | 0.01625 | 0.009155 | 0.004578 | -0.018311 | 0 | 0.12817 | -0.013733 | -0.15564 | 0.018311 | 0.045776 | -0.07782 | 0.082397 | 0.073242 | -0.050354 | -0.11902 | 121.5225 | 121.3806 | -0.6958 | 121.5408 | 121.5363 | 0.15564 | -0.81482 | 121.4859 | 121.4172 | -0.74158 | 121.5546 | 121.4584 | 0.041199 | -0.75073 | 121.6644 | 121.5454 | 121.5179 | -0.97962 | 121.6187 | 121.6095 | 121.582 | -0.94299
6428.8125 | 122.5616 | -121.5271 | 0.81024 | -0.19562 | 0.049759 | 0.060114 | 0.0046827 | 0.025697 | -0.0090128 | 0.026374 | -0.13855 | 0.010816 | 0.022356 | 0.035998 | 0.00017731 | 0.017318 | 0.07782 | 0.15106 | 0.1236 | 0.082397 | 0.10071 | 0.036621 | -0.11902 | 0.13275 | 0.1831 | 0.059509 | 0.032043 | 0.013733 | -0.032043 | -0.073242 | 121.5637 | 121.4081 | -0.70953 | 121.6782 | 121.6095 | 0.20142 | -0.73242 | 121.4951 | 121.4539 | -0.7782 | 121.6599 | 121.5866 | 0.13275 | -0.79651 | 121.6278 | 121.6049 | 121.6507 | -0.92926 | 121.5591 | 121.5408 | 121.7102 | -0.88348
6430.5625 | 122.5433 | -121.5408 | 0.82855 | -0.24139 | 0.049973 | 0.06225 | 0.0038281 | 0.025483 | -0.0028178 | 0.027869 | -0.23773 | 0.013166 | 0.024492 | 0.036852 | 0.0027407 | 0.016464 | 0.004578 | 0.004578 | -0.013733 | 0.004578 | 0.15564 | 0.004578 | -0.14191 | 0.009155 | 0.032043 | -0.07782 | 0.091553 | 0.059509 | -0.068665 | -0.1236 | 121.5454 | 121.3989 | -0.67291 | 121.5454 | 121.5454 | 0.14649 | -0.82397 | 121.4722 | 121.4172 | -0.737 | 121.55 | 121.463 | 0.045776 | -0.76904 | 121.6965 | 121.5454 | 121.5271 | -0.97046 | 121.6324 | 121.6003 | 121.5729 | -0.95215
6432.2656 | 122.5708 | -121.5363 | 0.79651 | 0.048523 | 0.046768 | 0.059473 | 0.0010511 | 0.024201 | -0.0064492 | 0.026588 | 0.082703 | 0.011243 | 0.022356 | 0.035143 | 0.0012455 | 0.017959 | 0.032043 | 0.10529 | 0.073242 | 0.041199 | 0.09613 | 0.032043 | -0.10529 | 0.09613 | 0.091553 | 0.027466 | 0.041199 | 0.036621 | -0.041199 | -0.10071 | 121.5683 | 121.431 | -0.70038 | 121.6415 | 121.5775 | 0.14649 | -0.76447 | 121.4951 | 121.4355 | -0.75531 | 121.6324 | 121.5637 | 0.12817 | -0.75989 | 121.6324 | 121.5683 | 121.6095 | -0.9018 | 121.5775 | 121.5729 | 121.6278 | -0.89722
6433.9688 | 122.5845 | -121.5134 | 0.80566 | 0.10956 | 0.051041 | 0.056696 | -0.0015125 | 0.026551 | -0.00046778 | 0.029365 | 0.036926 | 0.012952 | 0.02321 | 0.036852 | 0.0050907 | 0.017746 | 0.022888 | -0.004578 | -0.050354 | 0.004578 | 0.11444 | -0.009155 | -0.15106 | 0.054932 | 0.004578 | -0.07782 | 0.086975 | 0.050354 | -0.045776 | -0.10986 | 121.5042 | 121.3623 | -0.69122 | 121.5088 | 121.5179 | 0.15564 | -0.78278 | 121.4676 | 121.4035 | -0.71869 | 121.5683 | 121.4355 | 0.032043 | -0.75531 | 121.6278 | 121.5363 | 121.463 | -0.95673 | 121.6003 | 121.5637 | 121.5179 | -0.91553
6435.6875 | 122.5388 | -121.5271 | 0.82398 | -0.21088 | 0.051468 | 0.059045 | 0.0081007 | 0.026979 | -0.0019632 | 0.027869 | -0.20721 | 0.014234 | 0.027055 | 0.035784 | 0.0016727 | 0.015396 | 0.013733 | 0.009155 | 0 | 0.027466 | 0.12817 | -0.009155 | -0.13733 | 0.068665 | 0.091553 | -0.045776 | 0.09613 | 0.032043 | -0.050354 | -0.1236 | 121.5179 | 121.3898 | -0.6958 | 121.5363 | 121.5546 | 0.16479 | -0.81024 | 121.4767 | 121.4035 | -0.72785 | 121.5958 | 121.4813 | 0.07782 | -0.79193 | 121.6553 | 121.5408 | 121.5271 | -0.9613 | 121.6232 | 121.5591 | 121.6187 | -0.94757
6437.3906 | 122.6303 | -121.5042 | 0.78735 | -0.012512 | 0.04805 | 0.058405 | 0.0057507 | 0.025056 | -0.010081 | 0.027442 | 0.052185 | 0.010816 | 0.023851 | 0.035143 | -0.00046349 | 0.019455 | 0 | 0.068665 | 0.064087 | 0.032043 | 0.091553 | 0.027466 | -0.12817 | 0.082397 | 0.1236 | 0.036621 | 0.068665 | 0.022888 | -0.036621 | -0.091553 | 121.5317 | 121.376 | -0.6958 | 121.5729 | 121.5363 | 0.16022 | -0.78735 | 121.4676 | 121.4127 | -0.71869 | 121.5866 | 121.5408 | 0.12817 | -0.76447 | 121.5958 | 121.5042 | 121.5683 | -0.91553 | 121.5729 | 121.5271 | 121.6278 | -0.87891
6439.1406 | 122.5021 | -121.5591 | 0.81482 | 0.033264 | 0.0504 | 0.058832 | -1.7146e-05 | 0.02826 | 0.00017302 | 0.027442 | -0.024109 | 0.014234 | 0.025133 | 0.038347 | 0.0044497 | 0.015609 | 0.004578 | -0.018311 | -0.050354 | -0.009155 | 0.12817 | 0.004578 | -0.15564 | 0.022888 | -0.013733 | -0.10986 | 0.082397 | 0.068665 | -0.050354 | -0.11444 | 121.5637 | 121.4035 | -0.68664 | 121.5408 | 121.55 | 0.14649 | -0.81024 | 121.5088 | 121.4447 | -0.73242 | 121.582 | 121.4493 | 0.004578 | -0.74615 | 121.6873 | 121.5637 | 121.5088 | -0.97046 | 121.6415 | 121.6278 | 121.5454 | -0.92926
6440.8438 | 122.5067 | -121.5775 | 0.81482 | -0.18799 | 0.050614 | 0.059045 | 0.0068189 | 0.026765 | -0.007731 | 0.027656 | -0.16907 | 0.013379 | 0.025987 | 0.03557 | 0.00017731 | 0.017959 | 0.064087 | 0.11902 | 0.09613 | 0.082397 | 0.073242 | 0.041199 | -0.11444 | 0.10529 | 0.15106 | 0.022888 | 0.032043 | 0.054932 | -0.027466 | -0.091553 | 121.6187 | 121.463 | -0.74158 | 121.6965 | 121.6599 | 0.19684 | -0.75073 | 121.55 | 121.4859 | -0.78278 | 121.6827 | 121.6003 | 0.11444 | -0.75989 | 121.6507 | 121.6415 | 121.6736 | -0.92926 | 121.6095 | 121.6324 | 121.7285 | -0.90637
6442.5625 | 122.493 | -121.5729 | 0.82398 | -0.073547 | 0.049759 | 0.057123 | -0.00023075 | 0.027833 | -0.0011088 | 0.028297 | -0.062256 | 0.013593 | 0.02321 | 0.036852 | 0.0063723 | 0.016037 | 0.059509 | 0.041199 | -0.004578 | 0.018311 | 0.13275 | 0.004578 | -0.13275 | 0.045776 | 0.022888 | -0.10071 | 0.068665 | 0.073242 | -0.068665 | -0.10071 | 121.5775 | 121.4401 | -0.69122 | 121.6141 | 121.5912 | 0.15106 | -0.76447 | 121.5042 | 121.4722 | -0.75531 | 121.6187 | 121.4722 | 0 | -0.75073 | 121.7056 | 121.6324 | 121.5683 | -0.95673 | 121.6415 | 121.6461 | 121.5958 | -0.92468
6444.2656 | 122.5067 | -121.5866 | 0.83771 | -0.24902 | 0.0504 | 0.058618 | 0.0059643 | 0.026338 | -0.0070902 | 0.026801 | -0.19958 | 0.010816 | 0.026201 | 0.035998 | 0.00017731 | 0.017959 | 0 | 0.041199 | 0.013733 | 0.013733 | 0.11902 | 0.018311 | -0.13733 | 0.027466 | 0.059509 | -0.050354 | 0.082397 | 0.073242 | -0.073242 | -0.11444 | 121.6049 | 121.4493 | -0.71869 | 121.6278 | 121.6003 | 0.15106 | -0.83771 | 121.5134 | 121.4722 | -0.75531 | 121.6141 | 121.5363 | 0.064087 | -0.76447 | 121.7056 | 121.5866 | 121.6003 | -0.97504 | 121.669 | 121.6599 | 121.6461 | -0.95215
6445.9844 | 122.6257 | -121.5225 | 0.79193 | 0.10956 | 0.049973 | 0.057336 | -0.0010851 | 0.025056 | -0.002604 | 0.027869 | 0.12085 | 0.015088 | 0.021928 | 0.035784 | 0.0057315 | 0.016037 | 0.032043 | 0.022888 | -0.004578 | 0 | 0.1236 | 0.022888 | -0.13733 | 0.10529 | 0.068665 | 0.004578 | 0.064087 | 0.045776 | -0.022888 | -0.086975 | 121.5454 | 121.3852 | -0.66834 | 121.5454 | 121.5225 | 0.13733 | -0.75989 | 121.4996 | 121.4355 | -0.72784 | 121.6278 | 121.5271 | 0.091553 | -0.74616 | 121.6461 | 121.5546 | 121.5179 | -0.92926 | 121.5866 | 121.5683 | 121.5912 | -0.87891
6447.7031 | 122.6212 | -121.4996 | 0.79651 | 0.094299 | 0.049546 | 0.057764 | -1.7146e-05 | 0.026765 | -0.0028178 | 0.028937 | 0.11322 | 0.013379 | 0.021928 | 0.036638 | 0.0048769 | 0.019027 | 0.032043 | 0.004578 | -0.018311 | 0.004578 | 0.14648 | 0.004578 | -0.13733 | 0.07782 | 0.050354 | -0.013733 | 0.064087 | 0.059509 | -0.045776 | -0.073242 | 121.5042 | 121.3623 | -0.65003 | 121.5042 | 121.5042 | 0.14191 | -0.76447 | 121.4539 | 121.4264 | -0.73242 | 121.5775 | 121.4859 | 0.059509 | -0.737 | 121.6461 | 121.5317 | 121.4813 | -0.93384 | 121.5637 | 121.5591 | 121.55 | -0.86975
6449.4062 | 122.58 | -121.5363 | 0.80566 | 0.079041 | 0.047196 | 0.05755 | 0.0027601 | 0.026551 | -0.0070902 | 0.029365 | 0.15137 | 0.011457 | 0.023424 | 0.03557 | 0.00017731 | 0.017532 | 0.082397 | 0.11902 | 0.10986 | 0.050354 | 0.073242 | 0.036621 | -0.11444 | 0.13733 | 0.12817 | 0.045776 | 0.032043 | 0.036621 | -0.036621 | -0.082397 | 121.5729 | 121.4218 | -0.73242 | 121.6553 | 121.5866 | 0.16479 | -0.72327 | 121.4996 | 121.4539 | -0.77362 | 121.6736 | 121.582 | 0.12817 | -0.76904 | 121.6095 | 121.6187 | 121.6461 | -0.92011 | 121.5683 | 121.5729 | 121.6644 | -0.88806
6451.1094 | 122.644 | -121.4996 | 0.79651 | 0.12482 | 0.049118 | 0.057336 | -0.00023075 | 0.029115 | -0.0038858 | 0.024665 | 0.13611 | 0.014875 | 0.02086 | 0.035784 | 0.0055179 | 0.017532 | 0.041199 | 0.018311 | 0.004578 | 0.013733 | 0.09613 | 0.032043 | -0.12817 | 0.10986 | 0.086975 | 0 | 0.054932 | 0.050354 | -0.036621 | -0.068665 | 121.5317 | 121.3715 | -0.70038 | 121.5179 | 121.5134 | 0.14191 | -0.75531 | 121.463 | 121.431 | -0.74158 | 121.6095 | 121.4996 | 0.068665 | -0.74616 | 121.5958 | 121.5408 | 121.5042 | -0.92468 | 121.5546 | 121.55 | 121.5866 | -0.86517
6452.8125 | 122.5388 | -121.5729 | 0.84686 | -0.24139 | 0.048477 | 0.061182 | 0.0029737 | 0.028047 | -0.0045266 | 0.028297 | -0.2301 | 0.012952 | 0.026201 | 0.035784 | 0.0023135 | 0.016464 | 0.009155 | 0 | -0.032043 | -0.009155 | 0.13733 | 0 | -0.14648 | 0.009155 | 0.032043 | -0.082397 | 0.068665 | 0.082397 | -0.068665 | -0.11902 | 121.5729 | 121.4264 | -0.70953 | 121.5729 | 121.5637 | 0.13733 | -0.83771 | 121.5042 | 121.4539 | -0.7782 | 121.582 | 121.4905 | 0.036622 | -0.76447 | 121.7102 | 121.582 | 121.5408 | -0.99335 | 121.6415 | 121.6553 | 121.6049 | -0.96588
6454.5312 | 122.5571 | -121.5729 | 0.79651 | -0.18799 | 0.048905 | 0.058405 | 0.0014783 | 0.028047 | -0.004313 | 0.02616 | -0.22247 | 0.013379 | 0.020647 | 0.036638 | 0.0010317 | 0.016677 | 0.027466 | -0.009155 | -0.027466 | 0.022888 | 0.1236 | 0.013733 | -0.16479 | 0.036621 | 0.068665 | -0.054932 | 0.064087 | 0.07782 | -0.054932 | -0.10986 | 121.5866 | 121.4081 | -0.67291 | 121.5637 | 121.5958 | 0.18768 | -0.76904 | 121.5179 | 121.463 | -0.73242 | 121.6095 | 121.5179 | 0.054931 | -0.71869 | 121.6965 | 121.6003 | 121.5454 | -0.9613 | 121.637 | 121.6507 | 121.6415 | -0.90637
6456.2812 | 122.5204 | -121.5454 | 0.83771 | -0.24902 | 0.048477 | 0.058832 | 0.0053235 | 0.02527 | -0.0058084 | 0.027656 | -0.24536 | 0.014661 | 0.024065 | 0.036638 | 0.0016727 | 0.017532 | 0.004578 | -0.013733 | -0.018311 | -0.013733 | 0.11902 | -0.009155 | -0.16022 | 0.013733 | 0.027466 | -0.07782 | 0.086975 | 0.082397 | -0.073242 | -0.11444 | 121.5363 | 121.3852 | -0.71869 | 121.5317 | 121.5317 | 0.14648 | -0.83313 | 121.4722 | 121.431 | -0.75073 | 121.5591 | 121.4676 | 0.036621 | -0.75531 | 121.6644 | 121.55 | 121.5271 | -0.99792 | 121.6324 | 121.6278 | 121.5729 | -0.95215
6458.0469 | 122.5113 | -121.5775 | 0.83771 | -0.18799 | 0.049332 | 0.060114 | 0.0048963 | 0.026124 | -0.0064492 | 0.025947 | -0.14618 | 0.012097 | 0.023851 | 0.03557 | -0.00067729 | 0.016464 | 0.073242 | 0.1236 | 0.10986 | 0.059509 | 0.073242 | 0.032043 | -0.11444 | 0.09613 | 0.15106 | 0.022888 | 0.050354 | 0.045776 | -0.036621 | -0.091553 | 121.6095 | 121.463 | -0.76447 | 121.7011 | 121.637 | 0.17395 | -0.76447 | 121.5408 | 121.4859 | -0.78735 | 121.6736 | 121.6003 | 0.11444 | -0.79193 | 121.6507 | 121.6507 | 121.6873 | -0.95215 | 121.6278 | 121.6232 | 121.7285 | -0.92926
6459.75 | 122.644 | -121.5134 | 0.80109 | -0.012512 | 0.046982 | 0.060114 | 0.0042555 | 0.026551 | -0.0068766 | 0.026801 | 0.036926 | 0.011884 | 0.02321 | 0.033861 | 0.00060451 | 0.0186 | 0.032043 | 0.064087 | 0.059509 | 0.041199 | 0.09613 | 0.032043 | -0.1236 | 0.068665 | 0.091553 | 0.036621 | 0.054932 | 0.054932 | -0.045776 | -0.082397 | 121.5454 | 121.3898 | -0.70496 | 121.5775 | 121.5546 | 0.16479 | -0.76904 | 121.4676 | 121.431 | -0.74615 | 121.582 | 121.55 | 0.11902 | -0.74615 | 121.6095 | 121.5454 | 121.5729 | -0.92468 | 121.5683 | 121.5683 | 121.6049 | -0.88348
6461.4531 | 122.5113 | -121.5591 | 0.85144 | -0.18036 | 0.050827 | 0.056909 | 0.0044691 | 0.02826 | -0.004313 | 0.025306 | -0.2301 | 0.0082522 | 0.025987 | 0.033861 | -0.00024989 | 0.016037 | 0.086975 | 0.10986 | 0.086975 | 0.073242 | 0.086975 | 0.027466 | -0.13275 | 0.07782 | 0.1236 | -0.004578 | 0.059509 | 0.036621 | -0.045776 | -0.086975 | 121.5866 | 121.4264 | -0.76446 | 121.669 | 121.6324 | 0.20599 | -0.76446 | 121.5134 | 121.4722 | -0.79193 | 121.637 | 121.5546 | 0.082397 | -0.81482 | 121.6461 | 121.6461 | 121.6461 | -0.98419 | 121.6187 | 121.5958 | 121.6827 | -0.93841
6463.1562 | 122.6669 | -121.5271 | 0.80566 | -0.0354 | 0.048477 | 0.0599 | 0.0044691 | 0.026551 | -0.008372 | 0.025733 | -0.054626 | 0.008893 | 0.026201 | 0.034502 | -0.00067729 | 0.016037 | 0.054932 | 0.082397 | 0.07782 | 0.054932 | 0.09613 | 0.036621 | -0.11902 | 0.12817 | 0.14191 | 0.064087 | 0.050354 | 0.027466 | -0.032043 | -0.082397 | 121.5637 | 121.4081 | -0.70953 | 121.6095 | 121.582 | 0.17395 | -0.75073 | 121.4951 | 121.4447 | -0.75531 | 121.6553 | 121.5912 | 0.14648 | -0.7782 | 121.6232 | 121.582 | 121.6049 | -0.92468 | 121.5775 | 121.5546 | 121.669 | -0.88806
6464.8594 | 122.5891 | -121.5363 | 0.80566 | 0.14771 | 0.04506 | 0.059686 | -0.00065795 | 0.031037 | -0.003245 | 0.028083 | 0.12848 | 0.013166 | 0.020219 | 0.03557 | 0.0057315 | 0.015182 | 0.10986 | 0.11902 | 0.11902 | 0.073242 | 0.082397 | 0.045776 | -0.086975 | 0.16022 | 0.13733 | 0.050354 | 0.027466 | 0.013733 | -0.032043 | -0.064087 | 121.582 | 121.4493 | -0.72327 | 121.6553 | 121.6095 | 0.16022 | -0.6958 | 121.5042 | 121.4722 | -0.7782 | 121.6965 | 121.5866 | 0.11444 | -0.79193 | 121.6187 | 121.6461 | 121.6553 | -0.89264 | 121.5637 | 121.55 | 121.6736 | -0.86975
6466.6094 | 122.5525 | -121.6095 | 0.79193 | -0.12695 | 0.051255 | 0.059473 | 0.0029737 | 0.024842 | 0.00081382 | 0.02851 | -0.1767 | 0.014661 | 0.023637 | 0.037707 | 0.0067997 | 0.013046 | 0.07782 | 0.050354 | 0.022888 | 0.032043 | 0.11444 | -0.004578 | -0.14648 | 0.091553 | 0.086975 | -0.041199 | 0.082397 | 0.045776 | -0.059509 | -0.11444 | 121.6049 | 121.463 | -0.67749 | 121.6599 | 121.6415 | 0.17853 | -0.71411 | 121.55 | 121.4951 | -0.70953 | 121.7011 | 121.5683 | 0.073242 | -0.74616 | 121.7239 | 121.6873 | 121.6324 | -0.93841 | 121.6919 | 121.6553 | 121.6965 | -0.90637
6468.2969 | 122.644 | -121.5775 | 0.75531 | -0.11932 | 0.047196 | 0.059473 | 0.0031873 | 0.025697 | -0.007731 | 0.027228 | -0.092773 | 0.0073978 | 0.024492 | 0.03557 | -0.00067729 | 0.016891 | 0.086975 | 0.12817 | 0.11444 | 0.073242 | 0.086975 | 0.036621 | -0.11444 | 0.16479 | 0.17395 | 0.07782 | 0.036621 | 0.036621 | -0.027466 | -0.07782 | 121.6141 | 121.463 | -0.66834 | 121.7056 | 121.6507 | 0.18768 | -0.66834 | 121.55 | 121.4996 | -0.71869 | 121.7422 | 121.6553 | 0.15564 | -0.71869 | 121.6644 | 121.6644 | 121.6919 | -0.86975 | 121.6141 | 121.6141 | 121.7514 | -0.83313
6470 | 122.5891 | -121.5958 | 0.75989 | 0.033264 | 0.046768 | 0.058618 | 0.0014783 | 0.027192 | -0.0064492 | 0.027015 | 0.052185 | 0.012952 | 0.020647 | 0.035998 | 0.0016727 | 0.016677 | 0.059509 | 0.086975 | 0.064087 | 0.036621 | 0.091553 | 0.032043 | -0.10529 | 0.09613 | 0.10529 | 0.013733 | 0.050354 | 0.041199 | -0.013733 | -0.086975 | 121.6278 | 121.4905 | -0.66834 | 121.6827 | 121.6324 | 0.14191 | -0.70038 | 121.582 | 121.5088 | -0.70953 | 121.6919 | 121.6095 | 0.10071 | -0.71869 | 121.6873 | 121.6553 | 121.6599 | -0.86517 | 121.6461 | 121.637 | 121.7011 | -0.84686
6471.7188 | 122.525 | -121.6232 | 0.78278 | 0.033264 | 0.051468 | 0.057977 | -0.00044435 | 0.025697 | 0.0025228 | 0.02851 | -0.054626 | 0.014447 | 0.022142 | 0.037066 | 0.0078677 | 0.011764 | 0.045776 | -0.027466 | -0.054932 | -0.004578 | 0.13733 | 0 | -0.14648 | 0.018311 | 0 | -0.11902 | 0.082397 | 0.073242 | -0.068665 | -0.1236 | 121.6232 | 121.4767 | -0.64545 | 121.5958 | 121.6187 | 0.14191 | -0.737 | 121.5546 | 121.4996 | -0.70038 | 121.6415 | 121.5042 | 0.004577 | -0.70953 | 121.7606 | 121.669 | 121.5683 | -0.92926 | 121.7056 | 121.6965 | 121.6232 | -0.90637
6473.4219 | 122.5021 | -121.6278 | 0.78278 | -0.22614 | 0.052323 | 0.059473 | 0.0061781 | 0.02826 | -0.0036722 | 0.025519 | -0.20721 | 0.012738 | 0.024492 | 0.035998 | 0.00060451 | 0.01625 | 0 | 0.036621 | 0.009155 | 0 | 0.11902 | -0.004578 | -0.15564 | 0.032043 | 0.045776 | -0.068665 | 0.073242 | 0.073242 | -0.07782 | -0.10529 | 121.6232 | 121.4722 | -0.66376 | 121.6644 | 121.6278 | 0.15564 | -0.78278 | 121.55 | 121.5225 | -0.70953 | 121.6599 | 121.5591 | 0.036621 | -0.70953 | 121.7468 | 121.6278 | 121.637 | -0.93842 | 121.701 | 121.701 | 121.6736 | -0.88806
6475.125 | 122.5891 | -121.5866 | 0.77362 | -0.17273 | 0.0504 | 0.058405 | 0.0019055 | 0.027619 | -0.0081582 | 0.025519 | -0.15381 | 0.0099612 | 0.024065 | 0.033434 | -0.0013181 | 0.017746 | 0.091553 | 0.16022 | 0.11444 | 0.091553 | 0.091553 | 0.032043 | -0.11444 | 0.14191 | 0.1831 | 0.045776 | 0.041199 | 0.032043 | -0.013733 | -0.07782 | 121.6187 | 121.4722 | -0.68207 | 121.7468 | 121.6782 | 0.20599 | -0.68207 | 121.5729 | 121.5088 | -0.73242 | 121.7285 | 121.6324 | 0.1236 | -0.74158 | 121.6782 | 121.6782 | 121.701 | -0.88806 | 121.6278 | 121.6187 | 121.7697 | -0.85144
6476.8281 | 122.6166 | -121.5912 | 0.75989 | 0.033264 | 0.046341 | 0.060754 | 0.0012647 | 0.026979 | -0.0053812 | 0.024451 | 0.029297 | 0.012738 | 0.021287 | 0.034502 | 0.0014591 | 0.016677 | 0.027466 | 0.086975 | 0.064087 | 0.045776 | 0.07782 | 0.036621 | -0.10986 | 0.091553 | 0.091553 | 0.018311 | 0.068665 | 0.027466 | -0.027466 | -0.09613 | 121.6278 | 121.4813 | -0.68207 | 121.6782 | 121.637 | 0.15564 | -0.73242 | 121.5637 | 121.4951 | -0.69122 | 121.6827 | 121.6095 | 0.11444 | -0.73242 | 121.669 | 121.6187 | 121.6553 | -0.86975 | 121.6599 | 121.6187 | 121.6827 | -0.85602
6478.5938 | 122.644 | -121.5866 | 0.74158 | -0.1651 | 0.047623 | 0.059686 | 0.0034009 | 0.028047 | -0.007731 | 0.026801 | -0.10803 | 0.010175 | 0.025133 | 0.036638 | 0.00017731 | 0.016037 | 0.09613 | 0.14191 | 0.11444 | 0.068665 | 0.09613 | 0.018311 | -0.10986 | 0.16479 | 0.17395 | 0.082397 | 0.050354 | 0.027466 | -0.022888 | -0.068665 | 121.6049 | 121.4767 | -0.64545 | 121.7285 | 121.6553 | 0.17853 | -0.64545 | 121.5637 | 121.5179 | -0.69122 | 121.7514 | 121.669 | 0.15106 | -0.71411 | 121.6827 | 121.6827 | 121.701 | -0.85144 | 121.637 | 121.6141 | 121.7606 | -0.81024
6480.2969 | 122.612 | -121.5546 | 0.75989 | 0.14008 | 0.046768 | 0.057977 | -0.00087155 | 0.025483 | -0.0011088 | 0.02616 | 0.14374 | 0.014234 | 0.022142 | 0.034075 | 0.0063723 | 0.016037 | 0.13275 | 0.1236 | 0.10071 | 0.086975 | 0.07782 | 0.027466 | -0.10071 | 0.16937 | 0.14191 | 0.045776 | 0.050354 | 0.032043 | -0.032043 | -0.068665 | 121.582 | 121.4539 | -0.68207 | 121.6782 | 121.6415 | 0.18768 | -0.62714 | 121.5225 | 121.4859 | -0.70953 | 121.7239 | 121.6003 | 0.11444 | -0.72784 | 121.6324 | 121.6873 | 121.6553 | -0.8606 | 121.6049 | 121.5866 | 121.6965 | -0.82855
6482 | 122.5662 | -121.6095 | 0.75531 | -0.18036 | 0.050186 | 0.060541 | 0.0048963 | 0.028474 | -0.00025418 | 0.028937 | -0.26825 | 0.015088 | 0.024705 | 0.034716 | 0.0027407 | 0.013473 | 0.041199 | 0 | -0.018311 | 0.018311 | 0.1236 | -0.004578 | -0.14648 | 0.064087 | 0.054932 | -0.054932 | 0.09613 | 0.059509 | -0.045776 | -0.10071 | 121.6049 | 121.463 | -0.63171 | 121.6095 | 121.6278 | 0.16479 | -0.71411 | 121.5637 | 121.5088 | -0.65918 | 121.6736 | 121.5546 | 0.045776 | -0.6958 | 121.7331 | 121.6507 | 121.5912 | -0.90179 | 121.7056 | 121.669 | 121.6644 | -0.85602
6483.75 | 122.5754 | -121.6232 | 0.75989 | 0.071411 | 0.048264 | 0.056909 | 0.0010511 | 0.025483 | 0.00060022 | 0.028083 | 0.067444 | 0.014234 | 0.022142 | 0.036425 | 0.0063723 | 0.017105 | 0.022888 | -0.018311 | -0.050354 | -0.004578 | 0.13275 | 0.004578 | -0.14191 | 0.032043 | -0.009155 | -0.091553 | 0.091553 | 0.091553 | -0.054932 | -0.10529 | 121.6278 | 121.4813 | -0.62714 | 121.6049 | 121.6187 | 0.13733 | -0.737 | 121.5683 | 121.5179 | -0.66834 | 121.6553 | 121.5317 | 0.013733 | -0.66834 | 121.756 | 121.6461 | 121.5729 | -0.9018 | 121.7148 | 121.7148 | 121.6141 | -0.86517
6485.4531 | 122.5662 | -121.6049 | 0.75989 | -0.14221 | 0.052323 | 0.057764 | 0.0040417 | 0.026338 | 0.001882 | 0.028724 | -0.14618 | 0.017224 | 0.022996 | 0.036852 | 0.0025271 | 0.015182 | 0.054932 | 0.050354 | 0.032043 | 0.050354 | 0.1236 | 0.004578 | -0.15106 | 0.091553 | 0.09613 | -0.032043 | 0.068665 | 0.054932 | -0.045776 | -0.086975 | 121.6095 | 121.4539 | -0.63629 | 121.6553 | 121.6553 | 0.20142 | -0.70496 | 121.5591 | 121.5179 | -0.69122 | 121.6965 | 121.5729 | 0.054932 | -0.70496 | 121.7285 | 121.6599 | 121.637 | -0.91095 | 121.6736 | 121.6599 | 121.701 | -0.84686
6487.1562 | 122.5296 | -121.6507 | 0.7782 | -0.1651 | 0.049546 | 0.059686 | 0.0048963 | 0.028047 | -0.0047404 | 0.028083 | -0.21484 | 0.013379 | 0.025133 | 0.036425 | 0.00017731 | 0.017105 | -0.013733 | 0.027466 | -0.009155 | 0.004578 | 0.1236 | -0.009155 | -0.13733 | 0.018311 | 0.054932 | -0.059509 | 0.082397 | 0.086975 | -0.07782 | -0.1236 | 121.6415 | 121.5134 | -0.6546 | 121.6782 | 121.6553 | 0.14191 | -0.79193 | 121.5729 | 121.5271 | -0.6958 | 121.669 | 121.5912 | 0.064087 | -0.69122 | 121.7743 | 121.637 | 121.6415 | -0.91553 | 121.7331 | 121.7377 | 121.7056 | -0.90179
6488.8594 | 122.6395 | -121.6278 | 0.74158 | 0.018005 | 0.048477 | 0.059045 | 0.0031873 | 0.026551 | -0.00944 | 0.028297 | 0.052185 | 0.010816 | 0.02321 | 0.033221 | -0.00024989 | 0.019668 | 0.009155 | 0.082397 | 0.050354 | 0.027466 | 0.091553 | 0.045776 | -0.13275 | 0.09613 | 0.091553 | 0.013733 | 0.045776 | 0.027466 | -0.032043 | -0.073242 | 121.6736 | 121.4951 | -0.65002 | 121.7102 | 121.6553 | 0.16022 | -0.73242 | 121.5958 | 121.5546 | -0.6958 | 121.7239 | 121.6415 | 0.086975 | -0.71411 | 121.7194 | 121.637 | 121.6782 | -0.87433 | 121.6736 | 121.6553 | 121.7194 | -0.81482
6490.625 | 122.6395 | -121.5912 | 0.75073 | 0.17059 | 0.049759 | 0.056268 | 0.0010511 | 0.024629 | -0.0030314 | 0.029151 | 0.12848 | 0.013379 | 0.021715 | 0.037066 | 0.0063723 | 0.014755 | 0.10529 | 0.1236 | 0.091553 | 0.086975 | 0.091553 | 0.059509 | -0.10071 | 0.15564 | 0.13275 | 0.054932 | 0.045776 | 0.032043 | -0.027466 | -0.068665 | 121.6507 | 121.4905 | -0.65918 | 121.7148 | 121.6782 | 0.18768 | -0.64545 | 121.5637 | 121.5225 | -0.70496 | 121.7468 | 121.6461 | 0.1236 | -0.71869 | 121.6827 | 121.6965 | 121.6827 | -0.85144 | 121.637 | 121.6232 | 121.7239 | -0.8194
6492.3281 | 122.5296 | -121.6507 | 0.75531 | -0.1651 | 0.050186 | 0.059045 | 0.0048963 | 0.026979 | -0.004313 | 0.02616 | -0.23773 | 0.011457 | 0.024919 | 0.036425 | 0.00081811 | 0.017746 | 0.004578 | 0.009155 | 0.004578 | -0.013733 | 0.13733 | 0.004578 | -0.16479 | 0.013733 | 0.045776 | -0.073242 | 0.09613 | 0.068665 | -0.068665 | -0.11902 | 121.6553 | 121.4859 | -0.61798 | 121.6599 | 121.637 | 0.15106 | -0.75073 | 121.582 | 121.5317 | -0.65918 | 121.6644 | 121.5775 | 0.045777 | -0.68665 | 121.788 | 121.6553 | 121.6553 | -0.92011 | 121.7468 | 121.7194 | 121.6965 | -0.87433
6494.0312 | 122.6578 | -121.6095 | 0.71869 | -0.11169 | 0.04506 | 0.061823 | 0.0019055 | 0.026551 | -0.0090128 | 0.027015 | -0.062256 | 0.011243 | 0.022996 | 0.034929 | -3.629e-05 | 0.017318 | 0.082397 | 0.13733 | 0.10529 | 0.086975 | 0.091553 | 0.027466 | -0.12817 | 0.15106 | 0.17853 | 0.073242 | 0.036621 | 0.041199 | -0.027466 | -0.059509 | 121.637 | 121.4813 | -0.62714 | 121.7468 | 121.6965 | 0.21515 | -0.63629 | 121.582 | 121.55 | -0.68207 | 121.7606 | 121.6827 | 0.13275 | -0.67749 | 121.7011 | 121.6919 | 121.7148 | -0.84686 | 121.6461 | 121.6507 | 121.788 | -0.7782
6495.7344 | 122.6303 | -121.6187 | 0.73242 | 0.12482 | 0.050827 | 0.058405 | -0.0017261 | 0.026338 | -0.0023904 | 0.025733 | 0.12848 | 0.013379 | 0.020219 | 0.034716 | 0.0067997 | 0.016677 | 0.13733 | 0.10529 | 0.086975 | 0.073242 | 0.091553 | 0.054932 | -0.11902 | 0.16022 | 0.14191 | 0.045776 | 0.041199 | 0.022888 | -0.027466 | -0.068665 | 121.6736 | 121.4996 | -0.64087 | 121.7239 | 121.6919 | 0.19226 | -0.59509 | 121.5912 | 121.55 | -0.69122 | 121.7789 | 121.6644 | 0.11444 | -0.70953 | 121.7102 | 121.756 | 121.7056 | -0.85144 | 121.6599 | 121.6415 | 121.7606 | -0.80109
6497.4375 | 122.5296 | -121.6461 | 0.76446 | -0.11169 | 0.051041 | 0.056696 | 0.0046827 | 0.025697 | 0.0016684 | 0.027442 | -0.16144 | 0.015088 | 0.021928 | 0.034929 | 0.0035953 | 0.016677 | 0.091553 | 0.050354 | 0.027466 | 0.036621 | 0.10529 | 0.013733 | -0.12817 | 0.091553 | 0.086975 | -0.045776 | 0.064087 | 0.050354 | -0.059509 | -0.086975 | 121.6599 | 121.5179 | -0.65918 | 121.6965 | 121.6827 | 0.1648 | -0.67291 | 121.5866 | 121.5591 | -0.70038 | 121.7377 | 121.6003 | 0.041199 | -0.71411 | 121.7514 | 121.7377 | 121.6736 | -0.89264 | 121.7102 | 121.6965 | 121.7331 | -0.85144
6499.1875 | 122.5479 | -121.6324 | 0.77362 | 0.018005 | 0.051255 | 0.059259 | 0.0038281 | 0.02591 | 0.00060022 | 0.030646 | 0.059815 | 0.016584 | 0.024065 | 0.03557 | 0.0029543 | 0.015396 | 0 | -0.036621 | -0.041199 | -0.027466 | 0.13275 | 0 | -0.13733 | 0.022888 | -0.013733 | -0.10071 | 0.09613 | 0.059509 | -0.059509 | -0.11444 | 121.6324 | 121.4951 | -0.64087 | 121.5958 | 121.6049 | 0.10986 | -0.77362 | 121.5729 | 121.5179 | -0.67749 | 121.6553 | 121.5317 | 0.013733 | -0.71411 | 121.7651 | 121.6324 | 121.5912 | -0.91095 | 121.7285 | 121.6919 | 121.6187 | -0.88806
6500.8906 | 122.58 | -121.6553 | 0.75531 | -0.19562 | 0.053177 | 0.056909 | 0.0040417 | 0.028047 | -0.0017496 | 0.02851 | -0.18433 | 0.015302 | 0.023637 | 0.036638 | 0.0033817 | 0.014755 | 0.018311 | 0.018311 | -0.004578 | 0.027466 | 0.11902 | 0.009155 | -0.15106 | 0.064087 | 0.073242 | -0.045776 | 0.068665 | 0.064087 | -0.059509 | -0.10986 | 121.6644 | 121.5042 | -0.63629 | 121.6736 | 121.6827 | 0.17853 | -0.737 | 121.5958 | 121.5454 | -0.68665 | 121.7194 | 121.6095 | 0.064087 | -0.69122 | 121.7743 | 121.6736 | 121.6507 | -0.90637 | 121.7239 | 121.7194 | 121.7285 | -0.86517
6502.6406 | 122.6715 | -121.6461 | 0.72327 | -0.10406 | 0.046341 | 0.061182 | 0.0046827 | 0.026979 | -0.010295 | 0.025733 | -0.062256 | 0.011243 | 0.024919 | 0.036211 | -0.0036679 | 0.019241 | 0.059509 | 0.14648 | 0.10529 | 0.082397 | 0.09613 | 0.022888 | -0.09613 | 0.15106 | 0.16937 | 0.07782 | 0.059509 | 0.027466 | -0.036621 | -0.086975 | 121.669 | 121.55 | -0.62714 | 121.7926 | 121.7285 | 0.17853 | -0.66376 | 121.6095 | 121.5591 | -0.66376 | 121.7972 | 121.7239 | 0.16479 | -0.6958 | 121.7422 | 121.7056 | 121.7514 | -0.8194 | 121.7056 | 121.6736 | 121.8155 | -0.81024
6504.3281 | 122.6532 | -121.637 | 0.72784 | -0.04303 | 0.047837 | 0.056696 | 0.0055371 | 0.02591 | -0.0092264 | 0.024665 | -0.0088499 | 0.011029 | 0.024919 | 0.037493 | -0.0025999 | 0.017959 | 0.045776 | 0.086975 | 0.082397 | 0.064087 | 0.07782 | 0.004578 | -0.10986 | 0.11902 | 0.13733 | 0.054932 | 0.045776 | 0.041199 | -0.009155 | -0.086975 | 121.6415 | 121.5271 | -0.65002 | 121.7239 | 121.701 | 0.17395 | -0.68207 | 121.6278 | 121.55 | -0.68207 | 121.756 | 121.6919 | 0.14191 | -0.68665 | 121.7148 | 121.6827 | 121.7194 | -0.83771 | 121.6827 | 121.6782 | 121.7743 | -0.81482
6506.0469 | 122.6212 | -121.6324 | 0.72327 | 0.14008 | 0.047623 | 0.056482 | 0.0010511 | 0.028474 | -0.0036722 | 0.027869 | 0.13611 | 0.01167 | 0.021501 | 0.03557 | 0.0065859 | 0.0186 | 0.10986 | 0.13733 | 0.10529 | 0.073242 | 0.082397 | 0.045776 | -0.10986 | 0.15564 | 0.13733 | 0.054932 | 0.050354 | 0.036621 | -0.009155 | -0.07782 | 121.6782 | 121.5225 | -0.64087 | 121.7697 | 121.7056 | 0.18311 | -0.6134 | 121.6232 | 121.5546 | -0.67291 | 121.788 | 121.6873 | 0.13275 | -0.68665 | 121.7148 | 121.7422 | 121.7377 | -0.83313 | 121.6827 | 121.669 | 121.7697 | -0.80109
6507.75 | 122.6349 | -121.6095 | 0.72327 | 0.11719 | 0.047409 | 0.057336 | -0.0015125 | 0.028474 | -0.004313 | 0.024451 | 0.15137 | 0.014661 | 0.02086 | 0.036425 | 0.0046633 | 0.017105 | 0.1236 | 0.1236 | 0.10071 | 0.10071 | 0.082397 | 0.022888 | -0.10986 | 0.16479 | 0.14191 | 0.041199 | 0.045776 | 0.032043 | -0.041199 | -0.073242 | 121.6324 | 121.4996 | -0.64087 | 121.7331 | 121.7102 | 0.21057 | -0.59967 | 121.5683 | 121.5363 | -0.67749 | 121.7743 | 121.6507 | 0.11444 | -0.69122 | 121.6919 | 121.7331 | 121.7102 | -0.83313 | 121.6553 | 121.6415 | 121.7514 | -0.79651
6509.4688 | 122.6486 | -121.6278 | 0.72784 | 0.079041 | 0.049332 | 0.059686 | 0.0012647 | 0.026338 | -0.00046778 | 0.027228 | 0.052185 | 0.015515 | 0.022356 | 0.035357 | 0.0063723 | 0.016037 | 0.036621 | -0.022888 | -0.036621 | -0.009155 | 0.1236 | 0 | -0.15106 | 0.073242 | 0.013733 | -0.064087 | 0.09613 | 0.07782 | -0.050354 | -0.10071 | 121.6278 | 121.4767 | -0.60425 | 121.6049 | 121.6187 | 0.14191 | -0.69122 | 121.5775 | 121.5271 | -0.63171 | 121.701 | 121.5637 | 0.036621 | -0.65002 | 121.7514 | 121.6644 | 121.5912 | -0.87891 | 121.7239 | 121.7056 | 121.6415 | -0.82855
6511.1875 | 122.58 | -121.6507 | 0.75531 | -0.23376 | 0.049546 | 0.058618 | 0.0031873 | 0.026765 | -0.0028178 | 0.025092 | -0.19196 | 0.013166 | 0.025133 | 0.03557 | 0.0020999 | 0.017105 | 0.018311 | -0.009155 | -0.018311 | 0.004578 | 0.1236 | -0.018311 | -0.14191 | 0.018311 | 0.041199 | -0.07782 | 0.091553 | 0.086975 | -0.059509 | -0.11444 | 121.6324 | 121.5088 | -0.63171 | 121.6415 | 121.6553 | 0.14649 | -0.737 | 121.5912 | 121.5363 | -0.66376 | 121.669 | 121.5729 | 0.036621 | -0.66834 | 121.7743 | 121.669 | 121.6324 | -0.89722 | 121.7422 | 121.7377 | 121.6919 | -0.86975
6512.8906 | 122.5388 | -121.669 | 0.75989 | -0.17273 | 0.049546 | 0.056696 | 0.0057507 | 0.028474 | -0.0062356 | 0.02851 | -0.1767 | 0.011884 | 0.026628 | 0.034929 | -0.00067729 | 0.015609 | 0.054932 | 0.1236 | 0.09613 | 0.068665 | 0.082397 | 0.041199 | -0.11902 | 0.10986 | 0.16022 | 0.036621 | 0.045776 | 0.054932 | -0.032043 | -0.091553 | 121.7102 | 121.55 | -0.67749 | 121.7926 | 121.7377 | 0.18768 | -0.70496 | 121.637 | 121.5775 | -0.71411 | 121.7789 | 121.7056 | 0.12817 | -0.70496 | 121.7514 | 121.7239 | 121.7651 | -0.87891 | 121.7148 | 121.7239 | 121.8292 | -0.85144
6514.6406 | 122.5296 | -121.6782 | 0.75989 | 0.048523 | 0.052323 | 0.057764 | -0.00065795 | 0.024629 | 0.00017302 | 0.028297 | -0.0012209 | 0.013593 | 0.021715 | 0.035357 | 0.0061587 | 0.016891 | 0.013733 | -0.022888 | -0.064087 | -0.013733 | 0.13275 | 0.004578 | -0.14648 | 0.018311 | -0.022888 | -0.10071 | 0.086975 | 0.059509 | -0.045776 | -0.11444 | 121.6827 | 121.5317 | -0.62714 | 121.6553 | 121.6644 | 0.13275 | -0.74616 | 121.6324 | 121.5637 | -0.67291 | 121.6965 | 121.5775 | 0.013733 | -0.70038 | 121.8109 | 121.6919 | 121.6141 | -0.90637 | 121.7651 | 121.7377 | 121.6553 | -0.87433
6516.3438 | 122.6395 | -121.6278 | 0.71869 | 0.063782 | 0.050614 | 0.057764 | 0.00083745 | 0.026765 | -0.0030314 | 0.029151 | 0.082703 | 0.013379 | 0.023424 | 0.037066 | 0.0048769 | 0.017105 | 0.004578 | 0.009155 | -0.009155 | 0.004578 | 0.11902 | 0 | -0.16022 | 0.07782 | 0.036621 | -0.045776 | 0.07782 | 0.050354 | -0.041199 | -0.10071 | 121.6278 | 121.4676 | -0.59967 | 121.637 | 121.6324 | 0.16479 | -0.71411 | 121.5866 | 121.5271 | -0.64087 | 121.7056 | 121.582 | 0.054932 | -0.66834 | 121.7468 | 121.6324 | 121.6187 | -0.87891 | 121.7056 | 121.6782 | 121.6644 | -0.8194
6518.0469 | 122.5388 | -121.6644 | 0.78735 | -0.096436 | 0.051682 | 0.056696 | 0.0048963 | 0.027192 | -0.0011088 | 0.029792 | -0.11566 | 0.013806 | 0.024705 | 0.036638 | 0.0053043 | 0.016677 | 0.068665 | 0.059509 | 0.027466 | 0.036621 | 0.1236 | 0.004578 | -0.14191 | 0.073242 | 0.07782 | -0.054932 | 0.064087 | 0.059509 | -0.059509 | -0.10529 | 121.669 | 121.5225 | -0.66376 | 121.7239 | 121.701 | 0.17853 | -0.71869 | 121.6049 | 121.5591 | -0.72327 | 121.7377 | 121.6095 | 0.050354 | -0.72784 | 121.788 | 121.7331 | 121.6919 | -0.92926 | 121.7285 | 121.7239 | 121.7422 | -0.89264
6519.7656 | 122.6212 | -121.6415 | 0.72784 | 0.033264 | 0.049973 | 0.060114 | 0.0034009 | 0.026765 | -0.0090128 | 0.027656 | 0.075073 | 0.012952 | 0.024919 | 0.033221 | -0.00024989 | 0.018386 | 0.022888 | 0.09613 | 0.07782 | 0.041199 | 0.086975 | 0.032043 | -0.11902 | 0.10071 | 0.091553 | 0.013733 | 0.064087 | 0.036621 | -0.036621 | -0.086975 | 121.6736 | 121.5225 | -0.64087 | 121.7377 | 121.6827 | 0.16022 | -0.70496 | 121.6049 | 121.5546 | -0.66376 | 121.7422 | 121.6553 | 0.10071 | -0.69122 | 121.7285 | 121.6644 | 121.7194 | -0.84686 | 121.7056 | 121.6782 | 121.7331 | -0.81482
6521.4688 | 122.5891 | -121.6827 | 0.74158 | -0.20325 | 0.048691 | 0.057336 | 0.0048963 | 0.027192 | -0.001536 | 0.026801 | -0.21484 | 0.015088 | 0.024278 | 0.03792 | 0.0029543 | 0.016464 | 0.027466 | 0.013733 | -0.022888 | 0.027466 | 0.11444 | 0.009155 | -0.16022 | 0.045776 | 0.086975 | -0.054932 | 0.07782 | 0.059509 | -0.059509 | -0.10529 | 121.6919 | 121.5225 | -0.62714 | 121.6965 | 121.7102 | 0.18768 | -0.71411 | 121.6232 | 121.5775 | -0.66376 | 121.7285 | 121.6278 | 0.050354 | -0.68207 | 121.7972 | 121.7102 | 121.6599 | -0.90179 | 121.7606 | 121.7422 | 121.7697 | -0.84686
6523.1719 | 122.5388 | -121.6827 | 0.75989 | -0.17273 | 0.050186 | 0.058405 | 0.0074597 | 0.02527 | -0.004954 | 0.025519 | -0.15381 | 0.0099612 | 0.026414 | 0.036211 | -0.0017453 | 0.017318 | 0.068665 | 0.12817 | 0.11444 | 0.082397 | 0.10071 | 0.018311 | -0.11902 | 0.091553 | 0.15106 | 0.018311 | 0.054932 | 0.032043 | -0.027466 | -0.091553 | 121.701 | 121.5637 | -0.65918 | 121.8109 | 121.7651 | 0.20142 | -0.69122 | 121.6553 | 121.5912 | -0.70496 | 121.7743 | 121.701 | 0.10986 | -0.72784 | 121.7834 | 121.7514 | 121.7972 | -0.87891 | 121.7377 | 121.7148 | 121.8338 | -0.85144
6524.9062 | 122.5754 | -121.6965 | 0.75531 | -0.22614 | 0.049973 | 0.058191 | 0.0053235 | 0.026551 | -0.0017496 | 0.026588 | -0.19958 | 0.012097 | 0.024705 | 0.033221 | 0.0016727 | 0.015396 | -0.009155 | 0.013733 | -0.032043 | 0.018311 | 0.12817 | -0.004578 | -0.15106 | 0.027466 | 0.032043 | -0.073242 | 0.091553 | 0.064087 | -0.068665 | -0.1236 | 121.6919 | 121.5454 | -0.62714 | 121.7102 | 121.7148 | 0.16937 | -0.76447 | 121.6278 | 121.5729 | -0.66376 | 121.7239 | 121.6232 | 0.050354 | -0.69122 | 121.8246 | 121.6873 | 121.6644 | -0.90637 | 121.788 | 121.7606 | 121.7285 | -0.87891
6526.6094 | 122.5616 | -121.6827 | 0.75531 | -0.26428 | 0.050614 | 0.059259 | 0.0066053 | 0.027192 | -0.0028178 | 0.024238 | -0.22247 | 0.01402 | 0.026201 | 0.037066 | 0.0018863 | 0.016891 | -0.032043 | 0.013733 | -0.022888 | 0.004578 | 0.14191 | -0.018311 | -0.13275 | 0.009155 | 0.022888 | -0.082397 | 0.10071 | 0.07782 | -0.054932 | -0.11444 | 121.6644 | 121.55 | -0.6134 | 121.6965 | 121.6873 | 0.13733 | -0.78735 | 121.6278 | 121.5683 | -0.6546 | 121.6919 | 121.6003 | 0.032044 | -0.67749 | 121.8246 | 121.6507 | 121.6599 | -0.88806 | 121.7834 | 121.7606 | 121.7056 | -0.86975
6528.3281 | 122.6395 | -121.6278 | 0.71869 | 0.14008 | 0.046982 | 0.058405 | 0.00019645 | 0.024629 | -0.0055948 | 0.026801 | 0.18188 | 0.0099612 | 0.024278 | 0.037279 | 0.0038089 | 0.017959 | 0.09613 | 0.12817 | 0.09613 | 0.086975 | 0.068665 | 0.032043 | -0.10529 | 0.14648 | 0.13275 | 0.050354 | 0.041199 | 0.022888 | -0.022888 | -0.082397 | 121.6599 | 121.5225 | -0.65002 | 121.756 | 121.7148 | 0.19226 | -0.62256 | 121.6049 | 121.5454 | -0.67749 | 121.7743 | 121.6782 | 0.13275 | -0.6958 | 121.6965 | 121.7239 | 121.7239 | -0.82398 | 121.669 | 121.6507 | 121.7606 | -0.80109
6530.0781 | 122.5342 | -121.6461 | 0.74616 | -0.020142 | 0.0551 | 0.059259 | 0.00041005 | 0.024842 | -0.00068138 | 0.028937 | -0.024109 | 0.014875 | 0.022783 | 0.037279 | 0.0061587 | 0.016891 | 0.032043 | 0 | -0.013733 | 0.004578 | 0.12817 | 0.018311 | -0.13275 | 0.022888 | 0.009155 | -0.10071 | 0.082397 | 0.054932 | -0.054932 | -0.10529 | 121.6644 | 121.5134 | -0.61798 | 121.6461 | 121.6507 | 0.13733 | -0.71411 | 121.5912 | 121.5408 | -0.66376 | 121.669 | 121.5454 | 0.004578 | -0.69122 | 121.7743 | 121.6782 | 121.6324 | -0.87891 | 121.7285 | 121.701 | 121.6553 | -0.85144
6531.7812 | 122.5662 | -121.7056 | 0.75073 | -0.1651 | 0.049759 | 0.056909 | 0.0072461 | 0.028047 | -0.0075174 | 0.02616 | -0.16907 | 0.012097 | 0.024278 | 0.037279 | 0.0012455 | 0.017746 | 0.045776 | 0.14648 | 0.09613 | 0.073242 | 0.086975 | 0.041199 | -0.11444 | 0.082397 | 0.15106 | 0.032043 | 0.054932 | 0.045776 | -0.032043 | -0.10071 | 121.7468 | 121.5912 | -0.66376 | 121.8521 | 121.7789 | 0.18768 | -0.70496 | 121.6736 | 121.6049 | -0.6958 | 121.788 | 121.7377 | 0.13275 | -0.70496 | 121.7926 | 121.7514 | 121.8018 | -0.86517 | 121.7606 | 121.7514 | 121.8567 | -0.85144
6533.5469 | 122.6532 | -121.6507 | 0.70038 | 0.071411 | 0.04805 | 0.056482 | -0.00065795 | 0.028688 | -0.003245 | 0.026588 | 0.14374 | 0.013806 | 0.02321 | 0.035998 | 0.0029543 | 0.017318 | 0.10529 | 0.11902 | 0.10071 | 0.086975 | 0.091553 | 0.027466 | -0.11902 | 0.14648 | 0.13275 | 0.045776 | 0.045776 | 0.018311 | 0 | -0.068665 | 121.6782 | 121.5317 | -0.60882 | 121.7697 | 121.7377 | 0.20599 | -0.59509 | 121.6507 | 121.582 | -0.6546 | 121.7972 | 121.6965 | 0.11444 | -0.68207 | 121.7422 | 121.756 | 121.7514 | -0.8194 | 121.6965 | 121.669 | 121.7834 | -0.76904
6535.2969 | 122.6761 | -121.6278 | 0.70953 | -0.012512 | 0.047409 | 0.059259 | 0.0027601 | 0.02826 | -0.007731 | 0.024879 | 0.044556 | 0.012097 | 0.021928 | 0.035998 | 0.0014591 | 0.015609 | 0.013733 | 0.059509 | 0.064087 | 0.045776 | 0.091553 | 0.041199 | -0.13733 | 0.10071 | 0.10529 | 0.032043 | 0.050354 | 0.036621 | -0.045776 | -0.086975 | 121.669 | 121.4905 | -0.61798 | 121.6873 | 121.6736 | 0.18311 | -0.6958 | 121.582 | 121.5408 | -0.65918 | 121.7285 | 121.6599 | 0.11902 | -0.67291 | 121.7194 | 121.6415 | 121.6919 | -0.84686 | 121.6782 | 121.6644 | 121.7331 | -0.79651
6537.0312 | 122.6669 | -121.6507 | 0.69122 | 0.14008 | 0.049332 | 0.056268 | -0.00087155 | 0.027619 | -0.0021768 | 0.027656 | 0.13611 | 0.01402 | 0.022142 | 0.03557 | 0.0057315 | 0.01625 | 0.059509 | 0.027466 | 0.018311 | 0.022888 | 0.1236 | 0.013733 | -0.11902 | 0.1236 | 0.091553 | 0.009155 | 0.059509 | 0.045776 | -0.022888 | -0.073242 | 121.6644 | 121.5317 | -0.56763 | 121.6782 | 121.6736 | 0.14191 | -0.63171 | 121.6278 | 121.5775 | -0.63171 | 121.7743 | 121.6599 | 0.082397 | -0.64545 | 121.7743 | 121.7102 | 121.669 | -0.81024 | 121.7102 | 121.6965 | 121.7422 | -0.76447
6538.7344 | 122.5845 | -121.6919 | 0.75531 | -0.11932 | 0.049973 | 0.0599 | 0.0010511 | 0.02591 | -0.00046778 | 0.029365 | -0.13855 | 0.016156 | 0.023637 | 0.035998 | 0.0046633 | 0.014541 | 0.086975 | 0.045776 | 0.018311 | 0.032043 | 0.13275 | 0.004578 | -0.13275 | 0.082397 | 0.082397 | -0.032043 | 0.09613 | 0.054932 | -0.041199 | -0.11444 | 121.6965 | 121.5591 | -0.62256 | 121.7377 | 121.7239 | 0.16479 | -0.66834 | 121.6507 | 121.5775 | -0.65918 | 121.7743 | 121.6599 | 0.082398 | -0.70038 | 121.8246 | 121.7789 | 121.7102 | -0.88806 | 121.788 | 121.7468 | 121.7743 | -0.86975
6540.4688 | 122.6578 | -121.6507 | 0.72784 | -0.14221 | 0.047837 | 0.058191 | 0.0070325 | 0.029542 | -0.0098672 | 0.025092 | -0.1004 | 0.011457 | 0.022356 | 0.035357 | -0.0028135 | 0.017746 | 0.10071 | 0.16937 | 0.13275 | 0.091553 | 0.091553 | 0.027466 | -0.10529 | 0.13275 | 0.18768 | 0.086975 | 0.045776 | 0.027466 | -0.013733 | -0.082397 | 121.6782 | 121.5454 | -0.63629 | 121.8201 | 121.7422 | 0.19684 | -0.62714 | 121.637 | 121.5683 | -0.68207 | 121.7834 | 121.7377 | 0.16937 | -0.70038 | 121.7422 | 121.7514 | 121.7834 | -0.83313 | 121.6965 | 121.6782 | 121.8384 | -0.81024
6542.1719 | 122.7081 | -121.6415 | 0.73242 | -0.058289 | 0.046128 | 0.0599 | 0.0025465 | 0.023133 | -0.0092264 | 0.025947 | -0.16144 | 0.011243 | 0.022569 | 0.034502 | -0.00046349 | 0.017532 | 0.054932 | 0.09613 | 0.07782 | 0.059509 | 0.091553 | 0.027466 | -0.11902 | 0.13275 | 0.15564 | 0.068665 | 0.054932 | 0.050354 | -0.018311 | -0.07782 | 121.669 | 121.5225 | -0.64087 | 121.7377 | 121.7011 | 0.17853 | -0.67749 | 121.6232 | 121.5637 | -0.67749 | 121.7743 | 121.7102 | 0.14649 | -0.68207 | 121.7331 | 121.6965 | 121.7194 | -0.85144 | 121.6965 | 121.6919 | 121.7972 | -0.81024
6543.875 | 122.6715 | -121.6507 | 0.70038 | 0.063782 | 0.051468 | 0.056268 | 0.0014783 | 0.02826 | -0.0017496 | 0.027228 | 0.082703 | 0.014661 | 0.021715 | 0.036211 | 0.0046633 | 0.016037 | 0.054932 | -0.009155 | -0.022888 | -0.004578 | 0.13275 | -0.004578 | -0.15106 | 0.068665 | 0.027466 | -0.054932 | 0.073242 | 0.054932 | -0.041199 | -0.09613 | 121.6461 | 121.4996 | -0.56763 | 121.6415 | 121.6461 | 0.14648 | -0.64545 | 121.6095 | 121.5546 | -0.62714 | 121.7194 | 121.5958 | 0.041198 | -0.64545 | 121.7834 | 121.7056 | 121.6278 | -0.85144 | 121.7239 | 121.7056 | 121.6782 | -0.79651
6545.5781 | 122.5525 | -121.7102 | 0.74158 | -0.17273 | 0.051895 | 0.059045 | 0.0070325 | 0.02826 | -0.0034586 | 0.025519 | -0.19958 | 0.01167 | 0.026842 | 0.037279 | -0.0013181 | 0.0186 | 0.018311 | 0.022888 | -0.013733 | -0.013733 | 0.1236 | -0.013733 | -0.16479 | 0.022888 | 0.050354 | -0.068665 | 0.11444 | 0.082397 | -0.068665 | -0.10529 | 121.6965 | 121.5454 | -0.61798 | 121.7331 | 121.6965 | 0.15106 | -0.72327 | 121.6415 | 121.6049 | -0.62714 | 121.7331 | 121.6415 | 0.036621 | -0.65918 | 121.8338 | 121.7285 | 121.6965 | -0.90637 | 121.8246 | 121.7926 | 121.7606 | -0.84686
6547.2812 | 122.5616 | -121.6965 | 0.72784 | 0.056152 | 0.0504 | 0.057123 | -0.00044435 | 0.02591 | 0.0012412 | 0.028297 | 0.059815 | 0.014661 | 0.021715 | 0.037066 | 0.0042361 | 0.015396 | 0.022888 | -0.027466 | -0.036621 | -0.013733 | 0.12817 | 0 | -0.15106 | 0.041199 | -0.009155 | -0.091553 | 0.068665 | 0.073242 | -0.050354 | -0.10071 | 121.6965 | 121.5454 | -0.59967 | 121.669 | 121.6827 | 0.13733 | -0.70496 | 121.6461 | 121.5958 | -0.65918 | 121.7377 | 121.6049 | 0.009155 | -0.6546 | 121.8246 | 121.7194 | 121.6599 | -0.87891 | 121.7651 | 121.7697 | 121.6873 | -0.82855
6548.9844 | 122.58 | -121.701 | 0.72327 | -0.096436 | 0.049546 | 0.057977 | 0.0014783 | 0.028688 | -0.001536 | 0.027442 | -0.16144 | 0.014447 | 0.021928 | 0.036425 | 0.0065859 | 0.016037 | 0.082397 | 0.064087 | 0.009155 | 0.041199 | 0.1236 | 0 | -0.15564 | 0.09613 | 0.068665 | -0.045776 | 0.068665 | 0.068665 | -0.064087 | -0.10986 | 121.701 | 121.5454 | -0.59967 | 121.7651 | 121.7422 | 0.19684 | -0.64087 | 121.637 | 121.5912 | -0.6546 | 121.7972 | 121.6553 | 0.064087 | -0.6546 | 121.8246 | 121.7834 | 121.7102 | -0.87891 | 121.7697 | 121.7697 | 121.7697 | -0.83313
6550.7188 | 122.6669 | -121.6507 | 0.70953 | 0.12482 | 0.048905 | 0.059473 | 0.00062385 | 0.02591 | -0.002604 | 0.028297 | 0.13611 | 0.012097 | 0.021074 | 0.035143 | 0.0027407 | 0.017318 | 0.10986 | 0.11444 | 0.068665 | 0.086975 | 0.10986 | 0.009155 | -0.10071 | 0.1236 | 0.1236 | 0.041199 | 0.050354 | 0.022888 | -0.022888 | -0.064087 | 121.6599 | 121.55 | -0.59967 | 121.7651 | 121.7377 | 0.18768 | -0.59967 | 121.6278 | 121.5866 | -0.65918 | 121.7743 | 121.6919 | 0.10529 | -0.68665 | 121.7606 | 121.7606 | 121.7194 | -0.81024 | 121.701 | 121.6736 | 121.7743 | -0.77362
6552.4062 | 122.5937 | -121.6873 | 0.70496 | -0.22614 | 0.051468 | 0.058191 | 0.0046827 | 0.02591 | -0.0023904 | 0.027228 | -0.18433 | 0.015088 | 0.023851 | 0.038988 | 0.00017731 | 0.017105 | 0.013733 | -0.013733 | -0.013733 | 0 | 0.1236 | -0.009155 | -0.14648 | 0.013733 | 0.036621 | -0.082397 | 0.07782 | 0.073242 | -0.045776 | -0.1236 | 121.6782 | 121.5408 | -0.58136 | 121.6736 | 121.6873 | 0.14648 | -0.69122 | 121.6415 | 121.5637 | -0.62714 | 121.701 | 121.6049 | 0.041199 | -0.63171 | 121.8109 | 121.701 | 121.6736 | -0.85144 | 121.7651 | 121.7606 | 121.7239 | -0.82855
6554.1094 | 122.5662 | -121.7239 | 0.72327 | -0.19562 | 0.048477 | 0.058405 | 0.0087415 | 0.026124 | -0.0075174 | 0.025306 | -0.22247 | 0.01167 | 0.023851 | 0.036425 | -0.0011045 | 0.015823 | 0.059509 | 0.11902 | 0.09613 | 0.068665 | 0.10071 | 0.036621 | -0.13275 | 0.082397 | 0.13733 | -0.009155 | 0.050354 | 0.045776 | -0.036621 | -0.07782 | 121.7606 | 121.5912 | -0.62256 | 121.843 | 121.7926 | 0.20142 | -0.66376 | 121.6873 | 121.6461 | -0.67291 | 121.8063 | 121.7148 | 0.068665 | -0.67749 | 121.8246 | 121.7834 | 121.8201 | -0.85602 | 121.7743 | 121.7697 | 121.8613 | -0.80109
6555.8125 | 122.6212 | -121.6782 | 0.71869 | 0.11719 | 0.048691 | 0.057336 | 0.0027601 | 0.027833 | -0.006022 | 0.025947 | 0.12848 | 0.011029 | 0.023424 | 0.03557 | 0.00081811 | 0.0186 | 0.10071 | 0.11902 | 0.10529 | 0.068665 | 0.10529 | 0.050354 | -0.082397 | 0.14191 | 0.13733 | 0.041199 | 0.054932 | 0.045776 | -0.022888 | -0.068665 | 121.7285 | 121.5958 | -0.6134 | 121.7972 | 121.7468 | 0.15106 | -0.61798 | 121.6553 | 121.6095 | -0.66376 | 121.8201 | 121.7194 | 0.10986 | -0.67291 | 121.7834 | 121.7789 | 121.7834 | -0.80109 | 121.7331 | 121.7239 | 121.8155 | -0.78735
6557.5156 | 122.6852 | -121.6644 | 0.71869 | 0.14008 | 0.051041 | 0.058191 | 0.00041005 | 0.026338 | -0.0017496 | 0.02616 | 0.15137 | 0.012311 | 0.024065 | 0.034289 | 0.0046633 | 0.015182 | 0.050354 | -0.004578 | 0.013733 | 0.022888 | 0.12817 | 0.009155 | -0.11902 | 0.11444 | 0.082397 | -0.009155 | 0.041199 | 0.045776 | -0.009155 | -0.082397 | 121.6736 | 121.5454 | -0.59052 | 121.6599 | 121.6873 | 0.14191 | -0.66834 | 121.6553 | 121.582 | -0.67749 | 121.7789 | 121.6553 | 0.073242 | -0.67291 | 121.7926 | 121.7148 | 121.6782 | -0.83771 | 121.7056 | 121.7102 | 121.7468 | -0.80109
6559.2344 | 122.6807 | -121.669 | 0.68665 | 0.13245 | 0.049546 | 0.056696 | 0.0012647 | 0.02527 | -0.0019632 | 0.026801 | 0.12085 | 0.012525 | 0.021715 | 0.037493 | 0.0053043 | 0.01625 | 0.054932 | 0.036621 | 0.027466 | 0.036621 | 0.12817 | 0.027466 | -0.13275 | 0.13275 | 0.09613 | 0.013733 | 0.050354 | 0.045776 | -0.027466 | -0.082397 | 121.6965 | 121.5363 | -0.55847 | 121.7056 | 121.7056 | 0.16937 | -0.63171 | 121.6415 | 121.5866 | -0.63629 | 121.8018 | 121.6827 | 0.09613 | -0.64087 | 121.7972 | 121.7239 | 121.6965 | -0.8194 | 121.7194 | 121.7148 | 121.7651 | -0.76904
6560.9375 | 122.6578 | -121.6873 | 0.71869 | -0.17273 | 0.045487 | 0.057977 | 0.0012647 | 0.026765 | -0.0087992 | 0.025306 | -0.15381 | 0.011457 | 0.019579 | 0.033861 | 0.00060451 | 0.0186 | 0.11444 | 0.15106 | 0.11444 | 0.086975 | 0.073242 | 0.032043 | -0.10986 | 0.12817 | 0.18768 | 0.064087 | 0.036621 | 0.054932 | -0.018311 | -0.068665 | 121.7194 | 121.5775 | -0.64545 | 121.8384 | 121.7743 | 0.19684 | -0.60425 | 121.669 | 121.6187 | -0.68207 | 121.8155 | 121.7514 | 0.13275 | -0.66376 | 121.7606 | 121.8018 | 121.8018 | -0.82855 | 121.7239 | 121.7422 | 121.875 | -0.78735
6562.6406 | 122.6852 | -121.637 | 0.70496 | -0.096436 | 0.045273 | 0.057977 | 0.0055371 | 0.027406 | -0.007731 | 0.025519 | -0.12329 | 0.010816 | 0.022142 | 0.034075 | -0.00046349 | 0.016891 | 0.07782 | 0.10529 | 0.10529 | 0.041199 | 0.09613 | 0.032043 | -0.11902 | 0.15106 | 0.16479 | 0.064087 | 0.054932 | 0.041199 | -0.032043 | -0.073242 | 121.669 | 121.5179 | -0.60883 | 121.7422 | 121.6782 | 0.16022 | -0.62714 | 121.6049 | 121.5637 | -0.65002 | 121.788 | 121.701 | 0.13733 | -0.66376 | 121.7331 | 121.7148 | 121.7422 | -0.82398 | 121.6919 | 121.6782 | 121.8018 | -0.7782
6564.3281 | 122.6761 | -121.6736 | 0.70038 | 0.14008 | 0.0504 | 0.059045 | 0.00062385 | 0.027619 | 0.00060022 | 0.02851 | 0.12085 | 0.012738 | 0.023851 | 0.038134 | 0.0053043 | 0.014968 | 0.09613 | 0.036621 | 0.032043 | 0.027466 | 0.10986 | 0.022888 | -0.12817 | 0.11902 | 0.09613 | 0.013733 | 0.064087 | 0.045776 | -0.027466 | -0.086975 | 121.6965 | 121.5454 | -0.59051 | 121.7102 | 121.7011 | 0.15564 | -0.60425 | 121.6461 | 121.5866 | -0.63629 | 121.7926 | 121.6873 | 0.10071 | -0.6546 | 121.7834 | 121.7697 | 121.7056 | -0.82855 | 121.7377 | 121.7194 | 121.7697 | -0.78735
6566.0938 | 122.6669 | -121.6782 | 0.70038 | -0.020142 | 0.047837 | 0.060327 | 0.0034009 | 0.026765 | -0.0064492 | 0.025306 | 0.044556 | 0.011457 | 0.022783 | 0.033221 | -0.00089089 | 0.017105 | 0.059509 | 0.050354 | 0.054932 | 0.045776 | 0.10529 | 0.022888 | -0.11902 | 0.07782 | 0.086975 | -0.009155 | 0.045776 | 0.045776 | -0.018311 | -0.07782 | 121.701 | 121.5591 | -0.59509 | 121.7285 | 121.7239 | 0.16479 | -0.64087 | 121.6599 | 121.6003 | -0.6546 | 121.756 | 121.669 | 0.068665 | -0.6546 | 121.7834 | 121.7377 | 121.7331 | -0.8194 | 121.7239 | 121.7239 | 121.7651 | -0.7782
6567.7969 | 122.6807 | -121.6736 | 0.70496 | 0.11719 | 0.047623 | 0.058618 | -0.00087155 | 0.025697 | -0.0011088 | 0.026588 | 0.067444 | 0.010602 | 0.023637 | 0.035143 | 0.0048769 | 0.015823 | 0.11902 | 0.064087 | 0.059509 | 0.07782 | 0.086975 | 0.041199 | -0.10529 | 0.15106 | 0.1236 | 0.045776 | 0.041199 | 0.027466 | -0.013733 | -0.064087 | 121.7148 | 121.5683 | -0.61798 | 121.7377 | 121.7514 | 0.18311 | -0.58594 | 121.6599 | 121.6095 | -0.66376 | 121.8246 | 121.7194 | 0.10986 | -0.67749 | 121.7606 | 121.7926 | 121.7331 | -0.81024 | 121.7148 | 121.7011 | 121.7972 | -0.76904
6569.5156 | 122.6761 | -121.6782 | 0.68207 | 0.0027468 | 0.046982 | 0.060327 | 0.0059643 | 0.02527 | -0.0085856 | 0.026801 | 0.036926 | 0.010602 | 0.02556 | 0.035998 | 0.00039091 | 0.017318 | 0.041199 | 0.059509 | 0.064087 | 0.032043 | 0.09613 | 0.027466 | -0.11902 | 0.091553 | 0.091553 | 0.027466 | 0.050354 | 0.027466 | -0.045776 | -0.10986 | 121.7056 | 121.5591 | -0.58594 | 121.7377 | 121.7102 | 0.15106 | -0.64087 | 121.6324 | 121.5683 | -0.63171 | 121.7697 | 121.7056 | 0.13733 | -0.6546 | 121.7743 | 121.7194 | 121.7422 | -0.80109 | 121.7285 | 121.7056 | 121.7697 | -0.79193
6571.2188 | 122.6486 | -121.6873 | 0.70953 | 0.10956 | 0.050186 | 0.056696 | -0.00044435 | 0.025697 | 0.00038662 | 0.026588 | 0.021668 | 0.014875 | 0.023851 | 0.036425 | 0.0061587 | 0.015823 | 0.032043 | -0.027466 | -0.045776 | -0.009155 | 0.1236 | -0.004578 | -0.14191 | 0.068665 | -0.009155 | -0.091553 | 0.10529 | 0.068665 | -0.068665 | -0.10986 | 121.6827 | 121.5454 | -0.58594 | 121.6599 | 121.6782 | 0.13275 | -0.67749 | 121.6187 | 121.5775 | -0.60425 | 121.756 | 121.5958 | 0.01831 | -0.64087 | 121.8109 | 121.7194 | 121.6415 | -0.85144 | 121.7926 | 121.756 | 121.6782 | -0.8194
6572.9375 | 122.6944 | -121.6553 | 0.70496 | -0.17273 | 0.046128 | 0.059686 | 0.0038281 | 0.025056 | -0.0070902 | 0.025092 | -0.092773 | 0.010816 | 0.023851 | 0.032793 | -0.00067729 | 0.017318 | 0.11444 | 0.15564 | 0.11902 | 0.082397 | 0.082397 | 0.022888 | -0.13275 | 0.16479 | 0.1831 | 0.086975 | 0.059509 | 0.022888 | -0.013733 | -0.059509 | 121.6782 | 121.5225 | -0.62256 | 121.8109 | 121.7377 | 0.21515 | -0.59052 | 121.6415 | 121.5958 | -0.64545 | 121.8201 | 121.7422 | 0.14648 | -0.68207 | 121.7377 | 121.7697 | 121.7743 | -0.83771 | 121.7148 | 121.6782 | 121.8384 | -0.76447
6574.6719 | 122.5525 | -121.7102 | 0.73242 | 0.010376 | 0.049973 | 0.059686 | -0.0019397 | 0.028474 | 0.0027364 | 0.028724 | -0.0012209 | 0.014875 | 0.021501 | 0.033221 | 0.0061587 | 0.016677 | 0.045776 | -0.022888 | -0.045776 | 0 | 0.1236 | 0.004578 | -0.14648 | 0.027466 | -0.004578 | -0.11444 | 0.082397 | 0.073242 | -0.064087 | -0.10986 | 121.7148 | 121.5637 | -0.60883 | 121.6873 | 121.7102 | 0.14648 | -0.68665 | 121.6461 | 121.6003 | -0.65003 | 121.7377 | 121.5958 | -0.004578 | -0.65918 | 121.8338 | 121.756 | 121.6644 | -0.87891 | 121.7926 | 121.7834 | 121.7056 | -0.84229
6576.375 | 122.5891 | -121.7194 | 0.72784 | -0.11932 | 0.053818 | 0.057977 | 0.0051099 | 0.026338 | -4.058e-05 | 0.028937 | -0.16144 | 0.013379 | 0.02556 | 0.036425 | 0.0027407 | 0.015396 | 0.082397 | 0.050354 | 0.022888 | 0.050354 | 0.1236 | 0 | -0.16022 | 0.07782 | 0.10071 | -0.036621 | 0.073242 | 0.054932 | -0.032043 | -0.10529 | 121.7194 | 121.5591 | -0.60425 | 121.7697 | 121.7697 | 0.21057 | -0.64545 | 121.6873 | 121.6141 | -0.6546 | 121.7972 | 121.6827 | 0.068665 | -0.67291 | 121.843 | 121.8018 | 121.7422 | -0.88806 | 121.7926 | 121.7743 | 121.8201 | -0.83313
6578.0781 | 122.5571 | -121.7606 | 0.73242 | -0.25665 | 0.049332 | 0.058832 | 0.0046827 | 0.026124 | -0.0073038 | 0.027442 | -0.19196 | 0.010388 | 0.024705 | 0.035998 | -0.00067729 | 0.018814 | 0.041199 | 0.10071 | 0.041199 | 0.045776 | 0.09613 | 0.013733 | -0.13275 | 0.050354 | 0.091553 | -0.059509 | 0.086975 | 0.054932 | -0.059509 | -0.10986 | 121.7743 | 121.6278 | -0.63629 | 121.8613 | 121.8063 | 0.17853 | -0.69122 | 121.701 | 121.6507 | -0.64545 | 121.8109 | 121.701 | 0.050354 | -0.67749 | 121.8567 | 121.8018 | 121.8018 | -0.86517 | 121.8475 | 121.8155 | 121.8521 | -0.84229
6579.7812 | 122.6303 | -121.7102 | 0.68665 | 0.010376 | 0.046128 | 0.0599 | 0.0023329 | 0.02591 | -0.010508 | 0.027656 | 0.082703 | 0.012097 | 0.023424 | 0.035143 | -0.0013181 | 0.016037 | 0.050354 | 0.086975 | 0.059509 | 0.041199 | 0.07782 | 0.032043 | -0.11444 | 0.09613 | 0.091553 | 0.004578 | 0.054932 | 0.027466 | -0.022888 | -0.07782 | 121.7422 | 121.5958 | -0.60883 | 121.7972 | 121.7514 | 0.15564 | -0.63629 | 121.6873 | 121.6324 | -0.63171 | 121.8063 | 121.7148 | 0.082398 | -0.65918 | 121.788 | 121.7606 | 121.7697 | -0.80109 | 121.7651 | 121.7377 | 121.8018 | -0.76447
6581.4844 | 122.5845 | -121.7194 | 0.72784 | 0.025635 | 0.051041 | 0.060114 | 0.00062385 | 0.026124 | -4.058e-05 | 0.029365 | 0.014038 | 0.014661 | 0.021501 | 0.039202 | 0.0029543 | 0.016464 | 0.009155 | -0.050354 | -0.041199 | -0.009155 | 0.12817 | 0 | -0.13733 | 0.041199 | -0.004578 | -0.10529 | 0.082397 | 0.073242 | -0.073242 | -0.10529 | 121.7194 | 121.582 | -0.59967 | 121.669 | 121.7102 | 0.12817 | -0.71869 | 121.6461 | 121.6141 | -0.64545 | 121.7606 | 121.6141 | 0 | -0.6546 | 121.8475 | 121.7285 | 121.6782 | -0.86517 | 121.8018 | 121.7926 | 121.7148 | -0.83313
6583.1875 | 122.6715 | -121.6644 | 0.69122 | 0.08667 | 0.052109 | 0.059045 | 0.0010511 | 0.028901 | -0.0023904 | 0.029151 | 0.15137 | 0.014234 | 0.022142 | 0.035143 | 0.0038089 | 0.013687 | 0.036621 | 0.018311 | 0.004578 | 0.004578 | 0.10529 | 0.009155 | -0.14191 | 0.091553 | 0.068665 | -0.032043 | 0.050354 | 0.032043 | -0.041199 | -0.064087 | 121.6736 | 121.5225 | -0.58594 | 121.6827 | 121.669 | 0.14649 | -0.6546 | 121.6232 | 121.6003 | -0.64087 | 121.756 | 121.6324 | 0.032044 | -0.65918 | 121.7697 | 121.701 | 121.669 | -0.83313 | 121.7148 | 121.6965 | 121.7331 | -0.75531
6584.8906 | 122.5525 | -121.7422 | 0.72327 | -0.073547 | 0.05275 | 0.057123 | 0.00041005 | 0.02591 | 0.00038662 | 0.030219 | -0.062256 | 0.013593 | 0.024492 | 0.03557 | 0.0057315 | 0.017532 | 0.064087 | 0.022888 | 0.009155 | 0.022888 | 0.09613 | 0.004578 | -0.15106 | 0.059509 | 0.027466 | -0.086975 | 0.068665 | 0.073242 | -0.059509 | -0.09613 | 121.7468 | 121.5912 | -0.62714 | 121.7651 | 121.7651 | 0.17395 | -0.65918 | 121.6827 | 121.6461 | -0.6546 | 121.8018 | 121.6553 | 0.009155 | -0.65002 | 121.8384 | 121.8063 | 121.7514 | -0.87433 | 121.8109 | 121.8155 | 121.7697 | -0.8194
6586.625 | 122.6028 | -121.7056 | 0.73242 | -0.18036 | 0.049973 | 0.05755 | 0.0027601 | 0.02591 | -0.0040994 | 0.026374 | -0.20721 | 0.014234 | 0.023851 | 0.035998 | 0.0027407 | 0.016891 | 0.018311 | 0 | -0.018311 | 0.009155 | 0.1236 | 0 | -0.15106 | 0.027466 | 0.068665 | -0.059509 | 0.10529 | 0.068665 | -0.064087 | -0.10986 | 121.7056 | 121.5546 | -0.60883 | 121.7056 | 121.7148 | 0.16022 | -0.71411 | 121.6415 | 121.5958 | -0.62714 | 121.7331 | 121.6461 | 0.050354 | -0.66376 | 121.8292 | 121.7239 | 121.6873 | -0.88348 | 121.8109 | 121.7743 | 121.7743 | -0.84229
6588.3281 | 122.7036 | -121.701 | 0.66834 | -0.012512 | 0.04805 | 0.060327 | 0.0068189 | 0.027192 | -0.0096536 | 0.024451 | 0.052185 | 0.0099612 | 0.024065 | 0.033434 | -0.0019589 | 0.020309 | 0.013733 | 0.068665 | 0.064087 | 0.041199 | 0.09613 | 0.022888 | -0.11902 | 0.10529 | 0.13275 | 0.036621 | 0.050354 | 0.022888 | -0.032043 | -0.091553 | 121.7239 | 121.582 | -0.57221 | 121.7697 | 121.7422 | 0.16022 | -0.6546 | 121.669 | 121.6095 | -0.61798 | 121.8063 | 121.7377 | 0.12817 | -0.64545 | 121.7972 | 121.7148 | 121.7651 | -0.78735 | 121.7514 | 121.7239 | 121.8338 | -0.75989
6590.0312 | 122.6532 | -121.6782 | 0.69122 | 0.13245 | 0.047837 | 0.059045 | 0.00041005 | 0.023988 | -0.0030314 | 0.028083 | 0.16663 | 0.012952 | 0.018297 | 0.033861 | 0.0033817 | 0.017318 | 0.11902 | 0.11902 | 0.10529 | 0.073242 | 0.086975 | 0.041199 | -0.10986 | 0.14648 | 0.15106 | 0.041199 | 0.036621 | 0.022888 | -0.027466 | -0.054932 | 121.7194 | 121.5683 | -0.60425 | 121.7972 | 121.7514 | 0.18311 | -0.5722 | 121.6507 | 121.6232 | -0.6546 | 121.8246 | 121.7194 | 0.096131 | -0.66834 | 121.7651 | 121.7972 | 121.7834 | -0.80109 | 121.7148 | 121.701 | 121.8292 | -0.74616
6591.7344 | 122.6898 | -121.6782 | 0.6958 | 0.15533 | 0.049332 | 0.057764 | -0.00044435 | 0.027833 | -0.0021768 | 0.027442 | 0.13611 | 0.012738 | 0.021715 | 0.035143 | 0.0044497 | 0.017105 | 0.059509 | 0.032043 | 0.032043 | 0.022888 | 0.1236 | 0.050354 | -0.1236 | 0.10529 | 0.10986 | 0 | 0.032043 | 0.041199 | -0.013733 | -0.082397 | 121.7285 | 121.5546 | -0.5722 | 121.7102 | 121.701 | 0.14648 | -0.63629 | 121.6644 | 121.5958 | -0.66376 | 121.7834 | 121.6782 | 0.082397 | -0.6546 | 121.8018 | 121.7377 | 121.7102 | -0.8194 | 121.7102 | 121.7194 | 121.788 | -0.7782
6593.4531 | 122.6715 | -121.6965 | 0.70038 | -0.15747 | 0.049332 | 0.058191 | 0.0066053 | 0.02527 | -0.0090128 | 0.027015 | -0.077515 | 0.008893 | 0.021501 | 0.036211 | -0.0021725 | 0.016464 | 0.10986 | 0.15106 | 0.1236 | 0.086975 | 0.10071 | 0.036621 | -0.10529 | 0.14191 | 0.1831 | 0.073242 | 0.059509 | 0.036621 | 0 | -0.068665 | 121.7331 | 121.5912 | -0.59967 | 121.8475 | 121.7834 | 0.19226 | -0.59051 | 121.6965 | 121.6278 | -0.64087 | 121.8384 | 121.7697 | 0.14191 | -0.66376 | 121.7972 | 121.8063 | 121.8201 | -0.80566 | 121.756 | 121.7331 | 121.8796 | -0.76904
6595.1562 | 122.6852 | -121.701 | 0.68665 | -0.0048827 | 0.044632 | 0.060754 | 0.0014783 | 0.025483 | -0.0068766 | 0.025306 | 0.044556 | 0.010816 | 0.020647 | 0.035784 | -0.00089089 | 0.017318 | 0.041199 | 0.064087 | 0.045776 | 0.045776 | 0.10986 | 0.027466 | -0.1236 | 0.07782 | 0.091553 | 0.013733 | 0.050354 | 0.036621 | -0.041199 | -0.091553 | 121.7285 | 121.5775 | -0.57678 | 121.7651 | 121.7468 | 0.16937 | -0.64545 | 121.6599 | 121.6095 | -0.63629 | 121.7789 | 121.7148 | 0.10529 | -0.65002 | 121.8109 | 121.7422 | 121.7468 | -0.81024 | 121.7514 | 121.7377 | 121.7926 | -0.7782
6596.8594 | 122.6898 | -121.6827 | 0.6958 | 0.15533 | 0.051682 | 0.059045 | -0.00023075 | 0.026124 | -0.0011088 | 0.028297 | 0.11322 | 0.013379 | 0.022142 | 0.037066 | 0.0065859 | 0.014968 | 0.064087 | 0.045776 | 0.022888 | 0.022888 | 0.11902 | 0.018311 | -0.13275 | 0.13275 | 0.10071 | 0.013733 | 0.050354 | 0.045776 | -0.009155 | -0.068665 | 121.701 | 121.55 | -0.57678 | 121.7285 | 121.7056 | 0.15564 | -0.63171 | 121.6736 | 121.6141 | -0.64545 | 121.8155 | 121.6965 | 0.082398 | -0.65002 | 121.8018 | 121.7468 | 121.7056 | -0.82855 | 121.7331 | 121.7285 | 121.7834 | -0.76447
6598.6094 | 122.5845 | -121.7377 | 0.73242 | -0.19562 | 0.051468 | 0.059045 | 0.0072461 | 0.027833 | -0.0058084 | 0.027228 | -0.13092 | 0.010602 | 0.023424 | 0.035998 | 0.00060451 | 0.016677 | 0.10986 | 0.1236 | 0.10986 | 0.07782 | 0.10529 | 0.036621 | -0.11902 | 0.1236 | 0.16479 | 0.041199 | 0.045776 | 0.036621 | -0.032043 | -0.068665 | 121.7743 | 121.6187 | -0.62714 | 121.8613 | 121.8155 | 0.19684 | -0.62256 | 121.7056 | 121.669 | -0.68665 | 121.8613 | 121.7789 | 0.10986 | -0.6958 | 121.843 | 121.8475 | 121.8475 | -0.85144 | 121.7834 | 121.7743 | 121.9025 | -0.80109
6600.3125 | 122.7036 | -121.6919 | 0.67291 | 0.071411 | 0.050186 | 0.057764 | -0.00044435 | 0.025056 | -0.001536 | 0.026588 | 0.11322 | 0.013166 | 0.022996 | 0.037066 | 0.0038089 | 0.0139 | 0.064087 | 0 | -0.004578 | 0.009155 | 0.11444 | 0.022888 | -0.15564 | 0.091553 | 0.036621 | -0.041199 | 0.07782 | 0.054932 | -0.032043 | -0.082397 | 121.7148 | 121.5363 | -0.55847 | 121.6919 | 121.7011 | 0.16479 | -0.60883 | 121.6599 | 121.6095 | -0.59509 | 121.7834 | 121.6507 | 0.041198 | -0.61798 | 121.8063 | 121.756 | 121.6873 | -0.82855 | 121.7697 | 121.7468 | 121.7285 | -0.75531
6602.0156 | 122.6898 | -121.6553 | 0.67291 | 0.16296 | 0.048691 | 0.058618 | 0.0012647 | 0.026338 | -0.0038858 | 0.027656 | 0.075073 | 0.013593 | 0.02086 | 0.036638 | 0.0038089 | 0.016464 | 0.091553 | 0.073242 | 0.059509 | 0.059509 | 0.10986 | 0.036621 | -0.10071 | 0.14191 | 0.13275 | 0.022888 | 0.045776 | 0.041199 | -0.004578 | -0.068665 | 121.6919 | 121.5546 | -0.56305 | 121.7285 | 121.7148 | 0.16022 | -0.58136 | 121.6507 | 121.5866 | -0.62714 | 121.7972 | 121.6782 | 0.091553 | -0.63171 | 121.7651 | 121.7468 | 121.7148 | -0.77362 | 121.701 | 121.6965 | 121.788 | -0.74158
6603.7188 | 122.5937 | -121.7422 | 0.72327 | 0.0027468 | 0.052323 | 0.057977 | 0.0027601 | 0.027192 | 0.00081382 | 0.028297 | 0.10559 | 0.014661 | 0.023424 | 0.035357 | 0.0046633 | 0.015182 | -0.013733 | -0.054932 | -0.045776 | -0.018311 | 0.13733 | 0 | -0.15106 | 0.032043 | -0.022888 | -0.10071 | 0.09613 | 0.068665 | -0.073242 | -0.10986 | 121.7422 | 121.5912 | -0.58594 | 121.6873 | 121.7239 | 0.13275 | -0.737 | 121.669 | 121.6324 | -0.62714 | 121.7743 | 121.6415 | 0.009155 | -0.6546 | 121.8796 | 121.7285 | 121.6965 | -0.87433 | 121.8384 | 121.8109 | 121.7194 | -0.83313
6605.4062 | 122.6532 | -121.6873 | 0.69122 | 0.10193 | 0.048905 | 0.057764 | -0.0017261 | 0.028474 | -0.001536 | 0.027015 | 0.052185 | 0.013593 | 0.021501 | 0.035357 | 0.0035953 | 0.014755 | 0.013733 | 0 | -0.027466 | 0.009155 | 0.13275 | 0.013733 | -0.14191 | 0.041199 | 0.027466 | -0.091553 | 0.073242 | 0.064087 | -0.068665 | -0.11444 | 121.701 | 121.5454 | -0.55847 | 121.6873 | 121.6965 | 0.15106 | -0.67749 | 121.6187 | 121.5729 | -0.61798 | 121.7285 | 121.5958 | 0.022888 | -0.62714 | 121.8201 | 121.701 | 121.6599 | -0.83313 | 121.7606 | 121.7514 | 121.7148 | -0.80566
6607.1406 | 122.6166 | -121.7377 | 0.71869 | -0.21088 | 0.049973 | 0.057977 | 0.0014783 | 0.025697 | -0.0028178 | 0.029365 | -0.19196 | 0.013166 | 0.023851 | 0.035357 | 0.0025271 | 0.015182 | 0.022888 | 0.018311 | -0.009155 | 0.032043 | 0.12817 | 0.004578 | -0.13275 | 0.059509 | 0.07782 | -0.050354 | 0.09613 | 0.073242 | -0.045776 | -0.10986 | 121.7422 | 121.6049 | -0.59052 | 121.756 | 121.7697 | 0.16479 | -0.6958 | 121.6919 | 121.6278 | -0.62256 | 121.7972 | 121.6873 | 0.059509 | -0.64545 | 121.8658 | 121.7606 | 121.7285 | -0.85144 | 121.8338 | 121.8109 | 121.8155 | -0.82855
6608.8438 | 122.5662 | -121.7377 | 0.73242 | -0.21851 | 0.050186 | 0.05755 | 0.0068189 | 0.027619 | -0.0073038 | 0.025306 | -0.19196 | 0.012952 | 0.025133 | 0.036211 | -0.0015317 | 0.016891 | 0 | 0.018311 | 0.004578 | 0.009155 | 0.1236 | -0.013733 | -0.13733 | 0.032043 | 0.054932 | -0.050354 | 0.10071 | 0.059509 | -0.054932 | -0.12817 | 121.7239 | 121.6003 | -0.60883 | 121.756 | 121.7468 | 0.14648 | -0.73242 | 121.6827 | 121.6095 | -0.63171 | 121.7697 | 121.6873 | 0.07782 | -0.67291 | 121.8613 | 121.7377 | 121.7422 | -0.86975 | 121.8384 | 121.7972 | 121.7926 | -0.8606
6610.6094 | 122.5983 | -121.7239 | 0.70496 | 0.063782 | 0.049332 | 0.058832 | -0.0010851 | 0.025697 | -0.0034586 | 0.029151 | 0.067444 | 0.014234 | 0.022996 | 0.037066 | 0.0038089 | 0.016677 | -0.013733 | -0.009155 | -0.032043 | -0.004578 | 0.1236 | 0.018311 | -0.16479 | 0.022888 | -0.013733 | -0.086975 | 0.09613 | 0.050354 | -0.059509 | -0.11444 | 121.7422 | 121.5591 | -0.58136 | 121.7148 | 121.7194 | 0.16022 | -0.71869 | 121.6644 | 121.6095 | -0.60883 | 121.7468 | 121.637 | 0.027466 | -0.6546 | 121.8475 | 121.7102 | 121.6919 | -0.86975 | 121.8201 | 121.7743 | 121.7102 | -0.8194
6612.3281 | 122.6898 | -121.6873 | 0.69122 | 0.048523 | 0.051468 | 0.058191 | 0.0031873 | 0.02527 | -0.0030314 | 0.027869 | 0.11322 | 0.013166 | 0.024705 | 0.034929 | 0.0027407 | 0.018173 | 0 | 0.022888 | -0.018311 | -0.009155 | 0.13275 | 0.009155 | -0.13275 | 0.059509 | 0.022888 | -0.050354 | 0.073242 | 0.045776 | -0.036621 | -0.10529 | 121.6965 | 121.5546 | -0.55847 | 121.7102 | 121.6782 | 0.1236 | -0.69122 | 121.6507 | 121.582 | -0.61798 | 121.7468 | 121.637 | 0.054932 | -0.64545 | 121.8201 | 121.6873 | 121.669 | -0.82397 | 121.7606 | 121.7331 | 121.7102 | -0.79651
6614.0781 | 122.5937 | -121.7422 | 0.72327 | -0.27191 | 0.051682 | 0.059473 | 0.0072461 | 0.026979 | -0.0070902 | 0.025733 | -0.22247 | 0.013166 | 0.023637 | 0.035998 | 0.0012455 | 0.017318 | -0.022888 | 0.013733 | -0.022888 | -0.013733 | 0.13275 | -0.009155 | -0.13733 | 0.018311 | 0.041199 | -0.073242 | 0.09613 | 0.07782 | -0.054932 | -0.13275 | 121.7331 | 121.6049 | -0.59052 | 121.756 | 121.7285 | 0.1236 | -0.74616 | 121.6873 | 121.6095 | -0.62714 | 121.7606 | 121.669 | 0.059509 | -0.64545 | 121.875 | 121.7194 | 121.7194 | -0.8606 | 121.8384 | 121.8201 | 121.7834 | -0.85602
6615.7812 | 122.6944 | -121.6919 | 0.70038 | -0.1651 | 0.04506 | 0.058832 | 0.0040417 | 0.024201 | -0.00944 | 0.025092 | -0.062256 | 0.0099612 | 0.024705 | 0.035357 | -0.0017453 | 0.019241 | 0.068665 | 0.14191 | 0.11444 | 0.091553 | 0.082397 | 0.041199 | -0.10986 | 0.15106 | 0.17853 | 0.091553 | 0.045776 | 0.013733 | -0.022888 | -0.082397 | 121.7331 | 121.582 | -0.61798 | 121.8338 | 121.7834 | 0.20142 | -0.63171 | 121.669 | 121.6095 | -0.6546 | 121.843 | 121.7834 | 0.17395 | -0.68664 | 121.7743 | 121.7606 | 121.8063 | -0.81024 | 121.7377 | 121.7056 | 121.8704 | -0.78277
6617.5156 | 122.6624 | -121.7148 | 0.70496 | 0.10193 | 0.049546 | 0.057336 | 0.0010511 | 0.025697 | -0.0038858 | 0.027869 | 0.12085 | 0.01167 | 0.023851 | 0.036211 | 0.0012455 | 0.015823 | 0.09613 | 0.12817 | 0.11444 | 0.059509 | 0.073242 | 0.050354 | -0.11444 | 0.14648 | 0.14191 | 0.045776 | 0.036621 | 0.045776 | -0.027466 | -0.059509 | 121.7651 | 121.6003 | -0.63171 | 121.843 | 121.7743 | 0.17395 | -0.60883 | 121.6873 | 121.6553 | -0.66834 | 121.8613 | 121.7606 | 0.10528 | -0.65918 | 121.788 | 121.8109 | 121.8292 | -0.8194 | 121.7514 | 121.7606 | 121.8567 | -0.76447
6619.2188 | 122.6349 | -121.7239 | 0.72784 | 0.10193 | 0.049546 | 0.057764 | -0.00044435 | 0.024842 | -0.00046778 | 0.027442 | 0.036926 | 0.014875 | 0.022783 | 0.037493 | 0.0020999 | 0.015823 | 0.018311 | -0.036621 | -0.054932 | 0.004578 | 0.11902 | 0.022888 | -0.16022 | 0.041199 | -0.009155 | -0.091553 | 0.07782 | 0.068665 | -0.036621 | -0.10071 | 121.7468 | 121.5637 | -0.60883 | 121.6873 | 121.7285 | 0.16479 | -0.70953 | 121.6873 | 121.6232 | -0.65002 | 121.7651 | 121.6324 | 0.009155 | -0.65918 | 121.843 | 121.7422 | 121.669 | -0.88806 | 121.8018 | 121.7926 | 121.7148 | -0.82855
6620.9219 | 122.5983 | -121.7422 | 0.73242 | -0.10406 | 0.048905 | 0.058191 | 0.0010511 | 0.028047 | 0.0023092 | 0.027228 | -0.13855 | 0.013379 | 0.023424 | 0.035143 | 0.0040225 | 0.014328 | 0.068665 | 0.059509 | 0.013733 | 0.036621 | 0.12817 | 0.009155 | -0.14191 | 0.082397 | 0.091553 | -0.036621 | 0.068665 | 0.068665 | -0.041199 | -0.09613 | 121.7514 | 121.6003 | -0.60425 | 121.8018 | 121.7789 | 0.17853 | -0.66376 | 121.701 | 121.6461 | -0.66376 | 121.8246 | 121.7056 | 0.059509 | -0.66376 | 121.8704 | 121.8109 | 121.756 | -0.87433 | 121.8109 | 121.8109 | 121.8338 | -0.82855
6622.6562 | 122.6166 | -121.7102 | 0.73242 | -0.14221 | 0.052536 | 0.05755 | 0.0021191 | 0.02826 | -0.0040994 | 0.027656 | -0.1767 | 0.013593 | 0.023637 | 0.035998 | 0.0035953 | 0.017532 | 0.032043 | 0.041199 | 0 | 0.027466 | 0.11902 | 0.004578 | -0.14648 | 0.068665 | 0.073242 | -0.045776 | 0.07782 | 0.073242 | -0.045776 | -0.11902 | 121.7148 | 121.5637 | -0.6134 | 121.7514 | 121.7377 | 0.17395 | -0.70038 | 121.6644 | 121.5912 | -0.6546 | 121.7789 | 121.6644 | 0.073243 | -0.65918 | 121.8292 | 121.7422 | 121.7102 | -0.87891 | 121.788 | 121.7834 | 121.7834 | -0.85144
6624.3594 | 122.5845 | -121.7468 | 0.73242 | -0.20325 | 0.049332 | 0.0599 | 0.0074597 | 0.024629 | -0.0051676 | 0.024665 | -0.16907 | 0.012525 | 0.026842 | 0.035998 | -0.0013181 | 0.017959 | -0.022888 | 0.022888 | 0.009155 | -0.004578 | 0.13275 | 0.004578 | -0.14648 | 0.009155 | 0.050354 | -0.054932 | 0.10071 | 0.082397 | -0.054932 | -0.11444 | 121.7514 | 121.6003 | -0.59967 | 121.7697 | 121.7422 | 0.14191 | -0.75531 | 121.6919 | 121.6324 | -0.63171 | 121.756 | 121.6919 | 0.059509 | -0.65003 | 121.8796 | 121.7239 | 121.756 | -0.87891 | 121.8475 | 121.8292 | 121.7972 | -0.84686
6626.0625 | 122.6852 | -121.7056 | 0.70496 | 0.0027468 | 0.049546 | 0.059686 | 0.0029737 | 0.02591 | -0.0096536 | 0.02616 | 0.067444 | 0.010388 | 0.022569 | 0.035784 | -0.0021725 | 0.018386 | 0.027466 | 0.073242 | 0.064087 | 0.036621 | 0.086975 | 0.027466 | -0.09613 | 0.073242 | 0.09613 | 0.022888 | 0.059509 | 0.054932 | -0.027466 | -0.091553 | 121.7331 | 121.6095 | -0.61798 | 121.7789 | 121.7422 | 0.13275 | -0.67749 | 121.6782 | 121.6141 | -0.64545 | 121.7789 | 121.7285 | 0.11444 | -0.65002 | 121.7926 | 121.7331 | 121.7697 | -0.80109 | 121.7651 | 121.7606 | 121.8018 | -0.79651
6627.7812 | 122.699 | -121.6919 | 0.69122 | 0.11719 | 0.049118 | 0.060541 | -0.0021533 | 0.024629 | -4.058e-05 | 0.028297 | 0.12848 | 0.014875 | 0.022783 | 0.036211 | 0.0040225 | 0.016464 | 0.041199 | 0.004578 | 0.004578 | -0.004578 | 0.11444 | 0.013733 | -0.14191 | 0.09613 | 0.068665 | -0.004578 | 0.050354 | 0.054932 | -0.027466 | -0.082397 | 121.7056 | 121.55 | -0.57678 | 121.6965 | 121.6873 | 0.13733 | -0.65002 | 121.6644 | 121.6095 | -0.64087 | 121.788 | 121.6873 | 0.077819 | -0.63629 | 121.8063 | 121.7331 | 121.6965 | -0.83313 | 121.7422 | 121.7468 | 121.7606 | -0.77362
6629.5469 | 122.5937 | -121.7239 | 0.72784 | 0.018005 | 0.050614 | 0.055414 | -0.00087155 | 0.025697 | 0.00017302 | 0.02851 | 0.014038 | 0.013593 | 0.022142 | 0.037279 | 0.0046633 | 0.014755 | 0.009155 | -0.036621 | -0.054932 | -0.018311 | 0.14191 | 0.009155 | -0.14191 | 0.036621 | 0.004578 | -0.091553 | 0.086975 | 0.07782 | -0.068665 | -0.10529 | 121.7331 | 121.582 | -0.58594 | 121.6873 | 121.7056 | 0.1236 | -0.71869 | 121.6553 | 121.6187 | -0.64087 | 121.7606 | 121.6324 | 0.013733 | -0.65002 | 121.8658 | 121.7331 | 121.669 | -0.86975 | 121.8109 | 121.8018 | 121.7285 | -0.83313
6631.2656 | 122.699 | -121.6782 | 0.70953 | -0.14221 | 0.047623 | 0.057764 | 0.0057507 | 0.024629 | -0.0090128 | 0.026801 | -0.031738 | 0.010388 | 0.025774 | 0.035784 | -0.0023861 | 0.016891 | 0.082397 | 0.15106 | 0.12817 | 0.091553 | 0.09613 | 0.036621 | -0.09613 | 0.16479 | 0.18768 | 0.086975 | 0.041199 | 0.036621 | -0.013733 | -0.064087 | 121.7148 | 121.582 | -0.6134 | 121.8292 | 121.7697 | 0.18768 | -0.62714 | 121.6644 | 121.6141 | -0.66834 | 121.843 | 121.7651 | 0.15106 | -0.67291 | 121.7743 | 121.7606 | 121.8063 | -0.80566 | 121.7194 | 121.7148 | 121.8658 | -0.77362
6633.0312 | 122.5891 | -121.7285 | 0.72327 | 0.025635 | 0.051682 | 0.056482 | -0.0027941 | 0.023561 | -0.00025418 | 0.02616 | 0.029297 | 0.012952 | 0.023637 | 0.037707 | 0.0055179 | 0.015823 | -0.004578 | -0.036621 | -0.050354 | -0.009155 | 0.13733 | 0.004578 | -0.16479 | 0.022888 | -0.009155 | -0.086975 | 0.10071 | 0.073242 | -0.059509 | -0.10071 | 121.7331 | 121.5637 | -0.58594 | 121.6919 | 121.7194 | 0.15564 | -0.72784 | 121.669 | 121.6278 | -0.62256 | 121.7514 | 121.6415 | 0.013733 | -0.65002 | 121.8658 | 121.7239 | 121.6782 | -0.88806 | 121.8292 | 121.8018 | 121.7194 | -0.82398
6634.7344 | 122.5845 | -121.7468 | 0.72784 | -0.11169 | 0.051041 | 0.057123 | 0.00083745 | 0.027833 | -0.0013224 | 0.027869 | -0.14618 | 0.013806 | 0.024492 | 0.035357 | 0.0053043 | 0.014968 | 0.082397 | 0.041199 | 0.009155 | 0.041199 | 0.11902 | 0.004578 | -0.15564 | 0.10071 | 0.091553 | -0.041199 | 0.073242 | 0.073242 | -0.045776 | -0.10071 | 121.7514 | 121.5912 | -0.60883 | 121.788 | 121.788 | 0.19684 | -0.64545 | 121.701 | 121.6461 | -0.6546 | 121.8475 | 121.7056 | 0.059509 | -0.6546 | 121.8658 | 121.8292 | 121.756 | -0.88348 | 121.8201 | 121.8201 | 121.8384 | -0.82855
6636.4531 | 122.5891 | -121.7285 | 0.73242 | -0.20325 | 0.049973 | 0.0599 | 0.0048963 | 0.027833 | -0.0087992 | 0.025733 | -0.13855 | 0.010388 | 0.023637 | 0.033434 | -0.0013181 | 0.016464 | 0.059509 | 0.1236 | 0.11902 | 0.07782 | 0.086975 | 0.036621 | -0.11902 | 0.09613 | 0.16937 | 0.050354 | 0.036621 | 0.018311 | -0.045776 | -0.091553 | 121.7651 | 121.6095 | -0.64545 | 121.8521 | 121.8063 | 0.19684 | -0.67291 | 121.6827 | 121.637 | -0.6958 | 121.8246 | 121.7789 | 0.14191 | -0.71411 | 121.8155 | 121.788 | 121.8475 | -0.85144 | 121.7651 | 121.7468 | 121.8979 | -0.82398
6638.1562 | 122.7173 | -121.6919 | 0.70038 | -0.14221 | 0.047623 | 0.06225 | 0.0019055 | 0.025697 | -0.0092264 | 0.02616 | -0.13092 | 0.010175 | 0.023424 | 0.032793 | -3.629e-05 | 0.016037 | 0.09613 | 0.17395 | 0.13275 | 0.086975 | 0.082397 | 0.041199 | -0.11444 | 0.14191 | 0.19226 | 0.07782 | 0.059509 | 0.022888 | -0.018311 | -0.086975 | 121.7331 | 121.5775 | -0.61798 | 121.8658 | 121.7789 | 0.20142 | -0.60425 | 121.6736 | 121.6049 | -0.64087 | 121.8338 | 121.7697 | 0.16479 | -0.67749 | 121.7743 | 121.788 | 121.8246 | -0.81482 | 121.7514 | 121.7148 | 121.8842 | -0.78735
6639.8594 | 122.731 | -121.7102 | 0.68665 | -0.058289 | 0.044205 | 0.061395 | 0.0029737 | 0.02527 | -0.0085856 | 0.024024 | -0.062256 | 0.010175 | 0.021501 | 0.034929 | -0.00089089 | 0.017532 | 0.068665 | 0.10986 | 0.091553 | 0.059509 | 0.086975 | 0.036621 | -0.11444 | 0.13733 | 0.16022 | 0.064087 | 0.050354 | 0.045776 | -0.022888 | -0.082397 | 121.7468 | 121.5958 | -0.59967 | 121.8201 | 121.7697 | 0.17395 | -0.61798 | 121.6873 | 121.6278 | -0.63629 | 121.8475 | 121.7743 | 0.14648 | -0.64087 | 121.7972 | 121.7789 | 121.8018 | -0.80109 | 121.7606 | 121.756 | 121.8704 | -0.76904
6641.6094 | 122.5845 | -121.7239 | 0.74158 | -0.18799 | 0.049759 | 0.057977 | 0.0046827 | 0.023561 | -0.002604 | 0.025306 | -0.22247 | 0.011457 | 0.021928 | 0.034716 | 0.00017731 | 0.017105 | 0.10529 | 0.10529 | 0.091553 | 0.082397 | 0.10071 | 0.032043 | -0.12817 | 0.10071 | 0.11902 | 0 | 0.054932 | 0.041199 | -0.036621 | -0.082397 | 121.756 | 121.5958 | -0.64087 | 121.8292 | 121.8063 | 0.21057 | -0.63629 | 121.6873 | 121.6415 | -0.68665 | 121.8246 | 121.7239 | 0.082397 | -0.70038 | 121.8246 | 121.8292 | 121.8155 | -0.86975 | 121.7789 | 121.7651 | 121.843 | -0.82397
6643.3125 | 122.6944 | -121.7102 | 0.69122 | -0.012512 | 0.048691 | 0.056696 | 0.0034009 | 0.02527 | -0.0064492 | 0.025306 | 0.036926 | 0.010388 | 0.023424 | 0.034289 | 0.00017731 | 0.016891 | 0.045776 | 0.068665 | 0.064087 | 0.027466 | 0.09613 | 0.022888 | -0.13275 | 0.073242 | 0.082397 | 0.018311 | 0.050354 | 0.032043 | -0.041199 | -0.091553 | 121.7331 | 121.5775 | -0.59509 | 121.7789 | 121.7377 | 0.16022 | -0.64545 | 121.669 | 121.6187 | -0.64087 | 121.7834 | 121.7285 | 0.10986 | -0.65918 | 121.8063 | 121.756 | 121.7743 | -0.82397 | 121.7606 | 121.7422 | 121.7926 | -0.78278
6645.0938 | 122.58 | -121.7468 | 0.74616 | -0.21088 | 0.052536 | 0.0599 | 0.0048963 | 0.026765 | -0.0036722 | 0.025519 | -0.2301 | 0.012952 | 0.023637 | 0.034075 | 0.00081811 | 0.014968 | 0.09613 | 0.10529 | 0.073242 | 0.068665 | 0.10071 | 0.022888 | -0.10986 | 0.07782 | 0.10071 | -0.018311 | 0.073242 | 0.045776 | -0.050354 | -0.09613 | 121.7697 | 121.637 | -0.64545 | 121.8521 | 121.8155 | 0.17853 | -0.65003 | 121.6965 | 121.6507 | -0.67291 | 121.8246 | 121.7285 | 0.077819 | -0.70038 | 121.8475 | 121.843 | 121.8201 | -0.85602 | 121.8201 | 121.7926 | 121.8475 | -0.84228
6646.7969 | 122.6715 | -121.7194 | 0.68207 | 0.048523 | 0.049118 | 0.060327 | 0.0023329 | 0.025056 | -0.004954 | 0.025092 | 0.052185 | 0.012311 | 0.023424 | 0.03258 | 0.0016727 | 0.018814 | 0.073242 | 0.086975 | 0.068665 | 0.045776 | 0.091553 | 0.032043 | -0.12817 | 0.10986 | 0.10071 | 0.013733 | 0.041199 | 0.050354 | -0.022888 | -0.07782 | 121.7514 | 121.5912 | -0.59052 | 121.8063 | 121.7651 | 0.17395 | -0.60883 | 121.6965 | 121.6415 | -0.64087 | 121.8292 | 121.7331 | 0.091553 | -0.63171 | 121.8109 | 121.7926 | 121.788 | -0.81024 | 121.7606 | 121.7697 | 121.8201 | -0.75989
6648.5156 | 122.6303 | -121.7285 | 0.72784 | -0.18036 | 0.053177 | 0.059473 | 0.0025465 | 0.028901 | 0.0023092 | 0.027228 | -0.26825 | 0.012097 | 0.025346 | 0.037066 | 0.0033817 | 0.013259 | 0.045776 | 0.018311 | -0.013733 | 0.022888 | 0.12817 | 0 | -0.15106 | 0.073242 | 0.059509 | -0.059509 | 0.09613 | 0.059509 | -0.068665 | -0.10071 | 121.7285 | 121.5775 | -0.59967 | 121.7468 | 121.7514 | 0.17395 | -0.68207 | 121.6599 | 121.6278 | -0.63171 | 121.8018 | 121.669 | 0.041199 | -0.66834 | 121.8567 | 121.7743 | 121.7148 | -0.87891 | 121.8246 | 121.788 | 121.788 | -0.82855
6650.2188 | 122.7036 | -121.7239 | 0.70496 | -0.13458 | 0.049332 | 0.061395 | 0.0034009 | 0.027833 | -0.0070902 | 0.024665 | -0.085144 | 0.0099612 | 0.022356 | 0.035998 | -0.0011045 | 0.017105 | 0.091553 | 0.16937 | 0.12817 | 0.068665 | 0.09613 | 0.027466 | -0.1236 | 0.16937 | 0.19684 | 0.086975 | 0.050354 | 0.027466 | -0.022888 | -0.068665 | 121.7514 | 121.6003 | -0.60883 | 121.8933 | 121.7926 | 0.19226 | -0.6134 | 121.7011 | 121.6553 | -0.6546 | 121.8933 | 121.8109 | 0.15564 | -0.67749 | 121.8201 | 121.8155 | 121.8521 | -0.82855 | 121.7743 | 121.7514 | 121.9208 | -0.77362
6651.9375 | 122.7219 | -121.701 | 0.66834 | 0.14771 | 0.049759 | 0.056696 | 0.00019645 | 0.024842 | -0.0019632 | 0.027869 | 0.12848 | 0.012097 | 0.024278 | 0.036852 | 0.0044497 | 0.015823 | 0.050354 | 0.073242 | 0.027466 | 0.041199 | 0.11444 | 0.009155 | -0.12817 | 0.15106 | 0.11902 | -0.004578 | 0.064087 | 0.022888 | -0.045776 | -0.068665 | 121.7102 | 121.5729 | -0.55389 | 121.7743 | 121.7422 | 0.16937 | -0.61798 | 121.6553 | 121.6324 | -0.60425 | 121.8521 | 121.6965 | 0.064087 | -0.64545 | 121.8155 | 121.7514 | 121.7285 | -0.79651 | 121.7651 | 121.7239 | 121.8201 | -0.737
6653.7031 | 122.7173 | -121.7331 | 0.68207 | -0.0048827 | 0.045273 | 0.060541 | 0.0034009 | 0.024201 | -0.0075174 | 0.026374 | 0.044556 | 0.011029 | 0.022996 | 0.035143 | 0.0029543 | 0.018814 | 0.018311 | 0.07782 | 0.059509 | 0.050354 | 0.10071 | 0.032043 | -0.11902 | 0.086975 | 0.10986 | 0.041199 | 0.054932 | 0.041199 | -0.022888 | -0.068665 | 121.7651 | 121.6141 | -0.58136 | 121.8109 | 121.7834 | 0.16937 | -0.66376 | 121.7102 | 121.6644 | -0.62714 | 121.8201 | 121.7743 | 0.10986 | -0.64087 | 121.8338 | 121.7514 | 121.7926 | -0.80109 | 121.788 | 121.7743 | 121.843 | -0.75073
6655.4062 | 122.6852 | -121.7102 | 0.70038 | -0.020142 | 0.047409 | 0.059686 | 0.00062385 | 0.023347 | -0.0064492 | 0.027228 | 0.044556 | 0.011884 | 0.021715 | 0.034502 | 0.0031681 | 0.018173 | 0.022888 | 0.068665 | 0.068665 | 0.036621 | 0.10529 | 0.018311 | -0.12817 | 0.09613 | 0.086975 | 0.018311 | 0.054932 | 0.032043 | -0.041199 | -0.082397 | 121.7285 | 121.582 | -0.59509 | 121.7789 | 121.7468 | 0.1648 | -0.67749 | 121.669 | 121.6278 | -0.64545 | 121.8063 | 121.7285 | 0.10071 | -0.66833 | 121.8155 | 121.7331 | 121.7789 | -0.82855 | 121.7651 | 121.7422 | 121.7972 | -0.78277
6657.1094 | 122.6898 | -121.7285 | 0.70953 | -0.0048827 | 0.046341 | 0.057977 | 0.00062385 | 0.027192 | -0.0047404 | 0.025733 | 0.029297 | 0.010602 | 0.022142 | 0.036425 | 0.0018863 | 0.017105 | 0.059509 | 0.059509 | 0.050354 | 0.059509 | 0.09613 | 0.018311 | -0.12817 | 0.082397 | 0.082397 | 0.009155 | 0.059509 | 0.032043 | -0.018311 | -0.086975 | 121.7468 | 121.6003 | -0.6134 | 121.788 | 121.788 | 0.18768 | -0.65002 | 121.7102 | 121.6415 | -0.65002 | 121.8109 | 121.7377 | 0.09613 | -0.67749 | 121.8246 | 121.788 | 121.7789 | -0.83771 | 121.788 | 121.7606 | 121.8109 | -0.79651
6658.8125 | 122.6212 | -121.7422 | 0.71411 | -0.19562 | 0.051468 | 0.059473 | 0.0074597 | 0.02591 | 0.0012412 | 0.027656 | -0.26062 | 0.011884 | 0.024492 | 0.034929 | 0.0016727 | 0.013046 | 0.041199 | 0 | -0.013733 | 0.018311 | 0.12817 | -0.009155 | -0.14648 | 0.041199 | 0.054932 | -0.064087 | 0.09613 | 0.059509 | -0.068665 | -0.10071 | 121.7331 | 121.5958 | -0.58594 | 121.7422 | 121.7606 | 0.16479 | -0.67291 | 121.6736 | 121.6415 | -0.61798 | 121.7834 | 121.6782 | 0.036621 | -0.6546 | 121.8704 | 121.7834 | 121.7285 | -0.86059 | 121.8384 | 121.8018 | 121.7972 | -0.81482
6660.5625 | 122.5891 | -121.7468 | 0.70496 | 0.033264 | 0.052536 | 0.059045 | -0.0017261 | 0.022492 | 0.0016684 | 0.028937 | 0.0064086 | 0.013166 | 0.023851 | 0.034502 | 0.0080813 | 0.017532 | 0.009155 | -0.004578 | -0.059509 | -0.009155 | 0.13275 | -0.009155 | -0.16022 | 0.036621 | -0.004578 | -0.10529 | 0.07782 | 0.059509 | -0.059509 | -0.11902 | 121.7377 | 121.5866 | -0.57221 | 121.7422 | 121.7377 | 0.15106 | -0.6958 | 121.6873 | 121.6278 | -0.62714 | 121.7834 | 121.6415 | 0.013733 | -0.64545 | 121.8796 | 121.756 | 121.6873 | -0.86517 | 121.8246 | 121.8063 | 121.7422 | -0.82398
6662.2656 | 122.699 | -121.7102 | 0.66834 | 0.10193 | 0.049759 | 0.057336 | -0.00065795 | 0.023133 | -0.0017496 | 0.030433 | 0.14374 | 0.014447 | 0.022996 | 0.036425 | 0.0033817 | 0.017532 | 0.022888 | 0.027466 | -0.018311 | 0.009155 | 0.10986 | 0.009155 | -0.13733 | 0.091553 | 0.07782 | -0.027466 | 0.059509 | 0.059509 | -0.050354 | -0.10071 | 121.7194 | 121.5729 | -0.55847 | 121.7377 | 121.7194 | 0.14648 | -0.64545 | 121.6599 | 121.6095 | -0.60883 | 121.8018 | 121.6827 | 0.073242 | -0.60883 | 121.8201 | 121.7331 | 121.6919 | -0.80566 | 121.7697 | 121.7697 | 121.788 | -0.76904
6664.0781 | 122.6028 | -121.7468 | 0.73242 | -0.23376 | 0.048691 | 0.060754 | 0.0051099 | 0.029115 | -0.0045266 | 0.027228 | -0.26062 | 0.014234 | 0.022996 | 0.034929 | 0.0031681 | 0.020523 | -0.004578 | 0.018311 | -0.018311 | 0 | 0.1236 | -0.018311 | -0.16479 | 0.022888 | 0.045776 | -0.068665 | 0.10071 | 0.068665 | -0.059509 | -0.10529 | 121.7285 | 121.582 | -0.60883 | 121.7651 | 121.7468 | 0.16479 | -0.737 | 121.6873 | 121.6415 | -0.63171 | 121.7697 | 121.6782 | 0.036621 | -0.66376 | 121.8704 | 121.7422 | 121.7285 | -0.89722 | 121.8475 | 121.8155 | 121.7926 | -0.83771
6665.8438 | 122.699 | -121.7422 | 0.66376 | 0.11719 | 0.049118 | 0.059259 | 0.00019645 | 0.026338 | -0.0017496 | 0.028083 | 0.17426 | 0.012097 | 0.021074 | 0.034502 | 0.0020999 | 0.014968 | 0.10529 | 0.12817 | 0.10529 | 0.091553 | 0.082397 | 0.041199 | -0.09613 | 0.15564 | 0.14191 | 0.036621 | 0.036621 | 0.032043 | -0.013733 | -0.073242 | 121.7834 | 121.6461 | -0.58136 | 121.8704 | 121.8338 | 0.18768 | -0.55847 | 121.7285 | 121.669 | -0.62714 | 121.8979 | 121.7789 | 0.10986 | -0.63171 | 121.8246 | 121.8475 | 121.8475 | -0.75989 | 121.7789 | 121.7743 | 121.8842 | -0.737
6667.625 | 122.6349 | -121.7606 | 0.72784 | -0.22614 | 0.054673 | 0.056909 | 0.0036145 | 0.02591 | -0.0019632 | 0.027869 | -0.19958 | 0.014234 | 0.025133 | 0.037066 | 0.00060451 | 0.013687 | 0.013733 | -0.009155 | -0.027466 | 0.009155 | 0.13733 | -0.018311 | -0.15564 | 0.022888 | 0.045776 | -0.07782 | 0.09613 | 0.064087 | -0.059509 | -0.10986 | 121.7422 | 121.6049 | -0.59052 | 121.7514 | 121.7697 | 0.16479 | -0.71411 | 121.701 | 121.6507 | -0.63171 | 121.7834 | 121.6827 | 0.032043 | -0.66376 | 121.8979 | 121.7743 | 121.7331 | -0.88348 | 121.8567 | 121.8246 | 121.8063 | -0.83771
6669.4062 | 122.5891 | -121.7651 | 0.71869 | -0.088806 | 0.051041 | 0.056909 | 0.0034009 | 0.029542 | -0.00046778 | 0.02851 | -0.11566 | 0.012311 | 0.021715 | 0.036638 | 0.0057315 | 0.015609 | 0.073242 | 0.068665 | 0.013733 | 0.032043 | 0.12817 | 0.018311 | -0.14648 | 0.073242 | 0.07782 | -0.059509 | 0.064087 | 0.050354 | -0.054932 | -0.11444 | 121.7834 | 121.6187 | -0.59052 | 121.8338 | 121.7972 | 0.17853 | -0.64545 | 121.7102 | 121.6507 | -0.6546 | 121.8384 | 121.7056 | 0.054932 | -0.66834 | 121.8933 | 121.8384 | 121.7789 | -0.86517 | 121.8292 | 121.8155 | 121.843 | -0.83313
6671.1094 | 122.6166 | -121.7377 | 0.74616 | -0.26428 | 0.049973 | 0.0599 | 0.0046827 | 0.027406 | -0.0053812 | 0.026588 | -0.20721 | 0.01402 | 0.025346 | 0.038347 | -0.00067729 | 0.016677 | -0.018311 | 0.009155 | -0.022888 | 0 | 0.12817 | -0.009155 | -0.15564 | 0.013733 | 0.041199 | -0.07782 | 0.10986 | 0.068665 | -0.068665 | -0.14191 | 121.7285 | 121.582 | -0.61798 | 121.7468 | 121.7377 | 0.15564 | -0.76447 | 121.669 | 121.5958 | -0.63629 | 121.7514 | 121.6599 | 0.064087 | -0.67749 | 121.8658 | 121.7194 | 121.7148 | -0.9018 | 121.8475 | 121.8063 | 121.7789 | -0.88806
6672.875 | 122.7173 | -121.6965 | 0.6958 | 0.14771 | 0.046555 | 0.057336 | -0.00044435 | 0.023347 | -0.0036722 | 0.027228 | 0.067444 | 0.014447 | 0.021715 | 0.036211 | 0.0042361 | 0.018386 | 0.073242 | 0.091553 | 0.054932 | 0.073242 | 0.10071 | 0.041199 | -0.12817 | 0.12817 | 0.1236 | 0.045776 | 0.036621 | 0.036621 | -0.041199 | -0.07782 | 121.7377 | 121.5683 | -0.59509 | 121.788 | 121.7697 | 0.20142 | -0.62256 | 121.6553 | 121.6187 | -0.65918 | 121.8246 | 121.7422 | 0.1236 | -0.65918 | 121.7972 | 121.7697 | 121.7514 | -0.82398 | 121.7331 | 121.7331 | 121.8201 | -0.77362
6674.6719 | 122.6303 | -121.7514 | 0.72327 | 0.056152 | 0.049973 | 0.058191 | 0.0016919 | 0.025056 | -0.0034586 | 0.028724 | 0.067444 | 0.01402 | 0.022356 | 0.035784 | 0.0050907 | 0.018386 | 0.013733 | -0.032043 | -0.036621 | 0.009155 | 0.1236 | -0.004578 | -0.14191 | 0.027466 | -0.009155 | -0.073242 | 0.091553 | 0.068665 | -0.050354 | -0.10986 | 121.7468 | 121.6095 | -0.59967 | 121.7194 | 121.7606 | 0.15106 | -0.70953 | 121.701 | 121.6415 | -0.63171 | 121.7789 | 121.6782 | 0.036621 | -0.6546 | 121.875 | 121.7651 | 121.7148 | -0.86517 | 121.843 | 121.8201 | 121.7422 | -0.83313
6676.3906 | 122.6486 | -121.7331 | 0.70953 | 0.08667 | 0.050186 | 0.057977 | 0.00041005 | 0.026551 | -0.0040994 | 0.028937 | 0.059815 | 0.013593 | 0.022142 | 0.035143 | 0.0048769 | 0.018386 | 0.013733 | -0.022888 | -0.036621 | 0.004578 | 0.12817 | 0.004578 | -0.14191 | 0.022888 | 0 | -0.073242 | 0.091553 | 0.073242 | -0.054932 | -0.11444 | 121.7377 | 121.5912 | -0.58136 | 121.7102 | 121.7377 | 0.14649 | -0.6958 | 121.6782 | 121.6187 | -0.61798 | 121.756 | 121.6599 | 0.041199 | -0.63629 | 121.8613 | 121.7468 | 121.6965 | -0.85144 | 121.8246 | 121.8063 | 121.7331 | -0.82398
6678.1562 | 122.6212 | -121.7239 | 0.74158 | -0.18036 | 0.049759 | 0.058618 | 0.0044691 | 0.023774 | -0.0092264 | 0.027228 | -0.14618 | 0.010175 | 0.023637 | 0.036211 | -0.00024989 | 0.018814 | 0.073242 | 0.13275 | 0.10071 | 0.07782 | 0.091553 | 0.032043 | -0.11902 | 0.086975 | 0.16479 | 0.032043 | 0.045776 | 0.050354 | -0.032043 | -0.082397 | 121.756 | 121.6049 | -0.65002 | 121.8567 | 121.8018 | 0.19684 | -0.66834 | 121.6919 | 121.6415 | -0.6958 | 121.8109 | 121.756 | 0.11444 | -0.69122 | 121.8155 | 121.7972 | 121.8246 | -0.8606 | 121.7697 | 121.7743 | 121.8887 | -0.82397
6679.9219 | 122.5891 | -121.7789 | 0.737 | -0.1651 | 0.050186 | 0.059473 | 0.0051099 | 0.025697 | -0.0036722 | 0.025947 | -0.20721 | 0.010816 | 0.024705 | 0.035998 | -0.00046349 | 0.018386 | 0.004578 | 0.022888 | -0.018311 | -0.009155 | 0.11444 | 0.004578 | -0.16937 | 0.013733 | 0.045776 | -0.045776 | 0.09613 | 0.073242 | -0.068665 | -0.11902 | 121.7834 | 121.6095 | -0.62256 | 121.8018 | 121.7697 | 0.16022 | -0.73242 | 121.7102 | 121.6599 | -0.64087 | 121.7926 | 121.7331 | 0.073243 | -0.66376 | 121.8933 | 121.7834 | 121.7606 | -0.90637 | 121.875 | 121.8521 | 121.8246 | -0.85602
6681.7031 | 122.6257 | -121.7468 | 0.73242 | -0.26428 | 0.052109 | 0.059045 | 0.0044691 | 0.027406 | -0.0045266 | 0.025947 | -0.23773 | 0.014447 | 0.023851 | 0.035784 | -0.0011045 | 0.017532 | 0.009155 | 0 | -0.041199 | -0.013733 | 0.14648 | -0.004578 | -0.16022 | 0.018311 | 0.041199 | -0.068665 | 0.09613 | 0.07782 | -0.059509 | -0.10071 | 121.7422 | 121.5866 | -0.58594 | 121.7468 | 121.7331 | 0.14648 | -0.72327 | 121.6873 | 121.6461 | -0.63629 | 121.7651 | 121.6782 | 0.032043 | -0.6546 | 121.8933 | 121.756 | 121.7056 | -0.89264 | 121.843 | 121.8246 | 121.788 | -0.83313
6683.4688 | 122.6898 | -121.7194 | 0.70953 | 0.11719 | 0.046982 | 0.055414 | 0.0023329 | 0.026551 | -0.0058084 | 0.027442 | 0.13611 | 0.0097476 | 0.02321 | 0.035998 | 0.0012455 | 0.017959 | 0.10071 | 0.12817 | 0.10529 | 0.059509 | 0.086975 | 0.045776 | -0.10071 | 0.12817 | 0.14648 | 0.045776 | 0.050354 | 0.027466 | -0.004578 | -0.07782 | 121.7651 | 121.6187 | -0.62256 | 121.8475 | 121.7789 | 0.16022 | -0.60883 | 121.7148 | 121.6415 | -0.65918 | 121.8475 | 121.7651 | 0.1236 | -0.68207 | 121.8063 | 121.8201 | 121.8246 | -0.81024 | 121.7697 | 121.7468 | 121.8658 | -0.78735
6685.1719 | 122.6532 | -121.7422 | 0.70496 | -0.18036 | 0.048264 | 0.056909 | 0.0055371 | 0.027833 | -0.0081582 | 0.025306 | -0.16144 | 0.012525 | 0.022783 | 0.034289 | 0.0016727 | 0.014328 | 0.073242 | 0.16937 | 0.10529 | 0.082397 | 0.086975 | 0.027466 | -0.11444 | 0.13733 | 0.1831 | 0.068665 | 0.050354 | 0.013733 | -0.041199 | -0.068665 | 121.7697 | 121.6278 | -0.61798 | 121.9116 | 121.8246 | 0.19684 | -0.63171 | 121.701 | 121.6736 | -0.6546 | 121.8796 | 121.8109 | 0.13733 | -0.69122 | 121.8292 | 121.8155 | 121.8475 | -0.8194 | 121.7926 | 121.756 | 121.9254 | -0.77362
6686.9375 | 122.6486 | -121.7285 | 0.71869 | -0.21088 | 0.050186 | 0.058832 | 0.0034009 | 0.026551 | -0.0064492 | 0.027228 | -0.15381 | 0.010816 | 0.021287 | 0.036638 | 0.0025271 | 0.01625 | 0.09613 | 0.16479 | 0.11444 | 0.07782 | 0.073242 | 0.045776 | -0.11444 | 0.1236 | 0.17395 | 0.054932 | 0.036621 | 0.022888 | -0.027466 | -0.082397 | 121.7743 | 121.6141 | -0.64545 | 121.8933 | 121.8063 | 0.19226 | -0.62256 | 121.701 | 121.6461 | -0.68207 | 121.8521 | 121.7834 | 0.13733 | -0.6958 | 121.8018 | 121.8246 | 121.843 | -0.83313 | 121.7651 | 121.7514 | 121.9025 | -0.80109
6688.7031 | 122.6852 | -121.6965 | 0.70038 | 0.14771 | 0.048264 | 0.056268 | -0.0019397 | 0.023561 | -0.0028178 | 0.027015 | 0.12848 | 0.012952 | 0.022783 | 0.035784 | 0.0042361 | 0.015823 | 0.10986 | 0.12817 | 0.11444 | 0.073242 | 0.073242 | 0.041199 | -0.10529 | 0.16937 | 0.12817 | 0.068665 | 0.032043 | 0.036621 | -0.027466 | -0.068665 | 121.7377 | 121.5912 | -0.62714 | 121.8246 | 121.7697 | 0.17853 | -0.59051 | 121.669 | 121.6278 | -0.66833 | 121.8658 | 121.7651 | 0.13733 | -0.66376 | 121.7697 | 121.8063 | 121.8109 | -0.80566 | 121.7285 | 121.7331 | 121.8246 | -0.76904
6690.4062 | 122.6578 | -121.7285 | 0.71869 | -0.21088 | 0.049759 | 0.059686 | 0.0055371 | 0.024629 | -0.0068766 | 0.02616 | -0.14618 | 0.010388 | 0.022569 | 0.035784 | -0.00024989 | 0.015823 | 0.09613 | 0.14648 | 0.11444 | 0.086975 | 0.091553 | 0.054932 | -0.11902 | 0.14191 | 0.16937 | 0.045776 | 0.045776 | 0.022888 | -0.036621 | -0.07782 | 121.7834 | 121.6095 | -0.62714 | 121.875 | 121.8155 | 0.20599 | -0.62256 | 121.6919 | 121.6507 | -0.67291 | 121.8704 | 121.7743 | 0.1236 | -0.6958 | 121.8201 | 121.8246 | 121.843 | -0.83771 | 121.7743 | 121.7514 | 121.8979 | -0.79651
6692.1719 | 122.7219 | -121.7285 | 0.70496 | -0.14221 | 0.047623 | 0.060114 | 0.0029737 | 0.025056 | -0.0087992 | 0.026374 | -0.13855 | 0.008893 | 0.022356 | 0.035357 | 0.00081811 | 0.015823 | 0.1236 | 0.17853 | 0.11444 | 0.09613 | 0.091553 | 0.045776 | -0.10529 | 0.14191 | 0.17395 | 0.073242 | 0.041199 | 0.018311 | -0.027466 | -0.09613 | 121.7743 | 121.6232 | -0.6134 | 121.907 | 121.8246 | 0.20142 | -0.58136 | 121.701 | 121.6324 | -0.66376 | 121.8704 | 121.8018 | 0.16937 | -0.68665 | 121.8201 | 121.8521 | 121.843 | -0.81024 | 121.7697 | 121.7468 | 121.9025 | -0.80109
6693.9375 | 122.5891 | -121.7651 | 0.73242 | -0.088806 | 0.050827 | 0.056268 | 0.0010511 | 0.026551 | 0.0031638 | 0.028724 | -0.11566 | 0.015088 | 0.02086 | 0.03792 | 0.0055179 | 0.017105 | 0.091553 | 0.050354 | 0.013733 | 0.032043 | 0.12817 | 0.004578 | -0.14648 | 0.07782 | 0.041199 | -0.07782 | 0.091553 | 0.059509 | -0.059509 | -0.10071 | 121.7697 | 121.6187 | -0.60425 | 121.8155 | 121.7972 | 0.17853 | -0.64087 | 121.7056 | 121.6644 | -0.64087 | 121.843 | 121.6873 | 0.022888 | -0.67291 | 121.8933 | 121.8567 | 121.7789 | -0.87891 | 121.8567 | 121.8246 | 121.8063 | -0.83313
6695.7188 | 122.7127 | -121.7056 | 0.67749 | 0.08667 | 0.050186 | 0.058191 | 0.00041005 | 0.023347 | -0.0028178 | 0.028937 | 0.090332 | 0.011457 | 0.025133 | 0.036638 | 0.0044497 | 0.016677 | 0.022888 | 0.004578 | -0.022888 | -0.004578 | 0.12817 | 0.004578 | -0.13733 | 0.086975 | 0.027466 | -0.050354 | 0.082397 | 0.064087 | -0.045776 | -0.10071 | 121.7102 | 121.5683 | -0.54932 | 121.7102 | 121.701 | 0.13275 | -0.6546 | 121.6599 | 121.6049 | -0.59509 | 121.7926 | 121.6553 | 0.050354 | -0.6134 | 121.8338 | 121.7285 | 121.6827 | -0.81482 | 121.788 | 121.7697 | 121.7331 | -0.7782
6697.4062 | 122.6578 | -121.7422 | 0.71411 | -0.18036 | 0.053177 | 0.058832 | 0.0078871 | 0.026124 | -0.0021768 | 0.02851 | -0.23773 | 0.012952 | 0.025346 | 0.035998 | 0.0016727 | 0.014755 | 0.018311 | 0.018311 | -0.022888 | 0.013733 | 0.12817 | -0.009155 | -0.14191 | 0.045776 | 0.073242 | -0.054932 | 0.09613 | 0.064087 | -0.064087 | -0.10071 | 121.7331 | 121.6003 | -0.58594 | 121.7606 | 121.756 | 0.15564 | -0.6958 | 121.6782 | 121.6415 | -0.61798 | 121.788 | 121.6873 | 0.045776 | -0.65002 | 121.8704 | 121.7606 | 121.7194 | -0.85602 | 121.8384 | 121.8063 | 121.8155 | -0.81482
6699.1719 | 122.6898 | -121.7239 | 0.68207 | 0.079041 | 0.049759 | 0.057977 | -0.00044435 | 0.025697 | -0.0011088 | 0.028724 | 0.036926 | 0.012738 | 0.023851 | 0.037066 | 0.0038089 | 0.016677 | 0.018311 | 0.004578 | -0.032043 | -0.004578 | 0.13733 | 0.004578 | -0.14648 | 0.050354 | 0.013733 | -0.082397 | 0.064087 | 0.064087 | -0.073242 | -0.10071 | 121.7285 | 121.5775 | -0.54474 | 121.7285 | 121.7194 | 0.14191 | -0.66376 | 121.6507 | 121.6232 | -0.61798 | 121.7743 | 121.6415 | 0.018311 | -0.61798 | 121.8613 | 121.7422 | 121.6919 | -0.82855 | 121.788 | 121.788 | 121.7377 | -0.78278
6700.9531 | 122.6578 | -121.7377 | 0.72327 | -0.19562 | 0.049118 | 0.057977 | 0.0031873 | 0.028688 | -0.003245 | 0.027656 | -0.16144 | 0.012097 | 0.022996 | 0.035143 | 0.0053043 | 0.014328 | 0.018311 | 0.041199 | -0.004578 | 0.036621 | 0.1236 | 0.004578 | -0.13275 | 0.050354 | 0.07782 | -0.041199 | 0.073242 | 0.064087 | -0.064087 | -0.11902 | 121.7422 | 121.6049 | -0.59967 | 121.7789 | 121.7743 | 0.16937 | -0.70496 | 121.6736 | 121.6187 | -0.65002 | 121.788 | 121.6965 | 0.07782 | -0.65918 | 121.8613 | 121.756 | 121.7331 | -0.85602 | 121.8109 | 121.8018 | 121.8155 | -0.84229
6702.7188 | 122.7219 | -121.7148 | 0.70496 | -0.0048827 | 0.045487 | 0.058832 | 0.0029737 | 0.024201 | -0.0090128 | 0.025092 | 0.082703 | 0.010816 | 0.022996 | 0.035357 | 0.00081811 | 0.020309 | 0.032043 | 0.073242 | 0.041199 | 0.050354 | 0.10071 | 0.036621 | -0.11902 | 0.059509 | 0.10529 | 0.022888 | 0.059509 | 0.068665 | -0.013733 | -0.07782 | 121.7514 | 121.5958 | -0.60425 | 121.788 | 121.7651 | 0.16937 | -0.67291 | 121.701 | 121.637 | -0.64545 | 121.7743 | 121.7377 | 0.10071 | -0.63629 | 121.8155 | 121.7468 | 121.756 | -0.82398 | 121.7743 | 121.7834 | 121.8201 | -0.78278
6704.4219 | 122.7219 | -121.7102 | 0.69122 | -0.15747 | 0.04805 | 0.058832 | 0.0010511 | 0.025483 | -0.0090128 | 0.024665 | -0.11566 | 0.0097476 | 0.021715 | 0.033221 | -0.0011045 | 0.014968 | 0.11444 | 0.16022 | 0.13275 | 0.091553 | 0.07782 | 0.027466 | -0.10986 | 0.14191 | 0.20142 | 0.07782 | 0.054932 | 0.027466 | -0.032043 | -0.073242 | 121.7377 | 121.6003 | -0.6134 | 121.8704 | 121.8018 | 0.20142 | -0.57678 | 121.6782 | 121.637 | -0.63629 | 121.8521 | 121.788 | 0.15106 | -0.66376 | 121.788 | 121.8246 | 121.843 | -0.80109 | 121.7651 | 121.7377 | 121.9116 | -0.76447
6706.1875 | 122.7219 | -121.7422 | 0.6958 | -0.11932 | 0.049332 | 0.058405 | 0.0042555 | 0.027619 | -0.006022 | 0.024879 | -0.10803 | 0.0099612 | 0.020647 | 0.034502 | 0.0016727 | 0.016464 | 0.11902 | 0.15106 | 0.12817 | 0.086975 | 0.086975 | 0.041199 | -0.10529 | 0.12817 | 0.16937 | 0.07782 | 0.041199 | 0.045776 | -0.036621 | -0.07782 | 121.7834 | 121.637 | -0.60883 | 121.8933 | 121.8292 | 0.19226 | -0.57678 | 121.7056 | 121.6644 | -0.6546 | 121.8704 | 121.8201 | 0.15564 | -0.65002 | 121.8292 | 121.8613 | 121.8704 | -0.80109 | 121.7834 | 121.788 | 121.9116 | -0.77362
6707.8906 | 122.6898 | -121.7514 | 0.71411 | -0.1651 | 0.049118 | 0.058832 | 0.0036145 | 0.026979 | -0.006663 | 0.025947 | -0.15381 | 0.011457 | 0.023851 | 0.033861 | 0.00081811 | 0.01625 | 0.10986 | 0.14191 | 0.11902 | 0.086975 | 0.086975 | 0.036621 | -0.11902 | 0.1236 | 0.18768 | 0.059509 | 0.045776 | 0.027466 | -0.018311 | -0.054932 | 121.788 | 121.6324 | -0.62714 | 121.8933 | 121.8384 | 0.20599 | -0.60425 | 121.7331 | 121.6965 | -0.66834 | 121.875 | 121.8109 | 0.11444 | -0.68665 | 121.8384 | 121.8613 | 121.8704 | -0.83313 | 121.7972 | 121.7789 | 121.9391 | -0.76904
6709.6719 | 122.6028 | -121.8018 | 0.73242 | -0.20325 | 0.048691 | 0.0599 | -0.00065795 | 0.027192 | -0.0055948 | 0.025519 | -0.25299 | 0.010816 | 0.021715 | 0.033861 | 0.0016727 | 0.016677 | 0.082397 | 0.10529 | 0.07782 | 0.059509 | 0.091553 | 0.018311 | -0.11902 | 0.073242 | 0.11444 | -0.022888 | 0.059509 | 0.050354 | -0.059509 | -0.1236 | 121.8201 | 121.6827 | -0.64087 | 121.907 | 121.8613 | 0.17853 | -0.65003 | 121.7422 | 121.6782 | -0.67291 | 121.875 | 121.7789 | 0.10071 | -0.68207 | 121.8933 | 121.8842 | 121.8796 | -0.85144 | 121.8613 | 121.8521 | 121.9162 | -0.85602
6711.4375 | 122.5983 | -121.7972 | 0.71411 | -0.088806 | 0.050614 | 0.057977 | 0.0010511 | 0.02591 | 0.00060022 | 0.030006 | -0.13855 | 0.013379 | 0.022783 | 0.037279 | 0.0076541 | 0.015396 | 0.10529 | 0.073242 | 0.018311 | 0.027466 | 0.11444 | 0.013733 | -0.13733 | 0.086975 | 0.045776 | -0.073242 | 0.07782 | 0.064087 | -0.045776 | -0.09613 | 121.8109 | 121.6599 | -0.59967 | 121.8704 | 121.8246 | 0.16479 | -0.60883 | 121.7514 | 121.701 | -0.63629 | 121.8842 | 121.7239 | 0.022888 | -0.65002 | 121.9116 | 121.9025 | 121.8155 | -0.85144 | 121.875 | 121.8613 | 121.843 | -0.81024
6713.1562 | 122.5891 | -121.7743 | 0.70038 | 0.048523 | 0.052323 | 0.054773 | 0.0023329 | 0.028474 | -0.00046778 | 0.03086 | -0.024109 | 0.014661 | 0.023851 | 0.035784 | 0.0033817 | 0.0186 | 0.027466 | -0.018311 | -0.036621 | -0.004578 | 0.11902 | 0.004578 | -0.14648 | 0.013733 | 0.013733 | -0.10986 | 0.10071 | 0.07782 | -0.064087 | -0.10529 | 121.7789 | 121.6278 | -0.58136 | 121.756 | 121.7697 | 0.14191 | -0.67291 | 121.7102 | 121.669 | -0.59967 | 121.788 | 121.6644 | -0.004577 | -0.62256 | 121.8933 | 121.8018 | 121.7377 | -0.84686 | 121.875 | 121.8521 | 121.788 | -0.80566
6714.9375 | 122.6532 | -121.756 | 0.72784 | -0.20325 | 0.050614 | 0.058191 | 0.0048963 | 0.02591 | -0.002604 | 0.027656 | -0.20721 | 0.013379 | 0.024705 | 0.036638 | 0.00039091 | 0.017959 | 0.004578 | 0.027466 | -0.032043 | 0.009155 | 0.10529 | 0 | -0.16022 | 0.022888 | 0.064087 | -0.082397 | 0.073242 | 0.064087 | -0.068665 | -0.10529 | 121.756 | 121.5958 | -0.62256 | 121.7834 | 121.7651 | 0.16937 | -0.72327 | 121.6873 | 121.6507 | -0.6546 | 121.7789 | 121.6736 | 0.022889 | -0.66376 | 121.8613 | 121.7606 | 121.7239 | -0.88806 | 121.8292 | 121.8201 | 121.8201 | -0.83313
6716.7031 | 122.7402 | -121.7422 | 0.68665 | -0.012512 | 0.046128 | 0.058832 | 0.0027601 | 0.024842 | -0.0085856 | 0.024665 | 0.036926 | 0.01167 | 0.022142 | 0.033007 | -0.00067729 | 0.016464 | 0.022888 | 0.091553 | 0.054932 | 0.050354 | 0.10529 | 0.027466 | -0.11444 | 0.091553 | 0.1236 | 0.036621 | 0.041199 | 0.054932 | -0.036621 | -0.07782 | 121.7697 | 121.6278 | -0.58136 | 121.8338 | 121.7926 | 0.16479 | -0.66376 | 121.7056 | 121.6644 | -0.64545 | 121.8338 | 121.7789 | 0.11444 | -0.63171 | 121.8475 | 121.7651 | 121.7972 | -0.80109 | 121.7834 | 121.7972 | 121.8658 | -0.76447
6718.4688 | 122.731 | -121.7102 | 0.68207 | 0.12482 | 0.050614 | 0.059045 | 0.0025465 | 0.026765 | -0.0034586 | 0.028297 | 0.090332 | 0.011029 | 0.024065 | 0.035143 | 0.0040225 | 0.014968 | 0.10986 | 0.091553 | 0.073242 | 0.086975 | 0.082397 | 0.050354 | -0.10529 | 0.14191 | 0.11444 | 0.027466 | 0.022888 | 0.022888 | -0.027466 | -0.059509 | 121.7606 | 121.6049 | -0.59967 | 121.8018 | 121.7972 | 0.19226 | -0.5722 | 121.6827 | 121.6507 | -0.65918 | 121.8521 | 121.7377 | 0.086975 | -0.65918 | 121.7926 | 121.8201 | 121.7834 | -0.78735 | 121.7331 | 121.7331 | 121.8246 | -0.74158
6720.1719 | 122.7448 | -121.7285 | 0.68665 | -0.065918 | 0.0457 | 0.059259 | 0.0019055 | 0.026979 | -0.0081582 | 0.026374 | -0.046997 | 0.0091066 | 0.022783 | 0.033648 | -0.0021725 | 0.017532 | 0.059509 | 0.091553 | 0.082397 | 0.068665 | 0.10529 | 0.041199 | -0.11902 | 0.11444 | 0.16937 | 0.068665 | 0.041199 | 0.027466 | -0.004578 | -0.073242 | 121.7697 | 121.6095 | -0.58136 | 121.8201 | 121.7972 | 0.18768 | -0.62714 | 121.7239 | 121.6553 | -0.64545 | 121.843 | 121.7972 | 0.14191 | -0.65918 | 121.8338 | 121.788 | 121.8109 | -0.80566 | 121.7697 | 121.756 | 121.8979 | -0.75989

## Thermal Data
Fire Time | A Position - Middle
-0.824 | 14.5974
0.176 | 14.6021
1.176 | 14.6035
2.176 | 14.5998
3.176 | 15.8467
4.176 | 24.1941
5.176 | 75.6817
6.176 | 125.1002
7.176 | 171.0603
8.176 | 235.8329
9.176 | 272.7015
10.176 | 292.705
11.176 | 331.7906
12.176 | 363.0439
13.176 | 401.9252
14.176 | 445.7763
15.176 | 470.2591
16.176 | 499.3719
17.176 | 534.0854
18.176 | 547.0071
19.176 | 572.4352
20.1917 | 592.3685
21.176 | 601.55
22.176 | 575.231
23.176 | 544.5007
24.176 | 517.2794
25.176 | 491.4691
26.176 | 467.2013
27.176 | 445.4239
28.176 | 424.6221
29.176 | 406.1741
30.176 | 390.3865
31.176 | 375.0042
32.176 | 360.4217
33.176 | 347.2752
34.176 | 333.4999
35.176 | 321.9357
36.176 | 312.365
37.176 | 301.4327
38.176 | 290.4635
39.176 | 281.7924
40.176 | 274.6901
41.176 | 266.4722
42.176 | 257.3537
43.176 | 250.505
44.176 | 243.4414
45.176 | 237.0907
46.176 | 231.8668
47.176 | 228.3067
48.176 | 223.9734
49.176 | 219.7054
50.1917 | 215.0432
51.176 | 210.4843
52.176 | 206.8332
53.176 | 202.5424
54.176 | 199.1132
55.176 | 196.5114
56.176 | 192.8739
57.176 | 189.543
58.176 | 185.9531
59.176 | 183.3884
60.176 | 181.613
61.176 | 179.3229
62.176 | 176.8805
63.176 | 174.467
64.176 | 172.7977
65.176 | 170.9575
66.176 | 169.9712
67.176 | 169.0198
68.176 | 167.9003
69.176 | 167.7536
70.176 | 167.716
71.176 | 167.1633
72.176 | 167.6075
73.176 | 168.3032
74.176 | 168.0317
75.176 | 167.8261
76.176 | 169.1113
77.176 | 168.5801
78.176 | 168.8154
79.176 | 168.408
80.176 | 168.0698
81.176 | 167.8955
82.176 | 167.2181
83.176 | 169.0081
84.176 | 168.11
85.176 | 168.0089
86.176 | 168.1319
87.176 | 167.9652
88.176 | 168.5189
89.176 | 168.0579
90.176 | 170.0289
91.176 | 172.7381
92.176 | 175.029
93.176 | 176.8192
94.176 | 177.2703
95.176 | 178.0541
96.176 | 182.9193
97.176 | 184.3078
98.176 | 185.1999
99.176 | 185.6368
100.176 | 187.648
101.176 | 191.4394
102.176 | 195.5721
103.176 | 197.2138
104.176 | 197.9922
105.176 | 199.9803
106.176 | 201.7736
107.176 | 203.3357
108.176 | 202.6431
109.176 | 203.5792
110.176 | 203.3548
111.176 | 204.3948
112.176 | 203.6665
113.176 | 204.1564
114.176 | 203.379
115.176 | 206.3786
116.176 | 203.9346
117.176 | 202.4652
118.176 | 201.6092
119.176 | 200.8861
120.176 | 201.2786
121.176 | 201.3081
122.176 | 200.512
123.176 | 199.5924
124.176 | 197.415
125.176 | 196.66
126.176 | 196.1483
127.176 | 196.0408
128.176 | 194.841
129.176 | 194.1698
130.176 | 193.8522
131.176 | 194.0384
132.176 | 193.6364
133.176 | 193.2731
134.176 | 192.8322
135.176 | 193.6136
136.176 | 195.2143
137.176 | 195.1866
138.176 | 194.3946
139.176 | 193.9043
140.176 | 193.3676
141.176 | 192.5621
142.176 | 190.5677
143.176 | 189.8709
144.176 | 189.3413
145.176 | 188.3774
146.176 | 186.5467
147.176 | 184.7447
148.176 | 183.2552
149.176 | 181.877
150.176 | 179.7803
151.176 | 178.8665
152.176 | 178.8875
153.176 | 179.5321
154.176 | 179.2533
155.176 | 178.4886
156.176 | 178.0174
157.176 | 178.2354
158.176 | 178.9041
159.176 | 181.1594
160.176 | 182.095
161.176 | 182.8672
162.176 | 183.8417
163.176 | 184.4135
164.176 | 185.2967
165.176 | 184.1036
166.176 | 182.7196
167.176 | 182.2494
168.176 | 182.0087
169.176 | 181.7288
170.176 | 182.1133
171.176 | 181.6552
172.176 | 181.3283
173.176 | 181.641
174.176 | 181.525
175.176 | 181.5872
176.176 | 180.2342
177.176 | 179.8338
178.176 | 178.768
179.176 | 177.2469
180.176 | 176.3778
181.176 | 176.0532
182.176 | 176.718
183.176 | 176.5472
184.176 | 177.4263
185.176 | 176.7752
186.176 | 177.214
187.176 | 177.3372
188.176 | 176.5929
189.176 | 177.1552
190.176 | 176.7722
191.176 | 176.2661
192.176 | 176.2988
193.176 | 176.4797
194.176 | 180.5747
195.176 | 180.9709
196.176 | 181.0967
197.176 | 181.0319
198.176 | 180.4158
199.176 | 180.5533
200.1917 | 182.9309
201.176 | 183.6228
202.176 | 183.4819
203.176 | 184.1455
204.176 | 186.3758
205.176 | 186.5494
206.176 | 188.2468
207.176 | 188.2043
208.176 | 188.7156
209.176 | 188.5034
210.176 | 188.4163
211.176 | 189.5974
212.176 | 192.4238
213.176 | 192.5362
214.176 | 191.7959
215.176 | 191.0976
216.176 | 192.0032
217.176 | 190.436
218.176 | 190.18
219.176 | 190.0977
220.176 | 190.5381
221.176 | 193.3239
222.176 | 195.4017
223.176 | 196.2621
224.176 | 196.6068
225.176 | 197.5989
226.176 | 197.2192
227.176 | 196.3667
228.176 | 195.5817
229.176 | 194.923
230.176 | 193.9742
231.176 | 193.5343
232.176 | 192.9048
233.176 | 192.8061
234.176 | 193.4086
235.176 | 191.5031
236.176 | 192.4609
237.176 | 192.6156
238.176 | 193.2115
239.176 | 193.2144
240.176 | 192.1352
241.176 | 190.8415
242.176 | 189.535
243.176 | 187.724
244.176 | 187.7378
245.176 | 187.3969
246.176 | 186.9679
247.176 | 186.817
248.176 | 186.2548
249.176 | 186.5773
250.176 | 187.033
251.176 | 187.466
252.176 | 187.5512
253.176 | 188.5882
254.176 | 189.4786
255.176 | 190.0354
256.176 | 190.9036
257.176 | 190.7433
258.176 | 190.2056
259.176 | 190.8595
260.176 | 190.9334
261.176 | 191.1686
262.176 | 190.5994
263.176 | 191.9353
264.176 | 193.3936
265.176 | 196.2832
266.176 | 197.0326
267.176 | 196.8013
268.176 | 197.8077
269.176 | 197.7064
270.176 | 197.3804
271.176 | 197.9867
272.176 | 197.4424
273.176 | 199.6293
274.176 | 199.321
275.176 | 198.1087
276.176 | 197.5141
277.176 | 197.3728
278.176 | 197.969
279.176 | 197.8692
280.176 | 198.4718
281.176 | 198.9301
282.176 | 200.0151
283.176 | 199.55
284.176 | 200.153
285.176 | 201.1756
286.176 | 201.5907
287.176 | 202.5111
288.176 | 203.8544
289.176 | 204.5104
290.176 | 206.6885
291.176 | 208.2661
292.176 | 208.9959
293.176 | 208.3704
294.176 | 207.5615
295.176 | 206.4902
296.176 | 205.919
297.176 | 205.628
298.176 | 204.727
299.176 | 205.5194
300.176 | 205.0129
301.176 | 203.6735
302.176 | 203.4294
303.176 | 203.449
304.176 | 202.6173
305.176 | 201.99
306.176 | 201.8814
307.176 | 204.9336
308.176 | 206.421
309.176 | 206.2464
310.176 | 207.0483
311.176 | 205.4129
312.176 | 206.1935
313.176 | 207.2889
314.176 | 207.3605
315.176 | 205.5355
316.176 | 205.8308
317.176 | 203.6703
318.176 | 202.8263
319.176 | 202.7207
320.176 | 201.1533
321.176 | 200.0682
322.176 | 197.8847
323.176 | 196.1902
324.176 | 195.39
325.176 | 194.514
326.176 | 193.8863
327.176 | 193.5485
328.176 | 192.2553
329.176 | 191.9887
330.176 | 191.6605
331.176 | 191.9088
332.176 | 191.5413
333.176 | 192.4124
334.176 | 193.7372
335.176 | 193.173
336.176 | 193.1751
337.176 | 193.9417
338.176 | 194.5263
339.176 | 194.1948
340.176 | 193.2552
341.176 | 192.2033
342.176 | 192.4267
343.176 | 192.2341
344.176 | 192.125
345.176 | 193.8586
346.176 | 194.7611
347.176 | 196.1836
348.176 | 196.733
349.176 | 197.1922
350.176 | 198.1945
351.176 | 200.0714
352.176 | 200.8463
353.176 | 200.924
354.176 | 201.1545
355.176 | 200.8101
356.176 | 199.7026
357.176 | 198.2972
358.176 | 197.4508
359.176 | 197.7134
360.176 | 197.4927
361.176 | 195.7968
362.176 | 194.5712
363.176 | 194.327
364.176 | 193.351
365.176 | 194.1039
366.176 | 194.1109
367.176 | 193.5112
368.176 | 193.4633
369.176 | 193.4273
370.176 | 194.3835
371.176 | 195.9764
372.176 | 197.1772
373.176 | 199.4737
374.176 | 199.6877
375.176 | 199.7299
376.176 | 200.027
377.176 | 200.1556
378.176 | 200.1882
379.176 | 200.731
380.176 | 201.8937
381.176 | 203.2421
382.176 | 203.3942
383.176 | 203.7056
384.176 | 202.8631
385.176 | 202.3739
386.176 | 201.2026
387.176 | 200.6527
388.176 | 200.5346
389.176 | 201.2899
390.176 | 202.6472
391.176 | 202.4221
392.176 | 202.1748
393.176 | 202.7681
394.176 | 204.34
395.176 | 204.5987
396.176 | 205.3363
397.176 | 206.1207
398.176 | 206.766
399.176 | 206.8225
400.176 | 206.3617
401.176 | 206.0014
402.176 | 204.9856
403.176 | 203.3994
404.176 | 203.9902
405.176 | 203.9516
406.176 | 203.0786
407.176 | 202.7179
408.176 | 202.8919
409.176 | 201.8255
410.176 | 201.9599
411.176 | 200.8472
412.176 | 200.9629
413.176 | 199.5043
414.176 | 199.489
415.176 | 199.7342
416.176 | 199.3393
417.1917 | 199.3649
418.176 | 200.8913
419.176 | 199.785
420.1917 | 199.978
421.176 | 200.1941
422.176 | 200.4056
423.1917 | 200.9264
424.1917 | 201.7606
425.176 | 202.3414
426.176 | 203.0875
427.176 | 203.6091
428.176 | 203.1853
429.176 | 203.8614
430.176 | 204.0243
431.176 | 203.9333
432.176 | 205.2377
433.176 | 205.9782
434.176 | 207.7349
435.176 | 208.798
436.176 | 209.236
437.1917 | 209.2603
438.176 | 208.0715
439.176 | 209.171
440.176 | 210.465
441.176 | 212.2561
442.176 | 211.4059
443.176 | 210.3582
444.176 | 210.3486
445.176 | 210.8734
446.176 | 211.3944
447.176 | 212.0186
448.176 | 211.3277
449.176 | 211.1933
450.176 | 210.6357
451.176 | 210.4012
452.176 | 210.6398
453.176 | 211.4551
454.176 | 211.6709
455.176 | 212.419
456.176 | 210.7527
457.176 | 211.0848
458.176 | 210.4951
459.176 | 209.4204
460.176 | 208.398
461.176 | 208.4824
462.176 | 207.6763
463.176 | 208.0331
464.176 | 208.0549
465.176 | 208.7116
466.176 | 207.8613
467.176 | 210.512
468.176 | 212.7835
469.176 | 213.56
470.176 | 214.2305
471.176 | 213.9423
472.176 | 213.3243
473.176 | 211.4722
474.176 | 210.2412
475.1917 | 208.9941
476.176 | 208.7877
477.176 | 208.9649
478.176 | 208.4553
479.176 | 208.2795
480.1917 | 207.6481
481.1917 | 207.1827
482.176 | 206.4887
483.176 | 205.8888
484.176 | 207.3727
485.176 | 206.817
486.176 | 206.6904
487.176 | 207.5693
488.176 | 207.6317
489.176 | 208.5675
490.176 | 209.0575
491.176 | 209.1361
492.176 | 208.4935
493.176 | 208.1133
494.176 | 207.3976
495.176 | 207.5931
496.176 | 206.0171
497.176 | 205.7172
498.176 | 205.1101
499.176 | 205.7086
500.176 | 205.3856
501.176 | 204.9014
502.176 | 204.2346
503.176 | 204.4906
504.176 | 203.0529
505.176 | 203.4184
506.176 | 204.9845
507.176 | 205.5333
508.176 | 205.7951
509.176 | 205.315
510.176 | 205.2711
511.176 | 205.1537
512.176 | 205.9806
513.176 | 205.5094
514.176 | 205.5406
515.176 | 204.9609
516.176 | 205.1312
517.176 | 203.6555
518.176 | 204.0153
519.176 | 204.1567
520.176 | 204.6754
521.176 | 203.5468
522.176 | 202.6379
523.176 | 202.1863
524.176 | 201.153
525.176 | 201.2196
526.176 | 201.0544
527.176 | 201.6568
528.176 | 201.2802
529.176 | 200.6023
530.176 | 198.7806
531.176 | 199.6468
532.176 | 199.7492
533.176 | 199.5208
534.176 | 198.4262
535.176 | 198.2394
536.176 | 197.8252
537.176 | 197.3051
538.176 | 196.7986
539.176 | 196.5188
540.176 | 195.9334
541.176 | 196.4188
542.176 | 196.3452
543.176 | 199.0416
544.176 | 200.1515
545.176 | 201.4024
546.176 | 201.8702
547.176 | 201.652
548.176 | 200.1149
549.176 | 200.0354
550.176 | 200.3872
551.176 | 200.6955
552.176 | 200.8988
553.176 | 201.2242
554.176 | 201.2687
555.176 | 201.4417
556.176 | 201.557
557.176 | 202.5337
558.176 | 202.1329
559.176 | 201.3969
560.176 | 202.4273
561.176 | 203.2429
562.176 | 203.5096
563.176 | 204.2562
564.176 | 204.2914
565.176 | 204.1636
566.176 | 204.4564
567.176 | 204.6064
568.176 | 205.5885
569.176 | 204.9615
570.176 | 204.9731
571.176 | 205.1719
572.176 | 205.0046
573.176 | 205.6014
574.176 | 203.9764
575.176 | 203.4301
576.176 | 203.8007
577.176 | 204.6774
578.176 | 204.2243
579.176 | 203.7835
580.176 | 203.8657
581.176 | 203.9115
582.176 | 203.9192
583.176 | 204.6366
584.176 | 205.8455
585.176 | 205.4888
586.176 | 205.5218
587.176 | 204.4211
588.176 | 203.8992
589.176 | 203.6011
590.176 | 203.0925
591.176 | 204.0897
592.176 | 205.6761
593.176 | 205.0071
594.176 | 204.4272
595.176 | 205.4098
596.176 | 205.3365
597.176 | 204.0232
598.176 | 203.354
599.176 | 203.6946
600.176 | 203.5834
601.176 | 203.5589
602.176 | 202.6261
603.176 | 202.4323
604.176 | 201.2356
605.176 | 201.0236
606.176 | 201.0951
607.176 | 201.0864
608.176 | 200.386
609.176 | 200.3766
610.176 | 200.5255
611.176 | 200.7784
612.176 | 200.3604
613.176 | 200.3914
614.176 | 200.3075
615.176 | 200.501
616.176 | 200.0202
617.176 | 200.0928
618.176 | 200.1277
619.176 | 200.2673
620.176 | 200.6903
621.176 | 200.8191
622.176 | 200.6793
623.176 | 200.514
624.176 | 199.7258
625.176 | 199.6712
626.176 | 200.0508
627.176 | 200.4927
628.176 | 201.3527
629.176 | 201.9175
630.176 | 201.7325
631.176 | 201.6259
632.176 | 201.5436
633.176 | 200.5757
634.176 | 201.3224
635.176 | 202.0429
636.176 | 202.3967
637.176 | 202.2661
638.176 | 202.0135
639.176 | 201.4112
640.176 | 201.8468
641.176 | 202.0967
642.176 | 202.1897
643.176 | 200.9758
644.176 | 199.7403
645.1917 | 200.2462
646.176 | 199.6618
647.176 | 199.6344
648.176 | 199.4052
649.176 | 199.825
650.176 | 201.3278
651.176 | 202.9416
652.176 | 203.7388
653.176 | 203.645
654.176 | 203.7069
655.176 | 204.7728
656.176 | 205.2312
657.176 | 205.5538
658.176 | 206.363
659.176 | 207.6497
660.176 | 208.1207
661.176 | 210.0719
662.176 | 210.1512
663.176 | 209.2668
664.176 | 209.0077
665.176 | 209.0274
666.176 | 209.93
667.176 | 209.7606
668.176 | 209.2705
669.176 | 210.027
670.176 | 209.7899
671.176 | 210.4643
672.176 | 211.2587
673.176 | 211.0551
674.176 | 211.6346
675.176 | 212.3083
676.176 | 211.4809
677.176 | 211.6892
678.176 | 212.6686
679.176 | 211.4925
680.176 | 211.5063
681.176 | 212.2312
682.176 | 211.517
683.176 | 211.1978
684.176 | 211.7626
685.176 | 212.383
686.176 | 212.0082
687.176 | 212.2459
688.176 | 212.7383
689.176 | 213.4308
690.176 | 215.2139
691.176 | 215.1833
692.176 | 215.9937
693.176 | 216.1485
694.176 | 216.5831
695.176 | 216.0987
696.176 | 215.3522
697.176 | 216.0127
698.176 | 217.5665
699.176 | 218.305
700.176 | 218.1974
701.176 | 219.4156
702.176 | 218.9788
703.176 | 218.6483
704.176 | 220.4092
705.176 | 219.838
706.176 | 219.4835
707.176 | 218.5678
708.176 | 220.9624
709.176 | 221.6485
710.176 | 222.0268
711.176 | 221.355
712.176 | 221.1324
713.176 | 220.7606
714.176 | 220.9456
715.176 | 221.0052
716.176 | 221.6978
717.176 | 220.7541
718.176 | 220.5095
719.176 | 220.792
720.176 | 222.3077
721.176 | 222.7505
722.176 | 223.2908
723.176 | 223.7599
724.176 | 223.2692
725.176 | 222.8913
726.176 | 222.467
727.176 | 223.2738
728.176 | 224.0057
729.176 | 226.5447
730.176 | 228.7428
731.176 | 227.4905
732.176 | 226.7867
733.176 | 227.244
734.176 | 227.0619
735.176 | 225.2495
736.176 | 225.3478
737.176 | 225.3933
738.176 | 225.8039
739.176 | 228.0223
740.176 | 228.2245
741.176 | 228.8153
742.176 | 231.8751
743.176 | 233.8231
744.176 | 234.5533
745.176 | 238.0389
746.176 | 241.1744
747.176 | 242.6079
748.176 | 243.5787
749.176 | 244.8934
750.176 | 244.579
751.176 | 245.1372
752.176 | 245.4679
753.176 | 248.3411
754.176 | 250.4539
755.176 | 251.1277
756.176 | 251.0289
757.176 | 250.5443
758.176 | 249.418
759.176 | 249.1836
760.176 | 248.8143
761.176 | 247.6712
762.176 | 248.5879
763.176 | 247.058
764.176 | 247.5385
765.176 | 249.0363
766.176 | 250.431
767.176 | 253.2409
768.176 | 252.728
769.176 | 251.961
770.176 | 251.2532
771.176 | 250.1438
772.176 | 252.7585
773.176 | 257.4405
774.176 | 257.2446
775.176 | 259.2421
776.176 | 261.2196
777.176 | 264.0516
778.176 | 263.788
779.176 | 264.0956
780.176 | 264.0712
781.176 | 264.5986
782.176 | 265.3907
783.176 | 265.7121
784.176 | 269.9923
785.176 | 268.1533
786.176 | 273.144
787.176 | 273.9289
788.176 | 273.6785
789.176 | 272.0569
790.176 | 271.0115
791.176 | 269.7414
792.176 | 270.6111
793.176 | 269.2597
794.176 | 269.6048
795.176 | 279.4741
796.176 | 278.8211
797.176 | 279.735
798.176 | 278.9942
799.176 | 281.6911
800.176 | 281.7653
801.176 | 279.9611
802.176 | 280.8793
803.176 | 280.1945
804.176 | 291.0026
805.176 | 288.2245
806.176 | 288.6007
807.176 | 290.1155
808.176 | 296.9772
809.176 | 297.9569
810.176 | 297.6464
811.176 | 296.8037
812.176 | 297.0759
813.176 | 301.6123
814.176 | 299.093
815.176 | 298.0629
816.176 | 296.9343
817.176 | 295.1933
818.176 | 292.6753
819.176 | 291.7421
820.176 | 293.0156
821.176 | 292.2771
822.176 | 293.3278
823.176 | 293.9974
824.176 | 295.3899
825.176 | 295.9602
826.176 | 295.0873
827.176 | 294.7248
828.176 | 295.0225
829.176 | 293.5584
830.176 | 296.2844
831.176 | 296.8405
832.176 | 300.495
833.176 | 315.8577
834.176 | 314.0716
835.176 | 315.7991
836.176 | 315.002
837.176 | 313.8625
838.176 | 313.8015
839.176 | 331.4882
840.176 | 338.795
841.176 | 337.5711
842.176 | 338.73
843.176 | 337.1154
844.176 | 333.5741
845.176 | 331.0322
846.176 | 326.3064
847.176 | 326.8376
848.176 | 326.7711
849.176 | 324.6374
850.176 | 324.5352
851.176 | 327.5093
852.176 | 327.7788
853.176 | 328.3375
854.176 | 324.6051
855.176 | 325.3001
856.176 | 324.2615
857.176 | 320.4439
858.176 | 319.241
859.176 | 319.1553
860.176 | 318.2383
861.176 | 316.5945
862.176 | 317.309
863.176 | 315.8979
864.176 | 318.0176
865.176 | 314.1307
866.176 | 312.2237
867.176 | 313.4308
868.176 | 310.9181
869.176 | 310.2669
870.176 | 321.3947
871.176 | 328.8581
872.176 | 335.222
873.176 | 335.6205
874.176 | 333.9058
875.176 | 332.1583
876.176 | 331.4405
877.176 | 340.9681
878.176 | 358.7184
879.176 | 357.0236
880.176 | 378.2223
881.176 | 404.0492
882.176 | 397.0972
883.176 | 397.9135
884.176 | 390.8807
885.176 | 385.5566
886.176 | 382.5598
887.176 | 377.5299
888.176 | 373.597
889.176 | 369.2846
890.176 | 366.0399
891.176 | 360.9454
892.176 | 357.7613
893.176 | 356.9121
894.176 | 373.4078
895.176 | 398.0729
896.176 | 391.5936
897.176 | 387.2933
898.176 | 378.6103
899.176 | 371.5306
900.176 | 365.7232
901.176 | 363.1544
902.176 | 359.0868
903.176 | 359.3156
904.176 | 353.9544
905.176 | 350.9853
906.176 | 346.362
907.176 | 343.9774
908.176 | 341.6469
909.176 | 339.2048
910.176 | 337.8255
911.176 | 335.581
912.176 | 335.5164
913.176 | 334.5879
914.176 | 334.9116
915.176 | 350.134
916.176 | 346.2533
917.176 | 357.2419
918.176 | 375.8783
919.176 | 382.5152
920.176 | 399.4424
921.176 | 419.2622
922.176 | 428.2665
923.176 | 437.9577
924.176 | 435.3609
925.176 | 435.1673
926.176 | 443.7116
927.176 | 442.0158
928.176 | 455.246
929.176 | 478.2569
930.176 | 462.7465
931.176 | 456.8328
932.176 | 448.0476
933.176 | 445.7201
934.176 | 451.7837
935.176 | 468.7457
936.176 | 495.1582
937.176 | 518.5931
938.176 | 537.3453
939.176 | 542.7801
940.176 | 549.2046
941.176 | 548.7039
942.176 | 532.7144
943.176 | 523.4486
944.176 | 512.2714
945.176 | 502
946.176 | 489.0372
947.176 | 484.4985
948.176 | 489.7995
949.176 | 494.2476
950.176 | 518.7165
951.176 | 534.9965
952.176 | 525.1842
953.176 | 522.3724
954.176 | 512.3835
955.176 | 505.366
956.176 | 501.3473
957.176 | 487.9709
958.176 | 480.5015
959.176 | 482.7203
960.176 | 473.5844
961.176 | 478.4207
962.176 | 485.3836
963.176 | 501.7514
964.176 | 513.2772
965.176 | 530.7187
966.176 | 539.8841
967.176 | 539.1615
968.176 | 537.5175
969.176 | 526.9025
970.176 | 546.5093
971.176 | 535.5806
972.176 | 524.7639
973.176 | 513.1374
974.176 | 535.9858
975.176 | 556.5954
976.176 | 561.9221
977.176 | 584.882
978.176 | 576.4172
979.176 | 570.0001
980.176 | 555.9503
981.176 | 543.4826
982.176 | 543.5168
983.176 | 534.7777
984.176 | 528.2109
985.176 | 535.8865
986.176 | 523.53
987.176 | 530.2208
988.176 | 532.3907
989.176 | 535.1802
990.176 | 555.843
991.176 | 541.112
992.176 | 537.456
993.176 | 535.0589
994.176 | 548.8992
995.176 | 568.3097
996.176 | 564.6162
997.176 | 562.0483
998.176 | 551.2777
999.176 | 551.6039
1000.176 | 565.6723
1001.176 | 572.5467
1002.176 | 589.9196
1003.176 | 574.4508
1004.176 | 574.1518
1005.176 | 569.0689
1006.176 | 571.6308
1007.176 | 566.6745
1008.176 | 563.137
1009.176 | 578.4577
1010.176 | 568.0853
1011.176 | 565.5672
1012.176 | 563.6667
1013.176 | 551.4355
1014.176 | 544.6465
1015.176 | 537.7632
1016.176 | 550.704
1017.176 | 560.3245
1018.176 | 583.1111
1019.176 | 594.0034
1020.176 | 602.2729
1021.176 | 613.0569
1022.176 | 613.3662
1023.176 | 636.3173
1024.176 | 628.1849
1025.176 | 622.7385
1026.176 | 615.6026
1027.176 | 607.0089
1028.176 | 596.9384
1029.176 | 612.053
1030.176 | 608.0907
1031.176 | 612.9777
1032.176 | 611.677
1033.176 | 631.3281
1034.176 | 638.8735
1035.176 | 624.8328
1036.176 | 623.3714
1037.176 | 616.043
1038.176 | 610.8168
1039.176 | 594.9634
1040.176 | 613.8119
1041.176 | 608.9136
1042.176 | 602.7266
1043.176 | 599.669
1044.176 | 594.8407
1045.176 | 595.8228
1046.176 | 597.8087
1047.176 | 589.3007
1048.176 | 606.0739
1049.176 | 604.7413
1050.176 | 594.4195
1051.176 | 592.6513
1052.176 | 581.9035
1053.176 | 586.8519
1054.176 | 571.1653
1055.176 | 574.2184
1056.176 | 569.3973
1057.176 | 575.249
1058.176 | 569.0622
1059.176 | 570.6842
1060.176 | 582.9943
1061.176 | 584.2474
1062.176 | 595.6895
1063.176 | 601.4226
1064.176 | 602.6316
1065.176 | 616.5371
1066.176 | 614.8186
1067.176 | 633.778
1068.176 | 620.2299
1069.176 | 602.5866
1070.176 | 609.6107
1071.1917 | 606.7282
1072.176 | 593.6877
1073.176 | 599.3681
1074.176 | 608.291
1075.176 | 613.8956
1076.176 | 602.8776
1077.176 | 609.2392
1078.176 | 626.7133
1079.176 | 631.2364
1080.176 | 632.5094
1081.176 | 640.4515
1082.176 | 642.2065
1083.176 | 652.3172
1084.176 | 649.7289
1085.176 | 634.8742
1086.176 | 627.3594
1087.176 | 611.3159
1088.176 | 607.9886
1089.176 | 612.5158
1090.176 | 607.5924
1091.176 | 618.9925
1092.176 | 627.8637
1093.176 | 645.4225
1094.176 | 651.9357
1095.176 | 640.9611
1096.176 | 637.1065
1097.176 | 641.7691
1098.176 | 641.6014
1099.176 | 652.367
1100.176 | 662.22
1101.1917 | 665.2093
1102.176 | 669.4627
1103.176 | 675.7148
1104.176 | 672.2127
1105.176 | 681.6229
1106.176 | 662.7682
1107.176 | 651.6127
1108.176 | 656.9892
1109.176 | 656.5274
1110.176 | 648.5611
1111.176 | 653.1215
1112.176 | 652.0842
1113.176 | 652.5089
1114.176 | 632.4449
1115.176 | 619.5229
1116.176 | 620.2662
1117.176 | 611.995
1118.176 | 601.1235
1119.176 | 612.7104
1120.176 | 604.7182
1121.176 | 610.3895
1122.176 | 612.339
1123.176 | 603.1526
1124.176 | 611.2578
1125.176 | 606.6089
1126.176 | 600.7793
1127.176 | 613.7342
1128.176 | 630.0666
1129.176 | 633.2371
1130.176 | 635.2841
1131.176 | 647.0766
1132.176 | 642.3743
1133.176 | 644.4833
1134.176 | 637.1836
1135.176 | 644.9541
1136.176 | 639.1762
1137.176 | 637.8471
1138.176 | 647.2961
1139.176 | 651.4503
1140.176 | 662.7268
1141.176 | 668.9093
1142.176 | 680.9947
1143.176 | 672.696
1144.176 | 665.657
1145.176 | 651.8
1146.176 | 651.8232
1147.176 | 640.3603
1148.176 | 624.4537
1149.176 | 614.6127
1150.176 | 617.3315
1151.176 | 612.5322
1152.176 | 628.8949
1153.176 | 633.6359
1154.176 | 627.9031
1155.176 | 631.9097
1156.176 | 618.1239
1157.176 | 626.9358
1158.176 | 632.6465
1159.176 | 631.9244
1160.176 | 613.6494
1161.176 | 623.8884
1162.176 | 621.1942
1163.176 | 607.4915
1164.176 | 605.114
1165.176 | 602.319
1166.176 | 608.5943
1167.176 | 612.6607
1168.176 | 626.229
1169.176 | 630.5502
1170.176 | 628.9679
1171.176 | 611.3616
1172.176 | 599.0612
1173.176 | 616.83
1174.176 | 597.9484
1175.176 | 609.7799
1176.176 | 617.5239
1177.176 | 618.153
1178.176 | 628.7123
1179.176 | 635.3515
1180.176 | 618.5491
1181.176 | 617.3102
1182.176 | 614.3182
1183.176 | 607.5303
1184.176 | 619.7466
1185.176 | 625.5436
1186.176 | 635.482
1187.176 | 646.9571
1188.176 | 630.6666
1189.176 | 625.0693
1190.176 | 636.5315
1191.1917 | 632.5043
1192.176 | 628.4869
1193.176 | 643.2455
1194.176 | 624.1449
1195.176 | 621.7528
1196.176 | 619.7253
1197.176 | 606.6833
1198.176 | 605.1368
1199.176 | 608.279
1200.176 | 620.8356
1201.176 | 630.6764
1202.176 | 636.1923
1203.176 | 643.5692
1204.176 | 624.6197
1205.176 | 616.4788
1206.176 | 611.837
1207.176 | 610.4146
1208.176 | 600.8525
1209.176 | 581.9261
1210.176 | 570.5391
1211.176 | 574.7804
1212.176 | 587.911
1213.176 | 572.7245
1214.176 | 552.4719
1215.176 | 534.6785
1216.176 | 520.4252
1217.176 | 505.5691
1218.176 | 489.7671
1219.176 | 480.7038
1220.176 | 481.4543
1221.176 | 503.881
1222.176 | 505.2652
1223.176 | 499.7295
1224.176 | 497.4765
1225.176 | 503.4625
1226.176 | 491.0365
1227.176 | 479.6416
1228.176 | 491.8458
1229.176 | 503.0373
1230.176 | 532.2708
1231.176 | 550.2257
1232.176 | 534.2854
1233.176 | 516.5736
1234.176 | 502.1486
1235.176 | 488.0059
1236.176 | 478.1522
1237.176 | 470.4278
1238.176 | 459.1492
1239.176 | 449.4575
1240.176 | 445.5889
1241.176 | 440.1441
1242.176 | 434.1594
1243.176 | 430.607
1244.176 | 423.932
1245.176 | 416.7095
1246.176 | 411.5066
1247.176 | 410.8823
1248.176 | 433.5904
1249.176 | 432.8993
1250.176 | 429.3841
1251.176 | 445.9059
1252.176 | 457.3036
1253.176 | 472.796
1254.176 | 490.7862
1255.176 | 495.2904
1256.176 | 491.6399
1257.176 | 476.9189
1258.176 | 463.6925
1259.176 | 453.566
1260.176 | 444.4761
1261.176 | 440.3858
1262.176 | 432.1665
1263.176 | 427.3239
1264.176 | 422.9458
1265.176 | 418.3101
1266.176 | 417.0741
1267.176 | 415.9502
1268.176 | 424.6876
1269.176 | 432.5007
1270.176 | 427.9583
1271.176 | 427.2339
1272.176 | 426.6522
1273.176 | 424.9004
1274.176 | 447.5522
1275.176 | 439.2237
1276.176 | 433.6279
1277.176 | 428.4237
1278.176 | 421.0844
1279.176 | 420.1791
1280.176 | 418.5816
1281.176 | 414.14
1282.176 | 413.8051
1283.176 | 410.2385
1284.176 | 409.9945
1285.176 | 407.571
1286.176 | 403.1723
1287.176 | 396.4853
1288.176 | 393.9341
1289.176 | 402.0469
1290.176 | 422.5457
1291.176 | 440.5146
1292.176 | 457.6262
1293.176 | 446.4807
1294.176 | 470.7911
1295.176 | 478.3494
1296.176 | 488.861
1297.176 | 506.0498
1298.176 | 543.2959
1299.176 | 553.263
1300.176 | 546.0087
1301.176 | 531.2749
1302.176 | 512.0015
1303.176 | 495.6509
1304.176 | 483.3709
1305.176 | 483.8799
1306.176 | 476.1427
1307.176 | 468.5677
1308.176 | 460.8424
1309.176 | 453.4671
1310.176 | 445.086
1311.176 | 439.7065
1312.176 | 442.4226
1313.176 | 438.1804
1314.176 | 430.671
1315.176 | 425.1747
1316.176 | 422.1593
1317.176 | 421.1879
1318.176 | 421.6915
1319.176 | 418.59
1320.176 | 416.5723
1321.176 | 414.7172
1322.176 | 410.6534
1323.176 | 405.1825
1324.176 | 401.1465
1325.176 | 397.9295
1326.176 | 393.9615
1327.176 | 388.3571
1328.176 | 383.4559
1329.176 | 382.3431
1330.176 | 379.3051
1331.176 | 379.0598
1332.176 | 377.5827
1333.176 | 375.9298
1334.176 | 369.3824
1335.176 | 364.4768
1336.176 | 358.9002
1337.176 | 356.33
1338.176 | 353.3114
1339.176 | 349.7535
1340.176 | 347.9488
1341.176 | 347.227
1342.176 | 351.0509
1343.176 | 348.7167
1344.176 | 346.5127
1345.176 | 346.6786
1346.176 | 346.953
1347.176 | 347.6106
1348.176 | 347.9499
1349.176 | 347.9902
1350.176 | 344.1883
1351.176 | 343.7558
1352.176 | 345.3114
1353.176 | 358.2184
1354.176 | 358.8108
1355.176 | 356.3947
1356.176 | 356.5407
1357.176 | 353.7519
1358.176 | 353.0519
1359.176 | 356.0807
1360.176 | 372.384
1361.176 | 374.3394
1362.176 | 374.5317
1363.176 | 373.8712
1364.176 | 398.2802
1365.176 | 415.8781
1366.176 | 413.4698
1367.176 | 442.651
1368.176 | 446.3614
1369.176 | 464.2499
1370.176 | 456.7611
1371.176 | 446.2689
1372.176 | 441.3869
1373.176 | 433.5528
1374.176 | 426.3765
1375.176 | 422.8749
1376.176 | 416.6961
1377.176 | 411.6622
1378.176 | 411.8291
1379.176 | 409.2875
1380.176 | 405.9953
1381.176 | 402.8371
1382.176 | 420.744
1383.176 | 432.2797
1384.176 | 436.9804
1385.176 | 432.0905
1386.176 | 430.1328
1387.176 | 425.5276
1388.176 | 425.5483
1389.176 | 423.6261
1390.176 | 439.2473
1391.176 | 459.6969
1392.176 | 461.4206
1393.176 | 465.8394
1394.176 | 459.5791
1395.176 | 450.3595
1396.176 | 441.1436
1397.176 | 435.8517
1398.176 | 433.2701
1399.176 | 439.4408
1400.176 | 438.0932
1401.176 | 432.3306
1402.176 | 427.671
1403.176 | 422.9695
1404.176 | 420.843
1405.176 | 434.7223
1406.176 | 439.9227
1407.176 | 439.9261
1408.176 | 434.6951
1409.176 | 444.7459
1410.176 | 442.3053
1411.176 | 464.3118
1412.176 | 457.1762
1413.176 | 469.5432
1414.176 | 465.5561
1415.176 | 494.9122
1416.176 | 503.4507
1417.176 | 528.2432
1418.176 | 541.3959
1419.176 | 525.6961
1420.176 | 512.3457
1421.176 | 500.2102
1422.176 | 500.871
1423.176 | 508.2826
1424.176 | 508.0322
1425.176 | 520.8635
1426.176 | 510.6172
1427.176 | 498.4191
1428.176 | 488.7159
1429.176 | 477.3508
1430.176 | 469.5222
1431.176 | 458.6015
1432.176 | 452.0662
1433.176 | 444.8507
1434.176 | 437.1043
1435.176 | 431.0208
1436.176 | 424.0823
1437.176 | 422.4693
1438.176 | 417.5417
1439.176 | 412.096
1440.176 | 407.3409
1441.176 | 402.3491
1442.1917 | 396.6549
1443.176 | 393.6948
1444.176 | 390.4581
1445.176 | 393.2275
1446.176 | 394.7926
1447.176 | 394.8521
1448.176 | 395.3324
1449.176 | 396.327
1450.176 | 397.5896
1451.176 | 400.2781
1452.176 | 412.894
1453.176 | 422.6006
1454.176 | 417.8229
1455.176 | 413.3806
1456.176 | 409.6513
1457.176 | 411.4059
1458.176 | 407.2953
1459.176 | 405.8308
1460.176 | 412.026
1461.176 | 412.2646
1462.176 | 420.3912
1463.176 | 427.008
1464.176 | 421.4861
1465.176 | 416.1799
1466.176 | 412.1791
1467.176 | 407.5239
1468.176 | 406.9496
1469.176 | 412.7431
1470.176 | 410.3643
1471.176 | 406.3087
1472.176 | 406.2101
1473.176 | 411.9023
1474.176 | 455.1593
1475.176 | 446.5442
1476.176 | 442.513
1477.176 | 438.6185
1478.176 | 432.1446
1479.176 | 428.7845
1480.176 | 445.88
1481.176 | 439.8202
1482.176 | 447.4137
1483.176 | 449.8715
1484.176 | 448.4758
1485.176 | 454.0509
1486.176 | 466.6364
1487.176 | 493.2439
1488.176 | 499.0593
1489.176 | 497.7383
1490.176 | 500.6403
1491.176 | 522.3805
1492.176 | 525.7906
1493.176 | 511.8632
1494.176 | 500.6266
1495.176 | 494.435
1496.176 | 488.767
1497.176 | 483.304
1498.176 | 481.5986
1499.176 | 472.6187
1500.176 | 468.4615
1501.176 | 461.291
1502.176 | 460.0076
1503.176 | 458.9798
1504.176 | 468.7103
1505.176 | 463.6277
1506.176 | 459.7854
1507.176 | 454.7014
1508.176 | 447.8814
1509.176 | 444.1526
1510.176 | 459.8213
1511.176 | 483.5105
1512.176 | 484.3156
1513.176 | 518.184
1514.176 | 531.3597
1515.176 | 540.7074
1516.176 | 530.9698
1517.176 | 522.911
1518.176 | 522.7925
1519.176 | 513.9029
1520.176 | 521.7473
1521.176 | 516.4468
1522.176 | 506.5031
1523.176 | 499.4322
1524.176 | 519.4976
1525.176 | 552.7637
1526.176 | 547.8194
1527.176 | 538.7766
1528.176 | 527.1252
1529.176 | 519.4339
1530.176 | 513.4757
1531.176 | 508.89
1532.176 | 505.4053
1533.176 | 500.2151
1534.176 | 497.0864
1535.176 | 500.8423
1536.176 | 492.4713
1537.176 | 500.7264
1538.176 | 497.1595
1539.176 | 490.7419
1540.176 | 483.4585
1541.176 | 475.6772
1542.176 | 468.7284
1543.176 | 462.2465
1544.176 | 457.6137
1545.176 | 449.1902
1546.176 | 444.995
1547.176 | 446.8781
1548.176 | 440.4833
1549.176 | 446.1746
1550.176 | 445.5766
1551.176 | 441.5246
1552.176 | 445.9611
1553.176 | 444.8238
1554.176 | 446.0545
1555.176 | 451.9471
1556.176 | 457.6679
1557.176 | 455.6525
1558.176 | 451.9254
1559.1917 | 450.5219
1560.176 | 450.3528
1561.176 | 447.3662
1562.176 | 443.4145
1563.176 | 440.7003
1564.176 | 435.8771
1565.176 | 434.349
1566.176 | 429.9399
1567.176 | 432.3606
1568.176 | 446.1211
1569.176 | 453.7724
1570.176 | 474.85
1571.176 | 467.801
1572.176 | 477.4375
1573.176 | 490.4662
1574.176 | 483.4352
1575.176 | 475.6184
1576.176 | 471.8087
1577.176 | 462.8672
1578.176 | 463.6279
1579.176 | 469.6927
1580.176 | 466.0129
1581.176 | 470.8549
1582.176 | 470.9398
1583.176 | 463.3421
1584.176 | 458.7569
1585.176 | 466.0042
1586.176 | 462.0106
1587.176 | 463.8873
1588.176 | 466.9269
1589.176 | 484.2535
1590.176 | 486.6824
1591.176 | 485.8549
1592.176 | 482.4075
1593.176 | 476.4254
1594.176 | 478.2971
1595.176 | 475.6478
1596.176 | 501.5052
1597.176 | 492.2402
1598.176 | 485.4954
1599.176 | 481.8082
1600.176 | 484.9898
1601.176 | 483.6691
1602.176 | 480.9664
1603.176 | 480.8781
1604.176 | 474.0335
1605.176 | 473.2391
1606.176 | 465.8612
1607.176 | 455.0782
1608.176 | 451.4292
1609.176 | 452.9186
1610.176 | 454.6258
1611.176 | 452.7218
1612.176 | 450.9359
1613.176 | 448.9239
1614.176 | 457.1678
1615.176 | 469.2907
1616.176 | 475.7895
1617.176 | 475.5856
1618.176 | 477.8678
1619.176 | 474.5851
1620.176 | 467.9108
1621.176 | 470.7259
1622.176 | 479.927
1623.176 | 484.2318
1624.176 | 482.1028
1625.176 | 478.3838
1626.176 | 475.9873
1627.176 | 471.327
1628.176 | 470.508
1629.176 | 464.5219
1630.176 | 468.2499
1631.176 | 458.6676
1632.176 | 456.7739
1633.176 | 457.1703
1634.176 | 452.7602
1635.176 | 449.4323
1636.176 | 443.6065
1637.176 | 445.6603
1638.176 | 439.4722
1639.176 | 438.0991
1640.176 | 434.3067
1641.176 | 431.5983
1642.176 | 432.0868
1643.176 | 433.9301
1644.176 | 433.8501
1645.176 | 431.1775
1646.176 | 428.7862
1647.176 | 427.0435
1648.176 | 423.9441
1649.176 | 425.7864
1650.176 | 428.5026
1651.176 | 427.6996
1652.176 | 426.2416
1653.176 | 424.3642
1654.176 | 425.8266
1655.176 | 427.67
1656.176 | 431.7473
1657.176 | 432.4738
1658.176 | 435.8827
1659.176 | 440.9879
1660.176 | 445.8864
1661.176 | 449.3773
1662.176 | 448.4696
1663.176 | 446.9182
1664.176 | 447.336
1665.176 | 445.3305
1666.176 | 445.3783
1667.176 | 454.1077
1668.176 | 465.3426
1669.176 | 462.7458
1670.176 | 458.8869
1671.176 | 468.3332
1672.176 | 463.6915
1673.176 | 459.4387
1674.176 | 458.6221
1675.176 | 458.2317
1676.176 | 464.0434
1677.176 | 462.2117
1678.176 | 481.3838
1679.176 | 504.6574
1680.176 | 499.8218
1681.176 | 503.5684
1682.176 | 505.152
1683.176 | 498.6384
1684.176 | 493.7144
1685.176 | 489.3676
1686.176 | 516.6055
1687.176 | 515.0618
1688.176 | 518.5951
1689.176 | 512.8412
1690.176 | 506.4347
1691.176 | 499.4578
1692.176 | 493.3696
1693.176 | 486.0954
1694.176 | 482.1855
1695.176 | 477.3425
1696.176 | 474.0971
1697.176 | 471.6467
1698.176 | 477.3394
1699.176 | 479.4178
1700.176 | 478.0699
1701.176 | 473.0679
1702.176 | 472.9391
1703.176 | 484.4725
1704.176 | 495.9514
1705.176 | 491.7232
1706.176 | 489.0888
1707.176 | 487.5722
1708.176 | 480.0703
1709.176 | 479.1845
1710.176 | 473.7889
1711.176 | 468.532
1712.176 | 463.4093
1713.176 | 467.3122
1714.176 | 474.3523
1715.176 | 488.2574
1716.176 | 516.9414
1717.176 | 515.5188
1718.176 | 508.5318
1719.176 | 501.0254
1720.176 | 500.7481
1721.176 | 496.8514
1722.176 | 492.248
1723.176 | 499.2783
1724.176 | 501.0801
1725.176 | 505.0024
1726.176 | 499.1872
1727.176 | 492.3341
1728.176 | 485.7011
1729.176 | 487.4974
1730.176 | 487.5872
1731.176 | 485.8096
1732.176 | 479.5445
1733.176 | 477.9866
1734.176 | 478.7542
1735.176 | 475.5857
1736.176 | 471.9821
1737.176 | 473.3156
1738.176 | 471.3128
1739.176 | 471.2363
1740.176 | 474.3823
1741.176 | 469.7824
1742.176 | 464.6271
1743.176 | 462.9202
1744.176 | 459.4028
1745.176 | 451.4362
1746.176 | 451.3264
1747.176 | 449.38
1748.176 | 450.5619
1749.176 | 451.6659
1750.176 | 456.9716
1751.176 | 455.1592
1752.176 | 448.6069
1753.176 | 445.5651
1754.176 | 451.3529
1755.176 | 445.8436
1756.176 | 444.4649
1757.176 | 439.5234
1758.176 | 437.0599
1759.176 | 438.6778
1760.176 | 440.8439
1761.176 | 439.0116
1762.176 | 436.7328
1763.176 | 432.0013
1764.176 | 428.8619
1765.176 | 424.0667
1766.176 | 425.1334
1767.176 | 430.2265
1768.176 | 433.8984
1769.176 | 434.3241
1770.176 | 435.4694
1771.176 | 433.0772
1772.176 | 432.0481
1773.176 | 430.6808
1774.176 | 428.916
1775.176 | 430.327
1776.176 | 432.6982
1777.176 | 434.751
1778.176 | 433.165
1779.176 | 434.8469
1780.176 | 432.1797
1781.176 | 429.3872
1782.176 | 425.4282
1783.176 | 421.2875
1784.176 | 418.6641
1785.176 | 421.1048
1786.176 | 418.1175
1787.176 | 422.498
1788.176 | 426.218
1789.176 | 425.818
1790.176 | 428.2136
1791.176 | 446.3073
1792.176 | 449.5472
1793.176 | 446.4953
1794.176 | 446.3116
1795.176 | 440.1918
1796.176 | 433.3809
1797.176 | 431.0441
1798.176 | 431.1193
1799.176 | 429.6359
1800.176 | 428.6048
1801.176 | 430.1438
1802.1917 | 430.0562
1803.176 | 428.9159
1804.176 | 429.0758
1805.176 | 428.5474
1806.176 | 430.3191
1807.176 | 444.2719
1808.176 | 442.9004
1809.176 | 437.2495
1810.176 | 439.2963
1811.176 | 440.9326
1812.176 | 444.5448
1813.176 | 442.3831
1814.176 | 442.7276
1815.176 | 439.4314
1816.176 | 466.9838
1817.176 | 489.3973
1818.176 | 513.566
1819.176 | 510.6466
1820.176 | 522.1484
1821.176 | 533.9109
1822.176 | 551.7871
1823.176 | 556.5862
1824.176 | 566.2385
1825.176 | 584.0543
1826.176 | 593.7438
1827.176 | 585.6536
1828.176 | 575.8909
1829.176 | 559.4682
1830.176 | 551.155
1831.176 | 577.5185
1832.176 | 591.1785
1833.176 | 603.3995
1834.176 | 613.7075
1835.176 | 623.5158
1836.176 | 606.1786
1837.176 | 601.8467
1838.176 | 594.2728
1839.176 | 598.1195
1840.176 | 592.7986
1841.176 | 591.0893
1842.176 | 591.8318
1843.176 | 599.2523
1844.176 | 580.0008
1845.176 | 561.6945
1846.176 | 544.5005
1847.176 | 529.7969
1848.176 | 521.9383
1849.176 | 516.5469
1850.176 | 515.143
1851.176 | 514.1976
1852.176 | 532.4486
1853.176 | 524.5765
1854.176 | 520.2734
1855.176 | 516.7531
1856.176 | 506.855
1857.176 | 499.7182
1858.176 | 493.318
1859.176 | 483.5838
1860.176 | 478.7424
1861.176 | 472.8085
1862.176 | 463.7782
1863.176 | 455.4037
1864.176 | 453.0154
1865.176 | 451.8895
1866.176 | 451.8806
1867.176 | 450.8642
1868.176 | 444.7807
1869.176 | 438.9631
1870.176 | 439.5339
1871.176 | 441.204
1872.176 | 433.2488
1873.176 | 426.0514
1874.176 | 424.7058
1875.176 | 427.5772
1876.176 | 448.5985
1877.176 | 458.854
1878.176 | 462.4164
1879.176 | 466.2121
1880.176 | 471.1216
1881.176 | 475.1649
1882.176 | 482.7267
1883.176 | 485.3348
1884.176 | 490.1569
1885.176 | 507.7999
1886.176 | 511.3302
1887.176 | 522.41
1888.176 | 527.2266
1889.176 | 535.2865
1890.176 | 531.2561
1891.176 | 529.8692
1892.176 | 530.6803
1893.176 | 531.4143
1894.176 | 534.5632
1895.176 | 541.0905
1896.176 | 547.031
1897.176 | 548.7746
1898.176 | 552.3864
1899.176 | 550.7086
1900.176 | 553.8749
1901.176 | 556.1824
1902.176 | 567.9744
1903.176 | 572.1969
1904.176 | 568.7124
1905.176 | 573.2797
1906.176 | 574.8195
1907.176 | 567.9365
1908.176 | 574.6837
1909.176 | 582.2827
1910.176 | 579.389
1911.176 | 587.8485
1912.176 | 584.5604
1913.176 | 583.495
1914.176 | 577.0908
1915.176 | 585.158
1916.176 | 588.6963
1917.176 | 592.4273
1918.176 | 600.3871
1919.176 | 602.126
1920.176 | 605.1041
1921.176 | 622.602
1922.1917 | 633.7462
1923.176 | 631.0565
1924.176 | 637.1443
1925.176 | 643.7632
1926.176 | 645.0746
1927.176 | 652.8183
1928.176 | 658.8727
1929.176 | 667.8165
1930.176 | 658.7386
1931.176 | 661.5066
1932.176 | 663.1898
1933.176 | 657.9561
1934.176 | 650.8949
1935.176 | 650.2717
1936.176 | 646.7157
1937.176 | 653.7755
1938.176 | 657.7328
1939.176 | 659.8416
1940.176 | 659.3758
1941.176 | 643.2755
1942.176 | 638.4249
1943.176 | 642.6288
1944.176 | 634.074
1945.176 | 640.0621
1946.176 | 640.1764
1947.176 | 641.6021
1948.176 | 640.5696
1949.176 | 648.3788
1950.176 | 652.6963
1951.176 | 663.5142
1952.176 | 667.957
1953.176 | 651.67
1954.176 | 647.5011
1955.176 | 641.3882
1956.176 | 640.8453
1957.176 | 645.5181
1958.176 | 643.1618
1959.176 | 651.7273
1960.176 | 652.1724
1961.176 | 652.8172
1962.176 | 662.7534
1963.176 | 661.9264
1964.176 | 663.0024
1965.176 | 659.0671
1966.176 | 660.7134
1967.176 | 655.3218
1968.176 | 665.933
1969.176 | 666.762
1970.176 | 669.4154
1971.176 | 663.0493
1972.176 | 662.5473
1973.176 | 657.9086
1974.176 | 654.7797
1975.176 | 650.4172
1976.176 | 651.7546
1977.176 | 651.5915
1978.176 | 645.3307
1979.176 | 649.3292
1980.176 | 653.6937
1981.176 | 654.0374
1982.176 | 655.6377
1983.176 | 647.9637
1984.176 | 640.3921
1985.176 | 638.0044
1986.176 | 642.2115
1987.176 | 640.5999
1988.176 | 645.08
1989.176 | 644.4538
1990.176 | 644.8657
1991.176 | 639.7878
1992.176 | 626.6783
1993.176 | 622.3661
1994.176 | 616.4523
1995.176 | 614.9892
1996.176 | 622.4894
1997.176 | 633.8452
1998.176 | 641.9582
1999.176 | 640.2833
2000.176 | 632.8622
2001.176 | 633.4379
2002.176 | 624.1352
2003.176 | 631.8113
2004.176 | 626.3034
2005.176 | 616.4551
2006.176 | 624.2892
2007.176 | 632.401
2008.176 | 635.8473
2009.176 | 631.2989
2010.176 | 627.5752
2011.176 | 618.4868
2012.176 | 634.362
2013.176 | 634.1846
2014.176 | 645.346
2015.176 | 642.868
2016.176 | 640.0118
2017.176 | 644.9495
2018.176 | 650.8534
2019.176 | 634.0726
2020.176 | 632.6273
2021.176 | 629.38
2022.176 | 639.4547
2023.176 | 632.0323
2024.176 | 640.8314
2025.176 | 655.1677
2026.176 | 644.2861
2027.176 | 653.5681
2028.176 | 641.2179
2029.176 | 649.1215
2030.176 | 655.315
2031.176 | 657.3821
2032.176 | 657.2493
2033.176 | 664.6809
2034.176 | 657.7642
2035.176 | 653.6844
2036.176 | 651.5213
2037.176 | 654.3578
2038.176 | 629.9818
2039.176 | 622.8606
2040.176 | 630.9205
2041.176 | 620.089
2042.176 | 617.6658
2043.176 | 622.5584
2044.176 | 618.8103
2045.176 | 601.125
2046.176 | 594.6102
2047.176 | 586.9943
2048.176 | 588.6394
2049.176 | 586.8538
2050.176 | 585.3655
2051.176 | 602.7795
2052.176 | 598.1165
2053.176 | 604.7554
2054.176 | 599.5925
2055.176 | 602.0196
2056.176 | 589.4075
2057.176 | 587.3743
2058.176 | 573.1935
2059.176 | 560.1897
2060.176 | 573.6349
2061.176 | 560.4375
2062.1917 | 581.1977
2063.176 | 572.2598
2064.176 | 567.185
2065.176 | 570.388
2066.176 | 582.584
2067.176 | 589.1351
2068.176 | 593.3921
2069.176 | 608.6974
2070.176 | 607.9897
2071.176 | 620.1699
2072.176 | 619.374
2073.176 | 607.0148
2074.176 | 593.6767
2075.176 | 588.6208
2076.176 | 576.8834
2077.176 | 568.6179
2078.176 | 559.3368
2079.176 | 571.0538
2080.176 | 569.7355
2081.176 | 589.6492
2082.176 | 593.4646
2083.176 | 583.7749
2084.176 | 565.9208
2085.176 | 568.3688
2086.176 | 584.2755
2087.176 | 573.361
2088.176 | 559.5812
2089.176 | 548.5026
2090.176 | 550.3305
2091.176 | 549.6712
2092.176 | 546.6028
2093.176 | 536.6645
2094.176 | 526.3849
2095.176 | 516.9676
2096.176 | 511.3096
2097.176 | 518.0121
2098.176 | 513.556
2099.176 | 526.6623
2100.176 | 534.784
2101.176 | 534.0867
2102.176 | 539.8831
2103.176 | 539.6498
2104.176 | 529.3771
2105.176 | 529.8293
2106.176 | 533.4209
2107.176 | 541.9018
2108.176 | 532.7396
2109.176 | 523.2906
2110.176 | 533.1807
2111.176 | 538.78
2112.176 | 535.9502
2113.176 | 533.8514
2114.176 | 523.9929
2115.176 | 523.4239
2116.176 | 535.9051
2117.176 | 541.717
2118.176 | 554.7914
2119.176 | 564.0506
2120.176 | 564.7117
2121.176 | 552.9265
2122.176 | 544.8639
2123.176 | 539.0742
2124.176 | 540.7185
2125.176 | 549.723
2126.176 | 543.4776
2127.176 | 535.376
2128.176 | 527.4392
2129.176 | 523.5499
2130.176 | 532.8154
2131.176 | 536.6539
2132.176 | 531.1091
2133.176 | 535.6659
2134.176 | 535.2021
2135.176 | 528.3004
2136.176 | 542.9453
2137.176 | 526.4844
2138.176 | 533.6016
2139.176 | 540.4848
2140.176 | 548.9484
2141.176 | 539.9666
2142.176 | 541.4442
2143.176 | 534.4417
2144.176 | 544.2872
2145.176 | 566.0351
2146.176 | 548.6005
2147.176 | 540.6795
2148.176 | 538.0061
2149.176 | 521.3047
2150.176 | 517.4641
2151.176 | 532.2794
2152.176 | 527.5404
2153.176 | 519.1631
2154.176 | 526.5262
2155.176 | 526.5153
2156.176 | 518.9956
2157.176 | 525.7831
2158.176 | 530.0681
2159.176 | 520.6666
2160.176 | 538.8595
2161.176 | 549.2605
2162.176 | 534.8997
2163.176 | 538.9707
2164.176 | 558.7117
2165.176 | 554.4616
2166.176 | 550.4152
2167.176 | 577.4243
2168.176 | 570.0197
2169.176 | 573.4067
2170.176 | 574.1751
2171.176 | 557.2593
2172.176 | 571.2026
2173.176 | 553.0591
2174.176 | 561.7529
2175.176 | 563.2883
2176.176 | 559.5061
2177.176 | 581.8436
2178.176 | 565.6711
2179.176 | 559.7564
2180.176 | 545.2756
2181.176 | 544.9534
2182.176 | 531.4271
2183.176 | 522.547
2184.176 | 520.0506
2185.176 | 504.6205
2186.176 | 498.37
2187.176 | 490.5714
2188.176 | 486.8571
2189.176 | 481.7914
2190.176 | 474.9101
2191.176 | 469.0452
2192.176 | 459.813
2193.176 | 456.2689
2194.176 | 449.9058
2195.176 | 454.3959
2196.176 | 465.0764
2197.176 | 460.3845
2198.176 | 475.1671
2199.176 | 469.5245
2200.176 | 465.6917
2201.176 | 468.2661
2202.176 | 464.3777
2203.176 | 456.3791
2204.176 | 467.0726
2205.176 | 470.5542
2206.176 | 470.2003
2207.176 | 484.1544
2208.176 | 487.6102
2209.176 | 504.854
2210.176 | 525.7865
2211.176 | 532.7659
2212.1917 | 534.275
2213.176 | 547.8501
2214.176 | 558.6954
2215.176 | 579.6491
2216.176 | 564.4766
2217.176 | 545.4692
2218.176 | 530.7046
2219.176 | 534.0303
2220.176 | 534.2236
2221.176 | 539.8962
2222.176 | 568.6158
2223.176 | 570.6576
2224.176 | 559.4271
2225.176 | 569.2966
2226.176 | 569.6429
2227.176 | 550.9778
2228.176 | 550.6557
2229.176 | 574.9305
2230.176 | 568.5718
2231.176 | 551.2399
2232.176 | 555.4503
2233.176 | 560.7459
2234.176 | 545.4855
2235.176 | 529.241
2236.176 | 518.9956
2237.176 | 505.3236
2238.176 | 500.9327
2239.176 | 495.5075
2240.176 | 524.5946
2241.176 | 514.2308
2242.176 | 503.8893
2243.176 | 520.0868
2244.176 | 517.6971
2245.176 | 525.7212
2246.176 | 509.7909
2247.176 | 498.6189
2248.176 | 490.3652
2249.176 | 482.9729
2250.176 | 475.9612
2251.176 | 497.2456
2252.176 | 495.2184
2253.176 | 514.0196
2254.176 | 504.0012
2255.176 | 517.6467
2256.176 | 530.9802
2257.176 | 538.5554
2258.176 | 533.6545
2259.176 | 526.1703
2260.176 | 513.6889
2261.176 | 512.219
2262.176 | 505.5056
2263.176 | 524.9477
2264.176 | 532.9072
2265.176 | 524.5323
2266.176 | 534.6624
2267.176 | 537.4921
2268.176 | 535.2937
2269.176 | 533.4887
2270.176 | 537.5927
2271.176 | 529.0245
2272.1917 | 511.5845
2273.176 | 501.2755
2274.176 | 489.7253
2275.176 | 479.3201
2276.176 | 466.715
2277.176 | 457.0854
2278.176 | 451.0521
2279.176 | 445.0056
2280.176 | 444.4942
2281.176 | 456.1846
2282.176 | 465.6165
2283.176 | 484.957
2284.176 | 488.1872
2285.176 | 482.9372
2286.176 | 482.2606
2287.176 | 491.777
2288.176 | 487.3949
2289.176 | 476.7733
2290.176 | 483.0715
2291.176 | 470.5921
2292.176 | 479.4225
2293.176 | 480.5577
2294.176 | 482.8913
2295.176 | 490.1743
2296.176 | 498.0022
2297.176 | 494.7511
2298.176 | 504.4123
2299.176 | 504.5778
2300.176 | 519.2671
2301.176 | 549.5577
2302.176 | 545.0543
2303.176 | 542.4412
2304.176 | 538.3912
2305.176 | 541.3068
2306.176 | 529.8122
2307.176 | 513.6181
2308.176 | 498.8276
2309.176 | 488.606
2310.176 | 491.1409
2311.176 | 479.3564
2312.176 | 469.9489
2313.176 | 464.0571
2314.176 | 460.7889
2315.176 | 465.5437
2316.176 | 466.216
2317.176 | 484.1946
2318.176 | 506.1645
2319.176 | 503.0602
2320.176 | 508.3248
2321.176 | 508.7675
2322.176 | 510.2259
2323.176 | 529.7007
2324.176 | 527.3819
2325.176 | 532.8699
2326.176 | 538.9841
2327.176 | 532.7495
2328.176 | 530.4579
2329.176 | 530.6333
2330.176 | 538.4529
2331.176 | 550.2543
2332.176 | 553.0898
2333.176 | 545.9876
2334.176 | 534.6844
2335.176 | 523.6384
2336.176 | 519.4612
2337.176 | 531.7035
2338.176 | 548.4359
2339.176 | 542.416
2340.176 | 553.6503
2341.176 | 540.0257
2342.176 | 547.1829
2343.176 | 537.9452
2344.176 | 541.6511
2345.176 | 539.0582
2346.1917 | 537.169
2347.1917 | 543.4873
2348.176 | 539.9276
2349.176 | 525.2452
2350.176 | 514.4628
2351.176 | 519.2544
2352.176 | 535.8307
2353.176 | 523.6486
2354.176 | 521.8864
2355.176 | 514.2277
2356.176 | 513.5936
2357.176 | 523.0062
2358.176 | 517.5636
2359.176 | 522.9658
2360.176 | 512.0763
2361.176 | 503.6534
2362.176 | 512.5149
2363.176 | 526.7446
2364.176 | 519.4922
2365.176 | 533.0007
2366.176 | 521.6562
2367.176 | 512.6991
2368.176 | 502.9602
2369.176 | 498.4876
2370.176 | 494.1241
2371.176 | 487.8838
2372.176 | 495.2124
2373.176 | 491.8752
2374.176 | 495.8199
2375.176 | 492.8794
2376.176 | 490.7061
2377.176 | 490.4511
2378.176 | 491.3729
2379.176 | 508.1009
2380.176 | 506.3738
2381.176 | 513.4888
2382.176 | 513.6025
2383.176 | 529.4827
2384.176 | 528.3019
2385.176 | 537.9595
2386.176 | 550.1919
2387.176 | 553.6846
2388.176 | 544.9673
2389.176 | 550.0794
2390.176 | 551.9181
2391.176 | 550.9243
2392.176 | 533.5602
2393.176 | 534.8623
2394.176 | 548.385
2395.176 | 543.5945
2396.176 | 548.7556
2397.176 | 545.1718
2398.176 | 548.0188
2399.176 | 546.6967
2400.176 | 534.5494
2401.176 | 536.1467
2402.176 | 558.0973
2403.176 | 554.179
2404.176 | 544.9684
2405.176 | 551.343
2406.176 | 565.9748
2407.176 | 558.2195
2408.176 | 563.9913
2409.176 | 569.7852
2410.176 | 568.968
2411.176 | 576.3206
2412.176 | 569.916
2413.176 | 571.3693
2414.176 | 563.2398
2415.176 | 542.4394
2416.176 | 568.531
2417.176 | 561.2475
2418.176 | 553.7402
2419.176 | 568.3167
2420.176 | 562.8723
2421.176 | 542.615
2422.176 | 529.4222
2423.176 | 529.2328
2424.176 | 528.6639
2425.176 | 536.2725
2426.176 | 530.878
2427.176 | 528.3336
2428.176 | 523.6444
2429.176 | 529.2522
2430.176 | 527.2812
2431.176 | 520.1812
2432.176 | 523.7012
2433.176 | 524.1968
2434.176 | 527.3453
2435.176 | 526.5086
2436.176 | 519.895
2437.176 | 516.0833
2438.176 | 507.8968
2439.176 | 499.4551
2440.176 | 488.4708
2441.176 | 506.4167
2442.176 | 498.1533
2443.176 | 509.8946
2444.176 | 509.9439
2445.176 | 510.9072
2446.176 | 522.051
2447.176 | 525.5681
2448.176 | 541.3415
2449.176 | 535.3758
2450.176 | 537.2792
2451.176 | 546.9857
2452.176 | 547.3897
2453.176 | 544.1345
2454.176 | 533.8252
2455.176 | 527.8583
2456.176 | 522.1998
2457.176 | 518.4373
2458.176 | 523.1035
2459.176 | 537.6351
2460.176 | 549.7336
2461.176 | 542.8289
2462.176 | 543.0468
2463.176 | 552.0592
2464.176 | 536.7481
2465.176 | 540.8906
2466.176 | 534.5671
2467.176 | 532.9994
2468.176 | 536.4611
2469.176 | 535.3433
2470.176 | 530.8792
2471.176 | 527.8645
2472.176 | 525.8337
2473.176 | 541.9388
2474.176 | 545.6482
2475.176 | 544.5853
2476.176 | 546.5048
2477.176 | 537.1865
2478.176 | 534.6277
2479.176 | 527.3446
2480.176 | 532.7974
2481.176 | 538.9662
2482.176 | 544.1484
2483.176 | 546.8873
2484.176 | 540.9746
2485.176 | 534.7441
2486.176 | 535.2266
2487.176 | 539.087
2488.176 | 543.0732
2489.176 | 535.5047
2490.176 | 546.8856
2491.176 | 550.9648
2492.176 | 551.0567
2493.176 | 542.8589
2494.176 | 541.2869
2495.176 | 546.0693
2496.176 | 540.109
2497.176 | 544.7159
2498.176 | 547.9287
2499.176 | 537.4046
2500.176 | 537.2266
2501.176 | 534.3399
2502.176 | 544.5124
2503.176 | 530.9253
2504.176 | 523.8664
2505.176 | 516.952
2506.176 | 531.4955
2507.176 | 520.1927
2508.176 | 510.6588
2509.176 | 506.9133
2510.176 | 495.6454
2511.176 | 487.5669
2512.176 | 487.0423
2513.176 | 501.6656
2514.176 | 496.2668
2515.176 | 493.2056
2516.176 | 502.1813
2517.176 | 500.8029
2518.176 | 502.3593
2519.176 | 506.712
2520.176 | 498.1644
2521.176 | 495.6502
2522.176 | 489.2768
2523.176 | 485.366
2524.176 | 496.8401
2525.176 | 489.4512
2526.176 | 493.7113
2527.176 | 489.8198
2528.176 | 489.6616
2529.176 | 483.8484
2530.176 | 478.0041
2531.176 | 473.0172
2532.176 | 472.447
2533.176 | 478.1494
2534.176 | 496.4042
2535.176 | 496.7777
2536.176 | 490.3231
2537.176 | 498.9113
2538.176 | 500.6245
2539.176 | 498.7411
2540.176 | 492.2413
2541.176 | 492.9942
2542.176 | 493.4349
2543.176 | 493.7873
2544.176 | 501.4675
2545.176 | 501.3018
2546.176 | 508.8185
2547.176 | 515.0288
2548.176 | 515.1925
2549.176 | 507.1578
2550.176 | 508.7238
2551.176 | 507.8531
2552.176 | 507.9691
2553.176 | 502.5241
2554.176 | 497.5257
2555.176 | 502.8674
2556.176 | 505.7747
2557.176 | 505.9549
2558.176 | 501.256
2559.176 | 507.6
2560.176 | 502.3309
2561.176 | 509.1768
2562.176 | 505.6295
2563.176 | 508.8555
2564.176 | 505.9602
2565.176 | 509.0768
2566.176 | 510.613
2567.176 | 520.2291
2568.176 | 511.7008
2569.176 | 520.539
2570.176 | 517.7093
2571.176 | 504.2473
2572.176 | 491.6875
2573.176 | 483.0413
2574.176 | 478.3244
2575.176 | 485.3542
2576.176 | 496.7906
2577.176 | 493.2287
2578.176 | 503.3451
2579.176 | 510.3165
2580.176 | 506.6842
2581.176 | 512.6229
2582.176 | 527.7518
2583.176 | 525.264
2584.176 | 528.425
2585.176 | 528.4713
2586.176 | 526.1879
2587.176 | 515.8009
2588.176 | 507.1628
2589.176 | 506.9072
2590.176 | 511.3376
2591.176 | 505.4792
2592.176 | 501.2197
2593.176 | 504.7299
2594.176 | 498.2803
2595.176 | 501.3446
2596.176 | 501.9498
2597.176 | 506.5714
2598.176 | 508.8495
2599.176 | 509.7914
2600.176 | 508.7068
2601.176 | 507.9567
2602.176 | 511.9294
2603.176 | 504.1165
2604.176 | 508.3265
2605.176 | 502.3452
2606.176 | 494.1047
2607.176 | 507.7304
2608.176 | 507.361
2609.176 | 512.7729
2610.176 | 512.0302
2611.176 | 516.5654
2612.176 | 518.0181
2613.176 | 512.6705
2614.176 | 510.8739
2615.176 | 513.5468
2616.176 | 517.4167
2617.176 | 507.0607
2618.176 | 504.4905
2619.176 | 497.6085
2620.176 | 495.0463
2621.176 | 496.2717
2622.176 | 502.072
2623.176 | 504.0867
2624.176 | 500.0153
2625.176 | 494.5487
2626.176 | 494.9262
2627.176 | 488.3048
2628.176 | 492.7602
2629.176 | 487.8252
2630.176 | 485.0694
2631.176 | 480.1597
2632.176 | 476.4282
2633.176 | 473.087
2634.176 | 476.0924
2635.176 | 476.1172
2636.176 | 487.3243
2637.176 | 492.5832
2638.176 | 492.1484
2639.176 | 490.4646
2640.176 | 483.7074
2641.176 | 477.2812
2642.176 | 481.7486
2643.176 | 485.6906
2644.176 | 486.8106
2645.176 | 483.5797
2646.176 | 487.2774
2647.176 | 479.2915
2648.176 | 472.3848
2649.176 | 471.6909
2650.176 | 464.0765
2651.176 | 482.9742
2652.176 | 478.9097
2653.176 | 478.3742
2654.176 | 476.7392
2655.176 | 474.9913
2656.176 | 481.8047
2657.176 | 481.703
2658.176 | 484.3462
2659.176 | 479.2218
2660.176 | 473.7759
2661.176 | 471.7806
2662.176 | 466.8816
2663.176 | 462.7586
2664.176 | 473.0794
2665.176 | 479.3898
2666.176 | 482.3125
2667.176 | 478.7729
2668.176 | 478.2031
2669.176 | 473.5395
2670.176 | 468.6181
2671.176 | 471.4809
2672.176 | 478.6309
2673.176 | 481.3054
2674.176 | 475.3669
2675.176 | 467.8883
2676.176 | 466.646
2677.176 | 463.3985
2678.176 | 462.0593
2679.176 | 457.0251
2680.176 | 452.6544
2681.176 | 449.0808
2682.176 | 446.3011
2683.176 | 449.394
2684.176 | 454.2802
2685.176 | 453.4473
2686.176 | 453.0285
2687.176 | 451.2661
2688.176 | 450.755
2689.176 | 456.7299
2690.176 | 453.0672
2691.176 | 447.1757
2692.176 | 442.2913
2693.176 | 441.7404
2694.176 | 448.5256
2695.176 | 448.7361
2696.176 | 445.8995
2697.176 | 459.7404
2698.176 | 458.7695
2699.176 | 461.4021
2700.176 | 463.3637
2701.176 | 478.9698
2702.176 | 486.9371
2703.176 | 487.0622
2704.176 | 484.5424
2705.176 | 488.7049
2706.176 | 480.9933
2707.176 | 479.9565
2708.176 | 479.9595
2709.176 | 483.7856
2710.176 | 496.5425
2711.176 | 501.4954
2712.176 | 500.7814
2713.176 | 503.5171
2714.176 | 506.7824
2715.176 | 508.1891
2716.176 | 509.5909
2717.176 | 503.6625
2718.176 | 500.4958
2719.176 | 509.3022
2720.176 | 518.9768
2721.176 | 515.0558
2722.176 | 510.3677
2723.176 | 505.2816
2724.176 | 502.9262
2725.176 | 497.5943
2726.176 | 490.6309
2727.176 | 485.7281
2728.176 | 499.1178
2729.176 | 494.4289
2730.176 | 493.3077
2731.176 | 492.03
2732.176 | 491.7182
2733.176 | 486.2157
2734.176 | 491.2316
2735.176 | 493.2415
2736.176 | 493.2655
2737.176 | 489.4832
2738.176 | 489.8123
2739.176 | 484.0238
2740.176 | 483.9492
2741.176 | 481.9269
2742.176 | 484.6386
2743.176 | 479.2649
2744.176 | 480.6289
2745.176 | 480.2312
2746.176 | 486.2279
2747.176 | 497.4891
2748.176 | 506.7288
2749.176 | 499.3299
2750.176 | 499.7088
2751.176 | 493.5589
2752.176 | 487.9905
2753.176 | 484.5908
2754.176 | 485.0158
2755.176 | 492.027
2756.176 | 498.5881
2757.176 | 492.6061
2758.176 | 489.8361
2759.176 | 493.3915
2760.176 | 491.2122
2761.176 | 485.4285
2762.176 | 490.6299
2763.176 | 490.8625
2764.176 | 488.0124
2765.176 | 489.9749
2766.176 | 492.2001
2767.176 | 489.4803
2768.176 | 491.197
2769.176 | 488.2331
2770.176 | 482.0766
2771.176 | 482.4583
2772.176 | 483.0395
2773.176 | 479.8667
2774.176 | 478.1026
2775.176 | 476.2121
2776.176 | 474.9009
2777.176 | 474.4982
2778.176 | 481.4455
2779.176 | 478.6151
2780.176 | 474.0849
2781.176 | 471.1187
2782.176 | 465.7644
2783.176 | 460.7687
2784.176 | 465.2952
2785.176 | 468.752
2786.176 | 468.4832
2787.176 | 467.5146
2788.176 | 465.1541
2789.176 | 463.6268
2790.176 | 468.6923
2791.176 | 468.8393
2792.176 | 469.1718
2793.176 | 470.1694
2794.176 | 476.9562
2795.176 | 485.0486
2796.176 | 483.8474
2797.176 | 483.6169
2798.176 | 480.9154
2799.176 | 484.2
2800.176 | 490.5824
2801.176 | 490.7278
2802.176 | 485.8956
2803.176 | 490.7821
2804.176 | 489.2676
2805.176 | 494.6017
2806.176 | 498.5177
2807.176 | 498.2327
2808.176 | 497.5507
2809.176 | 495.1285
2810.176 | 497.4318
2811.176 | 496.0807
2812.176 | 498.0183
2813.176 | 503.0572
2814.176 | 498.4802
2815.176 | 495.8468
2816.176 | 495.2631
2817.176 | 497.426
2818.176 | 494.5135
2819.176 | 487.7226
2820.176 | 483.222
2821.176 | 489.4482
2822.176 | 483.4109
2823.176 | 481.2321
2824.176 | 483.3503
2825.176 | 484.4158
2826.176 | 480.4879
2827.176 | 480.4411
2828.176 | 483.0098
2829.176 | 486.4889
2830.176 | 490.4401
2831.176 | 490.6949
2832.176 | 489.7666
2833.176 | 486.9082
2834.176 | 485.817
2835.176 | 482.1196
2836.176 | 491.9087
2837.176 | 493.038
2838.176 | 492.3296
2839.176 | 504.3495
2840.176 | 522.1846
2841.176 | 519.5045
2842.176 | 519.7851
2843.176 | 520.228
2844.176 | 521.0541
2845.176 | 512.3709
2846.176 | 505.6484
2847.176 | 503.3613
2848.176 | 497.9455
2849.176 | 498.1667
2850.176 | 502.1218
2851.176 | 494.1639
2852.176 | 494.3179
2853.176 | 500.633
2854.176 | 493.6112
2855.176 | 485.2782
2856.176 | 479.3878
2857.176 | 473.8053
2858.176 | 473.6149
2859.176 | 471.9715
2860.176 | 472.2805
2861.176 | 471.1773
2862.176 | 467.4163
2863.176 | 469.1858
2864.176 | 472.9446
2865.176 | 471.7894
2866.176 | 467.6095
2867.176 | 466.9798
2868.176 | 466.5623
2869.176 | 464.266
2870.176 | 462.6113
2871.176 | 460.8048
2872.176 | 460.3047
2873.176 | 460.5647
2874.176 | 458.0501
2875.176 | 454.3181
2876.176 | 452.9718
2877.176 | 450.4196
2878.176 | 449.7897
2879.176 | 457.958
2880.176 | 456.4246
2881.176 | 456.0213
2882.176 | 457.7932
2883.176 | 456.7474
2884.176 | 457.0043
2885.176 | 459.0704
2886.176 | 459.6514
2887.176 | 455.8191
2888.176 | 453.2691
2889.176 | 451.7282
2890.176 | 454.5988
2891.176 | 453.7742
2892.176 | 452.3414
2893.176 | 453.7839
2894.176 | 455.2022
2895.176 | 461.2931
2896.176 | 464.399
2897.176 | 468.097
2898.176 | 481.4351
2899.176 | 482.4038
2900.176 | 492.45
2901.176 | 493.6466
2902.176 | 496.938
2903.176 | 497.2029
2904.176 | 492.2876
2905.176 | 492.3379
2906.176 | 490.4293
2907.176 | 491.7603
2908.176 | 487.5029
2909.176 | 480.0221
2910.176 | 475.1991
2911.176 | 470.218
2912.176 | 462.7756
2913.176 | 458.3682
2914.176 | 454.9847
2915.176 | 458.64
2916.176 | 462.2424
2917.176 | 461.5412
2918.176 | 465.7394
2919.176 | 470.8993
2920.176 | 468.9551
2921.176 | 469.974
2922.176 | 469.468
2923.176 | 465.6886
2924.176 | 466.9885
2925.176 | 464.5653
2926.176 | 464.6132
2927.176 | 466.9614
2928.176 | 470.0901
2929.176 | 482.475
2930.176 | 486.292
2931.176 | 491.6666
2932.176 | 489.8106
2933.176 | 488.0493
2934.176 | 492.3751
2935.176 | 490.3397
2936.176 | 485.907
2937.176 | 489.2137
2938.176 | 489.6784
2939.176 | 490.5599
2940.176 | 488.0799
2941.176 | 482.8934
2942.176 | 476.374
2943.176 | 472.9765
2944.176 | 470.3655
2945.176 | 469.8958
2946.176 | 470.4232
2947.176 | 468.4329
2948.176 | 463.4336
2949.176 | 461.7035
2950.176 | 460.0783
2951.176 | 461.4314
2952.176 | 460.178
2953.176 | 456.7679
2954.176 | 453.9075
2955.176 | 448.7667
2956.176 | 446.8975
2957.176 | 445.8151
2958.176 | 445.312
2959.176 | 441.4728
2960.176 | 438.2868
2961.176 | 436.9964
2962.176 | 442.0759
2963.176 | 445.2101
2964.176 | 452.6601
2965.176 | 449.7523
2966.176 | 449.6724
2967.176 | 447.4988
2968.176 | 453.6365
2969.176 | 451.9187
2970.176 | 449.9636
2971.176 | 451.7642
2972.176 | 452.0679
2973.176 | 450.9896
2974.176 | 448.4098
2975.1917 | 444.6591
2976.1917 | 442.4914
2977.176 | 445.0304
2978.176 | 450.6535
2979.176 | 455.4901
2980.176 | 458.3311
2981.176 | 457.6121
2982.176 | 456.7649
2983.1917 | 455.6685
2984.1917 | 453.9036
2985.1917 | 455.3914
2986.176 | 452.0721
2987.176 | 450.2718
2988.176 | 443.2725
2989.176 | 443.042
2990.176 | 442.2153
2991.176 | 438.0688
2992.176 | 433.9673
2993.176 | 430.0475
2994.176 | 428.8001
2995.176 | 428.7446
2996.176 | 429.8872
2997.176 | 431.4944
2998.176 | 438.263
2999.176 | 437.3484
3000.176 | 455.3192
3001.176 | 455.4385
3002.176 | 454.8987
3003.176 | 455.8367
3004.176 | 454.3771
3005.176 | 453.3932
3006.176 | 455.8443
3007.176 | 454.0992
3008.176 | 457.3024
3009.176 | 459.0954
3010.176 | 458.8301
3011.176 | 461.5709
3012.176 | 461.9413
3013.176 | 461.4937
3014.176 | 458.1349
3015.176 | 456.2341
3016.176 | 454.8563
3017.176 | 454.9635
3018.176 | 456.4521
3019.176 | 455.8423
3020.176 | 456.0571
3021.176 | 455.4364
3022.176 | 453.3492
3023.176 | 450.2386
3024.176 | 449.3263
3025.176 | 448.3195
3026.176 | 449.7659
3027.176 | 448.6553
3028.176 | 446.5697
3029.176 | 446.3414
3030.176 | 453.2297
3031.176 | 453.6746
3032.176 | 459.588
3033.176 | 465.3308
3034.176 | 463.9218
3035.176 | 461.8416
3036.176 | 461.1969
3037.176 | 459.5188
3038.176 | 458.5198
3039.176 | 459.9952
3040.176 | 462.0045
3041.176 | 459.511
3042.176 | 461.5636
3043.176 | 460.6567
3044.176 | 456.3207
3045.176 | 453.7937
3046.176 | 450.9132
3047.176 | 447.9602
3048.176 | 445.5956
3049.176 | 443.1676
3050.176 | 440.8103
3051.176 | 441.4885
3052.176 | 444.6845
3053.176 | 444.4556
3054.176 | 442.6744
3055.176 | 439.1024
3056.176 | 438.5326
3057.176 | 444.2738
3058.176 | 449.5605
3059.176 | 448.7334
3060.176 | 445.3749
3061.176 | 443.2543
3062.176 | 444.6236
3063.176 | 446.0636
3064.176 | 449.2415
3065.176 | 452.5609
3066.176 | 454.8624
3067.176 | 458.0357
3068.176 | 458.4671
3069.176 | 454.6212
3070.176 | 455.8864
3071.176 | 454.3526
3072.176 | 454.34
3073.176 | 451.301
3074.176 | 449.8547
3075.176 | 456.3307
3076.176 | 460.5608
3077.176 | 461.6672
3078.176 | 465.8555
3079.176 | 468.8276
3080.176 | 471.1906
3081.176 | 469.9178
3082.176 | 467.9765
3083.176 | 466.1332
3084.176 | 469.1885
3085.176 | 468.8101
3086.176 | 476.3668
3087.176 | 473.9101
3088.176 | 470.5475
3089.176 | 467.2999
3090.176 | 463.8371
3091.176 | 462.0429
3092.176 | 457.8478
3093.176 | 457.3482
3094.176 | 455.0631
3095.176 | 459.3291
3096.176 | 459.193
3097.176 | 457.4418
3098.176 | 454.2996
3099.176 | 455.3627
3100.176 | 456.0662
3101.176 | 456.6831
3102.176 | 458.9461
3103.176 | 460.9318
3104.176 | 459.6232
3105.176 | 457.7885
3106.176 | 461.1338
3107.176 | 461.7452
3108.176 | 465.4401
3109.176 | 473.9062
3110.176 | 475.5584
3111.176 | 477.8679
3112.176 | 471.7896
3113.176 | 469.1276
3114.176 | 465.4209
3115.176 | 467.5742
3116.176 | 466.7118
3117.176 | 464.5407
3118.176 | 462.7758
3119.176 | 460.1952
3120.176 | 458.6849
3121.176 | 456.9079
3122.176 | 457.4581
3123.176 | 458.9987
3124.176 | 453.4609
3125.176 | 450.5027
3126.176 | 449.2063
3127.176 | 448.786
3128.176 | 447.4191
3129.176 | 447.1414
3130.176 | 447.1128
3131.176 | 448.0182
3132.176 | 446.1362
3133.176 | 446.5454
3134.176 | 444.0931
3135.176 | 441.4357
3136.176 | 443.7482
3137.176 | 444.9716
3138.176 | 447.5475
3139.176 | 445.2101
3140.176 | 442.8901
3141.176 | 440.8172
3142.176 | 442.0432
3143.1917 | 440.8245
3144.176 | 442.6107
3145.176 | 439.5558
3146.176 | 434.9603
3147.176 | 430.4368
3148.176 | 431.7391
3149.176 | 433.621
3150.176 | 432.1352
3151.176 | 435.3061
3152.176 | 438.9316
3153.176 | 439.9651
3154.176 | 441.1585
3155.176 | 442.3631
3156.176 | 446.6586
3157.176 | 446.4291
3158.176 | 444.9655
3159.176 | 442.9762
3160.176 | 443.0519
3161.176 | 442.0773
3162.176 | 442.51
3163.176 | 439.4412
3164.176 | 437.3063
3165.176 | 437.2005
3166.176 | 434.769
3167.176 | 432.5877
3168.176 | 429.1324
3169.176 | 430.5879
3170.176 | 429.7731
3171.176 | 432.2315
3172.176 | 432.6958
3173.1917 | 434.8673
3174.176 | 440.1737
3175.176 | 440.2638
3176.176 | 443.5151
3177.176 | 443.4296
3178.176 | 441.7066
3179.176 | 438.674
3180.176 | 435.4341
3181.176 | 430.6882
3182.176 | 427.0243
3183.176 | 425.3508
3184.176 | 423.9974
3185.176 | 422.816
3186.176 | 424.9792
3187.176 | 427.8917
3188.176 | 428.4046
3189.176 | 431.6661
3190.176 | 431.9021
3191.176 | 436.6238
3192.176 | 440.8235
3193.176 | 442.109
3194.176 | 444.866
3195.176 | 445.5306
3196.176 | 449.5884
3197.176 | 454.0834
3198.176 | 453.0177
3199.176 | 451.1795
3200.176 | 453.4161
3201.176 | 451.9316
3202.176 | 453.8822
3203.1917 | 453.7913
3204.176 | 450.192
3205.176 | 448.5319
3206.176 | 445.0059
3207.176 | 442.8371
3208.176 | 439.8577
3209.176 | 441.6076
3210.176 | 440.7811
3211.176 | 439.4703
3212.176 | 436.6173
3213.176 | 436.1398
3214.176 | 433.8213
3215.176 | 432.1387
3216.176 | 432.7156
3217.176 | 431.4475
3218.176 | 436.2179
3219.176 | 438.1992
3220.176 | 439.3376
3221.176 | 439.27
3222.176 | 437.2005
3223.176 | 435.0515
3224.176 | 432.3459
3225.176 | 431.4915
3226.2229 | 430.6644
3227.176 | 430.8366
3228.176 | 430.0826
3229.176 | 424.2246
3230.176 | 424.4636
3231.176 | 423.4925
3232.176 | 423.1168
3233.1917 | 422.1389
3234.176 | 418.2484
3235.176 | 415.695
3236.176 | 415.0723
3237.176 | 415.2326
3238.176 | 417.8067
3239.176 | 413.7345
3240.176 | 409.5593
3241.176 | 411.9878
3242.176 | 412.0991
3243.176 | 412.7288
3244.176 | 409.759
3245.176 | 407.9418
3246.176 | 408.0427
3247.176 | 411.8686
3248.176 | 411.3034
3249.176 | 414.0128
3250.176 | 415.2938
3251.176 | 412.9511
3252.176 | 413.0384
3253.176 | 413.7866
3254.176 | 412.5945
3255.176 | 412.0864
3256.176 | 413.484
3257.176 | 412.5051
3258.176 | 408.3503
3259.176 | 404.82
3260.176 | 403.1024
3261.176 | 401.4682
3262.176 | 402.301
3263.176 | 406.0059
3264.176 | 407.6281
3265.176 | 409.7531
3266.176 | 411.0651
3267.176 | 410.9452
3268.176 | 410.6168
3269.176 | 408.6895
3270.176 | 404.2331
3271.1917 | 406.8227
3272.176 | 407.6976
3273.176 | 410.481
3274.1917 | 412.7064
3275.1917 | 417.6005
3276.176 | 421.7512
3277.176 | 423.2678
3278.176 | 426.2969
3279.176 | 427.7809
3280.176 | 432.1214
3281.176 | 434.3361
3282.176 | 433.027
3283.176 | 435.2902
3284.176 | 437.4359
3285.176 | 435.9269
3286.176 | 435.0154
3287.176 | 430.5115
3288.176 | 429.7691
3289.176 | 431.2433
3290.176 | 431.0302
3291.176 | 434.4997
3292.176 | 438.8865
3293.1917 | 441.9679
3294.176 | 443.3318
3295.176 | 442.4675
3296.176 | 445.1705
3297.176 | 444.8776
3298.176 | 444.1202
3299.176 | 442.6468
3300.176 | 443.0834
3301.176 | 445.8345
3302.176 | 447.9229
3303.176 | 451.1271
3304.176 | 449.9544
3305.176 | 451.0538
3306.176 | 445.8557
3307.176 | 439.331
3308.176 | 436.3968
3309.176 | 435.1536
3310.176 | 432.1915
3311.176 | 432.8339
3312.176 | 431.6876
3313.176 | 439.8425
3314.176 | 443.9632
3315.176 | 450.073
3316.176 | 454.7311
3317.176 | 456.4248
3318.176 | 459.4165
3319.176 | 463.3578
3320.176 | 469.2205
3321.176 | 471.5064
3322.176 | 471.8367
3323.176 | 469.9471
3324.176 | 465.1764
3325.176 | 459.9743
3326.176 | 456.4379
3327.176 | 460.283
3328.176 | 456.7777
3329.176 | 451.082
3330.176 | 449.005
3331.176 | 449.5015
3332.176 | 448.9192
3333.176 | 447.4288
3334.176 | 448.1939
3335.176 | 446.1402
3336.176 | 445.6126
3337.176 | 443.6626
3338.176 | 447.2091
3339.176 | 447.6848
3340.176 | 444.3162
3341.176 | 443.9985
3342.176 | 446.2838
3343.176 | 445.9862
3344.176 | 448.9305
3345.176 | 450.3157
3346.176 | 451.9505
3347.176 | 447.8766
3348.176 | 449.8574
3349.176 | 451.8674
3350.176 | 454.5371
3351.176 | 451.4364
3352.176 | 450.309
3353.176 | 451.7313
3354.176 | 450.1041
3355.176 | 447.5675
3356.176 | 447.5102
3357.176 | 450.5167
3358.176 | 452.9648
3359.176 | 450.3172
3360.176 | 452.068
3361.176 | 450.7758
3362.176 | 449.8043
3363.176 | 450.5397
3364.176 | 449.224
3365.176 | 448.0571
3366.176 | 450.4243
3367.176 | 448.4925
3368.176 | 447.2853
3369.176 | 451.3733
3370.176 | 455.0836
3371.176 | 458.0913
3372.176 | 457.5114
3373.176 | 457.809
3374.176 | 454.5861
3375.176 | 452.7944
3376.176 | 455.5789
3377.176 | 454.1358
3378.176 | 459.111
3379.176 | 465.882
3380.176 | 472.6181
3381.176 | 473.4412
3382.176 | 478.0274
3383.176 | 480.5503
3384.176 | 481.8141
3385.176 | 484.0181
3386.176 | 488.0171
3387.176 | 488.8899
3388.176 | 486.0651
3389.176 | 482.6937
3390.176 | 482.6056
3391.176 | 481.919
3392.176 | 484.2637
3393.176 | 483.3297
3394.176 | 483.3564
3395.176 | 487.3451
3396.176 | 488.3002
3397.176 | 494.3332
3398.176 | 503.6868
3399.176 | 508.4405
3400.176 | 511.7594
3401.176 | 518.9405
3402.176 | 523.2163
3403.176 | 529.5435
3404.176 | 535.2816
3405.176 | 543.6322
3406.176 | 552.6559
3407.176 | 550.6952
3408.176 | 549.7894
3409.176 | 545.5634
3410.176 | 535.6743
3411.176 | 529.7068
3412.176 | 526.9814
3413.176 | 526.5889
3414.176 | 521.5406
3415.176 | 519.1545
3416.176 | 516.0524
3417.176 | 515.6262
3418.176 | 509.2109
3419.176 | 510.425
3420.176 | 515.9613
3421.176 | 516.5772
3422.176 | 512.0662
3423.176 | 511.8571
3424.176 | 517.5469
3425.176 | 518.0375
3426.176 | 516.2718
3427.176 | 509.2691
3428.176 | 507.1651
3429.176 | 508.7218
3430.176 | 518.0169
3431.176 | 514.44
3432.176 | 516.0379
3433.176 | 523.666
3434.176 | 527.3687
3435.176 | 530.9598
3436.176 | 539.1517
3437.176 | 545.2278
3438.176 | 544.7512
3439.176 | 534.8615
3440.176 | 539.323
3441.176 | 543.179
3442.176 | 544.2889
3443.176 | 549.6032
3444.176 | 557.5768
3445.176 | 560.023
3446.176 | 564.7127
3447.176 | 567.9285
3448.176 | 573.9517
3449.176 | 571.2406
3450.176 | 581.1242
3451.176 | 570.4111
3452.176 | 567.8349
3453.176 | 558.3191
3454.176 | 550.0676
3455.176 | 556.2397
3456.1917 | 557.1061
3457.1917 | 561.5197
3458.1917 | 563.8733
3459.176 | 565.0163
3460.176 | 569.0101
3461.176 | 570.5545
3462.176 | 563.3382
3463.176 | 552.0774
3464.176 | 542.7962
3465.176 | 535.5691
3466.176 | 535.6316
3467.176 | 541.2918
3468.176 | 545.2028
3469.176 | 552.483
3470.176 | 554.7865
3471.176 | 554.0156
3472.176 | 554.8122
3473.176 | 555.8821
3474.176 | 560.2772
3475.176 | 556.6518
3476.176 | 559.0417
3477.176 | 562.4386
3478.176 | 558.996
3479.176 | 558.5261
3480.176 | 555.5615
3481.176 | 556.3254
3482.176 | 555.7378
3483.176 | 556.9754
3484.176 | 558.3018
3485.176 | 563.7892
3486.176 | 568.5965
3487.176 | 565.5648
3488.176 | 568.4823
3489.176 | 567.444
3490.176 | 559.4268
3491.176 | 553.1519
3492.176 | 555.2176
3493.176 | 554.1172
3494.176 | 554.6567
3495.176 | 551.5352
3496.176 | 546.1607
3497.176 | 540.7484
3498.176 | 549.7473
3499.176 | 559.961
3500.176 | 565.9235
3501.176 | 562.9686
3502.176 | 555.9279
3503.176 | 555.2959
3504.176 | 558.818
3505.176 | 560.0342
3506.176 | 556.7988
3507.176 | 559.0658
3508.176 | 560.4985
3509.176 | 562.5195
3510.176 | 572.7119
3511.176 | 577.4072
3512.176 | 577.044
3513.176 | 574.5133
3514.176 | 569.465
3515.176 | 568.8791
3516.176 | 571.4347
3517.176 | 579.0682
3518.176 | 576.1048
3519.176 | 574.5271
3520.176 | 578.3817
3521.176 | 576.041
3522.176 | 577.6378
3523.176 | 579.7021
3524.176 | 578.1573
3525.176 | 575.4511
3526.176 | 579.5454
3527.176 | 575.4918
3528.176 | 572.5328
3529.176 | 571.223
3530.176 | 565.8329
3531.176 | 563.6533
3532.176 | 563.9589
3533.176 | 572.043
3534.176 | 577.2665
3535.176 | 586.008
3536.176 | 590.3935
3537.176 | 595.8855
3538.176 | 603.4255
3539.176 | 609.1777
3540.176 | 617.588
3541.176 | 626.5941
3542.176 | 631.7518
3543.176 | 627.5463
3544.176 | 631.7291
3545.176 | 636.0894
3546.176 | 642.4957
3547.176 | 649.9311
3548.176 | 647.5706
3549.176 | 649.3011
3550.176 | 652.844
3551.176 | 647.0606
3552.176 | 649.3729
3553.176 | 648.7918
3554.176 | 639.2814
3555.176 | 634.1031
3556.176 | 630.1263
3557.176 | 621.7983
3558.176 | 615.8483
3559.176 | 615.6076
3560.176 | 608.653
3561.176 | 606.6615
3562.176 | 620.9905
3563.176 | 626.7736
3564.176 | 629.8305
3565.176 | 629.064
3566.176 | 626.2553
3567.176 | 623.2088
3568.176 | 628.4706
3569.176 | 629.9773
3570.176 | 636.9881
3571.176 | 636.0538
3572.176 | 643.0372
3573.176 | 644.4463
3574.176 | 645.5608
3575.176 | 642.2507
3576.176 | 642.5365
3577.176 | 639.2716
3578.176 | 640.7694
3579.176 | 641.8917
3580.176 | 636.8936
3581.176 | 635.6275
3582.176 | 642.6266
3583.176 | 644.6901
3584.176 | 647.9028
3585.176 | 650.4435
3586.176 | 652.7264
3587.176 | 654.8689
3588.176 | 652.2655
3589.176 | 645.8408
3590.176 | 646.363
3591.176 | 647.784
3592.176 | 651.804
3593.176 | 649.6042
3594.176 | 656.0771
3595.176 | 653.2323
3596.176 | 648.3688
3597.176 | 659.6072
3598.176 | 661.4834
3599.176 | 660.1586
3600.176 | 667.5772
3601.176 | 679.133
3602.176 | 685.7969
3603.176 | 679.2024
3604.176 | 675.8097
3605.176 | 674.9487
3606.176 | 677.7551
3607.176 | 684.183
3608.176 | 684.5391
3609.176 | 686.9945
3610.176 | 690.2229
3611.176 | 686.244
3612.176 | 683.6614
3613.176 | 680.5941
3614.176 | 683.218
3615.176 | 685.5392
3616.176 | 687.0467
3617.176 | 684.5477
3618.176 | 686.4781
3619.176 | 687.4744
3620.176 | 688.7481
3621.176 | 686.5886
3622.176 | 686.6961
3623.176 | 684.1115
3624.176 | 681.5268
3625.176 | 675.7183
3626.176 | 672.4226
3627.176 | 674.8701
3628.176 | 663.0319
3629.176 | 665.3275
3630.176 | 668.4974
3631.176 | 673.0116
3632.176 | 679.1265
3633.176 | 682.5138
3634.176 | 685.8839
3635.176 | 684.4462
3636.176 | 682.1312
3637.176 | 680.7715
3638.176 | 679.3949
3639.176 | 669.0628
3640.176 | 656.8006
3641.176 | 653.7539
3642.176 | 648.3697
3643.176 | 644.3329
3644.176 | 646.5713
3645.176 | 644.3288
3646.176 | 645.5414
3647.176 | 647.3367
3648.176 | 649.5877
3649.176 | 656.3356
3650.176 | 660.9691
3651.176 | 669.4203
3652.176 | 672.613
3653.176 | 678.1177
3654.176 | 675.4389
3655.176 | 673.4284
3656.176 | 672.7856
3657.176 | 677.6663
3658.176 | 676.6416
3659.176 | 675.988
3660.176 | 678.4002
3661.176 | 679.3904
3662.176 | 679.8613
3663.176 | 677.4421
3664.176 | 672.1321
3665.176 | 675.7945
3666.176 | 679.3566
3667.176 | 681.6804
3668.176 | 681.2254
3669.176 | 683.3739
3670.176 | 682.9477
3671.176 | 685.378
3672.176 | 684.3721
3673.176 | 682.1433
3674.176 | 680.6471
3675.176 | 682.1498
3676.176 | 679.7554
3677.176 | 676.9818
3678.176 | 677.494
3679.176 | 680.5161
3680.176 | 685.0867
3681.176 | 687.6066
3682.176 | 684.6992
3683.176 | 687.8409
3684.176 | 689.6752
3685.176 | 690.8511
3686.176 | 691.0044
3687.176 | 692.0949
3688.176 | 692.2877
3689.176 | 691.2859
3690.176 | 692.3371
3691.176 | 694.4028
3692.176 | 691.2119
3693.176 | 697.9077
3694.176 | 699.9272
3695.176 | 698.6779
3696.176 | 695.7232
3697.176 | 694.8068
3698.176 | 689.3297
3699.176 | 684.433
3700.176 | 682.0156
3701.176 | 685.9544
3702.176 | 687.4207
3703.176 | 691.0705
3704.176 | 692.6586
3705.176 | 690.8837
3706.176 | 692.6512
3707.176 | 691.0038
3708.176 | 692.6683
3709.176 | 693.9676
3710.176 | 694.5404
3711.176 | 693.4275
3712.176 | 691.579
3713.176 | 681.0506
3714.176 | 680.709
3715.176 | 679.0515
3716.176 | 681.0319
3717.176 | 683.8445
3718.176 | 683.4068
3719.176 | 682.3178
3720.176 | 685.739
3721.176 | 685.0002
3722.176 | 686.7272
3723.176 | 692.2784
3724.176 | 699.6752
3725.176 | 702.6076
3726.176 | 702.8294
3727.176 | 699.6125
3728.176 | 694.5832
3729.176 | 694.443
3730.176 | 690.6312
3731.176 | 687.893
3732.176 | 688.8211
3733.176 | 692.3305
3734.176 | 694.18
3735.176 | 692.1112
3736.176 | 691.5464
3737.176 | 688.7829
3738.176 | 686.9418
3739.176 | 687.0855
3740.176 | 686.4442
3741.176 | 686.229
3742.176 | 690.9745
3743.176 | 695.5706
3744.176 | 691.4949
3745.176 | 688.1403
3746.176 | 684.6536
3747.176 | 676.1793
3748.176 | 673.2374
3749.176 | 675.9857
3750.176 | 680.2348
3751.176 | 681.765
3752.176 | 680.8528
3753.176 | 683.3837
3754.176 | 686.9875
3755.176 | 689.6965
3756.176 | 685.4636
3757.176 | 687.4189
3758.176 | 688.9285
3759.176 | 690.3345
3760.176 | 689.3874
3761.176 | 686.105
3762.176 | 680.851
3763.176 | 680.0373
3764.176 | 677.6666
3765.176 | 678.0228
3766.176 | 682.8352
3767.176 | 684.6739
3768.176 | 689.2044
3769.176 | 689.7135
3770.176 | 689.3784
3771.176 | 693.7775
3772.176 | 696.5174
3773.176 | 697.3092
3774.176 | 698.3422
3775.176 | 700.1919
3776.176 | 700.5297
3777.176 | 696.4197
3778.176 | 694.2175
3779.176 | 690.8736
3780.176 | 687.5605
3781.176 | 684.9381
3782.176 | 684.308
3783.176 | 681.7561
3784.176 | 684.0159
3785.176 | 682.1743
3786.176 | 683.6322
3787.176 | 683.4465
3788.176 | 685.0844
3789.176 | 689.6793
3790.176 | 689.3512
3791.176 | 689.3305
3792.176 | 690.4488
3793.176 | 691.2893
3794.176 | 695.2471
3795.176 | 695.0385
3796.176 | 694.491
3797.176 | 694.6183
3798.176 | 693.3684
3799.176 | 692.2901
3800.176 | 690.4434
3801.176 | 688.8584
3802.176 | 691.2743
3803.176 | 694.5358
3804.176 | 695.6911
3805.176 | 695.8008
3806.176 | 694.7199
3807.176 | 695.5973
3808.176 | 693.4702
3809.176 | 690.9426
3810.176 | 687.2547
3811.176 | 686.2407
3812.176 | 682.2638
3813.176 | 686.6981
3814.176 | 694.5686
3815.176 | 694.7736
3816.176 | 698.5174
3817.176 | 699.5951
3818.176 | 697.1645
3819.176 | 694.2749
3820.176 | 692.6189
3821.176 | 691.7478
3822.176 | 693.5593
3823.176 | 694.4248
3824.176 | 691.7411
3825.176 | 691.2795
3826.176 | 689.864
3827.176 | 685.985
3828.176 | 686.7013
3829.176 | 688.8367
3830.176 | 690.0952
3831.176 | 689.4437
3832.176 | 687.4076
3833.176 | 687.0846
3834.176 | 691.0629
3835.176 | 692.1977
3836.176 | 687.2385
3837.176 | 685.3789
3838.176 | 694.7241
3839.176 | 703.5081
3840.176 | 702.6586
3841.176 | 698.7183
3842.176 | 696.8062
3843.176 | 695.1836
3844.176 | 695.1152
3845.176 | 698.4077
3846.176 | 693.7243
3847.176 | 693.7753
3848.176 | 693.1105
3849.176 | 689.9662
3850.176 | 688.5353
3851.176 | 685.7447
3852.176 | 683.8938
3853.176 | 682.5279
3854.176 | 682.0843
3855.176 | 686.1288
3856.176 | 687.1405
3857.176 | 682.9765
3858.176 | 680.0651
3859.176 | 681.8031
3860.176 | 683.8615
3861.176 | 684.9162
3862.176 | 685.6226
3863.176 | 688.8855
3864.176 | 687.547
3865.176 | 688.2856
3866.176 | 686.1871
3867.176 | 685.7274
3868.176 | 687.487
3869.176 | 684.7344
3870.176 | 682.5089
3871.176 | 679.8739
3872.176 | 680.291
3873.176 | 685.2507
3874.176 | 688.3569
3875.176 | 687.9659
3876.176 | 684.335
3877.176 | 682.0726
3878.176 | 682.4267
3879.176 | 682.8153
3880.176 | 680.8071
3881.176 | 675.9576
3882.176 | 674.1086
3883.176 | 671.348
3884.176 | 671.0598
3885.176 | 674.5443
3886.176 | 671.1722
3887.176 | 671.9416
3888.176 | 674.3475
3889.176 | 673.2197
3890.176 | 669.0271
3891.176 | 667.1104
3892.176 | 667.9281
3893.176 | 669.0205
3894.176 | 667.3593
3895.176 | 669.3625
3896.176 | 670.1006
3897.176 | 671.4938
3898.176 | 672.2819
3899.176 | 675.2564
3900.176 | 678.6795
3901.176 | 681.7127
3902.176 | 680.6528
3903.176 | 679.158
3904.176 | 675.2932
3905.176 | 674.506
3906.176 | 674.2782
3907.176 | 674.9772
3908.176 | 676.2704
3909.176 | 678.1588
3910.176 | 676.3299
3911.176 | 676.1056
3912.176 | 675.6151
3913.176 | 674.6462
3914.176 | 673.1276
3915.176 | 672.1049
3916.176 | 671.4765
3917.176 | 669.569
3918.176 | 665.3973
3919.176 | 662.9224
3920.176 | 659.1177
3921.176 | 654.6324
3922.176 | 651.0967
3923.176 | 649.1538
3924.176 | 643.1085
3925.176 | 641.0913
3926.176 | 640.297
3927.176 | 638.5706
3928.176 | 637.9032
3929.176 | 636.3062
3930.176 | 635.9774
3931.176 | 635.6762
3932.176 | 636.2616
3933.176 | 637.387
3934.176 | 638.2327
3935.176 | 638.8518
3936.176 | 637.246
3937.176 | 639.6101
3938.176 | 640.7484
3939.176 | 644.571
3940.176 | 646.3756
3941.176 | 647.7865
3942.176 | 648.1817
3943.176 | 648.5306
3944.176 | 646.4039
3945.176 | 648.7985
3946.176 | 651.188
3947.176 | 651.8303
3948.176 | 653.5035
3949.176 | 654.0062
3950.176 | 650.6468
3951.176 | 649.6417
3952.176 | 651.3505
3953.176 | 649.5742
3954.176 | 650.1397
3955.176 | 649.5194
3956.176 | 649.6478
3957.176 | 650.3195
3958.176 | 654.5826
3959.176 | 659.3596
3960.176 | 665.9939
3961.176 | 668.7658
3962.176 | 669.3331
3963.176 | 668.6744
3964.176 | 669.1812
3965.176 | 664.1272
3966.176 | 660.9994
3967.176 | 656.3229
3968.176 | 655.3709
3969.176 | 655.3197
3970.176 | 654.8853
3971.176 | 655.4057
3972.176 | 656.3442
3973.176 | 654.8831
3974.176 | 653.4829
3975.176 | 654.6304
3976.176 | 654.1069
3977.176 | 659.5791
3978.176 | 662.7953
3979.176 | 668.3079
3980.176 | 668.9236
3981.176 | 669.2199
3982.176 | 667.256
3983.176 | 668.7824
3984.176 | 667.0474
3985.176 | 665.2717
3986.176 | 660.9115
3987.176 | 661.0382
3988.176 | 660.5507
3989.176 | 662.1252
3990.176 | 662.3381
3991.176 | 667.3044
3992.176 | 668.2077
3993.176 | 672.2847
3994.176 | 671.937
3995.176 | 670.4406
3996.176 | 668.7398
3997.176 | 664.9834
3998.176 | 664.2907
3999.176 | 665.3691
4000.176 | 668.623
4001.176 | 666.6642
4002.176 | 661.4457
4003.176 | 660.5808
4004.176 | 661.7065
4005.176 | 662.3944
4006.176 | 662.9876
4007.176 | 661.3292
4008.176 | 660.9462
4009.176 | 661.6595
4010.176 | 662.2349
4011.176 | 656.3863
4012.176 | 657.977
4013.176 | 657.2654
4014.176 | 658.384
4015.176 | 654.6372
4016.176 | 653.5001
4017.176 | 653.1868
4018.176 | 651.8547
4019.176 | 649.8052
4020.176 | 657.461
4021.176 | 666.1744
4022.176 | 673.5593
4023.176 | 680.7776
4024.176 | 680.8119
4025.176 | 676.45
4026.176 | 676.7324
4027.176 | 682.959
4028.176 | 685.9134
4029.176 | 687.378
4030.176 | 685.7136
4031.176 | 690.0167
4032.176 | 687.7044
4033.176 | 687.0726
4034.176 | 686.3301
4035.176 | 685.4105
4036.176 | 684.6696
4037.176 | 689.6641
4038.176 | 689.7823
4039.176 | 686.2128
4040.176 | 680.052
4041.176 | 675.8506
4042.176 | 680.3752
4043.176 | 678.672
4044.176 | 676.9263
4045.176 | 679.8132
4046.176 | 678.2604
4047.176 | 678.7173
4048.176 | 682.0259
4049.176 | 681.2838
4050.176 | 677.6822
4051.176 | 678.1904
4052.176 | 678.671
4053.176 | 674.3196
4054.176 | 669.7891
4055.176 | 662.1493
4056.176 | 662.4892
4057.176 | 658.8987
4058.176 | 657.5678
4059.176 | 663.073
4060.176 | 665.4485
4061.176 | 671.5872
4062.176 | 672.7145
4063.176 | 669.5218
4064.176 | 670.6574
4065.176 | 670.2109
4066.176 | 667.7211
4067.176 | 666
4068.176 | 664.0888
4069.176 | 667.7804
4070.176 | 668.2636
4071.176 | 668.9514
4072.176 | 669.8556
4073.176 | 670.7786
4074.176 | 670.1771
4075.176 | 669.4944
4076.176 | 669.8788
4077.176 | 671.0697
4078.176 | 670.7572
4079.176 | 671.4096
4080.176 | 669.542
4081.176 | 671.0172
4082.176 | 671.0298
4083.176 | 669.9573
4084.176 | 667.6755
4085.176 | 665.4668
4086.176 | 665.4093
4087.176 | 662.1108
4088.176 | 661.3034
4089.176 | 661.7028
4090.176 | 659.9209
4091.176 | 661.7567
4092.176 | 664.2628
4093.176 | 664.9735
4094.176 | 666.6993
4095.176 | 669.3315
4096.176 | 670.8744
4097.176 | 672.5025
4098.176 | 673.5943
4099.176 | 673.6596
4100.176 | 673.8576
4101.176 | 674.9449
4102.176 | 676.9039
4103.176 | 680.3239
4104.176 | 682.5993
4105.176 | 685.8099
4106.176 | 685.3004
4107.176 | 683.5933
4108.176 | 683.5752
4109.176 | 685.1682
4110.176 | 683.9391
4111.176 | 683.9923
4112.176 | 683.8153
4113.176 | 684.479
4114.176 | 682.504
4115.176 | 679.7628
4116.176 | 678.0478
4117.176 | 676.2296
4118.176 | 673.8494
4119.176 | 671.1137
4120.176 | 667.5815
4121.176 | 663.9861
4122.176 | 660.1886
4123.176 | 658.7508
4124.176 | 657.9688
4125.176 | 657.8799
4126.176 | 656.7352
4127.176 | 657.1587
4128.176 | 655.8959
4129.176 | 654.9213
4130.176 | 655.9457
4131.176 | 657.8267
4132.176 | 657.6278
4133.176 | 660.1107
4134.176 | 661.0387
4135.176 | 658.3285
4136.176 | 658.9858
4137.176 | 659.8219
4138.176 | 661.9155
4139.176 | 664.0154
4140.176 | 665.9052
4141.176 | 668.8466
4142.176 | 672.8255
4143.176 | 675.5509
4144.176 | 680.8168
4145.176 | 685.648
4146.176 | 691.3484
4147.176 | 696.3857
4148.176 | 699.8684
4149.176 | 703.7198
4150.176 | 707.6745
4151.176 | 710.0716
4152.176 | 716.0848
4153.176 | 720.8937
4154.176 | 723.5337
4155.176 | 725.0408
4156.176 | 724.8604
4157.176 | 722.74
4158.176 | 721.0114
4159.176 | 717.221
4160.176 | 715.2437
4161.176 | 713.5294
4162.176 | 710.7693
4163.176 | 706.4603
4164.176 | 703.6043
4165.176 | 701.639
4166.176 | 700.1087
4167.176 | 699.0381
4168.176 | 698.8414
4169.176 | 695.4378
4170.176 | 693.4891
4171.176 | 694.6874
4172.176 | 695.4342
4173.176 | 696.5292
4174.176 | 697.607
4175.176 | 699.576
4176.176 | 703.1965
4177.176 | 704.7337
4178.176 | 704.1045
4179.176 | 703.2429
4180.176 | 699.318
4181.176 | 697.6289
4182.176 | 697.1758
4183.176 | 694.8478
4184.176 | 691.5932
4185.176 | 690.0111
4186.176 | 688.08
4187.176 | 687.5821
4188.176 | 684.9924
4189.176 | 679.3843
4190.176 | 675.1399
4191.176 | 672.8183
4192.176 | 672.0711
4193.176 | 671.2654
4194.176 | 668.5651
4195.176 | 666.3093
4196.176 | 665.5184
4197.176 | 665.1227
4198.176 | 667.3534
4199.176 | 668.7325
4200.176 | 667.9567
4201.176 | 667.8698
4202.176 | 670.1067
4203.1917 | 672.7377
4204.176 | 674.4138
4205.176 | 675.0353
4206.176 | 676.7593
4207.176 | 677.5538
4208.176 | 678.6748
4209.176 | 679.4436
4210.176 | 679.1508
4211.176 | 676.3026
4212.176 | 674.7726
4213.176 | 674.4865
4214.176 | 673.7555
4215.176 | 671.1397
4216.176 | 668.0285
4217.176 | 665.774
4218.176 | 664.2165
4219.176 | 662.5715
4220.176 | 662.093
4221.176 | 668.7113
4222.176 | 673.9534
4223.176 | 677.1538
4224.176 | 678.6305
4225.176 | 678.5408
4226.176 | 679.1516
4227.176 | 676.151
4228.176 | 673.9825
4229.176 | 670.6393
4230.176 | 669.9459
4231.176 | 668.9561
4232.176 | 668.1623
4233.176 | 670.4159
4234.176 | 670.2467
4235.176 | 672.9367
4236.176 | 674.7048
4237.176 | 675.3514
4238.176 | 675.0056
4239.176 | 675.7668
4240.176 | 678.0973
4241.176 | 679.6857
4242.176 | 680.791
4243.176 | 680.3318
4244.176 | 680.1428
4245.176 | 680.4888
4246.176 | 681.1859
4247.176 | 681.2481
4248.176 | 683.4175
4249.176 | 684.4754
4250.176 | 682.7474
4251.176 | 681.848
4252.176 | 679.272
4253.176 | 680.8529
4254.176 | 682.2244
4255.176 | 682.007
4256.176 | 682.5755
4257.176 | 681.9852
4258.176 | 682.3741
4259.176 | 682.711
4260.176 | 679.0632
4261.176 | 676.7825
4262.1917 | 675.8293
4263.1917 | 673.2295
4264.176 | 672.3944
4265.176 | 671.3004
4266.176 | 668.3835
4267.176 | 666.635
4268.176 | 665.2264
4269.176 | 664.9083
4270.176 | 667.314
4271.176 | 668.2089
4272.176 | 666.9142
4273.176 | 666.4171
4274.176 | 665.8785
4275.176 | 670.1119
4276.176 | 678.3413
4277.176 | 679.2173
4278.176 | 678.6742
4279.176 | 680.588
4280.176 | 684.259
4281.176 | 686.6697
4282.176 | 687.2686
4283.176 | 688.3454
4284.176 | 686.9749
4285.176 | 687.1892
4286.176 | 687.7401
4287.176 | 687.3457
4288.176 | 684.2424
4289.176 | 683.4264
4290.176 | 682.2855
4291.176 | 678.8655
4292.176 | 676.743
4293.176 | 675.4926
4294.176 | 681.11
4295.176 | 682.6866
4296.176 | 679.4852
4297.176 | 677.6422
4298.176 | 675.6363
4299.176 | 674.524
4300.176 | 675.2553
4301.176 | 676.2078
4302.176 | 677.6799
4303.176 | 681.2793
4304.176 | 682.9552
4305.176 | 684.0696
4306.176 | 684.1801
4307.176 | 685.4537
4308.176 | 685.6114
4309.176 | 683.0987
4310.176 | 680.9711
4311.176 | 677.7249
4312.176 | 674.994
4313.176 | 674.0101
4314.176 | 675.7105
4315.176 | 680.5647
4316.176 | 681.5022
4317.176 | 682.2807
4318.176 | 682.5749
4319.176 | 684.942
4320.176 | 684.5552
4321.176 | 683.1666
4322.176 | 681.6419
4323.176 | 683.2269
4324.176 | 685.0837
4325.176 | 685.123
4326.176 | 683.4807
4327.176 | 681.166
4328.176 | 679.0682
4329.176 | 677.7976
4330.176 | 679.0778
4331.176 | 680.035
4332.176 | 682.5416
4333.176 | 682.0417
4334.176 | 682.5947
4335.176 | 688.2048
4336.176 | 688.8333
4337.176 | 684.8567
4338.176 | 679.409
4339.176 | 672.9866
4340.176 | 673.3033
4341.176 | 680.0613
4342.176 | 680.87
4343.176 | 682.5142
4344.176 | 684.9196
4345.176 | 684.7091
4346.176 | 682.3806
4347.176 | 681.7986
4348.176 | 679.3628
4349.176 | 678.0267
4350.176 | 678.6308
4351.176 | 681.6496
4352.176 | 684.5574
4353.176 | 685.031
4354.176 | 686.7891
4355.176 | 689.318
4356.176 | 691.8833
4357.176 | 694.4914
4358.176 | 694.6419
4359.176 | 696.9711
4360.176 | 696.5353
4361.176 | 696.8952
4362.176 | 696.1997
4363.176 | 696.563
4364.176 | 697.4161
4365.176 | 698.7438
4366.176 | 699.8691
4367.176 | 699.6087
4368.176 | 698.8122
4369.176 | 697.078
4370.176 | 696.1604
4371.176 | 694.3327
4372.176 | 692.6438
4373.176 | 690.1364
4374.176 | 689.0463
4375.176 | 685.7553
4376.176 | 686.006
4377.176 | 683.8113
4378.176 | 681.812
4379.176 | 679.9937
4380.176 | 681.9408
4381.176 | 679.9129
4382.176 | 677.3988
4383.176 | 674.0471
4384.176 | 673.1062
4385.176 | 669.1139
4386.176 | 665.6387
4387.176 | 667.093
4388.176 | 671.2123
4389.176 | 673.3959
4390.176 | 672.9908
4391.176 | 675.1207
4392.176 | 676.3053
4393.176 | 677.6525
4394.176 | 678.4923
4395.176 | 676.6462
4396.176 | 673.1132
4397.176 | 670.1692
4398.176 | 668.8646
4399.176 | 666.0104
4400.176 | 666.9954
4401.176 | 668.0428
4402.176 | 669.5971
4403.176 | 669.3446
4404.176 | 669.5359
4405.176 | 670.3434
4406.176 | 671.8391
4407.176 | 670.6567
4408.176 | 668.0564
4409.176 | 666.8104
4410.176 | 668.328
4411.176 | 672.1294
4412.176 | 671.6328
4413.176 | 670.4926
4414.176 | 668.7833
4415.176 | 669.6046
4416.176 | 668.9721
4417.176 | 666.0742
4418.176 | 665.4561
4419.176 | 661.8317
4420.176 | 659.8477
4421.176 | 657.2696
4422.176 | 657.5508
4423.176 | 655.9282
4424.176 | 655.8387
4425.176 | 655.0702
4426.176 | 654.2193
4427.176 | 654.8837
4428.176 | 655.942
4429.176 | 661.2859
4430.176 | 664.3418
4431.176 | 666.8136
4432.176 | 667.832
4433.176 | 668.3499
4434.1917 | 668.1083
4435.176 | 667.4986
4436.176 | 667.4732
4437.176 | 668.0101
4438.176 | 668.4349
4439.176 | 670.3276
4440.176 | 672.1997
4441.176 | 671.9999
4442.176 | 669.7527
4443.176 | 672.8446
4444.176 | 677.2682
4445.176 | 679.8271
4446.176 | 679.8207
4447.176 | 679.7114
4448.176 | 679.8271
4449.176 | 679.819
4450.176 | 680.9752
4451.176 | 680.5717
4452.176 | 682.1434
4453.176 | 684.4826
4454.176 | 685.4653
4455.176 | 686.3572
4456.176 | 687.3499
4457.176 | 689.3952
4458.176 | 691.4245
4459.176 | 691.0191
4460.176 | 688.1101
4461.176 | 682.8239
4462.176 | 679.8646
4463.176 | 678.1792
4464.176 | 677.16
4465.176 | 673.9588
4466.176 | 671.6939
4467.176 | 668.3086
4468.176 | 665.3027
4469.176 | 663.8211
4470.176 | 661.6259
4471.176 | 663.34
4472.176 | 663.5409
4473.176 | 663.8497
4474.176 | 665.2386
4475.176 | 664.8503
4476.176 | 663.3775
4477.176 | 662.9174
4478.1917 | 661.3469
4479.176 | 660.7246
4480.176 | 658.9341
4481.176 | 656.1785
4482.176 | 652.7947
4483.176 | 654.7027
4484.176 | 659.1989
4485.176 | 659.6474
4486.176 | 663.0655
4487.176 | 665.0019
4488.176 | 664.9189
4489.176 | 662.5377
4490.176 | 663.7837
4491.176 | 665.3974
4492.176 | 668.0572
4493.176 | 673.1374
4494.176 | 674.3074
4495.176 | 674.887
4496.176 | 675.9109
4497.176 | 679.6402
4498.176 | 679.5254
4499.176 | 677.6247
4500.176 | 675.7016
4501.176 | 674.7392
4502.176 | 673.4319
4503.176 | 671.8413
4504.176 | 667.5659
4505.176 | 665.7685
4506.176 | 662.8736
4507.176 | 662.1981
4508.176 | 661.2636
4509.176 | 658.0169
4510.176 | 656.1794
4511.176 | 655.3236
4512.176 | 660.207
4513.176 | 662.2232
4514.176 | 661.1873
4515.176 | 659.393
4516.176 | 659.8423
4517.176 | 662.1658
4518.176 | 664.4281
4519.176 | 665.8988
4520.176 | 668.695
4521.176 | 671.6291
4522.176 | 671.5966
4523.176 | 674.8229
4524.176 | 673.9737
4525.176 | 672.696
4526.176 | 674.4682
4527.176 | 674.8178
4528.176 | 676.4117
4529.176 | 676.9248
4530.176 | 679.3896
4531.176 | 681.0387
4532.176 | 681.0405
4533.176 | 680.3609
4534.176 | 683.1507
4535.176 | 685.6898
4536.176 | 687.3962
4537.176 | 690.2367
4538.176 | 690.9055
4539.176 | 690.9172
4540.176 | 690.0375
4541.176 | 688.7499
4542.176 | 686.4187
4543.176 | 686.8255
4544.176 | 687.094
4545.176 | 687.1976
4546.176 | 686.1145
4547.176 | 686.6114
4548.176 | 685.7992
4549.176 | 685.0348
4550.176 | 678.6251
4551.176 | 672.9928
4552.176 | 671.4428
4553.176 | 667.7043
4554.176 | 664.4037
4555.176 | 661.1215
4556.176 | 659.6587
4557.176 | 657.8711
4558.176 | 659.4696
4559.176 | 662.0951
4560.176 | 658.872
4561.176 | 655.4693
4562.176 | 655.3363
4563.1917 | 656.4245
4564.176 | 656.4257
4565.176 | 654.977
4566.176 | 658.6678
4567.176 | 660.5529
4568.176 | 662.2456
4569.176 | 660.5235
4570.176 | 660.573
4571.176 | 660.0205
4572.176 | 657.6867
4573.176 | 656.2005
4574.176 | 651.9951
4575.176 | 650.6965
4576.176 | 656.0466
4577.176 | 654.366
4578.176 | 657.0241
4579.176 | 656.4805
4580.176 | 658.5414
4581.176 | 659.2327
4582.176 | 661.0573
4583.176 | 660.4259
4584.176 | 663.9343
4585.176 | 658.9472
4586.176 | 659.7708
4587.176 | 661.948
4588.176 | 660.5552
4589.176 | 663.3294
4590.176 | 671.2399
4591.176 | 672.3677
4592.176 | 669.163
4593.176 | 669.8739
4594.176 | 668.233
4595.176 | 674.1646
4596.176 | 673.4298
4597.176 | 674.65
4598.176 | 671.4868
4599.176 | 668.4241
4600.176 | 671.4773
4601.176 | 670.9669
4602.176 | 672.9004
4603.176 | 674.5492
4604.176 | 673.3828
4605.176 | 676.68
4606.176 | 674.5171
4607.176 | 676.7318
4608.176 | 678.9902
4609.176 | 677.7218
4610.176 | 677.4278
4611.176 | 673.4783
4612.176 | 678.2384
4613.176 | 675.3
4614.176 | 675.279
4615.176 | 675.8475
4616.176 | 673.5454
4617.176 | 669.5141
4618.176 | 666.85
4619.176 | 662.4061
4620.176 | 663.021
4621.176 | 666.9497
4622.176 | 666.824
4623.1917 | 669.177
4624.176 | 670.49
4625.176 | 666.7885
4626.176 | 667.6619
4627.176 | 665.5918
4628.176 | 665.4459
4629.176 | 665.5343
4630.176 | 663.5752
4631.176 | 666.1266
4632.176 | 665.2338
4633.176 | 666.9593
4634.176 | 669.0771
4635.176 | 670.6624
4636.176 | 671.5596
4637.176 | 668.9316
4638.176 | 669.2602
4639.176 | 669.3593
4640.176 | 667.6623
4641.176 | 668.0457
4642.176 | 668.2784
4643.176 | 665.3343
4644.176 | 666.2804
4645.176 | 660.8396
4646.176 | 660.8745
4647.176 | 662.8858
4648.176 | 668.425
4649.176 | 668.1786
4650.176 | 662.8375
4651.176 | 662.0572
4652.176 | 659.2982
4653.176 | 661.7284
4654.176 | 660.5121
4655.176 | 664.0748
4656.176 | 663.0224
4657.176 | 660.8518
4658.176 | 664.7608
4659.176 | 662.8275
4660.176 | 663.0498
4661.176 | 662.2412
4662.176 | 660.8381
4663.176 | 654.5864
4664.176 | 650.7269
4665.176 | 651.3701
4666.176 | 650.0807
4667.176 | 658.0725
4668.176 | 658.4041
4669.176 | 664.4661
4670.176 | 667.828
4671.176 | 668.3863
4672.176 | 670.1478
4673.176 | 668.6482
4674.176 | 664.1345
4675.176 | 659.4641
4676.176 | 655.8308
4677.176 | 649.4273
4678.176 | 647.1838
4679.176 | 646.7647
4680.176 | 649.8506
4681.176 | 645.715
4682.176 | 645.0763
4683.176 | 645.4611
4684.176 | 646.2321
4685.176 | 644.7784
4686.176 | 644.3539
4687.176 | 641.1411
4688.176 | 641.8216
4689.176 | 640.6619
4690.176 | 637.9946
4691.176 | 640.689
4692.176 | 637.863
4693.176 | 637.0289
4694.176 | 634.4387
4695.176 | 628.8662
4696.176 | 630.3931
4697.176 | 631.3877
4698.176 | 630.709
4699.176 | 631.3802
4700.176 | 631.5396
4701.176 | 639.0409
4702.176 | 642.5868
4703.176 | 642.2304
4704.176 | 642.5982
4705.176 | 644.6086
4706.176 | 644.5022
4707.176 | 644.3066
4708.176 | 643.2721
4709.176 | 645.4803
4710.176 | 639.6933
4711.176 | 641.0138
4712.176 | 643.3249
4713.176 | 645.0728
4714.176 | 643.07
4715.176 | 643.8888
4716.176 | 641.5982
4717.176 | 642.6171
4718.176 | 643.7618
4719.176 | 640.7129
4720.176 | 644.4653
4721.176 | 642.6991
4722.176 | 642.7983
4723.176 | 642.5384
4724.176 | 642.0466
4725.176 | 639.1498
4726.176 | 639.3802
4727.176 | 640.001
4728.176 | 640.5151
4729.176 | 639.1109
4730.176 | 636.7235
4731.176 | 640.197
4732.176 | 640.4251
4733.176 | 641.0571
4734.176 | 642.0927
4735.176 | 644.6187
4736.176 | 641.8817
4737.176 | 643.1907
4738.176 | 644.6065
4739.176 | 649.5581
4740.176 | 652.0941
4741.176 | 663.7227
4742.176 | 668.7025
4743.176 | 666.8068
4744.176 | 671.1248
4745.176 | 664.4023
4746.176 | 662.0484
4747.176 | 659.2642
4748.176 | 662.0616
4749.176 | 662.465
4750.176 | 662.3186
4751.176 | 659.187
4752.176 | 658.0469
4753.176 | 655.7968
4754.176 | 659.2808
4755.176 | 659.6161
4756.176 | 659.3972
4757.176 | 662.4526
4758.176 | 662.0191
4759.176 | 660.1551
4760.176 | 658.2904
4761.176 | 658.8876
4762.176 | 659.2429
4763.176 | 658.7772
4764.176 | 659.183
4765.176 | 661.4877
4766.176 | 659.1228
4767.176 | 660.5451
4768.176 | 666.2428
4769.176 | 670.3095
4770.176 | 673.0824
4771.176 | 675.1513
4772.176 | 674.497
4773.176 | 672.9361
4774.176 | 671.2247
4775.176 | 669.6798
4776.176 | 669.32
4777.176 | 665.5786
4778.176 | 664.6114
4779.176 | 662.4592
4780.176 | 665.3476
4781.176 | 669.0389
4782.176 | 670.5565
4783.176 | 668.4751
4784.176 | 671.6278
4785.176 | 673.0723
4786.176 | 676.6254
4787.176 | 681.2327
4788.176 | 682.8138
4789.176 | 678.1985
4790.176 | 676.0314
4791.176 | 672.519
4792.176 | 666.8471
4793.176 | 665.3141
4794.176 | 667.6815
4795.176 | 665.8152
4796.176 | 667.0172
4797.176 | 666.615
4798.176 | 668.9325
4799.176 | 670.3013
4800.176 | 671.745
4801.176 | 670.1582
4802.176 | 667.6018
4803.176 | 666.5367
4804.176 | 667.6702
4805.176 | 672.8548
4806.176 | 671.722
4807.176 | 676.6415
4808.176 | 676.4364
4809.176 | 678.7824
4810.176 | 678.1108
4811.176 | 677.6583
4812.176 | 674.9562
4813.176 | 674.9166
4814.176 | 671.9602
4815.176 | 668.2892
4816.176 | 665.864
4817.176 | 664.9494
4818.176 | 661.9014
4819.176 | 659.6064
4820.176 | 658.5355
4821.176 | 659.6784
4822.176 | 658.2801
4823.176 | 656.8426
4824.176 | 656.3766
4825.176 | 657.8325
4826.176 | 661.1247
4827.176 | 668.1386
4828.176 | 676.6792
4829.176 | 674.851
4830.176 | 674.7269
4831.176 | 672.306
4832.176 | 669.4701
4833.176 | 666.8837
4834.176 | 667.6493
4835.176 | 665.4826
4836.176 | 663.8714
4837.176 | 663.1651
4838.176 | 668.237
4839.176 | 672.6586
4840.176 | 672.1365
4841.176 | 673.5247
4842.176 | 674.432
4843.176 | 673.04
4844.176 | 671.2468
4845.176 | 667.3143
4846.176 | 667.1482
4847.176 | 666.3521
4848.176 | 671.7911
4849.176 | 676.637
4850.176 | 672.9942
4851.176 | 675.2827
4852.176 | 672.2708
4853.176 | 670.3291
4854.176 | 668.3325
4855.176 | 667.682
4856.176 | 668.8042
4857.176 | 670.8693
4858.176 | 670.4309
4859.176 | 670.0838
4860.176 | 666.9547
4861.176 | 663.0101
4862.176 | 660.1562
4863.176 | 658.0322
4864.176 | 656.6972
4865.176 | 655.8172
4866.176 | 655.5713
4867.176 | 651.8376
4868.176 | 655.7565
4869.176 | 656.7333
4870.176 | 658.3646
4871.176 | 665.291
4872.176 | 665.9205
4873.176 | 667.5181
4874.176 | 666.16
4875.176 | 664.977
4876.176 | 663.2871
4877.176 | 661.3567
4878.176 | 658.6704
4879.176 | 656.3945
4880.176 | 653.752
4881.176 | 653.0554
4882.176 | 654.4547
4883.176 | 653.9023
4884.176 | 652.8218
4885.176 | 651.1985
4886.176 | 649.9416
4887.176 | 650.3077
4888.176 | 652.4141
4889.176 | 651.764
4890.176 | 650.6936
4891.176 | 651.0547
4892.176 | 652.6396
4893.176 | 653.1928
4894.176 | 651.2518
4895.176 | 648.9515
4896.176 | 648.2945
4897.176 | 648.2391
4898.176 | 648.1614
4899.176 | 646.8358
4900.176 | 646.0671
4901.176 | 646.538
4902.176 | 647.5305
4903.176 | 647.6681
4904.176 | 647.5026
4905.176 | 646.8597
4906.176 | 646.6741
4907.176 | 646.6442
4908.176 | 649.6703
4909.176 | 650.6336
4910.176 | 648.9857
4911.176 | 647.458
4912.176 | 648.7238
4913.176 | 652.7845
4914.176 | 653.8314
4915.176 | 654.9788
4916.176 | 656.5283
4917.176 | 659.2157
4918.176 | 662.5676
4919.176 | 664.1762
4920.176 | 663.693
4921.176 | 661.5882
4922.176 | 660.5283
4923.176 | 660.0686
4924.176 | 661.679
4925.176 | 661.6909
4926.176 | 660.5446
4927.176 | 661.2414
4928.176 | 665.3776
4929.176 | 666.3017
4930.176 | 669.1455
4931.176 | 669.0752
4932.176 | 666.6972
4933.176 | 665.9431
4934.176 | 665.6697
4935.176 | 663.8364
4936.176 | 664.8415
4937.176 | 665.7431
4938.176 | 666.5116
4939.176 | 667.8192
4940.176 | 668.5838
4941.176 | 667.5415
4942.176 | 671.7753
4943.176 | 676.7937
4944.176 | 678.3288
4945.176 | 678.8097
4946.176 | 677.5649
4947.176 | 675.4254
4948.176 | 679.8225
4949.176 | 682.5667
4950.176 | 683.4683
4951.176 | 684.637
4952.176 | 684.6462
4953.176 | 686.4413
4954.176 | 688.9338
4955.176 | 688.6436
4956.176 | 688.5383
4957.176 | 688.3568
4958.176 | 687.1448
4959.176 | 687.1304
4960.176 | 686.0032
4961.176 | 686.4269
4962.176 | 683.0014
4963.176 | 680.8717
4964.176 | 677.9345
4965.176 | 677.0418
4966.176 | 675.4404
4967.176 | 675.9382
4968.176 | 676.7887
4969.176 | 673.1796
4970.176 | 669.9309
4971.176 | 667.0522
4972.176 | 665.5225
4973.176 | 662.4525
4974.176 | 662.2503
4975.176 | 663.7903
4976.176 | 663.3262
4977.176 | 660.8914
4978.176 | 657.9375
4979.176 | 656.7351
4980.176 | 655.4229
4981.176 | 656.4741
4982.176 | 655.0146
4983.176 | 651.378
4984.176 | 650.9474
4985.176 | 649.26
4986.176 | 650.5864
4987.176 | 650.059
4988.176 | 651.2792
4989.176 | 651.8075
4990.176 | 654.2498
4991.176 | 651.801
4992.176 | 653.2676
4993.176 | 652.2372
4994.176 | 652.7299
4995.176 | 653.4338
4996.176 | 654.8108
4997.176 | 657.8972
4998.176 | 658.9874
4999.176 | 660.829
5000.176 | 664.586
5001.176 | 668.1509
5002.176 | 670.3559
5003.176 | 669.2393
5004.176 | 664.412
5005.176 | 661.6868
5006.176 | 662.5151
5007.176 | 662.1539
5008.176 | 658.7384
5009.176 | 657.8137
5010.176 | 657.6699
5011.176 | 656.2736
5012.176 | 655.2147
5013.176 | 654.0178
5014.176 | 653.5914
5015.176 | 653.0421
5016.176 | 651.1079
5017.176 | 649.9611
5018.176 | 649.1786
5019.176 | 649.9188
5020.176 | 650.7476
5021.176 | 654.3224
5022.176 | 654.1506
5023.176 | 653.0452
5024.176 | 654.732
5025.176 | 654.9598
5026.176 | 656.2346
5027.176 | 654.2223
5028.176 | 653.5507
5029.176 | 653.0242
5030.176 | 653.9382
5031.176 | 654.3807
5032.176 | 652.747
5033.176 | 654.1796
5034.176 | 654.4103
5035.176 | 654.8849
5036.176 | 656.218
5037.176 | 656.4968
5038.176 | 656.8577
5039.176 | 661.3801
5040.176 | 667.0944
5041.176 | 669.4843
5042.176 | 671.4042
5043.176 | 671.4843
5044.176 | 672.9418
5045.176 | 671.2546
5046.176 | 670.6397
5047.176 | 667.1947
5048.176 | 664.0184
5049.176 | 664.3273
5050.176 | 664.4329
5051.176 | 667.0694
5052.176 | 668.922
5053.176 | 669.8
5054.176 | 669.6891
5055.176 | 667.9022
5056.176 | 665.3201
5057.176 | 670.4463
5058.176 | 673.4849
5059.176 | 671.9954
5060.176 | 672.6766
5061.176 | 673.0035
5062.176 | 673.8167
5063.176 | 673.0676
5064.176 | 671.1174
5065.176 | 671.8044
5066.176 | 672.7856
5067.176 | 674.3683
5068.176 | 673.8625
5069.176 | 672.7019
5070.176 | 671.937
5071.176 | 670.3573
5072.176 | 670.6191
5073.176 | 672.3783
5074.176 | 673.0643
5075.176 | 670.9336
5076.176 | 673.6808
5077.176 | 672.3654
5078.176 | 677.229
5079.176 | 677.0526
5080.176 | 676.4939
5081.176 | 676.4409
5082.176 | 675.0165
5083.176 | 671.1715
5084.176 | 670.5682
5085.176 | 668.6057
5086.176 | 665.1164
5087.176 | 662.288
5088.176 | 660.0401
5089.176 | 654.3469
5090.176 | 656.9232
5091.176 | 655.0723
5092.176 | 652.4681
5093.176 | 648.6637
5094.176 | 650.9895
5095.176 | 654.1395
5096.176 | 653.5348
5097.176 | 651.5751
5098.176 | 646.8079
5099.176 | 653.8128
5100.176 | 654.2901
5101.176 | 655.798
5102.176 | 650.118
5103.176 | 651.23
5104.176 | 649.1258
5105.176 | 653.5295
5106.176 | 652.379
5107.176 | 652.9945
5108.176 | 651.8113
5109.176 | 651.3629
5110.176 | 651.882
5111.176 | 648.4303
5112.176 | 654.8657
5113.176 | 649.8461
5114.176 | 650.5147
5115.176 | 648.3936
5116.176 | 656.8081
5117.176 | 653.7192
5118.176 | 654.2033
5119.176 | 650.0285
5120.176 | 649.9105
5121.176 | 642.0324
5122.176 | 646.818
5123.176 | 642.2625
5124.176 | 644.8727
5125.176 | 643.5291
5126.176 | 641.9028
5127.176 | 635.3584
5128.176 | 640.467
5129.1917 | 641.8741
5130.176 | 642.0982
5131.176 | 640.7695
5132.176 | 639.4828
5133.176 | 637.1485
5134.1917 | 638.9726
5135.1917 | 641.777
5136.176 | 642.235
5137.176 | 641.4176
5138.176 | 635.4993
5139.176 | 637.6497
5140.176 | 636.8898
5141.176 | 634.2575
5142.176 | 631.7561
5143.176 | 635.8713
5144.176 | 635.5948
5145.176 | 631.9938
5146.176 | 639.5353
5147.176 | 644.5835
5148.176 | 644.3662
5149.176 | 647.749
5150.176 | 646.6749
5151.176 | 648.1842
5152.176 | 648.8233
5153.176 | 646.8086
5154.176 | 649.4415
5155.176 | 649.4386
5156.176 | 656.9837
5157.176 | 658.0693
5158.176 | 655.8099
5159.176 | 657.7397
5160.176 | 656.9985
5161.176 | 657.8279
5162.176 | 654.0199
5163.176 | 662.573
5164.176 | 664.6971
5165.176 | 663.9509
5166.176 | 664.6462
5167.176 | 668.8419
5168.176 | 670.6781
5169.176 | 667.9836
5170.176 | 667.2814
5171.176 | 672.5283
5172.176 | 671.4746
5173.176 | 666.9653
5174.176 | 671.6066
5175.176 | 676.8772
5176.176 | 678.8772
5177.176 | 681.1141
5178.176 | 681.5573
5179.176 | 681.2431
5180.176 | 679.4916
5181.176 | 678.3311
5182.176 | 678.269
5183.176 | 677.7349
5184.176 | 675.6982
5185.176 | 676.5986
5186.176 | 675.1117
5187.176 | 676.5062
5188.176 | 673.5567
5189.176 | 674.1495
5190.176 | 673.2721
5191.176 | 673.7048
5192.176 | 674.2874
5193.176 | 675.4781
5194.176 | 681.0122
5195.176 | 678.233
5196.176 | 680.3225
5197.176 | 674.3512
5198.176 | 677.1329
5199.176 | 677.2096
5200.176 | 678.8156
5201.176 | 675.6086
5202.176 | 673.7243
5203.176 | 675.5304
5204.176 | 674.9637
5205.176 | 673.2929
5206.176 | 672.7118
5207.176 | 672.8568
5208.176 | 671.5001
5209.176 | 671.9882
5210.176 | 670.0682
5211.176 | 667.2044
5212.176 | 667.308
5213.176 | 665.1018
5214.176 | 664.9964
5215.176 | 664.2619
5216.176 | 661.5701
5217.176 | 660.3972
5218.176 | 660.6188
5219.176 | 658.8028
5220.176 | 655.6827
5221.176 | 655.8547
5222.176 | 653.8506
5223.176 | 649.4701
5224.176 | 645.5935
5225.176 | 644.5701
5226.176 | 642.8505
5227.176 | 641.4504
5228.176 | 641.9489
5229.176 | 646.2071
5230.176 | 646.9088
5231.176 | 647.2406
5232.176 | 646.5077
5233.176 | 645.3782
5234.176 | 642.7908
5235.176 | 640.5272
5236.176 | 641.3926
5237.176 | 640.2841
5238.176 | 638.7696
5239.176 | 636.9989
5240.176 | 633.8726
5241.176 | 630.9396
5242.176 | 628.2541
5243.176 | 629.0088
5244.176 | 629.2729
5245.176 | 628.9532
5246.176 | 628.4434
5247.176 | 632.2396
5248.176 | 634.8226
5249.176 | 634.7284
5250.176 | 636.2188
5251.176 | 637.0064
5252.176 | 636.8218
5253.176 | 634.5334
5254.176 | 632.1941
5255.176 | 631.2751
5256.176 | 630.4751
5257.176 | 630.1458
5258.176 | 630.016
5259.176 | 632.5078
5260.176 | 632.4558
5261.176 | 631.8358
5262.176 | 631.5447
5263.176 | 633.1445
5264.176 | 632.3748
5265.176 | 632.1782
5266.176 | 634.3018
5267.176 | 635.2251
5268.176 | 635.2696
5269.176 | 637.3751
5270.176 | 638.5727
5271.176 | 642.0988
5272.176 | 645.3111
5273.176 | 645.5535
5274.176 | 648.2441
5275.176 | 651.0132
5276.176 | 654.2203
5277.176 | 655.6836
5278.176 | 657.3918
5279.176 | 659.9581
5280.176 | 659.4906
5281.176 | 659.8472
5282.176 | 665.0326
5283.176 | 664.4799
5284.176 | 664.0852
5285.176 | 663.2453
5286.176 | 660.6091
5287.176 | 658.1577
5288.176 | 657.5555
5289.176 | 656.13
5290.176 | 660.0656
5291.176 | 661.6949
5292.176 | 660.844
5293.176 | 661.5282
5294.176 | 662.3711
5295.176 | 660.3385
5296.176 | 657.8642
5297.176 | 654.8318
5298.176 | 654.1337
5299.176 | 655.3998
5300.176 | 655.9664
5301.176 | 659.5196
5302.176 | 656.8061
5303.176 | 656.2125
5304.176 | 656.1987
5305.1917 | 661.2054
5306.176 | 660.7048
5307.176 | 661.3678
5308.176 | 661.6301
5309.176 | 663.222
5310.176 | 666.5722
5311.176 | 671.6184
5312.176 | 675.7963
5313.176 | 680.9082
5314.176 | 684.649
5315.176 | 686.31
5316.176 | 685.904
5317.176 | 685.5268
5318.176 | 687.4219
5319.176 | 689.9153
5320.176 | 687.7374
5321.176 | 691.2276
5322.176 | 695.0467
5323.176 | 697.7807
5324.176 | 698.7105
5325.176 | 700.237
5326.176 | 700.049
5327.176 | 699.2153
5328.176 | 700.1601
5329.176 | 698.703
5330.176 | 699.3639
5331.176 | 700.6871
5332.176 | 700.3514
5333.176 | 703.1493
5334.176 | 704.7368
5335.1917 | 709.6684
5336.176 | 712.4251
5337.176 | 715.96
5338.176 | 718.8792
5339.176 | 720.5001
5340.176 | 723.9776
5341.176 | 723.4844
5342.176 | 722.5947
5343.176 | 724.2014
5344.176 | 724.3049
5345.176 | 722.5927
5346.176 | 718.1902
5347.176 | 716.1762
5348.176 | 714.4476
5349.176 | 713.8325
5350.176 | 712.9235
5351.176 | 714.0822
5352.176 | 716.5945
5353.176 | 715.4571
5354.176 | 713.8985
5355.176 | 710.8484
5356.176 | 709.3062
5357.176 | 706.4333
5358.176 | 703.6212
5359.176 | 704.8436
5360.176 | 704.0262
5361.176 | 703.7796
5362.176 | 698.3795
5363.176 | 692.5253
5364.176 | 686.4629
5365.176 | 680.1889
5366.176 | 676.9008
5367.176 | 673.0248
5368.176 | 667.6463
5369.176 | 663.6774
5370.176 | 659.7985
5371.176 | 657.0321
5372.176 | 654.7789
5373.176 | 652.9249
5374.176 | 652.442
5375.176 | 652.5617
5376.176 | 651.7446
5377.176 | 651.8157
5378.176 | 650.8923
5379.176 | 650.4761
5380.176 | 651.7073
5381.176 | 652.814
5382.176 | 652.7336
5383.176 | 654.0404
5384.176 | 655.5149
5385.176 | 658.0727
5386.176 | 658.9063
5387.176 | 658.8952
5388.176 | 657.1128
5389.176 | 655.5322
5390.176 | 654.4296
5391.176 | 653.3557
5392.176 | 651.1719
5393.176 | 650.3747
5394.176 | 650.3992
5395.1917 | 649.1511
5396.176 | 648.1002
5397.176 | 648.6888
5398.176 | 648.5759
5399.176 | 647.6076
5400.176 | 645.7463
5401.176 | 643.0176
5402.176 | 640.397
5403.176 | 639.5257
5404.176 | 641.0205
5405.176 | 644.3846
5406.176 | 645.0889
5407.176 | 644.5343
5408.176 | 645.1828
5409.176 | 644.7316
5410.176 | 645.0624
5411.176 | 644.6402
5412.176 | 644.4623
5413.176 | 642.927
5414.176 | 642.3652
5415.176 | 642.8637
5416.176 | 645.4358
5417.176 | 644.0723
5418.176 | 642.8287
5419.176 | 641.0973
5420.176 | 640.2762
5421.176 | 641.8106
5422.176 | 644.1508
5423.176 | 645.5326
5424.176 | 647.5607
5425.1917 | 655.6838
5426.176 | 657.3394
5427.176 | 657.5232
5428.176 | 657.3854
5429.176 | 654.6957
5430.176 | 655.5813
5431.176 | 654.6326
5432.176 | 655.8973
5433.176 | 655.8172
5434.176 | 657.9412
5435.176 | 660.9237
5436.176 | 665.5278
5437.176 | 671.9391
5438.176 | 673.9651
5439.176 | 675.2165
5440.176 | 678.8196
5441.176 | 684.3345
5442.176 | 686.4935
5443.176 | 691.668
5444.176 | 696.9574
5445.176 | 699.287
5446.176 | 703.2137
5447.176 | 707.9156
5448.176 | 713.0852
5449.176 | 715.7581
5450.176 | 715.8279
5451.176 | 713.9731
5452.176 | 712.441
5453.176 | 710.0495
5454.176 | 707.9893
5455.176 | 708.8117
5456.176 | 710.4765
5457.176 | 709.8042
5458.176 | 709.8439
5459.176 | 708.7403
5460.176 | 707.9903
5461.176 | 705.6626
5462.176 | 705.4192
5463.176 | 705.9105
5464.176 | 703.725
5465.176 | 701.4221
5466.176 | 699.0818
5467.176 | 697.623
5468.176 | 695.7193
5469.176 | 694.8658
5470.176 | 693.9033
5471.176 | 693.4755
5472.176 | 692.4809
5473.176 | 690.8797
5474.176 | 691.7715
5475.176 | 693.8131
5476.176 | 695.118
5477.176 | 695.9543
5478.176 | 697.0137
5479.176 | 696.9262
5480.176 | 697.1451
5481.176 | 696.0604
5482.176 | 694.8254
5483.176 | 693.2938
5484.176 | 690.1969
5485.176 | 691.0863
5486.176 | 689.1258
5487.176 | 687.5032
5488.176 | 688.548
5489.176 | 686.8344
5490.176 | 688.5548
5491.176 | 688.5444
5492.176 | 687.7772
5493.176 | 686.7446
5494.176 | 684.3257
5495.176 | 684.8082
5496.176 | 685.9982
5497.176 | 684.9853
5498.176 | 681.6974
5499.176 | 678.3415
5500.176 | 677.1817
5501.176 | 675.276
5502.176 | 672.4983
5503.176 | 669.8879
5504.176 | 669.4048
5505.176 | 668.5641
5506.176 | 667.3782
5507.176 | 667.7855
5508.176 | 671.8008
5509.176 | 672.1857
5510.176 | 670.2344
5511.176 | 667.8492
5512.176 | 666.4721
5513.176 | 665.3395
5514.176 | 665.1669
5515.176 | 664.035
5516.176 | 661.5316
5517.176 | 661.1944
5518.176 | 664.1873
5519.176 | 667.3536
5520.176 | 669.6231
5521.176 | 670.5806
5522.176 | 672.6933
5523.176 | 675.6691
5524.176 | 679.0552
5525.176 | 680.6662
5526.176 | 683.133
5527.176 | 690.5079
5528.176 | 693.2032
5529.176 | 694.7502
5530.176 | 696.5383
5531.176 | 698.4323
5532.176 | 700.5865
5533.176 | 699.8197
5534.176 | 697.7099
5535.176 | 695.3794
5536.176 | 694.5743
5537.176 | 695.4905
5538.176 | 695.2103
5539.176 | 694.5317
5540.176 | 694.3251
5541.176 | 691.3603
5542.176 | 689.7634
5543.176 | 689.7212
5544.176 | 688.2982
5545.176 | 685.9153
5546.176 | 683.9744
5547.176 | 681.7225
5548.176 | 680.8314
5549.176 | 680.6036
5550.176 | 678.5969
5551.176 | 677.8539
5552.176 | 676.8255
5553.176 | 675.2766
5554.176 | 672.868
5555.176 | 672.0109
5556.176 | 671.9956
5557.176 | 672.1117
5558.176 | 671.3728
5559.176 | 669.7739
5560.176 | 666.3281
5561.176 | 666.1386
5562.176 | 666.361
5563.176 | 665.208
5564.176 | 662.267
5565.176 | 658.6643
5566.176 | 656.8265
5567.176 | 655.2363
5568.176 | 655.0399
5569.176 | 655.7542
5570.176 | 654.7783
5571.176 | 653.8993
5572.176 | 652.5065
5573.176 | 650.8056
5574.176 | 648.5265
5575.176 | 648.1703
5576.176 | 647.3737
5577.176 | 646.6783
5578.176 | 646.1422
5579.176 | 646.5864
5580.176 | 648.9682
5581.176 | 652.5947
5582.176 | 657.6707
5583.176 | 657.3851
5584.176 | 656.7162
5585.176 | 654.4201
5586.176 | 653.8155
5587.176 | 653.0114
5588.176 | 654.0703
5589.176 | 655.815
5590.176 | 656.3612
5591.176 | 655.158
5592.176 | 653.3871
5593.176 | 652.8023
5594.176 | 652.9151
5595.176 | 652.534
5596.176 | 654.1899
5597.176 | 655.105
5598.176 | 655.5925
5599.176 | 653.8861
5600.176 | 652.2428
5601.176 | 650.5959
5602.176 | 649.1539
5603.176 | 646.3864
5604.176 | 644.1023
5605.176 | 641.9865
5606.176 | 641.0441
5607.176 | 641.8126
5608.176 | 639.8742
5609.176 | 640.4342
5610.176 | 641.5502
5611.176 | 642.1753
5612.176 | 643.6438
5613.176 | 645.6883
5614.176 | 648.7183
5615.176 | 650.2826
5616.176 | 652.6337
5617.176 | 658.4196
5618.176 | 664.6485
5619.176 | 666.3466
5620.176 | 668.2907
5621.176 | 668.7969
5622.176 | 670.3478
5623.176 | 674.9293
5624.176 | 677.9477
5625.176 | 681.3678
5626.176 | 681.7209
5627.2073 | 680.8862
5628.176 | 680.2103
5629.176 | 678.6854
5630.176 | 681.4593
5631.176 | 681.6943
5632.176 | 681.98
5633.176 | 681.5128
5634.176 | 679.7398
5635.176 | 679.2631
5636.176 | 678.8354
5637.176 | 676.4076
5638.176 | 674.1696
5639.176 | 671.1581
5640.176 | 670.4568
5641.176 | 670.2219
5642.176 | 669.3942
5643.176 | 668.7626
5644.176 | 669.128
5645.176 | 673.161
5646.176 | 673.7622
5647.176 | 673.6608
5648.176 | 674.4416
5649.176 | 675.1444
5650.176 | 675.4995
5651.176 | 674.6371
5652.176 | 677.5246
5653.176 | 682.163
5654.176 | 688.2137
5655.176 | 692.8093
5656.176 | 696.6612
5657.176 | 696.1027
5658.176 | 694.4352
5659.176 | 692.3385
5660.176 | 693.6622
5661.176 | 697.352
5662.176 | 701.668
5663.176 | 701.3977
5664.176 | 699.0155
5665.176 | 696.7986
5666.176 | 693.4221
5667.176 | 691.1518
5668.176 | 694.2964
5669.176 | 698.4006
5670.176 | 700.5425
5671.176 | 702.3469
5672.176 | 703.7523
5673.176 | 704.2461
5674.176 | 702.0109
5675.176 | 700.5596
5676.176 | 699.5058
5677.176 | 703.4409
5678.176 | 704.9581
5679.176 | 703.0322
5680.176 | 699.8999
5681.176 | 696.927
5682.176 | 693.7279
5683.176 | 690.2699
5684.176 | 688.6875
5685.176 | 686.2715
5686.176 | 686.1046
5687.176 | 686.3164
5688.176 | 685.6764
5689.176 | 690.8252
5690.176 | 692.2849
5691.176 | 692.4253
5692.176 | 690.6268
5693.176 | 687.2358
5694.176 | 684.4055
5695.176 | 683.1808
5696.176 | 682.754
5697.176 | 685.9797
5698.176 | 686.8993
5699.176 | 684.1466
5700.176 | 680.8721
5701.176 | 682.4155
5702.176 | 686.7644
5703.176 | 684.9715
5704.176 | 681.4182
5705.176 | 680.6131
5706.176 | 678.2941
5707.176 | 676.6327
5708.176 | 675.1015
5709.176 | 673.9009
5710.176 | 673.1953
5711.176 | 670.2594
5712.176 | 667.881
5713.176 | 663.8789
5714.176 | 661.0121
5715.176 | 658.4878
5716.176 | 657.2951
5717.176 | 668.0082
5718.176 | 672.8208
5719.176 | 672.1578
5720.176 | 668.9385
5721.176 | 665.279
5722.176 | 661.4328
5723.176 | 660.9114
5724.176 | 661.4528
5725.176 | 661.5957
5726.176 | 660.7692
5727.176 | 659.5867
5728.176 | 658.5279
5729.176 | 658.5324
5730.176 | 663.1257
5731.176 | 665.0366
5732.176 | 666.0656
5733.176 | 666.1439
5734.176 | 668.4064
5735.176 | 672.3344
5736.176 | 673.954
5737.176 | 678.5473
5738.176 | 680.0414
5739.176 | 683.5017
5740.176 | 690.5801
5741.176 | 695.2252
5742.176 | 695.7866
5743.176 | 692.9419
5744.176 | 690.5594
5745.176 | 690.6314
5746.176 | 692.004
5747.176 | 691.4277
5748.176 | 693.4645
5749.176 | 693.5244
5750.176 | 695.5699
5751.176 | 696.6091
5752.176 | 693.5728
5753.176 | 687.8515
5754.176 | 684.773
5755.176 | 682.7341
5756.176 | 678.2367
5757.176 | 675.8709
5758.176 | 672.6641
5759.176 | 669.9965
5760.176 | 668.5683
5761.176 | 665.0015
5762.176 | 664.8702
5763.176 | 668.2639
5764.176 | 673.6919
5765.176 | 675.4134
5766.176 | 676.2637
5767.176 | 681.0586
5768.176 | 689.929
5769.176 | 695.259
5770.176 | 694.6524
5771.176 | 691.6789
5772.176 | 689.6038
5773.176 | 688.7296
5774.176 | 690.6257
5775.176 | 695.5342
5776.176 | 702.5712
5777.176 | 702.8053
5778.176 | 701.8969
5779.176 | 698.5631
5780.176 | 694.389
5781.176 | 696.1001
5782.176 | 695.2696
5783.176 | 693.0655
5784.176 | 690.851
5785.176 | 690.1448
5786.176 | 690.414
5787.176 | 691.726
5788.176 | 688.2556
5789.176 | 686.1987
5790.176 | 684.8264
5791.176 | 682.0029
5792.176 | 680.2457
5793.176 | 680.1941
5794.176 | 683.7064
5795.176 | 681.5995
5796.176 | 676.5451
5797.176 | 673.142
5798.176 | 673.2732
5799.176 | 672.6291
5800.176 | 671.3123
5801.176 | 669.9155
5802.176 | 666.3088
5803.176 | 664.7704
5804.176 | 663.4052
5805.176 | 661.7199
5806.176 | 661.0633
5807.176 | 660.8133
5808.176 | 663.5796
5809.176 | 664.7636
5810.176 | 668.3643
5811.176 | 670.4115
5812.176 | 673.3221
5813.176 | 675.4205
5814.176 | 674.5436
5815.176 | 672.5883
5816.176 | 669.8413
5817.176 | 667.0167
5818.176 | 664.4821
5819.176 | 664.3647
5820.176 | 665.5723
5821.176 | 666.447
5822.176 | 665.2176
5823.176 | 662.1198
5824.176 | 659.5962
5825.176 | 655.7873
5826.176 | 651.8502
5827.176 | 649.3954
5828.176 | 647.15
5829.176 | 643.0677
5830.176 | 639.4739
5831.176 | 636.0655
5832.176 | 635.3501
5833.176 | 634.1749
5834.176 | 634.7433
5835.176 | 635.3681
5836.176 | 634.4011
5837.176 | 632.3109
5838.176 | 629.1172
5839.176 | 631.5687
5840.176 | 632.9041
5841.176 | 633.6545
5842.176 | 631.8257
5843.176 | 632.1811
5844.176 | 633.0254
5845.176 | 635.563
5846.176 | 636.6833
5847.176 | 638.5086
5848.176 | 638.5486
5849.176 | 639.8035
5850.176 | 641.958
5851.176 | 650.5859
5852.176 | 657.3074
5853.176 | 660.1081
5854.176 | 661.8498
5855.176 | 661.4701
5856.176 | 663.7214
5857.176 | 664.9451
5858.176 | 666.6862
5859.176 | 669.0692
5860.176 | 675.9345
5861.176 | 681.2804
5862.176 | 683.1993
5863.176 | 686.5561
5864.176 | 692.9847
5865.176 | 696.6978
5866.176 | 695.6906
5867.176 | 695.3086
5868.176 | 693.5301
5869.176 | 695.9214
5870.176 | 693.2245
5871.176 | 695.7402
5872.176 | 699.752
5873.176 | 701.0481
5874.176 | 705.2484
5875.176 | 709.3296
5876.176 | 715.4943
5877.176 | 718.4908
5878.176 | 716.7711
5879.176 | 724.6708
5880.176 | 727.9863
5881.176 | 732.3225
5882.176 | 727.8643
5883.176 | 719.0878
5884.176 | 725.3265
5885.176 | 727.742
5886.176 | 726.9144
5887.176 | 723.6731
5888.176 | 719.8682
5889.176 | 717.019
5890.176 | 716.8458
5891.176 | 721.5884
5892.176 | 724.8391
5893.176 | 727.6225
5894.176 | 729.7167
5895.176 | 727.3655
5896.176 | 722.847
5897.176 | 721.9546
5898.176 | 719.9596
5899.176 | 715.9276
5900.176 | 711.7308
5901.176 | 706.419
5902.176 | 700.847
5903.176 | 697.7841
5904.176 | 700.0747
5905.176 | 702.3536
5906.176 | 698.8569
5907.176 | 691.9083
5908.176 | 685.6503
5909.176 | 680.4187
5910.176 | 675.3114
5911.176 | 672.2633
5912.176 | 671.6712
5913.176 | 669.68
5914.176 | 667.9948
5915.176 | 667.2135
5916.176 | 665.1658
5917.176 | 662.8838
5918.176 | 660.0172
5919.176 | 658.9825
5920.176 | 656.7233
5921.176 | 656.5429
5922.176 | 656.6433
5923.176 | 654.2095
5924.176 | 651.0966
5925.176 | 650.2492
5926.176 | 651.7751
5927.176 | 653.9872
5928.176 | 655.84
5929.176 | 656.3316
5930.176 | 660.1162
5931.176 | 661.914
5932.176 | 665.4721
5933.176 | 669.3526
5934.176 | 673.4307
5935.176 | 678.8817
5936.176 | 684.8912
5937.176 | 686.7581
5938.176 | 692.0325
5939.176 | 702.3795
5940.176 | 712.9266
5941.176 | 715.4722
5942.176 | 714.8679
5943.176 | 720.2564
5944.176 | 720.0965
5945.176 | 719.5379
5946.176 | 720.4177
5947.176 | 716.8915
5948.176 | 722.7368
5949.176 | 727.9084
5950.176 | 726.2565
5951.176 | 720.2626
5952.176 | 714.7364
5953.176 | 712.3755
5954.176 | 710.7292
5955.176 | 705.3066
5956.176 | 701.1588
5957.176 | 699.0183
5958.176 | 705.9171
5959.176 | 710.6627
5960.176 | 718.0255
5961.176 | 718.1288
5962.176 | 712.8396
5963.176 | 720.1154
5964.176 | 728.7826
5965.176 | 726.7826
5966.176 | 723.1626
5967.176 | 720.5022
5968.176 | 717.095
5969.176 | 713.6455
5970.176 | 717.5142
5971.176 | 716.6633
5972.176 | 716.7864
5973.176 | 712.3349
5974.176 | 708.2797
5975.176 | 712.592
5976.176 | 711.7216
5977.176 | 714.226
5978.176 | 718.0368
5979.176 | 719.0731
5980.176 | 715.5967
5981.176 | 715.8702
5982.176 | 714.1438
5983.176 | 716.0139
5984.176 | 718.5647
5985.176 | 720.4641
5986.176 | 722.8267
5987.176 | 726.3841
5988.176 | 725.1723
5989.176 | 723.4991
5990.176 | 725.0451
5991.176 | 722.7833
5992.176 | 729.3093
5993.176 | 729.0687
5994.176 | 726.6884
5995.176 | 730.5872
5996.176 | 735.1898
5997.176 | 740.6547
5998.176 | 749.126
5999.176 | 748.8951
6000.1917 | 742.2006
6001.176 | 736.6583
6002.176 | 737.2868
6003.176 | 732.7838
6004.176 | 727.6522
6005.176 | 721.2995
6006.176 | 718.1177
6007.176 | 712.2218
6008.176 | 710.9297
6009.176 | 712.212
6010.176 | 713.8792
6011.176 | 713.3477
6012.176 | 716.6688
6013.176 | 720.28
6014.176 | 726.5534
6015.176 | 733.7685
6016.176 | 738.9846
6017.176 | 741.6801
6018.176 | 739.8411
6019.176 | 739.2428
6020.176 | 734.5123
6021.176 | 729.8309
6022.176 | 725.0738
6023.176 | 720.9731
6024.176 | 715.3296
6025.176 | 711.5832
6026.176 | 711.3028
6027.176 | 711.406
6028.176 | 711.8511
6029.176 | 711.5388
6030.176 | 717.3466
6031.176 | 721.6367
6032.176 | 719.338
6033.176 | 715.7092
6034.176 | 711.2956
6035.176 | 711.527
6036.176 | 712.724
6037.176 | 710.8614
6038.176 | 707.5486
6039.176 | 703.4679
6040.176 | 701.1176
6041.176 | 703.7794
6042.176 | 708.2703
6043.176 | 709.0692
6044.176 | 712.6325
6045.176 | 719.0052
6046.176 | 719.6264
6047.176 | 723.6175
6048.176 | 726.3444
6049.176 | 727.2464
6050.176 | 724.1194
6051.176 | 721.0562
6052.176 | 725.679
6053.176 | 731.1296
6054.176 | 734.7954
6055.176 | 736.5558
6056.176 | 730.8454
6057.176 | 730.4657
6058.176 | 737.9477
6059.176 | 740.9015
6060.176 | 737.0318
6061.176 | 732.8339
6062.176 | 737.6205
6063.176 | 739.392
6064.176 | 734.1828
6065.176 | 727.4637
6066.176 | 721.8469
6067.176 | 716.1723
6068.176 | 709.2818
6069.176 | 702.7235
6070.176 | 697.6846
6071.176 | 694.8673
6072.176 | 693.5572
6073.176 | 694.527
6074.176 | 693.9512
6075.176 | 702.7544
6076.176 | 710.4071
6077.176 | 713.3398
6078.176 | 710.3695
6079.176 | 707.4133
6080.176 | 712.6658
6081.176 | 711.9412
6082.176 | 714.1889
6083.176 | 710.7877
6084.176 | 706.5104
6085.176 | 700.7062
6086.176 | 702.6646
6087.176 | 707.165
6088.176 | 704.856
6089.176 | 703.778
6090.176 | 711.5789
6091.176 | 720.2311
6092.176 | 727.0737
6093.176 | 730.1053
6094.176 | 728.3136
6095.176 | 724.4832
6096.176 | 721.9139
6097.176 | 717.8919
6098.176 | 714.5865
6099.176 | 710.9356
6100.176 | 709.1675
6101.176 | 706.1449
6102.176 | 704.6069
6103.176 | 702.8958
6104.176 | 700.0325
6105.176 | 696.7165
6106.176 | 694.1517
6107.176 | 691.4585
6108.176 | 690.841
6109.176 | 689.8721
6110.176 | 692.7078
6111.176 | 691.8335
6112.176 | 689.4767
6113.176 | 689.9391
6114.176 | 695.0936
6115.176 | 694.9048
6116.176 | 696.4514
6117.176 | 696.1848
6118.176 | 692.9338
6119.176 | 693.9832
6120.176 | 695.0382
6121.176 | 690.6908
6122.176 | 688.6651
6123.176 | 693.8867
6124.176 | 696.9097
6125.176 | 700.7414
6126.176 | 701.0938
6127.176 | 700.6432
6128.176 | 703.755
6129.176 | 703.3329
6130.176 | 706.5262
6131.176 | 708.2514
6132.176 | 714.2929
6133.176 | 718.269
6134.176 | 714.14
6135.176 | 711.3221
6136.176 | 708.1015
6137.1917 | 703.2463
6138.176 | 705.9057
6139.176 | 715.7439
6140.176 | 718.9008
6141.176 | 715.4747
6142.176 | 712.7531
6143.176 | 708.0553
6144.176 | 701.4508
6145.176 | 695.9332
6146.176 | 692.6526
6147.176 | 692.0954
6148.176 | 693.1578
6149.176 | 694.5955
6150.176 | 694.64
6151.176 | 695.0141
6152.176 | 692.6671
6153.176 | 689.8553
6154.176 | 687.8422
6155.176 | 687.5383
6156.176 | 684.8471
6157.176 | 687.0065
6158.176 | 689.0132
6159.176 | 688.8052
6160.176 | 690.6397
6161.176 | 692.0059
6162.176 | 689.3501
6163.176 | 686.325
6164.176 | 683.0934
6165.176 | 683.6073
6166.176 | 682.1162
6167.176 | 683.7593
6168.176 | 685.216
6169.176 | 685.4799
6170.176 | 688.5798
6171.176 | 691.8351
6172.176 | 694.056
6173.176 | 695.0656
6174.176 | 692.88
6175.176 | 693.667
6176.176 | 695.2645
6177.176 | 693.6892
6178.176 | 690.4995
6179.176 | 689.6884
6180.176 | 687.0617
6181.176 | 682.486
6182.176 | 685.6315
6183.176 | 687.218
6184.176 | 689.4391
6185.176 | 687.5163
6186.176 | 685.574
6187.176 | 682.519
6188.176 | 678.5197
6189.176 | 676.8506
6190.176 | 678.8563
6191.176 | 685.5503
6192.176 | 691.3355
6193.176 | 698.8651
6194.176 | 700.6739
6195.176 | 696.1642
6196.176 | 692.7913
6197.176 | 691.3774
6198.176 | 692.1324
6199.176 | 693.0333
6200.176 | 692.9568
6201.176 | 690.4891
6202.176 | 692.2743
6203.176 | 694.107
6204.176 | 695.2652
6205.176 | 694.9599
6206.176 | 691.4584
6207.176 | 692.7725
6208.176 | 691.5891
6209.176 | 693.2598
6210.176 | 697.4433
6211.176 | 699.8461
6212.176 | 695.5059
6213.176 | 693.5529
6214.176 | 689.5891
6215.176 | 687.1239
6216.176 | 685.9373
6217.176 | 687.7305
6218.176 | 684.6841
6219.176 | 682.7715
6220.176 | 684.199
6221.176 | 685.5987
6222.176 | 691.3285
6223.176 | 690.0992
6224.176 | 685.7636
6225.176 | 684.8735
6226.176 | 687.9941
6227.2073 | 688.1762
6228.176 | 687.1615
6229.176 | 685.5504
6230.176 | 684.4529
6231.176 | 687.942
6232.176 | 692.7311
6233.176 | 690.3031
6234.176 | 688.278
6235.176 | 692.6562
6236.176 | 703.2933
6237.176 | 708.685
6238.176 | 703.8371
6239.176 | 699.5968
6240.176 | 698.0152
6241.176 | 698.5931
6242.176 | 699.6284
6243.176 | 696.1882
6244.176 | 691.4749
6245.176 | 687.0854
6246.176 | 684.6674
6247.176 | 688.2116
6248.176 | 693.4029
6249.176 | 698.5692
6250.176 | 697.0638
6251.176 | 691.5535
6252.176 | 686.9505
6253.176 | 683.4024
6254.176 | 678.3523
6255.176 | 677.9648
6256.176 | 682.9288
6257.176 | 682.1413
6258.176 | 685.3079
6259.176 | 685.7863
6260.176 | 686.5286
6261.176 | 686.4493
6262.176 | 683.0546
6263.176 | 684.8127
6264.176 | 686.7618
6265.176 | 692.0204
6266.176 | 694.4943
6267.176 | 695.1596
6268.176 | 690.9633
6269.176 | 686.5468
6270.176 | 681.5472
6271.176 | 679.8328
6272.176 | 682.1352
6273.176 | 681.5462
6274.176 | 680.8095
6275.176 | 678.7387
6276.176 | 678.8207
6277.176 | 677.6231
6278.176 | 675.3812
6279.176 | 680.5356
6280.176 | 691.5334
6281.176 | 700.6395
6282.176 | 705.1269
6283.176 | 705.1083
6284.176 | 705.1822
6285.176 | 704.6726
6286.176 | 703.3533
6287.176 | 705.6513
6288.176 | 702.8115
6289.176 | 698.5366
6290.176 | 695.352
6291.176 | 695.4359
6292.176 | 692.4124
6293.176 | 690.0874
6294.176 | 685.6471
6295.176 | 683.6211
6296.1917 | 682.5885
6297.176 | 677.9486
6298.176 | 675.7517
6299.176 | 676.0641
6300.176 | 679.5624
6301.176 | 681.7779
6302.176 | 683.9142
6303.176 | 689.6246
6304.176 | 699.0525
6305.176 | 706.6419
6306.176 | 706.2096
6307.176 | 702.6009
6308.176 | 703.2027
6309.176 | 700.377
6310.176 | 696.219
6311.176 | 691.1266
6312.176 | 685.4511
6313.176 | 681.2012
6314.176 | 678.4438
6315.176 | 688.0749
6316.176 | 693.6094
6317.176 | 692.5549
6318.176 | 694.8726
6319.176 | 695.3801
6320.176 | 691.3727
6321.176 | 687.3945
6322.176 | 683.2855
6323.176 | 681.3871
6324.176 | 682.5762
6325.176 | 682.6132
6326.1917 | 682.2675
6327.176 | 680.3178
6328.176 | 678.6695
6329.176 | 685.804
6330.176 | 690.2843
6331.176 | 697.0515
6332.176 | 701.4956
6333.176 | 708.9781
6334.176 | 714.3959
6335.176 | 714.3349
6336.176 | 719.2517
6337.176 | 719.0703
6338.176 | 714.1721
6339.176 | 707.7638
6340.176 | 702.0464
6341.176 | 694.6245
6342.176 | 686.9273
6343.176 | 682.6837
6344.176 | 681.0745
6345.176 | 679.1571
6346.176 | 676.139
6347.176 | 675.4545
6348.176 | 674.3936
6349.176 | 673.7159
6350.176 | 672.2401
6351.176 | 671.4288
6352.176 | 668.692
6353.176 | 666.7843
6354.176 | 664.0537
6355.176 | 660.8946
6356.176 | 660.7776
6357.176 | 667.0363
6358.176 | 668.0648
6359.176 | 668.7483
6360.176 | 672.5218
6361.176 | 677.6452
6362.176 | 675.8823
6363.176 | 673.8767
6364.176 | 670.8619
6365.176 | 666.665
6366.176 | 666.1622
6367.176 | 668.5535
6368.176 | 668.6412
6369.176 | 667.6705
6370.176 | 667.0973
6371.176 | 669.8062
6372.176 | 672.5901
6373.176 | 670.1182
6374.176 | 669.111
6375.176 | 675.5599
6376.176 | 680.7343
6377.176 | 682.0715
6378.176 | 683.1254
6379.176 | 682.1248
6380.176 | 682.6616
6381.176 | 693.7112
6382.176 | 702.2912
6383.176 | 700.9166
6384.176 | 701.0762
6385.176 | 704.6999
6386.176 | 701.7746
6387.176 | 708.8965
6388.176 | 711.7938
6389.176 | 712.5864
6390.176 | 708.342
6391.176 | 702.525
6392.176 | 698.4852
6393.176 | 695.0354
6394.176 | 690.3048
6395.176 | 686.1426
6396.176 | 684.1529
6397.176 | 681.73
6398.176 | 679.5617
6399.176 | 678.8974
6400.176 | 678.9584
6401.176 | 677.6913
6402.176 | 675.5253
6403.176 | 673.3631
6404.176 | 673.4924
6405.176 | 673.6048
6406.176 | 671.7549
6407.176 | 672.1974
6408.176 | 683.2895
6409.176 | 693.7372
6410.176 | 701.3821
6411.176 | 713.3321
6412.176 | 720.3386
6413.176 | 724.7287
6414.176 | 723.0299
6415.176 | 717.1594
6416.176 | 714.4763
6417.176 | 711.2389
6418.176 | 708.4831
6419.176 | 705.3609
6420.176 | 703.1019
6421.176 | 702.4753
6422.176 | 698.9917
6423.176 | 696.0265
6424.176 | 693.3743
6425.176 | 691.9283
6426.176 | 690.0019
6427.176 | 690.1621
6428.176 | 687.7213
6429.176 | 686.2226
6430.176 | 691.4316
6431.176 | 690.3671
6432.176 | 687.1355
6433.176 | 687.4815
6434.176 | 688.4912
6435.176 | 693.8778
6436.176 | 695.9294
6437.176 | 695.4717
6438.176 | 696.7212
6439.176 | 698.2884
6440.176 | 694.4405
6441.176 | 690.6793
6442.176 | 689.3589
6443.176 | 687.7925
6444.176 | 696.1125
6445.176 | 694.6739
6446.176 | 691.9997
6447.176 | 691.4735
6448.176 | 689.3212
6449.176 | 689.2611
6450.176 | 693.3429
6451.176 | 693.3315
6452.176 | 691.4416
6453.176 | 691.2634
6454.176 | 698.1332
6455.176 | 696.4032
6456.176 | 693.1589
6457.176 | 690.8696
6458.176 | 691.7168
6459.176 | 700.9675
6460.176 | 701.6565
6461.176 | 698.6555
6462.176 | 692.7602
6463.176 | 689.1545
6464.176 | 689.6783
6465.176 | 691.0693
6466.176 | 687.1412
6467.176 | 688.0568
6468.176 | 687.932
6469.176 | 685.0128
6470.176 | 681.3772
6471.176 | 678.7541
6472.176 | 676.2322
6473.176 | 672.7808
6474.176 | 669.1991
6475.176 | 666.4371
6476.1917 | 666.597
6477.176 | 662.6368
6478.176 | 659.9629
6479.176 | 662.4631
6480.176 | 662.0486
6481.176 | 664.6486
6482.176 | 666.531
6483.176 | 667.0185
6484.176 | 670.0158
6485.176 | 670.4789
6486.176 | 669.9752
6487.176 | 667.9256
6488.176 | 666.2406
6489.176 | 665.1439
6490.176 | 665.8813
6491.176 | 668.5756
6492.176 | 666.8965
6493.176 | 666.0543
6494.176 | 667.219
6495.176 | 669.561
6496.176 | 667.812
6497.176 | 666.3833
6498.176 | 665.2345
6499.176 | 664.1912
6500.176 | 664.5079
6501.176 | 666.7232
6502.176 | 669.3816
6503.176 | 670.8664
6504.176 | 671.5979
6505.176 | 671.4859
6506.176 | 670.6335
6507.176 | 669.876
6508.176 | 673.8874
6509.176 | 674.5208
6510.176 | 674.8414
6511.176 | 674.2083
6512.176 | 672.0249
6513.176 | 671.6168
6514.176 | 668.9267
6515.176 | 666.0094
6516.176 | 664.8151
6517.176 | 662.9126
6518.176 | 660.6528
6519.176 | 662.9107
6520.176 | 661.1748
6521.176 | 661.3687
6522.176 | 660.8436
6523.176 | 659.5543
6524.176 | 659.4682
6525.176 | 659.7735
6526.176 | 660.2631
6527.176 | 658.7203
6528.176 | 658.1257
6529.176 | 656.1623
6530.176 | 654.1042
6531.176 | 653.1599
6532.176 | 650.0102
6533.176 | 649.9423
6534.176 | 650.0986
6535.176 | 650.9124
6536.176 | 651.1095
6537.176 | 649.2631
6538.176 | 649.8351
6539.176 | 648.749
6540.176 | 647.517
6541.176 | 648.0603
6542.176 | 649.138
6543.176 | 650.3577
6544.176 | 649.1824
6545.176 | 650.9646
6546.176 | 652.5212
6547.176 | 652.4531
6548.176 | 651.0947
6549.176 | 649.6315
6550.176 | 649.0056
6551.176 | 649.3884
6552.176 | 649.285
6553.176 | 648.5144
6554.176 | 648.0253
6555.176 | 645.4429
6556.176 | 644.3165
6557.176 | 645.9642
6558.176 | 654.879
6559.176 | 658.545
6560.176 | 661.0838
6561.176 | 660.9183
6562.176 | 659.5287
6563.176 | 658.8253
6564.176 | 657.0979
6565.176 | 654.0881
6566.176 | 651.9647
6567.176 | 651.3427
6568.176 | 652.2648
6569.176 | 653.9685
6570.176 | 651.9543
6571.176 | 649.8313
6572.176 | 653.4988
6573.176 | 658.207
6574.176 | 658.4624
6575.176 | 657.686
6576.176 | 657.4161
6577.176 | 655.9255
6578.176 | 654.8531
6579.176 | 654.9256
6580.176 | 655.4337
6581.176 | 655.8257
6582.176 | 654.6012
6583.176 | 652.9244
6584.176 | 652.8861
6585.176 | 654.5435
6586.176 | 652.8767
6587.176 | 654.8079
6588.176 | 663.5694
6589.176 | 669.7435
6590.176 | 671.1278
6591.176 | 669.2462
6592.176 | 664.9037
6593.176 | 662.031
6594.176 | 661.4028
6595.176 | 658.0396
6596.176 | 656.299
6597.176 | 659.8578
6598.176 | 659.1343
6599.176 | 655.9542
6600.176 | 653.5548
6601.176 | 651.1602
6602.176 | 648.1758
6603.176 | 647.5756
6604.176 | 647.1636
6605.176 | 643.5351
6606.176 | 639.1223
6607.176 | 637.0419
6608.176 | 636.4614
6609.176 | 638.2901
6610.176 | 650.0032
6611.176 | 650.9141
6612.176 | 649.6612
6613.176 | 647.3562
6614.176 | 646.409
6615.176 | 645.2987
6616.176 | 643.9555
6617.176 | 642.6386
6618.176 | 642.9713
6619.176 | 649.3381
6620.176 | 651.9056
6621.176 | 651.5759
6622.176 | 654.2554
6623.176 | 658.3377
6624.176 | 659.9972
6625.176 | 662.759
6626.176 | 670.7515
6627.176 | 682.1402
6628.176 | 691.5038
6629.176 | 695.2776
6630.176 | 693.2155
6631.176 | 691.3893
6632.176 | 692.2065
6633.176 | 695.1867
6634.176 | 689.7914
6635.176 | 684.6234
6636.176 | 682.8704
6637.176 | 685.921
6638.176 | 685.0773
6639.176 | 681.79
6640.176 | 676.9277
6641.176 | 671.9903
6642.176 | 667.8117
6643.176 | 663.0035
6644.176 | 659.5362
6645.176 | 657.661
6646.176 | 659.0938
6647.176 | 665.5757
6648.176 | 677.0674
6649.176 | 675.6384
6650.176 | 672.491
6651.176 | 670.3721
6652.176 | 667.4613
6653.176 | 665.6626
6654.176 | 663.9218
6655.176 | 668.1293
6656.176 | 666.3826
6657.176 | 664.3366
6658.176 | 663.205
6659.176 | 661.5491
6660.176 | 661.9895
6661.176 | 664.0776
6662.176 | 669.4755
6663.176 | 668.2944
6664.176 | 665.2894
6665.176 | 664.6579
6666.176 | 664.7811
6667.176 | 663.9742
6668.176 | 664.4305
6669.176 | 670.2589
6670.176 | 681.331
6671.176 | 687.9841
6672.176 | 688.0089
6673.176 | 687.421
6674.176 | 686.0022
6675.176 | 687.2973
6676.176 | 684.9458
6677.176 | 681.9164
6678.176 | 680.0204
6679.176 | 684.8863
6680.176 | 685.6541
6681.176 | 683.6915
6682.176 | 680.8696
6683.176 | 678.8815
6684.176 | 676.5118
6685.176 | 675.7023
6686.176 | 675.0941
6687.176 | 680.2764
6688.176 | 679.566
6689.176 | 678.9788
6690.176 | 676.2853
6691.176 | 678.0173
6692.176 | 683.0496
6693.176 | 680.9173
6694.176 | 677.3633
6695.176 | 676.0931
6696.176 | 679.9891
6697.176 | 684.2286
6698.176 | 680.8756
6699.176 | 677.1564
6700.176 | 676.7398
6701.176 | 676.2318
6702.176 | 674.0709
6703.176 | 672.5105
6704.176 | 670.4134
6705.176 | 671.6717
6706.176 | 671.4857
6707.176 | 673.8053
6708.176 | 672.2456
6709.176 | 669.3607
6710.176 | 666.5498
6711.176 | 664.3721
6712.176 | 668.9616
6713.176 | 675.2214
6714.176 | 682.3945
6715.176 | 681.5696
6716.1917 | 679.4858
6717.176 | 677.38
6718.176 | 674.834
6719.176 | 671.2735
6720.176 | 667.5494