## Test Conditions
DESIREE-FIRE Test Number 4 - Circuit Simulator Data Only
Test Date: | 2009-11-12
DCSim DAQ Start Time | 10:31
DCSim Time for Synchronization | 10:32
Heat Source Synchronization | 0:55 | minutes:seconds
Heat Source DAQ Start Time | 10:31
Fire Time | 11:20
Offset | 0:49 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2940 | seconds
Heat Source Offset | 0:49 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2935 | seconds
Heat Source Stop Time | 13:12
Test Duration | 1:52 | minutes:seconds
| 6720 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
MOV 2 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the air temperature 3', 5', and 7' down the cable tray located in C-Position. These are labeled as "C-Position - 3'", "C-Position - Middle", " C-Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.90625 | 121.8338 | -61.2488 | 60.3333 | -0.051651 | 0.0046078 | 0.065183 | 0.060534 | 0.00086307 | -0.0075388 | -2.3544e-05 | -0.052765 | 0.0042425 | 0.067054 | 0.056241 | -0.010679 | 0.025272 | -0.0038709 | -0.045776 | 60.2051 | -61.2213 | 60.3928 | -61.0519 | -61.4548 | -61.441 | 0 | 60.1913 | -61.2808 | 60.3241 | -61.235 | -61.3861 | -61.3907 | 0.027466 | -0.12817 | 0.059509 | 0.19684 | -0.19226 | -0.20599 | -0.21973 | -0.23346 | -0.032044 | -0.14191 | -0.009155 | 0.013733 | -0.14191 | -0.13733 | -0.10986 | -0.10529 | 0.16937 | 121.6141 | 0.045777 | 121.6049 | 121.4264 | 121.4722 | 121.4539 | 121.4401 | -121.5546 | -121.6141 | 121.6415 | 121.5729 | 61.203 | 61.2488
0.78125 | 121.9116 | -61.1664 | 60.3561 | -0.074539 | 0.003967 | 0.065396 | 0.059039 | 0.00043587 | -0.0094614 | -0.00045074 | 0.011322 | 0.0027471 | 0.065772 | 0.048977 | -0.0098246 | 0.022708 | -0.0023755 | -0.050354 | 60.1501 | -61.2076 | 60.4477 | -60.9833 | -61.3953 | -61.3724 | 0.064087 | 60.141 | -61.2396 | 60.4248 | -61.116 | -61.2213 | -61.2717 | -0.041199 | -0.20599 | 0.091553 | 0.18311 | -0.20599 | -0.22888 | -0.16479 | -0.18768 | -0.073242 | -0.21515 | 0.068665 | 0.050354 | -0.10529 | -0.054931 | -0.032043 | 0.018311 | 0.22431 | 121.6553 | 0.1236 | 121.6644 | 121.3577 | 121.3806 | 121.3165 | 121.3074 | -121.5637 | -121.5958 | 121.6141 | 121.5912 | 61.116 | 61.2305
2.5312 | 121.9208 | -61.2762 | 60.2692 | -0.16609 | 0.0069578 | 0.067533 | 0.059893 | 0.00064947 | -0.0081796 | -0.0021597 | -0.049713 | 0.0038153 | 0.067268 | 0.057736 | -0.011106 | 0.024204 | -0.0038709 | -0.15106 | 60.0723 | -61.29 | 60.4477 | -61.0153 | -61.4594 | -61.409 | -0.009155 | 60.0906 | -61.3037 | 60.379 | -61.1893 | -61.3129 | -61.3312 | -0.013733 | -0.19684 | 0.17853 | 0.26093 | -0.13275 | -0.18311 | -0.11902 | -0.16937 | -0.027466 | -0.17853 | 0.10986 | 0.086975 | -0.054932 | -0.036621 | -0.027466 | -0.009155 | 0.27466 | 121.7377 | 0.11444 | 121.6827 | 121.3623 | 121.3943 | 121.3486 | 121.3669 | -121.5591 | -121.5729 | 121.7239 | 121.6553 | 61.1252 | 61.2671
4.2188 | 121.9208 | -61.171 | 60.3882 | -0.11269 | 0.0048214 | 0.06561 | 0.057971 | -0.0023413 | -0.0077524 | -0.0015189 | 0.020477 | 0.0029607 | 0.066841 | 0.054318 | -0.012174 | 0.024204 | -0.0045117 | -0.045776 | 60.141 | -61.2076 | 60.4706 | -60.9741 | -61.3861 | -61.3586 | 0.086975 | 60.1501 | -61.2259 | 60.4431 | -61.1114 | -61.2213 | -61.2534 | -0.036622 | -0.24719 | 0.082397 | 0.19684 | -0.18768 | -0.21515 | -0.15106 | -0.17853 | -0.054932 | -0.23804 | 0.054931 | 0.059509 | -0.082398 | -0.050354 | -0.027466 | 0.004578 | 0.23346 | 121.6782 | 0.11444 | 121.669 | 121.3486 | 121.376 | 121.3119 | 121.3211 | -121.5958 | -121.6141 | 121.6415 | 121.6141 | 61.1252 | 61.2579
5.9688 | 121.7697 | -61.3037 | 60.3195 | -0.082169 | 0.0078122 | 0.067319 | 0.064166 | -0.0053321 | -0.007966 | -0.0032277 | -0.11075 | 0.0055243 | 0.065345 | 0.066922 | -0.012174 | 0.025272 | -0.0047253 | -0.16479 | 60.1135 | -61.2946 | 60.3241 | -61.1526 | -61.5738 | -61.5509 | -0.15106 | 60.1044 | -61.3083 | 60.2417 | -61.3358 | -61.4685 | -61.4548 | 0.009155 | -0.20599 | 0.004578 | 0.15106 | -0.24719 | -0.27008 | -0.25635 | -0.27924 | -0.004578 | -0.21515 | -0.07782 | -0.032043 | -0.15106 | -0.16479 | -0.14648 | -0.16022 | 0.14191 | 121.6187 | -0.027465 | 121.55 | 121.4081 | 121.4127 | 121.4172 | 121.4081 | -121.6141 | -121.6278 | 121.6278 | 121.5454 | 61.1389 | 61.1526
7.7188 | 121.8796 | -61.2167 | 60.3149 | -0.097427 | 0.0054624 | 0.065183 | 0.060748 | 0.00022207 | -0.006898 | -0.0042959 | 0.0021667 | 0.0016791 | 0.065345 | 0.050046 | -0.011533 | 0.025699 | -0.0047253 | -0.11444 | 60.1273 | -61.2167 | 60.4248 | -61.0016 | -61.4319 | -61.3907 | 0.004578 | 60.141 | -61.2442 | 60.3699 | -61.1847 | -61.29 | -61.3266 | 0 | -0.18768 | 0.10986 | 0.21515 | -0.17395 | -0.21515 | -0.17395 | -0.21515 | -0.027466 | -0.17395 | 0.054932 | 0.032044 | -0.10986 | -0.073242 | -0.082397 | -0.045776 | 0.21515 | 121.6415 | 0.05951 | 121.6141 | 121.344 | 121.3852 | 121.344 | 121.3577 | -121.5317 | -121.5591 | 121.6415 | 121.5866 | 61.1023 | 61.2213
9.3906 | 121.9299 | -61.1526 | 60.3745 | -0.11269 | 0.0048214 | 0.063687 | 0.060748 | 0.0010767 | -0.010316 | -0.0015189 | 0.0052185 | 0.0016791 | 0.064704 | 0.052823 | -0.012388 | 0.022281 | -0.0034435 | 0.045776 | 60.1593 | -61.171 | 60.5438 | -60.8734 | -61.3037 | -61.2762 | 0.2243 | 60.173 | -61.203 | 60.4706 | -61.0611 | -61.171 | -61.2305 | -0.01831 | -0.21515 | 0.16937 | 0.27924 | -0.1236 | -0.15106 | -0.10529 | -0.13275 | -0.050354 | -0.20142 | 0.09613 | 0.091553 | -0.07782 | -0.01831 | -0.027466 | 0.032044 | 0.29755 | 121.7148 | 0.14191 | 121.6736 | 121.3303 | 121.376 | 121.312 | 121.3257 | -121.5454 | -121.5775 | 121.6965 | 121.6232 | 61.1984 | 61.377
11.1406 | 121.8979 | -61.2808 | 60.2463 | -0.1432 | 0.007385 | 0.067746 | 0.061816 | 0.00043587 | -0.006257 | -0.00087794 | -0.064972 | 0.0053107 | 0.062141 | 0.054104 | -0.011747 | 0.024417 | -0.0055799 | -0.15106 | 60.0906 | -61.2717 | 60.434 | -61.0245 | -61.4685 | -61.4227 | -0.041199 | 60.0815 | -61.3129 | 60.3653 | -61.2122 | -61.3312 | -61.3312 | 0.009156 | -0.15564 | 0.18768 | 0.25635 | -0.14191 | -0.18768 | -0.15106 | -0.19684 | -0.032043 | -0.16479 | 0.11902 | 0.068665 | -0.050354 | -0.050354 | -0.018311 | -0.018311 | 0.24719 | 121.7056 | 0.10071 | 121.6782 | 121.3623 | 121.3943 | 121.3715 | 121.3623 | -121.5179 | -121.5591 | 121.7148 | 121.6461 | 61.1298 | 61.2396
12.8281 | 121.8842 | -61.235 | 60.3378 | -0.13557 | 0.007385 | 0.066892 | 0.061816 | -0.0038367 | -0.006257 | -0.0047231 | -0.040558 | 0.0033881 | 0.067695 | 0.054532 | -0.012174 | 0.023135 | -0.0051525 | -0.11902 | 60.1318 | -61.235 | 60.4385 | -60.9924 | -61.4365 | -61.3815 | 0.027466 | 60.1135 | -61.2442 | 60.3745 | -61.1893 | -61.3083 | -61.3266 | 0 | -0.20599 | 0.10071 | 0.24261 | -0.14649 | -0.20142 | -0.14649 | -0.20142 | -0.009156 | -0.2243 | 0.036621 | 0.045776 | -0.091553 | -0.073243 | -0.082397 | -0.064087 | 0.24261 | 121.6736 | 0.054932 | 121.6187 | 121.3669 | 121.3577 | 121.3669 | 121.3486 | -121.5729 | -121.582 | 121.6736 | 121.6095 | 61.116 | 61.2625
14.5625 | 121.8658 | -61.2076 | 60.347 | -0.12794 | 0.0052488 | 0.063901 | 0.060321 | -0.0070409 | -0.0083932 | -0.00087794 | -0.034454 | 0.0021063 | 0.062568 | 0.062222 | -0.0096108 | 0.022922 | -0.0030163 | -0.10071 | 60.1227 | -61.2213 | 60.4523 | -61.0016 | -61.4182 | -61.3861 | 0.013733 | 60.1318 | -61.2534 | 60.3699 | -61.2122 | -61.3129 | -61.3174 | -0.013732 | -0.2243 | 0.10529 | 0.20599 | -0.17853 | -0.21057 | -0.16479 | -0.19684 | -0.045776 | -0.21515 | 0.022888 | -0.004577 | -0.10986 | -0.10529 | -0.064087 | -0.059509 | 0.21973 | 121.6736 | 0.041199 | 121.6232 | 121.344 | 121.3852 | 121.3303 | 121.3394 | -121.5683 | -121.6003 | 121.6599 | 121.5775 | 61.1069 | 61.2213
16.2969 | 121.8246 | -61.29 | 60.3012 | -0.12794 | 0.0067442 | 0.064756 | 0.063311 | -0.0017005 | -0.006898 | -0.00066434 | -0.09549 | 0.0036017 | 0.066627 | 0.054318 | -0.012388 | 0.022708 | -0.0038709 | -0.22888 | 60.1227 | -61.3129 | 60.3195 | -61.1389 | -61.5692 | -61.528 | -0.14648 | 60.1273 | -61.3312 | 60.2692 | -61.3129 | -61.4639 | -61.441 | -0.022888 | -0.17853 | 0.018311 | 0.15106 | -0.23804 | -0.27924 | -0.21515 | -0.25635 | -0.041199 | -0.17395 | -0.032043 | -0.022888 | -0.15106 | -0.17395 | -0.10986 | -0.13275 | 0.17395 | 121.6324 | 0.018311 | 121.6003 | 121.4355 | 121.4584 | 121.4127 | 121.4172 | -121.6141 | -121.6324 | 121.6095 | 121.5591 | 61.0611 | 61.1435
18.0625 | 121.8979 | -61.2167 | 60.3424 | -0.12032 | 0.0043942 | 0.065396 | 0.061175 | -0.0014867 | -0.010316 | -0.0010915 | 0.0021667 | 0.0057379 | 0.066413 | 0.049191 | -0.012174 | 0.022495 | -0.0025891 | -0.068665 | 60.1501 | -61.235 | 60.4431 | -60.9833 | -61.4319 | -61.3815 | 0.022888 | 60.1776 | -61.235 | 60.379 | -61.1618 | -61.2762 | -61.3129 | -0.01831 | -0.19226 | 0.10071 | 0.23346 | -0.1648 | -0.21515 | -0.14649 | -0.19684 | -0.01831 | -0.16479 | 0.036621 | 0.054932 | -0.09613 | -0.059509 | -0.07782 | -0.041199 | 0.25177 | 121.6782 | 0.073242 | 121.6141 | 121.3852 | 121.4127 | 121.3669 | 121.3943 | -121.5775 | -121.5775 | 121.6599 | 121.5958 | 61.1481 | 61.2396
19.7344 | 121.8384 | -61.2717 | 60.3058 | -0.074539 | 0.0065304 | 0.064542 | 0.065234 | -0.0038367 | -0.0056162 | -0.0040823 | -0.11685 | 0.0061651 | 0.065345 | 0.053036 | -0.013029 | 0.025912 | -0.0038709 | -0.064087 | 60.141 | -61.2625 | 60.4111 | -61.0382 | -61.4822 | -61.4456 | 0.022888 | 60.1547 | -61.2808 | 60.347 | -61.2213 | -61.3724 | -61.3815 | 0.009155 | -0.16479 | 0.10529 | 0.23346 | -0.17395 | -0.21057 | -0.18311 | -0.21973 | -0.009156 | -0.15106 | 0.041199 | 0.050354 | -0.10986 | -0.10071 | -0.10071 | -0.091552 | 0.2243 | 121.6736 | 0.05951 | 121.6278 | 121.4035 | 121.4355 | 121.4127 | 121.4264 | -121.5683 | -121.5866 | 121.6827 | 121.6187 | 61.2076 | 61.2946
21.4688 | 121.8842 | -61.203 | 60.3699 | -0.10506 | 0.0050352 | 0.067533 | 0.060534 | -0.0027685 | -0.0098886 | -0.0030141 | 0.0021667 | 0.0010381 | 0.064491 | 0.058377 | -0.012602 | 0.023776 | -0.0034435 | -0.059509 | 60.1547 | -61.2122 | 60.4477 | -60.9924 | -61.4227 | -61.3907 | 0.036621 | 60.1501 | -61.2442 | 60.3973 | -61.1572 | -61.2396 | -61.2854 | -0.009155 | -0.21515 | 0.07782 | 0.21057 | -0.18768 | -0.21973 | -0.17853 | -0.21057 | -0.041199 | -0.21973 | 0.027466 | 0.045776 | -0.082397 | -0.036621 | -0.041198 | 0.004578 | 0.21973 | 121.6599 | 0.086975 | 121.6415 | 121.3669 | 121.3943 | 121.3577 | 121.3531 | -121.582 | -121.6141 | 121.6507 | 121.6003 | 61.1435 | 61.2396
23.2344 | 121.7926 | -61.3266 | 60.3195 | -0.10506 | 0.0082394 | 0.066251 | 0.066729 | -0.0012731 | -0.0041208 | -0.0017325 | -0.12601 | 0.0044561 | 0.066627 | 0.062649 | -0.010893 | 0.024204 | -0.0070751 | -0.22888 | 60.1135 | -61.3129 | 60.3104 | -61.1755 | -61.6241 | -61.5646 | -0.18768 | 60.1181 | -61.3403 | 60.2371 | -61.3449 | -61.4639 | -61.4685 | 0.013733 | -0.20599 | -0.009155 | 0.15106 | -0.23804 | -0.29755 | -0.25177 | -0.31128 | -0.013733 | -0.20142 | -0.082397 | -0.018311 | -0.14191 | -0.13733 | -0.12817 | -0.1236 | 0.13733 | 121.6232 | -0.004578 | 121.5775 | 121.4264 | 121.4584 | 121.4401 | 121.4447 | -121.6324 | -121.6599 | 121.637 | 121.5637 | 61.0977 | 61.1389
24.9688 | 121.7926 | -61.3266 | 60.3012 | -0.074539 | 0.007385 | 0.066464 | 0.06502 | -0.00020513 | -0.0075388 | -0.00066434 | -0.086334 | 0.0057379 | 0.067695 | 0.053464 | -0.010038 | 0.022922 | 0.0023243 | -0.21515 | 60.1227 | -61.322 | 60.3012 | -61.1801 | -61.5967 | -61.5555 | -0.1831 | 60.1273 | -61.3541 | 60.2463 | -61.3632 | -61.4914 | -61.4548 | 0.004578 | -0.17853 | 0 | 0.14648 | -0.22888 | -0.27008 | -0.23346 | -0.27466 | -0.027466 | -0.17395 | -0.054931 | -0.036621 | -0.12817 | -0.16479 | -0.10071 | -0.13733 | 0.14191 | 121.6232 | -0.009155 | 121.6003 | 121.4447 | 121.4813 | 121.4493 | 121.4539 | -121.6232 | -121.6553 | 121.6278 | 121.5729 | 61.1115 | 61.1435
26.7031 | 121.7834 | -61.3129 | 60.3149 | -0.082169 | 0.0071714 | 0.067105 | 0.062671 | 0.0015039 | -0.0066844 | -0.0019461 | -0.10159 | 0.0044561 | 0.065345 | 0.055386 | -0.0098246 | 0.026126 | -0.0025891 | -0.11444 | 60.141 | -61.2717 | 60.3973 | -61.0428 | -61.5005 | -61.4914 | -0.045776 | 60.1547 | -61.3312 | 60.2829 | -61.2991 | -61.4319 | -61.4365 | 0.041199 | -0.17395 | 0.082398 | 0.27008 | -0.17853 | -0.18768 | -0.21973 | -0.22888 | -0.018311 | -0.16022 | -0.032043 | 0.013733 | -0.1236 | -0.11902 | -0.10529 | -0.10071 | 0.22888 | 121.669 | 0.032044 | 121.6141 | 121.4127 | 121.4859 | 121.4539 | 121.4676 | -121.5866 | -121.6461 | 121.7102 | 121.5958 | 61.1984 | 61.2671
28.4531 | 121.907 | -61.2717 | 60.2829 | -0.089798 | 0.005676 | 0.068387 | 0.063952 | 0.0015039 | -0.0058298 | -0.00066434 | -0.04361 | 0.0044561 | 0.065986 | 0.052182 | -0.010465 | 0.024204 | -0.0060071 | -0.12817 | 60.1135 | -61.2717 | 60.434 | -60.9924 | -61.4639 | -61.4182 | -0.022888 | 60.0586 | -61.3174 | 60.3699 | -61.1984 | -61.3358 | -61.322 | 0 | -0.16937 | 0.15106 | 0.27923 | -0.14648 | -0.19226 | -0.14648 | -0.19226 | -0.045777 | -0.2243 | 0.086975 | 0.073242 | -0.050354 | -0.064087 | -0.004577 | -0.01831 | 0.27923 | 121.7056 | 0.11902 | 121.6873 | 121.3852 | 121.376 | 121.3852 | 121.3303 | -121.5546 | -121.6003 | 121.7056 | 121.6415 | 61.1435 | 61.2488
30.2031 | 121.8887 | -61.2396 | 60.347 | -0.11269 | 0.0043942 | 0.064542 | 0.061175 | -0.0040503 | -0.0064706 | -0.0023733 | 0.0052185 | 0.0021063 | 0.064491 | 0.05795 | -0.011533 | 0.021426 | -0.0028027 | -0.064087 | 60.1639 | -61.2122 | 60.4385 | -60.9879 | -61.4273 | -61.3907 | 0.036621 | 60.1181 | -61.2671 | 60.3882 | -61.171 | -61.2762 | -61.3174 | 0.027466 | -0.18311 | 0.091553 | 0.25177 | -0.15106 | -0.18768 | -0.17853 | -0.21515 | -0.027466 | -0.22888 | 0.041199 | 0.068665 | -0.07782 | -0.036621 | -0.050354 | -0.009155 | 0.2243 | 121.6507 | 0.096131 | 121.6553 | 121.376 | 121.3852 | 121.4035 | 121.3577 | -121.5591 | -121.6141 | 121.6782 | 121.6278 | 61.1755 | 61.2762
31.8906 | 121.8521 | -61.2579 | 60.3378 | -0.051651 | 0.0061032 | 0.067319 | 0.062671 | -0.0017005 | -0.01053 | -0.0042959 | -0.074127 | 0.0050971 | 0.065772 | 0.057095 | -0.011747 | 0.024204 | -0.0023755 | -0.064087 | 60.1501 | -61.2534 | 60.4248 | -61.0336 | -61.4777 | -61.4456 | 0.027466 | 60.141 | -61.29 | 60.3287 | -61.2305 | -61.3678 | -61.3815 | 0.004578 | -0.18768 | 0.086975 | 0.22431 | -0.18768 | -0.21973 | -0.19226 | -0.2243 | -0.032043 | -0.19684 | -0.009156 | 0.027466 | -0.1236 | -0.10986 | -0.091553 | -0.07782 | 0.21973 | 121.6782 | 0.059509 | 121.6187 | 121.4035 | 121.431 | 121.4081 | 121.3989 | -121.5912 | -121.6278 | 121.6827 | 121.5866 | 61.1938 | 61.2854
33.6406 | 121.8979 | -61.2625 | 60.2921 | -0.12794 | 0.0043942 | 0.066464 | 0.061816 | 0.0012903 | -0.0049754 | -0.0023733 | -0.016144 | 0.0031745 | 0.067268 | 0.057095 | -0.012602 | 0.02399 | -0.0036573 | -0.12817 | 60.0769 | -61.2396 | 60.4523 | -60.9787 | -61.4502 | -61.3998 | 0.022888 | 60.0769 | -61.322 | 60.3836 | -61.1847 | -61.3083 | -61.3129 | 0.022888 | -0.21515 | 0.16022 | 0.28381 | -0.13733 | -0.18768 | -0.16022 | -0.21057 | -0.059509 | -0.21515 | 0.091553 | 0.07782 | -0.050354 | -0.045777 | 0.009155 | 0.013732 | 0.26093 | 121.6919 | 0.13733 | 121.7056 | 121.3165 | 121.3989 | 121.3394 | 121.3394 | -121.5317 | -121.6141 | 121.7148 | 121.6461 | 61.1343 | 61.2854
35.3281 | 121.907 | -61.1984 | 60.3607 | -0.11269 | 0.0031126 | 0.064542 | 0.060962 | 8.47e-06 | -0.0083932 | -0.0038687 | 0.017425 | 0.0055243 | 0.067054 | 0.056668 | -0.011106 | 0.024844 | -0.0036573 | -0.045776 | 60.1456 | -61.2167 | 60.4477 | -60.9833 | -61.409 | -61.3907 | 0.045776 | 60.1364 | -61.2534 | 60.4202 | -61.1389 | -61.235 | -61.29 | -0.018311 | -0.21515 | 0.086975 | 0.21515 | -0.19226 | -0.21057 | -0.17395 | -0.19226 | -0.054932 | -0.2243 | 0.059509 | 0.059509 | -0.091553 | -0.036621 | -0.036621 | 0.018311 | 0.23346 | 121.6644 | 0.11444 | 121.6736 | 121.3623 | 121.3898 | 121.344 | 121.3348 | -121.5775 | -121.6141 | 121.6461 | 121.6187 | 61.1526 | 61.2442
37.0625 | 121.8887 | -61.203 | 60.3516 | -0.15083 | 0.007385 | 0.065183 | 0.061389 | -0.0019141 | -0.0083932 | -0.0047231 | -0.0039367 | 0.0036017 | 0.066841 | 0.056027 | -0.011106 | 0.02164 | -0.0034435 | -0.050354 | 60.141 | -61.2076 | 60.434 | -60.9924 | -61.4273 | -61.3815 | 0.045776 | 60.1318 | -61.2625 | 60.4065 | -61.1435 | -61.2488 | -61.2762 | -0.004578 | -0.21057 | 0.082398 | 0.21057 | -0.17853 | -0.2243 | -0.17395 | -0.21973 | -0.059509 | -0.21973 | 0.054932 | 0.059509 | -0.073242 | -0.045776 | -0.013733 | 0.013733 | 0.21515 | 121.6415 | 0.11902 | 121.669 | 121.3486 | 121.3943 | 121.344 | 121.3348 | -121.5591 | -121.6141 | 121.637 | 121.6095 | 61.1526 | 61.2488
38.8125 | 121.8475 | -61.2579 | 60.347 | -0.089798 | 0.0046078 | 0.065396 | 0.062457 | -0.0031957 | -0.0060434 | -0.0013051 | -0.1077 | 0.0050971 | 0.064918 | 0.051755 | -0.011747 | 0.025912 | -0.0057935 | -0.059509 | 60.1959 | -61.2167 | 60.4202 | -61.0474 | -61.4456 | -61.441 | -0.004578 | 60.1868 | -61.2762 | 60.3287 | -61.2259 | -61.3678 | -61.3724 | 0.041199 | -0.15106 | 0.073242 | 0.21057 | -0.1831 | -0.18768 | -0.2243 | -0.22888 | -0.01831 | -0.16022 | -0.018311 | 0.032044 | -0.11444 | -0.10986 | -0.09613 | -0.091553 | 0.16937 | 121.637 | 0.050354 | 121.6049 | 121.4127 | 121.463 | 121.4539 | 121.4447 | -121.5637 | -121.6232 | 121.6782 | 121.5866 | 61.1984 | 61.2534
40.5625 | 121.7834 | -61.2442 | 60.4019 | -0.036392 | 0.003967 | 0.064328 | 0.063098 | 0.0023585 | -0.0090342 | -0.0013051 | -0.068024 | 0.0061651 | 0.065772 | 0.051968 | -0.010252 | 0.023135 | -0.0040845 | -0.027466 | 60.2051 | -61.2213 | 60.4248 | -61.0428 | -61.4365 | -61.4182 | 0.036621 | 60.228 | -61.2579 | 60.3333 | -61.2259 | -61.3312 | -61.3815 | 0.022889 | -0.19684 | 0.022888 | 0.20142 | -0.17395 | -0.19226 | -0.19684 | -0.21515 | -0.013733 | -0.17395 | -0.068665 | 0.018311 | -0.13733 | -0.086975 | -0.1236 | -0.073242 | 0.17853 | 121.6461 | 0.032044 | 121.5912 | 121.4264 | 121.4859 | 121.4493 | 121.4722 | -121.6232 | -121.6599 | 121.669 | 121.5775 | 61.2167 | 61.2808
42.25 | 121.788 | -61.2991 | 60.2783 | -0.06691 | 0.0075986 | 0.067105 | 0.063952 | -0.0014867 | -0.0060434 | 0.0010447 | -0.10464 | 0.0029607 | 0.067268 | 0.062649 | -0.01132 | 0.024204 | -0.01028 | -0.19684 | 60.1547 | -61.3083 | 60.3149 | -61.171 | -61.5829 | -61.5463 | -0.1831 | 60.1273 | -61.3358 | 60.2371 | -61.3678 | -61.5143 | -61.4822 | -0.009156 | -0.1236 | 0.036621 | 0.12817 | -0.24719 | -0.28381 | -0.23804 | -0.27466 | -0.036621 | -0.15106 | -0.041198 | -0.068665 | -0.18311 | -0.21515 | -0.14648 | -0.17853 | 0.13733 | 121.6232 | -0.032044 | 121.5729 | 121.463 | 121.463 | 121.4539 | 121.4264 | -121.5866 | -121.6141 | 121.6141 | 121.5363 | 61.1023 | 61.116
44 | 121.907 | -61.1938 | 60.3836 | -0.082169 | 0.003967 | 0.064969 | 0.060748 | -0.0066137 | -0.006257 | -0.0025869 | 0.011322 | 0.0059515 | 0.0662 | 0.053677 | -0.011747 | 0.02164 | -0.0028027 | -0.064087 | 60.1639 | -61.2167 | 60.4614 | -60.9741 | -61.3861 | -61.3541 | 0.064087 | 60.1593 | -61.2534 | 60.4294 | -61.1114 | -61.2167 | -61.2808 | -0.022888 | -0.21973 | 0.07782 | 0.21973 | -0.16022 | -0.19226 | -0.13733 | -0.16937 | -0.059509 | -0.2243 | 0.045776 | 0.082398 | -0.086975 | -0.022888 | -0.027466 | 0.036621 | 0.24262 | 121.6782 | 0.14191 | 121.6827 | 121.3806 | 121.4127 | 121.3577 | 121.3531 | -121.6003 | -121.637 | 121.6553 | 121.6232 | 61.1298 | 61.2579
45.7344 | 121.9116 | -61.1755 | 60.3516 | -0.06691 | 0.0035398 | 0.066678 | 0.061602 | -0.0025549 | -0.0054026 | -0.0019461 | 0.011322 | 0.0046697 | 0.066627 | 0.051327 | -0.013029 | 0.023776 | -0.0051525 | -0.050354 | 60.1501 | -61.1984 | 60.466 | -60.9604 | -61.3861 | -61.3266 | 0.10986 | 60.1547 | -61.2396 | 60.4431 | -61.0886 | -61.1938 | -61.2488 | -0.022888 | -0.20142 | 0.11444 | 0.21515 | -0.15106 | -0.21057 | -0.12817 | -0.18768 | -0.064087 | -0.19684 | 0.091553 | 0.086975 | -0.073242 | -0.018311 | -0.009155 | 0.045776 | 0.23804 | 121.6644 | 0.15106 | 121.6827 | 121.3486 | 121.3943 | 121.3257 | 121.3303 | -121.55 | -121.5912 | 121.6415 | 121.6187 | 61.1252 | 61.2854
47.4062 | 121.9162 | -61.1847 | 60.347 | -0.082169 | 0.0052488 | 0.065183 | 0.061175 | -0.0042639 | -0.0083932 | -0.0019461 | -0.022247 | 0.0016791 | 0.064918 | 0.055813 | -0.013456 | 0.02399 | -0.0030163 | 0.068665 | 60.1822 | -61.1618 | 60.5621 | -60.8871 | -61.2991 | -61.29 | 0.19684 | 60.1822 | -61.1984 | 60.4523 | -61.084 | -61.1984 | -61.2671 | 0.022888 | -0.16479 | 0.21515 | 0.29755 | -0.10529 | -0.11444 | -0.12817 | -0.13733 | -0.013733 | -0.16479 | 0.10529 | 0.10071 | -0.082398 | -0.013733 | -0.068665 | 0 | 0.27466 | 121.7239 | 0.11444 | 121.6507 | 121.344 | 121.3806 | 121.3669 | 121.3669 | -121.5088 | -121.5454 | 121.7468 | 121.637 | 61.2534 | 61.3815
49.1406 | 121.8338 | -61.2625 | 60.3195 | -0.097427 | 0.0050352 | 0.065183 | 0.065875 | -0.00084593 | -0.0073252 | -0.00023714 | -0.11075 | 0.0038153 | 0.065132 | 0.056454 | -0.013883 | 0.024204 | -0.0036573 | -0.082397 | 60.1364 | -61.2808 | 60.4156 | -61.0199 | -61.4731 | -61.4456 | 0.013733 | 60.1593 | -61.2991 | 60.3516 | -61.2259 | -61.3541 | -61.377 | -0.018311 | -0.1831 | 0.09613 | 0.24262 | -0.18311 | -0.21057 | -0.1648 | -0.19226 | -0.036621 | -0.16022 | 0.032043 | 0.036621 | -0.11444 | -0.091553 | -0.07782 | -0.054932 | 0.26093 | 121.6965 | 0.073242 | 121.6507 | 121.4172 | 121.4584 | 121.3989 | 121.4218 | -121.6003 | -121.6187 | 121.6782 | 121.6141 | 61.1801 | 61.2762
50.8281 | 121.9162 | -61.1801 | 60.379 | -0.074539 | 0.0035398 | 0.065396 | 0.062243 | -0.0012731 | -0.0094614 | 0.00083106 | -0.01004 | 0.0029607 | 0.0662 | 0.048764 | -0.010679 | 0.021854 | -0.0064343 | 0.068665 | 60.1868 | -61.1664 | 60.5438 | -60.8688 | -61.322 | -61.2854 | 0.20142 | 60.1593 | -61.1938 | 60.4523 | -61.0748 | -61.1984 | -61.2442 | 0.013733 | -0.19226 | 0.1648 | 0.31128 | -0.10529 | -0.14191 | -0.11902 | -0.15564 | -0.013733 | -0.21973 | 0.073243 | 0.10529 | -0.064087 | -0.01831 | -0.050354 | -0.004577 | 0.29755 | 121.7102 | 0.11902 | 121.6461 | 121.3531 | 121.3531 | 121.3669 | 121.3394 | -121.5454 | -121.5729 | 121.7239 | 121.6324 | 61.2488 | 61.3815
52.5781 | 121.9345 | -61.1618 | 60.379 | -0.12032 | 0.0037534 | 0.063901 | 0.061389 | -0.0046911 | -0.0092478 | -0.0025869 | -0.0069885 | 0.0029607 | 0.065986 | 0.051327 | -0.0087564 | 0.02164 | -0.0040845 | 0.068665 | 60.1822 | -61.1526 | 60.5621 | -60.8688 | -61.3174 | -61.2625 | 0.21057 | 60.1547 | -61.203 | 60.4797 | -61.0748 | -61.1893 | -61.2259 | 0.009155 | -0.19684 | 0.18311 | 0.29297 | -0.10071 | -0.15564 | -0.10986 | -0.1648 | -0.041199 | -0.2243 | 0.10071 | 0.086975 | -0.064087 | -0.027466 | -0.022888 | 0.013733 | 0.28381 | 121.7148 | 0.12817 | 121.6827 | 121.3348 | 121.3577 | 121.344 | 121.3165 | -121.5317 | -121.582 | 121.7239 | 121.6415 | 61.2305 | 61.3724
54.3281 | 121.843 | -61.2579 | 60.3378 | -0.074539 | 0.0058896 | 0.066251 | 0.06502 | -0.0031957 | -0.006257 | -0.00066434 | -0.092438 | 0.0048833 | 0.065772 | 0.051755 | -0.013029 | 0.023776 | -0.0062207 | -0.064087 | 60.1639 | -61.2579 | 60.4065 | -61.0382 | -61.4639 | -61.4548 | 0.022888 | 60.1547 | -61.2717 | 60.3287 | -61.235 | -61.3678 | -61.3724 | 0 | -0.17395 | 0.068664 | 0.21973 | -0.19684 | -0.20599 | -0.19684 | -0.20599 | -0.013732 | -0.18311 | -0.009156 | 0.022889 | -0.11444 | -0.10986 | -0.10071 | -0.096131 | 0.21973 | 121.6644 | 0.036621 | 121.6003 | 121.4218 | 121.4264 | 121.4218 | 121.4127 | -121.5958 | -121.6095 | 121.6644 | 121.5866 | 61.1938 | 61.2808
56.0625 | 121.9254 | -61.2488 | 60.2554 | -0.097427 | 0.0067442 | 0.067319 | 0.064807 | 0.0029993 | -0.0077524 | -0.0023733 | -0.06192 | 0.0040289 | 0.065559 | 0.043637 | -0.0091836 | 0.024844 | -0.0019483 | -0.17853 | 60.0952 | -61.2625 | 60.4156 | -61.0336 | -61.4822 | -61.4502 | -0.032043 | 60.0677 | -61.3037 | 60.379 | -61.1893 | -61.3312 | -61.3266 | -0.013733 | -0.16022 | 0.16022 | 0.21515 | -0.20142 | -0.23346 | -0.18768 | -0.21973 | -0.054932 | -0.18768 | 0.1236 | 0.059509 | -0.07782 | -0.082398 | -0.022888 | -0.027466 | 0.22888 | 121.6782 | 0.11444 | 121.6827 | 121.3577 | 121.3715 | 121.344 | 121.3165 | -121.5179 | -121.5591 | 121.6644 | 121.6278 | 61.0703 | 61.2167
57.8125 | 121.9162 | -61.171 | 60.3561 | -0.12032 | 0.0035398 | 0.066678 | 0.061175 | -0.0019141 | -0.010102 | -0.0010915 | 0.0021667 | 0.0046697 | 0.066413 | 0.053464 | -0.0087564 | 0.021213 | -0.0049389 | -0.064087 | 60.141 | -61.2076 | 60.4706 | -60.965 | -61.4044 | -61.3815 | 0.054932 | 60.1547 | -61.2305 | 60.4294 | -61.1114 | -61.2213 | -61.2717 | -0.036622 | -0.21515 | 0.11444 | 0.20599 | -0.21057 | -0.23346 | -0.17395 | -0.19684 | -0.05951 | -0.20142 | 0.073242 | 0.059509 | -0.10071 | -0.050354 | -0.041198 | 0.009156 | 0.24262 | 121.6782 | 0.11902 | 121.6599 | 121.3486 | 121.3852 | 121.3119 | 121.3257 | -121.5637 | -121.5866 | 121.6415 | 121.6003 | 61.1069 | 61.2259
59.5625 | 121.8063 | -61.2762 | 60.3195 | -0.05928 | 0.0071714 | 0.066678 | 0.064807 | -0.00084593 | -0.0073252 | 0.0018991 | -0.1138 | 0.0042425 | 0.067268 | 0.056027 | -0.011747 | 0.022281 | -2.571e-05 | -0.091553 | 60.1456 | -61.2717 | 60.4019 | -61.0474 | -61.4639 | -61.4548 | -0.036621 | 60.141 | -61.3037 | 60.3058 | -61.2717 | -61.4136 | -61.409 | 0.004578 | -0.17395 | 0.082398 | 0.22888 | -0.17853 | -0.18768 | -0.18311 | -0.19226 | -0.027466 | -0.17853 | -0.013733 | 0.004578 | -0.13275 | -0.13733 | -0.10529 | -0.10986 | 0.2243 | 121.6736 | 0.032044 | 121.6095 | 121.4172 | 121.4447 | 121.4218 | 121.4172 | -121.5912 | -121.6232 | 121.6782 | 121.582 | 61.1847 | 61.2396
61.2344 | 121.8979 | -61.2122 | 60.3561 | -0.089798 | 0.0067442 | 0.066251 | 0.059253 | -0.0017005 | -0.0090342 | 0.00083106 | -0.01004 | 0.0040289 | 0.067909 | 0.051114 | -0.011533 | 0.022708 | -0.0060071 | -0.082397 | 60.1456 | -61.235 | 60.4431 | -60.9879 | -61.4273 | -61.3907 | 0.018311 | 60.1501 | -61.2396 | 60.3745 | -61.1664 | -61.29 | -61.322 | -0.022888 | -0.21057 | 0.086975 | 0.2243 | -0.17853 | -0.21515 | -0.15564 | -0.19226 | -0.027466 | -0.20599 | 0.018311 | 0.045776 | -0.10986 | -0.07782 | -0.082397 | -0.050354 | 0.24719 | 121.6782 | 0.073242 | 121.6141 | 121.3806 | 121.3898 | 121.3577 | 121.3623 | -121.5912 | -121.5958 | 121.6553 | 121.5866 | 61.1298 | 61.2305
62.9844 | 121.9208 | -61.1435 | 60.3699 | -0.074539 | 0.0050352 | 0.064542 | 0.060321 | -0.0023413 | -0.0047616 | -0.0025869 | -0.0069885 | 0.0038153 | 0.065986 | 0.052395 | -0.012388 | 0.023776 | -0.0032299 | 0.045776 | 60.1089 | -61.2122 | 60.5621 | -60.8551 | -61.2946 | -61.2717 | 0.19684 | 60.1639 | -61.1664 | 60.4797 | -61.0611 | -61.1618 | -61.2442 | -0.068664 | -0.26093 | 0.19226 | 0.28839 | -0.12817 | -0.15106 | -0.059509 | -0.082398 | -0.022888 | -0.20599 | 0.10986 | 0.082398 | -0.10071 | -0.01831 | -0.07782 | 0.004578 | 0.35706 | 121.7743 | 0.10529 | 121.6461 | 121.3211 | 121.3303 | 121.2524 | 121.3074 | -121.582 | -121.5363 | 121.7056 | 121.6232 | 61.1893 | 61.3403
64.7344 | 121.7972 | -61.2213 | 60.4202 | -0.051651 | 0.003967 | 0.064542 | 0.061389 | -0.0042639 | -0.010316 | -0.0019461 | -0.049713 | 0.0063787 | 0.067695 | 0.056241 | -0.010252 | 0.022495 | 0.00040169 | 0.032043 | 60.1868 | -61.1893 | 60.4431 | -61.0016 | -61.4182 | -61.3953 | 0.054932 | 60.2142 | -61.2488 | 60.3287 | -61.1938 | -61.322 | -61.377 | 0.032043 | -0.23346 | 0.022888 | 0.21973 | -0.17395 | -0.19684 | -0.20599 | -0.22888 | -0.027466 | -0.20599 | -0.091553 | 0.027465 | -0.15564 | -0.10071 | -0.12817 | -0.073242 | 0.18768 | 121.6324 | 0.054931 | 121.5775 | 121.376 | 121.463 | 121.4081 | 121.4355 | -121.6095 | -121.669 | 121.6644 | 121.55 | 61.2534 | 61.2762
66.4219 | 121.7834 | -61.322 | 60.3104 | -0.06691 | 0.0063168 | 0.066892 | 0.063952 | 0.0025721 | -0.0054026 | -0.0017325 | -0.11075 | 0.0018927 | 0.066627 | 0.056881 | -0.011747 | 0.024417 | -0.00023931 | -0.13733 | 60.1593 | -61.29 | 60.347 | -61.1206 | -61.5601 | -61.5234 | -0.11444 | 60.1181 | -61.3403 | 60.2737 | -61.3129 | -61.4594 | -61.441 | 0.032043 | -0.15106 | 0.036621 | 0.20142 | -0.20142 | -0.23804 | -0.23346 | -0.27008 | -0.018311 | -0.19226 | -0.036621 | 0.009155 | -0.11902 | -0.13733 | -0.10071 | -0.11902 | 0.16937 | 121.637 | 0.027466 | 121.6141 | 121.4493 | 121.4584 | 121.4813 | 121.4401 | -121.6003 | -121.6507 | 121.669 | 121.5958 | 61.1847 | 61.2076
68.1719 | 121.8201 | -61.2808 | 60.3241 | -0.097427 | 0.0052488 | 0.066037 | 0.063311 | 0.00022207 | -0.006898 | -0.0023733 | -0.09549 | 0.0068059 | 0.067909 | 0.05795 | -0.0091836 | 0.025699 | -0.0064343 | -0.091553 | 60.1685 | -61.2671 | 60.4019 | -61.0336 | -61.4868 | -61.4594 | -0.009155 | 60.1547 | -61.3083 | 60.3058 | -61.2579 | -61.409 | -61.4044 | 0.013733 | -0.15564 | 0.07782 | 0.24719 | -0.17853 | -0.20599 | -0.19226 | -0.21973 | -0.027466 | -0.16937 | -0.018311 | 0.022888 | -0.1236 | -0.12817 | -0.09613 | -0.10071 | 0.23346 | 121.669 | 0.050354 | 121.6141 | 121.4355 | 121.463 | 121.4493 | 121.4355 | -121.5912 | -121.6324 | 121.6827 | 121.5866 | 61.1893 | 61.2717
69.9219 | 121.9162 | -61.1755 | 60.3378 | -0.044022 | 0.0043942 | 0.067105 | 0.059253 | 8.47e-06 | -0.009675 | -0.0023733 | 0.029632 | 0.0042425 | 0.066841 | 0.054745 | -0.0093972 | 0.021854 | -0.0017347 | -0.027466 | 60.1639 | -61.1938 | 60.5072 | -60.9146 | -61.3495 | -61.3129 | 0.13733 | 60.1593 | -61.2259 | 60.4568 | -61.0886 | -61.1893 | -61.2305 | -0.018311 | -0.17395 | 0.16937 | 0.26093 | -0.13733 | -0.17395 | -0.11902 | -0.15564 | -0.050354 | -0.17853 | 0.11902 | 0.086975 | -0.054932 | -0.013733 | -0.004578 | 0.036621 | 0.27924 | 121.7011 | 0.13733 | 121.6827 | 121.3577 | 121.3852 | 121.3394 | 121.3348 | -121.5317 | -121.5637 | 121.6827 | 121.6324 | 61.1481 | 61.3129
71.5938 | 121.875 | -61.2122 | 60.3287 | -0.13557 | 0.0041806 | 0.065396 | 0.061816 | -0.0021277 | -0.0090342 | -0.0019461 | -0.0039367 | 0.0033881 | 0.066413 | 0.057522 | -0.010252 | 0.023563 | -0.0038709 | -0.10986 | 60.1364 | -61.235 | 60.434 | -61.0107 | -61.4456 | -61.409 | 0.027466 | 60.1227 | -61.2762 | 60.3699 | -61.1847 | -61.3083 | -61.3174 | -0.022888 | -0.19226 | 0.10529 | 0.20142 | -0.19684 | -0.23346 | -0.17395 | -0.21057 | -0.064087 | -0.20599 | 0.041199 | 0.027466 | -0.10529 | -0.096131 | -0.041199 | -0.032044 | 0.2243 | 121.669 | 0.091553 | 121.6461 | 121.3715 | 121.3989 | 121.3486 | 121.3348 | -121.5637 | -121.6049 | 121.6461 | 121.582 | 61.1023 | 61.2396
73.3438 | 121.9299 | -61.2808 | 60.2783 | -0.12032 | 0.008453 | 0.070523 | 0.063311 | -0.0010595 | -0.0064706 | -0.0040823 | -0.068024 | 0.0025335 | 0.069404 | 0.045773 | -0.010038 | 0.023563 | -0.0068615 | -0.12817 | 60.0998 | -61.2808 | 60.434 | -61.0062 | -61.4639 | -61.4227 | -0.018311 | 60.0449 | -61.3129 | 60.3699 | -61.203 | -61.3129 | -61.3312 | 0 | -0.17853 | 0.15564 | 0.27466 | -0.14191 | -0.18311 | -0.14191 | -0.18311 | -0.032043 | -0.23346 | 0.091553 | 0.07782 | -0.050354 | -0.032043 | -0.018311 | 0 | 0.27466 | 121.7148 | 0.10986 | 121.6827 | 121.3806 | 121.3577 | 121.3806 | 121.3257 | -121.5591 | -121.5912 | 121.7148 | 121.6507 | 61.1526 | 61.2625
75.0938 | 121.8292 | -61.2762 | 60.3333 | -0.13557 | 0.0046078 | 0.065183 | 0.062671 | -0.0042639 | -0.0094614 | -0.0028005 | -0.1077 | 0.0055243 | 0.068977 | 0.059445 | -0.012388 | 0.024631 | -0.0047253 | -0.09613 | 60.1501 | -61.2534 | 60.4156 | -61.0336 | -61.4685 | -61.4594 | -0.009155 | 60.1593 | -61.29 | 60.3195 | -61.2579 | -61.409 | -61.4182 | 0.022888 | -0.18311 | 0.082397 | 0.24262 | -0.18311 | -0.19226 | -0.20599 | -0.21515 | -0.013733 | -0.17395 | -0.013733 | 0.01831 | -0.14191 | -0.13275 | -0.12817 | -0.11902 | 0.21973 | 121.669 | 0.032043 | 121.6095 | 121.4035 | 121.4493 | 121.4264 | 121.4355 | -121.5866 | -121.6232 | 121.6919 | 121.5958 | 61.1801 | 61.2671
76.7812 | 121.9025 | -61.2213 | 60.3012 | -0.11269 | 0.0048214 | 0.067533 | 0.060107 | -0.0044775 | -0.0092478 | -0.0021597 | -0.049713 | 0.0044561 | 0.066413 | 0.054959 | -0.010893 | 0.024204 | -0.0053661 | -0.10529 | 60.1135 | -61.2259 | 60.4431 | -60.9879 | -61.4502 | -61.409 | 0.013733 | 60.0861 | -61.3037 | 60.3836 | -61.1801 | -61.3083 | -61.3129 | -0.004578 | -0.18768 | 0.14191 | 0.23346 | -0.18768 | -0.22888 | -0.18311 | -0.2243 | -0.082398 | -0.21515 | 0.082398 | 0.041198 | -0.091553 | -0.086976 | -0.009155 | -0.004578 | 0.23804 | 121.669 | 0.1236 | 121.6873 | 121.3394 | 121.3898 | 121.3348 | 121.3074 | -121.5271 | -121.6049 | 121.6644 | 121.6049 | 61.116 | 61.235
78.5312 | 121.9574 | -61.1572 | 60.3561 | -0.082169 | 0.0043942 | 0.064542 | 0.05968 | -0.0010595 | -0.0088206 | -0.0038687 | 0.026581 | 0.0025335 | 0.065986 | 0.05859 | -0.011747 | 0.022067 | -0.0053661 | 0.041199 | 60.1547 | -61.1893 | 60.5347 | -60.8826 | -61.3083 | -61.2946 | 0.20142 | 60.1639 | -61.2167 | 60.4797 | -61.0703 | -61.1755 | -61.2167 | -0.032043 | -0.20142 | 0.17853 | 0.27466 | -0.13733 | -0.15106 | -0.10529 | -0.11902 | -0.059509 | -0.19226 | 0.1236 | 0.086976 | -0.059509 | -0.01831 | 0 | 0.041199 | 0.3067 | 121.7239 | 0.14648 | 121.6965 | 121.344 | 121.3806 | 121.312 | 121.3211 | -121.5454 | -121.5729 | 121.6919 | 121.637 | 61.1984 | 61.3586
80.2656 | 121.8979 | -61.2579 | 60.26 | -0.097427 | 0.0058896 | 0.067746 | 0.063739 | -0.0046911 | -0.0064706 | -0.0034415 | -0.086334 | 0.0044561 | 0.066841 | 0.056668 | -0.012602 | 0.022281 | -0.0034435 | -0.20599 | 60.1135 | -61.3037 | 60.3653 | -61.0977 | -61.5326 | -61.4868 | -0.082397 | 60.0861 | -61.3312 | 60.3653 | -61.2488 | -61.3449 | -61.3449 | -0.045776 | -0.14648 | 0.10529 | 0.16022 | -0.22888 | -0.27466 | -0.1831 | -0.22888 | -0.073242 | -0.17395 | 0.10529 | 0.009156 | -0.086975 | -0.086975 | -0.013733 | -0.013733 | 0.20599 | 121.669 | 0.082398 | 121.6965 | 121.4172 | 121.4172 | 121.3715 | 121.344 | -121.5637 | -121.5912 | 121.6232 | 121.6232 | 61.0519 | 61.1755
81.9531 | 121.9528 | -61.1893 | 60.3653 | -0.097427 | 0.0041806 | 0.06561 | 0.060321 | 0.0025721 | -0.0083932 | -0.0028005 | -0.022247 | 0.0038153 | 0.066413 | 0.055173 | -0.010679 | 0.02399 | -0.0066479 | 0.050354 | 60.1639 | -61.1893 | 60.5438 | -60.8734 | -61.3312 | -61.2946 | 0.20599 | 60.1822 | -61.1801 | 60.466 | -61.0703 | -61.1801 | -61.2305 | 0 | -0.20142 | 0.17853 | 0.31586 | -0.10529 | -0.14191 | -0.10529 | -0.14191 | 0.009155 | -0.18311 | 0.10071 | 0.11902 | -0.041199 | 0.009155 | -0.050354 | 0 | 0.31586 | 121.7331 | 0.10986 | 121.6461 | 121.3531 | 121.3623 | 121.3531 | 121.3715 | -121.5546 | -121.5454 | 121.7331 | 121.6553 | 61.2396 | 61.3953
83.7031 | 121.7789 | -61.3083 | 60.3012 | -0.13557 | 0.0078122 | 0.06796 | 0.063739 | 0.00064947 | -0.006898 | -0.0036551 | -0.10159 | 0.0061651 | 0.06855 | 0.054532 | -0.012388 | 0.025058 | -0.0023755 | -0.20142 | 60.1318 | -61.3083 | 60.3149 | -61.171 | -61.5875 | -61.5463 | -0.15564 | 60.1501 | -61.3266 | 60.2142 | -61.3678 | -61.5005 | -61.4639 | 0 | -0.16937 | 0.013733 | 0.13733 | -0.23804 | -0.27923 | -0.23804 | -0.27923 | -0.01831 | -0.15106 | -0.086975 | -0.059509 | -0.15564 | -0.19226 | -0.13733 | -0.17395 | 0.13733 | 121.6232 | -0.041199 | 121.5408 | 121.4401 | 121.4767 | 121.4401 | 121.4584 | -121.6095 | -121.6278 | 121.6232 | 121.5225 | 61.1069 | 61.1526
85.4375 | 121.8384 | -61.2488 | 60.3699 | -0.044022 | 0.0063168 | 0.066464 | 0.062671 | -0.0053321 | -0.0077524 | -0.0040823 | -0.086334 | 0.0048833 | 0.068336 | 0.05795 | -0.012388 | 0.02399 | -0.0025891 | -0.027466 | 60.2005 | -61.2625 | 60.4156 | -61.0657 | -61.4548 | -61.4456 | 0 | 60.2005 | -61.2808 | 60.3195 | -61.2167 | -61.3541 | -61.3586 | -0.013733 | -0.16937 | 0.045776 | 0.1831 | -0.19684 | -0.20599 | -0.18311 | -0.19226 | -0.032044 | -0.16937 | -0.050354 | 0.032043 | -0.10986 | -0.10529 | -0.07782 | -0.073242 | 0.19684 | 121.6782 | 0.064087 | 121.6003 | 121.463 | 121.4813 | 121.4493 | 121.4493 | -121.6324 | -121.6507 | 121.6644 | 121.5683 | 61.2213 | 61.2488
87.125 | 121.8109 | -61.3083 | 60.3058 | -0.15083 | 0.010162 | 0.067105 | 0.063952 | 8.47e-06 | -0.0066844 | -0.0019461 | -0.098541 | 0.0048833 | 0.068977 | 0.048977 | -0.010893 | 0.025272 | -0.0057935 | -0.21057 | 60.1318 | -61.3174 | 60.2783 | -61.1938 | -61.6013 | -61.5646 | -0.18768 | 60.1181 | -61.3541 | 60.2325 | -61.3586 | -61.4685 | -61.4502 | -0.009155 | -0.17395 | -0.027466 | 0.11444 | -0.25635 | -0.29297 | -0.24719 | -0.28381 | -0.045776 | -0.18768 | -0.073242 | -0.050354 | -0.14191 | -0.16022 | -0.09613 | -0.11444 | 0.1236 | 121.5958 | -0.004578 | 121.5866 | 121.4493 | 121.4722 | 121.4401 | 121.4264 | -121.6232 | -121.6599 | 121.5866 | 121.5408 | 61.0977 | 61.1206
88.875 | 121.8887 | -61.2762 | 60.2692 | -0.089798 | 0.0058896 | 0.065824 | 0.062671 | -0.00020513 | -0.0058298 | -0.0038687 | -0.04361 | 0.0038153 | 0.067695 | 0.061368 | -0.010038 | 0.024844 | -0.0032299 | -0.21973 | 60.1318 | -61.2991 | 60.3287 | -61.116 | -61.5829 | -61.528 | -0.1236 | 60.1089 | -61.3541 | 60.3058 | -61.2625 | -61.3861 | -61.3907 | -0.022888 | -0.13733 | 0.059509 | 0.16022 | -0.25177 | -0.3067 | -0.22888 | -0.28381 | -0.07782 | -0.16022 | 0.036621 | 0.013733 | -0.11444 | -0.10986 | -0.036621 | -0.032043 | 0.1831 | 121.6278 | 0.091553 | 121.6599 | 121.431 | 121.463 | 121.4081 | 121.3852 | -121.5683 | -121.6232 | 121.6049 | 121.582 | 61.0565 | 61.1526
90.625 | 121.8475 | -61.1847 | 60.4019 | -0.089798 | 0.0054624 | 0.066037 | 0.05968 | -0.0070409 | -0.006898 | -0.0010915 | -0.01004 | 0.0048833 | 0.067268 | 0.055173 | -0.011533 | 0.023135 | -0.0038709 | 0.045776 | 60.1913 | -61.1847 | 60.5255 | -60.9055 | -61.3449 | -61.3129 | 0.16479 | 60.1776 | -61.2305 | 60.4019 | -61.1389 | -61.2488 | -61.2854 | 0 | -0.21057 | 0.1236 | 0.27923 | -0.12817 | -0.16022 | -0.12817 | -0.16022 | -0.045777 | -0.2243 | 0 | 0.045776 | -0.10071 | -0.064087 | -0.054931 | -0.01831 | 0.27923 | 121.7102 | 0.091553 | 121.6324 | 121.376 | 121.4081 | 121.376 | 121.3623 | -121.5866 | -121.6324 | 121.7102 | 121.5866 | 61.2305 | 61.3495
92.2969 | 121.9208 | -61.1984 | 60.3653 | -0.12032 | 0.0052488 | 0.065824 | 0.060748 | -0.0068273 | -0.008607 | -0.0013051 | -0.0039367 | 0.0033881 | 0.066627 | 0.053036 | -0.010893 | 0.023349 | -0.0057935 | 0.068665 | 60.1913 | -61.171 | 60.5576 | -60.8414 | -61.29 | -61.29 | 0.20599 | 60.1639 | -61.2076 | 60.4797 | -61.0794 | -61.1893 | -61.2488 | 0.027466 | -0.17395 | 0.19226 | 0.35706 | -0.091553 | -0.091553 | -0.11902 | -0.11902 | -0.009156 | -0.20142 | 0.11444 | 0.11902 | -0.050354 | 0.009155 | -0.041198 | 0.018311 | 0.32959 | 121.7285 | 0.12817 | 121.6873 | 121.3623 | 121.3715 | 121.3898 | 121.3623 | -121.5363 | -121.5729 | 121.756 | 121.6782 | 61.2671 | 61.4044
94.0312 | 121.8155 | -61.2854 | 60.3195 | -0.089798 | 0.0069578 | 0.064969 | 0.065875 | -0.0068273 | -0.0081796 | -0.0032277 | -0.1138 | 0.0046697 | 0.066627 | 0.06094 | -0.013883 | 0.024844 | -0.0055799 | -0.086975 | 60.1501 | -61.2717 | 60.3928 | -61.0382 | -61.5005 | -61.4685 | -0.027466 | 60.141 | -61.2946 | 60.2921 | -61.29 | -61.4227 | -61.4273 | 0.013733 | -0.16937 | 0.073242 | 0.24719 | -0.18311 | -0.21515 | -0.19684 | -0.22888 | -0.009156 | -0.17853 | -0.027466 | -0.004578 | -0.14191 | -0.13733 | -0.13275 | -0.12817 | 0.23346 | 121.6644 | 0.004578 | 121.5866 | 121.4218 | 121.4355 | 121.4355 | 121.4264 | -121.5912 | -121.6141 | 121.6782 | 121.5775 | 61.1984 | 61.2579
95.7188 | 121.9116 | -61.1801 | 60.3653 | -0.05928 | 0.003967 | 0.066251 | 0.060534 | -0.00041873 | -0.010743 | -0.0021597 | -0.0039367 | 0.0036017 | 0.064704 | 0.050686 | -0.011961 | 0.022067 | -0.0017347 | 0.050354 | 60.1868 | -61.1755 | 60.5667 | -60.8688 | -61.3174 | -61.2762 | 0.18768 | 60.2097 | -61.1893 | 60.4706 | -61.0703 | -61.1801 | -61.2167 | 0.004578 | -0.17853 | 0.20142 | 0.31128 | -0.09613 | -0.13733 | -0.10071 | -0.14191 | -0.009155 | -0.15564 | 0.10529 | 0.10986 | -0.036621 | 0 | -0.027466 | 0.009155 | 0.3067 | 121.7422 | 0.11902 | 121.6599 | 121.3623 | 121.3989 | 121.3669 | 121.3898 | -121.5408 | -121.5546 | 121.7468 | 121.6507 | 61.2305 | 61.3678
97.4531 | 121.9299 | -61.2534 | 60.2737 | -0.16609 | 0.0058896 | 0.067533 | 0.062671 | -0.0031957 | -0.0066844 | -0.0013051 | -0.068024 | 0.0025335 | 0.065559 | 0.057522 | -0.01367 | 0.024417 | -0.0049389 | -0.13275 | 60.1044 | -61.2671 | 60.4294 | -61.0016 | -61.4777 | -61.4319 | -0.018311 | 60.054 | -61.3129 | 60.379 | -61.1984 | -61.3266 | -61.3174 | -0.013733 | -0.16937 | 0.15564 | 0.25177 | -0.17853 | -0.2243 | -0.16479 | -0.21057 | -0.059509 | -0.21973 | 0.10528 | 0.054932 | -0.064087 | -0.073242 | -0.004578 | -0.013733 | 0.2655 | 121.6965 | 0.11444 | 121.6919 | 121.3715 | 121.3669 | 121.3577 | 121.3074 | -121.5408 | -121.5866 | 121.6827 | 121.6324 | 61.1206 | 61.235
99.2031 | 121.7834 | -61.2305 | 60.4111 | -0.05928 | 0.005676 | 0.066037 | 0.060321 | -0.0042639 | -0.0075388 | -0.0015189 | -0.040558 | 0.0068059 | 0.067909 | 0.053464 | -0.01132 | 0.02399 | -0.0032299 | -0.032043 | 60.2188 | -61.2213 | 60.4294 | -61.0291 | -61.4365 | -61.4319 | 0.032043 | 60.2142 | -61.2717 | 60.3241 | -61.2305 | -61.3449 | -61.3632 | 0.009156 | -0.19226 | 0.01831 | 0.20142 | -0.20142 | -0.20599 | -0.21057 | -0.21515 | -0.041198 | -0.19684 | -0.086975 | 0 | -0.13275 | -0.11444 | -0.091553 | -0.073243 | 0.19226 | 121.6507 | 0.041198 | 121.5958 | 121.4401 | 121.4859 | 121.4493 | 121.4447 | -121.6324 | -121.6827 | 121.6599 | 121.5546 | 61.1984 | 61.2625
100.8906 | 121.8567 | -61.2488 | 60.3653 | -0.11269 | 0.0041806 | 0.066678 | 0.063525 | 0.0012903 | -0.0049754 | -0.00045074 | -0.064972 | 0.0036017 | 0.065986 | 0.051327 | -0.011533 | 0.025912 | -2.571e-05 | -0.036621 | 60.2234 | -61.2442 | 60.4019 | -61.0474 | -61.4639 | -61.4594 | -0.022888 | 60.1868 | -61.2717 | 60.3333 | -61.2213 | -61.3586 | -61.377 | 0.004577 | -0.14191 | 0.036622 | 0.20142 | -0.21057 | -0.21515 | -0.21515 | -0.21973 | -0.022888 | -0.17853 | -0.032043 | 0.027466 | -0.12817 | -0.10986 | -0.10529 | -0.086976 | 0.19684 | 121.6461 | 0.050354 | 121.6049 | 121.4676 | 121.4584 | 121.4722 | 121.4355 | -121.6095 | -121.637 | 121.6507 | 121.582 | 61.2122 | 61.2259
102.6406 | 121.8063 | -61.2442 | 60.379 | -0.05928 | 0.0054624 | 0.064969 | 0.061816 | -0.0010595 | -0.0094614 | -0.0021597 | -0.013092 | 0.0044561 | 0.06855 | 0.049191 | -0.011961 | 0.025912 | -0.0051525 | 0.050354 | 60.2005 | -61.1938 | 60.4752 | -60.9695 | -61.3907 | -61.3724 | 0.091553 | 60.1959 | -61.2442 | 60.347 | -61.2076 | -61.3266 | -61.3815 | 0.050354 | -0.17853 | 0.096131 | 0.27466 | -0.12817 | -0.14648 | -0.17853 | -0.19684 | 0 | -0.1831 | -0.032043 | 0.036621 | -0.13733 | -0.082397 | -0.13733 | -0.082397 | 0.22431 | 121.669 | 0.036621 | 121.5912 | 121.3943 | 121.4401 | 121.4447 | 121.4401 | -121.5729 | -121.6232 | 121.7194 | 121.5912 | 61.2946 | 61.3358
104.3906 | 121.9254 | -61.2671 | 60.2509 | -0.12794 | 0.007385 | 0.068387 | 0.061816 | -0.00063233 | -0.0094614 | -0.0017325 | -0.04361 | 0.0029607 | 0.067481 | 0.05325 | -0.012174 | 0.022708 | -0.0055799 | -0.12817 | 60.0998 | -61.2534 | 60.4294 | -60.9924 | -61.4548 | -61.4182 | -0.022888 | 60.0632 | -61.3449 | 60.3836 | -61.1893 | -61.322 | -61.322 | 0.013733 | -0.15106 | 0.17853 | 0.27466 | -0.15106 | -0.18768 | -0.16479 | -0.20142 | -0.07782 | -0.18768 | 0.13275 | 0.07782 | -0.054931 | -0.054931 | 0.022889 | 0.022889 | 0.26093 | 121.6827 | 0.15564 | 121.7285 | 121.3531 | 121.4081 | 121.3669 | 121.3303 | -121.5042 | -121.5958 | 121.6965 | 121.6507 | 61.1389 | 61.2442
106.0625 | 121.9391 | -61.1847 | 60.3653 | -0.089798 | 0.0058896 | 0.06326 | 0.059253 | -0.0055457 | -0.0077524 | -0.0049367 | 0.020477 | 0.0031745 | 0.06919 | 0.050686 | -0.010679 | 0.024204 | -0.0015209 | 0.041199 | 60.1639 | -61.1664 | 60.5347 | -60.8963 | -61.3266 | -61.3037 | 0.19684 | 60.173 | -61.2122 | 60.4752 | -61.0565 | -61.1618 | -61.2259 | 0.01831 | -0.20142 | 0.16937 | 0.28839 | -0.11902 | -0.14191 | -0.13733 | -0.16022 | -0.027466 | -0.19226 | 0.10986 | 0.12817 | -0.041199 | 0.022888 | -0.013733 | 0.050354 | 0.27008 | 121.7011 | 0.15564 | 121.6873 | 121.3303 | 121.3852 | 121.3486 | 121.3577 | -121.5317 | -121.5775 | 121.7194 | 121.6599 | 61.2259 | 61.3815
107.7969 | 121.8338 | -61.2579 | 60.3836 | -0.10506 | 0.0067442 | 0.06561 | 0.063525 | -0.0044775 | -0.0066844 | -0.0015189 | -0.071076 | 0.0036017 | 0.065772 | 0.068204 | -0.012602 | 0.023776 | -0.0060071 | -0.045776 | 60.1913 | -61.2305 | 60.4111 | -61.0428 | -61.4639 | -61.4639 | 0.027466 | 60.1776 | -61.2808 | 60.3333 | -61.2259 | -61.3541 | -61.3632 | 0.027466 | -0.19226 | 0.027466 | 0.21515 | -0.20599 | -0.20599 | -0.23346 | -0.23346 | -0.022888 | -0.20599 | -0.050354 | 0.032044 | -0.10528 | -0.09613 | -0.082397 | -0.073242 | 0.18768 | 121.6415 | 0.054932 | 121.6141 | 121.4218 | 121.4584 | 121.4493 | 121.4355 | -121.6141 | -121.6644 | 121.669 | 121.5912 | 61.2122 | 61.2854
109.5625 | 121.8567 | -61.2579 | 60.3149 | -0.074539 | 0.0063168 | 0.066037 | 0.062884 | -0.0010595 | -0.0071116 | -0.0010915 | -0.077179 | 0.0048833 | 0.064704 | 0.055173 | -0.011961 | 0.025058 | -0.0042981 | -0.054932 | 60.1822 | -61.2442 | 60.4065 | -61.0199 | -61.496 | -61.4685 | 0.027466 | 60.1318 | -61.3037 | 60.3378 | -61.235 | -61.3632 | -61.3678 | 0.013733 | -0.13275 | 0.091553 | 0.23804 | -0.21057 | -0.23804 | -0.2243 | -0.25177 | -0.045776 | -0.1831 | 0.022889 | 0.022889 | -0.10986 | -0.10528 | -0.064087 | -0.059509 | 0.22431 | 121.6507 | 0.068665 | 121.6415 | 121.4264 | 121.4355 | 121.4401 | 121.3898 | -121.5591 | -121.6187 | 121.6644 | 121.5958 | 61.203 | 61.2854
111.2344 | 121.8384 | -61.3037 | 60.2829 | -0.074539 | 0.0050352 | 0.067533 | 0.062243 | -0.0010595 | -0.007966 | -0.0038687 | -0.086334 | 0.0046697 | 0.068336 | 0.0556 | -0.010252 | 0.024631 | -0.0064343 | -0.20599 | 60.1227 | -61.3129 | 60.3058 | -61.1298 | -61.5784 | -61.5326 | -0.12817 | 60.0952 | -61.3358 | 60.2966 | -61.3037 | -61.4319 | -61.4365 | -0.009155 | -0.16022 | 0.022888 | 0.17395 | -0.22888 | -0.27466 | -0.21973 | -0.2655 | -0.032043 | -0.18768 | 0.013733 | 0 | -0.13275 | -0.12817 | -0.10071 | -0.096131 | 0.1831 | 121.6187 | 0.032043 | 121.6324 | 121.4355 | 121.431 | 121.4264 | 121.3989 | -121.5958 | -121.6187 | 121.6095 | 121.6003 | 61.0977 | 61.1755
112.9844 | 121.8384 | -61.2305 | 60.3882 | -0.05928 | 0.0054624 | 0.064756 | 0.062243 | -0.00020513 | -0.0073252 | -2.3544e-05 | -0.049713 | 0.0027471 | 0.064918 | 0.059018 | -0.011533 | 0.022495 | -0.0032299 | -0.036621 | 60.2234 | -61.2396 | 60.3882 | -61.0657 | -61.4639 | -61.4639 | 0.004578 | 60.2005 | -61.2671 | 60.3241 | -61.2259 | -61.3495 | -61.3586 | -0.009155 | -0.1648 | 0 | 0.16479 | -0.23346 | -0.23346 | -0.2243 | -0.2243 | -0.036621 | -0.18768 | -0.064087 | 0.004578 | -0.12817 | -0.11902 | -0.091553 | -0.082397 | 0.17395 | 121.6278 | 0.041199 | 121.5912 | 121.463 | 121.4676 | 121.4539 | 121.431 | -121.6278 | -121.6553 | 121.6187 | 121.5546 | 61.1938 | 61.235
114.7188 | 121.843 | -61.2625 | 60.3836 | -0.11269 | 0.0063168 | 0.06561 | 0.062243 | 0.0017175 | -0.0071116 | 0.00061746 | -0.049713 | 0.0055243 | 0.067054 | 0.058377 | -0.011106 | 0.024631 | -0.0064343 | -0.045776 | 60.1959 | -61.2488 | 60.4111 | -61.0519 | -61.4594 | -61.4456 | -0.004578 | 60.2051 | -61.29 | 60.3241 | -61.2213 | -61.3632 | -61.3678 | 0.013733 | -0.18768 | 0.027466 | 0.21057 | -0.18311 | -0.19684 | -0.19684 | -0.21057 | -0.027466 | -0.17853 | -0.059509 | 0.041199 | -0.10529 | -0.10071 | -0.07782 | -0.073242 | 0.19684 | 121.6599 | 0.068665 | 121.6141 | 121.4447 | 121.4951 | 121.4584 | 121.4676 | -121.6324 | -121.6736 | 121.6736 | 121.5866 | 61.2167 | 61.2579
116.4531 | 121.8201 | -61.2671 | 60.3241 | -0.044022 | 0.0071714 | 0.065396 | 0.062884 | -0.0017005 | -0.01053 | -0.0028005 | -0.09549 | 0.0053107 | 0.068122 | 0.059659 | -0.011747 | 0.025485 | -0.0040845 | -0.086975 | 60.1181 | -61.2762 | 60.4019 | -61.0336 | -61.4777 | -61.4731 | 0 | 60.1273 | -61.3037 | 60.3149 | -61.2717 | -61.4044 | -61.4044 | -0.009155 | -0.20599 | 0.07782 | 0.23346 | -0.20599 | -0.21057 | -0.19684 | -0.20142 | -0.036621 | -0.19684 | -0.009156 | -0.004577 | -0.13733 | -0.13733 | -0.10071 | -0.10071 | 0.24262 | 121.6782 | 0.032044 | 121.6187 | 121.3943 | 121.431 | 121.3852 | 121.3943 | -121.6003 | -121.6278 | 121.669 | 121.582 | 61.1801 | 61.2671
118.2031 | 121.9208 | -61.2579 | 60.2737 | -0.15846 | 0.0071714 | 0.065396 | 0.060962 | 0.0029993 | -0.0077524 | -0.0015189 | -0.046661 | 0.0040289 | 0.066841 | 0.054959 | -0.010893 | 0.024204 | -0.0042981 | -0.15106 | 60.0861 | -61.2946 | 60.4248 | -61.0062 | -61.4548 | -61.4319 | -0.022888 | 60.0906 | -61.3129 | 60.3745 | -61.1984 | -61.3312 | -61.322 | -0.036621 | -0.18768 | 0.15106 | 0.25177 | -0.17395 | -0.19684 | -0.13733 | -0.16022 | -0.054931 | -0.18311 | 0.10071 | 0.05951 | -0.064086 | -0.073242 | -0.009155 | -0.018311 | 0.28839 | 121.7194 | 0.11444 | 121.6873 | 121.3806 | 121.4035 | 121.344 | 121.3486 | -121.5683 | -121.5866 | 121.6827 | 121.6324 | 61.1069 | 61.235
119.8906 | 121.7972 | -61.2122 | 60.4065 | -0.082169 | 0.005676 | 0.065396 | 0.05968 | -0.0049047 | -0.010957 | -0.0040823 | -0.0008851 | 0.0036017 | 0.067481 | 0.050259 | -0.011747 | 0.02399 | -0.0010937 | 0.009155 | 60.228 | -61.203 | 60.4202 | -61.0199 | -61.4502 | -61.4044 | 0.054932 | 60.2234 | -61.2534 | 60.3241 | -61.2122 | -61.3312 | -61.3632 | 0.009155 | -0.17853 | 0.013733 | 0.19226 | -0.19226 | -0.23804 | -0.20142 | -0.24719 | -0.041199 | -0.18311 | -0.082397 | 0 | -0.15106 | -0.11902 | -0.10986 | -0.07782 | 0.18311 | 121.6232 | 0.041199 | 121.5775 | 121.431 | 121.4767 | 121.4401 | 121.4355 | -121.6095 | -121.6599 | 121.6324 | 121.5363 | 61.2213 | 61.2671
121.6406 | 121.8796 | -61.2167 | 60.3561 | -0.13557 | 0.005676 | 0.065183 | 0.060534 | -0.0021277 | -0.0083932 | -0.0047231 | 0.020477 | 0.0040289 | 0.067481 | 0.049618 | -0.01132 | 0.023349 | -0.0032299 | -0.064087 | 60.1547 | -61.2213 | 60.4248 | -61.0016 | -61.441 | -61.3907 | 0.018311 | 60.141 | -61.2625 | 60.3882 | -61.1755 | -61.2854 | -61.29 | -0.004577 | -0.20142 | 0.068665 | 0.21515 | -0.17395 | -0.2243 | -0.16937 | -0.21973 | -0.045776 | -0.21515 | 0.032044 | 0.041199 | -0.073242 | -0.068664 | -0.027466 | -0.022888 | 0.21973 | 121.6461 | 0.086975 | 121.6507 | 121.376 | 121.4035 | 121.3715 | 121.3577 | -121.5775 | -121.6187 | 121.6415 | 121.6049 | 61.1526 | 61.235
123.3906 | 121.9025 | -61.203 | 60.3653 | -0.11269 | 0.0063168 | 0.06796 | 0.061175 | -0.0027685 | -0.0088206 | -0.0013051 | 0.014374 | 0.0033881 | 0.066413 | 0.051541 | -0.011961 | 0.02164 | -0.00023931 | -0.068665 | 60.1501 | -61.2076 | 60.4523 | -60.997 | -61.4044 | -61.3861 | 0.050354 | 60.1593 | -61.2579 | 60.4111 | -61.1389 | -61.2534 | -61.2808 | -0.004578 | -0.21515 | 0.086976 | 0.20599 | -0.1831 | -0.20142 | -0.17853 | -0.19684 | -0.054932 | -0.20599 | 0.045777 | 0.064087 | -0.07782 | -0.050354 | -0.022888 | 0.004578 | 0.21057 | 121.6599 | 0.11902 | 121.669 | 121.3577 | 121.4172 | 121.3531 | 121.3623 | -121.5729 | -121.6232 | 121.6553 | 121.6141 | 61.1343 | 61.2534
125.0781 | 121.8796 | -61.2167 | 60.3424 | -0.089798 | 0.0065304 | 0.064756 | 0.061816 | -0.00084593 | -0.0073252 | -0.0030141 | -0.019196 | 0.0031745 | 0.067481 | 0.051755 | -0.010893 | 0.024844 | -0.0019483 | -0.09613 | 60.1547 | -61.2213 | 60.4385 | -61.0291 | -61.4365 | -61.3998 | 0.009155 | 60.1639 | -61.2442 | 60.3699 | -61.171 | -61.2991 | -61.3129 | -0.004577 | -0.18768 | 0.096131 | 0.18768 | -0.18311 | -0.21973 | -0.17853 | -0.21515 | -0.027466 | -0.17853 | 0.027466 | 0.045777 | -0.09613 | -0.082397 | -0.068664 | -0.054931 | 0.19226 | 121.6599 | 0.073243 | 121.6141 | 121.376 | 121.4081 | 121.3715 | 121.3806 | -121.5637 | -121.5866 | 121.6553 | 121.5866 | 61.1206 | 61.2259
126.8125 | 121.8887 | -61.1847 | 60.4111 | -0.044022 | 0.0048214 | 0.067105 | 0.060962 | -0.0023413 | -0.0081796 | -0.0066457 | -0.016144 | 0.0014655 | 0.065772 | 0.04855 | -0.012815 | 0.02164 | 0.00040169 | 0.064087 | 60.1959 | -61.1801 | 60.5347 | -60.9146 | -61.3495 | -61.322 | 0.16022 | 60.1913 | -61.203 | 60.4431 | -61.1114 | -61.2076 | -61.2534 | 0.004577 | -0.21515 | 0.1236 | 0.27008 | -0.13733 | -0.1648 | -0.14191 | -0.16937 | -0.018311 | -0.21973 | 0.032043 | 0.073242 | -0.068665 | -0.022889 | -0.050354 | -0.004578 | 0.2655 | 121.7148 | 0.091553 | 121.6461 | 121.376 | 121.3943 | 121.3806 | 121.376 | -121.5912 | -121.6141 | 121.7194 | 121.6278 | 61.2488 | 61.3449
128.5625 | 121.8201 | -61.2808 | 60.3333 | -0.051651 | 0.0069578 | 0.064542 | 0.06502 | -0.00041873 | -0.0081796 | -0.0042959 | -0.10159 | 0.0057379 | 0.064918 | 0.055173 | -0.011533 | 0.024844 | -0.0021619 | -0.09613 | 60.173 | -61.2625 | 60.4111 | -61.0519 | -61.4822 | -61.4731 | -0.009155 | 60.1547 | -61.2808 | 60.3241 | -61.2579 | -61.4182 | -61.4044 | 0.018311 | -0.16022 | 0.07782 | 0.22888 | -0.19226 | -0.20142 | -0.21057 | -0.21973 | 0 | -0.17853 | -0.009155 | 0.022888 | -0.1236 | -0.13733 | -0.1236 | -0.13733 | 0.21057 | 121.6736 | 0.022888 | 121.6049 | 121.4355 | 121.4355 | 121.4539 | 121.4355 | -121.5958 | -121.6141 | 121.6919 | 121.6049 | 61.1847 | 61.2717
130.3125 | 121.8887 | -61.2305 | 60.2921 | -0.15083 | 0.0067442 | 0.068601 | 0.060748 | 0.0017175 | -0.007966 | -0.0045095 | -0.019196 | 0.0046697 | 0.067268 | 0.053677 | -0.01132 | 0.022922 | -0.0045117 | -0.11902 | 60.0998 | -61.2442 | 60.4523 | -60.9741 | -61.4502 | -61.409 | 0.032043 | 60.0815 | -61.2762 | 60.3607 | -61.1801 | -61.3083 | -61.3083 | -0.013733 | -0.19226 | 0.16022 | 0.25635 | -0.17853 | -0.21973 | -0.16479 | -0.20599 | -0.045776 | -0.21057 | 0.068665 | 0.050354 | -0.07782 | -0.07782 | -0.032044 | -0.032044 | 0.27008 | 121.6965 | 0.09613 | 121.637 | 121.344 | 121.3577 | 121.3303 | 121.312 | -121.5363 | -121.5683 | 121.6827 | 121.5912 | 61.1114 | 61.2625
131.9844 | 121.875 | -61.1893 | 60.4156 | -0.097427 | 0.0024716 | 0.065396 | 0.060321 | -0.0031957 | -0.010316 | -0.0036551 | -0.019196 | 0.0036017 | 0.0662 | 0.049405 | -0.01132 | 0.021854 | -0.0019483 | 0.064087 | 60.1685 | -61.1893 | 60.5255 | -60.91 | -61.3358 | -61.3358 | 0.1831 | 60.1776 | -61.2076 | 60.4202 | -61.116 | -61.2396 | -61.2717 | 0 | -0.24719 | 0.10986 | 0.27924 | -0.14648 | -0.14648 | -0.14648 | -0.14648 | -0.018311 | -0.23804 | 0.004578 | 0.073242 | -0.082397 | -0.050354 | -0.064086 | -0.032043 | 0.27924 | 121.7148 | 0.091553 | 121.6278 | 121.3577 | 121.3852 | 121.3577 | 121.3669 | -121.6049 | -121.6232 | 121.7148 | 121.6095 | 61.2534 | 61.3724
133.7188 | 121.8292 | -61.2396 | 60.3699 | -0.05928 | 0.0043942 | 0.06561 | 0.062884 | -0.0017005 | -0.0092478 | -0.0038687 | -0.080231 | 0.0042425 | 0.065559 | 0.059018 | -0.013029 | 0.022708 | -0.0042981 | -0.041199 | 60.2097 | -61.2442 | 60.4019 | -61.0657 | -61.4594 | -61.4456 | 0.013733 | 60.2051 | -61.2534 | 60.3333 | -61.2259 | -61.3678 | -61.3678 | -0.004578 | -0.16022 | 0.032044 | 0.17395 | -0.20599 | -0.21973 | -0.20142 | -0.21515 | -0.013733 | -0.16479 | -0.036621 | 0.013733 | -0.12817 | -0.12817 | -0.11444 | -0.11444 | 0.17853 | 121.6461 | 0.027466 | 121.5866 | 121.4539 | 121.4584 | 121.4493 | 121.4447 | -121.6141 | -121.6232 | 121.6415 | 121.5729 | 61.1984 | 61.2534
135.3906 | 121.9345 | -61.2579 | 60.2692 | -0.18898 | 0.0067442 | 0.068601 | 0.063098 | -0.0021277 | -0.006898 | -0.0025869 | -0.052765 | 0.0040289 | 0.0662 | 0.049191 | -0.012174 | 0.025272 | -0.0023755 | -0.14648 | 60.1089 | -61.2808 | 60.4248 | -61.0245 | -61.4777 | -61.4182 | -0.022888 | 60.0861 | -61.3083 | 60.3745 | -61.1938 | -61.3129 | -61.2991 | -0.022888 | -0.16022 | 0.15564 | 0.23346 | -0.16022 | -0.21973 | -0.13733 | -0.19684 | -0.050354 | -0.1831 | 0.10529 | 0.064087 | -0.041198 | -0.054931 | 0.009156 | -0.004577 | 0.25635 | 121.7056 | 0.11444 | 121.6827 | 121.3898 | 121.3943 | 121.3669 | 121.344 | -121.55 | -121.5775 | 121.6827 | 121.6324 | 61.1115 | 61.235
137.1406 | 121.9208 | -61.2442 | 60.3149 | -0.15846 | 0.0080258 | 0.067746 | 0.061602 | 0.0010767 | -0.0081796 | 0.00061746 | -0.019196 | 0.0031745 | 0.0662 | 0.052395 | -0.011106 | 0.022708 | -0.0060071 | -0.13275 | 60.1044 | -61.2579 | 60.4477 | -60.9741 | -61.4548 | -61.409 | 0.032043 | 60.0906 | -61.2717 | 60.3882 | -61.1893 | -61.2946 | -61.3129 | -0.013733 | -0.21057 | 0.13275 | 0.27008 | -0.16479 | -0.21057 | -0.15106 | -0.19684 | -0.027465 | -0.2243 | 0.073243 | 0.054932 | -0.068664 | -0.050354 | -0.041199 | -0.022889 | 0.28381 | 121.7056 | 0.082397 | 121.6599 | 121.3623 | 121.3623 | 121.3486 | 121.3348 | -121.5729 | -121.5866 | 121.6919 | 121.6324 | 61.1115 | 61.2762
138.8281 | 121.8155 | -61.2762 | 60.3882 | -0.10506 | 0.0050352 | 0.063901 | 0.063311 | -0.0034095 | -0.0071116 | -0.0038687 | -0.068024 | 0.0031745 | 0.066841 | 0.0556 | -0.011747 | 0.023776 | -0.0055799 | -0.022888 | 60.2509 | -61.2305 | 60.4202 | -61.0474 | -61.4502 | -61.4456 | 0.018311 | 60.2509 | -61.2442 | 60.3195 | -61.2305 | -61.3724 | -61.377 | 0.045776 | -0.13733 | 0.032043 | 0.22888 | -0.16937 | -0.17395 | -0.21515 | -0.21973 | 0.032043 | -0.13733 | -0.068665 | 0.045776 | -0.10071 | -0.09613 | -0.13275 | -0.12817 | 0.18311 | 121.6507 | 0.013733 | 121.5637 | 121.4813 | 121.4951 | 121.5271 | 121.5271 | -121.6187 | -121.6324 | 121.6965 | 121.5958 | 61.2534 | 61.2946
140.5938 | 121.9254 | -61.1847 | 60.3607 | -0.082169 | 0.0052488 | 0.063687 | 0.060748 | -0.00020513 | -0.0073252 | -0.0023733 | 0.011322 | 0.0033881 | 0.066841 | 0.051327 | -0.01132 | 0.023135 | -0.0045117 | -0.045776 | 60.1639 | -61.2122 | 60.4523 | -60.9833 | -61.4182 | -61.3861 | 0.064087 | 60.1547 | -61.2625 | 60.4202 | -61.1343 | -61.2488 | -61.2717 | -0.027466 | -0.19684 | 0.091553 | 0.20142 | -0.20142 | -0.23346 | -0.17395 | -0.20599 | -0.07782 | -0.20599 | 0.059509 | 0.050354 | -0.086975 | -0.064087 | -0.009155 | 0.013733 | 0.22888 | 121.6644 | 0.12817 | 121.6827 | 121.376 | 121.4172 | 121.3486 | 121.3394 | -121.5729 | -121.6232 | 121.637 | 121.6049 | 61.1389 | 61.2488
142.3281 | 121.8887 | -61.2488 | 60.347 | -0.10506 | 0.0046078 | 0.065824 | 0.059893 | -0.0029821 | -0.0083932 | -0.0015189 | -0.0039367 | 0.0061651 | 0.067268 | 0.050046 | -0.011961 | 0.022708 | -0.0042981 | -0.086975 | 60.1547 | -61.2305 | 60.434 | -60.997 | -61.4319 | -61.3907 | 0.018311 | 60.1593 | -61.2762 | 60.3561 | -61.1847 | -61.3129 | -61.3083 | 0.01831 | -0.19226 | 0.086975 | 0.25177 | -0.14191 | -0.18311 | -0.16022 | -0.20142 | -0.027466 | -0.18768 | 0.009155 | 0.064087 | -0.05951 | -0.064087 | -0.032044 | -0.036621 | 0.23346 | 121.6644 | 0.091553 | 121.6324 | 121.3852 | 121.4355 | 121.4035 | 121.4081 | -121.5775 | -121.6232 | 121.6827 | 121.6049 | 61.1618 | 61.2671
144.0156 | 121.9208 | -61.1938 | 60.3928 | -0.089798 | 0.0063168 | 0.064328 | 0.060748 | -0.0036231 | -0.0071116 | -0.0028005 | -0.01004 | 0.0018927 | 0.067481 | 0.05795 | -0.013242 | 0.023349 | -0.0042981 | 0.059509 | 60.173 | -61.1755 | 60.5576 | -60.8688 | -61.3037 | -61.2946 | 0.20599 | 60.1913 | -61.203 | 60.4614 | -61.084 | -61.2122 | -61.235 | 0.018311 | -0.21973 | 0.16479 | 0.32501 | -0.10071 | -0.10986 | -0.11902 | -0.12817 | -0.009155 | -0.20142 | 0.068665 | 0.10986 | -0.041198 | -0.01831 | -0.032043 | -0.009155 | 0.3067 | 121.7331 | 0.11902 | 121.6644 | 121.3486 | 121.3943 | 121.3669 | 121.3852 | -121.5683 | -121.5958 | 121.7514 | 121.6553 | 61.2534 | 61.3998
145.7656 | 121.8933 | -61.2213 | 60.3287 | -0.082169 | 0.0058896 | 0.064969 | 0.059893 | -0.0053321 | -0.0081796 | -0.0032277 | -0.028351 | 0.0029607 | 0.0662 | 0.054318 | -0.012602 | 0.023776 | -0.0064343 | -0.068665 | 60.1868 | -61.235 | 60.434 | -61.0016 | -61.4227 | -61.3998 | 0.027466 | 60.1318 | -61.2534 | 60.3928 | -61.1572 | -61.2717 | -61.2808 | -0.013733 | -0.14191 | 0.10529 | 0.21973 | -0.17853 | -0.20142 | -0.1648 | -0.18768 | -0.032044 | -0.19684 | 0.064087 | 0.064086 | -0.05951 | -0.050354 | -0.027466 | -0.01831 | 0.23346 | 121.669 | 0.09613 | 121.6461 | 121.4218 | 121.3852 | 121.4081 | 121.3531 | -121.5637 | -121.582 | 121.6553 | 121.6141 | 61.1526 | 61.2488
147.4375 | 121.9345 | -61.1847 | 60.3195 | -0.06691 | 0.0054624 | 0.065824 | 0.05968 | -0.0034095 | -0.0094614 | -0.00087794 | -0.028351 | 0.0036017 | 0.067268 | 0.055173 | -0.011961 | 0.02164 | -0.0034435 | -0.018311 | 60.1868 | -61.2167 | 60.4797 | -60.9467 | -61.3586 | -61.3312 | 0.12817 | 60.173 | -61.2305 | 60.4477 | -61.084 | -61.1984 | -61.2305 | -0.032044 | -0.13275 | 0.16022 | 0.23804 | -0.14648 | -0.17395 | -0.11444 | -0.14191 | -0.045777 | -0.14648 | 0.12817 | 0.10071 | -0.045777 | -0.013733 | 0 | 0.032044 | 0.27008 | 121.6965 | 0.14648 | 121.6782 | 121.4035 | 121.4035 | 121.3715 | 121.3577 | -121.5363 | -121.55 | 121.6644 | 121.6324 | 61.1664 | 61.3129
149.1719 | 121.8704 | -61.2259 | 60.3287 | -0.12794 | 0.0065304 | 0.066678 | 0.060321 | -0.0031957 | -0.006898 | 0.00040366 | -0.046661 | 0.0036017 | 0.067695 | 0.058163 | -0.012602 | 0.025058 | -0.0066479 | -0.10986 | 60.1044 | -61.2625 | 60.4523 | -60.9879 | -61.4365 | -61.3907 | 0.018311 | 60.1227 | -61.2671 | 60.3745 | -61.203 | -61.3037 | -61.3129 | -0.036621 | -0.2243 | 0.1236 | 0.23804 | -0.1648 | -0.21057 | -0.12817 | -0.17395 | -0.041199 | -0.20599 | 0.045777 | 0.022888 | -0.086975 | -0.07782 | -0.045776 | -0.036621 | 0.27466 | 121.7148 | 0.064087 | 121.6415 | 121.3669 | 121.3898 | 121.3303 | 121.3486 | -121.5912 | -121.5958 | 121.6782 | 121.6003 | 61.116 | 61.2442
150.9375 | 121.7926 | -61.3266 | 60.3241 | -0.074539 | 0.0078122 | 0.066037 | 0.064593 | -0.0025549 | -0.0075388 | 0.00019006 | -0.12296 | 0.0040289 | 0.064704 | 0.056454 | -0.010252 | 0.025912 | -0.0045117 | -0.17853 | 60.1456 | -61.322 | 60.3195 | -61.171 | -61.5967 | -61.5601 | -0.16937 | 60.1273 | -61.3403 | 60.2325 | -61.3861 | -61.4914 | -61.4731 | 0.004578 | -0.17853 | -0.004578 | 0.15564 | -0.23346 | -0.27008 | -0.23804 | -0.27466 | -0.013733 | -0.19684 | -0.091553 | -0.059509 | -0.14648 | -0.16479 | -0.13275 | -0.15106 | 0.15106 | 121.6415 | -0.045776 | 121.5729 | 121.4676 | 121.4676 | 121.4722 | 121.4539 | -121.6461 | -121.6644 | 121.6461 | 121.5591 | 61.1481 | 61.1572
152.6875 | 121.8155 | -61.2854 | 60.3058 | -0.1432 | 0.0052488 | 0.067105 | 0.065875 | -0.0034095 | -0.0094614 | -0.0021597 | -0.12296 | 0.0031745 | 0.067695 | 0.059445 | -0.011747 | 0.024204 | -0.0034435 | -0.10071 | 60.1639 | -61.2717 | 60.4156 | -61.0428 | -61.496 | -61.4731 | -0.041199 | 60.1501 | -61.3129 | 60.3012 | -61.2808 | -61.4273 | -61.4136 | 0.013733 | -0.14191 | 0.10986 | 0.24261 | -0.18768 | -0.21057 | -0.20142 | -0.22431 | -0.027466 | -0.15564 | -0.004578 | 0.004577 | -0.12817 | -0.14191 | -0.10071 | -0.11444 | 0.22888 | 121.6873 | 0.032043 | 121.6141 | 121.4355 | 121.463 | 121.4493 | 121.4355 | -121.5775 | -121.6187 | 121.701 | 121.5866 | 61.1847 | 61.2442
154.4219 | 121.7926 | -61.3037 | 60.3012 | -0.028763 | 0.005676 | 0.066251 | 0.062243 | -0.0010595 | -0.0066844 | -0.0032277 | -0.11075 | 0.0053107 | 0.066627 | 0.050473 | -0.013883 | 0.025699 | -0.0049389 | -0.11902 | 60.1593 | -61.2579 | 60.3973 | -61.0703 | -61.5234 | -61.496 | -0.054932 | 60.1318 | -61.3266 | 60.2737 | -61.3174 | -61.4456 | -61.4365 | 0.045776 | -0.14191 | 0.096131 | 0.23346 | -0.19226 | -0.21973 | -0.23804 | -0.2655 | -0.022888 | -0.16937 | -0.027465 | -0.013733 | -0.13275 | -0.14191 | -0.10986 | -0.11902 | 0.18768 | 121.6553 | 0.009155 | 121.6003 | 121.4172 | 121.4584 | 121.463 | 121.4355 | -121.5591 | -121.6278 | 121.7011 | 121.5775 | 61.1847 | 61.2488
156.125 | 121.9025 | -61.203 | 60.3607 | -0.089798 | 0.0037534 | 0.065183 | 0.056689 | 0.0040675 | -0.011811 | -0.0023733 | 0.0021667 | 0.0031745 | 0.064277 | 0.047482 | -0.011533 | 0.023349 | -0.0019483 | -0.032043 | 60.1456 | -61.1984 | 60.4843 | -60.9467 | -61.3724 | -61.322 | 0.12817 | 60.1639 | -61.235 | 60.4523 | -61.0794 | -61.1984 | -61.2442 | 0.004578 | -0.21515 | 0.1236 | 0.25635 | -0.11902 | -0.16937 | -0.1236 | -0.17395 | -0.032043 | -0.19684 | 0.091553 | 0.1236 | -0.041199 | 0.004578 | -0.009156 | 0.036621 | 0.25177 | 121.6827 | 0.15564 | 121.6873 | 121.344 | 121.3989 | 121.3486 | 121.3669 | -121.5591 | -121.5958 | 121.6873 | 121.6553 | 61.171 | 61.3312
157.8125 | 121.8796 | -61.2213 | 60.3241 | -0.12032 | 0.0041806 | 0.067746 | 0.061389 | 0.0023585 | -0.0092478 | -0.0045095 | -0.034454 | 0.0048833 | 0.065772 | 0.062649 | -0.010465 | 0.02399 | -0.0034435 | -0.11902 | 60.1227 | -61.2442 | 60.434 | -60.997 | -61.4548 | -61.3998 | 0.050354 | 60.0815 | -61.2625 | 60.3836 | -61.1801 | -61.3174 | -61.3129 | -0.022889 | -0.20142 | 0.10986 | 0.2243 | -0.17853 | -0.23346 | -0.15564 | -0.21057 | -0.041199 | -0.24262 | 0.059509 | 0.041198 | -0.091553 | -0.096131 | -0.050354 | -0.054932 | 0.24719 | 121.6782 | 0.082397 | 121.6461 | 121.3669 | 121.344 | 121.344 | 121.3028 | -121.5683 | -121.5866 | 121.6553 | 121.6049 | 61.1023 | 61.2717
159.5469 | 121.8063 | -61.235 | 60.3836 | -0.074539 | 0.0061032 | 0.064115 | 0.062243 | 0.0015039 | -0.0092478 | -0.0040823 | -0.055817 | 0.0044561 | 0.067909 | 0.056668 | -0.011533 | 0.025485 | -0.00066651 | -0.032043 | 60.2325 | -61.2305 | 60.3928 | -61.0474 | -61.4502 | -61.4365 | 0.004578 | 60.2234 | -61.2488 | 60.3424 | -61.2396 | -61.3678 | -61.3724 | 0.004577 | -0.15106 | 0.009155 | 0.18768 | -0.20142 | -0.21515 | -0.20599 | -0.21973 | -0.013733 | -0.16022 | -0.041199 | -0.004578 | -0.13733 | -0.13275 | -0.1236 | -0.11902 | 0.18311 | 121.6232 | 0.009155 | 121.5912 | 121.463 | 121.4722 | 121.4676 | 121.4584 | -121.6141 | -121.6324 | 121.6278 | 121.5775 | 61.203 | 61.2396
161.3125 | 121.907 | -61.203 | 60.379 | -0.10506 | 0.0048214 | 0.06796 | 0.059893 | -0.0061865 | -0.010316 | -0.0036551 | 0.0021667 | 0.0036017 | 0.067909 | 0.051114 | -0.010679 | 0.023349 | -0.0032299 | -0.054932 | 60.1547 | -61.235 | 60.4431 | -60.9879 | -61.4136 | -61.3815 | 0.054932 | 60.1639 | -61.2488 | 60.4385 | -61.1252 | -61.2213 | -61.2625 | -0.032043 | -0.2243 | 0.064087 | 0.21515 | -0.17853 | -0.21057 | -0.14649 | -0.17853 | -0.045776 | -0.21515 | 0.05951 | 0.07782 | -0.059509 | -0.01831 | -0.013733 | 0.027466 | 0.24719 | 121.6782 | 0.1236 | 121.6873 | 121.3898 | 121.4127 | 121.3577 | 121.3669 | -121.6141 | -121.6278 | 121.6461 | 121.6415 | 61.1481 | 61.2579
163 | 121.7743 | -61.3174 | 60.2875 | -0.074539 | 0.0067442 | 0.067533 | 0.065234 | -0.0017005 | -0.006898 | -2.3544e-05 | -0.11685 | 0.0053107 | 0.067054 | 0.062008 | -0.011747 | 0.025485 | -0.0036573 | -0.18768 | 60.1501 | -61.2991 | 60.3104 | -61.1618 | -61.6013 | -61.5555 | -0.16937 | 60.1456 | -61.3129 | 60.2509 | -61.3358 | -61.4914 | -61.4548 | 0.018311 | -0.13733 | 0.022888 | 0.15564 | -0.23804 | -0.28381 | -0.25635 | -0.30212 | 0.004578 | -0.14191 | -0.036622 | -0.01831 | -0.13733 | -0.17395 | -0.14191 | -0.17853 | 0.13733 | 121.6095 | -0.022888 | 121.5637 | 121.4493 | 121.4584 | 121.4676 | 121.463 | -121.5866 | -121.6003 | 121.6278 | 121.5683 | 61.1298 | 61.1481
164.75 | 121.9528 | -61.1755 | 60.3836 | -0.082169 | 0.0048214 | 0.064542 | 0.059253 | -0.0010595 | -0.0092478 | -0.0034415 | -0.013092 | 0.0036017 | 0.066627 | 0.052823 | -0.010679 | 0.02399 | -0.0060071 | 0.032043 | 60.1593 | -61.1984 | 60.5255 | -60.878 | -61.3358 | -61.2946 | 0.18768 | 60.173 | -61.2213 | 60.4889 | -61.0428 | -61.1618 | -61.2122 | -0.022888 | -0.2243 | 0.14191 | 0.29755 | -0.11902 | -0.16022 | -0.096131 | -0.13733 | -0.045776 | -0.21057 | 0.10529 | 0.13275 | -0.036621 | 0.013733 | 0.009155 | 0.059509 | 0.32043 | 121.7239 | 0.17853 | 121.7102 | 121.3577 | 121.3943 | 121.3348 | 121.3486 | -121.582 | -121.6049 | 121.701 | 121.6644 | 61.2076 | 61.3632
166.4844 | 121.875 | -61.2305 | 60.3561 | -0.089798 | 0.0082394 | 0.06561 | 0.06203 | -0.00041873 | -0.0081796 | -0.0032277 | 0.0021667 | 0.0031745 | 0.065986 | 0.053464 | -0.010893 | 0.023349 | -0.0060071 | -0.09613 | 60.1456 | -61.2122 | 60.4477 | -61.0153 | -61.4685 | -61.3998 | -0.004578 | 60.1501 | -61.2762 | 60.3745 | -61.1801 | -61.3083 | -61.3174 | 0.018311 | -0.21057 | 0.091553 | 0.21515 | -0.16937 | -0.23804 | -0.18768 | -0.25635 | -0.045776 | -0.20599 | 0.018311 | 0.050354 | -0.086975 | -0.07782 | -0.041199 | -0.032044 | 0.19684 | 121.6599 | 0.09613 | 121.6507 | 121.3577 | 121.4264 | 121.376 | 121.3806 | -121.5683 | -121.6324 | 121.6782 | 121.6049 | 61.1343 | 61.2259
168.2188 | 121.8933 | -61.235 | 60.3378 | -0.1432 | 0.0050352 | 0.066251 | 0.061175 | -0.0012731 | -0.0094614 | -0.0025869 | -0.040558 | 0.0048833 | 0.065986 | 0.044705 | -0.012174 | 0.021854 | -0.0057935 | -0.10071 | 60.1273 | -61.2305 | 60.4385 | -60.9879 | -61.4502 | -61.409 | 0.013733 | 60.1273 | -61.2396 | 60.3836 | -61.1938 | -61.3083 | -61.3083 | 0.004577 | -0.21057 | 0.10071 | 0.24719 | -0.17395 | -0.21515 | -0.17853 | -0.21973 | -0.004578 | -0.21057 | 0.045776 | 0.041198 | -0.073243 | -0.073243 | -0.068665 | -0.068665 | 0.24262 | 121.669 | 0.045776 | 121.6232 | 121.3577 | 121.3669 | 121.3623 | 121.3623 | -121.5683 | -121.5775 | 121.6736 | 121.6187 | 61.1343 | 61.2488
169.9062 | 121.7697 | -61.3174 | 60.3012 | -0.11269 | 0.0078122 | 0.067105 | 0.064593 | 0.0040675 | -0.0075388 | -0.0013051 | -0.13821 | 0.0040289 | 0.066627 | 0.054959 | -0.01132 | 0.025485 | -0.0019483 | -0.19684 | 60.1364 | -61.3129 | 60.3012 | -61.1755 | -61.5829 | -61.5417 | -0.18768 | 60.1364 | -61.3449 | 60.2371 | -61.3541 | -61.4868 | -61.4548 | 0.004578 | -0.16479 | 0 | 0.14191 | -0.2243 | -0.2655 | -0.22888 | -0.27008 | -0.027466 | -0.16479 | -0.064086 | -0.036621 | -0.13733 | -0.16937 | -0.10986 | -0.14191 | 0.13733 | 121.6141 | -0.009155 | 121.582 | 121.4493 | 121.4813 | 121.4539 | 121.4539 | -121.6141 | -121.6461 | 121.6187 | 121.5546 | 61.1206 | 61.1298
171.6562 | 121.9208 | -61.2946 | 60.2417 | -0.13557 | 0.0061032 | 0.067105 | 0.061816 | -0.0038367 | -0.006898 | -0.00045074 | -0.049713 | 0.0036017 | 0.065345 | 0.059231 | -0.011106 | 0.025485 | -0.0045117 | -0.13733 | 60.0952 | -61.2854 | 60.4202 | -61.0153 | -61.4731 | -61.4319 | -0.027466 | 60.0723 | -61.3129 | 60.3653 | -61.2076 | -61.3449 | -61.3083 | 0.009156 | -0.14648 | 0.17853 | 0.27924 | -0.13733 | -0.17853 | -0.14648 | -0.18768 | -0.01831 | -0.16937 | 0.1236 | 0.086975 | -0.013733 | -0.050354 | 0.004577 | -0.032044 | 0.27008 | 121.7056 | 0.10529 | 121.6782 | 121.3806 | 121.3852 | 121.3898 | 121.3669 | -121.5271 | -121.5546 | 121.7148 | 121.6599 | 61.1572 | 61.2671
173.4062 | 121.8796 | -61.2259 | 60.3516 | -0.12032 | 0.003967 | 0.063047 | 0.061816 | -0.0042639 | -0.0077524 | -0.00045074 | -0.031403 | 0.0040289 | 0.065559 | 0.05325 | -0.0093972 | 0.025058 | -0.0072889 | -0.10986 | 60.1547 | -61.2396 | 60.4385 | -61.0062 | -61.4502 | -61.3907 | 0.009155 | 60.1639 | -61.2579 | 60.379 | -61.1938 | -61.3037 | -61.3083 | -0.013733 | -0.19684 | 0.086976 | 0.21973 | -0.1648 | -0.2243 | -0.15106 | -0.21057 | -0.032044 | -0.18768 | 0.027466 | 0.032043 | -0.082398 | -0.07782 | -0.050354 | -0.045776 | 0.23346 | 121.6782 | 0.064087 | 121.637 | 121.3943 | 121.4218 | 121.3806 | 121.3898 | -121.5912 | -121.6095 | 121.6644 | 121.6049 | 61.116 | 61.235
175.1562 | 121.8658 | -61.2122 | 60.4019 | -0.05928 | 0.0071714 | 0.066251 | 0.05968 | -0.0059729 | -0.010957 | -0.00087794 | -0.058869 | 0.0061651 | 0.065559 | 0.053464 | -0.011106 | 0.024204 | -0.0045117 | 0.050354 | 60.1822 | -61.1755 | 60.5209 | -60.9146 | -61.3449 | -61.3174 | 0.16022 | 60.2005 | -61.2213 | 60.4111 | -61.1343 | -61.2762 | -61.2946 | 0.036621 | -0.21973 | 0.11902 | 0.29755 | -0.10529 | -0.13275 | -0.14191 | -0.16937 | -0.009155 | -0.20142 | 0.009155 | 0.07782 | -0.082398 | -0.064087 | -0.073243 | -0.054932 | 0.26093 | 121.6965 | 0.086975 | 121.6324 | 121.3577 | 121.4218 | 121.3943 | 121.4127 | -121.5775 | -121.6232 | 121.7331 | 121.6232 | 61.2625 | 61.3724
176.8281 | 121.9208 | -61.2442 | 60.3012 | -0.11269 | 0.0075986 | 0.066678 | 0.062457 | 0.0015039 | -0.0060434 | -0.0015189 | -0.064972 | 0.0029607 | 0.062782 | 0.057522 | -0.010893 | 0.024844 | 0.00082889 | -0.11902 | 60.0906 | -61.2717 | 60.4477 | -61.0016 | -61.4685 | -61.4182 | 0.004578 | 60.0632 | -61.2991 | 60.3973 | -61.1755 | -61.3129 | -61.2946 | -0.027465 | -0.21057 | 0.14648 | 0.24262 | -0.17395 | -0.2243 | -0.14648 | -0.19684 | -0.054931 | -0.23804 | 0.096131 | 0.068665 | -0.050354 | -0.068664 | 0.004577 | -0.013733 | 0.27008 | 121.7194 | 0.1236 | 121.6965 | 121.3623 | 121.3623 | 121.3348 | 121.3074 | -121.5729 | -121.6003 | 121.6919 | 121.6415 | 61.1252 | 61.2488
178.5625 | 121.9116 | -61.2671 | 60.2829 | -0.16609 | 0.0058896 | 0.068601 | 0.064166 | -0.0036231 | -0.0058298 | -0.0021597 | -0.098541 | 0.0044561 | 0.064491 | 0.054959 | -0.013883 | 0.024417 | -0.0057935 | -0.20142 | 60.1227 | -61.322 | 60.3699 | -61.084 | -61.5326 | -61.5051 | -0.068665 | 60.0861 | -61.3358 | 60.3561 | -61.2076 | -61.3403 | -61.3266 | -0.054931 | -0.16022 | 0.086975 | 0.18311 | -0.23804 | -0.2655 | -0.18311 | -0.21057 | -0.068664 | -0.19684 | 0.073242 | 0.059509 | -0.059509 | -0.073242 | 0.009155 | -0.004578 | 0.23804 | 121.6919 | 0.12817 | 121.6919 | 121.4447 | 121.4218 | 121.3898 | 121.3531 | -121.6049 | -121.6187 | 121.637 | 121.6232 | 61.0657 | 61.1984
180.2344 | 121.9162 | -61.1847 | 60.3745 | -0.12032 | 0.003967 | 0.066251 | 0.060748 | -0.0034095 | -0.01117 | -0.00023714 | -0.019196 | 0.0029607 | 0.065132 | 0.049832 | -0.01367 | 0.022495 | -0.0070751 | 0.059509 | 60.2005 | -61.1801 | 60.5438 | -60.8917 | -61.3266 | -61.3174 | 0.16479 | 60.1822 | -61.2122 | 60.4294 | -61.0886 | -61.2167 | -61.2442 | 0.004577 | -0.17395 | 0.16937 | 0.29297 | -0.13275 | -0.14191 | -0.13733 | -0.14648 | -0.027466 | -0.19226 | 0.054931 | 0.09613 | -0.05951 | -0.032044 | -0.032044 | -0.004578 | 0.28839 | 121.7239 | 0.1236 | 121.6415 | 121.3806 | 121.3943 | 121.3852 | 121.3669 | -121.5546 | -121.5866 | 121.7285 | 121.6141 | 61.2442 | 61.3495
181.9844 | 121.8384 | -61.2854 | 60.3653 | -0.036392 | 0.0061032 | 0.064756 | 0.064166 | -0.0012731 | -0.0083932 | -0.0015189 | -0.089386 | 0.0033881 | 0.067054 | 0.061368 | -0.014524 | 0.02399 | -0.0070751 | -0.041199 | 60.2005 | -61.2305 | 60.4019 | -61.0474 | -61.4639 | -61.4548 | 0.013733 | 60.1776 | -61.2625 | 60.3424 | -61.2213 | -61.3586 | -61.3403 | 0.054931 | -0.1648 | 0.036622 | 0.23804 | -0.16937 | -0.17853 | -0.2243 | -0.23346 | 0.022888 | -0.18768 | -0.022888 | 0.064087 | -0.054932 | -0.073243 | -0.07782 | -0.096131 | 0.18311 | 121.6324 | 0.041199 | 121.6049 | 121.431 | 121.4401 | 121.4859 | 121.463 | -121.5958 | -121.6278 | 121.6873 | 121.6278 | 61.2442 | 61.2991
183.7188 | 121.9482 | -61.1893 | 60.3516 | -0.12794 | 0.0046078 | 0.066251 | 0.058825 | -0.00063233 | -0.0090342 | -0.0032277 | -0.01004 | 0.0031745 | 0.067268 | 0.0462 | -0.00897 | 0.023776 | -0.0057935 | 0.036621 | 60.1868 | -61.1755 | 60.5255 | -60.8963 | -61.3266 | -61.3083 | 0.20599 | 60.173 | -61.2259 | 60.466 | -61.0657 | -61.1893 | -61.2305 | 0.013733 | -0.16479 | 0.17395 | 0.29297 | -0.11902 | -0.13733 | -0.13275 | -0.15106 | -0.036621 | -0.17853 | 0.11444 | 0.1236 | -0.041199 | 0 | -0.004578 | 0.036621 | 0.27924 | 121.701 | 0.16022 | 121.6919 | 121.3623 | 121.3989 | 121.376 | 121.3623 | -121.5271 | -121.5775 | 121.7148 | 121.6553 | 61.2259 | 61.3953
185.4531 | 121.788 | -61.2305 | 60.4477 | -0.082169 | 0.0041806 | 0.064328 | 0.061175 | -0.0029821 | -0.006898 | -0.00087794 | -0.077179 | 0.0072333 | 0.067909 | 0.054745 | -0.011747 | 0.024204 | -0.0038709 | -0.027466 | 60.2142 | -61.2122 | 60.4202 | -61.0382 | -61.441 | -61.4319 | 0.045776 | 60.228 | -61.2213 | 60.3424 | -61.2076 | -61.3403 | -61.3586 | 0.018311 | -0.23346 | -0.027466 | 0.19226 | -0.20142 | -0.21057 | -0.21973 | -0.22888 | 0.009156 | -0.21973 | -0.10529 | 0.022888 | -0.12817 | -0.10986 | -0.13733 | -0.11902 | 0.17395 | 121.6324 | 0.013732 | 121.5637 | 121.4264 | 121.4493 | 121.4447 | 121.4584 | -121.6599 | -121.669 | 121.6507 | 121.5729 | 61.203 | 61.2762
187.1406 | 121.8796 | -61.2305 | 60.3195 | -0.089798 | 0.0033262 | 0.067746 | 0.062671 | -0.00020513 | -0.010102 | -0.0017325 | -0.037506 | 0.0042425 | 0.066627 | 0.053464 | -0.0096108 | 0.023563 | -0.0055799 | -0.10529 | 60.1364 | -61.2442 | 60.434 | -60.9924 | -61.4365 | -61.3953 | 0.009155 | 60.1501 | -61.2854 | 60.3745 | -61.1938 | -61.2946 | -61.3266 | -0.013733 | -0.1831 | 0.11444 | 0.23804 | -0.16479 | -0.20599 | -0.15106 | -0.19226 | -0.054931 | -0.16937 | 0.054932 | 0.036621 | -0.09613 | -0.064087 | -0.041199 | -0.009156 | 0.25177 | 121.6782 | 0.091552 | 121.6599 | 121.3806 | 121.4355 | 121.3669 | 121.3806 | -121.5637 | -121.6049 | 121.6644 | 121.6049 | 61.1252 | 61.2396
188.8906 | 121.8887 | -61.2305 | 60.3287 | -0.12032 | 0.0063168 | 0.066037 | 0.061602 | -0.0061865 | -0.007966 | -0.0032277 | -0.031403 | 0.0055243 | 0.06385 | 0.054745 | -0.012174 | 0.024417 | 0.00061529 | -0.11444 | 60.1135 | -61.2442 | 60.434 | -60.9833 | -61.4456 | -61.3861 | 0.018311 | 60.1456 | -61.2671 | 60.379 | -61.1893 | -61.2946 | -61.2991 | -0.013733 | -0.21515 | 0.10529 | 0.24719 | -0.15564 | -0.21515 | -0.14191 | -0.20142 | -0.036621 | -0.1831 | 0.050354 | 0.041199 | -0.068664 | -0.064087 | -0.032043 | -0.027466 | 0.26093 | 121.6782 | 0.07782 | 121.6461 | 121.3577 | 121.4127 | 121.344 | 121.376 | -121.5729 | -121.5958 | 121.6644 | 121.6095 | 61.116 | 61.2488
190.5781 | 121.8109 | -61.2488 | 60.3973 | -0.044022 | 0.0063168 | 0.064328 | 0.06438 | -0.00041873 | -0.009675 | -0.00066434 | -0.092438 | 0.0068059 | 0.067909 | 0.057309 | -0.010679 | 0.02399 | -0.0036573 | -0.032043 | 60.2234 | -61.2305 | 60.4019 | -61.0519 | -61.4685 | -61.4639 | 0.018311 | 60.2142 | -61.2808 | 60.3333 | -61.2213 | -61.3495 | -61.3586 | 0.01831 | -0.17395 | 0.004578 | 0.19684 | -0.21515 | -0.21973 | -0.23346 | -0.23804 | -0.032044 | -0.18311 | -0.064087 | 0.027466 | -0.10986 | -0.10071 | -0.07782 | -0.068664 | 0.17853 | 121.6324 | 0.05951 | 121.6141 | 121.4539 | 121.4951 | 121.4722 | 121.463 | -121.6278 | -121.6782 | 121.6507 | 121.582 | 61.2167 | 61.2671
192.3281 | 121.8018 | -61.2259 | 60.4019 | -0.05928 | 0.0048214 | 0.063047 | 0.062457 | -0.0019141 | -0.01117 | -0.0015189 | -0.06192 | 0.0040289 | 0.068977 | 0.058804 | -0.013242 | 0.023135 | -0.0053661 | -0.022888 | 60.2417 | -61.2305 | 60.4019 | -61.0382 | -61.4594 | -61.441 | 0.022888 | 60.2142 | -61.2534 | 60.3333 | -61.2396 | -61.3632 | -61.3953 | -0.004578 | -0.16022 | 0 | 0.18768 | -0.21515 | -0.23346 | -0.21057 | -0.22888 | -0.027466 | -0.18768 | -0.068665 | -0.013733 | -0.16937 | -0.13733 | -0.14191 | -0.10986 | 0.19226 | 121.6324 | 0.013733 | 121.5866 | 121.4722 | 121.4676 | 121.4676 | 121.4401 | -121.6324 | -121.6553 | 121.6278 | 121.5591 | 61.203 | 61.2488
194.0781 | 121.8979 | -61.2076 | 60.3653 | -0.12794 | 0.003967 | 0.065183 | 0.060107 | 0.0032129 | -0.0090342 | -0.00087794 | -0.0039367 | 0.0036017 | 0.067695 | 0.056454 | -0.014524 | 0.022067 | -0.0057935 | -0.064087 | 60.1593 | -61.2259 | 60.4431 | -60.9924 | -61.4319 | -61.3998 | 0.045776 | 60.1776 | -61.2762 | 60.3836 | -61.1481 | -61.2671 | -61.29 | -0.01831 | -0.20599 | 0.07782 | 0.21515 | -0.19226 | -0.2243 | -0.17395 | -0.20599 | -0.068664 | -0.18768 | 0.018311 | 0.05951 | -0.082397 | -0.059509 | -0.013733 | 0.009155 | 0.23346 | 121.669 | 0.12817 | 121.6599 | 121.3852 | 121.4539 | 121.3669 | 121.3852 | -121.5912 | -121.6415 | 121.6507 | 121.5912 | 61.1435 | 61.2534
195.8281 | 121.8063 | -61.2991 | 60.3287 | -0.074539 | 0.005676 | 0.067105 | 0.064593 | -0.0021277 | -0.0077524 | -0.0025869 | -0.1199 | 0.0065923 | 0.067268 | 0.053036 | -0.011533 | 0.025912 | -0.0057935 | -0.19226 | 60.1593 | -61.322 | 60.2966 | -61.203 | -61.6241 | -61.5829 | -0.17395 | 60.141 | -61.3358 | 60.2646 | -61.3632 | -61.4777 | -61.4594 | -0.022888 | -0.16937 | -0.032043 | 0.09613 | -0.28381 | -0.32501 | -0.26093 | -0.30213 | -0.036621 | -0.18768 | -0.064087 | -0.064087 | -0.16022 | -0.17853 | -0.1236 | -0.14191 | 0.11902 | 121.6187 | -0.027466 | 121.6003 | 121.4813 | 121.4767 | 121.4584 | 121.4401 | -121.6507 | -121.6644 | 121.5958 | 121.5637 | 61.1069 | 61.1252
197.5625 | 121.875 | -61.2122 | 60.3195 | -0.10506 | 0.0058896 | 0.067105 | 0.060107 | -0.0055457 | -0.007966 | -0.0021597 | -0.019196 | 0.0031745 | 0.068122 | 0.061795 | -0.01132 | 0.022495 | -0.0049389 | -0.09613 | 60.1685 | -61.2396 | 60.4431 | -61.0107 | -61.441 | -61.4182 | 0.004578 | 60.1364 | -61.2808 | 60.3882 | -61.1847 | -61.29 | -61.3083 | -0.027466 | -0.15106 | 0.1236 | 0.20142 | -0.20599 | -0.22888 | -0.17853 | -0.20142 | -0.068665 | -0.1831 | 0.068665 | 0.027466 | -0.096131 | -0.07782 | -0.027466 | -0.009155 | 0.22888 | 121.6827 | 0.096131 | 121.669 | 121.4081 | 121.4172 | 121.3806 | 121.3486 | -121.5591 | -121.6003 | 121.6553 | 121.6003 | 61.116 | 61.2167
199.2344 | 121.8292 | -61.2122 | 60.4065 | -0.10506 | 0.0035398 | 0.066464 | 0.061816 | 0.0032129 | -0.01053 | -0.00066434 | -0.025299 | 0.0055243 | 0.0662 | 0.059018 | -0.010465 | 0.024417 | -0.0023755 | 0.059509 | 60.1913 | -61.1801 | 60.5118 | -60.9375 | -61.3632 | -61.3541 | 0.1236 | 60.2234 | -61.2305 | 60.3653 | -61.1618 | -61.2946 | -61.3312 | 0.032043 | -0.21515 | 0.10529 | 0.27466 | -0.14191 | -0.15106 | -0.17395 | -0.1831 | -0.018311 | -0.18311 | -0.041199 | 0.050354 | -0.11902 | -0.082398 | -0.10071 | -0.064087 | 0.24262 | 121.6919 | 0.068665 | 121.5958 | 121.3715 | 121.4539 | 121.4035 | 121.4355 | -121.5866 | -121.637 | 121.7239 | 121.5775 | 61.2717 | 61.3358
200.9844 | 121.8384 | -61.2625 | 60.3745 | -0.097427 | 0.0031126 | 0.062619 | 0.063525 | -0.0034095 | -0.007966 | -0.0010915 | -0.068024 | 0.0021063 | 0.067481 | 0.054532 | -0.010465 | 0.024204 | -0.0053661 | -0.036621 | 60.2509 | -61.2488 | 60.3928 | -61.0428 | -61.4594 | -61.441 | -0.004578 | 60.2097 | -61.2488 | 60.3424 | -61.2167 | -61.3678 | -61.3586 | 0.013733 | -0.1236 | 0.01831 | 0.21973 | -0.17853 | -0.19684 | -0.19226 | -0.21057 | 0.013733 | -0.16479 | -0.032044 | 0.045776 | -0.096131 | -0.10529 | -0.10986 | -0.11902 | 0.20599 | 121.6415 | 0.032043 | 121.5912 | 121.4996 | 121.4584 | 121.5134 | 121.4722 | -121.6232 | -121.6232 | 121.6553 | 121.6049 | 61.2259 | 61.2579
202.7344 | 121.843 | -61.2671 | 60.347 | -0.05928 | 0.0065304 | 0.065183 | 0.062671 | -0.0025549 | -0.0094614 | -0.0013051 | -0.077179 | 0.0025335 | 0.065986 | 0.054745 | -0.014311 | 0.027408 | -0.0021619 | -0.045776 | 60.173 | -61.2488 | 60.4019 | -61.0519 | -61.4777 | -61.441 | 0.004578 | 60.1776 | -61.2946 | 60.347 | -61.2213 | -61.3724 | -61.3678 | 0.018311 | -0.17395 | 0.054932 | 0.21515 | -0.17395 | -0.21057 | -0.19226 | -0.22888 | -0.027466 | -0.16937 | 0 | 0.045777 | -0.10071 | -0.10528 | -0.073242 | -0.077819 | 0.19684 | 121.6507 | 0.073243 | 121.6415 | 121.4218 | 121.4722 | 121.4401 | 121.4447 | -121.5958 | -121.6415 | 121.669 | 121.6141 | 61.2213 | 61.2717
204.4219 | 121.9254 | -61.29 | 60.2509 | -0.12032 | 0.0067442 | 0.067746 | 0.063098 | -0.0021277 | -0.0073252 | -0.0021597 | -0.058869 | 0.0046697 | 0.066627 | 0.050686 | -0.01132 | 0.022708 | -0.0017347 | -0.14191 | 60.1135 | -61.2946 | 60.4294 | -61.0107 | -61.4731 | -61.4319 | -0.018311 | 60.0632 | -61.2808 | 60.3745 | -61.1984 | -61.3312 | -61.3037 | -0.004578 | -0.13733 | 0.17853 | 0.27924 | -0.14191 | -0.18311 | -0.13733 | -0.17853 | 0.009155 | -0.18768 | 0.1236 | 0.091553 | -0.013733 | -0.041199 | -0.022888 | -0.050354 | 0.28381 | 121.7239 | 0.082398 | 121.6553 | 121.4081 | 121.344 | 121.4035 | 121.3531 | -121.5454 | -121.5317 | 121.7194 | 121.6644 | 61.1481 | 61.2717
206.1875 | 121.8018 | -61.3037 | 60.3333 | -0.074539 | 0.010162 | 0.066464 | 0.064166 | 0.0019311 | -0.0075388 | -0.0036551 | -0.1138 | 0.0057379 | 0.067909 | 0.056454 | -0.012602 | 0.02399 | -0.0064343 | -0.16022 | 60.173 | -61.2854 | 60.3195 | -61.1481 | -61.5829 | -61.5463 | -0.16022 | 60.1135 | -61.3541 | 60.2554 | -61.3358 | -61.4639 | -61.441 | 0.018311 | -0.16022 | -0.013733 | 0.15564 | -0.24262 | -0.27924 | -0.26093 | -0.29755 | -0.050354 | -0.21973 | -0.07782 | -0.032043 | -0.13733 | -0.16022 | -0.086975 | -0.10986 | 0.13733 | 121.6049 | 0.018311 | 121.6095 | 121.4584 | 121.4676 | 121.4767 | 121.4172 | -121.6187 | -121.6873 | 121.6232 | 121.5591 | 61.1435 | 61.1435
207.9375 | 121.8109 | -61.3037 | 60.3104 | -0.10506 | 0.0082394 | 0.066464 | 0.063525 | 0.00022207 | -0.006257 | -0.0017325 | -0.09549 | 0.0057379 | 0.065345 | 0.051541 | -0.011106 | 0.024417 | -0.0023755 | -0.2243 | 60.1364 | -61.3083 | 60.3012 | -61.1664 | -61.5967 | -61.5646 | -0.1831 | 60.1181 | -61.3541 | 60.26 | -61.3312 | -61.4685 | -61.4273 | -0.004578 | -0.17395 | -0.009156 | 0.13733 | -0.26093 | -0.29297 | -0.25635 | -0.28839 | -0.050354 | -0.19226 | -0.050354 | -0.027466 | -0.1236 | -0.16479 | -0.073242 | -0.11444 | 0.14191 | 121.6095 | 0.022888 | 121.6141 | 121.4447 | 121.4722 | 121.4401 | 121.4218 | -121.6187 | -121.6644 | 121.6049 | 121.5637 | 61.0794 | 61.1206
209.6719 | 121.8063 | -61.2305 | 60.4202 | -0.044022 | 0.0063168 | 0.064969 | 0.060321 | -0.0027685 | -0.0071116 | -0.0023733 | -0.031403 | 0.0059515 | 0.065986 | 0.058163 | -0.010252 | 0.023776 | -0.0013073 | -0.027466 | 60.2417 | -61.2396 | 60.4065 | -61.0291 | -61.4594 | -61.4273 | 0.032043 | 60.2371 | -61.2305 | 60.3241 | -61.2213 | -61.3586 | -61.3586 | -0.009155 | -0.17853 | -0.013733 | 0.20142 | -0.19684 | -0.22888 | -0.18768 | -0.21973 | 0 | -0.1831 | -0.09613 | 0.009156 | -0.12817 | -0.12817 | -0.12817 | -0.12817 | 0.21057 | 121.6461 | 0.009156 | 121.5546 | 121.4813 | 121.4676 | 121.4722 | 121.4676 | -121.6599 | -121.6507 | 121.637 | 121.5546 | 61.203 | 61.2625
211.3594 | 121.9345 | -61.2625 | 60.2646 | -0.13557 | 0.0086668 | 0.065183 | 0.062457 | 0.00064947 | -0.008607 | -0.0025869 | -0.046661 | 0.0038153 | 0.069618 | 0.054959 | -0.011533 | 0.025058 | -0.0019483 | -0.12817 | 60.1181 | -61.2625 | 60.4294 | -61.0107 | -61.4594 | -61.4182 | -0.013733 | 60.0723 | -61.29 | 60.3699 | -61.2076 | -61.3312 | -61.3174 | 0 | -0.14648 | 0.16479 | 0.25177 | -0.15564 | -0.19684 | -0.15564 | -0.19684 | -0.027466 | -0.19226 | 0.10529 | 0.054931 | -0.054932 | -0.068665 | -0.027466 | -0.041199 | 0.25177 | 121.6919 | 0.082397 | 121.6599 | 121.3806 | 121.3623 | 121.3806 | 121.3348 | -121.5271 | -121.5546 | 121.6919 | 121.6324 | 61.1343 | 61.2488
213.125 | 121.8201 | -61.3129 | 60.2966 | -0.089798 | 0.0065304 | 0.066037 | 0.063311 | 0.0051355 | -0.0054026 | -0.0023733 | -0.098541 | 0.0059515 | 0.065772 | 0.051755 | -0.010893 | 0.022922 | -0.0036573 | -0.21057 | 60.1456 | -61.3037 | 60.3012 | -61.171 | -61.6104 | -61.5601 | -0.16022 | 60.0952 | -61.3541 | 60.2737 | -61.3449 | -61.4777 | -61.4273 | 0.009155 | -0.15106 | 0.004577 | 0.14191 | -0.24719 | -0.29755 | -0.25635 | -0.3067 | -0.041199 | -0.20142 | -0.022888 | -0.032044 | -0.11444 | -0.16479 | -0.073242 | -0.1236 | 0.13275 | 121.6049 | 0.009155 | 121.6278 | 121.4493 | 121.4493 | 121.4584 | 121.4081 | -121.6003 | -121.6507 | 121.6141 | 121.5866 | 61.1023 | 61.1526
214.8125 | 121.8887 | -61.2396 | 60.3333 | -0.089798 | 0.0024716 | 0.06561 | 0.060534 | -0.0017005 | -0.0094614 | -0.0023733 | -0.037506 | 0.0036017 | 0.063636 | 0.051114 | -0.013456 | 0.022495 | -0.0040845 | -0.13275 | 60.1227 | -61.2579 | 60.4294 | -60.9741 | -61.4456 | -61.3953 | 0.013733 | 60.1501 | -61.2671 | 60.379 | -61.1938 | -61.3083 | -61.3174 | -0.018311 | -0.21057 | 0.09613 | 0.2655 | -0.15564 | -0.20599 | -0.13733 | -0.18768 | -0.027466 | -0.18311 | 0.045776 | 0.045776 | -0.07782 | -0.068665 | -0.050354 | -0.041199 | 0.28381 | 121.6873 | 0.073242 | 121.6461 | 121.3806 | 121.4172 | 121.3623 | 121.3898 | -121.5912 | -121.6003 | 121.669 | 121.6187 | 61.1069 | 61.2534
216.5625 | 121.8155 | -61.2991 | 60.3241 | -0.12032 | 0.0061032 | 0.067105 | 0.06203 | 0.0027857 | -0.0075388 | -0.00023714 | -0.083283 | 0.0061651 | 0.068977 | 0.060086 | -0.011533 | 0.024204 | -0.0034435 | -0.21515 | 60.1501 | -61.3129 | 60.3149 | -61.1481 | -61.5921 | -61.528 | -0.15564 | 60.1044 | -61.3449 | 60.2783 | -61.322 | -61.4365 | -61.4227 | -0.013733 | -0.17395 | -0.009156 | 0.15106 | -0.22888 | -0.29297 | -0.21515 | -0.27924 | -0.045777 | -0.21973 | -0.045777 | -0.022888 | -0.1236 | -0.13733 | -0.077819 | -0.091552 | 0.16479 | 121.6278 | 0.022889 | 121.6232 | 121.463 | 121.4493 | 121.4493 | 121.4035 | -121.637 | -121.669 | 121.6141 | 121.5775 | 61.084 | 61.1435
218.25 | 121.8201 | -61.1847 | 60.3973 | -0.10506 | 0.0024716 | 0.067533 | 0.05968 | 0.0010767 | -0.0083932 | -0.0013051 | -0.0039367 | 0.0059515 | 0.067481 | 0.052823 | -0.011106 | 0.020145 | -0.0049389 | 0.050354 | 60.1959 | -61.1984 | 60.498 | -60.9192 | -61.3632 | -61.3174 | 0.11444 | 60.2142 | -61.235 | 60.379 | -61.1618 | -61.3037 | -61.322 | -0.013733 | -0.20142 | 0.10071 | 0.2655 | -0.13275 | -0.17853 | -0.11902 | -0.16479 | -0.050354 | -0.18311 | -0.018311 | 0.022888 | -0.13733 | -0.11902 | -0.086975 | -0.068665 | 0.27924 | 121.6965 | 0.073242 | 121.6141 | 121.3943 | 121.4493 | 121.3806 | 121.3989 | -121.5958 | -121.6324 | 121.6827 | 121.5637 | 61.235 | 61.2991
219.9844 | 121.8933 | -61.2213 | 60.3699 | -0.082169 | 0.005676 | 0.064115 | 0.061389 | -0.0023413 | -0.006257 | -0.0049367 | -0.0069885 | 0.0033881 | 0.065132 | 0.04385 | -0.012174 | 0.024417 | -0.0015209 | -0.07782 | 60.1593 | -61.2396 | 60.4294 | -61.0153 | -61.4319 | -61.409 | 0.027466 | 60.1822 | -61.2717 | 60.379 | -61.1801 | -61.2946 | -61.3174 | -0.018311 | -0.21057 | 0.059509 | 0.20599 | -0.18768 | -0.21057 | -0.16937 | -0.19226 | -0.050354 | -0.18768 | 0.009155 | 0.041198 | -0.096131 | -0.073243 | -0.045777 | -0.022889 | 0.2243 | 121.669 | 0.091552 | 121.6507 | 121.3989 | 121.4539 | 121.3806 | 121.4035 | -121.6095 | -121.6415 | 121.6507 | 121.6003 | 61.1435 | 61.2488
221.7344 | 121.8979 | -61.1984 | 60.4202 | -0.11269 | 0.005676 | 0.064969 | 0.058825 | -0.0049047 | -0.0094614 | -0.00066434 | -0.01004 | 0.0036017 | 0.064918 | 0.056454 | -0.011747 | 0.025272 | -0.0047253 | 0.073242 | 60.2142 | -61.1847 | 60.5301 | -60.91 | -61.3449 | -61.3312 | 0.18768 | 60.1685 | -61.2167 | 60.4385 | -61.1023 | -61.2122 | -61.235 | 0.013733 | -0.20599 | 0.10986 | 0.28839 | -0.13275 | -0.14648 | -0.14648 | -0.16022 | -0.018311 | -0.25177 | 0.018311 | 0.09613 | -0.036621 | -0.013733 | -0.01831 | 0.004578 | 0.27466 | 121.7148 | 0.11444 | 121.6553 | 121.3989 | 121.3852 | 121.4127 | 121.3669 | -121.6049 | -121.637 | 121.7285 | 121.637 | 61.2717 | 61.3861
223.4844 | 121.7834 | -61.3266 | 60.3104 | -0.10506 | 0.0061032 | 0.067533 | 0.065234 | -0.0021277 | -0.0094614 | -0.0010915 | -0.092438 | 0.0033881 | 0.066841 | 0.055813 | -0.014311 | 0.025699 | -0.0034435 | -0.19684 | 60.1135 | -61.2808 | 60.3241 | -61.171 | -61.5784 | -61.5509 | -0.19684 | 60.1364 | -61.3678 | 60.2554 | -61.3358 | -61.4868 | -61.4548 | 0.045776 | -0.19684 | 0.013733 | 0.15564 | -0.2243 | -0.25177 | -0.27008 | -0.29755 | -0.041199 | -0.17395 | -0.054932 | -0.009155 | -0.12817 | -0.16022 | -0.086975 | -0.11902 | 0.10986 | 121.6049 | 0.032044 | 121.6232 | 121.3943 | 121.5042 | 121.4401 | 121.463 | -121.5912 | -121.6782 | 121.6507 | 121.582 | 61.1298 | 61.1298
225.2188 | 121.9345 | -61.2854 | 60.2737 | -0.12032 | 0.0058896 | 0.066037 | 0.061816 | -0.0031957 | -0.0088206 | -0.0023733 | -0.046661 | 0.0040289 | 0.066627 | 0.056241 | -0.013456 | 0.025058 | -0.0066479 | -0.13275 | 60.1181 | -61.29 | 60.4385 | -61.0062 | -61.4685 | -61.4273 | -0.009155 | 60.054 | -61.3358 | 60.3836 | -61.1984 | -61.3266 | -61.3129 | -0.004578 | -0.15564 | 0.16479 | 0.27923 | -0.14191 | -0.18311 | -0.13733 | -0.17853 | -0.050354 | -0.21973 | 0.10986 | 0.086975 | -0.027466 | -0.041199 | 0.022888 | 0.009155 | 0.28381 | 121.7285 | 0.13733 | 121.7194 | 121.4081 | 121.3898 | 121.4035 | 121.3394 | -121.5637 | -121.6095 | 121.7239 | 121.669 | 61.1526 | 61.2762
226.9062 | 121.9299 | -61.2625 | 60.2783 | -0.10506 | 0.0067442 | 0.066037 | 0.062457 | 0.0015039 | -0.0077524 | -0.00023714 | -0.058869 | 0.0033881 | 0.065772 | 0.051968 | -0.01132 | 0.025272 | -0.0047253 | -0.13733 | 60.1318 | -61.2762 | 60.434 | -61.0199 | -61.4639 | -61.4365 | -0.018311 | 60.0723 | -61.29 | 60.3836 | -61.1984 | -61.322 | -61.3129 | -0.013733 | -0.14648 | 0.15564 | 0.24262 | -0.17395 | -0.20142 | -0.16022 | -0.18768 | -0.027466 | -0.20599 | 0.10529 | 0.064087 | -0.050354 | -0.059509 | -0.022888 | -0.032043 | 0.25635 | 121.7102 | 0.091553 | 121.6736 | 121.4081 | 121.3623 | 121.3943 | 121.3348 | -121.5546 | -121.5683 | 121.6965 | 121.6461 | 61.1252 | 61.2442
228.6406 | 121.7926 | -61.2991 | 60.3424 | -0.089798 | 0.0069578 | 0.064328 | 0.063952 | -0.0023413 | -0.0098886 | -0.0028005 | -0.10464 | 0.0046697 | 0.066413 | 0.058163 | -0.012602 | 0.025912 | -0.0040845 | -0.14191 | 60.1776 | -61.3129 | 60.3424 | -61.1206 | -61.5738 | -61.5555 | -0.13275 | 60.1135 | -61.3358 | 60.26 | -61.3266 | -61.4594 | -61.4319 | -0.013733 | -0.16479 | 0 | 0.17853 | -0.25635 | -0.27466 | -0.24262 | -0.26093 | -0.036621 | -0.22888 | -0.082397 | -0.027466 | -0.13275 | -0.16022 | -0.096131 | -0.1236 | 0.19226 | 121.6553 | 0.009155 | 121.5958 | 121.4905 | 121.4493 | 121.4767 | 121.4127 | -121.6553 | -121.6782 | 121.6415 | 121.5591 | 61.1572 | 61.1664
230.3125 | 121.8521 | -61.2579 | 60.3287 | -0.089798 | 0.0063168 | 0.066251 | 0.063952 | 0.00043587 | -0.0066844 | -0.0015189 | -0.1077 | 0.0044561 | 0.065559 | 0.056454 | -0.013029 | 0.025699 | -0.0049389 | -0.10071 | 60.1776 | -61.2808 | 60.4156 | -61.0382 | -61.4777 | -61.4319 | 0.009155 | 60.1501 | -61.3037 | 60.3424 | -61.2305 | -61.3632 | -61.3678 | -0.022888 | -0.15106 | 0.086975 | 0.21973 | -0.17395 | -0.21973 | -0.15106 | -0.19684 | -0.045776 | -0.17853 | 0.013733 | 0.027466 | -0.10986 | -0.10528 | -0.064087 | -0.059509 | 0.24262 | 121.6965 | 0.073242 | 121.6461 | 121.4584 | 121.4539 | 121.4355 | 121.4081 | -121.6095 | -121.6324 | 121.6736 | 121.6003 | 61.1572 | 61.2671
232.0625 | 121.8887 | -61.203 | 60.4111 | -0.10506 | 0.0067442 | 0.065183 | 0.059893 | -0.0023413 | -0.0075388 | -0.0015189 | 0.0021667 | 0.0044561 | 0.067909 | 0.0509 | -0.012815 | 0.024844 | -0.0079297 | 0.068665 | 60.1913 | -61.1893 | 60.5164 | -60.9238 | -61.322 | -61.2946 | 0.16937 | 60.2051 | -61.2396 | 60.4202 | -61.1298 | -61.2625 | -61.29 | 0.013733 | -0.21973 | 0.10529 | 0.27924 | -0.091553 | -0.11902 | -0.10529 | -0.13275 | -0.036621 | -0.20599 | 0.009155 | 0.073242 | -0.086975 | -0.059509 | -0.050354 | -0.022888 | 0.2655 | 121.7056 | 0.10986 | 121.6599 | 121.3806 | 121.4447 | 121.3943 | 121.4081 | -121.6003 | -121.6507 | 121.7194 | 121.6232 | 61.2717 | 61.3724
233.7969 | 121.9208 | -61.1847 | 60.3836 | -0.074539 | 0.003967 | 0.064542 | 0.058398 | -0.0014867 | -0.0083932 | -0.0032277 | 0.0082703 | 0.0055243 | 0.064704 | 0.049832 | -0.01132 | 0.02399 | -0.0079297 | 0.064087 | 60.1822 | -61.1847 | 60.5576 | -60.8597 | -61.3129 | -61.2946 | 0.20599 | 60.1822 | -61.1984 | 60.4568 | -61.0794 | -61.1984 | -61.2305 | 0 | -0.20142 | 0.17395 | 0.32501 | -0.10986 | -0.12817 | -0.10986 | -0.12817 | -0.013733 | -0.20142 | 0.073242 | 0.10528 | -0.045777 | -0.013733 | -0.032044 | 0 | 0.32501 | 121.7422 | 0.11902 | 121.6553 | 121.3669 | 121.3806 | 121.3669 | 121.3669 | -121.5683 | -121.582 | 121.7422 | 121.6415 | 61.2488 | 61.3907
235.4688 | 121.8887 | -61.2259 | 60.347 | -0.1432 | 0.0054624 | 0.064969 | 0.06203 | -0.0031957 | -0.0092478 | -0.0032277 | -0.022247 | 0.0036017 | 0.066413 | 0.052395 | -0.012602 | 0.025272 | -0.0051525 | -0.10529 | 60.1273 | -61.203 | 60.4294 | -61.0107 | -61.4639 | -61.3953 | 0.009155 | 60.1318 | -61.2534 | 60.3836 | -61.1938 | -61.3037 | -61.3129 | 0.022888 | -0.21973 | 0.082397 | 0.21515 | -0.16937 | -0.23804 | -0.19226 | -0.26093 | -0.027466 | -0.21515 | 0.036621 | 0.032043 | -0.086975 | -0.07782 | -0.059509 | -0.050354 | 0.19226 | 121.6324 | 0.059509 | 121.637 | 121.3303 | 121.3852 | 121.3531 | 121.3577 | -121.55 | -121.6003 | 121.6553 | 121.6095 | 61.1206 | 61.235
237.2188 | 121.8567 | -61.2534 | 60.3149 | -0.06691 | 0.005676 | 0.066037 | 0.060107 | 0.0019311 | -0.009675 | -0.0013051 | -0.089386 | 0.0044561 | 0.067268 | 0.056241 | -0.013456 | 0.024631 | -0.0034435 | -0.082397 | 60.1822 | -61.2717 | 60.4065 | -61.0428 | -61.4777 | -61.4594 | 0.018311 | 60.1456 | -61.29 | 60.3424 | -61.2213 | -61.3495 | -61.3495 | -0.01831 | -0.13275 | 0.091553 | 0.21057 | -0.20599 | -0.2243 | -0.18768 | -0.20599 | -0.036621 | -0.16937 | 0.027466 | 0.032044 | -0.09613 | -0.09613 | -0.059509 | -0.059509 | 0.22888 | 121.6782 | 0.068665 | 121.6324 | 121.4539 | 121.4355 | 121.4355 | 121.3989 | -121.5866 | -121.6049 | 121.6599 | 121.5958 | 61.171 | 61.2717
238.8906 | 121.8842 | -61.2396 | 60.3333 | -0.12032 | 0.0069578 | 0.064115 | 0.061389 | -0.00041873 | -0.0088206 | -0.0036551 | -0.034454 | 0.0033881 | 0.066413 | 0.058804 | -0.011533 | 0.023563 | -0.0072889 | -0.09613 | 60.1181 | -61.235 | 60.4385 | -60.997 | -61.4639 | -61.4136 | 0.013733 | 60.0998 | -61.2808 | 60.3928 | -61.1801 | -61.2991 | -61.2946 | 0.004578 | -0.21515 | 0.10529 | 0.24262 | -0.17395 | -0.2243 | -0.17853 | -0.22888 | -0.041199 | -0.23346 | 0.059509 | 0.059509 | -0.054932 | -0.059509 | -0.013733 | -0.01831 | 0.23804 | 121.6736 | 0.10071 | 121.6736 | 121.3531 | 121.3806 | 121.3577 | 121.3394 | -121.5683 | -121.6141 | 121.6782 | 121.6324 | 61.1435 | 61.2534
240.6406 | 121.8658 | -61.1984 | 60.4019 | -0.11269 | 0.0046078 | 0.066251 | 0.059893 | -0.0036231 | -0.0094614 | -0.00066434 | -0.019196 | 0.0029607 | 0.065986 | 0.050046 | -0.012602 | 0.023135 | -0.0053661 | 0.054932 | 60.1776 | -61.1847 | 60.5164 | -60.9146 | -61.3403 | -61.3174 | 0.17853 | 60.1959 | -61.2396 | 60.4156 | -61.1389 | -61.2534 | -61.2808 | 0.013733 | -0.2243 | 0.11444 | 0.28381 | -0.11902 | -0.14191 | -0.13275 | -0.15564 | -0.041199 | -0.20599 | 0.013732 | 0.059509 | -0.082398 | -0.054932 | -0.041199 | -0.013733 | 0.27008 | 121.701 | 0.10071 | 121.6553 | 121.3623 | 121.4355 | 121.376 | 121.3943 | -121.5866 | -121.6415 | 121.7148 | 121.6141 | 61.2534 | 61.377
242.375 | 121.9254 | -61.1755 | 60.3699 | -0.11269 | 0.0041806 | 0.065396 | 0.059893 | -0.0049047 | -0.010957 | -0.0045095 | -0.022247 | 0.0048833 | 0.064491 | 0.054745 | -0.013456 | 0.025485 | -0.0055799 | 0.059509 | 60.1822 | -61.1893 | 60.5667 | -60.8826 | -61.3266 | -61.2854 | 0.21057 | 60.1822 | -61.1938 | 60.4614 | -61.084 | -61.2122 | -61.235 | -0.013733 | -0.18768 | 0.19684 | 0.29297 | -0.10986 | -0.15106 | -0.09613 | -0.13733 | -0.018311 | -0.18768 | 0.091553 | 0.091553 | -0.059509 | -0.036621 | -0.041198 | -0.01831 | 0.3067 | 121.756 | 0.10986 | 121.6553 | 121.3715 | 121.376 | 121.3577 | 121.3577 | -121.5591 | -121.5637 | 121.7422 | 121.637 | 61.235 | 61.3861
244.1094 | 121.9208 | -61.1801 | 60.379 | -0.06691 | 0.0043942 | 0.066464 | 0.060962 | 0.00064947 | -0.0098886 | -0.0019461 | -0.0008851 | 0.0048833 | 0.065345 | 0.053464 | -0.010893 | 0.022922 | -0.0083569 | 0.073242 | 60.1913 | -61.1755 | 60.5621 | -60.8917 | -61.3449 | -61.2991 | 0.19226 | 60.1685 | -61.2213 | 60.4523 | -61.0977 | -61.2213 | -61.2534 | 0.004578 | -0.18768 | 0.18311 | 0.28839 | -0.11902 | -0.16479 | -0.1236 | -0.16937 | -0.041198 | -0.21057 | 0.073243 | 0.082398 | -0.073242 | -0.041198 | -0.032044 | 0 | 0.28381 | 121.7377 | 0.1236 | 121.6736 | 121.3669 | 121.3898 | 121.3715 | 121.3486 | -121.5546 | -121.6003 | 121.7422 | 121.6324 | 61.2534 | 61.3724
245.7969 | 121.9391 | -61.2488 | 60.2875 | -0.16609 | 0.005676 | 0.06796 | 0.06203 | -0.0014867 | -0.0090342 | -0.00023714 | -0.037506 | 0.0053107 | 0.065559 | 0.061154 | -0.012602 | 0.024844 | -0.0049389 | -0.13733 | 60.0952 | -61.2534 | 60.4523 | -60.997 | -61.4548 | -61.4044 | 0.032043 | 60.0906 | -61.3083 | 60.3882 | -61.171 | -61.3129 | -61.3083 | -0.004578 | -0.19226 | 0.1648 | 0.25177 | -0.15564 | -0.20599 | -0.15106 | -0.20142 | -0.05951 | -0.19684 | 0.10071 | 0.07782 | -0.05951 | -0.064087 | 0 | -0.004577 | 0.25635 | 121.7056 | 0.13733 | 121.6965 | 121.3486 | 121.3989 | 121.344 | 121.3394 | -121.5408 | -121.5958 | 121.7011 | 121.637 | 61.1114 | 61.2808
247.5469 | 121.8063 | -61.203 | 60.4294 | -0.044022 | 0.0058896 | 0.065396 | 0.062884 | -0.0046911 | -0.010102 | -0.0021597 | -0.034454 | 0.0057379 | 0.065559 | 0.054532 | -0.013029 | 0.024417 | -0.0034435 | -0.009155 | 60.2417 | -61.2122 | 60.4202 | -61.0382 | -61.4502 | -61.4136 | 0.045776 | 60.2188 | -61.2396 | 60.3378 | -61.2167 | -61.3403 | -61.3678 | -0.009155 | -0.18768 | -0.009155 | 0.1648 | -0.21057 | -0.24719 | -0.20142 | -0.23804 | -0.036621 | -0.21057 | -0.091552 | -0.013733 | -0.16479 | -0.13733 | -0.12817 | -0.10071 | 0.17395 | 121.6324 | 0.022888 | 121.5775 | 121.4539 | 121.4584 | 121.4447 | 121.4218 | -121.6415 | -121.669 | 121.6232 | 121.5408 | 61.1938 | 61.2488
249.2812 | 121.8292 | -61.2396 | 60.3882 | -0.10506 | 0.0037534 | 0.063901 | 0.060534 | -0.00063233 | -0.010743 | -0.0034415 | -0.080231 | 0.0048833 | 0.065559 | 0.058377 | -0.011961 | 0.024631 | -0.0045117 | -0.018311 | 60.228 | -61.2488 | 60.3928 | -61.0611 | -61.4731 | -61.4639 | 0.004578 | 60.2005 | -61.2808 | 60.3241 | -61.2305 | -61.3495 | -61.3495 | -0.009155 | -0.16022 | 0.004577 | 0.17853 | -0.2243 | -0.23346 | -0.21515 | -0.2243 | -0.041199 | -0.18768 | -0.064087 | 0.009155 | -0.10986 | -0.10986 | -0.068664 | -0.068664 | 0.18768 | 121.6415 | 0.050354 | 121.6049 | 121.4767 | 121.4813 | 121.4676 | 121.4401 | -121.637 | -121.669 | 121.6324 | 121.5637 | 61.2213 | 61.2442
250.9688 | 121.843 | -61.2671 | 60.3561 | -0.044022 | 0.0063168 | 0.066464 | 0.063098 | -0.0027685 | -0.009675 | 0.00061746 | -0.055817 | 0.0033881 | 0.068763 | 0.062436 | -0.010893 | 0.025058 | -0.0051525 | -0.036621 | 60.2097 | -61.2671 | 60.4019 | -61.0748 | -61.4685 | -61.441 | -0.009155 | 60.2142 | -61.2625 | 60.3287 | -61.2213 | -61.3724 | -61.3678 | 0 | -0.14648 | 0.045777 | 0.19226 | -0.17395 | -0.20142 | -0.17395 | -0.20142 | 0.004578 | -0.14191 | -0.027466 | 0.045777 | -0.10071 | -0.10528 | -0.10529 | -0.10986 | 0.19226 | 121.669 | 0.041199 | 121.5912 | 121.4767 | 121.4767 | 121.4767 | 121.4813 | -121.6232 | -121.6187 | 121.669 | 121.5958 | 61.2305 | 61.2579
252.7031 | 121.8979 | -61.235 | 60.3516 | -0.089798 | 0.0054624 | 0.065824 | 0.059893 | -0.0042639 | -0.0075388 | -0.0034415 | -0.019196 | 0.0018927 | 0.068763 | 0.049832 | -0.011106 | 0.024631 | -0.0034435 | -0.073242 | 60.1456 | -61.235 | 60.4431 | -60.9924 | -61.4273 | -61.3861 | 0.027466 | 60.1547 | -61.2808 | 60.3836 | -61.171 | -61.2854 | -61.2946 | 0 | -0.20599 | 0.091553 | 0.24261 | -0.15106 | -0.19226 | -0.15106 | -0.19226 | -0.045777 | -0.19684 | 0.032044 | 0.064087 | -0.05951 | -0.050354 | -0.013733 | -0.004577 | 0.24261 | 121.6782 | 0.10986 | 121.6644 | 121.3806 | 121.4355 | 121.3806 | 121.3898 | -121.5866 | -121.6324 | 121.6782 | 121.6187 | 61.1618 | 61.2625
254.375 | 121.9574 | -61.1526 | 60.379 | -0.12032 | 0.0050352 | 0.065183 | 0.060962 | -0.0023413 | -0.0088206 | -0.00087794 | -0.019196 | 0.0050971 | 0.067695 | 0.048123 | -0.010038 | 0.022495 | -0.0045117 | 0.041199 | 60.1685 | -61.1801 | 60.5667 | -60.8597 | -61.29 | -61.2717 | 0.20142 | 60.1547 | -61.2076 | 60.4889 | -61.0611 | -61.1893 | -61.2122 | -0.027466 | -0.21057 | 0.18768 | 0.29297 | -0.11902 | -0.13733 | -0.091552 | -0.10986 | -0.054932 | -0.2243 | 0.10986 | 0.091553 | -0.059509 | -0.036621 | -0.004577 | 0.018311 | 0.32044 | 121.7468 | 0.14648 | 121.6965 | 121.3486 | 121.3623 | 121.3211 | 121.3074 | -121.5591 | -121.5866 | 121.7194 | 121.6415 | 61.1938 | 61.3541
256.125 | 121.907 | -61.2625 | 60.2692 | -0.12794 | 0.0061032 | 0.06561 | 0.064166 | 0.0034265 | -0.0094614 | -0.0028005 | -0.077179 | 0.0044561 | 0.064491 | 0.059872 | -0.014097 | 0.025272 | -0.0062207 | -0.19226 | 60.1318 | -61.2854 | 60.3928 | -61.0748 | -61.5097 | -61.4731 | -0.050354 | 60.0723 | -61.3037 | 60.3699 | -61.2076 | -61.3358 | -61.3174 | -0.022888 | -0.13733 | 0.1236 | 0.18768 | -0.21057 | -0.24719 | -0.18768 | -0.2243 | -0.041199 | -0.19684 | 0.10071 | 0.054931 | -0.054932 | -0.073242 | -0.013733 | -0.032043 | 0.21057 | 121.6782 | 0.09613 | 121.6736 | 121.4172 | 121.376 | 121.3943 | 121.3348 | -121.5546 | -121.5729 | 121.6553 | 121.6324 | 61.0703 | 61.2122
257.7969 | 121.8292 | -61.2396 | 60.3882 | -0.021133 | 0.005676 | 0.065824 | 0.063098 | -0.0023413 | -0.0098886 | -0.0030141 | -0.086334 | 0.0033881 | 0.067268 | 0.053677 | -0.012174 | 0.027408 | -0.0045117 | -0.032043 | 60.228 | -61.2442 | 60.3928 | -61.0748 | -61.4822 | -61.4777 | 0.013733 | 60.1959 | -61.2854 | 60.3424 | -61.2213 | -61.3586 | -61.3541 | -0.004578 | -0.16022 | 0.004577 | 0.16479 | -0.23804 | -0.24262 | -0.23346 | -0.23804 | -0.045776 | -0.19226 | -0.045777 | 0.018311 | -0.11444 | -0.11902 | -0.068665 | -0.073243 | 0.16937 | 121.637 | 0.064087 | 121.6278 | 121.4722 | 121.4813 | 121.4676 | 121.4355 | -121.6324 | -121.6736 | 121.6324 | 121.582 | 61.2076 | 61.2534
259.5312 | 121.962 | -61.171 | 60.3882 | -0.074539 | 0.0061032 | 0.066678 | 0.06203 | 0.00086307 | -0.0075388 | -0.0034415 | 0.020477 | 0.0053107 | 0.065345 | 0.0462 | -0.012815 | 0.024417 | -0.0023755 | 0.036621 | 60.2097 | -61.1664 | 60.5209 | -60.8917 | -61.3358 | -61.3037 | 0.20142 | 60.1822 | -61.2213 | 60.4889 | -61.0474 | -61.1664 | -61.2167 | 0.004577 | -0.17853 | 0.13275 | 0.27923 | -0.13275 | -0.16479 | -0.13733 | -0.16937 | -0.050354 | -0.20599 | 0.10071 | 0.1236 | -0.045777 | 0.004577 | 0.004577 | 0.054931 | 0.27466 | 121.6873 | 0.17395 | 121.7102 | 121.376 | 121.4035 | 121.3806 | 121.3531 | -121.5546 | -121.6095 | 121.6919 | 121.6599 | 61.2076 | 61.3724
261.2812 | 121.907 | -61.2717 | 60.2692 | -0.1432 | 0.0061032 | 0.066892 | 0.06203 | -0.0029821 | -0.0077524 | -0.0036551 | -0.080231 | 0.0048833 | 0.066627 | 0.060513 | -0.01367 | 0.02399 | -0.0057935 | -0.21973 | 60.1456 | -61.3129 | 60.3516 | -61.1069 | -61.5463 | -61.5051 | -0.09613 | 60.0952 | -61.3174 | 60.3516 | -61.2305 | -61.3632 | -61.3541 | -0.041199 | -0.1236 | 0.082397 | 0.16479 | -0.23346 | -0.27466 | -0.19226 | -0.23346 | -0.045777 | -0.17395 | 0.082397 | 0.041198 | -0.082398 | -0.091553 | -0.036621 | -0.045776 | 0.20599 | 121.6644 | 0.086975 | 121.669 | 121.4584 | 121.4127 | 121.4172 | 121.3669 | -121.582 | -121.5866 | 121.6232 | 121.6232 | 61.0519 | 61.1755
262.9688 | 121.9437 | -61.1572 | 60.3836 | -0.10506 | 0.0031126 | 0.062619 | 0.060321 | -0.0046911 | -0.0088206 | -0.0017325 | -0.0039367 | 0.0040289 | 0.065345 | 0.056241 | -0.012602 | 0.023349 | -0.0055799 | 0.050354 | 60.173 | -61.2305 | 60.5576 | -60.8643 | -61.3037 | -61.2717 | 0.19684 | 60.173 | -61.1938 | 60.4843 | -61.0565 | -61.171 | -61.2167 | -0.073242 | -0.21057 | 0.17395 | 0.29297 | -0.11444 | -0.14648 | -0.041198 | -0.073242 | -0.036621 | -0.21057 | 0.10071 | 0.10071 | -0.059509 | -0.013732 | -0.022888 | 0.022889 | 0.36621 | 121.788 | 0.13733 | 121.6782 | 121.4035 | 121.3669 | 121.3303 | 121.3303 | -121.6141 | -121.5775 | 121.7148 | 121.6415 | 61.2076 | 61.3541
264.7188 | 121.9299 | -61.171 | 60.3836 | -0.11269 | 0.0041806 | 0.064542 | 0.060321 | -0.00020513 | -0.010316 | -0.00045074 | 0.0021667 | 0.0027471 | 0.067695 | 0.048764 | -0.013029 | 0.025058 | -0.0051525 | -0.045776 | 60.1501 | -61.2305 | 60.4889 | -60.965 | -61.3815 | -61.3403 | 0.11902 | 60.173 | -61.2076 | 60.466 | -61.0977 | -61.1938 | -61.2213 | -0.05951 | -0.23346 | 0.10529 | 0.20599 | -0.16937 | -0.21057 | -0.10986 | -0.15106 | -0.036622 | -0.21057 | 0.082397 | 0.073242 | -0.050354 | -0.022889 | -0.013732 | 0.013733 | 0.2655 | 121.7194 | 0.10986 | 121.6736 | 121.3806 | 121.3806 | 121.3211 | 121.344 | -121.6141 | -121.5912 | 121.6599 | 121.637 | 61.1252 | 61.29
266.4062 | 121.8979 | -61.2259 | 60.347 | -0.10506 | 0.0069578 | 0.067533 | 0.060534 | -0.0029821 | -0.009675 | -0.0015189 | -0.04361 | 0.0063787 | 0.066841 | 0.055813 | -0.012815 | 0.023349 | -0.0049389 | -0.091553 | 60.1639 | -61.2213 | 60.4431 | -61.0199 | -61.4502 | -61.409 | 0.009155 | 60.1501 | -61.2671 | 60.3882 | -61.1801 | -61.2946 | -61.3037 | 0.004578 | -0.18311 | 0.09613 | 0.20599 | -0.18311 | -0.2243 | -0.18768 | -0.22888 | -0.041199 | -0.19684 | 0.041199 | 0.045776 | -0.07782 | -0.068665 | -0.036621 | -0.027466 | 0.20142 | 121.6644 | 0.086975 | 121.6553 | 121.3852 | 121.4172 | 121.3898 | 121.376 | -121.5683 | -121.6141 | 121.669 | 121.6141 | 61.1343 | 61.235
268.1562 | 121.843 | -61.2259 | 60.3973 | -0.10506 | 0.0037534 | 0.065396 | 0.063098 | -0.0034095 | -0.0083932 | -0.0017325 | -0.089386 | 0.0050971 | 0.06855 | 0.058377 | -0.012174 | 0.02399 | -0.0010937 | -0.027466 | 60.2646 | -61.2305 | 60.3973 | -61.0657 | -61.496 | -61.4639 | 0.013733 | 60.2234 | -61.2625 | 60.347 | -61.2213 | -61.3449 | -61.3495 | -0.004578 | -0.13275 | 0 | 0.16022 | -0.23804 | -0.27008 | -0.23346 | -0.2655 | -0.036621 | -0.17395 | -0.050354 | 0.004578 | -0.1236 | -0.11902 | -0.086975 | -0.082398 | 0.16479 | 121.6278 | 0.041199 | 121.6095 | 121.4951 | 121.4859 | 121.4905 | 121.4493 | -121.6278 | -121.6599 | 121.6232 | 121.5729 | 61.1984 | 61.2396
269.9062 | 121.8246 | -61.2122 | 60.3836 | -0.051651 | 0.0052488 | 0.063687 | 0.064166 | -0.0038367 | -0.0092478 | -0.0015189 | -0.074127 | 0.0048833 | 0.068122 | 0.054745 | -0.010679 | 0.024204 | -0.0030163 | -0.022888 | 60.228 | -61.235 | 60.4156 | -61.0657 | -61.4685 | -61.441 | 0.009155 | 60.228 | -61.2671 | 60.3149 | -61.2305 | -61.3586 | -61.3586 | -0.022888 | -0.15564 | 0.032043 | 0.14648 | -0.22888 | -0.25635 | -0.20599 | -0.23346 | -0.054932 | -0.15564 | -0.068665 | -0.018311 | -0.14648 | -0.14648 | -0.091553 | -0.091553 | 0.16937 | 121.6507 | 0.036621 | 121.582 | 121.463 | 121.4951 | 121.4401 | 121.4401 | -121.6187 | -121.6507 | 121.6278 | 121.5271 | 61.1893 | 61.2213
271.5938 | 121.9254 | -61.2717 | 60.2921 | -0.17372 | 0.0054624 | 0.066037 | 0.061602 | -0.0038367 | -0.009675 | -0.0023733 | -0.064972 | 0.00082453 | 0.065772 | 0.052609 | -0.013883 | 0.024631 | -0.0075025 | -0.13733 | 60.1273 | -61.29 | 60.4523 | -60.9924 | -61.4685 | -61.4136 | 0.013733 | 60.1044 | -61.2991 | 60.3882 | -61.1801 | -61.29 | -61.2991 | -0.018311 | -0.1648 | 0.16022 | 0.27923 | -0.14191 | -0.19684 | -0.1236 | -0.17853 | -0.027466 | -0.18768 | 0.096131 | 0.091552 | -0.027466 | -0.018311 | 0 | 0.009155 | 0.29755 | 121.7422 | 0.11902 | 121.6873 | 121.4172 | 121.4035 | 121.3989 | 121.376 | -121.582 | -121.5912 | 121.7239 | 121.6599 | 61.1343 | 61.2854
273.3281 | 121.8475 | -61.2625 | 60.3149 | -0.1432 | 0.0063168 | 0.06561 | 0.063952 | 0.0010767 | -0.0098886 | -0.0019461 | -0.092438 | 0.0059515 | 0.067909 | 0.054959 | -0.011961 | 0.023563 | -0.0030163 | -0.054932 | 60.1822 | -61.2946 | 60.4019 | -61.0291 | -61.4868 | -61.4456 | 0.004578 | 60.1639 | -61.3129 | 60.3333 | -61.2213 | -61.3632 | -61.3586 | -0.032044 | -0.13275 | 0.086976 | 0.23346 | -0.18311 | -0.2243 | -0.15106 | -0.19226 | -0.050354 | -0.15106 | 0.018311 | 0.041199 | -0.096131 | -0.10071 | -0.045777 | -0.050354 | 0.2655 | 121.6965 | 0.091553 | 121.6461 | 121.4767 | 121.4767 | 121.4447 | 121.4264 | -121.6095 | -121.6278 | 121.6644 | 121.5958 | 61.2076 | 61.2671
275.0781 | 121.8796 | -61.2305 | 60.3241 | -0.1432 | 0.0050352 | 0.066464 | 0.060534 | 0.0012903 | -0.0083932 | -0.0040823 | -0.016144 | 0.0025335 | 0.067909 | 0.059018 | -0.011106 | 0.023563 | -0.0064343 | -0.09613 | 60.1227 | -61.2579 | 60.4523 | -60.9879 | -61.4685 | -61.409 | 0.018311 | 60.141 | -61.2854 | 60.3745 | -61.203 | -61.2808 | -61.3037 | -0.027466 | -0.20142 | 0.12817 | 0.24262 | -0.17853 | -0.23804 | -0.15106 | -0.21057 | -0.054931 | -0.18311 | 0.050354 | 0.027466 | -0.073242 | -0.050354 | -0.018311 | 0.004577 | 0.27008 | 121.7102 | 0.082397 | 121.6599 | 121.3806 | 121.4264 | 121.3531 | 121.3715 | -121.582 | -121.6095 | 121.6827 | 121.6049 | 61.1343 | 61.2488
276.8125 | 121.8384 | -61.2534 | 60.347 | -0.11269 | 0.0048214 | 0.066251 | 0.06203 | -0.0017005 | -0.0083932 | -0.0032277 | -0.098541 | 0.0055243 | 0.066841 | 0.054959 | -0.013456 | 0.025485 | -0.0019483 | -0.050354 | 60.2051 | -61.2625 | 60.4111 | -61.0428 | -61.4594 | -61.4639 | 0.022888 | 60.1639 | -61.3129 | 60.3516 | -61.2167 | -61.3586 | -61.3541 | -0.009155 | -0.14191 | 0.064087 | 0.21057 | -0.21057 | -0.20599 | -0.20142 | -0.19684 | -0.059509 | -0.18311 | 0.004577 | 0.036621 | -0.10071 | -0.10529 | -0.041199 | -0.045777 | 0.21973 | 121.6736 | 0.09613 | 121.6644 | 121.4676 | 121.4767 | 121.4584 | 121.4172 | -121.6095 | -121.6599 | 121.6644 | 121.6049 | 61.203 | 61.2762
278.5625 | 121.8155 | -61.2213 | 60.4111 | -0.06691 | 0.0035398 | 0.064542 | 0.061175 | -0.0061865 | -0.0088206 | 0.00061746 | -0.052765 | 0.0040289 | 0.067268 | 0.059659 | -0.01132 | 0.025058 | -0.0034435 | -0.027466 | 60.2325 | -61.2305 | 60.4065 | -61.0519 | -61.4456 | -61.4502 | 0.004578 | 60.2509 | -61.2717 | 60.3333 | -61.235 | -61.3586 | -61.377 | -0.009156 | -0.17853 | -0.004578 | 0.16937 | -0.22888 | -0.22431 | -0.21973 | -0.21515 | -0.050354 | -0.16022 | -0.07782 | -0.013733 | -0.15564 | -0.13733 | -0.10529 | -0.086976 | 0.17853 | 121.637 | 0.036621 | 121.6049 | 121.463 | 121.5225 | 121.4539 | 121.4722 | -121.6415 | -121.6827 | 121.6278 | 121.5546 | 61.1938 | 61.2259
280.2969 | 121.8338 | -61.2396 | 60.379 | -0.089798 | 0.0043942 | 0.066464 | 0.063098 | -0.0029821 | -0.0073252 | -0.0038687 | -0.074127 | 0.0048833 | 0.065132 | 0.057309 | -0.011533 | 0.024204 | -0.0047253 | -0.041199 | 60.2142 | -61.235 | 60.3973 | -61.0748 | -61.4731 | -61.4456 | 0.004578 | 60.2234 | -61.2762 | 60.347 | -61.2442 | -61.3632 | -61.3632 | 0.004578 | -0.16479 | 0.018311 | 0.16479 | -0.20599 | -0.23346 | -0.21057 | -0.23804 | -0.036621 | -0.15564 | -0.032043 | -0.004578 | -0.1236 | -0.1236 | -0.086975 | -0.086975 | 0.16022 | 121.6324 | 0.032043 | 121.6232 | 121.4493 | 121.4996 | 121.4539 | 121.463 | -121.6141 | -121.6553 | 121.637 | 121.5866 | 61.1984 | 61.2442
282.0469 | 121.8384 | -61.2579 | 60.3241 | -0.12794 | 0.0069578 | 0.066464 | 0.063952 | 0.0021447 | -0.0092478 | -0.0015189 | -0.089386 | 0.0063787 | 0.064918 | 0.050473 | -0.01132 | 0.02399 | -0.0045117 | -0.07782 | 60.1822 | -61.2671 | 60.4156 | -61.0336 | -61.4731 | -61.4548 | 0.013733 | 60.1685 | -61.322 | 60.3424 | -61.2122 | -61.3724 | -61.3495 | -0.009155 | -0.14191 | 0.091552 | 0.22431 | -0.19684 | -0.21515 | -0.18768 | -0.20599 | -0.064086 | -0.15564 | 0.01831 | 0.045777 | -0.091552 | -0.11444 | -0.027466 | -0.050354 | 0.23346 | 121.6827 | 0.10986 | 121.6644 | 121.4493 | 121.4905 | 121.4401 | 121.4264 | -121.5912 | -121.6461 | 121.6736 | 121.6003 | 61.1801 | 61.2717
283.7344 | 121.9208 | -61.2625 | 60.3058 | -0.097427 | 0.0063168 | 0.065824 | 0.059893 | -0.0053321 | -0.007966 | -0.0015189 | -0.019196 | 0.0040289 | 0.063636 | 0.054104 | -0.010893 | 0.023563 | -0.0032299 | -0.1236 | 60.1089 | -61.2625 | 60.4568 | -60.9787 | -61.4502 | -61.4044 | 0.013733 | 60.1089 | -61.2946 | 60.3745 | -61.1847 | -61.3174 | -61.2808 | 0 | -0.19684 | 0.15106 | 0.28381 | -0.14191 | -0.18768 | -0.14191 | -0.18768 | -0.032044 | -0.19684 | 0.068665 | 0.07782 | -0.018311 | -0.054932 | 0.013733 | -0.022888 | 0.28381 | 121.7194 | 0.10986 | 121.669 | 121.3715 | 121.4035 | 121.3715 | 121.3715 | -121.5683 | -121.6003 | 121.7194 | 121.637 | 61.1389 | 61.2762
285.4844 | 121.875 | -61.2488 | 60.3378 | -0.12794 | 0.0069578 | 0.066037 | 0.059893 | -0.00084593 | -0.0075388 | -0.0030141 | -0.025299 | 0.0036017 | 0.067054 | 0.045773 | -0.012174 | 0.025058 | 0.0023243 | -0.10529 | 60.1547 | -61.2625 | 60.4431 | -60.9833 | -61.4594 | -61.3998 | 0.027466 | 60.1318 | -61.2762 | 60.3607 | -61.1755 | -61.3037 | -61.3083 | -0.013733 | -0.18311 | 0.10529 | 0.2655 | -0.15106 | -0.21057 | -0.13733 | -0.19684 | -0.027466 | -0.20599 | 0.022888 | 0.073242 | -0.05951 | -0.054932 | -0.032044 | -0.027466 | 0.27924 | 121.7056 | 0.10071 | 121.637 | 121.4172 | 121.4081 | 121.4035 | 121.3806 | -121.6003 | -121.6141 | 121.6919 | 121.6095 | 61.1435 | 61.2762
287.1719 | 121.9437 | -61.2579 | 60.2646 | -0.10506 | 0.0065304 | 0.067319 | 0.061389 | -0.0027685 | -0.007966 | -0.0045095 | -0.04361 | 0.0036017 | 0.066841 | 0.064145 | -0.012388 | 0.024844 | -0.0053661 | -0.13275 | 60.141 | -61.2991 | 60.4431 | -61.0016 | -61.4731 | -61.4136 | 0.013733 | 60.0906 | -61.3174 | 60.3836 | -61.1801 | -61.3037 | -61.2946 | -0.041198 | -0.1236 | 0.17853 | 0.25635 | -0.15564 | -0.21515 | -0.11444 | -0.17395 | -0.059509 | -0.17395 | 0.11902 | 0.07782 | -0.036621 | -0.045776 | 0.022888 | 0.013733 | 0.29755 | 121.7422 | 0.13733 | 121.7011 | 121.4401 | 121.4081 | 121.3989 | 121.3486 | -121.5637 | -121.582 | 121.7011 | 121.6415 | 61.1252 | 61.2717
288.9219 | 121.9482 | -61.1938 | 60.3836 | -0.11269 | 0.0046078 | 0.066251 | 0.060962 | -0.0023413 | -0.0071116 | -0.0013051 | 0.011322 | 0.0040289 | 0.065772 | 0.055813 | -0.012174 | 0.024204 | -0.0036573 | -0.032043 | 60.1868 | -61.235 | 60.4797 | -60.9604 | -61.3815 | -61.322 | 0.10986 | 60.1822 | -61.235 | 60.4614 | -61.1069 | -61.1984 | -61.235 | -0.041198 | -0.19684 | 0.09613 | 0.23346 | -0.12817 | -0.18768 | -0.086975 | -0.14649 | -0.041198 | -0.20142 | 0.07782 | 0.086975 | -0.041198 | -0.004577 | 0 | 0.036621 | 0.27466 | 121.7148 | 0.12817 | 121.6965 | 121.4218 | 121.4172 | 121.3806 | 121.376 | -121.6187 | -121.6187 | 121.6736 | 121.6553 | 61.1618 | 61.3037
290.6719 | 121.8155 | -61.2305 | 60.4202 | -0.082169 | 0.0033262 | 0.06561 | 0.060962 | -0.0036231 | -0.0088206 | -0.0023733 | -0.046661 | 0.0055243 | 0.065772 | 0.054745 | -0.011747 | 0.024417 | -0.0053661 | -0.013733 | 60.2051 | -61.2167 | 60.4248 | -61.0291 | -61.4685 | -61.4136 | 0.059509 | 60.2371 | -61.2534 | 60.3516 | -61.2076 | -61.3266 | -61.3586 | 0.013733 | -0.21515 | 0.004578 | 0.20142 | -0.1831 | -0.23804 | -0.19684 | -0.25177 | -0.022888 | -0.1831 | -0.068665 | 0.022888 | -0.12817 | -0.09613 | -0.10529 | -0.073242 | 0.18768 | 121.6415 | 0.045776 | 121.6049 | 121.4218 | 121.4905 | 121.4355 | 121.4676 | -121.637 | -121.6736 | 121.6553 | 121.582 | 61.2167 | 61.29
292.3594 | 121.9162 | -61.171 | 60.4019 | -0.12032 | 0.003967 | 0.065396 | 0.061389 | -0.0036231 | -0.010743 | -0.0047231 | -0.013092 | 0.0046697 | 0.067909 | 0.048977 | -0.011961 | 0.023135 | -0.0013073 | 0.068665 | 60.1776 | -61.1755 | 60.5301 | -60.9055 | -61.3541 | -61.3037 | 0.18768 | 60.1913 | -61.2167 | 60.4431 | -61.1023 | -61.2167 | -61.2396 | -0.004578 | -0.2243 | 0.12817 | 0.2655 | -0.13275 | -0.18311 | -0.12817 | -0.17853 | -0.045777 | -0.21057 | 0.041198 | 0.068664 | -0.068665 | -0.045777 | -0.022888 | 0 | 0.27008 | 121.7056 | 0.11444 | 121.6599 | 121.3531 | 121.4081 | 121.3486 | 121.3623 | -121.5775 | -121.6187 | 121.701 | 121.6141 | 61.2396 | 61.3586
294.1094 | 121.8704 | -61.2717 | 60.3516 | -0.06691 | 0.0061032 | 0.064969 | 0.063739 | -0.00041873 | -0.0081796 | 0.0012583 | -0.092438 | 0.0065923 | 0.066841 | 0.06564 | -0.011961 | 0.026126 | -0.0053661 | -0.054932 | 60.1913 | -61.2534 | 60.4065 | -61.0565 | -61.4777 | -61.4548 | 0.022888 | 60.1913 | -61.2808 | 60.3561 | -61.2122 | -61.3586 | -61.3495 | 0.01831 | -0.16022 | 0.054932 | 0.21515 | -0.18311 | -0.20599 | -0.20142 | -0.2243 | -0.009156 | -0.16022 | 0.004578 | 0.059509 | -0.07782 | -0.086976 | -0.068664 | -0.07782 | 0.19684 | 121.6599 | 0.068665 | 121.637 | 121.4447 | 121.4722 | 121.463 | 121.463 | -121.6049 | -121.6324 | 121.6782 | 121.6278 | 61.2167 | 61.2946
295.7969 | 121.9574 | -61.1755 | 60.3653 | -0.082169 | 0.0052488 | 0.063901 | 0.061389 | -0.0010595 | -0.007966 | -0.0021597 | 0.0082703 | 0.0050971 | 0.066627 | 0.049405 | -0.011747 | 0.025272 | -0.0062207 | 0.032043 | 60.1959 | -61.1847 | 60.5301 | -60.8917 | -61.3312 | -61.2946 | 0.19684 | 60.1456 | -61.2305 | 60.4935 | -61.0519 | -61.1664 | -61.2122 | -0.009155 | -0.16937 | 0.16479 | 0.28381 | -0.11902 | -0.15564 | -0.10986 | -0.14648 | -0.054932 | -0.21973 | 0.12817 | 0.1236 | -0.036621 | 0.009155 | 0.018311 | 0.064087 | 0.29297 | 121.7148 | 0.17853 | 121.7239 | 121.3806 | 121.376 | 121.3715 | 121.3211 | -121.55 | -121.5958 | 121.7056 | 121.669 | 61.2076 | 61.3724
297.5312 | 121.9025 | -61.235 | 60.3378 | -0.097427 | 0.003967 | 0.065824 | 0.060534 | -0.0029821 | -0.0088206 | -0.0028005 | -0.034454 | 0.0055243 | 0.067695 | 0.051114 | -0.013883 | 0.023349 | -0.0015209 | -0.10529 | 60.1044 | -61.2579 | 60.4477 | -60.997 | -61.4548 | -61.3953 | 0.022888 | 60.141 | -61.2854 | 60.3745 | -61.1938 | -61.2991 | -61.3129 | -0.022889 | -0.23346 | 0.10986 | 0.23804 | -0.16022 | -0.21973 | -0.13733 | -0.19684 | -0.050354 | -0.19684 | 0.036621 | 0.041198 | -0.07782 | -0.064087 | -0.027466 | -0.013733 | 0.26093 | 121.7056 | 0.091552 | 121.6599 | 121.3623 | 121.4264 | 121.3394 | 121.376 | -121.5958 | -121.6232 | 121.6827 | 121.6095 | 61.1298 | 61.2579
299.2812 | 121.8338 | -61.2854 | 60.3973 | -0.051651 | 0.0048214 | 0.065396 | 0.062671 | -0.0034095 | -0.01053 | -0.0019461 | -0.10159 | 0.0048833 | 0.065132 | 0.056454 | -0.01132 | 0.025272 | -0.0068615 | -0.045776 | 60.2142 | -61.2396 | 60.3882 | -61.0611 | -61.4731 | -61.441 | -0.004578 | 60.2142 | -61.2625 | 60.3561 | -61.2167 | -61.3541 | -61.3495 | 0.045776 | -0.18311 | -0.009155 | 0.2243 | -0.15564 | -0.18768 | -0.20142 | -0.23346 | 0.022888 | -0.18311 | -0.041199 | 0.068664 | -0.064087 | -0.068665 | -0.086975 | -0.091553 | 0.17853 | 121.6278 | 0.045776 | 121.6187 | 121.4539 | 121.4767 | 121.4996 | 121.4996 | -121.637 | -121.6599 | 121.6736 | 121.6415 | 61.2396 | 61.2808
300.9688 | 121.9299 | -61.1618 | 60.379 | -0.097427 | 0.0050352 | 0.066251 | 0.058825 | 0.00043587 | -0.007966 | -0.0025869 | 0.017425 | 0.0018927 | 0.066841 | 0.051327 | -0.011961 | 0.024631 | -0.0049389 | 0.068665 | 60.1959 | -61.1618 | 60.5576 | -60.8643 | -61.3129 | -61.2991 | 0.21057 | 60.1959 | -61.203 | 60.4889 | -61.0474 | -61.1847 | -61.2213 | 0 | -0.1831 | 0.17853 | 0.29755 | -0.13733 | -0.15106 | -0.13733 | -0.15106 | -0.041199 | -0.1831 | 0.10986 | 0.11444 | -0.059509 | -0.022888 | -0.01831 | 0.018311 | 0.29755 | 121.7194 | 0.15564 | 121.6919 | 121.3577 | 121.3989 | 121.3577 | 121.3577 | -121.5408 | -121.582 | 121.7194 | 121.6507 | 61.2305 | 61.3724
302.7188 | 121.8201 | -61.2946 | 60.3287 | -0.15846 | 0.0080258 | 0.067105 | 0.065875 | -0.0014867 | -0.0049754 | 0.00061746 | -0.09549 | 0.0061651 | 0.0662 | 0.061368 | -0.012174 | 0.024204 | -0.0066479 | -0.21973 | 60.1456 | -61.3266 | 60.3058 | -61.1618 | -61.6241 | -61.5692 | -0.17853 | 60.1273 | -61.377 | 60.2692 | -61.3449 | -61.4639 | -61.4365 | -0.032043 | -0.1831 | -0.022888 | 0.13275 | -0.27466 | -0.32959 | -0.24262 | -0.29755 | -0.082397 | -0.20142 | -0.059509 | -0.050354 | -0.14191 | -0.16937 | -0.059509 | -0.086975 | 0.1648 | 121.6324 | 0.032043 | 121.6461 | 121.4722 | 121.5042 | 121.4401 | 121.4218 | -121.6553 | -121.7056 | 121.6003 | 121.5637 | 61.0748 | 61.116
304.4531 | 121.9162 | -61.235 | 60.3333 | -0.097427 | 0.0065304 | 0.066892 | 0.06203 | 0.0032129 | -0.0077524 | -0.0032277 | -0.0069885 | 0.0044561 | 0.066627 | 0.049832 | -0.01132 | 0.024417 | -0.0017347 | -0.11902 | 60.141 | -61.2579 | 60.4477 | -60.9833 | -61.4594 | -61.3953 | 0.032043 | 60.0998 | -61.3083 | 60.3882 | -61.1755 | -61.2991 | -61.2991 | -0.022889 | -0.19226 | 0.11444 | 0.25177 | -0.16022 | -0.22431 | -0.13733 | -0.20142 | -0.073243 | -0.23346 | 0.054932 | 0.059509 | -0.064087 | -0.064087 | 0.009156 | 0.009156 | 0.27466 | 121.7056 | 0.13275 | 121.6965 | 121.3989 | 121.4081 | 121.376 | 121.3348 | -121.5912 | -121.6415 | 121.6827 | 121.6232 | 61.116 | 61.2671
306.2031 | 121.9208 | -61.2808 | 60.3149 | -0.12032 | 0.0065304 | 0.064969 | 0.063311 | -0.0010595 | -0.0064706 | -0.00023714 | -0.10159 | 0.0033881 | 0.064704 | 0.055813 | -0.01367 | 0.027835 | -0.0021619 | -0.21057 | 60.1364 | -61.2991 | 60.3699 | -61.0886 | -61.5417 | -61.4594 | -0.064087 | 60.1044 | -61.3174 | 60.3653 | -61.1984 | -61.3586 | -61.3083 | -0.01831 | -0.17853 | 0.054932 | 0.19226 | -0.17853 | -0.26093 | -0.16022 | -0.24262 | -0.036621 | -0.21057 | 0.050354 | 0.082398 | -0.027466 | -0.07782 | 0.009155 | -0.041199 | 0.21057 | 121.669 | 0.11902 | 121.6827 | 121.4355 | 121.4218 | 121.4172 | 121.3852 | -121.6141 | -121.6324 | 121.6507 | 121.6461 | 61.0703 | 61.2167
307.9375 | 121.8613 | -61.2579 | 60.3378 | -0.036392 | 0.007385 | 0.066464 | 0.063952 | -0.0014867 | -0.0071116 | -0.0023733 | -0.089386 | 0.0048833 | 0.065559 | 0.06564 | -0.012174 | 0.024204 | -0.0062207 | -0.050354 | 60.2234 | -61.2671 | 60.4294 | -61.0428 | -61.4777 | -61.4594 | 0.041199 | 60.1685 | -61.3037 | 60.3516 | -61.203 | -61.3449 | -61.3586 | -0.009155 | -0.11444 | 0.091552 | 0.21515 | -0.20142 | -0.21973 | -0.19226 | -0.21057 | -0.045776 | -0.16937 | 0.013732 | 0.054932 | -0.10071 | -0.086975 | -0.054932 | -0.041199 | 0.2243 | 121.6965 | 0.10071 | 121.6553 | 121.4905 | 121.4722 | 121.4813 | 121.4264 | -121.6049 | -121.6415 | 121.6873 | 121.6095 | 61.2076 | 61.2991
309.625 | 121.8109 | -61.3129 | 60.2875 | -0.12794 | 0.0065304 | 0.06796 | 0.06502 | -0.0029821 | -0.006898 | -0.0040823 | -0.098541 | 0.0059515 | 0.066413 | 0.058163 | -0.011747 | 0.026126 | -0.00045291 | -0.20142 | 60.173 | -61.3129 | 60.3104 | -61.171 | -61.6058 | -61.5509 | -0.18768 | 60.1501 | -61.3586 | 60.2417 | -61.3632 | -61.4822 | -61.4548 | 0 | -0.11444 | 0.022888 | 0.14191 | -0.23804 | -0.29297 | -0.23804 | -0.29297 | -0.045777 | -0.13733 | -0.045777 | -0.050354 | -0.14191 | -0.16937 | -0.09613 | -0.1236 | 0.14191 | 121.6232 | -0.004577 | 121.6003 | 121.4859 | 121.5088 | 121.4859 | 121.463 | -121.6003 | -121.6461 | 121.6232 | 121.5546 | 61.1114 | 61.1252
311.3594 | 121.8201 | -61.2534 | 60.379 | -0.051651 | 0.0041806 | 0.065396 | 0.061389 | -0.0053321 | -0.0092478 | -0.0019461 | -0.052765 | 0.0048833 | 0.067268 | 0.056241 | -0.0098246 | 0.023349 | -0.0019483 | -0.036621 | 60.2417 | -61.2579 | 60.4065 | -61.0519 | -61.4731 | -61.4456 | 0.004578 | 60.2051 | -61.2946 | 60.3333 | -61.2305 | -61.3586 | -61.3632 | -0.004578 | -0.13733 | 0.027466 | 0.20142 | -0.19226 | -0.21973 | -0.18768 | -0.21515 | -0.041199 | -0.17395 | -0.045776 | 0.022888 | -0.10986 | -0.10529 | -0.068664 | -0.064087 | 0.20599 | 121.6644 | 0.064087 | 121.6278 | 121.4996 | 121.4996 | 121.4951 | 121.4584 | -121.637 | -121.6736 | 121.6599 | 121.5866 | 61.2167 | 61.2579
313.1094 | 121.9437 | -61.1801 | 60.379 | -0.11269 | 0.0061032 | 0.066251 | 0.060321 | -0.0017005 | -0.0092478 | -0.0038687 | 0.0082703 | 0.0036017 | 0.066841 | 0.050046 | -0.010465 | 0.024204 | -0.0053661 | -0.059509 | 60.173 | -61.2076 | 60.4752 | -60.9421 | -61.3907 | -61.3358 | 0.10986 | 60.1639 | -61.235 | 60.4431 | -61.0886 | -61.2076 | -61.235 | -0.027466 | -0.20599 | 0.096131 | 0.23804 | -0.15564 | -0.21057 | -0.12817 | -0.18311 | -0.054931 | -0.21515 | 0.064087 | 0.091553 | -0.054931 | -0.027466 | 0 | 0.027465 | 0.2655 | 121.6827 | 0.14648 | 121.6782 | 121.3806 | 121.3989 | 121.3531 | 121.344 | -121.5866 | -121.6141 | 121.6553 | 121.6232 | 61.1206 | 61.29
314.7812 | 121.8201 | -61.2991 | 60.3195 | -0.10506 | 0.0065304 | 0.065824 | 0.063525 | 0.0023585 | -0.0090342 | -0.0042959 | -0.092438 | 0.0036017 | 0.066841 | 0.051968 | -0.0096108 | 0.024417 | -0.0049389 | -0.23346 | 60.1318 | -61.3403 | 60.3104 | -61.1618 | -61.6013 | -61.5326 | -0.14648 | 60.141 | -61.3403 | 60.2692 | -61.322 | -61.4502 | -61.4182 | -0.041199 | -0.18768 | -0.009155 | 0.13733 | -0.23346 | -0.30212 | -0.19226 | -0.26093 | -0.041199 | -0.17853 | -0.050354 | -0.022888 | -0.11902 | -0.15106 | -0.07782 | -0.10986 | 0.17853 | 121.6507 | 0.018311 | 121.6095 | 121.4722 | 121.4813 | 121.431 | 121.4401 | -121.6599 | -121.6599 | 121.6095 | 121.5683 | 61.0657 | 61.1526
316.5312 | 121.9666 | -61.1755 | 60.3882 | -0.074539 | 0.0035398 | 0.066892 | 0.059253 | -0.0036231 | -0.008607 | -0.00066434 | 0.0082703 | 0.0031745 | 0.067268 | 0.051327 | -0.013029 | 0.024844 | -0.0055799 | 0.027466 | 60.1868 | -61.1938 | 60.5301 | -60.8734 | -61.3266 | -61.2946 | 0.17853 | 60.173 | -61.2167 | 60.4889 | -61.0428 | -61.1755 | -61.1984 | -0.018311 | -0.20142 | 0.14191 | 0.30212 | -0.11902 | -0.15106 | -0.10071 | -0.13275 | -0.041199 | -0.21515 | 0.10071 | 0.13275 | -0.022888 | 0 | 0.018311 | 0.041199 | 0.32044 | 121.7239 | 0.17395 | 121.7056 | 121.3806 | 121.3898 | 121.3623 | 121.3486 | -121.582 | -121.6049 | 121.7056 | 121.6644 | 61.203 | 61.3541
318.2969 | 121.9391 | -61.2534 | 60.2783 | -0.16609 | 0.0061032 | 0.066251 | 0.060962 | -0.00041873 | -0.0060434 | -0.00066434 | -0.031403 | 0.0061651 | 0.067054 | 0.054745 | -0.01367 | 0.026981 | -0.0025891 | -0.13275 | 60.0815 | -61.29 | 60.4431 | -61.0016 | -61.4685 | -61.4136 | 0 | 60.0861 | -61.3083 | 60.3836 | -61.1847 | -61.2946 | -61.2991 | -0.036621 | -0.19684 | 0.16479 | 0.25177 | -0.16022 | -0.21515 | -0.1236 | -0.17853 | -0.054932 | -0.19226 | 0.10529 | 0.068665 | -0.045776 | -0.041199 | 0.009156 | 0.013733 | 0.28839 | 121.7331 | 0.1236 | 121.6919 | 121.3715 | 121.3943 | 121.3348 | 121.3394 | -121.5683 | -121.5866 | 121.6965 | 121.637 | 61.1206 | 61.2534
319.9844 | 121.8292 | -61.2122 | 60.4111 | -0.074539 | 0.0058896 | 0.063687 | 0.061175 | -0.0031957 | -0.009675 | -0.0023733 | -0.01004 | 0.0040289 | 0.067695 | 0.049191 | -0.0093972 | 0.024631 | -0.0038709 | 0.054932 | 60.2142 | -61.1984 | 60.4843 | -60.9558 | -61.3861 | -61.3449 | 0.11444 | 60.2463 | -61.2305 | 60.3516 | -61.1755 | -61.2946 | -61.3312 | 0.013733 | -0.19684 | 0.073242 | 0.25635 | -0.13275 | -0.17395 | -0.14648 | -0.18768 | -0.018311 | -0.16479 | -0.05951 | 0.036621 | -0.11902 | -0.082398 | -0.10071 | -0.064087 | 0.24261 | 121.6827 | 0.054932 | 121.582 | 121.4127 | 121.4767 | 121.4264 | 121.4584 | -121.6095 | -121.6415 | 121.6965 | 121.5637 | 61.2671 | 61.3266
321.7344 | 121.9025 | -61.1847 | 60.4065 | -0.074539 | 0.0050352 | 0.067533 | 0.060107 | -0.0042639 | -0.0073252 | -0.0032277 | -0.01004 | 0.0050971 | 0.06385 | 0.051327 | -0.013883 | 0.023776 | -0.0040845 | 0.073242 | 60.1913 | -61.1893 | 60.5209 | -60.9192 | -61.3358 | -61.3037 | 0.17395 | 60.173 | -61.2076 | 60.4477 | -61.1023 | -61.2213 | -61.2442 | -0.004578 | -0.21515 | 0.11444 | 0.2655 | -0.11902 | -0.15106 | -0.11444 | -0.14648 | -0.022889 | -0.23346 | 0.041199 | 0.082397 | -0.05951 | -0.036621 | -0.036621 | -0.013732 | 0.27008 | 121.7102 | 0.10529 | 121.6553 | 121.3806 | 121.3806 | 121.376 | 121.3577 | -121.5958 | -121.6141 | 121.7056 | 121.6324 | 61.2579 | 61.3586
323.5 | 121.9162 | -61.1847 | 60.3699 | -0.10506 | 0.0035398 | 0.064115 | 0.061175 | -0.0031957 | -0.007966 | -0.0030141 | 0.0082703 | 0.0029607 | 0.066841 | 0.050259 | -0.011106 | 0.023135 | -0.0019483 | -0.050354 | 60.173 | -61.2167 | 60.4477 | -60.9924 | -61.409 | -61.3724 | 0.07782 | 60.1593 | -61.2534 | 60.4294 | -61.1206 | -61.2305 | -61.2488 | -0.032044 | -0.19684 | 0.07782 | 0.19226 | -0.18768 | -0.22431 | -0.15564 | -0.19226 | -0.068665 | -0.21057 | 0.059509 | 0.064087 | -0.064087 | -0.045777 | 0.004578 | 0.022888 | 0.2243 | 121.6644 | 0.13275 | 121.6827 | 121.3898 | 121.4127 | 121.3577 | 121.344 | -121.5866 | -121.6232 | 121.6324 | 121.6141 | 61.1343 | 61.2625
325.25 | 121.907 | -61.2762 | 60.2783 | -0.10506 | 0.0061032 | 0.066251 | 0.063525 | 0.00086307 | -0.006257 | -0.0040823 | -0.1077 | 0.0055243 | 0.065986 | 0.051541 | -0.013029 | 0.026981 | -0.0045117 | -0.21057 | 60.1593 | -61.2946 | 60.3607 | -61.0977 | -61.5829 | -61.5143 | -0.09613 | 60.1181 | -61.3266 | 60.3378 | -61.2579 | -61.3815 | -61.3678 | -0.018311 | -0.11902 | 0.082398 | 0.17853 | -0.23804 | -0.3067 | -0.21973 | -0.28839 | -0.050354 | -0.16022 | 0.05951 | 0.01831 | -0.091553 | -0.10529 | -0.041199 | -0.054932 | 0.19684 | 121.6553 | 0.068664 | 121.6644 | 121.4539 | 121.4447 | 121.4355 | 121.3943 | -121.5729 | -121.6049 | 121.637 | 121.6141 | 61.0657 | 61.1801
326.9375 | 121.8567 | -61.2442 | 60.3928 | -0.051651 | 0.0063168 | 0.061978 | 0.065234 | -0.0023413 | -0.006898 | -0.0034415 | -0.092438 | 0.0059515 | 0.067268 | 0.054959 | -0.013883 | 0.026126 | -0.0077161 | -0.050354 | 60.2417 | -61.2442 | 60.3836 | -61.0748 | -61.4731 | -61.4594 | 0.013733 | 60.2234 | -61.2579 | 60.347 | -61.2122 | -61.3632 | -61.3541 | 0 | -0.15106 | -0.009155 | 0.16937 | -0.21515 | -0.22888 | -0.21515 | -0.22888 | -0.013733 | -0.16937 | -0.045776 | 0.032044 | -0.10986 | -0.11902 | -0.09613 | -0.10528 | 0.16937 | 121.6278 | 0.045777 | 121.6049 | 121.4859 | 121.4813 | 121.4859 | 121.4676 | -121.637 | -121.6507 | 121.6278 | 121.5912 | 61.1938 | 61.2579
328.6875 | 121.843 | -61.3083 | 60.3287 | -0.10506 | 0.0078122 | 0.065824 | 0.064166 | 0.0040675 | -0.0071116 | -0.0032277 | -0.10159 | 0.0040289 | 0.064918 | 0.058377 | -0.011533 | 0.023349 | -0.0013073 | -0.23804 | 60.1456 | -61.3312 | 60.3012 | -61.171 | -61.6013 | -61.5601 | -0.16937 | 60.141 | -61.3586 | 60.2737 | -61.3266 | -61.4639 | -61.4227 | -0.022888 | -0.1831 | -0.027466 | 0.13733 | -0.25177 | -0.29297 | -0.22888 | -0.27008 | -0.050354 | -0.18768 | -0.054931 | -0.01831 | -0.11444 | -0.15564 | -0.064086 | -0.10529 | 0.16022 | 121.6324 | 0.032044 | 121.6324 | 121.4767 | 121.4996 | 121.4539 | 121.4493 | -121.6599 | -121.6873 | 121.6095 | 121.582 | 61.0703 | 61.1389
330.4375 | 121.9391 | -61.1847 | 60.4019 | -0.074539 | 0.0048214 | 0.064969 | 0.061389 | -0.0025549 | -0.006898 | -0.00066434 | 0.017425 | 0.0023199 | 0.068122 | 0.045987 | -0.011533 | 0.023776 | -0.0042981 | 0.059509 | 60.1685 | -61.203 | 60.5621 | -60.8505 | -61.3174 | -61.2854 | 0.20599 | 60.1959 | -61.2305 | 60.4889 | -61.0565 | -61.1801 | -61.203 | -0.018311 | -0.23346 | 0.16022 | 0.33417 | -0.10071 | -0.13275 | -0.082397 | -0.11444 | -0.045777 | -0.20599 | 0.086975 | 0.12817 | -0.018311 | 0.004577 | 0.027466 | 0.050354 | 0.35248 | 121.7651 | 0.17395 | 121.7194 | 121.3715 | 121.4264 | 121.3531 | 121.3806 | -121.6049 | -121.6324 | 121.7468 | 121.6736 | 61.2442 | 61.3907
332.1875 | 121.8292 | -61.2946 | 60.3104 | -0.074539 | 0.0052488 | 0.066251 | 0.064807 | 0.0023585 | -0.006898 | -0.0013051 | -0.083283 | 0.0025335 | 0.066627 | 0.052609 | -0.011747 | 0.024417 | -0.0025891 | -0.2243 | 60.1456 | -61.3129 | 60.3058 | -61.1481 | -61.6013 | -61.5509 | -0.13733 | 60.1364 | -61.3449 | 60.2783 | -61.3129 | -61.4456 | -61.4273 | -0.01831 | -0.16479 | -0.004578 | 0.14648 | -0.25635 | -0.3067 | -0.23804 | -0.28839 | -0.050354 | -0.17395 | -0.032044 | -0.01831 | -0.13275 | -0.15106 | -0.082397 | -0.10071 | 0.16479 | 121.6187 | 0.032044 | 121.6232 | 121.4584 | 121.4813 | 121.4401 | 121.431 | -121.6232 | -121.6553 | 121.6003 | 121.5729 | 61.0703 | 61.1572
333.875 | 121.8613 | -61.2396 | 60.3653 | -0.089798 | 0.0054624 | 0.066678 | 0.065448 | -0.0014867 | -0.0049754 | -0.0042959 | -0.083283 | 0.0044561 | 0.063423 | 0.056241 | -0.014311 | 0.025912 | -0.0051525 | -0.050354 | 60.1913 | -61.2854 | 60.3928 | -61.0428 | -61.4822 | -61.4639 | 0.045776 | 60.173 | -61.29 | 60.3653 | -61.2076 | -61.3632 | -61.3632 | -0.045776 | -0.17395 | 0.027466 | 0.19684 | -0.2243 | -0.24262 | -0.17853 | -0.19684 | -0.050354 | -0.19226 | 0 | 0.032043 | -0.1236 | -0.1236 | -0.073242 | -0.073242 | 0.24261 | 121.6782 | 0.082397 | 121.6553 | 121.4767 | 121.463 | 121.431 | 121.4127 | -121.6507 | -121.6553 | 121.6324 | 121.6049 | 61.1893 | 61.2854
335.6094 | 121.7972 | -61.3129 | 60.3241 | -0.082169 | 0.0080258 | 0.066464 | 0.063098 | 0.00022207 | -0.0081796 | -0.0032277 | -0.092438 | 0.0038153 | 0.064704 | 0.062436 | -0.0098246 | 0.022708 | -0.0075025 | -0.20142 | 60.1685 | -61.3403 | 60.3287 | -61.1572 | -61.5921 | -61.5555 | -0.16022 | 60.1318 | -61.3586 | 60.2463 | -61.3403 | -61.4777 | -61.4548 | -0.027466 | -0.15564 | 0.004577 | 0.15564 | -0.24262 | -0.27924 | -0.21515 | -0.25177 | -0.045777 | -0.19226 | -0.07782 | -0.027466 | -0.14191 | -0.16479 | -0.09613 | -0.11902 | 0.1831 | 121.669 | 0.018311 | 121.6049 | 121.5088 | 121.4905 | 121.4813 | 121.4447 | -121.6644 | -121.6827 | 121.6415 | 121.5591 | 61.1114 | 61.1526
337.3594 | 121.8521 | -61.2396 | 60.4111 | -0.074539 | 0.0048214 | 0.064542 | 0.060534 | -0.0036231 | -0.0073252 | -0.0015189 | -0.068024 | 0.0059515 | 0.067054 | 0.050046 | -0.01132 | 0.025912 | -0.0034435 | -0.032043 | 60.2646 | -61.2442 | 60.3882 | -61.0611 | -61.4731 | -61.4685 | 0.009155 | 60.2142 | -61.2762 | 60.3378 | -61.2213 | -61.3495 | -61.3403 | -0.004578 | -0.14648 | -0.022888 | 0.17853 | -0.22888 | -0.23346 | -0.2243 | -0.22888 | -0.036621 | -0.19684 | -0.073242 | 0.018311 | -0.10071 | -0.10986 | -0.064087 | -0.073242 | 0.18311 | 121.6324 | 0.054932 | 121.6141 | 121.5088 | 121.4905 | 121.5042 | 121.4539 | -121.6553 | -121.6873 | 121.6278 | 121.5775 | 61.2076 | 61.2488
339.1094 | 121.9162 | -61.2167 | 60.3653 | -0.11269 | 0.003967 | 0.065824 | 0.05968 | -0.0055457 | -0.0094614 | -0.0019461 | 0.011322 | 0.0036017 | 0.067481 | 0.049191 | -0.010038 | 0.022495 | -0.0025891 | -0.064087 | 60.173 | -61.2442 | 60.4431 | -60.9924 | -61.4319 | -61.3861 | 0.045776 | 60.1639 | -61.2534 | 60.434 | -61.1298 | -61.2442 | -61.2625 | -0.027466 | -0.19226 | 0.07782 | 0.2243 | -0.16937 | -0.21515 | -0.14191 | -0.18768 | -0.036621 | -0.20142 | 0.068665 | 0.086975 | -0.045776 | -0.027466 | -0.009155 | 0.009155 | 0.25177 | 121.6873 | 0.1236 | 121.6873 | 121.4172 | 121.4172 | 121.3898 | 121.3806 | -121.6095 | -121.6187 | 121.6599 | 121.6507 | 61.1526 | 61.2625
340.7969 | 121.9299 | -61.2808 | 60.2783 | -0.12032 | 0.0052488 | 0.065183 | 0.062457 | 8.47e-06 | -0.0071116 | -0.0045095 | -0.055817 | 0.0038153 | 0.070899 | 0.047909 | -0.014311 | 0.02399 | -0.0015209 | -0.1831 | 60.1181 | -61.322 | 60.3928 | -61.0291 | -61.5234 | -61.4502 | -0.027466 | 60.0906 | -61.3037 | 60.3699 | -61.2167 | -61.3541 | -61.2991 | -0.041198 | -0.16022 | 0.11444 | 0.25177 | -0.16937 | -0.24261 | -0.12817 | -0.20142 | -0.022888 | -0.18768 | 0.091553 | 0.064087 | -0.01831 | -0.073242 | 0.004578 | -0.050354 | 0.29297 | 121.7148 | 0.086975 | 121.6736 | 121.4401 | 121.3943 | 121.3989 | 121.3715 | -121.6003 | -121.582 | 121.6736 | 121.6507 | 61.0977 | 61.2534
342.5469 | 121.7972 | -61.2259 | 60.4065 | -0.028763 | 0.0054624 | 0.063687 | 0.060962 | -0.0019141 | -0.0083932 | -0.0013051 | -0.037506 | 0.0048833 | 0.0662 | 0.058804 | -0.012174 | 0.025058 | -0.0038709 | -0.041199 | 60.2509 | -61.2167 | 60.4065 | -61.0382 | -61.4502 | -61.4227 | 0.032043 | 60.228 | -61.2396 | 60.347 | -61.2167 | -61.3541 | -61.3586 | 0.009155 | -0.15564 | 0 | 0.18768 | -0.19684 | -0.2243 | -0.20599 | -0.23346 | -0.013733 | -0.17853 | -0.059509 | 0.009155 | -0.13275 | -0.12817 | -0.11902 | -0.11444 | 0.17853 | 121.6232 | 0.022888 | 121.5866 | 121.4676 | 121.4676 | 121.4767 | 121.4539 | -121.6232 | -121.6461 | 121.6324 | 121.5729 | 61.1847 | 61.2579
344.2969 | 121.907 | -61.2076 | 60.3928 | -0.097427 | 0.0054624 | 0.064969 | 0.058612 | -0.0027685 | -0.010316 | -0.0032277 | 0.0082703 | 0.0040289 | 0.067268 | 0.048123 | -0.013029 | 0.022708 | -0.0045117 | 0.050354 | 60.1959 | -61.1984 | 60.5255 | -60.9146 | -61.3358 | -61.322 | 0.15106 | 60.1822 | -61.2305 | 60.4477 | -61.116 | -61.235 | -61.2488 | 0.009156 | -0.19684 | 0.13275 | 0.29297 | -0.11444 | -0.12817 | -0.1236 | -0.13733 | -0.022888 | -0.21057 | 0.054932 | 0.091553 | -0.041198 | -0.027465 | -0.01831 | -0.004577 | 0.28381 | 121.7239 | 0.11444 | 121.6782 | 121.3943 | 121.4127 | 121.4035 | 121.3898 | -121.5912 | -121.6232 | 121.7331 | 121.6553 | 61.2579 | 61.3586
345.9844 | 121.8384 | -61.3312 | 60.3149 | -0.082169 | 0.005676 | 0.06561 | 0.064593 | 0.0034265 | -0.007966 | -0.00087794 | -0.092438 | 0.0055243 | 0.065986 | 0.0556 | -0.012815 | 0.02399 | -0.0042981 | -0.22888 | 60.1639 | -61.322 | 60.2966 | -61.171 | -61.6013 | -61.5555 | -0.1831 | 60.1318 | -61.3632 | 60.2737 | -61.3312 | -61.4502 | -61.4227 | 0.009156 | -0.15106 | -0.01831 | 0.16022 | -0.2243 | -0.27008 | -0.23346 | -0.27924 | -0.032043 | -0.1831 | -0.041198 | 0 | -0.091552 | -0.11902 | -0.059509 | -0.086975 | 0.15106 | 121.6187 | 0.032043 | 121.637 | 121.4859 | 121.4951 | 121.4951 | 121.463 | -121.637 | -121.6782 | 121.6278 | 121.6049 | 61.1023 | 61.1481
347.7344 | 121.8933 | -61.2396 | 60.3241 | -0.10506 | 0.0075986 | 0.065183 | 0.061602 | -0.00063233 | -0.0060434 | -0.0017325 | 0.0082703 | 0.0027471 | 0.0662 | 0.048123 | -0.01132 | 0.025912 | -0.0030163 | -0.10529 | 60.1685 | -61.2396 | 60.4294 | -61.0153 | -61.4456 | -61.3953 | -0.004578 | 60.1456 | -61.2625 | 60.379 | -61.1847 | -61.3037 | -61.3083 | 0 | -0.15564 | 0.10528 | 0.2243 | -0.15564 | -0.20599 | -0.15564 | -0.20599 | -0.022888 | -0.17853 | 0.054931 | 0.054932 | -0.068665 | -0.064087 | -0.045777 | -0.041199 | 0.2243 | 121.669 | 0.07782 | 121.6415 | 121.4081 | 121.4081 | 121.4081 | 121.3852 | -121.5637 | -121.5866 | 121.669 | 121.6187 | 61.1343 | 61.235
349.4688 | 121.9528 | -61.1755 | 60.3607 | -0.15846 | 0.0046078 | 0.064115 | 0.058825 | 0.00086307 | -0.008607 | 0.00040366 | 0.0052185 | 0.0038153 | 0.066841 | 0.0509 | -0.01132 | 0.022708 | -0.0042981 | 0.045776 | 60.1959 | -61.1938 | 60.5713 | -60.8368 | -61.2946 | -61.2717 | 0.21057 | 60.2051 | -61.1984 | 60.4797 | -61.0703 | -61.1664 | -61.2122 | -0.018311 | -0.16479 | 0.21057 | 0.33874 | -0.09613 | -0.11902 | -0.077819 | -0.10071 | -0.022888 | -0.15564 | 0.11902 | 0.10529 | -0.036621 | 0.009155 | -0.013733 | 0.032043 | 0.35706 | 121.7651 | 0.12817 | 121.6782 | 121.3898 | 121.4035 | 121.3715 | 121.3806 | -121.5546 | -121.5591 | 121.7468 | 121.6553 | 61.2213 | 61.3861
351.1562 | 121.8842 | -61.2442 | 60.3516 | -0.082169 | 0.0037534 | 0.063901 | 0.062671 | -0.0014867 | -0.008607 | -0.0025869 | -0.0008851 | 0.0033881 | 0.065345 | 0.055813 | -0.011961 | 0.023776 | -0.0032299 | -0.10071 | 60.1364 | -61.2534 | 60.4385 | -61.0245 | -61.4594 | -61.409 | 0.013733 | 60.1501 | -61.2625 | 60.379 | -61.1938 | -61.2946 | -61.3174 | -0.009155 | -0.21515 | 0.086976 | 0.21973 | -0.16479 | -0.21515 | -0.15564 | -0.20599 | -0.01831 | -0.20142 | 0.027466 | 0.050354 | -0.073242 | -0.050354 | -0.054932 | -0.032044 | 0.22888 | 121.6919 | 0.068664 | 121.6415 | 121.3898 | 121.4127 | 121.3806 | 121.3943 | -121.6049 | -121.6141 | 121.6827 | 121.6232 | 61.1435 | 61.2579
352.8438 | 121.907 | -61.2488 | 60.3333 | -0.15846 | 0.0069578 | 0.066037 | 0.061602 | -0.0023413 | -0.0077524 | -0.0023733 | -0.049713 | 0.0025335 | 0.064277 | 0.056241 | -0.011747 | 0.025272 | -0.0045117 | -0.11902 | 60.1318 | -61.2442 | 60.4523 | -61.0107 | -61.4548 | -61.409 | 0.027466 | 60.0861 | -61.2762 | 60.3836 | -61.1938 | -61.3083 | -61.3174 | 0.004577 | -0.20142 | 0.11902 | 0.23804 | -0.16022 | -0.20599 | -0.16479 | -0.21057 | -0.027466 | -0.24719 | 0.050354 | 0.054931 | -0.068665 | -0.05951 | -0.041199 | -0.032044 | 0.23346 | 121.6965 | 0.082397 | 121.6599 | 121.376 | 121.3623 | 121.3806 | 121.3348 | -121.5775 | -121.6095 | 121.7011 | 121.6324 | 61.1298 | 61.2762
354.5938 | 121.8246 | -61.3129 | 60.3195 | -0.074539 | 0.0058896 | 0.067746 | 0.061389 | -0.0031957 | -0.0075388 | -0.0021597 | -0.12601 | 0.0042425 | 0.067054 | 0.053891 | -0.013029 | 0.027408 | -0.0083569 | -0.10071 | 60.1547 | -61.2991 | 60.4065 | -61.0565 | -61.4914 | -61.4639 | -0.036621 | 60.1547 | -61.3174 | 60.3149 | -61.2671 | -61.4182 | -61.3861 | 0.013733 | -0.16479 | 0.086975 | 0.25635 | -0.15106 | -0.17853 | -0.1648 | -0.19226 | -0.004578 | -0.16479 | -0.004578 | 0.045776 | -0.073242 | -0.10529 | -0.068664 | -0.10071 | 0.24261 | 121.7056 | 0.050354 | 121.6324 | 121.4539 | 121.4722 | 121.4676 | 121.4676 | -121.6187 | -121.637 | 121.7194 | 121.6278 | 61.2122 | 61.2762
356.3125 | 121.9528 | -61.1755 | 60.3882 | -0.11269 | 0.0052488 | 0.065824 | 0.059466 | -0.0038367 | -0.0081796 | -0.0025869 | 0.0052185 | 0.0031745 | 0.0662 | 0.0556 | -0.012602 | 0.023135 | -0.00088011 | 0.064087 | 60.2005 | -61.1984 | 60.5576 | -60.8826 | -61.3174 | -61.2946 | 0.20142 | 60.2051 | -61.203 | 60.4752 | -61.0703 | -61.1755 | -61.203 | -0.022888 | -0.18768 | 0.16937 | 0.29297 | -0.11902 | -0.14191 | -0.096131 | -0.11902 | -0.027466 | -0.18311 | 0.086975 | 0.10529 | -0.027466 | 0 | 0 | 0.027466 | 0.31586 | 121.756 | 0.13275 | 121.6782 | 121.3989 | 121.4081 | 121.376 | 121.3806 | -121.5866 | -121.5912 | 121.7331 | 121.6507 | 61.2396 | 61.377
358 | 121.9299 | -61.203 | 60.3607 | -0.11269 | 0.0041806 | 0.067533 | 0.062243 | -0.0021277 | -0.0088206 | -0.0036551 | -0.0069885 | 0.0044561 | 0.066627 | 0.048123 | -0.01132 | 0.02399 | -0.0025891 | 0.054932 | 60.2188 | -61.1755 | 60.553 | -60.878 | -61.3266 | -61.29 | 0.19684 | 60.1868 | -61.2213 | 60.4477 | -61.084 | -61.1938 | -61.2259 | 0.027466 | -0.14191 | 0.19226 | 0.32501 | -0.086975 | -0.1236 | -0.11444 | -0.15106 | -0.01831 | -0.17395 | 0.086975 | 0.11902 | -0.022888 | 0.009155 | -0.004578 | 0.027465 | 0.29755 | 121.7285 | 0.13733 | 121.669 | 121.3943 | 121.4081 | 121.4218 | 121.3898 | -121.5363 | -121.582 | 121.756 | 121.6507 | 61.2579 | 61.3998
359.7344 | 121.9437 | -61.1801 | 60.3882 | -0.12794 | 0.005676 | 0.064542 | 0.061602 | -0.0072547 | -0.0083932 | -0.0028005 | -0.013092 | 0.0033881 | 0.065345 | 0.053036 | -0.014097 | 0.024844 | -0.0034435 | 0.054932 | 60.1776 | -61.1847 | 60.5438 | -60.8597 | -61.3083 | -61.2717 | 0.20599 | 60.2051 | -61.2122 | 60.4706 | -61.0657 | -61.1526 | -61.2076 | -0.004577 | -0.21057 | 0.15564 | 0.32044 | -0.091552 | -0.12817 | -0.086975 | -0.1236 | -0.032043 | -0.18311 | 0.082397 | 0.11444 | -0.027466 | 0.027466 | 0.004577 | 0.059509 | 0.32501 | 121.7285 | 0.14648 | 121.6827 | 121.3623 | 121.4172 | 121.3577 | 121.3852 | -121.5729 | -121.6003 | 121.7239 | 121.6507 | 61.235 | 61.3861
361.4062 | 121.9574 | -61.203 | 60.3607 | -0.12032 | 0.0043942 | 0.064115 | 0.060962 | -0.0051183 | -0.0081796 | -0.0013051 | -0.0008851 | 0.0038153 | 0.066627 | 0.055813 | -0.012174 | 0.02399 | -0.0060071 | 0.009155 | 60.2005 | -61.1847 | 60.5347 | -60.9329 | -61.3541 | -61.3083 | 0.16937 | 60.1776 | -61.2396 | 60.4706 | -61.0748 | -61.1938 | -61.2213 | 0.018311 | -0.16022 | 0.17395 | 0.27008 | -0.10529 | -0.15106 | -0.1236 | -0.16937 | -0.036621 | -0.18311 | 0.10986 | 0.12817 | -0.01831 | 0.009155 | 0.018311 | 0.045776 | 0.25177 | 121.7194 | 0.16479 | 121.7102 | 121.3852 | 121.4172 | 121.4035 | 121.3806 | -121.5454 | -121.6003 | 121.7377 | 121.6736 | 61.2122 | 61.3724
363.1719 | 121.8338 | -61.29 | 60.3104 | -0.05928 | 0.0078122 | 0.065183 | 0.065234 | 0.0027857 | -0.0088206 | -0.00066434 | -0.1138 | 0.0057379 | 0.066413 | 0.05795 | -0.012174 | 0.026553 | -0.0045117 | -0.09613 | 60.173 | -61.2762 | 60.4065 | -61.0611 | -61.5051 | -61.4777 | -0.018311 | 60.1776 | -61.322 | 60.3149 | -61.2808 | -61.4273 | -61.3998 | 0.013733 | -0.13733 | 0.09613 | 0.22888 | -0.18768 | -0.21515 | -0.20142 | -0.22888 | -0.032043 | -0.13275 | 0.004577 | 0.009155 | -0.10986 | -0.13733 | -0.07782 | -0.10529 | 0.21515 | 121.6827 | 0.041198 | 121.637 | 121.4493 | 121.4996 | 121.463 | 121.4676 | -121.5866 | -121.6324 | 121.6965 | 121.6049 | 61.1938 | 61.2717
364.9219 | 121.9254 | -61.171 | 60.3653 | -0.10506 | 0.0061032 | 0.065396 | 0.059893 | -0.00063233 | -0.007966 | -0.0023733 | -0.019196 | 0.0031745 | 0.064704 | 0.048123 | -0.011533 | 0.022922 | -0.0066479 | -0.068665 | 60.173 | -61.2442 | 60.4523 | -60.9833 | -61.3998 | -61.3541 | 0.073242 | 60.173 | -61.2167 | 60.4431 | -61.1023 | -61.2122 | -61.2488 | -0.073243 | -0.19226 | 0.086976 | 0.18768 | -0.18311 | -0.22888 | -0.10986 | -0.15564 | -0.045777 | -0.19226 | 0.07782 | 0.068664 | -0.07782 | -0.041199 | -0.032043 | 0.004578 | 0.26093 | 121.6965 | 0.11444 | 121.6599 | 121.4172 | 121.3898 | 121.344 | 121.344 | -121.6095 | -121.582 | 121.6232 | 121.6141 | 61.1023 | 61.2442
366.6094 | 121.9162 | -61.1893 | 60.3699 | -0.082169 | 0.0054624 | 0.064328 | 0.060962 | -0.0021277 | -0.008607 | -0.00023714 | -0.016144 | 0.0014655 | 0.066841 | 0.051541 | -0.012602 | 0.025485 | -0.0055799 | 0.068665 | 60.1959 | -61.1893 | 60.5576 | -60.8871 | -61.3403 | -61.2991 | 0.1831 | 60.2051 | -61.2488 | 60.4614 | -61.0886 | -61.2122 | -61.235 | 0 | -0.17395 | 0.18768 | 0.30212 | -0.10986 | -0.15106 | -0.10986 | -0.15106 | -0.059509 | -0.16479 | 0.091553 | 0.10071 | -0.045776 | -0.022888 | 0.013733 | 0.036621 | 0.30212 | 121.7468 | 0.16022 | 121.7102 | 121.3852 | 121.4539 | 121.3852 | 121.3943 | -121.5591 | -121.6187 | 121.7468 | 121.6507 | 61.2579 | 61.3724
368.375 | 121.8933 | -61.2396 | 60.3561 | -0.15083 | 0.0054624 | 0.066037 | 0.060321 | -0.00041873 | -0.0083932 | -0.0028005 | -0.064972 | 0.0048833 | 0.064918 | 0.046414 | -0.011106 | 0.027194 | -0.0060071 | -0.10986 | 60.1501 | -61.2488 | 60.4385 | -61.0016 | -61.4594 | -61.3998 | 0.009155 | 60.1501 | -61.2854 | 60.379 | -61.1984 | -61.322 | -61.3083 | -0.009155 | -0.20599 | 0.082398 | 0.23804 | -0.16022 | -0.21973 | -0.15106 | -0.21057 | -0.045776 | -0.20599 | 0.022888 | 0.041199 | -0.068665 | -0.082397 | -0.022889 | -0.036621 | 0.24719 | 121.6873 | 0.086975 | 121.6644 | 121.3989 | 121.4355 | 121.3898 | 121.3898 | -121.6049 | -121.6415 | 121.6782 | 121.6187 | 61.1298 | 61.2488
370.0625 | 121.9391 | -61.1664 | 60.3516 | -0.12794 | 0.0035398 | 0.06561 | 0.062243 | -0.0038367 | -0.0083932 | -0.0042959 | -0.01004 | 0.0040289 | 0.066413 | 0.05795 | -0.011961 | 0.025058 | -0.0042981 | -0.022888 | 60.1639 | -61.2259 | 60.498 | -60.9283 | -61.3586 | -61.3174 | 0.14191 | 60.1868 | -61.235 | 60.466 | -61.0794 | -61.1938 | -61.2167 | -0.059509 | -0.18768 | 0.14648 | 0.23804 | -0.15106 | -0.19226 | -0.091553 | -0.13275 | -0.068664 | -0.16479 | 0.11444 | 0.086975 | -0.050354 | -0.027466 | 0.01831 | 0.041198 | 0.29755 | 121.7239 | 0.15564 | 121.701 | 121.3898 | 121.4218 | 121.3303 | 121.3531 | -121.5775 | -121.5866 | 121.6644 | 121.6324 | 61.1435 | 61.3083
371.8125 | 121.8201 | -61.235 | 60.4477 | -0.051651 | 0.0046078 | 0.063474 | 0.063098 | -0.0025549 | -0.0094614 | -0.0032277 | -0.06192 | 0.0031745 | 0.065772 | 0.054104 | -0.012815 | 0.024631 | -0.0023755 | -0.004578 | 60.2509 | -61.2122 | 60.4202 | -61.0519 | -61.4594 | -61.4227 | 0.041199 | 60.2417 | -61.235 | 60.3516 | -61.203 | -61.3403 | -61.3495 | 0.022888 | -0.19684 | -0.027466 | 0.1831 | -0.18768 | -0.22431 | -0.21057 | -0.24719 | 0 | -0.20599 | -0.096131 | 0.032043 | -0.11444 | -0.10529 | -0.11444 | -0.10529 | 0.16022 | 121.6324 | 0.032043 | 121.5866 | 121.463 | 121.4767 | 121.4859 | 121.4767 | -121.6599 | -121.6827 | 121.6553 | 121.5866 | 61.2305 | 61.2762
373.5938 | 121.8796 | -61.2122 | 60.3745 | -0.15083 | 0.005676 | 0.064756 | 0.060321 | -0.0036231 | -0.0064706 | -0.0015189 | -0.01004 | 0.0040289 | 0.066627 | 0.055813 | -0.012815 | 0.025485 | -0.0051525 | -0.10529 | 60.1501 | -61.2717 | 60.4431 | -61.0062 | -61.4548 | -61.3953 | 0.004578 | 60.1501 | -61.2808 | 60.3973 | -61.1893 | -61.2854 | -61.3083 | -0.059509 | -0.22431 | 0.068664 | 0.20599 | -0.18311 | -0.24262 | -0.1236 | -0.18311 | -0.068665 | -0.22431 | 0.022888 | 0.022888 | -0.096131 | -0.073242 | -0.027466 | -0.004577 | 0.2655 | 121.7148 | 0.091553 | 121.6782 | 121.4218 | 121.431 | 121.3623 | 121.3623 | -121.6461 | -121.6553 | 121.6553 | 121.6095 | 61.1069 | 61.2167
375.3438 | 121.8613 | -61.2808 | 60.3241 | -0.097427 | 0.0063168 | 0.066892 | 0.063525 | -0.00063233 | -0.0077524 | -0.0019461 | -0.11075 | 0.0046697 | 0.065345 | 0.051541 | -0.012174 | 0.024631 | -0.0030163 | -0.082397 | 60.1547 | -61.2808 | 60.4248 | -61.0611 | -61.496 | -61.4639 | -0.022888 | 60.1593 | -61.3083 | 60.3241 | -61.2579 | -61.3907 | -61.3815 | 0 | -0.16937 | 0.10071 | 0.21973 | -0.18311 | -0.21515 | -0.18311 | -0.21515 | -0.027466 | -0.1648 | 0 | 0.022888 | -0.10071 | -0.10986 | -0.073242 | -0.082397 | 0.21973 | 121.7056 | 0.050354 | 121.6324 | 121.4355 | 121.4676 | 121.4355 | 121.4401 | -121.6049 | -121.6324 | 121.7056 | 121.6049 | 61.1984 | 61.2579
377.0156 | 121.8109 | -61.2854 | 60.3241 | -0.089798 | 0.0063168 | 0.066464 | 0.064166 | 0.0012903 | -0.0088206 | -0.0010915 | -0.13211 | 0.0048833 | 0.065772 | 0.060513 | -0.011747 | 0.026767 | -0.0042981 | -0.10529 | 60.1959 | -61.2762 | 60.3882 | -61.0794 | -61.528 | -61.5005 | -0.064087 | 60.1547 | -61.3358 | 60.2875 | -61.3083 | -61.4548 | -61.4182 | 0.009155 | -0.12817 | 0.064087 | 0.20599 | -0.21515 | -0.24262 | -0.2243 | -0.25177 | -0.050354 | -0.16937 | -0.036621 | -0.022889 | -0.13275 | -0.16937 | -0.082398 | -0.11902 | 0.19684 | 121.6644 | 0.027465 | 121.6232 | 121.4722 | 121.4905 | 121.4813 | 121.4401 | -121.6003 | -121.6599 | 121.6736 | 121.5729 | 61.1801 | 61.2213
378.7812 | 121.9345 | -61.1755 | 60.3607 | -0.11269 | 0.003967 | 0.064969 | 0.061389 | -0.0038367 | -0.0060434 | -0.0032277 | 0.0021667 | 0.0042425 | 0.065559 | 0.055813 | -0.010893 | 0.025485 | -0.0068615 | 0.050354 | 60.1913 | -61.2305 | 60.553 | -60.8734 | -61.3174 | -61.2991 | 0.21515 | 60.2142 | -61.2122 | 60.4752 | -61.0657 | -61.1664 | -61.2122 | -0.054932 | -0.16937 | 0.19226 | 0.30212 | -0.1236 | -0.14191 | -0.068664 | -0.086975 | -0.036621 | -0.14648 | 0.11444 | 0.10986 | -0.036621 | 0.009155 | 0 | 0.045776 | 0.35706 | 121.7834 | 0.14648 | 121.6873 | 121.4218 | 121.4264 | 121.3669 | 121.3898 | -121.5912 | -121.5729 | 121.7285 | 121.6507 | 61.2259 | 61.3907
380.4688 | 121.7926 | -61.3266 | 60.3195 | -0.12032 | 0.0061032 | 0.068173 | 0.065875 | 0.0025721 | -0.01053 | 0.00061746 | -0.098541 | 0.0057379 | 0.065986 | 0.062008 | -0.011961 | 0.024204 | -2.571e-05 | -0.19226 | 60.1685 | -61.3358 | 60.3241 | -61.1618 | -61.6058 | -61.5692 | -0.17395 | 60.1318 | -61.3449 | 60.2692 | -61.3312 | -61.4594 | -61.4319 | -0.009155 | -0.15106 | 0.004578 | 0.1648 | -0.24262 | -0.27924 | -0.23346 | -0.27008 | -0.018311 | -0.18768 | -0.050354 | -0.004578 | -0.10529 | -0.13275 | -0.086975 | -0.11444 | 0.17395 | 121.6599 | 0.013733 | 121.6141 | 121.5042 | 121.4767 | 121.4951 | 121.4584 | -121.6553 | -121.6644 | 121.6507 | 121.5958 | 61.1343 | 61.1526
382.2188 | 121.8979 | -61.2213 | 60.3607 | -0.15846 | 0.0069578 | 0.066251 | 0.060748 | -0.0029821 | -0.008607 | -0.0013051 | -0.025299 | 0.0033881 | 0.068763 | 0.051327 | -0.011747 | 0.025699 | -0.0023755 | -0.09613 | 60.1639 | -61.2442 | 60.434 | -61.0062 | -61.4365 | -61.409 | -0.018311 | 60.1639 | -61.2762 | 60.3882 | -61.1847 | -61.2946 | -61.2946 | -0.022889 | -0.19684 | 0.073242 | 0.21515 | -0.18768 | -0.21515 | -0.16479 | -0.19226 | -0.054932 | -0.19684 | 0.027466 | 0.036621 | -0.073243 | -0.073243 | -0.018311 | -0.018311 | 0.23804 | 121.6782 | 0.091553 | 121.6644 | 121.4081 | 121.4401 | 121.3852 | 121.3852 | -121.6049 | -121.637 | 121.6553 | 121.6095 | 61.1252 | 61.203
383.9688 | 121.9025 | -61.2167 | 60.3653 | -0.1432 | 0.0048214 | 0.064542 | 0.060321 | -0.0021277 | -0.0066844 | -0.0028005 | -0.022247 | 0.0048833 | 0.067695 | 0.056668 | -0.012174 | 0.024844 | -0.0051525 | -0.064087 | 60.2005 | -61.2259 | 60.4523 | -61.0062 | -61.4365 | -61.3861 | 0.027466 | 60.1685 | -61.2717 | 60.4065 | -61.1435 | -61.2534 | -61.2671 | -0.009155 | -0.1648 | 0.086976 | 0.21057 | -0.16937 | -0.21973 | -0.16022 | -0.21057 | -0.054931 | -0.19684 | 0.041199 | 0.073242 | -0.050354 | -0.036621 | 0.004577 | 0.01831 | 0.21973 | 121.6782 | 0.12817 | 121.6782 | 121.4264 | 121.4401 | 121.4172 | 121.3852 | -121.5912 | -121.637 | 121.669 | 121.6232 | 61.1526 | 61.2442
385.6406 | 121.8613 | -61.2488 | 60.347 | -0.05928 | 0.0078122 | 0.066037 | 0.062884 | 0.0036401 | -0.007966 | -0.00087794 | -0.13211 | 0.0057379 | 0.06919 | 0.055813 | -0.014524 | 0.025272 | 0.00061529 | -0.086975 | 60.1776 | -61.2946 | 60.4156 | -61.0428 | -61.4914 | -61.4594 | 0.013733 | 60.1501 | -61.2991 | 60.3516 | -61.2305 | -61.3678 | -61.3449 | -0.045777 | -0.16937 | 0.068664 | 0.20599 | -0.21057 | -0.24262 | -0.16479 | -0.19684 | -0.050354 | -0.19684 | 0.004577 | 0.01831 | -0.096131 | -0.11902 | -0.045777 | -0.068665 | 0.25177 | 121.7102 | 0.068664 | 121.6507 | 121.4722 | 121.4493 | 121.4264 | 121.3989 | -121.6415 | -121.6461 | 121.6644 | 121.6003 | 61.1618 | 61.2625
387.375 | 121.8018 | -61.322 | 60.3149 | -0.1432 | 0.0058896 | 0.066678 | 0.062243 | 0.00022207 | -0.0092478 | -0.0017325 | -0.12296 | 0.0050971 | 0.067481 | 0.052823 | -0.012602 | 0.024417 | -0.0053661 | -0.23804 | 60.1456 | -61.3266 | 60.2829 | -61.203 | -61.6058 | -61.5738 | -0.17395 | 60.141 | -61.3541 | 60.2554 | -61.3449 | -61.4731 | -61.4456 | -0.004578 | -0.16937 | -0.032043 | 0.11902 | -0.25177 | -0.28381 | -0.24719 | -0.27924 | -0.032044 | -0.17395 | -0.059509 | -0.022889 | -0.1236 | -0.15106 | -0.091553 | -0.11902 | 0.1236 | 121.6095 | 0.009155 | 121.6095 | 121.4722 | 121.4951 | 121.4676 | 121.463 | -121.6415 | -121.669 | 121.6049 | 121.5775 | 61.084 | 61.1481
389.125 | 121.8338 | -61.2396 | 60.3836 | -0.021133 | 0.0069578 | 0.065824 | 0.061602 | 0.00086307 | -0.008607 | -2.3544e-05 | -0.058869 | 0.0068059 | 0.067268 | 0.05325 | -0.0093972 | 0.02399 | -0.0051525 | -0.036621 | 60.2234 | -61.2488 | 60.3973 | -61.0565 | -61.4914 | -61.4548 | 0.009155 | 60.2051 | -61.2808 | 60.3424 | -61.2167 | -61.3449 | -61.3312 | -0.009155 | -0.16022 | 0.013733 | 0.1831 | -0.21515 | -0.25177 | -0.20599 | -0.24262 | -0.041199 | -0.17853 | -0.041199 | 0.022888 | -0.091553 | -0.10529 | -0.050354 | -0.064087 | 0.19226 | 121.6461 | 0.064087 | 121.6232 | 121.4722 | 121.4859 | 121.463 | 121.4447 | -121.6324 | -121.6644 | 121.637 | 121.582 | 61.203 | 61.2488
390.8594 | 121.8201 | -61.2946 | 60.3058 | -0.15083 | 0.0061032 | 0.065824 | 0.064166 | 0.0034265 | -0.0081796 | -0.00087794 | -0.10464 | 0.0063787 | 0.065559 | 0.054532 | -0.014097 | 0.025058 | -0.0040845 | -0.23346 | 60.1501 | -61.3174 | 60.2966 | -61.1801 | -61.6058 | -61.5555 | -0.17395 | 60.141 | -61.3586 | 60.2737 | -61.3083 | -61.4502 | -61.409 | -0.022888 | -0.15564 | -0.009155 | 0.11444 | -0.26093 | -0.31128 | -0.23804 | -0.28839 | -0.064087 | -0.16479 | -0.032043 | -0.013733 | -0.11444 | -0.15564 | -0.050354 | -0.091552 | 0.13733 | 121.6141 | 0.050354 | 121.6324 | 121.4676 | 121.4996 | 121.4447 | 121.4355 | -121.6232 | -121.6644 | 121.5912 | 121.5683 | 61.0611 | 61.1206
392.6094 | 121.9391 | -61.1893 | 60.347 | -0.12794 | 0.0037534 | 0.065396 | 0.058184 | -0.00020513 | -0.0098886 | -0.0025869 | 0.023529 | 0.0055243 | 0.0662 | 0.049832 | -0.011961 | 0.02399 | -0.0032299 | -0.045776 | 60.173 | -61.2213 | 60.4752 | -60.965 | -61.3861 | -61.3403 | 0.11444 | 60.1776 | -61.2442 | 60.4523 | -61.0931 | -61.1938 | -61.2122 | -0.032043 | -0.17395 | 0.12817 | 0.2243 | -0.15106 | -0.19684 | -0.11902 | -0.16479 | -0.054932 | -0.16937 | 0.10529 | 0.09613 | -0.022888 | -0.004578 | 0.032044 | 0.050354 | 0.25635 | 121.6965 | 0.15106 | 121.6965 | 121.3943 | 121.4218 | 121.3623 | 121.3669 | -121.5683 | -121.5912 | 121.6644 | 121.6415 | 61.1435 | 61.3037
394.2969 | 121.9025 | -61.235 | 60.347 | -0.12794 | 0.0075986 | 0.065824 | 0.060748 | -0.0019141 | -0.0066844 | -0.00023714 | -0.01004 | 0.0038153 | 0.064491 | 0.045987 | -0.01367 | 0.023135 | -0.0047253 | -0.091553 | 60.1913 | -61.2442 | 60.4385 | -61.0062 | -61.4502 | -61.4136 | -0.004578 | 60.1364 | -61.2717 | 60.3882 | -61.1984 | -61.2991 | -61.3129 | -0.009156 | -0.15564 | 0.091553 | 0.22888 | -0.17853 | -0.21515 | -0.16937 | -0.20599 | -0.036621 | -0.21057 | 0.041199 | 0.036621 | -0.07782 | -0.064087 | -0.041199 | -0.027466 | 0.23804 | 121.6827 | 0.073242 | 121.6599 | 121.4355 | 121.4081 | 121.4264 | 121.3715 | -121.5912 | -121.6187 | 121.6736 | 121.6232 | 61.1435 | 61.2305
395.9844 | 121.8109 | -61.3129 | 60.3333 | -0.18898 | 0.0080258 | 0.06561 | 0.06438 | 0.0021447 | -0.007966 | -0.0023733 | -0.089386 | 0.0063787 | 0.06385 | 0.052182 | -0.013029 | 0.025272 | -0.0057935 | -0.2243 | 60.1685 | -61.3358 | 60.2829 | -61.1893 | -61.6196 | -61.5646 | -0.18768 | 60.1181 | -61.3724 | 60.2646 | -61.3541 | -61.4731 | -61.4273 | -0.022888 | -0.1648 | -0.050354 | 0.1236 | -0.25177 | -0.3067 | -0.22888 | -0.28381 | -0.059509 | -0.21515 | -0.068665 | -0.041199 | -0.11444 | -0.16022 | -0.054932 | -0.10071 | 0.14648 | 121.6187 | 0.01831 | 121.637 | 121.5042 | 121.4905 | 121.4813 | 121.431 | -121.669 | -121.7056 | 121.5958 | 121.5775 | 61.0886 | 61.1252
397.7344 | 121.788 | -61.3129 | 60.3241 | -0.089798 | 0.0067442 | 0.06796 | 0.061816 | -0.0031957 | -0.010743 | -0.0049367 | -0.11075 | 0.0046697 | 0.0662 | 0.060513 | -0.010465 | 0.025912 | -0.0030163 | -0.21057 | 60.1639 | -61.3174 | 60.3149 | -61.171 | -61.5921 | -61.5509 | -0.15564 | 60.1685 | -61.3403 | 60.2509 | -61.3632 | -61.4914 | -61.4548 | -0.004578 | -0.16022 | -0.009156 | 0.14191 | -0.23804 | -0.27924 | -0.23346 | -0.27466 | -0.027466 | -0.15564 | -0.073243 | -0.050354 | -0.14191 | -0.17853 | -0.11444 | -0.15106 | 0.14648 | 121.6324 | -0.022888 | 121.5912 | 121.4813 | 121.5088 | 121.4767 | 121.4813 | -121.6415 | -121.6644 | 121.6278 | 121.5637 | 61.1023 | 61.1572
399.5 | 121.8475 | -61.2854 | 60.3516 | 0.017014 | 0.0065304 | 0.065183 | 0.062243 | -0.0044775 | -0.0092478 | -0.0032277 | -0.080231 | 0.0055243 | 0.067268 | 0.049618 | -0.012388 | 0.024844 | -0.0068615 | -0.064087 | 60.2325 | -61.2488 | 60.4065 | -61.0565 | -61.4548 | -61.441 | 0 | 60.2188 | -61.2854 | 60.347 | -61.235 | -61.3632 | -61.3495 | 0.036621 | -0.11902 | 0.054932 | 0.22888 | -0.15564 | -0.16937 | -0.19226 | -0.20599 | 0 | -0.13275 | -0.004577 | 0.050354 | -0.064087 | -0.07782 | -0.064087 | -0.07782 | 0.19226 | 121.6553 | 0.050354 | 121.6324 | 121.4813 | 121.5042 | 121.5179 | 121.5042 | -121.6003 | -121.637 | 121.6919 | 121.6324 | 61.2213 | 61.2854
401.1875 | 121.8338 | -61.3037 | 60.3195 | -0.15083 | 0.0026852 | 0.066464 | 0.065661 | -0.00063233 | -0.0077524 | -0.00087794 | -0.089386 | 0.0046697 | 0.067268 | 0.057522 | -0.012174 | 0.026553 | -0.0023755 | -0.23804 | 60.1501 | -61.3174 | 60.3012 | -61.1618 | -61.5967 | -61.5326 | -0.15564 | 60.1227 | -61.3129 | 60.2783 | -61.322 | -61.441 | -61.4227 | -0.013733 | -0.16937 | -0.018311 | 0.14191 | -0.22888 | -0.29297 | -0.21515 | -0.27924 | -0.009155 | -0.19684 | -0.041199 | -0.01831 | -0.11902 | -0.13733 | -0.10986 | -0.12817 | 0.15564 | 121.6187 | -0.009155 | 121.5912 | 121.4676 | 121.4355 | 121.4539 | 121.4264 | -121.637 | -121.6324 | 121.6049 | 121.582 | 61.0657 | 61.1481
402.9531 | 121.8704 | -61.2808 | 60.3104 | -0.10506 | 0.0075986 | 0.066464 | 0.06438 | -0.0049047 | -0.0077524 | -0.0019461 | -0.077179 | 0.0050971 | 0.06855 | 0.054959 | -0.011747 | 0.024204 | 0.00018809 | -0.086975 | 60.1868 | -61.2946 | 60.4065 | -61.0336 | -61.5005 | -61.4594 | 0.018311 | 60.1685 | -61.3174 | 60.3561 | -61.2213 | -61.3678 | -61.3541 | -0.013733 | -0.1236 | 0.09613 | 0.24719 | -0.17853 | -0.21973 | -0.16479 | -0.20599 | -0.036621 | -0.14191 | 0.045776 | 0.05951 | -0.073242 | -0.086975 | -0.036621 | -0.050354 | 0.26093 | 121.7011 | 0.096131 | 121.6736 | 121.4813 | 121.4859 | 121.4676 | 121.4493 | -121.6049 | -121.6278 | 121.6873 | 121.637 | 61.1938 | 61.2991
404.7031 | 121.8613 | -61.2762 | 60.3653 | -0.06691 | 0.005676 | 0.066037 | 0.062457 | -0.0040503 | -0.0064706 | -0.0034415 | -0.074127 | 0.0042425 | 0.064918 | 0.059231 | -0.013029 | 0.024844 | -0.0038709 | -0.054932 | 60.2142 | -61.2762 | 60.3928 | -61.0565 | -61.4731 | -61.4502 | 0.013733 | 60.1822 | -61.2946 | 60.3424 | -61.2213 | -61.3449 | -61.3358 | 0 | -0.15106 | 0.027466 | 0.21973 | -0.17395 | -0.19684 | -0.17395 | -0.19684 | -0.018311 | -0.18311 | -0.022888 | 0.054932 | -0.059509 | -0.068665 | -0.041198 | -0.050354 | 0.21973 | 121.669 | 0.073243 | 121.637 | 121.4905 | 121.4767 | 121.4905 | 121.4584 | -121.6415 | -121.6599 | 121.669 | 121.6187 | 61.2213 | 61.29
406.3906 | 121.7972 | -61.3129 | 60.3516 | -0.10506 | 0.0071714 | 0.066251 | 0.060321 | -0.00020513 | -0.008607 | -0.00066434 | -0.092438 | 0.0046697 | 0.067481 | 0.054745 | -0.011961 | 0.02634 | -0.0075025 | -0.19684 | 60.1501 | -61.3174 | 60.3104 | -61.1481 | -61.6013 | -61.5509 | -0.16022 | 60.1501 | -61.3403 | 60.2692 | -61.3403 | -61.4594 | -61.4319 | -0.004578 | -0.20142 | -0.041198 | 0.16479 | -0.23804 | -0.28839 | -0.23346 | -0.28381 | -0.027466 | -0.20142 | -0.082397 | -0.027466 | -0.11902 | -0.14648 | -0.091553 | -0.11902 | 0.16937 | 121.6278 | 0 | 121.6095 | 121.4676 | 121.4905 | 121.463 | 121.463 | -121.669 | -121.6919 | 121.6232 | 121.582 | 61.116 | 61.1526
408.1562 | 121.8475 | -61.2808 | 60.3561 | -0.082169 | 0.0069578 | 0.062833 | 0.060962 | 0.0027857 | -0.0066844 | -0.0023733 | -0.071076 | 0.0053107 | 0.068122 | 0.05325 | -0.0096108 | 0.02634 | -0.0015209 | -0.054932 | 60.1959 | -61.2717 | 60.4111 | -61.0291 | -61.4548 | -61.4639 | 0.018311 | 60.1913 | -61.2762 | 60.3378 | -61.2167 | -61.3449 | -61.3449 | 0.009156 | -0.16022 | 0.054932 | 0.25177 | -0.18311 | -0.17395 | -0.19226 | -0.18311 | 0.004578 | -0.1648 | -0.01831 | 0.064087 | -0.064087 | -0.064087 | -0.068665 | -0.068665 | 0.24261 | 121.6827 | 0.059509 | 121.6141 | 121.4676 | 121.4676 | 121.4767 | 121.4722 | -121.6278 | -121.6324 | 121.6919 | 121.6187 | 61.2259 | 61.2991
410.125 | 121.8979 | -61.235 | 60.3607 | -0.17372 | 0.0058896 | 0.064115 | 0.060321 | -0.00084593 | -0.0083932 | -0.0032277 | 0.044891 | 0.0048833 | 0.067054 | 0.049832 | -0.011106 | 0.022708 | -0.0023755 | -0.10071 | 60.1913 | -61.2259 | 60.4431 | -61.0016 | -61.4502 | -61.3907 | -0.004578 | 60.1547 | -61.2625 | 60.3653 | -61.1893 | -61.2854 | -61.29 | 0.009155 | -0.16937 | 0.082397 | 0.23346 | -0.15564 | -0.21515 | -0.1648 | -0.2243 | -0.027466 | -0.20599 | 0.004577 | 0.045776 | -0.054932 | -0.050354 | -0.027466 | -0.022888 | 0.2243 | 121.669 | 0.073242 | 121.6278 | 121.4172 | 121.4172 | 121.4264 | 121.3898 | -121.5866 | -121.6232 | 121.6782 | 121.6003 | 61.1343 | 61.2305
413.9219 | 121.8567 | -61.1938 | 60.3928 | -0.11269 | 0.0063168 | 0.065396 | 0.057116 | -0.0025549 | -0.0090342 | -0.0034415 | 0.017425 | 0.0055243 | 0.066841 | 0.053464 | -0.010893 | 0.02399 | -0.0040845 | 0.041199 | 60.2097 | -61.2076 | 60.5026 | -60.9283 | -61.3449 | -61.3266 | 0.16479 | 60.2371 | -61.2305 | 60.4065 | -61.1526 | -61.2762 | -61.2808 | -0.013733 | -0.1831 | 0.10986 | 0.2655 | -0.13275 | -0.15106 | -0.11902 | -0.13733 | -0.036621 | -0.15564 | 0.013733 | 0.041199 | -0.086975 | -0.082397 | -0.050354 | -0.045776 | 0.27924 | 121.7102 | 0.07782 | 121.637 | 121.4172 | 121.4676 | 121.4035 | 121.431 | -121.6003 | -121.6232 | 121.6965 | 121.6003 | 61.235 | 61.3586
417.2656 | 121.8979 | -61.2305 | 60.3516 | -0.12032 | 0.003967 | 0.067105 | 0.062243 | -0.0025549 | -0.0081796 | -0.00045074 | -0.019196 | 0.0036017 | 0.066841 | 0.053036 | -0.013456 | 0.026553 | -0.01028 | -0.13733 | 60.1135 | -61.2717 | 60.4294 | -60.997 | -61.4594 | -61.3953 | 0.018311 | 60.1364 | -61.2625 | 60.3882 | -61.1984 | -61.3129 | -61.2991 | -0.041198 | -0.23804 | 0.07782 | 0.23346 | -0.16479 | -0.22888 | -0.1236 | -0.18768 | -0.032043 | -0.21515 | 0.036622 | 0.032044 | -0.068664 | -0.082397 | -0.036621 | -0.050354 | 0.27466 | 121.701 | 0.064087 | 121.6507 | 121.3852 | 121.3989 | 121.344 | 121.3669 | -121.6232 | -121.6141 | 121.6599 | 121.6187 | 61.0931 | 61.2488
422.9375 | 121.9299 | -61.1755 | 60.3973 | -0.082169 | 0.0067442 | 0.065824 | 0.060962 | -0.0057593 | -0.009675 | -0.0021597 | 0.011322 | 0.0031745 | 0.065345 | 0.051755 | -0.012174 | 0.024844 | -0.0042981 | 0.059509 | 60.2005 | -61.171 | 60.5438 | -60.8963 | -61.3312 | -61.3083 | 0.1831 | 60.1822 | -61.2167 | 60.4568 | -61.1069 | -61.2122 | -61.2259 | 0.004578 | -0.19684 | 0.14648 | 0.27924 | -0.13275 | -0.15564 | -0.13733 | -0.16022 | -0.041199 | -0.21515 | 0.059509 | 0.068664 | -0.050354 | -0.036621 | -0.009155 | 0.004578 | 0.27466 | 121.7148 | 0.10986 | 121.6736 | 121.3715 | 121.3989 | 121.376 | 121.3577 | -121.5683 | -121.6141 | 121.7194 | 121.6324 | 61.235 | 61.3586
424.7031 | 121.8063 | -61.235 | 60.434 | -0.044022 | 0.0050352 | 0.064328 | 0.061816 | -0.0010595 | -0.01053 | -0.0017325 | -0.046661 | 0.0048833 | 0.0662 | 0.060086 | -0.012602 | 0.025058 | -0.0051525 | -0.013733 | 60.2554 | -61.235 | 60.4111 | -61.0382 | -61.4548 | -61.4136 | 0.064087 | 60.2097 | -61.2717 | 60.3378 | -61.2167 | -61.322 | -61.3358 | 0 | -0.17853 | -0.022888 | 0.19684 | -0.17853 | -0.21973 | -0.17853 | -0.21973 | -0.036621 | -0.2243 | -0.09613 | 0.01831 | -0.10071 | -0.086975 | -0.064087 | -0.050354 | 0.19684 | 121.6461 | 0.054931 | 121.6095 | 121.4905 | 121.4813 | 121.4905 | 121.4447 | -121.669 | -121.7056 | 121.6461 | 121.5729 | 61.2213 | 61.2991
426.4531 | 121.907 | -61.235 | 60.347 | -0.12032 | 0.0065304 | 0.065396 | 0.061816 | -0.00041873 | -0.0064706 | -0.0047231 | -0.037506 | 0.0046697 | 0.0662 | 0.047696 | -0.012174 | 0.024631 | -0.0098523 | -0.11444 | 60.1273 | -61.2534 | 60.4385 | -60.9833 | -61.4685 | -61.409 | 0.027466 | 60.1318 | -61.2762 | 60.3836 | -61.1893 | -61.2854 | -61.2854 | -0.018311 | -0.21973 | 0.091553 | 0.25177 | -0.17395 | -0.23346 | -0.15564 | -0.21515 | -0.041199 | -0.21515 | 0.036621 | 0.045776 | -0.050354 | -0.050354 | -0.009155 | -0.009155 | 0.27008 | 121.6919 | 0.086975 | 121.6599 | 121.3806 | 121.4081 | 121.3623 | 121.3669 | -121.6003 | -121.6232 | 121.6736 | 121.6187 | 61.1206 | 61.2625
428.2031 | 121.843 | -61.3129 | 60.347 | -0.1432 | 0.005676 | 0.064756 | 0.065875 | -0.0021277 | -0.0098886 | -0.00087794 | -0.080231 | 0.0042425 | 0.068122 | 0.056241 | -0.012388 | 0.025699 | -0.0066479 | -0.23346 | 60.1776 | -61.3358 | 60.3104 | -61.1664 | -61.5921 | -61.5417 | -0.15106 | 60.1501 | -61.3266 | 60.2875 | -61.3129 | -61.4594 | -61.4182 | -0.022888 | -0.16937 | -0.036621 | 0.14648 | -0.22888 | -0.27924 | -0.20599 | -0.25635 | -0.013733 | -0.19684 | -0.059509 | 0 | -0.10529 | -0.14648 | -0.091553 | -0.13275 | 0.16937 | 121.6461 | 0.013733 | 121.6141 | 121.5134 | 121.4767 | 121.4905 | 121.463 | -121.6827 | -121.6736 | 121.6232 | 121.6003 | 61.0794 | 61.1618
429.9375 | 121.9482 | -61.1984 | 60.3516 | -0.10506 | 0.0061032 | 0.064542 | 0.060321 | -0.0017005 | -0.0088206 | -0.0034415 | 0.023529 | 0.0044561 | 0.067695 | 0.053036 | -0.011961 | 0.024417 | -0.0038709 | -0.032043 | 60.1822 | -61.2305 | 60.498 | -60.9375 | -61.3495 | -61.3266 | 0.15106 | 60.1868 | -61.2076 | 60.4797 | -61.0886 | -61.203 | -61.1938 | -0.032044 | -0.16937 | 0.14648 | 0.26093 | -0.12817 | -0.15106 | -0.09613 | -0.11902 | -0.009156 | -0.16479 | 0.12817 | 0.10986 | 0.004577 | -0.004578 | 0.013733 | 0.004578 | 0.29297 | 121.7285 | 0.11902 | 121.6873 | 121.4127 | 121.3943 | 121.3806 | 121.3852 | -121.582 | -121.5591 | 121.6965 | 121.6782 | 61.1664 | 61.3495
431.6094 | 121.8338 | -61.2259 | 60.3973 | -0.12032 | 0.0037534 | 0.064756 | 0.061816 | 0.0019311 | -0.0094614 | -0.0019461 | -0.037506 | 0.0050971 | 0.065986 | 0.049618 | -0.0098246 | 0.02399 | -0.011775 | 0.050354 | 60.2142 | -61.1938 | 60.4752 | -60.9512 | -61.4044 | -61.3678 | 0.091553 | 60.2371 | -61.2488 | 60.3653 | -61.1801 | -61.2991 | -61.3403 | 0.032043 | -0.18311 | 0.07782 | 0.27466 | -0.14191 | -0.17853 | -0.17395 | -0.21057 | -0.022888 | -0.16022 | -0.032044 | 0.045776 | -0.11444 | -0.073242 | -0.091553 | -0.050354 | 0.24262 | 121.669 | 0.068664 | 121.6141 | 121.4081 | 121.4859 | 121.4401 | 121.463 | -121.5912 | -121.6461 | 121.701 | 121.5912 | 61.2762 | 61.3174
433.3594 | 121.9254 | -61.2762 | 60.2783 | -0.097427 | 0.007385 | 0.064542 | 0.063525 | -0.00041873 | -0.008607 | -0.0019461 | -0.06192 | 0.0057379 | 0.067054 | 0.055173 | -0.012174 | 0.025699 | -0.0034435 | -0.21057 | 60.1501 | -61.3312 | 60.3653 | -61.0886 | -61.5509 | -61.5005 | -0.082397 | 60.1227 | -61.3403 | 60.347 | -61.2259 | -61.3586 | -61.2991 | -0.054932 | -0.12817 | 0.086975 | 0.18768 | -0.2243 | -0.27466 | -0.16937 | -0.21973 | -0.064087 | -0.15564 | 0.068665 | 0.050354 | -0.022888 | -0.082398 | 0.041199 | -0.018311 | 0.24261 | 121.6965 | 0.11444 | 121.6873 | 121.4813 | 121.463 | 121.4264 | 121.3989 | -121.6095 | -121.6187 | 121.6415 | 121.6232 | 61.0657 | 61.1938
435.0312 | 121.8521 | -61.2671 | 60.347 | -0.044022 | 0.0046078 | 0.066251 | 0.063098 | 0.00022207 | -0.008607 | -0.0010915 | -0.080231 | 0.0050971 | 0.066841 | 0.057522 | -0.013029 | 0.023563 | -0.0038709 | -0.041199 | 60.2417 | -61.2305 | 60.4065 | -61.0611 | -61.4777 | -61.4548 | 0.004578 | 60.1868 | -61.2991 | 60.3424 | -61.2122 | -61.3586 | -61.3449 | 0.036621 | -0.10529 | 0.059509 | 0.20599 | -0.18768 | -0.21057 | -0.2243 | -0.24719 | -0.032043 | -0.16022 | -0.004578 | 0.054932 | -0.07782 | -0.091553 | -0.045777 | -0.05951 | 0.16937 | 121.637 | 0.086975 | 121.6415 | 121.4722 | 121.4859 | 121.5088 | 121.4539 | -121.5775 | -121.6461 | 121.6736 | 121.6095 | 61.2259 | 61.2717
436.7188 | 121.9528 | -61.2625 | 60.2692 | -0.10506 | 0.0054624 | 0.067319 | 0.062884 | 0.0015039 | -0.0083932 | -0.0015189 | -0.058869 | 0.0063787 | 0.066413 | 0.054104 | -0.012174 | 0.025485 | -0.0030163 | -0.15106 | 60.1227 | -61.2946 | 60.4248 | -61.0336 | -61.4914 | -61.4227 | -0.004578 | 60.0906 | -61.3129 | 60.3928 | -61.1938 | -61.3266 | -61.2991 | -0.032044 | -0.14648 | 0.15564 | 0.22888 | -0.16022 | -0.22888 | -0.12817 | -0.19684 | -0.050354 | -0.17853 | 0.1236 | 0.068664 | -0.036621 | -0.064087 | 0.013733 | -0.013733 | 0.26093 | 121.7194 | 0.11902 | 121.7056 | 121.4172 | 121.4035 | 121.3852 | 121.3531 | -121.5637 | -121.582 | 121.6873 | 121.6553 | 61.1114 | 61.2579
438.4688 | 121.9025 | -61.2213 | 60.3516 | -0.12032 | 0.0037534 | 0.063687 | 0.059039 | -0.0010595 | -0.0083932 | -0.0034415 | -0.016144 | 0.0018927 | 0.067054 | 0.051114 | -0.013242 | 0.024204 | 0.0027515 | -0.091553 | 60.1685 | -61.2579 | 60.4202 | -61.0153 | -61.4456 | -61.3953 | 0.022888 | 60.1685 | -61.2762 | 60.3882 | -61.1755 | -61.29 | -61.2808 | -0.036622 | -0.18311 | 0.068665 | 0.20599 | -0.17395 | -0.22431 | -0.13733 | -0.18768 | -0.054932 | -0.18311 | 0.036622 | 0.045776 | -0.05951 | -0.068665 | -0.004578 | -0.013733 | 0.24262 | 121.6782 | 0.10071 | 121.6644 | 121.4264 | 121.4447 | 121.3898 | 121.3898 | -121.6095 | -121.6278 | 121.6415 | 121.6095 | 61.1298 | 61.2442
440.1719 | 121.9254 | -61.2534 | 60.3058 | -0.11269 | 0.0048214 | 0.065824 | 0.061602 | -0.0010595 | -0.0075388 | -0.0019461 | -0.046661 | 0.0040289 | 0.065132 | 0.054532 | -0.012388 | 0.025699 | -0.0068615 | -0.14191 | 60.1273 | -61.2854 | 60.4614 | -60.9924 | -61.4777 | -61.4136 | 0.027466 | 60.1135 | -61.3083 | 60.3882 | -61.1801 | -61.3037 | -61.2946 | -0.032043 | -0.17853 | 0.15564 | 0.26093 | -0.16022 | -0.2243 | -0.12817 | -0.19226 | -0.054932 | -0.19226 | 0.082398 | 0.073242 | -0.041199 | -0.050354 | 0.013733 | 0.004578 | 0.29297 | 121.7468 | 0.12817 | 121.6965 | 121.4127 | 121.4218 | 121.3806 | 121.3669 | -121.5912 | -121.6141 | 121.7148 | 121.6415 | 61.1114 | 61.2808
441.9062 | 121.9482 | -61.2671 | 60.2829 | -0.12032 | 0.0058896 | 0.067105 | 0.062243 | -0.0010595 | -0.0073252 | -0.0040823 | -0.058869 | 0.0033881 | 0.064704 | 0.053036 | -0.013456 | 0.02399 | -0.0055799 | -0.13733 | 60.1044 | -61.2762 | 60.4248 | -61.0291 | -61.4777 | -61.4319 | -0.009155 | 60.1044 | -61.3403 | 60.3882 | -61.2122 | -61.322 | -61.2946 | -0.009155 | -0.17853 | 0.14191 | 0.23804 | -0.16479 | -0.21057 | -0.15564 | -0.20142 | -0.073242 | -0.17853 | 0.10529 | 0.054932 | -0.027466 | -0.054931 | 0.045776 | 0.018311 | 0.24719 | 121.7011 | 0.12817 | 121.7285 | 121.3806 | 121.4447 | 121.3715 | 121.3715 | -121.5591 | -121.6232 | 121.6919 | 121.6553 | 61.1298 | 61.2579
443.5781 | 121.8796 | -61.2167 | 60.3973 | -0.11269 | 0.005676 | 0.065183 | 0.060748 | -0.0038367 | -0.0092478 | -0.0023733 | -0.046661 | 0.0038153 | 0.066841 | 0.061795 | -0.010465 | 0.024417 | -0.0040845 | -0.09613 | 60.1639 | -61.235 | 60.434 | -61.0199 | -61.4456 | -61.3998 | 0.013733 | 60.1776 | -61.2854 | 60.3836 | -61.1847 | -61.2946 | -61.2946 | -0.01831 | -0.23346 | 0.036621 | 0.19684 | -0.18311 | -0.22888 | -0.1648 | -0.21057 | -0.068664 | -0.21973 | -0.013733 | 0.032044 | -0.07782 | -0.07782 | -0.009156 | -0.009156 | 0.21515 | 121.669 | 0.10071 | 121.669 | 121.3989 | 121.463 | 121.3806 | 121.3943 | -121.6324 | -121.6827 | 121.6507 | 121.6003 | 61.1206 | 61.2305
445.3125 | 121.9116 | -61.1938 | 60.4019 | -0.044022 | 0.0063168 | 0.063474 | 0.059893 | 0.00064947 | -0.0083932 | -0.0023733 | -0.016144 | 0.0044561 | 0.067054 | 0.0556 | -0.012815 | 0.024844 | -0.0049389 | 0.064087 | 60.1913 | -61.1893 | 60.5347 | -60.9238 | -61.3541 | -61.3174 | 0.1831 | 60.2005 | -61.2534 | 60.4477 | -61.1023 | -61.2122 | -61.2305 | 0.004578 | -0.21057 | 0.13275 | 0.27008 | -0.1236 | -0.16022 | -0.12817 | -0.16479 | -0.059509 | -0.20142 | 0.045776 | 0.091553 | -0.036621 | -0.01831 | 0.022888 | 0.041199 | 0.2655 | 121.7239 | 0.15106 | 121.7011 | 121.3806 | 121.4539 | 121.3852 | 121.3943 | -121.5912 | -121.6553 | 121.7285 | 121.6415 | 61.2579 | 61.377
446.9844 | 121.8292 | -61.2854 | 60.3104 | -0.089798 | 0.0054624 | 0.064542 | 0.062884 | -0.0017005 | -0.0071116 | -0.0030141 | -0.12906 | 0.0033881 | 0.065772 | 0.061795 | -0.012388 | 0.026126 | -0.0089977 | -0.11444 | 60.1593 | -61.3083 | 60.3928 | -61.0748 | -61.5143 | -61.4914 | -0.045776 | 60.173 | -61.322 | 60.2966 | -61.29 | -61.4502 | -61.4044 | -0.022889 | -0.15106 | 0.082397 | 0.21057 | -0.20599 | -0.22888 | -0.1831 | -0.20599 | -0.036621 | -0.13733 | -0.013733 | -0.004578 | -0.11902 | -0.16479 | -0.082398 | -0.12817 | 0.23346 | 121.7011 | 0.032043 | 121.6187 | 121.4676 | 121.4951 | 121.4447 | 121.4584 | -121.6187 | -121.6324 | 121.6782 | 121.582 | 61.171 | 61.2396
448.7344 | 121.7972 | -61.3449 | 60.3012 | -0.074539 | 0.0054624 | 0.066037 | 0.062884 | 0.00064947 | -0.0064706 | -0.0015189 | -0.1199 | 0.0055243 | 0.065986 | 0.055173 | -0.012815 | 0.025058 | -0.0077161 | -0.19226 | 60.1776 | -61.3129 | 60.2921 | -61.1938 | -61.6425 | -61.5829 | -0.17853 | 60.1456 | -61.3495 | 60.2509 | -61.3449 | -61.4822 | -61.4456 | 0.032044 | -0.1236 | -0.009155 | 0.15106 | -0.23804 | -0.29755 | -0.27008 | -0.32959 | -0.004577 | -0.15564 | -0.050354 | 0 | -0.10071 | -0.13733 | -0.096131 | -0.13275 | 0.11902 | 121.6049 | 0.004577 | 121.6003 | 121.4905 | 121.4951 | 121.5225 | 121.4905 | -121.6141 | -121.6507 | 121.637 | 121.5958 | 61.1526 | 61.1664
450.5 | 121.8567 | -61.2534 | 60.347 | -0.051651 | 0.0069578 | 0.068173 | 0.062884 | -0.0029821 | -0.007966 | -0.0034415 | -0.068024 | 0.0046697 | 0.066841 | 0.056668 | -0.010465 | 0.025485 | -0.0064343 | -0.064087 | 60.2509 | -61.2762 | 60.4065 | -61.0519 | -61.4777 | -61.4548 | 0.022888 | 60.1822 | -61.2991 | 60.3516 | -61.203 | -61.3541 | -61.3495 | -0.022888 | -0.096131 | 0.059509 | 0.20142 | -0.20142 | -0.2243 | -0.17853 | -0.20142 | -0.045776 | -0.16479 | 0.004577 | 0.050354 | -0.09613 | -0.10071 | -0.050354 | -0.054932 | 0.2243 | 121.6827 | 0.09613 | 121.6507 | 121.5271 | 121.4813 | 121.5042 | 121.4355 | -121.6232 | -121.6461 | 121.6599 | 121.6049 | 61.1893 | 61.2762
452.1719 | 121.9345 | -61.2946 | 60.26 | -0.12032 | 0.0071714 | 0.066037 | 0.060748 | -0.0014867 | -0.007966 | -0.0034415 | -0.049713 | 0.0025335 | 0.065345 | 0.054959 | -0.010465 | 0.025912 | -0.0023755 | -0.15564 | 60.1273 | -61.2991 | 60.4111 | -61.0199 | -61.4685 | -61.4319 | -0.027466 | 60.1135 | -61.322 | 60.379 | -61.1984 | -61.322 | -61.2991 | -0.004577 | -0.13275 | 0.15106 | 0.27466 | -0.13733 | -0.17395 | -0.13275 | -0.16937 | -0.027465 | -0.14648 | 0.11902 | 0.096131 | -0.004577 | -0.027465 | 0.022888 | 0 | 0.27924 | 121.7102 | 0.1236 | 121.701 | 121.4264 | 121.4355 | 121.4218 | 121.4081 | -121.5591 | -121.582 | 121.7056 | 121.6736 | 61.1389 | 61.2671
453.9062 | 121.8018 | -61.3266 | 60.3058 | -0.12032 | 0.0048214 | 0.066251 | 0.061816 | -0.0031957 | -0.008607 | -0.0017325 | -0.074127 | 0.0055243 | 0.0662 | 0.056454 | -0.012388 | 0.026553 | -0.0042981 | -0.21057 | 60.1685 | -61.3266 | 60.3012 | -61.1893 | -61.6104 | -61.5646 | -0.20599 | 60.1227 | -61.3541 | 60.2509 | -61.3541 | -61.4822 | -61.4319 | 0 | -0.13733 | -0.004578 | 0.13733 | -0.23804 | -0.28381 | -0.23804 | -0.28381 | -0.027466 | -0.1831 | -0.054932 | -0.027466 | -0.10529 | -0.15564 | -0.07782 | -0.12817 | 0.13733 | 121.6278 | 0 | 121.6049 | 121.4951 | 121.4767 | 121.4951 | 121.4493 | -121.6324 | -121.6599 | 121.6278 | 121.5775 | 61.116 | 61.1206
455.6562 | 121.9116 | -61.2213 | 60.3653 | -0.12032 | 0.0058896 | 0.064542 | 0.060321 | -0.0044775 | -0.0060434 | -0.0045095 | -0.016144 | 0.0012517 | 0.067054 | 0.048764 | -0.010679 | 0.024631 | -0.0032299 | -0.059509 | 60.2234 | -61.2305 | 60.4385 | -61.0062 | -61.4319 | -61.3953 | 0.045776 | 60.1685 | -61.2579 | 60.4065 | -61.1572 | -61.2534 | -61.2534 | -0.009156 | -0.14191 | 0.073243 | 0.21515 | -0.17395 | -0.21057 | -0.16479 | -0.20142 | -0.036622 | -0.19684 | 0.041199 | 0.064086 | -0.032044 | -0.032044 | 0.004578 | 0.004578 | 0.2243 | 121.669 | 0.10071 | 121.6644 | 121.4539 | 121.4264 | 121.4447 | 121.3898 | -121.5958 | -121.6232 | 121.6599 | 121.6278 | 61.1618 | 61.2671
457.4062 | 121.8613 | -61.2808 | 60.3516 | -0.05928 | 0.0041806 | 0.066892 | 0.061602 | -0.0051183 | -0.0077524 | -0.00045074 | -0.10464 | 0.0042425 | 0.067481 | 0.057095 | -0.012602 | 0.025912 | -0.0036573 | -0.09613 | 60.1868 | -61.2808 | 60.3928 | -61.0565 | -61.5005 | -61.4594 | 0.004578 | 60.1639 | -61.322 | 60.3241 | -61.2671 | -61.4044 | -61.3724 | 0 | -0.16479 | 0.041199 | 0.2243 | -0.17853 | -0.21973 | -0.17853 | -0.21973 | -0.041198 | -0.18768 | -0.027465 | 0.013733 | -0.091552 | -0.1236 | -0.050354 | -0.082398 | 0.2243 | 121.6736 | 0.054931 | 121.6461 | 121.4676 | 121.4859 | 121.4676 | 121.4447 | -121.6324 | -121.6736 | 121.6736 | 121.6049 | 61.1847 | 61.2854
459.1562 | 121.9666 | -61.1801 | 60.3928 | -0.074539 | 0.0026852 | 0.065183 | 0.060107 | -0.0049047 | -0.0098886 | -0.0030141 | 0.0021667 | 0.0044561 | 0.06385 | 0.054532 | -0.013242 | 0.02399 | -0.0053661 | 0.032043 | 60.2097 | -61.2259 | 60.5347 | -60.8688 | -61.3312 | -61.2991 | 0.20599 | 60.1776 | -61.2213 | 60.4889 | -61.0565 | -61.1801 | -61.1938 | -0.045776 | -0.1831 | 0.14191 | 0.31128 | -0.11902 | -0.15106 | -0.073242 | -0.10529 | -0.041198 | -0.21515 | 0.096131 | 0.1236 | -0.013733 | 0 | 0.027465 | 0.041198 | 0.35706 | 121.7606 | 0.16479 | 121.7102 | 121.4355 | 121.3989 | 121.3898 | 121.3577 | -121.6187 | -121.6141 | 121.7148 | 121.669 | 61.2122 | 61.3861
460.8438 | 121.8201 | -61.3037 | 60.3287 | -0.097427 | 0.0065304 | 0.064969 | 0.063952 | 0.0012903 | -0.0077524 | -0.0010915 | -0.092438 | 0.0048833 | 0.0662 | 0.051968 | -0.013029 | 0.025699 | -0.0010937 | -0.23346 | 60.1456 | -61.3541 | 60.2921 | -61.203 | -61.6058 | -61.5692 | -0.17395 | 60.1273 | -61.3632 | 60.2646 | -61.3312 | -61.4548 | -61.4227 | -0.050354 | -0.1831 | -0.036621 | 0.10071 | -0.2655 | -0.30212 | -0.21515 | -0.25177 | -0.059509 | -0.20142 | -0.064087 | -0.027466 | -0.11902 | -0.15106 | -0.059509 | -0.091553 | 0.15106 | 121.6461 | 0.032043 | 121.6278 | 121.4996 | 121.4905 | 121.4493 | 121.431 | -121.6827 | -121.6919 | 121.5958 | 121.5683 | 61.0703 | 61.1298
462.5938 | 121.9391 | -61.2671 | 60.2875 | -0.12032 | 0.0082394 | 0.068601 | 0.061602 | 0.0027857 | -0.0088206 | -0.0013051 | -0.049713 | 0.0046697 | 0.065559 | 0.05325 | -0.014311 | 0.027194 | -0.0038709 | -0.14191 | 60.1273 | -61.2946 | 60.4065 | -61.0291 | -61.4639 | -61.4182 | -0.027466 | 60.1044 | -61.29 | 60.3882 | -61.1984 | -61.322 | -61.2808 | -0.027466 | -0.16022 | 0.11902 | 0.23804 | -0.15106 | -0.19684 | -0.1236 | -0.16937 | -0.022888 | -0.18311 | 0.10071 | 0.068665 | -0.013733 | -0.054931 | 0.009155 | -0.032043 | 0.2655 | 121.7011 | 0.091553 | 121.6782 | 121.4218 | 121.3943 | 121.3943 | 121.3715 | -121.582 | -121.5775 | 121.6736 | 121.6553 | 61.1252 | 61.2396
464.2656 | 121.8567 | -61.203 | 60.4294 | -0.089798 | 0.0058896 | 0.064969 | 0.060534 | 0.0015039 | -0.007966 | -0.00087794 | -0.031403 | 0.0050971 | 0.067268 | 0.0509 | -0.011747 | 0.026126 | -0.0017347 | 0.050354 | 60.2051 | -61.2076 | 60.5118 | -60.9238 | -61.3358 | -61.3358 | 0.16022 | 60.2142 | -61.2213 | 60.4019 | -61.1664 | -61.2625 | -61.2762 | -0.004578 | -0.2243 | 0.082398 | 0.27924 | -0.13275 | -0.13275 | -0.12817 | -0.12817 | -0.01831 | -0.21515 | -0.027465 | 0.036621 | -0.073242 | -0.059509 | -0.054932 | -0.041199 | 0.28381 | 121.7194 | 0.054931 | 121.6232 | 121.4127 | 121.4355 | 121.4081 | 121.4172 | -121.637 | -121.6507 | 121.7148 | 121.6049 | 61.2534 | 61.3632
466.0156 | 121.8658 | -61.3083 | 60.2966 | -0.11269 | 0.0069578 | 0.06561 | 0.063311 | 0.00086307 | -0.0083932 | 0.00019006 | -0.083283 | 0.0025335 | 0.068336 | 0.0556 | -0.013883 | 0.025699 | -0.0042981 | -0.2243 | 60.1776 | -61.3174 | 60.3241 | -61.1481 | -61.5829 | -61.5372 | -0.13275 | 60.0998 | -61.3312 | 60.3104 | -61.3037 | -61.4044 | -61.3724 | -0.009155 | -0.11902 | 0.027466 | 0.16022 | -0.22888 | -0.27466 | -0.21973 | -0.2655 | -0.022888 | -0.19684 | 0.013733 | 0.004578 | -0.064086 | -0.09613 | -0.041198 | -0.073242 | 0.16937 | 121.6415 | 0.027466 | 121.6415 | 121.4951 | 121.431 | 121.4859 | 121.4081 | -121.6141 | -121.6278 | 121.6324 | 121.6187 | 61.084 | 61.1755
467.7031 | 121.9437 | -61.1618 | 60.379 | -0.13557 | 0.0033262 | 0.065183 | 0.060107 | -0.0019141 | -0.01053 | -0.0040823 | -0.0008851 | 0.0021063 | 0.066841 | 0.053891 | -0.010465 | 0.025058 | -0.0036573 | 0.041199 | 60.173 | -61.2167 | 60.553 | -60.8597 | -61.3129 | -61.2808 | 0.20599 | 60.2005 | -61.2167 | 60.4843 | -61.0748 | -61.1755 | -61.2122 | -0.054932 | -0.20599 | 0.17395 | 0.30212 | -0.11902 | -0.15106 | -0.064087 | -0.09613 | -0.054932 | -0.17853 | 0.10529 | 0.086975 | -0.050354 | -0.013733 | 0.004578 | 0.041199 | 0.35706 | 121.7697 | 0.14191 | 121.701 | 121.3898 | 121.4172 | 121.3348 | 121.3623 | -121.5958 | -121.5958 | 121.7148 | 121.6461 | 61.203 | 61.3678
469.4531 | 121.9574 | -61.2762 | 60.2875 | -0.16609 | 0.0082394 | 0.068814 | 0.06203 | -0.00063233 | -0.0077524 | -2.3544e-05 | -0.06192 | 0.0021063 | 0.067909 | 0.049191 | -0.012174 | 0.023563 | -0.0045117 | -0.15106 | 60.1364 | -61.2991 | 60.4248 | -61.0199 | -61.4731 | -61.4273 | -0.018311 | 60.0998 | -61.3129 | 60.3836 | -61.203 | -61.3174 | -61.2946 | -0.022888 | -0.15106 | 0.13733 | 0.25635 | -0.15106 | -0.19684 | -0.12817 | -0.17395 | -0.036621 | -0.18768 | 0.09613 | 0.073242 | -0.018311 | -0.041199 | 0.01831 | -0.004578 | 0.27924 | 121.7239 | 0.10986 | 121.6965 | 121.4355 | 121.4127 | 121.4127 | 121.376 | -121.5866 | -121.6003 | 121.7011 | 121.6599 | 61.1252 | 61.2579
471.2031 | 121.907 | -61.2259 | 60.3561 | -0.12794 | 0.0041806 | 0.066037 | 0.062457 | -0.0014867 | -0.0066844 | -0.0010915 | -0.028351 | 0.0038153 | 0.067481 | 0.050686 | -0.012602 | 0.026126 | -0.0051525 | -0.10986 | 60.141 | -61.2671 | 60.4294 | -61.0062 | -61.4502 | -61.3953 | 0.032043 | 60.1501 | -61.2762 | 60.3745 | -61.1938 | -61.2946 | -61.2946 | -0.041199 | -0.21515 | 0.073242 | 0.21973 | -0.16937 | -0.2243 | -0.12817 | -0.1831 | -0.050354 | -0.20599 | 0.018311 | 0.032043 | -0.068665 | -0.068665 | -0.018311 | -0.018311 | 0.26093 | 121.6965 | 0.082397 | 121.6507 | 121.4081 | 121.4264 | 121.3669 | 121.376 | -121.6232 | -121.6324 | 121.6553 | 121.6003 | 61.116 | 61.2579
472.9375 | 121.9345 | -61.2625 | 60.2966 | -0.16609 | 0.0067442 | 0.068601 | 0.062884 | -0.0017005 | -0.0066844 | -0.0036551 | -0.034454 | 0.0036017 | 0.066627 | 0.061795 | -0.014524 | 0.026126 | -0.0042981 | -0.12817 | 60.1456 | -61.2762 | 60.4431 | -61.0062 | -61.4548 | -61.4136 | 0.036621 | 60.1181 | -61.3037 | 60.3973 | -61.1847 | -61.2946 | -61.2854 | -0.013733 | -0.15106 | 0.14648 | 0.25635 | -0.15106 | -0.19226 | -0.13733 | -0.17853 | -0.041199 | -0.17853 | 0.10071 | 0.07782 | -0.022888 | -0.032044 | 0.018311 | 0.009155 | 0.27008 | 121.7194 | 0.11902 | 121.7011 | 121.4218 | 121.4218 | 121.4081 | 121.3806 | -121.5729 | -121.6003 | 121.7056 | 121.6599 | 61.1343 | 61.2991
474.6719 | 121.9208 | -61.29 | 60.3104 | -0.10506 | 0.0093076 | 0.066464 | 0.063525 | 0.0027857 | -0.0094614 | -0.0030141 | -0.089386 | 0.0036017 | 0.064918 | 0.0556 | -0.013456 | 0.027408 | -0.0057935 | -0.21973 | 60.1639 | -61.2946 | 60.3241 | -61.1298 | -61.5646 | -61.5234 | -0.10986 | 60.1135 | -61.3266 | 60.3333 | -61.2488 | -61.377 | -61.3449 | -0.004578 | -0.14648 | 0.013733 | 0.16022 | -0.23346 | -0.27466 | -0.22888 | -0.27008 | -0.036621 | -0.19684 | 0.022888 | 0.041199 | -0.054932 | -0.086975 | -0.018311 | -0.050354 | 0.16479 | 121.6187 | 0.07782 | 121.6599 | 121.4584 | 121.4401 | 121.4539 | 121.4035 | -121.6049 | -121.637 | 121.6141 | 121.6232 | 61.0703 | 61.1801
476.3594 | 121.8567 | -61.2579 | 60.347 | -0.10506 | 0.0080258 | 0.06561 | 0.063952 | -0.0029821 | -0.0094614 | -0.0042959 | -0.086334 | 0.0061651 | 0.066413 | 0.052395 | -0.014738 | 0.024631 | -0.0075025 | -0.054932 | 60.2005 | -61.2671 | 60.4065 | -61.0474 | -61.4777 | -61.4502 | 0.027466 | 60.1959 | -61.2762 | 60.3516 | -61.2396 | -61.377 | -61.3449 | -0.009155 | -0.14648 | 0.059509 | 0.21057 | -0.19226 | -0.21973 | -0.1831 | -0.21057 | -0.01831 | -0.15106 | 0.004577 | 0.018311 | -0.086975 | -0.11902 | -0.068665 | -0.10071 | 0.21973 | 121.6736 | 0.036621 | 121.6278 | 121.4676 | 121.4722 | 121.4584 | 121.4539 | -121.6141 | -121.6232 | 121.6644 | 121.6095 | 61.203 | 61.2854
478.1094 | 121.8109 | -61.322 | 60.3287 | -0.11269 | 0.009094 | 0.06796 | 0.063311 | 8.47e-06 | -0.0075388 | -2.3544e-05 | -0.11075 | 0.0038153 | 0.064918 | 0.054532 | -0.012174 | 0.025058 | -0.0040845 | -0.18768 | 60.1822 | -61.3312 | 60.3012 | -61.1481 | -61.5967 | -61.5509 | -0.16022 | 60.1685 | -61.3541 | 60.2554 | -61.3358 | -61.4502 | -61.4136 | -0.009156 | -0.14648 | -0.027466 | 0.17395 | -0.22888 | -0.27466 | -0.21973 | -0.2655 | -0.032044 | -0.16022 | -0.073242 | -0.013733 | -0.091553 | -0.12817 | -0.059509 | -0.09613 | 0.18311 | 121.6324 | 0.018311 | 121.6095 | 121.5134 | 121.5225 | 121.5042 | 121.4905 | -121.6599 | -121.6827 | 121.6232 | 121.5775 | 61.1343 | 61.1618
479.8594 | 121.9528 | -61.1755 | 60.3928 | -0.074539 | 0.0058896 | 0.065396 | 0.059039 | -0.0023413 | -0.0088206 | -0.0013051 | -0.0008851 | 0.0065923 | 0.066627 | 0.050473 | -0.011106 | 0.02399 | -0.0036573 | 0.036621 | 60.2097 | -61.1893 | 60.5301 | -60.8551 | -61.3174 | -61.2854 | 0.20599 | 60.1868 | -61.2167 | 60.4752 | -61.0519 | -61.1801 | -61.1938 | -0.013733 | -0.1831 | 0.13733 | 0.32043 | -0.10986 | -0.14191 | -0.09613 | -0.12817 | -0.041199 | -0.20599 | 0.082398 | 0.1236 | -0.018311 | -0.004578 | 0.022888 | 0.036621 | 0.33417 | 121.7194 | 0.16479 | 121.6919 | 121.3989 | 121.4035 | 121.3852 | 121.3623 | -121.582 | -121.6095 | 121.7056 | 121.6507 | 61.2122 | 61.3815
481.5469 | 121.9254 | -61.2579 | 60.2875 | -0.15083 | 0.0078122 | 0.065183 | 0.059466 | 0.00064947 | -0.0056162 | -0.0013051 | -0.052765 | 0.0059515 | 0.064491 | 0.055813 | -0.012815 | 0.025485 | -0.0055799 | -0.17853 | 60.1135 | -61.3129 | 60.4065 | -61.0428 | -61.4822 | -61.4502 | -0.018311 | 60.1135 | -61.3129 | 60.3973 | -61.2076 | -61.3358 | -61.3037 | -0.054931 | -0.17395 | 0.11902 | 0.21515 | -0.19226 | -0.2243 | -0.13733 | -0.16937 | -0.054931 | -0.17395 | 0.10986 | 0.050354 | -0.045776 | -0.077819 | 0.009155 | -0.022888 | 0.27008 | 121.7194 | 0.10529 | 121.7102 | 121.4264 | 121.4264 | 121.3715 | 121.3715 | -121.6003 | -121.6003 | 121.6644 | 121.6553 | 61.0794 | 61.2396
483.2969 | 121.8338 | -61.3083 | 60.3104 | -0.11269 | 0.009094 | 0.066037 | 0.064593 | -0.0036231 | -0.0071116 | -0.0025869 | -0.074127 | 0.0059515 | 0.067909 | 0.056668 | -0.013242 | 0.024844 | -0.0055799 | -0.21973 | 60.1501 | -61.3586 | 60.2921 | -61.1755 | -61.6196 | -61.5692 | -0.17395 | 60.1364 | -61.3541 | 60.2829 | -61.322 | -61.4594 | -61.409 | -0.050354 | -0.16022 | -0.018311 | 0.13275 | -0.26093 | -0.31128 | -0.21057 | -0.26093 | -0.045776 | -0.17395 | -0.027466 | -0.013732 | -0.10071 | -0.15106 | -0.054932 | -0.10529 | 0.18311 | 121.6507 | 0.032044 | 121.637 | 121.5088 | 121.4905 | 121.4584 | 121.4447 | -121.669 | -121.6644 | 121.6003 | 121.5912 | 61.0886 | 61.1343
485.0469 | 121.8613 | -61.2488 | 60.3836 | -0.06691 | 0.0046078 | 0.064328 | 0.063098 | -0.0031957 | -0.010316 | -0.00045074 | -0.052765 | 0.0018927 | 0.068977 | 0.05325 | -0.01132 | 0.024844 | -0.0023755 | -0.036621 | 60.2325 | -61.2625 | 60.3882 | -61.0748 | -61.4731 | -61.4548 | 0.009155 | 60.2371 | -61.2808 | 60.3424 | -61.2167 | -61.3586 | -61.3449 | -0.013733 | -0.15106 | 0.004578 | 0.17395 | -0.20599 | -0.2243 | -0.19226 | -0.21057 | -0.032044 | -0.14648 | -0.041199 | 0.032043 | -0.096131 | -0.10986 | -0.064087 | -0.07782 | 0.18768 | 121.6507 | 0.064087 | 121.6232 | 121.4951 | 121.5179 | 121.4813 | 121.4859 | -121.6461 | -121.6644 | 121.637 | 121.5912 | 61.2122 | 61.2579
486.7344 | 121.9437 | -61.1618 | 60.4019 | -0.13557 | 0.003967 | 0.064542 | 0.061175 | 0.0015039 | -0.011384 | -0.00087794 | 0.017425 | 0.0033881 | 0.065559 | 0.049405 | -0.012815 | 0.025272 | -0.0070751 | 0.045776 | 60.2005 | -61.203 | 60.5438 | -60.8643 | -61.3174 | -61.29 | 0.21973 | 60.173 | -61.2076 | 60.4752 | -61.0565 | -61.1618 | -61.1938 | -0.041199 | -0.20142 | 0.14191 | 0.29755 | -0.12817 | -0.15564 | -0.086975 | -0.11444 | -0.045777 | -0.22888 | 0.073242 | 0.10528 | -0.032044 | 0 | 0.013733 | 0.045777 | 0.33875 | 121.7468 | 0.15106 | 121.6827 | 121.4035 | 121.3806 | 121.3623 | 121.3348 | -121.6049 | -121.6095 | 121.7056 | 121.637 | 61.2076 | 61.3815
488.4844 | 121.8109 | -61.2396 | 60.434 | -0.10506 | 0.0069578 | 0.065183 | 0.061175 | -0.0025549 | -0.010316 | -0.0057913 | -0.025299 | 0.0044561 | 0.068336 | 0.054959 | -0.011961 | 0.025485 | -0.0051525 | 0.027466 | 60.2188 | -61.2167 | 60.4385 | -60.9924 | -61.441 | -61.409 | 0.068665 | 60.2234 | -61.2442 | 60.347 | -61.1938 | -61.3312 | -61.3449 | 0.022888 | -0.21515 | 0.004578 | 0.24719 | -0.16937 | -0.20142 | -0.19226 | -0.2243 | -0.004578 | -0.21057 | -0.086975 | 0.045776 | -0.10529 | -0.091553 | -0.10071 | -0.086975 | 0.2243 | 121.6553 | 0.050354 | 121.5912 | 121.4355 | 121.4676 | 121.4584 | 121.463 | -121.6507 | -121.6782 | 121.6782 | 121.5866 | 61.2671 | 61.3083
490.25 | 121.9345 | -61.1938 | 60.4202 | -0.089798 | 0.0033262 | 0.064328 | 0.058398 | -0.0029821 | -0.008607 | -0.0030141 | 0.0052185 | 0.0023199 | 0.0662 | 0.059018 | -0.015379 | 0.024204 | -0.0023755 | -0.050354 | 60.1776 | -61.2488 | 60.4568 | -60.9695 | -61.3953 | -61.3541 | 0.091553 | 60.1593 | -61.2579 | 60.4385 | -61.1023 | -61.2122 | -61.2396 | -0.054931 | -0.24261 | 0.036621 | 0.22431 | -0.16022 | -0.20142 | -0.10529 | -0.14648 | -0.064087 | -0.26093 | 0.018311 | 0.091553 | -0.045776 | -0.01831 | 0.018311 | 0.045777 | 0.27924 | 121.7056 | 0.15564 | 121.6965 | 121.4264 | 121.4172 | 121.3715 | 121.3531 | -121.669 | -121.6782 | 121.6507 | 121.6324 | 61.1435 | 61.2854
492 | 121.8613 | -61.2076 | 60.4248 | -0.074539 | 0.0071714 | 0.064328 | 0.060962 | -0.0017005 | -0.007966 | -0.0051505 | -0.019196 | 0.0031745 | 0.065132 | 0.049191 | -0.010679 | 0.022708 | -0.0023755 | 0.064087 | 60.2188 | -61.2167 | 60.5118 | -60.9375 | -61.3449 | -61.3312 | 0.16022 | 60.2417 | -61.2305 | 60.4019 | -61.1664 | -61.2808 | -61.2854 | -0.009155 | -0.20599 | 0.086975 | 0.27008 | -0.1236 | -0.13733 | -0.11444 | -0.12817 | -0.022888 | -0.18311 | -0.022888 | 0.041199 | -0.077819 | -0.073242 | -0.054931 | -0.050354 | 0.27924 | 121.7285 | 0.064087 | 121.6324 | 121.4355 | 121.4722 | 121.4264 | 121.4493 | -121.6415 | -121.6553 | 121.7194 | 121.6095 | 61.2717 | 61.3678
493.75 | 121.8384 | -61.2122 | 60.3973 | -0.06691 | 0.0071714 | 0.066037 | 0.059253 | 0.0019311 | -0.012452 | -0.00066434 | -0.040558 | 0.0048833 | 0.064704 | 0.055813 | -0.013883 | 0.024204 | -0.0047253 | 0.054932 | 60.2005 | -61.2076 | 60.5164 | -60.9467 | -61.3632 | -61.3266 | 0.15106 | 60.2325 | -61.2305 | 60.3973 | -61.1664 | -61.29 | -61.2717 | 0.004577 | -0.19684 | 0.11902 | 0.2655 | -0.11444 | -0.15106 | -0.11902 | -0.15564 | -0.018311 | -0.1648 | 0 | 0.045776 | -0.059509 | -0.07782 | -0.041198 | -0.059509 | 0.26093 | 121.7239 | 0.064087 | 121.6278 | 121.4081 | 121.463 | 121.4127 | 121.4447 | -121.6049 | -121.6278 | 121.7285 | 121.6095 | 61.2671 | 61.3632
495.5 | 121.8109 | -61.3449 | 60.3058 | -0.15846 | 0.0069578 | 0.066892 | 0.062671 | -0.00063233 | -0.0094614 | 0.00040366 | -0.1077 | 0.0040289 | 0.065986 | 0.057309 | -0.013456 | 0.025485 | -0.0017347 | -0.2243 | 60.1913 | -61.322 | 60.2829 | -61.2076 | -61.6241 | -61.5646 | -0.1831 | 60.1547 | -61.3586 | 60.2463 | -61.3724 | -61.4868 | -61.4227 | 0.022889 | -0.11444 | -0.022888 | 0.13733 | -0.21973 | -0.27924 | -0.24262 | -0.30213 | -0.013733 | -0.15106 | -0.059509 | -0.027465 | -0.077819 | -0.14191 | -0.064086 | -0.12817 | 0.11444 | 121.6049 | -0.013732 | 121.6049 | 121.5134 | 121.5134 | 121.5363 | 121.4996 | -121.6278 | -121.6644 | 121.6278 | 121.5912 | 61.1206 | 61.1618
497.1875 | 121.8658 | -61.2671 | 60.347 | -0.06691 | 0.0054624 | 0.06561 | 0.062671 | -0.0031957 | -0.010316 | -0.0032277 | -0.098541 | 0.0055243 | 0.068977 | 0.051327 | -0.013883 | 0.024417 | -0.0038709 | -0.054932 | 60.1776 | -61.2762 | 60.4156 | -61.0428 | -61.4777 | -61.4639 | 0.032043 | 60.1776 | -61.3037 | 60.347 | -61.2305 | -61.3678 | -61.3266 | -0.009155 | -0.16937 | 0.068664 | 0.2243 | -0.19684 | -0.21057 | -0.18768 | -0.20142 | -0.036621 | -0.16937 | 0 | 0.036621 | -0.059509 | -0.10071 | -0.022888 | -0.064087 | 0.23346 | 121.6919 | 0.073242 | 121.6507 | 121.4539 | 121.4813 | 121.4447 | 121.4447 | -121.6232 | -121.6507 | 121.6827 | 121.6141 | 61.2122 | 61.2991
498.9219 | 121.8109 | -61.2213 | 60.3973 | -0.1432 | 0.0041806 | 0.065183 | 0.06203 | -0.0017005 | -0.0081796 | -0.0038687 | -0.046661 | 0.0044561 | 0.0662 | 0.055173 | -0.012602 | 0.026553 | -0.0079297 | -0.032043 | 60.2554 | -61.2442 | 60.4065 | -61.0519 | -61.4685 | -61.4365 | 0.032043 | 60.2554 | -61.2442 | 60.3287 | -61.2305 | -61.3403 | -61.3312 | -0.022889 | -0.14191 | 0.009155 | 0.16937 | -0.21515 | -0.24719 | -0.19226 | -0.2243 | -0.022889 | -0.14191 | -0.068665 | -0.009156 | -0.10986 | -0.11902 | -0.086975 | -0.09613 | 0.19226 | 121.6507 | 0.013733 | 121.5729 | 121.4996 | 121.4996 | 121.4767 | 121.4767 | -121.6415 | -121.6415 | 121.6278 | 121.55 | 61.1893 | 61.2534
500.6719 | 121.9528 | -61.1847 | 60.3699 | -0.12032 | 0.0050352 | 0.064756 | 0.060534 | -0.0036231 | -0.0094614 | -0.0042959 | -0.0039367 | 0.0027471 | 0.066627 | 0.049618 | -0.012174 | 0.024844 | -0.0077161 | 0.041199 | 60.1868 | -61.203 | 60.5392 | -60.8734 | -61.3083 | -61.2946 | 0.19684 | 60.2051 | -61.2213 | 60.4797 | -61.0474 | -61.1984 | -61.203 | -0.018311 | -0.1831 | 0.16937 | 0.31128 | -0.10986 | -0.1236 | -0.091553 | -0.10529 | -0.036621 | -0.16479 | 0.10986 | 0.13733 | -0.018311 | -0.013733 | 0.01831 | 0.022888 | 0.32959 | 121.7422 | 0.17395 | 121.701 | 121.3898 | 121.4264 | 121.3715 | 121.3898 | -121.5729 | -121.5912 | 121.7239 | 121.6644 | 61.2259 | 61.3815
502.3594 | 121.8887 | -61.2396 | 60.3561 | -0.1432 | 0.0041806 | 0.066678 | 0.060748 | -0.0059729 | -0.006898 | -0.0034415 | -0.025299 | 0.0029607 | 0.065132 | 0.048337 | -0.011106 | 0.02399 | -0.0038709 | -0.10071 | 60.1822 | -61.2396 | 60.4294 | -61.0245 | -61.441 | -61.409 | 0.004578 | 60.173 | -61.2671 | 60.379 | -61.1984 | -61.3037 | -61.29 | 0 | -0.17395 | 0.073242 | 0.21515 | -0.16937 | -0.20142 | -0.16937 | -0.20142 | -0.027466 | -0.18311 | 0.022888 | 0.041199 | -0.050354 | -0.064087 | -0.022888 | -0.036621 | 0.21515 | 121.669 | 0.068665 | 121.6461 | 121.4218 | 121.4401 | 121.4218 | 121.4127 | -121.5958 | -121.6232 | 121.669 | 121.6187 | 61.1389 | 61.2442
504.125 | 121.7926 | -61.3037 | 60.3333 | -0.051651 | 0.0065304 | 0.066678 | 0.063739 | -0.0025549 | -0.010743 | -0.0013051 | -0.12296 | 0.0059515 | 0.065986 | 0.058163 | -0.012174 | 0.028049 | -0.0038709 | -0.16479 | 60.1547 | -61.2991 | 60.3333 | -61.1435 | -61.5967 | -61.5601 | -0.12817 | 60.1501 | -61.3541 | 60.2737 | -61.3449 | -61.4731 | -61.4182 | 0.004578 | -0.17853 | 0 | 0.16022 | -0.25635 | -0.29297 | -0.26093 | -0.29755 | -0.050354 | -0.18311 | -0.059509 | -0.041199 | -0.11444 | -0.16937 | -0.064087 | -0.11902 | 0.15564 | 121.6324 | 0.009155 | 121.6278 | 121.4539 | 121.5042 | 121.4584 | 121.4539 | -121.6324 | -121.6873 | 121.637 | 121.5775 | 61.1389 | 61.1755
505.8125 | 121.9025 | -61.2259 | 60.3607 | -0.11269 | 0.0054624 | 0.066251 | 0.060534 | -0.0068273 | -0.0090342 | -0.0023733 | -0.01004 | 0.0016791 | 0.064063 | 0.052823 | -0.013883 | 0.025912 | -0.0070751 | -0.09613 | 60.1776 | -61.2534 | 60.434 | -61.0245 | -61.4502 | -61.3953 | 0.013733 | 60.173 | -61.2717 | 60.3882 | -61.1893 | -61.3129 | -61.29 | -0.027466 | -0.18311 | 0.073242 | 0.20142 | -0.16937 | -0.2243 | -0.14191 | -0.19684 | -0.045776 | -0.18768 | 0.027466 | 0.036621 | -0.064087 | -0.086975 | -0.018311 | -0.041199 | 0.22888 | 121.6873 | 0.082397 | 121.6599 | 121.431 | 121.4447 | 121.4035 | 121.3989 | -121.6141 | -121.6324 | 121.6599 | 121.6141 | 61.1298 | 61.2396
507.5625 | 121.8109 | -61.3403 | 60.3287 | -0.06691 | 0.009094 | 0.066892 | 0.064807 | 0.0015039 | -0.0077524 | -0.0028005 | -0.10159 | 0.0046697 | 0.065559 | 0.058804 | -0.012815 | 0.025272 | -0.0062207 | -0.21057 | 60.1913 | -61.3037 | 60.3058 | -61.1984 | -61.6241 | -61.5921 | -0.17853 | 60.1501 | -61.3632 | 60.2509 | -61.3586 | -61.4731 | -61.4227 | 0.036621 | -0.13733 | -0.022888 | 0.14191 | -0.25177 | -0.28381 | -0.28839 | -0.32044 | -0.022888 | -0.17853 | -0.07782 | -0.018311 | -0.082397 | -0.13275 | -0.059509 | -0.10986 | 0.10529 | 121.6095 | 0.004577 | 121.6141 | 121.4951 | 121.5134 | 121.5317 | 121.4905 | -121.6324 | -121.6919 | 121.6461 | 121.5912 | 61.1298 | 61.1618
509.2344 | 121.962 | -61.1618 | 60.3882 | -0.11269 | 0.0054624 | 0.063901 | 0.060962 | -0.0021277 | -0.0092478 | -0.0025869 | -0.01004 | 0.0038153 | 0.067909 | 0.051968 | -0.012174 | 0.025912 | -0.0066479 | 0.036621 | 60.1959 | -61.2167 | 60.553 | -60.8597 | -61.3129 | -61.2808 | 0.20599 | 60.1868 | -61.2259 | 60.4889 | -61.0657 | -61.1801 | -61.2122 | -0.054932 | -0.19226 | 0.16479 | 0.30212 | -0.11902 | -0.15106 | -0.064087 | -0.09613 | -0.064087 | -0.20142 | 0.10071 | 0.09613 | -0.050354 | -0.018311 | 0.013733 | 0.045776 | 0.35706 | 121.7697 | 0.16022 | 121.7148 | 121.4127 | 121.4127 | 121.3577 | 121.3486 | -121.6049 | -121.6141 | 121.7148 | 121.6507 | 61.1984 | 61.3678
510.9844 | 121.8475 | -61.2579 | 60.3699 | -0.089798 | 0.0065304 | 0.064969 | 0.063311 | -0.0023413 | -0.0092478 | -0.0032277 | -0.077179 | 0.0065923 | 0.065772 | 0.059018 | -0.015165 | 0.025485 | -0.0017347 | -0.045776 | 60.2463 | -61.2808 | 60.4065 | -61.0428 | -61.4914 | -61.4502 | 0.032043 | 60.1685 | -61.2991 | 60.3653 | -61.2305 | -61.3586 | -61.3312 | -0.022888 | -0.1236 | 0.036621 | 0.21515 | -0.19226 | -0.23346 | -0.16937 | -0.21057 | -0.041198 | -0.20142 | -0.004578 | 0.027466 | -0.073242 | -0.10071 | -0.032044 | -0.05951 | 0.23804 | 121.6873 | 0.068664 | 121.6644 | 121.5271 | 121.4676 | 121.5042 | 121.4264 | -121.6507 | -121.669 | 121.6644 | 121.6232 | 61.2122 | 61.29
512.75 | 121.8155 | -61.2305 | 60.4111 | -0.10506 | 0.0028988 | 0.063474 | 0.061389 | -0.0025549 | -0.0081796 | -0.0017325 | -0.04361 | 0.0040289 | 0.067481 | 0.058804 | -0.013029 | 0.024631 | -0.0036573 | -0.027466 | 60.2509 | -61.235 | 60.4111 | -61.0519 | -61.4594 | -61.4365 | 0.027466 | 60.2509 | -61.235 | 60.3424 | -61.2259 | -61.3541 | -61.3312 | -0.004577 | -0.16022 | 0 | 0.17853 | -0.20599 | -0.22888 | -0.20142 | -0.22431 | -0.004577 | -0.16022 | -0.068665 | 0.004578 | -0.10071 | -0.1236 | -0.096131 | -0.11902 | 0.1831 | 121.6461 | 0.009155 | 121.5775 | 121.4859 | 121.4859 | 121.4813 | 121.4813 | -121.6461 | -121.6461 | 121.6415 | 121.5729 | 61.203 | 61.2579
514.4375 | 121.8292 | -61.3174 | 60.3104 | -0.082169 | 0.0069578 | 0.066464 | 0.063311 | 0.00022207 | -0.009675 | -0.0013051 | -0.1199 | 0.0070197 | 0.066413 | 0.060513 | -0.013883 | 0.025699 | -0.0038709 | -0.10986 | 60.1868 | -61.2991 | 60.3928 | -61.0611 | -61.5097 | -61.496 | -0.050354 | 60.1822 | -61.322 | 60.2875 | -61.2946 | -61.4548 | -61.3907 | 0.018311 | -0.1236 | 0.082397 | 0.25635 | -0.17853 | -0.19226 | -0.19684 | -0.21057 | -0.004577 | -0.12817 | -0.022888 | 0.022888 | -0.073242 | -0.13733 | -0.068665 | -0.13275 | 0.23804 | 121.6919 | 0.027465 | 121.6095 | 121.4859 | 121.5042 | 121.5042 | 121.4996 | -121.6095 | -121.6324 | 121.7102 | 121.6049 | 61.2076 | 61.2671
516.1875 | 121.8658 | -61.3037 | 60.2737 | -0.11269 | 0.0069578 | 0.066037 | 0.061816 | -0.0019141 | -0.0071116 | -0.0013051 | -0.064972 | 0.0031745 | 0.063423 | 0.046414 | -0.012174 | 0.027194 | -0.0032299 | -0.22888 | 60.1639 | -61.3174 | 60.3058 | -61.1389 | -61.5738 | -61.5326 | -0.16937 | 60.1318 | -61.3495 | 60.2966 | -61.2854 | -61.4365 | -61.3815 | -0.013733 | -0.10986 | 0.032043 | 0.16479 | -0.22888 | -0.27008 | -0.21515 | -0.25635 | -0.045776 | -0.14191 | 0.022888 | 0.018311 | -0.07782 | -0.13275 | -0.032044 | -0.086975 | 0.17853 | 121.6232 | 0.064087 | 121.6461 | 121.4813 | 121.4813 | 121.4676 | 121.4355 | -121.5912 | -121.6232 | 121.6095 | 121.6003 | 61.0748 | 61.1343
517.9375 | 121.9391 | -61.2579 | 60.2692 | -0.12032 | 0.0086668 | 0.066251 | 0.062243 | 0.00043587 | -0.0088206 | -0.0040823 | -0.04361 | 0.0033881 | 0.066413 | 0.054959 | -0.011961 | 0.025058 | -0.0040845 | -0.14648 | 60.1135 | -61.2854 | 60.4248 | -61.0199 | -61.4822 | -61.4365 | -0.018311 | 60.1089 | -61.3037 | 60.4019 | -61.1893 | -61.3266 | -61.2854 | -0.027465 | -0.15564 | 0.15564 | 0.23804 | -0.17853 | -0.2243 | -0.15106 | -0.19684 | -0.045776 | -0.16022 | 0.13275 | 0.068665 | -0.027465 | -0.068664 | 0.018311 | -0.022888 | 0.2655 | 121.7102 | 0.11444 | 121.7056 | 121.3989 | 121.4127 | 121.3715 | 121.3669 | -121.5546 | -121.5729 | 121.6827 | 121.6599 | 61.1115 | 61.2396
519.6875 | 121.8613 | -61.2808 | 60.3607 | -0.10506 | 0.005676 | 0.06561 | 0.062884 | 0.00043587 | -0.0077524 | -0.0015189 | -0.068024 | 0.0048833 | 0.067268 | 0.056881 | -0.011961 | 0.025272 | -0.0025891 | -0.050354 | 60.2051 | -61.2946 | 60.4065 | -61.0382 | -61.4914 | -61.4594 | 0.027466 | 60.1868 | -61.29 | 60.3378 | -61.2259 | -61.3586 | -61.3403 | -0.013733 | -0.15564 | 0.045776 | 0.24262 | -0.17853 | -0.21057 | -0.16479 | -0.19684 | -0.009155 | -0.17395 | -0.022888 | 0.054932 | -0.059509 | -0.07782 | -0.050354 | -0.068665 | 0.25635 | 121.7011 | 0.064087 | 121.6278 | 121.4996 | 121.4767 | 121.4859 | 121.4676 | -121.6553 | -121.6507 | 121.6873 | 121.6187 | 61.2305 | 61.3083
521.375 | 121.9299 | -61.2213 | 60.379 | -0.13557 | 0.0063168 | 0.068387 | 0.058184 | -0.0029821 | -0.0090342 | -0.0034415 | 0.0082703 | 0.0059515 | 0.0662 | 0.057095 | -0.011106 | 0.02399 | -0.0081433 | -0.064087 | 60.2142 | -61.235 | 60.4202 | -61.0107 | -61.4365 | -61.3907 | 0.054932 | 60.1822 | -61.2717 | 60.4111 | -61.1481 | -61.2534 | -61.2396 | -0.013733 | -0.16479 | 0.041199 | 0.21057 | -0.16937 | -0.21515 | -0.15564 | -0.20142 | -0.050354 | -0.19684 | 0.032044 | 0.073242 | -0.018311 | -0.032044 | 0.032043 | 0.01831 | 0.2243 | 121.6553 | 0.1236 | 121.6827 | 121.4493 | 121.4539 | 121.4355 | 121.4035 | -121.6141 | -121.6507 | 121.6415 | 121.6324 | 61.1572 | 61.2762
523.125 | 121.8658 | -61.2762 | 60.347 | -0.074539 | 0.0065304 | 0.066464 | 0.062243 | -0.0014867 | -0.010957 | -0.0017325 | -0.089386 | 0.0050971 | 0.066627 | 0.055386 | -0.012388 | 0.025912 | -0.0047253 | -0.10071 | 60.1776 | -61.3174 | 60.3973 | -61.0382 | -61.496 | -61.4456 | 0.013733 | 60.1822 | -61.2808 | 60.347 | -61.2305 | -61.3678 | -61.3495 | -0.041199 | -0.16937 | 0.050354 | 0.23804 | -0.16937 | -0.21973 | -0.12817 | -0.17853 | -0.004578 | -0.16479 | 0 | 0.045776 | -0.073242 | -0.091553 | -0.068664 | -0.086975 | 0.27924 | 121.7148 | 0.050354 | 121.6278 | 121.4951 | 121.463 | 121.4539 | 121.4584 | -121.6644 | -121.6278 | 121.6736 | 121.6232 | 61.1755 | 61.29
524.8125 | 121.9528 | -61.171 | 60.4065 | -0.089798 | 0.003967 | 0.066464 | 0.059466 | -0.0044775 | -0.01053 | -0.0034415 | 0.023529 | 0.0042425 | 0.064491 | 0.050473 | -0.01132 | 0.024417 | -0.0077161 | 0.041199 | 60.1913 | -61.2259 | 60.5576 | -60.8551 | -61.3037 | -61.2808 | 0.21057 | 60.1913 | -61.1938 | 60.4797 | -61.0474 | -61.1847 | -61.1938 | -0.054932 | -0.21515 | 0.15106 | 0.31586 | -0.10986 | -0.13275 | -0.054932 | -0.07782 | -0.022889 | -0.21515 | 0.073242 | 0.1236 | -0.022889 | -0.013733 | 0 | 0.009156 | 0.37079 | 121.7834 | 0.14649 | 121.6736 | 121.4172 | 121.3852 | 121.3623 | 121.3623 | -121.6324 | -121.6003 | 121.7285 | 121.6507 | 61.2122 | 61.3815
526.5625 | 121.8018 | -61.2991 | 60.3195 | -0.10506 | 0.0075986 | 0.064328 | 0.063525 | -0.0025549 | -0.008607 | -0.0040823 | -0.10464 | 0.0046697 | 0.067481 | 0.058163 | -0.013242 | 0.02634 | -0.0013073 | -0.21973 | 60.1593 | -61.3266 | 60.2783 | -61.1847 | -61.6241 | -61.5601 | -0.17395 | 60.1318 | -61.3495 | 60.2692 | -61.3312 | -61.4777 | -61.4136 | -0.027466 | -0.16022 | -0.041199 | 0.11444 | -0.26093 | -0.32501 | -0.23346 | -0.29755 | -0.050354 | -0.18768 | -0.050354 | -0.032044 | -0.11444 | -0.17853 | -0.064087 | -0.12817 | 0.14191 | 121.6049 | 0.01831 | 121.6187 | 121.4859 | 121.4813 | 121.4584 | 121.431 | -121.6461 | -121.669 | 121.5775 | 121.5683 | 61.0794 | 61.1252
528.2969 | 121.9345 | -61.2717 | 60.26 | -0.10506 | 0.0069578 | 0.066251 | 0.061389 | -0.0017005 | -0.0083932 | -0.00087794 | -0.028351 | 0.0031745 | 0.066627 | 0.060727 | -0.012602 | 0.024844 | -0.0060071 | -0.13733 | 60.1227 | -61.29 | 60.4202 | -61.0199 | -61.4777 | -61.4365 | 0.004578 | 60.1044 | -61.2946 | 60.3882 | -61.1847 | -61.3129 | -61.29 | -0.018311 | -0.13733 | 0.16022 | 0.25177 | -0.16479 | -0.20599 | -0.14648 | -0.18768 | -0.022889 | -0.15564 | 0.12817 | 0.086975 | -0.018311 | -0.041199 | 0.004578 | -0.01831 | 0.27008 | 121.7102 | 0.10986 | 121.6827 | 121.4127 | 121.3989 | 121.3943 | 121.376 | -121.55 | -121.5546 | 121.6919 | 121.6599 | 61.1343 | 61.2762
529.9688 | 121.8292 | -61.2305 | 60.4431 | -0.074539 | 0.0037534 | 0.065183 | 0.061602 | -0.0017005 | -0.007966 | -0.0019461 | -0.031403 | 0.0042425 | 0.067695 | 0.051327 | -0.012174 | 0.022281 | -0.0023755 | 0.009155 | 60.2509 | -61.2259 | 60.4568 | -61.0062 | -61.441 | -61.4182 | 0.054932 | 60.26 | -61.2625 | 60.3424 | -61.2122 | -61.3403 | -61.3266 | 0.004578 | -0.19226 | 0.013733 | 0.2243 | -0.18768 | -0.21057 | -0.19226 | -0.21515 | -0.032043 | -0.1831 | -0.10071 | 0.018311 | -0.09613 | -0.10986 | -0.064087 | -0.07782 | 0.21973 | 121.6827 | 0.050354 | 121.6049 | 121.4767 | 121.5225 | 121.4813 | 121.4905 | -121.669 | -121.7056 | 121.6873 | 121.5729 | 61.2396 | 61.2854
531.7188 | 121.8979 | -61.2259 | 60.3516 | -0.10506 | 0.0043942 | 0.06796 | 0.059466 | -0.0040503 | -0.0075388 | -0.0036551 | 0.0052185 | 0.0040289 | 0.064918 | 0.054959 | -0.012602 | 0.024204 | -0.0079297 | -0.09613 | 60.173 | -61.2305 | 60.4385 | -61.0245 | -61.4502 | -61.4044 | 0.009155 | 60.1685 | -61.2762 | 60.3699 | -61.1893 | -61.3037 | -61.2854 | -0.004578 | -0.17853 | 0.086976 | 0.20142 | -0.17853 | -0.2243 | -0.17395 | -0.21973 | -0.050354 | -0.18311 | 0.018311 | 0.036621 | -0.059509 | -0.07782 | -0.009155 | -0.027466 | 0.20599 | 121.669 | 0.086975 | 121.6461 | 121.4035 | 121.4447 | 121.3989 | 121.3943 | -121.582 | -121.6278 | 121.6644 | 121.5958 | 61.1298 | 61.235
533.4531 | 121.9254 | -61.3037 | 60.2829 | -0.15083 | 0.0071714 | 0.067319 | 0.062457 | -0.0021277 | -0.006898 | -0.0049367 | -0.080231 | 0.0027471 | 0.0662 | 0.04855 | -0.014097 | 0.024844 | -0.00066651 | -0.21057 | 60.1456 | -61.3174 | 60.3561 | -61.1023 | -61.5601 | -61.5005 | -0.086975 | 60.1181 | -61.3174 | 60.3607 | -61.2396 | -61.3586 | -61.3174 | -0.013733 | -0.13733 | 0.073242 | 0.20142 | -0.19684 | -0.25635 | -0.1831 | -0.24262 | -0.013733 | -0.1648 | 0.07782 | 0.064087 | -0.013733 | -0.054932 | 0 | -0.041199 | 0.21515 | 121.6736 | 0.07782 | 121.6782 | 121.463 | 121.4355 | 121.4493 | 121.4218 | -121.6003 | -121.6003 | 121.6599 | 121.6644 | 61.0931 | 61.2167
535.2031 | 121.8658 | -61.2671 | 60.347 | -0.044022 | 0.0067442 | 0.064328 | 0.062884 | 0.0021447 | -0.0083932 | -0.0051505 | -0.10159 | 0.0040289 | 0.067268 | 0.059659 | -0.012174 | 0.024631 | -0.0030163 | -0.068665 | 60.1959 | -61.2625 | 60.4202 | -61.0611 | -61.4822 | -61.4639 | 0.018311 | 60.1822 | -61.2991 | 60.3516 | -61.2305 | -61.377 | -61.3358 | 0.004578 | -0.15106 | 0.073242 | 0.20599 | -0.19684 | -0.21515 | -0.20142 | -0.21973 | -0.032043 | -0.16479 | 0.004577 | 0.036621 | -0.068664 | -0.10986 | -0.036621 | -0.07782 | 0.20142 | 121.6827 | 0.068664 | 121.6507 | 121.4584 | 121.4813 | 121.463 | 121.4493 | -121.6095 | -121.6461 | 121.6873 | 121.6187 | 61.1984 | 61.2854
536.8906 | 121.9162 | -61.1847 | 60.3973 | -0.12032 | 0.0054624 | 0.064756 | 0.060962 | -0.0021277 | -0.01053 | -0.0015189 | 0.023529 | 0.0042425 | 0.067054 | 0.050473 | -0.012388 | 0.025699 | -0.0055799 | -0.059509 | 60.1776 | -61.235 | 60.4523 | -60.9741 | -61.4182 | -61.3724 | 0.073242 | 60.1685 | -61.2579 | 60.4294 | -61.1206 | -61.2259 | -61.235 | -0.050354 | -0.21973 | 0.054932 | 0.21057 | -0.18768 | -0.23346 | -0.13733 | -0.18311 | -0.073243 | -0.22888 | 0.032043 | 0.064087 | -0.050354 | -0.041199 | 0.022889 | 0.032044 | 0.26093 | 121.6873 | 0.13733 | 121.6873 | 121.4127 | 121.4264 | 121.3623 | 121.3531 | -121.6324 | -121.6553 | 121.637 | 121.6141 | 61.1252 | 61.2579
538.6406 | 121.9437 | -61.1847 | 60.4156 | -0.12032 | 0.0046078 | 0.06561 | 0.057971 | -0.0025549 | -0.010316 | -0.0023733 | 0.0082703 | 0.0018927 | 0.064704 | 0.05325 | -0.012815 | 0.024844 | -0.0062207 | 0.059509 | 60.2097 | -61.1938 | 60.5392 | -60.8826 | -61.322 | -61.2946 | 0.21973 | 60.2325 | -61.203 | 60.4568 | -61.0886 | -61.2076 | -61.2213 | -0.009156 | -0.20599 | 0.1236 | 0.30212 | -0.10986 | -0.13733 | -0.10071 | -0.12817 | -0.018311 | -0.18311 | 0.041199 | 0.09613 | -0.036621 | -0.022889 | -0.01831 | -0.004578 | 0.31128 | 121.7331 | 0.11444 | 121.6599 | 121.4035 | 121.4355 | 121.3943 | 121.4172 | -121.6095 | -121.6187 | 121.7239 | 121.6415 | 61.2442 | 61.4044
540.3906 | 121.8979 | -61.1938 | 60.4156 | -0.06691 | 0.0031126 | 0.063901 | 0.059466 | -0.0012731 | -0.0083932 | -0.0023733 | -0.037506 | 0.0023199 | 0.064918 | 0.053891 | -0.013242 | 0.024631 | -0.0019483 | 0.059509 | 60.1868 | -61.2122 | 60.5072 | -60.9283 | -61.3449 | -61.3174 | 0.16479 | 60.2142 | -61.2167 | 60.434 | -61.1298 | -61.2625 | -61.2625 | -0.01831 | -0.22888 | 0.091553 | 0.2655 | -0.1236 | -0.15106 | -0.10529 | -0.13275 | -0.022888 | -0.20142 | 0.018311 | 0.064087 | -0.068664 | -0.068664 | -0.045776 | -0.045776 | 0.28381 | 121.7194 | 0.086975 | 121.6507 | 121.3989 | 121.431 | 121.3806 | 121.4081 | -121.6278 | -121.6324 | 121.7011 | 121.6278 | 61.2534 | 61.3586
542.0938 | 121.9528 | -61.1938 | 60.3928 | -0.1432 | 0.0037534 | 0.065396 | 0.059893 | -0.0010595 | -0.011384 | -0.0015189 | -0.019196 | 0.0025335 | 0.066413 | 0.053036 | -0.013883 | 0.022708 | -0.0053661 | 0.068665 | 60.2142 | -61.203 | 60.553 | -60.8688 | -61.3129 | -61.2991 | 0.2243 | 60.2188 | -61.2076 | 60.4889 | -61.0748 | -61.1938 | -61.2122 | -0.009155 | -0.17853 | 0.16022 | 0.32501 | -0.10528 | -0.11902 | -0.09613 | -0.10986 | -0.013733 | -0.17395 | 0.096131 | 0.11902 | -0.01831 | 0 | -0.004577 | 0.013733 | 0.33417 | 121.756 | 0.13275 | 121.6965 | 121.4172 | 121.4264 | 121.4081 | 121.4127 | -121.5958 | -121.6003 | 121.7468 | 121.6827 | 61.2625 | 61.4182
543.8438 | 121.8201 | -61.2167 | 60.3928 | -0.06691 | 0.0035398 | 0.063687 | 0.060962 | -0.0017005 | -0.009675 | -0.0023733 | -0.068024 | 0.0036017 | 0.064491 | 0.054104 | -0.013883 | 0.024204 | -0.0038709 | -0.036621 | 60.2554 | -61.2442 | 60.4065 | -61.0519 | -61.4594 | -61.441 | 0.018311 | 60.2737 | -61.2808 | 60.3378 | -61.235 | -61.3632 | -61.3495 | -0.027466 | -0.13733 | 0.013733 | 0.16479 | -0.2243 | -0.24262 | -0.19684 | -0.21515 | -0.064087 | -0.11902 | -0.054931 | -0.01831 | -0.13275 | -0.14648 | -0.068664 | -0.082397 | 0.19226 | 121.6507 | 0.045777 | 121.6187 | 121.4996 | 121.5546 | 121.4722 | 121.4905 | -121.637 | -121.6736 | 121.6232 | 121.5546 | 61.1801 | 61.235
545.5938 | 121.7926 | -61.3037 | 60.3012 | -0.074539 | 0.0054624 | 0.066464 | 0.063952 | 0.0017175 | -0.0098886 | -0.0021597 | -0.10159 | 0.0042425 | 0.064491 | 0.056881 | -0.012602 | 0.025912 | -0.0045117 | -0.20599 | 60.1501 | -61.3174 | 60.3104 | -61.1572 | -61.6013 | -61.5601 | -0.16479 | 60.1456 | -61.3403 | 60.2646 | -61.3586 | -61.5005 | -61.4319 | -0.013733 | -0.15106 | 0.009156 | 0.14648 | -0.25635 | -0.29755 | -0.24262 | -0.28381 | -0.036621 | -0.15564 | -0.036621 | -0.054932 | -0.12817 | -0.19684 | -0.091553 | -0.16022 | 0.16022 | 121.6278 | -0.018311 | 121.6049 | 121.4676 | 121.4859 | 121.4539 | 121.4493 | -121.6187 | -121.6415 | 121.6141 | 121.5683 | 61.0977 | 61.1389
547.3438 | 121.8567 | -61.2854 | 60.3378 | -0.097427 | 0.0069578 | 0.066251 | 0.063952 | -0.0014867 | -0.008607 | -0.0045095 | -0.083283 | 0.0038153 | 0.067268 | 0.054745 | -0.0098246 | 0.02399 | -0.0034435 | -0.073242 | 60.2005 | -61.2808 | 60.4065 | -61.0474 | -61.496 | -61.4594 | 0.027466 | 60.1776 | -61.322 | 60.3561 | -61.2213 | -61.3678 | -61.3358 | 0.004577 | -0.13733 | 0.068664 | 0.23804 | -0.17395 | -0.21057 | -0.17853 | -0.21515 | -0.036621 | -0.16022 | 0.01831 | 0.064087 | -0.050354 | -0.082398 | -0.013733 | -0.045777 | 0.23346 | 121.6873 | 0.10071 | 121.6782 | 121.4813 | 121.4996 | 121.4859 | 121.463 | -121.6187 | -121.6599 | 121.6919 | 121.6415 | 61.2122 | 61.3129
549.0938 | 121.9391 | -61.2579 | 60.26 | -0.12794 | 0.0095212 | 0.068173 | 0.064593 | -0.00063233 | -0.0073252 | -0.0019461 | -0.06192 | 0.0038153 | 0.067909 | 0.055173 | -0.011961 | 0.02634 | -0.0057935 | -0.13275 | 60.1273 | -61.2854 | 60.4156 | -61.0153 | -61.4914 | -61.4319 | 0 | 60.0998 | -61.3403 | 60.3745 | -61.1801 | -61.322 | -61.2854 | -0.027465 | -0.13275 | 0.15564 | 0.24262 | -0.17395 | -0.23346 | -0.14648 | -0.20599 | -0.082397 | -0.16022 | 0.11444 | 0.07782 | -0.027465 | -0.064086 | 0.054932 | 0.018311 | 0.27008 | 121.701 | 0.16022 | 121.7148 | 121.4127 | 121.4401 | 121.3852 | 121.3577 | -121.5454 | -121.6003 | 121.6736 | 121.6324 | 61.1252 | 61.2579
550.7656 | 121.9437 | -61.1755 | 60.4111 | -0.074539 | 0.0050352 | 0.066892 | 0.059893 | -0.0059729 | -0.0077524 | -2.3544e-05 | 0.020477 | 0.0036017 | 0.065345 | 0.050259 | -0.011961 | 0.024844 | -0.00023931 | 0.041199 | 60.2051 | -61.2076 | 60.5484 | -60.878 | -61.3174 | -61.2946 | 0.21515 | 60.2234 | -61.1893 | 60.4752 | -61.0611 | -61.1847 | -61.2213 | -0.032044 | -0.20599 | 0.13733 | 0.29755 | -0.11902 | -0.14191 | -0.086975 | -0.10986 | -0.013733 | -0.18768 | 0.064087 | 0.11444 | -0.045776 | -0.009155 | -0.032043 | 0.004578 | 0.32959 | 121.756 | 0.12817 | 121.6644 | 121.4127 | 121.4127 | 121.3806 | 121.3989 | -121.6187 | -121.6003 | 121.7239 | 121.6507 | 61.2167 | 61.3907
552.5156 | 121.8521 | -61.29 | 60.3195 | -0.089798 | 0.0061032 | 0.066678 | 0.062671 | -0.0017005 | -0.009675 | -0.0015189 | -0.089386 | 0.0059515 | 0.065559 | 0.056668 | -0.013242 | 0.026126 | -0.0075025 | -0.07782 | 60.2051 | -61.2808 | 60.3973 | -61.0474 | -61.4914 | -61.4594 | 0.009155 | 60.1913 | -61.2991 | 60.3516 | -61.2396 | -61.3724 | -61.3312 | 0.009155 | -0.11444 | 0.07782 | 0.24262 | -0.16937 | -0.20142 | -0.17853 | -0.21057 | -0.009155 | -0.12817 | 0.032043 | 0.050354 | -0.041199 | -0.082397 | -0.032044 | -0.073242 | 0.23346 | 121.6782 | 0.059509 | 121.6507 | 121.4859 | 121.4905 | 121.4951 | 121.4813 | -121.6003 | -121.6187 | 121.6873 | 121.6415 | 61.2122 | 61.2991
554.2656 | 121.8109 | -61.322 | 60.3333 | -0.06691 | 0.0065304 | 0.067746 | 0.063098 | -0.0010595 | -0.0075388 | -0.00066434 | -0.089386 | 0.0042425 | 0.0662 | 0.053464 | -0.015379 | 0.025058 | -0.0034435 | -0.17853 | 60.173 | -61.322 | 60.3012 | -61.1572 | -61.6058 | -61.5601 | -0.14648 | 60.1593 | -61.3632 | 60.26 | -61.3358 | -61.4777 | -61.4182 | 0 | -0.16022 | -0.032044 | 0.16479 | -0.23804 | -0.28381 | -0.23804 | -0.28381 | -0.041199 | -0.17395 | -0.073242 | -0.013733 | -0.096131 | -0.15564 | -0.054932 | -0.11444 | 0.16479 | 121.6232 | 0.027466 | 121.6232 | 121.4951 | 121.5225 | 121.4951 | 121.4813 | -121.6553 | -121.6965 | 121.6232 | 121.582 | 61.1435 | 61.1755
555.9531 | 121.9437 | -61.2534 | 60.2737 | -0.13557 | 0.007385 | 0.066251 | 0.063525 | 0.0010767 | -0.007966 | -0.0015189 | -0.04361 | 0.0050971 | 0.065345 | 0.057309 | -0.012602 | 0.026126 | -0.0025891 | -0.16937 | 60.1456 | -61.2946 | 60.4294 | -61.0382 | -61.4868 | -61.441 | -0.022888 | 60.1044 | -61.3174 | 60.379 | -61.203 | -61.322 | -61.2808 | -0.041199 | -0.12817 | 0.15564 | 0.21515 | -0.18768 | -0.23346 | -0.14648 | -0.19226 | -0.064087 | -0.16937 | 0.10528 | 0.050354 | -0.027466 | -0.068664 | 0.036621 | -0.004577 | 0.25635 | 121.7239 | 0.11444 | 121.6965 | 121.4401 | 121.4218 | 121.3989 | 121.3577 | -121.5683 | -121.5912 | 121.6827 | 121.6324 | 61.084 | 61.2305
557.7031 | 121.9116 | -61.2579 | 60.347 | -0.10506 | 0.0061032 | 0.065824 | 0.061816 | -0.0023413 | -0.0081796 | -0.0032277 | 0.011322 | 0.0033881 | 0.064918 | 0.051541 | -0.011106 | 0.022708 | -0.0015209 | -0.1236 | 60.173 | -61.2762 | 60.4202 | -61.0153 | -61.4731 | -61.4044 | 0 | 60.1685 | -61.29 | 60.379 | -61.1938 | -61.2991 | -61.2808 | -0.01831 | -0.17395 | 0.073242 | 0.24262 | -0.14648 | -0.21515 | -0.12817 | -0.19684 | -0.032043 | -0.17853 | 0.032043 | 0.064087 | -0.022888 | -0.041198 | 0.009155 | -0.009155 | 0.26093 | 121.6965 | 0.09613 | 121.669 | 121.4493 | 121.4584 | 121.431 | 121.4264 | -121.6232 | -121.637 | 121.6782 | 121.637 | 61.1343 | 61.2579
559.3906 | 121.962 | -61.1664 | 60.3607 | -0.12794 | 0.0026852 | 0.06561 | 0.060107 | -0.0027685 | -0.010316 | -0.00087794 | -0.01004 | 0.0036017 | 0.0662 | 0.047055 | -0.011961 | 0.025058 | -0.0053661 | -0.027466 | 60.2005 | -61.2259 | 60.5164 | -60.9283 | -61.3495 | -61.3083 | 0.15564 | 60.2142 | -61.2167 | 60.466 | -61.0886 | -61.2122 | -61.1984 | -0.059509 | -0.16022 | 0.15564 | 0.23804 | -0.14191 | -0.18311 | -0.082398 | -0.1236 | -0.050354 | -0.14648 | 0.10529 | 0.07782 | -0.032043 | -0.045776 | 0.018311 | 0.004578 | 0.29755 | 121.7422 | 0.12817 | 121.6827 | 121.4264 | 121.431 | 121.3669 | 121.3806 | -121.5866 | -121.5775 | 121.6827 | 121.6324 | 61.1389 | 61.322
561.1406 | 121.8796 | -61.2534 | 60.3561 | -0.082169 | 0.0050352 | 0.063474 | 0.064807 | 0.00064947 | -0.0090342 | -0.0045095 | -0.10159 | 0.0063787 | 0.064918 | 0.050686 | -0.012174 | 0.024631 | -0.0062207 | -0.050354 | 60.2051 | -61.2717 | 60.4019 | -61.0519 | -61.4822 | -61.4594 | 0.032043 | 60.2051 | -61.2854 | 60.3516 | -61.2259 | -61.3861 | -61.3312 | -0.01831 | -0.15106 | 0.045777 | 0.20142 | -0.20599 | -0.22888 | -0.18768 | -0.21057 | -0.032043 | -0.15106 | -0.004578 | 0.027466 | -0.07782 | -0.13275 | -0.045777 | -0.10071 | 0.21973 | 121.6736 | 0.059509 | 121.637 | 121.4767 | 121.4905 | 121.4584 | 121.4584 | -121.6278 | -121.6415 | 121.6553 | 121.6049 | 61.203 | 61.2854
562.875 | 121.8018 | -61.3083 | 60.3104 | -0.05928 | 0.0078122 | 0.06561 | 0.064807 | -0.0014867 | -0.0088206 | -0.0017325 | -0.11685 | 0.0046697 | 0.067268 | 0.055173 | -0.012602 | 0.023776 | -0.0015209 | -0.16937 | 60.1685 | -61.3312 | 60.3149 | -61.1481 | -61.6104 | -61.5555 | -0.15106 | 60.1685 | -61.3632 | 60.26 | -61.3266 | -61.4639 | -61.3998 | -0.022888 | -0.14191 | 0.004577 | 0.16022 | -0.24719 | -0.30212 | -0.2243 | -0.27924 | -0.054931 | -0.14191 | -0.050354 | -0.01831 | -0.091552 | -0.15564 | -0.036621 | -0.10071 | 0.18311 | 121.6461 | 0.036621 | 121.6232 | 121.4996 | 121.5317 | 121.4767 | 121.4767 | -121.6415 | -121.6736 | 121.6232 | 121.5683 | 61.1389 | 61.1572
564.625 | 121.8292 | -61.3174 | 60.3195 | -0.15083 | 0.0080258 | 0.066251 | 0.064593 | -0.0031957 | -0.0075388 | -0.0036551 | -0.064972 | 0.0057379 | 0.065345 | 0.052823 | -0.01132 | 0.024417 | -0.0049389 | -0.22888 | 60.1547 | -61.3266 | 60.2875 | -61.1938 | -61.615 | -61.5646 | -0.15106 | 60.0998 | -61.3495 | 60.2783 | -61.3174 | -61.4594 | -61.4044 | -0.009155 | -0.16479 | -0.032043 | 0.1236 | -0.24719 | -0.29755 | -0.23804 | -0.28839 | -0.032043 | -0.21973 | -0.041199 | 0 | -0.086975 | -0.14191 | -0.054932 | -0.10986 | 0.13275 | 121.6141 | 0.032043 | 121.6278 | 121.4813 | 121.4493 | 121.4722 | 121.4172 | -121.6461 | -121.669 | 121.6049 | 121.5958 | 61.0886 | 61.1664
566.375 | 121.9528 | -61.1893 | 60.3607 | -0.051651 | 0.003967 | 0.064969 | 0.059039 | -0.0059729 | -0.007966 | -0.0013051 | -0.0069885 | 0.0042425 | 0.066413 | 0.053677 | -0.012815 | 0.026126 | -0.0064343 | -0.009155 | 60.1959 | -61.203 | 60.5026 | -60.9329 | -61.3495 | -61.3174 | 0.15564 | 60.1685 | -61.2213 | 60.466 | -61.0977 | -61.203 | -61.2122 | -0.013733 | -0.16479 | 0.14191 | 0.25635 | -0.12817 | -0.16022 | -0.11444 | -0.14648 | -0.032043 | -0.19226 | 0.10529 | 0.091553 | -0.022888 | -0.013733 | 0.009155 | 0.01831 | 0.27008 | 121.7056 | 0.1236 | 121.6873 | 121.3989 | 121.3898 | 121.3852 | 121.3577 | -121.5637 | -121.582 | 121.6919 | 121.6553 | 61.1801 | 61.3449
568.0625 | 121.8292 | -61.3174 | 60.3287 | -0.10506 | 0.0048214 | 0.068601 | 0.064166 | -0.0021277 | -0.008607 | -0.0049367 | -0.077179 | 0.0038153 | 0.064918 | 0.046628 | -0.013029 | 0.025912 | -0.0025891 | -0.23346 | 60.1547 | -61.3312 | 60.2783 | -61.1618 | -61.6058 | -61.5555 | -0.16022 | 60.1456 | -61.3449 | 60.2829 | -61.3358 | -61.4502 | -61.409 | -0.013733 | -0.17395 | -0.050354 | 0.15564 | -0.23804 | -0.28839 | -0.2243 | -0.27466 | -0.027466 | -0.1831 | -0.045776 | -0.01831 | -0.091553 | -0.13275 | -0.064087 | -0.10529 | 0.16937 | 121.6095 | 0.009156 | 121.6278 | 121.4859 | 121.4905 | 121.4722 | 121.463 | -121.6599 | -121.6736 | 121.5958 | 121.6003 | 61.084 | 61.1572
569.75 | 121.8384 | -61.2442 | 60.4111 | -0.036392 | 0.0041806 | 0.063474 | 0.061175 | 0.0015039 | -0.0090342 | -0.00087794 | -0.068024 | 0.0057379 | 0.065772 | 0.054959 | -0.010893 | 0.024844 | -0.0038709 | -0.045776 | 60.26 | -61.2396 | 60.3882 | -61.0748 | -61.5005 | -61.4548 | 0.004578 | 60.2417 | -61.2717 | 60.3333 | -61.2305 | -61.3541 | -61.3403 | 0.004578 | -0.15106 | -0.022888 | 0.16937 | -0.21057 | -0.25635 | -0.21515 | -0.26093 | -0.027465 | -0.16937 | -0.07782 | 0.013733 | -0.09613 | -0.10986 | -0.068665 | -0.082398 | 0.16479 | 121.6278 | 0.041198 | 121.6049 | 121.4996 | 121.5134 | 121.5042 | 121.4859 | -121.6507 | -121.6827 | 121.6324 | 121.5775 | 61.1984 | 61.2488
571.5 | 121.8292 | -61.2991 | 60.2966 | -0.097427 | 0.0097348 | 0.066037 | 0.061816 | -0.0055457 | -0.0058298 | -0.0032277 | -0.06192 | 0.0046697 | 0.066413 | 0.057309 | -0.011961 | 0.026981 | -0.0017347 | -0.20599 | 60.1822 | -61.3358 | 60.2921 | -61.1938 | -61.6333 | -61.5875 | -0.16022 | 60.141 | -61.3678 | 60.2737 | -61.3541 | -61.4914 | -61.4182 | -0.036621 | -0.11444 | -0.004578 | 0.10528 | -0.28839 | -0.33417 | -0.25177 | -0.29755 | -0.068665 | -0.15564 | -0.022888 | -0.054932 | -0.11902 | -0.19226 | -0.050354 | -0.1236 | 0.14191 | 121.6278 | 0.013733 | 121.6415 | 121.5179 | 121.5088 | 121.4813 | 121.4401 | -121.6324 | -121.6644 | 121.5912 | 121.5729 | 61.0931 | 61.1389
573.25 | 121.8567 | -61.3266 | 60.2783 | -0.089798 | 0.0065304 | 0.067746 | 0.063739 | -0.0042639 | -0.0071116 | -0.0051505 | -0.074127 | 0.0068059 | 0.065132 | 0.053891 | -0.013242 | 0.025912 | -0.0032299 | -0.22888 | 60.1822 | -61.3083 | 60.3149 | -61.1526 | -61.5829 | -61.5417 | -0.14648 | 60.1501 | -61.3495 | 60.2921 | -61.322 | -61.4365 | -61.4044 | 0.01831 | -0.09613 | 0.036621 | 0.17395 | -0.21515 | -0.25635 | -0.23346 | -0.27466 | -0.022888 | -0.12817 | 0.013733 | 0.004578 | -0.07782 | -0.10986 | -0.054932 | -0.086975 | 0.15564 | 121.6232 | 0.027466 | 121.6415 | 121.4905 | 121.4996 | 121.5088 | 121.4767 | -121.5866 | -121.6278 | 121.6415 | 121.6187 | 61.0977 | 61.1801
575 | 121.9391 | -61.171 | 60.3699 | -0.082169 | 0.0048214 | 0.066251 | 0.057757 | -0.0083227 | -0.009675 | -0.0021597 | -0.0008851 | 0.0033881 | 0.066413 | 0.045773 | -0.013456 | 0.025272 | -0.0042981 | 0.064087 | 60.228 | -61.2213 | 60.5438 | -60.8734 | -61.322 | -61.2991 | 0.20599 | 60.2234 | -61.2259 | 60.466 | -61.0748 | -61.1984 | -61.2259 | -0.050354 | -0.14191 | 0.17395 | 0.29755 | -0.12817 | -0.15106 | -0.07782 | -0.10071 | -0.054932 | -0.14648 | 0.09613 | 0.09613 | -0.054932 | -0.027466 | 0 | 0.027466 | 0.3479 | 121.7651 | 0.15106 | 121.6919 | 121.4493 | 121.4493 | 121.3989 | 121.3943 | -121.5912 | -121.5958 | 121.7148 | 121.637 | 61.235 | 61.377
576.75 | 121.8521 | -61.2534 | 60.3699 | -0.082169 | 0.0067442 | 0.064756 | 0.06502 | 0.0025721 | -0.0071116 | -0.0030141 | -0.080231 | 0.0036017 | 0.065132 | 0.059445 | -0.013029 | 0.025485 | -0.0077161 | -0.036621 | 60.2417 | -61.29 | 60.3882 | -61.0703 | -61.4822 | -61.4548 | 0.004578 | 60.2005 | -61.2808 | 60.3561 | -61.2442 | -61.3586 | -61.3312 | -0.036621 | -0.12817 | 0.018311 | 0.18311 | -0.20142 | -0.22888 | -0.1648 | -0.19226 | -0.027466 | -0.16937 | -0.013733 | 0.009155 | -0.07782 | -0.10529 | -0.050354 | -0.07782 | 0.21973 | 121.6782 | 0.036621 | 121.637 | 121.5317 | 121.4813 | 121.4951 | 121.4539 | -121.6599 | -121.6507 | 121.6415 | 121.6095 | 61.2167 | 61.2579
578.4375 | 121.8933 | -61.2213 | 60.3653 | -0.13557 | 0.003967 | 0.065183 | 0.058398 | 0.00022207 | -0.0088206 | -0.0023733 | 0.0052185 | 0.0027471 | 0.066841 | 0.049191 | -0.013242 | 0.022922 | -0.0010937 | -0.082397 | 60.1822 | -61.2442 | 60.4202 | -61.0199 | -61.4502 | -61.3998 | 0.004578 | 60.1822 | -61.2442 | 60.3928 | -61.1801 | -61.2946 | -61.2808 | -0.022889 | -0.18311 | 0.054932 | 0.20142 | -0.17853 | -0.22888 | -0.15564 | -0.20599 | -0.022889 | -0.18311 | 0.027466 | 0.041198 | -0.05951 | -0.073243 | -0.036621 | -0.050354 | 0.22431 | 121.6644 | 0.064087 | 121.637 | 121.4264 | 121.4264 | 121.4035 | 121.4035 | -121.6095 | -121.6095 | 121.6415 | 121.6141 | 61.1389 | 61.2259
580.1875 | 121.8704 | -61.2625 | 60.3653 | -0.074539 | 0.0058896 | 0.066251 | 0.06203 | 0.0012903 | -0.0092478 | -0.0034415 | -0.06192 | 0.0050971 | 0.065772 | 0.051968 | -0.011961 | 0.025058 | -0.0032299 | -0.050354 | 60.1959 | -61.2625 | 60.4111 | -61.0428 | -61.4731 | -61.4685 | 0.013733 | 60.1868 | -61.3037 | 60.347 | -61.2259 | -61.3678 | -61.3266 | 0 | -0.16937 | 0.045777 | 0.21973 | -0.20599 | -0.21057 | -0.20599 | -0.21057 | -0.041199 | -0.17853 | -0.01831 | 0.036621 | -0.064087 | -0.10529 | -0.022888 | -0.064087 | 0.21973 | 121.6736 | 0.07782 | 121.6507 | 121.4584 | 121.4905 | 121.4584 | 121.4493 | -121.6278 | -121.669 | 121.6736 | 121.6095 | 61.2122 | 61.2762
581.9375 | 121.843 | -61.3174 | 60.3104 | -0.097427 | 0.0054624 | 0.065824 | 0.063311 | -0.00063233 | -0.01117 | -0.0034415 | -0.089386 | 0.0046697 | 0.0662 | 0.05795 | -0.013456 | 0.023563 | -0.0057935 | -0.21515 | 60.1776 | -61.322 | 60.2966 | -61.1389 | -61.5921 | -61.5509 | -0.13275 | 60.1501 | -61.322 | 60.2921 | -61.3083 | -61.4456 | -61.3907 | -0.004577 | -0.13275 | -0.013733 | 0.17853 | -0.23346 | -0.27466 | -0.22888 | -0.27008 | -0.004577 | -0.16022 | -0.018311 | 0.009155 | -0.073242 | -0.12817 | -0.068665 | -0.1236 | 0.1831 | 121.6187 | 0.013732 | 121.6141 | 121.4996 | 121.4722 | 121.4951 | 121.4676 | -121.6324 | -121.6324 | 121.6141 | 121.6095 | 61.1023 | 61.1847
583.6875 | 121.8658 | -61.2122 | 60.4065 | -0.11269 | 0.0041806 | 0.065183 | 0.058825 | 0.0038537 | -0.010316 | -0.0028005 | -0.01004 | 0.0038153 | 0.065986 | 0.055173 | -0.014524 | 0.024417 | -0.0036573 | 0.064087 | 60.2188 | -61.1938 | 60.5072 | -60.9375 | -61.3632 | -61.3312 | 0.14648 | 60.2371 | -61.2259 | 60.4019 | -61.1664 | -61.2808 | -61.2717 | 0.01831 | -0.18768 | 0.10071 | 0.27466 | -0.11902 | -0.15106 | -0.13733 | -0.16937 | -0.013733 | -0.16937 | -0.004577 | 0.045776 | -0.059509 | -0.068665 | -0.045776 | -0.054932 | 0.25635 | 121.7011 | 0.059509 | 121.6278 | 121.4127 | 121.463 | 121.431 | 121.4493 | -121.6003 | -121.6324 | 121.7194 | 121.6141 | 61.2762 | 61.3586
585.3594 | 121.8292 | -61.2991 | 60.2921 | -0.12032 | 0.0065304 | 0.067319 | 0.062243 | 0.00086307 | -0.008607 | 0.0010447 | -0.086334 | 0.0059515 | 0.066841 | 0.054104 | -0.013242 | 0.026126 | -0.0077161 | -0.23346 | 60.1685 | -61.3449 | 60.2829 | -61.1801 | -61.5921 | -61.5601 | -0.16479 | 60.1685 | -61.3724 | 60.2921 | -61.3174 | -61.4548 | -61.3998 | -0.045777 | -0.1236 | -0.009155 | 0.11902 | -0.26093 | -0.29297 | -0.21515 | -0.24719 | -0.073242 | -0.1236 | 0 | -0.018311 | -0.10071 | -0.15564 | -0.027466 | -0.082398 | 0.16479 | 121.6278 | 0.054931 | 121.6644 | 121.5134 | 121.5408 | 121.4676 | 121.4676 | -121.637 | -121.6644 | 121.582 | 121.5912 | 61.0657 | 61.1343
587.1094 | 121.9299 | -61.203 | 60.3745 | -0.10506 | 0.0054624 | 0.065824 | 0.059466 | -0.0059729 | -0.0098886 | -0.00087794 | -0.0069885 | 0.0027471 | 0.065345 | 0.057309 | -0.012388 | 0.023563 | -0.0030163 | -0.068665 | 60.1822 | -61.2305 | 60.4477 | -60.9833 | -61.4044 | -61.3724 | 0.086975 | 60.1776 | -61.2534 | 60.4431 | -61.116 | -61.2213 | -61.2076 | -0.027466 | -0.19226 | 0.073242 | 0.21973 | -0.16937 | -0.20142 | -0.14191 | -0.17395 | -0.050354 | -0.19684 | 0.068664 | 0.086975 | -0.004578 | -0.01831 | 0.045776 | 0.032044 | 0.24719 | 121.6782 | 0.13733 | 121.6965 | 121.4127 | 121.431 | 121.3852 | 121.3806 | -121.6049 | -121.6278 | 121.6507 | 121.6461 | 61.1343 | 61.29
588.8438 | 121.9391 | -61.2717 | 60.2966 | -0.15846 | 0.0063168 | 0.067319 | 0.060107 | -0.0029821 | -0.0075388 | -0.0013051 | -0.04361 | 0.0046697 | 0.065772 | 0.051541 | -0.013883 | 0.02399 | -0.0038709 | -0.13733 | 60.1181 | -61.3083 | 60.4294 | -61.0016 | -61.4639 | -61.4182 | 0.027466 | 60.1089 | -61.2991 | 60.4019 | -61.1893 | -61.2991 | -61.2671 | -0.036622 | -0.17853 | 0.13275 | 0.27008 | -0.14648 | -0.19226 | -0.10986 | -0.15564 | -0.027466 | -0.18768 | 0.10529 | 0.082397 | 0.004577 | -0.027466 | 0.032043 | 0 | 0.3067 | 121.7377 | 0.10986 | 121.701 | 121.4264 | 121.4081 | 121.3898 | 121.3806 | -121.6049 | -121.5958 | 121.701 | 121.6736 | 61.1343 | 61.2991
590.5781 | 121.962 | -61.1847 | 60.3745 | -0.089798 | 0.0078122 | 0.064115 | 0.05968 | -0.00084593 | -0.010316 | -0.0060049 | 0.023529 | 0.0038153 | 0.065772 | 0.057309 | -0.014738 | 0.023776 | -0.0040845 | -0.022888 | 60.2051 | -61.2259 | 60.4935 | -60.9283 | -61.377 | -61.3358 | 0.15564 | 60.1868 | -61.2305 | 60.4706 | -61.1023 | -61.2076 | -61.1938 | -0.041199 | -0.16937 | 0.11902 | 0.25635 | -0.15106 | -0.19226 | -0.10986 | -0.15106 | -0.045777 | -0.18768 | 0.09613 | 0.082397 | -0.009156 | -0.022889 | 0.036621 | 0.022888 | 0.29755 | 121.7194 | 0.12817 | 121.7011 | 121.431 | 121.4172 | 121.3898 | 121.3715 | -121.6003 | -121.6049 | 121.6782 | 121.6553 | 61.1618 | 61.3403
592.3281 | 121.9574 | -61.2579 | 60.2783 | -0.1432 | 0.0063168 | 0.06561 | 0.060748 | 0.00064947 | -0.0073252 | -0.00066434 | -0.068024 | 0.0033881 | 0.065986 | 0.057736 | -0.014311 | 0.026981 | -0.0042981 | -0.14191 | 60.1273 | -61.2946 | 60.4248 | -61.0336 | -61.4868 | -61.4365 | -0.004578 | 60.1227 | -61.3129 | 60.3928 | -61.1938 | -61.3174 | -61.2762 | -0.036621 | -0.15106 | 0.14648 | 0.22431 | -0.17853 | -0.22888 | -0.14191 | -0.19226 | -0.054931 | -0.15564 | 0.11444 | 0.064087 | -0.01831 | -0.059509 | 0.036621 | -0.004578 | 0.26093 | 121.7194 | 0.11902 | 121.7056 | 121.4218 | 121.4355 | 121.3852 | 121.3806 | -121.5729 | -121.5912 | 121.6827 | 121.6507 | 61.116 | 61.2534
594 | 121.8384 | -61.2122 | 60.434 | -0.051651 | 0.0026852 | 0.06561 | 0.061816 | -0.0061865 | -0.01053 | -0.0023733 | -0.040558 | 0.0057379 | 0.068122 | 0.052823 | -0.012815 | 0.023776 | -0.0030163 | 0.041199 | 60.2188 | -61.2442 | 60.4706 | -60.9924 | -61.4227 | -61.3998 | 0.09613 | 60.2509 | -61.235 | 60.3699 | -61.2076 | -61.3129 | -61.3358 | -0.032044 | -0.21515 | 0.036621 | 0.21973 | -0.18768 | -0.21057 | -0.15564 | -0.17853 | -0.022888 | -0.18311 | -0.064087 | 0.004577 | -0.1236 | -0.10071 | -0.10071 | -0.07782 | 0.25177 | 121.7148 | 0.027465 | 121.6049 | 121.463 | 121.4859 | 121.431 | 121.463 | -121.6782 | -121.669 | 121.6827 | 121.582 | 61.2534 | 61.3083
595.7344 | 121.8613 | -61.2671 | 60.3836 | -0.044022 | 0.005676 | 0.066678 | 0.063098 | 0.0019311 | -0.010316 | -0.0040823 | -0.09549 | 0.0048833 | 0.066627 | 0.052823 | -0.011961 | 0.025485 | -0.0066479 | -0.032043 | 60.2554 | -61.2396 | 60.3973 | -61.0748 | -61.4822 | -61.4639 | 0.009155 | 60.2005 | -61.3037 | 60.347 | -61.2305 | -61.3586 | -61.3403 | 0.027466 | -0.12817 | 0.013733 | 0.19226 | -0.19684 | -0.21515 | -0.2243 | -0.24262 | -0.036621 | -0.18311 | -0.036621 | 0.036621 | -0.073242 | -0.091553 | -0.036621 | -0.054932 | 0.16479 | 121.637 | 0.073242 | 121.6507 | 121.4951 | 121.5042 | 121.5225 | 121.4676 | -121.6232 | -121.6873 | 121.6644 | 121.6141 | 61.235 | 61.2762
597.4219 | 121.8704 | -61.2671 | 60.3653 | -0.089798 | 0.0061032 | 0.06561 | 0.063952 | -0.00063233 | -0.0090342 | -0.0013051 | -0.083283 | 0.0025335 | 0.065986 | 0.054745 | -0.013242 | 0.025699 | -0.0023755 | -0.054932 | 60.2325 | -61.2762 | 60.4065 | -61.0428 | -61.4868 | -61.4548 | 0.041199 | 60.1822 | -61.29 | 60.347 | -61.2259 | -61.3632 | -61.3358 | -0.009155 | -0.13275 | 0.041199 | 0.2243 | -0.18768 | -0.21973 | -0.17853 | -0.21057 | -0.022888 | -0.18311 | -0.01831 | 0.041199 | -0.068664 | -0.09613 | -0.045776 | -0.073242 | 0.23346 | 121.6827 | 0.064087 | 121.637 | 121.5088 | 121.4722 | 121.4996 | 121.4493 | -121.6415 | -121.6553 | 121.6736 | 121.6141 | 61.2122 | 61.3083
599.1562 | 121.8018 | -61.3312 | 60.3149 | -0.11269 | 0.0082394 | 0.062619 | 0.063525 | -0.00020513 | -0.008607 | -0.0021597 | -0.089386 | 0.0050971 | 0.067268 | 0.053036 | -0.012602 | 0.025912 | -0.0045117 | -0.19684 | 60.1639 | -61.3449 | 60.3104 | -61.171 | -61.6196 | -61.5601 | -0.16022 | 60.1822 | -61.3312 | 60.2554 | -61.3678 | -61.5051 | -61.4273 | -0.013733 | -0.15106 | -0.004577 | 0.16022 | -0.22888 | -0.28839 | -0.21515 | -0.27466 | 0 | -0.13275 | -0.059509 | -0.036621 | -0.09613 | -0.17395 | -0.09613 | -0.17395 | 0.17395 | 121.6553 | -0.036621 | 121.5866 | 121.5088 | 121.5134 | 121.4951 | 121.5134 | -121.6599 | -121.6461 | 121.6415 | 121.5866 | 61.1343 | 61.171
600.9062 | 121.8842 | -61.2213 | 60.3516 | -0.089798 | 0.0052488 | 0.065396 | 0.062671 | 0.0044947 | -0.0088206 | -0.0045095 | -0.0039367 | 0.0033881 | 0.067909 | 0.049618 | -0.013456 | 0.026553 | -0.0045117 | -0.12817 | 60.1868 | -61.2305 | 60.4111 | -61.0199 | -61.4548 | -61.3953 | 0.004578 | 60.1501 | -61.3037 | 60.3882 | -61.1847 | -61.2946 | -61.2762 | -0.009156 | -0.16479 | 0.05951 | 0.20142 | -0.17395 | -0.23346 | -0.16479 | -0.2243 | -0.082398 | -0.20142 | 0.036622 | 0.036621 | -0.054932 | -0.073243 | 0.027466 | 0.009155 | 0.21057 | 121.6415 | 0.11902 | 121.6919 | 121.4172 | 121.4539 | 121.4081 | 121.3715 | -121.582 | -121.6553 | 121.6324 | 121.6095 | 61.0931 | 61.2259
602.5938 | 121.8796 | -61.2396 | 60.4111 | -0.12794 | 0.0037534 | 0.063474 | 0.057544 | -0.0021277 | -0.010102 | -0.0023733 | -0.013092 | 0.0025335 | 0.067909 | 0.053036 | -0.011961 | 0.028049 | -0.0036573 | 0.054932 | 60.2142 | -61.2122 | 60.5118 | -60.9283 | -61.3632 | -61.3312 | 0.14191 | 60.2142 | -61.235 | 60.4019 | -61.1526 | -61.2671 | -61.2625 | 0.027466 | -0.19684 | 0.10071 | 0.31128 | -0.091553 | -0.1236 | -0.11902 | -0.15106 | 0.004578 | -0.19684 | -0.009155 | 0.086975 | -0.022888 | -0.027466 | -0.027466 | -0.032044 | 0.28381 | 121.7239 | 0.082397 | 121.637 | 121.4264 | 121.4493 | 121.4539 | 121.4539 | -121.6232 | -121.6461 | 121.7514 | 121.6415 | 61.2946 | 61.3815
604.3281 | 121.9162 | -61.2076 | 60.379 | -0.074539 | 0.0052488 | 0.064756 | 0.059466 | 0.0015039 | -0.008607 | -0.0015189 | 0.0021667 | 0.0023199 | 0.064918 | 0.054745 | -0.01367 | 0.025058 | -0.0025891 | -0.045776 | 60.2005 | -61.235 | 60.434 | -61.0107 | -61.4502 | -61.3907 | 0.059509 | 60.1639 | -61.2625 | 60.4019 | -61.1526 | -61.2579 | -61.2579 | -0.027465 | -0.17853 | 0.054932 | 0.19684 | -0.18311 | -0.24261 | -0.15564 | -0.21515 | -0.054931 | -0.21515 | 0.022889 | 0.054932 | -0.050354 | -0.050354 | 0.004577 | 0.004577 | 0.2243 | 121.669 | 0.10986 | 121.6644 | 121.4355 | 121.4264 | 121.4081 | 121.3715 | -121.6141 | -121.6415 | 121.6415 | 121.6095 | 61.1618 | 61.2671
606 | 121.8201 | -61.2442 | 60.434 | -0.0058748 | 0.0054624 | 0.065183 | 0.061389 | -0.0034095 | -0.008607 | -0.0010915 | -0.058869 | 0.0070197 | 0.065345 | 0.051327 | -0.013456 | 0.025272 | -0.0075025 | -0.036621 | 60.2554 | -61.235 | 60.3973 | -61.0611 | -61.4685 | -61.4502 | 0.032043 | 60.2509 | -61.2717 | 60.3424 | -61.2259 | -61.3678 | -61.3312 | 0.009156 | -0.17853 | -0.036621 | 0.18311 | -0.20599 | -0.2243 | -0.21515 | -0.23346 | -0.027465 | -0.18311 | -0.091553 | 0.018311 | -0.086975 | -0.1236 | -0.05951 | -0.096131 | 0.17395 | 121.6324 | 0.045776 | 121.6141 | 121.4905 | 121.5225 | 121.4996 | 121.4951 | -121.669 | -121.7056 | 121.6415 | 121.5866 | 61.2076 | 61.2762
607.75 | 121.9528 | -61.2579 | 60.2829 | -0.12794 | 0.0065304 | 0.068173 | 0.061389 | -0.0021277 | -0.007966 | -0.0015189 | -0.052765 | 0.0048833 | 0.064704 | 0.054532 | -0.01367 | 0.026126 | -0.0030163 | -0.1236 | 60.1318 | -61.3037 | 60.4202 | -61.0153 | -61.4868 | -61.4365 | -0.013733 | 60.0906 | -61.3083 | 60.3973 | -61.1938 | -61.3083 | -61.2808 | -0.045776 | -0.15106 | 0.13733 | 0.24262 | -0.17853 | -0.22888 | -0.13275 | -0.1831 | -0.050354 | -0.19226 | 0.11444 | 0.064087 | -0.022888 | -0.050354 | 0.027466 | 0 | 0.28839 | 121.7239 | 0.11444 | 121.7056 | 121.4355 | 121.3989 | 121.3898 | 121.3486 | -121.5866 | -121.5912 | 121.6782 | 121.6553 | 61.1343 | 61.2442
609.5 | 121.9299 | -61.2717 | 60.3012 | -0.15846 | 0.0071714 | 0.064756 | 0.05968 | 0.0010767 | -0.0073252 | -0.00066434 | -0.031403 | 0.0031745 | 0.067481 | 0.050473 | -0.013883 | 0.025058 | -0.0017347 | -0.13275 | 60.0952 | -61.29 | 60.4477 | -60.997 | -61.4685 | -61.4182 | 0.032043 | 60.1318 | -61.2946 | 60.3882 | -61.1938 | -61.3037 | -61.2854 | -0.018311 | -0.20599 | 0.14648 | 0.27466 | -0.14648 | -0.19684 | -0.12817 | -0.17853 | -0.022889 | -0.16937 | 0.086976 | 0.077819 | -0.013733 | -0.032044 | 0.009156 | -0.009155 | 0.29297 | 121.7377 | 0.10071 | 121.6827 | 121.3852 | 121.4264 | 121.3669 | 121.4035 | -121.5912 | -121.5958 | 121.7194 | 121.6599 | 61.1389 | 61.3037
611.1875 | 121.8109 | -61.3266 | 60.3058 | -0.028763 | 0.0069578 | 0.065183 | 0.063525 | 0.0023585 | -0.0077524 | -0.0025869 | -0.13211 | 0.0048833 | 0.067268 | 0.053036 | -0.013029 | 0.025058 | -0.0040845 | -0.18768 | 60.1456 | -61.3312 | 60.3149 | -61.171 | -61.6104 | -61.5555 | -0.15564 | 60.173 | -61.3586 | 60.2554 | -61.3541 | -61.4777 | -61.4227 | -0.004578 | -0.16022 | 0.009155 | 0.15564 | -0.22888 | -0.28381 | -0.2243 | -0.27924 | -0.032044 | -0.13275 | -0.050354 | -0.027466 | -0.09613 | -0.15106 | -0.064086 | -0.11902 | 0.16022 | 121.6461 | 0.004578 | 121.6141 | 121.4767 | 121.5317 | 121.4722 | 121.4996 | -121.637 | -121.6644 | 121.6415 | 121.582 | 61.1389 | 61.171
612.9375 | 121.907 | -61.2259 | 60.3745 | -0.12794 | 0.0061032 | 0.065824 | 0.060962 | 8.47e-06 | -0.008607 | -0.0032277 | -0.0008851 | 0.0048833 | 0.066841 | 0.060513 | -0.011747 | 0.024844 | -0.0064343 | -0.10986 | 60.1913 | -61.2488 | 60.4294 | -61.0107 | -61.4685 | -61.3998 | 0.018311 | 60.173 | -61.3129 | 60.3836 | -61.1893 | -61.3037 | -61.2808 | -0.022888 | -0.18311 | 0.054931 | 0.21515 | -0.17395 | -0.24262 | -0.15106 | -0.21973 | -0.086975 | -0.20142 | 0.009155 | 0.036621 | -0.054932 | -0.07782 | 0.032043 | 0.009155 | 0.23804 | 121.6782 | 0.1236 | 121.6965 | 121.4401 | 121.4859 | 121.4172 | 121.3989 | -121.6232 | -121.6873 | 121.6553 | 121.6095 | 61.116 | 61.2442
614.6875 | 121.875 | -61.2076 | 60.4065 | -0.11269 | 0.0061032 | 0.064328 | 0.059253 | -0.0029821 | -0.010743 | -0.0013051 | -0.034454 | 0.0046697 | 0.066627 | 0.052182 | -0.012174 | 0.024631 | -0.0060071 | 0.064087 | 60.2097 | -61.1984 | 60.5072 | -60.9329 | -61.3541 | -61.3266 | 0.16479 | 60.228 | -61.2167 | 60.4065 | -61.1572 | -61.2762 | -61.2671 | 0.009156 | -0.19684 | 0.10071 | 0.27466 | -0.11902 | -0.14648 | -0.12817 | -0.15564 | -0.009155 | -0.17853 | 0 | 0.050354 | -0.059509 | -0.068664 | -0.050354 | -0.059509 | 0.2655 | 121.7056 | 0.059509 | 121.6232 | 121.4081 | 121.4447 | 121.4172 | 121.4355 | -121.6049 | -121.6232 | 121.7148 | 121.6141 | 61.2717 | 61.3724
616.375 | 121.8658 | -61.3129 | 60.2783 | -0.10506 | 0.0086668 | 0.064115 | 0.063311 | -0.00041873 | -0.0090342 | -0.0010915 | -0.092438 | 0.0059515 | 0.065772 | 0.057522 | -0.013242 | 0.026767 | -0.0042981 | -0.21057 | 60.1639 | -61.3266 | 60.3287 | -61.1435 | -61.5921 | -61.5463 | -0.14191 | 60.1501 | -61.3541 | 60.3058 | -61.2991 | -61.4365 | -61.3678 | -0.013733 | -0.11444 | 0.050354 | 0.16937 | -0.23346 | -0.27924 | -0.21973 | -0.2655 | -0.041199 | -0.12817 | 0.027466 | 0.013733 | -0.054932 | -0.1236 | -0.013733 | -0.082397 | 0.18311 | 121.6553 | 0.054932 | 121.6599 | 121.4905 | 121.5042 | 121.4767 | 121.463 | -121.6049 | -121.6324 | 121.6415 | 121.6187 | 61.1023 | 61.171
618.125 | 121.9345 | -61.1755 | 60.3836 | -0.13557 | 0.0033262 | 0.065183 | 0.060748 | -0.0040503 | -0.0075388 | -0.0038687 | -0.01004 | 0.0044561 | 0.065345 | 0.054318 | -0.013029 | 0.024204 | -0.0083569 | 0.064087 | 60.2051 | -61.1847 | 60.5576 | -60.8917 | -61.3403 | -61.3083 | 0.20142 | 60.1822 | -61.2396 | 60.466 | -61.0794 | -61.2076 | -61.2122 | -0.009155 | -0.17853 | 0.17395 | 0.28381 | -0.13275 | -0.16479 | -0.1236 | -0.15564 | -0.064087 | -0.20142 | 0.082397 | 0.09613 | -0.036621 | -0.032044 | 0.027466 | 0.032043 | 0.29297 | 121.7422 | 0.16022 | 121.7056 | 121.3898 | 121.4218 | 121.3806 | 121.3577 | -121.5683 | -121.6232 | 121.7331 | 121.6415 | 61.2396 | 61.377
619.8125 | 121.907 | -61.2213 | 60.3516 | -0.12794 | 0.0050352 | 0.06561 | 0.061175 | -0.0019141 | -0.0083932 | -0.0023733 | -0.034454 | 0.0036017 | 0.064491 | 0.062863 | -0.012602 | 0.023349 | -0.0055799 | -0.10071 | 60.1593 | -61.2946 | 60.4202 | -61.0245 | -61.4639 | -61.409 | 0.004578 | 60.1776 | -61.2717 | 60.3973 | -61.1893 | -61.3083 | -61.2808 | -0.073243 | -0.19226 | 0.068665 | 0.19684 | -0.18768 | -0.24262 | -0.11444 | -0.16937 | -0.050354 | -0.17395 | 0.045777 | 0.032043 | -0.05951 | -0.086976 | -0.009156 | -0.036622 | 0.27008 | 121.7148 | 0.082397 | 121.669 | 121.4539 | 121.4493 | 121.3806 | 121.3989 | -121.6461 | -121.6232 | 121.6415 | 121.6187 | 61.1206 | 61.2259
621.5625 | 121.8018 | -61.3449 | 60.3149 | -0.12032 | 0.0065304 | 0.068173 | 0.065448 | 0.0010767 | -0.0047616 | -0.0015189 | -0.13211 | 0.0050971 | 0.068122 | 0.061368 | -0.012602 | 0.02634 | -0.0038709 | -0.21973 | 60.1639 | -61.322 | 60.2966 | -61.1984 | -61.647 | -61.5875 | -0.16479 | 60.1364 | -61.3541 | 60.2692 | -61.3495 | -61.4639 | -61.4227 | 0.022889 | -0.15106 | -0.01831 | 0.14648 | -0.24261 | -0.30212 | -0.2655 | -0.32501 | -0.009155 | -0.17853 | -0.045776 | -0.004577 | -0.077819 | -0.11902 | -0.068664 | -0.10986 | 0.1236 | 121.6187 | 0.004578 | 121.6232 | 121.4859 | 121.4905 | 121.5088 | 121.4813 | -121.637 | -121.669 | 121.6415 | 121.6141 | 61.1252 | 61.1801
623.25 | 121.7972 | -61.3358 | 60.3149 | -0.12032 | 0.0086668 | 0.065824 | 0.065234 | 0.0010767 | -0.0083932 | -0.0025869 | -0.089386 | 0.0050971 | 0.065559 | 0.054959 | -0.012388 | 0.025485 | -0.0034435 | -0.21057 | 60.1685 | -61.322 | 60.3012 | -61.1755 | -61.6241 | -61.5738 | -0.18768 | 60.1685 | -61.3678 | 60.2463 | -61.3724 | -61.4822 | -61.4227 | 0.013733 | -0.14648 | -0.013733 | 0.16022 | -0.23804 | -0.28839 | -0.25177 | -0.30213 | -0.032044 | -0.14648 | -0.068664 | -0.036621 | -0.086975 | -0.14648 | -0.054931 | -0.11444 | 0.14648 | 121.6232 | -0.004577 | 121.6141 | 121.4905 | 121.5363 | 121.5042 | 121.5042 | -121.637 | -121.6827 | 121.637 | 121.582 | 61.1252 | 61.1481
624.9375 | 121.962 | -61.203 | 60.3836 | -0.089798 | 0.0041806 | 0.066037 | 0.05968 | -0.00063233 | -0.0073252 | -0.0017325 | -0.0039367 | 0.0027471 | 0.067054 | 0.048977 | -0.011961 | 0.022922 | -0.0079297 | -0.045776 | 60.2005 | -61.2625 | 60.4523 | -60.965 | -61.3998 | -61.3541 | 0.09613 | 60.2005 | -61.2671 | 60.4614 | -61.0977 | -61.2076 | -61.1984 | -0.059509 | -0.18311 | 0.068665 | 0.23804 | -0.15106 | -0.19684 | -0.091553 | -0.13733 | -0.064087 | -0.18311 | 0.07782 | 0.10529 | 0.004578 | -0.004578 | 0.068665 | 0.059509 | 0.29755 | 121.7148 | 0.16937 | 121.7285 | 121.463 | 121.4676 | 121.4035 | 121.4035 | -121.6461 | -121.6507 | 121.6553 | 121.6644 | 61.1572 | 61.2991
626.6875 | 121.9391 | -61.1893 | 60.3928 | -0.051651 | 0.002258 | 0.064969 | 0.060534 | -0.0040503 | -0.0075388 | -0.0030141 | 0.0052185 | 0.0046697 | 0.066413 | 0.053464 | -0.011961 | 0.025058 | -0.0042981 | -0.064087 | 60.1959 | -61.2442 | 60.4431 | -61.0107 | -61.4456 | -61.3953 | 0.064087 | 60.173 | -61.2488 | 60.434 | -61.1298 | -61.2213 | -61.2259 | -0.054932 | -0.19684 | 0.050354 | 0.17853 | -0.20599 | -0.25635 | -0.15106 | -0.20142 | -0.059509 | -0.21973 | 0.041199 | 0.059509 | -0.036621 | -0.032043 | 0.022888 | 0.027466 | 0.23346 | 121.6873 | 0.11902 | 121.6827 | 121.4401 | 121.4218 | 121.3852 | 121.3623 | -121.637 | -121.6415 | 121.6324 | 121.6232 | 61.1252 | 61.2534
628.375 | 121.9208 | -61.2488 | 60.3241 | -0.18898 | 0.005676 | 0.065396 | 0.063311 | -0.00063233 | -0.0083932 | -0.0034415 | -0.034454 | 0.0044561 | 0.0662 | 0.051114 | -0.014311 | 0.024417 | -0.0062207 | -0.12817 | 60.1547 | -61.2625 | 60.4523 | -60.997 | -61.4594 | -61.4182 | 0.027466 | 60.141 | -61.2991 | 60.3973 | -61.1984 | -61.3037 | -61.2808 | -0.013733 | -0.16937 | 0.12817 | 0.25177 | -0.16937 | -0.21057 | -0.15564 | -0.19684 | -0.050354 | -0.18311 | 0.073242 | 0.050354 | -0.032044 | -0.054932 | 0.01831 | -0.004578 | 0.2655 | 121.7148 | 0.10071 | 121.6965 | 121.4172 | 121.4401 | 121.4035 | 121.3898 | -121.5866 | -121.6232 | 121.7011 | 121.6461 | 61.1206 | 61.2762
630.125 | 121.9482 | -61.171 | 60.3836 | -0.1432 | 0.0054624 | 0.066678 | 0.059039 | -0.0046911 | -0.0077524 | -0.00045074 | -0.0039367 | 0.0042425 | 0.065132 | 0.0556 | -0.013029 | 0.025485 | -0.0049389 | 0.059509 | 60.2097 | -61.1938 | 60.5576 | -60.878 | -61.3083 | -61.2991 | 0.22888 | 60.2097 | -61.2076 | 60.4843 | -61.084 | -61.1893 | -61.1984 | -0.022889 | -0.17395 | 0.17395 | 0.29297 | -0.12817 | -0.13733 | -0.10528 | -0.11444 | -0.036622 | -0.17395 | 0.10071 | 0.086975 | -0.027466 | -0.018311 | 0.009156 | 0.018311 | 0.31586 | 121.7514 | 0.1236 | 121.6919 | 121.4035 | 121.4172 | 121.3806 | 121.3806 | -121.5775 | -121.5912 | 121.7285 | 121.6553 | 61.2305 | 61.3998
631.8125 | 121.8109 | -61.322 | 60.3378 | -0.097427 | 0.0069578 | 0.066678 | 0.065448 | -0.0051183 | -0.0075388 | -0.0030141 | -0.1138 | 0.0063787 | 0.0662 | 0.064358 | -0.012815 | 0.024204 | -0.0030163 | -0.18768 | 60.1639 | -61.3358 | 60.3195 | -61.1618 | -61.6104 | -61.5555 | -0.16479 | 60.1868 | -61.3449 | 60.26 | -61.3586 | -61.496 | -61.4319 | -0.013733 | -0.17395 | -0.018311 | 0.16022 | -0.23346 | -0.28839 | -0.21973 | -0.27466 | -0.022889 | -0.15106 | -0.07782 | -0.036622 | -0.10986 | -0.17395 | -0.086975 | -0.15106 | 0.17395 | 121.6553 | -0.013733 | 121.6049 | 121.4996 | 121.5317 | 121.4859 | 121.5088 | -121.6736 | -121.6827 | 121.6415 | 121.582 | 61.1343 | 61.1572
633.5625 | 121.8155 | -61.3174 | 60.3378 | -0.13557 | 0.0063168 | 0.065396 | 0.063739 | -0.00041873 | -0.006898 | -0.0015189 | -0.1199 | 0.0053107 | 0.064704 | 0.04855 | -0.012602 | 0.02634 | -0.0064343 | -0.16022 | 60.1776 | -61.3495 | 60.3149 | -61.1526 | -61.5921 | -61.5555 | -0.13733 | 60.1501 | -61.3586 | 60.26 | -61.3358 | -61.4639 | -61.4136 | -0.032043 | -0.16022 | -0.022889 | 0.1648 | -0.23804 | -0.27466 | -0.20599 | -0.24261 | -0.041199 | -0.18768 | -0.07782 | -0.01831 | -0.09613 | -0.14648 | -0.054931 | -0.10529 | 0.19684 | 121.6644 | 0.022889 | 121.6187 | 121.5271 | 121.5088 | 121.4951 | 121.4676 | -121.6873 | -121.6965 | 121.6324 | 121.5775 | 61.1572 | 61.1801
635.25 | 121.8933 | -61.235 | 60.3699 | -0.11269 | 0.0050352 | 0.066251 | 0.061602 | 0.00086307 | -0.008607 | -0.0032277 | -0.013092 | 0.0038153 | 0.065132 | 0.047909 | -0.011747 | 0.025699 | -0.0038709 | -0.11444 | 60.1639 | -61.2808 | 60.434 | -61.0336 | -61.4639 | -61.4044 | 0.018311 | 60.1685 | -61.2854 | 60.3836 | -61.1847 | -61.3037 | -61.2808 | -0.045777 | -0.20599 | 0.064087 | 0.20142 | -0.16937 | -0.22888 | -0.1236 | -0.18311 | -0.050354 | -0.20142 | 0.013733 | 0.050354 | -0.045777 | -0.068665 | 0.004577 | -0.018311 | 0.24719 | 121.7148 | 0.10071 | 121.669 | 121.4447 | 121.4539 | 121.3989 | 121.4035 | -121.6507 | -121.6553 | 121.669 | 121.6187 | 61.1206 | 61.2534
637 | 121.9116 | -61.2488 | 60.3104 | -0.074539 | 0.008453 | 0.065396 | 0.06203 | -0.0034095 | -0.007966 | -0.0015189 | -0.028351 | 0.0027471 | 0.0662 | 0.051968 | -0.014097 | 0.024204 | 0.00061529 | -0.12817 | 60.1181 | -61.2808 | 60.4385 | -61.0062 | -61.4594 | -61.4227 | 0.013733 | 60.1181 | -61.2946 | 60.3882 | -61.2076 | -61.3174 | -61.2762 | -0.032044 | -0.19226 | 0.12817 | 0.24261 | -0.17395 | -0.21057 | -0.14191 | -0.17853 | -0.045777 | -0.19226 | 0.07782 | 0.041198 | -0.027466 | -0.068665 | 0.018311 | -0.022888 | 0.27466 | 121.7194 | 0.086975 | 121.6827 | 121.3989 | 121.4127 | 121.3669 | 121.3669 | -121.5912 | -121.6049 | 121.6873 | 121.637 | 61.1206 | 61.2625
638.7656 | 121.875 | -61.2854 | 60.347 | -0.097427 | 0.0065304 | 0.066037 | 0.062884 | 0.0010767 | -0.0094614 | -0.00066434 | -0.1077 | 0.0042425 | 0.068763 | 0.056454 | -0.010893 | 0.027621 | -0.0038709 | -0.10071 | 60.1959 | -61.2808 | 60.4202 | -61.0657 | -61.5005 | -61.4731 | 0.004578 | 60.1685 | -61.3312 | 60.3378 | -61.235 | -61.377 | -61.3495 | 0.004577 | -0.15106 | 0.073242 | 0.21973 | -0.18768 | -0.21515 | -0.19226 | -0.21973 | -0.045777 | -0.17853 | -0.009155 | 0.050354 | -0.064087 | -0.091553 | -0.01831 | -0.045776 | 0.21515 | 121.701 | 0.096131 | 121.669 | 121.4767 | 121.4996 | 121.4813 | 121.4539 | -121.6278 | -121.6782 | 121.7056 | 121.6232 | 61.1847 | 61.29
640.4375 | 121.9345 | -61.2762 | 60.2783 | -0.11269 | 0.0086668 | 0.067319 | 0.064807 | 0.00064947 | -0.0071116 | -0.0019461 | -0.080231 | 0.0038153 | 0.065345 | 0.060086 | -0.013029 | 0.025485 | -0.0057935 | -0.21057 | 60.1547 | -61.3403 | 60.3424 | -61.1023 | -61.5646 | -61.5234 | -0.07782 | 60.1364 | -61.3541 | 60.3699 | -61.2076 | -61.3541 | -61.3083 | -0.064087 | -0.1236 | 0.064087 | 0.17395 | -0.24719 | -0.28839 | -0.18311 | -0.2243 | -0.07782 | -0.14191 | 0.091553 | 0.068664 | -0.032044 | -0.07782 | 0.045776 | 0 | 0.23804 | 121.6827 | 0.14648 | 121.7239 | 121.4951 | 121.4905 | 121.431 | 121.4127 | -121.6187 | -121.6324 | 121.6187 | 121.6461 | 61.0657 | 61.1984
642.1875 | 121.907 | -61.2213 | 60.3241 | -0.15846 | 0.0075986 | 0.064969 | 0.060748 | -0.00020513 | -0.0077524 | -0.00023714 | -0.046661 | 0.0036017 | 0.063423 | 0.051114 | -0.013242 | 0.024417 | -0.0030163 | -0.13733 | 60.1776 | -61.2625 | 60.4294 | -61.0016 | -61.4731 | -61.4136 | 0.036621 | 60.1318 | -61.2762 | 60.3973 | -61.1847 | -61.2808 | -61.2854 | -0.041199 | -0.14648 | 0.10528 | 0.21973 | -0.19226 | -0.25177 | -0.15106 | -0.21057 | -0.054932 | -0.19226 | 0.073242 | 0.036621 | -0.064087 | -0.05951 | -0.009155 | -0.004578 | 0.26093 | 121.6919 | 0.091553 | 121.6736 | 121.4401 | 121.4081 | 121.3989 | 121.3531 | -121.5866 | -121.6003 | 121.6507 | 121.6187 | 61.084 | 61.2579
643.875 | 121.8796 | -61.2854 | 60.3836 | -0.089798 | 0.0058896 | 0.066251 | 0.062457 | -0.0040503 | -0.0098886 | -0.0025869 | -0.092438 | 0.0042425 | 0.0662 | 0.050686 | -0.013242 | 0.026553 | -0.0055799 | -0.036621 | 60.2417 | -61.2488 | 60.3882 | -61.0886 | -61.4777 | -61.4502 | 0.004578 | 60.228 | -61.2808 | 60.347 | -61.2259 | -61.3541 | -61.3312 | 0.036621 | -0.14191 | 0.004578 | 0.19684 | -0.16479 | -0.19226 | -0.20142 | -0.22888 | 0.004577 | -0.15564 | -0.036621 | 0.059509 | -0.045777 | -0.068665 | -0.050354 | -0.073242 | 0.16022 | 121.637 | 0.054932 | 121.6278 | 121.4905 | 121.5088 | 121.5271 | 121.5134 | -121.6324 | -121.6644 | 121.6736 | 121.6324 | 61.2488 | 61.29
645.625 | 121.8338 | -61.2534 | 60.3973 | -0.05928 | 0.0046078 | 0.066678 | 0.061389 | -0.0021277 | -0.0077524 | -0.00087794 | -0.077179 | 0.0046697 | 0.065345 | 0.055813 | -0.012815 | 0.026126 | -0.0047253 | -0.036621 | 60.2554 | -61.2579 | 60.3836 | -61.0748 | -61.4914 | -61.4502 | 0.022888 | 60.2463 | -61.2671 | 60.3424 | -61.235 | -61.3586 | -61.3403 | -0.004578 | -0.14191 | -0.013733 | 0.17853 | -0.19684 | -0.23804 | -0.19226 | -0.23346 | -0.013733 | -0.15106 | -0.054932 | 0.018311 | -0.086975 | -0.10529 | -0.073242 | -0.091553 | 0.18311 | 121.6415 | 0.032044 | 121.6095 | 121.5134 | 121.5134 | 121.5088 | 121.4996 | -121.6553 | -121.6644 | 121.637 | 121.5958 | 61.2167 | 61.2762
647.3125 | 121.8887 | -61.2122 | 60.4202 | -0.089798 | 0.0037534 | 0.064542 | 0.060107 | -0.0034095 | -0.010957 | -0.0013051 | -0.034454 | 0.0040289 | 0.067481 | 0.055813 | -0.012602 | 0.025058 | -0.00088011 | 0.054932 | 60.2051 | -61.235 | 60.5164 | -60.9329 | -61.3541 | -61.3266 | 0.11444 | 60.26 | -61.2396 | 60.4065 | -61.1572 | -61.2717 | -61.2579 | -0.022888 | -0.21515 | 0.09613 | 0.27924 | -0.11444 | -0.14191 | -0.091553 | -0.11902 | -0.027466 | -0.16022 | -0.013733 | 0.054931 | -0.045777 | -0.059509 | -0.018311 | -0.032043 | 0.30212 | 121.7514 | 0.082397 | 121.6461 | 121.4401 | 121.4996 | 121.4172 | 121.4722 | -121.6553 | -121.6599 | 121.7285 | 121.6187 | 61.2671 | 61.3266
649.0625 | 121.7926 | -61.3266 | 60.3012 | -0.097427 | 0.0086668 | 0.067533 | 0.06438 | -0.0019141 | -0.008607 | -0.0025869 | -0.11075 | 0.0042425 | 0.066413 | 0.054104 | -0.01132 | 0.02634 | -0.0034435 | -0.20599 | 60.1959 | -61.3586 | 60.3104 | -61.1801 | -61.6196 | -61.5601 | -0.19226 | 60.1593 | -61.3998 | 60.2417 | -61.3678 | -61.496 | -61.4227 | -0.032044 | -0.10529 | 0.009156 | 0.14648 | -0.23346 | -0.29297 | -0.20142 | -0.26093 | -0.073242 | -0.14191 | -0.059509 | -0.041199 | -0.09613 | -0.16937 | -0.022888 | -0.096131 | 0.17853 | 121.669 | 0.032043 | 121.6415 | 121.5546 | 121.5591 | 121.5225 | 121.4859 | -121.6599 | -121.701 | 121.637 | 121.5683 | 61.1206 | 61.1343
650.8125 | 121.8018 | -61.2991 | 60.3287 | -0.11269 | 0.0058896 | 0.065824 | 0.065875 | 0.0038537 | -0.009675 | -0.0023733 | -0.09549 | 0.0044561 | 0.067909 | 0.048977 | -0.013029 | 0.027835 | -0.0040845 | -0.16022 | 60.1685 | -61.3312 | 60.3333 | -61.1389 | -61.5921 | -61.5601 | -0.13733 | 60.1593 | -61.3495 | 60.2783 | -61.3403 | -61.4731 | -61.3953 | -0.032044 | -0.16022 | 0.004578 | 0.16022 | -0.26093 | -0.29297 | -0.22888 | -0.26093 | -0.050354 | -0.16937 | -0.050354 | -0.041199 | -0.096131 | -0.17395 | -0.045777 | -0.1236 | 0.19226 | 121.6644 | 0.009155 | 121.6278 | 121.4996 | 121.5088 | 121.4676 | 121.4584 | -121.6599 | -121.6782 | 121.6324 | 121.5775 | 61.1389 | 61.1618
652.5156 | 121.9025 | -61.2305 | 60.347 | -0.15846 | 0.0069578 | 0.066037 | 0.061175 | -0.0010595 | -0.0071116 | -0.0025869 | 0.014374 | 0.0050971 | 0.065559 | 0.044919 | -0.01132 | 0.024631 | -0.0045117 | -0.082397 | 60.2097 | -61.235 | 60.4385 | -61.0199 | -61.4548 | -61.409 | 0.027466 | 60.1822 | -61.2625 | 60.3973 | -61.1801 | -61.2854 | -61.2808 | -0.004577 | -0.13733 | 0.091553 | 0.21057 | -0.17853 | -0.2243 | -0.17395 | -0.21973 | -0.032043 | -0.16479 | 0.050354 | 0.050354 | -0.050354 | -0.054931 | -0.018311 | -0.022888 | 0.21515 | 121.6736 | 0.082397 | 121.6599 | 121.4447 | 121.4447 | 121.4401 | 121.4127 | -121.582 | -121.6095 | 121.669 | 121.6278 | 61.1481 | 61.2579
654.25 | 121.962 | -61.1984 | 60.3973 | -0.028763 | 0.0041806 | 0.066037 | 0.059893 | -0.0046911 | -0.010316 | -0.0021597 | -0.0069885 | 0.0044561 | 0.065772 | 0.049405 | -0.013242 | 0.022922 | -0.0040845 | 0.045776 | 60.1959 | -61.2167 | 60.5484 | -60.8643 | -61.3129 | -61.2762 | 0.19684 | 60.228 | -61.203 | 60.466 | -61.0657 | -61.1664 | -61.1893 | -0.018311 | -0.20142 | 0.15106 | 0.33417 | -0.07782 | -0.11444 | -0.059509 | -0.09613 | -0.004578 | -0.16937 | 0.068664 | 0.13275 | 0.009155 | 0.032043 | 0.013733 | 0.036621 | 0.35248 | 121.7651 | 0.13733 | 121.669 | 121.4127 | 121.431 | 121.3943 | 121.4264 | -121.6141 | -121.6003 | 121.7468 | 121.6644 | 61.2442 | 61.3953
655.9219 | 121.8567 | -61.2579 | 60.3424 | -0.036392 | 0.0067442 | 0.065824 | 0.061602 | -0.0040503 | -0.0073252 | -0.0015189 | -0.077179 | 0.0050971 | 0.066413 | 0.057309 | -0.014097 | 0.024844 | -0.0038709 | -0.045776 | 60.2509 | -61.2762 | 60.4019 | -61.0519 | -61.4868 | -61.4594 | 0.018311 | 60.1913 | -61.3083 | 60.3653 | -61.2305 | -61.3678 | -61.3129 | -0.01831 | -0.091553 | 0.05951 | 0.20599 | -0.20142 | -0.22888 | -0.18311 | -0.21057 | -0.050354 | -0.15106 | 0.022888 | 0.027466 | -0.054931 | -0.10986 | -0.004577 | -0.059509 | 0.2243 | 121.6782 | 0.07782 | 121.6736 | 121.5271 | 121.4996 | 121.5088 | 121.4493 | -121.6187 | -121.6507 | 121.6599 | 121.6232 | 61.2122 | 61.2762
657.6562 | 121.7972 | -61.3174 | 60.3149 | -0.12794 | 0.0063168 | 0.066251 | 0.064166 | 0.0012903 | -0.007966 | -0.0032277 | -0.10464 | 0.0063787 | 0.066627 | 0.062008 | -0.012815 | 0.024631 | -0.0075025 | -0.1831 | 60.1776 | -61.322 | 60.2966 | -61.1847 | -61.615 | -61.5738 | -0.17395 | 60.1501 | -61.3449 | 60.2417 | -61.3724 | -61.5005 | -61.4319 | -0.004577 | -0.13733 | -0.01831 | 0.13275 | -0.25635 | -0.29755 | -0.25177 | -0.29297 | -0.027466 | -0.16479 | -0.073242 | -0.054931 | -0.11444 | -0.1831 | -0.086975 | -0.15564 | 0.13733 | 121.6187 | -0.027465 | 121.5866 | 121.4996 | 121.4951 | 121.4951 | 121.4676 | -121.637 | -121.6599 | 121.6141 | 121.5591 | 61.1343 | 61.1435
659.3438 | 121.8933 | -61.2442 | 60.3745 | -0.12032 | 0.0046078 | 0.064115 | 0.060534 | 0.00043587 | -0.0073252 | -0.0036551 | -0.0039367 | 0.0059515 | 0.066841 | 0.055386 | -0.014097 | 0.023563 | -0.0036573 | -0.091553 | 60.1685 | -61.2488 | 60.4248 | -61.0062 | -61.4456 | -61.4044 | 0.018311 | 60.1639 | -61.2762 | 60.3836 | -61.1847 | -61.3083 | -61.2808 | -0.004577 | -0.20599 | 0.050354 | 0.23804 | -0.16022 | -0.20142 | -0.15564 | -0.19684 | -0.032043 | -0.21057 | 0.009155 | 0.05951 | -0.036621 | -0.064087 | -0.004578 | -0.032044 | 0.24261 | 121.6736 | 0.091553 | 121.6599 | 121.4172 | 121.4401 | 121.4127 | 121.4081 | -121.6232 | -121.6507 | 121.669 | 121.6278 | 61.1526 | 61.2625
661.0781 | 121.9162 | -61.2488 | 60.3745 | -0.15846 | 0.0067442 | 0.064969 | 0.061602 | -0.00063233 | -0.010316 | -0.0010915 | -0.013092 | 0.0042425 | 0.064704 | 0.052395 | -0.013883 | 0.024631 | -0.0047253 | -0.10986 | 60.1547 | -61.2625 | 60.4294 | -61.0153 | -61.4685 | -61.4044 | 0.032043 | 60.1639 | -61.2762 | 60.3928 | -61.1893 | -61.3037 | -61.2808 | -0.013733 | -0.21973 | 0.054931 | 0.23346 | -0.15564 | -0.21973 | -0.14191 | -0.20599 | -0.027466 | -0.21057 | 0.01831 | 0.059509 | -0.032044 | -0.054932 | -0.004578 | -0.027466 | 0.24719 | 121.6919 | 0.086975 | 121.669 | 121.4172 | 121.4401 | 121.4035 | 121.4127 | -121.637 | -121.6507 | 121.6782 | 121.6415 | 61.1389 | 61.2808
662.8438 | 121.8246 | -61.3358 | 60.3058 | -0.05928 | 0.009094 | 0.066037 | 0.066302 | 0.0027857 | -0.0094614 | -0.0032277 | -0.1138 | 0.0059515 | 0.066841 | 0.050686 | -0.014311 | 0.025485 | -0.0057935 | -0.11444 | 60.1959 | -61.3083 | 60.3699 | -61.1023 | -61.5509 | -61.5143 | -0.068665 | 60.1639 | -61.3495 | 60.2783 | -61.3312 | -61.4639 | -61.4136 | 0.027465 | -0.10986 | 0.064087 | 0.23346 | -0.17853 | -0.21515 | -0.20599 | -0.24261 | -0.013733 | -0.14191 | -0.027466 | 0.004577 | -0.07782 | -0.12817 | -0.064087 | -0.11444 | 0.20599 | 121.6782 | 0.01831 | 121.6278 | 121.5042 | 121.5134 | 121.5317 | 121.4996 | -121.6141 | -121.6553 | 121.7056 | 121.6141 | 61.2213 | 61.2671
664.5156 | 121.962 | -61.2122 | 60.4019 | -0.11269 | 0.0043942 | 0.066251 | 0.05968 | -0.0034095 | -0.009675 | -0.0040823 | 0.0052185 | 0.0048833 | 0.06919 | 0.054959 | -0.012815 | 0.025485 | -0.0049389 | 0.013733 | 60.228 | -61.203 | 60.5118 | -60.9283 | -61.3541 | -61.3083 | 0.20142 | 60.1959 | -61.2442 | 60.4889 | -61.084 | -61.1893 | -61.1938 | 0.009155 | -0.17395 | 0.10986 | 0.28381 | -0.096131 | -0.14191 | -0.10529 | -0.15106 | -0.032044 | -0.20599 | 0.086975 | 0.12817 | 0.01831 | 0.022888 | 0.050354 | 0.054932 | 0.27466 | 121.7148 | 0.16022 | 121.7331 | 121.431 | 121.4401 | 121.4401 | 121.4081 | -121.6049 | -121.6461 | 121.7239 | 121.7011 | 61.2259 | 61.4136
666.25 | 121.8842 | -61.203 | 60.4019 | -0.074539 | 0.0050352 | 0.063047 | 0.061602 | 0.0015039 | -0.0081796 | -0.0017325 | 0.0021667 | 0.0036017 | 0.065132 | 0.055386 | -0.012815 | 0.025058 | -0.0062207 | 0.045776 | 60.1959 | -61.2122 | 60.5072 | -60.9375 | -61.3586 | -61.3129 | 0.17853 | 60.2234 | -61.2076 | 60.4111 | -61.1435 | -61.2442 | -61.2579 | -0.009155 | -0.20599 | 0.10529 | 0.2655 | -0.10986 | -0.15564 | -0.10071 | -0.14648 | -0.004578 | -0.17853 | 0.009155 | 0.059509 | -0.054932 | -0.041199 | -0.050354 | -0.036621 | 0.27466 | 121.7194 | 0.064087 | 121.6187 | 121.4081 | 121.431 | 121.3989 | 121.4264 | -121.6141 | -121.6095 | 121.7102 | 121.6141 | 61.2488 | 61.3815
667.9375 | 121.8384 | -61.235 | 60.3928 | -0.036392 | 0.0024716 | 0.061551 | 0.061602 | -0.0038367 | -0.011811 | -0.0032277 | -0.06192 | 0.0044561 | 0.0662 | 0.051327 | -0.013029 | 0.024204 | -0.0075025 | -0.032043 | 60.2692 | -61.2488 | 60.379 | -61.0703 | -61.4822 | -61.4594 | 0.013733 | 60.2463 | -61.2808 | 60.3424 | -61.2396 | -61.3678 | -61.3312 | -0.013733 | -0.1236 | -0.013733 | 0.16479 | -0.22431 | -0.24719 | -0.21057 | -0.23346 | -0.045777 | -0.14648 | -0.050354 | -0.004578 | -0.096131 | -0.13275 | -0.050354 | -0.086975 | 0.17853 | 121.6278 | 0.041199 | 121.6232 | 121.5179 | 121.5271 | 121.5042 | 121.4813 | -121.6415 | -121.6736 | 121.6141 | 121.5775 | 61.203 | 61.2488
669.6719 | 121.8704 | -61.2625 | 60.3607 | -0.06691 | 0.0063168 | 0.066037 | 0.06438 | -0.0059729 | -0.008607 | -2.3544e-05 | -0.077179 | 0.0053107 | 0.067268 | 0.05325 | -0.012388 | 0.025485 | -0.0032299 | -0.064087 | 60.2188 | -61.2808 | 60.4065 | -61.0565 | -61.4914 | -61.4548 | 0.022888 | 60.1959 | -61.3037 | 60.3607 | -61.2259 | -61.3632 | -61.322 | -0.018311 | -0.14191 | 0.045776 | 0.20599 | -0.19226 | -0.22888 | -0.17395 | -0.21057 | -0.041199 | -0.16479 | 0 | 0.036621 | -0.059509 | -0.10071 | -0.01831 | -0.059509 | 0.2243 | 121.6873 | 0.07782 | 121.6644 | 121.4996 | 121.4996 | 121.4813 | 121.4584 | -121.6415 | -121.6644 | 121.669 | 121.6232 | 61.1984 | 61.2854
671.3438 | 121.9482 | -61.2671 | 60.2737 | -0.12032 | 0.0069578 | 0.066464 | 0.063098 | 0.0023585 | -0.0077524 | -0.0040823 | -0.049713 | 0.0029607 | 0.066627 | 0.051327 | -0.012602 | 0.023135 | -0.0034435 | -0.13275 | 60.1456 | -61.29 | 60.4202 | -61.0245 | -61.4914 | -61.441 | -0.004578 | 60.1044 | -61.3083 | 60.3745 | -61.2076 | -61.322 | -61.2808 | -0.022888 | -0.12817 | 0.14648 | 0.24262 | -0.17395 | -0.2243 | -0.15106 | -0.20142 | -0.041199 | -0.16937 | 0.10071 | 0.059509 | -0.013733 | -0.054931 | 0.027466 | -0.013732 | 0.2655 | 121.7102 | 0.10071 | 121.6827 | 121.4355 | 121.4127 | 121.4127 | 121.3715 | -121.5637 | -121.582 | 121.6873 | 121.6415 | 61.1343 | 61.2625
673.0938 | 121.9528 | -61.2717 | 60.26 | -0.12032 | 0.005676 | 0.065396 | 0.061389 | 0.00043587 | -0.0075388 | -0.0032277 | -0.09549 | 0.0033881 | 0.066627 | 0.0509 | -0.012174 | 0.024631 | -0.0030163 | -0.1831 | 60.141 | -61.2946 | 60.4065 | -61.0519 | -61.5189 | -61.4777 | -0.018311 | 60.1227 | -61.3174 | 60.3882 | -61.2076 | -61.3403 | -61.29 | -0.022889 | -0.11902 | 0.14648 | 0.21973 | -0.20599 | -0.24719 | -0.1831 | -0.2243 | -0.045777 | -0.13733 | 0.12817 | 0.064086 | -0.018311 | -0.068665 | 0.027466 | -0.022888 | 0.24262 | 121.7011 | 0.10986 | 121.7056 | 121.4355 | 121.4401 | 121.4127 | 121.3943 | -121.5546 | -121.5775 | 121.6782 | 121.6599 | 61.0886 | 61.2534
674.7812 | 121.8521 | -61.2625 | 60.3333 | -0.06691 | 0.0054624 | 0.066037 | 0.063952 | 0.00086307 | -0.0064706 | -0.0028005 | -0.092438 | 0.0053107 | 0.065132 | 0.05859 | -0.01367 | 0.026981 | -0.0025891 | -0.07782 | 60.1868 | -61.3266 | 60.3882 | -61.0474 | -61.496 | -61.4685 | -0.009155 | 60.1639 | -61.3083 | 60.3607 | -61.2442 | -61.3815 | -61.3312 | -0.064087 | -0.14648 | 0.054932 | 0.21515 | -0.20599 | -0.23346 | -0.14191 | -0.16937 | -0.045777 | -0.16937 | 0.027466 | 0.01831 | -0.068665 | -0.11902 | -0.022888 | -0.073242 | 0.27924 | 121.7148 | 0.064087 | 121.669 | 121.5134 | 121.4722 | 121.4493 | 121.4264 | -121.6599 | -121.6415 | 121.6507 | 121.6232 | 61.1847 | 61.2534
676.5312 | 121.9437 | -61.2808 | 60.2829 | -0.18135 | 0.0075986 | 0.068387 | 0.061816 | 8.47e-06 | -0.0071116 | -0.0038687 | -0.040558 | 0.0046697 | 0.064277 | 0.053891 | -0.013242 | 0.025912 | -0.0049389 | -0.13733 | 60.1364 | -61.3174 | 60.4156 | -61.0245 | -61.4777 | -61.441 | -0.004578 | 60.0861 | -61.3129 | 60.3973 | -61.1847 | -61.3129 | -61.2671 | -0.036621 | -0.14648 | 0.13275 | 0.25635 | -0.16022 | -0.19684 | -0.1236 | -0.16022 | -0.032043 | -0.19684 | 0.11444 | 0.096131 | 0.013733 | -0.032043 | 0.045776 | 0 | 0.29297 | 121.7331 | 0.12817 | 121.7102 | 121.4539 | 121.3989 | 121.4172 | 121.3669 | -121.6003 | -121.5958 | 121.6965 | 121.6782 | 61.1435 | 61.2762
678.2812 | 121.9437 | -61.2534 | 60.3058 | -0.15846 | 0.007385 | 0.065183 | 0.061602 | 0.0015039 | -0.0077524 | -0.0034415 | -0.028351 | 0.0044561 | 0.064704 | 0.0556 | -0.010893 | 0.024417 | -0.0023755 | -0.12817 | 60.1364 | -61.2808 | 60.4385 | -60.9924 | -61.4548 | -61.409 | 0.036621 | 60.1181 | -61.2991 | 60.3928 | -61.1893 | -61.2991 | -61.2762 | -0.027466 | -0.16937 | 0.13275 | 0.26093 | -0.15564 | -0.20142 | -0.12817 | -0.17395 | -0.045776 | -0.18768 | 0.086975 | 0.064087 | -0.022888 | -0.045776 | 0.022888 | 0 | 0.28839 | 121.7194 | 0.10986 | 121.6919 | 121.4172 | 121.4172 | 121.3898 | 121.3715 | -121.5866 | -121.6049 | 121.6919 | 121.6461 | 61.1252 | 61.29
680.0312 | 121.8521 | -61.2213 | 60.4431 | -0.051651 | 0.0048214 | 0.064542 | 0.061389 | -0.0014867 | -0.011598 | -0.00066434 | -0.025299 | 0.0050971 | 0.065559 | 0.056881 | -0.011533 | 0.024417 | -0.0047253 | 0.064087 | 60.2417 | -61.2442 | 60.4752 | -60.9558 | -61.3953 | -61.3632 | 0.13733 | 60.2188 | -61.2305 | 60.3882 | -61.1984 | -61.2946 | -61.2946 | -0.022889 | -0.20142 | 0.032044 | 0.2655 | -0.14191 | -0.17395 | -0.11902 | -0.15106 | -0.009156 | -0.2243 | -0.054931 | 0.022888 | -0.073243 | -0.073243 | -0.064087 | -0.064087 | 0.28839 | 121.7194 | 0.032044 | 121.6187 | 121.4859 | 121.4493 | 121.463 | 121.4401 | -121.6873 | -121.6736 | 121.6965 | 121.6095 | 61.2854 | 61.3586
681.7188 | 121.8155 | -61.3266 | 60.3195 | -0.1432 | 0.0082394 | 0.065183 | 0.06203 | -0.0051183 | -0.0098886 | -0.0030141 | -0.1077 | 0.0055243 | 0.065559 | 0.058163 | -0.013242 | 0.025485 | -0.0025891 | -0.1236 | 60.2005 | -61.2991 | 60.3653 | -61.0977 | -61.5601 | -61.5143 | -0.073242 | 60.1822 | -61.3312 | 60.2692 | -61.3266 | -61.4639 | -61.3998 | 0.027466 | -0.11902 | 0.045776 | 0.22888 | -0.18768 | -0.23346 | -0.21515 | -0.26093 | -0.004578 | -0.13733 | -0.050354 | 0 | -0.073242 | -0.13733 | -0.068664 | -0.13275 | 0.20142 | 121.6644 | 0.004578 | 121.6003 | 121.4996 | 121.5134 | 121.5271 | 121.5088 | -121.6187 | -121.6507 | 121.6919 | 121.5958 | 61.203 | 61.2534
683.4688 | 121.8338 | -61.3129 | 60.3012 | -0.12032 | 0.0067442 | 0.066678 | 0.060962 | -0.00063233 | -0.008607 | -0.0010915 | -0.11075 | 0.0065923 | 0.066841 | 0.055813 | -0.010893 | 0.025485 | -0.0066479 | -0.21973 | 60.1868 | -61.3586 | 60.2646 | -61.2167 | -61.615 | -61.5738 | -0.17853 | 60.1456 | -61.3586 | 60.2692 | -61.3495 | -61.4914 | -61.4227 | -0.045777 | -0.11444 | -0.036621 | 0.09613 | -0.26093 | -0.30212 | -0.21515 | -0.25635 | -0.045777 | -0.15564 | -0.032043 | -0.036621 | -0.10986 | -0.17853 | -0.064086 | -0.13275 | 0.14191 | 121.6232 | 0.009156 | 121.6278 | 121.5454 | 121.5042 | 121.4996 | 121.4584 | -121.6599 | -121.6599 | 121.5775 | 121.582 | 61.0931 | 61.1343
685.2344 | 121.8246 | -61.2488 | 60.4202 | -0.12794 | 0.0054624 | 0.065824 | 0.060962 | -0.0064001 | -0.007966 | -0.00023714 | -0.049713 | 0.0044561 | 0.065986 | 0.047482 | -0.010465 | 0.025058 | -0.0049389 | -0.036621 | 60.26 | -61.2579 | 60.4019 | -61.0611 | -61.4594 | -61.4319 | 0.032043 | 60.2371 | -61.2579 | 60.3378 | -61.2305 | -61.3541 | -61.3266 | -0.009156 | -0.16022 | -0.01831 | 0.18768 | -0.18311 | -0.21057 | -0.17395 | -0.20142 | -0.009156 | -0.1831 | -0.082397 | 0.01831 | -0.07782 | -0.10529 | -0.068664 | -0.09613 | 0.19684 | 121.6599 | 0.027466 | 121.5958 | 121.5179 | 121.4951 | 121.5088 | 121.4859 | -121.6782 | -121.6782 | 121.6507 | 121.5866 | 61.2122 | 61.2808
686.9844 | 121.9345 | -61.2854 | 60.3058 | -0.12032 | 0.0082394 | 0.065183 | 0.063311 | 0.0021447 | -0.0083932 | 0.00083106 | -0.031403 | 0.0046697 | 0.064918 | 0.056241 | -0.013883 | 0.025485 | -0.0070751 | -0.21057 | 60.1868 | -61.3541 | 60.3561 | -61.0931 | -61.5509 | -61.5005 | -0.073242 | 60.0998 | -61.3449 | 60.3653 | -61.2259 | -61.3403 | -61.2991 | -0.068665 | -0.11902 | 0.050354 | 0.19226 | -0.21515 | -0.2655 | -0.14648 | -0.19684 | -0.05951 | -0.20599 | 0.059509 | 0.059509 | -0.013733 | -0.054932 | 0.045777 | 0.004578 | 0.26093 | 121.7102 | 0.11902 | 121.7102 | 121.5408 | 121.4447 | 121.4722 | 121.3852 | -121.6599 | -121.6507 | 121.6415 | 121.6507 | 61.0748 | 61.2122
688.6719 | 121.8246 | -61.3174 | 60.3241 | -0.10506 | 0.0099484 | 0.066251 | 0.065234 | 0.0034265 | -0.0073252 | -0.0028005 | -0.089386 | 0.0048833 | 0.066627 | 0.05859 | -0.012388 | 0.023349 | -0.0013073 | -0.10986 | 60.2051 | -61.3174 | 60.3836 | -61.0794 | -61.528 | -61.4914 | -0.045776 | 60.1776 | -61.3449 | 60.2829 | -61.3174 | -61.4456 | -61.3907 | 0 | -0.11902 | 0.059509 | 0.23804 | -0.17395 | -0.21057 | -0.17395 | -0.21057 | -0.027466 | -0.14648 | -0.041199 | 0 | -0.073242 | -0.12817 | -0.045776 | -0.10071 | 0.23804 | 121.7011 | 0.027466 | 121.6278 | 121.5225 | 121.5225 | 121.5225 | 121.4951 | -121.6415 | -121.669 | 121.7011 | 121.6003 | 61.2076 | 61.2717
690.4062 | 121.875 | -61.2717 | 60.3287 | -0.10506 | 0.0050352 | 0.065183 | 0.063098 | 0.00064947 | -0.0090342 | -0.0017325 | -0.064972 | 0.0057379 | 0.066841 | 0.057309 | -0.013456 | 0.025485 | -0.0053661 | -0.086975 | 60.1959 | -61.3174 | 60.4065 | -61.0245 | -61.496 | -61.4594 | 0 | 60.1868 | -61.322 | 60.3424 | -61.2442 | -61.3541 | -61.322 | -0.045777 | -0.13275 | 0.07782 | 0.24719 | -0.18768 | -0.22431 | -0.14191 | -0.17853 | -0.050354 | -0.14191 | 0.013733 | 0.027465 | -0.050354 | -0.082398 | 0 | -0.032044 | 0.29297 | 121.7239 | 0.077819 | 121.6644 | 121.5134 | 121.5088 | 121.4676 | 121.4584 | -121.6461 | -121.6507 | 121.6782 | 121.6141 | 61.1847 | 61.2717
692.1562 | 121.8567 | -61.3312 | 60.2966 | -0.10506 | 0.0065304 | 0.066678 | 0.061175 | -0.0023413 | -0.006898 | -0.0021597 | -0.080231 | 0.0063787 | 0.065986 | 0.0556 | -0.014097 | 0.024631 | -0.0023755 | -0.2243 | 60.2005 | -61.322 | 60.3104 | -61.1481 | -61.5784 | -61.5417 | -0.13275 | 60.1456 | -61.3724 | 60.2966 | -61.3174 | -61.4502 | -61.3724 | 0.009156 | -0.096131 | 0.013733 | 0.18311 | -0.21057 | -0.24719 | -0.21973 | -0.25635 | -0.041198 | -0.15106 | 0 | 0.013733 | -0.041198 | -0.11902 | 0 | -0.07782 | 0.17395 | 121.6324 | 0.054931 | 121.669 | 121.5225 | 121.5179 | 121.5317 | 121.4767 | -121.6187 | -121.669 | 121.6415 | 121.6278 | 61.1069 | 61.1984
693.8438 | 121.7972 | -61.3129 | 60.3195 | -0.097427 | 0.007385 | 0.066678 | 0.065875 | -0.0010595 | -0.007966 | 0.00040366 | -0.071076 | 0.0044561 | 0.065772 | 0.049191 | -0.013242 | 0.025272 | -0.0036573 | -0.19684 | 60.1776 | -61.3449 | 60.3104 | -61.1755 | -61.5967 | -61.5555 | -0.15564 | 60.1776 | -61.3495 | 60.2554 | -61.3495 | -61.4822 | -61.4182 | -0.032044 | -0.14191 | -0.009155 | 0.13733 | -0.24262 | -0.28381 | -0.21057 | -0.25177 | -0.036621 | -0.14191 | -0.064087 | -0.036621 | -0.10529 | -0.16937 | -0.068665 | -0.13275 | 0.16937 | 121.6553 | 0 | 121.6049 | 121.5225 | 121.5271 | 121.4905 | 121.4905 | -121.6644 | -121.669 | 121.6232 | 121.5683 | 61.116 | 61.1572
695.5781 | 121.8109 | -61.2213 | 60.4202 | -0.089798 | 0.0054624 | 0.061978 | 0.059466 | 0.0025721 | -0.0090342 | -0.0057913 | -0.028351 | 0.0025335 | 0.068336 | 0.055173 | -0.011533 | 0.025485 | -0.0055799 | -0.050354 | 60.2463 | -61.2396 | 60.3928 | -61.0474 | -61.4639 | -61.4365 | 0.041199 | 60.2463 | -61.2442 | 60.3378 | -61.2213 | -61.3358 | -61.322 | -0.018311 | -0.17395 | -0.027466 | 0.17395 | -0.21515 | -0.24262 | -0.19684 | -0.2243 | -0.022889 | -0.17395 | -0.082397 | 0 | -0.10071 | -0.11444 | -0.077819 | -0.091552 | 0.19226 | 121.6324 | 0.022889 | 121.582 | 121.4859 | 121.4905 | 121.4676 | 121.4676 | -121.6599 | -121.6644 | 121.6141 | 121.5591 | 61.171 | 61.2625
697.3125 | 121.875 | -61.203 | 60.4202 | -0.06691 | 0.0050352 | 0.065183 | 0.05733 | 0.00086307 | -0.009675 | -0.0028005 | 0.014374 | 0.0036017 | 0.0662 | 0.047268 | -0.012815 | 0.024204 | -0.0062207 | 0.036621 | 60.2188 | -61.2259 | 60.498 | -60.9375 | -61.3586 | -61.3083 | 0.16022 | 60.2371 | -61.2259 | 60.4111 | -61.1435 | -61.2579 | -61.2488 | -0.022888 | -0.20142 | 0.07782 | 0.2655 | -0.10529 | -0.15564 | -0.082398 | -0.13275 | -0.022888 | -0.1831 | -0.009155 | 0.059509 | -0.045776 | -0.054932 | -0.022888 | -0.032044 | 0.28839 | 121.7239 | 0.082397 | 121.637 | 121.4447 | 121.463 | 121.4218 | 121.4401 | -121.6461 | -121.6461 | 121.7011 | 121.6141 | 61.2396 | 61.3632
699.0781 | 121.9574 | -61.1755 | 60.3973 | -0.10506 | 0.0037534 | 0.064328 | 0.05968 | -0.0066137 | -0.012025 | -0.0034415 | 0.035736 | 0.0036017 | 0.065559 | 0.053036 | -0.011533 | 0.026126 | -0.0019483 | 0.027466 | 60.2051 | -61.2076 | 60.5255 | -60.9238 | -61.3403 | -61.3037 | 0.18768 | 60.2005 | -61.2579 | 60.4843 | -61.0657 | -61.1847 | -61.171 | -0.032044 | -0.19226 | 0.12817 | 0.25177 | -0.12817 | -0.16479 | -0.09613 | -0.13275 | -0.082398 | -0.19684 | 0.086975 | 0.10986 | 0.004578 | -0.009155 | 0.086976 | 0.073243 | 0.28381 | 121.7331 | 0.19226 | 121.7422 | 121.4127 | 121.4584 | 121.3806 | 121.376 | -121.6049 | -121.6553 | 121.701 | 121.6599 | 61.203 | 61.3632
700.7656 | 121.8063 | -61.3083 | 60.3287 | -0.10506 | 0.0046078 | 0.06561 | 0.061602 | 0.0012903 | -0.008607 | -0.00087794 | -0.10159 | 0.0040289 | 0.064918 | 0.059872 | -0.013242 | 0.026126 | -0.0042981 | -0.15106 | 60.173 | -61.3449 | 60.3241 | -61.1389 | -61.6104 | -61.5509 | -0.13733 | 60.1776 | -61.3541 | 60.2646 | -61.3449 | -61.4685 | -61.409 | -0.036621 | -0.15564 | -0.004577 | 0.16937 | -0.24261 | -0.30212 | -0.20599 | -0.2655 | -0.045776 | -0.15106 | -0.064087 | -0.036621 | -0.10071 | -0.16022 | -0.054932 | -0.11444 | 0.20599 | 121.669 | 0.009155 | 121.6187 | 121.5179 | 121.5317 | 121.4813 | 121.4859 | -121.6736 | -121.6827 | 121.6324 | 121.5729 | 61.1572 | 61.171
702.5 | 121.9528 | -61.2717 | 60.2966 | -0.17372 | 0.0099484 | 0.066892 | 0.06203 | -0.0017005 | -0.0083932 | -0.0047231 | -0.01004 | 0.0046697 | 0.066841 | 0.058163 | -0.013883 | 0.023776 | -0.0030163 | -0.14191 | 60.1227 | -61.2946 | 60.434 | -61.0153 | -61.4822 | -61.409 | -0.004578 | 60.1089 | -61.3174 | 60.3928 | -61.1938 | -61.2991 | -61.2808 | -0.022889 | -0.17395 | 0.13733 | 0.25635 | -0.13733 | -0.21057 | -0.11444 | -0.18768 | -0.045777 | -0.18768 | 0.09613 | 0.077819 | -0.009156 | -0.027466 | 0.036621 | 0.018311 | 0.27924 | 121.7285 | 0.1236 | 121.7102 | 121.4172 | 121.4264 | 121.3943 | 121.3806 | -121.5912 | -121.6141 | 121.7056 | 121.6644 | 61.1298 | 61.2671
704.25 | 121.9666 | -61.2991 | 60.2875 | -0.1432 | 0.007385 | 0.067746 | 0.062457 | -0.0019141 | -0.009675 | -0.0019461 | -0.022247 | 0.0033881 | 0.066627 | 0.051541 | -0.014951 | 0.026553 | -0.00045291 | -0.16022 | 60.1318 | -61.29 | 60.4294 | -61.0245 | -61.4822 | -61.4227 | -0.004578 | 60.1181 | -61.3083 | 60.3973 | -61.1938 | -61.3358 | -61.2762 | 0.009155 | -0.15564 | 0.14191 | 0.27466 | -0.1236 | -0.18311 | -0.13275 | -0.19226 | -0.009156 | -0.16937 | 0.10986 | 0.10528 | 0.022888 | -0.036621 | 0.032044 | -0.027465 | 0.2655 | 121.7194 | 0.11444 | 121.7056 | 121.4218 | 121.4264 | 121.431 | 121.4172 | -121.5775 | -121.5958 | 121.7285 | 121.6965 | 61.1389 | 61.2946
705.9219 | 121.8933 | -61.1664 | 60.4065 | -0.089798 | 0.0050352 | 0.066678 | 0.05968 | -0.0010595 | -0.0081796 | -0.0021597 | -0.01004 | 0.0046697 | 0.0662 | 0.047696 | -0.012602 | 0.025912 | -0.0085705 | 0.045776 | 60.2097 | -61.2305 | 60.5164 | -60.9375 | -61.3495 | -61.3129 | 0.15564 | 60.2188 | -61.2213 | 60.4202 | -61.1526 | -61.2717 | -61.2534 | -0.064087 | -0.19684 | 0.10986 | 0.22888 | -0.14648 | -0.18311 | -0.082397 | -0.11902 | -0.054931 | -0.18768 | 0.013733 | 0.013733 | -0.086975 | -0.10529 | -0.032044 | -0.050354 | 0.29297 | 121.7468 | 0.068664 | 121.6415 | 121.4401 | 121.4401 | 121.376 | 121.3852 | -121.637 | -121.6278 | 121.6827 | 121.5866 | 61.2122 | 61.322
707.6719 | 121.962 | -61.1847 | 60.3882 | -0.11269 | 0.0058896 | 0.064542 | 0.058612 | -0.0034095 | -0.0088206 | -0.0036551 | 0.017425 | 0.0029607 | 0.065132 | 0.051114 | -0.013242 | 0.026553 | -0.0047253 | 0.018311 | 60.2325 | -61.2305 | 60.5026 | -60.9192 | -61.3403 | -61.2991 | 0.1831 | 60.2005 | -61.2305 | 60.466 | -61.0703 | -61.1938 | -61.1984 | -0.045777 | -0.15564 | 0.11444 | 0.2655 | -0.11444 | -0.15564 | -0.068664 | -0.10986 | -0.045777 | -0.18768 | 0.077819 | 0.11444 | -0.013733 | -0.009156 | 0.032044 | 0.036621 | 0.31128 | 121.7331 | 0.16022 | 121.6965 | 121.463 | 121.431 | 121.4172 | 121.3852 | -121.6187 | -121.6187 | 121.6873 | 121.6507 | 61.203 | 61.3678
709.4219 | 121.843 | -61.235 | 60.3973 | -0.11269 | 0.0048214 | 0.064542 | 0.060962 | -0.0031957 | -0.0090342 | -0.0025869 | -0.074127 | 0.0050971 | 0.067268 | 0.052182 | -0.014311 | 0.025485 | -0.0032299 | -0.032043 | 60.2509 | -61.2488 | 60.3745 | -61.084 | -61.5005 | -61.4502 | -0.009155 | 60.2417 | -61.2579 | 60.3378 | -61.2213 | -61.3541 | -61.3083 | -0.013733 | -0.14649 | -0.022888 | 0.15106 | -0.21515 | -0.2655 | -0.20142 | -0.25177 | -0.022889 | -0.15564 | -0.059509 | 0.013733 | -0.073243 | -0.11902 | -0.050354 | -0.09613 | 0.16479 | 121.6232 | 0.036622 | 121.5958 | 121.4996 | 121.4996 | 121.4859 | 121.4767 | -121.6461 | -121.6553 | 121.6095 | 121.5729 | 61.203 | 61.2259
711.1719 | 121.8796 | -61.2625 | 60.347 | -0.089798 | 0.0054624 | 0.064756 | 0.06203 | 0.00064947 | -0.0098886 | -0.0017325 | -0.10159 | 0.0061651 | 0.065559 | 0.055386 | -0.014311 | 0.027621 | -0.0060071 | -0.068665 | 60.2234 | -61.2808 | 60.3973 | -61.0474 | -61.5097 | -61.4594 | 0.018311 | 60.1913 | -61.3083 | 60.3607 | -61.2442 | -61.3861 | -61.3266 | -0.018311 | -0.1236 | 0.050354 | 0.21515 | -0.19684 | -0.24719 | -0.17853 | -0.22888 | -0.045777 | -0.15564 | 0.013733 | 0.01831 | -0.064087 | -0.1236 | -0.01831 | -0.077819 | 0.23346 | 121.6782 | 0.064087 | 121.669 | 121.5042 | 121.4996 | 121.4859 | 121.4539 | -121.6278 | -121.6553 | 121.6599 | 121.6232 | 61.1938 | 61.2808
712.8594 | 121.8292 | -61.2396 | 60.4294 | -0.028763 | 0.0052488 | 0.062619 | 0.05968 | -0.00063233 | -0.0088206 | -0.0015189 | -0.034454 | 0.0057379 | 0.064277 | 0.052395 | -0.012815 | 0.023563 | -0.0034435 | -0.041199 | 60.2737 | -61.2717 | 60.3928 | -61.0519 | -61.4594 | -61.4227 | 0.064087 | 60.26 | -61.2534 | 60.3333 | -61.2305 | -61.3403 | -61.3312 | -0.032043 | -0.15564 | -0.036621 | 0.18768 | -0.1831 | -0.21973 | -0.15106 | -0.18768 | -0.013733 | -0.16937 | -0.09613 | 0.009155 | -0.091553 | -0.10071 | -0.07782 | -0.086975 | 0.21973 | 121.6644 | 0.022888 | 121.5866 | 121.5454 | 121.5134 | 121.5134 | 121.4996 | -121.701 | -121.6827 | 121.6324 | 121.5729 | 61.1984 | 61.3037
714.6094 | 121.9437 | -61.235 | 60.2966 | -0.18898 | 0.0071714 | 0.066251 | 0.06203 | -0.0021277 | -0.0075388 | -0.0019461 | -0.049713 | 0.0040289 | 0.06385 | 0.053677 | -0.012388 | 0.02399 | -0.0030163 | -0.14191 | 60.1364 | -61.3174 | 60.434 | -61.0107 | -61.4868 | -61.4273 | 0.009155 | 60.0906 | -61.2946 | 60.3928 | -61.1801 | -61.3037 | -61.2762 | -0.082398 | -0.16022 | 0.13733 | 0.2243 | -0.19226 | -0.25177 | -0.10986 | -0.16937 | -0.05951 | -0.20599 | 0.09613 | 0.054931 | -0.041199 | -0.068665 | 0.018311 | -0.009155 | 0.3067 | 121.7514 | 0.11444 | 121.6873 | 121.4539 | 121.3852 | 121.3715 | 121.3257 | -121.6141 | -121.5912 | 121.669 | 121.6278 | 61.0931 | 61.2442
716.3594 | 121.8246 | -61.2167 | 60.4156 | -0.10506 | 0.0046078 | 0.066037 | 0.06203 | -0.0029821 | -0.0098886 | -2.3544e-05 | -0.034454 | 0.0046697 | 0.065986 | 0.0509 | -0.011747 | 0.025485 | -0.0047253 | -0.027466 | 60.2417 | -61.2488 | 60.4111 | -61.0382 | -61.4731 | -61.4319 | 0.045776 | 60.2692 | -61.2625 | 60.3333 | -61.2122 | -61.3358 | -61.322 | -0.032043 | -0.17395 | -0.004577 | 0.17853 | -0.21515 | -0.25635 | -0.18311 | -0.2243 | -0.045776 | -0.14648 | -0.082397 | 0.004578 | -0.10529 | -0.11902 | -0.059509 | -0.073242 | 0.21057 | 121.6599 | 0.050354 | 121.5958 | 121.4905 | 121.5317 | 121.4584 | 121.4859 | -121.6644 | -121.6782 | 121.6278 | 121.55 | 61.1893 | 61.2625
718.0938 | 121.8018 | -61.3358 | 60.3012 | -0.13557 | 0.0075986 | 0.066892 | 0.062457 | -0.0017005 | -0.0083932 | -0.0032277 | -0.10159 | 0.0046697 | 0.067268 | 0.051968 | -0.012602 | 0.028262 | -0.0025891 | -0.20599 | 60.1868 | -61.3495 | 60.3012 | -61.1847 | -61.6058 | -61.5509 | -0.17395 | 60.1639 | -61.377 | 60.2509 | -61.377 | -61.5143 | -61.4365 | -0.013733 | -0.11444 | 0 | 0.15106 | -0.21515 | -0.27008 | -0.20142 | -0.25635 | -0.041199 | -0.13733 | -0.050354 | -0.041199 | -0.10071 | -0.17853 | -0.059509 | -0.13733 | 0.1648 | 121.6507 | 0 | 121.6278 | 121.5363 | 121.5408 | 121.5225 | 121.4996 | -121.6507 | -121.6782 | 121.637 | 121.5866 | 61.1298 | 61.1618
719.7812 | 121.8521 | -61.2167 | 60.434 | -0.13557 | 0.0043942 | 0.066892 | 0.059039 | -0.00063233 | -0.0088206 | 0.00061746 | -0.01004 | 0.0038153 | 0.065772 | 0.056454 | -0.01367 | 0.025699 | -0.0051525 | 0.054932 | 60.2417 | -61.2396 | 60.4935 | -60.9421 | -61.377 | -61.3449 | 0.1236 | 60.2371 | -61.2396 | 60.4019 | -61.1755 | -61.2991 | -61.29 | -0.022888 | -0.19226 | 0.059509 | 0.27466 | -0.12817 | -0.16022 | -0.10529 | -0.13733 | -0.022888 | -0.19684 | -0.032043 | 0.041199 | -0.073242 | -0.082397 | -0.050354 | -0.059509 | 0.29755 | 121.7331 | 0.064087 | 121.6415 | 121.4813 | 121.4767 | 121.4584 | 121.4539 | -121.6736 | -121.6736 | 121.7102 | 121.6187 | 61.2717 | 61.3403
721.5156 | 121.9025 | -61.2488 | 60.3653 | -0.12794 | 0.007385 | 0.064328 | 0.060534 | -0.00020513 | -0.0088206 | -0.0045095 | -0.0039367 | 0.0029607 | 0.065772 | 0.048337 | -0.014311 | 0.023776 | -0.0047253 | -0.10071 | 60.1822 | -61.2625 | 60.4156 | -61.0245 | -61.4639 | -61.4044 | 0.022888 | 60.1959 | -61.2854 | 60.3973 | -61.1847 | -61.2991 | -61.2717 | -0.013733 | -0.18311 | 0.050354 | 0.2243 | -0.15564 | -0.21515 | -0.14191 | -0.20142 | -0.036621 | -0.16937 | 0.032044 | 0.064087 | -0.022888 | -0.050354 | 0.013733 | -0.013733 | 0.23804 | 121.6782 | 0.10071 | 121.6827 | 121.4447 | 121.4813 | 121.431 | 121.4447 | -121.6278 | -121.6507 | 121.6644 | 121.6461 | 61.1481 | 61.2717
723.2656 | 121.8979 | -61.2167 | 60.3607 | -0.12794 | 0.0048214 | 0.063474 | 0.060321 | -0.00084593 | -0.007966 | -0.0051505 | -0.022247 | 0.0027471 | 0.064277 | 0.051114 | -0.012174 | 0.025058 | -0.0034435 | -0.10071 | 60.1913 | -61.2305 | 60.4248 | -61.0199 | -61.4594 | -61.3953 | 0.018311 | 60.1639 | -61.2671 | 60.379 | -61.1984 | -61.3083 | -61.29 | -0.013733 | -0.16937 | 0.064087 | 0.19684 | -0.17853 | -0.24262 | -0.16479 | -0.22888 | -0.050354 | -0.19684 | 0.01831 | 0.018311 | -0.073242 | -0.091553 | -0.022888 | -0.041199 | 0.21057 | 121.6553 | 0.068665 | 121.6461 | 121.4218 | 121.431 | 121.4081 | 121.3806 | -121.5912 | -121.6278 | 121.6415 | 121.5958 | 61.116 | 61.235
724.9531 | 121.8155 | -61.3449 | 60.3149 | -0.13557 | 0.0093076 | 0.064756 | 0.06502 | -0.0025549 | -0.008607 | -0.0045095 | -0.12296 | 0.0050971 | 0.065559 | 0.056881 | -0.014097 | 0.025699 | 0.00018809 | -0.19226 | 60.2005 | -61.3495 | 60.3012 | -61.1847 | -61.615 | -61.5692 | -0.15106 | 60.1822 | -61.3312 | 60.26 | -61.3632 | -61.5005 | -61.4227 | -0.004577 | -0.11444 | -0.013733 | 0.16022 | -0.2243 | -0.27008 | -0.21973 | -0.2655 | 0.013733 | -0.13275 | -0.054931 | -0.01831 | -0.077819 | -0.15564 | -0.091552 | -0.16937 | 0.1648 | 121.6507 | -0.032043 | 121.5912 | 121.55 | 121.5134 | 121.5454 | 121.5271 | -121.6644 | -121.6461 | 121.6461 | 121.6049 | 61.1526 | 61.1938
726.7031 | 121.962 | -61.2717 | 60.2737 | -0.11269 | 0.0080258 | 0.066892 | 0.062884 | -0.0019141 | -0.0075388 | -0.0028005 | -0.052765 | 0.0036017 | 0.067481 | 0.049832 | -0.012815 | 0.025699 | -0.0040845 | -0.12817 | 60.1135 | -61.3037 | 60.4248 | -61.0199 | -61.5005 | -61.441 | 0.009155 | 60.1089 | -61.3174 | 60.3973 | -61.2076 | -61.3037 | -61.2808 | -0.032044 | -0.16022 | 0.15106 | 0.25177 | -0.16937 | -0.22888 | -0.13733 | -0.19684 | -0.045777 | -0.1648 | 0.1236 | 0.064086 | -0.009156 | -0.032044 | 0.036621 | 0.013733 | 0.28381 | 121.7285 | 0.10986 | 121.7148 | 121.4172 | 121.4264 | 121.3852 | 121.3806 | -121.5775 | -121.5912 | 121.6965 | 121.669 | 61.1435 | 61.2808
728.4531 | 121.8338 | -61.3083 | 60.3104 | -0.05928 | 0.0069578 | 0.067319 | 0.063311 | -0.00041873 | -0.008607 | -0.0025869 | -0.098541 | 0.0050971 | 0.064918 | 0.049405 | -0.014311 | 0.027408 | -0.0051525 | -0.10986 | 60.2097 | -61.3037 | 60.3699 | -61.0703 | -61.5234 | -61.4731 | -0.022888 | 60.173 | -61.3266 | 60.3104 | -61.2946 | -61.441 | -61.3861 | 0.004578 | -0.10071 | 0.059509 | 0.23804 | -0.16479 | -0.21515 | -0.16937 | -0.21973 | -0.01831 | -0.13733 | 0 | 0.013733 | -0.077819 | -0.13275 | -0.059509 | -0.11444 | 0.23346 | 121.6736 | 0.032043 | 121.637 | 121.5134 | 121.4996 | 121.5179 | 121.4813 | -121.6141 | -121.637 | 121.6782 | 121.6187 | 61.1984 | 61.2854
730.1562 | 121.8292 | -61.3174 | 60.3378 | -0.074539 | 0.0052488 | 0.067105 | 0.064807 | -0.0019141 | -0.0083932 | -0.0015189 | -0.12601 | 0.0050971 | 0.0662 | 0.048764 | -0.011533 | 0.025699 | -0.0045117 | -0.10986 | 60.2097 | -61.29 | 60.3973 | -61.0931 | -61.5234 | -61.496 | -0.064087 | 60.1639 | -61.3403 | 60.2829 | -61.2991 | -61.441 | -61.4044 | 0.027466 | -0.12817 | 0.059509 | 0.2243 | -0.17853 | -0.20599 | -0.20599 | -0.23346 | -0.022888 | -0.17395 | -0.054932 | 0.018311 | -0.086975 | -0.1236 | -0.064087 | -0.10071 | 0.19684 | 121.6873 | 0.041199 | 121.6232 | 121.4996 | 121.5042 | 121.5271 | 121.4813 | -121.6278 | -121.6782 | 121.7148 | 121.6003 | 61.2076 | 61.2534
731.8906 | 121.843 | -61.3037 | 60.3058 | -0.06691 | 0.007385 | 0.065396 | 0.064593 | 0.0012903 | -0.0098886 | -0.0070731 | -0.080231 | 0.0044561 | 0.065772 | 0.053677 | -0.013456 | 0.025058 | -0.0053661 | -0.10529 | 60.1776 | -61.2991 | 60.3928 | -61.0703 | -61.5097 | -61.4731 | -0.018311 | 60.1913 | -61.3266 | 60.3195 | -61.2717 | -61.4273 | -61.3586 | 0.004578 | -0.12817 | 0.086975 | 0.23346 | -0.16937 | -0.20599 | -0.17395 | -0.21057 | -0.022888 | -0.11444 | 0.013733 | 0.032044 | -0.054932 | -0.1236 | -0.032044 | -0.10071 | 0.22888 | 121.6919 | 0.054932 | 121.6461 | 121.4767 | 121.5179 | 121.4813 | 121.4951 | -121.6049 | -121.6324 | 121.6965 | 121.6232 | 61.1984 | 61.2854
733.6406 | 121.9254 | -61.235 | 60.3424 | -0.1432 | 0.0063168 | 0.065396 | 0.057544 | 0.0019311 | -0.0077524 | -0.0045095 | -0.0039367 | 0.0033881 | 0.067268 | 0.056454 | -0.010893 | 0.022922 | -0.0042981 | -0.1236 | 60.1318 | -61.2808 | 60.4385 | -60.9879 | -61.4685 | -61.4136 | 0.013733 | 60.141 | -61.2991 | 60.3836 | -61.1847 | -61.29 | -61.2671 | -0.045777 | -0.21057 | 0.096131 | 0.24719 | -0.17853 | -0.23346 | -0.13275 | -0.18768 | -0.064087 | -0.20142 | 0.041199 | 0.050354 | -0.032044 | -0.054932 | 0.032043 | 0.009155 | 0.29297 | 121.7194 | 0.11444 | 121.6827 | 121.4127 | 121.4401 | 121.3669 | 121.376 | -121.6232 | -121.6415 | 121.6736 | 121.6187 | 61.1114 | 61.2488
735.3906 | 121.907 | -61.2305 | 60.379 | -0.13557 | 0.0043942 | 0.068173 | 0.059893 | 0.00043587 | -0.008607 | -0.0040823 | 0.017425 | 0.0038153 | 0.067054 | 0.051541 | -0.014311 | 0.025699 | -0.0038709 | -0.11444 | 60.1868 | -61.2534 | 60.4248 | -61.0291 | -61.4639 | -61.3998 | 0.009155 | 60.1685 | -61.2762 | 60.3745 | -61.203 | -61.2991 | -61.2717 | -0.022888 | -0.19226 | 0.045777 | 0.20142 | -0.16937 | -0.23346 | -0.14648 | -0.21057 | -0.045776 | -0.21057 | -0.004577 | 0.027466 | -0.041198 | -0.068664 | 0.004578 | -0.022888 | 0.2243 | 121.6782 | 0.073242 | 121.6507 | 121.4401 | 121.4447 | 121.4172 | 121.3989 | -121.6324 | -121.6553 | 121.6553 | 121.6049 | 61.116 | 61.2396
737.1406 | 121.875 | -61.2762 | 60.347 | -0.051651 | 0.0048214 | 0.068173 | 0.064807 | -0.0061865 | -0.0081796 | -0.0036551 | -0.077179 | 0.0053107 | 0.066627 | 0.044491 | -0.012815 | 0.027835 | -0.0094251 | -0.068665 | 60.2234 | -61.29 | 60.4111 | -61.0565 | -61.5051 | -61.4685 | 0.027466 | 60.1776 | -61.3083 | 60.3516 | -61.235 | -61.3586 | -61.322 | -0.013733 | -0.1236 | 0.064087 | 0.21973 | -0.19226 | -0.22888 | -0.17853 | -0.21515 | -0.032044 | -0.16937 | 0.004577 | 0.041199 | -0.045776 | -0.082398 | -0.013732 | -0.050354 | 0.23346 | 121.701 | 0.073243 | 121.6599 | 121.5134 | 121.4859 | 121.4996 | 121.4539 | -121.637 | -121.6553 | 121.6873 | 121.6278 | 61.2076 | 61.3037
738.8281 | 121.9345 | -61.2442 | 60.3012 | -0.16609 | 0.0078122 | 0.067105 | 0.061816 | 0.00022207 | -0.0081796 | -0.0045095 | -0.037506 | 0.0027471 | 0.065559 | 0.053464 | -0.01132 | 0.024204 | -0.0051525 | -0.13275 | 60.1318 | -61.29 | 60.4477 | -60.9879 | -61.4685 | -61.3953 | 0.022888 | 60.141 | -61.2991 | 60.3973 | -61.1893 | -61.2946 | -61.2946 | -0.045776 | -0.16937 | 0.14648 | 0.25635 | -0.15106 | -0.2243 | -0.10529 | -0.17853 | -0.054931 | -0.16022 | 0.096131 | 0.054932 | -0.050354 | -0.050354 | 0.004577 | 0.004577 | 0.30212 | 121.7377 | 0.10986 | 121.6965 | 121.4218 | 121.4401 | 121.376 | 121.3852 | -121.5912 | -121.6003 | 121.6919 | 121.6415 | 61.1115 | 61.2671
740.5625 | 121.9116 | -61.2305 | 60.3424 | -0.1432 | 0.0046078 | 0.066464 | 0.059893 | -0.0036231 | -0.007966 | -0.0032277 | -0.028351 | 0.0038153 | 0.067268 | 0.049405 | -0.013029 | 0.023776 | -0.0010937 | -0.12817 | 60.1685 | -61.29 | 60.4294 | -61.0062 | -61.4868 | -61.4227 | 0.045776 | 60.1318 | -61.3083 | 60.3928 | -61.1893 | -61.2808 | -61.29 | -0.059509 | -0.17395 | 0.086975 | 0.2243 | -0.19226 | -0.25635 | -0.13275 | -0.19684 | -0.07782 | -0.21057 | 0.050354 | 0.041199 | -0.059509 | -0.050354 | 0.018311 | 0.027466 | 0.28381 | 121.7194 | 0.11902 | 121.7011 | 121.4584 | 121.4401 | 121.3989 | 121.3623 | -121.6324 | -121.6507 | 121.6599 | 121.6232 | 61.1023 | 61.2762
742.2969 | 121.9299 | -61.29 | 60.2829 | -0.16609 | 0.0054624 | 0.065396 | 0.06438 | 0.0072717 | -0.0075388 | -0.00066434 | -0.080231 | 0.0033881 | 0.065986 | 0.05325 | -0.013242 | 0.027621 | -0.0042981 | -0.22888 | 60.1776 | -61.3403 | 60.3607 | -61.1023 | -61.5738 | -61.5051 | -0.073242 | 60.1364 | -61.3403 | 60.3745 | -61.2305 | -61.3632 | -61.3129 | -0.050354 | -0.10529 | 0.07782 | 0.18768 | -0.21515 | -0.28381 | -0.1648 | -0.23346 | -0.050354 | -0.14648 | 0.091553 | 0.059509 | -0.022888 | -0.073242 | 0.027466 | -0.022888 | 0.23804 | 121.701 | 0.10986 | 121.7148 | 121.5179 | 121.4767 | 121.4676 | 121.4264 | -121.6232 | -121.6232 | 121.6507 | 121.6644 | 61.0611 | 61.2167
743.9844 | 121.8658 | -61.29 | 60.347 | -0.10506 | 0.0058896 | 0.068173 | 0.061602 | -0.0038367 | -0.007966 | -0.0017325 | -0.098541 | 0.0046697 | 0.0662 | 0.061154 | -0.014311 | 0.025699 | -0.0049389 | -0.082397 | 60.2097 | -61.2762 | 60.4019 | -61.0474 | -61.5097 | -61.4548 | 0.013733 | 60.1822 | -61.2991 | 60.347 | -61.235 | -61.3586 | -61.322 | 0.013733 | -0.13733 | 0.054932 | 0.24262 | -0.1648 | -0.21973 | -0.17853 | -0.23346 | -0.009155 | -0.16479 | 0 | 0.054932 | -0.032043 | -0.068665 | -0.022888 | -0.05951 | 0.22888 | 121.6782 | 0.064087 | 121.6461 | 121.4859 | 121.4813 | 121.4996 | 121.4722 | -121.6232 | -121.6461 | 121.6919 | 121.637 | 61.2076 | 61.3037
745.7344 | 121.8567 | -61.2167 | 60.4202 | -0.074539 | 0.0037534 | 0.063687 | 0.060321 | 0.0025721 | -0.010957 | -0.0025869 | -0.016144 | 0.0027471 | 0.064277 | 0.058804 | -0.01132 | 0.024844 | -0.0028027 | 0.050354 | 60.2463 | -61.2122 | 60.4797 | -60.965 | -61.3907 | -61.3632 | 0.13275 | 60.2509 | -61.2671 | 60.3882 | -61.1938 | -61.2991 | -61.2946 | 0.004578 | -0.17395 | 0.059509 | 0.25177 | -0.14648 | -0.17395 | -0.15106 | -0.17853 | -0.050354 | -0.16937 | -0.032043 | 0.022888 | -0.07782 | -0.082397 | -0.027466 | -0.032043 | 0.24719 | 121.6919 | 0.073242 | 121.6553 | 121.4584 | 121.5179 | 121.463 | 121.4676 | -121.6324 | -121.6873 | 121.6965 | 121.6049 | 61.2671 | 61.3495
747.4844 | 121.8475 | -61.2991 | 60.3333 | -0.11269 | 0.0075986 | 0.065183 | 0.065448 | -0.0023413 | -0.0077524 | -0.0034415 | -0.12601 | 0.0053107 | 0.067054 | 0.055386 | -0.01367 | 0.024844 | -0.0051525 | -0.10529 | 60.2097 | -61.2991 | 60.3836 | -61.0748 | -61.5143 | -61.4777 | -0.032043 | 60.1776 | -61.322 | 60.3149 | -61.2717 | -61.4319 | -61.3678 | 0 | -0.1236 | 0.050354 | 0.2243 | -0.17853 | -0.21515 | -0.17853 | -0.21515 | -0.022888 | -0.15564 | -0.018311 | 0.027466 | -0.068665 | -0.13275 | -0.045777 | -0.10986 | 0.2243 | 121.6827 | 0.050354 | 121.637 | 121.5088 | 121.4996 | 121.5088 | 121.4767 | -121.6324 | -121.6553 | 121.6827 | 121.6141 | 61.1938 | 61.2671
749.1719 | 121.8613 | -61.2671 | 60.347 | -0.028763 | 0.003967 | 0.065396 | 0.063311 | 0.0021447 | -0.0083932 | -0.0021597 | -0.098541 | 0.0061651 | 0.0662 | 0.055386 | -0.011533 | 0.027194 | -0.0042981 | -0.059509 | 60.2371 | -61.3129 | 60.4248 | -61.0474 | -61.4868 | -61.4639 | 0.022888 | 60.2097 | -61.2991 | 60.347 | -61.2305 | -61.3495 | -61.3083 | -0.045776 | -0.10986 | 0.07782 | 0.21973 | -0.19684 | -0.21973 | -0.15106 | -0.17395 | -0.032043 | -0.13733 | 0 | 0.036621 | -0.041199 | -0.082397 | -0.009156 | -0.050354 | 0.2655 | 121.7377 | 0.068664 | 121.6461 | 121.55 | 121.5088 | 121.5042 | 121.4767 | -121.6599 | -121.6461 | 121.6919 | 121.6141 | 61.2076 | 61.29
750.9219 | 121.8475 | -61.322 | 60.3241 | -0.06691 | 0.0099484 | 0.067105 | 0.060748 | -0.0034095 | -0.0088206 | -0.0019461 | -0.092438 | 0.0065923 | 0.067695 | 0.058163 | -0.010679 | 0.026981 | -0.0025891 | -0.11444 | 60.2188 | -61.3083 | 60.3607 | -61.0794 | -61.5463 | -61.5051 | -0.054932 | 60.173 | -61.3083 | 60.2875 | -61.3129 | -61.4365 | -61.3724 | 0.013732 | -0.10529 | 0.036621 | 0.24261 | -0.18311 | -0.22431 | -0.19684 | -0.23804 | 0.013732 | -0.15106 | -0.036621 | 0.009155 | -0.050354 | -0.11444 | -0.064086 | -0.12817 | 0.22888 | 121.669 | -0.004577 | 121.5958 | 121.5271 | 121.4813 | 121.5408 | 121.4951 | -121.6324 | -121.6324 | 121.6827 | 121.6095 | 61.2076 | 61.2671
752.6719 | 121.9437 | -61.2762 | 60.2875 | -0.11269 | 0.0075986 | 0.066037 | 0.060321 | -0.0036231 | -0.008607 | -0.0015189 | -0.058869 | 0.0033881 | 0.065559 | 0.057095 | -0.013883 | 0.025912 | -0.0045117 | -0.20142 | 60.1822 | -61.2991 | 60.3653 | -61.0703 | -61.496 | -61.4365 | -0.054932 | 60.1044 | -61.3358 | 60.3973 | -61.2076 | -61.3403 | -61.2762 | -0.022888 | -0.10529 | 0.077819 | 0.20599 | -0.16022 | -0.21973 | -0.13733 | -0.19684 | -0.059509 | -0.18311 | 0.10986 | 0.068664 | 0 | -0.064087 | 0.059509 | -0.004578 | 0.22888 | 121.6644 | 0.12817 | 121.7331 | 121.4813 | 121.4401 | 121.4584 | 121.3806 | -121.5866 | -121.6232 | 121.6415 | 121.6736 | 61.0748 | 61.2213
754.3594 | 121.8933 | -61.29 | 60.3516 | -0.074539 | 0.007385 | 0.066251 | 0.063098 | -0.0027685 | -0.009675 | -0.0023733 | -0.064972 | 0.0038153 | 0.065772 | 0.05325 | -0.011106 | 0.025912 | -0.0025891 | -0.086975 | 60.2097 | -61.2946 | 60.4065 | -61.0474 | -61.496 | -61.4685 | 0.032043 | 60.1868 | -61.29 | 60.3516 | -61.2259 | -61.3632 | -61.3083 | -0.004578 | -0.14191 | 0.054932 | 0.24262 | -0.17853 | -0.20599 | -0.17395 | -0.20142 | 0 | -0.16479 | 0 | 0.064087 | -0.018311 | -0.073242 | -0.018311 | -0.073242 | 0.24719 | 121.7011 | 0.064087 | 121.6415 | 121.5042 | 121.4767 | 121.4996 | 121.4767 | -121.6461 | -121.6415 | 121.6965 | 121.6415 | 61.203 | 61.322
756.0938 | 121.9482 | -61.203 | 60.3882 | -0.13557 | 0.0046078 | 0.064328 | 0.060748 | -0.00041873 | -0.010316 | -0.0017325 | 0.020477 | 0.0018927 | 0.065559 | 0.053036 | -0.011961 | 0.023563 | -0.00088011 | 0.045776 | 60.2097 | -61.203 | 60.5347 | -60.878 | -61.3174 | -61.29 | 0.21057 | 60.2188 | -61.2122 | 60.4752 | -61.0703 | -61.1847 | -61.1893 | 0 | -0.17853 | 0.14648 | 0.32501 | -0.086975 | -0.11444 | -0.086975 | -0.11444 | -0.009155 | -0.16937 | 0.086975 | 0.13275 | 0.013733 | 0.018311 | 0.022888 | 0.027466 | 0.32501 | 121.7377 | 0.14191 | 121.6873 | 121.4127 | 121.431 | 121.4127 | 121.4218 | -121.5912 | -121.6003 | 121.7377 | 121.6782 | 61.2488 | 61.4136
757.8594 | 121.9666 | -61.2808 | 60.2783 | -0.12032 | 0.007385 | 0.064328 | 0.062457 | -0.0042639 | -0.0098886 | -0.0021597 | -0.040558 | 0.0044561 | 0.064704 | 0.0556 | -0.014951 | 0.025058 | -0.0047253 | -0.15106 | 60.1501 | -61.3174 | 60.4156 | -61.0336 | -61.4868 | -61.4319 | -0.013733 | 60.1135 | -61.3037 | 60.3882 | -61.2076 | -61.3174 | -61.2762 | -0.036621 | -0.12817 | 0.13733 | 0.24719 | -0.15106 | -0.20599 | -0.11444 | -0.16937 | -0.022888 | -0.16479 | 0.10986 | 0.073242 | 0.004578 | -0.036621 | 0.027466 | -0.013733 | 0.28381 | 121.7331 | 0.09613 | 121.6919 | 121.4676 | 121.4172 | 121.431 | 121.3943 | -121.5958 | -121.582 | 121.6965 | 121.669 | 61.1298 | 61.2671
759.5469 | 121.9574 | -61.2762 | 60.2783 | -0.089798 | 0.007385 | 0.066892 | 0.062671 | 0.0029993 | -0.0090342 | -0.0062185 | -0.04361 | 0.0040289 | 0.066627 | 0.053891 | -0.014097 | 0.026126 | -0.0051525 | -0.15564 | 60.1593 | -61.2946 | 60.4156 | -61.0336 | -61.4868 | -61.4365 | -0.013733 | 60.0998 | -61.3174 | 60.3882 | -61.2167 | -61.3312 | -61.2717 | -0.018311 | -0.11902 | 0.13733 | 0.24262 | -0.16022 | -0.21057 | -0.14191 | -0.19226 | -0.041199 | -0.17853 | 0.10986 | 0.059509 | 0.004578 | -0.054932 | 0.045777 | -0.013733 | 0.26093 | 121.7102 | 0.10071 | 121.7056 | 121.4539 | 121.4172 | 121.4355 | 121.376 | -121.5729 | -121.5958 | 121.6919 | 121.6644 | 61.1206 | 61.2625
761.2812 | 121.9437 | -61.2946 | 60.2875 | -0.15083 | 0.0063168 | 0.066892 | 0.062884 | 0.0015039 | -0.011384 | -0.0015189 | -0.034454 | 0.0038153 | 0.064704 | 0.051541 | -0.014738 | 0.02634 | -0.0047253 | -0.13275 | 60.1501 | -61.3083 | 60.4248 | -61.0245 | -61.496 | -61.4456 | 0 | 60.1181 | -61.3129 | 60.3745 | -61.1984 | -61.3312 | -61.2854 | -0.013733 | -0.13733 | 0.13733 | 0.27008 | -0.15106 | -0.20142 | -0.13733 | -0.18768 | -0.01831 | -0.16937 | 0.086975 | 0.096131 | 0.009156 | -0.036621 | 0.027466 | -0.018311 | 0.28381 | 121.7331 | 0.11444 | 121.6873 | 121.4584 | 121.431 | 121.4447 | 121.4127 | -121.5958 | -121.6003 | 121.7194 | 121.669 | 61.1618 | 61.2946
763.0469 | 121.9711 | -61.2122 | 60.3699 | -0.12794 | 0.0048214 | 0.065396 | 0.05968 | -0.0023413 | -0.007966 | -0.0028005 | 0.0052185 | 0.0055243 | 0.066413 | 0.047482 | -0.013456 | 0.024844 | -0.0066479 | -0.004578 | 60.2325 | -61.2396 | 60.5164 | -60.9238 | -61.3358 | -61.3129 | 0.17853 | 60.1913 | -61.2076 | 60.4706 | -61.0977 | -61.1847 | -61.1893 | -0.027466 | -0.13733 | 0.14648 | 0.28839 | -0.10071 | -0.1236 | -0.073242 | -0.09613 | 0.004577 | -0.17853 | 0.10071 | 0.11444 | 0.022888 | 0.027466 | 0.018311 | 0.022889 | 0.31586 | 121.756 | 0.10986 | 121.6782 | 121.4722 | 121.3989 | 121.4447 | 121.4035 | -121.6095 | -121.5775 | 121.7285 | 121.6827 | 61.2076 | 61.3907
764.7344 | 121.9299 | -61.1847 | 60.3882 | -0.12032 | 0.0035398 | 0.065824 | 0.060321 | -0.0049047 | -0.0075388 | -0.00066434 | 0.0021667 | 0.0021063 | 0.0662 | 0.048337 | -0.014951 | 0.025912 | -0.0070751 | 0.036621 | 60.2097 | -61.1893 | 60.5438 | -60.8826 | -61.3449 | -61.2991 | 0.2243 | 60.2188 | -61.2488 | 60.4752 | -61.0657 | -61.1755 | -61.1755 | -0.004578 | -0.17853 | 0.15564 | 0.30212 | -0.11444 | -0.16022 | -0.10986 | -0.15564 | -0.064087 | -0.16937 | 0.086975 | 0.11902 | 0.009155 | 0.009155 | 0.073242 | 0.073242 | 0.3067 | 121.7331 | 0.1831 | 121.7239 | 121.3989 | 121.4676 | 121.3943 | 121.4035 | -121.5775 | -121.637 | 121.7285 | 121.6599 | 61.2213 | 61.409
766.4688 | 121.9299 | -61.2076 | 60.3745 | -0.12794 | 0.0061032 | 0.065824 | 0.063311 | -0.0042639 | -0.0088206 | -0.0028005 | -0.01004 | 0.0027471 | 0.066627 | 0.04855 | -0.013456 | 0.027194 | -0.0032299 | -0.054932 | 60.1959 | -61.2488 | 60.434 | -61.0153 | -61.4365 | -61.3815 | 0.068665 | 60.1868 | -61.2442 | 60.4431 | -61.1389 | -61.2259 | -61.2213 | -0.041198 | -0.17853 | 0.059509 | 0.19226 | -0.17395 | -0.22888 | -0.13275 | -0.18768 | -0.036621 | -0.18768 | 0.068664 | 0.068665 | -0.013732 | -0.01831 | 0.022889 | 0.018311 | 0.23346 | 121.6827 | 0.10529 | 121.6873 | 121.4447 | 121.431 | 121.4035 | 121.3943 | -121.6232 | -121.6187 | 121.6415 | 121.6507 | 61.1526 | 61.2762
768.2031 | 121.907 | -61.203 | 60.4111 | -0.12032 | 0.0052488 | 0.063687 | 0.061175 | -0.0027685 | -0.013093 | -0.0030141 | -0.028351 | 0.0063787 | 0.064491 | 0.0509 | -0.013456 | 0.024417 | -0.0049389 | 0.059509 | 60.2142 | -61.2167 | 60.5072 | -60.9558 | -61.3724 | -61.3266 | 0.16937 | 60.228 | -61.2305 | 60.4385 | -61.1206 | -61.235 | -61.2259 | -0.013733 | -0.19684 | 0.09613 | 0.24719 | -0.1236 | -0.16937 | -0.10986 | -0.15564 | -0.027466 | -0.18311 | 0.027466 | 0.082398 | -0.022888 | -0.032043 | 0.004578 | -0.004577 | 0.26093 | 121.7239 | 0.10986 | 121.669 | 121.431 | 121.4584 | 121.4172 | 121.431 | -121.6278 | -121.6415 | 121.7102 | 121.6415 | 61.2625 | 61.3724
769.9531 | 121.9254 | -61.2488 | 60.3241 | -0.10506 | 0.0058896 | 0.067746 | 0.062243 | -0.0027685 | -0.010102 | -0.0055777 | -0.06192 | 0.0038153 | 0.065559 | 0.0556 | -0.013883 | 0.025272 | -0.0042981 | -0.11444 | 60.1456 | -61.2808 | 60.4431 | -60.9924 | -61.4639 | -61.4182 | 0.018311 | 60.1456 | -61.3083 | 60.3928 | -61.2076 | -61.3083 | -61.2671 | -0.032044 | -0.17853 | 0.11902 | 0.25635 | -0.16937 | -0.21515 | -0.13733 | -0.18311 | -0.05951 | -0.17853 | 0.068664 | 0.041198 | -0.018311 | -0.05951 | 0.041199 | 0 | 0.28839 | 121.7239 | 0.10071 | 121.7011 | 121.4264 | 121.4539 | 121.3943 | 121.3943 | -121.6049 | -121.6324 | 121.6919 | 121.6415 | 61.1343 | 61.2671
771.625 | 121.9666 | -61.2625 | 60.3012 | -0.17372 | 0.009094 | 0.065396 | 0.06438 | 0.0019311 | -0.0092478 | -0.0025869 | -0.068024 | 0.0021063 | 0.065986 | 0.054318 | -0.015379 | 0.026126 | -0.0051525 | -0.12817 | 60.1364 | -61.29 | 60.434 | -61.0336 | -61.5005 | -61.4502 | 0.013733 | 60.1044 | -61.3312 | 60.4065 | -61.1984 | -61.3174 | -61.2671 | -0.027466 | -0.16479 | 0.13275 | 0.22888 | -0.18768 | -0.23804 | -0.16022 | -0.21057 | -0.068665 | -0.19684 | 0.10529 | 0.064087 | -0.004578 | -0.054932 | 0.064087 | 0.013733 | 0.25635 | 121.7239 | 0.13275 | 121.7377 | 121.4264 | 121.4355 | 121.3989 | 121.3669 | -121.5912 | -121.6324 | 121.6965 | 121.669 | 61.1343 | 61.2762
773.375 | 121.9437 | -61.2762 | 60.3012 | -0.18135 | 0.0063168 | 0.066464 | 0.063739 | -0.0046911 | -0.010743 | -0.0025869 | -0.086334 | 0.0038153 | 0.067695 | 0.04855 | -0.014311 | 0.025272 | -0.0049389 | -0.12817 | 60.141 | -61.3037 | 60.4294 | -61.0199 | -61.4822 | -61.4182 | 0.022888 | 60.1135 | -61.3174 | 60.4111 | -61.1847 | -61.3174 | -61.2808 | -0.027466 | -0.16022 | 0.12817 | 0.25635 | -0.14191 | -0.20599 | -0.11444 | -0.17853 | -0.041199 | -0.18768 | 0.10986 | 0.091553 | -0.004578 | -0.041199 | 0.036621 | 0 | 0.28381 | 121.7331 | 0.13275 | 121.7285 | 121.4447 | 121.431 | 121.4172 | 121.3898 | -121.6049 | -121.6187 | 121.7056 | 121.6873 | 61.1481 | 61.2991
775.125 | 121.8887 | -61.2488 | 60.3516 | -0.089798 | 0.0061032 | 0.065396 | 0.06438 | 0.0019311 | -0.0081796 | -0.0053641 | -0.1138 | 0.0046697 | 0.064277 | 0.058804 | -0.015165 | 0.027408 | -0.0051525 | -0.054932 | 60.2142 | -61.2946 | 60.4111 | -61.0611 | -61.4822 | -61.4594 | 0.027466 | 60.1913 | -61.2991 | 60.3607 | -61.2305 | -61.377 | -61.3129 | -0.045777 | -0.13733 | 0.05951 | 0.18768 | -0.21057 | -0.23346 | -0.16479 | -0.18768 | -0.050354 | -0.16022 | 0.009156 | 0.01831 | -0.064087 | -0.12817 | -0.013733 | -0.07782 | 0.23346 | 121.7056 | 0.068664 | 121.6599 | 121.5088 | 121.4905 | 121.463 | 121.4401 | -121.6461 | -121.6507 | 121.6599 | 121.6095 | 61.1938 | 61.2762
776.8125 | 121.9162 | -61.2305 | 60.3378 | -0.10506 | 0.0041806 | 0.065824 | 0.062884 | 0.00064947 | -0.0071116 | -0.00066434 | -0.0069885 | 0.0029607 | 0.065345 | 0.0509 | -0.012174 | 0.024844 | -0.0030163 | -0.09613 | 60.1364 | -61.2717 | 60.4385 | -60.997 | -61.4639 | -61.409 | 0.036621 | 60.1685 | -61.2854 | 60.3836 | -61.203 | -61.3037 | -61.2762 | -0.041198 | -0.20142 | 0.10071 | 0.23346 | -0.17853 | -0.23346 | -0.13733 | -0.19226 | -0.054931 | -0.16937 | 0.045776 | 0.027466 | -0.045776 | -0.073242 | 0.009155 | -0.018311 | 0.27466 | 121.7102 | 0.082397 | 121.669 | 121.4081 | 121.4539 | 121.3669 | 121.3989 | -121.6095 | -121.6232 | 121.669 | 121.6141 | 61.1343 | 61.2671
778.5625 | 121.9162 | -61.2488 | 60.3699 | -0.13557 | 0.0046078 | 0.064969 | 0.060962 | -0.0021277 | -0.011598 | -0.0010915 | -0.022247 | 0.0040289 | 0.067268 | 0.050473 | -0.014097 | 0.024631 | -0.0051525 | -0.064087 | 60.2097 | -61.2717 | 60.4294 | -61.0245 | -61.4639 | -61.4044 | 0.036621 | 60.2097 | -61.2625 | 60.4065 | -61.1893 | -61.2854 | -61.2671 | -0.022888 | -0.16022 | 0.059509 | 0.2243 | -0.15564 | -0.21515 | -0.13275 | -0.19226 | -0.013733 | -0.16022 | 0.036621 | 0.059509 | -0.018311 | -0.036621 | -0.004578 | -0.022888 | 0.24719 | 121.701 | 0.073242 | 121.669 | 121.4813 | 121.4722 | 121.4584 | 121.4584 | -121.6415 | -121.6324 | 121.6782 | 121.6553 | 61.1847 | 61.2854
780.3281 | 121.8475 | -61.2946 | 60.3241 | -0.13557 | 0.005676 | 0.066464 | 0.064166 | -0.0040503 | -0.0081796 | -0.0023733 | -0.09549 | 0.0055243 | 0.067909 | 0.06329 | -0.01367 | 0.026767 | -0.0021619 | -0.2243 | 60.173 | -61.3586 | 60.3104 | -61.1664 | -61.5967 | -61.5509 | -0.14191 | 60.1776 | -61.3449 | 60.2921 | -61.3312 | -61.4502 | -61.3907 | -0.064087 | -0.15106 | -0.013733 | 0.12817 | -0.25635 | -0.30212 | -0.19226 | -0.23804 | -0.050354 | -0.14648 | -0.032044 | -0.036621 | -0.09613 | -0.15564 | -0.045776 | -0.10529 | 0.19226 | 121.669 | 0.013733 | 121.637 | 121.5317 | 121.5225 | 121.4676 | 121.4722 | -121.6827 | -121.669 | 121.6049 | 121.5866 | 61.0703 | 61.1526
782.0156 | 121.9208 | -61.2442 | 60.3333 | -0.11269 | 0.0050352 | 0.066037 | 0.06203 | -0.0029821 | -0.006898 | -0.0023733 | -0.034454 | 0.0033881 | 0.067481 | 0.049191 | -0.012815 | 0.025485 | -0.0049389 | -0.10529 | 60.1639 | -61.2808 | 60.4156 | -61.0153 | -61.4685 | -61.409 | 0.004578 | 60.1685 | -61.2671 | 60.3928 | -61.1801 | -61.3037 | -61.2717 | -0.036621 | -0.16937 | 0.082397 | 0.22888 | -0.16479 | -0.2243 | -0.12817 | -0.18768 | -0.022888 | -0.1648 | 0.059509 | 0.064087 | -0.027465 | -0.059509 | -0.004577 | -0.036621 | 0.2655 | 121.6965 | 0.086975 | 121.6599 | 121.4447 | 121.4355 | 121.4081 | 121.4127 | -121.6141 | -121.6003 | 121.6599 | 121.637 | 61.1389 | 61.2488
783.7656 | 121.9162 | -61.2488 | 60.3607 | -0.13557 | 0.0041806 | 0.064328 | 0.061816 | -0.0038367 | -0.011384 | -0.0023733 | -0.022247 | 0.0042425 | 0.065345 | 0.048123 | -0.013029 | 0.025485 | -0.0062207 | -0.091553 | 60.173 | -61.2717 | 60.4294 | -61.0153 | -61.4594 | -61.3907 | 0.018311 | 60.2097 | -61.2717 | 60.3882 | -61.1984 | -61.3083 | -61.2625 | -0.022888 | -0.18768 | 0.068664 | 0.23346 | -0.14191 | -0.21057 | -0.11902 | -0.18768 | -0.022888 | -0.15106 | 0.027466 | 0.050354 | -0.013733 | -0.05951 | 0.009155 | -0.036622 | 0.25635 | 121.701 | 0.073242 | 121.6599 | 121.4447 | 121.4813 | 121.4218 | 121.4584 | -121.6324 | -121.6324 | 121.6782 | 121.637 | 61.1572 | 61.2671
785.5156 | 121.9482 | -61.1664 | 60.3973 | -0.12794 | 0.0054624 | 0.063687 | 0.060534 | -0.0061865 | -0.0081796 | -0.0053641 | -0.022247 | 0.0048833 | 0.063636 | 0.055173 | -0.014097 | 0.025912 | -0.010066 | 0.050354 | 60.1959 | -61.2259 | 60.5392 | -60.8734 | -61.322 | -61.2808 | 0.19226 | 60.228 | -61.203 | 60.4935 | -61.0703 | -61.1755 | -61.171 | -0.059509 | -0.20142 | 0.14191 | 0.29297 | -0.11444 | -0.15564 | -0.054932 | -0.09613 | -0.036621 | -0.16937 | 0.09613 | 0.096131 | -0.004577 | -0.009155 | 0.032044 | 0.027466 | 0.35248 | 121.7651 | 0.13275 | 121.6965 | 121.4218 | 121.431 | 121.3623 | 121.3943 | -121.6232 | -121.6003 | 121.7056 | 121.6599 | 61.2167 | 61.3586
787.2031 | 121.8246 | -61.2488 | 60.4202 | -0.036392 | 0.0046078 | 0.066464 | 0.061816 | 0.00043587 | -0.010743 | -0.00045074 | -0.10464 | 0.0038153 | 0.068122 | 0.052609 | -0.01367 | 0.024417 | -0.0021619 | -0.013733 | 60.2646 | -61.2442 | 60.3973 | -61.0565 | -61.4639 | -61.4365 | 0.032043 | 60.2829 | -61.2534 | 60.347 | -61.2305 | -61.3678 | -61.3266 | 0.004577 | -0.15564 | -0.022888 | 0.19226 | -0.18768 | -0.21515 | -0.19226 | -0.21973 | -0.004578 | -0.13733 | -0.073242 | 0.01831 | -0.07782 | -0.11902 | -0.073242 | -0.11444 | 0.18768 | 121.6415 | 0.022888 | 121.6003 | 121.5088 | 121.5363 | 121.5134 | 121.5317 | -121.6644 | -121.6736 | 121.6461 | 121.5958 | 61.235 | 61.2808
788.9688 | 121.8933 | -61.2534 | 60.347 | -0.089798 | 0.0046078 | 0.066892 | 0.058825 | -0.0025549 | -0.0088206 | 0.00019006 | -0.028351 | 0.0031745 | 0.06385 | 0.048764 | -0.013242 | 0.025058 | -0.0053661 | -0.086975 | 60.1822 | -61.2671 | 60.4385 | -61.0153 | -61.4456 | -61.4044 | 0.009155 | 60.173 | -61.2717 | 60.3882 | -61.1938 | -61.3083 | -61.2808 | -0.013733 | -0.16479 | 0.091553 | 0.23804 | -0.15106 | -0.19226 | -0.13733 | -0.17853 | -0.01831 | -0.17395 | 0.041199 | 0.059509 | -0.027466 | -0.054932 | -0.009156 | -0.036622 | 0.25177 | 121.7056 | 0.077819 | 121.6599 | 121.4493 | 121.4447 | 121.4355 | 121.4264 | -121.6141 | -121.6187 | 121.6919 | 121.6415 | 61.1664 | 61.2625
790.7188 | 121.8933 | -61.2167 | 60.3561 | -0.097427 | 0.0050352 | 0.066037 | 0.062457 | -0.0027685 | -0.008607 | -0.0038687 | -0.055817 | 0.0027471 | 0.067909 | 0.048764 | -0.013242 | 0.026126 | -0.0047253 | -0.082397 | 60.1776 | -61.2762 | 60.4294 | -61.0382 | -61.4594 | -61.3998 | 0.018311 | 60.1959 | -61.2854 | 60.3928 | -61.1984 | -61.2991 | -61.2762 | -0.059509 | -0.17853 | 0.073242 | 0.17853 | -0.18311 | -0.24262 | -0.1236 | -0.18311 | -0.068664 | -0.16022 | 0.036621 | 0.018311 | -0.059509 | -0.082397 | 0.009155 | -0.013733 | 0.23804 | 121.7056 | 0.086975 | 121.6782 | 121.4539 | 121.4813 | 121.3943 | 121.4127 | -121.6324 | -121.6415 | 121.6461 | 121.6095 | 61.1343 | 61.235
792.4062 | 121.9482 | -61.2808 | 60.2783 | -0.12794 | 0.0063168 | 0.066037 | 0.060534 | -0.00041873 | -0.0083932 | -0.0019461 | -0.083283 | 0.0044561 | 0.064918 | 0.053464 | -0.013242 | 0.027621 | -0.0062207 | -0.11444 | 60.1456 | -61.29 | 60.4202 | -61.0291 | -61.4868 | -61.4365 | -0.009155 | 60.1135 | -61.3266 | 60.4111 | -61.1893 | -61.322 | -61.2671 | -0.009155 | -0.13275 | 0.14191 | 0.25177 | -0.15564 | -0.20599 | -0.14648 | -0.19684 | -0.045776 | -0.16479 | 0.13275 | 0.091553 | 0.013733 | -0.041198 | 0.059509 | 0.004578 | 0.26093 | 121.7102 | 0.13733 | 121.7377 | 121.4355 | 121.4401 | 121.4264 | 121.3943 | -121.5683 | -121.6049 | 121.701 | 121.6919 | 61.1664 | 61.2717
794.1562 | 121.8658 | -61.2167 | 60.4111 | -0.13557 | 0.0052488 | 0.064115 | 0.06203 | -0.0025549 | -0.0088206 | -0.0017325 | -0.046661 | 0.0048833 | 0.064277 | 0.051541 | -0.013242 | 0.024417 | -0.0036573 | 0.054932 | 60.2051 | -61.235 | 60.5209 | -60.9238 | -61.3678 | -61.3266 | 0.15564 | 60.2234 | -61.235 | 60.434 | -61.1435 | -61.2579 | -61.2442 | -0.01831 | -0.20599 | 0.10986 | 0.29297 | -0.10986 | -0.15106 | -0.091553 | -0.13275 | -0.01831 | -0.18768 | 0.022888 | 0.073242 | -0.027466 | -0.041199 | -0.009156 | -0.022889 | 0.31128 | 121.756 | 0.091552 | 121.669 | 121.4401 | 121.4584 | 121.4218 | 121.4401 | -121.6461 | -121.6461 | 121.7377 | 121.6507 | 61.2717 | 61.3724
795.9062 | 121.8338 | -61.2259 | 60.4202 | -0.06691 | 0.0043942 | 0.063901 | 0.061389 | -0.0044775 | -0.007966 | -0.0034415 | -0.046661 | 0.0040289 | 0.066413 | 0.046414 | -0.01367 | 0.023776 | -2.571e-05 | 0.032043 | 60.2554 | -61.2579 | 60.4385 | -61.0153 | -61.4685 | -61.4273 | 0.054932 | 60.26 | -61.2579 | 60.3653 | -61.2213 | -61.3403 | -61.2991 | -0.032044 | -0.16479 | 0.018311 | 0.21057 | -0.20142 | -0.24262 | -0.16937 | -0.21057 | -0.032044 | -0.16022 | -0.054932 | 0.004578 | -0.073242 | -0.11444 | -0.041198 | -0.082397 | 0.24262 | 121.6965 | 0.036622 | 121.6232 | 121.5134 | 121.5179 | 121.4813 | 121.4859 | -121.6782 | -121.6782 | 121.6644 | 121.5912 | 61.2579 | 61.2808
797.5938 | 121.8979 | -61.3129 | 60.2829 | -0.12032 | 0.0071714 | 0.066037 | 0.064593 | -0.0025549 | -0.0066844 | -0.00023714 | -0.11075 | 0.0036017 | 0.064491 | 0.052395 | -0.011961 | 0.028262 | -0.0038709 | -0.20599 | 60.1822 | -61.3312 | 60.3104 | -61.1481 | -61.6013 | -61.5509 | -0.11444 | 60.1364 | -61.3312 | 60.3241 | -61.2717 | -61.3907 | -61.322 | -0.018311 | -0.10071 | 0.027466 | 0.16479 | -0.23804 | -0.28839 | -0.21973 | -0.27008 | -0.018311 | -0.14648 | 0.041199 | 0.041199 | -0.009155 | -0.07782 | 0.009156 | -0.059509 | 0.18311 | 121.6415 | 0.05951 | 121.6553 | 121.5134 | 121.4676 | 121.4951 | 121.4493 | -121.6141 | -121.6141 | 121.6232 | 121.637 | 61.1069 | 61.1984
799.3438 | 121.8704 | -61.2167 | 60.4019 | -0.12794 | 0.0069578 | 0.065183 | 0.060107 | -0.0051183 | -0.01053 | -0.00087794 | -0.037506 | 0.0016791 | 0.065772 | 0.053677 | -0.011533 | 0.024631 | -0.0068615 | 0.054932 | 60.2371 | -61.2167 | 60.4935 | -60.9421 | -61.3861 | -61.3449 | 0.13733 | 60.2463 | -61.2305 | 60.4019 | -61.171 | -61.29 | -61.2671 | 0 | -0.16479 | 0.091552 | 0.27466 | -0.12817 | -0.16937 | -0.12817 | -0.16937 | -0.013733 | -0.15564 | 0 | 0.045777 | -0.050354 | -0.073242 | -0.036621 | -0.059509 | 0.27466 | 121.7102 | 0.05951 | 121.6324 | 121.4539 | 121.4767 | 121.4539 | 121.463 | -121.6187 | -121.6324 | 121.7102 | 121.6187 | 61.2717 | 61.3541
801.0781 | 121.8613 | -61.2442 | 60.3836 | -0.10506 | 0.0037534 | 0.064328 | 0.062671 | 0.0010767 | -0.010316 | -0.0047231 | -0.09549 | 0.0055243 | 0.0662 | 0.050686 | -0.011533 | 0.025272 | -0.0034435 | -0.032043 | 60.2646 | -61.2534 | 60.3928 | -61.0657 | -61.4822 | -61.4502 | 0.009155 | 60.26 | -61.2808 | 60.3424 | -61.2259 | -61.3678 | -61.3266 | -0.009155 | -0.11902 | 0.009155 | 0.17853 | -0.20599 | -0.23804 | -0.19684 | -0.22888 | -0.036621 | -0.1236 | -0.041199 | 0.018311 | -0.082397 | -0.1236 | -0.045776 | -0.086975 | 0.18768 | 121.6461 | 0.054932 | 121.6232 | 121.5179 | 121.5408 | 121.5088 | 121.5042 | -121.637 | -121.6644 | 121.637 | 121.5866 | 61.2122 | 61.2534
802.8125 | 121.8155 | -61.3403 | 60.3195 | -0.12794 | 0.0069578 | 0.065396 | 0.06438 | -0.0019141 | -0.0094614 | -0.00066434 | -0.10464 | 0.0074469 | 0.065345 | 0.049832 | -0.012388 | 0.026126 | -0.0094251 | -0.19226 | 60.1959 | -61.3541 | 60.2966 | -61.171 | -61.615 | -61.5601 | -0.17395 | 60.2097 | -61.3403 | 60.2417 | -61.3586 | -61.5005 | -61.4182 | -0.013733 | -0.1236 | -0.022888 | 0.16937 | -0.21973 | -0.27466 | -0.20599 | -0.26093 | 0 | -0.10986 | -0.07782 | -0.018311 | -0.07782 | -0.16022 | -0.07782 | -0.16022 | 0.18311 | 121.6507 | -0.018311 | 121.582 | 121.55 | 121.55 | 121.5363 | 121.55 | -121.6736 | -121.6599 | 121.637 | 121.582 | 61.1481 | 61.1664
804.5625 | 121.8155 | -61.3129 | 60.3424 | -0.097427 | 0.0075986 | 0.066464 | 0.06502 | -0.00020513 | -0.0088206 | -0.0015189 | -0.10159 | 0.0050971 | 0.067054 | 0.058377 | -0.014097 | 0.02634 | -0.0028027 | -0.19226 | 60.1776 | -61.3449 | 60.3058 | -61.171 | -61.615 | -61.5692 | -0.15564 | 60.1822 | -61.3724 | 60.2509 | -61.3586 | -61.496 | -61.4136 | -0.032044 | -0.16479 | -0.036621 | 0.14191 | -0.25635 | -0.30212 | -0.2243 | -0.27008 | -0.059509 | -0.16022 | -0.091553 | -0.045777 | -0.10071 | -0.18311 | -0.041199 | -0.1236 | 0.17395 | 121.6507 | 0.013732 | 121.6232 | 121.5225 | 121.5546 | 121.4905 | 121.4951 | -121.6873 | -121.7148 | 121.6187 | 121.5637 | 61.1206 | 61.1572
806.2344 | 121.962 | -61.2762 | 60.2966 | -0.15846 | 0.0050352 | 0.064542 | 0.060534 | 8.47e-06 | -0.0064706 | -0.00066434 | -0.06192 | 0.0036017 | 0.067695 | 0.047055 | -0.012815 | 0.024417 | -0.0066479 | -0.12817 | 60.1639 | -61.29 | 60.4156 | -61.0245 | -61.4914 | -61.4365 | -0.013733 | 60.0815 | -61.3312 | 60.3928 | -61.2076 | -61.3266 | -61.2671 | -0.013733 | -0.13275 | 0.11902 | 0.25177 | -0.16022 | -0.21515 | -0.14648 | -0.20142 | -0.054932 | -0.21515 | 0.09613 | 0.068664 | 0.009155 | -0.050354 | 0.064087 | 0.004578 | 0.2655 | 121.7056 | 0.1236 | 121.7239 | 121.4539 | 121.4127 | 121.4401 | 121.3577 | -121.5866 | -121.6278 | 121.6919 | 121.669 | 61.1481 | 61.2625
807.9219 | 121.8613 | -61.2762 | 60.3424 | -0.06691 | 0.007385 | 0.066892 | 0.063311 | -0.0038367 | -0.0083932 | -0.0021597 | -0.086334 | 0.0055243 | 0.067054 | 0.0556 | -0.011747 | 0.02634 | -0.0045117 | -0.073242 | 60.1959 | -61.3037 | 60.3973 | -61.0519 | -61.496 | -61.4685 | 0.013733 | 60.1822 | -61.3129 | 60.3561 | -61.235 | -61.377 | -61.3312 | -0.027466 | -0.14648 | 0.054932 | 0.2243 | -0.19226 | -0.21973 | -0.16479 | -0.19226 | -0.036621 | -0.16022 | 0.013733 | 0.041199 | -0.054932 | -0.10071 | -0.018311 | -0.064087 | 0.25177 | 121.7011 | 0.07782 | 121.669 | 121.4996 | 121.4951 | 121.4722 | 121.4584 | -121.6461 | -121.6553 | 121.6736 | 121.6324 | 61.203 | 61.29
809.6719 | 121.843 | -61.2488 | 60.434 | -0.082169 | 0.005676 | 0.062619 | 0.062457 | -0.00020513 | -0.0081796 | -0.0047231 | -0.022247 | 0.0036017 | 0.064063 | 0.043637 | -0.012815 | 0.025058 | -0.0030163 | 0.036621 | 60.2554 | -61.2213 | 60.4385 | -60.997 | -61.4319 | -61.3998 | 0.082397 | 60.2554 | -61.235 | 60.3653 | -61.2076 | -61.3083 | -61.3129 | 0.027466 | -0.17853 | 0.004578 | 0.25177 | -0.15106 | -0.18311 | -0.17853 | -0.21057 | 0.013733 | -0.17853 | -0.068665 | 0.041198 | -0.064087 | -0.05951 | -0.07782 | -0.073243 | 0.2243 | 121.6599 | 0.027465 | 121.6003 | 121.4767 | 121.4905 | 121.5042 | 121.5042 | -121.6553 | -121.669 | 121.6873 | 121.6141 | 61.2854 | 61.3312
811.3438 | 121.8384 | -61.235 | 60.4294 | -0.089798 | 0.0037534 | 0.066251 | 0.05968 | -0.0031957 | -0.0083932 | -0.0030141 | -0.031403 | 0.0050971 | 0.066413 | 0.057522 | -0.011533 | 0.025058 | -0.0019483 | -0.027466 | 60.26 | -61.2671 | 60.379 | -61.0748 | -61.4868 | -61.4502 | 0.018311 | 60.2783 | -61.2946 | 60.347 | -61.2488 | -61.3586 | -61.322 | -0.032044 | -0.16937 | -0.050354 | 0.16022 | -0.21515 | -0.25177 | -0.1831 | -0.21973 | -0.05951 | -0.15106 | -0.082397 | -0.013733 | -0.086975 | -0.1236 | -0.027465 | -0.064087 | 0.19226 | 121.6461 | 0.045777 | 121.6415 | 121.5271 | 121.5729 | 121.4951 | 121.5134 | -121.6965 | -121.7239 | 121.6141 | 121.582 | 61.2076 | 61.2534
813.1094 | 121.9528 | -61.2808 | 60.26 | -0.1432 | 0.0075986 | 0.065396 | 0.062671 | 0.00064947 | -0.0090342 | -0.0019461 | -0.077179 | 0.0044561 | 0.065559 | 0.053036 | -0.014951 | 0.025485 | -0.0081433 | -0.16479 | 60.1547 | -61.3174 | 60.3928 | -61.0474 | -61.4868 | -61.4548 | -0.027466 | 60.1273 | -61.3174 | 60.4019 | -61.2122 | -61.3358 | -61.2717 | -0.036621 | -0.10529 | 0.13275 | 0.23346 | -0.17395 | -0.20599 | -0.13733 | -0.16937 | -0.036621 | -0.13275 | 0.14191 | 0.068665 | 0.009156 | -0.054931 | 0.045777 | -0.01831 | 0.27008 | 121.7102 | 0.10529 | 121.7194 | 121.4722 | 121.4447 | 121.4355 | 121.4081 | -121.5775 | -121.5775 | 121.6736 | 121.6827 | 61.116 | 61.2534
814.7969 | 121.9528 | -61.2625 | 60.2829 | -0.13557 | 0.0088804 | 0.066251 | 0.060321 | 8.47e-06 | -0.0088206 | -0.0019461 | -0.034454 | 0.0027471 | 0.067054 | 0.04855 | -0.013883 | 0.025912 | -0.0047253 | -0.13275 | 60.141 | -61.3083 | 60.4202 | -61.0382 | -61.4868 | -61.4502 | -0.018311 | 60.1089 | -61.3266 | 60.4019 | -61.1984 | -61.3083 | -61.2625 | -0.045777 | -0.14191 | 0.13733 | 0.2243 | -0.18768 | -0.2243 | -0.14191 | -0.17853 | -0.064087 | -0.17395 | 0.11902 | 0.064087 | 0 | -0.045777 | 0.064087 | 0.01831 | 0.27008 | 121.7285 | 0.12817 | 121.7285 | 121.4493 | 121.4355 | 121.4035 | 121.3715 | -121.5912 | -121.6095 | 121.6827 | 121.6644 | 61.1298 | 61.2442
816.5312 | 121.9116 | -61.2808 | 60.2966 | -0.082169 | 0.0093076 | 0.064328 | 0.064807 | -0.0017005 | -0.0090342 | -0.0055777 | -0.089386 | 0.0038153 | 0.068336 | 0.048337 | -0.011533 | 0.025699 | 0.00040169 | -0.21515 | 60.1913 | -61.3403 | 60.3195 | -61.1481 | -61.5921 | -61.5509 | -0.1236 | 60.1501 | -61.3678 | 60.3424 | -61.2854 | -61.3953 | -61.3312 | -0.059509 | -0.10529 | 0.022888 | 0.13275 | -0.27008 | -0.31128 | -0.21057 | -0.25177 | -0.086975 | -0.14648 | 0.045776 | -0.004577 | -0.050354 | -0.11444 | 0.036621 | -0.027466 | 0.19226 | 121.6599 | 0.082398 | 121.7102 | 121.5317 | 121.5179 | 121.4722 | 121.431 | -121.637 | -121.6644 | 121.6003 | 121.6232 | 61.0657 | 61.1572
818.2656 | 121.9574 | -61.2808 | 60.2875 | -0.10506 | 0.0075986 | 0.064969 | 0.063098 | 0.00043587 | -0.006257 | -0.00066434 | -0.068024 | 0.0031745 | 0.0662 | 0.057522 | -0.013456 | 0.025912 | -0.0079297 | -0.19684 | 60.1639 | -61.3541 | 60.3607 | -61.0886 | -61.5417 | -61.4868 | -0.041199 | 60.1181 | -61.3174 | 60.3928 | -61.2167 | -61.3312 | -61.2671 | -0.073242 | -0.1236 | 0.073242 | 0.19226 | -0.20599 | -0.26093 | -0.13275 | -0.18768 | -0.036621 | -0.16937 | 0.10529 | 0.064087 | 0.013733 | -0.050354 | 0.050354 | -0.013733 | 0.2655 | 121.7148 | 0.10071 | 121.7102 | 121.5179 | 121.4355 | 121.4447 | 121.3989 | -121.6415 | -121.6049 | 121.6415 | 121.6736 | 61.084 | 61.2396
820.0156 | 121.8704 | -61.3129 | 60.3104 | -0.13557 | 0.0067442 | 0.06561 | 0.060534 | -0.0025549 | -0.006898 | -0.00045074 | -0.089386 | 0.0061651 | 0.0662 | 0.05325 | -0.01367 | 0.024631 | -0.0038709 | -0.21973 | 60.1685 | -61.3632 | 60.2921 | -61.1618 | -61.6013 | -61.5463 | -0.15106 | 60.1639 | -61.3541 | 60.2966 | -61.3266 | -61.4685 | -61.3907 | -0.050354 | -0.14191 | -0.018311 | 0.15106 | -0.23346 | -0.28839 | -0.18311 | -0.23804 | -0.041199 | -0.14648 | -0.013733 | -0.013733 | -0.07782 | -0.15564 | -0.036621 | -0.11444 | 0.20142 | 121.6553 | 0.027466 | 121.6507 | 121.5317 | 121.5179 | 121.4813 | 121.4767 | -121.6736 | -121.6644 | 121.6049 | 121.6095 | 61.0931 | 61.1618
821.75 | 121.8979 | -61.2991 | 60.2921 | -0.12032 | 0.0075986 | 0.066251 | 0.062243 | 0.00043587 | -0.010102 | -0.0055777 | -0.10159 | 0.0044561 | 0.065559 | 0.063077 | -0.014524 | 0.025912 | -0.0021619 | -0.21515 | 60.1959 | -61.3266 | 60.3104 | -61.1389 | -61.5875 | -61.5372 | -0.14191 | 60.1593 | -61.3632 | 60.3241 | -61.29 | -61.4136 | -61.3541 | -0.027466 | -0.09613 | 0.018311 | 0.16022 | -0.23804 | -0.28839 | -0.21057 | -0.26093 | -0.064087 | -0.13275 | 0.032044 | 0.009155 | -0.054932 | -0.11444 | 0.009155 | -0.050354 | 0.18768 | 121.637 | 0.073242 | 121.6873 | 121.5225 | 121.5225 | 121.4951 | 121.4584 | -121.6187 | -121.6553 | 121.6095 | 121.6232 | 61.084 | 61.1572
823.4844 | 121.9345 | -61.2213 | 60.3745 | -0.089798 | 0.0061032 | 0.06561 | 0.059466 | -0.0021277 | -0.0081796 | -0.0051505 | 0.0052185 | 0.0040289 | 0.066627 | 0.044491 | -0.013242 | 0.023776 | -0.0060071 | -0.082397 | 60.2005 | -61.2442 | 60.4248 | -61.0153 | -61.4548 | -61.409 | 0.009155 | 60.1685 | -61.2854 | 60.3973 | -61.1893 | -61.3037 | -61.2579 | -0.022889 | -0.17395 | 0.050354 | 0.20599 | -0.18768 | -0.23346 | -0.16479 | -0.21057 | -0.064087 | -0.20599 | 0.022888 | 0.032043 | -0.036622 | -0.082398 | 0.027465 | -0.018311 | 0.22888 | 121.669 | 0.09613 | 121.6827 | 121.4447 | 121.4539 | 121.4218 | 121.3898 | -121.6187 | -121.6599 | 121.6461 | 121.6187 | 61.1389 | 61.2305
825.2344 | 121.8704 | -61.2625 | 60.3928 | -0.089798 | 0.0061032 | 0.063474 | 0.060748 | -0.0025549 | -0.010957 | -0.0015189 | -0.071076 | 0.0044561 | 0.064918 | 0.049832 | -0.013029 | 0.024844 | -0.0038709 | -0.036621 | 60.2646 | -61.2671 | 60.3882 | -61.0748 | -61.4731 | -61.4502 | 0.009155 | 60.2188 | -61.2808 | 60.3516 | -61.2396 | -61.3815 | -61.3174 | -0.004578 | -0.12817 | -0.004577 | 0.18768 | -0.18768 | -0.21057 | -0.1831 | -0.20599 | -0.018311 | -0.17395 | -0.041199 | 0.022888 | -0.054932 | -0.11902 | -0.036621 | -0.10071 | 0.19226 | 121.6553 | 0.041199 | 121.6324 | 121.5317 | 121.4996 | 121.5271 | 121.4813 | -121.6599 | -121.6736 | 121.6507 | 121.6141 | 61.2259 | 61.2717
826.9219 | 121.9116 | -61.2442 | 60.347 | -0.17372 | 0.0063168 | 0.066678 | 0.058825 | 0.0023585 | -0.006898 | -0.0028005 | -0.016144 | 0.0050971 | 0.063636 | 0.051327 | -0.013883 | 0.025272 | -0.0034435 | -0.11902 | 60.141 | -61.2991 | 60.4202 | -60.9924 | -61.4548 | -61.4044 | 0.041199 | 60.1227 | -61.2946 | 60.3928 | -61.1893 | -61.3083 | -61.2579 | -0.054931 | -0.20599 | 0.073242 | 0.25177 | -0.16022 | -0.21057 | -0.10529 | -0.15564 | -0.050354 | -0.2243 | 0.045776 | 0.054932 | -0.013733 | -0.064087 | 0.036621 | -0.013733 | 0.3067 | 121.7194 | 0.10529 | 121.6873 | 121.4401 | 121.4172 | 121.3852 | 121.3669 | -121.6461 | -121.6415 | 121.6644 | 121.637 | 61.1252 | 61.2854
828.6562 | 121.8979 | -61.2167 | 60.3882 | -0.1432 | 0.0061032 | 0.063901 | 0.058825 | -0.0040503 | -0.010102 | -0.0032277 | -0.01004 | 0.0050971 | 0.068336 | 0.047055 | -0.01367 | 0.025058 | -0.0023755 | -0.091553 | 60.1822 | -61.2671 | 60.434 | -61.0153 | -61.4731 | -61.3861 | 0.022888 | 60.1868 | -61.2534 | 60.3745 | -61.1984 | -61.29 | -61.2625 | -0.050354 | -0.20599 | 0.045776 | 0.20142 | -0.16937 | -0.25635 | -0.11902 | -0.20599 | -0.036621 | -0.20142 | -0.013733 | 0.018311 | -0.045776 | -0.073242 | -0.009155 | -0.036621 | 0.25177 | 121.7011 | 0.054932 | 121.6278 | 121.4493 | 121.4401 | 121.3989 | 121.4035 | -121.6553 | -121.6415 | 121.6507 | 121.5912 | 61.1252 | 61.2396
830.4062 | 121.9299 | -61.29 | 60.2875 | -0.13557 | 0.0069578 | 0.066251 | 0.062457 | -0.0010595 | -0.006257 | -0.0053641 | -0.068024 | 0.0046697 | 0.065559 | 0.052609 | -0.013456 | 0.026981 | -0.0077161 | -0.21057 | 60.1639 | -61.3495 | 60.3333 | -61.1114 | -61.5738 | -61.5234 | -0.073242 | 60.141 | -61.3586 | 60.3653 | -61.2305 | -61.3632 | -61.3037 | -0.059509 | -0.1236 | 0.045776 | 0.17853 | -0.23346 | -0.28381 | -0.17395 | -0.2243 | -0.068665 | -0.14648 | 0.077819 | 0.059509 | -0.013733 | -0.073242 | 0.054932 | -0.004577 | 0.23804 | 121.6827 | 0.12817 | 121.7239 | 121.5134 | 121.4996 | 121.4539 | 121.431 | -121.637 | -121.6461 | 121.6232 | 121.6553 | 61.0794 | 61.2167
832.1562 | 121.962 | -61.2946 | 60.2875 | -0.097427 | 0.007385 | 0.068387 | 0.062671 | -0.0019141 | -0.0088206 | -0.0017325 | -0.06192 | 0.0029607 | 0.06385 | 0.0462 | -0.014738 | 0.024631 | -0.0023755 | -0.13275 | 60.1547 | -61.2991 | 60.4156 | -61.0336 | -61.4914 | -61.4365 | 0.009155 | 60.1273 | -61.3449 | 60.3973 | -61.2122 | -61.3312 | -61.2717 | -0.004577 | -0.13275 | 0.12817 | 0.26093 | -0.14191 | -0.19684 | -0.13733 | -0.19226 | -0.050354 | -0.16022 | 0.10986 | 0.082398 | 0.022889 | -0.036621 | 0.073243 | 0.013733 | 0.2655 | 121.7148 | 0.13275 | 121.7422 | 121.4539 | 121.4722 | 121.4493 | 121.4218 | -121.5866 | -121.6324 | 121.7102 | 121.6919 | 61.1618 | 61.3037
833.8438 | 121.8475 | -61.29 | 60.3333 | -0.097427 | 0.0075986 | 0.068601 | 0.063098 | 0.0029993 | -0.007966 | -0.0042959 | -0.11685 | 0.0063787 | 0.067481 | 0.055386 | -0.012815 | 0.028476 | -0.0066479 | -0.086975 | 60.2234 | -61.2991 | 60.3836 | -61.0519 | -61.528 | -61.4777 | -0.018311 | 60.1822 | -61.3174 | 60.3287 | -61.2717 | -61.4182 | -61.3678 | -0.009155 | -0.10986 | 0.050354 | 0.23804 | -0.18768 | -0.23804 | -0.17853 | -0.22888 | -0.027466 | -0.15106 | -0.004578 | 0.018311 | -0.07782 | -0.12817 | -0.050354 | -0.10071 | 0.24719 | 121.6827 | 0.045777 | 121.6461 | 121.5225 | 121.4996 | 121.5134 | 121.4722 | -121.6324 | -121.6507 | 121.6736 | 121.6187 | 61.203 | 61.2717
835.5938 | 121.8292 | -61.2167 | 60.4385 | -0.089798 | 0.0063168 | 0.064969 | 0.059039 | -0.00084593 | -0.01053 | -0.0013051 | -0.022247 | 0.0040289 | 0.068122 | 0.054318 | -0.013029 | 0.024631 | -0.0021619 | -0.004578 | 60.2463 | -61.2534 | 60.4019 | -61.0428 | -61.4639 | -61.4365 | 0.045776 | 60.2646 | -61.2488 | 60.3607 | -61.2122 | -61.3266 | -61.322 | -0.036621 | -0.19226 | -0.036621 | 0.17395 | -0.21973 | -0.24719 | -0.1831 | -0.21057 | -0.032043 | -0.17395 | -0.07782 | 0.004578 | -0.10529 | -0.10986 | -0.073242 | -0.07782 | 0.21057 | 121.6553 | 0.036621 | 121.6095 | 121.4996 | 121.5134 | 121.463 | 121.4813 | -121.6919 | -121.6873 | 121.6187 | 121.5775 | 61.2122 | 61.2625
837.3281 | 121.8933 | -61.2625 | 60.3424 | -0.12794 | 0.0067442 | 0.06326 | 0.063311 | -0.00084593 | -0.01053 | -0.0015189 | -0.077179 | 0.0065923 | 0.066413 | 0.055173 | -0.010893 | 0.024417 | -0.0017347 | -0.086975 | 60.1959 | -61.3083 | 60.3882 | -61.0657 | -61.5005 | -61.4822 | 0.013733 | 60.1868 | -61.3083 | 60.3561 | -61.2442 | -61.3724 | -61.3312 | -0.045777 | -0.14648 | 0.045777 | 0.19684 | -0.21973 | -0.23804 | -0.17395 | -0.19226 | -0.045777 | -0.15564 | 0.013733 | 0.01831 | -0.068665 | -0.10986 | -0.022888 | -0.064086 | 0.24262 | 121.6965 | 0.064087 | 121.6644 | 121.5042 | 121.4951 | 121.4584 | 121.4493 | -121.6507 | -121.6507 | 121.6507 | 121.6187 | 61.1755 | 61.2762
839.0781 | 121.907 | -61.2534 | 60.3424 | -0.12032 | 0.0063168 | 0.064969 | 0.060321 | -0.0064001 | -0.0073252 | -0.0023733 | -0.01004 | 0.0040289 | 0.066627 | 0.050686 | -0.011747 | 0.025912 | -0.0049389 | -0.12817 | 60.1318 | -61.29 | 60.4202 | -61.0062 | -61.4731 | -61.3998 | 0.027466 | 60.1959 | -61.2808 | 60.3882 | -61.2076 | -61.3083 | -61.2671 | -0.036621 | -0.21057 | 0.07782 | 0.24719 | -0.14648 | -0.21973 | -0.10986 | -0.18311 | -0.027466 | -0.14648 | 0.045777 | 0.045776 | -0.013733 | -0.054932 | 0.013733 | -0.027466 | 0.28381 | 121.7102 | 0.073242 | 121.669 | 121.4218 | 121.4767 | 121.3852 | 121.4493 | -121.6324 | -121.6232 | 121.6736 | 121.6415 | 61.1252 | 61.2808
840.7656 | 121.9116 | -61.2167 | 60.3607 | -0.074539 | 0.0037534 | 0.06561 | 0.060534 | -0.0036231 | -0.0071116 | -0.00087794 | 0.0082703 | 0.0021063 | 0.064704 | 0.050046 | -0.012388 | 0.025058 | -0.0010937 | -0.07782 | 60.2142 | -61.2579 | 60.4202 | -61.0107 | -61.4639 | -61.3953 | 0.041199 | 60.173 | -61.2442 | 60.3973 | -61.1755 | -61.2808 | -61.2488 | -0.041199 | -0.14648 | 0.059509 | 0.20599 | -0.17853 | -0.24719 | -0.13733 | -0.20599 | -0.027466 | -0.18768 | 0.036621 | 0.041199 | -0.032043 | -0.064087 | -0.004577 | -0.036621 | 0.24719 | 121.6782 | 0.068665 | 121.6415 | 121.4722 | 121.4172 | 121.431 | 121.3898 | -121.6187 | -121.6049 | 121.637 | 121.6141 | 61.1389 | 61.2579
842.5156 | 121.9437 | -61.1984 | 60.4065 | -0.13557 | 0.0041806 | 0.064115 | 0.061175 | -0.0040503 | -0.01053 | -0.0047231 | -0.019196 | 0.0038153 | 0.06385 | 0.057309 | -0.013456 | 0.02399 | -0.0036573 | 0.073242 | 60.228 | -61.2076 | 60.5347 | -60.91 | -61.3586 | -61.3083 | 0.19226 | 60.2051 | -61.2213 | 60.4706 | -61.0977 | -61.2167 | -61.1984 | -0.009156 | -0.17853 | 0.12817 | 0.28839 | -0.10986 | -0.16022 | -0.10071 | -0.15106 | -0.022888 | -0.20142 | 0.064087 | 0.10071 | 0 | -0.018311 | 0.022888 | 0.004577 | 0.29755 | 121.7422 | 0.1236 | 121.6919 | 121.4355 | 121.4264 | 121.4264 | 121.4035 | -121.6141 | -121.6278 | 121.7331 | 121.669 | 61.2717 | 61.3907
844.2656 | 121.8704 | -61.3174 | 60.3287 | -0.16609 | 0.0058896 | 0.064969 | 0.063739 | -0.0023413 | -0.01117 | -0.0040823 | -0.089386 | 0.0042425 | 0.065345 | 0.05859 | -0.01367 | 0.02634 | -0.0038709 | -0.2243 | 60.173 | -61.3586 | 60.3012 | -61.171 | -61.6104 | -61.5463 | -0.14648 | 60.1685 | -61.3403 | 60.3058 | -61.322 | -61.4502 | -61.3815 | -0.041199 | -0.15564 | -0.027466 | 0.14648 | -0.22888 | -0.29297 | -0.18768 | -0.25177 | -0.022888 | -0.16022 | -0.022888 | -0.004577 | -0.064087 | -0.13275 | -0.041199 | -0.10986 | 0.18768 | 121.6599 | 0.018311 | 121.6461 | 121.5317 | 121.5088 | 121.4905 | 121.4859 | -121.6873 | -121.669 | 121.6187 | 121.6232 | 61.0931 | 61.171
845.9531 | 121.9803 | -61.1893 | 60.3745 | -0.12032 | 0.0061032 | 0.06326 | 0.061175 | -0.00063233 | -0.012239 | -0.0049367 | 0.023529 | 0.0042425 | 0.066413 | 0.047268 | -0.014097 | 0.025912 | -0.0066479 | 0.004578 | 60.2051 | -61.2213 | 60.5118 | -60.9238 | -61.3403 | -61.3266 | 0.17853 | 60.2234 | -61.2167 | 60.4797 | -61.084 | -61.1984 | -61.1938 | -0.032043 | -0.16937 | 0.13733 | 0.2655 | -0.13733 | -0.15106 | -0.10529 | -0.11902 | -0.027466 | -0.15106 | 0.10529 | 0.10529 | -0.004578 | -0.009155 | 0.022888 | 0.018311 | 0.29755 | 121.7331 | 0.13275 | 121.6965 | 121.4264 | 121.4401 | 121.3943 | 121.4127 | -121.5958 | -121.5912 | 121.7011 | 121.669 | 61.1938 | 61.3678
847.7031 | 121.8475 | -61.3037 | 60.3378 | -0.17372 | 0.0075986 | 0.06561 | 0.061389 | -0.00063233 | -0.006257 | -0.0015189 | -0.092438 | 0.0055243 | 0.065986 | 0.054959 | -0.014097 | 0.025699 | 0.0012561 | -0.22888 | 60.1913 | -61.3495 | 60.2829 | -61.1893 | -61.6333 | -61.5692 | -0.16937 | 60.1639 | -61.3678 | 60.2921 | -61.3358 | -61.4685 | -61.3907 | -0.045776 | -0.14648 | -0.054932 | 0.11444 | -0.2655 | -0.32959 | -0.21973 | -0.28381 | -0.064087 | -0.17395 | -0.045777 | -0.032043 | -0.086975 | -0.16479 | -0.022888 | -0.10071 | 0.16022 | 121.6324 | 0.032044 | 121.6599 | 121.5408 | 121.5317 | 121.4951 | 121.4676 | -121.6873 | -121.7056 | 121.5866 | 121.5958 | 61.0748 | 61.1343
849.4531 | 121.8338 | -61.3312 | 60.3378 | -0.10506 | 0.0075986 | 0.065824 | 0.06438 | 0.0015039 | -0.010102 | -0.0023733 | -0.098541 | 0.0042425 | 0.063423 | 0.057095 | -0.012602 | 0.027408 | -0.0028027 | -0.17853 | 60.1913 | -61.3129 | 60.3058 | -61.171 | -61.6058 | -61.5601 | -0.14648 | 60.1685 | -61.3541 | 60.2692 | -61.3495 | -61.4685 | -61.3861 | 0.018311 | -0.14648 | -0.032044 | 0.16022 | -0.22888 | -0.27466 | -0.24719 | -0.29297 | -0.022888 | -0.16937 | -0.068665 | -0.01831 | -0.054931 | -0.13733 | -0.032043 | -0.11444 | 0.14191 | 121.6187 | 0.004578 | 121.6232 | 121.5042 | 121.5225 | 121.5225 | 121.4996 | -121.6507 | -121.6919 | 121.637 | 121.6003 | 61.1526 | 61.1847
851.2188 | 121.8796 | -61.2534 | 60.3607 | -0.082169 | 0.0058896 | 0.066037 | 0.063952 | -0.0019141 | -0.0098886 | -0.00087794 | -0.058869 | 0.0048833 | 0.065345 | 0.054745 | -0.012602 | 0.024631 | -0.0089977 | -0.041199 | 60.2692 | -61.2762 | 60.3928 | -61.0794 | -61.5051 | -61.4731 | 0.013733 | 60.2188 | -61.3129 | 60.347 | -61.235 | -61.3495 | -61.2991 | -0.022888 | -0.091553 | 0.032043 | 0.17395 | -0.21973 | -0.25177 | -0.19684 | -0.22888 | -0.059509 | -0.14191 | -0.013733 | 0.018311 | -0.045776 | -0.09613 | 0.013733 | -0.036621 | 0.19684 | 121.669 | 0.07782 | 121.6599 | 121.5454 | 121.5317 | 121.5225 | 121.4722 | -121.637 | -121.6736 | 121.6461 | 121.6003 | 61.2122 | 61.2671
852.9688 | 121.9437 | -61.2488 | 60.2829 | -0.1432 | 0.0078122 | 0.065396 | 0.061175 | -0.0017005 | -0.0092478 | -0.0013051 | -0.049713 | 0.0050971 | 0.063636 | 0.052395 | -0.013456 | 0.02634 | -0.0045117 | -0.12817 | 60.1273 | -61.2946 | 60.4248 | -61.0062 | -61.4777 | -61.4227 | 0.022888 | 60.1364 | -61.322 | 60.3973 | -61.1984 | -61.3083 | -61.2579 | -0.045777 | -0.15564 | 0.14191 | 0.24261 | -0.17395 | -0.22888 | -0.12817 | -0.1831 | -0.073242 | -0.14648 | 0.11444 | 0.050354 | -0.009156 | -0.05951 | 0.064086 | 0.013732 | 0.28839 | 121.7194 | 0.1236 | 121.7194 | 121.4218 | 121.4584 | 121.376 | 121.3852 | -121.5775 | -121.6049 | 121.6736 | 121.6461 | 61.1206 | 61.2717
854.6406 | 121.8704 | -61.2534 | 60.3699 | -0.044022 | 0.0061032 | 0.066678 | 0.062457 | 0.0015039 | -0.0090342 | -0.0010915 | -0.049713 | 0.0044561 | 0.067054 | 0.048764 | -0.011533 | 0.026981 | -0.0049389 | -0.041199 | 60.2325 | -61.2534 | 60.4019 | -61.0657 | -61.4822 | -61.4594 | -0.004578 | 60.2097 | -61.2854 | 60.3516 | -61.2213 | -61.3632 | -61.322 | 0 | -0.13733 | 0.032044 | 0.18768 | -0.20599 | -0.22888 | -0.20599 | -0.22888 | -0.032043 | -0.16022 | -0.018311 | 0.032044 | -0.068664 | -0.10986 | -0.036621 | -0.07782 | 0.18768 | 121.6553 | 0.064087 | 121.637 | 121.4859 | 121.4951 | 121.4859 | 121.463 | -121.6232 | -121.6553 | 121.6553 | 121.6049 | 61.2122 | 61.2488
856.3906 | 121.9299 | -61.2076 | 60.4202 | -0.06691 | 0.0048214 | 0.064542 | 0.061175 | 0.0015039 | -0.010316 | -0.0023733 | -0.022247 | 0.0025335 | 0.066413 | 0.056027 | -0.013242 | 0.025058 | -0.0030163 | 0.045776 | 60.2417 | -61.203 | 60.5072 | -60.9283 | -61.3632 | -61.3266 | 0.17395 | 60.2234 | -61.2717 | 60.4523 | -61.0977 | -61.203 | -61.1984 | 0.004578 | -0.17853 | 0.086975 | 0.27924 | -0.11902 | -0.15564 | -0.1236 | -0.16022 | -0.064086 | -0.19684 | 0.032044 | 0.10986 | 0.009156 | 0.004578 | 0.073242 | 0.068664 | 0.27466 | 121.7102 | 0.17395 | 121.7239 | 121.4447 | 121.4951 | 121.4493 | 121.431 | -121.6232 | -121.6919 | 121.7148 | 121.6599 | 61.2534 | 61.3815
858.1406 | 121.8796 | -61.2671 | 60.3928 | -0.089798 | 0.0033262 | 0.066464 | 0.063952 | -0.0017005 | -0.010102 | -0.0017325 | -0.086334 | 0.0048833 | 0.065559 | 0.056881 | -0.013883 | 0.027621 | -0.0030163 | -0.050354 | 60.2463 | -61.29 | 60.3973 | -61.0794 | -61.496 | -61.4594 | 0.013733 | 60.2234 | -61.29 | 60.3561 | -61.203 | -61.3449 | -61.3129 | -0.022888 | -0.14648 | 0.004578 | 0.18768 | -0.19226 | -0.22888 | -0.16937 | -0.20599 | -0.022888 | -0.16937 | -0.036621 | 0.064087 | -0.045776 | -0.07782 | -0.022888 | -0.054932 | 0.21057 | 121.6873 | 0.086975 | 121.6461 | 121.5363 | 121.5134 | 121.5134 | 121.4905 | -121.6827 | -121.6827 | 121.6644 | 121.6232 | 61.2167 | 61.2808
859.8281 | 121.962 | -61.1984 | 60.3882 | -0.12794 | 0.007385 | 0.063474 | 0.057544 | -0.0031957 | -0.007966 | -0.00066434 | -0.019196 | 0.0044561 | 0.065559 | 0.048977 | -0.01132 | 0.025912 | -0.0064343 | -0.045776 | 60.2188 | -61.235 | 60.434 | -60.997 | -61.4365 | -61.3861 | 0.09613 | 60.2142 | -61.2671 | 60.4614 | -61.1206 | -61.203 | -61.2076 | -0.036621 | -0.16937 | 0.045776 | 0.20142 | -0.18768 | -0.23804 | -0.15106 | -0.20142 | -0.068665 | -0.17395 | 0.073242 | 0.07782 | -0.009156 | -0.004578 | 0.059509 | 0.064087 | 0.23804 | 121.669 | 0.14649 | 121.7285 | 121.4539 | 121.4813 | 121.4172 | 121.4127 | -121.6232 | -121.6553 | 121.6324 | 121.6599 | 61.1526 | 61.2946
861.5781 | 121.8246 | -61.2213 | 60.4202 | -0.082169 | 0.0054624 | 0.064542 | 0.061816 | -0.0057593 | -0.0090342 | -0.0021597 | -0.046661 | 0.0048833 | 0.0662 | 0.056241 | -0.014311 | 0.025272 | -0.0030163 | -0.032043 | 60.2875 | -61.2442 | 60.3973 | -61.0519 | -61.4777 | -61.4273 | 0.054932 | 60.2783 | -61.2625 | 60.3561 | -61.2213 | -61.3495 | -61.2991 | -0.022889 | -0.13275 | -0.022888 | 0.16937 | -0.20599 | -0.25635 | -0.1831 | -0.23346 | -0.041199 | -0.14191 | -0.064087 | 0 | -0.07782 | -0.12817 | -0.036621 | -0.086975 | 0.19226 | 121.6415 | 0.041199 | 121.6187 | 121.5317 | 121.5408 | 121.5088 | 121.4996 | -121.6644 | -121.6827 | 121.6187 | 121.5775 | 61.1893 | 61.2762
863.3125 | 121.9437 | -61.1755 | 60.3745 | -0.06691 | 0.0037534 | 0.063474 | 0.05968 | -0.0012731 | -0.0077524 | -0.0025869 | -0.0069885 | 0.0042425 | 0.064277 | 0.050259 | -0.012815 | 0.025485 | -0.0064343 | 0.050354 | 60.2188 | -61.2122 | 60.5347 | -60.8917 | -61.322 | -61.3083 | 0.18768 | 60.2371 | -61.203 | 60.4752 | -61.0931 | -61.1938 | -61.1801 | -0.036621 | -0.15564 | 0.16022 | 0.28381 | -0.13275 | -0.14648 | -0.096131 | -0.10986 | -0.027466 | -0.13733 | 0.10071 | 0.082397 | -0.004578 | -0.018311 | 0.022888 | 0.009155 | 0.32043 | 121.7468 | 0.10986 | 121.6782 | 121.431 | 121.4401 | 121.3943 | 121.4127 | -121.5866 | -121.5775 | 121.7102 | 121.6507 | 61.2259 | 61.3632
865.0781 | 121.843 | -61.235 | 60.4019 | -0.028763 | 0.0048214 | 0.063047 | 0.060748 | -0.00020513 | -0.0071116 | -0.0034415 | -0.049713 | 0.0038153 | 0.065772 | 0.050686 | -0.014524 | 0.025485 | -0.0023755 | -0.022888 | 60.2646 | -61.2579 | 60.3882 | -61.0657 | -61.4731 | -61.4319 | 0.041199 | 60.2783 | -61.2671 | 60.3607 | -61.2442 | -61.3495 | -61.3174 | -0.022889 | -0.13733 | -0.013733 | 0.16937 | -0.19684 | -0.23804 | -0.17395 | -0.21515 | -0.032044 | -0.1236 | -0.041199 | -0.009156 | -0.082398 | -0.11444 | -0.050354 | -0.082397 | 0.19226 | 121.6461 | 0.022888 | 121.6278 | 121.5225 | 121.5454 | 121.4996 | 121.5134 | -121.6599 | -121.669 | 121.6232 | 121.5958 | 61.2122 | 61.2762
866.75 | 121.9574 | -61.203 | 60.3745 | -0.10506 | 0.0046078 | 0.064542 | 0.063952 | -0.0021277 | -0.010957 | -0.0021597 | 0.017425 | 0.0036017 | 0.064491 | 0.047482 | -0.012815 | 0.026767 | -0.0057935 | -0.041199 | 60.2188 | -61.2305 | 60.4477 | -61.0016 | -61.4136 | -61.3724 | 0.10071 | 60.2142 | -61.2579 | 60.4797 | -61.1206 | -61.203 | -61.1847 | -0.027466 | -0.15564 | 0.073242 | 0.20142 | -0.16937 | -0.21057 | -0.14191 | -0.1831 | -0.054932 | -0.16022 | 0.10529 | 0.082398 | 0.018311 | 0 | 0.073243 | 0.054932 | 0.22888 | 121.6782 | 0.13733 | 121.7377 | 121.4493 | 121.4722 | 121.4218 | 121.4172 | -121.6049 | -121.6324 | 121.6507 | 121.6827 | 61.1618 | 61.3037
868.5 | 121.875 | -61.2534 | 60.3745 | -0.11269 | 0.0043942 | 0.065396 | 0.062671 | -0.00063233 | -0.009675 | -0.0015189 | -0.10159 | 0.0061651 | 0.066627 | 0.058163 | -0.014311 | 0.025912 | -0.0030163 | -0.054932 | 60.2005 | -61.2854 | 60.4111 | -61.0657 | -61.5051 | -61.4639 | 0.036621 | 60.2005 | -61.3037 | 60.3561 | -61.2396 | -61.3724 | -61.322 | -0.032043 | -0.17395 | 0.036621 | 0.18768 | -0.21057 | -0.25177 | -0.17853 | -0.21973 | -0.050354 | -0.17395 | -0.018311 | 0.013733 | -0.068664 | -0.11902 | -0.01831 | -0.068664 | 0.21973 | 121.6965 | 0.064087 | 121.6599 | 121.4859 | 121.5042 | 121.4539 | 121.4539 | -121.6599 | -121.6782 | 121.6644 | 121.6095 | 61.1984 | 61.29
870.2656 | 121.9574 | -61.1847 | 60.3745 | -0.1432 | 0.0028988 | 0.066037 | 0.059466 | -0.0049047 | -0.0081796 | -0.0032277 | 0.011322 | 0.0029607 | 0.065132 | 0.046841 | -0.011533 | 0.025485 | -0.0028027 | 0.018311 | 60.2371 | -61.2259 | 60.5255 | -60.9146 | -61.3541 | -61.3129 | 0.1831 | 60.2005 | -61.2259 | 60.4706 | -61.0748 | -61.1893 | -61.1938 | -0.041199 | -0.13733 | 0.15106 | 0.27008 | -0.12817 | -0.16937 | -0.086975 | -0.12817 | -0.041199 | -0.17395 | 0.09613 | 0.10986 | -0.009156 | -0.004578 | 0.032043 | 0.036621 | 0.31128 | 121.7514 | 0.15106 | 121.6965 | 121.463 | 121.4264 | 121.4218 | 121.3852 | -121.6003 | -121.6003 | 121.7102 | 121.6553 | 61.203 | 61.3678
871.9531 | 121.8887 | -61.2854 | 60.347 | -0.11269 | 0.0080258 | 0.064328 | 0.061602 | -0.0010595 | -0.0092478 | -0.0032277 | -0.09549 | 0.0061651 | 0.066841 | 0.056241 | -0.014311 | 0.028476 | -0.0045117 | -0.059509 | 60.2463 | -61.2854 | 60.4065 | -61.0474 | -61.5051 | -61.4685 | 0.027466 | 60.2005 | -61.2991 | 60.3607 | -61.235 | -61.3586 | -61.3037 | 0 | -0.10071 | 0.059509 | 0.23804 | -0.18311 | -0.21973 | -0.18311 | -0.21973 | -0.013733 | -0.14648 | 0.013733 | 0.050354 | -0.018311 | -0.073243 | -0.004578 | -0.05951 | 0.23804 | 121.6919 | 0.064087 | 121.6599 | 121.5317 | 121.4996 | 121.5317 | 121.4859 | -121.6324 | -121.6461 | 121.6919 | 121.6461 | 61.2259 | 61.3129
873.7031 | 121.9711 | -61.2808 | 60.2875 | -0.11269 | 0.009094 | 0.069669 | 0.062243 | -0.0019141 | -0.0083932 | -0.0053641 | -0.055817 | 0.0038153 | 0.066841 | 0.049405 | -0.013242 | 0.027194 | -0.0028027 | -0.16022 | 60.1593 | -61.3174 | 60.4065 | -61.0245 | -61.496 | -61.4639 | -0.013733 | 60.1364 | -61.3358 | 60.4065 | -61.203 | -61.3358 | -61.2625 | -0.036621 | -0.12817 | 0.11902 | 0.25635 | -0.18311 | -0.21515 | -0.14648 | -0.17853 | -0.054931 | -0.15106 | 0.11902 | 0.07782 | 0.018311 | -0.054931 | 0.073242 | 0 | 0.29297 | 121.7239 | 0.13275 | 121.7422 | 121.4767 | 121.4722 | 121.4401 | 121.4172 | -121.6049 | -121.6232 | 121.6873 | 121.6873 | 61.1206 | 61.2671
875.4531 | 121.8384 | -61.203 | 60.4294 | -0.082169 | 0.0031126 | 0.064115 | 0.060962 | -0.0031957 | -0.012025 | -0.0030141 | -0.037506 | 0.0040289 | 0.065132 | 0.052609 | -0.013242 | 0.024844 | -0.00023931 | -0.032043 | 60.2509 | -61.2534 | 60.4065 | -61.0474 | -61.4639 | -61.4136 | 0.054932 | 60.2554 | -61.2488 | 60.3561 | -61.2167 | -61.3403 | -61.3083 | -0.050354 | -0.17853 | -0.022888 | 0.15564 | -0.21057 | -0.26093 | -0.16022 | -0.21057 | -0.045776 | -0.17395 | -0.073242 | -0.013733 | -0.10529 | -0.13733 | -0.05951 | -0.091553 | 0.20599 | 121.6599 | 0.032043 | 121.6049 | 121.5042 | 121.5042 | 121.4539 | 121.4584 | -121.6827 | -121.6782 | 121.6095 | 121.5591 | 61.171 | 61.2579
877.2031 | 121.9803 | -61.1847 | 60.3928 | -0.10506 | 0.0050352 | 0.063901 | 0.058612 | -0.00084593 | -0.0098886 | -0.0042959 | -0.0008851 | 0.0050971 | 0.066413 | 0.051541 | -0.013456 | 0.026126 | -0.0042981 | 0.027466 | 60.2325 | -61.2122 | 60.5118 | -60.91 | -61.3449 | -61.3129 | 0.19226 | 60.2097 | -61.2259 | 60.498 | -61.0657 | -61.1618 | -61.171 | -0.027466 | -0.16022 | 0.11902 | 0.27466 | -0.12817 | -0.16022 | -0.10071 | -0.13275 | -0.041199 | -0.1831 | 0.10529 | 0.11902 | 0.013733 | 0.022888 | 0.054932 | 0.064087 | 0.30212 | 121.7239 | 0.16022 | 121.7239 | 121.4447 | 121.4355 | 121.4172 | 121.3943 | -121.6049 | -121.6187 | 121.6965 | 121.6827 | 61.2122 | 61.377
878.9531 | 121.9345 | -61.2488 | 60.347 | -0.12794 | 0.0041806 | 0.064115 | 0.060321 | -0.0057593 | -0.0094614 | -0.0019461 | -0.034454 | 0.0050971 | 0.065559 | 0.051114 | -0.015592 | 0.025272 | -0.0051525 | -0.11902 | 60.1685 | -61.2808 | 60.4477 | -61.0382 | -61.4639 | -61.3998 | 0.004578 | 60.2097 | -61.2762 | 60.3882 | -61.1847 | -61.2854 | -61.2625 | -0.032044 | -0.17853 | 0.10071 | 0.21057 | -0.15106 | -0.21515 | -0.11902 | -0.18311 | -0.027466 | -0.13733 | 0.041199 | 0.064087 | -0.013733 | -0.036621 | 0.013733 | -0.009155 | 0.24262 | 121.7285 | 0.091553 | 121.6644 | 121.4493 | 121.4859 | 121.4172 | 121.4584 | -121.6278 | -121.6232 | 121.6965 | 121.637 | 61.1298 | 61.2534
880.6406 | 121.8338 | -61.203 | 60.4248 | -0.082169 | 0.0028988 | 0.063047 | 0.06203 | -0.00084593 | -0.01117 | -0.0019461 | -0.06192 | 0.0040289 | 0.065986 | 0.051114 | -0.013883 | 0.02634 | -0.0072889 | 0.032043 | 60.2554 | -61.235 | 60.4248 | -61.0153 | -61.4594 | -61.4136 | 0.068665 | 60.2463 | -61.2488 | 60.3653 | -61.2167 | -61.3312 | -61.3083 | -0.032043 | -0.16937 | 0 | 0.18768 | -0.21057 | -0.25635 | -0.17853 | -0.22431 | -0.045776 | -0.17853 | -0.05951 | -0.013733 | -0.10529 | -0.12817 | -0.05951 | -0.082398 | 0.21973 | 121.6599 | 0.032043 | 121.6141 | 121.4905 | 121.4951 | 121.4584 | 121.4493 | -121.6599 | -121.6736 | 121.6278 | 121.5683 | 61.235 | 61.2717
882.375 | 121.8292 | -61.2625 | 60.4111 | -0.028763 | 0.0024716 | 0.066037 | 0.06203 | -0.0029821 | -0.010957 | -0.00066434 | -0.046661 | 0.0046697 | 0.066841 | 0.051755 | -0.013883 | 0.024417 | -0.0040845 | -0.032043 | 60.2921 | -61.2717 | 60.3973 | -61.0794 | -61.4777 | -61.441 | 0.013733 | 60.2509 | -61.2625 | 60.3561 | -61.235 | -61.3678 | -61.3083 | -0.009155 | -0.11902 | -0.013733 | 0.1831 | -0.17853 | -0.21515 | -0.16937 | -0.20599 | 0 | -0.16022 | -0.054932 | 0.027466 | -0.045777 | -0.10529 | -0.045777 | -0.10529 | 0.19226 | 121.669 | 0.027466 | 121.6187 | 121.5637 | 121.5134 | 121.5546 | 121.5134 | -121.6827 | -121.6736 | 121.6599 | 121.6187 | 61.2305 | 61.2762
884.125 | 121.8338 | -61.2396 | 60.4294 | -0.089798 | 0.0054624 | 0.066464 | 0.058612 | -0.0014867 | -0.0083932 | -0.00087794 | -0.046661 | 0.0070197 | 0.065772 | 0.053464 | -0.013242 | 0.024417 | -0.0066479 | 0.022888 | 60.26 | -61.2396 | 60.4156 | -61.0107 | -61.4548 | -61.3998 | 0.054932 | 60.2783 | -61.2625 | 60.3699 | -61.2213 | -61.3129 | -61.2946 | 0 | -0.16937 | -0.013733 | 0.22888 | -0.16022 | -0.21515 | -0.16022 | -0.21515 | -0.022888 | -0.15106 | -0.059509 | 0.018311 | -0.054932 | -0.073242 | -0.032044 | -0.050354 | 0.22888 | 121.6553 | 0.041199 | 121.6324 | 121.4996 | 121.5408 | 121.4996 | 121.5179 | -121.669 | -121.6919 | 121.6553 | 121.6095 | 61.2625 | 61.2946
885.8125 | 121.8842 | -61.2808 | 60.3424 | -0.11269 | 0.0054624 | 0.065396 | 0.06203 | -0.00041873 | -0.0098886 | -0.0023733 | -0.098541 | 0.0042425 | 0.06385 | 0.05795 | -0.015165 | 0.026981 | -0.0038709 | -0.07782 | 60.2234 | -61.2946 | 60.4019 | -61.0657 | -61.5097 | -61.4731 | 0.022888 | 60.1913 | -61.3129 | 60.3561 | -61.2396 | -61.3586 | -61.3266 | -0.013733 | -0.11902 | 0.05951 | 0.21515 | -0.19226 | -0.22888 | -0.17853 | -0.21515 | -0.032043 | -0.15106 | 0.013733 | 0.041199 | -0.045776 | -0.07782 | -0.013733 | -0.045777 | 0.22888 | 121.6965 | 0.073242 | 121.669 | 121.5179 | 121.5042 | 121.5042 | 121.4722 | -121.637 | -121.6553 | 121.6827 | 121.637 | 61.203 | 61.3037
887.5469 | 121.8018 | -61.2991 | 60.3607 | -0.097427 | 0.0071714 | 0.065396 | 0.065875 | 0.00043587 | -0.0077524 | -0.00066434 | -0.1077 | 0.0065923 | 0.066627 | 0.062863 | -0.013242 | 0.030612 | -0.0066479 | -0.13733 | 60.1868 | -61.3266 | 60.3333 | -61.1435 | -61.6013 | -61.5509 | -0.10986 | 60.1639 | -61.3586 | 60.2829 | -61.3403 | -61.4731 | -61.3953 | -0.027466 | -0.17395 | -0.027466 | 0.15564 | -0.25177 | -0.30212 | -0.2243 | -0.27466 | -0.05951 | -0.19684 | -0.07782 | -0.041199 | -0.096131 | -0.17395 | -0.036621 | -0.11444 | 0.18311 | 121.6599 | 0.018311 | 121.6415 | 121.5134 | 121.5225 | 121.4859 | 121.463 | -121.6873 | -121.7194 | 121.6324 | 121.582 | 61.1618 | 61.1893
889.2969 | 121.8979 | -61.235 | 60.3699 | -0.074539 | 0.003967 | 0.067319 | 0.057971 | -0.0017005 | -0.011811 | -0.0017325 | 0.0052185 | 0.0012517 | 0.067054 | 0.055173 | -0.012388 | 0.02634 | -0.0028027 | -0.082397 | 60.2188 | -61.2717 | 60.4111 | -61.0153 | -61.4548 | -61.4136 | 0.013733 | 60.1959 | -61.2854 | 60.3973 | -61.1847 | -61.3083 | -61.2534 | -0.036621 | -0.15106 | 0.041199 | 0.21973 | -0.17853 | -0.21973 | -0.14191 | -0.18311 | -0.050354 | -0.17395 | 0.027466 | 0.050354 | -0.018311 | -0.073243 | 0.032043 | -0.022889 | 0.25635 | 121.6827 | 0.10071 | 121.6827 | 121.4905 | 121.4813 | 121.4539 | 121.431 | -121.6415 | -121.6553 | 121.6461 | 121.6324 | 61.1526 | 61.2488
890.9844 | 121.9711 | -61.1938 | 60.3973 | -0.12794 | 0.0033262 | 0.064756 | 0.060748 | -0.0014867 | -0.01053 | -0.0028005 | 0.014374 | 0.0038153 | 0.065132 | 0.052823 | -0.01132 | 0.024844 | -0.0021619 | -0.013733 | 60.2325 | -61.2213 | 60.498 | -60.9375 | -61.3815 | -61.3174 | 0.17395 | 60.2188 | -61.2305 | 60.4752 | -61.0931 | -61.1938 | -61.1755 | -0.027465 | -0.1648 | 0.10071 | 0.25635 | -0.1236 | -0.18768 | -0.096131 | -0.16022 | -0.036621 | -0.17853 | 0.07782 | 0.10071 | 0.018311 | 0 | 0.054932 | 0.036621 | 0.28381 | 121.7194 | 0.13733 | 121.7056 | 121.4539 | 121.4493 | 121.4264 | 121.4127 | -121.6187 | -121.6278 | 121.6919 | 121.669 | 61.1801 | 61.3678
892.7188 | 121.9254 | -61.2167 | 60.3745 | -0.089798 | 0.0050352 | 0.06561 | 0.059466 | -0.0023413 | -0.0075388 | 0.0018991 | -0.019196 | 0.0023199 | 0.065132 | 0.04855 | -0.013029 | 0.024844 | -0.0032299 | -0.07782 | 60.2142 | -61.2625 | 60.4202 | -61.0199 | -61.4639 | -61.4044 | 0.018311 | 60.1959 | -61.2808 | 60.3882 | -61.1847 | -61.2991 | -61.2579 | -0.045776 | -0.16022 | 0.045776 | 0.19684 | -0.18768 | -0.24719 | -0.14191 | -0.20142 | -0.064087 | -0.17853 | 0.013733 | 0.032044 | -0.041199 | -0.082397 | 0.022888 | -0.01831 | 0.24262 | 121.6827 | 0.096131 | 121.669 | 121.4767 | 121.4767 | 121.431 | 121.4127 | -121.637 | -121.6553 | 121.637 | 121.6049 | 61.1389 | 61.235
894.4688 | 121.8384 | -61.2534 | 60.3973 | -0.05928 | 0.003967 | 0.066251 | 0.063311 | 0.0010767 | -0.011811 | -0.0015189 | -0.06192 | 0.0048833 | 0.066627 | 0.054745 | -0.013242 | 0.025485 | -0.0066479 | -0.036621 | 60.2692 | -61.2671 | 60.3928 | -61.0794 | -61.4777 | -61.4548 | 0.018311 | 60.2737 | -61.2671 | 60.347 | -61.2396 | -61.3632 | -61.3083 | -0.013733 | -0.12817 | -0.004578 | 0.17395 | -0.20142 | -0.2243 | -0.18768 | -0.21057 | -0.013733 | -0.1236 | -0.050354 | 0.013733 | -0.054932 | -0.10986 | -0.041199 | -0.09613 | 0.18768 | 121.6599 | 0.027466 | 121.6141 | 121.5363 | 121.5408 | 121.5225 | 121.5271 | -121.6644 | -121.6644 | 121.6461 | 121.6003 | 61.2167 | 61.2717
896.2344 | 121.8567 | -61.322 | 60.3012 | -0.097427 | 0.0078122 | 0.066037 | 0.062884 | -0.00063233 | -0.010743 | -0.0013051 | -0.11075 | 0.0068059 | 0.0662 | 0.059445 | -0.014097 | 0.026126 | -0.0036573 | -0.20599 | 60.173 | -61.3312 | 60.3058 | -61.1572 | -61.5967 | -61.5372 | -0.13275 | 60.1685 | -61.3495 | 60.3104 | -61.3174 | -61.441 | -61.3678 | -0.009156 | -0.12817 | 0.004578 | 0.16479 | -0.21515 | -0.27466 | -0.20599 | -0.2655 | -0.027466 | -0.13275 | 0.009156 | 0.004577 | -0.045777 | -0.11902 | -0.018311 | -0.091553 | 0.17395 | 121.637 | 0.032043 | 121.6599 | 121.5042 | 121.5179 | 121.4951 | 121.4905 | -121.6324 | -121.6507 | 121.6278 | 121.6324 | 61.116 | 61.1893
897.9062 | 121.843 | -61.2396 | 60.434 | -0.089798 | 0.0043942 | 0.065183 | 0.058612 | -0.0012731 | -0.010957 | -2.3544e-05 | -0.031403 | 0.0050971 | 0.065559 | 0.054959 | -0.014524 | 0.024204 | -0.0023755 | 0.032043 | 60.2325 | -61.235 | 60.4431 | -61.0016 | -61.4365 | -61.3998 | 0.086975 | 60.2692 | -61.2396 | 60.3699 | -61.2305 | -61.3312 | -61.29 | 0.004578 | -0.20142 | 0.009155 | 0.23804 | -0.16022 | -0.19684 | -0.1648 | -0.20142 | 0 | -0.16479 | -0.064087 | 0.009155 | -0.050354 | -0.091553 | -0.050354 | -0.091553 | 0.23346 | 121.6782 | 0.009155 | 121.6095 | 121.4676 | 121.5088 | 121.4722 | 121.5088 | -121.669 | -121.6736 | 121.6827 | 121.6095 | 61.2717 | 61.3266
899.6406 | 121.8613 | -61.2442 | 60.4248 | -0.097427 | 0.0043942 | 0.064115 | 0.062884 | -0.0023413 | -0.010743 | -0.0049367 | -0.071076 | 0.0055243 | 0.067481 | 0.056454 | -0.012174 | 0.02634 | -0.0015209 | -0.027466 | 60.2463 | -61.2625 | 60.379 | -61.0703 | -61.4777 | -61.4502 | 0.004578 | 60.2463 | -61.2854 | 60.3516 | -61.2534 | -61.3495 | -61.3174 | -0.01831 | -0.17853 | -0.045777 | 0.17395 | -0.20599 | -0.23346 | -0.18768 | -0.21515 | -0.041198 | -0.17853 | -0.073243 | -0.009155 | -0.073242 | -0.10529 | -0.032044 | -0.064087 | 0.19226 | 121.6415 | 0.032043 | 121.637 | 121.5088 | 121.5317 | 121.4905 | 121.4905 | -121.6873 | -121.7102 | 121.6232 | 121.5958 | 61.2167 | 61.2488
901.3906 | 121.8292 | -61.2442 | 60.4202 | -0.097427 | 0.0043942 | 0.064328 | 0.060748 | -0.0055457 | -0.011384 | -0.0030141 | -0.025299 | 0.0048833 | 0.066413 | 0.051541 | -0.011747 | 0.025485 | -0.0057935 | -0.027466 | 60.26 | -61.2625 | 60.4111 | -61.0565 | -61.4685 | -61.4182 | 0.032043 | 60.2829 | -61.2671 | 60.3653 | -61.2122 | -61.3449 | -61.29 | -0.01831 | -0.16022 | -0.009155 | 0.18768 | -0.17395 | -0.2243 | -0.15564 | -0.20599 | -0.022888 | -0.13733 | -0.054932 | 0.032044 | -0.045776 | -0.10071 | -0.022888 | -0.07782 | 0.20599 | 121.6736 | 0.054932 | 121.6324 | 121.5225 | 121.55 | 121.5042 | 121.5271 | -121.6827 | -121.6873 | 121.6553 | 121.6095 | 61.2167 | 61.2762
903.0781 | 121.9116 | -61.235 | 60.3607 | -0.10506 | 0.003967 | 0.065396 | 0.060321 | -0.0027685 | -0.0090342 | -0.0010915 | -0.025299 | 0.0055243 | 0.065559 | 0.053464 | -0.011961 | 0.025272 | -0.0036573 | -0.10529 | 60.1776 | -61.2442 | 60.4156 | -61.0291 | -61.4731 | -61.4044 | 0 | 60.1776 | -61.29 | 60.4019 | -61.1938 | -61.2946 | -61.2579 | -0.009156 | -0.18311 | 0.054931 | 0.20599 | -0.16937 | -0.23804 | -0.16022 | -0.22888 | -0.054932 | -0.18311 | 0.041199 | 0.041198 | -0.022889 | -0.05951 | 0.032043 | -0.004578 | 0.21515 | 121.6599 | 0.09613 | 121.6919 | 121.4218 | 121.4676 | 121.4127 | 121.4127 | -121.6049 | -121.6507 | 121.6507 | 121.637 | 61.1298 | 61.235
904.8281 | 121.8842 | -61.2717 | 60.3287 | -0.082169 | 0.007385 | 0.066464 | 0.061816 | 0.00043587 | -0.0092478 | -0.0040823 | -0.10159 | 0.0057379 | 0.065986 | 0.056668 | -0.015592 | 0.026981 | -0.0075025 | -0.068665 | 60.2234 | -61.29 | 60.4019 | -61.0519 | -61.5051 | -61.4548 | 0.018311 | 60.2097 | -61.3083 | 60.3653 | -61.2305 | -61.3632 | -61.2946 | -0.018311 | -0.10529 | 0.073243 | 0.21973 | -0.18311 | -0.23346 | -0.1648 | -0.21515 | -0.036622 | -0.11902 | 0.036621 | 0.041198 | -0.022889 | -0.091553 | 0.013733 | -0.054931 | 0.23804 | 121.6919 | 0.07782 | 121.6736 | 121.5134 | 121.5179 | 121.4951 | 121.4813 | -121.6187 | -121.637 | 121.6736 | 121.637 | 61.203 | 61.29
906.5781 | 121.8521 | -61.235 | 60.4248 | -0.06691 | 0.0043942 | 0.065396 | 0.059893 | -0.0010595 | -0.010316 | -0.0034415 | -0.034454 | 0.0057379 | 0.067268 | 0.04855 | -0.014524 | 0.026981 | -0.0055799 | 0.064087 | 60.2097 | -61.2122 | 60.4889 | -60.9604 | -61.3724 | -61.3632 | 0.12817 | 60.2325 | -61.235 | 60.3928 | -61.1801 | -61.3083 | -61.2762 | 0.022888 | -0.21515 | 0.064087 | 0.27466 | -0.12817 | -0.13733 | -0.15106 | -0.16022 | 0 | -0.19226 | -0.032044 | 0.054931 | -0.041199 | -0.073243 | -0.041199 | -0.073243 | 0.25177 | 121.7011 | 0.054931 | 121.6278 | 121.4218 | 121.4676 | 121.4447 | 121.4676 | -121.637 | -121.6599 | 121.7239 | 121.6278 | 61.2991 | 61.3632
908.3281 | 121.8567 | -61.3312 | 60.3149 | -0.097427 | 0.0071714 | 0.065396 | 0.062457 | 0.0029993 | -0.0098886 | -0.0036551 | -0.083283 | 0.0044561 | 0.065559 | 0.053036 | -0.014524 | 0.025485 | -0.0049389 | -0.22888 | 60.1959 | -61.3312 | 60.3058 | -61.1481 | -61.6013 | -61.5509 | -0.15106 | 60.1822 | -61.3541 | 60.3058 | -61.3174 | -61.4502 | -61.3632 | 0 | -0.11902 | -0.009155 | 0.18311 | -0.21973 | -0.27008 | -0.21973 | -0.27008 | -0.022888 | -0.13275 | -0.009155 | 0.013733 | -0.032043 | -0.11902 | -0.009155 | -0.09613 | 0.18311 | 121.637 | 0.036621 | 121.6599 | 121.5271 | 121.5363 | 121.5271 | 121.5134 | -121.6461 | -121.669 | 121.637 | 121.637 | 61.1023 | 61.1801
910.0312 | 121.9299 | -61.1938 | 60.3928 | -0.11269 | 0.0054624 | 0.066251 | 0.058825 | -0.00041873 | -0.009675 | -0.0051505 | -0.022247 | 0.0025335 | 0.066413 | 0.049832 | -0.013883 | 0.027408 | -0.0079297 | 0.045776 | 60.2509 | -61.2305 | 60.5347 | -60.9146 | -61.3358 | -61.322 | 0.18768 | 60.2234 | -61.2396 | 60.4797 | -61.1023 | -61.203 | -61.1847 | -0.036621 | -0.14191 | 0.14191 | 0.27924 | -0.12817 | -0.14191 | -0.091552 | -0.10529 | -0.045776 | -0.16937 | 0.086975 | 0.091553 | 0.009156 | -0.009155 | 0.054932 | 0.036621 | 0.31586 | 121.7651 | 0.13733 | 121.7194 | 121.4813 | 121.463 | 121.4447 | 121.4172 | -121.6232 | -121.6324 | 121.7285 | 121.6736 | 61.2396 | 61.3815
911.7812 | 121.8567 | -61.2946 | 60.3333 | -0.11269 | 0.0061032 | 0.065183 | 0.06203 | -0.0025549 | -0.009675 | -0.0053641 | -0.09549 | 0.0053107 | 0.067909 | 0.052823 | -0.012602 | 0.025912 | -0.0068615 | -0.21973 | 60.173 | -61.3449 | 60.2921 | -61.1664 | -61.6013 | -61.5601 | -0.13733 | 60.1868 | -61.3632 | 60.3012 | -61.322 | -61.441 | -61.377 | -0.050354 | -0.16022 | -0.041199 | 0.12817 | -0.2655 | -0.3067 | -0.21515 | -0.25635 | -0.068664 | -0.14648 | -0.032044 | -0.027465 | -0.082397 | -0.14648 | -0.013733 | -0.07782 | 0.17853 | 121.637 | 0.041199 | 121.6644 | 121.5179 | 121.55 | 121.4676 | 121.4813 | -121.6782 | -121.6965 | 121.5866 | 121.5958 | 61.0748 | 61.1572
913.5156 | 121.9116 | -61.2396 | 60.3287 | -0.097427 | 0.0080258 | 0.067105 | 0.060748 | -0.0019141 | -0.0092478 | -0.00045074 | -0.040558 | 0.0031745 | 0.0662 | 0.048123 | -0.011533 | 0.025912 | -0.0021619 | -0.10986 | 60.1776 | -61.2671 | 60.4202 | -61.0107 | -61.496 | -61.4273 | 0.045776 | 60.1501 | -61.2854 | 60.4156 | -61.2076 | -61.2991 | -61.2625 | -0.027466 | -0.15106 | 0.091553 | 0.22888 | -0.18768 | -0.25635 | -0.16022 | -0.22888 | -0.045776 | -0.17853 | 0.086975 | 0.032043 | -0.022888 | -0.059509 | 0.022888 | -0.013733 | 0.25635 | 121.6873 | 0.077819 | 121.701 | 121.4447 | 121.4355 | 121.4172 | 121.3898 | -121.5958 | -121.6141 | 121.6599 | 121.6553 | 61.1298 | 61.2854
915.25 | 121.9849 | -61.1618 | 60.379 | -0.12032 | 0.0065304 | 0.063474 | 0.05968 | -0.0049047 | -0.0098886 | 0.0014719 | -0.0008851 | 0.0038153 | 0.067481 | 0.052823 | -0.013029 | 0.025058 | -0.0066479 | 0.032043 | 60.2371 | -61.2442 | 60.5118 | -60.9009 | -61.3403 | -61.322 | 0.19684 | 60.2097 | -61.2167 | 60.5072 | -61.0519 | -61.1618 | -61.1343 | -0.082398 | -0.14191 | 0.13275 | 0.26092 | -0.16022 | -0.17853 | -0.077819 | -0.09613 | -0.054932 | -0.16937 | 0.12817 | 0.10986 | 0.027466 | 0 | 0.082398 | 0.054932 | 0.34332 | 121.756 | 0.16479 | 121.7239 | 121.4813 | 121.4264 | 121.3989 | 121.3715 | -121.6232 | -121.5958 | 121.6736 | 121.669 | 61.1938 | 61.3586
916.9375 | 121.8384 | -61.2213 | 60.4294 | -0.074539 | 0.0061032 | 0.063901 | 0.060321 | -0.00020513 | -0.010957 | -0.0032277 | -0.022247 | 0.0055243 | 0.067054 | 0.046628 | -0.015379 | 0.025272 | -0.0015209 | 0.050354 | 60.2509 | -61.2167 | 60.4614 | -60.9833 | -61.4273 | -61.3953 | 0.091553 | 60.2737 | -61.2579 | 60.3699 | -61.2167 | -61.3129 | -61.3083 | 0.004577 | -0.17853 | 0.032044 | 0.23804 | -0.17395 | -0.20599 | -0.17853 | -0.21057 | -0.036622 | -0.15564 | -0.059509 | 0.004577 | -0.086976 | -0.091553 | -0.050354 | -0.054931 | 0.23346 | 121.6782 | 0.041199 | 121.6278 | 121.4676 | 121.5317 | 121.4722 | 121.4951 | -121.6461 | -121.6873 | 121.6827 | 121.5912 | 61.2717 | 61.3129
918.625 | 121.9482 | -61.2808 | 60.2829 | -0.074539 | 0.007385 | 0.065396 | 0.061816 | -0.0036231 | -0.01053 | -0.0021597 | -0.080231 | 0.0048833 | 0.065772 | 0.052823 | -0.015165 | 0.026126 | -0.0047253 | -0.18768 | 60.1547 | -61.3586 | 60.379 | -61.0748 | -61.5417 | -61.4868 | -0.022888 | 60.141 | -61.322 | 60.3928 | -61.2213 | -61.3358 | -61.2717 | -0.07782 | -0.12817 | 0.09613 | 0.20599 | -0.20599 | -0.26093 | -0.12817 | -0.1831 | -0.041198 | -0.14191 | 0.10986 | 0.05951 | 0.009156 | -0.054931 | 0.050354 | -0.013733 | 0.28381 | 121.7377 | 0.10071 | 121.7148 | 121.5134 | 121.463 | 121.4355 | 121.4218 | -121.6415 | -121.6049 | 121.6599 | 121.6736 | 61.0931 | 61.2579
920.375 | 121.9666 | -61.2625 | 60.3104 | -0.19661 | 0.0063168 | 0.065183 | 0.062457 | -0.00063233 | -0.010743 | -0.0036551 | -0.068024 | 0.0053107 | 0.065132 | 0.057095 | -0.012815 | 0.02634 | -0.0013073 | -0.14191 | 60.141 | -61.3083 | 60.4156 | -61.0382 | -61.4914 | -61.4502 | -0.004578 | 60.1181 | -61.3129 | 60.4065 | -61.2167 | -61.3129 | -61.2488 | -0.045777 | -0.16937 | 0.10529 | 0.2243 | -0.18768 | -0.22888 | -0.14191 | -0.1831 | -0.050354 | -0.19226 | 0.09613 | 0.045776 | 0.013733 | -0.050354 | 0.064087 | 0 | 0.27008 | 121.7239 | 0.09613 | 121.7194 | 121.4493 | 121.431 | 121.4035 | 121.3806 | -121.6187 | -121.6232 | 121.6782 | 121.669 | 61.1206 | 61.2579
922.125 | 121.8796 | -61.2854 | 60.3836 | -0.05928 | 0.0069578 | 0.063687 | 0.063098 | 0.0023585 | -0.010957 | -0.0021597 | -0.098541 | 0.0038153 | 0.068122 | 0.051327 | -0.014097 | 0.026553 | -0.0057935 | -0.068665 | 60.2051 | -61.3129 | 60.3882 | -61.0657 | -61.5051 | -61.4639 | 0.022888 | 60.1959 | -61.3037 | 60.3561 | -61.2305 | -61.377 | -61.3129 | -0.027466 | -0.17853 | 0.004578 | 0.21973 | -0.17853 | -0.21973 | -0.15106 | -0.19226 | -0.018311 | -0.18768 | -0.027466 | 0.054931 | -0.027466 | -0.091553 | -0.009155 | -0.073242 | 0.24719 | 121.7011 | 0.073242 | 121.6599 | 121.5179 | 121.4996 | 121.4905 | 121.4813 | -121.6965 | -121.6873 | 121.6736 | 121.6415 | 61.2167 | 61.3083
923.7969 | 121.9574 | -61.29 | 60.2921 | -0.17372 | 0.0078122 | 0.066678 | 0.060534 | 0.0044947 | -0.006898 | -0.00023714 | -0.077179 | 0.0027471 | 0.066841 | 0.048764 | -0.015379 | 0.02634 | -0.0045117 | -0.14648 | 60.1456 | -61.3129 | 60.4248 | -61.0474 | -61.496 | -61.4456 | -0.009155 | 60.1135 | -61.322 | 60.3973 | -61.2076 | -61.3403 | -61.2625 | -0.022888 | -0.14648 | 0.13275 | 0.24262 | -0.15564 | -0.20599 | -0.13275 | -0.18311 | -0.032043 | -0.17853 | 0.10529 | 0.082397 | 0.027466 | -0.050354 | 0.059509 | -0.018311 | 0.2655 | 121.7377 | 0.11444 | 121.7194 | 121.4584 | 121.4355 | 121.4355 | 121.4035 | -121.6049 | -121.6141 | 121.7148 | 121.6873 | 61.1435 | 61.2808
925.5469 | 121.9299 | -61.1755 | 60.4202 | -0.11269 | 0.0063168 | 0.065183 | 0.059253 | 8.47e-06 | -0.0094614 | -0.0042959 | -0.022247 | 0.0027471 | 0.065772 | 0.056027 | -0.014097 | 0.02634 | 0.0016833 | 0.064087 | 60.2234 | -61.203 | 60.5255 | -60.9283 | -61.3586 | -61.3358 | 0.1831 | 60.228 | -61.2579 | 60.4477 | -61.0977 | -61.2076 | -61.1801 | -0.027466 | -0.19684 | 0.10529 | 0.24719 | -0.16022 | -0.18311 | -0.13275 | -0.15564 | -0.082398 | -0.19226 | 0.027466 | 0.07782 | -0.004578 | -0.032044 | 0.07782 | 0.050354 | 0.27466 | 121.7285 | 0.16022 | 121.7056 | 121.4264 | 121.4859 | 121.3989 | 121.4035 | -121.6232 | -121.6782 | 121.701 | 121.6232 | 61.2396 | 61.3586
927.2969 | 121.9345 | -61.235 | 60.3836 | -0.12032 | 0.0052488 | 0.06561 | 0.060748 | -0.00020513 | -0.008607 | -0.0028005 | -0.0069885 | 0.0046697 | 0.065772 | 0.0509 | -0.011747 | 0.024631 | -0.0028027 | -0.073242 | 60.2142 | -61.2442 | 60.4111 | -61.0382 | -61.441 | -61.3998 | 0.032043 | 60.1959 | -61.2717 | 60.3973 | -61.1801 | -61.2854 | -61.2534 | -0.009156 | -0.16937 | 0.027466 | 0.19684 | -0.1648 | -0.20599 | -0.15564 | -0.19684 | -0.036621 | -0.18768 | 0.013733 | 0.054931 | -0.018311 | -0.050354 | 0.01831 | -0.013733 | 0.20599 | 121.6553 | 0.091552 | 121.669 | 121.4584 | 121.4676 | 121.4493 | 121.431 | -121.6278 | -121.6553 | 121.6461 | 121.6324 | 61.1618 | 61.2671
928.9844 | 121.8292 | -61.3358 | 60.3104 | -0.082169 | 0.008453 | 0.068173 | 0.063098 | 0.0019311 | -0.0088206 | -0.0034415 | -0.11685 | 0.0053107 | 0.065772 | 0.049191 | -0.014738 | 0.028476 | -0.0055799 | -0.1236 | 60.2234 | -61.3266 | 60.3424 | -61.1206 | -61.5829 | -61.5372 | -0.091553 | 60.1685 | -61.3541 | 60.2829 | -61.3266 | -61.4594 | -61.3861 | 0.009155 | -0.086975 | 0.032043 | 0.21515 | -0.20142 | -0.24719 | -0.21057 | -0.25635 | -0.018311 | -0.14191 | -0.027466 | 0.009155 | -0.050354 | -0.1236 | -0.032043 | -0.10529 | 0.20599 | 121.669 | 0.027466 | 121.637 | 121.55 | 121.5225 | 121.5591 | 121.5042 | -121.637 | -121.6644 | 121.6782 | 121.6187 | 61.2122 | 61.2442
930.7344 | 121.9254 | -61.2122 | 60.3607 | -0.12032 | 0.0052488 | 0.066464 | 0.060107 | 0.0015039 | -0.006898 | -0.0038687 | 0.014374 | 0.0029607 | 0.065345 | 0.04321 | -0.011533 | 0.023135 | -0.0021619 | -0.073242 | 60.2051 | -61.2579 | 60.4294 | -61.0336 | -61.4639 | -61.4273 | 0.027466 | 60.2051 | -61.2854 | 60.4202 | -61.1755 | -61.2717 | -61.2442 | -0.045777 | -0.15564 | 0.068664 | 0.17853 | -0.21515 | -0.25177 | -0.16937 | -0.20599 | -0.073242 | -0.15564 | 0.059509 | 0.036621 | -0.032044 | -0.059509 | 0.041198 | 0.013733 | 0.22431 | 121.6873 | 0.10986 | 121.7056 | 121.463 | 121.4905 | 121.4172 | 121.4172 | -121.6187 | -121.6461 | 121.6415 | 121.6324 | 61.1389 | 61.2396
932.4844 | 121.9711 | -61.1938 | 60.4019 | -0.089798 | 0.0050352 | 0.067319 | 0.060962 | -0.0064001 | -0.009675 | -0.0042959 | -0.01004 | 0.0061651 | 0.066413 | 0.043637 | -0.011533 | 0.026126 | -0.0028027 | -0.050354 | 60.2371 | -61.2579 | 60.4614 | -60.9833 | -61.409 | -61.3678 | 0.10986 | 60.2005 | -61.2579 | 60.4614 | -61.0977 | -61.2167 | -61.1801 | -0.064087 | -0.16479 | 0.059509 | 0.21057 | -0.17395 | -0.21515 | -0.10986 | -0.15106 | -0.064087 | -0.20142 | 0.059509 | 0.096131 | 0.013733 | -0.022888 | 0.07782 | 0.041199 | 0.27466 | 121.7194 | 0.16022 | 121.7194 | 121.4951 | 121.4584 | 121.431 | 121.3943 | -121.6599 | -121.6599 | 121.6553 | 121.6553 | 61.1435 | 61.3037
934.1719 | 121.8155 | -61.3495 | 60.3195 | -0.16609 | 0.007385 | 0.065396 | 0.063525 | 0.00022207 | -0.010743 | -0.0034415 | -0.14127 | 0.0048833 | 0.064704 | 0.056881 | -0.014311 | 0.025912 | -0.0034435 | -0.18768 | 60.2188 | -61.3495 | 60.3012 | -61.1984 | -61.6241 | -61.5738 | -0.18768 | 60.1959 | -61.3632 | 60.2509 | -61.3632 | -61.4685 | -61.4044 | 0 | -0.10071 | -0.018311 | 0.15106 | -0.2243 | -0.27466 | -0.2243 | -0.27466 | -0.013733 | -0.1236 | -0.068665 | -0.013733 | -0.054932 | -0.11902 | -0.041199 | -0.10529 | 0.15106 | 121.6507 | 0 | 121.6141 | 121.5683 | 121.5591 | 121.5683 | 121.5454 | -121.669 | -121.6827 | 121.6507 | 121.6003 | 61.1618 | 61.1618
935.875 | 121.8292 | -61.3083 | 60.3149 | -0.12794 | 0.0048214 | 0.066251 | 0.063952 | 0.00064947 | -0.01053 | -2.3544e-05 | -0.098541 | 0.0061651 | 0.068122 | 0.060513 | -0.014311 | 0.02634 | -0.0051525 | -0.2243 | 60.1547 | -61.3495 | 60.2737 | -61.2122 | -61.6379 | -61.5784 | -0.16937 | 60.1776 | -61.3678 | 60.2646 | -61.3358 | -61.4731 | -61.3724 | -0.041198 | -0.16022 | -0.041198 | 0.096131 | -0.27008 | -0.32959 | -0.22888 | -0.28839 | -0.059509 | -0.13733 | -0.050354 | -0.027465 | -0.064086 | -0.16479 | -0.004577 | -0.10529 | 0.13733 | 121.6232 | 0.032044 | 121.6324 | 121.5042 | 121.5454 | 121.463 | 121.4859 | -121.6644 | -121.6827 | 121.582 | 121.5729 | 61.084 | 61.1389
937.6094 | 121.8658 | -61.2854 | 60.3424 | -0.11269 | 0.0082394 | 0.064328 | 0.062671 | -0.0023413 | -0.0088206 | -0.0042959 | -0.080231 | 0.0044561 | 0.065772 | 0.052395 | -0.012174 | 0.025485 | -0.0034435 | -0.091553 | 60.2051 | -61.3129 | 60.4019 | -61.0657 | -61.4914 | -61.4777 | 0.027466 | 60.2097 | -61.3174 | 60.3516 | -61.235 | -61.3678 | -61.3129 | -0.027466 | -0.13733 | 0.05951 | 0.21973 | -0.19226 | -0.20599 | -0.16479 | -0.17853 | -0.032044 | -0.13275 | 0.009155 | 0.050354 | -0.027466 | -0.082398 | 0.004578 | -0.050354 | 0.24719 | 121.7148 | 0.082398 | 121.669 | 121.5179 | 121.5271 | 121.4905 | 121.4951 | -121.6553 | -121.6599 | 121.6873 | 121.637 | 61.1938 | 61.3129
939.3438 | 121.8521 | -61.2946 | 60.3378 | -0.074539 | 0.008453 | 0.065396 | 0.061602 | 0.0017175 | -0.0073252 | -0.00023714 | -0.089386 | 0.0070197 | 0.064918 | 0.054745 | -0.011106 | 0.026126 | -0.0032299 | -0.10529 | 60.1913 | -61.2946 | 60.4019 | -61.0703 | -61.5143 | -61.4731 | 0.004578 | 60.1959 | -61.3037 | 60.3333 | -61.2717 | -61.4044 | -61.3449 | 0 | -0.14648 | 0.064087 | 0.22431 | -0.17853 | -0.21973 | -0.17853 | -0.21973 | -0.009155 | -0.14191 | -0.004578 | 0.022889 | -0.050354 | -0.10986 | -0.041199 | -0.10071 | 0.22431 | 121.6965 | 0.032044 | 121.637 | 121.4859 | 121.4996 | 121.4859 | 121.4905 | -121.6324 | -121.6415 | 121.6965 | 121.6278 | 61.1893 | 61.2991
941.1094 | 121.9299 | -61.2808 | 60.3424 | -0.18135 | 0.0063168 | 0.065824 | 0.059039 | -0.0042639 | -0.0075388 | -0.0028005 | -0.013092 | 0.0036017 | 0.067695 | 0.050046 | -0.013456 | 0.025912 | -0.0017347 | -0.13733 | 60.1547 | -61.2717 | 60.4431 | -60.9833 | -61.4685 | -61.409 | 0.027466 | 60.1364 | -61.2854 | 60.3973 | -61.203 | -61.29 | -61.2534 | 0.009156 | -0.18768 | 0.10071 | 0.29755 | -0.12817 | -0.18768 | -0.13733 | -0.19684 | -0.004577 | -0.20599 | 0.054932 | 0.07782 | 0.027466 | -0.009155 | 0.032043 | -0.004578 | 0.28839 | 121.7148 | 0.082397 | 121.6827 | 121.4264 | 121.4218 | 121.4355 | 121.4172 | -121.6141 | -121.6278 | 121.7239 | 121.6782 | 61.1435 | 61.3083
942.7969 | 121.9666 | -61.2122 | 60.3653 | -0.12794 | 0.0063168 | 0.064542 | 0.061175 | -0.0042639 | -0.0081796 | -0.0042959 | 0.0052185 | 0.0038153 | 0.06855 | 0.051114 | -0.013883 | 0.024631 | -0.0057935 | 0 | 60.2325 | -61.2213 | 60.5164 | -60.9283 | -61.3449 | -61.2991 | 0.17853 | 60.2051 | -61.2442 | 60.4843 | -61.0886 | -61.1938 | -61.171 | -0.009155 | -0.13275 | 0.15106 | 0.28381 | -0.086975 | -0.13275 | -0.07782 | -0.1236 | -0.032044 | -0.16022 | 0.11902 | 0.1236 | 0.041199 | 0.01831 | 0.073243 | 0.050354 | 0.29297 | 121.7377 | 0.15564 | 121.7285 | 121.4539 | 121.4493 | 121.4447 | 121.4172 | -121.5866 | -121.6095 | 121.7285 | 121.6965 | 61.2122 | 61.3907
944.5312 | 121.9711 | -61.1938 | 60.4156 | -0.18135 | 0.005676 | 0.065183 | 0.061175 | -0.0036231 | -0.0092478 | -0.00087794 | 0.0052185 | 0.0033881 | 0.065132 | 0.053677 | -0.013456 | 0.025912 | -0.0085705 | -0.050354 | 60.2188 | -61.235 | 60.4568 | -60.9924 | -61.4273 | -61.3495 | 0.10529 | 60.2005 | -61.2579 | 60.4523 | -61.116 | -61.1984 | -61.1984 | -0.041198 | -0.19684 | 0.041199 | 0.20142 | -0.15564 | -0.23346 | -0.11444 | -0.19226 | -0.064087 | -0.21515 | 0.036622 | 0.07782 | -0.004577 | -0.004577 | 0.05951 | 0.05951 | 0.24261 | 121.6919 | 0.14191 | 121.7102 | 121.4539 | 121.4584 | 121.4127 | 121.3943 | -121.6507 | -121.6736 | 121.6507 | 121.6461 | 61.1435 | 61.2991
946.2344 | 121.9345 | -61.1984 | 60.4065 | -0.12032 | 0.0046078 | 0.067533 | 0.05968 | -0.0040503 | -0.0075388 | -0.0015189 | -0.016144 | 0.0048833 | 0.065559 | 0.050259 | -0.013456 | 0.025485 | -0.0049389 | -0.064087 | 60.2051 | -61.2717 | 60.4523 | -61.0107 | -61.4273 | -61.377 | 0.073242 | 60.2097 | -61.2762 | 60.4431 | -61.1343 | -61.2305 | -61.203 | -0.073242 | -0.20142 | 0.045777 | 0.18768 | -0.17853 | -0.22888 | -0.10529 | -0.15564 | -0.07782 | -0.19684 | 0.036621 | 0.064087 | -0.004578 | -0.032044 | 0.073242 | 0.045776 | 0.26093 | 121.7239 | 0.14191 | 121.7194 | 121.4767 | 121.4859 | 121.4035 | 121.4081 | -121.6782 | -121.6827 | 121.6507 | 121.6415 | 61.1343 | 61.2717
947.9688 | 121.8567 | -61.2305 | 60.4156 | -0.11269 | 0.0050352 | 0.064542 | 0.060107 | -0.0051183 | -0.0092478 | 0.00061746 | -0.034454 | 0.0040289 | 0.065559 | 0.055386 | -0.013883 | 0.02634 | -0.0051525 | 0.045776 | 60.2417 | -61.2305 | 60.4614 | -60.9741 | -61.4044 | -61.3724 | 0.10986 | 60.2417 | -61.2442 | 60.379 | -61.1984 | -61.3266 | -61.2946 | 0 | -0.17395 | 0.045777 | 0.25635 | -0.14191 | -0.17395 | -0.14191 | -0.17395 | -0.013733 | -0.17395 | -0.036621 | 0.032044 | -0.064087 | -0.09613 | -0.050354 | -0.082397 | 0.25635 | 121.6919 | 0.045777 | 121.6232 | 121.4722 | 121.4859 | 121.4722 | 121.4722 | -121.6461 | -121.6599 | 121.6919 | 121.6095 | 61.2762 | 61.3403
949.7188 | 121.8796 | -61.2717 | 60.3516 | -0.082169 | 0.007385 | 0.065824 | 0.063525 | 8.47e-06 | -0.0075388 | -0.0038687 | -0.11075 | 0.0059515 | 0.067054 | 0.057095 | -0.012815 | 0.024631 | -0.0049389 | -0.07782 | 60.2417 | -61.322 | 60.3973 | -61.0611 | -61.5143 | -61.4639 | 0.022888 | 60.2051 | -61.3312 | 60.3653 | -61.2305 | -61.3632 | -61.3266 | -0.050354 | -0.10986 | 0.045777 | 0.21057 | -0.19226 | -0.24262 | -0.14191 | -0.19226 | -0.05951 | -0.14648 | 0.013733 | 0.041198 | -0.054932 | -0.091553 | 0.004578 | -0.032043 | 0.26093 | 121.7194 | 0.10071 | 121.6965 | 121.5637 | 121.5363 | 121.5134 | 121.4767 | -121.6736 | -121.6827 | 121.669 | 121.637 | 61.1938 | 61.2946
951.4062 | 121.8979 | -61.1938 | 60.4202 | -0.074539 | 0.0050352 | 0.065396 | 0.060748 | -0.00020513 | -0.0088206 | -0.0030141 | -0.031403 | 0.0044561 | 0.0662 | 0.055173 | -0.012602 | 0.024631 | -0.0028027 | 0.045776 | 60.2463 | -61.2671 | 60.5164 | -60.9375 | -61.3541 | -61.3403 | 0.15106 | 60.2417 | -61.235 | 60.4065 | -61.1481 | -61.2671 | -61.2442 | -0.073242 | -0.17395 | 0.09613 | 0.25635 | -0.14648 | -0.16022 | -0.073242 | -0.086975 | -0.041198 | -0.17853 | -0.013733 | 0.045777 | -0.050354 | -0.073242 | -0.009156 | -0.032044 | 0.32959 | 121.7834 | 0.086975 | 121.6415 | 121.5134 | 121.4767 | 121.4401 | 121.4355 | -121.6873 | -121.6553 | 121.7102 | 121.6003 | 61.2396 | 61.3449
953.1562 | 121.8887 | -61.3083 | 60.2966 | -0.06691 | 0.0086668 | 0.066251 | 0.063952 | -0.00063233 | -0.0066844 | -0.0055777 | -0.080231 | 0.0063787 | 0.067909 | 0.056881 | -0.013456 | 0.027621 | -0.0017347 | -0.21973 | 60.1639 | -61.3312 | 60.3149 | -61.1572 | -61.6058 | -61.5463 | -0.13733 | 60.1685 | -61.3724 | 60.3104 | -61.2991 | -61.4227 | -61.3403 | -0.022888 | -0.13275 | 0.01831 | 0.15106 | -0.23804 | -0.29755 | -0.21515 | -0.27466 | -0.064086 | -0.12817 | 0.013733 | 0.009156 | -0.032043 | -0.11444 | 0.032043 | -0.050354 | 0.17395 | 121.6461 | 0.073242 | 121.6827 | 121.4951 | 121.5408 | 121.4722 | 121.4767 | -121.6278 | -121.669 | 121.6232 | 121.6187 | 61.0886 | 61.171
954.8438 | 121.8658 | -61.2305 | 60.4111 | -0.097427 | 0.0048214 | 0.064115 | 0.059893 | -0.0029821 | -0.0094614 | -0.0040823 | -0.028351 | 0.0044561 | 0.065772 | 0.046414 | -0.013029 | 0.026981 | -0.0057935 | 0.059509 | 60.2371 | -61.2442 | 60.498 | -60.9375 | -61.3815 | -61.3495 | 0.14191 | 60.2463 | -61.2488 | 60.4019 | -61.171 | -61.2808 | -61.2534 | -0.013733 | -0.17395 | 0.086975 | 0.29297 | -0.11902 | -0.15106 | -0.10529 | -0.13733 | -0.01831 | -0.16479 | -0.009155 | 0.05951 | -0.022888 | -0.050354 | -0.004578 | -0.032044 | 0.3067 | 121.7422 | 0.07782 | 121.6507 | 121.4813 | 121.4951 | 121.4676 | 121.4767 | -121.6553 | -121.6599 | 121.7285 | 121.6324 | 61.29 | 61.3724
956.5938 | 121.9482 | -61.1893 | 60.4202 | -0.12032 | 0.0058896 | 0.064115 | 0.060962 | -0.0019141 | -0.010102 | -0.00045074 | -0.0069885 | 0.0042425 | 0.063423 | 0.051114 | -0.012174 | 0.023563 | -0.0045117 | 0.068665 | 60.2325 | -61.2122 | 60.5347 | -60.9192 | -61.3586 | -61.3174 | 0.19684 | 60.2188 | -61.235 | 60.4843 | -61.0886 | -61.2213 | -61.1755 | -0.022888 | -0.18768 | 0.11444 | 0.27008 | -0.12817 | -0.16937 | -0.10529 | -0.14648 | -0.045776 | -0.20142 | 0.064087 | 0.10071 | 0.013733 | -0.032043 | 0.059509 | 0.013733 | 0.29297 | 121.7468 | 0.14648 | 121.7194 | 121.4447 | 121.4539 | 121.4218 | 121.4081 | -121.6324 | -121.6553 | 121.7239 | 121.6736 | 61.2579 | 61.3861
958.2812 | 121.8567 | -61.322 | 60.3424 | -0.10506 | 0.0065304 | 0.064542 | 0.064593 | 0.0017175 | -0.0083932 | -0.0040823 | -0.10159 | 0.0055243 | 0.065772 | 0.059872 | -0.013883 | 0.025912 | -0.0045117 | -0.23804 | 60.2097 | -61.3541 | 60.2921 | -61.171 | -61.6058 | -61.5417 | -0.13733 | 60.1547 | -61.3678 | 60.2921 | -61.322 | -61.4502 | -61.377 | -0.032044 | -0.13275 | -0.050354 | 0.15106 | -0.21973 | -0.28381 | -0.18768 | -0.25177 | -0.045777 | -0.18768 | -0.050354 | 0 | -0.054932 | -0.12817 | -0.009155 | -0.082397 | 0.18311 | 121.6461 | 0.045777 | 121.6599 | 121.5637 | 121.5225 | 121.5317 | 121.4767 | -121.6965 | -121.7102 | 121.6141 | 121.6141 | 61.084 | 61.1847
960.0312 | 121.9666 | -61.1893 | 60.379 | -0.11269 | 0.0043942 | 0.064756 | 0.061389 | 0.0021447 | -0.01053 | -0.0047231 | -0.013092 | 0.0036017 | 0.0662 | 0.046414 | -0.012815 | 0.02634 | -0.0032299 | 0.064087 | 60.228 | -61.2167 | 60.5347 | -60.9009 | -61.3358 | -61.2991 | 0.21057 | 60.228 | -61.235 | 60.4752 | -61.0886 | -61.1984 | -61.1893 | -0.027466 | -0.15106 | 0.15564 | 0.28839 | -0.10986 | -0.14648 | -0.082397 | -0.11902 | -0.045776 | -0.15106 | 0.096131 | 0.10071 | 0 | -0.009155 | 0.045776 | 0.036621 | 0.31586 | 121.7514 | 0.14648 | 121.7102 | 121.4447 | 121.463 | 121.4172 | 121.4172 | -121.5958 | -121.6141 | 121.7239 | 121.6644 | 61.2534 | 61.3998
961.7344 | 121.8521 | -61.3083 | 60.3424 | -0.074539 | 0.0078122 | 0.066678 | 0.064166 | -0.0034095 | -0.010102 | -0.0034415 | -0.12296 | 0.0057379 | 0.064063 | 0.056027 | -0.012815 | 0.029117 | -0.0057935 | -0.086975 | 60.2325 | -61.29 | 60.3607 | -61.0748 | -61.528 | -61.4822 | -0.022888 | 60.173 | -61.3174 | 60.3195 | -61.2946 | -61.4227 | -61.3449 | 0.018311 | -0.10986 | 0.018311 | 0.23346 | -0.17395 | -0.21973 | -0.19226 | -0.23804 | -0.009155 | -0.16937 | -0.022888 | 0.013733 | -0.036621 | -0.11444 | -0.027466 | -0.10528 | 0.21515 | 121.6507 | 0.022888 | 121.637 | 121.5225 | 121.4905 | 121.5408 | 121.4813 | -121.6324 | -121.6599 | 121.669 | 121.6278 | 61.2213 | 61.2854
963.4688 | 121.8613 | -61.3037 | 60.3516 | -0.06691 | 0.0058896 | 0.064542 | 0.063098 | 0.0027857 | -0.0073252 | -0.0023733 | -0.089386 | 0.0050971 | 0.067695 | 0.058804 | -0.012388 | 0.025912 | -0.0019483 | -0.10986 | 60.2005 | -61.3312 | 60.379 | -61.0703 | -61.5143 | -61.4639 | 0.004578 | 60.2097 | -61.3312 | 60.3424 | -61.2579 | -61.409 | -61.3174 | -0.027466 | -0.15106 | 0.027466 | 0.23346 | -0.16022 | -0.21057 | -0.13275 | -0.18311 | -0.027466 | -0.14191 | -0.009155 | 0.045776 | -0.013733 | -0.10529 | 0.013733 | -0.07782 | 0.26093 | 121.7102 | 0.073242 | 121.6736 | 121.5317 | 121.5408 | 121.5042 | 121.5134 | -121.6827 | -121.6827 | 121.6827 | 121.6461 | 61.1938 | 61.3083
965.2188 | 121.8521 | -61.2305 | 60.4477 | -0.12794 | 0.0054624 | 0.06561 | 0.060534 | -0.0019141 | -0.0092478 | -0.0013051 | -0.040558 | 0.0042425 | 0.064491 | 0.052182 | -0.010038 | 0.025699 | -0.0038709 | 0 | 60.2371 | -61.2442 | 60.4111 | -61.0382 | -61.4731 | -61.4365 | 0.050354 | 60.2554 | -61.2762 | 60.3561 | -61.2076 | -61.3266 | -61.3129 | -0.013733 | -0.21057 | -0.036621 | 0.19226 | -0.20599 | -0.24261 | -0.19226 | -0.22888 | -0.045776 | -0.19226 | -0.091553 | 0.022888 | -0.082397 | -0.09613 | -0.036621 | -0.050354 | 0.20599 | 121.6553 | 0.068664 | 121.6324 | 121.4813 | 121.5317 | 121.4676 | 121.4859 | -121.6919 | -121.7239 | 121.6415 | 121.5866 | 61.2305 | 61.2808
966.9062 | 121.907 | -61.2259 | 60.3699 | -0.10506 | 0.0061032 | 0.066678 | 0.059253 | -0.0034095 | -0.008607 | -0.0019461 | 0.014374 | 0.0042425 | 0.065772 | 0.056668 | -0.014097 | 0.026553 | -0.0053661 | -0.07782 | 60.1959 | -61.2579 | 60.4248 | -61.0245 | -61.4685 | -61.4044 | 0.009155 | 60.2097 | -61.2854 | 60.379 | -61.1847 | -61.3083 | -61.2488 | -0.032044 | -0.17395 | 0.054932 | 0.20142 | -0.17853 | -0.24262 | -0.14648 | -0.21057 | -0.059509 | -0.16022 | 0.009155 | 0.041199 | -0.022888 | -0.082398 | 0.036621 | -0.022889 | 0.23346 | 121.6827 | 0.10071 | 121.6644 | 121.4539 | 121.4951 | 121.4218 | 121.4355 | -121.6278 | -121.6553 | 121.6507 | 121.6049 | 61.1481 | 61.235
968.6562 | 121.9666 | -61.1938 | 60.4019 | -0.15846 | 0.0028988 | 0.064969 | 0.058184 | -0.0055457 | -0.0094614 | -0.0042959 | 0.0082703 | 0.0042425 | 0.065559 | 0.045346 | -0.015379 | 0.025272 | -0.0045117 | 0.045776 | 60.1959 | -61.2167 | 60.5255 | -60.8963 | -61.3358 | -61.2991 | 0.20142 | 60.2325 | -61.2442 | 60.4843 | -61.0931 | -61.1893 | -61.1847 | -0.022888 | -0.20599 | 0.1236 | 0.29755 | -0.10528 | -0.14191 | -0.082397 | -0.11902 | -0.050354 | -0.16937 | 0.082397 | 0.10071 | 0.009156 | 0.004578 | 0.05951 | 0.054932 | 0.32043 | 121.7422 | 0.15106 | 121.7285 | 121.4127 | 121.4767 | 121.3898 | 121.4264 | -121.6187 | -121.6461 | 121.7194 | 121.6782 | 61.2396 | 61.3953
970.3438 | 121.8887 | -61.3037 | 60.2692 | -0.074539 | 0.0054624 | 0.064328 | 0.063952 | -0.00063233 | -0.0075388 | -0.0015189 | -0.10159 | 0.0057379 | 0.065132 | 0.055173 | -0.013883 | 0.027621 | -0.0010937 | -0.21057 | 60.1913 | -61.3586 | 60.3195 | -61.1755 | -61.6058 | -61.5372 | -0.13733 | 60.1456 | -61.3815 | 60.3149 | -61.3083 | -61.4182 | -61.3449 | -0.054932 | -0.07782 | 0.050354 | 0.12817 | -0.23346 | -0.30212 | -0.17853 | -0.24719 | -0.07782 | -0.1236 | 0.045776 | -0.004578 | -0.041199 | -0.11444 | 0.036621 | -0.036621 | 0.18311 | 121.6782 | 0.073242 | 121.6965 | 121.55 | 121.5271 | 121.4951 | 121.4493 | -121.6278 | -121.6507 | 121.6232 | 121.6187 | 61.0931 | 61.1664
972.0781 | 121.9116 | -61.2396 | 60.3699 | -0.12032 | 0.0063168 | 0.064115 | 0.060107 | 0.0023585 | -0.0098886 | -0.00087794 | -0.01004 | 0.0038153 | 0.065986 | 0.050473 | -0.013883 | 0.025485 | -0.0023755 | -0.11902 | 60.1822 | -61.235 | 60.4294 | -61.0199 | -61.4822 | -61.4273 | 0.013733 | 60.1822 | -61.2854 | 60.3928 | -61.1938 | -61.3083 | -61.2625 | 0.004578 | -0.18768 | 0.059509 | 0.21973 | -0.18768 | -0.24262 | -0.19226 | -0.24719 | -0.045776 | -0.18768 | 0.022888 | 0.045776 | -0.022888 | -0.068665 | 0.022888 | -0.022889 | 0.21515 | 121.6644 | 0.091552 | 121.6782 | 121.4172 | 121.4676 | 121.4218 | 121.4218 | -121.6049 | -121.6553 | 121.669 | 121.6324 | 61.1206 | 61.2534
973.8125 | 121.9803 | -61.2076 | 60.3836 | -0.06691 | 0.0033262 | 0.064756 | 0.057971 | -0.0068273 | -0.0071116 | 0.0014719 | 0.0082703 | 0.0057379 | 0.063636 | 0.051755 | -0.014951 | 0.024844 | -0.0034435 | 0.018311 | 60.2371 | -61.2305 | 60.5164 | -60.9146 | -61.3541 | -61.322 | 0.16022 | 60.2234 | -61.2534 | 60.4889 | -61.0977 | -61.203 | -61.1664 | -0.022888 | -0.14648 | 0.13275 | 0.29297 | -0.11444 | -0.14648 | -0.091552 | -0.1236 | -0.045776 | -0.16022 | 0.10529 | 0.10986 | 0.041199 | 0.004578 | 0.086975 | 0.050354 | 0.31586 | 121.7468 | 0.15564 | 121.7422 | 121.4676 | 121.4767 | 121.4447 | 121.431 | -121.6141 | -121.637 | 121.7239 | 121.6965 | 61.2259 | 61.3678
975.5625 | 121.8521 | -61.2442 | 60.4111 | -0.097427 | 0.0048214 | 0.063687 | 0.062671 | -0.0061865 | -0.0094614 | -0.0021597 | -0.086334 | 0.0063787 | 0.065772 | 0.047909 | -0.014951 | 0.026126 | -0.0028027 | -0.027466 | 60.2921 | -61.2625 | 60.4111 | -61.0611 | -61.4822 | -61.4365 | 0.045776 | 60.2921 | -61.2534 | 60.3607 | -61.2442 | -61.3403 | -61.3129 | -0.01831 | -0.11902 | 0 | 0.18311 | -0.19226 | -0.23804 | -0.17395 | -0.21973 | -0.009155 | -0.11902 | -0.050354 | 0 | -0.068664 | -0.09613 | -0.059509 | -0.086975 | 0.20142 | 121.6736 | 0.009155 | 121.6141 | 121.5546 | 121.5454 | 121.5363 | 121.5363 | -121.6736 | -121.6644 | 121.6553 | 121.6049 | 61.2167 | 61.29
977.25 | 121.875 | -61.2076 | 60.4156 | -0.036392 | 0.0063168 | 0.066892 | 0.060534 | 0.00064947 | -0.010316 | 0.00019006 | -0.028351 | 0.0036017 | 0.064704 | 0.050046 | -0.015806 | 0.024631 | -0.0019483 | 0.041199 | 60.2234 | -61.2259 | 60.5072 | -60.9375 | -61.3724 | -61.322 | 0.15564 | 60.2371 | -61.2259 | 60.4156 | -61.1481 | -61.2762 | -61.235 | -0.01831 | -0.19226 | 0.091553 | 0.27008 | -0.11444 | -0.16479 | -0.09613 | -0.14648 | -0.01831 | -0.17853 | 0 | 0.05951 | -0.027465 | -0.068664 | -0.009155 | -0.050354 | 0.28839 | 121.7331 | 0.07782 | 121.6415 | 121.4493 | 121.463 | 121.431 | 121.4447 | -121.6415 | -121.6415 | 121.7148 | 121.6232 | 61.2488 | 61.3632
979 | 121.8246 | -61.3129 | 60.3424 | -0.12794 | 0.007385 | 0.064756 | 0.066516 | -0.00020513 | -0.012239 | -0.0021597 | -0.1199 | 0.0044561 | 0.067268 | 0.056027 | -0.01367 | 0.028262 | -0.0068615 | -0.17853 | 60.1822 | -61.3449 | 60.3058 | -61.1618 | -61.615 | -61.5601 | -0.14191 | 60.1822 | -61.3449 | 60.2692 | -61.3312 | -61.4822 | -61.3907 | -0.032044 | -0.16022 | -0.036621 | 0.15106 | -0.24719 | -0.30212 | -0.21515 | -0.27008 | -0.032044 | -0.16022 | -0.073242 | -0.018311 | -0.07782 | -0.16937 | -0.045776 | -0.13733 | 0.18311 | 121.6507 | 0.013733 | 121.6141 | 121.5271 | 121.5271 | 121.4951 | 121.4951 | -121.6873 | -121.6873 | 121.6187 | 121.582 | 61.1343 | 61.171
980.75 | 121.9711 | -61.2808 | 60.2737 | -0.15846 | 0.0082394 | 0.066464 | 0.062671 | -0.0057593 | -0.0081796 | -0.0025869 | -0.037506 | 0.0031745 | 0.066413 | 0.049191 | -0.012388 | 0.027194 | -0.0060071 | -0.13275 | 60.141 | -61.3083 | 60.4065 | -61.0245 | -61.4914 | -61.4319 | 0.004578 | 60.1227 | -61.3541 | 60.4065 | -61.1938 | -61.322 | -61.2534 | -0.027466 | -0.13275 | 0.13275 | 0.25635 | -0.15106 | -0.21057 | -0.1236 | -0.1831 | -0.073242 | -0.15106 | 0.13275 | 0.086975 | 0.027466 | -0.041198 | 0.10071 | 0.032044 | 0.28381 | 121.7148 | 0.16022 | 121.7606 | 121.4493 | 121.4767 | 121.4218 | 121.4035 | -121.582 | -121.6278 | 121.6873 | 121.6873 | 61.1481 | 61.2854
982.4375 | 121.9391 | -61.2946 | 60.2966 | -0.11269 | 0.0065304 | 0.067105 | 0.059893 | -0.0040503 | -0.007966 | -0.0042959 | -0.080231 | 0.0031745 | 0.064063 | 0.05859 | -0.013029 | 0.025699 | -0.0034435 | -0.21973 | 60.1959 | -61.3541 | 60.3333 | -61.1298 | -61.5784 | -61.5189 | -0.091553 | 60.141 | -61.3358 | 60.3607 | -61.235 | -61.3632 | -61.2625 | -0.059509 | -0.10071 | 0.036621 | 0.16479 | -0.2243 | -0.28381 | -0.16479 | -0.2243 | -0.041198 | -0.15564 | 0.064087 | 0.05951 | 0.032044 | -0.068664 | 0.073242 | -0.027466 | 0.2243 | 121.6873 | 0.10071 | 121.6965 | 121.55 | 121.4767 | 121.4905 | 121.4355 | -121.6507 | -121.6324 | 121.6278 | 121.6553 | 61.0748 | 61.203
984.1875 | 121.9482 | -61.2671 | 60.2875 | -0.15083 | 0.0067442 | 0.064756 | 0.061175 | -0.0014867 | -0.0064706 | -0.0019461 | -0.040558 | 0.0044561 | 0.064277 | 0.045559 | -0.015165 | 0.024844 | -0.0017347 | -0.14191 | 60.141 | -61.3037 | 60.4156 | -61.0062 | -61.4822 | -61.4182 | 0.004578 | 60.1501 | -61.322 | 60.4065 | -61.1893 | -61.2946 | -61.2579 | -0.036621 | -0.14648 | 0.12817 | 0.26093 | -0.15106 | -0.21515 | -0.11444 | -0.17853 | -0.054931 | -0.13733 | 0.11902 | 0.07782 | 0.009155 | -0.027466 | 0.064086 | 0.027465 | 0.29755 | 121.7194 | 0.13275 | 121.7285 | 121.4447 | 121.4722 | 121.4081 | 121.4172 | -121.5912 | -121.6095 | 121.6827 | 121.6736 | 61.1252 | 61.2717
985.9375 | 121.8384 | -61.3312 | 60.3149 | -0.11269 | 0.0063168 | 0.066892 | 0.063952 | 0.0017175 | -0.0083932 | -0.0051505 | -0.12296 | 0.0055243 | 0.067909 | 0.054959 | -0.013029 | 0.025485 | -0.0030163 | -0.21057 | 60.2051 | -61.3586 | 60.2829 | -61.1938 | -61.6287 | -61.5875 | -0.19226 | 60.1547 | -61.3678 | 60.2737 | -61.3495 | -61.4822 | -61.3861 | -0.027466 | -0.10986 | -0.032043 | 0.13733 | -0.25635 | -0.29755 | -0.22888 | -0.27008 | -0.036621 | -0.16022 | -0.041198 | -0.01831 | -0.054931 | -0.15106 | -0.01831 | -0.11444 | 0.16479 | 121.6415 | 0.018311 | 121.6415 | 121.5637 | 121.5225 | 121.5363 | 121.4859 | -121.6736 | -121.6827 | 121.6141 | 121.6049 | 61.1206 | 61.1389
987.625 | 121.8384 | -61.2259 | 60.4065 | -0.06691 | 0.0063168 | 0.063901 | 0.062243 | -0.0036231 | -0.01117 | -0.0042959 | -0.046661 | 0.0057379 | 0.067054 | 0.05795 | -0.01367 | 0.025485 | -0.0060071 | -0.041199 | 60.26 | -61.2717 | 60.4065 | -61.0519 | -61.4822 | -61.4319 | 0.050354 | 60.2829 | -61.2625 | 60.347 | -61.2305 | -61.3541 | -61.3174 | -0.045776 | -0.14648 | 0 | 0.17395 | -0.20599 | -0.25635 | -0.16022 | -0.21057 | -0.036621 | -0.1236 | -0.059509 | -0.004578 | -0.091553 | -0.12817 | -0.054932 | -0.091553 | 0.21973 | 121.6782 | 0.032043 | 121.6095 | 121.5317 | 121.5454 | 121.4859 | 121.5088 | -121.6782 | -121.669 | 121.6324 | 121.5729 | 61.1847 | 61.2762
989.375 | 121.8567 | -61.235 | 60.4385 | -0.082169 | 0.003967 | 0.065824 | 0.060107 | -0.0029821 | -0.010102 | -0.0049367 | -0.013092 | 0.0059515 | 0.066627 | 0.050259 | -0.013029 | 0.023563 | -0.0032299 | 0.041199 | 60.2737 | -61.2534 | 60.4477 | -60.9833 | -61.409 | -61.3861 | 0.09613 | 60.2509 | -61.235 | 60.3745 | -61.203 | -61.322 | -61.2762 | -0.018311 | -0.16479 | 0.009155 | 0.25177 | -0.15106 | -0.17395 | -0.13275 | -0.15564 | 0 | -0.18768 | -0.064087 | 0.032043 | -0.041199 | -0.086975 | -0.041199 | -0.086975 | 0.27008 | 121.7011 | 0.032043 | 121.6095 | 121.5271 | 121.4859 | 121.5088 | 121.4859 | -121.6919 | -121.6736 | 121.6827 | 121.6095 | 61.2762 | 61.3312
991.125 | 121.8292 | -61.235 | 60.434 | -0.05928 | 0.0035398 | 0.065396 | 0.062884 | -0.0040503 | -0.0098886 | -0.0036551 | -0.052765 | 0.0044561 | 0.065559 | 0.053464 | -0.014097 | 0.026553 | -0.0032299 | -0.027466 | 60.2737 | -61.2717 | 60.4019 | -61.0657 | -61.4731 | -61.4456 | 0.050354 | 60.2783 | -61.2534 | 60.3516 | -61.2259 | -61.3495 | -61.2991 | -0.036621 | -0.16022 | -0.032043 | 0.16937 | -0.21057 | -0.23804 | -0.17395 | -0.20142 | -0.018311 | -0.15564 | -0.082398 | 0.009155 | -0.064087 | -0.11444 | -0.045776 | -0.09613 | 0.20599 | 121.6736 | 0.027466 | 121.6049 | 121.5454 | 121.5317 | 121.5088 | 121.5134 | -121.7056 | -121.6873 | 121.637 | 121.5866 | 61.2076 | 61.2854
992.875 | 121.8521 | -61.3495 | 60.3104 | -0.12794 | 0.0069578 | 0.067105 | 0.066089 | -0.0012731 | -0.0066844 | -0.0021597 | -0.080231 | 0.0070197 | 0.066627 | 0.053036 | -0.014524 | 0.025699 | -0.0047253 | -0.21057 | 60.173 | -61.3541 | 60.2829 | -61.1984 | -61.6379 | -61.5921 | -0.16479 | 60.1868 | -61.3815 | 60.2783 | -61.3495 | -61.4731 | -61.377 | -0.004578 | -0.13733 | -0.027466 | 0.15106 | -0.24261 | -0.28839 | -0.23804 | -0.28381 | -0.032044 | -0.1236 | -0.032044 | 0 | -0.027466 | -0.1236 | 0.004578 | -0.091552 | 0.15564 | 121.637 | 0.032044 | 121.6599 | 121.5271 | 121.5683 | 121.5225 | 121.5363 | -121.6644 | -121.6919 | 121.6324 | 121.6278 | 61.1389 | 61.1847
994.625 | 121.8613 | -61.2762 | 60.4248 | -0.05928 | 0.0048214 | 0.064115 | 0.063952 | -0.00063233 | -0.0081796 | -0.0023733 | -0.068024 | 0.0059515 | 0.066413 | 0.054104 | -0.014097 | 0.026981 | -0.0010937 | -0.041199 | 60.2783 | -61.2762 | 60.379 | -61.0748 | -61.496 | -61.4594 | 0.013733 | 60.2554 | -61.2762 | 60.3607 | -61.2167 | -61.3449 | -61.2991 | 0 | -0.14648 | -0.045777 | 0.20142 | -0.18311 | -0.21973 | -0.18311 | -0.21973 | 0 | -0.16937 | -0.064087 | 0.059509 | -0.022888 | -0.068665 | -0.022888 | -0.068665 | 0.20142 | 121.6553 | 0.059509 | 121.637 | 121.5546 | 121.5317 | 121.5546 | 121.5317 | -121.7011 | -121.7011 | 121.6553 | 121.637 | 61.235 | 61.29
996.3125 | 121.8521 | -61.322 | 60.3378 | -0.11269 | 0.0082394 | 0.065396 | 0.062457 | -0.0014867 | -0.0090342 | -0.0038687 | -0.083283 | 0.0050971 | 0.066627 | 0.053891 | -0.01367 | 0.02634 | -0.0038709 | -0.091553 | 60.2188 | -61.3174 | 60.3928 | -61.0703 | -61.5234 | -61.4777 | -0.018311 | 60.1959 | -61.3312 | 60.3287 | -61.2671 | -61.3953 | -61.3266 | 0.004577 | -0.11902 | 0.054931 | 0.25177 | -0.15564 | -0.20142 | -0.16022 | -0.20599 | -0.009156 | -0.14191 | -0.009156 | 0.054931 | -0.004578 | -0.073243 | 0.004578 | -0.064087 | 0.24719 | 121.7102 | 0.064087 | 121.6599 | 121.5363 | 121.5271 | 121.5408 | 121.5179 | -121.6553 | -121.669 | 121.7148 | 121.6507 | 61.2305 | 61.3037
998.0625 | 121.9574 | -61.2259 | 60.3928 | -0.16609 | 0.0031126 | 0.066892 | 0.059466 | -0.0027685 | -0.0081796 | -0.0040823 | 0.029632 | 0.0059515 | 0.066627 | 0.046414 | -0.014311 | 0.026553 | -0.0034435 | -0.073242 | 60.2051 | -61.2762 | 60.4202 | -61.0016 | -61.4365 | -61.3815 | 0.068665 | 60.1822 | -61.2717 | 60.4385 | -61.1206 | -61.2167 | -61.2076 | -0.050354 | -0.18768 | 0.027466 | 0.2243 | -0.15564 | -0.21057 | -0.10529 | -0.16022 | -0.045776 | -0.21057 | 0.045777 | 0.10529 | 0.01831 | 0.009155 | 0.064086 | 0.054931 | 0.27466 | 121.6965 | 0.15106 | 121.7102 | 121.4813 | 121.4539 | 121.431 | 121.4081 | -121.669 | -121.6644 | 121.6461 | 121.6644 | 61.1526 | 61.2946
999.8125 | 121.8842 | -61.2946 | 60.3516 | -0.097427 | 0.0067442 | 0.065824 | 0.063952 | 0.00022207 | -0.0073252 | -0.0034415 | -0.10464 | 0.0038153 | 0.064918 | 0.054318 | -0.014951 | 0.025058 | -0.0032299 | -0.064087 | 60.2051 | -61.3037 | 60.3973 | -61.0428 | -61.4914 | -61.4639 | 0.036621 | 60.2188 | -61.29 | 60.3516 | -61.235 | -61.3632 | -61.3037 | -0.009155 | -0.14648 | 0.045777 | 0.25177 | -0.16937 | -0.19684 | -0.16022 | -0.18768 | 0.004578 | -0.13275 | 0 | 0.05951 | -0.009155 | -0.068664 | -0.013733 | -0.073242 | 0.26093 | 121.7011 | 0.054932 | 121.6415 | 121.5088 | 121.5088 | 121.4996 | 121.5134 | -121.6553 | -121.6415 | 121.6919 | 121.6461 | 61.2305 | 61.3312
1001.5625 | 121.9345 | -61.2396 | 60.3882 | -0.12032 | 0.0071714 | 0.066251 | 0.059893 | 0.0017175 | -0.010743 | -0.00066434 | 0.011322 | 0.0048833 | 0.0662 | 0.045773 | -0.013242 | 0.025058 | -0.00023931 | -0.068665 | 60.2325 | -61.235 | 60.4294 | -61.0153 | -61.4548 | -61.4044 | 0.041199 | 60.2005 | -61.2671 | 60.4156 | -61.171 | -61.2488 | -61.2305 | 0.004578 | -0.15564 | 0.041198 | 0.2243 | -0.16479 | -0.21515 | -0.16937 | -0.21973 | -0.027466 | -0.18768 | 0.027465 | 0.068665 | 0.009155 | -0.009155 | 0.036621 | 0.018311 | 0.21973 | 121.6644 | 0.096131 | 121.6827 | 121.4676 | 121.4676 | 121.4722 | 121.4401 | -121.6232 | -121.6553 | 121.669 | 121.6553 | 61.171 | 61.2808
1003.25 | 121.9574 | -61.2579 | 60.2966 | -0.15846 | 0.0095212 | 0.067319 | 0.062884 | 0.0017175 | -0.0073252 | -0.0017325 | -0.058869 | 0.0038153 | 0.064704 | 0.05859 | -0.014311 | 0.024204 | -0.0066479 | -0.13275 | 60.1501 | -61.3083 | 60.4065 | -61.0291 | -61.5005 | -61.4365 | 0.013733 | 60.1227 | -61.3266 | 60.4019 | -61.1938 | -61.2991 | -61.2534 | -0.050354 | -0.14648 | 0.10986 | 0.22888 | -0.17853 | -0.24261 | -0.12817 | -0.19226 | -0.068664 | -0.17395 | 0.10529 | 0.064087 | 0.004578 | -0.041198 | 0.073242 | 0.027466 | 0.27924 | 121.7148 | 0.13275 | 121.7285 | 121.4584 | 121.4493 | 121.4081 | 121.3806 | -121.6049 | -121.6232 | 121.6644 | 121.6599 | 61.1252 | 61.2717
1005 | 121.9803 | -61.1801 | 60.4111 | -0.097427 | 0.0046078 | 0.064542 | 0.060107 | -0.0019141 | -0.0090342 | -0.0017325 | -0.019196 | 0.0031745 | 0.065559 | 0.059231 | -0.014097 | 0.024844 | -0.0077161 | 0.050354 | 60.2325 | -61.203 | 60.5392 | -60.9055 | -61.3312 | -61.2946 | 0.2243 | 60.2371 | -61.2259 | 60.4706 | -61.0748 | -61.1938 | -61.1664 | -0.022888 | -0.17853 | 0.12817 | 0.27466 | -0.11444 | -0.15106 | -0.091553 | -0.12817 | -0.045776 | -0.17395 | 0.059509 | 0.10529 | 0.013733 | -0.013733 | 0.059509 | 0.032043 | 0.29755 | 121.7422 | 0.15106 | 121.6965 | 121.4355 | 121.463 | 121.4127 | 121.4172 | -121.6141 | -121.637 | 121.7194 | 121.6507 | 61.2305 | 61.4044
1006.7344 | 121.8658 | -61.203 | 60.4294 | -0.10506 | 0.0050352 | 0.066678 | 0.059893 | -0.0036231 | -0.008607 | -0.0032277 | -0.016144 | 0.0048833 | 0.0662 | 0.047055 | -0.015592 | 0.026767 | -0.0062207 | 0.064087 | 60.2463 | -61.2396 | 60.5026 | -60.9604 | -61.377 | -61.3449 | 0.15106 | 60.2463 | -61.235 | 60.4019 | -61.171 | -61.2946 | -61.2442 | -0.036621 | -0.1831 | 0.073243 | 0.24262 | -0.14191 | -0.17395 | -0.10529 | -0.13733 | -0.032043 | -0.1831 | -0.027465 | 0.032044 | -0.041199 | -0.091553 | -0.009156 | -0.05951 | 0.27924 | 121.7422 | 0.064087 | 121.637 | 121.4859 | 121.4813 | 121.4493 | 121.4493 | -121.669 | -121.6644 | 121.7056 | 121.6049 | 61.2671 | 61.3541
1008.4844 | 121.9162 | -61.2122 | 60.4294 | -0.15846 | 0.0058896 | 0.063687 | 0.05968 | -0.0014867 | -0.011598 | -0.0010915 | -0.019196 | 0.0029607 | 0.065772 | 0.059659 | -0.014738 | 0.024631 | -0.0062207 | 0.054932 | 60.2509 | -61.235 | 60.498 | -60.9421 | -61.3541 | -61.3312 | 0.17853 | 60.2417 | -61.2396 | 60.4477 | -61.1298 | -61.2488 | -61.2213 | -0.022888 | -0.17853 | 0.068665 | 0.27008 | -0.11902 | -0.14191 | -0.096131 | -0.11902 | -0.027466 | -0.18768 | 0.018311 | 0.082397 | -0.009155 | -0.036621 | 0.018311 | -0.009155 | 0.29297 | 121.7331 | 0.10986 | 121.6873 | 121.4859 | 121.4813 | 121.463 | 121.4539 | -121.6644 | -121.669 | 121.7102 | 121.6599 | 61.2671 | 61.3907
1010.1562 | 121.9803 | -61.2717 | 60.2921 | -0.13557 | 0.005676 | 0.065183 | 0.063952 | -0.0014867 | -0.0083932 | -0.0019461 | -0.049713 | 0.0040289 | 0.063636 | 0.046841 | -0.015165 | 0.027408 | -0.0045117 | -0.12817 | 60.1547 | -61.2991 | 60.4065 | -61.0382 | -61.496 | -61.441 | -0.004578 | 60.1318 | -61.3266 | 60.4065 | -61.1938 | -61.3083 | -61.2671 | -0.027466 | -0.13733 | 0.11444 | 0.23346 | -0.16937 | -0.22431 | -0.14191 | -0.19684 | -0.054932 | -0.16022 | 0.11444 | 0.077819 | 0.004577 | -0.036622 | 0.059509 | 0.01831 | 0.26093 | 121.7056 | 0.13275 | 121.7331 | 121.4539 | 121.4584 | 121.4264 | 121.4035 | -121.5912 | -121.6187 | 121.6782 | 121.6782 | 61.1435 | 61.2671
1011.9062 | 121.9299 | -61.2442 | 60.3607 | -0.15846 | 0.0067442 | 0.066892 | 0.061175 | -0.00041873 | -0.008607 | -0.0032277 | -0.034454 | 0.0046697 | 0.064277 | 0.043637 | -0.015165 | 0.023563 | -0.0064343 | -0.11444 | 60.1822 | -61.2946 | 60.4156 | -61.0062 | -61.4868 | -61.4227 | 0.036621 | 60.1685 | -61.29 | 60.4065 | -61.2259 | -61.3083 | -61.2579 | -0.050354 | -0.17853 | 0.054931 | 0.23804 | -0.17853 | -0.24261 | -0.12817 | -0.19226 | -0.045776 | -0.19226 | 0.045776 | 0.018311 | -0.013733 | -0.064087 | 0.032043 | -0.018311 | 0.28839 | 121.7102 | 0.064087 | 121.6965 | 121.4767 | 121.4584 | 121.4264 | 121.4127 | -121.6553 | -121.6507 | 121.6599 | 121.6507 | 61.1298 | 61.2808
1013.5781 | 121.9482 | -61.2122 | 60.4156 | -0.06691 | 0.0063168 | 0.066464 | 0.058184 | -0.00084593 | -0.0066844 | -0.0017325 | -0.0069885 | 0.0053107 | 0.066627 | 0.052182 | -0.014097 | 0.024844 | -0.0030163 | -0.054932 | 60.2097 | -61.2442 | 60.4431 | -61.0107 | -61.4502 | -61.3815 | 0.064087 | 60.2188 | -61.2671 | 60.4431 | -61.1252 | -61.235 | -61.203 | -0.032044 | -0.20599 | 0.027466 | 0.20142 | -0.16937 | -0.23804 | -0.13733 | -0.20599 | -0.054932 | -0.19684 | 0.027466 | 0.086975 | 0.009155 | -0.022888 | 0.064087 | 0.032044 | 0.23346 | 121.6873 | 0.14191 | 121.7102 | 121.4539 | 121.4859 | 121.4218 | 121.431 | -121.6599 | -121.6827 | 121.6553 | 121.6553 | 61.1572 | 61.2762
1015.3125 | 122.0032 | -61.1938 | 60.4111 | -0.06691 | 0.0067442 | 0.064542 | 0.062671 | 0.0012903 | -0.010743 | -0.0017325 | -0.0039367 | 0.0055243 | 0.067909 | 0.049832 | -0.014097 | 0.024631 | -0.0047253 | 0.041199 | 60.2188 | -61.2259 | 60.5255 | -60.91 | -61.3495 | -61.2991 | 0.22888 | 60.2188 | -61.2122 | 60.5164 | -61.0748 | -61.1893 | -61.1572 | -0.032043 | -0.19226 | 0.11444 | 0.28381 | -0.10528 | -0.15564 | -0.073242 | -0.1236 | -0.01831 | -0.19226 | 0.10529 | 0.11902 | 0.036621 | 0.004578 | 0.054931 | 0.022888 | 0.31586 | 121.7514 | 0.13733 | 121.7285 | 121.4447 | 121.431 | 121.4127 | 121.4127 | -121.637 | -121.6232 | 121.7194 | 121.7102 | 61.235 | 61.4227
1017.0625 | 121.9482 | -61.2762 | 60.3104 | -0.12032 | 0.005676 | 0.065183 | 0.062457 | -0.0010595 | -0.0088206 | -0.0049367 | -0.058869 | 0.0023199 | 0.065559 | 0.051541 | -0.015592 | 0.025272 | -0.0025891 | -0.13275 | 60.141 | -61.3174 | 60.4385 | -61.0062 | -61.4685 | -61.4182 | 0.022888 | 60.1364 | -61.3129 | 60.4294 | -61.1755 | -61.2991 | -61.2579 | -0.041199 | -0.16937 | 0.12817 | 0.27008 | -0.14191 | -0.19226 | -0.10071 | -0.15106 | -0.036621 | -0.17395 | 0.11902 | 0.10071 | 0.01831 | -0.022888 | 0.054931 | 0.013733 | 0.31128 | 121.756 | 0.13733 | 121.7422 | 121.4584 | 121.4493 | 121.4172 | 121.4127 | -121.6278 | -121.6232 | 121.7148 | 121.7056 | 61.1435 | 61.2991
1018.7344 | 121.8338 | -61.3449 | 60.3424 | -0.089798 | 0.0050352 | 0.062833 | 0.064593 | 0.0032129 | -0.0092478 | -0.0017325 | -0.13821 | 0.0044561 | 0.067054 | 0.056454 | -0.014951 | 0.027835 | -0.0010937 | -0.20142 | 60.1959 | -61.3724 | 60.2737 | -61.2213 | -61.647 | -61.5784 | -0.17395 | 60.1959 | -61.3861 | 60.2829 | -61.3586 | -61.5005 | -61.3907 | -0.027465 | -0.14648 | -0.068664 | 0.1236 | -0.23346 | -0.30212 | -0.20599 | -0.27466 | -0.041198 | -0.14648 | -0.059509 | -0.013733 | -0.045776 | -0.15564 | -0.004578 | -0.11444 | 0.15106 | 121.6461 | 0.027465 | 121.669 | 121.5683 | 121.582 | 121.5408 | 121.5408 | -121.7148 | -121.7285 | 121.6187 | 121.6278 | 61.1435 | 61.171
1020.4844 | 121.9116 | -61.235 | 60.3745 | -0.16609 | 0.0048214 | 0.06561 | 0.061389 | -0.00020513 | -0.009675 | -0.0028005 | -0.022247 | 0.0048833 | 0.065559 | 0.048337 | -0.015165 | 0.024204 | -0.0049389 | -0.082397 | 60.2097 | -61.2808 | 60.4294 | -61.0291 | -61.4639 | -61.409 | 0.032043 | 60.1959 | -61.29 | 60.3973 | -61.1893 | -61.3129 | -61.2488 | -0.045777 | -0.16479 | 0.054931 | 0.20599 | -0.17395 | -0.22888 | -0.12817 | -0.18311 | -0.054932 | -0.17853 | 0.022888 | 0.045776 | -0.013733 | -0.07782 | 0.041199 | -0.022888 | 0.25177 | 121.7102 | 0.10071 | 121.6873 | 121.4905 | 121.4859 | 121.4447 | 121.431 | -121.6553 | -121.6644 | 121.6644 | 121.6324 | 61.1526 | 61.2671
1022.25 | 121.8887 | -61.3266 | 60.3104 | -0.11269 | 0.005676 | 0.064969 | 0.062671 | -0.00041873 | -0.0073252 | -0.0060049 | -0.1077 | 0.0040289 | 0.067054 | 0.047055 | -0.014738 | 0.026553 | -0.0066479 | -0.20599 | 60.1913 | -61.3449 | 60.3149 | -61.1664 | -61.6196 | -61.5555 | -0.13733 | 60.1913 | -61.3358 | 60.3012 | -61.3266 | -61.441 | -61.3724 | -0.018311 | -0.11902 | 0.004577 | 0.16022 | -0.22888 | -0.29297 | -0.21057 | -0.27466 | -0.009155 | -0.11902 | -0.009156 | 0 | -0.045776 | -0.11444 | -0.036621 | -0.10529 | 0.17853 | 121.6599 | 0.009155 | 121.637 | 121.5363 | 121.5271 | 121.5179 | 121.5179 | -121.6553 | -121.6461 | 121.6415 | 121.6278 | 61.1206 | 61.1893
1023.9375 | 121.8842 | -61.2762 | 60.3516 | -0.074539 | 0.0058896 | 0.065396 | 0.061602 | 0.0010767 | -0.010316 | -0.0045095 | -0.10159 | 0.0053107 | 0.066413 | 0.052395 | -0.013242 | 0.026553 | -0.0062207 | -0.050354 | 60.2463 | -61.3037 | 60.3928 | -61.0565 | -61.4914 | -61.4594 | 0.050354 | 60.2142 | -61.2946 | 60.3745 | -61.2122 | -61.3632 | -61.2946 | -0.027466 | -0.10529 | 0.041199 | 0.21973 | -0.18311 | -0.21515 | -0.15564 | -0.18768 | -0.018311 | -0.13733 | 0.022889 | 0.064087 | -0.018311 | -0.086975 | 0 | -0.068664 | 0.24719 | 121.6965 | 0.082398 | 121.669 | 121.55 | 121.5088 | 121.5225 | 121.4905 | -121.6553 | -121.6461 | 121.669 | 121.6507 | 61.2259 | 61.3266
1025.6719 | 121.8613 | -61.322 | 60.3195 | -0.089798 | 0.0069578 | 0.065183 | 0.061816 | 8.47e-06 | -0.007966 | -0.0040823 | -0.086334 | 0.0061651 | 0.064918 | 0.057522 | -0.012602 | 0.025272 | -0.0017347 | -0.22888 | 60.1685 | -61.3495 | 60.2783 | -61.1893 | -61.6516 | -61.5829 | -0.16479 | 60.1868 | -61.377 | 60.2692 | -61.3266 | -61.4502 | -61.3724 | -0.027466 | -0.15106 | -0.041199 | 0.13275 | -0.26093 | -0.32959 | -0.23346 | -0.30212 | -0.054932 | -0.13275 | -0.050354 | -0.004578 | -0.050354 | -0.12817 | 0.004578 | -0.073242 | 0.16022 | 121.6278 | 0.050354 | 121.6461 | 121.5179 | 121.5637 | 121.4905 | 121.5088 | -121.669 | -121.6965 | 121.6003 | 121.5912 | 61.0931 | 61.1572
1027.4219 | 121.8292 | -61.2213 | 60.4385 | -0.051651 | 0.0050352 | 0.064115 | 0.061816 | -0.0023413 | -0.010316 | -0.0019461 | -0.052765 | 0.0055243 | 0.067054 | 0.056454 | -0.011961 | 0.026126 | -0.0040845 | -0.032043 | 60.2921 | -61.2579 | 60.3973 | -61.0657 | -61.4777 | -61.4319 | 0.050354 | 60.2692 | -61.2396 | 60.3607 | -61.2259 | -61.3541 | -61.29 | -0.036622 | -0.14648 | -0.041199 | 0.15564 | -0.21057 | -0.25635 | -0.17395 | -0.21973 | -0.018311 | -0.16937 | -0.07782 | -0.004578 | -0.068665 | -0.13275 | -0.050354 | -0.11444 | 0.19226 | 121.6553 | 0.013733 | 121.6003 | 121.55 | 121.5088 | 121.5134 | 121.4905 | -121.6965 | -121.6782 | 121.6187 | 121.582 | 61.1893 | 61.2717
1029.1875 | 121.8796 | -61.2717 | 60.3516 | -0.074539 | 0.0086668 | 0.066892 | 0.062671 | -0.00084593 | -0.010743 | -0.0025869 | -0.055817 | 0.0046697 | 0.0662 | 0.053891 | -0.012388 | 0.025485 | -0.0051525 | -0.064087 | 60.2234 | -61.29 | 60.3973 | -61.0428 | -61.5005 | -61.4594 | 0.022888 | 60.2097 | -61.3083 | 60.3607 | -61.2213 | -61.3632 | -61.2991 | -0.018311 | -0.12817 | 0.045777 | 0.22888 | -0.18768 | -0.22888 | -0.16937 | -0.21057 | -0.036622 | -0.14191 | 0.009156 | 0.050354 | -0.027466 | -0.091553 | 0.009156 | -0.054931 | 0.24719 | 121.6873 | 0.086976 | 121.669 | 121.5134 | 121.5179 | 121.4951 | 121.4813 | -121.6415 | -121.6599 | 121.669 | 121.6324 | 61.2076 | 61.2946
1030.875 | 121.8658 | -61.29 | 60.3653 | -0.089798 | 0.0061032 | 0.064328 | 0.061816 | -0.00020513 | -0.010102 | 0.00019006 | -0.09549 | 0.0044561 | 0.067481 | 0.050259 | -0.014738 | 0.027408 | -0.0032299 | -0.082397 | 60.2097 | -61.3129 | 60.3882 | -61.0703 | -61.5143 | -61.4822 | -0.004578 | 60.2097 | -61.3449 | 60.3516 | -61.2625 | -61.3998 | -61.3174 | -0.022888 | -0.15564 | 0.022889 | 0.21973 | -0.19226 | -0.2243 | -0.16937 | -0.20142 | -0.054932 | -0.15564 | -0.013733 | 0.027466 | -0.027466 | -0.10986 | 0.027466 | -0.054931 | 0.24262 | 121.7011 | 0.082398 | 121.6965 | 121.5225 | 121.5546 | 121.4996 | 121.4996 | -121.6782 | -121.7102 | 121.6782 | 121.6415 | 61.2076 | 61.2854
1032.6406 | 121.8842 | -61.2534 | 60.3745 | -0.11269 | 0.005676 | 0.065824 | 0.060321 | 0.00086307 | -0.0081796 | -0.0045095 | -0.064972 | 0.0040289 | 0.066841 | 0.055173 | -0.014951 | 0.026767 | -0.0062207 | -0.045776 | 60.2692 | -61.2991 | 60.3973 | -61.0657 | -61.496 | -61.4731 | 0.018311 | 60.2234 | -61.2808 | 60.3699 | -61.2167 | -61.3586 | -61.2808 | -0.045776 | -0.10529 | 0.022888 | 0.18768 | -0.21973 | -0.24262 | -0.17395 | -0.19684 | -0.027466 | -0.15106 | -0.004578 | 0.036621 | -0.027466 | -0.10529 | 0 | -0.07782 | 0.23346 | 121.6965 | 0.064087 | 121.6507 | 121.5683 | 121.5042 | 121.5225 | 121.4767 | -121.6736 | -121.6553 | 121.6507 | 121.6232 | 61.2076 | 61.2717
1034.3281 | 121.907 | -61.2396 | 60.3424 | -0.13557 | 0.008453 | 0.065183 | 0.060962 | -0.0012731 | -0.0071116 | -0.0030141 | -0.0008851 | 0.0038153 | 0.065986 | 0.047909 | -0.013883 | 0.02399 | -0.0038709 | -0.10071 | 60.1868 | -61.2717 | 60.4111 | -61.0199 | -61.4731 | -61.4182 | 0.022888 | 60.1593 | -61.2991 | 60.3745 | -61.1984 | -61.2991 | -61.2625 | -0.032043 | -0.15564 | 0.068665 | 0.21973 | -0.17853 | -0.23346 | -0.14648 | -0.20142 | -0.059509 | -0.18311 | 0.032044 | 0.041199 | -0.022888 | -0.059509 | 0.036621 | 0 | 0.25177 | 121.6827 | 0.10071 | 121.6736 | 121.4584 | 121.4584 | 121.4264 | 121.3989 | -121.6141 | -121.6415 | 121.6507 | 121.6141 | 61.1389 | 61.2625
1036.0625 | 121.8384 | -61.2579 | 60.4156 | -0.044022 | 0.0046078 | 0.066678 | 0.061816 | 0.0025721 | -0.012239 | -0.0019461 | -0.049713 | 0.0044561 | 0.066841 | 0.049618 | -0.014097 | 0.025272 | -0.0038709 | -0.027466 | 60.3058 | -61.2534 | 60.379 | -61.0611 | -61.4731 | -61.4594 | 0.013733 | 60.2783 | -61.2579 | 60.347 | -61.2488 | -61.3586 | -61.2991 | 0.004578 | -0.10986 | -0.036621 | 0.19684 | -0.20142 | -0.21515 | -0.20599 | -0.21973 | 0 | -0.13733 | -0.068664 | 0.009156 | -0.041198 | -0.10071 | -0.041198 | -0.10071 | 0.19226 | 121.6324 | 0.009156 | 121.6049 | 121.5591 | 121.5363 | 121.5637 | 121.5363 | -121.669 | -121.6736 | 121.637 | 121.6049 | 61.2305 | 61.2717
1037.75 | 121.8796 | -61.2854 | 60.3745 | -0.097427 | 0.0046078 | 0.065396 | 0.060748 | -0.0010595 | -0.008607 | -0.0019461 | -0.071076 | 0.0070197 | 0.065559 | 0.050259 | -0.014524 | 0.026553 | -0.00045291 | -0.050354 | 60.2737 | -61.3037 | 60.4019 | -61.0703 | -61.4731 | -61.4548 | 0.009155 | 60.2371 | -61.3083 | 60.3607 | -61.2396 | -61.3495 | -61.3083 | -0.018311 | -0.10071 | 0.027466 | 0.21515 | -0.16937 | -0.18768 | -0.15106 | -0.16937 | -0.022889 | -0.13733 | -0.013733 | 0.045776 | -0.022889 | -0.064087 | 0 | -0.041198 | 0.23346 | 121.7056 | 0.068665 | 121.669 | 121.5775 | 121.5454 | 121.5591 | 121.5225 | -121.6782 | -121.6827 | 121.6873 | 121.6461 | 61.235 | 61.2946
1039.4844 | 121.8338 | -61.3037 | 60.3104 | -0.10506 | 0.008453 | 0.066037 | 0.062671 | 0.0017175 | -0.0075388 | -0.00045074 | -0.098541 | 0.0044561 | 0.065345 | 0.056668 | -0.012602 | 0.028262 | -0.0053661 | -0.14648 | 60.2142 | -61.3266 | 60.3241 | -61.1481 | -61.6013 | -61.5509 | -0.11902 | 60.1959 | -61.3724 | 60.2875 | -61.3358 | -61.4548 | -61.3724 | -0.022888 | -0.096131 | 0.013733 | 0.15564 | -0.24719 | -0.29755 | -0.2243 | -0.27466 | -0.068664 | -0.11444 | -0.022888 | -0.032043 | -0.068664 | -0.15106 | 0 | -0.082398 | 0.17853 | 121.6507 | 0.036621 | 121.6599 | 121.5408 | 121.5683 | 121.5179 | 121.4996 | -121.637 | -121.6827 | 121.6278 | 121.5912 | 61.1572 | 61.1847
1041.2344 | 121.9482 | -61.2717 | 60.3012 | -0.22713 | 0.0063168 | 0.064969 | 0.061389 | -0.0029821 | -0.0071116 | -2.3544e-05 | -0.028351 | 0.0053107 | 0.063209 | 0.051755 | -0.014524 | 0.026553 | -0.0064343 | -0.12817 | 60.1776 | -61.322 | 60.4111 | -61.0336 | -61.4822 | -61.441 | 0.004578 | 60.1089 | -61.3312 | 60.4019 | -61.2076 | -61.3174 | -61.2396 | -0.050354 | -0.1236 | 0.10986 | 0.23804 | -0.16937 | -0.21057 | -0.11902 | -0.16022 | -0.05951 | -0.19226 | 0.10071 | 0.064086 | 0.032043 | -0.045777 | 0.091553 | 0.013733 | 0.28839 | 121.7331 | 0.1236 | 121.7331 | 121.4996 | 121.4401 | 121.4493 | 121.3806 | -121.6232 | -121.6324 | 121.6827 | 121.6736 | 61.1435 | 61.2762
1042.9844 | 121.9574 | -61.1893 | 60.3973 | -0.1432 | 0.0048214 | 0.065396 | 0.059466 | -0.0017005 | -0.0090342 | -0.0019461 | 0.0052185 | 0.0033881 | 0.064918 | 0.052609 | -0.014524 | 0.026981 | -0.00066651 | 0.054932 | 60.2509 | -61.2213 | 60.5301 | -60.8963 | -61.3495 | -61.3129 | 0.19226 | 60.2371 | -61.2167 | 60.4889 | -61.1023 | -61.203 | -61.1755 | -0.032043 | -0.14649 | 0.13275 | 0.29297 | -0.1236 | -0.16022 | -0.091553 | -0.12817 | -0.027466 | -0.16022 | 0.091553 | 0.086975 | 0.013733 | -0.013733 | 0.041199 | 0.013733 | 0.32501 | 121.7514 | 0.11444 | 121.7056 | 121.4722 | 121.4539 | 121.4401 | 121.4264 | -121.6187 | -121.6141 | 121.7194 | 121.6782 | 61.2442 | 61.3815
1044.6719 | 121.9574 | -61.2442 | 60.3195 | -0.1432 | 0.007385 | 0.066251 | 0.061389 | 0.00022207 | -0.0092478 | -0.0032277 | -0.013092 | 0.0053107 | 0.06385 | 0.049405 | -0.01367 | 0.026553 | -0.0045117 | -0.12817 | 60.1501 | -61.29 | 60.434 | -61.0107 | -61.4868 | -61.4319 | 0.027466 | 60.1685 | -61.3129 | 60.4019 | -61.1938 | -61.2991 | -61.2579 | -0.045776 | -0.16937 | 0.11444 | 0.23346 | -0.18768 | -0.24261 | -0.14191 | -0.19684 | -0.068664 | -0.15106 | 0.082398 | 0.050354 | -0.013733 | -0.054931 | 0.054931 | 0.013733 | 0.27924 | 121.7239 | 0.11902 | 121.7148 | 121.4401 | 121.4813 | 121.3943 | 121.4127 | -121.6095 | -121.6324 | 121.6782 | 121.6461 | 61.116 | 61.2717
1046.4062 | 121.9528 | -61.2534 | 60.3104 | -0.1432 | 0.0080258 | 0.065183 | 0.061602 | -0.0051183 | -0.0083932 | -0.0036551 | -0.031403 | 0.0042425 | 0.064277 | 0.060513 | -0.014951 | 0.025485 | -0.0053661 | -0.13275 | 60.1318 | -61.2946 | 60.4156 | -61.0291 | -61.4777 | -61.441 | 0.009155 | 60.141 | -61.3174 | 60.4065 | -61.1984 | -61.3083 | -61.2305 | -0.041199 | -0.17853 | 0.10529 | 0.2243 | -0.18768 | -0.2243 | -0.14648 | -0.1831 | -0.064087 | -0.16937 | 0.09613 | 0.054932 | 0.022888 | -0.054932 | 0.086975 | 0.009155 | 0.2655 | 121.7102 | 0.11902 | 121.7239 | 121.4264 | 121.4584 | 121.3852 | 121.3943 | -121.6049 | -121.6278 | 121.669 | 121.6599 | 61.1206 | 61.2625
1048.1562 | 121.9757 | -61.2122 | 60.3745 | -0.18135 | 0.0050352 | 0.063901 | 0.060962 | -0.0042639 | -0.0094614 | -0.0021597 | 0.011322 | 0.0038153 | 0.067054 | 0.055173 | -0.014738 | 0.026126 | -0.0062207 | -0.036621 | 60.2371 | -61.2534 | 60.4706 | -60.9741 | -61.3861 | -61.3358 | 0.14191 | 60.2142 | -61.235 | 60.466 | -61.1069 | -61.2076 | -61.1801 | -0.041199 | -0.13733 | 0.09613 | 0.23804 | -0.1236 | -0.17395 | -0.082397 | -0.13275 | -0.022888 | -0.16022 | 0.091552 | 0.10529 | 0.032043 | 0.004577 | 0.054931 | 0.027465 | 0.27924 | 121.7239 | 0.12817 | 121.701 | 121.4905 | 121.4493 | 121.4493 | 121.4264 | -121.6278 | -121.6095 | 121.6827 | 121.6782 | 61.1755 | 61.3541
1049.8281 | 121.843 | -61.322 | 60.347 | -0.16609 | 0.0054624 | 0.066678 | 0.06502 | -0.00020513 | -0.0077524 | -0.0010915 | -0.13211 | 0.0050971 | 0.067695 | 0.0556 | -0.014951 | 0.027621 | -0.0055799 | -0.10986 | 60.228 | -61.3266 | 60.3607 | -61.1206 | -61.5555 | -61.5097 | -0.064087 | 60.1868 | -61.3358 | 60.2966 | -61.3266 | -61.4594 | -61.3724 | -0.004578 | -0.11902 | 0.013733 | 0.20142 | -0.18768 | -0.23346 | -0.18311 | -0.22888 | -0.013733 | -0.16022 | -0.050354 | -0.004578 | -0.050354 | -0.13733 | -0.036621 | -0.1236 | 0.20599 | 121.6873 | 0.009155 | 121.6324 | 121.5546 | 121.5225 | 121.55 | 121.5088 | -121.6736 | -121.6827 | 121.6827 | 121.6187 | 61.2122 | 61.2579
1051.5781 | 121.8567 | -61.3266 | 60.3424 | -0.12032 | 0.0075986 | 0.066251 | 0.063098 | -0.0027685 | -0.0081796 | -0.0021597 | -0.089386 | 0.0063787 | 0.062782 | 0.053891 | -0.013029 | 0.024417 | -0.0064343 | -0.21515 | 60.2234 | -61.3632 | 60.2692 | -61.2076 | -61.6333 | -61.5738 | -0.16937 | 60.173 | -61.3586 | 60.2829 | -61.3495 | -61.4685 | -61.3632 | -0.036621 | -0.11902 | -0.073242 | 0.11902 | -0.24719 | -0.3067 | -0.21057 | -0.27008 | -0.032044 | -0.16937 | -0.059509 | -0.022888 | -0.036621 | -0.14191 | -0.004577 | -0.10986 | 0.15564 | 121.6324 | 0.009156 | 121.6415 | 121.5866 | 121.5317 | 121.55 | 121.4996 | -121.7056 | -121.7011 | 121.5958 | 121.6095 | 61.1115 | 61.1572
1053.3281 | 121.8933 | -61.2534 | 60.3561 | -0.074539 | 0.007385 | 0.063474 | 0.061816 | 0.0019311 | -0.01053 | 0.00019006 | -0.10159 | 0.0057379 | 0.065559 | 0.060513 | -0.01367 | 0.025272 | -0.0055799 | -0.068665 | 60.2234 | -61.3312 | 60.3973 | -61.0519 | -61.496 | -61.4685 | 0.013733 | 60.2188 | -61.3083 | 60.3607 | -61.2396 | -61.3586 | -61.3083 | -0.07782 | -0.13275 | 0.041199 | 0.20142 | -0.21515 | -0.24262 | -0.13733 | -0.1648 | -0.054932 | -0.13733 | 0.004578 | 0.013733 | -0.054932 | -0.10529 | 0 | -0.050354 | 0.27924 | 121.7285 | 0.068665 | 121.669 | 121.5546 | 121.5271 | 121.4767 | 121.4722 | -121.6873 | -121.6644 | 121.6507 | 121.6141 | 61.1847 | 61.2671
1055.0625 | 121.8384 | -61.2991 | 60.3424 | -0.1432 | 0.0080258 | 0.06561 | 0.062457 | 0.0049219 | -0.0083932 | -0.0070731 | -0.080231 | 0.0059515 | 0.067909 | 0.054959 | -0.013883 | 0.026767 | -0.00045291 | -0.1236 | 60.2188 | -61.322 | 60.3607 | -61.1114 | -61.5601 | -61.528 | -0.082397 | 60.1822 | -61.3586 | 60.2966 | -61.322 | -61.4502 | -61.3815 | -0.022888 | -0.1236 | 0.018311 | 0.18768 | -0.22888 | -0.26093 | -0.20599 | -0.23804 | -0.05951 | -0.16022 | -0.045776 | -0.022888 | -0.082398 | -0.15106 | -0.022888 | -0.091552 | 0.21057 | 121.6827 | 0.036622 | 121.6553 | 121.5408 | 121.5408 | 121.5179 | 121.4813 | -121.6644 | -121.7011 | 121.6599 | 121.5958 | 61.1755 | 61.2167
1056.75 | 121.8933 | -61.29 | 60.3882 | -0.05928 | 0.0048214 | 0.062833 | 0.060321 | -0.0038367 | -0.01117 | -0.0017325 | -0.074127 | 0.0046697 | 0.064491 | 0.055813 | -0.012174 | 0.02634 | -0.0036573 | -0.050354 | 60.2646 | -61.2854 | 60.3882 | -61.0611 | -61.4777 | -61.4594 | 0 | 60.228 | -61.3037 | 60.3561 | -61.2213 | -61.3541 | -61.3129 | 0.004578 | -0.1236 | 0 | 0.22888 | -0.16937 | -0.18768 | -0.17395 | -0.19226 | -0.013733 | -0.16022 | -0.032044 | 0.068665 | -0.022888 | -0.064087 | -0.009155 | -0.050354 | 0.2243 | 121.6736 | 0.082398 | 121.6599 | 121.55 | 121.5317 | 121.5546 | 121.5179 | -121.6736 | -121.6919 | 121.6782 | 121.6461 | 61.2396 | 61.29
1058.4844 | 121.9803 | -61.2946 | 60.2692 | -0.15083 | 0.0086668 | 0.067105 | 0.061602 | 0.0029993 | -0.0049754 | -0.0045095 | -0.06192 | 0.0025335 | 0.064704 | 0.049618 | -0.014311 | 0.025485 | -0.0017347 | -0.13275 | 60.1456 | -61.3037 | 60.4019 | -61.0291 | -61.496 | -61.4365 | -0.004578 | 60.1227 | -61.3358 | 60.4111 | -61.203 | -61.3266 | -61.2579 | -0.009155 | -0.1236 | 0.13275 | 0.2655 | -0.14191 | -0.20142 | -0.13275 | -0.19226 | -0.041198 | -0.14648 | 0.14191 | 0.091553 | 0.036621 | -0.032043 | 0.077819 | 0.009155 | 0.27466 | 121.7056 | 0.13275 | 121.7468 | 121.4493 | 121.4584 | 121.4401 | 121.4172 | -121.5729 | -121.6049 | 121.6965 | 121.7056 | 61.1618 | 61.29
1060.2344 | 121.8338 | -61.2534 | 60.4294 | -0.051651 | 0.0058896 | 0.06561 | 0.059253 | -0.0012731 | -0.009675 | -0.0013051 | -0.028351 | 0.0036017 | 0.065345 | 0.053464 | -0.013242 | 0.02634 | -0.0021619 | -0.032043 | 60.2921 | -61.2625 | 60.3836 | -61.0657 | -61.4777 | -61.4456 | 0.022888 | 60.2966 | -61.2625 | 60.347 | -61.2259 | -61.3312 | -61.2991 | -0.009155 | -0.13733 | -0.045776 | 0.18768 | -0.19226 | -0.2243 | -0.18311 | -0.21515 | -0.009155 | -0.13275 | -0.082397 | 0.027466 | -0.045776 | -0.07782 | -0.036621 | -0.068665 | 0.19684 | 121.6461 | 0.036621 | 121.6095 | 121.5546 | 121.5591 | 121.5454 | 121.55 | -121.6919 | -121.6919 | 121.637 | 121.6003 | 61.2213 | 61.2762
1061.9844 | 121.8384 | -61.3083 | 60.347 | -0.10506 | 0.0063168 | 0.066037 | 0.064593 | -0.0019141 | -0.0088206 | -0.0025869 | -0.083283 | 0.0050971 | 0.067695 | 0.056027 | -0.013883 | 0.026126 | -0.0028027 | -0.2243 | 60.2051 | -61.3541 | 60.2737 | -61.1984 | -61.6333 | -61.5875 | -0.17395 | 60.1776 | -61.3724 | 60.2783 | -61.3495 | -61.4548 | -61.3724 | -0.045776 | -0.14191 | -0.073242 | 0.10986 | -0.27923 | -0.32501 | -0.23346 | -0.27924 | -0.064086 | -0.16937 | -0.068665 | -0.041198 | -0.064086 | -0.14648 | 0 | -0.082398 | 0.15564 | 121.6278 | 0.022888 | 121.6507 | 121.5591 | 121.55 | 121.5134 | 121.4859 | -121.701 | -121.7194 | 121.582 | 121.5866 | 61.084 | 61.1343
1063.7344 | 121.9757 | -61.1755 | 60.3882 | -0.11269 | 0.0041806 | 0.06326 | 0.058612 | -0.0029821 | -0.0092478 | -0.0034415 | 0.023529 | 0.0033881 | 0.0662 | 0.044919 | -0.014524 | 0.023776 | -0.0032299 | 0.032043 | 60.2097 | -61.2442 | 60.5484 | -60.878 | -61.3083 | -61.2946 | 0.19684 | 60.2417 | -61.2213 | 60.498 | -61.0657 | -61.1893 | -61.1664 | -0.068665 | -0.17853 | 0.16022 | 0.29755 | -0.11902 | -0.13275 | -0.050354 | -0.064087 | -0.045776 | -0.14649 | 0.10986 | 0.10986 | 0.009155 | -0.013733 | 0.054931 | 0.032043 | 0.36621 | 121.7926 | 0.15564 | 121.7194 | 121.4539 | 121.463 | 121.3852 | 121.4172 | -121.6324 | -121.6095 | 121.7239 | 121.6736 | 61.2076 | 61.3724
1065.4219 | 121.8933 | -61.2396 | 60.3882 | -0.051651 | 0.0065304 | 0.064969 | 0.063739 | -0.0061865 | -0.0073252 | -0.0040823 | -0.074127 | 0.0061651 | 0.065132 | 0.051114 | -0.015806 | 0.028903 | -0.0057935 | -0.041199 | 60.2875 | -61.2717 | 60.3928 | -61.0748 | -61.4914 | -61.4548 | 0.004578 | 60.2234 | -61.2991 | 60.3699 | -61.2305 | -61.3586 | -61.2946 | -0.032043 | -0.10071 | 0.004577 | 0.16479 | -0.21515 | -0.25177 | -0.18311 | -0.21973 | -0.059509 | -0.1648 | -0.018311 | 0.009155 | -0.054932 | -0.11902 | 0.004577 | -0.05951 | 0.19684 | 121.6644 | 0.068664 | 121.669 | 121.5591 | 121.5225 | 121.5271 | 121.463 | -121.6599 | -121.6873 | 121.6324 | 121.6095 | 61.1984 | 61.2442
1067.1719 | 121.9757 | -61.1938 | 60.3928 | -0.13557 | 0.0046078 | 0.065183 | 0.060534 | 0.0015039 | -0.007966 | -0.0032277 | 0.029632 | 0.0014655 | 0.0662 | 0.045987 | -0.012815 | 0.026126 | -0.0023755 | -0.054932 | 60.2188 | -61.2671 | 60.4385 | -61.0062 | -61.4182 | -61.377 | 0.091553 | 60.2234 | -61.2488 | 60.4614 | -61.1023 | -61.2122 | -61.1801 | -0.073242 | -0.17395 | 0.045777 | 0.18768 | -0.1831 | -0.2243 | -0.10986 | -0.15106 | -0.054931 | -0.16937 | 0.068665 | 0.091553 | 0.013733 | -0.01831 | 0.068664 | 0.036621 | 0.26093 | 121.7056 | 0.14648 | 121.7102 | 121.4859 | 121.4722 | 121.4127 | 121.4172 | -121.6599 | -121.6415 | 121.6324 | 121.6553 | 61.1389 | 61.2854
1068.8594 | 121.843 | -61.2167 | 60.434 | -0.097427 | 0.0050352 | 0.064328 | 0.05968 | -0.0036231 | -0.011384 | -0.00087794 | -0.034454 | 0.0057379 | 0.064704 | 0.049832 | -0.013456 | 0.02634 | -0.0045117 | 0.022888 | 60.2692 | -61.2259 | 60.4294 | -61.0245 | -61.4502 | -61.3998 | 0.073242 | 60.2692 | -61.2534 | 60.3653 | -61.2167 | -61.3266 | -61.29 | -0.009155 | -0.16479 | -0.004578 | 0.19226 | -0.18311 | -0.23346 | -0.17395 | -0.2243 | -0.036621 | -0.16479 | -0.068665 | 0 | -0.073242 | -0.10986 | -0.036621 | -0.073242 | 0.20142 | 121.6553 | 0.036621 | 121.6187 | 121.4951 | 121.5225 | 121.4859 | 121.4859 | -121.6599 | -121.6873 | 121.6461 | 121.582 | 61.2396 | 61.29
1070.6094 | 121.9299 | -61.2579 | 60.3058 | -0.1432 | 0.0061032 | 0.06561 | 0.060748 | -0.0025549 | -0.0077524 | -0.0021597 | -0.016144 | 0.0038153 | 0.06385 | 0.050473 | -0.013242 | 0.024631 | -0.0045117 | -0.12817 | 60.1501 | -61.2762 | 60.4294 | -61.0107 | -61.4822 | -61.4227 | 0.032043 | 60.1456 | -61.2854 | 60.4019 | -61.2076 | -61.3312 | -61.2396 | -0.01831 | -0.15564 | 0.1236 | 0.24719 | -0.16479 | -0.2243 | -0.14648 | -0.20599 | -0.027465 | -0.16022 | 0.096131 | 0.050354 | 0.018311 | -0.073242 | 0.045776 | -0.045777 | 0.2655 | 121.7056 | 0.077819 | 121.6873 | 121.4264 | 121.431 | 121.4081 | 121.4035 | -121.582 | -121.5912 | 121.6873 | 121.6599 | 61.1298 | 61.29
1072.3594 | 121.9803 | -61.1755 | 60.4248 | -0.074539 | 0.0037534 | 0.064756 | 0.060748 | -0.0031957 | -0.012452 | -0.0042959 | 0.026581 | 0.0038153 | 0.065772 | 0.055813 | -0.014951 | 0.02634 | -0.0085705 | 0.064087 | 60.26 | -61.2259 | 60.5255 | -60.9009 | -61.3266 | -61.3037 | 0.21973 | 60.2646 | -61.2396 | 60.4935 | -61.0611 | -61.1847 | -61.1572 | -0.050354 | -0.16479 | 0.10071 | 0.27466 | -0.12817 | -0.15106 | -0.07782 | -0.10071 | -0.064087 | -0.16022 | 0.068664 | 0.11444 | 0.01831 | -0.009155 | 0.082397 | 0.054932 | 0.32501 | 121.7514 | 0.17853 | 121.7331 | 121.4859 | 121.5042 | 121.4355 | 121.4401 | -121.6507 | -121.6644 | 121.701 | 121.669 | 61.2396 | 61.3953
1074.0469 | 121.9345 | -61.1618 | 60.4294 | -0.097427 | 0.0058896 | 0.065396 | 0.060962 | -0.0017005 | -0.0092478 | -0.00087794 | -0.034454 | 0.0021063 | 0.065986 | 0.052823 | -0.014738 | 0.025912 | -0.0045117 | 0.059509 | 60.2234 | -61.2167 | 60.5026 | -60.9375 | -61.3724 | -61.3312 | 0.17395 | 60.26 | -61.235 | 60.466 | -61.1114 | -61.1984 | -61.1938 | -0.054932 | -0.20599 | 0.073243 | 0.2243 | -0.16937 | -0.21057 | -0.11444 | -0.15564 | -0.073242 | -0.16937 | 0.036621 | 0.050354 | -0.032044 | -0.036621 | 0.041198 | 0.036621 | 0.27924 | 121.7194 | 0.1236 | 121.701 | 121.4401 | 121.4951 | 121.3852 | 121.4218 | -121.6461 | -121.6644 | 121.6644 | 121.6278 | 61.2213 | 61.3358
1075.8125 | 121.9299 | -61.2625 | 60.3104 | -0.15083 | 0.0054624 | 0.067319 | 0.062457 | -0.0021277 | -0.0077524 | -0.0021597 | -0.098541 | 0.0057379 | 0.0662 | 0.051541 | -0.014097 | 0.02634 | -0.0040845 | -0.2243 | 60.1913 | -61.3495 | 60.3378 | -61.1252 | -61.5646 | -61.5097 | -0.091553 | 60.1593 | -61.3541 | 60.3561 | -61.2534 | -61.3495 | -61.2625 | -0.086975 | -0.11902 | 0.027466 | 0.13733 | -0.24719 | -0.30212 | -0.16022 | -0.21515 | -0.091553 | -0.15106 | 0.045776 | 0.009155 | 0 | -0.086975 | 0.091553 | 0.004578 | 0.2243 | 121.6873 | 0.10071 | 121.7102 | 121.5408 | 121.5134 | 121.4539 | 121.4218 | -121.6599 | -121.6644 | 121.6003 | 121.6187 | 61.0382 | 61.171
1077.5469 | 121.962 | -61.2671 | 60.2921 | -0.082169 | 0.0063168 | 0.064542 | 0.060748 | -0.00063233 | -0.010316 | -0.0049367 | -0.055817 | 0.0023199 | 0.068122 | 0.049405 | -0.014097 | 0.025912 | -0.0040845 | -0.16022 | 60.1639 | -61.3129 | 60.3836 | -61.0519 | -61.4868 | -61.441 | -0.013733 | 60.1547 | -61.3312 | 60.3973 | -61.2167 | -61.3449 | -61.2534 | -0.045776 | -0.12817 | 0.091553 | 0.21515 | -0.17395 | -0.21973 | -0.12817 | -0.17395 | -0.064087 | -0.13733 | 0.10529 | 0.050354 | 0.013733 | -0.07782 | 0.07782 | -0.013733 | 0.26093 | 121.6965 | 0.11444 | 121.7285 | 121.4767 | 121.4859 | 121.431 | 121.4218 | -121.6049 | -121.6232 | 121.6507 | 121.6644 | 61.1069 | 61.2534
1079.2969 | 121.8567 | -61.322 | 60.3424 | -0.16609 | 0.0052488 | 0.067533 | 0.063311 | -0.0055457 | -0.010316 | -0.0021597 | -0.14127 | 0.0053107 | 0.067054 | 0.052823 | -0.013242 | 0.027621 | -0.0036573 | -0.21515 | 60.1822 | -61.3541 | 60.2875 | -61.1984 | -61.6333 | -61.5921 | -0.16022 | 60.1547 | -61.377 | 60.2829 | -61.3449 | -61.4594 | -61.3724 | -0.032044 | -0.16022 | -0.054931 | 0.1236 | -0.27008 | -0.31128 | -0.23804 | -0.27924 | -0.054932 | -0.18768 | -0.059509 | -0.022889 | -0.050354 | -0.13733 | 0.004578 | -0.082398 | 0.15564 | 121.6415 | 0.032043 | 121.6599 | 121.5363 | 121.5317 | 121.5042 | 121.4767 | -121.6965 | -121.7194 | 121.6095 | 121.6049 | 61.1069 | 61.1618
1080.9844 | 121.8842 | -61.2717 | 60.3516 | -0.12032 | 0.0065304 | 0.065396 | 0.062671 | 0.0012903 | -0.011598 | -0.0019461 | -0.11075 | 0.0040289 | 0.064491 | 0.052609 | -0.013456 | 0.026981 | -0.0032299 | -0.07782 | 60.2417 | -61.3129 | 60.4065 | -61.0382 | -61.5051 | -61.4639 | 0.022888 | 60.2234 | -61.3037 | 60.3653 | -61.2305 | -61.3586 | -61.2991 | -0.041199 | -0.10986 | 0.054932 | 0.23346 | -0.19226 | -0.23346 | -0.15106 | -0.19226 | -0.032044 | -0.12817 | 0.013733 | 0.041198 | -0.027466 | -0.086976 | 0.004578 | -0.054932 | 0.27466 | 121.7194 | 0.073242 | 121.669 | 121.5546 | 121.5271 | 121.5134 | 121.4951 | -121.6644 | -121.6553 | 121.6782 | 121.637 | 61.1938 | 61.2946
1082.7344 | 121.9254 | -61.2625 | 60.3699 | -0.13557 | 0.0046078 | 0.066251 | 0.058825 | 0.00022207 | -0.0092478 | -0.0042959 | -0.0008851 | 0.0057379 | 0.065132 | 0.047482 | -0.013456 | 0.027621 | -0.0083569 | -0.11902 | 60.2097 | -61.2808 | 60.4065 | -61.0245 | -61.4639 | -61.409 | 0 | 60.2005 | -61.2854 | 60.4111 | -61.1938 | -61.2854 | -61.2534 | -0.018311 | -0.16022 | 0.036621 | 0.23804 | -0.14648 | -0.20142 | -0.12817 | -0.18311 | -0.022888 | -0.16937 | 0.041199 | 0.068664 | 0.009155 | -0.022888 | 0.032043 | 0 | 0.25635 | 121.6873 | 0.091552 | 121.6965 | 121.4905 | 121.4859 | 121.4722 | 121.463 | -121.6507 | -121.6553 | 121.669 | 121.6736 | 61.1435 | 61.2625
1084.4688 | 121.9894 | -61.171 | 60.3973 | -0.089798 | 0.0046078 | 0.062833 | 0.060107 | -0.00063233 | -0.0088206 | -0.0015189 | -0.0039367 | 0.0033881 | 0.064704 | 0.046628 | -0.014524 | 0.025272 | 0.00018809 | 0.041199 | 60.2417 | -61.2396 | 60.5255 | -60.8917 | -61.3495 | -61.3174 | 0.22888 | 60.2509 | -61.1893 | 60.4935 | -61.0611 | -61.1618 | -61.171 | -0.068665 | -0.15564 | 0.12817 | 0.27923 | -0.14648 | -0.17853 | -0.07782 | -0.10986 | -0.018311 | -0.14649 | 0.09613 | 0.10986 | 0 | 0.009155 | 0.018311 | 0.027466 | 0.3479 | 121.7651 | 0.12817 | 121.6827 | 121.4813 | 121.4401 | 121.4127 | 121.4218 | -121.637 | -121.5866 | 121.6965 | 121.6644 | 61.2122 | 61.3998
1086.2188 | 121.9666 | -61.2671 | 60.3012 | -0.12032 | 0.0082394 | 0.065824 | 0.061389 | 0.0021447 | -0.0073252 | -0.0030141 | -0.037506 | 0.0033881 | 0.064704 | 0.051114 | -0.014097 | 0.027835 | -0.0047253 | -0.14191 | 60.1273 | -61.3037 | 60.4248 | -61.0291 | -61.5005 | -61.441 | 0.004578 | 60.1318 | -61.322 | 60.4202 | -61.1938 | -61.3083 | -61.2442 | -0.036621 | -0.17395 | 0.1236 | 0.23804 | -0.17395 | -0.23346 | -0.13733 | -0.19684 | -0.054931 | -0.16937 | 0.11902 | 0.073242 | 0.022888 | -0.041199 | 0.077819 | 0.013732 | 0.27466 | 121.7285 | 0.12817 | 121.7422 | 121.431 | 121.4539 | 121.3943 | 121.3989 | -121.6049 | -121.6232 | 121.6919 | 121.6873 | 61.1252 | 61.2717
1087.9062 | 121.8292 | -61.322 | 60.347 | -0.11269 | 0.0069578 | 0.068173 | 0.063739 | -0.00084593 | -0.0073252 | -0.0034415 | -0.11685 | 0.0068059 | 0.067054 | 0.056241 | -0.014311 | 0.025699 | -0.0049389 | -0.17853 | 60.2234 | -61.3449 | 60.2966 | -61.1664 | -61.615 | -61.5601 | -0.15564 | 60.1639 | -61.3541 | 60.2966 | -61.3495 | -61.4914 | -61.3953 | -0.022889 | -0.1236 | -0.050354 | 0.15564 | -0.23804 | -0.29297 | -0.21515 | -0.27008 | -0.032044 | -0.18311 | -0.050354 | -0.027466 | -0.073243 | -0.16937 | -0.041199 | -0.13733 | 0.17853 | 121.6415 | 0.004578 | 121.6507 | 121.5683 | 121.5179 | 121.5454 | 121.4859 | -121.6919 | -121.701 | 121.6187 | 121.6187 | 61.1435 | 61.1664
1089.6562 | 121.9666 | -61.29 | 60.3058 | -0.13557 | 0.0052488 | 0.065824 | 0.063952 | -0.0036231 | -0.0083932 | -0.0015189 | -0.040558 | 0.0061651 | 0.068977 | 0.056241 | -0.01367 | 0.028049 | -0.0030163 | -0.17395 | 60.1593 | -61.3037 | 60.3973 | -61.0291 | -61.4914 | -61.4365 | -0.018311 | 60.1593 | -61.3266 | 60.3973 | -61.1984 | -61.3266 | -61.2534 | -0.013733 | -0.14648 | 0.091553 | 0.26093 | -0.14648 | -0.20142 | -0.13275 | -0.18768 | -0.036621 | -0.14648 | 0.091553 | 0.091553 | 0.036621 | -0.036621 | 0.073242 | 0 | 0.27466 | 121.7011 | 0.12817 | 121.7239 | 121.463 | 121.4859 | 121.4493 | 121.4493 | -121.6095 | -121.6324 | 121.6873 | 121.6873 | 61.116 | 61.2717
1091.4219 | 121.8704 | -61.2991 | 60.3424 | -0.18135 | 0.0075986 | 0.066464 | 0.062457 | -0.00084593 | -0.0088206 | -0.0023733 | -0.077179 | 0.0057379 | 0.064918 | 0.051755 | -0.01367 | 0.028476 | -0.0034435 | -0.21973 | 60.2142 | -61.3495 | 60.3058 | -61.1618 | -61.6013 | -61.5601 | -0.15106 | 60.173 | -61.3495 | 60.3012 | -61.3174 | -61.441 | -61.3815 | -0.050354 | -0.12817 | -0.036621 | 0.13733 | -0.26093 | -0.30212 | -0.21057 | -0.25177 | -0.050354 | -0.16937 | -0.041199 | -0.018311 | -0.082398 | -0.14191 | -0.032044 | -0.091553 | 0.18768 | 121.6553 | 0.032043 | 121.6507 | 121.5637 | 121.5225 | 121.5134 | 121.4722 | -121.6919 | -121.6919 | 121.6049 | 121.6003 | 61.0794 | 61.1481
1093.1875 | 121.8567 | -61.3129 | 60.3378 | -0.10506 | 0.0082394 | 0.065396 | 0.061816 | 0.0019311 | -0.0083932 | -0.0053641 | -0.1199 | 0.0053107 | 0.066841 | 0.055173 | -0.013242 | 0.027408 | -0.00088011 | -0.10529 | 60.2188 | -61.2854 | 60.3973 | -61.0657 | -61.5143 | -61.4822 | -0.022888 | 60.2142 | -61.3495 | 60.3378 | -61.2762 | -61.4044 | -61.3403 | 0.027466 | -0.11902 | 0.059509 | 0.24719 | -0.16937 | -0.20142 | -0.19684 | -0.22888 | -0.036621 | -0.1236 | 0 | 0.036621 | -0.027466 | -0.091553 | 0.009155 | -0.054932 | 0.21973 | 121.6827 | 0.073242 | 121.6873 | 121.5042 | 121.5637 | 121.5317 | 121.5271 | -121.6232 | -121.6873 | 121.7102 | 121.6507 | 61.2076 | 61.29
1094.875 | 121.9666 | -61.1801 | 60.4202 | -0.12794 | 0.0054624 | 0.064969 | 0.060962 | -0.0014867 | -0.012239 | -0.0030141 | 0.020477 | 0.0042425 | 0.068763 | 0.048337 | -0.012174 | 0.025912 | -0.00088011 | -0.054932 | 60.2371 | -61.2946 | 60.4477 | -60.9924 | -61.3998 | -61.3632 | 0.10986 | 60.2188 | -61.2579 | 60.466 | -61.1023 | -61.1984 | -61.1801 | -0.11444 | -0.1831 | 0.027466 | 0.18768 | -0.1831 | -0.21973 | -0.068664 | -0.10529 | -0.07782 | -0.20142 | 0.045776 | 0.07782 | 0 | -0.01831 | 0.07782 | 0.05951 | 0.30212 | 121.7422 | 0.15564 | 121.7239 | 121.5317 | 121.4767 | 121.4172 | 121.3989 | -121.7148 | -121.6782 | 121.6278 | 121.6461 | 61.1252 | 61.29
1096.625 | 121.9345 | -61.235 | 60.379 | -0.05928 | 0.0050352 | 0.066037 | 0.060534 | 0.0012903 | -0.0088206 | -0.00066434 | 0.0021667 | 0.0016791 | 0.066841 | 0.048123 | -0.015592 | 0.028903 | -0.0066479 | -0.086975 | 60.2142 | -61.2717 | 60.4385 | -61.0199 | -61.4639 | -61.3998 | 0.041199 | 60.2142 | -61.2762 | 60.3973 | -61.1847 | -61.29 | -61.2305 | -0.036621 | -0.16479 | 0.05951 | 0.21515 | -0.1648 | -0.22888 | -0.12817 | -0.19226 | -0.041199 | -0.16479 | 0.018311 | 0.050354 | 0.004577 | -0.054932 | 0.045776 | -0.013733 | 0.25177 | 121.7102 | 0.091553 | 121.6736 | 121.4859 | 121.4905 | 121.4493 | 121.4493 | -121.6507 | -121.6553 | 121.6736 | 121.6324 | 61.1481 | 61.2762
1098.3281 | 121.907 | -61.2213 | 60.3836 | -0.15846 | 0.0067442 | 0.064328 | 0.061602 | -0.0036231 | -0.009675 | -0.0023733 | -0.034454 | 0.0040289 | 0.0662 | 0.049405 | -0.014524 | 0.024204 | -0.0034435 | -0.10529 | 60.2005 | -61.2717 | 60.4294 | -61.0428 | -61.4548 | -61.409 | 0.013733 | 60.2234 | -61.2534 | 60.4065 | -61.1893 | -61.2991 | -61.2396 | -0.050354 | -0.18311 | 0.045776 | 0.17853 | -0.18768 | -0.23346 | -0.13733 | -0.18311 | -0.032044 | -0.16022 | 0.022888 | 0.032043 | -0.018311 | -0.07782 | 0.013733 | -0.045776 | 0.22888 | 121.701 | 0.064087 | 121.6599 | 121.4722 | 121.4767 | 121.4218 | 121.4447 | -121.6553 | -121.637 | 121.6507 | 121.6278 | 61.116 | 61.235
1100.0781 | 121.8567 | -61.322 | 60.3241 | -0.097427 | 0.007385 | 0.064969 | 0.062671 | 0.0032129 | -0.0066844 | -0.0049367 | -0.11075 | 0.0055243 | 0.067268 | 0.0509 | -0.014311 | 0.026981 | -0.0062207 | -0.21515 | 60.1868 | -61.3724 | 60.2875 | -61.203 | -61.6333 | -61.5646 | -0.16479 | 60.1959 | -61.3907 | 60.3012 | -61.3403 | -61.4594 | -61.3632 | -0.050354 | -0.13733 | -0.036621 | 0.11902 | -0.24262 | -0.31128 | -0.19226 | -0.26093 | -0.068665 | -0.12817 | -0.022889 | -0.018311 | -0.041199 | -0.13733 | 0.027466 | -0.068665 | 0.16937 | 121.6599 | 0.050354 | 121.6919 | 121.5591 | 121.5866 | 121.5088 | 121.5179 | -121.6965 | -121.7148 | 121.6095 | 121.6232 | 61.1069 | 61.1572
1101.8281 | 121.9391 | -61.2167 | 60.379 | -0.16609 | 0.0026852 | 0.064756 | 0.05968 | -0.0042639 | -0.010102 | -0.0021597 | -0.013092 | 0.0029607 | 0.065986 | 0.049191 | -0.012388 | 0.027408 | -0.0030163 | -0.073242 | 60.228 | -61.2808 | 60.4202 | -61.0336 | -61.4548 | -61.4044 | 0.018311 | 60.2097 | -61.2625 | 60.4111 | -61.171 | -61.2671 | -61.2305 | -0.064087 | -0.15106 | 0.041199 | 0.18311 | -0.18768 | -0.23804 | -0.1236 | -0.17395 | -0.045776 | -0.16937 | 0.032044 | 0.045777 | -0.013733 | -0.050354 | 0.032043 | -0.004578 | 0.24719 | 121.701 | 0.091553 | 121.6736 | 121.5088 | 121.4722 | 121.4447 | 121.4264 | -121.6599 | -121.6415 | 121.637 | 121.6278 | 61.1435 | 61.235
1103.5781 | 121.9711 | -61.2946 | 60.2829 | -0.17372 | 0.008453 | 0.066892 | 0.063525 | 0.0023585 | -0.0073252 | 0.00083106 | -0.077179 | 0.0038153 | 0.065132 | 0.0462 | -0.014951 | 0.026126 | -0.0042981 | -0.13733 | 60.1547 | -61.2946 | 60.4294 | -61.0245 | -61.496 | -61.4319 | -0.004578 | 60.141 | -61.3312 | 60.4156 | -61.1847 | -61.3174 | -61.2305 | 0 | -0.12817 | 0.14648 | 0.27008 | -0.13733 | -0.20142 | -0.13733 | -0.20142 | -0.036621 | -0.14191 | 0.13275 | 0.10986 | 0.064087 | -0.022888 | 0.10071 | 0.013733 | 0.27008 | 121.7239 | 0.14648 | 121.7468 | 121.4493 | 121.4722 | 121.4493 | 121.4355 | -121.5775 | -121.6141 | 121.7239 | 121.7102 | 61.1572 | 61.29
1105.3281 | 121.962 | -61.203 | 60.4065 | -0.06691 | 0.003967 | 0.063687 | 0.060748 | -0.0017005 | -0.010743 | -0.0038687 | 0.0021667 | 0.0027471 | 0.064277 | 0.046414 | -0.01367 | 0.025485 | -0.0034435 | 0.059509 | 60.2417 | -61.235 | 60.5576 | -60.8963 | -61.3266 | -61.3037 | 0.21973 | 60.26 | -61.2305 | 60.498 | -61.0794 | -61.1847 | -61.1664 | -0.032043 | -0.1648 | 0.15106 | 0.3067 | -0.10071 | -0.1236 | -0.068665 | -0.091553 | -0.027466 | -0.14648 | 0.091553 | 0.1236 | 0.036621 | 0.018311 | 0.064087 | 0.045777 | 0.33874 | 121.7926 | 0.15106 | 121.7285 | 121.4767 | 121.4905 | 121.4447 | 121.463 | -121.6415 | -121.637 | 121.7606 | 121.7011 | 61.2625 | 61.4227
1107.0156 | 121.9437 | -61.2305 | 60.3516 | -0.12032 | 0.0054624 | 0.063901 | 0.059893 | -0.0034095 | -0.01117 | -0.0049367 | -0.013092 | 0.0038153 | 0.067909 | 0.055386 | -0.01367 | 0.025272 | -0.0057935 | -0.082397 | 60.2188 | -61.2579 | 60.4202 | -61.0199 | -61.4548 | -61.3907 | 0.036621 | 60.2417 | -61.2671 | 60.4019 | -61.1893 | -61.2762 | -61.235 | -0.027466 | -0.13275 | 0.068665 | 0.21057 | -0.16022 | -0.2243 | -0.13275 | -0.19684 | -0.036621 | -0.10986 | 0.050355 | 0.041199 | -0.004577 | -0.045776 | 0.032044 | -0.009155 | 0.23804 | 121.6782 | 0.07782 | 121.669 | 121.4767 | 121.5088 | 121.4493 | 121.4722 | -121.6095 | -121.6187 | 121.6507 | 121.6324 | 61.1481 | 61.2671
1108.7656 | 122.0032 | -61.1664 | 60.4065 | -0.097427 | 0.0063168 | 0.065396 | 0.060748 | -0.00084593 | -0.012239 | -0.0064321 | -0.028351 | 0.0042425 | 0.065772 | 0.05325 | -0.015165 | 0.025699 | -0.0023755 | 0.041199 | 60.2417 | -61.2259 | 60.5392 | -60.91 | -61.3358 | -61.3129 | 0.20142 | 60.2188 | -61.2122 | 60.5255 | -61.0519 | -61.1572 | -61.1481 | -0.059509 | -0.1648 | 0.13275 | 0.25635 | -0.14648 | -0.16937 | -0.086975 | -0.10986 | -0.045776 | -0.18768 | 0.11902 | 0.11444 | 0.018311 | 0.009155 | 0.064087 | 0.054931 | 0.31586 | 121.7651 | 0.16022 | 121.7377 | 121.4676 | 121.431 | 121.4081 | 121.3852 | -121.6324 | -121.6187 | 121.7056 | 121.6919 | 61.2076 | 61.3678
1110.5 | 121.9437 | -61.1847 | 60.4019 | -0.11269 | 0.0052488 | 0.064115 | 0.061389 | -0.0074683 | -0.009675 | -0.0028005 | -0.034454 | 0.0046697 | 0.064491 | 0.054959 | -0.013456 | 0.026126 | -0.0072889 | 0.059509 | 60.2325 | -61.2122 | 60.5392 | -60.9146 | -61.3632 | -61.3174 | 0.18768 | 60.2463 | -61.2259 | 60.4752 | -61.0977 | -61.1984 | -61.1893 | -0.027466 | -0.16937 | 0.13733 | 0.27008 | -0.13275 | -0.17853 | -0.10529 | -0.15106 | -0.041199 | -0.15564 | 0.073242 | 0.086975 | -0.004578 | -0.013733 | 0.036621 | 0.027466 | 0.29755 | 121.7514 | 0.12817 | 121.701 | 121.4447 | 121.4722 | 121.4172 | 121.431 | -121.6141 | -121.6278 | 121.7239 | 121.6599 | 61.2442 | 61.3724
1112.1875 | 121.9574 | -61.2762 | 60.2875 | -0.097427 | 0.0075986 | 0.065396 | 0.060962 | -0.0010595 | -0.0098886 | -0.0038687 | -0.080231 | 0.0023199 | 0.0615 | 0.058377 | -0.014524 | 0.026553 | -0.0034435 | -0.13275 | 60.141 | -61.3083 | 60.4202 | -61.0291 | -61.5005 | -61.4365 | -0.027466 | 60.173 | -61.322 | 60.4065 | -61.1984 | -61.3266 | -61.2442 | -0.032044 | -0.14648 | 0.13275 | 0.24719 | -0.16022 | -0.2243 | -0.12817 | -0.19226 | -0.045776 | -0.11444 | 0.11902 | 0.07782 | 0.032043 | -0.050354 | 0.077819 | -0.004578 | 0.27924 | 121.7285 | 0.1236 | 121.7285 | 121.4493 | 121.4951 | 121.4172 | 121.4493 | -121.5958 | -121.6095 | 121.6965 | 121.6827 | 61.1435 | 61.2488
1113.9531 | 121.8979 | -61.2717 | 60.3378 | -0.074539 | 0.0061032 | 0.064756 | 0.063098 | -0.0012731 | -0.010102 | -0.0032277 | -0.13516 | 0.0040289 | 0.064704 | 0.051755 | -0.016447 | 0.027408 | -0.0051525 | -0.073242 | 60.2142 | -61.2991 | 60.4019 | -61.0657 | -61.5005 | -61.4639 | 0.022888 | 60.2188 | -61.3174 | 60.3836 | -61.2396 | -61.3724 | -61.3083 | -0.027466 | -0.1236 | 0.064087 | 0.20599 | -0.19226 | -0.22888 | -0.1648 | -0.20142 | -0.045777 | -0.11902 | 0.045776 | 0.032043 | -0.036622 | -0.10071 | 0.009155 | -0.054931 | 0.23346 | 121.701 | 0.07782 | 121.7011 | 121.5134 | 121.5363 | 121.4859 | 121.4905 | -121.637 | -121.6553 | 121.6736 | 121.6553 | 61.1984 | 61.2946
1115.7031 | 121.8384 | -61.3403 | 60.3333 | -0.1432 | 0.0067442 | 0.066678 | 0.065661 | -0.0023413 | -0.0083932 | 0.00061746 | -0.1138 | 0.0070197 | 0.064918 | 0.054104 | -0.012388 | 0.028262 | -0.0057935 | -0.2243 | 60.2097 | -61.3632 | 60.2783 | -61.1847 | -61.6425 | -61.5692 | -0.16479 | 60.1547 | -61.3541 | 60.2966 | -61.322 | -61.4594 | -61.3678 | -0.022888 | -0.1236 | -0.054932 | 0.15564 | -0.22888 | -0.30212 | -0.20599 | -0.27924 | -0.013733 | -0.17853 | -0.036621 | 0.018311 | -0.027466 | -0.11902 | -0.013733 | -0.10529 | 0.17853 | 121.6415 | 0.032044 | 121.6507 | 121.5729 | 121.5088 | 121.55 | 121.4951 | -121.6965 | -121.6873 | 121.6187 | 121.637 | 61.116 | 61.1755
1117.3906 | 121.9528 | -61.1938 | 60.3882 | -0.1432 | 0.0058896 | 0.06561 | 0.060534 | -0.0019141 | -0.0073252 | -0.0015189 | -0.0069885 | 0.0050971 | 0.065132 | 0.043637 | -0.013456 | 0.026981 | -0.0021619 | -0.064087 | 60.2371 | -61.2671 | 60.434 | -61.0107 | -61.4227 | -61.3724 | 0.091553 | 60.2325 | -61.2717 | 60.4752 | -61.1023 | -61.2167 | -61.1938 | -0.073242 | -0.15106 | 0.045776 | 0.18311 | -0.17853 | -0.22888 | -0.10528 | -0.15564 | -0.077819 | -0.15564 | 0.086975 | 0.091553 | 0 | -0.022888 | 0.077819 | 0.054931 | 0.25635 | 121.7011 | 0.16937 | 121.7468 | 121.5042 | 121.5042 | 121.431 | 121.4264 | -121.6553 | -121.6599 | 121.6278 | 121.669 | 61.1298 | 61.2854
1119.1719 | 121.8613 | -61.3129 | 60.3241 | -0.074539 | 0.0080258 | 0.064969 | 0.064166 | -0.0014867 | -0.009675 | -0.0034415 | -0.11075 | 0.0046697 | 0.067054 | 0.066067 | -0.013242 | 0.026981 | -0.0047253 | -0.22888 | 60.2234 | -61.3724 | 60.3012 | -61.1526 | -61.5921 | -61.528 | -0.14648 | 60.2097 | -61.3403 | 60.3149 | -61.322 | -61.441 | -61.3678 | -0.059509 | -0.10071 | -0.022889 | 0.16022 | -0.21515 | -0.27924 | -0.15564 | -0.21973 | -0.027466 | -0.11444 | -0.009156 | -0.009155 | -0.054932 | -0.12817 | -0.027466 | -0.10071 | 0.21973 | 121.6736 | 0.018311 | 121.6553 | 121.5958 | 121.55 | 121.5363 | 121.5225 | -121.6965 | -121.6644 | 121.6141 | 121.6278 | 61.084 | 61.1664
1120.8594 | 121.843 | -61.3266 | 60.3378 | -0.16609 | 0.005676 | 0.068173 | 0.06438 | 0.0047083 | -0.0088206 | -0.0030141 | -0.09549 | 0.0057379 | 0.066841 | 0.054104 | -0.014738 | 0.025912 | -0.0064343 | -0.21057 | 60.1959 | -61.3632 | 60.2921 | -61.1893 | -61.6287 | -61.5784 | -0.16937 | 60.1913 | -61.3815 | 60.2829 | -61.3403 | -61.4685 | -61.3586 | -0.036621 | -0.14191 | -0.045777 | 0.13733 | -0.25177 | -0.30212 | -0.21515 | -0.2655 | -0.054932 | -0.14648 | -0.054932 | -0.013733 | -0.032044 | -0.14191 | 0.022888 | -0.086975 | 0.17395 | 121.6553 | 0.041199 | 121.6644 | 121.5591 | 121.5729 | 121.5225 | 121.5179 | -121.701 | -121.7194 | 121.6187 | 121.6095 | 61.116 | 61.1572
1122.5938 | 121.8338 | -61.3174 | 60.347 | -0.097427 | 0.0075986 | 0.066892 | 0.061389 | -0.0019141 | -0.010316 | -0.00066434 | -0.098541 | 0.0076605 | 0.068122 | 0.060727 | -0.012602 | 0.028262 | -0.0057935 | -0.13275 | 60.2142 | -61.3174 | 60.347 | -61.1023 | -61.5646 | -61.5326 | -0.086975 | 60.1959 | -61.3724 | 60.3012 | -61.3312 | -61.4594 | -61.3815 | 0 | -0.13275 | 0 | 0.21515 | -0.21515 | -0.24719 | -0.21515 | -0.24719 | -0.054931 | -0.15106 | -0.045777 | -0.013733 | -0.064087 | -0.14191 | -0.009156 | -0.086976 | 0.21515 | 121.6644 | 0.041198 | 121.6736 | 121.5317 | 121.5683 | 121.5317 | 121.5134 | -121.6644 | -121.7194 | 121.6644 | 121.6187 | 61.1847 | 61.2305
1124.3438 | 121.9208 | -61.1847 | 60.3973 | -0.11269 | 0.0037534 | 0.065183 | 0.058398 | -0.0064001 | -0.0081796 | -0.0045095 | 0.011322 | 0.0053107 | 0.066627 | 0.058377 | -0.014951 | 0.02634 | -0.0051525 | 0.045776 | 60.2554 | -61.2305 | 60.5026 | -60.9238 | -61.3449 | -61.3174 | 0.16479 | 60.2509 | -61.2442 | 60.4843 | -61.1023 | -61.2122 | -61.1801 | -0.045777 | -0.14191 | 0.10529 | 0.26093 | -0.13275 | -0.16022 | -0.086975 | -0.11444 | -0.05951 | -0.14649 | 0.086975 | 0.082397 | 0.004577 | -0.027466 | 0.064087 | 0.032044 | 0.3067 | 121.7331 | 0.14191 | 121.7285 | 121.4859 | 121.4951 | 121.4401 | 121.4355 | -121.6278 | -121.6415 | 121.6873 | 121.669 | 61.2305 | 61.3495
1126.0938 | 121.8613 | -61.3358 | 60.3012 | -0.12794 | 0.0075986 | 0.064756 | 0.061175 | 0.0019311 | -0.007966 | -0.0017325 | -0.086334 | 0.0040289 | 0.066627 | 0.057309 | -0.014738 | 0.026981 | -0.0042981 | -0.22888 | 60.2142 | -61.3403 | 60.3149 | -61.1481 | -61.6013 | -61.5509 | -0.12817 | 60.1776 | -61.3586 | 60.3333 | -61.3174 | -61.4502 | -61.3449 | -0.004578 | -0.086975 | 0.013733 | 0.18768 | -0.21515 | -0.2655 | -0.21057 | -0.26093 | -0.022889 | -0.1236 | 0.032044 | 0.01831 | -0.009156 | -0.11444 | 0.013733 | -0.091552 | 0.19226 | 121.6553 | 0.041199 | 121.6919 | 121.5546 | 121.5363 | 121.55 | 121.5134 | -121.6415 | -121.6599 | 121.6507 | 121.669 | 61.1069 | 61.2076
1127.7812 | 121.8475 | -61.2167 | 60.4294 | -0.097427 | 0.0058896 | 0.064756 | 0.060962 | -0.0049047 | -0.010316 | 0.0014719 | -0.040558 | 0.0040289 | 0.064277 | 0.050046 | -0.015165 | 0.024844 | -0.0040845 | 0.036621 | 60.2783 | -61.235 | 60.4019 | -61.0062 | -61.4365 | -61.409 | 0.082397 | 60.2554 | -61.2534 | 60.3653 | -61.203 | -61.3174 | -61.2946 | -0.01831 | -0.15106 | -0.027465 | 0.21057 | -0.19226 | -0.21973 | -0.17395 | -0.20142 | -0.036621 | -0.17395 | -0.064087 | 0.013733 | -0.07782 | -0.10071 | -0.041199 | -0.064087 | 0.22888 | 121.637 | 0.050354 | 121.6187 | 121.5134 | 121.5088 | 121.4951 | 121.4722 | -121.6644 | -121.6827 | 121.6187 | 121.582 | 61.2534 | 61.2991
1129.5469 | 121.8201 | -61.3449 | 60.3378 | -0.12032 | 0.0082394 | 0.06561 | 0.063739 | 0.00086307 | -0.0071116 | -0.0032277 | -0.11075 | 0.0074469 | 0.066841 | 0.0556 | -0.015165 | 0.028903 | -0.0068615 | -0.20142 | 60.2142 | -61.3358 | 60.3012 | -61.1847 | -61.615 | -61.5738 | -0.1831 | 60.1822 | -61.3586 | 60.2692 | -61.3449 | -61.4731 | -61.3861 | 0.009156 | -0.1236 | -0.036622 | 0.16022 | -0.22888 | -0.27008 | -0.23804 | -0.27924 | -0.013733 | -0.15564 | -0.068665 | 0 | -0.041198 | -0.12817 | -0.027465 | -0.11444 | 0.15106 | 121.637 | 0.013733 | 121.6278 | 121.55 | 121.5408 | 121.5591 | 121.5271 | -121.6736 | -121.6965 | 121.6461 | 121.6141 | 61.1435 | 61.1618
1131.2344 | 121.8658 | -61.2625 | 60.4248 | -0.051651 | 0.0058896 | 0.063901 | 0.063098 | -0.0070409 | -0.0098886 | -0.0030141 | -0.058869 | 0.0040289 | 0.070259 | 0.05325 | -0.013883 | 0.026126 | -0.0055799 | -0.032043 | 60.3058 | -61.2671 | 60.3928 | -61.0611 | -61.4777 | -61.4502 | 0.004578 | 60.2921 | -61.2808 | 60.3653 | -61.235 | -61.3541 | -61.2854 | -0.004578 | -0.11902 | -0.032044 | 0.20142 | -0.18768 | -0.21515 | -0.1831 | -0.21057 | -0.018311 | -0.13275 | -0.05951 | 0.027466 | -0.022888 | -0.091553 | -0.004577 | -0.073242 | 0.20599 | 121.6599 | 0.045777 | 121.6461 | 121.5729 | 121.5729 | 121.5683 | 121.5546 | -121.6919 | -121.7056 | 121.6553 | 121.6278 | 61.2305 | 61.2671
1133 | 121.8887 | -61.2579 | 60.3699 | -0.036392 | 0.008453 | 0.065183 | 0.061816 | 0.0032129 | -0.006898 | -0.0047231 | -0.080231 | 0.0040289 | 0.065772 | 0.052823 | -0.011961 | 0.028476 | -0.0034435 | -0.036621 | 60.2829 | -61.2854 | 60.3973 | -61.0657 | -61.496 | -61.4594 | 0.022888 | 60.2234 | -61.2991 | 60.3836 | -61.2213 | -61.3632 | -61.29 | -0.027465 | -0.086975 | 0.027466 | 0.19226 | -0.20142 | -0.23804 | -0.17395 | -0.21057 | -0.041198 | -0.14648 | 0.013733 | 0.036622 | -0.032043 | -0.10528 | 0.009155 | -0.064087 | 0.21973 | 121.6827 | 0.07782 | 121.6827 | 121.5683 | 121.5225 | 121.5408 | 121.4813 | -121.6553 | -121.669 | 121.6553 | 121.6415 | 61.2213 | 61.2808
1134.75 | 121.8842 | -61.2854 | 60.3607 | -0.10506 | 0.0061032 | 0.066892 | 0.063098 | 0.0017175 | -0.01053 | -2.3544e-05 | -0.092438 | 0.0048833 | 0.065559 | 0.052609 | -0.014524 | 0.027194 | -0.0036573 | -0.091553 | 60.2142 | -61.3083 | 60.3973 | -61.0611 | -61.5005 | -61.4731 | 0 | 60.2097 | -61.3266 | 60.3516 | -61.2488 | -61.3953 | -61.3358 | -0.022889 | -0.14648 | 0.036621 | 0.2243 | -0.18768 | -0.21515 | -0.16479 | -0.19226 | -0.041199 | -0.15106 | -0.009156 | 0.036621 | -0.050354 | -0.10986 | -0.009155 | -0.068665 | 0.24719 | 121.7056 | 0.07782 | 121.6782 | 121.5225 | 121.5363 | 121.4996 | 121.4951 | -121.669 | -121.6873 | 121.6827 | 121.637 | 61.1938 | 61.2854
1136.4531 | 121.8887 | -61.2762 | 60.4294 | -0.06691 | 0.0058896 | 0.065396 | 0.060534 | -0.00020513 | -0.009675 | -0.0028005 | -0.049713 | 0.0050971 | 0.066841 | 0.051968 | -0.012388 | 0.026767 | -0.0055799 | -0.041199 | 60.2966 | -61.2717 | 60.3836 | -61.084 | -61.4868 | -61.4502 | 0.004578 | 60.2737 | -61.2854 | 60.379 | -61.2213 | -61.3312 | -61.2808 | 0.004578 | -0.13275 | -0.045776 | 0.19226 | -0.17395 | -0.21057 | -0.17853 | -0.21515 | -0.009155 | -0.15564 | -0.050354 | 0.054932 | -0.004578 | -0.054932 | 0.004577 | -0.045777 | 0.18768 | 121.6553 | 0.064087 | 121.6644 | 121.5683 | 121.5591 | 121.5729 | 121.55 | -121.701 | -121.7148 | 121.6599 | 121.6553 | 61.235 | 61.2808
1138.2031 | 121.9299 | -61.2305 | 60.3241 | -0.15083 | 0.0065304 | 0.064328 | 0.060534 | 0.0021447 | -0.007966 | -0.0032277 | 0.0052185 | 0.0046697 | 0.061714 | 0.053677 | -0.013242 | 0.025699 | -0.0053661 | -0.14648 | 60.1685 | -61.3083 | 60.4294 | -60.9833 | -61.4548 | -61.3998 | 0.018311 | 60.1593 | -61.3083 | 60.4111 | -61.1984 | -61.2946 | -61.235 | -0.07782 | -0.15564 | 0.10528 | 0.24719 | -0.16937 | -0.2243 | -0.091552 | -0.14648 | -0.07782 | -0.1648 | 0.086975 | 0.032044 | -0.004577 | -0.064087 | 0.073243 | 0.013733 | 0.32501 | 121.7377 | 0.10986 | 121.7194 | 121.4767 | 121.4676 | 121.3989 | 121.3898 | -121.6324 | -121.6324 | 121.6599 | 121.6415 | 61.084 | 61.2488
1139.8906 | 121.9254 | -61.2122 | 60.3516 | -0.13557 | 0.005676 | 0.066251 | 0.061816 | -0.0057593 | -0.009675 | -0.0032277 | -0.019196 | 0.0010381 | 0.065132 | 0.04855 | -0.014524 | 0.026767 | -0.0051525 | -0.15106 | 60.2005 | -61.3037 | 60.4202 | -61.0153 | -61.4685 | -61.4136 | 0.009155 | 60.1868 | -61.2991 | 60.4065 | -61.1938 | -61.2808 | -61.2396 | -0.091553 | -0.15106 | 0.068665 | 0.19684 | -0.20142 | -0.25635 | -0.10986 | -0.16479 | -0.086975 | -0.16479 | 0.054932 | 0.01831 | -0.027466 | -0.068665 | 0.059509 | 0.01831 | 0.28839 | 121.7239 | 0.10528 | 121.7056 | 121.5042 | 121.4859 | 121.4127 | 121.3989 | -121.6553 | -121.6507 | 121.6324 | 121.6187 | 61.0611 | 61.2213
1141.6406 | 121.9711 | -61.2671 | 60.3012 | -0.18898 | 0.0069578 | 0.067533 | 0.062457 | -0.0038367 | -0.0064706 | -0.0017325 | -0.046661 | 0.0044561 | 0.065986 | 0.051541 | -0.013242 | 0.02634 | -0.0053661 | -0.14648 | 60.173 | -61.3083 | 60.4202 | -61.0382 | -61.4822 | -61.4227 | -0.009155 | 60.1273 | -61.3266 | 60.434 | -61.1893 | -61.3174 | -61.235 | -0.041199 | -0.12817 | 0.11902 | 0.22888 | -0.15564 | -0.21515 | -0.11444 | -0.17395 | -0.059509 | -0.17395 | 0.13275 | 0.07782 | 0.032044 | -0.050354 | 0.091553 | 0.009155 | 0.27008 | 121.7285 | 0.13733 | 121.7606 | 121.4813 | 121.4539 | 121.4401 | 121.3943 | -121.6095 | -121.6278 | 121.6873 | 121.7011 | 61.1206 | 61.2579
1143.3906 | 121.9711 | -61.2534 | 60.2829 | -0.19661 | 0.0078122 | 0.068814 | 0.063098 | 0.0040675 | -0.0073252 | -0.0025869 | -0.046661 | 0.0027471 | 0.065132 | 0.061154 | -0.015806 | 0.027194 | -0.0038709 | -0.17853 | 60.173 | -61.3037 | 60.4202 | -61.0428 | -61.4822 | -61.4273 | -0.004578 | 60.1181 | -61.322 | 60.4202 | -61.2076 | -61.3174 | -61.2488 | -0.050354 | -0.10986 | 0.13733 | 0.21057 | -0.17395 | -0.22888 | -0.1236 | -0.17853 | -0.068664 | -0.1648 | 0.13733 | 0.045776 | 0.004578 | -0.064087 | 0.073242 | 0.004577 | 0.26093 | 121.7239 | 0.11444 | 121.7422 | 121.4767 | 121.4401 | 121.4264 | 121.3715 | -121.5866 | -121.6049 | 121.6736 | 121.6736 | 61.0748 | 61.2488
1145.1562 | 121.8933 | -61.3037 | 60.3745 | -0.074539 | 0.0063168 | 0.066678 | 0.063525 | -0.0049047 | -0.0094614 | -0.0042959 | -0.086334 | 0.0042425 | 0.066627 | 0.058804 | -0.012815 | 0.026981 | -0.0032299 | -0.082397 | 60.2463 | -61.2854 | 60.4111 | -61.0657 | -61.5097 | -61.4594 | 0.032043 | 60.2142 | -61.3037 | 60.3882 | -61.2305 | -61.3678 | -61.2854 | 0.018311 | -0.12817 | 0.036621 | 0.23804 | -0.15564 | -0.20599 | -0.17395 | -0.2243 | 0 | -0.16022 | 0.013733 | 0.073242 | 0.018311 | -0.064087 | 0.018311 | -0.064087 | 0.21973 | 121.6965 | 0.073242 | 121.6919 | 121.5317 | 121.5179 | 121.55 | 121.5179 | -121.6599 | -121.6782 | 121.7148 | 121.6919 | 61.2213 | 61.3358
1146.8438 | 121.8704 | -61.2076 | 60.4385 | -0.082169 | 0.005676 | 0.064542 | 0.060107 | 0.0029993 | -0.01117 | -0.0053641 | -0.013092 | 0.0048833 | 0.065345 | 0.0509 | -0.012174 | 0.027408 | -0.0013073 | 0.036621 | 60.2509 | -61.2488 | 60.4843 | -60.965 | -61.3953 | -61.3632 | 0.11444 | 60.2737 | -61.235 | 60.379 | -61.171 | -61.2854 | -61.2625 | -0.041198 | -0.18768 | 0.045776 | 0.24262 | -0.15564 | -0.18768 | -0.11444 | -0.14648 | -0.027465 | -0.16479 | -0.05951 | 0.036622 | -0.054931 | -0.077819 | -0.027466 | -0.050354 | 0.28381 | 121.7331 | 0.064087 | 121.6141 | 121.4996 | 121.5088 | 121.4584 | 121.4813 | -121.6873 | -121.6736 | 121.6919 | 121.5866 | 61.2442 | 61.322
1148.5938 | 121.8475 | -61.3312 | 60.3241 | -0.10506 | 0.0071714 | 0.066251 | 0.06438 | 0.00086307 | -0.0083932 | -0.0021597 | -0.1077 | 0.0042425 | 0.0662 | 0.054745 | -0.014524 | 0.026126 | -0.0049389 | -0.21973 | 60.228 | -61.3449 | 60.2737 | -61.2213 | -61.6333 | -61.5646 | -0.16479 | 60.1959 | -61.3632 | 60.2737 | -61.3495 | -61.4685 | -61.377 | -0.013733 | -0.096131 | -0.050354 | 0.10986 | -0.23346 | -0.30212 | -0.21973 | -0.28839 | -0.032043 | -0.12817 | -0.050354 | -0.01831 | -0.045776 | -0.13733 | -0.013733 | -0.10529 | 0.1236 | 121.6187 | 0.013733 | 121.637 | 121.5729 | 121.5591 | 121.5591 | 121.5271 | -121.669 | -121.6873 | 121.6049 | 121.6049 | 61.1114 | 61.1664
1150.3281 | 121.8842 | -61.2625 | 60.4019 | -0.089798 | 0.0063168 | 0.063474 | 0.061175 | 8.47e-06 | -0.009675 | 0.00019006 | -0.068024 | 0.0061651 | 0.067268 | 0.054745 | -0.014951 | 0.026767 | -0.0042981 | -0.050354 | 60.2921 | -61.2762 | 60.4019 | -61.0748 | -61.4868 | -61.4731 | 0 | 60.2692 | -61.3129 | 60.3699 | -61.2076 | -61.3403 | -61.2808 | -0.013733 | -0.10986 | 0 | 0.18768 | -0.21057 | -0.2243 | -0.19684 | -0.21057 | -0.050354 | -0.13275 | -0.032044 | 0.054931 | -0.018311 | -0.07782 | 0.032043 | -0.027466 | 0.20142 | 121.6782 | 0.10529 | 121.6827 | 121.5683 | 121.582 | 121.5546 | 121.5317 | -121.6782 | -121.7148 | 121.6644 | 121.6324 | 61.2122 | 61.2625
1152.0781 | 121.8475 | -61.2991 | 60.3378 | -0.089798 | 0.005676 | 0.063474 | 0.062457 | -0.0019141 | -0.0090342 | -0.0034415 | -0.080231 | 0.0070197 | 0.065559 | 0.055813 | -0.012602 | 0.028262 | -0.0064343 | -0.14191 | 60.2509 | -61.3266 | 60.3561 | -61.1069 | -61.5555 | -61.5097 | -0.091553 | 60.1776 | -61.3449 | 60.2966 | -61.3129 | -61.4639 | -61.3678 | -0.027466 | -0.086976 | 0.01831 | 0.19226 | -0.21057 | -0.25635 | -0.18311 | -0.22888 | -0.045777 | -0.16022 | -0.041199 | -0.013733 | -0.068665 | -0.1648 | -0.022888 | -0.11902 | 0.21973 | 121.6827 | 0.032044 | 121.6415 | 121.5775 | 121.5225 | 121.55 | 121.4767 | -121.6644 | -121.6827 | 121.6553 | 121.5958 | 61.1572 | 61.2076
1153.7656 | 121.9803 | -61.2671 | 60.2921 | -0.16609 | 0.0075986 | 0.065396 | 0.060321 | -0.0010595 | -0.0090342 | -0.0023733 | -0.034454 | 0.0042425 | 0.066413 | 0.047696 | -0.013883 | 0.025058 | -0.0045117 | -0.14648 | 60.1776 | -61.2946 | 60.4065 | -61.0291 | -61.4822 | -61.4365 | 0.004578 | 60.1227 | -61.3129 | 60.4156 | -61.1893 | -61.3174 | -61.2488 | -0.027466 | -0.11444 | 0.11444 | 0.23804 | -0.16937 | -0.21515 | -0.14191 | -0.18768 | -0.045776 | -0.16937 | 0.1236 | 0.07782 | 0.018311 | -0.050354 | 0.064087 | -0.004578 | 0.2655 | 121.7011 | 0.1236 | 121.7285 | 121.4722 | 121.4355 | 121.4447 | 121.3898 | -121.5866 | -121.6049 | 121.6736 | 121.6827 | 61.1206 | 61.2717
1155.5156 | 121.9208 | -61.2213 | 60.3607 | -0.17372 | 0.0048214 | 0.064756 | 0.059253 | 0.0034265 | -0.009675 | -0.0025869 | -0.0008851 | 0.0048833 | 0.06385 | 0.044919 | -0.012602 | 0.025485 | -0.0042981 | -0.14648 | 60.1776 | -61.2854 | 60.4248 | -61.0153 | -61.4868 | -61.4227 | 0.027466 | 60.1593 | -61.2854 | 60.4065 | -61.1938 | -61.2946 | -61.2396 | -0.064087 | -0.18311 | 0.064087 | 0.20599 | -0.20142 | -0.2655 | -0.13733 | -0.20142 | -0.064087 | -0.20142 | 0.045776 | 0.027465 | -0.018311 | -0.073243 | 0.045776 | -0.009156 | 0.27008 | 121.7102 | 0.091552 | 121.6919 | 121.463 | 121.4447 | 121.3989 | 121.3806 | -121.6461 | -121.6461 | 121.6461 | 121.6278 | 61.0748 | 61.2488
1157.2656 | 121.8384 | -61.3083 | 60.3745 | -0.10506 | 0.0086668 | 0.066464 | 0.06203 | 0.0032129 | -0.007966 | -0.0017325 | -0.086334 | 0.0053107 | 0.065559 | 0.058377 | -0.014738 | 0.027408 | -0.0038709 | -0.16937 | 60.2142 | -61.3358 | 60.3149 | -61.1481 | -61.5967 | -61.5509 | -0.1236 | 60.1868 | -61.3495 | 60.2829 | -61.3358 | -61.4502 | -61.3632 | -0.027465 | -0.16022 | -0.05951 | 0.16022 | -0.24261 | -0.28839 | -0.21515 | -0.26093 | -0.041198 | -0.18768 | -0.091553 | -0.027465 | -0.054931 | -0.14191 | -0.013733 | -0.10071 | 0.18768 | 121.6507 | 0.013733 | 121.6324 | 121.55 | 121.5363 | 121.5225 | 121.4951 | -121.7102 | -121.7239 | 121.6232 | 121.5912 | 61.1389 | 61.1847
1159.0156 | 121.907 | -61.1938 | 60.4385 | -0.097427 | 0.0067442 | 0.065824 | 0.058825 | -0.0010595 | -0.008607 | -0.0036551 | 0.0021667 | 0.0033881 | 0.065345 | 0.048977 | -0.014097 | 0.025058 | -0.0030163 | 0.036621 | 60.2554 | -61.2534 | 60.5072 | -60.9329 | -61.3724 | -61.3129 | 0.17395 | 60.2783 | -61.203 | 60.4568 | -61.1206 | -61.235 | -61.203 | -0.059509 | -0.18311 | 0.068664 | 0.26093 | -0.11902 | -0.17853 | -0.059509 | -0.11902 | -0.009155 | -0.16022 | 0.01831 | 0.073243 | -0.009155 | -0.041198 | 0 | -0.032043 | 0.32044 | 121.7606 | 0.082398 | 121.6599 | 121.5088 | 121.4813 | 121.4493 | 121.4722 | -121.6919 | -121.6415 | 121.7011 | 121.6507 | 61.2305 | 61.3678
1160.7031 | 121.9345 | -61.2122 | 60.3561 | -0.097427 | 0.0067442 | 0.067533 | 0.05968 | 0.0012903 | -0.0083932 | -0.0057913 | -0.01004 | 0.0053107 | 0.066627 | 0.046841 | -0.014951 | 0.025699 | -0.0066479 | -0.11444 | 60.2142 | -61.2671 | 60.4156 | -61.0245 | -61.4502 | -61.3953 | 0.013733 | 60.2188 | -61.2717 | 60.4156 | -61.1801 | -61.2808 | -61.2442 | -0.054932 | -0.14191 | 0.059509 | 0.18768 | -0.18311 | -0.23804 | -0.12817 | -0.1831 | -0.059509 | -0.13733 | 0.059509 | 0.032043 | -0.032044 | -0.068665 | 0.027465 | -0.009156 | 0.24262 | 121.6827 | 0.091552 | 121.6873 | 121.4813 | 121.4905 | 121.4264 | 121.431 | -121.6232 | -121.6278 | 121.6278 | 121.6278 | 61.0977 | 61.2259
1162.4375 | 121.9803 | -61.1847 | 60.4019 | -0.06691 | 0.0026852 | 0.064328 | 0.059893 | -0.0023413 | -0.010743 | -0.0032277 | 0.014374 | 0.0042425 | 0.065345 | 0.053891 | -0.014311 | 0.026553 | -0.0055799 | 0.009155 | 60.2554 | -61.2305 | 60.5255 | -60.91 | -61.3495 | -61.3083 | 0.20599 | 60.2371 | -61.2076 | 60.5072 | -61.0794 | -61.1847 | -61.1481 | -0.045777 | -0.14648 | 0.1236 | 0.27466 | -0.1236 | -0.1648 | -0.07782 | -0.11902 | -0.022889 | -0.16479 | 0.10529 | 0.10528 | 0.036621 | 0 | 0.05951 | 0.022889 | 0.32043 | 121.756 | 0.12817 | 121.7148 | 121.4859 | 121.4447 | 121.4401 | 121.4218 | -121.6324 | -121.6095 | 121.7102 | 121.6919 | 61.1938 | 61.3907
1164.1875 | 121.8567 | -61.2122 | 60.4431 | -0.082169 | 0.0067442 | 0.066037 | 0.059466 | -0.0025549 | -0.0083932 | -0.00045074 | -0.0008851 | 0.0040289 | 0.065345 | 0.056241 | -0.014097 | 0.025058 | -0.0042981 | 0.022888 | 60.2783 | -61.2259 | 60.4523 | -61.0107 | -61.4594 | -61.3998 | 0.086975 | 60.2829 | -61.2488 | 60.3653 | -61.2076 | -61.3266 | -61.2762 | -0.013733 | -0.16479 | 0.009156 | 0.20142 | -0.18768 | -0.24719 | -0.17395 | -0.23346 | -0.036621 | -0.16022 | -0.07782 | 0.004577 | -0.064087 | -0.11444 | -0.027466 | -0.07782 | 0.21515 | 121.6782 | 0.041198 | 121.6141 | 121.5042 | 121.5317 | 121.4905 | 121.4951 | -121.669 | -121.6919 | 121.6644 | 121.5775 | 61.235 | 61.2991
1165.875 | 121.9757 | -61.2762 | 60.2921 | -0.15083 | 0.008453 | 0.066037 | 0.063098 | 0.0012903 | -0.0090342 | -0.0028005 | -0.071076 | 0.0040289 | 0.065345 | 0.0509 | -0.015806 | 0.026126 | -0.0036573 | -0.1831 | 60.1776 | -61.322 | 60.4065 | -61.0382 | -61.4868 | -61.4456 | -0.022888 | 60.1639 | -61.3174 | 60.4065 | -61.2076 | -61.322 | -61.2488 | -0.045776 | -0.11444 | 0.11444 | 0.23804 | -0.16937 | -0.21057 | -0.1236 | -0.16479 | -0.041199 | -0.12817 | 0.11444 | 0.068664 | 0.027466 | -0.045776 | 0.068665 | -0.004577 | 0.28381 | 121.7285 | 0.10986 | 121.7239 | 121.4996 | 121.4813 | 121.4539 | 121.4401 | -121.6141 | -121.6095 | 121.6827 | 121.6827 | 61.0931 | 61.2534
1167.625 | 121.9666 | -61.2625 | 60.3287 | -0.15846 | 0.0067442 | 0.067319 | 0.060534 | 0.0025721 | -0.006257 | -0.0021597 | -0.049713 | 0.0029607 | 0.06385 | 0.053677 | -0.01367 | 0.027408 | -0.0064343 | -0.13275 | 60.1456 | -61.3449 | 60.4294 | -61.0291 | -61.4868 | -61.409 | 0.018311 | 60.1273 | -61.3037 | 60.4294 | -61.1801 | -61.29 | -61.2396 | -0.082398 | -0.1831 | 0.10071 | 0.23346 | -0.14648 | -0.2243 | -0.064087 | -0.14191 | -0.041199 | -0.20142 | 0.10071 | 0.082397 | 0.022888 | -0.027466 | 0.064087 | 0.013733 | 0.31586 | 121.7743 | 0.1236 | 121.7331 | 121.4905 | 121.431 | 121.4081 | 121.3898 | -121.6736 | -121.6324 | 121.6919 | 121.6919 | 61.1298 | 61.2808
1169.3906 | 121.8521 | -61.3129 | 60.3745 | -0.089798 | 0.0035398 | 0.064756 | 0.061816 | -0.0017005 | -0.0075388 | -0.0030141 | -0.10464 | 0.0048833 | 0.065559 | 0.055813 | -0.014097 | 0.026553 | -0.0042981 | -0.23346 | 60.1913 | -61.3266 | 60.3058 | -61.1893 | -61.6287 | -61.5646 | -0.13733 | 60.1913 | -61.3586 | 60.3104 | -61.3358 | -61.4548 | -61.3678 | -0.013733 | -0.18311 | -0.068665 | 0.1236 | -0.25177 | -0.31586 | -0.23804 | -0.30212 | -0.045777 | -0.18311 | -0.064087 | -0.022888 | -0.054932 | -0.14191 | -0.009155 | -0.09613 | 0.13733 | 121.6324 | 0.022889 | 121.669 | 121.5179 | 121.55 | 121.5042 | 121.5042 | -121.7011 | -121.7331 | 121.6187 | 121.6232 | 61.0794 | 61.1755
1171.1406 | 121.9025 | -61.2442 | 60.4019 | -0.089798 | 0.0050352 | 0.064328 | 0.061816 | -0.0010595 | -0.01117 | -0.0053641 | -0.11075 | 0.0061651 | 0.064918 | 0.063717 | -0.015165 | 0.027194 | -0.0053661 | -0.07782 | 60.228 | -61.2991 | 60.3928 | -61.0428 | -61.4914 | -61.4594 | 0.036621 | 60.2509 | -61.2946 | 60.379 | -61.2259 | -61.3495 | -61.2854 | -0.054931 | -0.17395 | -0.009156 | 0.20142 | -0.21515 | -0.24719 | -0.16022 | -0.19226 | -0.050354 | -0.15106 | -0.022889 | 0.018311 | -0.041198 | -0.10529 | 0.009156 | -0.054931 | 0.25635 | 121.6919 | 0.068665 | 121.6736 | 121.5271 | 121.5454 | 121.4722 | 121.4951 | -121.701 | -121.6965 | 121.637 | 121.6232 | 61.1664 | 61.2808
1172.8281 | 121.8933 | -61.3129 | 60.3149 | -0.082169 | 0.009094 | 0.063047 | 0.061602 | 0.00086307 | -0.0088206 | -0.0028005 | -0.10159 | 0.0055243 | 0.0662 | 0.053036 | -0.013242 | 0.025912 | -0.0068615 | -0.21973 | 60.2005 | -61.3358 | 60.3149 | -61.1526 | -61.5921 | -61.5417 | -0.13275 | 60.1913 | -61.3815 | 60.3149 | -61.3037 | -61.4182 | -61.3358 | -0.022888 | -0.11444 | 0 | 0.16022 | -0.22888 | -0.27924 | -0.20599 | -0.25635 | -0.068665 | -0.1236 | 0 | 0.009155 | -0.022888 | -0.10529 | 0.045777 | -0.036621 | 0.18311 | 121.6507 | 0.07782 | 121.6965 | 121.5363 | 121.5729 | 121.5134 | 121.5042 | -121.6507 | -121.6965 | 121.6278 | 121.6278 | 61.0931 | 61.1801
1174.5781 | 121.9757 | -61.1435 | 60.4019 | -0.11269 | 0.0054624 | 0.063474 | 0.060748 | -0.0040503 | -0.0081796 | -0.0025869 | 0.0021667 | 0.0040289 | 0.064277 | 0.048123 | -0.013456 | 0.025058 | -0.0042981 | 0.022888 | 60.2234 | -61.2305 | 60.5438 | -60.8826 | -61.3174 | -61.2808 | 0.20599 | 60.2417 | -61.2167 | 60.5209 | -61.0748 | -61.171 | -61.1526 | -0.086975 | -0.17853 | 0.14191 | 0.26093 | -0.13733 | -0.17395 | -0.050354 | -0.086975 | -0.073242 | -0.16022 | 0.11902 | 0.068665 | -0.009155 | -0.027465 | 0.064087 | 0.045777 | 0.3479 | 121.7743 | 0.14191 | 121.7377 | 121.4539 | 121.4584 | 121.3669 | 121.3852 | -121.6324 | -121.6187 | 121.6873 | 121.6644 | 61.1664 | 61.3495
1176.2812 | 121.9254 | -61.2167 | 60.3653 | -0.082169 | 0.003967 | 0.064115 | 0.059253 | 0.0010767 | -0.01053 | -0.00087794 | -0.019196 | 0.0057379 | 0.0662 | 0.051114 | -0.014738 | 0.025912 | -0.0045117 | -0.09613 | 60.2005 | -61.2488 | 60.434 | -61.0291 | -61.441 | -61.409 | 0.036621 | 60.2234 | -61.2762 | 60.434 | -61.1618 | -61.2671 | -61.2213 | -0.032043 | -0.1648 | 0.068665 | 0.18768 | -0.19226 | -0.2243 | -0.16022 | -0.19226 | -0.059509 | -0.14191 | 0.068665 | 0.054932 | -0.004577 | -0.050354 | 0.054932 | 0.009155 | 0.21973 | 121.6827 | 0.11444 | 121.7102 | 121.4493 | 121.4996 | 121.4172 | 121.4401 | -121.6141 | -121.6415 | 121.6507 | 121.6507 | 61.1206 | 61.2534
1178.0312 | 122.0123 | -61.1984 | 60.3928 | -0.12794 | 0.0026852 | 0.066678 | 0.058398 | 0.0010767 | -0.0090342 | -0.0034415 | -0.0039367 | 0.0033881 | 0.0662 | 0.047055 | -0.013883 | 0.023563 | -0.0038709 | -0.022888 | 60.2417 | -61.2396 | 60.5072 | -60.9512 | -61.3815 | -61.322 | 0.14191 | 60.2417 | -61.2488 | 60.4889 | -61.0886 | -61.203 | -61.1572 | -0.041199 | -0.15106 | 0.11444 | 0.24719 | -0.1236 | -0.18311 | -0.082397 | -0.14191 | -0.050354 | -0.15106 | 0.096131 | 0.10986 | 0.041198 | -0.004578 | 0.091552 | 0.045776 | 0.28839 | 121.7468 | 0.16022 | 121.7377 | 121.4813 | 121.4905 | 121.4401 | 121.4401 | -121.6324 | -121.6415 | 121.7056 | 121.6873 | 61.1755 | 61.3403
1179.7344 | 121.8338 | -61.2259 | 60.4431 | -0.05928 | 0.0048214 | 0.064542 | 0.062243 | -0.0017005 | -0.010957 | -0.0040823 | -0.064972 | 0.0029607 | 0.065559 | 0.057736 | -0.014524 | 0.025699 | -0.0055799 | -0.022888 | 60.2737 | -61.2213 | 60.4111 | -61.0428 | -61.4639 | -61.4227 | 0.054932 | 60.3012 | -61.2625 | 60.3836 | -61.2167 | -61.3358 | -61.2808 | 0.004578 | -0.16937 | -0.032043 | 0.1831 | -0.19684 | -0.23804 | -0.20142 | -0.24262 | -0.036621 | -0.14191 | -0.059509 | 0.009155 | -0.054932 | -0.10986 | -0.018311 | -0.073242 | 0.17853 | 121.6324 | 0.045776 | 121.6461 | 121.4951 | 121.5637 | 121.4996 | 121.5271 | -121.6644 | -121.7056 | 121.637 | 121.6095 | 61.203 | 61.2808
1181.4844 | 121.8704 | -61.2122 | 60.4568 | -0.074539 | 0.0048214 | 0.064328 | 0.060321 | -0.0014867 | -0.010957 | -0.0028005 | -0.052765 | 0.0072333 | 0.06385 | 0.044064 | -0.015165 | 0.026126 | -0.0072889 | 0.050354 | 60.2829 | -61.2213 | 60.5026 | -60.965 | -61.3815 | -61.3586 | 0.13275 | 60.2783 | -61.2122 | 60.434 | -61.1755 | -61.2991 | -61.2717 | -0.009155 | -0.17395 | 0.045777 | 0.24719 | -0.14648 | -0.16937 | -0.13733 | -0.16022 | 0 | -0.17853 | -0.022888 | 0.036621 | -0.059509 | -0.086975 | -0.059509 | -0.086975 | 0.25635 | 121.7239 | 0.036621 | 121.6461 | 121.5042 | 121.4905 | 121.4951 | 121.4905 | -121.6782 | -121.669 | 121.7148 | 121.6461 | 61.2625 | 61.3449
1183.1719 | 121.9757 | -61.1847 | 60.4202 | -0.10506 | 0.0048214 | 0.064756 | 0.05968 | -0.00041873 | -0.01053 | -0.0028005 | -0.022247 | 0.0036017 | 0.068336 | 0.054745 | -0.013456 | 0.025912 | -0.0013073 | -0.073242 | 60.2371 | -61.2534 | 60.4568 | -60.9924 | -61.4273 | -61.3632 | 0.07782 | 60.2325 | -61.2625 | 60.4706 | -61.1023 | -61.2076 | -61.1755 | -0.068665 | -0.1831 | 0.036621 | 0.19226 | -0.17853 | -0.24262 | -0.10986 | -0.17395 | -0.07782 | -0.18768 | 0.050354 | 0.082397 | 0.009155 | -0.022889 | 0.086975 | 0.054931 | 0.26093 | 121.7102 | 0.16022 | 121.7331 | 121.4905 | 121.4951 | 121.4218 | 121.4172 | -121.6736 | -121.6827 | 121.6415 | 121.6553 | 61.1114 | 61.2625
1184.9062 | 121.8796 | -61.2717 | 60.3882 | -0.12794 | 0.0061032 | 0.066251 | 0.061389 | -0.00063233 | -0.010957 | 0.00083106 | -0.1199 | 0.0042425 | 0.067054 | 0.049618 | -0.014097 | 0.026767 | -0.0047253 | -0.091553 | 60.2417 | -61.3083 | 60.4156 | -61.0519 | -61.4777 | -61.4685 | 0.018311 | 60.2325 | -61.3083 | 60.3836 | -61.2305 | -61.3632 | -61.2762 | -0.036622 | -0.14649 | 0.027465 | 0.21973 | -0.19684 | -0.20599 | -0.16022 | -0.16937 | -0.036622 | -0.15564 | -0.004578 | 0.041198 | -0.004578 | -0.091553 | 0.032044 | -0.054931 | 0.25635 | 121.7239 | 0.07782 | 121.6919 | 121.55 | 121.5408 | 121.5134 | 121.5042 | -121.6965 | -121.6965 | 121.6873 | 121.6553 | 61.1801 | 61.29
1186.6562 | 121.9299 | -61.2122 | 60.3653 | -0.12032 | 0.0033262 | 0.066678 | 0.060534 | -0.0046911 | -0.011598 | -0.0032277 | -0.040558 | 0.0055243 | 0.065986 | 0.0462 | -0.014951 | 0.024417 | -0.0028027 | -0.11902 | 60.1822 | -61.2671 | 60.4431 | -61.0016 | -61.4594 | -61.3998 | 0.036621 | 60.2097 | -61.2717 | 60.4248 | -61.1893 | -61.29 | -61.235 | -0.054932 | -0.18311 | 0.07782 | 0.21057 | -0.18768 | -0.24719 | -0.13275 | -0.19226 | -0.059509 | -0.15564 | 0.05951 | 0.022888 | -0.022888 | -0.07782 | 0.036621 | -0.018311 | 0.2655 | 121.7102 | 0.082397 | 121.6965 | 121.4493 | 121.4813 | 121.3943 | 121.4218 | -121.6324 | -121.637 | 121.6553 | 121.637 | 61.0931 | 61.2488
1188.3438 | 121.8246 | -61.322 | 60.3424 | -0.13557 | 0.007385 | 0.067105 | 0.063098 | -0.0027685 | -0.0088206 | -0.0010915 | -0.13211 | 0.0040289 | 0.064491 | 0.048764 | -0.015165 | 0.027408 | -0.0045117 | -0.19226 | 60.2234 | -61.3083 | 60.3378 | -61.171 | -61.6058 | -61.5463 | -0.16022 | 60.2325 | -61.3358 | 60.3012 | -61.3541 | -61.4777 | -61.3815 | 0.013732 | -0.11902 | -0.004577 | 0.15106 | -0.22431 | -0.28381 | -0.23804 | -0.29755 | -0.013733 | -0.10986 | -0.041199 | -0.032044 | -0.05951 | -0.15564 | -0.045777 | -0.14191 | 0.13733 | 121.6461 | -0.018311 | 121.637 | 121.5317 | 121.5683 | 121.5454 | 121.5546 | -121.6507 | -121.6782 | 121.6599 | 121.6232 | 61.1298 | 61.1618
1190.0938 | 121.8933 | -61.2946 | 60.347 | -0.12032 | 0.0061032 | 0.066678 | 0.061175 | 0.0025721 | -0.0083932 | -0.0038687 | -0.1077 | 0.0050971 | 0.0662 | 0.056241 | -0.015592 | 0.027194 | -0.0036573 | -0.22888 | 60.228 | -61.2854 | 60.3333 | -61.1435 | -61.5829 | -61.528 | -0.14191 | 60.1913 | -61.3312 | 60.3516 | -61.2762 | -61.4182 | -61.3174 | 0.009156 | -0.11902 | -0.013733 | 0.15106 | -0.23346 | -0.28839 | -0.24262 | -0.29755 | -0.036621 | -0.15564 | 0.004577 | 0.018311 | -0.022888 | -0.1236 | 0.013733 | -0.086975 | 0.14191 | 121.6187 | 0.054932 | 121.6827 | 121.5134 | 121.5225 | 121.5225 | 121.4859 | -121.6324 | -121.6782 | 121.6278 | 121.6461 | 61.0657 | 61.1526
1191.7812 | 121.9757 | -61.1526 | 60.4202 | -0.10506 | 0.0037534 | 0.063901 | 0.057971 | -0.0025549 | -0.010957 | -0.0021597 | -0.022247 | 0.0046697 | 0.065345 | 0.049191 | -0.012388 | 0.024631 | -0.0053661 | 0.064087 | 60.26 | -61.2213 | 60.5713 | -60.878 | -61.322 | -61.2808 | 0.22888 | 60.2783 | -61.203 | 60.5255 | -61.0519 | -61.171 | -61.1572 | -0.068664 | -0.16022 | 0.15106 | 0.27466 | -0.12817 | -0.16937 | -0.05951 | -0.10071 | -0.050354 | -0.14191 | 0.10529 | 0.10071 | -0.004578 | -0.01831 | 0.045776 | 0.032044 | 0.34332 | 121.7926 | 0.15106 | 121.7285 | 121.4813 | 121.4813 | 121.4127 | 121.431 | -121.6415 | -121.6232 | 121.7239 | 121.6782 | 61.2167 | 61.3815
1193.5312 | 121.843 | -61.2122 | 60.4706 | -0.089798 | 0.0031126 | 0.061551 | 0.062457 | -0.0029821 | -0.0092478 | -0.0010915 | -0.080231 | 0.0059515 | 0.067268 | 0.0556 | -0.012174 | 0.027835 | -0.0040845 | -0.041199 | 60.3378 | -61.2259 | 60.4202 | -61.0336 | -61.4502 | -61.4365 | 0.036621 | 60.3012 | -61.2671 | 60.3882 | -61.2076 | -61.322 | -61.2808 | -0.013733 | -0.13275 | -0.050354 | 0.17853 | -0.2243 | -0.23804 | -0.21057 | -0.2243 | -0.054932 | -0.16937 | -0.082397 | 0.004577 | -0.068665 | -0.10986 | -0.013733 | -0.054931 | 0.19226 | 121.6461 | 0.059509 | 121.6553 | 121.5637 | 121.5683 | 121.55 | 121.5134 | -121.6965 | -121.7377 | 121.6324 | 121.6003 | 61.171 | 61.2488
1195.2188 | 121.8704 | -61.1938 | 60.4614 | -0.06691 | 0.0050352 | 0.063687 | 0.063739 | 0.00086307 | -0.012239 | -0.0028005 | -0.06192 | 0.0044561 | 0.066627 | 0.054532 | -0.013242 | 0.025912 | -0.0053661 | -0.054932 | 60.3241 | -61.2259 | 60.4065 | -61.0474 | -61.4548 | -61.4456 | -0.004578 | 60.3058 | -61.2991 | 60.3928 | -61.2076 | -61.322 | -61.2579 | -0.032043 | -0.13733 | -0.054932 | 0.14649 | -0.25177 | -0.26093 | -0.21973 | -0.22888 | -0.10528 | -0.15564 | -0.068665 | -0.013733 | -0.064087 | -0.12817 | 0.041198 | -0.022888 | 0.17853 | 121.6324 | 0.091552 | 121.6919 | 121.55 | 121.6049 | 121.5179 | 121.4996 | -121.6873 | -121.7606 | 121.6003 | 121.5866 | 61.1389 | 61.1893
1196.9688 | 121.9208 | -61.203 | 60.3973 | -0.12794 | 0.0069578 | 0.064542 | 0.060534 | -0.0025549 | -0.007966 | -0.0017325 | -0.016144 | 0.0029607 | 0.067481 | 0.044705 | -0.014951 | 0.027621 | -0.0064343 | -0.086975 | 60.2646 | -61.2442 | 60.4431 | -61.0016 | -61.441 | -61.377 | 0.032043 | 60.2417 | -61.2579 | 60.4431 | -61.1664 | -61.2579 | -61.2122 | -0.041199 | -0.13275 | 0.045776 | 0.20142 | -0.17395 | -0.23804 | -0.13275 | -0.19684 | -0.054932 | -0.15564 | 0.045776 | 0.036621 | -0.009155 | -0.054932 | 0.045777 | 0 | 0.24262 | 121.6873 | 0.091553 | 121.7011 | 121.5088 | 121.4996 | 121.4676 | 121.4447 | -121.6415 | -121.6553 | 121.6461 | 121.6461 | 61.116 | 61.235
1198.6562 | 121.8567 | -61.2717 | 60.3561 | -0.074539 | 0.008453 | 0.065396 | 0.063739 | 0.0021447 | -0.0073252 | -0.0030141 | -0.098541 | 0.0048833 | 0.065132 | 0.052823 | -0.014524 | 0.027408 | -0.0055799 | -0.23804 | 60.2005 | -61.3174 | 60.3287 | -61.1481 | -61.5829 | -61.5326 | -0.15106 | 60.2188 | -61.3449 | 60.3287 | -61.2854 | -61.4182 | -61.3358 | -0.045777 | -0.15564 | -0.027466 | 0.1236 | -0.26093 | -0.31128 | -0.21515 | -0.2655 | -0.073243 | -0.13733 | -0.027466 | -0.013733 | -0.064087 | -0.14648 | 0.009156 | -0.073242 | 0.16937 | 121.6461 | 0.05951 | 121.6736 | 121.5179 | 121.5637 | 121.4722 | 121.4905 | -121.6736 | -121.7011 | 121.6003 | 121.6003 | 61.0336 | 61.1206
1200.4062 | 121.8979 | -61.2579 | 60.3607 | -0.074539 | 0.0065304 | 0.064542 | 0.063098 | -0.0019141 | -0.009675 | 0.0014719 | -0.1199 | 0.0042425 | 0.06385 | 0.057095 | -0.01367 | 0.027408 | -0.0081433 | -0.10529 | 60.2692 | -61.3037 | 60.4294 | -61.0336 | -61.4777 | -61.4365 | 0.027466 | 60.2463 | -61.3037 | 60.4065 | -61.1984 | -61.322 | -61.2579 | -0.045776 | -0.091553 | 0.068664 | 0.22431 | -0.17853 | -0.21973 | -0.13275 | -0.17395 | -0.045776 | -0.11444 | 0.045776 | 0.05951 | 0 | -0.064086 | 0.045776 | -0.01831 | 0.27008 | 121.7331 | 0.10529 | 121.7102 | 121.5729 | 121.55 | 121.5271 | 121.5042 | -121.6644 | -121.6644 | 121.6873 | 121.6644 | 61.1526 | 61.2854
1202.1562 | 121.907 | -61.2991 | 60.3378 | -0.1432 | 0.007385 | 0.067746 | 0.062457 | 0.0029993 | -0.0098886 | -0.0040823 | -0.049713 | 0.0046697 | 0.068122 | 0.053677 | -0.013456 | 0.027835 | -0.0034435 | -0.22888 | 60.2554 | -61.3266 | 60.3424 | -61.1206 | -61.5646 | -61.5143 | -0.12817 | 60.2188 | -61.3495 | 60.3653 | -61.2625 | -61.3907 | -61.2991 | -0.027466 | -0.082398 | 0.004577 | 0.17853 | -0.21515 | -0.2655 | -0.18768 | -0.23804 | -0.050354 | -0.11902 | 0.027465 | 0.036621 | 0 | -0.091553 | 0.050354 | -0.041199 | 0.20599 | 121.669 | 0.086975 | 121.7148 | 121.582 | 121.5683 | 121.5546 | 121.5179 | -121.6644 | -121.6873 | 121.6415 | 121.6644 | 61.0703 | 61.171
1203.9062 | 121.9254 | -61.1755 | 60.4065 | -0.12032 | 0.0035398 | 0.066464 | 0.060962 | -0.0031957 | -0.0083932 | -0.00066434 | 0.0052185 | 0.0042425 | 0.065345 | 0.045559 | -0.014524 | 0.026553 | -0.0040845 | -0.11444 | 60.2737 | -61.2625 | 60.4568 | -60.9924 | -61.4319 | -61.377 | 0.027466 | 60.2371 | -61.2442 | 60.4431 | -61.1572 | -61.2534 | -61.2122 | -0.086975 | -0.13275 | 0.050354 | 0.1831 | -0.20142 | -0.25635 | -0.11444 | -0.16937 | -0.068665 | -0.16937 | 0.036621 | 0.01831 | -0.036621 | -0.07782 | 0.032044 | -0.009155 | 0.27008 | 121.7194 | 0.086975 | 121.6873 | 121.5363 | 121.4813 | 121.4493 | 121.4127 | -121.669 | -121.6507 | 121.6324 | 121.6187 | 61.0611 | 61.203
1205.6562 | 121.843 | -61.1893 | 60.4614 | -0.051651 | 0.005676 | 0.064969 | 0.061175 | -0.0038367 | -0.0088206 | -0.00045074 | -0.034454 | 0.0055243 | 0.065559 | 0.049618 | -0.014951 | 0.025058 | -0.0028027 | 0.009155 | 60.3104 | -61.2167 | 60.4523 | -60.997 | -61.4044 | -61.3724 | 0.064087 | 60.3149 | -61.2167 | 60.4202 | -61.171 | -61.2946 | -61.2442 | -0.027466 | -0.15106 | -0.009155 | 0.19226 | -0.1831 | -0.21515 | -0.15564 | -0.18768 | -0.027466 | -0.14649 | -0.041199 | 0.018311 | -0.054932 | -0.10529 | -0.027466 | -0.07782 | 0.21973 | 121.669 | 0.045777 | 121.637 | 121.5271 | 121.5317 | 121.4996 | 121.5042 | -121.6782 | -121.6782 | 121.6415 | 121.6095 | 61.1984 | 61.2534
1207.3906 | 121.8475 | -61.29 | 60.3882 | -0.11269 | 0.0061032 | 0.065396 | 0.064166 | -0.00041873 | -0.010316 | -0.0032277 | -0.10159 | 0.0059515 | 0.067268 | 0.051968 | -0.015165 | 0.025912 | -0.0015209 | -0.21973 | 60.2325 | -61.3449 | 60.3333 | -61.1618 | -61.6058 | -61.5326 | -0.17395 | 60.228 | -61.3449 | 60.3333 | -61.3129 | -61.4319 | -61.3358 | -0.054932 | -0.15564 | -0.054932 | 0.12817 | -0.24262 | -0.31586 | -0.18768 | -0.26093 | -0.054932 | -0.16022 | -0.054932 | -0.022888 | -0.045776 | -0.14191 | 0.009156 | -0.086975 | 0.18311 | 121.6782 | 0.032044 | 121.6782 | 121.5775 | 121.5729 | 121.5225 | 121.5179 | -121.7331 | -121.7331 | 121.6232 | 121.6232 | 61.0703 | 61.116
1209.0938 | 121.9849 | -61.1481 | 60.4477 | -0.11269 | 0.0058896 | 0.062406 | 0.062671 | -0.0034095 | -0.01117 | -0.00066434 | -0.0039367 | 0.0038153 | 0.064918 | 0.051968 | -0.012602 | 0.025485 | -0.0025891 | 0.013733 | 60.2463 | -61.1984 | 60.5576 | -60.8688 | -61.3083 | -61.2808 | 0.22888 | 60.2875 | -61.1847 | 60.553 | -61.0245 | -61.1481 | -61.1069 | -0.050354 | -0.20142 | 0.10986 | 0.27924 | -0.13275 | -0.16022 | -0.082398 | -0.10986 | -0.036621 | -0.16022 | 0.10529 | 0.1236 | 0.041198 | 0 | 0.077819 | 0.036621 | 0.32959 | 121.756 | 0.16022 | 121.7377 | 121.4447 | 121.4722 | 121.3943 | 121.4355 | -121.6461 | -121.6324 | 121.7056 | 121.7011 | 61.1618 | 61.377
1210.8438 | 121.9299 | -61.2762 | 60.3424 | -0.12794 | 0.0058896 | 0.066251 | 0.06203 | -0.0036231 | -0.007966 | -0.0032277 | -0.10464 | 0.0072333 | 0.065345 | 0.051968 | -0.015379 | 0.027621 | -0.0032299 | -0.2243 | 60.2463 | -61.2991 | 60.3561 | -61.116 | -61.5555 | -61.5005 | -0.11444 | 60.1913 | -61.3266 | 60.3928 | -61.2259 | -61.3495 | -61.2671 | -0.022888 | -0.09613 | 0.013733 | 0.16022 | -0.2243 | -0.27924 | -0.20142 | -0.25635 | -0.050354 | -0.15106 | 0.050354 | 0.050354 | 0.009155 | -0.073242 | 0.059509 | -0.022888 | 0.1831 | 121.6553 | 0.10071 | 121.7194 | 121.5454 | 121.5179 | 121.5225 | 121.4676 | -121.6415 | -121.669 | 121.6324 | 121.669 | 61.0519 | 61.1618
1212.5938 | 121.9986 | -61.1572 | 60.4294 | -0.089798 | 0.0054624 | 0.064756 | 0.058398 | -0.0034095 | -0.006898 | -0.0013051 | 0.023529 | 0.0040289 | 0.065132 | 0.051755 | -0.01602 | 0.024631 | -0.0089977 | 0.018311 | 60.2692 | -61.2076 | 60.5621 | -60.8597 | -61.2991 | -61.2534 | 0.21973 | 60.2921 | -61.1847 | 60.5301 | -61.0291 | -61.1526 | -61.0977 | -0.050354 | -0.16022 | 0.13275 | 0.29755 | -0.09613 | -0.14191 | -0.045776 | -0.091552 | -0.027465 | -0.13733 | 0.10071 | 0.12817 | 0.05951 | 0.004578 | 0.086975 | 0.032043 | 0.3479 | 121.7697 | 0.15564 | 121.7148 | 121.4767 | 121.4767 | 121.4264 | 121.4493 | -121.637 | -121.6141 | 121.7194 | 121.6873 | 61.1755 | 61.377
1214.3438 | 121.9482 | -61.2259 | 60.3653 | -0.18135 | 0.0061032 | 0.066464 | 0.060962 | -0.0042639 | -0.011384 | -0.0049367 | -0.064972 | 0.0044561 | 0.065772 | 0.052823 | -0.015806 | 0.02634 | -0.0047253 | -0.16022 | 60.1822 | -61.2808 | 60.4706 | -60.9833 | -61.441 | -61.3907 | 0.032043 | 60.1959 | -61.2946 | 60.466 | -61.1435 | -61.2625 | -61.1984 | -0.054932 | -0.18311 | 0.10529 | 0.24262 | -0.1648 | -0.21515 | -0.10986 | -0.16022 | -0.068665 | -0.16937 | 0.10071 | 0.082397 | 0.027466 | -0.036621 | 0.096131 | 0.032044 | 0.29755 | 121.7514 | 0.15106 | 121.7606 | 121.463 | 121.4905 | 121.4081 | 121.4218 | -121.6461 | -121.6599 | 121.6965 | 121.6919 | 61.0657 | 61.2579
1216.0312 | 121.9757 | -61.2488 | 60.347 | -0.23476 | 0.0088804 | 0.067319 | 0.060962 | 0.0019311 | -0.0090342 | -0.0010915 | -0.092438 | 0.0042425 | 0.0662 | 0.054745 | -0.016233 | 0.027408 | -0.0051525 | -0.15564 | 60.1959 | -61.2671 | 60.4477 | -61.0016 | -61.4594 | -61.409 | -0.004578 | 60.1822 | -61.2854 | 60.4568 | -61.171 | -61.3037 | -61.2122 | -0.018311 | -0.15106 | 0.10071 | 0.24719 | -0.16022 | -0.21057 | -0.14191 | -0.19226 | -0.036621 | -0.16479 | 0.10986 | 0.07782 | 0.036621 | -0.054932 | 0.073242 | -0.018311 | 0.2655 | 121.7148 | 0.11444 | 121.7422 | 121.463 | 121.4676 | 121.4447 | 121.431 | -121.6141 | -121.6324 | 121.6965 | 121.7056 | 61.0931 | 61.2442
1217.7812 | 121.875 | -61.1572 | 60.4935 | -0.12032 | 0.0033262 | 0.065183 | 0.05968 | 0.0023585 | -0.013093 | -0.0057913 | -0.028351 | 0.0038153 | 0.065132 | 0.054104 | -0.013029 | 0.02634 | -0.0047253 | 0.041199 | 60.3104 | -61.1847 | 60.5164 | -60.9283 | -61.3541 | -61.3266 | 0.14191 | 60.3104 | -61.1984 | 60.4523 | -61.1526 | -61.2671 | -61.2167 | -0.027465 | -0.1831 | 0.022888 | 0.22888 | -0.16937 | -0.19684 | -0.14191 | -0.16937 | -0.041198 | -0.1831 | -0.041198 | 0.004578 | -0.059509 | -0.10986 | -0.018311 | -0.068665 | 0.25635 | 121.701 | 0.045776 | 121.6507 | 121.4951 | 121.5088 | 121.4676 | 121.4676 | -121.6782 | -121.6919 | 121.6736 | 121.6095 | 61.1984 | 61.2991
1219.4844 | 121.9757 | -61.1343 | 60.4202 | -0.13557 | 0.0058896 | 0.063474 | 0.061389 | -0.0059729 | -0.012025 | -0.0021597 | -0.0069885 | 0.0053107 | 0.065132 | 0.051541 | -0.016233 | 0.027408 | -0.0066479 | 0.027466 | 60.2783 | -61.1755 | 60.5713 | -60.8643 | -61.29 | -61.2579 | 0.21515 | 60.2966 | -61.1938 | 60.5438 | -61.0336 | -61.1389 | -61.1343 | -0.041199 | -0.14191 | 0.15106 | 0.27008 | -0.1236 | -0.15564 | -0.082398 | -0.11444 | -0.05951 | -0.1236 | 0.1236 | 0.10071 | 0 | -0.004578 | 0.05951 | 0.054932 | 0.31128 | 121.7468 | 0.16022 | 121.7377 | 121.4539 | 121.4905 | 121.4127 | 121.431 | -121.5958 | -121.6141 | 121.7056 | 121.6782 | 61.1618 | 61.3495
1221.2344 | 121.8613 | -61.2122 | 60.4568 | -0.089798 | 0.0063168 | 0.062833 | 0.062671 | -0.0019141 | -0.008607 | -0.0030141 | -0.089386 | 0.0048833 | 0.0662 | 0.057095 | -0.014097 | 0.028903 | -0.0025891 | -0.041199 | 60.3241 | -61.2396 | 60.4111 | -61.0474 | -61.4685 | -61.4365 | 0.018311 | 60.2875 | -61.2442 | 60.4202 | -61.1847 | -61.3083 | -61.2442 | -0.027466 | -0.13275 | -0.045776 | 0.1648 | -0.2243 | -0.25635 | -0.19684 | -0.22888 | -0.032044 | -0.16937 | -0.036621 | 0.027466 | -0.032044 | -0.096131 | 0 | -0.064087 | 0.19226 | 121.6507 | 0.05951 | 121.6644 | 121.5637 | 121.5317 | 121.5363 | 121.4996 | -121.6965 | -121.7011 | 121.6232 | 121.6324 | 61.171 | 61.2305
1222.9844 | 121.9482 | -61.2625 | 60.3516 | -0.13557 | 0.007385 | 0.065183 | 0.063739 | -0.0029821 | -0.008607 | -0.0055777 | -0.086334 | 0.0053107 | 0.065986 | 0.050473 | -0.014738 | 0.025699 | -0.0047253 | -0.23804 | 60.2325 | -61.3129 | 60.379 | -61.0886 | -61.5234 | -61.4685 | -0.068665 | 60.1913 | -61.3174 | 60.434 | -61.203 | -61.3312 | -61.2305 | -0.050354 | -0.11902 | 0.027466 | 0.17395 | -0.20599 | -0.26093 | -0.15564 | -0.21057 | -0.054932 | -0.16022 | 0.082398 | 0.059509 | 0.032043 | -0.068665 | 0.086975 | -0.013733 | 0.2243 | 121.6919 | 0.11444 | 121.7514 | 121.5454 | 121.5088 | 121.4951 | 121.4539 | -121.6644 | -121.669 | 121.6415 | 121.6965 | 61.0245 | 61.1938
1224.7344 | 121.8475 | -61.1893 | 60.466 | -0.051651 | 0.0067442 | 0.064542 | 0.061602 | -0.0038367 | -0.0092478 | -0.0045095 | -0.04361 | 0.0044561 | 0.065772 | 0.054532 | -0.01367 | 0.025699 | -0.0072889 | -0.036621 | 60.3195 | -61.2167 | 60.4202 | -61.0153 | -61.441 | -61.4044 | 0.027466 | 60.3424 | -61.2305 | 60.3928 | -61.203 | -61.322 | -61.2534 | -0.027466 | -0.14648 | -0.045776 | 0.17395 | -0.21515 | -0.25177 | -0.18768 | -0.2243 | -0.041199 | -0.1236 | -0.073242 | -0.013733 | -0.064087 | -0.13275 | -0.022888 | -0.091552 | 0.20142 | 121.637 | 0.027466 | 121.6232 | 121.5363 | 121.5729 | 121.5088 | 121.5317 | -121.6827 | -121.6965 | 121.6095 | 121.582 | 61.1526 | 61.2167
1226.5 | 121.8384 | -61.2122 | 60.4523 | -0.089798 | 0.005676 | 0.064328 | 0.059893 | 8.47e-06 | -0.01053 | -0.0032277 | -0.071076 | 0.0044561 | 0.065772 | 0.051541 | -0.013242 | 0.025272 | -0.0045117 | -0.054932 | 60.2966 | -61.235 | 60.4202 | -61.0245 | -61.4548 | -61.3953 | 0.036621 | 60.3333 | -61.235 | 60.3973 | -61.1938 | -61.3174 | -61.2717 | -0.022888 | -0.15564 | -0.032044 | 0.18768 | -0.18311 | -0.24262 | -0.16022 | -0.21973 | -0.022888 | -0.11902 | -0.054932 | 0.01831 | -0.059509 | -0.10529 | -0.036621 | -0.082398 | 0.21057 | 121.6553 | 0.041198 | 121.6324 | 121.5317 | 121.5683 | 121.5088 | 121.5454 | -121.6873 | -121.6873 | 121.6324 | 121.6095 | 61.1572 | 61.2488
1228.1875 | 121.9482 | -61.1481 | 60.4752 | -0.082169 | 0.0061032 | 0.06561 | 0.057544 | -0.0014867 | -0.0083932 | -0.0013051 | -0.028351 | 0.0029607 | 0.062995 | 0.054959 | -0.012174 | 0.027194 | -0.0060071 | 0.032043 | 60.2921 | -61.2076 | 60.5438 | -60.91 | -61.3403 | -61.2946 | 0.17395 | 60.2737 | -61.203 | 60.5026 | -61.0657 | -61.1801 | -61.1526 | -0.05951 | -0.18311 | 0.068664 | 0.23804 | -0.14648 | -0.19226 | -0.086975 | -0.13275 | -0.054932 | -0.20142 | 0.027466 | 0.082397 | -0.004578 | -0.032044 | 0.050354 | 0.022888 | 0.29755 | 121.7514 | 0.13733 | 121.7056 | 121.4996 | 121.4767 | 121.4401 | 121.4218 | -121.6827 | -121.6782 | 121.6919 | 121.6507 | 61.1801 | 61.322
1229.9375 | 121.9345 | -61.2076 | 60.3882 | -0.12794 | 0.0061032 | 0.064969 | 0.060962 | -0.00063233 | -0.010316 | -0.0028005 | -0.0069885 | 0.0042425 | 0.066841 | 0.048123 | -0.013242 | 0.024844 | -0.0034435 | -0.12817 | 60.2554 | -61.2122 | 60.4431 | -61.0062 | -61.4502 | -61.3861 | 0.009155 | 60.228 | -61.2534 | 60.4431 | -61.1755 | -61.2625 | -61.2076 | -0.004577 | -0.13275 | 0.054931 | 0.20142 | -0.17853 | -0.24261 | -0.17395 | -0.23804 | -0.045776 | -0.16022 | 0.054931 | 0.032044 | 0 | -0.054931 | 0.045776 | -0.009155 | 0.20599 | 121.6553 | 0.07782 | 121.6965 | 121.4676 | 121.4813 | 121.463 | 121.4355 | -121.6003 | -121.6415 | 121.6507 | 121.6507 | 61.0794 | 61.2167
1231.6719 | 121.9757 | -61.1481 | 60.4614 | -0.036392 | 0.0050352 | 0.063901 | 0.060534 | -0.0042639 | -0.0083932 | -0.0060049 | -0.0069885 | 0.0040289 | 0.066841 | 0.050686 | -0.011533 | 0.025058 | -0.0062207 | 0.027466 | 60.2783 | -61.1984 | 60.5484 | -60.8551 | -61.3083 | -61.2717 | 0.22888 | 60.2692 | -61.1893 | 60.5209 | -61.0336 | -61.1343 | -61.116 | -0.050354 | -0.18311 | 0.086975 | 0.29297 | -0.1236 | -0.16022 | -0.073242 | -0.10986 | -0.041199 | -0.19226 | 0.059509 | 0.11444 | 0.032043 | 0.013733 | 0.073242 | 0.054932 | 0.34332 | 121.7468 | 0.15564 | 121.7102 | 121.4767 | 121.4584 | 121.4264 | 121.4172 | -121.6599 | -121.6507 | 121.6965 | 121.669 | 61.1755 | 61.377
1233.3438 | 121.843 | -61.1893 | 60.4843 | -0.036392 | 0.0048214 | 0.062192 | 0.063739 | -0.0019141 | -0.01117 | -0.0028005 | -0.034454 | 0.0042425 | 0.067268 | 0.053891 | -0.012815 | 0.025912 | -0.0032299 | -0.045776 | 60.3104 | -61.2442 | 60.4248 | -61.0245 | -61.441 | -61.4136 | 0.059509 | 60.3195 | -61.2305 | 60.4202 | -61.1938 | -61.3037 | -61.2488 | -0.054932 | -0.17395 | -0.059509 | 0.16479 | -0.2243 | -0.25177 | -0.16937 | -0.19684 | -0.041199 | -0.16479 | -0.064087 | -0.004578 | -0.059509 | -0.11444 | -0.01831 | -0.073242 | 0.21973 | 121.669 | 0.036621 | 121.6507 | 121.5546 | 121.55 | 121.4996 | 121.5088 | -121.7285 | -121.7148 | 121.6141 | 121.6095 | 61.1435 | 61.2488
1235.0938 | 121.8567 | -61.2259 | 60.4614 | -0.12794 | 0.0054624 | 0.066892 | 0.061389 | 8.47e-06 | -0.010102 | -0.0030141 | -0.046661 | 0.0050971 | 0.065559 | 0.052823 | -0.014311 | 0.026767 | -0.0062207 | -0.059509 | 60.3241 | -61.2305 | 60.4294 | -61.0291 | -61.4365 | -61.4136 | 0.050354 | 60.3149 | -61.2442 | 60.4019 | -61.2076 | -61.3174 | -61.2671 | -0.004578 | -0.13733 | -0.032044 | 0.19684 | -0.18768 | -0.21057 | -0.1831 | -0.20599 | -0.018311 | -0.14649 | -0.059509 | 0.01831 | -0.041199 | -0.091553 | -0.022888 | -0.073242 | 0.20142 | 121.6599 | 0.036621 | 121.6461 | 121.5546 | 121.5591 | 121.55 | 121.5408 | -121.6919 | -121.7056 | 121.6553 | 121.6278 | 61.1664 | 61.2762
1236.7812 | 121.9025 | -61.2167 | 60.3653 | -0.1432 | 0.0080258 | 0.064756 | 0.06203 | -0.0034095 | -0.010743 | -0.0010915 | -0.031403 | 0.0046697 | 0.067268 | 0.047055 | -0.013029 | 0.02634 | -0.0047253 | -0.12817 | 60.228 | -61.2762 | 60.4477 | -60.9741 | -61.4365 | -61.3724 | 0.022888 | 60.2417 | -61.2762 | 60.434 | -61.1847 | -61.29 | -61.2259 | -0.059509 | -0.13733 | 0.082398 | 0.24262 | -0.15564 | -0.21973 | -0.09613 | -0.16022 | -0.059509 | -0.1236 | 0.068665 | 0.032044 | -0.009155 | -0.073242 | 0.050354 | -0.013733 | 0.30212 | 121.7239 | 0.091553 | 121.7102 | 121.5042 | 121.5179 | 121.4447 | 121.4584 | -121.6415 | -121.6415 | 121.6644 | 121.6507 | 61.0886 | 61.2396
1238.5469 | 121.8567 | -61.2991 | 60.3333 | -0.10506 | 0.0099484 | 0.064969 | 0.065234 | -0.0017005 | -0.010316 | -0.0010915 | -0.1077 | 0.0048833 | 0.064063 | 0.055813 | -0.016233 | 0.027621 | -0.0040845 | -0.1236 | 60.2371 | -61.2991 | 60.3973 | -61.0886 | -61.5326 | -61.4822 | -0.054932 | 60.2417 | -61.3266 | 60.3241 | -61.2808 | -61.4365 | -61.3358 | 0 | -0.09613 | 0.064087 | 0.21057 | -0.18311 | -0.23346 | -0.18311 | -0.23346 | -0.027466 | -0.091553 | -0.009155 | 0.01831 | -0.036621 | -0.13733 | -0.009155 | -0.10986 | 0.21057 | 121.6965 | 0.045776 | 121.6507 | 121.5363 | 121.5683 | 121.5363 | 121.5408 | -121.6324 | -121.6599 | 121.6965 | 121.6232 | 61.1755 | 61.2442
1240.2344 | 121.9482 | -61.2396 | 60.3561 | -0.16609 | 0.0093076 | 0.06561 | 0.062243 | 0.0012903 | -0.0081796 | -0.0042959 | -0.040558 | 0.0036017 | 0.064491 | 0.05325 | -0.014524 | 0.026553 | -0.0062207 | -0.14191 | 60.1868 | -61.2991 | 60.4568 | -60.9833 | -61.4639 | -61.3861 | 0.041199 | 60.1959 | -61.29 | 60.4385 | -61.1801 | -61.2854 | -61.2305 | -0.059509 | -0.16937 | 0.10071 | 0.25635 | -0.14648 | -0.2243 | -0.086975 | -0.1648 | -0.050354 | -0.16022 | 0.082398 | 0.059509 | 0.009155 | -0.045776 | 0.059509 | 0.004578 | 0.31586 | 121.756 | 0.10986 | 121.7285 | 121.4859 | 121.4859 | 121.4264 | 121.4355 | -121.6553 | -121.6461 | 121.6965 | 121.6782 | 61.0977 | 61.2808
1241.9844 | 121.9711 | -61.1618 | 60.4202 | -0.089798 | 0.0024716 | 0.064115 | 0.061602 | -0.0019141 | -0.009675 | -0.0045095 | -0.028351 | 0.0031745 | 0.0662 | 0.045559 | -0.012815 | 0.025272 | -0.0042981 | 0 | 60.2554 | -61.2305 | 60.5621 | -60.8643 | -61.3129 | -61.2579 | 0.21973 | 60.26 | -61.203 | 60.5255 | -61.0336 | -61.1618 | -61.1252 | -0.068665 | -0.16479 | 0.14191 | 0.29755 | -0.096131 | -0.15106 | -0.027466 | -0.082397 | -0.041199 | -0.16022 | 0.10529 | 0.12817 | 0.036621 | 0 | 0.07782 | 0.041199 | 0.36621 | 121.7926 | 0.16937 | 121.7285 | 121.4859 | 121.463 | 121.4172 | 121.4218 | -121.6507 | -121.6232 | 121.7239 | 121.6873 | 61.1618 | 61.3815
1243.7344 | 121.8521 | -61.235 | 60.4797 | -0.028763 | 0.002258 | 0.064969 | 0.060748 | -0.0014867 | -0.010316 | -0.0040823 | -0.049713 | 0.0036017 | 0.065986 | 0.053464 | -0.013456 | 0.025272 | -0.0019483 | -0.036621 | 60.3149 | -61.235 | 60.4294 | -61.0291 | -61.4502 | -61.409 | 0.059509 | 60.3058 | -61.2579 | 60.3973 | -61.1938 | -61.3037 | -61.2579 | 0 | -0.1648 | -0.050354 | 0.20599 | -0.17395 | -0.21515 | -0.17395 | -0.21515 | -0.022889 | -0.17395 | -0.082397 | 0.041198 | -0.022889 | -0.068665 | 0 | -0.045776 | 0.20599 | 121.6644 | 0.064087 | 121.6553 | 121.55 | 121.5637 | 121.55 | 121.5408 | -121.7148 | -121.7377 | 121.6644 | 121.6324 | 61.1984 | 61.2946
1245.4219 | 121.8475 | -61.2808 | 60.3516 | -0.16609 | 0.0058896 | 0.066251 | 0.06438 | 8.47e-06 | -0.0088206 | -0.0051505 | -0.12601 | 0.0023199 | 0.0662 | 0.054532 | -0.01367 | 0.028049 | -0.0045117 | -0.12817 | 60.2417 | -61.2946 | 60.4019 | -61.0703 | -61.5051 | -61.4594 | -0.022888 | 60.2142 | -61.322 | 60.3516 | -61.2854 | -61.409 | -61.3266 | -0.013733 | -0.10986 | 0.050355 | 0.21057 | -0.17853 | -0.2243 | -0.16479 | -0.21057 | -0.041198 | -0.13733 | 0 | -0.004577 | -0.045776 | -0.12817 | -0.004578 | -0.086976 | 0.22431 | 121.6965 | 0.036621 | 121.6736 | 121.5363 | 121.5363 | 121.5225 | 121.4951 | -121.6461 | -121.6736 | 121.6827 | 121.6324 | 61.1526 | 61.2579
1247.1719 | 121.8384 | -61.3083 | 60.3653 | -0.097427 | 0.0069578 | 0.065824 | 0.065661 | 8.47e-06 | -0.0083932 | 0.0012583 | -0.12601 | 0.0063787 | 0.063636 | 0.05325 | -0.012388 | 0.027194 | -0.0075025 | -0.17395 | 60.2417 | -61.3266 | 60.3333 | -61.1481 | -61.5875 | -61.5417 | -0.1236 | 60.2097 | -61.3129 | 60.3012 | -61.3129 | -61.4456 | -61.3495 | -0.01831 | -0.1236 | -0.032043 | 0.16022 | -0.23346 | -0.27923 | -0.21515 | -0.26093 | -0.004577 | -0.15564 | -0.064087 | -0.004577 | -0.041198 | -0.13733 | -0.036621 | -0.13275 | 0.17853 | 121.6599 | 0 | 121.6141 | 121.5683 | 121.5225 | 121.55 | 121.5179 | -121.6919 | -121.6782 | 121.6415 | 121.6095 | 61.1343 | 61.1847
1248.9219 | 121.9345 | -61.235 | 60.3699 | -0.11269 | 0.0093076 | 0.066037 | 0.061389 | 8.47e-06 | -0.0098886 | -0.0032277 | -0.01004 | 0.0029607 | 0.067268 | 0.042569 | -0.015165 | 0.025272 | -0.0057935 | -0.14191 | 60.2417 | -61.2579 | 60.4248 | -61.0062 | -61.4685 | -61.3953 | 0.018311 | 60.2325 | -61.2762 | 60.4248 | -61.1801 | -61.2854 | -61.2122 | -0.022889 | -0.12817 | 0.054932 | 0.22888 | -0.16022 | -0.23346 | -0.13733 | -0.21057 | -0.041199 | -0.13733 | 0.054932 | 0.054931 | 0.022888 | -0.050354 | 0.064087 | -0.009155 | 0.25177 | 121.6827 | 0.09613 | 121.7011 | 121.4996 | 121.5088 | 121.4767 | 121.4676 | -121.6278 | -121.6461 | 121.6599 | 121.6599 | 61.0931 | 61.2534
1250.6719 | 121.8155 | -61.3129 | 60.3561 | -0.097427 | 0.0041806 | 0.067319 | 0.06502 | 8.47e-06 | -0.0066844 | -0.0051505 | -0.1138 | 0.0044561 | 0.065559 | 0.056027 | -0.014524 | 0.024844 | -0.0062207 | -0.21057 | 60.1913 | -61.3266 | 60.3287 | -61.1572 | -61.5829 | -61.5555 | -0.15564 | 60.2234 | -61.3403 | 60.3058 | -61.3266 | -61.4685 | -61.3678 | -0.013733 | -0.1648 | -0.027466 | 0.15564 | -0.24262 | -0.27008 | -0.22888 | -0.25635 | -0.027466 | -0.13275 | -0.050354 | -0.013733 | -0.054932 | -0.15564 | -0.027466 | -0.12817 | 0.16937 | 121.6553 | 0.013733 | 121.6461 | 121.5179 | 121.5637 | 121.5042 | 121.5363 | -121.6827 | -121.6965 | 121.6415 | 121.6187 | 61.1023 | 61.1572
1252.3594 | 121.8887 | -61.2625 | 60.3928 | -0.06691 | 0.003967 | 0.066464 | 0.062884 | 0.0017175 | -0.012025 | -0.0017325 | -0.055817 | 0.0057379 | 0.065559 | 0.051114 | -0.014524 | 0.028049 | -0.0057935 | -0.091553 | 60.2875 | -61.2946 | 60.3973 | -61.0474 | -61.4868 | -61.4456 | 0.027466 | 60.26 | -61.29 | 60.4019 | -61.2076 | -61.3403 | -61.2579 | -0.032044 | -0.10529 | 0.004578 | 0.21515 | -0.18311 | -0.2243 | -0.15106 | -0.19226 | -0.027466 | -0.13275 | 0.009156 | 0.054931 | 0.004577 | -0.07782 | 0.032043 | -0.050354 | 0.24719 | 121.6919 | 0.082397 | 121.6919 | 121.582 | 121.55 | 121.55 | 121.5225 | -121.6873 | -121.6827 | 121.6599 | 121.6644 | 61.171 | 61.29
1254.1094 | 121.8887 | -61.1893 | 60.4477 | -0.12032 | 0.0052488 | 0.064115 | 0.059466 | -0.0025549 | -0.010957 | -0.00066434 | -0.0039367 | 0.0036017 | 0.067481 | 0.050259 | -0.012815 | 0.027408 | -0.0047253 | 0.022888 | 60.2783 | -61.2442 | 60.498 | -60.9283 | -61.3586 | -61.322 | 0.16022 | 60.2737 | -61.2259 | 60.434 | -61.1481 | -61.2579 | -61.2076 | -0.054932 | -0.16937 | 0.050354 | 0.26093 | -0.13275 | -0.16937 | -0.077819 | -0.11444 | -0.036621 | -0.17395 | -0.013733 | 0.041199 | -0.018311 | -0.068665 | 0.01831 | -0.032044 | 0.31586 | 121.7422 | 0.07782 | 121.6599 | 121.5225 | 121.4996 | 121.4676 | 121.463 | -121.6919 | -121.6736 | 121.6873 | 121.6232 | 61.2122 | 61.3495
1255.7969 | 121.8613 | -61.2213 | 60.4385 | -0.097427 | 0.0052488 | 0.061978 | 0.062457 | -0.0019141 | -0.012025 | -0.0023733 | -0.055817 | 0.0059515 | 0.065132 | 0.0509 | -0.01367 | 0.024844 | -0.0062207 | -0.050354 | 60.3104 | -61.2488 | 60.3836 | -61.0794 | -61.4868 | -61.4594 | 0.022888 | 60.2966 | -61.2946 | 60.3699 | -61.2122 | -61.3403 | -61.2808 | -0.027466 | -0.12817 | -0.054932 | 0.14191 | -0.23804 | -0.2655 | -0.21057 | -0.23804 | -0.073243 | -0.14191 | -0.068665 | 0.009155 | -0.05951 | -0.11902 | 0.013733 | -0.045776 | 0.16937 | 121.6324 | 0.082398 | 121.6644 | 121.5591 | 121.5912 | 121.5317 | 121.5179 | -121.6873 | -121.7331 | 121.6049 | 121.5912 | 61.171 | 61.2442
1257.5469 | 121.9711 | -61.2579 | 60.2829 | -0.18135 | 0.0071714 | 0.066678 | 0.06203 | 0.00064947 | -0.0073252 | -0.0021597 | -0.034454 | 0.0042425 | 0.066413 | 0.051968 | -0.01367 | 0.025058 | -0.0034435 | -0.16479 | 60.173 | -61.29 | 60.4294 | -61.0245 | -61.4868 | -61.4273 | -0.013733 | 60.1456 | -61.3266 | 60.4294 | -61.1893 | -61.2991 | -61.2259 | -0.032043 | -0.10986 | 0.14648 | 0.23346 | -0.16937 | -0.22888 | -0.13733 | -0.19684 | -0.068664 | -0.13733 | 0.14648 | 0.068665 | 0.032044 | -0.041198 | 0.10071 | 0.027466 | 0.2655 | 121.7194 | 0.13733 | 121.756 | 121.463 | 121.4722 | 121.431 | 121.4035 | -121.5729 | -121.6095 | 121.6873 | 121.6873 | 61.0931 | 61.2442
1259.2344 | 121.8796 | -61.2808 | 60.3607 | -0.13557 | 0.0063168 | 0.064328 | 0.063525 | -0.00041873 | -0.0094614 | -0.0032277 | -0.086334 | 0.0063787 | 0.065132 | 0.049405 | -0.014311 | 0.027194 | -0.0019483 | -0.12817 | 60.2325 | -61.3312 | 60.3973 | -61.0474 | -61.5051 | -61.4731 | -0.009155 | 60.2417 | -61.3174 | 60.3607 | -61.2671 | -61.3907 | -61.3129 | -0.050354 | -0.12817 | 0.036621 | 0.23346 | -0.19226 | -0.2243 | -0.14191 | -0.17395 | -0.036621 | -0.11902 | 0 | 0.013733 | -0.032043 | -0.10986 | 0.004578 | -0.073242 | 0.28381 | 121.7285 | 0.050354 | 121.6782 | 121.5637 | 121.5591 | 121.5134 | 121.5225 | -121.6919 | -121.6782 | 121.6782 | 121.6415 | 61.1526 | 61.2717
1260.9844 | 121.8933 | -61.2488 | 60.379 | -0.082169 | 0.0067442 | 0.067319 | 0.062457 | -0.0010595 | -0.011384 | -0.0045095 | -0.071076 | 0.0040289 | 0.064277 | 0.054532 | -0.014097 | 0.026767 | -0.0038709 | -0.10529 | 60.228 | -61.3129 | 60.3928 | -61.0428 | -61.5005 | -61.4731 | 0.027466 | 60.2234 | -61.322 | 60.3836 | -61.2259 | -61.3495 | -61.2946 | -0.064087 | -0.15106 | 0.013733 | 0.20599 | -0.2243 | -0.25177 | -0.16022 | -0.18768 | -0.073242 | -0.15564 | 0.004578 | 0.022888 | -0.045777 | -0.10071 | 0.027465 | -0.027466 | 0.27008 | 121.7056 | 0.09613 | 121.7056 | 121.5408 | 121.5454 | 121.4767 | 121.4722 | -121.6919 | -121.701 | 121.6415 | 121.6324 | 61.1435 | 61.2762
1262.7344 | 121.9437 | -61.2534 | 60.3195 | -0.21187 | 0.0052488 | 0.064542 | 0.060534 | -0.0046911 | -0.0088206 | -0.0025869 | -0.025299 | 0.0036017 | 0.067268 | 0.046414 | -0.015165 | 0.026553 | -0.0047253 | -0.15564 | 60.1593 | -61.2946 | 60.4294 | -61.0016 | -61.4731 | -61.409 | 0.027466 | 60.1456 | -61.3358 | 60.4111 | -61.2076 | -61.322 | -61.2488 | -0.041199 | -0.16022 | 0.10986 | 0.25177 | -0.15564 | -0.21973 | -0.11444 | -0.17853 | -0.082397 | -0.17395 | 0.091553 | 0.045776 | 0.004578 | -0.068664 | 0.086975 | 0.013733 | 0.29297 | 121.7239 | 0.12817 | 121.7468 | 121.4539 | 121.4813 | 121.4127 | 121.3989 | -121.6141 | -121.6553 | 121.6827 | 121.6644 | 61.0977 | 61.2808
1264.4219 | 121.8613 | -61.2579 | 60.4019 | -0.089798 | 0.0065304 | 0.064756 | 0.061816 | -0.0017005 | -0.012239 | -0.0023733 | -0.064972 | 0.0033881 | 0.065345 | 0.054959 | -0.014311 | 0.027408 | -0.0034435 | -0.059509 | 60.2921 | -61.2854 | 60.3745 | -61.0886 | -61.496 | -61.4731 | 0.009155 | 60.2554 | -61.3083 | 60.3516 | -61.2488 | -61.3678 | -61.3037 | -0.027465 | -0.10986 | -0.027466 | 0.16937 | -0.21515 | -0.23804 | -0.18768 | -0.21057 | -0.050354 | -0.14648 | -0.050355 | 0.009156 | -0.045776 | -0.10986 | 0.004578 | -0.059509 | 0.19684 | 121.6599 | 0.05951 | 121.6599 | 121.5775 | 121.5637 | 121.55 | 121.5134 | -121.6873 | -121.7102 | 121.6324 | 121.6095 | 61.1984 | 61.2671
1266.1875 | 121.9574 | -61.2076 | 60.3882 | -0.10506 | 0.0041806 | 0.065824 | 0.059253 | -0.0059729 | -0.0098886 | -0.0017325 | 0.011322 | 0.0057379 | 0.064704 | 0.051755 | -0.015165 | 0.023349 | -0.0021619 | 0.027466 | 60.2463 | -61.2305 | 60.5209 | -60.8871 | -61.3403 | -61.3174 | 0.21515 | 60.2509 | -61.235 | 60.4935 | -61.1023 | -61.1984 | -61.1664 | -0.022888 | -0.14191 | 0.13275 | 0.32043 | -0.10986 | -0.13275 | -0.086975 | -0.10986 | -0.027465 | -0.13733 | 0.10528 | 0.10529 | 0.041199 | 0.009156 | 0.068664 | 0.036621 | 0.34332 | 121.7514 | 0.13275 | 121.7285 | 121.4767 | 121.4859 | 121.4539 | 121.4584 | -121.6187 | -121.6232 | 121.7285 | 121.701 | 61.235 | 61.4227
1267.9375 | 121.9574 | -61.1984 | 60.4019 | -0.11269 | 0.0050352 | 0.064115 | 0.060534 | -0.0083227 | -0.0083932 | -0.0019461 | 0.0052185 | 0.0040289 | 0.065772 | 0.056668 | -0.014524 | 0.025912 | -0.0040845 | 0.009155 | 60.2005 | -61.2579 | 60.5209 | -60.9009 | -61.3449 | -61.29 | 0.21973 | 60.2051 | -61.2488 | 60.4889 | -61.0794 | -61.1893 | -61.1618 | -0.05951 | -0.20142 | 0.11902 | 0.29755 | -0.091553 | -0.14648 | -0.032043 | -0.086975 | -0.050354 | -0.19684 | 0.086975 | 0.11902 | 0.036621 | 0.009155 | 0.086975 | 0.059509 | 0.35706 | 121.7789 | 0.16937 | 121.7377 | 121.4584 | 121.4539 | 121.3989 | 121.4035 | -121.6599 | -121.6507 | 121.7194 | 121.6873 | 61.2076 | 61.4182
1269.6875 | 121.8567 | -61.2534 | 60.4477 | -0.044022 | 0.0063168 | 0.063901 | 0.058184 | -0.0036231 | -0.0092478 | -0.0030141 | -0.034454 | 0.0072333 | 0.065345 | 0.055173 | -0.015165 | 0.026981 | -0.0028027 | -0.018311 | 60.26 | -61.2808 | 60.4019 | -61.0474 | -61.4777 | -61.4365 | 0.068665 | 60.2783 | -61.2991 | 60.3653 | -61.2396 | -61.3403 | -61.2946 | -0.027466 | -0.18768 | -0.045776 | 0.20599 | -0.1831 | -0.2243 | -0.15564 | -0.19684 | -0.045776 | -0.16937 | -0.082398 | 0.013733 | -0.041199 | -0.086975 | 0.004577 | -0.041199 | 0.23346 | 121.6827 | 0.059509 | 121.6644 | 121.5408 | 121.5775 | 121.5134 | 121.5317 | -121.7285 | -121.7468 | 121.6553 | 121.6187 | 61.235 | 61.322
1271.375 | 121.9025 | -61.2259 | 60.3516 | -0.12794 | 0.0050352 | 0.064756 | 0.060962 | -0.0044775 | -0.0088206 | -0.0013051 | -0.019196 | 0.0036017 | 0.064704 | 0.049832 | -0.015379 | 0.027408 | -0.0023755 | -0.10529 | 60.2142 | -61.2991 | 60.3882 | -61.0565 | -61.5005 | -61.4273 | 0.027466 | 60.1959 | -61.3129 | 60.3745 | -61.2076 | -61.3312 | -61.2579 | -0.073242 | -0.13733 | 0.036622 | 0.16937 | -0.20142 | -0.27466 | -0.12817 | -0.20142 | -0.086975 | -0.15564 | 0.022889 | 0.01831 | -0.032044 | -0.10529 | 0.054931 | -0.018311 | 0.24261 | 121.6873 | 0.10529 | 121.6873 | 121.5134 | 121.5088 | 121.4401 | 121.4218 | -121.6507 | -121.6644 | 121.6141 | 121.6003 | 61.1206 | 61.2534
1273.125 | 121.9391 | -61.2488 | 60.3745 | -0.082169 | 0.0054624 | 0.064969 | 0.061389 | -0.0053321 | -0.010316 | -0.0030141 | -0.019196 | 0.0050971 | 0.067481 | 0.047268 | -0.012174 | 0.026767 | -0.0015209 | -0.091553 | 60.1822 | -61.2854 | 60.4065 | -61.0519 | -61.496 | -61.4227 | 0.032043 | 60.1959 | -61.3129 | 60.3973 | -61.203 | -61.3174 | -61.2488 | -0.036621 | -0.19226 | 0.032043 | 0.19684 | -0.17395 | -0.24719 | -0.13733 | -0.21057 | -0.064087 | -0.17853 | 0.022888 | 0.045776 | 0 | -0.068665 | 0.064087 | -0.004578 | 0.23346 | 121.6919 | 0.10986 | 121.7102 | 121.4676 | 121.5088 | 121.431 | 121.4447 | -121.6599 | -121.6873 | 121.6553 | 121.6461 | 61.1572 | 61.2808
1274.875 | 121.9116 | -61.2213 | 60.3836 | -0.12794 | 0.0031126 | 0.065183 | 0.05968 | -0.0057593 | -0.010743 | -0.0025869 | -0.013092 | 0.0055243 | 0.062995 | 0.051541 | -0.014524 | 0.025485 | -0.0049389 | 0.036621 | 60.2097 | -61.2671 | 60.4935 | -60.9558 | -61.3907 | -61.3586 | 0.1831 | 60.2371 | -61.2808 | 60.434 | -61.1664 | -61.2762 | -61.2213 | -0.045777 | -0.17395 | 0.10986 | 0.2655 | -0.13733 | -0.16937 | -0.091553 | -0.1236 | -0.05951 | -0.14648 | 0.050354 | 0.054931 | 0 | -0.054932 | 0.05951 | 0.004578 | 0.31128 | 121.7606 | 0.11444 | 121.7148 | 121.4767 | 121.5179 | 121.431 | 121.4584 | -121.6507 | -121.6644 | 121.7148 | 121.6553 | 61.2579 | 61.4044
1276.5625 | 121.962 | -61.2213 | 60.3836 | -0.05928 | 0.0041806 | 0.066464 | 0.060107 | -0.0036231 | -0.01117 | -0.0021597 | -0.04361 | 0.0027471 | 0.063209 | 0.056881 | -0.014311 | 0.026126 | -0.0072889 | 0.050354 | 60.228 | -61.2442 | 60.5072 | -60.9467 | -61.377 | -61.3358 | 0.21057 | 60.2142 | -61.2671 | 60.434 | -61.1435 | -61.2396 | -61.1984 | -0.022889 | -0.15564 | 0.1236 | 0.27466 | -0.11444 | -0.15564 | -0.091552 | -0.13275 | -0.045777 | -0.16937 | 0.050354 | 0.077819 | 0.022888 | -0.018311 | 0.068665 | 0.027466 | 0.29755 | 121.7514 | 0.1236 | 121.7011 | 121.4722 | 121.4813 | 121.4493 | 121.4355 | -121.6278 | -121.6507 | 121.7285 | 121.6553 | 61.2717 | 61.4319
1278.2969 | 121.8979 | -61.29 | 60.3287 | -0.044022 | 0.0065304 | 0.062833 | 0.062243 | -0.00063233 | -0.0098886 | -0.0010915 | -0.092438 | 0.0057379 | 0.065986 | 0.054745 | -0.016447 | 0.026553 | -0.0053661 | -0.07782 | 60.2142 | -61.3358 | 60.3607 | -61.1069 | -61.5417 | -61.5005 | 0.041199 | 60.2188 | -61.3449 | 60.3516 | -61.2671 | -61.3998 | -61.3174 | -0.045776 | -0.11444 | 0.032044 | 0.1831 | -0.21057 | -0.25177 | -0.16479 | -0.20599 | -0.054932 | -0.10986 | 0.022888 | 0.022888 | -0.027466 | -0.10986 | 0.027466 | -0.054931 | 0.22888 | 121.6965 | 0.07782 | 121.6965 | 121.55 | 121.5637 | 121.5042 | 121.5088 | -121.6644 | -121.6736 | 121.6507 | 121.6415 | 61.2122 | 61.3312
1280.0469 | 121.907 | -61.3174 | 60.3241 | -0.097427 | 0.0052488 | 0.06326 | 0.062243 | -0.0010595 | -0.006898 | -0.00066434 | -0.10464 | 0.0046697 | 0.065345 | 0.058377 | -0.014524 | 0.02634 | -0.0034435 | -0.073242 | 60.2142 | -61.3312 | 60.3561 | -61.1023 | -61.5372 | -61.5005 | 0.018311 | 60.1959 | -61.3815 | 60.3424 | -61.2579 | -61.3998 | -61.3266 | -0.013733 | -0.10986 | 0.032043 | 0.21515 | -0.1831 | -0.21973 | -0.16937 | -0.20599 | -0.064087 | -0.12817 | 0.01831 | 0.059509 | -0.009155 | -0.082397 | 0.054932 | -0.01831 | 0.22888 | 121.6873 | 0.1236 | 121.7239 | 121.5454 | 121.5775 | 121.5317 | 121.5134 | -121.6553 | -121.7056 | 121.6736 | 121.6599 | 61.2442 | 61.3358
1281.7969 | 121.9803 | -61.2305 | 60.3333 | -0.11269 | 0.0054624 | 0.063687 | 0.060534 | 8.47e-06 | -0.0090342 | -0.0017325 | -0.016144 | 0.0044561 | 0.065986 | 0.053036 | -0.012602 | 0.023135 | -0.0032299 | 0 | 60.1959 | -61.2808 | 60.4568 | -60.9512 | -61.409 | -61.3632 | 0.19684 | 60.2005 | -61.2808 | 60.4568 | -61.1389 | -61.2396 | -61.203 | -0.050354 | -0.13733 | 0.1236 | 0.27924 | -0.13275 | -0.17853 | -0.082397 | -0.12817 | -0.050354 | -0.13275 | 0.1236 | 0.091553 | 0.027466 | -0.009155 | 0.07782 | 0.041199 | 0.32959 | 121.7377 | 0.14191 | 121.7377 | 121.4767 | 121.4813 | 121.4264 | 121.431 | -121.6141 | -121.6141 | 121.6873 | 121.6873 | 61.2305 | 61.4273
1283.5625 | 121.8796 | -61.3678 | 60.2783 | -0.13557 | 0.0065304 | 0.064969 | 0.06438 | -0.0038367 | -0.01117 | -0.0019461 | -0.10464 | 0.0065923 | 0.067054 | 0.060513 | -0.014951 | 0.025485 | -0.0025891 | -0.25177 | 60.1501 | -61.3861 | 60.2509 | -61.203 | -61.6516 | -61.5921 | -0.13733 | 60.1318 | -61.409 | 60.26 | -61.3541 | -61.4822 | -61.3953 | -0.01831 | -0.12817 | -0.027466 | 0.16479 | -0.2243 | -0.28381 | -0.20599 | -0.2655 | -0.041199 | -0.14648 | -0.01831 | 0.013733 | -0.027466 | -0.11444 | 0.013733 | -0.073242 | 0.1831 | 121.637 | 0.054932 | 121.669 | 121.5363 | 121.5408 | 121.5179 | 121.4996 | -121.6644 | -121.6873 | 121.6187 | 121.6278 | 61.116 | 61.2305
1285.25 | 121.9803 | -61.2946 | 60.2509 | -0.12794 | 0.0058896 | 0.066464 | 0.061602 | -0.0036231 | -0.0075388 | 0.00019006 | -0.040558 | 0.0033881 | 0.065559 | 0.045773 | -0.012815 | 0.026126 | -0.0045117 | -0.17395 | 60.0952 | -61.3724 | 60.3745 | -61.0565 | -61.528 | -61.4594 | 0.022888 | 60.0952 | -61.3632 | 60.3745 | -61.2305 | -61.3403 | -61.2808 | -0.077819 | -0.15564 | 0.1236 | 0.23804 | -0.16479 | -0.23346 | -0.086976 | -0.15564 | -0.068664 | -0.15564 | 0.1236 | 0.064087 | 0.013733 | -0.045776 | 0.082397 | 0.022888 | 0.31586 | 121.7468 | 0.13275 | 121.7377 | 121.4676 | 121.4584 | 121.3898 | 121.3898 | -121.6232 | -121.6141 | 121.669 | 121.669 | 61.1206 | 61.3174
1287 | 121.8658 | -61.2946 | 60.3836 | -0.12794 | 0.0052488 | 0.064542 | 0.061602 | -0.0042639 | -0.008607 | -0.0010915 | -0.058869 | 0.0048833 | 0.06385 | 0.053464 | -0.013883 | 0.026553 | -0.0083569 | 0.009155 | 60.2097 | -61.2808 | 60.4065 | -61.0291 | -61.4639 | -61.4456 | 0.10529 | 60.2234 | -61.2946 | 60.3333 | -61.2717 | -61.377 | -61.3449 | 0.013733 | -0.17395 | 0.022888 | 0.2655 | -0.15106 | -0.16937 | -0.1648 | -0.18311 | 0 | -0.16022 | -0.050354 | 0.022889 | -0.050354 | -0.082397 | -0.050354 | -0.082397 | 0.25177 | 121.6873 | 0.022889 | 121.6278 | 121.4905 | 121.5179 | 121.5042 | 121.5179 | -121.6644 | -121.6782 | 121.7011 | 121.6278 | 61.3037 | 61.3998
1288.6719 | 121.9254 | -61.29 | 60.3149 | -0.1432 | 0.0052488 | 0.066464 | 0.062457 | -0.0087499 | -0.0088206 | -0.00087794 | -0.019196 | 0.0046697 | 0.064918 | 0.050259 | -0.014311 | 0.026126 | -0.0057935 | -0.10529 | 60.173 | -61.3312 | 60.3607 | -61.084 | -61.5234 | -61.4594 | 0.027466 | 60.1685 | -61.3586 | 60.3745 | -61.2396 | -61.3449 | -61.2808 | -0.041199 | -0.14191 | 0.045777 | 0.20599 | -0.16937 | -0.23346 | -0.12817 | -0.19226 | -0.068665 | -0.14648 | 0.05951 | 0.050354 | 0.009155 | -0.054932 | 0.07782 | 0.013733 | 0.24719 | 121.6919 | 0.11902 | 121.7331 | 121.5042 | 121.5271 | 121.463 | 121.4584 | -121.6461 | -121.6736 | 121.6507 | 121.6644 | 61.1847 | 61.3174
1290.4219 | 121.875 | -61.29 | 60.3653 | -0.051651 | 0.0050352 | 0.064115 | 0.064166 | -0.0014867 | -0.0094614 | -0.0057913 | -0.080231 | 0.0055243 | 0.0662 | 0.056668 | -0.014097 | 0.026126 | -0.0023755 | -0.068665 | 60.2463 | -61.3358 | 60.3149 | -61.1343 | -61.5509 | -61.5097 | 0.013733 | 60.2005 | -61.3266 | 60.3058 | -61.29 | -61.4227 | -61.3403 | -0.045776 | -0.11902 | -0.050354 | 0.15564 | -0.21973 | -0.26093 | -0.17395 | -0.21515 | -0.036621 | -0.1648 | -0.059509 | 0 | -0.050354 | -0.13275 | -0.013733 | -0.09613 | 0.20142 | 121.6507 | 0.036621 | 121.6324 | 121.582 | 121.5271 | 121.5363 | 121.4905 | -121.701 | -121.6919 | 121.6049 | 121.5958 | 61.2213 | 61.3037
1292.1094 | 121.8887 | -61.2579 | 60.3607 | -0.089798 | 0.0067442 | 0.064115 | 0.061175 | -0.0040503 | -0.0088206 | -0.0015189 | -0.031403 | 0.0040289 | 0.0662 | 0.050686 | -0.013029 | 0.02634 | -0.0077161 | 0.013733 | 60.1913 | -61.29 | 60.4248 | -60.997 | -61.4319 | -61.3815 | 0.15106 | 60.2188 | -61.3312 | 60.3745 | -61.2167 | -61.3358 | -61.29 | -0.032043 | -0.16937 | 0.064087 | 0.26093 | -0.1236 | -0.17395 | -0.091553 | -0.14191 | -0.073242 | -0.14191 | 0.013733 | 0.041199 | -0.032043 | -0.077819 | 0.041199 | -0.004577 | 0.29297 | 121.7148 | 0.11444 | 121.7056 | 121.4813 | 121.55 | 121.4493 | 121.4767 | -121.6507 | -121.6919 | 121.6827 | 121.6324 | 61.2717 | 61.409
1293.8594 | 121.9803 | -61.2717 | 60.3195 | -0.10506 | 0.0054624 | 0.064115 | 0.061175 | -0.0049047 | -0.010743 | -0.0040823 | -0.0039367 | 0.0031745 | 0.066627 | 0.046841 | -0.014951 | 0.027408 | -0.0057935 | 0.009155 | 60.1822 | -61.3037 | 60.4614 | -60.9467 | -61.4044 | -61.3586 | 0.2243 | 60.1776 | -61.3083 | 60.4523 | -61.1343 | -61.2442 | -61.2167 | -0.032044 | -0.13733 | 0.14191 | 0.32501 | -0.086976 | -0.13275 | -0.054932 | -0.10071 | -0.036622 | -0.14191 | 0.13275 | 0.13733 | 0.054931 | 0.027465 | 0.091553 | 0.064087 | 0.35706 | 121.7651 | 0.17395 | 121.7606 | 121.4859 | 121.4859 | 121.4539 | 121.4493 | -121.6232 | -121.6278 | 121.7331 | 121.7239 | 61.2808 | 61.496
1295.6094 | 121.9894 | -61.2213 | 60.3561 | -0.097427 | 0.0046078 | 0.065396 | 0.05968 | -0.0027685 | -0.0094614 | -0.0053641 | -0.0039367 | 0.0023199 | 0.066627 | 0.054532 | -0.015379 | 0.025485 | -0.0070751 | 0.013733 | 60.1501 | -61.3037 | 60.4706 | -60.9375 | -61.3998 | -61.3495 | 0.20599 | 60.1868 | -61.2991 | 60.4477 | -61.1298 | -61.2442 | -61.1984 | -0.082398 | -0.20599 | 0.11444 | 0.28381 | -0.12817 | -0.17853 | -0.045776 | -0.09613 | -0.07782 | -0.16937 | 0.091553 | 0.091552 | 0.022888 | -0.022889 | 0.10071 | 0.054931 | 0.36621 | 121.7743 | 0.16937 | 121.7468 | 121.4539 | 121.4859 | 121.3715 | 121.4081 | -121.6599 | -121.6553 | 121.6919 | 121.669 | 61.235 | 61.4273
1297.2812 | 121.8658 | -61.409 | 60.2463 | -0.12794 | 0.005676 | 0.066037 | 0.065448 | -0.0017005 | -0.0088206 | -0.0047231 | -0.13211 | 0.0050971 | 0.063636 | 0.056027 | -0.014524 | 0.027621 | -0.0047253 | -0.25177 | 60.1501 | -61.3953 | 60.1959 | -61.2854 | -61.7065 | -61.6333 | -0.17853 | 60.1089 | -61.4731 | 60.2188 | -61.4227 | -61.5417 | -61.4456 | 0.013733 | -0.096131 | -0.050354 | 0.1236 | -0.2243 | -0.29755 | -0.23804 | -0.31128 | -0.064086 | -0.13733 | -0.027466 | -0.013732 | -0.036621 | -0.13275 | 0.027465 | -0.068665 | 0.10986 | 121.5912 | 0.050354 | 121.6919 | 121.5454 | 121.582 | 121.5591 | 121.5179 | -121.6415 | -121.7194 | 121.6049 | 121.6278 | 61.1572 | 61.2305
1299.0469 | 121.9574 | -61.3449 | 60.2051 | -0.13557 | 0.0071714 | 0.063687 | 0.062243 | -0.0019141 | -0.0066844 | 0.00083106 | -0.074127 | 0.0042425 | 0.063636 | 0.049191 | -0.013883 | 0.028262 | -0.0057935 | -0.20599 | 60.1135 | -61.3953 | 60.347 | -61.1114 | -61.5692 | -61.5234 | -0.013733 | 60.0769 | -61.4182 | 60.3378 | -61.29 | -61.4182 | -61.3129 | -0.050354 | -0.091553 | 0.14191 | 0.23346 | -0.17853 | -0.2243 | -0.12817 | -0.17395 | -0.073242 | -0.12817 | 0.13275 | 0.054932 | 0.032044 | -0.073242 | 0.10529 | 0 | 0.28381 | 121.7422 | 0.12817 | 121.756 | 121.5088 | 121.4951 | 121.4584 | 121.4218 | -121.6003 | -121.6232 | 121.6919 | 121.6827 | 61.1389 | 61.3312
1300.8125 | 121.8292 | -61.3953 | 60.2966 | -0.12032 | 0.0071714 | 0.065824 | 0.065234 | -0.0023413 | -0.0088206 | -0.0038687 | -0.1199 | 0.0059515 | 0.067268 | 0.056668 | -0.01367 | 0.026553 | -0.0036573 | -0.17395 | 60.1593 | -61.4227 | 60.2371 | -61.2305 | -61.6837 | -61.6425 | -0.10986 | 60.0906 | -61.4548 | 60.2234 | -61.4182 | -61.5417 | -61.4365 | -0.027465 | -0.13733 | -0.059509 | 0.16479 | -0.24719 | -0.28839 | -0.21973 | -0.26093 | -0.059509 | -0.20599 | -0.073242 | -0.022888 | -0.041198 | -0.14648 | 0.018311 | -0.086975 | 0.19226 | 121.6599 | 0.036621 | 121.6782 | 121.582 | 121.5454 | 121.5546 | 121.4859 | -121.7194 | -121.7514 | 121.6324 | 121.6187 | 61.2213 | 61.2854
1302.5625 | 121.875 | -61.3541 | 60.2783 | -0.11269 | 0.005676 | 0.065183 | 0.064593 | 0.0029993 | -0.0081796 | -0.0042959 | -0.10159 | 0.0033881 | 0.066627 | 0.049405 | -0.012815 | 0.026767 | -0.0092115 | -0.13275 | 60.1547 | -61.4227 | 60.3058 | -61.1481 | -61.6058 | -61.5555 | 0.013733 | 60.141 | -61.4182 | 60.2692 | -61.3358 | -61.4731 | -61.3861 | -0.068664 | -0.1236 | 0.027466 | 0.20599 | -0.20142 | -0.25177 | -0.13275 | -0.18311 | -0.064087 | -0.13733 | -0.009155 | 0.018311 | -0.032043 | -0.11902 | 0.032044 | -0.054931 | 0.27466 | 121.7285 | 0.082398 | 121.6873 | 121.5775 | 121.5591 | 121.5088 | 121.4951 | -121.701 | -121.6965 | 121.6599 | 121.6232 | 61.2213 | 61.3678
1304.25 | 121.9666 | -61.2625 | 60.3241 | -0.089798 | 0.0048214 | 0.064115 | 0.059466 | -0.0070409 | -0.009675 | -0.0034415 | 0.020477 | 0.0046697 | 0.065345 | 0.041928 | -0.013456 | 0.026767 | -0.0049389 | 0.004578 | 60.1639 | -61.3266 | 60.4523 | -60.9695 | -61.409 | -61.3815 | 0.21973 | 60.173 | -61.322 | 60.4156 | -61.1572 | -61.2717 | -61.2396 | -0.064087 | -0.16022 | 0.12817 | 0.29297 | -0.11902 | -0.14648 | -0.054932 | -0.082398 | -0.059509 | -0.15106 | 0.091552 | 0.10529 | 0.022888 | -0.009155 | 0.082397 | 0.050354 | 0.35706 | 121.7789 | 0.16479 | 121.7377 | 121.4905 | 121.4951 | 121.4264 | 121.4355 | -121.6507 | -121.6461 | 121.7148 | 121.6782 | 61.2671 | 61.4822
1306 | 121.9254 | -61.3632 | 60.2325 | -0.12794 | 0.0069578 | 0.06561 | 0.063739 | 0.0057763 | -0.010743 | -0.0025869 | -0.086334 | 0.0046697 | 0.06385 | 0.047696 | -0.013883 | 0.02634 | -0.0030163 | -0.24261 | 60.1456 | -61.4319 | 60.2325 | -61.2305 | -61.6837 | -61.6241 | -0.11902 | 60.0769 | -61.4365 | 60.26 | -61.3724 | -61.496 | -61.3953 | -0.068665 | -0.086975 | 0 | 0.13275 | -0.26093 | -0.32044 | -0.19226 | -0.25177 | -0.073242 | -0.15564 | 0.027466 | -0.009155 | -0.032044 | -0.13275 | 0.041198 | -0.05951 | 0.20142 | 121.6644 | 0.064087 | 121.6965 | 121.5775 | 121.5134 | 121.5088 | 121.4401 | -121.6644 | -121.669 | 121.5958 | 121.6232 | 61.1206 | 61.2442
1307.75 | 121.9803 | -61.2717 | 60.3104 | -0.10506 | 0.0046078 | 0.06326 | 0.058398 | -0.0057593 | -0.010102 | -0.0028005 | 0.0082703 | 0.0027471 | 0.067695 | 0.0462 | -0.015806 | 0.024844 | -0.0030163 | -0.064087 | 60.141 | -61.3495 | 60.3928 | -61.0428 | -61.4685 | -61.4044 | 0.14191 | 60.1456 | -61.3266 | 60.4156 | -61.1664 | -61.2808 | -61.2259 | -0.07782 | -0.16937 | 0.082397 | 0.22888 | -0.13275 | -0.19684 | -0.054932 | -0.11902 | -0.054932 | -0.16479 | 0.10529 | 0.10529 | 0.045776 | -0.009156 | 0.10071 | 0.045776 | 0.3067 | 121.7422 | 0.16022 | 121.7422 | 121.4905 | 121.4722 | 121.4127 | 121.4172 | -121.6599 | -121.637 | 121.6644 | 121.6873 | 61.2076 | 61.4136
1309.5 | 121.9482 | -61.3861 | 60.2097 | -0.1432 | 0.0069578 | 0.064542 | 0.062243 | 0.0012903 | -0.0075388 | -0.0051505 | -0.089386 | 0.0033881 | 0.064063 | 0.051114 | -0.015592 | 0.026981 | -0.0051525 | -0.26093 | 60.0952 | -61.4319 | 60.26 | -61.2167 | -61.6699 | -61.5967 | -0.07782 | 60.0632 | -61.4273 | 60.3012 | -61.3266 | -61.4548 | -61.3495 | -0.045777 | -0.11444 | 0.050354 | 0.16937 | -0.21057 | -0.28381 | -0.16479 | -0.23804 | -0.041199 | -0.14649 | 0.091552 | 0.059509 | 0.036621 | -0.068665 | 0.07782 | -0.027466 | 0.21515 | 121.6919 | 0.10071 | 121.7285 | 121.5271 | 121.4905 | 121.4813 | 121.4493 | -121.6415 | -121.637 | 121.6461 | 121.6873 | 61.1252 | 61.3083
1311.1875 | 121.9711 | -61.3678 | 60.2509 | -0.1432 | 0.0080258 | 0.065396 | 0.060962 | -0.0034095 | -0.010316 | -0.0025869 | -0.058869 | 0.0040289 | 0.067695 | 0.057095 | -0.014738 | 0.027408 | -0.0062207 | -0.1831 | 60.0632 | -61.3998 | 60.3195 | -61.1114 | -61.5829 | -61.5234 | -0.004578 | 60.054 | -61.4136 | 60.3195 | -61.2808 | -61.4044 | -61.322 | -0.032043 | -0.18768 | 0.068665 | 0.25635 | -0.15564 | -0.21515 | -0.1236 | -0.18311 | -0.045776 | -0.19684 | 0.068665 | 0.086975 | 0.045777 | -0.036621 | 0.091553 | 0.009155 | 0.28839 | 121.7194 | 0.13275 | 121.7331 | 121.463 | 121.4676 | 121.431 | 121.4218 | -121.6507 | -121.6644 | 121.6873 | 121.6873 | 61.1847 | 61.3632
1312.9375 | 121.9254 | -61.2808 | 60.3378 | -0.12032 | 0.0033262 | 0.064328 | 0.062243 | -0.0017005 | -0.008607 | -0.0040823 | -0.0008851 | 0.0048833 | 0.064704 | 0.054959 | -0.013242 | 0.024417 | -0.0030163 | -0.022888 | 60.1456 | -61.3266 | 60.4111 | -61.0291 | -61.4777 | -61.4227 | 0.16937 | 60.173 | -61.3358 | 60.3882 | -61.1984 | -61.3083 | -61.2625 | -0.045776 | -0.19226 | 0.073242 | 0.25177 | -0.14191 | -0.19684 | -0.09613 | -0.15106 | -0.054931 | -0.16479 | 0.050354 | 0.082398 | 0.018311 | -0.027466 | 0.073242 | 0.027465 | 0.29755 | 121.7377 | 0.13733 | 121.7239 | 121.4722 | 121.5088 | 121.4264 | 121.4539 | -121.6644 | -121.6736 | 121.6919 | 121.669 | 61.2579 | 61.4502
1314.625 | 121.907 | -61.3358 | 60.2829 | -0.15083 | 0.0075986 | 0.065183 | 0.062671 | -0.0017005 | -0.012025 | -0.0045095 | -0.022247 | 0.0065923 | 0.064704 | 0.051968 | -0.014097 | 0.023563 | -0.0045117 | -0.16022 | 60.1273 | -61.3586 | 60.3241 | -61.1069 | -61.5463 | -61.496 | 0.013733 | 60.1227 | -61.377 | 60.3195 | -61.2808 | -61.3953 | -61.3129 | -0.022889 | -0.15564 | 0.041199 | 0.22888 | -0.16022 | -0.21057 | -0.13733 | -0.18768 | -0.041199 | -0.16022 | 0.036621 | 0.054931 | 0.022888 | -0.05951 | 0.064087 | -0.018311 | 0.25177 | 121.6827 | 0.09613 | 121.6965 | 121.4859 | 121.4996 | 121.463 | 121.4584 | -121.6415 | -121.6599 | 121.6599 | 121.6553 | 61.1755 | 61.3495
1316.375 | 121.962 | -61.2854 | 60.3058 | -0.10506 | 0.0043942 | 0.066464 | 0.060534 | -0.0055457 | -0.0081796 | -0.0030141 | -0.0008851 | 0.0036017 | 0.065132 | 0.048123 | -0.015379 | 0.024631 | -0.0066479 | -0.11444 | 60.141 | -61.3495 | 60.379 | -61.0428 | -61.4777 | -61.4273 | 0.14648 | 60.1501 | -61.3449 | 60.4019 | -61.171 | -61.2808 | -61.2534 | -0.064087 | -0.16479 | 0.073242 | 0.24261 | -0.14191 | -0.19226 | -0.07782 | -0.12817 | -0.05951 | -0.15564 | 0.096131 | 0.11444 | 0.032043 | 0.004577 | 0.091553 | 0.064087 | 0.3067 | 121.7285 | 0.17395 | 121.7468 | 121.4905 | 121.4951 | 121.4264 | 121.4355 | -121.6553 | -121.6507 | 121.6644 | 121.6873 | 61.171 | 61.4319
1318.125 | 121.9666 | -61.3495 | 60.228 | -0.15083 | 0.0065304 | 0.066464 | 0.061602 | 0.0012903 | -0.010957 | -0.0049367 | -0.071076 | 0.0021063 | 0.065772 | 0.051968 | -0.015806 | 0.026553 | -0.0077161 | -0.21973 | 60.0632 | -61.4136 | 60.3287 | -61.1023 | -61.5829 | -61.5234 | 0.018311 | 60.0494 | -61.409 | 60.3378 | -61.2808 | -61.3861 | -61.3129 | -0.064087 | -0.1648 | 0.10071 | 0.24719 | -0.17395 | -0.23346 | -0.10986 | -0.16937 | -0.05951 | -0.17853 | 0.10986 | 0.068664 | 0.036621 | -0.036621 | 0.096131 | 0.022889 | 0.31128 | 121.7422 | 0.12817 | 121.7468 | 121.4767 | 121.4584 | 121.4127 | 121.3989 | -121.6415 | -121.637 | 121.6782 | 121.6873 | 61.1298 | 61.3678
1319.8594 | 121.9803 | -61.2854 | 60.3012 | -0.12794 | 0.0046078 | 0.06326 | 0.061175 | -0.0044775 | -0.010316 | -0.0040823 | -0.016144 | 0.0055243 | 0.0662 | 0.042996 | -0.013242 | 0.028262 | -0.0055799 | -0.022888 | 60.1456 | -61.3266 | 60.4385 | -60.9787 | -61.4182 | -61.3998 | 0.23346 | 60.1685 | -61.3037 | 60.3973 | -61.1618 | -61.2808 | -61.2442 | -0.041199 | -0.15564 | 0.13733 | 0.3067 | -0.11444 | -0.13275 | -0.073242 | -0.091553 | -0.018311 | -0.13275 | 0.096131 | 0.1236 | 0.041198 | 0.004577 | 0.059509 | 0.022888 | 0.3479 | 121.7651 | 0.14191 | 121.7011 | 121.4722 | 121.4722 | 121.431 | 121.4539 | -121.6278 | -121.6049 | 121.7239 | 121.6827 | 61.2625 | 61.5189
1321.5469 | 121.8658 | -61.3083 | 60.3607 | -0.097427 | 0.0063168 | 0.064115 | 0.060321 | -0.0021277 | -0.008607 | -0.00045074 | -0.040558 | 0.0042425 | 0.064277 | 0.056027 | -0.013883 | 0.025699 | -0.0045117 | -0.073242 | 60.1868 | -61.3449 | 60.3424 | -61.1069 | -61.5555 | -61.4914 | 0.082397 | 60.2234 | -61.3586 | 60.3012 | -61.29 | -61.4227 | -61.3586 | -0.036621 | -0.17395 | -0.018311 | 0.20142 | -0.1831 | -0.24719 | -0.14648 | -0.21057 | -0.050354 | -0.13733 | -0.05951 | 0.018311 | -0.050354 | -0.11444 | 0 | -0.064086 | 0.23804 | 121.6873 | 0.068665 | 121.6599 | 121.5317 | 121.582 | 121.4951 | 121.5317 | -121.7056 | -121.7194 | 121.6507 | 121.6095 | 61.235 | 61.3907
1323.2969 | 122.0078 | -61.2762 | 60.3058 | -0.097427 | 0.0043942 | 0.064969 | 0.061389 | 0.00086307 | -0.010316 | -0.0047231 | -0.040558 | 0.0044561 | 0.065772 | 0.048977 | -0.012602 | 0.02869 | -0.0072889 | -0.10529 | 60.173 | -61.3312 | 60.434 | -60.9879 | -61.4456 | -61.3953 | 0.20142 | 60.1593 | -61.3312 | 60.4248 | -61.1343 | -61.2442 | -61.2213 | -0.054932 | -0.13275 | 0.12817 | 0.28839 | -0.11902 | -0.16937 | -0.064087 | -0.11444 | -0.054932 | -0.14648 | 0.11902 | 0.14191 | 0.054932 | 0.032043 | 0.10986 | 0.086975 | 0.34332 | 121.7651 | 0.19684 | 121.756 | 121.5042 | 121.4905 | 121.4493 | 121.4355 | -121.637 | -121.637 | 121.7102 | 121.7011 | 61.171 | 61.4777
1325.0312 | 121.8933 | -61.3586 | 60.2646 | -0.05928 | 0.0048214 | 0.064969 | 0.06502 | -0.0027685 | -0.0094614 | -0.0015189 | -0.1199 | 0.0059515 | 0.065132 | 0.057522 | -0.015592 | 0.026981 | -0.0040845 | -0.21515 | 60.1501 | -61.3815 | 60.3149 | -61.1343 | -61.5829 | -61.5463 | 0.018311 | 60.1547 | -61.3998 | 60.3058 | -61.3083 | -61.4502 | -61.3632 | -0.022888 | -0.11444 | 0.050354 | 0.22431 | -0.18768 | -0.2243 | -0.16479 | -0.20142 | -0.041198 | -0.10986 | 0.041199 | 0.050354 | -0.004577 | -0.091552 | 0.036621 | -0.050354 | 0.24719 | 121.6965 | 0.091552 | 121.7056 | 121.5317 | 121.5546 | 121.5088 | 121.5134 | -121.6461 | -121.6644 | 121.6736 | 121.6644 | 61.1435 | 61.377
1326.7812 | 121.9528 | -61.2946 | 60.3149 | -0.082169 | 0.0041806 | 0.06326 | 0.060962 | 0.0021447 | -0.0077524 | -2.3544e-05 | -0.028351 | 0.0050971 | 0.067268 | 0.049405 | -0.015379 | 0.025058 | -0.0025891 | -0.10986 | 60.1501 | -61.29 | 60.4523 | -60.9879 | -61.441 | -61.3861 | 0.19226 | 60.1547 | -61.3083 | 60.4111 | -61.1801 | -61.29 | -61.2534 | 0.004578 | -0.16479 | 0.13733 | 0.3067 | -0.091552 | -0.14648 | -0.09613 | -0.15106 | -0.013733 | -0.16022 | 0.096131 | 0.11444 | 0.041199 | 0.004578 | 0.054932 | 0.018311 | 0.30212 | 121.7422 | 0.12817 | 121.7194 | 121.4401 | 121.463 | 121.4447 | 121.4493 | -121.6049 | -121.6232 | 121.7468 | 121.7056 | 61.1847 | 61.4868
1328.5469 | 121.8842 | -61.3861 | 60.2921 | -0.10506 | 0.0058896 | 0.066251 | 0.06438 | -0.0012731 | -0.0092478 | -0.0038687 | -0.1077 | 0.0036017 | 0.066413 | 0.048123 | -0.015165 | 0.026767 | -0.0047253 | -0.27924 | 60.1593 | -61.3907 | 60.3104 | -61.1343 | -61.5921 | -61.5509 | -0.004578 | 60.1227 | -61.4136 | 60.2921 | -61.3449 | -61.4685 | -61.3861 | -0.004578 | -0.13275 | 0.018311 | 0.25177 | -0.16479 | -0.20599 | -0.16022 | -0.20142 | -0.027466 | -0.16937 | 0 | 0.041198 | 0 | -0.082398 | 0.027466 | -0.054932 | 0.25635 | 121.7011 | 0.068664 | 121.7056 | 121.55 | 121.5363 | 121.5454 | 121.5088 | -121.6827 | -121.7056 | 121.6965 | 121.6782 | 61.1069 | 61.3815
1330.2344 | 121.9391 | -61.29 | 60.2783 | -0.1432 | 0.0046078 | 0.066464 | 0.060748 | -0.0025549 | -0.0090342 | -0.0034415 | -0.052765 | 0.0042425 | 0.065345 | 0.055813 | -0.013242 | 0.025912 | -0.0036573 | -0.32959 | 60.1181 | -61.3724 | 60.3424 | -61.1114 | -61.5463 | -61.4822 | 0 | 60.1456 | -61.3678 | 60.3241 | -61.2625 | -61.3907 | -61.322 | -0.082397 | -0.16022 | 0.064087 | 0.17853 | -0.19226 | -0.25635 | -0.10986 | -0.17395 | -0.07782 | -0.13275 | 0.045777 | 0.027466 | -0.032043 | -0.10071 | 0.045777 | -0.022888 | 0.26093 | 121.7148 | 0.10529 | 121.6919 | 121.4905 | 121.5134 | 121.4081 | 121.4355 | -121.6507 | -121.6461 | 121.6324 | 121.6141 | 60.9604 | 61.29
1331.9844 | 121.8338 | -61.3815 | 60.26 | -0.089798 | 0.0069578 | 0.065824 | 0.063952 | -0.0014867 | -0.0083932 | -0.0021597 | -0.12601 | 0.0065923 | 0.062995 | 0.052182 | -0.012388 | 0.027194 | -0.0032299 | -0.44861 | 60.1318 | -61.4319 | 60.228 | -61.2488 | -61.6882 | -61.6425 | -0.15106 | 60.1318 | -61.4227 | 60.2188 | -61.4182 | -61.5646 | -61.4548 | -0.050354 | -0.12817 | -0.032044 | 0.13275 | -0.26093 | -0.3067 | -0.21057 | -0.25635 | -0.041198 | -0.12817 | -0.041199 | -0.036621 | -0.073242 | -0.1831 | -0.032044 | -0.14191 | 0.18311 | 121.6599 | 0.004577 | 121.6415 | 121.5637 | 121.5546 | 121.5134 | 121.5134 | -121.6919 | -121.6827 | 121.6095 | 121.6003 | 60.9329 | 61.2305
1333.6719 | 121.875 | -61.3174 | 60.347 | -0.11269 | 0.0048214 | 0.066251 | 0.057971 | -0.00020513 | -0.010102 | -0.0036551 | -0.034454 | 0.0044561 | 0.065345 | 0.049618 | -0.013029 | 0.025485 | -0.0075025 | -0.25177 | 60.2005 | -61.3083 | 60.3745 | -61.0703 | -61.5051 | -61.4639 | 0.091553 | 60.1959 | -61.3266 | 60.3104 | -61.2808 | -61.3953 | -61.3495 | 0.009155 | -0.14648 | 0.027466 | 0.24719 | -0.14648 | -0.18768 | -0.15564 | -0.19684 | -0.009155 | -0.15106 | -0.036621 | 0.036621 | -0.032043 | -0.07782 | -0.022888 | -0.068665 | 0.23804 | 121.6827 | 0.045776 | 121.637 | 121.5088 | 121.5225 | 121.5179 | 121.5134 | -121.6553 | -121.6736 | 121.6919 | 121.6278 | 61.0657 | 61.409
1335.4219 | 121.843 | -61.3129 | 60.3653 | -0.082169 | 0.0050352 | 0.063474 | 0.059253 | -0.0036231 | -0.0094614 | -0.0036551 | -0.034454 | 0.0018927 | 0.066627 | 0.057095 | -0.014738 | 0.026553 | -0.0017347 | -0.32044 | 60.2188 | -61.3449 | 60.3241 | -61.1069 | -61.5555 | -61.5097 | 0.054932 | 60.1868 | -61.3495 | 60.3058 | -61.2991 | -61.3998 | -61.3586 | -0.032044 | -0.14648 | -0.041198 | 0.20599 | -0.19684 | -0.24262 | -0.16479 | -0.21057 | -0.036621 | -0.17853 | -0.059509 | 0.013733 | -0.045777 | -0.086975 | -0.009156 | -0.050354 | 0.23804 | 121.669 | 0.050354 | 121.6553 | 121.5637 | 121.5363 | 121.5317 | 121.4996 | -121.7102 | -121.7148 | 121.637 | 121.6187 | 60.9924 | 61.3678
1337.1875 | 121.9803 | -61.2305 | 60.3424 | -0.10506 | 0.0052488 | 0.064115 | 0.059253 | -0.0046911 | -0.0090342 | -0.0019461 | -0.0039367 | 0.0061651 | 0.065986 | 0.051968 | -0.014524 | 0.025699 | -0.0055799 | -0.31586 | 60.1547 | -61.3037 | 60.4523 | -60.9604 | -61.4136 | -61.3815 | 0.2243 | 60.1776 | -61.3312 | 60.4248 | -61.1526 | -61.2625 | -61.2213 | -0.073242 | -0.18768 | 0.10986 | 0.27008 | -0.15106 | -0.1831 | -0.07782 | -0.10986 | -0.10071 | -0.16479 | 0.082398 | 0.07782 | 0.009156 | -0.032043 | 0.10986 | 0.068665 | 0.34332 | 121.756 | 0.17853 | 121.756 | 121.4584 | 121.5088 | 121.3852 | 121.4081 | -121.6461 | -121.6736 | 121.6827 | 121.6553 | 60.9146 | 61.4548
1338.9688 | 121.9803 | -61.3586 | 60.2417 | -0.18898 | 0.0058896 | 0.064756 | 0.060107 | -0.00084593 | -0.0081796 | -0.0025869 | -0.046661 | 0.0044561 | 0.064063 | 0.048123 | -0.015165 | 0.027621 | -0.0068615 | -0.53558 | 60.0632 | -61.4365 | 60.347 | -61.0886 | -61.5692 | -61.496 | 0.032043 | 60.0632 | -61.3861 | 60.3424 | -61.2762 | -61.3861 | -61.322 | -0.077819 | -0.17853 | 0.10529 | 0.27008 | -0.13733 | -0.21057 | -0.05951 | -0.13275 | -0.027465 | -0.17853 | 0.10071 | 0.082398 | 0.036622 | -0.027465 | 0.064087 | 0 | 0.3479 | 121.7834 | 0.10986 | 121.7285 | 121.4996 | 121.4493 | 121.4218 | 121.4218 | -121.6782 | -121.6278 | 121.7056 | 121.7011 | 60.8231 | 61.3907
1340.7188 | 121.9025 | -61.3678 | 60.2646 | -0.06691 | 0.005676 | 0.063047 | 0.064593 | 0.0012903 | -0.009675 | -0.0038687 | -0.080231 | 0.0040289 | 0.066627 | 0.055386 | -0.015165 | 0.027621 | -0.0060071 | -0.50812 | 60.1227 | -61.3998 | 60.3104 | -61.1435 | -61.5921 | -61.5692 | 0.032043 | 60.141 | -61.3998 | 60.2783 | -61.322 | -61.4456 | -61.3678 | -0.032043 | -0.14191 | 0.045777 | 0.2243 | -0.20142 | -0.2243 | -0.16937 | -0.19226 | -0.032043 | -0.1236 | 0.013733 | 0.045777 | 0 | -0.07782 | 0.032043 | -0.045777 | 0.25635 | 121.7102 | 0.07782 | 121.6782 | 121.5225 | 121.5408 | 121.4905 | 121.5088 | -121.6644 | -121.6644 | 121.6782 | 121.6461 | 60.8597 | 61.3998
1342.4062 | 121.8658 | -61.4044 | 60.2692 | -0.12794 | 0.0069578 | 0.063687 | 0.063311 | 0.0025721 | -0.0092478 | -0.0032277 | -0.1138 | 0.0038153 | 0.066413 | 0.054532 | -0.014311 | 0.028476 | -0.0036573 | -0.58594 | 60.141 | -61.4182 | 60.2966 | -61.1618 | -61.615 | -61.5875 | -0.027466 | 60.1273 | -61.4182 | 60.2417 | -61.4044 | -61.5143 | -61.4365 | -0.013733 | -0.12817 | 0.027466 | 0.24262 | -0.18311 | -0.21057 | -0.16937 | -0.19684 | -0.013733 | -0.14191 | -0.027466 | 0 | -0.032043 | -0.10986 | -0.01831 | -0.09613 | 0.25635 | 121.7148 | 0.013733 | 121.6599 | 121.5591 | 121.5454 | 121.5454 | 121.5317 | -121.6873 | -121.6873 | 121.701 | 121.6461 | 60.8185 | 61.377
1344.1562 | 121.962 | -61.2946 | 60.3058 | -0.1432 | 0.0065304 | 0.064542 | 0.058184 | 0.0010767 | -0.0094614 | -0.0013051 | -0.016144 | 0.0033881 | 0.065132 | 0.045987 | -0.012602 | 0.026981 | -0.0068615 | -0.48981 | 60.1593 | -61.3174 | 60.4248 | -60.997 | -61.4502 | -61.4044 | 0.20599 | 60.1318 | -61.3541 | 60.3882 | -61.203 | -61.3037 | -61.2717 | -0.022888 | -0.14648 | 0.11902 | 0.29755 | -0.10986 | -0.15564 | -0.086975 | -0.13275 | -0.059509 | -0.17395 | 0.082398 | 0.091553 | 0.022889 | -0.009155 | 0.082398 | 0.050354 | 0.32044 | 121.7422 | 0.15106 | 121.7422 | 121.4767 | 121.4859 | 121.4539 | 121.4264 | -121.6232 | -121.6599 | 121.7194 | 121.6827 | 60.8047 | 61.5005
1345.9062 | 121.8521 | -61.4227 | 60.2646 | -0.10506 | 0.0099484 | 0.066678 | 0.06502 | 8.47e-06 | -0.012025 | -0.0025869 | -0.092438 | 0.0078741 | 0.068122 | 0.064572 | -0.014311 | 0.028903 | -2.571e-05 | -0.80566 | 60.0998 | -61.4502 | 60.1639 | -61.2854 | -61.7386 | -61.6608 | -0.15564 | 60.054 | -61.4594 | 60.1822 | -61.4456 | -61.5601 | -61.4731 | -0.027466 | -0.16479 | -0.10071 | 0.13733 | -0.23804 | -0.31586 | -0.21057 | -0.28839 | -0.036622 | -0.21057 | -0.082397 | -0.022889 | -0.050354 | -0.13733 | -0.013732 | -0.10071 | 0.16479 | 121.6141 | 0.013733 | 121.6415 | 121.55 | 121.5134 | 121.5225 | 121.4767 | -121.7148 | -121.7239 | 121.5866 | 121.6049 | 60.6171 | 61.2671
1347.6562 | 121.8292 | -61.4456 | 60.2188 | -0.10506 | 0.0063168 | 0.066892 | 0.060962 | 0.0059901 | -0.0090342 | -0.00066434 | -0.11075 | 0.0048833 | 0.066627 | 0.055386 | -0.014524 | 0.027194 | -0.0015209 | -0.86517 | 60.1044 | -61.4731 | 60.1547 | -61.3174 | -61.7523 | -61.702 | -0.16937 | 60.0861 | -61.4685 | 60.1639 | -61.4639 | -61.615 | -61.4777 | -0.027465 | -0.11444 | -0.064087 | 0.12817 | -0.25635 | -0.3067 | -0.22888 | -0.27924 | -0.022888 | -0.13275 | -0.054932 | -0.01831 | -0.032043 | -0.16937 | -0.009155 | -0.14648 | 0.15564 | 121.6278 | 0.004578 | 121.6324 | 121.5775 | 121.5546 | 121.55 | 121.5317 | -121.6919 | -121.6873 | 121.6003 | 121.6095 | 60.5804 | 61.2762
1349.3438 | 121.9803 | -61.2991 | 60.3012 | -0.15846 | 0.0043942 | 0.066892 | 0.058825 | -0.0010595 | -0.010957 | -0.0036551 | 0.014374 | 0.0016791 | 0.0662 | 0.049618 | -0.014097 | 0.025485 | 0.00018809 | -0.66834 | 60.1273 | -61.3541 | 60.4202 | -60.9833 | -61.4365 | -61.4273 | 0.21515 | 60.1501 | -61.3678 | 60.3836 | -61.1755 | -61.29 | -61.2442 | -0.054932 | -0.17395 | 0.11902 | 0.31586 | -0.12817 | -0.13733 | -0.073242 | -0.082397 | -0.068665 | -0.15106 | 0.082398 | 0.1236 | 0.054931 | 0.009155 | 0.1236 | 0.07782 | 0.37079 | 121.7743 | 0.19226 | 121.7514 | 121.4813 | 121.5179 | 121.4264 | 121.4493 | -121.6553 | -121.669 | 121.7194 | 121.6827 | 60.6308 | 61.5143
1351.1094 | 121.9391 | -61.3586 | 60.2463 | -0.097427 | 0.0050352 | 0.066464 | 0.062243 | -0.0029821 | -0.010316 | -0.0032277 | 0.0021667 | 0.0031745 | 0.063636 | 0.048337 | -0.015592 | 0.024204 | -0.0034435 | -0.87433 | 60.0906 | -61.3998 | 60.2692 | -61.1435 | -61.5875 | -61.528 | 0.009155 | 60.0906 | -61.3998 | 60.2875 | -61.3129 | -61.4273 | -61.3495 | -0.041198 | -0.15564 | 0.022888 | 0.21515 | -0.16937 | -0.22888 | -0.12817 | -0.18768 | -0.041198 | -0.15564 | 0.041199 | 0.045777 | 0.009156 | -0.068664 | 0.050354 | -0.027466 | 0.25635 | 121.669 | 0.086975 | 121.6873 | 121.4905 | 121.4905 | 121.4493 | 121.4493 | -121.6461 | -121.6461 | 121.6278 | 121.6461 | 60.4843 | 61.3678
1352.8594 | 121.9666 | -61.3953 | 60.1501 | -0.12794 | 0.0078122 | 0.066678 | 0.060107 | 0.00086307 | -0.0098886 | -0.0015189 | -0.064972 | 0.0053107 | 0.06385 | 0.044278 | -0.013456 | 0.02869 | -0.0030163 | -0.9613 | 60.0174 | -61.4594 | 60.2737 | -61.1526 | -61.6196 | -61.5692 | -0.009155 | 60.0128 | -61.4731 | 60.2921 | -61.3312 | -61.4456 | -61.3632 | -0.064087 | -0.13275 | 0.1236 | 0.24262 | -0.17395 | -0.2243 | -0.10986 | -0.16022 | -0.077819 | -0.13733 | 0.14191 | 0.064087 | 0.032044 | -0.050354 | 0.10986 | 0.027465 | 0.3067 | 121.7331 | 0.14191 | 121.7651 | 121.4767 | 121.4859 | 121.4127 | 121.4081 | -121.6095 | -121.6232 | 121.669 | 121.6873 | 60.434 | 61.3861
1354.6094 | 121.8475 | -61.4639 | 60.2188 | -0.05928 | 0.0075986 | 0.067319 | 0.062243 | 0.0032129 | -0.0088206 | -0.0034415 | -0.1199 | 0.0048833 | 0.066413 | 0.050046 | -0.015592 | 0.026981 | -0.0049389 | -1.1078 | 60.0906 | -61.5051 | 60.1776 | -61.3129 | -61.7569 | -61.702 | -0.16022 | 60.0723 | -61.5051 | 60.1456 | -61.5005 | -61.6241 | -61.5234 | -0.041199 | -0.12817 | -0.041199 | 0.15106 | -0.23804 | -0.29297 | -0.19684 | -0.25177 | -0.041199 | -0.14648 | -0.073242 | -0.036621 | -0.059509 | -0.16022 | -0.01831 | -0.11902 | 0.19226 | 121.6827 | 0.004578 | 121.6507 | 121.5958 | 121.5775 | 121.5546 | 121.5363 | -121.7239 | -121.7239 | 121.6415 | 121.6095 | 60.3561 | 61.3037
1356.2969 | 121.8933 | -61.4273 | 60.2371 | -0.074539 | 0.008453 | 0.065396 | 0.063739 | -0.0010595 | -0.009675 | -0.0017325 | -0.086334 | 0.0050971 | 0.065772 | 0.058163 | -0.014097 | 0.026981 | -0.0060071 | -1.0666 | 60.0998 | -61.4548 | 60.2463 | -61.2076 | -61.6608 | -61.6058 | 0.013733 | 60.0998 | -61.4594 | 60.2188 | -61.3953 | -61.5417 | -61.4365 | -0.027466 | -0.13733 | 0.009155 | 0.21973 | -0.17853 | -0.23346 | -0.15106 | -0.20599 | -0.032044 | -0.13733 | -0.018311 | 0.032043 | -0.009155 | -0.11444 | 0.022889 | -0.082397 | 0.24719 | 121.7011 | 0.064087 | 121.6782 | 121.5546 | 121.5591 | 121.5271 | 121.5271 | -121.6919 | -121.6965 | 121.6736 | 121.6461 | 60.3607 | 61.441
1358.0469 | 121.9482 | -61.409 | 60.1822 | -0.16609 | 0.0082394 | 0.065824 | 0.061602 | -0.00020513 | -0.010316 | 0.0010447 | -0.016144 | 0.0042425 | 0.065132 | 0.050473 | -0.014311 | 0.026981 | -0.0060071 | -1.1902 | 60.0403 | -61.4365 | 60.2966 | -61.1298 | -61.6104 | -61.5555 | 0.027466 | 60.0037 | -61.4639 | 60.2783 | -61.3449 | -61.4594 | -61.3815 | -0.027465 | -0.14191 | 0.11444 | 0.27924 | -0.14648 | -0.20142 | -0.11902 | -0.17395 | -0.054931 | -0.17853 | 0.09613 | 0.064087 | 0.027466 | -0.050354 | 0.082397 | 0.004577 | 0.3067 | 121.7331 | 0.11902 | 121.7422 | 121.4767 | 121.4676 | 121.4493 | 121.4127 | -121.6187 | -121.6461 | 121.7056 | 121.6873 | 60.2188 | 61.4365
1359.7969 | 121.8521 | -61.4548 | 60.1959 | -0.1432 | 0.0043942 | 0.066251 | 0.064166 | 0.00022207 | -0.01117 | -0.0032277 | -0.12906 | 0.0044561 | 0.066841 | 0.054532 | -0.01367 | 0.028262 | -0.0038709 | -1.2451 | 60.1044 | -61.4868 | 60.1913 | -61.2442 | -61.7157 | -61.6791 | -0.086975 | 60.0769 | -61.4914 | 60.1456 | -61.4731 | -61.6241 | -61.5097 | -0.032043 | -0.091553 | -0.004578 | 0.21057 | -0.2243 | -0.26093 | -0.19226 | -0.22888 | -0.036621 | -0.11902 | -0.050354 | -0.01831 | -0.054932 | -0.16937 | -0.018311 | -0.13275 | 0.24261 | 121.6782 | 0.018311 | 121.637 | 121.5912 | 121.5683 | 121.5591 | 121.5317 | -121.6827 | -121.6873 | 121.6461 | 121.6003 | 60.2097 | 61.3678
1361.5625 | 121.8613 | -61.3815 | 60.2646 | -0.12032 | 0.0037534 | 0.065396 | 0.058612 | 0.00043587 | -0.010957 | -0.00066434 | -0.016144 | 0.0050971 | 0.064704 | 0.044705 | -0.014097 | 0.02634 | -0.0023755 | -1.1719 | 60.0906 | -61.3998 | 60.2921 | -61.1206 | -61.5784 | -61.5189 | 0.11902 | 60.1364 | -61.4365 | 60.228 | -61.3449 | -61.4639 | -61.409 | -0.01831 | -0.17395 | 0.027466 | 0.26093 | -0.13733 | -0.19684 | -0.11902 | -0.17853 | -0.054931 | -0.12817 | -0.036621 | 0.036621 | -0.027466 | -0.082397 | 0.027465 | -0.027466 | 0.27924 | 121.6919 | 0.091552 | 121.6644 | 121.4905 | 121.5729 | 121.4722 | 121.5179 | -121.6644 | -121.701 | 121.6736 | 121.6095 | 60.2097 | 61.5006
1363.25 | 121.9894 | -61.3861 | 60.2097 | -0.097427 | 0.0058896 | 0.066037 | 0.05968 | -0.0040503 | -0.0090342 | -0.0015189 | 0.035736 | 0.0029607 | 0.064704 | 0.054318 | -0.014311 | 0.026126 | -0.0034435 | -1.3229 | 60.0861 | -61.4136 | 60.3012 | -61.1023 | -61.5417 | -61.4914 | 0.15564 | 60.0677 | -61.4136 | 60.3149 | -61.2671 | -61.3678 | -61.3312 | -0.027466 | -0.1236 | 0.091552 | 0.28381 | -0.10529 | -0.15564 | -0.07782 | -0.12817 | -0.027466 | -0.14191 | 0.10528 | 0.11902 | 0.054931 | 0.01831 | 0.082397 | 0.045776 | 0.31128 | 121.7148 | 0.14648 | 121.7285 | 121.4996 | 121.4813 | 121.4722 | 121.4539 | -121.6232 | -121.6232 | 121.6873 | 121.701 | 60.0632 | 61.5417
1364.9844 | 121.843 | -61.5051 | 60.1776 | -0.082169 | 0.0046078 | 0.066037 | 0.060534 | -0.0023413 | -0.011598 | -0.0028005 | -0.04361 | 0.0044561 | 0.065559 | 0.054104 | -0.015379 | 0.025272 | -0.0072889 | -1.355 | 59.9899 | -61.5189 | 60.1685 | -61.2579 | -61.6974 | -61.6608 | 0.091553 | 60.0037 | -61.528 | 60.1181 | -61.4868 | -61.5875 | -61.528 | -0.013733 | -0.18768 | -0.009155 | 0.24719 | -0.15564 | -0.19226 | -0.14191 | -0.17853 | -0.022888 | -0.17395 | -0.059509 | 0.018311 | -0.022888 | -0.082397 | 0 | -0.059509 | 0.26092 | 121.6873 | 0.041199 | 121.6461 | 121.5088 | 121.5317 | 121.4951 | 121.5088 | -121.6965 | -121.7056 | 121.6736 | 121.6232 | 60.1501 | 61.5967
1366.7344 | 121.8475 | -62.3062 | 59.3491 | -0.11269 | 0.0069578 | 0.065396 | 0.06737 | 0.00064947 | -0.010316 | -0.0036551 | -0.09549 | 0.0070197 | 0.065559 | 0.049191 | -0.014738 | 0.028476 | -0.0010937 | -1.7258 | 59.198 | -62.384 | 59.2712 | -62.1964 | -62.6495 | -62.59 | -0.1831 | 59.1843 | -62.4069 | 59.3124 | -62.3337 | -62.4573 | -62.3337 | -0.07782 | -0.15106 | -0.07782 | 0.10986 | -0.28381 | -0.34332 | -0.20599 | -0.2655 | -0.10071 | -0.16479 | -0.036621 | -0.027466 | -0.027466 | -0.15106 | 0.073242 | -0.050354 | 0.18768 | 121.6553 | 0.073242 | 121.7194 | 121.582 | 121.5912 | 121.5042 | 121.4905 | -121.7331 | -121.756 | 121.5775 | 121.6187 | 60.5804 | 62.1231
1368.4844 | 121.9849 | -62.8784 | 58.7448 | -0.097427 | 0.0052488 | 0.064542 | 0.059039 | -0.0021277 | -0.01117 | -0.0032277 | -0.0039367 | 0.0042425 | 0.064277 | 0.050046 | -0.016447 | 0.027621 | -0.0038709 | -1.593 | 58.58 | -62.9013 | 58.873 | -62.5168 | -62.9791 | -62.9333 | 0.1831 | 58.5892 | -62.8922 | 58.8318 | -62.7411 | -62.8464 | -62.8189 | -0.022888 | -0.1648 | 0.12817 | 0.36163 | -0.054932 | -0.10071 | -0.032044 | -0.07782 | -0.013733 | -0.15564 | 0.086975 | 0.13733 | 0.059509 | 0.032043 | 0.073242 | 0.045776 | 0.38452 | 121.7743 | 0.15106 | 121.7239 | 121.4813 | 121.4813 | 121.4584 | 121.4676 | -121.6461 | -121.637 | 121.7514 | 121.7102 | 61.2854 | 63.0615
1370.1719 | 121.9482 | -62.1689 | 59.4452 | -0.12794 | 0.0069578 | 0.065183 | 0.064166 | 0.0025721 | -0.0092478 | -0.0051505 | -0.092438 | 0.0031745 | 0.065986 | 0.054532 | -0.015379 | 0.027835 | -0.0030163 | -1.8951 | 59.3124 | -62.2147 | 59.436 | -62.0041 | -62.4664 | -62.4069 | -0.09613 | 59.317 | -62.2284 | 59.5047 | -62.1185 | -62.2559 | -62.1597 | -0.045777 | -0.13275 | -0.009155 | 0.16479 | -0.23804 | -0.29755 | -0.19226 | -0.25177 | -0.05951 | -0.12817 | 0.05951 | 0.050354 | 0.009155 | -0.086975 | 0.068665 | -0.027465 | 0.21057 | 121.6507 | 0.10986 | 121.7331 | 121.5271 | 121.5454 | 121.4813 | 121.4859 | -121.6599 | -121.6736 | 121.6049 | 121.6736 | 60.2737 | 62.0728
1371.9219 | 121.8887 | -62.0041 | 59.6558 | -0.12032 | 0.0067442 | 0.065183 | 0.061816 | 0.0023585 | -0.01117 | -2.3544e-05 | -0.074127 | 0.0059515 | 0.064277 | 0.056027 | -0.014097 | 0.027194 | -0.0045117 | -1.8219 | 59.5276 | -62.0132 | 59.6649 | -61.7981 | -62.2238 | -62.1964 | 0.009155 | 59.5276 | -62.0316 | 59.6375 | -61.972 | -62.1002 | -62.0132 | -0.009156 | -0.12817 | 0.009155 | 0.20599 | -0.19226 | -0.21973 | -0.18311 | -0.21057 | -0.027466 | -0.12817 | -0.018311 | 0.032043 | -0.009156 | -0.096131 | 0.01831 | -0.068665 | 0.21515 | 121.6782 | 0.059509 | 121.669 | 121.5408 | 121.5591 | 121.5317 | 121.5317 | -121.669 | -121.6873 | 121.669 | 121.6415 | 60.1822 | 62.0132
1373.6719 | 121.8979 | -62.0087 | 59.6649 | -0.089798 | 0.0048214 | 0.064542 | 0.063739 | -0.00020513 | -0.010316 | -0.0025869 | -0.083283 | 0.0055243 | 0.067054 | 0.056241 | -0.015379 | 0.027408 | -0.0032299 | -1.9226 | 59.5184 | -62.027 | 59.6695 | -61.7386 | -62.2284 | -62.178 | 0.027466 | 59.5505 | -62.0453 | 59.6649 | -61.9446 | -62.0728 | -61.9949 | -0.018311 | -0.14648 | 0.004578 | 0.27008 | -0.16937 | -0.21973 | -0.15106 | -0.20142 | -0.036621 | -0.11444 | 0 | 0.064087 | 0.013733 | -0.064087 | 0.050354 | -0.027466 | 0.28839 | 121.6965 | 0.10071 | 121.7102 | 121.5454 | 121.5958 | 121.5271 | 121.5591 | -121.6919 | -121.7102 | 121.6782 | 121.6736 | 60.0861 | 62.0361
1375.3594 | 121.9711 | -62.0041 | 59.5688 | -0.18898 | 0.0075986 | 0.068387 | 0.062671 | -0.0025549 | -0.0077524 | -0.0017325 | -0.022247 | 0.0050971 | 0.065559 | 0.045987 | -0.014097 | 0.026767 | 0.00061529 | -2.0737 | 59.4406 | -62.0316 | 59.697 | -61.7203 | -62.2101 | -62.146 | 0.009155 | 59.436 | -62.0544 | 59.6924 | -61.8988 | -62.0361 | -61.9446 | -0.027466 | -0.12817 | 0.12817 | 0.28381 | -0.14191 | -0.20599 | -0.11444 | -0.17853 | -0.050354 | -0.13275 | 0.1236 | 0.10529 | 0.059509 | -0.032044 | 0.10986 | 0.01831 | 0.31128 | 121.7285 | 0.15564 | 121.7468 | 121.4722 | 121.4905 | 121.4447 | 121.4401 | -121.6003 | -121.6232 | 121.701 | 121.6965 | 59.9304 | 62.0132
1377.125 | 121.8979 | -62.1094 | 59.5322 | -0.10506 | 0.0067442 | 0.063901 | 0.06438 | -0.00020513 | -0.0075388 | -0.00087794 | -0.092438 | 0.0040289 | 0.065559 | 0.056027 | -0.01367 | 0.026553 | -0.0023755 | -2.1927 | 59.4269 | -62.1414 | 59.5184 | -61.9354 | -62.4023 | -62.3337 | -0.14648 | 59.3811 | -62.1826 | 59.5184 | -62.1185 | -62.2467 | -62.1506 | -0.032043 | -0.10529 | -0.013733 | 0.17395 | -0.2243 | -0.29297 | -0.19226 | -0.26093 | -0.073242 | -0.15106 | -0.013733 | -0.009155 | -0.041199 | -0.13733 | 0.032043 | -0.064087 | 0.20599 | 121.6599 | 0.064087 | 121.7011 | 121.5683 | 121.5637 | 121.5363 | 121.4905 | -121.6736 | -121.7148 | 121.6278 | 121.6278 | 59.9167 | 61.9629
1378.8594 | 121.8475 | -62.2055 | 59.4589 | -0.1432 | 0.0067442 | 0.065824 | 0.061389 | -0.0027685 | -0.007966 | -0.0030141 | -0.098541 | 0.0046697 | 0.0662 | 0.047482 | -0.01367 | 0.027194 | -0.0045117 | -2.243 | 59.3628 | -62.2467 | 59.3948 | -62.0544 | -62.5168 | -62.439 | -0.17395 | 59.317 | -62.2467 | 59.4086 | -62.233 | -62.3474 | -62.2284 | -0.041199 | -0.09613 | -0.064087 | 0.15106 | -0.23346 | -0.31128 | -0.19226 | -0.27008 | -0.041199 | -0.14191 | -0.050354 | -0.027466 | -0.022889 | -0.14191 | 0.01831 | -0.10071 | 0.19226 | 121.6415 | 0.013733 | 121.6553 | 121.6095 | 121.5637 | 121.5683 | 121.5225 | -121.7056 | -121.7056 | 121.6003 | 121.6141 | 59.9625 | 62.0316
1380.625 | 121.9757 | -62.1506 | 59.4452 | -0.082169 | 0.0037534 | 0.064969 | 0.058184 | -0.0029821 | -0.0090342 | -0.0025869 | 0.014374 | 0.0044561 | 0.066841 | 0.049405 | -0.014524 | 0.025485 | -0.00045291 | -2.0782 | 59.285 | -62.2101 | 59.5322 | -61.8439 | -62.3245 | -62.2604 | 0.21515 | 59.2758 | -62.2192 | 59.523 | -62.0453 | -62.1414 | -62.1094 | -0.059509 | -0.16022 | 0.086976 | 0.3067 | -0.10986 | -0.17395 | -0.050354 | -0.11444 | -0.068664 | -0.16937 | 0.07782 | 0.10529 | 0.041199 | 0.009156 | 0.10986 | 0.07782 | 0.36621 | 121.7422 | 0.17395 | 121.7422 | 121.4951 | 121.4951 | 121.4355 | 121.4264 | -121.6553 | -121.6644 | 121.6827 | 121.6736 | 60.0723 | 62.3657
1382.3125 | 121.9391 | -62.2925 | 59.3124 | -0.11269 | 0.0043942 | 0.064756 | 0.060107 | -0.0049047 | -0.012666 | -0.0023733 | -0.016144 | 0.0038153 | 0.065986 | 0.053891 | -0.013029 | 0.025058 | -0.0036573 | -2.2842 | 59.1614 | -62.3062 | 59.3536 | -62.059 | -62.5031 | -62.4481 | 0 | 59.1797 | -62.3474 | 59.3719 | -62.265 | -62.3383 | -62.2696 | -0.013733 | -0.15106 | 0.041199 | 0.23346 | -0.15564 | -0.21057 | -0.14191 | -0.19684 | -0.054932 | -0.13275 | 0.059509 | 0.027465 | 0.022888 | -0.045777 | 0.07782 | 0.009155 | 0.24719 | 121.6599 | 0.082397 | 121.7194 | 121.4676 | 121.5271 | 121.4539 | 121.4722 | -121.6187 | -121.6599 | 121.6461 | 121.6644 | 60.0082 | 62.2925
1384.0625 | 121.9666 | -62.4023 | 59.1934 | -0.13557 | 0.0078122 | 0.065396 | 0.062243 | 0.0021447 | -0.009675 | -0.0032277 | -0.046661 | 0.0053107 | 0.065345 | 0.052395 | -0.015592 | 0.025699 | -0.0057935 | -2.3575 | 59.024 | -62.4435 | 59.285 | -62.1094 | -62.6129 | -62.5442 | 0.009155 | 59.0469 | -62.4573 | 59.2941 | -62.3154 | -62.4298 | -62.3566 | -0.041198 | -0.16937 | 0.091553 | 0.29297 | -0.14191 | -0.21057 | -0.10071 | -0.16937 | -0.054931 | -0.14648 | 0.10071 | 0.086975 | 0.045777 | -0.027466 | 0.10071 | 0.027465 | 0.33417 | 121.7285 | 0.14191 | 121.7514 | 121.4676 | 121.5042 | 121.4264 | 121.4493 | -121.637 | -121.6507 | 121.6873 | 121.6965 | 60.0449 | 62.4115
1385.8125 | 121.8475 | -62.5305 | 59.1751 | -0.082169 | 0.0037534 | 0.062406 | 0.060962 | -0.0019141 | -0.011598 | -0.0040823 | -0.06192 | 0.0048833 | 0.064918 | 0.056881 | -0.014951 | 0.027408 | -0.0075025 | -2.33 | 59.0424 | -62.5534 | 59.1156 | -62.2925 | -62.7411 | -62.7182 | 0.018311 | 59.0378 | -62.5534 | 59.1019 | -62.4939 | -62.6129 | -62.5442 | -0.022888 | -0.13275 | -0.059509 | 0.23804 | -0.18768 | -0.21057 | -0.16479 | -0.18768 | -0.022888 | -0.13733 | -0.073242 | 0.036622 | -0.013732 | -0.082397 | 0.009156 | -0.059509 | 0.26093 | 121.669 | 0.05951 | 121.6553 | 121.5958 | 121.5912 | 121.5729 | 121.5683 | -121.7285 | -121.7285 | 121.6461 | 121.6324 | 60.2005 | 62.5488
1387.4844 | 121.962 | -64.5035 | 57.0923 | -0.12794 | 0.0075986 | 0.065183 | 0.061175 | -0.0019141 | -0.0094614 | -0.0034415 | 0.0082703 | 0.0036017 | 0.063636 | 0.049405 | -0.012602 | 0.027621 | -0.0019483 | -2.5269 | 56.8222 | -64.6774 | 57.074 | -64.3158 | -64.7964 | -64.7415 | 0.09613 | 56.8497 | -64.6729 | 57.1701 | -64.4257 | -64.4852 | -64.4348 | -0.17395 | -0.27008 | -0.01831 | 0.18768 | -0.23804 | -0.29297 | -0.064087 | -0.11902 | -0.16937 | -0.24261 | 0.07782 | 0.07782 | 0.068665 | 0.018311 | 0.23804 | 0.18768 | 0.36163 | 121.7514 | 0.24719 | 121.843 | 121.4996 | 121.5225 | 121.3257 | 121.3531 | -121.7697 | -121.7651 | 121.5775 | 121.6736 | 61.9766 | 64.5996
1389.25 | 121.9574 | -62.677 | 58.905 | -0.13557 | 0.0033262 | 0.06561 | 0.057971 | 0.0019311 | -0.010102 | -0.0038687 | -0.025299 | 0.0033881 | 0.065986 | 0.0556 | -0.013883 | 0.027621 | -0.0034435 | -2.4765 | 58.7219 | -62.7731 | 58.9279 | -62.4756 | -62.9288 | -62.8738 | 0.050354 | 58.7402 | -62.8006 | 58.9645 | -62.6175 | -62.7274 | -62.6678 | -0.09613 | -0.1831 | 0.022888 | 0.20142 | -0.19684 | -0.25177 | -0.10071 | -0.15564 | -0.1236 | -0.16479 | 0.05951 | 0.059509 | 0.009155 | -0.050354 | 0.13275 | 0.073242 | 0.29755 | 121.701 | 0.1831 | 121.7651 | 121.4951 | 121.5408 | 121.3989 | 121.4172 | -121.6782 | -121.7056 | 121.6049 | 121.6415 | 60.2005 | 62.7274
1391 | 121.9666 | -62.6678 | 58.9417 | -0.082169 | 0.0031126 | 0.065824 | 0.060962 | -0.0031957 | -0.012025 | -0.0023733 | -0.0039367 | 0.0036017 | 0.064491 | 0.050686 | -0.014951 | 0.024204 | -0.0070751 | -2.4399 | 58.7631 | -62.7274 | 59.0378 | -62.352 | -62.8372 | -62.7823 | 0.17395 | 58.7723 | -62.7457 | 59.0012 | -62.5717 | -62.6816 | -62.645 | -0.059509 | -0.17853 | 0.096131 | 0.31586 | -0.11444 | -0.16937 | -0.054932 | -0.10986 | -0.07782 | -0.16937 | 0.05951 | 0.096131 | 0.022889 | -0.013733 | 0.10071 | 0.064087 | 0.37537 | 121.7651 | 0.17395 | 121.7468 | 121.4905 | 121.5179 | 121.431 | 121.4401 | -121.669 | -121.6873 | 121.7056 | 121.669 | 60.228 | 62.8418
1392.7031 | 121.8567 | -63.2172 | 58.4564 | -0.051651 | 0.0058896 | 0.063687 | 0.061816 | -0.0089637 | -0.013307 | -0.0045095 | -0.092438 | 0.0046697 | 0.065132 | 0.050259 | -0.015379 | 0.026767 | -0.0032299 | -2.6138 | 58.3145 | -63.2446 | 58.4335 | -62.9974 | -63.446 | -63.4094 | 0.022888 | 58.3145 | -63.2492 | 58.3832 | -63.2034 | -63.327 | -63.2538 | -0.027466 | -0.14191 | -0.022888 | 0.21973 | -0.19226 | -0.22888 | -0.16479 | -0.20142 | -0.032044 | -0.14191 | -0.073242 | 0.013733 | -0.036621 | -0.10986 | -0.004577 | -0.077819 | 0.24719 | 121.6782 | 0.045777 | 121.6324 | 121.5591 | 121.5637 | 121.5317 | 121.5317 | -121.7011 | -121.7056 | 121.6507 | 121.6003 | 60.6033 | 63.2401
1394.4531 | 121.994 | -63.1302 | 58.4518 | -0.11269 | 0.0058896 | 0.064969 | 0.060321 | -0.0046911 | -0.011384 | -0.0023733 | 0.011322 | 0.0040289 | 0.065559 | 0.0462 | -0.014097 | 0.027835 | -0.0085705 | -2.6413 | 58.3054 | -63.1714 | 58.5709 | -62.8098 | -63.2721 | -63.2355 | 0.16479 | 58.3237 | -63.1622 | 58.5617 | -63.0066 | -63.1165 | -63.0661 | -0.041199 | -0.14648 | 0.11902 | 0.32043 | -0.10529 | -0.14191 | -0.064087 | -0.10071 | -0.032043 | -0.12817 | 0.10986 | 0.1236 | 0.064087 | 0.013733 | 0.09613 | 0.045776 | 0.36163 | 121.7422 | 0.15564 | 121.7239 | 121.4767 | 121.4859 | 121.4355 | 121.4539 | -121.6232 | -121.6141 | 121.701 | 121.6919 | 60.4889 | 63.295
1396.2031 | 121.875 | -63.3545 | 58.2458 | -0.11269 | 0.0061032 | 0.06561 | 0.063098 | -0.0023413 | -0.009675 | -0.0023733 | -0.13821 | 0.0031745 | 0.065132 | 0.05795 | -0.014097 | 0.027621 | -0.0081433 | -2.8244 | 58.168 | -63.414 | 58.3008 | -63.1119 | -63.6246 | -63.5651 | -0.045776 | 58.1543 | -63.4094 | 58.255 | -63.3682 | -63.501 | -63.4186 | -0.059509 | -0.07782 | 0.054931 | 0.24262 | -0.21057 | -0.27008 | -0.15106 | -0.21057 | -0.054932 | -0.091553 | 0.009155 | -0.013733 | -0.064087 | -0.14648 | -0.009155 | -0.091553 | 0.30212 | 121.7148 | 0.041199 | 121.6644 | 121.582 | 121.5637 | 121.5225 | 121.5088 | -121.6599 | -121.6553 | 121.6553 | 121.6095 | 60.5301 | 63.3087
1397.9688 | 121.843 | -65.5884 | 56.0669 | -0.12032 | 0.0046078 | 0.064115 | 0.059893 | -0.0042639 | -0.012239 | -0.0053641 | -0.046661 | 0.0072333 | 0.065132 | 0.049832 | -0.014738 | 0.025699 | -0.0023755 | -3.1494 | 55.5862 | -65.9042 | 56.1676 | -65.2451 | -65.712 | -65.6387 | 0.11444 | 55.9525 | -65.6708 | 55.9204 | -65.6616 | -65.6891 | -65.5701 | -0.31586 | -0.48065 | 0.10071 | 0.34332 | -0.050354 | -0.1236 | 0.2655 | 0.19226 | -0.082397 | -0.11444 | -0.14649 | -0.073242 | 0.018311 | -0.10071 | 0.10071 | -0.018311 | 0.65918 | 122.0718 | 0.009155 | 121.5912 | 121.4905 | 121.6232 | 121.1746 | 121.5408 | -121.9711 | -121.7377 | 121.756 | 121.5088 | 62.439 | 65.7028
1399.6562 | 121.8796 | -63.7848 | 57.8888 | -0.074539 | 0.007385 | 0.066037 | 0.062457 | -0.0042639 | -0.008607 | -0.0032277 | -0.098541 | 0.0061651 | 0.067695 | 0.053677 | -0.012388 | 0.027194 | -0.0047253 | -2.9617 | 57.7286 | -63.8031 | 57.8934 | -63.5101 | -63.9999 | -63.9542 | 0 | 57.7377 | -63.8077 | 57.8888 | -63.7253 | -63.8672 | -63.7802 | -0.018311 | -0.16022 | 0.004578 | 0.27466 | -0.16937 | -0.21515 | -0.15106 | -0.19684 | -0.022888 | -0.15106 | 0 | 0.059509 | 0.004578 | -0.082397 | 0.027466 | -0.059509 | 0.29297 | 121.6965 | 0.082397 | 121.6965 | 121.5317 | 121.5454 | 121.5134 | 121.5225 | -121.6919 | -121.6965 | 121.6782 | 121.6736 | 60.8231 | 63.7848
1401.4062 | 121.8613 | -63.8809 | 57.7744 | -0.089798 | 0.005676 | 0.062619 | 0.061389 | 0.00022207 | -0.010743 | -0.0038687 | -0.049713 | 0.0050971 | 0.066413 | 0.049618 | -0.013456 | 0.025058 | -0.0036573 | -2.9846 | 57.6462 | -63.9313 | 57.7332 | -63.6292 | -64.1144 | -64.0869 | 0.032043 | 57.637 | -63.9313 | 57.7286 | -63.8535 | -63.9771 | -63.9175 | -0.050354 | -0.12817 | -0.041199 | 0.25177 | -0.20599 | -0.23346 | -0.15564 | -0.18311 | -0.050354 | -0.13733 | -0.045776 | 0.027465 | -0.036622 | -0.096131 | 0.013732 | -0.045777 | 0.30212 | 121.6644 | 0.077819 | 121.6599 | 121.5775 | 121.5683 | 121.5271 | 121.5179 | -121.7056 | -121.7056 | 121.6141 | 121.6095 | 60.8963 | 63.913
1403.1094 | 121.9666 | -70.079 | 51.4664 | -0.13557 | 0.0095212 | 0.064969 | 0.059893 | -0.0023413 | -0.009675 | -0.0030141 | -0.034454 | 0.0036017 | 0.065559 | 0.047055 | -0.013242 | 0.027835 | -0.0066479 | -3.8452 | 51.297 | -70.166 | 51.5579 | -69.754 | -70.3217 | -70.2438 | -0.13733 | 51.3382 | -70.1889 | 51.5625 | -70.015 | -70.1385 | -70.0745 | -0.086975 | -0.16937 | 0.091552 | 0.32501 | -0.16479 | -0.24261 | -0.077819 | -0.15564 | -0.10986 | -0.12817 | 0.09613 | 0.064087 | 0.004578 | -0.059509 | 0.11444 | 0.050354 | 0.41199 | 121.7239 | 0.17395 | 121.7514 | 121.463 | 121.5271 | 121.376 | 121.4172 | -121.6324 | -121.6553 | 121.637 | 121.6415 | 66.2338 | 69.9417
1404.8125 | 121.9849 | -64.2105 | 57.399 | -0.17372 | 0.005676 | 0.065396 | 0.06203 | 0.0027857 | -0.0088206 | -0.0034415 | -0.04361 | 0.0048833 | 0.0662 | 0.049832 | -0.01132 | 0.027835 | -0.0045117 | -3.2593 | 57.2479 | -64.2288 | 57.4951 | -63.8718 | -64.3936 | -64.3112 | 0.027466 | 57.2388 | -64.2242 | 57.5134 | -64.0869 | -64.1968 | -64.1144 | -0.018311 | -0.15106 | 0.09613 | 0.33874 | -0.10071 | -0.18311 | -0.082397 | -0.16479 | -0.013733 | -0.16022 | 0.11444 | 0.1236 | 0.09613 | 0.013733 | 0.10986 | 0.027466 | 0.35706 | 121.7239 | 0.13733 | 121.7377 | 121.4767 | 121.463 | 121.4584 | 121.4493 | -121.6278 | -121.6232 | 121.7056 | 121.7239 | 60.9512 | 64.238
1406.5625 | 121.9208 | -71.2784 | 50.3036 | -0.089798 | 0.0050352 | 0.064969 | 0.060321 | -0.0012731 | -0.008607 | -0.0042959 | -0.0069885 | 0.0044561 | 0.0662 | 0.054532 | -0.014951 | 0.026126 | -0.0049389 | -4.0375 | 50.1526 | -71.3562 | 50.3632 | -70.9808 | -71.5027 | -71.4615 | -0.12817 | 50.1572 | -71.3745 | 50.3494 | -71.2051 | -71.3333 | -71.2601 | -0.07782 | -0.15106 | 0.059509 | 0.29755 | -0.18311 | -0.22431 | -0.10529 | -0.14648 | -0.096131 | -0.14648 | 0.045776 | 0.073242 | 0.01831 | -0.054932 | 0.11444 | 0.041199 | 0.37537 | 121.7194 | 0.16937 | 121.7239 | 121.5088 | 121.5317 | 121.431 | 121.4355 | -121.6599 | -121.6782 | 121.6415 | 121.6278 | 67.2409 | 71.1502
1408.3125 | 121.875 | -66.5039 | 55.2017 | -0.082169 | 0.0058896 | 0.065183 | 0.062457 | -0.0023413 | -0.010102 | -0.0023733 | -0.11075 | 0.0063787 | 0.066841 | 0.051755 | -0.014738 | 0.026126 | -0.0068615 | -3.5385 | 55.4306 | -66.1194 | 55.5862 | -65.8127 | -66.2933 | -66.2201 | -0.16022 | 55.426 | -66.2338 | 55.1239 | -66.4902 | -66.6229 | -66.4948 | 0.38452 | 0.22888 | 0.38452 | 0.69122 | 0.28381 | 0.21057 | -0.10071 | -0.17395 | 0.27008 | 0.2243 | -0.07782 | 0.013733 | 0.009155 | -0.11902 | -0.26093 | -0.3891 | 0.3067 | 121.7056 | -0.25635 | 121.3577 | 121.55 | 121.6599 | 121.9345 | 121.9299 | -121.3211 | -121.4355 | 122.0901 | 121.6278 | 62.9654 | 66.3437
1409.9844 | 121.9437 | -66.4627 | 55.1285 | -0.082169 | 0.0067442 | 0.063901 | 0.059893 | 0.00086307 | -0.0092478 | -2.3544e-05 | -0.019196 | 0.0036017 | 0.064277 | 0.056027 | -0.015592 | 0.02634 | -0.0019483 | -3.5934 | 55.0964 | -66.4032 | 55.2109 | -66.1697 | -66.6595 | -66.5771 | -0.045776 | 55.014 | -66.5039 | 55.188 | -66.3849 | -66.5085 | -66.4261 | 0.05951 | -0.032043 | 0.082397 | 0.29297 | -0.11444 | -0.19684 | -0.17395 | -0.25635 | -0.041198 | -0.11444 | 0.059509 | 0.07782 | 0.036622 | -0.045776 | 0.07782 | -0.004578 | 0.23346 | 121.6141 | 0.11902 | 121.6919 | 121.4996 | 121.5179 | 121.5591 | 121.4767 | -121.5317 | -121.6324 | 121.6736 | 121.6507 | 62.8693 | 66.4169
1411.7344 | 121.8842 | -66.5863 | 55.0735 | -0.089798 | 0.0061032 | 0.06561 | 0.062884 | 0.00086307 | -0.010102 | -0.0015189 | -0.077179 | 0.0031745 | 0.065345 | 0.061368 | -0.015379 | 0.02634 | -0.0047253 | -3.6621 | 54.9637 | -66.5726 | 55.0827 | -66.2979 | -66.774 | -66.7328 | 0.050354 | 54.9454 | -66.6138 | 55.069 | -66.5176 | -66.6504 | -66.568 | 0.013733 | -0.10986 | 0.009156 | 0.28839 | -0.14648 | -0.18768 | -0.16022 | -0.20142 | -0.027466 | -0.12817 | -0.004577 | 0.068665 | 0.018311 | -0.064087 | 0.045777 | -0.036621 | 0.27466 | 121.6553 | 0.096131 | 121.6827 | 121.5363 | 121.5591 | 121.55 | 121.5317 | -121.6461 | -121.6873 | 121.669 | 121.6553 | 62.9242 | 66.6367
1413.4375 | 121.9391 | -67.6071 | 53.9795 | -0.15083 | 0.0033262 | 0.064969 | 0.060321 | -0.0027685 | -0.011598 | -0.00087794 | -0.025299 | 0.0018927 | 0.065559 | 0.053891 | -0.014311 | 0.025912 | -0.0049389 | -4.3808 | 54.0985 | -67.3737 | 54.126 | -67.2272 | -67.7536 | -67.7032 | -0.71869 | 53.8513 | -67.6804 | 54.0436 | -67.5156 | -67.6025 | -67.5842 | 0.23346 | 0.11902 | 0.14648 | 0.37994 | -0.09613 | -0.14648 | -0.32959 | -0.37994 | -0.073242 | -0.12817 | 0.064087 | 0.091553 | 0.022888 | 0.004578 | 0.09613 | 0.07782 | 0.14648 | 121.4996 | 0.16479 | 121.7239 | 121.4722 | 121.5317 | 121.7056 | 121.4584 | -121.3531 | -121.6599 | 121.7331 | 121.6507 | 63.2263 | 66.8884
1415.1875 | 121.8567 | -66.4124 | 55.2887 | -0.1432 | 0.0063168 | 0.064756 | 0.063952 | -0.0017005 | -0.0075388 | -0.0051505 | -0.12601 | 0.0063787 | 0.065986 | 0.054532 | -0.015806 | 0.028262 | -0.0019483 | -3.9185 | 55.1514 | -66.3986 | 55.2795 | -66.0736 | -66.6 | -66.5588 | -0.064087 | 55.1376 | -66.4169 | 55.2521 | -66.3483 | -66.4948 | -66.394 | 0.013733 | -0.13733 | -0.009155 | 0.33875 | -0.14648 | -0.18768 | -0.16022 | -0.20142 | -0.004577 | -0.15106 | -0.036621 | 0.064087 | 0.018311 | -0.082397 | 0.022888 | -0.07782 | 0.32501 | 121.6782 | 0.068664 | 121.669 | 121.55 | 121.5546 | 121.5637 | 121.55 | -121.6873 | -121.7056 | 121.6919 | 121.6644 | 62.4939 | 66.3483
1416.9375 | 121.9482 | -66.5817 | 54.9911 | -0.15083 | 0.0063168 | 0.066678 | 0.060534 | -0.0017005 | -0.008607 | -0.0036551 | -0.04361 | 0.0029607 | 0.067054 | 0.050473 | -0.012174 | 0.025272 | -0.0030163 | -4.0009 | 54.863 | -66.6092 | 55.1193 | -66.2109 | -66.7648 | -66.7145 | 0.004578 | 54.8584 | -66.6275 | 55.0964 | -66.4856 | -66.6183 | -66.5314 | -0.027466 | -0.12817 | 0.12817 | 0.37079 | -0.13275 | -0.18311 | -0.10529 | -0.15564 | -0.045776 | -0.13275 | 0.10529 | 0.09613 | 0.050354 | -0.036621 | 0.09613 | 0.009155 | 0.39825 | 121.7285 | 0.14191 | 121.7239 | 121.4722 | 121.4859 | 121.4447 | 121.4401 | -121.6003 | -121.6187 | 121.7011 | 121.6782 | 62.5809 | 66.5863
1418.6875 | 121.8613 | -66.6595 | 55.0049 | -0.05928 | 0.0050352 | 0.065396 | 0.063098 | -0.0051183 | -0.010957 | -0.0023733 | -0.071076 | 0.0044561 | 0.066413 | 0.052395 | -0.014951 | 0.025699 | -0.0040845 | -4.0741 | 54.8859 | -66.6687 | 54.982 | -66.3712 | -66.861 | -66.8472 | -0.009155 | 54.9042 | -66.7007 | 54.9637 | -66.6138 | -66.7465 | -66.6641 | -0.009155 | -0.11902 | -0.022888 | 0.28839 | -0.18768 | -0.20142 | -0.17853 | -0.19226 | -0.041199 | -0.10071 | -0.041199 | 0.045776 | -0.004578 | -0.086975 | 0.036621 | -0.045776 | 0.29755 | 121.6507 | 0.086975 | 121.6644 | 121.5546 | 121.6049 | 121.5454 | 121.5637 | -121.6736 | -121.7056 | 121.6415 | 121.6232 | 62.5854 | 66.6504
1420.3906 | 121.8292 | -68.1839 | 53.4714 | -0.097427 | 0.007385 | 0.064756 | 0.062457 | -0.0023413 | -0.0075388 | 0.00061746 | -0.10464 | 0.0057379 | 0.064277 | 0.052182 | -0.016233 | 0.02933 | -0.0019483 | -4.3213 | 53.3157 | -68.2343 | 53.4302 | -67.923 | -68.4631 | -68.4128 | -0.018311 | 53.3386 | -68.248 | 53.4256 | -68.1656 | -68.3166 | -68.2068 | -0.050354 | -0.15564 | -0.041199 | 0.26093 | -0.22888 | -0.27924 | -0.17853 | -0.22888 | -0.064087 | -0.13275 | -0.045777 | 0.018311 | -0.022888 | -0.13275 | 0.041199 | -0.068664 | 0.31128 | 121.6644 | 0.082398 | 121.6736 | 121.55 | 121.5866 | 121.4996 | 121.5225 | -121.7056 | -121.7194 | 121.6141 | 121.6095 | 63.8626 | 68.1656
1422.1406 | 121.8384 | -68.1015 | 53.5629 | -0.044022 | 0.003967 | 0.064115 | 0.060321 | -0.0038367 | -0.010102 | -0.0034415 | -0.040558 | 0.0055243 | 0.065986 | 0.052182 | -0.01367 | 0.025272 | -0.0079297 | -4.3991 | 53.389 | -68.1885 | 53.5172 | -67.8268 | -68.3304 | -68.2938 | -0.004578 | 53.4164 | -68.1839 | 53.4897 | -68.0786 | -68.2068 | -68.1152 | -0.086976 | -0.17395 | -0.045776 | 0.27466 | -0.19226 | -0.22888 | -0.10528 | -0.14191 | -0.082398 | -0.14648 | -0.073242 | 0.022888 | -0.013733 | -0.10529 | 0.068665 | -0.022888 | 0.36163 | 121.7056 | 0.10529 | 121.6736 | 121.5775 | 121.6003 | 121.4905 | 121.5179 | -121.7514 | -121.7468 | 121.6187 | 121.5912 | 63.7024 | 68.0969
1423.8281 | 121.962 | -69.5297 | 52.0203 | -0.15846 | 0.0075986 | 0.066037 | 0.06203 | -0.0031957 | -0.0075388 | 0.0010447 | -0.052765 | 0.0021063 | 0.065986 | 0.054532 | -0.014738 | 0.025272 | -0.0047253 | -4.7516 | 51.8784 | -69.5984 | 52.1576 | -69.1727 | -69.7495 | -69.6762 | -0.036621 | 51.8784 | -69.6213 | 52.1484 | -69.4107 | -69.5526 | -69.4565 | -0.068665 | -0.14191 | 0.13733 | 0.35706 | -0.14648 | -0.21973 | -0.077819 | -0.15106 | -0.091553 | -0.14191 | 0.12817 | 0.11902 | 0.073242 | -0.022888 | 0.1648 | 0.068665 | 0.42572 | 121.756 | 0.21057 | 121.7697 | 121.4767 | 121.4996 | 121.4081 | 121.4081 | -121.6187 | -121.6415 | 121.6873 | 121.6782 | 64.7781 | 69.4931
1425.5781 | 121.907 | -69.9188 | 51.7044 | -0.036392 | 0.0058896 | 0.066251 | 0.060534 | 0.0021447 | -0.0090342 | -0.0010915 | -0.1077 | 0.0063787 | 0.065559 | 0.053677 | -0.015806 | 0.02634 | -0.0055799 | -4.8019 | 51.6129 | -69.96 | 51.7273 | -69.6121 | -70.1202 | -70.0928 | 0.027466 | 51.5671 | -69.9783 | 51.7364 | -69.8456 | -69.9829 | -69.8914 | -0.041199 | -0.091553 | 0.022888 | 0.3067 | -0.17395 | -0.20142 | -0.13275 | -0.16022 | -0.05951 | -0.13733 | 0.032043 | 0.073242 | 0.027466 | -0.064087 | 0.086976 | -0.004577 | 0.3479 | 121.6873 | 0.13275 | 121.7148 | 121.5729 | 121.5454 | 121.5317 | 121.4859 | -121.6644 | -121.6827 | 121.6461 | 121.6553 | 65.1169 | 69.9463
1427.2656 | 121.8384 | -70.2209 | 51.4343 | -0.097427 | 0.0065304 | 0.068601 | 0.062671 | -0.00084593 | -0.0071116 | -0.0025869 | -0.10159 | 0.0053107 | 0.065986 | 0.051755 | -0.015592 | 0.026767 | -0.0030163 | -5.1453 | 51.3611 | -70.2347 | 51.3977 | -69.9463 | -70.5002 | -70.4407 | -0.20142 | 51.3199 | -70.2576 | 51.4069 | -70.1935 | -70.34 | -70.2072 | -0.013733 | -0.073242 | -0.036621 | 0.27466 | -0.21973 | -0.27924 | -0.20599 | -0.2655 | -0.036621 | -0.11444 | -0.027466 | 0.027466 | 0.013733 | -0.11902 | 0.050354 | -0.082398 | 0.28839 | 121.6324 | 0.064087 | 121.6644 | 121.5958 | 121.5775 | 121.582 | 121.5408 | -121.669 | -121.6919 | 121.6187 | 121.6278 | 65.0757 | 70.0195
1429.0156 | 121.9254 | -70.5231 | 51.0635 | -0.082169 | 0.0067442 | 0.064328 | 0.062671 | 0.0012903 | -0.010743 | -0.0013051 | -0.0008851 | 0.0036017 | 0.064063 | 0.045346 | -0.013883 | 0.025699 | -0.0015209 | -5.2689 | 50.9079 | -70.578 | 51.1185 | -70.1843 | -70.7336 | -70.6787 | -0.045776 | 50.9308 | -70.5963 | 51.1276 | -70.4361 | -70.5597 | -70.4819 | -0.054932 | -0.15564 | 0.054931 | 0.33875 | -0.15564 | -0.21057 | -0.10071 | -0.15564 | -0.073242 | -0.13275 | 0.064087 | 0.086975 | 0.041198 | -0.036621 | 0.11444 | 0.036621 | 0.39368 | 121.6965 | 0.16022 | 121.7239 | 121.4859 | 121.5271 | 121.431 | 121.4539 | -121.6415 | -121.6599 | 121.6415 | 121.6507 | 65.2542 | 70.4773
1430.7031 | 121.9803 | -71.0678 | 50.5142 | -0.12794 | 0.0031126 | 0.064969 | 0.058398 | 8.47e-06 | -0.010743 | -0.0034415 | 0.020477 | 0.0027471 | 0.066413 | 0.050473 | -0.016233 | 0.025912 | -0.0055799 | -5.3192 | 50.354 | -71.1044 | 50.6699 | -70.61 | -71.1639 | -71.1365 | 0.14191 | 50.3769 | -71.1273 | 50.6287 | -70.9122 | -71.0358 | -70.9946 | -0.036621 | -0.16022 | 0.15564 | 0.45776 | -0.068665 | -0.09613 | -0.032044 | -0.059509 | -0.059509 | -0.13733 | 0.11444 | 0.15564 | 0.073242 | 0.032043 | 0.13275 | 0.091552 | 0.49439 | 121.7743 | 0.21515 | 121.756 | 121.4584 | 121.5042 | 121.4218 | 121.4447 | -121.6187 | -121.6415 | 121.7377 | 121.6965 | 65.7486 | 71.2097
1432.4531 | 121.9482 | -72.5464 | 49.0448 | -0.11269 | 0.008453 | 0.067105 | 0.061816 | 0.00043587 | -0.009675 | -0.0040823 | -0.031403 | 0.0042425 | 0.064704 | 0.047268 | -0.01602 | 0.02933 | -0.0021619 | -5.7129 | 49.0448 | -72.4365 | 49.1455 | -72.1756 | -72.7386 | -72.6746 | 0.013733 | 48.8937 | -72.5967 | 49.1409 | -72.4274 | -72.551 | -72.4777 | 0.10986 | 0 | 0.10071 | 0.37079 | -0.12817 | -0.19226 | -0.23804 | -0.30212 | -0.050354 | -0.15106 | 0.09613 | 0.11902 | 0.068665 | -0.004577 | 0.11902 | 0.045777 | 0.26093 | 121.582 | 0.16937 | 121.7377 | 121.4813 | 121.4905 | 121.5912 | 121.4401 | -121.4813 | -121.6415 | 121.6919 | 121.6873 | 66.8335 | 72.5601
1434.1875 | 121.8384 | -71.2234 | 50.4639 | -0.05928 | 0.0065304 | 0.064542 | 0.061175 | 0.0017175 | -0.01117 | -0.0015189 | -0.04361 | 0.0050971 | 0.065986 | 0.053891 | -0.015379 | 0.025699 | -0.0053661 | -5.809 | 50.2716 | -71.3013 | 50.3998 | -70.9122 | -71.4294 | -71.402 | 0.013733 | 50.3082 | -71.2738 | 50.386 | -71.1777 | -71.283 | -71.2189 | -0.07782 | -0.19226 | -0.064087 | 0.31128 | -0.17853 | -0.20599 | -0.10071 | -0.12817 | -0.050354 | -0.15564 | -0.07782 | 0.045777 | 0.004578 | -0.059509 | 0.054932 | -0.009155 | 0.3891 | 121.7011 | 0.096131 | 121.6599 | 121.5729 | 121.582 | 121.4951 | 121.5317 | -121.7651 | -121.7377 | 121.6232 | 121.6095 | 65.4144 | 71.2372
1435.9375 | 121.8887 | -71.9421 | 49.7177 | -0.044022 | 0.0065304 | 0.067746 | 0.062884 | -0.0051183 | -0.0094614 | -0.0019461 | -0.083283 | 0.0057379 | 0.068122 | 0.050686 | -0.014738 | 0.02634 | -0.0077161 | -5.9509 | 49.7223 | -71.7911 | 49.704 | -71.5897 | -72.171 | -72.0016 | 0.018311 | 49.6445 | -71.8826 | 49.8596 | -71.727 | -71.8872 | -71.9193 | 0.15106 | 0.004578 | -0.013733 | 0.35248 | -0.059509 | -0.22888 | -0.21057 | -0.37994 | 0.05951 | -0.073242 | 0.14191 | 0.21515 | 0.022889 | 0.054932 | -0.036621 | -0.004578 | 0.20142 | 121.4951 | 0.15564 | 121.7422 | 121.5134 | 121.5271 | 121.6644 | 121.5866 | -121.5088 | -121.6003 | 121.6461 | 121.8018 | 65.9912 | 71.9604
1437.7031 | 121.8613 | -71.4249 | 50.2121 | -0.16609 | 0.0065304 | 0.066037 | 0.06438 | 0.00022207 | -0.0060434 | -0.0034415 | -0.09549 | 0.0055243 | 0.066413 | 0.056668 | -0.014738 | 0.027408 | -0.0017347 | -6.3446 | 50.2213 | -71.3745 | 50.2304 | -71.0266 | -71.5851 | -71.5485 | -0.36163 | 50.0519 | -71.5485 | 50.235 | -71.3562 | -71.5576 | -71.4569 | 0.050354 | 0.009155 | 0.018311 | 0.39825 | -0.1236 | -0.16022 | -0.17395 | -0.21057 | -0.1236 | -0.16022 | 0.022888 | 0.068665 | -0.032043 | -0.13275 | 0.091553 | -0.009155 | 0.3479 | 121.6049 | 0.19226 | 121.7834 | 121.5958 | 121.6003 | 121.6461 | 121.4767 | -121.5866 | -121.7606 | 121.6553 | 121.6599 | 65.0803 | 71.0632
1439.3906 | 121.843 | -71.4523 | 50.2121 | -0.074539 | 0.0033262 | 0.066251 | 0.062671 | 0.0015039 | -0.011811 | -0.0034415 | -0.013092 | 0.0048833 | 0.064918 | 0.048764 | -0.012388 | 0.02634 | -0.0064343 | -6.3995 | 50.061 | -71.5118 | 50.1846 | -71.1136 | -71.6583 | -71.6217 | 0 | 50.0931 | -71.5256 | 50.1663 | -71.3745 | -71.5118 | -71.4569 | -0.059509 | -0.15106 | -0.027466 | 0.33875 | -0.16937 | -0.20599 | -0.10986 | -0.14648 | -0.073242 | -0.11902 | -0.045776 | 0.07782 | -0.004577 | -0.059509 | 0.068665 | 0.013733 | 0.39826 | 121.6965 | 0.15106 | 121.6919 | 121.5729 | 121.6187 | 121.5134 | 121.5454 | -121.7239 | -121.7377 | 121.637 | 121.6187 | 65.0528 | 71.4523
1441.1406 | 121.8658 | -72.5784 | 49.0768 | -0.10506 | 0.0069578 | 0.065396 | 0.063952 | 0.00022207 | -0.0092478 | -0.0045095 | -0.1077 | 0.0061651 | 0.066413 | 0.051327 | -0.015165 | 0.026553 | -0.0057935 | -6.9031 | 48.9349 | -72.6746 | 48.999 | -72.2992 | -72.8851 | -72.8119 | -0.19226 | 48.9212 | -72.6425 | 49.0631 | -72.5372 | -72.6791 | -72.551 | -0.096131 | -0.14191 | -0.07782 | 0.27924 | -0.23346 | -0.3067 | -0.13733 | -0.21057 | -0.064087 | -0.15564 | -0.013733 | 0.041199 | 0.027466 | -0.10071 | 0.091553 | -0.036621 | 0.37537 | 121.6736 | 0.10529 | 121.7056 | 121.6095 | 121.5637 | 121.5134 | 121.4996 | -121.7514 | -121.7194 | 121.5775 | 121.6415 | 65.6754 | 72.3862
1442.8438 | 121.9437 | -72.8165 | 48.7518 | -0.15846 | 0.0067442 | 0.066678 | 0.061175 | -0.0017005 | -0.010102 | -0.0034415 | -0.028351 | 0.0040289 | 0.066841 | 0.042142 | -0.015165 | 0.028049 | -0.0034435 | -6.871 | 48.6099 | -72.876 | 48.848 | -72.3999 | -72.9858 | -72.9538 | 0.091553 | 48.6008 | -72.8897 | 48.8663 | -72.6974 | -72.8348 | -72.7524 | -0.05951 | -0.14191 | 0.09613 | 0.41657 | -0.13733 | -0.16937 | -0.077819 | -0.10986 | -0.073242 | -0.15106 | 0.11444 | 0.11902 | 0.064087 | -0.018311 | 0.13733 | 0.054931 | 0.47608 | 121.7239 | 0.19226 | 121.756 | 121.4859 | 121.4905 | 121.4264 | 121.4172 | -121.6278 | -121.6415 | 121.6644 | 121.6827 | 65.9454 | 72.908
1444.6094 | 121.9757 | -72.7844 | 48.8113 | -0.1432 | 0.0071714 | 0.067319 | 0.062457 | -0.0049047 | -0.007966 | -0.0047231 | -0.04361 | 0.0048833 | 0.067268 | 0.0509 | -0.015806 | 0.026553 | -0.0036573 | -7.164 | 48.674 | -72.8119 | 48.9166 | -72.3404 | -72.9446 | -72.8943 | -0.027466 | 48.674 | -72.8256 | 48.9349 | -72.6288 | -72.7844 | -72.6654 | -0.027466 | -0.13733 | 0.10529 | 0.44403 | -0.10986 | -0.16022 | -0.082397 | -0.13275 | -0.041199 | -0.13733 | 0.1236 | 0.15564 | 0.11902 | 0 | 0.16022 | 0.041199 | 0.4715 | 121.7285 | 0.19684 | 121.7606 | 121.4859 | 121.4996 | 121.4584 | 121.4584 | -121.6232 | -121.637 | 121.7011 | 121.7194 | 65.6204 | 72.757
1446.3594 | 121.8567 | -73.1003 | 48.5596 | -0.051651 | 0.00119 | 0.064542 | 0.059893 | -0.0044775 | -0.010316 | -0.0040823 | -0.037506 | 0.0050971 | 0.068763 | 0.046841 | -0.014097 | 0.024631 | -0.0021619 | -7.2235 | 48.4543 | -73.1415 | 48.5275 | -72.7341 | -73.2742 | -73.2559 | 0.059509 | 48.4497 | -73.1552 | 48.5275 | -73.0179 | -73.1598 | -73.0728 | -0.041198 | -0.10529 | -0.032043 | 0.36621 | -0.15564 | -0.17395 | -0.11444 | -0.13275 | -0.054931 | -0.10986 | -0.032043 | 0.082398 | 0.027466 | -0.059509 | 0.082397 | -0.004578 | 0.40741 | 121.669 | 0.13733 | 121.6827 | 121.5958 | 121.6049 | 121.5546 | 121.55 | -121.701 | -121.7148 | 121.6278 | 121.6278 | 65.8768 | 73.1598
1448.0469 | 121.9757 | -73.8007 | 47.7859 | -0.10506 | 0.0069578 | 0.06561 | 0.062457 | -0.0012731 | -0.0092478 | -0.0034415 | -0.086334 | 0.0040289 | 0.065559 | 0.058163 | -0.015806 | 0.026981 | -0.0028027 | -7.7362 | 47.6624 | -73.8556 | 47.8683 | -73.3841 | -73.9609 | -73.9243 | -0.082397 | 47.644 | -73.8876 | 47.9187 | -73.6588 | -73.8235 | -73.7091 | -0.054932 | -0.1236 | 0.082397 | 0.41656 | -0.1236 | -0.16022 | -0.068664 | -0.10528 | -0.086975 | -0.14191 | 0.13275 | 0.14191 | 0.091553 | -0.022888 | 0.17853 | 0.064087 | 0.4715 | 121.7239 | 0.22888 | 121.8063 | 121.5179 | 121.5317 | 121.463 | 121.4447 | -121.6415 | -121.6736 | 121.669 | 121.7194 | 66.0645 | 73.7183
1449.7812 | 121.9208 | -74.1531 | 47.4426 | -0.10506 | 0.0028988 | 0.064328 | 0.059039 | -0.0046911 | -0.010316 | -0.0062185 | 0.0082703 | 0.0046697 | 0.065345 | 0.045987 | -0.015379 | 0.025058 | -0.0062207 | -8.0658 | 46.8567 | -74.5926 | 47.3602 | -73.819 | -74.3546 | -74.3134 | 0.15564 | 47.2824 | -74.2401 | 47.5021 | -74.0479 | -74.1852 | -74.0799 | -0.43945 | -0.58594 | -0.082398 | 0.33417 | -0.16022 | -0.20142 | 0.27924 | 0.23804 | -0.086975 | -0.16022 | 0.059509 | 0.10528 | 0.073242 | -0.032044 | 0.16022 | 0.054931 | 0.77362 | 121.9528 | 0.19226 | 121.7422 | 121.4493 | 121.5225 | 121.0098 | 121.4355 | -122.0352 | -121.6827 | 121.5134 | 121.6553 | 66.0873 | 74.3088
1451.5312 | 121.9757 | -74.8077 | 46.756 | -0.12794 | 0.0035398 | 0.064756 | 0.059466 | -0.0031957 | -0.012879 | -0.0040823 | -0.0069885 | 0.0031745 | 0.062995 | 0.04321 | -0.015165 | 0.026126 | -0.0042981 | -8.2077 | 46.6187 | -74.881 | 46.8246 | -74.4324 | -75.0092 | -74.9954 | 0.064087 | 46.5454 | -74.9817 | 46.8933 | -74.6384 | -74.7665 | -74.707 | -0.073242 | -0.13733 | 0.068665 | 0.37537 | -0.18768 | -0.20142 | -0.11444 | -0.12817 | -0.17395 | -0.21057 | 0.13733 | 0.16937 | 0.10071 | 0.041198 | 0.27466 | 0.21515 | 0.44861 | 121.7056 | 0.34332 | 121.875 | 121.4996 | 121.5271 | 121.4264 | 121.3531 | -121.637 | -121.7377 | 121.6324 | 121.701 | 66.6 | 74.8718
1453.2344 | 121.8292 | -75.9567 | 45.694 | -0.15083 | 0.0063168 | 0.066678 | 0.065875 | -0.00084593 | -0.0077524 | -0.00045074 | -0.1199 | 0.0036017 | 0.063636 | 0.051755 | -0.011961 | 0.028903 | -0.0021619 | -8.8669 | 45.5887 | -75.9979 | 45.6528 | -75.6363 | -76.236 | -76.1902 | -0.2243 | 45.5612 | -76.0391 | 45.6665 | -75.9247 | -76.0712 | -75.9613 | -0.041199 | -0.10529 | -0.041199 | 0.32043 | -0.23346 | -0.27924 | -0.19226 | -0.23804 | -0.082398 | -0.13275 | -0.027466 | 0.032043 | -0.004578 | -0.11444 | 0.07782 | -0.032043 | 0.36163 | 121.6507 | 0.11444 | 121.7056 | 121.5866 | 121.6003 | 121.5454 | 121.5179 | -121.6919 | -121.7331 | 121.6095 | 121.6232 | 67.0898 | 75.7324
1454.9844 | 121.9437 | -76.0483 | 45.5521 | -0.089798 | 0.0061032 | 0.064115 | 0.059039 | 0.00022207 | -0.0083932 | -0.0038687 | -0.01004 | 0.0040289 | 0.066627 | 0.045346 | -0.013242 | 0.026981 | -0.0057935 | -8.9401 | 45.3049 | -76.1673 | 45.5704 | -75.65 | -76.2497 | -76.2314 | 0.21973 | 45.3918 | -76.1261 | 45.5795 | -75.9613 | -76.062 | -76.0071 | -0.11902 | -0.24719 | 0.018311 | 0.39825 | -0.18311 | -0.20142 | -0.064087 | -0.082398 | -0.07782 | -0.16022 | 0.027466 | 0.086975 | 0.041199 | -0.013733 | 0.11902 | 0.064087 | 0.51727 | 121.7377 | 0.16479 | 121.7056 | 121.4722 | 121.5179 | 121.3531 | 121.4401 | -121.7194 | -121.6782 | 121.6187 | 121.6278 | 67.1082 | 76.268
1456.7344 | 121.8613 | -76.712 | 44.8975 | -0.12032 | 0.007385 | 0.066464 | 0.065661 | 0.0023585 | -0.010743 | -0.0017325 | -0.1138 | 0.0040289 | 0.064918 | 0.057736 | -0.015165 | 0.028903 | -0.0036573 | -9.3475 | 44.7418 | -76.799 | 45.0851 | -76.1398 | -76.767 | -76.7349 | 0.1236 | 44.902 | -76.6937 | 44.8837 | -76.6846 | -76.8311 | -76.6891 | -0.086975 | -0.15564 | 0.18768 | 0.5722 | -0.022888 | -0.054932 | 0.064087 | 0.032043 | 0.01831 | 0.004578 | -0.013733 | 0.027466 | 0.022888 | -0.11902 | 0.004578 | -0.13733 | 0.65918 | 121.8842 | 0.009156 | 121.5775 | 121.5408 | 121.5958 | 121.4539 | 121.6141 | -121.6965 | -121.5912 | 121.7972 | 121.5958 | 67.3645 | 76.8356
1458.4688 | 121.9711 | -77.1973 | 44.3802 | -0.082169 | 0.0075986 | 0.066678 | 0.061389 | -0.0031957 | -0.008607 | -0.00045074 | 0.029632 | 0.0040289 | 0.0662 | 0.051755 | -0.015379 | 0.026126 | -0.0083569 | -9.7046 | 44.2566 | -77.2202 | 44.4901 | -76.6937 | -77.3071 | -77.2659 | 0.068665 | 44.2337 | -77.2842 | 44.5175 | -77.0142 | -77.1332 | -77.0828 | -0.022888 | -0.1236 | 0.10986 | 0.50354 | -0.068664 | -0.10986 | -0.045776 | -0.086975 | -0.086975 | -0.14648 | 0.13733 | 0.18311 | 0.11444 | 0.064087 | 0.20142 | 0.15106 | 0.52643 | 121.7102 | 0.27008 | 121.8018 | 121.4767 | 121.5179 | 121.4539 | 121.431 | -121.6003 | -121.6644 | 121.6873 | 121.7148 | 67.4927 | 77.2659
1460.1719 | 121.8887 | -76.4053 | 45.2454 | -0.12794 | 0.0063168 | 0.066464 | 0.061816 | -0.0012731 | -0.01053 | -0.0019461 | -0.089386 | 0.0050971 | 0.067268 | 0.054318 | -0.01367 | 0.025912 | 0.0021107 | -9.8099 | 45.0851 | -76.4557 | 45.2683 | -75.9521 | -76.5701 | -76.5427 | -0.022888 | 45.1172 | -76.4603 | 45.2866 | -76.2772 | -76.4236 | -76.3184 | -0.050354 | -0.16022 | 0.022889 | 0.45319 | -0.13733 | -0.16479 | -0.086976 | -0.11444 | -0.054932 | -0.12817 | 0.041199 | 0.12817 | 0.086975 | -0.018311 | 0.14191 | 0.036621 | 0.50354 | 121.7239 | 0.1831 | 121.7468 | 121.5408 | 121.5775 | 121.4905 | 121.5225 | -121.701 | -121.7056 | 121.6736 | 121.6919 | 66.5955 | 76.3824
1461.875 | 121.9254 | -78.4882 | 43.0573 | -0.12794 | 0.0086668 | 0.065396 | 0.061175 | -0.0019141 | -0.0088206 | -0.0040823 | -0.074127 | 0.0061651 | 0.065345 | 0.057522 | -0.013029 | 0.025699 | -0.0075025 | -10.0937 | 43.9545 | -77.5955 | 42.8467 | -78.1998 | -78.3829 | -78.0533 | -0.2655 | 43.4784 | -77.9663 | 43.3319 | -77.7649 | -77.7512 | -78.4515 | 0.89264 | 0.89722 | -0.21057 | 0.28839 | 0.43487 | 0.10528 | -0.45776 | -0.78735 | 0.52185 | 0.42114 | 0.27466 | 0.72327 | 0.036621 | 0.737 | -0.48523 | 0.21515 | -0.60425 | 120.4422 | 0.20142 | 121.2982 | 121.55 | 121.4447 | 122.4426 | 121.9666 | -120.6528 | -121.0236 | 121.3348 | 121.8201 | 68.3945 | 78.2227
1463.6406 | 121.8979 | -77.33 | 44.2841 | -0.074539 | 0.0067442 | 0.064756 | 0.062457 | -0.0017005 | -0.0094614 | -0.0015189 | -0.10159 | 0.0068059 | 0.06385 | 0.055386 | -0.014951 | 0.027408 | -0.0025891 | -10.7437 | 44.1696 | -77.3804 | 44.339 | -76.8768 | -77.4948 | -77.4628 | -0.022888 | 44.1879 | -77.4033 | 44.3298 | -77.1973 | -77.3712 | -77.2614 | -0.050354 | -0.11444 | 0.054931 | 0.45319 | -0.13275 | -0.16479 | -0.082398 | -0.11444 | -0.073242 | -0.096131 | 0.045776 | 0.13275 | 0.068664 | -0.041199 | 0.14191 | 0.032043 | 0.50354 | 121.7194 | 0.20599 | 121.7331 | 121.55 | 121.5912 | 121.4996 | 121.5179 | -121.6644 | -121.6873 | 121.669 | 121.6599 | 66.5863 | 77.3071
1465.3438 | 121.9849 | -77.9205 | 43.6203 | -0.15846 | 0.007385 | 0.06796 | 0.063098 | -0.00020513 | -0.008607 | -0.0053641 | -0.080231 | 0.0040289 | 0.066413 | 0.055386 | -0.015165 | 0.026553 | -0.0042981 | -11.1465 | 43.5333 | -77.9434 | 43.7805 | -77.4033 | -78.0075 | -77.948 | -0.022888 | 43.5837 | -77.9205 | 43.7668 | -77.774 | -77.9297 | -77.7969 | -0.022888 | -0.086975 | 0.16022 | 0.51727 | -0.027466 | -0.086975 | -0.004578 | -0.064087 | 0 | -0.036621 | 0.14648 | 0.14648 | 0.1236 | -0.009155 | 0.1236 | -0.009155 | 0.54016 | 121.7239 | 0.14648 | 121.6873 | 121.4767 | 121.5042 | 121.4539 | 121.5042 | -121.5637 | -121.5408 | 121.701 | 121.6873 | 66.774 | 77.8976
1467.0781 | 121.8201 | -78.1082 | 43.5425 | -0.10506 | 0.0078122 | 0.067105 | 0.063525 | -0.0012731 | -0.010102 | -0.0021597 | -0.098541 | 0.0036017 | 0.064704 | 0.048977 | -0.012815 | 0.026553 | -0.0019483 | -11.8378 | 43.4235 | -78.1494 | 43.483 | -77.7512 | -78.3554 | -78.3005 | -0.21515 | 43.4143 | -78.1677 | 43.5104 | -78.0487 | -78.2181 | -78.0853 | -0.041199 | -0.11902 | -0.059509 | 0.35706 | -0.19226 | -0.24719 | -0.15106 | -0.20599 | -0.05951 | -0.12817 | -0.032043 | 0.059509 | 0.022888 | -0.10986 | 0.082398 | -0.050354 | 0.39825 | 121.6324 | 0.11902 | 121.6782 | 121.5729 | 121.582 | 121.5317 | 121.5225 | -121.6919 | -121.7102 | 121.5912 | 121.6187 | 66.2704 | 77.8931
1468.7656 | 121.9025 | -78.273 | 43.3594 | -0.097427 | 0.009094 | 0.066464 | 0.062457 | -0.0049047 | -0.010743 | -0.00087794 | -0.086334 | 0.0068059 | 0.065132 | 0.052823 | -0.014951 | 0.027408 | -0.0036573 | -12.0438 | 43.2404 | -78.3096 | 43.3914 | -77.8244 | -78.4378 | -78.4058 | -0.036621 | 43.1992 | -78.3417 | 43.3914 | -78.1357 | -78.2867 | -78.1952 | -0.036621 | -0.11902 | 0.032043 | 0.44861 | -0.13275 | -0.16479 | -0.096131 | -0.12817 | -0.068665 | -0.16022 | 0.032043 | 0.13733 | 0.07782 | -0.013733 | 0.14648 | 0.054932 | 0.48523 | 121.701 | 0.20599 | 121.7331 | 121.55 | 121.5408 | 121.5134 | 121.4722 | -121.669 | -121.701 | 121.6644 | 121.6644 | 66.2292 | 78.2364
1470.4844 | 121.8246 | -78.3829 | 43.2724 | -0.12032 | 0.0054624 | 0.064328 | 0.061175 | -0.0025549 | -0.0094614 | -0.0042959 | -0.031403 | 0.0050971 | 0.064918 | 0.049191 | -0.013242 | 0.02634 | 0.0010425 | -12.4191 | 43.1351 | -78.4561 | 43.2266 | -77.98 | -78.5797 | -78.5248 | -0.073242 | 43.1625 | -78.4653 | 43.2266 | -78.3005 | -78.4332 | -78.3554 | -0.073242 | -0.13733 | -0.045776 | 0.40283 | -0.14191 | -0.19684 | -0.068664 | -0.1236 | -0.082397 | -0.10986 | -0.045776 | 0.082398 | 0.027466 | -0.050354 | 0.10986 | 0.032043 | 0.47607 | 121.6827 | 0.16479 | 121.6919 | 121.5912 | 121.6278 | 121.5179 | 121.5454 | -121.7285 | -121.7377 | 121.6095 | 121.6095 | 65.9637 | 78.3096
1472.2031 | 121.843 | -77.124 | 44.5541 | -0.12032 | 0.005676 | 0.068173 | 0.062671 | -0.0014867 | -0.0092478 | -0.0010915 | -0.09549 | 0.0053107 | 0.0662 | 0.056241 | -0.014311 | 0.029117 | -0.0055799 | -12.2269 | 44.2383 | -77.3117 | 44.4168 | -76.8127 | -77.6093 | -77.6367 | -0.10529 | 44.1193 | -77.4216 | 44.3893 | -77.0645 | -77.211 | -77.0645 | -0.18768 | -0.31586 | -0.13733 | 0.31128 | -0.5127 | -0.48523 | -0.32501 | -0.29755 | -0.29755 | -0.43488 | -0.1648 | 0.059509 | 0.059509 | -0.086976 | 0.35706 | 0.21057 | 0.49896 | 121.7285 | 0.35706 | 121.8109 | 121.55 | 121.5408 | 121.3623 | 121.2433 | -121.8658 | -121.9757 | 121.5408 | 121.5134 | 64.8972 | 77.0187
1473.9219 | 121.8384 | -77.9572 | 43.6844 | -0.082169 | 0.0048214 | 0.066251 | 0.061602 | -0.0068273 | -0.010102 | -0.0036551 | -0.0039367 | 0.0036017 | 0.064491 | 0.051968 | -0.012174 | 0.023563 | -0.0047253 | -12.9227 | 43.5287 | -78.0121 | 43.6386 | -77.5452 | -78.1494 | -78.1219 | -0.018311 | 43.5699 | -78.0258 | 43.6478 | -77.8702 | -78.0258 | -77.9343 | -0.054932 | -0.15564 | -0.045776 | 0.41199 | -0.16479 | -0.19226 | -0.10986 | -0.13733 | -0.068665 | -0.11444 | -0.036621 | 0.086975 | 0.022888 | -0.068665 | 0.091553 | 0 | 0.46692 | 121.6507 | 0.15564 | 121.6736 | 121.5408 | 121.5958 | 121.4859 | 121.5271 | -121.6965 | -121.7102 | 121.5958 | 121.6049 | 65.0345 | 77.9388
1475.6562 | 121.9528 | -78.1586 | 43.4052 | -0.13557 | 0.0054624 | 0.065396 | 0.059253 | 0.00022207 | -0.008607 | -0.0023733 | -0.01004 | 0.0029607 | 0.068122 | 0.04855 | -0.014738 | 0.027835 | -0.0042981 | -13.2523 | 43.2632 | -78.1815 | 43.5699 | -77.6138 | -78.2639 | -78.2135 | -0.013733 | 43.2816 | -78.2227 | 43.5654 | -77.9617 | -78.1219 | -78.0396 | -0.022889 | -0.14191 | 0.1648 | 0.54474 | -0.054932 | -0.10529 | -0.032043 | -0.082397 | -0.064087 | -0.1236 | 0.16022 | 0.19684 | 0.11902 | 0.036621 | 0.1831 | 0.10071 | 0.56763 | 121.7514 | 0.26093 | 121.788 | 121.4447 | 121.5042 | 121.4218 | 121.4401 | -121.5866 | -121.6278 | 121.7285 | 121.7239 | 64.9063 | 78.1448
1477.3594 | 121.875 | -77.5452 | 44.1101 | -0.06691 | 0.0020444 | 0.064328 | 0.061175 | -0.0027685 | -0.010957 | -0.0034415 | -0.058869 | 0.0046697 | 0.065345 | 0.051755 | -0.01602 | 0.027194 | -0.0075025 | -13.1607 | 43.7988 | -77.71 | 43.9774 | -77.3849 | -77.98 | -77.9709 | 0.045776 | 43.7576 | -77.7649 | 44.0781 | -77.4261 | -77.5726 | -77.4673 | -0.1648 | -0.31128 | -0.13275 | 0.16022 | -0.42572 | -0.43488 | -0.26092 | -0.27008 | -0.21973 | -0.35248 | -0.032043 | 0.11902 | 0.07782 | -0.027466 | 0.29755 | 0.19226 | 0.32501 | 121.6873 | 0.33875 | 121.843 | 121.5088 | 121.5225 | 121.344 | 121.3028 | -121.8201 | -121.875 | 121.5225 | 121.6232 | 64.3845 | 77.5909
1479.0625 | 121.9757 | -77.124 | 44.4626 | -0.074539 | 0.0041806 | 0.064542 | 0.058612 | -0.0089637 | -0.0092478 | -0.0030141 | -0.01004 | 0.0031745 | 0.0662 | 0.054532 | -0.015592 | 0.025272 | -0.0032299 | -13.4171 | 44.3207 | -77.1561 | 44.5816 | -76.5839 | -77.2018 | -77.1881 | 0.1236 | 44.2703 | -77.2202 | 44.5541 | -76.9638 | -77.092 | -77.0096 | -0.032044 | -0.14191 | 0.11902 | 0.54016 | -0.064087 | -0.07782 | -0.032043 | -0.045776 | -0.096131 | -0.19226 | 0.091553 | 0.16022 | 0.11444 | 0.032043 | 0.21057 | 0.12817 | 0.5722 | 121.7377 | 0.25635 | 121.7743 | 121.4767 | 121.4905 | 121.4447 | 121.3943 | -121.6187 | -121.6827 | 121.7056 | 121.6782 | 63.707 | 77.2476
1480.8125 | 121.8246 | -76.3412 | 45.3461 | -0.05928 | 0.003967 | 0.065824 | 0.059466 | -0.0038367 | -0.009675 | -0.0028005 | -0.037506 | 0.0038153 | 0.063636 | 0.049191 | -0.016233 | 0.025272 | -0.0057935 | -13.4857 | 45.1813 | -76.3184 | 45.3644 | -75.8377 | -76.4374 | -76.4191 | 0.009155 | 45.2362 | -76.3138 | 45.2957 | -76.2268 | -76.3367 | -76.3092 | 0.022889 | -0.16479 | 0.018311 | 0.50354 | -0.077819 | -0.09613 | -0.10071 | -0.11902 | 0.027466 | -0.10986 | -0.050354 | 0.11444 | 0.032044 | 0.004578 | 0.004578 | -0.022888 | 0.48065 | 121.6827 | 0.086975 | 121.6095 | 121.4996 | 121.55 | 121.5225 | 121.5775 | -121.6644 | -121.6599 | 121.7056 | 121.637 | 62.8555 | 76.3504
1482.5938 | 121.8796 | -76.8723 | 44.7281 | -0.12794 | 0.0050352 | 0.065183 | 0.063739 | -0.0027685 | -0.010102 | -0.0017325 | -0.09549 | 0.0063787 | 0.064063 | 0.0556 | -0.014524 | 0.028049 | -0.0066479 | -14.1953 | 44.6365 | -76.886 | 44.8059 | -76.4328 | -77.0737 | -77.0096 | -0.24261 | 44.7006 | -76.8723 | 44.7601 | -76.8036 | -76.9592 | -76.8265 | -0.013733 | -0.091552 | 0.07782 | 0.43945 | -0.13733 | -0.20142 | -0.1236 | -0.18768 | 0 | -0.027465 | 0.032044 | 0.068664 | 0.045776 | -0.086976 | 0.045776 | -0.086976 | 0.45319 | 121.6919 | 0.068664 | 121.6324 | 121.5225 | 121.5729 | 121.5088 | 121.5729 | -121.6141 | -121.6003 | 121.6782 | 121.6324 | 62.677 | 76.6296
1484.2969 | 121.8933 | -76.918 | 44.6777 | -0.13557 | 0.005676 | 0.063901 | 0.060748 | 0.0015039 | -0.010102 | -0.0015189 | -0.016144 | 0.0053107 | 0.063636 | 0.053036 | -0.015379 | 0.025912 | -0.0049389 | -14.1724 | 44.5267 | -76.9501 | 44.8059 | -76.387 | -77.0187 | -76.973 | 0.091553 | 44.577 | -76.9913 | 44.7327 | -76.7899 | -76.9363 | -76.8585 | -0.032043 | -0.15106 | 0.12817 | 0.53101 | -0.054931 | -0.10071 | -0.022888 | -0.068665 | -0.073242 | -0.10071 | 0.054932 | 0.12817 | 0.059509 | -0.01831 | 0.13275 | 0.054932 | 0.56305 | 121.756 | 0.20142 | 121.7239 | 121.4767 | 121.5683 | 121.4447 | 121.4951 | -121.6278 | -121.669 | 121.7239 | 121.6507 | 62.7457 | 77.0096
1486.0469 | 121.8842 | -77.3209 | 44.2841 | -0.089798 | 0.0071714 | 0.065396 | 0.062243 | -0.0027685 | -0.01053 | -0.0047231 | -0.10159 | 0.0044561 | 0.065345 | 0.0556 | -0.016447 | 0.027621 | -0.0060071 | -14.5981 | 44.1925 | -77.3758 | 44.3481 | -76.8356 | -77.4857 | -77.4399 | -0.059509 | 44.2062 | -77.3941 | 44.3436 | -77.1881 | -77.3621 | -77.2247 | -0.054931 | -0.091553 | 0.064087 | 0.48523 | -0.11902 | -0.16479 | -0.064087 | -0.10986 | -0.073242 | -0.07782 | 0.059509 | 0.13275 | 0.096131 | -0.041199 | 0.16937 | 0.032043 | 0.54016 | 121.7239 | 0.20599 | 121.7377 | 121.5683 | 121.6003 | 121.5134 | 121.5271 | -121.6599 | -121.6782 | 121.669 | 121.6644 | 62.7228 | 77.2614
1487.7344 | 121.962 | -77.1103 | 44.4489 | -0.10506 | 0.0043942 | 0.068387 | 0.059253 | -0.00041873 | -0.01053 | 0.0014719 | 0.011322 | 0.0038153 | 0.064491 | 0.047909 | -0.014097 | 0.025058 | -0.0023755 | -14.653 | 44.4992 | -76.9821 | 44.7098 | -76.474 | -77.0828 | -77.0966 | -0.022888 | 44.458 | -77.0233 | 44.7784 | -76.918 | -77.092 | -77.0187 | 0.12817 | 0.050354 | 0.26093 | 0.63629 | 0.013733 | 0.027466 | -0.11444 | -0.10071 | 0.086976 | 0.009155 | 0.32959 | 0.19226 | 0.091553 | 0.018311 | 0.004577 | -0.068665 | 0.50812 | 121.6919 | 0.10528 | 121.8018 | 121.4813 | 121.4813 | 121.6095 | 121.5683 | -121.431 | -121.4722 | 121.8201 | 121.8887 | 62.4573 | 77.0874
1489.4062 | 121.8567 | -77.2797 | 44.3481 | -0.10506 | 0.0058896 | 0.064756 | 0.062671 | -0.0036231 | -0.007966 | -0.0019461 | -0.068024 | 0.0046697 | 0.065345 | 0.060299 | -0.017088 | 0.027835 | -0.0032299 | -15.1291 | 44.2017 | -77.3392 | 44.3344 | -76.8814 | -77.5223 | -77.4582 | -0.1831 | 44.22 | -77.3621 | 44.3573 | -77.2064 | -77.3575 | -77.2339 | -0.059509 | -0.14649 | -0.013733 | 0.39825 | -0.17853 | -0.24262 | -0.11902 | -0.18311 | -0.082398 | -0.12817 | 0.009155 | 0.073242 | 0.045776 | -0.07782 | 0.12817 | 0.004578 | 0.45776 | 121.6736 | 0.15564 | 121.7194 | 121.5408 | 121.582 | 121.4813 | 121.4996 | -121.6873 | -121.7102 | 121.6141 | 121.637 | 62.1506 | 77.0966
1491.0938 | 121.8796 | -77.0462 | 44.5908 | -0.11269 | 0.0067442 | 0.066678 | 0.065448 | -0.0042639 | -0.0083932 | -0.0030141 | -0.080231 | 0.0048833 | 0.064491 | 0.051968 | -0.015592 | 0.028262 | -0.0017347 | -15.1978 | 44.4534 | -77.1011 | 44.6136 | -76.5701 | -77.2156 | -77.1698 | -0.013733 | 44.4672 | -77.1103 | 44.6274 | -76.8997 | -77.0782 | -76.973 | -0.054931 | -0.13733 | 0.022888 | 0.47608 | -0.1236 | -0.16937 | -0.068665 | -0.11444 | -0.064087 | -0.1236 | 0.036621 | 0.14648 | 0.073243 | -0.032043 | 0.13733 | 0.032044 | 0.53101 | 121.7148 | 0.21057 | 121.7377 | 121.5546 | 121.5775 | 121.4996 | 121.5134 | -121.6919 | -121.7011 | 121.6599 | 121.6736 | 61.8484 | 77.0325
1492.7656 | 121.843 | -76.918 | 44.7418 | -0.028763 | 0.007385 | 0.062833 | 0.060748 | -0.00063233 | -0.009675 | -0.0023733 | -0.016144 | 0.0057379 | 0.066627 | 0.053464 | -0.012815 | 0.023563 | -0.0028027 | -15.4221 | 44.5587 | -76.9592 | 44.7144 | -76.4648 | -77.0966 | -77.0691 | 0.004578 | 44.5679 | -76.9959 | 44.6777 | -76.8311 | -76.9684 | -76.8906 | -0.041199 | -0.18311 | -0.027466 | 0.45319 | -0.15106 | -0.17853 | -0.10986 | -0.13733 | -0.07782 | -0.17395 | -0.064087 | 0.086975 | 0.027466 | -0.050354 | 0.10529 | 0.027466 | 0.49438 | 121.6736 | 0.16479 | 121.6736 | 121.5179 | 121.5637 | 121.4767 | 121.4859 | -121.701 | -121.7377 | 121.6324 | 121.5958 | 61.496 | 76.9226
1494.4531 | 121.962 | -75.4349 | 46.1792 | -0.13557 | 0.0080258 | 0.066892 | 0.060107 | -0.0051183 | -0.008607 | -0.0028005 | -0.031403 | 0.0044561 | 0.06385 | 0.048337 | -0.016233 | 0.026126 | -0.0072889 | -15.239 | 45.9824 | -75.4715 | 46.2296 | -74.9405 | -75.5859 | -75.531 | -0.041199 | 45.9778 | -75.5081 | 46.2799 | -75.2747 | -75.3983 | -75.3067 | -0.036622 | -0.19684 | 0.050354 | 0.49438 | -0.096131 | -0.15106 | -0.059509 | -0.11444 | -0.073243 | -0.20142 | 0.10071 | 0.16022 | 0.12817 | 0.036621 | 0.20142 | 0.10986 | 0.53101 | 121.7011 | 0.23346 | 121.788 | 121.4539 | 121.4859 | 121.4172 | 121.4127 | -121.6507 | -121.6873 | 121.6644 | 121.7148 | 60.1959 | 75.3937
1496.1406 | 121.875 | -72.8622 | 48.793 | -0.051651 | 0.0061032 | 0.06561 | 0.062243 | 0.0010767 | -0.010102 | -0.0038687 | -0.077179 | 0.0055243 | 0.064918 | 0.050473 | -0.015379 | 0.028262 | -0.0045117 | -14.7263 | 48.6237 | -72.9263 | 48.8205 | -72.3953 | -73.0087 | -72.9813 | 0.032043 | 48.6465 | -72.8851 | 48.793 | -72.7432 | -72.8851 | -72.7844 | -0.064087 | -0.16937 | 0.027466 | 0.46692 | -0.11902 | -0.14648 | -0.054931 | -0.082397 | -0.022888 | -0.14648 | 0 | 0.11902 | 0.07782 | -0.022888 | 0.10071 | 0 | 0.53101 | 121.7468 | 0.14191 | 121.6782 | 121.55 | 121.5317 | 121.4859 | 121.5088 | -121.7194 | -121.6782 | 121.6827 | 121.6553 | 58.136 | 72.8943
1497.8281 | 121.843 | -71.9238 | 49.7314 | -0.097427 | 0.0071714 | 0.064328 | 0.06203 | 0.00043587 | -0.011598 | -0.0042959 | -0.06192 | 0.0042425 | 0.067054 | 0.052182 | -0.014311 | 0.027194 | -0.0025891 | -14.6439 | 49.6307 | -71.9513 | 49.7131 | -71.521 | -72.0932 | -72.0749 | -0.032043 | 49.6216 | -71.9467 | 49.6948 | -71.8185 | -71.965 | -71.9009 | -0.027466 | -0.10071 | -0.01831 | 0.40283 | -0.15106 | -0.16937 | -0.1236 | -0.14191 | -0.022888 | -0.10986 | -0.036621 | 0.10529 | 0.022888 | -0.041199 | 0.045776 | -0.018311 | 0.4303 | 121.6644 | 0.12817 | 121.6415 | 121.582 | 121.5683 | 121.5546 | 121.5454 | -121.6827 | -121.6782 | 121.637 | 121.6187 | 57.28 | 71.8918
1499.5781 | 121.8155 | -71.3562 | 50.2625 | -0.1432 | 0.0065304 | 0.066251 | 0.063098 | -0.00084593 | -0.0077524 | -0.0030141 | -0.10464 | 0.0055243 | 0.064491 | 0.049618 | -0.014524 | 0.027621 | -0.0030163 | -14.7263 | 50.1205 | -71.4111 | 50.267 | -70.9808 | -71.6034 | -71.553 | -0.15106 | 50.1572 | -71.4157 | 50.2258 | -71.3196 | -71.4844 | -71.3608 | -0.054932 | -0.14191 | 0.004578 | 0.37537 | -0.19684 | -0.24719 | -0.14191 | -0.19226 | -0.059509 | -0.10529 | -0.036621 | 0.036621 | -0.004578 | -0.12817 | 0.054931 | -0.068665 | 0.4303 | 121.6782 | 0.09613 | 121.6415 | 121.5317 | 121.5729 | 121.4767 | 121.5134 | -121.6736 | -121.6782 | 121.6232 | 121.582 | 56.6299 | 71.2051
1501.2656 | 121.8338 | -71.5988 | 50.0427 | -0.10506 | 0.0050352 | 0.064115 | 0.059253 | -0.0019141 | -0.01053 | -0.0034415 | -0.028351 | 0.0040289 | 0.066627 | 0.048764 | -0.014524 | 0.025485 | -0.0066479 | -14.9689 | 49.8367 | -71.6675 | 50.0336 | -71.1639 | -71.7636 | -71.7224 | 0.07782 | 49.8779 | -71.6721 | 49.9878 | -71.5256 | -71.6446 | -71.5668 | -0.068664 | -0.20599 | -0.009156 | 0.43488 | -0.1236 | -0.16479 | -0.054932 | -0.096131 | -0.073242 | -0.16479 | -0.054932 | 0.073242 | 0.032044 | -0.045776 | 0.10529 | 0.027466 | 0.50354 | 121.701 | 0.14648 | 121.6599 | 121.5042 | 121.55 | 121.4355 | 121.4767 | -121.7102 | -121.7148 | 121.6324 | 121.5866 | 56.6299 | 71.6766
1503.0156 | 121.9116 | -71.1823 | 50.3998 | -0.11269 | 0.0050352 | 0.064969 | 0.058825 | -0.00063233 | -0.007966 | -0.0030141 | -0.01004 | 0.0025335 | 0.064918 | 0.046841 | -0.013456 | 0.025699 | -0.0077161 | -15.3214 | 50.1709 | -71.3058 | 50.4868 | -70.697 | -71.347 | -71.2967 | -0.018311 | 50.267 | -71.2418 | 50.4593 | -71.109 | -71.2326 | -71.1136 | -0.1236 | -0.22888 | 0.086975 | 0.48523 | -0.11444 | -0.1648 | 0.009155 | -0.041199 | -0.059509 | -0.13275 | 0.05951 | 0.073242 | 0.068665 | -0.050354 | 0.12817 | 0.009155 | 0.60883 | 121.7926 | 0.13275 | 121.7011 | 121.4767 | 121.5088 | 121.3531 | 121.4493 | -121.7056 | -121.6415 | 121.669 | 121.6415 | 55.8609 | 71.1639
1504.8281 | 121.8338 | -70.3308 | 51.3062 | -0.10506 | 0.0071714 | 0.063901 | 0.062457 | 0.0010767 | -0.010743 | -0.0047231 | -0.016144 | 0.0027471 | 0.065559 | 0.042569 | -0.01367 | 0.027835 | -0.0038709 | -15.1566 | 51.1642 | -70.3262 | 51.3199 | -69.8959 | -70.4865 | -70.4453 | 0.059509 | 51.1826 | -70.3674 | 51.2558 | -70.2576 | -70.3903 | -70.3217 | 0.004578 | -0.14191 | 0.013733 | 0.43488 | -0.11444 | -0.15564 | -0.11902 | -0.16022 | -0.036621 | -0.1236 | -0.050354 | 0.073243 | 0.009156 | -0.059509 | 0.045777 | -0.022888 | 0.4303 | 121.6461 | 0.10986 | 121.6232 | 121.4905 | 121.55 | 121.4951 | 121.5134 | -121.6324 | -121.6736 | 121.6507 | 121.5866 | 55.1743 | 70.3903
1506.5781 | 121.9208 | -69.1635 | 52.446 | -0.10506 | 0.0065304 | 0.065396 | 0.059893 | -0.0025549 | -0.008607 | -0.0021597 | -0.016144 | 0.0040289 | 0.064704 | 0.047268 | -0.015592 | 0.02399 | -0.0062207 | -15.0742 | 52.3956 | -69.0903 | 52.6062 | -68.6234 | -69.2642 | -69.2276 | -0.07782 | 52.2903 | -69.2047 | 52.5101 | -69.0308 | -69.1498 | -69.0628 | 0.073242 | -0.050354 | 0.16022 | 0.54016 | -0.064087 | -0.10071 | -0.13733 | -0.17395 | -0.041199 | -0.15564 | 0.064087 | 0.13275 | 0.10071 | 0.013733 | 0.14191 | 0.054932 | 0.46692 | 121.6965 | 0.17395 | 121.7148 | 121.4859 | 121.4951 | 121.5591 | 121.4539 | -121.5363 | -121.6507 | 121.7697 | 121.6736 | 54.0894 | 69.0857
1508.3438 | 121.9162 | -69.6991 | 51.8921 | -0.13557 | 0.0082394 | 0.066464 | 0.059466 | -0.00084593 | -0.0083932 | -0.0034415 | -0.013092 | 0.0018927 | 0.067268 | 0.049832 | -0.015379 | 0.026767 | -0.0075025 | -15.6052 | 51.741 | -69.7449 | 51.9379 | -69.2917 | -69.8914 | -69.8273 | -0.004578 | 51.7364 | -69.754 | 51.947 | -69.5847 | -69.6945 | -69.6396 | -0.045776 | -0.15106 | 0.045776 | 0.40741 | -0.12817 | -0.19226 | -0.082398 | -0.14648 | -0.054931 | -0.15564 | 0.054931 | 0.11444 | 0.05951 | 0.004578 | 0.11444 | 0.059509 | 0.45319 | 121.6827 | 0.16937 | 121.701 | 121.4859 | 121.4905 | 121.4401 | 121.4355 | -121.637 | -121.6461 | 121.637 | 121.6461 | 54.0939 | 69.6945
1510.0938 | 121.8979 | -69.9326 | 51.6541 | -0.10506 | 0.0052488 | 0.065396 | 0.061602 | -0.0023413 | -0.0075388 | -0.0036551 | -0.034454 | 0.0040289 | 0.065559 | 0.052182 | -0.01602 | 0.026553 | -0.0030163 | -16.0446 | 51.4847 | -69.9692 | 51.6953 | -69.4977 | -70.1248 | -70.0607 | -0.032043 | 51.5305 | -69.9921 | 51.6953 | -69.8593 | -69.9692 | -69.9005 | -0.036621 | -0.16937 | 0.041198 | 0.43488 | -0.12817 | -0.19226 | -0.091553 | -0.15564 | -0.059509 | -0.1236 | 0.041198 | 0.073242 | 0.032043 | -0.036621 | 0.091552 | 0.022888 | 0.4715 | 121.6644 | 0.13275 | 121.6873 | 121.4539 | 121.5225 | 121.4172 | 121.463 | -121.6232 | -121.6461 | 121.6278 | 121.6278 | 53.8879 | 69.9005
1511.7812 | 121.843 | -68.6188 | 53.0273 | -0.089798 | 0.005676 | 0.066251 | 0.063311 | 0.0023585 | -0.0088206 | -0.0013051 | -0.12601 | 0.0036017 | 0.065772 | 0.051755 | -0.015379 | 0.027408 | -0.0064343 | -15.6738 | 52.8854 | -68.6783 | 53.0457 | -68.1976 | -68.8522 | -68.8065 | -0.041199 | 52.8854 | -68.6966 | 52.9907 | -68.5776 | -68.6966 | -68.5959 | -0.05951 | -0.14191 | 0.01831 | 0.42114 | -0.18768 | -0.23346 | -0.12817 | -0.17395 | -0.07782 | -0.14191 | -0.036621 | 0.041198 | 0.022888 | -0.07782 | 0.10071 | 0 | 0.48065 | 121.7239 | 0.11902 | 121.6873 | 121.5637 | 121.582 | 121.5042 | 121.5042 | -121.7056 | -121.7239 | 121.6644 | 121.6095 | 52.9449 | 68.5776
1513.5312 | 121.8979 | -67.2546 | 54.3137 | -0.11269 | 0.0065304 | 0.067746 | 0.061389 | -0.0023413 | -0.0094614 | -0.0047231 | -0.037506 | 0.0031745 | 0.064918 | 0.042355 | -0.014738 | 0.026126 | -0.00045291 | -15.4495 | 54.1809 | -67.305 | 54.3869 | -66.8289 | -67.4377 | -67.3782 | -0.036621 | 54.1809 | -67.3096 | 54.3777 | -67.186 | -67.2958 | -67.2043 | -0.050354 | -0.13275 | 0.073242 | 0.42572 | -0.1236 | -0.1831 | -0.073242 | -0.13275 | -0.054931 | -0.13275 | 0.064087 | 0.068665 | 0.050354 | -0.041198 | 0.10528 | 0.013733 | 0.47607 | 121.6919 | 0.1236 | 121.6873 | 121.4859 | 121.4905 | 121.4355 | 121.4355 | -121.6187 | -121.6232 | 121.6415 | 121.6324 | 51.8051 | 67.218
1515.2812 | 122.0078 | -83.6792 | 37.8845 | -0.089798 | 0.0061032 | 0.064115 | 0.060534 | -0.0025549 | -0.0075388 | -0.00045074 | -0.0069885 | 0.0036017 | 0.067695 | 0.0509 | -0.015379 | 0.025272 | -0.0079297 | -22.1146 | 38.1683 | -83.3038 | 38.53 | -82.5302 | -83.2993 | -83.2809 | -0.28839 | 38.2004 | -83.3176 | 37.4405 | -84.0454 | -84.1049 | -83.67 | 0.37537 | 0.28381 | 0.64545 | 1.149 | 0.39825 | 0.37994 | 0.022888 | 0.004578 | 0.36163 | 0.31586 | -0.44403 | -0.36621 | 0.009155 | -0.42572 | -0.35248 | -0.78735 | 0.77362 | 121.8338 | -0.72784 | 120.7581 | 121.4722 | 121.5179 | 121.8475 | 121.8796 | -121.1884 | -121.2021 | 122.2092 | 121.1197 | 61.5646 | 83.3908
1516.9688 | 121.7743 | -82.0908 | 39.6103 | -0.051651 | 0.0061032 | 0.062833 | 0.06438 | 0.00043587 | -0.0092478 | -0.0030141 | -0.086334 | 0.0044561 | 0.064277 | 0.055386 | -0.015806 | 0.02869 | -0.0057935 | -22.9523 | 40.21 | -82.3242 | 38.8092 | -82.2052 | -83.0063 | -82.8827 | 0.3479 | 38.9282 | -82.5302 | 39.3494 | -83.6426 | -82.9468 | -82.0404 | -0.23346 | 0.59967 | -0.80109 | -0.11444 | -0.79193 | -0.91553 | -0.55847 | -0.68207 | -0.43945 | -0.68207 | -0.26093 | -1.5518 | 0.050354 | -0.85602 | 0.48981 | -0.41656 | 0.11902 | 121.1334 | -1.1124 | 121.8796 | 122.5342 | 121.4584 | 122.3007 | 121.019 | -121.9345 | -122.1405 | 120.9 | 121.4401 | 59.1385 | 82.4387
1518.7188 | 121.8201 | -53.4531 | 68.0649 | -0.18898 | 0.0058896 | 0.064115 | 0.059039 | -0.0040503 | -0.007966 | -0.0042959 | -0.034454 | 0.0050971 | 0.062568 | 0.054318 | -0.014311 | 0.024631 | -0.0042981 | -9.7366 | 67.9504 | -53.421 | 68.1656 | -53.2242 | -53.6865 | -53.5446 | 0.25177 | 67.9276 | -53.4073 | 68.0969 | -53.3936 | -53.4988 | -53.5263 | 0.032043 | -0.11444 | 0.10071 | 0.22888 | -0.091553 | -0.23346 | -0.1236 | -0.2655 | 0.045776 | -0.13733 | 0.032044 | 0.059509 | -0.073242 | -0.045776 | -0.11902 | -0.091552 | 0.19684 | 121.5866 | 0.013733 | 121.5042 | 121.3715 | 121.3348 | 121.4035 | 121.3806 | -121.4859 | -121.4722 | 121.6187 | 121.55 | 43.7164 | 53.7048
1520.4688 | 121.6736 | -64.2517 | 57.1243 | -0.12032 | 0.0071714 | 0.06561 | 0.061816 | 0.0015039 | -0.0088206 | -0.0034415 | -0.1199 | 0.0055243 | 0.065986 | 0.058163 | -0.015165 | 0.028476 | -0.0036573 | -13.9572 | 59.3262 | -62.0865 | 59.7015 | -61.3586 | -62.1002 | -62.1094 | -1.3687 | 59.2438 | -62.1964 | 57.4356 | -64.1235 | -64.4669 | -64.5721 | 2.1652 | 2.2018 | 2.5772 | 2.8931 | 2.1423 | 2.1515 | -0.022888 | -0.013733 | 2.0554 | 2.1194 | 0.31128 | 0.12817 | -0.32043 | -0.21515 | -2.3758 | -2.2705 | 0.72784 | 121.788 | -1.9272 | 119.632 | 121.4127 | 121.4401 | 123.5779 | 123.4955 | -119.2108 | -119.3207 | 123.9532 | 121.6873 | 50.2945 | 62.883
1522.2188 | 121.4813 | -61.4685 | 60.3378 | -0.089798 | 0.0063168 | 0.066464 | 0.058825 | 0.00043587 | -0.01117 | -0.0025869 | -0.049713 | 0.0040289 | 0.067268 | 0.04855 | -0.014524 | 0.024631 | -0.0047253 | -13.4537 | 59.2117 | -61.9171 | 60.3653 | -60.9879 | -61.4319 | -60.8231 | -0.42572 | 59.8526 | -61.6104 | 59.2987 | -61.5005 | -61.5372 | -61.5509 | -0.44861 | -1.1261 | 0.027465 | 0.48065 | 0.64545 | 0.036621 | 1.0941 | 0.48523 | -0.14191 | -0.48523 | -1.0391 | -0.032043 | -0.082397 | -0.068664 | 0.05951 | 0.073243 | 0.92926 | 122.2824 | 0.10986 | 120.9091 | 121.1288 | 121.463 | 120.6802 | 121.3211 | -122.2549 | -121.9482 | 121.8338 | 120.7672 | 48.0148 | 61.0428
1523.9062 | 121.5546 | -60.7315 | 60.5118 | -0.082169 | 0.0071714 | 0.066251 | 0.062243 | -0.0010595 | -0.009675 | -0.0032277 | -0.083283 | 0.0076605 | 0.067481 | 0.0556 | -0.014097 | 0.027835 | -0.0047253 | -13.765 | 59.7473 | -61.2854 | 59.9213 | -60.7681 | -60.9695 | -61.2762 | 0.92926 | 60.4843 | -60.6308 | 60.4889 | -60.8231 | -60.4248 | -60.4752 | -0.55389 | -0.76447 | -0.59052 | -0.036621 | -0.54474 | -0.23804 | 0.009155 | 0.31586 | 0.10071 | -0.027466 | -0.022888 | -0.091553 | 0.25635 | 0.3067 | 0.15564 | 0.20599 | 0.51727 | 121.2067 | -0.19226 | 121.1197 | 121.0327 | 121.1151 | 120.4788 | 121.2158 | -121.7972 | -121.1426 | 120.6528 | 121.2204 | 46.9666 | 61.6608
1525.6406 | 121.5591 | -65.0803 | 56.0349 | -0.05928 | 0.0069578 | 0.065396 | 0.062457 | 0.00064947 | -0.01117 | -0.0015189 | -0.077179 | 0.0065923 | 0.067268 | 0.049618 | -0.014097 | 0.026553 | -0.0077161 | -13.4262 | 56.6895 | -64.3936 | 56.4835 | -64.5813 | -64.9475 | -65.1535 | 1.0666 | 55.8014 | -65.3229 | 56.3873 | -65.126 | -65.2039 | -64.9979 | 0.68664 | 0.6546 | 0.44861 | 0.49896 | -0.073242 | 0.13275 | -0.75989 | -0.55389 | -0.24262 | -0.23346 | 0.35248 | -0.045777 | 0.082397 | -0.1236 | 0.32501 | 0.11902 | -0.18768 | 120.8771 | 0.19684 | 121.7102 | 121.0831 | 121.1243 | 121.7697 | 120.8817 | -120.4285 | -121.3577 | 121.5637 | 121.4676 | 51.6541 | 66.1468
1527.3281 | 121.5591 | -69.7952 | 51.3474 | -0.17372 | 0.0080258 | 0.066678 | 0.062671 | 0.0010767 | -0.0088206 | -0.0051505 | -0.028351 | 0.0029607 | 0.063636 | 0.052823 | -0.015806 | 0.025058 | -0.0025891 | -15.3534 | 53.801 | -67.218 | 52.8671 | -69.1132 | -70.1706 | -69.928 | -2.2202 | 51.297 | -70.0333 | 52.3865 | -69.136 | -69.9051 | -69.8914 | 2.5772 | 2.4536 | 1.5198 | 0.68207 | -0.13275 | -0.37537 | -2.71 | -2.9526 | -0.23804 | -0.050354 | 1.0391 | 0.65918 | -0.09613 | -0.10986 | 0.14191 | 0.12817 | -1.8951 | 120.0851 | 0.89722 | 122.4197 | 121.019 | 121.3303 | 123.5962 | 121.0922 | -118.5654 | -121.3806 | 122.6624 | 122.1817 | 54.4418 | 67.5751
1529.0781 | 121.5363 | -62.1231 | 59.0286 | -0.16609 | 0.0071714 | 0.06561 | 0.061389 | 8.47e-06 | -0.010102 | -0.00045074 | -0.086334 | 0.0059515 | 0.063423 | 0.052823 | -0.015592 | 0.026126 | -0.0036573 | -13.353 | 58.7814 | -62.3062 | 58.992 | -61.853 | -62.3291 | -62.0087 | 0.14648 | 58.9417 | -62.0636 | 59.3308 | -62.027 | -62.2467 | -62.1872 | -0.1831 | -0.24719 | -0.036621 | 0.27008 | 0.11444 | -0.20599 | 0.29755 | -0.022889 | 0.059509 | -0.086975 | 0.30213 | 0.09613 | -0.064087 | -0.1236 | -0.1236 | -0.1831 | 0.45319 | 121.2982 | 0.036621 | 121.3943 | 121.0876 | 121.0052 | 120.9045 | 121.0648 | -121.3348 | -121.0922 | 121.1151 | 121.4539 | 48.7701 | 62.2696
1530.8125 | 121.4035 | -60.1685 | 60.9695 | -0.12032 | 0.0069578 | 0.064328 | 0.060321 | -0.0038367 | -0.0075388 | -0.0038687 | -0.037506 | 0.0042425 | 0.065345 | 0.048123 | -0.014097 | 0.025485 | -0.0023755 | -11.8469 | 62.2742 | -58.9462 | 61.5097 | -59.6695 | -59.8755 | -59.7198 | -0.23804 | 61.3174 | -59.5413 | 61.6562 | -59.7839 | -60.1135 | -60.7361 | 1.2222 | 1.3046 | 0.54016 | 0.49896 | 0.44861 | 0.29297 | -0.77362 | -0.92926 | 0.62714 | 0.3479 | 0.68665 | 0.38452 | -0.56763 | 0.054932 | -1.1948 | -0.5722 | -0.72327 | 120.4559 | -0.24261 | 121.1975 | 121.2204 | 120.8588 | 122.4426 | 121.4859 | -119.9158 | -120.5109 | 121.6782 | 121.8246 | 48.3215 | 59.9304
1532.5 | 121.5317 | -0.56763 | 120.8908 | -0.12032 | 0.0067442 | 0.062192 | 0.060534 | -0.0046911 | -0.0098886 | -0.0053641 | -0.013092 | 0.0048833 | 0.064277 | 0.047909 | -0.015806 | 0.028476 | -0.0087841 | 11.6272 | 120.6848 | -0.58594 | 120.7489 | -0.28839 | -0.51727 | -0.42114 | 0.54474 | 120.6573 | -0.5722 | 120.726 | -0.36621 | -0.3891 | -0.35706 | -0.01831 | -0.20599 | -0.14191 | 0.27924 | 0.14648 | 0.050354 | 0.16479 | 0.068664 | -0.004578 | -0.23346 | -0.1648 | 0.20142 | 0.21057 | 0.17853 | 0.21515 | 0.18311 | 0.29755 | 121.3348 | 0.20599 | 121.2982 | 121.2708 | 121.2296 | 121.2524 | 121.225 | -121.4767 | -121.463 | 121.3165 | 121.2936 | 12.1948 | 1.1124
1534.25 | 121.6919 | -0.51727 | 121.0373 | -0.13557 | 0.0075986 | 0.061551 | 0.059466 | -0.0031957 | -0.0094614 | -0.0030141 | -0.013092 | 0.0048833 | 0.066413 | 0.050686 | -0.017515 | 0.026767 | -0.0051525 | 11.7462 | 120.8588 | -0.53558 | 120.9366 | -0.2243 | -0.44861 | -0.36163 | 0.49439 | 120.8267 | -0.54016 | 120.9412 | -0.27924 | -0.30212 | -0.32044 | -0.01831 | -0.17853 | -0.10071 | 0.29297 | 0.15564 | 0.068665 | 0.17395 | 0.086975 | -0.022888 | -0.21057 | -0.09613 | 0.23804 | 0.19684 | 0.21515 | 0.21973 | 0.23804 | 0.31128 | 121.4722 | 0.26093 | 121.4813 | 121.3943 | 121.3669 | 121.376 | 121.344 | -121.5729 | -121.5775 | 121.4539 | 121.4584 | 12.2635 | 1.0117
1535.9375 | 121.6095 | -0.65002 | 121.019 | -0.15846 | 0.008453 | 0.066037 | 0.063098 | -0.0012731 | -0.011598 | -0.0051505 | -0.13821 | 0.0061651 | 0.066413 | 0.047696 | -0.015165 | 0.025485 | -0.0047253 | 11.6638 | 120.8679 | -0.65918 | 120.7993 | -0.43945 | -0.65918 | -0.5722 | 0.23346 | 120.8038 | -0.65918 | 120.7901 | -0.52185 | -0.5722 | -0.48523 | -0.009156 | -0.15106 | -0.21973 | 0.21057 | 0.077819 | -0.009156 | 0.086975 | 0 | -0.009156 | -0.21515 | -0.22888 | 0.12817 | 0.1648 | 0.077819 | 0.17395 | 0.086975 | 0.21973 | 121.4584 | 0.13733 | 121.4493 | 121.5271 | 121.463 | 121.5179 | 121.4539 | -121.6782 | -121.6782 | 121.4493 | 121.4401 | 12.3138 | 0.88348
1537.625 | 121.637 | -0.6546 | 121.0236 | -0.13557 | 0.007385 | 0.063687 | 0.063525 | 8.47e-06 | -0.0071116 | -0.0051505 | -0.12601 | 0.0063787 | 0.065345 | 0.055173 | -0.013883 | 0.025058 | -0.0070751 | 11.7599 | 120.8771 | -0.66834 | 120.8313 | -0.43945 | -0.66376 | -0.59052 | 0.21057 | 120.8176 | -0.65918 | 120.8084 | -0.52643 | -0.5722 | -0.51727 | -0.013733 | -0.14648 | -0.19226 | 0.21515 | 0.064087 | -0.009155 | 0.07782 | 0.004578 | -0.004578 | -0.20599 | -0.21515 | 0.12817 | 0.13733 | 0.082397 | 0.14191 | 0.086975 | 0.22888 | 121.4996 | 0.13275 | 121.4676 | 121.5454 | 121.4767 | 121.5317 | 121.4722 | -121.6919 | -121.6827 | 121.4859 | 121.463 | 12.4146 | 0.86517
1539.3906 | 121.7697 | -0.65918 | 120.9549 | -0.097427 | 0.0054624 | 0.063687 | 0.060962 | -0.00063233 | -0.009675 | -0.0028005 | 0.014374 | 0.0042425 | 0.066413 | 0.044064 | -0.014524 | 0.025058 | -0.0060071 | 11.9797 | 120.7764 | -0.6958 | 120.8908 | -0.32044 | -0.55847 | -0.49439 | 0.46692 | 120.7352 | -0.68665 | 120.8817 | -0.4303 | -0.44403 | -0.45319 | -0.036621 | -0.17853 | -0.064087 | 0.33874 | 0.16479 | 0.10071 | 0.20142 | 0.13733 | -0.027466 | -0.21973 | -0.073242 | 0.22888 | 0.20599 | 0.21515 | 0.23346 | 0.24261 | 0.37537 | 121.5866 | 0.25635 | 121.5683 | 121.4722 | 121.4218 | 121.4355 | 121.3943 | -121.6507 | -121.6415 | 121.55 | 121.5408 | 12.6389 | 1.1261
1541.1406 | 121.8292 | -5.7495 | 115.6952 | -0.12794 | 0.005676 | 0.064756 | 0.061389 | -0.00063233 | -0.010743 | -0.0032277 | 0.011322 | 0.0042425 | 0.065132 | 0.047696 | -0.014951 | 0.025699 | -0.0049389 | 9.7183 | 115.5533 | -5.8594 | 115.7547 | -5.4382 | -5.69 | -5.6168 | 0.58594 | 115.5624 | -5.777 | 115.7089 | -5.4932 | -5.5847 | -5.5984 | -0.10986 | -0.14191 | 0.05951 | 0.31128 | 0.13275 | 0.05951 | 0.24261 | 0.16937 | -0.027466 | -0.13275 | 0.013733 | 0.25635 | 0.15106 | 0.16479 | 0.17853 | 0.19226 | 0.42114 | 121.6141 | 0.28381 | 121.4859 | 121.4127 | 121.3394 | 121.3028 | 121.312 | -121.5546 | -121.4722 | 121.5042 | 121.4584 | 15.4678 | 6.3354
1542.8438 | 121.8155 | -7.37 | 114.1708 | -0.082169 | 0.0054624 | 0.064542 | 0.057544 | -0.0025549 | -0.010957 | -0.0030141 | -0.037506 | 0.0053107 | 0.065986 | 0.053677 | -0.015379 | 0.025485 | -0.0068615 | 8.9401 | 114.0427 | -7.3654 | 114.1251 | -7.0724 | -7.3517 | -7.283 | 0.12817 | 113.9648 | -7.4112 | 114.1388 | -7.196 | -7.2418 | -7.2327 | 0.004578 | -0.12817 | -0.045776 | 0.29755 | 0.086975 | 0.01831 | 0.082397 | 0.013732 | -0.041199 | -0.20599 | -0.032043 | 0.17395 | 0.13733 | 0.12817 | 0.17853 | 0.16937 | 0.29297 | 121.4905 | 0.21515 | 121.55 | 121.4081 | 121.376 | 121.4127 | 121.3348 | -121.5363 | -121.582 | 121.4951 | 121.5088 | 16.3101 | 7.4982
1544.6094 | 121.6782 | -1.3962 | 120.2499 | -0.10506 | 0.0080258 | 0.06561 | 0.064166 | 0.0025721 | -0.0094614 | 0.00061746 | -0.1138 | 0.0080877 | 0.064918 | 0.052823 | -0.016233 | 0.028049 | -0.0077161 | 12.0255 | 120.0439 | -1.4557 | 120.1172 | -1.1124 | -1.3504 | -1.2863 | 0.3891 | 120.0623 | -1.3962 | 120.0989 | -1.2314 | -1.2863 | -1.2039 | -0.059509 | -0.20599 | -0.13275 | 0.28381 | 0.10986 | 0.045776 | 0.16937 | 0.10529 | 0 | -0.18768 | -0.15106 | 0.1648 | 0.19226 | 0.10986 | 0.19226 | 0.10986 | 0.34332 | 121.5729 | 0.1648 | 121.4951 | 121.4996 | 121.4584 | 121.4401 | 121.4584 | -121.7056 | -121.6461 | 121.5134 | 121.4951 | 13.4216 | 1.7853
1546.3438 | 121.7422 | -1.7532 | 119.8654 | -0.10506 | 0.0061032 | 0.065824 | 0.062671 | -0.0031957 | -0.0077524 | -0.0028005 | -0.034454 | 0.0059515 | 0.067054 | 0.046841 | -0.013456 | 0.027408 | -0.0064343 | 11.9934 | 119.7327 | -1.7258 | 119.7876 | -1.4191 | -1.6937 | -1.593 | 0.2655 | 119.6823 | -1.7715 | 119.7647 | -1.5701 | -1.6022 | -1.5701 | 0.027466 | -0.13275 | -0.077819 | 0.33417 | 0.16022 | 0.059509 | 0.13275 | 0.032043 | -0.01831 | -0.1831 | -0.10071 | 0.18311 | 0.18311 | 0.15106 | 0.20142 | 0.16937 | 0.3067 | 121.5134 | 0.20142 | 121.5363 | 121.4584 | 121.4539 | 121.4859 | 121.4355 | -121.5912 | -121.637 | 121.5408 | 121.5179 | 13.7466 | 2.0187
1548.0938 | 121.6141 | -8.812 | 113.8321 | -0.19661 | 0.0065304 | 0.062192 | 0.062457 | 0.0019311 | -0.010316 | -0.00087794 | -0.074127 | 0.0033881 | 0.066413 | 0.059018 | -0.014738 | 0.025058 | -0.0034435 | 7.4799 | 111.438 | -9.8282 | 111.9873 | -9.0683 | -9.2331 | -8.8989 | 0.018311 | 111.8454 | -9.3246 | 112.1017 | -8.9264 | -8.8165 | -8.551 | -1.0162 | -2.3941 | -1.8448 | -0.25635 | -0.086975 | -0.42114 | 0.92926 | 0.59509 | -0.51269 | -1.9867 | -1.7303 | -0.11444 | 0.26093 | -0.004577 | 0.77362 | 0.50812 | 0.75989 | 121.8155 | 0.39825 | 121.4264 | 121.2662 | 121.17 | 120.2499 | 120.6573 | -123.6603 | -123.1567 | 120.7993 | 120.9137 | 16.2918 | 8.8303
1549.7812 | 121.6599 | -12.0895 | 109.4421 | -0.097427 | 0.0052488 | 0.065824 | 0.059253 | 0.0012903 | -0.0092478 | -0.0021597 | -0.0039367 | 0.0061651 | 0.065986 | 0.046414 | -0.015165 | 0.027194 | -0.0055799 | 6.0516 | 109.3231 | -11.9705 | 110.1334 | -11.8561 | -12.2131 | -12.2452 | -1.1536 | 108.8699 | -12.4558 | 109.0805 | -12.0804 | -12.0895 | -11.5402 | 0.11902 | -0.11902 | 0.69122 | 0.23346 | -0.15564 | -0.1236 | -0.27466 | -0.24261 | -0.36621 | -0.5722 | -0.36163 | 0.009156 | 0.54932 | 0 | 0.91553 | 0.36621 | 0.11444 | 122.1039 | 0.37537 | 121.5363 | 121.2936 | 121.3257 | 121.4127 | 120.9595 | -121.4127 | -121.8979 | 122.2229 | 121.17 | 18.1412 | 10.936
1551.5156 | 121.6507 | -1.7258 | 119.7922 | -0.12032 | 0.0071714 | 0.06561 | 0.061602 | -0.0038367 | -0.010316 | 0.0012583 | -0.037506 | 0.0038153 | 0.064704 | 0.046414 | -0.01602 | 0.026767 | -0.0068615 | 12.3184 | 119.6228 | -1.8173 | 119.7556 | -1.3687 | -1.6663 | -1.6479 | 0.45319 | 119.6411 | -1.7212 | 119.5312 | -1.9226 | -1.6525 | -1.5106 | -0.091553 | -0.16937 | -0.036621 | 0.35706 | 0.07782 | 0.059509 | 0.16937 | 0.15106 | 0.004578 | -0.15106 | -0.26093 | -0.19684 | 0.21515 | 0.073242 | 0.21057 | 0.068664 | 0.44861 | 121.5729 | -0.20142 | 121.2524 | 121.4401 | 121.3623 | 121.3486 | 121.3669 | -121.6095 | -121.5134 | 121.4813 | 121.257 | 14.0442 | 2.179
1553.2656 | 121.6049 | -0.5127 | 121.1288 | -0.082169 | 0.0075986 | 0.065183 | 0.062884 | 0.00022207 | -0.01117 | -0.0017325 | -0.089386 | 0.0061651 | 0.067054 | 0.057095 | -0.014524 | 0.023563 | -0.0062207 | 13.2019 | 120.9915 | -0.4715 | 120.932 | -0.23346 | -0.46692 | -0.39825 | 0.55389 | 120.9229 | -0.53558 | 120.9 | -0.3891 | -0.36163 | -0.36621 | 0.041198 | -0.13733 | -0.19684 | 0.27924 | 0.11444 | 0.045776 | 0.073243 | 0.004578 | -0.022888 | -0.20599 | -0.22888 | 0.1236 | 0.14648 | 0.15106 | 0.16937 | 0.17395 | 0.23804 | 121.4035 | 0.14648 | 121.4355 | 121.463 | 121.4584 | 121.5042 | 121.4355 | -121.6003 | -121.6644 | 121.4447 | 121.4127 | 13.7146 | 1.0666
1554.9688 | 121.6232 | -0.48981 | 121.1655 | -0.097427 | 0.009094 | 0.064969 | 0.063739 | -0.0021277 | -0.009675 | -0.0032277 | -0.1077 | 0.0063787 | 0.067054 | 0.054532 | -0.013883 | 0.026553 | -0.0034435 | 13.1195 | 121.0648 | -0.49439 | 121.0007 | -0.24261 | -0.49896 | -0.4303 | 0.19684 | 120.9732 | -0.49896 | 120.9641 | -0.3891 | -0.45319 | -0.37537 | -0.004578 | -0.10071 | -0.16479 | 0.24719 | 0.059509 | -0.009155 | 0.064087 | -0.004577 | -0.009155 | -0.19226 | -0.20142 | 0.10071 | 0.11444 | 0.036621 | 0.1236 | 0.045776 | 0.25177 | 121.4951 | 0.10986 | 121.463 | 121.5591 | 121.4722 | 121.5546 | 121.463 | -121.6599 | -121.6644 | 121.4905 | 121.4539 | 13.6093 | 0.68664
1556.7188 | 121.6461 | -0.62256 | 121.0236 | -0.12794 | 0.0063168 | 0.065183 | 0.064166 | 0.0025721 | -0.0075388 | 0.00040366 | -0.13516 | 0.0089423 | 0.062782 | 0.057736 | -0.015806 | 0.027621 | -0.0057935 | 13.0737 | 120.9641 | -0.62256 | 120.8908 | -0.36621 | -0.66376 | -0.56763 | 0.16479 | 120.9 | -0.62714 | 120.8633 | -0.53558 | -0.63629 | -0.55389 | 0 | -0.05951 | -0.13275 | 0.25635 | 0.054932 | -0.041198 | 0.054932 | -0.041198 | -0.004577 | -0.1236 | -0.16022 | 0.086976 | 0.068665 | -0.013733 | 0.073242 | -0.009156 | 0.25635 | 121.5134 | 0.091553 | 121.4905 | 121.5866 | 121.5271 | 121.5866 | 121.5225 | -121.6461 | -121.6507 | 121.5134 | 121.4859 | 13.6963 | 0.78735
1558.4844 | 121.6599 | -0.64545 | 121.0739 | -0.05928 | 0.0043942 | 0.06326 | 0.060534 | -0.0010595 | -0.009675 | -0.0023733 | -0.040558 | 0.0059515 | 0.065132 | 0.048337 | -0.014738 | 0.025699 | -0.0055799 | 13.2202 | 120.8954 | -0.65002 | 120.8542 | -0.34332 | -0.58136 | -0.54016 | 0.33417 | 120.845 | -0.64087 | 120.8176 | -0.50812 | -0.52643 | -0.5127 | -0.004577 | -0.17853 | -0.21973 | 0.30212 | 0.10529 | 0.064087 | 0.10986 | 0.068664 | 0.004578 | -0.22888 | -0.25635 | 0.13733 | 0.13275 | 0.11902 | 0.12817 | 0.11444 | 0.3067 | 121.5042 | 0.13275 | 121.4584 | 121.5454 | 121.4859 | 121.5408 | 121.4905 | -121.7239 | -121.7148 | 121.4996 | 121.463 | 13.8657 | 0.97961
1560.25 | 121.6278 | -3.9688 | 117.7917 | -0.12032 | 0.0061032 | 0.063901 | 0.060748 | -0.00063233 | -0.0092478 | -0.0013051 | -0.013092 | 0.0080877 | 0.062995 | 0.053677 | -0.014311 | 0.025699 | -0.00066651 | 12.2314 | 118.3319 | -3.2867 | 117.9382 | -3.2867 | -3.4515 | -3.479 | 0.15106 | 117.7277 | -3.7399 | 117.4667 | -3.7628 | -3.7674 | -3.717 | 0.68207 | 0.54016 | 0.14648 | 0.68207 | 0.48981 | 0.51727 | -0.19226 | -0.1648 | 0.22888 | -0.064087 | -0.32501 | 0.20599 | 0.25177 | 0.20142 | 0.022888 | -0.027466 | 0 | 121.225 | -0.022888 | 121.2067 | 121.6187 | 121.4676 | 122.3007 | 121.6965 | -121.0785 | -121.5317 | 121.907 | 121.4355 | 16.2003 | 4.1199
1561.9531 | 121.6919 | -3.0029 | 118.5974 | -0.10506 | 0.0075986 | 0.062406 | 0.064166 | -0.0010595 | -0.0081796 | -0.0013051 | -0.12296 | 0.0080877 | 0.065772 | 0.050686 | -0.01367 | 0.028262 | -0.00088011 | 12.0895 | 118.6569 | -2.8931 | 118.6523 | -2.5269 | -2.8381 | -2.7695 | 0.24719 | 118.6478 | -2.829 | 118.4463 | -2.8885 | -2.9526 | -2.9068 | 0.10986 | 0.059509 | 0.054932 | 0.47608 | 0.23346 | 0.1648 | 0.1236 | 0.054931 | 0.17395 | 0.050354 | -0.15106 | 0.11444 | 0.096131 | 0.050354 | -0.07782 | -0.1236 | 0.36621 | 121.5454 | -0.05951 | 121.2753 | 121.55 | 121.4767 | 121.6599 | 121.6507 | -121.4905 | -121.4264 | 121.6553 | 121.4493 | 15.0925 | 3.2501
1563.7031 | 121.7056 | -5.4016 | 116.2125 | -0.12032 | 0.008453 | 0.064756 | 0.062671 | -0.0027685 | -0.0081796 | -0.0019461 | -0.098541 | 0.0057379 | 0.064704 | 0.051968 | -0.013242 | 0.026767 | -0.0064343 | 10.5194 | 116.098 | -5.4291 | 115.8554 | -5.4062 | -5.6808 | -5.5527 | -0.28839 | 115.8417 | -5.6213 | 116.066 | -5.3238 | -5.3284 | -5.3329 | -0.027466 | -0.11444 | -0.35706 | -0.004578 | -0.15106 | -0.27924 | -0.1236 | -0.25177 | -0.21973 | -0.37079 | -0.14648 | 0.077819 | 0.068664 | 0.073242 | 0.28839 | 0.29297 | 0.022888 | 121.2845 | 0.29755 | 121.6873 | 121.5271 | 121.463 | 121.4996 | 121.2433 | -121.6415 | -121.8338 | 121.257 | 121.4676 | 15.921 | 5.1132
1565.4688 | 121.6827 | -1.6388 | 120.0348 | -0.15846 | 0.0078122 | 0.064328 | 0.063525 | 0.0017175 | -0.006898 | -0.0021597 | -0.1077 | 0.0063787 | 0.065559 | 0.047909 | -0.015806 | 0.027835 | -0.0098523 | 12.1811 | 119.046 | -2.3758 | 119.2474 | -1.9867 | -2.243 | -1.9958 | 0.1831 | 119.1971 | -2.2339 | 119.9661 | -1.3733 | -1.4557 | -1.4236 | -0.737 | -0.98877 | -0.78735 | -0.3479 | -0.35706 | -0.60425 | 0.37994 | 0.13275 | -0.59509 | -0.83771 | -0.068665 | 0.2655 | 0.21515 | 0.18311 | 0.81024 | 0.7782 | 0.3891 | 121.6232 | 0.8606 | 122.2 | 121.4218 | 121.431 | 120.6848 | 120.8359 | -122.4106 | -122.2687 | 120.8862 | 121.6049 | 13.8199 | 1.8219
1567.2188 | 121.6599 | -16.713 | 104.6539 | -0.18135 | 0.0075986 | 0.065824 | 0.060534 | -0.0017005 | -0.0092478 | -0.0038687 | -0.028351 | 0.0044561 | 0.064491 | 0.047482 | -0.013029 | 0.025272 | -0.0042981 | 3.3875 | 104.5212 | -16.7358 | 104.6173 | -16.5115 | -16.8961 | -16.8228 | -0.9613 | 104.4983 | -16.7496 | 104.599 | -16.7313 | -16.8137 | -16.8091 | -0.022888 | -0.13275 | -0.036621 | 0.20142 | -0.10986 | -0.1831 | -0.086975 | -0.16022 | -0.036621 | -0.15564 | -0.054932 | -0.01831 | -0.09613 | -0.10071 | -0.059509 | -0.064087 | 0.2243 | 121.3531 | 0.018311 | 121.3486 | 121.257 | 121.2479 | 121.2341 | 121.2112 | -121.3898 | -121.4035 | 121.3303 | 121.312 | 20.1004 | 15.7516
1568.9688 | 121.6873 | -3.2043 | 118.4052 | -0.097427 | 0.0065304 | 0.06326 | 0.06502 | -0.0057593 | -0.0092478 | -0.0023733 | -0.064972 | 0.0078741 | 0.06385 | 0.051541 | -0.016233 | 0.026553 | -0.0053661 | 11.9705 | 118.2404 | -3.2272 | 118.19 | -2.9572 | -3.1906 | -3.1174 | 0.18768 | 118.1992 | -3.2364 | 118.2404 | -3.035 | -3.0899 | -3.0533 | -0.022888 | -0.16479 | -0.21515 | 0.24719 | 0.086975 | 0.013733 | 0.10986 | 0.036621 | -0.032043 | -0.20599 | -0.16479 | 0.16937 | 0.15106 | 0.11444 | 0.1831 | 0.14648 | 0.27008 | 121.4172 | 0.20142 | 121.4767 | 121.4676 | 121.4355 | 121.4447 | 121.4035 | -121.6324 | -121.6415 | 121.3943 | 121.4447 | 15.1749 | 3.392
1570.6562 | 121.6278 | -5.7999 | 115.741 | -0.05928 | 0.0082394 | 0.063474 | 0.062671 | 0.0012903 | -0.0094614 | -0.0021597 | -0.086334 | 0.0061651 | 0.064277 | 0.051114 | -0.015592 | 0.027408 | -0.0017347 | 9.9747 | 115.4114 | -5.9647 | 115.4343 | -5.6351 | -5.8685 | -5.8319 | -0.15564 | 115.5029 | -5.8365 | 115.5441 | -5.7587 | -5.7724 | -5.6534 | -0.1648 | -0.32959 | -0.3067 | 0.16479 | -0.032043 | -0.068664 | 0.13275 | 0.096131 | -0.036621 | -0.23804 | -0.19684 | 0.041199 | 0.14648 | 0.027466 | 0.18311 | 0.064087 | 0.32959 | 121.3989 | 0.07782 | 121.3806 | 121.376 | 121.3394 | 121.2112 | 121.3028 | -121.7056 | -121.5775 | 121.2341 | 121.344 | 15.7745 | 5.6442
1572.4062 | 121.6507 | -9.1461 | 112.1933 | -0.17372 | 0.0067442 | 0.065396 | 0.062457 | -0.0038367 | -0.0098886 | -0.0032277 | 0.0021667 | 0.0033881 | 0.066413 | 0.047482 | -0.013456 | 0.024844 | -0.0045117 | 8.6014 | 112.3947 | -9.0363 | 112.2757 | -8.6792 | -9.0912 | -9.0729 | -0.15106 | 112.0148 | -9.1919 | 112.1658 | -9.0134 | -8.9996 | -9.1324 | 0.10986 | 0.20142 | 0.082398 | 0.46692 | 0.073242 | 0.054931 | -0.036621 | -0.054932 | -0.045777 | -0.17853 | -0.027465 | 0.13275 | 0.013733 | 0.14648 | 0.05951 | 0.19226 | 0.35706 | 121.312 | 0.17853 | 121.3577 | 121.431 | 121.2067 | 121.5408 | 121.1609 | -121.2296 | -121.3852 | 121.4218 | 121.312 | 17.7475 | 8.9951
1574.1719 | 121.5775 | -1.6708 | 119.9295 | -0.05928 | 0.0099484 | 0.064542 | 0.062671 | -0.0034095 | -0.008607 | -0.0030141 | -0.089386 | 0.0050971 | 0.065559 | 0.055386 | -0.014097 | 0.026767 | -0.0045117 | 13.0875 | 119.7601 | -1.6846 | 119.751 | -1.2955 | -1.6296 | -1.5884 | 0.29297 | 119.6823 | -1.7029 | 119.751 | -1.474 | -1.5472 | -1.5106 | -0.013733 | -0.16937 | -0.17853 | 0.37537 | 0.082397 | 0.041198 | 0.09613 | 0.054931 | -0.032044 | -0.24719 | -0.17853 | 0.19684 | 0.16022 | 0.1236 | 0.19226 | 0.15564 | 0.3891 | 121.4355 | 0.22888 | 121.4539 | 121.4447 | 121.3852 | 121.431 | 121.3531 | -121.6141 | -121.6324 | 121.4218 | 121.4218 | 14.7583 | 1.9638
1575.8594 | 121.6415 | -1.3367 | 120.2911 | -0.089798 | 0.0088804 | 0.066037 | 0.063739 | 0.0040675 | -0.0073252 | -0.0023733 | -0.092438 | 0.0085149 | 0.065986 | 0.056881 | -0.014524 | 0.025699 | -0.0038709 | 13.3759 | 120.2133 | -1.2955 | 120.0943 | -1.0254 | -1.3138 | -1.2543 | 0.20142 | 120.1218 | -1.3138 | 120.0851 | -1.236 | -1.2543 | -1.1993 | 0.041199 | -0.07782 | -0.19684 | 0.31128 | 0.082398 | 0.022888 | 0.041199 | -0.018311 | 0.022888 | -0.16937 | -0.20599 | 0.10071 | 0.13733 | 0.082398 | 0.11444 | 0.05951 | 0.27008 | 121.3898 | 0.07782 | 121.3989 | 121.5088 | 121.4355 | 121.55 | 121.4584 | -121.5866 | -121.6049 | 121.431 | 121.4218 | 14.7125 | 1.5381
1577.6094 | 121.7194 | -1.0712 | 120.6482 | -0.13557 | 0.0088804 | 0.063901 | 0.064166 | 0.0012903 | -0.010102 | -0.0010915 | -0.09549 | 0.0074469 | 0.066413 | 0.050046 | -0.015592 | 0.029117 | -0.0019483 | 13.5086 | 120.2087 | -1.3641 | 119.8105 | -1.3 | -1.5518 | -1.3046 | 0.78278 | 120.0577 | -1.4145 | 120.5475 | -0.75531 | -0.93842 | -0.93842 | -0.29297 | -0.43945 | -0.83771 | -0.22888 | -0.23346 | -0.48065 | 0.05951 | -0.18768 | -0.34332 | -0.59052 | -0.10071 | 0.31586 | 0.13275 | 0.13275 | 0.47607 | 0.47607 | 0.064087 | 121.1746 | 0.65918 | 121.962 | 121.5729 | 121.4722 | 121.2799 | 121.1288 | -122.0123 | -122.0627 | 120.8817 | 121.6187 | 14.5798 | 1.8539
1579.3594 | 121.701 | -9.7458 | 111.7355 | -0.10506 | 0.0037534 | 0.065183 | 0.060748 | 0.0017175 | -0.012452 | -0.0038687 | 0.023529 | 0.0046697 | 0.065345 | 0.050046 | -0.014951 | 0.026126 | -0.0040845 | 8.194 | 111.8362 | -9.5078 | 111.7126 | -9.3018 | -9.6268 | -9.6176 | 0.027466 | 111.6074 | -9.6634 | 111.5662 | -9.9106 | -9.6863 | -9.4757 | 0.23804 | 0.10071 | -0.022889 | 0.44403 | 0.12817 | 0.11902 | -0.10986 | -0.11902 | 0.082398 | -0.12817 | -0.16937 | -0.16479 | 0.27008 | 0.05951 | 0.18768 | -0.022888 | 0.20599 | 121.2204 | -0.24719 | 121.2296 | 121.344 | 121.2708 | 121.582 | 121.3531 | -121.2433 | -121.3989 | 121.4584 | 121.312 | 17.9398 | 9.7733
1581.1094 | 121.5866 | -12.8448 | 108.4396 | -0.082169 | 0.007385 | 0.066464 | 0.06438 | 0.00086307 | -0.0073252 | -0.0030141 | -0.080231 | 0.0059515 | 0.062995 | 0.048764 | -0.014311 | 0.025058 | -0.0013073 | 6.2668 | 108.5175 | -12.8311 | 107.9819 | -13.1332 | -13.3163 | -13.2706 | -0.37079 | 107.9865 | -13.2111 | 108.2703 | -12.8265 | -12.7853 | -12.767 | 0.013733 | 0.07782 | -0.45776 | -0.28839 | -0.42572 | -0.4715 | -0.43945 | -0.48523 | -0.36621 | -0.45319 | -0.16937 | 0.018311 | 0.07782 | 0.05951 | 0.44403 | 0.42572 | -0.30212 | 120.813 | 0.38452 | 121.4813 | 121.3486 | 121.1975 | 121.3623 | 120.8313 | -121.2708 | -121.6507 | 120.8267 | 121.1151 | 19.1116 | 12.4741
1582.7969 | 121.5088 | -13.5132 | 107.9407 | -0.15083 | 0.0061032 | 0.06326 | 0.059039 | -0.00063233 | -0.0094614 | -0.0030141 | -0.0069885 | 0.0063787 | 0.062141 | 0.048123 | -0.013029 | 0.026126 | -0.0060071 | 6.3171 | 108.7234 | -12.3871 | 108.989 | -11.9751 | -12.3917 | -12.3322 | -0.027466 | 108.5587 | -12.561 | 107.5378 | -13.7421 | -13.71 | -13.559 | 1.1261 | 0.78278 | 1.0483 | 1.5381 | 1.181 | 1.1215 | 0.054932 | -0.004578 | 0.95215 | 0.61798 | -0.40283 | -0.22888 | -0.045776 | -0.19684 | -0.99793 | -1.149 | 0.41199 | 121.376 | -1.181 | 120.0989 | 121.1105 | 121.1197 | 122.2366 | 122.0718 | -120.3278 | -120.5017 | 122.5021 | 121.051 | 19.8303 | 13.4857
1584.5469 | 121.3211 | -20.1553 | 100.9094 | -0.16609 | 0.0075986 | 0.063687 | 0.061602 | 0.00086307 | -0.009675 | -0.0023733 | -0.0008851 | 0.0053107 | 0.065345 | 0.048337 | -0.016233 | 0.027835 | -0.0047253 | 1.1536 | 100.708 | -20.2011 | 100.8545 | -19.9402 | -20.2469 | -20.224 | 0.81024 | 100.7401 | -20.137 | 100.708 | -20.2423 | -20.2515 | -20.1416 | -0.045777 | -0.20142 | -0.054932 | 0.21515 | -0.068665 | -0.091553 | -0.022888 | -0.045776 | 0.01831 | -0.16937 | -0.20142 | -0.086976 | 0.013732 | -0.096131 | -0.004578 | -0.11444 | 0.26093 | 121.0556 | -0.10529 | 120.845 | 120.9091 | 120.8771 | 120.8633 | 120.8954 | -121.1105 | -121.0464 | 121.0098 | 120.8633 | 21.3089 | 20.9656
1586.2969 | 121.1426 | -17.3264 | 103.6606 | -0.10506 | 0.009094 | 0.064542 | 0.064166 | 0.00043587 | -0.0081796 | -0.00045074 | -0.098541 | 0.0065923 | 0.063636 | 0.047696 | -0.015592 | 0.027835 | -0.0049389 | 2.7786 | 103.093 | -17.8848 | 103.4637 | -17.1432 | -17.6331 | -17.6788 | -0.086975 | 103.1067 | -17.7521 | 103.4317 | -17.4774 | -17.3584 | -17.363 | -0.55847 | -0.56763 | -0.19684 | 0.18311 | -0.35248 | -0.3067 | 0.20599 | 0.25177 | -0.42572 | -0.55389 | -0.22888 | -0.15106 | -0.036621 | -0.032043 | 0.3891 | 0.39368 | 0.74158 | 121.3486 | 0.27466 | 121.1838 | 120.9778 | 120.8588 | 120.4193 | 120.433 | -121.5454 | -121.4127 | 120.7901 | 120.7581 | 20.105 | 17.2394
1587.9844 | 121.5088 | -0.19684 | 121.2524 | -0.11269 | 0.0080258 | 0.063901 | 0.05968 | -0.0031957 | -0.0090342 | -0.0013051 | -0.0039367 | 0.0050971 | 0.064277 | 0.042782 | -0.014097 | 0.025912 | -0.0045117 | 14.8911 | 121.0922 | -0.16479 | 121.1197 | 0.23804 | -0.10071 | -0.013733 | 0.29755 | 121.0144 | -0.19684 | 121.1105 | -0.009155 | -0.050354 | 0.009155 | 0.032043 | -0.16022 | -0.13275 | 0.43488 | 0.18311 | 0.09613 | 0.15106 | 0.064087 | 0 | -0.23804 | -0.14191 | 0.18768 | 0.20599 | 0.14648 | 0.20599 | 0.14648 | 0.40283 | 121.2845 | 0.18768 | 121.3074 | 121.257 | 121.2112 | 121.2891 | 121.2112 | -121.4172 | -121.4493 | 121.3165 | 121.3074 | 15.0879 | 0.49438
1589.7344 | 121.5546 | -0.21515 | 121.3623 | -0.11269 | 0.010376 | 0.064756 | 0.063952 | 0.0012903 | -0.01053 | 0.00019006 | -0.10159 | 0.0057379 | 0.063423 | 0.056027 | -0.015379 | 0.026767 | -0.0064343 | 15.1566 | 121.2021 | -0.19226 | 121.1929 | 0.23346 | -0.09613 | -0.045776 | 0.35248 | 121.1288 | -0.19226 | 121.1838 | -0.027466 | -0.07782 | -0.022888 | 0.022888 | -0.16022 | -0.16937 | 0.44861 | 0.16937 | 0.11902 | 0.14648 | 0.096131 | 0.022888 | -0.23346 | -0.17853 | 0.18768 | 0.19226 | 0.13733 | 0.16937 | 0.11444 | 0.42572 | 121.3852 | 0.16479 | 121.376 | 121.3943 | 121.3211 | 121.4172 | 121.344 | -121.5546 | -121.5546 | 121.4081 | 121.3989 | 15.3717 | 0.56763
1591.4219 | 121.6141 | -0.20599 | 121.3898 | -0.15083 | 0.0050352 | 0.06561 | 0.060748 | 0.0010767 | -0.0075388 | -0.0028005 | -0.025299 | 0.0048833 | 0.065559 | 0.050259 | -0.012602 | 0.02634 | -0.0032299 | 15.4999 | 121.1975 | -0.19226 | 121.2708 | 0.31586 | -0.036621 | 0.022888 | 0.42572 | 121.1609 | -0.19226 | 121.1975 | -0.009155 | -0.032043 | -0.018311 | 0.013733 | -0.19226 | -0.11902 | 0.52185 | 0.22888 | 0.16937 | 0.21515 | 0.15564 | 0.013733 | -0.22888 | -0.19226 | 0.19684 | 0.18768 | 0.17395 | 0.17395 | 0.16022 | 0.50812 | 121.463 | 0.18311 | 121.3898 | 121.3898 | 121.3531 | 121.4035 | 121.3669 | -121.582 | -121.582 | 121.4767 | 121.4035 | 15.7059 | 0.63171
1593.1562 | 121.5958 | -0.22888 | 121.376 | -0.12794 | 0.0063168 | 0.067746 | 0.062884 | -0.0046911 | -0.0092478 | -0.0023733 | -0.083283 | 0.0061651 | 0.064491 | 0.052395 | -0.014524 | 0.026981 | -0.0064343 | 15.5594 | 121.2753 | -0.23804 | 121.1517 | 0.15106 | -0.2243 | -0.11444 | 0.14648 | 121.1884 | -0.23346 | 121.1563 | -0.10071 | -0.15106 | -0.082397 | -0.009155 | -0.10071 | -0.22431 | 0.37994 | 0.11444 | 0.004578 | 0.1236 | 0.013733 | -0.004577 | -0.18768 | -0.21973 | 0.12817 | 0.14649 | 0.07782 | 0.15106 | 0.082397 | 0.3891 | 121.3898 | 0.13275 | 121.3898 | 121.5134 | 121.4218 | 121.5042 | 121.4172 | -121.6141 | -121.6095 | 121.3806 | 121.3852 | 15.7883 | 0.37537
1594.9062 | 121.5866 | -0.24261 | 121.4172 | -0.11269 | 0.0080258 | 0.066678 | 0.062457 | 0.0010767 | -0.0092478 | -0.00087794 | -0.10159 | 0.0065923 | 0.065772 | 0.054104 | -0.014097 | 0.026981 | -0.0015209 | 15.8066 | 121.2891 | -0.21515 | 121.1884 | 0.16937 | -0.20142 | -0.12817 | 0.16479 | 121.2296 | -0.24261 | 121.1609 | -0.1236 | -0.19226 | -0.10529 | 0.027466 | -0.12817 | -0.22888 | 0.41199 | 0.11444 | 0.041199 | 0.086975 | 0.013733 | 0 | -0.18768 | -0.25635 | 0.11902 | 0.13733 | 0.050354 | 0.13733 | 0.050354 | 0.38452 | 121.4035 | 0.11902 | 121.4035 | 121.5042 | 121.4722 | 121.5317 | 121.4722 | -121.6324 | -121.6599 | 121.431 | 121.4035 | 16.0492 | 0.40741
1596.6562 | 121.6553 | -0.23346 | 121.376 | -0.13557 | 0.0075986 | 0.067105 | 0.062243 | -0.0010595 | -0.010316 | -0.0036551 | -0.055817 | 0.0036017 | 0.065986 | 0.048764 | -0.012174 | 0.028262 | -0.00066651 | 15.976 | 121.2982 | -0.21973 | 121.1929 | 0.20142 | -0.19684 | -0.1236 | 0.15564 | 121.1838 | -0.25177 | 121.2067 | -0.10071 | -0.15106 | -0.086975 | 0.013732 | -0.07782 | -0.18311 | 0.43488 | 0.10986 | 0.036621 | 0.096131 | 0.022889 | -0.018311 | -0.19226 | -0.16937 | 0.13275 | 0.14648 | 0.082397 | 0.16479 | 0.10071 | 0.42114 | 121.4127 | 0.15106 | 121.4584 | 121.5179 | 121.4355 | 121.5317 | 121.4172 | -121.5958 | -121.6278 | 121.4264 | 121.4401 | 16.2094 | 0.3891
1598.4062 | 121.6278 | -0.25635 | 121.4218 | -0.05928 | 0.0050352 | 0.063901 | 0.06203 | -0.0031957 | -0.01117 | 0.00061746 | -0.019196 | 0.0042425 | 0.064491 | 0.049832 | -0.014097 | 0.025485 | -0.0040845 | 16.3147 | 121.2708 | -0.24719 | 121.1884 | 0.20142 | -0.16479 | -0.11444 | 0.28381 | 121.2387 | -0.24719 | 121.1792 | -0.1236 | -0.13733 | -0.10986 | 0.009156 | -0.15106 | -0.23346 | 0.45776 | 0.14191 | 0.091553 | 0.13275 | 0.082397 | 0.009156 | -0.18311 | -0.24262 | 0.13275 | 0.14649 | 0.11902 | 0.13733 | 0.10986 | 0.44861 | 121.4355 | 0.1236 | 121.4264 | 121.5179 | 121.4859 | 121.5271 | 121.4951 | -121.669 | -121.669 | 121.4447 | 121.4355 | 16.571 | 0.54016
1600.1562 | 121.6736 | -0.2243 | 121.431 | -0.089798 | 0.0058896 | 0.063901 | 0.061602 | -0.00063233 | -0.01053 | -0.0010915 | -0.046661 | 0.0044561 | 0.06385 | 0.051541 | -0.014097 | 0.026767 | -0.0032299 | 16.7358 | 121.2982 | -0.25177 | 121.1975 | 0.2243 | -0.16937 | -0.10986 | 0.27924 | 121.2479 | -0.27008 | 121.2112 | -0.09613 | -0.15106 | -0.10529 | -0.027466 | -0.13275 | -0.23346 | 0.44861 | 0.11444 | 0.054931 | 0.14191 | 0.082397 | -0.045777 | -0.1831 | -0.21973 | 0.12817 | 0.11902 | 0.073242 | 0.1648 | 0.11902 | 0.47607 | 121.4493 | 0.17395 | 121.4813 | 121.55 | 121.5179 | 121.5225 | 121.4722 | -121.6827 | -121.7011 | 121.4218 | 121.4355 | 16.9601 | 0.50354
1601.8438 | 121.7789 | -0.21973 | 121.376 | -0.089798 | 0.0067442 | 0.064969 | 0.060107 | -0.0038367 | -0.010316 | -0.0021597 | 0.023529 | 0.0025335 | 0.064277 | 0.045346 | -0.013456 | 0.025272 | -0.0068615 | 17.0654 | 121.257 | -0.2243 | 121.2616 | 0.32044 | -0.10529 | -0.013733 | 0.29755 | 121.2021 | -0.23346 | 121.2936 | 0.009155 | -0.018311 | -0.004578 | -0.004577 | -0.11902 | -0.11444 | 0.54016 | 0.20599 | 0.11444 | 0.21057 | 0.11902 | -0.013732 | -0.17395 | -0.082398 | 0.22888 | 0.21515 | 0.20142 | 0.22888 | 0.21515 | 0.54474 | 121.4859 | 0.24261 | 121.5271 | 121.4813 | 121.4355 | 121.4767 | 121.4218 | -121.6003 | -121.6095 | 121.4813 | 121.5134 | 17.2852 | 0.51727
1603.5938 | 121.6827 | -0.25635 | 121.4218 | -0.12032 | 0.0054624 | 0.065824 | 0.06203 | -0.0027685 | -0.010102 | -0.0028005 | -0.034454 | 0.0044561 | 0.064063 | 0.051968 | -0.014097 | 0.02634 | -0.0034435 | 17.45 | 121.2662 | -0.23804 | 121.2433 | 0.27466 | -0.16479 | -0.07782 | 0.32959 | 121.2341 | -0.24719 | 121.2021 | -0.10071 | -0.13733 | -0.12817 | 0.018311 | -0.15564 | -0.17853 | 0.53101 | 0.17853 | 0.091553 | 0.16022 | 0.073242 | 0.009156 | -0.18768 | -0.21973 | 0.15564 | 0.12817 | 0.11902 | 0.11902 | 0.10986 | 0.5127 | 121.4813 | 0.14648 | 121.4493 | 121.5042 | 121.4813 | 121.5225 | 121.4905 | -121.6599 | -121.669 | 121.4996 | 121.4584 | 17.7063 | 0.58594
1605.3594 | 121.756 | -0.2243 | 121.4081 | -0.13557 | 0.0035398 | 0.064328 | 0.06203 | -0.0064001 | -0.009675 | -0.0032277 | 0.0052185 | 0.0050971 | 0.064918 | 0.044278 | -0.015806 | 0.026767 | -0.010493 | 17.8207 | 121.2799 | -0.21973 | 121.2845 | 0.33417 | -0.10529 | -0.022888 | 0.27008 | 121.2067 | -0.24261 | 121.2936 | -0.041199 | -0.050354 | -0.045776 | 0.004577 | -0.12817 | -0.1236 | 0.55847 | 0.20142 | 0.11902 | 0.19684 | 0.11444 | -0.018311 | -0.20142 | -0.11444 | 0.18311 | 0.17853 | 0.17395 | 0.19684 | 0.19226 | 0.55389 | 121.5042 | 0.20142 | 121.5363 | 121.4996 | 121.4493 | 121.5042 | 121.431 | -121.6278 | -121.6507 | 121.5088 | 121.5179 | 18.045 | 0.49439
1607.1094 | 121.6736 | -0.25177 | 121.4584 | -0.12794 | 0.0078122 | 0.066892 | 0.066089 | 0.0019311 | -0.0083932 | -0.0047231 | -0.11685 | 0.0053107 | 0.063636 | 0.054959 | -0.017515 | 0.027408 | -0.0064343 | 18.2144 | 121.3394 | -0.2243 | 121.2433 | 0.29297 | -0.20142 | -0.11902 | 0.16937 | 121.2708 | -0.23804 | 121.2204 | -0.16022 | -0.19684 | -0.11444 | 0.027466 | -0.11902 | -0.21515 | 0.54474 | 0.13275 | 0.050354 | 0.10529 | 0.022888 | 0.013733 | -0.18768 | -0.23804 | 0.091553 | 0.13733 | 0.054932 | 0.1236 | 0.041199 | 0.51727 | 121.4676 | 0.07782 | 121.4584 | 121.5637 | 121.5088 | 121.5912 | 121.5225 | -121.6827 | -121.6965 | 121.4951 | 121.4722 | 18.4662 | 0.42114
1608.7969 | 121.6644 | -0.27008 | 121.463 | -0.074539 | 0.0048214 | 0.064756 | 0.063098 | 0.00086307 | -0.012025 | -0.0010915 | -0.046661 | 0.0070197 | 0.064277 | 0.057095 | -0.015379 | 0.027194 | -0.0055799 | 18.5989 | 121.3165 | -0.25177 | 121.225 | 0.31586 | -0.17395 | -0.10529 | 0.27924 | 121.2753 | -0.26093 | 121.225 | -0.14191 | -0.17395 | -0.14648 | 0.018311 | -0.14648 | -0.23804 | 0.58594 | 0.1648 | 0.096131 | 0.14648 | 0.07782 | 0.009156 | -0.18768 | -0.23804 | 0.12817 | 0.1236 | 0.096131 | 0.11444 | 0.086975 | 0.56763 | 121.4767 | 0.11902 | 121.4859 | 121.5683 | 121.5363 | 121.5866 | 121.5454 | -121.7148 | -121.7239 | 121.4951 | 121.4951 | 18.869 | 0.54932
1610.5469 | 121.8109 | -0.21057 | 121.4035 | -0.13557 | 0.0069578 | 0.067105 | 0.065448 | -0.0019141 | -0.010102 | -0.0032277 | -0.06192 | 0.0038153 | 0.064918 | 0.052823 | -0.015379 | 0.028476 | -0.0019483 | 19.0704 | 121.3028 | -0.22888 | 121.3257 | 0.41657 | -0.13275 | -0.013733 | 0.22888 | 121.2067 | -0.2243 | 121.3623 | -0.027466 | -0.050354 | -0.004578 | -0.018311 | -0.10071 | -0.077819 | 0.62714 | 0.19684 | 0.07782 | 0.21515 | 0.096131 | -0.013733 | -0.19684 | -0.041198 | 0.18311 | 0.20599 | 0.16022 | 0.21973 | 0.17395 | 0.64545 | 121.5546 | 0.19684 | 121.5866 | 121.5317 | 121.431 | 121.5134 | 121.4172 | -121.6324 | -121.6278 | 121.5363 | 121.5729 | 19.281 | 0.43945
1612.2969 | 121.8475 | -0.21973 | 121.4172 | -0.1432 | 0.0050352 | 0.063474 | 0.060321 | -0.0019141 | -0.010102 | -0.0019461 | 0.017425 | 0.0050971 | 0.064277 | 0.044705 | -0.01367 | 0.028476 | -0.010066 | 19.5877 | 121.2479 | -0.22888 | 121.3669 | 0.52185 | -0.027466 | 0.041199 | 0.44861 | 121.2158 | -0.23804 | 121.3486 | 0.013733 | -0.004578 | -0.027466 | -0.009155 | -0.16937 | -0.050354 | 0.74158 | 0.26093 | 0.19226 | 0.27008 | 0.20142 | -0.01831 | -0.20142 | -0.068664 | 0.23346 | 0.19226 | 0.21515 | 0.21057 | 0.23346 | 0.75073 | 121.5958 | 0.25177 | 121.5866 | 121.4767 | 121.4539 | 121.4676 | 121.4355 | -121.6461 | -121.6553 | 121.5866 | 121.5683 | 19.8074 | 0.66834
1614.0469 | 121.7972 | -0.23804 | 121.4401 | -0.15083 | 0.0078122 | 0.065183 | 0.064593 | -0.00063233 | -0.0066844 | -0.0034415 | -0.098541 | 0.0057379 | 0.064063 | 0.051541 | -0.013883 | 0.02634 | -0.0062207 | 19.9539 | 121.3303 | -0.26093 | 121.2891 | 0.40741 | -0.17395 | -0.073242 | 0.19684 | 121.2387 | -0.24719 | 121.3394 | -0.050354 | -0.09613 | -0.022888 | -0.022888 | -0.10986 | -0.15106 | 0.64545 | 0.16479 | 0.064087 | 0.18768 | 0.086975 | -0.009155 | -0.20142 | -0.10071 | 0.18768 | 0.21515 | 0.14191 | 0.2243 | 0.15106 | 0.66834 | 121.55 | 0.19684 | 121.5866 | 121.5912 | 121.4859 | 121.5683 | 121.4767 | -121.701 | -121.6873 | 121.5271 | 121.5775 | 20.192 | 0.43488
1615.7344 | 121.8063 | -0.24261 | 121.4127 | -0.044022 | 0.007385 | 0.066037 | 0.065234 | 0.00064947 | -0.0075388 | -0.0013051 | -0.089386 | 0.0057379 | 0.066413 | 0.054104 | -0.016447 | 0.027408 | -0.0021619 | 20.4254 | 121.3257 | -0.26093 | 121.257 | 0.39825 | -0.18768 | -0.091553 | 0.17853 | 121.2524 | -0.25635 | 121.2982 | -0.09613 | -0.1236 | -0.073242 | -0.01831 | -0.086975 | -0.15564 | 0.64087 | 0.15106 | 0.054932 | 0.16937 | 0.073242 | -0.013733 | -0.16022 | -0.11444 | 0.14649 | 0.16937 | 0.11902 | 0.18311 | 0.13275 | 0.65918 | 121.5179 | 0.16022 | 121.5546 | 121.5866 | 121.5088 | 121.5683 | 121.4951 | -121.6736 | -121.669 | 121.4996 | 121.5408 | 20.668 | 0.42114
1617.4844 | 121.701 | -0.34332 | 121.3715 | -0.06691 | 0.0080258 | 0.064756 | 0.061602 | 0.00022207 | -0.010316 | -0.0040823 | -0.04361 | 0.0053107 | 0.065345 | 0.051968 | -0.014097 | 0.027194 | -0.0015209 | 20.9564 | 121.2662 | -0.32044 | 121.1929 | 0.36163 | -0.21515 | -0.15106 | 0.29297 | 121.2204 | -0.32959 | 121.1746 | -0.20142 | -0.24261 | -0.2243 | 0.022888 | -0.10529 | -0.17853 | 0.70496 | 0.19226 | 0.12817 | 0.16937 | 0.10529 | 0.013733 | -0.15106 | -0.19684 | 0.14191 | 0.11902 | 0.10071 | 0.10529 | 0.086975 | 0.68207 | 121.5134 | 0.12817 | 121.5042 | 121.5866 | 121.55 | 121.6095 | 121.5637 | -121.6919 | -121.701 | 121.5363 | 121.5179 | 21.2997 | 0.63629
1619.2344 | 121.8109 | -0.30212 | 121.3852 | -0.13557 | 0.009094 | 0.064115 | 0.063098 | -0.0012731 | -0.009675 | -0.0032277 | -0.016144 | 0.0059515 | 0.061714 | 0.056241 | -0.015379 | 0.025912 | -0.0030163 | 21.666 | 121.2479 | -0.29755 | 121.3074 | 0.54474 | -0.091553 | -0.027466 | 0.41657 | 121.17 | -0.29297 | 121.2845 | -0.082397 | -0.10529 | -0.091553 | 0.004578 | -0.13733 | -0.07782 | 0.84686 | 0.27466 | 0.21057 | 0.27008 | 0.20599 | 0.009155 | -0.21515 | -0.10071 | 0.21973 | 0.21057 | 0.19684 | 0.20142 | 0.18768 | 0.84228 | 121.6049 | 0.21057 | 121.5775 | 121.5454 | 121.463 | 121.55 | 121.4722 | -121.6827 | -121.6782 | 121.6095 | 121.5866 | 21.9681 | 0.71869
1620.9219 | 121.756 | -0.33417 | 121.4035 | -0.0058748 | 0.0067442 | 0.064542 | 0.062457 | -0.0027685 | -0.010102 | -0.0040823 | -0.09549 | 0.0061651 | 0.064277 | 0.0509 | -0.014311 | 0.025912 | -0.0042981 | 22.197 | 121.2616 | -0.32501 | 121.225 | 0.41657 | -0.19684 | -0.14648 | 0.29297 | 121.2204 | -0.33417 | 121.225 | -0.16022 | -0.21973 | -0.16022 | 0.009155 | -0.14191 | -0.17853 | 0.75073 | 0.18768 | 0.13733 | 0.17853 | 0.12817 | 0 | -0.1831 | -0.17853 | 0.17395 | 0.17395 | 0.11444 | 0.17395 | 0.11444 | 0.74158 | 121.55 | 0.17395 | 121.5591 | 121.5866 | 121.5546 | 121.5958 | 121.5546 | -121.7285 | -121.7377 | 121.5591 | 121.5591 | 22.5311 | 0.62714
1622.6719 | 121.788 | -0.33875 | 121.3806 | -0.1432 | 0.0082394 | 0.066037 | 0.061816 | -0.00020513 | -0.012025 | 0.00040366 | -0.0008851 | 0.0046697 | 0.063209 | 0.051541 | -0.014524 | 0.025058 | -0.0047253 | 22.8149 | 121.2296 | -0.31586 | 121.2799 | 0.55389 | -0.10986 | -0.050354 | 0.3891 | 121.1609 | -0.31128 | 121.2296 | -0.13733 | -0.15564 | -0.15564 | 0.022888 | -0.15106 | -0.10071 | 0.89264 | 0.28839 | 0.22888 | 0.2655 | 0.20599 | 0.027466 | -0.21973 | -0.15106 | 0.20142 | 0.18311 | 0.18311 | 0.15564 | 0.15564 | 0.86975 | 121.5958 | 0.17395 | 121.5408 | 121.5454 | 121.4722 | 121.5683 | 121.4996 | -121.6965 | -121.6919 | 121.6187 | 121.5683 | 23.1537 | 0.72784
1624.4219 | 121.8246 | -0.33875 | 121.3486 | -0.13557 | 0.0065304 | 0.066037 | 0.06203 | -0.0049047 | -0.008607 | -0.00087794 | -0.022247 | 0.0057379 | 0.062354 | 0.042782 | -0.014738 | 0.024844 | -0.0030163 | 23.2773 | 121.2112 | -0.32501 | 121.2158 | 0.50812 | -0.21057 | -0.11444 | 0.2655 | 121.1563 | -0.34332 | 121.2158 | -0.15106 | -0.18768 | -0.16937 | 0.013733 | -0.13733 | -0.13275 | 0.84686 | 0.2243 | 0.12817 | 0.21057 | 0.11444 | -0.004578 | -0.19226 | -0.13275 | 0.18768 | 0.16937 | 0.15106 | 0.17395 | 0.15564 | 0.83313 | 121.5408 | 0.19226 | 121.5591 | 121.5363 | 121.4996 | 121.55 | 121.4951 | -121.6736 | -121.6919 | 121.5546 | 121.5546 | 23.616 | 0.60425
1626.125 | 121.8292 | -0.33875 | 121.3577 | -0.16609 | 0.0082394 | 0.065183 | 0.061389 | -0.0019141 | -0.0083932 | -0.00066434 | -0.0008851 | 0.0046697 | 0.065132 | 0.054104 | -0.01602 | 0.02634 | -0.0051525 | 23.9731 | 121.1975 | -0.32501 | 121.2845 | 0.60883 | -0.11444 | -0.059509 | 0.44403 | 121.1517 | -0.3479 | 121.2479 | -0.11902 | -0.15564 | -0.13733 | 0.013733 | -0.16022 | -0.073242 | 0.94757 | 0.27924 | 0.2243 | 0.2655 | 0.21057 | -0.009155 | -0.20599 | -0.10986 | 0.21973 | 0.20142 | 0.18311 | 0.21057 | 0.19226 | 0.93384 | 121.6095 | 0.22888 | 121.5958 | 121.5225 | 121.4996 | 121.5363 | 121.4905 | -121.6827 | -121.7056 | 121.6232 | 121.5866 | 24.3118 | 0.78278
1627.8906 | 121.788 | -0.36163 | 121.3669 | -0.074539 | 0.0080258 | 0.06561 | 0.065448 | 0.00043587 | -0.0083932 | -0.0010915 | -0.11075 | 0.0061651 | 0.066413 | 0.049405 | -0.017515 | 0.028476 | -0.0023755 | 24.6689 | 121.2662 | -0.35248 | 121.2479 | 0.57678 | -0.21515 | -0.12817 | 0.32959 | 121.2067 | -0.35248 | 121.225 | -0.19684 | -0.23804 | -0.18768 | 0.009155 | -0.10071 | -0.11902 | 0.93841 | 0.23346 | 0.14648 | 0.2243 | 0.13733 | 0.009155 | -0.16022 | -0.14191 | 0.16479 | 0.17395 | 0.1236 | 0.1648 | 0.11444 | 0.92926 | 121.6003 | 0.15564 | 121.5775 | 121.6187 | 121.5591 | 121.6278 | 121.5683 | -121.7194 | -121.7194 | 121.6095 | 121.5866 | 25.0305 | 0.69122
1629.6406 | 121.8063 | -0.3479 | 121.3669 | -0.11269 | 0.0078122 | 0.066892 | 0.06203 | -0.0014867 | -0.011598 | -0.0019461 | -0.0069885 | 0.0055243 | 0.063423 | 0.044064 | -0.013029 | 0.024844 | -0.0060071 | 25.3738 | 121.257 | -0.32501 | 121.2387 | 0.64087 | -0.17853 | -0.091553 | 0.23804 | 121.2021 | -0.33417 | 121.225 | -0.16479 | -0.19226 | -0.15564 | 0.022888 | -0.10986 | -0.12817 | 0.98877 | 0.25635 | 0.16937 | 0.23346 | 0.14648 | 0.013733 | -0.16479 | -0.14191 | 0.1831 | 0.19226 | 0.15564 | 0.17853 | 0.14191 | 0.96588 | 121.5637 | 0.16937 | 121.5591 | 121.582 | 121.5363 | 121.6049 | 121.55 | -121.6919 | -121.701 | 121.5866 | 121.5729 | 25.7217 | 0.58594
1631.3281 | 121.8567 | -0.32959 | 121.3669 | -0.10506 | 0.0067442 | 0.066892 | 0.063311 | -0.0029821 | -0.0088206 | -0.0023733 | -0.0069885 | 0.0046697 | 0.064277 | 0.048123 | -0.016233 | 0.027194 | -0.0087841 | 26.2115 | 121.2158 | -0.32959 | 121.3165 | 0.78735 | -0.082397 | -0.032043 | 0.44861 | 121.1609 | -0.33875 | 121.2891 | -0.07782 | -0.1236 | -0.11902 | 0 | -0.15106 | -0.050354 | 1.1169 | 0.29755 | 0.24719 | 0.29755 | 0.24719 | -0.009155 | -0.20599 | -0.07782 | 0.25177 | 0.21057 | 0.20599 | 0.21973 | 0.21515 | 1.1169 | 121.6461 | 0.26093 | 121.6278 | 121.5454 | 121.4996 | 121.5454 | 121.4905 | -121.6965 | -121.7056 | 121.6461 | 121.6187 | 26.5411 | 0.7782
1633.1094 | 121.8384 | -0.3479 | 121.3531 | -0.06691 | 0.0052488 | 0.063901 | 0.063739 | -0.0019141 | -0.0090342 | -0.0015189 | -0.064972 | 0.0057379 | 0.065132 | 0.054318 | -0.015165 | 0.026126 | -0.0042981 | 26.9165 | 121.2341 | -0.3479 | 121.2341 | 0.71411 | -0.1831 | -0.091553 | 0.23804 | 121.1609 | -0.35706 | 121.2158 | -0.16937 | -0.20142 | -0.17853 | 0 | -0.11902 | -0.11902 | 1.062 | 0.25635 | 0.16479 | 0.25635 | 0.16479 | -0.009156 | -0.19226 | -0.13733 | 0.17853 | 0.16937 | 0.14648 | 0.17853 | 0.15564 | 1.062 | 121.582 | 0.18768 | 121.5729 | 121.582 | 121.5179 | 121.582 | 121.5088 | -121.701 | -121.7102 | 121.582 | 121.5637 | 27.2644 | 0.58594
1634.7969 | 121.8246 | -0.37537 | 121.3211 | -0.12794 | 0.0095212 | 0.064328 | 0.063098 | -0.0036231 | -0.010102 | -0.0040823 | -0.064972 | 0.0050971 | 0.063423 | 0.050473 | -0.014738 | 0.026767 | -0.0070751 | 27.6535 | 121.1975 | -0.38452 | 121.1838 | 0.70496 | -0.22888 | -0.13275 | 0.24261 | 121.138 | -0.41199 | 121.1746 | -0.23346 | -0.27008 | -0.23346 | -0.009155 | -0.1236 | -0.13733 | 1.0803 | 0.24261 | 0.14648 | 0.25177 | 0.15564 | -0.036621 | -0.18311 | -0.14648 | 0.14191 | 0.14191 | 0.10528 | 0.17853 | 0.14191 | 1.0895 | 121.5683 | 0.17853 | 121.5866 | 121.582 | 121.55 | 121.5729 | 121.5134 | -121.7056 | -121.7331 | 121.5591 | 121.55 | 28.0289 | 0.61798
1636.5469 | 121.8246 | -1.0345 | 120.694 | -0.097427 | 0.0071714 | 0.068387 | 0.062457 | -0.0044775 | -0.01117 | -0.0017325 | -0.031403 | 0.0046697 | 0.062995 | 0.044491 | -0.015806 | 0.026126 | -0.0062207 | 28.4637 | 120.5154 | -1.0208 | 120.6162 | 0.21515 | -0.79193 | -0.70496 | 0.4303 | 120.4926 | -1.0345 | 120.5612 | -0.8194 | -0.86517 | -0.85602 | 0.013733 | -0.17853 | -0.07782 | 1.2497 | 0.32959 | 0.24261 | 0.31586 | 0.22888 | 0 | -0.20142 | -0.13275 | 0.21515 | 0.17853 | 0.16937 | 0.17853 | 0.16937 | 1.236 | 121.637 | 0.21515 | 121.5958 | 121.5363 | 121.5271 | 121.55 | 121.5271 | -121.7148 | -121.7285 | 121.6507 | 121.5958 | 29.4983 | 1.4648
1638.2969 | 121.8796 | -0.32044 | 121.376 | -0.15846 | 0.0069578 | 0.06561 | 0.062671 | -0.0031957 | -0.0077524 | -0.0010915 | -0.028351 | 0.0048833 | 0.065772 | 0.044064 | -0.015592 | 0.028049 | -0.0060071 | 30.0064 | 121.3165 | -0.28839 | 121.3074 | 0.91553 | -0.086975 | -0.004578 | 0.3067 | 121.2387 | -0.31128 | 121.2982 | -0.09613 | -0.12817 | -0.091553 | 0.032044 | -0.05951 | -0.068665 | 1.236 | 0.31586 | 0.23346 | 0.28381 | 0.20142 | 0.009156 | -0.13733 | -0.07782 | 0.22431 | 0.22888 | 0.19226 | 0.21973 | 0.1831 | 1.2039 | 121.5958 | 0.21515 | 121.6095 | 121.6049 | 121.55 | 121.637 | 121.5591 | -121.6644 | -121.6873 | 121.6278 | 121.6187 | 30.3268 | 0.62714
1639.9844 | 121.8658 | -0.29297 | 121.3989 | -0.23476 | 0.008453 | 0.066892 | 0.063311 | -0.00020513 | -0.0090342 | -0.0019461 | -0.074127 | 0.0061651 | 0.061286 | 0.0509 | -0.015379 | 0.026981 | -0.0062207 | 30.6976 | 121.2616 | -0.27466 | 121.3531 | 1.0208 | -0.064087 | 0.009155 | 0.27008 | 121.2296 | -0.28381 | 121.3486 | -0.086975 | -0.12817 | -0.09613 | 0.018311 | -0.13733 | -0.045777 | 1.3138 | 0.30212 | 0.22888 | 0.28381 | 0.21057 | 0.009156 | -0.16937 | -0.050354 | 0.20599 | 0.19684 | 0.16479 | 0.18768 | 0.15564 | 1.2955 | 121.6278 | 0.19684 | 121.6324 | 121.5363 | 121.5134 | 121.5546 | 121.5225 | -121.6736 | -121.6827 | 121.6461 | 121.6415 | 30.9906 | 0.56305
1641.75 | 121.8887 | -0.30212 | 121.3943 | -0.12794 | 0.0082394 | 0.06561 | 0.063739 | -0.0021277 | -0.0077524 | -0.0036551 | -0.022247 | 0.0044561 | 0.064918 | 0.05325 | -0.014311 | 0.025699 | -0.0040845 | 31.2698 | 121.312 | -0.29755 | 121.2982 | 1.0025 | -0.086975 | -0.018311 | 0.28839 | 121.2021 | -0.32044 | 121.3028 | -0.10071 | -0.11902 | -0.11444 | 0.004578 | -0.082397 | -0.09613 | 1.3046 | 0.28381 | 0.21515 | 0.27923 | 0.21057 | -0.018311 | -0.19226 | -0.091553 | 0.20142 | 0.18768 | 0.18311 | 0.20599 | 0.20142 | 1.3 | 121.5958 | 0.21973 | 121.6232 | 121.6095 | 121.5225 | 121.6141 | 121.5042 | -121.6919 | -121.7148 | 121.6003 | 121.6049 | 31.572 | 0.59052
1643.4844 | 121.7697 | -0.36163 | 121.4493 | -0.082169 | 0.0088804 | 0.06561 | 0.063311 | -0.0025549 | -0.011598 | -0.00023714 | -0.09549 | 0.0083013 | 0.064918 | 0.051114 | -0.014738 | 0.027194 | -0.0040845 | 31.778 | 121.3486 | -0.32959 | 121.2296 | 0.95673 | -0.14191 | -0.086975 | 0.28381 | 121.2662 | -0.32959 | 121.1975 | -0.20142 | -0.25635 | -0.21057 | 0.032043 | -0.10071 | -0.21973 | 1.3184 | 0.27466 | 0.21973 | 0.24261 | 0.18768 | 0.032043 | -0.18311 | -0.25177 | 0.16022 | 0.15106 | 0.10528 | 0.11902 | 0.073242 | 1.2863 | 121.5591 | 0.12817 | 121.5271 | 121.6782 | 121.5958 | 121.7102 | 121.6278 | -121.7789 | -121.7789 | 121.5912 | 121.5591 | 32.1396 | 0.64545
1645.2344 | 121.8613 | -0.33875 | 121.3852 | -0.20424 | 0.0086668 | 0.067533 | 0.064166 | -0.0010595 | -0.0094614 | -0.0053641 | -0.1199 | 0.0053107 | 0.064277 | 0.055173 | -0.014951 | 0.027835 | -0.0047253 | 32.2723 | 121.3165 | -0.33417 | 121.225 | 1.0025 | -0.17853 | -0.11444 | 0.1831 | 121.2158 | -0.33417 | 121.2845 | -0.15564 | -0.21973 | -0.16022 | 0.004578 | -0.068665 | -0.16022 | 1.3412 | 0.2243 | 0.16022 | 0.21973 | 0.15564 | 0.004578 | -0.16937 | -0.10071 | 0.18311 | 0.17853 | 0.11902 | 0.17395 | 0.11444 | 1.3367 | 121.5591 | 0.17853 | 121.6187 | 121.6507 | 121.55 | 121.6553 | 121.5546 | -121.7194 | -121.7194 | 121.5637 | 121.6232 | 32.6111 | 0.52185
1647.0312 | 121.7697 | -0.36163 | 121.4081 | -0.10506 | 0.011871 | 0.067105 | 0.065661 | 0.0025721 | -0.0092478 | -0.0028005 | -0.1077 | 0.0065923 | 0.067695 | 0.059018 | -0.014311 | 0.029758 | -0.0066479 | 32.8125 | 121.2936 | -0.3479 | 121.2341 | 1.0529 | -0.16937 | -0.10529 | 0.24719 | 121.2204 | -0.37537 | 121.2204 | -0.24719 | -0.3067 | -0.23804 | 0.013733 | -0.11444 | -0.17395 | 1.4145 | 0.25635 | 0.19226 | 0.24261 | 0.17853 | -0.013733 | -0.18768 | -0.18768 | 0.11444 | 0.1236 | 0.054931 | 0.13733 | 0.068664 | 1.4008 | 121.582 | 0.12817 | 121.5958 | 121.6415 | 121.5958 | 121.6553 | 121.582 | -121.756 | -121.7834 | 121.5958 | 121.582 | 33.1741 | 0.60882
1648.7188 | 121.8018 | -0.42572 | 121.376 | -0.089798 | 0.0088804 | 0.066678 | 0.063952 | -0.0027685 | -0.007966 | 0.00083106 | -0.1138 | 0.0065923 | 0.064063 | 0.056027 | -0.014097 | 0.02869 | -0.0068615 | 33.1146 | 121.2524 | -0.41657 | 121.1884 | 1.03 | -0.17853 | -0.13733 | 0.30212 | 121.1929 | -0.41657 | 121.2067 | -0.24719 | -0.28381 | -0.24719 | 0.009155 | -0.1236 | -0.18768 | 1.4557 | 0.28839 | 0.24719 | 0.27924 | 0.23804 | 0.009155 | -0.18311 | -0.16937 | 0.17853 | 0.17853 | 0.14191 | 0.16937 | 0.13275 | 1.4465 | 121.6049 | 0.16937 | 121.6232 | 121.669 | 121.6095 | 121.6782 | 121.6187 | -121.7926 | -121.7926 | 121.6141 | 121.6324 | 33.5403 | 0.72784
1650.4688 | 121.7834 | -0.4303 | 121.3806 | -0.097427 | 0.0080258 | 0.064328 | 0.061816 | -0.0042639 | -0.0092478 | -0.0023733 | -0.06192 | 0.0083013 | 0.064277 | 0.050046 | -0.011533 | 0.028262 | -0.0047253 | 33.4396 | 121.2341 | -0.40741 | 121.17 | 1.0712 | -0.19226 | -0.12817 | 0.3067 | 121.1929 | -0.4303 | 121.138 | -0.27924 | -0.32501 | -0.29755 | 0.022888 | -0.14648 | -0.21057 | 1.5015 | 0.30212 | 0.23804 | 0.27924 | 0.21515 | 0 | -0.18768 | -0.24262 | 0.15106 | 0.13275 | 0.10529 | 0.13275 | 0.10529 | 1.4786 | 121.5775 | 0.15106 | 121.5683 | 121.6415 | 121.6232 | 121.6644 | 121.6232 | -121.788 | -121.8109 | 121.6003 | 121.5683 | 33.8699 | 0.737
1652.2188 | 121.8567 | -0.42114 | 121.3074 | -0.1432 | 0.0097348 | 0.066464 | 0.062243 | -0.0023413 | -0.0092478 | -0.0034415 | -0.052765 | 0.0046697 | 0.06385 | 0.046841 | -0.01666 | 0.026981 | -0.0070751 | 33.6685 | 121.2112 | -0.3891 | 121.2112 | 1.1536 | -0.16022 | -0.073242 | 0.23346 | 121.1517 | -0.40283 | 121.2067 | -0.2243 | -0.26093 | -0.2243 | 0.032044 | -0.09613 | -0.09613 | 1.5747 | 0.3479 | 0.26093 | 0.31586 | 0.22888 | 0.018311 | -0.15564 | -0.10071 | 0.19684 | 0.19684 | 0.16022 | 0.17853 | 0.14191 | 1.5427 | 121.6003 | 0.17853 | 121.6095 | 121.6003 | 121.5546 | 121.6324 | 121.5729 | -121.6965 | -121.7102 | 121.6324 | 121.6278 | 34.0897 | 0.6546
1653.9062 | 121.8704 | -0.39825 | 121.3303 | -0.17372 | 0.010162 | 0.064969 | 0.061816 | -0.0087499 | -0.007966 | -0.0010915 | -0.016144 | 0.0040289 | 0.064491 | 0.04385 | -0.016233 | 0.026981 | -0.0025891 | 33.8882 | 121.1975 | -0.39368 | 121.1792 | 1.1765 | -0.16022 | -0.073242 | 0.24719 | 121.1655 | -0.42572 | 121.1838 | -0.2243 | -0.26093 | -0.2243 | 0.004577 | -0.13275 | -0.15106 | 1.5747 | 0.32501 | 0.23804 | 0.32044 | 0.23346 | -0.027466 | -0.16479 | -0.14648 | 0.17395 | 0.17395 | 0.13733 | 0.20142 | 0.16479 | 1.5701 | 121.5729 | 0.20142 | 121.6095 | 121.5912 | 121.5912 | 121.5958 | 121.5637 | -121.7239 | -121.756 | 121.5775 | 121.582 | 34.2865 | 0.64545
1655.6719 | 121.7834 | -0.48981 | 121.344 | -0.05928 | 0.0069578 | 0.063687 | 0.063952 | 0.0032129 | -0.0083932 | -0.00066434 | -0.10159 | 0.0057379 | 0.064491 | 0.059872 | -0.01602 | 0.026553 | -0.0094251 | 34.0118 | 121.2158 | -0.45776 | 121.1105 | 1.1215 | -0.23804 | -0.16479 | 0.30212 | 121.1472 | -0.4715 | 121.1105 | -0.32959 | -0.37537 | -0.34332 | 0.032043 | -0.12817 | -0.23346 | 1.6113 | 0.32501 | 0.25177 | 0.29297 | 0.21973 | 0.01831 | -0.19684 | -0.23346 | 0.16022 | 0.14648 | 0.11444 | 0.12817 | 0.096131 | 1.5793 | 121.5683 | 0.14191 | 121.582 | 121.6736 | 121.6187 | 121.7056 | 121.637 | -121.8018 | -121.8155 | 121.6003 | 121.6003 | 34.5016 | 0.79193
1657.3594 | 121.8521 | -0.93384 | 120.7809 | -0.18135 | 0.0082394 | 0.067533 | 0.06502 | -0.0046911 | -0.0081796 | 0.00061746 | -0.055817 | 0.0044561 | 0.062995 | 0.045132 | -0.014738 | 0.026981 | -0.0066479 | 33.6639 | 120.6619 | -0.93384 | 120.6894 | 0.737 | -0.66834 | -0.58594 | 0.23804 | 120.5978 | -0.93384 | 120.6757 | -0.75989 | -0.77362 | -0.737 | 0 | -0.11902 | -0.091553 | 1.6708 | 0.3479 | 0.2655 | 0.3479 | 0.2655 | 0 | -0.18311 | -0.10529 | 0.17395 | 0.19684 | 0.16022 | 0.19684 | 0.16022 | 1.6708 | 121.6232 | 0.17395 | 121.6095 | 121.5958 | 121.5317 | 121.5958 | 121.5317 | -121.7148 | -121.7148 | 121.6232 | 121.6095 | 34.5978 | 1.1719
1659.1094 | 121.8201 | -2.1881 | 119.5404 | -0.12794 | 0.0093076 | 0.066678 | 0.062671 | -0.0025549 | -0.0094614 | -0.00045074 | -0.022247 | 0.0061651 | 0.063209 | 0.050686 | -0.01367 | 0.026126 | -0.0038709 | 32.9269 | 119.4168 | -2.1423 | 119.4901 | -0.37994 | -1.8311 | -1.7807 | 0.40283 | 119.3802 | -2.1378 | 119.339 | -2.0508 | -2.0233 | -2.0142 | 0.045776 | -0.1236 | -0.050354 | 1.8082 | 0.40741 | 0.35705 | 0.36163 | 0.31128 | 0.050354 | -0.16022 | -0.20142 | 0.13733 | 0.17395 | 0.16479 | 0.1236 | 0.11444 | 1.7624 | 121.6324 | 0.086975 | 121.4767 | 121.5591 | 121.5179 | 121.6049 | 121.5683 | -121.6827 | -121.6782 | 121.6782 | 121.5271 | 35.1151 | 2.5909
1660.8125 | 121.9116 | -2.2476 | 119.4489 | -0.12794 | 0.0093076 | 0.066678 | 0.06203 | -0.0053321 | -0.0081796 | -0.0019461 | -0.04361 | 0.0042425 | 0.062568 | 0.050473 | -0.015379 | 0.026981 | -0.0040845 | 32.9544 | 119.2703 | -2.1423 | 119.3619 | -0.46692 | -1.9272 | -1.886 | 1.4236 | 119.22 | -2.2934 | 119.3573 | -2.0462 | -2.1149 | -2.0599 | 0.10529 | -0.17853 | -0.086976 | 1.7807 | 0.36163 | 0.32044 | 0.25635 | 0.21515 | -0.045776 | -0.22888 | -0.091553 | 0.20142 | 0.18768 | 0.13275 | 0.23346 | 0.17853 | 1.6754 | 121.5042 | 0.24719 | 121.6507 | 121.4127 | 121.5134 | 121.5179 | 121.4676 | -121.5912 | -121.7422 | 121.6095 | 121.6049 | 35.202 | 3.6713
1662.5625 | 121.8658 | -0.64087 | 121.1014 | -0.13557 | 0.012085 | 0.066464 | 0.066516 | 0.0021447 | -0.0071116 | -0.0015189 | -0.11075 | 0.0059515 | 0.062995 | 0.053036 | -0.01602 | 0.029117 | -0.0051525 | 34.3094 | 120.9824 | -0.66376 | 120.9366 | 1.0712 | -0.41199 | -0.3479 | 0.21973 | 120.8908 | -0.66376 | 120.9915 | -0.48981 | -0.50354 | -0.44403 | -0.022888 | -0.11902 | -0.16479 | 1.712 | 0.29297 | 0.22888 | 0.31586 | 0.25177 | -0.022888 | -0.21057 | -0.10986 | 0.15106 | 0.19684 | 0.13733 | 0.21973 | 0.16022 | 1.7349 | 121.6003 | 0.17395 | 121.6553 | 121.6461 | 121.5546 | 121.6232 | 121.5317 | -121.7651 | -121.7651 | 121.5775 | 121.6324 | 34.9503 | 0.8606
1664.25 | 121.8384 | -2.1286 | 119.6228 | -0.097427 | 0.0099484 | 0.067533 | 0.065875 | -0.0023413 | -0.0064706 | -0.0010915 | -0.12601 | 0.0074469 | 0.065559 | 0.049618 | -0.013456 | 0.026767 | -0.0010937 | 33.2474 | 119.6869 | -1.8814 | 119.5953 | -0.17395 | -1.6296 | -1.6113 | 0.14648 | 119.5541 | -1.9821 | 119.3893 | -2.0142 | -2.1378 | -2.005 | 0.24719 | 0.064087 | -0.027466 | 1.9547 | 0.51727 | 0.49896 | 0.27008 | 0.25177 | 0.14648 | -0.068665 | -0.23346 | 0.11444 | 0.1236 | -0.009155 | -0.022888 | -0.15564 | 1.7075 | 121.4767 | -0.032043 | 121.3715 | 121.5683 | 121.5363 | 121.8155 | 121.6827 | -121.5042 | -121.6049 | 121.7239 | 121.5179 | 35.376 | 2.2751
1666.0156 | 121.6965 | -7.7728 | 113.887 | -0.1432 | 0.010589 | 0.067319 | 0.065448 | -0.0019141 | -0.0077524 | 0.00061746 | -0.13211 | 0.0068059 | 0.065772 | 0.05325 | -0.01367 | 0.027621 | -0.0051525 | 28.1525 | 113.7909 | -7.7637 | 113.6948 | -6.0654 | -7.6675 | -7.6218 | 0.036621 | 113.7085 | -7.8003 | 113.6627 | -7.7454 | -7.814 | -7.7499 | 0.009155 | -0.09613 | -0.19226 | 1.7075 | 0.15106 | 0.10529 | 0.14191 | 0.09613 | -0.027466 | -0.17853 | -0.2243 | 0.027466 | 0.022888 | -0.041199 | 0.050354 | -0.013733 | 1.6983 | 121.4584 | 0.054932 | 121.463 | 121.5546 | 121.5088 | 121.5637 | 121.4813 | -121.6507 | -121.6873 | 121.4676 | 121.4355 | 35.9253 | 7.8094
1667.7656 | 121.669 | -17.7658 | 103.7201 | -0.11269 | 0.0071714 | 0.067533 | 0.062243 | -0.00020513 | -0.0073252 | -0.00023714 | -0.031403 | 0.0055243 | 0.065986 | 0.049191 | -0.014097 | 0.028476 | -0.0047253 | 20.1965 | 104.5303 | -16.8228 | 103.9673 | -15.8936 | -17.72 | -17.7246 | -0.41199 | 103.6285 | -17.7063 | 103.5782 | -17.7383 | -17.9535 | -18.0725 | 0.94299 | 0.81024 | 0.24719 | 1.8723 | 0.041199 | 0.045776 | -0.90179 | -0.89722 | 0.059509 | -0.091553 | -0.14191 | 0.027466 | -0.3067 | -0.18768 | -0.36621 | -0.24719 | 0.92926 | 120.7901 | -0.032043 | 121.2845 | 121.3531 | 121.3348 | 122.2961 | 121.3943 | -120.5429 | -121.4264 | 121.7331 | 121.344 | 37.9623 | 17.3538
1669.4531 | 120.845 | -75.737 | 44.7601 | -0.12794 | 0.0080258 | 0.069882 | 0.063952 | 8.47e-06 | -0.0094614 | -0.00066434 | -0.025299 | 0.0059515 | 0.065986 | 0.049832 | -0.012388 | 0.027408 | -0.0081433 | -31.9702 | 44.632 | -75.7416 | 44.6136 | -73.7595 | -75.5859 | -75.4395 | -0.21973 | 44.7006 | -75.8286 | 44.7968 | -75.7599 | -75.8972 | -75.6317 | -0.004577 | -0.12817 | -0.14648 | 1.9775 | 0.29755 | 0.15106 | 0.30212 | 0.15564 | -0.091552 | -0.059509 | 0.036621 | -0.022888 | 0.10529 | -0.16022 | 0.19684 | -0.068665 | 1.9821 | 120.3552 | 0.068664 | 120.6253 | 120.3735 | 120.5292 | 120.369 | 120.4376 | -120.5017 | -120.5887 | 120.3506 | 120.5338 | 43.7668 | 75.5173
1671.2188 | 121.4447 | -116.185 | 4.9301 | -0.12032 | 0.0086668 | 0.069242 | 0.063952 | -0.0023413 | -0.0088206 | 0.00019006 | -0.013092 | 0.0048833 | 0.063209 | 0.053891 | -0.014738 | 0.027408 | -0.0028027 | -64.8514 | 4.5868 | -116.4139 | 4.7058 | -113.53 | -116.0156 | -116.0614 | -0.39368 | 4.6967 | -116.4047 | 4.8798 | -115.7547 | -116.0248 | -115.9241 | -0.22888 | -0.34332 | -0.2243 | 2.655 | 0.1236 | 0.16937 | 0.35248 | 0.39825 | -0.21973 | -0.23346 | -0.050354 | 0.4303 | 0.26093 | 0.16022 | 0.48065 | 0.37994 | 2.8839 | 121.1197 | 0.65002 | 121.2845 | 121.0007 | 121.1014 | 120.7718 | 120.8817 | -121.344 | -121.3348 | 120.8908 | 121.0648 | 51.3336 | 115.7913
1672.9375 | 120.8908 | -68.1564 | 52.5558 | -0.097427 | 0.0075986 | 0.066251 | 0.062457 | -0.0021277 | -0.011598 | -0.0017325 | -0.016144 | 0.0048833 | 0.064277 | 0.047909 | -0.014311 | 0.028262 | -0.0049389 | -22.2107 | 54.9866 | -65.7715 | 53.8971 | -63.6658 | -65.5701 | -66.4124 | -3.7216 | 53.5858 | -67.1036 | 52.3544 | -68.0099 | -68.486 | -68.3166 | 2.3849 | 2.4307 | 1.3412 | 4.4907 | 1.7441 | 2.5864 | -0.64087 | 0.20142 | 1.0529 | 1.03 | -0.20142 | 0.14648 | -0.16022 | -0.32959 | -1.2131 | -1.3824 | 2.1057 | 119.6686 | -0.90637 | 119.458 | 120.7581 | 120.6894 | 123.143 | 121.7422 | -118.3273 | -119.6594 | 122.0535 | 120.5109 | 45.9457 | 64.4348
1674.7031 | 120.9274 | -0.26093 | 120.9503 | -0.12032 | 0.010376 | 0.065183 | 0.065875 | -0.00020513 | -0.0081796 | -0.0021597 | -0.1138 | 0.0046697 | 0.064063 | 0.056881 | -0.015806 | 0.027408 | -0.0068615 | 33.0002 | 120.7626 | -0.24261 | 120.7352 | 1.6937 | 0.073242 | 0.12817 | 0.46692 | 120.7169 | -0.22888 | 120.7214 | -0.10071 | -0.15564 | -0.10529 | 0.01831 | -0.18768 | -0.21515 | 1.9547 | 0.3891 | 0.33417 | 0.37079 | 0.31586 | 0.032043 | -0.23346 | -0.22888 | 0.16022 | 0.15564 | 0.10529 | 0.1236 | 0.073242 | 1.9363 | 120.9778 | 0.12817 | 120.9503 | 121.0052 | 120.9457 | 121.0236 | 120.9778 | -121.1929 | -121.1792 | 120.9961 | 120.9824 | 33.2611 | 0.72784
1676.3906 | 121.3486 | -0.1831 | 121.0236 | -0.13557 | 0.012085 | 0.067319 | 0.063311 | -0.0036231 | -0.0060434 | -0.00045074 | -0.055817 | 0.0048833 | 0.062568 | 0.049191 | -0.015165 | 0.027835 | -0.0064343 | 32.8857 | 120.8588 | -0.17395 | 120.932 | 1.8311 | 0.20599 | 0.26093 | 0.36621 | 120.8405 | -0.17853 | 120.9503 | 0.059509 | 0.004578 | 0.064087 | 0.009155 | -0.16479 | -0.091553 | 2.0142 | 0.44403 | 0.3891 | 0.43488 | 0.37994 | 0.004577 | -0.18311 | -0.073243 | 0.24261 | 0.24719 | 0.18768 | 0.24261 | 0.18311 | 2.005 | 121.106 | 0.23804 | 121.1288 | 121.0327 | 121.019 | 121.0419 | 121.0236 | -121.1975 | -121.2021 | 121.1151 | 121.1334 | 33.0688 | 0.54932
1678.1406 | 121.2845 | -0.21515 | 121.1197 | -0.097427 | 0.010803 | 0.064328 | 0.061602 | -0.0019141 | -0.0081796 | -0.0030141 | -0.04361 | 0.0061651 | 0.062782 | 0.054532 | -0.015592 | 0.027408 | -0.0060071 | 32.7164 | 120.9549 | -0.19226 | 120.9091 | 1.7761 | 0.14191 | 0.20142 | 0.40283 | 120.9045 | -0.20142 | 120.8542 | -0.064087 | -0.10071 | -0.10071 | 0.022888 | -0.1648 | -0.21057 | 1.9913 | 0.41657 | 0.35706 | 0.39368 | 0.33417 | 0.013733 | -0.21515 | -0.2655 | 0.15106 | 0.11444 | 0.11444 | 0.10071 | 0.10071 | 1.9684 | 121.1014 | 0.13733 | 121.0556 | 121.1472 | 121.106 | 121.17 | 121.1197 | -121.312 | -121.3211 | 121.1243 | 121.0693 | 32.9315 | 0.61798
1679.8281 | 121.344 | -0.2243 | 121.1197 | -0.11269 | 0.010376 | 0.065396 | 0.062884 | -0.00084593 | -0.0088206 | -0.0017325 | -0.019196 | 0.0044561 | 0.064918 | 0.049618 | -0.015592 | 0.02634 | -0.0064343 | 32.5562 | 120.9457 | -0.19226 | 120.9915 | 1.8494 | 0.20142 | 0.24261 | 0.43488 | 120.9137 | -0.21057 | 120.9229 | -0.036621 | -0.086975 | -0.068665 | 0.032043 | -0.17395 | -0.12817 | 2.0737 | 0.46692 | 0.42572 | 0.43488 | 0.39368 | 0.013733 | -0.20599 | -0.19684 | 0.18768 | 0.15564 | 0.13733 | 0.14191 | 0.1236 | 2.0416 | 121.1838 | 0.17395 | 121.1334 | 121.138 | 121.1243 | 121.17 | 121.138 | -121.312 | -121.3303 | 121.2158 | 121.1472 | 32.7805 | 0.65918
1681.5781 | 121.4035 | -0.24261 | 121.0968 | -0.097427 | 0.012298 | 0.066464 | 0.061816 | -0.0051183 | -0.0083932 | -0.0013051 | -0.01004 | 0.0044561 | 0.064491 | 0.046628 | -0.013883 | 0.026767 | -0.0066479 | 32.4692 | 120.9595 | -0.21515 | 121.0144 | 1.8723 | 0.19684 | 0.23346 | 0.44403 | 120.9183 | -0.24261 | 120.9412 | -0.045776 | -0.091553 | -0.054932 | 0.027466 | -0.13733 | -0.082398 | 2.1149 | 0.47607 | 0.43945 | 0.44861 | 0.41199 | 0 | -0.17853 | -0.15564 | 0.19684 | 0.18768 | 0.15106 | 0.18768 | 0.15106 | 2.0874 | 121.2296 | 0.19684 | 121.1838 | 121.1746 | 121.1609 | 121.2021 | 121.1609 | -121.312 | -121.3394 | 121.257 | 121.1838 | 32.7118 | 0.68665
1683.3281 | 121.376 | -0.26093 | 121.1472 | -0.11269 | 0.013153 | 0.069882 | 0.067584 | 0.00043587 | -0.0071116 | 0.00040366 | -0.10464 | 0.0065923 | 0.065132 | 0.051114 | -0.015165 | 0.027621 | -0.0040845 | 32.1945 | 121.051 | -0.24719 | 120.8908 | 1.7441 | 0.050354 | 0.11444 | 0.15564 | 120.9457 | -0.2655 | 120.9183 | -0.15564 | -0.21057 | -0.12817 | 0.013733 | -0.096131 | -0.25635 | 2.005 | 0.37537 | 0.31128 | 0.36163 | 0.29755 | -0.004578 | -0.20142 | -0.22888 | 0.10529 | 0.13275 | 0.050354 | 0.13733 | 0.054932 | 1.9913 | 121.138 | 0.10986 | 121.1838 | 121.2982 | 121.2112 | 121.3119 | 121.2067 | -121.3943 | -121.4127 | 121.1517 | 121.1792 | 32.4554 | 0.41657
1685.0938 | 121.4035 | -0.28381 | 121.138 | -0.13557 | 0.012939 | 0.067319 | 0.066516 | -0.00084593 | -0.0071116 | -0.0019461 | -0.098541 | 0.0074469 | 0.065345 | 0.054745 | -0.015165 | 0.025699 | -0.0034435 | 31.9519 | 121.0648 | -0.28381 | 120.9274 | 1.7624 | 0.059509 | 0.10529 | 0.16022 | 120.9503 | -0.27466 | 120.9274 | -0.16479 | -0.21973 | -0.14648 | 0 | -0.073242 | -0.21057 | 2.0462 | 0.3891 | 0.34332 | 0.3891 | 0.34332 | 0.009155 | -0.18768 | -0.21057 | 0.11902 | 0.13733 | 0.064086 | 0.12817 | 0.054931 | 2.0462 | 121.2112 | 0.10986 | 121.2021 | 121.3486 | 121.225 | 121.3486 | 121.2341 | -121.4218 | -121.4127 | 121.2112 | 121.2112 | 32.2357 | 0.44403
1686.7969 | 121.4172 | -0.32044 | 121.1426 | -0.13557 | 0.011444 | 0.066251 | 0.062457 | -0.0038367 | -0.0088206 | 0.00040366 | -0.031403 | 0.0057379 | 0.06385 | 0.046841 | -0.015165 | 0.027408 | -0.0079297 | 31.778 | 120.9961 | -0.28839 | 120.9366 | 1.8173 | 0.10529 | 0.11902 | 0.33417 | 120.9503 | -0.28381 | 120.9 | -0.16479 | -0.19226 | -0.1831 | 0.032044 | -0.14648 | -0.20599 | 2.1378 | 0.43945 | 0.42572 | 0.40741 | 0.39368 | 0.036622 | -0.19226 | -0.24262 | 0.15564 | 0.13733 | 0.12817 | 0.10071 | 0.091552 | 2.1057 | 121.225 | 0.11902 | 121.1838 | 121.2845 | 121.2341 | 121.3165 | 121.2708 | -121.431 | -121.4264 | 121.257 | 121.2204 | 32.0984 | 0.6546
1688.5469 | 121.4355 | -0.31128 | 121.1472 | -0.15846 | 0.013366 | 0.068814 | 0.066089 | 0.0025721 | -0.006257 | -0.00023714 | -0.1077 | 0.0072333 | 0.064277 | 0.051114 | -0.015165 | 0.025485 | -0.0038709 | 31.7093 | 121.0602 | -0.31128 | 120.8908 | 1.7624 | 0.032043 | 0.073242 | 0.14648 | 120.9869 | -0.32501 | 120.9183 | -0.21973 | -0.27008 | -0.19226 | 0 | -0.086975 | -0.25635 | 2.0737 | 0.38452 | 0.34332 | 0.38452 | 0.34332 | -0.013733 | -0.16022 | -0.22888 | 0.091552 | 0.11902 | 0.041198 | 0.13275 | 0.054931 | 2.0737 | 121.2021 | 0.10529 | 121.2433 | 121.3715 | 121.3119 | 121.3715 | 121.2982 | -121.4584 | -121.4722 | 121.2021 | 121.2296 | 32.0206 | 0.45776
1690.25 | 121.5637 | -0.2655 | 121.0831 | -0.15846 | 0.012085 | 0.069455 | 0.063098 | -0.0010595 | -0.0073252 | 0.00019006 | -0.04361 | 0.0050971 | 0.064277 | 0.047482 | -0.014524 | 0.027194 | -0.0064343 | 31.5216 | 121.0007 | -0.27466 | 121.0419 | 1.9821 | 0.16937 | 0.21515 | 0.29297 | 120.9274 | -0.27924 | 121.0236 | -0.086975 | -0.11902 | -0.09613 | -0.009155 | -0.082398 | -0.041199 | 2.2476 | 0.48065 | 0.43488 | 0.48981 | 0.44403 | -0.013733 | -0.15564 | -0.059509 | 0.17853 | 0.16937 | 0.14648 | 0.18311 | 0.16022 | 2.2568 | 121.3165 | 0.19226 | 121.3028 | 121.2753 | 121.2067 | 121.2662 | 121.1929 | -121.3577 | -121.3623 | 121.3074 | 121.2891 | 31.7871 | 0.55847
1692.0625 | 121.582 | -0.28839 | 121.138 | -0.11269 | 0.0093076 | 0.066464 | 0.065234 | -0.0021277 | -0.0049754 | -0.0010915 | -0.0008851 | 0.0042425 | 0.064704 | 0.047268 | -0.015592 | 0.025912 | -0.0060071 | 31.3385 | 121.0007 | -0.29755 | 121.0556 | 2.005 | 0.21515 | 0.23804 | 0.45319 | 120.9229 | -0.29297 | 121.0327 | -0.07782 | -0.10529 | -0.086975 | -0.009155 | -0.13733 | -0.082397 | 2.2934 | 0.52643 | 0.50354 | 0.53558 | 0.5127 | -0.004578 | -0.21515 | -0.10529 | 0.21057 | 0.20142 | 0.18311 | 0.20599 | 0.18768 | 2.3026 | 121.3531 | 0.21515 | 121.3257 | 121.2982 | 121.2158 | 121.2891 | 121.2112 | -121.4355 | -121.431 | 121.344 | 121.3211 | 31.6269 | 0.74158
1693.7969 | 121.5363 | -0.32501 | 121.17 | -0.044022 | 0.012085 | 0.069242 | 0.067157 | -0.0029821 | -0.0077524 | 0.00061746 | -0.086334 | 0.0072333 | 0.062568 | 0.058804 | -0.017301 | 0.027835 | -0.0038709 | 31.1279 | 121.0464 | -0.34332 | 121.019 | 1.9547 | 0.13733 | 0.14648 | 0.32959 | 121.0052 | -0.33875 | 120.9961 | -0.15106 | -0.21515 | -0.16022 | -0.018311 | -0.1236 | -0.15106 | 2.2797 | 0.4715 | 0.46234 | 0.48981 | 0.48065 | -0.013733 | -0.16479 | -0.17395 | 0.17395 | 0.1648 | 0.10986 | 0.17853 | 0.1236 | 2.298 | 121.3623 | 0.18768 | 121.3348 | 121.3898 | 121.344 | 121.3715 | 121.3303 | -121.5134 | -121.5088 | 121.344 | 121.3211 | 31.4529 | 0.6546
1695.5312 | 121.582 | -0.31586 | 121.1426 | -0.15083 | 0.011017 | 0.068387 | 0.063739 | -0.0021277 | -0.0054026 | -0.0010915 | -0.037506 | 0.0055243 | 0.064277 | 0.040433 | -0.013242 | 0.026553 | -0.0060071 | 30.9311 | 121.0052 | -0.3067 | 121.0098 | 1.973 | 0.15106 | 0.17395 | 0.24261 | 120.9595 | -0.32959 | 121.0052 | -0.15106 | -0.17853 | -0.14191 | 0.009155 | -0.13733 | -0.13275 | 2.2888 | 0.48981 | 0.46692 | 0.48065 | 0.45776 | -0.013733 | -0.1831 | -0.13733 | 0.16479 | 0.17395 | 0.13733 | 0.18768 | 0.15106 | 2.2797 | 121.3165 | 0.17853 | 121.3348 | 121.312 | 121.2891 | 121.3211 | 121.2753 | -121.4493 | -121.4722 | 121.3257 | 121.3211 | 31.2469 | 0.55847
1697.2812 | 121.4996 | -0.37079 | 121.1746 | -0.16609 | 0.012085 | 0.06796 | 0.068225 | 0.0019311 | -0.0075388 | -0.00066434 | -0.11685 | 0.0072333 | 0.063209 | 0.050046 | -0.016447 | 0.028049 | -0.0032299 | 30.6976 | 121.0648 | -0.3479 | 120.9366 | 1.8814 | 0.027466 | 0.059509 | 0.15564 | 121.0098 | -0.38452 | 120.9274 | -0.27466 | -0.32501 | -0.24261 | 0.022889 | -0.10986 | -0.23804 | 2.2522 | 0.4303 | 0.39825 | 0.40741 | 0.37537 | -0.013732 | -0.16479 | -0.24719 | 0.096131 | 0.12817 | 0.045777 | 0.14191 | 0.059509 | 2.2293 | 121.2845 | 0.10986 | 121.312 | 121.4127 | 121.3943 | 121.4355 | 121.3806 | -121.5225 | -121.5591 | 121.3074 | 121.2982 | 31.0684 | 0.52643
1698.9844 | 121.6553 | -0.32044 | 121.1334 | -0.15846 | 0.012939 | 0.069455 | 0.065661 | -0.0014867 | -0.0071116 | -0.00087794 | -0.06192 | 0.0050971 | 0.065345 | 0.054318 | -0.013456 | 0.025912 | -0.0047253 | 30.4688 | 121.0419 | -0.33417 | 121.0464 | 2.0508 | 0.13733 | 0.20142 | 0.25177 | 120.9412 | -0.3479 | 121.0648 | -0.13275 | -0.17395 | -0.10529 | -0.013732 | -0.091553 | -0.086975 | 2.3712 | 0.52185 | 0.45776 | 0.53558 | 0.4715 | -0.027465 | -0.19226 | -0.068665 | 0.18768 | 0.21515 | 0.14649 | 0.24261 | 0.17395 | 2.3849 | 121.3806 | 0.21515 | 121.4127 | 121.376 | 121.2891 | 121.3623 | 121.2616 | -121.4676 | -121.4813 | 121.3669 | 121.3852 | 30.7892 | 0.57221
1700.7344 | 121.669 | -0.34332 | 121.1243 | -0.17372 | 0.013153 | 0.07031 | 0.06502 | -0.00020513 | -0.0066844 | -0.00066434 | -0.055817 | 0.0063787 | 0.065986 | 0.052182 | -0.01602 | 0.02634 | -0.0010937 | 30.2399 | 121.0236 | -0.33417 | 121.0648 | 2.092 | -0.1831 | 0.21973 | 0.29755 | 120.9503 | -0.34332 | 121.0739 | -0.15106 | -0.17395 | -0.1236 | 0.009156 | -0.10071 | -0.05951 | 2.4353 | 0.56305 | 0.16022 | 0.55389 | 0.15106 | 0 | -0.17395 | -0.050354 | 0.19226 | 0.21973 | 0.16937 | 0.21973 | 0.16937 | 2.4261 | 121.3989 | 0.19226 | 121.4172 | 121.3577 | 121.2936 | 121.3669 | 121.2936 | -121.4584 | -121.4676 | 121.4081 | 121.4172 | 30.5832 | 0.64087
1702.4531 | 121.637 | -0.37537 | 121.1655 | -0.15846 | 0.012939 | 0.068173 | 0.066089 | 0.00043587 | -0.0060434 | 0.0012583 | -0.09549 | 0.0061651 | 0.067481 | 0.048123 | -0.014311 | 0.028262 | -0.0045117 | 29.9561 | 121.0464 | -0.39368 | 120.9686 | 1.9867 | 0.091553 | 0.10529 | 0.19684 | 120.9824 | -0.40283 | 121.0144 | -0.20142 | -0.25635 | -0.21057 | -0.018311 | -0.11902 | -0.19684 | 2.3621 | 0.48065 | 0.46692 | 0.49896 | 0.48523 | -0.027466 | -0.1831 | -0.15106 | 0.17395 | 0.16479 | 0.11902 | 0.19226 | 0.14648 | 2.3804 | 121.3623 | 0.20142 | 121.4172 | 121.4401 | 121.3852 | 121.4218 | 121.3577 | -121.5591 | -121.5683 | 121.344 | 121.3898 | 30.3314 | 0.5722
1704.1875 | 121.6782 | -0.37994 | 121.138 | -0.20424 | 0.012939 | 0.068173 | 0.065875 | -0.0021277 | -0.0064706 | -0.00045074 | -0.04361 | 0.0055243 | 0.064918 | 0.051327 | -0.014097 | 0.026981 | -0.0019483 | 29.8508 | 121.0098 | -0.36621 | 121.0556 | 2.1011 | 0.17853 | 0.18768 | 0.27466 | 120.9503 | -0.39368 | 121.051 | -0.17853 | -0.22888 | -0.16937 | 0.013733 | -0.12817 | -0.082397 | 2.4811 | 0.56763 | 0.55847 | 0.55389 | 0.54474 | -0.013733 | -0.18768 | -0.086975 | 0.20142 | 0.21057 | 0.15106 | 0.2243 | 0.16479 | 2.4673 | 121.4218 | 0.21515 | 121.4447 | 121.376 | 121.344 | 121.3898 | 121.3303 | -121.5042 | -121.5317 | 121.4355 | 121.431 | 30.2307 | 0.6546
1705.9062 | 121.6324 | -0.43945 | 121.1105 | -0.10506 | 0.010376 | 0.067319 | 0.066089 | 8.47e-06 | -0.0075388 | 0.0018991 | -0.031403 | 0.0068059 | 0.065132 | 0.049618 | -0.014951 | 0.026126 | -0.0042981 | 29.5853 | 120.9961 | -0.42114 | 121.0052 | 2.0828 | 0.20142 | 0.1831 | 0.42572 | 120.9366 | -0.44861 | 120.9549 | -0.23804 | -0.27466 | -0.25635 | 0.01831 | -0.11444 | -0.10529 | 2.5223 | 0.62256 | 0.64087 | 0.60425 | 0.62256 | -0.009155 | -0.17395 | -0.15564 | 0.20142 | 0.1831 | 0.16479 | 0.19226 | 0.17395 | 2.504 | 121.4264 | 0.21057 | 121.4035 | 121.4172 | 121.3852 | 121.4355 | 121.376 | -121.5317 | -121.5591 | 121.4447 | 121.3943 | 30.0247 | 0.86517
1707.6562 | 121.6507 | -0.48523 | 121.0648 | -0.12794 | 0.01123 | 0.066892 | 0.064807 | -0.0031957 | -0.0071116 | 0.0016855 | -0.022247 | 0.0059515 | 0.063636 | 0.04385 | -0.014951 | 0.026126 | -0.0057935 | 29.3518 | 120.9229 | -0.45776 | 120.9732 | 2.0645 | 0.15564 | 0.13275 | 0.40283 | 120.8725 | -0.46234 | 120.9091 | -0.28839 | -0.33875 | -0.32044 | 0.027465 | -0.14191 | -0.091552 | 2.5497 | 0.61798 | 0.64087 | 0.59052 | 0.6134 | 0.022888 | -0.19226 | -0.15564 | 0.19684 | 0.16479 | 0.14648 | 0.14191 | 0.1236 | 2.5223 | 121.431 | 0.17395 | 121.3715 | 121.3806 | 121.3348 | 121.4081 | 121.3577 | -121.5225 | -121.5271 | 121.4584 | 121.3943 | 29.837 | 0.88806
1709.375 | 121.6553 | -0.48065 | 121.0419 | -0.15846 | 0.01358 | 0.067746 | 0.068225 | -0.00041873 | -0.006898 | -0.00045074 | -0.11075 | 0.0053107 | 0.067054 | 0.050473 | -0.015806 | 0.027194 | -0.0045117 | 29.0039 | 120.9824 | -0.48523 | 120.8725 | 1.973 | 0.032043 | 0 | 0.16937 | 120.9 | -0.5127 | 120.9045 | -0.3479 | -0.39368 | -0.32044 | -0.004577 | -0.059509 | -0.16937 | 2.4536 | 0.48065 | 0.5127 | 0.48523 | 0.51727 | -0.032043 | -0.14191 | -0.13733 | 0.13275 | 0.16022 | 0.086975 | 0.19226 | 0.11902 | 2.4582 | 121.3577 | 0.1648 | 121.4172 | 121.4676 | 121.4127 | 121.463 | 121.3806 | -121.5271 | -121.5546 | 121.3531 | 121.3852 | 29.4846 | 0.65003
1711.1562 | 121.5912 | -0.52643 | 121.106 | -0.06691 | 0.014648 | 0.067319 | 0.065875 | -0.0034095 | -0.0043344 | -0.00023714 | -0.025299 | 0.0076605 | 0.064704 | 0.044278 | -0.014097 | 0.025058 | -0.0072889 | 28.8162 | 120.9915 | -0.48981 | 120.8817 | 2.0142 | 0.073242 | 0.041199 | 0.29755 | 120.9412 | -0.5127 | 120.8542 | -0.36163 | -0.42572 | -0.39368 | 0.036621 | -0.11444 | -0.2243 | 2.5406 | 0.56763 | 0.59967 | 0.53101 | 0.56305 | 0.013733 | -0.16479 | -0.25177 | 0.1648 | 0.13275 | 0.10071 | 0.11902 | 0.086975 | 2.504 | 121.3715 | 0.15106 | 121.3669 | 121.4813 | 121.4539 | 121.5179 | 121.4676 | -121.5958 | -121.6187 | 121.4081 | 121.3806 | 29.3427 | 0.82397
1712.9844 | 121.669 | -0.44403 | 121.106 | -0.13557 | 0.013366 | 0.069242 | 0.066516 | -0.0025549 | -0.0054026 | -0.00066434 | -0.013092 | 0.0053107 | 0.065986 | 0.051327 | -0.014738 | 0.026553 | -0.0019483 | 28.8071 | 120.9915 | -0.43488 | 120.9732 | 2.1378 | 0.17395 | 0.15564 | 0.24719 | 120.8862 | -0.44403 | 120.9549 | -0.29297 | -0.33417 | -0.28381 | 0.009156 | -0.11444 | -0.13275 | 2.5818 | 0.59967 | 0.61798 | 0.59052 | 0.60882 | 0 | -0.21973 | -0.15106 | 0.15106 | 0.16022 | 0.10986 | 0.16022 | 0.10986 | 2.5726 | 121.4081 | 0.15106 | 121.3989 | 121.4264 | 121.3303 | 121.4355 | 121.3303 | -121.5408 | -121.55 | 121.4172 | 121.3989 | 29.2511 | 0.69122
1714.6875 | 121.6873 | -0.46234 | 121.0831 | -0.15083 | 0.012726 | 0.068387 | 0.066302 | -0.00041873 | -0.007966 | 0.00040366 | -0.040558 | 0.0050971 | 0.063423 | 0.056881 | -0.014097 | 0.026126 | -0.0047253 | 28.6057 | 120.9778 | -0.45319 | 120.9961 | 2.1881 | 0.17853 | 0.16022 | 0.2655 | 120.9091 | -0.47607 | 120.9732 | -0.28839 | -0.32501 | -0.27466 | 0.009155 | -0.10529 | -0.086975 | 2.6505 | 0.62256 | 0.64087 | 0.6134 | 0.63171 | -0.013733 | -0.17395 | -0.10986 | 0.17395 | 0.18768 | 0.13733 | 0.20142 | 0.15106 | 2.6413 | 121.4493 | 0.18768 | 121.4493 | 121.431 | 121.3852 | 121.4401 | 121.3715 | -121.5363 | -121.5591 | 121.4584 | 121.4355 | 29.068 | 0.72784
1716.4375 | 121.7377 | -0.45319 | 121.1288 | -0.16609 | 0.014648 | 0.068173 | 0.067157 | 0.00043587 | -0.00348 | -0.0015189 | -0.077179 | 0.0044561 | 0.063636 | 0.052609 | -0.016874 | 0.026553 | -0.0030163 | 28.5278 | 121.0236 | -0.43945 | 121.0419 | 2.243 | 0.21515 | 0.16479 | 0.27466 | 120.9503 | -0.44403 | 121.0419 | -0.23346 | -0.29755 | -0.22888 | 0.013733 | -0.10528 | -0.086975 | 2.6962 | 0.61798 | 0.66834 | 0.60425 | 0.6546 | 0.009155 | -0.17853 | -0.086975 | 0.21973 | 0.2243 | 0.15564 | 0.21515 | 0.14649 | 2.6825 | 121.4813 | 0.21057 | 121.4859 | 121.463 | 121.3943 | 121.4767 | 121.4035 | -121.5683 | -121.5729 | 121.4951 | 121.4951 | 28.981 | 0.72784
1718.1875 | 121.6187 | -0.5127 | 121.17 | -0.12794 | 0.014007 | 0.068173 | 0.069934 | 0.0015039 | -0.006257 | 0.00040366 | -0.10159 | 0.0068059 | 0.06385 | 0.050473 | -0.01367 | 0.026767 | -0.00066651 | 28.3447 | 121.0464 | -0.48981 | 120.8908 | 2.124 | 0.07782 | 0.032043 | 0.16022 | 120.9778 | -0.49439 | 120.9137 | -0.39368 | -0.44861 | -0.37079 | 0.022888 | -0.1236 | -0.27924 | 2.6367 | 0.54474 | 0.59052 | 0.52185 | 0.56763 | 0.01831 | -0.19226 | -0.25635 | 0.11902 | 0.14191 | 0.064087 | 0.1236 | 0.045777 | 2.6138 | 121.3806 | 0.10071 | 121.4081 | 121.5363 | 121.4722 | 121.5591 | 121.4905 | -121.6599 | -121.6644 | 121.4035 | 121.4264 | 28.8574 | 0.67291
1719.8906 | 121.637 | -0.49439 | 121.1334 | -0.11269 | 0.014435 | 0.068814 | 0.069079 | 0.00086307 | -0.0056162 | -2.3544e-05 | -0.11685 | 0.0078741 | 0.066841 | 0.05325 | -0.014738 | 0.028049 | -0.0021619 | 28.1525 | 121.0556 | -0.48981 | 120.9229 | 2.1927 | 0.10529 | 0.091553 | 0.16022 | 120.9686 | -0.49439 | 120.9457 | -0.38452 | -0.42572 | -0.36621 | 0.004578 | -0.07782 | -0.21057 | 2.6871 | 0.58594 | 0.59967 | 0.58136 | 0.59509 | 0 | -0.16479 | -0.18768 | 0.10986 | 0.12817 | 0.068665 | 0.12817 | 0.068665 | 2.6825 | 121.4127 | 0.10986 | 121.4401 | 121.5454 | 121.463 | 121.55 | 121.463 | -121.6232 | -121.6278 | 121.4172 | 121.4401 | 28.6469 | 0.6546
1721.6562 | 121.6232 | -0.49896 | 121.1472 | -0.15083 | 0.014221 | 0.069669 | 0.069293 | -0.00041873 | -0.004548 | -2.3544e-05 | -0.098541 | 0.0083013 | 0.068122 | 0.048977 | -0.014738 | 0.027408 | -0.0057935 | 27.5665 | 121.0464 | -0.48065 | 120.932 | 2.2339 | 0.10986 | 0.086975 | 0.16937 | 120.9824 | -0.50812 | 120.9274 | -0.39825 | -0.46234 | -0.37537 | 0.01831 | -0.10071 | -0.21515 | 2.7328 | 0.58594 | 0.60883 | 0.56763 | 0.59052 | -0.009156 | -0.16479 | -0.21973 | 0.10071 | 0.1236 | 0.036621 | 0.13275 | 0.045777 | 2.7145 | 121.4127 | 0.10986 | 121.4355 | 121.5271 | 121.4905 | 121.5454 | 121.4813 | -121.6278 | -121.6553 | 121.431 | 121.4264 | 28.0655 | 0.66834
1723.3438 | 121.6415 | -0.50812 | 121.1792 | -0.10506 | 0.012512 | 0.068814 | 0.066943 | -0.0023413 | -0.0054026 | 0.00040366 | -0.046661 | 0.0068059 | 0.063636 | 0.046414 | -0.01367 | 0.026767 | -0.0034435 | 27.3788 | 121.0602 | -0.50354 | 120.9274 | 2.2156 | 0.18768 | 0.12817 | 0.29755 | 120.9778 | -0.49896 | 120.9183 | -0.36163 | -0.40283 | -0.37994 | 0.004578 | -0.11902 | -0.25177 | 2.7237 | 0.63629 | 0.6958 | 0.63171 | 0.69122 | 0.009156 | -0.20142 | -0.26093 | 0.14648 | 0.12817 | 0.10529 | 0.11902 | 0.09613 | 2.7191 | 121.431 | 0.13733 | 121.4172 | 121.5637 | 121.4767 | 121.5683 | 121.4859 | -121.6827 | -121.6782 | 121.4355 | 121.4264 | 27.887 | 0.80566
1725.0938 | 121.6873 | -0.49439 | 121.1426 | -0.12794 | 0.014007 | 0.06796 | 0.068438 | -0.0014867 | -0.0043344 | 0.0033945 | -0.046661 | 0.0085149 | 0.064491 | 0.048123 | -0.013029 | 0.028476 | -0.0023755 | 27.2003 | 121.0556 | -0.49439 | 120.9503 | 2.3163 | 0.19226 | 0.1236 | 0.30212 | 120.9961 | -0.50812 | 120.9641 | -0.34332 | -0.39368 | -0.36163 | 0 | -0.086975 | -0.19226 | 2.8107 | 0.61798 | 0.68665 | 0.61798 | 0.68665 | -0.013733 | -0.14648 | -0.17853 | 0.15106 | 0.13275 | 0.10071 | 0.14648 | 0.11444 | 2.8107 | 121.4447 | 0.16479 | 121.4722 | 121.55 | 121.5042 | 121.55 | 121.4905 | -121.637 | -121.6507 | 121.4447 | 121.4584 | 27.6947 | 0.79651
1726.8438 | 121.6827 | -0.4715 | 121.1746 | -0.11269 | 0.014862 | 0.067533 | 0.06972 | 0.0027857 | -0.0056162 | -0.00066434 | -0.092438 | 0.0044561 | 0.065132 | 0.045559 | -0.014951 | 0.02933 | -0.0070751 | 25.7538 | 121.051 | -0.46234 | 121.0144 | 2.4445 | 0.24261 | 0.1831 | 0.32959 | 121.0098 | -0.48065 | 121.0007 | -0.31586 | -0.37994 | -0.31586 | 0.009156 | -0.1236 | -0.16022 | 2.916 | 0.6546 | 0.71411 | 0.64545 | 0.70496 | -0.009155 | -0.16479 | -0.17395 | 0.15564 | 0.15564 | 0.091553 | 0.1648 | 0.10071 | 2.9068 | 121.4767 | 0.1648 | 121.4813 | 121.5134 | 121.4905 | 121.5225 | 121.4813 | -121.637 | -121.6553 | 121.4859 | 121.4722 | 26.2253 | 0.80109
1728.5938 | 121.7148 | -0.50354 | 121.1609 | -0.089798 | 0.015503 | 0.06796 | 0.066943 | -0.0019141 | -0.0058298 | 0.0023265 | -0.074127 | 0.0070197 | 0.063636 | 0.045346 | -0.013883 | 0.027194 | -0.0030163 | 25.7904 | 121.0281 | -0.48981 | 120.9869 | 2.4536 | 0.2243 | 0.17853 | 0.33875 | 120.9686 | -0.49896 | 120.9778 | -0.32959 | -0.39368 | -0.3479 | 0.013733 | -0.13275 | -0.17395 | 2.9572 | 0.68207 | 0.72784 | 0.66834 | 0.71411 | 0.004578 | -0.19226 | -0.18311 | 0.17395 | 0.15564 | 0.10986 | 0.15106 | 0.10529 | 2.9434 | 121.4767 | 0.16937 | 121.4767 | 121.5179 | 121.4676 | 121.5317 | 121.4722 | -121.6507 | -121.6599 | 121.4905 | 121.4813 | 26.2939 | 0.84228
1730.2812 | 121.6644 | -0.52185 | 121.1655 | -0.12794 | 0.015503 | 0.070096 | 0.067584 | -0.0012731 | -0.004548 | -0.00087794 | -0.077179 | 0.0053107 | 0.064918 | 0.046414 | -0.011961 | 0.02869 | -0.0051525 | 26.3397 | 121.0464 | -0.50812 | 120.9091 | 2.3117 | 0.16479 | 0.11444 | 0.14191 | 121.0052 | -0.53101 | 120.932 | -0.41657 | -0.4715 | -0.41199 | 0.013733 | -0.11902 | -0.25635 | 2.8336 | 0.63629 | 0.68665 | 0.62256 | 0.67291 | -0.009155 | -0.16022 | -0.23346 | 0.10529 | 0.10986 | 0.050354 | 0.11902 | 0.059509 | 2.8198 | 121.4172 | 0.11444 | 121.463 | 121.5546 | 121.5363 | 121.5683 | 121.5271 | -121.6736 | -121.6965 | 121.431 | 121.4539 | 26.8616 | 0.66376
1732.0312 | 121.7194 | -0.53558 | 121.1426 | -0.044022 | 0.014435 | 0.068814 | 0.064593 | -0.0017005 | -0.0075388 | 0.0018991 | 0.014374 | 0.0048833 | 0.064491 | 0.048977 | -0.01602 | 0.027194 | -0.0040845 | 25.8591 | 121.0098 | -0.48065 | 121.0281 | 2.5314 | 0.32501 | 0.23804 | 0.39368 | 121.0007 | -0.48981 | 120.9595 | -0.35248 | -0.37537 | -0.36163 | 0.054931 | -0.13275 | -0.11444 | 3.067 | 0.77362 | 0.86059 | 0.71869 | 0.80566 | 0.045776 | -0.14191 | -0.1831 | 0.18311 | 0.17395 | 0.16022 | 0.12817 | 0.11444 | 3.0121 | 121.5088 | 0.13733 | 121.4493 | 121.4905 | 121.4905 | 121.5454 | 121.5363 | -121.6232 | -121.6324 | 121.5637 | 121.4951 | 26.3947 | 0.92926
1733.7812 | 121.7697 | -0.52185 | 121.1472 | -0.15846 | 0.013794 | 0.069242 | 0.065875 | -0.0027685 | -0.0043344 | 0.0012583 | 0.0021667 | 0.0068059 | 0.065345 | 0.049405 | -0.01367 | 0.02634 | -0.0040845 | 24.2569 | 121.0373 | -0.47607 | 120.9869 | 2.5543 | 0.32959 | 0.25177 | 0.24261 | 120.9595 | -0.5127 | 121.0098 | -0.32501 | -0.35706 | -0.33875 | 0.045777 | -0.10986 | -0.16022 | 3.0762 | 0.77362 | 0.85144 | 0.72784 | 0.80566 | 0.009156 | -0.18768 | -0.13733 | 0.19684 | 0.18311 | 0.16479 | 0.17395 | 0.15564 | 3.0304 | 121.463 | 0.18768 | 121.5225 | 121.5134 | 121.4722 | 121.5591 | 121.4813 | -121.6232 | -121.6599 | 121.5088 | 121.5317 | 24.7787 | 0.76447
1735.4688 | 121.701 | -0.50812 | 121.1975 | -0.19661 | 0.014221 | 0.06796 | 0.069507 | 0.0010767 | -0.002839 | -0.0013051 | -0.09549 | 0.0048833 | 0.065559 | 0.047482 | -0.014311 | 0.028049 | -0.0064343 | 24.2981 | 121.0785 | -0.47607 | 121.0052 | 2.5589 | 0.33417 | 0.23346 | 0.28839 | 121.0144 | -0.48523 | 121.0052 | -0.37079 | -0.41657 | -0.35706 | 0.032044 | -0.11902 | -0.19226 | 3.067 | 0.74158 | 0.84228 | 0.70953 | 0.81024 | 0.022889 | -0.18311 | -0.19226 | 0.13733 | 0.15106 | 0.091553 | 0.12817 | 0.068664 | 3.035 | 121.4813 | 0.11444 | 121.4905 | 121.5546 | 121.4996 | 121.5866 | 121.5225 | -121.6736 | -121.6827 | 121.5134 | 121.5134 | 24.8062 | 0.79651
1737.2344 | 121.6827 | -0.50354 | 121.225 | -0.13557 | 0.015075 | 0.069882 | 0.068866 | 0.00086307 | -0.0041208 | 0.0014719 | -0.098541 | 0.0053107 | 0.062995 | 0.050046 | -0.016233 | 0.027408 | -0.0062207 | 24.2294 | 121.1014 | -0.4715 | 120.9961 | 2.6001 | 0.30212 | 0.21973 | 0.2243 | 121.0327 | -0.50354 | 120.9732 | -0.39825 | -0.43945 | -0.37537 | 0.032043 | -0.1236 | -0.22888 | 3.1036 | 0.72327 | 0.80566 | 0.69122 | 0.77362 | 0 | -0.19226 | -0.25177 | 0.10529 | 0.12817 | 0.064087 | 0.12817 | 0.064087 | 3.0716 | 121.4676 | 0.10529 | 121.4767 | 121.5729 | 121.5363 | 121.6049 | 121.5363 | -121.6965 | -121.7285 | 121.4996 | 121.4767 | 24.733 | 0.72784
1739 | 121.6919 | -0.51727 | 121.2387 | -0.12032 | 0.014862 | 0.068601 | 0.065661 | -0.0040503 | -0.0058298 | 0.0025401 | -0.0039367 | 0.0044561 | 0.064277 | 0.046414 | -0.014738 | 0.027408 | -0.0040845 | 24.1379 | 121.1014 | -0.48981 | 120.9824 | 2.6367 | 0.32044 | 0.24261 | 0.31586 | 121.0236 | -0.49896 | 120.9641 | -0.35706 | -0.39825 | -0.38452 | 0.027466 | -0.13733 | -0.25635 | 3.154 | 0.75989 | 0.83771 | 0.73242 | 0.81024 | 0.018311 | -0.21515 | -0.27466 | 0.16022 | 0.13275 | 0.11902 | 0.11444 | 0.10071 | 3.1265 | 121.4722 | 0.14191 | 121.463 | 121.5912 | 121.5225 | 121.6187 | 121.5408 | -121.7285 | -121.7377 | 121.4996 | 121.4813 | 24.6552 | 0.83313
1740.75 | 121.6919 | -0.50812 | 121.2387 | -0.11269 | 0.015716 | 0.069242 | 0.069079 | 0.00043587 | -0.00348 | -2.3544e-05 | -0.09549 | 0.0050971 | 0.065559 | 0.051755 | -0.016447 | 0.027194 | -0.0032299 | 24.1058 | 121.1334 | -0.4715 | 120.9824 | 2.6459 | 0.29755 | 0.21515 | 0.15564 | 121.0281 | -0.48981 | 120.9961 | -0.40741 | -0.46692 | -0.38452 | 0.036621 | -0.10529 | -0.25635 | 3.154 | 0.72327 | 0.80566 | 0.68665 | 0.76904 | 0.018311 | -0.21057 | -0.24261 | 0.10071 | 0.1236 | 0.041199 | 0.10529 | 0.022888 | 3.1174 | 121.4539 | 0.082397 | 121.4859 | 121.6049 | 121.5179 | 121.6415 | 121.5363 | -121.7102 | -121.7285 | 121.4905 | 121.5042 | 24.614 | 0.66376
1742.4531 | 121.6873 | -0.50354 | 121.2479 | -0.11269 | 0.016571 | 0.070523 | 0.06972 | 0.0021447 | -0.0049754 | 0.0018991 | -0.089386 | 0.0053107 | 0.0662 | 0.049618 | -0.014311 | 0.027194 | -0.0040845 | 24.1882 | 121.1426 | -0.48065 | 120.9961 | 2.7191 | 0.31586 | 0.22888 | 0.15106 | 121.0693 | -0.49896 | 120.9915 | -0.41199 | -0.44403 | -0.3891 | 0.022888 | -0.10529 | -0.25177 | 3.2227 | 0.73242 | 0.8194 | 0.70953 | 0.79651 | 0.004578 | -0.17853 | -0.25635 | 0.091553 | 0.11444 | 0.059509 | 0.10986 | 0.054931 | 3.1998 | 121.4767 | 0.086975 | 121.4905 | 121.6232 | 121.5683 | 121.6461 | 121.5729 | -121.7285 | -121.7468 | 121.4996 | 121.4951 | 24.6918 | 0.6546
1744.2031 | 121.8018 | -0.46234 | 121.2067 | -0.17372 | 0.014648 | 0.069028 | 0.066089 | 0.00086307 | -0.0054026 | 0.0027537 | -0.01004 | 0.0057379 | 0.065132 | 0.054104 | -0.013456 | 0.025699 | -0.0045117 | 24.2477 | 121.0785 | -0.45319 | 121.1151 | 2.9388 | 0.48523 | 0.37994 | 0.4303 | 121.0327 | -0.46692 | 121.0876 | -0.23804 | -0.27466 | -0.26093 | 0.009155 | -0.12817 | -0.091553 | 3.4012 | 0.84228 | 0.94757 | 0.83313 | 0.93841 | -0.004578 | -0.17395 | -0.11902 | 0.2243 | 0.20142 | 0.18768 | 0.20599 | 0.19226 | 3.392 | 121.5683 | 0.22888 | 121.5546 | 121.5317 | 121.4996 | 121.5408 | 121.4951 | -121.6599 | -121.6736 | 121.5775 | 121.55 | 24.7101 | 0.89264
1745.9531 | 121.8338 | -0.43488 | 121.2112 | -0.15083 | 0.011657 | 0.068173 | 0.06438 | -0.0029821 | -0.0039072 | 0.0025401 | 0.035736 | 0.0053107 | 0.062782 | 0.052395 | -0.014738 | 0.025485 | -0.0047253 | 24.1333 | 121.0968 | -0.45776 | 121.1563 | 3.035 | 0.51727 | 0.40741 | 0.44861 | 121.0373 | -0.44403 | 121.1105 | -0.21057 | -0.25177 | -0.24719 | -0.022889 | -0.11444 | -0.054932 | 3.4698 | 0.84228 | 0.95215 | 0.86517 | 0.97504 | -0.009156 | -0.17395 | -0.10071 | 0.2243 | 0.18768 | 0.18311 | 0.19684 | 0.19226 | 3.4927 | 121.6141 | 0.23346 | 121.5546 | 121.5546 | 121.4813 | 121.5317 | 121.4722 | -121.669 | -121.6553 | 121.5912 | 121.5454 | 24.5682 | 0.88348
1747.7188 | 121.7285 | -0.48065 | 121.2479 | -0.11269 | 0.016571 | 0.068814 | 0.070575 | -0.0023413 | -0.0039072 | 0.0029673 | -0.092438 | 0.0055243 | 0.065345 | 0.051327 | -0.015806 | 0.02634 | -0.0066479 | 23.9777 | 121.1563 | -0.43945 | 121.0739 | 2.9709 | 0.42572 | 0.32959 | 0.29755 | 121.0739 | -0.48523 | 121.051 | -0.32959 | -0.3891 | -0.32959 | 0.041199 | -0.091553 | -0.17395 | 3.4515 | 0.81024 | 0.90637 | 0.76904 | 0.86517 | -0.004577 | -0.17395 | -0.19684 | 0.15106 | 0.15106 | 0.091553 | 0.15564 | 0.09613 | 3.4103 | 121.5134 | 0.15564 | 121.5363 | 121.5958 | 121.5591 | 121.637 | 121.5546 | -121.6873 | -121.7331 | 121.5546 | 121.5317 | 24.4583 | 0.7782
1749.4688 | 121.8475 | -0.43945 | 121.2067 | -0.2195 | 0.016998 | 0.07031 | 0.068438 | -0.0010595 | -0.0041208 | 0.00040366 | -0.025299 | 0.0048833 | 0.063636 | 0.056241 | -0.015379 | 0.026553 | -0.0070751 | 24.0921 | 121.1426 | -0.40741 | 121.1517 | 3.0991 | 0.50812 | 0.46234 | 0.3067 | 121.0464 | -0.44861 | 121.1472 | -0.2243 | -0.2655 | -0.2243 | 0.032043 | -0.064087 | -0.054932 | 3.5385 | 0.90179 | 0.94757 | 0.86975 | 0.91553 | -0.009155 | -0.16022 | -0.059509 | 0.21515 | 0.21515 | 0.17395 | 0.2243 | 0.18311 | 3.5065 | 121.5591 | 0.2243 | 121.5958 | 121.55 | 121.4951 | 121.582 | 121.4859 | -121.6141 | -121.6553 | 121.5912 | 121.5866 | 24.5316 | 0.74615
1751.1562 | 121.8475 | -0.4303 | 121.2158 | -0.12794 | 0.015716 | 0.067746 | 0.071643 | 0.00043587 | -0.0019846 | 0.00083106 | -0.046661 | 0.0059515 | 0.062354 | 0.052823 | -0.015592 | 0.02634 | -0.0042981 | 24.1699 | 121.17 | -0.43488 | 121.1243 | 3.0853 | 0.89722 | 0.41657 | 0.24719 | 121.0739 | -0.46234 | 121.1655 | -0.23804 | -0.29297 | -0.21515 | -0.004577 | -0.045776 | -0.091552 | 3.5156 | 0.84686 | 1.3275 | 0.85144 | 1.3321 | -0.032043 | -0.14191 | -0.050354 | 0.19226 | 0.21515 | 0.13733 | 0.24719 | 0.16937 | 3.5202 | 121.5591 | 0.2243 | 121.6278 | 121.6049 | 121.5363 | 121.6003 | 121.5042 | -121.6507 | -121.6782 | 121.5546 | 121.5958 | 24.6002 | 0.67749
1752.9219 | 121.8704 | -0.41657 | 121.2158 | -0.11269 | 0.015503 | 0.070737 | 0.072284 | 0.0038537 | 0.0029288 | 0.0023265 | -0.04361 | 0.0072333 | 0.065345 | 0.052823 | -0.013456 | 0.026553 | -0.0021619 | 24.2477 | 121.17 | -0.42114 | 121.1517 | 3.1494 | 1.0254 | 0.45776 | 0.27924 | 121.0648 | -0.44403 | 121.1746 | -0.2243 | -0.27924 | -0.20142 | -0.004578 | -0.045776 | -0.064087 | 3.566 | 0.87433 | 1.442 | 0.87891 | 1.4465 | -0.027466 | -0.15106 | -0.041198 | 0.19226 | 0.21515 | 0.13733 | 0.24261 | 0.1648 | 3.5706 | 121.5729 | 0.21973 | 121.6187 | 121.5912 | 121.5088 | 121.5866 | 121.4813 | -121.637 | -121.6599 | 121.5683 | 121.5912 | 24.6643 | 0.6958
1754.6094 | 121.756 | -0.46234 | 121.2799 | -0.13557 | 0.016571 | 0.07031 | 0.075702 | 0.00022207 | 0.00036525 | 0.0014719 | -0.1199 | 0.0072333 | 0.064918 | 0.052182 | -0.013242 | 0.024204 | -0.0057935 | 24.2111 | 121.2067 | -0.44861 | 121.0419 | 3.0716 | 0.90179 | 0.35248 | 0.15106 | 121.1197 | -0.48065 | 121.0648 | -0.37537 | -0.40741 | -0.33417 | 0.013733 | -0.073242 | -0.23804 | 3.5339 | 0.81482 | 1.3641 | 0.80109 | 1.3504 | -0.018311 | -0.16022 | -0.21515 | 0.086975 | 0.12817 | 0.054931 | 0.14649 | 0.073242 | 3.5202 | 121.4905 | 0.10529 | 121.5454 | 121.6553 | 121.6003 | 121.669 | 121.582 | -121.7285 | -121.7606 | 121.5042 | 121.5271 | 24.6735 | 0.6134
1756.3438 | 121.8246 | -0.41657 | 121.2662 | -0.15083 | 0.015289 | 0.069028 | 0.071429 | -0.0042639 | -0.00070275 | 0.0012583 | 0.0021667 | 0.0059515 | 0.066413 | 0.0462 | -0.015165 | 0.027194 | -0.0040845 | 24.202 | 121.17 | -0.41199 | 121.1243 | 3.2181 | 1.0208 | 0.45776 | 0.27924 | 121.0739 | -0.44861 | 121.1426 | -0.2655 | -0.28839 | -0.26093 | 0.004578 | -0.09613 | -0.14191 | 3.6346 | 0.87433 | 1.4374 | 0.86975 | 1.4328 | -0.032043 | -0.19226 | -0.1236 | 0.15106 | 0.15564 | 0.12817 | 0.18768 | 0.16022 | 3.6301 | 121.5363 | 0.18311 | 121.5912 | 121.582 | 121.5225 | 121.5866 | 121.4905 | -121.6782 | -121.7148 | 121.5408 | 121.5591 | 24.6185 | 0.6958
1758.125 | 121.8384 | -0.44403 | 121.3074 | -0.12032 | 0.017425 | 0.070096 | 0.072924 | -0.0057593 | -0.001771 | 0.0044627 | -0.016144 | 0.0044561 | 0.063209 | 0.044705 | -0.014311 | 0.026767 | -0.0047253 | 24.1241 | 121.1609 | -0.41657 | 121.1975 | 3.3554 | 1.0574 | 0.53101 | 0.4303 | 121.0922 | -0.4303 | 121.1563 | -0.2243 | -0.24719 | -0.23804 | 0.027466 | -0.14648 | -0.10986 | 3.7994 | 0.97504 | 1.5015 | 0.94757 | 1.474 | 0.013733 | -0.21515 | -0.15106 | 0.21973 | 0.20599 | 0.19684 | 0.19226 | 0.18311 | 3.772 | 121.6141 | 0.20599 | 121.5866 | 121.5775 | 121.5225 | 121.6049 | 121.5363 | -121.7239 | -121.7377 | 121.6415 | 121.6003 | 24.5682 | 0.87433
1759.8281 | 121.8796 | -0.3891 | 121.2708 | -0.13557 | 0.016357 | 0.068814 | 0.071002 | -0.0078955 | -0.0019846 | 0.0012583 | 0.011322 | 0.0053107 | 0.06385 | 0.052823 | -0.014524 | 0.026981 | -0.0077161 | 24.0646 | 121.1929 | -0.39825 | 121.2387 | 3.447 | 1.181 | 0.56763 | 0.46234 | 121.1014 | -0.42114 | 121.2067 | -0.17395 | -0.20599 | -0.19684 | -0.009155 | -0.07782 | -0.032044 | 3.8361 | 0.95673 | 1.5701 | 0.96588 | 1.5793 | -0.032044 | -0.16937 | -0.064087 | 0.21515 | 0.19226 | 0.1831 | 0.2243 | 0.21515 | 3.8452 | 121.637 | 0.24719 | 121.6278 | 121.5912 | 121.5225 | 121.582 | 121.4905 | -121.669 | -121.6919 | 121.6278 | 121.5958 | 24.4537 | 0.85144
1761.5625 | 121.8018 | -0.45776 | 121.312 | -0.16609 | 0.015503 | 0.067533 | 0.071002 | -0.00084593 | 0.00015165 | 0.0033945 | -0.031403 | 0.0040289 | 0.062995 | 0.062008 | -0.014738 | 0.026553 | -0.0062207 | 24.0189 | 121.1426 | -0.41657 | 121.1792 | 3.4332 | 1.149 | 0.53101 | 0.41657 | 121.1334 | -0.43488 | 121.1288 | -0.27008 | -0.30212 | -0.29297 | 0.041199 | -0.16937 | -0.13275 | 3.891 | 0.98877 | 1.6068 | 0.94757 | 1.5656 | 0.022889 | -0.17853 | -0.18311 | 0.18768 | 0.1648 | 0.15564 | 0.14191 | 0.13275 | 3.8498 | 121.5958 | 0.16479 | 121.5637 | 121.5591 | 121.5683 | 121.6003 | 121.5912 | -121.7285 | -121.7468 | 121.637 | 121.5866 | 24.4766 | 0.87433
1763.25 | 121.7651 | -0.48981 | 121.3669 | -0.10506 | 0.016784 | 0.070096 | 0.07207 | -0.00063233 | -0.00048915 | 0.0018991 | -0.058869 | 0.0074469 | 0.064918 | 0.045987 | -0.015592 | 0.025912 | -0.0038709 | 24.0417 | 121.2021 | -0.44403 | 121.0968 | 3.3646 | 1.1719 | 0.44403 | 0.3067 | 121.1609 | -0.45319 | 121.0831 | -0.32959 | -0.36621 | -0.32501 | 0.045776 | -0.16479 | -0.27008 | 3.8544 | 0.93384 | 1.6617 | 0.88806 | 1.6159 | 0.036621 | -0.20599 | -0.28381 | 0.16022 | 0.16479 | 0.1236 | 0.12817 | 0.086975 | 3.8086 | 121.5408 | 0.1236 | 121.5363 | 121.6461 | 121.6141 | 121.6919 | 121.6507 | -121.8109 | -121.8201 | 121.5866 | 121.5729 | 24.5316 | 0.79651
1765 | 121.8887 | -0.38452 | 121.3211 | -0.20424 | 0.018707 | 0.067746 | 0.074847 | 0.0015039 | 0.00079245 | -0.00087794 | -0.052765 | 0.0042425 | 0.064704 | 0.057736 | -0.014738 | 0.027621 | -0.0045117 | 24.2661 | 121.1792 | -0.37537 | 121.2387 | 3.598 | 1.3321 | 0.60425 | 0.30212 | 121.1563 | -0.40741 | 121.2433 | -0.17853 | -0.21973 | -0.1831 | 0.009155 | -0.14191 | -0.082398 | 3.9825 | 0.98877 | 1.7166 | 0.97961 | 1.7075 | -0.022889 | -0.16479 | -0.07782 | 0.20599 | 0.20142 | 0.16479 | 0.22431 | 0.18768 | 3.9734 | 121.6141 | 0.22888 | 121.6507 | 121.5546 | 121.5637 | 121.5637 | 121.5408 | -121.6965 | -121.7285 | 121.6232 | 121.6278 | 24.6506 | 0.68664
1766.75 | 121.8796 | -0.3479 | 121.3669 | -0.12794 | 0.016144 | 0.07031 | 0.074633 | -0.0044775 | 0.0020742 | 0.00061746 | -0.01004 | 0.0031745 | 0.064918 | 0.05325 | -0.01367 | 0.025485 | -0.0060071 | 24.1791 | 121.2341 | -0.31586 | 121.2845 | 3.7079 | 1.4877 | 0.65918 | 0.46234 | 121.2112 | -0.34332 | 121.2845 | -0.1236 | -0.16022 | -0.14648 | 0.032043 | -0.13275 | -0.082397 | 4.0558 | 1.0071 | 1.8356 | 0.97504 | 1.8036 | 0.004577 | -0.15564 | -0.082397 | 0.2243 | 0.20142 | 0.18768 | 0.19684 | 0.18311 | 4.0237 | 121.6003 | 0.21973 | 121.6278 | 121.55 | 121.5546 | 121.582 | 121.5591 | -121.6827 | -121.7102 | 121.6324 | 121.6324 | 24.527 | 0.81024
1768.4375 | 121.7697 | -0.39825 | 121.4172 | -0.074539 | 0.014435 | 0.069455 | 0.07442 | -0.00041873 | -0.00070275 | 0.00083106 | -0.058869 | 0.0063787 | 0.065772 | 0.057736 | -0.01367 | 0.026767 | -0.0010937 | 24.0646 | 121.2845 | -0.37079 | 121.1792 | 3.6255 | 1.2039 | 0.56305 | 0.31128 | 121.2341 | -0.37537 | 121.1655 | -0.26093 | -0.31128 | -0.28381 | 0.027465 | -0.13275 | -0.23804 | 4.0237 | 0.9613 | 1.6022 | 0.93384 | 1.5747 | 0.022888 | -0.1831 | -0.25177 | 0.13733 | 0.11444 | 0.086975 | 0.091553 | 0.064087 | 3.9963 | 121.55 | 0.11444 | 121.5408 | 121.6553 | 121.6095 | 121.6827 | 121.6324 | -121.788 | -121.7926 | 121.5775 | 121.5637 | 24.4629 | 0.70953
1770.1875 | 121.8201 | -0.36621 | 121.4401 | -0.1432 | 0.01828 | 0.071164 | 0.075915 | -0.00063233 | 0.0029288 | -0.0013051 | -0.1199 | 0.0089423 | 0.064918 | 0.047268 | -0.013883 | 0.028262 | -0.0049389 | 24.2661 | 121.312 | -0.3479 | 121.1838 | 3.7079 | 1.3779 | 0.58594 | 0.16022 | 121.2753 | -0.36163 | 121.2341 | -0.21057 | -0.27008 | -0.20142 | 0.018311 | -0.12817 | -0.25635 | 4.0741 | 0.95215 | 1.7441 | 0.93384 | 1.7258 | 0.004578 | -0.16479 | -0.20599 | 0.15564 | 0.16479 | 0.09613 | 0.16022 | 0.091552 | 4.0558 | 121.5317 | 0.15106 | 121.5958 | 121.6599 | 121.637 | 121.6782 | 121.6415 | -121.788 | -121.8018 | 121.55 | 121.6003 | 24.6323 | 0.52643
1771.9375 | 121.8475 | -0.32044 | 121.4035 | -0.15083 | 0.016571 | 0.069455 | 0.073138 | -0.0042639 | -0.0013438 | 0.0018991 | -0.016144 | 0.0044561 | 0.062782 | 0.051755 | -0.013883 | 0.02634 | -0.0064343 | 24.0555 | 121.2982 | -0.31586 | 121.2708 | 3.8681 | 1.3275 | 0.69122 | 0.24719 | 121.2433 | -0.33875 | 121.2891 | -0.15564 | -0.19684 | -0.14648 | 0.004578 | -0.10528 | -0.13275 | 4.1885 | 1.0117 | 1.648 | 1.0071 | 1.6434 | -0.01831 | -0.16022 | -0.11444 | 0.1648 | 0.17395 | 0.1236 | 0.19226 | 0.14191 | 4.184 | 121.5866 | 0.18311 | 121.6278 | 121.6141 | 121.582 | 121.6187 | 121.5637 | -121.7194 | -121.7422 | 121.5912 | 121.6095 | 24.3759 | 0.56763
1773.7031 | 121.8201 | -0.31586 | 121.4539 | -0.15083 | 0.016571 | 0.069242 | 0.075274 | -0.00084593 | -0.00027555 | 0.0025401 | -0.11685 | 0.0046697 | 0.064491 | 0.048337 | -0.014524 | 0.027194 | 0.0012561 | 24.1058 | 121.3623 | -0.31586 | 121.2341 | 3.8406 | 1.2955 | 0.62256 | 0.16022 | 121.3028 | -0.31586 | 121.2891 | -0.17853 | -0.24719 | -0.17395 | 0 | -0.091552 | -0.21973 | 4.1565 | 0.93842 | 1.6113 | 0.93842 | 1.6113 | 0 | -0.15106 | -0.16479 | 0.13733 | 0.14191 | 0.068665 | 0.14191 | 0.068665 | 4.1565 | 121.55 | 0.13733 | 121.6049 | 121.6782 | 121.6187 | 121.6782 | 121.6187 | -121.7697 | -121.7697 | 121.55 | 121.6049 | 24.4217 | 0.47607
1775.4375 | 121.8155 | -0.29755 | 121.4996 | -0.13557 | 0.017853 | 0.071591 | 0.077838 | 0.0010767 | 0.0035696 | 0.0014719 | -0.09549 | 0.0053107 | 0.066627 | 0.057736 | -0.01602 | 0.028049 | -0.0023755 | 24.0372 | 121.3943 | -0.30212 | 121.2433 | 3.9139 | 1.3733 | 0.65002 | 0.15564 | 121.3348 | -0.31586 | 121.2891 | -0.19226 | -0.24261 | -0.16937 | -0.004578 | -0.10529 | -0.25635 | 4.2114 | 0.94757 | 1.6708 | 0.95215 | 1.6754 | -0.018311 | -0.16479 | -0.21057 | 0.10528 | 0.12817 | 0.054931 | 0.14648 | 0.073242 | 4.216 | 121.5454 | 0.1236 | 121.6049 | 121.6965 | 121.6507 | 121.6919 | 121.6324 | -121.8018 | -121.8155 | 121.5408 | 121.5866 | 24.3347 | 0.45319
1777.125 | 121.875 | -0.26093 | 121.4676 | -0.19661 | 0.021057 | 0.070523 | 0.075702 | -0.0017005 | 0.0014334 | 0.0033945 | -0.028351 | 0.0042425 | 0.064277 | 0.051327 | -0.013029 | 0.025699 | -0.0089977 | 24.1653 | 121.3531 | -0.26093 | 121.3486 | 4.1107 | 1.506 | 0.76904 | 0.28381 | 121.2753 | -0.27466 | 121.3486 | -0.09613 | -0.13275 | -0.082397 | 0 | -0.11444 | -0.11902 | 4.3716 | 1.03 | 1.767 | 1.03 | 1.767 | -0.013733 | -0.19226 | -0.11902 | 0.1648 | 0.17853 | 0.12817 | 0.19226 | 0.14191 | 4.3716 | 121.6095 | 0.17853 | 121.6232 | 121.6141 | 121.55 | 121.6141 | 121.5363 | -121.7285 | -121.7422 | 121.6095 | 121.6095 | 24.4263 | 0.54474
1778.875 | 121.8018 | -0.31586 | 121.5225 | -0.082169 | 0.01828 | 0.069669 | 0.074847 | -0.0017005 | 0.0010062 | 0.0031809 | -0.071076 | 0.0059515 | 0.064491 | 0.053677 | -0.01367 | 0.026981 | -0.0053661 | 24.1333 | 121.4035 | -0.30212 | 121.2845 | 4.0466 | 1.5427 | 0.6958 | 0.31128 | 121.3669 | -0.30212 | 121.2662 | -0.16937 | -0.2243 | -0.19226 | 0.013733 | -0.11902 | -0.23804 | 4.3625 | 1.0117 | 1.8585 | 0.99792 | 1.8448 | 0.013733 | -0.15564 | -0.25635 | 0.14648 | 0.1236 | 0.091553 | 0.10986 | 0.07782 | 4.3488 | 121.5866 | 0.13275 | 121.5683 | 121.7056 | 121.669 | 121.7194 | 121.6827 | -121.8246 | -121.8246 | 121.6003 | 121.582 | 24.4492 | 0.62714
1780.6406 | 121.9208 | -0.26093 | 121.4767 | -0.16609 | 0.018493 | 0.071378 | 0.075488 | -0.0014867 | 0.0014334 | 0.0042491 | -0.0069885 | 0.0038153 | 0.064491 | 0.052182 | -0.015379 | 0.024417 | -0.0051525 | 24.5499 | 121.3348 | -0.24719 | 121.4172 | 4.2801 | 1.8082 | 0.84228 | 0.44861 | 121.312 | -0.27008 | 121.4035 | -0.032043 | -0.07782 | -0.059509 | 0.013733 | -0.14191 | -0.05951 | 4.541 | 1.1032 | 2.0691 | 1.0895 | 2.0554 | -0.009156 | -0.1648 | -0.073243 | 0.22888 | 0.20142 | 0.18311 | 0.21057 | 0.19226 | 4.5273 | 121.6644 | 0.23804 | 121.6736 | 121.582 | 121.582 | 121.5958 | 121.5729 | -121.7239 | -121.7468 | 121.6782 | 121.6644 | 24.8108 | 0.70953
1782.3906 | 121.8979 | -0.24719 | 121.4859 | -0.15083 | 0.02127 | 0.072019 | 0.072711 | 0.0017175 | 0.0027152 | 0.0042491 | -0.031403 | 0.0016791 | 0.065345 | 0.053891 | -0.016874 | 0.025485 | -0.0032299 | 24.5316 | 121.376 | -0.25177 | 121.3898 | 4.3167 | 1.6983 | 0.83313 | 0.30212 | 121.312 | -0.25177 | 121.3989 | -0.064087 | -0.091553 | -0.068665 | -0.004578 | -0.10986 | -0.09613 | 4.5639 | 1.0803 | 1.9455 | 1.0849 | 1.9501 | -0.004578 | -0.17395 | -0.086975 | 0.1831 | 0.17853 | 0.15564 | 0.1831 | 0.16022 | 4.5685 | 121.6415 | 0.18768 | 121.6507 | 121.6278 | 121.5637 | 121.6232 | 121.5591 | -121.7377 | -121.7377 | 121.637 | 121.6461 | 24.7787 | 0.54932
1784.1406 | 121.8338 | -0.27466 | 121.5408 | -0.12794 | 0.019561 | 0.072019 | 0.073779 | -0.0027685 | 0.0027152 | 0.0031809 | -0.034454 | 0.0027471 | 0.065132 | 0.049405 | -0.014951 | 0.027194 | -0.0049389 | 24.6963 | 121.3715 | -0.24719 | 121.3806 | 4.3396 | 1.6205 | 0.82398 | 0.3891 | 121.3577 | -0.27924 | 121.3165 | -0.11902 | -0.16479 | -0.16937 | 0.027466 | -0.16937 | -0.16022 | 4.6143 | 1.0986 | 1.8951 | 1.0712 | 1.8677 | -0.004578 | -0.18311 | -0.22431 | 0.15564 | 0.10529 | 0.10986 | 0.10986 | 0.11444 | 4.5868 | 121.6278 | 0.16022 | 121.5958 | 121.6187 | 121.637 | 121.6461 | 121.6324 | -121.788 | -121.8201 | 121.6553 | 121.5912 | 24.971 | 0.66376
1785.8438 | 121.7926 | -0.29755 | 121.5271 | -0.097427 | 0.018707 | 0.069455 | 0.076556 | -0.0046911 | 0.0029288 | 0.0040353 | -0.068024 | 0.0059515 | 0.062568 | 0.051755 | -0.013883 | 0.024844 | -0.0045117 | 24.7559 | 121.4127 | -0.27924 | 121.3074 | 4.303 | 1.5472 | 0.76904 | 0.31128 | 121.3852 | -0.31128 | 121.2891 | -0.16937 | -0.19684 | -0.17395 | 0.01831 | -0.11444 | -0.21973 | 4.6005 | 1.0666 | 1.8448 | 1.0483 | 1.8265 | -0.013733 | -0.14191 | -0.23804 | 0.12817 | 0.1236 | 0.10071 | 0.13733 | 0.11444 | 4.5822 | 121.5866 | 0.14191 | 121.6003 | 121.6919 | 121.6965 | 121.7102 | 121.6827 | -121.8063 | -121.8384 | 121.6049 | 121.5866 | 25.0534 | 0.60882
1787.5938 | 121.9391 | -0.24719 | 121.5134 | -0.15083 | 0.017853 | 0.069882 | 0.074206 | 0.0012903 | 0.001647 | 0.0027537 | -0.013092 | 0.0053107 | 0.064277 | 0.051968 | -0.014951 | 0.025699 | -0.0045117 | 24.8566 | 121.376 | -0.23804 | 121.4447 | 4.5776 | 1.7899 | 0.91553 | 0.44861 | 121.3394 | -0.23804 | 121.4218 | -0.013733 | -0.045776 | -0.022888 | 0.009155 | -0.13733 | -0.068665 | 4.8248 | 1.1627 | 2.037 | 1.1536 | 2.0279 | 0.009155 | -0.17395 | -0.091553 | 0.23346 | 0.2243 | 0.20142 | 0.21515 | 0.19226 | 4.8157 | 121.6827 | 0.2243 | 121.6599 | 121.6141 | 121.5775 | 121.6232 | 121.5866 | -121.7514 | -121.7514 | 121.6919 | 121.669 | 25.1038 | 0.6958
1789.3438 | 121.9025 | -0.25177 | 121.5363 | -0.15083 | 0.01828 | 0.068387 | 0.071643 | -0.0040503 | 0.00057885 | 0.0033945 | -0.040558 | 0.0042425 | 0.064704 | 0.052395 | -0.014951 | 0.026981 | -0.0042981 | 25.2548 | 121.376 | -0.22888 | 121.4539 | 4.5776 | 1.5701 | 0.90179 | 0.44861 | 121.3669 | -0.25177 | 121.4172 | -0.022888 | -0.082397 | -0.050354 | 0.022888 | -0.16022 | -0.082398 | 4.8294 | 1.1536 | 1.8219 | 1.1307 | 1.799 | 0 | -0.16937 | -0.11902 | 0.22888 | 0.20142 | 0.16937 | 0.20142 | 0.16937 | 4.8065 | 121.6827 | 0.22888 | 121.669 | 121.6049 | 121.6187 | 121.6278 | 121.6187 | -121.7651 | -121.788 | 121.7056 | 121.669 | 25.5066 | 0.70038
1791.125 | 121.8475 | -0.27008 | 121.5546 | -0.089798 | 0.019775 | 0.07031 | 0.077838 | -0.0023413 | 0.0010062 | 0.0033945 | -0.037506 | 0.0053107 | 0.062995 | 0.053677 | -0.015806 | 0.026126 | -0.0075025 | 25.2777 | 121.4218 | -0.23804 | 121.4081 | 4.6005 | 1.5793 | 0.87891 | 0.38452 | 121.3898 | -0.27466 | 121.3348 | -0.10529 | -0.15106 | -0.13733 | 0.032044 | -0.13275 | -0.14648 | 4.8706 | 1.149 | 1.8494 | 1.1169 | 1.8173 | -0.004577 | -0.16479 | -0.21973 | 0.1648 | 0.13275 | 0.11902 | 0.13733 | 0.1236 | 4.8386 | 121.6461 | 0.16937 | 121.6095 | 121.6599 | 121.6644 | 121.6919 | 121.6599 | -121.7926 | -121.8292 | 121.6782 | 121.6049 | 25.5478 | 0.6546
1792.8281 | 121.843 | -0.27924 | 121.5179 | -0.19661 | 0.021911 | 0.072446 | 0.078265 | -0.0012731 | 0.0022878 | 0.0055307 | -0.12601 | 0.0070197 | 0.065772 | 0.057736 | -0.014951 | 0.027408 | -0.0083569 | 25.4242 | 121.4951 | -0.26093 | 121.3257 | 4.5456 | 1.4923 | 0.78735 | 0.16022 | 121.4127 | -0.2655 | 121.3394 | -0.16937 | -0.19684 | -0.12817 | 0.018311 | -0.022888 | -0.19226 | 4.8248 | 1.0666 | 1.7715 | 1.0483 | 1.7532 | 0.013733 | -0.10528 | -0.17853 | 0.10986 | 0.15106 | 0.082398 | 0.13733 | 0.068665 | 4.8065 | 121.5866 | 0.09613 | 121.6049 | 121.756 | 121.6782 | 121.7743 | 121.6919 | -121.7789 | -121.7834 | 121.6049 | 121.6187 | 25.7034 | 0.43945
1794.5938 | 121.8704 | -0.27466 | 121.5866 | -0.11269 | 0.020202 | 0.071378 | 0.076556 | -0.0021277 | 0.0029288 | 0.0033945 | -0.077179 | 0.0057379 | 0.062141 | 0.045987 | -0.014311 | 0.026981 | 0.00040169 | 25.6714 | 121.4676 | -0.25177 | 121.3486 | 4.66 | 1.5793 | 0.81482 | 0.28839 | 121.4035 | -0.25635 | 121.3715 | -0.10071 | -0.16479 | -0.10529 | 0.022888 | -0.11902 | -0.23804 | 4.9347 | 1.0895 | 1.8539 | 1.0666 | 1.8311 | 0.01831 | -0.18311 | -0.21515 | 0.17395 | 0.16937 | 0.10986 | 0.15106 | 0.091553 | 4.9118 | 121.6003 | 0.15564 | 121.6278 | 121.7194 | 121.6599 | 121.7422 | 121.6782 | -121.8384 | -121.843 | 121.6232 | 121.6461 | 25.946 | 0.56305
1796.3438 | 121.907 | -0.23346 | 121.5637 | -0.12794 | 0.019134 | 0.07031 | 0.07442 | -0.0021277 | 0.0027152 | 0.0046763 | -0.0069885 | 0.0050971 | 0.065345 | 0.049832 | -0.016233 | 0.02634 | -0.0049389 | 25.8041 | 121.4401 | -0.21515 | 121.4584 | 4.8477 | 1.7212 | 0.95673 | 0.4303 | 121.3852 | -0.23346 | 121.4218 | -0.027466 | -0.068665 | -0.064087 | 0.01831 | -0.1236 | -0.10529 | 5.0812 | 1.1902 | 1.9546 | 1.1719 | 1.9363 | 0 | -0.17853 | -0.14191 | 0.20599 | 0.16937 | 0.16479 | 0.16937 | 0.16479 | 5.0629 | 121.6736 | 0.20599 | 121.6553 | 121.6553 | 121.6187 | 121.6736 | 121.6187 | -121.7789 | -121.7972 | 121.6919 | 121.6553 | 26.0376 | 0.66376
1798.0469 | 121.9254 | -0.2243 | 121.5363 | -0.13557 | 0.021484 | 0.073514 | 0.080188 | 0.00064947 | 0.006774 | 0.0036081 | -0.092438 | 0.0055243 | 0.063209 | 0.050686 | -0.013242 | 0.025912 | -0.0047253 | 26.001 | 121.4767 | -0.23346 | 121.3943 | 4.8294 | 1.9226 | 0.89722 | 0.22888 | 121.4081 | -0.24719 | 121.463 | -0.036621 | -0.09613 | -0.018311 | -0.009155 | -0.059509 | -0.14191 | 5.0537 | 1.1215 | 2.1469 | 1.1307 | 2.1561 | -0.022888 | -0.12817 | -0.073242 | 0.18768 | 0.20599 | 0.12817 | 0.22888 | 0.15106 | 5.0629 | 121.6278 | 0.21057 | 121.7102 | 121.7102 | 121.6553 | 121.7011 | 121.6324 | -121.7697 | -121.7834 | 121.6187 | 121.6873 | 26.2253 | 0.45319
1799.7969 | 121.8246 | -0.27924 | 121.5866 | -0.11269 | 0.018493 | 0.07266 | 0.079547 | 0.0015039 | 0.0042104 | 0.0051035 | -0.058869 | 0.0055243 | 0.063423 | 0.049832 | -0.016447 | 0.027835 | -0.0038709 | 25.9369 | 121.4905 | -0.23346 | 121.3394 | 4.834 | 1.8951 | 0.8606 | 0.3067 | 121.4355 | -0.26093 | 121.3486 | -0.12817 | -0.16937 | -0.13733 | 0.045777 | -0.09613 | -0.24719 | 5.1132 | 1.1398 | 2.1744 | 1.0941 | 2.1286 | 0.018311 | -0.15106 | -0.23804 | 0.15106 | 0.14191 | 0.10986 | 0.1236 | 0.091552 | 5.0674 | 121.5729 | 0.13275 | 121.6095 | 121.7239 | 121.6965 | 121.7697 | 121.7148 | -121.8201 | -121.8475 | 121.6187 | 121.6278 | 26.2161 | 0.58594
1801.5469 | 121.9025 | -0.23804 | 121.5408 | -0.21187 | 0.020843 | 0.073728 | 0.076129 | -0.0017005 | 0.0029288 | 0.0061717 | -0.034454 | 0.0038153 | 0.065345 | 0.049618 | -0.014524 | 0.026126 | -0.0021619 | 25.7538 | 121.4493 | -0.21973 | 121.4172 | 5.0034 | 1.7853 | 0.96588 | 0.25635 | 121.3989 | -0.22888 | 121.4401 | -0.059509 | -0.091553 | -0.045776 | 0.01831 | -0.091553 | -0.1236 | 5.2414 | 1.2039 | 2.0233 | 1.1856 | 2.005 | 0.009155 | -0.14191 | -0.10071 | 0.17853 | 0.19226 | 0.14648 | 0.18311 | 0.13733 | 5.2231 | 121.637 | 0.16937 | 121.669 | 121.669 | 121.6278 | 121.6873 | 121.637 | -121.7606 | -121.7697 | 121.6553 | 121.6782 | 25.9918 | 0.49439
1803.25 | 121.875 | -0.25177 | 121.5729 | -0.15083 | 0.021484 | 0.07266 | 0.077624 | 0.00064947 | 0.003356 | 0.0018991 | -0.11075 | 0.0087287 | 0.06385 | 0.054104 | -0.015592 | 0.027194 | -0.0028027 | 25.8682 | 121.4905 | -0.22888 | 121.4081 | 5.0125 | 1.799 | 0.9201 | 0.33417 | 121.4401 | -0.23804 | 121.4218 | -0.068665 | -0.11444 | -0.068665 | 0.022888 | -0.082397 | -0.16479 | 5.2643 | 1.1719 | 2.0508 | 1.149 | 2.0279 | 0.013733 | -0.13275 | -0.15106 | 0.1831 | 0.1831 | 0.13733 | 0.16937 | 0.1236 | 5.2414 | 121.637 | 0.16937 | 121.6599 | 121.7194 | 121.6782 | 121.7422 | 121.6919 | -121.8018 | -121.8109 | 121.6599 | 121.6736 | 26.12 | 0.58594
1805 | 121.8979 | -0.22888 | 121.5637 | -0.15846 | 0.020202 | 0.072873 | 0.074206 | -0.00063233 | 0.0037832 | 0.0025401 | -0.022247 | 0.0046697 | 0.063423 | 0.050473 | -0.014738 | 0.027835 | -0.0040845 | 16.0721 | 121.4584 | -0.21515 | 121.4264 | 4.9713 | 1.8311 | 0.95673 | 0.25635 | 121.4035 | -0.24261 | 121.431 | -0.054932 | -0.091553 | -0.045776 | 0.013733 | -0.10529 | -0.13733 | 5.2002 | 1.1856 | 2.0599 | 1.1719 | 2.0462 | -0.013733 | -0.16022 | -0.13275 | 0.17395 | 0.18311 | 0.13733 | 0.19684 | 0.15106 | 5.1865 | 121.6415 | 0.18768 | 121.6736 | 121.6736 | 121.6461 | 121.6873 | 121.6324 | -121.7789 | -121.8063 | 121.6553 | 121.6599 | 16.301 | 0.48523
1806.75 | 121.8887 | -0.23804 | 121.6095 | -0.12032 | 0.021484 | 0.072873 | 0.077197 | 0.0012903 | 0.0027152 | 0.0021127 | -0.092438 | 0.0061651 | 0.066413 | 0.054318 | -0.016233 | 0.02869 | -0.0042981 | 22.7966 | 121.4951 | -0.23804 | 121.4264 | 4.9988 | 1.8219 | 0.92926 | 0.34332 | 121.4584 | -0.24261 | 121.4355 | -0.068665 | -0.12817 | -0.07782 | 0 | -0.11444 | -0.1831 | 5.2368 | 1.1673 | 2.0599 | 1.1673 | 2.0599 | -0.004578 | -0.15106 | -0.17395 | 0.16937 | 0.16022 | 0.10986 | 0.16479 | 0.11444 | 5.2368 | 121.6644 | 0.17395 | 121.6782 | 121.7331 | 121.701 | 121.7331 | 121.6965 | -121.8475 | -121.8521 | 121.6644 | 121.6736 | 23.0347 | 0.58136
1808.4375 | 121.8887 | -0.23346 | 121.5958 | -0.1432 | 0.022766 | 0.072873 | 0.078906 | -0.00084593 | 0.0018606 | 0.0057443 | -0.10464 | 0.0072333 | 0.064063 | 0.044919 | -0.015592 | 0.027621 | -0.0025891 | 23.3231 | 121.5454 | -0.23346 | 121.3806 | 5.0629 | 1.6983 | 0.89264 | 0.16479 | 121.4447 | -0.24719 | 121.4447 | -0.09613 | -0.13733 | -0.082397 | 0 | -0.050354 | -0.21515 | 5.2963 | 1.1261 | 1.9318 | 1.1261 | 1.9318 | -0.013733 | -0.15106 | -0.15106 | 0.13733 | 0.15106 | 0.09613 | 0.16479 | 0.10986 | 5.2963 | 121.6141 | 0.15106 | 121.6919 | 121.7789 | 121.6919 | 121.7789 | 121.6782 | -121.8292 | -121.843 | 121.6141 | 121.6782 | 23.5565 | 0.39825
1810.1875 | 121.8384 | -0.24261 | 121.6232 | -0.1432 | 0.022979 | 0.071591 | 0.079547 | -0.0025549 | 0.0042104 | 0.0036081 | -0.1077 | 0.0078741 | 0.063423 | 0.056881 | -0.015806 | 0.028903 | -0.0034435 | 22.4762 | 121.5179 | -0.24719 | 121.376 | 5.1178 | 1.7761 | 0.87433 | 0.16022 | 121.463 | -0.24719 | 121.3806 | -0.14648 | -0.20142 | -0.11902 | -0.004577 | -0.10529 | -0.24719 | 5.3604 | 1.1169 | 2.0187 | 1.1215 | 2.0233 | -0.004577 | -0.16022 | -0.24262 | 0.096131 | 0.1236 | 0.041199 | 0.12817 | 0.045776 | 5.365 | 121.6232 | 0.10071 | 121.6278 | 121.7651 | 121.7102 | 121.7606 | 121.7056 | -121.8704 | -121.8704 | 121.6187 | 121.6232 | 22.7188 | 0.40283
1811.875 | 121.8796 | -0.24261 | 121.6187 | -0.12032 | 0.02127 | 0.07266 | 0.077411 | 0.00022207 | 0.003356 | 0.0053171 | -0.071076 | 0.0059515 | 0.065986 | 0.051541 | -0.015379 | 0.026126 | -0.0038709 | 21.7987 | 121.5408 | -0.23346 | 121.4127 | 5.2002 | 1.9409 | 0.93842 | 0.33417 | 121.4539 | -0.23346 | 121.4401 | -0.054932 | -0.12817 | -0.086975 | 0.009156 | -0.077819 | -0.20599 | 5.4428 | 1.181 | 2.1835 | 1.1719 | 2.1744 | 0.009156 | -0.16479 | -0.17853 | 0.18768 | 0.15564 | 0.11444 | 0.14648 | 0.10528 | 5.4337 | 121.6461 | 0.17853 | 121.6736 | 121.7743 | 121.6873 | 121.7834 | 121.6965 | -121.8521 | -121.8521 | 121.6553 | 121.6827 | 22.0413 | 0.57678
1813.5781 | 121.8338 | -0.23804 | 121.6324 | -0.10506 | 0.022125 | 0.074369 | 0.078906 | 0.00064947 | 0.0057058 | 0.0033945 | -0.09549 | 0.0076605 | 0.064277 | 0.052182 | -0.017301 | 0.027835 | -0.0038709 | 24.2477 | 121.55 | -0.21515 | 121.3806 | 5.2277 | 1.7853 | 0.8606 | 0.16022 | 121.4767 | -0.23804 | 121.3989 | -0.13733 | -0.21515 | -0.1236 | 0.022888 | -0.082397 | -0.25177 | 5.4657 | 1.0986 | 2.0233 | 1.0757 | 2.0004 | 0 | -0.15564 | -0.23346 | 0.10071 | 0.11444 | 0.022888 | 0.11444 | 0.022888 | 5.4428 | 121.5958 | 0.10071 | 121.637 | 121.7651 | 121.7148 | 121.788 | 121.7148 | -121.8475 | -121.8704 | 121.6187 | 121.637 | 24.4858 | 0.39825
1815.3281 | 121.962 | -0.20599 | 121.5912 | -0.19661 | 0.019989 | 0.0733 | 0.077624 | 0.0015039 | 0.0046378 | 0.0061717 | -0.034454 | 0.0053107 | 0.065132 | 0.049405 | -0.012174 | 0.025912 | -0.0021619 | 26.2894 | 121.5042 | -0.17395 | 121.5134 | 5.4657 | 2.0462 | 1.0574 | 0.28839 | 121.4218 | -0.21515 | 121.5134 | 0.018311 | -0.022888 | 0.013733 | 0.032044 | -0.086976 | -0.07782 | 5.6717 | 1.2634 | 2.2522 | 1.2314 | 2.2202 | -0.009155 | -0.16937 | -0.07782 | 0.22431 | 0.21973 | 0.18311 | 0.22888 | 0.19226 | 5.6396 | 121.6873 | 0.23346 | 121.7285 | 121.6782 | 121.637 | 121.7102 | 121.6278 | -121.7651 | -121.8063 | 121.7194 | 121.7194 | 26.4954 | 0.49439
1817.0938 | 121.8658 | -0.23346 | 121.6232 | -0.1432 | 0.023834 | 0.0733 | 0.077197 | -0.0012731 | 0.0059194 | 0.0055307 | -0.1077 | 0.0070197 | 0.065345 | 0.053677 | -0.014097 | 0.027408 | -0.0049389 | 21.3318 | 121.5546 | -0.2243 | 121.4355 | 5.3604 | 2.3712 | 1.0117 | 0.28839 | 121.4493 | -0.23804 | 121.4218 | -0.10986 | -0.14648 | -0.09613 | 0.009155 | -0.068665 | -0.18768 | 5.5939 | 1.2451 | 2.6047 | 1.236 | 2.5955 | -0.004578 | -0.17395 | -0.20142 | 0.1236 | 0.13733 | 0.086975 | 0.14191 | 0.091553 | 5.5847 | 121.6599 | 0.12817 | 121.6599 | 121.7789 | 121.6873 | 121.788 | 121.6827 | -121.8475 | -121.8613 | 121.669 | 121.6553 | 21.5652 | 0.52185
1818.7969 | 121.9025 | -0.24261 | 121.637 | -0.11269 | 0.022339 | 0.071164 | 0.073565 | -0.00063233 | 0.00015165 | 0.0042491 | -0.013092 | 0.0048833 | 0.065559 | 0.052395 | -0.015379 | 0.028049 | -0.0047253 | 26.651 | 121.5317 | -0.19226 | 121.4722 | 5.5206 | 1.6617 | 1.0345 | 0.37994 | 121.4722 | -0.20142 | 121.4401 | -0.068665 | -0.10986 | -0.091553 | 0.050354 | -0.10529 | -0.16479 | 5.7632 | 1.2772 | 1.9043 | 1.2268 | 1.8539 | 0.041199 | -0.16479 | -0.19684 | 0.17395 | 0.15106 | 0.13275 | 0.10986 | 0.091553 | 5.7129 | 121.6644 | 0.13275 | 121.6415 | 121.7239 | 121.6736 | 121.7743 | 121.7148 | -121.8292 | -121.8384 | 121.7148 | 121.6827 | 26.8936 | 0.62256
1820.5469 | 121.9116 | -0.2243 | 121.637 | -0.12794 | 0.022552 | 0.072232 | 0.076342 | 0.0015039 | 0.0018606 | 0.0042491 | -0.058869 | 0.0080877 | 0.0662 | 0.043423 | -0.015165 | 0.027835 | -0.0083569 | 25.0717 | 121.55 | -0.21057 | 121.4584 | 5.5115 | 1.6296 | 1.0208 | 0.35706 | 121.5088 | -0.23346 | 121.4813 | -0.050354 | -0.10071 | -0.045776 | 0.013733 | -0.086975 | -0.17853 | 5.7358 | 1.2451 | 1.8539 | 1.2314 | 1.8402 | -0.009155 | -0.12817 | -0.15564 | 0.17395 | 0.17853 | 0.1236 | 0.18768 | 0.13275 | 5.722 | 121.669 | 0.1831 | 121.7148 | 121.7606 | 121.7422 | 121.7743 | 121.7331 | -121.8475 | -121.8704 | 121.6827 | 121.7056 | 25.296 | 0.58136
1822.2969 | 121.875 | -0.24261 | 121.6599 | -0.097427 | 0.021484 | 0.0733 | 0.072711 | -0.0012731 | 0.00036525 | 0.0021127 | -0.028351 | 0.0072333 | 0.065986 | 0.046414 | -0.014524 | 0.027835 | -0.0081433 | 14.9048 | 121.5454 | -0.20142 | 121.3989 | 5.4565 | 1.5427 | 0.98877 | 0.31586 | 121.4905 | -0.22888 | 121.4127 | -0.091553 | -0.1236 | -0.09613 | 0.041199 | -0.11444 | -0.26093 | 5.6992 | 1.2314 | 1.7853 | 1.1902 | 1.7441 | 0.013733 | -0.16937 | -0.24719 | 0.15106 | 0.14649 | 0.11902 | 0.13275 | 0.10529 | 5.658 | 121.6003 | 0.13733 | 121.6415 | 121.7468 | 121.7194 | 121.788 | 121.7331 | -121.8613 | -121.8887 | 121.6415 | 121.6553 | 15.1474 | 0.55847
1823.9844 | 121.962 | -0.19684 | 121.6324 | -0.21187 | 0.023834 | 0.075223 | 0.07442 | 0.0025721 | 0.0037832 | 0.0057443 | -0.019196 | 0.0057379 | 0.06385 | 0.050046 | -0.015165 | 0.026767 | -0.0010937 | 16.1224 | 121.5637 | -0.14648 | 121.5225 | 5.6442 | 1.6754 | 1.1124 | 0.30212 | 121.4447 | -0.20142 | 121.5271 | 0.009155 | -0.022888 | 0.022888 | 0.050354 | -0.068664 | -0.10986 | 5.8411 | 1.3092 | 1.8723 | 1.2589 | 1.8219 | -0.004578 | -0.18768 | -0.10528 | 0.20599 | 0.21973 | 0.17395 | 0.2243 | 0.17853 | 5.7907 | 121.669 | 0.21057 | 121.7285 | 121.7102 | 121.6461 | 121.7606 | 121.6415 | -121.7789 | -121.8338 | 121.7194 | 121.7239 | 16.3193 | 0.49896
1825.7344 | 121.8979 | -0.21057 | 121.6599 | -0.12032 | 0.026184 | 0.07266 | 0.076342 | -0.0017005 | 0.0031424 | 0.0046763 | -0.10464 | 0.0057379 | 0.064704 | 0.051327 | -0.016447 | 0.028049 | -0.0055799 | 16.4291 | 121.6003 | -0.20142 | 121.4081 | 5.5527 | 1.5198 | 0.98877 | 0.17395 | 121.5088 | -0.22888 | 121.463 | -0.10071 | -0.14191 | -0.082397 | 0.009155 | -0.059509 | -0.25177 | 5.7632 | 1.1993 | 1.7303 | 1.1902 | 1.7212 | -0.018311 | -0.15106 | -0.19684 | 0.10986 | 0.12817 | 0.068664 | 0.14649 | 0.086975 | 5.7541 | 121.6095 | 0.12817 | 121.6919 | 121.8018 | 121.7377 | 121.8109 | 121.7194 | -121.8613 | -121.8887 | 121.6187 | 121.6736 | 16.6397 | 0.38452
1827.4844 | 121.9894 | -0.18768 | 121.6232 | -0.17372 | 0.021698 | 0.071805 | 0.074206 | 0.00022207 | 0.0020742 | 0.0042491 | 0.014374 | 0.0070197 | 0.065559 | 0.054104 | -0.014951 | 0.026553 | -0.0057935 | 25.09 | 121.5179 | -0.1831 | 121.5179 | 5.7449 | 1.7578 | 1.1444 | 0.37994 | 121.4676 | -0.17853 | 121.55 | 0.041199 | 0 | 0.027466 | 0.004578 | -0.10529 | -0.10529 | 5.9326 | 1.3321 | 1.9455 | 1.3275 | 1.9409 | 0.009155 | -0.15564 | -0.073242 | 0.22888 | 0.21515 | 0.18768 | 0.20599 | 0.17853 | 5.928 | 121.701 | 0.21973 | 121.7285 | 121.701 | 121.6461 | 121.7056 | 121.6553 | -121.8063 | -121.8018 | 121.7056 | 121.7377 | 25.2777 | 0.56763
1829.25 | 121.8521 | -0.25635 | 121.6873 | -0.13557 | 0.024261 | 0.072873 | 0.076983 | 0.0021447 | 0.0029288 | 0.0038217 | -0.11685 | 0.0076605 | 0.066413 | 0.050473 | -0.014524 | 0.027621 | -0.0023755 | 24.1241 | 121.5866 | -0.20599 | 121.4264 | 5.6396 | 1.5884 | 0.99335 | 0.16479 | 121.5271 | -0.21057 | 121.4264 | -0.12817 | -0.16937 | -0.086975 | 0.050354 | -0.10071 | -0.26092 | 5.896 | 1.2497 | 1.8448 | 1.1993 | 1.7944 | 0.045777 | -0.16022 | -0.26092 | 0.12817 | 0.16937 | 0.086975 | 0.1236 | 0.041198 | 5.8456 | 121.6324 | 0.082397 | 121.637 | 121.7926 | 121.7377 | 121.843 | 121.7834 | -121.8933 | -121.8979 | 121.6827 | 121.6827 | 24.3805 | 0.42114
1830.9375 | 121.9162 | -0.21973 | 121.6599 | -0.12794 | 0.023193 | 0.071164 | 0.076556 | -0.0027685 | 0.00036525 | 0.0053171 | -0.052765 | 0.0065923 | 0.066627 | 0.049405 | -0.01367 | 0.026553 | -0.0055799 | 24.2432 | 121.5591 | -0.21515 | 121.4172 | 5.6717 | 1.6617 | 1.0666 | 0.3067 | 121.5271 | -0.21515 | 121.4539 | -0.082397 | -0.12817 | -0.07782 | 0.004578 | -0.10071 | -0.24262 | 5.8914 | 1.2863 | 1.8814 | 1.2817 | 1.8768 | 0.004578 | -0.13275 | -0.20599 | 0.13733 | 0.14191 | 0.091553 | 0.13733 | 0.086975 | 5.8868 | 121.6324 | 0.13275 | 121.669 | 121.7743 | 121.7422 | 121.7789 | 121.7468 | -121.875 | -121.875 | 121.637 | 121.6736 | 24.4629 | 0.52643
1832.6875 | 122.0169 | -0.17395 | 121.6324 | -0.15846 | 0.021911 | 0.07266 | 0.072924 | -0.0021277 | 0.0029288 | 0.0046763 | -0.01004 | 0.0061651 | 0.064704 | 0.050046 | -0.014524 | 0.024417 | -0.0045117 | 24.4995 | 121.5317 | -0.16937 | 121.5408 | 5.8548 | 1.8127 | 1.2085 | 0.43945 | 121.4722 | -0.17395 | 121.5683 | 0.054932 | 0.032043 | 0.041199 | 0.004577 | -0.10071 | -0.091552 | 6.0287 | 1.3824 | 1.9867 | 1.3779 | 1.9821 | 0 | -0.16022 | -0.064087 | 0.22888 | 0.21515 | 0.20599 | 0.21515 | 0.20599 | 6.0242 | 121.7102 | 0.22888 | 121.7422 | 121.701 | 121.6461 | 121.7056 | 121.6461 | -121.8018 | -121.8063 | 121.7148 | 121.7422 | 24.6735 | 0.6134
1834.4375 | 121.994 | -0.16479 | 121.6415 | -0.20424 | 0.026397 | 0.074155 | 0.073565 | -0.0049047 | 0.0029288 | 0.0046763 | -0.049713 | 0.0031745 | 0.065772 | 0.054959 | -0.014524 | 0.028262 | -0.0092115 | 24.8062 | 121.5546 | -0.17395 | 121.5591 | 5.8823 | 1.8402 | 1.1765 | 0.32959 | 121.4767 | -0.17853 | 121.5637 | 0.041199 | -0.004578 | 0.018311 | -0.009155 | -0.086976 | -0.082398 | 6.0471 | 1.3412 | 2.005 | 1.3504 | 2.0142 | -0.013733 | -0.16479 | -0.07782 | 0.20599 | 0.18311 | 0.16022 | 0.19684 | 0.17395 | 6.0562 | 121.7331 | 0.21973 | 121.7422 | 121.7285 | 121.6553 | 121.7194 | 121.6415 | -121.8155 | -121.8201 | 121.7239 | 121.7285 | 24.971 | 0.49438
1836.1875 | 121.9528 | -0.20599 | 121.669 | -0.17372 | 0.022552 | 0.072446 | 0.074633 | -0.0019141 | 0.0029288 | 0.0070261 | 0.017425 | 0.0038153 | 0.065986 | 0.048123 | -0.01602 | 0.026767 | -0.0040845 | 25.6027 | 121.5454 | -0.16022 | 121.55 | 5.9097 | 1.9043 | 1.1719 | 0.43488 | 121.4996 | -0.17853 | 121.5271 | 0.013733 | -0.022888 | -0.013733 | 0.045777 | -0.1236 | -0.11902 | 6.1157 | 1.3779 | 2.1103 | 1.3321 | 2.0645 | 0.027466 | -0.16937 | -0.14191 | 0.21973 | 0.19226 | 0.18311 | 0.16479 | 0.15564 | 6.0699 | 121.7102 | 0.19226 | 121.7056 | 121.7056 | 121.6782 | 121.7514 | 121.7056 | -121.8292 | -121.8475 | 121.756 | 121.7331 | 25.8087 | 0.64087
1837.875 | 121.8887 | -0.20599 | 121.6827 | -0.1432 | 0.025116 | 0.072873 | 0.076342 | 0.0027857 | 0.0037832 | 0.0065989 | -0.10464 | 0.0095831 | 0.067054 | 0.052395 | -0.014951 | 0.027835 | -0.0055799 | 26.12 | 121.5912 | -0.18768 | 121.5042 | 5.8411 | 1.8127 | 1.0757 | 0.28381 | 121.5363 | -0.19684 | 121.4859 | -0.09613 | -0.14191 | -0.07782 | 0.018311 | -0.091552 | -0.17853 | 6.0471 | 1.2817 | 2.0187 | 1.2634 | 2.0004 | 0.009156 | -0.14648 | -0.19684 | 0.10986 | 0.12817 | 0.064087 | 0.11902 | 0.054931 | 6.0287 | 121.6919 | 0.10071 | 121.6827 | 121.7789 | 121.7331 | 121.7972 | 121.7422 | -121.8704 | -121.8796 | 121.7102 | 121.6919 | 26.326 | 0.48981
1839.625 | 122.0215 | -0.17395 | 121.637 | -0.18898 | 0.023193 | 0.073514 | 0.074206 | -0.0046911 | 0.0037832 | 0.0023265 | -0.0039367 | 0.0046697 | 0.062995 | 0.050259 | -0.015165 | 0.024631 | -0.0064343 | 27.1957 | 121.5546 | -0.16479 | 121.5958 | 6.015 | 2.0233 | 1.236 | 0.45776 | 121.4905 | -0.18768 | 121.5729 | 0.064087 | 0.036621 | 0.036621 | 0.009155 | -0.082398 | -0.041199 | 6.189 | 1.4099 | 2.1973 | 1.4008 | 2.1881 | -0.013733 | -0.14648 | -0.064087 | 0.23804 | 0.21057 | 0.21057 | 0.2243 | 0.2243 | 6.1798 | 121.7606 | 0.25177 | 121.7606 | 121.7194 | 121.6782 | 121.7285 | 121.6644 | -121.8018 | -121.8246 | 121.7697 | 121.7468 | 27.3697 | 0.63171
1841.3594 | 121.8796 | -0.21973 | 121.6919 | -0.11269 | 0.026184 | 0.071805 | 0.076342 | -0.00020513 | 0.004424 | 0.0038217 | -0.12601 | 0.0063787 | 0.064491 | 0.052395 | -0.015806 | 0.02933 | -0.0032299 | 26.5137 | 121.6003 | -0.19684 | 121.4584 | 5.8548 | 1.8082 | 1.0529 | 0.19684 | 121.5546 | -0.20599 | 121.4676 | -0.10986 | -0.17853 | -0.086975 | 0.022889 | -0.091553 | -0.23346 | 6.0745 | 1.2726 | 2.0279 | 1.2497 | 2.005 | 0.013733 | -0.13733 | -0.22431 | 0.10986 | 0.13275 | 0.041199 | 0.11902 | 0.027466 | 6.0516 | 121.6553 | 0.096131 | 121.6736 | 121.7972 | 121.7606 | 121.8201 | 121.7743 | -121.8887 | -121.8979 | 121.6782 | 121.6873 | 26.7334 | 0.41657
1843.0469 | 122.0352 | -0.17853 | 121.6599 | -0.17372 | 0.025757 | 0.072446 | 0.071643 | -0.0010595 | 0.0057058 | 0.0018991 | -0.019196 | 0.0059515 | 0.067054 | 0.04086 | -0.013456 | 0.027621 | -0.0083569 | 23.0347 | 121.582 | -0.16937 | 121.5683 | 6.0104 | 2.124 | 1.2222 | 0.44861 | 121.5042 | -0.16479 | 121.5958 | 0.068665 | 0.050354 | 0.041199 | 0.009155 | -0.07782 | -0.091553 | 6.189 | 1.4008 | 2.3026 | 1.3916 | 2.2934 | 0.013733 | -0.15564 | -0.064087 | 0.24719 | 0.21973 | 0.22888 | 0.20599 | 0.21515 | 6.1798 | 121.7377 | 0.23346 | 121.7606 | 121.7514 | 121.669 | 121.7606 | 121.6827 | -121.8292 | -121.8246 | 121.7468 | 121.7743 | 23.2132 | 0.62714
1844.75 | 122.0306 | -0.17853 | 121.6599 | -0.12032 | 0.024261 | 0.07266 | 0.073779 | -0.0021277 | 0.006133 | 0.0027537 | -0.0069885 | 0.0038153 | 0.066627 | 0.045987 | -0.014738 | 0.025485 | -0.0055799 | 24.472 | 121.5546 | -0.16479 | 121.5683 | 5.9921 | -0.85602 | 1.1581 | 0.44861 | 121.5134 | -0.19226 | 121.5912 | 0.059509 | 0.027466 | 0.041199 | 0.013733 | -0.10529 | -0.091553 | 6.1707 | 1.3367 | -0.67749 | 1.3229 | -0.69122 | -0.013733 | -0.14648 | -0.068664 | 0.23804 | 0.21973 | 0.20599 | 0.23346 | 0.21973 | 6.1569 | 121.7331 | 0.25177 | 121.7834 | 121.7194 | 121.7056 | 121.7331 | 121.6919 | -121.8246 | -121.8521 | 121.7468 | 121.7697 | 24.6506 | 0.62714
1846.5 | 121.8933 | -0.21515 | 121.7285 | -0.12032 | 0.024048 | 0.072019 | 0.075488 | -0.00084593 | 0.0037832 | 0.0033945 | -0.040558 | 0.0074469 | 0.064704 | 0.040433 | -0.013242 | 0.028903 | -0.0028027 | 20.8603 | 121.6095 | -0.20599 | 121.463 | 5.8502 | 2.1698 | 1.0803 | 0.32044 | 121.5591 | -0.21057 | 121.4447 | -0.086975 | -0.1236 | -0.09613 | 0.009155 | -0.11902 | -0.2655 | 6.0654 | 1.2955 | 2.3849 | 1.2863 | 2.3758 | 0.004578 | -0.16937 | -0.28381 | 0.12817 | 0.11902 | 0.091553 | 0.11444 | 0.086975 | 6.0562 | 121.669 | 0.1236 | 121.6553 | 121.8155 | 121.7697 | 121.8246 | 121.7743 | -121.9345 | -121.9391 | 121.6782 | 121.6599 | 21.0754 | 0.53558
1848.2812 | 122.0123 | -0.18768 | 121.6965 | -0.2195 | 0.026611 | 0.073514 | 0.073352 | 0.00086307 | 0.004424 | 0.0055307 | 0.0052185 | 0.0061651 | 0.061927 | 0.042355 | -0.014738 | 0.026767 | -0.0038709 | 21.8903 | 121.5363 | -0.16937 | 121.55 | 5.983 | 2.2293 | 1.1856 | 0.34332 | 121.4996 | -0.18768 | 121.5775 | 0.041199 | 0.009155 | 0.027466 | 0.01831 | -0.16022 | -0.14648 | 6.1707 | 1.3733 | 2.417 | 1.355 | 2.3987 | 0 | -0.19684 | -0.11902 | 0.22888 | 0.21515 | 0.19684 | 0.21515 | 0.19684 | 6.1523 | 121.7194 | 0.22888 | 121.7651 | 121.7056 | 121.6873 | 121.7239 | 121.6873 | -121.8658 | -121.8842 | 121.7377 | 121.7651 | 22.0779 | 0.53101
1849.9688 | 121.9757 | -0.1831 | 121.6873 | -0.17372 | 0.027893 | 0.073514 | 0.073565 | 0.0021447 | 0.0054922 | 0.0044627 | -0.052765 | 0.0065923 | 0.06385 | 0.04855 | -0.01666 | 0.02869 | -0.0049389 | 20.018 | 121.5775 | -0.15564 | 121.55 | 6.0196 | 2.2018 | 1.1856 | 0.3067 | 121.5317 | -0.16937 | 121.5637 | 0 | -0.022888 | 0.013733 | 0.027465 | -0.10986 | -0.13733 | 6.2027 | 1.3687 | 2.3849 | 1.3412 | 2.3575 | 0.013732 | -0.15564 | -0.1236 | 0.1831 | 0.19684 | 0.16022 | 0.18311 | 0.14649 | 6.1752 | 121.7056 | 0.16937 | 121.7331 | 121.7331 | 121.701 | 121.7606 | 121.7148 | -121.843 | -121.8567 | 121.7331 | 121.7468 | 20.2011 | 0.48981
1851.7031 | 121.8933 | -0.21515 | 121.701 | -0.13557 | 0.026184 | 0.07266 | 0.073993 | -0.0014867 | 0.003356 | 0.0044627 | -0.052765 | 0.0059515 | 0.064704 | 0.054532 | -0.01602 | 0.025485 | -0.0015209 | 22.9156 | 121.582 | -0.21057 | 121.4813 | 5.928 | 2.1011 | 1.0986 | 0.33875 | 121.5775 | -0.20599 | 121.4676 | -0.068665 | -0.10986 | -0.10529 | 0.004578 | -0.11902 | -0.21973 | 6.1432 | 1.3138 | 2.3163 | 1.3092 | 2.3117 | 0.009155 | -0.1236 | -0.23346 | 0.14648 | 0.10986 | 0.10529 | 0.10071 | 0.096131 | 6.1386 | 121.6919 | 0.13733 | 121.6736 | 121.7926 | 121.7834 | 121.7972 | 121.7926 | -121.9116 | -121.907 | 121.6965 | 121.6827 | 23.1308 | 0.55389
1853.4531 | 121.9437 | -0.19684 | 121.6827 | -0.12032 | 0.028747 | 0.072873 | 0.077838 | -0.0034095 | 0.0065604 | 0.0070261 | -0.12601 | 0.0061651 | 0.065132 | 0.055813 | -0.01602 | 0.027194 | -0.0042981 | 20.0958 | 121.637 | -0.17853 | 121.4767 | 5.8823 | 2.7786 | 1.0895 | 0.17395 | 121.55 | -0.20142 | 121.5088 | -0.07782 | -0.10986 | -0.073242 | 0.01831 | -0.045776 | -0.20599 | 6.0791 | 1.2863 | 2.9755 | 1.268 | 2.9572 | -0.004578 | -0.13275 | -0.17395 | 0.11902 | 0.1236 | 0.086975 | 0.12817 | 0.091553 | 6.0608 | 121.6553 | 0.1236 | 121.7102 | 121.8155 | 121.7514 | 121.8338 | 121.7468 | -121.8613 | -121.8842 | 121.6736 | 121.7056 | 20.2927 | 0.37079
1855.2188 | 121.9025 | -0.21515 | 121.7194 | -0.12794 | 0.028961 | 0.071805 | 0.074206 | -0.0010595 | 0.0072012 | 0.0042491 | -0.068024 | 0.0057379 | 0.0662 | 0.049191 | -0.016233 | 0.026767 | -0.0049389 | 16.0355 | 121.6187 | -0.19226 | 121.4813 | 5.9006 | 6.4957 | 1.1398 | 0.32959 | 121.5591 | -0.19684 | 121.4859 | -0.068665 | -0.13275 | -0.086975 | 0.022888 | -0.10071 | -0.23804 | 6.1157 | 1.355 | 6.7108 | 1.3321 | 6.6879 | 0.018311 | -0.16022 | -0.23346 | 0.14648 | 0.12817 | 0.082398 | 0.10986 | 0.064087 | 6.0928 | 121.6736 | 0.12817 | 121.6827 | 121.8109 | 121.756 | 121.8338 | 121.7743 | -121.9116 | -121.9162 | 121.6965 | 121.701 | 16.2506 | 0.54474
1856.9062 | 121.994 | -0.16937 | 121.6324 | -0.64674 | 0.58075 | 0.076078 | 0.062457 | -0.0029821 | 0.55002 | 0.0070261 | 0.011322 | 0.0070197 | 0.062995 | 0.044278 | -0.011961 | 0.027621 | -0.0023755 | 65.863 | 121.4905 | -0.10986 | 121.5454 | 6.3904 | 85.5057 | 1.5747 | 0.4715 | 121.4905 | -0.1831 | 121.5729 | 0.054932 | 0.032043 | 0.032043 | 0.05951 | -0.14191 | -0.086975 | 6.5598 | 1.7441 | 85.675 | 1.6846 | 85.6155 | -0.013732 | -0.14191 | -0.059509 | 0.22431 | 0.20142 | 0.20142 | 0.21515 | 0.21515 | 6.5002 | 121.6553 | 0.23804 | 121.756 | 121.6003 | 121.6736 | 121.6599 | 121.6599 | -121.7422 | -121.8155 | 121.7148 | 121.7422 | 66.0324 | 0.64087
1858.6562 | 121.962 | -0.19226 | 121.5958 | -0.9214 | 0.80548 | 0.076932 | 0.060748 | -0.0029821 | 0.77689 | 0.0048899 | -0.019196 | 0.0072333 | 0.065132 | 0.047909 | -0.014311 | 0.02869 | -0.0070751 | 70.9534 | 121.4264 | -0.10986 | 121.4767 | 6.3721 | 119.0689 | 1.5244 | 0.46234 | 121.4493 | -0.17853 | 121.5271 | 0.07782 | 0.041199 | 0.032043 | 0.082398 | -0.16937 | -0.11902 | 6.5643 | 1.7166 | 119.2612 | 1.6342 | 119.1788 | 0.013733 | -0.14648 | -0.068664 | 0.27008 | 0.2243 | 0.23346 | 0.21057 | 0.21973 | 6.4819 | 121.5866 | 0.25635 | 121.7056 | 121.5363 | 121.6278 | 121.6187 | 121.6415 | -121.7056 | -121.7743 | 121.669 | 121.7194 | 71.1456 | 0.6546
1860.3906 | 121.8018 | -0.21057 | 121.6232 | -0.9977 | 0.81851 | 0.077146 | 0.063952 | 0.0012903 | 0.78671 | 0.0057443 | -0.10159 | 0.01001 | 0.065345 | 0.046628 | -0.015379 | 0.027408 | -0.0038709 | 78.447 | 121.4539 | -0.13275 | 121.344 | 6.1935 | 120.7993 | 1.3229 | 0.1831 | 121.4813 | -0.21515 | 121.3898 | -0.1236 | -0.16022 | -0.086975 | 0.07782 | -0.16937 | -0.27924 | 6.4041 | 1.5335 | 121.0098 | 1.4557 | 120.932 | -0.004578 | -0.14191 | -0.23346 | 0.086975 | 0.1236 | 0.050354 | 0.12817 | 0.054932 | 6.3263 | 121.4767 | 0.091553 | 121.6049 | 121.5866 | 121.6965 | 121.6644 | 121.6919 | -121.756 | -121.8384 | 121.5546 | 121.6003 | 78.6575 | 0.39368
1862.1562 | 121.8109 | -0.21057 | 121.6324 | -0.85274 | 0.80997 | 0.076078 | 0.058612 | -0.0021277 | 0.77646 | 0.0055307 | -0.046661 | 0.0072333 | 0.0662 | 0.046628 | -0.013456 | 0.025485 | -0.0098523 | 63.8351 | 121.3943 | -0.10986 | 121.3806 | 6.1707 | 120.9137 | 1.4236 | 0.39825 | 121.4264 | -0.18768 | 121.4035 | -0.041199 | -0.07782 | -0.050354 | 0.10071 | -0.23804 | -0.25177 | 6.3812 | 1.6342 | 121.1243 | 1.5335 | 121.0236 | 0.022888 | -0.20599 | -0.22888 | 0.16937 | 0.16022 | 0.13275 | 0.13733 | 0.10986 | 6.2805 | 121.4905 | 0.14648 | 121.5912 | 121.5042 | 121.6141 | 121.6049 | 121.637 | -121.7422 | -121.8201 | 121.5912 | 121.6141 | 64.0457 | 0.60882
1863.8438 | 121.9162 | -0.17395 | 121.5637 | -0.96718 | 0.80676 | 0.078214 | 0.064166 | -0.00084593 | 0.77368 | 0.0044627 | -0.09549 | 0.0085149 | 0.0662 | 0.04855 | -0.016233 | 0.026981 | -0.0028027 | 80.9921 | 121.4264 | -0.091553 | 121.4081 | 6.189 | 120.8908 | 1.4465 | 0.31128 | 121.3852 | -0.17853 | 121.4996 | 0.041199 | 0.009155 | 0.059509 | 0.082397 | -0.13733 | -0.15564 | 6.3629 | 1.6205 | 121.0648 | 1.5381 | 120.9824 | -0.004578 | -0.17853 | -0.064087 | 0.21515 | 0.23346 | 0.1831 | 0.23804 | 0.18768 | 6.2805 | 121.4996 | 0.21973 | 121.6782 | 121.5179 | 121.5637 | 121.6003 | 121.5591 | -121.6553 | -121.7422 | 121.582 | 121.6736 | 81.1661 | 0.48523
1865.5938 | 121.8521 | -0.17853 | 121.5454 | -0.95955 | 0.798 | 0.077146 | 0.061816 | -0.0010595 | 0.77133 | 0.0061717 | -0.019196 | 0.0072333 | 0.064063 | 0.056027 | -0.014311 | 0.028262 | -0.0028027 | 68.6737 | 121.4218 | -0.091553 | 121.3715 | 5.9875 | 120.8817 | 1.4053 | 0.28381 | 121.4127 | -0.18768 | 121.4355 | 0.004578 | -0.022888 | -0.009155 | 0.086975 | -0.1236 | -0.17395 | 6.1661 | 1.5839 | 121.0602 | 1.4969 | 120.9732 | -0.009155 | -0.13275 | -0.10986 | 0.18311 | 0.16937 | 0.15564 | 0.17853 | 0.16479 | 6.0791 | 121.463 | 0.19226 | 121.6232 | 121.5134 | 121.6003 | 121.6003 | 121.5912 | -121.637 | -121.7331 | 121.55 | 121.6141 | 68.8522 | 0.46234
1867.3438 | 121.8338 | -0.19226 | 121.5683 | -0.88325 | 0.7948 | 0.078427 | 0.06502 | 0.0015039 | 0.76578 | 0.0059579 | -0.083283 | 0.0091559 | 0.065132 | 0.050686 | -0.014311 | 0.027408 | -2.571e-05 | 67.5568 | 121.4355 | -0.12817 | 121.3028 | 5.8731 | 120.7901 | 1.3275 | 0.21515 | 121.4447 | -0.19226 | 121.4127 | -0.041199 | -0.091553 | -0.027466 | 0.064087 | -0.13275 | -0.2655 | 6.0654 | 1.5198 | 120.9824 | 1.4557 | 120.9183 | 0 | -0.1236 | -0.15564 | 0.15106 | 0.16479 | 0.10071 | 0.16479 | 0.10071 | 6.0013 | 121.431 | 0.15106 | 121.6049 | 121.5637 | 121.637 | 121.6278 | 121.637 | -121.6965 | -121.7606 | 121.4951 | 121.6049 | 67.749 | 0.40741
1869.1094 | 121.8338 | -0.18768 | 121.5637 | -0.88325 | 0.78754 | 0.076505 | 0.062884 | -0.00041873 | 0.75915 | 0.0053171 | -0.028351 | 0.0093695 | 0.061927 | 0.048764 | -0.01602 | 0.026126 | -0.0034435 | 67.3965 | 121.3669 | -0.10071 | 121.344 | 5.928 | 120.8588 | 1.4053 | 0.27924 | 121.3898 | -0.18768 | 121.4127 | -0.018311 | -0.045776 | -0.009155 | 0.086975 | -0.19684 | -0.21973 | 6.1157 | 1.593 | 121.0464 | 1.506 | 120.9595 | 0 | -0.17395 | -0.15106 | 0.16937 | 0.17853 | 0.14191 | 0.17853 | 0.14191 | 6.0287 | 121.4447 | 0.16937 | 121.6003 | 121.4676 | 121.5775 | 121.5546 | 121.5775 | -121.6644 | -121.7514 | 121.5317 | 121.6003 | 67.5842 | 0.46692
1870.7969 | 121.7651 | -0.21057 | 121.5317 | -0.91377 | 0.78433 | 0.076718 | 0.065875 | -0.00063233 | 0.75638 | 0.0072397 | -0.1138 | 0.0076605 | 0.065772 | 0.047268 | -0.015806 | 0.027194 | -0.0028027 | 71.3974 | 121.431 | -0.13733 | 121.2524 | 5.8228 | 120.7718 | 1.3046 | 0.17853 | 121.4218 | -0.21057 | 121.3486 | -0.082397 | -0.12817 | -0.068665 | 0.073242 | -0.10071 | -0.27924 | 6.0333 | 1.5152 | 120.9824 | 1.442 | 120.9091 | 0 | -0.10986 | -0.1831 | 0.12817 | 0.14191 | 0.082397 | 0.14191 | 0.082397 | 5.9601 | 121.3898 | 0.12817 | 121.5591 | 121.5683 | 121.6324 | 121.6415 | 121.6324 | -121.669 | -121.7422 | 121.463 | 121.5591 | 71.608 | 0.3891
1872.5469 | 121.7606 | -0.20142 | 121.5408 | -0.85274 | 0.7822 | 0.077359 | 0.068438 | 0.0010767 | 0.75189 | 0.0065989 | -0.11075 | 0.010651 | 0.065132 | 0.05795 | -0.01666 | 0.027621 | -0.0040845 | 70.3812 | 121.4264 | -0.12817 | 121.2662 | 5.777 | 120.7718 | 1.3184 | 0.16479 | 121.4355 | -0.19684 | 121.3669 | -0.09613 | -0.13733 | -0.073242 | 0.073242 | -0.11444 | -0.27466 | 5.9784 | 1.5198 | 120.9732 | 1.4465 | 120.9 | 0.004578 | -0.10529 | -0.17395 | 0.10529 | 0.12817 | 0.064087 | 0.1236 | 0.059509 | 5.9052 | 121.3943 | 0.10071 | 121.5637 | 121.5546 | 121.6324 | 121.6278 | 121.637 | -121.669 | -121.7377 | 121.4676 | 121.5683 | 70.5826 | 0.36621
1874.2969 | 121.7926 | -0.2243 | 121.5317 | -0.87563 | 0.776 | 0.078641 | 0.064807 | -0.0061865 | 0.74484 | 0.0070261 | -0.077179 | 0.0089423 | 0.064704 | 0.050686 | -0.01602 | 0.027621 | -0.0057935 | 73.1781 | 121.3943 | -0.14191 | 121.257 | 5.7953 | 120.8221 | 1.3321 | 0.31128 | 121.4035 | -0.20599 | 121.3531 | -0.050354 | -0.10986 | -0.059509 | 0.082397 | -0.13733 | -0.27466 | 6.0196 | 1.5564 | 121.0464 | 1.474 | 120.9641 | 0.01831 | -0.12817 | -0.17853 | 0.17395 | 0.16479 | 0.11444 | 0.14649 | 0.096131 | 5.9372 | 121.3989 | 0.15564 | 121.5591 | 121.5363 | 121.6095 | 121.6187 | 121.6278 | -121.6736 | -121.7377 | 121.4813 | 121.5775 | 73.4024 | 0.53558
1876 | 121.7834 | -0.20599 | 121.5729 | -0.90614 | 0.77151 | 0.076078 | 0.06737 | 0.0010767 | 0.74271 | 0.0065989 | -0.092438 | 0.0089423 | 0.067054 | 0.049618 | -0.012815 | 0.026981 | -0.00066651 | 61.3495 | 121.3806 | -0.14648 | 121.2982 | 5.7632 | 120.8359 | 1.3641 | 0.36621 | 121.3943 | -0.19226 | 121.3852 | -0.027466 | -0.086975 | -0.036621 | 0.05951 | -0.19226 | -0.27466 | 5.9692 | 1.5701 | 121.0419 | 1.5106 | 120.9824 | 0.013733 | -0.17853 | -0.18768 | 0.17853 | 0.16937 | 0.11902 | 0.15564 | 0.10529 | 5.9097 | 121.4447 | 0.16479 | 121.5775 | 121.5271 | 121.5866 | 121.5866 | 121.6003 | -121.7194 | -121.7651 | 121.5042 | 121.5912 | 61.5555 | 0.57221
1877.75 | 121.875 | -0.19226 | 121.5225 | -0.93666 | 0.70444 | 0.079923 | 0.1306 | -0.0014867 | 0.73736 | 0.0070261 | 0.014374 | 0.0057379 | 0.06855 | 0.046841 | -0.013883 | 0.027408 | -0.0010937 | 121.1517 | 121.3486 | -0.11444 | 121.3257 | 5.9921 | 120.8817 | 1.4282 | 0.35706 | 121.3623 | -0.18768 | 121.4218 | 0.041199 | 0.018311 | 0.027466 | 0.07782 | -0.17395 | -0.19684 | 6.1844 | 1.6205 | 121.0739 | 1.5427 | 120.9961 | 0.004578 | -0.16022 | -0.10071 | 0.23346 | 0.21973 | 0.21057 | 0.21515 | 0.20599 | 6.1066 | 121.4401 | 0.22888 | 121.6095 | 121.463 | 121.55 | 121.5408 | 121.5546 | -121.637 | -121.7102 | 121.5179 | 121.6141 | 121.344 | 0.54932
1879.5156 | 121.7377 | -0.21057 | 121.5317 | -0.82985 | 0.53461 | 0.076718 | 0.29808 | 0.0027857 | 0.73416 | 0.0074533 | -0.083283 | 0.0070197 | 0.065559 | 0.044705 | -0.014097 | 0.027194 | -0.0040845 | 121.1472 | 121.3623 | -0.16022 | 121.225 | 5.8868 | 120.845 | 1.3046 | 0.32501 | 121.3989 | -0.21057 | 121.3074 | -0.073242 | -0.10986 | -0.07782 | 0.050354 | -0.16937 | -0.3067 | 6.0974 | 1.5152 | 121.0556 | 1.4648 | 121.0052 | 0 | -0.13275 | -0.2243 | 0.13733 | 0.13275 | 0.10071 | 0.13275 | 0.10071 | 6.0471 | 121.3852 | 0.13733 | 121.5179 | 121.5225 | 121.6095 | 121.5729 | 121.6095 | -121.6919 | -121.7422 | 121.4355 | 121.5179 | 121.3577 | 0.53558
1881.2656 | 121.8109 | -0.1831 | 121.5271 | -0.89088 | 0.48462 | 0.079282 | 0.34358 | 0.0015039 | 0.72967 | 0.0076669 | -0.028351 | 0.0089423 | 0.063423 | 0.047696 | -0.014951 | 0.02634 | -0.00045291 | 121.1838 | 121.3577 | -0.10071 | 121.2936 | 5.8914 | 120.9045 | 1.3962 | 0.27466 | 121.3623 | -0.18768 | 121.376 | 0 | -0.054932 | -0.009155 | 0.082397 | -0.16937 | -0.23346 | 6.0745 | 1.5793 | 121.0876 | 1.4969 | 121.0052 | -0.004578 | -0.16479 | -0.15106 | 0.1831 | 0.17395 | 0.12817 | 0.17853 | 0.13275 | 5.9921 | 121.3943 | 0.18768 | 121.5637 | 121.4584 | 121.55 | 121.5408 | 121.5454 | -121.6278 | -121.7148 | 121.4767 | 121.5591 | 121.3669 | 0.45776
1882.9531 | 121.843 | -0.19226 | 121.5042 | -0.868 | 0.46176 | 0.079068 | 0.36089 | 0.00043587 | 0.72583 | 0.0068125 | 0.0021667 | 0.0093695 | 0.067268 | 0.050046 | -0.01367 | 0.02634 | -0.0053661 | 121.2021 | 121.3348 | -0.09613 | 121.2982 | 5.8456 | 120.9137 | 1.4145 | 0.33875 | 121.3486 | -0.19226 | 121.3989 | 0.018311 | 0 | 0.027466 | 0.096131 | -0.16937 | -0.20599 | 6.0379 | 1.6068 | 121.106 | 1.5106 | 121.0098 | 0 | -0.15564 | -0.10528 | 0.21057 | 0.21973 | 0.19226 | 0.21973 | 0.19226 | 5.9418 | 121.3943 | 0.21057 | 121.5912 | 121.431 | 121.5408 | 121.5271 | 121.5408 | -121.6003 | -121.6965 | 121.4905 | 121.5912 | 121.3943 | 0.53101
1884.7031 | 121.8109 | -0.18768 | 121.4676 | -0.87563 | 0.45172 | 0.080136 | 0.36922 | -0.0025549 | 0.72455 | 0.0051035 | -0.016144 | 0.0074469 | 0.064491 | 0.047268 | -0.015592 | 0.026126 | 0.00061529 | 121.1884 | 121.3348 | -0.1236 | 121.2845 | 5.7999 | 120.8862 | 1.4008 | 0.27924 | 121.3531 | -0.20142 | 121.3715 | -0.013733 | -0.022888 | 0 | 0.064087 | -0.13275 | -0.1831 | 5.9875 | 1.5884 | 121.0739 | 1.5244 | 121.0098 | -0.013733 | -0.11444 | -0.09613 | 0.17395 | 0.18768 | 0.16479 | 0.20142 | 0.17853 | 5.9235 | 121.4081 | 0.18768 | 121.5729 | 121.4584 | 121.5546 | 121.5225 | 121.5408 | -121.5912 | -121.669 | 121.4722 | 121.5591 | 121.376 | 0.46692
1886.4531 | 121.7148 | -0.21515 | 121.5454 | -0.868 | 0.44232 | 0.078214 | 0.37264 | -0.0017005 | 0.72134 | 0.0068125 | -0.077179 | 0.010438 | 0.065772 | 0.051755 | -0.01666 | 0.026553 | -0.0042981 | 121.1472 | 121.3669 | -0.12817 | 121.2296 | -0.041199 | 120.8496 | 1.2817 | 0.31128 | 121.376 | -0.21057 | 121.2845 | -0.082397 | -0.1236 | -0.086975 | 0.086975 | -0.17853 | -0.31586 | 0.17395 | 1.4969 | 121.0648 | 1.4099 | 120.9778 | 0.004578 | -0.16937 | -0.26093 | 0.13275 | 0.12817 | 0.091553 | 0.1236 | 0.086975 | 0.086975 | 121.3577 | 0.12817 | 121.4951 | 121.4951 | 121.5866 | 121.582 | 121.5912 | -121.6736 | -121.756 | 121.4447 | 121.4996 | 121.3623 | 0.52643
1888.2031 | 121.7148 | -0.23804 | 121.5134 | -0.89851 | 0.43869 | 0.079068 | 0.37328 | -0.0070409 | 0.71344 | 0.0068125 | -0.040558 | 0.0083013 | 0.063423 | 0.056881 | -0.014311 | 0.026553 | -0.0017347 | 121.1472 | 121.3806 | -0.11902 | 121.2296 | -0.027466 | 120.8588 | 1.3 | 0.33417 | 121.376 | -0.21515 | 121.2845 | -0.068665 | -0.11902 | -0.091553 | 0.11902 | -0.13275 | -0.28381 | 0.21057 | 1.5381 | 121.0968 | 1.4191 | 120.9778 | 0.022888 | -0.13733 | -0.22888 | 0.16937 | 0.14648 | 0.11902 | 0.1236 | 0.09613 | 0.091553 | 121.3486 | 0.14648 | 121.4996 | 121.4996 | 121.5912 | 121.6187 | 121.6141 | -121.6324 | -121.7285 | 121.4676 | 121.5225 | 121.3852 | 0.5722
1889.8906 | 121.7697 | -0.20142 | 121.4996 | -0.82985 | 0.43741 | 0.088895 | 0.37435 | -0.00020513 | 0.71536 | 0.0010447 | -0.15042 | 0.0078741 | 0.066627 | 0.055173 | -0.015592 | 0.02869 | -0.0042981 | 121.2112 | 121.3577 | -0.12817 | 121.2799 | 0.018311 | 120.9 | -0.018311 | 0.3479 | 121.3715 | -0.17853 | 121.376 | -0.018311 | -0.068665 | -0.022888 | 0.073242 | -0.14191 | -0.21973 | 0.21973 | 0.18311 | 121.1014 | 0.10986 | 121.0281 | 0.022888 | -0.12817 | -0.1236 | 0.18311 | 0.17853 | 0.13275 | 0.15564 | 0.10986 | 0.14649 | 121.4081 | 0.16022 | 121.5546 | 121.4859 | 121.55 | 121.5591 | 121.5729 | -121.6278 | -121.6782 | 121.4813 | 121.5775 | 121.4127 | 0.54932
1891.6406 | 121.7194 | -0.20599 | 121.5225 | -0.84511 | 0.43655 | 0.089536 | 0.37349 | 0.0029993 | 0.71216 | -0.0021597 | -0.11075 | 0.0091559 | 0.065132 | 0.049832 | -0.015592 | 0.029544 | -0.0045117 | 121.1792 | 121.3852 | -0.12817 | 121.2067 | -0.045776 | 120.7993 | -0.064087 | 0.19226 | 121.3715 | -0.21057 | 121.3257 | -0.07782 | -0.11444 | -0.059509 | 0.07782 | -0.13733 | -0.31586 | 0.16022 | 0.14191 | 121.0052 | 0.064087 | 120.9274 | -0.004577 | -0.15106 | -0.19684 | 0.12817 | 0.14649 | 0.091553 | 0.15106 | 0.09613 | 0.082398 | 121.3348 | 0.13275 | 121.5363 | 121.5134 | 121.582 | 121.5912 | 121.5775 | -121.6507 | -121.7331 | 121.4127 | 121.5317 | 121.3852 | 0.39826
1893.4062 | 121.8063 | -0.17853 | 121.4859 | -0.86037 | 0.44168 | 0.10235 | 0.37905 | -0.0031957 | 0.70917 | -0.0038687 | -0.0039367 | 0.0085149 | 0.065559 | 0.043637 | -0.014738 | 0.027621 | -0.0028027 | 121.1792 | 121.3394 | -0.10071 | 121.2799 | 0.054932 | 120.9 | 0.018311 | 0.30212 | 121.3211 | -0.1831 | 121.3669 | 0.018311 | -0.009155 | 0.009155 | 0.07782 | -0.14648 | -0.20599 | 0.23346 | 0.19684 | 121.0785 | 0.11902 | 121.0007 | -0.004577 | -0.16479 | -0.11902 | 0.19684 | 0.18768 | 0.16937 | 0.19226 | 0.17395 | 0.15564 | 121.3806 | 0.20142 | 121.55 | 121.4401 | 121.5042 | 121.5179 | 121.4996 | -121.5866 | -121.669 | 121.4584 | 121.5454 | 121.3577 | 0.48065
1895.1562 | 121.8338 | -0.14648 | 121.4859 | -0.097427 | -0.047303 | 0.0017368 | 0.025073 | -0.0021277 | -0.009675 | -0.0023733 | -0.0008851 | 0.0057379 | 0.067481 | 0.048764 | -0.016447 | 0.025272 | -0.0049389 | 0.40741 | 0.49439 | 0.46234 | 0.52185 | 0.6134 | 0.51727 | 0.54016 | 0.45776 | 121.3211 | -0.13275 | 121.4264 | 0.09613 | 0.073242 | 0.068665 | 0.60882 | -120.9915 | -120.9641 | 0.75989 | 0.68664 | 0.66376 | 0.07782 | 0.054932 | 0.013733 | -0.16479 | -0.059509 | 0.24261 | 0.21515 | 0.21973 | 0.20142 | 0.20599 | 0.15106 | 0.05951 | 0.22888 | 121.5591 | 0.032044 | 121.4539 | 0.64087 | 121.4676 | -121.0236 | -121.6187 | 0.66833 | 121.5729 | 0.55389 | 0.60425
1896.8438 | 121.843 | -0.16479 | 121.5454 | -0.13557 | -0.04538 | 0.0034456 | 0.025927 | -0.0021277 | -0.0088206 | -0.0042959 | -0.028351 | 0.0070197 | 0.065132 | 0.045132 | -0.017729 | 0.027621 | -0.0023755 | 0.07782 | 0.21057 | 0.15564 | 0.15106 | 0.22888 | 0.13275 | 0.20599 | 0.27008 | 121.4035 | -0.16937 | 121.431 | 0.004578 | -0.022888 | 0.004578 | 0.32044 | -121.3348 | -121.3943 | 0.39368 | 0.37079 | 0.29755 | 0.050354 | -0.022889 | -0.004578 | -0.14191 | -0.11444 | 0.16937 | 0.16937 | 0.14191 | 0.17395 | 0.14649 | 0.073242 | -0.004578 | 0.17395 | 121.6003 | 0.054931 | 121.5729 | 0.37537 | 121.5683 | -121.3898 | -121.7148 | 0.31586 | 121.5958 | 0.24261 | 0.43488
1898.5938 | 121.8384 | -0.19226 | 121.6141 | -0.05928 | -0.04773 | 0.002164 | 0.027423 | -0.00020513 | -0.0077524 | -0.00066434 | -0.11685 | 0.0046697 | 0.064918 | 0.05325 | -0.017942 | 0.025912 | -0.0085705 | 0.013733 | 0.19684 | 0.11444 | 0.073242 | 0.13733 | 0.068665 | 0.13733 | 0.31586 | 121.4584 | -0.17395 | 121.4218 | -0.018311 | -0.07782 | -0.032043 | 0.3067 | -121.4172 | -121.5408 | 0.32959 | 0.32959 | 0.26093 | 0.022888 | -0.045776 | 0.018311 | -0.15564 | -0.19226 | 0.17395 | 0.16022 | 0.11444 | 0.14191 | 0.09613 | 0.022888 | -0.041199 | 0.15564 | 121.5958 | 0.082397 | 121.6324 | 0.3891 | 121.6507 | -121.4996 | -121.788 | 0.2655 | 121.6141 | 0.20599 | 0.50812
1900.3594 | 121.875 | -0.16479 | 121.637 | -0.12794 | -0.047089 | 0.0023776 | 0.023791 | -0.0029821 | -0.0094614 | -0.0034415 | -0.052765 | 0.0061651 | 0.061927 | 0.052395 | -0.015592 | 0.026981 | -0.0030163 | 0.064087 | 0.15564 | 0.13275 | 0.15564 | 0.2655 | 0.15564 | 0.21973 | 0.42572 | 121.4859 | -0.16479 | 121.4539 | 0.032043 | -0.004578 | 0.009155 | 0.29755 | -121.4813 | -121.4813 | 0.4303 | 0.38452 | 0.32044 | 0.086976 | 0.022889 | 0 | -0.15106 | -0.18311 | 0.19684 | 0.17395 | 0.16022 | 0.17395 | 0.16022 | 0.13275 | 0.022889 | 0.19684 | 121.6187 | 0.022889 | 121.6507 | 0.32044 | 121.6507 | -121.5042 | -121.8018 | 0.32044 | 121.6187 | 0.22888 | 0.59052
1902.1094 | 121.8796 | -0.18768 | 121.6507 | -0.12794 | -0.044312 | 0.0028048 | 0.026782 | -0.0042639 | -0.010957 | -0.0030141 | -0.12296 | 0.0063787 | 0.063423 | 0.056668 | -0.016447 | 0.026981 | -0.0051525 | 0.022888 | 0.15564 | 0.073242 | 0.068665 | 0.15564 | 0.036621 | 0.10529 | 0.3479 | 121.4996 | -0.15106 | 121.463 | -0.009155 | -0.064087 | -0.013733 | 0.26092 | -121.4951 | -121.582 | 0.34332 | 0.29297 | 0.2243 | 0.032044 | -0.036621 | 0.036621 | -0.15106 | -0.18768 | 0.17853 | 0.17395 | 0.1236 | 0.13733 | 0.086975 | 0.082398 | -0.004577 | 0.14191 | 121.6141 | 0.082398 | 121.6507 | 0.34332 | 121.6873 | -121.5775 | -121.8018 | 0.25635 | 121.6507 | 0.21057 | 0.53558
1903.7969 | 121.8246 | -0.17395 | 121.637 | -0.097427 | -0.044525 | 0.0043002 | 0.029345 | 0.0044947 | -0.0088206 | -0.0028005 | -0.12601 | 0.0053107 | 0.065986 | 0.047055 | -0.015379 | 0.02933 | -0.0085705 | -0.041199 | 0.13275 | 0.032043 | -0.004578 | 0.032043 | -0.059509 | 0.027466 | 0.17853 | 121.5225 | -0.18768 | 121.4127 | -0.091553 | -0.15564 | -0.064087 | 0.20599 | -121.5042 | -121.6415 | 0.20599 | 0.20142 | 0.11444 | -0.004577 | -0.091552 | -0.013733 | -0.11444 | -0.2243 | 0.082397 | 0.10986 | 0.01831 | 0.1236 | 0.032043 | 0 | -0.036621 | 0.09613 | 121.6003 | 0.10071 | 121.7102 | 0.3067 | 121.6965 | -121.6049 | -121.8246 | 0.16937 | 121.5866 | 0.13275 | 0.35248
1905.5469 | 121.8887 | -0.18768 | 121.6827 | -0.06691 | -0.047516 | 0.0028048 | 0.026568 | -0.0027685 | -0.007966 | -0.0040823 | -0.086334 | 0.0055243 | 0.064063 | 0.046841 | -0.013456 | 0.026553 | -0.0030163 | -0.022888 | 0.16022 | 0.054932 | 0.018311 | 0.09613 | 0.032043 | 0.082397 | 0.33417 | 121.5088 | -0.19226 | 121.4813 | -0.013733 | -0.073242 | -0.018311 | 0.24261 | -121.5225 | -121.6644 | 0.28381 | 0.27008 | 0.21973 | 0.027465 | -0.022889 | -0.004578 | -0.17395 | -0.20142 | 0.17395 | 0.16937 | 0.11444 | 0.17395 | 0.11902 | 0.041198 | -0.036621 | 0.17853 | 121.6736 | 0.10528 | 121.701 | 0.3479 | 121.6965 | -121.6278 | -121.875 | 0.20599 | 121.669 | 0.16479 | 0.52185
1907.2969 | 121.962 | -0.15564 | 121.6644 | -0.21187 | -0.04538 | 0.0057956 | 0.026996 | 0.0017175 | -0.009675 | -0.0028005 | -0.013092 | 0.0068059 | 0.066413 | 0.049618 | -0.011106 | 0.027194 | -0.0085705 | 0.004578 | 0.073242 | 0.068665 | 0.09613 | 0.21515 | 0.050354 | 0.12817 | 0.32044 | 121.4996 | -0.15106 | 121.55 | 0.059509 | 0.018311 | 0.068665 | 0.22431 | -121.5912 | -121.5683 | 0.37079 | 0.28381 | 0.20599 | 0.059509 | -0.018311 | 0.004578 | -0.16479 | -0.11444 | 0.21515 | 0.22431 | 0.17395 | 0.21973 | 0.16937 | 0.14648 | 0.027465 | 0.21057 | 121.701 | 0.004577 | 121.6507 | 0.22888 | 121.6553 | -121.5958 | -121.8155 | 0.25177 | 121.7056 | 0.16022 | 0.47608
1909 | 121.9849 | -0.15564 | 121.6415 | -0.15083 | -0.04773 | 0.004941 | 0.024218 | -0.0081091 | -0.0083932 | -0.0036551 | 0.014374 | 0.0044561 | 0.063636 | 0.051755 | -0.016447 | 0.027621 | -0.0036573 | 0.027466 | 0.09613 | 0.086975 | 0.13733 | 0.25177 | 0.15106 | 0.19226 | 0.45776 | 121.5134 | -0.14648 | 121.5683 | 0.07782 | 0.041199 | 0.059509 | 0.24261 | -121.5454 | -121.5042 | 0.40741 | 0.3479 | 0.3067 | 0.10529 | 0.064087 | 0.009156 | -0.12817 | -0.073243 | 0.23346 | 0.21515 | 0.19684 | 0.20599 | 0.18768 | 0.16479 | 0.050354 | 0.2243 | 121.7148 | 0.009155 | 121.6599 | 0.25177 | 121.669 | -121.5546 | -121.788 | 0.29297 | 121.7239 | 0.18311 | 0.6134
1910.75 | 121.875 | -0.20142 | 121.6965 | -0.15083 | -0.043457 | 0.0043002 | 0.029559 | -0.0014867 | -0.007966 | -0.0060049 | -0.098541 | 0.0055243 | 0.064063 | 0.045987 | -0.015165 | 0.027621 | -0.0038709 | -0.082397 | 0.086975 | 0.009155 | -0.041199 | 0.018311 | -0.082397 | 0.018311 | 0.17395 | 121.5271 | -0.18768 | 121.4676 | -0.082397 | -0.13733 | -0.064087 | 0.21057 | -121.6095 | -121.7377 | 0.21973 | 0.21973 | 0.11902 | 0.009156 | -0.091552 | 0.013733 | -0.16937 | -0.22888 | 0.11902 | 0.13733 | 0.064087 | 0.1236 | 0.050354 | 0.009156 | -0.050354 | 0.10529 | 121.6553 | 0.07782 | 121.7148 | 0.28839 | 121.7285 | -121.6873 | -121.8842 | 0.16022 | 121.669 | 0.11902 | 0.37537
1912.5 | 121.9482 | -0.16937 | 121.6873 | -0.12794 | -0.046234 | 0.0023776 | 0.024646 | -0.0019141 | -0.0081796 | -0.0057913 | -0.019196 | 0.0044561 | 0.065559 | 0.047909 | -0.015806 | 0.025272 | -0.0051525 | -0.050354 | 0.07782 | 0.050354 | 0.045776 | 0.12817 | 0.032043 | 0.11444 | 0.27466 | 121.5134 | -0.16937 | 121.5271 | -0.004578 | -0.045776 | 0.009155 | 0.21973 | -121.6095 | -121.6415 | 0.29755 | 0.28381 | 0.20142 | 0.064087 | -0.018311 | 0 | -0.17395 | -0.16022 | 0.16479 | 0.17853 | 0.1236 | 0.17853 | 0.1236 | 0.07782 | -0.004578 | 0.16479 | 121.6965 | 0.027466 | 121.6827 | 0.24719 | 121.6827 | -121.637 | -121.8567 | 0.21515 | 121.6965 | 0.11902 | 0.44403
1914.25 | 121.9849 | -0.16479 | 121.6965 | -0.1432 | -0.047089 | 0.0023776 | 0.024859 | -0.0029821 | -0.0088206 | -0.0015189 | -0.019196 | 0.0027471 | 0.065132 | 0.049405 | -0.015592 | 0.02634 | -0.0081433 | -0.032043 | 0.07782 | 0.054932 | 0.050354 | 0.13275 | 0.036621 | 0.10071 | 0.29755 | 121.5317 | -0.16937 | 121.55 | 0.013733 | 0 | 0.013733 | 0.21973 | -121.6187 | -121.6461 | 0.29755 | 0.2655 | 0.20142 | 0.045776 | -0.018311 | -0.004578 | -0.16479 | -0.14648 | 0.17853 | 0.17853 | 0.16479 | 0.18311 | 0.16937 | 0.077819 | -0.004578 | 0.18311 | 121.7194 | 0.022888 | 121.701 | 0.24261 | 121.6965 | -121.6415 | -121.8658 | 0.21515 | 121.7148 | 0.13275 | 0.46234
1915.9375 | 121.9757 | -0.13733 | 121.6919 | -0.16609 | -0.047089 | 0.003232 | 0.025714 | -0.0021277 | -0.0066844 | -0.00066434 | -0.040558 | 0.0063787 | 0.064491 | 0.044919 | -0.014097 | 0.027194 | -0.0042981 | -0.032043 | 0.064087 | 0.045776 | 0.045776 | 0.16022 | 0.027466 | 0.09613 | 0.28381 | 121.5225 | -0.17395 | 121.55 | 0.018311 | -0.018311 | 0.009155 | 0.18311 | -121.6278 | -121.6461 | 0.29755 | 0.23346 | 0.16479 | 0.050354 | -0.01831 | -0.036621 | -0.16937 | -0.14191 | 0.15564 | 0.14648 | 0.11902 | 0.1831 | 0.15564 | 0.11444 | 0 | 0.19226 | 121.7239 | 0.018311 | 121.6965 | 0.20142 | 121.6599 | -121.6461 | -121.8658 | 0.18311 | 121.6873 | 0.10529 | 0.42114
1917.6719 | 121.9025 | -0.20599 | 121.701 | -0.13557 | -0.045807 | 0.0034456 | 0.028277 | -0.0023413 | -0.0092478 | -0.0040823 | -0.11685 | 0.0055243 | 0.065132 | 0.054959 | -0.017515 | 0.026126 | -0.0021619 | -0.086975 | 0.07782 | -0.004578 | -0.050354 | 0.009155 | -0.10071 | -0.013733 | 0.16479 | 121.5866 | -0.19226 | 121.5088 | -0.091553 | -0.11902 | -0.059509 | 0.20142 | -121.6232 | -121.7514 | 0.21515 | 0.19226 | 0.10529 | -0.009155 | -0.09613 | 0.013733 | -0.11444 | -0.19226 | 0.11444 | 0.14649 | 0.086975 | 0.13275 | 0.073242 | 0.013733 | -0.045776 | 0.10071 | 121.701 | 0.082398 | 121.7789 | 0.28381 | 121.7926 | -121.7056 | -121.8933 | 0.15564 | 121.7148 | 0.11902 | 0.37079
1919.4375 | 121.8842 | -0.18768 | 121.7422 | -0.097427 | -0.046234 | 0.0051546 | 0.028705 | 0.0012903 | -0.0081796 | -0.0049367 | -0.11685 | 0.0044561 | 0.064491 | 0.051541 | -0.015165 | 0.027835 | -0.0040845 | -0.036621 | 0.086975 | 0.032043 | -0.004578 | 0.059509 | -0.068665 | 0.018311 | 0.25635 | 121.5637 | -0.20142 | 121.4951 | -0.07782 | -0.13733 | -0.054932 | 0.21973 | -121.6553 | -121.7468 | 0.24719 | 0.20599 | 0.11902 | -0.013732 | -0.10071 | -0.013733 | -0.17853 | -0.24719 | 0.10986 | 0.13275 | 0.050354 | 0.14648 | 0.064087 | 0.027466 | -0.036621 | 0.1236 | 121.6965 | 0.054932 | 121.7651 | 0.27466 | 121.7514 | -121.7102 | -121.9437 | 0.1831 | 121.6827 | 0.15106 | 0.44403
1921.2031 | 121.9254 | -0.20142 | 121.7377 | -0.12794 | -0.045166 | 0.0019504 | 0.029132 | -0.00084593 | -0.0056162 | -0.0049367 | -0.1138 | 0.0068059 | 0.065559 | 0.054104 | -0.014738 | 0.027194 | -0.0066479 | -0.022888 | 0.07782 | 0.013733 | 0.032043 | 0.10986 | -0.009155 | 0.059509 | 0.33875 | 121.5775 | -0.16937 | 121.5408 | -0.036621 | -0.07782 | -0.032043 | 0.21515 | -121.6599 | -121.7056 | 0.31128 | 0.26093 | 0.19226 | 0.045776 | -0.022888 | 0.032043 | -0.16022 | -0.19684 | 0.1648 | 0.16937 | 0.1236 | 0.13733 | 0.091553 | 0.09613 | 0.01831 | 0.13275 | 121.7102 | 0.064087 | 121.7468 | 0.27924 | 121.7789 | -121.7239 | -121.907 | 0.23346 | 121.7422 | 0.17853 | 0.54016
1922.9062 | 121.907 | -0.21057 | 121.7697 | -0.2195 | -0.044098 | 0.0028048 | 0.027636 | 0.00086307 | -0.0058298 | -0.0047231 | -0.12296 | 0.0057379 | 0.065345 | 0.048123 | -0.013242 | 0.029544 | -0.0051525 | -0.09613 | 0.086975 | -0.004578 | -0.068665 | -0.022888 | -0.11902 | -0.036621 | 0.17853 | 121.5729 | -0.18768 | 121.5042 | -0.086975 | -0.14648 | -0.059509 | 0.20599 | -121.6827 | -121.8384 | 0.18768 | 0.17395 | 0.091552 | -0.032043 | -0.11444 | 0.022888 | -0.19684 | -0.2655 | 0.1236 | 0.15106 | 0.064087 | 0.12817 | 0.041199 | -0.01831 | -0.064087 | 0.10071 | 121.6919 | 0.091553 | 121.7606 | 0.29755 | 121.7834 | -121.7743 | -121.9574 | 0.14191 | 121.7148 | 0.11444 | 0.3891
1924.6719 | 122.0306 | -0.16479 | 121.7377 | -0.10506 | -0.045807 | 0.003873 | 0.024432 | 0.0025721 | -0.0098886 | -0.0030141 | -0.0039367 | 0.0065923 | 0.064704 | 0.044064 | -0.013883 | 0.028049 | -0.0040845 | -0.054932 | 0.068665 | 0.050354 | 0.045776 | 0.15564 | 0.050354 | 0.11902 | 0.33417 | 121.5317 | -0.16022 | 121.5912 | 0.059509 | 0.036621 | 0.045776 | 0.21515 | -121.669 | -121.6919 | 0.32044 | 0.28381 | 0.21515 | 0.068665 | 0 | 0.004578 | -0.20599 | -0.14648 | 0.2243 | 0.21057 | 0.20142 | 0.20599 | 0.19684 | 0.10529 | -0.004578 | 0.21973 | 121.7514 | 0.018311 | 121.6919 | 0.23346 | 121.6965 | -121.6873 | -121.8979 | 0.21057 | 121.756 | 0.10986 | 0.49896
1926.4219 | 121.9391 | -0.17395 | 121.7514 | -0.15083 | -0.043671 | 0.0034456 | 0.026355 | -0.00084593 | -0.0073252 | 0.00061746 | -0.083283 | 0.0057379 | 0.065559 | 0.051114 | -0.015379 | 0.027408 | -0.0032299 | -0.027466 | 0.07782 | 0.027466 | 0.018311 | 0.1236 | 0.004578 | 0.059509 | 0.35248 | 121.5912 | -0.16479 | 121.5591 | -0.022888 | -0.091553 | -0.032043 | 0.20142 | -121.6736 | -121.7331 | 0.29755 | 0.23346 | 0.17853 | 0.032043 | -0.022888 | 0.009155 | -0.16022 | -0.19226 | 0.15106 | 0.14191 | 0.082397 | 0.13275 | 0.073242 | 0.09613 | -0.009155 | 0.14191 | 121.7239 | 0.050354 | 121.756 | 0.25177 | 121.7651 | -121.7239 | -121.9162 | 0.19226 | 121.7331 | 0.14648 | 0.52643
1928.1719 | 121.9345 | -0.19684 | 121.7743 | -0.051651 | -0.046662 | 0.0043002 | 0.026568 | 0.0038537 | -0.011598 | -0.0034415 | -0.028351 | 0.0048833 | 0.065986 | 0.0462 | -0.013883 | 0.028262 | -0.0038709 | -0.032043 | 0.082397 | 0.064087 | 0.027466 | 0.11444 | 0.022888 | 0.086975 | 0.37079 | 121.5958 | -0.19226 | 121.5225 | -0.045776 | -0.068665 | -0.059509 | 0.26093 | -121.6919 | -121.7468 | 0.31128 | 0.28381 | 0.21973 | 0.022888 | -0.041199 | 0.004577 | -0.17853 | -0.25177 | 0.15106 | 0.13733 | 0.12817 | 0.13275 | 0.1236 | 0.050354 | -0.036621 | 0.14648 | 121.7148 | 0.01831 | 121.788 | 0.27924 | 121.7926 | -121.7102 | -121.9666 | 0.2243 | 121.7194 | 0.1648 | 0.56763
1929.8594 | 121.9482 | -0.20142 | 121.7606 | -0.10506 | -0.049866 | 0.0013094 | 0.0255 | 0.00086307 | -0.007966 | -0.0028005 | -0.064972 | 0.0063787 | 0.067054 | 0.047268 | -0.016874 | 0.025699 | -0.0051525 | -0.059509 | 0.11444 | 0.041199 | -0.018311 | 0.054932 | -0.022888 | 0.050354 | 0.31128 | 121.6049 | -0.19226 | 121.5225 | -0.032043 | -0.09613 | -0.050354 | 0.24262 | -121.6461 | -121.7789 | 0.25635 | 0.25177 | 0.17853 | 0.009155 | -0.064087 | 0.009155 | -0.15564 | -0.23804 | 0.16937 | 0.15106 | 0.10529 | 0.14191 | 0.096131 | 0.013733 | -0.05951 | 0.16022 | 121.7148 | 0.073242 | 121.7972 | 0.31586 | 121.8063 | -121.7194 | -121.9528 | 0.18311 | 121.7239 | 0.14191 | 0.5127
1931.5938 | 121.9757 | -0.16937 | 121.7422 | -0.10506 | -0.045166 | 0.0047274 | 0.026568 | -0.0014867 | -0.006257 | -0.0010915 | -0.1077 | 0.0072333 | 0.06385 | 0.044919 | -0.014097 | 0.027835 | -0.0053661 | -0.041199 | 0.064087 | 0.018311 | 0.009155 | 0.13275 | 0.013733 | 0.07782 | 0.34332 | 121.582 | -0.15564 | 121.5683 | -0.013733 | -0.054932 | -0.009155 | 0.18768 | -121.6782 | -121.7331 | 0.30212 | 0.24719 | 0.18311 | 0.059509 | -0.004578 | 0.013733 | -0.16022 | -0.17395 | 0.15564 | 0.16022 | 0.11444 | 0.14649 | 0.10071 | 0.11444 | -0.009156 | 0.14191 | 121.7239 | 0.045776 | 121.7377 | 0.23346 | 121.7514 | -121.7239 | -121.8979 | 0.17853 | 121.7377 | 0.12817 | 0.5127
1933.3438 | 121.9986 | -0.16022 | 121.7468 | -0.10506 | -0.044098 | 0.0045138 | 0.026782 | 0.00022207 | -0.006257 | -0.0013051 | -0.064972 | 0.0061651 | 0.0662 | 0.047696 | -0.01367 | 0.028049 | -0.0023755 | -0.091553 | 0.064087 | 0 | -0.041199 | 0.041199 | -0.073242 | 0.009155 | 0.21057 | 121.6141 | -0.16479 | 121.6003 | 0 | -0.054932 | 0.009155 | 0.16022 | -121.6827 | -121.788 | 0.20142 | 0.16937 | 0.086975 | 0.009155 | -0.073242 | -0.004578 | -0.13275 | -0.14648 | 0.16022 | 0.16937 | 0.10528 | 0.17395 | 0.10986 | 0.041199 | -0.041199 | 0.16479 | 121.7651 | 0.064087 | 121.7789 | 0.2243 | 121.7743 | -121.7468 | -121.9116 | 0.11902 | 121.7606 | 0.068664 | 0.37079
1935.0938 | 121.9711 | -0.1831 | 121.7651 | -0.074539 | -0.04538 | 0.0062228 | 0.028277 | 0.00064947 | -0.0077524 | -0.0021597 | -0.086334 | 0.0076605 | 0.062782 | 0.053036 | -0.014311 | 0.027194 | -0.0045117 | -0.09613 | 0.064087 | -0.004578 | -0.045776 | 0.036621 | -0.082397 | 0.004578 | 0.20599 | 121.5912 | -0.17853 | 121.582 | -0.041199 | -0.091553 | -0.022888 | 0.17853 | -121.701 | -121.8109 | 0.21973 | 0.18768 | 0.10071 | 0.009156 | -0.077819 | 0.004577 | -0.17395 | -0.18311 | 0.14191 | 0.16022 | 0.091552 | 0.15564 | 0.086975 | 0.041199 | -0.041198 | 0.13733 | 121.7606 | 0.068665 | 121.7697 | 0.24719 | 121.7743 | -121.7697 | -121.9437 | 0.13733 | 121.7651 | 0.086975 | 0.3891
1936.7812 | 122.0261 | -0.16022 | 121.7651 | -0.15846 | -0.046875 | 0.0043002 | 0.027423 | -0.0031957 | -0.0056162 | -0.0034415 | -0.068024 | 0.0050971 | 0.064704 | 0.049191 | -0.012815 | 0.027408 | -0.0049389 | -0.10071 | 0.07782 | 0.009155 | -0.022888 | 0.045776 | -0.068665 | 0.018311 | 0.2243 | 121.6141 | -0.16479 | 121.6049 | 0.018311 | -0.027466 | 0.036621 | 0.16937 | -121.6873 | -121.788 | 0.20599 | 0.17853 | 0.091552 | 0.009156 | -0.07782 | -0.004578 | -0.15106 | -0.16022 | 0.17853 | 0.19684 | 0.13275 | 0.20142 | 0.13733 | 0.036621 | -0.032043 | 0.18311 | 121.7697 | 0.068665 | 121.7789 | 0.23804 | 121.7743 | -121.756 | -121.9299 | 0.13733 | 121.7651 | 0.059509 | 0.38452
1938.5312 | 121.9482 | -0.19226 | 121.7789 | -0.036392 | -0.046234 | 0.0023776 | 0.027636 | -0.0021277 | -0.010102 | -0.0057913 | -0.055817 | 0.0057379 | 0.064491 | 0.047696 | -0.015379 | 0.026767 | -0.0038709 | -0.082397 | 0.086975 | 0.022888 | -0.018311 | 0.073242 | -0.004578 | 0.059509 | 0.32501 | 121.6187 | -0.19226 | 121.5225 | -0.059509 | -0.082397 | -0.054932 | 0.21515 | -121.6919 | -121.7972 | 0.2655 | 0.25177 | 0.18768 | 0.036621 | -0.027466 | 0 | -0.16022 | -0.25635 | 0.13275 | 0.13733 | 0.10986 | 0.13733 | 0.10986 | 0.050354 | -0.041199 | 0.13275 | 121.7148 | 0.064087 | 121.8109 | 0.27924 | 121.8109 | -121.756 | -121.9711 | 0.17395 | 121.7148 | 0.10986 | 0.51727
1940.2969 | 121.9894 | -0.17395 | 121.7606 | -0.12794 | -0.046021 | 0.0019504 | 0.026141 | 0.00043587 | -0.0071116 | -0.0021597 | -0.06192 | 0.0076605 | 0.065559 | 0.051755 | -0.015165 | 0.026553 | -0.0066479 | -0.027466 | 0.073242 | 0.004578 | 0.009155 | 0.12817 | -0.004578 | 0.054932 | 0.35248 | 121.637 | -0.16479 | 121.5866 | 0.009155 | -0.036621 | 0.004578 | 0.17853 | -121.6873 | -121.7514 | 0.30212 | 0.22888 | 0.16937 | 0.050354 | -0.009156 | 0.009155 | -0.1236 | -0.17395 | 0.1831 | 0.17853 | 0.13733 | 0.16937 | 0.12817 | 0.1236 | 0.004577 | 0.17395 | 121.7514 | 0.068664 | 121.8018 | 0.24719 | 121.8109 | -121.756 | -121.9254 | 0.1831 | 121.7606 | 0.14648 | 0.52643
1941.9844 | 121.9894 | -0.19226 | 121.7651 | -0.097427 | -0.047303 | 0.0019504 | 0.025287 | -0.0017005 | -0.0081796 | -0.0049367 | -0.068024 | 0.0063787 | 0.065132 | 0.052182 | -0.014097 | 0.027621 | -0.0055799 | -0.068665 | 0.091553 | 0.027466 | -0.009155 | 0.073242 | -0.004578 | 0.054932 | 0.35248 | 121.6324 | -0.17853 | 121.5729 | -0.009155 | -0.068665 | -0.018311 | 0.21973 | -121.6736 | -121.7743 | 0.2655 | 0.24719 | 0.18768 | 0.027466 | -0.032044 | 0.013733 | -0.13275 | -0.19226 | 0.18311 | 0.17395 | 0.1236 | 0.16022 | 0.10986 | 0.045776 | -0.036621 | 0.16937 | 121.7514 | 0.064087 | 121.8109 | 0.28381 | 121.8246 | -121.7377 | -121.9437 | 0.18311 | 121.7651 | 0.1236 | 0.54474
1943.7344 | 122.0306 | -0.17853 | 121.7743 | -0.12032 | -0.045594 | 0.003873 | 0.028064 | -0.0010595 | -0.0056162 | -0.0021597 | -0.049713 | 0.0057379 | 0.064918 | 0.048977 | -0.015379 | 0.026981 | -0.0053661 | -0.10071 | 0.054932 | 0 | -0.045776 | 0.050354 | -0.068665 | 0.018311 | 0.21973 | 121.5958 | -0.16937 | 121.6278 | 0.013733 | -0.032043 | 0.027466 | 0.17853 | -121.7194 | -121.8201 | 0.22888 | 0.19684 | 0.10986 | 0.018311 | -0.068665 | 0.009155 | -0.17853 | -0.14648 | 0.19226 | 0.20599 | 0.14648 | 0.19684 | 0.13733 | 0.050354 | -0.045776 | 0.18311 | 121.7972 | 0.054932 | 121.7651 | 0.23346 | 121.7743 | -121.7743 | -121.9437 | 0.13275 | 121.8063 | 0.07782 | 0.39826
1945.4844 | 122.0581 | -0.16937 | 121.7697 | -0.1432 | -0.044953 | 0.0053684 | 0.025927 | -0.0029821 | -0.0092478 | -0.0032277 | 0.023529 | 0.0072333 | 0.065345 | 0.047696 | -0.014951 | 0.025272 | -0.0070751 | -0.041199 | 0.054932 | 0.022888 | 0.018311 | 0.13275 | 0.018311 | 0.086975 | 0.32959 | 121.5912 | -0.15564 | 121.6141 | 0.041199 | 0 | 0.022888 | 0.19226 | -121.7148 | -121.7514 | 0.30212 | 0.25635 | 0.18768 | 0.064087 | -0.004577 | 0.013733 | -0.17853 | -0.15564 | 0.21057 | 0.19226 | 0.16937 | 0.17853 | 0.15564 | 0.10986 | -0.004577 | 0.19684 | 121.7697 | 0.032044 | 121.7468 | 0.22431 | 121.7606 | -121.7468 | -121.9254 | 0.18768 | 121.7834 | 0.12817 | 0.49896
1947.2344 | 122.049 | -0.16479 | 121.7331 | -0.16609 | -0.044525 | 0.0045138 | 0.024005 | -0.0057593 | -0.0081796 | -0.0030141 | -0.01004 | 0.0070197 | 0.064704 | 0.047482 | -0.01602 | 0.028262 | -0.0057935 | -0.059509 | 0.009155 | 0.032043 | 0.054932 | 0.15564 | 0.013733 | 0.091553 | 0.32501 | 121.5866 | -0.14648 | 121.6278 | 0.036621 | 0.009155 | 0.018311 | 0.19684 | -121.7239 | -121.6782 | 0.32044 | 0.25635 | 0.17853 | 0.05951 | -0.01831 | 0.018311 | -0.14648 | -0.10528 | 0.20142 | 0.18311 | 0.17395 | 0.16479 | 0.15564 | 0.1236 | 0.022889 | 0.18311 | 121.7743 | -0.022888 | 121.7331 | 0.17395 | 121.7514 | -121.701 | -121.8796 | 0.21973 | 121.7926 | 0.10529 | 0.48981
1948.9844 | 121.9894 | -0.17395 | 121.7743 | -0.082169 | -0.045166 | 0.0023776 | 0.025287 | 8.47e-06 | -0.0094614 | -0.0036551 | -0.080231 | 0.0050971 | 0.065772 | 0.04855 | -0.016233 | 0.025485 | -0.0045117 | -0.050354 | 0.068665 | 0.004578 | 0.004578 | 0.086975 | -0.004578 | 0.050354 | 0.36163 | 121.6324 | -0.1831 | 121.6049 | -0.004578 | -0.050354 | -0.013733 | 0.17853 | -121.7056 | -121.7697 | 0.26092 | 0.2243 | 0.16937 | 0.045776 | -0.009156 | -0.009155 | -0.14191 | -0.16937 | 0.16937 | 0.16022 | 0.1236 | 0.16937 | 0.13275 | 0.082397 | 0 | 0.17853 | 121.788 | 0.064087 | 121.8155 | 0.24261 | 121.8063 | -121.7697 | -121.9574 | 0.17853 | 121.7789 | 0.1236 | 0.53558
1950.6875 | 122.0398 | -0.17395 | 121.7834 | -0.1432 | -0.045594 | 0.0040866 | 0.027209 | -0.00084593 | -0.0083932 | -0.0045095 | -0.083283 | 0.0055243 | 0.064491 | 0.054532 | -0.016874 | 0.027194 | -0.0015209 | -0.09613 | 0.064087 | -0.018311 | -0.054932 | 0.036621 | -0.073242 | -0.009155 | 0.19226 | 121.6049 | -0.18768 | 121.6095 | -0.032043 | -0.073242 | -0.013733 | 0.15564 | -121.7194 | -121.8384 | 0.21057 | 0.16479 | 0.10071 | 0.009156 | -0.054931 | -0.013733 | -0.17853 | -0.17395 | 0.14191 | 0.16022 | 0.10071 | 0.17395 | 0.11444 | 0.054932 | -0.036621 | 0.15564 | 121.7972 | 0.082398 | 121.7926 | 0.23804 | 121.7789 | -121.8018 | -121.9711 | 0.11902 | 121.7834 | 0.07782 | 0.36621
1952.4375 | 122.0169 | -0.16937 | 121.7834 | -0.089798 | -0.046448 | -0.00018577 | 0.022723 | -0.0046911 | -0.011384 | -0.0034415 | 0.011322 | 0.0042425 | 0.064918 | 0.045132 | -0.013883 | 0.026126 | -0.0092115 | -0.013733 | 0.054932 | 0.050354 | 0.086975 | 0.16479 | 0.064087 | 0.1236 | 0.43488 | 121.6049 | -0.16479 | 121.6049 | 0.009155 | -0.027466 | -0.009155 | 0.21973 | -121.7285 | -121.6965 | 0.33417 | 0.29297 | 0.23346 | 0.073242 | 0.013733 | 0.004578 | -0.17853 | -0.17853 | 0.17853 | 0.16022 | 0.14191 | 0.15564 | 0.13733 | 0.11444 | 0.036621 | 0.17395 | 121.7697 | 0.004578 | 121.7697 | 0.22431 | 121.7743 | -121.7331 | -121.9482 | 0.25635 | 121.7743 | 0.15564 | 0.60425
1954.1875 | 122.0123 | -0.16022 | 121.8063 | -0.10506 | -0.044312 | 0.0019504 | 0.02785 | -0.0010595 | -0.0090342 | -0.0049367 | -0.068024 | 0.0065923 | 0.066413 | 0.056454 | -0.015379 | 0.02634 | -0.0038709 | -0.045776 | 0.073242 | 0.009155 | 0.018311 | 0.10071 | -0.004578 | 0.054932 | 0.37537 | 121.6461 | -0.16479 | 121.6187 | -0.009155 | -0.045776 | -0.009155 | 0.16937 | -121.7331 | -121.788 | 0.26093 | 0.21515 | 0.15564 | 0.045777 | -0.013733 | -0.004578 | -0.16022 | -0.18768 | 0.15106 | 0.15106 | 0.11444 | 0.15564 | 0.11902 | 0.091553 | 0.009156 | 0.15564 | 121.7834 | 0.064087 | 121.8109 | 0.23346 | 121.8063 | -121.7972 | -121.9711 | 0.17853 | 121.7789 | 0.11444 | 0.53558
1955.8906 | 122.0947 | -0.15106 | 121.7743 | -0.12032 | -0.043885 | 0.0028048 | 0.026996 | 0.0015039 | -0.006257 | -0.0042959 | -0.064972 | 0.0048833 | 0.063636 | 0.055386 | -0.014951 | 0.026981 | -0.0036573 | -0.09613 | 0.032043 | 0 | -0.018311 | 0.082397 | -0.045776 | 0.054932 | 0.27466 | 121.6324 | -0.15564 | 121.669 | 0.045776 | -0.004578 | 0.059509 | 0.15106 | -121.7422 | -121.7926 | 0.23346 | 0.20599 | 0.10529 | 0.054932 | -0.045776 | -0.004578 | -0.14191 | -0.10529 | 0.19684 | 0.21057 | 0.14648 | 0.21515 | 0.15106 | 0.082397 | -0.018311 | 0.20142 | 121.8246 | 0.032043 | 121.788 | 0.18311 | 121.7834 | -121.7743 | -121.9299 | 0.13275 | 121.8201 | 0.054932 | 0.42572
1957.6406 | 122.0673 | -0.13733 | 121.7651 | -0.16609 | -0.045166 | 0.0045138 | 0.024859 | -0.0044775 | -0.0073252 | -0.0034415 | -0.0039367 | 0.0053107 | 0.064063 | 0.047268 | -0.014524 | 0.026767 | -0.0010937 | -0.045776 | 0.004578 | 0.018311 | 0.068665 | 0.16022 | 0.027466 | 0.10071 | 0.33417 | 121.6278 | -0.14648 | 121.6736 | 0.059509 | 0.018311 | 0.059509 | 0.15564 | -121.7606 | -121.6965 | 0.29755 | 0.23804 | 0.16479 | 0.082397 | 0.009155 | -0.009155 | -0.13733 | -0.091553 | 0.19684 | 0.19684 | 0.15564 | 0.20599 | 0.16479 | 0.14191 | 0.050354 | 0.20599 | 121.8201 | -0.013733 | 121.7743 | 0.14191 | 121.7651 | -121.7468 | -121.9116 | 0.20599 | 121.8109 | 0.091553 | 0.4715
1959.4062 | 121.9666 | -0.18768 | 121.7972 | -0.10506 | -0.044312 | 0.003873 | 0.027423 | -0.0017005 | -0.006257 | -0.0042959 | -0.10464 | 0.0042425 | 0.063636 | 0.044919 | -0.018797 | 0.027621 | -0.0085705 | -0.11902 | 0.041199 | 0 | -0.073242 | -0.013733 | -0.11444 | -0.027466 | 0.17853 | 121.6415 | -0.18768 | 121.5591 | -0.07782 | -0.1236 | -0.059509 | 0.18768 | -121.756 | -121.8704 | 0.17395 | 0.16022 | 0.073242 | -0.027466 | -0.11444 | 0 | -0.15564 | -0.23804 | 0.10986 | 0.12817 | 0.064087 | 0.12817 | 0.064087 | -0.013733 | -0.073242 | 0.10986 | 121.7468 | 0.041199 | 121.8292 | 0.22888 | 121.8292 | -121.7972 | -121.9849 | 0.11444 | 121.7468 | 0.068664 | 0.36621
1961.1875 | 121.9574 | -0.17853 | 121.8201 | -0.12032 | -0.046021 | 0.0045138 | 0.026996 | 0.0032129 | -0.0088206 | -0.0023733 | -0.083283 | 0.0063787 | 0.062782 | 0.049405 | -0.014524 | 0.028049 | -0.0045117 | -0.059509 | 0.064087 | 0 | -0.036621 | 0.059509 | -0.064087 | -0.018311 | 0.27008 | 121.637 | -0.1831 | 121.5729 | -0.064087 | -0.12817 | -0.068665 | 0.17853 | -121.756 | -121.8567 | 0.23804 | 0.16022 | 0.11444 | -0.018311 | -0.064087 | -0.004577 | -0.18311 | -0.24719 | 0.11444 | 0.10986 | 0.050354 | 0.11444 | 0.054931 | 0.059509 | -0.036621 | 0.11902 | 121.756 | 0.064087 | 121.8201 | 0.24261 | 121.8155 | -121.8201 | -122.0032 | 0.14191 | 121.7514 | 0.11902 | 0.44861
1962.875 | 121.9849 | -0.18768 | 121.8063 | -0.11269 | -0.044098 | 0.0025912 | 0.026782 | 0.00043587 | -0.008607 | -0.0017325 | -0.080231 | 0.0061651 | 0.063209 | 0.046841 | -0.014524 | 0.026981 | -0.0019483 | -0.10071 | 0.041199 | -0.036621 | -0.07782 | -0.009155 | -0.11902 | -0.013733 | 0.17853 | 121.6644 | -0.17853 | 121.5866 | -0.07782 | -0.1236 | -0.059509 | 0.15106 | -121.7651 | -121.8842 | 0.17853 | 0.17395 | 0.068664 | 0.022888 | -0.082398 | 0.009155 | -0.14191 | -0.21973 | 0.10986 | 0.12817 | 0.064087 | 0.11902 | 0.054932 | 0.027466 | -0.041199 | 0.10071 | 121.7651 | 0.07782 | 121.843 | 0.22888 | 121.8521 | -121.843 | -121.9849 | 0.10986 | 121.7743 | 0.086975 | 0.36621
1964.625 | 122.0856 | -0.13275 | 121.8018 | -0.18898 | -0.043244 | 0.0045138 | 0.026355 | -0.00084593 | -0.006898 | -0.0047231 | -0.031403 | 0.0053107 | 0.062568 | 0.040646 | -0.014311 | 0.025912 | -0.0028027 | -0.032043 | -0.009155 | 0.036621 | 0.050354 | 0.16479 | 0.027466 | 0.10529 | 0.33875 | 121.6141 | -0.14648 | 121.6965 | 0.059509 | 0.027466 | 0.045776 | 0.16937 | -121.8109 | -121.7514 | 0.29755 | 0.23804 | 0.16022 | 0.068665 | -0.009155 | -0.013733 | -0.18768 | -0.10529 | 0.19226 | 0.17853 | 0.16022 | 0.19226 | 0.17395 | 0.12817 | 0.013733 | 0.20599 | 121.843 | -0.045776 | 121.7606 | 0.1236 | 121.7468 | -121.7651 | -121.9482 | 0.18311 | 121.8292 | 0.10071 | 0.4715
1966.375 | 121.9803 | -0.16937 | 121.8246 | -0.13557 | -0.043671 | 0.0040866 | 0.029559 | 0.0019311 | -0.0066844 | -0.0036551 | -0.09549 | 0.0044561 | 0.064704 | 0.048123 | -0.014524 | 0.027621 | -0.0049389 | -0.11444 | 0.064087 | -0.013733 | -0.091553 | -0.027466 | -0.12817 | -0.027466 | 0.18768 | 121.6965 | -0.17395 | 121.5912 | -0.086975 | -0.1236 | -0.050354 | 0.15564 | -121.7606 | -121.9162 | 0.14191 | 0.14191 | 0.041199 | -0.013733 | -0.11444 | -0.004577 | -0.12817 | -0.23346 | 0.082398 | 0.11902 | 0.045777 | 0.1236 | 0.050354 | -0.013733 | -0.07782 | 0.086975 | 121.7651 | 0.07782 | 121.8704 | 0.23346 | 121.8658 | -121.8384 | -121.9986 | 0.07782 | 121.7606 | 0.054932 | 0.35706
1968.0625 | 121.9666 | -0.15564 | 121.8338 | -0.15083 | -0.042176 | 0.004941 | 0.025927 | 0.0029993 | -0.0081796 | -0.0036551 | -0.09549 | 0.0053107 | 0.065132 | 0.049618 | -0.013883 | 0.027194 | -0.00066651 | -0.10529 | 0.050354 | -0.013733 | -0.07782 | -0.009155 | -0.10986 | -0.022888 | 0.17853 | 121.6644 | -0.18768 | 121.5591 | -0.082397 | -0.13275 | -0.059509 | 0.14191 | -121.7834 | -121.9116 | 0.14649 | 0.13275 | 0.045777 | -0.009155 | -0.09613 | -0.032043 | -0.16937 | -0.27466 | 0.073243 | 0.096131 | 0.022889 | 0.12817 | 0.054932 | 0.004578 | -0.064087 | 0.10529 | 121.7468 | 0.064087 | 121.8521 | 0.20599 | 121.8201 | -121.8475 | -122.0215 | 0.07782 | 121.7148 | 0.050354 | 0.33417
1969.8125 | 122.113 | -0.15106 | 121.7972 | -0.11269 | -0.046662 | 0.0025912 | 0.024432 | 0.00064947 | -0.012025 | -0.0013051 | 0.032684 | 0.0046697 | 0.064491 | 0.052823 | -0.015165 | 0.027835 | -0.0055799 | -0.009155 | 0.032043 | 0.07782 | 0.09613 | 0.21973 | 0.10529 | 0.15106 | 0.46234 | 121.6278 | -0.15564 | 121.6873 | 0.091553 | 0.045776 | 0.073242 | 0.22888 | -121.7651 | -121.701 | 0.37079 | 0.30212 | 0.25635 | 0.073242 | 0.027466 | -0.004578 | -0.16937 | -0.10986 | 0.24261 | 0.2243 | 0.19684 | 0.22888 | 0.20142 | 0.14191 | 0.01831 | 0.24719 | 121.843 | -0.045777 | 121.7834 | 0.18311 | 121.7789 | -121.7194 | -121.9528 | 0.24719 | 121.8384 | 0.14191 | 0.6134
1971.5625 | 122.0993 | -0.14191 | 121.8063 | -0.12794 | -0.042603 | 0.0057956 | 0.025287 | 0.0021447 | -0.0077524 | -0.0023733 | -0.06192 | 0.0042425 | 0.062782 | 0.045132 | -0.015592 | 0.029117 | -0.0070751 | -0.022888 | 0.013733 | 0.018311 | 0.045776 | 0.15106 | 0.009155 | 0.07782 | 0.31586 | 121.6187 | -0.12817 | 121.7377 | 0.07782 | 0.032043 | 0.07782 | 0.16022 | -121.7926 | -121.7606 | 0.29297 | 0.21973 | 0.15106 | 0.059509 | -0.009156 | 0.013733 | -0.18768 | -0.068664 | 0.21973 | 0.21973 | 0.17395 | 0.20599 | 0.16022 | 0.13275 | 0.027465 | 0.20599 | 121.8658 | -0.004578 | 121.7468 | 0.15564 | 121.7606 | -121.788 | -121.9345 | 0.18768 | 121.8796 | 0.11902 | 0.45776
1973.3125 | 122.0993 | -0.14648 | 121.8109 | -0.12794 | -0.046875 | 0.0043002 | 0.023578 | 0.0023585 | -0.009675 | -0.00087794 | -0.01004 | 0.0057379 | 0.063636 | 0.049832 | -0.016447 | 0.025272 | -0.0068615 | -0.013733 | 0.041199 | 0.045776 | 0.091553 | 0.21057 | 0.09613 | 0.15564 | 0.48065 | 121.6278 | -0.13275 | 121.6873 | 0.086975 | 0.041199 | 0.059509 | 0.19226 | -121.7697 | -121.7194 | 0.35706 | 0.30212 | 0.24261 | 0.10986 | 0.050354 | 0.013733 | -0.1831 | -0.1236 | 0.23346 | 0.20599 | 0.18768 | 0.19226 | 0.17395 | 0.1648 | 0.045777 | 0.21973 | 121.8201 | -0.004577 | 121.7606 | 0.18768 | 121.7743 | -121.7651 | -121.9437 | 0.23804 | 121.8338 | 0.13275 | 0.62714
1975.0156 | 122.0352 | -0.1831 | 121.8109 | -0.12794 | -0.044739 | 0.0040866 | 0.028064 | -0.0040503 | -0.0090342 | -0.0034415 | -0.055817 | 0.0044561 | 0.064918 | 0.059872 | -0.016233 | 0.027621 | -0.0034435 | -0.045776 | 0.082397 | 0.022888 | -0.004578 | 0.068665 | -0.022888 | 0.059509 | 0.37079 | 121.6782 | -0.15564 | 121.6461 | 0 | -0.050354 | -0.013733 | 0.20599 | -121.7285 | -121.8155 | 0.25177 | 0.24261 | 0.16022 | 0.036621 | -0.045776 | 0.027465 | -0.13275 | -0.16479 | 0.1831 | 0.16937 | 0.13275 | 0.14191 | 0.10529 | 0.045777 | -0.027466 | 0.15564 | 121.8018 | 0.059509 | 121.8338 | 0.2655 | 121.8613 | -121.788 | -121.9666 | 0.17853 | 121.8292 | 0.13733 | 0.55389
1976.7656 | 121.9711 | -0.19226 | 121.8246 | -0.11269 | -0.044098 | 0.0043002 | 0.028277 | -0.0025549 | -0.0064706 | -0.0017325 | -0.1077 | 0.0072333 | 0.063209 | 0.055386 | -0.015592 | 0.027194 | -0.00023931 | -0.10986 | 0.050354 | -0.004578 | -0.054932 | -0.013733 | -0.12817 | -0.027466 | 0.17853 | 121.7102 | -0.16479 | 121.582 | -0.10071 | -0.14648 | -0.073242 | 0.18768 | -121.7743 | -121.8796 | 0.17853 | 0.16479 | 0.064087 | -0.022888 | -0.1236 | 0.027466 | -0.11444 | -0.24262 | 0.091553 | 0.11902 | 0.045777 | 0.091553 | 0.018311 | -0.009155 | -0.050354 | 0.064087 | 121.7468 | 0.054932 | 121.875 | 0.24261 | 121.9025 | -121.8292 | -121.9894 | 0.13733 | 121.7743 | 0.082398 | 0.37079
1978.5312 | 122.1222 | -0.14648 | 121.7834 | -0.18135 | -0.044525 | 0.0045138 | 0.025287 | -0.0040503 | -0.006898 | -0.0047231 | -0.013092 | 0.0057379 | 0.062995 | 0.050686 | -0.014524 | 0.026981 | -0.0042981 | -0.036621 | 0.009155 | 0.022888 | 0.068665 | 0.16937 | 0.022888 | 0.10071 | 0.32501 | 121.6461 | -0.13733 | 121.7148 | 0.064087 | 0.022888 | 0.064087 | 0.16937 | -121.7743 | -121.7148 | 0.31586 | 0.24719 | 0.16937 | 0.07782 | 0 | 0.009155 | -0.13733 | -0.068664 | 0.21057 | 0.21057 | 0.16937 | 0.20142 | 0.16022 | 0.14649 | 0.045777 | 0.20142 | 121.8521 | -0.013733 | 121.7834 | 0.15564 | 121.7926 | -121.7606 | -121.9208 | 0.21515 | 121.8613 | 0.10986 | 0.4715
1980.2812 | 122.0718 | -0.16937 | 121.8063 | -0.17372 | -0.04538 | 0.0040866 | 0.024859 | 8.47e-06 | -0.006898 | -0.00045074 | -0.01004 | 0.0048833 | 0.065986 | 0.048764 | -0.012815 | 0.027621 | -0.0036573 | -0.050354 | 0.013733 | 0.045776 | 0.036621 | 0.14191 | 0.013733 | 0.09613 | 0.31128 | 121.6187 | -0.14191 | 121.6644 | 0.009155 | -0.004578 | 0.022888 | 0.21515 | -121.7926 | -121.7697 | 0.31128 | 0.2655 | 0.18311 | 0.050354 | -0.032043 | 0.027466 | -0.18768 | -0.14191 | 0.17853 | 0.19226 | 0.16479 | 0.16479 | 0.13733 | 0.096131 | -0.009155 | 0.15106 | 121.8063 | -0.032043 | 121.7606 | 0.18311 | 121.788 | -121.7606 | -121.9482 | 0.20599 | 121.8338 | 0.11902 | 0.48065
1981.9688 | 122.1359 | -0.14191 | 121.8018 | -0.13557 | -0.048157 | 0.003232 | 0.025073 | -0.0029821 | -0.007966 | -0.0019461 | 0.014374 | 0.0021063 | 0.063423 | 0.050259 | -0.015379 | 0.027621 | -0.0047253 | -0.032043 | 0.054932 | 0.036621 | 0.07782 | 0.20599 | 0.091553 | 0.16022 | 0.45319 | 121.6461 | -0.16022 | 121.7285 | 0.09613 | 0.054932 | 0.073242 | 0.17853 | -121.7468 | -121.7239 | 0.3479 | 0.30212 | 0.23346 | 0.1236 | 0.054932 | -0.01831 | -0.15564 | -0.073242 | 0.23804 | 0.21515 | 0.19684 | 0.23346 | 0.21515 | 0.16937 | 0.041199 | 0.25635 | 121.8887 | 0.018311 | 121.8063 | 0.19684 | 121.788 | -121.7651 | -121.962 | 0.21973 | 121.8704 | 0.10986 | 0.59509
1983.7188 | 121.994 | -0.19684 | 121.8567 | -0.10506 | -0.042816 | 0.003873 | 0.029132 | -0.0012731 | -0.0092478 | -0.0038687 | -0.12906 | 0.0063787 | 0.062354 | 0.050473 | -0.017301 | 0.026767 | -0.0055799 | -0.082397 | 0.032043 | -0.004578 | -0.045776 | 0.013733 | -0.10986 | -0.032043 | 0.21057 | 121.701 | -0.17853 | 121.6003 | -0.091553 | -0.13275 | -0.050354 | 0.19226 | -121.8246 | -121.9025 | 0.21057 | 0.1648 | 0.086975 | -0.027465 | -0.10529 | 0.01831 | -0.15564 | -0.25635 | 0.10529 | 0.14648 | 0.064087 | 0.12817 | 0.045777 | 0.018311 | -0.041198 | 0.086975 | 121.7789 | 0.036621 | 121.8796 | 0.22888 | 121.8979 | -121.8613 | -122.0352 | 0.15106 | 121.7972 | 0.11444 | 0.40741
1985.4688 | 122.1497 | -0.13733 | 121.8063 | -0.12032 | -0.04538 | 0.0062228 | 0.023791 | -0.0027685 | -0.0077524 | -0.0017325 | -0.046661 | 0.0061651 | 0.064277 | 0.045559 | -0.017088 | 0.028903 | -0.0066479 | -0.036621 | 0.009155 | 0.032043 | 0.059509 | 0.16022 | 0.022888 | 0.086975 | 0.3479 | 121.6507 | -0.14648 | 121.7377 | 0.086975 | 0.018311 | 0.059509 | 0.16937 | -121.7972 | -121.7468 | 0.29755 | 0.2243 | 0.16022 | 0.054932 | -0.009155 | -0.009155 | -0.15564 | -0.068664 | 0.2243 | 0.19684 | 0.15564 | 0.20599 | 0.16479 | 0.12817 | 0.027466 | 0.23346 | 121.8842 | -0.022888 | 121.7972 | 0.14648 | 121.788 | -121.7743 | -121.9528 | 0.19684 | 121.875 | 0.10071 | 0.48523
1987.2188 | 121.9849 | -0.17853 | 121.875 | -0.12794 | -0.044953 | 0.0034456 | 0.027423 | 0.0019311 | -0.0073252 | -0.0030141 | -0.1077 | 0.0057379 | 0.063209 | 0.055386 | -0.015379 | 0.026767 | -0.0070751 | -0.10071 | 0.045776 | -0.018311 | -0.064087 | -0.013733 | -0.11902 | -0.022888 | 0.1831 | 121.701 | -0.17853 | 121.6049 | -0.09613 | -0.15106 | -0.073242 | 0.16022 | -121.8292 | -121.9391 | 0.16479 | 0.15564 | 0.059509 | -0.004577 | -0.10071 | 0 | -0.17395 | -0.27008 | 0.082398 | 0.10529 | 0.027466 | 0.10529 | 0.027466 | 0.004578 | -0.045776 | 0.082398 | 121.7834 | 0.064087 | 121.8796 | 0.2243 | 121.8796 | -121.8933 | -122.0535 | 0.11444 | 121.7834 | 0.07782 | 0.36163
1988.9062 | 122.0169 | -0.16022 | 121.843 | -0.12032 | -0.046021 | 0.0034456 | 0.026355 | 0.00022207 | -0.0092478 | -0.0028005 | -0.089386 | 0.0065923 | 0.063423 | 0.052823 | -0.016447 | 0.027621 | -0.0053661 | -0.064087 | 0.036621 | 0.009155 | 0 | 0.086975 | -0.032043 | 0.041199 | 0.34332 | 121.7148 | -0.17395 | 121.6599 | -0.027466 | -0.064087 | -0.022888 | 0.16937 | -121.8063 | -121.843 | 0.24719 | 0.20142 | 0.12817 | 0.032044 | -0.041198 | -0.013733 | -0.12817 | -0.18311 | 0.13275 | 0.13733 | 0.09613 | 0.15106 | 0.10986 | 0.07782 | -0.009155 | 0.14648 | 121.8338 | 0.027466 | 121.8887 | 0.19684 | 121.875 | -121.8338 | -122.0169 | 0.16022 | 121.8201 | 0.09613 | 0.50354
1990.6562 | 122.0398 | -0.16022 | 121.8475 | -0.12032 | -0.043457 | 0.0045138 | 0.028491 | -0.00041873 | -0.0071116 | -0.0013051 | -0.080231 | 0.0063787 | 0.062995 | 0.047482 | -0.013242 | 0.024204 | -0.0025891 | -0.10071 | 0.041199 | -0.022888 | -0.073242 | 0.022888 | -0.10071 | -0.018311 | 0.19684 | 121.6782 | -0.17853 | 121.6553 | -0.027466 | -0.091553 | -0.013733 | 0.13733 | -121.8063 | -121.9208 | 0.1831 | 0.14191 | 0.059509 | 0.004577 | -0.07782 | -0.018311 | -0.16937 | -0.19226 | 0.13275 | 0.14648 | 0.068664 | 0.16479 | 0.086975 | 0.045776 | -0.050354 | 0.15106 | 121.8338 | 0.064087 | 121.8567 | 0.20142 | 121.8384 | -121.8704 | -122.0261 | 0.086975 | 121.8155 | 0.059509 | 0.35706
1992.3906 | 122.1085 | -0.13733 | 121.8292 | -0.10506 | -0.044525 | 0.0053684 | 0.023578 | 0.0019311 | -0.0060434 | -0.0036551 | -0.034454 | 0.0042425 | 0.064918 | 0.044278 | -0.014951 | 0.026553 | -0.0040845 | -0.041199 | -0.009155 | 0.027466 | 0.064087 | 0.15564 | 0.018311 | 0.086975 | 0.3479 | 121.6599 | -0.13733 | 121.7194 | 0.073242 | 0.027466 | 0.064087 | 0.16479 | -121.8384 | -121.7651 | 0.29297 | 0.2243 | 0.15564 | 0.059509 | -0.009155 | 0 | -0.16937 | -0.10986 | 0.21057 | 0.20142 | 0.16479 | 0.20142 | 0.16479 | 0.12817 | 0.036621 | 0.21057 | 121.8567 | -0.036621 | 121.7972 | 0.12817 | 121.7972 | -121.8018 | -121.9666 | 0.20142 | 121.8567 | 0.09613 | 0.48523
1994.0781 | 122.0169 | -0.17853 | 121.8796 | -0.097427 | -0.041748 | 0.0034456 | 0.028491 | 0.0021447 | -0.0073252 | -0.0036551 | -0.098541 | 0.0063787 | 0.064491 | 0.054318 | -0.014311 | 0.026126 | -0.0060071 | -0.09613 | 0.045776 | -0.032043 | -0.091553 | -0.032043 | -0.1236 | -0.027466 | 0.1831 | 121.7239 | -0.17395 | 121.637 | -0.07782 | -0.13275 | -0.032043 | 0.14648 | -121.8338 | -121.9711 | 0.14648 | 0.15106 | 0.054932 | 0.004577 | -0.091553 | 0.004578 | -0.15564 | -0.24262 | 0.10071 | 0.14648 | 0.045777 | 0.14191 | 0.041199 | 0 | -0.05951 | 0.09613 | 121.8109 | 0.077819 | 121.8979 | 0.2243 | 121.9025 | -121.9116 | -122.0535 | 0.086975 | 121.8155 | 0.082398 | 0.36163
1995.7812 | 122.1542 | -0.11902 | 121.8384 | -0.12032 | -0.05008 | 0.0028048 | 0.024432 | -0.0014867 | -0.0094614 | -0.0038687 | 0.014374 | 0.0057379 | 0.064277 | 0.046841 | -0.014524 | 0.026553 | -0.0049389 | -0.027466 | 0.018311 | 0.041199 | 0.091553 | 0.1831 | 0.064087 | 0.15564 | 0.46692 | 121.6919 | -0.13275 | 121.7697 | 0.12817 | 0.09613 | 0.091553 | 0.16022 | -121.8201 | -121.7468 | 0.30212 | 0.27466 | 0.18311 | 0.11444 | 0.022888 | -0.013732 | -0.14648 | -0.068665 | 0.24719 | 0.21057 | 0.21515 | 0.2243 | 0.22888 | 0.14191 | 0.050354 | 0.26093 | 121.9025 | -0.022888 | 121.8246 | 0.13733 | 121.8109 | -121.7972 | -121.9711 | 0.21057 | 121.8887 | 0.091553 | 0.58594
1997.5156 | 122.0215 | -0.17853 | 121.8887 | -0.06691 | -0.047943 | 0.0047274 | 0.026782 | -0.0031957 | -0.007966 | -0.0038687 | -0.031403 | 0.0036017 | 0.0662 | 0.048123 | -0.015379 | 0.026981 | -0.0042981 | -0.050354 | 0.041199 | 0.032043 | 0.004578 | 0.07782 | -0.013733 | 0.059509 | 0.39825 | 121.7194 | -0.16022 | 121.637 | -0.004578 | -0.064087 | -0.036621 | 0.21057 | -121.8475 | -121.8842 | 0.25635 | 0.23804 | 0.16479 | 0.027466 | -0.045776 | 0.018311 | -0.16937 | -0.25177 | 0.17395 | 0.14191 | 0.11444 | 0.1236 | 0.09613 | 0.045777 | -0.027465 | 0.15564 | 121.7972 | 0.009156 | 121.8796 | 0.21973 | 121.8979 | -121.8567 | -122.049 | 0.18311 | 121.8155 | 0.12817 | 0.57678
1999.2656 | 122.1405 | -0.1236 | 121.8475 | -0.16609 | -0.044525 | 0.0040866 | 0.02785 | -0.00063233 | -0.0073252 | -0.0023733 | -0.10159 | 0.0040289 | 0.062354 | 0.047055 | -0.015806 | 0.02634 | -0.0038709 | -0.086975 | 0.022888 | -0.004578 | -0.013733 | 0.054932 | -0.064087 | 0.018311 | 0.27466 | 121.6873 | -0.13275 | 121.7468 | 0.054932 | 0.013733 | 0.073242 | 0.11902 | -121.8246 | -121.8613 | 0.17853 | 0.14191 | 0.059509 | 0.022889 | -0.059509 | -0.009155 | -0.16022 | -0.10071 | 0.17853 | 0.19684 | 0.13733 | 0.20599 | 0.14648 | 0.05951 | -0.009155 | 0.18768 | 121.8796 | 0.027466 | 121.8201 | 0.14648 | 121.8109 | -121.8521 | -121.9803 | 0.10986 | 121.8704 | 0.036621 | 0.39825
2000.9688 | 122.1451 | -0.13733 | 121.8384 | -0.20424 | -0.04303 | 0.0064364 | 0.025927 | -0.0019141 | -0.0092478 | -0.0036551 | -0.089386 | 0.0042425 | 0.0615 | 0.051114 | -0.016447 | 0.026553 | -0.0068615 | -0.091553 | 0.022888 | -0.013733 | -0.013733 | 0.068665 | -0.036621 | 0.045776 | 0.28839 | 121.6965 | -0.13733 | 121.7606 | 0.073242 | 0.022888 | 0.091553 | 0.1236 | -121.8155 | -121.8521 | 0.20599 | 0.18311 | 0.10071 | 0.059509 | -0.022888 | 0 | -0.14191 | -0.07782 | 0.21057 | 0.22888 | 0.16022 | 0.22888 | 0.16022 | 0.082398 | 0 | 0.21057 | 121.8979 | 0.036621 | 121.8338 | 0.16022 | 121.8338 | -121.8521 | -121.9757 | 0.1236 | 121.8979 | 0.045776 | 0.42572
2002.7188 | 122.1588 | -0.13275 | 121.8338 | -0.089798 | -0.047516 | 0.0025912 | 0.021441 | -0.0031957 | -0.006257 | -0.0034415 | 0.0082703 | 0.0046697 | 0.063636 | 0.053036 | -0.014951 | 0.023349 | -0.0042981 | -0.064087 | 0.018311 | 0.027466 | 0.036621 | 0.15106 | 0.050354 | 0.13275 | 0.42114 | 121.6965 | -0.1236 | 121.7514 | 0.10986 | 0.07782 | 0.091553 | 0.16022 | -121.8155 | -121.7972 | 0.28381 | 0.2655 | 0.18311 | 0.10529 | 0.022888 | 0.009155 | -0.13733 | -0.082397 | 0.24261 | 0.2243 | 0.21057 | 0.21515 | 0.20142 | 0.1236 | 0.009155 | 0.23346 | 121.875 | -0.009155 | 121.8201 | 0.15106 | 121.8292 | -121.8063 | -121.9574 | 0.16937 | 121.8842 | 0.068664 | 0.55389
2004.4844 | 122.1497 | -0.11902 | 121.8292 | -0.18135 | -0.04538 | 0.0045138 | 0.028705 | 0.0029993 | -0.0058298 | -0.00087794 | -0.077179 | 0.0055243 | 0.064491 | 0.047909 | -0.017729 | 0.028049 | -0.0072889 | -0.022888 | -0.013733 | 0.013733 | 0.045776 | 0.14191 | 0.009155 | 0.054932 | 0.33417 | 121.6919 | -0.10071 | 121.7834 | 0.09613 | 0.050354 | 0.10986 | 0.13275 | -121.843 | -121.7834 | 0.26093 | 0.17395 | 0.12817 | 0.041199 | -0.004578 | 0.018311 | -0.13733 | -0.045777 | 0.21515 | 0.22888 | 0.16937 | 0.21057 | 0.15106 | 0.12817 | 0.032043 | 0.19684 | 121.8842 | -0.027466 | 121.7926 | 0.10529 | 121.8109 | -121.8155 | -121.9299 | 0.16479 | 121.9025 | 0.096131 | 0.45319
2006.25 | 122.1634 | -0.09613 | 121.8475 | -0.13557 | -0.04538 | 0.0023776 | 0.021441 | -0.0076819 | -0.0094614 | -0.0025869 | -0.016144 | 0.0050971 | 0.065132 | 0.047696 | -0.016874 | 0.025699 | -0.0049389 | -0.018311 | 0.009155 | 0.032043 | 0.10071 | 0.19684 | 0.068665 | 0.1236 | 0.48065 | 121.7056 | -0.13733 | 121.7743 | 0.13733 | 0.09613 | 0.091553 | 0.12817 | -121.8384 | -121.7468 | 0.29297 | 0.21973 | 0.16479 | 0.091553 | 0.036622 | -0.041199 | -0.14191 | -0.073242 | 0.23346 | 0.18768 | 0.19226 | 0.22888 | 0.23346 | 0.1648 | 0.068665 | 0.27466 | 121.9116 | -0.022888 | 121.843 | 0.10528 | 121.8018 | -121.8155 | -121.9849 | 0.19684 | 121.8704 | 0.077819 | 0.57678
2007.9531 | 122.0215 | -0.15564 | 121.8887 | -0.097427 | -0.043885 | 0.003873 | 0.029345 | 0.0029993 | -0.0092478 | -0.0021597 | -0.10464 | 0.0063787 | 0.064277 | 0.053036 | -0.01602 | 0.02933 | -0.0047253 | -0.059509 | 0.045776 | 0.013733 | -0.018311 | 0.054932 | -0.059509 | 0 | 0.30212 | 121.7834 | -0.15564 | 121.6736 | -0.013733 | -0.086975 | -0.022888 | 0.16937 | -121.843 | -121.907 | 0.21057 | 0.15564 | 0.096131 | -0.013733 | -0.073242 | 0 | -0.10529 | -0.21515 | 0.14191 | 0.13275 | 0.068665 | 0.13275 | 0.068665 | 0.041199 | -0.032044 | 0.14191 | 121.8292 | 0.032043 | 121.9391 | 0.20142 | 121.9391 | -121.875 | -122.0444 | 0.13733 | 121.8292 | 0.096131 | 0.45776
2009.6875 | 122.1497 | -0.12817 | 121.8384 | -0.10506 | -0.044953 | 0.0023776 | 0.023364 | -0.0019141 | -0.0075388 | -0.0042959 | -0.013092 | 0.0065923 | 0.06385 | 0.054532 | -0.014524 | 0.026553 | -0.0025891 | -0.036621 | 0.009155 | 0.018311 | 0.059509 | 0.17853 | 0.059509 | 0.14648 | 0.46692 | 121.6873 | -0.13275 | 121.7834 | 0.13733 | 0.10071 | 0.10529 | 0.14649 | -121.8292 | -121.7789 | 0.3067 | 0.27466 | 0.18768 | 0.12817 | 0.041198 | -0.004577 | -0.15106 | -0.054932 | 0.2655 | 0.23346 | 0.22888 | 0.23804 | 0.23346 | 0.16022 | 0.041198 | 0.27008 | 121.9162 | -0.009156 | 121.8201 | 0.13733 | 121.8155 | -121.8201 | -121.9711 | 0.18768 | 121.9116 | 0.091553 | 0.59509
2011.4531 | 122.1405 | -0.10529 | 121.8658 | -0.15083 | -0.048157 | 0.0051546 | 0.023791 | -0.0049047 | -0.0090342 | -0.0023733 | -0.0008851 | 0.0048833 | 0.065559 | 0.048764 | -0.017515 | 0.025272 | -0.0047253 | -0.064087 | 0 | 0.018311 | 0.045776 | 0.13733 | 0.027466 | 0.10071 | 0.40741 | 121.7148 | -0.11444 | 121.7834 | 0.11902 | 0.091553 | 0.09613 | 0.1236 | -121.8658 | -121.8201 | 0.24262 | 0.20599 | 0.13275 | 0.082397 | 0.009155 | -0.009155 | -0.15106 | -0.082398 | 0.22431 | 0.20142 | 0.19684 | 0.21057 | 0.20599 | 0.11902 | 0.027465 | 0.23346 | 121.8979 | -0.018311 | 121.8292 | 0.10529 | 121.8201 | -121.8475 | -121.9803 | 0.15106 | 121.8887 | 0.041199 | 0.5127
2013.1406 | 122.0535 | -0.13733 | 121.8842 | -0.12032 | -0.042816 | 0.004941 | 0.024005 | -0.0014867 | -0.008607 | -0.0040823 | -0.04361 | 0.0063787 | 0.065559 | 0.048123 | -0.015379 | 0.026767 | -0.0060071 | -0.036621 | 0.022888 | 0.004578 | 0.027466 | 0.11444 | 0.022888 | 0.09613 | 0.42114 | 121.756 | -0.13275 | 121.6873 | 0.009155 | -0.036621 | -0.004578 | 0.14191 | -121.8613 | -121.8567 | 0.25177 | 0.23346 | 0.16022 | 0.091552 | 0.01831 | 0.004578 | -0.12817 | -0.19684 | 0.14648 | 0.13275 | 0.10071 | 0.12817 | 0.09613 | 0.10986 | 0.022888 | 0.14191 | 121.8201 | 0.01831 | 121.8887 | 0.16022 | 121.8933 | -121.8796 | -122.0169 | 0.16479 | 121.8246 | 0.10071 | 0.55847
2014.8906 | 122.049 | -0.14648 | 121.9208 | -0.11269 | -0.046234 | 0.003873 | 0.024432 | -0.0027685 | -0.01117 | -0.0015189 | -0.074127 | 0.0053107 | 0.064277 | 0.045132 | -0.016447 | 0.028049 | -0.0064343 | -0.045776 | 0.022888 | -0.009155 | -0.013733 | 0.07782 | -0.027466 | 0.032043 | 0.37537 | 121.7697 | -0.14648 | 121.669 | -0.009155 | -0.045776 | -0.032043 | 0.13733 | -121.8979 | -121.9345 | 0.2243 | 0.17853 | 0.11902 | 0.041198 | -0.018311 | 0 | -0.15106 | -0.25177 | 0.13733 | 0.11444 | 0.10071 | 0.11444 | 0.10071 | 0.086975 | -0.004578 | 0.13733 | 121.8155 | 0.032043 | 121.9162 | 0.16937 | 121.9162 | -121.9299 | -122.0673 | 0.13275 | 121.8155 | 0.10071 | 0.52185
2016.6406 | 122.1222 | -0.11902 | 121.8704 | -0.11269 | -0.043885 | 0.0034456 | 0.024859 | -0.0038367 | -0.0083932 | -0.0032277 | -0.0069885 | 0.0046697 | 0.064491 | 0.045132 | -0.014524 | 0.025912 | -0.0087841 | -0.073242 | -0.009155 | 0.013733 | 0.013733 | 0.10071 | -0.009155 | 0.068665 | 0.31128 | 121.7422 | -0.13275 | 121.7285 | 0.054932 | 0.004578 | 0.045776 | 0.13275 | -121.8796 | -121.8567 | 0.21973 | 0.18768 | 0.10986 | 0.054932 | -0.022888 | -0.013732 | -0.12817 | -0.14191 | 0.17395 | 0.16479 | 0.1236 | 0.17853 | 0.13733 | 0.086975 | 0 | 0.18768 | 121.8613 | -0.022888 | 121.875 | 0.10986 | 121.8613 | -121.8567 | -122.0032 | 0.13275 | 121.8475 | 0.045777 | 0.4303
2018.3906 | 122.0947 | -0.14648 | 121.8933 | -0.10506 | -0.04538 | 0.002164 | 0.028705 | -0.00063233 | -0.0056162 | -0.0034415 | -0.11075 | 0.0050971 | 0.064277 | 0.051327 | -0.015379 | 0.028262 | -0.0010937 | -0.045776 | 0.045776 | 0 | -0.004578 | 0.068665 | -0.041199 | 0.022888 | 0.37994 | 121.7743 | -0.15106 | 121.7148 | 0.041199 | -0.013733 | 0.018311 | 0.14648 | -121.8475 | -121.8979 | 0.21515 | 0.16937 | 0.10529 | 0.022888 | -0.041199 | -0.004578 | -0.11902 | -0.17853 | 0.18768 | 0.16479 | 0.13275 | 0.16937 | 0.13733 | 0.068665 | -0.004578 | 0.19226 | 121.8658 | 0.045776 | 121.9254 | 0.19226 | 121.9208 | -121.8933 | -122.0444 | 0.14191 | 121.8613 | 0.10071 | 0.52643
2020.0781 | 122.1405 | -0.13733 | 121.8887 | -0.097427 | -0.045166 | 0.003232 | 0.029559 | -0.00041873 | -0.0083932 | -0.0047231 | -0.1138 | 0.0080877 | 0.064918 | 0.04855 | -0.014738 | 0.027621 | -0.0030163 | -0.09613 | 0.036621 | -0.018311 | -0.045776 | 0.032043 | -0.09613 | -0.009155 | 0.23804 | 121.7606 | -0.13733 | 121.7606 | 0.045776 | 0 | 0.068665 | 0.11902 | -121.8521 | -121.9345 | 0.16937 | 0.12817 | 0.041199 | 0.009156 | -0.077819 | 0 | -0.12817 | -0.12817 | 0.18311 | 0.20599 | 0.13733 | 0.20599 | 0.13733 | 0.050354 | -0.027465 | 0.18311 | 121.8979 | 0.054932 | 121.8979 | 0.17395 | 121.8979 | -121.907 | -122.0261 | 0.091553 | 121.8979 | 0.041199 | 0.37537
2021.8281 | 122.1497 | -0.086975 | 121.8704 | -0.17372 | -0.044739 | 0.003873 | 0.029559 | 0.0012903 | -0.0075388 | -0.0025869 | -0.077179 | 0.0044561 | 0.0662 | 0.050686 | -0.017729 | 0.025912 | -0.0062207 | -0.10071 | 0.013733 | -0.004578 | -0.022888 | 0.059509 | -0.064087 | 0.036621 | 0.27924 | 121.7514 | -0.11902 | 121.7834 | 0.091553 | 0.041199 | 0.10529 | 0.082397 | -121.8567 | -121.8933 | 0.14648 | 0.1236 | 0.022888 | 0.041199 | -0.059509 | -0.032044 | -0.11902 | -0.086975 | 0.17853 | 0.19226 | 0.12817 | 0.22431 | 0.16022 | 0.064087 | -0.01831 | 0.21057 | 121.9025 | 0.018311 | 121.8704 | 0.10071 | 121.8384 | -121.875 | -121.9894 | 0.064087 | 121.8704 | -0.013733 | 0.36621
2023.5781 | 122.0993 | -0.14191 | 121.9391 | -0.10506 | -0.044525 | 0.0025912 | 0.026996 | 8.47e-06 | -0.011384 | -0.0019461 | -0.12906 | 0.0055243 | 0.065559 | 0.053464 | -0.014738 | 0.027835 | -0.0049389 | -0.054932 | 0.036621 | -0.009155 | -0.004578 | 0.086975 | -0.041199 | 0.032043 | 0.36621 | 121.7651 | -0.13733 | 121.756 | 0.059509 | -0.013733 | 0.022888 | 0.13275 | -121.9025 | -121.9437 | 0.22888 | 0.17395 | 0.10071 | 0.041198 | -0.032044 | 0.004578 | -0.17395 | -0.18311 | 0.20142 | 0.16479 | 0.12817 | 0.16022 | 0.1236 | 0.09613 | 0.004577 | 0.19684 | 121.8933 | 0.045776 | 121.9025 | 0.17853 | 121.907 | -121.9482 | -122.0764 | 0.13733 | 121.8979 | 0.086975 | 0.50812
2025.3281 | 122.1313 | -0.10986 | 121.8933 | -0.13557 | -0.049225 | 0.003873 | 0.026996 | -0.0014867 | -0.0098886 | -0.0023733 | -0.01004 | 0.0057379 | 0.062782 | 0.041501 | -0.013883 | 0.026981 | -0.0025891 | -0.036621 | 0.004578 | 0.032043 | 0.064087 | 0.15564 | 0.059509 | 0.11902 | 0.4715 | 121.7514 | -0.12817 | 121.7651 | 0.10529 | 0.07782 | 0.086975 | 0.14191 | -121.8887 | -121.8292 | 0.2655 | 0.22888 | 0.16937 | 0.086976 | 0.027466 | -0.018311 | -0.14191 | -0.12817 | 0.21515 | 0.19684 | 0.18768 | 0.21515 | 0.20599 | 0.1236 | 0.032044 | 0.23346 | 121.8933 | -0.027465 | 121.8796 | 0.11444 | 121.8613 | -121.8613 | -122.0215 | 0.17395 | 121.875 | 0.073242 | 0.58136
2027.0938 | 122.081 | -0.14648 | 121.9345 | -0.11269 | -0.042603 | 0.0023776 | 0.028064 | 0.0019311 | -0.010316 | -0.0021597 | -0.098541 | 0.0065923 | 0.064704 | 0.041928 | -0.014738 | 0.027621 | -0.0040845 | -0.054932 | 0.018311 | -0.018311 | -0.004578 | 0.07782 | -0.032043 | 0.032043 | 0.34332 | 121.7651 | -0.11902 | 121.7377 | 0.027466 | -0.022888 | 0.022888 | 0.12817 | -121.9162 | -121.9391 | 0.2243 | 0.17853 | 0.11444 | 0.050354 | -0.013732 | 0.027465 | -0.16937 | -0.19684 | 0.17395 | 0.16937 | 0.1236 | 0.14191 | 0.096131 | 0.096131 | 0.013733 | 0.14649 | 121.8567 | 0.036622 | 121.8842 | 0.16479 | 121.9116 | -121.9528 | -122.0535 | 0.14191 | 121.8842 | 0.091552 | 0.48981
2028.7812 | 122.049 | -0.15106 | 121.9437 | -0.15846 | -0.04773 | 0.0036594 | 0.024646 | -0.0031957 | -0.009675 | -0.0045095 | -0.028351 | 0.0055243 | 0.064704 | 0.048764 | -0.013029 | 0.025699 | -0.0042981 | -0.086975 | 0.041199 | 0.009155 | -0.054932 | 0.050354 | -0.064087 | 0.018311 | 0.35706 | 121.7926 | -0.14191 | 121.6873 | -0.009155 | -0.059509 | -0.032043 | 0.16022 | -121.9025 | -121.9986 | 0.20142 | 0.16937 | 0.086975 | 0.009156 | -0.073242 | 0.009155 | -0.15106 | -0.25635 | 0.14191 | 0.11902 | 0.091553 | 0.10986 | 0.082398 | 0.041199 | -0.064087 | 0.13275 | 121.8292 | 0.032044 | 121.9345 | 0.19226 | 121.9437 | -121.9345 | -122.0856 | 0.09613 | 121.8384 | 0.064087 | 0.50812
2030.5312 | 122.1771 | -0.10986 | 121.9025 | -0.15083 | -0.044312 | 0.0064364 | 0.027209 | 0.00064947 | -0.0071116 | -0.0047231 | -0.080231 | 0.0074469 | 0.064704 | 0.053464 | -0.015806 | 0.025912 | -0.0036573 | -0.059509 | 0.004578 | -0.013733 | -0.009155 | 0.059509 | -0.050354 | 0.027466 | 0.27466 | 121.756 | -0.11902 | 121.8018 | 0.10071 | 0.036621 | 0.10986 | 0.09613 | -121.8979 | -121.9116 | 0.16937 | 0.13733 | 0.059509 | 0.041199 | -0.036621 | -0.009156 | -0.14648 | -0.10071 | 0.21057 | 0.21973 | 0.14648 | 0.22888 | 0.15564 | 0.073242 | 0.004578 | 0.21973 | 121.9208 | 0.018311 | 121.875 | 0.11444 | 121.8658 | -121.9162 | -122.0215 | 0.10071 | 121.9116 | 0.050354 | 0.38452
2032.2812 | 122.0901 | -0.14648 | 121.9025 | -0.074539 | -0.046448 | 0.0023776 | 0.028705 | -0.00063233 | -0.0077524 | -0.00087794 | -0.092438 | 0.0046697 | 0.064918 | 0.04855 | -0.016874 | 0.025699 | -0.0053661 | -0.054932 | 0.041199 | 0.013733 | -0.032043 | 0.059509 | -0.036621 | 0.022888 | 0.37079 | 121.788 | -0.14191 | 121.7377 | 0.045776 | -0.027466 | 0.041199 | 0.16022 | -121.8613 | -121.9345 | 0.20599 | 0.16937 | 0.10986 | 0.009155 | -0.050354 | 0.004577 | -0.11444 | -0.16479 | 0.19226 | 0.18768 | 0.11902 | 0.18311 | 0.11444 | 0.045776 | -0.045776 | 0.18768 | 121.8796 | 0.027466 | 121.9299 | 0.18768 | 121.9345 | -121.8887 | -122.0444 | 0.11444 | 121.8842 | 0.091552 | 0.51727
2033.9844 | 122.1176 | -0.11902 | 121.9162 | -0.097427 | -0.045166 | 0.004941 | 0.029559 | -0.0019141 | -0.0077524 | -0.0028005 | -0.074127 | 0.0070197 | 0.064704 | 0.051114 | -0.015592 | 0.029117 | -0.0047253 | -0.045776 | 0.009155 | -0.009155 | -0.013733 | 0.068665 | -0.036621 | 0.022888 | 0.38452 | 121.7697 | -0.12817 | 121.7422 | 0.045776 | -0.009155 | 0.041199 | 0.10986 | -121.907 | -121.9299 | 0.18768 | 0.14191 | 0.082398 | 0.032043 | -0.027466 | -0.009155 | -0.14649 | -0.17395 | 0.16479 | 0.16022 | 0.10986 | 0.16937 | 0.11902 | 0.07782 | -0.004578 | 0.17395 | 121.8704 | 0.01831 | 121.8979 | 0.12817 | 121.8887 | -121.9254 | -122.0444 | 0.10529 | 121.8613 | 0.073243 | 0.50354
2035.75 | 122.0581 | -0.16022 | 121.9299 | -0.051651 | -0.044953 | 0.0019504 | 0.025287 | -0.0042639 | -0.0081796 | -0.0049367 | -0.019196 | 0.0059515 | 0.063423 | 0.051114 | -0.013456 | 0.027408 | -0.0034435 | -0.091553 | 0.050354 | -0.022888 | -0.054932 | 0.041199 | -0.064087 | 0.013733 | 0.36163 | 121.7697 | -0.14191 | 121.6827 | -0.013733 | -0.054932 | -0.045776 | 0.13733 | -121.8796 | -121.9849 | 0.20142 | 0.17395 | 0.09613 | 0.036621 | -0.041199 | 0.01831 | -0.16022 | -0.24719 | 0.14648 | 0.11444 | 0.10528 | 0.096131 | 0.086975 | 0.064087 | -0.032044 | 0.12817 | 121.8246 | 0.073242 | 121.9116 | 0.21057 | 121.9299 | -121.9528 | -122.0718 | 0.10528 | 121.843 | 0.068664 | 0.52185
2037.5 | 122.1222 | -0.12817 | 121.907 | -0.1432 | -0.045166 | 0.003873 | 0.024218 | -0.0025549 | -0.0092478 | -0.0062185 | -0.028351 | 0.0042425 | 0.064063 | 0.048123 | -0.015379 | 0.023776 | -0.0042981 | -0.07782 | -0.004578 | 0.004578 | -0.018311 | 0.086975 | -0.022888 | 0.068665 | 0.28381 | 121.7422 | -0.10071 | 121.7514 | 0.073242 | 0.032043 | 0.054932 | 0.13275 | -121.9116 | -121.9254 | 0.21515 | 0.19684 | 0.10529 | 0.064087 | -0.027466 | 0.027466 | -0.16479 | -0.15564 | 0.20142 | 0.18311 | 0.16022 | 0.15564 | 0.13275 | 0.082397 | -0.022889 | 0.17395 | 121.8521 | -0.009156 | 121.843 | 0.1236 | 121.8704 | -121.9025 | -122.0078 | 0.10986 | 121.8796 | 0.050354 | 0.41199
2039.25 | 122.0306 | -0.15564 | 121.9437 | -0.12794 | -0.044525 | 0.0053684 | 0.028064 | -0.00041873 | -0.0071116 | 0.00019006 | -0.10159 | 0.0046697 | 0.064277 | 0.056027 | -0.017515 | 0.026767 | -0.0083569 | -0.10986 | 0.009155 | -0.036621 | -0.10529 | -0.041199 | -0.14648 | -0.054932 | 0.17395 | 121.7972 | -0.1236 | 121.669 | -0.032043 | -0.082397 | -0.009155 | 0.11902 | -121.9345 | -122.049 | 0.11444 | 0.10071 | 0.009156 | -0.018311 | -0.10986 | 0.032044 | -0.14648 | -0.27466 | 0.1236 | 0.14649 | 0.073243 | 0.11444 | 0.041199 | -0.004578 | -0.068665 | 0.091553 | 121.7926 | 0.045776 | 121.9208 | 0.16479 | 121.9528 | -121.9803 | -122.0673 | 0.050354 | 121.8246 | 0.045777 | 0.32959
2040.9531 | 122.1863 | -0.11444 | 121.9254 | -0.11269 | -0.046234 | 0.0023776 | 0.024005 | -0.0057593 | -0.008607 | -0.0013051 | 0.0082703 | 0.0057379 | 0.066413 | 0.04321 | -0.015592 | 0.027835 | -0.0034435 | -0.022888 | 0 | 0.009155 | 0.064087 | 0.18768 | 0.059509 | 0.13275 | 0.49439 | 121.7697 | -0.11444 | 121.788 | 0.14648 | 0.1236 | 0.10529 | 0.1236 | -121.9254 | -121.8613 | 0.30212 | 0.24719 | 0.17395 | 0.1236 | 0.050354 | 0 | -0.15564 | -0.13733 | 0.26093 | 0.21973 | 0.23804 | 0.21973 | 0.23804 | 0.17853 | 0.054932 | 0.26093 | 121.9025 | -0.009155 | 121.8842 | 0.11444 | 121.8842 | -121.9162 | -122.0398 | 0.17853 | 121.9025 | 0.091553 | 0.60883
2042.6875 | 122.0398 | -0.14648 | 121.9437 | -0.097427 | -0.041748 | 0.004941 | 0.027423 | -0.00020513 | -0.0083932 | -0.0023733 | -0.1077 | 0.0057379 | 0.065345 | 0.052823 | -0.015806 | 0.029758 | -0.0075025 | -0.10071 | 0.022888 | -0.036621 | -0.10529 | -0.032043 | -0.12817 | -0.054932 | 0.17395 | 121.8246 | -0.13275 | 121.6782 | -0.032043 | -0.091553 | -0.013733 | 0.10986 | -121.9208 | -122.049 | 0.11444 | 0.091552 | 0.01831 | -0.018311 | -0.091553 | 0.013733 | -0.11902 | -0.2655 | 0.11444 | 0.13275 | 0.054931 | 0.11902 | 0.041198 | 0.004578 | -0.068665 | 0.10071 | 121.8109 | 0.059509 | 121.9574 | 0.16937 | 121.9711 | -121.9803 | -122.0764 | 0.041198 | 121.8246 | 0.045776 | 0.32043
2044.4375 | 122.1039 | -0.1236 | 121.9574 | -0.082169 | -0.044953 | 0.0019504 | 0.029132 | 0.0023585 | -0.008607 | -0.0042959 | -0.09549 | 0.0074469 | 0.065345 | 0.057095 | -0.015592 | 0.027194 | -0.0051525 | -0.068665 | 0.018311 | -0.022888 | -0.027466 | 0.064087 | -0.045776 | 0.027466 | 0.38452 | 121.8018 | -0.1236 | 121.7194 | 0.036621 | -0.022888 | 0.027466 | 0.10071 | -121.9391 | -121.9849 | 0.18768 | 0.15106 | 0.07782 | 0.050354 | -0.022888 | 0 | -0.15564 | -0.23804 | 0.16022 | 0.15106 | 0.10071 | 0.15106 | 0.10071 | 0.086975 | -0.004578 | 0.16022 | 121.843 | 0.041199 | 121.9254 | 0.14191 | 121.9254 | -121.9803 | -122.081 | 0.09613 | 121.843 | 0.054931 | 0.50812
2046.1406 | 122.1542 | -0.1236 | 121.9299 | -0.16609 | -0.045166 | 0.0019504 | 0.02315 | -0.0034095 | -0.0088206 | -0.0032277 | 0.011322 | 0.0046697 | 0.064491 | 0.054959 | -0.015165 | 0.025912 | -0.01092 | -0.082397 | -0.027466 | -0.004578 | -0.018311 | 0.091553 | -0.022888 | 0.068665 | 0.28839 | 121.7834 | -0.11444 | 121.7606 | 0.073242 | 0.027466 | 0.068665 | 0.11902 | -121.9574 | -121.9482 | 0.21515 | 0.19226 | 0.10071 | 0.073243 | -0.01831 | 0.009155 | -0.14648 | -0.16937 | 0.19684 | 0.19226 | 0.15106 | 0.18311 | 0.14191 | 0.096131 | -0.013733 | 0.18768 | 121.875 | -0.022888 | 121.8979 | 0.09613 | 121.907 | -121.9345 | -122.0444 | 0.10528 | 121.8842 | 0.041199 | 0.41199
2047.8906 | 122.1497 | -0.11444 | 121.9299 | -0.1432 | -0.045166 | 0.0034456 | 0.023364 | 0.0025721 | -0.0083932 | -0.0060049 | -0.028351 | 0.0042425 | 0.063423 | 0.040433 | -0.016233 | 0.026553 | -0.0017347 | -0.064087 | -0.032043 | 0.009155 | 0.032043 | 0.14191 | -0.013733 | 0.07782 | 0.32501 | 121.7422 | -0.10529 | 121.788 | 0.07782 | 0.050354 | 0.082397 | 0.1236 | -121.962 | -121.8979 | 0.25635 | 0.19226 | 0.10071 | 0.068665 | -0.022888 | 0.009155 | -0.18768 | -0.14191 | 0.19226 | 0.19684 | 0.16479 | 0.18768 | 0.15564 | 0.13275 | 0.022888 | 0.18311 | 121.8933 | -0.041198 | 121.8475 | 0.082398 | 121.8567 | -121.9208 | -122.0352 | 0.14648 | 121.9025 | 0.050354 | 0.43945
2049.6406 | 122.1313 | -0.11444 | 121.9208 | -0.17372 | -0.044525 | 0.0036594 | 0.022509 | -0.00020513 | -0.0083932 | -0.0075003 | 0.0021667 | 0.0036017 | 0.063423 | 0.043637 | -0.016874 | 0.026553 | -0.0013073 | -0.086975 | -0.027466 | 0.013733 | 0 | 0.064087 | -0.041199 | 0.059509 | 0.29755 | 121.756 | -0.10071 | 121.7651 | 0.064087 | 0.027466 | 0.059509 | 0.12817 | -121.9482 | -121.9208 | 0.17853 | 0.17395 | 0.073242 | 0.045776 | -0.054932 | 0.013733 | -0.16479 | -0.15564 | 0.17853 | 0.17395 | 0.14191 | 0.16022 | 0.12817 | 0.050354 | -0.013733 | 0.1648 | 121.8658 | -0.041199 | 121.8567 | 0.086975 | 121.8704 | -121.907 | -122.0215 | 0.11444 | 121.8796 | 0.027466 | 0.41199
2051.3906 | 122.1451 | -0.10529 | 121.9345 | -0.13557 | -0.044525 | 0.0036594 | 0.023578 | -0.00084593 | -0.011384 | -0.0042959 | -0.022247 | 0.0040289 | 0.0662 | 0.047482 | -0.018369 | 0.027408 | -0.0040845 | -0.09613 | -0.018311 | 0.009155 | -0.013733 | 0.068665 | -0.032043 | 0.054932 | 0.31128 | 121.7468 | -0.10529 | 121.7377 | 0.045776 | 0.009155 | 0.059509 | 0.11444 | -121.9528 | -121.9482 | 0.17395 | 0.16022 | 0.073243 | 0.045777 | -0.041198 | 0 | -0.18768 | -0.19684 | 0.15106 | 0.16479 | 0.11444 | 0.16479 | 0.11444 | 0.05951 | -0.022888 | 0.15106 | 121.843 | -0.027466 | 121.8521 | 0.086975 | 121.8521 | -121.9254 | -122.0398 | 0.091553 | 121.843 | 0.009156 | 0.41656
2053.1406 | 122.0627 | -0.14191 | 121.9345 | -0.15846 | -0.044312 | 0.005582 | 0.028705 | -0.0014867 | -0.007966 | -0.0077139 | -0.12601 | 0.0057379 | 0.064063 | 0.054104 | -0.017729 | 0.027408 | -0.0053661 | -0.13275 | 0.004578 | -0.032043 | -0.091553 | -0.041199 | -0.13275 | -0.059509 | 0.1831 | 121.8246 | -0.11902 | 121.7056 | -0.050354 | -0.091553 | 0.004578 | 0.10986 | -121.9299 | -122.0261 | 0.10071 | 0.082398 | 0.009156 | -0.027466 | -0.10071 | 0.022888 | -0.10986 | -0.22888 | 0.091553 | 0.14649 | 0.050354 | 0.1236 | 0.027466 | -0.009156 | -0.05951 | 0.068665 | 121.8246 | 0.036621 | 121.9437 | 0.14649 | 121.9666 | -121.9666 | -122.0535 | 0.050354 | 121.8475 | 0.009156 | 0.32501
2054.8281 | 122.2 | -0.082397 | 121.9116 | -0.20424 | -0.044312 | 0.0034456 | 0.027209 | -0.0017005 | -0.0073252 | -0.0032277 | -0.080231 | 0.0065923 | 0.064704 | 0.051114 | -0.015806 | 0.028903 | -0.0072889 | -0.045776 | -0.036621 | -0.004578 | 0.041199 | 0.13275 | -0.009155 | 0.073242 | 0.32959 | 121.7789 | -0.09613 | 121.843 | 0.11902 | 0.068665 | 0.11902 | 0.077819 | -121.9482 | -121.8704 | 0.21515 | 0.15564 | 0.073242 | 0.07782 | -0.004577 | -0.013733 | -0.13275 | -0.068664 | 0.20142 | 0.20142 | 0.15106 | 0.21515 | 0.16479 | 0.13733 | 0.045777 | 0.21515 | 121.9391 | -0.032043 | 121.875 | 0.045776 | 121.8613 | -121.9162 | -122.0078 | 0.1236 | 121.9254 | 0.036621 | 0.41199
2056.5781 | 122.0993 | -0.12817 | 121.9482 | -0.097427 | -0.044525 | 0.003873 | 0.023364 | -0.0034095 | -0.011598 | -0.0040823 | -0.037506 | 0.0042425 | 0.061286 | 0.056241 | -0.015806 | 0.025058 | -0.0042981 | -0.064087 | 0 | -0.013733 | -0.004578 | 0.10071 | -0.013733 | 0.050354 | 0.40741 | 121.8018 | -0.10529 | 121.7102 | 0.032043 | -0.018311 | -0.009155 | 0.11444 | -121.9482 | -121.9528 | 0.22888 | 0.17853 | 0.11444 | 0.064087 | 0 | 0.022888 | -0.14648 | -0.23804 | 0.16022 | 0.11902 | 0.10986 | 0.096131 | 0.086975 | 0.11444 | 0.009155 | 0.13733 | 121.8155 | 0.013733 | 121.907 | 0.12817 | 121.9299 | -121.962 | -122.0535 | 0.1236 | 121.8384 | 0.064087 | 0.53558
2058.3281 | 122.168 | -0.10986 | 121.9391 | -0.17372 | -0.044525 | 0.0030184 | 0.026996 | -0.0017005 | -0.0083932 | -0.0042959 | -0.01004 | 0.0063787 | 0.0662 | 0.047909 | -0.016233 | 0.026126 | -0.0089977 | -0.10071 | -0.009155 | -0.004578 | -0.022888 | 0.091553 | -0.032043 | 0.064087 | 0.33875 | 121.788 | -0.10986 | 121.7743 | 0.086975 | 0.064087 | 0.082397 | 0.10529 | -121.9482 | -121.962 | 0.20142 | 0.17395 | 0.07782 | 0.068665 | -0.027465 | 0 | -0.15106 | -0.16479 | 0.19684 | 0.19226 | 0.17395 | 0.19226 | 0.17395 | 0.096131 | -0.01831 | 0.19684 | 121.8842 | -0.004577 | 121.8979 | 0.10071 | 121.8979 | -121.9437 | -122.049 | 0.086975 | 121.8842 | 0.009155 | 0.44861
2060.0781 | 122.1771 | -0.1236 | 121.9391 | -0.1432 | -0.047089 | 0.0043002 | 0.024646 | 0.0012903 | -0.01053 | -0.0062185 | -0.037506 | 0.0059515 | 0.065772 | 0.048764 | -0.016447 | 0.025272 | -0.0070751 | -0.041199 | -0.027466 | 0 | 0.041199 | 0.12817 | 0.022888 | 0.10071 | 0.47607 | 121.8063 | -0.10529 | 121.7651 | 0.082397 | 0.041199 | 0.073242 | 0.1236 | -121.9666 | -121.8979 | 0.25177 | 0.2243 | 0.14648 | 0.10071 | 0.022888 | 0.01831 | -0.13275 | -0.17395 | 0.20599 | 0.19684 | 0.16479 | 0.17853 | 0.14649 | 0.12817 | 0.041199 | 0.18768 | 121.8704 | -0.027466 | 121.9116 | 0.09613 | 121.9299 | -121.9391 | -122.0444 | 0.16479 | 121.8887 | 0.082397 | 0.59967
2061.7656 | 122.0993 | -0.13733 | 121.9711 | -0.15083 | -0.045594 | 0.0045138 | 0.026568 | 0.00064947 | -0.010316 | -0.0017325 | -0.1138 | 0.0063787 | 0.065772 | 0.054104 | -0.015165 | 0.02869 | -0.0047253 | -0.068665 | -0.018311 | -0.022888 | -0.009155 | 0.068665 | -0.054932 | 0.018311 | 0.37537 | 121.8338 | -0.1236 | 121.7468 | 0.036621 | -0.018311 | 0.045776 | 0.11444 | -121.9894 | -121.9803 | 0.20599 | 0.15564 | 0.082397 | 0.041199 | -0.032044 | 0.013733 | -0.13733 | -0.2243 | 0.17395 | 0.18311 | 0.11902 | 0.16937 | 0.10528 | 0.091553 | 0.013733 | 0.16022 | 121.8704 | 0.004577 | 121.9574 | 0.11902 | 121.9711 | -121.994 | -122.0947 | 0.12817 | 121.8842 | 0.068664 | 0.5127
2063.5156 | 122.081 | -0.13733 | 121.9757 | -0.17372 | -0.041962 | 0.0034456 | 0.028705 | 0.0036401 | -0.009675 | -0.0038687 | -0.098541 | 0.0050971 | 0.063423 | 0.054318 | -0.013456 | 0.027408 | -0.0038709 | -0.091553 | -0.018311 | -0.032043 | -0.059509 | 0.004578 | -0.12817 | -0.045776 | 0.24261 | 121.8521 | -0.1236 | 121.7148 | -0.022888 | -0.091553 | -0.013733 | 0.10529 | -121.994 | -122.0352 | 0.14191 | 0.091553 | 0.009155 | -0.013733 | -0.096131 | 0.013733 | -0.1236 | -0.26093 | 0.11444 | 0.1236 | 0.045776 | 0.10986 | 0.032043 | 0.036621 | -0.027466 | 0.10071 | 121.8384 | 0.013732 | 121.9757 | 0.11902 | 121.9894 | -122.0078 | -122.0993 | 0.07782 | 121.8521 | 0.045776 | 0.37994
2065.2656 | 122.2 | -0.082397 | 121.9437 | -0.13557 | -0.045594 | 0.0053684 | 0.026141 | 0.00064947 | -0.0077524 | -0.0038687 | -0.074127 | 0.0061651 | 0.064063 | 0.046628 | -0.014951 | 0.028476 | -0.011348 | -0.09613 | -0.018311 | -0.022888 | 0.009155 | 0.086975 | -0.041199 | 0.032043 | 0.30212 | 121.7789 | -0.10071 | 121.8246 | 0.086975 | 0.064087 | 0.11444 | 0.059509 | -121.962 | -121.9345 | 0.16937 | 0.11444 | 0.041198 | 0.054931 | -0.018311 | -0.018311 | -0.16479 | -0.11902 | 0.16937 | 0.19684 | 0.14648 | 0.21515 | 0.1648 | 0.10986 | 0.032043 | 0.18768 | 121.9254 | 0.004577 | 121.8796 | 0.064086 | 121.8613 | -121.9666 | -122.0444 | 0.091552 | 121.907 | -0.013733 | 0.38452
2066.9531 | 122.1634 | -0.10071 | 121.9437 | -0.10506 | -0.045594 | 0.0019504 | 0.026141 | -0.0031957 | -0.008607 | -0.0034415 | -0.01004 | 0.0050971 | 0.062141 | 0.048764 | -0.014951 | 0.025699 | -0.0051525 | -0.10529 | -0.032043 | -0.004578 | 0.004578 | 0.073242 | -0.036621 | 0.036621 | 0.30212 | 121.788 | -0.10529 | 121.7743 | 0.068665 | 0.041199 | 0.073242 | 0.09613 | -121.9757 | -121.9391 | 0.17395 | 0.13733 | 0.064087 | 0.041199 | -0.032043 | -0.004578 | -0.15564 | -0.16937 | 0.16937 | 0.17395 | 0.14191 | 0.17853 | 0.14649 | 0.07782 | 0.009156 | 0.17395 | 121.8796 | -0.027465 | 121.8933 | 0.068665 | 121.8887 | -121.9482 | -122.049 | 0.10529 | 121.875 | -0.004578 | 0.40283
2068.7031 | 122.1313 | -0.11902 | 121.9391 | -0.11269 | -0.044312 | 0.0047274 | 0.026996 | 0.0017175 | -0.0081796 | -0.0038687 | -0.1199 | 0.0068059 | 0.065986 | 0.059231 | -0.016447 | 0.02869 | -0.0066479 | -0.13733 | -0.013733 | -0.041199 | -0.082397 | -0.009155 | -0.13275 | -0.045776 | 0.2243 | 121.8201 | -0.12817 | 121.7651 | 0.027466 | -0.018311 | 0.054932 | 0.07782 | -121.9528 | -122.0215 | 0.10986 | 0.073243 | -0.013732 | -0.004577 | -0.091552 | -0.009155 | -0.11902 | -0.17395 | 0.14649 | 0.17395 | 0.10071 | 0.18311 | 0.10986 | 0.032044 | -0.041198 | 0.15564 | 121.8933 | 0.027466 | 121.9482 | 0.10529 | 121.9391 | -121.9803 | -122.0673 | 0.036622 | 121.8842 | -0.01831 | 0.34332
2070.3906 | 122.1176 | -0.13275 | 121.9666 | -0.17372 | -0.044953 | 0.003232 | 0.028064 | -0.00041873 | -0.009675 | -0.0042959 | -0.089386 | 0.0063787 | 0.0615 | 0.051755 | -0.016233 | 0.028903 | -0.0077161 | -0.086975 | -0.009155 | -0.032043 | -0.036621 | 0.064087 | -0.054932 | 0.004578 | 0.37079 | 121.8292 | -0.11902 | 121.7651 | 0.064087 | -0.004578 | 0.036621 | 0.10071 | -121.9757 | -122.0032 | 0.19684 | 0.13733 | 0.077819 | 0.036621 | -0.022889 | 0.013732 | -0.13733 | -0.20142 | 0.19684 | 0.16937 | 0.12817 | 0.15564 | 0.11444 | 0.09613 | -0.004578 | 0.18311 | 121.8842 | 0.022888 | 121.9482 | 0.1236 | 121.962 | -121.9986 | -122.0856 | 0.09613 | 121.8979 | 0.045776 | 0.50354
2072.1406 | 122.081 | -0.14191 | 121.9849 | -0.12032 | -0.046448 | 0.0036594 | 0.024432 | -0.00084593 | -0.009675 | -0.0017325 | -0.046661 | 0.0065923 | 0.062995 | 0.057095 | -0.015592 | 0.028476 | 0.00082889 | -0.14191 | 0.004578 | -0.050354 | -0.09613 | -0.004578 | -0.09613 | -0.022888 | 0.33875 | 121.8567 | -0.14191 | 121.701 | 0.004578 | -0.045776 | -0.018311 | 0.091553 | -121.9803 | -122.081 | 0.13733 | 0.11902 | 0.045777 | 0.027466 | -0.045776 | 0 | -0.12817 | -0.28381 | 0.14649 | 0.1236 | 0.096131 | 0.1236 | 0.096131 | 0.045776 | -0.045776 | 0.14649 | 121.843 | 0.054932 | 121.9986 | 0.14649 | 121.9986 | -122.0352 | -122.1268 | 0.045777 | 121.843 | 0 | 0.48065
2073.8281 | 122.0856 | -0.15564 | 121.9711 | -0.051651 | -0.047303 | 0.0051546 | 0.026996 | -0.0014867 | -0.01053 | -0.0028005 | -0.077179 | 0.0046697 | 0.066841 | 0.051755 | -0.015379 | 0.027621 | -0.0038709 | -0.15564 | 0.027466 | -0.045776 | -0.10071 | 0.009155 | -0.10529 | -0.027466 | 0.35706 | 121.8292 | -0.15106 | 121.701 | 0 | -0.041199 | -0.009155 | 0.10986 | -121.9437 | -122.0718 | 0.16479 | 0.12817 | 0.050354 | 0.01831 | -0.05951 | 0.004578 | -0.14191 | -0.27008 | 0.15564 | 0.14649 | 0.11444 | 0.14191 | 0.10986 | 0.054931 | -0.054932 | 0.15106 | 121.8521 | 0.073242 | 121.9803 | 0.18311 | 121.9849 | -122.0169 | -122.1222 | 0.054932 | 121.8567 | 0 | 0.5127
2075.5625 | 122.0718 | -0.11902 | 121.9803 | -0.1432 | -0.044739 | 0.003873 | 0.029986 | 0.0019311 | -0.010957 | -0.0023733 | -0.092438 | 0.0076605 | 0.065345 | 0.051114 | -0.016874 | 0.026767 | -0.0049389 | -0.082397 | 0 | -0.036621 | -0.073242 | 0.004578 | -0.11444 | -0.041199 | 0.27924 | 121.8384 | -0.13275 | 121.7148 | -0.018311 | -0.07782 | 0 | 0.082398 | -121.9803 | -122.0535 | 0.1236 | 0.07782 | 0.004578 | -0.004578 | -0.07782 | -0.013732 | -0.14191 | -0.2655 | 0.10071 | 0.11902 | 0.041199 | 0.13275 | 0.054931 | 0.041199 | -0.036621 | 0.11444 | 121.8475 | 0.036621 | 121.9711 | 0.11902 | 121.9574 | -122.0169 | -122.113 | 0.045777 | 121.8338 | 0.036622 | 0.39825
2077.25 | 122.168 | -0.11444 | 121.9528 | -0.16609 | -0.046448 | 0.002164 | 0.022723 | 0.00064947 | -0.009675 | -0.0021597 | -0.0069885 | 0.0050971 | 0.065986 | 0.045132 | -0.012602 | 0.02634 | -0.0049389 | -0.10529 | -0.022888 | -0.032043 | -0.032043 | 0.054932 | -0.054932 | 0.032043 | 0.31586 | 121.8246 | -0.10529 | 121.7789 | 0.064087 | 0.027466 | 0.082397 | 0.082398 | -121.9757 | -121.9849 | 0.16937 | 0.14648 | 0.059509 | 0.064086 | -0.022889 | 0.009155 | -0.12817 | -0.17395 | 0.17853 | 0.19684 | 0.14191 | 0.18768 | 0.13275 | 0.086975 | 0 | 0.16937 | 121.8842 | 0.009155 | 121.9299 | 0.091553 | 121.9391 | -121.9849 | -122.0581 | 0.082398 | 121.8933 | 0.009155 | 0.4303
2078.9375 | 122.0947 | -0.12817 | 121.9711 | -0.15846 | -0.042389 | 0.0047274 | 0.0255 | -0.0027685 | -0.008607 | -0.0040823 | -0.1199 | 0.0042425 | 0.064277 | 0.047482 | -0.016233 | 0.028476 | -0.0028027 | -0.09613 | -0.013733 | -0.027466 | -0.073242 | 0.013733 | -0.1236 | -0.050354 | 0.27924 | 121.8246 | -0.11902 | 121.7285 | -0.018311 | -0.068665 | -0.004578 | 0.10071 | -121.9849 | -122.0444 | 0.14191 | 0.07782 | 0.004578 | -0.022888 | -0.09613 | 0.009155 | -0.14648 | -0.24261 | 0.10986 | 0.1236 | 0.059509 | 0.11444 | 0.050354 | 0.041199 | -0.045776 | 0.10071 | 121.8475 | 0.013733 | 121.9437 | 0.11444 | 121.9528 | -121.9986 | -122.0901 | 0.054932 | 121.8567 | 0.032044 | 0.40741
2080.6875 | 122.2092 | -0.1236 | 121.9666 | -0.082169 | -0.046448 | 0.0019504 | 0.024218 | -0.00041873 | -0.0071116 | -0.0025869 | -0.0039367 | 0.0048833 | 0.064704 | 0.050259 | -0.014738 | 0.026553 | -0.0062207 | -0.073242 | -0.036621 | -0.009155 | 0.027466 | 0.13275 | 0.036621 | 0.086975 | 0.48065 | 121.8246 | -0.09613 | 121.8063 | 0.11444 | 0.073242 | 0.10071 | 0.11444 | -122.0032 | -121.9391 | 0.25635 | 0.21057 | 0.16022 | 0.09613 | 0.045776 | 0.027466 | -0.14191 | -0.16022 | 0.23804 | 0.2243 | 0.19684 | 0.19684 | 0.16937 | 0.14191 | 0.036621 | 0.21057 | 121.9025 | -0.027466 | 121.9208 | 0.086975 | 121.9482 | -121.9757 | -122.0627 | 0.15106 | 121.9299 | 0.050354 | 0.60425
2082.3906 | 122.0718 | -0.14648 | 122.0032 | -0.16609 | -0.041748 | 0.002164 | 0.028064 | 0.0012903 | -0.0075388 | -0.0017325 | -0.10159 | 0.0048833 | 0.064491 | 0.053036 | -0.015165 | 0.028903 | -0.0030163 | -0.15106 | -0.004578 | -0.027466 | -0.11444 | -0.059509 | -0.15564 | -0.073242 | 0.20142 | 121.8658 | -0.13733 | 121.7056 | -0.022888 | -0.091553 | -0.004578 | 0.11902 | -122.0078 | -122.1176 | 0.086975 | 0.073242 | -0.009156 | -0.045776 | -0.12817 | 0.009155 | -0.13733 | -0.29755 | 0.1236 | 0.14191 | 0.054931 | 0.13275 | 0.045776 | -0.032043 | -0.086975 | 0.11444 | 121.843 | 0.022888 | 122.0032 | 0.14191 | 122.0123 | -122.0306 | -122.1405 | 0.032043 | 121.8521 | -0.004578 | 0.3479
2084.1406 | 122.1313 | -0.12817 | 121.9894 | -0.10506 | -0.044525 | 0.005582 | 0.025073 | -0.0038367 | -0.0081796 | -0.0019461 | -0.01004 | 0.0061651 | 0.064277 | 0.046414 | -0.017088 | 0.025485 | -0.0064343 | -0.07782 | -0.027466 | -0.018311 | 0 | 0.091553 | -0.004578 | 0.059509 | 0.43945 | 121.8338 | -0.1236 | 121.7422 | 0.045776 | 0 | 0.027466 | 0.10986 | -122.0169 | -121.9894 | 0.21973 | 0.18768 | 0.1236 | 0.07782 | 0.013733 | 0.004578 | -0.15564 | -0.24719 | 0.17395 | 0.15564 | 0.12817 | 0.15106 | 0.1236 | 0.10986 | 0.018311 | 0.16937 | 121.8658 | -0.009155 | 121.9574 | 0.10071 | 121.962 | -122.0078 | -122.113 | 0.12817 | 121.8704 | 0.050354 | 0.56763
2085.8281 | 122.1451 | -0.14648 | 121.9482 | -0.15083 | -0.044953 | 0.002164 | 0.028277 | -0.0025549 | -0.0088206 | -0.0019461 | -0.1077 | 0.0048833 | 0.065772 | 0.050686 | -0.016447 | 0.026126 | -0.0081433 | -0.09613 | -0.009155 | -0.050354 | -0.050354 | 0.027466 | -0.059509 | -0.009155 | 0.39368 | 121.8567 | -0.12817 | 121.7834 | 0.054932 | -0.004578 | 0.036621 | 0.09613 | -121.9574 | -121.9986 | 0.17395 | 0.13733 | 0.086975 | 0.041199 | -0.009155 | 0.01831 | -0.091553 | -0.16479 | 0.20142 | 0.18311 | 0.14191 | 0.1648 | 0.1236 | 0.07782 | 0 | 0.18311 | 121.9116 | 0.041199 | 121.9849 | 0.13733 | 122.0032 | -121.9986 | -122.0764 | 0.09613 | 121.9299 | 0.050354 | 0.54016
2087.5781 | 122.168 | -0.082397 | 121.9482 | -0.1432 | -0.045594 | 0.0043002 | 0.024646 | -0.0017005 | -0.0075388 | -0.0023733 | -0.022247 | 0.0063787 | 0.064491 | 0.044064 | -0.016447 | 0.028476 | -0.0070751 | -0.07782 | -0.036621 | -0.013733 | -0.013733 | 0.12817 | -0.036621 | 0.054932 | 0.33417 | 121.8018 | -0.10529 | 121.8018 | 0.091553 | 0.045776 | 0.082397 | 0.068664 | -121.9849 | -121.962 | 0.21057 | 0.13733 | 0.045776 | 0.068665 | -0.022888 | -0.022889 | -0.14648 | -0.14648 | 0.17395 | 0.16479 | 0.12817 | 0.18768 | 0.15106 | 0.14191 | 0 | 0.19684 | 121.907 | -0.022888 | 121.907 | 0.045776 | 121.8842 | -121.962 | -122.0535 | 0.068664 | 121.8842 | 0.004577 | 0.41656
2089.2656 | 122.1863 | -0.10986 | 121.9757 | -0.18135 | -0.044739 | 0.0036594 | 0.024859 | -0.0059729 | -0.0075388 | -0.0021597 | -0.022247 | 0.0048833 | 0.064918 | 0.051114 | -0.016447 | 0.027194 | -0.0045117 | -0.091553 | -0.050354 | -0.013733 | -0.013733 | 0.082397 | -0.045776 | 0.054932 | 0.31586 | 121.8109 | -0.09613 | 121.7972 | 0.068665 | 0.050354 | 0.073242 | 0.09613 | -122.0261 | -121.9894 | 0.19226 | 0.16479 | 0.064087 | 0.068665 | -0.032043 | 0.013733 | -0.16479 | -0.17853 | 0.17853 | 0.18311 | 0.16022 | 0.16937 | 0.14648 | 0.09613 | 0 | 0.16479 | 121.8933 | -0.036621 | 121.907 | 0.059509 | 121.9208 | -121.9894 | -122.0718 | 0.09613 | 121.907 | 0.01831 | 0.42572
2091.0156 | 122.1451 | -0.11902 | 121.9803 | -0.15083 | -0.045166 | 0.0019504 | 0.026141 | -0.0010595 | -0.0094614 | -0.0032277 | -0.13821 | 0.0078741 | 0.065132 | 0.049618 | -0.018156 | 0.027194 | -0.0042981 | -0.09613 | -0.022888 | -0.032043 | -0.032043 | 0.036621 | -0.073242 | -0.009155 | 0.37994 | 121.8475 | -0.10529 | 121.7972 | 0.054932 | 0.004578 | 0.050354 | 0.086976 | -122.0032 | -122.0123 | 0.15564 | 0.10986 | 0.045777 | 0.022888 | -0.041199 | 0.013733 | -0.13275 | -0.18311 | 0.17395 | 0.16937 | 0.1236 | 0.15564 | 0.10986 | 0.068664 | 0 | 0.16022 | 121.9025 | 0.009155 | 121.9528 | 0.096131 | 121.9666 | -122.0123 | -122.0856 | 0.086976 | 121.9162 | 0.022889 | 0.49896
2092.7656 | 122.2321 | -0.082397 | 121.9803 | -0.1432 | -0.048584 | 0.0040866 | 0.02315 | -0.0051183 | -0.011384 | -0.0047231 | 0.029632 | 0.0050971 | 0.0662 | 0.047909 | -0.01602 | 0.025485 | -0.0047253 | -0.059509 | -0.027466 | -0.004578 | 0.045776 | 0.16937 | 0.050354 | 0.09613 | 0.51727 | 121.788 | -0.09613 | 121.875 | 0.14191 | 0.11902 | 0.10529 | 0.077819 | -122.0078 | -121.9345 | 0.25177 | 0.17853 | 0.13275 | 0.10071 | 0.054932 | -0.013733 | -0.19226 | -0.10529 | 0.2243 | 0.18768 | 0.20142 | 0.20142 | 0.21515 | 0.17395 | 0.050354 | 0.23804 | 121.9711 | -0.022888 | 121.8842 | 0.054931 | 121.8704 | -121.9849 | -122.0764 | 0.12817 | 121.9574 | 0.022888 | 0.59967
2094.5312 | 122.1954 | -0.11444 | 121.9711 | -0.10506 | -0.04538 | 0.0045138 | 0.023364 | -0.0021277 | -0.008607 | -0.0030141 | -0.034454 | 0.0050971 | 0.066841 | 0.047055 | -0.016447 | 0.027408 | -0.0060071 | -0.10529 | -0.036621 | -0.036621 | -0.022888 | 0.086975 | -0.054932 | 0.041199 | 0.31586 | 121.8246 | -0.09613 | 121.8018 | 0.082397 | 0.041199 | 0.07782 | 0.07782 | -122.0078 | -121.994 | 0.20142 | 0.15564 | 0.059509 | 0.07782 | -0.018311 | 0.018311 | -0.14648 | -0.16937 | 0.19684 | 0.19226 | 0.15564 | 0.17395 | 0.13733 | 0.1236 | 0.013733 | 0.17853 | 121.8979 | 0 | 121.9208 | 0.07782 | 121.9391 | -122.0078 | -122.0673 | 0.091553 | 121.9162 | 0.009155 | 0.4303
2096.2812 | 122.1634 | -0.13733 | 121.9986 | -0.12794 | -0.044098 | 0.0017368 | 0.029132 | 0.0036401 | -0.0077524 | -0.0028005 | -0.1138 | 0.0046697 | 0.065986 | 0.051114 | -0.01666 | 0.025912 | 0.0016833 | -0.091553 | -0.013733 | -0.041199 | -0.032043 | 0.041199 | -0.068665 | -0.004578 | 0.37537 | 121.8521 | -0.11902 | 121.8018 | 0.059509 | 0.004578 | 0.054932 | 0.09613 | -122.0123 | -122.0306 | 0.17853 | 0.13275 | 0.068664 | 0.036621 | -0.027466 | 0.01831 | -0.14648 | -0.19684 | 0.19684 | 0.19226 | 0.14191 | 0.17395 | 0.1236 | 0.082398 | 0.009156 | 0.17853 | 121.9208 | 0.027466 | 121.9711 | 0.1236 | 121.9894 | -122.0398 | -122.1176 | 0.10529 | 121.9391 | 0.045776 | 0.5127
2097.9688 | 122.2092 | -0.10986 | 121.9803 | -0.18898 | -0.046234 | 0.0023776 | 0.027636 | 0.0025721 | -0.0090342 | -0.0053641 | -0.089386 | 0.0053107 | 0.063636 | 0.050473 | -0.01602 | 0.026553 | -0.0028027 | -0.11444 | -0.018311 | -0.050354 | -0.064087 | 0.022888 | -0.10071 | -0.032043 | 0.2655 | 121.8384 | -0.13275 | 121.8246 | 0.086975 | 0.032043 | 0.10071 | 0.059509 | -121.9986 | -122.0444 | 0.13275 | 0.07782 | 0.009155 | 0.018311 | -0.050354 | -0.022888 | -0.14191 | -0.15564 | 0.19684 | 0.21057 | 0.14191 | 0.23346 | 0.16479 | 0.073242 | -0.013733 | 0.21973 | 121.9574 | 0.032043 | 121.9711 | 0.091552 | 121.9482 | -122.0306 | -122.113 | 0.045776 | 121.9345 | -0.004578 | 0.37537
2099.7188 | 122.1085 | -0.13733 | 122.0032 | -0.1432 | -0.047943 | 0.0010958 | 0.024859 | -0.0017005 | -0.0081796 | -0.0021597 | -0.013092 | 0.0048833 | 0.065559 | 0.054104 | -0.014524 | 0.025272 | -0.0051525 | -0.10071 | -0.041199 | -0.022888 | -0.054932 | 0.045776 | -0.064087 | 0.009155 | 0.39825 | 121.8567 | -0.11902 | 121.7331 | 0.032043 | -0.027466 | 0 | 0.11444 | -122.0444 | -122.0581 | 0.18311 | 0.14648 | 0.073242 | 0.032043 | -0.041199 | 0.01831 | -0.14648 | -0.27008 | 0.16937 | 0.13733 | 0.10986 | 0.11902 | 0.091553 | 0.068664 | -0.032044 | 0.15106 | 121.8521 | -0.018311 | 121.9757 | 0.09613 | 121.994 | -122.0261 | -122.1222 | 0.082397 | 121.8704 | 0.036621 | 0.53558
2101.4062 | 122.1497 | -0.12817 | 121.9757 | -0.051651 | -0.043244 | 0.0053684 | 0.029559 | 0.0049219 | -0.0081796 | -0.0032277 | -0.083283 | 0.0046697 | 0.062141 | 0.050686 | -0.017729 | 0.02933 | -0.0051525 | -0.09613 | -0.018311 | -0.032043 | -0.041199 | 0.036621 | -0.082397 | 0 | 0.35706 | 121.8521 | -0.1236 | 121.7743 | 0.032043 | -0.022888 | 0.022888 | 0.096131 | -121.994 | -122.0169 | 0.1648 | 0.12817 | 0.045777 | 0.032043 | -0.050354 | 0.004578 | -0.1236 | -0.20142 | 0.16022 | 0.15106 | 0.10529 | 0.14648 | 0.10071 | 0.068664 | -0.009156 | 0.15564 | 121.8979 | 0.013732 | 121.9757 | 0.10986 | 121.9803 | -122.0078 | -122.0993 | 0.086975 | 121.9025 | 0.032044 | 0.48523
2103.1719 | 122.1268 | -0.14648 | 121.9986 | -0.05928 | -0.046875 | 0.0030184 | 0.025287 | -0.0010595 | -0.0092478 | -0.0023733 | -0.074127 | 0.0065923 | 0.065132 | 0.052823 | -0.015165 | 0.027835 | -0.0017347 | -0.15564 | -0.004578 | -0.068665 | -0.10529 | -0.018311 | -0.10986 | -0.045776 | 0.3479 | 121.8613 | -0.12817 | 121.7285 | 0.013733 | -0.050354 | -0.004578 | 0.077819 | -122.0032 | -122.1039 | 0.12817 | 0.10071 | 0.036621 | 0.022889 | -0.041198 | 0.01831 | -0.13733 | -0.27008 | 0.16022 | 0.14191 | 0.09613 | 0.1236 | 0.07782 | 0.050354 | -0.036621 | 0.14191 | 121.8567 | 0.064087 | 121.9894 | 0.14191 | 122.0078 | -122.0673 | -122.1268 | 0.041198 | 121.875 | -0.009156 | 0.49438
2104.8594 | 122.1634 | -0.09613 | 121.9849 | -0.15083 | -0.04773 | 0.0028048 | 0.025287 | 0.00086307 | -0.0088206 | -0.0028005 | -0.074127 | 0.0063787 | 0.064491 | 0.045773 | -0.015165 | 0.027835 | -0.0023755 | -0.10071 | -0.013733 | -0.041199 | -0.064087 | 0.036621 | -0.068665 | -0.004578 | 0.37079 | 121.875 | -0.11902 | 121.788 | 0.054932 | 0.004578 | 0.054932 | 0.054931 | -121.9986 | -122.049 | 0.13275 | 0.091552 | 0.027465 | 0.036621 | -0.027466 | -0.022889 | -0.10986 | -0.19684 | 0.15106 | 0.15106 | 0.10071 | 0.17395 | 0.1236 | 0.07782 | -0.022888 | 0.17395 | 121.907 | 0.027466 | 121.994 | 0.082397 | 121.9711 | -122.0261 | -122.1039 | 0.032043 | 121.8842 | -0.004578 | 0.46692
2106.6094 | 122.2321 | -0.10071 | 121.9757 | -0.17372 | -0.046234 | 0.0030184 | 0.023791 | -0.0038367 | -0.010316 | -0.0021597 | -0.0069885 | 0.0031745 | 0.064063 | 0.040646 | -0.01602 | 0.025912 | -0.0053661 | -0.082397 | -0.041199 | -0.004578 | 0.032043 | 0.13275 | 0.022888 | 0.082397 | 0.49439 | 121.8613 | -0.09613 | 121.8384 | 0.13275 | 0.09613 | 0.086975 | 0.09613 | -122.0169 | -121.9437 | 0.23346 | 0.18311 | 0.1236 | 0.086975 | 0.027466 | 0.004578 | -0.11444 | -0.13733 | 0.23346 | 0.18768 | 0.19684 | 0.1831 | 0.19226 | 0.13733 | 0.036621 | 0.22888 | 121.9345 | -0.036621 | 121.9574 | 0.059509 | 121.962 | -121.9803 | -122.0718 | 0.13275 | 121.9391 | 0.018311 | 0.59509
2108.3594 | 122.2275 | -0.07782 | 121.9482 | -0.1432 | -0.045594 | 0.0045138 | 0.02785 | -0.00020513 | -0.006898 | -0.0064321 | -0.068024 | 0.0050971 | 0.0662 | 0.048337 | -0.015806 | 0.029117 | -0.0051525 | -0.10071 | -0.041199 | -0.054932 | -0.022888 | 0.091553 | -0.059509 | 0.018311 | 0.31586 | 121.8201 | -0.086975 | 121.8613 | 0.11444 | 0.054932 | 0.14191 | 0.022888 | -121.9894 | -121.9711 | 0.16937 | 0.096131 | 0.018311 | 0.073243 | -0.004577 | -0.009155 | -0.12817 | -0.086975 | 0.19226 | 0.21973 | 0.13275 | 0.22888 | 0.14191 | 0.14649 | 0.032044 | 0.20142 | 121.9482 | 0.013733 | 121.907 | 0.036621 | 121.8979 | -122.0032 | -122.0352 | 0.054932 | 121.9391 | -0.022888 | 0.39368
2110.125 | 122.1359 | -0.12817 | 122.0306 | -0.10506 | -0.044739 | 0.0051546 | 0.029986 | 0.0036401 | -0.0092478 | -0.0038687 | -0.11075 | 0.0080877 | 0.065132 | 0.053464 | -0.015379 | 0.029117 | -0.0036573 | -0.10071 | -0.027466 | -0.032043 | -0.054932 | 0.027466 | -0.09613 | -0.018311 | 0.32959 | 121.8613 | -0.09613 | 121.756 | 0.032043 | -0.045776 | 0.009155 | 0.096131 | -122.0581 | -122.0856 | 0.15564 | 0.10986 | 0.032044 | 0.013732 | -0.064087 | 0.032044 | -0.16937 | -0.27466 | 0.16022 | 0.13733 | 0.082398 | 0.10528 | 0.050354 | 0.059509 | -0.022889 | 0.12817 | 121.8521 | 0.004577 | 121.9574 | 0.10071 | 121.9894 | -122.0627 | -122.1268 | 0.073242 | 121.8842 | 0.027466 | 0.45776
2111.8281 | 122.2412 | -0.082397 | 121.9849 | -0.13557 | -0.045594 | 0.0043002 | 0.025073 | -0.00063233 | -0.0073252 | -0.0028005 | -0.064972 | 0.0063787 | 0.062782 | 0.053677 | -0.01666 | 0.028262 | -0.0038709 | -0.09613 | -0.045776 | -0.022888 | -0.009155 | 0.086975 | -0.073242 | 0.013733 | 0.32501 | 121.8475 | -0.09613 | 121.8475 | 0.11902 | 0.07782 | 0.13275 | 0.059509 | -122.0306 | -121.994 | 0.16937 | 0.09613 | 0.009155 | 0.036621 | -0.050354 | -0.013733 | -0.13733 | -0.13733 | 0.20142 | 0.21515 | 0.16022 | 0.22888 | 0.17395 | 0.10986 | 0.013733 | 0.21515 | 121.9437 | -0.022888 | 121.9437 | 0.036621 | 121.9299 | -122.0078 | -122.081 | 0.073242 | 121.9299 | -0.013733 | 0.40741
2113.5781 | 122.2366 | -0.091553 | 121.9894 | -0.11269 | -0.047943 | 0.0034456 | 0.026141 | -0.0029821 | -0.01117 | -0.0040823 | 0.014374 | 0.0033881 | 0.065772 | 0.041073 | -0.014311 | 0.027194 | -0.0023755 | -0.10986 | -0.036621 | -0.041199 | -0.027466 | 0.09613 | -0.027466 | 0.045776 | 0.41199 | 121.8201 | -0.10071 | 121.8475 | 0.14191 | 0.11902 | 0.11444 | 0.050354 | -122.0261 | -122.0169 | 0.18768 | 0.13733 | 0.064087 | 0.086975 | 0.013733 | -0.009155 | -0.16937 | -0.14191 | 0.23346 | 0.20599 | 0.21057 | 0.21515 | 0.21973 | 0.13733 | 0.013733 | 0.24262 | 121.9482 | 0.004578 | 121.9208 | 0.054932 | 121.9116 | -122.0306 | -122.0901 | 0.064087 | 121.9391 | -0.01831 | 0.50354
2115.3438 | 122.1176 | -0.13733 | 121.9986 | -0.16609 | -0.044739 | 0.0034456 | 0.028064 | 0.0029993 | -0.0064706 | -0.0047231 | -0.1077 | 0.0070197 | 0.062354 | 0.0509 | -0.016874 | 0.025912 | -0.0038709 | -0.15564 | -0.022888 | -0.07782 | -0.11902 | -0.064087 | -0.15106 | -0.073242 | 0.19684 | 121.875 | -0.13275 | 121.7514 | -0.027466 | -0.064087 | 0 | 0.059509 | -122.0215 | -122.1176 | 0.073242 | 0.064087 | -0.013733 | 0.004578 | -0.073242 | 0.004578 | -0.1236 | -0.24719 | 0.10986 | 0.13733 | 0.073242 | 0.13275 | 0.068664 | 0.013733 | -0.041199 | 0.10529 | 121.8842 | 0.054932 | 122.0078 | 0.11444 | 122.0123 | -122.0764 | -122.1313 | 0.01831 | 121.8887 | -0.018311 | 0.33417
2117.1094 | 122.1268 | -0.1236 | 122.049 | -0.06691 | -0.045807 | 0.0034456 | 0.02785 | 0.0049219 | -0.0075388 | -0.0017325 | -0.10464 | 0.0053107 | 0.065986 | 0.056881 | -0.015806 | 0.026553 | -0.0028027 | -0.14191 | -0.013733 | -0.064087 | -0.12817 | -0.050354 | -0.16479 | -0.07782 | 0.20599 | 121.8842 | -0.11444 | 121.7514 | -0.013733 | -0.064087 | 0.004578 | 0.059509 | -122.0627 | -122.1771 | 0.073242 | 0.045776 | -0.041199 | -0.013733 | -0.10071 | 0.009155 | -0.16479 | -0.29755 | 0.10986 | 0.12817 | 0.059509 | 0.11902 | 0.050354 | 0.013733 | -0.064087 | 0.10071 | 121.8658 | 0.050354 | 121.9986 | 0.10986 | 122.0078 | -122.113 | -122.1634 | -0.004578 | 121.875 | -0.018311 | 0.32959
2118.7969 | 122.1817 | -0.12817 | 122.0123 | -0.12032 | -0.044953 | 0.003232 | 0.02785 | 0.00022207 | -0.0088206 | -0.00045074 | -0.071076 | 0.0057379 | 0.067054 | 0.047696 | -0.015379 | 0.027835 | -0.0032299 | -0.10986 | -0.036621 | -0.064087 | -0.050354 | 0.045776 | -0.073242 | 0 | 0.37079 | 121.8796 | -0.1236 | 121.788 | 0.054932 | -0.004578 | 0.041199 | 0.064087 | -122.0489 | -122.0627 | 0.17395 | 0.12817 | 0.054932 | 0.064087 | -0.009155 | 0.004578 | -0.13275 | -0.2243 | 0.18311 | 0.16937 | 0.1236 | 0.16479 | 0.11902 | 0.10986 | 0.013733 | 0.17853 | 121.9116 | 0.027466 | 122.0032 | 0.091553 | 122.0078 | -122.0764 | -122.1359 | 0.07782 | 121.9162 | 0.018311 | 0.49896
2120.5469 | 122.2595 | -0.086975 | 121.9711 | -0.15083 | -0.043244 | 0.0043002 | 0.025927 | 0.00064947 | -0.0081796 | -0.0030141 | -0.025299 | 0.0050971 | 0.064277 | 0.051327 | -0.014524 | 0.025485 | -0.0062207 | -0.068665 | -0.073242 | -0.004578 | 0.018311 | 0.13733 | -0.032043 | 0.045776 | 0.36163 | 121.8246 | -0.07782 | 121.8613 | 0.12817 | 0.086975 | 0.12817 | 0.082397 | -122.0444 | -121.9528 | 0.2243 | 0.13275 | 0.054932 | 0.050354 | -0.027465 | 0.009155 | -0.14648 | -0.10986 | 0.21515 | 0.21515 | 0.17395 | 0.20599 | 0.16479 | 0.14191 | 0.022889 | 0.20599 | 121.9391 | -0.068664 | 121.9025 | 0.013733 | 121.9116 | -121.9757 | -122.049 | 0.10529 | 121.9482 | 0.01831 | 0.44861
2122.3125 | 122.1451 | -0.11902 | 122.0398 | -0.10506 | -0.04303 | 0.005582 | 0.02785 | -0.0010595 | -0.0098886 | -0.0030141 | -0.10464 | 0.0068059 | 0.062568 | 0.047482 | -0.017515 | 0.02869 | -0.0013073 | -0.10529 | -0.027466 | -0.045776 | -0.073242 | 0.022888 | -0.11444 | -0.027466 | 0.32959 | 121.8796 | -0.10071 | 121.7651 | -0.013733 | -0.054932 | 0.018311 | 0.073243 | -122.0673 | -122.113 | 0.14191 | 0.091553 | 0.004578 | 0.01831 | -0.068665 | 0.018311 | -0.16022 | -0.27466 | 0.10529 | 0.13733 | 0.064087 | 0.11902 | 0.045776 | 0.068664 | -0.027466 | 0.086975 | 121.8658 | 0.01831 | 121.9803 | 0.091553 | 121.9986 | -122.0856 | -122.1405 | 0.045777 | 121.8842 | 0.013733 | 0.44861
2124 | 122.2183 | -0.10986 | 121.994 | -0.13557 | -0.043885 | 0.00045503 | 0.025073 | -0.0029821 | -0.009675 | -0.0034415 | 0.0052185 | 0.0061651 | 0.065559 | 0.051541 | -0.013456 | 0.026553 | -0.0047253 | -0.13733 | -0.059509 | -0.018311 | -0.059509 | 0.050354 | -0.073242 | 0.009155 | 0.31128 | 121.8567 | -0.10986 | 121.7972 | 0.064087 | 0.041199 | 0.07782 | 0.091552 | -122.0535 | -122.0535 | 0.16022 | 0.11902 | 0.036621 | 0.027466 | -0.054931 | 0 | -0.13733 | -0.19684 | 0.17395 | 0.18768 | 0.15106 | 0.18768 | 0.15106 | 0.068665 | -0.041198 | 0.17395 | 121.907 | -0.041198 | 121.9666 | 0.050354 | 121.9666 | -122.0123 | -122.1039 | 0.050354 | 121.907 | -0.027466 | 0.42114
2125.75 | 122.2366 | -0.07782 | 122.0078 | -0.20424 | -0.044098 | 0.0062228 | 0.026355 | 8.47e-06 | -0.006898 | -0.0032277 | -0.037506 | 0.0050971 | 0.066627 | 0.04855 | -0.01602 | 0.028049 | -0.0064343 | -0.073242 | -0.064087 | -0.009155 | 0.018311 | 0.10986 | -0.032043 | 0.045776 | 0.3479 | 121.8567 | -0.086975 | 121.8658 | 0.12817 | 0.09613 | 0.13275 | 0.068665 | -122.0718 | -121.9894 | 0.18768 | 0.1236 | 0.045777 | 0.054931 | -0.022888 | -0.009155 | -0.15106 | -0.14191 | 0.20599 | 0.21057 | 0.17395 | 0.21973 | 0.1831 | 0.11902 | 0.027466 | 0.21515 | 121.9528 | -0.054932 | 121.9437 | 0.013733 | 121.9345 | -122.0169 | -122.0947 | 0.096131 | 121.9437 | 0.004578 | 0.42572
2127.5 | 122.168 | -0.14191 | 122.0398 | -0.082169 | -0.044739 | 0.0019504 | 0.027209 | 0.0012903 | -0.0081796 | -0.00045074 | -0.12296 | 0.0061651 | 0.064277 | 0.059872 | -0.015379 | 0.027621 | -0.00045291 | -0.10986 | -0.022888 | -0.059509 | -0.064087 | 0.045776 | -0.082397 | -0.009155 | 0.37079 | 121.9116 | -0.10071 | 121.788 | 0.036621 | -0.027466 | 0.041199 | 0.082398 | -122.0627 | -122.1039 | 0.18768 | 0.13275 | 0.05951 | 0.050354 | -0.022888 | 0.041199 | -0.12817 | -0.25177 | 0.17853 | 0.18311 | 0.11444 | 0.14191 | 0.073242 | 0.10528 | -0.004578 | 0.13733 | 121.8887 | 0.036621 | 122.0123 | 0.11902 | 122.0535 | -122.0993 | -122.1405 | 0.07782 | 121.9299 | 0.032044 | 0.5127
2129.25 | 122.2458 | -0.091553 | 122.0444 | -0.097427 | -0.048157 | 0.0019504 | 0.025287 | -0.00063233 | -0.01117 | -0.0030141 | 0.020477 | 0.0031745 | 0.065772 | 0.048764 | -0.016447 | 0.026553 | -0.0060071 | -0.082397 | -0.064087 | -0.018311 | 0.022888 | 0.15106 | 0.013733 | 0.07782 | 0.50812 | 121.8567 | -0.09613 | 121.8567 | 0.14191 | 0.11902 | 0.10986 | 0.073242 | -122.1085 | -122.0215 | 0.24261 | 0.16937 | 0.10529 | 0.096131 | 0.032044 | -0.004577 | -0.18768 | -0.18768 | 0.23346 | 0.20142 | 0.21057 | 0.20599 | 0.21515 | 0.16937 | 0.041199 | 0.23804 | 121.9528 | -0.045776 | 121.9528 | 0.027466 | 121.9482 | -122.0627 | -122.1405 | 0.11444 | 121.9482 | 0.009156 | 0.59967
2130.9531 | 122.1451 | -0.13275 | 122.0398 | -0.11269 | -0.041107 | 0.0062228 | 0.026782 | -0.0042639 | -0.007966 | -0.0028005 | -0.1077 | 0.0036017 | 0.062354 | 0.04855 | -0.014951 | 0.027621 | -0.0030163 | -0.15106 | -0.004578 | -0.059509 | -0.12817 | -0.059509 | -0.16022 | -0.07782 | 0.1831 | 121.8979 | -0.1236 | 121.7606 | -0.018311 | -0.068665 | 0.004578 | 0.073242 | -122.0444 | -122.168 | 0.073242 | 0.054931 | -0.027466 | -0.018311 | -0.10071 | 0.009155 | -0.14191 | -0.27924 | 0.11444 | 0.13733 | 0.064086 | 0.12817 | 0.054931 | 0 | -0.068665 | 0.10528 | 121.8842 | 0.054931 | 122.0215 | 0.12817 | 122.0306 | -122.0993 | -122.1634 | 0.004577 | 121.8933 | -0.018311 | 0.31586
2132.7031 | 122.1222 | -0.13733 | 122.0444 | -0.11269 | -0.045594 | 0.0030184 | 0.026141 | -0.0046911 | -0.0081796 | -0.0047231 | -0.049713 | 0.0059515 | 0.0615 | 0.056668 | -0.014097 | 0.02933 | -0.0028027 | -0.16022 | -0.041199 | -0.036621 | -0.09613 | -0.009155 | -0.11444 | -0.027466 | 0.37079 | 121.9208 | -0.11902 | 121.7468 | 0.004578 | -0.045776 | -0.009155 | 0.10071 | -122.0856 | -122.1405 | 0.12817 | 0.10986 | 0.022888 | 0.009155 | -0.07782 | 0.01831 | -0.1236 | -0.29755 | 0.14191 | 0.12817 | 0.091553 | 0.10986 | 0.073243 | 0.027466 | -0.059509 | 0.1236 | 121.8658 | -0.004578 | 122.0398 | 0.09613 | 122.0581 | -122.081 | -122.1634 | 0.041199 | 121.8842 | -0.022888 | 0.50812
2134.4531 | 122.2824 | -0.086975 | 122.0123 | -0.12032 | -0.046448 | 0.00088223 | 0.021869 | 0.00043587 | -0.0090342 | -0.0049367 | -0.0069885 | 0.0061651 | 0.064063 | 0.044919 | -0.014951 | 0.026126 | -0.0068615 | -0.091553 | -0.059509 | -0.027466 | 0.004578 | 0.13275 | 0.009155 | 0.091553 | 0.46692 | 121.8521 | -0.09613 | 121.8842 | 0.13733 | 0.13275 | 0.12817 | 0.059509 | -122.0718 | -122.0078 | 0.21973 | 0.17853 | 0.09613 | 0.11902 | 0.036621 | -0.009155 | -0.16022 | -0.12817 | 0.2243 | 0.21515 | 0.21973 | 0.2243 | 0.22888 | 0.16022 | 0.032044 | 0.23346 | 121.9803 | -0.032043 | 121.9482 | 0.027466 | 121.9391 | -122.0398 | -122.1085 | 0.091553 | 121.9711 | -0.004578 | 0.55389
2136.2188 | 122.1451 | -0.1236 | 122.0261 | -0.1432 | -0.044098 | 0.003873 | 0.029132 | -0.00084593 | -0.011598 | -0.0015189 | -0.083283 | 0.0057379 | 0.067268 | 0.054104 | -0.017301 | 0.026553 | -0.0053661 | -0.14648 | -0.013733 | -0.073242 | -0.11444 | -0.054932 | -0.17395 | -0.07782 | 0.20599 | 121.907 | -0.10529 | 121.7789 | -0.009155 | -0.059509 | 0.004578 | 0.050354 | -122.0398 | -122.1405 | 0.068664 | 0.045776 | -0.050354 | -0.004578 | -0.10071 | 0.01831 | -0.11902 | -0.24719 | 0.11444 | 0.12817 | 0.064087 | 0.10986 | 0.045777 | 0.01831 | -0.041199 | 0.096131 | 121.8842 | 0.059509 | 122.0123 | 0.10986 | 122.0306 | -122.0993 | -122.1313 | 0.009155 | 121.9025 | -0.022888 | 0.32959
2137.9062 | 122.2733 | -0.091553 | 121.994 | -0.15083 | -0.047943 | 0.003232 | 0.025927 | 0.00064947 | -0.012025 | -0.0062185 | -0.01004 | 0.0046697 | 0.065345 | 0.05325 | -0.015379 | 0.026126 | -0.0053661 | -0.086975 | -0.036621 | -0.018311 | 0.018311 | 0.14191 | 0.018311 | 0.086975 | 0.50812 | 121.8521 | -0.09613 | 121.8887 | 0.17853 | 0.12817 | 0.12817 | 0.073242 | -122.0306 | -121.9757 | 0.23346 | 0.17853 | 0.10986 | 0.10529 | 0.036622 | -0.004577 | -0.14191 | -0.10529 | 0.27008 | 0.21973 | 0.21973 | 0.2243 | 0.2243 | 0.16022 | 0.036622 | 0.27466 | 121.9849 | -0.01831 | 121.9482 | 0.054932 | 121.9437 | -122.0123 | -122.0901 | 0.10986 | 121.9803 | 0.004578 | 0.59967
2139.6406 | 122.2412 | -0.10071 | 122.0123 | -0.10506 | -0.042389 | 0.0028048 | 0.025287 | -0.0019141 | -0.0088206 | -0.0040823 | -0.0008851 | 0.0050971 | 0.064704 | 0.057309 | -0.016447 | 0.02634 | -0.0057935 | -0.086975 | -0.041199 | -0.009155 | 0.013733 | 0.11902 | 0 | 0.068665 | 0.49439 | 121.8613 | -0.09613 | 121.8521 | 0.1236 | 0.086975 | 0.10529 | 0.091553 | -122.0535 | -121.9986 | 0.21973 | 0.16937 | 0.10071 | 0.07782 | 0.009155 | 0.004578 | -0.15106 | -0.16022 | 0.2243 | 0.20599 | 0.18768 | 0.20142 | 0.1831 | 0.12817 | 0.022888 | 0.21973 | 121.9482 | -0.032044 | 121.9574 | 0.059509 | 121.962 | -122.0215 | -122.1085 | 0.11444 | 121.9528 | 0.013733 | 0.59509
2141.3906 | 122.1222 | -0.14191 | 122.0398 | -0.11269 | -0.047089 | 0.0017368 | 0.024859 | -0.0010595 | -0.010743 | -0.0053641 | -0.058869 | 0.0040289 | 0.065345 | 0.048977 | -0.01666 | 0.026126 | -0.0057935 | -0.15564 | -0.032043 | -0.054932 | -0.10529 | -0.022888 | -0.10529 | -0.027466 | 0.35706 | 121.9208 | -0.11444 | 121.7468 | 0 | -0.041199 | 0.004578 | 0.086975 | -122.0718 | -122.1451 | 0.11902 | 0.11444 | 0.036621 | 0.027466 | -0.050354 | 0.027466 | -0.11902 | -0.29297 | 0.14191 | 0.14649 | 0.10071 | 0.11902 | 0.073242 | 0.032044 | -0.050354 | 0.11444 | 121.8613 | 0.022889 | 122.0352 | 0.10986 | 122.0627 | -122.0947 | -122.1542 | 0.036621 | 121.8887 | -0.013733 | 0.49896
2143.1562 | 122.2549 | -0.086975 | 122.0169 | -0.11269 | -0.048798 | 0.00045503 | 0.026568 | 0.0010767 | -0.010957 | -0.0021597 | 0.011322 | 0.0070197 | 0.063636 | 0.046414 | -0.01602 | 0.026767 | -0.0015209 | -0.068665 | -0.059509 | -0.009155 | 0.027466 | 0.13733 | 0.027466 | 0.07782 | 0.49439 | 121.843 | -0.07782 | 121.875 | 0.16022 | 0.11902 | 0.13733 | 0.07782 | -122.0764 | -121.9894 | 0.2243 | 0.16479 | 0.11444 | 0.086975 | 0.036621 | 0.009155 | -0.17395 | -0.14191 | 0.24719 | 0.2243 | 0.20599 | 0.21515 | 0.19684 | 0.14648 | 0.036621 | 0.23804 | 121.9528 | -0.050354 | 121.9208 | 0.027466 | 121.9299 | -122.0261 | -122.0947 | 0.11444 | 121.962 | 0.01831 | 0.58136
2144.8438 | 122.2778 | -0.07782 | 122.0215 | -0.18135 | -0.043671 | 0.005582 | 0.02785 | -0.0046911 | -0.008607 | -0.0028005 | -0.080231 | 0.0042425 | 0.061714 | 0.05795 | -0.015165 | 0.028476 | -0.0049389 | -0.10071 | -0.054932 | -0.022888 | -0.022888 | 0.073242 | -0.050354 | 0.032043 | 0.33417 | 121.8658 | -0.086975 | 121.8887 | 0.1236 | 0.068665 | 0.14191 | 0.054932 | -122.0764 | -122.0444 | 0.15106 | 0.10986 | 0.027466 | 0.054931 | -0.027466 | -0.009155 | -0.15564 | -0.13275 | 0.20142 | 0.21973 | 0.14649 | 0.22888 | 0.15564 | 0.09613 | 0 | 0.21057 | 121.9757 | -0.032044 | 121.9528 | 0.022888 | 121.9437 | -122.0444 | -122.1085 | 0.054932 | 121.9666 | -0.022888 | 0.41199
2146.6094 | 122.168 | -0.11902 | 122.0444 | -0.11269 | -0.045166 | 0.003873 | 0.026355 | -0.0046911 | -0.012025 | -0.0021597 | -0.025299 | 0.0061651 | 0.063209 | 0.045773 | -0.014738 | 0.025699 | -0.0023755 | -0.091553 | -0.045776 | -0.032043 | -0.045776 | 0.054932 | -0.050354 | 0.018311 | 0.41657 | 121.9025 | -0.11444 | 121.7789 | 0.027466 | -0.004578 | 0.009155 | 0.086976 | -122.0901 | -122.0901 | 0.17395 | 0.13733 | 0.068665 | 0.050354 | -0.018311 | 0.004578 | -0.14191 | -0.2655 | 0.14649 | 0.12817 | 0.11444 | 0.1236 | 0.10986 | 0.086975 | -0.013733 | 0.14191 | 121.8933 | -0.013733 | 122.0169 | 0.073243 | 122.0215 | -122.0764 | -122.1588 | 0.073243 | 121.8979 | 0.027466 | 0.53558
2148.375 | 122.2137 | -0.086975 | 122.0398 | -0.10506 | -0.049012 | 0.0025912 | 0.023364 | -0.0044775 | -0.0094614 | -0.0049367 | -0.04361 | 0.0050971 | 0.063423 | 0.0509 | -0.01602 | 0.02634 | -0.0053661 | -0.086975 | -0.059509 | -0.018311 | 0.018311 | 0.10529 | -0.009155 | 0.064087 | 0.48523 | 121.8658 | -0.07782 | 121.8384 | 0.11902 | 0.086975 | 0.10071 | 0.068664 | -122.0993 | -122.0215 | 0.19226 | 0.15106 | 0.07782 | 0.082398 | 0.009156 | 0.009155 | -0.17395 | -0.20142 | 0.20599 | 0.18768 | 0.17395 | 0.17853 | 0.16479 | 0.1236 | 0.036622 | 0.19684 | 121.9162 | -0.041198 | 121.9437 | 0.027466 | 121.9528 | -122.0581 | -122.1176 | 0.10529 | 121.9254 | 0 | 0.5722
2150.0625 | 122.2321 | -0.082397 | 121.9803 | -0.17372 | -0.045807 | 0.0030184 | 0.024646 | -0.0017005 | -0.010102 | -0.0068593 | -0.013092 | 0.0053107 | 0.063423 | 0.041501 | -0.015806 | 0.026126 | -0.0055799 | -0.13275 | -0.054932 | -0.041199 | -0.045776 | 0.054932 | -0.059509 | 0.022888 | 0.3479 | 121.8704 | -0.10071 | 121.8475 | 0.10529 | 0.068665 | 0.082397 | 0.041198 | -122.0352 | -122.0261 | 0.13733 | 0.10528 | 0.022888 | 0.064087 | -0.01831 | -0.018311 | -0.10986 | -0.13275 | 0.18768 | 0.16479 | 0.15106 | 0.18311 | 0.16937 | 0.096131 | -0.004577 | 0.20599 | 121.9482 | -0.013733 | 121.9711 | 0.027465 | 121.9528 | -122.0215 | -122.081 | 0.036621 | 121.9299 | -0.050354 | 0.4303
2151.8125 | 122.2046 | -0.10529 | 122.0261 | -0.1432 | -0.044098 | 0.0043002 | 0.028491 | 0.0017175 | -0.01053 | -0.0051505 | -0.12296 | 0.0044561 | 0.063423 | 0.050473 | -0.017515 | 0.028476 | -0.0032299 | -0.15106 | -0.027466 | -0.050354 | -0.10071 | -0.027466 | -0.15106 | -0.041199 | 0.2243 | 121.8658 | -0.10071 | 121.8201 | 0.041199 | -0.009155 | 0.059509 | 0.054932 | -122.0535 | -122.1268 | 0.07782 | 0.064087 | -0.045776 | 0.009155 | -0.10071 | 0.004578 | -0.16022 | -0.20599 | 0.14649 | 0.16479 | 0.096131 | 0.16022 | 0.091553 | 0.022888 | -0.050354 | 0.14191 | 121.9208 | 0.022888 | 121.9666 | 0.07782 | 121.9711 | -122.0764 | -122.1268 | 0.004578 | 121.9254 | -0.045776 | 0.32959
2153.5938 | 122.2229 | -0.10071 | 122.0306 | -0.1432 | -0.046234 | 0.0047274 | 0.0255 | -0.0017005 | -0.0098886 | -0.0038687 | -0.040558 | 0.0044561 | 0.065986 | 0.052182 | -0.017942 | 0.027194 | -0.0060071 | -0.086975 | -0.07782 | -0.027466 | 0.032043 | 0.12817 | 0 | 0.054932 | 0.47607 | 121.9025 | -0.10529 | 121.8613 | 0.11444 | 0.07782 | 0.09613 | 0.073242 | -122.1085 | -121.9986 | 0.22888 | 0.15564 | 0.10071 | 0.082398 | 0.027466 | -0.004578 | -0.12817 | -0.16937 | 0.21515 | 0.19684 | 0.17853 | 0.20142 | 0.18311 | 0.15564 | 0.059509 | 0.21973 | 121.9666 | -0.050354 | 122.0078 | 0.022888 | 122.0032 | -122.0581 | -122.1359 | 0.13275 | 121.962 | 0.013733 | 0.57678
2155.2656 | 122.2321 | -0.09613 | 122.0078 | -0.15083 | -0.046021 | 0.0030184 | 0.025073 | -0.0012731 | -0.0092478 | -0.0038687 | -0.046661 | 0.0059515 | 0.064277 | 0.044919 | -0.014951 | 0.027621 | -0.0055799 | -0.10071 | -0.045776 | -0.018311 | -0.027466 | 0.059509 | -0.064087 | 0.018311 | 0.32501 | 121.8887 | -0.10071 | 121.8521 | 0.086975 | 0.054932 | 0.073242 | 0.077819 | -122.0535 | -122.0352 | 0.15564 | 0.11444 | 0.032043 | 0.036622 | -0.045776 | -0.004578 | -0.11902 | -0.15564 | 0.1831 | 0.16937 | 0.15106 | 0.17395 | 0.15564 | 0.07782 | -0.009155 | 0.18768 | 121.9528 | -0.027465 | 121.9894 | 0.050354 | 121.9849 | -122.0261 | -122.1085 | 0.068664 | 121.9482 | -0.004578 | 0.42114
2157.0156 | 122.1771 | -0.10986 | 122.0261 | -0.10506 | -0.044525 | 0.0043002 | 0.027423 | -0.00041873 | -0.0081796 | -0.0032277 | -0.12906 | 0.0059515 | 0.061714 | 0.051541 | -0.01666 | 0.02869 | -2.571e-05 | -0.086975 | -0.013733 | -0.045776 | -0.045776 | 0.041199 | -0.07782 | -0.013733 | 0.3891 | 121.9254 | -0.10986 | 121.8384 | 0.064087 | 0.018311 | 0.068665 | 0.064087 | -122.0398 | -122.0718 | 0.15106 | 0.09613 | 0.032043 | 0.032043 | -0.032044 | 0 | -0.10071 | -0.18768 | 0.17395 | 0.17853 | 0.12817 | 0.17853 | 0.12817 | 0.086975 | 0 | 0.17395 | 121.9482 | 0.032043 | 122.0352 | 0.09613 | 122.0352 | -122.0718 | -122.1359 | 0.064087 | 121.9482 | 0.022888 | 0.49896
2158.7188 | 122.1542 | -0.14191 | 122.0718 | -0.12794 | -0.046234 | 0.0047274 | 0.025287 | -0.0053321 | -0.008607 | -0.0023733 | -0.028351 | 0.0063787 | 0.064918 | 0.050259 | -0.014951 | 0.02634 | -0.0045117 | -0.12817 | -0.050354 | -0.036621 | -0.07782 | 0.027466 | -0.086975 | -0.018311 | 0.37994 | 121.9025 | -0.11444 | 121.7834 | 0.027466 | -0.013733 | -0.004578 | 0.10529 | -122.1222 | -122.1497 | 0.16937 | 0.1236 | 0.054932 | 0.01831 | -0.050354 | 0.027466 | -0.16937 | -0.28839 | 0.16937 | 0.13733 | 0.12817 | 0.10986 | 0.10071 | 0.064087 | -0.041199 | 0.14191 | 121.8979 | -0.013733 | 122.0169 | 0.091553 | 122.0444 | -122.1085 | -122.1863 | 0.064087 | 121.9254 | 0.013733 | 0.52185
2160.4688 | 122.2321 | -0.082397 | 122.0352 | -0.12794 | -0.044525 | 0.0025912 | 0.026141 | -0.00084593 | -0.0077524 | -0.00087794 | -0.037506 | 0.0050971 | 0.063209 | 0.052395 | -0.015806 | 0.026767 | -0.0049389 | -0.11902 | -0.059509 | -0.036621 | -0.041199 | 0.050354 | -0.059509 | 0.022888 | 0.31128 | 121.8796 | -0.086975 | 121.8338 | 0.068665 | 0.032043 | 0.073242 | 0.045776 | -122.0947 | -122.0764 | 0.13275 | 0.10528 | 0.022888 | 0.059509 | -0.022888 | -0.004578 | -0.15564 | -0.20142 | 0.15106 | 0.15564 | 0.11444 | 0.16022 | 0.11902 | 0.086975 | -0.004578 | 0.15564 | 121.9208 | -0.022888 | 121.9666 | 0.022888 | 121.962 | -122.0718 | -122.1222 | 0.041198 | 121.9162 | -0.036622 | 0.39368
2162.2344 | 122.2458 | -0.091553 | 122.0306 | -0.1432 | -0.044953 | 0.0036594 | 0.025073 | -0.00041873 | -0.0092478 | -0.0053641 | -0.034454 | 0.0057379 | 0.062782 | 0.048764 | -0.017088 | 0.025272 | -0.0055799 | -0.10071 | -0.07782 | -0.009155 | 0.009155 | 0.1236 | -0.041199 | 0.045776 | 0.34332 | 121.875 | -0.082397 | 121.8658 | 0.082397 | 0.059509 | 0.091553 | 0.082398 | -122.1085 | -122.0215 | 0.21515 | 0.13733 | 0.050354 | 0.054931 | -0.032044 | 0.009156 | -0.15564 | -0.1648 | 0.17395 | 0.18311 | 0.15106 | 0.17395 | 0.14191 | 0.13275 | 0.01831 | 0.16479 | 121.9482 | -0.068665 | 121.9574 | 0.013733 | 121.9666 | -122.0398 | -122.113 | 0.10071 | 121.9574 | -0.009155 | 0.43488
2164 | 122.2824 | -0.07782 | 122.0398 | -0.12032 | -0.044312 | 0.0045138 | 0.026355 | -0.0029821 | -0.0071116 | -0.0032277 | -0.013092 | 0.0053107 | 0.063209 | 0.047482 | -0.01602 | 0.027408 | -0.0030163 | -0.10986 | -0.064087 | -0.022888 | 0 | 0.11902 | 0 | 0.073242 | 0.46692 | 121.8796 | -0.091553 | 121.8979 | 0.16022 | 0.11902 | 0.12817 | 0.054932 | -122.1039 | -122.0398 | 0.19684 | 0.15106 | 0.07782 | 0.09613 | 0.022888 | -0.013733 | -0.16022 | -0.14191 | 0.23804 | 0.20599 | 0.19684 | 0.21973 | 0.21057 | 0.14191 | 0.022888 | 0.25177 | 121.9894 | -0.041199 | 121.9711 | 0.013733 | 121.9574 | -122.0627 | -122.1313 | 0.07782 | 121.9757 | -0.032043 | 0.54474
2165.7031 | 122.2641 | -0.091553 | 122.0032 | -0.05928 | -0.046021 | 0.0023776 | 0.0255 | -0.0012731 | -0.010316 | 0.0012583 | -0.022247 | 0.0036017 | 0.063636 | 0.050473 | -0.015592 | 0.02634 | -0.0066479 | -0.086975 | -0.054932 | -0.013733 | 0.050354 | 0.14648 | 0.009155 | 0.054932 | 0.51727 | 121.8842 | -0.091553 | 121.9025 | 0.14191 | 0.11902 | 0.1236 | 0.07782 | -122.0581 | -121.9528 | 0.23804 | 0.14649 | 0.10071 | 0.068665 | 0.022888 | 0 | -0.11902 | -0.10071 | 0.23346 | 0.21515 | 0.21057 | 0.21515 | 0.21057 | 0.16022 | 0.064087 | 0.23346 | 121.994 | -0.041199 | 121.9757 | 0.036621 | 121.9757 | -122.0169 | -122.0947 | 0.14191 | 121.994 | 0.004578 | 0.60883
2167.4531 | 122.2916 | -0.068665 | 122.0078 | -0.15846 | -0.043457 | 0.004941 | 0.029773 | -0.0014867 | -0.0088206 | -0.0045095 | -0.09549 | 0.0065923 | 0.065772 | 0.058377 | -0.017301 | 0.026981 | -0.0040845 | -0.068665 | -0.054932 | -0.036621 | 0.009155 | 0.09613 | -0.027466 | 0.027466 | 0.33875 | 121.8933 | -0.068665 | 121.9254 | 0.13275 | 0.09613 | 0.14191 | 0.032044 | -122.0627 | -121.9986 | 0.16479 | 0.096131 | 0.041199 | 0.064087 | 0.009155 | 0 | -0.11444 | -0.082397 | 0.20142 | 0.21057 | 0.16479 | 0.21057 | 0.16479 | 0.13275 | 0.045776 | 0.20142 | 121.994 | -0.018311 | 121.962 | 0.013733 | 121.962 | -122.0444 | -122.0764 | 0.07782 | 121.994 | 0 | 0.40741
2169.1406 | 122.1588 | -0.12817 | 122.0627 | -0.15846 | -0.043457 | 0.0047274 | 0.026996 | 0.0032129 | -0.010743 | -0.0030141 | -0.15347 | 0.0063787 | 0.065559 | 0.049618 | -0.015165 | 0.02869 | -0.0075025 | -0.15564 | -0.013733 | -0.050354 | -0.10986 | -0.054932 | -0.16022 | -0.068665 | 0.19684 | 121.9437 | -0.1236 | 121.7926 | -0.009155 | -0.073242 | 0.013733 | 0.07782 | -122.0764 | -122.1725 | 0.073242 | 0.059509 | -0.032043 | -0.018311 | -0.10986 | 0.004578 | -0.11902 | -0.27008 | 0.11902 | 0.14191 | 0.054932 | 0.13733 | 0.050354 | -0.004578 | -0.059509 | 0.11444 | 121.9162 | 0.036621 | 122.0673 | 0.11444 | 122.0718 | -122.113 | -122.1863 | 0.018311 | 121.9208 | -0.027466 | 0.32501
2170.9062 | 122.2092 | -0.10529 | 122.081 | -0.051651 | -0.044953 | 0.0045138 | 0.026568 | -0.0014867 | -0.0094614 | -0.0036551 | -0.12906 | 0.0059515 | 0.063636 | 0.04855 | -0.014738 | 0.024844 | -0.0032299 | -0.091553 | -0.022888 | -0.050354 | -0.041199 | 0.041199 | -0.07782 | -0.018311 | 0.40741 | 121.9299 | -0.10071 | 121.8384 | 0.086975 | 0.027466 | 0.064087 | 0.054932 | -122.1039 | -122.1222 | 0.14649 | 0.086975 | 0.027466 | 0.032043 | -0.027466 | 0.004578 | -0.15106 | -0.24262 | 0.19226 | 0.16937 | 0.13275 | 0.1648 | 0.12817 | 0.091553 | 0.009155 | 0.18768 | 121.9391 | 0.027466 | 122.0306 | 0.082398 | 122.0352 | -122.1313 | -122.1817 | 0.064087 | 121.9437 | 0.013733 | 0.5127
2172.6719 | 122.1405 | -0.1236 | 122.0764 | -0.10506 | -0.043244 | 0.003232 | 0.028064 | 0.0010767 | -0.009675 | -0.0040823 | -0.11075 | 0.0078741 | 0.064491 | 0.049405 | -0.015592 | 0.029544 | -0.0036573 | -0.10986 | -0.018311 | -0.050354 | -0.082397 | 0 | -0.14191 | -0.064087 | 0.27466 | 121.9116 | -0.10071 | 121.7972 | 0.013733 | -0.064087 | 0.022888 | 0.073242 | -122.0947 | -122.1588 | 0.1236 | 0.059509 | -0.018311 | -0.013733 | -0.091553 | 0.022888 | -0.16479 | -0.27924 | 0.13733 | 0.14648 | 0.059509 | 0.1236 | 0.036621 | 0.050354 | -0.032043 | 0.11444 | 121.8979 | 0.032043 | 122.0123 | 0.10528 | 122.0352 | -122.1268 | -122.1771 | 0.041199 | 121.9208 | 0.013733 | 0.39825
2174.3594 | 122.2092 | -0.091553 | 122.0581 | -0.044022 | -0.045594 | 0.0053684 | 0.025714 | -0.0044775 | -0.009675 | -0.0036551 | -0.09549 | 0.0065923 | 0.065132 | 0.053464 | -0.014524 | 0.027194 | -0.0032299 | -0.10071 | -0.045776 | -0.032043 | -0.036621 | 0.050354 | -0.086975 | -0.013733 | 0.40283 | 121.9482 | -0.10986 | 121.8384 | 0.064087 | 0.022888 | 0.059509 | 0.05951 | -122.1039 | -122.0947 | 0.14191 | 0.07782 | 0.004578 | 0.01831 | -0.054932 | -0.01831 | -0.10986 | -0.21973 | 0.15564 | 0.15106 | 0.11444 | 0.16937 | 0.13275 | 0.082397 | -0.004578 | 0.17395 | 121.9482 | -0.013733 | 122.0581 | 0.045777 | 122.0398 | -122.0901 | -122.168 | 0.054932 | 121.9299 | -0.009155 | 0.49439
2176.125 | 122.2778 | -0.064087 | 122.0261 | -0.13557 | -0.04303 | 0.0040866 | 0.025714 | -0.00084593 | -0.0088206 | -0.0021597 | -0.080231 | 0.0057379 | 0.064063 | 0.052395 | -0.014524 | 0.026981 | -0.0025891 | -0.10071 | -0.050354 | -0.032043 | -0.018311 | 0.064087 | -0.036621 | 0.045776 | 0.32044 | 121.8842 | -0.091553 | 121.9116 | 0.13275 | 0.07782 | 0.14191 | 0.032044 | -122.0764 | -122.0444 | 0.12817 | 0.10986 | 0.027466 | 0.077819 | -0.004578 | -0.027466 | -0.14191 | -0.11444 | 0.19684 | 0.20599 | 0.14191 | 0.23346 | 0.16937 | 0.09613 | 0.013732 | 0.2243 | 122.0032 | -0.018311 | 121.9757 | 0.013733 | 121.9482 | -122.0581 | -122.1176 | 0.045776 | 121.9757 | -0.036621 | 0.38452
2177.8906 | 122.168 | -0.12817 | 122.0581 | -0.12794 | -0.043671 | 0.0036594 | 0.027636 | 0.00086307 | -0.0092478 | -0.0038687 | -0.12296 | 0.0061651 | 0.06385 | 0.049405 | -0.013456 | 0.030185 | -0.0051525 | -0.10071 | -0.036621 | -0.045776 | -0.054932 | 0.041199 | -0.086975 | -0.013733 | 0.34332 | 121.9391 | -0.091553 | 121.8292 | 0.041199 | -0.032043 | 0.027466 | 0.082398 | -122.0947 | -122.113 | 0.16937 | 0.11444 | 0.041199 | 0.032043 | -0.041199 | 0.036621 | -0.11902 | -0.22888 | 0.16937 | 0.15564 | 0.096131 | 0.11902 | 0.05951 | 0.086975 | -0.009156 | 0.13275 | 121.9208 | 0.009155 | 122.0306 | 0.091553 | 122.0673 | -122.1039 | -122.1497 | 0.073242 | 121.9574 | 0.027466 | 0.4715
2179.6406 | 122.2458 | -0.09613 | 122.0352 | -0.15846 | -0.046234 | 0.0028048 | 0.025287 | -0.0012731 | -0.0075388 | -0.0064321 | -0.0069885 | 0.0053107 | 0.062995 | 0.039578 | -0.014097 | 0.028262 | -0.0045117 | -0.12817 | -0.054932 | -0.036621 | -0.050354 | 0.050354 | -0.068665 | 0.018311 | 0.32044 | 121.907 | -0.082397 | 121.8475 | 0.07782 | 0.041199 | 0.082397 | 0.059509 | -122.0901 | -122.0856 | 0.14648 | 0.11444 | 0.027465 | 0.054932 | -0.032044 | 0.013733 | -0.12817 | -0.18768 | 0.17395 | 0.17853 | 0.13733 | 0.16479 | 0.1236 | 0.086975 | -0.013733 | 0.16022 | 121.9299 | -0.018311 | 121.9894 | 0.041198 | 122.0032 | -122.0718 | -122.1176 | 0.045776 | 121.9437 | -0.032044 | 0.41657
2181.3281 | 122.2549 | -0.07782 | 122.0444 | -0.1432 | -0.04538 | 0.004941 | 0.025287 | 8.47e-06 | -0.0077524 | -0.0032277 | -0.013092 | 0.0050971 | 0.063636 | 0.046841 | -0.01666 | 0.028049 | -0.0053661 | -0.091553 | -0.064087 | -0.018311 | -0.009155 | 0.11444 | -0.032043 | 0.036621 | 0.35706 | 121.8704 | -0.091553 | 121.8658 | 0.09613 | 0.064087 | 0.09613 | 0.059509 | -122.1085 | -122.0535 | 0.19226 | 0.11444 | 0.045777 | 0.054932 | -0.013732 | -0.013733 | -0.17395 | -0.17853 | 0.17395 | 0.17395 | 0.14191 | 0.18768 | 0.15564 | 0.13275 | 0.009156 | 0.18768 | 121.9574 | -0.045776 | 121.962 | 0.013733 | 121.9482 | -122.0627 | -122.1359 | 0.068665 | 121.9437 | -0.013733 | 0.43488
2183.0938 | 122.2687 | -0.073242 | 122.0673 | -0.13557 | -0.04773 | 0.003232 | 0.025714 | -0.0051183 | -0.0075388 | -0.0013051 | -0.013092 | 0.0053107 | 0.062782 | 0.051114 | -0.01666 | 0.026126 | -0.0081433 | -0.086975 | -0.068665 | -0.022888 | 0.009155 | 0.13275 | 0.009155 | 0.059509 | 0.5127 | 121.8796 | -0.07782 | 121.9025 | 0.14191 | 0.09613 | 0.13275 | 0.050354 | -122.1359 | -122.0581 | 0.20599 | 0.13275 | 0.082397 | 0.082397 | 0.032043 | -0.004578 | -0.18768 | -0.16479 | 0.21515 | 0.20599 | 0.16937 | 0.21057 | 0.17395 | 0.15564 | 0.032043 | 0.21973 | 121.9803 | -0.045777 | 121.9574 | 0.004577 | 121.9528 | -122.0901 | -122.1451 | 0.082397 | 121.9757 | -0.013733 | 0.58594
2184.8438 | 122.3007 | -0.068665 | 122.0123 | -0.1432 | -0.044739 | 0.004941 | 0.027209 | -0.0044775 | -0.0077524 | -0.0025869 | -0.06192 | 0.0061651 | 0.06385 | 0.046628 | -0.017301 | 0.028049 | -0.0072889 | -0.064087 | -0.082397 | -0.022888 | 0.022888 | 0.11902 | -0.013733 | 0.050354 | 0.36163 | 121.9116 | -0.073242 | 121.9254 | 0.15106 | 0.10071 | 0.14191 | 0.045777 | -122.0947 | -121.9894 | 0.18768 | 0.11902 | 0.054932 | 0.073242 | 0.009155 | -0.004577 | -0.10071 | -0.086975 | 0.21973 | 0.21057 | 0.16937 | 0.21515 | 0.17395 | 0.14191 | 0.045776 | 0.2243 | 121.9986 | -0.059509 | 121.9849 | -0.013732 | 121.9803 | -122.0352 | -122.0856 | 0.091553 | 121.994 | 0.004578 | 0.4303
2186.6094 | 122.2916 | -0.07782 | 122.0352 | -0.11269 | -0.046662 | 0.0025912 | 0.025073 | -0.0021277 | -0.01053 | -0.0040823 | -0.034454 | 0.0053107 | 0.062995 | 0.049405 | -0.01367 | 0.024204 | -0.0040845 | -0.086975 | -0.059509 | -0.036621 | 0.027466 | 0.13733 | 0.009155 | 0.068665 | 0.50812 | 121.8979 | -0.07782 | 121.9116 | 0.15106 | 0.11444 | 0.1236 | 0.041199 | -122.0947 | -122.0078 | 0.21515 | 0.14649 | 0.086975 | 0.10529 | 0.045776 | 0 | -0.13733 | -0.1236 | 0.22888 | 0.20142 | 0.19226 | 0.20142 | 0.19226 | 0.17395 | 0.064087 | 0.22888 | 121.9894 | -0.022888 | 121.9757 | 0.018311 | 121.9757 | -122.0718 | -122.113 | 0.10529 | 121.9894 | -0.009155 | 0.58594
2188.2969 | 122.1588 | -0.1236 | 122.0535 | -0.17372 | -0.044312 | 0.0034456 | 0.028064 | 0.0025721 | -0.0081796 | -0.00066434 | -0.11685 | 0.0053107 | 0.065345 | 0.052182 | -0.015165 | 0.026126 | -0.0025891 | -0.14191 | -0.013733 | -0.064087 | -0.10986 | -0.041199 | -0.15106 | -0.091553 | 0.21057 | 121.9482 | -0.1236 | 121.8155 | 0 | -0.064087 | 0.013733 | 0.059509 | -122.0673 | -122.1634 | 0.082397 | 0.032043 | -0.027466 | -0.027466 | -0.086975 | 0 | -0.10529 | -0.23804 | 0.1236 | 0.13733 | 0.059509 | 0.13733 | 0.059509 | 0.022888 | -0.045776 | 0.1236 | 121.9391 | 0.050354 | 122.0718 | 0.10986 | 122.0718 | -122.1176 | -122.1771 | 0.013733 | 121.9391 | -0.018311 | 0.33417
2190.0469 | 122.168 | -0.13275 | 122.0947 | -0.17372 | -0.045594 | 0.0053684 | 0.028491 | -0.00041873 | -0.007966 | -0.0036551 | -0.11685 | 0.0065923 | 0.065345 | 0.050046 | -0.016233 | 0.025699 | -0.0017347 | -0.15564 | -0.018311 | -0.073242 | -0.10529 | -0.059509 | -0.17395 | -0.07782 | 0.20142 | 121.9574 | -0.12817 | 121.8063 | -0.022888 | -0.068665 | 0.013733 | 0.059509 | -122.113 | -122.2 | 0.073242 | 0.054931 | -0.041199 | -0.004578 | -0.10071 | 0.004577 | -0.13733 | -0.28839 | 0.10986 | 0.14648 | 0.064086 | 0.14191 | 0.059509 | 0.013733 | -0.032044 | 0.10529 | 121.9345 | 0.054931 | 122.0856 | 0.11444 | 122.0901 | -122.168 | -122.2229 | 0.027465 | 121.9391 | -0.022889 | 0.33417
2191.7344 | 122.1817 | -0.10986 | 122.081 | -0.15846 | -0.044098 | 0.004941 | 0.0302 | 0.00043587 | -0.0083932 | -0.0047231 | -0.098541 | 0.0057379 | 0.066413 | 0.042142 | -0.014738 | 0.027621 | -0.0013073 | -0.13275 | -0.022888 | -0.050354 | -0.10529 | -0.041199 | -0.13733 | -0.068665 | 0.23346 | 121.9391 | -0.11444 | 121.8246 | 0.009155 | -0.041199 | 0.032043 | 0.059509 | -122.1039 | -122.1863 | 0.068664 | 0.041198 | -0.027466 | -0.018311 | -0.086975 | -0.004578 | -0.14191 | -0.25635 | 0.11902 | 0.14191 | 0.068664 | 0.14648 | 0.073242 | 0.009155 | -0.054932 | 0.1236 | 121.9391 | 0.027466 | 122.0535 | 0.086975 | 122.049 | -122.1313 | -122.1954 | 0.004577 | 121.9345 | -0.022888 | 0.34332
2193.4844 | 122.2229 | -0.10071 | 122.081 | -0.15846 | -0.04538 | 0.003873 | 0.024005 | -0.00084593 | -0.010102 | -0.0021597 | -0.019196 | 0.0048833 | 0.06385 | 0.0509 | -0.016233 | 0.02634 | -0.0062207 | -0.13275 | -0.054932 | -0.027466 | -0.054932 | 0.054932 | -0.059509 | 0.013733 | 0.32044 | 121.8933 | -0.11444 | 121.875 | 0.082397 | 0.045776 | 0.082397 | 0.073242 | -122.1359 | -122.1359 | 0.15564 | 0.11444 | 0.041199 | 0.041199 | -0.032043 | -0.013733 | -0.18768 | -0.20599 | 0.18311 | 0.18311 | 0.14648 | 0.19684 | 0.16022 | 0.082398 | -0.027466 | 0.19684 | 121.9894 | -0.027466 | 122.0078 | 0.045776 | 121.994 | -122.1085 | -122.1954 | 0.045776 | 121.9757 | -0.032043 | 0.42114
2195.2344 | 122.1725 | -0.1236 | 122.0993 | -0.051651 | -0.047089 | 0.0025912 | 0.0255 | -0.0017005 | -0.009675 | -0.0032277 | -0.068024 | 0.0080877 | 0.065345 | 0.049832 | -0.017088 | 0.028903 | -0.0062207 | -0.16479 | -0.018311 | -0.054932 | -0.10986 | -0.018311 | -0.10986 | -0.036621 | 0.37994 | 121.9666 | -0.11444 | 121.7926 | 0.009155 | -0.036621 | 0.009155 | 0.068664 | -122.1176 | -122.2092 | 0.10528 | 0.086975 | 0.013733 | 0.018311 | -0.054931 | 0.009155 | -0.13275 | -0.3067 | 0.13275 | 0.13275 | 0.086975 | 0.1236 | 0.07782 | 0.036621 | -0.054931 | 0.1236 | 121.907 | 0.036621 | 122.081 | 0.10528 | 122.0901 | -122.1542 | -122.2137 | 0.013733 | 121.9162 | -0.041199 | 0.50354
2197 | 122.3053 | -0.082397 | 122.0398 | -0.12794 | -0.048371 | 0.00045503 | 0.023578 | -0.0036231 | -0.010957 | -0.0034415 | -0.0069885 | 0.0044561 | 0.064918 | 0.048764 | -0.016874 | 0.02869 | -0.0068615 | -0.10529 | -0.059509 | -0.032043 | 0.009155 | 0.13733 | 0.022888 | 0.064087 | 0.49439 | 121.8979 | -0.082397 | 121.9254 | 0.17395 | 0.14648 | 0.13733 | 0.050354 | -122.0993 | -122.0306 | 0.21973 | 0.14648 | 0.10528 | 0.09613 | 0.054931 | 0 | -0.14191 | -0.11444 | 0.25635 | 0.21973 | 0.22888 | 0.21973 | 0.22888 | 0.16937 | 0.041198 | 0.25635 | 122.0078 | -0.027466 | 121.9803 | 0.022888 | 121.9803 | -122.0718 | -122.1222 | 0.091552 | 122.0078 | -0.022889 | 0.57678
2198.7031 | 122.2321 | -0.091553 | 122.0535 | -0.10506 | -0.044953 | 0.0030184 | 0.028491 | 0.00022207 | -0.0083932 | -0.00087794 | -0.092438 | 0.0074469 | 0.064277 | 0.047909 | -0.014951 | 0.027194 | -0.0034435 | -0.09613 | -0.022888 | -0.050354 | -0.045776 | 0.036621 | -0.07782 | -0.022888 | 0.41657 | 121.9299 | -0.09613 | 121.8521 | 0.064087 | 0.013733 | 0.073242 | 0.041199 | -122.0764 | -122.0993 | 0.12817 | 0.068665 | 0.013733 | 0.027466 | -0.027466 | -0.004577 | -0.1236 | -0.20142 | 0.15564 | 0.16479 | 0.10529 | 0.16937 | 0.10986 | 0.086975 | 0.004578 | 0.16022 | 121.9482 | 0.027466 | 122.0261 | 0.068665 | 122.0215 | -122.1039 | -122.1497 | 0.045777 | 121.9437 | -0.004577 | 0.50812
2200.4688 | 122.287 | -0.054932 | 122.0306 | -0.19661 | -0.042816 | 0.0023776 | 0.025287 | -0.0021277 | -0.009675 | -0.0028005 | -0.040558 | 0.0061651 | 0.064491 | 0.056668 | -0.017942 | 0.026981 | -0.0072889 | -0.064087 | -0.07782 | -0.022888 | 0.018311 | 0.13275 | -0.022888 | 0.068665 | 0.36621 | 121.8933 | -0.068665 | 121.9254 | 0.1236 | 0.07782 | 0.13275 | 0.032044 | -122.1085 | -122.0123 | 0.18768 | 0.1236 | 0.032044 | 0.091553 | 0 | -0.013733 | -0.13733 | -0.10529 | 0.17853 | 0.18768 | 0.13275 | 0.20142 | 0.14649 | 0.15564 | 0.041199 | 0.19226 | 121.994 | -0.054932 | 121.962 | -0.022888 | 121.9482 | -122.0535 | -122.0993 | 0.073243 | 121.9803 | -0.009155 | 0.42114
2202.2188 | 122.3145 | -0.073242 | 122.0398 | -0.097427 | -0.045807 | 0.0025912 | 0.022509 | -0.0034095 | -0.010102 | -0.0025869 | -0.022247 | 0.0038153 | 0.06385 | 0.048123 | -0.013883 | 0.026981 | -0.0068615 | -0.09613 | -0.054932 | -0.032043 | 0.013733 | 0.13733 | 0.027466 | 0.091553 | 0.49896 | 121.9162 | -0.068665 | 121.9299 | 0.1831 | 0.14191 | 0.13275 | 0.041199 | -122.0947 | -122.0261 | 0.21057 | 0.16479 | 0.10071 | 0.1236 | 0.059509 | 0.004577 | -0.1236 | -0.10986 | 0.25635 | 0.20599 | 0.21515 | 0.20142 | 0.21057 | 0.16937 | 0.045776 | 0.25177 | 121.9986 | -0.022889 | 121.9849 | 0.01831 | 121.9894 | -122.0718 | -122.1085 | 0.086975 | 122.0032 | -0.022888 | 0.5722
2203.9219 | 122.1909 | -0.13733 | 122.0673 | -0.082169 | -0.046875 | 0.0010958 | 0.026355 | -0.0019141 | -0.010102 | -0.0055777 | -0.074127 | 0.0070197 | 0.065132 | 0.050686 | -0.014951 | 0.029117 | -0.0036573 | -0.15564 | -0.018311 | -0.059509 | -0.10529 | -0.004578 | -0.10529 | -0.041199 | 0.37537 | 121.962 | -0.12817 | 121.8018 | 0.004578 | -0.027466 | 0.004578 | 0.07782 | -122.0856 | -122.1725 | 0.13275 | 0.09613 | 0.032043 | 0.01831 | -0.045777 | 0.009155 | -0.10529 | -0.2655 | 0.14191 | 0.14191 | 0.10986 | 0.13275 | 0.10071 | 0.054931 | -0.045777 | 0.13275 | 121.9299 | 0.041198 | 122.0901 | 0.11902 | 122.0993 | -122.1268 | -122.1954 | 0.032043 | 121.9391 | -0.018311 | 0.5127
2205.6719 | 122.1954 | -0.11902 | 122.0993 | -0.082169 | -0.046234 | 0.005582 | 0.026568 | -0.0014867 | -0.010316 | -0.0025869 | -0.046661 | 0.0046697 | 0.06385 | 0.050473 | -0.017729 | 0.025912 | -0.0042981 | -0.091553 | -0.032043 | -0.027466 | -0.050354 | 0.045776 | -0.068665 | 0.009155 | 0.41657 | 121.9482 | -0.09613 | 121.8018 | 0.041199 | -0.013733 | 0.009155 | 0.091553 | -122.1313 | -122.1497 | 0.16479 | 0.12817 | 0.050354 | 0.036621 | -0.041199 | 0.022889 | -0.15106 | -0.29755 | 0.16022 | 0.12817 | 0.10529 | 0.10528 | 0.082397 | 0.073242 | -0.022888 | 0.13733 | 121.8979 | -0.004577 | 122.0444 | 0.086976 | 122.0673 | -122.1268 | -122.1954 | 0.068665 | 121.9208 | 0.027466 | 0.53558
2207.3594 | 122.287 | -0.07782 | 122.0535 | -0.11269 | -0.047303 | 0.003873 | 0.024859 | -0.0019141 | -0.0083932 | -0.0047231 | -0.019196 | 0.0036017 | 0.064063 | 0.053036 | -0.013883 | 0.026553 | -0.0045117 | -0.073242 | -0.059509 | -0.013733 | 0.032043 | 0.15106 | 0.018311 | 0.082397 | 0.5127 | 121.8887 | -0.068665 | 121.9254 | 0.16937 | 0.11444 | 0.12817 | 0.064087 | -122.113 | -122.0215 | 0.22888 | 0.16022 | 0.096131 | 0.09613 | 0.032044 | 0.009155 | -0.16479 | -0.12817 | 0.24719 | 0.20599 | 0.19226 | 0.19684 | 0.18311 | 0.16479 | 0.045776 | 0.23804 | 121.994 | -0.045776 | 121.9574 | 0.018311 | 121.9666 | -122.0673 | -122.1222 | 0.10986 | 122.0032 | 0.004578 | 0.59052
2209.1094 | 122.2275 | -0.11444 | 122.0718 | -0.1432 | -0.04538 | 0.0047274 | 0.027209 | 0.00064947 | -0.0083932 | -0.0057913 | -0.09549 | 0.0057379 | 0.064277 | 0.053036 | -0.016874 | 0.026553 | -0.0032299 | -0.10071 | -0.032043 | -0.041199 | -0.041199 | 0.045776 | -0.07782 | -0.009155 | 0.40283 | 121.9574 | -0.091553 | 121.8613 | 0.073242 | 0.018311 | 0.045776 | 0.073242 | -122.1039 | -122.113 | 0.16022 | 0.10529 | 0.036621 | 0.032044 | -0.036621 | 0.022888 | -0.11444 | -0.21057 | 0.18768 | 0.16022 | 0.13275 | 0.13733 | 0.10986 | 0.086975 | 0 | 0.16479 | 121.9528 | 0.009156 | 122.049 | 0.082398 | 122.0718 | -122.113 | -122.1634 | 0.073242 | 121.9757 | 0.013733 | 0.51727
2210.7969 | 122.1725 | -0.10529 | 122.113 | -0.1432 | -0.044098 | 0.0028048 | 0.028277 | -0.00084593 | -0.0083932 | -0.0062185 | -0.11685 | 0.0050971 | 0.064277 | 0.054959 | -0.015379 | 0.028262 | -0.0070751 | -0.12817 | -0.027466 | -0.050354 | -0.11444 | -0.054932 | -0.16479 | -0.082397 | 0.2243 | 121.9666 | -0.1236 | 121.7972 | -0.027466 | -0.073242 | -0.009155 | 0.054932 | -122.1405 | -122.2275 | 0.050354 | 0.022889 | -0.059509 | -0.032043 | -0.11444 | -0.01831 | -0.14648 | -0.31586 | 0.07782 | 0.096131 | 0.032044 | 0.11444 | 0.050354 | -0.004578 | -0.064087 | 0.09613 | 121.9208 | 0.022888 | 122.0901 | 0.07782 | 122.0718 | -122.1634 | -122.2366 | -0.009155 | 121.9025 | -0.022888 | 0.32959
2212.5469 | 122.2824 | -0.068665 | 122.081 | -0.16609 | -0.047516 | 0.002164 | 0.022296 | -0.0064001 | -0.011811 | -0.0025869 | -0.0069885 | 0.0042425 | 0.064491 | 0.045987 | -0.014097 | 0.025912 | -0.0045117 | -0.073242 | -0.054932 | -0.022888 | 0.013733 | 0.1236 | 0.013733 | 0.054932 | 0.50812 | 121.9299 | -0.068665 | 121.9025 | 0.13275 | 0.10529 | 0.11444 | 0.045777 | -122.1359 | -122.0673 | 0.19226 | 0.1236 | 0.082398 | 0.07782 | 0.036621 | 0 | -0.15106 | -0.17853 | 0.20142 | 0.18311 | 0.17395 | 0.18311 | 0.17395 | 0.14648 | 0.036621 | 0.20142 | 121.9711 | -0.032044 | 121.9986 | 0.013733 | 121.9986 | -122.1039 | -122.1497 | 0.082398 | 121.9711 | -0.004577 | 0.57678
2214.25 | 122.1817 | -0.11902 | 122.1039 | -0.082169 | -0.043457 | 0.004941 | 0.030414 | -0.00084593 | -0.0098886 | -0.0040823 | -0.098541 | 0.0044561 | 0.066413 | 0.054745 | -0.01666 | 0.028262 | -0.0038709 | -0.12817 | -0.054932 | -0.036621 | -0.086975 | -0.036621 | -0.14191 | -0.059509 | 0.25635 | 121.9666 | -0.10071 | 121.8018 | -0.009155 | -0.059509 | 0.009155 | 0.082398 | -122.1588 | -122.1909 | 0.082398 | 0.05951 | -0.022888 | -0.022888 | -0.10529 | 0.018311 | -0.13733 | -0.30212 | 0.10986 | 0.12817 | 0.05951 | 0.10986 | 0.041199 | 0 | -0.050354 | 0.091553 | 121.9025 | -0.018311 | 122.0673 | 0.064087 | 122.0856 | -122.1405 | -122.2046 | 0.032044 | 121.9208 | -0.009155 | 0.37537
2216 | 122.2961 | -0.059509 | 122.0261 | -0.10506 | -0.043457 | 0.005582 | 0.026568 | 0.00043587 | -0.0083932 | -0.0047231 | -0.052765 | 0.0038153 | 0.064704 | 0.056881 | -0.01666 | 0.028262 | -0.0070751 | -0.059509 | -0.068665 | -0.032043 | 0.009155 | 0.10986 | -0.027466 | 0.041199 | 0.36163 | 121.9208 | -0.082397 | 121.9345 | 0.13275 | 0.09613 | 0.15106 | 0.027466 | -122.0947 | -122.0169 | 0.16937 | 0.10071 | 0.032043 | 0.073242 | 0.004577 | -0.022888 | -0.10529 | -0.091553 | 0.19226 | 0.21057 | 0.15564 | 0.23346 | 0.17853 | 0.14191 | 0.041198 | 0.21515 | 122.0169 | -0.036622 | 122.0032 | -0.009156 | 121.9803 | -122.0581 | -122.1085 | 0.068664 | 121.994 | 0 | 0.42114
2217.6875 | 122.2961 | -0.068665 | 122.0627 | -0.18135 | -0.045594 | 0.003873 | 0.025927 | 8.47e-06 | -0.0092478 | -0.0038687 | -0.071076 | 0.0055243 | 0.061927 | 0.046628 | -0.017515 | 0.028903 | -0.0036573 | -0.11444 | -0.050354 | -0.013733 | 0.004578 | 0.082397 | -0.050354 | 0.018311 | 0.33875 | 121.9208 | -0.086975 | 121.9299 | 0.11902 | 0.086975 | 0.14191 | 0.054932 | -122.113 | -122.0581 | 0.15106 | 0.086976 | 0.018311 | 0.032044 | -0.036621 | -0.01831 | -0.14191 | -0.13275 | 0.18768 | 0.21057 | 0.15564 | 0.22888 | 0.17395 | 0.09613 | 0.018311 | 0.20599 | 122.0169 | -0.036621 | 122.0078 | 0.018311 | 121.9894 | -122.0764 | -122.1497 | 0.073243 | 121.9986 | -0.045776 | 0.40741
2219.4375 | 122.1817 | -0.11902 | 122.1268 | -0.15083 | -0.045594 | 0.0028048 | 0.027636 | 8.47e-06 | -0.0081796 | -0.0036551 | -0.11685 | 0.0083013 | 0.064063 | 0.04855 | -0.014951 | 0.027621 | -0.0045117 | -0.1236 | -0.027466 | -0.050354 | -0.091553 | -0.041199 | -0.16022 | -0.07782 | 0.22888 | 121.962 | -0.10529 | 121.8063 | -0.013733 | -0.054932 | 0.009155 | 0.068665 | -122.1542 | -122.2183 | 0.07782 | 0.041199 | -0.041198 | -0.027466 | -0.10986 | 0.013733 | -0.16479 | -0.32043 | 0.10529 | 0.12817 | 0.064087 | 0.11444 | 0.050354 | 0.009155 | -0.041199 | 0.091553 | 121.9116 | 0.022888 | 122.0673 | 0.091553 | 122.081 | -122.1771 | -122.2321 | 0.027466 | 121.9254 | -0.004577 | 0.3479
2221.2031 | 122.3465 | -0.059509 | 122.049 | -0.082169 | -0.046448 | 0.002164 | 0.022937 | -0.0031957 | -0.0064706 | -0.0030141 | 0.023529 | 0.0048833 | 0.064063 | 0.044064 | -0.016233 | 0.024631 | -0.0040845 | -0.07782 | -0.059509 | -0.013733 | 0.036621 | 0.16022 | 0.027466 | 0.091553 | 0.52185 | 121.9299 | -0.082397 | 121.9437 | 0.16937 | 0.12817 | 0.13275 | 0.045776 | -122.1085 | -122.0123 | 0.21973 | 0.15106 | 0.086975 | 0.10529 | 0.041199 | -0.022888 | -0.11902 | -0.10529 | 0.22888 | 0.19226 | 0.18768 | 0.21515 | 0.21057 | 0.17395 | 0.050354 | 0.25177 | 122.0261 | -0.045776 | 122.0123 | 0 | 121.9894 | -122.0627 | -122.1313 | 0.09613 | 122.0032 | -0.018311 | 0.58136
2222.8906 | 122.3328 | -0.082397 | 122.0306 | -0.089798 | -0.04538 | 0.0013094 | 0.023364 | -0.0042639 | -0.0075388 | -0.0032277 | 0.0082703 | 0.0065923 | 0.065559 | 0.047909 | -0.014097 | 0.025912 | -0.0030163 | -0.09613 | -0.054932 | -0.036621 | -0.004578 | 0.10071 | 0.004578 | 0.073242 | 0.46234 | 121.9208 | -0.091553 | 121.9391 | 0.15106 | 0.13275 | 0.12817 | 0.045776 | -122.0856 | -122.0352 | 0.18311 | 0.15564 | 0.086975 | 0.10986 | 0.041199 | -0.009156 | -0.10986 | -0.091553 | 0.23346 | 0.21057 | 0.21515 | 0.21973 | 0.2243 | 0.13733 | 0.032043 | 0.24261 | 122.0306 | -0.018311 | 122.0123 | 0.027465 | 122.0032 | -122.0673 | -122.1222 | 0.077819 | 122.0215 | -0.013733 | 0.54474
2224.6406 | 122.3053 | -0.068665 | 122.0215 | -0.1432 | -0.043885 | 0.0043002 | 0.028491 | -0.0010595 | -0.0073252 | -0.0021597 | -0.080231 | 0.0070197 | 0.064491 | 0.053036 | -0.015165 | 0.027621 | -0.0089977 | -0.068665 | -0.059509 | -0.018311 | 0.013733 | 0.09613 | -0.041199 | 0.032043 | 0.3479 | 121.9162 | -0.050354 | 121.962 | 0.12817 | 0.086975 | 0.14648 | 0.050354 | -122.081 | -122.0078 | 0.16479 | 0.10071 | 0.027466 | 0.050354 | -0.022888 | 0.018311 | -0.10528 | -0.059509 | 0.19684 | 0.21515 | 0.15564 | 0.19684 | 0.13733 | 0.11444 | 0.032044 | 0.17853 | 122.0123 | -0.041198 | 121.9666 | 0.009156 | 121.9849 | -122.0398 | -122.0718 | 0.082398 | 122.0306 | 0 | 0.41656
2226.3281 | 122.1909 | -0.11902 | 122.0856 | -0.15083 | -0.044953 | 0.003232 | 0.02785 | 0.0015039 | -0.0088206 | -0.0042959 | -0.11685 | 0.0068059 | 0.066413 | 0.055386 | -0.014738 | 0.029971 | -0.0042981 | -0.13733 | -0.018311 | -0.068665 | -0.12817 | -0.059509 | -0.15564 | -0.059509 | 0.21515 | 122.0078 | -0.10986 | 121.8246 | -0.018311 | -0.073242 | 0.018311 | 0.050354 | -122.1039 | -122.2137 | 0.05951 | 0.05951 | -0.036621 | 0.009156 | -0.086975 | 0.009156 | -0.07782 | -0.26093 | 0.10071 | 0.13733 | 0.045777 | 0.12817 | 0.036621 | 0.009156 | -0.059509 | 0.091552 | 121.9345 | 0.050354 | 122.1176 | 0.10071 | 122.1268 | -122.1542 | -122.1954 | -0.009155 | 121.9437 | -0.01831 | 0.33417
2228.0781 | 122.2412 | -0.10529 | 122.0856 | -0.10506 | -0.045594 | 0.003232 | 0.028277 | 0.0021447 | -0.009675 | -0.0030141 | -0.089386 | 0.0059515 | 0.062995 | 0.052395 | -0.015379 | 0.027621 | -0.0062207 | -0.1236 | -0.036621 | -0.068665 | -0.045776 | 0.041199 | -0.086975 | -0.009155 | 0.40741 | 121.9894 | -0.086975 | 121.8796 | 0.059509 | 0.013733 | 0.068665 | 0.036621 | -122.1222 | -122.1313 | 0.14649 | 0.096131 | 0.018311 | 0.05951 | -0.01831 | 0.018311 | -0.09613 | -0.20599 | 0.16479 | 0.17395 | 0.11902 | 0.15564 | 0.10071 | 0.10986 | 0.022889 | 0.14648 | 121.9666 | 0.032044 | 122.0764 | 0.068665 | 122.0947 | -122.1542 | -122.1725 | 0.05951 | 121.9849 | -0.01831 | 0.5127
2229.8281 | 122.1771 | -0.13275 | 122.0993 | -0.11269 | -0.047943 | 0.00024143 | 0.026355 | -0.0044775 | -0.0064706 | -0.0019461 | -0.019196 | 0.0059515 | 0.06385 | 0.042569 | -0.014311 | 0.026553 | -0.0055799 | -0.14191 | -0.041199 | -0.036621 | -0.091553 | 0.013733 | -0.091553 | -0.032043 | 0.38452 | 121.9711 | -0.11902 | 121.8109 | 0.027466 | -0.022888 | 0 | 0.09613 | -122.1405 | -122.1909 | 0.14648 | 0.10071 | 0.041198 | 0.004578 | -0.054932 | 0.013732 | -0.12817 | -0.28839 | 0.16022 | 0.13275 | 0.10986 | 0.11902 | 0.096131 | 0.050354 | -0.054932 | 0.14649 | 121.9299 | -0.004578 | 122.0901 | 0.091552 | 122.1039 | -122.1359 | -122.2183 | 0.041198 | 121.9437 | -0.009156 | 0.51727
2231.5625 | 122.287 | -0.086975 | 122.0673 | -0.10506 | -0.044739 | 0.0034456 | 0.025927 | -0.00063233 | -0.0054026 | -2.3544e-05 | -0.077179 | 0.0057379 | 0.064063 | 0.048123 | -0.015806 | 0.02933 | -0.0066479 | -0.13275 | -0.027466 | -0.027466 | -0.059509 | 0.009155 | -0.09613 | -0.009155 | 0.27008 | 121.9437 | -0.10529 | 121.9208 | 0.09613 | 0.059509 | 0.10529 | 0.059509 | -122.0947 | -122.1268 | 0.09613 | 0.07782 | -0.009155 | 0.018311 | -0.068664 | -0.018311 | -0.1236 | -0.14648 | 0.1831 | 0.19226 | 0.14648 | 0.21057 | 0.16479 | 0.036621 | -0.032043 | 0.20142 | 122.0261 | 0 | 122.049 | 0.059509 | 122.0306 | -122.0947 | -122.1725 | 0.027466 | 122.0078 | -0.045776 | 0.35706
2233.3125 | 122.1725 | -0.11444 | 122.0901 | -0.11269 | -0.042603 | 0.0040866 | 0.027636 | 0.0027857 | -0.009675 | -0.0028005 | -0.09549 | 0.0055243 | 0.065132 | 0.049191 | -0.016233 | 0.02634 | -0.0049389 | -0.12817 | -0.013733 | -0.059509 | -0.082397 | 0.009155 | -0.11902 | -0.059509 | 0.28839 | 121.9894 | -0.09613 | 121.8292 | 0.009155 | -0.050354 | 0.022888 | 0.054932 | -122.1039 | -122.1725 | 0.1236 | 0.054932 | -0.004578 | 0 | -0.05951 | 0.018311 | -0.10071 | -0.26093 | 0.1236 | 0.13733 | 0.064087 | 0.11902 | 0.045776 | 0.068664 | -0.022888 | 0.10528 | 121.9254 | 0.045776 | 122.0856 | 0.10071 | 122.1039 | -122.1497 | -122.1863 | 0.032044 | 121.9437 | -0.013733 | 0.40283
2235 | 122.168 | -0.11444 | 122.1176 | -0.15846 | -0.043457 | 0.0030184 | 0.027423 | 0.0036401 | -0.010957 | -0.0060049 | -0.10464 | 0.0063787 | 0.064704 | 0.047055 | -0.015592 | 0.025699 | -0.0032299 | -0.14191 | -0.018311 | -0.064087 | -0.11444 | -0.059509 | -0.15106 | -0.073242 | 0.20142 | 121.9986 | -0.091553 | 121.8063 | -0.009155 | -0.054932 | 0.009155 | 0.050354 | -122.1359 | -122.2321 | 0.054932 | 0.041199 | -0.036621 | -0.009155 | -0.086975 | 0.022888 | -0.11902 | -0.31128 | 0.10529 | 0.1236 | 0.059509 | 0.10071 | 0.036621 | 0.004578 | -0.050354 | 0.082398 | 121.8979 | 0.045776 | 122.0901 | 0.09613 | 122.113 | -122.1817 | -122.2092 | 0 | 121.9208 | -0.027466 | 0.31586
2236.7344 | 122.3419 | -0.07782 | 122.0581 | -0.17372 | -0.046448 | 0.0023776 | 0.024646 | -0.00041873 | -0.0094614 | -0.0047231 | 0.035736 | 0.0050971 | 0.065132 | 0.0462 | -0.015379 | 0.027621 | -0.0057935 | -0.091553 | -0.041199 | -0.036621 | 0.004578 | 0.11902 | 0.027466 | 0.07782 | 0.47607 | 121.9391 | -0.086975 | 121.9482 | 0.16022 | 0.1236 | 0.15564 | 0.041199 | -122.0993 | -122.0535 | 0.19684 | 0.15564 | 0.10529 | 0.11444 | 0.064087 | -0.009155 | -0.11902 | -0.10986 | 0.23804 | 0.23346 | 0.20142 | 0.24261 | 0.21057 | 0.15564 | 0.041199 | 0.24719 | 122.0352 | -0.004578 | 122.0261 | 0.036621 | 122.0169 | -122.0947 | -122.1451 | 0.082398 | 122.0261 | -0.013733 | 0.55389
2238.4375 | 122.3053 | -0.064087 | 122.0535 | -0.097427 | -0.046021 | 0.0036594 | 0.025714 | 0.00064947 | -0.010743 | -0.0042959 | 0.029632 | 0.0040289 | 0.064704 | 0.045559 | -0.01666 | 0.026981 | -0.0060071 | -0.07782 | -0.07782 | -0.036621 | 0.022888 | 0.16022 | 0.018311 | 0.086975 | 0.52185 | 121.9299 | -0.082397 | 121.9437 | 0.17853 | 0.14191 | 0.14191 | 0.027466 | -122.1313 | -122.0306 | 0.2243 | 0.15106 | 0.082398 | 0.1236 | 0.054932 | -0.01831 | -0.1236 | -0.10986 | 0.24261 | 0.20599 | 0.20599 | 0.2243 | 0.2243 | 0.19684 | 0.059509 | 0.26092 | 122.0261 | -0.041199 | 122.0123 | -0.013733 | 121.994 | -122.0901 | -122.1359 | 0.086975 | 122.0078 | -0.013733 | 0.58594
2240.1875 | 122.2458 | -0.10986 | 122.1268 | -0.097427 | -0.043671 | 0.0028048 | 0.027636 | 0.0017175 | -0.0077524 | -0.0036551 | -0.10159 | 0.0055243 | 0.064063 | 0.047909 | -0.017088 | 0.027408 | -0.0079297 | -0.09613 | -0.022888 | -0.045776 | -0.045776 | 0.036621 | -0.059509 | -0.018311 | 0.42572 | 121.9849 | -0.10986 | 121.8842 | 0.07782 | 0.009155 | 0.059509 | 0.064087 | -122.1497 | -122.1725 | 0.14648 | 0.091552 | 0.050354 | 0.027465 | -0.013733 | 0 | -0.14191 | -0.24261 | 0.18768 | 0.16937 | 0.11902 | 0.16937 | 0.11902 | 0.082397 | 0 | 0.18768 | 121.994 | 0.022888 | 122.0947 | 0.086975 | 122.0947 | -122.1725 | -122.2366 | 0.064087 | 121.994 | 0.013733 | 0.53558
2241.9375 | 122.1817 | -0.13733 | 122.1085 | -0.082169 | -0.046021 | 0.00024143 | 0.022082 | -0.0029821 | -0.011811 | -0.00087794 | -0.046661 | 0.0061651 | 0.065772 | 0.048764 | -0.01602 | 0.026767 | -0.0055799 | -0.11444 | -0.032043 | -0.050354 | -0.064087 | 0.009155 | -0.091553 | -0.009155 | 0.40283 | 121.9849 | -0.11444 | 121.8246 | 0.041199 | -0.013733 | 0.004578 | 0.086975 | -122.1405 | -122.1725 | 0.14648 | 0.12817 | 0.045776 | 0.041199 | -0.041199 | 0.022888 | -0.1236 | -0.28381 | 0.17853 | 0.14191 | 0.1236 | 0.11902 | 0.10071 | 0.059509 | -0.013733 | 0.15564 | 121.9391 | 0.018311 | 122.0993 | 0.10529 | 122.1222 | -122.1588 | -122.2229 | 0.073242 | 121.962 | 0.022888 | 0.54016
2243.6406 | 122.1771 | -0.11444 | 122.1085 | -0.1432 | -0.042816 | 0.0051546 | 0.028064 | 0.00043587 | -0.0066844 | -0.0042959 | -0.089386 | 0.0057379 | 0.063636 | 0.048764 | -0.015379 | 0.027835 | -0.0045117 | -0.13275 | -0.027466 | -0.050354 | -0.10071 | -0.009155 | -0.1236 | -0.064087 | 0.2655 | 121.9849 | -0.09613 | 121.8338 | -0.004578 | -0.059509 | 0.004578 | 0.064087 | -122.1359 | -122.2092 | 0.10529 | 0.050354 | -0.009155 | -0.013733 | -0.073242 | 0.018311 | -0.1236 | -0.27466 | 0.10986 | 0.11902 | 0.054932 | 0.10071 | 0.036621 | 0.041199 | -0.050354 | 0.091552 | 121.9299 | 0.022888 | 122.081 | 0.086975 | 122.0993 | -122.1588 | -122.2046 | 0.013733 | 121.9482 | -0.01831 | 0.37994
2245.3906 | 122.3099 | -0.073242 | 122.0581 | -0.18135 | -0.043885 | 0.0043002 | 0.025927 | 0.00022207 | -0.0094614 | -0.0021597 | -0.049713 | 0.0061651 | 0.065986 | 0.043423 | -0.01602 | 0.02933 | -0.0064343 | -0.10529 | -0.045776 | -0.032043 | -0.004578 | 0.07782 | -0.068665 | 0.027466 | 0.33875 | 121.9482 | -0.068665 | 121.9482 | 0.1236 | 0.07782 | 0.15106 | 0.041199 | -122.1039 | -122.0627 | 0.15106 | 0.10071 | 0.004577 | 0.059509 | -0.036622 | 0.004577 | -0.10986 | -0.10986 | 0.19684 | 0.2243 | 0.15106 | 0.21973 | 0.14649 | 0.10986 | 0.027465 | 0.19226 | 122.0169 | -0.013733 | 122.0169 | 0.027466 | 122.0215 | -122.0901 | -122.1268 | 0.068664 | 122.0215 | -0.032044 | 0.41199
2247.1406 | 122.2046 | -0.13275 | 122.1085 | -0.05928 | -0.046448 | 0.0028048 | 0.026568 | -0.0036231 | -0.006257 | -0.0034415 | -0.068024 | 0.0083013 | 0.065132 | 0.048337 | -0.013456 | 0.027621 | -0.0060071 | -0.15106 | -0.013733 | -0.064087 | -0.10529 | -0.009155 | -0.11444 | -0.036621 | 0.36163 | 121.9711 | -0.11444 | 121.8384 | 0.032043 | -0.027466 | 0.022888 | 0.068664 | -122.1222 | -122.2137 | 0.1236 | 0.09613 | 0.01831 | 0.027466 | -0.050354 | 0.01831 | -0.13733 | -0.27008 | 0.16479 | 0.15564 | 0.10529 | 0.13733 | 0.086975 | 0.054932 | -0.041199 | 0.14648 | 121.9528 | 0.050354 | 122.0856 | 0.11902 | 122.1039 | -122.1725 | -122.2229 | 0.027465 | 121.9711 | -0.018311 | 0.49438
2248.8281 | 122.319 | -0.07782 | 122.0581 | -0.16609 | -0.04538 | 0.0045138 | 0.026141 | -0.0025549 | -0.0083932 | -0.0032277 | -0.055817 | 0.0061651 | 0.064918 | 0.049832 | -0.016874 | 0.027408 | -0.0077161 | -0.10986 | -0.032043 | -0.036621 | -0.018311 | 0.073242 | -0.050354 | 0.027466 | 0.33417 | 121.9299 | -0.07782 | 121.9666 | 0.13275 | 0.082397 | 0.14648 | 0.041199 | -122.0901 | -122.0764 | 0.15106 | 0.10529 | 0.027466 | 0.064087 | -0.013733 | 0 | -0.12817 | -0.091552 | 0.21057 | 0.2243 | 0.16022 | 0.2243 | 0.16022 | 0.10986 | 0.01831 | 0.21057 | 122.0444 | 0.004578 | 122.0078 | 0.045777 | 122.0078 | -122.0947 | -122.1359 | 0.059509 | 122.0444 | -0.032043 | 0.41199
2250.5781 | 122.2092 | -0.10071 | 122.1085 | -0.12794 | -0.044525 | 0.0043002 | 0.026355 | -0.0010595 | -0.010102 | -0.0025869 | -0.089386 | 0.0078741 | 0.064918 | 0.0462 | -0.015379 | 0.026767 | -0.0053661 | -0.14191 | -0.032043 | -0.054932 | -0.12817 | -0.059509 | -0.15564 | -0.045776 | 0.21057 | 121.9757 | -0.10986 | 121.8521 | -0.013733 | -0.064087 | 0.013733 | 0.045776 | -122.1405 | -122.2366 | 0.041199 | 0.054932 | -0.054932 | 0.009156 | -0.10071 | -0.009155 | -0.13275 | -0.25635 | 0.086975 | 0.11444 | 0.036621 | 0.1236 | 0.045776 | -0.004577 | -0.073242 | 0.09613 | 121.962 | 0.022889 | 122.0856 | 0.068665 | 122.0764 | -122.1634 | -122.2183 | -0.027466 | 121.9528 | -0.041199 | 0.31128
2252.2656 | 122.1817 | -0.10986 | 122.1359 | -0.16609 | -0.043885 | 0.0060092 | 0.027636 | 8.47e-06 | -0.0081796 | -0.00066434 | -0.089386 | 0.0057379 | 0.064491 | 0.044919 | -0.015806 | 0.028049 | -0.0055799 | -0.12817 | -0.018311 | -0.027466 | -0.1236 | -0.036621 | -0.15564 | -0.064087 | 0.23346 | 121.9711 | -0.10071 | 121.8292 | -0.022888 | -0.073242 | 0.013733 | 0.082397 | -122.1542 | -122.2595 | 0.073242 | 0.045776 | -0.045777 | -0.036621 | -0.12817 | 0.009155 | -0.16479 | -0.3067 | 0.086975 | 0.1236 | 0.036621 | 0.11444 | 0.027466 | -0.009155 | -0.09613 | 0.07782 | 121.9299 | 0.009155 | 122.0718 | 0.091552 | 122.081 | -122.1634 | -122.2366 | -0.013733 | 121.9391 | -0.018311 | 0.34332
2254.0312 | 122.1863 | -0.11444 | 122.0993 | -0.15083 | -0.044312 | 0.0051546 | 0.026782 | -0.00063233 | -0.0090342 | -0.0013051 | -0.092438 | 0.0061651 | 0.065345 | 0.053677 | -0.014951 | 0.026981 | -0.0047253 | -0.11444 | -0.013733 | -0.045776 | -0.086975 | 0.009155 | -0.1236 | -0.045776 | 0.29297 | 122.0032 | -0.10071 | 121.8384 | 0.009155 | -0.064087 | 0.022888 | 0.068665 | -122.113 | -122.1863 | 0.1236 | 0.068665 | -0.009155 | 0 | -0.07782 | 0.013733 | -0.09613 | -0.26093 | 0.1236 | 0.13733 | 0.050354 | 0.1236 | 0.036621 | 0.054931 | -0.041199 | 0.10986 | 121.9391 | 0.032043 | 122.1039 | 0.10071 | 122.1176 | -122.1451 | -122.2 | 0.027466 | 121.9528 | 0 | 0.40741
2255.7812 | 122.287 | -0.091553 | 122.0581 | -0.082169 | -0.046662 | 0.0034456 | 0.025073 | -0.0029821 | -0.0081796 | -0.00023714 | -0.016144 | 0.0065923 | 0.064063 | 0.041928 | -0.012815 | 0.025058 | -0.0045117 | -0.082397 | -0.059509 | -0.027466 | 0.013733 | 0.10986 | 0.018311 | 0.068665 | 0.49896 | 121.9849 | -0.086975 | 121.907 | 0.13733 | 0.086975 | 0.10071 | 0.064087 | -122.1176 | -122.0444 | 0.20142 | 0.16022 | 0.10986 | 0.096131 | 0.045777 | 0.004578 | -0.073242 | -0.15106 | 0.22888 | 0.19226 | 0.17853 | 0.18768 | 0.17395 | 0.13733 | 0.041199 | 0.2243 | 121.994 | -0.032043 | 122.0718 | 0.032044 | 122.0764 | -122.0856 | -122.1451 | 0.10529 | 121.9986 | 0.009156 | 0.59052
2257.4688 | 122.2595 | -0.086975 | 122.0764 | -0.15083 | -0.044953 | 0.003232 | 0.028277 | 0.00043587 | -0.008607 | -0.0042959 | -0.058869 | 0.0055243 | 0.067054 | 0.042569 | -0.016874 | 0.028049 | -0.0017347 | -0.14648 | -0.004578 | -0.045776 | -0.09613 | -0.004578 | -0.13733 | -0.036621 | 0.26093 | 121.9849 | -0.10071 | 121.907 | 0.064087 | 0.018311 | 0.082397 | 0.041199 | -122.081 | -122.1725 | 0.082397 | 0.050354 | -0.050354 | 0.009155 | -0.091553 | -0.013733 | -0.091553 | -0.16937 | 0.15106 | 0.16937 | 0.10529 | 0.18311 | 0.11902 | 0.041198 | -0.050354 | 0.1648 | 122.0078 | 0.041198 | 122.0856 | 0.082397 | 122.0718 | -122.1222 | -122.1771 | -0.009155 | 121.994 | -0.059509 | 0.3479
2259.2344 | 122.2458 | -0.1236 | 122.1222 | -0.05928 | -0.045594 | 0.002164 | 0.026782 | 0.0029993 | -0.009675 | -0.00045074 | -0.055817 | 0.0065923 | 0.064491 | 0.049618 | -0.017515 | 0.026981 | -0.0025891 | -0.09613 | -0.027466 | -0.045776 | -0.050354 | 0.036621 | -0.07782 | -0.018311 | 0.41657 | 121.9757 | -0.091553 | 121.8704 | 0.07782 | 0.009155 | 0.07782 | 0.07782 | -122.1497 | -122.1725 | 0.16022 | 0.10528 | 0.045776 | 0.027465 | -0.032044 | 0.032043 | -0.14648 | -0.25177 | 0.20142 | 0.20142 | 0.13275 | 0.16937 | 0.10071 | 0.082397 | -0.004578 | 0.16937 | 121.962 | 0.01831 | 122.0673 | 0.09613 | 122.0993 | -122.168 | -122.2137 | 0.073242 | 121.994 | 0.027466 | 0.54016
2260.9375 | 122.1817 | -0.1236 | 122.1176 | -0.097427 | -0.041748 | 0.0045138 | 0.029132 | -0.0010595 | -0.0081796 | -0.0049367 | -0.089386 | 0.0055243 | 0.064491 | 0.053464 | -0.014951 | 0.02869 | -0.0023755 | -0.13275 | -0.022888 | -0.050354 | -0.10071 | -0.059509 | -0.16022 | -0.07782 | 0.2243 | 121.9894 | -0.10986 | 121.8201 | -0.027466 | -0.082397 | -0.004578 | 0.073242 | -122.1405 | -122.2183 | 0.064087 | 0.045776 | -0.036621 | -0.027466 | -0.10986 | 0.013733 | -0.12817 | -0.29755 | 0.09613 | 0.11902 | 0.041199 | 0.10529 | 0.027466 | -0.009155 | -0.050354 | 0.082397 | 121.9299 | 0.027466 | 122.0993 | 0.10071 | 122.113 | -122.168 | -122.2275 | 0.022888 | 121.9437 | -0.009155 | 0.3479
2262.6875 | 122.2092 | -0.11444 | 122.1085 | -0.082169 | -0.045594 | 0.0010958 | 0.025927 | -0.0031957 | -0.0094614 | -0.0021597 | -0.046661 | 0.0053107 | 0.064918 | 0.045346 | -0.015165 | 0.027621 | -0.0055799 | -0.14648 | -0.009155 | -0.050354 | -0.11902 | -0.022888 | -0.11444 | -0.036621 | 0.37079 | 122.0078 | -0.11444 | 121.8384 | 0.018311 | -0.032043 | 0.022888 | 0.064087 | -122.1176 | -122.2275 | 0.091553 | 0.07782 | 0 | 0.013733 | -0.064087 | 0 | -0.10071 | -0.27008 | 0.13275 | 0.13733 | 0.082398 | 0.13733 | 0.082398 | 0.027466 | -0.068665 | 0.13275 | 121.9528 | 0.041199 | 122.1222 | 0.10529 | 122.1222 | -122.1588 | -122.2229 | -0.004578 | 121.9528 | -0.032043 | 0.48523
2264.4375 | 122.1954 | -0.10986 | 122.1222 | -0.12032 | -0.043885 | 0.0045138 | 0.026996 | 0.00064947 | -0.0077524 | -0.0030141 | -0.1077 | 0.0070197 | 0.06385 | 0.052395 | -0.01666 | 0.027194 | -0.0062207 | -0.12817 | -0.009155 | -0.032043 | -0.10529 | -0.013733 | -0.14648 | -0.059509 | 0.25635 | 122.0032 | -0.09613 | 121.8384 | -0.018311 | -0.064087 | 0.022888 | 0.07782 | -122.1313 | -122.2275 | 0.09613 | 0.050354 | -0.036621 | -0.027466 | -0.11444 | 0.013733 | -0.11902 | -0.28381 | 0.091552 | 0.13275 | 0.045776 | 0.11902 | 0.032043 | 0.01831 | -0.073243 | 0.077819 | 121.9345 | 0.022888 | 122.0993 | 0.10071 | 122.113 | -122.1542 | -122.2183 | 0.004577 | 121.9482 | -0.018311 | 0.36621
2266.1406 | 122.3236 | -0.073242 | 122.0993 | -0.13557 | -0.045166 | 0.003232 | 0.024218 | 0.00022207 | -0.010743 | -0.0062185 | 0.026581 | 0.0027471 | 0.067695 | 0.045559 | -0.016233 | 0.025485 | -0.0021619 | -0.11902 | -0.064087 | -0.013733 | -0.032043 | 0.086975 | -0.027466 | 0.059509 | 0.41199 | 121.9437 | -0.082397 | 121.9345 | 0.15106 | 0.12817 | 0.13275 | 0.059509 | -122.1634 | -122.1313 | 0.16022 | 0.13275 | 0.045776 | 0.073242 | -0.013733 | -0.009155 | -0.15564 | -0.16479 | 0.2243 | 0.20599 | 0.20142 | 0.21515 | 0.21057 | 0.10071 | -0.01831 | 0.23346 | 122.0169 | -0.050354 | 122.0261 | 0.009155 | 122.0169 | -122.113 | -122.1817 | 0.041199 | 122.0078 | -0.045777 | 0.48523
2267.8906 | 122.2549 | -0.11444 | 122.1222 | -0.089798 | -0.045594 | 0.0034456 | 0.028705 | -0.00020513 | -0.0073252 | -0.0030141 | -0.064972 | 0.0059515 | 0.066413 | 0.049191 | -0.015806 | 0.027194 | -0.0055799 | -0.13733 | -0.018311 | -0.036621 | -0.10529 | -0.018311 | -0.086975 | -0.022888 | 0.37994 | 121.9666 | -0.11902 | 121.8567 | 0.045776 | -0.013733 | 0.041199 | 0.07782 | -122.1405 | -122.2275 | 0.09613 | 0.091553 | 0.027466 | 0.013733 | -0.050354 | -0.004578 | -0.15564 | -0.2655 | 0.16022 | 0.15564 | 0.10071 | 0.16022 | 0.10529 | 0.01831 | -0.068665 | 0.16479 | 121.9757 | 0.01831 | 122.0856 | 0.09613 | 122.081 | -122.1588 | -122.2412 | 0.009155 | 121.9711 | -0.022888 | 0.49439
2269.6406 | 122.287 | -0.07782 | 122.0627 | -0.15083 | -0.044525 | 0.0036594 | 0.022937 | -0.0019141 | -0.008607 | -0.0040823 | 0.0021667 | 0.0074469 | 0.063209 | 0.040219 | -0.015592 | 0.027408 | -0.0025891 | -0.11902 | -0.041199 | -0.013733 | -0.041199 | 0.054932 | -0.054932 | 0.032043 | 0.33875 | 121.9757 | -0.09613 | 121.8887 | 0.073242 | 0.059509 | 0.091553 | 0.064087 | -122.1039 | -122.1039 | 0.13275 | 0.10986 | 0.022888 | 0.045776 | -0.041199 | -0.01831 | -0.086975 | -0.17395 | 0.15106 | 0.16937 | 0.13733 | 0.18768 | 0.15564 | 0.068665 | -0.027466 | 0.16937 | 121.9849 | -0.027466 | 122.0718 | 0.036621 | 122.0535 | -122.0764 | -122.1588 | 0.036621 | 121.9666 | -0.041199 | 0.41657
2271.3281 | 122.3007 | -0.082397 | 122.0856 | -0.16609 | -0.044953 | 0.003232 | 0.026782 | -0.0076819 | -0.007966 | -0.0032277 | -0.0069885 | 0.0040289 | 0.063423 | 0.047909 | -0.019224 | 0.027621 | -0.0062207 | -0.1236 | -0.050354 | -0.013733 | -0.050354 | 0.054932 | -0.050354 | 0.032043 | 0.35706 | 121.962 | -0.082397 | 121.9254 | 0.10071 | 0.073242 | 0.11444 | 0.068664 | -122.1359 | -122.1359 | 0.13733 | 0.11444 | 0.032043 | 0.045776 | -0.036621 | 0 | -0.1236 | -0.16022 | 0.18311 | 0.19684 | 0.15564 | 0.19684 | 0.15564 | 0.068665 | -0.036621 | 0.18311 | 122.0078 | -0.036621 | 122.0444 | 0.032043 | 122.0444 | -122.0993 | -122.168 | 0.032043 | 122.0078 | -0.041199 | 0.43945
2273.0781 | 122.2 | -0.12817 | 122.1176 | -0.044022 | -0.047303 | 0.001523 | 0.026568 | -0.0076819 | -0.010743 | -0.0019461 | -0.040558 | 0.0048833 | 0.06385 | 0.052823 | -0.016447 | 0.027835 | -0.0032299 | -0.16022 | -0.027466 | -0.050354 | -0.10529 | -0.022888 | -0.11902 | -0.041199 | 0.3891 | 121.994 | -0.10529 | 121.8292 | 0.022888 | -0.022888 | 0 | 0.07782 | -122.1451 | -122.2229 | 0.10529 | 0.086975 | 0.009155 | 0.009155 | -0.068665 | 0.022888 | -0.1236 | -0.28839 | 0.15106 | 0.12817 | 0.10529 | 0.10529 | 0.082398 | 0.027466 | -0.054932 | 0.12817 | 121.9345 | 0.022888 | 122.0993 | 0.10071 | 122.1222 | -122.168 | -122.2229 | 0.022888 | 121.9574 | -0.032043 | 0.51727
2274.8438 | 122.2504 | -0.11444 | 122.1176 | -0.10506 | -0.046234 | 0.00088223 | 0.027423 | 0.00022207 | -0.0081796 | -0.0034415 | -0.074127 | 0.0059515 | 0.065132 | 0.046414 | -0.01666 | 0.02634 | -0.0070751 | -0.13733 | -0.009155 | -0.068665 | -0.10529 | -0.027466 | -0.11444 | -0.050354 | 0.36163 | 122.0032 | -0.11444 | 121.8567 | 0.027466 | -0.013733 | 0.027466 | 0.045776 | -122.1268 | -122.2229 | 0.086975 | 0.064087 | 0 | 0.018311 | -0.045776 | 0 | -0.11444 | -0.26093 | 0.14191 | 0.14191 | 0.10071 | 0.14191 | 0.10071 | 0.041199 | -0.036621 | 0.14191 | 121.9711 | 0.05951 | 122.1176 | 0.10529 | 122.1176 | -122.1863 | -122.2321 | 0.009155 | 121.9711 | -0.022888 | 0.47607
2276.6094 | 122.2 | -0.13733 | 122.1405 | -0.051651 | -0.047089 | 0.0025912 | 0.026782 | 0.00043587 | -0.010957 | -0.0060049 | -0.046661 | 0.0065923 | 0.064704 | 0.052395 | -0.012602 | 0.026981 | -0.0045117 | -0.14648 | -0.022888 | -0.050354 | -0.11444 | -0.018311 | -0.11444 | -0.018311 | 0.39368 | 121.994 | -0.12817 | 121.8292 | 0.004578 | -0.045776 | 0.013733 | 0.086975 | -122.1634 | -122.2549 | 0.11902 | 0.11902 | 0.022888 | 0.032043 | -0.064087 | 0.009155 | -0.14648 | -0.31128 | 0.14191 | 0.15106 | 0.091553 | 0.14191 | 0.082398 | 0.032043 | -0.064087 | 0.13275 | 121.9574 | 0.027466 | 122.1222 | 0.11444 | 122.1313 | -122.1909 | -122.2687 | 0.022888 | 121.9666 | -0.009155 | 0.53101
2278.375 | 122.2961 | -0.10071 | 122.081 | -0.16609 | -0.041962 | 0.003232 | 0.023578 | -0.00041873 | -0.0090342 | -0.0023733 | -0.0069885 | 0.0061651 | 0.065345 | 0.047482 | -0.015806 | 0.027194 | -0.0051525 | -0.082397 | -0.059509 | -0.027466 | -0.018311 | 0.10071 | -0.036621 | 0.027466 | 0.35248 | 121.962 | -0.09613 | 121.9116 | 0.091553 | 0.054932 | 0.091553 | 0.073242 | -122.1405 | -122.0993 | 0.20142 | 0.12817 | 0.064087 | 0.054932 | -0.009155 | 0.004578 | -0.11902 | -0.16937 | 0.19226 | 0.19226 | 0.15564 | 0.18768 | 0.15106 | 0.12817 | 0.009155 | 0.18768 | 122.0078 | -0.032043 | 122.0581 | 0.041199 | 122.0627 | -122.1085 | -122.1771 | 0.082397 | 122.0123 | 0.018311 | 0.45319
2280.1406 | 122.2778 | -0.086975 | 122.0718 | -0.15846 | -0.044525 | 0.0040866 | 0.025927 | -0.0034095 | -0.0092478 | -0.0021597 | -0.016144 | 0.0053107 | 0.064704 | 0.048337 | -0.016447 | 0.027408 | -0.0049389 | -0.10529 | -0.064087 | -0.022888 | -0.018311 | 0.086975 | -0.054932 | 0.036621 | 0.3479 | 121.9528 | -0.091553 | 121.9208 | 0.082397 | 0.059509 | 0.09613 | 0.064087 | -122.1359 | -122.0901 | 0.17395 | 0.1236 | 0.032043 | 0.059509 | -0.032044 | -0.004578 | -0.11902 | -0.15106 | 0.16937 | 0.1831 | 0.14648 | 0.18768 | 0.15106 | 0.10986 | 0.004577 | 0.17395 | 122.0123 | -0.041199 | 122.0444 | 0.022888 | 122.0398 | -122.0947 | -122.1634 | 0.068664 | 122.0078 | -0.018311 | 0.43488
2281.8281 | 122.3328 | -0.073242 | 122.0901 | -0.2195 | -0.046021 | 0.0053684 | 0.025714 | 0.0036401 | -0.0066844 | -0.0028005 | -0.052765 | 0.0057379 | 0.062568 | 0.053464 | -0.016874 | 0.02634 | -0.0023755 | -0.064087 | -0.064087 | 0 | 0.018311 | 0.11902 | -0.022888 | 0.045776 | 0.37994 | 121.9574 | -0.091553 | 121.9711 | 0.13733 | 0.091553 | 0.14191 | 0.073242 | -122.1542 | -122.0718 | 0.19226 | 0.11902 | 0.050354 | 0.045776 | -0.022888 | -0.018311 | -0.13275 | -0.11902 | 0.21057 | 0.21515 | 0.16479 | 0.23346 | 0.18311 | 0.11902 | 0.018311 | 0.22888 | 122.0627 | -0.064087 | 122.049 | 0.009155 | 122.0306 | -122.0901 | -122.1817 | 0.091553 | 122.0444 | 0.009155 | 0.45319
2283.5781 | 122.3602 | -0.059509 | 122.0627 | -0.11269 | -0.04538 | 0.0030184 | 0.0255 | -0.0010595 | -0.010316 | -0.0025869 | -0.01004 | 0.0048833 | 0.063423 | 0.051968 | -0.014738 | 0.027194 | -0.0072889 | -0.091553 | -0.059509 | -0.022888 | 0.027466 | 0.14648 | 0.018311 | 0.09613 | 0.52643 | 121.9437 | -0.07782 | 121.9711 | 0.17395 | 0.12817 | 0.15106 | 0.036621 | -122.1222 | -122.0352 | 0.20599 | 0.15564 | 0.07782 | 0.11902 | 0.041199 | -0.018311 | -0.11902 | -0.091553 | 0.23346 | 0.21057 | 0.18768 | 0.22888 | 0.20599 | 0.16937 | 0.050354 | 0.25177 | 122.049 | -0.036621 | 122.0215 | 0 | 122.0032 | -122.0856 | -122.1405 | 0.086975 | 122.0306 | -0.032044 | 0.58594
2285.3281 | 122.3419 | -0.07782 | 122.081 | -0.19661 | -0.045594 | 0.003232 | 0.027209 | -0.0034095 | -0.0077524 | -0.0023733 | -0.052765 | 0.0046697 | 0.064491 | 0.047482 | -0.017942 | 0.027194 | -0.0042981 | -0.054932 | -0.082397 | -0.004578 | 0.032043 | 0.13275 | -0.022888 | 0.059509 | 0.37537 | 121.9482 | -0.059509 | 121.9757 | 0.13275 | 0.09613 | 0.13733 | 0.073242 | -122.1634 | -122.049 | 0.21057 | 0.13733 | 0.054932 | 0.064087 | -0.01831 | 0.018311 | -0.13275 | -0.10529 | 0.21057 | 0.21515 | 0.17395 | 0.19684 | 0.15564 | 0.13733 | 0.036621 | 0.19226 | 122.0352 | -0.077819 | 122.0078 | -0.004577 | 122.0261 | -122.0856 | -122.1405 | 0.10986 | 122.0535 | 0.022888 | 0.45319
2287.0781 | 122.3419 | -0.10071 | 122.0856 | -0.19661 | -0.047516 | 0.0019504 | 0.025287 | -0.0025549 | -0.0094614 | -0.0040823 | -0.0039367 | 0.0055243 | 0.065345 | 0.044919 | -0.015806 | 0.026126 | -0.0047253 | -0.11444 | -0.059509 | -0.022888 | -0.004578 | 0.10986 | -0.009155 | 0.064087 | 0.46234 | 121.9482 | -0.086975 | 121.9666 | 0.13733 | 0.1236 | 0.12817 | 0.07782 | -122.1451 | -122.0901 | 0.21057 | 0.1648 | 0.091553 | 0.086975 | 0.013733 | 0.013733 | -0.13733 | -0.11902 | 0.23804 | 0.22888 | 0.2243 | 0.21515 | 0.21057 | 0.13275 | 0.01831 | 0.2243 | 122.0535 | -0.036621 | 122.0352 | 0.041199 | 122.0489 | -122.1085 | -122.1725 | 0.09613 | 122.0673 | -0.013733 | 0.56305
2288.8438 | 122.2275 | -0.11444 | 122.113 | -0.15846 | -0.044525 | 0.0010958 | 0.027636 | -0.00084593 | -0.009675 | -0.0032277 | -0.12296 | 0.0063787 | 0.064704 | 0.050259 | -0.016874 | 0.02869 | -0.0060071 | -0.09613 | -0.036621 | -0.054932 | -0.041199 | 0.054932 | -0.09613 | -0.022888 | 0.37537 | 122.0078 | -0.09613 | 121.8796 | 0.041199 | -0.027466 | 0.036621 | 0.059509 | -122.1497 | -122.1542 | 0.16937 | 0.091553 | 0.018311 | 0.032044 | -0.041198 | 0.018311 | -0.10529 | -0.23346 | 0.15564 | 0.15106 | 0.086975 | 0.13275 | 0.068664 | 0.10986 | 0.013733 | 0.13733 | 121.9757 | 0.018311 | 122.1039 | 0.07782 | 122.1222 | -122.168 | -122.2092 | 0.073242 | 121.994 | 0.018311 | 0.48981
2290.5312 | 122.2275 | -0.10986 | 122.1268 | -0.11269 | -0.043671 | 0.0043002 | 0.027209 | -0.0034095 | -0.010316 | -0.0038687 | -0.13211 | 0.0063787 | 0.065986 | 0.049405 | -0.015379 | 0.026767 | -0.0042981 | -0.09613 | -0.045776 | -0.032043 | -0.041199 | 0.045776 | -0.07782 | -0.004578 | 0.39825 | 121.994 | -0.091553 | 121.8933 | 0.054932 | -0.013733 | 0.059509 | 0.07782 | -122.1725 | -122.168 | 0.15564 | 0.10529 | 0.032043 | 0.027465 | -0.045777 | 0.01831 | -0.13275 | -0.23346 | 0.16479 | 0.16937 | 0.09613 | 0.15106 | 0.07782 | 0.077819 | -0.009156 | 0.14649 | 121.9849 | -0.013733 | 122.0856 | 0.064087 | 122.1039 | -122.1588 | -122.2183 | 0.068664 | 122.0032 | 0.013733 | 0.50812
2292.2812 | 122.319 | -0.064087 | 122.081 | -0.1432 | -0.04538 | 2.7834e-05 | 0.022509 | 8.47e-06 | -0.0092478 | -0.0034415 | -0.0008851 | 0.0044561 | 0.063209 | 0.047482 | -0.012174 | 0.026981 | -0.0030163 | -0.068665 | -0.054932 | -0.032043 | 0.027466 | 0.16022 | 0.013733 | 0.082397 | 0.54474 | 121.9437 | -0.09613 | 121.9528 | 0.16479 | 0.13275 | 0.14648 | 0.032044 | -122.1359 | -122.0535 | 0.2243 | 0.14648 | 0.07782 | 0.11444 | 0.045776 | -0.032043 | -0.13733 | -0.12817 | 0.22888 | 0.21057 | 0.19684 | 0.24261 | 0.22888 | 0.19226 | 0.059509 | 0.26092 | 122.049 | -0.022889 | 122.0398 | 0.009155 | 122.0078 | -122.113 | -122.1771 | 0.091553 | 122.0169 | -0.004578 | 0.60883
2294.0312 | 122.3145 | -0.086975 | 122.0901 | -0.12794 | -0.04773 | 0.002164 | 0.025927 | -0.00041873 | -0.0088206 | -0.0017325 | -0.034454 | 0.0046697 | 0.064063 | 0.048977 | -0.015165 | 0.027835 | -2.571e-05 | -0.07782 | -0.068665 | -0.018311 | 0.032043 | 0.1236 | -0.013733 | 0.064087 | 0.50354 | 121.9666 | -0.07782 | 121.9437 | 0.13733 | 0.10071 | 0.11444 | 0.068664 | -122.1588 | -122.0581 | 0.21057 | 0.15106 | 0.073242 | 0.082398 | 0.004578 | 0.009155 | -0.1236 | -0.14648 | 0.2243 | 0.20142 | 0.18768 | 0.19226 | 0.17853 | 0.14191 | 0.050354 | 0.21515 | 122.0215 | -0.050354 | 122.0444 | 0.01831 | 122.0535 | -122.1085 | -122.168 | 0.11902 | 122.0306 | 0.009155 | 0.59052
2295.7188 | 122.2229 | -0.12817 | 122.1085 | -0.097427 | -0.045807 | 0.001523 | 0.024218 | -0.0014867 | -0.009675 | -0.0023733 | -0.025299 | 0.0057379 | 0.063423 | 0.046841 | -0.015165 | 0.026126 | -0.0015209 | -0.15106 | -0.032043 | -0.050354 | -0.091553 | -0.004578 | -0.10071 | -0.022888 | 0.39825 | 122.0169 | -0.11902 | 121.8338 | 0.009155 | -0.018311 | 0.004578 | 0.07782 | -122.1405 | -122.2 | 0.1236 | 0.10529 | 0.027466 | 0.027466 | -0.050354 | 0.009155 | -0.091552 | -0.27466 | 0.13733 | 0.13275 | 0.10986 | 0.1236 | 0.10071 | 0.045776 | -0.041199 | 0.12817 | 121.9528 | 0.018311 | 122.1359 | 0.096131 | 122.1451 | -122.1588 | -122.2275 | 0.036621 | 121.962 | -0.022888 | 0.52643
2297.4688 | 122.2229 | -0.1236 | 122.1039 | -0.15846 | -0.043457 | 0.0053684 | 0.028918 | 0.0029993 | -0.0090342 | -0.0021597 | -0.11685 | 0.0048833 | 0.064277 | 0.047268 | -0.016233 | 0.027835 | -0.0075025 | -0.12817 | -0.004578 | -0.050354 | -0.11444 | -0.050354 | -0.16022 | -0.073242 | 0.21515 | 122.0078 | -0.10529 | 121.8613 | 0.009155 | -0.059509 | 0.013733 | 0.073242 | -122.1085 | -122.2183 | 0.073242 | 0.050354 | -0.036621 | -0.022888 | -0.10986 | 0.01831 | -0.096131 | -0.24262 | 0.13275 | 0.13733 | 0.064087 | 0.11902 | 0.045777 | 0 | -0.064087 | 0.11444 | 121.9666 | 0.045776 | 122.113 | 0.11902 | 122.1313 | -122.1542 | -122.2092 | 0.009155 | 121.9849 | -0.004578 | 0.33875
2299.2344 | 122.2961 | -0.07782 | 122.1039 | -0.12794 | -0.044525 | 0.003873 | 0.023578 | -0.0023413 | -0.0081796 | -0.0051505 | -0.013092 | 0.0057379 | 0.065132 | 0.044278 | -0.015806 | 0.026981 | -0.0057935 | -0.091553 | -0.068665 | -0.013733 | -0.018311 | 0.10529 | -0.045776 | 0.036621 | 0.35706 | 121.9437 | -0.086975 | 121.9162 | 0.10529 | 0.054932 | 0.09613 | 0.064087 | -122.1725 | -122.1222 | 0.18311 | 0.11444 | 0.032044 | 0.050354 | -0.032043 | -0.009155 | -0.16022 | -0.18768 | 0.18311 | 0.17395 | 0.13275 | 0.1831 | 0.14191 | 0.11902 | -0.004578 | 0.19226 | 122.0032 | -0.054932 | 122.0306 | 0.009155 | 122.0215 | -122.1176 | -122.1909 | 0.059509 | 121.994 | -0.013733 | 0.43488
2300.9375 | 122.3145 | -0.09613 | 122.081 | -0.12794 | -0.044312 | 0.0040866 | 0.029132 | -0.0017005 | -0.0066844 | -0.0047231 | -0.10464 | 0.0055243 | 0.065345 | 0.051114 | -0.014951 | 0.028476 | -0.0030163 | -0.13733 | -0.045776 | -0.041199 | -0.073242 | 0.022888 | -0.11902 | -0.027466 | 0.27008 | 122.0032 | -0.10986 | 121.9482 | 0.091553 | 0.045776 | 0.11444 | 0.054931 | -122.1268 | -122.1542 | 0.11902 | 0.068664 | -0.022889 | 0.013733 | -0.07782 | -0.013733 | -0.07782 | -0.13275 | 0.18768 | 0.21057 | 0.14191 | 0.2243 | 0.15564 | 0.064087 | -0.032043 | 0.20142 | 122.0581 | -0.004577 | 122.113 | 0.050354 | 122.0993 | -122.1222 | -122.1909 | 0.022888 | 122.0444 | -0.041199 | 0.36621
2302.6875 | 122.2092 | -0.1236 | 122.1176 | -0.12794 | -0.041748 | 0.0013094 | 0.028918 | -0.0019141 | -0.0073252 | -0.0010915 | -0.1077 | 0.0065923 | 0.064063 | 0.051541 | -0.016874 | 0.026981 | -0.0030163 | -0.14191 | -0.009155 | -0.073242 | -0.11902 | -0.041199 | -0.15564 | -0.07782 | 0.20599 | 122.0169 | -0.10071 | 121.843 | -0.013733 | -0.059509 | 0.013733 | 0.050354 | -122.1268 | -122.2366 | 0.082397 | 0.045776 | -0.032044 | -0.004578 | -0.082398 | 0.022888 | -0.10071 | -0.27466 | 0.10986 | 0.13733 | 0.064087 | 0.11444 | 0.041199 | 0.032043 | -0.045777 | 0.086975 | 121.9437 | 0.064087 | 122.1176 | 0.11444 | 122.1405 | -122.1909 | -122.2183 | 0.004577 | 121.9666 | -0.018311 | 0.32959
2304.4531 | 122.2092 | -0.13275 | 122.1268 | -0.15083 | -0.043457 | 0.0043002 | 0.029132 | 0.0010767 | -0.0077524 | -0.0040823 | -0.12906 | 0.0044561 | 0.065132 | 0.051541 | -0.01602 | 0.028262 | -0.0053661 | -0.16479 | -0.018311 | -0.064087 | -0.11444 | -0.064087 | -0.14191 | -0.059509 | 0.23346 | 121.994 | -0.11444 | 121.8658 | -0.004578 | -0.068665 | 0.013733 | 0.068664 | -122.1451 | -122.2412 | 0.068664 | 0.073242 | -0.009156 | 0.004578 | -0.07782 | 0.01831 | -0.13275 | -0.26093 | 0.12817 | 0.14648 | 0.064086 | 0.12817 | 0.045776 | 0 | -0.050354 | 0.10986 | 121.9803 | 0.045776 | 122.1085 | 0.11444 | 122.1268 | -122.1909 | -122.2412 | 0.01831 | 121.9986 | -0.032044 | 0.36621
2306.2031 | 122.2275 | -0.1236 | 122.1313 | -0.12794 | -0.044312 | 0.0036594 | 0.027209 | 0.0019311 | -0.009675 | -0.0038687 | -0.1199 | 0.0042425 | 0.064063 | 0.047909 | -0.016447 | 0.02869 | -0.0010937 | -0.16479 | -0.027466 | -0.050354 | -0.11902 | -0.045776 | -0.16022 | -0.059509 | 0.2243 | 122.0078 | -0.11444 | 121.8567 | -0.022888 | -0.07782 | 0.013733 | 0.073242 | -122.1588 | -122.2504 | 0.07782 | 0.064087 | -0.036621 | -0.009155 | -0.10986 | 0.009155 | -0.1236 | -0.27466 | 0.10071 | 0.13733 | 0.045776 | 0.12817 | 0.036621 | 0.004578 | -0.068665 | 0.091553 | 121.9711 | 0.022888 | 122.1222 | 0.09613 | 122.1313 | -122.1817 | -122.2458 | 0.004577 | 121.9803 | -0.041199 | 0.3479
2307.9531 | 122.2275 | -0.12817 | 122.1313 | -0.082169 | -0.044953 | 0.0028048 | 0.02785 | -0.00063233 | -0.0098886 | -0.0049367 | -0.064972 | 0.0070197 | 0.064918 | 0.048337 | -0.015165 | 0.028262 | -0.0019483 | -0.14648 | -0.027466 | -0.059509 | -0.10986 | -0.018311 | -0.10986 | -0.032043 | 0.38452 | 122.0398 | -0.1236 | 121.8475 | 0.022888 | -0.036621 | 0.009155 | 0.068665 | -122.1588 | -122.2412 | 0.10986 | 0.096131 | 0.018311 | 0.027466 | -0.050354 | 0.004578 | -0.091553 | -0.28381 | 0.15106 | 0.13733 | 0.091553 | 0.13275 | 0.086975 | 0.041198 | -0.050354 | 0.14648 | 121.9711 | 0.032043 | 122.1634 | 0.10071 | 122.168 | -122.1909 | -122.2549 | 0.018311 | 121.9757 | -0.01831 | 0.5127
2309.6406 | 122.2504 | -0.091553 | 122.1268 | -0.11269 | -0.04538 | 0.0034456 | 0.024218 | -0.00041873 | -0.010743 | -0.0040823 | -0.019196 | 0.0061651 | 0.062141 | 0.046414 | -0.017088 | 0.027194 | -0.0079297 | -0.082397 | -0.064087 | -0.032043 | 0 | 0.10071 | -0.018311 | 0.036621 | 0.48065 | 121.9849 | -0.086975 | 121.8933 | 0.064087 | 0.018311 | 0.045776 | 0.05951 | -122.1909 | -122.1268 | 0.19226 | 0.12817 | 0.073242 | 0.068664 | 0.013732 | 0.004578 | -0.14191 | -0.23346 | 0.15564 | 0.13733 | 0.10986 | 0.13275 | 0.10529 | 0.13275 | 0.032043 | 0.15106 | 121.9803 | -0.032044 | 122.0718 | 0.027466 | 122.0764 | -122.1588 | -122.2137 | 0.091553 | 121.9849 | 0.009156 | 0.57221
2311.3906 | 122.3373 | -0.068665 | 122.0718 | -0.12032 | -0.041107 | 0.005582 | 0.026782 | 0.0025721 | -0.0060434 | -0.0036551 | -0.052765 | 0.0055243 | 0.06385 | 0.051327 | -0.015379 | 0.026767 | -0.0051525 | -0.11444 | -0.041199 | -0.027466 | -0.036621 | 0.068665 | -0.068665 | 0.004578 | 0.33875 | 121.962 | -0.082397 | 121.9757 | 0.1236 | 0.07782 | 0.14191 | 0.041199 | -122.113 | -122.1085 | 0.13733 | 0.073243 | 0 | 0.032044 | -0.041199 | -0.013732 | -0.10986 | -0.09613 | 0.19226 | 0.21057 | 0.14649 | 0.2243 | 0.16022 | 0.096131 | -0.009155 | 0.20599 | 122.0581 | -0.013733 | 122.0444 | 0.027466 | 122.0306 | -122.0993 | -122.1542 | 0.032044 | 122.0444 | -0.045776 | 0.40741
2313.1406 | 122.2595 | -0.09613 | 122.1313 | -0.12032 | -0.04538 | 0.0034456 | 0.027209 | -0.0017005 | -0.0092478 | -0.00023714 | -0.064972 | 0.0061651 | 0.062782 | 0.048123 | -0.017088 | 0.026553 | -0.0068615 | -0.10986 | -0.032043 | -0.059509 | -0.059509 | 0.022888 | -0.073242 | -0.004578 | 0.4303 | 122.0032 | -0.09613 | 121.8933 | 0.068665 | 0 | 0.054932 | 0.036621 | -122.1634 | -122.1909 | 0.11902 | 0.091552 | 0.022888 | 0.054931 | -0.013733 | 0 | -0.12817 | -0.23804 | 0.16479 | 0.15106 | 0.09613 | 0.15106 | 0.09613 | 0.082397 | 0 | 0.16479 | 121.9894 | 0.027466 | 122.0993 | 0.064087 | 122.0993 | -122.1909 | -122.2275 | 0.036621 | 121.9894 | -0.013733 | 0.52643
2314.8438 | 122.2229 | -0.1236 | 122.1268 | -0.028763 | -0.044312 | 0.003232 | 0.029345 | -0.00041873 | -0.0064706 | -0.0021597 | -0.10464 | 0.0053107 | 0.065559 | 0.050686 | -0.014524 | 0.028476 | -0.0049389 | -0.10529 | -0.032043 | -0.036621 | -0.059509 | 0.022888 | -0.11444 | -0.036621 | 0.34332 | 122.0215 | -0.091553 | 121.8796 | 0.018311 | -0.045776 | 0.018311 | 0.086975 | -122.1588 | -122.1863 | 0.14648 | 0.086975 | 0.009155 | 0 | -0.07782 | 0.032043 | -0.10529 | -0.24719 | 0.14191 | 0.14191 | 0.07782 | 0.10986 | 0.045777 | 0.059509 | -0.022888 | 0.10986 | 121.9711 | 0.004578 | 122.113 | 0.091553 | 122.1451 | -122.1634 | -122.2183 | 0.064087 | 122.0032 | 0.01831 | 0.46692
2316.5938 | 122.3557 | -0.073242 | 122.0718 | -0.12794 | -0.047089 | 0.0019504 | 0.022296 | -0.0044775 | -0.0073252 | -0.0040823 | 0.023529 | 0.0046697 | 0.063423 | 0.045346 | -0.014951 | 0.026981 | -0.0049389 | -0.086975 | -0.068665 | -0.018311 | 0.004578 | 0.12817 | 0.022888 | 0.091553 | 0.49896 | 121.9528 | -0.07782 | 121.9849 | 0.17853 | 0.13275 | 0.15106 | 0.054931 | -122.1405 | -122.0673 | 0.20142 | 0.16479 | 0.09613 | 0.10986 | 0.041199 | -0.004578 | -0.11902 | -0.086975 | 0.25177 | 0.2243 | 0.20599 | 0.22888 | 0.21057 | 0.14649 | 0.022889 | 0.25635 | 122.0627 | -0.050354 | 122.0306 | 0.004577 | 122.0261 | -122.0901 | -122.1497 | 0.07782 | 122.0581 | -0.013733 | 0.5722
2318.3438 | 122.2275 | -0.14191 | 122.1313 | -0.082169 | -0.046021 | 0.003232 | 0.024218 | -0.0010595 | -0.009675 | -0.0036551 | -0.064972 | 0.0042425 | 0.060432 | 0.052823 | -0.014311 | 0.028476 | -0.0085705 | -0.16479 | -0.013733 | -0.059509 | -0.11902 | -0.022888 | -0.11444 | -0.045776 | 0.39368 | 122.0306 | -0.11902 | 121.8521 | 0.009155 | -0.036621 | 0.018311 | 0.082398 | -122.1451 | -122.2504 | 0.11902 | 0.096131 | 0.027466 | 0.013733 | -0.054932 | 0.022888 | -0.10071 | -0.27924 | 0.15106 | 0.16022 | 0.10529 | 0.13733 | 0.082398 | 0.036621 | -0.05951 | 0.12817 | 121.9711 | 0.045776 | 122.1497 | 0.12817 | 122.1725 | -122.1909 | -122.2504 | 0.022888 | 121.994 | -0.022888 | 0.53558
2320.1094 | 122.2275 | -0.10529 | 122.1176 | -0.16609 | -0.046021 | 0.003873 | 0.026568 | -0.0012731 | -0.0071116 | -0.0040823 | -0.089386 | 0.0070197 | 0.063209 | 0.052395 | -0.017515 | 0.026767 | -0.00066651 | -0.13733 | -0.004578 | -0.041199 | -0.10986 | -0.032043 | -0.14648 | -0.054932 | 0.2243 | 122.0032 | -0.11444 | 121.8658 | 0.009155 | -0.041199 | 0.022888 | 0.064087 | -122.1222 | -122.2275 | 0.073243 | 0.050354 | -0.041198 | -0.013733 | -0.10529 | -0.009155 | -0.11444 | -0.25177 | 0.11444 | 0.12817 | 0.064087 | 0.13733 | 0.073242 | 0.009156 | -0.068664 | 0.1236 | 121.9803 | 0.036621 | 122.1176 | 0.10071 | 122.1085 | -122.1588 | -122.2321 | -0.004577 | 121.9711 | -0.032043 | 0.32959
2321.8125 | 122.2687 | -0.11444 | 122.1176 | -0.1432 | -0.04303 | 0.003232 | 0.027636 | 0.00086307 | -0.0098886 | -0.0019461 | -0.083283 | 0.0063787 | 0.063423 | 0.053464 | -0.015379 | 0.027408 | -0.0034435 | -0.10529 | -0.032043 | -0.054932 | -0.059509 | 0.045776 | -0.054932 | -0.013733 | 0.42572 | 122.0169 | -0.10071 | 121.907 | 0.073242 | 0.022888 | 0.068665 | 0.059509 | -122.1497 | -122.1771 | 0.16022 | 0.10071 | 0.059509 | 0.041199 | 0 | 0.013733 | -0.10071 | -0.21057 | 0.18768 | 0.18311 | 0.13733 | 0.16937 | 0.1236 | 0.10071 | -0.004577 | 0.17395 | 122.0078 | 0.022889 | 122.1176 | 0.082398 | 122.1313 | -122.1725 | -122.2183 | 0.054932 | 122.0215 | 0.009155 | 0.54016
2323.5625 | 122.2275 | -0.11902 | 122.1542 | -0.082169 | -0.044312 | 0.0028048 | 0.022937 | -0.0023413 | -0.012025 | -0.0017325 | -0.025299 | 0.0063787 | 0.065986 | 0.044705 | -0.01367 | 0.026981 | -0.0021619 | -0.13733 | -0.036621 | -0.050354 | -0.091553 | 0.013733 | -0.09613 | -0.027466 | 0.40283 | 122.0078 | -0.11444 | 121.8384 | 0.013733 | -0.027466 | -0.013733 | 0.068665 | -122.1909 | -122.2458 | 0.13275 | 0.091553 | 0.022889 | 0.022888 | -0.045776 | 0.004578 | -0.14648 | -0.31586 | 0.13275 | 0.10529 | 0.091553 | 0.10071 | 0.086975 | 0.064087 | -0.041199 | 0.12817 | 121.9528 | 0.013733 | 122.1222 | 0.082398 | 122.1268 | -122.2046 | -122.2687 | 0.027466 | 121.9574 | -0.01831 | 0.52185
2325.2656 | 122.3557 | -0.068665 | 122.0856 | -0.15083 | -0.044312 | 0.0036594 | 0.026355 | -0.0023413 | -0.0092478 | -0.0023733 | -0.055817 | 0.0061651 | 0.062995 | 0.049191 | -0.016233 | 0.028049 | -0.0049389 | -0.086975 | -0.041199 | -0.018311 | -0.009155 | 0.086975 | -0.041199 | 0.050354 | 0.36163 | 121.994 | -0.086975 | 121.9986 | 0.12817 | 0.068665 | 0.14648 | 0.050354 | -122.1268 | -122.0947 | 0.15564 | 0.11902 | 0.027466 | 0.068665 | -0.022888 | -0.01831 | -0.091552 | -0.086975 | 0.19684 | 0.21515 | 0.13733 | 0.23346 | 0.15564 | 0.10529 | 0.009156 | 0.21515 | 122.0856 | -0.022888 | 122.081 | 0.027466 | 122.0627 | -122.1039 | -122.1725 | 0.05951 | 122.0673 | -0.01831 | 0.4303
2327.0156 | 122.2733 | -0.1236 | 122.1405 | -0.06691 | -0.047303 | 0.0036594 | 0.026782 | -0.0025549 | -0.009675 | -0.00066434 | -0.089386 | 0.0055243 | 0.063423 | 0.049191 | -0.015379 | 0.02869 | -0.0025891 | -0.10986 | -0.018311 | -0.045776 | -0.064087 | 0.032043 | -0.059509 | -0.004578 | 0.42114 | 122.0169 | -0.10529 | 121.907 | 0.064087 | 0.018311 | 0.064087 | 0.07782 | -122.1588 | -122.2046 | 0.15564 | 0.11902 | 0.064087 | 0.041198 | -0.013733 | 0.01831 | -0.1236 | -0.23346 | 0.18768 | 0.18768 | 0.14191 | 0.16937 | 0.1236 | 0.077819 | -0.018311 | 0.16937 | 122.0123 | 0.027465 | 122.1222 | 0.10528 | 122.1405 | -122.1863 | -122.2458 | 0.059509 | 122.0306 | 0.013733 | 0.54474
2328.7812 | 122.2275 | -0.12817 | 122.1588 | -0.089798 | -0.046662 | 0.0030184 | 0.0255 | 0.0017175 | -0.010102 | -0.0047231 | -0.04361 | 0.0057379 | 0.064918 | 0.04855 | -0.013883 | 0.028262 | -0.0042981 | -0.15564 | -0.009155 | -0.050354 | -0.11902 | -0.009155 | -0.1236 | -0.027466 | 0.37079 | 122.0123 | -0.10986 | 121.875 | 0.032043 | -0.009155 | 0.018311 | 0.07782 | -122.168 | -122.2778 | 0.11902 | 0.10071 | 0.004578 | 0.022888 | -0.073242 | 0.018311 | -0.14648 | -0.28381 | 0.16022 | 0.14649 | 0.11902 | 0.12817 | 0.10071 | 0.041199 | -0.068665 | 0.14191 | 121.9849 | 0.041199 | 122.1222 | 0.11902 | 122.1405 | -122.2092 | -122.2687 | 0.009155 | 122.0032 | -0.027466 | 0.49896
2330.5312 | 122.2641 | -0.1236 | 122.1451 | -0.13557 | -0.045594 | 0.0025912 | 0.026568 | 0.0040675 | -0.0098886 | -0.0013051 | -0.080231 | 0.0068059 | 0.0662 | 0.049832 | -0.015806 | 0.027408 | -0.0042981 | -0.11444 | -0.018311 | -0.068665 | -0.07782 | 0.018311 | -0.082397 | 0.004578 | 0.40741 | 122.0123 | -0.091553 | 121.9116 | 0.068665 | 0.009155 | 0.068665 | 0.054931 | -122.1634 | -122.2229 | 0.14191 | 0.12817 | 0.041199 | 0.073243 | -0.013732 | 0.032043 | -0.13275 | -0.23346 | 0.19226 | 0.19226 | 0.13275 | 0.16022 | 0.10071 | 0.086976 | -0.009155 | 0.16022 | 122.0032 | 0.050354 | 122.1039 | 0.10528 | 122.1359 | -122.2137 | -122.2366 | 0.045776 | 122.0352 | 0.009155 | 0.53101
2332.2812 | 122.3007 | -0.082397 | 122.1085 | -0.15083 | -0.044525 | 0.0023776 | 0.024859 | 0.0017175 | -0.0094614 | -0.0017325 | 0.011322 | 0.0057379 | 0.064277 | 0.043423 | -0.014951 | 0.026767 | -0.0038709 | -0.11902 | -0.064087 | -0.041199 | -0.050354 | 0.054932 | -0.059509 | 0.032043 | 0.33875 | 121.9803 | -0.091553 | 121.9208 | 0.07782 | 0.045776 | 0.091553 | 0.041198 | -122.1725 | -122.1588 | 0.13733 | 0.11444 | 0.022888 | 0.073242 | -0.01831 | -0.009156 | -0.12817 | -0.18768 | 0.16022 | 0.17395 | 0.12817 | 0.18311 | 0.13733 | 0.096131 | -0.009155 | 0.16937 | 122.0123 | -0.022888 | 122.0718 | 0.01831 | 122.0627 | -122.1497 | -122.2 | 0.032043 | 122.0032 | -0.036622 | 0.42114
2333.9688 | 122.3053 | -0.064087 | 122.113 | -0.15846 | -0.04538 | 0.0043002 | 0.02315 | 0.00022207 | -0.0094614 | -0.0023733 | -0.01004 | 0.0042425 | 0.064918 | 0.047696 | -0.016874 | 0.025058 | -0.0066479 | -0.10071 | -0.054932 | -0.009155 | -0.027466 | 0.082397 | -0.054932 | 0.041199 | 0.34332 | 121.9849 | -0.09613 | 121.9299 | 0.091553 | 0.059509 | 0.10071 | 0.054932 | -122.168 | -122.1405 | 0.14648 | 0.10529 | 0.009155 | 0.050354 | -0.045777 | -0.032043 | -0.12817 | -0.18311 | 0.15564 | 0.1648 | 0.1236 | 0.19684 | 0.15564 | 0.091552 | -0.018311 | 0.18768 | 122.0261 | -0.045777 | 122.081 | 0.009155 | 122.049 | -122.1222 | -122.2092 | 0.036621 | 121.994 | -0.036621 | 0.40741
2335.7344 | 122.2458 | -0.12817 | 122.1588 | -0.10506 | -0.046662 | 0.0030184 | 0.0255 | -0.0061865 | -0.01053 | -0.0030141 | -0.037506 | 0.0050971 | 0.0662 | 0.046628 | -0.016233 | 0.028049 | -0.00045291 | -0.091553 | -0.059509 | -0.027466 | -0.073242 | 0.036621 | -0.07782 | -0.004578 | 0.43488 | 122.0078 | -0.10529 | 121.8613 | 0.032043 | -0.009155 | 0.004578 | 0.10071 | -122.2183 | -122.2321 | 0.1648 | 0.1236 | 0.050354 | 0.022888 | -0.050354 | 0.022888 | -0.15106 | -0.29755 | 0.16022 | 0.13275 | 0.11902 | 0.10986 | 0.096131 | 0.064087 | -0.045776 | 0.13733 | 121.9666 | -0.032043 | 122.113 | 0.068665 | 122.1359 | -122.1863 | -122.2641 | 0.054932 | 121.9894 | 0.036621 | 0.56305
2337.4844 | 122.2961 | -0.09613 | 122.1085 | -0.17372 | -0.047303 | 0.0047274 | 0.024432 | 0.00086307 | -0.0088206 | -0.0060049 | -0.0039367 | 0.0044561 | 0.064277 | 0.0462 | -0.018797 | 0.025699 | -0.0070751 | -0.11444 | -0.050354 | -0.036621 | -0.036621 | 0.050354 | -0.064087 | 0.018311 | 0.36163 | 122.0078 | -0.07782 | 121.9162 | 0.082397 | 0.054932 | 0.091553 | 0.059509 | -122.1588 | -122.1451 | 0.14648 | 0.11444 | 0.032043 | 0.054932 | -0.027466 | 0.01831 | -0.10071 | -0.19226 | 0.17853 | 0.18768 | 0.15106 | 0.16937 | 0.13275 | 0.086975 | 0 | 0.16022 | 121.994 | -0.013733 | 122.0856 | 0.045776 | 122.1039 | -122.1451 | -122.1863 | 0.059509 | 122.0123 | -0.018311 | 0.45776
2339.2344 | 122.2412 | -0.1236 | 122.1405 | -0.15846 | -0.042389 | 0.004941 | 0.027209 | -0.0010595 | -0.0098886 | -0.0028005 | -0.10464 | 0.0057379 | 0.065132 | 0.057736 | -0.01602 | 0.029544 | -0.0034435 | -0.10529 | -0.022888 | -0.041199 | -0.054932 | 0.022888 | -0.09613 | -0.032043 | 0.3479 | 122.0215 | -0.07782 | 121.8796 | 0.018311 | -0.045776 | 0.036621 | 0.082397 | -122.1634 | -122.1954 | 0.14648 | 0.091553 | 0.027466 | 0.009156 | -0.054931 | 0.045776 | -0.11902 | -0.26093 | 0.14191 | 0.16022 | 0.07782 | 0.11444 | 0.032044 | 0.064087 | -0.013733 | 0.096131 | 121.9574 | 0.018311 | 122.0993 | 0.10071 | 122.1451 | -122.1817 | -122.2183 | 0.068664 | 122.0032 | 0.01831 | 0.4715
2340.9375 | 122.2275 | -0.1236 | 122.1222 | -0.044022 | -0.047303 | 0.0028048 | 0.026996 | -0.0017005 | -0.010957 | -0.0030141 | -0.080231 | 0.0068059 | 0.064277 | 0.051968 | -0.015806 | 0.026126 | -0.0045117 | -0.16479 | -0.004578 | -0.059509 | -0.10529 | -0.018311 | -0.11444 | -0.022888 | 0.41199 | 122.0261 | -0.13275 | 121.8567 | 0.009155 | -0.032043 | 0.013733 | 0.064087 | -122.1268 | -122.2275 | 0.10528 | 0.10071 | 0.009155 | 0.036621 | -0.054932 | -0.009155 | -0.09613 | -0.2655 | 0.13275 | 0.13733 | 0.091553 | 0.14648 | 0.10071 | 0.041198 | -0.045777 | 0.14191 | 121.9894 | 0.054931 | 122.1588 | 0.11902 | 122.1497 | -122.1817 | -122.2549 | 0.01831 | 121.9803 | -0.041199 | 0.53558
2342.6875 | 122.2961 | -0.086975 | 122.1176 | -0.074539 | -0.044953 | 0.00088223 | 0.024218 | 0.0010767 | -0.0090342 | -0.0019461 | -0.028351 | 0.0068059 | 0.063423 | 0.050046 | -0.014524 | 0.025058 | -0.0040845 | -0.10529 | -0.054932 | -0.009155 | -0.036621 | 0.059509 | -0.064087 | 0.032043 | 0.35706 | 121.9711 | -0.10071 | 121.9482 | 0.086975 | 0.054932 | 0.07782 | 0.07782 | -122.1725 | -122.1542 | 0.14648 | 0.11902 | 0.022888 | 0.041198 | -0.054932 | -0.013733 | -0.14648 | -0.16937 | 0.17395 | 0.16479 | 0.14191 | 0.17853 | 0.15564 | 0.068664 | -0.027466 | 0.18768 | 122.0489 | -0.045777 | 122.0718 | 0.032043 | 122.0581 | -122.1268 | -122.2183 | 0.050354 | 122.0352 | -0.018311 | 0.44403
2344.4375 | 122.3465 | -0.068665 | 122.081 | -0.12032 | -0.042603 | 0.0040866 | 0.026996 | -0.00063233 | -0.0094614 | -0.0062185 | -0.077179 | 0.0048833 | 0.064063 | 0.046841 | -0.016233 | 0.027194 | -0.0047253 | -0.054932 | -0.059509 | -0.032043 | 0.018311 | 0.10071 | -0.027466 | 0.059509 | 0.3891 | 121.9894 | -0.073242 | 121.994 | 0.14648 | 0.10071 | 0.16022 | 0.036622 | -122.1405 | -122.0627 | 0.16937 | 0.12817 | 0.041199 | 0.091552 | 0.004577 | -0.004577 | -0.091553 | -0.086975 | 0.21515 | 0.22888 | 0.16937 | 0.23346 | 0.17395 | 0.13275 | 0.050354 | 0.21973 | 122.0673 | -0.027466 | 122.0627 | 0.009156 | 122.0581 | -122.113 | -122.1542 | 0.086976 | 122.0627 | 0.013733 | 0.45776
2346.2188 | 122.2733 | -0.1236 | 122.1405 | -0.13557 | -0.046448 | 2.7834e-05 | 0.026996 | -0.00084593 | -0.0075388 | -0.0032277 | -0.074127 | 0.0050971 | 0.063209 | 0.051114 | -0.017301 | 0.027408 | -0.0083569 | -0.15564 | -0.013733 | -0.045776 | -0.10986 | -0.018311 | -0.09613 | -0.041199 | 0.39825 | 122.0444 | -0.10986 | 121.907 | 0.032043 | -0.022888 | 0.032043 | 0.07782 | -122.1542 | -122.2504 | 0.10528 | 0.082397 | 0.027466 | 0.004577 | -0.050354 | 0.013733 | -0.09613 | -0.23346 | 0.15564 | 0.15564 | 0.10071 | 0.14191 | 0.086975 | 0.027465 | -0.064087 | 0.14191 | 122.0169 | 0.032043 | 122.1542 | 0.10986 | 122.168 | -122.1863 | -122.2504 | 0.013733 | 122.0306 | -0.032044 | 0.52185
2347.9062 | 122.2412 | -0.12817 | 122.113 | -0.10506 | -0.044739 | 0.0025912 | 0.026355 | -0.0014867 | -0.01117 | -0.0036551 | -0.074127 | 0.0061651 | 0.065132 | 0.041501 | -0.015165 | 0.027835 | -0.0036573 | -0.15106 | -0.004578 | -0.054932 | -0.10071 | -0.032043 | -0.10071 | -0.027466 | 0.3891 | 122.0535 | -0.10529 | 121.9025 | 0.036621 | -0.027466 | 0.027466 | 0.073242 | -122.1176 | -122.2137 | 0.096131 | 0.10071 | 0.027466 | 0.027466 | -0.045776 | 0.022888 | -0.059509 | -0.21057 | 0.1648 | 0.15564 | 0.10071 | 0.13275 | 0.07782 | 0.022889 | -0.045776 | 0.14191 | 122.0078 | 0.050354 | 122.1588 | 0.1236 | 122.1817 | -122.168 | -122.2183 | 0.027466 | 122.0306 | -0.022888 | 0.51727
2349.6406 | 122.3602 | -0.054932 | 122.1222 | -0.16609 | -0.045594 | 0.0047274 | 0.025073 | 0.0012903 | -0.01053 | -0.0025869 | -0.064972 | 0.0044561 | 0.063209 | 0.044705 | -0.015379 | 0.026126 | -0.0038709 | -0.07782 | -0.059509 | 0.004578 | 0.013733 | 0.13733 | -0.032043 | 0.064087 | 0.38452 | 121.994 | -0.07782 | 121.9986 | 0.14191 | 0.091553 | 0.15106 | 0.05951 | -122.1817 | -122.1085 | 0.19226 | 0.11902 | 0.022889 | 0.059509 | -0.036621 | -0.022888 | -0.12817 | -0.1236 | 0.19684 | 0.20599 | 0.14649 | 0.22888 | 0.16937 | 0.13275 | 0.009155 | 0.21973 | 122.0764 | -0.064087 | 122.0718 | -0.004577 | 122.049 | -122.1176 | -122.2 | 0.068665 | 122.0535 | -0.022888 | 0.43945
2351.3906 | 122.2412 | -0.09613 | 122.1359 | -0.1432 | -0.044525 | 0.0030184 | 0.026568 | 0.0017175 | -0.0090342 | -0.0021597 | -0.10464 | 0.0063787 | 0.064704 | 0.051968 | -0.015806 | 0.02869 | -0.0040845 | -0.13733 | -0.018311 | -0.045776 | -0.11902 | -0.027466 | -0.15106 | -0.059509 | 0.21973 | 122.0444 | -0.10986 | 121.8979 | 0.009155 | -0.045776 | 0.009155 | 0.050354 | -122.1542 | -122.2549 | 0.068664 | 0.036621 | -0.054932 | -0.013733 | -0.10529 | -0.013733 | -0.091552 | -0.23804 | 0.10528 | 0.10528 | 0.050354 | 0.11902 | 0.064087 | 0.01831 | -0.073243 | 0.11902 | 122.0078 | 0.027465 | 122.1542 | 0.077819 | 122.1405 | -122.1817 | -122.2458 | -0.022889 | 121.994 | -0.041199 | 0.31586
2353.1406 | 122.3648 | -0.068665 | 122.1176 | -0.15846 | -0.046234 | 0.0036594 | 0.022296 | -0.0034095 | -0.010743 | -0.0023733 | 0.020477 | 0.0044561 | 0.064918 | 0.044278 | -0.015806 | 0.025272 | -0.0081433 | -0.086975 | -0.073242 | -0.004578 | 0.018311 | 0.13733 | 0.027466 | 0.086975 | 0.54474 | 121.994 | -0.073242 | 121.994 | 0.16479 | 0.1236 | 0.13733 | 0.064087 | -122.1909 | -122.0993 | 0.20599 | 0.15564 | 0.096131 | 0.091553 | 0.032044 | -0.004577 | -0.1236 | -0.1236 | 0.23346 | 0.20599 | 0.19226 | 0.21057 | 0.19684 | 0.14191 | 0.022889 | 0.23804 | 122.0673 | -0.068664 | 122.0673 | -0.004577 | 122.0627 | -122.1222 | -122.1909 | 0.086976 | 122.0627 | -0.01831 | 0.6134
2354.8438 | 122.2321 | -0.1236 | 122.1497 | -0.097427 | -0.04538 | 0.0010958 | 0.026355 | -0.00041873 | -0.01117 | -0.0032277 | -0.06192 | 0.0072333 | 0.065132 | 0.057522 | -0.01602 | 0.028903 | -0.0077161 | -0.15564 | -0.013733 | -0.064087 | -0.10986 | -0.022888 | -0.10529 | -0.022888 | 0.39368 | 122.0123 | -0.10071 | 121.875 | 0.022888 | -0.027466 | 0.027466 | 0.059509 | -122.1634 | -122.2595 | 0.10071 | 0.10071 | 0.01831 | 0.041199 | -0.041199 | 0.022888 | -0.13733 | -0.27466 | 0.14648 | 0.15106 | 0.09613 | 0.12817 | 0.073242 | 0.041199 | -0.045776 | 0.1236 | 121.9757 | 0.050354 | 122.113 | 0.10986 | 122.1359 | -122.2137 | -122.2504 | 0.013733 | 121.9986 | -0.032044 | 0.51727
2356.5938 | 122.319 | -0.07782 | 122.1176 | -0.15083 | -0.044739 | 0.0028048 | 0.024432 | -0.0027685 | -0.0083932 | -0.0057913 | -0.016144 | 0.0063787 | 0.065772 | 0.046841 | -0.015592 | 0.028049 | -0.0057935 | -0.12817 | -0.054932 | -0.018311 | -0.045776 | 0.068665 | -0.068665 | 0.032043 | 0.35248 | 121.9711 | -0.082397 | 121.9391 | 0.10071 | 0.054932 | 0.09613 | 0.059509 | -122.1725 | -122.1634 | 0.14649 | 0.10986 | 0.009155 | 0.050354 | -0.050354 | -0.004577 | -0.14648 | -0.17853 | 0.17853 | 0.17395 | 0.13275 | 0.17853 | 0.13733 | 0.086976 | -0.027465 | 0.18311 | 122.0215 | -0.036621 | 122.0535 | 0.022888 | 122.049 | -122.1359 | -122.2 | 0.032044 | 122.0169 | -0.050354 | 0.4303
2358.3594 | 122.3236 | -0.082397 | 122.1039 | -0.13557 | -0.046234 | 0.0013094 | 0.024646 | -0.0044775 | -0.010102 | -0.0019461 | -0.031403 | 0.0038153 | 0.064704 | 0.046841 | -0.015165 | 0.025485 | -0.0036573 | -0.12817 | -0.050354 | -0.022888 | -0.050354 | 0.059509 | -0.054932 | 0.036621 | 0.39368 | 121.994 | -0.10071 | 121.9574 | 0.10529 | 0.073242 | 0.09613 | 0.059509 | -122.1542 | -122.1542 | 0.14191 | 0.11902 | 0.027465 | 0.059509 | -0.032044 | -0.018311 | -0.10986 | -0.14648 | 0.18768 | 0.17853 | 0.15564 | 0.19684 | 0.17395 | 0.082397 | -0.027466 | 0.20599 | 122.0581 | -0.027466 | 122.0947 | 0.032043 | 122.0764 | -122.1268 | -122.2046 | 0.032043 | 122.0398 | -0.045777 | 0.47607
2360.125 | 122.3511 | -0.082397 | 122.1039 | -0.10506 | -0.046662 | 0.0047274 | 0.023364 | -0.0023413 | -0.0098886 | -0.0032277 | -0.022247 | 0.0029607 | 0.061714 | 0.045346 | -0.017301 | 0.027408 | -0.0055799 | -0.13733 | -0.050354 | -0.022888 | -0.013733 | 0.064087 | -0.041199 | 0.050354 | 0.41199 | 122.0078 | -0.082397 | 121.9711 | 0.14648 | 0.11444 | 0.11444 | 0.059509 | -122.1542 | -122.1176 | 0.14648 | 0.13275 | 0.041198 | 0.073242 | -0.018311 | 0 | -0.096131 | -0.13275 | 0.22888 | 0.19684 | 0.19684 | 0.19684 | 0.19684 | 0.086975 | 0.009155 | 0.22888 | 122.0535 | -0.027466 | 122.0901 | 0.032043 | 122.0901 | -122.1268 | -122.1863 | 0.068664 | 122.0535 | -0.054932 | 0.49438
2361.8125 | 122.3648 | -0.073242 | 122.1085 | -0.082169 | -0.045166 | 0.0025912 | 0.025714 | -0.0029821 | -0.010316 | -0.0042959 | -0.0069885 | 0.0042425 | 0.063636 | 0.045987 | -0.017942 | 0.026981 | -0.0047253 | -0.082397 | -0.064087 | -0.027466 | 0.032043 | 0.13275 | 0.018311 | 0.10071 | 0.52185 | 122.0078 | -0.050354 | 122.0215 | 0.16479 | 0.13733 | 0.16022 | 0.045776 | -122.1725 | -122.0764 | 0.20599 | 0.17395 | 0.091553 | 0.12817 | 0.045777 | 0.022888 | -0.10071 | -0.086975 | 0.23804 | 0.23346 | 0.21057 | 0.21057 | 0.18768 | 0.16022 | 0.059509 | 0.21515 | 122.0718 | -0.036621 | 122.0581 | 0.009155 | 122.081 | -122.1359 | -122.1588 | 0.10529 | 122.0947 | -0.009155 | 0.59509
2363.5625 | 122.2824 | -0.091553 | 122.1634 | -0.06691 | -0.044312 | 0.0025912 | 0.027209 | -0.0021277 | -0.0071116 | -0.0028005 | -0.1138 | 0.0074469 | 0.065345 | 0.050473 | -0.017301 | 0.026767 | -0.0030163 | -0.091553 | -0.032043 | -0.036621 | -0.027466 | 0.045776 | -0.068665 | -0.004578 | 0.43488 | 122.049 | -0.09613 | 121.9437 | 0.091553 | 0.022888 | 0.064087 | 0.054932 | -122.1954 | -122.1909 | 0.13733 | 0.086975 | 0.022888 | 0.032043 | -0.032044 | -0.004577 | -0.11444 | -0.21973 | 0.18311 | 0.15564 | 0.11444 | 0.16022 | 0.11902 | 0.082397 | 0.009155 | 0.18768 | 122.0398 | 0.004578 | 122.1451 | 0.05951 | 122.1405 | -122.2 | -122.2595 | 0.064087 | 122.0352 | 0 | 0.52643
2365.3281 | 122.3602 | -0.07782 | 122.1176 | -0.12032 | -0.045807 | 0.0013094 | 0.026355 | 0.0019311 | -0.0083932 | -0.0045095 | 0.0021667 | 0.0053107 | 0.061927 | 0.051114 | -0.015592 | 0.026126 | -0.0064343 | -0.07782 | -0.082397 | -0.009155 | 0.041199 | 0.16937 | 0.022888 | 0.09613 | 0.53101 | 122.0032 | -0.068665 | 122.0123 | 0.16937 | 0.14648 | 0.12817 | 0.068665 | -122.2 | -122.0764 | 0.24719 | 0.17395 | 0.10071 | 0.10528 | 0.032043 | 0.009155 | -0.11444 | -0.10529 | 0.24719 | 0.20599 | 0.2243 | 0.19684 | 0.21515 | 0.17853 | 0.050354 | 0.23804 | 122.081 | -0.073242 | 122.0718 | -0.004577 | 122.081 | -122.1268 | -122.1863 | 0.11902 | 122.0901 | 0 | 0.60883
2367.0781 | 122.3694 | -0.064087 | 122.1039 | -0.082169 | -0.044953 | 0.0030184 | 0.024432 | -0.0053321 | -0.0098886 | -0.0062185 | -0.0069885 | 0.0070197 | 0.06385 | 0.049191 | -0.014524 | 0.025272 | -0.0068615 | -0.059509 | -0.050354 | 0.009155 | 0.036621 | 0.16022 | 0.022888 | 0.086975 | 0.53101 | 122.0169 | -0.07782 | 121.9986 | 0.17395 | 0.13275 | 0.14191 | 0.073242 | -122.1542 | -122.0673 | 0.2243 | 0.15106 | 0.086975 | 0.07782 | 0.013733 | -0.013733 | -0.086975 | -0.10529 | 0.23804 | 0.20599 | 0.19684 | 0.21973 | 0.21057 | 0.15106 | 0.027466 | 0.25177 | 122.0764 | -0.059509 | 122.0947 | 0.013733 | 122.081 | -122.0947 | -122.1817 | 0.10071 | 122.0627 | 0.004578 | 0.59509
2368.7812 | 122.2961 | -0.086975 | 122.1039 | -0.15846 | -0.043457 | 0.0028048 | 0.025287 | -0.00084593 | -0.0088206 | -0.0049367 | -0.040558 | 0.0046697 | 0.063636 | 0.044491 | -0.016447 | 0.026981 | -0.0079297 | -0.11444 | -0.045776 | -0.022888 | -0.027466 | 0.050354 | -0.041199 | 0.013733 | 0.34332 | 122.0123 | -0.086975 | 121.9574 | 0.082397 | 0.045776 | 0.091553 | 0.064087 | -122.1497 | -122.1313 | 0.13733 | 0.10071 | 0.045776 | 0.036621 | -0.018311 | 0 | -0.091553 | -0.14648 | 0.16937 | 0.17853 | 0.13275 | 0.17853 | 0.13275 | 0.073242 | -0.004578 | 0.16937 | 122.0444 | -0.022888 | 122.0993 | 0.041199 | 122.0993 | -122.1268 | -122.1909 | 0.059509 | 122.0444 | -0.027466 | 0.4303
2370.5312 | 122.3465 | -0.045776 | 122.1222 | -0.19661 | -0.04538 | 0.0034456 | 0.026355 | 0.00022207 | -0.0064706 | -0.0025869 | -0.074127 | 0.0040289 | 0.063636 | 0.048764 | -0.015806 | 0.025058 | -0.0066479 | -0.050354 | -0.073242 | -0.004578 | 0.022888 | 0.11902 | -0.018311 | 0.068665 | 0.39368 | 122.0032 | -0.054932 | 122.0215 | 0.16479 | 0.09613 | 0.14191 | 0.041198 | -122.1954 | -122.0993 | 0.16479 | 0.11444 | 0.027465 | 0.073243 | -0.013733 | -0.009156 | -0.11902 | -0.10071 | 0.21057 | 0.18768 | 0.14191 | 0.19684 | 0.15106 | 0.1236 | 0.027466 | 0.21973 | 122.0764 | -0.068664 | 122.0581 | -0.027466 | 122.049 | -122.1268 | -122.1771 | 0.068664 | 122.0673 | -0.004578 | 0.43945
2372.2188 | 122.2641 | -0.091553 | 122.1268 | -0.12032 | -0.042389 | 0.0028048 | 0.028064 | -0.00063233 | -0.0073252 | -0.0053641 | -0.11075 | 0.0057379 | 0.063423 | 0.049405 | -0.014738 | 0.026767 | -0.0040845 | -0.1236 | -0.018311 | -0.045776 | -0.07782 | -0.022888 | -0.13733 | -0.045776 | 0.27008 | 122.0306 | -0.10529 | 121.9254 | 0.036621 | -0.032043 | 0.045776 | 0.045777 | -122.1451 | -122.2046 | 0.068665 | 0.045777 | -0.045776 | 0 | -0.091553 | -0.013733 | -0.09613 | -0.20142 | 0.12817 | 0.13733 | 0.05951 | 0.15106 | 0.073243 | 0.022888 | -0.032044 | 0.14191 | 122.0306 | 0.027465 | 122.1359 | 0.073242 | 122.1222 | -122.1725 | -122.2321 | 0.013733 | 122.0169 | -0.032043 | 0.36163
2373.9688 | 122.2458 | -0.09613 | 122.168 | -0.17372 | -0.042816 | 0.0028048 | 0.027209 | 0.00086307 | -0.0083932 | -0.0042959 | -0.12906 | 0.0063787 | 0.063636 | 0.056027 | -0.013883 | 0.027194 | -0.0023755 | -0.13275 | -0.022888 | -0.073242 | -0.10071 | -0.041199 | -0.14648 | -0.054932 | 0.23346 | 122.0673 | -0.10071 | 121.8887 | 0 | -0.050354 | 0.022888 | 0.022888 | -122.1909 | -122.2687 | 0.054931 | 0.041198 | -0.050354 | 0.01831 | -0.073242 | -0.004578 | -0.10071 | -0.27924 | 0.09613 | 0.11902 | 0.045776 | 0.1236 | 0.050354 | 0.032043 | -0.027466 | 0.10071 | 121.9894 | 0.050354 | 122.168 | 0.073242 | 122.1634 | -122.2412 | -122.2687 | -0.004578 | 121.9849 | -0.036621 | 0.32959
2375.7188 | 122.3465 | -0.059509 | 122.1222 | -0.19661 | -0.045166 | 0.0051546 | 0.026782 | -0.0014867 | -0.007966 | -0.0025869 | -0.10159 | 0.0070197 | 0.064491 | 0.051114 | -0.01666 | 0.027408 | -0.0051525 | -0.11902 | -0.041199 | -0.027466 | -0.041199 | 0.064087 | -0.064087 | 0.004578 | 0.32501 | 122.0078 | -0.082397 | 121.9986 | 0.13733 | 0.07782 | 0.14191 | 0.032043 | -122.1634 | -122.1634 | 0.1236 | 0.064087 | -0.004578 | 0.032044 | -0.036621 | -0.022888 | -0.11444 | -0.1236 | 0.19684 | 0.20142 | 0.13733 | 0.2243 | 0.16022 | 0.091553 | -0.013733 | 0.21973 | 122.081 | -0.013733 | 122.0901 | 0.01831 | 122.0673 | -122.1497 | -122.2046 | 0.01831 | 122.0581 | -0.05951 | 0.38452
2377.4688 | 122.2733 | -0.091553 | 122.1497 | -0.10506 | -0.04538 | 0.0034456 | 0.025927 | -0.0021277 | -0.01053 | -0.0032277 | -0.1077 | 0.0061651 | 0.064063 | 0.056454 | -0.015592 | 0.027194 | -0.0092115 | -0.10529 | -0.022888 | -0.036621 | -0.045776 | 0.013733 | -0.07782 | -0.009155 | 0.43488 | 122.0398 | -0.09613 | 121.9345 | 0.068665 | 0.013733 | 0.07782 | 0.054932 | -122.1725 | -122.1954 | 0.10529 | 0.082398 | 0.013733 | 0.027466 | -0.041199 | -0.004577 | -0.10986 | -0.21515 | 0.16022 | 0.16937 | 0.10529 | 0.17395 | 0.10986 | 0.050354 | -0.009155 | 0.16479 | 122.0306 | 0.013733 | 122.1359 | 0.068665 | 122.1313 | -122.1863 | -122.2458 | 0.045777 | 122.0261 | -0.013733 | 0.52643
2379.1562 | 122.3694 | -0.091553 | 122.0856 | -0.15846 | -0.048584 | 0.0019504 | 0.022723 | -0.0042639 | -0.0094614 | -0.0023733 | -0.01004 | 0.0046697 | 0.063209 | 0.045773 | -0.013456 | 0.02634 | -0.0064343 | -0.073242 | -0.054932 | -0.032043 | 0.041199 | 0.14191 | 0.018311 | 0.10529 | 0.53101 | 122.0306 | -0.073242 | 122.0169 | 0.16479 | 0.14648 | 0.15106 | 0.05951 | -122.1405 | -122.0444 | 0.23346 | 0.19684 | 0.10986 | 0.13733 | 0.050354 | 0.018311 | -0.054931 | -0.068664 | 0.25635 | 0.24261 | 0.23804 | 0.2243 | 0.21973 | 0.17395 | 0.073242 | 0.23804 | 122.0901 | -0.022889 | 122.1039 | 0.036621 | 122.1222 | -122.1176 | -122.1588 | 0.13275 | 122.1085 | 0.018311 | 0.62256
2380.9219 | 122.3602 | -0.041199 | 122.1039 | -0.15083 | -0.044953 | 0.0030184 | 0.028277 | 0.0010767 | -0.007966 | -0.0034415 | -0.083283 | 0.0036017 | 0.064063 | 0.049832 | -0.017729 | 0.028049 | -0.0049389 | -0.050354 | -0.059509 | -0.013733 | 0.018311 | 0.11444 | -0.036621 | 0.045776 | 0.37994 | 122.0078 | -0.059509 | 122.0169 | 0.13733 | 0.091553 | 0.16022 | 0.027466 | -122.1634 | -122.0856 | 0.15564 | 0.086975 | 0.004578 | 0.059509 | -0.022888 | -0.01831 | -0.096131 | -0.086975 | 0.17853 | 0.20142 | 0.13275 | 0.21973 | 0.15106 | 0.12817 | 0.032044 | 0.19684 | 122.0764 | -0.045776 | 122.0673 | -0.01831 | 122.049 | -122.1176 | -122.1634 | 0.05951 | 122.0581 | -0.009155 | 0.42114
2382.6094 | 122.3694 | -0.068665 | 122.0993 | -0.15083 | -0.046234 | 0.004941 | 0.025927 | 0.0010767 | -0.0092478 | -0.0053641 | -0.080231 | 0.0059515 | 0.06385 | 0.051541 | -0.016874 | 0.027835 | -0.0042981 | -0.059509 | -0.064087 | -0.004578 | 0.041199 | 0.1236 | -0.027466 | 0.054932 | 0.40283 | 121.994 | -0.073242 | 122.0398 | 0.16022 | 0.091553 | 0.16479 | 0.064087 | -122.1634 | -122.0581 | 0.19226 | 0.1236 | 0.041199 | 0.05951 | -0.022888 | -0.004577 | -0.10529 | -0.059509 | 0.22888 | 0.23346 | 0.16022 | 0.23804 | 0.16479 | 0.12817 | 0.045777 | 0.23346 | 122.113 | -0.059509 | 122.0673 | 0.004578 | 122.0627 | -122.1039 | -122.1725 | 0.10986 | 122.1085 | 0.009156 | 0.4715
2384.375 | 122.2733 | -0.10529 | 122.1634 | -0.10506 | -0.044525 | 0.0017368 | 0.025927 | 0.0027857 | -0.0075388 | -0.0036551 | -0.10159 | 0.0085149 | 0.065986 | 0.052823 | -0.015592 | 0.029117 | -0.0019483 | -0.086975 | -0.050354 | -0.050354 | -0.054932 | 0.045776 | -0.068665 | 0 | 0.4303 | 122.0352 | -0.1236 | 121.962 | 0.07782 | 0.032043 | 0.059509 | 0.054932 | -122.2137 | -122.2183 | 0.15106 | 0.10529 | 0.036621 | 0.050354 | -0.018311 | -0.01831 | -0.12817 | -0.20142 | 0.18311 | 0.16479 | 0.13733 | 0.1831 | 0.15564 | 0.09613 | -0.004578 | 0.20142 | 122.0856 | 0 | 122.1588 | 0.054932 | 122.1405 | -122.2137 | -122.287 | 0.050354 | 122.0673 | 0.018311 | 0.53558
2386.0938 | 122.3557 | -0.064087 | 122.1176 | -0.15846 | -0.044312 | 0.0040866 | 0.024218 | 0.0019311 | -0.0066844 | -0.0023733 | -0.064972 | 0.0053107 | 0.063423 | 0.049191 | -0.013456 | 0.025912 | -0.0030163 | -0.041199 | -0.064087 | -0.013733 | 0.022888 | 0.12817 | -0.013733 | 0.059509 | 0.40283 | 122.0123 | -0.054932 | 122.0215 | 0.16022 | 0.091553 | 0.15564 | 0.050354 | -122.1817 | -122.0947 | 0.19226 | 0.1236 | 0.050354 | 0.073242 | 0 | 0.009155 | -0.10529 | -0.096131 | 0.2243 | 0.21973 | 0.15564 | 0.21057 | 0.14649 | 0.14191 | 0.036621 | 0.21515 | 122.0764 | -0.050354 | 122.0673 | 0 | 122.0764 | -122.1313 | -122.1725 | 0.086975 | 122.0856 | 0.022888 | 0.46692
2387.8438 | 122.2504 | -0.11902 | 122.1542 | -0.12032 | -0.045166 | 0.003232 | 0.026355 | -0.0010595 | -0.008607 | -0.0034415 | -0.11075 | 0.0061651 | 0.063636 | 0.053677 | -0.015806 | 0.030399 | -0.0049389 | -0.10071 | -0.041199 | -0.036621 | -0.064087 | 0.032043 | -0.10529 | -0.032043 | 0.35248 | 122.0352 | -0.10986 | 121.9208 | 0.032043 | -0.036621 | 0.032043 | 0.082398 | -122.1954 | -122.2183 | 0.15106 | 0.086976 | 0.013733 | 0.004578 | -0.068665 | 0.009156 | -0.11902 | -0.23346 | 0.15106 | 0.15106 | 0.082398 | 0.14191 | 0.073242 | 0.068664 | -0.027466 | 0.14191 | 122.0306 | -0.004578 | 122.1451 | 0.07782 | 122.1542 | -122.1909 | -122.2641 | 0.054932 | 122.0398 | 0.018311 | 0.4715
2389.5938 | 122.2458 | -0.12817 | 122.1542 | -0.05928 | -0.046234 | 0.0017368 | 0.024218 | -0.0010595 | -0.010743 | -0.0038687 | -0.04361 | 0.0057379 | 0.066627 | 0.047268 | -0.014951 | 0.027835 | -0.0042981 | -0.16022 | -0.045776 | -0.045776 | -0.091553 | 0.009155 | -0.09613 | -0.022888 | 0.41657 | 122.049 | -0.10986 | 121.8658 | 0.022888 | -0.009155 | 0.004578 | 0.082398 | -122.2 | -122.2458 | 0.13733 | 0.10529 | 0.032044 | 0.022888 | -0.050354 | 0.018311 | -0.10529 | -0.28839 | 0.15106 | 0.13275 | 0.11902 | 0.11444 | 0.10071 | 0.054931 | -0.045777 | 0.13275 | 121.9757 | 0 | 122.1588 | 0.082398 | 122.1771 | -122.2 | -122.2641 | 0.036621 | 121.994 | -0.032043 | 0.54474
2391.2812 | 122.2366 | -0.10071 | 122.1771 | -0.18135 | -0.045807 | 0.0043002 | 0.027209 | 0.0019311 | -0.0047616 | -0.0049367 | -0.092438 | 0.0057379 | 0.065559 | 0.051327 | -0.015806 | 0.02869 | -0.0064343 | -0.14648 | -0.022888 | -0.054932 | -0.10986 | -0.027466 | -0.14648 | -0.050354 | 0.2243 | 122.0581 | -0.10986 | 121.907 | 0.009155 | -0.041199 | 0.022888 | 0.045776 | -122.2 | -122.287 | 0.073242 | 0.050354 | -0.045776 | 0.004578 | -0.091552 | -0.009155 | -0.11902 | -0.27008 | 0.10986 | 0.1236 | 0.059509 | 0.13275 | 0.068664 | 0.027466 | -0.054931 | 0.11902 | 122.0169 | 0.032044 | 122.168 | 0.07782 | 122.1588 | -122.2321 | -122.287 | -0.009155 | 122.0078 | -0.045776 | 0.32501
2393.0312 | 122.3648 | -0.059509 | 122.1039 | -0.12794 | -0.044525 | 0.0023776 | 0.023364 | -0.0012731 | -0.010316 | -0.0032277 | 0.017425 | 0.0038153 | 0.065772 | 0.043637 | -0.014951 | 0.026981 | -0.0077161 | -0.10529 | -0.054932 | -0.018311 | -0.027466 | 0.09613 | -0.027466 | 0.068665 | 0.4303 | 122.0032 | -0.068665 | 122.0032 | 0.16022 | 0.1236 | 0.14191 | 0.041198 | -122.1588 | -122.1313 | 0.15564 | 0.12817 | 0.032043 | 0.086976 | -0.009155 | -0.009156 | -0.10071 | -0.10071 | 0.21973 | 0.20142 | 0.1831 | 0.21057 | 0.19226 | 0.11444 | -0.009155 | 0.22888 | 122.0718 | -0.036621 | 122.0718 | 0.004577 | 122.0627 | -122.1222 | -122.1725 | 0.032043 | 122.0627 | -0.045777 | 0.48981
2394.7812 | 122.2961 | -0.07782 | 122.1497 | -0.1432 | -0.045594 | 0.0028048 | 0.028064 | 0.00043587 | -0.0098886 | -0.0040823 | -0.092438 | 0.0061651 | 0.064918 | 0.049191 | -0.016233 | 0.027621 | -0.0038709 | -0.11902 | -0.027466 | -0.041199 | -0.082397 | 0 | -0.1236 | -0.018311 | 0.27466 | 122.0261 | -0.10071 | 121.962 | 0.068665 | 0.018311 | 0.07782 | 0.036621 | -122.1771 | -122.2321 | 0.07782 | 0.059509 | -0.045776 | 0.022888 | -0.082397 | -0.022888 | -0.1236 | -0.18768 | 0.14649 | 0.15564 | 0.096131 | 0.17853 | 0.11902 | 0.041199 | -0.041198 | 0.16937 | 122.0627 | 0.013733 | 122.1268 | 0.050354 | 122.1039 | -122.1909 | -122.2504 | -0.004577 | 122.0398 | -0.041199 | 0.35248
2396.4688 | 122.3831 | -0.054932 | 122.1039 | -0.11269 | -0.046234 | 0.0023776 | 0.024646 | -0.0036231 | -0.010743 | -0.0053641 | 0.020477 | 0.0057379 | 0.06385 | 0.051327 | -0.018156 | 0.026126 | -0.0049389 | -0.073242 | -0.045776 | -0.022888 | 0.013733 | 0.14648 | 0.009155 | 0.10986 | 0.53101 | 122.0078 | -0.073242 | 122.0261 | 0.18768 | 0.14191 | 0.14648 | 0.032044 | -122.1497 | -122.0901 | 0.20142 | 0.16479 | 0.064087 | 0.13275 | 0.032043 | -0.01831 | -0.096131 | -0.07782 | 0.24261 | 0.20142 | 0.19684 | 0.21973 | 0.21515 | 0.16937 | 0.036621 | 0.26092 | 122.0993 | -0.022888 | 122.081 | 0.009156 | 122.0627 | -122.1268 | -122.1771 | 0.068665 | 122.081 | -0.01831 | 0.58594
2398.2188 | 122.2504 | -0.1236 | 122.1588 | -0.12794 | -0.043885 | 0.0025912 | 0.028705 | 0.0029993 | -0.0075388 | -0.0049367 | -0.10159 | 0.0048833 | 0.065559 | 0.049618 | -0.018156 | 0.027194 | -0.0034435 | -0.1236 | -0.027466 | -0.050354 | -0.10529 | -0.041199 | -0.16937 | -0.059509 | 0.25635 | 122.049 | -0.10529 | 121.9208 | 0.009155 | -0.050354 | 0.032043 | 0.073242 | -122.1863 | -122.2641 | 0.082397 | 0.064087 | -0.045777 | -0.009155 | -0.11902 | 0.01831 | -0.10986 | -0.23804 | 0.13275 | 0.15564 | 0.073242 | 0.13733 | 0.054932 | 0.009155 | -0.054932 | 0.11444 | 122.0261 | 0.022888 | 122.1542 | 0.09613 | 122.1725 | -122.2092 | -122.2641 | 0.01831 | 122.0444 | 0 | 0.37994
2399.9688 | 122.3831 | -0.059509 | 122.1222 | -0.082169 | -0.046875 | 0.0051546 | 0.024432 | -0.0038367 | -0.0092478 | -0.0030141 | -0.01004 | 0.0055243 | 0.06385 | 0.048977 | -0.01666 | 0.028049 | -0.0049389 | -0.082397 | -0.045776 | -0.009155 | 0.027466 | 0.14191 | -0.004578 | 0.09613 | 0.5127 | 121.9894 | -0.07782 | 122.0261 | 0.17853 | 0.14191 | 0.14648 | 0.050354 | -122.168 | -122.0947 | 0.20142 | 0.15564 | 0.054931 | 0.10528 | 0.004577 | -0.018311 | -0.13275 | -0.09613 | 0.23804 | 0.20599 | 0.20142 | 0.2243 | 0.21973 | 0.15106 | 0.036621 | 0.25635 | 122.1039 | -0.036621 | 122.0673 | 0.013733 | 122.049 | -122.1313 | -122.2 | 0.086975 | 122.0856 | -0.022888 | 0.5722
2401.7188 | 122.3282 | -0.068665 | 122.1497 | -0.1432 | -0.045166 | 0.0030184 | 0.023364 | 0.00086307 | -0.008607 | -0.0028005 | -0.04361 | 0.0044561 | 0.064277 | 0.047268 | -0.014951 | 0.027194 | -0.0077161 | -0.082397 | -0.054932 | -0.013733 | 0.018311 | 0.11902 | -0.018311 | 0.050354 | 0.37994 | 122.0169 | -0.054932 | 121.9986 | 0.11902 | 0.082397 | 0.11444 | 0.054932 | -122.2046 | -122.1313 | 0.18768 | 0.11902 | 0.050354 | 0.064087 | -0.004578 | 0.013733 | -0.13275 | -0.15106 | 0.18768 | 0.18311 | 0.15106 | 0.16937 | 0.13733 | 0.13275 | 0.032044 | 0.17395 | 122.0535 | -0.041199 | 122.0718 | 0.013733 | 122.0856 | -122.1634 | -122.2046 | 0.086976 | 122.0673 | -0.013732 | 0.44861
2403.4219 | 122.3465 | -0.068665 | 122.1268 | -0.16609 | -0.046662 | 0.001523 | 0.024646 | -0.0012731 | -0.0094614 | -0.0038687 | -0.028351 | 0.0053107 | 0.066841 | 0.048123 | -0.017942 | 0.025699 | -0.0047253 | -0.11902 | -0.041199 | -0.018311 | -0.036621 | 0.07782 | -0.054932 | 0.036621 | 0.35706 | 122.0169 | -0.086975 | 121.962 | 0.09613 | 0.064087 | 0.086975 | 0.050354 | -122.168 | -122.1634 | 0.14649 | 0.10529 | 0.013733 | 0.054932 | -0.036621 | -0.01831 | -0.10986 | -0.16479 | 0.16479 | 0.15564 | 0.13275 | 0.17395 | 0.15106 | 0.096131 | -0.01831 | 0.1831 | 122.0489 | -0.022888 | 122.1039 | 0.027466 | 122.0856 | -122.1451 | -122.2137 | 0.032044 | 122.0306 | -0.050354 | 0.42572
2405.1719 | 122.2733 | -0.09613 | 122.1405 | -0.15083 | -0.043885 | 0.0028048 | 0.030627 | 0.0027857 | -0.0083932 | -0.0072867 | -0.11685 | 0.0078741 | 0.062995 | 0.049832 | -0.016874 | 0.028262 | -0.0085705 | -0.14191 | -0.013733 | -0.054932 | -0.09613 | -0.013733 | -0.13275 | -0.036621 | 0.2655 | 122.0535 | -0.091553 | 121.9345 | 0.022888 | -0.013733 | 0.050354 | 0.041198 | -122.1542 | -122.2366 | 0.082397 | 0.059509 | -0.036621 | 0.018311 | -0.077819 | 0.004577 | -0.086975 | -0.20599 | 0.11902 | 0.14648 | 0.082397 | 0.14191 | 0.07782 | 0.041199 | -0.041198 | 0.11444 | 122.0261 | 0.041199 | 122.1451 | 0.082397 | 122.1497 | -122.1954 | -122.2321 | 0 | 122.0306 | -0.045777 | 0.36163
2406.875 | 122.3877 | -0.054932 | 122.1268 | -0.1432 | -0.04773 | 0.0028048 | 0.022723 | -0.0017005 | -0.0081796 | -0.0045095 | 0.0021667 | 0.0046697 | 0.062995 | 0.0509 | -0.014524 | 0.027408 | -0.0040845 | -0.09613 | -0.064087 | -0.009155 | 0.013733 | 0.13733 | 0.009155 | 0.086975 | 0.52185 | 121.9986 | -0.068665 | 122.0215 | 0.16937 | 0.13733 | 0.16022 | 0.045777 | -122.1909 | -122.113 | 0.19226 | 0.14191 | 0.064087 | 0.09613 | 0.01831 | -0.013733 | -0.12817 | -0.10529 | 0.22431 | 0.21515 | 0.19226 | 0.22888 | 0.20599 | 0.14648 | 0.022888 | 0.23804 | 122.0901 | -0.054932 | 122.0673 | -0.009155 | 122.0535 | -122.1359 | -122.1954 | 0.068665 | 122.0764 | -0.041198 | 0.57678
2408.625 | 122.3694 | -0.054932 | 122.1405 | -0.18135 | -0.044312 | 0.003232 | 0.027209 | -0.0034095 | -0.0075388 | -0.0040823 | -0.089386 | 0.0042425 | 0.064063 | 0.053464 | -0.017515 | 0.027408 | -0.0015209 | -0.050354 | -0.064087 | -0.013733 | 0.032043 | 0.11902 | -0.036621 | 0.064087 | 0.37994 | 122.0306 | -0.068665 | 122.0306 | 0.14648 | 0.091553 | 0.16937 | 0.041199 | -122.2046 | -122.1085 | 0.17395 | 0.11902 | 0.018311 | 0.07782 | -0.022888 | -0.013733 | -0.10986 | -0.10986 | 0.20142 | 0.22431 | 0.14649 | 0.23804 | 0.16022 | 0.13275 | 0.045776 | 0.21515 | 122.0993 | -0.050354 | 122.0993 | -0.009155 | 122.0856 | -122.1542 | -122.2092 | 0.086975 | 122.0856 | 0.004578 | 0.43488
2410.3125 | 122.2366 | -0.1236 | 122.1588 | -0.074539 | -0.046021 | 0.0010958 | 0.027423 | -0.00020513 | -0.0092478 | -0.0055777 | -0.077179 | 0.0055243 | 0.06385 | 0.054959 | -0.015592 | 0.027835 | -0.0060071 | -0.14191 | -0.018311 | -0.050354 | -0.091553 | 0 | -0.10986 | -0.032043 | 0.39825 | 122.081 | -0.10071 | 121.8842 | 0.022888 | -0.027466 | 0.018311 | 0.073242 | -122.1771 | -122.2504 | 0.1236 | 0.091553 | 0.013733 | 0.018311 | -0.059509 | 0.022888 | -0.077819 | -0.27466 | 0.14648 | 0.14191 | 0.09613 | 0.11902 | 0.073242 | 0.050354 | -0.041199 | 0.1236 | 121.9849 | 0.032043 | 122.1817 | 0.10528 | 122.2046 | -122.2092 | -122.2595 | 0.032043 | 122.0078 | -0.018311 | 0.52185
2412.0156 | 122.3282 | -0.073242 | 122.1313 | -0.18898 | -0.045594 | 0.0023776 | 0.0255 | 0.0023585 | -0.01053 | -0.0036551 | -0.031403 | 0.0050971 | 0.063636 | 0.048977 | -0.01602 | 0.025272 | 0.0014697 | -0.091553 | -0.07782 | -0.027466 | 0.018311 | 0.11444 | -0.054932 | 0.068665 | 0.3891 | 122.0306 | -0.064087 | 121.9711 | 0.10529 | 0.073242 | 0.10071 | 0.045776 | -122.2092 | -122.113 | 0.18768 | 0.14191 | 0.01831 | 0.096131 | -0.027466 | 0.009155 | -0.10071 | -0.16022 | 0.17853 | 0.17395 | 0.14648 | 0.1648 | 0.13733 | 0.14191 | 0.045777 | 0.16937 | 122.0352 | -0.050354 | 122.0947 | -0.004578 | 122.1039 | -122.1588 | -122.1954 | 0.091553 | 122.0444 | -0.018311 | 0.46234
2413.7812 | 122.2916 | -0.09613 | 122.1771 | -0.06691 | -0.044312 | 0.0023776 | 0.026996 | 0.0010767 | -0.010102 | -0.0025869 | -0.10464 | 0.0072333 | 0.065132 | 0.05795 | -0.015592 | 0.026767 | -0.0060071 | -0.10986 | -0.027466 | -0.032043 | -0.068665 | 0 | -0.07782 | 0.004578 | 0.42114 | 122.0581 | -0.086975 | 121.9574 | 0.07782 | 0.013733 | 0.059509 | 0.064087 | -122.2046 | -122.2458 | 0.09613 | 0.10071 | 0.01831 | 0.036621 | -0.045777 | 0.009155 | -0.11902 | -0.21973 | 0.17395 | 0.15564 | 0.10986 | 0.14648 | 0.10071 | 0.032043 | -0.036622 | 0.16479 | 122.0444 | 0.004577 | 122.1451 | 0.068664 | 122.1542 | -122.2092 | -122.2641 | 0.027465 | 122.0535 | -0.013733 | 0.51727
2415.5625 | 122.3648 | -0.059509 | 122.1542 | -0.15846 | -0.043885 | 0.0023776 | 0.025927 | -0.00020513 | -0.0092478 | -0.0040823 | -0.06192 | 0.0044561 | 0.062995 | 0.054104 | -0.015165 | 0.029117 | -0.0010937 | -0.059509 | -0.068665 | 0.004578 | 0.036621 | 0.13275 | -0.004578 | 0.064087 | 0.40283 | 122.0123 | -0.064087 | 122.0352 | 0.16937 | 0.10529 | 0.16479 | 0.064087 | -122.2229 | -122.1176 | 0.19226 | 0.1236 | 0.054931 | 0.059509 | -0.009156 | -0.004578 | -0.14191 | -0.11902 | 0.22888 | 0.2243 | 0.16479 | 0.22888 | 0.16937 | 0.12817 | 0.032043 | 0.23346 | 122.0993 | -0.073243 | 122.0764 | -0.009156 | 122.0718 | -122.1497 | -122.2183 | 0.09613 | 122.0947 | 0 | 0.46234
2417.25 | 122.3511 | -0.064087 | 122.1451 | -0.12032 | -0.045807 | 0.0040866 | 0.027209 | 0.0019311 | -0.0073252 | -0.00087794 | -0.089386 | 0.0085149 | 0.062141 | 0.047055 | -0.015379 | 0.031039 | -0.0051525 | -0.10986 | -0.027466 | -0.018311 | -0.050354 | 0.032043 | -0.09613 | 0.009155 | 0.31586 | 122.0261 | -0.068665 | 121.9986 | 0.11902 | 0.068665 | 0.09613 | 0.045776 | -122.1725 | -122.1954 | 0.09613 | 0.073242 | -0.032043 | 0.027466 | -0.077819 | -0.004578 | -0.11902 | -0.14648 | 0.18311 | 0.16022 | 0.13275 | 0.16479 | 0.13733 | 0.050354 | -0.032043 | 0.18768 | 122.0673 | -0.009155 | 122.0947 | 0.036621 | 122.0901 | -122.1634 | -122.2137 | 0.013733 | 122.0627 | -0.045776 | 0.37994
2419 | 122.2504 | -0.091553 | 122.1588 | -0.16609 | -0.045807 | 0.0023776 | 0.026355 | -0.0010595 | -0.007966 | -0.00023714 | -0.14127 | 0.0063787 | 0.06385 | 0.045346 | -0.018583 | 0.028262 | -0.0049389 | -0.086975 | -0.022888 | -0.022888 | -0.041199 | 0.041199 | -0.10529 | -0.022888 | 0.36621 | 122.0627 | -0.09613 | 121.9299 | 0.032043 | -0.032043 | 0.054932 | 0.068665 | -122.1817 | -122.2 | 0.13275 | 0.068665 | -0.013733 | 0 | -0.082398 | -0.004577 | -0.09613 | -0.22888 | 0.1236 | 0.14649 | 0.05951 | 0.15106 | 0.064087 | 0.064087 | -0.018311 | 0.12817 | 122.0261 | 0 | 122.1588 | 0.068665 | 122.1542 | -122.1817 | -122.2549 | 0.050354 | 122.0215 | 0.004578 | 0.45776
2420.6875 | 122.3511 | -0.073242 | 122.1222 | -0.10506 | -0.043885 | 0.0010958 | 0.028064 | -0.00063233 | -0.0083932 | -0.0036551 | -0.071076 | 0.0074469 | 0.064704 | 0.058804 | -0.015379 | 0.027621 | -0.0030163 | -0.1236 | -0.027466 | -0.036621 | -0.045776 | 0.032043 | -0.10071 | -0.004578 | 0.32959 | 122.0169 | -0.091553 | 122.0078 | 0.13275 | 0.041199 | 0.14648 | 0.036621 | -122.1497 | -122.168 | 0.10529 | 0.068664 | -0.027466 | 0.032043 | -0.064087 | -0.018311 | -0.10528 | -0.11444 | 0.20599 | 0.21973 | 0.11444 | 0.23804 | 0.13275 | 0.068664 | -0.009155 | 0.2243 | 122.0993 | 0.009155 | 122.1085 | 0.045776 | 122.0901 | -122.1588 | -122.2137 | 0.027466 | 122.081 | -0.050354 | 0.40283
2422.4219 | 122.287 | -0.086975 | 122.1863 | -0.13557 | -0.044953 | 0.003873 | 0.022296 | -0.0017005 | -0.011598 | -0.0028005 | -0.034454 | 0.0053107 | 0.060859 | 0.048123 | -0.016233 | 0.028049 | -0.0051525 | -0.09613 | -0.059509 | -0.018311 | -0.022888 | 0.091553 | -0.027466 | 0.027466 | 0.4715 | 122.0535 | -0.064087 | 121.9299 | 0.07782 | 0.013733 | 0.027466 | 0.068664 | -122.2458 | -122.2092 | 0.17853 | 0.11444 | 0.059509 | 0.045777 | -0.009155 | 0.022888 | -0.13275 | -0.25635 | 0.16479 | 0.11444 | 0.10071 | 0.091553 | 0.07782 | 0.10986 | -0.004577 | 0.14191 | 121.994 | -0.041198 | 122.1176 | 0.027466 | 122.1405 | -122.2046 | -122.2504 | 0.064087 | 122.0169 | -0.009155 | 0.55847
2424.1719 | 122.3557 | -0.059509 | 122.1313 | -0.15083 | -0.044098 | 0.00088223 | 0.022296 | 0.00022207 | -0.0098886 | -0.0032277 | -0.0008851 | 0.0046697 | 0.065345 | 0.042142 | -0.017088 | 0.026981 | -0.0068615 | -0.11444 | -0.041199 | -0.036621 | -0.018311 | 0.082397 | -0.013733 | 0.07782 | 0.43945 | 122.0123 | -0.07782 | 121.994 | 0.13275 | 0.11444 | 0.13733 | 0.022888 | -122.1725 | -122.1497 | 0.14191 | 0.13733 | 0.045776 | 0.11444 | 0.022888 | -0.018311 | -0.11902 | -0.13733 | 0.19226 | 0.19684 | 0.17395 | 0.21515 | 0.19226 | 0.11902 | 0.01831 | 0.21057 | 122.0718 | -0.004578 | 122.0901 | 0.01831 | 122.0718 | -122.168 | -122.2092 | 0.041198 | 122.0535 | -0.054932 | 0.49896
2425.9375 | 122.2733 | -0.09613 | 122.1771 | -0.10506 | -0.042603 | 0.003232 | 0.026996 | 0.0019311 | -0.0073252 | -0.0040823 | -0.10464 | 0.0061651 | 0.062354 | 0.048764 | -0.016447 | 0.028903 | -0.0034435 | -0.07782 | -0.022888 | -0.022888 | -0.045776 | 0.059509 | -0.091553 | 0 | 0.41199 | 122.0398 | -0.091553 | 121.9574 | 0.054932 | 0.009155 | 0.045776 | 0.073242 | -122.2 | -122.2229 | 0.15564 | 0.09613 | 0.004577 | 0.022888 | -0.068665 | 0.004577 | -0.13733 | -0.21973 | 0.15106 | 0.14191 | 0.10528 | 0.13733 | 0.10071 | 0.082397 | -0.022888 | 0.14649 | 122.049 | 0 | 122.1313 | 0.073242 | 122.1359 | -122.2 | -122.2687 | 0.050354 | 122.0535 | 0.01831 | 0.50812
2427.6875 | 122.3923 | -0.082397 | 122.1085 | -0.1432 | -0.043671 | 0.0025912 | 0.024218 | -0.0010595 | -0.0092478 | -0.0036551 | -0.025299 | 0.0050971 | 0.063423 | 0.041714 | -0.015806 | 0.024844 | -0.0040845 | -0.073242 | -0.041199 | -0.013733 | 0.009155 | 0.13733 | 0.027466 | 0.082397 | 0.51727 | 122.0123 | -0.073242 | 122.0398 | 0.17395 | 0.14191 | 0.15564 | 0.068664 | -122.1497 | -122.0993 | 0.21973 | 0.16479 | 0.10986 | 0.09613 | 0.041199 | 0.009155 | -0.09613 | -0.068664 | 0.25635 | 0.23804 | 0.2243 | 0.22888 | 0.21515 | 0.15106 | 0.022888 | 0.24719 | 122.113 | -0.027466 | 122.0856 | 0.041198 | 122.0947 | -122.1222 | -122.1817 | 0.091552 | 122.1222 | 0.009155 | 0.59967
2429.375 | 122.3877 | -0.054932 | 122.1268 | -0.17372 | -0.046448 | 0.0045138 | 0.024859 | 0.0036401 | -0.0081796 | -0.0013051 | -0.068024 | 0.0065923 | 0.061714 | 0.048764 | -0.015379 | 0.027408 | -0.0064343 | -0.045776 | -0.068665 | 0.009155 | 0.022888 | 0.12817 | -0.022888 | 0.068665 | 0.3891 | 121.9894 | -0.054932 | 122.049 | 0.15564 | 0.10529 | 0.15564 | 0.064087 | -122.1954 | -122.1039 | 0.18311 | 0.1236 | 0.032044 | 0.05951 | -0.032043 | 0 | -0.13733 | -0.07782 | 0.21057 | 0.21057 | 0.16022 | 0.21057 | 0.16022 | 0.11902 | 0.013733 | 0.21057 | 122.1039 | -0.07782 | 122.0444 | -0.013733 | 122.0444 | -122.1176 | -122.1817 | 0.07782 | 122.1039 | 0.009156 | 0.44403
2431.1406 | 122.3007 | -0.073242 | 122.1497 | -0.16609 | -0.045166 | 0.0040866 | 0.023791 | -0.0023413 | -0.010743 | -0.0045095 | -0.0069885 | 0.0042425 | 0.063209 | 0.057309 | -0.017088 | 0.02634 | -0.00066651 | -0.07782 | -0.059509 | -0.018311 | 0.018311 | 0.11902 | 0.004578 | 0.082397 | 0.51727 | 122.0261 | -0.073242 | 121.9666 | 0.1236 | 0.082397 | 0.10529 | 0.054931 | -122.2092 | -122.1313 | 0.19226 | 0.15564 | 0.07782 | 0.10071 | 0.022889 | 0 | -0.1236 | -0.1831 | 0.19684 | 0.17853 | 0.15564 | 0.17853 | 0.15564 | 0.13733 | 0.036622 | 0.19684 | 122.0398 | -0.041198 | 122.0993 | 0.013733 | 122.0993 | -122.168 | -122.2229 | 0.091553 | 122.0398 | -0.004578 | 0.59052
2432.875 | 122.2687 | -0.11444 | 122.1863 | -0.15083 | -0.044098 | 0.0043002 | 0.02785 | -0.0017005 | -0.0083932 | -0.0055777 | -0.1138 | 0.0048833 | 0.065986 | 0.057309 | -0.018369 | 0.02634 | -0.0028027 | -0.13275 | -0.013733 | -0.054932 | -0.091553 | -0.032043 | -0.14648 | -0.045776 | 0.24261 | 122.0581 | -0.10529 | 121.9299 | 0.009155 | -0.041199 | 0.032043 | 0.059509 | -122.2 | -122.2778 | 0.082398 | 0.068665 | -0.032043 | 0.009156 | -0.091552 | 0.009155 | -0.12817 | -0.25635 | 0.1236 | 0.14648 | 0.073242 | 0.13733 | 0.064087 | 0.022889 | -0.036621 | 0.11444 | 122.0352 | 0.041199 | 122.1634 | 0.10071 | 122.1725 | -122.2412 | -122.2916 | 0.022888 | 122.0444 | -0.01831 | 0.35706
2434.625 | 122.2595 | -0.10986 | 122.168 | -0.18135 | -0.045807 | 0.0036594 | 0.027209 | -0.00020513 | -0.006898 | -0.0028005 | -0.1077 | 0.0080877 | 0.065559 | 0.049405 | -0.016233 | 0.02933 | -0.0062207 | -0.12817 | -0.022888 | -0.059509 | -0.10986 | -0.045776 | -0.16022 | -0.050354 | 0.23804 | 122.0535 | -0.11902 | 121.9208 | 0.009155 | -0.045776 | 0.027466 | 0.050354 | -122.1909 | -122.2778 | 0.064087 | 0.059509 | -0.050354 | 0.009155 | -0.10071 | -0.009156 | -0.11444 | -0.24719 | 0.11902 | 0.13733 | 0.064087 | 0.14649 | 0.073243 | 0.013733 | -0.050354 | 0.12817 | 122.0398 | 0.036621 | 122.1725 | 0.086975 | 122.1634 | -122.2275 | -122.287 | 0 | 122.0306 | -0.018311 | 0.3479
2436.375 | 122.2824 | -0.10529 | 122.1634 | -0.082169 | -0.046234 | 0.004941 | 0.026355 | 0.0019311 | -0.0075388 | -0.0017325 | -0.089386 | 0.0063787 | 0.065986 | 0.051327 | -0.013456 | 0.026981 | -0.00066651 | -0.13275 | -0.022888 | -0.032043 | -0.10986 | -0.018311 | -0.13275 | -0.045776 | 0.27008 | 122.0627 | -0.091553 | 121.9391 | 0.041199 | -0.045776 | 0.050354 | 0.073243 | -122.1863 | -122.2733 | 0.086975 | 0.05951 | -0.027465 | -0.013733 | -0.10071 | 0.013733 | -0.10071 | -0.2243 | 0.14649 | 0.15564 | 0.05951 | 0.14191 | 0.045777 | 0.013732 | -0.07782 | 0.13275 | 122.0306 | 0.009155 | 122.1542 | 0.082398 | 122.168 | -122.1954 | -122.2549 | -0.004577 | 122.0444 | -0.027465 | 0.37537
2438.125 | 122.2595 | -0.10529 | 122.1634 | -0.11269 | -0.044525 | 0.00088223 | 0.02785 | 0.00022207 | -0.009675 | -0.0028005 | -0.1138 | 0.0063787 | 0.062141 | 0.051968 | -0.014311 | 0.029758 | -0.0030163 | -0.10071 | -0.032043 | -0.022888 | -0.073242 | 0.004578 | -0.10071 | -0.041199 | 0.34332 | 122.081 | -0.09613 | 121.9299 | 0.009155 | -0.059509 | 0.032043 | 0.082398 | -122.1954 | -122.2366 | 0.10986 | 0.064087 | 0.004578 | -0.018311 | -0.07782 | 0.009156 | -0.082397 | -0.23346 | 0.11444 | 0.13733 | 0.045777 | 0.12817 | 0.036621 | 0.027466 | -0.050354 | 0.10528 | 122.0261 | -0.009155 | 122.1771 | 0.073243 | 122.1863 | -122.1863 | -122.2595 | 0.032044 | 122.0352 | 0.004578 | 0.44861
2439.8125 | 122.3923 | -0.050354 | 122.1497 | -0.089798 | -0.04068 | 0.0040866 | 0.023791 | -0.00084593 | -0.0077524 | -0.0010915 | -0.04361 | 0.0044561 | 0.063423 | 0.053464 | -0.015592 | 0.027621 | -0.0055799 | -0.050354 | -0.050354 | -0.009155 | 0.032043 | 0.13733 | -0.027466 | 0.064087 | 0.39368 | 122.0123 | -0.054932 | 122.0352 | 0.14648 | 0.09613 | 0.16479 | 0.041199 | -122.2 | -122.1176 | 0.18768 | 0.11444 | 0.022888 | 0.073242 | -0.018311 | -0.004578 | -0.13733 | -0.11444 | 0.19684 | 0.21515 | 0.14648 | 0.21973 | 0.15106 | 0.14648 | 0.041198 | 0.20142 | 122.0901 | -0.041199 | 122.0673 | 0 | 122.0627 | -122.1588 | -122.2046 | 0.082397 | 122.0856 | 0 | 0.44403
2441.5781 | 122.3007 | -0.10071 | 122.2046 | -0.12032 | -0.046448 | 0.0036594 | 0.022509 | -0.0040503 | -0.0098886 | -0.0030141 | -0.037506 | 0.0050971 | 0.063636 | 0.041287 | -0.015806 | 0.024204 | -0.0025891 | -0.073242 | -0.064087 | -0.013733 | 0 | 0.1236 | 0 | 0.059509 | 0.50812 | 122.0306 | -0.068665 | 121.9574 | 0.073242 | 0.068665 | 0.064087 | 0.086975 | -122.2687 | -122.2046 | 0.2243 | 0.16022 | 0.10071 | 0.073242 | 0.013733 | 0.032043 | -0.17395 | -0.24719 | 0.17395 | 0.1648 | 0.16937 | 0.13275 | 0.13733 | 0.13733 | 0.013733 | 0.14191 | 122.0261 | -0.050354 | 122.0993 | 0.036621 | 122.1313 | -122.2183 | -122.2733 | 0.10071 | 122.0581 | 0.027466 | 0.60883
2443.2656 | 122.406 | -0.068665 | 122.1313 | -0.12032 | -0.046875 | 0.0023776 | 0.023578 | -0.0017005 | -0.010102 | -0.0034415 | 0.0052185 | 0.0057379 | 0.062141 | 0.047696 | -0.015806 | 0.024844 | -0.00045291 | -0.068665 | -0.068665 | -0.018311 | 0.032043 | 0.17395 | 0.027466 | 0.10529 | 0.55847 | 122.0032 | -0.068665 | 122.0535 | 0.16022 | 0.15106 | 0.14648 | 0.050354 | -122.2 | -122.0993 | 0.24261 | 0.17395 | 0.096131 | 0.1236 | 0.045777 | 0 | -0.12817 | -0.07782 | 0.22888 | 0.21515 | 0.21973 | 0.21515 | 0.21973 | 0.19226 | 0.050354 | 0.22888 | 122.1222 | -0.050354 | 122.0718 | 0 | 122.0718 | -122.1497 | -122.2 | 0.10071 | 122.1222 | 0 | 0.62714
2445.0156 | 122.3007 | -0.082397 | 122.1817 | -0.082169 | -0.044739 | 0.005582 | 0.027423 | 0.00022207 | -0.0098886 | -0.0036551 | -0.12296 | 0.0065923 | 0.062354 | 0.052609 | -0.017942 | 0.025912 | -0.0055799 | -0.091553 | -0.036621 | -0.018311 | -0.009155 | 0.045776 | -0.059509 | 0 | 0.43945 | 122.0764 | -0.07782 | 121.9711 | 0.073242 | 0.022888 | 0.068665 | 0.064086 | -122.2183 | -122.1909 | 0.12817 | 0.082397 | 0.022888 | 0.018311 | -0.041198 | 0.004577 | -0.10529 | -0.21057 | 0.15564 | 0.15106 | 0.10528 | 0.14649 | 0.10071 | 0.064087 | 0.009156 | 0.15106 | 122.049 | -0.01831 | 122.1542 | 0.045776 | 122.1588 | -122.2 | -122.2595 | 0.073242 | 122.0535 | -0.009156 | 0.52185
2446.7812 | 122.3053 | -0.09613 | 122.1634 | -0.11269 | -0.044312 | 0.003232 | 0.024859 | 0.0027857 | -0.0075388 | -0.0036551 | -0.074127 | 0.0074469 | 0.065559 | 0.051541 | -0.016874 | 0.02933 | -0.0042981 | -0.1236 | -0.022888 | -0.050354 | -0.086975 | 0 | -0.13275 | -0.036621 | 0.28839 | 122.0764 | -0.10529 | 121.962 | 0.045776 | 0.004578 | 0.068665 | 0.045776 | -122.1863 | -122.2504 | 0.09613 | 0.059509 | -0.036621 | 0.013733 | -0.082397 | -0.009156 | -0.086975 | -0.20142 | 0.14191 | 0.16479 | 0.10071 | 0.17395 | 0.10986 | 0.050354 | -0.036621 | 0.15106 | 122.0673 | 0.027466 | 122.1817 | 0.073242 | 122.1725 | -122.2137 | -122.2687 | 0.009155 | 122.0581 | -0.027466 | 0.38452
2448.4844 | 122.3419 | -0.086975 | 122.1725 | -0.12794 | -0.04538 | 0.0057956 | 0.028491 | -0.0017005 | -0.0077524 | -0.0040823 | -0.089386 | 0.0053107 | 0.064277 | 0.049191 | -0.014738 | 0.026553 | -0.0034435 | -0.1236 | -0.009155 | -0.032043 | -0.073242 | 0.018311 | -0.11902 | -0.009155 | 0.30212 | 122.049 | -0.086975 | 121.994 | 0.09613 | 0.050354 | 0.09613 | 0.054932 | -122.1817 | -122.2458 | 0.10529 | 0.07782 | -0.032044 | 0.022888 | -0.086976 | 0 | -0.1236 | -0.17853 | 0.1831 | 0.1831 | 0.13733 | 0.1831 | 0.13733 | 0.050354 | -0.041199 | 0.1831 | 122.081 | 0.022888 | 122.1359 | 0.07782 | 122.1359 | -122.2046 | -122.2595 | 0.013733 | 122.081 | -0.036621 | 0.3891
2450.2344 | 122.3236 | -0.082397 | 122.1451 | -0.18135 | -0.044312 | 0.003232 | 0.025927 | -0.00063233 | -0.0092478 | -0.0032277 | -0.022247 | 0.0033881 | 0.064918 | 0.042996 | -0.01602 | 0.027194 | -0.0066479 | -0.10986 | -0.073242 | 0 | -0.009155 | 0.082397 | -0.054932 | 0.041199 | 0.35248 | 122.0215 | -0.082397 | 121.9894 | 0.10986 | 0.064087 | 0.10529 | 0.082397 | -122.2183 | -122.1542 | 0.16479 | 0.1236 | 0.027465 | 0.041199 | -0.054932 | 0 | -0.1236 | -0.15564 | 0.19226 | 0.18768 | 0.14648 | 0.18768 | 0.14648 | 0.082397 | -0.009155 | 0.19226 | 122.0718 | -0.073242 | 122.1039 | 0.009155 | 122.1039 | -122.1451 | -122.2275 | 0.073242 | 122.0718 | -0.027466 | 0.43488
2451.9844 | 122.3053 | -0.091553 | 122.1771 | -0.12794 | -0.045166 | 0.0062228 | 0.026782 | -0.00063233 | -0.0092478 | -0.0055777 | -0.086334 | 0.0057379 | 0.062568 | 0.049191 | -0.017301 | 0.02869 | -0.0038709 | -0.14191 | -0.022888 | -0.036621 | -0.09613 | -0.013733 | -0.11444 | -0.041199 | 0.27466 | 122.0627 | -0.09613 | 121.9482 | 0.050354 | 0 | 0.054932 | 0.054932 | -122.2 | -122.2733 | 0.07782 | 0.050354 | -0.022888 | -0.004578 | -0.07782 | -0.004577 | -0.11444 | -0.22888 | 0.14191 | 0.14649 | 0.091553 | 0.15106 | 0.09613 | 0.022888 | -0.059509 | 0.14648 | 122.0444 | 0.013733 | 122.1588 | 0.068665 | 122.1542 | -122.2137 | -122.2733 | -0.004577 | 122.0398 | -0.050354 | 0.36621
2453.7344 | 122.4014 | -0.059509 | 122.1359 | -0.13557 | -0.046662 | 0.0045138 | 0.022937 | -0.0068273 | -0.011384 | -0.0030141 | 0.0021667 | 0.0042425 | 0.06385 | 0.044919 | -0.016447 | 0.026553 | -0.0034435 | -0.09613 | -0.054932 | -0.009155 | 0.009155 | 0.13275 | 0.027466 | 0.082397 | 0.51727 | 121.994 | -0.068665 | 122.0444 | 0.17853 | 0.13275 | 0.14648 | 0.050354 | -122.1909 | -122.1268 | 0.19226 | 0.14191 | 0.086975 | 0.091552 | 0.036621 | -0.009156 | -0.14191 | -0.091552 | 0.23804 | 0.20599 | 0.19226 | 0.21515 | 0.20142 | 0.14191 | 0.01831 | 0.24719 | 122.113 | -0.045777 | 122.0627 | 0.004577 | 122.0535 | -122.1451 | -122.2046 | 0.068664 | 122.1039 | -0.036621 | 0.57678
2455.4219 | 122.3557 | -0.07782 | 122.1359 | -0.15083 | -0.046021 | 0.0030184 | 0.024859 | -0.0017005 | -0.0075388 | -0.0013051 | -0.040558 | 0.0057379 | 0.065345 | 0.050686 | -0.016447 | 0.023776 | -0.0036573 | -0.073242 | -0.068665 | 0.009155 | 0.018311 | 0.14191 | -0.022888 | 0.064087 | 0.40741 | 122.0261 | -0.07782 | 121.994 | 0.10986 | 0.082397 | 0.12817 | 0.086975 | -122.2046 | -122.1176 | 0.21973 | 0.14191 | 0.054932 | 0.054932 | -0.032043 | 0 | -0.10986 | -0.14191 | 0.18768 | 0.20599 | 0.16022 | 0.20599 | 0.16022 | 0.13275 | 0.009156 | 0.18768 | 122.0718 | -0.07782 | 122.1039 | 0.009155 | 122.1039 | -122.1268 | -122.2137 | 0.096131 | 122.0718 | 0.004578 | 0.48523
2457.1875 | 122.2504 | -0.10071 | 122.1863 | -0.12032 | -0.042176 | 0.0036594 | 0.028064 | 8.47e-06 | -0.0083932 | -0.0034415 | -0.14432 | 0.0070197 | 0.061927 | 0.050046 | -0.016447 | 0.027621 | -0.0038709 | -0.15564 | -0.004578 | -0.059509 | -0.11444 | -0.064087 | -0.17395 | -0.059509 | 0.23804 | 122.081 | -0.11444 | 121.9208 | 0.004578 | -0.050354 | 0.022888 | 0.041199 | -122.1909 | -122.3007 | 0.036621 | 0.041199 | -0.073242 | 0 | -0.11444 | -0.013733 | -0.10528 | -0.2655 | 0.10529 | 0.1236 | 0.050354 | 0.13733 | 0.064087 | -0.004578 | -0.054932 | 0.11902 | 122.0352 | 0.054931 | 122.1954 | 0.09613 | 122.1817 | -122.2458 | -122.3007 | -0.013733 | 122.0215 | -0.054932 | 0.33875
2458.9375 | 122.2778 | -0.10986 | 122.2046 | -0.082169 | -0.045807 | 0.002164 | 0.023578 | -0.0040503 | -0.007966 | -0.0057913 | -0.049713 | 0.0070197 | 0.062782 | 0.054745 | -0.014311 | 0.028049 | -0.0055799 | -0.14648 | -0.013733 | -0.050354 | -0.10071 | 0.013733 | -0.10071 | -0.009155 | 0.42114 | 122.0764 | -0.086975 | 121.8933 | 0.032043 | -0.018311 | 0.004578 | 0.059509 | -122.2183 | -122.3053 | 0.1236 | 0.10071 | 0.009155 | 0.041199 | -0.050354 | 0.022888 | -0.12817 | -0.31128 | 0.14191 | 0.11444 | 0.091552 | 0.091553 | 0.068664 | 0.064087 | -0.050354 | 0.11902 | 121.9803 | 0.036621 | 122.1634 | 0.09613 | 122.1863 | -122.2549 | -122.2916 | 0.009155 | 122.0032 | -0.036621 | 0.53101
2460.7031 | 122.2504 | -0.1236 | 122.1542 | -0.082169 | -0.049012 | 0.0034456 | 0.0255 | -0.0042639 | -0.0098886 | -0.0045095 | -0.04361 | 0.0050971 | 0.064063 | 0.048764 | -0.015379 | 0.026981 | -0.0023755 | -0.14648 | -0.022888 | -0.054932 | -0.10071 | 0.004578 | -0.09613 | -0.032043 | 0.40741 | 122.0673 | -0.10529 | 121.9162 | 0.022888 | -0.032043 | 0.013733 | 0.068664 | -122.1771 | -122.2549 | 0.12817 | 0.091553 | 0.027466 | 0.022889 | -0.041198 | 0.01831 | -0.086975 | -0.23804 | 0.14648 | 0.13733 | 0.091553 | 0.11902 | 0.073243 | 0.05951 | -0.045776 | 0.12817 | 122.0215 | 0.032044 | 122.1725 | 0.10071 | 122.1909 | -122.2092 | -122.2595 | 0.022888 | 122.0398 | -0.022888 | 0.53101
2462.4219 | 122.2687 | -0.10986 | 122.1863 | -0.097427 | -0.046021 | 0.001523 | 0.024646 | 0.0015039 | -0.012025 | -0.0042959 | -0.052765 | 0.0057379 | 0.065345 | 0.050259 | -0.017088 | 0.025272 | -0.0025891 | -0.15564 | -0.027466 | -0.045776 | -0.09613 | -0.013733 | -0.10529 | -0.027466 | 0.40741 | 122.0764 | -0.10986 | 121.9254 | 0.032043 | -0.022888 | 0.018311 | 0.064087 | -122.2137 | -122.2824 | 0.09613 | 0.082397 | 0.004577 | 0.01831 | -0.05951 | 0 | -0.10986 | -0.26093 | 0.14191 | 0.12817 | 0.086975 | 0.12817 | 0.086975 | 0.032043 | -0.050354 | 0.14191 | 122.0352 | 0.01831 | 122.1863 | 0.082397 | 122.1863 | -122.2321 | -122.2961 | 0.013733 | 122.0352 | -0.045777 | 0.51727
2464.1719 | 122.406 | -0.054932 | 122.1863 | -0.15083 | -0.046448 | 0.0025912 | 0.022937 | -0.0014867 | -0.010316 | -0.00023714 | 0.0021667 | 0.0042425 | 0.064063 | 0.044919 | -0.01602 | 0.02634 | -0.0042981 | -0.068665 | -0.054932 | -0.013733 | 0.054932 | 0.16937 | 0.032043 | 0.11444 | 0.56763 | 121.994 | -0.050354 | 122.0535 | 0.17853 | 0.14648 | 0.14648 | 0.041199 | -122.2412 | -122.1313 | 0.22431 | 0.16937 | 0.086975 | 0.12817 | 0.045776 | 0.004578 | -0.19226 | -0.13275 | 0.23346 | 0.20142 | 0.20142 | 0.19684 | 0.19684 | 0.18311 | 0.068665 | 0.22888 | 122.1039 | -0.041199 | 122.0444 | 0 | 122.049 | -122.2 | -122.2366 | 0.10986 | 122.1085 | -0.013733 | 0.62256
2465.875 | 122.2458 | -0.10986 | 122.1771 | -0.12794 | -0.042603 | 0.0036594 | 0.028491 | 0.00022207 | -0.010957 | -0.00087794 | -0.10464 | 0.0059515 | 0.065559 | 0.055386 | -0.016233 | 0.027621 | -0.0060071 | -0.11902 | -0.036621 | -0.041199 | -0.09613 | -0.027466 | -0.13733 | -0.054932 | 0.26093 | 122.0627 | -0.10986 | 121.9116 | -0.027466 | -0.064087 | 0.004578 | 0.068664 | -122.2137 | -122.2733 | 0.082397 | 0.054931 | -0.027466 | -0.013733 | -0.09613 | 0 | -0.11444 | -0.2655 | 0.082397 | 0.11444 | 0.045776 | 0.11444 | 0.045776 | 0.013733 | -0.054931 | 0.082397 | 122.0215 | 0.004578 | 122.1725 | 0.073242 | 122.1725 | -122.2183 | -122.287 | 0.013733 | 122.0215 | -0.009156 | 0.37079
2467.6406 | 122.2824 | -0.086975 | 122.1909 | -0.15846 | -0.044312 | 0.004941 | 0.027423 | -0.0023413 | -0.007966 | -0.0057913 | -0.089386 | 0.0061651 | 0.06385 | 0.051541 | -0.015592 | 0.027194 | -0.0030163 | -0.13275 | -0.022888 | -0.036621 | -0.10986 | -0.013733 | -0.13275 | -0.045776 | 0.2655 | 122.0627 | -0.10529 | 121.9437 | 0.032043 | -0.032043 | 0.032043 | 0.050354 | -122.2137 | -122.3007 | 0.073242 | 0.041199 | -0.045776 | -0.009155 | -0.09613 | -0.018311 | -0.12817 | -0.24719 | 0.11902 | 0.11902 | 0.054932 | 0.13733 | 0.073243 | 0.022888 | -0.073242 | 0.13733 | 122.049 | 0.013733 | 122.168 | 0.064087 | 122.1497 | -122.2275 | -122.2961 | -0.022888 | 122.0306 | -0.045776 | 0.35248
2469.3281 | 122.2458 | -0.10529 | 122.1725 | -0.1432 | -0.044098 | 0.0053684 | 0.028705 | -0.0010595 | -0.0094614 | -0.0036551 | -0.10464 | 0.0055243 | 0.064704 | 0.051968 | -0.017088 | 0.02869 | -0.0060071 | -0.10529 | -0.032043 | -0.045776 | -0.068665 | 0.018311 | -0.10529 | -0.032043 | 0.3479 | 122.0673 | -0.10071 | 121.9345 | 0.027466 | -0.041199 | 0.036621 | 0.05951 | -122.2046 | -122.2412 | 0.1236 | 0.073243 | 0 | 0.013733 | -0.05951 | 0.004578 | -0.10528 | -0.23804 | 0.13275 | 0.14191 | 0.064087 | 0.13733 | 0.059509 | 0.064087 | -0.022889 | 0.12817 | 122.0352 | 0.013733 | 122.168 | 0.073243 | 122.1725 | -122.2183 | -122.2733 | 0.036621 | 122.0398 | 0 | 0.45319
2471.0938 | 122.3419 | -0.059509 | 122.1405 | -0.12794 | -0.045166 | 0.002164 | 0.021655 | 0.00043587 | -0.0088206 | -0.0036551 | -0.016144 | 0.0040289 | 0.064491 | 0.053891 | -0.016447 | 0.027621 | -0.0051525 | -0.11902 | -0.073242 | -0.022888 | -0.032043 | 0.068665 | -0.032043 | 0.036621 | 0.35706 | 122.0398 | -0.091553 | 121.9849 | 0.10529 | 0.073242 | 0.09613 | 0.036621 | -122.2137 | -122.1725 | 0.12817 | 0.09613 | 0.027466 | 0.059509 | -0.009155 | -0.032044 | -0.10071 | -0.15564 | 0.16479 | 0.15564 | 0.13275 | 0.18768 | 0.16479 | 0.091553 | -0.009155 | 0.19684 | 122.0764 | -0.050354 | 122.1313 | -0.013733 | 122.0993 | -122.1634 | -122.2321 | 0.027466 | 122.0444 | -0.05951 | 0.41656
2472.8594 | 122.2916 | -0.11902 | 122.1863 | -0.12032 | -0.044953 | 0.001523 | 0.024432 | -0.0023413 | -0.0092478 | -0.0047231 | -0.016144 | 0.0042425 | 0.065345 | 0.047909 | -0.01602 | 0.026553 | -0.0047253 | -0.10071 | -0.045776 | -0.027466 | -0.059509 | 0.045776 | -0.050354 | 0.004578 | 0.4303 | 122.0535 | -0.086975 | 121.9162 | 0.054932 | -0.004578 | 0.018311 | 0.091553 | -122.2321 | -122.2458 | 0.16479 | 0.1236 | 0.068665 | 0.032044 | -0.022888 | 0.032044 | -0.13275 | -0.27008 | 0.17395 | 0.13733 | 0.11444 | 0.10529 | 0.082397 | 0.073242 | -0.032043 | 0.14191 | 122.0032 | -0.01831 | 122.1405 | 0.073243 | 122.1725 | -122.2137 | -122.2733 | 0.05951 | 122.0352 | 0.018311 | 0.54932
2474.5469 | 122.2824 | -0.11902 | 122.2046 | -0.17372 | -0.044953 | 0.0025912 | 0.027209 | 0.0029993 | -0.007966 | -0.0036551 | -0.12296 | 0.0055243 | 0.063209 | 0.052395 | -0.01666 | 0.026981 | -0.0077161 | -0.13733 | -0.032043 | -0.050354 | -0.10529 | -0.022888 | -0.14648 | -0.045776 | 0.26093 | 122.0673 | -0.10529 | 121.9254 | 0.018311 | -0.041199 | 0.041199 | 0.068665 | -122.2366 | -122.3099 | 0.096131 | 0.073243 | -0.027465 | 0.004578 | -0.09613 | 0.013733 | -0.13733 | -0.27924 | 0.13733 | 0.16022 | 0.07782 | 0.14649 | 0.064087 | 0.027466 | -0.054932 | 0.1236 | 122.0306 | 0.018311 | 122.1725 | 0.086976 | 122.1863 | -122.2549 | -122.3099 | 0.013733 | 122.0444 | -0.01831 | 0.37994
2476.2969 | 122.2916 | -0.091553 | 122.1725 | -0.18898 | -0.045166 | 0.003873 | 0.0255 | -0.0019141 | -0.0088206 | -0.0025869 | -0.01004 | 0.0050971 | 0.065345 | 0.046841 | -0.016233 | 0.025058 | -0.0057935 | -0.068665 | -0.050354 | -0.009155 | 0 | 0.09613 | -0.013733 | 0.054932 | 0.49896 | 122.0535 | -0.091553 | 121.9482 | 0.086975 | 0.045776 | 0.064087 | 0.082398 | -122.2229 | -122.1725 | 0.18768 | 0.14649 | 0.07782 | 0.064087 | -0.004578 | 0 | -0.11902 | -0.2243 | 0.17853 | 0.15564 | 0.13733 | 0.15564 | 0.13733 | 0.10528 | 0.009155 | 0.17853 | 122.0398 | -0.041199 | 122.1451 | 0.041199 | 122.1451 | -122.1817 | -122.2641 | 0.091553 | 122.0398 | 0.022888 | 0.59052
2478.0625 | 122.2641 | -0.1236 | 122.1634 | -0.1432 | -0.044525 | 0.001523 | 0.026782 | -0.0019141 | -0.012666 | -0.0040823 | -0.025299 | 0.0050971 | 0.067268 | 0.042355 | -0.015592 | 0.028262 | -0.0053661 | -0.11902 | -0.027466 | -0.027466 | -0.07782 | 0.032043 | -0.068665 | 0.004578 | 0.44403 | 122.0718 | -0.09613 | 121.907 | 0.045776 | 0 | 0.013733 | 0.09613 | -122.1909 | -122.2412 | 0.15564 | 0.12817 | 0.054931 | 0.032044 | -0.041199 | 0.027466 | -0.091553 | -0.25635 | 0.16937 | 0.13733 | 0.1236 | 0.10986 | 0.09613 | 0.059509 | -0.050354 | 0.14191 | 122.0032 | 0 | 122.168 | 0.09613 | 122.1954 | -122.1909 | -122.2595 | 0.045776 | 122.0306 | 0.004577 | 0.56763
2479.8281 | 122.3511 | -0.07782 | 122.168 | -0.089798 | -0.046662 | 0.0019504 | 0.023791 | 0.00043587 | -0.011811 | -0.0034415 | -0.013092 | 0.0044561 | 0.062354 | 0.049618 | -0.015592 | 0.02634 | -0.0068615 | -0.059509 | -0.064087 | -0.013733 | 0.022888 | 0.1236 | 0.027466 | 0.091553 | 0.54932 | 122.0398 | -0.073242 | 122.0169 | 0.15564 | 0.11444 | 0.13275 | 0.064087 | -122.2321 | -122.1451 | 0.20142 | 0.16937 | 0.10529 | 0.10529 | 0.041199 | 0.004578 | -0.12817 | -0.15106 | 0.23346 | 0.21057 | 0.19226 | 0.20599 | 0.18768 | 0.13733 | 0.036621 | 0.22888 | 122.0901 | -0.050354 | 122.113 | 0.013733 | 122.1176 | -122.1817 | -122.2412 | 0.10071 | 122.0947 | 0.018311 | 0.62714
2481.5938 | 123.8342 | -0.09613 | 122.1542 | -0.12032 | -0.04773 | 0.0025912 | 0.024218 | -0.0066137 | -0.011811 | -0.0034415 | -0.013092 | 0.0038153 | 0.062995 | 0.051755 | -0.015165 | 0.02634 | -0.0038709 | 0.29297 | -0.054932 | -0.036621 | 0.99335 | 0.59052 | 0.009155 | 0.65002 | 1.2222 | 122.0398 | -0.059509 | 121.9894 | 1.5472 | 5.0629 | 0.41199 | 0.059509 | -122.2092 | -121.1609 | 0.68664 | 0.74615 | 0.10528 | 0.68665 | 0.045776 | 0.036621 | -0.11444 | -0.16479 | 1.6434 | 0.50812 | 5.159 | 0.4715 | 5.1224 | 0.62714 | 1.03 | 1.6068 | 122.049 | -0.018311 | 122.0993 | 0.041198 | 122.1359 | -122.1909 | -122.2137 | 1.0895 | 122.0856 | 0.3891 | 1.3184
2483.2969 | 122.4976 | -0.091553 | 122.1634 | -0.097427 | -0.046021 | 0.0030184 | 0.026355 | -0.00063233 | -0.01117 | -0.0040823 | -0.098541 | 0.0061651 | 0.064277 | 0.052609 | -0.017729 | 0.02634 | -0.0053661 | -0.07782 | -0.018311 | -0.036621 | 0.17853 | 0.091553 | -0.07782 | 0.050354 | 0.62714 | 122.0718 | -0.073242 | 122.2229 | 0.42114 | 1.2405 | 0.21973 | 0.054932 | -122.1817 | -121.9849 | 0.18311 | 0.14191 | 0.013733 | 0.086975 | -0.041199 | 0.018311 | -0.091553 | 0.059509 | 0.5127 | 0.31128 | 1.3321 | 0.29297 | 1.3138 | 0.12817 | 0.21515 | 0.49438 | 122.2961 | 0.01831 | 122.1451 | 0.073242 | 122.1634 | -122.2 | -122.2366 | 0.27008 | 122.3145 | 0.013733 | 0.71869
2485.0469 | 122.5525 | -0.068665 | 122.1588 | -0.13557 | -0.044525 | 0.0023776 | 0.023578 | -0.0012731 | -0.0073252 | -0.0057913 | -0.013092 | 0.0061651 | 0.064277 | 0.045559 | -0.017301 | 0.027835 | -0.0028027 | 0.38452 | -0.050354 | -0.009155 | 0.39368 | 0.1831 | 0.050354 | 0.44403 | 0.46234 | 122.0581 | -0.082397 | 122.3785 | 0.36163 | 1.3916 | 0.29297 | 0.05951 | -122.2092 | -121.7651 | 0.25177 | 0.5127 | 0.11902 | 0.45319 | 0.059509 | -0.013732 | -0.10071 | 0.21973 | 0.4303 | 0.36163 | 1.4603 | 0.37537 | 1.474 | 0.19226 | 0.40283 | 0.44403 | 122.4609 | -0.041199 | 122.1405 | 0.018311 | 122.1268 | -122.168 | -122.2412 | 0.46234 | 122.4472 | 0.45319 | 0.53101
2486.8125 | 122.4792 | -0.054932 | 122.1542 | -0.17372 | -0.044312 | 0.003873 | 0.024646 | -0.0010595 | -0.0077524 | -0.0070731 | -0.064972 | 0.0050971 | 0.062568 | 0.053464 | -0.017301 | 0.028049 | -0.0045117 | 0.027466 | -0.050354 | -0.004578 | 0.11444 | 0.34332 | 0.091553 | 0.12817 | 0.46692 | 122.0078 | -0.059509 | 122.5204 | 0.27008 | 0.39825 | 0.52643 | 0.050354 | -122.2046 | -122.0398 | 0.39825 | 0.18311 | 0.14649 | 0.13275 | 0.096131 | -0.004577 | -0.14648 | 0.36621 | 0.32501 | 0.58136 | 0.45319 | 0.58594 | 0.45776 | 0.3479 | 0.11902 | 0.32959 | 122.58 | -0.045776 | 122.0673 | 0.004578 | 122.0627 | -122.1588 | -122.2137 | 0.16937 | 122.5754 | 0.082398 | 0.52185
2488.5 | 122.3557 | -0.09613 | 122.1863 | -0.06691 | -0.045166 | 0.0040866 | 0.024218 | -0.0046911 | -0.0094614 | -0.0042959 | -0.025299 | 0.0040289 | 0.062141 | 0.049832 | -0.01666 | 0.025699 | -0.0066479 | -0.009155 | -0.050354 | -0.009155 | 0.073242 | 0.086975 | -0.027466 | 0.073242 | 0.52643 | 122.0581 | -0.082397 | 122.049 | 0.15564 | 0.24261 | 0.082397 | 0.086975 | -122.2366 | -122.113 | 0.1831 | 0.16937 | 0.068664 | 0.082397 | -0.018311 | 0.013733 | -0.12817 | -0.13733 | 0.25177 | 0.17853 | 0.33874 | 0.16479 | 0.32501 | 0.09613 | 0.082397 | 0.23804 | 122.1313 | -0.041199 | 122.1405 | 0.045776 | 122.1542 | -122.1954 | -122.2687 | 0.16937 | 122.1451 | 0.086975 | 0.62256
2490.25 | 122.4014 | -0.068665 | 122.1634 | -0.17372 | -0.045166 | 0.0030184 | 0.025927 | -0.00084593 | -0.010957 | -0.0023733 | -0.11075 | 0.0080877 | 0.062995 | 0.051327 | -0.018583 | 0.026767 | -0.0015209 | -0.091553 | -0.036621 | -0.022888 | -0.032043 | 0.045776 | -0.091553 | 0.036621 | 0.37537 | 122.0581 | -0.07782 | 122.0169 | 0.11444 | 0.12817 | 0.16479 | 0.045777 | -122.2 | -122.1954 | 0.11444 | 0.10529 | -0.022888 | 0.059509 | -0.068665 | -0.009155 | -0.10529 | -0.14648 | 0.18311 | 0.23346 | 0.19684 | 0.24261 | 0.20599 | 0.068664 | -0.009155 | 0.19226 | 122.0947 | -0.013733 | 122.1359 | 0.032044 | 122.1268 | -122.1863 | -122.2412 | 0.036622 | 122.0856 | -0.022888 | 0.44403
2492.0156 | 122.3511 | -0.091553 | 122.1497 | -0.17372 | -0.046448 | 0.0040866 | 0.022937 | 0.00043587 | -0.01053 | -0.0064321 | -0.040558 | 0.0063787 | 0.064063 | 0.046628 | -0.016233 | 0.025912 | -0.0034435 | -0.10071 | -0.050354 | -0.013733 | -0.013733 | 0.073242 | -0.041199 | 0.050354 | 0.37537 | 122.0306 | -0.064087 | 122.0352 | 0.091553 | 0.064087 | 0.13275 | 0.07782 | -122.2 | -122.1634 | 0.16479 | 0.14191 | 0.050354 | 0.064087 | -0.027466 | 0.027466 | -0.11902 | -0.11444 | 0.18311 | 0.2243 | 0.15564 | 0.19684 | 0.12817 | 0.086975 | 0 | 0.15564 | 122.0993 | -0.036621 | 122.0947 | 0.041199 | 122.1222 | -122.1634 | -122.2137 | 0.07782 | 122.1268 | -0.009155 | 0.46692
2493.7031 | 122.374 | -0.07782 | 122.1634 | -0.1432 | -0.046448 | 0.0017368 | 0.023578 | -0.0027685 | -0.011598 | -0.0032277 | -0.025299 | 0.0031745 | 0.061927 | 0.049191 | -0.016874 | 0.026981 | -0.0053661 | -0.022888 | -0.059509 | -0.004578 | 0.068665 | 0.14191 | 0.013733 | 0.10071 | 0.5722 | 122.0535 | -0.054932 | 122.0398 | 0.17395 | 0.19684 | 0.14648 | 0.073242 | -122.2229 | -122.0947 | 0.21973 | 0.17853 | 0.091553 | 0.10529 | 0.018311 | 0.022888 | -0.10986 | -0.1236 | 0.25177 | 0.2243 | 0.27466 | 0.20142 | 0.25177 | 0.14649 | 0.073243 | 0.22888 | 122.0947 | -0.054931 | 122.1085 | 0.018311 | 122.1313 | -122.168 | -122.2183 | 0.14649 | 122.1176 | 0.054932 | 0.65002
2495.4375 | 122.3923 | -0.09613 | 122.1954 | -0.051651 | -0.045807 | 0.001523 | 0.028277 | -0.0049047 | -0.010316 | -0.0042959 | -0.089386 | 0.0065923 | 0.066413 | 0.047482 | -0.017729 | 0.026553 | -0.0072889 | -0.14191 | -0.004578 | -0.059509 | -0.032043 | 0.013733 | -0.082397 | 0.018311 | 0.56763 | 122.0856 | -0.09613 | 121.9849 | 0.11902 | 0.29755 | 0.21057 | 0.036621 | -122.2 | -122.2275 | 0.10986 | 0.11444 | 0.013733 | 0.07782 | -0.022888 | 0 | -0.10986 | -0.21057 | 0.21515 | 0.3067 | 0.39368 | 0.3067 | 0.39368 | 0.073242 | 0.027466 | 0.21515 | 122.081 | 0.054931 | 122.1817 | 0.091552 | 122.1817 | -122.2549 | -122.2916 | 0.064087 | 122.081 | -0.045777 | 0.66376
2497.1875 | 122.3373 | -0.10529 | 122.2 | -0.11269 | -0.046021 | 0.0013094 | 0.025714 | 0.00022207 | -0.010316 | -0.0021597 | -0.080231 | 0.0072333 | 0.064063 | 0.050046 | -0.015592 | 0.026981 | -0.0060071 | -0.14191 | -0.004578 | -0.068665 | -0.036621 | 0.022888 | -0.10986 | -0.009155 | 0.54474 | 122.0764 | -0.10986 | 121.962 | 0.086975 | 0.24719 | 0.12817 | 0.036621 | -122.2046 | -122.2366 | 0.12817 | 0.096131 | -0.004577 | 0.05951 | -0.041198 | -0.004577 | -0.1236 | -0.23804 | 0.19226 | 0.23346 | 0.35248 | 0.23804 | 0.35706 | 0.091553 | 0.032044 | 0.19684 | 122.0718 | 0.064087 | 122.1863 | 0.10071 | 122.1817 | -122.2687 | -122.3099 | 0.068665 | 122.0673 | -0.036621 | 0.65002
2498.9375 | 122.4518 | -0.050354 | 122.168 | -0.15083 | -0.04303 | 0.0047274 | 0.026355 | 0.0012903 | -0.0083932 | -0.0045095 | -0.071076 | 0.0044561 | 0.06385 | 0.044705 | -0.015806 | 0.028476 | -0.0042981 | -0.059509 | -0.045776 | -0.009155 | 0.07782 | 0.14191 | -0.022888 | 0.082397 | 0.52643 | 122.0444 | -0.07782 | 122.1085 | 0.19226 | 0.34332 | 0.27466 | 0.041199 | -122.2137 | -122.0901 | 0.19226 | 0.13275 | 0.027466 | 0.091552 | -0.013733 | -0.027466 | -0.1236 | -0.05951 | 0.24261 | 0.32501 | 0.39368 | 0.35248 | 0.42114 | 0.15106 | 0.086975 | 0.27008 | 122.1863 | -0.036621 | 122.1222 | 0.004578 | 122.0947 | -122.1771 | -122.2458 | 0.12817 | 122.1588 | -0.009155 | 0.57678
2500.6406 | 122.319 | -0.10071 | 122.2321 | -0.12032 | -0.043244 | 0.0062228 | 0.028277 | -0.0021277 | -0.0075388 | -0.0038687 | -0.12601 | 0.0068059 | 0.063423 | 0.048337 | -0.017301 | 0.028049 | -0.0047253 | -0.10986 | -0.018311 | -0.045776 | 0 | 0.036621 | -0.1236 | -0.004578 | 0.44403 | 122.0856 | -0.10071 | 121.9574 | 0.064087 | 0.1831 | 0.14191 | 0.054932 | -122.2504 | -122.2321 | 0.13733 | 0.09613 | -0.022888 | 0.041198 | -0.07782 | 0 | -0.14648 | -0.27466 | 0.1648 | 0.24262 | 0.28381 | 0.24262 | 0.28381 | 0.082397 | 0.045776 | 0.1648 | 122.0581 | 0.027465 | 122.1863 | 0.082397 | 122.1863 | -122.2778 | -122.3328 | 0.10071 | 122.0581 | -0.009155 | 0.54474
2502.3906 | 122.3465 | -0.11444 | 122.1725 | -0.1432 | -0.043885 | 0.0057956 | 0.026782 | -0.0014867 | -0.0083932 | -0.0030141 | -0.098541 | 0.0053107 | 0.064277 | 0.053677 | -0.015165 | 0.028049 | -0.0064343 | -0.14191 | -0.018311 | -0.027466 | -0.068665 | -0.022888 | -0.14191 | -0.032043 | 0.38452 | 122.0856 | -0.09613 | 121.9574 | 0.073242 | 0.17853 | 0.12817 | 0.086975 | -122.1909 | -122.2412 | 0.091553 | 0.082398 | -0.027466 | -0.004577 | -0.11444 | 0.018311 | -0.086975 | -0.21515 | 0.18768 | 0.24262 | 0.29297 | 0.2243 | 0.27466 | 0.004578 | -0.041199 | 0.16937 | 122.0535 | 0.009155 | 122.1817 | 0.09613 | 122.2 | -122.2 | -122.2687 | 0.045776 | 122.0718 | -0.027466 | 0.49896
2504.1406 | 122.4243 | -0.073242 | 122.1634 | -0.11269 | -0.045166 | 0.003232 | 0.024218 | 8.47e-06 | -0.007966 | -0.0019461 | -0.092438 | 0.0061651 | 0.064277 | 0.04855 | -0.014311 | 0.029117 | -0.0060071 | -0.14191 | -0.027466 | -0.036621 | -0.018311 | 0.041199 | -0.10986 | 0.018311 | 0.45319 | 122.0764 | -0.082397 | 122.0398 | 0.16022 | 0.31128 | 0.22888 | 0.036621 | -122.1909 | -122.1817 | 0.11444 | 0.091553 | -0.036621 | 0.054932 | -0.073242 | -0.009155 | -0.086975 | -0.1236 | 0.23346 | 0.30212 | 0.38452 | 0.31128 | 0.39368 | 0.07782 | 0.01831 | 0.24261 | 122.1222 | 0.009155 | 122.1588 | 0.045776 | 122.1497 | -122.2 | -122.2458 | 0.054931 | 122.113 | -0.068665 | 0.52643
2505.8906 | 122.3373 | -0.091553 | 122.1451 | -0.17372 | -0.043671 | 0.0034456 | 0.026355 | 0.0047083 | -0.0090342 | -0.0019461 | -0.068024 | 0.0063787 | 0.065345 | 0.046414 | -0.015806 | 0.025699 | -0.0038709 | -0.1236 | -0.027466 | -0.054932 | -0.036621 | 0.004578 | -0.14191 | 0 | 0.39368 | 122.0764 | -0.10529 | 121.9986 | 0.09613 | 0.23346 | 0.13733 | 0.036621 | -122.1725 | -122.1817 | 0.096131 | 0.091553 | -0.050354 | 0.054932 | -0.086975 | -0.013733 | -0.068665 | -0.14648 | 0.18768 | 0.22888 | 0.32501 | 0.24262 | 0.33875 | 0.05951 | 0.018311 | 0.20142 | 122.1039 | 0.027466 | 122.1817 | 0.064087 | 122.168 | -122.2 | -122.2504 | 0.054932 | 122.0901 | -0.032043 | 0.48523
2507.6406 | 122.4014 | -0.073242 | 122.1451 | -0.1432 | -0.046021 | 0.0030184 | 0.0255 | -0.0010595 | -0.0083932 | -0.0032277 | 0.011322 | 0.0053107 | 0.064704 | 0.050473 | -0.015379 | 0.02634 | -0.0030163 | -0.10986 | -0.054932 | -0.022888 | 0.032043 | 0.086975 | -0.036621 | 0.07782 | 0.52643 | 122.0398 | -0.09613 | 122.0535 | 0.1831 | 0.33875 | 0.21057 | 0.050354 | -122.2 | -122.113 | 0.16022 | 0.15106 | 0.036621 | 0.10071 | -0.013733 | -0.022888 | -0.10529 | -0.091553 | 0.25635 | 0.28381 | 0.41199 | 0.3067 | 0.43488 | 0.10986 | 0.054931 | 0.27924 | 122.1497 | -0.032044 | 122.1359 | 0.01831 | 122.113 | -122.168 | -122.2412 | 0.10529 | 122.1268 | -0.036621 | 0.59967
2509.3906 | 122.4289 | -0.064087 | 122.1405 | -0.12794 | -0.04303 | 0.0028048 | 0.023578 | -0.0049047 | -0.0088206 | -0.0055777 | -0.0008851 | 0.0050971 | 0.065986 | 0.049832 | -0.017088 | 0.027408 | -0.0019483 | -0.09613 | -0.064087 | -0.022888 | 0.045776 | 0.10986 | -0.004578 | 0.07782 | 0.56305 | 122.0261 | -0.086975 | 122.0581 | 0.20599 | 0.36621 | 0.24719 | 0.041199 | -122.2046 | -122.0947 | 0.17395 | 0.14191 | 0.059509 | 0.10071 | 0.01831 | -0.022888 | -0.11444 | -0.082398 | 0.27008 | 0.31128 | 0.4303 | 0.33417 | 0.45319 | 0.13275 | 0.068664 | 0.29297 | 122.1451 | -0.041199 | 122.113 | 0 | 122.0901 | -122.1634 | -122.2275 | 0.10986 | 122.1222 | -0.032043 | 0.62714
2511.0938 | 122.4289 | -0.054932 | 122.1268 | -0.18898 | -0.044739 | 0.003232 | 0.026141 | 8.47e-06 | -0.0090342 | -0.0057913 | -0.058869 | 0.0070197 | 0.064063 | 0.05325 | -0.017942 | 0.026553 | -0.0051525 | -0.054932 | -0.036621 | -0.004578 | 0.082397 | 0.13733 | -0.018311 | 0.073242 | 0.52185 | 122.0261 | -0.068665 | 122.0947 | 0.21515 | 0.32501 | 0.26093 | 0.050354 | -122.1634 | -122.0444 | 0.19226 | 0.12817 | 0.036621 | 0.07782 | -0.013733 | -0.013733 | -0.10071 | -0.032043 | 0.27008 | 0.31586 | 0.37994 | 0.32959 | 0.39368 | 0.14191 | 0.086975 | 0.28381 | 122.1634 | -0.032043 | 122.0947 | 0.018311 | 122.081 | -122.1313 | -122.1954 | 0.13733 | 122.1497 | 0 | 0.57678
2512.8594 | 122.4289 | -0.059509 | 122.1542 | -0.16609 | -0.043885 | 0.002164 | 0.024432 | -0.00084593 | -0.007966 | -0.0015189 | -0.058869 | 0.0033881 | 0.065345 | 0.050473 | -0.018156 | 0.02634 | -0.0066479 | -0.068665 | -0.054932 | -0.004578 | 0.091553 | 0.15564 | -0.022888 | 0.091553 | 0.53558 | 122.0261 | -0.068665 | 122.0901 | 0.20142 | 0.34332 | 0.24261 | 0.054931 | -122.2092 | -122.0627 | 0.21515 | 0.15106 | 0.036621 | 0.096131 | -0.01831 | -0.009156 | -0.12817 | -0.064087 | 0.26093 | 0.30212 | 0.40283 | 0.31128 | 0.41199 | 0.16022 | 0.096131 | 0.27008 | 122.1588 | -0.050354 | 122.0947 | 0.004577 | 122.0856 | -122.1588 | -122.2229 | 0.15106 | 122.1497 | -0.009156 | 0.59509
2514.625 | 122.2778 | -0.10986 | 122.2092 | -0.12794 | -0.044312 | 0.0034456 | 0.028277 | 0.0010767 | -0.01053 | -0.00066434 | -0.10464 | 0.0070197 | 0.065345 | 0.051541 | -0.017729 | 0.029544 | -0.0032299 | -0.10529 | -0.027466 | -0.045776 | 0.013733 | 0.013733 | -0.14191 | 0.009155 | 0.41199 | 122.0718 | -0.11444 | 122.0444 | 0.022888 | 0.073242 | 0.091553 | 0.064087 | -122.2366 | -122.1954 | 0.1236 | 0.11902 | -0.032044 | 0.054931 | -0.096131 | -0.004578 | -0.13733 | -0.16479 | 0.13275 | 0.20142 | 0.18311 | 0.20599 | 0.18768 | 0.059509 | 0.059509 | 0.13733 | 122.1588 | 0.01831 | 122.1863 | 0.082397 | 122.1817 | -122.2549 | -122.3236 | 0.1236 | 122.1542 | 0.004577 | 0.52185
2516.3125 | 122.287 | -0.10986 | 122.2046 | -0.11269 | -0.045807 | 0.0036594 | 0.026141 | 0.0010767 | -0.010316 | -0.0021597 | -0.058869 | 0.0050971 | 0.064491 | 0.046628 | -0.01602 | 0.025912 | -0.0075025 | -0.16937 | -0.013733 | -0.045776 | -0.086975 | -0.009155 | -0.10529 | 0.004578 | 0.55389 | 122.0718 | -0.10071 | 122.113 | 0.10986 | 0.091553 | 0.20599 | 0.064087 | -122.2183 | -122.2916 | 0.10071 | 0.11444 | 0.004577 | 0.050354 | -0.05951 | 0.009155 | -0.13275 | -0.091553 | 0.21973 | 0.31586 | 0.20142 | 0.3067 | 0.19226 | 0.036621 | -0.041199 | 0.21057 | 122.2137 | 0.032043 | 122.1725 | 0.09613 | 122.1817 | -122.2504 | -122.3053 | 0.022888 | 122.2229 | -0.05951 | 0.66376
2518.0625 | 122.319 | -0.082397 | 122.1634 | -0.12794 | -0.044739 | 0.0040866 | 0.028491 | -0.0010595 | -0.010102 | -0.0025869 | -0.09549 | 0.0057379 | 0.065132 | 0.048337 | -0.016447 | 0.029117 | -0.0053661 | -0.14191 | -0.018311 | -0.045776 | 0.004578 | 0.086975 | -0.054932 | 0.091553 | 0.5722 | 122.0718 | -0.091553 | 122.2 | 0.15106 | 0.091553 | 0.28839 | 0.036621 | -122.1817 | -122.1588 | 0.16937 | 0.17395 | 0.027465 | 0.13733 | -0.009156 | -0.009156 | -0.091553 | 0.036621 | 0.23346 | 0.37079 | 0.17395 | 0.37994 | 0.18311 | 0.13275 | 0.050354 | 0.24261 | 122.2916 | 0.027465 | 122.1634 | 0.064086 | 122.1542 | -122.2092 | -122.2549 | 0.086975 | 122.2824 | -0.05951 | 0.6546
2519.8125 | 122.3145 | -0.086975 | 122.1863 | -0.12032 | -0.043885 | 0.0036594 | 0.024646 | 0.0021447 | -0.010957 | -0.0017325 | -0.064972 | 0.0074469 | 0.065345 | 0.048337 | -0.016874 | 0.027835 | -0.0049389 | -0.09613 | -0.054932 | -0.036621 | -0.041199 | 0.059509 | -0.068665 | 0.009155 | 0.42114 | 122.0764 | -0.086975 | 121.9849 | 0.073242 | 0.009155 | 0.064087 | 0.050354 | -122.2412 | -122.2275 | 0.14648 | 0.09613 | 0.01831 | 0.045776 | -0.032044 | 0 | -0.10986 | -0.20142 | 0.16022 | 0.15106 | 0.09613 | 0.15106 | 0.09613 | 0.09613 | -0.004578 | 0.16022 | 122.0718 | -0.018311 | 122.1634 | 0.032043 | 122.1634 | -122.2229 | -122.2733 | 0.045776 | 122.0718 | -0.009155 | 0.50812
2521.5 | 122.3282 | -0.10529 | 122.1863 | -0.11269 | -0.046021 | 0.0040866 | 0.024005 | 0.0049219 | -0.010102 | -0.0021597 | -0.083283 | 0.0061651 | 0.062995 | 0.045346 | -0.017301 | 0.025912 | -0.0047253 | -0.1236 | -0.018311 | -0.050354 | -0.07782 | 0.009155 | -0.07782 | 0 | 0.42572 | 122.0535 | -0.091553 | 121.9666 | 0.07782 | 0.022888 | 0.073242 | 0.054932 | -122.2046 | -122.2641 | 0.11444 | 0.10529 | 0.027466 | 0.050354 | -0.027466 | 0.013733 | -0.13275 | -0.21973 | 0.18311 | 0.17853 | 0.12817 | 0.16479 | 0.11444 | 0.059509 | -0.027466 | 0.16937 | 122.0581 | 0.032043 | 122.1451 | 0.086975 | 122.1588 | -122.2366 | -122.2778 | 0.027466 | 122.0718 | -0.01831 | 0.53101
2523.2656 | 122.3053 | -0.11902 | 122.1771 | -0.089798 | -0.044739 | 0.003873 | 0.024432 | 0.0040675 | -0.010743 | -0.00087794 | -0.064972 | 0.0061651 | 0.064063 | 0.051968 | -0.016874 | 0.028903 | -0.0045117 | -0.14648 | -0.013733 | -0.045776 | -0.09613 | -0.009155 | -0.10986 | -0.018311 | 0.39825 | 122.081 | -0.091553 | 121.9574 | 0.068665 | 0.004578 | 0.050354 | 0.073243 | -122.1909 | -122.2733 | 0.10986 | 0.10071 | 0.009156 | 0.027465 | -0.064087 | 0.027466 | -0.09613 | -0.21973 | 0.18768 | 0.16937 | 0.1236 | 0.14191 | 0.096131 | 0.036621 | -0.050354 | 0.16022 | 122.049 | 0.032043 | 122.1725 | 0.10529 | 122.2 | -122.2229 | -122.2687 | 0.022889 | 122.0764 | -0.027465 | 0.51727
2525.0312 | 122.3785 | -0.07782 | 122.1542 | -0.097427 | -0.046875 | 0.0030184 | 0.022723 | -0.0034095 | -0.0092478 | -0.0060049 | 0.0082703 | 0.0061651 | 0.064918 | 0.04321 | -0.013883 | 0.027194 | -0.0047253 | -0.10986 | -0.050354 | -0.009155 | -0.036621 | 0.073242 | -0.050354 | 0.027466 | 0.3891 | 122.0398 | -0.07782 | 122.0032 | 0.11444 | 0.086975 | 0.11444 | 0.068665 | -122.2046 | -122.1909 | 0.15106 | 0.10529 | 0.027466 | 0.036621 | -0.041199 | 0 | -0.11444 | -0.15106 | 0.19226 | 0.19226 | 0.16479 | 0.19226 | 0.16479 | 0.082397 | -0.027466 | 0.19226 | 122.081 | -0.041199 | 122.1176 | 0.027466 | 122.1176 | -122.1634 | -122.2321 | 0.041199 | 122.081 | -0.032043 | 0.46692
2526.7812 | 122.3831 | -0.082397 | 122.1542 | -0.15083 | -0.044525 | 0.0025912 | 0.023791 | -0.0019141 | -0.010743 | -0.0049367 | -0.0039367 | 0.0042425 | 0.063636 | 0.047482 | -0.016874 | 0.023776 | -0.0030163 | -0.1236 | -0.054932 | -0.013733 | -0.032043 | 0.073242 | -0.036621 | 0.054932 | 0.42114 | 122.0398 | -0.064087 | 122.0123 | 0.12817 | 0.11444 | 0.13275 | 0.068664 | -122.2092 | -122.1863 | 0.15564 | 0.13733 | 0.045776 | 0.068665 | -0.022888 | 0.01831 | -0.11444 | -0.14191 | 0.21057 | 0.21515 | 0.19684 | 0.19684 | 0.17853 | 0.086975 | -0.01831 | 0.19226 | 122.0764 | -0.041199 | 122.1039 | 0.027465 | 122.1222 | -122.168 | -122.2183 | 0.050354 | 122.0947 | -0.041199 | 0.50354
2528.4844 | 122.3145 | -0.10529 | 122.1863 | -0.044022 | -0.044953 | 0.0036594 | 0.027423 | 0.0038537 | -0.0083932 | -0.0038687 | -0.09549 | 0.0070197 | 0.06385 | 0.04086 | -0.017942 | 0.027621 | -0.0070751 | -0.11444 | -0.032043 | -0.036621 | -0.059509 | 0.013733 | -0.064087 | -0.004578 | 0.44861 | 122.081 | -0.09613 | 121.9528 | 0.082397 | 0.013733 | 0.064087 | 0.068665 | -122.2183 | -122.2458 | 0.11902 | 0.10071 | 0.041199 | 0.032043 | -0.027466 | 0.009156 | -0.10528 | -0.23346 | 0.18768 | 0.16937 | 0.11902 | 0.16022 | 0.10986 | 0.050354 | -0.022888 | 0.17853 | 122.049 | 0.004578 | 122.1771 | 0.073243 | 122.1863 | -122.2229 | -122.2824 | 0.045777 | 122.0581 | -0.009155 | 0.55389
2530.2344 | 122.3648 | -0.073242 | 122.1725 | -0.12032 | -0.045807 | 0.0030184 | 0.024432 | 0.0019311 | -0.0075388 | -0.0042959 | -0.025299 | 0.0059515 | 0.064063 | 0.043423 | -0.015165 | 0.026767 | -0.0072889 | -0.073242 | -0.07782 | 0.004578 | 0.018311 | 0.11902 | -0.022888 | 0.059509 | 0.3891 | 122.0398 | -0.064087 | 122.0123 | 0.11902 | 0.07782 | 0.1236 | 0.07782 | -122.2504 | -122.1542 | 0.19226 | 0.13275 | 0.050354 | 0.054931 | -0.027466 | 0.009155 | -0.13275 | -0.16022 | 0.19226 | 0.19684 | 0.15106 | 0.18768 | 0.14191 | 0.11444 | 0.013733 | 0.18311 | 122.0764 | -0.082398 | 122.1039 | -0.004578 | 122.113 | -122.168 | -122.2366 | 0.091553 | 122.0856 | 0 | 0.46234
2531.9844 | 122.3694 | -0.07782 | 122.1817 | -0.19661 | -0.045594 | 0.003232 | 0.024646 | -0.00020513 | -0.01053 | -0.0032277 | -0.031403 | 0.0057379 | 0.063636 | 0.053891 | -0.017301 | 0.026981 | -0.0030163 | -0.091553 | -0.054932 | -0.004578 | -0.013733 | 0.10986 | -0.041199 | 0.045776 | 0.39825 | 122.0627 | -0.073242 | 121.994 | 0.10986 | 0.073242 | 0.10986 | 0.073242 | -122.2366 | -122.1954 | 0.18768 | 0.1236 | 0.036621 | 0.050354 | -0.036621 | 0.004578 | -0.11902 | -0.18768 | 0.18768 | 0.18768 | 0.15106 | 0.18311 | 0.14648 | 0.11444 | -0.009155 | 0.18311 | 122.0673 | -0.050354 | 122.1359 | 0.022888 | 122.1405 | -122.1863 | -122.2549 | 0.064087 | 122.0718 | -0.013733 | 0.47607
2533.6719 | 122.2733 | -0.10529 | 122.2229 | -0.15846 | -0.045166 | 0.0047274 | 0.028277 | 0.0012903 | -0.010102 | -0.0049367 | -0.12601 | 0.0072333 | 0.064277 | 0.046841 | -0.017515 | 0.02869 | -0.0077161 | -0.15106 | -0.022888 | -0.054932 | -0.10986 | -0.041199 | -0.15106 | -0.041199 | 0.25635 | 122.0856 | -0.091553 | 121.9437 | 0.009155 | -0.045776 | 0.036621 | 0.050354 | -122.2458 | -122.3328 | 0.064087 | 0.064087 | -0.045776 | 0.013733 | -0.09613 | 0.013733 | -0.13733 | -0.27923 | 0.11444 | 0.14191 | 0.05951 | 0.12817 | 0.045777 | 0.013733 | -0.054931 | 0.10071 | 122.0352 | 0.032044 | 122.1771 | 0.082398 | 122.1909 | -122.2778 | -122.3145 | -0.004577 | 122.049 | -0.045776 | 0.36163
2535.4219 | 122.3877 | -0.054932 | 122.1634 | -0.15083 | -0.048157 | 0.0043002 | 0.025073 | -0.0031957 | -0.010743 | -0.0034415 | -0.022247 | 0.0053107 | 0.063636 | 0.041073 | -0.015806 | 0.028476 | -0.00023931 | -0.10986 | -0.054932 | 0.009155 | -0.036621 | 0.068665 | -0.045776 | 0.045776 | 0.41199 | 122.049 | -0.068665 | 122.0032 | 0.12817 | 0.09613 | 0.11902 | 0.064087 | -122.2183 | -122.2 | 0.1236 | 0.10071 | 0.009156 | 0.036621 | -0.054931 | -0.013733 | -0.11444 | -0.16022 | 0.18311 | 0.17395 | 0.15106 | 0.18768 | 0.16479 | 0.05951 | -0.045776 | 0.19684 | 122.0718 | -0.064087 | 122.1176 | 0 | 122.1039 | -122.1542 | -122.2321 | 0.018311 | 122.0581 | -0.054931 | 0.46692
2537.1875 | 122.3236 | -0.091553 | 122.2046 | -0.15083 | -0.045166 | 0.0030184 | 0.028918 | 0.0017175 | -0.0092478 | -0.0030141 | -0.1199 | 0.0050971 | 0.064704 | 0.051327 | -0.016874 | 0.027835 | -0.0025891 | -0.1236 | -0.032043 | -0.045776 | -0.07782 | -0.004578 | -0.14648 | -0.041199 | 0.28839 | 122.0718 | -0.091553 | 121.9757 | 0.032043 | 0 | 0.07782 | 0.045777 | -122.2366 | -122.2824 | 0.086975 | 0.050354 | -0.054931 | 0.004577 | -0.10071 | 0 | -0.13275 | -0.22888 | 0.1236 | 0.16937 | 0.091553 | 0.16937 | 0.091553 | 0.041198 | -0.032044 | 0.1236 | 122.0673 | 0.013733 | 122.1634 | 0.05951 | 122.1634 | -122.2504 | -122.2961 | 0.013733 | 122.0673 | -0.032043 | 0.37994
2538.9531 | 122.319 | -0.10986 | 122.1954 | -0.089798 | -0.047089 | 0.0030184 | 0.026355 | -0.0012731 | -0.009675 | -0.0036551 | -0.09549 | 0.0061651 | 0.06385 | 0.0509 | -0.018156 | 0.026767 | -0.0085705 | -0.10071 | -0.013733 | -0.045776 | -0.036621 | 0.059509 | -0.064087 | 0.013733 | 0.46234 | 122.081 | -0.082397 | 121.9894 | 0.082397 | 0.013733 | 0.082397 | 0.064087 | -122.2092 | -122.2321 | 0.16937 | 0.1236 | 0.045776 | 0.059509 | -0.018311 | 0.027466 | -0.11444 | -0.20599 | 0.19226 | 0.19226 | 0.1236 | 0.16479 | 0.09613 | 0.10528 | 0.009155 | 0.16479 | 122.0718 | 0.032043 | 122.1634 | 0.09613 | 122.1909 | -122.2412 | -122.2778 | 0.073242 | 122.0993 | 0.009155 | 0.5722
2540.7031 | 122.2961 | -0.10071 | 122.2 | -0.12794 | -0.042603 | 0.0043002 | 0.027423 | -0.00041873 | -0.01053 | -0.0032277 | -0.1138 | 0.0070197 | 0.064491 | 0.04855 | -0.015806 | 0.026553 | -0.0053661 | -0.086975 | -0.036621 | -0.022888 | -0.041199 | 0.036621 | -0.086975 | 0.004578 | 0.41199 | 122.0764 | -0.082397 | 121.9711 | 0.054932 | -0.004578 | 0.059509 | 0.07782 | -122.2366 | -122.2412 | 0.13733 | 0.10529 | 0.013733 | 0.027466 | -0.064087 | 0.018311 | -0.1236 | -0.22888 | 0.15564 | 0.16022 | 0.09613 | 0.14191 | 0.077819 | 0.059509 | -0.018311 | 0.13733 | 122.0535 | -0.013733 | 122.1588 | 0.064087 | 122.1771 | -122.2229 | -122.2824 | 0.059509 | 122.0718 | 0.013733 | 0.5127
2542.3906 | 122.3236 | -0.073242 | 122.1817 | -0.15083 | -0.047089 | 0.003232 | 0.026996 | -0.00063233 | -0.0092478 | -0.0025869 | -0.083283 | 0.0070197 | 0.065132 | 0.048123 | -0.016447 | 0.025485 | -0.0049389 | -0.13733 | -0.027466 | -0.041199 | -0.09613 | -0.009155 | -0.1236 | -0.036621 | 0.28381 | 122.0993 | -0.091553 | 121.9803 | 0.045776 | 0 | 0.073242 | 0.032043 | -122.2092 | -122.2778 | 0.064087 | 0.036621 | -0.050354 | 0.004578 | -0.082397 | -0.018311 | -0.082398 | -0.20142 | 0.11902 | 0.14648 | 0.073242 | 0.16479 | 0.091553 | 0.032044 | -0.054931 | 0.13733 | 122.0718 | 0.013733 | 122.1909 | 0.045776 | 122.1725 | -122.2229 | -122.2733 | -0.022888 | 122.0535 | -0.064087 | 0.35706
2544.1406 | 122.3602 | -0.068665 | 122.1634 | -0.19661 | -0.043457 | 0.0028048 | 0.021869 | -0.0012731 | -0.009675 | -0.0064321 | -0.022247 | 0.0061651 | 0.063636 | 0.047055 | -0.016233 | 0.028476 | -0.0045117 | -0.086975 | -0.050354 | -0.013733 | 0 | 0.11902 | -0.041199 | 0.054932 | 0.39825 | 122.0444 | -0.07782 | 122.0078 | 0.10986 | 0.086975 | 0.10071 | 0.054932 | -122.2137 | -122.1634 | 0.18768 | 0.1236 | 0.027466 | 0.068665 | -0.027466 | -0.009155 | -0.11902 | -0.15564 | 0.17853 | 0.16937 | 0.15564 | 0.17853 | 0.16479 | 0.13275 | 0.013733 | 0.18768 | 122.0856 | -0.036621 | 122.1222 | 0.018311 | 122.113 | -122.1771 | -122.2412 | 0.068665 | 122.0764 | -0.01831 | 0.46692
2545.8906 | 122.2687 | -0.091553 | 122.2137 | -0.082169 | -0.042176 | 0.0040866 | 0.028705 | -0.0012731 | -0.0081796 | -0.0013051 | -0.12296 | 0.0046697 | 0.065559 | 0.059445 | -0.01602 | 0.02869 | -0.0025891 | -0.10071 | -0.032043 | -0.036621 | -0.10071 | -0.004578 | -0.11902 | -0.032043 | 0.32959 | 122.0764 | -0.082397 | 121.9299 | 0.013733 | -0.050354 | 0.041199 | 0.054932 | -122.2458 | -122.3145 | 0.086975 | 0.05951 | -0.027466 | 0.004578 | -0.082398 | 0.009156 | -0.13733 | -0.28381 | 0.10529 | 0.13275 | 0.041199 | 0.1236 | 0.032043 | 0.032043 | -0.064087 | 0.09613 | 122.0123 | 0.004578 | 122.1588 | 0.05951 | 122.168 | -122.2504 | -122.2961 | -0.009155 | 122.0215 | -0.009155 | 0.42114
2547.6406 | 122.3145 | -0.10529 | 122.168 | -0.1432 | -0.043244 | 0.0045138 | 0.027423 | -0.0027685 | -0.0071116 | -0.0032277 | -0.098541 | 0.0068059 | 0.063209 | 0.045773 | -0.015592 | 0.02933 | -0.0042981 | -0.13275 | -0.022888 | -0.036621 | -0.091553 | -0.009155 | -0.12817 | -0.036621 | 0.28381 | 122.1039 | -0.091553 | 121.962 | 0.036621 | -0.013733 | 0.045776 | 0.068665 | -122.1909 | -122.2595 | 0.096131 | 0.068665 | -0.022888 | 0 | -0.091553 | 0.013733 | -0.064087 | -0.20599 | 0.14191 | 0.15106 | 0.091553 | 0.13733 | 0.07782 | 0.027466 | -0.054932 | 0.12817 | 122.0535 | 0.013733 | 122.1954 | 0.082398 | 122.2092 | -122.2046 | -122.2595 | 0.013733 | 122.0673 | -0.027465 | 0.3891
2549.3281 | 122.3602 | -0.082397 | 122.1405 | -0.18898 | -0.045166 | 0.0028048 | 0.025714 | -0.0038367 | -0.01117 | -0.0017325 | 0.0052185 | 0.0059515 | 0.062995 | 0.045346 | -0.014311 | 0.026553 | -0.0057935 | -0.09613 | -0.045776 | 0 | -0.018311 | 0.09613 | -0.054932 | 0.036621 | 0.37079 | 122.0398 | -0.07782 | 121.994 | 0.091553 | 0.064087 | 0.10986 | 0.082397 | -122.1863 | -122.1588 | 0.17853 | 0.11902 | 0.027465 | 0.036621 | -0.054932 | 0.004577 | -0.10071 | -0.14648 | 0.17395 | 0.19226 | 0.14648 | 0.18768 | 0.14191 | 0.09613 | -0.018311 | 0.16937 | 122.0718 | -0.045776 | 122.1176 | 0.036621 | 122.1222 | -122.1405 | -122.2183 | 0.064086 | 122.0764 | -0.013733 | 0.45319
2551.0938 | 122.3557 | -0.086975 | 122.168 | -0.17372 | -0.046448 | 0.0043002 | 0.024218 | -0.0012731 | -0.0094614 | -0.0040823 | -0.0069885 | 0.0042425 | 0.064704 | 0.051327 | -0.018156 | 0.025272 | -0.0045117 | -0.10986 | -0.041199 | -0.009155 | -0.032043 | 0.059509 | -0.054932 | 0.036621 | 0.3891 | 122.0352 | -0.086975 | 122.0032 | 0.09613 | 0.059509 | 0.09613 | 0.07782 | -122.2092 | -122.2 | 0.14648 | 0.1236 | 0.032043 | 0.045776 | -0.045777 | 0 | -0.13275 | -0.16479 | 0.1831 | 0.1831 | 0.14648 | 0.1831 | 0.14648 | 0.068664 | -0.022888 | 0.1831 | 122.0901 | -0.032044 | 122.1222 | 0.045776 | 122.1222 | -122.1771 | -122.2549 | 0.054932 | 122.0901 | -0.022888 | 0.47607
2552.7812 | 122.2961 | -0.10071 | 122.2137 | -0.044022 | -0.044525 | 0.001523 | 0.028064 | -0.0061865 | -0.013307 | -0.00066434 | -0.046661 | 0.0044561 | 0.064063 | 0.049191 | -0.017515 | 0.027194 | -0.0070751 | -0.14648 | -0.004578 | -0.045776 | -0.086975 | -0.022888 | -0.10071 | -0.009155 | 0.42572 | 122.0947 | -0.10529 | 121.9437 | 0.036621 | -0.018311 | 0.041199 | 0.054932 | -122.2183 | -122.3007 | 0.07782 | 0.091553 | 0 | 0.036621 | -0.054932 | -0.004578 | -0.11902 | -0.27008 | 0.13733 | 0.14191 | 0.082397 | 0.14649 | 0.086975 | 0.022888 | -0.041199 | 0.14191 | 122.049 | 0.041198 | 122.2 | 0.09613 | 122.1954 | -122.2595 | -122.319 | 0.013733 | 122.0444 | -0.045776 | 0.52643
2554.5312 | 122.287 | -0.10071 | 122.1909 | -0.097427 | -0.043671 | 0.0036594 | 0.024646 | -0.0036231 | -0.0094614 | -0.0023733 | -0.019196 | 0.0057379 | 0.0662 | 0.047909 | -0.01602 | 0.026981 | -0.0049389 | -0.073242 | -0.054932 | -0.009155 | -0.032043 | 0.082397 | -0.032043 | 0.036621 | 0.49439 | 122.0718 | -0.091553 | 121.9482 | 0.082397 | 0.018311 | 0.041199 | 0.091553 | -122.2458 | -122.2229 | 0.18311 | 0.13733 | 0.068665 | 0.045776 | -0.022888 | 0.009155 | -0.11902 | -0.24262 | 0.18311 | 0.14191 | 0.11902 | 0.13275 | 0.10986 | 0.091552 | -0.022888 | 0.17395 | 122.0398 | -0.045777 | 122.1634 | 0.045776 | 122.1725 | -122.2 | -122.2824 | 0.068665 | 122.0489 | 0.027466 | 0.59509
2556.2812 | 122.4289 | -0.059509 | 122.1542 | -0.13557 | -0.046234 | 0.001523 | 0.02315 | 0.00043587 | -0.0098886 | -0.0032277 | -0.016144 | 0.0059515 | 0.064063 | 0.044491 | -0.015806 | 0.024844 | -0.0079297 | -0.068665 | -0.054932 | 0 | 0.054932 | 0.18768 | 0.045776 | 0.10529 | 0.5722 | 122.0535 | -0.054932 | 122.0581 | 0.18768 | 0.15106 | 0.15106 | 0.059509 | -122.2092 | -122.0993 | 0.24719 | 0.16479 | 0.10528 | 0.10529 | 0.045776 | 0.004577 | -0.10071 | -0.096131 | 0.24719 | 0.21057 | 0.21057 | 0.20599 | 0.20599 | 0.18768 | 0.054932 | 0.24261 | 122.113 | -0.054932 | 122.1085 | 0.004577 | 122.113 | -122.1542 | -122.2092 | 0.11444 | 122.1176 | -0.009156 | 0.63171
2558.0312 | 122.3099 | -0.10071 | 122.1817 | -0.082169 | -0.043671 | 0.0030184 | 0.025714 | -0.0040503 | -0.0092478 | -0.00087794 | -0.058869 | 0.0063787 | 0.064918 | 0.039151 | -0.01666 | 0.027194 | -0.0051525 | -0.13733 | 0 | -0.050354 | -0.07782 | -0.013733 | -0.091553 | -0.032043 | 0.43488 | 122.0947 | -0.10071 | 121.9528 | 0.036621 | -0.009155 | 0.022888 | 0.050354 | -122.1817 | -122.2595 | 0.086975 | 0.068665 | 0.009155 | 0.018311 | -0.041199 | 0 | -0.086975 | -0.22888 | 0.13733 | 0.1236 | 0.091553 | 0.1236 | 0.091553 | 0.036621 | -0.027466 | 0.13733 | 122.0535 | 0.050354 | 122.1954 | 0.10071 | 122.1954 | -122.2321 | -122.2824 | 0.022888 | 122.0535 | -0.036621 | 0.53558
2559.7188 | 122.3419 | -0.07782 | 122.1725 | -0.12794 | -0.044098 | 0.0030184 | 0.026141 | -0.0021277 | -0.0094614 | -0.0032277 | -0.09549 | 0.0074469 | 0.0615 | 0.050046 | -0.01666 | 0.028262 | -0.0062207 | -0.14648 | -0.009155 | -0.022888 | -0.09613 | 0 | -0.13275 | -0.036621 | 0.28839 | 122.0947 | -0.09613 | 121.9757 | 0.064087 | -0.004578 | 0.068665 | 0.054932 | -122.1817 | -122.2687 | 0.07782 | 0.041199 | -0.054931 | -0.013733 | -0.10986 | -0.01831 | -0.077819 | -0.19684 | 0.14191 | 0.14649 | 0.073242 | 0.16479 | 0.091552 | 0.022888 | -0.073242 | 0.16022 | 122.0718 | 0.013733 | 122.1909 | 0.068665 | 122.1725 | -122.1954 | -122.2687 | -0.01831 | 122.0535 | -0.068664 | 0.36621
2561.4688 | 122.2961 | -0.09613 | 122.1954 | -0.15083 | -0.044312 | 0.0019504 | 0.022082 | 0.00043587 | -0.0090342 | -0.0019461 | -0.022247 | 0.0036017 | 0.065132 | 0.050046 | -0.015379 | 0.026126 | -0.0055799 | -0.082397 | -0.045776 | -0.013733 | -0.018311 | 0.082397 | -0.027466 | 0.059509 | 0.49896 | 122.0627 | -0.082397 | 121.9345 | 0.064087 | 0.022888 | 0.059509 | 0.082397 | -122.2412 | -122.2137 | 0.17853 | 0.15564 | 0.068664 | 0.073242 | -0.013733 | 0.013733 | -0.13275 | -0.26093 | 0.16022 | 0.15564 | 0.11902 | 0.14191 | 0.10528 | 0.09613 | -0.004578 | 0.14648 | 122.0169 | -0.032043 | 122.1451 | 0.050354 | 122.1588 | -122.2092 | -122.2778 | 0.077819 | 122.0306 | 0.013733 | 0.59509
2563.2344 | 122.3419 | -0.082397 | 122.1725 | -0.12032 | -0.043671 | 0.0025912 | 0.029132 | 0.0012903 | -0.0071116 | -0.0042959 | -0.1077 | 0.0072333 | 0.06385 | 0.051755 | -0.018156 | 0.027408 | -0.0038709 | -0.11444 | -0.013733 | -0.054932 | -0.068665 | 0 | -0.10986 | -0.009155 | 0.31128 | 122.0673 | -0.07782 | 122.0032 | 0.07782 | 0.041199 | 0.091553 | 0.027465 | -122.1863 | -122.2412 | 0.082397 | 0.073242 | -0.027466 | 0.045777 | -0.054931 | 0.004577 | -0.10528 | -0.16937 | 0.16022 | 0.17395 | 0.1236 | 0.16937 | 0.11902 | 0.054932 | -0.013733 | 0.15564 | 122.081 | 0.041199 | 122.1451 | 0.068664 | 122.1497 | -122.2275 | -122.2504 | 0.013732 | 122.0856 | -0.032044 | 0.39368
2564.9844 | 122.2687 | -0.09613 | 122.2229 | -0.19661 | -0.043457 | 0.0053684 | 0.028705 | 0.0025721 | -0.0088206 | -0.0030141 | -0.1138 | 0.0046697 | 0.064491 | 0.051114 | -0.016233 | 0.029971 | -0.0049389 | -0.13275 | -0.018311 | -0.032043 | -0.086975 | -0.022888 | -0.15106 | -0.064087 | 0.2655 | 122.0901 | -0.09613 | 121.9299 | -0.013733 | -0.064087 | 0.018311 | 0.064087 | -122.2412 | -122.3099 | 0.073242 | 0.032043 | -0.054932 | -0.032044 | -0.11902 | 0 | -0.13275 | -0.29297 | 0.082397 | 0.11444 | 0.032043 | 0.11444 | 0.032043 | 0.009155 | -0.054932 | 0.082397 | 122.0261 | 0.013732 | 122.1863 | 0.077819 | 122.1863 | -122.2549 | -122.319 | 0.009155 | 122.0261 | -0.036621 | 0.36163
2566.6719 | 122.319 | -0.082397 | 122.2137 | -0.16609 | -0.044312 | 0.0036594 | 0.024859 | 0.0017175 | -0.0098886 | -0.0042959 | -0.080231 | 0.0070197 | 0.064277 | 0.051114 | -0.017088 | 0.027194 | -0.0015209 | -0.13275 | -0.032043 | -0.032043 | -0.10986 | -0.013733 | -0.13733 | -0.032043 | 0.28381 | 122.0993 | -0.10529 | 121.9849 | 0.050354 | -0.018311 | 0.059509 | 0.050354 | -122.2458 | -122.3236 | 0.068664 | 0.050354 | -0.054932 | 0 | -0.10529 | -0.022889 | -0.11444 | -0.22888 | 0.13275 | 0.14191 | 0.064086 | 0.16479 | 0.086975 | 0.01831 | -0.07782 | 0.15564 | 122.0901 | 0 | 122.2046 | 0.050354 | 122.1817 | -122.2458 | -122.319 | -0.027466 | 122.0673 | -0.050354 | 0.36621
2568.4219 | 122.4289 | -0.073242 | 122.1588 | -0.10506 | -0.04538 | 0.001523 | 0.022509 | -0.00084593 | -0.0092478 | -0.0021597 | 0.0082703 | 0.0033881 | 0.06385 | 0.049832 | -0.014738 | 0.024417 | -0.00023931 | -0.091553 | -0.054932 | -0.022888 | 0.004578 | 0.10529 | 0.022888 | 0.086975 | 0.52185 | 122.0352 | -0.073242 | 122.0444 | 0.16937 | 0.14191 | 0.14191 | 0.050354 | -122.2137 | -122.1542 | 0.17853 | 0.16022 | 0.09613 | 0.10986 | 0.045776 | 0 | -0.1236 | -0.11444 | 0.24261 | 0.21515 | 0.21515 | 0.21515 | 0.21515 | 0.12817 | 0.027466 | 0.24261 | 122.1176 | -0.032044 | 122.1085 | 0.01831 | 122.1085 | -122.1817 | -122.2321 | 0.07782 | 122.1176 | -0.018311 | 0.59509
2570.1719 | 122.3923 | -0.07782 | 122.1817 | -0.15846 | -0.046662 | 0.0030184 | 0.024218 | -0.0021277 | -0.0081796 | -0.0032277 | 0.0052185 | 0.0057379 | 0.062995 | 0.048337 | -0.017088 | 0.027408 | -0.0030163 | -0.11444 | -0.045776 | -0.032043 | -0.032043 | 0.073242 | -0.032043 | 0.050354 | 0.42572 | 122.0673 | -0.050354 | 122.0078 | 0.1236 | 0.086975 | 0.11902 | 0.045777 | -122.2275 | -122.2137 | 0.15106 | 0.12817 | 0.045777 | 0.082397 | 0 | 0.027466 | -0.11444 | -0.17395 | 0.20142 | 0.19684 | 0.16479 | 0.16937 | 0.13733 | 0.10529 | 0 | 0.17395 | 122.0581 | -0.013733 | 122.1176 | 0.032044 | 122.1451 | -122.2137 | -122.2321 | 0.045777 | 122.0856 | -0.036621 | 0.50354
2571.8594 | 122.3831 | -0.064087 | 122.1909 | -0.089798 | -0.045166 | 0.00088223 | 0.025287 | -0.0031957 | -0.011598 | -0.0040823 | -0.028351 | 0.0050971 | 0.062568 | 0.044491 | -0.016874 | 0.027408 | -0.0053661 | -0.054932 | -0.073242 | 0.004578 | 0.041199 | 0.13733 | 0.027466 | 0.082397 | 0.55847 | 122.0718 | -0.064087 | 122.0261 | 0.15564 | 0.11444 | 0.1236 | 0.068665 | -122.2641 | -122.1497 | 0.20142 | 0.14648 | 0.091553 | 0.077819 | 0.022888 | 0 | -0.11902 | -0.16479 | 0.21973 | 0.18768 | 0.17853 | 0.18768 | 0.17853 | 0.13275 | 0.036621 | 0.21973 | 122.0901 | -0.07782 | 122.1359 | -0.009155 | 122.1359 | -122.1863 | -122.2549 | 0.10529 | 122.0901 | 0.009155 | 0.62256
2573.625 | 122.2687 | -0.10529 | 122.2046 | -0.16609 | -0.042603 | 0.003873 | 0.026141 | 0.00086307 | -0.0090342 | -0.0036551 | -0.13211 | 0.0050971 | 0.064491 | 0.051968 | -0.01666 | 0.028049 | -0.0068615 | -0.1236 | -0.022888 | -0.054932 | -0.10529 | -0.050354 | -0.15106 | -0.064087 | 0.25177 | 122.0993 | -0.10986 | 121.962 | 0 | -0.050354 | 0.036621 | 0.050354 | -122.2275 | -122.3099 | 0.054932 | 0.041199 | -0.045776 | -0.009155 | -0.09613 | -0.004577 | -0.10529 | -0.24262 | 0.10529 | 0.14191 | 0.054932 | 0.14648 | 0.059509 | 0.004578 | -0.050354 | 0.10986 | 122.0718 | 0.032044 | 122.2092 | 0.082398 | 122.2046 | -122.2595 | -122.3145 | 0 | 122.0673 | -0.01831 | 0.35706
2575.3906 | 122.2641 | -0.10071 | 122.1909 | -0.17372 | -0.04303 | 0.0045138 | 0.027636 | -0.0012731 | -0.0092478 | -0.00045074 | -0.1138 | 0.0057379 | 0.062995 | 0.043423 | -0.014951 | 0.027835 | -0.0057935 | -0.086975 | -0.013733 | -0.041199 | -0.064087 | 0.004578 | -0.12817 | -0.041199 | 0.32501 | 122.113 | -0.10071 | 121.9482 | 0.009155 | -0.045776 | 0.027466 | 0.059509 | -122.2046 | -122.2549 | 0.10529 | 0.059509 | -0.027466 | 0 | -0.086975 | 0 | -0.07782 | -0.24262 | 0.10986 | 0.12817 | 0.054932 | 0.12817 | 0.054932 | 0.045777 | -0.022888 | 0.10986 | 122.0489 | 0.027466 | 122.2137 | 0.086975 | 122.2137 | -122.2321 | -122.2916 | 0.036621 | 122.0489 | 0.013733 | 0.42572
2577.1406 | 122.287 | -0.09613 | 122.1909 | -0.1432 | -0.045594 | 0.002164 | 0.026141 | 0.0034265 | -0.010102 | -0.0025869 | -0.025299 | 0.0063787 | 0.065559 | 0.053464 | -0.015592 | 0.029117 | -0.0062207 | -0.13275 | -0.018311 | -0.036621 | -0.082397 | 0.022888 | -0.091553 | 0 | 0.43945 | 122.1176 | -0.10529 | 121.9345 | 0.041199 | -0.004578 | 0.018311 | 0.059509 | -122.2092 | -122.2733 | 0.11902 | 0.09613 | 0.004577 | 0.036621 | -0.054932 | -0.009156 | -0.073242 | -0.25635 | 0.13733 | 0.11444 | 0.091552 | 0.1236 | 0.10071 | 0.059509 | -0.045776 | 0.14649 | 122.0398 | 0.01831 | 122.2229 | 0.077819 | 122.2137 | -122.2275 | -122.2961 | 0.013733 | 122.0306 | -0.036621 | 0.53558
2578.8594 | 122.4197 | -0.068665 | 122.1954 | -0.12032 | -0.045166 | 0.0023776 | 0.022082 | -0.00063233 | -0.0090342 | -0.0019461 | 0.0021667 | 0.0059515 | 0.062568 | 0.044919 | -0.017942 | 0.025699 | -0.0055799 | -0.059509 | -0.073242 | 0.013733 | 0.022888 | 0.16022 | 0.032043 | 0.086975 | 0.57678 | 122.0673 | -0.059509 | 122.0398 | 0.1831 | 0.14191 | 0.14648 | 0.082398 | -122.2687 | -122.1725 | 0.22888 | 0.15564 | 0.10071 | 0.073242 | 0.01831 | 0.009156 | -0.12817 | -0.15564 | 0.25177 | 0.21515 | 0.21057 | 0.20599 | 0.20142 | 0.14648 | 0.009155 | 0.24261 | 122.0993 | -0.086975 | 122.1268 | -0.004577 | 122.1359 | -122.1817 | -122.2549 | 0.091553 | 122.1085 | 0.009156 | 0.64545
2580.625 | 122.2916 | -0.10529 | 122.2275 | -0.1432 | -0.045594 | 0.0023776 | 0.027423 | 0.0029993 | -0.0098886 | -0.0040823 | -0.1138 | 0.0072333 | 0.064491 | 0.046841 | -0.01602 | 0.028262 | -0.0062207 | -0.10071 | -0.013733 | -0.045776 | -0.10071 | -0.036621 | -0.14648 | -0.059509 | 0.26093 | 122.0856 | -0.10986 | 121.9482 | 0.013733 | -0.041199 | 0.022888 | 0.05951 | -122.2412 | -122.3282 | 0.068665 | 0.045777 | -0.041198 | -0.013733 | -0.10071 | -0.004577 | -0.14191 | -0.27924 | 0.11902 | 0.12817 | 0.064087 | 0.13275 | 0.068664 | 0.009155 | -0.054932 | 0.1236 | 122.0581 | 0.032043 | 122.1954 | 0.091553 | 122.1909 | -122.2733 | -122.3373 | 0.004578 | 122.0535 | 0.004578 | 0.36621
2582.3125 | 122.287 | -0.091553 | 122.2137 | -0.12032 | -0.041321 | 0.0060092 | 0.027209 | -0.0027685 | -0.011811 | -0.0040823 | -0.11075 | 0.0053107 | 0.068122 | 0.048123 | -0.016447 | 0.026767 | -0.0042981 | -0.13275 | -0.018311 | -0.041199 | -0.09613 | -0.041199 | -0.14191 | -0.045776 | 0.27466 | 122.0856 | -0.11444 | 121.9528 | 0.004578 | -0.050354 | 0.036621 | 0.050354 | -122.2321 | -122.3099 | 0.050354 | 0.045777 | -0.050354 | -0.004577 | -0.10071 | -0.022888 | -0.12817 | -0.26093 | 0.096131 | 0.12817 | 0.041199 | 0.15106 | 0.064087 | 0 | -0.054931 | 0.11902 | 122.0673 | 0.022888 | 122.2 | 0.073242 | 122.1771 | -122.2549 | -122.3282 | -0.004577 | 122.0444 | -0.041198 | 0.36621
2584.0781 | 122.2961 | -0.11444 | 122.2229 | -0.05928 | -0.046662 | 0.0034456 | 0.026782 | 0.0051355 | -0.0090342 | -0.0053641 | -0.058869 | 0.0074469 | 0.062568 | 0.049618 | -0.016447 | 0.029544 | -0.0042981 | -0.13733 | -0.022888 | -0.036621 | -0.091553 | -0.018311 | -0.09613 | -0.022888 | 0.42572 | 122.1039 | -0.09613 | 121.9482 | 0.045776 | -0.022888 | 0.036621 | 0.07782 | -122.2458 | -122.3145 | 0.09613 | 0.091553 | 0.018311 | 0.013733 | -0.059509 | 0.018311 | -0.11902 | -0.27466 | 0.16022 | 0.15106 | 0.091553 | 0.13275 | 0.073242 | 0.01831 | -0.054932 | 0.14191 | 122.0444 | 0.013733 | 122.2 | 0.091553 | 122.2183 | -122.2595 | -122.319 | 0.022888 | 122.0627 | -0.022888 | 0.54016
2585.8281 | 122.3282 | -0.09613 | 122.1863 | -0.097427 | -0.045594 | 0.003873 | 0.0255 | -0.0038367 | -0.0077524 | -0.0051505 | -0.077179 | 0.0059515 | 0.065559 | 0.051755 | -0.015379 | 0.028903 | -0.0053661 | -0.13275 | -0.009155 | -0.059509 | -0.09613 | -0.004578 | -0.1236 | -0.036621 | 0.27924 | 122.1085 | -0.10071 | 121.994 | 0.032043 | -0.009155 | 0.068665 | 0.036621 | -122.1954 | -122.2824 | 0.091552 | 0.059509 | -0.027466 | 0.022888 | -0.064087 | -0.004578 | -0.07782 | -0.19226 | 0.12817 | 0.16479 | 0.086975 | 0.16937 | 0.091553 | 0.054931 | -0.036621 | 0.13275 | 122.0947 | 0.050354 | 122.2092 | 0.086975 | 122.2046 | -122.2458 | -122.287 | 0 | 122.0901 | -0.036621 | 0.37537
2587.5156 | 122.3648 | -0.086975 | 122.1771 | -0.15846 | -0.04303 | 0.0025912 | 0.027636 | 0.00064947 | -0.0083932 | -0.0042959 | -0.089386 | 0.0063787 | 0.063423 | 0.049191 | -0.016874 | 0.029117 | -0.0021619 | -0.12817 | -0.022888 | -0.045776 | -0.068665 | 0.022888 | -0.11902 | -0.013733 | 0.3067 | 122.0718 | -0.086975 | 122.0078 | 0.09613 | 0.032043 | 0.10529 | 0.041199 | -122.2 | -122.2458 | 0.10986 | 0.073242 | -0.032044 | 0.032043 | -0.073243 | 0 | -0.10529 | -0.16937 | 0.1831 | 0.19226 | 0.11902 | 0.19226 | 0.11902 | 0.068664 | -0.022889 | 0.1831 | 122.0947 | 0.022888 | 122.1588 | 0.064087 | 122.1588 | -122.2229 | -122.2641 | 0.01831 | 122.0947 | -0.041199 | 0.39368
2589.2656 | 122.3877 | -0.068665 | 122.1771 | -0.2195 | -0.046662 | 0.0017368 | 0.022296 | -0.0038367 | -0.0092478 | -0.0030141 | 0.0021667 | 0.0050971 | 0.062995 | 0.044705 | -0.01602 | 0.024417 | -0.0019483 | -0.10071 | -0.050354 | -0.009155 | -0.027466 | 0.064087 | -0.045776 | 0.054932 | 0.41657 | 122.081 | -0.086975 | 122.0169 | 0.12817 | 0.086975 | 0.10529 | 0.05951 | -122.2275 | -122.2046 | 0.13275 | 0.1236 | 0.022889 | 0.064087 | -0.036621 | -0.01831 | -0.09613 | -0.16022 | 0.19684 | 0.17395 | 0.15564 | 0.19226 | 0.17395 | 0.073242 | -0.018311 | 0.21515 | 122.1039 | -0.041199 | 122.168 | 0.018311 | 122.1497 | -122.1863 | -122.2641 | 0.041199 | 122.0856 | -0.032043 | 0.48523
2591.0156 | 122.4289 | -0.054932 | 122.1634 | -0.1432 | -0.044525 | 0.0010958 | 0.023578 | -0.0040503 | -0.0092478 | -0.0038687 | 0.0021667 | 0.0059515 | 0.064704 | 0.044919 | -0.015592 | 0.02634 | -0.0066479 | -0.09613 | -0.059509 | -0.032043 | -0.009155 | 0.11444 | 0 | 0.086975 | 0.50354 | 122.049 | -0.086975 | 122.0764 | 0.1831 | 0.14648 | 0.15564 | 0.022889 | -122.2229 | -122.1725 | 0.16937 | 0.14191 | 0.054932 | 0.11902 | 0.032043 | -0.032043 | -0.11444 | -0.086975 | 0.23804 | 0.21057 | 0.20142 | 0.24261 | 0.23346 | 0.14648 | 0.022888 | 0.27008 | 122.1634 | -0.027466 | 122.1359 | -0.004577 | 122.1039 | -122.1954 | -122.2504 | 0.045777 | 122.1313 | -0.041198 | 0.55847
2592.7031 | 122.3465 | -0.086975 | 122.1817 | -0.097427 | -0.045594 | 0.0040866 | 0.02315 | -0.0012731 | -0.0098886 | -0.0025869 | -0.016144 | 0.0061651 | 0.0615 | 0.051114 | -0.017942 | 0.025272 | -0.0060071 | -0.059509 | -0.068665 | -0.013733 | 0.027466 | 0.1236 | 0.009155 | 0.07782 | 0.55389 | 122.0901 | -0.064087 | 121.994 | 0.10529 | 0.059509 | 0.086975 | 0.073242 | -122.2504 | -122.1542 | 0.21057 | 0.16479 | 0.09613 | 0.091553 | 0.022888 | 0.022888 | -0.091553 | -0.18768 | 0.19226 | 0.17395 | 0.14648 | 0.15106 | 0.1236 | 0.13733 | 0.041199 | 0.16937 | 122.0581 | -0.054932 | 122.1542 | 0.01831 | 122.1771 | -122.1954 | -122.2458 | 0.11444 | 122.081 | 0.027466 | 0.64087
2594.4688 | 122.3831 | -0.073242 | 122.1771 | -0.17372 | -0.044953 | 0.0023776 | 0.024859 | 0.0038537 | -0.0092478 | -0.00066434 | -0.04361 | 0.0031745 | 0.066413 | 0.051968 | -0.016233 | 0.027194 | -0.0038709 | -0.07782 | -0.054932 | 0.009155 | 0.027466 | 0.13275 | -0.018311 | 0.059509 | 0.41657 | 122.0764 | -0.054932 | 122.0352 | 0.11902 | 0.082397 | 0.13275 | 0.082397 | -122.2321 | -122.1497 | 0.20599 | 0.13275 | 0.054931 | 0.050354 | -0.027466 | 0.01831 | -0.10071 | -0.14191 | 0.19226 | 0.20599 | 0.15564 | 0.18768 | 0.13733 | 0.1236 | 0.018311 | 0.17395 | 122.0901 | -0.064087 | 122.1313 | 0.01831 | 122.1497 | -122.168 | -122.2321 | 0.10071 | 122.1085 | -0.004578 | 0.48981
2596.1562 | 122.4014 | -0.032043 | 122.1863 | -0.18135 | -0.042389 | 0.003873 | 0.024432 | 0.0019311 | -0.008607 | -0.0040823 | -0.071076 | 0.0074469 | 0.062568 | 0.051327 | -0.01602 | 0.025272 | -0.0045117 | -0.059509 | -0.07782 | 0 | 0.036621 | 0.14648 | -0.013733 | 0.07782 | 0.4303 | 122.0673 | -0.059509 | 122.0673 | 0.14648 | 0.09613 | 0.16022 | 0.032043 | -122.2641 | -122.1497 | 0.17853 | 0.10986 | 0.01831 | 0.07782 | -0.013733 | -0.027466 | -0.11902 | -0.11902 | 0.17853 | 0.19226 | 0.12817 | 0.21973 | 0.15564 | 0.14648 | 0.036621 | 0.20599 | 122.1268 | -0.07782 | 122.1268 | -0.045777 | 122.0993 | -122.1863 | -122.2458 | 0.068664 | 122.0993 | -0.027466 | 0.46234
2597.9062 | 122.2687 | -0.07782 | 122.2412 | -0.15083 | -0.044739 | 0.002164 | 0.027636 | -0.0012731 | -0.0090342 | -0.0057913 | -0.13821 | 0.0065923 | 0.064704 | 0.054104 | -0.016874 | 0.02634 | -0.0036573 | -0.11444 | -0.032043 | -0.036621 | -0.091553 | -0.022888 | -0.14191 | -0.045776 | 0.28381 | 122.1268 | -0.086975 | 121.9299 | 0.022888 | -0.050354 | 0.032043 | 0.041199 | -122.2733 | -122.3328 | 0.054932 | 0.032044 | -0.064087 | -0.009155 | -0.10529 | -0.009155 | -0.11444 | -0.31128 | 0.10071 | 0.10986 | 0.027466 | 0.11902 | 0.036621 | 0.013733 | -0.054932 | 0.10986 | 122.0169 | 0.004578 | 122.2137 | 0.045777 | 122.2046 | -122.2778 | -122.3282 | -0.013733 | 122.0078 | -0.036621 | 0.36163
2599.6562 | 122.4106 | -0.054932 | 122.168 | -0.16609 | -0.040894 | 0.0047274 | 0.025927 | 0.00043587 | -0.0064706 | -0.0040823 | -0.077179 | 0.0061651 | 0.064491 | 0.051755 | -0.016447 | 0.025912 | -0.0049389 | -0.041199 | -0.059509 | 0.004578 | 0.032043 | 0.13275 | -0.027466 | 0.073242 | 0.40283 | 122.0764 | -0.059509 | 122.0764 | 0.16022 | 0.10986 | 0.18768 | 0.05951 | -122.2275 | -122.1359 | 0.18768 | 0.12817 | 0.027466 | 0.068664 | -0.032044 | -0.004577 | -0.091553 | -0.091553 | 0.21515 | 0.24261 | 0.16479 | 0.24719 | 0.16937 | 0.12817 | 0.027465 | 0.21973 | 122.1359 | -0.064087 | 122.1359 | -0.004577 | 122.1313 | -122.1634 | -122.2275 | 0.086975 | 122.1313 | 0.013733 | 0.45776
2601.3438 | 122.2961 | -0.09613 | 122.2229 | -0.15846 | -0.043671 | 0.003873 | 0.028064 | 0.0042811 | -0.0077524 | -0.0021597 | -0.09549 | 0.0050971 | 0.062354 | 0.051541 | -0.01666 | 0.027835 | -0.0062207 | -0.10986 | -0.018311 | -0.027466 | -0.10529 | -0.022888 | -0.14191 | -0.045776 | 0.27008 | 122.1085 | -0.10529 | 121.962 | 0.009155 | -0.045776 | 0.032043 | 0.068664 | -122.2412 | -122.3282 | 0.073242 | 0.050354 | -0.045777 | -0.01831 | -0.11444 | -0.009156 | -0.11444 | -0.26093 | 0.10528 | 0.12817 | 0.050354 | 0.13733 | 0.05951 | 0.004578 | -0.07782 | 0.11444 | 122.0673 | 0.009155 | 122.2137 | 0.077819 | 122.2046 | -122.2504 | -122.3282 | -0.009156 | 122.0581 | -0.013733 | 0.36621
2603.1094 | 122.4106 | -0.059509 | 122.1817 | -0.13557 | -0.045807 | 0.0040866 | 0.025073 | 0.00064947 | -0.0090342 | -0.0045095 | -0.031403 | 0.0036017 | 0.067481 | 0.040219 | -0.014524 | 0.02634 | -0.0049389 | -0.091553 | -0.036621 | -0.013733 | -0.004578 | 0.10529 | 0 | 0.07782 | 0.48065 | 122.0673 | -0.064087 | 122.0535 | 0.16937 | 0.11902 | 0.16022 | 0.045776 | -122.2183 | -122.1863 | 0.16479 | 0.13733 | 0.059509 | 0.091553 | 0.013733 | -0.004578 | -0.11444 | -0.12817 | 0.22888 | 0.21973 | 0.17853 | 0.2243 | 0.18311 | 0.11902 | 0.009155 | 0.23346 | 122.1176 | -0.022888 | 122.1313 | 0.022888 | 122.1268 | -122.1954 | -122.2458 | 0.054931 | 122.113 | -0.032044 | 0.54016
2604.8125 | 122.2687 | -0.10529 | 122.2183 | -0.16609 | -0.043885 | 0.0030184 | 0.026568 | 0.0010767 | -0.0092478 | -0.0038687 | -0.086334 | 0.0063787 | 0.063423 | 0.0462 | -0.018156 | 0.028476 | -0.0028027 | -0.10071 | -0.032043 | -0.050354 | -0.068665 | 0 | -0.1236 | -0.041199 | 0.33417 | 122.1085 | -0.09613 | 121.9528 | 0.009155 | -0.050354 | 0.032043 | 0.054932 | -122.2504 | -122.287 | 0.10529 | 0.064087 | -0.01831 | 0.009155 | -0.073242 | 0.009156 | -0.10986 | -0.2655 | 0.11444 | 0.13733 | 0.054932 | 0.12817 | 0.045776 | 0.050354 | -0.018311 | 0.10528 | 122.049 | 0.018311 | 122.2046 | 0.073243 | 122.2137 | -122.2687 | -122.3145 | 0.036621 | 122.0581 | 0.004578 | 0.43945
2606.5625 | 122.2778 | -0.091553 | 122.2046 | -0.13557 | -0.043671 | 0.003232 | 0.026568 | 0.0021447 | -0.0066844 | -0.0034415 | -0.1077 | 0.0080877 | 0.064918 | 0.053891 | -0.016874 | 0.02869 | -0.0042981 | -0.09613 | -0.018311 | -0.027466 | -0.036621 | 0.041199 | -0.091553 | -0.004578 | 0.39368 | 122.113 | -0.086975 | 121.962 | 0.054932 | -0.041199 | 0.045776 | 0.064087 | -122.2229 | -122.2412 | 0.13275 | 0.086975 | 0 | 0.022888 | -0.064087 | 0.004578 | -0.091553 | -0.24262 | 0.14649 | 0.13733 | 0.050354 | 0.13275 | 0.045776 | 0.068665 | -0.009155 | 0.14191 | 122.0489 | 0.009155 | 122.2 | 0.073242 | 122.2046 | -122.2321 | -122.2916 | 0.054932 | 122.0535 | -0.004577 | 0.48523
2608.3281 | 122.2824 | -0.10071 | 122.2 | -0.16609 | -0.042816 | 0.0040866 | 0.025927 | 0.0025721 | -0.0066844 | -0.0036551 | -0.086334 | 0.0072333 | 0.064063 | 0.0509 | -0.015806 | 0.02869 | -0.0064343 | -0.11902 | -0.018311 | -0.050354 | -0.10529 | -0.032043 | -0.13733 | -0.036621 | 0.2655 | 122.0947 | -0.086975 | 121.9482 | 0.018311 | -0.032043 | 0.032043 | 0.050354 | -122.2183 | -122.3053 | 0.068665 | 0.064087 | -0.036621 | 0.013733 | -0.086975 | 0.013733 | -0.10528 | -0.25177 | 0.11902 | 0.13275 | 0.068665 | 0.11902 | 0.054932 | 0.018311 | -0.054932 | 0.10529 | 122.0352 | 0.032043 | 122.1817 | 0.082397 | 122.1954 | -122.2504 | -122.287 | -0.004578 | 122.0489 | -0.018311 | 0.36621
2610.0938 | 122.3923 | -0.064087 | 122.1771 | -0.13557 | -0.043671 | 0.0034456 | 0.022937 | -0.00084593 | -0.008607 | -0.0038687 | -0.055817 | 0.0057379 | 0.062995 | 0.0509 | -0.015592 | 0.027408 | -0.0049389 | -0.059509 | -0.068665 | 0.004578 | 0.041199 | 0.14191 | -0.018311 | 0.07782 | 0.4303 | 122.0398 | -0.050354 | 122.0627 | 0.16022 | 0.09613 | 0.16022 | 0.068665 | -122.2458 | -122.1359 | 0.20599 | 0.14191 | 0.045776 | 0.073242 | -0.022889 | 0.013733 | -0.13733 | -0.11444 | 0.2243 | 0.2243 | 0.16022 | 0.21057 | 0.14648 | 0.13733 | 0.036621 | 0.21057 | 122.113 | -0.073243 | 122.0901 | -0.004578 | 122.1039 | -122.1725 | -122.2275 | 0.10529 | 122.1268 | 0.004578 | 0.49439
2611.875 | 122.2778 | -0.10529 | 122.2321 | -0.1432 | -0.044312 | 0.0034456 | 0.026141 | 0.0012903 | -0.0094614 | -0.0036551 | -0.10159 | 0.0048833 | 0.065986 | 0.051755 | -0.015806 | 0.026981 | -0.0021619 | -0.13275 | -0.022888 | -0.054932 | -0.09613 | -0.018311 | -0.14648 | -0.032043 | 0.27008 | 122.1222 | -0.091553 | 121.9528 | 0.013733 | -0.041199 | 0.032043 | 0.050354 | -122.2549 | -122.3282 | 0.086975 | 0.073243 | -0.041198 | 0.022889 | -0.091552 | 0.013733 | -0.10986 | -0.27924 | 0.11902 | 0.13733 | 0.064087 | 0.1236 | 0.050354 | 0.036621 | -0.041198 | 0.10529 | 122.0444 | 0.032044 | 122.2137 | 0.082398 | 122.2275 | -122.287 | -122.3236 | 0.009156 | 122.0581 | -0.027465 | 0.37537
2613.5625 | 122.3831 | -0.064087 | 122.1954 | -0.17372 | -0.043457 | 0.0030184 | 0.0255 | -0.0014867 | -0.0077524 | -0.0038687 | -0.077179 | 0.0048833 | 0.064491 | 0.051755 | -0.016447 | 0.026553 | -0.0064343 | -0.13275 | -0.041199 | -0.036621 | -0.064087 | 0.036621 | -0.10529 | 0 | 0.31128 | 122.0947 | -0.068665 | 122.0444 | 0.10529 | 0.054932 | 0.12817 | 0.027466 | -122.2366 | -122.2595 | 0.10071 | 0.064087 | -0.041199 | 0.036621 | -0.068665 | -0.004578 | -0.10071 | -0.15106 | 0.16937 | 0.19226 | 0.11902 | 0.19684 | 0.1236 | 0.073242 | -0.027466 | 0.17395 | 122.113 | -0.004578 | 122.1634 | 0.022888 | 122.1588 | -122.2321 | -122.2641 | 0 | 122.1085 | -0.068664 | 0.37537
2615.3281 | 122.4106 | -0.059509 | 122.1771 | -0.10506 | -0.045594 | 0.0034456 | 0.024218 | -0.0042639 | -0.0088206 | -0.0036551 | 0.014374 | 0.0036017 | 0.063423 | 0.047055 | -0.015806 | 0.027194 | -0.0021619 | -0.086975 | -0.073242 | -0.022888 | 0.045776 | 0.16479 | 0.032043 | 0.10071 | 0.58594 | 122.0673 | -0.059509 | 122.0398 | 0.16937 | 0.14191 | 0.14648 | 0.036621 | -122.2504 | -122.1313 | 0.2243 | 0.16022 | 0.091552 | 0.1236 | 0.054931 | 0 | -0.10986 | -0.13733 | 0.22888 | 0.20599 | 0.20142 | 0.20599 | 0.20142 | 0.18768 | 0.068664 | 0.22888 | 122.0993 | -0.050354 | 122.1268 | -0.013733 | 122.1268 | -122.2 | -122.2366 | 0.10528 | 122.0993 | -0.027466 | 0.64545
2617.0938 | 122.3236 | -0.091553 | 122.2092 | -0.097427 | -0.043671 | 0.0023776 | 0.025714 | -0.00020513 | -0.011384 | -0.0036551 | -0.092438 | 0.0050971 | 0.063209 | 0.048977 | -0.017088 | 0.026126 | -0.0066479 | -0.10529 | -0.004578 | -0.054932 | -0.032043 | 0.050354 | -0.054932 | 0.013733 | 0.45776 | 122.1085 | -0.082397 | 122.0078 | 0.09613 | 0.032043 | 0.086975 | 0.036621 | -122.2137 | -122.2412 | 0.14191 | 0.10529 | 0.036621 | 0.068665 | 0 | 0.009156 | -0.10071 | -0.20142 | 0.18768 | 0.17853 | 0.1236 | 0.16937 | 0.11444 | 0.10529 | 0.022889 | 0.17853 | 122.0901 | 0.050354 | 122.1909 | 0.086975 | 122.2 | -122.2641 | -122.2916 | 0.05951 | 122.0993 | -0.013733 | 0.54932
2618.8594 | 122.3923 | -0.07782 | 122.1909 | -0.13557 | -0.043457 | 0.0030184 | 0.025714 | -0.0012731 | -0.007966 | -0.0023733 | -0.071076 | 0.0044561 | 0.065132 | 0.051968 | -0.016874 | 0.029117 | -0.0040845 | -0.11444 | -0.032043 | -0.027466 | -0.045776 | 0.050354 | -0.091553 | 0.018311 | 0.36163 | 122.0718 | -0.091553 | 122.0444 | 0.1236 | 0.082397 | 0.15564 | 0.050354 | -122.2229 | -122.2366 | 0.12817 | 0.096131 | -0.013733 | 0.045777 | -0.064087 | -0.013733 | -0.11902 | -0.14648 | 0.20142 | 0.23346 | 0.16022 | 0.24719 | 0.17395 | 0.07782 | -0.01831 | 0.21515 | 122.1359 | -0.004577 | 122.1634 | 0.045777 | 122.1497 | -122.2183 | -122.2824 | 0.032044 | 122.1222 | -0.036621 | 0.43945
2620.625 | 122.3969 | -0.073242 | 122.1634 | -0.13557 | -0.044739 | 0.0017368 | 0.021655 | 0.0010767 | -0.012666 | -0.0038687 | 0.0082703 | 0.0074469 | 0.065345 | 0.051755 | -0.015165 | 0.027835 | -0.0040845 | -0.054932 | -0.064087 | -0.022888 | 0.041199 | 0.15564 | 0.041199 | 0.10071 | 0.56763 | 122.0627 | -0.054932 | 122.0627 | 0.15564 | 0.14191 | 0.14191 | 0.050354 | -122.2275 | -122.1222 | 0.22888 | 0.17395 | 0.11444 | 0.1236 | 0.064087 | 0.01831 | -0.10071 | -0.10071 | 0.22888 | 0.21515 | 0.21515 | 0.19684 | 0.19684 | 0.17853 | 0.064087 | 0.21057 | 122.1176 | -0.041199 | 122.1176 | 0.009155 | 122.1359 | -122.1863 | -122.2183 | 0.11444 | 122.1359 | 0.01831 | 0.64087
2622.3281 | 122.4014 | -0.073242 | 122.1863 | -0.1432 | -0.04773 | 0.0040866 | 0.024005 | -0.0046911 | -0.0098886 | -0.0028005 | 0.0021667 | 0.0048833 | 0.060859 | 0.047909 | -0.015165 | 0.025912 | -0.0057935 | -0.10986 | -0.050354 | -0.022888 | -0.013733 | 0.07782 | -0.032043 | 0.054932 | 0.43488 | 122.0444 | -0.07782 | 122.0444 | 0.16022 | 0.12817 | 0.14648 | 0.050354 | -122.2366 | -122.2 | 0.15106 | 0.12817 | 0.041199 | 0.07782 | -0.009155 | -0.004578 | -0.14191 | -0.14191 | 0.23346 | 0.21973 | 0.20142 | 0.2243 | 0.20599 | 0.10071 | 0.009155 | 0.23804 | 122.1222 | -0.027466 | 122.1222 | 0.022888 | 122.1176 | -122.2092 | -122.2641 | 0.059509 | 122.1176 | -0.036621 | 0.50812
2624.0938 | 122.3785 | -0.068665 | 122.1817 | -0.16609 | -0.043885 | 0.0040866 | 0.024005 | -0.0021277 | -0.009675 | -0.0028005 | -0.04361 | 0.0053107 | 0.064277 | 0.050046 | -0.01602 | 0.024417 | -0.0051525 | -0.091553 | -0.064087 | -0.004578 | -0.013733 | 0.091553 | -0.054932 | 0.050354 | 0.38452 | 122.0627 | -0.07782 | 122.0123 | 0.10071 | 0.07782 | 0.11902 | 0.064087 | -122.2458 | -122.1954 | 0.16022 | 0.11902 | 0.013733 | 0.054932 | -0.050354 | -0.009155 | -0.11902 | -0.16937 | 0.16937 | 0.18768 | 0.14649 | 0.19684 | 0.15564 | 0.096131 | -0.009155 | 0.17853 | 122.0901 | -0.059509 | 122.1405 | 0.004578 | 122.1313 | -122.1863 | -122.2595 | 0.054932 | 122.081 | -0.022888 | 0.45319
2625.7812 | 122.3785 | -0.086975 | 122.2046 | -0.15083 | -0.046234 | 0.0023776 | 0.025073 | 0.00022207 | -0.012666 | -0.0053641 | -0.0039367 | 0.0050971 | 0.065345 | 0.045773 | -0.016447 | 0.025912 | -0.0047253 | -0.11902 | -0.059509 | -0.027466 | -0.050354 | 0.073242 | -0.050354 | 0.036621 | 0.41657 | 122.0764 | -0.073242 | 122.0306 | 0.10529 | 0.064087 | 0.11444 | 0.059509 | -122.2641 | -122.2549 | 0.16022 | 0.1236 | 0.036621 | 0.064087 | -0.022888 | 0.013733 | -0.12817 | -0.17395 | 0.19226 | 0.20142 | 0.15106 | 0.18768 | 0.13733 | 0.10071 | -0.022888 | 0.17853 | 122.1039 | -0.032043 | 122.1497 | 0.027466 | 122.1634 | -122.2321 | -122.2778 | 0.036621 | 122.1176 | -0.032044 | 0.50354
2627.5312 | 122.2916 | -0.11444 | 122.2275 | -0.13557 | -0.041962 | 0.0025912 | 0.027423 | -0.0029821 | -0.0094614 | -0.0047231 | -0.14737 | 0.0048833 | 0.064704 | 0.050686 | -0.01666 | 0.030185 | -0.0085705 | -0.13275 | -0.022888 | -0.050354 | -0.10986 | -0.045776 | -0.14191 | -0.050354 | 0.28839 | 122.113 | -0.10986 | 121.9711 | 0.009155 | -0.050354 | 0.041199 | 0.064087 | -122.2504 | -122.3373 | 0.068665 | 0.064087 | -0.027466 | 0 | -0.091553 | 0.004578 | -0.11444 | -0.25635 | 0.1236 | 0.15564 | 0.064087 | 0.15106 | 0.059509 | 0.004578 | -0.059509 | 0.11902 | 122.081 | 0.027466 | 122.2229 | 0.091553 | 122.2275 | -122.2778 | -122.3373 | 0.004578 | 122.0856 | -0.01831 | 0.40283
2629.2344 | 122.3099 | -0.086975 | 122.2275 | -0.089798 | -0.044525 | 0.00066863 | 0.026355 | -0.0014867 | -0.010957 | -0.0028005 | -0.031403 | 0.0048833 | 0.063209 | 0.051541 | -0.017729 | 0.026126 | -0.0075025 | -0.068665 | -0.064087 | -0.018311 | -0.009155 | 0.082397 | -0.022888 | 0.050354 | 0.49439 | 122.1039 | -0.073242 | 121.9711 | 0.068665 | 0.018311 | 0.059509 | 0.068664 | -122.2916 | -122.2366 | 0.16937 | 0.13733 | 0.064087 | 0.068665 | -0.004577 | 0.013733 | -0.1236 | -0.25635 | 0.15564 | 0.14648 | 0.10529 | 0.13275 | 0.091553 | 0.10071 | 0.009156 | 0.14191 | 122.0444 | -0.045776 | 122.1771 | 0.022888 | 122.1909 | -122.2458 | -122.3007 | 0.07782 | 122.0581 | 0.01831 | 0.58136
2630.9844 | 122.3602 | -0.082397 | 122.2 | -0.15846 | -0.04538 | 0.002164 | 0.025073 | 0.0034265 | -0.01053 | -0.0019461 | -0.022247 | 0.0044561 | 0.063636 | 0.054318 | -0.014951 | 0.027621 | -0.0085705 | -0.064087 | -0.054932 | -0.004578 | 0.022888 | 0.11902 | -0.004578 | 0.073242 | 0.53101 | 122.0901 | -0.07782 | 122.0215 | 0.12817 | 0.082397 | 0.10986 | 0.077819 | -122.2549 | -122.1771 | 0.20142 | 0.15564 | 0.077819 | 0.07782 | 0 | 0.004577 | -0.10986 | -0.17853 | 0.21057 | 0.19226 | 0.16479 | 0.18768 | 0.16022 | 0.1236 | 0.027466 | 0.20599 | 122.0993 | -0.050354 | 122.168 | 0.027465 | 122.1725 | -122.2046 | -122.2778 | 0.10528 | 122.1039 | 0.01831 | 0.6134
2632.7344 | 122.3053 | -0.10529 | 122.2092 | -0.13557 | -0.044312 | 0.0010958 | 0.024646 | -0.0083227 | -0.010102 | -0.0030141 | -0.034454 | 0.0050971 | 0.063423 | 0.050046 | -0.01602 | 0.024417 | -0.0077161 | -0.086975 | -0.050354 | -0.013733 | -0.036621 | 0.073242 | -0.036621 | 0.027466 | 0.48065 | 122.0947 | -0.082397 | 121.9711 | 0.054932 | 0.027466 | 0.036621 | 0.091553 | -122.2595 | -122.2458 | 0.17853 | 0.13275 | 0.068665 | 0.041199 | -0.022888 | 0.022889 | -0.11444 | -0.23804 | 0.16022 | 0.14191 | 0.13275 | 0.11902 | 0.10986 | 0.086975 | -0.022888 | 0.13733 | 122.0535 | -0.036621 | 122.1771 | 0.054932 | 122.2 | -122.2229 | -122.2916 | 0.068665 | 122.0764 | 0.018311 | 0.58594
2634.4219 | 122.3648 | -0.064087 | 122.2 | -0.12032 | -0.044312 | 0.0019504 | 0.025073 | -0.0014867 | -0.0071116 | -0.0049367 | -0.040558 | 0.0040289 | 0.062141 | 0.049832 | -0.015592 | 0.025058 | -0.0028027 | -0.09613 | -0.064087 | -0.013733 | -0.013733 | 0.09613 | -0.041199 | 0.059509 | 0.40741 | 122.0993 | -0.059509 | 122.0123 | 0.10071 | 0.068665 | 0.11444 | 0.050354 | -122.2641 | -122.2137 | 0.16022 | 0.1236 | 0.022888 | 0.073242 | -0.027466 | 0.004578 | -0.10071 | -0.18768 | 0.1648 | 0.17853 | 0.13275 | 0.17395 | 0.12817 | 0.10986 | 0 | 0.16022 | 122.0718 | -0.050354 | 122.1588 | 0 | 122.1634 | -122.2137 | -122.2595 | 0.050354 | 122.0764 | -0.032043 | 0.4715
2636.1719 | 122.3785 | -0.045776 | 122.1909 | -0.15083 | -0.045166 | 0.003873 | 0.025073 | -0.0021277 | -0.0094614 | -0.0032277 | -0.058869 | 0.0036017 | 0.06385 | 0.047696 | -0.016874 | 0.027408 | -0.0036573 | -0.073242 | -0.064087 | 0.018311 | 0.027466 | 0.13275 | -0.032043 | 0.073242 | 0.42114 | 122.0581 | -0.073242 | 122.0398 | 0.12817 | 0.07782 | 0.1236 | 0.064087 | -122.2549 | -122.1634 | 0.17853 | 0.11902 | 0.013733 | 0.054931 | -0.050354 | -0.027466 | -0.13275 | -0.15106 | 0.17395 | 0.16937 | 0.1236 | 0.19684 | 0.15106 | 0.11444 | 0.009155 | 0.20142 | 122.113 | -0.082398 | 122.1313 | -0.018311 | 122.1039 | -122.1725 | -122.2641 | 0.073242 | 122.0856 | -0.027466 | 0.46692
2637.8594 | 122.374 | -0.07782 | 122.1909 | -0.20424 | -0.044739 | 0.0028048 | 0.025073 | -0.0038367 | -0.01117 | -0.0010915 | -0.019196 | 0.0048833 | 0.062141 | 0.051327 | -0.01602 | 0.026767 | -0.0045117 | -0.054932 | -0.059509 | -0.022888 | 0.036621 | 0.12817 | 0.018311 | 0.07782 | 0.55847 | 122.081 | -0.059509 | 122.0306 | 0.14648 | 0.10529 | 0.11902 | 0.054932 | -122.2504 | -122.1542 | 0.20599 | 0.15564 | 0.096131 | 0.10071 | 0.041199 | 0.018311 | -0.10986 | -0.16022 | 0.2243 | 0.19684 | 0.18311 | 0.17853 | 0.16479 | 0.15106 | 0.059509 | 0.20599 | 122.0901 | -0.036621 | 122.1405 | 0.018311 | 122.1588 | -122.2137 | -122.2504 | 0.11444 | 122.1085 | 0.022888 | 0.63629
2639.625 | 122.3923 | -0.050354 | 122.2046 | -0.19661 | -0.044098 | 0.0025912 | 0.024218 | -0.0036231 | -0.011384 | -0.0049367 | -0.046661 | 0.0038153 | 0.063209 | 0.046414 | -0.018156 | 0.024417 | -0.010707 | -0.073242 | -0.059509 | -0.004578 | 0.018311 | 0.12817 | -0.027466 | 0.054932 | 0.4303 | 122.0856 | -0.054932 | 122.049 | 0.11902 | 0.082397 | 0.13275 | 0.045776 | -122.2641 | -122.1863 | 0.17853 | 0.10529 | 0.022888 | 0.05951 | -0.022888 | -0.004578 | -0.11902 | -0.15564 | 0.16937 | 0.18311 | 0.13275 | 0.18768 | 0.13733 | 0.13275 | 0.022889 | 0.17395 | 122.1039 | -0.054931 | 122.1405 | -0.009155 | 122.1359 | -122.2092 | -122.2595 | 0.068665 | 122.0993 | -0.022888 | 0.48065
2641.375 | 122.2824 | -0.10529 | 122.2366 | -0.097427 | -0.041962 | 0.0034456 | 0.026141 | -0.0019141 | -0.0090342 | -2.3544e-05 | -0.14127 | 0.0076605 | 0.061927 | 0.048764 | -0.017301 | 0.027194 | -0.0023755 | -0.10071 | -0.022888 | -0.059509 | -0.073242 | -0.027466 | -0.15564 | -0.064087 | 0.30212 | 122.113 | -0.091553 | 121.9437 | 0.004578 | -0.064087 | 0.022888 | 0.045777 | -122.2595 | -122.3099 | 0.07782 | 0.041199 | -0.050354 | -0.004578 | -0.096131 | 0.013733 | -0.1236 | -0.29297 | 0.10986 | 0.12817 | 0.041199 | 0.11444 | 0.027466 | 0.032043 | -0.013733 | 0.096131 | 122.0352 | 0.036621 | 122.2046 | 0.082398 | 122.2183 | -122.2961 | -122.3282 | 0.032044 | 122.049 | 0.004578 | 0.40741
2643.0781 | 122.4152 | -0.054932 | 122.1909 | -0.097427 | -0.044098 | 0.0051546 | 0.025073 | -0.0012731 | -0.008607 | -0.0036551 | -0.077179 | 0.0050971 | 0.064704 | 0.0556 | -0.01666 | 0.026981 | -0.0042981 | -0.032043 | -0.068665 | 0.004578 | 0.041199 | 0.11444 | -0.013733 | 0.073242 | 0.42114 | 122.0673 | -0.064087 | 122.1085 | 0.16022 | 0.13275 | 0.16937 | 0.05951 | -122.2595 | -122.1497 | 0.16937 | 0.12817 | 0.041199 | 0.068664 | -0.018311 | -0.009155 | -0.1236 | -0.082398 | 0.21515 | 0.22431 | 0.18768 | 0.23346 | 0.19684 | 0.10986 | 0.036621 | 0.2243 | 122.1725 | -0.073243 | 122.1313 | -0.013733 | 122.1222 | -122.1863 | -122.2549 | 0.096131 | 122.1634 | 0.022889 | 0.47607
2644.8438 | 122.3785 | -0.068665 | 122.2137 | -0.18135 | -0.046875 | -0.00018577 | 0.023364 | 0.0010767 | -0.0092478 | -0.0040823 | -0.016144 | 0.0070197 | 0.063209 | 0.047909 | -0.018583 | 0.025272 | -0.0030163 | -0.11444 | -0.045776 | -0.009155 | -0.027466 | 0.054932 | -0.045776 | 0.041199 | 0.3891 | 122.081 | -0.082397 | 122.0032 | 0.091553 | 0.064087 | 0.10529 | 0.05951 | -122.2595 | -122.2412 | 0.1236 | 0.10986 | 0.022889 | 0.050354 | -0.036621 | -0.013732 | -0.13275 | -0.21057 | 0.16022 | 0.17395 | 0.13275 | 0.18768 | 0.14648 | 0.064087 | -0.018311 | 0.17395 | 122.0856 | -0.036621 | 122.1634 | 0.022889 | 122.1497 | -122.2229 | -122.2961 | 0.041199 | 122.0718 | -0.045776 | 0.45776
2646.6094 | 122.3831 | -0.07782 | 122.1954 | -0.18135 | -0.044525 | 0.0013094 | 0.0255 | 0.00064947 | -0.010743 | -0.00045074 | -0.055817 | 0.0061651 | 0.065986 | 0.050259 | -0.016447 | 0.028262 | -0.0045117 | -0.086975 | -0.068665 | -0.013733 | 0.013733 | 0.10529 | -0.045776 | 0.050354 | 0.40283 | 122.0718 | -0.068665 | 122.0215 | 0.10071 | 0.07782 | 0.1236 | 0.064087 | -122.2641 | -122.1817 | 0.18311 | 0.12817 | 0.032044 | 0.064087 | -0.032043 | 0.009155 | -0.1236 | -0.17395 | 0.17853 | 0.20142 | 0.15564 | 0.19226 | 0.14649 | 0.11902 | 0.027466 | 0.16937 | 122.0901 | -0.054932 | 122.1405 | 0.009155 | 122.1497 | -122.2092 | -122.2641 | 0.091553 | 122.0993 | -0.009155 | 0.48065
2648.375 | 122.2778 | -0.10986 | 122.2412 | -0.18898 | -0.042176 | 0.003873 | 0.029345 | -0.0025549 | -0.010743 | -0.0028005 | -0.13211 | 0.0072333 | 0.064063 | 0.057309 | -0.016874 | 0.026767 | -0.0051525 | -0.1236 | -0.018311 | -0.036621 | -0.086975 | -0.050354 | -0.15106 | -0.073242 | 0.27466 | 122.1497 | -0.09613 | 121.9437 | 0.004578 | -0.036621 | 0.032043 | 0.073242 | -122.2595 | -122.3282 | 0.059509 | 0.036621 | -0.041199 | -0.036621 | -0.11444 | 0.013733 | -0.091553 | -0.29755 | 0.11444 | 0.14191 | 0.073242 | 0.12817 | 0.059509 | -0.013733 | -0.050354 | 0.10071 | 122.0398 | 0.01831 | 122.2458 | 0.091552 | 122.2595 | -122.2778 | -122.3373 | 0.022888 | 122.0535 | -0.013733 | 0.38452
2650.0781 | 122.3511 | -0.073242 | 122.2046 | -0.10506 | -0.043244 | 0.0013094 | 0.027636 | -0.0027685 | -0.0077524 | -0.0025869 | -0.1138 | 0.0061651 | 0.062782 | 0.050046 | -0.017088 | 0.029544 | -0.0015209 | -0.1236 | -0.022888 | -0.045776 | -0.082397 | 0 | -0.12817 | -0.018311 | 0.31128 | 122.1085 | -0.09613 | 122.0169 | 0.059509 | 0.013733 | 0.07782 | 0.027466 | -122.2275 | -122.287 | 0.073242 | 0.054931 | -0.054932 | 0.027465 | -0.082398 | -0.022888 | -0.096131 | -0.18768 | 0.13275 | 0.15106 | 0.086975 | 0.17395 | 0.10986 | 0.045776 | -0.036621 | 0.15564 | 122.113 | 0.022888 | 122.2046 | 0.050354 | 122.1817 | -122.2504 | -122.3007 | -0.009155 | 122.0901 | -0.050354 | 0.38452
2651.8281 | 122.406 | -0.050354 | 122.1588 | -0.20424 | -0.044098 | 0.0036594 | 0.026141 | 8.47e-06 | -0.0077524 | -0.0028005 | -0.071076 | 0.0068059 | 0.065345 | 0.05325 | -0.015806 | 0.02869 | -0.0081433 | -0.036621 | -0.041199 | 0.004578 | 0.032043 | 0.12817 | -0.027466 | 0.07782 | 0.43488 | 122.0901 | -0.068665 | 122.081 | 0.16479 | 0.11444 | 0.16937 | 0.054932 | -122.2 | -122.1268 | 0.17853 | 0.12817 | 0.022888 | 0.073242 | -0.032044 | -0.018311 | -0.068664 | -0.077819 | 0.21515 | 0.21973 | 0.16479 | 0.23804 | 0.18311 | 0.1236 | 0.027465 | 0.23346 | 122.1497 | -0.045777 | 122.1588 | 0.009155 | 122.1405 | -122.1542 | -122.2275 | 0.082397 | 122.1313 | 0.013733 | 0.48523
2653.5781 | 122.2961 | -0.10071 | 122.2137 | -0.1432 | -0.042816 | 0.0023776 | 0.026568 | -0.0012731 | -0.009675 | -0.0025869 | -0.13821 | 0.0053107 | 0.063423 | 0.046841 | -0.015592 | 0.026126 | -0.0064343 | -0.086975 | -0.041199 | -0.032043 | -0.050354 | 0.032043 | -0.086975 | -0.013733 | 0.40283 | 122.1222 | -0.068665 | 121.962 | 0.032043 | -0.032043 | 0.050354 | 0.068665 | -122.2549 | -122.2641 | 0.13275 | 0.086975 | 0.013733 | 0.01831 | -0.054932 | 0.032043 | -0.091553 | -0.25177 | 0.13275 | 0.15106 | 0.068665 | 0.11902 | 0.036622 | 0.064086 | -0.018311 | 0.10071 | 122.0306 | -0.009156 | 122.1909 | 0.059509 | 122.2229 | -122.2458 | -122.2824 | 0.050354 | 122.0627 | 0.013733 | 0.50354
2655.2656 | 122.374 | -0.073242 | 122.1954 | -0.18135 | -0.044312 | 0.0045138 | 0.024005 | -0.00063233 | -0.0090342 | -0.0068593 | -0.037506 | 0.0048833 | 0.065559 | 0.046414 | -0.015165 | 0.027621 | -0.0017347 | -0.086975 | -0.059509 | -0.027466 | -0.009155 | 0.10529 | -0.041199 | 0.059509 | 0.40283 | 122.1085 | -0.068665 | 122.0306 | 0.091553 | 0.07782 | 0.1236 | 0.045776 | -122.2549 | -122.2046 | 0.17853 | 0.13275 | 0.032043 | 0.086975 | -0.013733 | 0.004577 | -0.086976 | -0.16479 | 0.16479 | 0.19684 | 0.15106 | 0.19226 | 0.14649 | 0.13275 | 0.018311 | 0.16022 | 122.0993 | -0.032043 | 122.1771 | 0.013733 | 122.1817 | -122.2229 | -122.2641 | 0.064087 | 122.1039 | -0.013733 | 0.47607
2657.0156 | 122.3282 | -0.086975 | 122.2137 | -0.082169 | -0.046021 | 0.0028048 | 0.022082 | -0.0051183 | -0.011384 | -0.0034415 | -0.016144 | 0.0050971 | 0.065772 | 0.049618 | -0.017942 | 0.027835 | -0.0062207 | -0.073242 | -0.041199 | -0.009155 | 0 | 0.09613 | 0 | 0.059509 | 0.52185 | 122.1085 | -0.091553 | 121.9666 | 0.086975 | 0.022888 | 0.054932 | 0.07782 | -122.2549 | -122.2137 | 0.1831 | 0.14648 | 0.086975 | 0.068664 | 0.009155 | -0.004578 | -0.10529 | -0.24719 | 0.17395 | 0.14191 | 0.10986 | 0.14649 | 0.11444 | 0.10528 | 0.009155 | 0.17853 | 122.0581 | -0.032044 | 122.2 | 0.045776 | 122.1954 | -122.2229 | -122.3053 | 0.086975 | 122.0535 | 0.013733 | 0.60883
2658.7031 | 122.3419 | -0.082397 | 122.1954 | -0.15083 | -0.046234 | 0.0017368 | 0.024859 | 0.00043587 | -0.0090342 | -0.0010915 | -0.11075 | 0.0061651 | 0.061714 | 0.055173 | -0.01901 | 0.029544 | -0.0013073 | -0.082397 | -0.027466 | -0.018311 | -0.032043 | 0.073242 | -0.059509 | 0.013733 | 0.47607 | 122.1085 | -0.073242 | 122.0169 | 0.091553 | 0.032043 | 0.091553 | 0.064086 | -122.2229 | -122.2275 | 0.15564 | 0.09613 | 0.022888 | 0.032044 | -0.041198 | 0.009155 | -0.086976 | -0.17853 | 0.17395 | 0.17395 | 0.11444 | 0.16479 | 0.10529 | 0.091553 | -0.013732 | 0.16479 | 122.0901 | -0.009155 | 122.1817 | 0.054931 | 122.1909 | -122.2137 | -122.2687 | 0.050354 | 122.0993 | 0 | 0.55847
2660.4688 | 122.3969 | -0.050354 | 122.1863 | -0.15083 | -0.043885 | 0.0040866 | 0.025287 | -0.0036231 | -0.0092478 | -0.0040823 | -0.089386 | 0.0050971 | 0.067268 | 0.043637 | -0.015806 | 0.029117 | -0.0066479 | -0.082397 | -0.041199 | -0.027466 | -0.009155 | 0.082397 | -0.059509 | 0.045776 | 0.40283 | 122.1039 | -0.059509 | 122.0856 | 0.15106 | 0.09613 | 0.16022 | 0.022888 | -122.2275 | -122.1954 | 0.13275 | 0.09613 | -0.009155 | 0.073242 | -0.032043 | -0.009155 | -0.082397 | -0.10071 | 0.20142 | 0.21057 | 0.14648 | 0.21973 | 0.15564 | 0.10986 | 0.018311 | 0.21057 | 122.1451 | -0.013733 | 122.1634 | 0.009155 | 122.1542 | -122.2137 | -122.2458 | 0.041199 | 122.1359 | -0.032043 | 0.45319
2662.1562 | 122.4014 | -0.050354 | 122.2 | -0.13557 | -0.045166 | 0.003232 | 0.026355 | 0.0017175 | -0.0092478 | 0.00040366 | -0.071076 | 0.0055243 | 0.06385 | 0.0509 | -0.016874 | 0.028049 | -0.0062207 | -0.10071 | -0.032043 | -0.022888 | -0.009155 | 0.082397 | -0.050354 | 0.041199 | 0.37994 | 122.0947 | -0.068665 | 122.0718 | 0.14191 | 0.10529 | 0.16937 | 0.027466 | -122.2321 | -122.2092 | 0.13275 | 0.091553 | 0 | 0.064087 | -0.027466 | -0.018311 | -0.10528 | -0.12817 | 0.19226 | 0.21973 | 0.15564 | 0.23804 | 0.17395 | 0.10528 | 0.013733 | 0.21057 | 122.1405 | -0.009155 | 122.1634 | 0.018311 | 122.1451 | -122.2229 | -122.2687 | 0.041199 | 122.1222 | -0.050354 | 0.4303
2663.9219 | 122.3877 | -0.064087 | 122.2 | -0.20424 | -0.043885 | 0.0040866 | 0.0255 | -0.00063233 | -0.0075388 | -2.3544e-05 | -0.092438 | 0.0063787 | 0.064277 | 0.043423 | -0.015379 | 0.02933 | -0.0070751 | -0.13275 | -0.032043 | -0.036621 | -0.045776 | 0.041199 | -0.09613 | 0.013733 | 0.32044 | 122.0993 | -0.10071 | 122.0535 | 0.11902 | 0.064087 | 0.13275 | 0.027466 | -122.2321 | -122.2458 | 0.10529 | 0.07782 | -0.032043 | 0.050354 | -0.059509 | -0.036621 | -0.10071 | -0.14648 | 0.18311 | 0.19684 | 0.12817 | 0.23346 | 0.1648 | 0.07782 | -0.009155 | 0.21973 | 122.1542 | 0.004578 | 122.2 | 0.032044 | 122.1634 | -122.2366 | -122.3007 | 0.018311 | 122.1176 | -0.068664 | 0.38452
2665.6719 | 122.374 | -0.073242 | 122.1863 | -0.12032 | -0.046662 | 0.0023776 | 0.0255 | 0.00022207 | -0.0088206 | -0.0057913 | -0.0039367 | 0.0061651 | 0.064918 | 0.04086 | -0.016447 | 0.027621 | -0.0028027 | -0.11444 | -0.059509 | -0.009155 | -0.032043 | 0.059509 | -0.064087 | 0.045776 | 0.40283 | 122.0856 | -0.073242 | 122.0078 | 0.10986 | 0.07782 | 0.11444 | 0.064087 | -122.2458 | -122.2183 | 0.13275 | 0.11902 | 0.009155 | 0.054931 | -0.054932 | 0 | -0.10071 | -0.17853 | 0.18311 | 0.18768 | 0.15106 | 0.18768 | 0.15106 | 0.068664 | -0.022888 | 0.18311 | 122.081 | -0.050354 | 122.1588 | 0.013733 | 122.1588 | -122.1954 | -122.2595 | 0.041199 | 122.081 | -0.041199 | 0.47607
2667.3594 | 122.3969 | -0.059509 | 122.1771 | -0.16609 | -0.044525 | 0.0043002 | 0.025714 | -0.0031957 | -0.0094614 | -0.0028005 | -0.046661 | 0.0050971 | 0.065559 | 0.046841 | -0.017942 | 0.028049 | -0.0049389 | -0.059509 | -0.064087 | 0.018311 | 0.027466 | 0.14191 | -0.009155 | 0.064087 | 0.44403 | 122.0764 | -0.068665 | 122.0444 | 0.13275 | 0.10529 | 0.13733 | 0.07782 | -122.2412 | -122.1497 | 0.20142 | 0.1236 | 0.050354 | 0.045776 | -0.027466 | -0.009156 | -0.10071 | -0.13275 | 0.19226 | 0.19684 | 0.16479 | 0.20599 | 0.17395 | 0.1236 | 0.009155 | 0.20142 | 122.113 | -0.082398 | 122.1451 | -0.004578 | 122.1359 | -122.1588 | -122.2458 | 0.086975 | 122.1039 | 0 | 0.50354
2669.1094 | 122.4335 | -0.064087 | 122.1954 | -0.13557 | -0.044098 | 0.00088223 | 0.023364 | -0.00020513 | -0.007966 | -0.0038687 | -0.0069885 | 0.0048833 | 0.064063 | 0.04321 | -0.018156 | 0.028476 | -0.0049389 | -0.050354 | -0.054932 | -0.013733 | 0.054932 | 0.1831 | 0.045776 | 0.1236 | 0.57678 | 122.0901 | -0.050354 | 122.0718 | 0.1831 | 0.14191 | 0.15106 | 0.050354 | -122.2504 | -122.1405 | 0.24719 | 0.18768 | 0.10986 | 0.13733 | 0.059509 | 0.013733 | -0.10529 | -0.1236 | 0.24719 | 0.21515 | 0.20599 | 0.20142 | 0.19226 | 0.19684 | 0.068665 | 0.23346 | 122.1222 | -0.041199 | 122.1405 | 0.009155 | 122.1542 | -122.2092 | -122.2458 | 0.11902 | 122.1359 | 0.013733 | 0.64087
2670.8125 | 122.3785 | -0.07782 | 122.2046 | -0.12794 | -0.046875 | 0.0053684 | 0.022937 | -0.0012731 | -0.0088206 | -0.0055777 | -0.049713 | 0.0070197 | 0.062995 | 0.051114 | -0.017515 | 0.026553 | -0.0049389 | -0.064087 | -0.059509 | -0.004578 | 0.045776 | 0.12817 | 0.018311 | 0.091553 | 0.54474 | 122.0856 | -0.059509 | 122.0352 | 0.13733 | 0.10986 | 0.1236 | 0.073242 | -122.2641 | -122.1588 | 0.20599 | 0.16937 | 0.096131 | 0.096131 | 0.022889 | 0.018311 | -0.11902 | -0.16937 | 0.21515 | 0.20142 | 0.18768 | 0.1831 | 0.16937 | 0.13275 | 0.050354 | 0.19684 | 122.0947 | -0.054931 | 122.1451 | 0.018311 | 122.1634 | -122.2092 | -122.2641 | 0.1236 | 122.113 | 0.013733 | 0.62256
2672.5625 | 122.3007 | -0.11902 | 122.2046 | -0.12794 | -0.044525 | 0.0023776 | 0.0255 | 0.00064947 | -0.012452 | -0.0013051 | -0.092438 | 0.0085149 | 0.062782 | 0.048123 | -0.017088 | 0.027621 | -0.0085705 | -0.13733 | -0.013733 | -0.041199 | -0.10071 | -0.018311 | -0.10529 | -0.013733 | 0.4303 | 122.1451 | -0.11444 | 121.9482 | 0.045776 | -0.018311 | 0.041199 | 0.07782 | -122.2183 | -122.3053 | 0.10071 | 0.10529 | 0.013733 | 0.027466 | -0.064087 | 0.004578 | -0.059509 | -0.25635 | 0.16479 | 0.16022 | 0.10071 | 0.15564 | 0.09613 | 0.022888 | -0.059509 | 0.16022 | 122.0627 | 0.027466 | 122.2595 | 0.10529 | 122.2641 | -122.2458 | -122.319 | 0.018311 | 122.0673 | -0.01831 | 0.54932
2674.3125 | 122.3053 | -0.1236 | 122.2046 | -0.074539 | -0.046662 | 0.0025912 | 0.025714 | -0.0010595 | -0.0098886 | -0.0032277 | -0.083283 | 0.0059515 | 0.062568 | 0.048123 | -0.016233 | 0.026981 | -0.0030163 | -0.12817 | -0.018311 | -0.041199 | -0.086975 | -0.009155 | -0.11444 | -0.013733 | 0.44403 | 122.1405 | -0.086975 | 121.9666 | 0.041199 | -0.009155 | 0.050354 | 0.082397 | -122.2229 | -122.2916 | 0.11444 | 0.10986 | 0.009155 | 0.027466 | -0.073242 | 0.036621 | -0.064087 | -0.23804 | 0.16479 | 0.17395 | 0.11444 | 0.13733 | 0.07782 | 0.032044 | -0.045776 | 0.12817 | 122.0535 | 0.022888 | 122.2275 | 0.10528 | 122.2641 | -122.2458 | -122.2916 | 0.036621 | 122.0901 | -0.004578 | 0.56763
2676.0625 | 122.4106 | -0.036621 | 122.2 | -0.15083 | -0.047089 | 0.0028048 | 0.022937 | -0.0025549 | -0.010957 | -0.0040823 | 0.011322 | 0.0044561 | 0.062782 | 0.048764 | -0.015592 | 0.024631 | -0.0066479 | -0.050354 | -0.054932 | 0.004578 | 0.041199 | 0.17395 | 0.032043 | 0.11444 | 0.59052 | 122.0764 | -0.054932 | 122.0764 | 0.20142 | 0.14648 | 0.13733 | 0.041199 | -122.2549 | -122.1588 | 0.21057 | 0.15106 | 0.068664 | 0.10986 | 0.027465 | -0.018311 | -0.1236 | -0.1236 | 0.23804 | 0.17395 | 0.18311 | 0.19226 | 0.20142 | 0.16937 | 0.036621 | 0.25635 | 122.1313 | -0.05951 | 122.1313 | -0.018311 | 122.113 | -122.1954 | -122.2549 | 0.07782 | 122.113 | -0.013733 | 0.62714
2677.8125 | 122.3053 | -0.10986 | 122.2321 | -0.074539 | -0.044739 | 0.0028048 | 0.026355 | -0.0029821 | -0.010102 | -0.0034415 | -0.064972 | 0.0068059 | 0.064704 | 0.048764 | -0.01666 | 0.028262 | -0.0028027 | -0.13733 | -0.013733 | -0.064087 | -0.091553 | -0.018311 | -0.10071 | -0.009155 | 0.44403 | 122.1588 | -0.10071 | 121.9391 | 0.027466 | -0.013733 | 0.027466 | 0.045776 | -122.2458 | -122.3236 | 0.091552 | 0.10071 | 0.009155 | 0.054932 | -0.036621 | 0.009155 | -0.073243 | -0.29297 | 0.13733 | 0.13733 | 0.09613 | 0.12817 | 0.086975 | 0.045776 | -0.027466 | 0.12817 | 122.0398 | 0.050354 | 122.2595 | 0.09613 | 122.2687 | -122.2961 | -122.3328 | 0.01831 | 122.049 | -0.027466 | 0.55389
2679.5781 | 122.2824 | -0.091553 | 122.2183 | -0.12794 | -0.041107 | 0.0053684 | 0.027636 | 0.00043587 | -0.0092478 | -0.0038687 | -0.12601 | 0.0048833 | 0.064277 | 0.0462 | -0.01666 | 0.028262 | -0.0023755 | -0.073242 | -0.032043 | -0.032043 | -0.059509 | 0.027466 | -0.09613 | -0.009155 | 0.37079 | 122.1359 | -0.091553 | 121.962 | 0.013733 | -0.032043 | 0.045776 | 0.05951 | -122.2504 | -122.2778 | 0.11902 | 0.082398 | -0.004577 | 0.022888 | -0.064087 | 0 | -0.082398 | -0.25635 | 0.10529 | 0.13733 | 0.05951 | 0.13733 | 0.05951 | 0.059509 | -0.027466 | 0.10529 | 122.0535 | 0 | 122.2275 | 0.05951 | 122.2275 | -122.2504 | -122.3099 | 0.032044 | 122.0535 | 0.018311 | 0.46234
2681.2812 | 122.406 | -0.054932 | 122.1909 | -0.1432 | -0.043885 | 0.0040866 | 0.023578 | 0.0023585 | -0.010102 | -0.0019461 | -0.052765 | 0.0040289 | 0.066841 | 0.045559 | -0.01666 | 0.027408 | -0.0040845 | -0.059509 | -0.07782 | -0.004578 | 0.032043 | 0.13733 | -0.018311 | 0.073242 | 0.43488 | 122.0856 | -0.064087 | 122.0535 | 0.14191 | 0.086975 | 0.1236 | 0.050354 | -122.2687 | -122.1588 | 0.19226 | 0.12817 | 0.036621 | 0.07782 | -0.013733 | -0.009155 | -0.10529 | -0.13733 | 0.19684 | 0.17853 | 0.14191 | 0.18768 | 0.15106 | 0.14191 | 0.036621 | 0.20599 | 122.1176 | -0.073242 | 122.1497 | -0.022888 | 122.1405 | -122.1954 | -122.2549 | 0.086975 | 122.1085 | -0.004577 | 0.48981
2682.9844 | 122.3831 | -0.064087 | 122.1771 | -0.13557 | -0.045166 | 0.002164 | 0.022296 | -0.0049047 | -0.009675 | -0.0013051 | -0.031403 | 0.0046697 | 0.065559 | 0.048123 | -0.016233 | 0.026767 | -0.0079297 | -0.07782 | -0.068665 | -0.004578 | 0 | 0.11444 | -0.041199 | 0.064087 | 0.41199 | 122.0856 | -0.086975 | 122.0398 | 0.11902 | 0.07782 | 0.1236 | 0.059509 | -122.2458 | -122.1771 | 0.17853 | 0.12817 | 0.022888 | 0.068665 | -0.036621 | -0.022888 | -0.091553 | -0.13733 | 0.18311 | 0.18768 | 0.14191 | 0.21057 | 0.16479 | 0.11902 | 0.004578 | 0.20599 | 122.1268 | -0.064087 | 122.1725 | -0.004578 | 122.1497 | -122.1817 | -122.2641 | 0.064087 | 122.1039 | -0.013733 | 0.47607
2684.7344 | 122.2916 | -0.10071 | 122.2366 | -0.12032 | -0.042176 | 0.0036594 | 0.029345 | -0.0031957 | -0.0083932 | -0.0015189 | -0.12296 | 0.0063787 | 0.062995 | 0.045773 | -0.017515 | 0.026981 | -0.0053661 | -0.13275 | -0.009155 | -0.050354 | -0.09613 | -0.036621 | -0.14648 | -0.045776 | 0.28381 | 122.1222 | -0.073242 | 121.9711 | 0 | -0.041199 | 0.027466 | 0.050354 | -122.2458 | -122.3328 | 0.064087 | 0.054932 | -0.045776 | 0.004578 | -0.09613 | 0.027466 | -0.11444 | -0.2655 | 0.10071 | 0.12817 | 0.059509 | 0.10071 | 0.032043 | 0.013733 | -0.045776 | 0.073242 | 122.0444 | 0.041199 | 122.1954 | 0.091553 | 122.2229 | -122.287 | -122.3099 | 0.004578 | 122.0718 | -0.032043 | 0.38452
2686.4844 | 122.3785 | -0.068665 | 122.1863 | -0.18135 | -0.044098 | 0.0034456 | 0.022082 | -0.0012731 | -0.009675 | -0.0051505 | -0.037506 | 0.0053107 | 0.063636 | 0.047696 | -0.015806 | 0.026126 | -0.0045117 | -0.064087 | -0.073242 | -0.004578 | 0.004578 | 0.11902 | -0.045776 | 0.045776 | 0.41657 | 122.0947 | -0.068665 | 122.0261 | 0.11444 | 0.091553 | 0.11444 | 0.064087 | -122.2595 | -122.1817 | 0.18768 | 0.11444 | 0.022889 | 0.050354 | -0.041198 | 0 | -0.091552 | -0.16022 | 0.18311 | 0.18311 | 0.16022 | 0.18311 | 0.16022 | 0.1236 | 0.009156 | 0.18311 | 122.0947 | -0.068664 | 122.1634 | -0.004577 | 122.1634 | -122.1909 | -122.2549 | 0.073243 | 122.0947 | 0.004578 | 0.48523
2688.1719 | 122.4014 | -0.059509 | 122.2046 | -0.12794 | -0.046234 | 0.0017368 | 0.024432 | -0.0021277 | -0.0094614 | -0.0036551 | -0.019196 | 0.0050971 | 0.062354 | 0.043423 | -0.017942 | 0.025485 | -0.010066 | -0.10071 | -0.041199 | -0.027466 | -0.009155 | 0.086975 | -0.022888 | 0.032043 | 0.44403 | 122.0947 | -0.059509 | 122.0398 | 0.13733 | 0.10986 | 0.13733 | 0.032043 | -122.2458 | -122.2137 | 0.14648 | 0.091552 | 0.036621 | 0.059509 | 0.004578 | 0 | -0.10986 | -0.16479 | 0.19684 | 0.19684 | 0.16937 | 0.19684 | 0.16937 | 0.11444 | 0.018311 | 0.19684 | 122.0993 | -0.013733 | 122.1542 | 0.01831 | 122.1542 | -122.2321 | -122.2641 | 0.050354 | 122.0993 | -0.041199 | 0.50354
2689.9375 | 122.3877 | -0.054932 | 122.1954 | -0.15083 | -0.043457 | 0.0030184 | 0.023791 | -0.00020513 | -0.010316 | -0.0034415 | -0.06192 | 0.0050971 | 0.065345 | 0.049405 | -0.018369 | 0.02634 | -0.0047253 | -0.068665 | -0.073242 | 0 | 0.022888 | 0.11444 | -0.041199 | 0.073242 | 0.4303 | 122.0947 | -0.07782 | 122.0444 | 0.10071 | 0.086975 | 0.13275 | 0.054932 | -122.2687 | -122.1725 | 0.16937 | 0.12817 | 0.013733 | 0.073242 | -0.041199 | -0.022888 | -0.10071 | -0.15106 | 0.15564 | 0.18768 | 0.14191 | 0.21057 | 0.16479 | 0.11444 | 0.022888 | 0.17853 | 122.1222 | -0.073242 | 122.1725 | -0.01831 | 122.1497 | -122.1954 | -122.2733 | 0.07782 | 122.0993 | -0.013733 | 0.48523
2691.6875 | 122.3236 | -0.091553 | 122.2092 | -0.15083 | -0.043457 | 0.0057956 | 0.028064 | 0.00043587 | -0.0098886 | -0.0030141 | -0.1199 | 0.0080877 | 0.061714 | 0.053891 | -0.017301 | 0.027835 | -0.0032299 | -0.082397 | -0.036621 | -0.041199 | -0.027466 | 0.059509 | -0.07782 | -0.004578 | 0.42572 | 122.1176 | -0.082397 | 122.0123 | 0.059509 | -0.009155 | 0.059509 | 0.050354 | -122.2458 | -122.2366 | 0.15106 | 0.086975 | 0.013733 | 0.036621 | -0.036621 | 0.009156 | -0.091552 | -0.19684 | 0.15106 | 0.15106 | 0.082398 | 0.14191 | 0.073242 | 0.10071 | 0.013733 | 0.14191 | 122.0947 | 0.004578 | 122.2 | 0.054932 | 122.2092 | -122.2504 | -122.2916 | 0.064087 | 122.1039 | 0.009156 | 0.51727
2693.375 | 122.3007 | -0.091553 | 122.2 | -0.1432 | -0.043457 | 0.0036594 | 0.027423 | 0.0025721 | -0.0081796 | -0.0019461 | -0.11685 | 0.0053107 | 0.065345 | 0.048764 | -0.01666 | 0.02869 | -0.0060071 | -0.082397 | -0.041199 | -0.027466 | -0.032043 | 0.050354 | -0.086975 | 0.009155 | 0.41199 | 122.1497 | -0.09613 | 121.9986 | 0.073242 | -0.013733 | 0.068665 | 0.064087 | -122.2412 | -122.2321 | 0.14191 | 0.10071 | 0.004578 | 0.036621 | -0.059509 | -0.004577 | -0.050354 | -0.20142 | 0.16479 | 0.16022 | 0.07782 | 0.16479 | 0.082397 | 0.07782 | -0.004577 | 0.16937 | 122.0947 | -0.013733 | 122.2458 | 0.050354 | 122.2412 | -122.2275 | -122.2961 | 0.05951 | 122.0901 | 0.009156 | 0.50354
2695.1406 | 122.287 | -0.11444 | 122.2412 | -0.082169 | -0.044525 | 0.00066863 | 0.023364 | -0.0042639 | -0.012452 | -0.0036551 | -0.049713 | 0.0059515 | 0.063209 | 0.048977 | -0.016874 | 0.028049 | -0.0053661 | -0.10986 | -0.045776 | -0.032043 | -0.07782 | 0.018311 | -0.086975 | 0 | 0.45319 | 122.1313 | -0.091553 | 121.9437 | 0.036621 | -0.004578 | 0.018311 | 0.082398 | -122.287 | -122.319 | 0.13275 | 0.11444 | 0.027466 | 0.032043 | -0.054932 | 0.022888 | -0.10986 | -0.29755 | 0.15106 | 0.13275 | 0.10986 | 0.10986 | 0.086975 | 0.050354 | -0.045777 | 0.12817 | 122.0352 | -0.013733 | 122.2229 | 0.068665 | 122.2458 | -122.2733 | -122.3328 | 0.036621 | 122.0581 | 0.004578 | 0.56763
2696.8281 | 122.3511 | -0.09613 | 122.2137 | -0.074539 | -0.044098 | 0.002164 | 0.026141 | 8.47e-06 | -0.010102 | -0.0013051 | -0.098541 | 0.0057379 | 0.065345 | 0.047696 | -0.015806 | 0.02634 | -0.0045117 | -0.09613 | -0.018311 | -0.027466 | -0.027466 | 0.059509 | -0.054932 | -0.009155 | 0.4715 | 122.1359 | -0.086975 | 122.0306 | 0.082397 | 0.045776 | 0.082397 | 0.068664 | -122.2321 | -122.2412 | 0.15564 | 0.086975 | 0.041198 | 0.018311 | -0.027466 | 0.009155 | -0.07782 | -0.1831 | 0.17853 | 0.17853 | 0.14191 | 0.16937 | 0.13275 | 0.086975 | 0 | 0.16937 | 122.1176 | 0.009155 | 122.2229 | 0.077819 | 122.2321 | -122.2412 | -122.3007 | 0.068664 | 122.1268 | 0 | 0.56763
2698.5781 | 122.3877 | -0.059509 | 122.2137 | -0.1432 | -0.043885 | 0.003873 | 0.024859 | -0.0031957 | -0.0094614 | -0.0045095 | -0.022247 | 0.0057379 | 0.062354 | 0.049832 | -0.015806 | 0.027621 | -0.0057935 | -0.073242 | -0.054932 | -0.004578 | 0.013733 | 0.13275 | 0.013733 | 0.07782 | 0.5722 | 122.1039 | -0.073242 | 122.0352 | 0.14648 | 0.1236 | 0.1236 | 0.054931 | -122.2687 | -122.2 | 0.19226 | 0.13733 | 0.073242 | 0.082398 | 0.018311 | -0.013733 | -0.10986 | -0.17853 | 0.20599 | 0.1831 | 0.1831 | 0.19684 | 0.19684 | 0.13733 | 0.018311 | 0.21973 | 122.1085 | -0.050354 | 122.1771 | 0.004577 | 122.1634 | -122.2183 | -122.287 | 0.073242 | 122.0947 | -0.013733 | 0.63171
2700.3281 | 122.3969 | -0.064087 | 122.2046 | -0.13557 | -0.045166 | 0.003873 | 0.025073 | -0.0025549 | -0.0092478 | -0.0057913 | -0.098541 | 0.0048833 | 0.062995 | 0.047909 | -0.015592 | 0.028049 | -0.0034435 | -0.10986 | -0.032043 | -0.032043 | -0.036621 | 0.054932 | -0.09613 | 0.009155 | 0.37994 | 122.1085 | -0.082397 | 122.0627 | 0.13275 | 0.091553 | 0.15564 | 0.032044 | -122.2366 | -122.2412 | 0.11902 | 0.073242 | -0.032043 | 0.041198 | -0.064087 | -0.01831 | -0.096131 | -0.14191 | 0.19684 | 0.21973 | 0.15564 | 0.23804 | 0.17395 | 0.086975 | -0.004578 | 0.21515 | 122.1451 | 0 | 122.1909 | 0.032044 | 122.1725 | -122.2366 | -122.287 | 0.027466 | 122.1268 | -0.045776 | 0.44403
2702.0938 | 122.3831 | -0.068665 | 122.1909 | -0.1432 | -0.044739 | 0.0013094 | 0.022937 | 0.00064947 | -0.011811 | -0.0038687 | -0.013092 | 0.0059515 | 0.062995 | 0.0509 | -0.013883 | 0.025485 | -0.0053661 | -0.07782 | -0.059509 | 0 | 0.027466 | 0.13275 | 0 | 0.068665 | 0.56763 | 122.0764 | -0.073242 | 122.0352 | 0.15106 | 0.09613 | 0.11902 | 0.068665 | -122.2504 | -122.1634 | 0.20142 | 0.13733 | 0.068665 | 0.068665 | 0 | -0.004577 | -0.11444 | -0.15564 | 0.21973 | 0.18768 | 0.16479 | 0.19226 | 0.16937 | 0.13275 | 0.027466 | 0.2243 | 122.1085 | -0.059509 | 122.1497 | 0.009156 | 122.1451 | -122.1909 | -122.2641 | 0.096131 | 122.1039 | -0.009155 | 0.63629
2703.8594 | 122.4289 | -0.068665 | 122.1817 | -0.1432 | -0.046021 | 0.0028048 | 0.025287 | -0.0031957 | -0.010316 | -0.0019461 | 0.0021667 | 0.0042425 | 0.064277 | 0.046414 | -0.01666 | 0.02634 | -0.0064343 | -0.086975 | -0.041199 | -0.004578 | 0.004578 | 0.10986 | 0.022888 | 0.086975 | 0.52185 | 122.0718 | -0.068665 | 122.0718 | 0.17853 | 0.14191 | 0.16479 | 0.064087 | -122.2229 | -122.1771 | 0.17853 | 0.15564 | 0.091553 | 0.091553 | 0.027466 | 0 | -0.10986 | -0.10986 | 0.24719 | 0.23346 | 0.21057 | 0.23346 | 0.21057 | 0.11444 | 0.009156 | 0.24719 | 122.1405 | -0.036621 | 122.1405 | 0.027466 | 122.1405 | -122.1863 | -122.2504 | 0.073243 | 122.1405 | -0.01831 | 0.59052
2705.625 | 122.4289 | -0.059509 | 122.1771 | -0.15083 | -0.045807 | 0.0030184 | 0.022723 | -0.0021277 | -0.010957 | -0.0015189 | 0.0021667 | 0.0063787 | 0.0662 | 0.049832 | -0.017729 | 0.025272 | -0.0055799 | -0.10071 | -0.041199 | -0.018311 | -0.013733 | 0.09613 | -0.018311 | 0.064087 | 0.48065 | 122.0947 | -0.082397 | 122.0581 | 0.16937 | 0.12817 | 0.14648 | 0.041198 | -122.2183 | -122.1909 | 0.15564 | 0.1236 | 0.041198 | 0.082398 | 0 | -0.022888 | -0.082397 | -0.11902 | 0.22888 | 0.20599 | 0.18768 | 0.22888 | 0.21057 | 0.11444 | 0.004578 | 0.25177 | 122.1405 | -0.022888 | 122.1771 | 0.01831 | 122.1542 | -122.1954 | -122.2595 | 0.045776 | 122.1176 | -0.041199 | 0.54016
2707.375 | 122.3831 | -0.054932 | 122.2092 | -0.17372 | -0.042816 | 0.0034456 | 0.024218 | 0.00086307 | -0.009675 | -0.0023733 | -0.064972 | 0.0040289 | 0.065986 | 0.05325 | -0.018369 | 0.025485 | -0.0042981 | -0.059509 | -0.064087 | -0.004578 | 0.018311 | 0.13275 | -0.036621 | 0.086975 | 0.44403 | 122.0764 | -0.059509 | 122.0581 | 0.12817 | 0.10071 | 0.14191 | 0.050354 | -122.2733 | -122.1909 | 0.18768 | 0.14191 | 0.018311 | 0.091553 | -0.032043 | -0.004577 | -0.13275 | -0.15106 | 0.18311 | 0.19684 | 0.15564 | 0.20142 | 0.16022 | 0.13733 | 0.022889 | 0.18768 | 122.1176 | -0.059509 | 122.1359 | -0.009155 | 122.1313 | -122.2137 | -122.2687 | 0.073243 | 122.113 | -0.004577 | 0.49896
2709.125 | 122.319 | -0.086975 | 122.2321 | -0.12032 | -0.042816 | 0.0034456 | 0.026141 | -0.0036231 | -0.0083932 | -0.0034415 | -0.12601 | 0.0046697 | 0.062141 | 0.051755 | -0.018369 | 0.028049 | -0.0066479 | -0.091553 | -0.022888 | -0.050354 | -0.032043 | 0.050354 | -0.07782 | 0.004578 | 0.43945 | 122.1451 | -0.086975 | 121.9894 | 0.059509 | -0.018311 | 0.050354 | 0.036621 | -122.2549 | -122.2641 | 0.13733 | 0.091553 | 0.009155 | 0.054932 | -0.027466 | 0 | -0.086975 | -0.24262 | 0.14648 | 0.13733 | 0.068664 | 0.13733 | 0.068664 | 0.10071 | 0.018311 | 0.14648 | 122.0764 | 0.027466 | 122.2321 | 0.064087 | 122.2321 | -122.2824 | -122.319 | 0.054932 | 122.0764 | -0.004578 | 0.52643
2710.8125 | 122.4014 | -0.050354 | 122.1909 | -0.15846 | -0.041962 | 0.0036594 | 0.024432 | -0.0029821 | -0.0098886 | -0.0010915 | -0.052765 | 0.0063787 | 0.064063 | 0.049191 | -0.015379 | 0.025699 | -0.0038709 | -0.07782 | -0.050354 | -0.009155 | 0.018311 | 0.14191 | -0.027466 | 0.082397 | 0.44403 | 122.0993 | -0.050354 | 122.0535 | 0.12817 | 0.09613 | 0.11444 | 0.041199 | -122.2412 | -122.1725 | 0.19226 | 0.13275 | 0.022888 | 0.091552 | -0.018311 | 0 | -0.091553 | -0.13733 | 0.17853 | 0.16479 | 0.14648 | 0.16479 | 0.14648 | 0.15106 | 0.027466 | 0.17853 | 122.1039 | -0.041199 | 122.1497 | 0 | 122.1497 | -122.2 | -122.2412 | 0.068665 | 122.1039 | -0.027466 | 0.49439
2712.5625 | 122.2916 | -0.09613 | 122.2183 | -0.10506 | -0.042816 | 0.0043002 | 0.02785 | 0.0017175 | -0.0090342 | -0.0025869 | -0.13821 | 0.0044561 | 0.064704 | 0.055173 | -0.017515 | 0.028049 | -0.0051525 | -0.09613 | -0.013733 | -0.050354 | -0.059509 | 0.009155 | -0.11902 | -0.032043 | 0.3479 | 122.1359 | -0.09613 | 121.9711 | 0.013733 | -0.050354 | 0.041199 | 0.045776 | -122.2321 | -122.2778 | 0.10528 | 0.064087 | -0.022889 | 0.018311 | -0.068665 | 0 | -0.082398 | -0.24719 | 0.10986 | 0.13733 | 0.045776 | 0.13733 | 0.045776 | 0.059509 | -0.009155 | 0.10986 | 122.0673 | 0.036621 | 122.2321 | 0.082397 | 122.2321 | -122.2687 | -122.3145 | 0.036621 | 122.0673 | 0 | 0.44403
2714.3125 | 122.3969 | -0.050354 | 122.2183 | -0.21187 | -0.044312 | 0.0053684 | 0.024859 | -0.0027685 | -0.0098886 | -0.0040823 | -0.037506 | 0.0059515 | 0.064704 | 0.045559 | -0.015592 | 0.027835 | -0.0057935 | -0.054932 | -0.054932 | -0.009155 | 0.041199 | 0.14191 | -0.018311 | 0.068665 | 0.43945 | 122.1039 | -0.045776 | 122.0718 | 0.16022 | 0.10529 | 0.14648 | 0.041199 | -122.2733 | -122.1771 | 0.19226 | 0.11902 | 0.032043 | 0.07782 | -0.009156 | 0.004578 | -0.11444 | -0.14648 | 0.21057 | 0.19684 | 0.15564 | 0.19226 | 0.15106 | 0.15106 | 0.050354 | 0.20599 | 122.1176 | -0.045777 | 122.1497 | -0.004578 | 122.1542 | -122.2275 | -122.2641 | 0.091553 | 122.1222 | -0.004578 | 0.48981
2716 | 122.3145 | -0.082397 | 122.2275 | -0.12032 | -0.043885 | 0.0025912 | 0.02785 | 0.0017175 | -0.01053 | -0.0047231 | -0.11075 | 0.0057379 | 0.063636 | 0.052395 | -0.017729 | 0.029544 | -0.0070751 | -0.07782 | -0.036621 | -0.041199 | -0.032043 | 0.059509 | -0.07782 | 0.009155 | 0.4303 | 122.1176 | -0.086975 | 122.0123 | 0.068665 | -0.009155 | 0.054932 | 0.041198 | -122.2641 | -122.2595 | 0.14191 | 0.091552 | 0.004577 | 0.050354 | -0.036621 | -0.004578 | -0.10986 | -0.21515 | 0.15106 | 0.13733 | 0.073242 | 0.14191 | 0.07782 | 0.10071 | 0.009156 | 0.15564 | 122.0993 | 0.004578 | 122.2046 | 0.045776 | 122.2 | -122.2687 | -122.3145 | 0.050354 | 122.0947 | 0.004577 | 0.5127
2717.75 | 122.3694 | -0.082397 | 122.2 | -0.12032 | -0.044312 | 0.001523 | 0.022937 | 0.0015039 | -0.0094614 | -0.0028005 | -0.01004 | 0.0057379 | 0.064063 | 0.042355 | -0.014524 | 0.027194 | -0.0025891 | -0.13275 | -0.050354 | -0.022888 | -0.027466 | 0.068665 | -0.045776 | 0.032043 | 0.39368 | 122.0947 | -0.064087 | 122.0169 | 0.10071 | 0.068665 | 0.09613 | 0.059509 | -122.2504 | -122.2275 | 0.15106 | 0.11444 | 0.036621 | 0.054931 | -0.022888 | 0.01831 | -0.10528 | -0.1831 | 0.18311 | 0.17853 | 0.15106 | 0.16022 | 0.13275 | 0.091553 | -0.004578 | 0.1648 | 122.081 | -0.027466 | 122.1588 | 0.032043 | 122.1771 | -122.2229 | -122.2641 | 0.054931 | 122.0993 | -0.050354 | 0.47607
2719.4531 | 122.3785 | -0.064087 | 122.1954 | -0.10506 | -0.044098 | 0.0028048 | 0.022509 | 0.0027857 | -0.0088206 | -0.0036551 | -0.049713 | 0.0053107 | 0.064277 | 0.053036 | -0.016874 | 0.025912 | -0.0077161 | -0.091553 | -0.059509 | 0.009155 | -0.009155 | 0.09613 | -0.050354 | 0.041199 | 0.39825 | 122.0673 | -0.059509 | 122.0352 | 0.10529 | 0.068665 | 0.11444 | 0.073242 | -122.2549 | -122.2046 | 0.16022 | 0.10529 | 0.013733 | 0.032044 | -0.059509 | 0.004578 | -0.12817 | -0.16022 | 0.16937 | 0.17853 | 0.13275 | 0.17395 | 0.12817 | 0.086975 | -0.01831 | 0.16479 | 122.0947 | -0.068664 | 122.1268 | 0.004578 | 122.1313 | -122.1863 | -122.2549 | 0.054932 | 122.0993 | -0.027466 | 0.46234
2721.2188 | 122.3328 | -0.10986 | 122.2412 | -0.074539 | -0.044525 | 0.00045503 | 0.024646 | -0.0023413 | -0.012666 | -0.0021597 | -0.074127 | 0.0072333 | 0.064277 | 0.051541 | -0.015379 | 0.028476 | -0.0017347 | -0.12817 | -0.004578 | -0.041199 | -0.082397 | -0.018311 | -0.10529 | -0.009155 | 0.4303 | 122.1451 | -0.086975 | 121.9849 | 0.054932 | 0.009155 | 0.050354 | 0.068664 | -122.2458 | -122.3236 | 0.091552 | 0.10071 | 0.004577 | 0.032044 | -0.064087 | 0.022888 | -0.09613 | -0.25635 | 0.16479 | 0.16022 | 0.11902 | 0.13733 | 0.09613 | 0.022888 | -0.041198 | 0.14191 | 122.0718 | 0.036621 | 122.2321 | 0.10529 | 122.2549 | -122.2824 | -122.3282 | 0.027466 | 122.0947 | -0.018311 | 0.54016
2722.9688 | 122.4289 | -0.073242 | 122.2046 | -0.082169 | -0.047089 | 0.003232 | 0.021014 | -0.0029821 | -0.01053 | -0.0049367 | 0.011322 | 0.0050971 | 0.063423 | 0.042142 | -0.016447 | 0.02634 | -0.0072889 | -0.064087 | -0.050354 | 0 | 0.041199 | 0.17395 | 0.032043 | 0.1236 | 0.62714 | 122.0673 | -0.064087 | 122.1039 | 0.19226 | 0.16022 | 0.16022 | 0.073242 | -122.2549 | -122.1634 | 0.24719 | 0.19684 | 0.10529 | 0.1236 | 0.032043 | 0.009155 | -0.13733 | -0.10071 | 0.2655 | 0.23346 | 0.23346 | 0.2243 | 0.2243 | 0.17395 | 0.041199 | 0.25635 | 122.168 | -0.050354 | 122.1313 | 0.022888 | 122.1405 | -122.2046 | -122.2687 | 0.11444 | 122.1771 | 0.009155 | 0.70038
2724.7344 | 122.374 | -0.059509 | 122.1863 | -0.17372 | -0.044525 | 0.0013094 | 0.024646 | -0.0012731 | -0.0092478 | -0.0053641 | -0.031403 | 0.0070197 | 0.062354 | 0.0462 | -0.016447 | 0.02634 | -0.0049389 | -0.091553 | -0.068665 | -0.013733 | 0 | 0.091553 | -0.041199 | 0.045776 | 0.41199 | 122.113 | -0.059509 | 122.049 | 0.11444 | 0.07782 | 0.10986 | 0.045776 | -122.2549 | -122.1863 | 0.15106 | 0.10528 | 0.01831 | 0.059509 | -0.027466 | 0 | -0.073242 | -0.13733 | 0.17395 | 0.16937 | 0.13733 | 0.16937 | 0.13733 | 0.10529 | 0.013733 | 0.17395 | 122.1085 | -0.054932 | 122.1725 | -0.009156 | 122.1725 | -122.2 | -122.2458 | 0.059509 | 122.1085 | -0.032044 | 0.4715
2726.4375 | 122.3373 | -0.10071 | 122.2412 | -0.089798 | -0.045807 | 0.0019504 | 0.024859 | -0.0034095 | -0.010743 | -0.0021597 | -0.11075 | 0.0059515 | 0.062995 | 0.052823 | -0.017942 | 0.028476 | -0.0066479 | -0.12817 | -0.009155 | -0.059509 | -0.082397 | -0.009155 | -0.091553 | -0.004578 | 0.44861 | 122.1497 | -0.11444 | 121.9803 | 0.050354 | -0.009155 | 0.045776 | 0.041199 | -122.2504 | -122.3236 | 0.091553 | 0.09613 | 0.009155 | 0.054931 | -0.032044 | -0.013733 | -0.091553 | -0.26093 | 0.15106 | 0.14648 | 0.091553 | 0.16022 | 0.10529 | 0.050354 | -0.022888 | 0.16479 | 122.0947 | 0.050354 | 122.2641 | 0.091553 | 122.2504 | -122.3007 | -122.3557 | 0.018311 | 122.081 | -0.027466 | 0.54932
2728.1875 | 122.4701 | -0.068665 | 122.2092 | -0.074539 | -0.047089 | 0.0045138 | 0.020587 | -0.0012731 | -0.010743 | -0.0036551 | -0.025299 | 0.0053107 | 0.065986 | 0.049405 | -0.018583 | 0.025912 | -0.0051525 | -0.054932 | -0.059509 | -0.004578 | 0.045776 | 0.15564 | 0.022888 | 0.13275 | 0.58594 | 122.0764 | -0.041199 | 122.0993 | 0.20142 | 0.16479 | 0.17395 | 0.064087 | -122.2687 | -122.1634 | 0.22431 | 0.20142 | 0.091553 | 0.13733 | 0.027466 | 0.027466 | -0.13275 | -0.10986 | 0.27008 | 0.24261 | 0.23346 | 0.21515 | 0.20599 | 0.16022 | 0.050354 | 0.24262 | 122.1405 | -0.054931 | 122.1176 | 0.009156 | 122.1451 | -122.2137 | -122.2504 | 0.11444 | 122.168 | 0.013733 | 0.6546
2729.9531 | 122.4518 | -0.073242 | 122.2229 | -0.12794 | -0.042389 | 0.0019504 | 0.022937 | -0.00084593 | -0.010743 | -0.0023733 | -0.019196 | 0.0063787 | 0.0662 | 0.050046 | -0.01602 | 0.027621 | -0.0064343 | -0.064087 | -0.054932 | -0.013733 | 0.036621 | 0.16022 | 0.022888 | 0.10986 | 0.59967 | 122.0718 | -0.059509 | 122.1039 | 0.19226 | 0.16022 | 0.16937 | 0.059509 | -122.2778 | -122.1863 | 0.23346 | 0.18311 | 0.09613 | 0.1236 | 0.036621 | 0.013733 | -0.15106 | -0.11902 | 0.2655 | 0.24261 | 0.23346 | 0.22888 | 0.21973 | 0.17395 | 0.050354 | 0.25177 | 122.1634 | -0.041199 | 122.1313 | 0.01831 | 122.1451 | -122.2366 | -122.2824 | 0.10986 | 122.1771 | 0.009155 | 0.67291
2731.7188 | 122.3007 | -0.09613 | 122.2412 | -0.15083 | -0.046662 | 0.0017368 | 0.02315 | 0.0059901 | -0.010743 | -0.0045095 | -0.040558 | 0.0068059 | 0.064277 | 0.0462 | -0.015379 | 0.027194 | -0.0028027 | -0.11902 | -0.027466 | -0.027466 | -0.064087 | 0 | -0.082397 | -0.004578 | 0.4715 | 122.1588 | -0.10071 | 121.9757 | 0.036621 | 0.004578 | 0.022888 | 0.068664 | -122.2687 | -122.3053 | 0.09613 | 0.091552 | 0.013733 | 0.022888 | -0.054931 | -0.004578 | -0.082398 | -0.2655 | 0.13275 | 0.11902 | 0.10071 | 0.1236 | 0.10529 | 0.027466 | -0.036621 | 0.13733 | 122.0764 | 0 | 122.2595 | 0.068664 | 122.2549 | -122.2687 | -122.3419 | 0.032043 | 122.0718 | -0.022889 | 0.56763
2733.4062 | 122.4197 | -0.068665 | 122.1817 | -0.15846 | -0.045807 | 0.00024143 | 0.022296 | -0.0070409 | -0.01053 | -0.0042959 | -0.016144 | 0.0031745 | 0.064063 | 0.047696 | -0.016447 | 0.026981 | -0.0019483 | -0.09613 | -0.064087 | -0.009155 | -0.009155 | 0.086975 | -0.018311 | 0.07782 | 0.50354 | 122.1039 | -0.064087 | 122.0764 | 0.15564 | 0.13733 | 0.13733 | 0.05951 | -122.2458 | -122.1909 | 0.15564 | 0.14649 | 0.050354 | 0.086975 | -0.009156 | 0.004578 | -0.07782 | -0.10529 | 0.22431 | 0.20599 | 0.20599 | 0.20142 | 0.20142 | 0.09613 | 0 | 0.21973 | 122.1405 | -0.054932 | 122.168 | 0.004578 | 122.1725 | -122.1909 | -122.2458 | 0.05951 | 122.1451 | -0.027465 | 0.5722
2735.1562 | 122.3053 | -0.10986 | 122.2458 | -0.06691 | -0.046662 | 0.0040866 | 0.026355 | -0.0038367 | -0.012666 | -0.0055777 | -0.10159 | 0.0074469 | 0.062141 | 0.048337 | -0.01666 | 0.025272 | -0.0036573 | -0.13733 | -0.018311 | -0.054932 | -0.091553 | -0.004578 | -0.09613 | -0.013733 | 0.44861 | 122.1451 | -0.09613 | 121.962 | 0.036621 | -0.009155 | 0.022888 | 0.054931 | -122.2641 | -122.3373 | 0.10529 | 0.09613 | 0.013733 | 0.041199 | -0.041198 | 0.013733 | -0.10071 | -0.28381 | 0.14648 | 0.13275 | 0.10071 | 0.11902 | 0.086975 | 0.050354 | -0.036621 | 0.13275 | 122.0581 | 0.036621 | 122.2412 | 0.091552 | 122.2549 | -122.3007 | -122.3419 | 0.01831 | 122.0718 | -0.027466 | 0.55847
2736.9062 | 122.3282 | -0.09613 | 122.2595 | -0.051651 | -0.046875 | 0.0028048 | 0.023578 | 0.0012903 | -0.01053 | -0.0057913 | -0.083283 | 0.0053107 | 0.063209 | 0.047055 | -0.017301 | 0.026126 | -0.0062207 | -0.1236 | -0.009155 | -0.064087 | -0.082397 | -0.009155 | -0.11444 | -0.022888 | 0.44861 | 122.1405 | -0.10529 | 121.9757 | 0.050354 | -0.013733 | 0.032043 | 0.032043 | -122.2687 | -122.3419 | 0.086975 | 0.073242 | -0.018311 | 0.041199 | -0.050354 | -0.009156 | -0.11902 | -0.28381 | 0.14648 | 0.12817 | 0.082397 | 0.13733 | 0.091553 | 0.054932 | -0.01831 | 0.15564 | 122.081 | 0.054932 | 122.2458 | 0.086975 | 122.2366 | -122.3236 | -122.3648 | 0.013733 | 122.0718 | -0.027466 | 0.54474
2738.6562 | 122.3465 | -0.10071 | 122.2183 | -0.097427 | -0.042816 | 0.0030184 | 0.024005 | -0.0049047 | -0.0088206 | -0.0045095 | -0.083283 | 0.0044561 | 0.064277 | 0.047268 | -0.014097 | 0.028903 | -0.0072889 | -0.10071 | -0.009155 | -0.032043 | -0.059509 | 0.009155 | -0.086975 | -0.009155 | 0.46692 | 122.1542 | -0.082397 | 122.0032 | 0.082397 | 0.018311 | 0.073242 | 0.068665 | -122.2275 | -122.2778 | 0.10986 | 0.091553 | 0.013733 | 0.022888 | -0.054932 | 0.018311 | -0.064087 | -0.21515 | 0.18311 | 0.17395 | 0.11902 | 0.15564 | 0.10071 | 0.041198 | -0.027466 | 0.16479 | 122.0856 | 0.022888 | 122.2366 | 0.091553 | 122.2549 | -122.2504 | -122.3007 | 0.041199 | 122.1039 | 0 | 0.56763
2740.3438 | 122.3602 | -0.086975 | 122.1863 | -0.21187 | -0.042816 | 0.0034456 | 0.024859 | -0.00020513 | -0.010957 | -0.0021597 | -0.11075 | 0.0057379 | 0.065132 | 0.049618 | -0.015379 | 0.028049 | -0.0032299 | -0.11902 | -0.009155 | -0.032043 | -0.07782 | 0.004578 | -0.13275 | -0.027466 | 0.32044 | 122.1222 | -0.086975 | 122.0261 | 0.068665 | 0.018311 | 0.082397 | 0.054932 | -122.1954 | -122.2641 | 0.091553 | 0.059509 | -0.045776 | 0.004577 | -0.10071 | 0 | -0.064087 | -0.16022 | 0.15564 | 0.16937 | 0.10529 | 0.16937 | 0.10529 | 0.036621 | -0.045777 | 0.15564 | 122.113 | 0.022888 | 122.2092 | 0.07782 | 122.2092 | -122.2183 | -122.2733 | 0.009155 | 122.113 | -0.032044 | 0.40741
2742.1094 | 122.4472 | -0.054932 | 122.1771 | -0.11269 | -0.047089 | 2.7834e-05 | 0.022509 | -0.0010595 | -0.011811 | -0.0053641 | -0.019196 | 0.0050971 | 0.063636 | 0.046628 | -0.015592 | 0.02634 | -0.0057935 | -0.086975 | -0.073242 | -0.032043 | 0.027466 | 0.14191 | 0.018311 | 0.10529 | 0.56763 | 122.0993 | -0.068665 | 122.0901 | 0.17853 | 0.13733 | 0.16022 | 0.022889 | -122.2504 | -122.1497 | 0.19684 | 0.16022 | 0.073243 | 0.13733 | 0.050354 | -0.013733 | -0.07782 | -0.086975 | 0.23346 | 0.21515 | 0.19226 | 0.22888 | 0.20599 | 0.17395 | 0.059509 | 0.24719 | 122.1588 | -0.041199 | 122.168 | -0.01831 | 122.1542 | -122.2092 | -122.2458 | 0.082398 | 122.1451 | -0.032043 | 0.62256
2743.8594 | 122.3877 | -0.064087 | 122.2092 | -0.22713 | -0.042816 | 0.0057956 | 0.024218 | -0.00063233 | -0.0075388 | -0.0049367 | -0.055817 | 0.0050971 | 0.063636 | 0.04385 | -0.017301 | 0.02634 | -0.0030163 | -0.059509 | -0.07782 | 0.004578 | 0.050354 | 0.14191 | -0.027466 | 0.068665 | 0.42572 | 122.0856 | -0.064087 | 122.0718 | 0.13733 | 0.11444 | 0.14648 | 0.068665 | -122.287 | -122.1588 | 0.20599 | 0.13275 | 0.036621 | 0.064087 | -0.032044 | 0 | -0.1236 | -0.13733 | 0.20142 | 0.21057 | 0.17853 | 0.21057 | 0.17853 | 0.13733 | 0.045776 | 0.20142 | 122.1359 | -0.082398 | 122.1497 | -0.013733 | 122.1497 | -122.2046 | -122.2733 | 0.11444 | 122.1359 | 0.004578 | 0.48981
2745.625 | 122.3419 | -0.091553 | 122.2595 | -0.11269 | -0.046234 | 0.0017368 | 0.025714 | -0.0053321 | -0.011384 | -0.0055777 | -0.086334 | 0.0057379 | 0.0662 | 0.045987 | -0.016874 | 0.027194 | -0.0051525 | -0.12817 | -0.018311 | -0.032043 | -0.068665 | 0.009155 | -0.082397 | -0.022888 | 0.45319 | 122.1405 | -0.082397 | 121.9894 | 0.073242 | 0.004578 | 0.054932 | 0.05951 | -122.2778 | -122.3282 | 0.10071 | 0.068665 | 0.009156 | 0.009155 | -0.050354 | 0.009156 | -0.11902 | -0.27008 | 0.16479 | 0.14649 | 0.096131 | 0.13733 | 0.086975 | 0.041198 | -0.036622 | 0.15564 | 122.0718 | 0.013732 | 122.2229 | 0.073242 | 122.2321 | -122.2916 | -122.3419 | 0.022888 | 122.081 | -0.036621 | 0.54474
2747.3125 | 122.319 | -0.10529 | 122.2595 | -0.13557 | -0.043885 | 0.0023776 | 0.027423 | 0.0025721 | -0.0083932 | -0.0019461 | -0.1199 | 0.0068059 | 0.064277 | 0.053891 | -0.017088 | 0.026981 | -0.0089977 | -0.086975 | -0.036621 | -0.027466 | -0.036621 | 0.059509 | -0.07782 | 0 | 0.4303 | 122.1451 | -0.091553 | 122.0078 | 0.054932 | -0.009155 | 0.054932 | 0.07782 | -122.2961 | -122.2961 | 0.16479 | 0.10529 | 0.027466 | 0.027466 | -0.050354 | 0.013733 | -0.11444 | -0.25177 | 0.16022 | 0.16022 | 0.096131 | 0.14649 | 0.082398 | 0.086975 | -0.009155 | 0.14649 | 122.0993 | -0.009155 | 122.2366 | 0.068665 | 122.2504 | -122.287 | -122.3511 | 0.068665 | 122.113 | 0.018311 | 0.53558
2749.0781 | 122.3511 | -0.086975 | 122.2183 | -0.15083 | -0.045807 | 0.0013094 | 0.027209 | -0.00063233 | -0.008607 | -0.0015189 | -0.098541 | 0.0042425 | 0.06385 | 0.054318 | -0.016874 | 0.028049 | -0.0028027 | -0.082397 | -0.009155 | -0.032043 | -0.036621 | 0.054932 | -0.068665 | 0.004578 | 0.48523 | 122.1176 | -0.086975 | 122.0261 | 0.10071 | 0.036621 | 0.09613 | 0.054932 | -122.2275 | -122.2549 | 0.14191 | 0.091553 | 0.01831 | 0.036621 | -0.036622 | 0 | -0.10071 | -0.19226 | 0.18768 | 0.1831 | 0.1236 | 0.1831 | 0.1236 | 0.086975 | -0.004578 | 0.18768 | 122.113 | 0.022888 | 122.2046 | 0.07782 | 122.2046 | -122.2504 | -122.3053 | 0.050354 | 122.113 | 0.004578 | 0.5722
2750.8438 | 122.438 | -0.045776 | 122.1909 | -0.17372 | -0.042816 | 0.0045138 | 0.022082 | 0.00086307 | -0.0092478 | -0.0042959 | -0.052765 | 0.0055243 | 0.063209 | 0.047268 | -0.017088 | 0.027835 | 0.0031787 | -0.045776 | -0.073242 | -0.009155 | 0.041199 | 0.15106 | -0.022888 | 0.073242 | 0.43945 | 122.0947 | -0.064087 | 122.0947 | 0.16479 | 0.11902 | 0.15106 | 0.036621 | -122.2641 | -122.1497 | 0.19684 | 0.11902 | 0.022888 | 0.082397 | -0.013733 | -0.018311 | -0.09613 | -0.09613 | 0.21057 | 0.19684 | 0.16479 | 0.21515 | 0.18311 | 0.16022 | 0.050354 | 0.22888 | 122.1588 | -0.064087 | 122.1588 | -0.027466 | 122.1405 | -122.2 | -122.2549 | 0.086975 | 122.1405 | 0 | 0.48523
2752.5312 | 122.3694 | -0.073242 | 122.2046 | -0.12032 | -0.043457 | 0.002164 | 0.023791 | -0.0021277 | -0.0083932 | -0.0040823 | -0.013092 | 0.0048833 | 0.062354 | 0.04855 | -0.015592 | 0.027408 | -0.0057935 | -0.11444 | -0.050354 | -0.027466 | -0.022888 | 0.073242 | -0.045776 | 0.036621 | 0.39368 | 122.1359 | -0.073242 | 122.0215 | 0.091553 | 0.064087 | 0.09613 | 0.045776 | -122.2549 | -122.2275 | 0.14648 | 0.10986 | 0.027466 | 0.064087 | -0.01831 | 0 | -0.068665 | -0.18311 | 0.16479 | 0.16937 | 0.13733 | 0.16937 | 0.13733 | 0.10071 | 0.004578 | 0.16479 | 122.0947 | -0.022888 | 122.2092 | 0.022888 | 122.2092 | -122.2321 | -122.2778 | 0.050354 | 122.0947 | -0.041199 | 0.46692
2754.2812 | 122.3145 | -0.09613 | 122.2275 | -0.15083 | -0.044098 | 0.0017368 | 0.029986 | -0.0025549 | -0.0088206 | -0.0036551 | -0.11075 | 0.0065923 | 0.065132 | 0.0509 | -0.016233 | 0.027621 | -0.0025891 | -0.14648 | -0.018311 | -0.059509 | -0.07782 | -0.036621 | -0.14648 | -0.054932 | 0.29755 | 122.1313 | -0.10071 | 121.962 | -0.009155 | -0.050354 | 0.041199 | 0.036621 | -122.2458 | -122.3053 | 0.059509 | 0.041198 | -0.050354 | 0.004577 | -0.086975 | -0.004578 | -0.09613 | -0.2655 | 0.086975 | 0.13733 | 0.045776 | 0.14191 | 0.050354 | 0.022888 | -0.018311 | 0.091553 | 122.0627 | 0.041198 | 122.2321 | 0.077819 | 122.2275 | -122.287 | -122.3282 | 0.01831 | 122.0581 | -0.050354 | 0.39368
2755.9844 | 122.3007 | -0.10071 | 122.2366 | -0.15846 | -0.042603 | 0.003232 | 0.028064 | -0.00041873 | -0.010102 | -0.0021597 | -0.10464 | 0.0076605 | 0.06385 | 0.051541 | -0.014524 | 0.027835 | -0.0042981 | -0.07782 | -0.032043 | -0.036621 | -0.045776 | 0.050354 | -0.091553 | -0.022888 | 0.40741 | 122.1359 | -0.086975 | 121.9666 | 0.032043 | -0.032043 | 0.045776 | 0.064087 | -122.2687 | -122.2824 | 0.15106 | 0.07782 | 0.009155 | 0.013733 | -0.054932 | 0.013733 | -0.10071 | -0.27008 | 0.13275 | 0.14648 | 0.068665 | 0.13275 | 0.054932 | 0.086975 | -0.009155 | 0.11902 | 122.0535 | 0.004578 | 122.2229 | 0.068665 | 122.2366 | -122.2733 | -122.3236 | 0.054932 | 122.0673 | 0.022888 | 0.50812
2757.7344 | 122.3099 | -0.1236 | 122.2 | -0.11269 | -0.044739 | 0.0023776 | 0.023364 | -0.0036231 | -0.0092478 | -0.0015189 | -0.040558 | 0.0072333 | 0.064704 | 0.045132 | -0.016233 | 0.02399 | -0.0045117 | -0.13275 | -0.009155 | -0.022888 | -0.086975 | 0.018311 | -0.086975 | 0 | 0.4715 | 122.1268 | -0.07782 | 121.9528 | 0.032043 | -0.009155 | 0.009155 | 0.10071 | -122.2092 | -122.287 | 0.14191 | 0.1236 | 0.036621 | 0.022888 | -0.064087 | 0.045776 | -0.073242 | -0.24719 | 0.15564 | 0.13275 | 0.11444 | 0.086975 | 0.068665 | 0.041199 | -0.064087 | 0.10986 | 122.0306 | 0.013733 | 122.2046 | 0.11444 | 122.2504 | -122.2229 | -122.2778 | 0.036621 | 122.0764 | -0.009155 | 0.59509
2759.4219 | 122.4197 | -0.059509 | 122.2092 | -0.13557 | -0.045594 | 0.00066863 | 0.024218 | -0.0023413 | -0.011384 | -0.0036551 | -0.0069885 | 0.0050971 | 0.064491 | 0.047482 | -0.016447 | 0.024844 | -0.0030163 | -0.064087 | -0.07782 | -0.018311 | 0.050354 | 0.1831 | 0.036621 | 0.10071 | 0.59509 | 122.0673 | -0.07782 | 122.0901 | 0.1831 | 0.15564 | 0.16022 | 0.041198 | -122.287 | -122.1588 | 0.24261 | 0.16022 | 0.09613 | 0.11902 | 0.054932 | -0.018311 | -0.14191 | -0.11902 | 0.24261 | 0.21973 | 0.21515 | 0.23804 | 0.23346 | 0.20142 | 0.068665 | 0.26092 | 122.168 | -0.059509 | 122.1451 | -0.018311 | 122.1268 | -122.2275 | -122.287 | 0.10986 | 122.1497 | -0.004578 | 0.6546
2761.1875 | 122.3236 | -0.086975 | 122.2229 | -0.13557 | -0.045166 | 2.7834e-05 | 0.026568 | -0.0014867 | -0.010957 | -0.0015189 | -0.09549 | 0.0065923 | 0.06385 | 0.048977 | -0.01602 | 0.028476 | -0.00088011 | -0.086975 | -0.018311 | -0.027466 | -0.045776 | 0.050354 | -0.059509 | 0.022888 | 0.44403 | 122.1588 | -0.09613 | 122.0123 | 0.068665 | 0.004578 | 0.068665 | 0.059509 | -122.2412 | -122.2687 | 0.13733 | 0.10986 | 0.027466 | 0.050354 | -0.032043 | -0.009155 | -0.064087 | -0.21057 | 0.15564 | 0.15564 | 0.091553 | 0.16479 | 0.10071 | 0.07782 | -0.01831 | 0.16479 | 122.1085 | 0.009155 | 122.2549 | 0.068664 | 122.2458 | -122.2504 | -122.319 | 0.041199 | 122.0993 | 0 | 0.53101
2762.9375 | 122.4243 | -0.054932 | 122.2092 | -0.17372 | -0.041535 | 0.0040866 | 0.024646 | -0.0010595 | -0.0083932 | -0.0040823 | -0.037506 | 0.0040289 | 0.064063 | 0.045559 | -0.017515 | 0.025272 | -0.0079297 | -0.050354 | -0.064087 | -0.009155 | 0.036621 | 0.12817 | -0.013733 | 0.073242 | 0.45319 | 122.1176 | -0.059509 | 122.0764 | 0.14648 | 0.11902 | 0.15106 | 0.045777 | -122.2733 | -122.1725 | 0.18311 | 0.12817 | 0.041199 | 0.082397 | -0.004578 | -0.004577 | -0.091552 | -0.13275 | 0.20142 | 0.20599 | 0.17395 | 0.21057 | 0.17853 | 0.13733 | 0.045776 | 0.20599 | 122.1359 | -0.054932 | 122.1771 | -0.009155 | 122.1725 | -122.2183 | -122.2687 | 0.091553 | 122.1313 | 0.004578 | 0.50812
2764.6875 | 122.4289 | -0.054932 | 122.1909 | -0.15083 | -0.040894 | 0.0062228 | 0.026141 | 0.00086307 | -0.006898 | -0.0028005 | -0.064972 | 0.0042425 | 0.062782 | 0.045773 | -0.016447 | 0.027194 | -0.0049389 | -0.041199 | -0.068665 | 0 | 0.041199 | 0.14648 | -0.018311 | 0.068665 | 0.44861 | 122.0856 | -0.059509 | 122.1039 | 0.16479 | 0.1236 | 0.16479 | 0.054932 | -122.2595 | -122.1497 | 0.20142 | 0.1236 | 0.036621 | 0.068665 | -0.018311 | -0.004577 | -0.10529 | -0.086975 | 0.21973 | 0.21973 | 0.17853 | 0.2243 | 0.1831 | 0.14648 | 0.041199 | 0.2243 | 122.1634 | -0.068665 | 122.1451 | -0.013733 | 122.1405 | -122.1909 | -122.2504 | 0.096131 | 122.1588 | 0.013733 | 0.50354
2766.375 | 122.438 | -0.064087 | 122.1954 | -0.074539 | -0.047943 | 0.003232 | 0.023791 | -0.0055457 | -0.0098886 | -0.0030141 | -0.019196 | 0.0059515 | 0.064918 | 0.042355 | -0.018583 | 0.025272 | -0.0049389 | -0.10071 | -0.054932 | -0.013733 | 0.009155 | 0.11902 | 0.004578 | 0.073242 | 0.52185 | 122.0947 | -0.073242 | 122.0856 | 0.1831 | 0.14191 | 0.16022 | 0.050354 | -122.2504 | -122.1863 | 0.18311 | 0.13733 | 0.068665 | 0.086975 | 0.018311 | -0.009155 | -0.10071 | -0.10986 | 0.24719 | 0.2243 | 0.20599 | 0.23346 | 0.21515 | 0.13275 | 0.022888 | 0.25635 | 122.1588 | -0.041199 | 122.168 | 0.009155 | 122.1588 | -122.2092 | -122.2687 | 0.073242 | 122.1497 | -0.036621 | 0.58594
2768.125 | 122.406 | -0.059509 | 122.2046 | -0.18135 | -0.047089 | 0.0017368 | 0.023364 | 0.0021447 | -0.0083932 | -0.0036551 | -0.0039367 | 0.0040289 | 0.067481 | 0.04385 | -0.017729 | 0.026126 | -0.0045117 | -0.10986 | -0.036621 | -0.022888 | -0.013733 | 0.073242 | -0.027466 | 0.059509 | 0.44861 | 122.1085 | -0.064087 | 122.0673 | 0.13733 | 0.10986 | 0.12817 | 0.036621 | -122.2412 | -122.2183 | 0.13275 | 0.11902 | 0.032043 | 0.082397 | -0.004578 | -0.004578 | -0.096131 | -0.13733 | 0.19684 | 0.18768 | 0.16937 | 0.19226 | 0.17395 | 0.09613 | 0.009155 | 0.20142 | 122.1313 | -0.013733 | 122.1725 | 0.022888 | 122.168 | -122.2275 | -122.2687 | 0.045776 | 122.1268 | -0.050354 | 0.50812
2769.8125 | 122.3511 | -0.091553 | 122.2504 | -0.082169 | -0.043457 | 0.0030184 | 0.027423 | -0.0029821 | -0.010957 | -0.0047231 | -0.09549 | 0.0050971 | 0.066413 | 0.054959 | -0.017088 | 0.027408 | -0.0038709 | -0.11444 | -0.018311 | -0.045776 | -0.068665 | 0 | -0.086975 | -0.018311 | 0.45319 | 122.1359 | -0.091553 | 121.994 | 0.073242 | 0.022888 | 0.068665 | 0.045777 | -122.2687 | -122.319 | 0.091553 | 0.073242 | 0.004578 | 0.027465 | -0.041199 | 0 | -0.11444 | -0.25635 | 0.16479 | 0.16022 | 0.11444 | 0.16022 | 0.11444 | 0.045776 | -0.022889 | 0.16479 | 122.0856 | 0.027465 | 122.2275 | 0.073242 | 122.2275 | -122.2961 | -122.3419 | 0.022888 | 122.0856 | -0.022888 | 0.54474
2771.5625 | 122.3694 | -0.068665 | 122.2137 | -0.1432 | -0.043671 | 0.0025912 | 0.027636 | -0.00084593 | -0.010957 | -0.0010915 | -0.10159 | 0.0055243 | 0.065772 | 0.052609 | -0.016447 | 0.028476 | -0.0040845 | -0.12817 | -0.013733 | -0.045776 | -0.07782 | 0.013733 | -0.1236 | -0.018311 | 0.33417 | 122.1268 | -0.09613 | 122.0306 | 0.07782 | 0.032043 | 0.07782 | 0.022889 | -122.2275 | -122.2916 | 0.082398 | 0.050354 | -0.054931 | 0.027465 | -0.07782 | -0.027465 | -0.086975 | -0.1831 | 0.14649 | 0.14649 | 0.10071 | 0.17395 | 0.12817 | 0.059509 | -0.032044 | 0.17395 | 122.1268 | 0.032043 | 122.2229 | 0.054932 | 122.1954 | -122.2595 | -122.3099 | -0.009155 | 122.0993 | -0.059509 | 0.40283
2773.25 | 122.3785 | -0.073242 | 122.2092 | -0.10506 | -0.042176 | 0.003873 | 0.024005 | 0.0015039 | -0.0094614 | -0.0030141 | -0.031403 | 0.0055243 | 0.064918 | 0.042569 | -0.014097 | 0.027408 | -0.0030163 | -0.07782 | -0.045776 | 0 | 0.022888 | 0.13733 | -0.045776 | 0.064087 | 0.43488 | 122.1222 | -0.054932 | 122.0535 | 0.11444 | 0.082397 | 0.10986 | 0.073242 | -122.2549 | -122.1863 | 0.21057 | 0.13733 | 0.027466 | 0.064087 | -0.045776 | 0.01831 | -0.086975 | -0.15564 | 0.18768 | 0.18311 | 0.15564 | 0.16479 | 0.13733 | 0.13733 | 0.022888 | 0.16937 | 122.1085 | -0.045776 | 122.1771 | 0.027466 | 122.1954 | -122.2092 | -122.2641 | 0.09613 | 122.1268 | -0.004578 | 0.50812
2775 | 122.406 | -0.064087 | 122.1863 | -0.21187 | -0.042389 | 0.0036594 | 0.025287 | -0.0012731 | -0.0083932 | -0.0045095 | -0.016144 | 0.0063787 | 0.063636 | 0.045559 | -0.016233 | 0.026553 | -0.0049389 | -0.059509 | -0.050354 | -0.004578 | 0.041199 | 0.15564 | -0.018311 | 0.07782 | 0.46234 | 122.1176 | -0.059509 | 122.0764 | 0.13733 | 0.10071 | 0.15564 | 0.059509 | -122.2366 | -122.1451 | 0.21973 | 0.14191 | 0.045776 | 0.082398 | -0.013733 | 0.004578 | -0.068664 | -0.10986 | 0.20142 | 0.21973 | 0.1648 | 0.21515 | 0.16022 | 0.16022 | 0.045777 | 0.19684 | 122.1359 | -0.045776 | 122.1771 | 0.013733 | 122.1817 | -122.1909 | -122.2458 | 0.10529 | 122.1405 | 0.004578 | 0.52643
2776.7656 | 122.4243 | -0.068665 | 122.1909 | -0.11269 | -0.04538 | 0.0013094 | 0.021869 | -0.0042639 | -0.0088206 | -0.0028005 | -0.031403 | 0.0057379 | 0.064918 | 0.051968 | -0.015379 | 0.027194 | -0.0062207 | -0.10071 | -0.041199 | -0.018311 | -0.027466 | 0.07782 | -0.045776 | 0.064087 | 0.46234 | 122.0947 | -0.086975 | 122.0398 | 0.13733 | 0.10071 | 0.12817 | 0.050354 | -122.2321 | -122.2183 | 0.14649 | 0.13275 | 0.022889 | 0.082398 | -0.027465 | -0.01831 | -0.09613 | -0.15106 | 0.20599 | 0.19684 | 0.16937 | 0.21515 | 0.18768 | 0.096131 | -0.009155 | 0.2243 | 122.1268 | -0.022888 | 122.1817 | 0.027466 | 122.1634 | -122.2092 | -122.2778 | 0.041199 | 122.1085 | -0.032043 | 0.53101
2778.4531 | 122.3785 | -0.054932 | 122.2046 | -0.082169 | -0.04538 | 0.0034456 | 0.024432 | -0.0034095 | -0.0083932 | -0.0034415 | -0.031403 | 0.0068059 | 0.065986 | 0.049405 | -0.017729 | 0.026767 | -0.0049389 | -0.09613 | -0.050354 | 0 | -0.018311 | 0.054932 | -0.059509 | 0.032043 | 0.41657 | 122.1176 | -0.068665 | 122.0444 | 0.10529 | 0.054932 | 0.10529 | 0.054932 | -122.2549 | -122.2229 | 0.10986 | 0.086975 | -0.004577 | 0.032043 | -0.059509 | -0.013733 | -0.086975 | -0.16022 | 0.16022 | 0.16022 | 0.10986 | 0.17395 | 0.1236 | 0.054932 | -0.018311 | 0.17395 | 122.113 | -0.050354 | 122.1863 | 0.004578 | 122.1725 | -122.2046 | -122.2733 | 0.036621 | 122.0993 | -0.041198 | 0.4715
2780.2031 | 122.3877 | -0.068665 | 122.2092 | -0.15846 | -0.045807 | 0.0025912 | 0.024432 | -0.0017005 | -0.0098886 | -0.0042959 | -0.037506 | 0.0074469 | 0.064277 | 0.047268 | -0.017729 | 0.027408 | -0.0070751 | -0.11444 | -0.045776 | -0.004578 | -0.027466 | 0.059509 | -0.064087 | 0.036621 | 0.41657 | 122.0901 | -0.073242 | 122.0398 | 0.11902 | 0.07782 | 0.10986 | 0.064087 | -122.2549 | -122.2366 | 0.12817 | 0.10529 | 0.004578 | 0.041199 | -0.059509 | -0.004577 | -0.11902 | -0.16937 | 0.18768 | 0.17853 | 0.14649 | 0.18311 | 0.15106 | 0.064087 | -0.022888 | 0.19226 | 122.113 | -0.041198 | 122.1634 | 0.022889 | 122.1588 | -122.2137 | -122.2824 | 0.041199 | 122.1085 | -0.045776 | 0.48523
2781.9688 | 122.3602 | -0.086975 | 122.2137 | -0.16609 | -0.044525 | 0.00665 | 0.026141 | 0.00022207 | -0.012025 | -0.0038687 | -0.12296 | 0.0053107 | 0.065986 | 0.047909 | -0.018583 | 0.026981 | -0.0081433 | -0.07782 | -0.013733 | -0.041199 | -0.013733 | 0.068665 | -0.07782 | 0.013733 | 0.49439 | 122.1359 | -0.082397 | 122.0261 | 0.086975 | 0.032043 | 0.086975 | 0.045776 | -122.2275 | -122.2275 | 0.15564 | 0.10071 | 0.009155 | 0.054932 | -0.036621 | 0.004578 | -0.07782 | -0.18768 | 0.17395 | 0.17395 | 0.11902 | 0.16937 | 0.11444 | 0.10986 | 0.027466 | 0.16937 | 122.1085 | 0.027466 | 122.2183 | 0.073242 | 122.2229 | -122.2549 | -122.2961 | 0.073242 | 122.113 | 0.009155 | 0.58136
2783.7344 | 122.4289 | -0.050354 | 122.2092 | -0.21187 | -0.041321 | 0.0045138 | 0.026568 | 0.0012903 | -0.007966 | 0.00019006 | -0.071076 | 0.0048833 | 0.060645 | 0.051327 | -0.017088 | 0.028049 | -0.0062207 | -0.050354 | -0.064087 | 0.004578 | 0.054932 | 0.14648 | -0.018311 | 0.064087 | 0.43488 | 122.113 | -0.054932 | 122.0947 | 0.15106 | 0.11444 | 0.14191 | 0.054932 | -122.2733 | -122.1542 | 0.19684 | 0.11444 | 0.032043 | 0.059509 | -0.022889 | -0.004578 | -0.09613 | -0.11444 | 0.20142 | 0.19226 | 0.16479 | 0.19684 | 0.16937 | 0.14191 | 0.050354 | 0.20599 | 122.1497 | -0.068665 | 122.168 | -0.013733 | 122.1634 | -122.2046 | -122.2641 | 0.10529 | 122.1451 | 0 | 0.48523
2785.4219 | 122.3328 | -0.07782 | 122.2366 | -0.16609 | -0.04303 | 0.0025912 | 0.027636 | -0.00020513 | -0.0081796 | -0.0030141 | -0.098541 | 0.0072333 | 0.065345 | 0.045132 | -0.015592 | 0.029117 | -0.0081433 | -0.1236 | -0.004578 | -0.050354 | -0.086975 | 0 | -0.14191 | -0.022888 | 0.32501 | 122.1451 | -0.086975 | 122.0169 | 0.054932 | -0.013733 | 0.045776 | 0.027466 | -122.2412 | -122.3236 | 0.07782 | 0.054932 | -0.064087 | 0.027466 | -0.091553 | -0.009155 | -0.091552 | -0.21973 | 0.13275 | 0.1236 | 0.064087 | 0.13275 | 0.073242 | 0.050354 | -0.036621 | 0.14191 | 122.1039 | 0.045776 | 122.2321 | 0.073242 | 122.2229 | -122.287 | -122.3236 | -0.009155 | 122.0947 | -0.045776 | 0.40283
2787.1875 | 122.3145 | -0.1236 | 122.2275 | -0.089798 | -0.044525 | 0.0028048 | 0.023578 | 0.00022207 | -0.010743 | 0.00019006 | -0.058869 | 0.0055243 | 0.063423 | 0.048123 | -0.014311 | 0.026553 | -0.0070751 | -0.11902 | -0.036621 | -0.027466 | -0.059509 | 0.045776 | -0.082397 | -0.009155 | 0.46234 | 122.1359 | -0.086975 | 121.962 | 0.054932 | 0.009155 | 0.022888 | 0.09613 | -122.2641 | -122.287 | 0.16937 | 0.11444 | 0.041199 | 0.018311 | -0.054931 | 0.036621 | -0.091553 | -0.2655 | 0.17853 | 0.14648 | 0.13275 | 0.10986 | 0.09613 | 0.073242 | -0.032043 | 0.14191 | 122.0489 | -0.009155 | 122.2229 | 0.086975 | 122.2595 | -122.2549 | -122.3145 | 0.064087 | 122.0856 | 0.004577 | 0.58594
2788.875 | 122.3236 | -0.10071 | 122.2137 | -0.097427 | -0.044525 | 0.0051546 | 0.024432 | -0.0023413 | -0.0094614 | -0.0051505 | -0.11075 | 0.0048833 | 0.062995 | 0.046414 | -0.015806 | 0.026767 | -0.0062207 | -0.082397 | -0.018311 | -0.041199 | -0.018311 | 0.054932 | -0.073242 | 0.013733 | 0.45776 | 122.1405 | -0.07782 | 122.0215 | 0.059509 | 0.013733 | 0.059509 | 0.059509 | -122.2321 | -122.2321 | 0.15564 | 0.11444 | 0.027466 | 0.054932 | -0.032043 | 0.022888 | -0.073242 | -0.19226 | 0.16022 | 0.16022 | 0.11444 | 0.13733 | 0.091553 | 0.096131 | 0.022888 | 0.13733 | 122.0993 | 0.022888 | 122.2183 | 0.082397 | 122.2412 | -122.2549 | -122.2916 | 0.082397 | 122.1222 | 0.018311 | 0.55847
2790.625 | 122.3923 | -0.059509 | 122.2137 | -0.13557 | -0.043671 | 0.0040866 | 0.028277 | 0.00064947 | -0.0092478 | -0.0049367 | -0.086334 | 0.0065923 | 0.064063 | 0.051541 | -0.017729 | 0.02869 | -0.0038709 | -0.1236 | -0.004578 | -0.036621 | -0.054932 | 0.036621 | -0.10986 | -0.004578 | 0.34332 | 122.1405 | -0.073242 | 122.0764 | 0.10986 | 0.059509 | 0.1236 | 0.022888 | -122.2183 | -122.2687 | 0.09613 | 0.054931 | -0.050354 | 0.032043 | -0.073242 | -0.013733 | -0.073242 | -0.13733 | 0.16937 | 0.1831 | 0.11902 | 0.19684 | 0.13275 | 0.073242 | -0.018311 | 0.18311 | 122.1497 | 0.032043 | 122.2137 | 0.054931 | 122.2 | -122.2504 | -122.287 | 0.004577 | 122.1359 | -0.064087 | 0.40283
2792.3125 | 122.4197 | -0.064087 | 122.2275 | -0.18898 | -0.046875 | 0.0040866 | 0.022937 | -0.0046911 | -0.0094614 | -0.0023733 | 0.017425 | 0.0061651 | 0.064704 | 0.045987 | -0.014311 | 0.02634 | -0.0049389 | -0.09613 | -0.059509 | -0.027466 | -0.027466 | 0.10071 | -0.009155 | 0.059509 | 0.49439 | 122.1039 | -0.07782 | 122.0673 | 0.16022 | 0.12817 | 0.14191 | 0.036621 | -122.287 | -122.2549 | 0.1648 | 0.1236 | 0.054932 | 0.086975 | 0.018311 | -0.013733 | -0.1236 | -0.16022 | 0.2243 | 0.20599 | 0.19226 | 0.21973 | 0.20599 | 0.12817 | 0 | 0.23804 | 122.1451 | -0.032043 | 122.1817 | 0.004578 | 122.168 | -122.2549 | -122.3053 | 0.036621 | 122.1313 | -0.032043 | 0.55847
2794.0625 | 122.3923 | -0.064087 | 122.2183 | -0.15083 | -0.046662 | 0.0036594 | 0.022723 | -0.0031957 | -0.0098886 | -0.0019461 | -0.028351 | 0.0057379 | 0.062568 | 0.0556 | -0.016447 | 0.028049 | -0.0062207 | -0.073242 | -0.068665 | -0.009155 | 0.036621 | 0.14191 | 0.022888 | 0.082397 | 0.58594 | 122.1039 | -0.059509 | 122.0535 | 0.16022 | 0.11444 | 0.1236 | 0.054932 | -122.287 | -122.1817 | 0.20599 | 0.14648 | 0.086975 | 0.091552 | 0.032043 | 0.004578 | -0.11444 | -0.16479 | 0.2243 | 0.18768 | 0.17853 | 0.1831 | 0.17395 | 0.15106 | 0.045776 | 0.21973 | 122.113 | -0.05951 | 122.1634 | -0.004578 | 122.168 | -122.2275 | -122.2778 | 0.10071 | 122.1176 | -0.009155 | 0.65002
2795.8125 | 122.438 | -0.059509 | 122.1817 | -0.12032 | -0.044953 | 0.0023776 | 0.025073 | -0.0031957 | -0.012025 | -0.0032277 | -0.046661 | 0.0050971 | 0.063209 | 0.04086 | -0.015806 | 0.026126 | -0.0066479 | -0.059509 | -0.054932 | -0.009155 | 0.041199 | 0.15106 | 0.027466 | 0.11444 | 0.60425 | 122.1176 | -0.059509 | 122.081 | 0.1831 | 0.13733 | 0.15564 | 0.050354 | -122.2366 | -122.1405 | 0.21057 | 0.17395 | 0.086975 | 0.1236 | 0.036621 | 0 | -0.064087 | -0.10071 | 0.24261 | 0.21515 | 0.19684 | 0.21515 | 0.19684 | 0.16022 | 0.050354 | 0.24261 | 122.1405 | -0.045777 | 122.1771 | 0.004577 | 122.1771 | -122.1909 | -122.2412 | 0.10071 | 122.1405 | 0 | 0.66376
2797.5 | 122.3373 | -0.09613 | 122.2229 | -0.11269 | -0.046875 | 0.003232 | 0.022509 | 0.0017175 | -0.010102 | -0.0036551 | -0.058869 | 0.0050971 | 0.063636 | 0.051755 | -0.01666 | 0.027194 | -0.0032299 | -0.091553 | -0.045776 | -0.004578 | -0.009155 | 0.064087 | -0.041199 | 0.045776 | 0.52643 | 122.1268 | -0.082397 | 121.9803 | 0.054932 | 0.018311 | 0.045776 | 0.091552 | -122.2687 | -122.2321 | 0.16022 | 0.14191 | 0.054931 | 0.050354 | -0.036621 | 0.013733 | -0.09613 | -0.24261 | 0.15106 | 0.14191 | 0.11444 | 0.12817 | 0.10071 | 0.068665 | -0.004577 | 0.13733 | 122.0627 | -0.041198 | 122.2092 | 0.050354 | 122.2229 | -122.2275 | -122.3053 | 0.086975 | 122.0764 | 0.004577 | 0.62256
2799.2656 | 122.3419 | -0.073242 | 122.2321 | -0.15846 | -0.042603 | 0.0036594 | 0.025287 | -0.0029821 | -0.0094614 | -0.0023733 | -0.09549 | 0.0063787 | 0.062995 | 0.05795 | -0.015592 | 0.027194 | -0.00066651 | -0.1236 | 0 | -0.045776 | -0.09613 | -0.027466 | -0.14191 | -0.036621 | 0.30212 | 122.1313 | -0.10529 | 121.9757 | 0.022888 | -0.018311 | 0.032043 | 0.027466 | -122.2321 | -122.3282 | 0.045776 | 0.036621 | -0.068665 | 0.009155 | -0.096131 | -0.032044 | -0.10071 | -0.25635 | 0.09613 | 0.10529 | 0.054931 | 0.13733 | 0.086975 | 0.01831 | -0.050354 | 0.12817 | 122.081 | 0.045776 | 122.2366 | 0.073242 | 122.2046 | -122.2778 | -122.3373 | -0.022888 | 122.0489 | -0.050354 | 0.37537
2801.0312 | 122.3007 | -0.10986 | 122.2321 | -0.097427 | -0.044525 | 0.0017368 | 0.024218 | -0.0040503 | -0.012452 | -0.0045095 | -0.046661 | 0.0055243 | 0.066627 | 0.041928 | -0.017088 | 0.026767 | -0.0023755 | -0.16479 | -0.013733 | -0.059509 | -0.10071 | 0 | -0.086975 | -0.013733 | 0.45319 | 122.1588 | -0.091553 | 121.9666 | 0.036621 | -0.018311 | 0.027466 | 0.050354 | -122.2458 | -122.3328 | 0.10986 | 0.09613 | 0.022888 | 0.045776 | -0.027466 | 0.01831 | -0.073243 | -0.2655 | 0.14648 | 0.13733 | 0.091552 | 0.11902 | 0.073242 | 0.059509 | -0.041199 | 0.12817 | 122.0581 | 0.045776 | 122.2504 | 0.09613 | 122.2687 | -122.2916 | -122.3236 | 0.009155 | 122.0764 | -0.054932 | 0.56305
2802.7812 | 122.3511 | -0.086975 | 122.2229 | -0.16609 | -0.046662 | 0.0025912 | 0.022082 | -0.00020513 | -0.010102 | -0.0030141 | -0.034454 | 0.0042425 | 0.063209 | 0.047909 | -0.015379 | 0.027194 | -0.0066479 | -0.068665 | -0.041199 | 0.004578 | -0.004578 | 0.10071 | -0.013733 | 0.07782 | 0.54474 | 122.1222 | -0.064087 | 121.9986 | 0.073242 | 0.050354 | 0.059509 | 0.091553 | -122.2641 | -122.2275 | 0.18768 | 0.16479 | 0.073242 | 0.073242 | -0.018311 | 0.022888 | -0.10071 | -0.2243 | 0.16022 | 0.14648 | 0.13733 | 0.1236 | 0.11444 | 0.09613 | -0.009156 | 0.13733 | 122.0627 | -0.045777 | 122.1863 | 0.045776 | 122.2092 | -122.2183 | -122.287 | 0.082397 | 122.0856 | 0.01831 | 0.63171
2804.5312 | 122.3465 | -0.086975 | 122.2641 | -0.10506 | -0.044312 | 0.0019504 | 0.025287 | 0.00022207 | -0.0077524 | -0.0010915 | -0.092438 | 0.0074469 | 0.064063 | 0.052182 | -0.017301 | 0.026126 | -0.0013073 | -0.11902 | -0.022888 | -0.045776 | -0.086975 | 0 | -0.082397 | -0.004578 | 0.46234 | 122.1634 | -0.091553 | 122.0032 | 0.073242 | 0.013733 | 0.073242 | 0.041199 | -122.287 | -122.3511 | 0.086975 | 0.082397 | 0.004578 | 0.041198 | -0.036621 | -0.004578 | -0.10071 | -0.26093 | 0.16022 | 0.16022 | 0.10071 | 0.16479 | 0.10529 | 0.045776 | -0.041199 | 0.16479 | 122.0947 | 0.022888 | 122.2549 | 0.064087 | 122.2504 | -122.3099 | -122.3557 | 0 | 122.0901 | -0.032044 | 0.54932
2806.2969 | 122.4152 | -0.054932 | 122.1954 | -0.12794 | -0.042389 | 0.003232 | 0.026996 | 0.0015039 | -0.008607 | -0.0036551 | -0.080231 | 0.0078741 | 0.065772 | 0.050473 | -0.016874 | 0.027835 | -0.0053661 | -0.09613 | -0.032043 | -0.045776 | 0.013733 | 0.09613 | -0.036621 | 0.041199 | 0.41199 | 122.0856 | -0.050354 | 122.0856 | 0.14191 | 0.09613 | 0.15106 | 0.009156 | -122.2275 | -122.1817 | 0.15106 | 0.096131 | 0.018311 | 0.086975 | 0.009155 | 0.004578 | -0.10986 | -0.10986 | 0.19684 | 0.20599 | 0.15106 | 0.20142 | 0.14648 | 0.14191 | 0.059509 | 0.19226 | 122.1359 | 0.013733 | 122.1359 | 0.022889 | 122.1405 | -122.2412 | -122.2458 | 0.068665 | 122.1405 | -0.041198 | 0.46692
2808 | 122.3831 | -0.041199 | 122.1863 | -0.1432 | -0.045807 | 0.001523 | 0.024432 | 8.47e-06 | -0.0098886 | -0.0055777 | -0.022247 | 0.0063787 | 0.064491 | 0.044064 | -0.016874 | 0.028049 | -0.0060071 | -0.09613 | -0.068665 | -0.022888 | -0.009155 | 0.10071 | -0.041199 | 0.059509 | 0.39825 | 122.1039 | -0.073242 | 122.0306 | 0.10529 | 0.068665 | 0.10071 | 0.018311 | -122.2549 | -122.1954 | 0.14191 | 0.10071 | 0 | 0.082397 | -0.018311 | -0.032043 | -0.082397 | -0.15564 | 0.14649 | 0.14191 | 0.10986 | 0.17395 | 0.14191 | 0.1236 | 0.013733 | 0.17853 | 122.1039 | -0.045777 | 122.1771 | -0.027466 | 122.1451 | -122.2092 | -122.2595 | 0.032044 | 122.0718 | -0.054931 | 0.43945
2809.6875 | 122.3145 | -0.10071 | 122.2641 | -0.097427 | -0.045807 | 0.002164 | 0.025714 | 0.00064947 | -0.010102 | -0.0017325 | -0.046661 | 0.0057379 | 0.062568 | 0.051968 | -0.015592 | 0.026126 | -0.0036573 | -0.14648 | -0.018311 | -0.050354 | -0.082397 | 0.018311 | -0.10529 | 0.004578 | 0.45776 | 122.168 | -0.09613 | 121.9574 | 0.032043 | -0.009155 | 0.018311 | 0.050354 | -122.2824 | -122.3465 | 0.11902 | 0.10529 | -0.004578 | 0.054932 | -0.054932 | 0.004578 | -0.09613 | -0.3067 | 0.13275 | 0.11902 | 0.091553 | 0.11444 | 0.086975 | 0.068665 | -0.032043 | 0.12817 | 122.0535 | 0.032043 | 122.2641 | 0.082397 | 122.2687 | -122.3145 | -122.3602 | 0.018311 | 122.0581 | -0.045776 | 0.55847
2811.4375 | 122.4701 | -0.054932 | 122.2183 | -0.16609 | -0.046875 | 0.0013094 | 0.023364 | 0.0015039 | -0.012239 | -0.0034415 | -0.01004 | 0.0048833 | 0.062995 | 0.047268 | -0.017942 | 0.026767 | -0.0053661 | -0.068665 | -0.059509 | -0.004578 | 0.054932 | 0.1831 | 0.041199 | 0.10529 | 0.59509 | 122.0993 | -0.064087 | 122.1085 | 0.20142 | 0.15106 | 0.16479 | 0.050354 | -122.2778 | -122.1634 | 0.23804 | 0.16022 | 0.096131 | 0.10986 | 0.045777 | -0.009155 | -0.11902 | -0.10986 | 0.25635 | 0.21973 | 0.20599 | 0.22888 | 0.21515 | 0.18768 | 0.05951 | 0.2655 | 122.1725 | -0.054931 | 122.1634 | -0.004577 | 122.1542 | -122.2229 | -122.2824 | 0.10986 | 122.1634 | -0.013733 | 0.65002
2813.1875 | 122.3145 | -0.09613 | 122.2321 | -0.089798 | -0.045166 | -0.00018577 | 0.023364 | -0.0010595 | -0.01053 | -0.0028005 | -0.058869 | 0.0063787 | 0.061714 | 0.042355 | -0.016233 | 0.02869 | -0.0064343 | -0.13275 | -0.027466 | -0.054932 | -0.091553 | -0.004578 | -0.10529 | -0.004578 | 0.44861 | 122.1725 | -0.086975 | 121.9757 | 0.036621 | -0.009155 | 0.032043 | 0.041198 | -122.2595 | -122.3236 | 0.091552 | 0.091552 | -0.009156 | 0.050354 | -0.050354 | 0.009155 | -0.05951 | -0.25635 | 0.13275 | 0.12817 | 0.086975 | 0.11902 | 0.07782 | 0.050354 | -0.036621 | 0.1236 | 122.0627 | 0.027466 | 122.2595 | 0.068664 | 122.2687 | -122.287 | -122.319 | 0.004577 | 122.0718 | -0.036621 | 0.54474
2814.9375 | 122.3236 | -0.091553 | 122.2458 | -0.06691 | -0.044098 | 0.0040866 | 0.023578 | -0.0025549 | -0.0092478 | -0.0053641 | -0.037506 | 0.0070197 | 0.064277 | 0.045559 | -0.018369 | 0.025699 | -0.0089977 | -0.07782 | -0.054932 | -0.027466 | -0.022888 | 0.07782 | -0.032043 | 0.054932 | 0.52643 | 122.1176 | -0.073242 | 121.994 | 0.059509 | 0.009155 | 0.045776 | 0.064087 | -122.3007 | -122.2687 | 0.16937 | 0.14649 | 0.05951 | 0.082398 | -0.004577 | 0.018311 | -0.12817 | -0.25177 | 0.15106 | 0.13733 | 0.10071 | 0.11902 | 0.082397 | 0.10529 | 0.004578 | 0.13275 | 122.0673 | -0.027466 | 122.1909 | 0.036621 | 122.2092 | -122.2733 | -122.319 | 0.068665 | 122.0856 | 0.013733 | 0.61798
2816.6406 | 122.4197 | -0.054932 | 122.2046 | -0.23476 | -0.044312 | 0.0036594 | 0.0255 | 0.0010767 | -0.010957 | -0.0051505 | -0.06192 | 0.0059515 | 0.063209 | 0.040005 | -0.017515 | 0.026767 | -0.0051525 | -0.045776 | -0.073242 | 0 | 0.045776 | 0.13733 | -0.022888 | 0.082397 | 0.43945 | 122.1222 | -0.059509 | 122.0993 | 0.15564 | 0.11444 | 0.16479 | 0.054932 | -122.2778 | -122.1588 | 0.19226 | 0.13733 | 0.032044 | 0.082397 | -0.022888 | -0.004577 | -0.082398 | -0.10529 | 0.21057 | 0.21973 | 0.16937 | 0.2243 | 0.17395 | 0.13733 | 0.045776 | 0.21515 | 122.1588 | -0.073242 | 122.1817 | -0.01831 | 122.1771 | -122.2046 | -122.2641 | 0.10071 | 122.1542 | 0.009156 | 0.49438
2818.3906 | 122.3465 | -0.086975 | 122.2275 | -0.11269 | -0.042603 | 0.003232 | 0.026782 | 0.0023585 | -0.008607 | -0.0034415 | -0.11685 | 0.0057379 | 0.065559 | 0.048764 | -0.017301 | 0.027408 | -0.0062207 | -0.11444 | -0.013733 | -0.027466 | -0.07782 | 0.004578 | -0.12817 | -0.027466 | 0.33875 | 122.1176 | -0.086975 | 122.0169 | 0.068665 | 0.004578 | 0.064087 | 0.059509 | -122.2412 | -122.3053 | 0.091553 | 0.059509 | -0.041199 | 0 | -0.10071 | 0 | -0.10986 | -0.21057 | 0.15564 | 0.15106 | 0.091553 | 0.15106 | 0.091553 | 0.032044 | -0.050354 | 0.15564 | 122.1039 | 0.013733 | 122.2046 | 0.073242 | 122.2046 | -122.2549 | -122.3145 | 0.009155 | 122.1039 | -0.027466 | 0.42572
2820.0938 | 122.4564 | -0.045776 | 122.2137 | -0.1432 | -0.045594 | 0.0040866 | 0.022509 | -0.0014867 | -0.012666 | -0.0045095 | -0.016144 | 0.0055243 | 0.064063 | 0.050473 | -0.01666 | 0.028476 | -0.0036573 | -0.091553 | -0.068665 | -0.018311 | 0.004578 | 0.10986 | 0.004578 | 0.073242 | 0.50354 | 122.0947 | -0.073242 | 122.0947 | 0.16479 | 0.16937 | 0.14191 | 0.027465 | -122.2824 | -122.2092 | 0.15564 | 0.11902 | 0.050354 | 0.091553 | 0.022889 | -0.027466 | -0.11902 | -0.11902 | 0.21057 | 0.18768 | 0.21515 | 0.21515 | 0.24261 | 0.12817 | 0.022889 | 0.23804 | 122.168 | -0.050354 | 122.168 | -0.022889 | 122.1405 | -122.2321 | -122.287 | 0.050354 | 122.1405 | -0.045777 | 0.54932
2821.8594 | 122.3007 | -0.09613 | 122.2321 | -0.15083 | -0.044312 | 0.0051546 | 0.026782 | 0.0019311 | -0.0083932 | -0.0049367 | -0.14127 | 0.0057379 | 0.064491 | 0.055386 | -0.017088 | 0.02869 | -0.0064343 | -0.1236 | -0.022888 | -0.036621 | -0.086975 | -0.036621 | -0.14648 | -0.059509 | 0.3067 | 122.1542 | -0.086975 | 121.9666 | 0 | -0.059509 | 0.009155 | 0.059509 | -122.2549 | -122.319 | 0.059509 | 0.036621 | -0.050354 | -0.022888 | -0.10986 | 0.009155 | -0.07782 | -0.2655 | 0.09613 | 0.10528 | 0.036621 | 0.09613 | 0.027466 | 0 | -0.050354 | 0.086975 | 122.0535 | 0.013733 | 122.2412 | 0.073242 | 122.2504 | -122.2687 | -122.319 | 0.009155 | 122.0627 | -0.027466 | 0.40283
2823.6094 | 122.438 | -0.050354 | 122.2137 | -0.15083 | -0.042816 | 0.0045138 | 0.027423 | -0.0046911 | -0.01053 | -0.0015189 | -0.074127 | 0.0057379 | 0.064277 | 0.054959 | -0.016233 | 0.027621 | -0.0049389 | -0.059509 | -0.054932 | -0.004578 | 0.036621 | 0.10986 | -0.013733 | 0.064087 | 0.42114 | 122.1039 | -0.064087 | 122.1085 | 0.16479 | 0.10986 | 0.17395 | 0.045776 | -122.2687 | -122.1771 | 0.16022 | 0.11444 | 0.036621 | 0.068665 | -0.009155 | -0.013733 | -0.10986 | -0.10529 | 0.21515 | 0.2243 | 0.16022 | 0.23804 | 0.17395 | 0.11444 | 0.041199 | 0.22888 | 122.1725 | -0.050354 | 122.168 | -0.004578 | 122.1542 | -122.2183 | -122.2778 | 0.086975 | 122.1588 | -0.009155 | 0.4715
2825.3594 | 122.374 | -0.059509 | 122.2183 | -0.17372 | -0.04303 | 0.0025912 | 0.024859 | -0.0025549 | -0.010316 | -0.0060049 | -0.025299 | 0.0048833 | 0.062782 | 0.044919 | -0.014951 | 0.027621 | -0.0030163 | -0.10071 | -0.059509 | -0.013733 | -0.027466 | 0.07782 | -0.054932 | 0.045776 | 0.41199 | 122.0947 | -0.059509 | 122.0306 | 0.09613 | 0.059509 | 0.10529 | 0.045776 | -122.2778 | -122.2458 | 0.13733 | 0.10528 | 0.004577 | 0.059509 | -0.041199 | 0 | -0.1236 | -0.18768 | 0.15564 | 0.16479 | 0.11902 | 0.16479 | 0.11902 | 0.091553 | -0.013733 | 0.15564 | 122.0901 | -0.045776 | 122.1542 | 0 | 122.1542 | -122.2321 | -122.2778 | 0.032043 | 122.0901 | -0.041199 | 0.4715
2827.0625 | 122.3145 | -0.09613 | 122.2412 | -0.18135 | -0.042603 | 0.0051546 | 0.025927 | -0.0027685 | -0.009675 | -0.0010915 | -0.12296 | 0.0059515 | 0.064491 | 0.04855 | -0.015165 | 0.029544 | -0.0060071 | -0.091553 | -0.022888 | -0.022888 | -0.050354 | 0.013733 | -0.10071 | -0.027466 | 0.3891 | 122.1588 | -0.073242 | 121.994 | 0.032043 | -0.032043 | 0.036621 | 0.073242 | -122.2641 | -122.2916 | 0.10986 | 0.068664 | -0.004578 | -0.004578 | -0.07782 | 0.022888 | -0.082398 | -0.24719 | 0.12817 | 0.13275 | 0.064087 | 0.10986 | 0.041199 | 0.036621 | -0.027466 | 0.10529 | 122.0673 | 0 | 122.2321 | 0.073242 | 122.2549 | -122.2641 | -122.3145 | 0.045776 | 122.0901 | 0.004577 | 0.48523
2828.8281 | 122.4335 | -0.036621 | 122.2321 | -0.22713 | -0.043457 | 0.0023776 | 0.027209 | -0.0023413 | -0.0090342 | -0.0057913 | -0.068024 | 0.0055243 | 0.064277 | 0.049191 | -0.01602 | 0.029117 | -0.0045117 | -0.086975 | -0.018311 | -0.036621 | 0.004578 | 0.09613 | -0.032043 | 0.054932 | 0.39825 | 122.1222 | -0.073242 | 122.0856 | 0.14648 | 0.09613 | 0.16937 | 0 | -122.2504 | -122.2275 | 0.13275 | 0.091553 | 0.004578 | 0.091553 | 0.004578 | -0.036621 | -0.10986 | -0.14648 | 0.18311 | 0.20599 | 0.13275 | 0.24261 | 0.16937 | 0.13275 | 0.041199 | 0.21973 | 122.1588 | 0.01831 | 122.1954 | 0.01831 | 122.1588 | -122.2687 | -122.3053 | 0.041199 | 122.1222 | -0.050354 | 0.43488
2830.5156 | 122.3969 | -0.068665 | 122.2229 | -0.1432 | -0.045807 | 0.0030184 | 0.025927 | 0.0019311 | -0.0094614 | -0.0036551 | -0.083283 | 0.0061651 | 0.064063 | 0.048337 | -0.014524 | 0.029117 | -0.0021619 | -0.10529 | -0.036621 | -0.018311 | -0.073242 | 0.027466 | -0.086975 | 0.009155 | 0.35248 | 122.1313 | -0.09613 | 122.0673 | 0.12817 | 0.091553 | 0.14648 | 0.050354 | -122.2595 | -122.2961 | 0.096131 | 0.07782 | -0.01831 | 0.027466 | -0.068664 | -0.027465 | -0.091552 | -0.15564 | 0.19684 | 0.21515 | 0.16022 | 0.24261 | 0.18768 | 0.045777 | -0.054931 | 0.2243 | 122.1634 | -0.01831 | 122.2275 | 0.032044 | 122.2 | -122.2412 | -122.319 | -0.004577 | 122.1359 | -0.036621 | 0.42114
2832.2812 | 122.4289 | -0.059509 | 122.2092 | -0.1432 | -0.045594 | 0.0019504 | 0.024005 | -0.0021277 | -0.0090342 | -0.0045095 | -0.016144 | 0.0055243 | 0.065559 | 0.047268 | -0.015379 | 0.026767 | -0.0060071 | -0.054932 | -0.054932 | -0.009155 | 0.045776 | 0.1831 | 0.041199 | 0.11902 | 0.63629 | 122.1039 | -0.068665 | 122.113 | 0.19226 | 0.15106 | 0.16479 | 0.050354 | -122.2641 | -122.1634 | 0.24261 | 0.17853 | 0.10071 | 0.12817 | 0.050354 | -0.009156 | -0.10528 | -0.09613 | 0.25177 | 0.2243 | 0.21057 | 0.23346 | 0.21973 | 0.19226 | 0.054931 | 0.26093 | 122.1817 | -0.045777 | 122.1725 | 0.004577 | 122.1634 | -122.2183 | -122.2778 | 0.10528 | 122.1725 | 0.004577 | 0.6958
2834.0469 | 122.4335 | -0.064087 | 122.2275 | -0.16609 | -0.046448 | 0.0030184 | 0.021655 | -0.00020513 | -0.01053 | -2.3544e-05 | -0.0008851 | 0.0040289 | 0.064704 | 0.043637 | -0.015592 | 0.027835 | -0.0032299 | -0.059509 | -0.054932 | -0.009155 | 0.050354 | 0.16937 | 0.036621 | 0.10986 | 0.60883 | 122.113 | -0.045776 | 122.0947 | 0.1831 | 0.15564 | 0.15106 | 0.054932 | -122.2824 | -122.1771 | 0.23346 | 0.17395 | 0.10071 | 0.11902 | 0.045776 | 0.018311 | -0.11444 | -0.13275 | 0.24719 | 0.21515 | 0.21973 | 0.19684 | 0.20142 | 0.17853 | 0.059509 | 0.22888 | 122.1405 | -0.045777 | 122.1588 | 0.009155 | 122.1771 | -122.2366 | -122.2733 | 0.11444 | 122.1588 | 0.004578 | 0.67291
2835.7969 | 122.438 | -0.045776 | 122.2137 | -0.20424 | -0.04068 | 0.0019504 | 0.023791 | 0.00064947 | -0.0083932 | -0.0025869 | -0.058869 | 0.0048833 | 0.062568 | 0.053891 | -0.018369 | 0.029117 | -0.0075025 | -0.050354 | -0.068665 | 0.004578 | 0.054932 | 0.14191 | -0.022888 | 0.07782 | 0.46234 | 122.1176 | -0.059509 | 122.1039 | 0.16479 | 0.11444 | 0.15564 | 0.050354 | -122.2824 | -122.1588 | 0.18768 | 0.1236 | 0.022888 | 0.073242 | -0.027466 | -0.013733 | -0.09613 | -0.10986 | 0.21057 | 0.20142 | 0.16022 | 0.21515 | 0.17395 | 0.13733 | 0.050354 | 0.2243 | 122.1634 | -0.073243 | 122.1771 | -0.022889 | 122.1634 | -122.2092 | -122.2733 | 0.10071 | 122.1497 | -0.004578 | 0.50812
2837.5469 | 122.3145 | -0.082397 | 122.2504 | -0.12032 | -0.043244 | 0.003873 | 0.0255 | 0.00043587 | -0.009675 | -0.0025869 | -0.13211 | 0.0059515 | 0.064491 | 0.051114 | -0.016874 | 0.027621 | -0.0019483 | -0.11444 | -0.004578 | -0.036621 | -0.07782 | -0.022888 | -0.15106 | -0.036621 | 0.29755 | 122.1405 | -0.091553 | 121.9849 | 0.018311 | -0.036621 | 0.036621 | 0.045776 | -122.2549 | -122.3282 | 0.059509 | 0.045776 | -0.068665 | 0 | -0.11444 | -0.009156 | -0.10986 | -0.2655 | 0.10071 | 0.11902 | 0.045776 | 0.12817 | 0.054932 | 0.013733 | -0.041199 | 0.10986 | 122.0764 | 0.032043 | 122.2321 | 0.077819 | 122.2229 | -122.287 | -122.3419 | 0.004577 | 122.0673 | -0.032044 | 0.37994
2839.25 | 122.319 | -0.086975 | 122.2458 | -0.11269 | -0.041321 | 0.0043002 | 0.026782 | 0.00086307 | -0.0081796 | -0.0042959 | -0.09549 | 0.0068059 | 0.066627 | 0.046414 | -0.016447 | 0.029117 | -0.0019483 | -0.091553 | -0.041199 | -0.036621 | -0.050354 | 0.022888 | -0.10071 | -0.009155 | 0.41657 | 122.1497 | -0.086975 | 121.9894 | 0.032043 | -0.045776 | 0.045776 | 0.050354 | -122.287 | -122.2961 | 0.10986 | 0.07782 | -0.013733 | 0.027466 | -0.064087 | 0 | -0.096131 | -0.25635 | 0.11902 | 0.13275 | 0.041199 | 0.13275 | 0.041199 | 0.059509 | -0.013733 | 0.11902 | 122.0764 | -0.004578 | 122.2366 | 0.045776 | 122.2366 | -122.2824 | -122.3328 | 0.036621 | 122.0764 | -0.004578 | 0.50354
2841 | 122.3145 | -0.10529 | 122.2504 | -0.097427 | -0.045807 | 0.0013094 | 0.024432 | 0.00043587 | -0.010316 | -0.0038687 | -0.058869 | 0.0061651 | 0.063209 | 0.053677 | -0.015165 | 0.026981 | -0.0021619 | -0.14191 | -0.013733 | -0.045776 | -0.086975 | -0.013733 | -0.10529 | -0.013733 | 0.46692 | 122.1634 | -0.10071 | 121.9711 | 0.050354 | -0.013733 | 0.009155 | 0.05951 | -122.2641 | -122.3373 | 0.091553 | 0.091553 | 0 | 0.032043 | -0.05951 | 0.004578 | -0.086975 | -0.27924 | 0.15564 | 0.11444 | 0.091553 | 0.10986 | 0.086975 | 0.032043 | -0.041199 | 0.15106 | 122.0718 | 0.032043 | 122.2641 | 0.091553 | 122.2687 | -122.2961 | -122.3511 | 0.018311 | 122.0764 | -0.036621 | 0.5722
2842.75 | 122.3328 | -0.09613 | 122.2549 | -0.12794 | -0.047516 | 0.0028048 | 0.023578 | -0.0036231 | -0.0094614 | -0.0017325 | -0.037506 | 0.0072333 | 0.06385 | 0.045987 | -0.017301 | 0.026553 | -0.0053661 | -0.13733 | -0.027466 | -0.041199 | -0.086975 | 0.022888 | -0.091553 | -0.009155 | 0.47607 | 122.168 | -0.086975 | 121.962 | 0.054932 | -0.009155 | 0.018311 | 0.054931 | -122.2824 | -122.3419 | 0.11902 | 0.086975 | 0.004577 | 0.032044 | -0.050354 | 0.009155 | -0.086975 | -0.29297 | 0.15106 | 0.11444 | 0.086975 | 0.10529 | 0.07782 | 0.064087 | -0.045776 | 0.14191 | 122.0489 | 0.013733 | 122.2549 | 0.068664 | 122.2641 | -122.2961 | -122.3419 | 0.009155 | 122.0581 | -0.041199 | 0.5722
2844.5 | 122.4564 | -0.054932 | 122.1863 | -0.10506 | -0.045166 | 0.00088223 | 0.023364 | -0.0057593 | -0.0090342 | -0.0060049 | 0.0052185 | 0.0070197 | 0.062568 | 0.043637 | -0.01602 | 0.028903 | -0.0034435 | -0.07782 | -0.064087 | -0.009155 | 0.022888 | 0.14648 | 0.036621 | 0.10986 | 0.59052 | 122.081 | -0.050354 | 122.0947 | 0.18768 | 0.16022 | 0.17395 | 0.045777 | -122.2504 | -122.1634 | 0.20142 | 0.16479 | 0.091553 | 0.11902 | 0.045776 | 0.004578 | -0.10528 | -0.091552 | 0.24261 | 0.22888 | 0.21515 | 0.2243 | 0.21057 | 0.15564 | 0.032043 | 0.23804 | 122.1451 | -0.054932 | 122.1313 | -0.009155 | 122.1359 | -122.1954 | -122.2366 | 0.07782 | 122.1497 | -0.022888 | 0.64545
2846.1875 | 122.319 | -0.11902 | 122.2321 | -0.082169 | -0.043671 | 0.001523 | 0.026568 | -0.0038367 | -0.010957 | -0.0023733 | -0.10159 | 0.0074469 | 0.064918 | 0.048337 | -0.016874 | 0.026553 | -0.0077161 | -0.12817 | -0.027466 | -0.054932 | -0.091553 | -0.013733 | -0.091553 | -0.004578 | 0.46234 | 122.1588 | -0.10529 | 121.9803 | 0.050354 | -0.013733 | 0.032043 | 0.064087 | -122.2595 | -122.3236 | 0.10529 | 0.11444 | 0.027466 | 0.050354 | -0.036621 | 0.013733 | -0.073243 | -0.25177 | 0.16937 | 0.15106 | 0.10529 | 0.13733 | 0.091553 | 0.041199 | -0.036621 | 0.15564 | 122.0856 | 0.027466 | 122.2641 | 0.091553 | 122.2778 | -122.287 | -122.3373 | 0.027466 | 122.0993 | -0.009155 | 0.58136
2847.9375 | 122.3099 | -0.091553 | 122.2687 | -0.10506 | -0.044525 | 0.0025912 | 0.027423 | 0.0015039 | -0.009675 | -0.0021597 | -0.12601 | 0.0048833 | 0.062995 | 0.050686 | -0.017301 | 0.028049 | -0.00088011 | -0.09613 | -0.022888 | -0.050354 | -0.07782 | 0.004578 | -0.11444 | -0.022888 | 0.37537 | 122.1725 | -0.09613 | 121.9757 | 0.022888 | -0.027466 | 0.027466 | 0.041199 | -122.2916 | -122.3465 | 0.096131 | 0.068665 | -0.022888 | 0.027466 | -0.064087 | -0.004577 | -0.096131 | -0.29297 | 0.11444 | 0.11902 | 0.064087 | 0.1236 | 0.068664 | 0.054932 | -0.027466 | 0.11902 | 122.0718 | 0.027466 | 122.2687 | 0.068665 | 122.2641 | -122.319 | -122.3648 | 0.013733 | 122.0673 | -0.004577 | 0.46692
2849.6875 | 122.2916 | -0.10986 | 122.2275 | -0.16609 | -0.041748 | 0.003232 | 0.024859 | 0.00043587 | -0.008607 | -0.0060049 | -0.1138 | 0.0065923 | 0.063423 | 0.045987 | -0.016233 | 0.027621 | -0.0025891 | -0.14191 | -0.009155 | -0.059509 | -0.091553 | -0.027466 | -0.14648 | -0.059509 | 0.29755 | 122.1817 | -0.10529 | 121.9711 | -0.009155 | -0.068665 | 0.018311 | 0.050354 | -122.2366 | -122.319 | 0.082397 | 0.050354 | -0.036621 | 0 | -0.086975 | 0.004577 | -0.045776 | -0.25635 | 0.10071 | 0.12817 | 0.041198 | 0.1236 | 0.036621 | 0.032043 | -0.032044 | 0.096131 | 122.0764 | 0.050354 | 122.287 | 0.10071 | 122.2916 | -122.287 | -122.3328 | 0.01831 | 122.081 | -0.032044 | 0.40741
2851.3906 | 122.4472 | -0.068665 | 122.1909 | -0.12794 | -0.042603 | 0.0013094 | 0.023364 | -0.0070409 | -0.0090342 | -0.0021597 | 0.0021667 | 0.0046697 | 0.062995 | 0.0509 | -0.015165 | 0.025912 | -0.0060071 | -0.1236 | -0.027466 | -0.018311 | -0.013733 | 0.10071 | -0.022888 | 0.082397 | 0.50354 | 122.1176 | -0.073242 | 122.0764 | 0.16937 | 0.12817 | 0.13733 | 0.050354 | -122.2183 | -122.2046 | 0.16937 | 0.15106 | 0.045777 | 0.10071 | -0.004577 | -0.004577 | -0.073242 | -0.11444 | 0.23804 | 0.20599 | 0.19684 | 0.21057 | 0.20142 | 0.11902 | 0.004578 | 0.24261 | 122.1497 | -0.009155 | 122.1909 | 0.041199 | 122.1863 | -122.2092 | -122.2641 | 0.054932 | 122.1451 | -0.054931 | 0.5722
2853.1562 | 122.3511 | -0.10986 | 122.2458 | -0.18898 | -0.043885 | 0.00088223 | 0.027209 | -0.0012731 | -0.01117 | -0.0019461 | -0.064972 | 0.0059515 | 0.063423 | 0.051327 | -0.018369 | 0.028049 | -0.0036573 | -0.13275 | -0.018311 | -0.022888 | -0.073242 | 0.004578 | -0.082397 | -0.013733 | 0.4715 | 122.2 | -0.09613 | 122.0123 | 0.07782 | 0.022888 | 0.064087 | 0.086975 | -122.2641 | -122.319 | 0.11444 | 0.09613 | 0.027466 | 0.009155 | -0.059509 | 0.013733 | -0.045777 | -0.23346 | 0.18768 | 0.17395 | 0.13275 | 0.16022 | 0.11902 | 0.027466 | -0.050354 | 0.17395 | 122.1085 | 0.004577 | 122.2961 | 0.091552 | 122.3099 | -122.2687 | -122.3419 | 0.036621 | 122.1222 | -0.022888 | 0.58136
2854.8594 | 122.3511 | -0.082397 | 122.2366 | -0.15083 | -0.044953 | 0.0017368 | 0.026996 | 0.00086307 | -0.0094614 | -0.0055777 | -0.089386 | 0.0050971 | 0.064491 | 0.054745 | -0.016233 | 0.026553 | -0.0057935 | -0.082397 | -0.041199 | -0.041199 | -0.027466 | 0.073242 | -0.059509 | 0.013733 | 0.49439 | 122.1268 | -0.09613 | 122.0306 | 0.10529 | 0.045776 | 0.082397 | 0.041198 | -122.2778 | -122.2641 | 0.15564 | 0.09613 | 0.022888 | 0.054932 | -0.01831 | -0.013733 | -0.10986 | -0.20599 | 0.18768 | 0.16479 | 0.12817 | 0.17853 | 0.14191 | 0.11444 | 0.013733 | 0.20142 | 122.1268 | 0 | 122.2229 | 0.041198 | 122.2092 | -122.2778 | -122.3328 | 0.054931 | 122.113 | 0 | 0.57678
2856.625 | 122.3053 | -0.10529 | 122.2549 | -0.17372 | -0.044525 | 0.0034456 | 0.026568 | 0.0040675 | -0.010316 | -0.0049367 | -0.086334 | 0.0059515 | 0.064918 | 0.047909 | -0.016874 | 0.02634 | -0.0015209 | -0.11444 | -0.004578 | -0.032043 | -0.082397 | 0 | -0.13275 | -0.045776 | 0.32044 | 122.1497 | -0.091553 | 121.9666 | 0 | -0.036621 | 0.036621 | 0.073243 | -122.2595 | -122.3373 | 0.10529 | 0.05951 | -0.027465 | -0.013733 | -0.10071 | 0.013733 | -0.10529 | -0.28839 | 0.10529 | 0.14191 | 0.068665 | 0.12817 | 0.054932 | 0.032043 | -0.050354 | 0.091553 | 122.0581 | 0.027465 | 122.2412 | 0.10071 | 122.2549 | -122.287 | -122.3465 | 0.022889 | 122.0718 | -0.009155 | 0.42572
2858.375 | 122.3236 | -0.11444 | 122.2595 | -0.11269 | -0.044953 | 0.001523 | 0.024218 | 0.0012903 | -0.01117 | -0.0045095 | -0.016144 | 0.0044561 | 0.063209 | 0.04321 | -0.01602 | 0.026767 | -0.0068615 | -0.07782 | -0.036621 | -0.022888 | -0.022888 | 0.086975 | -0.036621 | 0.018311 | 0.5127 | 122.1542 | -0.082397 | 121.9803 | 0.054932 | 0.004578 | 0.041199 | 0.091553 | -122.2961 | -122.2824 | 0.20142 | 0.13275 | 0.07782 | 0.041199 | -0.013733 | 0.032044 | -0.10529 | -0.27923 | 0.16937 | 0.15564 | 0.11902 | 0.1236 | 0.086975 | 0.10986 | 0 | 0.13733 | 122.0627 | -0.013733 | 122.2366 | 0.07782 | 122.2687 | -122.2824 | -122.3419 | 0.091553 | 122.0947 | 0.036621 | 0.62714
2860.0625 | 122.3511 | -0.091553 | 122.2412 | -0.097427 | -0.041962 | 0.0019504 | 0.024218 | 0.0010767 | -0.010957 | -0.0023733 | -0.09549 | 0.0078741 | 0.063209 | 0.050686 | -0.017729 | 0.026126 | -0.0013073 | -0.068665 | -0.036621 | -0.050354 | -0.022888 | 0.059509 | -0.064087 | 0.009155 | 0.48065 | 122.1313 | -0.07782 | 122.0261 | 0.09613 | 0.032043 | 0.086975 | 0.041199 | -122.2778 | -122.2641 | 0.15106 | 0.10071 | 0.027466 | 0.059509 | -0.013733 | 0.013733 | -0.10986 | -0.21515 | 0.18768 | 0.17853 | 0.1236 | 0.16479 | 0.10986 | 0.10986 | 0.027466 | 0.17395 | 122.1039 | 0.013733 | 122.2092 | 0.054932 | 122.2229 | -122.2916 | -122.319 | 0.068665 | 122.1176 | 0.022888 | 0.57221
2861.7656 | 122.4289 | -0.059509 | 122.2229 | -0.11269 | -0.046021 | 0.0040866 | 0.019732 | -0.0019141 | -0.0098886 | -0.0023733 | 0.011322 | 0.0040289 | 0.06385 | 0.044919 | -0.017088 | 0.027194 | -0.0036573 | -0.07782 | -0.059509 | 0 | 0.032043 | 0.16022 | 0.013733 | 0.09613 | 0.60425 | 122.1176 | -0.068665 | 122.0764 | 0.17395 | 0.14191 | 0.15106 | 0.059509 | -122.2824 | -122.1909 | 0.21973 | 0.15564 | 0.073242 | 0.09613 | 0.013733 | -0.009156 | -0.10528 | -0.14648 | 0.23346 | 0.21057 | 0.20142 | 0.21973 | 0.21057 | 0.16022 | 0.032043 | 0.24261 | 122.1451 | -0.059509 | 122.1863 | 0 | 122.1771 | -122.2229 | -122.2916 | 0.091552 | 122.1359 | -0.018311 | 0.66376
2863.5312 | 122.4426 | -0.045776 | 122.2092 | -0.12032 | -0.045166 | 0.0043002 | 0.023578 | -0.0023413 | -0.012025 | -0.0072867 | 0.014374 | 0.0068059 | 0.063636 | 0.038724 | -0.018583 | 0.027621 | -0.0072889 | -0.10071 | -0.059509 | -0.009155 | -0.004578 | 0.091553 | -0.022888 | 0.068665 | 0.49439 | 122.1405 | -0.073242 | 122.0581 | 0.16022 | 0.12817 | 0.14191 | 0.036621 | -122.2687 | -122.2137 | 0.13733 | 0.11444 | 0.022888 | 0.07782 | -0.013733 | -0.027466 | -0.068664 | -0.15106 | 0.20599 | 0.18768 | 0.17395 | 0.21515 | 0.20142 | 0.10071 | 0.004577 | 0.23346 | 122.1313 | -0.050354 | 122.2137 | -0.013733 | 122.1863 | -122.2183 | -122.2824 | 0.041198 | 122.1039 | -0.054932 | 0.54016
2865.2969 | 122.438 | -0.054932 | 122.2 | -0.20424 | -0.042603 | 0.0028048 | 0.025287 | -0.00063233 | -0.009675 | -0.0013051 | -0.046661 | 0.0042425 | 0.062141 | 0.050046 | -0.018583 | 0.025912 | -0.0057935 | -0.045776 | -0.054932 | 0.009155 | 0.027466 | 0.12817 | -0.027466 | 0.068665 | 0.45319 | 122.0947 | -0.050354 | 122.113 | 0.16022 | 0.09613 | 0.17395 | 0.064087 | -122.2549 | -122.1725 | 0.18311 | 0.1236 | 0.027466 | 0.05951 | -0.036621 | 0.004578 | -0.10528 | -0.086975 | 0.21515 | 0.22888 | 0.15106 | 0.2243 | 0.14648 | 0.11902 | 0.018311 | 0.21057 | 122.1634 | -0.064087 | 122.1451 | 0 | 122.1497 | -122.1909 | -122.2504 | 0.082398 | 122.168 | 0.009156 | 0.50812
2867 | 122.3419 | -0.091553 | 122.2458 | -0.10506 | -0.041321 | 0.003232 | 0.025287 | 0.0017175 | -0.008607 | -0.0034415 | -0.11075 | 0.0080877 | 0.066841 | 0.050473 | -0.017301 | 0.025699 | -0.0060071 | -0.068665 | -0.013733 | -0.027466 | -0.027466 | 0.041199 | -0.082397 | -0.004578 | 0.45319 | 122.1634 | -0.086975 | 122.0032 | 0.064087 | -0.013733 | 0.050354 | 0.064087 | -122.2595 | -122.2733 | 0.13275 | 0.086975 | 0.009156 | 0.022888 | -0.054931 | 0.004578 | -0.082398 | -0.24262 | 0.15564 | 0.14191 | 0.07782 | 0.13733 | 0.073242 | 0.068665 | 0 | 0.15106 | 122.0901 | 0.013733 | 122.2504 | 0.07782 | 122.2549 | -122.2733 | -122.3328 | 0.064087 | 122.0947 | 0.022888 | 0.54474
2868.75 | 122.4197 | -0.064087 | 122.2183 | -0.12794 | -0.044953 | 0.003232 | 0.022509 | -0.0040503 | -0.010957 | -0.0040823 | 0.029632 | 0.0065923 | 0.064704 | 0.050259 | -0.017301 | 0.026126 | -0.0040845 | -0.064087 | -0.059509 | -0.004578 | 0.041199 | 0.15564 | 0.045776 | 0.10529 | 0.6134 | 122.1359 | -0.073242 | 122.0764 | 0.1831 | 0.12817 | 0.15106 | 0.059509 | -122.2778 | -122.1771 | 0.21973 | 0.16937 | 0.10986 | 0.10986 | 0.050354 | -0.009155 | -0.082398 | -0.14191 | 0.24719 | 0.21515 | 0.19226 | 0.2243 | 0.20142 | 0.16022 | 0.045777 | 0.25635 | 122.1497 | -0.054931 | 122.2092 | 0.004578 | 122.2 | -122.2229 | -122.2916 | 0.10529 | 122.1405 | 0 | 0.67749
2870.4531 | 122.3236 | -0.10529 | 122.2275 | -0.082169 | -0.046234 | 0.00024143 | 0.024432 | 0.0017175 | -0.010743 | -0.0036551 | -0.025299 | 0.0050971 | 0.064918 | 0.049191 | -0.014951 | 0.025272 | -0.0040845 | -0.086975 | -0.027466 | -0.022888 | -0.07782 | 0.036621 | -0.068665 | 0.009155 | 0.48981 | 122.1725 | -0.10071 | 121.9757 | 0.054932 | 0.018311 | 0.027466 | 0.082398 | -122.2549 | -122.3053 | 0.14191 | 0.11444 | 0.036621 | 0.032043 | -0.045777 | 0.004578 | -0.054932 | -0.25177 | 0.16022 | 0.13275 | 0.1236 | 0.12817 | 0.11902 | 0.059509 | -0.054932 | 0.15564 | 122.0764 | -0.004578 | 122.2733 | 0.07782 | 122.2778 | -122.2504 | -122.3282 | 0.027466 | 122.081 | 0.018311 | 0.59509
2872.2188 | 122.3694 | -0.086975 | 122.2549 | -0.11269 | -0.043885 | 0.0017368 | 0.024646 | -0.0036231 | -0.0088206 | -0.0023733 | -0.09549 | 0.0055243 | 0.062995 | 0.047055 | -0.016233 | 0.028903 | -0.0017347 | -0.086975 | -0.022888 | -0.027466 | -0.041199 | 0.036621 | -0.068665 | 0.009155 | 0.50812 | 122.1634 | -0.10071 | 122.0352 | 0.091553 | 0.027466 | 0.086975 | 0.059509 | -122.2778 | -122.2961 | 0.1236 | 0.09613 | 0.01831 | 0.036621 | -0.041199 | -0.013733 | -0.091553 | -0.21973 | 0.17853 | 0.17395 | 0.11444 | 0.18768 | 0.12817 | 0.064087 | -0.013733 | 0.19226 | 122.1359 | 0.004578 | 122.2641 | 0.064087 | 122.2504 | -122.2824 | -122.3557 | 0.045776 | 122.1222 | 0 | 0.59509
2873.9219 | 122.319 | -0.11444 | 122.2412 | -0.19661 | -0.043244 | 0.0036594 | 0.026568 | -0.0014867 | -0.010743 | -0.0079275 | -0.098541 | 0.0059515 | 0.061927 | 0.041501 | -0.01602 | 0.027621 | -0.0051525 | -0.11902 | -0.009155 | -0.036621 | -0.10529 | -0.032043 | -0.14648 | -0.027466 | 0.29755 | 122.1634 | -0.09613 | 121.9894 | 0.004578 | -0.045776 | 0.036621 | 0.07782 | -122.2504 | -122.3465 | 0.082398 | 0.086975 | -0.032043 | 0.009155 | -0.10986 | 0.018311 | -0.07782 | -0.25177 | 0.11902 | 0.15106 | 0.068665 | 0.13275 | 0.050354 | 0.004578 | -0.068665 | 0.10071 | 122.0856 | 0.027466 | 122.2595 | 0.10529 | 122.2778 | -122.2778 | -122.3373 | 0.009155 | 122.1039 | -0.004578 | 0.41199
2875.6719 | 122.3511 | -0.073242 | 122.2275 | -0.12794 | -0.043457 | 0.0017368 | 0.026141 | 0.0017175 | -0.010102 | -0.0028005 | -0.1077 | 0.0059515 | 0.064491 | 0.048123 | -0.015379 | 0.027408 | -0.0051525 | -0.091553 | -0.032043 | -0.036621 | -0.022888 | 0.059509 | -0.068665 | 0.009155 | 0.48065 | 122.1222 | -0.068665 | 122.0261 | 0.07782 | 0.032043 | 0.059509 | 0.036621 | -122.2595 | -122.2504 | 0.13275 | 0.082397 | 0.004577 | 0.045776 | -0.032044 | 0.004577 | -0.10529 | -0.20142 | 0.15106 | 0.13275 | 0.10529 | 0.12817 | 0.10071 | 0.09613 | 0.013733 | 0.14649 | 122.0947 | 0.004578 | 122.1909 | 0.041199 | 122.1954 | -122.2641 | -122.2961 | 0.050354 | 122.0993 | -0.018311 | 0.55389
2877.3594 | 122.3557 | -0.091553 | 122.2092 | -0.074539 | -0.042389 | 0.0030184 | 0.026782 | -0.0017005 | -0.0081796 | -0.0045095 | -0.089386 | 0.0063787 | 0.066627 | 0.044491 | -0.015592 | 0.024417 | -0.00066651 | -0.13275 | -0.004578 | -0.050354 | -0.086975 | -0.027466 | -0.1236 | -0.032043 | 0.31586 | 122.168 | -0.086975 | 122.0078 | 0.045776 | -0.018311 | 0.073242 | 0.041199 | -122.2137 | -122.2961 | 0.064087 | 0.05951 | -0.032043 | 0.018311 | -0.073242 | 0.004578 | -0.041198 | -0.20142 | 0.13733 | 0.16479 | 0.073242 | 0.16022 | 0.068664 | 0.022888 | -0.036621 | 0.13275 | 122.0947 | 0.045776 | 122.2549 | 0.086975 | 122.2595 | -122.2595 | -122.2961 | 0.004578 | 122.0993 | -0.041198 | 0.40741
2879.1094 | 122.3877 | -0.073242 | 122.1909 | -0.16609 | -0.041962 | 0.0036594 | 0.0255 | 0.0010767 | -0.0075388 | -0.0070731 | -0.074127 | 0.0036017 | 0.065132 | 0.050473 | -0.01602 | 0.02634 | -0.0030163 | -0.1236 | -0.018311 | -0.041199 | -0.064087 | 0.018311 | -0.11902 | -0.004578 | 0.35248 | 122.1222 | -0.086975 | 122.0398 | 0.10071 | 0.059509 | 0.10986 | 0.032043 | -122.2092 | -122.2549 | 0.091553 | 0.068664 | -0.045777 | 0.036621 | -0.07782 | -0.013733 | -0.068665 | -0.15106 | 0.17395 | 0.18311 | 0.13275 | 0.19684 | 0.14648 | 0.05951 | -0.022888 | 0.18768 | 122.1268 | 0.022888 | 122.2092 | 0.054931 | 122.1954 | -122.2321 | -122.2778 | 0.009155 | 122.113 | -0.050354 | 0.42572
2880.875 | 122.3877 | -0.068665 | 122.2046 | -0.20424 | -0.044525 | 0.0030184 | 0.022723 | -0.00041873 | -0.011598 | -0.0042959 | 0.0021667 | 0.0074469 | 0.065132 | 0.047696 | -0.015806 | 0.026126 | -0.0010937 | -0.10986 | -0.059509 | -0.013733 | -0.027466 | 0.086975 | -0.045776 | 0.036621 | 0.40283 | 122.1085 | -0.082397 | 122.0398 | 0.10529 | 0.086975 | 0.10986 | 0.054932 | -122.2641 | -122.2321 | 0.15564 | 0.10529 | 0.022889 | 0.050354 | -0.032043 | -0.013732 | -0.096131 | -0.16479 | 0.17395 | 0.17853 | 0.15564 | 0.19226 | 0.16937 | 0.10071 | -0.013733 | 0.18768 | 122.1222 | -0.045776 | 122.1909 | 0.009156 | 122.1771 | -122.2183 | -122.287 | 0.041199 | 122.1085 | -0.041198 | 0.4715
2882.5781 | 122.3145 | -0.09613 | 122.2504 | -0.13557 | -0.04303 | 0.004941 | 0.02785 | 0.0019311 | -0.010743 | -0.0023733 | -0.10159 | 0.0070197 | 0.065345 | 0.052609 | -0.018156 | 0.027621 | -0.00066651 | -0.11902 | -0.004578 | -0.036621 | -0.10071 | -0.054932 | -0.15106 | -0.027466 | 0.30212 | 122.1497 | -0.091553 | 121.9711 | 0 | -0.032043 | 0.036621 | 0.059509 | -122.2549 | -122.3511 | 0.041198 | 0.068664 | -0.054932 | 0.009155 | -0.11444 | 0.004577 | -0.10071 | -0.27924 | 0.09613 | 0.13275 | 0.064087 | 0.12817 | 0.05951 | -0.018311 | -0.064087 | 0.091553 | 122.0627 | 0.032043 | 122.2412 | 0.091552 | 122.2458 | -122.287 | -122.3419 | -0.004578 | 122.0673 | -0.022889 | 0.39825
2884.3281 | 122.3831 | -0.07782 | 122.2 | -0.097427 | -0.041962 | 0.003232 | 0.022509 | -0.0053321 | -0.006898 | -0.0047231 | 0.0082703 | 0.0070197 | 0.06385 | 0.047696 | -0.014524 | 0.025272 | -0.0081433 | -0.11444 | -0.036621 | 0 | -0.045776 | 0.068665 | -0.054932 | 0.032043 | 0.4303 | 122.1268 | -0.082397 | 122.0535 | 0.10071 | 0.073242 | 0.10071 | 0.07782 | -122.2366 | -122.2458 | 0.14649 | 0.10986 | 0.022888 | 0.032043 | -0.054932 | -0.004577 | -0.073242 | -0.14648 | 0.17853 | 0.17853 | 0.15106 | 0.18311 | 0.15564 | 0.068665 | -0.045776 | 0.18311 | 122.1359 | -0.036621 | 122.2092 | 0.041199 | 122.2046 | -122.2 | -122.2824 | 0.032044 | 122.1313 | -0.036621 | 0.50812
2886.0781 | 122.4243 | -0.045776 | 122.2275 | -0.18898 | -0.043457 | 0.0045138 | 0.025287 | 0.0038537 | -0.009675 | -0.0047231 | -0.089386 | 0.0057379 | 0.062995 | 0.048337 | -0.015806 | 0.026981 | -0.0060071 | -0.10071 | -0.045776 | -0.041199 | 0.004578 | 0.086975 | -0.045776 | 0.050354 | 0.4303 | 122.1085 | -0.059509 | 122.0993 | 0.15106 | 0.09613 | 0.16022 | 0.004577 | -122.2733 | -122.2229 | 0.13275 | 0.09613 | 0 | 0.091553 | -0.004577 | -0.013733 | -0.11902 | -0.12817 | 0.19684 | 0.20599 | 0.14191 | 0.21973 | 0.15564 | 0.12817 | 0.045777 | 0.21057 | 122.1588 | -0.004577 | 122.168 | 0 | 122.1542 | -122.2687 | -122.287 | 0.050354 | 122.1451 | -0.054932 | 0.47607
2887.8438 | 122.3373 | -0.082397 | 122.2595 | -0.12794 | -0.04538 | 0.002164 | 0.023791 | 0.00064947 | -0.01117 | -0.0047231 | -0.031403 | 0.0046697 | 0.062354 | 0.045559 | -0.015592 | 0.026126 | -0.0028027 | -0.07782 | -0.041199 | -0.013733 | -0.004578 | 0.09613 | -0.018311 | 0.054932 | 0.54932 | 122.1359 | -0.064087 | 122.0032 | 0.073242 | 0.027466 | 0.041199 | 0.068664 | -122.3007 | -122.2641 | 0.17853 | 0.13733 | 0.064086 | 0.068665 | -0.004578 | 0.01831 | -0.1236 | -0.25635 | 0.15564 | 0.1236 | 0.10986 | 0.10529 | 0.091553 | 0.10986 | 0.009155 | 0.13733 | 122.0673 | -0.027466 | 122.2 | 0.041198 | 122.2183 | -122.2733 | -122.3236 | 0.077819 | 122.0856 | 0.004577 | 0.63171
2889.5312 | 122.3282 | -0.10986 | 122.2412 | -0.11269 | -0.045594 | 0.002164 | 0.023364 | -0.0038367 | -0.009675 | -0.0023733 | -0.028351 | 0.0048833 | 0.064918 | 0.049191 | -0.015379 | 0.025699 | -0.0062207 | -0.07782 | -0.041199 | -0.013733 | -0.041199 | 0.07782 | -0.032043 | 0.032043 | 0.50812 | 122.1542 | -0.082397 | 122.0078 | 0.050354 | 0.018311 | 0.027466 | 0.09613 | -122.2824 | -122.2824 | 0.18768 | 0.14191 | 0.07782 | 0.045776 | -0.01831 | 0.027466 | -0.086975 | -0.23346 | 0.16022 | 0.13733 | 0.12817 | 0.10986 | 0.10071 | 0.091553 | -0.027466 | 0.13275 | 122.0901 | -0.027466 | 122.2366 | 0.068664 | 122.2641 | -122.2549 | -122.3236 | 0.068664 | 122.1176 | 0.032043 | 0.61798
2891.2812 | 122.4518 | -0.059509 | 122.2092 | -0.21187 | -0.044739 | 0.0045138 | 0.023791 | 0.0015039 | -0.009675 | -0.0057913 | -0.055817 | 0.0055243 | 0.064277 | 0.048977 | -0.017301 | 0.026126 | -0.0047253 | -0.050354 | -0.068665 | -0.018311 | 0.045776 | 0.12817 | -0.027466 | 0.07782 | 0.45776 | 122.1176 | -0.064087 | 122.1085 | 0.16479 | 0.10529 | 0.16937 | 0.041198 | -122.2778 | -122.1634 | 0.18768 | 0.13733 | 0.032043 | 0.096131 | -0.009155 | -0.004578 | -0.091552 | -0.10071 | 0.2243 | 0.22888 | 0.16479 | 0.23346 | 0.16937 | 0.14649 | 0.064087 | 0.22888 | 122.1725 | -0.050354 | 122.1817 | -0.009156 | 122.1771 | -122.2275 | -122.2733 | 0.10528 | 122.168 | 0.009155 | 0.51727
2893.0469 | 122.438 | -0.068665 | 122.2137 | -0.12794 | -0.046234 | 0.0019504 | 0.021014 | -0.0034095 | -0.01117 | -0.0038687 | 0.0082703 | 0.0057379 | 0.063209 | 0.042782 | -0.015806 | 0.026126 | -0.0066479 | -0.068665 | -0.050354 | -0.009155 | 0.054932 | 0.16022 | 0.022888 | 0.09613 | 0.60883 | 122.1268 | -0.064087 | 122.0947 | 0.17395 | 0.15564 | 0.15564 | 0.05951 | -122.2641 | -122.1588 | 0.22888 | 0.16479 | 0.091553 | 0.10528 | 0.032043 | 0.004578 | -0.086975 | -0.11902 | 0.24261 | 0.22431 | 0.22431 | 0.21973 | 0.21973 | 0.16937 | 0.064087 | 0.23804 | 122.1588 | -0.041199 | 122.1909 | 0.018311 | 122.1954 | -122.2229 | -122.2778 | 0.1236 | 122.1634 | 0 | 0.67749
2894.7344 | 122.3557 | -0.082397 | 122.2275 | -0.074539 | -0.044525 | 0.0023776 | 0.026782 | -0.00020513 | -0.0094614 | -0.0051505 | -0.10464 | 0.0074469 | 0.064063 | 0.049405 | -0.01901 | 0.029117 | -0.0028027 | -0.14191 | -0.022888 | -0.032043 | -0.07782 | 0 | -0.12817 | -0.032043 | 0.33417 | 122.1451 | -0.10071 | 122.0398 | 0.054932 | 0.013733 | 0.091553 | 0.050354 | -122.2504 | -122.3053 | 0.082397 | 0.050354 | -0.045777 | 0 | -0.096131 | -0.018311 | -0.082397 | -0.18768 | 0.13733 | 0.17395 | 0.09613 | 0.19226 | 0.11444 | 0.032043 | -0.045777 | 0.15564 | 122.1405 | 0.009155 | 122.2458 | 0.059509 | 122.2275 | -122.2595 | -122.3282 | 0.004577 | 122.1222 | -0.05951 | 0.41656
2896.4844 | 122.3282 | -0.10071 | 122.2549 | -0.19661 | -0.041748 | 0.001523 | 0.027423 | 0.0019311 | -0.0094614 | -0.0028005 | -0.098541 | 0.0072333 | 0.0662 | 0.053677 | -0.015592 | 0.027408 | -0.0064343 | -0.14191 | -0.022888 | -0.036621 | -0.11444 | -0.059509 | -0.15564 | -0.054932 | 0.32959 | 122.1588 | -0.091553 | 121.9894 | 0.009155 | -0.050354 | 0.032043 | 0.064087 | -122.2778 | -122.3694 | 0.041199 | 0.045776 | -0.054932 | -0.018311 | -0.11902 | 0.009155 | -0.096131 | -0.2655 | 0.10986 | 0.13275 | 0.050354 | 0.1236 | 0.041199 | -0.022888 | -0.07782 | 0.10071 | 122.081 | 0.013733 | 122.2504 | 0.07782 | 122.2595 | -122.2916 | -122.3465 | -0.013733 | 122.0901 | -0.041199 | 0.4303
2898.2344 | 122.4289 | -0.032043 | 122.1725 | -0.19661 | -0.043457 | 0.0045138 | 0.024646 | -0.0038367 | -0.008607 | -0.0040823 | -0.058869 | 0.0057379 | 0.064277 | 0.048977 | -0.015165 | 0.027194 | -0.0051525 | -0.050354 | -0.054932 | 0 | 0.027466 | 0.10986 | -0.027466 | 0.059509 | 0.43945 | 122.1222 | -0.07782 | 122.1176 | 0.16937 | 0.10986 | 0.17395 | 0.032043 | -122.2275 | -122.1451 | 0.14191 | 0.091552 | 0.004577 | 0.059509 | -0.027466 | -0.045777 | -0.050354 | -0.054931 | 0.20142 | 0.20599 | 0.14191 | 0.25177 | 0.18768 | 0.10986 | 0.027466 | 0.24719 | 122.1954 | -0.054932 | 122.2 | -0.022889 | 122.1542 | -122.1725 | -122.2504 | 0.059509 | 122.1497 | -0.018311 | 0.4715
2899.9219 | 122.3557 | -0.086975 | 122.2504 | -0.097427 | -0.043244 | 0.0040866 | 0.022509 | -0.0040503 | -0.010316 | -0.0060049 | -0.025299 | 0.0050971 | 0.064704 | 0.042142 | -0.017301 | 0.027408 | -0.0034435 | -0.064087 | -0.068665 | -0.004578 | 0.013733 | 0.12817 | -0.004578 | 0.064087 | 0.57678 | 122.1085 | -0.082397 | 122.0306 | 0.10529 | 0.064087 | 0.082397 | 0.082397 | -122.319 | -122.2366 | 0.21515 | 0.15106 | 0.082397 | 0.068665 | 0 | 0.004578 | -0.14191 | -0.21973 | 0.19226 | 0.16937 | 0.15106 | 0.16479 | 0.14648 | 0.13275 | 0.018311 | 0.18768 | 122.113 | -0.064087 | 122.1909 | 0.01831 | 122.1954 | -122.2549 | -122.3328 | 0.10071 | 122.1176 | 0.022888 | 0.66376
2901.6719 | 122.3648 | -0.082397 | 122.2458 | -0.20424 | -0.04538 | 0.0034456 | 0.026996 | -0.00020513 | -0.0094614 | -0.00066434 | -0.074127 | 0.0063787 | 0.061714 | 0.051541 | -0.017515 | 0.028049 | -0.0047253 | -0.086975 | -0.045776 | -0.036621 | -0.027466 | 0.041199 | -0.068665 | 0.009155 | 0.50812 | 122.1451 | -0.091553 | 122.049 | 0.09613 | 0.018311 | 0.073242 | 0.045776 | -122.2916 | -122.2733 | 0.1236 | 0.091552 | 0.013732 | 0.045776 | -0.032044 | -0.009156 | -0.10071 | -0.19684 | 0.17853 | 0.15564 | 0.10071 | 0.16479 | 0.10986 | 0.07782 | 0.009155 | 0.18768 | 122.1405 | -0.009155 | 122.2366 | 0.036621 | 122.2275 | -122.2824 | -122.3373 | 0.054931 | 122.1313 | -0.004578 | 0.59051
2903.375 | 122.3877 | -0.059509 | 122.2458 | -0.13557 | -0.044525 | 0.003232 | 0.024218 | -0.0014867 | -0.0083932 | -0.0015189 | -0.089386 | 0.0057379 | 0.062141 | 0.057095 | -0.016447 | 0.028903 | -0.0049389 | -0.11444 | -0.013733 | -0.041199 | -0.07782 | 0.009155 | -0.10529 | -0.009155 | 0.35248 | 122.1359 | -0.073242 | 122.0535 | 0.09613 | 0.036621 | 0.11444 | 0.01831 | -122.2595 | -122.3236 | 0.068664 | 0.050354 | -0.045777 | 0.032044 | -0.064087 | -0.013733 | -0.10986 | -0.19226 | 0.15564 | 0.17395 | 0.09613 | 0.18768 | 0.10986 | 0.050354 | -0.036621 | 0.16937 | 122.1268 | 0.027466 | 122.2092 | 0.045776 | 122.1954 | -122.287 | -122.319 | -0.018311 | 122.113 | -0.054932 | 0.41199
2905.1406 | 122.319 | -0.091553 | 122.2321 | -0.10506 | -0.041962 | 0.004941 | 0.025927 | -0.0012731 | -0.0094614 | -0.0053641 | -0.09549 | 0.0053107 | 0.064277 | 0.041928 | -0.018156 | 0.028903 | -0.0075025 | -0.10071 | -0.009155 | -0.041199 | -0.045776 | 0.036621 | -0.10529 | -0.013733 | 0.41199 | 122.1725 | -0.086975 | 122.0123 | 0.036621 | -0.018311 | 0.045776 | 0.050354 | -122.2412 | -122.2778 | 0.12817 | 0.07782 | -0.013733 | 0.027466 | -0.064087 | 0.004578 | -0.05951 | -0.21973 | 0.12817 | 0.13733 | 0.073242 | 0.13275 | 0.068664 | 0.07782 | -0.004577 | 0.1236 | 122.0993 | 0.032044 | 122.2595 | 0.082398 | 122.2641 | -122.2733 | -122.319 | 0.045777 | 122.1039 | -0.009155 | 0.50354
2906.9062 | 122.3145 | -0.10986 | 122.2641 | -0.20424 | -0.043885 | 0.0045138 | 0.02785 | -0.00041873 | -0.0083932 | -0.0055777 | -0.11075 | 0.0050971 | 0.066413 | 0.048764 | -0.016447 | 0.026767 | -0.0055799 | -0.10071 | -0.032043 | -0.027466 | -0.041199 | 0.041199 | -0.091553 | -0.004578 | 0.4303 | 122.1405 | -0.082397 | 122.0032 | 0.036621 | -0.018311 | 0.032043 | 0.082397 | -122.2961 | -122.3053 | 0.15106 | 0.10529 | 0.01831 | 0.022888 | -0.064087 | 0.027466 | -0.1236 | -0.26093 | 0.14648 | 0.14191 | 0.091552 | 0.11444 | 0.064086 | 0.068665 | -0.013733 | 0.11902 | 122.0856 | -0.004577 | 122.2229 | 0.07782 | 122.2504 | -122.2916 | -122.3465 | 0.068664 | 122.113 | 0.009155 | 0.54016
2908.6094 | 122.2961 | -0.10529 | 122.2641 | -0.051651 | -0.046448 | 0.0030184 | 0.023364 | -0.00020513 | -0.01117 | -0.00023714 | -0.034454 | 0.0042425 | 0.064918 | 0.042569 | -0.016874 | 0.026767 | -0.0017347 | -0.14648 | -0.013733 | -0.045776 | -0.082397 | 0.018311 | -0.086975 | -0.013733 | 0.46692 | 122.1817 | -0.10071 | 121.9757 | 0.050354 | -0.004578 | 0.018311 | 0.05951 | -122.2778 | -122.3465 | 0.1236 | 0.091553 | 0.018311 | 0.032043 | -0.041199 | 0.004578 | -0.082397 | -0.28839 | 0.15564 | 0.1236 | 0.10071 | 0.11902 | 0.09613 | 0.064087 | -0.036621 | 0.15106 | 122.0764 | 0.032043 | 122.2824 | 0.091553 | 122.287 | -122.3099 | -122.3648 | 0.022889 | 122.081 | -0.041198 | 0.5722
2910.3594 | 122.3007 | -0.11444 | 122.2504 | -0.16609 | -0.042389 | 0.0036594 | 0.024646 | 0.00022207 | -0.0088206 | -0.0017325 | -0.10464 | 0.0061651 | 0.063423 | 0.053891 | -0.014097 | 0.028903 | -0.0072889 | -0.1236 | -0.013733 | -0.054932 | -0.11444 | -0.054932 | -0.17853 | -0.045776 | 0.31586 | 122.1817 | -0.09613 | 121.9986 | 0.018311 | -0.045776 | 0.032043 | 0.059509 | -122.2641 | -122.3648 | 0.059509 | 0.068665 | -0.064087 | 0.009156 | -0.1236 | 0.018311 | -0.068664 | -0.25177 | 0.13275 | 0.14648 | 0.068665 | 0.12817 | 0.050354 | 0 | -0.059509 | 0.11444 | 122.0947 | 0.041199 | 122.2778 | 0.10071 | 122.2961 | -122.3053 | -122.3465 | 0 | 122.113 | -0.009155 | 0.4303
2912.125 | 122.3419 | -0.09613 | 122.2733 | -0.13557 | -0.043885 | 0.0025912 | 0.025287 | 0.0025721 | -0.01117 | -0.0064321 | -0.074127 | 0.0080877 | 0.063423 | 0.050473 | -0.015592 | 0.027835 | -0.0042981 | -0.13275 | -0.018311 | -0.059509 | -0.09613 | 0 | -0.13733 | -0.032043 | 0.3067 | 122.1497 | -0.10529 | 121.9986 | 0.036621 | -0.013733 | 0.050354 | 0.036621 | -122.2916 | -122.3694 | 0.09613 | 0.064087 | -0.041199 | 0.027466 | -0.07782 | -0.009156 | -0.1236 | -0.27466 | 0.13275 | 0.14648 | 0.082397 | 0.15564 | 0.091553 | 0.059509 | -0.036621 | 0.14191 | 122.1039 | 0.041198 | 122.2549 | 0.077819 | 122.2458 | -122.3328 | -122.3785 | 0 | 122.0947 | -0.036621 | 0.40283
2913.8281 | 122.3511 | -0.10071 | 122.2641 | -0.11269 | -0.04538 | 0.0034456 | 0.025073 | 0.0015039 | -0.010743 | -0.0045095 | -0.049713 | 0.0070197 | 0.065132 | 0.048977 | -0.016233 | 0.028903 | -0.0028027 | -0.11902 | -0.009155 | -0.041199 | -0.086975 | 0.009155 | -0.086975 | -0.013733 | 0.46692 | 122.1909 | -0.10071 | 122.0306 | 0.059509 | 0.009155 | 0.059509 | 0.059509 | -122.2733 | -122.3511 | 0.10986 | 0.086975 | 0.013733 | 0.027466 | -0.045776 | 0 | -0.073242 | -0.23346 | 0.16022 | 0.16022 | 0.10986 | 0.16022 | 0.10986 | 0.050354 | -0.045776 | 0.16022 | 122.1313 | 0.032044 | 122.2916 | 0.091553 | 122.2916 | -122.3053 | -122.3648 | 0.013733 | 122.1313 | -0.018311 | 0.56763
2915.5781 | 122.4701 | -0.068665 | 122.2229 | -0.12794 | -0.047089 | 0.0023776 | 0.021869 | 0.0021447 | -0.013307 | -0.0038687 | 0.035736 | 0.0063787 | 0.064704 | 0.041073 | -0.017729 | 0.025058 | -0.0038709 | -0.073242 | -0.073242 | -0.022888 | 0.041199 | 0.1831 | 0.045776 | 0.1236 | 0.60883 | 122.113 | -0.064087 | 122.113 | 0.19684 | 0.15564 | 0.15106 | 0.045777 | -122.2961 | -122.1817 | 0.25177 | 0.19226 | 0.11444 | 0.14648 | 0.068664 | 0.004578 | -0.10986 | -0.10986 | 0.2655 | 0.21973 | 0.22431 | 0.21515 | 0.21973 | 0.20599 | 0.064087 | 0.26093 | 122.1771 | -0.050354 | 122.1771 | -0.004577 | 122.1817 | -122.2458 | -122.287 | 0.10986 | 122.1817 | -0.004577 | 0.67749
2917.3281 | 122.3923 | -0.064087 | 122.2366 | -0.18135 | -0.043671 | 0.0019504 | 0.0255 | -0.0017005 | -0.0098886 | -0.0045095 | -0.0039367 | 0.0055243 | 0.06385 | 0.057095 | -0.01602 | 0.026981 | -0.0045117 | -0.091553 | -0.064087 | 0.018311 | -0.009155 | 0.10529 | -0.036621 | 0.059509 | 0.43945 | 122.113 | -0.068665 | 122.0627 | 0.10986 | 0.07782 | 0.10986 | 0.082398 | -122.3007 | -122.2458 | 0.16937 | 0.1236 | 0.027466 | 0.041198 | -0.054932 | -0.004578 | -0.1236 | -0.17395 | 0.17395 | 0.17395 | 0.14191 | 0.17853 | 0.14649 | 0.086975 | -0.027466 | 0.17853 | 122.1313 | -0.082398 | 122.1817 | 0 | 122.1771 | -122.2183 | -122.3053 | 0.054932 | 122.1268 | -0.027466 | 0.50354
2919.0938 | 122.4014 | -0.07782 | 122.2321 | -0.13557 | -0.045166 | 0.0028048 | 0.023791 | 0.00043587 | -0.012025 | -0.0032277 | -0.022247 | 0.0048833 | 0.064491 | 0.042569 | -0.016447 | 0.02634 | -0.0040845 | -0.10986 | -0.036621 | -0.027466 | -0.027466 | 0.064087 | -0.045776 | 0.036621 | 0.42572 | 122.113 | -0.073242 | 122.0398 | 0.10071 | 0.059509 | 0.10986 | 0.050354 | -122.2687 | -122.2595 | 0.14191 | 0.11444 | 0.032044 | 0.064087 | -0.01831 | 0.004578 | -0.11902 | -0.19226 | 0.17853 | 0.18768 | 0.13733 | 0.18311 | 0.13275 | 0.091553 | 0 | 0.17395 | 122.113 | -0.009155 | 122.1863 | 0.041199 | 122.1909 | -122.2595 | -122.3053 | 0.050354 | 122.1176 | -0.032043 | 0.50354
2920.7969 | 122.3648 | -0.09613 | 122.2137 | -0.16609 | -0.046021 | 0.0034456 | 0.026355 | 0.00064947 | -0.0092478 | -0.0017325 | -0.098541 | 0.0053107 | 0.064491 | 0.053677 | -0.017301 | 0.028262 | -0.0057935 | -0.086975 | -0.036621 | -0.041199 | -0.032043 | 0.054932 | -0.068665 | 0.013733 | 0.5127 | 122.1725 | -0.09613 | 122.0535 | 0.091553 | 0.022888 | 0.082397 | 0.054931 | -122.2504 | -122.2458 | 0.15106 | 0.10986 | 0.027465 | 0.054932 | -0.027466 | 0 | -0.041199 | -0.16022 | 0.18768 | 0.17853 | 0.11902 | 0.17853 | 0.11902 | 0.096131 | 0.009156 | 0.18768 | 122.1497 | 0.004578 | 122.2687 | 0.059509 | 122.2687 | -122.2549 | -122.3099 | 0.064087 | 122.1497 | 0.009155 | 0.60882
2922.5625 | 122.319 | -0.073242 | 122.2824 | -0.12032 | -0.044739 | 0.0043002 | 0.027423 | -0.00020513 | -0.0081796 | -0.0057913 | -0.10464 | 0.0057379 | 0.064491 | 0.053464 | -0.019438 | 0.027621 | -0.0028027 | -0.09613 | -0.004578 | -0.045776 | -0.059509 | 0.032043 | -0.11902 | -0.032043 | 0.39825 | 122.1863 | -0.073242 | 122.0169 | 0.018311 | -0.050354 | 0.032043 | 0.027466 | -122.287 | -122.3419 | 0.10529 | 0.041199 | -0.045777 | 0.013733 | -0.073243 | 0 | -0.096131 | -0.2655 | 0.091553 | 0.10529 | 0.022888 | 0.10529 | 0.022888 | 0.077819 | -0.013733 | 0.091553 | 122.0901 | 0.041198 | 122.2595 | 0.068664 | 122.2595 | -122.3282 | -122.3557 | 0.013733 | 122.0901 | -0.022888 | 0.4715
2924.2812 | 122.3557 | -0.082397 | 122.2275 | -0.11269 | -0.042176 | 0.003232 | 0.025714 | -0.00041873 | -0.0090342 | -0.0053641 | -0.092438 | 0.0044561 | 0.062141 | 0.046414 | -0.01666 | 0.02869 | -0.0049389 | -0.073242 | -0.009155 | -0.032043 | -0.032043 | 0.068665 | -0.068665 | 0.022888 | 0.48981 | 122.1588 | -0.086975 | 122.0352 | 0.07782 | 0.027466 | 0.082397 | 0.050354 | -122.2366 | -122.2595 | 0.15106 | 0.10528 | 0.013732 | 0.054931 | -0.036622 | -0.004578 | -0.068665 | -0.19226 | 0.16022 | 0.16479 | 0.10986 | 0.16937 | 0.11444 | 0.10071 | 0 | 0.16479 | 122.1222 | 0.022888 | 122.2458 | 0.073242 | 122.2412 | -122.2595 | -122.3145 | 0.050354 | 122.1176 | 0.009155 | 0.5722
2926.0312 | 122.4289 | -0.045776 | 122.2092 | -0.082169 | -0.04538 | 0.0013094 | 0.019732 | 0.0015039 | -0.01117 | -0.0030141 | -0.016144 | 0.0053107 | 0.064704 | 0.047909 | -0.01602 | 0.026767 | -0.0025891 | -0.064087 | -0.064087 | 0.004578 | 0.032043 | 0.14648 | 0.027466 | 0.10071 | 0.60883 | 122.113 | -0.050354 | 122.0947 | 0.17395 | 0.13275 | 0.14648 | 0.050354 | -122.2733 | -122.1771 | 0.19226 | 0.14648 | 0.073242 | 0.09613 | 0.022888 | -0.004578 | -0.09613 | -0.11444 | 0.21973 | 0.19226 | 0.17853 | 0.19684 | 0.18311 | 0.14191 | 0.027465 | 0.2243 | 122.1451 | -0.068665 | 122.1634 | -0.018311 | 122.1588 | -122.2046 | -122.2595 | 0.077819 | 122.1405 | -0.018311 | 0.6546
2927.7812 | 122.3007 | -0.10071 | 122.2641 | -0.15083 | -0.041962 | 0.0051546 | 0.025927 | 0.00086307 | -0.010957 | -0.0049367 | -0.1077 | 0.0057379 | 0.064063 | 0.045132 | -0.018369 | 0.028476 | -0.0053661 | -0.10986 | -0.022888 | -0.045776 | -0.07782 | -0.013733 | -0.14191 | -0.041199 | 0.36621 | 122.1497 | -0.086975 | 121.9803 | 0.018311 | -0.041199 | 0.022888 | 0.054932 | -122.287 | -122.3419 | 0.086975 | 0.059509 | -0.041199 | 0.004577 | -0.096131 | 0.013733 | -0.11444 | -0.28381 | 0.11902 | 0.1236 | 0.059509 | 0.10986 | 0.045776 | 0.032043 | -0.032044 | 0.10529 | 122.0673 | 0.022888 | 122.2366 | 0.07782 | 122.2504 | -122.3099 | -122.3511 | 0.022888 | 122.081 | -0.009155 | 0.46692
2929.5469 | 122.3328 | -0.11444 | 122.2458 | -0.074539 | -0.045807 | 0.0010958 | 0.024218 | -0.00084593 | -0.0092478 | -0.0019461 | -0.055817 | 0.0068059 | 0.064491 | 0.044919 | -0.01666 | 0.026553 | -0.0060071 | -0.14191 | -0.009155 | -0.068665 | -0.11444 | -0.022888 | -0.09613 | -0.022888 | 0.47607 | 122.1954 | -0.09613 | 121.9894 | 0.032043 | -0.009155 | 0.032043 | 0.045776 | -122.2549 | -122.3602 | 0.091553 | 0.091553 | 0.018311 | 0.045777 | -0.027465 | 0.018311 | -0.050354 | -0.25635 | 0.14648 | 0.14648 | 0.10529 | 0.12817 | 0.086975 | 0.045777 | -0.045776 | 0.12817 | 122.0856 | 0.05951 | 122.2916 | 0.10529 | 122.3099 | -122.3145 | -122.3419 | 0 | 122.1039 | -0.027466 | 0.59052
2931.2969 | 122.3145 | -0.068665 | 122.2595 | -0.1432 | -0.042816 | 0.0025912 | 0.025927 | 0.0017175 | -0.010743 | -0.0060049 | -0.098541 | 0.0057379 | 0.06385 | 0.049191 | -0.015379 | 0.029544 | -0.0036573 | -0.086975 | -0.027466 | -0.045776 | -0.054932 | 0.032043 | -0.09613 | -0.013733 | 0.42114 | 122.1909 | -0.07782 | 122.0123 | 0.036621 | -0.009155 | 0.041199 | 0.022889 | -122.287 | -122.3145 | 0.10071 | 0.054932 | -0.027465 | 0.032043 | -0.050354 | -0.009155 | -0.068664 | -0.24719 | 0.10529 | 0.10986 | 0.05951 | 0.11902 | 0.068665 | 0.077819 | -0.009156 | 0.11444 | 122.0901 | 0.01831 | 122.2687 | 0.041199 | 122.2595 | -122.3053 | -122.3373 | 0.013733 | 122.081 | -0.01831 | 0.48981
2933.0469 | 122.3419 | -0.086975 | 122.2412 | -0.1432 | -0.043457 | 0.0043002 | 0.024432 | 0.0032129 | -0.0090342 | -0.0017325 | -0.080231 | 0.0061651 | 0.062995 | 0.049832 | -0.015592 | 0.028476 | -0.0034435 | -0.12817 | -0.022888 | -0.041199 | -0.09613 | -0.004578 | -0.11444 | -0.032043 | 0.32959 | 122.1542 | -0.11902 | 122.0261 | 0.064087 | 0.004578 | 0.082397 | 0.045776 | -122.2641 | -122.3373 | 0.082397 | 0.054932 | -0.027466 | 0.009156 | -0.073242 | -0.032044 | -0.086975 | -0.21515 | 0.15106 | 0.16937 | 0.091553 | 0.20142 | 0.1236 | 0.036621 | -0.054931 | 0.18311 | 122.1451 | 0.018311 | 122.2733 | 0.064087 | 122.2412 | -122.2824 | -122.3602 | -0.009155 | 122.113 | -0.041199 | 0.41656
2934.7344 | 122.4518 | -0.032043 | 122.2183 | -0.2195 | -0.043244 | 0.0040866 | 0.023578 | -0.0027685 | -0.0073252 | -0.0051505 | -0.04361 | 0.0059515 | 0.065772 | 0.047268 | -0.016874 | 0.025912 | -0.0047253 | -0.045776 | -0.054932 | 0.013733 | 0.036621 | 0.12817 | -0.018311 | 0.073242 | 0.46692 | 122.1313 | -0.032043 | 122.1039 | 0.15564 | 0.11902 | 0.16937 | 0.045776 | -122.2733 | -122.1817 | 0.16022 | 0.10529 | 0.013732 | 0.059509 | -0.032044 | 0 | -0.086975 | -0.11444 | 0.18768 | 0.20142 | 0.15106 | 0.20142 | 0.15106 | 0.11444 | 0.022888 | 0.18768 | 122.1359 | -0.068665 | 122.1634 | -0.022889 | 122.1634 | -122.2046 | -122.2504 | 0.068664 | 122.1359 | -0.013733 | 0.49896
2936.4844 | 122.4243 | -0.059509 | 122.2366 | -0.15083 | -0.043885 | 0.0017368 | 0.026568 | 8.47e-06 | -0.0094614 | -0.0038687 | -0.083283 | 0.0036017 | 0.062995 | 0.048977 | -0.018156 | 0.026981 | -0.0034435 | -0.1236 | -0.018311 | -0.036621 | -0.041199 | 0.059509 | -0.10071 | 0.009155 | 0.38452 | 122.1542 | -0.07782 | 122.0856 | 0.12817 | 0.068665 | 0.13733 | 0.022888 | -122.2549 | -122.2778 | 0.11902 | 0.068664 | -0.041199 | 0.045776 | -0.064087 | -0.018311 | -0.082397 | -0.15106 | 0.18768 | 0.19684 | 0.12817 | 0.21515 | 0.14649 | 0.09613 | -0.004578 | 0.20599 | 122.1634 | 0.01831 | 122.2321 | 0.041198 | 122.2137 | -122.2733 | -122.3145 | 0.01831 | 122.1451 | -0.064087 | 0.44403
2938.2344 | 122.4564 | -0.064087 | 122.2046 | -0.12794 | -0.043671 | 0.0010958 | 0.021228 | -0.0012731 | -0.010316 | -0.0028005 | 0.0021667 | 0.0033881 | 0.063636 | 0.046628 | -0.017729 | 0.025912 | -0.0066479 | -0.050354 | -0.064087 | -0.004578 | 0.022888 | 0.16479 | 0.018311 | 0.10529 | 0.6134 | 122.1222 | -0.059509 | 122.1039 | 0.19684 | 0.15564 | 0.16022 | 0.059509 | -122.2687 | -122.1817 | 0.22888 | 0.16937 | 0.082398 | 0.10986 | 0.022889 | 0.004578 | -0.082398 | -0.10071 | 0.26093 | 0.2243 | 0.21973 | 0.21973 | 0.21515 | 0.16937 | 0.027466 | 0.25635 | 122.1634 | -0.059509 | 122.1817 | 0 | 122.1863 | -122.2092 | -122.2641 | 0.086975 | 122.168 | 0.013733 | 0.67749
2939.9375 | 122.3785 | -0.073242 | 122.2412 | -0.13557 | -0.042603 | 0.0028048 | 0.026355 | 0.0019311 | -0.008607 | -0.0036551 | -0.089386 | 0.0046697 | 0.064704 | 0.051541 | -0.01901 | 0.027835 | -0.0053661 | -0.07782 | -0.027466 | -0.032043 | -0.027466 | 0.050354 | -0.07782 | 0.018311 | 0.51727 | 122.1588 | -0.082397 | 122.0535 | 0.082397 | 0.045776 | 0.09613 | 0.041199 | -122.2687 | -122.2687 | 0.1236 | 0.091553 | -0.004578 | 0.050354 | -0.045777 | -0.009155 | -0.082398 | -0.18768 | 0.15564 | 0.16937 | 0.11902 | 0.17853 | 0.12817 | 0.082397 | 0.004577 | 0.16479 | 122.1359 | 0.004577 | 122.2412 | 0.045776 | 122.2321 | -122.2733 | -122.3236 | 0.045776 | 122.1268 | -0.004578 | 0.59052
2941.7031 | 122.3099 | -0.082397 | 122.2504 | -0.097427 | -0.041962 | 0.0062228 | 0.025287 | 0.00064947 | -0.010316 | -0.0032277 | -0.098541 | 0.0044561 | 0.064491 | 0.058377 | -0.01602 | 0.029117 | -0.0062207 | -0.11444 | -0.022888 | -0.045776 | -0.07782 | -0.009155 | -0.14191 | -0.036621 | 0.35248 | 122.2 | -0.091553 | 122.0032 | 0 | -0.068665 | 0.032043 | 0.036621 | -122.2733 | -122.3282 | 0.073242 | 0.045776 | -0.05951 | 0.009155 | -0.096131 | -0.009156 | -0.050354 | -0.24719 | 0.082397 | 0.11444 | 0.013732 | 0.1236 | 0.022888 | 0.036621 | -0.032044 | 0.091553 | 122.0947 | 0.022888 | 122.2916 | 0.059509 | 122.2824 | -122.2961 | -122.3419 | 0.004577 | 122.0856 | -0.032044 | 0.43488
2943.4062 | 122.4518 | -0.045776 | 122.2137 | -0.12794 | -0.046875 | 0.0019504 | 0.023364 | 0.0017175 | -0.008607 | -0.0045095 | 0.020477 | 0.0048833 | 0.064704 | 0.047696 | -0.017301 | 0.025058 | -0.0051525 | -0.07782 | -0.064087 | 0 | 0.041199 | 0.16937 | 0.027466 | 0.091553 | 0.60883 | 122.1359 | -0.064087 | 122.1222 | 0.19684 | 0.15564 | 0.15106 | 0.045776 | -122.2778 | -122.1725 | 0.21515 | 0.13733 | 0.073242 | 0.091553 | 0.027466 | -0.018311 | -0.07782 | -0.091553 | 0.24261 | 0.19684 | 0.20142 | 0.21515 | 0.21973 | 0.16937 | 0.041199 | 0.26093 | 122.1863 | -0.064087 | 122.2 | -0.018311 | 122.1817 | -122.2137 | -122.2778 | 0.086975 | 122.168 | -0.032044 | 0.6546
2945.1562 | 122.438 | -0.050354 | 122.1954 | -0.17372 | -0.043457 | 0.0034456 | 0.024432 | 0.00043587 | -0.0088206 | -0.0066457 | -0.06192 | 0.0050971 | 0.062354 | 0.053677 | -0.018583 | 0.026767 | -0.0042981 | -0.09613 | -0.041199 | -0.027466 | -0.004578 | 0.091553 | -0.068665 | 0.032043 | 0.4303 | 122.1313 | -0.059509 | 122.1176 | 0.15106 | 0.10529 | 0.17395 | 0.022888 | -122.2366 | -122.2 | 0.14191 | 0.082397 | -0.018311 | 0.059509 | -0.041199 | -0.009155 | -0.064087 | -0.07782 | 0.20142 | 0.2243 | 0.15564 | 0.23346 | 0.16479 | 0.11902 | 0.022888 | 0.21057 | 122.1771 | -0.013733 | 122.1909 | 0.009155 | 122.1817 | -122.2229 | -122.2549 | 0.045776 | 122.168 | -0.045776 | 0.48065
2946.9219 | 122.3602 | -0.10071 | 122.2183 | -0.15083 | -0.043671 | 0.0040866 | 0.026568 | 0.00064947 | -0.011384 | -0.0028005 | -0.09549 | 0.0046697 | 0.063636 | 0.0509 | -0.017942 | 0.026981 | -0.0055799 | -0.11902 | -0.013733 | -0.036621 | -0.086975 | -0.004578 | -0.13275 | -0.032043 | 0.32959 | 122.1863 | -0.07782 | 122.0306 | 0.059509 | -0.004578 | 0.064087 | 0.064087 | -122.2321 | -122.3053 | 0.09613 | 0.068665 | -0.032043 | 0.004578 | -0.09613 | 0.022888 | -0.032044 | -0.18768 | 0.16022 | 0.1648 | 0.09613 | 0.14191 | 0.073242 | 0.032043 | -0.050354 | 0.13733 | 122.1085 | 0.022888 | 122.2641 | 0.086975 | 122.287 | -122.2549 | -122.2961 | 0.013733 | 122.1313 | -0.018311 | 0.4303
2948.6719 | 122.3053 | -0.091553 | 122.2595 | -0.15083 | -0.044098 | 0.003873 | 0.027636 | -0.0010595 | -0.0088206 | -0.0032277 | -0.092438 | 0.0068059 | 0.063423 | 0.051114 | -0.018156 | 0.02634 | -0.0030163 | -0.10529 | -0.036621 | -0.041199 | -0.064087 | 0.018311 | -0.13275 | -0.036621 | 0.37079 | 122.1725 | -0.086975 | 121.994 | 0.027466 | -0.036621 | 0.036621 | 0.050354 | -122.2961 | -122.3236 | 0.10986 | 0.054932 | -0.041198 | 0.004578 | -0.091552 | 0.004578 | -0.086975 | -0.2655 | 0.11902 | 0.12817 | 0.054932 | 0.1236 | 0.050354 | 0.05951 | -0.022888 | 0.11444 | 122.081 | 0.004578 | 122.2595 | 0.054932 | 122.2641 | -122.3007 | -122.3465 | 0.027466 | 122.0856 | -0.013733 | 0.46234
2950.3594 | 122.4152 | -0.073242 | 122.2229 | -0.16609 | -0.042176 | 0.0040866 | 0.023364 | -0.0014867 | -0.010316 | -0.0038687 | -0.025299 | 0.0061651 | 0.065772 | 0.04385 | -0.017301 | 0.027408 | -0.0064343 | -0.073242 | -0.064087 | 0.009155 | 0.022888 | 0.12817 | -0.036621 | 0.07782 | 0.46692 | 122.1176 | -0.045776 | 122.0901 | 0.13275 | 0.10529 | 0.13733 | 0.082397 | -122.287 | -122.2 | 0.20142 | 0.15106 | 0.036621 | 0.068665 | -0.045776 | 0.027466 | -0.10528 | -0.13275 | 0.20599 | 0.21057 | 0.17853 | 0.18311 | 0.15106 | 0.11902 | 0.013733 | 0.17853 | 122.1359 | -0.073242 | 122.1634 | 0.009155 | 122.1909 | -122.2137 | -122.2687 | 0.09613 | 122.1634 | 0 | 0.54016
2952.125 | 122.319 | -0.10529 | 122.2595 | -0.097427 | -0.044739 | 0.00045503 | 0.023791 | -0.00063233 | -0.01053 | -0.0021597 | -0.049713 | 0.0059515 | 0.06385 | 0.051541 | -0.018797 | 0.02634 | -0.0087841 | -0.16022 | -0.004578 | -0.045776 | -0.086975 | 0 | -0.09613 | -0.027466 | 0.47607 | 122.1588 | -0.10986 | 121.9849 | 0.036621 | -0.009155 | 0.013733 | 0.05951 | -122.2641 | -122.3465 | 0.10529 | 0.07782 | 0.009156 | 0.01831 | -0.050354 | -0.004577 | -0.10071 | -0.27466 | 0.14191 | 0.11902 | 0.096131 | 0.1236 | 0.10071 | 0.045776 | -0.041199 | 0.14648 | 122.0947 | 0.041198 | 122.2687 | 0.10071 | 122.2641 | -122.3053 | -122.3694 | 0.018311 | 122.0901 | -0.054931 | 0.58136
2953.9062 | 122.438 | -0.059509 | 122.2 | -0.15083 | -0.044098 | 0.0019504 | 0.020587 | 0.00022207 | -0.010957 | -0.0021597 | 0.017425 | 0.0065923 | 0.064918 | 0.05325 | -0.014951 | 0.025272 | -0.0045117 | -0.12817 | -0.059509 | -0.022888 | -0.027466 | 0.073242 | -0.032043 | 0.041199 | 0.46692 | 122.1176 | -0.086975 | 122.0718 | 0.13275 | 0.10986 | 0.1236 | 0.036621 | -122.2595 | -122.2275 | 0.13275 | 0.10071 | 0.027466 | 0.064087 | -0.009155 | -0.027466 | -0.082397 | -0.12817 | 0.19226 | 0.1831 | 0.16937 | 0.21057 | 0.19684 | 0.09613 | -0.004578 | 0.21973 | 122.1588 | -0.036621 | 122.2046 | 0 | 122.1771 | -122.2229 | -122.287 | 0.032043 | 122.1313 | -0.068665 | 0.52643
2955.6562 | 122.3282 | -0.10529 | 122.287 | -0.12794 | -0.043885 | 0.0023776 | 0.026782 | -0.00020513 | -0.012879 | -0.0032277 | -0.11685 | 0.0080877 | 0.063209 | 0.051114 | -0.01666 | 0.027621 | -0.0045117 | -0.15106 | -0.022888 | -0.041199 | -0.10529 | -0.041199 | -0.13733 | -0.032043 | 0.31128 | 122.1817 | -0.10071 | 121.9986 | 0.018311 | -0.041199 | 0.032043 | 0.064087 | -122.3099 | -122.3923 | 0.064087 | 0.073243 | -0.032043 | 0.009156 | -0.09613 | 0.004578 | -0.10528 | -0.28839 | 0.1236 | 0.13733 | 0.064087 | 0.13275 | 0.059509 | 0 | -0.064087 | 0.11902 | 122.0993 | 0.018311 | 122.2824 | 0.082398 | 122.287 | -122.3282 | -122.3877 | 0 | 122.1039 | -0.045776 | 0.41656
2957.3438 | 122.4197 | -0.064087 | 122.2275 | -0.16609 | -0.044525 | 0.0023776 | 0.023791 | -0.0057593 | -0.010316 | -0.0042959 | -0.0008851 | 0.0068059 | 0.062568 | 0.038937 | -0.016874 | 0.027408 | -0.0032299 | -0.09613 | -0.041199 | -0.022888 | -0.045776 | 0.07782 | -0.045776 | 0.045776 | 0.45319 | 122.1405 | -0.082397 | 122.0718 | 0.13275 | 0.10986 | 0.11902 | 0.041199 | -122.2687 | -122.2733 | 0.14191 | 0.10986 | 0.018311 | 0.068664 | -0.022888 | -0.01831 | -0.086975 | -0.15564 | 0.19684 | 0.18311 | 0.17395 | 0.20142 | 0.19226 | 0.10071 | -0.022888 | 0.21515 | 122.1542 | -0.018311 | 122.2229 | 0.022888 | 122.2046 | -122.2504 | -122.3099 | 0.018311 | 122.1359 | -0.032043 | 0.51727
2959.1094 | 122.4335 | -0.054932 | 122.2321 | -0.15083 | -0.04538 | 0.003232 | 0.022509 | -0.0021277 | -0.010957 | -0.0038687 | -0.019196 | 0.0059515 | 0.06385 | 0.047482 | -0.018797 | 0.025485 | -0.0040845 | -0.068665 | -0.073242 | -0.004578 | 0.036621 | 0.15106 | 0.018311 | 0.10071 | 0.6134 | 122.1313 | -0.059509 | 122.1039 | 0.16479 | 0.12817 | 0.15106 | 0.050354 | -122.3053 | -122.1954 | 0.20599 | 0.15564 | 0.073243 | 0.10529 | 0.022889 | -0.004577 | -0.10071 | -0.12817 | 0.21973 | 0.20599 | 0.18311 | 0.21057 | 0.18768 | 0.15564 | 0.041199 | 0.2243 | 122.1634 | -0.068664 | 122.1909 | -0.01831 | 122.1863 | -122.2366 | -122.2916 | 0.091553 | 122.1588 | -0.013733 | 0.66834
2960.7969 | 122.374 | -0.10071 | 122.2504 | -0.089798 | -0.044739 | 0.0025912 | 0.026568 | 0.0034265 | -0.0094614 | -0.0038687 | -0.11075 | 0.0061651 | 0.063636 | 0.056241 | -0.017301 | 0.026981 | -0.00045291 | -0.10071 | -0.013733 | -0.045776 | -0.032043 | 0.036621 | -0.07782 | 0.009155 | 0.50354 | 122.1725 | -0.082397 | 122.0444 | 0.10071 | 0.009155 | 0.073242 | 0.054932 | -122.2641 | -122.2824 | 0.13733 | 0.10986 | 0.022888 | 0.054931 | -0.032044 | 0.018311 | -0.07782 | -0.20599 | 0.20142 | 0.17395 | 0.10986 | 0.15564 | 0.091552 | 0.082397 | 0.013733 | 0.18311 | 122.1268 | 0.032043 | 122.2549 | 0.086975 | 122.2733 | -122.2961 | -122.3328 | 0.068665 | 122.1451 | 0 | 0.60425
2962.5469 | 122.3831 | -0.07782 | 122.2229 | -0.17372 | -0.045166 | 0.0013094 | 0.022082 | -0.0049047 | -0.011384 | -0.0013051 | -0.01004 | 0.0044561 | 0.065345 | 0.0509 | -0.017088 | 0.028476 | -0.0034435 | -0.073242 | -0.054932 | -0.004578 | 0.022888 | 0.14191 | 0.009155 | 0.082397 | 0.59509 | 122.1771 | -0.064087 | 122.049 | 0.13733 | 0.07782 | 0.10071 | 0.073242 | -122.2778 | -122.2 | 0.21973 | 0.16022 | 0.086975 | 0.086975 | 0.013733 | 0.013733 | -0.045776 | -0.17395 | 0.21515 | 0.17853 | 0.15564 | 0.1648 | 0.14191 | 0.14649 | 0.027466 | 0.20142 | 122.113 | -0.050354 | 122.2412 | 0.022888 | 122.2549 | -122.2275 | -122.287 | 0.10071 | 122.1268 | 0.004578 | 0.67291
2964.3125 | 122.3282 | -0.10071 | 122.2549 | -0.1432 | -0.044953 | 0.00088223 | 0.023791 | -0.0021277 | -0.01053 | -0.0013051 | -0.025299 | 0.0061651 | 0.064491 | 0.046841 | -0.017088 | 0.027194 | -0.0079297 | -0.091553 | -0.064087 | -0.022888 | -0.045776 | 0.041199 | -0.073242 | 0.004578 | 0.5127 | 122.1497 | -0.09613 | 122.0032 | 0.059509 | -0.004578 | 0.018311 | 0.07782 | -122.319 | -122.3007 | 0.14191 | 0.10529 | 0.027466 | 0.027466 | -0.050354 | 0.004578 | -0.10529 | -0.25177 | 0.16022 | 0.11902 | 0.09613 | 0.11444 | 0.091552 | 0.064087 | -0.022888 | 0.15564 | 122.0993 | -0.041199 | 122.2458 | 0.036621 | 122.2504 | -122.2778 | -122.3511 | 0.054932 | 122.1039 | 0.009155 | 0.6134
2966 | 122.3648 | -0.086975 | 122.2549 | -0.10506 | -0.04303 | 0.0043002 | 0.026355 | 0.00022207 | -0.01053 | -0.0034415 | -0.10464 | 0.0076605 | 0.06385 | 0.047268 | -0.017515 | 0.02933 | -0.0075025 | -0.07782 | -0.013733 | -0.045776 | -0.027466 | 0.041199 | -0.064087 | 0.018311 | 0.50354 | 122.1588 | -0.09613 | 122.0444 | 0.091553 | 0.032043 | 0.068665 | 0.041199 | -122.2687 | -122.2824 | 0.12817 | 0.10529 | 0.022888 | 0.064087 | -0.018311 | -0.009155 | -0.096131 | -0.21057 | 0.17853 | 0.15564 | 0.11902 | 0.16479 | 0.12817 | 0.086975 | 0.01831 | 0.18768 | 122.1405 | 0.032043 | 122.2549 | 0.073242 | 122.2458 | -122.3007 | -122.3511 | 0.059509 | 122.1313 | 0.009155 | 0.59052
2967.75 | 122.4243 | -0.064087 | 122.2687 | -0.15846 | -0.046021 | 0.002164 | 0.023791 | 8.47e-06 | -0.01053 | -0.0066457 | 0.017425 | 0.0040289 | 0.06385 | 0.03851 | -0.015592 | 0.02634 | -0.0047253 | -0.10071 | -0.032043 | -0.032043 | -0.036621 | 0.073242 | -0.050354 | 0.045776 | 0.47607 | 122.1176 | -0.068665 | 122.0947 | 0.12817 | 0.091553 | 0.11902 | 0.032044 | -122.3007 | -122.3053 | 0.13733 | 0.10986 | 0.013733 | 0.077819 | -0.018311 | -0.004578 | -0.15106 | -0.17395 | 0.19226 | 0.18311 | 0.15564 | 0.18768 | 0.16022 | 0.10529 | -0.004578 | 0.19684 | 122.1634 | 0 | 122.1863 | 0.032044 | 122.1817 | -122.3007 | -122.3373 | 0.027466 | 122.1588 | -0.036621 | 0.54016
2969.4531 | 122.406 | -0.073242 | 122.1954 | -0.12032 | -0.043671 | 0.0010958 | 0.024218 | -0.0014867 | -0.01117 | -0.0049367 | -0.0039367 | 0.0057379 | 0.063636 | 0.051968 | -0.014951 | 0.027621 | -0.0013073 | -0.10071 | -0.050354 | 0.004578 | -0.036621 | 0.054932 | -0.059509 | 0.050354 | 0.45319 | 122.1497 | -0.082397 | 122.0627 | 0.1236 | 0.082397 | 0.11444 | 0.07782 | -122.2458 | -122.2321 | 0.12817 | 0.1236 | 0.013733 | 0.045776 | -0.064087 | -0.009155 | -0.045777 | -0.13275 | 0.19684 | 0.18768 | 0.15564 | 0.19684 | 0.16479 | 0.050354 | -0.041199 | 0.20599 | 122.1451 | -0.054932 | 122.2321 | 0.022888 | 122.2229 | -122.1909 | -122.2778 | 0.036621 | 122.1359 | -0.027466 | 0.52643
2971.2031 | 122.3694 | -0.10071 | 122.2321 | -0.15083 | -0.044739 | 0.0023776 | 0.02785 | 0.0027857 | -0.010102 | -0.0034415 | -0.11685 | 0.0059515 | 0.065986 | 0.053891 | -0.018156 | 0.026553 | -0.0068615 | -0.09613 | -0.013733 | -0.036621 | -0.027466 | 0.054932 | -0.064087 | -0.004578 | 0.52643 | 122.1542 | -0.07782 | 122.0627 | 0.10071 | 0.032043 | 0.086975 | 0.064087 | -122.2458 | -122.2595 | 0.15564 | 0.09613 | 0.036621 | 0.032043 | -0.027466 | 0.022888 | -0.07782 | -0.16937 | 0.20142 | 0.18768 | 0.13275 | 0.16479 | 0.10986 | 0.091553 | 0.009155 | 0.17853 | 122.1405 | 0.022888 | 122.2321 | 0.086975 | 122.2549 | -122.2687 | -122.3099 | 0.073242 | 122.1634 | 0.004578 | 0.62714
2972.9688 | 122.4243 | -0.064087 | 122.2092 | -0.13557 | -0.044098 | 0.002164 | 0.022082 | -0.00020513 | -0.010316 | -0.0060049 | -0.0069885 | 0.0065923 | 0.064277 | 0.046628 | -0.014951 | 0.026981 | -0.0060071 | -0.10071 | -0.041199 | -0.022888 | -0.018311 | 0.068665 | -0.041199 | 0.054932 | 0.47607 | 122.1405 | -0.07782 | 122.1039 | 0.16479 | 0.10071 | 0.14648 | 0.041199 | -122.2504 | -122.2275 | 0.13275 | 0.11902 | 0.022888 | 0.07782 | -0.018311 | -0.013733 | -0.068664 | -0.10528 | 0.22888 | 0.21057 | 0.1648 | 0.2243 | 0.17853 | 0.091553 | 0.004577 | 0.24261 | 122.1817 | -0.018311 | 122.2183 | 0.022888 | 122.2046 | -122.2321 | -122.287 | 0.045776 | 122.168 | -0.036621 | 0.54016
2974.6562 | 122.3785 | -0.073242 | 122.2549 | -0.15083 | -0.042816 | 0.003232 | 0.023791 | 0.0010767 | -0.010957 | -0.0019461 | -0.1199 | 0.0057379 | 0.065559 | 0.049405 | -0.017942 | 0.028903 | -0.0023755 | -0.082397 | -0.027466 | -0.027466 | -0.022888 | 0.045776 | -0.059509 | 0.018311 | 0.5127 | 122.168 | -0.086975 | 122.0718 | 0.10986 | 0.041199 | 0.086975 | 0.045776 | -122.2824 | -122.2778 | 0.11902 | 0.091553 | 0.013733 | 0.045777 | -0.032043 | -0.013733 | -0.086975 | -0.18311 | 0.18311 | 0.16022 | 0.11444 | 0.17395 | 0.12817 | 0.073242 | 0.004578 | 0.19684 | 122.1588 | 0 | 122.2549 | 0.045776 | 122.2412 | -122.2824 | -122.3419 | 0.050354 | 122.1451 | -0.009155 | 0.58594
2976.4062 | 122.374 | -0.10071 | 122.2412 | -0.051651 | -0.045594 | 0.0019504 | 0.026355 | 0.0017175 | -0.010102 | -0.0051505 | -0.080231 | 0.0038153 | 0.06385 | 0.048337 | -0.017088 | 0.028049 | -0.0038709 | -0.10529 | -0.004578 | -0.045776 | -0.073242 | 0 | -0.10071 | -0.018311 | 0.48523 | 122.1817 | -0.10071 | 122.0398 | 0.091553 | -0.004578 | 0.068665 | 0.054932 | -122.2458 | -122.3145 | 0.10071 | 0.082397 | 0 | 0.027465 | -0.054932 | 0 | -0.059509 | -0.20142 | 0.19226 | 0.16937 | 0.09613 | 0.16937 | 0.09613 | 0.045776 | -0.027466 | 0.19226 | 122.1405 | 0.041198 | 122.2824 | 0.09613 | 122.2824 | -122.287 | -122.3419 | 0.027466 | 122.1405 | -0.004578 | 0.58594
2978.0938 | 122.374 | -0.086975 | 122.2275 | -0.1432 | -0.044312 | 0.0030184 | 0.026782 | -0.0014867 | -0.0077524 | -0.0051505 | -0.09549 | 0.0068059 | 0.064704 | 0.050686 | -0.014524 | 0.029758 | -0.0055799 | -0.1236 | -0.013733 | -0.041199 | -0.086975 | 0.009155 | -0.1236 | -0.018311 | 0.3479 | 122.1634 | -0.086975 | 122.0627 | 0.07782 | 0.013733 | 0.068665 | 0.045776 | -122.2412 | -122.3145 | 0.09613 | 0.068664 | -0.036621 | 0.022888 | -0.082397 | 0 | -0.064087 | -0.16479 | 0.16479 | 0.15564 | 0.10071 | 0.15564 | 0.10071 | 0.050354 | -0.045776 | 0.16479 | 122.1497 | 0.027466 | 122.2504 | 0.073242 | 122.2504 | -122.2687 | -122.3145 | 0 | 122.1497 | -0.036621 | 0.43488
2979.8438 | 122.3511 | -0.10529 | 122.2275 | -0.17372 | -0.042816 | 0.003232 | 0.025714 | -0.0042639 | -0.009675 | -0.0042959 | -0.14127 | 0.0057379 | 0.062995 | 0.051755 | -0.016233 | 0.026553 | -0.0055799 | -0.12817 | 0.004578 | -0.041199 | -0.10071 | 0 | -0.13275 | -0.032043 | 0.33417 | 122.168 | -0.10529 | 122.0352 | 0.059509 | -0.018311 | 0.050354 | 0.064087 | -122.2229 | -122.3282 | 0.10529 | 0.073243 | -0.027465 | 0.009156 | -0.091552 | 0 | -0.059509 | -0.19226 | 0.16479 | 0.15564 | 0.086975 | 0.15564 | 0.086975 | 0.041199 | -0.059509 | 0.16479 | 122.1405 | 0.045777 | 122.2733 | 0.10986 | 122.2733 | -122.2687 | -122.3328 | 0.004578 | 122.1405 | -0.022888 | 0.43945
2981.6094 | 122.438 | -0.050354 | 122.2046 | -0.12032 | -0.044525 | 0.0010958 | 0.022296 | -0.0036231 | -0.010743 | -0.0025869 | 0.014374 | 0.0048833 | 0.062354 | 0.04321 | -0.015806 | 0.027835 | -0.0057935 | -0.07782 | -0.054932 | -0.004578 | 0.050354 | 0.16479 | 0.036621 | 0.09613 | 0.61798 | 122.1222 | -0.054932 | 122.1313 | 0.17853 | 0.14191 | 0.15106 | 0.045776 | -122.2595 | -122.1542 | 0.21515 | 0.14648 | 0.086975 | 0.10071 | 0.041199 | -0.004578 | -0.082398 | -0.073242 | 0.22888 | 0.20142 | 0.19226 | 0.20599 | 0.19684 | 0.16937 | 0.054932 | 0.23346 | 122.1863 | -0.050354 | 122.1771 | -0.004578 | 122.1725 | -122.2092 | -122.2595 | 0.10071 | 122.1817 | -0.027466 | 0.66834
2983.3125 | 122.3373 | -0.091553 | 122.2504 | -0.12032 | -0.04538 | 0.0023776 | 0.023364 | -0.00063233 | -0.010316 | -0.0057913 | -0.052765 | 0.0046697 | 0.065345 | 0.041714 | -0.017515 | 0.026553 | -0.0049389 | -0.10071 | -0.045776 | -0.013733 | -0.059509 | 0.054932 | -0.064087 | 0.013733 | 0.49439 | 122.1405 | -0.09613 | 122.0215 | 0.068665 | 0.004578 | 0.041199 | 0.07782 | -122.2961 | -122.3099 | 0.14649 | 0.10529 | 0.027466 | 0.027466 | -0.050354 | -0.004577 | -0.10986 | -0.22888 | 0.16022 | 0.13275 | 0.096131 | 0.13733 | 0.10071 | 0.068665 | -0.045776 | 0.16479 | 122.1176 | -0.032043 | 122.2366 | 0.045777 | 122.2321 | -122.2641 | -122.3465 | 0.032044 | 122.113 | -0.009155 | 0.58594
2985.0781 | 122.3236 | -0.10529 | 122.2641 | -0.16609 | -0.044525 | 0.0025912 | 0.026355 | -0.0053321 | -0.012239 | -0.0030141 | -0.1138 | 0.0063787 | 0.064277 | 0.049832 | -0.018156 | 0.028049 | -0.0032299 | -0.11902 | -0.018311 | -0.036621 | -0.10529 | -0.027466 | -0.16479 | -0.050354 | 0.32501 | 122.168 | -0.10529 | 122.0215 | 0.027466 | -0.045776 | 0.032043 | 0.068665 | -122.2824 | -122.3694 | 0.07782 | 0.054932 | -0.059509 | -0.013733 | -0.12817 | 0 | -0.09613 | -0.24262 | 0.13275 | 0.13733 | 0.05951 | 0.13733 | 0.05951 | 0.009155 | -0.068665 | 0.13275 | 122.1268 | 0.01831 | 122.2733 | 0.086975 | 122.2733 | -122.3007 | -122.3694 | 0 | 122.1268 | -0.013733 | 0.4303
2986.7656 | 122.3328 | -0.10529 | 122.2687 | -0.082169 | -0.044739 | 0.0010958 | 0.023364 | -0.0027685 | -0.012452 | -0.0017325 | -0.046661 | 0.0063787 | 0.062782 | 0.053036 | -0.016447 | 0.027408 | -0.0017347 | -0.10529 | -0.032043 | -0.032043 | -0.064087 | 0.036621 | -0.07782 | 0.004578 | 0.52185 | 122.1634 | -0.1236 | 122.0078 | 0.050354 | 0.022888 | 0.018311 | 0.073243 | -122.3007 | -122.3328 | 0.14191 | 0.10986 | 0.027466 | 0.036621 | -0.045777 | -0.01831 | -0.10529 | -0.26093 | 0.15564 | 0.1236 | 0.12817 | 0.14191 | 0.14648 | 0.068664 | -0.032044 | 0.17395 | 122.1313 | 0 | 122.287 | 0.073243 | 122.2687 | -122.3007 | -122.3923 | 0.041199 | 122.113 | 0 | 0.62714
2988.5156 | 122.4106 | -0.073242 | 122.2412 | -0.12032 | -0.044739 | 0.0028048 | 0.022509 | 0.00086307 | -0.0083932 | -0.0068593 | 0.0021667 | 0.0038153 | 0.064491 | 0.049191 | -0.018369 | 0.026553 | -0.0053661 | -0.10986 | -0.041199 | -0.009155 | -0.036621 | 0.059509 | -0.064087 | 0.041199 | 0.45776 | 122.113 | -0.064087 | 122.0764 | 0.10986 | 0.07782 | 0.11902 | 0.064087 | -122.2824 | -122.2778 | 0.13275 | 0.11444 | 0.009155 | 0.050354 | -0.054932 | 0.009155 | -0.12817 | -0.1648 | 0.18311 | 0.19226 | 0.15106 | 0.18311 | 0.14191 | 0.068664 | -0.027466 | 0.17395 | 122.1405 | -0.032044 | 122.1771 | 0.032043 | 122.1863 | -122.2504 | -122.3053 | 0.036621 | 122.1497 | -0.036621 | 0.53101
2990.2031 | 122.3602 | -0.068665 | 122.2504 | -0.16609 | -0.044525 | 0.0025912 | 0.024218 | -0.0025549 | -0.010743 | -0.0060049 | -0.13821 | 0.0083013 | 0.065345 | 0.053036 | -0.018583 | 0.027408 | -0.0057935 | -0.086975 | -0.027466 | -0.036621 | -0.022888 | 0.073242 | -0.064087 | 0.004578 | 0.50354 | 122.1542 | -0.073242 | 122.0718 | 0.086975 | 0.027466 | 0.082397 | 0.032044 | -122.2778 | -122.2733 | 0.14191 | 0.073243 | 0.004578 | 0.041199 | -0.027466 | -0.004577 | -0.09613 | -0.17853 | 0.15564 | 0.15106 | 0.096131 | 0.15564 | 0.10071 | 0.10986 | 0.013733 | 0.16022 | 122.1451 | 0.009155 | 122.2275 | 0.041199 | 122.2229 | -122.287 | -122.3236 | 0.045777 | 122.1405 | -0.01831 | 0.5722
2991.9688 | 122.406 | -0.050354 | 122.2275 | -0.18898 | -0.042176 | 0.002164 | 0.022937 | -0.0057593 | -0.010957 | -0.0045095 | -0.025299 | 0.0068059 | 0.064277 | 0.057309 | -0.014951 | 0.02634 | -0.0032299 | -0.086975 | -0.068665 | -0.004578 | -0.013733 | 0.10529 | -0.036621 | 0.054932 | 0.43488 | 122.1039 | -0.068665 | 122.0947 | 0.10986 | 0.086975 | 0.10986 | 0.045776 | -122.2961 | -122.2412 | 0.15564 | 0.10529 | 0.013733 | 0.05951 | -0.032043 | -0.018311 | -0.1236 | -0.13275 | 0.16022 | 0.16022 | 0.13733 | 0.17853 | 0.15564 | 0.10986 | -0.009155 | 0.17853 | 122.1634 | -0.064087 | 122.1725 | -0.018311 | 122.1542 | -122.2321 | -122.2961 | 0.036621 | 122.1451 | -0.036621 | 0.48523
2993.7344 | 122.4335 | -0.059509 | 122.2366 | -0.15846 | -0.042603 | 0.0030184 | 0.024859 | 0.0012903 | -0.0071116 | -0.0040823 | -0.071076 | 0.0078741 | 0.062995 | 0.047909 | -0.017301 | 0.027194 | -0.0032299 | -0.064087 | -0.059509 | 0 | 0.041199 | 0.13733 | -0.018311 | 0.068665 | 0.48065 | 122.1359 | -0.068665 | 122.1359 | 0.16479 | 0.12817 | 0.16022 | 0.059509 | -122.2961 | -122.1954 | 0.19684 | 0.12817 | 0.041198 | 0.068665 | -0.018311 | -0.009156 | -0.10071 | -0.10071 | 0.2243 | 0.21973 | 0.18768 | 0.22888 | 0.19684 | 0.13733 | 0.041199 | 0.23346 | 122.2046 | -0.059509 | 122.2046 | 0 | 122.1954 | -122.2366 | -122.3053 | 0.10071 | 122.1954 | -0.004578 | 0.54016
2995.4844 | 122.3145 | -0.10071 | 122.2778 | -0.18135 | -0.042603 | 0.003873 | 0.027636 | -0.00063233 | -0.011384 | -0.0032277 | -0.1077 | 0.0055243 | 0.064491 | 0.051541 | -0.016447 | 0.027408 | -0.0049389 | -0.12817 | -0.013733 | -0.032043 | -0.09613 | -0.041199 | -0.16479 | -0.036621 | 0.32501 | 122.1405 | -0.09613 | 122.0352 | 0.018311 | -0.050354 | 0.036621 | 0.068665 | -122.2916 | -122.374 | 0.059509 | 0.064087 | -0.064087 | -0.004578 | -0.13275 | 0.004578 | -0.13733 | -0.24262 | 0.11902 | 0.13733 | 0.050354 | 0.13275 | 0.045776 | -0.009156 | -0.064087 | 0.11444 | 122.1313 | 0.01831 | 122.2366 | 0.086975 | 122.2412 | -122.3099 | -122.374 | 0.004578 | 122.1359 | -0.027466 | 0.42572
2997.1875 | 122.3602 | -0.086975 | 122.2549 | -0.11269 | -0.043671 | 0.0025912 | 0.024218 | -0.00041873 | -0.010316 | -0.0025869 | -0.083283 | 0.0061651 | 0.064918 | 0.050473 | -0.01602 | 0.026126 | -0.0051525 | -0.1236 | -0.009155 | -0.032043 | -0.068665 | -0.004578 | -0.091553 | -0.009155 | 0.46692 | 122.1634 | -0.086975 | 122.0352 | 0.082397 | 0.022888 | 0.068665 | 0.054932 | -122.2641 | -122.3236 | 0.082397 | 0.07782 | -0.004578 | 0.022888 | -0.05951 | 0 | -0.091553 | -0.21973 | 0.16937 | 0.15564 | 0.10986 | 0.15564 | 0.10986 | 0.027465 | -0.036622 | 0.16937 | 122.1222 | 0.022888 | 122.2504 | 0.07782 | 122.2504 | -122.287 | -122.3419 | 0.01831 | 122.1222 | -0.036621 | 0.55389
2998.9531 | 122.4197 | -0.064087 | 122.2549 | -0.18898 | -0.044739 | 0.0023776 | 0.02315 | -0.0031957 | -0.011598 | -0.0036551 | -0.016144 | 0.0061651 | 0.063209 | 0.050046 | -0.015806 | 0.028903 | -0.0055799 | -0.10529 | -0.050354 | -0.027466 | -0.009155 | 0.064087 | -0.041199 | 0.041199 | 0.48065 | 122.1222 | -0.07782 | 122.0901 | 0.13733 | 0.10071 | 0.1236 | 0.036621 | -122.3053 | -122.2641 | 0.12817 | 0.10529 | 0.022888 | 0.068665 | -0.013733 | -0.013733 | -0.13275 | -0.16479 | 0.20142 | 0.18768 | 0.1648 | 0.20142 | 0.17853 | 0.091553 | 0.018311 | 0.21515 | 122.168 | -0.022888 | 122.2 | 0.013733 | 122.1863 | -122.2824 | -122.3328 | 0.054932 | 122.1542 | -0.041199 | 0.54474
3000.7188 | 122.4197 | -0.041199 | 122.2275 | -0.097427 | -0.044739 | 0.0010958 | 0.023791 | -0.00063233 | -0.010957 | -0.0034415 | -0.037506 | 0.0050971 | 0.065772 | 0.051968 | -0.01666 | 0.02634 | -0.0036573 | -0.10071 | -0.054932 | -0.018311 | -0.027466 | 0.059509 | -0.050354 | 0.032043 | 0.45776 | 122.1222 | -0.073242 | 122.0947 | 0.13733 | 0.091553 | 0.1236 | 0.022888 | -122.2824 | -122.2549 | 0.10071 | 0.073242 | -0.009155 | 0.050354 | -0.032043 | -0.032043 | -0.10529 | -0.13275 | 0.17853 | 0.16479 | 0.13275 | 0.19684 | 0.16479 | 0.07782 | -0.009155 | 0.21057 | 122.168 | -0.036621 | 122.1954 | -0.013733 | 122.1634 | -122.2458 | -122.3007 | 0.013733 | 122.1359 | -0.059509 | 0.49896
3002.4844 | 122.4609 | -0.054932 | 122.2 | -0.12794 | -0.046662 | 0.00088223 | 0.021869 | -0.0017005 | -0.0088206 | -0.0049367 | -0.0039367 | 0.0061651 | 0.063209 | 0.047482 | -0.016874 | 0.025485 | -0.0038709 | -0.10071 | -0.059509 | -0.013733 | -0.009155 | 0.086975 | -0.018311 | 0.068665 | 0.52643 | 122.1176 | -0.082397 | 122.1268 | 0.16022 | 0.11444 | 0.14191 | 0.041199 | -122.2595 | -122.2092 | 0.14191 | 0.1236 | 0.036621 | 0.082398 | -0.004578 | -0.027465 | -0.082397 | -0.073242 | 0.21515 | 0.19684 | 0.16937 | 0.2243 | 0.19684 | 0.10071 | 0.004578 | 0.24261 | 122.2092 | -0.045776 | 122.2 | -0.004577 | 122.1725 | -122.2137 | -122.2824 | 0.045777 | 122.1817 | -0.045776 | 0.58136
3004.1875 | 122.4518 | -0.036621 | 122.2366 | -0.12794 | -0.04538 | 0.002164 | 0.023791 | -0.0021277 | -0.01117 | -0.0053641 | -0.019196 | 0.0048833 | 0.064491 | 0.047482 | -0.015165 | 0.025485 | -0.0057935 | -0.050354 | -0.054932 | -0.004578 | 0.059509 | 0.16937 | 0.022888 | 0.09613 | 0.64545 | 122.1359 | -0.050354 | 122.1359 | 0.18768 | 0.14648 | 0.15564 | 0.032043 | -122.2916 | -122.1771 | 0.20599 | 0.13275 | 0.059509 | 0.10071 | 0.027466 | -0.013733 | -0.10071 | -0.10071 | 0.2243 | 0.19226 | 0.18311 | 0.20599 | 0.19684 | 0.17395 | 0.064087 | 0.23804 | 122.1863 | -0.050354 | 122.1863 | -0.018311 | 122.1725 | -122.2412 | -122.287 | 0.09613 | 122.1725 | -0.013733 | 0.68207
3005.9375 | 122.4472 | -0.054932 | 122.2412 | -0.12032 | -0.046662 | 0.0010958 | 0.0255 | 0.00043587 | -0.012666 | -0.0045095 | -0.025299 | 0.0048833 | 0.064704 | 0.049618 | -0.019438 | 0.028262 | -0.0070751 | -0.091553 | -0.045776 | -0.018311 | 0 | 0.082397 | -0.004578 | 0.050354 | 0.50354 | 122.1405 | -0.073242 | 122.1085 | 0.14191 | 0.13275 | 0.14648 | 0.036621 | -122.287 | -122.2412 | 0.13733 | 0.10529 | 0.050354 | 0.068665 | 0.013733 | -0.01831 | -0.10071 | -0.13275 | 0.19684 | 0.20142 | 0.18768 | 0.21973 | 0.20599 | 0.10071 | 0.018311 | 0.21515 | 122.1817 | -0.027465 | 122.2137 | 0.009156 | 122.1954 | -122.2595 | -122.3145 | 0.054932 | 122.1634 | -0.036621 | 0.55847
3007.6875 | 122.3785 | -0.054932 | 122.2366 | -0.17372 | -0.041107 | 0.0023776 | 0.025927 | -0.0010595 | -0.0083932 | -0.0045095 | -0.068024 | 0.0061651 | 0.062568 | 0.049832 | -0.018369 | 0.026553 | -0.0036573 | -0.068665 | -0.050354 | 0.004578 | 0.022888 | 0.12817 | -0.032043 | 0.064087 | 0.46234 | 122.1268 | -0.045776 | 122.1039 | 0.11444 | 0.082397 | 0.13275 | 0.05951 | -122.287 | -122.2137 | 0.18311 | 0.11902 | 0.022889 | 0.059509 | -0.036621 | 0.009156 | -0.10986 | -0.13275 | 0.16937 | 0.18768 | 0.13733 | 0.17853 | 0.12817 | 0.1236 | 0.01831 | 0.16022 | 122.1497 | -0.054932 | 122.1725 | 0.004578 | 122.1817 | -122.2321 | -122.2824 | 0.07782 | 122.1588 | -0.013733 | 0.51727
3009.4531 | 122.3145 | -0.10529 | 122.2687 | -0.12794 | -0.047089 | 0.0019504 | 0.025287 | -0.0064001 | -0.010743 | -0.0038687 | -0.083283 | 0.0057379 | 0.065345 | 0.053464 | -0.01602 | 0.026553 | -0.0045117 | -0.14648 | -0.018311 | -0.059509 | -0.07782 | -0.009155 | -0.09613 | -0.022888 | 0.46692 | 122.1863 | -0.07782 | 122.0032 | 0.036621 | -0.004578 | 0.018311 | 0.045777 | -122.287 | -122.3465 | 0.096131 | 0.082398 | 0.009156 | 0.036621 | -0.036621 | 0.027466 | -0.082398 | -0.2655 | 0.14191 | 0.1236 | 0.10071 | 0.096131 | 0.073242 | 0.050354 | -0.018311 | 0.11444 | 122.081 | 0.041198 | 122.2641 | 0.086975 | 122.2916 | -122.3282 | -122.3465 | 0.027466 | 122.1085 | -0.041198 | 0.5722
3011.1562 | 122.3328 | -0.10071 | 122.2595 | -0.18898 | -0.043457 | 0.0030184 | 0.028491 | 0.0015039 | -0.010102 | -0.0049367 | -0.13211 | 0.0068059 | 0.062568 | 0.049618 | -0.017942 | 0.027408 | -0.0040845 | -0.10986 | 0.018311 | -0.032043 | -0.091553 | -0.027466 | -0.15106 | -0.036621 | 0.31586 | 122.1909 | -0.091553 | 122.0352 | 0.018311 | -0.027466 | 0.027466 | 0.068665 | -122.2412 | -122.3511 | 0.073242 | 0.064087 | -0.050354 | -0.004578 | -0.11902 | 0.009155 | -0.068664 | -0.2243 | 0.11902 | 0.12817 | 0.073242 | 0.11902 | 0.064087 | 0.004577 | -0.05951 | 0.10986 | 122.1268 | 0.050354 | 122.2824 | 0.11902 | 122.2916 | -122.2916 | -122.3511 | 0.009155 | 122.1359 | -0.009155 | 0.41657
3012.9062 | 122.3694 | -0.07782 | 122.2321 | -0.15846 | -0.044312 | 0.0017368 | 0.026996 | -0.0023413 | -0.009675 | -0.0032277 | -0.13516 | 0.0085149 | 0.062568 | 0.048764 | -0.016874 | 0.027194 | -0.0040845 | -0.07782 | -0.018311 | -0.041199 | -0.022888 | 0.064087 | -0.082397 | 0.018311 | 0.5127 | 122.1817 | -0.073242 | 122.0764 | 0.10071 | 0.032043 | 0.091553 | 0.036621 | -122.2504 | -122.2549 | 0.14191 | 0.096131 | -0.004577 | 0.05951 | -0.041198 | 0.004578 | -0.050354 | -0.15564 | 0.17853 | 0.16937 | 0.10986 | 0.16479 | 0.10529 | 0.10529 | 0.018311 | 0.17395 | 122.1497 | 0.022888 | 122.2549 | 0.059509 | 122.2595 | -122.2733 | -122.3053 | 0.054932 | 122.1542 | 0 | 0.59052
3014.6719 | 122.4792 | -0.050354 | 122.2321 | -0.1432 | -0.044953 | 0.00045503 | 0.024218 | -0.0021277 | -0.010957 | -0.0051505 | -0.0069885 | 0.0033881 | 0.062141 | 0.047909 | -0.016447 | 0.026126 | -0.0062207 | -0.059509 | -0.045776 | -0.004578 | 0.050354 | 0.17395 | 0.036621 | 0.10529 | 0.63629 | 122.1405 | -0.064087 | 122.1542 | 0.20142 | 0.16022 | 0.15106 | 0.045776 | -122.2778 | -122.1817 | 0.2243 | 0.15564 | 0.086975 | 0.10986 | 0.041199 | -0.013733 | -0.091553 | -0.07782 | 0.25177 | 0.20142 | 0.21057 | 0.21515 | 0.2243 | 0.17853 | 0.054932 | 0.2655 | 122.2183 | -0.041198 | 122.2046 | 0.004578 | 122.1909 | -122.2366 | -122.2961 | 0.10071 | 122.2046 | -0.009155 | 0.68665
3016.4219 | 122.406 | -0.064087 | 122.2549 | -0.15083 | -0.041321 | 0.0040866 | 0.021441 | 0.00064947 | -0.0092478 | -0.0057913 | -0.031403 | 0.0057379 | 0.063423 | 0.052182 | -0.01602 | 0.026126 | -0.0040845 | -0.064087 | -0.059509 | 0.009155 | 0.027466 | 0.13733 | -0.022888 | 0.064087 | 0.48065 | 122.1176 | -0.045776 | 122.113 | 0.13275 | 0.09613 | 0.13733 | 0.073242 | -122.3145 | -122.2275 | 0.20142 | 0.12817 | 0.041199 | 0.054932 | -0.032043 | 0.018311 | -0.13733 | -0.14191 | 0.19684 | 0.20142 | 0.16022 | 0.18311 | 0.14191 | 0.12817 | 0.018311 | 0.17853 | 122.1588 | -0.068664 | 122.1634 | 0.004578 | 122.1817 | -122.2458 | -122.3007 | 0.091553 | 122.1771 | 0 | 0.54474
3018.125 | 122.4747 | -0.045776 | 122.2458 | -0.15846 | -0.04538 | 0.00088223 | 0.022723 | -0.0017005 | -0.010316 | -0.0047231 | -0.028351 | 0.0053107 | 0.062782 | 0.045559 | -0.017942 | 0.025912 | -0.0036573 | -0.068665 | -0.050354 | -0.013733 | 0.045776 | 0.16479 | 0.032043 | 0.10986 | 0.62714 | 122.1359 | -0.064087 | 122.1588 | 0.21057 | 0.16937 | 0.16937 | 0.032043 | -122.2961 | -122.2 | 0.21057 | 0.15564 | 0.077819 | 0.1236 | 0.045776 | -0.018311 | -0.10986 | -0.086976 | 0.25635 | 0.21515 | 0.21515 | 0.23346 | 0.23346 | 0.17853 | 0.059509 | 0.27466 | 122.2229 | -0.036621 | 122.2 | -0.004578 | 122.1817 | -122.2595 | -122.3099 | 0.091552 | 122.2046 | -0.022889 | 0.67291
3019.8906 | 122.3694 | -0.086975 | 122.2504 | -0.11269 | -0.043885 | 0.0023776 | 0.026141 | 0.0032129 | -0.0094614 | -0.0045095 | -0.071076 | 0.0048833 | 0.063636 | 0.049405 | -0.018156 | 0.026981 | -0.0051525 | -0.086975 | -0.027466 | -0.022888 | -0.036621 | 0.054932 | -0.082397 | 0.013733 | 0.50812 | 122.1634 | -0.073242 | 122.081 | 0.091553 | 0.022888 | 0.07782 | 0.064087 | -122.2778 | -122.287 | 0.14191 | 0.10071 | 0.004578 | 0.036621 | -0.059509 | 0.013733 | -0.086975 | -0.16937 | 0.17853 | 0.16479 | 0.10986 | 0.15106 | 0.09613 | 0.07782 | -0.013733 | 0.16479 | 122.1542 | -0.004578 | 122.2366 | 0.059509 | 122.2504 | -122.2733 | -122.3236 | 0.050354 | 122.168 | 0 | 0.59509
3021.6406 | 122.3648 | -0.086975 | 122.2458 | -0.15846 | -0.044098 | 0.0034456 | 0.026355 | 0.0017175 | -0.012452 | -0.0053641 | -0.10159 | 0.0072333 | 0.065345 | 0.05325 | -0.017942 | 0.029117 | -0.0072889 | -0.09613 | -0.032043 | -0.045776 | -0.032043 | 0.07782 | -0.07782 | 0.022888 | 0.5127 | 122.1771 | -0.091553 | 122.0856 | 0.10071 | 0.032043 | 0.086975 | 0.041199 | -122.2778 | -122.2778 | 0.16479 | 0.10986 | 0.009155 | 0.068664 | -0.032044 | -0.004578 | -0.068665 | -0.16022 | 0.18768 | 0.17395 | 0.11902 | 0.17853 | 0.1236 | 0.1236 | 0.013733 | 0.19226 | 122.1771 | 0.013733 | 122.2687 | 0.054932 | 122.2641 | -122.2916 | -122.3373 | 0.054932 | 122.1725 | -0.009155 | 0.59967
3023.3281 | 122.319 | -0.11444 | 122.2549 | -0.16609 | -0.042603 | 0.0025912 | 0.026355 | -0.00041873 | -0.0088206 | -0.0017325 | -0.12601 | 0.0055243 | 0.063209 | 0.0462 | -0.01602 | 0.028049 | -0.0066479 | -0.13733 | -0.009155 | -0.054932 | -0.086975 | -0.032043 | -0.15106 | -0.045776 | 0.34332 | 122.1634 | -0.09613 | 122.0215 | 0.009155 | -0.050354 | 0.018311 | 0.059509 | -122.2641 | -122.3419 | 0.082398 | 0.068665 | -0.036621 | 0.009156 | -0.09613 | 0.018311 | -0.091553 | -0.23346 | 0.1236 | 0.13275 | 0.064087 | 0.11444 | 0.045776 | 0.022889 | -0.032043 | 0.10528 | 122.1176 | 0.045777 | 122.2595 | 0.10529 | 122.2778 | -122.3099 | -122.3511 | 0.027466 | 122.1359 | -0.022888 | 0.45776
3025.1094 | 122.3465 | -0.091553 | 122.2412 | -0.06691 | -0.044098 | 0.0013094 | 0.023578 | -0.0040503 | -0.010316 | -0.0051505 | -0.077179 | 0.0065923 | 0.064918 | 0.052823 | -0.017729 | 0.027408 | -0.0060071 | -0.13275 | -0.004578 | -0.036621 | -0.10071 | -0.009155 | -0.10986 | -0.013733 | 0.4715 | 122.1954 | -0.10986 | 122.0306 | 0.054932 | -0.004578 | 0.041199 | 0.054932 | -122.2458 | -122.3419 | 0.082398 | 0.07782 | -0.01831 | 0.022888 | -0.073242 | -0.01831 | -0.045776 | -0.21057 | 0.14649 | 0.13275 | 0.086975 | 0.15106 | 0.10529 | 0.027466 | -0.064087 | 0.16479 | 122.1405 | 0.032043 | 122.3053 | 0.086975 | 122.287 | -122.2778 | -122.3511 | -0.009155 | 122.1222 | -0.041198 | 0.56305
3026.875 | 122.3373 | -0.1236 | 122.2366 | -0.05928 | -0.045166 | 0.0030184 | 0.023791 | -0.0012731 | -0.010316 | -0.0045095 | -0.064972 | 0.0033881 | 0.06385 | 0.050259 | -0.014097 | 0.026553 | -0.0025891 | -0.14648 | -0.018311 | -0.036621 | -0.10071 | 0 | -0.091553 | -0.009155 | 0.48523 | 122.1863 | -0.09613 | 121.9986 | 0.054932 | -0.004578 | 0.013733 | 0.086975 | -122.2549 | -122.3373 | 0.1236 | 0.11444 | 0.032043 | 0.027466 | -0.054932 | 0.027466 | -0.050354 | -0.23804 | 0.17853 | 0.13733 | 0.11902 | 0.10986 | 0.091552 | 0.036621 | -0.064087 | 0.15106 | 122.0947 | 0.01831 | 122.2824 | 0.10528 | 122.3099 | -122.2733 | -122.3328 | 0.022888 | 122.1222 | -0.022888 | 0.60883
3028.6406 | 122.4289 | -0.064087 | 122.2092 | -0.17372 | -0.042816 | 0.003232 | 0.024005 | 0.0012903 | -0.010957 | -0.0047231 | -0.064972 | 0.0048833 | 0.06385 | 0.051114 | -0.017301 | 0.027621 | -0.0057935 | -0.09613 | -0.032043 | -0.022888 | -0.009155 | 0.073242 | -0.054932 | 0.041199 | 0.4303 | 122.1405 | -0.07782 | 122.1313 | 0.16479 | 0.10071 | 0.16022 | 0.041199 | -122.2412 | -122.2183 | 0.13733 | 0.10529 | 0.009155 | 0.064087 | -0.032044 | -0.013733 | -0.068664 | -0.077819 | 0.22888 | 0.2243 | 0.1648 | 0.23804 | 0.17853 | 0.09613 | 0.013733 | 0.24261 | 122.2092 | -0.009155 | 122.2183 | 0.032044 | 122.2046 | -122.2321 | -122.287 | 0.054932 | 122.1954 | -0.032043 | 0.49439
3030.3281 | 122.4197 | -0.082397 | 122.2275 | -0.15083 | -0.045166 | 0.003873 | 0.023364 | -0.0038367 | -0.010957 | -0.0028005 | -0.016144 | 0.0053107 | 0.065559 | 0.043637 | -0.017301 | 0.02634 | -0.0053661 | -0.10529 | -0.050354 | -0.032043 | -0.013733 | 0.068665 | -0.050354 | 0.032043 | 0.46234 | 122.1176 | -0.086975 | 122.0947 | 0.14648 | 0.091553 | 0.10529 | 0.050354 | -122.2778 | -122.2412 | 0.15106 | 0.11444 | 0.032043 | 0.064086 | -0.018311 | -0.004578 | -0.10986 | -0.13275 | 0.22888 | 0.18768 | 0.17395 | 0.19226 | 0.17853 | 0.10071 | 0.01831 | 0.23346 | 122.1817 | -0.018311 | 122.2046 | 0.032043 | 122.2 | -122.2595 | -122.3145 | 0.068664 | 122.1771 | -0.022889 | 0.54474
3032.0938 | 122.3373 | -0.10529 | 122.2504 | -0.12794 | -0.044312 | 0.002164 | 0.023364 | -0.0036231 | -0.0098886 | -0.0017325 | -0.025299 | 0.0057379 | 0.064277 | 0.053677 | -0.01666 | 0.028262 | -0.0013073 | -0.086975 | -0.041199 | -0.022888 | -0.027466 | 0.068665 | -0.050354 | 0.036621 | 0.54016 | 122.1542 | -0.07782 | 122.0352 | 0.059509 | 0.027466 | 0.032043 | 0.082398 | -122.2916 | -122.2778 | 0.17395 | 0.14191 | 0.054932 | 0.059509 | -0.027466 | 0.027466 | -0.09613 | -0.21515 | 0.16479 | 0.13733 | 0.13275 | 0.10986 | 0.10529 | 0.091553 | -0.004578 | 0.13733 | 122.113 | -0.018311 | 122.2321 | 0.064087 | 122.2595 | -122.2733 | -122.3282 | 0.07782 | 122.1405 | 0.018311 | 0.64545
3033.7812 | 122.3099 | -0.082397 | 122.2321 | -0.12032 | -0.043244 | 0.003232 | 0.027423 | 0.0032129 | -0.010102 | -0.0030141 | -0.092438 | 0.0061651 | 0.064491 | 0.047268 | -0.017301 | 0.02933 | -0.0049389 | -0.15106 | 0.009155 | -0.045776 | -0.10986 | -0.054932 | -0.17853 | -0.064087 | 0.32959 | 122.1588 | -0.10986 | 122.0261 | 0 | -0.045776 | 0.027466 | 0.036621 | -122.2229 | -122.3419 | 0.027465 | 0.01831 | -0.096131 | -0.018311 | -0.13275 | -0.027466 | -0.073243 | -0.20599 | 0.082397 | 0.10986 | 0.036621 | 0.13733 | 0.064087 | -0.009156 | -0.064087 | 0.10986 | 122.1359 | 0.054931 | 122.2687 | 0.091552 | 122.2412 | -122.2778 | -122.3419 | -0.027466 | 122.1085 | -0.068665 | 0.41199
3035.5469 | 122.3373 | -0.10529 | 122.2595 | -0.12032 | -0.046662 | 0.003232 | 0.022082 | -0.0034095 | -0.011598 | -0.0047231 | -0.04361 | 0.0053107 | 0.062782 | 0.053891 | -0.015806 | 0.027835 | -0.0066479 | -0.10071 | -0.050354 | -0.027466 | -0.045776 | 0.045776 | -0.086975 | 0 | 0.52185 | 122.1405 | -0.082397 | 122.0215 | 0.064087 | 0.013733 | 0.027466 | 0.07782 | -122.3099 | -122.3053 | 0.15106 | 0.10529 | 0.018311 | 0.027466 | -0.059509 | 0.022889 | -0.11902 | -0.23804 | 0.16937 | 0.13275 | 0.11902 | 0.10986 | 0.09613 | 0.073242 | -0.01831 | 0.14648 | 122.1039 | -0.022888 | 122.2229 | 0.054932 | 122.2458 | -122.287 | -122.3419 | 0.05951 | 122.1268 | 0.004578 | 0.62714
3037.2969 | 122.4106 | -0.050354 | 122.2275 | -0.18898 | -0.041107 | 0.0030184 | 0.024218 | -0.0040503 | -0.0092478 | 0.00061746 | -0.028351 | 0.0046697 | 0.063209 | 0.044705 | -0.015806 | 0.025485 | -0.0064343 | -0.082397 | -0.064087 | -0.004578 | 0.022888 | 0.1236 | -0.041199 | 0.064087 | 0.46692 | 122.1268 | -0.068665 | 122.1176 | 0.12817 | 0.082397 | 0.12817 | 0.045776 | -122.2916 | -122.2046 | 0.17395 | 0.11444 | 0.009155 | 0.068665 | -0.036621 | -0.018311 | -0.10071 | -0.10986 | 0.17853 | 0.17853 | 0.13275 | 0.19684 | 0.15106 | 0.12817 | 0.027466 | 0.19684 | 122.1863 | -0.059509 | 122.1954 | -0.013733 | 122.1771 | -122.2321 | -122.2961 | 0.073242 | 122.168 | -0.032043 | 0.51727
3039.0625 | 122.406 | -0.054932 | 122.2183 | -0.12794 | -0.043885 | 0.0013094 | 0.024859 | 0.0023585 | -0.01117 | -0.0053641 | -0.037506 | 0.0072333 | 0.061714 | 0.047482 | -0.016233 | 0.025485 | -0.0010937 | -0.1236 | -0.045776 | -0.009155 | -0.018311 | 0.068665 | -0.054932 | 0.050354 | 0.43945 | 122.168 | -0.07782 | 122.0947 | 0.11902 | 0.07782 | 0.10529 | 0.045777 | -122.2641 | -122.2366 | 0.1236 | 0.10529 | 0 | 0.059509 | -0.045777 | -0.022888 | -0.050354 | -0.1236 | 0.17395 | 0.16022 | 0.13275 | 0.18311 | 0.15564 | 0.07782 | -0.009156 | 0.19684 | 122.1725 | -0.036621 | 122.2458 | 0.009156 | 122.2229 | -122.2275 | -122.2961 | 0.036621 | 122.1497 | -0.068664 | 0.49438
3040.7656 | 122.3099 | -0.10986 | 122.2504 | -0.12794 | -0.044098 | 0.0040866 | 0.023791 | 0.0040675 | -0.0098886 | -0.0023733 | -0.11685 | 0.0057379 | 0.064918 | 0.051327 | -0.017515 | 0.030399 | -0.0068615 | -0.091553 | -0.045776 | -0.027466 | -0.041199 | 0.027466 | -0.10529 | -0.013733 | 0.41199 | 122.168 | -0.07782 | 122.0306 | 0.045776 | -0.027466 | 0.050354 | 0.082397 | -122.2961 | -122.2916 | 0.13733 | 0.09613 | 0.004577 | 0.013733 | -0.07782 | 0.032043 | -0.082397 | -0.21973 | 0.15564 | 0.16022 | 0.082397 | 0.12817 | 0.050354 | 0.054932 | -0.013733 | 0.1236 | 122.1085 | -0.01831 | 122.2458 | 0.064087 | 122.2778 | -122.2778 | -122.3282 | 0.068664 | 122.1405 | 0.01831 | 0.52185
3042.5156 | 122.4289 | -0.064087 | 122.2183 | -0.15846 | -0.040894 | 0.0047274 | 0.026782 | 0.0010767 | -0.010743 | -0.0025869 | -0.1138 | 0.0055243 | 0.062568 | 0.047268 | -0.017088 | 0.028049 | -0.0047253 | -0.086975 | -0.013733 | -0.022888 | 0 | 0.082397 | -0.036621 | 0.045776 | 0.44403 | 122.1405 | -0.054932 | 122.1497 | 0.15564 | 0.10071 | 0.17853 | 0.041199 | -122.2321 | -122.2183 | 0.14648 | 0.10986 | 0.027466 | 0.068664 | -0.013733 | 0.009155 | -0.07782 | -0.068665 | 0.21973 | 0.24261 | 0.1648 | 0.23346 | 0.15564 | 0.10528 | 0.022888 | 0.21057 | 122.2046 | 0.009155 | 122.1954 | 0.050354 | 122.2046 | -122.2412 | -122.2733 | 0.064087 | 122.2137 | -0.022888 | 0.50812
3044.2031 | 122.3145 | -0.091553 | 122.2733 | -0.10506 | -0.044953 | 0.0019504 | 0.024005 | 0.0015039 | -0.010957 | -0.0047231 | -0.064972 | 0.0057379 | 0.064704 | 0.042142 | -0.017515 | 0.027621 | -0.0032299 | -0.15564 | -0.022888 | -0.045776 | -0.10071 | 0.004578 | -0.10529 | -0.018311 | 0.50354 | 122.1817 | -0.091553 | 121.9986 | 0.059509 | -0.022888 | 0.022888 | 0.045777 | -122.2961 | -122.374 | 0.096131 | 0.073242 | -0.013733 | 0.027465 | -0.05951 | 0 | -0.091552 | -0.27466 | 0.15106 | 0.11444 | 0.068665 | 0.11444 | 0.068665 | 0.050354 | -0.054932 | 0.15106 | 122.0901 | 0.022888 | 122.2733 | 0.068665 | 122.2733 | -122.319 | -122.3648 | -0.009155 | 122.0901 | -0.064087 | 0.59509
3045.9688 | 122.3328 | -0.091553 | 122.2824 | -0.17372 | -0.043671 | 0.003232 | 0.028705 | -0.00020513 | -0.0088206 | -0.0017325 | -0.089386 | 0.0085149 | 0.06385 | 0.052182 | -0.01666 | 0.028262 | -0.0040845 | -0.12817 | -0.004578 | -0.045776 | -0.11444 | -0.018311 | -0.15564 | -0.041199 | 0.3479 | 122.1771 | -0.10529 | 122.0444 | 0.022888 | -0.036621 | 0.027466 | 0.045777 | -122.287 | -122.3969 | 0.073242 | 0.050354 | -0.064087 | 0.004577 | -0.10986 | -0.013733 | -0.10529 | -0.23804 | 0.11444 | 0.11902 | 0.054932 | 0.13275 | 0.068665 | 0.027465 | -0.068665 | 0.12817 | 122.1497 | 0.041198 | 122.2824 | 0.086975 | 122.2687 | -122.3282 | -122.3877 | -0.022888 | 122.1359 | -0.036621 | 0.43945
3047.6562 | 122.3373 | -0.10529 | 122.2733 | -0.12032 | -0.044312 | 0.003232 | 0.026782 | 0.0070581 | -0.009675 | -0.0032277 | -0.098541 | 0.0059515 | 0.065345 | 0.042142 | -0.014311 | 0.029758 | -0.0051525 | -0.091553 | -0.022888 | -0.036621 | -0.041199 | 0.027466 | -0.10986 | -0.013733 | 0.41199 | 122.1588 | -0.086975 | 122.0261 | 0.050354 | -0.022888 | 0.045776 | 0.068665 | -122.2961 | -122.3145 | 0.13275 | 0.091553 | -0.004577 | 0.022888 | -0.073242 | 0.018311 | -0.11444 | -0.24719 | 0.15564 | 0.15106 | 0.082398 | 0.13275 | 0.064087 | 0.064087 | -0.004578 | 0.13733 | 122.113 | 0.013733 | 122.2458 | 0.082398 | 122.2641 | -122.3099 | -122.3602 | 0.064087 | 122.1313 | 0.013733 | 0.51727
3049.4062 | 122.3145 | -0.10986 | 122.2412 | -0.13557 | -0.042389 | 0.0043002 | 0.026568 | -0.00020513 | -0.0098886 | -0.0049367 | -0.11075 | 0.0070197 | 0.064704 | 0.046414 | -0.01602 | 0.028262 | -0.0072889 | -0.11444 | -0.018311 | -0.027466 | -0.07782 | -0.013733 | -0.14191 | -0.032043 | 0.35248 | 122.168 | -0.09613 | 122.0215 | 0.009155 | -0.045776 | 0.032043 | 0.082397 | -122.2595 | -122.319 | 0.09613 | 0.07782 | -0.032044 | -0.004577 | -0.11444 | 0.013733 | -0.073242 | -0.21973 | 0.11902 | 0.14191 | 0.064087 | 0.12817 | 0.050354 | 0.013733 | -0.050354 | 0.10528 | 122.1176 | 0.009155 | 122.2641 | 0.091552 | 122.2778 | -122.2687 | -122.3373 | 0.032043 | 122.1313 | -0.004578 | 0.46234
3051.1719 | 122.3099 | -0.086975 | 122.2778 | -0.19661 | -0.041107 | 0.0043002 | 0.025927 | -0.00084593 | -0.007966 | -0.0060049 | -0.077179 | 0.0055243 | 0.062995 | 0.052395 | -0.015806 | 0.029758 | -0.0032299 | -0.11902 | 0.004578 | -0.054932 | -0.091553 | -0.032043 | -0.15564 | -0.050354 | 0.33875 | 122.1863 | -0.086975 | 122.0352 | 0.027466 | -0.045776 | 0.036621 | 0.032043 | -122.2733 | -122.3694 | 0.054932 | 0.036621 | -0.068665 | 0.004578 | -0.10071 | 0 | -0.091553 | -0.24262 | 0.11444 | 0.1236 | 0.041199 | 0.1236 | 0.041199 | 0.022889 | -0.036621 | 0.11444 | 122.1222 | 0.05951 | 122.2733 | 0.091553 | 122.2733 | -122.3328 | -122.3648 | -0.004578 | 122.1222 | -0.032044 | 0.42572
3052.9219 | 122.3145 | -0.091553 | 122.2641 | -0.1432 | -0.043457 | 0.0017368 | 0.021014 | -0.0034095 | -0.011598 | -0.0040823 | -0.031403 | 0.0055243 | 0.064491 | 0.047268 | -0.014524 | 0.028049 | -0.0045117 | -0.14648 | -0.013733 | -0.059509 | -0.10071 | 0 | -0.10071 | 0 | 0.48523 | 122.168 | -0.09613 | 122.0123 | 0.036621 | 0 | 0.013733 | 0.032044 | -122.2778 | -122.3648 | 0.091553 | 0.091553 | -0.009155 | 0.059509 | -0.041199 | -0.004577 | -0.09613 | -0.25177 | 0.12817 | 0.10529 | 0.091553 | 0.10986 | 0.09613 | 0.059509 | -0.041199 | 0.13275 | 122.1085 | 0.045776 | 122.2641 | 0.07782 | 122.2595 | -122.3236 | -122.3602 | -0.009155 | 122.1039 | -0.054931 | 0.57678
3054.6875 | 122.3694 | -0.091553 | 122.2733 | -0.13557 | -0.045166 | 0.0028048 | 0.023791 | -0.0040503 | -0.011598 | -0.0023733 | -0.013092 | 0.0042425 | 0.06385 | 0.044278 | -0.015592 | 0.027408 | -0.0025891 | -0.07782 | -0.054932 | -0.004578 | -0.004578 | 0.10529 | -0.009155 | 0.059509 | 0.58136 | 122.1588 | -0.064087 | 122.0535 | 0.10071 | 0.045776 | 0.086975 | 0.086975 | -122.3282 | -122.2778 | 0.19684 | 0.15106 | 0.082398 | 0.064087 | -0.004577 | 0.027466 | -0.11444 | -0.21973 | 0.19226 | 0.17853 | 0.13733 | 0.15106 | 0.10986 | 0.10986 | 0 | 0.1648 | 122.1176 | -0.050354 | 122.2229 | 0.036621 | 122.2504 | -122.2778 | -122.3373 | 0.086975 | 122.1451 | 0.013733 | 0.67291
3056.375 | 122.3694 | -0.086975 | 122.2504 | -0.12032 | -0.041107 | 0.0025912 | 0.025073 | 0.0047083 | -0.01053 | -0.0019461 | -0.089386 | 0.0063787 | 0.064277 | 0.048977 | -0.015806 | 0.027621 | -0.0049389 | -0.10071 | -0.013733 | -0.041199 | -0.027466 | 0.064087 | -0.064087 | 0.027466 | 0.51727 | 122.1817 | -0.073242 | 122.081 | 0.10071 | 0.050354 | 0.07782 | 0.045776 | -122.2641 | -122.2778 | 0.15106 | 0.11444 | 0.022888 | 0.068665 | -0.022888 | 0.013733 | -0.068664 | -0.16937 | 0.18768 | 0.16479 | 0.13733 | 0.15106 | 0.1236 | 0.10529 | 0.013733 | 0.17395 | 122.1542 | 0.027466 | 122.2549 | 0.073242 | 122.2687 | -122.2916 | -122.3236 | 0.059509 | 122.168 | -0.013733 | 0.60425
3058.125 | 122.3373 | -0.12817 | 122.2778 | -0.10506 | -0.047089 | 0.0025912 | 0.022082 | -0.0040503 | -0.0092478 | -0.0034415 | -0.031403 | 0.0055243 | 0.064063 | 0.046414 | -0.016447 | 0.028476 | -0.0032299 | -0.1236 | -0.027466 | -0.054932 | -0.091553 | 0.013733 | -0.10071 | -0.009155 | 0.49896 | 122.1817 | -0.10986 | 122.0078 | 0.054932 | 0 | 0.032043 | 0.073242 | -122.3053 | -122.3694 | 0.14191 | 0.11902 | 0.027466 | 0.045777 | -0.045776 | 0.018311 | -0.09613 | -0.27008 | 0.18311 | 0.16022 | 0.12817 | 0.14191 | 0.10986 | 0.068665 | -0.036621 | 0.16479 | 122.1176 | 0.027466 | 122.2916 | 0.10071 | 122.3099 | -122.3328 | -122.3877 | 0.036621 | 122.1359 | 0.004578 | 0.62714
3059.8281 | 122.4655 | -0.027466 | 122.2321 | -0.19661 | -0.042816 | 0.0028048 | 0.025287 | 8.47e-06 | -0.006257 | -0.0017325 | -0.040558 | 0.0055243 | 0.064918 | 0.044278 | -0.01666 | 0.027194 | -0.0077161 | -0.050354 | -0.064087 | 0.009155 | 0.041199 | 0.14191 | -0.018311 | 0.073242 | 0.48065 | 122.1359 | -0.041199 | 122.1451 | 0.17853 | 0.11902 | 0.16479 | 0.036621 | -122.2961 | -122.1909 | 0.16937 | 0.10071 | 0.009155 | 0.064087 | -0.027466 | -0.013733 | -0.096131 | -0.086975 | 0.20599 | 0.19226 | 0.14649 | 0.20599 | 0.16022 | 0.13275 | 0.032044 | 0.21973 | 122.1863 | -0.073242 | 122.1771 | -0.036621 | 122.1634 | -122.2229 | -122.2733 | 0.068665 | 122.1725 | -0.022888 | 0.50812
3061.5781 | 122.4426 | -0.050354 | 122.2137 | -0.089798 | -0.046021 | 0.0036594 | 0.022937 | -0.00084593 | -0.0088206 | -0.0049367 | 0.0021667 | 0.0050971 | 0.063209 | 0.049832 | -0.016874 | 0.027408 | -0.0028027 | -0.068665 | -0.054932 | -0.013733 | 0.036621 | 0.17395 | 0.036621 | 0.11444 | 0.64545 | 122.1313 | -0.054932 | 122.1313 | 0.19226 | 0.13733 | 0.15106 | 0.036621 | -122.2687 | -122.1771 | 0.2243 | 0.16479 | 0.086975 | 0.12817 | 0.050354 | -0.004578 | -0.082397 | -0.082397 | 0.24261 | 0.20142 | 0.18768 | 0.20599 | 0.19226 | 0.18768 | 0.050354 | 0.24719 | 122.1863 | -0.041199 | 122.1863 | -0.004578 | 122.1817 | -122.2275 | -122.2687 | 0.086975 | 122.1817 | -0.018311 | 0.6958
3063.3438 | 122.3053 | -0.09613 | 122.2641 | -0.17372 | -0.039612 | 0.0040866 | 0.025073 | -0.00041873 | -0.0075388 | -0.0060049 | -0.1077 | 0.0063787 | 0.064063 | 0.049405 | -0.018583 | 0.025912 | -0.0060071 | -0.1236 | 0.004578 | -0.064087 | -0.10986 | -0.064087 | -0.16937 | -0.07782 | 0.34332 | 122.1817 | -0.10986 | 122.0261 | 0.018311 | -0.050354 | 0.032043 | 0.032043 | -122.2595 | -122.374 | 0.032043 | 0.01831 | -0.073243 | -0.013733 | -0.10529 | -0.013733 | -0.082397 | -0.23804 | 0.11444 | 0.12817 | 0.045776 | 0.14191 | 0.059509 | 0 | -0.045776 | 0.12817 | 122.1359 | 0.068665 | 122.2916 | 0.10071 | 122.2778 | -122.3282 | -122.374 | -0.013733 | 122.1222 | -0.027466 | 0.43945
3065.0469 | 122.4426 | -0.059509 | 122.2412 | -0.089798 | -0.043457 | 0.0025912 | 0.022296 | -0.0027685 | -0.013307 | -0.0042959 | -0.013092 | 0.0063787 | 0.063636 | 0.046841 | -0.016874 | 0.026126 | -0.0036573 | -0.068665 | -0.045776 | -0.027466 | 0.041199 | 0.15106 | 0.013733 | 0.086975 | 0.63629 | 122.1542 | -0.064087 | 122.1222 | 0.17395 | 0.14191 | 0.15564 | 0.032043 | -122.287 | -122.2 | 0.21057 | 0.14648 | 0.073242 | 0.11444 | 0.041199 | -0.004578 | -0.086975 | -0.11902 | 0.23346 | 0.21515 | 0.20142 | 0.21973 | 0.20599 | 0.17853 | 0.068665 | 0.23804 | 122.1863 | -0.01831 | 122.2183 | 0.013733 | 122.2137 | -122.2687 | -122.3053 | 0.10071 | 122.1817 | -0.009156 | 0.6958
3066.7969 | 122.374 | -0.07782 | 122.2321 | -0.10506 | -0.043885 | 0.0028048 | 0.021869 | -0.0017005 | -0.0098886 | -0.0062185 | -0.013092 | 0.0053107 | 0.062354 | 0.045132 | -0.016233 | 0.025912 | -0.0045117 | -0.068665 | -0.045776 | -0.004578 | 0.009155 | 0.10986 | 0.009155 | 0.07782 | 0.60425 | 122.1634 | -0.07782 | 122.0673 | 0.1236 | 0.068665 | 0.091553 | 0.073242 | -122.2778 | -122.2229 | 0.18768 | 0.15564 | 0.086975 | 0.082398 | 0.013733 | 0 | -0.068665 | -0.16479 | 0.20142 | 0.16937 | 0.14649 | 0.16937 | 0.14649 | 0.11444 | 0.013733 | 0.20142 | 122.1451 | -0.041198 | 122.2412 | 0.032044 | 122.2412 | -122.2366 | -122.3099 | 0.086975 | 122.1451 | 0.009155 | 0.68207
3068.5625 | 122.3099 | -0.09613 | 122.3007 | -0.13557 | -0.041962 | 0.0028048 | 0.025287 | -0.0049047 | -0.01053 | 0.00061746 | -0.12296 | 0.0057379 | 0.064491 | 0.050046 | -0.017088 | 0.028476 | -0.0070751 | -0.11902 | -0.013733 | -0.036621 | -0.082397 | -0.022888 | -0.14191 | -0.059509 | 0.36163 | 122.1817 | -0.091553 | 122.0169 | 0.009155 | -0.045776 | 0.022888 | 0.059509 | -122.3145 | -122.3831 | 0.073242 | 0.036621 | -0.045777 | -0.022888 | -0.10529 | 0.004577 | -0.11902 | -0.28381 | 0.10528 | 0.11902 | 0.050354 | 0.11444 | 0.045777 | 0.013733 | -0.045776 | 0.10071 | 122.1085 | 0.022888 | 122.2733 | 0.082397 | 122.2778 | -122.3373 | -122.3923 | 0.013733 | 122.113 | -0.022889 | 0.45776
3070.3281 | 122.3511 | -0.10986 | 122.2641 | -0.021133 | -0.046448 | 0.0019504 | 0.0255 | -0.0012731 | -0.010743 | -0.0045095 | -0.04361 | 0.0053107 | 0.062568 | 0.044919 | -0.017088 | 0.027194 | -0.0049389 | -0.13733 | -0.013733 | -0.068665 | -0.10529 | -0.013733 | -0.1236 | -0.009155 | 0.47607 | 122.2 | -0.10986 | 122.0352 | 0.050354 | 0 | 0.041199 | 0.041198 | -122.2778 | -122.3694 | 0.09613 | 0.10071 | -0.013733 | 0.05951 | -0.054931 | 0 | -0.064087 | -0.22888 | 0.16022 | 0.15106 | 0.10986 | 0.15106 | 0.10986 | 0.054932 | -0.036621 | 0.16022 | 122.1451 | 0.054932 | 122.3099 | 0.09613 | 122.3099 | -122.3328 | -122.374 | 0.004577 | 122.1451 | -0.027466 | 0.58594
3072.0156 | 122.4289 | -0.050354 | 122.2092 | -0.17372 | -0.042603 | 0.0023776 | 0.022509 | -0.0023413 | -0.010743 | -0.0036551 | -0.034454 | 0.0061651 | 0.063636 | 0.04855 | -0.017088 | 0.026553 | -0.0051525 | -0.064087 | -0.064087 | 0.013733 | 0.036621 | 0.14648 | -0.018311 | 0.054932 | 0.48523 | 122.1268 | -0.054932 | 122.1405 | 0.15564 | 0.10071 | 0.15564 | 0.064087 | -122.2733 | -122.1725 | 0.19684 | 0.10529 | 0.032043 | 0.041199 | -0.032044 | -0.004578 | -0.082397 | -0.068664 | 0.20599 | 0.20599 | 0.15106 | 0.21057 | 0.15564 | 0.13275 | 0.022888 | 0.21057 | 122.1954 | -0.07782 | 122.1817 | -0.013733 | 122.1771 | -122.1954 | -122.2641 | 0.086975 | 122.1909 | -0.013733 | 0.53558
3073.7656 | 122.3923 | -0.050354 | 122.2366 | -0.15083 | -0.044098 | 0.002164 | 0.023791 | -0.0021277 | -0.010102 | -0.0049367 | -0.013092 | 0.0074469 | 0.063636 | 0.0462 | -0.017301 | 0.027835 | -0.0051525 | -0.09613 | -0.064087 | 0.004578 | 0.009155 | 0.10986 | -0.045776 | 0.059509 | 0.43945 | 122.1451 | -0.064087 | 122.0993 | 0.11902 | 0.082397 | 0.11444 | 0.054932 | -122.3007 | -122.2275 | 0.16022 | 0.10986 | 0.004578 | 0.054931 | -0.050354 | -0.013733 | -0.091552 | -0.13733 | 0.16937 | 0.16479 | 0.13275 | 0.17853 | 0.14648 | 0.10529 | 0.004577 | 0.18311 | 122.1634 | -0.068665 | 122.2092 | -0.013733 | 122.1954 | -122.2321 | -122.3007 | 0.059509 | 122.1497 | -0.045776 | 0.48981
3075.5312 | 122.3648 | -0.082397 | 122.2916 | -0.13557 | -0.043671 | 0.0045138 | 0.028064 | 0.0010767 | -0.008607 | -0.00066434 | -0.1138 | 0.0044561 | 0.064063 | 0.050046 | -0.016874 | 0.026981 | -0.0038709 | -0.086975 | -0.018311 | -0.045776 | -0.009155 | 0.073242 | -0.064087 | 0.004578 | 0.50812 | 122.1725 | -0.068665 | 122.0764 | 0.082397 | 0.013733 | 0.068665 | 0.036621 | -122.3099 | -122.3007 | 0.15564 | 0.086975 | 0.01831 | 0.050354 | -0.018311 | 0.013732 | -0.11902 | -0.21515 | 0.16479 | 0.15106 | 0.09613 | 0.13733 | 0.082398 | 0.11902 | 0.036621 | 0.15106 | 122.1451 | 0.027465 | 122.2412 | 0.064086 | 122.2549 | -122.3373 | -122.3602 | 0.073242 | 122.1588 | -0.004578 | 0.59051
3077.2188 | 122.2916 | -0.10529 | 122.2641 | -0.21187 | -0.042176 | 0.002164 | 0.028064 | 0.0019311 | -0.007966 | -0.0053641 | -0.098541 | 0.0063787 | 0.063423 | 0.046841 | -0.016447 | 0.029117 | -0.0030163 | -0.11902 | -0.032043 | -0.054932 | -0.10529 | -0.032043 | -0.15106 | -0.064087 | 0.31586 | 122.2 | -0.082397 | 122.0123 | 0.009155 | -0.045776 | 0.032043 | 0.050354 | -122.2961 | -122.3694 | 0.073243 | 0.041199 | -0.045776 | -0.009155 | -0.09613 | 0.022889 | -0.064087 | -0.25177 | 0.11444 | 0.13733 | 0.05951 | 0.11444 | 0.036621 | 0.022889 | -0.050354 | 0.091552 | 122.0947 | 0.022889 | 122.2824 | 0.073243 | 122.3053 | -122.319 | -122.3465 | 0 | 122.1176 | -0.013733 | 0.42114
3078.9844 | 122.3282 | -0.086975 | 122.2961 | -0.12032 | -0.044098 | 0.003232 | 0.026355 | -0.00020513 | -0.011384 | -0.0040823 | -0.11685 | 0.0057379 | 0.064277 | 0.047909 | -0.017729 | 0.027835 | -0.0064343 | -0.10529 | -0.018311 | -0.054932 | -0.054932 | 0.022888 | -0.10071 | -0.013733 | 0.4303 | 122.1817 | -0.091553 | 122.0581 | 0.036621 | -0.032043 | 0.050354 | 0.032043 | -122.3145 | -122.3511 | 0.10986 | 0.073242 | -0.013733 | 0.041199 | -0.045776 | -0.004578 | -0.11444 | -0.23804 | 0.1236 | 0.13733 | 0.054932 | 0.14191 | 0.05951 | 0.07782 | 0 | 0.12817 | 122.1497 | 0.036621 | 122.2733 | 0.068664 | 122.2687 | -122.3511 | -122.3877 | 0.032043 | 122.1451 | -0.018311 | 0.51727
3080.75 | 122.4289 | -0.059509 | 122.2275 | -0.1432 | -0.044525 | 0.0051546 | 0.021441 | -0.0059729 | -0.0092478 | -0.0030141 | 0.0021667 | 0.0057379 | 0.065345 | 0.045773 | -0.015806 | 0.026553 | -0.0028027 | -0.091553 | -0.041199 | -0.027466 | -0.036621 | 0.091553 | -0.050354 | 0.050354 | 0.48523 | 122.1451 | -0.07782 | 122.113 | 0.13275 | 0.10986 | 0.11902 | 0.032043 | -122.2687 | -122.2641 | 0.15106 | 0.10986 | 0.009155 | 0.07782 | -0.022888 | -0.018311 | -0.082397 | -0.11444 | 0.19226 | 0.17853 | 0.16937 | 0.19684 | 0.18768 | 0.11902 | -0.009155 | 0.21057 | 122.1909 | -0.013733 | 122.2229 | 0.01831 | 122.2046 | -122.2549 | -122.3053 | 0.022888 | 122.1725 | -0.032044 | 0.54474
3082.4375 | 122.3328 | -0.10529 | 122.2504 | -0.10506 | -0.046662 | 0.0019504 | 0.026141 | -0.0044775 | -0.010102 | -0.0038687 | -0.083283 | 0.0065923 | 0.064704 | 0.050686 | -0.017729 | 0.025912 | -0.0060071 | -0.14648 | -0.018311 | -0.059509 | -0.10986 | -0.004578 | -0.10529 | -0.013733 | 0.48981 | 122.1817 | -0.10529 | 122.0078 | 0.022888 | -0.013733 | 0.032043 | 0.045777 | -122.2687 | -122.3602 | 0.10071 | 0.091553 | 0 | 0.045776 | -0.045777 | 0 | -0.068664 | -0.24262 | 0.12817 | 0.13733 | 0.091553 | 0.13733 | 0.091553 | 0.054931 | -0.050354 | 0.12817 | 122.113 | 0.041198 | 122.287 | 0.086975 | 122.287 | -122.3099 | -122.3557 | -0.004577 | 122.113 | -0.041198 | 0.59509
3084.1875 | 122.4335 | -0.07782 | 122.2412 | -0.074539 | -0.044953 | 0.001523 | 0.020373 | -0.0019141 | -0.010743 | -0.0021597 | -0.013092 | 0.0044561 | 0.062995 | 0.0462 | -0.01666 | 0.024204 | -0.0042981 | -0.064087 | -0.054932 | -0.013733 | 0.041199 | 0.14648 | 0.018311 | 0.082397 | 0.60883 | 122.1039 | -0.064087 | 122.1039 | 0.15564 | 0.1236 | 0.11444 | 0.064087 | -122.2961 | -122.2 | 0.2243 | 0.16022 | 0.096131 | 0.09613 | 0.032044 | 0.013733 | -0.13733 | -0.13733 | 0.23346 | 0.19226 | 0.20142 | 0.17853 | 0.18768 | 0.16022 | 0.054932 | 0.21973 | 122.168 | -0.041199 | 122.168 | 0.022888 | 122.1817 | -122.2549 | -122.3053 | 0.11902 | 122.1817 | 0.013733 | 0.68665
3085.8906 | 122.4472 | -0.036621 | 122.2137 | -0.23476 | -0.04303 | 0.0023776 | 0.023364 | 0.0017175 | -0.01053 | -0.0019461 | -0.052765 | 0.0061651 | 0.063209 | 0.047055 | -0.017729 | 0.028903 | -0.0064343 | -0.045776 | -0.064087 | -0.009155 | 0.027466 | 0.13733 | -0.027466 | 0.073242 | 0.48523 | 122.1405 | -0.050354 | 122.168 | 0.16479 | 0.10986 | 0.16937 | 0.027466 | -122.2778 | -122.1863 | 0.17395 | 0.10986 | 0.009155 | 0.082397 | -0.018311 | -0.013733 | -0.073242 | -0.045776 | 0.20142 | 0.20599 | 0.14648 | 0.21973 | 0.16022 | 0.14648 | 0.036621 | 0.21515 | 122.2183 | -0.054932 | 122.1909 | -0.027466 | 122.1771 | -122.2229 | -122.2641 | 0.064087 | 122.2046 | -0.009155 | 0.52185
3087.6562 | 122.4289 | -0.064087 | 122.2504 | -0.17372 | -0.043671 | 0.003232 | 0.024646 | -0.0031957 | -0.0098886 | -0.0042959 | -0.0008851 | 0.0046697 | 0.063423 | 0.050686 | -0.016447 | 0.024417 | -0.0066479 | -0.091553 | -0.036621 | -0.018311 | -0.022888 | 0.068665 | -0.050354 | 0.045776 | 0.48065 | 122.1588 | -0.073242 | 122.113 | 0.1236 | 0.10529 | 0.1236 | 0.045776 | -122.287 | -122.2733 | 0.13275 | 0.10986 | 0.013733 | 0.064087 | -0.032043 | -0.009155 | -0.091553 | -0.13733 | 0.18768 | 0.18768 | 0.16937 | 0.19684 | 0.17853 | 0.086976 | -0.004577 | 0.19684 | 122.1863 | -0.01831 | 122.2321 | 0.027466 | 122.2229 | -122.2687 | -122.3236 | 0.041199 | 122.1771 | -0.027466 | 0.54474
3089.3594 | 122.4335 | -0.041199 | 122.2321 | -0.2195 | -0.044953 | 0.0013094 | 0.0255 | -0.0025549 | -0.0092478 | -0.0042959 | -0.01004 | 0.0055243 | 0.062568 | 0.050686 | -0.017088 | 0.024844 | -0.0062207 | -0.091553 | -0.045776 | -0.013733 | -0.009155 | 0.091553 | -0.022888 | 0.068665 | 0.51727 | 122.1313 | -0.059509 | 122.1359 | 0.16479 | 0.11902 | 0.15106 | 0.027466 | -122.2778 | -122.2412 | 0.13275 | 0.10986 | 0.018311 | 0.082398 | -0.009155 | -0.01831 | -0.10071 | -0.096131 | 0.20599 | 0.19226 | 0.16022 | 0.21057 | 0.17853 | 0.10529 | 0.004578 | 0.2243 | 122.1954 | -0.032043 | 122.1909 | -0.004577 | 122.1725 | -122.2458 | -122.2916 | 0.032044 | 122.1771 | -0.050354 | 0.55847
3091.125 | 122.4838 | -0.050354 | 122.2229 | -0.16609 | -0.045594 | 0.0025912 | 0.022296 | -0.0051183 | -0.0092478 | -0.0040823 | -0.0069885 | 0.0065923 | 0.065772 | 0.047482 | -0.018583 | 0.026553 | -0.0060071 | -0.054932 | -0.054932 | -0.004578 | 0.041199 | 0.15106 | 0.022888 | 0.10986 | 0.63629 | 122.1405 | -0.059509 | 122.1634 | 0.20599 | 0.16022 | 0.15564 | 0.045776 | -122.2778 | -122.1817 | 0.20142 | 0.16022 | 0.073242 | 0.11444 | 0.027466 | -0.009155 | -0.082397 | -0.059509 | 0.25635 | 0.20599 | 0.21057 | 0.21515 | 0.21973 | 0.15564 | 0.045777 | 0.2655 | 122.2229 | -0.050354 | 122.2 | -0.004578 | 122.1909 | -122.2275 | -122.2824 | 0.091553 | 122.2137 | -0.004578 | 0.68665
3092.8906 | 122.4335 | -0.064087 | 122.2412 | -0.089798 | -0.043457 | 0.0017368 | 0.023791 | -0.00063233 | -0.0083932 | -0.0034415 | -0.013092 | 0.0065923 | 0.060432 | 0.049618 | -0.017088 | 0.02634 | -0.0055799 | -0.10071 | -0.045776 | -0.032043 | -0.022888 | 0.07782 | -0.045776 | 0.050354 | 0.48981 | 122.1588 | -0.068665 | 122.113 | 0.14191 | 0.091553 | 0.1236 | 0.032044 | -122.287 | -122.2641 | 0.14191 | 0.11444 | 0.018311 | 0.082397 | -0.013733 | -0.004578 | -0.082398 | -0.12817 | 0.20599 | 0.18768 | 0.15564 | 0.19226 | 0.16022 | 0.10986 | 0.009155 | 0.21057 | 122.1817 | -0.013733 | 122.2275 | 0.018311 | 122.2229 | -122.2733 | -122.3099 | 0.041199 | 122.1771 | -0.036621 | 0.55389
3094.6875 | 122.4106 | -0.059509 | 122.2366 | -0.13557 | -0.042389 | 0.0034456 | 0.023791 | -0.0010595 | -0.0083932 | -0.0021597 | -0.071076 | 0.0063787 | 0.061927 | 0.049405 | -0.020292 | 0.028262 | -0.0075025 | -0.068665 | -0.068665 | -0.013733 | 0.041199 | 0.13733 | -0.041199 | 0.082397 | 0.48981 | 122.1405 | -0.068665 | 122.1222 | 0.13275 | 0.10529 | 0.13733 | 0.045776 | -122.3053 | -122.1954 | 0.19684 | 0.14191 | 0.01831 | 0.09613 | -0.027466 | -0.009156 | -0.09613 | -0.11444 | 0.19226 | 0.19684 | 0.16479 | 0.20599 | 0.17395 | 0.15106 | 0.054932 | 0.20142 | 122.1909 | -0.054932 | 122.2092 | -0.009156 | 122.2 | -122.2504 | -122.3053 | 0.10071 | 122.1817 | -0.009156 | 0.54932
3096.3906 | 122.3419 | -0.09613 | 122.2366 | -0.12794 | -0.04303 | 0.0034456 | 0.025927 | -0.0038367 | -0.008607 | -0.0051505 | -0.12601 | 0.0065923 | 0.061286 | 0.051114 | -0.015806 | 0.028049 | 0.0014697 | -0.12817 | -0.004578 | -0.059509 | -0.09613 | -0.032043 | -0.16022 | -0.036621 | 0.33875 | 122.1954 | -0.082397 | 122.0581 | 0.018311 | -0.045776 | 0.041199 | 0.036621 | -122.2412 | -122.3328 | 0.064087 | 0.059509 | -0.064087 | 0.022888 | -0.10071 | 0.013733 | -0.041198 | -0.17853 | 0.11444 | 0.13733 | 0.050354 | 0.1236 | 0.036621 | 0.027466 | -0.036621 | 0.10071 | 122.1405 | 0.054931 | 122.2778 | 0.091552 | 122.2916 | -122.2961 | -122.319 | 0 | 122.1542 | -0.032044 | 0.43488
3098.1562 | 122.4655 | -0.064087 | 122.2229 | -0.13557 | -0.044525 | 0.00066863 | 0.023364 | -0.0029821 | -0.011598 | -0.0036551 | -0.01004 | 0.0050971 | 0.062995 | 0.047268 | -0.015806 | 0.02634 | -0.0042981 | -0.10071 | -0.064087 | -0.013733 | 0.018311 | 0.1236 | 0 | 0.10071 | 0.59509 | 122.1451 | -0.073242 | 122.1497 | 0.19226 | 0.13733 | 0.15564 | 0.050354 | -122.287 | -122.2046 | 0.18768 | 0.1648 | 0.064087 | 0.11444 | 0.013733 | -0.009155 | -0.077819 | -0.073242 | 0.25635 | 0.21973 | 0.20142 | 0.22888 | 0.21057 | 0.13733 | 0.032044 | 0.2655 | 122.2229 | -0.050354 | 122.2183 | 0 | 122.2092 | -122.2366 | -122.2961 | 0.082398 | 122.2137 | -0.036621 | 0.65918
3099.8438 | 122.374 | -0.10071 | 122.2549 | -0.15083 | -0.043457 | -0.00018577 | 0.023364 | 8.47e-06 | -0.01053 | -0.0017325 | -0.089386 | 0.0074469 | 0.062568 | 0.050473 | -0.016874 | 0.028903 | -0.0015209 | -0.12817 | -0.018311 | -0.059509 | -0.064087 | 0.004578 | -0.09613 | -0.013733 | 0.49896 | 122.1725 | -0.10529 | 122.0581 | 0.059509 | 0.009155 | 0.059509 | 0.041199 | -122.2733 | -122.319 | 0.10529 | 0.086975 | 0.004578 | 0.045776 | -0.036621 | -0.004578 | -0.082398 | -0.19684 | 0.16022 | 0.16022 | 0.10986 | 0.16479 | 0.11444 | 0.064087 | -0.004578 | 0.16479 | 122.1634 | 0.041198 | 122.2778 | 0.082397 | 122.2733 | -122.3145 | -122.3602 | 0.036621 | 122.1588 | -0.027466 | 0.59967
3101.625 | 122.4289 | -0.059509 | 122.2137 | -0.15846 | -0.044739 | 0.004941 | 0.0208 | -0.00041873 | -0.011598 | -0.0025869 | -0.071076 | 0.0061651 | 0.063423 | 0.045559 | -0.01602 | 0.027408 | -0.0040845 | -0.036621 | -0.054932 | -0.004578 | 0.041199 | 0.13733 | -0.022888 | 0.073242 | 0.48523 | 122.1359 | -0.059509 | 122.1542 | 0.14648 | 0.10986 | 0.15106 | 0.054931 | -122.2687 | -122.1725 | 0.19684 | 0.13275 | 0.036621 | 0.07782 | -0.01831 | 0 | -0.07782 | -0.059509 | 0.20599 | 0.21057 | 0.16937 | 0.21057 | 0.16937 | 0.14191 | 0.045777 | 0.20599 | 122.2137 | -0.050354 | 122.1954 | 0.004577 | 122.1954 | -122.2183 | -122.2733 | 0.10071 | 122.2137 | 0.022888 | 0.54474
3103.3125 | 122.4472 | -0.054932 | 122.2366 | -0.11269 | -0.044312 | 0.0030184 | 0.023364 | -0.0034095 | -0.01053 | -0.0019461 | -0.031403 | 0.0061651 | 0.064277 | 0.045559 | -0.01901 | 0.028049 | -0.0042981 | -0.064087 | -0.050354 | -0.004578 | 0.059509 | 0.16022 | 0.018311 | 0.09613 | 0.64545 | 122.1359 | -0.050354 | 122.1451 | 0.18768 | 0.13733 | 0.16479 | 0.050354 | -122.287 | -122.1771 | 0.21515 | 0.15106 | 0.073243 | 0.10071 | 0.022889 | 0.004578 | -0.10071 | -0.091552 | 0.24261 | 0.21973 | 0.19226 | 0.21515 | 0.18768 | 0.16479 | 0.064087 | 0.23804 | 122.1954 | -0.045776 | 122.1863 | 0.004578 | 122.1909 | -122.2412 | -122.287 | 0.11444 | 122.2 | -0.009155 | 0.70038
3105.0625 | 122.3557 | -0.091553 | 122.2504 | -0.089798 | -0.044525 | 0.0036594 | 0.026141 | -0.0036231 | -0.010316 | -0.0062185 | -0.12296 | 0.0070197 | 0.06385 | 0.052182 | -0.017301 | 0.027835 | -0.0064343 | -0.07782 | -0.027466 | -0.032043 | -0.032043 | 0.073242 | -0.068665 | 0.022888 | 0.51727 | 122.1909 | -0.086975 | 122.0901 | 0.10071 | 0.027466 | 0.07782 | 0.05951 | -122.2778 | -122.2824 | 0.16479 | 0.11444 | 0.022888 | 0.054931 | -0.036622 | 0.004578 | -0.059509 | -0.16022 | 0.19226 | 0.16937 | 0.11902 | 0.16479 | 0.11444 | 0.10529 | 0 | 0.18768 | 122.1771 | 0.004577 | 122.2778 | 0.064087 | 122.2824 | -122.2824 | -122.3373 | 0.05951 | 122.1817 | 0.013733 | 0.60883
3106.7656 | 122.3648 | -0.091553 | 122.2412 | -0.089798 | -0.045807 | 0.003873 | 0.024859 | -0.0036231 | -0.010316 | -0.0030141 | -0.1077 | 0.0061651 | 0.064704 | 0.052395 | -0.016874 | 0.028262 | -0.0045117 | -0.10071 | -0.022888 | -0.036621 | -0.059509 | 0.022888 | -0.086975 | -0.018311 | 0.5127 | 122.1863 | -0.091553 | 122.081 | 0.10529 | 0.022888 | 0.073242 | 0.054932 | -122.2641 | -122.3007 | 0.11444 | 0.073242 | 0.004578 | 0.01831 | -0.050354 | 0 | -0.054932 | -0.16022 | 0.19684 | 0.16479 | 0.11444 | 0.16479 | 0.11444 | 0.059509 | -0.022888 | 0.19684 | 122.1725 | 0.013733 | 122.2778 | 0.068665 | 122.2778 | -122.2778 | -122.3328 | 0.032044 | 122.1725 | -0.009155 | 0.60425
3108.5156 | 122.3282 | -0.10071 | 122.2595 | -0.15083 | -0.044953 | 0.0036594 | 0.023578 | -0.0012731 | -0.01053 | -0.0045095 | -0.046661 | 0.0053107 | 0.064704 | 0.041928 | -0.015592 | 0.028049 | -0.0028027 | -0.14191 | -0.004578 | -0.059509 | -0.07782 | 0.022888 | -0.091553 | -0.009155 | 0.50812 | 122.2 | -0.09613 | 122.0123 | 0.045776 | 0 | 0.032043 | 0.041199 | -122.2641 | -122.3373 | 0.1236 | 0.091553 | 0.009155 | 0.050354 | -0.032044 | 0.004578 | -0.059509 | -0.24719 | 0.14648 | 0.13275 | 0.10071 | 0.12817 | 0.09613 | 0.082397 | -0.018311 | 0.14191 | 122.1085 | 0.054931 | 122.2961 | 0.09613 | 122.3007 | -122.319 | -122.3557 | 0.022888 | 122.113 | -0.041199 | 0.60883
3110.2812 | 122.3465 | -0.10529 | 122.2412 | -0.13557 | -0.041748 | 0.0017368 | 0.024646 | 0.0038537 | -0.0098886 | -0.0064321 | -0.12296 | 0.0042425 | 0.064491 | 0.055173 | -0.017088 | 0.026767 | -0.00088011 | -0.13733 | 0 | -0.045776 | -0.09613 | -0.004578 | -0.15106 | -0.036621 | 0.33875 | 122.1634 | -0.09613 | 122.049 | 0.050354 | -0.027466 | 0.054932 | 0.05951 | -122.2412 | -122.3373 | 0.10071 | 0.068665 | -0.045776 | 0.009155 | -0.10529 | 0.009156 | -0.07782 | -0.19226 | 0.15564 | 0.16022 | 0.07782 | 0.15106 | 0.068664 | 0.041198 | -0.050354 | 0.14648 | 122.1451 | 0.045776 | 122.2595 | 0.10529 | 122.2687 | -122.287 | -122.3373 | 0.009156 | 122.1542 | -0.032043 | 0.44403
3112.0469 | 122.3923 | -0.086975 | 122.2687 | -0.13557 | -0.042816 | 0.0017368 | 0.020373 | 0.00022207 | -0.0090342 | -0.0034415 | -0.019196 | 0.0055243 | 0.062995 | 0.044064 | -0.017301 | 0.026981 | -0.0062207 | -0.059509 | -0.050354 | -0.009155 | 0.009155 | 0.12817 | 0 | 0.086975 | 0.60883 | 122.1313 | -0.082397 | 122.0856 | 0.13275 | 0.086975 | 0.091553 | 0.07782 | -122.319 | -122.2595 | 0.21515 | 0.17395 | 0.086975 | 0.09613 | 0.009155 | 0.004578 | -0.13733 | -0.18311 | 0.21973 | 0.17853 | 0.17395 | 0.17395 | 0.16937 | 0.13733 | 0.01831 | 0.21515 | 122.168 | -0.041199 | 122.2137 | 0.036621 | 122.2183 | -122.2778 | -122.3511 | 0.09613 | 122.1725 | 0.027466 | 0.6958
3113.75 | 122.4243 | -0.054932 | 122.2412 | -0.10506 | -0.044953 | 0.0036594 | 0.022509 | -0.0021277 | -0.01117 | -0.0034415 | -0.031403 | 0.0057379 | 0.062354 | 0.044705 | -0.015806 | 0.027194 | -0.0049389 | -0.068665 | -0.045776 | -0.009155 | 0.018311 | 0.13733 | 0.009155 | 0.082397 | 0.62256 | 122.1359 | -0.073242 | 122.1176 | 0.16479 | 0.1236 | 0.11902 | 0.045777 | -122.287 | -122.2229 | 0.19226 | 0.13733 | 0.064087 | 0.091552 | 0.01831 | -0.01831 | -0.10529 | -0.1236 | 0.21973 | 0.17395 | 0.17853 | 0.19226 | 0.19684 | 0.14648 | 0.027466 | 0.23804 | 122.1909 | -0.036621 | 122.2092 | 0.009156 | 122.1909 | -122.2504 | -122.3145 | 0.073243 | 122.1725 | -0.013733 | 0.67749
3115.5156 | 122.3785 | -0.10529 | 122.2595 | -0.12794 | -0.042603 | 0.0034456 | 0.026782 | 0.00022207 | -0.0075388 | -0.0047231 | -0.092438 | 0.0048833 | 0.06385 | 0.048123 | -0.018583 | 0.028903 | -0.0064343 | -0.082397 | -0.022888 | -0.050354 | -0.050354 | 0.054932 | -0.068665 | 0.018311 | 0.53558 | 122.1771 | -0.073242 | 122.0856 | 0.09613 | 0.022888 | 0.07782 | 0.054932 | -122.2824 | -122.3099 | 0.16022 | 0.1236 | 0.036621 | 0.068665 | -0.018311 | 0.032044 | -0.082397 | -0.17395 | 0.20142 | 0.18311 | 0.12817 | 0.15106 | 0.09613 | 0.10529 | 0 | 0.16937 | 122.1588 | 0.027466 | 122.2504 | 0.082398 | 122.2824 | -122.3099 | -122.3328 | 0.054932 | 122.1909 | 0.022889 | 0.64087
3117.2656 | 122.4609 | -0.068665 | 122.2092 | -0.18135 | -0.044739 | 0.00024143 | 0.020587 | -0.0059729 | -0.0092478 | -0.0030141 | 0.011322 | 0.0050971 | 0.064918 | 0.052395 | -0.017942 | 0.026981 | -0.0034435 | -0.050354 | -0.041199 | 0.004578 | 0.059509 | 0.18768 | 0.036621 | 0.10071 | 0.63171 | 122.1405 | -0.050354 | 122.1359 | 0.20142 | 0.14648 | 0.16022 | 0.073243 | -122.2504 | -122.1497 | 0.25635 | 0.16937 | 0.10529 | 0.09613 | 0.032043 | 0.018311 | -0.068664 | -0.073242 | 0.27008 | 0.22888 | 0.21515 | 0.21057 | 0.19684 | 0.1831 | 0.054931 | 0.25177 | 122.1863 | -0.045777 | 122.1909 | 0.027466 | 122.2092 | -122.2046 | -122.2595 | 0.12817 | 122.2046 | 0.018311 | 0.70038
3119.0156 | 122.4243 | -0.045776 | 122.2321 | -0.15846 | -0.044098 | 0.0034456 | 0.021869 | -0.0029821 | -0.010316 | -0.0049367 | -0.013092 | 0.0048833 | 0.065345 | 0.045346 | -0.017088 | 0.026553 | -0.0066479 | -0.064087 | -0.041199 | -0.009155 | 0.036621 | 0.15106 | 0.018311 | 0.086975 | 0.64545 | 122.1451 | -0.059509 | 122.1313 | 0.1831 | 0.13275 | 0.15106 | 0.036621 | -122.2733 | -122.1954 | 0.19684 | 0.13275 | 0.064087 | 0.09613 | 0.027466 | -0.013733 | -0.086975 | -0.10071 | 0.22888 | 0.19684 | 0.17853 | 0.21057 | 0.19226 | 0.16022 | 0.045776 | 0.24261 | 122.1909 | -0.032044 | 122.2046 | 0.004577 | 122.1909 | -122.2412 | -122.2916 | 0.082397 | 122.1771 | -0.018311 | 0.69122
3120.7812 | 122.4106 | -0.059509 | 122.2321 | -0.19661 | -0.04538 | 0.0025912 | 0.024432 | 0.00086307 | -0.009675 | -0.0064321 | -0.071076 | 0.0042425 | 0.062995 | 0.0509 | -0.017301 | 0.027194 | -0.0062207 | -0.07782 | -0.059509 | -0.009155 | 0.004578 | 0.13733 | -0.041199 | 0.064087 | 0.4715 | 122.1222 | -0.059509 | 122.1222 | 0.13275 | 0.086975 | 0.12817 | 0.050354 | -122.2916 | -122.2275 | 0.19684 | 0.1236 | 0.01831 | 0.073242 | -0.032044 | 0 | -0.10986 | -0.10986 | 0.19226 | 0.18768 | 0.14648 | 0.18768 | 0.14648 | 0.14648 | 0.013733 | 0.19226 | 122.1817 | -0.050354 | 122.1817 | 0 | 122.1817 | -122.2412 | -122.2916 | 0.064087 | 122.1817 | -0.018311 | 0.53101
3122.4688 | 122.3831 | -0.09613 | 122.2595 | -0.10506 | -0.045594 | 0.0019504 | 0.025714 | -0.0061865 | -0.0088206 | -0.0030141 | -0.10159 | 0.0057379 | 0.064491 | 0.048123 | -0.016447 | 0.02634 | -0.0070751 | -0.12817 | 0 | -0.041199 | -0.064087 | 0.004578 | -0.073242 | 0.009155 | 0.5127 | 122.1954 | -0.073242 | 122.0764 | 0.082397 | 0.013733 | 0.073242 | 0.054931 | -122.2595 | -122.3236 | 0.10071 | 0.10528 | 0.022888 | 0.050354 | -0.032043 | 0.022888 | -0.064086 | -0.18311 | 0.17853 | 0.16937 | 0.10986 | 0.14648 | 0.086975 | 0.045777 | -0.022888 | 0.15564 | 122.1497 | 0.041199 | 122.2687 | 0.09613 | 122.2916 | -122.3007 | -122.3328 | 0.032043 | 122.1725 | -0.032044 | 0.60882
3124.2344 | 122.2916 | -0.10071 | 122.2733 | -0.15846 | -0.043671 | 0.0060092 | 0.026568 | 0.0017175 | -0.008607 | -0.0042959 | -0.12906 | 0.0057379 | 0.065986 | 0.04855 | -0.017088 | 0.029758 | -0.0045117 | -0.1236 | 0 | -0.054932 | -0.09613 | -0.036621 | -0.14648 | -0.059509 | 0.35706 | 122.1954 | -0.091553 | 122.0261 | -0.004578 | -0.068665 | 0.018311 | 0.045776 | -122.2733 | -122.3694 | 0.064087 | 0.041199 | -0.045776 | -0.004577 | -0.091552 | 0.009155 | -0.077819 | -0.24719 | 0.09613 | 0.11902 | 0.032043 | 0.10986 | 0.022888 | 0.018311 | -0.041198 | 0.086975 | 122.1176 | 0.054932 | 122.287 | 0.10071 | 122.2961 | -122.3282 | -122.3648 | 0.004578 | 122.1268 | -0.022888 | 0.45776
3126 | 122.4701 | -0.032043 | 122.2137 | -0.15083 | -0.041748 | 0.003232 | 0.022723 | 0.0017175 | -0.010316 | -0.0010915 | -0.040558 | 0.0061651 | 0.064277 | 0.048764 | -0.016233 | 0.027621 | -0.0038709 | -0.054932 | -0.068665 | 0.018311 | 0.022888 | 0.12817 | -0.032043 | 0.059509 | 0.46234 | 122.1451 | -0.064087 | 122.168 | 0.16479 | 0.09613 | 0.1831 | 0.050354 | -122.2824 | -122.1909 | 0.16022 | 0.091552 | 0 | 0.041198 | -0.050354 | -0.032044 | -0.068664 | -0.045776 | 0.19684 | 0.21515 | 0.12817 | 0.24719 | 0.16022 | 0.10986 | 0.004577 | 0.22888 | 122.2321 | -0.086976 | 122.2092 | -0.036622 | 122.1771 | -122.1954 | -122.2778 | 0.054931 | 122.2 | -0.022889 | 0.49438
3127.7031 | 122.4243 | -0.059509 | 122.2549 | -0.18898 | -0.043244 | 0.003232 | 0.024646 | -0.00084593 | -0.010316 | -0.0036551 | -0.052765 | 0.0055243 | 0.064704 | 0.041501 | -0.017301 | 0.025272 | -0.0077161 | -0.11902 | -0.064087 | -0.018311 | -0.013733 | 0.082397 | -0.050354 | 0.050354 | 0.44403 | 122.1451 | -0.068665 | 122.0993 | 0.11902 | 0.068665 | 0.11902 | 0.041198 | -122.319 | -122.2687 | 0.14191 | 0.10986 | 0.009155 | 0.068665 | -0.032043 | -0.009156 | -0.10986 | -0.15564 | 0.17853 | 0.17853 | 0.12817 | 0.18768 | 0.13733 | 0.10071 | 0.004578 | 0.18768 | 122.168 | -0.045776 | 122.2137 | -0.004578 | 122.2046 | -122.2733 | -122.3236 | 0.045776 | 122.1588 | -0.05951 | 0.50354
3129.4531 | 122.4106 | -0.064087 | 122.2321 | -0.17372 | -0.043244 | 0.003232 | 0.0208 | -0.0025549 | -0.011811 | -0.0042959 | -0.013092 | 0.0038153 | 0.064277 | 0.041501 | -0.018797 | 0.027835 | -0.0047253 | -0.10071 | -0.050354 | -0.004578 | -0.004578 | 0.086975 | -0.054932 | 0.054932 | 0.44861 | 122.1268 | -0.07782 | 122.1085 | 0.10986 | 0.073242 | 0.1236 | 0.059509 | -122.2824 | -122.2366 | 0.15106 | 0.11902 | 0.009155 | 0.05951 | -0.050354 | -0.013733 | -0.10529 | -0.1236 | 0.17395 | 0.18768 | 0.13733 | 0.20142 | 0.15106 | 0.091553 | 0 | 0.18768 | 122.1863 | -0.045776 | 122.2046 | 0.013733 | 122.1909 | -122.2366 | -122.3099 | 0.059509 | 122.1725 | -0.036621 | 0.5127
3131.2188 | 122.3282 | -0.10986 | 122.2549 | -0.12032 | -0.043671 | 0.0010958 | 0.024859 | 0.00043587 | -0.010743 | -0.0053641 | -0.052765 | 0.0055243 | 0.062354 | 0.042355 | -0.015806 | 0.026126 | -0.0060071 | -0.13275 | -0.009155 | -0.050354 | -0.086975 | 0 | -0.091553 | -0.004578 | 0.5127 | 122.1771 | -0.10986 | 122.0261 | 0.045776 | -0.022888 | 0.013733 | 0.059509 | -122.2641 | -122.3419 | 0.10986 | 0.10529 | 0.01831 | 0.045776 | -0.041199 | 0 | -0.07782 | -0.22888 | 0.15564 | 0.1236 | 0.086975 | 0.1236 | 0.086975 | 0.050354 | -0.036621 | 0.15564 | 122.1359 | 0.041199 | 122.287 | 0.10071 | 122.287 | -122.3053 | -122.3648 | 0.022888 | 122.1359 | -0.022888 | 0.62256
3132.9844 | 122.319 | -0.09613 | 122.2595 | -0.11269 | -0.044953 | 0.0028048 | 0.024859 | 8.47e-06 | -0.0092478 | -0.0017325 | -0.077179 | 0.0059515 | 0.064704 | 0.049191 | -0.017301 | 0.026767 | -0.0042981 | -0.14648 | -0.009155 | -0.050354 | -0.07782 | 0 | -0.09613 | -0.013733 | 0.5127 | 122.1863 | -0.09613 | 122.0215 | 0.054932 | -0.009155 | 0.009155 | 0.045776 | -122.2687 | -122.3373 | 0.09613 | 0.082397 | 0 | 0.036621 | -0.045776 | 0 | -0.073242 | -0.23804 | 0.15106 | 0.10528 | 0.086975 | 0.10528 | 0.086975 | 0.050354 | -0.027466 | 0.15106 | 122.1176 | 0.041199 | 122.2824 | 0.086975 | 122.2824 | -122.3099 | -122.3557 | 0.01831 | 122.1176 | -0.050354 | 0.60882
3134.75 | 122.4335 | -0.07782 | 122.2321 | -0.13557 | -0.044312 | 0.0017368 | 0.024005 | -0.0027685 | -0.010957 | -0.0032277 | -0.0039367 | 0.0063787 | 0.065345 | 0.043637 | -0.016874 | 0.027194 | -0.0040845 | -0.10986 | -0.041199 | -0.022888 | -0.027466 | 0.082397 | -0.050354 | 0.032043 | 0.48523 | 122.1313 | -0.073242 | 122.113 | 0.13275 | 0.082397 | 0.1236 | 0.054932 | -122.2733 | -122.2595 | 0.16022 | 0.10986 | 0.027466 | 0.054931 | -0.027466 | 0.004578 | -0.10071 | -0.11902 | 0.21057 | 0.20142 | 0.16022 | 0.19684 | 0.15564 | 0.10528 | -0.004578 | 0.20599 | 122.1863 | -0.018311 | 122.2046 | 0.036621 | 122.2092 | -122.2549 | -122.3053 | 0.050354 | 122.1909 | -0.032043 | 0.56305
3136.5156 | 122.3236 | -0.10071 | 122.2733 | -0.18898 | -0.043457 | 0.005582 | 0.026355 | 8.47e-06 | -0.012025 | -0.0030141 | -0.1138 | 0.0072333 | 0.062782 | 0.053036 | -0.01666 | 0.026981 | -0.0030163 | -0.10986 | -0.018311 | -0.045776 | -0.09613 | -0.027466 | -0.15564 | -0.059509 | 0.36163 | 122.1771 | -0.09613 | 122.0169 | -0.004578 | -0.059509 | 0.013733 | 0.054932 | -122.2916 | -122.3694 | 0.073242 | 0.041199 | -0.054932 | -0.013733 | -0.10986 | 0.004578 | -0.09613 | -0.25635 | 0.09613 | 0.11444 | 0.041199 | 0.10986 | 0.036621 | 0.01831 | -0.050354 | 0.091552 | 122.113 | 0.027465 | 122.2733 | 0.082397 | 122.2778 | -122.319 | -122.3694 | 0.004578 | 122.1176 | -0.009155 | 0.46234
3138.2031 | 122.4564 | -0.036621 | 122.2092 | -0.21187 | -0.043457 | 0.0036594 | 0.024005 | -0.00041873 | -0.01117 | -0.0025869 | -0.055817 | 0.0046697 | 0.061927 | 0.049405 | -0.017729 | 0.027408 | -0.0036573 | -0.036621 | -0.059509 | 0.004578 | 0.050354 | 0.12817 | -0.032043 | 0.073242 | 0.48523 | 122.1725 | -0.064087 | 122.1634 | 0.16479 | 0.1236 | 0.16022 | 0.041199 | -122.2687 | -122.1588 | 0.1648 | 0.10986 | 0.004578 | 0.068664 | -0.036621 | -0.027466 | -0.036621 | -0.045776 | 0.20142 | 0.19684 | 0.16022 | 0.2243 | 0.18768 | 0.1236 | 0.045776 | 0.22888 | 122.2275 | -0.064087 | 122.2366 | -0.022888 | 122.2092 | -122.2046 | -122.2733 | 0.086975 | 122.2 | 0 | 0.52185
3139.9531 | 122.3557 | -0.073242 | 122.2504 | -0.12794 | -0.041535 | 0.0034456 | 0.025714 | -0.0012731 | -0.012025 | -0.0040823 | -0.10159 | 0.0076605 | 0.064918 | 0.04855 | -0.018797 | 0.028262 | -0.0053661 | -0.073242 | -0.022888 | -0.032043 | -0.018311 | 0.064087 | -0.073242 | 0.018311 | 0.49896 | 122.1588 | -0.091553 | 122.0673 | 0.082397 | 0.009155 | 0.091553 | 0.041199 | -122.2733 | -122.2687 | 0.13733 | 0.091553 | 0 | 0.050354 | -0.041199 | -0.018311 | -0.091553 | -0.1831 | 0.15564 | 0.16479 | 0.082397 | 0.18311 | 0.10071 | 0.09613 | 0.013732 | 0.17395 | 122.1588 | 0.009155 | 122.2504 | 0.050354 | 122.2321 | -122.2824 | -122.3419 | 0.054931 | 122.1405 | 0 | 0.5722
3141.7188 | 122.493 | -0.045776 | 122.2137 | -0.13557 | -0.045594 | 0.001523 | 0.0208 | -0.0021277 | -0.011598 | -0.0013051 | -0.0039367 | 0.0046697 | 0.062141 | 0.042355 | -0.015592 | 0.027194 | -0.0066479 | -0.086975 | -0.054932 | -0.022888 | 0.041199 | 0.16479 | 0.032043 | 0.10986 | 0.63171 | 122.1313 | -0.064087 | 122.1634 | 0.21515 | 0.17395 | 0.16479 | 0.022888 | -122.2687 | -122.1725 | 0.21057 | 0.15564 | 0.077819 | 0.13275 | 0.054931 | -0.018311 | -0.082397 | -0.050354 | 0.26093 | 0.21057 | 0.21973 | 0.22888 | 0.23804 | 0.18768 | 0.064087 | 0.27924 | 122.2275 | -0.032044 | 122.1954 | -0.009156 | 122.1771 | -122.2366 | -122.2778 | 0.086975 | 122.2092 | -0.041199 | 0.67749
3143.4062 | 122.3694 | -0.09613 | 122.2458 | -0.082169 | -0.045807 | 0.0010958 | 0.0255 | -0.0068273 | -0.012879 | -0.0021597 | -0.074127 | 0.0076605 | 0.062995 | 0.059231 | -0.018156 | 0.026553 | -0.00066651 | -0.13733 | -0.013733 | -0.059509 | -0.10529 | -0.018311 | -0.11444 | -0.022888 | 0.49439 | 122.1771 | -0.086975 | 122.0444 | 0.054932 | 0.004578 | 0.045776 | 0.036621 | -122.2595 | -122.3511 | 0.077819 | 0.073242 | -0.018311 | 0.036621 | -0.054932 | 0.009155 | -0.068665 | -0.20142 | 0.15106 | 0.14191 | 0.10071 | 0.13275 | 0.091553 | 0.041198 | -0.045777 | 0.14191 | 122.1313 | 0.045776 | 122.2641 | 0.082397 | 122.2733 | -122.3053 | -122.3328 | -0.009156 | 122.1405 | -0.041199 | 0.59052
3145.1562 | 122.3282 | -0.10986 | 122.2595 | -0.082169 | -0.045166 | 0.001523 | 0.026141 | 0.0012903 | -0.01117 | -0.0040823 | -0.083283 | 0.0063787 | 0.068122 | 0.047055 | -0.015592 | 0.027408 | -0.0077161 | -0.14648 | -0.022888 | -0.050354 | -0.09613 | 0.004578 | -0.10529 | -0.022888 | 0.49439 | 122.2 | -0.091553 | 122.049 | 0.050354 | 0.009155 | 0.036621 | 0.059509 | -122.2824 | -122.3557 | 0.11444 | 0.086975 | 0.004577 | 0.027466 | -0.054932 | 0.01831 | -0.059509 | -0.21057 | 0.16022 | 0.14648 | 0.11902 | 0.12817 | 0.10071 | 0.054932 | -0.045776 | 0.14191 | 122.1405 | 0.027466 | 122.2916 | 0.086975 | 122.3099 | -122.3099 | -122.3511 | 0.013733 | 122.1588 | -0.036621 | 0.60425
3146.9062 | 122.3877 | -0.064087 | 122.2458 | -0.16609 | -0.043885 | 0.0034456 | 0.020587 | -0.0040503 | -0.0090342 | -0.0049367 | -0.031403 | 0.0065923 | 0.062782 | 0.050046 | -0.015379 | 0.024417 | -0.0062207 | -0.07782 | -0.050354 | -0.004578 | 0.004578 | 0.1236 | 0 | 0.082397 | 0.6134 | 122.1497 | -0.07782 | 122.0947 | 0.12817 | 0.082397 | 0.09613 | 0.059509 | -122.2961 | -122.2412 | 0.18768 | 0.14648 | 0.064087 | 0.086975 | 0.004578 | -0.013733 | -0.096131 | -0.15106 | 0.19226 | 0.16022 | 0.14648 | 0.17395 | 0.16022 | 0.12817 | 0.009156 | 0.20599 | 122.1725 | -0.045776 | 122.2275 | 0.013733 | 122.2137 | -122.2504 | -122.3236 | 0.068665 | 122.1588 | -0.013733 | 0.67749
3148.6094 | 122.4014 | -0.073242 | 122.2275 | -0.19661 | -0.042816 | 0.0019504 | 0.022509 | 0.00064947 | -0.0083932 | -0.0040823 | -0.022247 | 0.0048833 | 0.065559 | 0.04855 | -0.015592 | 0.026126 | -0.0032299 | -0.11444 | -0.054932 | -0.009155 | -0.032043 | 0.073242 | -0.059509 | 0.036621 | 0.46234 | 122.1313 | -0.073242 | 122.0901 | 0.10529 | 0.073242 | 0.10071 | 0.064087 | -122.2824 | -122.2595 | 0.14648 | 0.10986 | 0.013733 | 0.045776 | -0.050354 | 0 | -0.09613 | -0.13733 | 0.17853 | 0.17395 | 0.14648 | 0.17395 | 0.14648 | 0.082397 | -0.022888 | 0.17853 | 122.1634 | -0.045777 | 122.2046 | 0.01831 | 122.2046 | -122.2366 | -122.3007 | 0.041199 | 122.1634 | -0.041199 | 0.53558
3150.375 | 122.4152 | -0.064087 | 122.2366 | -0.13557 | -0.046662 | 0.0028048 | 0.023791 | -0.0014867 | -0.009675 | -0.0040823 | -0.016144 | 0.0055243 | 0.065345 | 0.052182 | -0.016874 | 0.026767 | -0.0079297 | -0.10529 | -0.045776 | -0.032043 | -0.032043 | 0.068665 | -0.054932 | 0.045776 | 0.45319 | 122.1451 | -0.082397 | 122.0993 | 0.10529 | 0.064087 | 0.10071 | 0.032044 | -122.2824 | -122.2687 | 0.13275 | 0.10986 | 0.009155 | 0.077819 | -0.022889 | -0.01831 | -0.091552 | -0.13733 | 0.16937 | 0.1648 | 0.12817 | 0.18311 | 0.14648 | 0.10071 | 0 | 0.18768 | 122.1817 | -0.013733 | 122.2275 | 0.018311 | 122.2092 | -122.2687 | -122.319 | 0.032044 | 122.1634 | -0.041199 | 0.51727
3152.1562 | 122.4152 | -0.054932 | 122.2321 | -0.18898 | -0.04303 | 0.003232 | 0.024859 | -0.0023413 | -0.0094614 | -0.0023733 | -0.064972 | 0.0070197 | 0.064277 | 0.045346 | -0.015806 | 0.026767 | -0.0049389 | -0.073242 | -0.041199 | -0.013733 | 0.022888 | 0.14191 | -0.027466 | 0.068665 | 0.49439 | 122.1222 | -0.041199 | 122.1176 | 0.13275 | 0.091553 | 0.12817 | 0.041199 | -122.2733 | -122.2092 | 0.19684 | 0.1236 | 0.027466 | 0.082398 | -0.013733 | 0.013733 | -0.10986 | -0.11444 | 0.18768 | 0.18311 | 0.14649 | 0.16937 | 0.13275 | 0.15564 | 0.036621 | 0.17395 | 122.1588 | -0.027466 | 122.1634 | 0.013733 | 122.1771 | -122.2458 | -122.2733 | 0.07782 | 122.1725 | -0.01831 | 0.54932
3153.8438 | 122.4518 | -0.050354 | 122.2321 | -0.082169 | -0.044739 | 0.00066863 | 0.021869 | 0.0010767 | -0.010957 | -0.0028005 | -0.031403 | 0.0031745 | 0.064918 | 0.047909 | -0.018369 | 0.026553 | -0.0030163 | -0.059509 | -0.050354 | -0.004578 | 0.045776 | 0.16022 | 0.041199 | 0.09613 | 0.64545 | 122.1497 | -0.059509 | 122.1359 | 0.18768 | 0.13733 | 0.15564 | 0.045776 | -122.2824 | -122.1863 | 0.21057 | 0.14648 | 0.091553 | 0.10071 | 0.045777 | -0.009155 | -0.082398 | -0.096131 | 0.23804 | 0.20599 | 0.18768 | 0.21515 | 0.19684 | 0.16479 | 0.050354 | 0.24719 | 122.1954 | -0.045776 | 122.2092 | 0 | 122.2 | -122.2366 | -122.2916 | 0.09613 | 122.1863 | -0.009155 | 0.6958
3155.5938 | 122.3373 | -0.082397 | 122.2549 | -0.15083 | -0.043885 | 0.0010958 | 0.022937 | -0.0031957 | -0.011384 | -0.0042959 | -0.046661 | 0.0070197 | 0.062568 | 0.046628 | -0.018369 | 0.027408 | -0.0045117 | -0.073242 | -0.050354 | -0.013733 | -0.018311 | 0.07782 | -0.036621 | 0.032043 | 0.55389 | 122.2 | -0.086975 | 122.049 | 0.068665 | 0.022888 | 0.041199 | 0.068664 | -122.3053 | -122.2733 | 0.16022 | 0.11444 | 0.045776 | 0.045776 | -0.022888 | -0.004578 | -0.054932 | -0.20599 | 0.15106 | 0.1236 | 0.10528 | 0.12817 | 0.10986 | 0.091553 | -0.004578 | 0.15564 | 122.1359 | -0.036621 | 122.287 | 0.032043 | 122.2824 | -122.2687 | -122.3419 | 0.064086 | 122.1313 | 0.009155 | 0.63629
3157.3594 | 122.3099 | -0.10529 | 122.2641 | -0.15846 | -0.040253 | 0.0047274 | 0.027636 | 0.0010767 | -0.0071116 | -0.0047231 | -0.1199 | 0.0072333 | 0.063209 | 0.0509 | -0.016233 | 0.028049 | -0.0094251 | -0.11902 | -0.013733 | -0.041199 | -0.10986 | -0.045776 | -0.16937 | -0.045776 | 0.3479 | 122.2 | -0.086975 | 122.0261 | 0.018311 | -0.041199 | 0.022888 | 0.064087 | -122.2778 | -122.374 | 0.05951 | 0.05951 | -0.064087 | -0.004577 | -0.12817 | 0.018311 | -0.064087 | -0.23804 | 0.1236 | 0.12817 | 0.064087 | 0.10986 | 0.045776 | -0.004577 | -0.068664 | 0.10529 | 122.113 | 0.027466 | 122.287 | 0.091553 | 122.3053 | -122.3053 | -122.3511 | -0.004577 | 122.1313 | -0.013733 | 0.45319
3159.0625 | 122.4289 | -0.054932 | 122.2458 | -0.15083 | -0.044312 | 0.0040866 | 0.024218 | 0.0029993 | -0.0094614 | -0.0057913 | -0.055817 | 0.0055243 | 0.065559 | 0.045132 | -0.016874 | 0.026126 | -0.0070751 | -0.068665 | -0.059509 | 0 | 0.009155 | 0.14191 | -0.032043 | 0.064087 | 0.49439 | 122.1405 | -0.054932 | 122.1359 | 0.12817 | 0.10071 | 0.12817 | 0.054932 | -122.3053 | -122.2366 | 0.19684 | 0.11902 | 0.022889 | 0.064087 | -0.032043 | 0 | -0.10529 | -0.10986 | 0.18311 | 0.18311 | 0.15564 | 0.18311 | 0.15564 | 0.14191 | 0.009155 | 0.18311 | 122.1909 | -0.059509 | 122.1954 | -0.004577 | 122.1954 | -122.2458 | -122.3007 | 0.064087 | 122.1909 | -0.013733 | 0.54932
3160.8281 | 122.3145 | -0.09613 | 122.2778 | -0.17372 | -0.041962 | 0.003232 | 0.024646 | 0.0044947 | -0.010743 | -0.0040823 | -0.12601 | 0.0076605 | 0.065559 | 0.051114 | -0.014951 | 0.028903 | -0.0047253 | -0.10986 | -0.036621 | -0.032043 | -0.07782 | -0.013733 | -0.11902 | -0.045776 | 0.37994 | 122.1954 | -0.091553 | 122.0261 | 0.009155 | -0.054932 | 0.027466 | 0.064087 | -122.3145 | -122.3557 | 0.082397 | 0.050354 | -0.022889 | -0.013733 | -0.086976 | 0.004577 | -0.082397 | -0.25177 | 0.10528 | 0.1236 | 0.041198 | 0.11902 | 0.036621 | 0.01831 | -0.045777 | 0.10071 | 122.1176 | -0.004578 | 122.287 | 0.059509 | 122.2916 | -122.3099 | -122.3694 | 0.01831 | 122.1222 | -0.013733 | 0.47607
3162.5938 | 122.3328 | -0.10529 | 122.2778 | -0.12032 | -0.045807 | 0.001523 | 0.024859 | 0.00043587 | -0.012452 | -0.0023733 | -0.080231 | 0.0065923 | 0.064704 | 0.049405 | -0.01666 | 0.028262 | -0.0032299 | -0.14648 | -0.018311 | -0.050354 | -0.09613 | -0.004578 | -0.10529 | -0.022888 | 0.48523 | 122.2092 | -0.086975 | 122.0261 | 0.064087 | -0.004578 | 0.045776 | 0.054932 | -122.2961 | -122.374 | 0.10071 | 0.082398 | 0 | 0.027466 | -0.054932 | 0.018311 | -0.068665 | -0.25177 | 0.16937 | 0.15106 | 0.10071 | 0.13275 | 0.082397 | 0.045776 | -0.045776 | 0.15106 | 122.113 | 0.032043 | 122.2961 | 0.086975 | 122.3145 | -122.3282 | -122.3648 | 0.009156 | 122.1313 | -0.041198 | 0.59052
3164.3594 | 122.3236 | -0.10529 | 122.2412 | -0.15083 | -0.040467 | 0.0013094 | 0.025714 | -0.0031957 | -0.008607 | -0.0038687 | -0.1199 | 0.0050971 | 0.061927 | 0.05325 | -0.01602 | 0.028049 | -0.0055799 | -0.10986 | -0.004578 | -0.036621 | -0.082397 | -0.013733 | -0.14191 | -0.064087 | 0.36621 | 122.1909 | -0.091553 | 122.0306 | 0.004578 | -0.041199 | 0.036621 | 0.068665 | -122.2458 | -122.3236 | 0.091553 | 0.041199 | -0.036621 | -0.027466 | -0.10529 | 0.013733 | -0.050354 | -0.21057 | 0.10986 | 0.14191 | 0.064087 | 0.12817 | 0.050354 | 0.022888 | -0.045776 | 0.096131 | 122.1222 | 0.032043 | 122.2824 | 0.10071 | 122.2961 | -122.2778 | -122.3328 | 0.022889 | 122.1359 | -0.004577 | 0.4715
3166.1094 | 122.3373 | -0.10986 | 122.2549 | -0.17372 | -0.045166 | 0.003232 | 0.024005 | -0.00063233 | -0.011598 | -0.0032277 | -0.04361 | 0.0063787 | 0.065559 | 0.0462 | -0.015379 | 0.027194 | -0.0049389 | -0.086975 | -0.032043 | -0.050354 | -0.064087 | 0.041199 | -0.082397 | 0.018311 | 0.5127 | 122.1725 | -0.10529 | 122.0261 | 0.07782 | 0.018311 | 0.027466 | 0.059509 | -122.287 | -122.319 | 0.15106 | 0.12817 | 0.027466 | 0.068665 | -0.032043 | 0.004577 | -0.082398 | -0.22888 | 0.18768 | 0.13733 | 0.12817 | 0.13275 | 0.1236 | 0.091553 | -0.013733 | 0.18311 | 122.1313 | 0.018311 | 122.2778 | 0.07782 | 122.2824 | -122.3053 | -122.3602 | 0.045776 | 122.1359 | 0.022888 | 0.62256
3167.8125 | 122.4152 | -0.054932 | 122.2321 | -0.15846 | -0.04538 | 0.0013094 | 0.022296 | 0.0029993 | -0.0098886 | -0.0032277 | -0.013092 | 0.0048833 | 0.064491 | 0.050259 | -0.017729 | 0.027194 | -0.0028027 | -0.086975 | -0.064087 | 0 | 0.013733 | 0.12817 | -0.045776 | 0.064087 | 0.46692 | 122.1222 | -0.068665 | 122.1085 | 0.11444 | 0.082397 | 0.10986 | 0.054932 | -122.2961 | -122.2183 | 0.18311 | 0.11902 | 0.009156 | 0.064087 | -0.045776 | -0.013733 | -0.10986 | -0.1236 | 0.16937 | 0.16479 | 0.13733 | 0.17853 | 0.15106 | 0.12817 | 0.013733 | 0.18311 | 122.1771 | -0.064087 | 122.1909 | -0.009155 | 122.1771 | -122.2321 | -122.3007 | 0.068665 | 122.1634 | -0.032043 | 0.52185
3169.5781 | 122.4152 | -0.082397 | 122.2366 | -0.12032 | -0.044739 | 0.0017368 | 0.024218 | -0.0017005 | -0.011811 | -0.0042959 | -0.034454 | 0.0044561 | 0.063636 | 0.045132 | -0.017729 | 0.024631 | -0.0049389 | -0.1236 | -0.041199 | -0.018311 | -0.022888 | 0.07782 | -0.064087 | 0.041199 | 0.46234 | 122.1222 | -0.091553 | 122.0993 | 0.1236 | 0.068665 | 0.10071 | 0.064086 | -122.2778 | -122.2595 | 0.16022 | 0.1236 | 0.01831 | 0.05951 | -0.045776 | -0.009156 | -0.11444 | -0.13733 | 0.20599 | 0.18311 | 0.15106 | 0.19226 | 0.16022 | 0.096131 | -0.004577 | 0.21515 | 122.1909 | -0.022888 | 122.2137 | 0.041198 | 122.2046 | -122.2549 | -122.3282 | 0.059509 | 122.1817 | -0.041199 | 0.54474
3171.3438 | 122.374 | -0.068665 | 122.2458 | -0.1432 | -0.043671 | 0.0030184 | 0.025287 | 8.47e-06 | -0.010957 | -0.0038687 | -0.1199 | 0.0080877 | 0.061927 | 0.054959 | -0.020078 | 0.027621 | -0.0053661 | -0.07782 | -0.022888 | -0.041199 | -0.032043 | 0.073242 | -0.064087 | 0.022888 | 0.53101 | 122.168 | -0.086975 | 122.081 | 0.082397 | 0.013733 | 0.086975 | 0.027466 | -122.2687 | -122.2778 | 0.14191 | 0.091553 | 0.004578 | 0.064087 | -0.022888 | -0.01831 | -0.07782 | -0.16479 | 0.15106 | 0.15564 | 0.082398 | 0.17395 | 0.10071 | 0.11444 | 0.009156 | 0.16937 | 122.168 | 0.018311 | 122.2549 | 0.045777 | 122.2366 | -122.287 | -122.3328 | 0.036622 | 122.1497 | -0.009155 | 0.59967
3173.1094 | 122.4197 | -0.050354 | 122.2183 | -0.16609 | -0.042603 | 0.001523 | 0.026355 | -0.0053321 | -0.010102 | -0.0064321 | -0.077179 | 0.0068059 | 0.062782 | 0.052395 | -0.017088 | 0.029117 | -0.0066479 | -0.10529 | -0.022888 | -0.036621 | -0.059509 | 0.041199 | -0.10529 | 0.009155 | 0.41199 | 122.168 | -0.073242 | 122.1268 | 0.1236 | 0.073242 | 0.13733 | 0.013733 | -122.2412 | -122.2778 | 0.091553 | 0.059509 | -0.054932 | 0.045776 | -0.068665 | -0.022888 | -0.050354 | -0.091553 | 0.17395 | 0.18768 | 0.1236 | 0.21057 | 0.14648 | 0.07782 | -0.022888 | 0.19684 | 122.2 | 0.013733 | 122.2412 | 0.027466 | 122.2183 | -122.2549 | -122.2916 | -0.009155 | 122.1771 | -0.054932 | 0.46234
3174.7969 | 122.4609 | -0.054932 | 122.2412 | -0.17372 | -0.044312 | 0.0036594 | 0.021014 | -0.0029821 | -0.012666 | -0.0038687 | 0.011322 | 0.0057379 | 0.064063 | 0.054959 | -0.017088 | 0.027621 | -0.0051525 | -0.09613 | -0.054932 | -0.027466 | -0.004578 | 0.10986 | -0.018311 | 0.082397 | 0.57678 | 122.1542 | -0.07782 | 122.1405 | 0.17395 | 0.14648 | 0.15564 | 0.027466 | -122.2961 | -122.2458 | 0.16479 | 0.13733 | 0.036621 | 0.10986 | 0.009155 | -0.022888 | -0.086975 | -0.10071 | 0.22888 | 0.21057 | 0.20142 | 0.23346 | 0.2243 | 0.13733 | 0.022888 | 0.25177 | 122.2183 | -0.027466 | 122.2321 | 0 | 122.2092 | -122.2687 | -122.319 | 0.050354 | 122.1954 | -0.041198 | 0.63171
3176.5625 | 122.3602 | -0.09613 | 122.2595 | -0.036392 | -0.043244 | 0.001523 | 0.0208 | -0.0023413 | -0.009675 | -0.0021597 | -0.034454 | 0.0065923 | 0.063209 | 0.043423 | -0.016874 | 0.026553 | -0.0019483 | -0.07782 | -0.032043 | -0.022888 | -0.018311 | 0.10529 | -0.027466 | 0.045776 | 0.57678 | 122.1817 | -0.082397 | 122.0581 | 0.082397 | 0.022888 | 0.059509 | 0.073242 | -122.2916 | -122.2778 | 0.20142 | 0.14191 | 0.068664 | 0.068664 | -0.004578 | 0.013733 | -0.077819 | -0.20142 | 0.17853 | 0.15564 | 0.11902 | 0.14191 | 0.10528 | 0.12817 | 0.004577 | 0.16479 | 122.1405 | -0.009155 | 122.2641 | 0.064087 | 122.2778 | -122.2824 | -122.3419 | 0.077819 | 122.1542 | 0.01831 | 0.67291
3178.2656 | 122.3419 | -0.10529 | 122.2687 | -0.1432 | -0.043671 | 0.003873 | 0.027423 | 0.00064947 | -0.012452 | -0.0028005 | -0.12296 | 0.0068059 | 0.0662 | 0.054959 | -0.017301 | 0.02869 | -0.0068615 | -0.13733 | -0.009155 | -0.041199 | -0.086975 | -0.032043 | -0.15106 | -0.050354 | 0.3479 | 122.2046 | -0.09613 | 122.0398 | 0.018311 | -0.041199 | 0.036621 | 0.064087 | -122.2778 | -122.3557 | 0.073243 | 0.054932 | -0.045776 | -0.009155 | -0.10986 | 0.009156 | -0.064087 | -0.22888 | 0.1236 | 0.14191 | 0.064087 | 0.13275 | 0.054931 | 0.009156 | -0.045776 | 0.11444 | 122.1359 | 0.032044 | 122.3007 | 0.096131 | 122.3099 | -122.3099 | -122.3648 | 0.018311 | 122.1451 | -0.032043 | 0.45319
3180.0312 | 122.4976 | -0.091553 | 122.2321 | -0.089798 | -0.044312 | 0.0030184 | 0.024005 | 0.0029993 | -0.012239 | -0.0038687 | -0.09549 | 0.0065923 | 0.063423 | 0.051968 | -0.01666 | 0.027408 | -0.0066479 | -0.15106 | -0.013733 | -0.041199 | -0.018311 | 0.027466 | -0.036621 | 0.17853 | 0.56763 | 122.2137 | -0.082397 | 122.1817 | 0.10529 | 0.018311 | 0.18768 | 0.050354 | -122.2458 | -122.2504 | 0.11902 | 0.27008 | 0.054932 | 0.21973 | 0.004578 | 0.009156 | -0.018311 | -0.050354 | 0.19684 | 0.27924 | 0.10986 | 0.27008 | 0.10071 | 0.068665 | 0.022888 | 0.18768 | 122.2641 | 0.027466 | 122.2961 | 0.07782 | 122.3053 | -122.2733 | -122.3145 | 0.073242 | 122.2733 | -0.059509 | 0.65918
3181.7969 | 122.4518 | -0.10986 | 122.2687 | -0.1432 | -0.040894 | 0.003232 | 0.026568 | -0.0036231 | -0.0081796 | -0.0047231 | -0.10464 | 0.0076605 | 0.062354 | 0.0556 | -0.015379 | 0.028476 | -0.0021619 | -0.14648 | -0.018311 | -0.050354 | -0.068665 | -0.009155 | -0.13275 | 0.1236 | 0.3891 | 122.1909 | -0.091553 | 122.113 | 0.027466 | -0.036621 | 0.15564 | 0.059509 | -122.287 | -122.3373 | 0.10071 | 0.23346 | -0.022888 | 0.17395 | -0.082397 | 0.01831 | -0.07782 | -0.15564 | 0.13733 | 0.2655 | 0.073242 | 0.24719 | 0.054932 | 0.041199 | -0.018311 | 0.11902 | 122.2046 | 0.032043 | 122.2824 | 0.091552 | 122.3007 | -122.319 | -122.3602 | 0.041198 | 122.2229 | -0.036621 | 0.49896
3183.5 | 122.374 | -0.09613 | 122.2641 | -0.097427 | -0.044739 | 0.00045503 | 0.024432 | 0.00086307 | -0.010743 | -0.0023733 | -0.058869 | 0.0065923 | 0.067054 | 0.052823 | -0.01666 | 0.026767 | -0.0028027 | -0.13733 | -0.009155 | -0.054932 | -0.064087 | 0.009155 | -0.082397 | -0.004578 | 0.50354 | 122.1725 | -0.086975 | 122.0764 | 0.07782 | 0.018311 | 0.073242 | 0.041198 | -122.2733 | -122.3282 | 0.10528 | 0.091552 | 0.013733 | 0.050354 | -0.027465 | 0.009155 | -0.091553 | -0.18768 | 0.17395 | 0.16937 | 0.11444 | 0.16022 | 0.10529 | 0.064087 | -0.009155 | 0.16479 | 122.1634 | 0.045777 | 122.2595 | 0.086975 | 122.2687 | -122.319 | -122.3511 | 0.032043 | 122.1725 | -0.041199 | 0.59967
3185.2656 | 122.3419 | -0.091553 | 122.2687 | -0.12032 | -0.041962 | 0.0023776 | 0.024432 | 0.0021447 | -0.010957 | -0.0030141 | -0.089386 | 0.0046697 | 0.063423 | 0.047696 | -0.017729 | 0.029117 | -0.0051525 | -0.086975 | -0.041199 | -0.036621 | -0.018311 | 0.064087 | -0.073242 | 0 | 0.50812 | 122.1863 | -0.091553 | 122.0718 | 0.07782 | 0.018311 | 0.07782 | 0.054932 | -122.3099 | -122.287 | 0.15564 | 0.091553 | 0.018311 | 0.036621 | -0.036621 | 0 | -0.082398 | -0.19684 | 0.16937 | 0.16937 | 0.10986 | 0.16937 | 0.10986 | 0.10071 | 0.01831 | 0.16937 | 122.1634 | -0.004578 | 122.2778 | 0.050354 | 122.2778 | -122.3053 | -122.3602 | 0.073242 | 122.1634 | 0.004578 | 0.59967
3186.9688 | 122.3785 | -0.10071 | 122.2824 | -0.13557 | -0.044098 | 0.0023776 | 0.023578 | 8.47e-06 | -0.0073252 | -0.0045095 | -0.089386 | 0.0078741 | 0.062782 | 0.049191 | -0.01666 | 0.028049 | -0.0040845 | -0.086975 | -0.018311 | -0.059509 | -0.050354 | 0.050354 | -0.068665 | 0.009155 | 0.53558 | 122.1771 | -0.086975 | 122.0764 | 0.10071 | 0.045776 | 0.082397 | 0.041199 | -122.3007 | -122.3328 | 0.15106 | 0.10986 | 0.032043 | 0.068664 | -0.009156 | 0.013733 | -0.10529 | -0.20599 | 0.20142 | 0.18311 | 0.14648 | 0.16937 | 0.13275 | 0.10986 | 0.009155 | 0.18768 | 122.1634 | 0.041198 | 122.2641 | 0.082397 | 122.2778 | -122.3419 | -122.3694 | 0.050354 | 122.1771 | 0.013733 | 0.63629
3188.7188 | 122.3236 | -0.09613 | 122.2824 | -0.18898 | -0.043457 | 0.0036594 | 0.026141 | 0.00022207 | -0.0092478 | -0.0036551 | -0.089386 | 0.0061651 | 0.065345 | 0.056454 | -0.015165 | 0.02634 | -0.0042981 | -0.1236 | -0.022888 | -0.041199 | -0.10529 | -0.036621 | -0.15106 | -0.050354 | 0.35248 | 122.2046 | -0.091553 | 122.0261 | 0.004578 | -0.054932 | 0.032043 | 0.054931 | -122.3053 | -122.3877 | 0.059509 | 0.045776 | -0.054932 | -0.009155 | -0.10986 | 0.004577 | -0.07782 | -0.25635 | 0.10071 | 0.12817 | 0.041198 | 0.1236 | 0.036621 | 0.004578 | -0.064087 | 0.096131 | 122.1176 | 0.018311 | 122.2961 | 0.073242 | 122.3007 | -122.3236 | -122.374 | -0.009156 | 122.1222 | -0.027466 | 0.44861
3190.4688 | 122.4243 | -0.045776 | 122.2366 | -0.18135 | -0.043885 | 0.0051546 | 0.021441 | -0.0036231 | -0.0090342 | -0.0013051 | -0.019196 | 0.0048833 | 0.06385 | 0.0462 | -0.016447 | 0.02634 | -0.0042981 | -0.064087 | -0.054932 | 0.013733 | 0.032043 | 0.14191 | -0.009155 | 0.059509 | 0.50354 | 122.1085 | -0.054932 | 122.1176 | 0.14191 | 0.10529 | 0.14648 | 0.059509 | -122.2916 | -122.2046 | 0.18768 | 0.10528 | 0.036621 | 0.045776 | -0.022888 | -0.009156 | -0.12817 | -0.11902 | 0.18768 | 0.19226 | 0.15106 | 0.20142 | 0.16022 | 0.12817 | 0.01831 | 0.19684 | 122.1725 | -0.068665 | 122.1634 | -0.009156 | 122.1542 | -122.2229 | -122.2916 | 0.077819 | 122.1634 | -0.018311 | 0.54932
3192.1875 | 122.3511 | -0.11902 | 122.2778 | -0.11269 | -0.044953 | 0.0017368 | 0.024005 | -0.0049047 | -0.0088206 | -0.0013051 | -0.04361 | 0.0085149 | 0.065132 | 0.045773 | -0.017301 | 0.026981 | -0.0040845 | -0.13733 | -0.009155 | -0.045776 | -0.10529 | -0.018311 | -0.10071 | -0.027466 | 0.49896 | 122.2 | -0.10986 | 122.0306 | 0.054932 | -0.009155 | 0.041199 | 0.073243 | -122.287 | -122.3831 | 0.10071 | 0.091553 | 0.018311 | 0.01831 | -0.054932 | 0.009156 | -0.07782 | -0.24719 | 0.17395 | 0.16022 | 0.10986 | 0.15106 | 0.10071 | 0.027465 | -0.05951 | 0.16479 | 122.1405 | 0.036621 | 122.3099 | 0.10986 | 122.319 | -122.3236 | -122.3877 | 0.013733 | 122.1497 | -0.01831 | 0.61798
3193.9531 | 122.4792 | -0.059509 | 122.2412 | -0.15083 | -0.047516 | 0.001523 | 0.021228 | -0.0029821 | -0.012239 | -0.0060049 | 0.014374 | 0.0085149 | 0.062141 | 0.045346 | -0.01602 | 0.027408 | -0.0075025 | -0.059509 | -0.054932 | 0.004578 | 0.032043 | 0.18768 | 0.041199 | 0.10529 | 0.6546 | 122.1497 | -0.059509 | 122.168 | 0.21057 | 0.15106 | 0.16479 | 0.064087 | -122.2961 | -122.2092 | 0.24719 | 0.16479 | 0.10071 | 0.10071 | 0.036621 | 0 | -0.091553 | -0.073242 | 0.27008 | 0.2243 | 0.21057 | 0.2243 | 0.21057 | 0.1831 | 0.027465 | 0.27008 | 122.2275 | -0.05951 | 122.2092 | 0.004577 | 122.2092 | -122.2366 | -122.3007 | 0.091552 | 122.2275 | 0 | 0.71411
3195.7031 | 122.493 | -0.045776 | 122.2366 | -0.11269 | -0.045166 | 0.0010958 | 0.0208 | -0.0014867 | -0.008607 | -0.0060049 | 0.014374 | 0.0076605 | 0.064063 | 0.046414 | -0.01602 | 0.026981 | -0.0036573 | -0.064087 | -0.045776 | -0.018311 | 0.036621 | 0.15106 | 0.032043 | 0.11444 | 0.64545 | 122.1451 | -0.068665 | 122.1634 | 0.19684 | 0.16022 | 0.16022 | 0.027465 | -122.2824 | -122.2 | 0.19684 | 0.16022 | 0.077819 | 0.13275 | 0.050354 | -0.022889 | -0.091552 | -0.073242 | 0.24261 | 0.20599 | 0.20599 | 0.22888 | 0.22888 | 0.16937 | 0.054932 | 0.2655 | 122.2321 | -0.027465 | 122.2137 | 0 | 122.1909 | -122.2549 | -122.3053 | 0.082397 | 122.2092 | -0.018311 | 0.69122
3197.4688 | 122.3419 | -0.10986 | 122.2778 | -0.1432 | -0.042816 | 0.00045503 | 0.02315 | 0.0019311 | -0.01053 | -0.0036551 | -0.034454 | 0.0065923 | 0.065559 | 0.041714 | -0.016447 | 0.027621 | -0.0068615 | -0.14648 | -0.032043 | -0.041199 | -0.073242 | 0.013733 | -0.086975 | -0.004578 | 0.5127 | 122.1817 | -0.086975 | 122.0169 | 0.041199 | -0.018311 | 0.018311 | 0.068664 | -122.3099 | -122.3511 | 0.1236 | 0.10529 | 0.022888 | 0.036621 | -0.045776 | 0.022888 | -0.09613 | -0.26093 | 0.15106 | 0.12817 | 0.091552 | 0.10529 | 0.068664 | 0.054932 | -0.032043 | 0.12817 | 122.1039 | 0.009156 | 122.2687 | 0.07782 | 122.2916 | -122.319 | -122.3648 | 0.036621 | 122.1268 | -0.036621 | 0.62256
3199.2344 | 122.3694 | -0.086975 | 122.2549 | -0.12032 | -0.043244 | 0.0036594 | 0.024005 | 0.0019311 | -0.012239 | -0.0045095 | -0.083283 | 0.0072333 | 0.063423 | 0.046628 | -0.017729 | 0.025912 | -0.0087841 | -0.10529 | 0 | -0.032043 | -0.041199 | 0.022888 | -0.073242 | -0.004578 | 0.54016 | 122.1817 | -0.091553 | 122.0856 | 0.091553 | 0.032043 | 0.068665 | 0.054932 | -122.2549 | -122.2961 | 0.10986 | 0.082397 | 0.013733 | 0.027465 | -0.041199 | -0.004578 | -0.073242 | -0.16937 | 0.17853 | 0.15564 | 0.11902 | 0.16022 | 0.1236 | 0.054931 | -0.009156 | 0.18311 | 122.1771 | 0.032043 | 122.2733 | 0.086975 | 122.2687 | -122.287 | -122.3465 | 0.045776 | 122.1725 | -0.018311 | 0.62714
3200.9375 | 122.3145 | -0.09613 | 122.2916 | -0.1432 | -0.040253 | 0.002164 | 0.025287 | -0.0010595 | -0.01117 | -0.0049367 | -0.1138 | 0.0061651 | 0.065345 | 0.054532 | -0.01666 | 0.027621 | -0.0079297 | -0.09613 | -0.018311 | -0.041199 | -0.073242 | 0 | -0.14648 | -0.050354 | 0.40283 | 122.2046 | -0.086975 | 122.0352 | 0.004578 | -0.054932 | 0.036621 | 0.054931 | -122.3099 | -122.3648 | 0.09613 | 0.045776 | -0.050354 | -0.009155 | -0.10529 | 0.009155 | -0.086975 | -0.25635 | 0.10071 | 0.13275 | 0.041198 | 0.1236 | 0.032043 | 0.041199 | -0.032043 | 0.091553 | 122.1222 | 0.022888 | 122.2916 | 0.077819 | 122.3007 | -122.3328 | -122.3785 | 0.022888 | 122.1313 | 0 | 0.49896
3202.6406 | 122.3831 | -0.091553 | 122.2595 | -0.19661 | -0.045594 | 0.0034456 | 0.024432 | -0.0012731 | -0.010316 | -0.00045074 | -0.071076 | 0.0068059 | 0.061927 | 0.050259 | -0.016233 | 0.027621 | -0.0038709 | -0.10071 | -0.018311 | -0.027466 | -0.041199 | 0.041199 | -0.059509 | 0.018311 | 0.54016 | 122.1909 | -0.091553 | 122.0901 | 0.10529 | 0.041199 | 0.091553 | 0.064087 | -122.2778 | -122.3007 | 0.13275 | 0.10986 | 0.032044 | 0.045777 | -0.032043 | 0 | -0.068664 | -0.16937 | 0.19684 | 0.18311 | 0.13275 | 0.18311 | 0.13275 | 0.068665 | -0.013733 | 0.19684 | 122.1817 | 0.009155 | 122.2824 | 0.073242 | 122.2824 | -122.287 | -122.3511 | 0.050354 | 122.1817 | -0.009155 | 0.63171
3204.3906 | 122.3465 | -0.10529 | 122.2412 | -0.097427 | -0.041748 | 0.0028048 | 0.025927 | 8.47e-06 | -0.0083932 | -0.0017325 | -0.092438 | 0.0076605 | 0.065132 | 0.047909 | -0.014951 | 0.029117 | -0.0015209 | -0.11902 | -0.022888 | -0.036621 | -0.10071 | -0.027466 | -0.15106 | -0.059509 | 0.33417 | 122.1863 | -0.091553 | 122.0444 | 0.027466 | -0.036621 | 0.032043 | 0.068665 | -122.2641 | -122.3419 | 0.07782 | 0.045777 | -0.045776 | -0.022888 | -0.11444 | 0.013733 | -0.054932 | -0.19684 | 0.13275 | 0.13733 | 0.068665 | 0.1236 | 0.054932 | 0.009155 | -0.064087 | 0.11902 | 122.1359 | 0.013733 | 122.2778 | 0.082398 | 122.2916 | -122.2778 | -122.3328 | 0.004578 | 122.1497 | -0.013733 | 0.43945
3206.1562 | 122.3465 | -0.10529 | 122.2687 | -0.15083 | -0.044098 | 0.0047274 | 0.027209 | 0.0062037 | -0.0098886 | -0.0028005 | -0.098541 | 0.0083013 | 0.063209 | 0.051968 | -0.015379 | 0.026767 | -0.0060071 | -0.13733 | -0.022888 | -0.045776 | -0.10529 | -0.032043 | -0.15564 | -0.041199 | 0.35248 | 122.1954 | -0.091553 | 122.0352 | 0.018311 | -0.045776 | 0.032043 | 0.05951 | -122.2916 | -122.374 | 0.073243 | 0.064087 | -0.050354 | 0.004577 | -0.10986 | 0.013733 | -0.073242 | -0.23346 | 0.1236 | 0.13733 | 0.05951 | 0.1236 | 0.045777 | 0.013733 | -0.05951 | 0.10986 | 122.1268 | 0.022888 | 122.287 | 0.082398 | 122.3007 | -122.3145 | -122.3602 | 0 | 122.1405 | -0.032043 | 0.45776
3207.8594 | 122.4701 | -0.068665 | 122.2366 | -0.074539 | -0.045807 | 0.002164 | 0.020373 | -0.0053321 | -0.0098886 | -0.0062185 | 0.029632 | 0.0040289 | 0.062782 | 0.047696 | -0.018797 | 0.02634 | 0.00018809 | -0.07782 | -0.050354 | -0.013733 | 0.045776 | 0.16479 | 0.032043 | 0.091553 | 0.66834 | 122.1542 | -0.064087 | 122.1451 | 0.19226 | 0.13733 | 0.14648 | 0.054932 | -122.287 | -122.1909 | 0.23346 | 0.16022 | 0.10071 | 0.10529 | 0.045776 | 0.004578 | -0.082397 | -0.091552 | 0.26093 | 0.21515 | 0.20599 | 0.21057 | 0.20142 | 0.17853 | 0.059509 | 0.25635 | 122.2092 | -0.036621 | 122.2183 | 0.018311 | 122.2229 | -122.2504 | -122.3007 | 0.11444 | 122.2137 | -0.009155 | 0.737
3209.625 | 122.4747 | -0.068665 | 122.2137 | -0.12032 | -0.048157 | 0.002164 | 0.020587 | -0.0014867 | -0.0092478 | -0.0034415 | 0.0082703 | 0.0068059 | 0.06385 | 0.04086 | -0.018369 | 0.025058 | -0.0068615 | -0.073242 | -0.050354 | -0.018311 | 0.032043 | 0.13733 | 0.022888 | 0.09613 | 0.63629 | 122.1359 | -0.050354 | 122.1451 | 0.20142 | 0.14191 | 0.16479 | 0.050354 | -122.2641 | -122.1817 | 0.20599 | 0.16479 | 0.091553 | 0.11444 | 0.041199 | 0.018311 | -0.07782 | -0.068664 | 0.27008 | 0.23346 | 0.21057 | 0.21515 | 0.19226 | 0.15564 | 0.050354 | 0.25177 | 122.1954 | -0.032043 | 122.1863 | 0.018311 | 122.2046 | -122.2321 | -122.2641 | 0.10071 | 122.2137 | -0.004577 | 0.70496
3211.3906 | 122.4518 | -0.054932 | 122.2229 | -0.20424 | -0.040894 | 0.0030184 | 0.0255 | 0.0038537 | -0.01053 | -0.0038687 | -0.049713 | 0.0042425 | 0.063209 | 0.050046 | -0.017088 | 0.026981 | -0.0094251 | -0.07782 | -0.032043 | -0.032043 | 0.018311 | 0.10529 | -0.041199 | 0.045776 | 0.46692 | 122.1451 | -0.07782 | 122.1771 | 0.14191 | 0.10071 | 0.1831 | 0.022889 | -122.2549 | -122.2046 | 0.16022 | 0.10071 | 0.013733 | 0.077819 | -0.009156 | -0.022888 | -0.077819 | -0.045776 | 0.19684 | 0.23804 | 0.15564 | 0.26092 | 0.17853 | 0.13733 | 0.050354 | 0.21973 | 122.2549 | 0 | 122.2229 | 0.022889 | 122.2 | -122.2549 | -122.3007 | 0.073243 | 122.2321 | -0.022888 | 0.52185
3213.0938 | 122.3236 | -0.09613 | 122.2321 | -0.12794 | -0.044525 | 0.0019504 | 0.023578 | 0.00064947 | -0.0094614 | -0.0028005 | -0.031403 | 0.0063787 | 0.064491 | 0.045773 | -0.01666 | 0.025912 | -0.0049389 | -0.14648 | -0.009155 | -0.050354 | -0.086975 | 0.004578 | -0.10071 | 0.004578 | 0.50354 | 122.1817 | -0.10071 | 122.0306 | 0.054932 | -0.009155 | 0.022888 | 0.045776 | -122.2412 | -122.319 | 0.10071 | 0.10071 | -0.004578 | 0.054932 | -0.050354 | -0.004578 | -0.050354 | -0.20142 | 0.15106 | 0.11902 | 0.086975 | 0.1236 | 0.091553 | 0.054932 | -0.036621 | 0.15564 | 122.1313 | 0.041199 | 122.2824 | 0.086975 | 122.2778 | -122.2824 | -122.3328 | 0.009155 | 122.1268 | -0.050354 | 0.59967
3214.8594 | 122.3511 | -0.10529 | 122.2733 | -0.097427 | -0.04303 | 0.0025912 | 0.024005 | -0.0010595 | -0.011384 | -0.0030141 | -0.071076 | 0.0065923 | 0.064491 | 0.049405 | -0.01602 | 0.027194 | -0.0032299 | -0.16022 | -0.013733 | -0.041199 | -0.082397 | -0.013733 | -0.10529 | -0.009155 | 0.50354 | 122.2229 | -0.10529 | 122.0261 | 0.045776 | -0.004578 | 0.022888 | 0.064087 | -122.287 | -122.3557 | 0.091553 | 0.096131 | 0 | 0.032044 | -0.064087 | 0 | -0.050354 | -0.24719 | 0.15106 | 0.12817 | 0.10071 | 0.12817 | 0.10071 | 0.027466 | -0.041198 | 0.15106 | 122.1313 | 0.027466 | 122.3282 | 0.091553 | 122.3282 | -122.3145 | -122.3785 | 0.022889 | 122.1313 | -0.054931 | 0.60883
3216.6406 | 122.3282 | -0.10986 | 122.2641 | -0.12794 | -0.044739 | 0.00024143 | 0.023791 | -0.0012731 | -0.012666 | -0.0036551 | -0.034454 | 0.0048833 | 0.064063 | 0.044064 | -0.01901 | 0.027835 | -0.0081433 | -0.14191 | -0.009155 | -0.027466 | -0.091553 | 0.004578 | -0.091553 | -0.009155 | 0.5127 | 122.1817 | -0.11444 | 122.0123 | 0.036621 | -0.009155 | 0.018311 | 0.082397 | -122.2733 | -122.3557 | 0.11444 | 0.10071 | 0.01831 | 0.018311 | -0.064087 | -0.004578 | -0.082397 | -0.25177 | 0.14648 | 0.12817 | 0.10071 | 0.13275 | 0.10529 | 0.032044 | -0.064087 | 0.15106 | 122.1268 | 0.018311 | 122.2961 | 0.10071 | 122.2916 | -122.2916 | -122.3785 | 0.01831 | 122.1222 | -0.032044 | 0.62256
3218.4062 | 122.3282 | -0.10986 | 122.2778 | -0.18898 | -0.042176 | 0.0047274 | 0.025714 | -0.00041873 | -0.010316 | -0.0049367 | -0.1138 | 0.0063787 | 0.064491 | 0.047909 | -0.017515 | 0.02869 | -0.0060071 | -0.14648 | -0.009155 | -0.064087 | -0.11902 | -0.059509 | -0.17395 | -0.059509 | 0.3479 | 122.2092 | -0.086975 | 122.0352 | 0.013733 | -0.045776 | 0.041199 | 0.045776 | -122.287 | -122.3969 | 0.050354 | 0.050354 | -0.064087 | 0.004578 | -0.10986 | 0.022888 | -0.068665 | -0.24262 | 0.1236 | 0.15106 | 0.064087 | 0.12817 | 0.041199 | 0.004578 | -0.054932 | 0.10071 | 122.1222 | 0.054932 | 122.2961 | 0.10071 | 122.319 | -122.3419 | -122.3648 | -0.009156 | 122.1451 | -0.036621 | 0.45776
3220.1562 | 122.3328 | -0.082397 | 122.2733 | -0.1432 | -0.042603 | 0.0030184 | 0.024432 | 0.0017175 | -0.011384 | -0.0038687 | -0.10159 | 0.0089423 | 0.063636 | 0.054532 | -0.017515 | 0.027194 | -0.0032299 | -0.1236 | -0.022888 | -0.064087 | -0.11444 | -0.032043 | -0.17395 | -0.045776 | 0.35248 | 122.2046 | -0.10529 | 122.0444 | 0.027466 | -0.041199 | 0.032043 | 0.01831 | -122.2961 | -122.3877 | 0.050354 | 0.036621 | -0.091553 | 0.018311 | -0.10986 | -0.022889 | -0.068664 | -0.22888 | 0.10986 | 0.11444 | 0.041198 | 0.13733 | 0.064087 | 0.032044 | -0.050354 | 0.13275 | 122.1497 | 0.041199 | 122.3099 | 0.059509 | 122.287 | -122.3373 | -122.3785 | -0.032044 | 122.1268 | -0.041199 | 0.43488
3221.8594 | 122.3602 | -0.091553 | 122.2595 | -0.097427 | -0.042389 | 0.0047274 | 0.024432 | 0.00043587 | -0.012452 | -0.0034415 | -0.077179 | 0.0068059 | 0.063423 | 0.044705 | -0.017729 | 0.028903 | -0.0034435 | -0.11444 | -0.022888 | -0.045776 | -0.064087 | 0.013733 | -0.07782 | -0.004578 | 0.54016 | 122.1954 | -0.10529 | 122.0764 | 0.10529 | 0.022888 | 0.07782 | 0.045777 | -122.2824 | -122.3236 | 0.10529 | 0.086975 | 0.013733 | 0.041198 | -0.032044 | -0.013733 | -0.064086 | -0.18311 | 0.19684 | 0.16937 | 0.11444 | 0.18311 | 0.12817 | 0.059509 | -0.018311 | 0.21057 | 122.1817 | 0.022888 | 122.3007 | 0.068665 | 122.287 | -122.3053 | -122.3648 | 0.027466 | 122.168 | -0.022888 | 0.63171
3223.625 | 122.3419 | -0.10529 | 122.2961 | -0.13557 | -0.043244 | 0.002164 | 0.02315 | -0.0021277 | -0.0083932 | -0.0047231 | -0.052765 | 0.0055243 | 0.063636 | 0.043423 | -0.016447 | 0.027621 | -0.0040845 | -0.14191 | -0.013733 | -0.045776 | -0.10071 | -0.004578 | -0.091553 | -0.013733 | 0.50354 | 122.1954 | -0.10986 | 122.0352 | 0.050354 | -0.013733 | 0.027466 | 0.05951 | -122.3099 | -122.3969 | 0.10071 | 0.091553 | 0.013733 | 0.032043 | -0.045777 | -0.004577 | -0.10071 | -0.26093 | 0.15564 | 0.13275 | 0.091553 | 0.13733 | 0.09613 | 0.041198 | -0.054932 | 0.16022 | 122.1451 | 0.032043 | 122.3053 | 0.091553 | 122.3007 | -122.3419 | -122.406 | 0.004578 | 122.1405 | -0.036621 | 0.60883
3225.3281 | 122.4197 | -0.064087 | 122.2504 | -0.10506 | -0.043671 | 0.0036594 | 0.0255 | 8.47e-06 | -0.010102 | -0.0042959 | -0.064972 | 0.0063787 | 0.065132 | 0.047696 | -0.016447 | 0.027835 | -0.0057935 | -0.10986 | -0.018311 | -0.032043 | -0.073242 | 0.022888 | -0.13275 | -0.013733 | 0.39825 | 122.1542 | -0.073242 | 122.0993 | 0.10986 | 0.036621 | 0.10986 | 0.032044 | -122.2687 | -122.3236 | 0.086975 | 0.050354 | -0.068664 | 0.01831 | -0.10071 | -0.009155 | -0.09613 | -0.15106 | 0.17395 | 0.17395 | 0.10071 | 0.18311 | 0.10986 | 0.054931 | -0.041199 | 0.18311 | 122.1725 | 0.013732 | 122.2275 | 0.045776 | 122.2183 | -122.2824 | -122.3236 | -0.009155 | 122.1634 | -0.045776 | 0.46234
3227.0938 | 122.4609 | -0.050354 | 122.2412 | -0.18898 | -0.047303 | -0.0010404 | 0.022723 | -0.0036231 | -0.010743 | -0.0034415 | 0.017425 | 0.0050971 | 0.064277 | 0.043637 | -0.017301 | 0.025272 | -0.0066479 | -0.10529 | -0.036621 | -0.013733 | -0.013733 | 0.10071 | -0.013733 | 0.082397 | 0.55847 | 122.1771 | -0.054932 | 122.1359 | 0.1831 | 0.14191 | 0.15106 | 0.036621 | -122.2778 | -122.2549 | 0.15106 | 0.13275 | 0.036621 | 0.09613 | 0 | -0.004578 | -0.064087 | -0.10529 | 0.23346 | 0.20142 | 0.19226 | 0.20599 | 0.19684 | 0.11444 | 0 | 0.23804 | 122.1909 | -0.022888 | 122.2321 | 0.013733 | 122.2275 | -122.2549 | -122.2961 | 0.036621 | 122.1863 | -0.054932 | 0.60883
3228.7812 | 122.3145 | -0.10529 | 122.2778 | -0.17372 | -0.039826 | 0.0023776 | 0.026996 | 0.0025721 | -0.01117 | -0.0028005 | -0.083283 | 0.0065923 | 0.064491 | 0.045559 | -0.01666 | 0.028049 | -0.0053661 | -0.11902 | -0.013733 | -0.041199 | -0.10529 | -0.036621 | -0.15106 | -0.054932 | 0.36621 | 122.1909 | -0.082397 | 122.0169 | -0.013733 | -0.068665 | 0.022888 | 0.064087 | -122.2916 | -122.3831 | 0.068665 | 0.050354 | -0.045776 | -0.013733 | -0.10986 | 0.022889 | -0.086975 | -0.26093 | 0.091553 | 0.12817 | 0.036621 | 0.10528 | 0.013732 | 0.004578 | -0.064087 | 0.068664 | 122.0993 | 0.027466 | 122.2733 | 0.091553 | 122.2961 | -122.319 | -122.3602 | 0 | 122.1222 | -0.013733 | 0.4715
3230.5312 | 122.3282 | -0.10071 | 122.2778 | -0.12032 | -0.043885 | 0.0017368 | 0.026141 | -0.00041873 | -0.01117 | -0.0030141 | -0.10464 | 0.0070197 | 0.062568 | 0.04855 | -0.01602 | 0.027835 | -0.0049389 | -0.11444 | -0.022888 | -0.041199 | -0.068665 | 0.018311 | -0.13275 | -0.032043 | 0.41657 | 122.1909 | -0.086975 | 122.0444 | 0.045776 | -0.050354 | 0.036621 | 0.059509 | -122.3007 | -122.3465 | 0.11902 | 0.068665 | -0.032043 | 0.009156 | -0.091552 | 0.013733 | -0.086975 | -0.23346 | 0.14648 | 0.13733 | 0.050354 | 0.1236 | 0.036621 | 0.05951 | -0.027466 | 0.13275 | 122.1313 | 0.018311 | 122.2778 | 0.07782 | 122.2916 | -122.319 | -122.3648 | 0.032043 | 122.1451 | -0.013733 | 0.51727
3232.2812 | 122.3557 | -0.091553 | 122.2412 | -0.17372 | -0.041107 | 0.0023776 | 0.024859 | 0.00043587 | -0.010743 | -0.0036551 | -0.089386 | 0.0078741 | 0.063636 | 0.051541 | -0.017729 | 0.027835 | -0.0023755 | -0.13733 | -0.009155 | -0.054932 | -0.09613 | -0.004578 | -0.12817 | -0.036621 | 0.37537 | 122.168 | -0.10071 | 122.081 | 0.059509 | 0 | 0.07782 | 0.036621 | -122.2504 | -122.3373 | 0.086975 | 0.054932 | -0.036621 | 0.018311 | -0.073242 | -0.009155 | -0.073242 | -0.16022 | 0.15106 | 0.16937 | 0.091553 | 0.17853 | 0.10071 | 0.050354 | -0.041198 | 0.16022 | 122.1817 | 0.045777 | 122.2687 | 0.082398 | 122.2595 | -122.2961 | -122.3419 | -0.004577 | 122.1725 | -0.045776 | 0.46692
3234.0469 | 122.3282 | -0.11444 | 122.2641 | -0.082169 | -0.046234 | 0.0017368 | 0.025287 | -0.0031957 | -0.01117 | -0.0025869 | -0.049713 | 0.0070197 | 0.065345 | 0.04385 | -0.015379 | 0.027194 | -0.0066479 | -0.14648 | -0.009155 | -0.073242 | -0.10986 | -0.009155 | -0.10986 | -0.022888 | 0.51727 | 122.1909 | -0.09613 | 122.0215 | 0.036621 | -0.004578 | 0.013733 | 0.041199 | -122.2733 | -122.374 | 0.10529 | 0.091553 | 0.004578 | 0.050354 | -0.036621 | 0.018311 | -0.073242 | -0.24262 | 0.15106 | 0.12817 | 0.10986 | 0.10986 | 0.091552 | 0.064087 | -0.036621 | 0.13275 | 122.1176 | 0.064087 | 122.287 | 0.10529 | 122.3053 | -122.3373 | -122.3602 | 0.004578 | 122.1359 | -0.032043 | 0.63171
3235.7344 | 122.4518 | -0.07782 | 122.2275 | -0.17372 | -0.045166 | 0.0025912 | 0.021014 | -0.0019141 | -0.011811 | -0.0036551 | 0.0052185 | 0.0068059 | 0.062354 | 0.043423 | -0.016447 | 0.026553 | -0.0049389 | -0.1236 | -0.036621 | -0.018311 | -0.009155 | 0.073242 | -0.036621 | 0.064087 | 0.5127 | 122.1634 | -0.073242 | 122.1222 | 0.14191 | 0.13733 | 0.14648 | 0.059509 | -122.2641 | -122.2366 | 0.15106 | 0.14191 | 0.041199 | 0.082398 | -0.01831 | 0.004578 | -0.064087 | -0.10529 | 0.21973 | 0.2243 | 0.21515 | 0.21973 | 0.21057 | 0.091553 | 0.009156 | 0.21515 | 122.1954 | -0.01831 | 122.2366 | 0.041199 | 122.2412 | -122.2458 | -122.3007 | 0.068665 | 122.2 | -0.045776 | 0.59052
3237.5 | 122.3282 | -0.10529 | 122.2733 | -0.15846 | -0.041962 | 0.0028048 | 0.025927 | 0.0019311 | -0.011811 | -0.0047231 | -0.06192 | 0.0059515 | 0.064918 | 0.048123 | -0.019224 | 0.029117 | -0.0025891 | -0.14648 | -0.018311 | -0.059509 | -0.091553 | 0.004578 | -0.10071 | -0.022888 | 0.50812 | 122.1954 | -0.10529 | 122.0032 | 0.041199 | -0.013733 | 0.027466 | 0.045777 | -122.2916 | -122.3648 | 0.10986 | 0.082398 | 0.004578 | 0.036621 | -0.041199 | 0 | -0.077819 | -0.27008 | 0.14649 | 0.13275 | 0.091553 | 0.13275 | 0.091553 | 0.064087 | -0.032044 | 0.14649 | 122.1085 | 0.041198 | 122.3007 | 0.086975 | 122.3007 | -122.3328 | -122.3785 | 0.013733 | 122.1085 | -0.041198 | 0.6134
3239.2656 | 122.3923 | -0.082397 | 122.2595 | -0.074539 | -0.042603 | 0.0017368 | 0.022082 | 8.47e-06 | -0.011384 | -0.0023733 | -0.022247 | 0.0031745 | 0.062995 | 0.041714 | -0.017301 | 0.027408 | -0.0062207 | -0.064087 | -0.050354 | -0.018311 | 0.004578 | 0.10986 | -0.004578 | 0.059509 | 0.61798 | 122.1542 | -0.086975 | 122.0764 | 0.10529 | 0.068665 | 0.07782 | 0.064086 | -122.3099 | -122.2549 | 0.19226 | 0.14191 | 0.077819 | 0.07782 | 0.013733 | -0.004578 | -0.10529 | -0.18311 | 0.18768 | 0.16022 | 0.15106 | 0.16479 | 0.15564 | 0.12817 | 0.022889 | 0.19226 | 122.1634 | -0.032043 | 122.2412 | 0.032043 | 122.2366 | -122.2778 | -122.3465 | 0.086975 | 122.1588 | 0.01831 | 0.70038
3241.0312 | 122.4838 | -0.050354 | 122.2275 | -0.089798 | -0.046662 | 0.001523 | 0.022082 | -0.00084593 | -0.0094614 | -0.0075003 | -0.0069885 | 0.0050971 | 0.064704 | 0.047055 | -0.016447 | 0.026981 | -0.0040845 | -0.07782 | -0.059509 | -0.013733 | 0.027466 | 0.14648 | 0.013733 | 0.09613 | 0.62714 | 122.1588 | -0.068665 | 122.1634 | 0.1831 | 0.15564 | 0.16022 | 0.036621 | -122.287 | -122.2 | 0.19684 | 0.14648 | 0.064087 | 0.10986 | 0.027466 | -0.018311 | -0.068665 | -0.064087 | 0.23346 | 0.21057 | 0.20599 | 0.22888 | 0.22431 | 0.16022 | 0.041199 | 0.25177 | 122.2321 | -0.045776 | 122.2275 | -0.009155 | 122.2092 | -122.2412 | -122.2961 | 0.07782 | 122.2137 | -0.027466 | 0.67749
3242.7969 | 122.4701 | -0.032043 | 122.2458 | -0.16609 | -0.041321 | 0.0019504 | 0.024859 | -0.0029821 | -0.010102 | -0.0049367 | -0.071076 | 0.0055243 | 0.061714 | 0.050473 | -0.017301 | 0.027408 | -0.0028027 | -0.054932 | -0.050354 | -0.004578 | 0.041199 | 0.12817 | -0.027466 | 0.07782 | 0.49896 | 122.1405 | -0.073242 | 122.1725 | 0.16937 | 0.10529 | 0.15564 | 0.027465 | -122.2961 | -122.2046 | 0.16022 | 0.10986 | 0.004577 | 0.082398 | -0.022888 | -0.041199 | -0.10529 | -0.073243 | 0.20142 | 0.18768 | 0.13733 | 0.22888 | 0.17853 | 0.13275 | 0.045777 | 0.24261 | 122.2458 | -0.045776 | 122.2137 | -0.018311 | 122.1725 | -122.2504 | -122.319 | 0.073242 | 122.2046 | -0.022889 | 0.53101
3244.5 | 122.3923 | -0.073242 | 122.2549 | -0.12032 | -0.046662 | 0.0017368 | 0.021228 | -0.0021277 | -0.01117 | -0.00045074 | -0.0069885 | 0.0059515 | 0.062568 | 0.049191 | -0.019865 | 0.026553 | -0.0070751 | -0.07782 | -0.041199 | -0.009155 | 0.018311 | 0.13275 | -0.009155 | 0.068665 | 0.63171 | 122.1725 | -0.068665 | 122.0901 | 0.13275 | 0.086975 | 0.09613 | 0.064087 | -122.2961 | -122.2366 | 0.20599 | 0.14191 | 0.064087 | 0.07782 | 0 | 0.004577 | -0.082398 | -0.16479 | 0.20599 | 0.16937 | 0.16022 | 0.16479 | 0.15564 | 0.14191 | 0.027466 | 0.20142 | 122.1588 | -0.032044 | 122.2412 | 0.032043 | 122.2458 | -122.2641 | -122.3236 | 0.091553 | 122.1634 | -0.004578 | 0.70496
3246.2656 | 122.3419 | -0.09613 | 122.2824 | -0.089798 | -0.046875 | 0.002164 | 0.026355 | 0.0021447 | -0.012025 | -0.0036551 | -0.089386 | 0.0068059 | 0.062782 | 0.056027 | -0.01602 | 0.028049 | -0.0070751 | -0.15106 | -0.027466 | -0.059509 | -0.09613 | -0.009155 | -0.10071 | -0.032043 | 0.51727 | 122.1909 | -0.10986 | 122.0352 | 0.032043 | -0.013733 | 0.032043 | 0.036621 | -122.3099 | -122.3785 | 0.086975 | 0.064087 | -0.004578 | 0.027466 | -0.041199 | -0.013733 | -0.091553 | -0.24719 | 0.12817 | 0.12817 | 0.082397 | 0.14191 | 0.09613 | 0.050354 | -0.036621 | 0.14191 | 122.1451 | 0.032043 | 122.3007 | 0.068664 | 122.287 | -122.3419 | -122.3923 | 0 | 122.1313 | -0.054932 | 0.6134
3248.0312 | 122.3282 | -0.07782 | 122.2778 | -0.18135 | -0.044739 | 0.00045503 | 0.026996 | -0.0014867 | -0.0092478 | -0.0030141 | -0.10159 | 0.0055243 | 0.06385 | 0.053464 | -0.016874 | 0.028903 | -0.0075025 | -0.13275 | -0.032043 | -0.050354 | -0.09613 | -0.027466 | -0.15564 | -0.059509 | 0.3479 | 122.1909 | -0.10529 | 122.049 | 0.018311 | -0.036621 | 0.036621 | 0.027466 | -122.3099 | -122.374 | 0.050354 | 0.018311 | -0.07782 | -0.009155 | -0.10529 | -0.027466 | -0.086975 | -0.22888 | 0.096131 | 0.11444 | 0.041199 | 0.14191 | 0.068665 | 0.022888 | -0.045776 | 0.1236 | 122.1542 | 0.018311 | 122.2961 | 0.045777 | 122.2687 | -122.3282 | -122.3831 | -0.01831 | 122.1268 | -0.054931 | 0.42572
3249.7344 | 122.3785 | -0.086975 | 122.2504 | -0.15846 | -0.041321 | 0.0010958 | 0.025714 | -0.0046911 | -0.007966 | -0.0034415 | -0.077179 | 0.0076605 | 0.064704 | 0.043637 | -0.017515 | 0.027621 | -0.0053661 | -0.10986 | -0.013733 | -0.036621 | -0.036621 | 0.032043 | -0.064087 | 0.004578 | 0.53558 | 122.1588 | -0.082397 | 122.081 | 0.10986 | 0.032043 | 0.082397 | 0.050354 | -122.2641 | -122.287 | 0.11902 | 0.091553 | 0.022888 | 0.041199 | -0.027466 | 0.004578 | -0.091553 | -0.16937 | 0.19684 | 0.16937 | 0.11902 | 0.16479 | 0.11444 | 0.068664 | 0 | 0.19226 | 122.1634 | 0.022888 | 122.2412 | 0.073242 | 122.2458 | -122.287 | -122.3328 | 0.050354 | 122.168 | -0.022888 | 0.62256
3251.4844 | 122.4152 | -0.086975 | 122.2549 | -0.1432 | -0.043244 | 0.0030184 | 0.022082 | -0.00063233 | -0.011811 | -0.0038687 | 0.0021667 | 0.0038153 | 0.06385 | 0.049191 | -0.016874 | 0.025272 | -0.0055799 | -0.073242 | -0.041199 | -0.022888 | 0.004578 | 0.13733 | -0.004578 | 0.07782 | 0.62714 | 122.1725 | -0.082397 | 122.081 | 0.13733 | 0.073242 | 0.10071 | 0.064087 | -122.2961 | -122.2504 | 0.2243 | 0.16479 | 0.082397 | 0.10071 | 0.01831 | 0.004578 | -0.082398 | -0.17395 | 0.2243 | 0.18768 | 0.16022 | 0.18311 | 0.15564 | 0.16022 | 0.027466 | 0.21973 | 122.1634 | -0.018311 | 122.2549 | 0.045776 | 122.2595 | -122.2778 | -122.3373 | 0.091553 | 122.168 | 0.013733 | 0.71411
3253.2344 | 122.3602 | -0.091553 | 122.2412 | -0.05928 | -0.043885 | 0.0028048 | 0.025073 | 0.0021447 | -0.011598 | -0.0034415 | -0.068024 | 0.0068059 | 0.063636 | 0.0462 | -0.017088 | 0.025912 | -0.0053661 | -0.15106 | -0.013733 | -0.07782 | -0.09613 | -0.009155 | -0.10071 | -0.027466 | 0.50812 | 122.2092 | -0.09613 | 122.049 | 0.054932 | -0.004578 | 0.041199 | 0.013733 | -122.2549 | -122.3373 | 0.082398 | 0.064087 | -0.009155 | 0.050354 | -0.022888 | -0.004577 | -0.032044 | -0.19226 | 0.14649 | 0.13275 | 0.086975 | 0.13733 | 0.091552 | 0.068665 | -0.01831 | 0.15106 | 122.1451 | 0.064087 | 122.3053 | 0.07782 | 122.3007 | -122.319 | -122.3373 | -0.004577 | 122.1405 | -0.059509 | 0.59967
3255 | 122.3465 | -0.10986 | 122.2824 | -0.1432 | -0.044098 | 0.0013094 | 0.027423 | 0.0032129 | -0.008607 | -0.0047231 | -0.10159 | 0.0070197 | 0.062995 | 0.051327 | -0.017729 | 0.027194 | -0.0045117 | -0.12817 | -0.013733 | -0.045776 | -0.11444 | -0.036621 | -0.16479 | -0.054932 | 0.36621 | 122.1909 | -0.10071 | 122.049 | 0.022888 | -0.032043 | 0.032043 | 0.064087 | -122.2961 | -122.3969 | 0.073242 | 0.054931 | -0.054932 | -0.009156 | -0.11902 | 0.009155 | -0.091553 | -0.23346 | 0.13275 | 0.14191 | 0.07782 | 0.13275 | 0.068665 | 0.009155 | -0.068665 | 0.1236 | 122.1497 | 0.032043 | 122.2916 | 0.09613 | 122.3007 | -122.3282 | -122.3831 | -0.004578 | 122.1588 | -0.018311 | 0.47607
3256.7031 | 122.3419 | -0.10071 | 122.2733 | -0.12032 | -0.043457 | 0.0013094 | 0.022723 | -0.00063233 | -0.010743 | -0.0045095 | -0.049713 | 0.0068059 | 0.064063 | 0.037442 | -0.015379 | 0.02634 | -0.0062207 | -0.15564 | -0.004578 | -0.068665 | -0.09613 | -0.013733 | -0.10071 | -0.018311 | 0.51727 | 122.1771 | -0.10986 | 122.0215 | 0.050354 | -0.004578 | 0.032043 | 0.032043 | -122.2778 | -122.3694 | 0.086975 | 0.082397 | 0 | 0.050354 | -0.032043 | -0.009155 | -0.09613 | -0.25177 | 0.15106 | 0.13275 | 0.09613 | 0.14191 | 0.10529 | 0.054932 | -0.027465 | 0.16022 | 122.1313 | 0.064087 | 122.287 | 0.09613 | 122.2778 | -122.3419 | -122.3831 | 0.004578 | 122.1222 | -0.054932 | 0.61798
3258.4688 | 122.4152 | -0.068665 | 122.2549 | -0.13557 | -0.044098 | 0.0040866 | 0.021869 | -0.00041873 | -0.010316 | -0.0047231 | -0.019196 | 0.0057379 | 0.063209 | 0.044278 | -0.015806 | 0.025912 | -0.0057935 | -0.11444 | -0.041199 | -0.013733 | -0.032043 | 0.068665 | -0.059509 | 0.032043 | 0.47607 | 122.1451 | -0.082397 | 122.0947 | 0.1236 | 0.073242 | 0.10529 | 0.054932 | -122.2961 | -122.287 | 0.13733 | 0.10071 | 0.009156 | 0.045776 | -0.045776 | -0.013732 | -0.10986 | -0.16022 | 0.19226 | 0.17395 | 0.14191 | 0.18768 | 0.15564 | 0.082398 | -0.01831 | 0.20599 | 122.1771 | -0.027466 | 122.2275 | 0.027466 | 122.2137 | -122.2687 | -122.3373 | 0.036622 | 122.1634 | -0.045776 | 0.54474
3260.1719 | 122.3511 | -0.09613 | 122.2687 | -0.17372 | -0.04303 | 0.003232 | 0.024005 | 0.00086307 | -0.0081796 | -0.0045095 | -0.092438 | 0.0044561 | 0.064063 | 0.04855 | -0.017729 | 0.02869 | -0.0025891 | -0.1236 | 0 | -0.045776 | -0.11444 | -0.022888 | -0.14648 | -0.032043 | 0.36621 | 122.1909 | -0.091553 | 122.0535 | 0.027466 | -0.027466 | 0.041199 | 0.050354 | -122.2687 | -122.3831 | 0.073242 | 0.064087 | -0.050354 | 0.013733 | -0.10071 | 0.004577 | -0.07782 | -0.21515 | 0.1236 | 0.13733 | 0.068664 | 0.13275 | 0.064087 | 0.022888 | -0.068665 | 0.11902 | 122.1451 | 0.045776 | 122.2824 | 0.09613 | 122.287 | -122.3145 | -122.3602 | -0.018311 | 122.1497 | -0.027466 | 0.46234
3261.9375 | 122.4472 | -0.045776 | 122.2229 | -0.16609 | -0.041321 | 0.002164 | 0.024646 | 0.00064947 | -0.0071116 | -0.0038687 | -0.068024 | 0.0065923 | 0.061927 | 0.045773 | -0.018369 | 0.028903 | -0.0089977 | -0.059509 | -0.050354 | -0.018311 | 0.036621 | 0.13275 | -0.022888 | 0.064087 | 0.49896 | 122.1451 | -0.064087 | 122.168 | 0.16937 | 0.1236 | 0.16022 | 0.027465 | -122.2733 | -122.1863 | 0.17853 | 0.10986 | 0.022888 | 0.082398 | -0.004577 | -0.018311 | -0.077819 | -0.054931 | 0.21515 | 0.20599 | 0.16937 | 0.2243 | 0.18768 | 0.15106 | 0.054932 | 0.23346 | 122.2321 | -0.032043 | 122.2092 | -0.004578 | 122.1909 | -122.2412 | -122.287 | 0.082397 | 122.2137 | -0.013733 | 0.54474
3263.7031 | 122.3373 | -0.086975 | 122.2504 | -0.15083 | -0.041107 | 0.0028048 | 0.026355 | -0.0029821 | -0.0094614 | -0.00087794 | -0.12296 | 0.0057379 | 0.062782 | 0.044491 | -0.017088 | 0.026767 | -0.0034435 | -0.10071 | -0.022888 | -0.036621 | -0.036621 | 0.032043 | -0.10529 | -0.018311 | 0.46234 | 122.1954 | -0.073242 | 122.0673 | 0.054932 | -0.032043 | 0.045776 | 0.050354 | -122.2733 | -122.287 | 0.11902 | 0.068664 | -0.018311 | 0.01831 | -0.068665 | 0.013733 | -0.054931 | -0.1831 | 0.14191 | 0.13275 | 0.054932 | 0.11902 | 0.041199 | 0.068664 | 0 | 0.12817 | 122.1405 | 0.013733 | 122.2687 | 0.064087 | 122.2824 | -122.287 | -122.3236 | 0.050354 | 122.1542 | -0.013733 | 0.54932
3265.3906 | 122.4701 | -0.064087 | 122.2412 | -0.12794 | -0.042389 | 0.003232 | 0.022296 | -0.00084593 | -0.01053 | -0.0023733 | -0.055817 | 0.0046697 | 0.062782 | 0.050473 | -0.018156 | 0.028903 | -0.0049389 | -0.073242 | -0.041199 | -0.027466 | 0.018311 | 0.11444 | -0.045776 | 0.050354 | 0.48981 | 122.1313 | -0.064087 | 122.1634 | 0.16022 | 0.09613 | 0.17395 | 0.036621 | -122.2824 | -122.2229 | 0.17853 | 0.11444 | 0.018311 | 0.07782 | -0.01831 | 0 | -0.10986 | -0.07782 | 0.2243 | 0.23804 | 0.16022 | 0.23804 | 0.16022 | 0.14191 | 0.045777 | 0.2243 | 122.2275 | -0.013733 | 122.1954 | 0.022888 | 122.1954 | -122.2687 | -122.3053 | 0.082398 | 122.2275 | -0.009155 | 0.55389
3267.1562 | 122.3465 | -0.10529 | 122.287 | -0.11269 | -0.044953 | 0.0017368 | 0.026141 | -0.0021277 | -0.011598 | -0.0055777 | -0.055817 | 0.0068059 | 0.065345 | 0.050046 | -0.01666 | 0.025485 | -0.0060071 | -0.15564 | -0.013733 | -0.045776 | -0.10529 | -0.022888 | -0.10986 | -0.022888 | 0.5127 | 122.2 | -0.091553 | 122.0306 | 0.045776 | -0.009155 | 0.036621 | 0.05951 | -122.3007 | -122.3923 | 0.082398 | 0.082398 | -0.004577 | 0.022888 | -0.064087 | 0.013733 | -0.086975 | -0.25635 | 0.15106 | 0.14191 | 0.096131 | 0.12817 | 0.082398 | 0.022888 | -0.05951 | 0.13733 | 122.1222 | 0.032043 | 122.2916 | 0.091553 | 122.3053 | -122.3328 | -122.3785 | 0 | 122.1359 | -0.050354 | 0.61798
3268.9219 | 122.4609 | -0.059509 | 122.2275 | -0.17372 | -0.042389 | 0.002164 | 0.024218 | -0.0014867 | -0.01053 | -0.0034415 | -0.092438 | 0.0053107 | 0.064277 | 0.051968 | -0.016447 | 0.027835 | -0.0015209 | -0.086975 | -0.054932 | -0.018311 | -0.004578 | 0.091553 | -0.050354 | 0.050354 | 0.47607 | 122.1634 | -0.064087 | 122.1588 | 0.16479 | 0.10986 | 0.16022 | 0.041198 | -122.2824 | -122.2321 | 0.15106 | 0.10986 | 0.009155 | 0.068665 | -0.032043 | -0.004578 | -0.064087 | -0.068665 | 0.2243 | 0.21973 | 0.16937 | 0.2243 | 0.17395 | 0.10986 | 0.013733 | 0.22888 | 122.2229 | -0.036621 | 122.2275 | 0.004577 | 122.2229 | -122.2458 | -122.2916 | 0.054931 | 122.2183 | -0.027466 | 0.53558
3270.6719 | 122.4335 | -0.054932 | 122.2229 | -0.17372 | -0.043244 | 0.0036594 | 0.022082 | 0.00064947 | -0.010316 | -0.0021597 | -0.031403 | 0.0059515 | 0.064918 | 0.045346 | -0.018369 | 0.02634 | -0.0096387 | -0.073242 | -0.059509 | -0.009155 | 0.004578 | 0.13275 | -0.050354 | 0.064087 | 0.49896 | 122.1542 | -0.068665 | 122.1039 | 0.12817 | 0.082397 | 0.11902 | 0.045777 | -122.2824 | -122.2183 | 0.18768 | 0.11902 | 0.004578 | 0.073242 | -0.041199 | -0.013733 | -0.068664 | -0.11902 | 0.18311 | 0.17395 | 0.13733 | 0.18768 | 0.15106 | 0.14191 | 0.013733 | 0.19684 | 122.1725 | -0.050354 | 122.2229 | -0.004577 | 122.2092 | -122.2321 | -122.2916 | 0.05951 | 122.1588 | -0.01831 | 0.55389
3272.375 | 122.3557 | -0.091553 | 122.2778 | -0.097427 | -0.044312 | 0.0019504 | 0.024005 | 0.00043587 | -0.010316 | -0.0042959 | -0.055817 | 0.0083013 | 0.064491 | 0.048764 | -0.015592 | 0.026981 | -0.0040845 | -0.14648 | -0.022888 | -0.086975 | -0.10529 | 0 | -0.11902 | -0.027466 | 0.52185 | 122.2183 | -0.10529 | 122.0444 | 0.045776 | -0.004578 | 0.032043 | 0.004578 | -122.3007 | -122.3831 | 0.091553 | 0.064087 | -0.027466 | 0.059509 | -0.032044 | -0.013733 | -0.059509 | -0.23346 | 0.13733 | 0.1236 | 0.086975 | 0.13733 | 0.10071 | 0.086975 | -0.018311 | 0.15106 | 122.1497 | 0.064087 | 122.3236 | 0.068665 | 122.3099 | -122.3648 | -122.3831 | -0.013733 | 122.1359 | -0.054931 | 0.6134
3274.1406 | 122.4472 | -0.045776 | 122.2366 | -0.17372 | -0.043244 | 0.003232 | 0.024646 | 0.0044947 | -0.010316 | -0.0038687 | -0.052765 | 0.0059515 | 0.065772 | 0.052182 | -0.019651 | 0.030399 | -0.0077161 | -0.11902 | -0.032043 | -0.050354 | -0.050354 | 0.050354 | -0.086975 | 0.018311 | 0.43945 | 122.1817 | -0.086975 | 122.1451 | 0.14191 | 0.091553 | 0.16937 | -0.004578 | -122.2687 | -122.287 | 0.09613 | 0.064087 | -0.041199 | 0.068665 | -0.036621 | -0.041199 | -0.054931 | -0.091552 | 0.18768 | 0.21515 | 0.13733 | 0.25635 | 0.17853 | 0.10071 | 0 | 0.22888 | 122.2321 | 0.018311 | 122.2687 | 0.013733 | 122.2275 | -122.287 | -122.3236 | -0.004578 | 122.1909 | -0.073243 | 0.48523
3275.875 | 122.3373 | -0.10986 | 122.2641 | -0.097427 | -0.043885 | 0.0030184 | 0.021655 | -0.0029821 | -0.01053 | -0.0023733 | -0.055817 | 0.0063787 | 0.063209 | 0.045132 | -0.016233 | 0.02634 | -0.0030163 | -0.13275 | -0.009155 | -0.032043 | -0.082397 | 0.022888 | -0.10071 | 0 | 0.53101 | 122.1725 | -0.091553 | 122.0169 | 0.045776 | 0 | 0.027466 | 0.07782 | -122.2733 | -122.3465 | 0.13275 | 0.10986 | 0.009155 | 0.032043 | -0.068665 | 0.01831 | -0.091553 | -0.24719 | 0.15564 | 0.13733 | 0.10986 | 0.11902 | 0.091553 | 0.054931 | -0.050354 | 0.13733 | 122.1085 | 0.022888 | 122.2641 | 0.10071 | 122.2824 | -122.2961 | -122.3557 | 0.027466 | 122.1268 | -0.022888 | 0.64087
3277.6406 | 122.319 | -0.086975 | 122.2504 | -0.089798 | -0.042389 | 0.003232 | 0.025927 | 0.0027857 | -0.01053 | -0.0023733 | -0.10159 | 0.0065923 | 0.063209 | 0.056454 | -0.017088 | 0.025912 | -0.0072889 | -0.13275 | -0.009155 | -0.050354 | -0.10529 | -0.027466 | -0.15106 | -0.045776 | 0.3479 | 122.2092 | -0.10986 | 122.0306 | -0.013733 | -0.059509 | 0.018311 | 0.036621 | -122.2595 | -122.3557 | 0.059509 | 0.041199 | -0.064087 | 0.004578 | -0.10071 | -0.022888 | -0.041199 | -0.21973 | 0.073242 | 0.10529 | 0.027466 | 0.12817 | 0.050354 | 0.022888 | -0.054932 | 0.09613 | 122.1405 | 0.041199 | 122.319 | 0.07782 | 122.2961 | -122.3007 | -122.3602 | -0.018311 | 122.1176 | -0.045776 | 0.43488
3279.4219 | 122.4884 | -0.050354 | 122.2 | -0.12794 | -0.044953 | 0.0013094 | 0.021441 | -0.0019141 | -0.01053 | -0.0062185 | -0.0008851 | 0.0042425 | 0.062995 | 0.049405 | -0.018583 | 0.025272 | -2.571e-05 | -0.082397 | -0.064087 | -0.004578 | 0.036621 | 0.16937 | 0.027466 | 0.11902 | 0.67291 | 122.1634 | -0.068665 | 122.1634 | 0.19226 | 0.15564 | 0.16022 | 0.045776 | -122.2641 | -122.1634 | 0.21973 | 0.16937 | 0.07782 | 0.1236 | 0.032044 | -0.018311 | -0.036621 | -0.036621 | 0.24261 | 0.21057 | 0.20599 | 0.22888 | 0.22431 | 0.17395 | 0.041199 | 0.26093 | 122.2321 | -0.059509 | 122.2321 | -0.013733 | 122.2137 | -122.2046 | -122.2687 | 0.086975 | 122.2137 | -0.032043 | 0.72327
3281.125 | 122.3648 | -0.09613 | 122.2321 | -0.11269 | -0.043244 | 0.0013094 | 0.024218 | -0.0042639 | -0.0090342 | -0.0032277 | -0.10159 | 0.0057379 | 0.065772 | 0.051327 | -0.019438 | 0.027835 | -0.0062207 | -0.11902 | -0.022888 | -0.050354 | -0.059509 | 0.013733 | -0.073242 | 0 | 0.53558 | 122.2046 | -0.082397 | 122.0947 | 0.086975 | 0.013733 | 0.07782 | 0.045776 | -122.2549 | -122.2916 | 0.10986 | 0.09613 | 0.022888 | 0.050354 | -0.022888 | 0.013733 | -0.027466 | -0.13733 | 0.1831 | 0.17395 | 0.10986 | 0.16022 | 0.09613 | 0.064087 | -0.009155 | 0.16937 | 122.1771 | 0.027466 | 122.287 | 0.073242 | 122.3007 | -122.2824 | -122.3145 | 0.036621 | 122.1909 | -0.022889 | 0.63171
3282.875 | 122.3511 | -0.09613 | 122.2595 | -0.13557 | -0.04538 | 0.0028048 | 0.022509 | 0.0023585 | -0.011384 | -0.0040823 | -0.016144 | 0.0057379 | 0.064491 | 0.045346 | -0.015165 | 0.025699 | -0.0019483 | -0.086975 | -0.041199 | -0.022888 | -0.022888 | 0.091553 | -0.027466 | 0.054932 | 0.57678 | 122.1863 | -0.082397 | 122.049 | 0.07782 | 0.022888 | 0.059509 | 0.073242 | -122.3007 | -122.2824 | 0.18768 | 0.15106 | 0.068664 | 0.07782 | -0.004578 | 0.013733 | -0.073242 | -0.21057 | 0.17395 | 0.15564 | 0.11902 | 0.14191 | 0.10528 | 0.11444 | 0 | 0.16022 | 122.1313 | -0.018311 | 122.2687 | 0.054931 | 122.2824 | -122.2824 | -122.3419 | 0.073242 | 122.1451 | 0.009155 | 0.67291
3284.6406 | 122.4838 | -0.032043 | 122.2183 | -0.16609 | -0.045594 | 0.001523 | 0.022723 | -0.00063233 | -0.012666 | -0.0038687 | -0.0039367 | 0.0061651 | 0.064063 | 0.046628 | -0.014738 | 0.026126 | -0.0034435 | -0.073242 | -0.059509 | -0.018311 | 0.036621 | 0.13733 | 0.022888 | 0.11444 | 0.63171 | 122.1268 | -0.07782 | 122.1542 | 0.18768 | 0.16022 | 0.15106 | 0.013732 | -122.2778 | -122.1817 | 0.16937 | 0.14648 | 0.054931 | 0.13275 | 0.041199 | -0.045777 | -0.091553 | -0.064087 | 0.21973 | 0.18311 | 0.19226 | 0.22888 | 0.23804 | 0.15564 | 0.054932 | 0.2655 | 122.2321 | -0.041198 | 122.2046 | -0.027466 | 122.1588 | -122.2366 | -122.2961 | 0.068664 | 122.1863 | -0.041199 | 0.66376
3286.3906 | 122.438 | -0.036621 | 122.2137 | -0.2195 | -0.041962 | 0.0051546 | 0.023791 | 0.00022207 | -0.007966 | -0.0036551 | -0.055817 | 0.0050971 | 0.063636 | 0.049191 | -0.017301 | 0.028049 | -0.0047253 | -0.059509 | -0.068665 | 0.004578 | 0.045776 | 0.1236 | -0.032043 | 0.068665 | 0.51727 | 122.1359 | -0.064087 | 122.1588 | 0.15106 | 0.10529 | 0.15564 | 0.041199 | -122.2824 | -122.168 | 0.16022 | 0.10529 | 0.004578 | 0.064087 | -0.036621 | -0.027466 | -0.07782 | -0.054932 | 0.18768 | 0.19226 | 0.14191 | 0.21973 | 0.16937 | 0.11902 | 0.041198 | 0.21515 | 122.2229 | -0.073243 | 122.2 | -0.032044 | 122.1725 | -122.2092 | -122.2778 | 0.082397 | 122.1954 | -0.022888 | 0.55389
3288.0781 | 122.3648 | -0.09613 | 122.2778 | -0.1432 | -0.04303 | 0.0034456 | 0.027423 | 8.47e-06 | -0.009675 | -0.0049367 | -0.1199 | 0.0046697 | 0.066627 | 0.051541 | -0.018156 | 0.027408 | -0.0066479 | -0.086975 | -0.018311 | -0.027466 | -0.022888 | 0.068665 | -0.068665 | 0.013733 | 0.54932 | 122.1725 | -0.07782 | 122.0993 | 0.082397 | 0.032043 | 0.07782 | 0.068664 | -122.2961 | -122.3007 | 0.16479 | 0.10986 | 0.027465 | 0.041199 | -0.041199 | 0.01831 | -0.10529 | -0.17853 | 0.17853 | 0.17395 | 0.12817 | 0.15564 | 0.10986 | 0.096131 | 0.004578 | 0.16022 | 122.1771 | 0.009155 | 122.2504 | 0.077819 | 122.2687 | -122.3053 | -122.3557 | 0.073242 | 122.1954 | 0.009155 | 0.64545
3289.8438 | 122.4426 | -0.054932 | 122.2321 | -0.17372 | -0.043885 | 0.0034456 | 0.023364 | -0.00020513 | -0.0092478 | -0.0038687 | -0.04361 | 0.0050971 | 0.065986 | 0.047696 | -0.017088 | 0.024631 | -0.0032299 | -0.07782 | -0.054932 | 0.004578 | 0.027466 | 0.15106 | -0.036621 | 0.064087 | 0.49896 | 122.1405 | -0.064087 | 122.1359 | 0.16022 | 0.091553 | 0.14191 | 0.05951 | -122.287 | -122.2046 | 0.20599 | 0.11902 | 0.018311 | 0.059509 | -0.041199 | -0.009155 | -0.091553 | -0.096131 | 0.21515 | 0.19684 | 0.14649 | 0.20599 | 0.15564 | 0.14648 | 0.022888 | 0.2243 | 122.2 | -0.05951 | 122.2046 | 0 | 122.1954 | -122.2275 | -122.2961 | 0.082398 | 122.1909 | -0.022888 | 0.55389
3291.6094 | 122.3602 | -0.07782 | 122.2824 | -0.16609 | -0.045594 | 0.0025912 | 0.023364 | 0.0034265 | -0.01117 | -0.0068593 | -0.028351 | 0.0046697 | 0.063423 | 0.052182 | -0.016233 | 0.026767 | -0.0047253 | -0.082397 | -0.036621 | -0.009155 | 0 | 0.09613 | -0.022888 | 0.045776 | 0.59509 | 122.1725 | -0.07782 | 122.0627 | 0.082397 | 0.036621 | 0.068665 | 0.068665 | -122.319 | -122.2824 | 0.17395 | 0.1236 | 0.054932 | 0.054931 | -0.013733 | 0 | -0.10986 | -0.21973 | 0.16022 | 0.14649 | 0.11444 | 0.14649 | 0.11444 | 0.10528 | 0.009155 | 0.16022 | 122.1405 | -0.027466 | 122.2504 | 0.041199 | 122.2504 | -122.2916 | -122.3602 | 0.07782 | 122.1405 | -0.004577 | 0.67291
3293.375 | 122.3511 | -0.068665 | 122.2549 | -0.17372 | -0.043885 | 0.0025912 | 0.025714 | -0.00063233 | -0.01053 | -0.0036551 | -0.1077 | 0.0072333 | 0.064063 | 0.054104 | -0.018583 | 0.028476 | -0.0053661 | -0.13275 | -0.013733 | -0.054932 | -0.091553 | -0.032043 | -0.14648 | -0.041199 | 0.36621 | 122.1863 | -0.10986 | 122.0627 | 0.032043 | -0.036621 | 0.041199 | 0.013733 | -122.2687 | -122.3465 | 0.036622 | 0.027466 | -0.077819 | 0.013733 | -0.091552 | -0.041198 | -0.068665 | -0.19226 | 0.10071 | 0.10986 | 0.032044 | 0.15106 | 0.073242 | 0.022889 | -0.036621 | 0.14191 | 122.1725 | 0.041199 | 122.2961 | 0.054932 | 122.2549 | -122.3099 | -122.3648 | -0.022888 | 122.1313 | -0.064086 | 0.43488
3295.0781 | 122.4426 | -0.032043 | 122.2412 | -0.20424 | -0.043457 | 0.0043002 | 0.024646 | 0.0021447 | -0.0098886 | -0.0015189 | -0.071076 | 0.0050971 | 0.061714 | 0.047055 | -0.017942 | 0.026767 | -0.0045117 | -0.050354 | -0.050354 | -0.018311 | 0.018311 | 0.13275 | -0.018311 | 0.059509 | 0.50812 | 122.1451 | -0.059509 | 122.1588 | 0.15106 | 0.10529 | 0.14191 | 0.013732 | -122.2916 | -122.2229 | 0.16479 | 0.091552 | 0.013732 | 0.07782 | 0 | -0.027466 | -0.09613 | -0.082398 | 0.18311 | 0.17395 | 0.13733 | 0.20142 | 0.16479 | 0.15106 | 0.036622 | 0.21057 | 122.2183 | -0.032043 | 122.2046 | -0.018311 | 122.1771 | -122.2595 | -122.3007 | 0.050354 | 122.1909 | -0.018311 | 0.54016
3296.8594 | 122.3236 | -0.10529 | 122.2504 | -0.15846 | -0.042603 | 0.003873 | 0.025927 | -0.0031957 | -0.010743 | -0.0017325 | -0.1077 | 0.0068059 | 0.062995 | 0.051327 | -0.017088 | 0.02634 | -0.0036573 | -0.13275 | -0.009155 | -0.045776 | -0.09613 | -0.022888 | -0.16022 | -0.041199 | 0.37537 | 122.2 | -0.086975 | 122.0261 | 0.013733 | -0.045776 | 0.013733 | 0.05951 | -122.2595 | -122.3465 | 0.082398 | 0.064087 | -0.054931 | 0.004577 | -0.11444 | 0.018311 | -0.050354 | -0.2243 | 0.11902 | 0.11902 | 0.05951 | 0.10071 | 0.041199 | 0.022888 | -0.050354 | 0.10071 | 122.113 | 0.036621 | 122.287 | 0.096131 | 122.3053 | -122.2961 | -122.3373 | 0.009156 | 122.1313 | -0.027465 | 0.48065
3298.5625 | 122.4518 | -0.050354 | 122.2183 | -0.12794 | -0.045166 | 0.00088223 | 0.021014 | -0.0046911 | -0.0081796 | -0.0042959 | 0.0082703 | 0.0044561 | 0.0615 | 0.045987 | -0.01666 | 0.027408 | -0.0057935 | -0.07782 | -0.059509 | -0.018311 | 0.064087 | 0.17853 | 0.018311 | 0.10071 | 0.66376 | 122.1359 | -0.041199 | 122.1497 | 0.19226 | 0.14648 | 0.16479 | 0.032043 | -122.2778 | -122.1542 | 0.22888 | 0.15106 | 0.068665 | 0.11902 | 0.036622 | 0.009155 | -0.082398 | -0.068665 | 0.24261 | 0.21515 | 0.19684 | 0.20599 | 0.18768 | 0.19684 | 0.082398 | 0.23346 | 122.1909 | -0.041198 | 122.1771 | -0.009155 | 122.1863 | -122.2366 | -122.2595 | 0.11444 | 122.2 | -0.027466 | 0.71411
3300.3281 | 122.4197 | -0.064087 | 122.2366 | -0.12032 | -0.042603 | 0.0053684 | 0.0255 | 0.00022207 | -0.0077524 | -0.0038687 | -0.086334 | 0.0070197 | 0.064491 | 0.044278 | -0.017301 | 0.026981 | -0.0030163 | -0.12817 | -0.027466 | -0.041199 | -0.068665 | 0.013733 | -0.1236 | -0.013733 | 0.40741 | 122.1542 | -0.091553 | 122.1222 | 0.086975 | 0.059509 | 0.10986 | 0.022888 | -122.2641 | -122.3053 | 0.07782 | 0.050354 | -0.059509 | 0.027466 | -0.082397 | -0.027466 | -0.082397 | -0.11444 | 0.15106 | 0.17395 | 0.1236 | 0.20142 | 0.15106 | 0.054932 | -0.027466 | 0.17853 | 122.2137 | 0.013733 | 122.2458 | 0.036621 | 122.2183 | -122.2778 | -122.3282 | -0.004578 | 122.1863 | -0.064087 | 0.4715
3302.1094 | 122.4014 | -0.07782 | 122.2504 | -0.16609 | -0.044312 | 0.0019504 | 0.025927 | 0.0025721 | -0.009675 | -0.0040823 | -0.052765 | 0.0057379 | 0.063209 | 0.052395 | -0.017942 | 0.027621 | -0.0070751 | -0.07782 | -0.064087 | -0.022888 | 0.009155 | 0.15106 | -0.027466 | 0.068665 | 0.52643 | 122.1497 | -0.07782 | 122.1176 | 0.1236 | 0.091553 | 0.1236 | 0.054932 | -122.3145 | -122.2412 | 0.22888 | 0.14649 | 0.050354 | 0.091553 | -0.004578 | 0 | -0.10071 | -0.13275 | 0.20142 | 0.20142 | 0.16937 | 0.20142 | 0.16937 | 0.17395 | 0.032043 | 0.20142 | 122.1954 | -0.041199 | 122.2275 | 0.013733 | 122.2275 | -122.2733 | -122.3282 | 0.086975 | 122.1954 | 0 | 0.60425
3303.8125 | 122.3785 | -0.091553 | 122.287 | -0.12794 | -0.04538 | 0.002164 | 0.025073 | 0.0027857 | -0.0098886 | -0.0040823 | -0.086334 | 0.0076605 | 0.059577 | 0.052823 | -0.017088 | 0.029117 | -0.0064343 | -0.11902 | -0.027466 | -0.045776 | -0.068665 | 0.018311 | -0.082397 | -0.004578 | 0.54474 | 122.2 | -0.07782 | 122.0764 | 0.07782 | 0.022888 | 0.064087 | 0.045777 | -122.3145 | -122.3557 | 0.10986 | 0.086975 | 0.009156 | 0.041198 | -0.036621 | 0.013733 | -0.086975 | -0.21057 | 0.16937 | 0.15564 | 0.11444 | 0.14191 | 0.10071 | 0.064087 | -0.022889 | 0.15564 | 122.1542 | 0.01831 | 122.2778 | 0.064087 | 122.2916 | -122.3328 | -122.3648 | 0.022888 | 122.168 | -0.027466 | 0.63629
3305.5625 | 122.4655 | -0.050354 | 122.2321 | -0.18135 | -0.044098 | -0.00061317 | 0.023578 | 0.0010767 | -0.012025 | -0.0053641 | 0.014374 | 0.0046697 | 0.062995 | 0.042569 | -0.016874 | 0.025699 | -0.0038709 | -0.068665 | -0.064087 | -0.036621 | 0.059509 | 0.1831 | 0.022888 | 0.09613 | 0.66834 | 122.1725 | -0.068665 | 122.1542 | 0.19226 | 0.14191 | 0.16022 | 0.013733 | -122.2961 | -122.1725 | 0.23346 | 0.14648 | 0.073242 | 0.13275 | 0.059509 | -0.018311 | -0.05951 | -0.07782 | 0.24261 | 0.21057 | 0.19226 | 0.22888 | 0.21057 | 0.21973 | 0.09613 | 0.26093 | 122.2229 | -0.027466 | 122.2412 | -0.013733 | 122.2229 | -122.2687 | -122.3007 | 0.10986 | 122.2046 | -0.018311 | 0.71869
3307.3125 | 122.3877 | -0.073242 | 122.2504 | -0.16609 | -0.043885 | 0.0023776 | 0.024646 | 0.00043587 | -0.010102 | -0.0036551 | -0.12601 | 0.0065923 | 0.064491 | 0.044064 | -0.017942 | 0.026767 | -0.0045117 | -0.10986 | 0 | -0.045776 | -0.086975 | 0 | -0.13733 | -0.032043 | 0.3891 | 122.1725 | -0.086975 | 122.0993 | 0.073242 | 0.027466 | 0.091553 | 0.027466 | -122.2504 | -122.3373 | 0.073242 | 0.041199 | -0.064087 | 0.013733 | -0.091553 | -0.013733 | -0.07782 | -0.15106 | 0.14648 | 0.16479 | 0.10071 | 0.17853 | 0.11444 | 0.045776 | -0.041199 | 0.16022 | 122.1863 | 0.045776 | 122.2595 | 0.073242 | 122.2458 | -122.2961 | -122.3373 | -0.013733 | 122.1725 | -0.036621 | 0.46234
3309.0781 | 122.3419 | -0.09613 | 122.2687 | -0.082169 | -0.046662 | 0.00024143 | 0.023578 | -0.0036231 | -0.012025 | -0.0036551 | -0.080231 | 0.0089423 | 0.064277 | 0.04855 | -0.017301 | 0.027408 | -0.0042981 | -0.15106 | -0.009155 | -0.073242 | -0.091553 | 0.004578 | -0.10986 | -0.009155 | 0.5127 | 122.2046 | -0.10986 | 122.0261 | 0.032043 | -0.009155 | 0.022888 | 0.022888 | -122.2778 | -122.3602 | 0.10071 | 0.086975 | -0.013733 | 0.064087 | -0.036621 | -0.013733 | -0.064087 | -0.24262 | 0.12817 | 0.11902 | 0.086975 | 0.13275 | 0.10071 | 0.07782 | -0.018311 | 0.14191 | 122.1359 | 0.064087 | 122.3145 | 0.086975 | 122.3007 | -122.3419 | -122.3785 | 0.004577 | 122.1222 | -0.054932 | 0.60882
3310.7812 | 122.406 | -0.059509 | 122.2458 | -0.16609 | -0.043457 | 0.00045503 | 0.020587 | 0.0042811 | -0.0094614 | -0.0042959 | -0.025299 | 0.0040289 | 0.064491 | 0.044919 | -0.01666 | 0.027835 | -0.0010937 | -0.11444 | -0.050354 | -0.018311 | -0.045776 | 0.059509 | -0.059509 | 0.032043 | 0.4715 | 122.1725 | -0.073242 | 122.0993 | 0.10071 | 0.059509 | 0.10071 | 0.041198 | -122.2961 | -122.2916 | 0.11902 | 0.091552 | 0 | 0.050354 | -0.041198 | -0.013733 | -0.073243 | -0.14648 | 0.16022 | 0.16022 | 0.11902 | 0.17395 | 0.13275 | 0.07782 | -0.027465 | 0.17395 | 122.1725 | -0.032043 | 122.2458 | 0.009155 | 122.2321 | -122.2641 | -122.319 | 0.013733 | 122.1588 | -0.054932 | 0.53101
3312.5312 | 122.4243 | -0.059509 | 122.2458 | -0.18898 | -0.041962 | 0.0034456 | 0.023791 | -0.0014867 | -0.011811 | -0.0025869 | -0.04361 | 0.0076605 | 0.062141 | 0.049405 | -0.017729 | 0.028903 | -0.0051525 | -0.07782 | -0.059509 | 0.009155 | 0.009155 | 0.10529 | -0.036621 | 0.054932 | 0.48523 | 122.1588 | -0.068665 | 122.1222 | 0.1236 | 0.082397 | 0.1236 | 0.068664 | -122.3053 | -122.2366 | 0.16479 | 0.11444 | 0.022888 | 0.045777 | -0.045776 | -0.009156 | -0.086976 | -0.1236 | 0.1831 | 0.1831 | 0.14191 | 0.19226 | 0.15106 | 0.096131 | 0 | 0.19226 | 122.1909 | -0.068664 | 122.2275 | 0 | 122.2183 | -122.2366 | -122.3145 | 0.068664 | 122.1817 | -0.018311 | 0.54474
3314.2812 | 122.406 | -0.064087 | 122.2412 | -0.16609 | -0.04068 | 0.0019504 | 0.02315 | -0.0044775 | -0.010102 | -0.0040823 | -0.046661 | 0.0063787 | 0.063423 | 0.046628 | -0.019224 | 0.025272 | -0.0089977 | -0.07782 | -0.054932 | -0.009155 | 0.013733 | 0.11902 | -0.036621 | 0.059509 | 0.49896 | 122.1451 | -0.073242 | 122.1268 | 0.10986 | 0.07782 | 0.12817 | 0.054932 | -122.2961 | -122.2275 | 0.18311 | 0.1236 | 0.027466 | 0.068664 | -0.027466 | -0.009155 | -0.09613 | -0.11444 | 0.17395 | 0.19226 | 0.14191 | 0.20142 | 0.15106 | 0.12817 | 0.022888 | 0.18311 | 122.2 | -0.045777 | 122.2183 | 0.009155 | 122.2092 | -122.2504 | -122.3145 | 0.07782 | 122.1909 | -0.013733 | 0.56305
3316.0312 | 122.4518 | -0.041199 | 122.2595 | -0.16609 | -0.043244 | 0.0023776 | 0.022937 | -0.0031957 | -0.0098886 | -0.0025869 | -0.080231 | 0.0063787 | 0.063423 | 0.047696 | -0.018369 | 0.028049 | -0.0030163 | -0.086975 | -0.041199 | -0.036621 | 0.004578 | 0.10071 | -0.041199 | 0.054932 | 0.48065 | 122.1588 | -0.064087 | 122.168 | 0.15106 | 0.10071 | 0.17853 | 0.004578 | -122.3007 | -122.2549 | 0.14191 | 0.096131 | 0 | 0.091553 | -0.004578 | -0.022888 | -0.10071 | -0.091552 | 0.19226 | 0.21973 | 0.14191 | 0.24261 | 0.1648 | 0.13733 | 0.041199 | 0.21515 | 122.2321 | -0.004578 | 122.2229 | 0 | 122.2 | -122.2961 | -122.3236 | 0.045777 | 122.2092 | -0.045776 | 0.52185
3317.7812 | 122.4243 | -0.082397 | 122.2229 | -0.16609 | -0.044953 | 0.0040866 | 0.022509 | -0.00063233 | -0.010957 | -0.0045095 | -0.013092 | 0.0055243 | 0.061927 | 0.050259 | -0.015592 | 0.029544 | -0.0047253 | -0.10986 | -0.041199 | -0.009155 | -0.032043 | 0.068665 | -0.059509 | 0.036621 | 0.49439 | 122.1634 | -0.086975 | 122.113 | 0.10986 | 0.086975 | 0.12817 | 0.073242 | -122.2641 | -122.2549 | 0.15106 | 0.11902 | 0.022888 | 0.045776 | -0.050354 | -0.004578 | -0.059509 | -0.10986 | 0.19226 | 0.21057 | 0.16937 | 0.21515 | 0.17395 | 0.07782 | -0.022888 | 0.19684 | 122.2 | -0.032044 | 122.2504 | 0.041198 | 122.2458 | -122.2321 | -122.3099 | 0.050354 | 122.1954 | -0.027466 | 0.57678
3319.4844 | 122.4152 | -0.082397 | 122.2137 | -0.16609 | -0.043885 | 0.0023776 | 0.021869 | 0.00022207 | -0.0092478 | -0.0019461 | -0.037506 | 0.0072333 | 0.065772 | 0.047909 | -0.017942 | 0.025485 | -0.0045117 | -0.064087 | -0.064087 | -0.018311 | 0.041199 | 0.13275 | -0.032043 | 0.064087 | 0.5127 | 122.1405 | -0.054932 | 122.1451 | 0.12817 | 0.10071 | 0.13275 | 0.064086 | -122.2778 | -122.1725 | 0.21515 | 0.14648 | 0.050354 | 0.082398 | -0.013732 | 0.027465 | -0.073242 | -0.068664 | 0.21057 | 0.21515 | 0.18311 | 0.18768 | 0.15564 | 0.15106 | 0.05951 | 0.18311 | 122.2 | -0.045776 | 122.1954 | 0.01831 | 122.2229 | -122.2321 | -122.2687 | 0.1236 | 122.2275 | 0.01831 | 0.59509
3321.2344 | 122.406 | -0.064087 | 122.2092 | -0.17372 | -0.043671 | 0.0030184 | 0.023364 | -0.00084593 | -0.01117 | -0.0062185 | -0.064972 | 0.0048833 | 0.060645 | 0.047696 | -0.016874 | 0.026553 | -0.0060071 | -0.11444 | -0.050354 | -0.018311 | -0.027466 | 0.073242 | -0.045776 | 0.045776 | 0.47607 | 122.1634 | -0.068665 | 122.1085 | 0.11444 | 0.07782 | 0.11444 | 0.045776 | -122.2595 | -122.2366 | 0.13733 | 0.10986 | 0.018311 | 0.064087 | -0.027465 | -0.004578 | -0.045776 | -0.10071 | 0.17853 | 0.17853 | 0.14191 | 0.18311 | 0.14649 | 0.091553 | -0.009155 | 0.18311 | 122.1771 | -0.032043 | 122.2321 | 0.013733 | 122.2275 | -122.2275 | -122.2778 | 0.036621 | 122.1725 | -0.050354 | 0.54016
3322.9219 | 122.3923 | -0.082397 | 122.2366 | -0.13557 | -0.044953 | 0.0028048 | 0.024859 | -0.0017005 | -0.013093 | -0.0028005 | -0.1199 | 0.0063787 | 0.064063 | 0.052823 | -0.018369 | 0.026981 | -0.0092115 | -0.12817 | -0.018311 | -0.041199 | -0.050354 | 0.018311 | -0.091553 | -0.009155 | 0.54474 | 122.2366 | -0.086975 | 122.0856 | 0.086975 | 0.013733 | 0.068665 | 0.041198 | -122.2549 | -122.287 | 0.10071 | 0.073242 | -0.009156 | 0.032044 | -0.050354 | -0.004578 | 0 | -0.15106 | 0.16937 | 0.15106 | 0.09613 | 0.15564 | 0.10071 | 0.05951 | -0.009155 | 0.17395 | 122.1725 | 0.022888 | 122.3236 | 0.064086 | 122.319 | -122.2778 | -122.3236 | 0.032043 | 122.168 | -0.045777 | 0.62714
3324.6875 | 122.3419 | -0.091553 | 122.2778 | -0.06691 | -0.044525 | 0.0025912 | 0.0255 | -0.0040503 | -0.011384 | -0.0017325 | -0.074127 | 0.0063787 | 0.064491 | 0.047055 | -0.016874 | 0.02634 | -0.0094251 | -0.15106 | -0.013733 | -0.068665 | -0.091553 | 0 | -0.10529 | -0.018311 | 0.51727 | 122.1954 | -0.11444 | 122.0306 | 0.045776 | -0.018311 | 0.018311 | 0.022888 | -122.2916 | -122.3694 | 0.091553 | 0.073242 | -0.013733 | 0.050354 | -0.036621 | -0.022888 | -0.082397 | -0.24719 | 0.13733 | 0.10986 | 0.073242 | 0.13275 | 0.09613 | 0.068665 | -0.022888 | 0.16022 | 122.1451 | 0.054932 | 122.3099 | 0.07782 | 122.287 | -122.3465 | -122.3923 | 0 | 122.1222 | -0.059509 | 0.60883
3326.4375 | 122.3282 | -0.10529 | 122.2778 | -0.097427 | -0.045166 | -0.00082677 | 0.024646 | -0.0017005 | -0.010316 | -0.0047231 | -0.077179 | 0.0059515 | 0.065559 | 0.050046 | -0.01666 | 0.025485 | -0.0053661 | -0.16479 | -0.009155 | -0.054932 | -0.082397 | -0.004578 | -0.10071 | -0.018311 | 0.50812 | 122.1954 | -0.10071 | 122.0352 | 0.041199 | -0.013733 | 0.032043 | 0.050354 | -122.287 | -122.3602 | 0.10071 | 0.086975 | 0.004578 | 0.036621 | -0.045776 | 0.004578 | -0.082397 | -0.24262 | 0.14649 | 0.13733 | 0.091553 | 0.13275 | 0.086975 | 0.050354 | -0.027465 | 0.14191 | 122.1359 | 0.045777 | 122.2961 | 0.096131 | 122.3007 | -122.3328 | -122.3785 | 0.022889 | 122.1405 | -0.059509 | 0.6134
3328.125 | 122.3602 | -0.10529 | 122.2595 | -0.10506 | -0.041107 | 0.002164 | 0.027423 | 0.00022207 | -0.010957 | -0.0032277 | -0.13211 | 0.0059515 | 0.064277 | 0.047909 | -0.017301 | 0.02634 | -0.0023755 | -0.14191 | -0.009155 | -0.054932 | -0.10529 | -0.018311 | -0.15106 | -0.045776 | 0.36621 | 122.2046 | -0.10071 | 122.049 | 0.032043 | -0.036621 | 0.032043 | 0.050354 | -122.2687 | -122.3648 | 0.086975 | 0.05951 | -0.045776 | 0.009156 | -0.09613 | 0.004578 | -0.054931 | -0.21057 | 0.13733 | 0.13733 | 0.068665 | 0.13275 | 0.064087 | 0.036621 | -0.050354 | 0.13275 | 122.1497 | 0.045777 | 122.3053 | 0.096131 | 122.3099 | -122.3145 | -122.3602 | 0 | 122.1542 | -0.036621 | 0.4715
3329.9062 | 122.4472 | -0.054932 | 122.2321 | -0.13557 | -0.044953 | 0.0019504 | 0.02315 | -0.0049047 | -0.011598 | -0.0062185 | -0.031403 | 0.0063787 | 0.062995 | 0.041928 | -0.017515 | 0.027835 | -0.0019483 | -0.068665 | -0.064087 | -0.009155 | 0.045776 | 0.15106 | 0.027466 | 0.091553 | 0.65918 | 122.1176 | -0.059509 | 122.1497 | 0.18768 | 0.14648 | 0.15564 | 0.045777 | -122.2961 | -122.1863 | 0.20599 | 0.14649 | 0.082398 | 0.10071 | 0.036621 | -0.004577 | -0.11444 | -0.082398 | 0.24261 | 0.21057 | 0.20142 | 0.21515 | 0.20599 | 0.16022 | 0.054931 | 0.24719 | 122.2092 | -0.054932 | 122.1771 | -0.009155 | 122.1725 | -122.2412 | -122.2916 | 0.10071 | 122.2046 | -0.013733 | 0.71411
3331.6562 | 122.3465 | -0.10529 | 122.2961 | -0.11269 | -0.044739 | 0.0019504 | 0.022509 | -0.0031957 | -0.01352 | -0.0034415 | -0.058869 | 0.0076605 | 0.064063 | 0.037869 | -0.016233 | 0.027194 | -0.0036573 | -0.15106 | -0.018311 | -0.059509 | -0.10071 | -0.013733 | -0.11444 | -0.022888 | 0.51727 | 122.2092 | -0.09613 | 122.0444 | 0.032043 | -0.004578 | 0.041199 | 0.045777 | -122.3145 | -122.3969 | 0.091553 | 0.082398 | -0.009155 | 0.036621 | -0.054932 | 0.009156 | -0.086976 | -0.25177 | 0.13733 | 0.14649 | 0.10071 | 0.13733 | 0.091552 | 0.045776 | -0.041199 | 0.12817 | 122.1405 | 0.041198 | 122.3053 | 0.086975 | 122.3145 | -122.3557 | -122.3923 | 0.004578 | 122.1497 | -0.045776 | 0.62256
3333.4062 | 122.4564 | -0.054932 | 122.2183 | -0.13557 | -0.04303 | 0.00024143 | 0.0208 | -0.0049047 | -0.010102 | -0.0025869 | -0.016144 | 0.0044561 | 0.062141 | 0.048123 | -0.017942 | 0.025699 | -0.0060071 | -0.10986 | -0.032043 | -0.027466 | -0.022888 | 0.09613 | -0.018311 | 0.059509 | 0.55847 | 122.1817 | -0.086975 | 122.1497 | 0.17395 | 0.13733 | 0.15106 | 0.027466 | -122.2504 | -122.2412 | 0.15106 | 0.11444 | 0.036621 | 0.086975 | 0.009155 | -0.032043 | -0.036621 | -0.068665 | 0.22888 | 0.20599 | 0.19226 | 0.23804 | 0.2243 | 0.1236 | 0.004578 | 0.26092 | 122.2366 | -0.004577 | 122.2687 | 0.022889 | 122.2366 | -122.2458 | -122.3053 | 0.032044 | 122.2046 | -0.054931 | 0.6134
3335.1719 | 122.4609 | -0.054932 | 122.2275 | -0.082169 | -0.046875 | 0.0023776 | 0.020587 | 8.47e-06 | -0.010957 | -0.0075003 | -0.025299 | 0.0042425 | 0.064063 | 0.046414 | -0.017088 | 0.024204 | -0.0049389 | -0.059509 | -0.041199 | -0.004578 | 0.050354 | 0.16022 | 0.022888 | 0.10986 | 0.6546 | 122.1405 | -0.059509 | 122.1542 | 0.17853 | 0.15106 | 0.16022 | 0.050354 | -122.2687 | -122.1771 | 0.21515 | 0.16479 | 0.07782 | 0.11444 | 0.027466 | -0.004577 | -0.086975 | -0.073242 | 0.23346 | 0.21515 | 0.20599 | 0.21973 | 0.21057 | 0.16479 | 0.054932 | 0.23804 | 122.2137 | -0.036621 | 122.2 | 0.013733 | 122.1954 | -122.2321 | -122.287 | 0.10529 | 122.2092 | -0.004577 | 0.70953
3336.875 | 122.4426 | -0.045776 | 122.2183 | -0.21187 | -0.042816 | 0.0013094 | 0.022937 | -0.0040503 | -0.01117 | -0.0051505 | -0.074127 | 0.0063787 | 0.062782 | 0.0509 | -0.017088 | 0.028903 | -0.0053661 | -0.064087 | -0.054932 | -0.022888 | 0.050354 | 0.14648 | -0.018311 | 0.068665 | 0.5127 | 122.1542 | -0.059509 | 122.168 | 0.16022 | 0.10529 | 0.16022 | 0.022888 | -122.2733 | -122.168 | 0.19226 | 0.11444 | 0.027465 | 0.091553 | 0.004577 | -0.013733 | -0.064087 | -0.050354 | 0.20599 | 0.20599 | 0.15106 | 0.21973 | 0.16479 | 0.16937 | 0.073242 | 0.21973 | 122.2275 | -0.032044 | 122.2137 | -0.009156 | 122.2 | -122.2412 | -122.2778 | 0.09613 | 122.2137 | -0.018311 | 0.55847
3338.6406 | 122.4243 | -0.059509 | 122.2595 | -0.20424 | -0.045166 | 0.0034456 | 0.02315 | 0.00043587 | -0.0094614 | -0.0064321 | -0.028351 | 0.0050971 | 0.062568 | 0.048123 | -0.016874 | 0.025912 | -0.0032299 | -0.10529 | -0.036621 | -0.018311 | -0.018311 | 0.059509 | -0.050354 | 0.041199 | 0.4715 | 122.1497 | -0.086975 | 122.0947 | 0.11444 | 0.059509 | 0.11444 | 0.041198 | -122.2961 | -122.2778 | 0.11902 | 0.10071 | 0.009155 | 0.05951 | -0.032043 | -0.027466 | -0.10986 | -0.16479 | 0.17395 | 0.17395 | 0.11902 | 0.20142 | 0.14648 | 0.07782 | 0 | 0.20142 | 122.1817 | -0.01831 | 122.2366 | 0.022888 | 122.2092 | -122.2778 | -122.3465 | 0.041198 | 122.1542 | -0.045777 | 0.53101
3340.4062 | 122.438 | -0.059509 | 122.2321 | -0.1432 | -0.044312 | 0.001523 | 0.023364 | -0.0042639 | -0.010316 | -0.0045095 | -0.022247 | 0.0053107 | 0.061073 | 0.047055 | -0.017942 | 0.029544 | -0.0051525 | -0.1236 | -0.054932 | -0.018311 | -0.027466 | 0.064087 | -0.059509 | 0.050354 | 0.50812 | 122.1588 | -0.064087 | 122.1085 | 0.10529 | 0.10529 | 0.13275 | 0.041198 | -122.287 | -122.2595 | 0.1236 | 0.10986 | 0 | 0.068665 | -0.041198 | -0.004578 | -0.073243 | -0.1236 | 0.16479 | 0.19226 | 0.16479 | 0.19684 | 0.16937 | 0.082398 | -0.009155 | 0.16937 | 122.1725 | -0.036621 | 122.2229 | 0.004577 | 122.2183 | -122.2504 | -122.2961 | 0.032043 | 122.168 | -0.064087 | 0.56763
3342.1875 | 122.4426 | -0.041199 | 122.2183 | -0.2195 | -0.041962 | 0.0030184 | 0.022937 | -0.0017005 | -0.0094614 | -0.0049367 | -0.071076 | 0.0050971 | 0.063423 | 0.047055 | -0.017088 | 0.025058 | -0.0015209 | -0.041199 | -0.059509 | -0.013733 | 0.041199 | 0.14648 | -0.022888 | 0.068665 | 0.50354 | 122.1268 | -0.059509 | 122.1542 | 0.15106 | 0.10986 | 0.15564 | 0.027466 | -122.2778 | -122.1771 | 0.18768 | 0.10986 | 0.018311 | 0.082398 | -0.009155 | -0.01831 | -0.091553 | -0.064087 | 0.19226 | 0.19684 | 0.15106 | 0.21515 | 0.16937 | 0.16022 | 0.054932 | 0.21057 | 122.2137 | -0.045776 | 122.1863 | -0.01831 | 122.168 | -122.2321 | -122.2778 | 0.082398 | 122.1954 | 0 | 0.54474
3343.9531 | 122.4792 | -0.050354 | 122.2183 | -0.15083 | -0.04538 | 0.0023776 | 0.024646 | -0.0023413 | -0.011811 | -0.0028005 | -0.058869 | 0.0048833 | 0.062568 | 0.049405 | -0.016874 | 0.027408 | -0.0013073 | -0.068665 | -0.050354 | -0.009155 | 0.054932 | 0.17395 | 0.013733 | 0.10529 | 0.68665 | 122.1588 | -0.050354 | 122.1771 | 0.19684 | 0.16022 | 0.16937 | 0.041199 | -122.2687 | -122.1634 | 0.2243 | 0.15564 | 0.064087 | 0.11444 | 0.022888 | 0 | -0.05951 | -0.041199 | 0.24719 | 0.21973 | 0.21057 | 0.21973 | 0.21057 | 0.1831 | 0.064087 | 0.24719 | 122.2275 | -0.041199 | 122.2092 | 0 | 122.2092 | -122.2275 | -122.2687 | 0.10529 | 122.2275 | -0.018311 | 0.737
3345.6406 | 122.4472 | -0.054932 | 122.2366 | -0.12032 | -0.042603 | 0.0017368 | 0.019519 | -0.0025549 | -0.013307 | -0.0036551 | -0.06192 | 0.0059515 | 0.0615 | 0.047909 | -0.016233 | 0.027194 | -0.0066479 | -0.059509 | -0.059509 | 0 | 0.054932 | 0.13733 | 0.013733 | 0.091553 | 0.67291 | 122.1588 | -0.073242 | 122.1542 | 0.18768 | 0.13733 | 0.14191 | 0.054932 | -122.2961 | -122.1817 | 0.19226 | 0.14649 | 0.068665 | 0.091553 | 0.013733 | -0.01831 | -0.07782 | -0.082397 | 0.24261 | 0.19684 | 0.19226 | 0.21515 | 0.21057 | 0.13733 | 0.054932 | 0.26092 | 122.2275 | -0.059509 | 122.2321 | -0.004577 | 122.2137 | -122.2366 | -122.3099 | 0.10986 | 122.2092 | -0.004577 | 0.72784
3347.3281 | 122.4701 | -0.054932 | 122.2183 | -0.17372 | -0.045594 | 0.0023776 | 0.024005 | 0.00064947 | -0.011384 | -0.0032277 | -0.028351 | 0.0057379 | 0.061927 | 0.045773 | -0.018369 | 0.02634 | -0.0098523 | -0.068665 | -0.068665 | -0.018311 | 0.041199 | 0.17395 | 0.018311 | 0.086975 | 0.66834 | 122.1725 | -0.068665 | 122.1497 | 0.19684 | 0.15106 | 0.15106 | 0.036621 | -122.287 | -122.1771 | 0.22888 | 0.14191 | 0.073243 | 0.10529 | 0.036622 | -0.013733 | -0.045777 | -0.068665 | 0.25177 | 0.20599 | 0.20599 | 0.21973 | 0.21973 | 0.19226 | 0.05951 | 0.2655 | 122.2183 | -0.050354 | 122.2412 | -0.013733 | 122.2275 | -122.2366 | -122.287 | 0.096131 | 122.2046 | -0.013733 | 0.72327
3349.0938 | 122.3602 | -0.086975 | 122.2504 | -0.1432 | -0.041748 | 0.0030184 | 0.027423 | 0.00022207 | -0.0081796 | -0.0028005 | -0.1138 | 0.0076605 | 0.063423 | 0.054318 | -0.018156 | 0.028476 | -0.0057935 | -0.11902 | -0.009155 | -0.064087 | -0.082397 | -0.009155 | -0.15106 | -0.036621 | 0.37994 | 122.2137 | -0.10071 | 122.0764 | 0.045776 | -0.022888 | 0.054932 | 0.022888 | -122.2595 | -122.3328 | 0.07782 | 0.050354 | -0.064087 | 0.027466 | -0.086975 | -0.013733 | -0.036621 | -0.17395 | 0.13275 | 0.14191 | 0.064087 | 0.15564 | 0.07782 | 0.054932 | -0.01831 | 0.14648 | 122.1771 | 0.054932 | 122.3145 | 0.07782 | 122.3007 | -122.3145 | -122.3511 | 0.004578 | 122.1634 | -0.032044 | 0.46692
3350.7812 | 122.4152 | -0.068665 | 122.2321 | -0.15083 | -0.043671 | 0.002164 | 0.021655 | -0.0042639 | -0.0098886 | -0.0047231 | -0.06192 | 0.0057379 | 0.061286 | 0.044064 | -0.016233 | 0.028049 | -0.0077161 | -0.11902 | -0.073242 | -0.004578 | -0.022888 | 0.059509 | -0.064087 | 0.032043 | 0.48981 | 122.1725 | -0.073242 | 122.113 | 0.1236 | 0.082397 | 0.09613 | 0.064087 | -122.3053 | -122.2549 | 0.12817 | 0.10071 | 0.004578 | 0.036621 | -0.059509 | -0.004577 | -0.05951 | -0.11902 | 0.19226 | 0.16479 | 0.15106 | 0.16937 | 0.15564 | 0.064087 | -0.01831 | 0.19684 | 122.1863 | -0.068664 | 122.2458 | -0.004577 | 122.2412 | -122.2366 | -122.3053 | 0.045777 | 122.1817 | -0.050354 | 0.55847
3352.5469 | 122.3877 | -0.082397 | 122.2549 | -0.13557 | -0.04303 | 0.0025912 | 0.026141 | -0.00084593 | -0.010316 | -0.0066457 | -0.13211 | 0.0065923 | 0.064277 | 0.047909 | -0.019438 | 0.02933 | -0.0042981 | -0.091553 | -0.018311 | -0.050354 | -0.009155 | 0.064087 | -0.068665 | 0.027466 | 0.56305 | 122.1954 | -0.09613 | 122.0993 | 0.086975 | 0.032043 | 0.091553 | 0.032043 | -122.2733 | -122.2641 | 0.14648 | 0.10986 | 0.013732 | 0.07782 | -0.018311 | -0.013733 | -0.059509 | -0.15564 | 0.16937 | 0.17395 | 0.11444 | 0.18768 | 0.12817 | 0.11444 | 0.041199 | 0.1831 | 122.1954 | 0.032043 | 122.2916 | 0.064086 | 122.2778 | -122.3053 | -122.3511 | 0.073242 | 122.1817 | -0.009156 | 0.64545
3354.3125 | 122.438 | -0.064087 | 122.2275 | -0.097427 | -0.045166 | 0.00088223 | 0.023364 | -0.0027685 | -0.008607 | -0.0036551 | -0.019196 | 0.0068059 | 0.062568 | 0.044064 | -0.017515 | 0.025485 | -0.0068615 | -0.073242 | -0.064087 | -0.009155 | 0.059509 | 0.15564 | 0.027466 | 0.091553 | 0.67291 | 122.1588 | -0.082397 | 122.1542 | 0.16937 | 0.13733 | 0.14648 | 0.054932 | -122.2916 | -122.168 | 0.21973 | 0.15564 | 0.091553 | 0.10071 | 0.036621 | -0.01831 | -0.068665 | -0.073242 | 0.23346 | 0.21057 | 0.20142 | 0.22888 | 0.21973 | 0.16479 | 0.068664 | 0.25177 | 122.2366 | -0.054932 | 122.2412 | 0 | 122.2229 | -122.2366 | -122.3099 | 0.1236 | 122.2183 | -0.009155 | 0.737
3356.0781 | 122.3831 | -0.082397 | 122.2549 | -0.12794 | -0.044312 | 0.003232 | 0.025927 | 0.0049219 | -0.012025 | -0.0042959 | -0.12296 | 0.0074469 | 0.063209 | 0.050046 | -0.01602 | 0.026553 | -0.0062207 | -0.082397 | -0.022888 | -0.032043 | -0.022888 | 0.07782 | -0.07782 | 0.018311 | 0.56305 | 122.2275 | -0.091553 | 122.1039 | 0.11444 | 0.022888 | 0.07782 | 0.050354 | -122.2778 | -122.2778 | 0.16022 | 0.10071 | 0.004577 | 0.050354 | -0.045777 | -0.009156 | -0.027466 | -0.15106 | 0.19684 | 0.16022 | 0.10528 | 0.16937 | 0.11444 | 0.10986 | 0.009155 | 0.20599 | 122.1954 | 0.009155 | 122.319 | 0.059509 | 122.3099 | -122.287 | -122.3465 | 0.059509 | 122.1863 | 0 | 0.64545
3357.7656 | 122.4243 | -0.050354 | 122.2504 | -0.18898 | -0.041962 | 0.0017368 | 0.022723 | -0.0014867 | -0.0083932 | -0.0042959 | -0.052765 | 0.0053107 | 0.065345 | 0.049618 | -0.017301 | 0.027194 | -0.0023755 | -0.068665 | -0.059509 | 0.004578 | 0.022888 | 0.1236 | -0.018311 | 0.064087 | 0.51727 | 122.168 | -0.064087 | 122.1405 | 0.14648 | 0.11444 | 0.13275 | 0.054932 | -122.3099 | -122.2275 | 0.17395 | 0.11444 | 0.032043 | 0.059509 | -0.022889 | -0.013733 | -0.082397 | -0.10986 | 0.19684 | 0.18311 | 0.16479 | 0.19684 | 0.17853 | 0.11902 | 0.01831 | 0.21057 | 122.2046 | -0.064087 | 122.2321 | -0.009155 | 122.2183 | -122.2458 | -122.3145 | 0.073242 | 122.1909 | -0.018311 | 0.56763
3359.5312 | 122.406 | -0.059509 | 122.2046 | -0.21187 | -0.044098 | 0.001523 | 0.023364 | -0.0078955 | -0.012025 | -0.0028005 | -0.034454 | 0.0048833 | 0.062995 | 0.042996 | -0.016874 | 0.028903 | -0.0042981 | -0.10986 | -0.022888 | -0.013733 | -0.027466 | 0.073242 | -0.050354 | 0.032043 | 0.47607 | 122.1634 | -0.064087 | 122.0901 | 0.10529 | 0.064087 | 0.11902 | 0.045776 | -122.2275 | -122.2321 | 0.13275 | 0.091552 | 0.009155 | 0.045776 | -0.036621 | -0.004578 | -0.041199 | -0.11444 | 0.16479 | 0.17853 | 0.1236 | 0.18311 | 0.12817 | 0.086975 | -0.013733 | 0.16937 | 122.1542 | -0.009155 | 122.2275 | 0.036621 | 122.2229 | -122.2183 | -122.2687 | 0.032043 | 122.1497 | -0.050354 | 0.53558
3361.2969 | 122.4701 | -0.045776 | 122.2366 | -0.19661 | -0.043671 | 0.0040866 | 0.025714 | 0.0010767 | -0.0094614 | -0.00087794 | -0.092438 | 0.0053107 | 0.063209 | 0.051755 | -0.018369 | 0.02869 | -0.0040845 | -0.054932 | -0.050354 | -0.022888 | 0.036621 | 0.11902 | -0.041199 | 0.068665 | 0.52185 | 122.1588 | -0.045776 | 122.1634 | 0.17395 | 0.11444 | 0.16937 | 0.022888 | -122.287 | -122.2 | 0.16479 | 0.11444 | 0.004577 | 0.091553 | -0.018311 | 0 | -0.07782 | -0.073242 | 0.21973 | 0.21515 | 0.16022 | 0.21515 | 0.16022 | 0.14191 | 0.059509 | 0.21973 | 122.2092 | -0.027466 | 122.2046 | -0.004578 | 122.2046 | -122.2595 | -122.2824 | 0.082397 | 122.2092 | -0.009156 | 0.56763
3362.9844 | 122.4106 | -0.082397 | 122.2504 | -0.1432 | -0.044525 | 0.00088223 | 0.024005 | 0.00064947 | -0.01053 | -0.0015189 | -0.046661 | 0.0053107 | 0.063636 | 0.044491 | -0.017301 | 0.02634 | -0.0055799 | -0.10071 | -0.036621 | -0.009155 | -0.009155 | 0.082397 | -0.059509 | 0.064087 | 0.48065 | 122.168 | -0.07782 | 122.1176 | 0.11444 | 0.082397 | 0.1236 | 0.073242 | -122.287 | -122.2595 | 0.16479 | 0.14648 | 0.022888 | 0.073242 | -0.050354 | 0.004577 | -0.082397 | -0.13275 | 0.19684 | 0.20599 | 0.16479 | 0.20142 | 0.16022 | 0.091552 | 0 | 0.19226 | 122.1954 | -0.027466 | 122.2458 | 0.045776 | 122.2504 | -122.2595 | -122.3282 | 0.073242 | 122.2 | -0.018311 | 0.56305
3364.75 | 122.319 | -0.10529 | 122.2504 | -0.18898 | -0.041962 | 0.003873 | 0.028918 | 0.0021447 | -0.010102 | -0.0045095 | -0.14127 | 0.0063787 | 0.062782 | 0.050259 | -0.018583 | 0.029544 | -0.0066479 | -0.11902 | -0.004578 | -0.036621 | -0.082397 | -0.036621 | -0.14648 | -0.054932 | 0.3891 | 122.2 | -0.10986 | 122.0398 | -0.004578 | -0.073242 | 0.022888 | 0.068665 | -122.2549 | -122.3328 | 0.068665 | 0.050354 | -0.041198 | -0.018311 | -0.10986 | -0.004577 | -0.050354 | -0.21057 | 0.10071 | 0.12817 | 0.032044 | 0.13275 | 0.036621 | 0 | -0.045776 | 0.10529 | 122.1497 | 0.032043 | 122.3099 | 0.10071 | 122.3053 | -122.287 | -122.3602 | 0.022889 | 122.1451 | -0.013733 | 0.49438
3366.5 | 122.3465 | -0.10071 | 122.2778 | -0.18135 | -0.044525 | 0.0047274 | 0.024859 | 0.0027857 | -0.010102 | -0.0070731 | -0.1077 | 0.0072333 | 0.064918 | 0.052823 | -0.017942 | 0.029117 | -0.0042981 | -0.12817 | -0.022888 | -0.054932 | -0.091553 | -0.027466 | -0.15564 | -0.045776 | 0.38452 | 122.1817 | -0.091553 | 122.0673 | 0.032043 | -0.032043 | 0.054932 | 0.045776 | -122.3007 | -122.3694 | 0.073242 | 0.054932 | -0.054932 | 0.009156 | -0.10071 | 0.009155 | -0.09613 | -0.21057 | 0.13275 | 0.15564 | 0.068665 | 0.14649 | 0.05951 | 0.027466 | -0.036621 | 0.1236 | 122.1588 | 0.032044 | 122.2733 | 0.07782 | 122.2824 | -122.3328 | -122.3694 | 0.009155 | 122.168 | -0.027466 | 0.48523
3368.2656 | 122.4014 | -0.073242 | 122.2366 | -0.11269 | -0.040467 | 0.0013094 | 0.024218 | -0.00020513 | -0.007966 | -0.0047231 | -0.10464 | 0.0057379 | 0.065132 | 0.052395 | -0.017088 | 0.026981 | -0.0075025 | -0.1236 | 0.009155 | -0.041199 | -0.073242 | 0.013733 | -0.13733 | -0.022888 | 0.40283 | 122.1771 | -0.10529 | 122.0993 | 0.064087 | 0.013733 | 0.086975 | 0.032043 | -122.2275 | -122.3099 | 0.086975 | 0.050354 | -0.064087 | 0.018311 | -0.09613 | -0.032044 | -0.059509 | -0.13733 | 0.13733 | 0.16022 | 0.086975 | 0.19226 | 0.11902 | 0.054932 | -0.032043 | 0.16937 | 122.2046 | 0.050354 | 122.2824 | 0.082397 | 122.2504 | -122.2778 | -122.3419 | 0 | 122.1725 | -0.050354 | 0.47607
3369.9688 | 122.4747 | -0.059509 | 122.2549 | -0.1432 | -0.043457 | 0.0036594 | 0.022296 | -0.0025549 | -0.012666 | -0.0025869 | -0.031403 | 0.0044561 | 0.064491 | 0.044491 | -0.015379 | 0.025912 | -0.0049389 | -0.068665 | -0.050354 | -0.022888 | 0.032043 | 0.16022 | 0.036621 | 0.10529 | 0.68665 | 122.1451 | -0.064087 | 122.1542 | 0.17853 | 0.15106 | 0.15106 | 0.036621 | -122.3053 | -122.2229 | 0.21973 | 0.16479 | 0.09613 | 0.12817 | 0.059509 | -0.004578 | -0.10986 | -0.10071 | 0.23804 | 0.21057 | 0.21057 | 0.21515 | 0.21515 | 0.1831 | 0.054931 | 0.24261 | 122.2183 | -0.027466 | 122.2092 | 0.009155 | 122.2046 | -122.2778 | -122.319 | 0.091552 | 122.2137 | -0.009156 | 0.74616
3371.7344 | 122.3877 | -0.082397 | 122.2687 | -0.10506 | -0.044098 | 0.0047274 | 0.024218 | -0.00041873 | -0.010316 | -0.0023733 | -0.09549 | 0.0063787 | 0.062782 | 0.047268 | -0.019438 | 0.027408 | -0.0077161 | -0.09613 | -0.018311 | -0.036621 | -0.036621 | 0.068665 | -0.073242 | 0.018311 | 0.56763 | 122.2137 | -0.086975 | 122.1039 | 0.10529 | 0.036621 | 0.09613 | 0.045776 | -122.287 | -122.3053 | 0.15106 | 0.10071 | 0.009155 | 0.054932 | -0.036621 | -0.004578 | -0.054932 | -0.16479 | 0.18768 | 0.17853 | 0.11902 | 0.1831 | 0.1236 | 0.10529 | 0 | 0.19226 | 122.1909 | 0.01831 | 122.3007 | 0.064086 | 122.2961 | -122.3053 | -122.3557 | 0.045776 | 122.1863 | -0.013733 | 0.65002
3373.4844 | 122.4564 | -0.059509 | 122.2321 | -0.13557 | -0.043671 | 0.0028048 | 0.019946 | -0.0061865 | -0.01117 | -0.0015189 | -0.0008851 | 0.0040289 | 0.0615 | 0.045346 | -0.016447 | 0.028262 | -0.0032299 | -0.10529 | -0.041199 | -0.036621 | -0.009155 | 0.09613 | -0.022888 | 0.064087 | 0.5722 | 122.1771 | -0.068665 | 122.1451 | 0.16937 | 0.13275 | 0.15106 | 0.022888 | -122.2733 | -122.2412 | 0.15564 | 0.1236 | 0.036621 | 0.10071 | 0.013733 | -0.009156 | -0.054932 | -0.086975 | 0.22888 | 0.21057 | 0.19226 | 0.21973 | 0.20142 | 0.13275 | 0.027466 | 0.23804 | 122.2137 | -0.004578 | 122.2458 | 0.01831 | 122.2366 | -122.2687 | -122.3007 | 0.050354 | 122.2046 | -0.045777 | 0.63171
3375.2656 | 122.406 | -0.054932 | 122.2412 | -0.17372 | -0.044312 | 0.0019504 | 0.021869 | -0.0034095 | -0.010102 | -0.0053641 | -0.022247 | 0.0046697 | 0.065132 | 0.0462 | -0.01666 | 0.02933 | -0.0013073 | -0.10071 | -0.036621 | -0.018311 | -0.027466 | 0.082397 | -0.050354 | 0.054932 | 0.46692 | 122.1634 | -0.07782 | 122.1085 | 0.10986 | 0.068665 | 0.10986 | 0.036621 | -122.2778 | -122.2687 | 0.13733 | 0.10986 | 0.004578 | 0.073243 | -0.032043 | -0.022888 | -0.07782 | -0.13275 | 0.16479 | 0.16479 | 0.1236 | 0.18768 | 0.14649 | 0.10071 | -0.009155 | 0.18768 | 122.1863 | -0.01831 | 122.2412 | 0.018311 | 122.2183 | -122.2595 | -122.319 | 0.027466 | 122.1634 | -0.045776 | 0.52185
3376.9688 | 122.374 | -0.07782 | 122.2229 | -0.097427 | -0.042816 | -0.00082677 | 0.026355 | 0.0021447 | -0.010743 | -0.00087794 | -0.11685 | 0.0065923 | 0.062782 | 0.051114 | -0.017088 | 0.028049 | -0.0066479 | -0.09613 | -0.018311 | -0.041199 | -0.032043 | 0.064087 | -0.073242 | 0.013733 | 0.53101 | 122.1954 | -0.086975 | 122.0856 | 0.073242 | 0.022888 | 0.082397 | 0.036621 | -122.2412 | -122.2549 | 0.14191 | 0.091553 | 0.004578 | 0.054932 | -0.032043 | -0.009155 | -0.027465 | -0.13733 | 0.15106 | 0.16022 | 0.10071 | 0.16937 | 0.10986 | 0.10529 | 0.009156 | 0.16022 | 122.1725 | 0.022888 | 122.2824 | 0.059509 | 122.2733 | -122.2641 | -122.3099 | 0.045777 | 122.1634 | -0.01831 | 0.60883
3378.7188 | 122.406 | -0.082397 | 122.2412 | -0.1432 | -0.044525 | 0.00024143 | 0.022296 | -0.0042639 | -0.010957 | -0.0030141 | -0.022247 | 0.0040289 | 0.064063 | 0.053677 | -0.017729 | 0.027621 | -0.0051525 | -0.07782 | -0.032043 | -0.018311 | 0.018311 | 0.12817 | 0.009155 | 0.09613 | 0.64087 | 122.168 | -0.064087 | 122.1268 | 0.14191 | 0.091553 | 0.11444 | 0.064086 | -122.2733 | -122.2229 | 0.21057 | 0.17853 | 0.091552 | 0.11444 | 0.027466 | 0.01831 | -0.073242 | -0.11444 | 0.2243 | 0.19684 | 0.17395 | 0.17853 | 0.15564 | 0.14649 | 0.036622 | 0.20599 | 122.1909 | -0.013732 | 122.2321 | 0.050354 | 122.2504 | -122.2595 | -122.3053 | 0.10071 | 122.2092 | 0.004577 | 0.72327
3380.4844 | 122.374 | -0.082397 | 122.2687 | -0.11269 | -0.043244 | 0.0019504 | 0.027209 | 0.0023585 | -0.013307 | -0.0023733 | -0.11075 | 0.0080877 | 0.064491 | 0.053464 | -0.018369 | 0.028049 | -0.0068615 | -0.082397 | -0.027466 | -0.050354 | -0.013733 | 0.059509 | -0.059509 | 0.009155 | 0.55847 | 122.2046 | -0.086975 | 122.0993 | 0.10529 | 0.041199 | 0.073242 | 0.032043 | -122.2961 | -122.2824 | 0.14191 | 0.091552 | 0.022888 | 0.059509 | -0.009155 | -0.004578 | -0.064087 | -0.16937 | 0.18768 | 0.15564 | 0.1236 | 0.16022 | 0.12817 | 0.10986 | 0.036621 | 0.19226 | 122.1863 | 0.022888 | 122.2916 | 0.054931 | 122.287 | -122.319 | -122.3557 | 0.068664 | 122.1817 | 0 | 0.64087
3382.25 | 122.4106 | -0.082397 | 122.2275 | -0.16609 | -0.042816 | 0.0013094 | 0.021869 | -0.0012731 | -0.010743 | -0.0057913 | -0.013092 | 0.0053107 | 0.062354 | 0.039364 | -0.016233 | 0.027408 | -0.0038709 | -0.11444 | -0.050354 | -0.032043 | -0.041199 | 0.054932 | -0.059509 | 0.041199 | 0.4715 | 122.1863 | -0.068665 | 122.0993 | 0.10986 | 0.068665 | 0.10529 | 0.050354 | -122.2778 | -122.2687 | 0.13733 | 0.1236 | 0.022888 | 0.073242 | -0.027466 | 0.013732 | -0.041199 | -0.12817 | 0.19226 | 0.18768 | 0.15106 | 0.17395 | 0.13733 | 0.086975 | -0.009156 | 0.17853 | 122.168 | -0.018311 | 122.2549 | 0.032043 | 122.2687 | -122.2595 | -122.2961 | 0.041198 | 122.1817 | -0.032044 | 0.55389
3384.0156 | 122.3328 | -0.11444 | 122.2733 | -0.15846 | -0.041748 | 0.003232 | 0.0255 | 0.0032129 | -0.011384 | -0.0032277 | -0.1077 | 0.0076605 | 0.063423 | 0.050686 | -0.017729 | 0.027835 | -0.0036573 | -0.13733 | -0.009155 | -0.050354 | -0.10071 | -0.050354 | -0.17395 | -0.073242 | 0.3891 | 122.1909 | -0.10071 | 122.0215 | 0.013733 | -0.054932 | 0.041199 | 0.064087 | -122.2824 | -122.374 | 0.064087 | 0.041199 | -0.059509 | -0.022888 | -0.1236 | 0.013733 | -0.082397 | -0.25177 | 0.12817 | 0.15564 | 0.059509 | 0.14191 | 0.045776 | 0 | -0.050354 | 0.11444 | 122.1222 | 0.041199 | 122.2916 | 0.10529 | 122.3053 | -122.3236 | -122.374 | 0.013733 | 122.1359 | -0.022888 | 0.50354
3385.7188 | 122.3602 | -0.09613 | 122.2549 | -0.13557 | -0.042176 | 0.0030184 | 0.024218 | 0.0017175 | -0.010743 | -0.0030141 | -0.11685 | 0.0072333 | 0.064918 | 0.051541 | -0.016447 | 0.028262 | -0.0038709 | -0.09613 | -0.018311 | -0.045776 | -0.050354 | 0.045776 | -0.091553 | 0 | 0.48065 | 122.2 | -0.09613 | 122.0718 | 0.036621 | -0.022888 | 0.045776 | 0.050354 | -122.2733 | -122.3053 | 0.14191 | 0.09613 | 0.004577 | 0.045776 | -0.045777 | 0 | -0.054932 | -0.18311 | 0.13275 | 0.14191 | 0.073242 | 0.14191 | 0.073242 | 0.091552 | -0.004578 | 0.13275 | 122.168 | 0.027465 | 122.2961 | 0.077819 | 122.2961 | -122.3007 | -122.3511 | 0.045776 | 122.168 | 0 | 0.57678
3387.4688 | 122.4106 | -0.064087 | 122.2321 | -0.10506 | -0.044525 | 0.001523 | 0.022509 | 0.0019311 | -0.011384 | -0.0038687 | -0.016144 | 0.0059515 | 0.063209 | 0.042996 | -0.014951 | 0.027194 | -0.0045117 | -0.11444 | -0.054932 | -0.009155 | -0.018311 | 0.073242 | -0.045776 | 0.045776 | 0.50354 | 122.1817 | -0.082397 | 122.0993 | 0.10986 | 0.086975 | 0.10529 | 0.054932 | -122.287 | -122.2504 | 0.13733 | 0.10986 | 0.018311 | 0.054931 | -0.036621 | -0.01831 | -0.050354 | -0.13275 | 0.17395 | 0.16937 | 0.15106 | 0.18768 | 0.16937 | 0.082397 | -0.009156 | 0.19226 | 122.1817 | -0.045777 | 122.2641 | 0.009155 | 122.2458 | -122.2412 | -122.3145 | 0.045776 | 122.1634 | -0.050354 | 0.56763
3389.2344 | 122.4243 | -0.059509 | 122.2458 | -0.17372 | -0.042816 | 0.0010958 | 0.023791 | 0.00022207 | -0.010743 | -0.0047231 | -0.049713 | 0.0057379 | 0.062995 | 0.042142 | -0.017729 | 0.026126 | -0.0040845 | -0.064087 | -0.059509 | -0.009155 | 0.027466 | 0.13733 | -0.013733 | 0.068665 | 0.53101 | 122.1405 | -0.068665 | 122.1313 | 0.1236 | 0.10529 | 0.14648 | 0.050354 | -122.3053 | -122.2183 | 0.19684 | 0.12817 | 0.045776 | 0.07782 | -0.004578 | -0.009156 | -0.10529 | -0.11444 | 0.1831 | 0.20599 | 0.16479 | 0.21515 | 0.17395 | 0.14648 | 0.036621 | 0.19226 | 122.2 | -0.050354 | 122.2092 | 0 | 122.2 | -122.2549 | -122.3145 | 0.086975 | 122.1909 | -0.004578 | 0.59052
3391 | 122.4243 | -0.054932 | 122.2229 | -0.18898 | -0.041962 | 0.0034456 | 0.022509 | 0.00064947 | -0.012025 | -0.0019461 | -0.028351 | 0.0072333 | 0.063209 | 0.038724 | -0.019651 | 0.02634 | -0.0040845 | -0.11902 | -0.050354 | -0.009155 | 0 | 0.086975 | -0.054932 | 0.050354 | 0.48065 | 122.1497 | -0.073242 | 122.1085 | 0.10529 | 0.073242 | 0.10986 | 0.045777 | -122.2733 | -122.2229 | 0.14191 | 0.10529 | 0 | 0.059509 | -0.045777 | -0.01831 | -0.073242 | -0.11444 | 0.16022 | 0.16479 | 0.12817 | 0.18311 | 0.14648 | 0.09613 | 0.009155 | 0.17853 | 122.1817 | -0.041199 | 122.2229 | 0.004578 | 122.2046 | -122.2321 | -122.2961 | 0.054932 | 122.1634 | -0.064087 | 0.53558
3392.7031 | 122.4838 | -0.059509 | 122.2229 | -0.11269 | -0.04538 | 0.0017368 | 0.019946 | 0.00043587 | -0.01117 | -0.0017325 | 0.014374 | 0.0048833 | 0.065132 | 0.040433 | -0.017515 | 0.02634 | -0.0066479 | -0.07782 | -0.041199 | -0.027466 | 0.041199 | 0.14648 | 0.013733 | 0.11444 | 0.6546 | 122.1451 | -0.07782 | 122.168 | 0.21515 | 0.14648 | 0.15564 | 0.032043 | -122.2641 | -122.1817 | 0.20599 | 0.17395 | 0.073242 | 0.14191 | 0.041199 | -0.018311 | -0.077819 | -0.054931 | 0.27466 | 0.21515 | 0.20599 | 0.23346 | 0.2243 | 0.17395 | 0.068665 | 0.29297 | 122.2458 | -0.013733 | 122.2229 | 0.01831 | 122.2046 | -122.2504 | -122.3007 | 0.10071 | 122.2275 | -0.018311 | 0.71411
3394.4688 | 122.3694 | -0.11444 | 122.2595 | -0.074539 | -0.044098 | 0.0019504 | 0.024646 | 8.47e-06 | -0.012239 | -0.0038687 | -0.092438 | 0.0059515 | 0.06385 | 0.048977 | -0.019438 | 0.026767 | -0.0045117 | -0.15106 | -0.018311 | -0.054932 | -0.07782 | -0.018311 | -0.11902 | -0.018311 | 0.5127 | 122.2046 | -0.10071 | 122.0444 | 0.059509 | -0.009155 | 0.041199 | 0.059509 | -122.2778 | -122.3373 | 0.09613 | 0.09613 | -0.004578 | 0.036621 | -0.064087 | 0.013733 | -0.054931 | -0.21515 | 0.17395 | 0.15564 | 0.10529 | 0.14191 | 0.091553 | 0.036621 | -0.022888 | 0.16022 | 122.1451 | 0.036621 | 122.3053 | 0.09613 | 122.319 | -122.3145 | -122.3602 | 0.036621 | 122.1588 | -0.036621 | 0.62714
3396.1562 | 122.4106 | -0.082397 | 122.2504 | -0.18135 | -0.044739 | 0.0019504 | 0.024646 | 0.0021447 | -0.0092478 | -0.0040823 | -0.01004 | 0.0044561 | 0.063636 | 0.03851 | -0.017729 | 0.025058 | -0.0049389 | -0.10529 | -0.050354 | -0.009155 | -0.009155 | 0.09613 | -0.059509 | 0.059509 | 0.48981 | 122.168 | -0.073242 | 122.1222 | 0.10986 | 0.091553 | 0.1236 | 0.073242 | -122.3007 | -122.2595 | 0.17853 | 0.14191 | 0.022888 | 0.068664 | -0.050354 | 0.009155 | -0.082397 | -0.12817 | 0.19226 | 0.20599 | 0.17395 | 0.19684 | 0.16479 | 0.10528 | 0 | 0.18311 | 122.1954 | -0.041199 | 122.2412 | 0.032043 | 122.2504 | -122.2595 | -122.3236 | 0.073242 | 122.2046 | -0.022889 | 0.5722
3397.9062 | 122.4197 | -0.064087 | 122.2458 | -0.18898 | -0.045807 | 0.00024143 | 0.0208 | 0.0047083 | -0.010316 | -0.00087794 | -0.016144 | 0.0055243 | 0.065132 | 0.050686 | -0.016233 | 0.025699 | -0.0047253 | -0.11444 | -0.041199 | -0.009155 | -0.036621 | 0.064087 | -0.068665 | 0.050354 | 0.49439 | 122.1634 | -0.054932 | 122.113 | 0.09613 | 0.068665 | 0.10071 | 0.054932 | -122.287 | -122.2824 | 0.12817 | 0.11444 | -0.004578 | 0.059509 | -0.05951 | 0.009155 | -0.082398 | -0.13275 | 0.16022 | 0.1648 | 0.13275 | 0.15564 | 0.1236 | 0.073242 | -0.027466 | 0.15106 | 122.168 | -0.032044 | 122.2183 | 0.022888 | 122.2275 | -122.2549 | -122.3007 | 0.027466 | 122.1771 | -0.050354 | 0.55847
3399.6094 | 122.4426 | -0.036621 | 122.2458 | -0.15083 | -0.042389 | 0.0025912 | 0.025714 | -0.00084593 | -0.0094614 | -0.0034415 | -0.077179 | 0.0057379 | 0.063636 | 0.049191 | -0.018797 | 0.028049 | -0.0053661 | -0.10529 | -0.032043 | -0.032043 | -0.013733 | 0.068665 | -0.07782 | 0.027466 | 0.48981 | 122.1634 | -0.082397 | 122.1588 | 0.15106 | 0.091553 | 0.16479 | 0.004578 | -122.2778 | -122.2595 | 0.10529 | 0.064087 | -0.041199 | 0.059509 | -0.045777 | -0.045776 | -0.082398 | -0.086976 | 0.18768 | 0.20142 | 0.12817 | 0.24719 | 0.17395 | 0.10071 | 0.01831 | 0.23346 | 122.2412 | 0 | 122.2458 | 0.004578 | 122.2 | -122.2778 | -122.3282 | 0.022888 | 122.1954 | -0.068665 | 0.52643
3401.3594 | 122.4518 | -0.064087 | 122.2183 | -0.18898 | -0.042389 | 0.0019504 | 0.021655 | 0.00086307 | -0.009675 | -0.0053641 | -0.052765 | 0.0074469 | 0.063423 | 0.050473 | -0.01666 | 0.02634 | -0.0070751 | -0.068665 | -0.045776 | 0.004578 | 0.045776 | 0.1236 | -0.009155 | 0.059509 | 0.54016 | 122.1725 | -0.059509 | 122.1725 | 0.14648 | 0.11902 | 0.15106 | 0.068665 | -122.2641 | -122.1725 | 0.18768 | 0.1236 | 0.054932 | 0.054931 | -0.013733 | 0.004578 | -0.045777 | -0.045777 | 0.21057 | 0.21515 | 0.18311 | 0.21057 | 0.17853 | 0.11902 | 0.041198 | 0.20599 | 122.2321 | -0.050354 | 122.2321 | 0.018311 | 122.2366 | -122.2137 | -122.2778 | 0.10986 | 122.2366 | -0.004578 | 0.60425
3403.1094 | 122.4655 | -0.050354 | 122.2321 | -0.15846 | -0.04303 | 0.0025912 | 0.027636 | 0.00086307 | -0.01117 | -0.0023733 | -0.098541 | 0.0072333 | 0.064277 | 0.055813 | -0.018369 | 0.028262 | -0.0077161 | -0.10071 | -0.032043 | -0.027466 | 0.004578 | 0.086975 | -0.041199 | 0.050354 | 0.49896 | 122.1634 | -0.073242 | 122.1588 | 0.15564 | 0.082397 | 0.17395 | 0.022888 | -122.2641 | -122.2275 | 0.13733 | 0.10071 | 0.009155 | 0.07782 | -0.013733 | -0.022888 | -0.068665 | -0.073243 | 0.20599 | 0.2243 | 0.13275 | 0.24719 | 0.15564 | 0.11444 | 0.032044 | 0.22888 | 122.2321 | -0.004577 | 122.2366 | 0.018311 | 122.2137 | -122.2595 | -122.3053 | 0.054932 | 122.2092 | -0.050354 | 0.54932
3404.875 | 122.3877 | -0.091553 | 122.2641 | -0.12032 | -0.043671 | 0.0034456 | 0.0255 | 0.00022207 | -0.010957 | -2.3544e-05 | -0.10464 | 0.0078741 | 0.064491 | 0.050259 | -0.017729 | 0.029117 | -0.0079297 | -0.11902 | -0.013733 | -0.036621 | -0.045776 | 0.027466 | -0.073242 | 0.004578 | 0.56305 | 122.1817 | -0.086975 | 122.0764 | 0.086975 | 0.036621 | 0.073242 | 0.054932 | -122.2778 | -122.3099 | 0.11902 | 0.096131 | 0.018311 | 0.041199 | -0.036621 | 0.004578 | -0.082397 | -0.18768 | 0.17853 | 0.16479 | 0.12817 | 0.16022 | 0.1236 | 0.064087 | -0.009155 | 0.17395 | 122.1634 | 0.022888 | 122.2687 | 0.07782 | 122.2733 | -122.3007 | -122.3511 | 0.045777 | 122.168 | -0.027466 | 0.6546
3406.6562 | 122.4335 | -0.064087 | 122.2641 | -0.17372 | -0.04538 | 0.00088223 | 0.021655 | -0.0029821 | -0.01053 | -0.0032277 | -0.031403 | 0.0057379 | 0.063636 | 0.050686 | -0.01666 | 0.027621 | -0.0023755 | -0.11902 | -0.050354 | -0.022888 | -0.022888 | 0.068665 | -0.054932 | 0.050354 | 0.4715 | 122.168 | -0.07782 | 122.0947 | 0.10986 | 0.064087 | 0.10529 | 0.041199 | -122.3145 | -122.287 | 0.13275 | 0.11444 | 0.009155 | 0.073242 | -0.032044 | -0.013733 | -0.09613 | -0.16937 | 0.17395 | 0.16937 | 0.12817 | 0.18311 | 0.14191 | 0.091553 | 0 | 0.18768 | 122.1725 | -0.027466 | 122.2458 | 0.013733 | 122.2321 | -122.287 | -122.3419 | 0.041199 | 122.1588 | -0.054932 | 0.53558
3408.3438 | 122.3969 | -0.059509 | 122.2549 | -0.15083 | -0.042603 | 0.002164 | 0.022296 | 0.00064947 | -0.01053 | -0.0066457 | -0.019196 | 0.0059515 | 0.060432 | 0.050473 | -0.018156 | 0.025912 | -0.0087841 | -0.10071 | -0.036621 | -0.004578 | -0.022888 | 0.068665 | -0.054932 | 0.041199 | 0.49439 | 122.1634 | -0.068665 | 122.1039 | 0.11902 | 0.059509 | 0.10071 | 0.054931 | -122.2916 | -122.2778 | 0.12817 | 0.10071 | 0.004577 | 0.045777 | -0.050354 | -0.009156 | -0.091553 | -0.15106 | 0.17853 | 0.16022 | 0.11902 | 0.16937 | 0.12817 | 0.073243 | -0.01831 | 0.18768 | 122.1725 | -0.032043 | 122.2321 | 0.022888 | 122.2229 | -122.2595 | -122.3236 | 0.036621 | 122.1634 | -0.041199 | 0.55389
3410.1094 | 122.3511 | -0.10071 | 122.2961 | -0.1432 | -0.044098 | 0.002164 | 0.022509 | 8.47e-06 | -0.012452 | -0.0010915 | -0.055817 | 0.0059515 | 0.062354 | 0.049191 | -0.017942 | 0.027835 | -0.0015209 | -0.1236 | 0.004578 | -0.036621 | -0.068665 | 0.032043 | -0.064087 | -0.004578 | 0.57678 | 122.1863 | -0.07782 | 122.0306 | 0.059509 | 0.009155 | 0.022888 | 0.064087 | -122.2916 | -122.3648 | 0.13275 | 0.09613 | 0.036621 | 0.032043 | -0.027466 | 0.022888 | -0.10986 | -0.2655 | 0.16022 | 0.1236 | 0.10986 | 0.10071 | 0.086975 | 0.068664 | -0.032044 | 0.13733 | 122.1085 | 0.041199 | 122.2641 | 0.10529 | 122.287 | -122.3328 | -122.374 | 0.032043 | 122.1313 | -0.022888 | 0.67749
3411.8125 | 122.3145 | -0.10071 | 122.2641 | -0.15083 | -0.044525 | 0.0034456 | 0.026141 | 0.0036401 | -0.010102 | -0.0049367 | -0.1199 | 0.0078741 | 0.062141 | 0.051114 | -0.01666 | 0.027835 | -0.0045117 | -0.11902 | -0.022888 | -0.050354 | -0.09613 | -0.032043 | -0.16022 | -0.050354 | 0.37994 | 122.2137 | -0.10529 | 122.0215 | 0.009155 | -0.045776 | 0.022888 | 0.050354 | -122.287 | -122.3602 | 0.068665 | 0.050354 | -0.059509 | 0 | -0.10986 | -0.004578 | -0.050354 | -0.24262 | 0.10986 | 0.1236 | 0.054932 | 0.12817 | 0.05951 | 0.018311 | -0.045776 | 0.11444 | 122.1268 | 0.027466 | 122.319 | 0.07782 | 122.3145 | -122.3145 | -122.3694 | 0.004578 | 122.1222 | -0.018311 | 0.48065
3413.5781 | 122.3373 | -0.10986 | 122.2412 | -0.097427 | -0.04538 | 0.00024143 | 0.022082 | -0.0019141 | -0.011811 | -0.0047231 | -0.037506 | 0.0061651 | 0.066627 | 0.047268 | -0.017515 | 0.027835 | -0.0062207 | -0.16022 | -0.027466 | -0.054932 | -0.07782 | 0 | -0.09613 | -0.004578 | 0.54016 | 122.2275 | -0.10529 | 122.0261 | 0.054932 | -0.009155 | 0.022888 | 0.054931 | -122.2687 | -122.319 | 0.10986 | 0.10529 | 0.013733 | 0.050354 | -0.041198 | 0.004577 | -0.013733 | -0.21515 | 0.16479 | 0.13275 | 0.10071 | 0.12817 | 0.096131 | 0.054932 | -0.022888 | 0.16022 | 122.1313 | 0.027466 | 122.3328 | 0.082397 | 122.3373 | -122.2961 | -122.3465 | 0.032043 | 122.1359 | -0.050354 | 0.65002
3415.3438 | 122.3373 | -0.10071 | 122.2778 | -0.11269 | -0.043671 | -0.00039957 | 0.021869 | -0.00063233 | -0.011598 | -0.0062185 | -0.052765 | 0.0059515 | 0.064918 | 0.048337 | -0.016233 | 0.027194 | -0.0013073 | -0.15106 | -0.004578 | -0.073242 | -0.086975 | 0.004578 | -0.091553 | -0.018311 | 0.53558 | 122.2 | -0.07782 | 122.0306 | 0.041199 | -0.009155 | 0.036621 | 0.027466 | -122.2824 | -122.3648 | 0.10529 | 0.082397 | 0.009155 | 0.054931 | -0.018311 | 0.022888 | -0.07782 | -0.24719 | 0.14191 | 0.13733 | 0.091553 | 0.11444 | 0.068665 | 0.07782 | -0.013733 | 0.11902 | 122.1085 | 0.068664 | 122.2778 | 0.09613 | 122.3007 | -122.3511 | -122.3557 | 0.013733 | 122.1313 | -0.050354 | 0.63629
3417.1094 | 122.374 | -0.091553 | 122.2778 | -0.17372 | -0.040894 | 0.002164 | 0.024005 | -0.00063233 | -0.008607 | -0.0036551 | -0.10464 | 0.0072333 | 0.063636 | 0.053036 | -0.017301 | 0.028903 | -0.0021619 | -0.07782 | -0.027466 | -0.050354 | -0.032043 | 0.059509 | -0.064087 | 0.022888 | 0.55389 | 122.1909 | -0.091553 | 122.0947 | 0.10071 | 0.036621 | 0.086975 | 0.041199 | -122.3053 | -122.3099 | 0.15106 | 0.11444 | 0.027466 | 0.073242 | -0.013733 | 0 | -0.086975 | -0.1831 | 0.19226 | 0.17853 | 0.12817 | 0.17853 | 0.12817 | 0.10986 | 0.018311 | 0.19226 | 122.1863 | 0.022888 | 122.2824 | 0.064087 | 122.2824 | -122.3282 | -122.3694 | 0.05951 | 122.1863 | 0.013733 | 0.64545
3418.8125 | 122.4564 | -0.050354 | 122.2366 | -0.15083 | -0.04303 | 0.0043002 | 0.023364 | 0.0017175 | -0.009675 | -0.0038687 | -0.064972 | 0.0063787 | 0.064063 | 0.049832 | -0.01901 | 0.026126 | -0.0023755 | -0.054932 | -0.041199 | -0.013733 | 0.041199 | 0.13733 | -0.022888 | 0.068665 | 0.54474 | 122.1359 | -0.032043 | 122.1725 | 0.16937 | 0.11444 | 0.16479 | 0.036621 | -122.2778 | -122.1954 | 0.18768 | 0.11902 | 0.027466 | 0.082398 | -0.009155 | 0.018311 | -0.10071 | -0.064087 | 0.21973 | 0.21515 | 0.16479 | 0.19684 | 0.14648 | 0.15106 | 0.054932 | 0.20142 | 122.2046 | -0.027466 | 122.168 | 0.009155 | 122.1863 | -122.2504 | -122.2687 | 0.091553 | 122.2229 | -0.004578 | 0.59509
3420.5781 | 122.3694 | -0.10529 | 122.287 | -0.10506 | -0.045807 | 0.00088223 | 0.022723 | 0.0019311 | -0.0094614 | -0.0017325 | -0.04361 | 0.0044561 | 0.062782 | 0.03851 | -0.017515 | 0.02634 | -0.0057935 | -0.09613 | -0.054932 | -0.027466 | -0.022888 | 0.07782 | -0.018311 | 0.050354 | 0.60883 | 122.1725 | -0.091553 | 122.0444 | 0.07782 | 0.032043 | 0.041199 | 0.07782 | -122.3419 | -122.3099 | 0.18311 | 0.15564 | 0.086975 | 0.07782 | 0.009155 | 0.013733 | -0.11444 | -0.24261 | 0.18311 | 0.14649 | 0.13733 | 0.13275 | 0.1236 | 0.10529 | 0.004578 | 0.16937 | 122.1359 | -0.027466 | 122.2641 | 0.050354 | 122.2778 | -122.3145 | -122.3785 | 0.082398 | 122.1497 | 0.009156 | 0.71411
3422.3281 | 122.319 | -0.091553 | 122.2824 | -0.12794 | -0.041535 | 0.0023776 | 0.024646 | 0.0025721 | -0.009675 | -0.0036551 | -0.12601 | 0.0072333 | 0.065345 | 0.0462 | -0.018369 | 0.027835 | -0.0034435 | -0.11444 | -0.009155 | -0.054932 | -0.07782 | -0.013733 | -0.15106 | -0.054932 | 0.41199 | 122.2137 | -0.082397 | 122.0352 | 0.018311 | -0.045776 | 0.032043 | 0.036621 | -122.2916 | -122.3602 | 0.07782 | 0.036621 | -0.059509 | 0 | -0.09613 | 0.009156 | -0.068665 | -0.24719 | 0.10986 | 0.1236 | 0.045777 | 0.11444 | 0.036621 | 0.041199 | -0.022888 | 0.10071 | 122.1176 | 0.045777 | 122.2961 | 0.082398 | 122.3053 | -122.3373 | -122.3648 | 0.013733 | 122.1268 | -0.022888 | 0.50354
3424.0938 | 122.3373 | -0.10529 | 122.2595 | -0.12032 | -0.042816 | 0.0030184 | 0.025287 | -0.0027685 | -0.010743 | -0.0036551 | -0.028351 | 0.0091559 | 0.064277 | 0.042569 | -0.01666 | 0.027621 | -0.0038709 | -0.15106 | -0.018311 | -0.032043 | -0.086975 | 0.027466 | -0.082397 | 0.013733 | 0.56763 | 122.2092 | -0.10071 | 122.0261 | 0.045776 | 0.004578 | 0.018311 | 0.073243 | -122.2778 | -122.3465 | 0.13275 | 0.11902 | 0.022889 | 0.045776 | -0.050354 | 0.004578 | -0.050354 | -0.23346 | 0.15106 | 0.1236 | 0.10986 | 0.11902 | 0.10529 | 0.059509 | -0.054932 | 0.14648 | 122.1268 | 0.013732 | 122.3099 | 0.086975 | 122.3145 | -122.2916 | -122.3602 | 0.018311 | 122.1313 | -0.045776 | 0.67291
3425.8594 | 122.4426 | -0.059509 | 122.2275 | -0.15846 | -0.042603 | 0.004941 | 0.022082 | 8.47e-06 | -0.0092478 | -0.0049367 | -0.025299 | 0.0050971 | 0.064063 | 0.052823 | -0.017301 | 0.027194 | -0.0047253 | -0.073242 | -0.032043 | -0.009155 | 0.022888 | 0.15564 | -0.032043 | 0.082397 | 0.52643 | 122.1313 | -0.059509 | 122.1542 | 0.16479 | 0.10071 | 0.14648 | 0.050354 | -122.2595 | -122.2046 | 0.21515 | 0.14191 | 0.027466 | 0.091552 | -0.022888 | 0 | -0.09613 | -0.073242 | 0.2243 | 0.20599 | 0.16022 | 0.20599 | 0.16022 | 0.16479 | 0.032043 | 0.2243 | 122.2137 | -0.022888 | 122.1909 | 0.027466 | 122.1909 | -122.2366 | -122.287 | 0.082397 | 122.2137 | -0.013733 | 0.58594
3427.625 | 122.3419 | -0.10986 | 122.2824 | -0.12794 | -0.044739 | 0.0019504 | 0.021441 | -0.0019141 | -0.01053 | -0.0042959 | -0.040558 | 0.0055243 | 0.063636 | 0.046628 | -0.017515 | 0.026553 | -0.0062207 | -0.10529 | -0.041199 | -0.032043 | -0.064087 | 0.022888 | -0.054932 | -0.009155 | 0.5722 | 122.1954 | -0.091553 | 122.0306 | 0.059509 | 0 | 0.022888 | 0.07782 | -122.3236 | -122.3465 | 0.13275 | 0.10071 | 0.054931 | 0.022888 | -0.022889 | 0.01831 | -0.086975 | -0.25177 | 0.16937 | 0.13275 | 0.10986 | 0.11444 | 0.091553 | 0.054931 | -0.032044 | 0.15106 | 122.1222 | -0.009156 | 122.287 | 0.068664 | 122.3053 | -122.3145 | -122.374 | 0.045776 | 122.1405 | 0.004577 | 0.68207
3429.3281 | 122.3602 | -0.073242 | 122.2824 | -0.13557 | -0.044312 | 0.0028048 | 0.0255 | 0.0042811 | -0.0090342 | -0.0057913 | -0.11075 | 0.0055243 | 0.063636 | 0.0509 | -0.01666 | 0.029117 | -0.0085705 | -0.10071 | -0.036621 | -0.045776 | -0.045776 | 0.041199 | -0.091553 | 0 | 0.49896 | 122.2092 | -0.091553 | 122.0535 | 0.059509 | -0.013733 | 0.059509 | 0.027466 | -122.319 | -122.3282 | 0.11444 | 0.073242 | -0.018311 | 0.045776 | -0.045777 | -0.018311 | -0.073243 | -0.22888 | 0.13275 | 0.13275 | 0.059509 | 0.15106 | 0.07782 | 0.086975 | 0 | 0.15106 | 122.1451 | 0.009155 | 122.3007 | 0.036621 | 122.2824 | -122.3282 | -122.374 | 0.027466 | 122.1268 | -0.027466 | 0.5722
3431.1094 | 122.4609 | -0.068665 | 122.2229 | -0.12032 | -0.046021 | -0.00061317 | 0.020587 | -0.0046911 | -0.012025 | -0.0036551 | -0.0008851 | 0.0044561 | 0.0662 | 0.049618 | -0.017729 | 0.027194 | -0.0038709 | -0.073242 | -0.045776 | 0.004578 | 0.045776 | 0.17395 | 0.032043 | 0.10071 | 0.67749 | 122.1588 | -0.068665 | 122.1451 | 0.20142 | 0.14648 | 0.16022 | 0.073243 | -122.2687 | -122.1771 | 0.24261 | 0.16937 | 0.10071 | 0.09613 | 0.027465 | 0 | -0.064087 | -0.077819 | 0.27008 | 0.22888 | 0.21515 | 0.22888 | 0.21515 | 0.16937 | 0.041198 | 0.27008 | 122.2137 | -0.050354 | 122.2275 | 0.022889 | 122.2275 | -122.2183 | -122.2916 | 0.11444 | 122.2137 | -0.004577 | 0.74616
3432.8125 | 122.3877 | -0.073242 | 122.2778 | -0.10506 | -0.042816 | 0.0034456 | 0.023578 | 0.0040675 | -0.0092478 | -0.0023733 | -0.080231 | 0.0074469 | 0.06385 | 0.047696 | -0.017301 | 0.027194 | -0.0070751 | -0.082397 | -0.009155 | -0.036621 | -0.027466 | 0.050354 | -0.064087 | 0.009155 | 0.56763 | 122.1909 | -0.091553 | 122.0901 | 0.10071 | 0.045776 | 0.10071 | 0.036621 | -122.287 | -122.3053 | 0.1236 | 0.082397 | 0.009155 | 0.045776 | -0.027466 | -0.018311 | -0.086975 | -0.18768 | 0.17395 | 0.17395 | 0.11902 | 0.19226 | 0.13733 | 0.086975 | 0.009155 | 0.19226 | 122.1817 | 0.027466 | 122.2824 | 0.064087 | 122.2641 | -122.3145 | -122.3694 | 0.045776 | 122.1634 | -0.009155 | 0.64087
3434.5781 | 122.3419 | -0.10071 | 122.2641 | -0.12032 | -0.042603 | 0.0036594 | 0.024005 | -0.0014867 | -0.009675 | -0.0028005 | -0.086334 | 0.0057379 | 0.064704 | 0.050473 | -0.01666 | 0.028476 | -0.0045117 | -0.13733 | 0.004578 | -0.045776 | -0.091553 | -0.022888 | -0.14648 | -0.032043 | 0.39368 | 122.2137 | -0.11902 | 122.0444 | 0.041199 | -0.041199 | 0.045776 | 0.054932 | -122.2595 | -122.3557 | 0.07782 | 0.068665 | -0.045776 | 0.013733 | -0.10071 | -0.018311 | -0.050354 | -0.21973 | 0.14191 | 0.14648 | 0.059509 | 0.16479 | 0.07782 | 0.022888 | -0.045777 | 0.16022 | 122.1634 | 0.050354 | 122.3328 | 0.10529 | 122.3145 | -122.3099 | -122.3831 | 0.009155 | 122.1451 | -0.036621 | 0.49439
3436.3281 | 122.4472 | -0.073242 | 122.2366 | -0.15846 | -0.044739 | 0.001523 | 0.021014 | -0.0017005 | -0.010316 | -0.0057913 | -0.016144 | 0.0068059 | 0.063209 | 0.051755 | -0.015806 | 0.027835 | -0.0015209 | -0.10529 | -0.018311 | -0.022888 | -0.027466 | 0.068665 | -0.045776 | 0.036621 | 0.53558 | 122.1542 | -0.068665 | 122.1085 | 0.1236 | 0.091553 | 0.10986 | 0.050354 | -122.2549 | -122.2641 | 0.14191 | 0.10986 | 0.027466 | 0.059509 | -0.022888 | 0.004577 | -0.082397 | -0.12817 | 0.19684 | 0.18311 | 0.16479 | 0.17853 | 0.16022 | 0.091553 | -0.004578 | 0.19226 | 122.1771 | 0.004577 | 122.2229 | 0.054931 | 122.2275 | -122.2595 | -122.3053 | 0.045776 | 122.1817 | -0.032044 | 0.60883
3438.0781 | 122.4472 | -0.054932 | 122.2412 | -0.1432 | -0.044098 | 0.003232 | 0.025287 | 0.0019311 | -0.010102 | -0.0047231 | -0.080231 | 0.0046697 | 0.063423 | 0.0509 | -0.017301 | 0.026553 | -0.0077161 | -0.1236 | -0.032043 | -0.032043 | -0.032043 | 0.059509 | -0.082397 | 0.032043 | 0.48523 | 122.1725 | -0.07782 | 122.1405 | 0.13733 | 0.09613 | 0.16022 | 0.022889 | -122.2733 | -122.2733 | 0.11444 | 0.086975 | -0.027465 | 0.064086 | -0.050354 | -0.022888 | -0.068665 | -0.10071 | 0.19226 | 0.21515 | 0.15106 | 0.23804 | 0.17395 | 0.091552 | 0 | 0.21515 | 122.2183 | 0 | 122.2504 | 0.022889 | 122.2275 | -122.2733 | -122.319 | 0.022889 | 122.1954 | -0.068664 | 0.54016
3439.8438 | 122.4152 | -0.064087 | 122.2549 | -0.15083 | -0.04303 | 0.00088223 | 0.023578 | -0.00041873 | -0.0077524 | -0.0062185 | -0.0069885 | 0.0053107 | 0.064491 | 0.042142 | -0.01666 | 0.02634 | -0.0053661 | -0.11902 | -0.054932 | -0.018311 | -0.018311 | 0.068665 | -0.050354 | 0.041199 | 0.50812 | 122.1725 | -0.07782 | 122.1039 | 0.10529 | 0.059509 | 0.10071 | 0.045776 | -122.3099 | -122.2733 | 0.13275 | 0.10529 | 0.013733 | 0.05951 | -0.032043 | -0.013733 | -0.082398 | -0.15106 | 0.16937 | 0.1648 | 0.1236 | 0.17853 | 0.13733 | 0.086976 | 0 | 0.18311 | 122.1817 | -0.036621 | 122.2504 | 0.009155 | 122.2366 | -122.2733 | -122.3328 | 0.045776 | 122.168 | -0.054932 | 0.5722
3441.6094 | 122.4564 | -0.041199 | 122.2275 | -0.19661 | -0.042603 | 0.0034456 | 0.024646 | -0.0014867 | -0.0092478 | -0.0049367 | -0.058869 | 0.0048833 | 0.062354 | 0.051968 | -0.017942 | 0.028049 | -0.0075025 | -0.054932 | -0.059509 | 0.004578 | 0.045776 | 0.14648 | -0.013733 | 0.091553 | 0.54932 | 122.1451 | -0.064087 | 122.1542 | 0.16479 | 0.11444 | 0.17395 | 0.045777 | -122.287 | -122.1817 | 0.18768 | 0.13275 | 0.027466 | 0.086975 | -0.018311 | -0.022888 | -0.082397 | -0.073242 | 0.20599 | 0.21515 | 0.15564 | 0.23804 | 0.17853 | 0.14191 | 0.041198 | 0.22888 | 122.2183 | -0.064087 | 122.2092 | -0.01831 | 122.1863 | -122.2229 | -122.2916 | 0.086975 | 122.1954 | -0.013733 | 0.59052
3443.3594 | 122.4701 | -0.064087 | 122.2458 | -0.15846 | -0.042389 | 0.0025912 | 0.025287 | 0.00064947 | -0.010102 | -0.0028005 | -0.080231 | 0.0027471 | 0.063423 | 0.04385 | -0.017088 | 0.02933 | -0.0057935 | -0.050354 | -0.054932 | -0.009155 | 0.045776 | 0.13733 | -0.027466 | 0.082397 | 0.54932 | 122.1497 | -0.059509 | 122.1634 | 0.16937 | 0.10071 | 0.17853 | 0.054932 | -122.3007 | -122.2 | 0.20142 | 0.14648 | 0.036621 | 0.091552 | -0.018311 | 0.004578 | -0.096131 | -0.082398 | 0.23346 | 0.24261 | 0.1648 | 0.23804 | 0.16022 | 0.14648 | 0.054931 | 0.22888 | 122.2229 | -0.045777 | 122.2092 | 0.009155 | 122.2137 | -122.2549 | -122.3053 | 0.10986 | 122.2275 | 0.013733 | 0.6134
3445.1094 | 122.4152 | -0.07782 | 122.2412 | -0.15846 | -0.043885 | 0.0034456 | 0.022296 | -0.0031957 | -0.0098886 | -0.0017325 | -0.025299 | 0.0065923 | 0.064918 | 0.044064 | -0.018583 | 0.028049 | -0.0047253 | -0.11444 | -0.045776 | -0.032043 | -0.022888 | 0.068665 | -0.059509 | 0.041199 | 0.50354 | 122.1909 | -0.082397 | 122.1039 | 0.11444 | 0.059509 | 0.10986 | 0.045777 | -122.287 | -122.2641 | 0.14649 | 0.11902 | 0.018311 | 0.073242 | -0.027466 | -0.004577 | -0.050354 | -0.13733 | 0.19226 | 0.18768 | 0.13733 | 0.19226 | 0.14191 | 0.10071 | 0.009155 | 0.19684 | 122.1863 | -0.013733 | 122.2733 | 0.032044 | 122.2687 | -122.2733 | -122.3236 | 0.054932 | 122.1817 | -0.036621 | 0.58136
3446.8125 | 122.4655 | -0.064087 | 122.2595 | -0.10506 | -0.045594 | 0.0023776 | 0.024218 | -0.0034095 | -0.010102 | -0.0049367 | -0.034454 | 0.0057379 | 0.065345 | 0.048977 | -0.019438 | 0.026126 | -0.0062207 | -0.10071 | -0.050354 | -0.027466 | -0.013733 | 0.07782 | -0.032043 | 0.073242 | 0.58136 | 122.1634 | -0.086975 | 122.1313 | 0.15564 | 0.1236 | 0.13733 | 0.036621 | -122.3099 | -122.2733 | 0.14191 | 0.13733 | 0.032044 | 0.10071 | -0.004577 | -0.022888 | -0.09613 | -0.12817 | 0.21973 | 0.20142 | 0.18768 | 0.2243 | 0.21057 | 0.10529 | 0.013733 | 0.24261 | 122.2183 | -0.022888 | 122.2504 | 0.013733 | 122.2275 | -122.287 | -122.3465 | 0.050354 | 122.1954 | -0.036621 | 0.64545
3448.5625 | 122.4609 | -0.054932 | 122.2366 | -0.12032 | -0.044525 | 0.0043002 | 0.022723 | -0.0017005 | -0.011598 | -0.0042959 | -0.031403 | 0.0057379 | 0.061073 | 0.048977 | -0.017729 | 0.027621 | -0.0062207 | -0.09613 | -0.054932 | -0.022888 | 0.013733 | 0.09613 | 0.009155 | 0.073242 | 0.62256 | 122.1497 | -0.054932 | 122.1497 | 0.18768 | 0.14191 | 0.15564 | 0.032044 | -122.2916 | -122.2229 | 0.15106 | 0.12817 | 0.064087 | 0.09613 | 0.032043 | 0 | -0.086975 | -0.086975 | 0.24261 | 0.21057 | 0.19684 | 0.21057 | 0.19684 | 0.11902 | 0.036621 | 0.24261 | 122.2046 | -0.032044 | 122.2046 | 0 | 122.2046 | -122.2595 | -122.2916 | 0.068665 | 122.2046 | -0.041198 | 0.67749
3450.3281 | 122.4106 | -0.07782 | 122.2366 | -0.12794 | -0.043244 | 0.0030184 | 0.024432 | -0.0036231 | -0.009675 | -0.0019461 | -0.016144 | 0.0055243 | 0.064277 | 0.051114 | -0.018797 | 0.025912 | -0.0032299 | -0.10071 | -0.036621 | -0.009155 | -0.018311 | 0.059509 | -0.050354 | 0.045776 | 0.50812 | 122.1771 | -0.07782 | 122.1039 | 0.10529 | 0.059509 | 0.11444 | 0.068665 | -122.2733 | -122.2549 | 0.13733 | 0.1236 | 0.027466 | 0.054931 | -0.041199 | 0 | -0.059509 | -0.13275 | 0.18311 | 0.19226 | 0.13733 | 0.19226 | 0.13733 | 0.068664 | -0.009156 | 0.18311 | 122.1817 | -0.027466 | 122.2549 | 0.041199 | 122.2549 | -122.2458 | -122.3145 | 0.059509 | 122.1817 | -0.022888 | 0.58594
3452.0312 | 122.4197 | -0.07782 | 122.2366 | -0.19661 | -0.043457 | 0.0023776 | 0.023791 | 0.00022207 | -0.011598 | -0.0017325 | -0.058869 | 0.0048833 | 0.062141 | 0.04385 | -0.016233 | 0.028049 | -0.0066479 | -0.10529 | -0.059509 | -0.036621 | -0.018311 | 0.068665 | -0.054932 | 0.050354 | 0.50354 | 122.1725 | -0.064087 | 122.0993 | 0.10986 | 0.068665 | 0.10529 | 0.041199 | -122.2961 | -122.2549 | 0.14649 | 0.12817 | 0.022888 | 0.086975 | -0.018311 | 0.013733 | -0.064087 | -0.13733 | 0.18768 | 0.18311 | 0.14649 | 0.16937 | 0.13275 | 0.10529 | 0.01831 | 0.17395 | 122.1634 | -0.022888 | 122.2366 | 0.018311 | 122.2504 | -122.2733 | -122.3007 | 0.059509 | 122.1771 | -0.027466 | 0.58136
3453.7812 | 122.4655 | -0.054932 | 122.2504 | -0.15083 | -0.042816 | 0.001523 | 0.022296 | -0.0064001 | -0.011384 | -0.0040823 | -0.022247 | 0.0053107 | 0.06385 | 0.042782 | -0.02136 | 0.028262 | -0.0060071 | -0.068665 | -0.045776 | -0.013733 | 0.045776 | 0.15564 | 0.018311 | 0.10986 | 0.70038 | 122.168 | -0.064087 | 122.1497 | 0.1831 | 0.15564 | 0.13733 | 0.041199 | -122.2961 | -122.2046 | 0.21057 | 0.16479 | 0.073243 | 0.1236 | 0.032044 | -0.009155 | -0.082397 | -0.10071 | 0.23804 | 0.19226 | 0.21057 | 0.20142 | 0.21973 | 0.16937 | 0.059509 | 0.24719 | 122.2137 | -0.032043 | 122.2321 | 0.009156 | 122.2229 | -122.2641 | -122.3145 | 0.10071 | 122.2046 | -0.013733 | 0.75531
3455.5469 | 122.4747 | -0.050354 | 122.2092 | -0.18135 | -0.043885 | 0.0017368 | 0.022082 | -0.0019141 | -0.01053 | -0.0023733 | -0.028351 | 0.0061651 | 0.06385 | 0.046414 | -0.01901 | 0.025699 | -0.0062207 | -0.082397 | -0.045776 | -0.018311 | 0.036621 | 0.14191 | 0.022888 | 0.10071 | 0.68207 | 122.1542 | -0.064087 | 122.168 | 0.19684 | 0.15106 | 0.16479 | 0.032043 | -122.2549 | -122.1725 | 0.19226 | 0.15106 | 0.073242 | 0.11902 | 0.041199 | -0.013733 | -0.054931 | -0.041198 | 0.24719 | 0.21515 | 0.20142 | 0.22888 | 0.21515 | 0.16022 | 0.054932 | 0.26093 | 122.2321 | -0.027465 | 122.2183 | 0.004578 | 122.2046 | -122.2275 | -122.2733 | 0.086975 | 122.2183 | -0.032043 | 0.73242
3457.3125 | 122.4747 | -0.036621 | 122.2504 | -0.1432 | -0.044953 | 0.0010958 | 0.022082 | -0.0046911 | -0.012452 | -0.0042959 | -0.025299 | 0.0040289 | 0.060432 | 0.045559 | -0.018369 | 0.024844 | -0.0075025 | -0.068665 | -0.050354 | -0.013733 | 0.050354 | 0.17395 | 0.050354 | 0.11444 | 0.69122 | 122.1771 | -0.054932 | 122.1542 | 0.20599 | 0.16022 | 0.16937 | 0.022888 | -122.3007 | -122.2 | 0.21057 | 0.15106 | 0.086975 | 0.12817 | 0.064087 | -0.018311 | -0.073242 | -0.09613 | 0.24262 | 0.20599 | 0.19684 | 0.22431 | 0.21515 | 0.18768 | 0.064087 | 0.26093 | 122.2092 | -0.036621 | 122.2321 | -0.013733 | 122.2137 | -122.2641 | -122.3053 | 0.086975 | 122.1909 | -0.032044 | 0.72784
3459.0156 | 122.3877 | -0.10071 | 122.2412 | -0.17372 | -0.043457 | 0.0017368 | 0.026568 | -0.00063233 | -0.0094614 | -0.0047231 | -0.14127 | 0.0055243 | 0.061073 | 0.048977 | -0.019651 | 0.028049 | -0.0040845 | -0.082397 | -0.004578 | -0.064087 | -0.013733 | 0.054932 | -0.07782 | 0.018311 | 0.59967 | 122.2046 | -0.082397 | 122.0901 | 0.10986 | 0.022888 | 0.068665 | 0.036621 | -122.2458 | -122.2549 | 0.15564 | 0.11902 | 0.022888 | 0.082398 | -0.013733 | 0.018311 | -0.036621 | -0.15106 | 0.21057 | 0.16937 | 0.1236 | 0.15106 | 0.10528 | 0.11902 | 0.050354 | 0.19226 | 122.1725 | 0.059509 | 122.287 | 0.09613 | 122.3053 | -122.3053 | -122.3236 | 0.086975 | 122.1909 | 0.018311 | 0.70038
3460.7969 | 122.4564 | -0.045776 | 122.2504 | -0.11269 | -0.044739 | 0.003232 | 0.022296 | -0.00084593 | -0.007966 | -0.0028005 | -0.034454 | 0.0042425 | 0.061714 | 0.04855 | -0.017729 | 0.026981 | -0.0013073 | -0.068665 | -0.064087 | 0 | 0.054932 | 0.16022 | 0.032043 | 0.10529 | 0.70038 | 122.1588 | -0.064087 | 122.1451 | 0.20142 | 0.14191 | 0.15564 | 0.045776 | -122.3145 | -122.1954 | 0.20599 | 0.15106 | 0.077819 | 0.10529 | 0.032043 | -0.018311 | -0.091553 | -0.10528 | 0.24719 | 0.20142 | 0.18768 | 0.21973 | 0.20599 | 0.16022 | 0.054932 | 0.2655 | 122.2092 | -0.064087 | 122.2229 | -0.018311 | 122.2046 | -122.2504 | -122.3145 | 0.10071 | 122.1909 | -0.022889 | 0.74615
3462.5625 | 122.374 | -0.086975 | 122.2549 | -0.18135 | -0.041962 | 0.0025912 | 0.025287 | 0.00043587 | -0.007966 | -0.0045095 | -0.13211 | 0.0065923 | 0.064063 | 0.051114 | -0.015592 | 0.028476 | -0.0057935 | -0.13733 | -0.018311 | -0.050354 | -0.073242 | -0.004578 | -0.13275 | -0.018311 | 0.41199 | 122.2183 | -0.091553 | 122.081 | 0.07782 | -0.009155 | 0.086975 | 0.036621 | -122.2733 | -122.3282 | 0.082397 | 0.068664 | -0.045776 | 0.032043 | -0.082397 | -0.004578 | -0.036621 | -0.17395 | 0.16479 | 0.17395 | 0.07782 | 0.17853 | 0.082398 | 0.045776 | -0.022888 | 0.16937 | 122.1725 | 0.032043 | 122.3099 | 0.068664 | 122.3053 | -122.3053 | -122.3465 | 0.013733 | 122.168 | -0.050354 | 0.49896
3464.3125 | 122.3419 | -0.086975 | 122.2778 | -0.17372 | -0.046875 | 0.0023776 | 0.0255 | 0.00043587 | -0.0098886 | -0.0034415 | -0.10464 | 0.0074469 | 0.064063 | 0.044491 | -0.015592 | 0.027194 | -0.0038709 | -0.14648 | -0.018311 | -0.050354 | -0.086975 | -0.022888 | -0.16022 | -0.036621 | 0.39368 | 122.2046 | -0.09613 | 122.0581 | 0.022888 | -0.027466 | 0.022888 | 0.036621 | -122.2961 | -122.3648 | 0.064087 | 0.050354 | -0.073242 | 0.013733 | -0.10986 | -0.009155 | -0.073242 | -0.21973 | 0.10986 | 0.10986 | 0.059509 | 0.11902 | 0.068664 | 0.027466 | -0.036621 | 0.11902 | 122.1542 | 0.032043 | 122.3007 | 0.068664 | 122.2916 | -122.3282 | -122.374 | 0 | 122.1451 | -0.059509 | 0.48065
3466 | 122.493 | -0.059509 | 122.2321 | -0.12794 | -0.045166 | 0.0017368 | 0.02315 | -0.0046911 | -0.01053 | -0.0021597 | -0.0039367 | 0.0042425 | 0.062568 | 0.047055 | -0.016447 | 0.027408 | -0.010066 | -0.073242 | -0.036621 | -0.004578 | 0.041199 | 0.16937 | 0.032043 | 0.11444 | 0.66834 | 122.1542 | -0.073242 | 122.1725 | 0.2243 | 0.16937 | 0.1831 | 0.054931 | -122.2687 | -122.1909 | 0.22888 | 0.17395 | 0.091552 | 0.11902 | 0.036621 | -0.013733 | -0.07782 | -0.05951 | 0.28381 | 0.24261 | 0.22888 | 0.25635 | 0.24261 | 0.17395 | 0.045777 | 0.29755 | 122.2458 | -0.032043 | 122.2275 | 0.022888 | 122.2137 | -122.2366 | -122.3053 | 0.10071 | 122.2321 | -0.013733 | 0.72784
3467.75 | 122.4106 | -0.064087 | 122.2504 | -0.18898 | -0.042176 | 0.0043002 | 0.021655 | 0.00086307 | -0.0098886 | -0.0038687 | -0.031403 | 0.0061651 | 0.063423 | 0.053677 | -0.015165 | 0.028049 | -0.0010937 | -0.11902 | -0.050354 | -0.013733 | -0.018311 | 0.073242 | -0.073242 | 0.045776 | 0.50812 | 122.1725 | -0.082397 | 122.0947 | 0.10986 | 0.07782 | 0.11902 | 0.050354 | -122.3007 | -122.2687 | 0.13733 | 0.10986 | -0.009155 | 0.059509 | -0.059509 | -0.01831 | -0.07782 | -0.15564 | 0.17395 | 0.18311 | 0.14191 | 0.20142 | 0.16022 | 0.086975 | -0.004578 | 0.19226 | 122.1771 | -0.036621 | 122.2549 | 0.013733 | 122.2366 | -122.2641 | -122.3328 | 0.045776 | 122.1588 | -0.054932 | 0.5722
3469.5156 | 122.3785 | -0.082397 | 122.2366 | -0.16609 | -0.043671 | -0.00039957 | 0.024859 | 0.0010767 | -0.010102 | -0.0025869 | -0.098541 | 0.0059515 | 0.064063 | 0.056454 | -0.01901 | 0.027408 | -0.0072889 | -0.10986 | -0.022888 | -0.036621 | -0.041199 | 0.018311 | -0.068665 | 0.004578 | 0.59052 | 122.2183 | -0.07782 | 122.0947 | 0.091553 | 0.013733 | 0.07782 | 0.045776 | -122.2595 | -122.2778 | 0.10071 | 0.086975 | 0.013732 | 0.041199 | -0.032044 | 0.004577 | -0.01831 | -0.14191 | 0.17395 | 0.16022 | 0.09613 | 0.15564 | 0.091553 | 0.054932 | -0.004578 | 0.16937 | 122.1725 | 0.013733 | 122.2961 | 0.059509 | 122.3007 | -122.2733 | -122.3145 | 0.041198 | 122.1771 | -0.027466 | 0.67291
3471.2344 | 122.4609 | -0.054932 | 122.2366 | -0.13557 | -0.043671 | 0.00066863 | 0.022509 | -0.0014867 | -0.011598 | -0.0034415 | -0.016144 | 0.0059515 | 0.063423 | 0.047696 | -0.016447 | 0.028262 | -0.0087841 | -0.064087 | -0.059509 | -0.004578 | 0.045776 | 0.16937 | 0.032043 | 0.091553 | 0.70038 | 122.168 | -0.068665 | 122.1359 | 0.19226 | 0.13275 | 0.15564 | 0.050354 | -122.2961 | -122.1909 | 0.22431 | 0.14649 | 0.086975 | 0.096131 | 0.036621 | -0.013733 | -0.068664 | -0.10071 | 0.24719 | 0.21057 | 0.18768 | 0.22431 | 0.20142 | 0.17395 | 0.050354 | 0.26093 | 122.2046 | -0.054931 | 122.2366 | -0.004577 | 122.2229 | -122.2412 | -122.3053 | 0.10071 | 122.1909 | -0.009155 | 0.75531
3472.9844 | 122.4426 | -0.073242 | 122.2412 | -0.15083 | -0.044953 | 0.0013094 | 0.023578 | -0.0046911 | -0.0071116 | -0.0040823 | -0.019196 | 0.0038153 | 0.062354 | 0.045346 | -0.016447 | 0.027621 | -0.0017347 | -0.11444 | -0.050354 | -0.032043 | -0.032043 | 0.07782 | -0.036621 | 0.041199 | 0.54474 | 122.168 | -0.068665 | 122.1176 | 0.13733 | 0.10529 | 0.11902 | 0.041199 | -122.2916 | -122.2733 | 0.15106 | 0.11444 | 0.036621 | 0.073242 | -0.004578 | 0.004577 | -0.073242 | -0.1236 | 0.21057 | 0.19226 | 0.17853 | 0.18768 | 0.17395 | 0.10986 | 0 | 0.20599 | 122.1863 | -0.018311 | 122.2366 | 0.022888 | 122.2412 | -122.2733 | -122.3099 | 0.041199 | 122.1909 | -0.041199 | 0.61798
3474.7344 | 122.4152 | -0.068665 | 122.2549 | -0.17372 | -0.043671 | 0.002164 | 0.02315 | -0.0019141 | -0.0092478 | -0.0075003 | -0.037506 | 0.0072333 | 0.063423 | 0.04321 | -0.020933 | 0.027835 | -0.0049389 | -0.10071 | -0.041199 | -0.032043 | -0.022888 | 0.068665 | -0.041199 | 0.032043 | 0.51727 | 122.1817 | -0.064087 | 122.0947 | 0.10071 | 0.082397 | 0.10529 | 0.036622 | -122.2961 | -122.2778 | 0.13733 | 0.10071 | 0.027466 | 0.064086 | -0.009156 | 0.004578 | -0.073242 | -0.16022 | 0.16937 | 0.17395 | 0.15106 | 0.16937 | 0.14648 | 0.10071 | 0.009155 | 0.1648 | 122.1588 | -0.009156 | 122.2458 | 0.027466 | 122.2504 | -122.287 | -122.319 | 0.045777 | 122.1634 | -0.032043 | 0.58594
3476.5 | 122.3602 | -0.10986 | 122.2824 | -0.082169 | -0.044098 | 0.0017368 | 0.024646 | 0.0015039 | -0.009675 | -0.0051505 | -0.09549 | 0.0080877 | 0.064704 | 0.059231 | -0.018583 | 0.026126 | -0.0055799 | -0.15106 | 0 | -0.050354 | -0.09613 | 0 | -0.10529 | -0.022888 | 0.55389 | 122.2 | -0.09613 | 122.0444 | 0.045776 | -0.009155 | 0.027466 | 0.059509 | -122.2824 | -122.3785 | 0.10986 | 0.086975 | 0.004577 | 0.027466 | -0.054932 | 0.013733 | -0.082398 | -0.23804 | 0.15564 | 0.13733 | 0.10071 | 0.1236 | 0.086975 | 0.050354 | -0.045776 | 0.14191 | 122.1405 | 0.050354 | 122.2961 | 0.10986 | 122.3099 | -122.3328 | -122.3785 | 0.013733 | 122.1542 | -0.041199 | 0.66376
3478.2031 | 122.3282 | -0.091553 | 122.2687 | -0.15846 | -0.041321 | 0.0025912 | 0.025714 | -0.0031957 | -0.011598 | -0.0049367 | -0.13821 | 0.0085149 | 0.062782 | 0.049618 | -0.017515 | 0.029117 | -0.0077161 | -0.10529 | -0.013733 | -0.045776 | -0.050354 | 0.027466 | -0.10529 | -0.013733 | 0.48065 | 122.2229 | -0.091553 | 122.049 | 0.041199 | -0.032043 | 0.050354 | 0.045777 | -122.2824 | -122.319 | 0.11902 | 0.07782 | -0.013733 | 0.032043 | -0.05951 | 0 | -0.045777 | -0.21973 | 0.13275 | 0.14191 | 0.05951 | 0.14191 | 0.05951 | 0.073242 | -0.004578 | 0.13275 | 122.1405 | 0.032043 | 122.3145 | 0.07782 | 122.3145 | -122.3145 | -122.3602 | 0.041199 | 122.1405 | -0.013733 | 0.57221
3479.9844 | 122.4106 | -0.086975 | 122.2733 | -0.16609 | -0.044525 | 0.003873 | 0.022296 | -0.0017005 | -0.010957 | -0.0051505 | -0.04361 | 0.0042425 | 0.063209 | 0.049832 | -0.016447 | 0.026767 | -0.0064343 | -0.073242 | -0.045776 | -0.022888 | 0.027466 | 0.13275 | 0.009155 | 0.07782 | 0.67749 | 122.1725 | -0.073242 | 122.0901 | 0.14191 | 0.091553 | 0.10529 | 0.064087 | -122.319 | -122.2458 | 0.21973 | 0.16479 | 0.09613 | 0.10071 | 0.032043 | 0.013733 | -0.10071 | -0.1831 | 0.22888 | 0.19226 | 0.17853 | 0.17853 | 0.16479 | 0.15564 | 0.050354 | 0.21515 | 122.1634 | -0.022888 | 122.2458 | 0.041199 | 122.2595 | -122.2961 | -122.3465 | 0.11444 | 122.1771 | 0.013733 | 0.76447
3481.6875 | 122.4335 | -0.068665 | 122.2366 | -0.21187 | -0.043671 | 0.0025912 | 0.021869 | -0.0042639 | -0.0088206 | -0.0017325 | -0.022247 | 0.0070197 | 0.062141 | 0.041287 | -0.017729 | 0.026767 | -0.0057935 | -0.10986 | -0.045776 | -0.018311 | -0.027466 | 0.073242 | -0.059509 | 0.041199 | 0.54016 | 122.1771 | -0.082397 | 122.1039 | 0.13275 | 0.10071 | 0.13275 | 0.050354 | -122.2824 | -122.2641 | 0.14191 | 0.10986 | 0.009156 | 0.05951 | -0.041198 | -0.013732 | -0.059509 | -0.13275 | 0.20142 | 0.20142 | 0.16937 | 0.21515 | 0.18311 | 0.091553 | -0.009155 | 0.21515 | 122.1863 | -0.027465 | 122.2595 | 0.022889 | 122.2458 | -122.2549 | -122.319 | 0.041199 | 122.1725 | -0.041198 | 0.60883
3483.4375 | 122.319 | -0.09613 | 122.2961 | -0.15846 | -0.041535 | 0.0040866 | 0.026782 | 0.00086307 | -0.010102 | -0.0038687 | -0.13516 | 0.0065923 | 0.064918 | 0.051968 | -0.016874 | 0.027835 | -0.0055799 | -0.1236 | -0.018311 | -0.050354 | -0.07782 | -0.032043 | -0.16479 | -0.059509 | 0.39368 | 122.2229 | -0.10986 | 122.0215 | -0.009155 | -0.064087 | 0.018311 | 0.045776 | -122.3145 | -122.374 | 0.064087 | 0.036621 | -0.068665 | -0.009155 | -0.11444 | -0.013733 | -0.073243 | -0.27466 | 0.086975 | 0.11444 | 0.032043 | 0.12817 | 0.045776 | 0.018311 | -0.027466 | 0.10071 | 122.1313 | 0.032043 | 122.3328 | 0.077819 | 122.319 | -122.3465 | -122.406 | 0.01831 | 122.1176 | -0.027466 | 0.48981
3485.2031 | 122.4609 | -0.032043 | 122.2321 | -0.20424 | -0.041962 | 0.0030184 | 0.023364 | 0.0021447 | -0.007966 | -0.0040823 | -0.071076 | 0.0072333 | 0.064704 | 0.048337 | -0.018369 | 0.027621 | -0.00023931 | -0.054932 | -0.050354 | 0.004578 | 0.041199 | 0.14191 | -0.022888 | 0.073242 | 0.55847 | 122.1771 | -0.050354 | 122.1542 | 0.16937 | 0.10529 | 0.16937 | 0.036621 | -122.2824 | -122.1909 | 0.17395 | 0.10529 | 0.009155 | 0.068664 | -0.027466 | -0.018311 | -0.054932 | -0.07782 | 0.20142 | 0.20142 | 0.13733 | 0.21973 | 0.15564 | 0.13733 | 0.036621 | 0.21973 | 122.2046 | -0.054932 | 122.2275 | -0.018311 | 122.2092 | -122.2275 | -122.2824 | 0.073242 | 122.1863 | -0.022889 | 0.59052
3486.9688 | 122.3877 | -0.086975 | 122.2504 | -0.1432 | -0.041962 | 0.002164 | 0.024432 | 0.00043587 | -0.009675 | -0.0030141 | -0.089386 | 0.0053107 | 0.064277 | 0.056241 | -0.018583 | 0.028049 | -0.0051525 | -0.082397 | -0.004578 | -0.032043 | -0.032043 | 0.073242 | -0.068665 | 0.036621 | 0.58594 | 122.2183 | -0.07782 | 122.0901 | 0.09613 | 0.032043 | 0.082397 | 0.054932 | -122.2549 | -122.2824 | 0.16022 | 0.1236 | 0.01831 | 0.068664 | -0.036622 | 0.009155 | -0.032043 | -0.16022 | 0.1831 | 0.16937 | 0.11902 | 0.16022 | 0.10986 | 0.10529 | 0 | 0.17395 | 122.168 | 0.027465 | 122.2961 | 0.082397 | 122.3053 | -122.2824 | -122.3282 | 0.054932 | 122.1771 | 0.004578 | 0.67291
3488.6719 | 122.4747 | -0.059509 | 122.2229 | -0.2195 | -0.043885 | 0.00045503 | 0.021441 | -0.0010595 | -0.011384 | -0.0047231 | -0.013092 | 0.0063787 | 0.061927 | 0.047268 | -0.014311 | 0.025699 | -0.0038709 | -0.11444 | -0.045776 | -0.009155 | -0.004578 | 0.11444 | 0 | 0.082397 | 0.62714 | 122.1497 | -0.045776 | 122.1405 | 0.16479 | 0.15106 | 0.14648 | 0.050354 | -122.2687 | -122.2275 | 0.17395 | 0.14191 | 0.059509 | 0.091552 | 0.009155 | 0.013733 | -0.073242 | -0.082397 | 0.2243 | 0.20599 | 0.21057 | 0.19226 | 0.19684 | 0.1236 | 0.004577 | 0.21057 | 122.1863 | -0.036621 | 122.1954 | 0.013733 | 122.2092 | -122.2321 | -122.2687 | 0.054931 | 122.2 | -0.054932 | 0.68665
3490.4219 | 122.4976 | -0.045776 | 122.2549 | -0.15846 | -0.044525 | 0.0023776 | 0.020373 | -0.0036231 | -0.010743 | -0.0040823 | -0.01004 | 0.0065923 | 0.066413 | 0.051968 | -0.017729 | 0.024844 | -0.0042981 | -0.07782 | -0.045776 | -0.009155 | 0.045776 | 0.16937 | 0.027466 | 0.11444 | 0.71869 | 122.1405 | -0.054932 | 122.168 | 0.19684 | 0.15106 | 0.16479 | 0.036621 | -122.3007 | -122.2092 | 0.21515 | 0.16022 | 0.073242 | 0.1236 | 0.036621 | -0.009156 | -0.11444 | -0.086975 | 0.24261 | 0.21057 | 0.19684 | 0.21973 | 0.20599 | 0.17853 | 0.054931 | 0.25177 | 122.2229 | -0.036621 | 122.1954 | 0 | 122.1863 | -122.2641 | -122.3099 | 0.091552 | 122.2137 | -0.032044 | 0.76447
3492.1875 | 122.4106 | -0.064087 | 122.2504 | -0.18135 | -0.041962 | 0.0017368 | 0.024432 | -0.0010595 | -0.011811 | -0.0040823 | -0.025299 | 0.0050971 | 0.064491 | 0.045132 | -0.018583 | 0.023776 | -0.0060071 | -0.09613 | -0.054932 | -0.018311 | -0.013733 | 0.091553 | -0.041199 | 0.036621 | 0.5127 | 122.1817 | -0.082397 | 122.0947 | 0.14191 | 0.073242 | 0.10071 | 0.045776 | -122.3053 | -122.2641 | 0.15564 | 0.10071 | 0.022888 | 0.054932 | -0.022888 | -0.01831 | -0.068664 | -0.15564 | 0.20599 | 0.1648 | 0.13733 | 0.18311 | 0.15564 | 0.10986 | 0.004578 | 0.2243 | 122.1771 | -0.036621 | 122.2641 | 0.009155 | 122.2458 | -122.2687 | -122.3328 | 0.050354 | 122.1588 | -0.032043 | 0.57678
3493.9375 | 122.4472 | -0.064087 | 122.2321 | -0.19661 | -0.041107 | 0.0034456 | 0.024005 | 0.0017175 | -0.01117 | -0.0036551 | -0.074127 | 0.0065923 | 0.0615 | 0.053891 | -0.018583 | 0.026767 | -0.0068615 | -0.050354 | -0.054932 | -0.009155 | 0.045776 | 0.14648 | -0.032043 | 0.068665 | 0.55389 | 122.1634 | -0.050354 | 122.1451 | 0.16479 | 0.10986 | 0.16022 | 0.054932 | -122.287 | -122.1863 | 0.21057 | 0.13275 | 0.032044 | 0.07782 | -0.022888 | 0.013733 | -0.068665 | -0.086975 | 0.22888 | 0.2243 | 0.17395 | 0.21057 | 0.16022 | 0.15564 | 0.054931 | 0.21515 | 122.1954 | -0.045777 | 122.2137 | 0.009155 | 122.2275 | -122.2412 | -122.2824 | 0.10986 | 122.2092 | 0.013733 | 0.61798
3495.6875 | 122.4152 | -0.045776 | 122.2458 | -0.20424 | -0.043885 | 0.00088223 | 0.023364 | -0.00020513 | -0.01117 | -0.0051505 | -0.04361 | 0.0057379 | 0.064063 | 0.04855 | -0.018156 | 0.027194 | -0.0064343 | -0.091553 | -0.050354 | -0.013733 | 0.032043 | 0.10986 | -0.045776 | 0.054932 | 0.53558 | 122.1817 | -0.07782 | 122.1268 | 0.13275 | 0.091553 | 0.12817 | 0.032043 | -122.2961 | -122.2137 | 0.15564 | 0.10071 | 0 | 0.068665 | -0.032043 | -0.032044 | -0.064087 | -0.11902 | 0.17853 | 0.17395 | 0.13733 | 0.20599 | 0.16937 | 0.1236 | 0.045776 | 0.21057 | 122.2046 | -0.036621 | 122.2595 | -0.004578 | 122.2275 | -122.2595 | -122.3236 | 0.077819 | 122.1725 | -0.045777 | 0.58136
3497.4531 | 122.4609 | -0.050354 | 122.2366 | -0.13557 | -0.044098 | 0.003873 | 0.020587 | -0.0068273 | -0.012025 | -0.0019461 | -0.028351 | 0.0061651 | 0.063209 | 0.049405 | -0.018797 | 0.023776 | -0.0075025 | -0.073242 | -0.050354 | -0.018311 | 0.041199 | 0.17395 | 0.022888 | 0.10529 | 0.70953 | 122.168 | -0.068665 | 122.1497 | 0.18768 | 0.12817 | 0.15564 | 0.032043 | -122.287 | -122.1954 | 0.2243 | 0.15564 | 0.073242 | 0.1236 | 0.041199 | -0.018311 | -0.068664 | -0.086975 | 0.23804 | 0.20599 | 0.17853 | 0.22431 | 0.19684 | 0.19226 | 0.05951 | 0.25635 | 122.2183 | -0.032043 | 122.2366 | 0 | 122.2183 | -122.2549 | -122.3053 | 0.091553 | 122.2 | -0.022888 | 0.75989
3499.1562 | 122.3969 | -0.091553 | 122.2595 | -0.11269 | -0.044098 | 0.0017368 | 0.025287 | 0.0019311 | -0.012666 | -0.0023733 | -0.13516 | 0.0072333 | 0.061286 | 0.044705 | -0.019865 | 0.028903 | -0.0064343 | -0.086975 | -0.009155 | -0.041199 | -0.018311 | 0.059509 | -0.07782 | 0.004578 | 0.6134 | 122.2137 | -0.082397 | 122.081 | 0.10071 | 0.027466 | 0.082397 | 0.050354 | -122.2687 | -122.2778 | 0.15106 | 0.096131 | 0.013733 | 0.045777 | -0.036621 | 0.009156 | -0.045776 | -0.17853 | 0.19226 | 0.17395 | 0.11902 | 0.16479 | 0.10986 | 0.10071 | 0.022888 | 0.18311 | 122.1634 | 0.032044 | 122.2961 | 0.082398 | 122.3053 | -122.3007 | -122.3419 | 0.073242 | 122.1725 | 0.004578 | 0.70496
3500.9219 | 122.3877 | -0.086975 | 122.2595 | -0.1432 | -0.042603 | 0.0030184 | 0.025927 | -0.0036231 | -0.009675 | -0.0032277 | -0.092438 | 0.0070197 | 0.062568 | 0.049618 | -0.016233 | 0.028903 | -0.0060071 | -0.13275 | -0.004578 | -0.041199 | -0.073242 | 0.009155 | -0.13275 | -0.018311 | 0.42114 | 122.2046 | -0.10071 | 122.0947 | 0.07782 | 0.013733 | 0.09613 | 0.045776 | -122.2641 | -122.3328 | 0.09613 | 0.068664 | -0.045776 | 0.022888 | -0.091552 | -0.013733 | -0.054931 | -0.16479 | 0.16479 | 0.1831 | 0.10071 | 0.19684 | 0.11444 | 0.050354 | -0.032043 | 0.17853 | 122.1954 | 0.036621 | 122.3053 | 0.082397 | 122.2916 | -122.3007 | -122.3602 | 0.013733 | 122.1817 | -0.045776 | 0.50812
3502.6875 | 122.4701 | -0.050354 | 122.2458 | -0.12032 | -0.042389 | 0.002164 | 0.02016 | -0.0029821 | -0.011811 | -0.0055777 | -0.0069885 | 0.0055243 | 0.066413 | 0.047482 | -0.018156 | 0.02634 | -0.0072889 | -0.09613 | -0.032043 | -0.018311 | 0.013733 | 0.1236 | 0 | 0.10529 | 0.66376 | 122.1588 | -0.073242 | 122.1588 | 0.20599 | 0.14648 | 0.16022 | 0.032043 | -122.2778 | -122.2321 | 0.17395 | 0.15564 | 0.050354 | 0.1236 | 0.018311 | -0.022888 | -0.086976 | -0.086976 | 0.25635 | 0.21057 | 0.19684 | 0.23346 | 0.21973 | 0.14191 | 0.032044 | 0.27924 | 122.2321 | -0.013732 | 122.2321 | 0.018311 | 122.2092 | -122.2641 | -122.319 | 0.064087 | 122.2092 | -0.045776 | 0.71411
3504.3906 | 122.3328 | -0.086975 | 122.2733 | -0.15083 | -0.042603 | 0.0030184 | 0.02315 | 0.0023585 | -0.01053 | -0.0034415 | -0.12601 | 0.0070197 | 0.064491 | 0.050259 | -0.017729 | 0.028049 | -0.0053661 | -0.09613 | -0.022888 | -0.032043 | -0.036621 | 0.036621 | -0.10529 | -0.018311 | 0.5127 | 122.2229 | -0.086975 | 122.0673 | 0.050354 | -0.045776 | 0.050354 | 0.054932 | -122.2961 | -122.3099 | 0.1236 | 0.068664 | -0.018311 | 0.013732 | -0.073243 | 0 | -0.050354 | -0.20599 | 0.13733 | 0.13733 | 0.041199 | 0.13733 | 0.041199 | 0.068664 | -0.004578 | 0.13733 | 122.1542 | 0.009155 | 122.3099 | 0.064087 | 122.3099 | -122.3053 | -122.3602 | 0.050354 | 122.1542 | -0.009155 | 0.59967
3506.1406 | 122.3602 | -0.09613 | 122.2961 | -0.12794 | -0.04303 | 0.002164 | 0.021014 | -0.0040503 | -0.012666 | -0.0030141 | -0.037506 | 0.0061651 | 0.062568 | 0.051114 | -0.014311 | 0.026553 | -0.0045117 | -0.091553 | -0.036621 | -0.018311 | -0.009155 | 0.086975 | -0.018311 | 0.041199 | 0.63629 | 122.2046 | -0.082397 | 122.0444 | 0.073242 | 0.045776 | 0.045776 | 0.077819 | -122.3328 | -122.3053 | 0.1831 | 0.13733 | 0.077819 | 0.05951 | 0 | 0.013733 | -0.091553 | -0.25177 | 0.16937 | 0.14191 | 0.14191 | 0.12817 | 0.12817 | 0.10529 | 0.009156 | 0.15564 | 122.1268 | -0.01831 | 122.287 | 0.059509 | 122.3007 | -122.3145 | -122.3785 | 0.086975 | 122.1405 | 0.004577 | 0.73242
3507.9062 | 122.374 | -0.07782 | 122.2687 | -0.1432 | -0.042176 | 0.002164 | 0.024646 | 0.0062037 | -0.010102 | -0.0025869 | -0.12906 | 0.0072333 | 0.064063 | 0.047055 | -0.018583 | 0.027835 | -0.0045117 | -0.086975 | -0.027466 | -0.036621 | -0.022888 | 0.064087 | -0.073242 | 0.032043 | 0.59509 | 122.2183 | -0.082397 | 122.0856 | 0.086975 | 0.041199 | 0.086975 | 0.041199 | -122.2961 | -122.2916 | 0.14191 | 0.10986 | 0.004578 | 0.068664 | -0.036621 | -0.004577 | -0.050354 | -0.18311 | 0.16479 | 0.16479 | 0.11902 | 0.16937 | 0.1236 | 0.10071 | 0.013733 | 0.16937 | 122.168 | 0.009155 | 122.3007 | 0.050354 | 122.2961 | -122.3053 | -122.3511 | 0.054932 | 122.1634 | -0.009155 | 0.67291
3509.6562 | 122.4518 | -0.073242 | 122.2504 | -0.16609 | -0.043244 | 0.00066863 | 0.021655 | -0.0017005 | -0.009675 | -0.0028005 | -0.025299 | 0.0057379 | 0.061286 | 0.053036 | -0.017515 | 0.026553 | -0.0070751 | -0.064087 | -0.045776 | -0.018311 | 0.059509 | 0.15564 | 0.004578 | 0.10986 | 0.70038 | 122.168 | -0.059509 | 122.1359 | 0.17395 | 0.1236 | 0.14648 | 0.054931 | -122.2961 | -122.1909 | 0.22888 | 0.18311 | 0.07782 | 0.12817 | 0.022889 | 0.013733 | -0.082397 | -0.11444 | 0.24719 | 0.21973 | 0.19684 | 0.20599 | 0.1831 | 0.17395 | 0.07782 | 0.23346 | 122.1954 | -0.027465 | 122.2275 | 0.027466 | 122.2412 | -122.2687 | -122.3099 | 0.13275 | 122.2092 | 0.009155 | 0.77362
3511.3438 | 122.4564 | -0.041199 | 122.2458 | -0.10506 | -0.042603 | 0.0036594 | 0.023364 | -0.0031957 | -0.009675 | -0.0036551 | -0.09549 | 0.0070197 | 0.065986 | 0.054959 | -0.017515 | 0.026767 | -0.0092115 | -0.11902 | -0.013733 | -0.032043 | -0.004578 | 0.082397 | -0.054932 | 0.045776 | 0.51727 | 122.1588 | -0.07782 | 122.1497 | 0.14648 | 0.10986 | 0.16022 | 0.009156 | -122.2595 | -122.2504 | 0.1236 | 0.086975 | -0.013733 | 0.077819 | -0.022889 | -0.036621 | -0.086976 | -0.096131 | 0.18768 | 0.20142 | 0.15106 | 0.23804 | 0.18768 | 0.11444 | 0.027465 | 0.2243 | 122.2275 | 0.01831 | 122.2366 | 0.027466 | 122.2 | -122.2778 | -122.3236 | 0.036621 | 122.1909 | -0.07782 | 0.55847
3513.1094 | 122.3648 | -0.091553 | 122.2733 | -0.12032 | -0.042816 | 0.0013094 | 0.025073 | 0.0053491 | -0.0088206 | -0.0034415 | -0.10464 | 0.0050971 | 0.062782 | 0.051968 | -0.01666 | 0.028262 | -0.0066479 | -0.091553 | -0.027466 | -0.041199 | -0.018311 | 0.054932 | -0.086975 | 0 | 0.56305 | 122.2275 | -0.068665 | 122.0718 | 0.082397 | -0.004578 | 0.068665 | 0.050354 | -122.3007 | -122.2916 | 0.14649 | 0.091553 | 0.004578 | 0.041199 | -0.045776 | 0.022888 | -0.045776 | -0.20142 | 0.17395 | 0.16022 | 0.086975 | 0.13733 | 0.064087 | 0.096131 | 0.022888 | 0.15106 | 122.1405 | 0.013733 | 122.2961 | 0.064087 | 122.319 | -122.3145 | -122.3419 | 0.073242 | 122.1634 | 0 | 0.6546
3514.8125 | 122.3831 | -0.10071 | 122.2778 | -0.11269 | -0.044953 | 0.0010958 | 0.024432 | -0.0012731 | -0.011811 | -0.0019461 | -0.077179 | 0.0065923 | 0.065345 | 0.047268 | -0.016233 | 0.027621 | -0.0053661 | -0.13275 | -0.009155 | -0.064087 | -0.09613 | -0.004578 | -0.091553 | -0.009155 | 0.55847 | 122.2275 | -0.10071 | 122.0627 | 0.082397 | 0.022888 | 0.07782 | 0.036621 | -122.287 | -122.374 | 0.09613 | 0.091553 | 0.009155 | 0.054932 | -0.027466 | 0 | -0.050354 | -0.21515 | 0.18311 | 0.17853 | 0.1236 | 0.17853 | 0.1236 | 0.059509 | -0.032043 | 0.18311 | 122.1634 | 0.054932 | 122.3282 | 0.091553 | 122.3282 | -122.3419 | -122.3785 | 0.004578 | 122.1634 | -0.032043 | 0.65918
3516.5781 | 122.4106 | -0.073242 | 122.2321 | -0.19661 | -0.044312 | 0.001523 | 0.024005 | -0.0031957 | -0.009675 | -0.0013051 | -0.013092 | 0.0048833 | 0.062995 | 0.042569 | -0.015806 | 0.024631 | -0.0036573 | -0.10071 | -0.054932 | -0.036621 | -0.013733 | 0.091553 | -0.041199 | 0.054932 | 0.51727 | 122.1588 | -0.091553 | 122.0993 | 0.11902 | 0.082397 | 0.10986 | 0.036621 | -122.287 | -122.2458 | 0.16479 | 0.12817 | 0.032043 | 0.091553 | -0.004578 | -0.018311 | -0.073243 | -0.13275 | 0.19226 | 0.18311 | 0.15564 | 0.20142 | 0.17395 | 0.12817 | 0.022888 | 0.21057 | 122.1909 | -0.018311 | 122.2504 | 0.01831 | 122.2321 | -122.2687 | -122.3236 | 0.059509 | 122.1725 | -0.027466 | 0.59052
3518.3438 | 122.4884 | -0.064087 | 122.2366 | -0.12794 | -0.043457 | 0.00088223 | 0.021441 | 0.0017175 | -0.01053 | -0.0034415 | -0.016144 | 0.0048833 | 0.064491 | 0.049618 | -0.019651 | 0.025058 | -0.0064343 | -0.07782 | -0.050354 | -0.027466 | 0.041199 | 0.16022 | 0.032043 | 0.11902 | 0.71411 | 122.1497 | -0.073242 | 122.1725 | 0.17853 | 0.14648 | 0.16022 | 0.036621 | -122.287 | -122.1954 | 0.2243 | 0.18311 | 0.09613 | 0.14649 | 0.059509 | -0.009155 | -0.086975 | -0.064087 | 0.24261 | 0.2243 | 0.21057 | 0.23346 | 0.21973 | 0.18768 | 0.068665 | 0.25177 | 122.2458 | -0.022888 | 122.2229 | 0.013733 | 122.2137 | -122.2641 | -122.3099 | 0.10529 | 122.2366 | -0.013733 | 0.7782
3520.0625 | 122.3877 | -0.082397 | 122.2778 | -0.12794 | -0.045807 | 0.0030184 | 0.02016 | -0.0046911 | -0.01117 | -0.0019461 | -0.034454 | 0.0038153 | 0.062995 | 0.041501 | -0.019438 | 0.026981 | -0.0034435 | -0.068665 | -0.041199 | -0.032043 | 0 | 0.10529 | -0.009155 | 0.068665 | 0.66834 | 122.2 | -0.073242 | 122.0673 | 0.10986 | 0.050354 | 0.09613 | 0.050354 | -122.319 | -122.2778 | 0.18768 | 0.15106 | 0.073242 | 0.10071 | 0.022888 | 0.009155 | -0.07782 | -0.21057 | 0.19226 | 0.17853 | 0.13275 | 0.16937 | 0.1236 | 0.13733 | 0.032043 | 0.18311 | 122.1405 | -0.009156 | 122.2733 | 0.041198 | 122.2824 | -122.3099 | -122.3511 | 0.082397 | 122.1497 | 0.013732 | 0.75073
3521.8438 | 122.4609 | -0.050354 | 122.2366 | -0.18898 | -0.041535 | 0.002164 | 0.025714 | 0.0034265 | -0.012452 | -0.0036551 | -0.071076 | 0.0068059 | 0.063636 | 0.049832 | -0.017729 | 0.027194 | -0.0019483 | -0.09613 | -0.022888 | -0.032043 | 0.009155 | 0.086975 | -0.041199 | 0.045776 | 0.52643 | 122.1725 | -0.07782 | 122.1542 | 0.13275 | 0.09613 | 0.15106 | 0.018311 | -122.2595 | -122.2275 | 0.13733 | 0.09613 | 0.009155 | 0.077819 | -0.009156 | -0.027466 | -0.064087 | -0.082397 | 0.18311 | 0.20142 | 0.14648 | 0.22888 | 0.17395 | 0.11902 | 0.041198 | 0.21057 | 122.2321 | 0.009155 | 122.2504 | 0.027466 | 122.2229 | -122.2687 | -122.3145 | 0.059509 | 122.2046 | -0.045776 | 0.57678
3523.6094 | 122.438 | -0.050354 | 122.2412 | -0.15846 | -0.04303 | 0.0028048 | 0.022296 | -0.0012731 | -0.01117 | -0.0036551 | -0.052765 | 0.0042425 | 0.064918 | 0.047055 | -0.017942 | 0.024631 | -0.0015209 | -0.07782 | -0.059509 | 0.004578 | 0.027466 | 0.15106 | -0.036621 | 0.050354 | 0.56763 | 122.1634 | -0.059509 | 122.1222 | 0.13733 | 0.10529 | 0.14648 | 0.054932 | -122.3007 | -122.2137 | 0.20142 | 0.10071 | 0.013733 | 0.045776 | -0.041199 | -0.009155 | -0.07782 | -0.11902 | 0.18768 | 0.19684 | 0.15564 | 0.20599 | 0.16479 | 0.14648 | 0.022888 | 0.19684 | 122.1817 | -0.064087 | 122.2229 | -0.009155 | 122.2137 | -122.2366 | -122.3007 | 0.07782 | 122.1725 | -0.027466 | 0.61798
3525.375 | 122.3328 | -0.10071 | 122.2778 | -0.19661 | -0.04068 | 0.0030184 | 0.026782 | 0.00064947 | -0.0081796 | -0.0055777 | -0.12601 | 0.0063787 | 0.064704 | 0.048977 | -0.017729 | 0.028476 | -0.0049389 | -0.13733 | -0.009155 | -0.059509 | -0.09613 | -0.059509 | -0.16479 | -0.032043 | 0.43488 | 122.2183 | -0.10529 | 122.049 | 0.027466 | -0.027466 | 0.041199 | 0.041199 | -122.287 | -122.374 | 0.041199 | 0.068665 | -0.064087 | 0.027466 | -0.10529 | -0.004578 | -0.059509 | -0.22888 | 0.12817 | 0.14191 | 0.073242 | 0.14649 | 0.07782 | 0 | -0.036621 | 0.13275 | 122.1542 | 0.050354 | 122.3236 | 0.091553 | 122.319 | -122.3373 | -122.3831 | 0.004578 | 122.1497 | -0.036621 | 0.53558
3527.0938 | 122.525 | -0.054932 | 122.2549 | -0.1432 | -0.044739 | 0.00088223 | 0.022296 | -0.0012731 | -0.010743 | -0.0021597 | -0.019196 | 0.0046697 | 0.064491 | 0.048123 | -0.017515 | 0.025058 | -0.0032299 | -0.11902 | -0.054932 | -0.018311 | -0.018311 | 0.086975 | -0.045776 | 0.054932 | 0.59509 | 122.1863 | -0.064087 | 122.1359 | 0.15564 | 0.11444 | 0.14648 | 0.036621 | -122.3099 | -122.2733 | 0.14191 | 0.10986 | 0.009156 | 0.073243 | -0.027465 | -0.009155 | -0.068665 | -0.11902 | 0.21057 | 0.20142 | 0.16937 | 0.21057 | 0.17853 | 0.10529 | 0 | 0.21973 | 122.2 | -0.036621 | 122.2504 | 0 | 122.2412 | -122.2733 | -122.319 | 0.036621 | 122.1909 | -0.064087 | 0.65002
3528.8594 | 122.4472 | -0.050354 | 122.2183 | -0.17372 | -0.043244 | 0.0040866 | 0.024859 | 0.0032129 | -0.0094614 | -0.0030141 | -0.058869 | 0.0061651 | 0.062782 | 0.05325 | -0.017301 | 0.026767 | -0.0072889 | -0.07782 | -0.059509 | -0.009155 | 0.036621 | 0.14648 | -0.022888 | 0.073242 | 0.58136 | 122.1725 | -0.073242 | 122.1542 | 0.15564 | 0.10986 | 0.15564 | 0.041199 | -122.2778 | -122.1817 | 0.19684 | 0.1236 | 0.027466 | 0.082397 | -0.013733 | -0.022888 | -0.045777 | -0.064087 | 0.20599 | 0.20599 | 0.16022 | 0.22888 | 0.18311 | 0.15564 | 0.045776 | 0.22888 | 122.2275 | -0.050354 | 122.2458 | -0.009155 | 122.2229 | -122.2275 | -122.2916 | 0.086975 | 122.2046 | -0.027466 | 0.63171
3530.625 | 122.4701 | -0.036621 | 122.2366 | -0.089798 | -0.04303 | 2.7834e-05 | 0.02315 | 0.0027857 | -0.01053 | -0.0032277 | 0.0052185 | 0.0065923 | 0.060005 | 0.044491 | -0.017515 | 0.02634 | -0.0051525 | -0.091553 | -0.045776 | -0.022888 | 0.004578 | 0.10071 | 0.009155 | 0.09613 | 0.64545 | 122.1542 | -0.073242 | 122.1542 | 0.18768 | 0.14191 | 0.16022 | 0.013733 | -122.2824 | -122.2321 | 0.13733 | 0.13275 | 0.045776 | 0.11902 | 0.032043 | -0.036621 | -0.082397 | -0.082397 | 0.2243 | 0.19684 | 0.17853 | 0.23346 | 0.21515 | 0.1236 | 0.027466 | 0.26092 | 122.2275 | -0.022888 | 122.2275 | -0.009155 | 122.1909 | -122.2595 | -122.3099 | 0.041199 | 122.1909 | -0.054932 | 0.68207
3532.3281 | 122.3465 | -0.10529 | 122.2687 | -0.097427 | -0.045594 | 0.0010958 | 0.024005 | -0.0031957 | -0.01117 | -0.00045074 | -0.068024 | 0.0080877 | 0.064491 | 0.045346 | -0.016874 | 0.026553 | -0.0040845 | -0.15106 | -0.004578 | -0.064087 | -0.07782 | -0.004578 | -0.10529 | -0.013733 | 0.5722 | 122.2321 | -0.10986 | 122.0215 | 0.032043 | -0.009155 | 0.032043 | 0.041199 | -122.2733 | -122.3465 | 0.10071 | 0.091553 | 0 | 0.050354 | -0.041199 | -0.004577 | -0.036621 | -0.24719 | 0.13733 | 0.13733 | 0.096131 | 0.14191 | 0.10071 | 0.059509 | -0.013733 | 0.14191 | 122.1313 | 0.059509 | 122.3419 | 0.10071 | 122.3373 | -122.3328 | -122.3785 | 0.027466 | 122.1268 | -0.045776 | 0.67749
3534.1406 | 122.4655 | -0.068665 | 122.2549 | -0.12794 | -0.044525 | 0.00045503 | 0.023791 | -0.0036231 | -0.01053 | -0.0055777 | -0.028351 | 0.0042425 | 0.064063 | 0.04385 | -0.017515 | 0.024844 | -0.00066651 | -0.11902 | -0.032043 | -0.032043 | -0.018311 | 0.082397 | -0.036621 | 0.064087 | 0.57678 | 122.168 | -0.07782 | 122.1268 | 0.14191 | 0.11902 | 0.14191 | 0.036622 | -122.287 | -122.2733 | 0.15106 | 0.13275 | 0.032044 | 0.09613 | -0.004578 | -0.009155 | -0.086975 | -0.12817 | 0.21057 | 0.21057 | 0.18768 | 0.21973 | 0.19684 | 0.11444 | 0.013732 | 0.21973 | 122.2046 | 0 | 122.2458 | 0.036622 | 122.2366 | -122.287 | -122.3328 | 0.050354 | 122.1954 | -0.050354 | 0.64545
3535.8438 | 122.3373 | -0.09613 | 122.2549 | -0.1432 | -0.040467 | 0.0045138 | 0.02785 | -0.0014867 | -0.0094614 | -0.0038687 | -0.13211 | 0.0063787 | 0.0615 | 0.049405 | -0.01901 | 0.027621 | -0.0049389 | -0.082397 | -0.027466 | -0.027466 | -0.045776 | 0.022888 | -0.10986 | -0.018311 | 0.50354 | 122.1909 | -0.086975 | 122.049 | 0.054932 | -0.041199 | 0.045776 | 0.068664 | -122.2824 | -122.3007 | 0.11902 | 0.077819 | -0.013733 | 0.009155 | -0.082397 | 0.009155 | -0.064087 | -0.20599 | 0.15106 | 0.14191 | 0.054931 | 0.13275 | 0.045776 | 0.050354 | -0.01831 | 0.14191 | 122.1359 | 0 | 122.2778 | 0.068664 | 122.287 | -122.2824 | -122.3419 | 0.050354 | 122.1451 | 0.013733 | 0.59967
3537.5781 | 122.4335 | -0.064087 | 122.2275 | -0.20424 | -0.044953 | 0.0034456 | 0.022937 | -0.0012731 | -0.011598 | -0.0032277 | -0.031403 | 0.0061651 | 0.062995 | 0.046841 | -0.015379 | 0.026126 | -0.0060071 | -0.11444 | -0.059509 | -0.013733 | -0.022888 | 0.059509 | -0.059509 | 0.032043 | 0.53101 | 122.1725 | -0.082397 | 122.0901 | 0.11902 | 0.068665 | 0.11902 | 0.050354 | -122.287 | -122.2504 | 0.1236 | 0.09613 | 0.004578 | 0.045776 | -0.045776 | -0.01831 | -0.054932 | -0.13733 | 0.18311 | 0.18311 | 0.13275 | 0.20142 | 0.15106 | 0.073242 | -0.009155 | 0.20142 | 122.1725 | -0.045776 | 122.2549 | 0.004578 | 122.2366 | -122.2412 | -122.3099 | 0.041199 | 122.1542 | -0.050354 | 0.59509
3539.3594 | 122.4747 | -0.041199 | 122.2549 | -0.15083 | -0.041962 | 0.0025912 | 0.024432 | 0.0023585 | -0.01053 | -0.0060049 | -0.074127 | 0.0042425 | 0.064063 | 0.046628 | -0.017515 | 0.028262 | -0.0028027 | -0.045776 | -0.032043 | -0.009155 | 0.036621 | 0.14191 | -0.045776 | 0.064087 | 0.55847 | 122.1817 | -0.054932 | 122.168 | 0.16479 | 0.10071 | 0.17395 | 0.032044 | -122.287 | -122.2183 | 0.18311 | 0.10529 | -0.004577 | 0.073242 | -0.036621 | -0.013733 | -0.073242 | -0.086975 | 0.20599 | 0.21515 | 0.14191 | 0.22888 | 0.15564 | 0.15106 | 0.045776 | 0.21973 | 122.2229 | -0.022888 | 122.2366 | 0.009156 | 122.2229 | -122.2641 | -122.3099 | 0.07782 | 122.2092 | -0.004577 | 0.59967
3541.0781 | 122.3511 | -0.11444 | 122.2641 | -0.1432 | -0.042389 | 0.0019504 | 0.026141 | 0.0036401 | -0.010743 | -0.0028005 | -0.15042 | 0.0083013 | 0.063423 | 0.040433 | -0.017942 | 0.027621 | -0.0057935 | -0.13733 | 0.004578 | -0.050354 | -0.10529 | -0.054932 | -0.16479 | -0.054932 | 0.42572 | 122.2229 | -0.09613 | 122.0261 | 0.004578 | -0.064087 | 0.036621 | 0.064087 | -122.2595 | -122.3694 | 0.059509 | 0.059509 | -0.050354 | -0.004578 | -0.11444 | 0.018311 | -0.041199 | -0.23804 | 0.11902 | 0.15106 | 0.050354 | 0.13275 | 0.032043 | -0.004578 | -0.054932 | 0.10071 | 122.1222 | 0.054932 | 122.319 | 0.11902 | 122.3373 | -122.3145 | -122.3602 | 0.009155 | 122.1405 | -0.022888 | 0.54016
3542.8594 | 122.3969 | -0.064087 | 122.2229 | -0.15083 | -0.042816 | 0.0040866 | 0.025287 | -0.00063233 | -0.009675 | -0.0068593 | -0.11685 | 0.0061651 | 0.064491 | 0.047909 | -0.016447 | 0.025912 | -0.0036573 | -0.13275 | -0.018311 | -0.041199 | -0.073242 | 0.009155 | -0.12817 | -0.018311 | 0.44403 | 122.2275 | -0.082397 | 122.0993 | 0.07782 | 0.022888 | 0.091553 | 0.022888 | -122.2412 | -122.2961 | 0.073242 | 0.045776 | -0.064087 | 0.022888 | -0.086975 | -0.01831 | 0.004578 | -0.1236 | 0.14191 | 0.15564 | 0.086975 | 0.17395 | 0.10528 | 0.050354 | -0.032043 | 0.16022 | 122.1817 | 0.022888 | 122.3099 | 0.045776 | 122.2916 | -122.2641 | -122.3053 | -0.009155 | 122.1634 | -0.068664 | 0.50812
3544.6406 | 122.4838 | -0.064087 | 122.2458 | -0.1432 | -0.044098 | 0.00066863 | 0.021869 | 0.00064947 | -0.012666 | -0.0045095 | -0.016144 | 0.0085149 | 0.063636 | 0.045773 | -0.017088 | 0.027621 | -0.0030163 | -0.082397 | -0.059509 | -0.018311 | 0.036621 | 0.15564 | 0.018311 | 0.11444 | 0.70496 | 122.1725 | -0.068665 | 122.168 | 0.2243 | 0.15106 | 0.16022 | 0.045776 | -122.3053 | -122.2092 | 0.21973 | 0.17853 | 0.082398 | 0.13275 | 0.036622 | -0.004578 | -0.073243 | -0.07782 | 0.28839 | 0.2243 | 0.21515 | 0.22888 | 0.21973 | 0.17395 | 0.054932 | 0.29297 | 122.2366 | -0.041198 | 122.2412 | 0.004578 | 122.2366 | -122.2641 | -122.3145 | 0.10071 | 122.2321 | -0.01831 | 0.76904
3546.3281 | 122.493 | -0.054932 | 122.2366 | -0.082169 | -0.045166 | 0.00066863 | 0.022082 | -0.0061865 | -0.012666 | -0.0021597 | 0.0021667 | 0.0074469 | 0.062782 | 0.050259 | -0.017942 | 0.025699 | -0.0060071 | -0.068665 | -0.054932 | -0.018311 | 0.027466 | 0.15106 | 0.027466 | 0.091553 | 0.70038 | 122.1588 | -0.050354 | 122.1542 | 0.20142 | 0.15106 | 0.16937 | 0.036621 | -122.2916 | -122.2092 | 0.20599 | 0.14649 | 0.082398 | 0.10986 | 0.045777 | 0.004578 | -0.07782 | -0.082397 | 0.25635 | 0.22431 | 0.20599 | 0.21973 | 0.20142 | 0.16937 | 0.045777 | 0.25177 | 122.2046 | -0.036621 | 122.2092 | 0 | 122.2137 | -122.2549 | -122.287 | 0.082398 | 122.2092 | -0.013733 | 0.75531
3548.0938 | 122.3373 | -0.091553 | 122.2824 | -0.10506 | -0.044525 | 2.7834e-05 | 0.023364 | -0.0031957 | -0.012879 | -0.0055777 | -0.086334 | 0.0076605 | 0.060859 | 0.048977 | -0.017729 | 0.026553 | -0.0047253 | -0.15564 | -0.009155 | -0.07782 | -0.10986 | 0.004578 | -0.10071 | -0.004578 | 0.5722 | 122.1909 | -0.10071 | 122.0261 | 0.050354 | -0.009155 | 0.036621 | 0.013733 | -122.2916 | -122.3923 | 0.096131 | 0.086975 | -0.009155 | 0.073242 | -0.022888 | -0.009155 | -0.091553 | -0.25635 | 0.14191 | 0.12817 | 0.082398 | 0.13733 | 0.091553 | 0.082398 | -0.032043 | 0.15106 | 122.1268 | 0.068665 | 122.2916 | 0.082398 | 122.2824 | -122.3602 | -122.3831 | -0.01831 | 122.1176 | -0.064087 | 0.66376
3549.8438 | 122.3923 | -0.11444 | 122.2824 | -0.17372 | -0.042816 | 0.00088223 | 0.024218 | 0.0012903 | -0.011384 | -0.0030141 | -0.086334 | 0.0085149 | 0.064491 | 0.048123 | -0.017088 | 0.028262 | -0.0040845 | -0.1236 | -0.004578 | -0.059509 | -0.07782 | -0.009155 | -0.10986 | -0.018311 | 0.58136 | 122.2137 | -0.082397 | 122.0718 | 0.068665 | 0.018311 | 0.059509 | 0.054932 | -122.287 | -122.3602 | 0.10529 | 0.09613 | 0.004578 | 0.041198 | -0.050354 | 0.032044 | -0.068665 | -0.21057 | 0.18311 | 0.17395 | 0.13275 | 0.14191 | 0.10071 | 0.050354 | -0.018311 | 0.15106 | 122.1542 | 0.054931 | 122.2961 | 0.10986 | 122.3282 | -122.3419 | -122.3648 | 0.036621 | 122.1863 | -0.009155 | 0.6958
3551.5938 | 122.3648 | -0.10986 | 122.2641 | -0.089798 | -0.044098 | 0.0034456 | 0.024005 | 0.0021447 | -0.013093 | -0.0034415 | -0.049713 | 0.0083013 | 0.066627 | 0.053036 | -0.01602 | 0.027194 | -0.00088011 | -0.15564 | -0.009155 | -0.059509 | -0.09613 | -0.009155 | -0.10986 | -0.013733 | 0.59052 | 122.2321 | -0.11902 | 122.0261 | 0.036621 | -0.027466 | 0.036621 | 0.050354 | -122.2733 | -122.3602 | 0.10071 | 0.09613 | 0 | 0.045776 | -0.050354 | -0.009156 | -0.032043 | -0.23804 | 0.14648 | 0.14648 | 0.082397 | 0.15564 | 0.091553 | 0.050354 | -0.036621 | 0.15564 | 122.1451 | 0.050354 | 122.3511 | 0.10071 | 122.3419 | -122.3236 | -122.3831 | 0.013733 | 122.1359 | -0.045777 | 0.70038
3553.2812 | 122.4701 | -0.050354 | 122.2458 | -0.18898 | -0.041321 | 0.0025912 | 0.025287 | 0.0010767 | -0.010743 | -2.3544e-05 | -0.089386 | 0.0065923 | 0.063423 | 0.039578 | -0.018583 | 0.029758 | -0.0030163 | -0.059509 | -0.045776 | -0.004578 | 0.036621 | 0.1236 | -0.041199 | 0.059509 | 0.5722 | 122.168 | -0.054932 | 122.1588 | 0.16937 | 0.11902 | 0.17853 | 0.045776 | -122.2916 | -122.2092 | 0.17395 | 0.10986 | 0.009155 | 0.064087 | -0.036621 | -0.004578 | -0.07782 | -0.086976 | 0.21973 | 0.22888 | 0.16937 | 0.23346 | 0.17395 | 0.12817 | 0.041199 | 0.22431 | 122.2137 | -0.041198 | 122.2229 | 0.004578 | 122.2183 | -122.2504 | -122.3007 | 0.086975 | 122.2092 | -0.009155 | 0.62256
3555.0469 | 122.4335 | -0.059509 | 122.2412 | -0.1432 | -0.044098 | 0.0030184 | 0.021655 | -0.0027685 | -0.012025 | -0.0032277 | -0.01004 | 0.0044561 | 0.062995 | 0.0462 | -0.017515 | 0.025912 | -0.0042981 | -0.10071 | -0.059509 | -0.022888 | -0.004578 | 0.086975 | -0.054932 | 0.045776 | 0.52643 | 122.1771 | -0.082397 | 122.0993 | 0.10529 | 0.09613 | 0.10986 | 0.036621 | -122.3007 | -122.2458 | 0.14648 | 0.10528 | 0.004577 | 0.068664 | -0.032044 | -0.022888 | -0.064087 | -0.14191 | 0.16479 | 0.16937 | 0.15564 | 0.19226 | 0.17853 | 0.10986 | 0.01831 | 0.18768 | 122.1817 | -0.036621 | 122.2595 | 0 | 122.2366 | -122.2641 | -122.3236 | 0.054931 | 122.1588 | -0.041199 | 0.58594
3556.75 | 122.3923 | -0.09613 | 122.2504 | -0.15083 | -0.042816 | 0.001523 | 0.025927 | -0.0025549 | -0.012025 | -0.0032277 | -0.1138 | 0.0059515 | 0.062141 | 0.052182 | -0.017515 | 0.028049 | -0.0079297 | -0.082397 | -0.027466 | -0.041199 | -0.027466 | 0.054932 | -0.073242 | 0.013733 | 0.63171 | 122.2092 | -0.10071 | 122.081 | 0.10986 | 0.045776 | 0.10529 | 0.054931 | -122.2778 | -122.2778 | 0.15106 | 0.10986 | 0.022888 | 0.054932 | -0.032043 | -0.004578 | -0.041199 | -0.16937 | 0.20599 | 0.20142 | 0.14191 | 0.20599 | 0.14648 | 0.096131 | 0.013733 | 0.21057 | 122.1817 | 0.013733 | 122.3099 | 0.068664 | 122.3053 | -122.2916 | -122.3511 | 0.068664 | 122.1771 | 0.013733 | 0.72784
3558.5156 | 122.4701 | -0.050354 | 122.2321 | -0.1432 | -0.041535 | 0.0053684 | 0.023578 | 0.00086307 | -0.0083932 | -0.0047231 | -0.080231 | 0.0057379 | 0.062782 | 0.050686 | -0.017301 | 0.026767 | -0.0060071 | -0.068665 | -0.022888 | -0.004578 | 0.022888 | 0.10986 | -0.027466 | 0.059509 | 0.55847 | 122.1634 | -0.050354 | 122.1542 | 0.16479 | 0.1236 | 0.17395 | 0.045776 | -122.2549 | -122.2092 | 0.16022 | 0.10986 | 0.022888 | 0.064087 | -0.022888 | 0 | -0.068665 | -0.07782 | 0.21515 | 0.2243 | 0.17395 | 0.2243 | 0.17395 | 0.11444 | 0.027466 | 0.21515 | 122.2046 | -0.01831 | 122.2137 | 0.027466 | 122.2137 | -122.2366 | -122.2824 | 0.073242 | 122.2046 | -0.018311 | 0.60883
3560.2656 | 122.4289 | -0.07782 | 122.2321 | -0.15083 | -0.042389 | 0.0034456 | 0.024218 | -0.00084593 | -0.010316 | -0.0032277 | -0.10464 | 0.0068059 | 0.063636 | 0.037869 | -0.019224 | 0.028049 | -0.0051525 | -0.12817 | -0.032043 | -0.054932 | -0.064087 | 0.022888 | -0.09613 | 0.004578 | 0.4715 | 122.1634 | -0.091553 | 122.113 | 0.11902 | 0.068665 | 0.13275 | 0.022888 | -122.2641 | -122.2961 | 0.10071 | 0.082398 | -0.01831 | 0.05951 | -0.041198 | -0.013733 | -0.068665 | -0.11902 | 0.19684 | 0.21057 | 0.14649 | 0.2243 | 0.16022 | 0.07782 | -0.009155 | 0.21057 | 122.2046 | 0.022889 | 122.2549 | 0.045777 | 122.2412 | -122.287 | -122.3236 | 0.013733 | 122.1909 | -0.050354 | 0.54932
3562.0156 | 122.4152 | -0.07782 | 122.2412 | -0.18898 | -0.041962 | 0.0023776 | 0.021441 | -0.0010595 | -0.010743 | -0.0032277 | -0.04361 | 0.0068059 | 0.064063 | 0.052182 | -0.015592 | 0.026126 | -0.0089977 | -0.11444 | -0.041199 | -0.022888 | 0 | 0.10071 | -0.054932 | 0.036621 | 0.53558 | 122.1725 | -0.068665 | 122.0993 | 0.11902 | 0.086975 | 0.1236 | 0.054932 | -122.2824 | -122.2412 | 0.17853 | 0.11444 | 0.022888 | 0.059509 | -0.032044 | 0.009155 | -0.068665 | -0.14191 | 0.19684 | 0.20142 | 0.16479 | 0.19226 | 0.15564 | 0.1236 | 0.022888 | 0.18768 | 122.168 | -0.018311 | 122.2412 | 0.036621 | 122.2504 | -122.2641 | -122.3099 | 0.07782 | 122.1771 | -0.036621 | 0.6134
3563.7812 | 122.3373 | -0.11902 | 122.2778 | -0.097427 | -0.044525 | 0.002164 | 0.022937 | -0.0019141 | -0.012025 | -0.0038687 | -0.064972 | 0.0080877 | 0.06385 | 0.040219 | -0.019224 | 0.025485 | -0.0045117 | -0.15106 | -0.013733 | -0.054932 | -0.082397 | 0.004578 | -0.09613 | -0.004578 | 0.58594 | 122.2229 | -0.11902 | 122.0123 | 0.032043 | -0.004578 | 0.022888 | 0.064087 | -122.2916 | -122.3602 | 0.1236 | 0.11444 | 0.022889 | 0.050354 | -0.041198 | 0 | -0.054932 | -0.2655 | 0.15106 | 0.14191 | 0.11444 | 0.14191 | 0.11444 | 0.05951 | -0.027465 | 0.15106 | 122.1313 | 0.041199 | 122.3419 | 0.10529 | 122.3419 | -122.3328 | -122.3969 | 0.036622 | 122.1313 | -0.032043 | 0.70496
3565.4844 | 122.3877 | -0.086975 | 122.2549 | -0.097427 | -0.043244 | 0.0010958 | 0.023364 | -0.0019141 | -0.009675 | -0.0055777 | -0.10464 | 0.0065923 | 0.06385 | 0.051327 | -0.017729 | 0.028049 | -0.0049389 | -0.091553 | -0.013733 | -0.064087 | -0.032043 | 0.050354 | -0.086975 | 0.022888 | 0.61798 | 122.2 | -0.073242 | 122.0947 | 0.10529 | 0.022888 | 0.09613 | 0.022888 | -122.2687 | -122.287 | 0.13733 | 0.10986 | 0 | 0.086975 | -0.022888 | 0.013733 | -0.054932 | -0.16022 | 0.19226 | 0.1831 | 0.10986 | 0.16937 | 0.09613 | 0.11444 | 0.032044 | 0.17853 | 122.168 | 0.050354 | 122.2733 | 0.073242 | 122.287 | -122.319 | -122.3282 | 0.054932 | 122.1817 | -0.004578 | 0.70496
3567.25 | 122.4335 | -0.054932 | 122.2183 | -0.16609 | -0.041321 | 0.0036594 | 0.023578 | -0.00020513 | -0.0088206 | -0.0045095 | -0.025299 | 0.0055243 | 0.063209 | 0.047268 | -0.018156 | 0.027194 | -0.0049389 | -0.082397 | -0.068665 | -0.004578 | 0.022888 | 0.15106 | -0.027466 | 0.07782 | 0.56305 | 122.1405 | -0.059509 | 122.1268 | 0.16937 | 0.091553 | 0.15564 | 0.050354 | -122.287 | -122.1954 | 0.20599 | 0.13275 | 0.027466 | 0.082398 | -0.022888 | -0.004577 | -0.07782 | -0.091553 | 0.22431 | 0.21057 | 0.14649 | 0.21515 | 0.15106 | 0.15564 | 0.027466 | 0.22888 | 122.1863 | -0.064087 | 122.2 | -0.013733 | 122.1954 | -122.2229 | -122.2778 | 0.07782 | 122.1817 | -0.027465 | 0.61798
3569 | 122.4426 | -0.050354 | 122.2595 | -0.12032 | -0.044098 | 0.0030184 | 0.019946 | -0.0021277 | -0.011384 | -0.0032277 | -0.031403 | 0.0061651 | 0.06385 | 0.040646 | -0.018156 | 0.02634 | -0.0036573 | -0.073242 | -0.041199 | -0.032043 | 0.045776 | 0.14648 | 0.013733 | 0.09613 | 0.72327 | 122.1542 | -0.059509 | 122.1176 | 0.19226 | 0.12817 | 0.15106 | 0.018311 | -122.3007 | -122.2137 | 0.19684 | 0.14648 | 0.064087 | 0.12817 | 0.045776 | -0.009155 | -0.10529 | -0.14191 | 0.24261 | 0.20142 | 0.17853 | 0.21057 | 0.18768 | 0.17853 | 0.077819 | 0.25177 | 122.1771 | -0.009156 | 122.2137 | 0.009155 | 122.2046 | -122.2916 | -122.319 | 0.09613 | 122.168 | -0.022888 | 0.77362
3570.7031 | 122.3328 | -0.091553 | 122.2595 | -0.15083 | -0.041107 | 0.0013094 | 0.026141 | 0.00043587 | -0.010102 | -0.0042959 | -0.11075 | 0.0063787 | 0.061927 | 0.042142 | -0.017088 | 0.02634 | -0.0075025 | -0.14648 | -0.013733 | -0.032043 | -0.10071 | -0.045776 | -0.15106 | -0.059509 | 0.43488 | 122.2229 | -0.091553 | 122.0261 | 0.004578 | -0.036621 | 0.032043 | 0.05951 | -122.2733 | -122.3602 | 0.045777 | 0.032044 | -0.059509 | -0.027466 | -0.11902 | 0 | -0.036621 | -0.23346 | 0.096131 | 0.1236 | 0.054932 | 0.1236 | 0.054932 | -0.013733 | -0.068665 | 0.096131 | 122.1176 | 0.01831 | 122.3145 | 0.07782 | 122.3145 | -122.2916 | -122.3511 | -0.009155 | 122.1176 | -0.054931 | 0.52643
3572.4688 | 122.4609 | -0.059509 | 122.2458 | -0.18898 | -0.041962 | 0.0034456 | 0.023578 | -0.0049047 | -0.011384 | -0.0036551 | -0.080231 | 0.0072333 | 0.063636 | 0.050473 | -0.019651 | 0.028049 | -0.0051525 | -0.10986 | -0.036621 | -0.041199 | -0.027466 | 0.054932 | -0.086975 | 0 | 0.51727 | 122.1817 | -0.068665 | 122.1497 | 0.13733 | 0.07782 | 0.14191 | 0.01831 | -122.2824 | -122.2733 | 0.11444 | 0.059509 | -0.027466 | 0.041199 | -0.045776 | -0.009156 | -0.064087 | -0.096131 | 0.19684 | 0.20142 | 0.13733 | 0.21057 | 0.14649 | 0.096131 | 0.013733 | 0.20599 | 122.2183 | 0.004578 | 122.2504 | 0.022888 | 122.2412 | -122.287 | -122.3145 | 0.032043 | 122.2092 | -0.050354 | 0.57678
3574.1719 | 122.4701 | -0.041199 | 122.2458 | -0.24239 | -0.041535 | 0.0028048 | 0.022937 | -0.00063233 | -0.0092478 | -0.0057913 | -0.058869 | 0.0031745 | 0.06385 | 0.044705 | -0.017301 | 0.027194 | -0.0042981 | -0.054932 | -0.054932 | 0 | 0.018311 | 0.1236 | -0.032043 | 0.07782 | 0.5722 | 122.1817 | -0.073242 | 122.1634 | 0.17853 | 0.11444 | 0.1831 | 0.041199 | -122.3007 | -122.2275 | 0.16479 | 0.11902 | 0.009156 | 0.07782 | -0.032043 | -0.032043 | -0.064087 | -0.082398 | 0.21973 | 0.2243 | 0.15564 | 0.25635 | 0.18768 | 0.1236 | 0.018311 | 0.25177 | 122.2366 | -0.054932 | 122.2549 | -0.013733 | 122.2229 | -122.2458 | -122.319 | 0.05951 | 122.2046 | -0.013733 | 0.6134
3575.9375 | 122.4701 | -0.036621 | 122.2778 | -0.18135 | -0.047303 | 0.0017368 | 0.021441 | 0.0017175 | -0.012879 | -0.0079275 | 0.014374 | 0.0046697 | 0.064704 | 0.0509 | -0.017729 | 0.026553 | -0.0055799 | -0.07782 | -0.027466 | -0.027466 | 0.045776 | 0.15564 | 0.041199 | 0.10071 | 0.74158 | 122.1817 | -0.054932 | 122.1405 | 0.19226 | 0.14648 | 0.16937 | 0.009155 | -122.3053 | -122.2321 | 0.19226 | 0.13733 | 0.07782 | 0.12817 | 0.068665 | -0.018311 | -0.09613 | -0.13733 | 0.22888 | 0.20599 | 0.18311 | 0.22431 | 0.20142 | 0.18311 | 0.073242 | 0.24719 | 122.1954 | 0 | 122.2366 | 0.009155 | 122.2183 | -122.3053 | -122.3328 | 0.082397 | 122.1771 | -0.041199 | 0.7782
3577.625 | 122.3328 | -0.091553 | 122.287 | -0.18898 | -0.042176 | 0.002164 | 0.026141 | 0.0017175 | -0.01053 | -0.0047231 | -0.11075 | 0.0068059 | 0.063636 | 0.051114 | -0.018369 | 0.028476 | -0.0064343 | -0.086975 | -0.018311 | -0.036621 | -0.064087 | 0.022888 | -0.1236 | -0.032043 | 0.51727 | 122.2366 | -0.086975 | 122.049 | 0.032043 | -0.022888 | 0.032043 | 0.054932 | -122.3053 | -122.3511 | 0.11444 | 0.05951 | -0.032043 | 0.004578 | -0.086975 | 0.004578 | -0.050354 | -0.23804 | 0.1236 | 0.1236 | 0.068665 | 0.11902 | 0.064087 | 0.059509 | -0.027466 | 0.11902 | 122.1359 | 0.01831 | 122.3236 | 0.073242 | 122.3282 | -122.3236 | -122.374 | 0.027466 | 122.1405 | 0.004578 | 0.60883
3579.375 | 122.3602 | -0.086975 | 122.2458 | -0.12794 | -0.041962 | 0.0019504 | 0.022937 | 0.0019311 | -0.010316 | -0.0055777 | -0.1199 | 0.0057379 | 0.0615 | 0.0462 | -0.015379 | 0.029117 | -0.0036573 | -0.13275 | 0 | -0.059509 | -0.10529 | -0.027466 | -0.14648 | -0.054932 | 0.4303 | 122.2229 | -0.091553 | 122.0535 | 0.036621 | -0.022888 | 0.041199 | 0.027466 | -122.2458 | -122.3511 | 0.059509 | 0.032043 | -0.059509 | 0.004577 | -0.086975 | -0.004578 | -0.022889 | -0.19226 | 0.1236 | 0.12817 | 0.064087 | 0.13275 | 0.068665 | 0.032043 | -0.045777 | 0.12817 | 122.1451 | 0.059509 | 122.3145 | 0.086975 | 122.3099 | -122.3053 | -122.3373 | -0.018311 | 122.1405 | -0.045776 | 0.51727
3581.1406 | 122.4289 | -0.068665 | 122.2549 | -0.18135 | -0.043457 | 0.00066863 | 0.021655 | 0.0012903 | -0.01053 | -0.0045095 | -0.0008851 | 0.0065923 | 0.062995 | 0.04855 | -0.01602 | 0.027194 | -0.0040845 | -0.12817 | -0.041199 | -0.027466 | -0.036621 | 0.059509 | -0.059509 | 0.041199 | 0.54016 | 122.1451 | -0.054932 | 122.1039 | 0.12817 | 0.068665 | 0.1236 | 0.041199 | -122.2961 | -122.2916 | 0.12817 | 0.10986 | 0.009156 | 0.068665 | -0.032043 | 0.013733 | -0.10986 | -0.15106 | 0.19684 | 0.19226 | 0.13733 | 0.17853 | 0.1236 | 0.086975 | -0.009155 | 0.18311 | 122.1588 | -0.013733 | 122.2 | 0.027466 | 122.2137 | -122.2824 | -122.3099 | 0.032044 | 122.1725 | -0.059509 | 0.60883
3582.8594 | 122.3557 | -0.10071 | 122.2824 | -0.15083 | -0.042603 | 0.002164 | 0.020587 | -0.0057593 | -0.011811 | -0.0036551 | -0.025299 | 0.0053107 | 0.062995 | 0.0462 | -0.017729 | 0.027621 | -0.0051525 | -0.07782 | -0.022888 | -0.027466 | -0.018311 | 0.07782 | -0.027466 | 0.050354 | 0.67291 | 122.1954 | -0.10529 | 122.0535 | 0.073242 | 0.050354 | 0.054932 | 0.073242 | -122.3053 | -122.3007 | 0.17853 | 0.15106 | 0.073242 | 0.07782 | 0 | -0.004578 | -0.086975 | -0.22888 | 0.17395 | 0.15564 | 0.15106 | 0.16022 | 0.15564 | 0.10529 | 0.009155 | 0.17853 | 122.1588 | 0.004578 | 122.3007 | 0.07782 | 122.2961 | -122.3099 | -122.3877 | 0.082397 | 122.1542 | 0.022888 | 0.77362
3584.6406 | 122.4472 | -0.050354 | 122.2275 | -0.24239 | -0.043885 | 0.0040866 | 0.022082 | -0.0012731 | -0.01053 | -0.00045074 | -0.022247 | 0.0053107 | 0.061714 | 0.049191 | -0.016874 | 0.026553 | -0.0042981 | -0.068665 | -0.045776 | 0.004578 | 0.022888 | 0.13733 | -0.032043 | 0.068665 | 0.5722 | 122.168 | -0.064087 | 122.1451 | 0.15106 | 0.09613 | 0.15106 | 0.054932 | -122.2733 | -122.2046 | 0.18768 | 0.11902 | 0.018311 | 0.064087 | -0.036621 | -0.013733 | -0.059509 | -0.082397 | 0.20142 | 0.20142 | 0.14648 | 0.21515 | 0.16022 | 0.13275 | 0.01831 | 0.21515 | 122.2092 | -0.050354 | 122.2321 | 0.004578 | 122.2183 | -122.2229 | -122.2916 | 0.073242 | 122.1954 | -0.018311 | 0.62256
3586.3906 | 122.3465 | -0.09613 | 122.2778 | -0.16609 | -0.041748 | 0.0010958 | 0.026782 | -0.00084593 | -0.0098886 | -0.0038687 | -0.13211 | 0.0070197 | 0.062995 | 0.050686 | -0.017729 | 0.028262 | 0.00082889 | -0.14191 | -0.013733 | -0.041199 | -0.091553 | -0.036621 | -0.17395 | -0.045776 | 0.44861 | 122.2595 | -0.10529 | 122.0398 | 0.013733 | -0.068665 | 0.032043 | 0.054931 | -122.2916 | -122.3694 | 0.059509 | 0.050354 | -0.07782 | -0.004577 | -0.13275 | -0.009156 | -0.018311 | -0.23804 | 0.10986 | 0.12817 | 0.027465 | 0.13733 | 0.036621 | 0.004578 | -0.050354 | 0.11902 | 122.1451 | 0.027466 | 122.3648 | 0.082397 | 122.3557 | -122.319 | -122.3831 | 0.004577 | 122.1359 | -0.045777 | 0.54474
3588.1562 | 122.4884 | -0.064087 | 122.2321 | -0.13557 | -0.041535 | 0.00045503 | 0.021014 | 8.47e-06 | -0.011811 | -0.0028005 | -0.016144 | 0.0042425 | 0.062568 | 0.0462 | -0.016233 | 0.025485 | -0.0034435 | -0.07782 | -0.036621 | -0.032043 | 0.032043 | 0.15106 | 0.004578 | 0.11444 | 0.71869 | 122.1725 | -0.059509 | 122.1497 | 0.21973 | 0.16479 | 0.16022 | 0.032044 | -122.2687 | -122.2 | 0.21515 | 0.17853 | 0.068665 | 0.14648 | 0.036621 | 0.004578 | -0.05951 | -0.082398 | 0.28381 | 0.2243 | 0.22888 | 0.21973 | 0.2243 | 0.18311 | 0.064086 | 0.27924 | 122.2092 | -0.004578 | 122.2321 | 0.027466 | 122.2366 | -122.2641 | -122.2916 | 0.09613 | 122.2137 | -0.013733 | 0.78278
3589.8594 | 122.3328 | -0.10071 | 122.2733 | -0.18898 | -0.042816 | 0.0025912 | 0.023364 | 0.0015039 | -0.0083932 | -0.0032277 | -0.13516 | 0.0061651 | 0.064704 | 0.0462 | -0.01602 | 0.026553 | -0.0042981 | -0.12817 | 0.009155 | -0.041199 | -0.11902 | -0.050354 | -0.16937 | -0.059509 | 0.44403 | 122.2183 | -0.086975 | 122.0215 | 0.013733 | -0.050354 | 0.036621 | 0.059509 | -122.2641 | -122.3923 | 0.050354 | 0.041199 | -0.068665 | -0.01831 | -0.12817 | 0.013733 | -0.054931 | -0.25177 | 0.11444 | 0.13733 | 0.050354 | 0.1236 | 0.036621 | -0.009155 | -0.07782 | 0.10071 | 122.1085 | 0.050354 | 122.3053 | 0.10986 | 122.319 | -122.3145 | -122.3602 | -0.018311 | 122.1222 | -0.027466 | 0.54474
3591.6094 | 122.3877 | -0.068665 | 122.2641 | -0.097427 | -0.043244 | 0.0019504 | 0.022082 | 0.00064947 | -0.01053 | -0.0070731 | -0.1077 | 0.0046697 | 0.064063 | 0.0556 | -0.018797 | 0.026553 | -0.0036573 | -0.10986 | -0.018311 | -0.064087 | -0.054932 | 0.032043 | -0.073242 | 0.013733 | 0.62256 | 122.2137 | -0.082397 | 122.0627 | 0.10071 | 0.022888 | 0.07782 | 0.004578 | -122.2824 | -122.319 | 0.10071 | 0.082398 | -0.004577 | 0.07782 | -0.009155 | -0.013732 | -0.050354 | -0.20142 | 0.16937 | 0.14649 | 0.091553 | 0.16022 | 0.10528 | 0.09613 | 0.009155 | 0.18311 | 122.1451 | 0.045776 | 122.2961 | 0.050354 | 122.2824 | -122.3282 | -122.3465 | 0.013733 | 122.1313 | -0.041198 | 0.69122
3593.375 | 122.3831 | -0.082397 | 122.2595 | -0.089798 | -0.042603 | 0.002164 | 0.027209 | -0.0019141 | -0.009675 | -0.0062185 | -0.098541 | 0.0076605 | 0.063423 | 0.047482 | -0.017301 | 0.028262 | -0.0021619 | -0.086975 | -0.018311 | -0.032043 | -0.027466 | 0.059509 | -0.082397 | 0.018311 | 0.64087 | 122.2092 | -0.09613 | 122.0901 | 0.10986 | 0.050354 | 0.09613 | 0.050354 | -122.2778 | -122.287 | 0.14191 | 0.10071 | 0 | 0.050354 | -0.050354 | -0.013733 | -0.050354 | -0.16937 | 0.19226 | 0.17853 | 0.13275 | 0.19226 | 0.14648 | 0.091552 | 0.004577 | 0.20599 | 122.1863 | 0.013732 | 122.3053 | 0.064086 | 122.2916 | -122.2916 | -122.3557 | 0.054931 | 122.1725 | -0.004578 | 0.72327
3595.1406 | 122.4243 | -0.054932 | 122.2321 | -0.10506 | -0.04303 | 0.0010958 | 0.020587 | -0.0023413 | -0.010102 | -0.0036551 | -0.01004 | 0.0059515 | 0.064918 | 0.042996 | -0.017729 | 0.025272 | -0.0081433 | -0.1236 | -0.027466 | -0.027466 | -0.027466 | 0.059509 | -0.064087 | 0.032043 | 0.55847 | 122.1909 | -0.082397 | 122.0947 | 0.12817 | 0.086975 | 0.11902 | 0.027466 | -122.2595 | -122.2595 | 0.11444 | 0.086975 | -0.009155 | 0.059509 | -0.036621 | -0.027465 | -0.041199 | -0.13733 | 0.18311 | 0.17395 | 0.14191 | 0.20142 | 0.16937 | 0.086975 | 0 | 0.21057 | 122.1771 | 0 | 122.2733 | 0.027466 | 122.2458 | -122.2595 | -122.3145 | 0.027466 | 122.1497 | -0.068664 | 0.6134
3596.9062 | 122.3373 | -0.10529 | 122.2733 | -0.13557 | -0.043457 | 0.00066863 | 0.021655 | -0.0064001 | -0.0071116 | -0.0028005 | -0.034454 | 0.0044561 | 0.064277 | 0.04855 | -0.018369 | 0.027621 | -0.00088011 | -0.14191 | -0.018311 | -0.050354 | -0.073242 | 0.041199 | -0.09613 | 0 | 0.60425 | 122.2183 | -0.10071 | 122.0306 | 0.064087 | 0.004578 | 0.027466 | 0.054932 | -122.2916 | -122.3465 | 0.14649 | 0.10529 | 0.009156 | 0.050354 | -0.045776 | 0.004578 | -0.054931 | -0.24261 | 0.16937 | 0.13275 | 0.10986 | 0.12817 | 0.10529 | 0.091553 | -0.022888 | 0.1648 | 122.1313 | 0.032043 | 122.319 | 0.086975 | 122.3236 | -122.3236 | -122.374 | 0.032044 | 122.1359 | -0.036621 | 0.70953
3598.6094 | 122.4976 | -0.054932 | 122.2458 | -0.1432 | -0.044312 | 0.00088223 | 0.0208 | 8.47e-06 | -0.011598 | -0.0040823 | -0.031403 | 0.0042425 | 0.06385 | 0.044064 | -0.01901 | 0.024844 | -0.0049389 | -0.064087 | -0.045776 | -0.018311 | 0.054932 | 0.16937 | 0.027466 | 0.11444 | 0.75989 | 122.1771 | -0.054932 | 122.168 | 0.21515 | 0.15564 | 0.16479 | 0.036621 | -122.2916 | -122.1909 | 0.22431 | 0.16937 | 0.082398 | 0.13275 | 0.045777 | 0 | -0.068665 | -0.07782 | 0.27008 | 0.21973 | 0.21057 | 0.21973 | 0.21057 | 0.18768 | 0.073243 | 0.27008 | 122.2229 | -0.027465 | 122.2321 | 0.009156 | 122.2321 | -122.2641 | -122.3007 | 0.10986 | 122.2229 | -0.009155 | 0.81482
3600.3594 | 122.3511 | -0.07782 | 122.2778 | -0.11269 | -0.041962 | 0.0017368 | 0.020373 | -0.0021277 | -0.010102 | -0.0030141 | -0.052765 | 0.0055243 | 0.061714 | 0.047482 | -0.017515 | 0.026767 | -0.0079297 | -0.068665 | -0.027466 | -0.018311 | -0.004578 | 0.09613 | -0.013733 | 0.073242 | 0.68207 | 122.1771 | -0.07782 | 122.0535 | 0.086975 | 0.036621 | 0.064087 | 0.059509 | -122.3053 | -122.2824 | 0.17395 | 0.15106 | 0.064087 | 0.091553 | 0.004578 | 0 | -0.10071 | -0.2243 | 0.16479 | 0.14191 | 0.11444 | 0.14191 | 0.11444 | 0.11444 | 0.013733 | 0.16479 | 122.1313 | -0.009155 | 122.2549 | 0.050354 | 122.2549 | -122.2961 | -122.3557 | 0.073242 | 122.1313 | 0.009155 | 0.75989
3602.125 | 122.3877 | -0.09613 | 122.287 | -0.17372 | -0.041321 | 0.001523 | 0.026141 | 0.00043587 | -0.012239 | -0.0042959 | -0.1199 | 0.0065923 | 0.063209 | 0.049191 | -0.01666 | 0.027194 | -0.0040845 | -0.07782 | -0.013733 | -0.036621 | -0.022888 | 0.064087 | -0.068665 | 0.009155 | 0.64545 | 122.2 | -0.064087 | 122.0856 | 0.091553 | 0.013733 | 0.086975 | 0.059509 | -122.3007 | -122.3099 | 0.16022 | 0.10528 | 0.027465 | 0.045776 | -0.032044 | 0.032043 | -0.086975 | -0.20142 | 0.18768 | 0.1831 | 0.10986 | 0.15106 | 0.07782 | 0.10071 | 0.013733 | 0.15564 | 122.1497 | 0.022888 | 122.2641 | 0.082397 | 122.2961 | -122.3236 | -122.3511 | 0.073242 | 122.1817 | 0.01831 | 0.74158
3603.8906 | 122.4976 | -0.064087 | 122.2366 | -0.13557 | -0.042176 | 2.7834e-05 | 0.019946 | -0.0010595 | -0.01352 | -0.0028005 | -0.0069885 | 0.0061651 | 0.06385 | 0.042782 | -0.018797 | 0.026767 | -0.0068615 | -0.068665 | -0.032043 | -0.013733 | 0.027466 | 0.16479 | 0.032043 | 0.10986 | 0.75989 | 122.1542 | -0.064087 | 122.1542 | 0.20142 | 0.14191 | 0.16479 | 0.050354 | -122.2687 | -122.2092 | 0.22888 | 0.17395 | 0.09613 | 0.1236 | 0.045776 | 0 | -0.082397 | -0.082397 | 0.2655 | 0.22888 | 0.20599 | 0.22888 | 0.20599 | 0.17853 | 0.041199 | 0.2655 | 122.2183 | -0.01831 | 122.2183 | 0.032044 | 122.2183 | -122.2504 | -122.3007 | 0.091553 | 122.2183 | -0.004578 | 0.82398
3605.6406 | 122.4792 | -0.059509 | 122.2595 | -0.16609 | -0.043457 | 0.0017368 | 0.021655 | -0.0019141 | -0.0098886 | -0.0038687 | -0.0008851 | 0.0042425 | 0.063209 | 0.04321 | -0.018583 | 0.028049 | -0.00045291 | -0.10071 | -0.041199 | -0.027466 | 0 | 0.1236 | -0.013733 | 0.068665 | 0.65918 | 122.168 | -0.045776 | 122.1268 | 0.19226 | 0.11902 | 0.16479 | 0.032043 | -122.3007 | -122.2595 | 0.1831 | 0.12817 | 0.045776 | 0.096131 | 0.013733 | 0.013733 | -0.091552 | -0.13275 | 0.25177 | 0.2243 | 0.17853 | 0.21057 | 0.16479 | 0.15106 | 0.027466 | 0.23804 | 122.1725 | -0.013733 | 122.2137 | 0.01831 | 122.2275 | -122.287 | -122.3053 | 0.059509 | 122.1863 | -0.041199 | 0.71869
3607.4062 | 122.3465 | -0.10986 | 122.287 | -0.1432 | -0.04538 | 2.7834e-05 | 0.021014 | -0.0021277 | -0.012666 | -0.0025869 | -0.025299 | 0.0050971 | 0.063423 | 0.046628 | -0.015806 | 0.026981 | -0.0025891 | -0.09613 | -0.041199 | -0.022888 | -0.041199 | 0.050354 | -0.068665 | 0.022888 | 0.6546 | 122.2229 | -0.086975 | 122.0398 | 0.054932 | 0.009155 | 0.032043 | 0.086975 | -122.3282 | -122.3282 | 0.16022 | 0.13275 | 0.041198 | 0.045776 | -0.045777 | 0.022888 | -0.064087 | -0.24719 | 0.16479 | 0.14191 | 0.11902 | 0.11902 | 0.09613 | 0.073242 | -0.018311 | 0.14191 | 122.1268 | -0.018311 | 122.3099 | 0.068664 | 122.3328 | -122.3099 | -122.374 | 0.068664 | 122.1497 | 0.013733 | 0.76447
3609.1094 | 122.4335 | -0.050354 | 122.2412 | -0.12032 | -0.044525 | 0.0013094 | 0.021869 | 0.0017175 | -0.011384 | -0.0021597 | -0.022247 | 0.0059515 | 0.062782 | 0.049405 | -0.017088 | 0.026981 | -0.0081433 | -0.068665 | -0.041199 | -0.018311 | 0.045776 | 0.13733 | 0.013733 | 0.086975 | 0.72784 | 122.168 | -0.07782 | 122.1222 | 0.15564 | 0.11902 | 0.14191 | 0.032043 | -122.2824 | -122.1954 | 0.18768 | 0.13733 | 0.064087 | 0.10529 | 0.032044 | -0.027466 | -0.073242 | -0.11902 | 0.20599 | 0.19226 | 0.16937 | 0.21973 | 0.19684 | 0.15564 | 0.064087 | 0.23346 | 122.2 | -0.022888 | 122.2458 | 0.009155 | 122.2183 | -122.2595 | -122.319 | 0.09613 | 122.1725 | -0.018311 | 0.7782
3610.8594 | 122.4792 | -0.050354 | 122.2549 | -0.10506 | -0.045594 | 0.0030184 | 0.022082 | -0.0019141 | -0.011384 | -0.0015189 | -0.0039367 | 0.0046697 | 0.064277 | 0.048123 | -0.017942 | 0.026981 | -0.0077161 | -0.054932 | -0.050354 | -0.013733 | 0.045776 | 0.17395 | 0.013733 | 0.10529 | 0.76446 | 122.1588 | -0.045776 | 122.1451 | 0.20599 | 0.15564 | 0.16937 | 0.036621 | -122.3053 | -122.2092 | 0.2243 | 0.15564 | 0.064087 | 0.11902 | 0.027466 | 0.004578 | -0.096131 | -0.10986 | 0.25635 | 0.21973 | 0.20599 | 0.21515 | 0.20142 | 0.18768 | 0.059509 | 0.25177 | 122.1909 | -0.036621 | 122.2046 | 0 | 122.2092 | -122.2687 | -122.3007 | 0.09613 | 122.1954 | -0.004578 | 0.81482
3612.6094 | 122.3923 | -0.11444 | 122.2504 | -0.097427 | -0.046448 | 0.0034456 | 0.024432 | -0.0010595 | -0.012452 | -0.0036551 | -0.10159 | 0.0055243 | 0.062354 | 0.051114 | -0.017515 | 0.026767 | -0.0079297 | -0.13275 | -0.004578 | -0.036621 | -0.082397 | -0.018311 | -0.10529 | -0.009155 | 0.59509 | 122.2183 | -0.091553 | 122.0673 | 0.068665 | 0.013733 | 0.064087 | 0.07782 | -122.2549 | -122.3328 | 0.09613 | 0.10529 | 0.009155 | 0.027466 | -0.068665 | 0.022888 | -0.032043 | -0.1831 | 0.18311 | 0.17853 | 0.12817 | 0.15564 | 0.10529 | 0.01831 | -0.045776 | 0.16022 | 122.1588 | 0.032043 | 122.3099 | 0.10986 | 122.3328 | -122.287 | -122.3419 | 0.032044 | 122.1817 | -0.01831 | 0.70953
3614.3125 | 122.4701 | -0.045776 | 122.2412 | -0.17372 | -0.043457 | 0.0010958 | 0.025073 | -0.0038367 | -0.008607 | -0.0038687 | -0.098541 | 0.0070197 | 0.061927 | 0.046628 | -0.017942 | 0.027621 | -0.0047253 | -0.050354 | -0.041199 | -0.004578 | 0.018311 | 0.10986 | -0.041199 | 0.068665 | 0.59509 | 122.1863 | -0.082397 | 122.1725 | 0.16022 | 0.10071 | 0.1831 | 0.041198 | -122.2824 | -122.2229 | 0.15564 | 0.11444 | 0.004577 | 0.073243 | -0.036621 | -0.036621 | -0.054932 | -0.068665 | 0.20599 | 0.22888 | 0.14648 | 0.2655 | 0.18311 | 0.11444 | 0.022889 | 0.24261 | 122.2549 | -0.036621 | 122.2687 | 0.004577 | 122.2321 | -122.2458 | -122.3236 | 0.064087 | 122.2183 | -0.004578 | 0.64087
3616.0781 | 122.3877 | -0.086975 | 122.2687 | -0.17372 | -0.044525 | 0.0025912 | 0.025287 | 0.0036401 | -0.0092478 | -0.0034415 | -0.1199 | 0.0061651 | 0.062354 | 0.045987 | -0.019438 | 0.026553 | -0.0036573 | -0.086975 | -0.009155 | -0.059509 | -0.013733 | 0.073242 | -0.068665 | 0.004578 | 0.63171 | 122.2183 | -0.091553 | 122.081 | 0.09613 | 0.032043 | 0.10529 | 0.027466 | -122.2778 | -122.2824 | 0.16022 | 0.091553 | 0.01831 | 0.064087 | -0.009156 | -0.004578 | -0.050354 | -0.18768 | 0.1831 | 0.19226 | 0.11902 | 0.19684 | 0.1236 | 0.13275 | 0.045776 | 0.18768 | 122.1725 | 0.050354 | 122.3099 | 0.07782 | 122.3053 | -122.3282 | -122.3602 | 0.073242 | 122.168 | 0 | 0.71869
3617.8281 | 122.3969 | -0.068665 | 122.2458 | -0.097427 | -0.043244 | 0.002164 | 0.024005 | -0.00084593 | -0.009675 | -0.0030141 | -0.083283 | 0.0055243 | 0.061714 | 0.042996 | -0.019651 | 0.026981 | -0.0042981 | -0.086975 | -0.013733 | -0.041199 | -0.032043 | 0.068665 | -0.073242 | 0.013733 | 0.66376 | 122.2137 | -0.091553 | 122.0947 | 0.09613 | 0.045776 | 0.09613 | 0.027466 | -122.2595 | -122.2778 | 0.13733 | 0.082398 | -0.004577 | 0.054932 | -0.032043 | -0.022888 | -0.032044 | -0.15106 | 0.16479 | 0.16479 | 0.11444 | 0.18768 | 0.13733 | 0.10986 | 0.009156 | 0.18768 | 122.1863 | 0.027466 | 122.3053 | 0.054932 | 122.2824 | -122.287 | -122.3373 | 0.036622 | 122.1634 | -0.01831 | 0.73242
3619.5938 | 122.4609 | -0.041199 | 122.2412 | -0.19661 | -0.043457 | 0.0043002 | 0.024432 | 0.0021447 | -0.010102 | -0.0040823 | -0.058869 | 0.0070197 | 0.062782 | 0.044278 | -0.015806 | 0.026981 | -0.0047253 | -0.064087 | -0.045776 | 0 | 0.027466 | 0.13275 | -0.013733 | 0.07782 | 0.59509 | 122.168 | -0.064087 | 122.168 | 0.1831 | 0.1236 | 0.17395 | 0.041199 | -122.287 | -122.2137 | 0.17395 | 0.11902 | 0.027466 | 0.07782 | -0.013733 | -0.022888 | -0.073242 | -0.073242 | 0.2243 | 0.21515 | 0.16479 | 0.23804 | 0.18768 | 0.13275 | 0.027466 | 0.24719 | 122.2321 | -0.045776 | 122.2321 | -0.004577 | 122.2092 | -122.2412 | -122.3053 | 0.068665 | 122.2092 | -0.022888 | 0.63629
3621.3594 | 122.4335 | -0.059509 | 122.2412 | -0.18135 | -0.043457 | 0.0028048 | 0.024218 | 8.47e-06 | -0.010743 | -0.0028005 | -0.034454 | 0.0061651 | 0.061927 | 0.051327 | -0.016233 | 0.02869 | -0.0019483 | -0.07782 | -0.045776 | -0.004578 | 0.009155 | 0.13733 | -0.036621 | 0.064087 | 0.59509 | 122.168 | -0.064087 | 122.0947 | 0.11902 | 0.07782 | 0.11902 | 0.054931 | -122.287 | -122.2321 | 0.19684 | 0.1236 | 0.022888 | 0.068665 | -0.032043 | -0.004578 | -0.073242 | -0.14648 | 0.17853 | 0.17853 | 0.13733 | 0.18311 | 0.14191 | 0.14191 | 0.013733 | 0.18311 | 122.1588 | -0.041198 | 122.2321 | 0.013733 | 122.2275 | -122.2458 | -122.3053 | 0.068664 | 122.1542 | -0.018311 | 0.6546
3623.125 | 122.3511 | -0.086975 | 122.2916 | -0.15083 | -0.041535 | 0.0043002 | 0.026355 | 0.00064947 | -0.009675 | -0.0028005 | -0.11685 | 0.0061651 | 0.06385 | 0.055173 | -0.017729 | 0.029758 | -0.0036573 | -0.086975 | -0.004578 | -0.054932 | -0.041199 | 0.032043 | -0.11444 | 0.004578 | 0.5722 | 122.2 | -0.07782 | 122.0535 | 0.032043 | -0.027466 | 0.054932 | 0.032043 | -122.2961 | -122.3328 | 0.11902 | 0.091553 | -0.027466 | 0.05951 | -0.059509 | 0.009155 | -0.091553 | -0.23804 | 0.11902 | 0.14191 | 0.059509 | 0.13275 | 0.050354 | 0.086975 | 0.013733 | 0.10986 | 122.1313 | 0.050354 | 122.2778 | 0.082397 | 122.287 | -122.3465 | -122.3694 | 0.045776 | 122.1405 | 0 | 0.65918
3624.8281 | 122.4197 | -0.050354 | 122.2641 | -0.18135 | -0.043244 | 0.0043002 | 0.020373 | 8.47e-06 | -0.009675 | -0.0055777 | 0.0021667 | 0.0055243 | 0.065559 | 0.045559 | -0.016233 | 0.025058 | -0.0019483 | -0.11444 | -0.050354 | -0.022888 | -0.041199 | 0.064087 | -0.064087 | 0.041199 | 0.58136 | 122.1863 | -0.068665 | 122.0993 | 0.11444 | 0.073242 | 0.10986 | 0.027466 | -122.3145 | -122.3053 | 0.11444 | 0.091553 | -0.013733 | 0.064087 | -0.041199 | -0.018311 | -0.07782 | -0.16479 | 0.16479 | 0.16022 | 0.1236 | 0.17853 | 0.14191 | 0.086975 | -0.018311 | 0.18311 | 122.168 | -0.027466 | 122.2549 | 0 | 122.2366 | -122.287 | -122.3328 | 0.009155 | 122.1497 | -0.064087 | 0.63171
3626.5781 | 122.4701 | -0.041199 | 122.2458 | -0.18135 | -0.043457 | 0.0010958 | 0.020587 | -0.0017005 | -0.010316 | -0.0030141 | 0.0021667 | 0.0059515 | 0.064704 | 0.044278 | -0.018797 | 0.025912 | -0.0034435 | -0.07782 | -0.059509 | -0.004578 | 0.064087 | 0.18768 | 0.032043 | 0.091553 | 0.75531 | 122.1497 | -0.07782 | 122.1451 | 0.20599 | 0.14191 | 0.16022 | 0.036621 | -122.3053 | -122.1817 | 0.22888 | 0.13275 | 0.073242 | 0.096131 | 0.036621 | -0.036621 | -0.096131 | -0.10071 | 0.24719 | 0.20142 | 0.18311 | 0.23804 | 0.21973 | 0.19226 | 0.068665 | 0.28381 | 122.2229 | -0.054931 | 122.2275 | -0.01831 | 122.1909 | -122.2504 | -122.3236 | 0.10529 | 122.1863 | -0.036621 | 0.79651
3628.3281 | 122.4655 | -0.064087 | 122.2458 | -0.11269 | -0.044739 | 0.002164 | 0.022082 | -0.00084593 | -0.011598 | -0.0042959 | -0.025299 | 0.0042425 | 0.063636 | 0.051114 | -0.016874 | 0.025272 | -0.0028027 | -0.11902 | -0.054932 | -0.022888 | 0 | 0.091553 | -0.027466 | 0.068665 | 0.65002 | 122.1863 | -0.073242 | 122.1405 | 0.16022 | 0.12817 | 0.15106 | 0.041199 | -122.3007 | -122.2458 | 0.15564 | 0.13275 | 0.036621 | 0.091553 | -0.004578 | -0.009155 | -0.05951 | -0.10529 | 0.2243 | 0.21515 | 0.19226 | 0.2243 | 0.20142 | 0.11444 | 0.022888 | 0.23346 | 122.2137 | -0.032044 | 122.2595 | 0.009155 | 122.2504 | -122.2687 | -122.319 | 0.064087 | 122.2046 | -0.054932 | 0.71411
3630.0938 | 122.3465 | -0.091553 | 122.2641 | -0.17372 | -0.040467 | 0.0040866 | 0.025714 | 0.0036401 | -0.008607 | -0.0017325 | -0.13821 | 0.0063787 | 0.061286 | 0.052182 | -0.018369 | 0.027621 | -0.0064343 | -0.14191 | -0.004578 | -0.050354 | -0.09613 | -0.041199 | -0.16937 | -0.041199 | 0.46234 | 122.2275 | -0.10071 | 122.0444 | 0.018311 | -0.059509 | 0.041199 | 0.041199 | -122.2687 | -122.3602 | 0.050354 | 0.050354 | -0.07782 | 0.009155 | -0.11902 | -0.009155 | -0.036621 | -0.21973 | 0.10986 | 0.13275 | 0.032044 | 0.14191 | 0.041199 | 0.009155 | -0.045776 | 0.11902 | 122.1451 | 0.045776 | 122.3282 | 0.086975 | 122.319 | -122.3145 | -122.3648 | -0.004577 | 122.1359 | -0.050354 | 0.55389
3631.7969 | 122.3969 | -0.10529 | 122.2687 | -0.17372 | -0.04303 | 0.002164 | 0.02315 | 0.0023585 | -0.012452 | -0.0032277 | -0.10464 | 0.0061651 | 0.063423 | 0.05325 | -0.018583 | 0.02869 | -0.0077161 | -0.10071 | -0.022888 | -0.050354 | -0.036621 | 0.059509 | -0.086975 | 0.018311 | 0.65918 | 122.2046 | -0.11444 | 122.0947 | 0.09613 | 0.041199 | 0.091553 | 0.054932 | -122.2916 | -122.3053 | 0.16479 | 0.1236 | 0.018311 | 0.068665 | -0.036621 | -0.009155 | -0.064087 | -0.17395 | 0.20142 | 0.19684 | 0.14649 | 0.20599 | 0.15564 | 0.10986 | 0.013733 | 0.21057 | 122.2092 | 0.027466 | 122.319 | 0.082398 | 122.3099 | -122.319 | -122.3831 | 0.068665 | 122.2 | 0.004578 | 0.76447
3633.5625 | 122.3831 | -0.073242 | 122.2824 | -0.11269 | -0.044525 | 0.0023776 | 0.024218 | 0.0012903 | -0.011384 | -0.0036551 | -0.098541 | 0.0068059 | 0.062995 | 0.044705 | -0.015165 | 0.027621 | -0.0062207 | -0.09613 | 0 | -0.045776 | -0.041199 | 0.068665 | -0.073242 | 0.009155 | 0.6546 | 122.2321 | -0.082397 | 122.0947 | 0.10071 | 0.036621 | 0.10071 | 0.027466 | -122.2824 | -122.3236 | 0.14191 | 0.082397 | 0 | 0.054931 | -0.027466 | -0.009155 | -0.050354 | -0.18768 | 0.17395 | 0.17395 | 0.10986 | 0.18311 | 0.11902 | 0.11444 | 0.004577 | 0.18311 | 122.1771 | 0.045776 | 122.3145 | 0.073242 | 122.3053 | -122.3282 | -122.3648 | 0.032043 | 122.168 | -0.022888 | 0.72784
3635.3281 | 122.3694 | -0.10071 | 122.3007 | -0.10506 | -0.044525 | 0.0010958 | 0.02315 | -0.0031957 | -0.0098886 | -0.0042959 | -0.074127 | 0.0050971 | 0.063636 | 0.042569 | -0.016874 | 0.023135 | -0.0042981 | -0.16937 | -0.018311 | -0.054932 | -0.086975 | 0 | -0.10529 | -0.013733 | 0.60883 | 122.2412 | -0.1236 | 122.0261 | 0.045776 | -0.009155 | 0.032043 | 0.045776 | -122.319 | -122.3877 | 0.10071 | 0.086975 | -0.004578 | 0.041199 | -0.050354 | -0.022888 | -0.059509 | -0.27466 | 0.14648 | 0.13275 | 0.091553 | 0.15564 | 0.11444 | 0.054932 | -0.032043 | 0.16937 | 122.1497 | 0.036621 | 122.3648 | 0.082397 | 122.3419 | -122.3557 | -122.4243 | 0.013733 | 122.1268 | -0.068665 | 0.70953
3637.0781 | 122.4655 | -0.068665 | 122.2137 | -0.13557 | -0.044739 | 0.001523 | 0.018664 | -0.0027685 | -0.011598 | -0.0036551 | 0.0052185 | 0.0063787 | 0.064277 | 0.04321 | -0.01602 | 0.026126 | -0.0047253 | -0.064087 | -0.064087 | -0.009155 | 0.045776 | 0.17395 | 0.032043 | 0.10529 | 0.77362 | 122.1542 | -0.064087 | 122.1542 | 0.19226 | 0.14191 | 0.16937 | 0.05951 | -122.2778 | -122.168 | 0.24261 | 0.17395 | 0.10071 | 0.11444 | 0.041198 | 0.004578 | -0.059509 | -0.059509 | 0.26093 | 0.23804 | 0.21057 | 0.23346 | 0.20599 | 0.1831 | 0.054931 | 0.25635 | 122.2183 | -0.054932 | 122.2183 | 0.004578 | 122.2229 | -122.2229 | -122.2778 | 0.11444 | 122.2229 | 0.004578 | 0.84229
3638.8281 | 122.4518 | -0.050354 | 122.2687 | -0.17372 | -0.042603 | 0.00024143 | 0.022082 | -0.0014867 | -0.012452 | -0.0038687 | -0.016144 | 0.0046697 | 0.062995 | 0.046628 | -0.017942 | 0.025912 | -0.0070751 | -0.068665 | -0.045776 | -0.009155 | 0.032043 | 0.14191 | 0.013733 | 0.091553 | 0.75073 | 122.1909 | -0.068665 | 122.1176 | 0.16937 | 0.11902 | 0.16022 | 0.041199 | -122.3145 | -122.2366 | 0.19226 | 0.14191 | 0.064087 | 0.10071 | 0.022888 | -0.018311 | -0.07782 | -0.15106 | 0.21973 | 0.21057 | 0.16937 | 0.22888 | 0.18768 | 0.15106 | 0.041198 | 0.23804 | 122.1863 | -0.036621 | 122.2595 | 0.004578 | 122.2412 | -122.2778 | -122.3373 | 0.082397 | 122.168 | -0.018311 | 0.80109
3640.5938 | 122.4335 | -0.054932 | 122.2412 | -0.18135 | -0.041962 | 0.0030184 | 0.020373 | 0.0019311 | -0.0094614 | -0.0036551 | -0.06192 | 0.0065923 | 0.061714 | 0.0509 | -0.018369 | 0.024844 | -0.0047253 | -0.073242 | -0.036621 | -0.013733 | 0.013733 | 0.13275 | -0.027466 | 0.073242 | 0.62714 | 122.1817 | -0.068665 | 122.1176 | 0.12817 | 0.082397 | 0.14191 | 0.041199 | -122.2778 | -122.2275 | 0.18768 | 0.12817 | 0.027466 | 0.086975 | -0.013733 | -0.013733 | -0.059509 | -0.1236 | 0.18311 | 0.19684 | 0.13733 | 0.21057 | 0.15106 | 0.14648 | 0.027466 | 0.19684 | 122.1863 | -0.022888 | 122.2504 | 0.018311 | 122.2366 | -122.2549 | -122.3099 | 0.068665 | 122.1725 | -0.01831 | 0.68207
3642.2812 | 122.3557 | -0.082397 | 122.2916 | -0.12794 | -0.044953 | 0.0010958 | 0.024859 | -0.00020513 | -0.010957 | -0.0049367 | -0.064972 | 0.0061651 | 0.064491 | 0.045559 | -0.018583 | 0.02634 | -0.0057935 | -0.16022 | -0.004578 | -0.064087 | -0.086975 | -0.013733 | -0.10986 | -0.027466 | 0.60425 | 122.2321 | -0.09613 | 122.0261 | 0.041199 | -0.009155 | 0.036621 | 0.01831 | -122.2961 | -122.3785 | 0.068664 | 0.054931 | -0.027466 | 0.036621 | -0.045776 | -0.013733 | -0.059509 | -0.2655 | 0.1236 | 0.11902 | 0.073242 | 0.13275 | 0.086975 | 0.050354 | -0.022888 | 0.13733 | 122.1222 | 0.059509 | 122.3282 | 0.077819 | 122.3145 | -122.3557 | -122.3877 | -0.004578 | 122.1085 | -0.07782 | 0.68664
3644.0469 | 122.3831 | -0.07782 | 122.2824 | -0.1432 | -0.041535 | 0.0034456 | 0.026568 | -0.0017005 | -0.010957 | -0.0055777 | -0.1077 | 0.0087287 | 0.064704 | 0.048337 | -0.017729 | 0.02869 | -0.0021619 | -0.1236 | -0.009155 | -0.045776 | -0.09613 | -0.004578 | -0.14191 | -0.050354 | 0.48065 | 122.1863 | -0.10529 | 122.0581 | 0.050354 | -0.009155 | 0.059509 | 0.032044 | -122.2916 | -122.3785 | 0.073242 | 0.027466 | -0.064087 | -0.004578 | -0.096131 | -0.027466 | -0.096131 | -0.22431 | 0.12817 | 0.13733 | 0.068665 | 0.16479 | 0.096131 | 0.041198 | -0.050354 | 0.15564 | 122.1634 | 0.036621 | 122.2916 | 0.068665 | 122.2641 | -122.3282 | -122.3877 | -0.01831 | 122.1359 | -0.045776 | 0.55847
3645.8125 | 122.4747 | -0.022888 | 122.2595 | -0.1432 | -0.041748 | 0.0036594 | 0.022082 | -0.00041873 | -0.012879 | -0.0064321 | -0.058869 | 0.0061651 | 0.062782 | 0.054532 | -0.018797 | 0.02869 | -0.0045117 | -0.032043 | -0.064087 | -0.013733 | 0.032043 | 0.11902 | -0.022888 | 0.064087 | 0.62256 | 122.1725 | -0.045776 | 122.168 | 0.17395 | 0.10986 | 0.16937 | 0.009155 | -122.3236 | -122.2275 | 0.14191 | 0.086975 | 0 | 0.07782 | -0.009155 | -0.022888 | -0.086975 | -0.091552 | 0.19684 | 0.19226 | 0.13275 | 0.21515 | 0.15564 | 0.13275 | 0.045776 | 0.21973 | 122.2137 | -0.050354 | 122.2183 | -0.041199 | 122.1954 | -122.2733 | -122.3053 | 0.054931 | 122.1909 | -0.009155 | 0.64545
3647.5156 | 122.4289 | -0.045776 | 122.2641 | -0.16609 | -0.045166 | 0.0025912 | 0.019946 | 0.0021447 | -0.009675 | -0.0036551 | -0.046661 | 0.0050971 | 0.062354 | 0.044491 | -0.01666 | 0.024417 | -0.0042981 | -0.086975 | -0.045776 | -0.018311 | -0.009155 | 0.10071 | -0.054932 | 0.068665 | 0.57678 | 122.1588 | -0.073242 | 122.0993 | 0.14191 | 0.07782 | 0.11902 | 0.027465 | -122.3099 | -122.2733 | 0.14648 | 0.11444 | -0.009156 | 0.086976 | -0.036621 | -0.027466 | -0.10529 | -0.16479 | 0.18768 | 0.16479 | 0.1236 | 0.19226 | 0.15106 | 0.11902 | 0.009156 | 0.21515 | 122.1725 | -0.027465 | 122.2321 | 0 | 122.2046 | -122.2824 | -122.3373 | 0.036621 | 122.1451 | -0.041199 | 0.62256
3649.2812 | 122.4518 | -0.050354 | 122.2321 | -0.22713 | -0.041107 | 0.0047274 | 0.022509 | 0.00064947 | -0.010743 | -0.0053641 | -0.064972 | 0.0046697 | 0.061073 | 0.043637 | -0.017515 | 0.029117 | -0.0040845 | -0.068665 | -0.041199 | -0.013733 | 0.041199 | 0.14648 | -0.032043 | 0.064087 | 0.64087 | 122.1725 | -0.050354 | 122.1451 | 0.16479 | 0.09613 | 0.16022 | 0.036621 | -122.2733 | -122.1909 | 0.19684 | 0.11444 | 0.018311 | 0.07782 | -0.01831 | 0 | -0.05951 | -0.086975 | 0.21515 | 0.21057 | 0.14648 | 0.21057 | 0.14648 | 0.16022 | 0.054932 | 0.21515 | 122.1954 | -0.027466 | 122.2229 | 0.009155 | 122.2229 | -122.2458 | -122.2824 | 0.091553 | 122.1954 | -0.018311 | 0.69122
3651.0469 | 122.4518 | -0.059509 | 122.2504 | -0.15846 | -0.041962 | 0.0036594 | 0.023791 | 0.0017175 | -0.0098886 | -0.0053641 | -0.1077 | 0.0063787 | 0.064491 | 0.046414 | -0.018583 | 0.025912 | -0.0049389 | -0.10986 | -0.009155 | -0.054932 | -0.022888 | 0.059509 | -0.086975 | 0.018311 | 0.56305 | 122.2046 | -0.054932 | 122.1542 | 0.13275 | 0.082397 | 0.15564 | 0.004577 | -122.2595 | -122.2733 | 0.11902 | 0.07782 | -0.027466 | 0.073243 | -0.032043 | 0.004577 | -0.045776 | -0.09613 | 0.19226 | 0.21515 | 0.14191 | 0.21057 | 0.13733 | 0.11444 | 0.032044 | 0.18768 | 122.2092 | 0.045777 | 122.2595 | 0.050354 | 122.2641 | -122.3053 | -122.3053 | 0.036621 | 122.2137 | -0.050354 | 0.62256
3652.8125 | 122.4884 | -0.045776 | 122.2458 | -0.13557 | -0.044098 | 0.00066863 | 0.021228 | -0.0044775 | -0.012239 | -0.0051505 | -0.019196 | 0.0042425 | 0.064063 | 0.045987 | -0.016447 | 0.025912 | -0.0021619 | -0.082397 | -0.050354 | -0.009155 | 0.036621 | 0.16022 | 0.027466 | 0.091553 | 0.75989 | 122.1497 | -0.064087 | 122.168 | 0.19684 | 0.15564 | 0.17395 | 0.036621 | -122.2961 | -122.2092 | 0.20599 | 0.13733 | 0.073242 | 0.10071 | 0.036621 | -0.018311 | -0.096131 | -0.07782 | 0.24261 | 0.21973 | 0.20142 | 0.23804 | 0.21973 | 0.16937 | 0.045776 | 0.26093 | 122.2321 | -0.041199 | 122.2137 | -0.004578 | 122.1954 | -122.2549 | -122.3099 | 0.082397 | 122.2137 | -0.036621 | 0.80566
3654.5781 | 122.3511 | -0.09613 | 122.2824 | -0.17372 | -0.039826 | 0.0013094 | 0.024432 | 8.47e-06 | -0.0092478 | -0.0042959 | -0.13211 | 0.0065923 | 0.061714 | 0.056027 | -0.018156 | 0.028049 | -0.0042981 | -0.12817 | -0.013733 | -0.054932 | -0.086975 | -0.013733 | -0.14191 | -0.050354 | 0.49896 | 122.2275 | -0.091553 | 122.0261 | 0.022888 | -0.036621 | 0.036621 | 0.041198 | -122.2961 | -122.3694 | 0.082397 | 0.045776 | -0.045777 | 0.004578 | -0.086975 | 0.004577 | -0.054932 | -0.25635 | 0.11902 | 0.13275 | 0.059509 | 0.12817 | 0.054932 | 0.041199 | -0.032043 | 0.11444 | 122.1176 | 0.041199 | 122.319 | 0.082397 | 122.3236 | -122.3373 | -122.374 | 0.009155 | 122.1222 | -0.032044 | 0.59509
3656.2812 | 122.4289 | -0.059509 | 122.2687 | -0.16609 | -0.043671 | 0.0034456 | 0.022296 | -0.0055457 | -0.012239 | -0.0036551 | -0.034454 | 0.0057379 | 0.06385 | 0.04385 | -0.016233 | 0.02634 | -0.0028027 | -0.11444 | -0.036621 | -0.032043 | -0.022888 | 0.086975 | -0.068665 | 0.041199 | 0.5722 | 122.1909 | -0.082397 | 122.1085 | 0.1236 | 0.07782 | 0.10529 | 0.027466 | -122.3053 | -122.2916 | 0.14648 | 0.10071 | -0.009156 | 0.073242 | -0.036622 | -0.022888 | -0.07782 | -0.16022 | 0.1831 | 0.16479 | 0.13733 | 0.18768 | 0.16022 | 0.11902 | 0.009155 | 0.20599 | 122.1909 | -0.004578 | 122.2733 | 0.022888 | 122.2504 | -122.3007 | -122.3511 | 0.036621 | 122.168 | -0.054932 | 0.63171
3658.0469 | 122.5067 | -0.059509 | 122.2412 | -0.11269 | -0.044098 | 0.0010958 | 0.021441 | -0.0021277 | -0.011384 | -0.0017325 | -0.0008851 | 0.0044561 | 0.062995 | 0.049618 | -0.017729 | 0.026767 | -0.0040845 | -0.068665 | -0.064087 | -0.009155 | 0.059509 | 0.16937 | 0.009155 | 0.10986 | 0.80109 | 122.1634 | -0.045776 | 122.168 | 0.1831 | 0.15106 | 0.14648 | 0.050354 | -122.3053 | -122.1817 | 0.22888 | 0.16937 | 0.068664 | 0.11902 | 0.01831 | 0.013733 | -0.07782 | -0.073242 | 0.24261 | 0.20599 | 0.21057 | 0.19226 | 0.19684 | 0.17853 | 0.068664 | 0.22888 | 122.2137 | -0.054932 | 122.2092 | -0.004578 | 122.2229 | -122.2504 | -122.287 | 0.11902 | 122.2275 | -0.009156 | 0.86059
3659.75 | 122.4472 | -0.045776 | 122.2412 | -0.22713 | -0.044098 | 0.001523 | 0.0208 | -0.0025549 | -0.010743 | -0.0036551 | -0.019196 | 0.0065923 | 0.062141 | 0.048977 | -0.016874 | 0.025699 | -0.0072889 | -0.10986 | -0.018311 | -0.027466 | -0.022888 | 0.073242 | -0.064087 | 0.050354 | 0.60883 | 122.2046 | -0.068665 | 122.1085 | 0.13733 | 0.086975 | 0.10986 | 0.01831 | -122.2595 | -122.2641 | 0.11902 | 0.09613 | -0.018311 | 0.07782 | -0.036621 | -0.022889 | -0.036621 | -0.13275 | 0.18311 | 0.15564 | 0.13275 | 0.17853 | 0.15564 | 0.10071 | 0.004578 | 0.20599 | 122.1771 | 0.009155 | 122.2733 | 0.027465 | 122.2504 | -122.2687 | -122.3099 | 0.022888 | 122.1542 | -0.064087 | 0.6546
3661.5156 | 122.4609 | -0.041199 | 122.2275 | -0.18135 | -0.040894 | 0.003232 | 0.021869 | -0.0023413 | -0.0090342 | -0.0032277 | -0.080231 | 0.0061651 | 0.063636 | 0.052609 | -0.018583 | 0.02869 | -0.0047253 | -0.041199 | -0.054932 | -0.013733 | 0.041199 | 0.1236 | -0.018311 | 0.086975 | 0.62714 | 122.1725 | -0.059509 | 122.1725 | 0.16937 | 0.10986 | 0.16479 | 0.027466 | -122.2824 | -122.1863 | 0.16479 | 0.12817 | 0.022888 | 0.10071 | -0.004578 | -0.01831 | -0.054932 | -0.054932 | 0.21057 | 0.20599 | 0.15106 | 0.2243 | 0.16937 | 0.13733 | 0.054932 | 0.22888 | 122.2321 | -0.041199 | 122.2321 | -0.013733 | 122.2137 | -122.2412 | -122.287 | 0.082398 | 122.2137 | 0 | 0.66834
3663.2812 | 122.3557 | -0.10529 | 122.2916 | -0.12794 | -0.043244 | 2.7834e-05 | 0.0208 | -0.0023413 | -0.009675 | -0.0049367 | -0.086334 | 0.0059515 | 0.061927 | 0.042996 | -0.017515 | 0.027835 | -0.0057935 | -0.16479 | -0.009155 | -0.050354 | -0.09613 | 0 | -0.11444 | -0.027466 | 0.62714 | 122.2458 | -0.09613 | 122.0352 | 0.050354 | -0.027466 | 0.036621 | 0.054932 | -122.3007 | -122.3877 | 0.10529 | 0.07782 | -0.009155 | 0.022888 | -0.064087 | 0.009156 | -0.045776 | -0.25635 | 0.15564 | 0.14191 | 0.07782 | 0.13275 | 0.068664 | 0.050354 | -0.045776 | 0.14648 | 122.1313 | 0.041199 | 122.3419 | 0.096131 | 122.3511 | -122.3419 | -122.3877 | 0.009156 | 122.1405 | -0.059509 | 0.73242
3665.0469 | 122.3831 | -0.07782 | 122.2549 | -0.15083 | -0.043671 | 0.0030184 | 0.025073 | -0.0021277 | -0.010316 | -0.0019461 | -0.098541 | 0.0083013 | 0.064277 | 0.049832 | -0.01602 | 0.027835 | -0.0060071 | -0.13733 | -0.004578 | -0.041199 | -0.082397 | -0.018311 | -0.14191 | -0.027466 | 0.48523 | 122.2366 | -0.082397 | 122.0764 | 0.059509 | -0.036621 | 0.07782 | 0.036621 | -122.2595 | -122.3373 | 0.059509 | 0.050354 | -0.064087 | 0.013733 | -0.10071 | -0.004577 | -0.018311 | -0.17853 | 0.13733 | 0.15564 | 0.041199 | 0.16022 | 0.045776 | 0.022888 | -0.041198 | 0.14191 | 122.1588 | 0.036621 | 122.319 | 0.073242 | 122.3145 | -122.2961 | -122.3373 | -0.004577 | 122.1542 | -0.059509 | 0.56305
3666.8125 | 122.3648 | -0.11444 | 122.2916 | -0.082169 | -0.045166 | 0.001523 | 0.023791 | 0.0019311 | -0.01053 | -0.0032277 | -0.071076 | 0.0068059 | 0.062782 | 0.047055 | -0.01901 | 0.026767 | -0.0042981 | -0.12817 | -0.004578 | -0.059509 | -0.09613 | 0 | -0.12817 | -0.018311 | 0.62256 | 122.2229 | -0.10529 | 122.0398 | 0.054932 | -0.009155 | 0.036621 | 0.054932 | -122.2961 | -122.3877 | 0.11444 | 0.09613 | -0.013733 | 0.041198 | -0.068665 | 0.009155 | -0.068665 | -0.25177 | 0.16937 | 0.15106 | 0.10529 | 0.14191 | 0.096131 | 0.059509 | -0.036621 | 0.16022 | 122.1451 | 0.054931 | 122.3282 | 0.10986 | 122.3373 | -122.3511 | -122.3969 | 0.018311 | 122.1542 | -0.013733 | 0.737
3668.5156 | 122.4747 | -0.054932 | 122.2321 | -0.19661 | -0.043457 | 0.002164 | 0.019305 | -0.0021277 | -0.012025 | -0.0036551 | 0.0021667 | 0.0038153 | 0.063209 | 0.045346 | -0.016447 | 0.025912 | -0.0079297 | -0.082397 | -0.045776 | -0.036621 | 0.009155 | 0.11902 | 0.004578 | 0.10529 | 0.71411 | 122.168 | -0.086975 | 122.1542 | 0.1831 | 0.14648 | 0.15564 | 0.018311 | -122.2778 | -122.2229 | 0.17395 | 0.16022 | 0.05951 | 0.14191 | 0.041199 | -0.032043 | -0.064087 | -0.07782 | 0.23804 | 0.21057 | 0.20142 | 0.24261 | 0.23346 | 0.15564 | 0.045776 | 0.27008 | 122.2412 | -0.009155 | 122.2549 | 0.009156 | 122.2229 | -122.2687 | -122.319 | 0.064087 | 122.2092 | -0.027465 | 0.76904
3670.2812 | 122.3969 | -0.10071 | 122.2733 | -0.15846 | -0.041962 | 0.003873 | 0.022509 | 0.0025721 | -0.011384 | -0.0032277 | -0.11685 | 0.0078741 | 0.063423 | 0.051114 | -0.014951 | 0.029758 | -0.0053661 | -0.082397 | -0.022888 | -0.045776 | -0.027466 | 0.059509 | -0.086975 | 0.018311 | 0.67291 | 122.2183 | -0.073242 | 122.0993 | 0.10529 | 0.027466 | 0.091553 | 0.054932 | -122.2961 | -122.3007 | 0.16022 | 0.11902 | 0.013733 | 0.064087 | -0.041199 | 0.027466 | -0.054931 | -0.17395 | 0.20599 | 0.19226 | 0.12817 | 0.16479 | 0.10071 | 0.10528 | 0.01831 | 0.17853 | 122.1725 | 0.022888 | 122.2916 | 0.07782 | 122.319 | -122.319 | -122.3465 | 0.073242 | 122.2 | 0.018311 | 0.77362
3672.0312 | 122.4014 | -0.086975 | 122.2687 | -0.16609 | -0.042176 | 0.002164 | 0.02315 | 0.00064947 | -0.01117 | -0.0028005 | -0.11075 | 0.0078741 | 0.064918 | 0.042996 | -0.016233 | 0.02869 | -0.0049389 | -0.091553 | -0.041199 | -0.041199 | -0.022888 | 0.068665 | -0.073242 | 0.009155 | 0.66376 | 122.2321 | -0.086975 | 122.0947 | 0.10986 | 0.027466 | 0.10986 | 0.045776 | -122.3099 | -122.2916 | 0.15564 | 0.09613 | 0.013733 | 0.050354 | -0.032043 | 0 | -0.036621 | -0.17395 | 0.19684 | 0.19684 | 0.11444 | 0.19684 | 0.11444 | 0.10986 | 0.018311 | 0.19684 | 122.1817 | 0 | 122.319 | 0.045776 | 122.319 | -122.3099 | -122.3557 | 0.064087 | 122.1817 | -0.004578 | 0.75073
3673.7969 | 122.3923 | -0.068665 | 122.2687 | -0.15846 | -0.04068 | 0.0025912 | 0.023791 | -0.0025549 | -0.01117 | -0.0023733 | -0.10159 | 0.0072333 | 0.0615 | 0.045773 | -0.017088 | 0.028262 | -0.0040845 | -0.13275 | -0.004578 | -0.050354 | -0.086975 | 0.004578 | -0.12817 | -0.018311 | 0.50354 | 122.1909 | -0.086975 | 122.0993 | 0.082397 | 0.018311 | 0.082397 | 0.018311 | -122.2733 | -122.3557 | 0.073243 | 0.050354 | -0.059509 | 0.032043 | -0.07782 | -0.01831 | -0.07782 | -0.16937 | 0.15106 | 0.15106 | 0.086976 | 0.16937 | 0.10529 | 0.054932 | -0.036621 | 0.16937 | 122.1863 | 0.045776 | 122.2778 | 0.064087 | 122.2595 | -122.319 | -122.3557 | -0.01831 | 122.168 | -0.064086 | 0.5722
3675.5625 | 122.4289 | -0.050354 | 122.2412 | -0.15846 | -0.043671 | 0.0025912 | 0.021655 | -0.0031957 | -0.0077524 | -0.00066434 | -0.025299 | 0.0050971 | 0.064918 | 0.048337 | -0.014311 | 0.024844 | -0.0057935 | -0.091553 | -0.050354 | -0.022888 | 0.018311 | 0.13275 | -0.041199 | 0.054932 | 0.62714 | 122.1725 | -0.059509 | 122.113 | 0.10986 | 0.09613 | 0.13275 | 0.027466 | -122.2916 | -122.2229 | 0.18311 | 0.10529 | 0.009155 | 0.07782 | -0.018311 | -0.009155 | -0.068665 | -0.12817 | 0.16022 | 0.18311 | 0.14648 | 0.19226 | 0.15564 | 0.15564 | 0.041199 | 0.16937 | 122.1725 | -0.027466 | 122.2321 | 0 | 122.2229 | -122.2641 | -122.3007 | 0.068665 | 122.1634 | -0.041199 | 0.67749
3677.3281 | 122.4838 | -0.054932 | 122.2321 | -0.12032 | -0.04303 | 0.00088223 | 0.022723 | -0.0012731 | -0.008607 | -0.0034415 | -0.013092 | 0.0046697 | 0.063423 | 0.0462 | -0.017729 | 0.027194 | -0.0083569 | -0.10071 | -0.036621 | -0.013733 | 0.009155 | 0.11902 | 0.009155 | 0.086975 | 0.72327 | 122.1771 | -0.054932 | 122.1542 | 0.19226 | 0.14191 | 0.16937 | 0.041199 | -122.2687 | -122.2229 | 0.17395 | 0.14191 | 0.064087 | 0.10071 | 0.022888 | 0 | -0.054932 | -0.07782 | 0.24719 | 0.22431 | 0.19684 | 0.22431 | 0.19684 | 0.13275 | 0.022888 | 0.24719 | 122.2092 | -0.022888 | 122.2321 | 0.018311 | 122.2321 | -122.2458 | -122.287 | 0.064087 | 122.2092 | -0.045776 | 0.7782
3679.0312 | 122.4747 | -0.050354 | 122.2458 | -0.15846 | -0.04303 | 0.0023776 | 0.023364 | 0.00086307 | -0.0073252 | -0.0057913 | -0.074127 | 0.0065923 | 0.064704 | 0.0509 | -0.018369 | 0.02634 | -0.0047253 | -0.082397 | -0.027466 | -0.018311 | 0.032043 | 0.11444 | -0.041199 | 0.064087 | 0.60425 | 122.1954 | -0.050354 | 122.1588 | 0.16479 | 0.10071 | 0.18768 | 0.032043 | -122.2733 | -122.2137 | 0.16479 | 0.11444 | 0.009155 | 0.082398 | -0.022888 | 0 | -0.050354 | -0.086976 | 0.21515 | 0.23804 | 0.15106 | 0.23804 | 0.15106 | 0.13275 | 0.050354 | 0.21515 | 122.2092 | -0.009155 | 122.2458 | 0.022888 | 122.2458 | -122.2641 | -122.2961 | 0.082397 | 122.2092 | -0.032043 | 0.6546
3680.7969 | 122.4014 | -0.082397 | 122.2916 | -0.15846 | -0.041535 | 0.002164 | 0.026141 | 0.0012903 | -0.0088206 | -0.0049367 | -0.09549 | 0.0055243 | 0.062568 | 0.040646 | -0.01901 | 0.02869 | -0.0070751 | -0.1236 | -0.022888 | -0.054932 | -0.068665 | 0.009155 | -0.12817 | -0.022888 | 0.53101 | 122.1909 | -0.082397 | 122.0901 | 0.086975 | 0.018311 | 0.09613 | 0.027465 | -122.3145 | -122.3602 | 0.091552 | 0.059509 | -0.045777 | 0.032044 | -0.073242 | 0 | -0.10071 | -0.20142 | 0.16937 | 0.17853 | 0.10071 | 0.17853 | 0.10071 | 0.064087 | -0.013733 | 0.16937 | 122.1725 | 0.032044 | 122.2733 | 0.059509 | 122.2733 | -122.3465 | -122.374 | 0.013732 | 122.1725 | -0.041199 | 0.6134
3682.5 | 122.4792 | -0.045776 | 122.2229 | -0.1432 | -0.044098 | 0.0017368 | 0.021228 | 0.0025721 | -0.01053 | -0.0038687 | 0.011322 | 0.0044561 | 0.063209 | 0.045132 | -0.017729 | 0.029117 | -0.0042981 | -0.11444 | -0.041199 | -0.027466 | 0.009155 | 0.11902 | 0 | 0.10071 | 0.72327 | 122.1954 | -0.07782 | 122.1588 | 0.19684 | 0.15106 | 0.16022 | 0.01831 | -122.2641 | -122.2137 | 0.16479 | 0.14648 | 0.045776 | 0.12817 | 0.027466 | -0.032044 | -0.027465 | -0.064087 | 0.24261 | 0.20599 | 0.19684 | 0.23804 | 0.22888 | 0.14649 | 0.036621 | 0.27466 | 122.2366 | -0.013733 | 122.2733 | 0.004577 | 122.2412 | -122.2504 | -122.3007 | 0.054931 | 122.2046 | -0.068665 | 0.76904
3684.2656 | 122.3648 | -0.091553 | 122.2824 | -0.15083 | -0.040253 | 0.002164 | 0.024218 | -0.00063233 | -0.010102 | -0.0072867 | -0.12601 | 0.0065923 | 0.060859 | 0.052823 | -0.019224 | 0.024844 | -0.0025891 | -0.07782 | -0.009155 | -0.041199 | -0.036621 | 0.054932 | -0.086975 | 0 | 0.63629 | 122.2229 | -0.091553 | 122.0581 | 0.073242 | -0.004578 | 0.07782 | 0.050354 | -122.2916 | -122.319 | 0.14649 | 0.091553 | 0.004578 | 0.041199 | -0.045776 | 0 | -0.05951 | -0.22431 | 0.16479 | 0.16937 | 0.086975 | 0.16937 | 0.086975 | 0.096131 | 0.004578 | 0.16479 | 122.1497 | 0.032044 | 122.3145 | 0.082398 | 122.3145 | -122.3236 | -122.374 | 0.054932 | 122.1497 | 0.013733 | 0.72784
3686.0156 | 122.374 | -0.09613 | 122.2824 | -0.10506 | -0.040894 | 0.0028048 | 0.024859 | 0.00043587 | -0.01053 | -0.0072867 | -0.10159 | 0.0063787 | 0.063636 | 0.050259 | -0.017729 | 0.031039 | -0.0051525 | -0.086975 | -0.004578 | -0.045776 | -0.027466 | 0.059509 | -0.086975 | 0.009155 | 0.65002 | 122.2275 | -0.086975 | 122.0718 | 0.073242 | 0.013733 | 0.086975 | 0.050354 | -122.287 | -122.3099 | 0.15564 | 0.10528 | 0.009155 | 0.054931 | -0.041199 | 0.009155 | -0.054932 | -0.21057 | 0.16937 | 0.1831 | 0.10986 | 0.17395 | 0.10071 | 0.10528 | 0.01831 | 0.16022 | 122.1588 | 0.041198 | 122.3145 | 0.091552 | 122.3236 | -122.3282 | -122.3694 | 0.068664 | 122.168 | 0.009155 | 0.74615
3687.7656 | 122.3282 | -0.091553 | 122.2733 | -0.12794 | -0.042603 | 0.003232 | 0.025073 | 0.0015039 | -0.0098886 | -0.0060049 | -0.10159 | 0.0057379 | 0.061714 | 0.044919 | -0.017301 | 0.029117 | -0.0053661 | -0.10986 | -0.009155 | -0.054932 | -0.064087 | 0.027466 | -0.12817 | -0.013733 | 0.57678 | 122.2321 | -0.10071 | 122.049 | 0.041199 | -0.041199 | 0.050354 | 0.036621 | -122.2824 | -122.3373 | 0.11902 | 0.07782 | -0.036621 | 0.041199 | -0.073242 | -0.009155 | -0.041198 | -0.2243 | 0.13275 | 0.14191 | 0.050354 | 0.15106 | 0.059509 | 0.082398 | -0.009155 | 0.14191 | 122.1497 | 0.045777 | 122.3328 | 0.082398 | 122.3236 | -122.3282 | -122.374 | 0.027466 | 122.1405 | -0.01831 | 0.66834
3689.4688 | 122.4884 | -0.050354 | 122.2229 | -0.18898 | -0.045594 | 0.00045503 | 0.019732 | 0.0012903 | -0.010957 | -0.0060049 | 0.020477 | 0.0061651 | 0.062354 | 0.045987 | -0.016874 | 0.025485 | -0.0045117 | -0.091553 | -0.045776 | -0.004578 | 0.009155 | 0.14191 | 0.009155 | 0.10986 | 0.737 | 122.1954 | -0.064087 | 122.1451 | 0.20142 | 0.15106 | 0.16479 | 0.045776 | -122.2687 | -122.2137 | 0.19226 | 0.16022 | 0.059509 | 0.11444 | 0.013733 | -0.013733 | -0.027465 | -0.077819 | 0.25177 | 0.21515 | 0.20142 | 0.22888 | 0.21515 | 0.14649 | 0.013733 | 0.2655 | 122.2092 | -0.041198 | 122.2595 | 0.004578 | 122.2458 | -122.2275 | -122.287 | 0.059509 | 122.1954 | -0.041199 | 0.78735
3691.2344 | 122.4701 | -0.032043 | 122.2412 | -0.12032 | -0.045594 | 0.002164 | 0.020373 | -0.0046911 | -0.0090342 | -0.0051505 | 0.026581 | 0.0040289 | 0.062354 | 0.04086 | -0.017942 | 0.025912 | -0.0066479 | -0.059509 | -0.059509 | -0.022888 | 0.036621 | 0.16022 | 0.022888 | 0.11444 | 0.78278 | 122.1909 | -0.073242 | 122.1405 | 0.20599 | 0.14191 | 0.14648 | 0.009155 | -122.3007 | -122.2046 | 0.19226 | 0.14648 | 0.054931 | 0.13733 | 0.045776 | -0.041199 | -0.050354 | -0.10071 | 0.23804 | 0.17853 | 0.17395 | 0.21973 | 0.21515 | 0.1831 | 0.059509 | 0.27924 | 122.2137 | -0.036621 | 122.2641 | -0.027466 | 122.2229 | -122.2641 | -122.3145 | 0.068664 | 122.1725 | -0.027466 | 0.81482
3693 | 122.4197 | -0.068665 | 122.2687 | -0.15846 | -0.044098 | 0.0017368 | 0.019732 | -0.0064001 | -0.01053 | -0.0042959 | -0.019196 | 0.0068059 | 0.062782 | 0.046841 | -0.018369 | 0.026981 | -0.0047253 | -0.07782 | -0.054932 | -0.013733 | 0.036621 | 0.1236 | -0.004578 | 0.064087 | 0.76446 | 122.1909 | -0.082397 | 122.0993 | 0.16022 | 0.10529 | 0.1236 | 0.054932 | -122.3236 | -122.2321 | 0.19226 | 0.13275 | 0.064087 | 0.07782 | 0.009155 | -0.013732 | -0.07782 | -0.16937 | 0.22888 | 0.19226 | 0.17395 | 0.20599 | 0.18768 | 0.13733 | 0.050354 | 0.24261 | 122.1817 | -0.041199 | 122.2733 | 0.013733 | 122.2595 | -122.2824 | -122.3511 | 0.10529 | 122.168 | -0.009155 | 0.83313
3694.7812 | 122.3831 | -0.082397 | 122.2733 | -0.12032 | -0.043885 | 0.00088223 | 0.025287 | -0.0019141 | -0.0092478 | -0.0055777 | -0.13516 | 0.0065923 | 0.062141 | 0.049405 | -0.018156 | 0.028049 | -0.0015209 | -0.13275 | 0.009155 | -0.045776 | -0.10529 | -0.018311 | -0.12817 | -0.032043 | 0.51727 | 122.2275 | -0.09613 | 122.0535 | 0.045776 | -0.022888 | 0.054932 | 0.036621 | -122.2641 | -122.3785 | 0.064086 | 0.050354 | -0.045777 | 0.013733 | -0.082398 | -0.013733 | -0.045776 | -0.21973 | 0.12817 | 0.13733 | 0.059509 | 0.15106 | 0.073242 | 0.027465 | -0.05951 | 0.14191 | 122.1497 | 0.054931 | 122.3236 | 0.091552 | 122.3099 | -122.319 | -122.3694 | -0.022889 | 122.1359 | -0.050354 | 0.59967
3696.5625 | 122.4701 | -0.041199 | 122.2458 | -0.18135 | -0.044312 | 0.0013094 | 0.021014 | -0.00063233 | -0.010102 | -0.0034415 | 0.0052185 | 0.0063787 | 0.06385 | 0.045987 | -0.017088 | 0.025699 | -0.0077161 | -0.068665 | -0.054932 | -0.009155 | 0.036621 | 0.17395 | 0.036621 | 0.1236 | 0.79193 | 122.1817 | -0.068665 | 122.1542 | 0.20142 | 0.15106 | 0.16022 | 0.032044 | -122.3007 | -122.2092 | 0.21515 | 0.16479 | 0.07782 | 0.13275 | 0.045776 | -0.027466 | -0.064087 | -0.091553 | 0.24262 | 0.20142 | 0.19226 | 0.22888 | 0.21973 | 0.1831 | 0.045776 | 0.27008 | 122.2229 | -0.045777 | 122.2504 | -0.013733 | 122.2229 | -122.2549 | -122.3145 | 0.07782 | 122.1954 | -0.027466 | 0.83313
3698.25 | 122.3373 | -0.10529 | 122.2687 | -0.12794 | -0.043671 | 0.0034456 | 0.023791 | 0.0029993 | -0.011598 | -0.0028005 | -0.1138 | 0.0048833 | 0.062354 | 0.052395 | -0.019224 | 0.027621 | -0.0051525 | -0.10529 | -0.032043 | -0.045776 | -0.07782 | -0.004578 | -0.14191 | -0.041199 | 0.54474 | 122.2275 | -0.10071 | 122.0352 | 0.022888 | -0.032043 | 0.041199 | 0.05951 | -122.3007 | -122.3465 | 0.10071 | 0.064087 | -0.036621 | 0.004577 | -0.096131 | 0.004578 | -0.041199 | -0.23346 | 0.12817 | 0.14649 | 0.073243 | 0.14191 | 0.068665 | 0.041198 | -0.032044 | 0.1236 | 122.1359 | 0.013733 | 122.3282 | 0.073243 | 122.3328 | -122.3145 | -122.3694 | 0.027466 | 122.1405 | 0 | 0.65002
3699.9375 | 122.4838 | -0.018311 | 122.2321 | -0.15083 | -0.046021 | 0.0025912 | 0.024646 | -0.0046911 | -0.0094614 | -0.0051505 | -0.0039367 | 0.0044561 | 0.065132 | 0.042782 | -0.016447 | 0.025058 | -0.0083569 | -0.091553 | -0.041199 | -0.022888 | 0.027466 | 0.12817 | 0 | 0.10986 | 0.77362 | 122.1542 | -0.059509 | 122.1588 | 0.19684 | 0.14648 | 0.16022 | -0.004577 | -122.2733 | -122.2046 | 0.14649 | 0.12817 | 0.018311 | 0.13275 | 0.022888 | -0.041198 | -0.07782 | -0.073243 | 0.21515 | 0.17853 | 0.16479 | 0.21973 | 0.20599 | 0.15106 | 0.050354 | 0.25635 | 122.2183 | -0.018311 | 122.2137 | -0.022888 | 122.1725 | -122.2549 | -122.2916 | 0.045777 | 122.1771 | -0.073242 | 0.79193
3701.7188 | 122.4609 | -0.059509 | 122.2504 | -0.17372 | -0.042816 | 0.0019504 | 0.022937 | -0.0010595 | -0.0098886 | -0.0023733 | -0.01004 | 0.0050971 | 0.063209 | 0.046628 | -0.01666 | 0.028476 | -0.0017347 | -0.11902 | -0.059509 | -0.022888 | 0 | 0.10071 | -0.027466 | 0.082397 | 0.70496 | 122.1725 | -0.064087 | 122.1359 | 0.16937 | 0.1236 | 0.15106 | 0.036621 | -122.3099 | -122.2504 | 0.16022 | 0.14191 | 0.032043 | 0.10528 | -0.004578 | -0.004578 | -0.07782 | -0.11444 | 0.22888 | 0.21057 | 0.1831 | 0.21515 | 0.18768 | 0.1236 | 0.022888 | 0.23346 | 122.2 | -0.036621 | 122.2366 | 0 | 122.2321 | -122.2733 | -122.3145 | 0.059509 | 122.1954 | -0.05951 | 0.76447
3703.4844 | 122.4792 | -0.059509 | 122.2504 | -0.19661 | -0.043671 | 0.0025912 | 0.022723 | -0.0012731 | -0.010102 | -0.0038687 | -0.058869 | 0.0061651 | 0.062782 | 0.042996 | -0.020078 | 0.026981 | -0.0047253 | -0.059509 | -0.041199 | -0.027466 | 0.045776 | 0.13733 | -0.032043 | 0.07782 | 0.64087 | 122.1634 | -0.054932 | 122.1634 | 0.16937 | 0.11444 | 0.16479 | 0.032043 | -122.2916 | -122.2046 | 0.19684 | 0.13733 | 0.027466 | 0.10529 | -0.004577 | 0.004577 | -0.086975 | -0.086975 | 0.22888 | 0.2243 | 0.17395 | 0.21973 | 0.16937 | 0.16479 | 0.073242 | 0.22431 | 122.2183 | -0.013733 | 122.2183 | 0.01831 | 122.2229 | -122.2778 | -122.3053 | 0.10528 | 122.2229 | 0 | 0.70038
3705.25 | 122.4792 | -0.032043 | 122.2504 | -0.21187 | -0.041107 | 0.0034456 | 0.022723 | 8.47e-06 | -0.010743 | -0.0040823 | -0.064972 | 0.0061651 | 0.063423 | 0.053891 | -0.017515 | 0.026126 | -0.0087841 | -0.045776 | -0.045776 | -0.004578 | 0.041199 | 0.1236 | -0.036621 | 0.07782 | 0.66376 | 122.1909 | -0.059509 | 122.1725 | 0.18768 | 0.11902 | 0.17853 | 0.027465 | -122.2961 | -122.2092 | 0.15564 | 0.10986 | -0.004578 | 0.082398 | -0.032043 | -0.027466 | -0.059509 | -0.07782 | 0.21973 | 0.21057 | 0.15106 | 0.23804 | 0.17853 | 0.12817 | 0.045777 | 0.24719 | 122.2321 | -0.041198 | 122.2504 | -0.013733 | 122.2229 | -122.2549 | -122.3099 | 0.073242 | 122.2046 | -0.013733 | 0.6958
3706.9531 | 122.4747 | -0.045776 | 122.2412 | -0.11269 | -0.044098 | 0.0017368 | 0.022296 | -0.0019141 | -0.01117 | -0.0040823 | -0.01004 | 0.0046697 | 0.063209 | 0.042782 | -0.019651 | 0.025058 | -0.0038709 | -0.068665 | -0.041199 | -0.022888 | 0.054932 | 0.1831 | 0.027466 | 0.11444 | 0.79651 | 122.2092 | -0.059509 | 122.1497 | 0.21057 | 0.14648 | 0.16022 | 0.022888 | -122.2824 | -122.1863 | 0.22888 | 0.16022 | 0.073242 | 0.13733 | 0.050354 | -0.013733 | -0.032044 | -0.091553 | 0.25635 | 0.20599 | 0.19226 | 0.21973 | 0.20599 | 0.20599 | 0.07782 | 0.27008 | 122.2092 | -0.018311 | 122.2687 | 0.004577 | 122.2549 | -122.2641 | -122.3007 | 0.10071 | 122.1954 | -0.022889 | 0.84229
3708.7188 | 122.3511 | -0.10071 | 122.2824 | -0.1432 | -0.043885 | 0.0010958 | 0.024859 | -0.0042639 | -0.010957 | -0.0042959 | -0.068024 | 0.0078741 | 0.065986 | 0.051114 | -0.018797 | 0.026126 | -0.0042981 | -0.15106 | -0.004578 | -0.064087 | -0.09613 | -0.004578 | -0.10071 | -0.009155 | 0.65002 | 122.2229 | -0.09613 | 122.0123 | 0.045776 | -0.009155 | 0.032043 | 0.036621 | -122.287 | -122.3785 | 0.09613 | 0.091553 | 0 | 0.054932 | -0.036621 | 0.004578 | -0.05951 | -0.27008 | 0.14648 | 0.13275 | 0.091553 | 0.12817 | 0.086975 | 0.059509 | -0.032043 | 0.14191 | 122.1085 | 0.059509 | 122.319 | 0.09613 | 122.3236 | -122.3465 | -122.3785 | 0.004578 | 122.113 | -0.050354 | 0.75073
3710.4844 | 122.3328 | -0.10071 | 122.287 | -0.16609 | -0.042389 | 0.0028048 | 0.026355 | -0.0031957 | -0.010102 | -0.0023733 | -0.11685 | 0.0065923 | 0.065132 | 0.054104 | -0.017515 | 0.027621 | -0.0094251 | -0.09613 | -0.009155 | -0.050354 | -0.045776 | 0.032043 | -0.10986 | -0.027466 | 0.59967 | 122.2275 | -0.10986 | 122.0444 | 0.027466 | -0.032043 | 0.041199 | 0.050354 | -122.2961 | -122.3328 | 0.13275 | 0.073242 | -0.009155 | 0.022888 | -0.059509 | -0.009155 | -0.059509 | -0.24261 | 0.12817 | 0.14191 | 0.068665 | 0.15106 | 0.07782 | 0.082397 | 0.004578 | 0.13733 | 122.1542 | 0.041199 | 122.3373 | 0.091553 | 122.3282 | -122.3373 | -122.3969 | 0.054932 | 122.1451 | 0.004578 | 0.70038
3712.25 | 122.3923 | -0.07782 | 122.2687 | -0.1432 | -0.043885 | 0.0010958 | 0.020587 | -0.0027685 | -0.012239 | -0.0034415 | -0.049713 | 0.0059515 | 0.062782 | 0.041714 | -0.016874 | 0.027194 | -0.0045117 | -0.09613 | -0.041199 | -0.022888 | 0.004578 | 0.09613 | -0.022888 | 0.050354 | 0.737 | 122.1817 | -0.07782 | 122.0444 | 0.09613 | 0.032043 | 0.054932 | 0.054932 | -122.3099 | -122.2641 | 0.17395 | 0.12817 | 0.054932 | 0.073242 | 0 | 0 | -0.086975 | -0.2243 | 0.17395 | 0.13275 | 0.10986 | 0.13275 | 0.10986 | 0.11902 | 0.027466 | 0.17395 | 122.1222 | -0.018311 | 122.2595 | 0.036621 | 122.2595 | -122.2916 | -122.3465 | 0.082398 | 122.1222 | -0.01831 | 0.81482
3713.9531 | 122.4655 | -0.064087 | 122.2321 | -0.16609 | -0.043885 | 0.0013094 | 0.024218 | 0.0017175 | -0.010316 | -0.0034415 | -0.1077 | 0.0048833 | 0.062995 | 0.049191 | -0.017942 | 0.024844 | -0.00023931 | -0.1236 | -0.018311 | -0.045776 | -0.022888 | 0.073242 | -0.07782 | 0.027466 | 0.60883 | 122.1954 | -0.086975 | 122.1451 | 0.15106 | 0.09613 | 0.16022 | 0.018311 | -122.2504 | -122.2549 | 0.13733 | 0.091553 | -0.013733 | 0.073242 | -0.032044 | -0.022888 | -0.036621 | -0.086975 | 0.21515 | 0.2243 | 0.16022 | 0.24719 | 0.1831 | 0.11902 | 0.022888 | 0.23804 | 122.2321 | 0.027465 | 122.2824 | 0.045776 | 122.2595 | -122.2778 | -122.319 | 0.041199 | 122.2092 | -0.059509 | 0.67291
3715.7188 | 122.4655 | -0.045776 | 122.2321 | -0.15846 | -0.04538 | 0.00088223 | 0.0208 | 0.0025721 | -0.010102 | -0.0013051 | 0.017425 | 0.0061651 | 0.061927 | 0.04385 | -0.018156 | 0.026553 | -0.0070751 | -0.054932 | -0.050354 | -0.027466 | 0.036621 | 0.17395 | 0.013733 | 0.10529 | 0.80109 | 122.1954 | -0.059509 | 122.1405 | 0.20599 | 0.15564 | 0.16479 | 0.01831 | -122.2824 | -122.1954 | 0.21973 | 0.15106 | 0.059509 | 0.13275 | 0.041199 | -0.013733 | -0.036621 | -0.091553 | 0.25177 | 0.21057 | 0.20142 | 0.2243 | 0.21515 | 0.20142 | 0.064087 | 0.2655 | 122.2 | -0.022888 | 122.2549 | -0.004578 | 122.2412 | -122.2595 | -122.2916 | 0.082397 | 122.1863 | -0.009156 | 0.84686
3717.4219 | 122.3419 | -0.11902 | 122.287 | -0.089798 | -0.042816 | -0.00018577 | 0.024859 | -0.0027685 | -0.011598 | -0.0049367 | -0.052765 | 0.0068059 | 0.062782 | 0.046841 | -0.016874 | 0.026767 | -0.00088011 | -0.15106 | -0.004578 | -0.073242 | -0.091553 | 0.004578 | -0.10071 | -0.022888 | 0.6546 | 122.2504 | -0.10071 | 122.0169 | 0.036621 | -0.009155 | 0.027466 | 0.045777 | -122.2916 | -122.3785 | 0.1236 | 0.096131 | 0.018311 | 0.050354 | -0.027466 | 0.018311 | -0.036621 | -0.27008 | 0.15564 | 0.14649 | 0.10986 | 0.12817 | 0.091553 | 0.07782 | -0.018311 | 0.13733 | 122.1176 | 0.068664 | 122.3511 | 0.11444 | 122.3694 | -122.3602 | -122.3877 | 0.027466 | 122.1359 | -0.032043 | 0.77362
3719.1875 | 122.4976 | -0.036621 | 122.2275 | -0.13557 | -0.044312 | -0.00061317 | 0.021869 | -0.0019141 | -0.0098886 | -0.0038687 | -0.01004 | 0.0065923 | 0.063209 | 0.050259 | -0.018156 | 0.027835 | -0.0057935 | -0.07782 | -0.041199 | -0.009155 | 0.050354 | 0.16937 | 0.027466 | 0.11444 | 0.81024 | 122.1771 | -0.054932 | 122.168 | 0.2243 | 0.16022 | 0.17395 | 0.027466 | -122.2687 | -122.1771 | 0.20599 | 0.15106 | 0.064087 | 0.1236 | 0.036621 | -0.018311 | -0.050354 | -0.059509 | 0.26093 | 0.21057 | 0.19684 | 0.22888 | 0.21515 | 0.17853 | 0.059509 | 0.27924 | 122.2229 | -0.032044 | 122.2321 | -0.004578 | 122.2137 | -122.2366 | -122.2824 | 0.086975 | 122.2046 | -0.041199 | 0.84686
3720.9531 | 122.4243 | -0.064087 | 122.2366 | -0.17372 | -0.044098 | 0.003232 | 0.022937 | -0.0010595 | -0.0092478 | -0.0060049 | -0.046661 | 0.0059515 | 0.062995 | 0.042569 | -0.017942 | 0.026126 | -0.00045291 | -0.10071 | -0.050354 | -0.009155 | 0.004578 | 0.086975 | -0.059509 | 0.036621 | 0.62256 | 122.1771 | -0.054932 | 122.0993 | 0.10986 | 0.07782 | 0.11902 | 0.054932 | -122.287 | -122.2321 | 0.15106 | 0.10071 | 0.004578 | 0.045776 | -0.050354 | 0.009155 | -0.059509 | -0.13733 | 0.17395 | 0.18311 | 0.14191 | 0.17395 | 0.13275 | 0.09613 | 0.013733 | 0.16479 | 122.1542 | -0.041199 | 122.2321 | 0.013733 | 122.2412 | -122.2458 | -122.2916 | 0.068665 | 122.1634 | -0.036621 | 0.68665
3722.6562 | 122.3877 | -0.068665 | 122.2687 | -0.10506 | -0.042176 | 0.0017368 | 0.026355 | 0.0044947 | -0.011598 | -0.00066434 | -0.1199 | 0.0072333 | 0.061714 | 0.053891 | -0.016233 | 0.027194 | -0.0042981 | -0.10529 | -0.004578 | -0.050354 | -0.032043 | 0.050354 | -0.07782 | 0.009155 | 0.6958 | 122.2458 | -0.09613 | 122.0856 | 0.10071 | 0.027466 | 0.091553 | 0.018311 | -122.2733 | -122.3007 | 0.11902 | 0.07782 | -0.009155 | 0.059509 | -0.027466 | -0.027465 | -0.022888 | -0.18311 | 0.16937 | 0.16022 | 0.096131 | 0.18768 | 0.1236 | 0.10071 | 0.018311 | 0.19684 | 122.1817 | 0.045776 | 122.3419 | 0.064087 | 122.3145 | -122.319 | -122.3648 | 0.036622 | 122.1542 | -0.036621 | 0.76447
3724.4219 | 122.3877 | -0.082397 | 122.2504 | -0.12032 | -0.042816 | -0.00061317 | 0.025073 | -0.00084593 | -0.010316 | -0.0034415 | -0.10464 | 0.0065923 | 0.062354 | 0.050473 | -0.016874 | 0.028476 | -0.0077161 | -0.10986 | -0.022888 | -0.032043 | -0.027466 | 0.064087 | -0.068665 | 0.009155 | 0.69122 | 122.2321 | -0.086975 | 122.1085 | 0.10986 | 0.032043 | 0.082397 | 0.050354 | -122.2733 | -122.2778 | 0.14648 | 0.091552 | 0.013732 | 0.041198 | -0.036622 | -0.004578 | -0.01831 | -0.14191 | 0.19226 | 0.16479 | 0.11444 | 0.16937 | 0.11902 | 0.09613 | 0.004577 | 0.19684 | 122.1954 | 0.009155 | 122.319 | 0.059509 | 122.3145 | -122.2824 | -122.3373 | 0.054931 | 122.1909 | -0.027466 | 0.77362
3726.125 | 122.3465 | -0.10529 | 122.2778 | -0.12032 | -0.045807 | 0.00024143 | 0.023578 | -0.0010595 | -0.012666 | -0.0047231 | -0.077179 | 0.0072333 | 0.062782 | 0.044278 | -0.015806 | 0.028476 | -0.0066479 | -0.14191 | 0 | -0.064087 | -0.11902 | -0.013733 | -0.10529 | -0.018311 | 0.6546 | 122.2183 | -0.10529 | 122.0352 | 0.045776 | -0.004578 | 0.045776 | 0.041199 | -122.2778 | -122.3969 | 0.091553 | 0.086975 | 0 | 0.045776 | -0.041199 | 0 | -0.059509 | -0.24262 | 0.15106 | 0.15106 | 0.10071 | 0.15106 | 0.10071 | 0.050354 | -0.054932 | 0.15106 | 122.1405 | 0.064087 | 122.3236 | 0.10529 | 122.3236 | -122.3419 | -122.3831 | -0.013733 | 122.1405 | -0.036621 | 0.75989
3727.8906 | 122.406 | -0.091553 | 122.2778 | -0.10506 | -0.042603 | 0.0034456 | 0.022509 | 0.0010767 | -0.012239 | -0.0023733 | -0.089386 | 0.0063787 | 0.064277 | 0.047696 | -0.017301 | 0.027408 | -0.0098523 | -0.086975 | -0.009155 | -0.054932 | -0.050354 | 0.036621 | -0.068665 | 0.013733 | 0.70038 | 122.2183 | -0.10986 | 122.0764 | 0.09613 | 0.027466 | 0.082397 | 0.036621 | -122.287 | -122.3282 | 0.12817 | 0.10529 | 0.022888 | 0.068665 | -0.013733 | -0.01831 | -0.059509 | -0.20142 | 0.18768 | 0.17395 | 0.11902 | 0.19226 | 0.13733 | 0.091553 | 0.004578 | 0.20599 | 122.1863 | 0.045777 | 122.3282 | 0.082398 | 122.3099 | -122.3328 | -122.3877 | 0.041199 | 122.168 | 0.004578 | 0.79193
3729.6406 | 122.3419 | -0.10529 | 122.287 | -0.11269 | -0.044525 | 2.7834e-05 | 0.023578 | -0.0027685 | -0.010102 | -0.0051505 | -0.031403 | 0.0059515 | 0.065132 | 0.048337 | -0.014311 | 0.027621 | -0.0057935 | -0.16479 | 0.013733 | -0.059509 | -0.10071 | 0.009155 | -0.11444 | -0.004578 | 0.64545 | 122.2183 | -0.09613 | 122.0261 | 0.050354 | -0.022888 | 0.036621 | 0.045777 | -122.2733 | -122.3877 | 0.11444 | 0.10071 | -0.009155 | 0.054931 | -0.054932 | 0.009156 | -0.068664 | -0.26093 | 0.15564 | 0.14191 | 0.082398 | 0.13275 | 0.073242 | 0.068664 | -0.041199 | 0.14648 | 122.1222 | 0.073242 | 122.3145 | 0.11902 | 122.3236 | -122.3465 | -122.3831 | 0.004578 | 122.1313 | -0.059509 | 0.75073
3731.4062 | 122.3282 | -0.10529 | 122.287 | -0.13557 | -0.044312 | 0.0010958 | 0.025714 | -0.00084593 | -0.009675 | -0.0023733 | -0.10159 | 0.0053107 | 0.064277 | 0.051114 | -0.01602 | 0.027835 | -0.0034435 | -0.11902 | -0.022888 | -0.036621 | -0.10071 | -0.013733 | -0.14191 | -0.050354 | 0.53101 | 122.2229 | -0.082397 | 122.0261 | 0.032043 | -0.054932 | 0.027466 | 0.068665 | -122.3099 | -122.3877 | 0.091553 | 0.054932 | -0.036621 | -0.013733 | -0.10529 | 0.022889 | -0.064087 | -0.26093 | 0.13733 | 0.13275 | 0.050354 | 0.10986 | 0.027465 | 0.022888 | -0.064087 | 0.11444 | 122.1085 | 0.013733 | 122.3053 | 0.082398 | 122.3282 | -122.3236 | -122.3694 | 0.004578 | 122.1313 | -0.013733 | 0.63629
3733.1094 | 122.4838 | -0.059509 | 122.2412 | -0.1432 | -0.043457 | 0.0013094 | 0.019519 | -0.0021277 | -0.010957 | -0.0055777 | 0.029632 | 0.0059515 | 0.0662 | 0.044064 | -0.014524 | 0.025485 | -0.0019483 | -0.09613 | -0.045776 | -0.018311 | 0.022888 | 0.14191 | 0.009155 | 0.091553 | 0.78278 | 122.1634 | -0.064087 | 122.1497 | 0.20599 | 0.13733 | 0.16479 | 0.041198 | -122.287 | -122.2183 | 0.20142 | 0.15106 | 0.068664 | 0.10986 | 0.027466 | -0.004578 | -0.07782 | -0.091553 | 0.2655 | 0.2243 | 0.19684 | 0.22888 | 0.20142 | 0.16022 | 0.041199 | 0.27008 | 122.2137 | -0.027465 | 122.2275 | 0.013733 | 122.2229 | -122.2595 | -122.3053 | 0.082397 | 122.2092 | -0.036621 | 0.84229
3734.8906 | 122.3785 | -0.086975 | 122.2504 | -0.11269 | -0.042176 | 0.0010958 | 0.023364 | -0.00084593 | -0.0088206 | -0.0017325 | -0.11075 | 0.0074469 | 0.060859 | 0.048337 | -0.018156 | 0.026767 | -0.0049389 | -0.14191 | -0.027466 | -0.068665 | -0.082397 | -0.004578 | -0.14191 | -0.036621 | 0.52643 | 122.2183 | -0.09613 | 122.0718 | 0.07782 | 0 | 0.07782 | 0.01831 | -122.2778 | -122.3328 | 0.082397 | 0.050354 | -0.054932 | 0.032044 | -0.073242 | -0.009155 | -0.032043 | -0.17853 | 0.16479 | 0.16479 | 0.086975 | 0.17395 | 0.09613 | 0.064087 | -0.013732 | 0.17395 | 122.168 | 0.041199 | 122.3145 | 0.059509 | 122.3053 | -122.319 | -122.3465 | 0.004578 | 122.1588 | -0.054932 | 0.6134
3736.6562 | 122.493 | -0.050354 | 122.2458 | -0.1432 | -0.045807 | 0.002164 | 0.021655 | 0.0027857 | -0.01053 | -0.0030141 | 0.0052185 | 0.0063787 | 0.061286 | 0.041928 | -0.018369 | 0.028049 | -0.0075025 | -0.086975 | -0.050354 | -0.018311 | 0.054932 | 0.19684 | 0.041199 | 0.13275 | 0.80566 | 122.1634 | -0.054932 | 122.1497 | 0.19684 | 0.16479 | 0.15564 | 0.032043 | -122.2961 | -122.1909 | 0.24719 | 0.18311 | 0.091553 | 0.15106 | 0.05951 | -0.004578 | -0.082398 | -0.096131 | 0.24719 | 0.20599 | 0.21515 | 0.21057 | 0.21973 | 0.21515 | 0.073243 | 0.25177 | 122.2046 | -0.032043 | 122.2183 | 0 | 122.2137 | -122.2641 | -122.3007 | 0.10529 | 122.2 | -0.036621 | 0.85602
3738.4062 | 122.4472 | -0.050354 | 122.2412 | -0.13557 | -0.043671 | 0.0019504 | 0.0208 | -0.0046911 | -0.010316 | -0.0055777 | -0.016144 | 0.0083013 | 0.062995 | 0.046628 | -0.017729 | 0.026553 | -0.0083569 | -0.07782 | -0.045776 | -0.027466 | 0.045776 | 0.15106 | 0.009155 | 0.10529 | 0.80566 | 122.1771 | -0.07782 | 122.1313 | 0.17395 | 0.13733 | 0.15564 | 0.022888 | -122.287 | -122.1954 | 0.20142 | 0.15564 | 0.059509 | 0.13275 | 0.036621 | -0.027466 | -0.064087 | -0.10986 | 0.2243 | 0.20599 | 0.18768 | 0.23346 | 0.21515 | 0.17853 | 0.073242 | 0.25177 | 122.2092 | -0.01831 | 122.2549 | 0.004578 | 122.2275 | -122.2687 | -122.319 | 0.09613 | 122.1817 | -0.027466 | 0.85602
3740.1719 | 122.4335 | -0.059509 | 122.2321 | -0.15846 | -0.042816 | 0.0017368 | 0.024646 | 0.0015039 | -0.009675 | -0.0042959 | -0.11075 | 0.0085149 | 0.063423 | 0.045559 | -0.019865 | 0.029544 | -0.0064343 | -0.13733 | -0.009155 | -0.045776 | -0.054932 | 0.045776 | -0.11902 | 0.004578 | 0.57678 | 122.2183 | -0.086975 | 122.1222 | 0.1236 | 0.064087 | 0.13733 | 0.013733 | -122.2412 | -122.287 | 0.10528 | 0.064087 | -0.05951 | 0.050354 | -0.073243 | -0.027466 | -0.013733 | -0.10986 | 0.1831 | 0.19684 | 0.1236 | 0.2243 | 0.15106 | 0.091552 | -0.009156 | 0.21057 | 122.2092 | 0.036621 | 122.3053 | 0.050354 | 122.2778 | -122.2778 | -122.319 | 0.004577 | 122.1817 | -0.07782 | 0.63629
3741.875 | 122.319 | -0.10071 | 122.287 | -0.13557 | -0.041321 | 0.0040866 | 0.024005 | 0.00022207 | -0.010957 | -0.0021597 | -0.1199 | 0.0065923 | 0.063423 | 0.0509 | -0.017515 | 0.027835 | -0.0057935 | -0.13275 | -0.009155 | -0.059509 | -0.086975 | -0.036621 | -0.16937 | -0.050354 | 0.52643 | 122.2321 | -0.09613 | 122.0306 | 0.018311 | -0.045776 | 0.045776 | 0.041199 | -122.2961 | -122.374 | 0.064087 | 0.050354 | -0.068665 | 0.009155 | -0.10986 | 0.004578 | -0.054931 | -0.25635 | 0.11902 | 0.14648 | 0.054932 | 0.14191 | 0.050354 | 0.022888 | -0.027466 | 0.11444 | 122.1268 | 0.050354 | 122.3282 | 0.091553 | 122.3328 | -122.3465 | -122.3831 | 0.013733 | 122.1313 | -0.032043 | 0.62714
3743.6406 | 122.374 | -0.10529 | 122.2778 | -0.15083 | -0.042603 | 0.0023776 | 0.022723 | 0.0059901 | -0.013947 | -0.0042959 | -0.074127 | 0.0070197 | 0.064491 | 0.048764 | -0.017515 | 0.02634 | -0.0064343 | -0.13275 | 0 | -0.068665 | -0.10071 | 0.004578 | -0.10071 | -0.022888 | 0.67291 | 122.2504 | -0.10529 | 122.0673 | 0.07782 | 0.004578 | 0.050354 | 0.036621 | -122.2778 | -122.3785 | 0.10986 | 0.082398 | 0.004578 | 0.045777 | -0.032043 | 0 | -0.027466 | -0.21057 | 0.18311 | 0.15564 | 0.10986 | 0.15564 | 0.10986 | 0.073243 | -0.032043 | 0.18311 | 122.1725 | 0.068665 | 122.3557 | 0.10529 | 122.3557 | -122.3465 | -122.3831 | 0.004578 | 122.1725 | -0.027465 | 0.7782
3745.3438 | 122.4289 | -0.054932 | 122.2458 | -0.18898 | -0.043671 | 0.002164 | 0.021869 | 0.00064947 | -0.0090342 | -0.0021597 | -0.040558 | 0.0042425 | 0.062995 | 0.049191 | -0.015806 | 0.026981 | -0.0060071 | -0.086975 | -0.041199 | -0.009155 | 0.013733 | 0.12817 | -0.041199 | 0.054932 | 0.6546 | 122.2137 | -0.064087 | 122.113 | 0.14191 | 0.09613 | 0.1236 | 0.045777 | -122.287 | -122.2321 | 0.18311 | 0.10986 | 0.013733 | 0.064087 | -0.032044 | -0.009155 | -0.032044 | -0.13275 | 0.19684 | 0.17853 | 0.15106 | 0.18768 | 0.16022 | 0.13733 | 0.022888 | 0.20599 | 122.1771 | -0.032044 | 122.2778 | 0.013733 | 122.2687 | -122.2549 | -122.3099 | 0.068665 | 122.168 | -0.032043 | 0.70953
3747.1094 | 122.438 | -0.068665 | 122.2549 | -0.20424 | -0.044739 | 0.001523 | 0.022509 | -0.0012731 | -0.010316 | -0.0040823 | -0.028351 | 0.0063787 | 0.064918 | 0.041928 | -0.017942 | 0.025058 | -0.0040845 | -0.10529 | -0.027466 | -0.041199 | -0.032043 | 0.073242 | -0.045776 | 0.050354 | 0.67749 | 122.1817 | -0.059509 | 122.1085 | 0.16022 | 0.10986 | 0.11902 | 0.027466 | -122.2824 | -122.287 | 0.14191 | 0.11902 | 0.022889 | 0.091553 | -0.004577 | 0.009156 | -0.073242 | -0.14648 | 0.22888 | 0.18768 | 0.17853 | 0.17853 | 0.16937 | 0.11444 | 0.009156 | 0.21973 | 122.168 | 0.013733 | 122.2412 | 0.041199 | 122.2504 | -122.2961 | -122.3145 | 0.036622 | 122.1771 | -0.036621 | 0.74616
3748.875 | 122.3877 | -0.064087 | 122.2687 | -0.10506 | -0.043885 | 0.0013094 | 0.0255 | -0.0017005 | -0.011811 | -0.0051505 | -0.092438 | 0.0070197 | 0.062995 | 0.046628 | -0.01901 | 0.026767 | -0.0075025 | -0.09613 | -0.009155 | -0.059509 | -0.041199 | 0.032043 | -0.07782 | 0.004578 | 0.71869 | 122.2275 | -0.07782 | 122.081 | 0.10986 | 0.032043 | 0.09613 | 0.004578 | -122.2778 | -122.3099 | 0.09613 | 0.068665 | -0.013733 | 0.064087 | -0.018311 | -0.013733 | -0.041199 | -0.18768 | 0.17395 | 0.16022 | 0.09613 | 0.17395 | 0.10986 | 0.091552 | 0.01831 | 0.18768 | 122.1588 | 0.050354 | 122.3053 | 0.054932 | 122.2916 | -122.3282 | -122.3465 | 0.022888 | 122.1451 | -0.032043 | 0.78278
3750.6406 | 122.3602 | -0.09613 | 122.2916 | -0.12794 | -0.040894 | 0.0019504 | 0.024646 | -0.00063233 | -0.01117 | -0.0036551 | -0.1199 | 0.0055243 | 0.062995 | 0.049191 | -0.015592 | 0.027408 | -0.0042981 | -0.1236 | 0 | -0.064087 | -0.091553 | -0.018311 | -0.16022 | -0.036621 | 0.53101 | 122.2183 | -0.09613 | 122.0352 | 0.041199 | -0.041199 | 0.050354 | 0.032043 | -122.2916 | -122.3831 | 0.077819 | 0.059509 | -0.064087 | 0.027466 | -0.09613 | 0 | -0.073242 | -0.25635 | 0.13733 | 0.14648 | 0.054931 | 0.14648 | 0.054931 | 0.045776 | -0.027466 | 0.13733 | 122.1313 | 0.064087 | 122.3145 | 0.09613 | 122.3145 | -122.3557 | -122.3877 | 0.004577 | 122.1313 | -0.027466 | 0.62714
3752.3281 | 122.3419 | -0.11444 | 122.3053 | -0.15083 | -0.04068 | 0.0036594 | 0.024859 | -0.0017005 | -0.010743 | -0.0032277 | -0.1077 | 0.0070197 | 0.063423 | 0.049832 | -0.017729 | 0.024631 | -0.0030163 | -0.14648 | -0.004578 | -0.045776 | -0.09613 | -0.027466 | -0.15106 | -0.036621 | 0.5127 | 122.2366 | -0.09613 | 122.0398 | 0.013733 | -0.036621 | 0.050354 | 0.068665 | -122.3099 | -122.4014 | 0.086975 | 0.07782 | -0.036621 | 0.009155 | -0.10529 | 0.018311 | -0.068665 | -0.2655 | 0.12817 | 0.16479 | 0.07782 | 0.14648 | 0.059509 | 0.01831 | -0.050354 | 0.10986 | 122.1359 | 0.041198 | 122.3328 | 0.10986 | 122.3511 | -122.3511 | -122.4014 | 0.018311 | 122.1542 | -0.032043 | 0.62714
3754.0938 | 122.4747 | -0.045776 | 122.2137 | -0.082169 | -0.044312 | 0.0017368 | 0.019732 | -0.0021277 | -0.012025 | -0.0055777 | -0.0069885 | 0.0068059 | 0.062568 | 0.051541 | -0.019438 | 0.025058 | -0.0047253 | -0.07782 | -0.036621 | -0.022888 | 0.050354 | 0.19226 | 0.041199 | 0.13275 | 0.8194 | 122.1909 | -0.073242 | 122.1451 | 0.20599 | 0.14648 | 0.15106 | 0.022888 | -122.2504 | -122.1634 | 0.23804 | 0.17853 | 0.086975 | 0.15564 | 0.064087 | -0.027466 | -0.022888 | -0.068664 | 0.25177 | 0.19684 | 0.19226 | 0.2243 | 0.21973 | 0.21515 | 0.073242 | 0.27924 | 122.2183 | -0.013733 | 122.2641 | 0.009155 | 122.2366 | -122.2366 | -122.287 | 0.09613 | 122.1909 | -0.032044 | 0.86517
3755.7969 | 122.4197 | -0.059509 | 122.2687 | -0.18135 | -0.043671 | 0.0025912 | 0.022723 | -0.0031957 | -0.011811 | -0.0049367 | -0.04361 | 0.0055243 | 0.063209 | 0.042569 | -0.017515 | 0.025485 | -0.0064343 | -0.10071 | -0.036621 | -0.022888 | -0.018311 | 0.10071 | -0.050354 | 0.050354 | 0.63171 | 122.1771 | -0.091553 | 122.1039 | 0.10986 | 0.068665 | 0.10986 | 0.036621 | -122.3053 | -122.287 | 0.16022 | 0.10986 | 0.009155 | 0.073242 | -0.027466 | -0.032044 | -0.091553 | -0.16479 | 0.16937 | 0.16937 | 0.12817 | 0.20142 | 0.16022 | 0.1236 | 0.004577 | 0.20142 | 122.1954 | -0.013733 | 122.2687 | 0.022888 | 122.2366 | -122.2916 | -122.3602 | 0.041198 | 122.1634 | -0.041199 | 0.69122
3757.5469 | 122.4106 | -0.064087 | 122.2321 | -0.1432 | -0.041748 | 0.00088223 | 0.022937 | -0.0012731 | -0.01053 | -0.0053641 | -0.028351 | 0.0048833 | 0.059791 | 0.041928 | -0.017729 | 0.026126 | -0.0055799 | -0.10986 | -0.045776 | -0.027466 | -0.027466 | 0.054932 | -0.064087 | 0.045776 | 0.63629 | 122.2092 | -0.068665 | 122.081 | 0.12817 | 0.068665 | 0.10986 | 0.036621 | -122.2778 | -122.2595 | 0.11902 | 0.10986 | 0 | 0.073242 | -0.036621 | -0.004578 | -0.022889 | -0.15106 | 0.19226 | 0.17395 | 0.13275 | 0.17853 | 0.13733 | 0.082398 | 0 | 0.19684 | 122.1497 | -0.01831 | 122.2778 | 0.018311 | 122.2733 | -122.2595 | -122.3007 | 0.036621 | 122.1451 | -0.045776 | 0.70038
3759.3125 | 122.3602 | -0.091553 | 122.287 | -0.18135 | -0.040894 | 0.0025912 | 0.026782 | -0.0036231 | -0.0094614 | -0.0010915 | -0.1077 | 0.0083013 | 0.06385 | 0.053464 | -0.019224 | 0.027194 | -0.0019483 | -0.13275 | -0.009155 | -0.068665 | -0.091553 | -0.013733 | -0.14191 | -0.032043 | 0.53558 | 122.2229 | -0.10071 | 122.0627 | 0.050354 | -0.018311 | 0.054932 | 0.022888 | -122.2961 | -122.3785 | 0.07782 | 0.05951 | -0.050354 | 0.036622 | -0.073242 | -0.009155 | -0.064087 | -0.2243 | 0.14191 | 0.14649 | 0.073242 | 0.15564 | 0.082397 | 0.054932 | -0.022888 | 0.15106 | 122.1634 | 0.05951 | 122.3236 | 0.082398 | 122.3145 | -122.3557 | -122.3877 | 0 | 122.1542 | -0.041198 | 0.62714
3761.0781 | 122.4335 | -0.045776 | 122.2595 | -0.15846 | -0.043885 | -0.00018577 | 0.019732 | -0.0055457 | -0.01117 | -0.0055777 | -0.034454 | 0.0063787 | 0.065345 | 0.046628 | -0.017301 | 0.026553 | -0.0030163 | -0.11444 | -0.032043 | -0.013733 | -0.036621 | 0.059509 | -0.082397 | 0.032043 | 0.64545 | 122.2 | -0.073242 | 122.1039 | 0.11444 | 0.07782 | 0.1236 | 0.032043 | -122.2916 | -122.2961 | 0.10528 | 0.077819 | -0.036621 | 0.045776 | -0.068664 | -0.027466 | -0.059509 | -0.15564 | 0.16022 | 0.16937 | 0.1236 | 0.19684 | 0.15106 | 0.073242 | -0.022888 | 0.18768 | 122.1771 | -0.01831 | 122.2733 | 0.013733 | 122.2458 | -122.2733 | -122.3328 | 0.009155 | 122.1497 | -0.068665 | 0.69122
3762.7969 | 122.4289 | -0.041199 | 122.2412 | -0.097427 | -0.043457 | 0.002164 | 0.022296 | -0.0012731 | -0.010743 | -0.0032277 | -0.019196 | 0.0072333 | 0.064063 | 0.043423 | -0.016447 | 0.024417 | -0.0066479 | -0.10529 | -0.050354 | -0.009155 | -0.027466 | 0.050354 | -0.054932 | 0.050354 | 0.65918 | 122.2046 | -0.086975 | 122.0993 | 0.13733 | 0.059509 | 0.10529 | 0.032044 | -122.2916 | -122.2687 | 0.091553 | 0.091553 | -0.013733 | 0.059509 | -0.045777 | -0.045776 | -0.036621 | -0.14191 | 0.17853 | 0.14649 | 0.10071 | 0.19226 | 0.14648 | 0.059509 | -0.018311 | 0.2243 | 122.1863 | -0.041199 | 122.2916 | -0.009155 | 122.2458 | -122.2504 | -122.3282 | 0.013733 | 122.1405 | -0.064087 | 0.70038
3764.5625 | 122.4243 | -0.059509 | 122.2733 | -0.15846 | -0.044525 | 0.0019504 | 0.023791 | 0.00043587 | -0.01352 | -0.0025869 | -0.013092 | 0.0044561 | 0.062782 | 0.044491 | -0.017942 | 0.026126 | -0.0042981 | -0.086975 | -0.018311 | 0 | -0.013733 | 0.068665 | -0.059509 | 0.041199 | 0.65002 | 122.1725 | -0.07782 | 122.113 | 0.11902 | 0.064087 | 0.11902 | 0.059509 | -122.2916 | -122.287 | 0.12817 | 0.10071 | 0 | 0.041199 | -0.059509 | -0.018311 | -0.10071 | -0.16022 | 0.17853 | 0.17853 | 0.1236 | 0.19684 | 0.14191 | 0.068665 | -0.013733 | 0.19684 | 122.1909 | -0.018311 | 122.2504 | 0.041198 | 122.2321 | -122.2733 | -122.3511 | 0.045776 | 122.1725 | -0.027466 | 0.70953
3766.3125 | 122.4701 | -0.032043 | 122.2595 | -0.12794 | -0.041748 | 0.0023776 | 0.024432 | -0.0027685 | -0.0098886 | -0.0028005 | -0.11075 | 0.0061651 | 0.062995 | 0.0556 | -0.017729 | 0.02933 | -0.0055799 | -0.10529 | -0.022888 | -0.036621 | -0.013733 | 0.064087 | -0.082397 | 0.032043 | 0.63171 | 122.2137 | -0.07782 | 122.1451 | 0.15106 | 0.10071 | 0.16937 | -0.004578 | -122.2824 | -122.2733 | 0.09613 | 0.064086 | -0.050354 | 0.068664 | -0.045776 | -0.045777 | -0.045776 | -0.11444 | 0.18311 | 0.20142 | 0.13275 | 0.24719 | 0.17853 | 0.10071 | 0.022888 | 0.22888 | 122.2229 | 0.013733 | 122.2916 | 0.009155 | 122.2458 | -122.2961 | -122.3373 | 0.01831 | 122.1771 | -0.073243 | 0.66376
3768.0781 | 122.438 | -0.050354 | 122.2504 | -0.21187 | -0.041321 | 0.001523 | 0.0208 | 0.0012903 | -0.0094614 | -0.0040823 | -0.055817 | 0.0095831 | 0.064063 | 0.045346 | -0.017515 | 0.028903 | -0.0038709 | -0.07782 | -0.045776 | 0 | 0.032043 | 0.13275 | -0.045776 | 0.059509 | 0.67749 | 122.1909 | -0.068665 | 122.1405 | 0.14648 | 0.086975 | 0.14191 | 0.050354 | -122.2961 | -122.2183 | 0.18311 | 0.10986 | 0.004578 | 0.059509 | -0.045776 | -0.018311 | -0.059509 | -0.10986 | 0.19684 | 0.19226 | 0.13733 | 0.21057 | 0.15564 | 0.13275 | 0.032043 | 0.21515 | 122.2092 | -0.045776 | 122.2595 | 0.004578 | 122.2412 | -122.2504 | -122.319 | 0.082397 | 122.1909 | -0.027466 | 0.72784
3769.8438 | 122.4152 | -0.073242 | 122.2458 | -0.2195 | -0.044098 | 0.0036594 | 0.021869 | -0.0023413 | -0.0081796 | -0.0017325 | -0.037506 | 0.0063787 | 0.061073 | 0.046414 | -0.017088 | 0.026981 | -0.0077161 | -0.1236 | -0.045776 | -0.018311 | -0.032043 | 0.064087 | -0.059509 | 0.041199 | 0.6546 | 122.1954 | -0.082397 | 122.1085 | 0.11902 | 0.068665 | 0.09613 | 0.054931 | -122.2916 | -122.2778 | 0.13733 | 0.11444 | 0.013733 | 0.05951 | -0.041198 | -0.009155 | -0.050354 | -0.13733 | 0.19226 | 0.16937 | 0.14191 | 0.17853 | 0.15106 | 0.082398 | -0.013732 | 0.20142 | 122.1909 | -0.027465 | 122.2778 | 0.027466 | 122.2687 | -122.2641 | -122.3282 | 0.041199 | 122.1817 | -0.050354 | 0.72784
3771.5469 | 122.3923 | -0.086975 | 122.2595 | -0.10506 | -0.042603 | 0.0010958 | 0.026996 | 0.0010767 | -0.009675 | -0.0030141 | -0.14432 | 0.0065923 | 0.061927 | 0.051968 | -0.018583 | 0.028049 | -0.0040845 | -0.13275 | -0.013733 | -0.041199 | -0.073242 | -0.009155 | -0.14191 | -0.027466 | 0.56305 | 122.2229 | -0.073242 | 122.0856 | 0.091553 | 0.018311 | 0.082397 | 0.045776 | -122.2733 | -122.3328 | 0.07782 | 0.059509 | -0.054932 | 0.013733 | -0.10071 | 0.013733 | -0.036621 | -0.17395 | 0.17853 | 0.16937 | 0.10529 | 0.15564 | 0.091553 | 0.032044 | -0.032043 | 0.16479 | 122.1588 | 0.027466 | 122.2961 | 0.073242 | 122.3099 | -122.3007 | -122.3328 | 0.013733 | 122.1725 | -0.045776 | 0.65002
3773.2969 | 122.3419 | -0.10529 | 122.2916 | -0.17372 | -0.041535 | 0.0045138 | 0.025287 | -0.00084593 | -0.009675 | -0.0030141 | -0.14737 | 0.0085149 | 0.060432 | 0.051755 | -0.017088 | 0.027408 | -0.0062207 | -0.12817 | -0.013733 | -0.045776 | -0.07782 | -0.013733 | -0.14648 | -0.041199 | 0.56305 | 122.2321 | -0.086975 | 122.0306 | 0.036621 | -0.054932 | 0.027466 | 0.05951 | -122.3053 | -122.3694 | 0.091553 | 0.064087 | -0.041198 | 0.004577 | -0.10071 | 0.018311 | -0.059509 | -0.26093 | 0.14191 | 0.13275 | 0.050354 | 0.11444 | 0.032043 | 0.032043 | -0.032044 | 0.1236 | 122.1176 | 0.032043 | 122.319 | 0.091553 | 122.3373 | -122.3373 | -122.3785 | 0.027466 | 122.1359 | -0.022888 | 0.66834
3775.0469 | 122.4289 | -0.068665 | 122.2321 | -0.15846 | -0.041962 | -0.00018577 | 0.021869 | 0.00064947 | -0.01053 | -0.0036551 | -0.034454 | 0.0048833 | 0.06385 | 0.048337 | -0.014524 | 0.025699 | -0.00045291 | -0.11902 | -0.032043 | -0.032043 | -0.032043 | 0.059509 | -0.064087 | 0.045776 | 0.66376 | 122.2 | -0.073242 | 122.0947 | 0.13275 | 0.07782 | 0.10529 | 0.036622 | -122.2641 | -122.2641 | 0.12817 | 0.11444 | 0.004578 | 0.077819 | -0.032044 | -0.004577 | -0.032044 | -0.13733 | 0.20142 | 0.17395 | 0.14649 | 0.17853 | 0.15106 | 0.091552 | 0 | 0.20599 | 122.168 | 0 | 122.2733 | 0.036622 | 122.2687 | -122.2641 | -122.3053 | 0.036622 | 122.1634 | -0.050354 | 0.73242
3776.75 | 122.4518 | -0.050354 | 122.2641 | -0.16609 | -0.04068 | 0.0023776 | 0.022509 | -0.00041873 | -0.0094614 | -0.0023733 | -0.046661 | 0.0065923 | 0.061927 | 0.048764 | -0.017729 | 0.027835 | -0.0028027 | -0.059509 | -0.041199 | -0.004578 | 0.041199 | 0.16022 | -0.022888 | 0.073242 | 0.70038 | 122.1817 | -0.059509 | 122.1542 | 0.16022 | 0.10529 | 0.14648 | 0.045776 | -122.3053 | -122.2229 | 0.21057 | 0.1236 | 0.027466 | 0.07782 | -0.01831 | -0.009155 | -0.082397 | -0.10986 | 0.21057 | 0.19684 | 0.15564 | 0.20599 | 0.16479 | 0.16479 | 0.045777 | 0.21973 | 122.2137 | -0.036621 | 122.2412 | 0.009155 | 122.2321 | -122.2687 | -122.3236 | 0.091553 | 122.2046 | -0.009155 | 0.75073
3778.5 | 122.3923 | -0.09613 | 122.2778 | -0.097427 | -0.043885 | 0.0023776 | 0.024005 | -0.00063233 | -0.011384 | -0.0066457 | -0.11075 | 0.0072333 | 0.064704 | 0.051327 | -0.017301 | 0.029117 | -0.0064343 | -0.12817 | 0 | -0.064087 | -0.068665 | 0 | -0.10071 | -0.013733 | 0.69122 | 122.2321 | -0.091553 | 122.0718 | 0.09613 | 0.018311 | 0.082397 | 0.032043 | -122.2778 | -122.3465 | 0.09613 | 0.082397 | -0.004578 | 0.050354 | -0.036621 | 0.004577 | -0.045776 | -0.20599 | 0.19226 | 0.17853 | 0.11444 | 0.17395 | 0.10986 | 0.064087 | -0.004578 | 0.18768 | 122.1634 | 0.064087 | 122.3236 | 0.09613 | 122.3282 | -122.3419 | -122.3694 | 0.027465 | 122.168 | -0.032044 | 0.78735
3780.2656 | 122.4106 | -0.082397 | 122.3007 | -0.16609 | -0.041748 | 0.0023776 | 0.022509 | 8.47e-06 | -0.010957 | -0.0062185 | -0.11685 | 0.0061651 | 0.061714 | 0.051114 | -0.016874 | 0.02869 | -0.0032299 | -0.09613 | -0.027466 | -0.036621 | -0.036621 | 0.054932 | -0.068665 | 0.013733 | 0.71411 | 122.2504 | -0.086975 | 122.0947 | 0.11902 | 0.050354 | 0.082397 | 0.045776 | -122.3282 | -122.3373 | 0.13733 | 0.09613 | 0.013732 | 0.050354 | -0.032044 | -0.004578 | -0.050354 | -0.20599 | 0.20142 | 0.16479 | 0.13275 | 0.16937 | 0.13733 | 0.091553 | 0 | 0.20599 | 122.1817 | 0.009155 | 122.3373 | 0.054931 | 122.3328 | -122.3373 | -122.3877 | 0.045776 | 122.1771 | -0.013733 | 0.79651
3781.9844 | 122.3785 | -0.10529 | 122.287 | -0.15083 | -0.044312 | 0.001523 | 0.022723 | 0.0012903 | -0.01053 | -0.0055777 | -0.068024 | 0.0076605 | 0.062995 | 0.045773 | -0.016447 | 0.028476 | -0.0053661 | -0.12817 | -0.009155 | -0.073242 | -0.091553 | -0.022888 | -0.10071 | -0.018311 | 0.71411 | 122.2092 | -0.10071 | 122.0535 | 0.082397 | -0.004578 | 0.054932 | 0.032044 | -122.2961 | -122.3785 | 0.082398 | 0.086975 | 0.004578 | 0.054931 | -0.027466 | 0.004578 | -0.07782 | -0.23346 | 0.18768 | 0.16022 | 0.10071 | 0.15564 | 0.09613 | 0.050354 | -0.018311 | 0.18311 | 122.1542 | 0.064087 | 122.3099 | 0.096131 | 122.3145 | -122.3602 | -122.3877 | 0.013733 | 122.1588 | -0.022888 | 0.8194
3783.75 | 122.3282 | -0.091553 | 122.3053 | -0.12794 | -0.041321 | 0.0023776 | 0.026782 | -0.0023413 | -0.012666 | -0.0038687 | -0.12906 | 0.0070197 | 0.063423 | 0.050686 | -0.01602 | 0.028903 | -0.0064343 | -0.10529 | -0.018311 | -0.073242 | -0.086975 | 0.009155 | -0.13733 | -0.027466 | 0.59052 | 122.2321 | -0.10071 | 122.0352 | 0.018311 | -0.050354 | 0.036621 | 0.018311 | -122.3236 | -122.3923 | 0.10071 | 0.064087 | -0.045776 | 0.045776 | -0.064087 | -0.009155 | -0.073242 | -0.27008 | 0.10986 | 0.12817 | 0.041199 | 0.13733 | 0.050354 | 0.082397 | -0.013733 | 0.11902 | 122.1359 | 0.054931 | 122.3328 | 0.073242 | 122.3236 | -122.3785 | -122.406 | 0.004578 | 122.1268 | -0.013733 | 0.68207
3785.5312 | 122.4655 | -0.054932 | 122.2641 | -0.11269 | -0.041107 | 0.0025912 | 0.021014 | -0.0025549 | -0.010102 | -0.0051505 | 0.0021667 | 0.0050971 | 0.065132 | 0.039364 | -0.016874 | 0.027835 | -0.0087841 | -0.082397 | -0.050354 | -0.013733 | 0.018311 | 0.14191 | 0.009155 | 0.09613 | 0.82398 | 122.168 | -0.045776 | 122.1725 | 0.21515 | 0.16937 | 0.16937 | 0.041199 | -122.3145 | -122.2458 | 0.19684 | 0.15106 | 0.064087 | 0.10986 | 0.022888 | 0.009156 | -0.09613 | -0.091553 | 0.27008 | 0.22431 | 0.22431 | 0.21515 | 0.21515 | 0.15564 | 0.032044 | 0.26093 | 122.2183 | -0.036621 | 122.2137 | 0.004578 | 122.2229 | -122.2778 | -122.3099 | 0.073243 | 122.2275 | -0.027465 | 0.87891
3787.2812 | 122.4701 | -0.045776 | 122.2733 | -0.22713 | -0.040894 | 0.0030184 | 0.022723 | -0.0044775 | -0.009675 | -0.0013051 | -0.046661 | 0.0057379 | 0.062141 | 0.043423 | -0.020506 | 0.026126 | -0.0051525 | -0.064087 | -0.041199 | -0.018311 | 0.032043 | 0.14648 | -0.022888 | 0.07782 | 0.70038 | 122.1817 | -0.073242 | 122.1451 | 0.16022 | 0.10986 | 0.15106 | 0.027465 | -122.3145 | -122.2412 | 0.19226 | 0.1236 | 0.022888 | 0.096131 | -0.004577 | -0.027466 | -0.091552 | -0.12817 | 0.20599 | 0.19684 | 0.15564 | 0.2243 | 0.18311 | 0.16479 | 0.050354 | 0.23346 | 122.2183 | -0.022888 | 122.2549 | 0.004577 | 122.2275 | -122.2916 | -122.3465 | 0.077819 | 122.1909 | -0.018311 | 0.74615
3788.9844 | 122.4014 | -0.068665 | 122.2549 | -0.15083 | -0.042176 | 0.001523 | 0.023364 | 0.0015039 | -0.009675 | -0.0019461 | -0.09549 | 0.0078741 | 0.064277 | 0.051114 | -0.017515 | 0.02869 | -0.0079297 | -0.082397 | -0.013733 | -0.032043 | -0.036621 | 0.054932 | -0.059509 | 0.018311 | 0.74158 | 122.2321 | -0.082397 | 122.0993 | 0.11444 | 0.041199 | 0.091553 | 0.036622 | -122.2687 | -122.2916 | 0.1236 | 0.086976 | 0.009156 | 0.050354 | -0.027466 | -0.013732 | -0.022888 | -0.15564 | 0.18311 | 0.16022 | 0.10986 | 0.17395 | 0.1236 | 0.086975 | -0.004578 | 0.19684 | 122.1817 | 0.01831 | 122.3145 | 0.054932 | 122.3007 | -122.287 | -122.3373 | 0.032044 | 122.168 | -0.013732 | 0.81024
3790.75 | 122.3511 | -0.10071 | 122.2916 | -0.17372 | -0.041321 | 0.0060092 | 0.023578 | 0.0010767 | -0.0075388 | -0.0066457 | -0.11685 | 0.0065923 | 0.063636 | 0.047909 | -0.015165 | 0.028049 | -0.0047253 | -0.15106 | 0.018311 | -0.059509 | -0.1236 | -0.045776 | -0.16479 | -0.027466 | 0.55389 | 122.2412 | -0.09613 | 122.0261 | 0.027466 | -0.054932 | 0.036621 | 0.041199 | -122.2733 | -122.4152 | 0.054932 | 0.073242 | -0.064087 | 0.032043 | -0.10529 | 0.004578 | -0.050354 | -0.2655 | 0.12817 | 0.13733 | 0.045776 | 0.13275 | 0.041198 | 0.013733 | -0.064087 | 0.1236 | 122.1222 | 0.07782 | 122.3373 | 0.11902 | 122.3419 | -122.3511 | -122.3877 | -0.022888 | 122.1268 | -0.050354 | 0.6546
3792.4531 | 122.3511 | -0.086975 | 122.2961 | -0.097427 | -0.042816 | -0.0018948 | 0.02016 | 0.0010767 | -0.010102 | -0.0049367 | -0.049713 | 0.0072333 | 0.063636 | 0.042142 | -0.015806 | 0.027835 | -0.0040845 | -0.15106 | -0.004578 | -0.054932 | -0.07782 | 0.022888 | -0.10529 | -0.009155 | 0.72784 | 122.2183 | -0.091553 | 122.0169 | 0.050354 | -0.004578 | 0.018311 | 0.032043 | -122.3007 | -122.374 | 0.10986 | 0.07782 | -0.018311 | 0.045777 | -0.050354 | -0.004578 | -0.07782 | -0.27924 | 0.13733 | 0.10529 | 0.082397 | 0.10986 | 0.086975 | 0.07782 | -0.022888 | 0.14191 | 122.1085 | 0.050354 | 122.3099 | 0.082397 | 122.3053 | -122.3511 | -122.3877 | 0.009155 | 122.1039 | -0.064087 | 0.81482
3794.2031 | 122.3419 | -0.10529 | 122.2778 | -0.11269 | -0.044312 | 0.0017368 | 0.022723 | -0.0025549 | -0.011598 | -0.0019461 | -0.06192 | 0.0078741 | 0.065132 | 0.051327 | -0.01666 | 0.02634 | -0.0087841 | -0.15106 | 0 | -0.068665 | -0.10071 | 0.004578 | -0.10071 | -0.018311 | 0.72784 | 122.2458 | -0.082397 | 122.0078 | 0.045776 | -0.004578 | 0.013733 | 0.036621 | -122.2778 | -122.3785 | 0.10986 | 0.086975 | 0.004578 | 0.050354 | -0.032043 | 0.022889 | -0.032043 | -0.27008 | 0.15106 | 0.11902 | 0.10071 | 0.09613 | 0.077819 | 0.073243 | -0.032043 | 0.12817 | 122.0901 | 0.068665 | 122.3282 | 0.10529 | 122.3511 | -122.3465 | -122.3602 | 0.004578 | 122.113 | -0.045776 | 0.83313
3795.9531 | 122.3373 | -0.091553 | 122.3007 | -0.17372 | -0.041535 | 0.0030184 | 0.023578 | -0.0036231 | -0.01053 | -0.0034415 | -0.098541 | 0.0080877 | 0.064918 | 0.04855 | -0.017515 | 0.028903 | -0.0064343 | -0.14191 | 0 | -0.064087 | -0.10071 | -0.032043 | -0.16022 | -0.041199 | 0.56763 | 122.2229 | -0.1236 | 122.0398 | 0.018311 | -0.045776 | 0.045776 | 0.027466 | -122.3007 | -122.4014 | 0.05951 | 0.050354 | -0.068664 | 0.022888 | -0.09613 | -0.032043 | -0.07782 | -0.26093 | 0.10986 | 0.13733 | 0.045777 | 0.16937 | 0.07782 | 0.032044 | -0.036621 | 0.14191 | 122.1634 | 0.064087 | 122.3465 | 0.091553 | 122.3145 | -122.3648 | -122.4243 | -0.009155 | 122.1313 | -0.050354 | 0.65918
3797.7031 | 122.3511 | -0.10986 | 122.2778 | -0.19661 | -0.042389 | 0.0010958 | 0.022082 | -0.00063233 | -0.009675 | -0.0015189 | -0.080231 | 0.0070197 | 0.06385 | 0.055173 | -0.01666 | 0.027194 | -0.0051525 | -0.13733 | 0 | -0.059509 | -0.10986 | -0.032043 | -0.15106 | -0.041199 | 0.56305 | 122.2229 | -0.10529 | 122.0444 | 0.041199 | -0.036621 | 0.045776 | 0.050354 | -122.2778 | -122.3877 | 0.07782 | 0.068664 | -0.041199 | 0.01831 | -0.091553 | 0.004577 | -0.054932 | -0.23346 | 0.15106 | 0.15564 | 0.073242 | 0.15106 | 0.068665 | 0.027466 | -0.050354 | 0.14649 | 122.1497 | 0.059509 | 122.3282 | 0.10986 | 122.3328 | -122.3373 | -122.3831 | 0 | 122.1542 | -0.027466 | 0.67291
3799.3906 | 122.4152 | -0.059509 | 122.2458 | -0.1432 | -0.043457 | 0.00066863 | 0.0208 | -0.0029821 | -0.011384 | -0.0064321 | 0.011322 | 0.0065923 | 0.062568 | 0.042569 | -0.01666 | 0.023563 | -0.0019483 | -0.13275 | -0.032043 | -0.022888 | -0.032043 | 0.068665 | -0.064087 | 0.022888 | 0.66834 | 122.1954 | -0.082397 | 122.081 | 0.11902 | 0.073242 | 0.1236 | 0.036621 | -122.2778 | -122.2778 | 0.12817 | 0.082397 | -0.004578 | 0.045776 | -0.041199 | -0.022888 | -0.050354 | -0.16479 | 0.17853 | 0.1831 | 0.13275 | 0.20599 | 0.15564 | 0.091553 | -0.009155 | 0.20142 | 122.1634 | -0.009155 | 122.2778 | 0.027466 | 122.2549 | -122.2687 | -122.3282 | 0.027466 | 122.1405 | -0.073242 | 0.72784
3801.1562 | 122.3557 | -0.11902 | 122.287 | -0.089798 | -0.041962 | 0.0025912 | 0.024859 | -0.0014867 | -0.012025 | -0.0023733 | -0.046661 | 0.0059515 | 0.065986 | 0.049191 | -0.016233 | 0.026981 | -0.0036573 | -0.14648 | 0.013733 | -0.068665 | -0.09613 | 0.009155 | -0.10529 | -0.018311 | 0.71869 | 122.2275 | -0.09613 | 122.0215 | 0.041199 | -0.018311 | 0.027466 | 0.050354 | -122.2733 | -122.3831 | 0.12817 | 0.10071 | 0.013733 | 0.050354 | -0.036621 | 0.022889 | -0.059509 | -0.2655 | 0.16022 | 0.14649 | 0.10071 | 0.1236 | 0.077819 | 0.07782 | -0.027465 | 0.13733 | 122.1176 | 0.082398 | 122.3236 | 0.13275 | 122.3465 | -122.3557 | -122.3831 | 0.022889 | 122.1405 | -0.027465 | 0.83771
3802.9219 | 122.3694 | -0.082397 | 122.287 | -0.16609 | -0.043244 | 0.0028048 | 0.023791 | 0.0032129 | -0.010743 | -0.0019461 | -0.1077 | 0.0061651 | 0.062995 | 0.055386 | -0.019224 | 0.027194 | -0.0042981 | -0.10986 | -0.032043 | -0.027466 | -0.036621 | 0.054932 | -0.064087 | 0.013733 | 0.70953 | 122.2458 | -0.07782 | 122.0673 | 0.086975 | 0 | 0.059509 | 0.054931 | -122.319 | -122.3236 | 0.13733 | 0.09613 | 0.01831 | 0.041199 | -0.036621 | 0.004577 | -0.041198 | -0.21973 | 0.16937 | 0.14191 | 0.082397 | 0.13733 | 0.07782 | 0.082398 | -0.009155 | 0.16479 | 122.1451 | -0.004577 | 122.3236 | 0.050354 | 122.3282 | -122.3145 | -122.3648 | 0.045776 | 122.1497 | -0.027466 | 0.79193
3804.6875 | 122.4197 | -0.068665 | 122.2321 | -0.2195 | -0.042816 | 0.001523 | 0.019946 | -0.0010595 | -0.011384 | -0.0028005 | -0.01004 | 0.0044561 | 0.06385 | 0.041928 | -0.017515 | 0.02634 | -0.0068615 | -0.10529 | -0.041199 | -0.004578 | -0.009155 | 0.10986 | -0.050354 | 0.059509 | 0.67749 | 122.1817 | -0.064087 | 122.0993 | 0.13733 | 0.07782 | 0.13275 | 0.064087 | -122.2733 | -122.2412 | 0.17853 | 0.12817 | 0.018311 | 0.064087 | -0.045776 | 0.004578 | -0.050354 | -0.13275 | 0.20599 | 0.20142 | 0.14649 | 0.19684 | 0.14191 | 0.11444 | -0.004577 | 0.20142 | 122.1634 | -0.036621 | 122.2458 | 0.027466 | 122.2504 | -122.2366 | -122.2961 | 0.05951 | 122.168 | -0.036621 | 0.74616
3806.4531 | 122.4701 | -0.045776 | 122.2275 | -0.2195 | -0.041321 | 0.002164 | 0.023364 | 0.00086307 | -0.008607 | -0.0032277 | -0.037506 | 0.0055243 | 0.062141 | 0.044705 | -0.020719 | 0.027621 | -0.0055799 | -0.059509 | -0.059509 | -0.013733 | 0.013733 | 0.14648 | -0.027466 | 0.07782 | 0.72327 | 122.1771 | -0.082397 | 122.1588 | 0.1831 | 0.11902 | 0.16937 | 0.032043 | -122.287 | -122.2137 | 0.19226 | 0.1236 | 0.01831 | 0.091553 | -0.013733 | -0.036621 | -0.050354 | -0.068665 | 0.22888 | 0.21515 | 0.16479 | 0.25177 | 0.20142 | 0.16022 | 0.027466 | 0.2655 | 122.2412 | -0.045776 | 122.2595 | -0.013733 | 122.2229 | -122.2412 | -122.3099 | 0.059509 | 122.2046 | -0.013733 | 0.76904
3808.2188 | 122.438 | -0.068665 | 122.2549 | -0.22713 | -0.04303 | 0.00088223 | 0.021441 | 0.0010767 | -0.01053 | -0.0045095 | -0.022247 | 0.0050971 | 0.063423 | 0.045346 | -0.01666 | 0.027621 | -0.0045117 | -0.09613 | -0.036621 | -0.032043 | -0.013733 | 0.10071 | -0.041199 | 0.059509 | 0.68665 | 122.1954 | -0.073242 | 122.1176 | 0.1236 | 0.068665 | 0.11444 | 0.036622 | -122.2916 | -122.2687 | 0.16937 | 0.12817 | 0.027466 | 0.091552 | -0.009156 | -0.004577 | -0.059509 | -0.13733 | 0.19226 | 0.18311 | 0.13733 | 0.18768 | 0.14191 | 0.13275 | 0.01831 | 0.19684 | 122.1909 | -0.004578 | 122.2687 | 0.032044 | 122.2641 | -122.287 | -122.3282 | 0.054932 | 122.1863 | -0.027465 | 0.75531
3809.9219 | 122.3602 | -0.086975 | 122.3053 | -0.074539 | -0.043457 | 0.0017368 | 0.024005 | -0.0021277 | -0.010957 | -0.0040823 | -0.089386 | 0.0059515 | 0.06385 | 0.051541 | -0.016874 | 0.025912 | -0.0053661 | -0.13733 | -0.018311 | -0.050354 | -0.09613 | -0.013733 | -0.10986 | -0.018311 | 0.72327 | 122.2412 | -0.11444 | 122.0398 | 0.059509 | -0.018311 | 0.045776 | 0.036621 | -122.3236 | -122.4014 | 0.073242 | 0.068664 | -0.022888 | 0.032043 | -0.059509 | -0.027466 | -0.064087 | -0.2655 | 0.14648 | 0.13275 | 0.068664 | 0.16022 | 0.09613 | 0.036621 | -0.045776 | 0.17395 | 122.1542 | 0.032043 | 122.3557 | 0.068664 | 122.3282 | -122.3557 | -122.4197 | -0.009155 | 122.1268 | -0.050354 | 0.81024
3811.6875 | 122.4289 | -0.059509 | 122.2229 | -0.2195 | -0.041535 | 0.0023776 | 0.022296 | -0.00063233 | -0.01053 | -0.0028005 | 0.014374 | 0.0059515 | 0.0615 | 0.041714 | -0.01901 | 0.025912 | -0.0036573 | -0.11902 | -0.022888 | -0.022888 | -0.032043 | 0.073242 | -0.064087 | 0.045776 | 0.71411 | 122.2092 | -0.073242 | 122.1039 | 0.14648 | 0.091553 | 0.1236 | 0.036621 | -122.2458 | -122.2549 | 0.13275 | 0.10528 | -0.004578 | 0.068664 | -0.041199 | -0.013733 | -0.013733 | -0.11902 | 0.20599 | 0.1831 | 0.15106 | 0.19684 | 0.16479 | 0.09613 | -0.009155 | 0.21973 | 122.1771 | 0 | 122.2824 | 0.036621 | 122.2687 | -122.2458 | -122.2961 | 0.027466 | 122.1634 | -0.05951 | 0.77362
3813.4531 | 122.4701 | -0.059509 | 122.2321 | -0.15083 | -0.041321 | 0.0025912 | 0.022723 | 0.0010767 | -0.0094614 | -0.0038687 | 0.0021667 | 0.0057379 | 0.064063 | 0.044705 | -0.019438 | 0.025485 | -0.0072889 | -0.10529 | -0.036621 | -0.018311 | -0.022888 | 0.082397 | -0.050354 | 0.068665 | 0.74616 | 122.1771 | -0.082397 | 122.1222 | 0.16022 | 0.13275 | 0.15106 | 0.041198 | -122.2687 | -122.2549 | 0.14191 | 0.12817 | 0.009155 | 0.086976 | -0.032043 | -0.022888 | -0.054932 | -0.10986 | 0.21973 | 0.21057 | 0.19226 | 0.23346 | 0.21515 | 0.10071 | -0.004577 | 0.24261 | 122.2046 | -0.01831 | 122.2595 | 0.022888 | 122.2366 | -122.2504 | -122.3145 | 0.036621 | 122.1817 | -0.045777 | 0.80566
3815.1562 | 122.3648 | -0.073242 | 122.2961 | -0.12794 | -0.041321 | 0.0034456 | 0.026141 | -0.0040503 | -0.0094614 | -0.0049367 | -0.13211 | 0.0055243 | 0.062995 | 0.053036 | -0.019651 | 0.028903 | -0.0060071 | -0.082397 | -0.013733 | -0.050354 | -0.027466 | 0.059509 | -0.068665 | 0.013733 | 0.74158 | 122.2412 | -0.091553 | 122.0901 | 0.082397 | 0 | 0.07782 | 0.022888 | -122.3099 | -122.3236 | 0.13275 | 0.086975 | 0.004577 | 0.064087 | -0.018311 | -0.018311 | -0.054932 | -0.20599 | 0.15564 | 0.15106 | 0.073242 | 0.16937 | 0.091553 | 0.10986 | 0.022888 | 0.17395 | 122.1817 | 0.036621 | 122.3328 | 0.059509 | 122.3145 | -122.3465 | -122.3877 | 0.045776 | 122.1634 | -0.009155 | 0.81482
3816.9219 | 122.4838 | -0.064087 | 122.2321 | -0.13557 | -0.043885 | 0.00088223 | 0.022082 | -0.0021277 | -0.012879 | -0.0034415 | 0.0052185 | 0.0068059 | 0.062995 | 0.040219 | -0.01901 | 0.025912 | -0.0028027 | -0.073242 | -0.045776 | -0.018311 | 0.050354 | 0.16479 | 0.018311 | 0.11902 | 0.89264 | 122.1954 | -0.054932 | 122.1771 | 0.20142 | 0.14648 | 0.16479 | 0.045776 | -122.2778 | -122.1817 | 0.22888 | 0.18311 | 0.082398 | 0.13733 | 0.036622 | 0.009155 | -0.036621 | -0.054932 | 0.2655 | 0.22888 | 0.21057 | 0.21973 | 0.20142 | 0.18311 | 0.068665 | 0.25635 | 122.2321 | -0.027465 | 122.2504 | 0.018311 | 122.2595 | -122.2504 | -122.287 | 0.11444 | 122.2412 | -0.009155 | 0.95673
3818.6875 | 122.3648 | -0.091553 | 122.287 | -0.097427 | -0.044525 | -0.00018577 | 0.022082 | 0.0017175 | -0.011384 | -0.0038687 | -0.083283 | 0.0059515 | 0.064918 | 0.052609 | -0.019651 | 0.027194 | -0.0092115 | -0.14648 | -0.004578 | -0.07782 | -0.091553 | -0.013733 | -0.10529 | 0 | 0.72327 | 122.2092 | -0.10529 | 122.0535 | 0.073242 | 0 | 0.045776 | 0.013733 | -122.2916 | -122.3785 | 0.07782 | 0.091553 | -0.013733 | 0.07782 | -0.027466 | -0.013733 | -0.07782 | -0.23346 | 0.16479 | 0.13733 | 0.091553 | 0.15106 | 0.10529 | 0.064087 | -0.013733 | 0.17853 | 122.1588 | 0.073242 | 122.3145 | 0.086975 | 122.3007 | -122.3648 | -122.3923 | 0 | 122.1451 | -0.054931 | 0.81482
3820.3906 | 122.3511 | -0.10071 | 122.2916 | -0.16609 | -0.040467 | -0.00061317 | 0.0255 | -0.0044775 | -0.0081796 | -0.0028005 | -0.1138 | 0.0059515 | 0.064277 | 0.046628 | -0.019224 | 0.026981 | -0.0025891 | -0.1236 | -0.009155 | -0.064087 | -0.10071 | -0.032043 | -0.16937 | -0.050354 | 0.57678 | 122.2641 | -0.11902 | 122.0352 | 0.045776 | -0.041199 | 0.045776 | 0.036621 | -122.3007 | -122.3923 | 0.068665 | 0.050354 | -0.068665 | 0.013733 | -0.10529 | -0.018311 | -0.027466 | -0.25635 | 0.14648 | 0.14648 | 0.059509 | 0.16479 | 0.07782 | 0.032044 | -0.036621 | 0.16479 | 122.1542 | 0.054932 | 122.3831 | 0.091553 | 122.3648 | -122.3557 | -122.4106 | 0 | 122.1359 | -0.022888 | 0.67749
3822.1719 | 122.3328 | -0.082397 | 122.2733 | -0.20424 | -0.042176 | 0.00066863 | 0.022723 | -0.0038367 | -0.010743 | -0.0034415 | -0.04361 | 0.0076605 | 0.06385 | 0.044064 | -0.01901 | 0.025058 | -0.0042981 | -0.10071 | -0.009155 | -0.032043 | -0.059509 | 0.027466 | -0.054932 | 0.004578 | 0.77362 | 122.2321 | -0.09613 | 122.0444 | 0.07782 | 0.004578 | 0.022888 | 0.050354 | -122.2824 | -122.3328 | 0.10986 | 0.086975 | 0.027465 | 0.036621 | -0.022889 | -0.013733 | -0.041198 | -0.22888 | 0.16022 | 0.10528 | 0.086975 | 0.11902 | 0.10071 | 0.059509 | -0.027466 | 0.17395 | 122.1405 | 0.022888 | 122.3282 | 0.073242 | 122.3145 | -122.3053 | -122.3694 | 0.022888 | 122.1268 | -0.018311 | 0.85602
3823.9375 | 122.3923 | -0.091553 | 122.2641 | -0.10506 | -0.043885 | 0.0010958 | 0.023364 | -0.0029821 | -0.010957 | -0.0028005 | -0.089386 | 0.0068059 | 0.063209 | 0.047055 | -0.017088 | 0.026553 | -0.0051525 | -0.1236 | -0.009155 | -0.059509 | -0.068665 | -0.013733 | -0.10071 | -0.009155 | 0.73242 | 122.2504 | -0.10986 | 122.0856 | 0.091553 | 0 | 0.059509 | 0.032044 | -122.2733 | -122.3328 | 0.07782 | 0.082398 | -0.009155 | 0.050354 | -0.041199 | -0.01831 | -0.013733 | -0.17853 | 0.18311 | 0.15106 | 0.091553 | 0.16937 | 0.10986 | 0.045776 | -0.009156 | 0.20142 | 122.1954 | 0.050354 | 122.3602 | 0.082398 | 122.3419 | -122.3236 | -122.374 | 0.022888 | 122.1771 | -0.032043 | 0.82398
3825.7031 | 122.3557 | -0.10529 | 122.2687 | -0.13557 | -0.045166 | 0.0030184 | 0.021655 | -0.0064001 | -0.012452 | -0.0060049 | -0.040558 | 0.0055243 | 0.063423 | 0.045559 | -0.017729 | 0.028049 | -0.0036573 | -0.14191 | 0 | -0.045776 | -0.086975 | 0.018311 | -0.10071 | -0.013733 | 0.76904 | 122.2321 | -0.11444 | 122.0306 | 0.064087 | 0.004578 | 0.018311 | 0.05951 | -122.2687 | -122.3557 | 0.1236 | 0.091553 | 0.004578 | 0.032043 | -0.054932 | -0.009155 | -0.036621 | -0.23804 | 0.16937 | 0.1236 | 0.10986 | 0.13275 | 0.11902 | 0.064087 | -0.041199 | 0.17853 | 122.1451 | 0.045776 | 122.3465 | 0.10529 | 122.3373 | -122.3145 | -122.3831 | 0.018311 | 122.1359 | -0.036621 | 0.87433
3827.4219 | 122.4106 | -0.07782 | 122.2916 | -0.13557 | -0.043457 | 0.0019504 | 0.021655 | 0.0015039 | -0.012452 | -0.0036551 | -0.028351 | 0.0057379 | 0.063423 | 0.042355 | -0.017301 | 0.025912 | -0.0045117 | -0.073242 | -0.045776 | -0.022888 | 0.018311 | 0.11902 | 0 | 0.07782 | 0.83313 | 122.2458 | -0.045776 | 122.0993 | 0.14648 | 0.082397 | 0.091553 | 0.054932 | -122.3373 | -122.2733 | 0.19684 | 0.15564 | 0.07782 | 0.10071 | 0.022888 | 0.032044 | -0.045776 | -0.19226 | 0.2243 | 0.16937 | 0.16022 | 0.13733 | 0.12817 | 0.14191 | 0.041199 | 0.19226 | 122.1451 | -0.022888 | 122.2916 | 0.032044 | 122.3236 | -122.3145 | -122.3373 | 0.096131 | 122.1771 | 0.004578 | 0.91095
3829.1875 | 122.3831 | -0.086975 | 122.2778 | -0.13557 | -0.042603 | 0.0023776 | 0.025073 | -0.0019141 | -0.010316 | -0.0053641 | -0.092438 | 0.0063787 | 0.064277 | 0.057736 | -0.018797 | 0.02869 | -0.0045117 | -0.091553 | -0.013733 | -0.054932 | -0.022888 | 0.059509 | -0.07782 | 0.022888 | 0.78278 | 122.2229 | -0.086975 | 122.081 | 0.10071 | 0.041199 | 0.086975 | 0.032043 | -122.2916 | -122.3007 | 0.14648 | 0.10986 | 0.009155 | 0.07782 | -0.022888 | 0 | -0.054932 | -0.19684 | 0.18768 | 0.17395 | 0.12817 | 0.17395 | 0.12817 | 0.11444 | 0.032044 | 0.18768 | 122.168 | 0.041199 | 122.3099 | 0.073242 | 122.3099 | -122.3328 | -122.3648 | 0.064087 | 122.168 | -0.004578 | 0.86975
3830.9531 | 122.3969 | -0.082397 | 122.2733 | -0.15083 | -0.043244 | -0.0010404 | 0.024218 | 0.00022207 | -0.010316 | -0.0023733 | -0.09549 | 0.0068059 | 0.062568 | 0.054104 | -0.018797 | 0.028262 | -0.0081433 | -0.091553 | -0.013733 | -0.050354 | -0.036621 | 0.054932 | -0.07782 | 0.009155 | 0.78278 | 122.2458 | -0.091553 | 122.0947 | 0.11902 | 0.041199 | 0.091553 | 0.032043 | -122.287 | -122.3099 | 0.13733 | 0.091552 | 0.004577 | 0.059509 | -0.027466 | -0.009156 | -0.027465 | -0.17853 | 0.20142 | 0.17395 | 0.1236 | 0.18311 | 0.13275 | 0.10529 | 0.013733 | 0.21057 | 122.1863 | 0.036621 | 122.3373 | 0.068664 | 122.3282 | -122.3236 | -122.3648 | 0.045776 | 122.1771 | -0.009156 | 0.86517
3832.7344 | 122.4197 | -0.059509 | 122.2549 | -0.17372 | -0.043244 | 0.002164 | 0.022509 | -0.0019141 | -0.008607 | -0.0032277 | -0.013092 | 0.0048833 | 0.065132 | 0.048764 | -0.017729 | 0.029117 | -0.0023755 | -0.11902 | -0.032043 | -0.027466 | -0.018311 | 0.07782 | -0.054932 | 0.041199 | 0.68665 | 122.1863 | -0.09613 | 122.1222 | 0.1236 | 0.073242 | 0.10986 | 0.032043 | -122.287 | -122.2733 | 0.13733 | 0.10071 | 0.004577 | 0.068665 | -0.027466 | -0.036621 | -0.068665 | -0.13275 | 0.1831 | 0.16937 | 0.13275 | 0.20599 | 0.16937 | 0.10529 | 0.009155 | 0.21973 | 122.2183 | -0.004577 | 122.2824 | 0.027466 | 122.2458 | -122.2824 | -122.3511 | 0.041198 | 122.1817 | -0.05951 | 0.74616
3834.5 | 122.3511 | -0.10071 | 122.2733 | -0.089798 | -0.044525 | 0.0019504 | 0.021228 | -0.0012731 | -0.012879 | -0.0047231 | -0.028351 | 0.0074469 | 0.063636 | 0.041928 | -0.018156 | 0.027194 | -0.0049389 | -0.11444 | -0.018311 | -0.032043 | -0.064087 | 0.064087 | -0.073242 | 0.013733 | 0.76446 | 122.2366 | -0.09613 | 122.0398 | 0.073242 | 0.004578 | 0.041199 | 0.068665 | -122.2916 | -122.3373 | 0.1648 | 0.11444 | 0.027466 | 0.045776 | -0.041199 | 0.004578 | -0.036621 | -0.23346 | 0.17395 | 0.14191 | 0.10529 | 0.13733 | 0.10071 | 0.09613 | -0.032044 | 0.16937 | 122.1359 | 0.013732 | 122.3328 | 0.082397 | 122.3373 | -122.3053 | -122.3694 | 0.036621 | 122.1405 | -0.013733 | 0.86517
3836.2656 | 122.3328 | -0.082397 | 122.2641 | -0.13557 | -0.043885 | 0.0023776 | 0.022509 | 0.0010767 | -0.0092478 | -0.0055777 | -0.14737 | 0.0072333 | 0.063209 | 0.050686 | -0.018369 | 0.028903 | -0.00088011 | -0.10529 | -0.013733 | -0.036621 | -0.050354 | 0.032043 | -0.11902 | -0.013733 | 0.67749 | 122.2458 | -0.086975 | 122.0673 | 0.045776 | -0.027466 | 0.045776 | 0.045776 | -122.2778 | -122.3145 | 0.11444 | 0.068664 | -0.036622 | 0.022888 | -0.082398 | -0.004578 | -0.01831 | -0.19684 | 0.12817 | 0.12817 | 0.054931 | 0.13275 | 0.059509 | 0.068664 | -0.013733 | 0.13275 | 122.1542 | 0.022888 | 122.3328 | 0.068664 | 122.3282 | -122.3007 | -122.3511 | 0.032043 | 122.1497 | -0.022889 | 0.75989
3838.0312 | 122.5021 | -0.054932 | 122.2595 | -0.17372 | -0.04303 | 0.0010958 | 0.020587 | -0.0010595 | -0.010102 | -0.0042959 | 0.0082703 | 0.0033881 | 0.062568 | 0.044705 | -0.017088 | 0.028476 | -0.0051525 | -0.091553 | -0.050354 | 0 | 0.032043 | 0.15564 | 0.009155 | 0.12817 | 0.87891 | 122.1725 | -0.073242 | 122.1771 | 0.23346 | 0.16479 | 0.1831 | 0.054932 | -122.3099 | -122.2275 | 0.21057 | 0.18311 | 0.064087 | 0.12817 | 0.009155 | -0.01831 | -0.086975 | -0.082397 | 0.28839 | 0.23804 | 0.21973 | 0.25635 | 0.23804 | 0.15564 | 0.032043 | 0.3067 | 122.2504 | -0.050354 | 122.2458 | 0.004578 | 122.2275 | -122.2595 | -122.3328 | 0.086975 | 122.2321 | -0.036621 | 0.93384
3839.7344 | 122.4747 | -0.045776 | 122.2412 | -0.18898 | -0.039398 | 0.0023776 | 0.021014 | 0.0047083 | -0.011384 | -0.0049367 | -0.046661 | 0.0074469 | 0.064063 | 0.047909 | -0.019438 | 0.025485 | -0.0068615 | -0.041199 | -0.041199 | -0.013733 | 0.032043 | 0.11444 | -0.036621 | 0.082397 | 0.72784 | 122.1863 | -0.050354 | 122.1725 | 0.17395 | 0.10071 | 0.17395 | 0.032043 | -122.2824 | -122.2092 | 0.16022 | 0.12817 | 0.009155 | 0.09613 | -0.022888 | -0.004578 | -0.054932 | -0.068665 | 0.21973 | 0.21973 | 0.14648 | 0.2243 | 0.15106 | 0.12817 | 0.045776 | 0.2243 | 122.2229 | -0.027466 | 122.2366 | 0.004577 | 122.2321 | -122.2549 | -122.2916 | 0.077819 | 122.2183 | 0.004577 | 0.77362
3841.4844 | 122.4243 | -0.068665 | 122.2458 | -0.16609 | -0.042816 | 0.0036594 | 0.021228 | 0.0010767 | -0.009675 | -0.0053641 | -0.022247 | 0.0042425 | 0.061927 | 0.043637 | -0.015806 | 0.025272 | -0.0060071 | -0.11902 | -0.032043 | -0.009155 | -0.041199 | 0.068665 | -0.064087 | 0.036621 | 0.70496 | 122.1863 | -0.082397 | 122.0947 | 0.11444 | 0.073242 | 0.10529 | 0.05951 | -122.2778 | -122.287 | 0.13733 | 0.10529 | 0.004578 | 0.045776 | -0.054932 | -0.013732 | -0.05951 | -0.15106 | 0.18311 | 0.17395 | 0.14191 | 0.18768 | 0.15564 | 0.07782 | -0.032044 | 0.19684 | 122.1771 | -0.022888 | 122.2687 | 0.036622 | 122.2549 | -122.2549 | -122.3282 | 0.027466 | 122.1634 | -0.050354 | 0.77362
3843.25 | 122.4335 | -0.064087 | 122.2275 | -0.15846 | -0.042816 | 0.0040866 | 0.021869 | 0.00064947 | -0.010743 | -0.0042959 | -0.071076 | 0.0061651 | 0.062995 | 0.0462 | -0.018156 | 0.024631 | -0.0036573 | -0.082397 | -0.050354 | 0.018311 | 0.027466 | 0.13275 | -0.027466 | 0.073242 | 0.75989 | 122.1725 | -0.050354 | 122.1405 | 0.16479 | 0.091553 | 0.14191 | 0.082398 | -122.2778 | -122.2 | 0.19684 | 0.13733 | 0.036621 | 0.054931 | -0.045777 | 0.013733 | -0.054932 | -0.086975 | 0.22888 | 0.20599 | 0.15564 | 0.19226 | 0.14191 | 0.11444 | 0.009155 | 0.21515 | 122.1909 | -0.068665 | 122.2229 | 0.013733 | 122.2366 | -122.2092 | -122.2778 | 0.091553 | 122.2046 | -0.01831 | 0.82398
3845.0156 | 122.3923 | -0.07782 | 122.2687 | -0.13557 | -0.044098 | 0.00066863 | 0.022509 | 0.00064947 | -0.011384 | -0.0023733 | -0.09549 | 0.0072333 | 0.062568 | 0.04855 | -0.01666 | 0.025912 | -0.0066479 | -0.10529 | -0.013733 | -0.059509 | -0.082397 | 0.013733 | -0.086975 | -0.013733 | 0.76446 | 122.2641 | -0.09613 | 122.0901 | 0.10986 | 0.018311 | 0.07782 | 0.018311 | -122.2824 | -122.3511 | 0.091553 | 0.064087 | -0.009155 | 0.045776 | -0.027466 | -0.01831 | -0.004578 | -0.17853 | 0.18768 | 0.15564 | 0.096131 | 0.17395 | 0.11444 | 0.073242 | -0.022888 | 0.20599 | 122.1863 | 0.045776 | 122.3602 | 0.064087 | 122.3419 | -122.3282 | -122.3648 | -0.004577 | 122.168 | -0.027466 | 0.84228
3846.7188 | 122.3877 | -0.091553 | 122.2824 | -0.11269 | -0.041535 | 0.0019504 | 0.025073 | -0.00084593 | -0.010102 | -0.0034415 | -0.09549 | 0.0050971 | 0.061286 | 0.050473 | -0.017942 | 0.027408 | -0.0049389 | -0.10529 | -0.004578 | -0.045776 | -0.041199 | 0.036621 | -0.082397 | 0.018311 | 0.79193 | 122.2321 | -0.086975 | 122.0947 | 0.10529 | 0.027466 | 0.068665 | 0.045777 | -122.287 | -122.3236 | 0.12817 | 0.10986 | 0.009156 | 0.064087 | -0.036621 | 0.004578 | -0.050354 | -0.18768 | 0.19684 | 0.16022 | 0.11902 | 0.15564 | 0.11444 | 0.082397 | 0.004577 | 0.19226 | 122.1817 | 0.041198 | 122.319 | 0.086975 | 122.3236 | -122.3282 | -122.3694 | 0.050354 | 122.1863 | -0.013733 | 0.88348
3848.4844 | 122.4472 | -0.059509 | 122.2778 | -0.097427 | -0.043671 | 0.0023776 | 0.020373 | -0.0031957 | -0.012025 | -0.0045095 | 0.0052185 | 0.0040289 | 0.062141 | 0.04385 | -0.017088 | 0.02634 | -0.0066479 | -0.11444 | -0.041199 | -0.045776 | -0.036621 | 0.07782 | -0.041199 | 0.050354 | 0.75989 | 122.2092 | -0.091553 | 122.1222 | 0.15564 | 0.086975 | 0.13275 | 0.013733 | -122.319 | -122.3145 | 0.13733 | 0.10986 | 0.01831 | 0.09613 | 0.004577 | -0.032044 | -0.068665 | -0.15564 | 0.21515 | 0.19226 | 0.14648 | 0.2243 | 0.17853 | 0.1236 | 0.009155 | 0.24719 | 122.2137 | 0.004577 | 122.3007 | 0.01831 | 122.2687 | -122.3236 | -122.3694 | 0.022888 | 122.1817 | -0.054932 | 0.8194
3850.1719 | 122.3602 | -0.10071 | 122.2916 | -0.15083 | -0.044525 | 0.0017368 | 0.022937 | 0.00064947 | -0.012452 | -0.0049367 | -0.031403 | 0.0074469 | 0.065132 | 0.042142 | -0.018583 | 0.025058 | -0.0062207 | -0.13733 | 0.004578 | -0.045776 | -0.09613 | 0.013733 | -0.10986 | 0 | 0.75531 | 122.2229 | -0.09613 | 122.0215 | 0.054932 | -0.022888 | 0.022888 | 0.054932 | -122.287 | -122.3877 | 0.11444 | 0.10071 | -0.009155 | 0.045776 | -0.064087 | 0.004578 | -0.068665 | -0.27008 | 0.15564 | 0.1236 | 0.07782 | 0.11902 | 0.073242 | 0.059509 | -0.050354 | 0.15106 | 122.1176 | 0.050354 | 122.319 | 0.10529 | 122.3236 | -122.3373 | -122.3877 | 0.004578 | 122.1222 | -0.036621 | 0.85602
3851.9375 | 122.3923 | -0.091553 | 122.2916 | -0.13557 | -0.041748 | 0.0028048 | 0.024218 | 0.0017175 | -0.010102 | -0.0047231 | -0.1077 | 0.0057379 | 0.064277 | 0.056241 | -0.017729 | 0.025272 | -0.0085705 | -0.086975 | -0.022888 | -0.041199 | -0.041199 | 0.036621 | -0.073242 | -0.004578 | 0.79651 | 122.2366 | -0.07782 | 122.0947 | 0.10529 | 0.022888 | 0.086975 | 0.050354 | -122.3145 | -122.3328 | 0.12817 | 0.086975 | 0.018311 | 0.036621 | -0.032043 | 0.013733 | -0.054932 | -0.19684 | 0.19684 | 0.17853 | 0.11444 | 0.16479 | 0.10071 | 0.07782 | 0 | 0.18311 | 122.1725 | 0.018311 | 122.3145 | 0.068665 | 122.3282 | -122.3328 | -122.3694 | 0.050354 | 122.1863 | 0.004578 | 0.88806
3853.7031 | 122.438 | -0.068665 | 122.2824 | -0.22713 | -0.044525 | 0.0017368 | 0.02016 | -0.0014867 | -0.012666 | -0.0049367 | -0.037506 | 0.0057379 | 0.064918 | 0.044491 | -0.015806 | 0.026553 | -0.0064343 | -0.09613 | -0.041199 | -0.013733 | -0.022888 | 0.10529 | -0.054932 | 0.064087 | 0.70953 | 122.2092 | -0.064087 | 122.1176 | 0.12817 | 0.073242 | 0.10986 | 0.054932 | -122.3236 | -122.3053 | 0.17395 | 0.13275 | 0.013733 | 0.07782 | -0.041199 | 0.004578 | -0.073243 | -0.16479 | 0.19684 | 0.17853 | 0.14191 | 0.17395 | 0.13733 | 0.11902 | -0.009155 | 0.19226 | 122.1817 | -0.027466 | 122.2733 | 0.027466 | 122.2778 | -122.2961 | -122.3465 | 0.045777 | 122.1863 | -0.027465 | 0.7782
3855.4531 | 122.3923 | -0.09613 | 122.2687 | -0.1432 | -0.045594 | 0.0023776 | 0.02016 | -0.00020513 | -0.010743 | -0.0015189 | -0.046661 | 0.0061651 | 0.062354 | 0.042782 | -0.018369 | 0.025912 | -0.0096387 | -0.068665 | -0.036621 | -0.018311 | 0 | 0.10986 | -0.009155 | 0.068665 | 0.85602 | 122.2183 | -0.073242 | 122.081 | 0.11902 | 0.068665 | 0.082397 | 0.077819 | -122.3053 | -122.2687 | 0.20599 | 0.16479 | 0.086975 | 0.086976 | 0.009156 | 0.022888 | -0.050354 | -0.18768 | 0.21515 | 0.17853 | 0.16479 | 0.15564 | 0.14191 | 0.12817 | 0.018311 | 0.19226 | 122.1542 | -0.01831 | 122.2916 | 0.059509 | 122.3145 | -122.287 | -122.3419 | 0.09613 | 122.1771 | 0.027465 | 0.95215
3857.1719 | 122.3831 | -0.086975 | 122.2824 | -0.12032 | -0.043244 | 0.0013094 | 0.024005 | 0.0032129 | -0.0092478 | -0.0032277 | -0.10464 | 0.0063787 | 0.064063 | 0.053464 | -0.01666 | 0.026767 | -0.0057935 | -0.086975 | -0.004578 | -0.050354 | -0.041199 | 0.032043 | -0.064087 | 0.004578 | 0.80109 | 122.2595 | -0.091553 | 122.0901 | 0.11444 | 0.022888 | 0.086975 | 0.036621 | -122.287 | -122.3236 | 0.11902 | 0.091553 | 0.022888 | 0.054932 | -0.013733 | -0.004578 | -0.022889 | -0.19226 | 0.20142 | 0.17395 | 0.10986 | 0.17853 | 0.11444 | 0.082397 | 0.009155 | 0.20599 | 122.1817 | 0.045776 | 122.3511 | 0.082397 | 122.3465 | -122.3328 | -122.374 | 0.045776 | 122.1771 | 0 | 0.88806
3858.9375 | 122.4289 | -0.064087 | 122.2366 | -0.10506 | -0.046234 | 0.0025912 | 0.019091 | -0.00084593 | -0.011811 | -0.0057913 | -0.022247 | 0.0061651 | 0.063636 | 0.047055 | -0.016233 | 0.026767 | -0.0049389 | -0.13275 | -0.036621 | -0.018311 | -0.027466 | 0.073242 | -0.068665 | 0.045776 | 0.71411 | 122.2137 | -0.091553 | 122.1039 | 0.11444 | 0.059509 | 0.09613 | 0.045776 | -122.2733 | -122.2641 | 0.13733 | 0.10986 | -0.004578 | 0.064087 | -0.050354 | -0.027466 | -0.022888 | -0.13275 | 0.17853 | 0.16022 | 0.1236 | 0.18768 | 0.15106 | 0.091553 | -0.009155 | 0.20599 | 122.1954 | -0.01831 | 122.3053 | 0.027466 | 122.2778 | -122.2549 | -122.3282 | 0.036621 | 122.168 | -0.068664 | 0.7782
3860.6875 | 122.4518 | -0.054932 | 122.2549 | -0.18898 | -0.04303 | -0.00018577 | 0.022509 | -0.0012731 | -0.009675 | -0.0072867 | -0.0069885 | 0.0055243 | 0.065132 | 0.040646 | -0.018583 | 0.025485 | -0.0036573 | -0.10529 | -0.018311 | -0.022888 | -0.009155 | 0.086975 | -0.027466 | 0.068665 | 0.7782 | 122.1909 | -0.082397 | 122.1359 | 0.16937 | 0.11444 | 0.14648 | 0.032044 | -122.2733 | -122.2641 | 0.14191 | 0.1236 | 0.027466 | 0.091553 | -0.004578 | -0.027465 | -0.064087 | -0.11902 | 0.22431 | 0.20142 | 0.16937 | 0.22888 | 0.19684 | 0.10986 | 0.013733 | 0.25177 | 122.2183 | 0.004577 | 122.2733 | 0.036621 | 122.2458 | -122.2778 | -122.3373 | 0.045777 | 122.1909 | -0.050354 | 0.83313
3862.3906 | 122.3511 | -0.11444 | 122.2778 | -0.15846 | -0.044098 | 0.00066863 | 0.022723 | -0.0044775 | -0.012452 | -0.0053641 | -0.064972 | 0.0076605 | 0.064704 | 0.050686 | -0.017729 | 0.024844 | -0.01092 | -0.13733 | -0.004578 | -0.050354 | -0.082397 | 0.013733 | -0.10529 | -0.013733 | 0.76446 | 122.2458 | -0.11444 | 122.0215 | 0.045776 | -0.013733 | 0.013733 | 0.064087 | -122.2824 | -122.3602 | 0.12817 | 0.10071 | 0.009155 | 0.036621 | -0.054932 | 0 | -0.032043 | -0.25635 | 0.16022 | 0.12817 | 0.10071 | 0.12817 | 0.10071 | 0.064087 | -0.032043 | 0.16022 | 122.1359 | 0.045776 | 122.3602 | 0.10986 | 122.3602 | -122.3282 | -122.3923 | 0.032044 | 122.1359 | -0.022888 | 0.87891
3864.1562 | 122.319 | -0.11902 | 122.2641 | -0.15846 | -0.039826 | 0.0047274 | 0.024005 | -0.00041873 | -0.0094614 | -0.0019461 | -0.12296 | 0.0076605 | 0.063636 | 0.052182 | -0.017729 | 0.027835 | -0.0053661 | -0.13275 | -0.013733 | -0.073242 | -0.09613 | -0.059509 | -0.18768 | -0.054932 | 0.60883 | 122.2366 | -0.1236 | 122.0306 | 0.027466 | -0.064087 | 0.050354 | 0.045777 | -122.2778 | -122.3602 | 0.05951 | 0.064087 | -0.068664 | 0.01831 | -0.11444 | -0.004577 | -0.027466 | -0.23346 | 0.14649 | 0.16937 | 0.054932 | 0.17395 | 0.059509 | 0.013733 | -0.022888 | 0.15106 | 122.1542 | 0.059509 | 122.3602 | 0.10529 | 122.3557 | -122.3373 | -122.3877 | 0.022889 | 122.1497 | -0.013732 | 0.72784
3865.8594 | 122.4197 | -0.068665 | 122.2549 | -0.15846 | -0.044525 | 0.0017368 | 0.021869 | 0.0027857 | -0.011384 | -0.0025869 | -0.034454 | 0.0059515 | 0.063209 | 0.044919 | -0.016447 | 0.026981 | -0.0070751 | -0.10529 | -0.018311 | -0.036621 | -0.027466 | 0.064087 | -0.064087 | 0.036621 | 0.74158 | 122.1817 | -0.09613 | 122.1085 | 0.13275 | 0.073242 | 0.11444 | 0.032044 | -122.2733 | -122.2824 | 0.13275 | 0.10529 | 0.004578 | 0.073242 | -0.027466 | -0.027465 | -0.073242 | -0.14648 | 0.20142 | 0.18311 | 0.14191 | 0.21057 | 0.16937 | 0.10071 | 0.009155 | 0.22888 | 122.2046 | 0.01831 | 122.2778 | 0.050354 | 122.2504 | -122.2916 | -122.3511 | 0.041199 | 122.1771 | -0.036621 | 0.81024
3867.6406 | 122.4518 | -0.064087 | 122.2412 | -0.15846 | -0.040039 | 0.0036594 | 0.023578 | 0.0021447 | -0.0092478 | -0.0055777 | -0.098541 | 0.0059515 | 0.063209 | 0.042569 | -0.016874 | 0.027835 | -0.0092115 | -0.1236 | -0.004578 | -0.022888 | -0.027466 | 0.050354 | -0.10986 | 0.009155 | 0.72784 | 122.2046 | -0.07782 | 122.1451 | 0.14648 | 0.086975 | 0.16479 | 0.041199 | -122.2458 | -122.2687 | 0.11444 | 0.073242 | -0.045776 | 0.032043 | -0.086975 | -0.013733 | -0.036621 | -0.09613 | 0.21057 | 0.22888 | 0.15106 | 0.24261 | 0.16479 | 0.073242 | -0.004578 | 0.2243 | 122.2229 | 0.01831 | 122.2824 | 0.059509 | 122.2687 | -122.2641 | -122.319 | 0.036621 | 122.2092 | -0.059509 | 0.79193
3869.4219 | 122.3465 | -0.10529 | 122.2687 | -0.12032 | -0.042176 | 0.0017368 | 0.025714 | 0.00064947 | -0.0094614 | -0.0053641 | -0.13211 | 0.0070197 | 0.064063 | 0.044278 | -0.016874 | 0.027621 | -0.0013073 | -0.11444 | 0.004578 | -0.054932 | -0.09613 | -0.050354 | -0.19226 | -0.045776 | 0.62256 | 122.2412 | -0.11444 | 122.049 | 0.018311 | -0.054932 | 0.032043 | 0.050354 | -122.2641 | -122.3648 | 0.054932 | 0.05951 | -0.086975 | 0.009156 | -0.13733 | -0.009155 | -0.027466 | -0.21973 | 0.1236 | 0.13733 | 0.050354 | 0.14648 | 0.059509 | 0.004578 | -0.041198 | 0.13275 | 122.1634 | 0.05951 | 122.3557 | 0.10986 | 122.3465 | -122.3236 | -122.3831 | 0.009156 | 122.1542 | -0.009155 | 0.72784
3871.1875 | 122.4289 | -0.082397 | 122.2687 | -0.15083 | -0.042603 | 0.0023776 | 0.024646 | -0.0017005 | -0.01053 | -0.0017325 | -0.10159 | 0.0070197 | 0.064704 | 0.043637 | -0.017942 | 0.026981 | -0.0081433 | -0.13733 | 0 | -0.050354 | -0.073242 | 0.004578 | -0.13275 | -0.013733 | 0.67749 | 122.2137 | -0.091553 | 122.1085 | 0.11444 | 0.041199 | 0.10986 | 0.032043 | -122.2687 | -122.3419 | 0.086975 | 0.068664 | -0.050354 | 0.036621 | -0.082397 | -0.009156 | -0.054932 | -0.16022 | 0.19684 | 0.19226 | 0.1236 | 0.20142 | 0.13275 | 0.054932 | -0.022888 | 0.20599 | 122.2 | 0.050354 | 122.3053 | 0.082397 | 122.2961 | -122.319 | -122.3602 | 0.009155 | 122.1909 | -0.054932 | 0.75989
3872.8906 | 122.3419 | -0.09613 | 122.2778 | -0.15846 | -0.043457 | 0.001523 | 0.024432 | -0.0023413 | -0.009675 | -0.0021597 | -0.1199 | 0.0078741 | 0.064491 | 0.045346 | -0.01602 | 0.028476 | -0.0060071 | -0.10529 | -0.013733 | -0.054932 | -0.059509 | 0.018311 | -0.12817 | -0.032043 | 0.68207 | 122.2595 | -0.09613 | 122.0535 | 0.050354 | -0.036621 | 0.036621 | 0.041198 | -122.2916 | -122.3373 | 0.11444 | 0.064087 | -0.032044 | 0.022889 | -0.073242 | 0 | -0.018311 | -0.2243 | 0.14648 | 0.13275 | 0.059509 | 0.13275 | 0.059509 | 0.073243 | -0.004577 | 0.14648 | 122.1497 | 0.041199 | 122.3557 | 0.082397 | 122.3557 | -122.3328 | -122.374 | 0.036621 | 122.1497 | -0.009156 | 0.7782
3874.6406 | 122.3511 | -0.086975 | 122.2824 | -0.12794 | -0.040039 | 0.0030184 | 0.022723 | 0.0021447 | -0.010743 | -0.0025869 | -0.1077 | 0.0048833 | 0.06385 | 0.047268 | -0.016233 | 0.027621 | -0.0070751 | -0.14648 | -0.013733 | -0.036621 | -0.10529 | -0.036621 | -0.15564 | -0.032043 | 0.60883 | 122.2458 | -0.10986 | 122.0444 | 0.036621 | -0.041199 | 0.036621 | 0.050354 | -122.2961 | -122.3877 | 0.050354 | 0.054932 | -0.068665 | 0.004578 | -0.11902 | -0.022888 | -0.036621 | -0.23804 | 0.1236 | 0.1236 | 0.045776 | 0.14648 | 0.068664 | 0 | -0.068665 | 0.14648 | 122.1542 | 0.022888 | 122.3557 | 0.073242 | 122.3328 | -122.319 | -122.3923 | -0.018311 | 122.1313 | -0.059509 | 0.6958
3876.3281 | 122.4152 | -0.059509 | 122.2321 | -0.15083 | -0.041321 | 0.002164 | 0.019091 | -0.00020513 | -0.0098886 | -0.0055777 | -0.0069885 | 0.0057379 | 0.062782 | 0.049618 | -0.017301 | 0.025912 | 0.0046741 | -0.1236 | -0.050354 | -0.013733 | -0.036621 | 0.073242 | -0.059509 | 0.045776 | 0.73242 | 122.2229 | -0.082397 | 122.1085 | 0.1236 | 0.086975 | 0.11902 | 0.045776 | -122.2824 | -122.2687 | 0.13275 | 0.10528 | 0 | 0.059509 | -0.045776 | -0.022888 | -0.009156 | -0.1236 | 0.1831 | 0.17853 | 0.14648 | 0.20142 | 0.16937 | 0.086975 | -0.022888 | 0.20599 | 122.1909 | -0.036621 | 122.3053 | 0.009155 | 122.2824 | -122.2458 | -122.3145 | 0.022888 | 122.168 | -0.064087 | 0.79193
3878.0938 | 122.4564 | -0.07782 | 122.2458 | -0.18898 | -0.041107 | 0.0017368 | 0.025073 | 0.0029993 | -0.010957 | -0.0038687 | -0.074127 | 0.0065923 | 0.062354 | 0.048977 | -0.018156 | 0.028476 | -0.0010937 | -0.13733 | 0.009155 | -0.045776 | -0.059509 | 0.036621 | -0.11902 | -0.004578 | 0.67749 | 122.2321 | -0.07782 | 122.1313 | 0.13733 | 0.059509 | 0.13275 | 0.032044 | -122.2366 | -122.3053 | 0.11444 | 0.073242 | -0.041199 | 0.041198 | -0.073243 | 0 | -0.013733 | -0.11444 | 0.21515 | 0.21057 | 0.13733 | 0.21057 | 0.13733 | 0.082397 | -0.013733 | 0.21515 | 122.2092 | 0.054931 | 122.3099 | 0.086975 | 122.3099 | -122.2916 | -122.3236 | 0.018311 | 122.2092 | -0.059509 | 0.75531
3879.8438 | 122.4701 | -0.045776 | 122.2366 | -0.18135 | -0.041535 | 0.0010958 | 0.021869 | -0.0017005 | -0.010316 | -0.0030141 | -0.077179 | 0.0038153 | 0.062354 | 0.045987 | -0.016874 | 0.027408 | -0.0070751 | -0.064087 | -0.041199 | -0.013733 | 0.027466 | 0.12817 | -0.036621 | 0.054932 | 0.75989 | 122.2137 | -0.07782 | 122.1771 | 0.17853 | 0.10529 | 0.16937 | 0.032043 | -122.2778 | -122.2092 | 0.17395 | 0.10071 | 0.009155 | 0.068665 | -0.022888 | -0.032044 | -0.022888 | -0.059509 | 0.2243 | 0.21515 | 0.15106 | 0.24719 | 0.18311 | 0.14191 | 0.041199 | 0.25635 | 122.2549 | -0.027466 | 122.2916 | 0.004577 | 122.2595 | -122.2504 | -122.3145 | 0.073242 | 122.2229 | -0.018311 | 0.80566
3881.5938 | 122.4655 | -0.059509 | 122.2366 | -0.16609 | -0.043244 | 0.0034456 | 0.022723 | 0.0036401 | -0.01117 | -0.0042959 | -0.037506 | 0.0061651 | 0.062568 | 0.050259 | -0.016874 | 0.025912 | -0.0072889 | -0.050354 | -0.036621 | 0.009155 | 0.036621 | 0.13275 | -0.036621 | 0.073242 | 0.76446 | 122.2 | -0.059509 | 122.1725 | 0.19226 | 0.11444 | 0.16479 | 0.068664 | -122.2733 | -122.2 | 0.19226 | 0.13275 | 0.022888 | 0.064087 | -0.045776 | 0 | -0.036621 | -0.064087 | 0.25177 | 0.2243 | 0.17395 | 0.2243 | 0.17395 | 0.1236 | 0.027466 | 0.25177 | 122.2321 | -0.045776 | 122.2595 | 0.022888 | 122.2595 | -122.2275 | -122.2961 | 0.09613 | 122.2321 | 0.009155 | 0.82397
3883.2969 | 122.4197 | -0.041199 | 122.2229 | -0.20424 | -0.044312 | 0.0025912 | 0.023364 | -0.0044775 | -0.012879 | -0.0057913 | -0.022247 | 0.0050971 | 0.061714 | 0.041073 | -0.020292 | 0.026126 | -0.0072889 | -0.091553 | -0.036621 | -0.027466 | 0 | 0.11444 | -0.050354 | 0.064087 | 0.74616 | 122.2137 | -0.068665 | 122.1222 | 0.13275 | 0.082397 | 0.11444 | 0.013733 | -122.2595 | -122.2229 | 0.15564 | 0.10529 | -0.009155 | 0.091553 | -0.022888 | -0.027466 | -0.009155 | -0.10071 | 0.17395 | 0.15564 | 0.1236 | 0.18311 | 0.15106 | 0.14191 | 0.027466 | 0.20142 | 122.1909 | -0.009155 | 122.2824 | 0.004578 | 122.2549 | -122.2504 | -122.2916 | 0.041199 | 122.1634 | -0.050354 | 0.78735
3885.0469 | 122.3648 | -0.091553 | 122.2733 | -0.16609 | -0.044098 | 0.00045503 | 0.019946 | 0.0012903 | -0.011598 | -0.0017325 | -0.049713 | 0.0042425 | 0.064491 | 0.0509 | -0.01666 | 0.028476 | -0.0040845 | -0.082397 | -0.041199 | -0.036621 | 0.004578 | 0.10071 | -0.018311 | 0.064087 | 0.88348 | 122.2137 | -0.082397 | 122.0627 | 0.09613 | 0.027466 | 0.059509 | 0.054932 | -122.3145 | -122.2687 | 0.19226 | 0.15564 | 0.073242 | 0.10071 | 0.01831 | 0.009156 | -0.059509 | -0.21057 | 0.18768 | 0.15106 | 0.11902 | 0.14191 | 0.10986 | 0.13733 | 0.041199 | 0.17853 | 122.1451 | -0.004578 | 122.2961 | 0.050354 | 122.3053 | -122.3099 | -122.3557 | 0.096131 | 122.1542 | 0.009156 | 0.97504
3886.8125 | 122.3282 | -0.10071 | 122.2778 | -0.20424 | -0.040253 | 0.0025912 | 0.024432 | 0.0010767 | -0.012025 | -0.0066457 | -0.14127 | 0.0065923 | 0.061073 | 0.045773 | -0.017515 | 0.026767 | -0.0047253 | -0.09613 | 0.004578 | -0.036621 | -0.07782 | -0.004578 | -0.14648 | -0.036621 | 0.66834 | 122.2549 | -0.10529 | 122.0444 | 0.022888 | -0.054932 | 0.041199 | 0.064087 | -122.2733 | -122.3557 | 0.09613 | 0.064087 | -0.045776 | 0 | -0.10986 | -0.004578 | -0.022888 | -0.23346 | 0.1236 | 0.14191 | 0.045776 | 0.14649 | 0.050354 | 0.032043 | -0.041199 | 0.12817 | 122.1497 | 0.041199 | 122.3602 | 0.10529 | 122.3557 | -122.3145 | -122.3831 | 0.022888 | 122.1451 | 0.004578 | 0.76904
3888.5781 | 122.3465 | -0.11444 | 122.2504 | -0.10506 | -0.045594 | 0.0010958 | 0.020373 | -0.0040503 | -0.010316 | -0.00087794 | -0.06192 | 0.0057379 | 0.064491 | 0.051327 | -0.017729 | 0.026981 | 0.00040169 | -0.10071 | -0.013733 | -0.041199 | -0.059509 | 0.041199 | -0.086975 | 0.009155 | 0.82398 | 122.2549 | -0.10071 | 122.0306 | 0.059509 | 0.009155 | 0.059509 | 0.073242 | -122.2641 | -122.3099 | 0.15564 | 0.1236 | 0.027466 | 0.050354 | -0.045776 | 0.013733 | 0.004578 | -0.21973 | 0.17395 | 0.17395 | 0.1236 | 0.16022 | 0.10986 | 0.082398 | -0.01831 | 0.16022 | 122.1313 | 0.027466 | 122.3557 | 0.10071 | 122.3694 | -122.2916 | -122.3511 | 0.054932 | 122.1451 | 0.013733 | 0.93842
3890.3438 | 122.4747 | -0.032043 | 122.2137 | -0.16609 | -0.042389 | 0.0040866 | 0.022937 | -0.0014867 | -0.009675 | -0.0028005 | -0.049713 | 0.0050971 | 0.06385 | 0.049618 | -0.017301 | 0.027408 | -0.0047253 | -0.068665 | -0.068665 | -0.013733 | 0.041199 | 0.13733 | -0.027466 | 0.073242 | 0.7782 | 122.2092 | -0.054932 | 122.168 | 0.17395 | 0.11444 | 0.17395 | 0.01831 | -122.2824 | -122.1725 | 0.16937 | 0.10529 | 0.004577 | 0.086975 | -0.013733 | -0.022889 | -0.004578 | -0.045776 | 0.20599 | 0.20599 | 0.14648 | 0.22888 | 0.16937 | 0.15106 | 0.054932 | 0.22888 | 122.2229 | -0.054932 | 122.2641 | -0.036622 | 122.2412 | -122.2275 | -122.2687 | 0.073242 | 122.2 | -0.036622 | 0.81024
3892.0469 | 122.4518 | -0.068665 | 122.2229 | -0.18898 | -0.041107 | 0.0013094 | 0.023578 | -0.00041873 | -0.0090342 | -0.0053641 | -0.098541 | 0.0050971 | 0.064491 | 0.04855 | -0.018156 | 0.026981 | -0.0036573 | -0.11902 | 0 | -0.059509 | -0.027466 | 0.050354 | -0.082397 | 0.032043 | 0.72327 | 122.1954 | -0.07782 | 122.1405 | 0.15106 | 0.068665 | 0.16022 | 0.009156 | -122.2229 | -122.2504 | 0.11902 | 0.10071 | -0.013732 | 0.091552 | -0.022888 | -0.009155 | -0.027465 | -0.082397 | 0.21973 | 0.22888 | 0.13733 | 0.23804 | 0.14649 | 0.10986 | 0.032043 | 0.22888 | 122.2183 | 0.059509 | 122.2733 | 0.068665 | 122.2641 | -122.2824 | -122.3007 | 0.041199 | 122.2092 | -0.050354 | 0.79193
3893.75 | 122.438 | -0.068665 | 122.2366 | -0.15083 | -0.042176 | 0.0023776 | 0.020587 | -0.0023413 | -0.01053 | -0.0053641 | -0.04361 | 0.0050971 | 0.063209 | 0.047268 | -0.019865 | 0.023776 | -0.0087841 | -0.086975 | -0.036621 | -0.027466 | 0.013733 | 0.13275 | -0.041199 | 0.082397 | 0.78278 | 122.1817 | -0.045776 | 122.1405 | 0.15106 | 0.07782 | 0.13733 | 0.041199 | -122.2733 | -122.2229 | 0.20142 | 0.15106 | 0.027466 | 0.10986 | -0.013733 | 0.022889 | -0.054931 | -0.09613 | 0.21973 | 0.20599 | 0.14649 | 0.18311 | 0.1236 | 0.16022 | 0.041199 | 0.19684 | 122.1863 | -0.009155 | 122.2275 | 0.032044 | 122.2504 | -122.2641 | -122.2824 | 0.082398 | 122.2092 | -0.01831 | 0.85144
3895.5 | 122.3511 | -0.086975 | 122.2549 | -0.24239 | -0.041748 | 0.0030184 | 0.023791 | -0.0014867 | -0.011384 | -0.0045095 | -0.10464 | 0.0070197 | 0.063636 | 0.048764 | -0.019438 | 0.02634 | -0.0030163 | -0.13275 | 0 | -0.054932 | -0.10986 | -0.041199 | -0.16022 | -0.027466 | 0.63171 | 122.2412 | -0.10071 | 122.0673 | 0.045776 | -0.027466 | 0.041199 | 0.032043 | -122.2549 | -122.3648 | 0.045776 | 0.059509 | -0.073242 | 0.027466 | -0.10528 | -0.013733 | -0.013733 | -0.18768 | 0.13275 | 0.12817 | 0.059509 | 0.14191 | 0.073242 | 0.013733 | -0.054931 | 0.14648 | 122.168 | 0.054932 | 122.3419 | 0.086975 | 122.3282 | -122.3099 | -122.3557 | -0.022888 | 122.1542 | -0.045776 | 0.71869
3897.25 | 122.3694 | -0.086975 | 122.2504 | -0.21187 | -0.041748 | 0.0036594 | 0.023578 | -0.00020513 | -0.009675 | -0.0032277 | -0.1077 | 0.0063787 | 0.063423 | 0.045559 | -0.016874 | 0.027408 | -0.0040845 | -0.13275 | 0.009155 | -0.054932 | -0.09613 | 0 | -0.15106 | -0.027466 | 0.64087 | 122.2412 | -0.11444 | 122.0673 | 0.068665 | -0.013733 | 0.050354 | 0.032043 | -122.2412 | -122.3465 | 0.086975 | 0.059509 | -0.064087 | 0.027466 | -0.09613 | -0.027466 | -0.009155 | -0.1831 | 0.15564 | 0.13733 | 0.073242 | 0.16479 | 0.10071 | 0.054932 | -0.041198 | 0.18311 | 122.1817 | 0.064087 | 122.3557 | 0.09613 | 122.3282 | -122.3053 | -122.3648 | -0.009155 | 122.1542 | -0.045776 | 0.72784
3899.0156 | 122.3969 | -0.082397 | 122.2641 | -0.12032 | -0.044098 | 0.0013094 | 0.02315 | -0.0017005 | -0.010316 | -0.0025869 | -0.092438 | 0.0063787 | 0.062782 | 0.049832 | -0.017088 | 0.026553 | -0.0023755 | -0.10986 | -0.004578 | -0.064087 | -0.064087 | 0.036621 | -0.073242 | 0.009155 | 0.82398 | 122.2458 | -0.091553 | 122.0993 | 0.10529 | 0.009155 | 0.082397 | 0.01831 | -122.2687 | -122.3282 | 0.11902 | 0.091552 | 0.009155 | 0.073242 | -0.009155 | -0.009156 | -0.01831 | -0.16479 | 0.18768 | 0.16479 | 0.091552 | 0.17395 | 0.10071 | 0.10071 | 0 | 0.19684 | 122.1909 | 0.059509 | 122.3373 | 0.077819 | 122.3282 | -122.3282 | -122.3557 | 0.01831 | 122.1817 | -0.027466 | 0.90637
3900.7656 | 122.3831 | -0.086975 | 122.2549 | -0.15846 | -0.042816 | 0.0019504 | 0.022296 | -0.0010595 | -0.010316 | -0.0025869 | -0.064972 | 0.0059515 | 0.064704 | 0.047696 | -0.017515 | 0.028049 | -0.0062207 | -0.10529 | -0.013733 | -0.045776 | -0.050354 | 0.045776 | -0.082397 | -0.004578 | 0.82398 | 122.2504 | -0.082397 | 122.0901 | 0.10529 | 0.022888 | 0.082397 | 0.041199 | -122.2687 | -122.3053 | 0.13275 | 0.082397 | 0.004578 | 0.041198 | -0.036621 | 0.004578 | -0.004578 | -0.16479 | 0.19226 | 0.16937 | 0.10986 | 0.16479 | 0.10528 | 0.091552 | -0.004578 | 0.18768 | 122.1725 | 0.032043 | 122.3328 | 0.073242 | 122.3373 | -122.3007 | -122.3373 | 0.036621 | 122.1771 | -0.018311 | 0.91095
3902.5312 | 122.4197 | -0.050354 | 122.2733 | -0.15083 | -0.045807 | 0.0019504 | 0.020587 | 0.0017175 | -0.010957 | -0.0038687 | -0.028351 | 0.0042425 | 0.064277 | 0.045346 | -0.017942 | 0.026553 | -0.0060071 | -0.1236 | -0.036621 | -0.036621 | -0.041199 | 0.064087 | -0.068665 | 0.036621 | 0.75531 | 122.1771 | -0.07782 | 122.0947 | 0.13275 | 0.091553 | 0.11444 | 0.013733 | -122.3099 | -122.3145 | 0.11444 | 0.086975 | -0.018311 | 0.073242 | -0.032044 | -0.027466 | -0.09613 | -0.17853 | 0.18311 | 0.16479 | 0.14191 | 0.19226 | 0.16937 | 0.10071 | -0.004578 | 0.21057 | 122.1725 | 0 | 122.2549 | 0.013733 | 122.2275 | -122.3099 | -122.3511 | 0.009155 | 122.1451 | -0.073242 | 0.80566
3904.2344 | 122.4655 | -0.041199 | 122.2549 | -0.18135 | -0.041321 | 0.0010958 | 0.024218 | 0.0044947 | -0.01117 | -0.0055777 | -0.058869 | 0.0059515 | 0.062995 | 0.051755 | -0.020933 | 0.027408 | -0.0053661 | -0.10071 | -0.013733 | -0.036621 | -0.018311 | 0.07782 | -0.082397 | 0.036621 | 0.75531 | 122.2 | -0.073242 | 122.168 | 0.16022 | 0.09613 | 0.16479 | 0.004578 | -122.2687 | -122.2733 | 0.11902 | 0.07782 | -0.041198 | 0.073242 | -0.045776 | -0.032043 | -0.054932 | -0.086975 | 0.20142 | 0.20599 | 0.13733 | 0.23804 | 0.16937 | 0.11444 | 0.01831 | 0.23346 | 122.2412 | 0.022888 | 122.2733 | 0.027466 | 122.2412 | -122.2916 | -122.3282 | 0.022888 | 122.2092 | -0.059509 | 0.79651
3906 | 122.438 | -0.064087 | 122.2504 | -0.21187 | -0.043457 | 0.00088223 | 0.021228 | -0.0019141 | -0.01117 | -0.0032277 | -0.0008851 | 0.0055243 | 0.065132 | 0.0462 | -0.019224 | 0.026553 | -0.0070751 | -0.1236 | -0.032043 | -0.013733 | -0.045776 | 0.068665 | -0.068665 | 0.059509 | 0.7782 | 122.2 | -0.068665 | 122.1176 | 0.13733 | 0.086975 | 0.11902 | 0.050354 | -122.2824 | -122.2961 | 0.13275 | 0.1236 | -0.004578 | 0.073242 | -0.054932 | -0.004578 | -0.050354 | -0.13275 | 0.20142 | 0.18311 | 0.15106 | 0.18768 | 0.15564 | 0.082398 | -0.032043 | 0.20599 | 122.1863 | -0.01831 | 122.2687 | 0.032044 | 122.2641 | -122.2641 | -122.319 | 0.018311 | 122.1817 | -0.059509 | 0.84228
3907.7656 | 122.3511 | -0.10986 | 122.3007 | -0.18135 | -0.040467 | 0.0023776 | 0.024859 | -0.00063233 | -0.010743 | -0.0038687 | -0.12906 | 0.0057379 | 0.065986 | 0.045132 | -0.017515 | 0.028049 | -0.0028027 | -0.11902 | -0.004578 | -0.054932 | -0.091553 | -0.036621 | -0.15106 | -0.041199 | 0.65918 | 122.2366 | -0.10986 | 122.049 | 0.027466 | -0.054932 | 0.045776 | 0.054931 | -122.3053 | -122.3923 | 0.073242 | 0.068664 | -0.041199 | 0.013733 | -0.09613 | 0 | -0.064087 | -0.25177 | 0.13733 | 0.15564 | 0.054931 | 0.15564 | 0.054931 | 0.018311 | -0.036621 | 0.13733 | 122.1588 | 0.050354 | 122.3465 | 0.10529 | 122.3465 | -122.3557 | -122.4106 | 0.01831 | 122.1588 | -0.009156 | 0.76904
3909.4688 | 122.4289 | -0.050354 | 122.2641 | -0.18135 | -0.041107 | 0.0017368 | 0.021228 | -0.0014867 | -0.01117 | -0.0023733 | -0.028351 | 0.0063787 | 0.060432 | 0.0509 | -0.017729 | 0.025485 | -0.0053661 | -0.09613 | -0.036621 | -0.013733 | -0.009155 | 0.086975 | -0.064087 | 0.032043 | 0.75989 | 122.2183 | -0.068665 | 122.1176 | 0.11444 | 0.073242 | 0.1236 | 0.036621 | -122.3007 | -122.2733 | 0.13733 | 0.082397 | -0.013733 | 0.045776 | -0.050354 | -0.018311 | -0.045776 | -0.14648 | 0.16479 | 0.17395 | 0.1236 | 0.19226 | 0.14191 | 0.10071 | 0.004578 | 0.18311 | 122.1863 | -0.022888 | 122.287 | 0.013733 | 122.2687 | -122.2778 | -122.3328 | 0.041199 | 122.168 | -0.045776 | 0.81024
3911.2188 | 122.4197 | -0.068665 | 122.2504 | -0.18898 | -0.043671 | 0.0013094 | 0.021228 | -0.0034095 | -0.01117 | -0.0055777 | -0.025299 | 0.0053107 | 0.064491 | 0.037015 | -0.017729 | 0.027408 | -0.0072889 | -0.10529 | -0.041199 | -0.013733 | -0.027466 | 0.059509 | -0.068665 | 0.050354 | 0.77362 | 122.2183 | -0.07782 | 122.113 | 0.13275 | 0.064087 | 0.11902 | 0.054932 | -122.2916 | -122.2778 | 0.12817 | 0.11902 | 0 | 0.064087 | -0.054932 | -0.009155 | -0.032043 | -0.13733 | 0.20142 | 0.18768 | 0.13275 | 0.19684 | 0.14191 | 0.073242 | -0.013733 | 0.21057 | 122.1909 | -0.027466 | 122.2961 | 0.027466 | 122.287 | -122.2641 | -122.3282 | 0.041199 | 122.1817 | -0.036621 | 0.84229
3912.9219 | 122.4701 | -0.041199 | 122.2412 | -0.16609 | -0.041535 | 0.0025912 | 0.022296 | 0.0017175 | -0.012879 | -0.0019461 | -0.080231 | 0.0050971 | 0.062141 | 0.045773 | -0.018583 | 0.027408 | -0.0051525 | -0.054932 | -0.045776 | -0.018311 | 0.027466 | 0.11902 | -0.036621 | 0.082397 | 0.78735 | 122.2321 | -0.073242 | 122.1817 | 0.16479 | 0.10986 | 0.16937 | 0.022888 | -122.287 | -122.2137 | 0.16022 | 0.1236 | 0.004578 | 0.10071 | -0.01831 | -0.032043 | -0.009155 | -0.059509 | 0.20599 | 0.21057 | 0.15106 | 0.24261 | 0.18311 | 0.13733 | 0.045777 | 0.23804 | 122.2549 | -0.027465 | 122.3053 | -0.004577 | 122.2733 | -122.2595 | -122.3145 | 0.068665 | 122.2229 | -0.013733 | 0.82855
3914.6875 | 122.3511 | -0.10529 | 122.2961 | -0.11269 | -0.041962 | -0.00061317 | 0.021869 | -0.0017005 | -0.011598 | -0.0021597 | -0.071076 | 0.0042425 | 0.06385 | 0.043637 | -0.019651 | 0.025699 | -0.0070751 | -0.15564 | -0.004578 | -0.068665 | -0.07782 | 0 | -0.10986 | -0.013733 | 0.79651 | 122.2641 | -0.086975 | 122.0352 | 0.054932 | 0.004578 | 0.027466 | 0.036621 | -122.3007 | -122.374 | 0.10529 | 0.091553 | -0.004577 | 0.054932 | -0.041198 | 0.018311 | -0.032044 | -0.26093 | 0.16022 | 0.13275 | 0.10986 | 0.11444 | 0.091553 | 0.068665 | -0.009155 | 0.14191 | 122.1222 | 0.064087 | 122.3511 | 0.10071 | 122.3694 | -122.3648 | -122.3831 | 0.027466 | 122.1405 | -0.050354 | 0.9018
3916.3906 | 122.4426 | -0.073242 | 122.2458 | -0.17372 | -0.044098 | 0.0028048 | 0.02016 | -0.0014867 | -0.011384 | -0.0057913 | -0.034454 | 0.0053107 | 0.062141 | 0.045987 | -0.018583 | 0.027835 | -0.0089977 | -0.12817 | -0.032043 | -0.013733 | -0.036621 | 0.068665 | -0.068665 | 0.041199 | 0.77362 | 122.2137 | -0.068665 | 122.1039 | 0.11902 | 0.064087 | 0.11902 | 0.059509 | -122.2778 | -122.2824 | 0.14191 | 0.11444 | 0.004577 | 0.054932 | -0.054932 | 0.004577 | -0.032044 | -0.14191 | 0.19226 | 0.19226 | 0.13733 | 0.18768 | 0.13275 | 0.082398 | -0.022888 | 0.18768 | 122.1725 | -0.01831 | 122.2824 | 0.041199 | 122.287 | -122.2595 | -122.3145 | 0.036621 | 122.1771 | -0.054932 | 0.84686
3918.1562 | 122.3694 | -0.09613 | 122.2595 | -0.1432 | -0.045807 | 0.0017368 | 0.021014 | -0.0010595 | -0.01117 | -0.0040823 | -0.09549 | 0.0063787 | 0.061714 | 0.051541 | -0.019438 | 0.027194 | -0.0062207 | -0.15106 | -0.004578 | -0.054932 | -0.10529 | -0.004578 | -0.11902 | -0.013733 | 0.81482 | 122.2595 | -0.10071 | 122.0444 | 0.059509 | -0.018311 | 0.022888 | 0.041198 | -122.2641 | -122.3648 | 0.091552 | 0.082397 | -0.022889 | 0.041199 | -0.064087 | -0.004578 | 0 | -0.21515 | 0.15564 | 0.11902 | 0.077819 | 0.1236 | 0.082397 | 0.050354 | -0.050354 | 0.16022 | 122.1451 | 0.050354 | 122.3602 | 0.091552 | 122.3557 | -122.3145 | -122.3602 | -0.009156 | 122.1405 | -0.054932 | 0.91095
3919.9062 | 122.4197 | -0.073242 | 122.2458 | -0.18898 | -0.042816 | -0.0018948 | 0.022509 | 0.0019311 | -0.012025 | -0.0032277 | -0.046661 | 0.0050971 | 0.063209 | 0.044919 | -0.015592 | 0.025912 | -0.0057935 | -0.059509 | -0.041199 | -0.018311 | 0.036621 | 0.12817 | -0.004578 | 0.091553 | 0.93384 | 122.2229 | -0.082397 | 122.113 | 0.16479 | 0.09613 | 0.11444 | 0.054931 | -122.287 | -122.2092 | 0.20142 | 0.16479 | 0.068664 | 0.10986 | 0.013733 | -0.009155 | -0.022889 | -0.13275 | 0.23804 | 0.18768 | 0.16937 | 0.19684 | 0.17853 | 0.14649 | 0.054932 | 0.24719 | 122.1954 | -0.022888 | 122.3053 | 0.032043 | 122.2961 | -122.2641 | -122.3282 | 0.10986 | 122.1863 | 0.013733 | 1.0071
3921.6719 | 122.4472 | -0.054932 | 122.2366 | -0.21187 | -0.041748 | 2.7834e-05 | 0.021228 | 0.0012903 | -0.011384 | -0.0034415 | -0.055817 | 0.0033881 | 0.064063 | 0.053464 | -0.017301 | 0.025912 | -0.0040845 | -0.054932 | -0.050354 | -0.004578 | 0.041199 | 0.14191 | -0.027466 | 0.082397 | 0.8194 | 122.1863 | -0.064087 | 122.168 | 0.16022 | 0.10071 | 0.17395 | 0.050354 | -122.287 | -122.1954 | 0.19684 | 0.13733 | 0.027466 | 0.086975 | -0.022888 | -0.009155 | -0.050354 | -0.068664 | 0.21515 | 0.22888 | 0.15564 | 0.23804 | 0.1648 | 0.14649 | 0.045777 | 0.2243 | 122.2321 | -0.045776 | 122.2504 | 0.004578 | 122.2412 | -122.2412 | -122.3007 | 0.096131 | 122.2229 | 0 | 0.87433
3923.375 | 122.3785 | -0.10071 | 122.2687 | -0.089798 | -0.041962 | 0.00024143 | 0.025073 | 0.00086307 | -0.01117 | -0.0040823 | -0.074127 | 0.0070197 | 0.062995 | 0.050046 | -0.018797 | 0.026767 | -0.0025891 | -0.10986 | 0.009155 | -0.068665 | -0.068665 | -0.013733 | -0.10071 | -0.004578 | 0.80109 | 122.2412 | -0.10071 | 122.0856 | 0.091553 | 0.013733 | 0.07782 | 0.032043 | -122.2595 | -122.3373 | 0.086975 | 0.09613 | 0 | 0.064087 | -0.032043 | 0 | -0.027466 | -0.18311 | 0.19226 | 0.17853 | 0.11444 | 0.17853 | 0.11444 | 0.054932 | 0 | 0.19226 | 122.1863 | 0.07782 | 122.3419 | 0.10986 | 122.3419 | -122.3373 | -122.3694 | 0.032043 | 122.1863 | -0.009155 | 0.90179
3925.1406 | 122.3465 | -0.09613 | 122.2778 | -0.16609 | -0.039612 | 0.002164 | 0.025073 | 0.00064947 | -0.011384 | -0.0042959 | -0.12601 | 0.0055243 | 0.063636 | 0.047055 | -0.018156 | 0.026981 | -0.0021619 | -0.11902 | -0.009155 | -0.041199 | -0.09613 | -0.022888 | -0.17853 | -0.045776 | 0.66834 | 122.2183 | -0.10529 | 122.0627 | 0.032043 | -0.050354 | 0.050354 | 0.054931 | -122.287 | -122.374 | 0.073242 | 0.050354 | -0.082398 | -0.004577 | -0.13733 | -0.009156 | -0.059509 | -0.21515 | 0.12817 | 0.14648 | 0.045776 | 0.15564 | 0.054932 | 0.018311 | -0.054931 | 0.13733 | 122.168 | 0.032044 | 122.3236 | 0.086975 | 122.3145 | -122.319 | -122.3831 | 0 | 122.1588 | -0.022889 | 0.76446
3926.875 | 122.4792 | -0.050354 | 122.2412 | -0.16609 | -0.042603 | 0.0045138 | 0.023791 | 0.0036401 | -0.009675 | -0.0047231 | -0.068024 | 0.0050971 | 0.064063 | 0.050473 | -0.018369 | 0.025272 | -0.0032299 | -0.082397 | -0.004578 | -0.027466 | 0.004578 | 0.086975 | -0.059509 | 0.054932 | 0.7782 | 122.2 | -0.082397 | 122.1863 | 0.17395 | 0.10071 | 0.17395 | 0.022888 | -122.2458 | -122.2366 | 0.13733 | 0.10529 | -0.009155 | 0.082398 | -0.032043 | -0.032043 | -0.041199 | -0.054932 | 0.2243 | 0.2243 | 0.15106 | 0.25635 | 0.18311 | 0.11444 | 0.032044 | 0.25635 | 122.2687 | 0.022888 | 122.2824 | 0.045776 | 122.2504 | -122.2687 | -122.3236 | 0.054932 | 122.2366 | -0.032043 | 0.82855
3928.625 | 122.4747 | -0.041199 | 122.2549 | -0.17372 | -0.042816 | 0.0010958 | 0.021228 | 0.0057763 | -0.01053 | -0.0077139 | -0.068024 | 0.0059515 | 0.062354 | 0.046414 | -0.01901 | 0.024844 | -0.0055799 | -0.045776 | -0.045776 | -0.013733 | 0.027466 | 0.13275 | -0.041199 | 0.068665 | 0.81482 | 122.1954 | -0.068665 | 122.168 | 0.18768 | 0.11902 | 0.17853 | 0.027466 | -122.3007 | -122.2275 | 0.17395 | 0.10986 | 0 | 0.082398 | -0.027466 | -0.027466 | -0.059509 | -0.086975 | 0.22888 | 0.21973 | 0.16022 | 0.24719 | 0.18768 | 0.14648 | 0.041199 | 0.25635 | 122.2366 | -0.032043 | 122.2641 | -0.004577 | 122.2366 | -122.2687 | -122.3236 | 0.068665 | 122.2092 | -0.004577 | 0.85602
3930.3906 | 122.4655 | -0.041199 | 122.2549 | -0.18135 | -0.043671 | 0.00024143 | 0.020587 | -0.0040503 | -0.012666 | -0.0038687 | -0.019196 | 0.0048833 | 0.063423 | 0.052609 | -0.017942 | 0.028903 | -0.0040845 | -0.059509 | -0.059509 | -0.004578 | 0.036621 | 0.16937 | 0.041199 | 0.11902 | 0.97504 | 122.1909 | -0.082397 | 122.168 | 0.21057 | 0.15106 | 0.15564 | 0.036621 | -122.3145 | -122.2183 | 0.21057 | 0.16022 | 0.082398 | 0.1236 | 0.045777 | -0.041198 | -0.064087 | -0.086975 | 0.25177 | 0.19684 | 0.19226 | 0.23804 | 0.23346 | 0.17395 | 0.041199 | 0.29297 | 122.2504 | -0.054931 | 122.2733 | -0.01831 | 122.2321 | -122.2595 | -122.3373 | 0.07782 | 122.2092 | -0.01831 | 1.0162
3932.1562 | 122.4152 | -0.059509 | 122.2549 | -0.15083 | -0.044098 | 0.0025912 | 0.021014 | -0.0021277 | -0.012452 | -0.0025869 | -0.028351 | 0.0040289 | 0.0615 | 0.045987 | -0.017301 | 0.027194 | -0.0028027 | -0.073242 | -0.032043 | -0.013733 | 0.036621 | 0.12817 | -0.009155 | 0.082397 | 0.93384 | 122.2092 | -0.07782 | 122.113 | 0.13733 | 0.091553 | 0.11444 | 0.045776 | -122.287 | -122.2183 | 0.18768 | 0.14191 | 0.050354 | 0.09613 | 0.004578 | -0.018311 | -0.045777 | -0.14191 | 0.19684 | 0.17395 | 0.15106 | 0.19226 | 0.16937 | 0.14191 | 0.050354 | 0.21515 | 122.1909 | -0.01831 | 122.287 | 0.027466 | 122.2687 | -122.2687 | -122.3328 | 0.09613 | 122.1725 | -0.013733 | 0.99335
3933.8594 | 122.5067 | -0.041199 | 122.2641 | -0.18898 | -0.044739 | 0.0010958 | 0.022082 | -0.00063233 | -0.01117 | -0.0045095 | -0.0008851 | 0.0044561 | 0.062141 | 0.048764 | -0.018583 | 0.026126 | -0.0053661 | -0.059509 | -0.045776 | -0.022888 | 0.045776 | 0.17853 | 0.022888 | 0.10071 | 0.97504 | 122.2 | -0.059509 | 122.1863 | 0.21973 | 0.14191 | 0.16479 | 0.018311 | -122.3099 | -122.2183 | 0.21973 | 0.14191 | 0.064087 | 0.1236 | 0.045776 | -0.01831 | -0.064087 | -0.07782 | 0.26093 | 0.20599 | 0.18311 | 0.2243 | 0.20142 | 0.20142 | 0.068664 | 0.27924 | 122.2458 | -0.022888 | 122.2595 | -0.004577 | 122.2412 | -122.287 | -122.3236 | 0.086975 | 122.2275 | -0.01831 | 1.0162
3935.6094 | 122.3557 | -0.10529 | 122.2824 | -0.12794 | -0.04303 | 0.0017368 | 0.025287 | 0.0015039 | -0.012239 | -0.0042959 | -0.12906 | 0.0072333 | 0.061714 | 0.046414 | -0.021574 | 0.027408 | -0.0094251 | -0.10529 | -0.013733 | -0.054932 | -0.036621 | 0.032043 | -0.10529 | -0.009155 | 0.7782 | 122.2595 | -0.10071 | 122.0673 | 0.054932 | -0.022888 | 0.050354 | 0.050354 | -122.2961 | -122.319 | 0.13733 | 0.096131 | 0 | 0.045777 | -0.050354 | 0.004578 | -0.022889 | -0.21515 | 0.16022 | 0.15564 | 0.082398 | 0.15106 | 0.07782 | 0.086975 | 0.018311 | 0.15564 | 122.168 | 0.041199 | 122.3602 | 0.091553 | 122.3648 | -122.3373 | -122.3831 | 0.068665 | 122.1725 | 0 | 0.88348
3937.375 | 122.4701 | -0.036621 | 122.2321 | -0.18898 | -0.043457 | 0.0025912 | 0.021441 | 0.00043587 | -0.010957 | -0.0023733 | -0.055817 | 0.0057379 | 0.062568 | 0.048764 | -0.017088 | 0.025912 | -0.0057935 | -0.050354 | -0.054932 | -0.009155 | 0.018311 | 0.13733 | -0.032043 | 0.068665 | 0.82855 | 122.2137 | -0.073242 | 122.1771 | 0.1831 | 0.10529 | 0.16022 | 0.027466 | -122.287 | -122.2137 | 0.17395 | 0.10529 | 0.004578 | 0.07782 | -0.022888 | -0.036621 | -0.018311 | -0.054932 | 0.21973 | 0.19684 | 0.14191 | 0.23346 | 0.17853 | 0.14648 | 0.027466 | 0.25635 | 122.2504 | -0.045777 | 122.287 | -0.018311 | 122.2504 | -122.2412 | -122.3053 | 0.054932 | 122.2137 | -0.013733 | 0.86517
3939.1562 | 122.4792 | -0.050354 | 122.2366 | -0.21187 | -0.040894 | 0.0045138 | 0.022937 | 8.47e-06 | -0.010957 | -0.0045095 | -0.074127 | 0.0063787 | 0.0615 | 0.049618 | -0.018797 | 0.027408 | -0.0040845 | -0.054932 | -0.036621 | -0.018311 | 0.045776 | 0.1236 | -0.022888 | 0.082397 | 0.82855 | 122.2229 | -0.064087 | 122.1771 | 0.18768 | 0.11444 | 0.17395 | 0.032043 | -122.2733 | -122.1909 | 0.17395 | 0.13275 | 0.027466 | 0.10071 | -0.004577 | -0.013733 | -0.013733 | -0.059509 | 0.23804 | 0.2243 | 0.16479 | 0.23804 | 0.17853 | 0.14191 | 0.064087 | 0.25177 | 122.2412 | -0.01831 | 122.287 | 0.013733 | 122.2733 | -122.2549 | -122.3007 | 0.09613 | 122.2275 | -0.004578 | 0.87891
3940.8594 | 122.3969 | -0.082397 | 122.2824 | -0.097427 | -0.042389 | 0.0013094 | 0.022937 | -0.00020513 | -0.01053 | -0.0028005 | -0.11685 | 0.0068059 | 0.061073 | 0.047055 | -0.017729 | 0.023776 | -0.0060071 | -0.10529 | 0.018311 | -0.054932 | -0.068665 | 0.032043 | -0.082397 | 0.032043 | 0.8606 | 122.2687 | -0.091553 | 122.0993 | 0.11444 | 0.022888 | 0.091553 | 0.027465 | -122.2641 | -122.3511 | 0.11444 | 0.11444 | 0 | 0.086975 | -0.027465 | -0.009156 | -0.013733 | -0.18311 | 0.19684 | 0.17395 | 0.10528 | 0.18311 | 0.11444 | 0.086975 | -0.013733 | 0.20599 | 122.1909 | 0.073243 | 122.3602 | 0.10071 | 122.3511 | -122.3373 | -122.374 | 0.013732 | 122.1817 | -0.022889 | 0.94299
3942.625 | 122.4701 | -0.045776 | 122.2412 | -0.2195 | -0.041962 | 0.0028048 | 0.021441 | -0.00020513 | -0.012879 | -0.0040823 | -0.052765 | 0.0031745 | 0.0615 | 0.0462 | -0.018797 | 0.029117 | -0.0025891 | -0.050354 | -0.027466 | -0.004578 | 0.027466 | 0.12817 | -0.032043 | 0.07782 | 0.82398 | 122.2046 | -0.073242 | 122.1817 | 0.1831 | 0.10986 | 0.17853 | 0.041198 | -122.2687 | -122.2137 | 0.17395 | 0.1236 | 0.013733 | 0.082398 | -0.027465 | -0.027466 | -0.036621 | -0.059509 | 0.22888 | 0.2243 | 0.15564 | 0.25177 | 0.18311 | 0.13275 | 0.032044 | 0.25635 | 122.2549 | -0.022888 | 122.2778 | 0.01831 | 122.2504 | -122.2458 | -122.3145 | 0.073242 | 122.2275 | -0.004578 | 0.86975
3944.3438 | 122.438 | -0.068665 | 122.2504 | -0.16609 | -0.041748 | 0.0019504 | 0.021014 | -0.00063233 | -0.010316 | -0.0021597 | -0.046661 | 0.0053107 | 0.061714 | 0.051541 | -0.017942 | 0.024417 | -0.0019483 | -0.10529 | -0.045776 | -0.027466 | -0.027466 | 0.086975 | -0.068665 | 0.068665 | 0.77362 | 122.2092 | -0.07782 | 122.1176 | 0.12817 | 0.082397 | 0.11444 | 0.041199 | -122.2961 | -122.2778 | 0.15564 | 0.13733 | 0 | 0.096131 | -0.041199 | -0.009155 | -0.041199 | -0.13275 | 0.19684 | 0.18311 | 0.15106 | 0.19226 | 0.16022 | 0.11444 | 0 | 0.20599 | 122.1954 | -0.01831 | 122.287 | 0.022889 | 122.2778 | -122.2778 | -122.3282 | 0.041199 | 122.1863 | -0.036621 | 0.84229
3946.1094 | 122.4426 | -0.054932 | 122.2137 | -0.2195 | -0.04068 | 0.0017368 | 0.019946 | -0.0017005 | -0.011598 | -0.0057913 | -0.055817 | 0.0050971 | 0.061927 | 0.045987 | -0.016874 | 0.02634 | -0.0049389 | -0.059509 | -0.045776 | -0.013733 | 0.032043 | 0.13733 | -0.018311 | 0.07782 | 0.82398 | 122.1863 | -0.082397 | 122.1725 | 0.17853 | 0.10986 | 0.15564 | 0.041199 | -122.2595 | -122.1817 | 0.19226 | 0.13275 | 0.036621 | 0.091553 | -0.004578 | -0.027465 | -0.027466 | -0.041199 | 0.23346 | 0.21057 | 0.16479 | 0.23804 | 0.19226 | 0.15106 | 0.045776 | 0.26092 | 122.2549 | -0.032043 | 122.2687 | 0.009156 | 122.2412 | -122.2275 | -122.2961 | 0.086975 | 122.2275 | -0.004577 | 0.87891
3947.8594 | 122.4609 | -0.036621 | 122.2092 | -0.19661 | -0.043244 | 0.004941 | 0.021655 | -0.00063233 | -0.010102 | -0.0032277 | -0.058869 | 0.0046697 | 0.061286 | 0.049618 | -0.01901 | 0.026126 | -0.0064343 | -0.059509 | -0.045776 | -0.009155 | 0.045776 | 0.12817 | -0.032043 | 0.07782 | 0.81482 | 122.2137 | -0.073242 | 122.1817 | 0.19226 | 0.1236 | 0.1831 | 0.027466 | -122.2549 | -122.1634 | 0.1648 | 0.11444 | 0.004578 | 0.086975 | -0.022888 | -0.036621 | 0.004578 | -0.027465 | 0.22888 | 0.21973 | 0.16022 | 0.25635 | 0.19684 | 0.13733 | 0.054931 | 0.2655 | 122.2549 | -0.036621 | 122.287 | -0.009155 | 122.2504 | -122.2183 | -122.2824 | 0.082397 | 122.2183 | -0.022888 | 0.85144
3949.6406 | 122.4701 | -0.045776 | 122.2321 | -0.15846 | -0.046448 | -0.001254 | 0.019519 | 0.0010767 | -0.01117 | -0.0036551 | -0.016144 | 0.0057379 | 0.062995 | 0.047268 | -0.017301 | 0.027194 | -0.0010937 | -0.10071 | -0.036621 | -0.027466 | -0.004578 | 0.10071 | -0.022888 | 0.086975 | 0.87891 | 122.2 | -0.07782 | 122.1542 | 0.19226 | 0.14191 | 0.15564 | 0.01831 | -122.2687 | -122.2366 | 0.14648 | 0.13275 | 0.022888 | 0.11444 | 0.004578 | -0.032044 | -0.032044 | -0.07782 | 0.23804 | 0.20142 | 0.18768 | 0.23346 | 0.21973 | 0.12817 | 0.022888 | 0.27008 | 122.2321 | -0.009155 | 122.2778 | 0.009155 | 122.2458 | -122.2595 | -122.3099 | 0.041198 | 122.2 | -0.054932 | 0.92468
3951.3438 | 122.3557 | -0.09613 | 122.2824 | -0.1432 | -0.040894 | 0.001523 | 0.026568 | -0.00063233 | -0.01117 | -0.0036551 | -0.13211 | 0.0068059 | 0.065345 | 0.05325 | -0.018156 | 0.026981 | -0.00088011 | -0.10071 | -0.013733 | -0.059509 | -0.041199 | 0.032043 | -0.091553 | 0.004578 | 0.81482 | 122.2321 | -0.091553 | 122.0993 | 0.068665 | -0.018311 | 0.054932 | 0.036621 | -122.2961 | -122.3236 | 0.12817 | 0.10071 | 0.004577 | 0.064087 | -0.032044 | 0.004577 | -0.050354 | -0.18311 | 0.16479 | 0.15106 | 0.077819 | 0.14649 | 0.073242 | 0.091552 | 0.01831 | 0.16022 | 122.1909 | 0.045776 | 122.3236 | 0.082397 | 122.3282 | -122.3419 | -122.374 | 0.054931 | 122.1954 | -0.004578 | 0.91095
3953.1094 | 122.438 | -0.032043 | 122.2366 | -0.17372 | -0.041748 | 0.0019504 | 0.025714 | 0.0012903 | -0.013307 | -0.0010915 | -0.098541 | 0.0072333 | 0.062141 | 0.053036 | -0.017729 | 0.02869 | -0.0030163 | -0.11444 | -0.018311 | -0.045776 | -0.032043 | 0.059509 | -0.091553 | 0.022888 | 0.76904 | 122.2046 | -0.059509 | 122.168 | 0.16022 | 0.086975 | 0.15564 | -0.013733 | -122.2549 | -122.2687 | 0.091552 | 0.054931 | -0.05951 | 0.068664 | -0.045777 | -0.027466 | -0.032043 | -0.068664 | 0.19226 | 0.18768 | 0.11902 | 0.21515 | 0.14648 | 0.10528 | 0.013733 | 0.21973 | 122.2275 | 0.027465 | 122.2641 | 0.013732 | 122.2366 | -122.2824 | -122.2961 | 0 | 122.2 | -0.082398 | 0.80109
3954.8125 | 122.3831 | -0.091553 | 122.2458 | -0.16609 | -0.043885 | 0.0023776 | 0.024005 | -0.0023413 | -0.0090342 | -0.0040823 | -0.09549 | 0.0070197 | 0.064704 | 0.056241 | -0.018156 | 0.02634 | -0.0042981 | -0.14191 | 0 | -0.064087 | -0.082397 | -0.004578 | -0.14648 | -0.027466 | 0.6958 | 122.2504 | -0.10529 | 122.0947 | 0.073242 | -0.009155 | 0.07782 | 0.027466 | -122.2458 | -122.3282 | 0.086975 | 0.064087 | -0.054931 | 0.036621 | -0.082397 | -0.013733 | 0.004577 | -0.15106 | 0.16479 | 0.16937 | 0.082398 | 0.18311 | 0.096131 | 0.059509 | -0.01831 | 0.17853 | 122.2 | 0.064087 | 122.3557 | 0.091553 | 122.3419 | -122.3099 | -122.3511 | 0.009156 | 122.1863 | -0.050354 | 0.78735
3956.5156 | 122.3373 | -0.11444 | 122.2733 | -0.10506 | -0.044739 | 0.00088223 | 0.021441 | 0.0036401 | -0.013093 | -0.0045095 | -0.040558 | 0.0068059 | 0.062995 | 0.042142 | -0.018583 | 0.026767 | -0.0030163 | -0.16937 | 0.018311 | -0.041199 | -0.10071 | -0.004578 | -0.10071 | -0.018311 | 0.83771 | 122.2275 | -0.10986 | 122.0581 | 0.073242 | -0.013733 | 0.013733 | 0.073242 | -122.2549 | -122.374 | 0.10986 | 0.09613 | 0.013733 | 0.022888 | -0.059509 | 0.004578 | -0.045776 | -0.21515 | 0.18768 | 0.12817 | 0.10071 | 0.1236 | 0.09613 | 0.036621 | -0.059509 | 0.18311 | 122.168 | 0.05951 | 122.3373 | 0.13275 | 122.3419 | -122.3145 | -122.3831 | 0.013733 | 122.1725 | -0.054932 | 0.95215
3958.2812 | 122.4243 | -0.068665 | 122.2733 | -0.15846 | -0.043244 | 0.0013094 | 0.021441 | -0.0038367 | -0.010316 | -0.0032277 | -0.034454 | 0.0063787 | 0.063636 | 0.045987 | -0.016233 | 0.02634 | -0.0083569 | -0.11902 | -0.036621 | -0.027466 | -0.032043 | 0.073242 | -0.068665 | 0.045776 | 0.8194 | 122.2183 | -0.07782 | 122.113 | 0.1236 | 0.07782 | 0.10986 | 0.041199 | -122.3099 | -122.3053 | 0.14191 | 0.11444 | 0 | 0.073242 | -0.041199 | -0.009155 | -0.054931 | -0.16022 | 0.19226 | 0.17853 | 0.14649 | 0.18768 | 0.15564 | 0.10071 | -0.004577 | 0.20142 | 122.1909 | -0.009155 | 122.2961 | 0.032044 | 122.287 | -122.3007 | -122.3511 | 0.036622 | 122.1817 | -0.050354 | 0.88806
3959.9844 | 122.3511 | -0.082397 | 122.2824 | -0.12794 | -0.041321 | 0.0013094 | 0.025287 | 0.0034265 | -0.010316 | -0.0038687 | -0.12296 | 0.0070197 | 0.061927 | 0.047268 | -0.017729 | 0.027835 | -0.0015209 | -0.10071 | 0 | -0.036621 | -0.054932 | 0.032043 | -0.10986 | -0.013733 | 0.79193 | 122.2549 | -0.09613 | 122.0581 | 0.064087 | -0.036621 | 0.068665 | 0.045776 | -122.2824 | -122.3373 | 0.11444 | 0.068664 | -0.027466 | 0.022888 | -0.073242 | -0.013733 | -0.027466 | -0.22431 | 0.14648 | 0.15106 | 0.045776 | 0.16479 | 0.059509 | 0.068664 | -0.018311 | 0.16022 | 122.1542 | 0.036621 | 122.3511 | 0.082397 | 122.3373 | -122.319 | -122.3785 | 0.027465 | 122.1405 | -0.018311 | 0.87433
3961.75 | 122.406 | -0.068665 | 122.287 | -0.18898 | -0.043885 | 0.0023776 | 0.022082 | 0.00043587 | -0.009675 | -0.0042959 | -0.1199 | 0.0080877 | 0.06385 | 0.046628 | -0.01666 | 0.028476 | -0.0028027 | -0.15106 | 0.013733 | -0.045776 | -0.086975 | 0 | -0.14191 | -0.022888 | 0.71411 | 122.2458 | -0.091553 | 122.0993 | 0.07782 | 0.009155 | 0.10071 | 0.022889 | -122.2733 | -122.374 | 0.068665 | 0.045777 | -0.073242 | 0.022888 | -0.096131 | -0.022888 | -0.041198 | -0.18768 | 0.14649 | 0.16937 | 0.07782 | 0.19226 | 0.10071 | 0.045776 | -0.041199 | 0.16937 | 122.1909 | 0.059509 | 122.3373 | 0.082398 | 122.3145 | -122.3328 | -122.3785 | -0.01831 | 122.168 | -0.082397 | 0.78278
3963.5156 | 122.3282 | -0.09613 | 122.2824 | -0.089798 | -0.041321 | 0.0019504 | 0.022723 | 0.00022207 | -0.011598 | -0.0032277 | -0.037506 | 0.0057379 | 0.065986 | 0.044491 | -0.018583 | 0.026126 | -0.0047253 | -0.11902 | -0.018311 | -0.032043 | -0.064087 | 0.032043 | -0.09613 | 0.027466 | 0.87433 | 122.2504 | -0.09613 | 122.049 | 0.082397 | -0.013733 | 0.032043 | 0.064087 | -122.3007 | -122.3465 | 0.12817 | 0.1236 | 0 | 0.059509 | -0.064087 | 0 | -0.032044 | -0.23346 | 0.17853 | 0.12817 | 0.082397 | 0.12817 | 0.082397 | 0.064086 | -0.032044 | 0.17853 | 122.1451 | 0.013732 | 122.3465 | 0.077819 | 122.3465 | -122.3145 | -122.3785 | 0.032043 | 122.1451 | -0.022889 | 0.97046
3965.2812 | 122.3557 | -0.082397 | 122.2595 | -0.16609 | -0.042389 | 0.00088223 | 0.024646 | -0.0010595 | -0.0088206 | -0.0047231 | -0.1138 | 0.0055243 | 0.064063 | 0.050686 | -0.017942 | 0.027194 | -0.0017347 | -0.1236 | -0.004578 | -0.064087 | -0.10529 | -0.041199 | -0.16937 | -0.036621 | 0.70038 | 122.2458 | -0.09613 | 122.0673 | 0.032043 | -0.032043 | 0.054932 | 0.01831 | -122.2641 | -122.3648 | 0.041198 | 0.045776 | -0.086976 | 0.027466 | -0.10529 | -0.013733 | -0.013732 | -0.19226 | 0.11444 | 0.13733 | 0.050354 | 0.15106 | 0.064087 | 0.022888 | -0.041199 | 0.12817 | 122.1634 | 0.059509 | 122.3419 | 0.077819 | 122.3282 | -122.3236 | -122.3557 | -0.022889 | 122.1497 | -0.041199 | 0.78277
3966.9844 | 122.3511 | -0.10071 | 122.2733 | -0.18135 | -0.041535 | 0.0017368 | 0.024859 | 0.0029993 | -0.011384 | -0.0051505 | -0.09549 | 0.0068059 | 0.063423 | 0.041073 | -0.017729 | 0.028049 | -0.0057935 | -0.13275 | -0.009155 | -0.050354 | -0.09613 | -0.022888 | -0.15106 | -0.045776 | 0.70496 | 122.2321 | -0.11444 | 122.049 | 0.045776 | -0.041199 | 0.054932 | 0.050354 | -122.2824 | -122.3694 | 0.07782 | 0.054932 | -0.050354 | 0.004578 | -0.10071 | -0.013733 | -0.041198 | -0.2243 | 0.14648 | 0.15564 | 0.059509 | 0.16937 | 0.073242 | 0.027466 | -0.045776 | 0.16022 | 122.1634 | 0.041199 | 122.3465 | 0.091553 | 122.3328 | -122.3236 | -122.3877 | 0.004578 | 122.1497 | -0.032043 | 0.80566
3968.75 | 122.3511 | -0.09613 | 122.2733 | -0.15083 | -0.044953 | 0.0019504 | 0.021228 | -0.00063233 | -0.012025 | -0.0040823 | -0.034454 | 0.0059515 | 0.063423 | 0.050259 | -0.017301 | 0.025699 | -0.0032299 | -0.1236 | -0.018311 | -0.064087 | -0.07782 | 0.041199 | -0.10071 | 0.004578 | 0.88348 | 122.2321 | -0.091553 | 122.0352 | 0.068665 | 0.004578 | 0.032043 | 0.032043 | -122.2916 | -122.3511 | 0.13733 | 0.10071 | -0.004578 | 0.068665 | -0.036621 | 0.004577 | -0.041198 | -0.23804 | 0.16479 | 0.12817 | 0.10071 | 0.1236 | 0.096131 | 0.10529 | -0.013733 | 0.16022 | 122.1268 | 0.045776 | 122.3236 | 0.077819 | 122.3282 | -122.3373 | -122.3648 | 0.01831 | 122.1313 | -0.027466 | 0.97961
3970.5156 | 122.3785 | -0.07782 | 122.2687 | -0.18135 | -0.041748 | 0.0017368 | 0.025927 | -0.0040503 | -0.007966 | -0.0025869 | -0.083283 | 0.0053107 | 0.066413 | 0.046414 | -0.017088 | 0.027835 | -0.0017347 | -0.12817 | 0 | -0.064087 | -0.09613 | 0.009155 | -0.13733 | -0.036621 | 0.72784 | 122.2321 | -0.09613 | 122.0993 | 0.086975 | 0.022888 | 0.09613 | 0.013733 | -122.2687 | -122.3648 | 0.086975 | 0.041199 | -0.059509 | 0.027466 | -0.073242 | -0.01831 | -0.036621 | -0.16937 | 0.16479 | 0.17395 | 0.10071 | 0.19226 | 0.11902 | 0.073242 | -0.032043 | 0.1831 | 122.1954 | 0.064087 | 122.3282 | 0.07782 | 122.3099 | -122.3328 | -122.3648 | -0.01831 | 122.1771 | -0.050354 | 0.80566
3972.2812 | 122.3877 | -0.09613 | 122.319 | -0.15083 | -0.042603 | 0.00024143 | 0.021869 | -0.0019141 | -0.010957 | -0.0053641 | -0.06192 | 0.0070197 | 0.061286 | 0.048123 | -0.018156 | 0.028049 | -0.0015209 | -0.13275 | -0.004578 | -0.07782 | -0.086975 | -0.004578 | -0.11902 | -0.022888 | 0.8606 | 122.2641 | -0.10529 | 122.0718 | 0.068665 | 0.009155 | 0.054932 | 0.01831 | -122.3236 | -122.406 | 0.091552 | 0.073242 | -0.022889 | 0.054932 | -0.041199 | -0.009156 | -0.054932 | -0.24719 | 0.16479 | 0.15106 | 0.10528 | 0.16022 | 0.11444 | 0.073242 | -0.009155 | 0.17395 | 122.1771 | 0.073242 | 122.3694 | 0.091552 | 122.3602 | -122.3969 | -122.4243 | 0.009155 | 122.168 | -0.036621 | 0.95673
3973.9844 | 122.3969 | -0.09613 | 122.2961 | -0.12794 | -0.041962 | 0.0028048 | 0.021228 | -0.0014867 | -0.0083932 | -0.0013051 | -0.083283 | 0.0083013 | 0.0615 | 0.045559 | -0.017942 | 0.02634 | -0.0075025 | -0.12817 | -0.004578 | -0.045776 | -0.045776 | 0.032043 | -0.073242 | 0.013733 | 0.87891 | 122.2412 | -0.10529 | 122.0901 | 0.10529 | 0.041199 | 0.082397 | 0.050354 | -122.3007 | -122.3419 | 0.12817 | 0.10986 | 0.022888 | 0.059509 | -0.027466 | -0.009156 | -0.054932 | -0.20599 | 0.20142 | 0.17853 | 0.13733 | 0.18768 | 0.14649 | 0.077819 | 0 | 0.21057 | 122.1954 | 0.041198 | 122.3465 | 0.091552 | 122.3373 | -122.3419 | -122.4014 | 0.050354 | 122.1863 | -0.032044 | 0.97504
3975.7344 | 122.4014 | -0.086975 | 122.2916 | -0.15083 | -0.043244 | 0.00088223 | 0.022723 | 0.0012903 | -0.0098886 | -0.0066457 | -0.098541 | 0.0046697 | 0.063636 | 0.043423 | -0.018583 | 0.027621 | -0.0066479 | -0.086975 | 0 | -0.041199 | -0.041199 | 0.073242 | -0.07782 | 0.018311 | 0.88348 | 122.2412 | -0.068665 | 122.0901 | 0.10986 | 0.036621 | 0.09613 | 0.045776 | -122.2916 | -122.3328 | 0.16022 | 0.10529 | 0.009155 | 0.05951 | -0.036621 | 0.01831 | -0.050354 | -0.20142 | 0.19684 | 0.1831 | 0.1236 | 0.16479 | 0.10529 | 0.11444 | 0 | 0.17853 | 122.1588 | 0.041199 | 122.3099 | 0.086975 | 122.3282 | -122.3328 | -122.3602 | 0.045776 | 122.1771 | 0 | 0.97046
3977.4844 | 122.3282 | -0.09613 | 122.2595 | -0.16609 | -0.041962 | 0.0025912 | 0.023364 | 0.0034265 | -0.009675 | -0.0015189 | -0.083283 | 0.0065923 | 0.065132 | 0.047268 | -0.01666 | 0.028903 | -0.0038709 | -0.13275 | 0.013733 | -0.059509 | -0.11444 | -0.036621 | -0.15564 | -0.045776 | 0.70953 | 122.2321 | -0.10529 | 122.0398 | 0.036621 | -0.041199 | 0.045776 | 0.036621 | -122.2458 | -122.374 | 0.059509 | 0.050354 | -0.05951 | 0.013733 | -0.096131 | -0.009156 | -0.027465 | -0.21973 | 0.13275 | 0.14191 | 0.054931 | 0.15106 | 0.064087 | 0.022888 | -0.054932 | 0.14191 | 122.1451 | 0.073242 | 122.3373 | 0.10986 | 122.3282 | -122.319 | -122.3648 | -0.018311 | 122.1359 | -0.036621 | 0.80566
3979.25 | 122.319 | -0.086975 | 122.2916 | -0.17372 | -0.043457 | 0.0036594 | 0.024005 | -0.00041873 | -0.010102 | -0.0028005 | -0.10464 | 0.0063787 | 0.064491 | 0.049405 | -0.016233 | 0.026981 | -0.0025891 | -0.1236 | -0.004578 | -0.045776 | -0.1236 | -0.041199 | -0.16479 | -0.050354 | 0.6958 | 122.2595 | -0.11444 | 122.0306 | 0.018311 | -0.041199 | 0.045776 | 0.041199 | -122.2961 | -122.4152 | 0.045776 | 0.036621 | -0.07782 | -0.004578 | -0.11902 | -0.027466 | -0.032044 | -0.26093 | 0.10529 | 0.13275 | 0.045776 | 0.16022 | 0.073242 | 0.004577 | -0.07782 | 0.13275 | 122.1451 | 0.041198 | 122.374 | 0.082397 | 122.3465 | -122.3373 | -122.406 | -0.036621 | 122.1176 | -0.036621 | 0.78278
3980.9531 | 122.4655 | -0.054932 | 122.2641 | -0.097427 | -0.043457 | 0.0010958 | 0.021869 | -0.0023413 | -0.01053 | -0.0036551 | 0.0021667 | 0.0036017 | 0.064704 | 0.039792 | -0.017088 | 0.025485 | -0.0049389 | -0.11444 | -0.027466 | -0.041199 | -0.036621 | 0.086975 | -0.036621 | 0.064087 | 0.87891 | 122.2 | -0.091553 | 122.1313 | 0.16479 | 0.11902 | 0.14191 | 0.013733 | -122.2916 | -122.3007 | 0.14191 | 0.11902 | 0.018311 | 0.10529 | 0.004578 | -0.036621 | -0.064087 | -0.13275 | 0.21973 | 0.19684 | 0.17395 | 0.23346 | 0.21057 | 0.12817 | 0.004578 | 0.25635 | 122.2229 | 0.013733 | 122.2916 | 0.027466 | 122.2549 | -122.3053 | -122.3557 | 0.018311 | 122.1863 | -0.059509 | 0.93384
3982.7188 | 122.4289 | -0.045776 | 122.2733 | -0.13557 | -0.04538 | 0.0028048 | 0.020587 | 0.0010767 | -0.01117 | -0.0021597 | -0.01004 | 0.0061651 | 0.065132 | 0.049405 | -0.018583 | 0.026981 | -0.0034435 | -0.10529 | -0.018311 | -0.022888 | -0.036621 | 0.082397 | -0.059509 | 0.036621 | 0.80566 | 122.1817 | -0.082397 | 122.1176 | 0.1236 | 0.064087 | 0.10529 | 0.022888 | -122.2916 | -122.3099 | 0.12817 | 0.082397 | -0.013733 | 0.059509 | -0.036621 | -0.036621 | -0.091552 | -0.15564 | 0.16937 | 0.15106 | 0.10986 | 0.18768 | 0.14648 | 0.10528 | -0.013733 | 0.20599 | 122.2 | 0.004577 | 122.2641 | 0.027465 | 122.2275 | -122.2961 | -122.3557 | 0.009155 | 122.1634 | -0.05951 | 0.85144
3984.5 | 122.3419 | -0.091553 | 122.3007 | -0.12794 | -0.039826 | 0.0025912 | 0.024646 | 0.0038537 | -0.009675 | 0.00019006 | -0.10159 | 0.0078741 | 0.063636 | 0.044919 | -0.016447 | 0.026767 | -0.0019483 | -0.10071 | -0.009155 | -0.036621 | -0.068665 | 0.013733 | -0.1236 | -0.027466 | 0.80109 | 122.2458 | -0.07782 | 122.0673 | 0.032043 | -0.032043 | 0.036621 | 0.054932 | -122.3099 | -122.3694 | 0.10529 | 0.064087 | -0.032043 | 0.009155 | -0.086975 | 0.013733 | -0.054931 | -0.23346 | 0.1236 | 0.12817 | 0.05951 | 0.11444 | 0.045777 | 0.050354 | -0.032044 | 0.10986 | 122.1451 | 0.027466 | 122.3236 | 0.082398 | 122.3373 | -122.3373 | -122.3785 | 0.022888 | 122.1588 | -0.009155 | 0.89264
3986.2031 | 122.4976 | -0.050354 | 122.2641 | -0.22713 | -0.046662 | 0.0010958 | 0.021228 | 0.0027857 | -0.0092478 | -0.0038687 | 0.014374 | 0.0065923 | 0.062782 | 0.045559 | -0.017729 | 0.024844 | -0.0038709 | -0.086975 | -0.050354 | -0.027466 | 0.032043 | 0.17395 | 0.009155 | 0.1236 | 1.0162 | 122.1954 | -0.068665 | 122.1817 | 0.2243 | 0.16479 | 0.17853 | 0.022888 | -122.3145 | -122.2321 | 0.2243 | 0.17395 | 0.059509 | 0.15106 | 0.036621 | -0.018311 | -0.068664 | -0.082397 | 0.27466 | 0.22888 | 0.21515 | 0.24719 | 0.23346 | 0.20142 | 0.059509 | 0.29297 | 122.2504 | -0.022888 | 122.2641 | 0 | 122.2458 | -122.2916 | -122.3328 | 0.082397 | 122.2321 | -0.036621 | 1.0666
3987.9688 | 122.3602 | -0.082397 | 122.2824 | -0.12032 | -0.041107 | 0.001523 | 0.0255 | -0.00020513 | -0.012666 | -0.0017325 | -0.12906 | 0.0065923 | 0.064918 | 0.053036 | -0.017088 | 0.028049 | -0.0036573 | -0.07782 | -0.018311 | -0.041199 | -0.036621 | 0.054932 | -0.09613 | 0.004578 | 0.86517 | 122.2412 | -0.073242 | 122.081 | 0.073242 | -0.004578 | 0.064087 | 0.041198 | -122.3007 | -122.319 | 0.13733 | 0.086975 | -0.013733 | 0.045777 | -0.054931 | 0.009155 | -0.041199 | -0.20142 | 0.15564 | 0.14648 | 0.077819 | 0.13733 | 0.068664 | 0.096131 | 0.004578 | 0.14648 | 122.1542 | 0.022888 | 122.3145 | 0.064086 | 122.3236 | -122.3236 | -122.3557 | 0.045776 | 122.1634 | 0.004577 | 0.94757
3989.6562 | 122.4655 | -0.059509 | 122.2778 | -0.10506 | -0.043885 | -0.00082677 | 0.019946 | -0.0027685 | -0.010102 | -0.0064321 | 0.011322 | 0.0059515 | 0.063636 | 0.04855 | -0.017729 | 0.02634 | -0.0053661 | -0.068665 | -0.059509 | -0.027466 | 0.041199 | 0.14648 | 0.013733 | 0.086975 | 1.0071 | 122.2183 | -0.059509 | 122.1542 | 0.19226 | 0.13275 | 0.16022 | 0.032043 | -122.3373 | -122.2366 | 0.20599 | 0.14648 | 0.073242 | 0.11444 | 0.041199 | 0 | -0.059509 | -0.1236 | 0.25177 | 0.21973 | 0.19226 | 0.21973 | 0.19226 | 0.17395 | 0.068665 | 0.25177 | 122.2137 | -0.032043 | 122.2778 | 0 | 122.2778 | -122.3053 | -122.3373 | 0.10071 | 122.2137 | -0.009156 | 1.0666
3991.4062 | 122.4747 | -0.064087 | 122.2504 | -0.20424 | -0.042389 | 0.0010958 | 0.020587 | -0.0051183 | -0.012025 | -0.0064321 | -0.0069885 | 0.0063787 | 0.064277 | 0.045987 | -0.019224 | 0.027621 | -0.0057935 | -0.086975 | -0.032043 | -0.009155 | 0.009155 | 0.10529 | -0.009155 | 0.086975 | 0.93384 | 122.2 | -0.068665 | 122.1588 | 0.1831 | 0.14648 | 0.14648 | 0.054932 | -122.2824 | -122.2412 | 0.16937 | 0.15106 | 0.054932 | 0.09613 | 0 | -0.004578 | -0.050354 | -0.091553 | 0.24719 | 0.21057 | 0.21057 | 0.21515 | 0.21515 | 0.11444 | 0.01831 | 0.25177 | 122.2275 | -0.022888 | 122.2687 | 0.032044 | 122.2641 | -122.2595 | -122.319 | 0.073242 | 122.2229 | -0.022888 | 0.99792
3993.1094 | 122.4701 | -0.045776 | 122.2412 | -0.12794 | -0.042176 | 0.0025912 | 0.02315 | 0.0021447 | -0.009675 | -0.0042959 | -0.089386 | 0.0055243 | 0.061927 | 0.04385 | -0.017515 | 0.026981 | -0.00088011 | -0.073242 | -0.041199 | -0.013733 | 0.022888 | 0.10986 | -0.032043 | 0.073242 | 0.85602 | 122.2046 | -0.064087 | 122.1817 | 0.16479 | 0.10071 | 0.17853 | 0.032043 | -122.2824 | -122.2183 | 0.15564 | 0.11902 | 0.013733 | 0.086975 | -0.01831 | -0.018311 | -0.036621 | -0.059509 | 0.21057 | 0.2243 | 0.14648 | 0.24261 | 0.1648 | 0.1236 | 0.036621 | 0.22888 | 122.2458 | -0.027466 | 122.2687 | 0.004577 | 122.2504 | -122.2549 | -122.3053 | 0.068664 | 122.2275 | -0.027466 | 0.90179
3994.8281 | 122.3419 | -0.086975 | 122.2687 | -0.18135 | -0.041962 | 0.0023776 | 0.0255 | 0.00022207 | -0.01117 | -0.0032277 | -0.11685 | 0.0061651 | 0.062782 | 0.047055 | -0.01901 | 0.028049 | -0.0079297 | -0.13275 | 0.004578 | -0.054932 | -0.10986 | -0.050354 | -0.18768 | -0.050354 | 0.72784 | 122.2458 | -0.09613 | 122.0627 | 0.022888 | -0.059509 | 0.041199 | 0.032043 | -122.2641 | -122.3785 | 0.036621 | 0.036621 | -0.10071 | 0.004578 | -0.13275 | -0.009155 | -0.022888 | -0.20599 | 0.10986 | 0.12817 | 0.027466 | 0.13733 | 0.036621 | 0.004578 | -0.054931 | 0.11902 | 122.1588 | 0.05951 | 122.3419 | 0.091553 | 122.3328 | -122.3236 | -122.3648 | -0.022888 | 122.1497 | -0.045776 | 0.81482
3996.5938 | 122.3419 | -0.09613 | 122.2733 | -0.16609 | -0.04068 | 0.00024143 | 0.024646 | 0.0032129 | -0.0088206 | -0.0034415 | -0.11685 | 0.0048833 | 0.064277 | 0.050046 | -0.018369 | 0.027621 | -0.00066651 | -0.15564 | 0.009155 | -0.050354 | -0.10529 | -0.045776 | -0.16479 | -0.045776 | 0.72327 | 122.287 | -0.10986 | 122.0627 | 0.036621 | -0.036621 | 0.050354 | 0.045776 | -122.2641 | -122.3785 | 0.050354 | 0.050354 | -0.068665 | 0.004578 | -0.11444 | -0.013733 | 0.013733 | -0.21057 | 0.13275 | 0.14648 | 0.059509 | 0.16022 | 0.073242 | 0.004578 | -0.054932 | 0.14648 | 122.1725 | 0.059509 | 122.3969 | 0.10528 | 122.3831 | -122.3236 | -122.3831 | -0.009156 | 122.1588 | -0.05951 | 0.8194
3998.3438 | 122.374 | -0.086975 | 122.2733 | -0.15846 | -0.041535 | 0.0010958 | 0.025927 | 0.00086307 | -0.010743 | -0.0038687 | -0.077179 | 0.0059515 | 0.06385 | 0.045346 | -0.018369 | 0.027408 | -0.0075025 | -0.10071 | -0.018311 | -0.041199 | -0.036621 | 0.050354 | -0.10529 | -0.004578 | 0.89264 | 122.2458 | -0.09613 | 122.0856 | 0.073242 | 0 | 0.068665 | 0.045776 | -122.2916 | -122.3099 | 0.13733 | 0.082397 | -0.018311 | 0.036621 | -0.064087 | -0.009155 | -0.027465 | -0.18768 | 0.16022 | 0.15564 | 0.086975 | 0.16479 | 0.09613 | 0.091553 | 0.004578 | 0.16937 | 122.1817 | 0.022888 | 122.3419 | 0.068664 | 122.3328 | -122.3145 | -122.3694 | 0.050354 | 122.1725 | -0.013733 | 0.97961
4000.0469 | 122.3373 | -0.10071 | 122.2961 | -0.1432 | -0.04303 | 0.003873 | 0.024218 | -0.0023413 | -0.010102 | -0.0030141 | -0.1077 | 0.0057379 | 0.064063 | 0.050046 | -0.017301 | 0.028903 | -0.0032299 | -0.1236 | 0.004578 | -0.059509 | -0.086975 | -0.032043 | -0.15564 | -0.041199 | 0.74616 | 122.2412 | -0.10071 | 122.0535 | 0.009155 | -0.045776 | 0.041199 | 0.041199 | -122.2916 | -122.3831 | 0.068665 | 0.059509 | -0.054932 | 0.01831 | -0.096131 | 0 | -0.054932 | -0.24262 | 0.10986 | 0.14191 | 0.054932 | 0.14191 | 0.054932 | 0.027466 | -0.027466 | 0.10986 | 122.1542 | 0.064087 | 122.3419 | 0.10529 | 122.3419 | -122.3557 | -122.3969 | 0.013733 | 122.1542 | -0.022888 | 0.84686
4001.75 | 122.4335 | -0.059509 | 122.2458 | -0.16609 | -0.044098 | 0.00088223 | 0.019519 | -0.0031957 | -0.010957 | -0.0030141 | -0.01004 | 0.0068059 | 0.061286 | 0.044919 | -0.017088 | 0.025485 | -0.0051525 | -0.11902 | -0.045776 | -0.036621 | -0.036621 | 0.086975 | -0.064087 | 0.050354 | 0.82398 | 122.2046 | -0.082397 | 122.1039 | 0.11902 | 0.073242 | 0.1236 | 0.022888 | -122.2916 | -122.2824 | 0.14648 | 0.10986 | -0.004578 | 0.086975 | -0.027466 | -0.022888 | -0.041199 | -0.14191 | 0.17853 | 0.1831 | 0.13275 | 0.20599 | 0.15564 | 0.1236 | 0 | 0.20142 | 122.1863 | -0.009155 | 122.287 | 0.013733 | 122.2641 | -122.2824 | -122.3282 | 0.022888 | 122.1634 | -0.05951 | 0.88348
4003.4531 | 122.3831 | -0.09613 | 122.2595 | -0.16609 | -0.044312 | -0.0016812 | 0.021228 | 0.0010767 | -0.009675 | -0.0049367 | -0.028351 | 0.0042425 | 0.062782 | 0.045773 | -0.016874 | 0.025058 | -0.0051525 | -0.073242 | -0.036621 | -0.018311 | -0.018311 | 0.09613 | -0.013733 | 0.068665 | 0.94757 | 122.2229 | -0.091553 | 122.0627 | 0.091553 | 0.022888 | 0.059509 | 0.077819 | -122.2961 | -122.2778 | 0.19226 | 0.16479 | 0.082397 | 0.086976 | 0.004578 | 0.004577 | -0.036621 | -0.19684 | 0.18768 | 0.15564 | 0.11902 | 0.15106 | 0.11444 | 0.11444 | 0 | 0.18311 | 122.1542 | -0.01831 | 122.3145 | 0.059509 | 122.319 | -122.2778 | -122.3511 | 0.077819 | 122.1588 | 0.022888 | 1.0437
4005.2188 | 122.3785 | -0.086975 | 122.2641 | -0.12794 | -0.042389 | 0.00045503 | 0.022509 | -0.00041873 | -0.010957 | -0.0036551 | -0.074127 | 0.0078741 | 0.064063 | 0.040005 | -0.018797 | 0.026553 | -0.0083569 | -0.14648 | -0.004578 | -0.045776 | -0.086975 | -0.004578 | -0.09613 | -0.009155 | 0.86517 | 122.2595 | -0.091553 | 122.0718 | 0.068665 | -0.004578 | 0.059509 | 0.041199 | -122.2687 | -122.3511 | 0.082397 | 0.07782 | -0.009155 | 0.036621 | -0.050354 | -0.004578 | -0.004578 | -0.19226 | 0.15564 | 0.14648 | 0.082397 | 0.15106 | 0.086975 | 0.041198 | -0.041199 | 0.16022 | 122.1634 | 0.041198 | 122.3511 | 0.082397 | 122.3465 | -122.3099 | -122.3557 | 0 | 122.1588 | -0.059509 | 0.95215
4006.9844 | 122.4197 | -0.073242 | 122.2412 | -0.18898 | -0.041107 | 0.002164 | 0.021869 | -0.0038367 | -0.010743 | -0.0032277 | -0.019196 | 0.0055243 | 0.063636 | 0.045773 | -0.018583 | 0.027408 | -0.0081433 | -0.11444 | -0.032043 | -0.027466 | -0.041199 | 0.064087 | -0.059509 | 0.041199 | 0.83313 | 122.1954 | -0.073242 | 122.113 | 0.12817 | 0.073242 | 0.10529 | 0.045776 | -122.2733 | -122.2824 | 0.13733 | 0.11444 | 0.013733 | 0.068665 | -0.032043 | 0 | -0.045776 | -0.12817 | 0.20142 | 0.17853 | 0.14648 | 0.17853 | 0.14648 | 0.091553 | -0.013733 | 0.20142 | 122.1863 | -0.004577 | 122.2687 | 0.041199 | 122.2687 | -122.2687 | -122.3145 | 0.032043 | 122.1863 | -0.041199 | 0.90637
4008.7344 | 122.4335 | -0.054932 | 122.2504 | -0.18898 | -0.044525 | 0.002164 | 0.022082 | -0.0042639 | -0.012025 | -0.0038687 | -0.016144 | 0.0072333 | 0.064918 | 0.049191 | -0.017515 | 0.027621 | -0.0032299 | -0.10529 | -0.032043 | -0.018311 | -0.036621 | 0.059509 | -0.064087 | 0.027466 | 0.87433 | 122.2 | -0.082397 | 122.113 | 0.15106 | 0.09613 | 0.11902 | 0.036621 | -122.2824 | -122.287 | 0.11444 | 0.082398 | -0.009155 | 0.045777 | -0.045776 | -0.027465 | -0.050354 | -0.13733 | 0.20599 | 0.17395 | 0.15106 | 0.20142 | 0.17853 | 0.07782 | -0.01831 | 0.23346 | 122.1954 | -0.013732 | 122.2824 | 0.022889 | 122.2549 | -122.2687 | -122.3328 | 0.018311 | 122.168 | -0.050354 | 0.92926
4011.7656 | 122.438 | -0.064087 | 122.2549 | -0.17372 | -0.044525 | 0.0025912 | 0.0208 | -0.0034095 | -0.010316 | -0.0032277 | -0.019196 | 0.0055243 | 0.06385 | 0.046414 | -0.017729 | 0.025058 | -0.0053661 | -0.1236 | -0.036621 | -0.036621 | -0.018311 | 0.068665 | -0.045776 | 0.064087 | 0.90637 | 122.1954 | -0.07782 | 122.1313 | 0.15564 | 0.11444 | 0.13733 | 0.027466 | -122.2916 | -122.2733 | 0.13275 | 0.12817 | 0.018311 | 0.10071 | -0.009155 | -0.013733 | -0.059509 | -0.1236 | 0.21973 | 0.20142 | 0.17853 | 0.21515 | 0.19226 | 0.10529 | 0.01831 | 0.23346 | 122.2092 | 0 | 122.2733 | 0.027466 | 122.2595 | -122.2916 | -122.3328 | 0.045776 | 122.1954 | -0.059509 | 0.97046
4014.4531 | 122.3785 | -0.086975 | 122.2595 | -0.15846 | -0.040039 | 0.002164 | 0.024005 | 0.0025721 | -0.010102 | -0.0055777 | -0.12601 | 0.0076605 | 0.061714 | 0.052182 | -0.01901 | 0.025485 | -0.0010937 | -0.11902 | 0 | -0.045776 | -0.091553 | -0.022888 | -0.14191 | -0.022888 | 0.75989 | 122.2321 | -0.10529 | 122.0856 | 0.068665 | -0.022888 | 0.064087 | 0.041199 | -122.2595 | -122.3511 | 0.064087 | 0.064087 | -0.054932 | 0.022888 | -0.096131 | -0.018311 | -0.027465 | -0.17395 | 0.15564 | 0.15106 | 0.064087 | 0.16937 | 0.082398 | 0.022888 | -0.045777 | 0.17395 | 122.1909 | 0.045776 | 122.3373 | 0.086975 | 122.319 | -122.3053 | -122.3648 | -0.004578 | 122.1725 | -0.032044 | 0.84686
4018.125 | 122.3602 | -0.086975 | 122.287 | -0.15083 | -0.043885 | 0.00045503 | 0.023578 | -0.0021277 | -0.011811 | -0.0032277 | -0.074127 | 0.0072333 | 0.062568 | 0.045773 | -0.018369 | 0.028903 | -0.0032299 | -0.14191 | -0.009155 | -0.054932 | -0.10071 | -0.004578 | -0.1236 | -0.018311 | 0.88806 | 122.2504 | -0.10529 | 122.0398 | 0.068665 | 0.004578 | 0.045776 | 0.032043 | -122.2961 | -122.3877 | 0.082397 | 0.068664 | -0.036621 | 0.036621 | -0.068664 | -0.018311 | -0.036621 | -0.24719 | 0.15564 | 0.13275 | 0.091553 | 0.15106 | 0.10986 | 0.050354 | -0.045776 | 0.17395 | 122.1451 | 0.045777 | 122.3557 | 0.07782 | 122.3373 | -122.3419 | -122.3923 | -0.013733 | 122.1268 | -0.054932 | 0.97504
4023.4375 | 122.3419 | -0.086975 | 122.2595 | -0.13557 | -0.041748 | 0.0023776 | 0.024646 | 0.0032129 | -0.01053 | -0.0045095 | -0.10159 | 0.0063787 | 0.06385 | 0.053677 | -0.017729 | 0.028476 | -0.0021619 | -0.10986 | -0.009155 | -0.054932 | -0.082397 | 0.004578 | -0.15564 | -0.032043 | 0.79193 | 122.2458 | -0.10071 | 122.0535 | 0.032043 | -0.036621 | 0.045776 | 0.032043 | -122.2687 | -122.3419 | 0.091553 | 0.054932 | -0.068665 | 0.022889 | -0.10071 | -0.013733 | -0.013732 | -0.20599 | 0.11902 | 0.13275 | 0.050354 | 0.14648 | 0.064087 | 0.05951 | -0.027465 | 0.13275 | 122.1542 | 0.045777 | 122.3465 | 0.07782 | 122.3328 | -122.3145 | -122.3602 | 0.004578 | 122.1405 | -0.022888 | 0.87891
4025.2188 | 122.4472 | -0.068665 | 122.2366 | -0.1432 | -0.042816 | 0.00045503 | 0.021869 | -0.0034095 | -0.012239 | -0.00066434 | 0.0082703 | 0.0061651 | 0.063423 | 0.051541 | -0.01666 | 0.027194 | -0.0077161 | -0.07782 | -0.036621 | -0.027466 | 0.041199 | 0.16479 | 0.004578 | 0.091553 | 1.0529 | 122.1909 | -0.073242 | 122.1542 | 0.19684 | 0.14191 | 0.14648 | 0.041199 | -122.2733 | -122.1954 | 0.23346 | 0.16022 | 0.073243 | 0.11902 | 0.032044 | -0.004577 | -0.045776 | -0.082397 | 0.2655 | 0.21515 | 0.21057 | 0.21973 | 0.21515 | 0.19226 | 0.068665 | 0.27008 | 122.2275 | -0.009155 | 122.2641 | 0.032044 | 122.2595 | -122.2641 | -122.3099 | 0.10986 | 122.2229 | -0.009155 | 1.1215
4026.9219 | 122.438 | -0.054932 | 122.2733 | -0.17372 | -0.041535 | 2.7834e-05 | 0.022723 | 0.0015039 | -0.012025 | -0.0070731 | -0.052765 | 0.0070197 | 0.063209 | 0.041287 | -0.016874 | 0.027621 | -0.0064343 | -0.10529 | -0.027466 | -0.027466 | -0.032043 | 0.059509 | -0.059509 | 0.036621 | 0.86517 | 122.2092 | -0.07782 | 122.1085 | 0.13733 | 0.059509 | 0.10529 | 0.027466 | -122.3007 | -122.3053 | 0.11444 | 0.091553 | -0.004577 | 0.064087 | -0.032043 | -0.022888 | -0.064087 | -0.16479 | 0.19226 | 0.16022 | 0.11444 | 0.18311 | 0.13733 | 0.086975 | -0.004577 | 0.21515 | 122.1863 | 0 | 122.287 | 0.027466 | 122.2641 | -122.3007 | -122.3511 | 0.022889 | 122.1634 | -0.050354 | 0.9201
4028.6719 | 122.4106 | -0.07782 | 122.2778 | -0.11269 | -0.046021 | 0.0019504 | 0.020587 | 0.00022207 | -0.012452 | -0.0049367 | -0.040558 | 0.0074469 | 0.062995 | 0.047268 | -0.017942 | 0.027194 | -0.010066 | -0.064087 | -0.041199 | -0.027466 | 0.022888 | 0.14191 | 0.004578 | 0.086975 | 1.0529 | 122.2046 | -0.086975 | 122.1451 | 0.16937 | 0.10986 | 0.13733 | 0.050354 | -122.319 | -122.2549 | 0.21973 | 0.16479 | 0.082398 | 0.11444 | 0.032044 | -0.009155 | -0.073242 | -0.13275 | 0.24719 | 0.21515 | 0.18768 | 0.2243 | 0.19684 | 0.16937 | 0.050354 | 0.25635 | 122.2321 | -0.013733 | 122.2916 | 0.036621 | 122.2824 | -122.3053 | -122.3648 | 0.10071 | 122.2229 | 0.013733 | 1.1307
4030.4375 | 122.3785 | -0.068665 | 122.2778 | -0.11269 | -0.041321 | 0.001523 | 0.024646 | 0.0051355 | -0.01117 | -0.0051505 | -0.12296 | 0.0070197 | 0.061927 | 0.046628 | -0.018583 | 0.026553 | -0.0064343 | -0.082397 | -0.009155 | -0.045776 | -0.022888 | 0.054932 | -0.082397 | 0.018311 | 0.91553 | 122.2137 | -0.086975 | 122.1039 | 0.10529 | 0.027466 | 0.082397 | 0.022889 | -122.287 | -122.3007 | 0.1236 | 0.086976 | -0.013732 | 0.064087 | -0.036621 | -0.01831 | -0.064087 | -0.17395 | 0.17395 | 0.15106 | 0.096131 | 0.16937 | 0.11444 | 0.10071 | 0.022888 | 0.19226 | 122.1909 | 0.036621 | 122.3007 | 0.05951 | 122.2824 | -122.3236 | -122.3648 | 0.045777 | 122.1725 | -0.013732 | 0.98419
4032.2188 | 122.3511 | -0.086975 | 122.2778 | -0.11269 | -0.045166 | 0.00024143 | 0.022082 | -0.0012731 | -0.0094614 | -0.0049367 | -0.06192 | 0.0033881 | 0.0662 | 0.039792 | -0.018583 | 0.027408 | -0.0019483 | -0.14191 | 0.009155 | -0.054932 | -0.10071 | -0.009155 | -0.11902 | -0.018311 | 0.9201 | 122.2321 | -0.10529 | 122.0306 | 0.054932 | -0.009155 | 0.032043 | 0.032043 | -122.2687 | -122.3785 | 0.07782 | 0.068664 | -0.032044 | 0.036621 | -0.064087 | -0.018311 | -0.045776 | -0.24719 | 0.14191 | 0.11902 | 0.07782 | 0.13733 | 0.096131 | 0.045777 | -0.045776 | 0.16022 | 122.1359 | 0.064087 | 122.3373 | 0.09613 | 122.319 | -122.3328 | -122.3831 | -0.013733 | 122.1176 | -0.054932 | 1.0071
4033.9219 | 122.4701 | -0.054932 | 122.2549 | -0.1432 | -0.043457 | 0.00066863 | 0.020373 | -0.0017005 | -0.012239 | -0.0013051 | 0.0021667 | 0.0057379 | 0.064277 | 0.049191 | -0.018797 | 0.026767 | -0.0075025 | -0.064087 | -0.041199 | -0.009155 | 0.041199 | 0.15564 | 0.032043 | 0.09613 | 1.0574 | 122.2137 | -0.086975 | 122.1542 | 0.20142 | 0.14191 | 0.16022 | 0.045777 | -122.2961 | -122.2137 | 0.21057 | 0.15106 | 0.086975 | 0.10528 | 0.041198 | -0.032043 | -0.041199 | -0.10071 | 0.25635 | 0.21515 | 0.19684 | 0.24719 | 0.22888 | 0.16479 | 0.050354 | 0.28839 | 122.2412 | -0.032044 | 122.3007 | 0.013733 | 122.2687 | -122.2641 | -122.3419 | 0.096131 | 122.2092 | -0.009155 | 1.1124
4035.6094 | 122.3923 | -0.07782 | 122.2641 | -0.13557 | -0.041107 | 0.0010958 | 0.023791 | -0.00063233 | -0.010102 | -0.0053641 | -0.11685 | 0.0074469 | 0.062568 | 0.045132 | -0.018369 | 0.028476 | -0.0070751 | -0.14648 | -0.004578 | -0.068665 | -0.086975 | 0.004578 | -0.13733 | -0.018311 | 0.76446 | 122.2412 | -0.082397 | 122.0947 | 0.07782 | 0.004578 | 0.086975 | 0.009155 | -122.2687 | -122.3511 | 0.082398 | 0.059509 | -0.059509 | 0.050354 | -0.068664 | -0.004577 | -0.022888 | -0.16937 | 0.15564 | 0.16479 | 0.082398 | 0.16937 | 0.086975 | 0.073243 | -0.01831 | 0.16022 | 122.1771 | 0.064087 | 122.3236 | 0.073242 | 122.319 | -122.3328 | -122.3465 | -0.009155 | 122.1725 | -0.068664 | 0.84228
4037.375 | 122.3969 | -0.073242 | 122.2733 | -0.18135 | -0.041962 | 0.00066863 | 0.021441 | 0.0015039 | -0.010743 | -0.0066457 | -0.12601 | 0.0078741 | 0.062141 | 0.053677 | -0.01666 | 0.028476 | -0.0051525 | -0.091553 | -0.009155 | -0.050354 | -0.032043 | 0.045776 | -0.07782 | 0.022888 | 0.93842 | 122.2412 | -0.07782 | 122.1085 | 0.1236 | 0.036621 | 0.082397 | 0.022888 | -122.2824 | -122.3053 | 0.11902 | 0.09613 | -0.004578 | 0.073242 | -0.027466 | -0.004578 | -0.032043 | -0.16479 | 0.19684 | 0.15564 | 0.10986 | 0.16022 | 0.11444 | 0.09613 | 0.018311 | 0.20142 | 122.1863 | 0.041199 | 122.319 | 0.064087 | 122.3145 | -122.3236 | -122.3511 | 0.041199 | 122.1817 | -0.018311 | 1.0117
4039.1562 | 122.438 | -0.045776 | 122.2549 | -0.17372 | -0.042603 | 0.0034456 | 0.022509 | -0.0025549 | -0.0090342 | -0.0034415 | -0.098541 | 0.0057379 | 0.062568 | 0.051755 | -0.01666 | 0.027194 | -0.0077161 | -0.10529 | -0.004578 | -0.045776 | -0.050354 | 0.045776 | -0.10986 | 0.013733 | 0.83313 | 122.1909 | -0.086975 | 122.1542 | 0.15106 | 0.073242 | 0.16022 | 0 | -122.2595 | -122.3053 | 0.091552 | 0.059509 | -0.064087 | 0.059509 | -0.064087 | -0.041199 | -0.064087 | -0.10071 | 0.19684 | 0.20599 | 0.11902 | 0.24719 | 0.16022 | 0.091552 | -0.004578 | 0.23804 | 122.2412 | 0.041198 | 122.2778 | 0.041198 | 122.2366 | -122.3007 | -122.3419 | -0.004578 | 122.2 | -0.05951 | 0.87891
4040.875 | 122.3694 | -0.10529 | 122.2824 | -0.17372 | -0.042816 | 0.0023776 | 0.022937 | 0.0021447 | -0.011811 | -0.0047231 | -0.086334 | 0.0065923 | 0.065132 | 0.044491 | -0.015165 | 0.027621 | -0.0040845 | -0.13275 | 0.004578 | -0.050354 | -0.10071 | -0.009155 | -0.14648 | -0.032043 | 0.77362 | 122.2458 | -0.11444 | 122.0764 | 0.059509 | -0.018311 | 0.054932 | 0.054932 | -122.2778 | -122.3831 | 0.096131 | 0.073243 | -0.041198 | 0.018311 | -0.09613 | -0.009155 | -0.036621 | -0.20599 | 0.16479 | 0.16022 | 0.086975 | 0.16937 | 0.09613 | 0.041199 | -0.050354 | 0.17395 | 122.1909 | 0.054932 | 122.3602 | 0.10986 | 122.3511 | -122.3328 | -122.3969 | 0.004578 | 122.1817 | -0.027465 | 0.87891
4042.6406 | 122.3465 | -0.10071 | 122.2824 | -0.15846 | -0.039826 | 0.0013094 | 0.025073 | 8.47e-06 | -0.010316 | -0.0055777 | -0.098541 | 0.0068059 | 0.064063 | 0.047696 | -0.017088 | 0.02634 | -0.0072889 | -0.14191 | 0.018311 | -0.064087 | -0.09613 | -0.027466 | -0.16022 | -0.059509 | 0.75073 | 122.2641 | -0.10529 | 122.049 | 0.022888 | -0.041199 | 0.050354 | 0.036621 | -122.2641 | -122.3785 | 0.073242 | 0.041199 | -0.059509 | 0.004578 | -0.09613 | -0.004578 | -0.018311 | -0.23346 | 0.1236 | 0.15106 | 0.059509 | 0.15564 | 0.064087 | 0.036621 | -0.032043 | 0.12817 | 122.1542 | 0.082398 | 122.3694 | 0.11902 | 122.3648 | -122.3465 | -122.3877 | 0.004578 | 122.1497 | -0.041199 | 0.85144
4044.3438 | 122.4655 | -0.045776 | 122.2687 | -0.17372 | -0.044953 | 0.0013094 | 0.018237 | 0.0049219 | -0.012239 | -0.0047231 | 0.0052185 | 0.0050971 | 0.064063 | 0.038724 | -0.019224 | 0.026553 | -0.0062207 | -0.050354 | -0.045776 | -0.013733 | 0.045776 | 0.16937 | 0.013733 | 0.10986 | 1.0757 | 122.1863 | -0.064087 | 122.1588 | 0.21057 | 0.15564 | 0.16937 | 0.032043 | -122.3145 | -122.2229 | 0.21515 | 0.15564 | 0.059509 | 0.1236 | 0.027466 | -0.018311 | -0.082398 | -0.10986 | 0.25635 | 0.21515 | 0.20142 | 0.23346 | 0.21973 | 0.18311 | 0.059509 | 0.27466 | 122.2229 | -0.032043 | 122.2504 | 0 | 122.2321 | -122.2824 | -122.3328 | 0.091552 | 122.2046 | -0.004578 | 1.1215
4046.1094 | 122.4335 | -0.068665 | 122.2641 | -0.15846 | -0.041962 | -0.0025358 | 0.019946 | -0.0042639 | -0.011384 | -0.0015189 | -0.016144 | 0.0070197 | 0.062141 | 0.037869 | -0.017942 | 0.02634 | -0.0034435 | -0.068665 | -0.036621 | -0.022888 | 0.013733 | 0.12817 | 0.004578 | 0.10529 | 1.0529 | 122.2183 | -0.068665 | 122.1268 | 0.16022 | 0.091553 | 0.1236 | 0.045777 | -122.3007 | -122.2504 | 0.19684 | 0.17395 | 0.073243 | 0.12817 | 0.027466 | 0 | -0.045776 | -0.13733 | 0.22888 | 0.19226 | 0.16022 | 0.19226 | 0.16022 | 0.15106 | 0.036621 | 0.22888 | 122.1954 | -0.013733 | 122.287 | 0.032044 | 122.287 | -122.287 | -122.3328 | 0.082398 | 122.1954 | 0 | 1.1215
4047.7969 | 122.3969 | -0.07782 | 122.2549 | -0.16609 | -0.04303 | 0.0025912 | 0.022082 | 0.0042811 | -0.010316 | -0.0030141 | -0.09549 | 0.0053107 | 0.0615 | 0.052395 | -0.017729 | 0.025485 | -0.0032299 | -0.13275 | 0.022888 | -0.032043 | -0.082397 | 0.004578 | -0.14191 | -0.022888 | 0.7782 | 122.2229 | -0.082397 | 122.1085 | 0.07782 | 0.009155 | 0.07782 | 0.045777 | -122.2321 | -122.3373 | 0.082398 | 0.054932 | -0.064087 | 0.009155 | -0.10986 | -0.004577 | -0.032044 | -0.14648 | 0.15564 | 0.15564 | 0.086975 | 0.16022 | 0.091552 | 0.036621 | -0.050354 | 0.16022 | 122.1909 | 0.054931 | 122.3053 | 0.10071 | 122.3007 | -122.287 | -122.3373 | -0.004577 | 122.1863 | -0.054931 | 0.85602
4049.5625 | 122.3282 | -0.091553 | 122.2961 | -0.1432 | -0.043244 | 0.00045503 | 0.022296 | -0.0021277 | -0.010102 | -0.0023733 | -0.046661 | 0.0044561 | 0.063423 | 0.048123 | -0.017301 | 0.025912 | -0.0042981 | -0.14648 | 0 | -0.045776 | -0.086975 | 0.013733 | -0.11444 | -0.004578 | 0.93842 | 122.2595 | -0.10986 | 122.0169 | 0.054932 | -0.009155 | 0.013733 | 0.045777 | -122.2961 | -122.3831 | 0.10529 | 0.086975 | -0.022888 | 0.041198 | -0.068665 | -0.01831 | -0.036622 | -0.27924 | 0.14649 | 0.10529 | 0.082398 | 0.1236 | 0.10071 | 0.059509 | -0.041199 | 0.16479 | 122.1268 | 0.045776 | 122.3694 | 0.091553 | 122.3511 | -122.3419 | -122.406 | 0.004578 | 122.1085 | -0.054931 | 1.03
4051.3281 | 122.3602 | -0.10071 | 122.2778 | -0.1432 | -0.041748 | 0.0036594 | 0.024859 | 0.00022207 | -0.0088206 | -0.0036551 | -0.086334 | 0.0057379 | 0.063636 | 0.054532 | -0.018583 | 0.027408 | -0.00088011 | -0.14648 | -0.009155 | -0.041199 | -0.10986 | -0.050354 | -0.17395 | -0.045776 | 0.76904 | 122.2366 | -0.10986 | 122.0535 | 0.041199 | -0.045776 | 0.054932 | 0.059509 | -122.287 | -122.3877 | 0.050354 | 0.054932 | -0.073242 | -0.004577 | -0.13275 | -0.009155 | -0.041199 | -0.2243 | 0.14191 | 0.15564 | 0.054932 | 0.16479 | 0.064087 | -0.009155 | -0.068664 | 0.15106 | 122.1634 | 0.032044 | 122.3465 | 0.091553 | 122.3373 | -122.319 | -122.3877 | -0.009155 | 122.1542 | -0.045776 | 0.86975
4053.0938 | 122.4609 | -0.054932 | 122.2824 | -0.12794 | -0.042816 | 0.0034456 | 0.019305 | 0.00022207 | -0.013307 | -0.0036551 | -0.0069885 | 0.0061651 | 0.060645 | 0.045987 | -0.017942 | 0.024631 | -0.0036573 | -0.086975 | -0.050354 | -0.018311 | 0.036621 | 0.16022 | 0.009155 | 0.10529 | 1.0712 | 122.2 | -0.068665 | 122.1634 | 0.19226 | 0.14191 | 0.16022 | 0.036621 | -122.3328 | -122.2458 | 0.21515 | 0.16022 | 0.064087 | 0.1236 | 0.027466 | -0.013733 | -0.082398 | -0.11902 | 0.24719 | 0.21515 | 0.19684 | 0.22888 | 0.21057 | 0.17853 | 0.054932 | 0.26093 | 122.2321 | -0.032043 | 122.2687 | 0.004578 | 122.2549 | -122.3007 | -122.3511 | 0.091553 | 122.2183 | -0.032043 | 1.1261
4054.7812 | 122.3511 | -0.082397 | 122.2778 | -0.19661 | -0.042603 | 0.001523 | 0.023791 | 0.00086307 | -0.011384 | -0.0030141 | -0.11075 | 0.0061651 | 0.064277 | 0.047482 | -0.020719 | 0.028476 | -0.0072889 | -0.13733 | 0.018311 | -0.050354 | -0.10529 | -0.041199 | -0.15564 | -0.041199 | 0.75531 | 122.2458 | -0.11444 | 122.0581 | 0.041199 | -0.045776 | 0.045776 | 0.032043 | -122.2595 | -122.3831 | 0.041198 | 0.041198 | -0.073243 | 0.009155 | -0.10529 | -0.032044 | -0.032043 | -0.21973 | 0.1236 | 0.12817 | 0.036621 | 0.16022 | 0.068665 | 0.009155 | -0.054932 | 0.15564 | 122.1725 | 0.068665 | 122.3602 | 0.10071 | 122.3282 | -122.3282 | -122.3923 | -0.022889 | 122.1405 | -0.054932 | 0.83771
4056.5625 | 122.4197 | -0.064087 | 122.2595 | -0.15083 | -0.043457 | 0.0019504 | 0.021014 | 8.47e-06 | -0.0092478 | -0.0028005 | -0.013092 | 0.0059515 | 0.065132 | 0.045773 | -0.018583 | 0.025699 | -0.00045291 | -0.11902 | -0.018311 | -0.018311 | -0.032043 | 0.068665 | -0.082397 | 0.041199 | 0.88348 | 122.2092 | -0.082397 | 122.1085 | 0.13275 | 0.07782 | 0.10986 | 0.045776 | -122.2778 | -122.2916 | 0.13275 | 0.10529 | -0.01831 | 0.05951 | -0.064086 | -0.01831 | -0.050354 | -0.15106 | 0.19684 | 0.17395 | 0.14191 | 0.19226 | 0.16022 | 0.086976 | -0.013732 | 0.21515 | 122.1909 | 0 | 122.2916 | 0.045776 | 122.2733 | -122.2778 | -122.3419 | 0.032044 | 122.1725 | -0.054932 | 0.94757
4058.3281 | 122.4792 | -0.045776 | 122.2321 | -0.22713 | -0.040467 | 0.001523 | 0.024005 | -0.0021277 | -0.010957 | -0.0075003 | -0.058869 | 0.0048833 | 0.061073 | 0.048977 | -0.019224 | 0.025272 | -0.0053661 | -0.041199 | -0.032043 | 0.009155 | 0.032043 | 0.12817 | -0.041199 | 0.07782 | 0.94299 | 122.1771 | -0.07782 | 122.1771 | 0.17395 | 0.11444 | 0.16937 | 0.054931 | -122.2641 | -122.2 | 0.17395 | 0.1236 | 0.004577 | 0.068665 | -0.050354 | -0.032044 | -0.054932 | -0.054932 | 0.21973 | 0.21515 | 0.16022 | 0.24719 | 0.19226 | 0.11902 | 0.022888 | 0.25177 | 122.2549 | -0.041198 | 122.2549 | 0.013733 | 122.2229 | -122.2229 | -122.3099 | 0.077819 | 122.2229 | 0.004577 | 0.98877
4060.0938 | 122.3557 | -0.086975 | 122.319 | -0.12794 | -0.042389 | 0.002164 | 0.023791 | -0.0040503 | -0.012239 | -0.0055777 | -0.068024 | 0.0057379 | 0.063423 | 0.049405 | -0.017729 | 0.026553 | -0.0032299 | -0.14648 | 0.004578 | -0.068665 | -0.10986 | -0.009155 | -0.11902 | -0.004578 | 0.9201 | 122.2458 | -0.10529 | 122.0444 | 0.054932 | -0.004578 | 0.027466 | 0.01831 | -122.3145 | -122.4289 | 0.07782 | 0.082397 | -0.032044 | 0.064087 | -0.050354 | -0.018311 | -0.073242 | -0.27466 | 0.14191 | 0.11444 | 0.082397 | 0.13275 | 0.10071 | 0.05951 | -0.041198 | 0.16022 | 122.1497 | 0.073243 | 122.3511 | 0.091553 | 122.3328 | -122.3877 | -122.4243 | -0.022888 | 122.1313 | -0.059509 | 1.0071
4061.7969 | 122.4884 | -0.07782 | 122.2504 | -0.16609 | -0.046234 | -0.00039957 | 0.020373 | -0.00041873 | -0.010316 | -0.0064321 | 0.0021667 | 0.0070197 | 0.062568 | 0.038937 | -0.017088 | 0.026126 | -0.0049389 | -0.073242 | -0.045776 | -0.027466 | 0.036621 | 0.15564 | 0.013733 | 0.11902 | 1.0712 | 122.1863 | -0.054932 | 122.1863 | 0.21057 | 0.15564 | 0.17853 | 0.050354 | -122.2961 | -122.2137 | 0.23346 | 0.19684 | 0.091553 | 0.14649 | 0.041199 | 0.022888 | -0.064087 | -0.064087 | 0.28839 | 0.25635 | 0.23346 | 0.23346 | 0.21057 | 0.18311 | 0.064087 | 0.2655 | 122.2412 | -0.01831 | 122.2412 | 0.032044 | 122.2641 | -122.2778 | -122.3053 | 0.11444 | 122.2641 | 0.004578 | 1.149
4063.5938 | 122.4106 | -0.068665 | 122.2504 | -0.20424 | -0.045807 | 0.00045503 | 0.022509 | -0.0027685 | -0.010743 | -0.0057913 | -0.034454 | 0.0057379 | 0.061286 | 0.041073 | -0.015806 | 0.024844 | -0.0047253 | -0.1236 | -0.045776 | -0.018311 | -0.022888 | 0.068665 | -0.073242 | 0.050354 | 0.88348 | 122.1817 | -0.086975 | 122.113 | 0.13275 | 0.059509 | 0.09613 | 0.050354 | -122.2961 | -122.2733 | 0.13733 | 0.11902 | -0.004577 | 0.068665 | -0.054931 | -0.01831 | -0.068664 | -0.13733 | 0.20142 | 0.16479 | 0.12817 | 0.1831 | 0.14648 | 0.086976 | -0.004577 | 0.21973 | 122.2 | -0.027465 | 122.2687 | 0.022889 | 122.2504 | -122.2687 | -122.3373 | 0.045777 | 122.1817 | -0.054931 | 0.95215
4065.3906 | 122.4014 | -0.041199 | 122.2549 | -0.18898 | -0.042176 | 0.0028048 | 0.022509 | 8.47e-06 | -0.0098886 | -0.0068593 | -0.034454 | 0.0063787 | 0.063209 | 0.049191 | -0.017515 | 0.02634 | -0.0066479 | -0.07782 | -0.041199 | -0.009155 | 0.004578 | 0.11902 | -0.064087 | 0.050354 | 0.89722 | 122.2321 | -0.059509 | 122.1313 | 0.13275 | 0.07782 | 0.1236 | 0.032044 | -122.2961 | -122.2504 | 0.16022 | 0.091553 | -0.022888 | 0.059509 | -0.054932 | -0.01831 | -0.022888 | -0.1236 | 0.17395 | 0.16479 | 0.11902 | 0.1831 | 0.13733 | 0.12817 | 0.013733 | 0.19226 | 122.1909 | -0.032044 | 122.2916 | 0 | 122.2733 | -122.2641 | -122.3145 | 0.045777 | 122.1725 | -0.036621 | 0.93842
4067.1406 | 122.3602 | -0.10529 | 122.2961 | -0.082169 | -0.045594 | -0.00018577 | 0.024005 | -0.0038367 | -0.01352 | -0.0032277 | -0.10464 | 0.0050971 | 0.064491 | 0.04855 | -0.018583 | 0.027194 | -0.0049389 | -0.13275 | 0.004578 | -0.059509 | -0.082397 | -0.027466 | -0.11444 | -0.018311 | 0.9201 | 122.2687 | -0.10986 | 122.0535 | 0.068665 | -0.009155 | 0.045776 | 0.045777 | -122.2916 | -122.3785 | 0.07782 | 0.086975 | -0.009155 | 0.041198 | -0.054932 | -0.004577 | -0.027466 | -0.24262 | 0.17395 | 0.15106 | 0.096131 | 0.15564 | 0.10071 | 0.032043 | -0.022888 | 0.17853 | 122.1634 | 0.064087 | 122.3785 | 0.10986 | 122.374 | -122.3557 | -122.406 | 0.022889 | 122.1588 | -0.027465 | 1.0254
4068.8438 | 122.4243 | -0.050354 | 122.2549 | -0.18135 | -0.043671 | 0.0017368 | 0.02315 | -0.0014867 | -0.0090342 | -0.0040823 | -0.01004 | 0.0061651 | 0.060432 | 0.044491 | -0.017515 | 0.02634 | -0.0042981 | -0.10986 | -0.022888 | -0.036621 | -0.022888 | 0.082397 | -0.059509 | 0.036621 | 0.86975 | 122.2183 | -0.082397 | 122.113 | 0.11902 | 0.091553 | 0.11902 | 0.013733 | -122.2778 | -122.2778 | 0.13275 | 0.086975 | -0.009155 | 0.073242 | -0.022888 | -0.032043 | -0.036621 | -0.14191 | 0.16937 | 0.16937 | 0.14191 | 0.20142 | 0.17395 | 0.11902 | 0.013733 | 0.20142 | 122.1954 | 0.013733 | 122.3007 | 0.027466 | 122.2687 | -122.2916 | -122.3373 | 0.027466 | 122.1634 | -0.059509 | 0.92011
4070.6094 | 122.4701 | -0.054932 | 122.2549 | -0.15846 | -0.044098 | 0.00066863 | 0.022937 | -0.00063233 | -0.010957 | -0.0049367 | 0.0021667 | 0.0057379 | 0.061927 | 0.042142 | -0.018583 | 0.025699 | -0.0053661 | -0.073242 | -0.045776 | -0.013733 | 0.041199 | 0.15564 | 0.013733 | 0.11444 | 1.0895 | 122.1954 | -0.082397 | 122.1497 | 0.20599 | 0.14648 | 0.15564 | 0.041199 | -122.3007 | -122.2137 | 0.21057 | 0.16937 | 0.068665 | 0.12817 | 0.027466 | -0.027465 | -0.059509 | -0.10529 | 0.26093 | 0.21057 | 0.20142 | 0.23804 | 0.22888 | 0.16937 | 0.054932 | 0.28839 | 122.2321 | -0.032043 | 122.2778 | 0.009156 | 122.2504 | -122.2687 | -122.3373 | 0.096131 | 122.2046 | -0.01831 | 1.1444
4072.375 | 122.3969 | -0.073242 | 122.2687 | -0.18898 | -0.041107 | 0.00024143 | 0.022937 | 0.0015039 | -0.010957 | -0.0038687 | -0.12601 | 0.0076605 | 0.063423 | 0.053677 | -0.017301 | 0.026126 | -0.0053661 | -0.086975 | -0.013733 | -0.054932 | -0.032043 | 0.045776 | -0.086975 | -0.004578 | 0.97961 | 122.2321 | -0.082397 | 122.1039 | 0.12817 | 0.027466 | 0.09613 | 0.01831 | -122.2824 | -122.3007 | 0.11902 | 0.068664 | -0.013733 | 0.050354 | -0.032043 | -0.009155 | -0.036621 | -0.16479 | 0.20142 | 0.16937 | 0.10071 | 0.17853 | 0.10986 | 0.10071 | 0.022889 | 0.21057 | 122.1863 | 0.041199 | 122.3145 | 0.059509 | 122.3053 | -122.3236 | -122.3511 | 0.041199 | 122.1771 | -0.013733 | 1.0529
4074.1562 | 122.3648 | -0.082397 | 122.2549 | -0.12032 | -0.041748 | 0.00024143 | 0.024218 | 0.0019311 | -0.012452 | -0.0038687 | -0.12601 | 0.0063787 | 0.061073 | 0.044705 | -0.017515 | 0.026553 | -0.0034435 | -0.091553 | -0.004578 | -0.036621 | -0.027466 | 0.050354 | -0.09613 | 0.009155 | 0.95215 | 122.2549 | -0.082397 | 122.0856 | 0.11444 | 0.009155 | 0.091553 | 0.045776 | -122.2595 | -122.2824 | 0.13275 | 0.091552 | -0.013733 | 0.045776 | -0.059509 | 0 | 0 | -0.16937 | 0.19684 | 0.17395 | 0.091552 | 0.17395 | 0.091552 | 0.086975 | 0.009155 | 0.19684 | 122.168 | 0.032043 | 122.3373 | 0.077819 | 122.3373 | -122.2916 | -122.3373 | 0.054931 | 122.168 | -0.009156 | 1.0345
4075.8594 | 122.493 | -0.064087 | 122.2412 | -0.15083 | -0.044953 | 0.001523 | 0.019305 | -0.0031957 | -0.010102 | -0.0040823 | -0.022247 | 0.0063787 | 0.061927 | 0.045346 | -0.017301 | 0.02634 | -0.0089977 | -0.091553 | -0.027466 | -0.022888 | 0.009155 | 0.1236 | 0 | 0.09613 | 1.03 | 122.2183 | -0.086975 | 122.1817 | 0.21057 | 0.13733 | 0.16479 | 0.041199 | -122.2687 | -122.2321 | 0.18768 | 0.16022 | 0.064087 | 0.11902 | 0.022888 | -0.022888 | -0.022888 | -0.059509 | 0.27466 | 0.22888 | 0.20142 | 0.25177 | 0.2243 | 0.14648 | 0.032043 | 0.29755 | 122.2687 | -0.004578 | 122.3053 | 0.036621 | 122.2824 | -122.2641 | -122.3282 | 0.073242 | 122.2458 | -0.027466 | 1.0941
4077.625 | 122.3557 | -0.09613 | 122.2778 | -0.17372 | -0.040894 | 0.0043002 | 0.022723 | -0.0031957 | -0.01053 | -0.0028005 | -0.11685 | 0.0057379 | 0.062568 | 0.054318 | -0.01901 | 0.02869 | -0.0047253 | -0.10071 | -0.018311 | -0.054932 | -0.050354 | 0.041199 | -0.10071 | -0.009155 | 0.91553 | 122.2595 | -0.09613 | 122.0718 | 0.054932 | -0.045776 | 0.036621 | 0.041198 | -122.2961 | -122.3282 | 0.13733 | 0.086975 | -0.004578 | 0.045777 | -0.045776 | 0 | -0.018311 | -0.20599 | 0.15106 | 0.13275 | 0.050354 | 0.13275 | 0.050354 | 0.096131 | 0.004578 | 0.15106 | 122.168 | 0.036621 | 122.3557 | 0.077819 | 122.3557 | -122.3328 | -122.374 | 0.045776 | 122.168 | -0.004578 | 1.0117
4079.3906 | 122.3465 | -0.10529 | 122.2595 | -0.074539 | -0.042603 | 2.7834e-05 | 0.021228 | -0.0019141 | -0.010957 | -0.0040823 | -0.055817 | 0.0059515 | 0.061714 | 0.046414 | -0.017729 | 0.027194 | -0.0055799 | -0.15106 | 0.018311 | -0.073242 | -0.091553 | 0.004578 | -0.10986 | -0.013733 | 0.94757 | 122.2458 | -0.11444 | 122.0215 | 0.054932 | -0.009155 | 0.018311 | 0.032044 | -122.2412 | -122.3511 | 0.10986 | 0.091553 | -0.004577 | 0.059509 | -0.036621 | -0.009155 | -0.013732 | -0.23804 | 0.16022 | 0.1236 | 0.096131 | 0.13275 | 0.10529 | 0.07782 | -0.018311 | 0.16937 | 122.1359 | 0.091553 | 122.3602 | 0.1236 | 122.3511 | -122.3328 | -122.374 | 0.013733 | 122.1268 | -0.045776 | 1.0529
4081.2031 | 122.4747 | -0.045776 | 122.2275 | -0.20424 | -0.041748 | 0.0025912 | 0.021655 | 0.0012903 | -0.01053 | -0.0047231 | -0.071076 | 0.0063787 | 0.062995 | 0.048977 | -0.017942 | 0.025272 | -0.0025891 | -0.050354 | -0.045776 | 0 | 0.032043 | 0.13275 | -0.036621 | 0.073242 | 0.93842 | 122.2046 | -0.050354 | 122.1909 | 0.19226 | 0.11444 | 0.16479 | 0.045776 | -122.2733 | -122.1954 | 0.17853 | 0.11902 | 0.009155 | 0.073242 | -0.036621 | -0.004578 | -0.022888 | -0.036621 | 0.23804 | 0.21057 | 0.16022 | 0.21515 | 0.16479 | 0.13275 | 0.032043 | 0.24261 | 122.2412 | -0.045776 | 122.2549 | 0 | 122.2504 | -122.2275 | -122.2778 | 0.077819 | 122.2366 | -0.004578 | 0.98419
4082.9844 | 122.3282 | -0.091553 | 122.2916 | -0.18135 | -0.043244 | 0.0060092 | 0.024859 | -0.0025549 | -0.01053 | -0.0070731 | -0.12296 | 0.0074469 | 0.064063 | 0.049618 | -0.017088 | 0.027408 | -0.0040845 | -0.11444 | 0.004578 | -0.036621 | -0.082397 | -0.032043 | -0.16022 | -0.054932 | 0.81024 | 122.2549 | -0.11444 | 122.0444 | 0.032043 | -0.045776 | 0.027466 | 0.054932 | -122.287 | -122.374 | 0.05951 | 0.036621 | -0.068664 | -0.018311 | -0.1236 | -0.022888 | -0.036621 | -0.24719 | 0.1236 | 0.11902 | 0.045777 | 0.14191 | 0.068665 | 0.004578 | -0.045776 | 0.14648 | 122.1588 | 0.041199 | 122.3694 | 0.096131 | 122.3465 | -122.3282 | -122.406 | 0.009156 | 122.1359 | -0.022888 | 0.9018
4084.7031 | 122.4289 | -0.054932 | 122.2733 | -0.25002 | -0.044739 | 0.0028048 | 0.020373 | 0.00043587 | -0.011384 | -0.0049367 | -0.022247 | 0.0023199 | 0.063636 | 0.044278 | -0.018156 | 0.025912 | -0.0057935 | -0.11902 | -0.018311 | -0.036621 | -0.009155 | 0.07782 | -0.054932 | 0.045776 | 0.90179 | 122.2046 | -0.073242 | 122.1176 | 0.13275 | 0.064087 | 0.12817 | 0.018311 | -122.2916 | -122.2824 | 0.13275 | 0.10071 | 0 | 0.082397 | -0.018311 | -0.01831 | -0.068664 | -0.15564 | 0.18768 | 0.18311 | 0.11902 | 0.20142 | 0.13733 | 0.11444 | 0.027466 | 0.20599 | 122.1909 | 0.01831 | 122.2778 | 0.036621 | 122.2595 | -122.3099 | -122.3465 | 0.045777 | 122.1725 | -0.064087 | 0.95673
4086.4219 | 122.3923 | -0.11902 | 122.2733 | -0.12032 | -0.04303 | 0.00066863 | 0.020587 | 0.0015039 | -0.01117 | -0.0034415 | -0.086334 | 0.0070197 | 0.062782 | 0.0462 | -0.016874 | 0.027408 | -0.0062207 | -0.11902 | 0.004578 | -0.050354 | -0.054932 | 0.013733 | -0.091553 | -0.004578 | 0.96588 | 122.2504 | -0.10071 | 122.1039 | 0.10986 | 0.027466 | 0.091553 | 0.068665 | -122.2687 | -122.3282 | 0.13275 | 0.11444 | 0.027466 | 0.045776 | -0.041199 | 0.018311 | -0.022888 | -0.16937 | 0.22888 | 0.21057 | 0.14649 | 0.19226 | 0.12817 | 0.064087 | -0.004578 | 0.21057 | 122.2046 | 0.054932 | 122.3511 | 0.1236 | 122.3694 | -122.3236 | -122.374 | 0.064087 | 122.2229 | 0 | 1.0849
4088.1719 | 122.4747 | -0.054932 | 122.1954 | -0.24239 | -0.041107 | 0.0019504 | 0.022723 | 0.0027857 | -0.0083932 | -0.0040823 | -0.055817 | 0.0044561 | 0.061073 | 0.046628 | -0.017942 | 0.02634 | -0.0070751 | -0.054932 | -0.027466 | -0.004578 | 0.013733 | 0.11902 | -0.032043 | 0.068665 | 0.93842 | 122.1954 | -0.050354 | 122.1817 | 0.16937 | 0.10986 | 0.17853 | 0.050354 | -122.2229 | -122.1817 | 0.17395 | 0.1236 | 0.022889 | 0.073243 | -0.027465 | 0.004578 | 0 | -0.013733 | 0.22431 | 0.23346 | 0.16479 | 0.22888 | 0.16022 | 0.1236 | 0.018311 | 0.21973 | 122.2321 | -0.022888 | 122.2458 | 0.027466 | 122.2504 | -122.2 | -122.2458 | 0.068665 | 122.2366 | 0 | 0.99335
4089.875 | 122.438 | -0.07782 | 122.2412 | -0.16609 | -0.04303 | -0.00039957 | 0.022723 | -0.0025549 | -0.011598 | -0.0030141 | -0.031403 | 0.0076605 | 0.064704 | 0.047909 | -0.017729 | 0.025699 | -0.0021619 | -0.11902 | -0.027466 | -0.036621 | -0.027466 | 0.07782 | -0.059509 | 0.041199 | 0.93384 | 122.2046 | -0.07782 | 122.1268 | 0.14648 | 0.10529 | 0.11902 | 0.041199 | -122.2687 | -122.2687 | 0.15564 | 0.11902 | 0.018311 | 0.07782 | -0.022888 | 0 | -0.036621 | -0.11444 | 0.2243 | 0.19684 | 0.18311 | 0.19684 | 0.18311 | 0.11444 | 0.009155 | 0.2243 | 122.2046 | 0.009155 | 122.2824 | 0.050354 | 122.2824 | -122.2778 | -122.319 | 0.050354 | 122.2046 | -0.041199 | 1.0117
4091.625 | 122.3877 | -0.082397 | 122.2824 | -0.12794 | -0.044312 | 0.001523 | 0.020587 | -0.0010595 | -0.011384 | -0.0034415 | -0.049713 | 0.0068059 | 0.064918 | 0.043637 | -0.017729 | 0.02869 | -0.0085705 | -0.082397 | -0.041199 | -0.036621 | -0.013733 | 0.091553 | -0.022888 | 0.054932 | 1.0208 | 122.2504 | -0.091553 | 122.0764 | 0.10071 | 0.050354 | 0.073242 | 0.045776 | -122.3236 | -122.2961 | 0.17395 | 0.13733 | 0.059509 | 0.091553 | 0.013733 | -0.009156 | -0.032044 | -0.20599 | 0.18311 | 0.15564 | 0.13275 | 0.16479 | 0.14191 | 0.12817 | 0.022888 | 0.19226 | 122.168 | -0.004578 | 122.3419 | 0.041198 | 122.3328 | -122.319 | -122.374 | 0.068664 | 122.1588 | 0 | 1.1032
4093.3281 | 122.3877 | -0.10071 | 122.2687 | -0.17372 | -0.042816 | 0.00088223 | 0.023791 | 0.00022207 | -0.012452 | -0.0049367 | -0.11075 | 0.0063787 | 0.065132 | 0.048337 | -0.018583 | 0.028049 | -0.0049389 | -0.13733 | 0.004578 | -0.064087 | -0.091553 | -0.009155 | -0.14648 | -0.027466 | 0.83771 | 122.2641 | -0.10529 | 122.0764 | 0.064087 | -0.009155 | 0.059509 | 0.036621 | -122.2641 | -122.3602 | 0.091553 | 0.073242 | -0.045776 | 0.036621 | -0.082397 | -0.004578 | -0.004578 | -0.19226 | 0.1648 | 0.16022 | 0.091553 | 0.16479 | 0.096131 | 0.054932 | -0.027466 | 0.16937 | 122.1817 | 0.068665 | 122.3694 | 0.10529 | 122.3648 | -122.3328 | -122.374 | 0.009155 | 122.1771 | -0.036621 | 0.93842
4095.0312 | 122.4426 | -0.059509 | 122.2916 | -0.16609 | -0.043244 | 0.00066863 | 0.021014 | -0.0023413 | -0.0092478 | -0.0028005 | -0.028351 | 0.0050971 | 0.06385 | 0.0462 | -0.019865 | 0.025699 | -0.0055799 | -0.07782 | -0.036621 | -0.018311 | 0.036621 | 0.14191 | 0.004578 | 0.09613 | 1.0941 | 122.1863 | -0.082397 | 122.1359 | 0.17853 | 0.1236 | 0.14648 | 0.041198 | -122.3282 | -122.2549 | 0.20142 | 0.15564 | 0.064087 | 0.11444 | 0.022889 | -0.022888 | -0.10529 | -0.15564 | 0.23804 | 0.20599 | 0.1831 | 0.22888 | 0.20599 | 0.16022 | 0.054932 | 0.26092 | 122.2183 | -0.01831 | 122.2687 | 0.022888 | 122.2458 | -122.3099 | -122.374 | 0.09613 | 122.1954 | -0.018311 | 1.1536
4096.7188 | 122.3602 | -0.10529 | 122.2733 | -0.22713 | -0.042603 | 0.002164 | 0.024005 | 0.00086307 | -0.010743 | -0.0032277 | -0.11075 | 0.0046697 | 0.059577 | 0.050046 | -0.01901 | 0.026767 | -0.0066479 | -0.13275 | 0.013733 | -0.059509 | -0.09613 | -0.009155 | -0.15106 | -0.027466 | 0.82398 | 122.2733 | -0.10071 | 122.0764 | 0.050354 | -0.013733 | 0.068665 | 0.045777 | -122.2595 | -122.3694 | 0.096131 | 0.07782 | -0.045776 | 0.032043 | -0.091553 | 0.004578 | 0 | -0.19684 | 0.15564 | 0.17395 | 0.091553 | 0.16937 | 0.086975 | 0.050354 | -0.036621 | 0.15106 | 122.1771 | 0.073242 | 122.374 | 0.11902 | 122.3785 | -122.3328 | -122.374 | 0.009156 | 122.1817 | -0.027465 | 0.92926
4098.4219 | 122.4838 | -0.068665 | 122.2504 | -0.12032 | -0.044953 | -0.00018577 | 0.02315 | -0.0029821 | -0.012879 | -0.0032277 | -0.013092 | 0.0061651 | 0.063423 | 0.045773 | -0.01666 | 0.025699 | -0.0068615 | -0.07782 | -0.041199 | -0.022888 | 0.027466 | 0.16479 | 0.004578 | 0.11902 | 1.0941 | 122.1909 | -0.068665 | 122.1817 | 0.24261 | 0.16937 | 0.17395 | 0.045777 | -122.2916 | -122.2229 | 0.23346 | 0.18768 | 0.073243 | 0.14191 | 0.027466 | 0 | -0.059509 | -0.068664 | 0.31128 | 0.24261 | 0.23804 | 0.24261 | 0.23804 | 0.18768 | 0.050354 | 0.31128 | 122.2504 | -0.018311 | 122.2595 | 0.027466 | 122.2595 | -122.2733 | -122.319 | 0.096131 | 122.2504 | -0.009155 | 1.1627
4100.125 | 122.374 | -0.086975 | 122.287 | -0.19661 | -0.042389 | 0.00088223 | 0.023364 | -0.0021277 | -0.011384 | -0.0047231 | -0.12296 | 0.0078741 | 0.062354 | 0.057736 | -0.018156 | 0.027408 | -0.0049389 | -0.086975 | -0.004578 | -0.050354 | -0.036621 | 0.050354 | -0.068665 | 0.009155 | 1.0025 | 122.2183 | -0.082397 | 122.1039 | 0.1236 | 0.036621 | 0.10071 | 0.036621 | -122.2916 | -122.3236 | 0.13733 | 0.09613 | 0.01831 | 0.059509 | -0.018311 | 0.004578 | -0.068664 | -0.1831 | 0.21057 | 0.18768 | 0.1236 | 0.18311 | 0.11902 | 0.10071 | 0.013733 | 0.20599 | 122.1863 | 0.045776 | 122.3007 | 0.082397 | 122.3053 | -122.3373 | -122.3694 | 0.050354 | 122.1909 | 0 | 1.0895
4101.8281 | 122.4838 | -0.050354 | 122.2504 | -0.15846 | -0.044312 | 2.7834e-05 | 0.019519 | -0.0010595 | -0.012239 | -0.0062185 | -0.01004 | 0.0044561 | 0.062995 | 0.0509 | -0.016447 | 0.026553 | -0.0051525 | -0.054932 | -0.045776 | -0.027466 | 0.036621 | 0.16022 | 0.013733 | 0.10071 | 1.1032 | 122.2092 | -0.054932 | 122.1542 | 0.2243 | 0.16022 | 0.16022 | 0.022888 | -122.2961 | -122.2137 | 0.21057 | 0.15106 | 0.064087 | 0.12817 | 0.041199 | -0.004578 | -0.041199 | -0.09613 | 0.27466 | 0.21057 | 0.21057 | 0.21515 | 0.21515 | 0.18768 | 0.064087 | 0.27924 | 122.2092 | -0.01831 | 122.2641 | 0.004578 | 122.2595 | -122.2778 | -122.3053 | 0.086975 | 122.2046 | -0.004578 | 1.1536
4103.5781 | 122.4518 | -0.050354 | 122.2458 | -0.21187 | -0.041748 | 0.0030184 | 0.021869 | 0.0012903 | -0.0098886 | -0.0070731 | -0.071076 | 0.0074469 | 0.065345 | 0.046628 | -0.020078 | 0.025912 | -0.0068615 | -0.050354 | -0.041199 | -0.009155 | 0.036621 | 0.13275 | -0.032043 | 0.07782 | 0.97504 | 122.1817 | -0.068665 | 122.1863 | 0.17853 | 0.10529 | 0.16022 | 0.041199 | -122.287 | -122.2092 | 0.18311 | 0.12817 | 0.018311 | 0.086975 | -0.022888 | -0.018311 | -0.064087 | -0.05951 | 0.22888 | 0.21057 | 0.15564 | 0.22888 | 0.17395 | 0.14191 | 0.045776 | 0.24719 | 122.2549 | -0.032044 | 122.2504 | 0.009155 | 122.2321 | -122.2549 | -122.3145 | 0.086975 | 122.2366 | 0 | 1.0254
4105.2812 | 122.3648 | -0.09613 | 122.2733 | -0.13557 | -0.04538 | -0.0010404 | 0.021014 | -0.0038367 | -0.012025 | -0.0028005 | -0.09549 | 0.0078741 | 0.064491 | 0.046414 | -0.018369 | 0.026553 | -0.0077161 | -0.13733 | 0 | -0.064087 | -0.09613 | -0.013733 | -0.11902 | -0.018311 | 0.9613 | 122.2595 | -0.10986 | 122.0535 | 0.059509 | 0 | 0.059509 | 0.032043 | -122.2733 | -122.3694 | 0.082397 | 0.077819 | -0.022889 | 0.045776 | -0.054932 | -0.013733 | -0.013733 | -0.21973 | 0.15564 | 0.15564 | 0.09613 | 0.16937 | 0.10986 | 0.050354 | -0.032043 | 0.16937 | 122.1634 | 0.064087 | 122.3694 | 0.09613 | 122.3557 | -122.3373 | -122.3831 | 0 | 122.1497 | -0.041199 | 1.0574
4106.9844 | 122.4609 | -0.045776 | 122.2549 | -0.13557 | -0.044525 | 2.7834e-05 | 0.022723 | 0.00022207 | -0.010743 | -0.0025869 | -0.025299 | 0.0061651 | 0.063636 | 0.047909 | -0.018369 | 0.026981 | -0.0038709 | -0.068665 | -0.032043 | -0.009155 | 0.036621 | 0.14648 | 0.009155 | 0.091553 | 1.1032 | 122.2046 | -0.082397 | 122.1405 | 0.1831 | 0.1236 | 0.14648 | 0.036621 | -122.287 | -122.2183 | 0.19226 | 0.13733 | 0.054931 | 0.10071 | 0.01831 | -0.036621 | -0.050354 | -0.11444 | 0.22888 | 0.19226 | 0.16937 | 0.22888 | 0.20599 | 0.15564 | 0.045776 | 0.2655 | 122.2229 | -0.022888 | 122.287 | 0.013733 | 122.2504 | -122.2641 | -122.3373 | 0.082397 | 122.1863 | -0.022889 | 1.149
4108.6875 | 122.3511 | -0.09613 | 122.2687 | -0.13557 | -0.04303 | 0.0023776 | 0.024218 | -0.0014867 | -0.0083932 | -0.0013051 | -0.14432 | 0.0065923 | 0.063423 | 0.052609 | -0.018156 | 0.027408 | -0.0072889 | -0.15106 | 0.009155 | -0.054932 | -0.091553 | -0.045776 | -0.16479 | -0.045776 | 0.81024 | 122.2366 | -0.10529 | 122.0673 | 0.022888 | -0.050354 | 0.045776 | 0.041198 | -122.2595 | -122.3602 | 0.050354 | 0.050354 | -0.068665 | 0.009156 | -0.10986 | -0.009156 | -0.032044 | -0.20142 | 0.11902 | 0.14191 | 0.045776 | 0.15106 | 0.054932 | 0.009156 | -0.036621 | 0.12817 | 122.1725 | 0.064087 | 122.3419 | 0.10528 | 122.3328 | -122.3236 | -122.374 | 0.004577 | 122.1634 | -0.054932 | 0.90637
4110.375 | 122.4564 | -0.054932 | 122.2458 | -0.16609 | -0.044312 | -0.00018577 | 0.020373 | -0.00041873 | -0.013093 | -0.0028005 | -0.013092 | 0.0068059 | 0.062568 | 0.047055 | -0.017088 | 0.025699 | -0.0064343 | -0.073242 | -0.041199 | -0.027466 | 0.041199 | 0.16022 | 0.018311 | 0.10986 | 1.1078 | 122.1954 | -0.068665 | 122.1588 | 0.20142 | 0.15106 | 0.15106 | 0.027466 | -122.287 | -122.2046 | 0.21515 | 0.16479 | 0.073243 | 0.13733 | 0.045777 | -0.013733 | -0.050354 | -0.086976 | 0.25635 | 0.20599 | 0.20599 | 0.21973 | 0.21973 | 0.18768 | 0.068665 | 0.27008 | 122.2275 | -0.013733 | 122.2641 | 0.013733 | 122.2504 | -122.2733 | -122.3145 | 0.096131 | 122.2137 | -0.01831 | 1.1627
4112.0781 | 122.4014 | -0.10986 | 122.287 | -0.13557 | -0.041748 | -0.00082677 | 0.022509 | -0.0029821 | -0.014802 | -0.0038687 | -0.080231 | 0.0080877 | 0.062995 | 0.039792 | -0.020292 | 0.027621 | -0.0079297 | -0.09613 | -0.009155 | -0.045776 | -0.036621 | 0.050354 | -0.082397 | 0.013733 | 1.0208 | 122.2229 | -0.082397 | 122.0993 | 0.11902 | 0.032043 | 0.086975 | 0.064087 | -122.2961 | -122.3236 | 0.16022 | 0.1236 | 0.027466 | 0.059509 | -0.036621 | 0.027466 | -0.064087 | -0.18768 | 0.22888 | 0.19684 | 0.14191 | 0.16937 | 0.11444 | 0.09613 | 0.009155 | 0.20142 | 122.1817 | 0.036621 | 122.3053 | 0.10071 | 122.3328 | -122.3328 | -122.3694 | 0.073242 | 122.2092 | 0.013733 | 1.1307
4113.7812 | 122.4655 | -0.045776 | 122.2183 | -0.2195 | -0.041962 | 0.0023776 | 0.022937 | 0.00043587 | -0.010316 | -0.0045095 | -0.046661 | 0.0050971 | 0.064491 | 0.04321 | -0.017515 | 0.028262 | -0.0038709 | -0.050354 | -0.032043 | -0.013733 | 0.032043 | 0.11902 | -0.041199 | 0.064087 | 0.96588 | 122.1954 | -0.054932 | 122.1725 | 0.18768 | 0.10529 | 0.1831 | 0.032043 | -122.2504 | -122.1863 | 0.16479 | 0.10986 | 0.004577 | 0.07782 | -0.027466 | -0.009156 | -0.022888 | -0.045777 | 0.23346 | 0.22888 | 0.15106 | 0.23804 | 0.16022 | 0.13275 | 0.045776 | 0.24261 | 122.2275 | -0.01831 | 122.2504 | 0.013733 | 122.2412 | -122.2321 | -122.2733 | 0.077819 | 122.2183 | -0.004578 | 1.0117
4115.5312 | 122.4152 | -0.068665 | 122.2412 | -0.16609 | -0.042389 | 0.003232 | 0.024432 | 0.0025721 | -0.010316 | -0.0053641 | -0.09549 | 0.0044561 | 0.063209 | 0.045132 | -0.019224 | 0.027621 | -0.010066 | -0.1236 | 0.009155 | -0.036621 | -0.07782 | 0.009155 | -0.13733 | -0.009155 | 0.88348 | 122.2321 | -0.10529 | 122.1176 | 0.10529 | 0.041199 | 0.10986 | 0.032044 | -122.2321 | -122.319 | 0.07782 | 0.05951 | -0.068664 | 0.027466 | -0.10071 | -0.036621 | -0.009155 | -0.1236 | 0.17395 | 0.17853 | 0.10986 | 0.21515 | 0.14649 | 0.045776 | -0.041199 | 0.21057 | 122.2229 | 0.045776 | 122.3373 | 0.07782 | 122.3007 | -122.2778 | -122.3465 | -0.009155 | 122.1863 | -0.054931 | 0.95215
4117.2344 | 122.4747 | -0.054932 | 122.2641 | -0.15846 | -0.044739 | 0.00045503 | 0.02016 | 0.00064947 | -0.011384 | -0.0028005 | 0.0021667 | 0.0068059 | 0.060859 | 0.049405 | -0.017088 | 0.025058 | -0.0079297 | -0.073242 | -0.036621 | -0.022888 | 0.036621 | 0.16022 | 0.013733 | 0.10986 | 1.1307 | 122.2229 | -0.073242 | 122.1542 | 0.20599 | 0.14648 | 0.16022 | 0.032044 | -122.3007 | -122.2275 | 0.21515 | 0.16479 | 0.068665 | 0.13275 | 0.036621 | -0.01831 | -0.041199 | -0.10986 | 0.26093 | 0.21515 | 0.20142 | 0.23346 | 0.21973 | 0.1831 | 0.059509 | 0.27924 | 122.2275 | -0.013733 | 122.2961 | 0.018311 | 122.2778 | -122.287 | -122.3373 | 0.091553 | 122.2092 | -0.01831 | 1.1856
4118.9375 | 122.3419 | -0.10529 | 122.2641 | -0.21187 | -0.043671 | 0.003873 | 0.024432 | 0.0036401 | -0.010102 | -0.0042959 | -0.1077 | 0.0087287 | 0.062354 | 0.044491 | -0.018369 | 0.027194 | -0.0049389 | -0.14191 | 0.009155 | -0.054932 | -0.09613 | -0.045776 | -0.15564 | -0.054932 | 0.83771 | 122.2595 | -0.10071 | 122.0627 | 0.018311 | -0.059509 | 0.036621 | 0.050354 | -122.2549 | -122.3602 | 0.05951 | 0.050354 | -0.050354 | 0 | -0.10071 | 0.004578 | -0.004578 | -0.20142 | 0.1236 | 0.14191 | 0.045777 | 0.13733 | 0.041199 | 0.009156 | -0.041198 | 0.11902 | 122.1634 | 0.064087 | 122.3602 | 0.11444 | 122.3648 | -122.319 | -122.3648 | 0.009156 | 122.168 | -0.036621 | 0.94299
4120.6406 | 122.4426 | -0.054932 | 122.2229 | -0.20424 | -0.041535 | 0.0028048 | 0.021869 | 0.00086307 | -0.008607 | -0.0028005 | -0.04361 | 0.0061651 | 0.064063 | 0.041928 | -0.01901 | 0.028476 | -0.0068615 | -0.059509 | -0.036621 | -0.022888 | 0.022888 | 0.14191 | -0.032043 | 0.059509 | 0.98877 | 122.2229 | -0.073242 | 122.1451 | 0.17395 | 0.10529 | 0.13733 | 0.032044 | -122.2595 | -122.2 | 0.19684 | 0.11444 | 0.022889 | 0.082397 | -0.009155 | -0.01831 | 0 | -0.077819 | 0.22888 | 0.19226 | 0.16022 | 0.21057 | 0.17853 | 0.16479 | 0.045776 | 0.24719 | 122.2183 | -0.013733 | 122.2961 | 0.018311 | 122.2778 | -122.2458 | -122.2961 | 0.07782 | 122.2 | -0.004577 | 1.0437
4122.3281 | 122.3923 | -0.086975 | 122.2824 | -0.13557 | -0.043671 | 0.001523 | 0.021014 | -0.0019141 | -0.011384 | -0.0032277 | -0.10159 | 0.0057379 | 0.061714 | 0.051327 | -0.018797 | 0.028049 | -0.0017347 | -0.09613 | -0.013733 | -0.054932 | -0.045776 | 0.041199 | -0.082397 | 0.004578 | 1.0345 | 122.2366 | -0.10986 | 122.0993 | 0.11444 | 0.036621 | 0.091553 | 0.032043 | -122.2961 | -122.3282 | 0.12817 | 0.091553 | 0.004578 | 0.05951 | -0.027465 | -0.022888 | -0.045777 | -0.18311 | 0.20142 | 0.17853 | 0.1236 | 0.20142 | 0.14648 | 0.096131 | 0.009156 | 0.2243 | 122.2092 | 0.041199 | 122.3465 | 0.073242 | 122.3236 | -122.3373 | -122.3923 | 0.041199 | 122.1863 | -0.009155 | 1.1215
4124.0312 | 122.4609 | -0.050354 | 122.2412 | -0.20424 | -0.042389 | 0.002164 | 0.021869 | -0.00084593 | -0.010957 | -0.0021597 | -0.040558 | 0.0059515 | 0.061286 | 0.047268 | -0.017515 | 0.028262 | -0.0017347 | -0.068665 | -0.045776 | -0.022888 | 0.041199 | 0.14191 | -0.036621 | 0.086975 | 0.99792 | 122.2046 | -0.068665 | 122.168 | 0.18768 | 0.11444 | 0.16937 | 0.027466 | -122.287 | -122.2 | 0.19226 | 0.13733 | 0.013733 | 0.10986 | -0.013733 | -0.018311 | -0.036621 | -0.073242 | 0.23804 | 0.21973 | 0.16479 | 0.23804 | 0.18311 | 0.16479 | 0.064087 | 0.25635 | 122.2366 | -0.022888 | 122.2733 | 0.004578 | 122.2549 | -122.2641 | -122.3099 | 0.091553 | 122.2183 | -0.018311 | 1.0483
4125.75 | 122.4747 | -0.050354 | 122.2275 | -0.15083 | -0.040253 | 0.0034456 | 0.022296 | 0.00022207 | -0.0092478 | -0.0042959 | -0.064972 | 0.0061651 | 0.062354 | 0.0462 | -0.020078 | 0.02634 | -0.0015209 | -0.09613 | -0.009155 | -0.036621 | 0.004578 | 0.11902 | -0.086975 | 0.068665 | 0.97504 | 122.2183 | -0.082397 | 122.1771 | 0.17395 | 0.09613 | 0.17395 | 0.013733 | -122.2366 | -122.2229 | 0.16937 | 0.11902 | -0.036621 | 0.10529 | -0.050354 | -0.032043 | -0.009155 | -0.050354 | 0.2243 | 0.2243 | 0.14648 | 0.25635 | 0.17853 | 0.15564 | 0.041199 | 0.25635 | 122.2595 | 0.027466 | 122.3007 | 0.041199 | 122.2687 | -122.2641 | -122.3099 | 0.054932 | 122.2275 | -0.045776 | 1.0254
4127.4375 | 122.3969 | -0.064087 | 122.2549 | -0.1432 | -0.041321 | 0.00024143 | 0.019091 | 0.00043587 | -0.01117 | -0.0055777 | -0.016144 | 0.0068059 | 0.062141 | 0.040433 | -0.018156 | 0.02634 | -0.0064343 | -0.11444 | -0.032043 | -0.022888 | -0.032043 | 0.073242 | -0.054932 | 0.041199 | 0.97961 | 122.2275 | -0.086975 | 122.113 | 0.13275 | 0.064087 | 0.10986 | 0.041199 | -122.287 | -122.287 | 0.13733 | 0.10529 | 0.009155 | 0.064087 | -0.032044 | -0.022888 | -0.027466 | -0.14191 | 0.19684 | 0.17395 | 0.12817 | 0.19684 | 0.15106 | 0.09613 | -0.009155 | 0.21973 | 122.2 | -0.009155 | 122.3145 | 0.032044 | 122.2916 | -122.2778 | -122.3419 | 0.032044 | 122.1771 | -0.050354 | 1.0437
4129.1406 | 122.4197 | -0.068665 | 122.2412 | -0.18135 | -0.042603 | 0.001523 | 0.020373 | 0.0015039 | -0.011384 | -0.0038687 | -0.019196 | 0.0061651 | 0.062141 | 0.046628 | -0.017515 | 0.025912 | -0.0049389 | -0.10529 | -0.041199 | -0.004578 | -0.022888 | 0.073242 | -0.059509 | 0.041199 | 0.96588 | 122.2046 | -0.073242 | 122.113 | 0.12817 | 0.073242 | 0.10986 | 0.064087 | -122.2824 | -122.2641 | 0.14191 | 0.10986 | 0.009156 | 0.045777 | -0.054931 | -0.004577 | -0.036621 | -0.12817 | 0.19684 | 0.17853 | 0.14191 | 0.18311 | 0.14648 | 0.07782 | -0.01831 | 0.20142 | 122.1863 | -0.036621 | 122.2778 | 0.027466 | 122.2733 | -122.2458 | -122.3145 | 0.045777 | 122.1817 | -0.036621 | 1.0345
4130.8281 | 122.374 | -0.11444 | 122.2733 | -0.097427 | -0.042816 | -0.00061317 | 0.025927 | 0.00022207 | -0.012239 | -0.0036551 | -0.086334 | 0.0074469 | 0.062782 | 0.050686 | -0.019651 | 0.028262 | -0.0017347 | -0.14191 | 0.013733 | -0.073242 | -0.082397 | -0.013733 | -0.11444 | -0.009155 | 1.0162 | 122.2549 | -0.10071 | 122.0901 | 0.091553 | 0.004578 | 0.068665 | 0.041199 | -122.2595 | -122.3557 | 0.10071 | 0.10529 | 0 | 0.064087 | -0.041199 | 0.013733 | -0.01831 | -0.1831 | 0.20599 | 0.18311 | 0.11902 | 0.16937 | 0.10529 | 0.059509 | -0.009155 | 0.19226 | 122.1909 | 0.086975 | 122.3557 | 0.12817 | 122.3694 | -122.3465 | -122.374 | 0.032044 | 122.2046 | -0.027466 | 1.1307
4132.5312 | 122.3923 | -0.07782 | 122.2504 | -0.18898 | -0.041748 | 0.00088223 | 0.022509 | 8.47e-06 | -0.01053 | -0.0057913 | -0.09549 | 0.0068059 | 0.06385 | 0.047055 | -0.01666 | 0.028049 | -0.0036573 | -0.1236 | 0.004578 | -0.059509 | -0.073242 | 0.013733 | -0.14191 | -0.013733 | 0.93384 | 122.2321 | -0.10071 | 122.0947 | 0.10529 | 0.036621 | 0.09613 | 0.018311 | -122.2458 | -122.3236 | 0.091553 | 0.064087 | -0.064087 | 0.045776 | -0.082398 | -0.022888 | -0.01831 | -0.15564 | 0.18311 | 0.17395 | 0.11444 | 0.19684 | 0.13733 | 0.073242 | -0.013733 | 0.20599 | 122.1954 | 0.064087 | 122.3328 | 0.082398 | 122.3099 | -122.3099 | -122.3511 | 0.004578 | 122.1725 | -0.045776 | 1.0117
4134.25 | 122.3923 | -0.09613 | 122.2733 | -0.13557 | -0.044312 | 0.0023776 | 0.022509 | -0.0017005 | -0.010957 | -0.0032277 | -0.09549 | 0.0072333 | 0.064704 | 0.053677 | -0.016447 | 0.027194 | -0.0042981 | -0.13275 | 0.009155 | -0.059509 | -0.041199 | 0.018311 | -0.082397 | 0.009155 | 1.0666 | 122.2321 | -0.082397 | 122.0856 | 0.10529 | 0.036621 | 0.073242 | 0.036621 | -122.2641 | -122.3145 | 0.11444 | 0.10528 | 0.013733 | 0.068664 | -0.022888 | 0.013733 | -0.041198 | -0.18768 | 0.20142 | 0.16937 | 0.13275 | 0.15564 | 0.11902 | 0.07782 | 0.01831 | 0.18768 | 122.168 | 0.068664 | 122.3145 | 0.10528 | 122.3282 | -122.3328 | -122.3557 | 0.054931 | 122.1817 | -0.036621 | 1.1627
4135.9375 | 122.4518 | -0.045776 | 122.2275 | -0.11269 | -0.04303 | 0.0017368 | 0.02016 | 0.00022207 | -0.010743 | -0.0030141 | -0.0069885 | 0.0061651 | 0.06385 | 0.048764 | -0.020292 | 0.025699 | -0.0064343 | -0.11444 | -0.018311 | -0.045776 | -0.013733 | 0.07782 | -0.045776 | 0.068665 | 1.0391 | 122.2321 | -0.10986 | 122.1405 | 0.15106 | 0.091553 | 0.14191 | 0 | -122.2458 | -122.2412 | 0.1236 | 0.11444 | 0 | 0.11444 | 0 | -0.064087 | 0.004578 | -0.086975 | 0.19684 | 0.18768 | 0.13733 | 0.25177 | 0.20142 | 0.1236 | 0.032043 | 0.26093 | 122.2504 | 0.027465 | 122.3419 | 0.027465 | 122.2778 | -122.2733 | -122.3373 | 0.032043 | 122.1863 | -0.068665 | 1.0849
4137.6406 | 122.4609 | -0.07782 | 122.2504 | -0.089798 | -0.043885 | 0.00024143 | 0.021441 | 0.0015039 | -0.011598 | -0.0036551 | -0.019196 | 0.0044561 | 0.062568 | 0.047909 | -0.017515 | 0.025912 | -0.0025891 | -0.073242 | -0.022888 | -0.013733 | 0.036621 | 0.13733 | 0.009155 | 0.10529 | 1.1948 | 122.2 | -0.073242 | 122.1451 | 0.1831 | 0.12817 | 0.15106 | 0.064087 | -122.2733 | -122.2137 | 0.21515 | 0.18311 | 0.086975 | 0.11902 | 0.022888 | 0.004578 | -0.050354 | -0.10528 | 0.26092 | 0.22888 | 0.20599 | 0.2243 | 0.20142 | 0.15106 | 0.050354 | 0.25635 | 122.2183 | -0.009155 | 122.2733 | 0.054932 | 122.2778 | -122.2641 | -122.3236 | 0.11444 | 122.2229 | 0.004578 | 1.2726
4139.3438 | 122.3328 | -0.10529 | 122.2824 | -0.19661 | -0.04068 | 0.0019504 | 0.024218 | 0.0019311 | -0.0092478 | -0.0040823 | -0.12601 | 0.0074469 | 0.062354 | 0.050259 | -0.018369 | 0.027835 | -0.0040845 | -0.11902 | 0.004578 | -0.045776 | -0.10529 | -0.013733 | -0.16479 | -0.045776 | 0.95673 | 122.2595 | -0.09613 | 122.049 | 0.027466 | -0.059509 | 0.041199 | 0.05951 | -122.2778 | -122.3877 | 0.091553 | 0.05951 | -0.059509 | 0 | -0.11902 | 0.009156 | -0.022889 | -0.23346 | 0.13275 | 0.14649 | 0.045777 | 0.13733 | 0.036621 | 0.032043 | -0.05951 | 0.1236 | 122.1451 | 0.050354 | 122.3557 | 0.10986 | 122.3648 | -122.3282 | -122.3785 | 0 | 122.1542 | -0.013733 | 1.062
4141.1094 | 122.4335 | -0.045776 | 122.2504 | -0.2195 | -0.040039 | 0.0030184 | 0.019946 | 0.0021447 | -0.01053 | -0.0034415 | -0.034454 | 0.0061651 | 0.063636 | 0.037442 | -0.016874 | 0.027408 | -0.0055799 | -0.064087 | -0.027466 | -0.009155 | 0.032043 | 0.14648 | -0.036621 | 0.082397 | 1.0941 | 122.1909 | -0.082397 | 122.1588 | 0.17395 | 0.091553 | 0.15106 | 0.036621 | -122.2778 | -122.2183 | 0.19226 | 0.12817 | 0.009155 | 0.091552 | -0.027466 | -0.036621 | -0.059509 | -0.091553 | 0.21973 | 0.19684 | 0.13733 | 0.23346 | 0.17395 | 0.15564 | 0.041198 | 0.25635 | 122.2412 | -0.018311 | 122.2733 | 0.01831 | 122.2366 | -122.2595 | -122.3328 | 0.077819 | 122.2046 | -0.018311 | 1.1398
4142.7969 | 122.3648 | -0.091553 | 122.2961 | -0.10506 | -0.043457 | -0.00061317 | 0.022723 | 0.0017175 | -0.013307 | -0.0040823 | -0.064972 | 0.0083013 | 0.061286 | 0.045773 | -0.018797 | 0.026126 | -0.0019483 | -0.14648 | 0 | -0.068665 | -0.09613 | -0.013733 | -0.11444 | -0.009155 | 1.1032 | 122.2733 | -0.12817 | 122.0581 | 0.068665 | 0 | 0.045776 | 0.022888 | -122.2961 | -122.3923 | 0.07782 | 0.082398 | -0.022888 | 0.05951 | -0.045776 | -0.036621 | -0.022889 | -0.23804 | 0.16022 | 0.13733 | 0.091553 | 0.17395 | 0.12817 | 0.054932 | -0.027465 | 0.19684 | 122.1863 | 0.068665 | 122.4014 | 0.091553 | 122.3648 | -122.3648 | -122.4243 | -0.004577 | 122.1497 | -0.054931 | 1.1948
4144.4844 | 122.4655 | -0.054932 | 122.2458 | -0.21187 | -0.038758 | 0.0034456 | 0.022723 | 0.00022207 | -0.0094614 | -0.0057913 | -0.083283 | 0.0057379 | 0.062568 | 0.048764 | -0.018369 | 0.02869 | -0.0021619 | -0.064087 | -0.032043 | -0.013733 | 0.022888 | 0.12817 | -0.032043 | 0.073242 | 1.1215 | 122.2046 | -0.073242 | 122.168 | 0.18768 | 0.10986 | 0.17395 | 0.041199 | -122.2778 | -122.2229 | 0.18311 | 0.12817 | 0.022889 | 0.086975 | -0.01831 | -0.01831 | -0.041199 | -0.07782 | 0.24261 | 0.22888 | 0.16479 | 0.24719 | 0.18311 | 0.14191 | 0.036621 | 0.26092 | 122.2412 | -0.01831 | 122.2778 | 0.022889 | 122.2595 | -122.2595 | -122.319 | 0.07782 | 122.2229 | -0.009155 | 1.1765
4146.1875 | 122.4701 | -0.054932 | 122.2366 | -0.10506 | -0.043671 | 0.0010958 | 0.02016 | 8.47e-06 | -0.012239 | -0.0028005 | -0.016144 | 0.0061651 | 0.062568 | 0.041928 | -0.018156 | 0.026981 | -0.0047253 | -0.07782 | -0.050354 | -0.013733 | 0.041199 | 0.16022 | 0 | 0.09613 | 1.2863 | 122.2 | -0.073242 | 122.1542 | 0.21515 | 0.14191 | 0.15106 | 0.041199 | -122.287 | -122.1954 | 0.21515 | 0.15106 | 0.054932 | 0.10986 | 0.013733 | -0.01831 | -0.036621 | -0.082397 | 0.27008 | 0.20599 | 0.19684 | 0.2243 | 0.21515 | 0.17395 | 0.054932 | 0.28839 | 122.2275 | -0.036621 | 122.2733 | 0.004578 | 122.2549 | -122.2504 | -122.3099 | 0.096131 | 122.2092 | -0.022888 | 1.3412
4147.8906 | 122.3969 | -0.086975 | 122.2778 | -0.15083 | -0.041107 | 0.00066863 | 0.023364 | 0.0023585 | -0.010743 | -0.0032277 | -0.089386 | 0.0070197 | 0.062782 | 0.049405 | -0.019865 | 0.026553 | -0.0053661 | -0.10986 | -0.009155 | -0.064087 | -0.041199 | 0.036621 | -0.086975 | 0.009155 | 1.181 | 122.2504 | -0.10071 | 122.0993 | 0.10986 | 0.022888 | 0.091553 | 0.022888 | -122.287 | -122.319 | 0.1236 | 0.09613 | 0 | 0.073242 | -0.022888 | -0.013733 | -0.027466 | -0.17853 | 0.19684 | 0.17853 | 0.10986 | 0.19226 | 0.1236 | 0.10071 | 0.022888 | 0.21057 | 122.2 | 0.054932 | 122.3511 | 0.07782 | 122.3373 | -122.3419 | -122.3785 | 0.045776 | 122.1863 | -0.022888 | 1.268
4149.6094 | 122.3557 | -0.086975 | 122.2733 | -0.12032 | -0.041535 | 0.0013094 | 0.024005 | 0.0038537 | -0.009675 | -0.0028005 | -0.11685 | 0.0076605 | 0.06385 | 0.052609 | -0.018583 | 0.027621 | -0.0030163 | -0.091553 | -0.009155 | -0.050354 | -0.045776 | 0.041199 | -0.10986 | -0.009155 | 1.1536 | 122.2504 | -0.10529 | 122.081 | 0.064087 | -0.013733 | 0.068665 | 0.036621 | -122.2824 | -122.319 | 0.12817 | 0.07782 | -0.022888 | 0.041199 | -0.059509 | -0.018311 | -0.022888 | -0.19226 | 0.15106 | 0.15564 | 0.073242 | 0.17395 | 0.091553 | 0.091553 | 0.004578 | 0.16937 | 122.1863 | 0.041199 | 122.3557 | 0.07782 | 122.3373 | -122.3236 | -122.3785 | 0.041199 | 122.168 | -0.004578 | 1.2405
4151.3125 | 122.4609 | -0.041199 | 122.2412 | -0.18898 | -0.043457 | 0.0045138 | 0.022509 | -0.0029821 | -0.009675 | -0.0047231 | -0.077179 | 0.0053107 | 0.062354 | 0.041073 | -0.018583 | 0.027621 | -0.00045291 | -0.086975 | -0.027466 | -0.041199 | 0.004578 | 0.10529 | -0.054932 | 0.041199 | 1.1765 | 122.1863 | -0.064087 | 122.1542 | 0.16479 | 0.091553 | 0.17395 | 0 | -122.2687 | -122.2366 | 0.14649 | 0.082398 | -0.013733 | 0.082398 | -0.013733 | -0.022888 | -0.054932 | -0.086975 | 0.20599 | 0.21515 | 0.13275 | 0.23804 | 0.15564 | 0.14649 | 0.045777 | 0.22888 | 122.2183 | 0.013733 | 122.2504 | 0.013733 | 122.2275 | -122.2824 | -122.3053 | 0.045777 | 122.1954 | -0.045776 | 1.2177
4153.0781 | 122.4976 | -0.036621 | 122.2412 | -0.10506 | -0.044525 | -0.00082677 | 0.018451 | 0.0012903 | -0.013093 | -0.00066434 | 0.0082703 | 0.0061651 | 0.062354 | 0.036374 | -0.017088 | 0.028049 | -0.0045117 | -0.059509 | -0.018311 | -0.022888 | 0.041199 | 0.1831 | 0.018311 | 0.11444 | 1.387 | 122.2 | -0.082397 | 122.1817 | 0.21515 | 0.15106 | 0.14648 | 0.013733 | -122.2595 | -122.2 | 0.21973 | 0.15106 | 0.054932 | 0.13733 | 0.041199 | -0.045776 | -0.041199 | -0.059509 | 0.25177 | 0.18311 | 0.18768 | 0.22888 | 0.23346 | 0.20599 | 0.064087 | 0.29755 | 122.2641 | 0.004577 | 122.2824 | 0.01831 | 122.2366 | -122.2641 | -122.3236 | 0.07782 | 122.2183 | -0.022888 | 1.4236
4154.7812 | 122.3785 | -0.09613 | 122.2733 | -0.15083 | -0.042176 | 0.00088223 | 0.025714 | 0.0019311 | -0.010957 | -0.0045095 | -0.1138 | 0.0053107 | 0.060432 | 0.051755 | -0.017088 | 0.02933 | -0.0053661 | -0.091553 | -0.009155 | -0.041199 | -0.027466 | 0.064087 | -0.073242 | 0.013733 | 1.2634 | 122.2321 | -0.07782 | 122.0947 | 0.086975 | 0.004578 | 0.07782 | 0.054931 | -122.2824 | -122.3007 | 0.16022 | 0.10986 | 0.022888 | 0.054932 | -0.032043 | 0.01831 | -0.041198 | -0.17853 | 0.1831 | 0.17395 | 0.10071 | 0.15564 | 0.082398 | 0.10529 | 0.013733 | 0.16479 | 122.1725 | 0.032044 | 122.3099 | 0.086975 | 122.3282 | -122.3145 | -122.3511 | 0.068664 | 122.1909 | 0.004577 | 1.3596
4156.5312 | 122.3877 | -0.086975 | 122.3007 | -0.11269 | -0.042603 | 0.0010958 | 0.022082 | 0.00064947 | -0.01053 | -0.0034415 | -0.12296 | 0.0036017 | 0.064277 | 0.048977 | -0.017729 | 0.025699 | -0.0010937 | -0.091553 | -0.004578 | -0.068665 | -0.045776 | 0.073242 | -0.082397 | 0.009155 | 1.3138 | 122.2183 | -0.086975 | 122.1039 | 0.11444 | 0.027466 | 0.10071 | 0.01831 | -122.3053 | -122.3465 | 0.16022 | 0.09613 | 0.004578 | 0.07782 | -0.013732 | 0 | -0.082397 | -0.19684 | 0.20142 | 0.18768 | 0.11444 | 0.18768 | 0.11444 | 0.14191 | 0.022889 | 0.20142 | 122.1909 | 0.064087 | 122.3053 | 0.082397 | 122.3053 | -122.3694 | -122.3877 | 0.041199 | 122.1909 | -0.004578 | 1.4008
4158.2344 | 122.4106 | -0.059509 | 122.2412 | -0.16609 | -0.044098 | 0.00066863 | 0.018451 | 0.0015039 | -0.011811 | -0.0030141 | -0.0039367 | 0.0068059 | 0.065132 | 0.038937 | -0.016874 | 0.024417 | -0.0047253 | -0.1236 | -0.045776 | -0.027466 | -0.027466 | 0.073242 | -0.068665 | 0.045776 | 1.2817 | 122.2183 | -0.086975 | 122.1085 | 0.14191 | 0.073242 | 0.11902 | 0.032043 | -122.287 | -122.2687 | 0.13275 | 0.10528 | -0.009156 | 0.073242 | -0.041199 | -0.027466 | -0.022888 | -0.13275 | 0.20142 | 0.17853 | 0.13275 | 0.20599 | 0.16022 | 0.10071 | 0 | 0.22888 | 122.1954 | -0.01831 | 122.3053 | 0.013733 | 122.2778 | -122.2687 | -122.3282 | 0.032043 | 122.168 | -0.064087 | 1.3412
4159.9375 | 122.374 | -0.086975 | 122.2687 | -0.15083 | -0.042389 | 0.00088223 | 0.020373 | 0.0021447 | -0.012452 | -0.0051505 | -0.01004 | 0.0078741 | 0.062782 | 0.044705 | -0.01602 | 0.02933 | -0.0017347 | -0.064087 | -0.013733 | -0.022888 | -0.004578 | 0.09613 | -0.022888 | 0.059509 | 1.442 | 122.2183 | -0.082397 | 122.0718 | 0.11444 | 0.041199 | 0.068665 | 0.064087 | -122.2824 | -122.2733 | 0.1831 | 0.14648 | 0.064087 | 0.082397 | 0 | 0.004578 | -0.050354 | -0.19684 | 0.20142 | 0.15564 | 0.12817 | 0.15106 | 0.1236 | 0.11902 | 0.01831 | 0.19684 | 122.1542 | 0.009155 | 122.3007 | 0.073242 | 122.3053 | -122.2916 | -122.3511 | 0.082397 | 122.1588 | 0.022888 | 1.5289
4161.625 | 122.4747 | -0.068665 | 122.2641 | -0.17372 | -0.043244 | -0.0023222 | 0.020373 | -0.0044775 | -0.010743 | -0.0057913 | -0.0069885 | 0.0036017 | 0.063209 | 0.041073 | -0.017942 | 0.028049 | -0.0036573 | -0.09613 | -0.032043 | -0.022888 | 0.032043 | 0.13275 | 0 | 0.10071 | 1.5015 | 122.1909 | -0.068665 | 122.1725 | 0.20599 | 0.14648 | 0.16022 | 0.045777 | -122.2961 | -122.2321 | 0.20142 | 0.16937 | 0.068665 | 0.1236 | 0.022888 | 0 | -0.073242 | -0.091553 | 0.27466 | 0.22888 | 0.21515 | 0.22888 | 0.21515 | 0.15564 | 0.054931 | 0.27466 | 122.2412 | -0.009155 | 122.2595 | 0.036622 | 122.2595 | -122.287 | -122.3328 | 0.10071 | 122.2412 | -0.027465 | 1.5701
4163.3438 | 122.3465 | -0.11444 | 122.3007 | -0.11269 | -0.04303 | 0.002164 | 0.020587 | -0.0023413 | -0.013093 | -0.0036551 | -0.052765 | 0.0053107 | 0.0615 | 0.044705 | -0.018156 | 0.025485 | -0.0045117 | -0.15106 | 0 | -0.068665 | -0.091553 | 0.013733 | -0.11902 | -0.022888 | 1.4328 | 122.2549 | -0.11902 | 122.0306 | 0.054932 | -0.004578 | 0.022888 | 0.045776 | -122.3007 | -122.3923 | 0.12817 | 0.091553 | -0.004578 | 0.045777 | -0.050354 | -0.004578 | -0.045776 | -0.27008 | 0.16937 | 0.13733 | 0.10986 | 0.14191 | 0.11444 | 0.082398 | -0.022888 | 0.17395 | 122.1497 | 0.068665 | 122.374 | 0.11444 | 122.3694 | -122.3694 | -122.4197 | 0.022888 | 122.1451 | -0.036621 | 1.5472
4165.0469 | 122.3831 | -0.073242 | 122.2916 | -0.10506 | -0.042389 | 0.0017368 | 0.02315 | 0.0029993 | -0.014375 | -0.0034415 | -0.10464 | 0.0055243 | 0.061927 | 0.048123 | -0.018369 | 0.025699 | -0.0066479 | -0.10986 | -0.009155 | -0.059509 | -0.045776 | 0.018311 | -0.086975 | 0.004578 | 1.506 | 122.2412 | -0.091553 | 122.081 | 0.10529 | 0.013733 | 0.07782 | 0.013733 | -122.3007 | -122.3373 | 0.091553 | 0.07782 | -0.013733 | 0.064087 | -0.027466 | -0.018311 | -0.050354 | -0.21057 | 0.17853 | 0.15106 | 0.086975 | 0.16937 | 0.10529 | 0.07782 | 0.013733 | 0.19684 | 122.1725 | 0.050354 | 122.3328 | 0.064087 | 122.3145 | -122.3511 | -122.3831 | 0.027466 | 122.1542 | -0.036621 | 1.5793
4166.75 | 122.3511 | -0.10071 | 122.2916 | -0.10506 | -0.04538 | 0.0010958 | 0.022723 | 0.00043587 | -0.011598 | -0.0051505 | -0.064972 | 0.0065923 | 0.064704 | 0.04855 | -0.017942 | 0.026981 | -0.0045117 | -0.15106 | 0.009155 | -0.064087 | -0.10071 | -0.022888 | -0.1236 | -0.022888 | 1.5381 | 122.2458 | -0.10529 | 122.0398 | 0.059509 | 0 | 0.050354 | 0.036621 | -122.2824 | -122.3923 | 0.07782 | 0.07782 | -0.022888 | 0.041199 | -0.059509 | -0.004578 | -0.045776 | -0.25177 | 0.16022 | 0.15106 | 0.10071 | 0.15564 | 0.10529 | 0.041199 | -0.036621 | 0.16479 | 122.1451 | 0.073242 | 122.3511 | 0.10986 | 122.3465 | -122.3557 | -122.3969 | 0 | 122.1405 | -0.050354 | 1.6388
4168.4375 | 122.4609 | -0.032043 | 122.2504 | -0.2195 | -0.040039 | 0.0034456 | 0.019732 | -0.0017005 | -0.008607 | -0.0060049 | -0.080231 | 0.0070197 | 0.062782 | 0.046414 | -0.017729 | 0.026126 | -0.0055799 | -0.045776 | -0.036621 | -0.022888 | 0.041199 | 0.12817 | -0.018311 | 0.068665 | 1.6159 | 122.2046 | -0.068665 | 122.168 | 0.19226 | 0.11444 | 0.17395 | 0.009155 | -122.287 | -122.2092 | 0.16022 | 0.10071 | 0.013732 | 0.091553 | 0.004577 | -0.036622 | -0.045776 | -0.082397 | 0.2243 | 0.20599 | 0.14648 | 0.24261 | 0.18311 | 0.15106 | 0.064087 | 0.26093 | 122.2366 | -0.013733 | 122.2733 | -0.004578 | 122.2366 | -122.2733 | -122.319 | 0.073242 | 122.2 | -0.013733 | 1.6479
4170.1406 | 122.4655 | -0.054932 | 122.2366 | -0.12794 | -0.043457 | 0.00088223 | 0.0208 | 0.0017175 | -0.010957 | -0.0021597 | -0.031403 | 0.0053107 | 0.061714 | 0.050686 | -0.018369 | 0.027621 | -0.0042981 | -0.068665 | -0.041199 | -0.013733 | 0.041199 | 0.15564 | 0.004578 | 0.10986 | 1.8173 | 122.2046 | -0.064087 | 122.1542 | 0.20142 | 0.14191 | 0.16937 | 0.041199 | -122.2778 | -122.1954 | 0.21057 | 0.16479 | 0.05951 | 0.1236 | 0.018311 | -0.009155 | -0.032043 | -0.082397 | 0.25635 | 0.22431 | 0.19684 | 0.23346 | 0.20599 | 0.16937 | 0.054932 | 0.2655 | 122.2183 | -0.027466 | 122.2687 | 0.013733 | 122.2595 | -122.2504 | -122.3007 | 0.096131 | 122.2092 | -0.013733 | 1.8723
4171.8438 | 122.3328 | -0.09613 | 122.2824 | -0.16609 | -0.038971 | 0.0019504 | 0.022509 | 0.00064947 | -0.0094614 | -0.0028005 | -0.13211 | 0.0080877 | 0.061286 | 0.048977 | -0.020933 | 0.029544 | -0.0040845 | -0.11444 | 0.009155 | -0.059509 | -0.07782 | -0.004578 | -0.14648 | -0.036621 | 1.6388 | 122.2733 | -0.091553 | 122.0352 | 0.036621 | -0.045776 | 0.022888 | 0.036621 | -122.2733 | -122.3602 | 0.091552 | 0.059509 | -0.050354 | 0.022888 | -0.086975 | 0.004577 | -0.009156 | -0.24719 | 0.13275 | 0.11902 | 0.050354 | 0.11444 | 0.045777 | 0.054931 | -0.018311 | 0.12817 | 122.1268 | 0.068664 | 122.3648 | 0.10528 | 122.3694 | -122.3419 | -122.374 | 0.01831 | 122.1313 | -0.018311 | 1.7349
4173.5938 | 122.3602 | -0.10529 | 122.2778 | -0.12032 | -0.043885 | 0.0013094 | 0.022296 | -0.00063233 | -0.012666 | -0.0015189 | -0.025299 | 0.0074469 | 0.061714 | 0.045132 | -0.016233 | 0.025485 | -0.0057935 | -0.086975 | -0.022888 | -0.036621 | -0.032043 | 0.054932 | -0.059509 | 0.032043 | 1.8402 | 122.2549 | -0.10071 | 122.0398 | 0.073242 | 0.013733 | 0.045776 | 0.068665 | -122.3007 | -122.3099 | 0.16022 | 0.13733 | 0.045777 | 0.068664 | -0.022888 | 0.004578 | -0.022888 | -0.23804 | 0.17853 | 0.15106 | 0.11902 | 0.14648 | 0.11444 | 0.091553 | 0.004578 | 0.17395 | 122.1405 | 0.013733 | 122.3557 | 0.082398 | 122.3602 | -122.3145 | -122.3785 | 0.073243 | 122.1451 | 0.018311 | 1.9455
4175.2969 | 122.3557 | -0.082397 | 122.287 | -0.16609 | -0.040253 | 0.0030184 | 0.025714 | 0.0012903 | -0.0088206 | -0.0053641 | -0.13211 | 0.0070197 | 0.061927 | 0.050259 | -0.019438 | 0.026767 | -0.0032299 | -0.091553 | 0.004578 | -0.036621 | -0.050354 | 0.045776 | -0.10986 | 0 | 1.8631 | 122.2412 | -0.09613 | 122.0764 | 0.068665 | -0.022888 | 0.050354 | 0.045776 | -122.2824 | -122.3373 | 0.12817 | 0.082397 | -0.027466 | 0.036621 | -0.073242 | -0.013733 | -0.045776 | -0.21057 | 0.15106 | 0.13275 | 0.059509 | 0.14648 | 0.073242 | 0.082397 | -0.013733 | 0.16479 | 122.1725 | 0.041199 | 122.3373 | 0.086975 | 122.3236 | -122.3236 | -122.3831 | 0.032043 | 122.1588 | -0.009156 | 1.9455
4177.0625 | 122.3831 | -0.10071 | 122.2641 | -0.15846 | -0.04303 | 0.001523 | 0.022723 | -0.00020513 | -0.0092478 | -0.0042959 | -0.086334 | 0.0080877 | 0.061927 | 0.049618 | -0.018156 | 0.02869 | -0.0064343 | -0.11902 | 0.009155 | -0.054932 | -0.045776 | 0.036621 | -0.082397 | 0.013733 | 2.005 | 122.2504 | -0.11444 | 122.081 | 0.11444 | 0.027466 | 0.086975 | 0.045776 | -122.2549 | -122.3099 | 0.13733 | 0.11444 | 0.018311 | 0.068665 | -0.027465 | -0.013733 | -0.013733 | -0.1831 | 0.21515 | 0.18768 | 0.12817 | 0.20142 | 0.14191 | 0.091553 | 0.009156 | 0.22888 | 122.1954 | 0.064087 | 122.3648 | 0.10986 | 122.3511 | -122.319 | -122.3785 | 0.054932 | 122.1817 | -0.018311 | 2.1057
4178.7656 | 122.4197 | -0.068665 | 122.2595 | -0.21187 | -0.042176 | 0.0030184 | 0.02315 | -0.0012731 | -0.010743 | -0.0051505 | -0.077179 | 0.0065923 | 0.063209 | 0.045773 | -0.018156 | 0.025912 | -0.0013073 | -0.12817 | 0.022888 | -0.045776 | -0.082397 | 0.013733 | -0.13275 | -0.009155 | 1.9592 | 122.2321 | -0.082397 | 122.1176 | 0.10529 | 0.022888 | 0.10071 | 0.022889 | -122.2366 | -122.3419 | 0.082398 | 0.05951 | -0.064086 | 0.036621 | -0.086975 | -0.013732 | -0.027465 | -0.14191 | 0.17395 | 0.16937 | 0.091553 | 0.18311 | 0.10528 | 0.059509 | -0.036621 | 0.18768 | 122.2 | 0.068664 | 122.3145 | 0.091553 | 122.3007 | -122.3053 | -122.3419 | -0.013732 | 122.1863 | -0.059509 | 2.0279
4180.4688 | 122.438 | -0.064087 | 122.2687 | -0.12794 | -0.042816 | 0.00088223 | 0.021655 | -0.00084593 | -0.012025 | -0.0047231 | -0.01004 | 0.0068059 | 0.062354 | 0.04321 | -0.018797 | 0.027621 | -0.00088011 | -0.082397 | -0.045776 | -0.018311 | 0.050354 | 0.12817 | 0.009155 | 0.09613 | 2.2751 | 122.2046 | -0.082397 | 122.1222 | 0.16937 | 0.1236 | 0.14191 | 0.045776 | -122.3145 | -122.2183 | 0.19226 | 0.16022 | 0.073242 | 0.11444 | 0.027466 | -0.01831 | -0.064087 | -0.14648 | 0.23346 | 0.20599 | 0.18768 | 0.2243 | 0.20599 | 0.14649 | 0.068665 | 0.25177 | 122.2046 | -0.027465 | 122.287 | 0.018311 | 122.2687 | -122.287 | -122.3511 | 0.11444 | 122.1863 | -0.01831 | 2.3392
4182.1875 | 122.4518 | -0.036621 | 122.2504 | -0.19661 | -0.041321 | 0.0034456 | 0.021014 | 0.0027857 | -0.0090342 | -0.0028005 | -0.025299 | 0.0050971 | 0.062782 | 0.044064 | -0.016874 | 0.026767 | -0.0042981 | -0.059509 | -0.036621 | -0.032043 | 0.041199 | 0.13733 | -0.022888 | 0.082397 | 2.2568 | 122.1771 | -0.068665 | 122.1588 | 0.16937 | 0.09613 | 0.15564 | 0.004578 | -122.287 | -122.2092 | 0.17395 | 0.11902 | 0.013733 | 0.11444 | 0.009155 | -0.032044 | -0.073242 | -0.091553 | 0.20599 | 0.19226 | 0.13275 | 0.22431 | 0.16479 | 0.16937 | 0.073242 | 0.23804 | 122.2275 | -0.004578 | 122.2458 | 0 | 122.2137 | -122.2824 | -122.319 | 0.07782 | 122.1954 | -0.022888 | 2.2934
4183.8906 | 122.3419 | -0.10529 | 122.3007 | -0.15083 | -0.044525 | 0.00088223 | 0.023578 | -0.0014867 | -0.012025 | -0.0030141 | -0.046661 | 0.0080877 | 0.061286 | 0.043423 | -0.017515 | 0.02869 | -0.0038709 | -0.14648 | 0.009155 | -0.07782 | -0.091553 | -0.009155 | -0.10986 | -0.013733 | 2.3392 | 122.2549 | -0.09613 | 122.0444 | 0.064087 | -0.022888 | 0.032043 | 0.027466 | -122.2916 | -122.3923 | 0.096131 | 0.091553 | -0.004577 | 0.064087 | -0.032043 | 0.009156 | -0.045776 | -0.25635 | 0.16937 | 0.13733 | 0.082398 | 0.12817 | 0.073242 | 0.068665 | -0.013733 | 0.16022 | 122.1405 | 0.086975 | 122.3511 | 0.11444 | 122.3602 | -122.3785 | -122.3969 | 0.013733 | 122.1497 | -0.041198 | 2.4445
4185.625 | 122.4335 | -0.059509 | 122.2504 | -0.17372 | -0.042389 | 0.00045503 | 0.018451 | -0.0049047 | -0.011811 | -0.0042959 | 0.014374 | 0.0048833 | 0.059577 | 0.048764 | -0.018156 | 0.026767 | -0.0038709 | -0.07782 | -0.050354 | -0.027466 | 0.041199 | 0.1236 | 0.004578 | 0.086975 | 2.5635 | 122.2183 | -0.064087 | 122.113 | 0.1831 | 0.10071 | 0.13275 | 0.032043 | -122.3007 | -122.2092 | 0.1831 | 0.14648 | 0.064087 | 0.11444 | 0.032044 | -0.004578 | -0.032043 | -0.13733 | 0.24261 | 0.19226 | 0.16022 | 0.19684 | 0.1648 | 0.15106 | 0.068665 | 0.24719 | 122.1771 | -0.022888 | 122.2824 | 0.009155 | 122.2778 | -122.2778 | -122.3145 | 0.10071 | 122.1725 | -0.018311 | 2.623
4187.3281 | 122.3282 | -0.10071 | 122.2824 | -0.19661 | -0.041962 | 0.0030184 | 0.024005 | 0.0036401 | -0.0071116 | -0.0010915 | -0.1199 | 0.0072333 | 0.062782 | 0.045132 | -0.018369 | 0.028049 | -0.0051525 | -0.1236 | 0 | -0.073242 | -0.1236 | -0.054932 | -0.16022 | -0.064087 | 2.3804 | 122.2641 | -0.11444 | 122.0261 | 0.027466 | -0.054932 | 0.041199 | 0.027466 | -122.2824 | -122.406 | 0.045776 | 0.036621 | -0.059509 | 0.009155 | -0.086975 | -0.013733 | -0.018311 | -0.25635 | 0.12817 | 0.14191 | 0.045776 | 0.15564 | 0.059509 | 0.01831 | -0.050354 | 0.14191 | 122.1405 | 0.073242 | 122.3785 | 0.10071 | 122.3648 | -122.3557 | -122.3969 | -0.022888 | 122.1268 | -0.022888 | 2.4811
4189.0781 | 122.4564 | -0.050354 | 122.2046 | -0.16609 | -0.042816 | 0.003232 | 0.022509 | -0.00041873 | -0.011598 | -0.0025869 | -0.058869 | 0.0046697 | 0.060218 | 0.050046 | -0.017088 | 0.028049 | -0.0062207 | -0.059509 | -0.045776 | -0.032043 | 0.027466 | 0.1236 | -0.032043 | 0.068665 | 2.6505 | 122.2046 | -0.068665 | 122.168 | 0.18768 | 0.10986 | 0.1831 | 0.018311 | -122.2504 | -122.1771 | 0.17395 | 0.11902 | 0.018311 | 0.10071 | 0 | -0.018311 | 0 | -0.036621 | 0.23804 | 0.23346 | 0.16022 | 0.25177 | 0.17853 | 0.15564 | 0.059509 | 0.25635 | 122.2366 | -0.013733 | 122.2733 | 0.004578 | 122.2549 | -122.2366 | -122.2733 | 0.07782 | 122.2183 | -0.009155 | 2.7008
4190.7969 | 122.4152 | -0.064087 | 122.2549 | -0.1432 | -0.045807 | -0.00082677 | 0.019946 | -0.00020513 | -0.011384 | -0.0038687 | -0.016144 | 0.0050971 | 0.061714 | 0.04385 | -0.01901 | 0.025272 | -0.0064343 | -0.073242 | -0.036621 | -0.009155 | 0.018311 | 0.12817 | -0.004578 | 0.073242 | 2.8793 | 122.2229 | -0.064087 | 122.1176 | 0.15564 | 0.091553 | 0.10529 | 0.054932 | -122.2916 | -122.2366 | 0.19226 | 0.13733 | 0.059509 | 0.082397 | 0.004577 | 0 | -0.032044 | -0.13733 | 0.21973 | 0.16937 | 0.15564 | 0.16937 | 0.15564 | 0.13733 | 0.027466 | 0.21973 | 122.1817 | -0.027466 | 122.287 | 0.027466 | 122.287 | -122.2641 | -122.319 | 0.082398 | 122.1817 | -0.009155 | 2.9434
4192.5469 | 122.4609 | -0.045776 | 122.2229 | -0.17372 | -0.040039 | 0.001523 | 0.022937 | -0.0010595 | -0.011384 | -0.0055777 | -0.052765 | 0.0053107 | 0.064491 | 0.045132 | -0.019651 | 0.026767 | -0.0066479 | -0.054932 | -0.022888 | -0.022888 | 0.032043 | 0.11444 | -0.036621 | 0.073242 | 2.8427 | 122.1909 | -0.068665 | 122.1725 | 0.18768 | 0.1236 | 0.17395 | 0.022888 | -122.2458 | -122.1909 | 0.16022 | 0.11902 | 0.009155 | 0.09613 | -0.013733 | -0.022889 | -0.032043 | -0.050354 | 0.23346 | 0.21973 | 0.16937 | 0.24261 | 0.19226 | 0.13733 | 0.054931 | 0.25635 | 122.2412 | 0 | 122.2595 | 0.022888 | 122.2366 | -122.2458 | -122.2916 | 0.077819 | 122.2183 | -0.009156 | 2.8885
4194.25 | 122.3511 | -0.11444 | 122.287 | -0.089798 | -0.042816 | 0.0013094 | 0.021014 | -0.0017005 | -0.013093 | -0.0057913 | -0.080231 | 0.0065923 | 0.06385 | 0.052395 | -0.017942 | 0.026981 | -0.0087841 | -0.15564 | 0.004578 | -0.068665 | -0.10071 | 0.004578 | -0.11444 | -0.013733 | 2.9205 | 122.2412 | -0.10529 | 122.0306 | 0.059509 | -0.022888 | 0.036621 | 0.045776 | -122.2824 | -122.3877 | 0.11902 | 0.10071 | 0 | 0.054932 | -0.045776 | 0.009155 | -0.045776 | -0.25635 | 0.17395 | 0.15106 | 0.091553 | 0.14191 | 0.082398 | 0.073243 | -0.032043 | 0.16479 | 122.1359 | 0.073243 | 122.3465 | 0.11902 | 122.3557 | -122.3557 | -122.3923 | 0.013733 | 122.1451 | -0.041199 | 3.035
4195.9375 | 122.4335 | -0.050354 | 122.2549 | -0.20424 | -0.045594 | 0.0030184 | 0.021869 | -0.00063233 | -0.011598 | -0.0081411 | -0.04361 | 0.0078741 | 0.063636 | 0.044064 | -0.018797 | 0.025699 | -0.0045117 | -0.07782 | -0.041199 | -0.027466 | 0.022888 | 0.13733 | -0.036621 | 0.068665 | 3.035 | 122.1954 | -0.082397 | 122.1176 | 0.15564 | 0.082397 | 0.12817 | 0.022888 | -122.2961 | -122.2321 | 0.18768 | 0.11902 | 0.013733 | 0.096131 | -0.009155 | -0.032043 | -0.059509 | -0.13733 | 0.20599 | 0.17853 | 0.13275 | 0.21057 | 0.16479 | 0.16479 | 0.050354 | 0.23804 | 122.2 | -0.013733 | 122.2778 | 0.009155 | 122.2458 | -122.2824 | -122.3373 | 0.073242 | 122.168 | -0.027466 | 3.0853
4197.6562 | 122.374 | -0.082397 | 122.2549 | -0.18135 | -0.043244 | 0.0025912 | 0.024859 | 0.0034265 | -0.012879 | -0.0028005 | -0.1199 | 0.0091559 | 0.062782 | 0.049191 | -0.017301 | 0.030185 | -0.0068615 | -0.086975 | -0.004578 | -0.054932 | -0.032043 | 0.041199 | -0.082397 | 0.009155 | 3.1403 | 122.2504 | -0.082397 | 122.0856 | 0.10529 | 0.013733 | 0.086975 | 0.027465 | -122.2595 | -122.287 | 0.1236 | 0.091552 | 0 | 0.064087 | -0.027465 | 0 | -0.004578 | -0.16937 | 0.18768 | 0.16937 | 0.09613 | 0.16937 | 0.09613 | 0.096131 | 0.022889 | 0.18768 | 122.168 | 0.050354 | 122.3328 | 0.077819 | 122.3328 | -122.3099 | -122.3373 | 0.050354 | 122.168 | -0.004578 | 3.2227
4199.3594 | 122.4747 | -0.054932 | 122.2275 | -0.15083 | -0.044525 | 0.00024143 | 0.02016 | -0.0021277 | -0.011598 | -0.0057913 | -0.028351 | 0.0036017 | 0.063636 | 0.042355 | -0.017515 | 0.027194 | -0.0064343 | -0.068665 | -0.032043 | -0.022888 | 0.054932 | 0.15564 | 0.027466 | 0.09613 | 3.3737 | 122.2 | -0.064087 | 122.1497 | 0.23804 | 0.15564 | 0.16479 | 0.032044 | -122.2595 | -122.1725 | 0.21057 | 0.15106 | 0.082398 | 0.11902 | 0.050354 | -0.009155 | -0.027466 | -0.07782 | 0.29297 | 0.21973 | 0.21057 | 0.22888 | 0.21973 | 0.17853 | 0.07782 | 0.30212 | 122.2137 | -0.009155 | 122.2641 | 0.022889 | 122.2549 | -122.2504 | -122.2916 | 0.10986 | 122.2046 | -0.013733 | 3.4287
4201.0781 | 122.4243 | -0.050354 | 122.2412 | -0.20424 | -0.042176 | 0.0028048 | 0.020373 | -0.0031957 | -0.010957 | -0.0045095 | -0.034454 | 0.0080877 | 0.062995 | 0.041714 | -0.018369 | 0.026981 | -0.0057935 | -0.073242 | -0.059509 | -0.013733 | 0.018311 | 0.13733 | -0.036621 | 0.073242 | 3.3463 | 122.1817 | -0.054932 | 122.1268 | 0.15564 | 0.09613 | 0.13275 | 0.036621 | -122.3007 | -122.2229 | 0.18768 | 0.1236 | 0.013733 | 0.086975 | -0.022888 | -0.004578 | -0.059509 | -0.11444 | 0.20599 | 0.18311 | 0.14648 | 0.18768 | 0.15106 | 0.15106 | 0.032044 | 0.21057 | 122.1817 | -0.045776 | 122.2366 | -0.009155 | 122.2321 | -122.2549 | -122.2961 | 0.068665 | 122.1771 | -0.022888 | 3.3966
4202.7812 | 122.3969 | -0.091553 | 122.2549 | -0.097427 | -0.044525 | 0.0010958 | 0.021228 | 0.0021447 | -0.012666 | -0.0038687 | -0.1077 | 0.0061651 | 0.064491 | 0.048977 | -0.020506 | 0.027194 | -0.0096387 | -0.11902 | 0 | -0.073242 | -0.091553 | -0.013733 | -0.10529 | -0.013733 | 3.4149 | 122.2549 | -0.10529 | 122.081 | 0.11444 | 0.009155 | 0.086975 | 0.018311 | -122.2549 | -122.3465 | 0.07782 | 0.07782 | -0.013733 | 0.059509 | -0.032044 | -0.013733 | 0 | -0.17395 | 0.20599 | 0.17853 | 0.10071 | 0.19226 | 0.11444 | 0.059509 | -0.018311 | 0.21973 | 122.1863 | 0.073242 | 122.3602 | 0.091553 | 122.3465 | -122.3282 | -122.3602 | 0 | 122.1725 | -0.027466 | 3.5065
4204.4688 | 122.4243 | -0.059509 | 122.2641 | -0.15846 | -0.043457 | 0.001523 | 0.018664 | -0.0021277 | -0.010316 | -0.0051505 | -0.016144 | 0.0036017 | 0.062141 | 0.047268 | -0.016447 | 0.026981 | -0.0032299 | -0.11444 | -0.022888 | -0.036621 | -0.036621 | 0.073242 | -0.064087 | 0.041199 | 3.4927 | 122.2092 | -0.09613 | 122.1085 | 0.13733 | 0.059509 | 0.11444 | 0.022888 | -122.287 | -122.3007 | 0.13275 | 0.10071 | -0.004578 | 0.07782 | -0.027466 | -0.036621 | -0.054932 | -0.15564 | 0.19684 | 0.17395 | 0.11902 | 0.21057 | 0.15564 | 0.10986 | 0 | 0.23346 | 122.2046 | 0.013733 | 122.3053 | 0.036621 | 122.2687 | -122.3007 | -122.3602 | 0.022888 | 122.168 | -0.054932 | 3.5522
4206.1875 | 122.3465 | -0.10986 | 122.2961 | -0.15083 | -0.04303 | 0.0013094 | 0.025287 | 0.00022207 | -0.013734 | -0.0042959 | -0.10159 | 0.0065923 | 0.065559 | 0.048337 | -0.019438 | 0.026553 | -0.0028027 | -0.15106 | 0.009155 | -0.068665 | -0.09613 | -0.022888 | -0.13275 | -0.018311 | 3.6118 | 122.2733 | -0.10986 | 122.0261 | 0.073242 | -0.009155 | 0.045776 | 0.041198 | -122.287 | -122.3923 | 0.086975 | 0.091552 | -0.022888 | 0.050354 | -0.064086 | 0 | -0.022889 | -0.27008 | 0.18311 | 0.15564 | 0.10071 | 0.15564 | 0.10071 | 0.045777 | -0.027465 | 0.18311 | 122.1359 | 0.07782 | 122.3831 | 0.11902 | 122.3831 | -122.3648 | -122.406 | 0.013733 | 122.1359 | -0.041199 | 3.7216
4207.8906 | 122.4518 | -0.050354 | 122.2229 | -0.25002 | -0.042389 | 0.0023776 | 0.022723 | 0.0012903 | -0.010102 | -0.0045095 | -0.068024 | 0.0059515 | 0.062141 | 0.045132 | -0.018583 | 0.024631 | -0.0032299 | -0.064087 | -0.041199 | -0.018311 | 0.032043 | 0.13275 | -0.013733 | 0.07782 | 3.7399 | 122.2229 | -0.064087 | 122.1542 | 0.1831 | 0.09613 | 0.16022 | 0.032043 | -122.2641 | -122.1909 | 0.18311 | 0.12817 | 0.036621 | 0.096131 | 0.004578 | -0.013733 | 0 | -0.068664 | 0.23346 | 0.21057 | 0.14648 | 0.2243 | 0.16022 | 0.15106 | 0.050354 | 0.24719 | 122.2183 | -0.022888 | 122.287 | 0.009155 | 122.2733 | -122.2412 | -122.287 | 0.082397 | 122.2046 | -0.013733 | 3.7903
4209.6406 | 122.3465 | -0.10529 | 122.3053 | -0.10506 | -0.043671 | 0.00088223 | 0.022509 | -0.0029821 | -0.01352 | -0.0053641 | -0.049713 | 0.0076605 | 0.063636 | 0.040433 | -0.016233 | 0.02634 | -0.0030163 | -0.16022 | 0.009155 | -0.07782 | -0.10986 | -0.013733 | -0.10986 | -0.018311 | 3.7857 | 122.2549 | -0.10071 | 122.0306 | 0.073242 | -0.009155 | 0.032043 | 0.027466 | -122.2961 | -122.4152 | 0.091553 | 0.086975 | -0.004577 | 0.059509 | -0.032043 | 0.004578 | -0.050354 | -0.27466 | 0.17853 | 0.13733 | 0.096131 | 0.13275 | 0.091553 | 0.064087 | -0.032043 | 0.17395 | 122.1313 | 0.086975 | 122.3557 | 0.11444 | 122.3602 | -122.3831 | -122.406 | -0.004577 | 122.1359 | -0.054931 | 3.891
4211.3438 | 122.3373 | -0.091553 | 122.2595 | -0.15083 | -0.039612 | -0.00039957 | 0.023578 | -0.0029821 | -0.011598 | -0.0051505 | -0.1199 | 0.0048833 | 0.0615 | 0.048123 | -0.017301 | 0.027408 | -0.0034435 | -0.10529 | -0.004578 | -0.059509 | -0.045776 | 0.022888 | -0.1236 | -0.013733 | 3.8406 | 122.2549 | -0.07782 | 122.049 | 0.059509 | -0.032043 | 0.041199 | 0.032044 | -122.2641 | -122.3053 | 0.11444 | 0.07782 | -0.032043 | 0.045776 | -0.064087 | 0.013733 | -0.004577 | -0.21057 | 0.15106 | 0.13275 | 0.05951 | 0.11902 | 0.045777 | 0.082397 | 0.013733 | 0.13733 | 122.1268 | 0.054931 | 122.3328 | 0.086975 | 122.3465 | -122.319 | -122.3373 | 0.045777 | 122.1405 | -0.013733 | 3.9322
4213.0469 | 122.3419 | -0.086975 | 122.3053 | -0.13557 | -0.043885 | 0.00088223 | 0.019091 | -0.00084593 | -0.011811 | -0.0034415 | -0.016144 | 0.0065923 | 0.062995 | 0.042569 | -0.016447 | 0.024844 | -0.0032299 | -0.091553 | -0.036621 | -0.036621 | -0.027466 | 0.068665 | -0.041199 | 0.027466 | 4.0695 | 122.2275 | -0.09613 | 122.0627 | 0.10071 | 0.032043 | 0.045776 | 0.050354 | -122.3419 | -122.3328 | 0.15564 | 0.11444 | 0.045776 | 0.064087 | -0.004578 | -0.009155 | -0.07782 | -0.24261 | 0.18768 | 0.13275 | 0.11902 | 0.14191 | 0.12817 | 0.10529 | 0.009155 | 0.19684 | 122.1588 | 0 | 122.3236 | 0.050354 | 122.3145 | -122.3419 | -122.4014 | 0.059509 | 122.1497 | -0.004578 | 4.1565
4214.7344 | 122.4335 | -0.054932 | 122.2412 | -0.18135 | -0.040039 | 0.0030184 | 0.022723 | 0.0015039 | -0.0092478 | -0.0060049 | -0.046661 | 0.0055243 | 0.063636 | 0.051114 | -0.018369 | 0.026767 | -0.0053661 | -0.064087 | -0.045776 | -0.022888 | 0.022888 | 0.13733 | -0.041199 | 0.086975 | 4.1565 | 122.1954 | -0.054932 | 122.1313 | 0.18768 | 0.09613 | 0.12817 | 0.032044 | -122.287 | -122.2183 | 0.19226 | 0.14191 | 0.013733 | 0.10986 | -0.018311 | 0 | -0.045776 | -0.10986 | 0.24261 | 0.18311 | 0.15106 | 0.18311 | 0.15106 | 0.16022 | 0.045776 | 0.24261 | 122.1863 | -0.022888 | 122.2504 | 0.009156 | 122.2504 | -122.2641 | -122.2961 | 0.07782 | 122.1863 | -0.009155 | 4.2114
4216.4375 | 122.3465 | -0.09613 | 122.2778 | -0.12032 | -0.044739 | 0.00024143 | 0.021014 | -0.00041873 | -0.01053 | -0.0040823 | -0.049713 | 0.0070197 | 0.06385 | 0.0509 | -0.016447 | 0.024631 | -0.0077161 | -0.12817 | -0.009155 | -0.07782 | -0.082397 | 0.013733 | -0.10529 | 0 | 4.216 | 122.2595 | -0.10529 | 122.0169 | 0.07782 | -0.009155 | 0.013733 | 0.01831 | -122.287 | -122.3602 | 0.10986 | 0.09613 | -0.009156 | 0.07782 | -0.027466 | -0.009156 | -0.018311 | -0.26093 | 0.17395 | 0.10986 | 0.086975 | 0.11902 | 0.096131 | 0.091553 | -0.004577 | 0.18311 | 122.1222 | 0.068665 | 122.3648 | 0.086975 | 122.3557 | -122.3557 | -122.3831 | 0.013733 | 122.113 | -0.032044 | 4.3121
4218.1406 | 122.4243 | -0.050354 | 122.2412 | -0.19661 | -0.043671 | 0.0019504 | 0.020587 | -0.0019141 | -0.012452 | -0.0036551 | -0.046661 | 0.0053107 | 0.062354 | 0.047909 | -0.019651 | 0.026981 | -0.0025891 | -0.09613 | -0.022888 | -0.009155 | -0.004578 | 0.11902 | -0.059509 | 0.059509 | 4.3442 | 122.1954 | -0.07782 | 122.1039 | 0.15564 | 0.064087 | 0.13275 | 0.041199 | -122.2641 | -122.2458 | 0.16937 | 0.10986 | -0.009155 | 0.068664 | -0.050354 | -0.027466 | -0.045776 | -0.13733 | 0.20599 | 0.18311 | 0.11444 | 0.21057 | 0.14191 | 0.12817 | 0.004577 | 0.23346 | 122.1817 | -0.013733 | 122.2733 | 0.027466 | 122.2458 | -122.2504 | -122.319 | 0.045776 | 122.1542 | -0.045776 | 4.3945
4219.8281 | 122.3602 | -0.10986 | 122.287 | -0.12794 | -0.043244 | 0.0013094 | 0.022937 | 0.00043587 | -0.013947 | -0.0036551 | -0.13211 | 0.0061651 | 0.062782 | 0.0509 | -0.019224 | 0.027408 | -0.0068615 | -0.082397 | 0 | -0.050354 | -0.032043 | 0.050354 | -0.09613 | 0.004578 | 4.454 | 122.2504 | -0.09613 | 122.0718 | 0.10529 | -0.004578 | 0.068665 | 0.059509 | -122.287 | -122.319 | 0.16022 | 0.11444 | 0.013733 | 0.054932 | -0.045776 | 0.013733 | -0.036621 | -0.21515 | 0.21515 | 0.17853 | 0.10529 | 0.16479 | 0.091552 | 0.10071 | 0.018311 | 0.20142 | 122.168 | 0.050354 | 122.3465 | 0.10986 | 122.3602 | -122.3373 | -122.3831 | 0.07782 | 122.1817 | 0.027466 | 4.5639
4221.5781 | 122.3465 | -0.10071 | 122.2641 | -0.11269 | -0.044098 | -0.0014676 | 0.021655 | -0.0042639 | -0.014161 | -0.0047231 | -0.046661 | 0.0085149 | 0.063423 | 0.048977 | -0.018583 | 0.026126 | -0.0021619 | -0.14648 | 0.018311 | -0.059509 | -0.10071 | 0 | -0.10986 | -0.022888 | 4.541 | 122.2366 | -0.10529 | 122.0352 | 0.07782 | -0.022888 | 0.022888 | 0.041199 | -122.2458 | -122.3648 | 0.10071 | 0.07782 | -0.009155 | 0.036621 | -0.050354 | -0.004578 | -0.027466 | -0.22888 | 0.17853 | 0.1236 | 0.07782 | 0.12817 | 0.082398 | 0.059509 | -0.041199 | 0.18311 | 122.1405 | 0.07782 | 122.3419 | 0.11902 | 122.3373 | -122.3236 | -122.3694 | 0 | 122.1359 | -0.045776 | 4.6417
4223.2812 | 122.3602 | -0.082397 | 122.2595 | -0.18135 | -0.041107 | 0.0010958 | 0.022937 | -0.00084593 | -0.010102 | -0.0042959 | -0.092438 | 0.0087287 | 0.061927 | 0.042996 | -0.018583 | 0.029544 | -0.0034435 | -0.12817 | 0 | -0.064087 | -0.082397 | 0 | -0.13275 | -0.018311 | 4.5364 | 122.2321 | -0.10071 | 122.0856 | 0.09613 | 0.018311 | 0.086975 | 0.01831 | -122.2595 | -122.3419 | 0.082397 | 0.064086 | -0.050354 | 0.045776 | -0.068664 | -0.018311 | -0.027465 | -0.17395 | 0.17853 | 0.16937 | 0.10071 | 0.18768 | 0.11902 | 0.064087 | -0.01831 | 0.19684 | 122.1863 | 0.064087 | 122.3328 | 0.082397 | 122.3145 | -122.3236 | -122.3602 | 0 | 122.168 | -0.045777 | 4.6188
4224.9844 | 122.4518 | -0.059509 | 122.2687 | -0.089798 | -0.044312 | 0.00088223 | 0.018023 | -0.0040503 | -0.010743 | -0.0051505 | -0.019196 | 0.0059515 | 0.062354 | 0.046841 | -0.019651 | 0.025272 | -0.0062207 | -0.07782 | -0.050354 | -0.013733 | 0.027466 | 0.16022 | 0.027466 | 0.091553 | 4.8935 | 122.1909 | -0.082397 | 122.1359 | 0.21515 | 0.14191 | 0.15564 | 0.045776 | -122.319 | -122.2412 | 0.21973 | 0.15106 | 0.086975 | 0.10529 | 0.041199 | -0.022888 | -0.07782 | -0.13275 | 0.27466 | 0.21515 | 0.20142 | 0.23804 | 0.2243 | 0.17395 | 0.041199 | 0.29755 | 122.2183 | -0.036621 | 122.2733 | 0.009155 | 122.2504 | -122.2824 | -122.3511 | 0.086975 | 122.1954 | -0.018311 | 4.953
4226.6875 | 122.4152 | -0.050354 | 122.2733 | -0.1432 | -0.042603 | 0.00066863 | 0.021655 | -0.0038367 | -0.0092478 | -0.0030141 | -0.031403 | 0.0085149 | 0.062995 | 0.050473 | -0.016874 | 0.025912 | -0.0021619 | -0.11902 | -0.036621 | -0.022888 | -0.036621 | 0.068665 | -0.064087 | 0.045776 | 4.8065 | 122.2 | -0.073242 | 122.0856 | 0.14648 | 0.073242 | 0.11902 | 0.027466 | -122.3099 | -122.3099 | 0.11902 | 0.09613 | -0.013733 | 0.068664 | -0.041199 | -0.022888 | -0.073242 | -0.18768 | 0.19684 | 0.16937 | 0.1236 | 0.19226 | 0.14648 | 0.091553 | -0.013733 | 0.21973 | 122.1588 | -0.013733 | 122.2733 | 0.013733 | 122.2504 | -122.2961 | -122.3465 | 0.013733 | 122.1359 | -0.068665 | 4.8569
4228.3906 | 122.3831 | -0.082397 | 122.2412 | -0.13557 | -0.042603 | 0.0019504 | 0.024646 | 8.47e-06 | -0.010743 | -0.0053641 | -0.1077 | 0.0070197 | 0.063636 | 0.054959 | -0.02136 | 0.025699 | -0.00045291 | -0.068665 | 0.004578 | -0.036621 | -0.032043 | 0.054932 | -0.07782 | 0.013733 | 4.953 | 122.2275 | -0.082397 | 122.081 | 0.12817 | 0.027466 | 0.091553 | 0.045776 | -122.2366 | -122.2733 | 0.13733 | 0.09613 | 0.004577 | 0.050354 | -0.041199 | 0 | -0.013733 | -0.16022 | 0.21057 | 0.17395 | 0.10986 | 0.17395 | 0.10986 | 0.091553 | 0.004578 | 0.21057 | 122.1634 | 0.041199 | 122.3099 | 0.086975 | 122.3099 | -122.2778 | -122.3236 | 0.050354 | 122.1634 | 0.013732 | 5.0354
4230.0938 | 122.4197 | -0.059509 | 122.2321 | -0.20424 | -0.042603 | 0.0010958 | 0.020373 | -0.0023413 | -0.0090342 | -0.0075003 | -0.031403 | 0.0072333 | 0.064063 | 0.053464 | -0.018797 | 0.02869 | -0.0068615 | -0.11902 | -0.027466 | -0.041199 | -0.027466 | 0.054932 | -0.054932 | 0.041199 | 4.9805 | 122.2229 | -0.09613 | 122.113 | 0.16022 | 0.07782 | 0.10986 | 0.01831 | -122.2595 | -122.2595 | 0.11444 | 0.10071 | 0.004577 | 0.082398 | -0.013733 | -0.036621 | -0.009156 | -0.11902 | 0.21973 | 0.16937 | 0.13733 | 0.20599 | 0.17395 | 0.096131 | 0.013733 | 0.25635 | 122.2092 | 0.013733 | 122.319 | 0.032043 | 122.2824 | -122.2733 | -122.3282 | 0.032043 | 122.1725 | -0.05951 | 5.04
4231.7969 | 122.3282 | -0.09613 | 122.2916 | -0.15083 | -0.040253 | 0.00066863 | 0.023791 | -0.00063233 | -0.010957 | -0.0015189 | -0.13516 | 0.0072333 | 0.062354 | 0.045773 | -0.018156 | 0.026767 | -0.0068615 | -0.10071 | -0.004578 | -0.064087 | -0.068665 | 0.004578 | -0.12817 | -0.036621 | 5.0217 | 122.2458 | -0.086975 | 122.0352 | 0.054932 | -0.050354 | 0.036621 | 0.032043 | -122.2961 | -122.3602 | 0.10071 | 0.059509 | -0.032044 | 0.027466 | -0.064087 | 0.009155 | -0.045776 | -0.25635 | 0.15106 | 0.13275 | 0.045776 | 0.1236 | 0.036621 | 0.068665 | -0.004578 | 0.14191 | 122.1222 | 0.059509 | 122.3328 | 0.091552 | 122.3419 | -122.3557 | -122.3785 | 0.027465 | 122.1313 | -0.004578 | 5.1178
4233.5 | 122.4564 | -0.041199 | 122.2275 | -0.20424 | -0.040467 | 0.0023776 | 0.021014 | -0.0023413 | -0.0083932 | -0.0015189 | -0.055817 | 0.0046697 | 0.061286 | 0.047268 | -0.015165 | 0.025912 | -0.0047253 | -0.059509 | -0.027466 | -0.013733 | 0.027466 | 0.13733 | -0.027466 | 0.073242 | 5.2048 | 122.2046 | -0.064087 | 122.168 | 0.21057 | 0.10986 | 0.16937 | 0.027466 | -122.2549 | -122.2 | 0.17853 | 0.11444 | 0.013733 | 0.086975 | -0.013733 | -0.022888 | -0.022888 | -0.059509 | 0.25177 | 0.21057 | 0.15106 | 0.23346 | 0.17395 | 0.15106 | 0.041199 | 0.27466 | 122.2321 | -0.013733 | 122.2687 | 0.013733 | 122.2458 | -122.2412 | -122.2916 | 0.068665 | 122.2092 | -0.01831 | 5.246
4235.2188 | 122.4289 | -0.036621 | 122.2137 | -0.19661 | -0.042816 | 0.0028048 | 0.020373 | -0.0014867 | -0.010957 | -0.0053641 | -0.055817 | 0.0053107 | 0.061073 | 0.051755 | -0.016233 | 0.028049 | -0.0072889 | -0.07782 | -0.032043 | -0.022888 | 0.013733 | 0.1236 | -0.027466 | 0.059509 | 5.3238 | 122.1909 | -0.082397 | 122.1313 | 0.17395 | 0.10071 | 0.14191 | 0.013733 | -122.2458 | -122.2 | 0.16022 | 0.09613 | 0.009155 | 0.082397 | -0.004578 | -0.045776 | -0.022888 | -0.082397 | 0.21057 | 0.17853 | 0.13733 | 0.2243 | 0.18311 | 0.14648 | 0.036621 | 0.25635 | 122.2137 | -0.009155 | 122.2733 | 0.004578 | 122.2275 | -122.2366 | -122.2961 | 0.050354 | 122.168 | -0.041199 | 5.3604
4236.9219 | 122.3419 | -0.12817 | 122.2778 | -0.074539 | -0.043671 | 0.00088223 | 0.02016 | -0.00041873 | -0.01053 | -0.0053641 | -0.077179 | 0.0083013 | 0.063423 | 0.047696 | -0.017942 | 0.026767 | -0.0025891 | -0.16937 | 0 | -0.064087 | -0.091553 | -0.009155 | -0.10986 | -0.009155 | 5.365 | 122.2733 | -0.11444 | 122.0261 | 0.082397 | -0.009155 | 0.027466 | 0.064087 | -122.2778 | -122.3694 | 0.11902 | 0.11902 | 0.018311 | 0.054932 | -0.045776 | 0.013733 | -0.004578 | -0.25177 | 0.21057 | 0.15564 | 0.11902 | 0.14191 | 0.10529 | 0.054932 | -0.027466 | 0.19684 | 122.1405 | 0.064087 | 122.3877 | 0.12817 | 122.4014 | -122.3419 | -122.3923 | 0.036621 | 122.1542 | -0.041199 | 5.4932
4238.625 | 122.4426 | -0.045776 | 122.2183 | -0.19661 | -0.041321 | 0.004941 | 0.021014 | -0.0012731 | -0.010316 | -0.0064321 | -0.049713 | 0.0050971 | 0.063636 | 0.047482 | -0.019651 | 0.025272 | -0.0055799 | -0.068665 | -0.064087 | -0.013733 | 0.018311 | 0.14191 | -0.022888 | 0.07782 | 5.4886 | 122.2229 | -0.07782 | 122.1405 | 0.20599 | 0.10071 | 0.16937 | 0.032043 | -122.2824 | -122.2 | 0.18768 | 0.1236 | 0.022888 | 0.091553 | -0.009155 | -0.032044 | 0.004577 | -0.07782 | 0.25177 | 0.21515 | 0.14648 | 0.24719 | 0.17853 | 0.15564 | 0.032044 | 0.28381 | 122.2183 | -0.050354 | 122.3007 | -0.018311 | 122.2687 | -122.2321 | -122.2961 | 0.064087 | 122.1863 | -0.022889 | 5.5344
4240.3438 | 122.3419 | -0.11444 | 122.2778 | -0.12032 | -0.043671 | 0.00024143 | 0.020373 | -0.0014867 | -0.011384 | -0.0064321 | -0.058869 | 0.0061651 | 0.062568 | 0.042782 | -0.018797 | 0.025058 | -0.01028 | -0.11902 | -0.009155 | -0.064087 | -0.073242 | 0.036621 | -0.09613 | 0 | 5.5573 | 122.2366 | -0.09613 | 122.0398 | 0.10986 | 0.013733 | 0.041199 | 0.050354 | -122.287 | -122.3511 | 0.15106 | 0.11444 | 0.018311 | 0.064087 | -0.032043 | 0.018311 | -0.041199 | -0.23804 | 0.2243 | 0.15564 | 0.12817 | 0.13733 | 0.10986 | 0.10071 | -0.009155 | 0.20599 | 122.1359 | 0.054932 | 122.3328 | 0.10529 | 122.3511 | -122.3419 | -122.374 | 0.041199 | 122.1542 | -0.004578 | 5.6717
4242.0469 | 122.3831 | -0.10529 | 122.2778 | -0.15083 | -0.044312 | 0.00024143 | 0.024005 | -0.0044775 | -0.010957 | -0.0036551 | -0.11075 | 0.0061651 | 0.060859 | 0.045132 | -0.018583 | 0.028903 | -0.0083569 | -0.10986 | 0.009155 | -0.064087 | -0.059509 | 0.027466 | -0.086975 | 0 | 5.6625 | 122.2412 | -0.10071 | 122.0718 | 0.14648 | 0.022888 | 0.086975 | 0.041199 | -122.2687 | -122.3373 | 0.13275 | 0.10529 | 0.018311 | 0.064087 | -0.022888 | 0.004578 | -0.036621 | -0.20599 | 0.25177 | 0.19226 | 0.12817 | 0.18768 | 0.1236 | 0.091553 | 0.004578 | 0.24719 | 122.1725 | 0.073242 | 122.3419 | 0.11444 | 122.3465 | -122.3419 | -122.3785 | 0.045777 | 122.1771 | -0.004577 | 5.7678
4243.7656 | 122.3923 | -0.082397 | 122.2641 | -0.15083 | -0.042389 | 0.0010958 | 0.019305 | -0.0025549 | -0.013307 | -0.0042959 | -0.025299 | 0.0061651 | 0.062995 | 0.045346 | -0.017301 | 0.025485 | -0.0060071 | -0.073242 | -0.036621 | -0.009155 | -0.004578 | 0.10071 | -0.013733 | 0.054932 | 5.8182 | 122.2 | -0.091553 | 122.0627 | 0.14191 | 0.07782 | 0.07782 | 0.073242 | -122.3007 | -122.2687 | 0.18311 | 0.13733 | 0.068664 | 0.064087 | -0.004578 | -0.009156 | -0.064087 | -0.20142 | 0.2243 | 0.16022 | 0.16022 | 0.16937 | 0.16937 | 0.10986 | 0.004577 | 0.23346 | 122.1542 | -0.027466 | 122.2916 | 0.045776 | 122.2824 | -122.2733 | -122.3557 | 0.077819 | 122.1451 | 0.009155 | 5.9006
4245.4531 | 122.3557 | -0.10986 | 122.2916 | -0.13557 | -0.041321 | 0.00088223 | 0.023364 | -0.0010595 | -0.009675 | -0.0064321 | -0.1077 | 0.0050971 | 0.062995 | 0.047055 | -0.017729 | 0.027194 | -0.0087841 | -0.13733 | 0 | -0.059509 | -0.09613 | -0.032043 | -0.15106 | -0.045776 | 5.6763 | 122.2412 | -0.11902 | 122.0398 | 0.073242 | -0.036621 | 0.059509 | 0.050354 | -122.2916 | -122.3877 | 0.07782 | 0.064087 | -0.041199 | 0.013733 | -0.091553 | -0.009156 | -0.050354 | -0.25177 | 0.18311 | 0.16937 | 0.073242 | 0.17853 | 0.082398 | 0.027466 | -0.036621 | 0.19226 | 122.1588 | 0.059509 | 122.3602 | 0.10986 | 122.3511 | -122.3511 | -122.4106 | 0.013733 | 122.1497 | -0.027466 | 5.7861
4247.1562 | 122.374 | -0.086975 | 122.2733 | -0.13557 | -0.04303 | 0.0010958 | 0.019519 | -0.0036231 | -0.012452 | -0.0045095 | -0.028351 | 0.0061651 | 0.064063 | 0.043637 | -0.017301 | 0.025912 | -0.0049389 | -0.068665 | -0.027466 | -0.036621 | -0.013733 | 0.082397 | -0.013733 | 0.064087 | 5.9875 | 122.2321 | -0.086975 | 122.0627 | 0.14191 | 0.032043 | 0.073242 | 0.050354 | -122.3007 | -122.287 | 0.16937 | 0.15106 | 0.073242 | 0.10071 | 0.022888 | 0 | -0.041198 | -0.21057 | 0.22888 | 0.16022 | 0.11902 | 0.16022 | 0.11902 | 0.11902 | 0.022888 | 0.22888 | 122.1497 | 0.009155 | 122.319 | 0.059509 | 122.319 | -122.3099 | -122.3602 | 0.073242 | 122.1497 | 0.01831 | 6.0745
4248.875 | 122.4243 | -0.068665 | 122.2504 | -0.18898 | -0.040894 | 0.0019504 | 0.0208 | 0.0015039 | -0.010316 | -0.0068593 | -0.028351 | 0.0061651 | 0.062995 | 0.044705 | -0.017088 | 0.026553 | -0.0025891 | -0.10071 | -0.009155 | -0.027466 | -0.041199 | 0.064087 | -0.07782 | 0.036621 | 6.0013 | 122.2229 | -0.082397 | 122.0947 | 0.16479 | 0.064087 | 0.11444 | 0.041199 | -122.2595 | -122.2916 | 0.13275 | 0.10529 | -0.009155 | 0.064087 | -0.050354 | -0.013732 | -0.027466 | -0.15564 | 0.23346 | 0.18311 | 0.13275 | 0.19684 | 0.14648 | 0.091553 | -0.013733 | 0.24719 | 122.1771 | 0.018311 | 122.3053 | 0.05951 | 122.2916 | -122.2778 | -122.3328 | 0.027466 | 122.1634 | -0.032043 | 6.0699
4250.625 | 122.4747 | -0.059509 | 122.1909 | -0.19661 | -0.043244 | 0.00088223 | 0.022296 | -0.00020513 | -0.012025 | -0.0017325 | -0.040558 | 0.0065923 | 0.061927 | 0.041073 | -0.017301 | 0.026981 | -0.0036573 | -0.082397 | -0.027466 | -0.027466 | 0.032043 | 0.14648 | 0.009155 | 0.11444 | 6.2439 | 122.2137 | -0.091553 | 122.1588 | 0.24261 | 0.16022 | 0.16937 | 0.032043 | -122.2183 | -122.1588 | 0.20599 | 0.17395 | 0.068664 | 0.14191 | 0.036621 | -0.032044 | 0.022888 | -0.032044 | 0.30212 | 0.22888 | 0.21973 | 0.26093 | 0.25177 | 0.17395 | 0.059509 | 0.33417 | 122.2504 | 0 | 122.3053 | 0.032043 | 122.2733 | -122.2183 | -122.2824 | 0.091552 | 122.2183 | -0.022888 | 6.3034
4252.3281 | 122.3694 | -0.086975 | 122.2641 | -0.1432 | -0.043671 | 0.0028048 | 0.021869 | 0.00086307 | -0.012879 | -0.0060049 | -0.1138 | 0.0085149 | 0.065559 | 0.048337 | -0.01901 | 0.02634 | -0.0051525 | -0.12817 | 0.018311 | -0.068665 | -0.082397 | -0.013733 | -0.11444 | -0.013733 | 6.1615 | 122.2595 | -0.086975 | 122.0581 | 0.10986 | 0.009155 | 0.064087 | 0.01831 | -122.2458 | -122.3465 | 0.073242 | 0.073242 | -0.027466 | 0.054932 | -0.045776 | 0 | -0.004578 | -0.20599 | 0.19684 | 0.15106 | 0.09613 | 0.15106 | 0.09613 | 0.054932 | -0.013732 | 0.19684 | 122.1451 | 0.086976 | 122.3465 | 0.10529 | 122.3465 | -122.3328 | -122.3511 | 0.004578 | 122.1451 | -0.041199 | 6.2485
4254.0312 | 122.4152 | -0.059509 | 122.2412 | -0.15846 | -0.043885 | 0.002164 | 0.019732 | 0.0051355 | -0.010102 | -0.0021597 | -0.013092 | 0.0050971 | 0.063209 | 0.047482 | -0.017088 | 0.026981 | -0.0045117 | -0.1236 | -0.022888 | -0.036621 | -0.032043 | 0.068665 | -0.082397 | 0.041199 | 6.2622 | 122.2183 | -0.086975 | 122.113 | 0.17395 | 0.082397 | 0.11902 | 0.022888 | -122.2641 | -122.2733 | 0.12817 | 0.10071 | -0.022888 | 0.07782 | -0.045776 | -0.027466 | -0.022888 | -0.12817 | 0.23346 | 0.17853 | 0.14191 | 0.20599 | 0.16937 | 0.10529 | 0.004578 | 0.26092 | 122.2 | 0.013733 | 122.3053 | 0.036621 | 122.2778 | -122.2778 | -122.3282 | 0.027466 | 122.1725 | -0.064087 | 6.3217
4255.7188 | 122.3282 | -0.11902 | 122.2961 | -0.18135 | -0.040253 | 0.0023776 | 0.02315 | 0.0036401 | -0.01117 | -0.0028005 | -0.1199 | 0.0083013 | 0.065132 | 0.049191 | -0.019224 | 0.026126 | -0.0045117 | -0.14191 | 0.004578 | -0.050354 | -0.10529 | -0.064087 | -0.16937 | -0.045776 | 6.2119 | 122.2275 | -0.10529 | 122.0398 | 0.064087 | -0.045776 | 0.045776 | 0.068665 | -122.2916 | -122.4014 | 0.054932 | 0.073243 | -0.050354 | 0.004578 | -0.11902 | 0.013733 | -0.068665 | -0.25635 | 0.18311 | 0.16479 | 0.073243 | 0.15106 | 0.05951 | -0.013733 | -0.054932 | 0.16937 | 122.1451 | 0.054932 | 122.3328 | 0.1236 | 122.3465 | -122.3465 | -122.4014 | 0.013733 | 122.1588 | -0.022888 | 6.3309
4257.4531 | 122.3557 | -0.10529 | 122.2504 | -0.089798 | -0.045166 | 0.001523 | 0.021869 | -0.00084593 | -0.013947 | -0.0032277 | -0.086334 | 0.0076605 | 0.065132 | 0.051968 | -0.016874 | 0.026981 | -0.0060071 | -0.14191 | 0.004578 | -0.059509 | -0.10529 | -0.013733 | -0.10986 | -0.013733 | 6.4087 | 122.2595 | -0.10986 | 122.0306 | 0.10529 | 0 | 0.064087 | 0.045777 | -122.2458 | -122.3557 | 0.091553 | 0.091553 | -0.004577 | 0.045776 | -0.050354 | -0.004577 | 0.009155 | -0.21973 | 0.21057 | 0.16937 | 0.10529 | 0.17395 | 0.10986 | 0.045776 | -0.045777 | 0.21515 | 122.1405 | 0.064087 | 122.3694 | 0.10986 | 122.3648 | -122.3099 | -122.3602 | 0 | 122.1359 | -0.036621 | 6.514
4259.1406 | 122.4152 | -0.073242 | 122.2458 | -0.20424 | -0.042389 | 0.0019504 | 0.021655 | -0.0038367 | -0.011811 | -0.0025869 | -0.019196 | 0.0053107 | 0.062782 | 0.040219 | -0.018156 | 0.025699 | -0.0051525 | -0.11444 | -0.027466 | -0.036621 | -0.027466 | 0.050354 | -0.059509 | 0.032043 | 6.5323 | 122.2229 | -0.09613 | 122.0947 | 0.16937 | 0.07782 | 0.1236 | 0.036621 | -122.2733 | -122.2733 | 0.1236 | 0.10529 | 0.013733 | 0.068664 | -0.022888 | -0.022888 | -0.022889 | -0.15106 | 0.24261 | 0.19684 | 0.15106 | 0.21973 | 0.17395 | 0.086975 | 0.009155 | 0.2655 | 122.1909 | 0.009155 | 122.319 | 0.045776 | 122.2961 | -122.2824 | -122.3419 | 0.045776 | 122.168 | -0.041199 | 6.6055
4260.8594 | 122.4106 | -0.064087 | 122.2458 | -0.22713 | -0.043671 | 0.0017368 | 0.020373 | -0.0027685 | -0.012452 | -0.0060049 | -0.019196 | 0.0036017 | 0.063423 | 0.047268 | -0.018156 | 0.02634 | -0.0019483 | -0.10986 | -0.013733 | -0.032043 | -0.027466 | 0.073242 | -0.059509 | 0.050354 | 6.5872 | 122.2092 | -0.09613 | 122.0901 | 0.17395 | 0.064087 | 0.11902 | 0.032044 | -122.2595 | -122.2733 | 0.13733 | 0.11444 | 0.004578 | 0.082397 | -0.027466 | -0.032043 | -0.036622 | -0.15564 | 0.23804 | 0.18311 | 0.12817 | 0.21515 | 0.16022 | 0.10529 | 0.004577 | 0.27008 | 122.1863 | 0.01831 | 122.3053 | 0.050354 | 122.2733 | -122.2778 | -122.3419 | 0.036621 | 122.1542 | -0.045776 | 6.6513
4262.6094 | 122.4655 | -0.041199 | 122.2321 | -0.16609 | -0.044312 | 0.00024143 | 0.021441 | -0.0055457 | -0.01117 | -0.0075003 | -0.01004 | 0.0046697 | 0.061714 | 0.049191 | -0.018797 | 0.02634 | -0.0066479 | -0.091553 | -0.022888 | -0.036621 | 0.004578 | 0.11444 | -0.013733 | 0.091553 | 6.7886 | 122.2137 | -0.082397 | 122.1588 | 0.23346 | 0.15564 | 0.17395 | 0.004578 | -122.2549 | -122.2275 | 0.15564 | 0.13275 | 0.027466 | 0.12817 | 0.022888 | -0.041198 | -0.018311 | -0.073243 | 0.27466 | 0.21515 | 0.19684 | 0.25635 | 0.23804 | 0.15106 | 0.041199 | 0.31586 | 122.2412 | 0.013733 | 122.2961 | 0.018311 | 122.2549 | -122.2687 | -122.3145 | 0.045777 | 122.2 | -0.050354 | 6.8298
4264.2969 | 122.374 | -0.10071 | 122.2687 | -0.12794 | -0.04538 | 0.0040866 | 0.023791 | 0.00022207 | -0.010743 | -0.00023714 | -0.1138 | 0.0068059 | 0.062141 | 0.045132 | -0.018797 | 0.026553 | -0.0028027 | -0.11902 | -0.004578 | -0.054932 | -0.054932 | 0.004578 | -0.10071 | 0.013733 | 6.7566 | 122.2412 | -0.09613 | 122.081 | 0.12817 | 0.018311 | 0.068665 | 0.045776 | -122.2733 | -122.3236 | 0.10529 | 0.11444 | 0 | 0.068665 | -0.045776 | 0.004578 | -0.027466 | -0.18768 | 0.22888 | 0.16937 | 0.11902 | 0.16479 | 0.11444 | 0.05951 | 0 | 0.2243 | 122.1771 | 0.050354 | 122.3373 | 0.09613 | 122.3419 | -122.3236 | -122.3648 | 0.045776 | 122.1817 | -0.018311 | 6.8573
4266 | 122.4609 | -0.050354 | 122.2229 | -0.18135 | -0.040253 | 0.002164 | 0.021655 | 0.0038537 | -0.009675 | -0.0047231 | -0.058869 | 0.0065923 | 0.061714 | 0.054532 | -0.017088 | 0.026981 | -0.0064343 | -0.050354 | -0.050354 | -0.018311 | 0.041199 | 0.14648 | -0.036621 | 0.064087 | 6.8848 | 122.2092 | -0.064087 | 122.168 | 0.21973 | 0.1236 | 0.1831 | 0.032043 | -122.2733 | -122.1817 | 0.19684 | 0.11444 | 0.013733 | 0.082398 | -0.01831 | -0.013733 | -0.013733 | -0.054931 | 0.27008 | 0.23346 | 0.17395 | 0.24719 | 0.18768 | 0.16479 | 0.05951 | 0.28381 | 122.2321 | -0.032043 | 122.2733 | 0 | 122.2595 | -122.2412 | -122.287 | 0.091553 | 122.2183 | 0 | 6.9351
4267.7031 | 122.3877 | -0.10071 | 122.2687 | -0.12032 | -0.042176 | 0.00088223 | 0.023791 | 0.0019311 | -0.010102 | -0.0042959 | -0.09549 | 0.0059515 | 0.0615 | 0.051541 | -0.017729 | 0.02634 | -0.0060071 | -0.11902 | 0.027466 | -0.068665 | -0.054932 | 0.009155 | -0.086975 | 0.009155 | 6.9489 | 122.2733 | -0.10986 | 122.081 | 0.16479 | 0.022888 | 0.086975 | 0.032043 | -122.2412 | -122.3236 | 0.10986 | 0.10986 | 0.013733 | 0.07782 | -0.01831 | -0.009155 | 0.004577 | -0.18768 | 0.2655 | 0.18768 | 0.1236 | 0.19684 | 0.13275 | 0.07782 | 0.013733 | 0.27466 | 122.1909 | 0.096131 | 122.3831 | 0.12817 | 122.374 | -122.3373 | -122.3785 | 0.045776 | 122.1817 | -0.018311 | 7.0496
4269.3906 | 122.4472 | -0.059509 | 122.2504 | -0.19661 | -0.039612 | 0.0013094 | 0.021014 | -0.0019141 | -0.0092478 | -0.0047231 | -0.046661 | 0.0044561 | 0.062995 | 0.051755 | -0.01666 | 0.027621 | -0.0075025 | -0.059509 | -0.050354 | 0 | 0.036621 | 0.13733 | -0.022888 | 0.07782 | 7.0633 | 122.2183 | -0.068665 | 122.1542 | 0.21973 | 0.10529 | 0.15564 | 0.059509 | -122.3007 | -122.2137 | 0.19684 | 0.13733 | 0.036621 | 0.07782 | -0.022888 | -0.009156 | -0.032043 | -0.09613 | 0.27924 | 0.21515 | 0.16479 | 0.22431 | 0.17395 | 0.13733 | 0.036621 | 0.28839 | 122.2229 | -0.050354 | 122.287 | 0.009155 | 122.2778 | -122.2504 | -122.319 | 0.09613 | 122.2137 | 0 | 7.1228
4271.0938 | 122.3831 | -0.082397 | 122.2504 | -0.12032 | -0.041321 | 0.00066863 | 0.024218 | -0.0014867 | -0.010957 | -0.0028005 | -0.11685 | 0.0063787 | 0.060645 | 0.052182 | -0.019651 | 0.026767 | -0.0028027 | -0.091553 | 0 | -0.036621 | -0.032043 | 0.054932 | -0.082397 | 0.009155 | 7.1457 | 122.2412 | -0.082397 | 122.0993 | 0.15106 | 0.036621 | 0.086975 | 0.045776 | -122.2504 | -122.2824 | 0.13733 | 0.091552 | 0 | 0.045776 | -0.045776 | 0 | -0.009155 | -0.15106 | 0.23346 | 0.16937 | 0.11902 | 0.16937 | 0.11902 | 0.091553 | 0.004578 | 0.23346 | 122.1817 | 0.036621 | 122.3236 | 0.082397 | 122.3236 | -122.287 | -122.3328 | 0.050354 | 122.1817 | -0.009156 | 7.2281
4272.7969 | 122.4747 | -0.054932 | 122.2137 | -0.16609 | -0.044098 | 0.00066863 | 0.020587 | -0.00020513 | -0.01117 | -0.0049367 | -0.034454 | 0.0048833 | 0.062141 | 0.044278 | -0.01602 | 0.025485 | -0.0013073 | -0.07782 | -0.054932 | -0.050354 | 0.041199 | 0.17395 | 0.036621 | 0.12817 | 7.3471 | 122.1863 | -0.073242 | 122.1497 | 0.28839 | 0.17853 | 0.1831 | 0.004578 | -122.2687 | -122.1725 | 0.22888 | 0.18311 | 0.091553 | 0.17853 | 0.086975 | -0.01831 | -0.027466 | -0.064087 | 0.34332 | 0.23804 | 0.23346 | 0.25635 | 0.25177 | 0.2243 | 0.091553 | 0.36163 | 122.2229 | -0.004578 | 122.2595 | 0 | 122.2412 | -122.2641 | -122.287 | 0.096131 | 122.2046 | -0.022888 | 7.402
4274.5312 | 122.3923 | -0.086975 | 122.2778 | -0.15083 | -0.041748 | 2.7834e-05 | 0.022509 | 0.0017175 | -0.012452 | -0.0045095 | -0.12296 | 0.0068059 | 0.064063 | 0.043637 | -0.018369 | 0.026767 | -0.0040845 | -0.10071 | 0 | -0.068665 | -0.041199 | 0.054932 | -0.073242 | 0.009155 | 7.2968 | 122.2366 | -0.10071 | 122.081 | 0.15564 | 0.036621 | 0.09613 | 0.01831 | -122.2778 | -122.319 | 0.14191 | 0.09613 | 0.013733 | 0.07782 | -0.004577 | -0.013733 | -0.041199 | -0.19684 | 0.24261 | 0.1831 | 0.1236 | 0.19684 | 0.13733 | 0.1236 | 0.027466 | 0.25635 | 122.1817 | 0.068665 | 122.3373 | 0.086975 | 122.3236 | -122.3465 | -122.3785 | 0.045776 | 122.168 | -0.013733 | 7.3837
4276.2344 | 122.4106 | -0.07782 | 122.2229 | -0.19661 | -0.040253 | 0.00088223 | 0.019091 | 0.0036401 | -0.011384 | -0.0028005 | -0.025299 | 0.0048833 | 0.062782 | 0.040219 | -0.01666 | 0.025912 | -0.0034435 | -0.11444 | -0.036621 | -0.022888 | -0.018311 | 0.10071 | -0.054932 | 0.050354 | 7.37 | 122.2046 | -0.073242 | 122.0947 | 0.18768 | 0.07782 | 0.11444 | 0.054932 | -122.2595 | -122.2412 | 0.17853 | 0.12817 | 0.022888 | 0.073242 | -0.032044 | 0.004578 | -0.01831 | -0.12817 | 0.2655 | 0.19226 | 0.15564 | 0.18768 | 0.15106 | 0.1236 | 0.004577 | 0.26092 | 122.168 | -0.013733 | 122.2778 | 0.041199 | 122.2824 | -122.2458 | -122.2961 | 0.059509 | 122.1725 | -0.036621 | 7.4478
4277.9531 | 122.4518 | -0.064087 | 122.2458 | -0.16609 | -0.044312 | 0.0010958 | 0.018664 | 0.0010767 | -0.011598 | -0.0053641 | -0.034454 | 0.0046697 | 0.062782 | 0.051755 | -0.018156 | 0.025058 | -0.0049389 | -0.068665 | -0.032043 | -0.032043 | 0.045776 | 0.13733 | 0.009155 | 0.10071 | 7.608 | 122.2137 | -0.064087 | 122.1313 | 0.2243 | 0.14648 | 0.17395 | 0.032044 | -122.2778 | -122.2 | 0.20142 | 0.1648 | 0.073242 | 0.13275 | 0.041198 | 0 | -0.032044 | -0.11444 | 0.28839 | 0.23804 | 0.21057 | 0.23804 | 0.21057 | 0.16937 | 0.077819 | 0.28839 | 122.1954 | 0 | 122.2778 | 0.032044 | 122.2778 | -122.2778 | -122.3099 | 0.10986 | 122.1954 | -0.004578 | 7.6721
4279.6719 | 122.4564 | -0.054932 | 122.2504 | -0.1432 | -0.043457 | 0.00024143 | 0.019305 | -0.0019141 | -0.011598 | -0.0040823 | -0.016144 | 0.0048833 | 0.062354 | 0.049618 | -0.019224 | 0.025699 | -0.0015209 | -0.064087 | -0.050354 | -0.032043 | 0.041199 | 0.16479 | 0.018311 | 0.10071 | 7.7042 | 122.1909 | -0.068665 | 122.1497 | 0.2655 | 0.15106 | 0.17853 | 0.022889 | -122.3007 | -122.2092 | 0.21973 | 0.15564 | 0.073243 | 0.13275 | 0.050354 | -0.013733 | -0.059509 | -0.10071 | 0.32043 | 0.23346 | 0.20599 | 0.24719 | 0.21973 | 0.19684 | 0.073242 | 0.33417 | 122.2183 | -0.018311 | 122.2595 | 0.004578 | 122.2458 | -122.2824 | -122.319 | 0.096131 | 122.2046 | -0.009155 | 7.7591
4281.3594 | 122.3694 | -0.091553 | 122.2778 | -0.1432 | -0.044739 | 0.0017368 | 0.019946 | -0.0017005 | -0.01117 | -0.0057913 | -0.040558 | 0.0057379 | 0.065345 | 0.047055 | -0.018156 | 0.027408 | -0.0019483 | -0.068665 | -0.036621 | -0.050354 | 0.009155 | 0.10071 | -0.009155 | 0.07782 | 7.7133 | 122.2412 | -0.086975 | 122.0718 | 0.16937 | 0.059509 | 0.10071 | 0.041199 | -122.3145 | -122.2687 | 0.19226 | 0.16937 | 0.082398 | 0.12817 | 0.041199 | 0.004578 | -0.036621 | -0.20599 | 0.26093 | 0.19226 | 0.15106 | 0.18768 | 0.14648 | 0.15106 | 0.059509 | 0.25635 | 122.1588 | 0.013733 | 122.3282 | 0.054932 | 122.3328 | -122.3282 | -122.3648 | 0.10071 | 122.1634 | 0.022888 | 7.8049
4283.0781 | 122.3785 | -0.064087 | 122.2641 | -0.12794 | -0.040253 | 2.7834e-05 | 0.028064 | 0.0015039 | -0.012879 | -0.0023733 | -0.11685 | 0.0080877 | 0.059577 | 0.048123 | -0.01901 | 0.027194 | -0.0079297 | -0.091553 | 0.004578 | -0.064087 | -0.027466 | 0.059509 | -0.073242 | 0.022888 | 7.7454 | 122.2412 | -0.10071 | 122.0993 | 0.16479 | 0.041199 | 0.10071 | 0 | -122.2595 | -122.2916 | 0.1236 | 0.086975 | -0.009155 | 0.086975 | -0.009155 | -0.036621 | -0.022888 | -0.16479 | 0.22888 | 0.1648 | 0.10529 | 0.20142 | 0.14191 | 0.1236 | 0.036621 | 0.2655 | 122.2 | 0.068665 | 122.3419 | 0.068665 | 122.3053 | -122.3282 | -122.3648 | 0.036621 | 122.1634 | -0.027466 | 7.8094
4284.7812 | 122.3557 | -0.10529 | 122.2641 | -0.15083 | -0.043671 | 0.00045503 | 0.020587 | -0.00063233 | -0.015016 | -0.0042959 | -0.040558 | 0.0059515 | 0.062782 | 0.050259 | -0.017515 | 0.02399 | -0.0040845 | -0.082397 | -0.036621 | -0.050354 | -0.013733 | 0.068665 | -0.041199 | 0.045776 | 7.8506 | 122.2229 | -0.091553 | 122.0215 | 0.13275 | 0.018311 | 0.054932 | 0.054932 | -122.3007 | -122.2778 | 0.17395 | 0.15106 | 0.064087 | 0.09613 | 0.009155 | 0.013733 | -0.041199 | -0.24262 | 0.23804 | 0.16022 | 0.1236 | 0.14649 | 0.10986 | 0.11902 | 0.036621 | 0.2243 | 122.113 | 0.013733 | 122.3145 | 0.068665 | 122.3282 | -122.3145 | -122.3557 | 0.091553 | 122.1268 | 0.022889 | 7.9559
4286.4688 | 122.4564 | -0.068665 | 122.2366 | -0.1432 | -0.041107 | 0.001523 | 0.022509 | -0.0017005 | -0.011384 | -0.0042959 | -0.083283 | 0.0072333 | 0.061286 | 0.051114 | -0.020078 | 0.02634 | -0.01092 | -0.064087 | -0.027466 | -0.032043 | 0.013733 | 0.10071 | -0.045776 | 0.054932 | 7.9285 | 122.1954 | -0.068665 | 122.1497 | 0.2243 | 0.10071 | 0.19226 | 0.036622 | -122.2641 | -122.2229 | 0.16937 | 0.1236 | 0.022889 | 0.086975 | -0.013733 | 0 | -0.041198 | -0.086975 | 0.29297 | 0.26093 | 0.16937 | 0.26093 | 0.16937 | 0.13275 | 0.045776 | 0.29297 | 122.2183 | 0.004577 | 122.2641 | 0.041199 | 122.2641 | -122.2687 | -122.3053 | 0.082398 | 122.2183 | 0.004578 | 7.9971
4288.1719 | 122.3419 | -0.10529 | 122.287 | -0.15083 | -0.044953 | 0.00045503 | 0.022296 | -0.0044775 | -0.011384 | -0.0064321 | -0.052765 | 0.0063787 | 0.064491 | 0.0509 | -0.017729 | 0.027835 | -0.0066479 | -0.15106 | 0 | -0.068665 | -0.09613 | -0.013733 | -0.1236 | -0.018311 | 7.9651 | 122.2412 | -0.10529 | 122.0169 | 0.10986 | -0.004578 | 0.054932 | 0.036621 | -122.287 | -122.3831 | 0.091553 | 0.086975 | -0.01831 | 0.050354 | -0.054931 | 0 | -0.045776 | -0.27008 | 0.21515 | 0.16022 | 0.10071 | 0.16022 | 0.10071 | 0.054932 | -0.027465 | 0.21515 | 122.1222 | 0.068665 | 122.3465 | 0.10529 | 122.3465 | -122.3557 | -122.3923 | 0.009156 | 122.1222 | -0.045776 | 8.0704
4289.8906 | 122.4976 | -0.054932 | 122.2412 | -0.13557 | -0.042603 | -0.00039957 | 0.019946 | -0.0019141 | -0.0090342 | -0.0034415 | -0.022247 | 0.0044561 | 0.062141 | 0.040646 | -0.018583 | 0.025485 | -0.0025891 | -0.068665 | -0.032043 | -0.009155 | 0.045776 | 0.15564 | 0.018311 | 0.1236 | 8.2214 | 122.1909 | -0.073242 | 122.1542 | 0.27924 | 0.17395 | 0.18768 | 0.045777 | -122.2733 | -122.1954 | 0.21057 | 0.17853 | 0.073243 | 0.13275 | 0.027466 | -0.01831 | -0.050354 | -0.086975 | 0.33417 | 0.24261 | 0.22888 | 0.26092 | 0.24719 | 0.16479 | 0.054931 | 0.35248 | 122.2275 | -0.022888 | 122.2641 | 0.022889 | 122.2458 | -122.2504 | -122.3145 | 0.10071 | 122.2092 | -0.013733 | 8.2764
4291.6406 | 122.3923 | -0.09613 | 122.2595 | -0.12032 | -0.042389 | 0.00088223 | 0.023578 | 0.0021447 | -0.012666 | -0.0025869 | -0.092438 | 0.0074469 | 0.062141 | 0.048337 | -0.019865 | 0.027408 | -0.0081433 | -0.091553 | 0.004578 | -0.073242 | -0.036621 | 0.050354 | -0.07782 | 0.009155 | 8.1757 | 122.2458 | -0.10529 | 122.0993 | 0.17395 | 0.036621 | 0.10071 | 0.022888 | -122.2549 | -122.2961 | 0.14648 | 0.10528 | 0.01831 | 0.082397 | -0.004578 | -0.009156 | -0.013732 | -0.16022 | 0.27008 | 0.19684 | 0.13275 | 0.20599 | 0.14191 | 0.1236 | 0.036621 | 0.27924 | 122.2046 | 0.07782 | 122.3511 | 0.10071 | 122.3419 | -122.3328 | -122.3648 | 0.059509 | 122.1954 | 0.004577 | 8.2718
4293.3438 | 122.4609 | -0.045776 | 122.2412 | -0.15846 | -0.041535 | 0.0013094 | 0.019091 | -0.0019141 | -0.012239 | -0.0060049 | -0.01004 | 0.0070197 | 0.062354 | 0.042355 | -0.017729 | 0.027408 | -0.0025891 | -0.073242 | -0.036621 | -0.018311 | 0.036621 | 0.16479 | 0.018311 | 0.09613 | 8.3862 | 122.2 | -0.07782 | 122.1268 | 0.25635 | 0.13733 | 0.16022 | 0.027465 | -122.2778 | -122.2046 | 0.21057 | 0.14191 | 0.064087 | 0.11444 | 0.036622 | -0.032044 | -0.041199 | -0.11444 | 0.30212 | 0.20599 | 0.18311 | 0.23804 | 0.21515 | 0.18311 | 0.054932 | 0.33417 | 122.2046 | -0.01831 | 122.2778 | 0.009155 | 122.2458 | -122.2595 | -122.319 | 0.082397 | 122.1725 | -0.027466 | 8.432
4295.0469 | 122.3282 | -0.10529 | 122.2687 | -0.12794 | -0.044098 | 0.00088223 | 0.023791 | -0.00020513 | -0.012666 | -0.0060049 | -0.098541 | 0.0078741 | 0.063636 | 0.045559 | -0.018369 | 0.026767 | -0.0032299 | -0.15106 | 0.009155 | -0.073242 | -0.10986 | -0.036621 | -0.10529 | -0.013733 | 8.3038 | 122.2504 | -0.11902 | 122.0306 | 0.10529 | -0.004578 | 0.032043 | 0.032044 | -122.2595 | -122.3785 | 0.068665 | 0.091553 | 0 | 0.059509 | -0.032044 | -0.013733 | -0.018311 | -0.23804 | 0.21057 | 0.13733 | 0.10071 | 0.15106 | 0.11444 | 0.036621 | -0.036621 | 0.22431 | 122.1497 | 0.082397 | 122.3694 | 0.11444 | 122.3557 | -122.3419 | -122.3877 | -0.004577 | 122.1359 | -0.045776 | 8.4091
4296.7344 | 122.4197 | -0.07782 | 122.2366 | -0.19661 | -0.042389 | 0.00088223 | 0.019946 | 0.00064947 | -0.010957 | -0.0034415 | -0.013092 | 0.0068059 | 0.063423 | 0.045773 | -0.016874 | 0.025485 | -0.0021619 | -0.11444 | -0.022888 | -0.032043 | -0.032043 | 0.054932 | -0.064087 | 0.032043 | 8.4457 | 122.2092 | -0.09613 | 122.0901 | 0.1831 | 0.073242 | 0.11902 | 0.045777 | -122.2595 | -122.2687 | 0.13275 | 0.10986 | 0.013733 | 0.064086 | -0.032044 | -0.01831 | -0.027466 | -0.14648 | 0.26092 | 0.19684 | 0.15106 | 0.21515 | 0.16937 | 0.086975 | 0 | 0.27924 | 122.1863 | 0.009155 | 122.3053 | 0.054932 | 122.287 | -122.2687 | -122.3328 | 0.045777 | 122.168 | -0.036621 | 8.5236
4298.4375 | 122.3877 | -0.086975 | 122.2595 | -0.12794 | -0.041748 | 0.002164 | 0.023578 | -0.0057593 | -0.013093 | -0.0064321 | -0.1138 | 0.0083013 | 0.0615 | 0.052182 | -0.017515 | 0.026553 | -0.0028027 | -0.07782 | 0.004578 | -0.068665 | -0.036621 | 0.050354 | -0.073242 | 0.009155 | 8.5739 | 122.2458 | -0.09613 | 122.0718 | 0.16937 | 0.041199 | 0.11444 | 0.01831 | -122.2549 | -122.2961 | 0.13733 | 0.09613 | 0.013733 | 0.07782 | -0.004577 | -0.009155 | -0.013732 | -0.18768 | 0.25635 | 0.20142 | 0.12817 | 0.21057 | 0.13733 | 0.11902 | 0.032044 | 0.2655 | 122.168 | 0.073243 | 122.3419 | 0.091553 | 122.3328 | -122.3282 | -122.3557 | 0.050354 | 122.1588 | 0.009155 | 8.6609
4300.1875 | 122.3328 | -0.11444 | 122.2687 | -0.17372 | -0.043671 | 2.7834e-05 | 0.022082 | -0.0014867 | -0.010743 | -0.0036551 | -0.049713 | 0.0068059 | 0.062354 | 0.045132 | -0.018583 | 0.026553 | -0.0040845 | -0.15564 | 0.009155 | -0.064087 | -0.10071 | 0.013733 | -0.10071 | -0.013733 | 8.6151 | 122.2595 | -0.10071 | 122.0078 | 0.11444 | -0.004578 | 0.041199 | 0.050354 | -122.2595 | -122.3694 | 0.12817 | 0.10071 | 0.013733 | 0.050354 | -0.036621 | 0.013733 | -0.009156 | -0.26093 | 0.22888 | 0.15564 | 0.10986 | 0.14191 | 0.09613 | 0.07782 | -0.036621 | 0.21515 | 122.1085 | 0.073242 | 122.3602 | 0.1236 | 122.374 | -122.3328 | -122.3694 | 0.013733 | 122.1222 | -0.041199 | 8.7296
4301.8906 | 122.4747 | -0.059509 | 122.2229 | -0.13557 | -0.045166 | 0.0019504 | 0.022723 | -0.0012731 | -0.012025 | -0.0040823 | -0.013092 | 0.0059515 | 0.063423 | 0.042782 | -0.017515 | 0.029117 | -0.0070751 | -0.10986 | -0.022888 | -0.032043 | -0.004578 | 0.10529 | -0.013733 | 0.086975 | 8.812 | 122.1909 | -0.082397 | 122.1268 | 0.24261 | 0.15106 | 0.16479 | 0.027466 | -122.2458 | -122.2275 | 0.16479 | 0.14648 | 0.045776 | 0.11902 | 0.01831 | -0.022888 | -0.032043 | -0.09613 | 0.30212 | 0.2243 | 0.21057 | 0.24719 | 0.23346 | 0.13733 | 0.027465 | 0.32501 | 122.2092 | 0.009155 | 122.2733 | 0.036621 | 122.2504 | -122.2549 | -122.3053 | 0.054931 | 122.1863 | -0.050354 | 8.8715
4303.6406 | 122.3969 | -0.10071 | 122.2504 | -0.17372 | -0.042389 | 0.0017368 | 0.022937 | 0.0015039 | -0.012666 | -0.0010915 | -0.1077 | 0.0040289 | 0.064491 | 0.053464 | -0.019224 | 0.027194 | -0.0051525 | -0.091553 | 0.009155 | -0.059509 | -0.027466 | 0.064087 | -0.082397 | 0.009155 | 8.8669 | 122.2183 | -0.091553 | 122.081 | 0.1831 | 0.045776 | 0.10071 | 0.041199 | -122.2412 | -122.2778 | 0.1648 | 0.10986 | 0.018311 | 0.068664 | -0.022888 | 0.009155 | -0.032043 | -0.16937 | 0.28381 | 0.20142 | 0.14648 | 0.19226 | 0.13733 | 0.1236 | 0.032043 | 0.27466 | 122.1725 | 0.068664 | 122.3099 | 0.10986 | 122.319 | -122.3099 | -122.3419 | 0.073242 | 122.1817 | 0.009155 | 8.9676
4305.375 | 122.3511 | -0.10071 | 122.2778 | -0.082169 | -0.044953 | 0.0017368 | 0.022509 | 0.00086307 | -0.010743 | -0.0028005 | -0.068024 | 0.0072333 | 0.062568 | 0.048977 | -0.017729 | 0.025699 | -0.0062207 | -0.14191 | 0.004578 | -0.064087 | -0.11444 | -0.018311 | -0.11902 | -0.022888 | 8.8943 | 122.2366 | -0.12817 | 122.0306 | 0.13733 | 0.004578 | 0.045776 | 0.036621 | -122.2733 | -122.3923 | 0.082397 | 0.07782 | -0.018311 | 0.041199 | -0.054932 | -0.027466 | -0.041199 | -0.24719 | 0.23804 | 0.14648 | 0.10529 | 0.17395 | 0.13275 | 0.045776 | -0.050354 | 0.2655 | 122.1588 | 0.068665 | 122.3648 | 0.10529 | 122.3373 | -122.3419 | -122.406 | -0.013733 | 122.1313 | -0.041199 | 8.9951
4307.0781 | 122.4335 | -0.082397 | 122.2275 | -0.15083 | -0.042176 | 0.0036594 | 0.024005 | -0.00020513 | -0.010743 | -0.0049367 | -0.10159 | 0.0074469 | 0.064918 | 0.041287 | -0.019651 | 0.027621 | -0.0036573 | -0.10986 | -0.009155 | -0.041199 | -0.036621 | 0.064087 | -0.09613 | 0.018311 | 8.9859 | 122.1954 | -0.082397 | 122.1405 | 0.21515 | 0.082397 | 0.16479 | 0.041198 | -122.2366 | -122.2641 | 0.14648 | 0.10071 | -0.013733 | 0.05951 | -0.054931 | 0 | -0.032043 | -0.086975 | 0.29755 | 0.24719 | 0.16479 | 0.24719 | 0.16479 | 0.10529 | 0.004578 | 0.29755 | 122.2229 | 0.032044 | 122.2778 | 0.073242 | 122.2778 | -122.2687 | -122.3099 | 0.045776 | 122.2229 | -0.027466 | 9.0683
4308.8125 | 122.3877 | -0.073242 | 122.2961 | -0.12032 | -0.042176 | 0.0023776 | 0.019519 | 0.00064947 | -0.012239 | -0.0021597 | -0.089386 | 0.0050971 | 0.064491 | 0.042782 | -0.018369 | 0.027835 | -0.0053661 | -0.11902 | 0.004578 | -0.050354 | -0.073242 | 0.004578 | -0.07782 | 0.004578 | 9.0866 | 122.2229 | -0.09613 | 122.0718 | 0.17853 | 0.022888 | 0.086975 | 0.022888 | -122.2916 | -122.3694 | 0.07782 | 0.07782 | -0.004578 | 0.054932 | -0.027466 | -0.022888 | -0.073243 | -0.22431 | 0.25177 | 0.16022 | 0.09613 | 0.1831 | 0.11902 | 0.054932 | -0.022888 | 0.27466 | 122.168 | 0.054932 | 122.319 | 0.07782 | 122.2961 | -122.3465 | -122.3923 | 0 | 122.1451 | -0.045777 | 9.1599
4310.6094 | 122.3511 | -0.086975 | 122.2733 | -0.1432 | -0.041107 | 0.0013094 | 0.024432 | -0.00041873 | -0.011384 | -0.0034415 | -0.077179 | 0.0080877 | 0.062995 | 0.044278 | -0.020078 | 0.02634 | -0.0062207 | -0.13275 | -0.013733 | -0.054932 | -0.09613 | -0.027466 | -0.16022 | -0.027466 | 9.0775 | 122.2321 | -0.091553 | 122.0306 | 0.11444 | -0.013733 | 0.054932 | 0.032043 | -122.287 | -122.3694 | 0.059509 | 0.059509 | -0.073242 | 0.027466 | -0.10528 | -0.004578 | -0.041198 | -0.24261 | 0.20142 | 0.14191 | 0.073242 | 0.14649 | 0.07782 | 0.027466 | -0.041198 | 0.20599 | 122.1222 | 0.041199 | 122.3236 | 0.073242 | 122.319 | -122.3282 | -122.3648 | -0.009155 | 122.1176 | -0.045776 | 9.1644
4312.3906 | 122.3282 | -0.082397 | 122.287 | -0.15083 | -0.039398 | 0.0025912 | 0.022082 | 0.0032129 | -0.010102 | -0.0036551 | -0.098541 | 0.0065923 | 0.062141 | 0.048123 | -0.01666 | 0.027194 | -0.0032299 | -0.09613 | 0.004578 | -0.059509 | -0.068665 | 0.013733 | -0.12817 | -0.027466 | 9.2468 | 122.2504 | -0.10529 | 122.0306 | 0.11444 | -0.018311 | 0.050354 | 0.022888 | -122.2824 | -122.3557 | 0.09613 | 0.054931 | -0.045777 | 0.032043 | -0.068665 | -0.022889 | -0.036621 | -0.25635 | 0.19684 | 0.13275 | 0.064086 | 0.15564 | 0.086975 | 0.073242 | -0.009156 | 0.21973 | 122.1359 | 0.064087 | 122.3557 | 0.086975 | 122.3328 | -122.3465 | -122.3923 | 0.013732 | 122.113 | -0.013733 | 9.3292
4314.125 | 122.3557 | -0.10986 | 122.2824 | -0.10506 | -0.044739 | -0.001254 | 0.021655 | -0.00041873 | -0.013734 | -0.0064321 | -0.040558 | 0.0057379 | 0.062995 | 0.041714 | -0.016447 | 0.027621 | -0.0098523 | -0.15564 | 0.004578 | -0.073242 | -0.09613 | -0.004578 | -0.11902 | -0.013733 | 9.3704 | 122.2458 | -0.11444 | 122.0215 | 0.1236 | -0.013733 | 0.050354 | 0.036621 | -122.2778 | -122.3785 | 0.10529 | 0.09613 | -0.009156 | 0.059509 | -0.045777 | -0.004578 | -0.036621 | -0.26093 | 0.23346 | 0.16022 | 0.09613 | 0.16479 | 0.10071 | 0.068664 | -0.022888 | 0.23804 | 122.1359 | 0.07782 | 122.3602 | 0.11444 | 122.3557 | -122.3557 | -122.3969 | 0.013733 | 122.1313 | -0.045777 | 9.4803
4315.8906 | 122.438 | -0.059509 | 122.2366 | -0.20424 | -0.042816 | 0.0010958 | 0.019091 | -0.0027685 | -0.01352 | -0.0030141 | -0.0069885 | 0.0074469 | 0.064491 | 0.042142 | -0.016874 | 0.02869 | -0.0049389 | -0.073242 | -0.036621 | -0.018311 | 0.013733 | 0.14191 | -0.004578 | 0.082397 | 9.613 | 122.2 | -0.064087 | 122.1039 | 0.25177 | 0.1236 | 0.14191 | 0.041198 | -122.2733 | -122.2229 | 0.20142 | 0.14191 | 0.054931 | 0.10071 | 0.013733 | -0.004578 | -0.036621 | -0.13275 | 0.31128 | 0.20142 | 0.1831 | 0.20599 | 0.18768 | 0.16022 | 0.032044 | 0.31586 | 122.168 | -0.01831 | 122.2641 | 0.022888 | 122.2595 | -122.2549 | -122.3007 | 0.073242 | 122.1634 | -0.013733 | 9.6725
4317.6562 | 122.3602 | -0.10071 | 122.2824 | -0.17372 | -0.043671 | 0.00088223 | 0.022296 | -0.00041873 | -0.012879 | -0.0042959 | -0.071076 | 0.0087287 | 0.062782 | 0.045987 | -0.018369 | 0.027408 | -0.0047253 | -0.15106 | 0.004578 | -0.073242 | -0.10071 | -0.018311 | -0.11902 | -0.022888 | 9.5856 | 122.2458 | -0.1236 | 122.0306 | 0.14648 | 0.009155 | 0.068665 | 0.027466 | -122.2778 | -122.3831 | 0.082397 | 0.07782 | -0.018311 | 0.050354 | -0.045777 | -0.022888 | -0.036621 | -0.25177 | 0.24719 | 0.16937 | 0.10986 | 0.19226 | 0.13275 | 0.054931 | -0.027466 | 0.27008 | 122.1542 | 0.07782 | 122.3694 | 0.10529 | 122.3465 | -122.3557 | -122.406 | 0 | 122.1313 | -0.050354 | 9.6863
4319.3594 | 122.4884 | -0.045776 | 122.2366 | -0.17372 | -0.041962 | 0.00024143 | 0.021655 | -0.0017005 | -0.012666 | -0.0064321 | 0.017425 | 0.0065923 | 0.062995 | 0.043423 | -0.019651 | 0.026553 | -0.0030163 | -0.064087 | -0.022888 | -0.032043 | 0.027466 | 0.15106 | 0.009155 | 0.086975 | 9.8282 | 122.1863 | -0.073242 | 122.1451 | 0.28839 | 0.16022 | 0.17853 | 0.013733 | -122.2595 | -122.2092 | 0.19684 | 0.13275 | 0.054931 | 0.11902 | 0.041198 | -0.027466 | -0.050354 | -0.091552 | 0.33417 | 0.2243 | 0.20599 | 0.25177 | 0.23346 | 0.18311 | 0.059509 | 0.36163 | 122.2183 | 0.009155 | 122.2595 | 0.022888 | 122.2321 | -122.2687 | -122.3099 | 0.073242 | 122.1909 | -0.018311 | 9.874
4321.125 | 122.4289 | -0.073242 | 122.2549 | -0.16609 | -0.04303 | 0.00088223 | 0.019946 | 0.00086307 | -0.010957 | -0.0070731 | -0.019196 | 0.0057379 | 0.062568 | 0.041073 | -0.019651 | 0.025912 | -0.0038709 | -0.10529 | -0.036621 | -0.013733 | -0.041199 | 0.064087 | -0.068665 | 0.045776 | 9.7733 | 122.2 | -0.09613 | 122.0901 | 0.20599 | 0.091553 | 0.1236 | 0.059509 | -122.2916 | -122.2961 | 0.13733 | 0.11902 | 0.004577 | 0.059509 | -0.054932 | -0.022888 | -0.054932 | -0.16479 | 0.27924 | 0.19684 | 0.16479 | 0.21973 | 0.18768 | 0.07782 | -0.027466 | 0.30212 | 122.1863 | -0.022888 | 122.2961 | 0.036621 | 122.2733 | -122.2687 | -122.3511 | 0.032043 | 122.1634 | -0.032044 | 9.8465
4322.8125 | 122.3648 | -0.10071 | 122.2687 | -0.15846 | -0.043244 | -0.0021084 | 0.021441 | -0.0025549 | -0.012239 | -0.0060049 | -0.098541 | 0.0061651 | 0.063423 | 0.048764 | -0.018797 | 0.027408 | -0.0042981 | -0.11902 | -0.004578 | -0.068665 | -0.086975 | -0.009155 | -0.11902 | -0.022888 | 9.819 | 122.2549 | -0.10529 | 122.0535 | 0.15106 | 0.004578 | 0.064087 | 0.032043 | -122.2733 | -122.3557 | 0.091553 | 0.07782 | -0.018311 | 0.045777 | -0.050354 | -0.004578 | -0.013733 | -0.21515 | 0.25177 | 0.1648 | 0.10529 | 0.16937 | 0.10986 | 0.05951 | -0.01831 | 0.25635 | 122.1588 | 0.064087 | 122.3602 | 0.09613 | 122.3557 | -122.3373 | -122.374 | 0.013733 | 122.1542 | -0.018311 | 9.9197
4324.5781 | 122.3511 | -0.082397 | 122.2778 | -0.1432 | -0.040253 | -0.001254 | 0.022509 | 0.0027857 | -0.012025 | -0.0034415 | -0.11075 | 0.0055243 | 0.063209 | 0.045773 | -0.017729 | 0.028262 | -0.0057935 | -0.09613 | -0.022888 | -0.054932 | -0.045776 | 0.036621 | -0.091553 | -0.018311 | 9.9289 | 122.2595 | -0.091553 | 122.049 | 0.13733 | -0.004578 | 0.07782 | 0.027465 | -122.3007 | -122.3236 | 0.11902 | 0.064086 | -0.009156 | 0.036621 | -0.036621 | -0.009156 | -0.018311 | -0.22888 | 0.21973 | 0.16022 | 0.077819 | 0.16937 | 0.086975 | 0.091553 | 0.009156 | 0.22888 | 122.1405 | 0.032044 | 122.3511 | 0.059509 | 122.3419 | -122.3328 | -122.3694 | 0.036621 | 122.1313 | -0.013733 | 10.0113
4326.3438 | 122.4106 | -0.091553 | 122.2641 | -0.23476 | -0.042176 | 0.0019504 | 0.021014 | -0.0055457 | -0.013093 | -0.0047231 | -0.016144 | 0.0057379 | 0.062354 | 0.044491 | -0.018797 | 0.027194 | -0.0083569 | -0.11902 | -0.018311 | -0.045776 | -0.027466 | 0.068665 | -0.073242 | 0.036621 | 10.0296 | 122.2092 | -0.09613 | 122.0947 | 0.21515 | 0.068665 | 0.1236 | 0.045777 | -122.2824 | -122.2916 | 0.16022 | 0.12817 | 0.018311 | 0.082397 | -0.027466 | -0.004577 | -0.054932 | -0.16937 | 0.3067 | 0.21515 | 0.16022 | 0.21973 | 0.16479 | 0.11444 | 0.01831 | 0.31128 | 122.1909 | 0.027465 | 122.3053 | 0.073242 | 122.3007 | -122.3099 | -122.3602 | 0.064087 | 122.1863 | -0.027466 | 10.1212
4328.1094 | 122.3328 | -0.10071 | 122.2641 | -0.13557 | -0.042603 | 0.0025912 | 0.023364 | 0.0010767 | -0.010957 | -0.0066457 | -0.13516 | 0.0070197 | 0.062354 | 0.04855 | -0.018583 | 0.028262 | -0.0045117 | -0.10986 | -0.022888 | -0.050354 | -0.054932 | 0.013733 | -0.14191 | -0.050354 | 10.0845 | 122.2412 | -0.09613 | 122.0398 | 0.10986 | -0.018311 | 0.059509 | 0.050354 | -122.287 | -122.319 | 0.11444 | 0.050354 | -0.041199 | 0 | -0.091553 | 0.004578 | -0.022888 | -0.2243 | 0.21057 | 0.16022 | 0.082397 | 0.15564 | 0.077819 | 0.064087 | -0.004578 | 0.20599 | 122.1359 | 0.027466 | 122.3373 | 0.07782 | 122.3419 | -122.3145 | -122.3602 | 0.045776 | 122.1405 | -0.009155 | 10.1852
4329.8125 | 122.3282 | -0.10986 | 122.2687 | -0.12032 | -0.043244 | -0.00018577 | 0.020373 | -0.00020513 | -0.014161 | -0.0079275 | -0.028351 | 0.0068059 | 0.064704 | 0.043423 | -0.015806 | 0.025912 | -0.0051525 | -0.14648 | 0.013733 | -0.059509 | -0.091553 | 0.009155 | -0.11444 | -0.009155 | 10.2127 | 122.2549 | -0.10529 | 121.9986 | 0.13733 | 0.009155 | 0.036621 | 0.050354 | -122.2549 | -122.3602 | 0.11902 | 0.10071 | -0.004578 | 0.050354 | -0.054932 | 0.004577 | -0.013733 | -0.27008 | 0.24719 | 0.14648 | 0.11902 | 0.14191 | 0.11444 | 0.068664 | -0.032044 | 0.24262 | 122.1039 | 0.073242 | 122.3602 | 0.1236 | 122.3648 | -122.3282 | -122.374 | 0.01831 | 122.1085 | -0.036621 | 10.3226
4331.5781 | 122.4197 | -0.054932 | 122.2687 | -0.1432 | -0.040039 | 0.0017368 | 0.019305 | -0.0014867 | -0.01117 | -0.0019461 | -0.022247 | 0.0057379 | 0.06385 | 0.044064 | -0.018583 | 0.027621 | -0.0047253 | -0.10986 | -0.045776 | -0.045776 | -0.009155 | 0.07782 | -0.064087 | 0.064087 | 10.3226 | 122.2092 | -0.09613 | 122.0947 | 0.21973 | 0.09613 | 0.12817 | 0.009156 | -122.3145 | -122.2778 | 0.13275 | 0.11902 | -0.009155 | 0.10986 | -0.018311 | -0.041198 | -0.05951 | -0.17395 | 0.27466 | 0.18311 | 0.15106 | 0.2243 | 0.19226 | 0.1236 | 0.036621 | 0.31586 | 122.1909 | 0 | 122.3053 | 0.009156 | 122.2641 | -122.3145 | -122.3648 | 0.045777 | 122.1497 | -0.054931 | 10.3775
4333.3281 | 122.4197 | -0.064087 | 122.2549 | -0.1432 | -0.043885 | 0.00088223 | 0.020587 | -0.0042639 | -0.013734 | -0.0023733 | -0.025299 | 0.0068059 | 0.064918 | 0.045773 | -0.017088 | 0.025912 | -0.0072889 | -0.064087 | -0.032043 | -0.013733 | 0.041199 | 0.14191 | 0 | 0.086975 | 10.5377 | 122.2046 | -0.07782 | 122.1085 | 0.2655 | 0.13275 | 0.14648 | 0.050354 | -122.287 | -122.2137 | 0.20599 | 0.15106 | 0.064087 | 0.10071 | 0.013733 | -0.013733 | -0.050354 | -0.14648 | 0.32959 | 0.21057 | 0.19684 | 0.2243 | 0.21057 | 0.15564 | 0.054932 | 0.34332 | 122.1863 | -0.01831 | 122.2824 | 0.032044 | 122.2687 | -122.2687 | -122.3328 | 0.10529 | 122.1725 | 0 | 10.6018
4335.0938 | 122.3373 | -0.10071 | 122.2778 | -0.1432 | -0.040039 | 0.00088223 | 0.02315 | -0.0012731 | -0.011384 | -0.0030141 | -0.13821 | 0.0068059 | 0.062782 | 0.048337 | -0.018369 | 0.027835 | -0.0075025 | -0.11902 | 0.013733 | -0.059509 | -0.09613 | -0.059509 | -0.17395 | -0.064087 | 10.4141 | 122.2183 | -0.12817 | 122.0078 | 0.11444 | -0.036621 | 0.036621 | 0.041199 | -122.2641 | -122.374 | 0.041199 | 0.036621 | -0.073242 | -0.004578 | -0.11444 | -0.027466 | -0.059509 | -0.27008 | 0.21515 | 0.13733 | 0.064087 | 0.1648 | 0.091553 | 0 | -0.036621 | 0.24262 | 122.1359 | 0.073242 | 122.3465 | 0.11444 | 122.319 | -122.3373 | -122.406 | 0.004578 | 122.1085 | -0.018311 | 10.5148
4336.8125 | 122.4426 | -0.064087 | 122.2412 | -0.21187 | -0.040894 | -0.00061317 | 0.019305 | -0.00084593 | -0.012879 | -0.0068593 | 0.0021667 | 0.0065923 | 0.064491 | 0.045987 | -0.018797 | 0.025272 | -0.0051525 | -0.11444 | -0.032043 | -0.032043 | -0.041199 | 0.068665 | -0.059509 | 0.036621 | 10.6705 | 122.1909 | -0.082397 | 122.1176 | 0.25177 | 0.10986 | 0.14191 | 0.032044 | -122.2733 | -122.2824 | 0.13275 | 0.10071 | 0.004578 | 0.068664 | -0.027466 | -0.01831 | -0.050354 | -0.1236 | 0.31586 | 0.20599 | 0.17395 | 0.2243 | 0.19226 | 0.10071 | -0.009156 | 0.33417 | 122.2 | 0 | 122.2733 | 0.032044 | 122.2549 | -122.2733 | -122.3236 | 0.022888 | 122.1817 | -0.050354 | 10.7346
4338.5625 | 122.4564 | -0.059509 | 122.2412 | -0.1432 | -0.044739 | 0.0010958 | 0.020373 | -0.0046911 | -0.010316 | -0.0049367 | -0.022247 | 0.0046697 | 0.061714 | 0.043637 | -0.018797 | 0.02634 | -0.0036573 | -0.068665 | -0.045776 | -0.032043 | 0.027466 | 0.16022 | 0.004578 | 0.09613 | 10.8719 | 122.1954 | -0.07782 | 122.1222 | 0.27924 | 0.13275 | 0.15106 | 0.027466 | -122.287 | -122.2137 | 0.21973 | 0.15564 | 0.064087 | 0.12817 | 0.036621 | -0.018311 | -0.045776 | -0.11902 | 0.33874 | 0.21057 | 0.19226 | 0.22888 | 0.21057 | 0.19226 | 0.059509 | 0.35706 | 122.2 | -0.013733 | 122.2733 | 0.013733 | 122.2549 | -122.2733 | -122.319 | 0.086975 | 122.1817 | -0.009156 | 10.9314
4340.3281 | 122.3785 | -0.10071 | 122.2733 | -0.13557 | -0.043457 | 0.00066863 | 0.022937 | 0.00022207 | -0.010743 | -0.0021597 | -0.10464 | 0.0065923 | 0.064277 | 0.047055 | -0.018797 | 0.026126 | -0.0042981 | -0.07782 | -0.009155 | -0.054932 | -0.032043 | 0.041199 | -0.068665 | 0.013733 | 10.8719 | 122.2504 | -0.09613 | 122.0718 | 0.19684 | 0.041199 | 0.086975 | 0.045776 | -122.2824 | -122.3053 | 0.14191 | 0.11444 | 0.032043 | 0.068665 | -0.013733 | 0.004578 | -0.022888 | -0.20142 | 0.29755 | 0.18768 | 0.14191 | 0.1831 | 0.13733 | 0.096131 | 0.022889 | 0.29297 | 122.168 | 0.045777 | 122.3465 | 0.091553 | 122.3511 | -122.3282 | -122.3694 | 0.068665 | 122.1725 | 0.022888 | 10.9726
4342.0938 | 122.4564 | -0.045776 | 122.2321 | -0.13557 | -0.043457 | -0.0014676 | 0.019519 | -0.0025549 | -0.013307 | -0.0021597 | -0.016144 | 0.0057379 | 0.062568 | 0.044491 | -0.01666 | 0.026553 | -0.0023755 | -0.050354 | -0.045776 | -0.032043 | 0.041199 | 0.17395 | 0.013733 | 0.11444 | 11.1191 | 122.2183 | -0.068665 | 122.1497 | 0.31586 | 0.15564 | 0.17853 | 0.013733 | -122.2778 | -122.1909 | 0.21973 | 0.16022 | 0.059509 | 0.14648 | 0.045776 | -0.022889 | -0.013733 | -0.082398 | 0.36163 | 0.2243 | 0.20142 | 0.24719 | 0.22431 | 0.20599 | 0.073242 | 0.38452 | 122.2183 | -0.013733 | 122.287 | 0 | 122.2641 | -122.2641 | -122.3007 | 0.086975 | 122.1954 | -0.004578 | 11.1649
4343.7969 | 122.4701 | -0.054932 | 122.2321 | -0.15846 | -0.04303 | 0.00045503 | 0.021014 | -0.00020513 | -0.010316 | -0.0038687 | -0.013092 | 0.0061651 | 0.0615 | 0.042355 | -0.01901 | 0.025272 | -0.0068615 | -0.073242 | -0.041199 | -0.022888 | 0.054932 | 0.1831 | 0.018311 | 0.12817 | 11.2106 | 122.2275 | -0.082397 | 122.1405 | 0.31128 | 0.16022 | 0.1831 | 0.032044 | -122.2733 | -122.1771 | 0.23804 | 0.18311 | 0.073243 | 0.15106 | 0.041199 | -0.027465 | -0.004578 | -0.091553 | 0.36621 | 0.23804 | 0.21515 | 0.2655 | 0.24261 | 0.20599 | 0.07782 | 0.39368 | 122.2229 | -0.018311 | 122.3099 | 0.013733 | 122.2824 | -122.2549 | -122.3145 | 0.10986 | 122.1954 | -0.01831 | 11.2656
4345.5625 | 122.3236 | -0.10986 | 122.2916 | -0.17372 | -0.040039 | 0.0013094 | 0.02315 | 0.0010767 | -0.012239 | -0.0038687 | -0.1138 | 0.0068059 | 0.064063 | 0.045346 | -0.019438 | 0.027408 | -0.0057935 | -0.091553 | 0.013733 | -0.050354 | -0.050354 | 0.018311 | -0.10071 | -0.022888 | 11.1145 | 122.2321 | -0.073242 | 122.049 | 0.13733 | -0.027466 | 0.059509 | 0.059509 | -122.2778 | -122.3419 | 0.12817 | 0.086975 | 0.009155 | 0.027466 | -0.050354 | 0.036621 | -0.059509 | -0.24262 | 0.24719 | 0.16937 | 0.082397 | 0.13275 | 0.045776 | 0.068665 | 0 | 0.21057 | 122.1222 | 0.064087 | 122.3053 | 0.1236 | 122.3419 | -122.3419 | -122.3648 | 0.059509 | 122.1588 | 0.01831 | 11.2244
4347.3281 | 122.3328 | -0.091553 | 122.2687 | -0.18135 | -0.042389 | 0.0010958 | 0.02315 | 0.00043587 | -0.0092478 | -0.0064321 | -0.12601 | 0.0089423 | 0.062354 | 0.048337 | -0.018369 | 0.027621 | -0.0051525 | -0.14648 | 0.018311 | -0.059509 | -0.11444 | -0.045776 | -0.16937 | -0.073242 | 11.1053 | 122.2458 | -0.10529 | 122.0261 | 0.13733 | -0.050354 | 0.050354 | 0.032044 | -122.2504 | -122.3831 | 0.045777 | 0.018311 | -0.07782 | -0.013733 | -0.10986 | -0.013733 | -0.022888 | -0.24262 | 0.22888 | 0.14191 | 0.041199 | 0.15564 | 0.054932 | 0.013733 | -0.054932 | 0.24262 | 122.1313 | 0.07782 | 122.3511 | 0.10986 | 122.3373 | -122.3282 | -122.374 | -0.022888 | 122.1176 | -0.054931 | 11.1969
4349.0312 | 122.3877 | -0.10529 | 122.2824 | -0.13557 | -0.042603 | 0.00024143 | 0.023578 | 0.0036401 | -0.010743 | -0.0023733 | -0.09549 | 0.0089423 | 0.065772 | 0.052609 | -0.016447 | 0.025058 | -0.0064343 | -0.091553 | 0 | -0.054932 | -0.041199 | 0.045776 | -0.086975 | 0.018311 | 11.3617 | 122.2412 | -0.07782 | 122.0673 | 0.21515 | 0.045776 | 0.09613 | 0.050354 | -122.2824 | -122.3236 | 0.15106 | 0.1236 | 0.018311 | 0.073243 | -0.032043 | 0.027466 | -0.041199 | -0.21515 | 0.32044 | 0.20142 | 0.15106 | 0.17395 | 0.1236 | 0.10071 | 0.013733 | 0.29297 | 122.1451 | 0.054932 | 122.319 | 0.10529 | 122.3465 | -122.3373 | -122.3602 | 0.064087 | 122.1725 | 0.013733 | 11.467
4350.7969 | 122.3557 | -0.082397 | 122.2549 | -0.18898 | -0.039185 | 2.7834e-05 | 0.022937 | -0.0010595 | -0.011811 | -0.0049367 | -0.083283 | 0.0078741 | 0.063636 | 0.049832 | -0.01666 | 0.026981 | -0.0064343 | -0.15106 | 0.018311 | -0.064087 | -0.09613 | -0.009155 | -0.16022 | -0.045776 | 11.3113 | 122.2549 | -0.10986 | 122.0581 | 0.16937 | -0.022888 | 0.054932 | 0.01831 | -122.2366 | -122.3511 | 0.073242 | 0.036621 | -0.07782 | 0.018311 | -0.09613 | -0.027466 | 0 | -0.19684 | 0.25177 | 0.13733 | 0.059509 | 0.16479 | 0.086975 | 0.054932 | -0.032043 | 0.27924 | 122.168 | 0.082398 | 122.3648 | 0.10071 | 122.3373 | -122.319 | -122.3648 | -0.013733 | 122.1405 | -0.068665 | 11.3937
4352.5781 | 122.3373 | -0.10529 | 122.2733 | -0.1432 | -0.042816 | -0.0010404 | 0.021655 | 0.0027857 | -0.011811 | -0.0021597 | -0.064972 | 0.0072333 | 0.064918 | 0.049405 | -0.017729 | 0.028049 | -0.0032299 | -0.15106 | 0.013733 | -0.073242 | -0.10529 | -0.004578 | -0.10986 | -0.013733 | 11.4853 | 122.2458 | -0.09613 | 122.0169 | 0.1831 | 0.004578 | 0.059509 | 0.032044 | -122.2595 | -122.3785 | 0.10071 | 0.091553 | -0.004577 | 0.059509 | -0.036621 | 0.009156 | -0.027465 | -0.25635 | 0.28839 | 0.16479 | 0.10986 | 0.15564 | 0.10071 | 0.068664 | -0.032044 | 0.27924 | 122.113 | 0.086975 | 122.3419 | 0.11902 | 122.3511 | -122.3465 | -122.3694 | 0 | 122.1222 | -0.045776 | 11.5906
4354.2812 | 122.4518 | -0.045776 | 122.2 | -0.21187 | -0.042176 | 0.0013094 | 0.022937 | 0.00022207 | -0.010102 | -0.0057913 | -0.068024 | 0.0068059 | 0.062354 | 0.045773 | -0.018369 | 0.026553 | -0.0077161 | -0.059509 | -0.041199 | -0.022888 | 0.027466 | 0.14191 | -0.036621 | 0.068665 | 11.6684 | 122.2 | -0.068665 | 122.1451 | 0.28839 | 0.11902 | 0.20142 | 0.022888 | -122.2412 | -122.1725 | 0.18768 | 0.11444 | 0.009155 | 0.091553 | -0.013733 | -0.022889 | 0 | -0.054931 | 0.33417 | 0.24719 | 0.16479 | 0.27008 | 0.18768 | 0.16479 | 0.050354 | 0.35706 | 122.2137 | -0.018311 | 122.2687 | 0.004577 | 122.2458 | -122.2229 | -122.2687 | 0.073242 | 122.1909 | -0.013733 | 11.7142
4356.0469 | 122.3465 | -0.09613 | 122.2412 | -0.13557 | -0.04303 | 2.7834e-05 | 0.021441 | -0.0010595 | -0.012239 | -0.0055777 | -0.028351 | 0.0057379 | 0.062995 | 0.041287 | -0.018369 | 0.024844 | -0.0045117 | -0.082397 | -0.013733 | -0.022888 | -0.022888 | 0.10529 | -0.032043 | 0.050354 | 11.7508 | 122.2321 | -0.086975 | 122.0535 | 0.21973 | 0.045776 | 0.10071 | 0.073242 | -122.2549 | -122.2641 | 0.20142 | 0.14648 | 0.064087 | 0.073242 | -0.009155 | 0.009155 | -0.009155 | -0.18768 | 0.31586 | 0.19684 | 0.14191 | 0.18768 | 0.13275 | 0.12817 | 0 | 0.3067 | 122.1405 | 0.009155 | 122.319 | 0.082397 | 122.3282 | -122.2641 | -122.3282 | 0.073242 | 122.1497 | 0.013733 | 11.8469
4357.8125 | 122.374 | -0.086975 | 122.2504 | -0.12032 | -0.041321 | -0.0010404 | 0.023578 | 0.0012903 | -0.01117 | -0.00087794 | -0.098541 | 0.0061651 | 0.062354 | 0.044919 | -0.01901 | 0.029544 | -0.0017347 | -0.086975 | -0.004578 | -0.045776 | -0.032043 | 0.073242 | -0.068665 | 0.022888 | 11.8011 | 122.2092 | -0.10529 | 122.0673 | 0.22888 | 0.036621 | 0.10529 | 0.041199 | -122.2549 | -122.2824 | 0.16022 | 0.10986 | 0.01831 | 0.068664 | -0.022889 | -0.018311 | -0.041199 | -0.1831 | 0.31586 | 0.19226 | 0.1236 | 0.21057 | 0.14191 | 0.11902 | 0.013733 | 0.33417 | 122.1725 | 0.041198 | 122.3145 | 0.082397 | 122.2961 | -122.2961 | -122.3557 | 0.054932 | 122.1542 | 0 | 11.8881
4359.5781 | 122.4152 | -0.064087 | 122.2549 | -0.19661 | -0.04068 | 0.00045503 | 0.019732 | 0.00043587 | -0.01117 | -0.0055777 | -0.013092 | 0.0068059 | 0.064704 | 0.038083 | -0.01666 | 0.024844 | -0.0047253 | -0.1236 | -0.041199 | -0.022888 | -0.018311 | 0.07782 | -0.064087 | 0.045776 | 11.911 | 122.2137 | -0.10071 | 122.0856 | 0.24719 | 0.073242 | 0.13275 | 0.041199 | -122.2961 | -122.2733 | 0.14191 | 0.10986 | 0 | 0.068664 | -0.041199 | -0.036621 | -0.041199 | -0.16937 | 0.31128 | 0.19684 | 0.13733 | 0.23346 | 0.17395 | 0.10071 | 0.004577 | 0.3479 | 122.1863 | -0.018311 | 122.3145 | 0.022888 | 122.2778 | -122.2778 | -122.3557 | 0.045776 | 122.1497 | -0.059509 | 11.9751
4361.3438 | 122.3831 | -0.10529 | 122.2504 | -0.15846 | -0.039612 | 0.0023776 | 0.023364 | -0.0025549 | -0.009675 | -0.0055777 | -0.098541 | 0.0074469 | 0.062782 | 0.046841 | -0.017729 | 0.024844 | -0.0064343 | -0.11902 | 0.004578 | -0.07782 | -0.10529 | -0.013733 | -0.15564 | -0.032043 | 11.9202 | 122.2412 | -0.10529 | 122.0535 | 0.16937 | 0.004578 | 0.073242 | 0.027466 | -122.2458 | -122.3557 | 0.091553 | 0.073243 | -0.050354 | 0.045777 | -0.07782 | 0 | -0.009155 | -0.19684 | 0.27466 | 0.17853 | 0.10986 | 0.17853 | 0.10986 | 0.064087 | -0.027466 | 0.27466 | 122.1588 | 0.082398 | 122.3465 | 0.10986 | 122.3465 | -122.3282 | -122.3557 | 0 | 122.1588 | -0.013733 | 12.0255
4363.125 | 122.4426 | -0.041199 | 122.2549 | -0.1432 | -0.043244 | -0.00018577 | 0.019946 | -0.0034095 | -0.010102 | -0.0045095 | -0.019196 | 0.0053107 | 0.06385 | 0.045773 | -0.01666 | 0.026553 | -0.0077161 | -0.082397 | -0.036621 | -0.036621 | 0.032043 | 0.14648 | 0.013733 | 0.10529 | 12.1994 | 122.2046 | -0.09613 | 122.1222 | 0.30212 | 0.13733 | 0.16479 | 0.004578 | -122.2916 | -122.2229 | 0.18768 | 0.14649 | 0.054932 | 0.14191 | 0.050354 | -0.054931 | -0.050354 | -0.13275 | 0.34332 | 0.20599 | 0.17853 | 0.26092 | 0.23346 | 0.18311 | 0.068664 | 0.39825 | 122.2183 | 0 | 122.3007 | 0.004578 | 122.2458 | -122.2916 | -122.3511 | 0.073242 | 122.1634 | -0.041198 | 12.2406
4364.8281 | 122.4655 | -0.054932 | 122.2183 | -0.15846 | -0.044739 | 0.0010958 | 0.018237 | -0.0010595 | -0.015229 | -0.0083547 | 0.0082703 | 0.0048833 | 0.062782 | 0.045346 | -0.019651 | 0.027408 | -0.0049389 | -0.068665 | -0.022888 | -0.018311 | 0.045776 | 0.17853 | 0.036621 | 0.11902 | 12.3596 | 122.1588 | -0.054932 | 122.1451 | 0.33417 | 0.16479 | 0.1831 | 0.036621 | -122.2412 | -122.1725 | 0.23346 | 0.17395 | 0.091553 | 0.13733 | 0.054932 | 0 | -0.05951 | -0.073242 | 0.3891 | 0.23804 | 0.21973 | 0.23804 | 0.21973 | 0.19684 | 0.064087 | 0.3891 | 122.2 | -0.004577 | 122.2137 | 0.032044 | 122.2137 | -122.2366 | -122.2733 | 0.10071 | 122.2 | -0.013733 | 12.4146
4366.5938 | 122.4564 | -0.054932 | 122.2321 | -0.15083 | -0.042816 | -0.00039957 | 0.021441 | -0.00041873 | -0.012025 | -0.0045095 | -0.0039367 | 0.0055243 | 0.064063 | 0.049405 | -0.019865 | 0.024417 | -0.0023755 | -0.10071 | -0.036621 | -0.041199 | 0.009155 | 0.11902 | -0.004578 | 0.082397 | 12.3825 | 122.1954 | -0.073242 | 122.1268 | 0.31586 | 0.15564 | 0.1831 | 0.013733 | -122.2687 | -122.2229 | 0.17395 | 0.13733 | 0.050354 | 0.1236 | 0.036621 | -0.01831 | -0.036621 | -0.10529 | 0.37079 | 0.23804 | 0.21057 | 0.25635 | 0.22888 | 0.16022 | 0.050354 | 0.3891 | 122.2 | 0.004578 | 122.2687 | 0.018311 | 122.2504 | -122.2733 | -122.3053 | 0.064087 | 122.1817 | -0.045776 | 12.4374
4368.3438 | 122.3557 | -0.10529 | 122.2549 | -0.12032 | -0.041107 | 0.0010958 | 0.02315 | -0.0023413 | -0.012666 | -0.0064321 | -0.086334 | 0.0083013 | 0.061927 | 0.047055 | -0.017729 | 0.026981 | -0.0072889 | -0.14648 | 0.027466 | -0.050354 | -0.10986 | -0.027466 | -0.12817 | -0.013733 | 12.3459 | 122.2778 | -0.10071 | 122.0123 | 0.20142 | -0.009155 | 0.073242 | 0.054932 | -122.2275 | -122.3648 | 0.07782 | 0.091553 | -0.022888 | 0.036621 | -0.07782 | 0.004578 | 0.022888 | -0.24262 | 0.3067 | 0.17853 | 0.096131 | 0.17395 | 0.091553 | 0.022888 | -0.059509 | 0.30212 | 122.113 | 0.07782 | 122.3785 | 0.13275 | 122.3831 | -122.3053 | -122.3557 | -0.004577 | 122.1176 | -0.041198 | 12.4512
4370.0469 | 122.4655 | -0.059509 | 122.2092 | -0.15083 | -0.041107 | 0.0019504 | 0.023791 | -0.0017005 | -0.010957 | -0.0021597 | -0.083283 | 0.0055243 | 0.060218 | 0.047268 | -0.01901 | 0.024204 | -0.0045117 | -0.045776 | -0.036621 | -0.036621 | 0.032043 | 0.1236 | -0.045776 | 0.068665 | 12.5702 | 122.1771 | -0.07782 | 122.1542 | 0.30212 | 0.1236 | 0.20142 | 0.022888 | -122.2458 | -122.1771 | 0.1831 | 0.12817 | 0.013733 | 0.10529 | -0.009155 | -0.018311 | -0.032043 | -0.054931 | 0.36163 | 0.26093 | 0.1831 | 0.27924 | 0.20142 | 0.16022 | 0.068664 | 0.37994 | 122.2321 | 0 | 122.2549 | 0.022888 | 122.2366 | -122.2458 | -122.287 | 0.091552 | 122.2137 | 0.013733 | 12.6297
4371.8281 | 122.3419 | -0.07782 | 122.2595 | -0.15083 | -0.041321 | 0.0010958 | 0.022509 | -0.00084593 | -0.010102 | -0.0042959 | -0.12906 | 0.0078741 | 0.064063 | 0.051541 | -0.019865 | 0.029544 | -0.0079297 | -0.091553 | -0.013733 | -0.050354 | -0.041199 | 0.036621 | -0.10529 | 0 | 12.6297 | 122.2458 | -0.091553 | 122.0627 | 0.21057 | -0.009155 | 0.073242 | 0.027466 | -122.2733 | -122.3007 | 0.11444 | 0.07782 | -0.027466 | 0.050354 | -0.054932 | -0.013733 | -0.013732 | -0.19684 | 0.28839 | 0.15106 | 0.068665 | 0.16479 | 0.082398 | 0.086975 | 0.009155 | 0.30212 | 122.1542 | 0.036621 | 122.3373 | 0.064087 | 122.3236 | -122.3099 | -122.3511 | 0.036621 | 122.1405 | -0.013733 | 12.7075
4373.5938 | 122.4838 | -0.050354 | 122.2595 | -0.16609 | -0.043244 | 0.00024143 | 0.019091 | 0.00022207 | -0.012239 | -0.0025869 | -0.028351 | 0.0065923 | 0.060432 | 0.046414 | -0.018369 | 0.026126 | -0.0055799 | -0.086975 | -0.045776 | -0.022888 | 0.032043 | 0.1831 | 0.027466 | 0.1236 | 12.8769 | 122.1771 | -0.082397 | 122.168 | 0.3479 | 0.16937 | 0.19226 | 0.027466 | -122.3053 | -122.2275 | 0.23346 | 0.17395 | 0.07782 | 0.14648 | 0.050354 | -0.032043 | -0.082397 | -0.091552 | 0.39825 | 0.24261 | 0.21973 | 0.27466 | 0.25177 | 0.20599 | 0.054931 | 0.4303 | 122.2504 | -0.022888 | 122.2595 | 0.004578 | 122.2275 | -122.2824 | -122.3419 | 0.082397 | 122.2183 | -0.036621 | 12.9272
4375.3438 | 122.3465 | -0.10529 | 122.2687 | -0.17372 | -0.043885 | -0.0014676 | 0.0208 | 0.00086307 | -0.01117 | -0.0062185 | -0.037506 | 0.0061651 | 0.061286 | 0.052182 | -0.018156 | 0.025912 | -0.0083569 | -0.10986 | -0.013733 | -0.054932 | -0.068665 | 0.027466 | -0.07782 | 0 | 12.7396 | 122.2504 | -0.11902 | 122.0123 | 0.21057 | 0.013733 | 0.054932 | 0.050354 | -122.2824 | -122.3373 | 0.13275 | 0.10529 | 0.027466 | 0.054932 | -0.022888 | -0.013733 | -0.018311 | -0.25635 | 0.31586 | 0.16022 | 0.11902 | 0.17395 | 0.13275 | 0.082398 | -0.013733 | 0.32959 | 122.1313 | 0.041199 | 122.3694 | 0.091553 | 122.3557 | -122.3236 | -122.3877 | 0.036621 | 122.1176 | -0.004577 | 12.8448
4377.0469 | 122.4518 | -0.054932 | 122.2641 | -0.18898 | -0.041962 | 0.00066863 | 0.018878 | -0.0023413 | -0.011598 | -0.0030141 | -0.0008851 | 0.0048833 | 0.061927 | 0.047696 | -0.019224 | 0.026981 | -0.0057935 | -0.07782 | -0.045776 | -0.022888 | 0.036621 | 0.14191 | 0.013733 | 0.091553 | 13.0096 | 122.1863 | -0.086975 | 122.1268 | 0.33417 | 0.14191 | 0.16937 | 0.032044 | -122.3099 | -122.2275 | 0.19684 | 0.14649 | 0.068665 | 0.11444 | 0.036621 | -0.032043 | -0.07782 | -0.13733 | 0.3891 | 0.22431 | 0.19684 | 0.25635 | 0.22888 | 0.16479 | 0.059509 | 0.42114 | 122.2137 | -0.022888 | 122.2733 | 0.009156 | 122.2412 | -122.287 | -122.3511 | 0.091553 | 122.1817 | -0.022888 | 13.0646
4378.8125 | 122.3236 | -0.09613 | 122.2458 | -0.18135 | -0.041535 | 0.0019504 | 0.022509 | -0.0010595 | -0.0098886 | -0.0025869 | -0.11685 | 0.0068059 | 0.063209 | 0.051541 | -0.017515 | 0.02634 | -0.0038709 | -0.11902 | 0 | -0.068665 | -0.082397 | -0.041199 | -0.16022 | -0.068665 | 12.8586 | 122.2412 | -0.09613 | 122.0215 | 0.14648 | -0.041199 | 0.045776 | 0.027465 | -122.2458 | -122.3282 | 0.054931 | 0.027465 | -0.064087 | 0 | -0.091552 | 0 | -0.004578 | -0.22431 | 0.24261 | 0.14191 | 0.054931 | 0.14191 | 0.054931 | 0.027466 | -0.013732 | 0.24261 | 122.1176 | 0.068665 | 122.3373 | 0.09613 | 122.3373 | -122.3145 | -122.3419 | 0.013733 | 122.1176 | -0.022889 | 12.9547
4380.5156 | 122.374 | -0.10071 | 122.2549 | -0.20424 | -0.041321 | 0.0028048 | 0.023791 | 0.0017175 | -0.010957 | -0.0045095 | -0.10464 | 0.0074469 | 0.062995 | 0.048123 | -0.017515 | 0.027408 | -0.0057935 | -0.091553 | -0.009155 | -0.041199 | -0.027466 | 0.059509 | -0.082397 | 0.022888 | 13.0692 | 122.2549 | -0.11902 | 122.0627 | 0.25177 | 0.036621 | 0.10071 | 0.059509 | -122.2641 | -122.2824 | 0.16022 | 0.1236 | 0.018311 | 0.064087 | -0.041198 | -0.018311 | 0 | -0.19226 | 0.35248 | 0.20142 | 0.13733 | 0.21973 | 0.15564 | 0.10071 | 0.013733 | 0.37079 | 122.1817 | 0.032044 | 122.374 | 0.091553 | 122.3557 | -122.2961 | -122.374 | 0.073242 | 122.1634 | 0.009155 | 13.1699
4382.2812 | 122.4106 | -0.054932 | 122.2412 | -0.20424 | -0.041107 | 0.001523 | 0.019732 | -0.0027685 | -0.0094614 | -0.0021597 | -0.028351 | 0.0072333 | 0.061073 | 0.042569 | -0.017301 | 0.026553 | -0.0060071 | -0.10986 | -0.032043 | -0.013733 | -0.036621 | 0.082397 | -0.059509 | 0.036621 | 13.1836 | 122.1954 | -0.082397 | 122.0764 | 0.28381 | 0.091553 | 0.13733 | 0.041199 | -122.2733 | -122.2778 | 0.13733 | 0.091553 | -0.004577 | 0.050354 | -0.045776 | -0.027465 | -0.045776 | -0.1648 | 0.33874 | 0.19226 | 0.14649 | 0.21973 | 0.17395 | 0.09613 | -0.022888 | 0.36621 | 122.1588 | -0.01831 | 122.2778 | 0.022889 | 122.2504 | -122.2549 | -122.3236 | 0.018311 | 122.1313 | -0.054931 | 13.2385
4383.9844 | 122.3419 | -0.10529 | 122.2641 | -0.21187 | -0.040894 | 0.0013094 | 0.023364 | 0.00064947 | -0.0094614 | -0.0025869 | -0.1199 | 0.0070197 | 0.064277 | 0.049405 | -0.01901 | 0.028262 | -0.0023755 | -0.11902 | 0.018311 | -0.059509 | -0.10529 | -0.041199 | -0.15564 | -0.054932 | 13.1424 | 122.2275 | -0.10986 | 122.0215 | 0.18768 | -0.032043 | 0.068665 | 0.045777 | -122.2458 | -122.3694 | 0.064087 | 0.050354 | -0.050354 | 0.004577 | -0.096131 | -0.004577 | -0.036621 | -0.24262 | 0.29297 | 0.17395 | 0.073243 | 0.17853 | 0.07782 | 0.01831 | -0.045777 | 0.29755 | 122.1313 | 0.07782 | 122.3373 | 0.1236 | 122.3328 | -122.3236 | -122.374 | 0 | 122.1268 | -0.013733 | 13.2477
4385.75 | 122.406 | -0.068665 | 122.2275 | -0.20424 | -0.041748 | 0.0019504 | 0.022937 | 0.0012903 | -0.010957 | -0.0055777 | -0.031403 | 0.0072333 | 0.060432 | 0.042569 | -0.018156 | 0.027621 | -0.0045117 | -0.10071 | -0.041199 | -0.013733 | 0.027466 | 0.13733 | -0.036621 | 0.07782 | 13.3896 | 122.2137 | -0.068665 | 122.0947 | 0.31128 | 0.10986 | 0.15106 | 0.054932 | -122.2687 | -122.2 | 0.20599 | 0.14649 | 0.032044 | 0.091553 | -0.022888 | 0 | -0.013733 | -0.13275 | 0.37994 | 0.21973 | 0.17853 | 0.21973 | 0.17853 | 0.15106 | 0.041199 | 0.37994 | 122.1634 | -0.027466 | 122.2824 | 0.027466 | 122.2824 | -122.2412 | -122.2961 | 0.096131 | 122.1634 | -0.032043 | 13.4583
4387.5469 | 122.4655 | -0.050354 | 122.2458 | -0.20424 | -0.041107 | 0.0010958 | 0.024432 | 0.0025721 | -0.01053 | -0.0053641 | -0.080231 | 0.0070197 | 0.062995 | 0.048337 | -0.020078 | 0.025912 | -0.0055799 | -0.068665 | -0.036621 | -0.032043 | 0.009155 | 0.10986 | -0.036621 | 0.073242 | 13.4857 | 122.1954 | -0.086975 | 122.1405 | 0.33417 | 0.11902 | 0.20142 | 0.018311 | -122.2824 | -122.2366 | 0.16022 | 0.1236 | 0.013733 | 0.10529 | -0.004578 | -0.036621 | -0.050354 | -0.10529 | 0.38452 | 0.25177 | 0.16937 | 0.28839 | 0.20599 | 0.14191 | 0.041198 | 0.42114 | 122.2275 | -0.004578 | 122.2824 | 0.013733 | 122.2458 | -122.2778 | -122.3328 | 0.059509 | 122.1909 | -0.018311 | 13.5361
4389.25 | 122.3511 | -0.11902 | 122.2641 | -0.082169 | -0.043671 | 0.0019504 | 0.021228 | -0.00020513 | -0.015229 | -0.0021597 | -0.092438 | 0.0074469 | 0.063423 | 0.047909 | -0.019224 | 0.025699 | -0.0075025 | -0.14191 | -0.009155 | -0.064087 | -0.10071 | -0.018311 | -0.10986 | -0.009155 | 13.4995 | 122.2778 | -0.10071 | 122.0123 | 0.22888 | 0 | 0.054932 | 0.054932 | -122.2733 | -122.3648 | 0.10071 | 0.10986 | 0.009156 | 0.054932 | -0.045776 | 0.018311 | 0.013733 | -0.25177 | 0.3479 | 0.17395 | 0.11902 | 0.15564 | 0.10071 | 0.045776 | -0.036621 | 0.32959 | 122.113 | 0.054932 | 122.3785 | 0.10986 | 122.3969 | -122.3282 | -122.3648 | 0.018311 | 122.1313 | -0.022888 | 13.6185
4391 | 122.374 | -0.064087 | 122.2687 | -0.19661 | -0.039612 | 0.0013094 | 0.023364 | 0.0012903 | -0.010316 | -0.0045095 | -0.10159 | 0.0083013 | 0.060432 | 0.050473 | -0.017942 | 0.027194 | -0.0051525 | -0.10071 | -0.004578 | -0.054932 | -0.036621 | 0.068665 | -0.064087 | 0.013733 | 13.6459 | 122.2549 | -0.10071 | 122.0718 | 0.27924 | 0.045776 | 0.11444 | 0.009155 | -122.2733 | -122.3053 | 0.13275 | 0.07782 | 0 | 0.068665 | -0.009155 | -0.036621 | -0.013733 | -0.19684 | 0.34332 | 0.17853 | 0.10986 | 0.21515 | 0.14648 | 0.1236 | 0.018311 | 0.37994 | 122.1725 | 0.050354 | 122.3557 | 0.059509 | 122.319 | -122.3236 | -122.3694 | 0.027466 | 122.1359 | -0.036621 | 13.71
4392.7656 | 122.3785 | -0.091553 | 122.2641 | -0.16609 | -0.041321 | 0.001523 | 0.024218 | 0.00064947 | -0.010743 | -0.0042959 | -0.080231 | 0.0076605 | 0.065132 | 0.048123 | -0.017942 | 0.026553 | -0.0023755 | -0.12817 | 0.004578 | -0.07782 | -0.086975 | -0.009155 | -0.16479 | -0.054932 | 13.6093 | 122.2366 | -0.091553 | 122.0535 | 0.23346 | 0.009155 | 0.10986 | 0.013733 | -122.2595 | -122.3511 | 0.082398 | 0.036621 | -0.073242 | 0.022888 | -0.086975 | 0 | -0.027466 | -0.21057 | 0.32501 | 0.20142 | 0.10071 | 0.20142 | 0.10071 | 0.068665 | -0.009155 | 0.32501 | 122.1451 | 0.082398 | 122.3282 | 0.096131 | 122.3282 | -122.3419 | -122.3557 | 0.004578 | 122.1451 | -0.036621 | 13.7009
4394.4688 | 122.374 | -0.082397 | 122.2687 | -0.11269 | -0.043671 | 0.0034456 | 0.022296 | -0.0038367 | -0.010957 | -0.0028005 | -0.077179 | 0.0083013 | 0.063636 | 0.048764 | -0.017301 | 0.029758 | -0.0053661 | -0.11444 | 0.018311 | -0.059509 | -0.064087 | 0.032043 | -0.091553 | 0.009155 | 13.8153 | 122.2183 | -0.11902 | 122.0718 | 0.28839 | 0.045776 | 0.10529 | 0.022888 | -122.2504 | -122.3328 | 0.11444 | 0.091552 | -0.009156 | 0.068664 | -0.032044 | -0.036622 | -0.050354 | -0.19684 | 0.37079 | 0.18768 | 0.12817 | 0.22431 | 0.16479 | 0.091552 | -0.004578 | 0.40741 | 122.1909 | 0.07782 | 122.3373 | 0.10071 | 122.3007 | -122.3282 | -122.3877 | 0.01831 | 122.1542 | -0.032044 | 13.8977
4396.2188 | 122.3785 | -0.068665 | 122.2687 | -0.16609 | -0.041535 | 0.0013094 | 0.02315 | 0.0015039 | -0.008607 | -0.0032277 | -0.074127 | 0.0083013 | 0.063209 | 0.050473 | -0.019438 | 0.026553 | -0.0023755 | -0.09613 | 0.027466 | -0.059509 | -0.054932 | 0.041199 | -0.082397 | 0.004578 | 13.916 | 122.2549 | -0.09613 | 122.0581 | 0.27924 | 0.036621 | 0.10986 | 0.009156 | -122.2412 | -122.3236 | 0.10986 | 0.073243 | -0.013732 | 0.064087 | -0.022888 | -0.027465 | -0.013733 | -0.21057 | 0.3479 | 0.17853 | 0.10529 | 0.20599 | 0.13275 | 0.10071 | 0.004577 | 0.37537 | 122.1542 | 0.086975 | 122.3511 | 0.096131 | 122.3236 | -122.3282 | -122.3648 | 0.013733 | 122.1268 | -0.027465 | 13.9847
4397.9844 | 122.4609 | -0.054932 | 122.2366 | -0.2195 | -0.040894 | -0.00039957 | 0.020587 | -0.0014867 | -0.010102 | -0.0040823 | -0.058869 | 0.0070197 | 0.063423 | 0.0462 | -0.017515 | 0.027835 | -0.0060071 | -0.064087 | -0.036621 | -0.027466 | 0.022888 | 0.11902 | -0.041199 | 0.073242 | 14.0579 | 122.1771 | -0.059509 | 122.1451 | 0.35706 | 0.13275 | 0.20142 | 0.027466 | -122.2733 | -122.2137 | 0.17395 | 0.12817 | 0.013733 | 0.10071 | -0.013733 | -0.004577 | -0.059509 | -0.091552 | 0.41199 | 0.25635 | 0.18768 | 0.26093 | 0.19226 | 0.14649 | 0.050354 | 0.41656 | 122.2046 | -0.009155 | 122.2366 | 0.018311 | 122.2321 | -122.2641 | -122.2961 | 0.07782 | 122.2 | -0.009155 | 14.1129
4399.75 | 122.4609 | -0.041199 | 122.2321 | -0.15846 | -0.042816 | 0.00066863 | 0.019732 | -0.0012731 | -0.01117 | -0.0042959 | -0.0039367 | 0.0070197 | 0.062354 | 0.051968 | -0.019438 | 0.024417 | -0.0075025 | -0.068665 | -0.032043 | -0.013733 | 0.036621 | 0.17853 | 0.045776 | 0.1236 | 14.241 | 122.1909 | -0.073242 | 122.1359 | 0.37994 | 0.16479 | 0.19684 | 0.027466 | -122.2641 | -122.1954 | 0.21973 | 0.16479 | 0.086975 | 0.13733 | 0.059509 | -0.032043 | -0.041199 | -0.096131 | 0.42114 | 0.23804 | 0.20599 | 0.27008 | 0.23804 | 0.19226 | 0.050354 | 0.45319 | 122.2092 | -0.01831 | 122.2641 | 0.009156 | 122.2321 | -122.2458 | -122.3053 | 0.07782 | 122.1771 | -0.027466 | 14.2822
4401.5156 | 122.4518 | -0.068665 | 122.2321 | -0.21187 | -0.041535 | 0.0017368 | 0.021228 | 8.47e-06 | -0.010743 | -0.0036551 | -0.034454 | 0.0065923 | 0.061927 | 0.043637 | -0.018156 | 0.028049 | -0.0060071 | -0.054932 | -0.054932 | -0.032043 | 0.018311 | 0.11902 | -0.018311 | 0.086975 | 14.2548 | 122.2137 | -0.073242 | 122.1313 | 0.33875 | 0.11444 | 0.17395 | 0.036622 | -122.287 | -122.2137 | 0.18768 | 0.15564 | 0.050354 | 0.11902 | 0.013732 | -0.004577 | -0.018311 | -0.10071 | 0.40741 | 0.24261 | 0.18311 | 0.24719 | 0.18768 | 0.15106 | 0.050354 | 0.41199 | 122.2046 | -0.022889 | 122.287 | 0.013733 | 122.2824 | -122.2641 | -122.3053 | 0.086976 | 122.2 | 0.013733 | 14.3234
4403.2031 | 122.3923 | -0.086975 | 122.2641 | -0.12794 | -0.040467 | 0.001523 | 0.022296 | 0.00064947 | -0.010957 | -0.0038687 | -0.10159 | 0.0070197 | 0.061927 | 0.0509 | -0.019865 | 0.025272 | -0.0045117 | -0.10071 | -0.004578 | -0.054932 | -0.036621 | 0.064087 | -0.073242 | 0.022888 | 14.2868 | 122.2504 | -0.082397 | 122.0718 | 0.29755 | 0.045776 | 0.1236 | 0.032043 | -122.2687 | -122.3007 | 0.15106 | 0.10986 | 0.013733 | 0.07782 | -0.01831 | 0.004578 | -0.013733 | -0.19226 | 0.38452 | 0.21057 | 0.13275 | 0.20599 | 0.12817 | 0.11902 | 0.018311 | 0.37994 | 122.1542 | 0.050354 | 122.3328 | 0.082397 | 122.3373 | -122.319 | -122.3465 | 0.050354 | 122.1588 | -0.013733 | 14.3738
4404.9688 | 122.4609 | -0.059509 | 122.2183 | -0.21187 | -0.04303 | 0.00024143 | 0.022082 | 0.0029993 | -0.012452 | -0.0049367 | -0.077179 | 0.0057379 | 0.064277 | 0.047482 | -0.018369 | 0.026981 | -0.0089977 | -0.073242 | -0.045776 | -0.022888 | 0.018311 | 0.10986 | -0.036621 | 0.054932 | 14.3967 | 122.1863 | -0.07782 | 122.1405 | 0.33875 | 0.12817 | 0.20142 | 0.036621 | -122.2641 | -122.2 | 0.16937 | 0.11444 | 0.022888 | 0.07782 | -0.013733 | -0.018311 | -0.032044 | -0.07782 | 0.39825 | 0.26093 | 0.18768 | 0.27924 | 0.20599 | 0.13275 | 0.041199 | 0.41657 | 122.2183 | -0.022888 | 122.2641 | 0.013733 | 122.2458 | -122.2412 | -122.2961 | 0.07782 | 122.2 | -0.013733 | 14.4562
4406.6875 | 122.4792 | -0.050354 | 122.2183 | -0.13557 | -0.043885 | 0.0017368 | 0.019519 | 0.0012903 | -0.011384 | -0.0055777 | 0.0021667 | 0.0068059 | 0.062782 | 0.042569 | -0.016874 | 0.025699 | -0.0051525 | -0.082397 | -0.027466 | -0.027466 | 0.036621 | 0.16937 | 0.004578 | 0.10986 | 14.5706 | 122.2046 | -0.073242 | 122.1405 | 0.40741 | 0.1831 | 0.21057 | 0.022888 | -122.2458 | -122.1817 | 0.21973 | 0.16022 | 0.054932 | 0.13733 | 0.032044 | -0.022888 | -0.013733 | -0.07782 | 0.45776 | 0.26093 | 0.23346 | 0.28381 | 0.25635 | 0.19684 | 0.064087 | 0.48065 | 122.2137 | 0 | 122.2778 | 0.022888 | 122.2549 | -122.2458 | -122.2916 | 0.086975 | 122.1909 | -0.032043 | 14.621
4408.4375 | 122.3511 | -0.086975 | 122.2595 | -0.11269 | -0.043457 | -0.00018577 | 0.023578 | 0.0025721 | -0.01053 | -0.0070731 | -0.080231 | 0.0074469 | 0.062995 | 0.044278 | -0.017515 | 0.025272 | -0.0034435 | -0.13733 | 0.013733 | -0.059509 | -0.086975 | -0.009155 | -0.10986 | 0 | 14.4745 | 122.2458 | -0.10986 | 122.0261 | 0.27466 | 0.032043 | 0.082397 | 0.027466 | -122.2458 | -122.3465 | 0.07782 | 0.086975 | -0.022888 | 0.059509 | -0.050354 | -0.022888 | -0.013732 | -0.23346 | 0.36163 | 0.16937 | 0.11902 | 0.19226 | 0.14191 | 0.050354 | -0.027466 | 0.38452 | 122.1359 | 0.073242 | 122.3557 | 0.10071 | 122.3328 | -122.319 | -122.3694 | 0 | 122.113 | -0.050354 | 14.5615
4410.1406 | 122.3465 | -0.10529 | 122.2412 | -0.22713 | -0.040894 | 0.0013094 | 0.025287 | 0.00043587 | -0.0075388 | -0.0045095 | -0.10464 | 0.0083013 | 0.062141 | 0.047909 | -0.019865 | 0.026126 | -0.0040845 | -0.14648 | -0.004578 | -0.068665 | -0.10529 | -0.045776 | -0.16479 | -0.045776 | 14.4836 | 122.2595 | -0.11444 | 122.0169 | 0.21515 | -0.022888 | 0.059509 | 0.036621 | -122.2458 | -122.3465 | 0.05951 | 0.05951 | -0.059509 | 0.022889 | -0.09613 | -0.009155 | 0.01831 | -0.2243 | 0.32044 | 0.16479 | 0.082398 | 0.17395 | 0.091553 | 0.022889 | -0.036621 | 0.32959 | 122.1313 | 0.064087 | 122.374 | 0.10071 | 122.3648 | -122.3099 | -122.3557 | 0 | 122.1222 | -0.041198 | 14.5889
4411.9062 | 122.3602 | -0.064087 | 122.2733 | -0.15083 | -0.041535 | -0.00018577 | 0.018878 | 8.47e-06 | -0.012666 | -0.0030141 | -0.013092 | 0.0055243 | 0.061927 | 0.0462 | -0.017301 | 0.028262 | -0.0040845 | -0.082397 | -0.022888 | -0.027466 | 0.009155 | 0.1236 | -0.022888 | 0.068665 | 14.7263 | 122.2458 | -0.07782 | 122.049 | 0.3067 | 0.068665 | 0.11444 | 0.036621 | -122.2961 | -122.2641 | 0.18768 | 0.13275 | 0.041199 | 0.096131 | 0.004578 | -0.013733 | -0.027465 | -0.2243 | 0.37079 | 0.17853 | 0.13275 | 0.19226 | 0.14649 | 0.15106 | 0.036621 | 0.38452 | 122.1268 | 0.004578 | 122.3236 | 0.041199 | 122.3099 | -122.3007 | -122.3511 | 0.073242 | 122.113 | -0.01831 | 14.7903
4413.6562 | 122.3557 | -0.073242 | 122.2733 | -0.1432 | -0.041535 | 0.0019504 | 0.022509 | -0.00041873 | -0.01117 | -0.0053641 | -0.1077 | 0.0072333 | 0.064704 | 0.047482 | -0.019865 | 0.026553 | -0.00066651 | -0.091553 | -0.004578 | -0.041199 | -0.027466 | 0.07782 | -0.07782 | 0.022888 | 14.7354 | 122.2412 | -0.086975 | 122.081 | 0.3067 | 0.059509 | 0.11444 | 0.032043 | -122.2778 | -122.3007 | 0.15106 | 0.09613 | -0.004578 | 0.064087 | -0.036621 | -0.013733 | -0.032043 | -0.19226 | 0.37994 | 0.18768 | 0.13275 | 0.20142 | 0.14648 | 0.11902 | 0.013733 | 0.39368 | 122.168 | 0.036621 | 122.3282 | 0.068664 | 122.3145 | -122.3145 | -122.3602 | 0.045776 | 122.1542 | -0.018311 | 14.8087
4415.3594 | 122.3282 | -0.073242 | 122.3236 | -0.06691 | -0.044525 | 2.7834e-05 | 0.022296 | -0.00084593 | -0.012879 | -0.0049367 | -0.06192 | 0.0070197 | 0.060859 | 0.041928 | -0.019224 | 0.027408 | -0.0013073 | -0.14191 | 0.036621 | -0.059509 | -0.082397 | 0 | -0.086975 | -0.009155 | 14.7675 | 122.2458 | -0.09613 | 122.0261 | 0.27924 | 0.032043 | 0.10071 | 0.013733 | -122.287 | -122.406 | 0.073242 | 0.064087 | -0.013733 | 0.050354 | -0.027466 | -0.022888 | -0.077819 | -0.29755 | 0.35248 | 0.17395 | 0.10529 | 0.19684 | 0.12817 | 0.059509 | -0.022888 | 0.37537 | 122.1222 | 0.09613 | 122.3419 | 0.10986 | 122.319 | -122.3831 | -122.4197 | -0.009155 | 122.0993 | -0.068665 | 14.8407
4417.125 | 122.4701 | -0.07782 | 122.2137 | -0.15083 | -0.039826 | 0.0034456 | 0.022723 | 0.0010767 | -0.010316 | -0.0015189 | -0.074127 | 0.0061651 | 0.064063 | 0.042782 | -0.021787 | 0.025912 | -0.0055799 | -0.10071 | -0.041199 | -0.059509 | -0.018311 | 0.086975 | -0.073242 | 0.036621 | 14.8911 | 122.168 | -0.07782 | 122.1176 | 0.36163 | 0.09613 | 0.19226 | 0.018311 | -122.2549 | -122.2321 | 0.16479 | 0.11444 | 0.004578 | 0.09613 | -0.013733 | 0 | -0.045776 | -0.09613 | 0.43945 | 0.27008 | 0.17395 | 0.27008 | 0.17395 | 0.14648 | 0.041198 | 0.43945 | 122.1954 | 0.01831 | 122.2458 | 0.036621 | 122.2458 | -122.2733 | -122.2916 | 0.059509 | 122.1954 | -0.022888 | 14.9689
4418.8906 | 122.3145 | -0.11444 | 122.2778 | -0.18898 | -0.040467 | 0.0017368 | 0.022509 | 0.0027857 | -0.010743 | -0.0055777 | -0.1138 | 0.0055243 | 0.064277 | 0.052395 | -0.018369 | 0.027408 | -0.0062207 | -0.13733 | -0.004578 | -0.068665 | -0.09613 | -0.032043 | -0.16022 | -0.054932 | 14.8453 | 122.2366 | -0.10071 | 122.0032 | 0.23804 | -0.045776 | 0.050354 | 0.045776 | -122.2824 | -122.374 | 0.082398 | 0.059509 | -0.045776 | 0.013733 | -0.091552 | 0.013733 | -0.041199 | -0.27466 | 0.35248 | 0.16479 | 0.068665 | 0.15106 | 0.054932 | 0.036622 | -0.027465 | 0.33875 | 122.1039 | 0.064087 | 122.3373 | 0.10986 | 122.3511 | -122.3465 | -122.3785 | 0.018311 | 122.1176 | -0.022888 | 14.9597
4420.5938 | 122.4655 | -0.027466 | 122.2778 | -0.13557 | -0.04303 | 0.0013094 | 0.01781 | 0.00064947 | -0.015016 | -0.0042959 | 0.014374 | 0.0061651 | 0.063423 | 0.04855 | -0.01602 | 0.026553 | -0.0038709 | -0.068665 | -0.022888 | -0.022888 | 0.045776 | 0.16022 | 0.027466 | 0.11444 | 15.1932 | 122.2137 | -0.064087 | 122.1405 | 0.41199 | 0.17395 | 0.19684 | 0.004578 | -122.3007 | -122.2321 | 0.18768 | 0.14191 | 0.054932 | 0.13733 | 0.050354 | -0.036621 | -0.064087 | -0.13733 | 0.43945 | 0.2243 | 0.20142 | 0.26093 | 0.23804 | 0.1831 | 0.068664 | 0.47607 | 122.2046 | 0 | 122.2778 | 0.004578 | 122.2412 | -122.3007 | -122.3419 | 0.073242 | 122.168 | -0.041199 | 15.2206
4422.375 | 122.406 | -0.09613 | 122.2183 | -0.15846 | -0.042389 | 0.0013094 | 0.024005 | -0.0019141 | -0.010743 | -0.0057913 | -0.092438 | 0.0091559 | 0.063423 | 0.050686 | -0.017515 | 0.027835 | -0.0049389 | -0.13275 | 0 | -0.059509 | -0.10986 | -0.022888 | -0.15564 | -0.036621 | 15.0879 | 122.2183 | -0.13275 | 122.049 | 0.29297 | 0.036621 | 0.11444 | 0.036621 | -122.2183 | -122.3282 | 0.073242 | 0.059509 | -0.05951 | 0.022888 | -0.096131 | -0.036621 | 0 | -0.16937 | 0.3891 | 0.21057 | 0.13275 | 0.24719 | 0.16937 | 0.036621 | -0.050354 | 0.42572 | 122.1817 | 0.059509 | 122.3511 | 0.09613 | 122.3145 | -122.2778 | -122.3511 | -0.013733 | 122.1451 | -0.036621 | 15.184
4424.1562 | 122.4243 | -0.059509 | 122.2778 | -0.1432 | -0.041962 | 2.7834e-05 | 0.021228 | 0.00022207 | -0.013947 | -0.0049367 | -0.0008851 | 0.0068059 | 0.062568 | 0.046414 | -0.017729 | 0.024844 | -0.0036573 | -0.064087 | -0.022888 | -0.009155 | 0.032043 | 0.13733 | 0.022888 | 0.09613 | 15.239 | 122.2092 | -0.068665 | 122.0993 | 0.40283 | 0.16022 | 0.18768 | 0.050354 | -122.3007 | -122.2458 | 0.19684 | 0.15564 | 0.082397 | 0.10528 | 0.032043 | -0.009156 | -0.068665 | -0.17853 | 0.46234 | 0.24719 | 0.21973 | 0.25635 | 0.22888 | 0.14648 | 0.041198 | 0.4715 | 122.168 | -0.013733 | 122.2778 | 0.036621 | 122.2687 | -122.287 | -122.3465 | 0.091552 | 122.1588 | -0.004578 | 15.2985
4425.8438 | 122.4564 | -0.054932 | 122.2321 | -0.17372 | -0.039612 | 0.003232 | 0.021869 | 0.0023585 | -0.01053 | -0.0038687 | -0.086334 | 0.0059515 | 0.062995 | 0.041287 | -0.017942 | 0.028049 | -0.0030163 | -0.1236 | -0.022888 | -0.041199 | -0.013733 | 0.07782 | -0.073242 | 0.022888 | 15.2298 | 122.2046 | -0.11444 | 122.1176 | 0.36163 | 0.10071 | 0.19684 | 0.013733 | -122.2549 | -122.2458 | 0.13275 | 0.07782 | -0.01831 | 0.064087 | -0.032043 | -0.059509 | -0.027466 | -0.11444 | 0.41656 | 0.25177 | 0.15564 | 0.31128 | 0.21515 | 0.11902 | 0.027466 | 0.47607 | 122.2321 | 0.018311 | 122.319 | 0.032044 | 122.2595 | -122.2733 | -122.3465 | 0.041199 | 122.1725 | -0.068664 | 15.2847
4427.6094 | 122.3282 | -0.10071 | 122.2412 | -0.1432 | -0.042603 | 0.0019504 | 0.025927 | 0.0015039 | -0.012239 | -0.0038687 | -0.13516 | 0.0078741 | 0.064277 | 0.047055 | -0.01666 | 0.028476 | -0.0049389 | -0.14191 | 0.013733 | -0.064087 | -0.10529 | -0.041199 | -0.17395 | -0.045776 | 15.184 | 122.2275 | -0.10986 | 122.0215 | 0.26093 | -0.018311 | 0.073242 | 0.036621 | -122.2275 | -122.3465 | 0.059509 | 0.054932 | -0.073242 | 0.018311 | -0.10986 | -0.009155 | -0.013733 | -0.21973 | 0.36163 | 0.17395 | 0.082397 | 0.18311 | 0.091552 | 0.022888 | -0.041199 | 0.37079 | 122.1313 | 0.07782 | 122.3373 | 0.11444 | 122.3282 | -122.3053 | -122.3511 | -0.004578 | 122.1222 | -0.041199 | 15.2847
4429.3125 | 122.4838 | -0.064087 | 122.2595 | -0.22713 | -0.044525 | 0.002164 | 0.021441 | -0.00041873 | -0.015656 | -0.0019461 | -0.0039367 | 0.0065923 | 0.064704 | 0.041501 | -0.018369 | 0.025699 | -0.0040845 | -0.07782 | -0.041199 | -0.032043 | 0.036621 | 0.17853 | 0.013733 | 0.1236 | 15.5411 | 122.1817 | -0.07782 | 122.1497 | 0.44861 | 0.17853 | 0.19684 | 0.032044 | -122.3007 | -122.2229 | 0.24261 | 0.18768 | 0.07782 | 0.15564 | 0.045776 | -0.013733 | -0.077819 | -0.10986 | 0.5127 | 0.26093 | 0.24261 | 0.27466 | 0.25635 | 0.21057 | 0.068664 | 0.52643 | 122.2275 | -0.009156 | 122.2595 | 0.022888 | 122.2458 | -122.2916 | -122.3373 | 0.10071 | 122.2137 | -0.013733 | 15.6052
4431.0781 | 122.3694 | -0.091553 | 122.2321 | -0.18898 | -0.040894 | 0.0013094 | 0.022937 | 0.0029993 | -0.01117 | -0.0049367 | -0.098541 | 0.0087287 | 0.063209 | 0.046628 | -0.019651 | 0.028262 | -0.0057935 | -0.15106 | 0.013733 | -0.054932 | -0.091553 | -0.022888 | -0.13733 | -0.027466 | 15.39 | 122.2183 | -0.10986 | 122.0352 | 0.28839 | 0.009155 | 0.09613 | 0.036621 | -122.2183 | -122.3236 | 0.068665 | 0.064087 | -0.045776 | 0.027466 | -0.082397 | -0.01831 | -0.013733 | -0.19684 | 0.37994 | 0.18768 | 0.10071 | 0.20599 | 0.11902 | 0.032044 | -0.036621 | 0.39825 | 122.1451 | 0.068665 | 122.3282 | 0.10529 | 122.3099 | -122.287 | -122.3419 | 0 | 122.1268 | -0.059509 | 15.4816
4432.7812 | 122.3236 | -0.10071 | 122.2549 | -0.20424 | -0.039826 | 0.0017368 | 0.022509 | 0.0032129 | -0.010316 | -0.0040823 | -0.13516 | 0.0080877 | 0.062995 | 0.055386 | -0.017942 | 0.027408 | -0.0068615 | -0.15564 | 0 | -0.073242 | -0.11444 | -0.050354 | -0.1831 | -0.068665 | 15.4129 | 122.2321 | -0.11444 | 122.0169 | 0.2655 | -0.036621 | 0.068665 | 0.027466 | -122.2549 | -122.3694 | 0.050354 | 0.032043 | -0.082397 | 0.004577 | -0.10986 | -0.013733 | -0.022888 | -0.23804 | 0.36621 | 0.16937 | 0.064087 | 0.18311 | 0.07782 | 0.022888 | -0.041199 | 0.37994 | 122.1313 | 0.073242 | 122.3465 | 0.10071 | 122.3328 | -122.3282 | -122.3694 | -0.013733 | 122.1176 | -0.054932 | 15.5136
4434.5312 | 122.4335 | -0.050354 | 122.2321 | -0.1432 | -0.043671 | 0.001523 | 0.020587 | -0.0023413 | -0.011598 | -0.0036551 | 0.011322 | 0.0080877 | 0.061927 | 0.044278 | -0.016447 | 0.026553 | -0.0032299 | -0.11444 | -0.036621 | -0.041199 | -0.018311 | 0.07782 | -0.059509 | 0.041199 | 15.6418 | 122.1909 | -0.086975 | 122.1039 | 0.39825 | 0.13275 | 0.18768 | 0.009155 | -122.2687 | -122.2504 | 0.12817 | 0.091553 | -0.009155 | 0.082398 | -0.01831 | -0.036621 | -0.041199 | -0.12817 | 0.44861 | 0.23804 | 0.18311 | 0.27466 | 0.21973 | 0.11902 | 0.022888 | 0.48523 | 122.1909 | 0.004578 | 122.2778 | 0.013733 | 122.2412 | -122.2733 | -122.319 | 0.032043 | 122.1542 | -0.064087 | 15.6921
4436.2969 | 122.4335 | -0.073242 | 122.2137 | -0.13557 | -0.042816 | -0.00039957 | 0.018878 | -0.0019141 | -0.013734 | -0.0060049 | -0.0069885 | 0.0089423 | 0.062568 | 0.048977 | -0.018156 | 0.02634 | -2.571e-05 | -0.11902 | -0.013733 | -0.036621 | -0.032043 | 0.073242 | -0.050354 | 0.059509 | 15.7333 | 122.1725 | -0.091553 | 122.0856 | 0.40741 | 0.13733 | 0.19226 | 0.036621 | -122.2275 | -122.2458 | 0.14648 | 0.13275 | 0.022888 | 0.09613 | -0.013733 | -0.018311 | -0.041199 | -0.12817 | 0.48065 | 0.2655 | 0.21057 | 0.28381 | 0.22888 | 0.10986 | 0.004578 | 0.49896 | 122.1771 | 0.022888 | 122.2641 | 0.059509 | 122.2458 | -122.2504 | -122.3053 | 0.041199 | 122.1588 | -0.045777 | 15.8066
4438.0625 | 122.4243 | -0.091553 | 122.2321 | -0.20424 | -0.039612 | 0.00045503 | 0.024005 | -0.00020513 | -0.011598 | -0.0023733 | -0.13211 | 0.0065923 | 0.062568 | 0.055813 | -0.020933 | 0.027408 | -0.0057935 | -0.13733 | 0 | -0.054932 | -0.07782 | 0.032043 | -0.12817 | -0.009155 | 15.7196 | 122.2183 | -0.10529 | 122.1085 | 0.37079 | 0.086975 | 0.15564 | 0.036621 | -122.2321 | -122.3099 | 0.1236 | 0.082398 | -0.036621 | 0.045777 | -0.073242 | -0.013733 | -0.013733 | -0.1236 | 0.46234 | 0.24719 | 0.17853 | 0.26093 | 0.19226 | 0.086975 | -0.022888 | 0.47607 | 122.2137 | 0.054932 | 122.3236 | 0.091553 | 122.3099 | -122.287 | -122.3373 | 0.013733 | 122.2 | -0.045776 | 15.8112
4439.8125 | 122.4335 | -0.068665 | 122.2183 | -0.18898 | -0.040253 | 0.0023776 | 0.021441 | 0.0032129 | -0.010316 | -0.0015189 | -0.086334 | 0.0068059 | 0.062354 | 0.048337 | -0.019224 | 0.026981 | -0.0047253 | -0.086975 | -0.013733 | -0.027466 | 0 | 0.11444 | -0.041199 | 0.068665 | 15.8707 | 122.2137 | -0.064087 | 122.1222 | 0.4303 | 0.11902 | 0.23346 | 0.041199 | -122.2321 | -122.2183 | 0.18311 | 0.13733 | 0.027466 | 0.096131 | -0.013733 | 0.004578 | -0.004578 | -0.096131 | 0.49896 | 0.30212 | 0.18768 | 0.29755 | 0.18311 | 0.14191 | 0.027466 | 0.49439 | 122.1863 | 0.013733 | 122.2778 | 0.054932 | 122.2824 | -122.2458 | -122.2824 | 0.068665 | 122.1909 | -0.01831 | 15.9393
4441.5156 | 122.4289 | -0.07782 | 122.2458 | -0.16609 | -0.043457 | 0.001523 | 0.022509 | -0.0042639 | -0.011811 | -0.0042959 | 0.0021667 | 0.0048833 | 0.062568 | 0.049191 | -0.017942 | 0.026767 | -0.0042981 | -0.10986 | -0.022888 | -0.032043 | -0.027466 | 0.07782 | -0.07782 | 0.036621 | 15.8798 | 122.1909 | -0.082397 | 122.0856 | 0.36621 | 0.10071 | 0.15106 | 0.045777 | -122.2687 | -122.2733 | 0.15564 | 0.11444 | 0 | 0.068664 | -0.045777 | -0.004577 | -0.054932 | -0.16022 | 0.44403 | 0.22888 | 0.17853 | 0.23346 | 0.18311 | 0.10986 | 0.004577 | 0.44861 | 122.168 | 0.009155 | 122.2733 | 0.054932 | 122.2687 | -122.2778 | -122.3282 | 0.050354 | 122.1634 | -0.032043 | 15.9576
4443.2812 | 122.4197 | -0.054932 | 122.2733 | -0.21187 | -0.042603 | -0.00061317 | 0.019091 | -0.0040503 | -0.012879 | -0.0025869 | -0.031403 | 0.0044561 | 0.061073 | 0.04385 | -0.018156 | 0.027194 | -0.0028027 | -0.07782 | -0.027466 | -0.041199 | 0.013733 | 0.13733 | -0.004578 | 0.086975 | 15.9943 | 122.2 | -0.07782 | 122.1085 | 0.4303 | 0.14191 | 0.17395 | 0.013733 | -122.3007 | -122.2595 | 0.19226 | 0.14191 | 0.050354 | 0.12817 | 0.036621 | -0.022888 | -0.073242 | -0.16479 | 0.48523 | 0.22888 | 0.19684 | 0.25177 | 0.21973 | 0.17853 | 0.054932 | 0.50812 | 122.1863 | 0.013733 | 122.2778 | 0.027466 | 122.2549 | -122.3145 | -122.3511 | 0.068665 | 122.1634 | -0.022888 | 16.0492
4444.9844 | 122.4838 | -0.041199 | 122.2275 | -0.16609 | -0.042389 | 0.0013094 | 0.020587 | -0.00063233 | -0.012666 | -0.0017325 | -0.025299 | 0.0050971 | 0.061927 | 0.048977 | -0.021147 | 0.027835 | -0.0040845 | -0.09613 | -0.022888 | -0.022888 | 0.018311 | 0.13275 | 0.004578 | 0.10529 | 16.0858 | 122.1954 | -0.07782 | 122.1268 | 0.46234 | 0.17395 | 0.21515 | 0.018311 | -122.2504 | -122.2092 | 0.17395 | 0.14649 | 0.045777 | 0.12817 | 0.027466 | -0.036621 | -0.032043 | -0.10071 | 0.50354 | 0.25635 | 0.21515 | 0.29297 | 0.25177 | 0.15564 | 0.041199 | 0.54016 | 122.2046 | 0 | 122.2733 | 0.018311 | 122.2366 | -122.2504 | -122.3053 | 0.05951 | 122.168 | -0.054931 | 16.127
4446.75 | 122.4609 | -0.054932 | 122.1954 | -0.19661 | -0.039826 | 0.003232 | 0.022723 | 0.0012903 | -0.01053 | -0.0015189 | -0.098541 | 0.0053107 | 0.062568 | 0.047696 | -0.018583 | 0.025485 | -0.0045117 | -0.059509 | -0.045776 | -0.022888 | 0.036621 | 0.11902 | -0.032043 | 0.059509 | 16.0721 | 122.2046 | -0.086975 | 122.1405 | 0.44403 | 0.13275 | 0.21515 | 0.032044 | -122.2412 | -122.1588 | 0.17395 | 0.11444 | 0.022889 | 0.082397 | -0.009155 | -0.032043 | 0.009155 | -0.054932 | 0.49896 | 0.27008 | 0.18768 | 0.30212 | 0.21973 | 0.14191 | 0.059509 | 0.53101 | 122.2275 | -0.022888 | 122.2916 | 0.009156 | 122.2595 | -122.2183 | -122.2824 | 0.091553 | 122.1954 | -0.004577 | 16.127
4448.4531 | 122.4014 | -0.07782 | 122.2549 | -0.22713 | -0.044098 | 0.001523 | 0.02016 | -0.0034095 | -0.011384 | -0.0032277 | -0.046661 | 0.0053107 | 0.060432 | 0.042569 | -0.018369 | 0.024631 | -0.0068615 | -0.10986 | -0.041199 | -0.036621 | -0.018311 | 0.059509 | -0.064087 | 0.027466 | 16.0858 | 122.2 | -0.11444 | 122.0718 | 0.37994 | 0.091553 | 0.16022 | 0.041199 | -122.2961 | -122.2733 | 0.13733 | 0.10529 | 0.013733 | 0.064087 | -0.027466 | -0.036621 | -0.054932 | -0.18311 | 0.45776 | 0.23804 | 0.16937 | 0.27466 | 0.20599 | 0.09613 | 0.01831 | 0.49439 | 122.1863 | -0.004578 | 122.3145 | 0.036621 | 122.2778 | -122.2916 | -122.3694 | 0.059509 | 122.1497 | -0.032043 | 16.1636
4450.2031 | 122.3602 | -0.082397 | 122.2595 | -0.16609 | -0.044953 | 0.0013094 | 0.022509 | -0.0012731 | -0.013734 | -0.0032277 | -0.10159 | 0.0076605 | 0.062354 | 0.047909 | -0.018156 | 0.026767 | -0.0057935 | -0.15106 | 0.009155 | -0.073242 | -0.082397 | -0.013733 | -0.13275 | -0.027466 | 16.0721 | 122.2595 | -0.10529 | 122.0306 | 0.34332 | 0.027466 | 0.10071 | 0.009155 | -122.2504 | -122.3419 | 0.068664 | 0.054931 | -0.050354 | 0.045776 | -0.059509 | -0.022889 | 0 | -0.22888 | 0.42572 | 0.18311 | 0.10986 | 0.20599 | 0.13275 | 0.059509 | -0.009155 | 0.44861 | 122.1359 | 0.082397 | 122.3648 | 0.091552 | 122.3419 | -122.3328 | -122.3648 | 0 | 122.113 | -0.068665 | 16.1545
4451.9844 | 122.3648 | -0.07782 | 122.2595 | -0.12794 | -0.040894 | 0.00045503 | 0.023364 | -0.0012731 | -0.01053 | -0.0042959 | -0.12906 | 0.0074469 | 0.0615 | 0.052823 | -0.018156 | 0.027194 | -0.0055799 | -0.082397 | -0.009155 | -0.054932 | -0.032043 | 0.059509 | -0.086975 | 0.009155 | 16.1407 | 122.2321 | -0.10529 | 122.0535 | 0.35248 | 0.032043 | 0.13275 | 0.022888 | -122.2687 | -122.2916 | 0.13733 | 0.086975 | -0.009155 | 0.064087 | -0.032043 | -0.027466 | -0.027465 | -0.20599 | 0.4303 | 0.21057 | 0.10986 | 0.23804 | 0.13733 | 0.11444 | 0.022889 | 0.45776 | 122.1588 | 0.045777 | 122.3373 | 0.068665 | 122.3099 | -122.3145 | -122.3648 | 0.045777 | 122.1313 | -0.004577 | 16.2186
4453.7031 | 122.3511 | -0.073242 | 122.2504 | -0.13557 | -0.040894 | 0.00088223 | 0.02315 | -0.00063233 | -0.0088206 | -0.0032277 | -0.13211 | 0.0085149 | 0.065132 | 0.048977 | -0.019224 | 0.028049 | -0.0021619 | -0.12817 | 0.018311 | -0.068665 | -0.10529 | -0.009155 | -0.15564 | -0.036621 | 16.127 | 122.2046 | -0.10071 | 122.0444 | 0.33875 | 0.022888 | 0.11902 | 0.004577 | -122.2321 | -122.3557 | 0.064087 | 0.036621 | -0.082398 | 0.032044 | -0.086975 | -0.027466 | -0.045776 | -0.20599 | 0.41199 | 0.19226 | 0.09613 | 0.21973 | 0.1236 | 0.05951 | -0.036621 | 0.43945 | 122.1451 | 0.086976 | 122.3053 | 0.091553 | 122.2778 | -122.319 | -122.3511 | -0.032044 | 122.1176 | -0.054932 | 16.2003
4455.4688 | 122.4106 | -0.064087 | 122.2275 | -0.11269 | -0.044525 | 0.003232 | 0.0208 | -0.0017005 | -0.011811 | -0.0077139 | 0.011322 | 0.0068059 | 0.062995 | 0.041501 | -0.018156 | 0.026981 | -0.0094251 | -0.10986 | -0.022888 | -0.041199 | -0.022888 | 0.054932 | -0.073242 | 0.032043 | 16.2643 | 122.2092 | -0.07782 | 122.0673 | 0.40283 | 0.091553 | 0.16479 | 0.022888 | -122.2504 | -122.2504 | 0.11902 | 0.09613 | -0.009155 | 0.073242 | -0.032043 | -0.013733 | -0.018311 | -0.16022 | 0.46692 | 0.22888 | 0.15564 | 0.24261 | 0.16937 | 0.096131 | 0.018311 | 0.48065 | 122.1451 | 0.018311 | 122.287 | 0.041199 | 122.2733 | -122.2687 | -122.3053 | 0.041199 | 122.1313 | -0.045776 | 16.3284
4457.1719 | 122.3648 | -0.07782 | 122.2412 | -0.13557 | -0.043885 | 0.0028048 | 0.024646 | 0.0034265 | -0.011811 | -0.0038687 | -0.12296 | 0.0070197 | 0.062568 | 0.052395 | -0.018369 | 0.02634 | -0.0083569 | -0.086975 | -0.013733 | -0.059509 | -0.027466 | 0.059509 | -0.086975 | 0.009155 | 16.2781 | 122.2504 | -0.11444 | 122.0764 | 0.3891 | 0.068665 | 0.13733 | 0.018311 | -122.2549 | -122.2687 | 0.13733 | 0.086975 | -0.009155 | 0.068664 | -0.027466 | -0.036621 | 0.009155 | -0.1648 | 0.46692 | 0.21515 | 0.14649 | 0.25177 | 0.18311 | 0.11902 | 0.032043 | 0.50354 | 122.1909 | 0.045776 | 122.3648 | 0.064087 | 122.3282 | -122.3007 | -122.3557 | 0.050354 | 122.1542 | -0.009155 | 16.3559
4458.9375 | 122.3282 | -0.10986 | 122.2595 | -0.12032 | -0.043457 | 0.00088223 | 0.021869 | -0.00041873 | -0.012239 | -0.0028005 | -0.049713 | 0.0061651 | 0.062782 | 0.044278 | -0.018369 | 0.02869 | -0.0013073 | -0.16479 | 0.022888 | -0.07782 | -0.10071 | -0.004578 | -0.09613 | -0.004578 | 16.2186 | 122.2595 | -0.11444 | 121.994 | 0.35248 | 0.013733 | 0.09613 | 0.032043 | -122.2366 | -122.3602 | 0.10529 | 0.10529 | 0.013733 | 0.073242 | -0.01831 | -0.004578 | 0 | -0.2655 | 0.46234 | 0.20599 | 0.1236 | 0.21057 | 0.12817 | 0.073242 | -0.022888 | 0.46692 | 122.1085 | 0.10071 | 122.374 | 0.13275 | 122.3694 | -122.3373 | -122.374 | 0.009155 | 122.1039 | -0.054932 | 16.3284
4460.7031 | 122.3602 | -0.059509 | 122.2687 | -0.17372 | -0.041321 | 0.00088223 | 0.022296 | -0.0010595 | -0.010102 | -0.0047231 | -0.1138 | 0.0070197 | 0.0615 | 0.044064 | -0.020506 | 0.028049 | -0.0036573 | -0.10529 | -0.013733 | -0.073242 | -0.054932 | 0.054932 | -0.086975 | 0.013733 | 16.301 | 122.2183 | -0.11902 | 122.0535 | 0.37537 | 0.050354 | 0.14648 | -0.013733 | -122.2824 | -122.3236 | 0.11444 | 0.073242 | -0.027466 | 0.086975 | -0.013733 | -0.05951 | -0.050354 | -0.21515 | 0.43487 | 0.20599 | 0.10986 | 0.2655 | 0.16937 | 0.12817 | 0.01831 | 0.49438 | 122.1725 | 0.059509 | 122.3373 | 0.045776 | 122.2778 | -122.3419 | -122.3877 | 0.004577 | 122.113 | -0.045777 | 16.3605
4462.4062 | 122.3511 | -0.091553 | 122.2549 | -0.12032 | -0.044098 | 0.00066863 | 0.021869 | 0.0010767 | -0.013093 | -0.0045095 | -0.086334 | 0.0059515 | 0.062782 | 0.047696 | -0.018583 | 0.026981 | -0.0019483 | -0.15106 | 0.022888 | -0.064087 | -0.09613 | -0.013733 | -0.1236 | -0.032043 | 16.2094 | 122.2229 | -0.11444 | 122.0215 | 0.37079 | 0.032043 | 0.12817 | 0.027466 | -122.2321 | -122.3511 | 0.07782 | 0.05951 | -0.032043 | 0.032044 | -0.059509 | -0.022888 | -0.032044 | -0.23346 | 0.46234 | 0.21973 | 0.1236 | 0.24262 | 0.14648 | 0.050354 | -0.032043 | 0.48523 | 122.1359 | 0.086975 | 122.3373 | 0.11444 | 122.3145 | -122.319 | -122.3694 | -0.004577 | 122.113 | -0.059509 | 16.301
4464.1719 | 122.319 | -0.10529 | 122.2641 | -0.13557 | -0.041321 | 0.0017368 | 0.021014 | 0.0010767 | -0.015016 | -0.0042959 | -0.040558 | 0.0059515 | 0.062995 | 0.044705 | -0.018369 | 0.027835 | -0.00045291 | -0.10986 | -0.009155 | -0.041199 | -0.073242 | 0.036621 | -0.086975 | -0.009155 | 16.2415 | 122.2458 | -0.12817 | 122.0078 | 0.36163 | 0.045776 | 0.09613 | 0.064087 | -122.2733 | -122.3373 | 0.14191 | 0.096131 | 0.018311 | 0.032044 | -0.045776 | -0.022888 | -0.01831 | -0.25635 | 0.46692 | 0.20142 | 0.15106 | 0.2243 | 0.17395 | 0.07782 | -0.032043 | 0.48981 | 122.1359 | 0.032044 | 122.374 | 0.096131 | 122.3511 | -122.3053 | -122.3923 | 0.032044 | 122.113 | -0.004577 | 16.3467
4465.8906 | 122.438 | -0.09613 | 122.2137 | -0.1432 | -0.044525 | 0.0017368 | 0.0208 | 0.00043587 | -0.012666 | -0.0040823 | -0.074127 | 0.0083013 | 0.062782 | 0.048337 | -0.017942 | 0.028049 | -0.0030163 | -0.11902 | -0.009155 | -0.054932 | -0.032043 | 0.054932 | -0.082397 | 0.032043 | 16.3239 | 122.2229 | -0.10529 | 122.1085 | 0.45319 | 0.13275 | 0.21057 | 0.041198 | -122.2229 | -122.2458 | 0.15106 | 0.12817 | 0.013733 | 0.086975 | -0.027465 | -0.009156 | 0.009155 | -0.10529 | 0.54932 | 0.3067 | 0.22888 | 0.31586 | 0.23804 | 0.10986 | 0.022889 | 0.55847 | 122.2137 | 0.045777 | 122.3282 | 0.086975 | 122.319 | -122.2687 | -122.319 | 0.064087 | 122.2046 | -0.022889 | 16.42
4467.6562 | 122.374 | -0.086975 | 122.2412 | -0.16609 | -0.042389 | 0.0010958 | 0.021014 | 0.0017175 | -0.01053 | -0.0032277 | -0.071076 | 0.0080877 | 0.061714 | 0.04321 | -0.019224 | 0.026981 | -0.0083569 | -0.09613 | 0 | -0.041199 | -0.050354 | 0.050354 | -0.086975 | 0.013733 | 16.3742 | 122.2275 | -0.10071 | 122.0673 | 0.40741 | 0.073242 | 0.16479 | 0.045776 | -122.2412 | -122.2916 | 0.13733 | 0.10071 | 0 | 0.054932 | -0.045776 | -0.013733 | -0.013733 | -0.17395 | 0.49438 | 0.25177 | 0.16022 | 0.2655 | 0.17395 | 0.091553 | -0.009155 | 0.50812 | 122.168 | 0.041199 | 122.3282 | 0.086975 | 122.3145 | -122.2824 | -122.3419 | 0.036621 | 122.1542 | -0.009155 | 16.4612
4469.4219 | 122.3236 | -0.082397 | 122.2549 | -0.1432 | -0.039398 | 2.7834e-05 | 0.021869 | 0.0021447 | -0.01053 | -0.00066434 | -0.11075 | 0.0063787 | 0.061073 | 0.044919 | -0.01901 | 0.026981 | -0.0047253 | -0.082397 | 0 | -0.045776 | -0.041199 | 0.050354 | -0.09613 | 0.009155 | 16.4017 | 122.2046 | -0.11902 | 122.0261 | 0.37994 | 0.041199 | 0.14191 | 0.036621 | -122.2549 | -122.2961 | 0.13275 | 0.091552 | -0.013733 | 0.054931 | -0.050354 | -0.036622 | -0.050354 | -0.22888 | 0.46234 | 0.2243 | 0.1236 | 0.26093 | 0.16022 | 0.09613 | 0.004577 | 0.49896 | 122.1451 | 0.045776 | 122.3236 | 0.082397 | 122.287 | -122.3007 | -122.374 | 0.041198 | 122.1085 | 0 | 16.4841
4471.1875 | 122.3557 | -0.091553 | 122.2687 | -0.11269 | -0.041748 | 0.0017368 | 0.018664 | -0.00041873 | -0.012025 | -0.0060049 | -0.01004 | 0.0059515 | 0.062354 | 0.039578 | -0.017515 | 0.027194 | -0.0042981 | -0.082397 | -0.022888 | -0.036621 | -0.032043 | 0.10071 | -0.041199 | 0.059509 | 16.5298 | 122.1909 | -0.09613 | 122.0352 | 0.41657 | 0.07782 | 0.12817 | 0.054932 | -122.2916 | -122.3007 | 0.19226 | 0.15106 | 0.050354 | 0.09613 | -0.004578 | -0.004577 | -0.07782 | -0.23346 | 0.50812 | 0.21973 | 0.16937 | 0.2243 | 0.17395 | 0.13733 | 0.004578 | 0.5127 | 122.1313 | 0.013733 | 122.287 | 0.068665 | 122.2824 | -122.3053 | -122.3648 | 0.05951 | 122.1268 | 0.009156 | 16.6214
4472.8906 | 122.3557 | -0.086975 | 122.2458 | -0.097427 | -0.041535 | 0.00088223 | 0.023364 | 0.0015039 | -0.0094614 | -0.0055777 | -0.10159 | 0.0059515 | 0.063209 | 0.042355 | -0.017729 | 0.027408 | -0.0040845 | -0.091553 | 0 | -0.045776 | -0.032043 | 0.068665 | -0.07782 | 0.009155 | 16.6946 | 122.2183 | -0.10986 | 122.0627 | 0.41199 | 0.068665 | 0.16022 | 0.041199 | -122.2458 | -122.2778 | 0.15564 | 0.09613 | 0.009155 | 0.054931 | -0.032044 | -0.022888 | -0.027466 | -0.18311 | 0.49896 | 0.24719 | 0.15564 | 0.27008 | 0.17853 | 0.11444 | 0.013733 | 0.52185 | 122.1725 | 0.045776 | 122.3282 | 0.086975 | 122.3053 | -122.2916 | -122.3557 | 0.054932 | 122.1497 | -0.004578 | 16.7816
4474.6562 | 122.3419 | -0.082397 | 122.2366 | -0.097427 | -0.041748 | 0.001523 | 0.024005 | 0.00064947 | -0.012666 | -0.0032277 | -0.09549 | 0.0061651 | 0.063423 | 0.0509 | -0.017301 | 0.028262 | -0.0019483 | -0.14648 | 0.013733 | -0.064087 | -0.11444 | -0.036621 | -0.16937 | -0.059509 | 16.5482 | 122.2183 | -0.11444 | 122.0032 | 0.34332 | -0.004578 | 0.091553 | 0.01831 | -122.2229 | -122.3511 | 0.045776 | 0.022888 | -0.086976 | 0.004578 | -0.10529 | -0.032044 | -0.01831 | -0.23346 | 0.42572 | 0.17395 | 0.077819 | 0.20599 | 0.10986 | 0.027466 | -0.050354 | 0.45776 | 122.1176 | 0.07782 | 122.3328 | 0.09613 | 122.3007 | -122.3007 | -122.3511 | -0.032044 | 122.0856 | -0.064087 | 16.6306
4476.4219 | 122.4701 | -0.064087 | 122.2321 | -0.089798 | -0.044098 | -0.00061317 | 0.019519 | 0.00086307 | -0.011598 | -0.0053641 | 0.029632 | 0.0068059 | 0.062141 | 0.041714 | -0.018583 | 0.024844 | -0.0036573 | -0.082397 | -0.036621 | -0.018311 | 0.027466 | 0.1831 | 0 | 0.1236 | 16.7953 | 122.1954 | -0.07782 | 122.1359 | 0.50354 | 0.19226 | 0.21973 | 0.045776 | -122.2687 | -122.2046 | 0.24719 | 0.18768 | 0.064087 | 0.14191 | 0.018311 | -0.013733 | -0.036621 | -0.096131 | 0.56763 | 0.28381 | 0.25635 | 0.29755 | 0.27008 | 0.20142 | 0.045777 | 0.58136 | 122.2137 | -0.01831 | 122.2733 | 0.027466 | 122.2595 | -122.2504 | -122.3099 | 0.091553 | 122.2 | -0.01831 | 16.8594
4478.125 | 122.4197 | -0.073242 | 122.2412 | -0.18898 | -0.043671 | -0.001254 | 0.021014 | 0.0015039 | -0.01117 | -0.0060049 | -0.01004 | 0.0061651 | 0.062141 | 0.040433 | -0.018583 | 0.024631 | -0.0062207 | -0.13275 | -0.036621 | -0.032043 | -0.036621 | 0.064087 | -0.054932 | 0.036621 | 16.6443 | 122.1954 | -0.086975 | 122.0581 | 0.43488 | 0.11444 | 0.17853 | 0.041199 | -122.2778 | -122.2778 | 0.13733 | 0.10986 | 0.01831 | 0.068664 | -0.022889 | -0.013733 | -0.045776 | -0.18311 | 0.50812 | 0.25177 | 0.18768 | 0.2655 | 0.20142 | 0.09613 | -0.004578 | 0.52185 | 122.1451 | -0.004578 | 122.2824 | 0.036621 | 122.2687 | -122.2733 | -122.3282 | 0.036621 | 122.1313 | -0.059509 | 16.7175
4479.8906 | 122.4014 | -0.068665 | 122.2366 | -0.1432 | -0.042816 | 0.001523 | 0.02016 | 0.0019311 | -0.014161 | -0.0038687 | -0.034454 | 0.0065923 | 0.064277 | 0.048337 | -0.019865 | 0.025912 | -0.00066651 | -0.073242 | -0.036621 | -0.032043 | 0.032043 | 0.10986 | 0 | 0.068665 | 16.7816 | 122.1817 | -0.082397 | 122.0444 | 0.44861 | 0.11444 | 0.17395 | 0.036622 | -122.2733 | -122.2046 | 0.17853 | 0.13733 | 0.068665 | 0.10071 | 0.032043 | -0.013732 | -0.054931 | -0.19226 | 0.51727 | 0.24261 | 0.18311 | 0.25635 | 0.19684 | 0.14191 | 0.064086 | 0.531 | 122.1268 | -0.004578 | 122.2641 | 0.032044 | 122.2504 | -122.2687 | -122.319 | 0.10071 | 122.113 | -0.004577 | 16.8503
4481.5938 | 122.3969 | -0.050354 | 122.2321 | -0.13557 | -0.042603 | 0.00088223 | 0.022296 | 0.00086307 | -0.012879 | -0.0032277 | -0.028351 | 0.0057379 | 0.065345 | 0.045346 | -0.019865 | 0.025912 | -0.0087841 | -0.10071 | -0.018311 | -0.041199 | -0.013733 | 0.09613 | -0.059509 | 0.054932 | 16.745 | 122.1863 | -0.086975 | 122.0627 | 0.44403 | 0.11444 | 0.19684 | 0.009155 | -122.2504 | -122.2458 | 0.14648 | 0.10529 | -0.009155 | 0.096131 | -0.01831 | -0.036621 | -0.045777 | -0.16937 | 0.49439 | 0.24719 | 0.16479 | 0.28381 | 0.20142 | 0.13733 | 0.027466 | 0.53101 | 122.1497 | 0.022888 | 122.2733 | 0.032043 | 122.2366 | -122.2733 | -122.319 | 0.036621 | 122.113 | -0.050354 | 16.7953
4483.375 | 122.4014 | -0.059509 | 122.2229 | -0.16609 | -0.04303 | 0.0028048 | 0.0208 | -0.00041873 | -0.012239 | -0.0034415 | -0.016144 | 0.0057379 | 0.060645 | 0.048764 | -0.020719 | 0.028262 | 0.00040169 | -0.073242 | -0.027466 | -0.041199 | 0.022888 | 0.1236 | -0.018311 | 0.07782 | 16.832 | 122.2229 | -0.082397 | 122.0535 | 0.4715 | 0.1236 | 0.16022 | 0.01831 | -122.2504 | -122.2 | 0.1831 | 0.13733 | 0.041198 | 0.11902 | 0.022888 | -0.022888 | 0 | -0.16937 | 0.53101 | 0.21973 | 0.1831 | 0.24261 | 0.20599 | 0.16479 | 0.064087 | 0.55389 | 122.1359 | 0.013733 | 122.3053 | 0.032043 | 122.2824 | -122.2641 | -122.3053 | 0.082397 | 122.113 | -0.013733 | 16.8915
4485.0625 | 122.406 | -0.064087 | 122.2046 | -0.2195 | -0.040039 | 0.00045503 | 0.022082 | -0.0019141 | -0.010102 | -0.0051505 | -0.028351 | 0.0063787 | 0.0615 | 0.042569 | -0.018583 | 0.026553 | -0.0047253 | -0.091553 | -0.032043 | -0.022888 | 0.004578 | 0.1236 | -0.032043 | 0.073242 | 16.9006 | 122.1817 | -0.091553 | 122.081 | 0.47607 | 0.11902 | 0.20142 | 0.041199 | -122.2366 | -122.2 | 0.18768 | 0.13733 | 0.032044 | 0.09613 | -0.009155 | -0.027466 | -0.022888 | -0.1236 | 0.54016 | 0.2655 | 0.18311 | 0.29297 | 0.21057 | 0.14648 | 0.027466 | 0.56763 | 122.1725 | -0.009155 | 122.2733 | 0.032044 | 122.2458 | -122.2275 | -122.2961 | 0.068665 | 122.1451 | -0.027466 | 16.9647
4486.8281 | 122.3648 | -0.091553 | 122.2412 | -0.15846 | -0.044525 | 0.00088223 | 0.021228 | 0.00064947 | -0.012879 | -0.0023733 | -0.058869 | 0.0070197 | 0.062354 | 0.047696 | -0.017942 | 0.027194 | -0.0068615 | -0.07782 | -0.032043 | -0.032043 | -0.013733 | 0.082397 | -0.036621 | 0.041199 | 16.9235 | 122.2046 | -0.10986 | 122.0215 | 0.41657 | 0.07782 | 0.13733 | 0.05951 | -122.2733 | -122.2549 | 0.17395 | 0.13275 | 0.054932 | 0.073242 | -0.004578 | -0.01831 | -0.036621 | -0.21973 | 0.50812 | 0.22888 | 0.16937 | 0.24719 | 0.18768 | 0.11444 | 0.01831 | 0.52643 | 122.1313 | 0 | 122.3145 | 0.05951 | 122.2961 | -122.2733 | -122.3511 | 0.07782 | 122.113 | 0.013733 | 17.0151
4488.6094 | 122.3923 | -0.07782 | 122.2412 | -0.1432 | -0.043671 | 0.0010958 | 0.023364 | 0.0027857 | -0.0092478 | -0.0083547 | -0.1138 | 0.0059515 | 0.064704 | 0.051968 | -0.019438 | 0.026981 | -0.0055799 | -0.13275 | 0.013733 | -0.064087 | -0.082397 | -0.013733 | -0.16022 | -0.027466 | 16.9052 | 122.1954 | -0.10071 | 122.0718 | 0.41657 | 0.073242 | 0.16937 | 0.013733 | -122.2275 | -122.3236 | 0.064087 | 0.050354 | -0.082397 | 0.036621 | -0.09613 | -0.022888 | -0.045776 | -0.16937 | 0.49439 | 0.24719 | 0.15106 | 0.27008 | 0.17395 | 0.050354 | -0.01831 | 0.51727 | 122.1725 | 0.07782 | 122.2961 | 0.091553 | 122.2733 | -122.3053 | -122.3419 | -0.004577 | 122.1497 | -0.054931 | 16.983
4490.3125 | 122.4609 | -0.054932 | 122.2 | -0.16609 | -0.044312 | 0.00045503 | 0.019732 | -0.0010595 | -0.011384 | -0.0038687 | -0.019196 | 0.0074469 | 0.062782 | 0.045559 | -0.020719 | 0.024844 | -0.0077161 | -0.10986 | -0.032043 | -0.041199 | -0.004578 | 0.09613 | -0.022888 | 0.07782 | 17.0654 | 122.1909 | -0.091553 | 122.1085 | 0.54016 | 0.16479 | 0.22888 | 0.013733 | -122.2321 | -122.2046 | 0.15106 | 0.13275 | 0.032044 | 0.11902 | 0.018311 | -0.036621 | -0.009155 | -0.091553 | 0.59509 | 0.28381 | 0.21973 | 0.32044 | 0.25635 | 0.13733 | 0.036621 | 0.63171 | 122.2 | 0.009156 | 122.2824 | 0.022889 | 122.2458 | -122.2412 | -122.2916 | 0.050354 | 122.1634 | -0.054931 | 17.1204
4492.0938 | 122.4014 | -0.073242 | 122.2275 | -0.18135 | -0.042816 | 0.0010958 | 0.021441 | 0.0012903 | -0.013093 | -0.0042959 | -0.06192 | 0.0068059 | 0.058936 | 0.051755 | -0.020719 | 0.026126 | -0.0025891 | -0.13733 | -0.032043 | -0.050354 | -0.022888 | 0.054932 | -0.064087 | 0.045776 | 17.038 | 122.1817 | -0.10071 | 122.0627 | 0.46234 | 0.10529 | 0.1831 | 0.022888 | -122.2595 | -122.2504 | 0.12817 | 0.11902 | 0.009155 | 0.09613 | -0.013733 | -0.027466 | -0.045776 | -0.16479 | 0.53558 | 0.25635 | 0.17853 | 0.28381 | 0.20599 | 0.10529 | 0.027466 | 0.56305 | 122.1634 | 0.018311 | 122.2824 | 0.041199 | 122.2549 | -122.2778 | -122.3282 | 0.050354 | 122.1359 | -0.064087 | 17.1112
4493.875 | 122.4335 | -0.036621 | 122.2137 | -0.19661 | -0.041962 | 0.0013094 | 0.02315 | 0.0059901 | -0.010102 | -0.0030141 | -0.092438 | 0.0065923 | 0.060645 | 0.0509 | -0.019438 | 0.029758 | -0.0075025 | -0.073242 | -0.050354 | -0.032043 | 0.022888 | 0.11444 | -0.027466 | 0.068665 | 17.1707 | 122.1863 | -0.07782 | 122.1405 | 0.51727 | 0.14648 | 0.25177 | 0.004578 | -122.2641 | -122.1909 | 0.15106 | 0.10529 | 0.009155 | 0.10071 | 0.004577 | -0.041199 | -0.027466 | -0.073242 | 0.55389 | 0.28839 | 0.18311 | 0.32959 | 0.2243 | 0.14648 | 0.054931 | 0.59509 | 122.2183 | -0.018311 | 122.2641 | -0.013733 | 122.2229 | -122.2458 | -122.2916 | 0.059509 | 122.1771 | -0.036621 | 17.2073
4495.5781 | 122.4472 | -0.059509 | 122.2046 | -0.18135 | -0.043885 | 0.00024143 | 0.0208 | -0.0034095 | -0.012025 | -0.0051505 | -0.022247 | 0.0057379 | 0.060005 | 0.048123 | -0.020292 | 0.027194 | -0.0066479 | -0.073242 | -0.041199 | -0.022888 | 0.059509 | 0.17853 | 0.027466 | 0.11444 | 17.3584 | 122.2 | -0.07782 | 122.1268 | 0.56763 | 0.19226 | 0.23804 | 0.036621 | -122.2458 | -122.1451 | 0.23804 | 0.17395 | 0.086975 | 0.13733 | 0.050354 | -0.018311 | -0.004578 | -0.07782 | 0.62714 | 0.29755 | 0.25177 | 0.31586 | 0.27008 | 0.20142 | 0.082397 | 0.64545 | 122.2046 | -0.018311 | 122.2778 | 0.01831 | 122.2595 | -122.2275 | -122.2824 | 0.11902 | 122.1863 | -0.013733 | 17.4179
4497.3438 | 122.319 | -0.10529 | 122.2687 | -0.15846 | -0.044525 | -0.0018948 | 0.023578 | 8.47e-06 | -0.012666 | -0.0036551 | -0.080231 | 0.0068059 | 0.062354 | 0.045132 | -0.019651 | 0.026553 | -0.0057935 | -0.12817 | -0.013733 | -0.050354 | -0.082397 | 0.022888 | -0.11902 | -0.018311 | 17.2073 | 122.1954 | -0.13733 | 121.994 | 0.42114 | 0.050354 | 0.10071 | 0.054932 | -122.2824 | -122.3511 | 0.12817 | 0.086975 | -0.013733 | 0.032043 | -0.068665 | -0.032043 | -0.073242 | -0.27466 | 0.52643 | 0.20599 | 0.15564 | 0.23804 | 0.18768 | 0.073242 | -0.032043 | 0.55847 | 122.1313 | 0.036621 | 122.3328 | 0.091553 | 122.3007 | -122.319 | -122.406 | 0.022889 | 122.0993 | -0.022888 | 17.3126
4499.125 | 122.3419 | -0.09613 | 122.2504 | -0.16609 | -0.041748 | 0.0013094 | 0.023364 | 0.0066309 | -0.010102 | -0.0030141 | -0.11685 | 0.0070197 | 0.063209 | 0.047909 | -0.018583 | 0.028476 | -0.0072889 | -0.086975 | -0.004578 | -0.059509 | -0.032043 | 0.054932 | -0.10986 | -0.004578 | 17.2394 | 122.2275 | -0.11902 | 122.0398 | 0.42572 | 0.032043 | 0.14648 | 0.036621 | -122.2549 | -122.2824 | 0.15106 | 0.091552 | -0.013733 | 0.054931 | -0.050354 | -0.022889 | -0.022888 | -0.21057 | 0.52185 | 0.24261 | 0.12817 | 0.2655 | 0.15106 | 0.11444 | 0.027466 | 0.54474 | 122.1588 | 0.054931 | 122.3465 | 0.091552 | 122.3236 | -122.3099 | -122.3694 | 0.064087 | 122.1359 | 0.009155 | 17.3355
4500.8281 | 122.4518 | -0.054932 | 122.2229 | -0.1432 | -0.042389 | -0.00082677 | 0.019091 | -0.0036231 | -0.012879 | -0.0087819 | -0.022247 | 0.0074469 | 0.062782 | 0.039364 | -0.017729 | 0.028049 | -0.0038709 | -0.073242 | -0.022888 | -0.027466 | 0.041199 | 0.15106 | 0.018311 | 0.11902 | 17.4088 | 122.1634 | -0.07782 | 122.1222 | 0.58594 | 0.20142 | 0.25635 | 0.027466 | -122.2458 | -122.1817 | 0.20599 | 0.17395 | 0.073243 | 0.14649 | 0.045777 | -0.022888 | -0.059509 | -0.10071 | 0.64087 | 0.31128 | 0.25635 | 0.33417 | 0.27924 | 0.17853 | 0.068665 | 0.66376 | 122.2 | 0.004578 | 122.2412 | 0.032044 | 122.2183 | -122.2504 | -122.3007 | 0.096131 | 122.1771 | -0.01831 | 17.4637
4502.5938 | 122.3511 | -0.11444 | 122.2641 | -0.089798 | -0.044525 | 0.00088223 | 0.020587 | 0.0027857 | -0.012452 | -0.0032277 | -0.1199 | 0.0072333 | 0.062568 | 0.048123 | -0.017729 | 0.027194 | -0.0055799 | -0.1236 | 0.004578 | -0.064087 | -0.086975 | -0.018311 | -0.1236 | -0.013733 | 17.3401 | 122.2229 | -0.11902 | 122.0078 | 0.43488 | 0.045776 | 0.13275 | 0.050354 | -122.2595 | -122.3511 | 0.09613 | 0.10071 | -0.009155 | 0.050354 | -0.059509 | -0.004578 | -0.041199 | -0.25635 | 0.54932 | 0.24719 | 0.16022 | 0.25177 | 0.16479 | 0.045776 | -0.022888 | 0.55389 | 122.1268 | 0.068665 | 122.3419 | 0.11902 | 122.3373 | -122.3282 | -122.3831 | 0.027466 | 122.1222 | -0.009155 | 17.4545
4504.3438 | 122.319 | -0.10071 | 122.2321 | -0.20424 | -0.041107 | 0.0017368 | 0.021655 | -0.0019141 | -0.0092478 | -0.0042959 | -0.13516 | 0.0087287 | 0.064704 | 0.048337 | -0.017301 | 0.027408 | -0.0034435 | -0.11902 | 0.009155 | -0.059509 | -0.10986 | -0.032043 | -0.16022 | -0.054932 | 17.3904 | 122.2183 | -0.10071 | 121.9986 | 0.39825 | 0.009155 | 0.14191 | 0.041199 | -122.2229 | -122.3419 | 0.068665 | 0.045776 | -0.059509 | 0.004577 | -0.10071 | 0 | -0.013733 | -0.23346 | 0.49896 | 0.24262 | 0.10986 | 0.24262 | 0.10986 | 0.027466 | -0.050354 | 0.49896 | 122.0993 | 0.068664 | 122.319 | 0.10986 | 122.319 | -122.2916 | -122.3328 | -0.009155 | 122.0993 | -0.018311 | 17.4912
4506.1094 | 122.3236 | -0.10071 | 122.2366 | -0.18135 | -0.040894 | 0.00066863 | 0.0255 | 0.0076989 | -0.010316 | -0.0040823 | -0.12601 | 0.0076605 | 0.063636 | 0.051327 | -0.017942 | 0.026981 | -0.0023755 | -0.12817 | 0.018311 | -0.073242 | -0.10986 | -0.027466 | -0.16479 | -0.054932 | 17.4316 | 122.2092 | -0.1236 | 122.0032 | 0.41199 | 0 | 0.12817 | 0.027466 | -122.2183 | -122.3465 | 0.073242 | 0.045776 | -0.064087 | 0.01831 | -0.091553 | -0.022888 | -0.027466 | -0.23346 | 0.5127 | 0.22888 | 0.10071 | 0.25177 | 0.1236 | 0.045776 | -0.036621 | 0.53558 | 122.1268 | 0.091553 | 122.3328 | 0.11902 | 122.3099 | -122.3099 | -122.3602 | -0.009155 | 122.1039 | -0.027466 | 17.5323
4507.875 | 122.3328 | -0.10529 | 122.2321 | -0.15846 | -0.04068 | 0.0023776 | 0.024646 | -0.00063233 | -0.0092478 | -0.0072867 | -0.12296 | 0.0070197 | 0.064277 | 0.0462 | -0.01901 | 0.027621 | -0.0030163 | -0.14191 | 0.018311 | -0.064087 | -0.10529 | -0.009155 | -0.17395 | -0.054932 | 17.5049 | 122.2183 | -0.11902 | 122.0078 | 0.42114 | 0.013733 | 0.13733 | 0.041199 | -122.2137 | -122.3373 | 0.096131 | 0.050354 | -0.068664 | 0.009155 | -0.10986 | -0.013733 | -0.013733 | -0.22431 | 0.52643 | 0.24262 | 0.11902 | 0.25635 | 0.13275 | 0.054932 | -0.041199 | 0.54016 | 122.1268 | 0.082398 | 122.3373 | 0.1236 | 122.3236 | -122.2961 | -122.3511 | 0 | 122.113 | -0.036621 | 17.6102
4509.6406 | 122.3557 | -0.09613 | 122.2321 | -0.16609 | -0.041107 | 0.00088223 | 0.021441 | 0.0015039 | -0.009675 | -0.00066434 | -0.1077 | 0.0074469 | 0.063209 | 0.038296 | -0.019224 | 0.027835 | -0.0042981 | -0.10529 | 0 | -0.059509 | -0.032043 | 0.073242 | -0.09613 | 0.009155 | 17.6331 | 122.2 | -0.10071 | 122.0444 | 0.48981 | 0.086975 | 0.16479 | 0.036621 | -122.2321 | -122.2641 | 0.16937 | 0.10528 | 0 | 0.068664 | -0.036621 | -0.004578 | -0.032044 | -0.18768 | 0.58594 | 0.26092 | 0.1831 | 0.2655 | 0.18768 | 0.13275 | 0.027466 | 0.59052 | 122.1451 | 0.059509 | 122.3007 | 0.09613 | 122.2961 | -122.2916 | -122.3328 | 0.064087 | 122.1405 | -0.009156 | 17.7292
4511.4062 | 122.4426 | -0.064087 | 122.2183 | -0.20424 | -0.044312 | 0.001523 | 0.018451 | 0.0025721 | -0.012239 | -0.0057913 | -0.0008851 | 0.0053107 | 0.064063 | 0.048977 | -0.017515 | 0.027408 | -0.0070751 | -0.07782 | -0.032043 | -0.027466 | 0.018311 | 0.14648 | -0.009155 | 0.09613 | 17.8116 | 122.1725 | -0.086975 | 122.1085 | 0.60883 | 0.20599 | 0.25635 | 0.036621 | -122.2504 | -122.2 | 0.21057 | 0.16022 | 0.054932 | 0.1236 | 0.018311 | -0.022888 | -0.045777 | -0.10986 | 0.67291 | 0.32044 | 0.27008 | 0.34332 | 0.29297 | 0.17395 | 0.045777 | 0.6958 | 122.1954 | -0.004577 | 122.2595 | 0.032044 | 122.2366 | -122.2458 | -122.3053 | 0.082398 | 122.1725 | -0.013733 | 17.8757
4513.1719 | 122.3007 | -0.10986 | 122.2275 | -0.18898 | -0.040039 | 0.0010958 | 0.023578 | 0.0012903 | -0.009675 | -0.0034415 | -0.12601 | 0.0083013 | 0.063636 | 0.046628 | -0.01901 | 0.028262 | -0.0045117 | -0.14191 | 0.009155 | -0.07782 | -0.10986 | -0.064087 | -0.19226 | -0.073242 | 17.72 | 122.2183 | -0.13733 | 121.994 | 0.41657 | 0.009155 | 0.14191 | 0.032043 | -122.2183 | -122.3373 | 0.045776 | 0.036621 | -0.082398 | 0.004578 | -0.11444 | -0.027466 | -0.009155 | -0.23346 | 0.52643 | 0.25177 | 0.11902 | 0.27924 | 0.14648 | 0.013733 | -0.032043 | 0.55389 | 122.1313 | 0.086975 | 122.3557 | 0.11902 | 122.3282 | -122.3053 | -122.3648 | 0 | 122.1039 | -0.032044 | 17.8299
4514.875 | 122.1222 | -0.39825 | 121.7514 | -0.18898 | -0.042603 | 0.001523 | 0.019732 | -0.00020513 | -0.01352 | -0.0030141 | -0.028351 | 0.0087287 | 0.063209 | 0.040646 | -0.019438 | 0.026767 | -0.0066479 | -0.16479 | -0.11902 | -0.12817 | -0.091553 | 0 | -0.12817 | -0.041199 | 17.6651 | 121.6965 | -0.42572 | 121.4813 | 0.19226 | -0.23346 | -0.1831 | 0.27008 | -121.8704 | -121.843 | 0.39825 | 0.35706 | 0.27008 | 0.086975 | 0 | -0.027466 | -0.054932 | -0.27008 | 0.59052 | 0.21515 | 0.16479 | 0.24261 | 0.19226 | 0.12817 | 0.036621 | 0.61798 | 121.907 | 0.009155 | 122.1222 | 0.27924 | 122.0947 | -121.8796 | -122.1771 | 0.3067 | 121.8796 | 0.23346 | 18.0634
4516.6406 | 122.1542 | -0.07782 | 122.0444 | -0.17372 | -0.042176 | 0.00088223 | 0.023578 | 0.0010767 | -0.010957 | -0.0010915 | -0.10464 | 0.0085149 | 0.062782 | 0.04855 | -0.018156 | 0.029544 | -0.0023755 | -0.091553 | 0.018311 | -0.050354 | -0.050354 | 0.032043 | -0.07782 | 0.013733 | 17.9626 | 122.0215 | -0.091553 | 121.843 | 0.52643 | 0.09613 | 0.1831 | 0.027466 | -122.0261 | -122.0947 | 0.10986 | 0.091553 | 0 | 0.064087 | -0.027466 | -0.013733 | -0.022889 | -0.20142 | 0.60425 | 0.26092 | 0.17395 | 0.27466 | 0.18768 | 0.082397 | 0 | 0.61798 | 121.9345 | 0.068665 | 122.113 | 0.096131 | 122.0993 | -122.0947 | -122.1359 | 0.027466 | 121.9208 | -0.013733 | 18.0405
4518.4062 | 122.2916 | -0.054932 | 122.0398 | -0.15083 | -0.042389 | 0.0013094 | 0.019305 | -0.0027685 | -0.0092478 | -0.0081411 | -0.01004 | 0.0070197 | 0.06385 | 0.035519 | -0.018369 | 0.025272 | -0.0070751 | -0.10071 | -0.022888 | -0.036621 | -0.004578 | 0.11444 | -0.018311 | 0.10071 | 18.1824 | 122.0306 | -0.07782 | 121.9711 | 0.61798 | 0.21057 | 0.26093 | 0.018311 | -122.0627 | -122.0444 | 0.16937 | 0.15564 | 0.036621 | 0.13733 | 0.01831 | -0.022888 | -0.009155 | -0.068665 | 0.67291 | 0.31586 | 0.2655 | 0.33875 | 0.28839 | 0.15106 | 0.032043 | 0.6958 | 122.049 | 0.013733 | 122.1085 | 0.032044 | 122.0856 | -122.0764 | -122.1176 | 0.050354 | 122.0261 | -0.045776 | 18.2373
4520.0938 | 122.2046 | -0.086975 | 122.1085 | -0.18135 | -0.04068 | 0.00088223 | 0.022723 | -0.0010595 | -0.0092478 | -0.0042959 | -0.1199 | 0.0083013 | 0.061714 | 0.049618 | -0.018156 | 0.029117 | -0.0077161 | -0.14191 | 0 | -0.068665 | -0.10071 | -0.013733 | -0.16022 | -0.041199 | 18.1 | 122.0947 | -0.10986 | 121.8979 | 0.46692 | 0.036621 | 0.14648 | 0.01831 | -122.1085 | -122.2092 | 0.073242 | 0.045776 | -0.073242 | 0.027466 | -0.091552 | -0.022888 | -0.013732 | -0.21057 | 0.55389 | 0.23346 | 0.1236 | 0.25635 | 0.14648 | 0.054932 | -0.032043 | 0.57678 | 122.0078 | 0.068665 | 122.2046 | 0.086975 | 122.1817 | -122.1771 | -122.2183 | -0.013733 | 121.9849 | -0.054932 | 18.187
4521.8594 | 122.3282 | -0.050354 | 122.0901 | -0.17372 | -0.04303 | -0.00039957 | 0.018023 | -0.0012731 | -0.01117 | -0.0042959 | 0.0021667 | 0.0068059 | 0.063209 | 0.044278 | -0.020078 | 0.025485 | -0.0040845 | -0.073242 | -0.004578 | -0.027466 | 0.036621 | 0.16022 | 0.022888 | 0.11444 | 18.3105 | 122.0581 | -0.068665 | 122.0123 | 0.64087 | 0.21057 | 0.27008 | 0.022888 | -122.0947 | -122.0535 | 0.21057 | 0.16479 | 0.073242 | 0.14191 | 0.050354 | -0.018311 | -0.032044 | -0.07782 | 0.69122 | 0.32044 | 0.26093 | 0.33875 | 0.27924 | 0.18768 | 0.064087 | 0.70953 | 122.081 | 0.022888 | 122.1268 | 0.045776 | 122.1085 | -122.1176 | -122.1588 | 0.086975 | 122.0627 | -0.022888 | 18.3609
4523.625 | 122.3602 | -0.036621 | 122.1039 | -0.18135 | -0.043244 | 0.0013094 | 0.0208 | -0.0025549 | -0.012666 | -0.0066457 | -0.022247 | 0.0050971 | 0.060859 | 0.042782 | -0.019651 | 0.02634 | -0.0032299 | -0.086975 | -0.027466 | -0.041199 | 0.018311 | 0.13733 | 0 | 0.09613 | 18.3197 | 122.0901 | -0.064087 | 122.0078 | 0.64087 | 0.21973 | 0.25635 | -0.004578 | -122.1313 | -122.0856 | 0.17395 | 0.13275 | 0.036621 | 0.13733 | 0.041199 | -0.027466 | -0.013733 | -0.096131 | 0.67749 | 0.29297 | 0.25635 | 0.32044 | 0.28381 | 0.17853 | 0.05951 | 0.70496 | 122.0718 | 0.013733 | 122.1542 | 0.009155 | 122.1268 | -122.1451 | -122.168 | 0.054932 | 122.0444 | -0.050354 | 18.3563
4525.3125 | 122.2092 | -0.10529 | 122.1634 | -0.1432 | -0.04068 | 0.00066863 | 0.023791 | -0.0019141 | -0.011811 | -0.0053641 | -0.12906 | 0.0097967 | 0.063209 | 0.046414 | -0.017088 | 0.028903 | -0.0051525 | -0.14648 | 0.022888 | -0.054932 | -0.11902 | -0.054932 | -0.15564 | -0.050354 | 18.132 | 122.1222 | -0.11444 | 121.9116 | 0.45319 | 0.013733 | 0.13275 | 0.050354 | -122.1405 | -122.2824 | 0.050354 | 0.054932 | -0.050354 | 0.004578 | -0.10071 | -0.009155 | -0.041199 | -0.25177 | 0.55847 | 0.23804 | 0.11902 | 0.24719 | 0.12817 | 0 | -0.064087 | 0.56763 | 122.0261 | 0.07782 | 122.2366 | 0.12817 | 122.2275 | -122.2183 | -122.2778 | -0.013733 | 122.0169 | -0.041198 | 18.2373
4527.0781 | 122.2504 | -0.082397 | 122.1497 | -0.12794 | -0.04068 | 0.00088223 | 0.024005 | 0.0010767 | -0.011811 | -0.0038687 | -0.1138 | 0.0078741 | 0.0615 | 0.045559 | -0.01901 | 0.027835 | -0.0060071 | -0.091553 | 0.009155 | -0.054932 | -0.032043 | 0.064087 | -0.082397 | 0.022888 | 18.4021 | 122.1359 | -0.10071 | 121.9711 | 0.54932 | 0.091553 | 0.18768 | 0.027465 | -122.1405 | -122.1817 | 0.14648 | 0.10528 | 0 | 0.07782 | -0.027465 | -0.018311 | -0.013733 | -0.17853 | 0.63171 | 0.27008 | 0.17395 | 0.28839 | 0.19226 | 0.11902 | 0.022889 | 0.65002 | 122.0718 | 0.064087 | 122.2366 | 0.091552 | 122.2183 | -122.2046 | -122.2504 | 0.050354 | 122.0535 | -0.009156 | 18.4845
4528.8438 | 122.2504 | -0.068665 | 122.1817 | -0.15083 | -0.04303 | 0.00066863 | 0.021014 | 0.0023585 | -0.011598 | -0.0032277 | -0.022247 | 0.0055243 | 0.063209 | 0.05325 | -0.018156 | 0.027194 | -0.0047253 | -0.091553 | -0.027466 | -0.041199 | -0.041199 | 0.068665 | -0.059509 | 0.027466 | 18.338 | 122.1359 | -0.1236 | 121.9299 | 0.53101 | 0.07782 | 0.13275 | 0.027466 | -122.2092 | -122.2229 | 0.13733 | 0.096131 | 0.009156 | 0.068665 | -0.01831 | -0.054931 | -0.045777 | -0.25177 | 0.59967 | 0.20142 | 0.14649 | 0.25635 | 0.20142 | 0.10986 | 0 | 0.6546 | 122.0535 | 0.013733 | 122.2595 | 0.041199 | 122.2046 | -122.2229 | -122.3053 | 0.027466 | 121.9986 | -0.022888 | 18.4067
4530.5938 | 122.2687 | -0.082397 | 122.1771 | -0.15846 | -0.038544 | 0.00045503 | 0.023364 | -0.0010595 | -0.009675 | -0.0038687 | -0.10464 | 0.0091559 | 0.062995 | 0.049191 | -0.018583 | 0.02869 | -0.0047253 | -0.10071 | -0.009155 | -0.036621 | -0.045776 | 0.045776 | -0.082397 | 0.004578 | 18.2831 | 122.1542 | -0.091553 | 121.9711 | 0.53558 | 0.07782 | 0.17853 | 0.045776 | -122.1863 | -122.2229 | 0.12817 | 0.086975 | 0 | 0.041199 | -0.045776 | -0.009156 | -0.022888 | -0.20599 | 0.61798 | 0.26092 | 0.16022 | 0.27008 | 0.16937 | 0.082397 | -0.009155 | 0.62714 | 122.0627 | 0.027466 | 122.2458 | 0.073242 | 122.2366 | -122.2137 | -122.2687 | 0.036621 | 122.0535 | -0.018311 | 18.3655
4532.2969 | 122.3557 | -0.07782 | 122.1497 | -0.13557 | -0.043671 | -0.00039957 | 0.02016 | -0.0014867 | -0.012452 | -0.0064321 | 0.0082703 | 0.0078741 | 0.062568 | 0.036374 | -0.017515 | 0.02634 | 0.00082889 | -0.11444 | -0.022888 | -0.032043 | -0.036621 | 0.086975 | -0.050354 | 0.050354 | 18.4982 | 122.0947 | -0.082397 | 122.0078 | 0.63629 | 0.1831 | 0.25177 | 0.045777 | -122.1725 | -122.1863 | 0.16479 | 0.12817 | 0.027466 | 0.082397 | -0.018311 | -0.004577 | -0.054931 | -0.14191 | 0.71411 | 0.32959 | 0.26092 | 0.33417 | 0.2655 | 0.11902 | -0.004578 | 0.71869 | 122.0901 | 0.009155 | 122.1771 | 0.054932 | 122.1725 | -122.1817 | -122.2321 | 0.041199 | 122.0856 | -0.036621 | 18.576
4534.0156 | 122.3511 | -0.054932 | 122.1725 | -0.15846 | -0.044098 | -0.00061317 | 0.022723 | -0.0025549 | -0.009675 | -0.0040823 | -0.0069885 | 0.0059515 | 0.0615 | 0.0462 | -0.019865 | 0.027408 | -0.0045117 | -0.073242 | -0.027466 | -0.041199 | 0.022888 | 0.13275 | 0.004578 | 0.09613 | 18.5486 | 122.1222 | -0.091553 | 122.0261 | 0.65002 | 0.19684 | 0.24719 | 0.013733 | -122.2 | -122.1497 | 0.18768 | 0.15106 | 0.05951 | 0.13733 | 0.045777 | -0.036621 | -0.050354 | -0.14648 | 0.70496 | 0.30212 | 0.25177 | 0.33874 | 0.28839 | 0.17395 | 0.064087 | 0.74158 | 122.1176 | 0.013733 | 122.2137 | 0.027466 | 122.1771 | -122.2137 | -122.2641 | 0.07782 | 122.081 | -0.01831 | 18.6035
4535.7969 | 122.3145 | -0.064087 | 122.1451 | -0.20424 | -0.041962 | 0.001523 | 0.022296 | 0.0029993 | -0.007966 | -0.0049367 | -0.1077 | 0.0080877 | 0.062995 | 0.051968 | -0.018583 | 0.027621 | -0.0034435 | -0.14191 | 0.022888 | -0.059509 | -0.082397 | 0.009155 | -0.13275 | -0.022888 | 18.4662 | 122.1497 | -0.11444 | 122.0123 | 0.58136 | 0.09613 | 0.21515 | 0.004578 | -122.1222 | -122.2275 | 0.073242 | 0.041199 | -0.068664 | 0.036621 | -0.073242 | -0.050354 | 0.004577 | -0.13275 | 0.64545 | 0.27924 | 0.16022 | 0.32959 | 0.21057 | 0.068664 | -0.022888 | 0.6958 | 122.1268 | 0.082397 | 122.2641 | 0.086975 | 122.2137 | -122.2046 | -122.2595 | -0.01831 | 122.0764 | -0.07782 | 18.5303
4537.5625 | 122.3373 | -0.064087 | 122.2 | -0.1432 | -0.041321 | 0.0025912 | 0.019946 | -0.0010595 | -0.011811 | -0.0055777 | -0.022247 | 0.0085149 | 0.061073 | 0.043637 | -0.020078 | 0.027621 | -0.0034435 | -0.11444 | -0.041199 | -0.032043 | -0.022888 | 0.064087 | -0.064087 | 0.050354 | 18.5532 | 122.1405 | -0.086975 | 122.0078 | 0.64087 | 0.14648 | 0.23346 | 0.032044 | -122.2412 | -122.2229 | 0.12817 | 0.11444 | 0 | 0.082397 | -0.032044 | -0.022888 | -0.059509 | -0.19226 | 0.70496 | 0.29755 | 0.21057 | 0.32043 | 0.23346 | 0.09613 | 0.009155 | 0.72784 | 122.0947 | -0.009156 | 122.2275 | 0.022888 | 122.2046 | -122.2321 | -122.287 | 0.041199 | 122.0718 | -0.050354 | 18.6172
4539.2812 | 122.3602 | -0.059509 | 122.1634 | -0.18898 | -0.041535 | 0.0019504 | 0.021441 | -0.0019141 | -0.015229 | -0.0049367 | -0.019196 | 0.0074469 | 0.06385 | 0.044278 | -0.018156 | 0.027194 | -0.0049389 | -0.11902 | -0.004578 | -0.036621 | -0.045776 | 0.054932 | -0.068665 | 0.022888 | 18.6172 | 122.1222 | -0.091553 | 122.0261 | 0.63629 | 0.14191 | 0.24261 | 0.022888 | -122.168 | -122.2092 | 0.11444 | 0.082397 | -0.009156 | 0.059509 | -0.032044 | -0.032044 | -0.041199 | -0.13733 | 0.6958 | 0.30212 | 0.20142 | 0.33417 | 0.23346 | 0.091553 | -0.009155 | 0.72784 | 122.1176 | 0.032043 | 122.2137 | 0.054931 | 122.1817 | -122.2 | -122.2549 | 0.013733 | 122.0856 | -0.05951 | 18.6768
4541.0625 | 122.3877 | -0.050354 | 122.1451 | -0.15083 | -0.041107 | 0.0017368 | 0.022937 | 0.0027857 | -0.010316 | -0.0030141 | -0.080231 | 0.0078741 | 0.05915 | 0.045559 | -0.019224 | 0.028049 | -0.00045291 | -0.10071 | 0 | -0.041199 | -0.004578 | 0.086975 | -0.064087 | 0.041199 | 18.7408 | 122.1313 | -0.073242 | 122.0764 | 0.67749 | 0.16479 | 0.29755 | 0.009155 | -122.1451 | -122.1497 | 0.13733 | 0.091553 | -0.013733 | 0.082398 | -0.022888 | -0.022888 | -0.013733 | -0.068665 | 0.72784 | 0.3479 | 0.21515 | 0.37079 | 0.23804 | 0.12817 | 0.036621 | 0.75073 | 122.1497 | 0.041199 | 122.2046 | 0.050354 | 122.1817 | -122.1863 | -122.2183 | 0.045776 | 122.1268 | -0.050354 | 18.7912
4542.7812 | 122.3511 | -0.064087 | 122.168 | -0.23476 | -0.042816 | 0.0013094 | 0.021441 | -0.0025549 | -0.012666 | -0.0038687 | -0.046661 | 0.0068059 | 0.062995 | 0.049618 | -0.018369 | 0.026553 | -0.0055799 | -0.11902 | -0.027466 | -0.032043 | -0.004578 | 0.07782 | -0.068665 | 0.036621 | 18.7637 | 122.1222 | -0.086975 | 122.0123 | 0.63629 | 0.16022 | 0.22888 | 0.032044 | -122.1954 | -122.1725 | 0.14191 | 0.10071 | -0.004578 | 0.068664 | -0.036622 | -0.022888 | -0.045777 | -0.15564 | 0.70038 | 0.29297 | 0.2243 | 0.31586 | 0.24719 | 0.10986 | 0.027465 | 0.72327 | 122.0993 | 0.004577 | 122.2092 | 0.036621 | 122.1863 | -122.2 | -122.2549 | 0.059509 | 122.0764 | -0.054932 | 18.8278
4544.5625 | 122.2824 | -0.082397 | 122.2137 | -0.12032 | -0.041321 | 0.0017368 | 0.024218 | 8.47e-06 | -0.014375 | -0.0077139 | -0.14432 | 0.0083013 | 0.062782 | 0.050473 | -0.017729 | 0.02869 | -0.00045291 | -0.07782 | -0.013733 | -0.045776 | -0.036621 | 0.050354 | -0.10986 | 0.009155 | 18.7912 | 122.1588 | -0.082397 | 121.994 | 0.61798 | 0.07782 | 0.20142 | 0.036621 | -122.2275 | -122.2504 | 0.13275 | 0.091552 | -0.027466 | 0.054931 | -0.064087 | 0 | -0.054932 | -0.21973 | 0.70038 | 0.28381 | 0.16022 | 0.28381 | 0.16022 | 0.09613 | 0.009155 | 0.70038 | 122.0764 | 0.032043 | 122.2412 | 0.068664 | 122.2412 | -122.2595 | -122.2961 | 0.045776 | 122.0764 | 0.004577 | 18.8736
4546.3125 | 122.2916 | -0.10071 | 122.2183 | -0.097427 | -0.04303 | -0.00039957 | 0.022296 | 0.00022207 | -0.0094614 | -0.0023733 | -0.10159 | 0.0070197 | 0.062141 | 0.043637 | -0.019865 | 0.027621 | -0.0047253 | -0.14191 | 0.013733 | -0.07782 | -0.086975 | -0.022888 | -0.1236 | -0.018311 | 18.8095 | 122.1817 | -0.10071 | 121.9803 | 0.6134 | 0.082397 | 0.17395 | 0.022888 | -122.2046 | -122.3053 | 0.07782 | 0.082397 | -0.022888 | 0.059509 | -0.045776 | 0 | -0.036621 | -0.23804 | 0.71411 | 0.27466 | 0.18311 | 0.27466 | 0.18311 | 0.054932 | -0.009155 | 0.71411 | 122.081 | 0.091553 | 122.2824 | 0.11444 | 122.2824 | -122.2961 | -122.319 | 0.013733 | 122.081 | -0.041199 | 18.9102
4548.0781 | 122.406 | -0.054932 | 122.1863 | -0.15846 | -0.044098 | 0.0023776 | 0.018451 | 0.00064947 | -0.011384 | -0.0066457 | -0.013092 | 0.0065923 | 0.061927 | 0.041073 | -0.01666 | 0.024844 | -0.0085705 | -0.073242 | -0.032043 | -0.018311 | 0.045776 | 0.1831 | 0.036621 | 0.11444 | 19.1025 | 122.1222 | -0.091553 | 122.0673 | 0.77362 | 0.25177 | 0.3067 | 0.036621 | -122.2183 | -122.1405 | 0.23804 | 0.16937 | 0.091553 | 0.13275 | 0.054932 | -0.036621 | -0.064087 | -0.11902 | 0.82855 | 0.36163 | 0.3067 | 0.39825 | 0.34332 | 0.20142 | 0.064087 | 0.86517 | 122.1588 | -0.013732 | 122.2137 | 0.022889 | 122.1771 | -122.2046 | -122.2778 | 0.10071 | 122.1222 | -0.01831 | 19.1574
4549.8438 | 122.3969 | -0.045776 | 122.1542 | -0.16609 | -0.040467 | 0.003232 | 0.023364 | 0.00086307 | -0.011384 | -0.0057913 | -0.077179 | 0.0072333 | 0.059791 | 0.048123 | -0.020719 | 0.029758 | -0.0047253 | -0.07782 | -0.022888 | -0.027466 | 0.018311 | 0.11902 | -0.050354 | 0.064087 | 19.0567 | 122.1451 | -0.073242 | 122.1039 | 0.73242 | 0.17853 | 0.32501 | 0.01831 | -122.1771 | -122.1359 | 0.16479 | 0.10986 | -0.004578 | 0.091553 | -0.022888 | -0.027466 | -0.009155 | -0.050354 | 0.7782 | 0.37079 | 0.2243 | 0.39825 | 0.25177 | 0.14649 | 0.045777 | 0.80566 | 122.1771 | 0.004578 | 122.2183 | 0.022888 | 122.1909 | -122.1817 | -122.2275 | 0.064087 | 122.1497 | -0.032044 | 19.1025
4551.5469 | 122.2824 | -0.10071 | 122.2 | -0.13557 | -0.044739 | 0.0017368 | 0.022937 | 0.00022207 | -0.013307 | -0.0040823 | -0.077179 | 0.0063787 | 0.062568 | 0.052823 | -0.018797 | 0.025699 | -0.0066479 | -0.13733 | -0.013733 | -0.059509 | -0.082397 | 0.004578 | -0.11444 | 0 | 19.1437 | 122.1725 | -0.10071 | 121.9528 | 0.62714 | 0.086975 | 0.16479 | 0.041199 | -122.2137 | -122.2824 | 0.10529 | 0.10071 | -0.013733 | 0.059509 | -0.054932 | 0 | -0.027466 | -0.24719 | 0.72784 | 0.2655 | 0.18768 | 0.2655 | 0.18768 | 0.064087 | -0.022888 | 0.72784 | 122.0535 | 0.045776 | 122.2733 | 0.086975 | 122.2733 | -122.2595 | -122.3007 | 0.018311 | 122.0535 | -0.036621 | 19.2444
4553.2969 | 122.3007 | -0.073242 | 122.2275 | -0.16609 | -0.042176 | 0.0019504 | 0.024005 | 0.00043587 | -0.011598 | -0.0051505 | -0.13211 | 0.0074469 | 0.064063 | 0.049618 | -0.01901 | 0.027835 | -0.0068615 | -0.10071 | 0.009155 | -0.045776 | -0.041199 | 0.059509 | -0.086975 | 0.018311 | 19.2581 | 122.1725 | -0.09613 | 122.0032 | 0.68665 | 0.11444 | 0.21973 | 0.027466 | -122.2183 | -122.2687 | 0.13275 | 0.091553 | -0.013733 | 0.064087 | -0.041199 | -0.022888 | -0.054932 | -0.2243 | 0.75989 | 0.29297 | 0.18768 | 0.31586 | 0.21057 | 0.10528 | 0.004577 | 0.78278 | 122.0993 | 0.054931 | 122.2687 | 0.082397 | 122.2458 | -122.2733 | -122.3236 | 0.032043 | 122.0764 | -0.027466 | 19.3314
4555 | 122.3145 | -0.073242 | 122.2046 | -0.15083 | -0.040894 | -0.00039957 | 0.022723 | 0.0027857 | -0.012025 | -0.0049367 | -0.11685 | 0.01001 | 0.064491 | 0.046841 | -0.018369 | 0.02634 | -0.0049389 | -0.091553 | 0.004578 | -0.059509 | -0.036621 | 0.059509 | -0.068665 | 0.022888 | 19.3405 | 122.1634 | -0.091553 | 122.0352 | 0.71869 | 0.1236 | 0.24719 | 0.013733 | -122.2 | -122.2412 | 0.13275 | 0.09613 | 0.004577 | 0.082397 | -0.009156 | -0.018311 | -0.041199 | -0.16937 | 0.79193 | 0.32043 | 0.19684 | 0.33874 | 0.21515 | 0.11902 | 0.022888 | 0.81024 | 122.1268 | 0.064087 | 122.2549 | 0.07782 | 122.2366 | -122.2641 | -122.2961 | 0.036621 | 122.1085 | -0.018311 | 19.4138
4556.7656 | 122.3511 | -0.07782 | 122.2 | -0.17372 | -0.041535 | 0.001523 | 0.019305 | 0.00022207 | -0.012239 | -0.0053641 | 0.011322 | 0.0068059 | 0.062995 | 0.043637 | -0.018156 | 0.025699 | -0.0040845 | -0.11444 | -0.036621 | -0.050354 | -0.041199 | 0.068665 | -0.059509 | 0.050354 | 19.4183 | 122.1176 | -0.09613 | 122.0352 | 0.74158 | 0.17395 | 0.27466 | 0.027466 | -122.2366 | -122.2412 | 0.14649 | 0.12817 | 0.018311 | 0.10071 | -0.009155 | -0.01831 | -0.082397 | -0.16479 | 0.8194 | 0.35248 | 0.25177 | 0.37079 | 0.27008 | 0.11902 | 0.009155 | 0.83771 | 122.1313 | 0.013733 | 122.2137 | 0.041199 | 122.1954 | -122.2504 | -122.2961 | 0.036621 | 122.113 | -0.036621 | 19.4962
4558.5469 | 122.3969 | -0.050354 | 122.1817 | -0.15083 | -0.045166 | -0.00061317 | 0.018664 | -0.0019141 | -0.011598 | -0.0064321 | -0.022247 | 0.0080877 | 0.062354 | 0.0462 | -0.019651 | 0.026767 | -0.0023755 | -0.082397 | -0.036621 | 0 | 0.041199 | 0.15106 | 0.013733 | 0.09613 | 19.6655 | 122.1405 | -0.086975 | 122.081 | 0.83313 | 0.24261 | 0.32501 | 0.050354 | -122.2183 | -122.1405 | 0.20142 | 0.14648 | 0.064087 | 0.09613 | 0.013733 | -0.036621 | -0.041199 | -0.10071 | 0.88348 | 0.37537 | 0.29297 | 0.41199 | 0.32959 | 0.15106 | 0.041199 | 0.92011 | 122.168 | -0.036621 | 122.2275 | 0.013733 | 122.1909 | -122.1817 | -122.2687 | 0.091553 | 122.1313 | -0.032043 | 19.7159
4560.3125 | 122.2733 | -0.10986 | 122.2137 | -0.1432 | -0.04303 | 0.001523 | 0.024646 | -0.0012731 | -0.012666 | -0.0034415 | -0.12906 | 0.0076605 | 0.064063 | 0.046841 | -0.017301 | 0.028476 | -0.0013073 | -0.11902 | -0.009155 | -0.068665 | -0.068665 | 0.018311 | -0.14648 | -0.032043 | 19.5374 | 122.1771 | -0.10986 | 121.9757 | 0.66376 | 0.059509 | 0.21057 | 0.041198 | -122.2229 | -122.2824 | 0.12817 | 0.07782 | -0.036621 | 0.036622 | -0.077819 | 0 | -0.036621 | -0.23804 | 0.77362 | 0.32043 | 0.16937 | 0.32043 | 0.16937 | 0.086976 | 0 | 0.77362 | 122.0856 | 0.05951 | 122.287 | 0.10071 | 122.287 | -122.2824 | -122.3236 | 0.041198 | 122.0856 | -0.009156 | 19.6472
4562.0156 | 122.2595 | -0.10071 | 122.2137 | -0.17372 | -0.041321 | 0.003232 | 0.023791 | 0.0042811 | -0.0094614 | -0.0034415 | -0.10159 | 0.0076605 | 0.067054 | 0.059231 | -0.016447 | 0.027194 | -0.0017347 | -0.12817 | 0.022888 | -0.073242 | -0.10986 | -0.045776 | -0.15564 | -0.045776 | 19.6609 | 122.1909 | -0.11902 | 121.9666 | 0.68665 | 0.073242 | 0.21515 | 0.027466 | -122.1909 | -122.3236 | 0.054932 | 0.054932 | -0.054932 | 0.027466 | -0.082398 | -0.018311 | -0.022888 | -0.24719 | 0.78735 | 0.31586 | 0.17395 | 0.33417 | 0.19226 | 0.027466 | -0.036621 | 0.80566 | 122.0856 | 0.09613 | 122.3099 | 0.1236 | 122.2916 | -122.287 | -122.3328 | -0.009155 | 122.0673 | -0.027466 | 19.7617
4563.7188 | 122.3282 | -0.07782 | 122.1771 | -0.1432 | -0.040253 | -0.00061317 | 0.022723 | 0.0023585 | -0.009675 | -0.0047231 | -0.1077 | 0.0087287 | 0.063636 | 0.046414 | -0.018583 | 0.028262 | -0.0034435 | -0.14648 | -0.004578 | -0.07782 | -0.086975 | -0.018311 | -0.1236 | -0.032043 | 19.8166 | 122.168 | -0.10986 | 122.0169 | 0.74616 | 0.12817 | 0.26093 | 0 | -122.1817 | -122.2641 | 0.059509 | 0.045777 | -0.045776 | 0.045777 | -0.045776 | -0.032043 | -0.009155 | -0.16022 | 0.82398 | 0.33875 | 0.20599 | 0.37079 | 0.23804 | 0.059509 | -0.009155 | 0.85602 | 122.1268 | 0.073242 | 122.2778 | 0.073242 | 122.2458 | -122.2549 | -122.287 | -0.009155 | 122.0947 | -0.068664 | 19.8944
4565.4844 | 122.3328 | -0.10529 | 122.2183 | -0.16609 | -0.041748 | 0.00088223 | 0.0208 | 0.0055627 | -0.011811 | -0.0030141 | -0.086334 | 0.0068059 | 0.064491 | 0.047268 | -0.018369 | 0.027621 | -0.0025891 | -0.09613 | -0.013733 | -0.041199 | -0.036621 | 0.07782 | -0.082397 | 0.018311 | 20.018 | 122.1954 | -0.09613 | 122.0215 | 0.78735 | 0.15564 | 0.27924 | 0.064087 | -122.2321 | -122.2549 | 0.18311 | 0.1236 | 0.022889 | 0.05951 | -0.041198 | 0.009156 | -0.022888 | -0.19684 | 0.89264 | 0.38452 | 0.26093 | 0.37537 | 0.25177 | 0.11902 | 0.004578 | 0.88348 | 122.1176 | 0.027466 | 122.2916 | 0.091553 | 122.3007 | -122.2595 | -122.3145 | 0.068665 | 122.1268 | 0.009156 | 20.1233
4567.1719 | 122.374 | -0.068665 | 122.2092 | -0.17372 | -0.043885 | 0.0010958 | 0.019305 | 0.00022207 | -0.012239 | -0.0064321 | -0.025299 | 0.0078741 | 0.063209 | 0.035306 | -0.018156 | 0.025699 | -0.0036573 | -0.11444 | -0.013733 | -0.041199 | -0.045776 | 0.059509 | -0.07782 | 0.041199 | 20.2194 | 122.1497 | -0.091553 | 122.0352 | 0.83313 | 0.19684 | 0.29755 | 0.027466 | -122.2229 | -122.2549 | 0.12817 | 0.10986 | -0.009155 | 0.082398 | -0.036621 | -0.022888 | -0.059509 | -0.17395 | 0.9018 | 0.36621 | 0.2655 | 0.3891 | 0.28839 | 0.10071 | -0.004577 | 0.92468 | 122.1268 | 0.027466 | 122.2412 | 0.054932 | 122.2183 | -122.2504 | -122.3007 | 0.022889 | 122.1039 | -0.045776 | 20.2881
4568.9375 | 122.4106 | -0.032043 | 122.1863 | -0.1432 | -0.042389 | -0.00039957 | 0.018451 | 0.0023585 | -0.01053 | -0.0013051 | -0.0008851 | 0.0076605 | 0.064063 | 0.044491 | -0.018797 | 0.02634 | 0.0023243 | -0.068665 | -0.036621 | -0.022888 | 0.041199 | 0.17395 | 0.032043 | 0.12817 | 20.4941 | 122.1451 | -0.059509 | 122.0947 | 0.92468 | 0.27008 | 0.35248 | 0.009155 | -122.2229 | -122.1451 | 0.20599 | 0.16022 | 0.064086 | 0.15106 | 0.054931 | -0.027466 | -0.041198 | -0.091552 | 0.95673 | 0.38452 | 0.30212 | 0.41199 | 0.32959 | 0.19684 | 0.064087 | 0.98419 | 122.1542 | -0.013733 | 122.2046 | -0.004578 | 122.1771 | -122.2092 | -122.2458 | 0.073242 | 122.1268 | -0.036622 | 20.5261
4570.7188 | 122.3648 | -0.059509 | 122.1725 | -0.19661 | -0.041748 | 0.001523 | 0.021014 | -0.00020513 | -0.012666 | -0.0036551 | -0.031403 | 0.0070197 | 0.063636 | 0.051327 | -0.018583 | 0.025272 | -0.0066479 | -0.086975 | -0.032043 | -0.022888 | 0 | 0.14648 | -0.054932 | 0.068665 | 20.6223 | 122.1817 | -0.082397 | 122.0535 | 0.86975 | 0.20599 | 0.31128 | 0.036621 | -122.2046 | -122.1725 | 0.20599 | 0.12817 | 0.004577 | 0.091553 | -0.032044 | -0.022888 | 0.009156 | -0.11902 | 0.92926 | 0.37079 | 0.2655 | 0.39368 | 0.28839 | 0.16937 | 0.022888 | 0.95215 | 122.1359 | -0.009155 | 122.2641 | 0.027466 | 122.2412 | -122.1954 | -122.2549 | 0.059509 | 122.113 | -0.027466 | 20.6818
4572.4219 | 122.2824 | -0.11902 | 122.2183 | -0.19661 | -0.041107 | 0.00088223 | 0.025927 | 0.0038537 | -0.011384 | -0.0034415 | -0.12601 | 0.0076605 | 0.062782 | 0.056027 | -0.018797 | 0.029117 | -0.0015209 | -0.13275 | 0.018311 | -0.082397 | -0.1236 | -0.064087 | -0.1831 | -0.041199 | 20.6268 | 122.1909 | -0.10986 | 121.9803 | 0.76904 | 0.073242 | 0.24261 | 0.036622 | -122.2 | -122.3419 | 0.054932 | 0.07782 | -0.064086 | 0.041198 | -0.10071 | 0.009156 | -0.027466 | -0.23804 | 0.88806 | 0.36163 | 0.19226 | 0.35248 | 0.18311 | 0.01831 | -0.041199 | 0.87891 | 122.0901 | 0.10071 | 122.3007 | 0.13733 | 122.3099 | -122.3007 | -122.3282 | -0.004577 | 122.0993 | -0.013732 | 20.7459
4574.2031 | 122.3694 | -0.068665 | 122.1817 | -0.12032 | -0.042816 | 0.00066863 | 0.019519 | 0.0012903 | -0.012666 | -0.0038687 | -0.037506 | 0.0065923 | 0.063423 | 0.042782 | -0.017942 | 0.026981 | -0.0081433 | -0.13275 | -0.004578 | -0.022888 | -0.032043 | 0.073242 | -0.07782 | 0.032043 | 20.929 | 122.1359 | -0.068665 | 122.0306 | 0.89264 | 0.19684 | 0.31586 | 0.045777 | -122.1863 | -122.2137 | 0.14191 | 0.10071 | -0.009155 | 0.054931 | -0.054932 | 0 | -0.045777 | -0.15106 | 0.9613 | 0.38452 | 0.2655 | 0.38452 | 0.2655 | 0.09613 | -0.009155 | 0.9613 | 122.0993 | 0.01831 | 122.2046 | 0.064087 | 122.2046 | -122.2046 | -122.2504 | 0.036622 | 122.0993 | -0.064086 | 20.9976
4575.9688 | 122.3648 | -0.073242 | 122.1954 | -0.13557 | -0.04303 | 0.001523 | 0.0208 | 0.00064947 | -0.01053 | -0.0047231 | -0.025299 | 0.0097967 | 0.064277 | 0.044278 | -0.018156 | 0.028049 | -0.0045117 | -0.11444 | -0.032043 | -0.018311 | -0.018311 | 0.086975 | -0.059509 | 0.045776 | 21.1441 | 122.1313 | -0.086975 | 122.0398 | 0.91095 | 0.21973 | 0.32501 | 0.054931 | -122.2275 | -122.2137 | 0.16022 | 0.11902 | 0.013733 | 0.064087 | -0.041198 | -0.013733 | -0.064087 | -0.15564 | 0.98419 | 0.39825 | 0.29297 | 0.41199 | 0.3067 | 0.10529 | 0 | 0.99793 | 122.1268 | -0.013732 | 122.2183 | 0.041199 | 122.2046 | -122.2137 | -122.2824 | 0.054931 | 122.113 | -0.041199 | 21.2173
4577.7344 | 122.4426 | -0.07782 | 122.1634 | -0.17372 | -0.041962 | 0.00024143 | 0.019305 | 0.0015039 | -0.010102 | -0.0047231 | -0.022247 | 0.0065923 | 0.062354 | 0.048337 | -0.019438 | 0.027621 | -0.0049389 | -0.082397 | -0.036621 | -0.032043 | 0.022888 | 0.15564 | 0.022888 | 0.11902 | 21.4233 | 122.1359 | -0.068665 | 122.0947 | 1.0345 | 0.29297 | 0.39825 | 0.045777 | -122.2 | -122.1405 | 0.23346 | 0.19684 | 0.10071 | 0.15106 | 0.054931 | 0.009155 | -0.027466 | -0.068664 | 1.1124 | 0.47607 | 0.37079 | 0.46692 | 0.36163 | 0.18768 | 0.054931 | 1.1032 | 122.1634 | -0.004578 | 122.2046 | 0.041199 | 122.2137 | -122.1954 | -122.2321 | 0.10071 | 122.1725 | -0.004577 | 21.5012
4579.4531 | 122.3923 | -0.045776 | 122.1817 | -0.18135 | -0.043244 | -0.00039957 | 0.020373 | -0.0023413 | -0.013307 | -0.0057913 | -0.046661 | 0.0085149 | 0.061927 | 0.045559 | -0.019438 | 0.024631 | -0.0019483 | -0.11444 | -0.022888 | -0.054932 | -0.036621 | 0.064087 | -0.050354 | 0.041199 | 21.5149 | 122.1497 | -0.09613 | 122.0581 | 0.97961 | 0.24261 | 0.35248 | -0.009156 | -122.2046 | -122.2183 | 0.10986 | 0.086975 | -0.004578 | 0.096131 | 0.004578 | -0.050354 | -0.032044 | -0.1236 | 1.0254 | 0.39825 | 0.28839 | 0.44861 | 0.33874 | 0.11902 | 0.018311 | 1.0757 | 122.1542 | 0.032044 | 122.2458 | 0.022888 | 122.1954 | -122.2366 | -122.2778 | 0.009155 | 122.1039 | -0.068665 | 21.5607
4581.2188 | 122.319 | -0.07782 | 122.2137 | -0.16609 | -0.042603 | 0.00045503 | 0.023364 | 0.0025721 | -0.012239 | -0.0034415 | -0.13211 | 0.0076605 | 0.0615 | 0.048764 | -0.018797 | 0.025912 | -0.0051525 | -0.073242 | 0.004578 | -0.054932 | -0.018311 | 0.045776 | -0.082397 | 0.027466 | 21.7575 | 122.168 | -0.086975 | 122.0444 | 0.9613 | 0.18768 | 0.32501 | 0.022888 | -122.2092 | -122.2321 | 0.1236 | 0.10529 | -0.004577 | 0.082398 | -0.027465 | -0.009155 | -0.045776 | -0.16937 | 1.0391 | 0.40283 | 0.2655 | 0.41199 | 0.27466 | 0.10071 | 0.036621 | 1.0483 | 122.1313 | 0.05951 | 122.2549 | 0.082398 | 122.2458 | -122.2687 | -122.3007 | 0.059509 | 122.1222 | 0.004578 | 21.8353
4582.9688 | 122.2961 | -0.10529 | 122.1771 | -0.16609 | -0.041962 | 0.003232 | 0.023578 | -0.00063233 | -0.0081796 | -0.0036551 | -0.10159 | 0.0093695 | 0.063636 | 0.05325 | -0.018583 | 0.029758 | -0.0045117 | -0.15106 | 0 | -0.086975 | -0.14191 | -0.041199 | -0.16937 | -0.064087 | 21.8582 | 122.1542 | -0.13733 | 121.9666 | 0.90179 | 0.09613 | 0.25635 | 0.018311 | -122.1771 | -122.319 | 0.064087 | 0.041199 | -0.064087 | 0.022888 | -0.082398 | -0.032043 | -0.022888 | -0.21057 | 1.0071 | 0.36163 | 0.20142 | 0.39368 | 0.23346 | 0.045776 | -0.054932 | 1.0391 | 122.1039 | 0.086975 | 122.2916 | 0.10529 | 122.2595 | -122.2641 | -122.3145 | -0.036621 | 122.0718 | -0.045776 | 21.9635
4584.7344 | 122.4152 | 0.42572 | 122.7081 | -0.15083 | -0.041107 | -0.0018948 | 0.022723 | 0.0053491 | -0.012452 | -0.0040823 | -0.1199 | 0.0065923 | 0.064491 | 0.045773 | -0.018797 | 0.027408 | -0.0077161 | 0.37537 | 0.50354 | 0.43488 | 0.41199 | 0.48981 | 0.37537 | 0.46692 | 22.728 | 122.6624 | 0.36163 | 122.5204 | 1.4923 | 0.65002 | 0.80109 | 0.009155 | -122.2046 | -122.2961 | 0.064087 | 0.041199 | -0.050354 | 0.032044 | -0.059509 | -0.064087 | -0.045776 | -0.18768 | 1.0666 | 0.37537 | 0.2243 | 0.43945 | 0.28839 | 0.054932 | -0.022888 | 1.1307 | 122.1588 | 0.068665 | 122.3007 | 0.07782 | 122.2366 | -122.2733 | -122.3465 | -0.013733 | 122.0947 | -0.050354 | 22.3022
4586.4375 | 122.4243 | -0.054932 | 122.1588 | -0.17372 | -0.042176 | -0.00018577 | 0.019305 | -0.00041873 | -0.010316 | -0.0047231 | 0.0052185 | 0.0061651 | 0.064491 | 0.04385 | -0.017515 | 0.027194 | -0.0053661 | -0.086975 | -0.032043 | -0.032043 | 0.018311 | 0.14191 | 0.009155 | 0.11444 | 22.7188 | 122.1359 | -0.09613 | 122.0901 | 1.1581 | 0.31128 | 0.40283 | 0.022889 | -122.1909 | -122.1405 | 0.19684 | 0.16937 | 0.064087 | 0.14648 | 0.041198 | -0.041198 | -0.022888 | -0.068664 | 1.2131 | 0.45776 | 0.36621 | 0.49896 | 0.40741 | 0.17395 | 0.050354 | 1.2543 | 122.1863 | 0 | 122.2321 | 0.022889 | 122.1909 | -122.1909 | -122.2549 | 0.073243 | 122.1451 | -0.032043 | 22.7737
4588.2031 | 122.4335 | 0.50812 | 122.8363 | -0.16609 | -0.042603 | 0.002164 | 0.019732 | -0.0021277 | -0.01117 | -0.0040823 | -0.019196 | 0.0068059 | 0.063209 | 0.044064 | -0.017729 | 0.025485 | -2.571e-05 | -0.10071 | -0.064087 | -0.054932 | 0.009155 | 0.14191 | 0.009155 | 0.09613 | 23.0576 | 122.168 | -0.064087 | 122.7539 | 1.8356 | 0.95673 | 1.0712 | -0.56305 | -122.9004 | -122.8271 | -0.36621 | -0.41199 | -0.49896 | 0.15106 | 0.064087 | -0.5722 | -0.66833 | -0.082398 | 1.3275 | 0.56305 | 0.44861 | 1.1353 | 1.0208 | 0.19684 | 0.064087 | 1.8997 | 122.818 | -0.009155 | 122.2321 | -0.5722 | 121.6599 | -122.8912 | -122.9004 | -0.49896 | 122.2458 | -0.60883 | 22.5494
4589.9844 | 122.2549 | 0.4303 | 122.7814 | -0.074539 | -0.045594 | -0.0038174 | 0.020587 | -0.0040503 | -0.013734 | -0.0023733 | -0.092438 | 0.0065923 | 0.064063 | 0.042142 | -0.019865 | 0.026553 | -0.00066651 | 0.32501 | 0.48523 | 0.39825 | 0.42114 | 0.49896 | 0.39368 | 0.48523 | 23.6618 | 122.7264 | 0.39368 | 122.5021 | 1.593 | 0.69122 | 0.82855 | -0.032044 | -122.2961 | -122.3602 | 0.068664 | 0.054931 | -0.036621 | 0.086975 | -0.004577 | -0.036621 | -0.054932 | -0.27924 | 1.1627 | 0.39825 | 0.26093 | 0.43487 | 0.29755 | 0.10071 | 0.022889 | 1.1993 | 122.1085 | 0.086975 | 122.3328 | 0.054931 | 122.2961 | -122.3831 | -122.3877 | -0.009155 | 122.0718 | -0.10529 | 23.2315
4591.75 | 122.4014 | -0.45319 | 121.8063 | -0.20424 | -0.041321 | 0.0023776 | 0.022296 | 0.00086307 | -0.0098886 | -0.0055777 | -0.071076 | 0.0063787 | 0.062568 | 0.0462 | -0.020078 | 0.02634 | -0.0023755 | -0.44861 | -0.41657 | -0.3891 | -0.35248 | -0.2243 | -0.41199 | -0.29297 | 23.3322 | 121.7148 | -0.46234 | 121.701 | 0.81482 | -0.13733 | 0.018311 | 0.064087 | -122.2229 | -122.1588 | 0.22888 | 0.16022 | 0.041199 | 0.09613 | -0.022888 | -0.009155 | -0.091552 | -0.10529 | 1.268 | 0.4715 | 0.31586 | 0.48065 | 0.32501 | 0.16479 | 0.036621 | 1.2772 | 122.1634 | -0.027466 | 122.1771 | 0.036621 | 122.168 | -122.1954 | -122.2687 | 0.10071 | 122.1542 | 0.004578 | 23.7854
4593.4531 | 122.287 | 0.46234 | 122.8088 | -0.12032 | -0.044312 | 0.00045503 | 0.022296 | 0.0021447 | -0.010102 | -0.0034415 | -0.068024 | 0.0078741 | 0.063636 | 0.052395 | -0.019438 | 0.026981 | -0.0045117 | 0.33875 | 0.49896 | 0.40283 | 0.49439 | 0.57678 | 0.46692 | 0.56763 | 24.3576 | 122.7722 | 0.46692 | 122.525 | 1.6846 | 0.71869 | 0.85602 | -0.059509 | -122.3099 | -122.3145 | 0.11444 | 0.10529 | 0.004578 | 0.16479 | 0.064087 | 0.004578 | -0.036621 | -0.28381 | 1.2222 | 0.39368 | 0.25635 | 0.3891 | 0.25177 | 0.17395 | 0.091553 | 1.2177 | 122.0581 | 0.09613 | 122.3053 | 0.036621 | 122.3099 | -122.406 | -122.3419 | 0.032044 | 122.0627 | -0.1236 | 23.8953
4595.2188 | 122.2549 | 0.63629 | 122.9645 | -0.089798 | -0.043885 | -0.0014676 | 0.021869 | -0.00020513 | -0.012452 | -0.0045095 | -0.064972 | 0.010438 | 0.063209 | 0.045559 | -0.019438 | 0.025912 | -0.0021619 | 0.79651 | 0.74616 | 0.6546 | 0.6958 | 0.80566 | 0.6958 | 0.77362 | 24.9527 | 122.9919 | 0.69122 | 122.7081 | 1.9135 | 0.91095 | 1.0574 | 0.01831 | -122.2183 | -122.2687 | 0.16937 | 0.13733 | 0.059509 | 0.11902 | 0.041199 | 0.054931 | 0.027465 | -0.25635 | 1.2772 | 0.42114 | 0.27466 | 0.36621 | 0.21973 | 0.15106 | 0.041199 | 1.2222 | 122.0169 | 0.091553 | 122.3007 | 0.10986 | 122.3557 | -122.3099 | -122.2733 | 0.059509 | 122.0718 | 0.16022 | 24.3164
4596.9219 | 122.3648 | -0.59967 | 121.7148 | -0.19661 | -0.041535 | 0.0013094 | 0.02016 | -0.0036231 | -0.010316 | -0.0042959 | -0.037506 | 0.0070197 | 0.062568 | 0.041714 | -0.01901 | 0.026553 | -0.0049389 | -0.75073 | -0.70038 | -0.6958 | -0.63171 | -0.52185 | -0.66376 | -0.59052 | 24.1974 | 121.5363 | -0.68665 | 121.4859 | 0.74158 | -0.25635 | -0.086975 | -0.096131 | -122.4152 | -122.3465 | 0.077819 | 0.009155 | -0.064087 | 0.10529 | 0.032044 | -0.086976 | -0.17853 | -0.22888 | 1.3412 | 0.5127 | 0.34332 | 0.59967 | 0.4303 | 0.17395 | 0.064087 | 1.4282 | 122.1725 | -0.004577 | 122.2229 | -0.10071 | 122.1359 | -122.4106 | -122.4014 | -0.032044 | 122.0856 | -0.15106 | 24.7971
4598.6875 | 122.3007 | -0.10529 | 122.1909 | -0.12794 | -0.039398 | 0.00024143 | 0.025073 | 0.0042811 | -0.013307 | -0.0057913 | -0.1077 | 0.0091559 | 0.064063 | 0.051114 | -0.016233 | 0.028903 | -0.0066479 | -0.14191 | 0.009155 | -0.086975 | -0.10986 | -0.036621 | -0.16937 | -0.054932 | 25.1404 | 122.1771 | -0.1236 | 121.9757 | 1.2131 | 0.15106 | 0.32044 | 0.018311 | -122.1817 | -122.3007 | 0.068665 | 0.050354 | -0.064087 | 0.032043 | -0.082398 | -0.01831 | -0.013733 | -0.21515 | 1.3184 | 0.42572 | 0.25635 | 0.44403 | 0.27466 | 0.050354 | -0.022888 | 1.3367 | 122.0993 | 0.09613 | 122.3007 | 0.11444 | 122.2824 | -122.2778 | -122.3145 | -0.004577 | 122.081 | -0.036621 | 25.2457
4600.3906 | 122.4243 | -0.64545 | 121.5958 | -0.18898 | -0.039185 | 0.0010958 | 0.021655 | 0.0015039 | -0.011598 | -0.0049367 | -0.071076 | 0.0097967 | 0.063209 | 0.035946 | -0.018156 | 0.029544 | -0.0040845 | -0.68665 | -0.6958 | -0.64087 | -0.56763 | -0.46234 | -0.64087 | -0.55389 | 25.1678 | 121.5454 | -0.65918 | 121.5271 | 0.79651 | -0.32501 | -0.16937 | 0.004578 | -122.2916 | -122.1634 | 0.18311 | 0.091553 | 0.004578 | 0.086975 | 0 | -0.013733 | -0.050354 | -0.068664 | 1.442 | 0.47607 | 0.32043 | 0.48981 | 0.33417 | 0.17853 | 0.073242 | 1.4557 | 122.1863 | -0.054932 | 122.2046 | -0.050354 | 122.1909 | -122.2366 | -122.2549 | 0.07782 | 122.1725 | -0.041199 | 25.8133
4602.1562 | 122.4335 | -0.35706 | 121.8475 | -0.18898 | -0.039185 | 0.003232 | 0.022937 | 0.0025721 | -0.010743 | -0.0042959 | -0.098541 | 0.0085149 | 0.063423 | 0.051541 | -0.019224 | 0.027194 | -0.0042981 | -0.36163 | -0.33417 | -0.31128 | -0.28381 | -0.18768 | -0.3479 | -0.24261 | 25.8499 | 121.8384 | -0.37994 | 121.7834 | 1.1215 | -0.004578 | 0.16022 | 0.045777 | -122.1817 | -122.1313 | 0.16937 | 0.11444 | 0.009156 | 0.068664 | -0.036621 | -0.022888 | -0.009155 | -0.064087 | 1.4786 | 0.51727 | 0.35248 | 0.54016 | 0.37537 | 0.1236 | 0.027466 | 1.5015 | 122.1634 | -0.022888 | 122.2183 | 0.022889 | 122.1954 | -122.1588 | -122.2275 | 0.073243 | 122.1405 | -0.004577 | 26.207
4603.8594 | 122.3785 | -0.054932 | 122.1817 | -0.17372 | -0.042603 | 0.001523 | 0.022082 | 0.0017175 | -0.013093 | -0.0030141 | -0.098541 | 0.0089423 | 0.062354 | 0.051114 | -0.020506 | 0.028049 | -0.0062207 | -0.12817 | 0.004578 | -0.064087 | -0.050354 | 0.059509 | -0.11444 | 0.022888 | 26.4587 | 122.1542 | -0.082397 | 122.0856 | 1.4603 | 0.29297 | 0.44861 | -0.009155 | -122.1771 | -122.2321 | 0.11444 | 0.07782 | -0.059509 | 0.086975 | -0.050354 | -0.027465 | -0.027466 | -0.096131 | 1.5152 | 0.50354 | 0.3479 | 0.531 | 0.37537 | 0.1236 | 0.013733 | 1.5427 | 122.168 | 0.068665 | 122.2366 | 0.05951 | 122.2092 | -122.2458 | -122.2641 | 0.004578 | 122.1405 | -0.073242 | 26.5137
4605.625 | 122.3145 | -0.091553 | 122.2229 | -0.13557 | -0.041535 | 0.0019504 | 0.022509 | -0.00020513 | -0.011384 | -0.0040823 | -0.13211 | 0.0085149 | 0.064491 | 0.051755 | -0.019224 | 0.028049 | -0.0072889 | -0.10071 | 0 | -0.045776 | -0.032043 | 0.059509 | -0.091553 | 0.013733 | 26.9348 | 122.1771 | -0.086975 | 122.0261 | 1.4603 | 0.23346 | 0.37994 | 0.045777 | -122.2229 | -122.2549 | 0.15106 | 0.10529 | 0 | 0.059509 | -0.045777 | 0.004578 | -0.045776 | -0.19684 | 1.5518 | 0.4715 | 0.32501 | 0.46692 | 0.32043 | 0.10528 | 0.013733 | 1.5472 | 122.113 | 0.045776 | 122.2641 | 0.091553 | 122.2687 | -122.2687 | -122.3099 | 0.05951 | 122.1176 | -0.009155 | 27.0264
4607.3281 | 122.319 | -0.10071 | 122.2458 | -0.15846 | -0.044953 | 0.00045503 | 0.023791 | -0.0027685 | -0.010957 | -0.0047231 | -0.068024 | 0.011079 | 0.063636 | 0.050259 | -0.018369 | 0.028903 | -0.0013073 | -0.14648 | 0.032043 | -0.050354 | -0.086975 | -0.004578 | -0.11902 | -0.004578 | 27.2919 | 122.2092 | -0.10529 | 122.0078 | 1.4603 | 0.21515 | 0.37537 | 0.050354 | -122.2137 | -122.3328 | 0.09613 | 0.09613 | -0.018311 | 0.045776 | -0.068665 | -0.004578 | -0.036622 | -0.23804 | 1.561 | 0.47607 | 0.31586 | 0.48065 | 0.32044 | 0.045776 | -0.036621 | 1.5656 | 122.113 | 0.082397 | 122.3145 | 0.13275 | 122.3099 | -122.2961 | -122.3511 | 0.013733 | 122.1085 | -0.045776 | 27.3926
4609.0938 | 122.3969 | -0.073242 | 122.2046 | -0.13557 | -0.042816 | 0.00088223 | 0.019519 | -0.0044775 | -0.011598 | -0.0045095 | 0.0021667 | 0.0050971 | 0.062995 | 0.046841 | -0.01901 | 0.026767 | -0.0019483 | -0.11444 | -0.027466 | -0.027466 | -0.027466 | 0.082397 | -0.032043 | 0.045776 | 27.8275 | 122.168 | -0.086975 | 122.0581 | 1.6067 | 0.34332 | 0.44861 | 0.045776 | -122.2321 | -122.2321 | 0.15564 | 0.11902 | 0.041199 | 0.073242 | -0.004577 | -0.013733 | -0.036621 | -0.14648 | 1.68 | 0.52185 | 0.41656 | 0.53558 | 0.4303 | 0.10986 | 0 | 1.6937 | 122.1451 | 0 | 122.2549 | 0.045776 | 122.2412 | -122.2321 | -122.2916 | 0.045776 | 122.1313 | -0.041199 | 27.9007
4610.7969 | 122.3099 | -0.09613 | 122.2366 | -0.097427 | -0.042603 | 0.002164 | 0.021014 | 0.0057763 | -0.014375 | -0.0042959 | -0.11075 | 0.0089423 | 0.062568 | 0.050046 | -0.019651 | 0.028262 | -0.0019483 | -0.11902 | 0 | -0.073242 | -0.086975 | -0.018311 | -0.09613 | -0.009155 | 28.212 | 122.2046 | -0.10986 | 122.0123 | 1.5839 | 0.23804 | 0.39825 | 0.022888 | -122.2366 | -122.3236 | 0.077819 | 0.086975 | 0 | 0.064087 | -0.022888 | -0.013733 | -0.032043 | -0.2243 | 1.68 | 0.49438 | 0.33417 | 0.50812 | 0.3479 | 0.054931 | -0.013733 | 1.6937 | 122.1222 | 0.073242 | 122.3145 | 0.09613 | 122.3007 | -122.3099 | -122.3465 | 0.009155 | 122.1085 | -0.022889 | 28.3081
4612.5625 | 122.287 | -0.10071 | 122.2046 | -0.16609 | -0.040253 | 0.0025912 | 0.024859 | 0.0010767 | -0.01117 | -0.0034415 | -0.13211 | 0.01236 | 0.064491 | 0.047482 | -0.019224 | 0.030612 | -0.0013073 | -0.1236 | 0.004578 | -0.050354 | -0.082397 | -0.032043 | -0.16479 | -0.059509 | 28.688 | 122.2229 | -0.11902 | 121.9711 | 1.5839 | 0.17853 | 0.37994 | 0.050354 | -122.2 | -122.287 | 0.068665 | 0.041199 | -0.064087 | -0.009155 | -0.11444 | -0.018311 | 0.01831 | -0.23346 | 1.6846 | 0.48065 | 0.27924 | 0.49896 | 0.29755 | 0.018311 | -0.032043 | 1.7029 | 122.0901 | 0.054932 | 122.3419 | 0.10529 | 122.3236 | -122.2549 | -122.3236 | 0.018311 | 122.0718 | -0.022888 | 28.7888
4614.3281 | 122.2824 | -0.10071 | 122.2046 | -0.13557 | -0.041321 | 0.0028048 | 0.022723 | 0.0017175 | -0.007966 | -0.0055777 | -0.1138 | 0.011933 | 0.06385 | 0.045132 | -0.017301 | 0.02869 | -0.0038709 | -0.086975 | 0 | -0.041199 | -0.059509 | 0.036621 | -0.09613 | -0.004578 | 29.1779 | 122.2046 | -0.10529 | 121.9986 | 1.6663 | 0.21973 | 0.40283 | 0.059509 | -122.2046 | -122.2641 | 0.13733 | 0.09613 | 0.004578 | 0.036621 | -0.054931 | -0.004578 | 0 | -0.20599 | 1.767 | 0.50354 | 0.32044 | 0.50812 | 0.32501 | 0.07782 | -0.01831 | 1.7715 | 122.1039 | 0.041199 | 122.3099 | 0.10071 | 122.3053 | -122.2458 | -122.3099 | 0.041199 | 122.0993 | 0.013733 | 29.2786
4616.0469 | 122.2687 | -0.10986 | 122.2137 | -0.15846 | -0.037262 | 0.0028048 | 0.022937 | 0.0019311 | -0.013093 | -0.0057913 | -0.10464 | 0.01236 | 0.065772 | 0.048123 | -0.015379 | 0.029758 | -0.0062207 | -0.14191 | 0.022888 | -0.064087 | -0.11444 | -0.059509 | -0.16022 | -0.041199 | 29.3564 | 122.2183 | -0.11902 | 121.9574 | 1.68 | 0.19684 | 0.39368 | 0.045776 | -122.1909 | -122.3282 | 0.050354 | 0.068664 | -0.050354 | 0.022888 | -0.09613 | -0.009156 | 0.004578 | -0.25635 | 1.7899 | 0.50354 | 0.3067 | 0.5127 | 0.31586 | 0.004578 | -0.050354 | 1.799 | 122.0764 | 0.086975 | 122.3373 | 0.13275 | 122.3282 | -122.2778 | -122.3328 | -0.004578 | 122.0673 | -0.032044 | 29.4662
4617.75 | 122.3419 | -0.082397 | 122.2183 | -0.12032 | -0.039826 | 0.00066863 | 0.022296 | -0.00084593 | -0.010743 | -0.0025869 | -0.10464 | 0.012788 | 0.063636 | 0.051114 | -0.016874 | 0.028903 | -0.0023755 | -0.091553 | 0 | -0.059509 | -0.041199 | 0.073242 | -0.064087 | 0.009155 | 29.8965 | 122.1954 | -0.086975 | 122.0306 | 1.8127 | 0.28381 | 0.46234 | 0.022888 | -122.2183 | -122.2595 | 0.15564 | 0.091552 | 0.01831 | 0.068664 | -0.004578 | -0.004578 | -0.022888 | -0.18768 | 1.8951 | 0.54474 | 0.36621 | 0.54932 | 0.37079 | 0.13275 | 0.01831 | 1.8997 | 122.1176 | 0.059509 | 122.2824 | 0.082397 | 122.2778 | -122.2778 | -122.3053 | 0.041198 | 122.113 | -0.009156 | 29.9789
4619.5 | 122.3099 | -0.086975 | 122.2137 | -0.1432 | -0.042176 | 0.00066863 | 0.022082 | 0.00043587 | -0.010102 | -0.0017325 | -0.089386 | 0.011506 | 0.065772 | 0.0509 | -0.018583 | 0.027835 | -0.0060071 | -0.09613 | 0.004578 | -0.059509 | -0.045776 | 0.068665 | -0.082397 | 0.009155 | 30.2765 | 122.1863 | -0.09613 | 122.0078 | 1.8448 | 0.26093 | 0.45319 | 0.027466 | -122.2092 | -122.2595 | 0.15564 | 0.09613 | 0.004578 | 0.068664 | -0.022888 | -0.009155 | -0.027466 | -0.20599 | 1.9318 | 0.54016 | 0.3479 | 0.54932 | 0.35706 | 0.12817 | 0.013733 | 1.9409 | 122.1039 | 0.064087 | 122.2824 | 0.091553 | 122.2733 | -122.2733 | -122.3099 | 0.041199 | 122.0947 | -0.009155 | 30.3635
4621.2656 | 122.3373 | -0.082397 | 122.2275 | -0.15083 | -0.041748 | 0.0025912 | 0.021655 | -0.0012731 | -0.012025 | -0.0042959 | -0.092438 | 0.010438 | 0.065772 | 0.047055 | -0.01666 | 0.028049 | -0.00045291 | -0.09613 | 0 | -0.073242 | -0.036621 | 0.068665 | -0.086975 | 0.013733 | 30.748 | 122.1863 | -0.082397 | 122.0215 | 1.9226 | 0.30212 | 0.48065 | 0.009155 | -122.2275 | -122.2641 | 0.15106 | 0.09613 | -0.004578 | 0.086975 | -0.013733 | 0 | -0.041199 | -0.20599 | 2.005 | 0.56305 | 0.38452 | 0.56305 | 0.38452 | 0.14191 | 0.036621 | 2.005 | 122.1039 | 0.073242 | 122.2687 | 0.082397 | 122.2687 | -122.3007 | -122.3099 | 0.045776 | 122.1039 | -0.013733 | 30.8304
4622.9688 | 122.3557 | -0.068665 | 122.2412 | -0.17372 | -0.044098 | 0.00066863 | 0.019519 | -0.0025549 | -0.013734 | -0.0051505 | 0.011322 | 0.0085149 | 0.063636 | 0.044705 | -0.016874 | 0.028903 | -0.0023755 | -0.059509 | -0.018311 | -0.009155 | 0.004578 | 0.13733 | 0.013733 | 0.082397 | 31.2424 | 122.1588 | -0.082397 | 122.0398 | 2.0142 | 0.37079 | 0.52185 | 0.05951 | -122.2595 | -122.2366 | 0.20599 | 0.15106 | 0.082398 | 0.091552 | 0.022888 | -0.013732 | -0.082398 | -0.20142 | 2.0828 | 0.59052 | 0.43945 | 0.60425 | 0.45319 | 0.14648 | 0.013733 | 2.0966 | 122.1222 | -0.009156 | 122.2412 | 0.050354 | 122.2275 | -122.2504 | -122.3236 | 0.073243 | 122.1085 | 0.009156 | 31.311
4624.7344 | 122.3007 | -0.1236 | 122.2183 | -0.11269 | -0.042176 | 0.002164 | 0.021869 | 0.00043587 | -0.0073252 | -0.0053641 | -0.077179 | 0.011933 | 0.065345 | 0.051541 | -0.019651 | 0.029971 | -0.0028027 | -0.13733 | 0.009155 | -0.059509 | -0.11444 | -0.027466 | -0.16022 | -0.041199 | 31.4941 | 122.1954 | -0.11444 | 121.962 | 1.973 | 0.24719 | 0.45319 | 0.064087 | -122.2092 | -122.3328 | 0.09613 | 0.082397 | -0.036621 | 0.01831 | -0.10071 | 0.009155 | -0.022888 | -0.25635 | 2.0966 | 0.57678 | 0.37079 | 0.56763 | 0.36163 | 0.032043 | -0.054932 | 2.0874 | 122.0764 | 0.068664 | 122.3099 | 0.13275 | 122.319 | -122.2778 | -122.3328 | 0.009155 | 122.0856 | -0.013733 | 31.6177
4626.4375 | 122.3923 | -0.059509 | 122.1588 | -0.18898 | -0.040467 | 0.0019504 | 0.021014 | -0.0031957 | -0.011811 | -0.0032277 | -0.049713 | 0.0093695 | 0.065986 | 0.045346 | -0.01901 | 0.029544 | -0.0047253 | -0.064087 | -0.050354 | -0.022888 | 0.022888 | 0.13275 | -0.027466 | 0.068665 | 32.0526 | 122.1222 | -0.068665 | 122.0901 | 2.1606 | 0.3891 | 0.56305 | 0.036621 | -122.2092 | -122.1359 | 0.19226 | 0.12817 | 0.032043 | 0.091553 | -0.004578 | -0.009156 | -0.036621 | -0.068664 | 2.2202 | 0.62256 | 0.44861 | 0.63171 | 0.45776 | 0.15564 | 0.045776 | 2.2293 | 122.1588 | -0.027466 | 122.1909 | 0.009155 | 122.1817 | -122.1817 | -122.2275 | 0.082397 | 122.1497 | -0.004578 | 32.1121
4628.2031 | 122.3785 | -0.064087 | 122.1817 | -0.20424 | -0.042389 | 0.0010958 | 0.021441 | 8.47e-06 | -0.010957 | -0.0034415 | -0.022247 | 0.010224 | 0.064491 | 0.044064 | -0.018583 | 0.028903 | -0.00066651 | -0.11902 | -0.027466 | -0.054932 | -0.050354 | 0.068665 | -0.064087 | 0.045776 | 32.3593 | 122.1542 | -0.091553 | 122.0398 | 2.1744 | 0.3891 | 0.55847 | 0.009155 | -122.2092 | -122.2321 | 0.13275 | 0.10986 | 0 | 0.10071 | -0.009155 | -0.027466 | -0.027466 | -0.14191 | 2.2385 | 0.62256 | 0.45319 | 0.65002 | 0.48065 | 0.1236 | 0.004578 | 2.2659 | 122.1313 | 0.027466 | 122.2458 | 0.036621 | 122.2183 | -122.2366 | -122.2733 | 0.013733 | 122.1039 | -0.054932 | 32.4234
4629.9219 | 122.3969 | -0.041199 | 122.1909 | -0.1432 | -0.043671 | -0.00018577 | 0.02016 | -0.0040503 | -0.011384 | -0.0042959 | -0.0039367 | 0.011292 | 0.065132 | 0.044491 | -0.019651 | 0.028903 | -0.0023755 | -0.1236 | -0.027466 | -0.050354 | -0.032043 | 0.064087 | -0.059509 | 0.054932 | 32.7713 | 122.1634 | -0.09613 | 122.0535 | 2.2522 | 0.41199 | 0.55389 | -0.009155 | -122.2183 | -122.2229 | 0.10529 | 0.096131 | -0.01831 | 0.10529 | -0.009155 | -0.054931 | -0.027466 | -0.13733 | 2.2934 | 0.59509 | 0.45319 | 0.65002 | 0.50812 | 0.11444 | 0.018311 | 2.3483 | 122.1497 | 0.022888 | 122.2595 | 0.013733 | 122.2046 | -122.2412 | -122.287 | 0.009156 | 122.0947 | -0.082397 | 32.8125
4631.6875 | 122.3419 | -0.082397 | 122.2046 | -0.17372 | -0.041962 | 0.003232 | 0.021869 | 0.0051355 | -0.009675 | -0.0045095 | -0.11685 | 0.011933 | 0.063209 | 0.053891 | -0.021147 | 0.028903 | -0.0060071 | -0.14648 | -0.018311 | -0.068665 | -0.068665 | 0.009155 | -0.13733 | -0.013733 | 33.1009 | 122.1634 | -0.10986 | 122.0215 | 2.2522 | 0.34332 | 0.54474 | 0.013732 | -122.2229 | -122.2733 | 0.091552 | 0.068664 | -0.054932 | 0.054932 | -0.068664 | -0.027466 | -0.041199 | -0.18311 | 2.3346 | 0.62714 | 0.42572 | 0.6546 | 0.45319 | 0.07782 | 0 | 2.3621 | 122.1313 | 0.050354 | 122.2733 | 0.064086 | 122.2458 | -122.2733 | -122.3145 | 0.013732 | 122.1039 | -0.064087 | 33.1833
4633.4375 | 122.3602 | -0.091553 | 122.2137 | -0.13557 | -0.04068 | 0.0025912 | 0.023791 | 0.00022207 | -0.012239 | -0.0036551 | -0.092438 | 0.013215 | 0.065345 | 0.050259 | -0.018156 | 0.026767 | -0.0017347 | -0.14191 | -0.013733 | -0.068665 | -0.09613 | 0 | -0.15106 | -0.009155 | 33.4625 | 122.1588 | -0.1236 | 122.0169 | 2.2888 | 0.33417 | 0.52643 | 0.022888 | -122.2275 | -122.3099 | 0.091553 | 0.082398 | -0.059509 | 0.05951 | -0.082397 | -0.032043 | -0.054932 | -0.19684 | 2.3804 | 0.61798 | 0.42572 | 0.65002 | 0.45776 | 0.068665 | -0.027465 | 2.4124 | 122.1405 | 0.054932 | 122.2824 | 0.07782 | 122.2504 | -122.2824 | -122.3373 | -0.004577 | 122.1085 | -0.050354 | 33.5541
4635.2031 | 122.319 | -0.15564 | 122.1405 | -0.17372 | -0.041321 | 0.0019504 | 0.022082 | 0.0012903 | -0.010102 | -0.0049367 | -0.10464 | 0.014069 | 0.067054 | 0.045773 | -0.018369 | 0.029544 | -0.0047253 | -0.15564 | -0.013733 | -0.09613 | -0.15564 | -0.07782 | -0.20599 | -0.091553 | 33.7051 | 122.1542 | -0.15106 | 121.9162 | 2.2522 | 0.24261 | 0.42572 | 0.05951 | -122.1542 | -122.2961 | 0.07782 | 0.064087 | -0.050354 | 0.004577 | -0.10986 | 0.004578 | 0.013733 | -0.2243 | 2.4078 | 0.58136 | 0.39826 | 0.57678 | 0.39368 | 0.01831 | -0.05951 | 2.4033 | 122.0673 | 0.082397 | 122.3053 | 0.14191 | 122.3099 | -122.2366 | -122.2916 | 0 | 122.0718 | 0 | 33.8608
4636.9062 | 122.374 | -0.52643 | 121.7468 | -0.17372 | -0.042176 | -0.00018577 | 0.019519 | -0.0010595 | -0.011811 | -0.0045095 | -0.019196 | 0.010865 | 0.06385 | 0.043637 | -0.017729 | 0.028049 | -0.0047253 | -0.60425 | -0.53558 | -0.54016 | -0.53558 | -0.41657 | -0.54932 | -0.44403 | 33.8242 | 121.6553 | -0.58594 | 121.5683 | 2.0004 | -0.013733 | 0.15564 | -0.013733 | -122.2824 | -122.2824 | 0.10986 | 0.082397 | -0.022888 | 0.09613 | -0.009155 | -0.059509 | -0.091553 | -0.17853 | 2.5269 | 0.68207 | 0.5127 | 0.74158 | 0.5722 | 0.1236 | 0.004578 | 2.5864 | 122.1542 | 0.004578 | 122.2412 | -0.009155 | 122.1817 | -122.287 | -122.3328 | -0.009155 | 122.0947 | -0.07782 | 34.3506
4638.6719 | 122.2412 | -0.29755 | 121.9894 | -0.12032 | -0.039612 | 0.00088223 | 0.022723 | 0.0015039 | -0.010316 | -0.0042959 | -0.11685 | 0.011079 | 0.066627 | 0.045132 | -0.020078 | 0.02869 | -0.0030163 | -0.17853 | -0.018311 | -0.10986 | -0.20599 | -0.16022 | -0.27924 | -0.16479 | 34.4238 | 122.0901 | -0.21973 | 121.7651 | 2.2064 | 0.11902 | 0.32044 | 0.18768 | -122.0078 | -122.1954 | 0.13733 | 0.13275 | 0.01831 | -0.054932 | -0.16937 | 0.077819 | 0.10071 | -0.2243 | 2.504 | 0.61798 | 0.41656 | 0.54016 | 0.33875 | -0.050354 | -0.096131 | 2.4261 | 121.9849 | 0.091552 | 122.3099 | 0.27923 | 122.3877 | -122.0993 | -122.2092 | 0.091552 | 122.0627 | 0.11902 | 34.7214
4640.375 | 122.3923 | -0.78735 | 121.4813 | -0.17372 | -0.041107 | -0.00018577 | 0.019305 | 8.47e-06 | -0.012879 | -0.0057913 | -0.034454 | 0.010651 | 0.067268 | 0.0462 | -0.01901 | 0.027194 | -0.00045291 | -0.81482 | -0.76446 | -0.75989 | -0.73242 | -0.59052 | -0.76446 | -0.64545 | 34.3781 | 121.4172 | -0.79651 | 121.2936 | 1.8265 | -0.2655 | -0.091553 | 0.027466 | -122.2458 | -122.2137 | 0.19684 | 0.14191 | 0.022889 | 0.11444 | -0.004577 | -0.009155 | -0.064087 | -0.18768 | 2.6138 | 0.6958 | 0.52185 | 0.70496 | 0.53101 | 0.16937 | 0.027466 | 2.623 | 122.0901 | -0.004577 | 122.2137 | 0.022889 | 122.2046 | -122.2412 | -122.2778 | 0.054932 | 122.081 | -0.027465 | 35.1654
4642.1406 | 122.4152 | 0.16937 | 122.4564 | -0.15083 | -0.04303 | 2.7834e-05 | 0.02016 | 0.0023585 | -0.012025 | -0.0072867 | -0.01004 | 0.011079 | 0.065132 | 0.044705 | -0.018583 | 0.027194 | -0.0045117 | -0.33417 | -0.30212 | -0.31128 | -0.10071 | 0.054932 | -0.07782 | 0.064087 | 35.5179 | 122.168 | -0.1236 | 122.319 | 2.9709 | 0.7782 | 0.92468 | -0.48065 | -122.7585 | -122.5571 | -0.11444 | -0.10529 | -0.24719 | 0.37537 | 0.23346 | -0.29297 | -0.28839 | -0.13733 | 2.8015 | 0.75531 | 0.60882 | 1.0483 | 0.90179 | 0.36621 | 0.21057 | 3.0945 | 122.4426 | 0.009155 | 122.2916 | -0.4715 | 121.9986 | -122.7676 | -122.58 | -0.27008 | 122.1497 | -0.50354 | 35.3485
4643.8438 | 122.3007 | -0.84686 | 121.4447 | -0.13557 | -0.040894 | 0.0030184 | 0.025287 | -0.0014867 | -0.011384 | -0.0034415 | -0.098541 | 0.012574 | 0.068122 | 0.054104 | -0.019651 | 0.029758 | -0.0010937 | -0.9201 | -0.75989 | -0.83771 | -0.87891 | -0.79651 | -0.92926 | -0.80109 | 34.8541 | 121.4081 | -0.87433 | 121.2067 | 1.8539 | -0.41199 | -0.2243 | 0.009155 | -122.2046 | -122.3236 | 0.050354 | 0.045777 | -0.082397 | 0.036622 | -0.091552 | -0.027466 | -0.036621 | -0.23804 | 2.7008 | 0.62256 | 0.43488 | 0.65003 | 0.46234 | 0.041199 | -0.041198 | 2.7283 | 122.081 | 0.07782 | 122.2824 | 0.086975 | 122.2549 | -122.2824 | -122.319 | -0.032043 | 122.0535 | -0.073242 | 35.701
4645.6094 | 122.2641 | -0.52643 | 121.7056 | -0.1432 | -0.042603 | 0.0017368 | 0.022082 | 0.0021447 | -0.010316 | -0.0053641 | -0.12296 | 0.014497 | 0.064704 | 0.053677 | -0.017088 | 0.031894 | -0.0040845 | -0.32044 | -0.13275 | -0.21973 | -0.3479 | -0.28381 | -0.42114 | -0.29297 | 35.5682 | 121.8842 | -0.39825 | 121.5637 | 2.211 | -0.11444 | 0.041199 | 0.3067 | -121.8384 | -122.0535 | 0.24262 | 0.23346 | 0.10529 | -0.073242 | -0.20142 | 0.12817 | 0.17853 | -0.14191 | 2.7374 | 0.56763 | 0.41199 | 0.43945 | 0.28381 | -0.064086 | -0.12817 | 2.6093 | 121.962 | 0.086976 | 122.2824 | 0.39368 | 122.4106 | -121.9254 | -122.1039 | 0.17853 | 122.0901 | 0.20599 | 36.0947
4647.375 | 122.3694 | -0.6958 | 121.5454 | -0.18898 | -0.040894 | 0.0028048 | 0.021869 | -0.00041873 | -0.010743 | -0.0062185 | -0.034454 | 0.01236 | 0.064918 | 0.052182 | -0.016874 | 0.027621 | -0.0032299 | -0.82855 | -0.78278 | -0.7782 | -0.71869 | -0.58594 | -0.76904 | -0.63171 | 35.701 | 121.4767 | -0.75989 | 121.3898 | 2.1744 | -0.16022 | -0.013733 | -0.082397 | -122.3282 | -122.2641 | 0.10986 | 0.064087 | -0.073242 | 0.14648 | 0.009155 | -0.064087 | -0.068664 | -0.15564 | 2.8702 | 0.68207 | 0.53558 | 0.74616 | 0.59967 | 0.19226 | 0.059509 | 2.9343 | 122.1497 | -0.004578 | 122.2366 | -0.086975 | 122.1725 | -122.3236 | -122.3053 | -0.022888 | 122.0856 | -0.13275 | 36.3968
4649.125 | 122.2641 | -0.082397 | 122.2366 | -0.12794 | -0.041748 | -0.00018577 | 0.019519 | -0.00020513 | -0.011811 | -0.0060049 | -0.04361 | 0.011292 | 0.067695 | 0.052395 | -0.017942 | 0.027408 | -0.00088011 | -0.10986 | 0.027466 | -0.059509 | -0.064087 | 0.036621 | -0.091553 | 0.018311 | 36.6119 | 122.1909 | -0.09613 | 121.9894 | 2.8336 | 0.40741 | 0.52643 | 0.022888 | -122.2092 | -122.3007 | 0.11902 | 0.10071 | -0.009156 | 0.07782 | -0.032044 | -0.013733 | -0.045776 | -0.24719 | 2.916 | 0.60882 | 0.48981 | 0.62256 | 0.50354 | 0.09613 | -0.004578 | 2.9297 | 122.0856 | 0.086975 | 122.287 | 0.10986 | 122.2733 | -122.2961 | -122.3328 | 0.01831 | 122.0718 | -0.027466 | 36.6943
4650.8438 | 122.319 | 0.3479 | 122.6303 | -0.13557 | -0.041107 | 0.00066863 | 0.021014 | -0.00063233 | -0.012239 | -0.0075003 | -0.09549 | 0.012788 | 0.065772 | 0.048764 | -0.01901 | 0.028049 | -0.0025891 | 0.3891 | 0.54474 | 0.45319 | 0.43488 | 0.50354 | 0.37079 | 0.48523 | 37.294 | 122.699 | 0.37079 | 122.4426 | 3.3371 | 0.85144 | 0.99792 | 0.10529 | -122.0856 | -122.1954 | 0.15564 | 0.13733 | 0.022889 | 0.032043 | -0.082397 | 0.022889 | 0.068665 | -0.18768 | 2.9892 | 0.65002 | 0.50354 | 0.62714 | 0.48065 | 0.050354 | -0.018311 | 2.9663 | 122.0718 | 0.091553 | 122.3282 | 0.19684 | 122.3511 | -122.1771 | -122.2595 | 0.086975 | 122.0947 | 0.041199 | 36.9461
4652.6094 | 122.406 | -0.49896 | 121.6873 | -0.22713 | -0.03833 | 0.001523 | 0.021655 | 0.0010767 | -0.012879 | -0.0036551 | -0.040558 | 0.013215 | 0.062782 | 0.04321 | -0.018583 | 0.02933 | -0.0028027 | -0.53101 | -0.53101 | -0.49896 | -0.45319 | -0.35248 | -0.53558 | -0.41657 | 36.8271 | 121.6553 | -0.55847 | 121.6049 | 2.5772 | 0.059509 | 0.1831 | 0 | -122.2183 | -122.1405 | 0.14648 | 0.082397 | -0.036621 | 0.082397 | -0.036621 | -0.05951 | -0.032044 | -0.082398 | 3.0762 | 0.68207 | 0.55847 | 0.74158 | 0.61798 | 0.14648 | 0.045776 | 3.1357 | 122.1634 | -0.032044 | 122.2137 | -0.032044 | 122.1542 | -122.1863 | -122.2458 | 0.045776 | 122.1039 | -0.032044 | 37.326
4654.3594 | 122.4152 | -0.064087 | 122.1359 | -0.16609 | -0.042816 | -0.00018577 | 0.019305 | -0.0027685 | -0.010957 | -0.0047231 | -0.0039367 | 0.011933 | 0.064063 | 0.03851 | -0.020506 | 0.027194 | -0.0085705 | -0.32044 | -0.27924 | -0.29755 | -0.16937 | -0.032043 | -0.15106 | -0.041199 | 37.4634 | 121.9986 | -0.21057 | 122.049 | 3.1174 | 0.56305 | 0.66376 | -0.23346 | -122.4152 | -122.3053 | 0.032044 | 0.022888 | -0.086975 | 0.25635 | 0.14648 | -0.14648 | -0.13733 | -0.086975 | 3.1815 | 0.72784 | 0.62714 | 0.87433 | 0.77362 | 0.2655 | 0.12817 | 3.3279 | 122.2595 | 0.01831 | 122.2092 | -0.21515 | 122.0627 | -122.4335 | -122.3465 | -0.10529 | 122.113 | -0.25635 | 37.5275
4656.0625 | 122.3145 | 0.091553 | 122.3648 | -0.18898 | -0.044098 | -0.00061317 | 0.019519 | -0.0027685 | -0.011811 | -0.0028005 | -0.058869 | 0.013428 | 0.067481 | 0.056881 | -0.018583 | 0.030826 | -0.0062207 | 0.054932 | 0.082397 | 0.073242 | 0.14191 | 0.25177 | 0.13275 | 0.20142 | 37.8708 | 122.3465 | 0.068665 | 122.2275 | 3.2822 | 0.64545 | 0.75073 | -0.018311 | -122.2824 | -122.2229 | 0.16022 | 0.10986 | 0.041198 | 0.12817 | 0.059509 | -0.022888 | -0.01831 | -0.13733 | 3.1906 | 0.65918 | 0.55389 | 0.68207 | 0.57678 | 0.17853 | 0.068665 | 3.2135 | 122.1588 | 0.009155 | 122.2778 | -0.009156 | 122.2549 | -122.2916 | -122.2961 | 0.050354 | 122.1359 | -0.036621 | 37.7792
4657.8281 | 122.3465 | 0.33417 | 122.5983 | -0.17372 | -0.041535 | 0.0017368 | 0.023791 | -0.00084593 | -0.010957 | -0.00023714 | -0.09549 | 0.012574 | 0.065345 | 0.047909 | -0.01901 | 0.028262 | -0.00088011 | 0.52643 | 0.65002 | 0.5722 | 0.5722 | 0.64087 | 0.49896 | 0.58136 | 38.3011 | 122.7173 | 0.44861 | 122.4106 | 3.5797 | 0.87891 | 0.99792 | 0.23804 | -121.9482 | -122.0261 | 0.3067 | 0.24719 | 0.1648 | 0.009155 | -0.073243 | 0.11444 | 0.11902 | -0.18768 | 3.2455 | 0.66376 | 0.54474 | 0.54932 | 0.4303 | 0.068664 | 0 | 3.1311 | 121.962 | 0.077819 | 122.2687 | 0.31586 | 122.3831 | -122.0261 | -122.1497 | 0.23804 | 122.0764 | 0.19226 | 37.9669
4659.5938 | 122.4152 | -0.25177 | 122.0398 | -0.13557 | -0.043457 | -0.001254 | 0.018878 | -0.00063233 | -0.010957 | -0.0053641 | -0.01004 | 0.011506 | 0.065986 | 0.042569 | -0.018583 | 0.028476 | 0.0018969 | -0.27466 | -0.2243 | -0.22888 | -0.16937 | -0.082397 | -0.20599 | -0.09613 | 37.8845 | 121.9849 | -0.24719 | 121.701 | 2.9755 | 0.41657 | 0.57678 | 0.022888 | -122.2641 | -122.2092 | 0.16937 | 0.15564 | 0.045776 | 0.13275 | 0.022888 | 0.004578 | -0.054932 | -0.33875 | 3.2272 | 0.82855 | 0.66834 | 0.82397 | 0.66376 | 0.14649 | 0.059509 | 3.2227 | 121.9482 | 0.004578 | 122.2321 | 0.027466 | 122.2366 | -122.2687 | -122.287 | 0.082397 | 121.9528 | -0.022888 | 38.1363
4661.2969 | 122.3511 | 0.018311 | 122.2733 | -0.17372 | -0.040467 | -0.0010404 | 0.019091 | 8.47e-06 | -0.012666 | -0.0045095 | -0.034454 | 0.011933 | 0.063209 | 0.041714 | -0.017729 | 0.029117 | -0.0017347 | 0.018311 | 0.086975 | 0.086975 | 0.10071 | 0.21057 | 0.07782 | 0.16022 | 38.324 | 122.2549 | 0.009155 | 122.1222 | 3.3966 | 0.62714 | 0.72327 | 0.068664 | -122.1863 | -122.1725 | 0.19226 | 0.14191 | 0.059509 | 0.073242 | -0.009155 | -0.009156 | -0.01831 | -0.15106 | 3.3783 | 0.70496 | 0.60883 | 0.71411 | 0.61798 | 0.1236 | 0.013733 | 3.3875 | 122.113 | 0 | 122.2458 | 0.068664 | 122.2366 | -122.1863 | -122.2641 | 0.082397 | 122.1039 | 0 | 38.3057
4663 | 122.4976 | 0.032043 | 122.2504 | -0.15083 | -0.044525 | 0.0017368 | 0.018878 | -0.0019141 | -0.012452 | -0.0051505 | -0.04361 | 0.012788 | 0.065986 | 0.046841 | -0.020292 | 0.028049 | -0.0017347 | -0.13275 | -0.12817 | -0.11444 | 0.041199 | 0.16479 | 0.032043 | 0.14191 | 38.4155 | 122.1863 | -0.036621 | 122.1725 | 3.511 | 0.6958 | 0.79193 | -0.14648 | -122.3785 | -122.2092 | 0.13275 | 0.10986 | 0 | 0.25635 | 0.14648 | -0.068664 | -0.064087 | -0.07782 | 3.479 | 0.75989 | 0.66376 | 0.82855 | 0.73242 | 0.27924 | 0.15564 | 3.5477 | 122.2092 | -0.013733 | 122.2229 | -0.16022 | 122.1542 | -122.3648 | -122.287 | 0.009156 | 122.1405 | -0.16479 | 38.3835
4664.7656 | 122.3282 | 0.63629 | 122.937 | -0.12032 | -0.043457 | 0.0010958 | 0.021228 | 0.0027857 | -0.012025 | -0.0075003 | -0.1138 | 0.015137 | 0.065132 | 0.059018 | -0.020292 | 0.030185 | -0.0025891 | 0.79651 | 0.82855 | 0.7782 | 0.76446 | 0.82398 | 0.6958 | 0.79651 | 39.1159 | 122.9782 | 0.66376 | 122.7448 | 4.1245 | 1.1948 | 1.3412 | 0.14191 | -122.1085 | -122.1725 | 0.18768 | 0.16022 | 0.059509 | 0.018311 | -0.082397 | 0.027465 | 0.041198 | -0.19226 | 3.4882 | 0.70496 | 0.55847 | 0.67749 | 0.53101 | 0.045777 | -0.013733 | 3.4607 | 122.081 | 0.050354 | 122.3145 | 0.19226 | 122.3419 | -122.1588 | -122.2733 | 0.12817 | 122.1085 | 0.16022 | 38.4796
4666.5469 | 122.2549 | -0.51727 | 121.7422 | -0.17372 | -0.040039 | 0.0019504 | 0.022723 | 0.00086307 | -0.01053 | -0.0083547 | -0.13821 | 0.015992 | 0.064704 | 0.054318 | -0.017942 | 0.03168 | -0.0047253 | 0.24261 | 0.44403 | 0.33875 | 0.050354 | 0.07782 | -0.10071 | -0.050354 | 38.2736 | 122.0901 | -0.16022 | 121.5271 | 2.948 | -0.022888 | 0.10529 | 0.85602 | -121.2982 | -121.6919 | 0.59509 | 0.46692 | 0.41656 | -0.3891 | -0.43945 | 0.35706 | 0.3479 | -0.21515 | 3.4653 | 0.62256 | 0.49438 | 0.2655 | 0.13733 | -0.26093 | -0.28839 | 3.1082 | 121.6873 | 0.10529 | 122.2504 | 0.9613 | 122.6074 | -121.4035 | -121.9025 | 0.56763 | 122.0444 | 0.75989 | 38.7909
4668.3125 | 122.3145 | 0.7782 | 123.1338 | -0.15083 | -0.042389 | 0.00024143 | 0.018664 | -0.0014867 | -0.016084 | -0.0036551 | -0.034454 | 0.013642 | 0.065345 | 0.04321 | -0.019438 | 0.02869 | -0.0013073 | 0.72784 | 0.90179 | 0.83313 | 0.81482 | 0.9613 | 0.79193 | 0.89722 | 39.4318 | 123.0881 | 0.76446 | 122.8363 | 4.3625 | 1.3824 | 1.4694 | 0.054932 | -122.2321 | -122.319 | 0.18311 | 0.11902 | 0.013733 | 0.064087 | -0.041199 | -0.013733 | -0.045776 | -0.29755 | 3.5843 | 0.69122 | 0.60425 | 0.70496 | 0.61798 | 0.12817 | -0.018311 | 3.598 | 122.0718 | 0.068664 | 122.3236 | 0.1236 | 122.3099 | -122.3007 | -122.3694 | 0.036621 | 122.0581 | -0.050354 | 38.6536
4670.0156 | 122.287 | -0.13733 | 122.1725 | -0.15846 | -0.042603 | 2.7834e-05 | 0.019305 | 0.00022207 | -0.008607 | -0.0028005 | -0.06192 | 0.014283 | 0.067054 | 0.044278 | -0.016874 | 0.02933 | 0.00061529 | -0.14648 | -0.054932 | -0.086975 | -0.091553 | 0.009155 | -0.11444 | -0.018311 | 38.6719 | 122.1451 | -0.14191 | 121.9254 | 3.5019 | 0.46692 | 0.55389 | 0.050354 | -122.2275 | -122.2641 | 0.14648 | 0.11902 | 0.022888 | 0.068664 | -0.027466 | -0.004578 | -0.027465 | -0.24719 | 3.6392 | 0.69122 | 0.60425 | 0.6958 | 0.60883 | 0.09613 | -0.004578 | 3.6438 | 122.0673 | 0.032043 | 122.287 | 0.082397 | 122.2824 | -122.2595 | -122.3145 | 0.045776 | 122.0627 | -0.009155 | 38.8092
4671.7812 | 122.3831 | -0.082397 | 122.1222 | -0.20424 | -0.039826 | 0.0023776 | 0.021655 | -0.0017005 | -0.011598 | -0.0051505 | -0.06192 | 0.011933 | 0.066627 | 0.047268 | -0.020506 | 0.02869 | -0.0045117 | -0.10071 | -0.059509 | -0.068665 | -0.018311 | 0.091553 | -0.054932 | 0.050354 | 38.8275 | 122.081 | -0.11902 | 122.0306 | 3.6438 | 0.56305 | 0.68665 | 0.013732 | -122.1817 | -122.1405 | 0.17395 | 0.13275 | 0.027465 | 0.11902 | 0.013733 | -0.036622 | -0.041198 | -0.091552 | 3.7262 | 0.76904 | 0.64545 | 0.80566 | 0.68207 | 0.16022 | 0.050354 | 3.7628 | 122.1497 | 0.009156 | 122.2 | 0.022888 | 122.1634 | -122.1909 | -122.2412 | 0.064086 | 122.113 | -0.018311 | 38.9099
4673.5469 | 122.2595 | -0.13275 | 122.1909 | -0.1432 | -0.042176 | -0.00082677 | 0.02016 | 0.0017175 | -0.01352 | -0.0040823 | -0.077179 | 0.015778 | 0.067481 | 0.050259 | -0.016874 | 0.02933 | -0.0038709 | -0.1831 | -0.018311 | -0.10071 | -0.14191 | -0.032043 | -0.13733 | -0.045776 | 38.6719 | 122.1817 | -0.16022 | 121.9116 | 3.5889 | 0.45776 | 0.55389 | 0.032043 | -122.2092 | -122.3328 | 0.10071 | 0.086975 | -0.004578 | 0.054932 | -0.036621 | -0.027466 | -0.009155 | -0.27924 | 3.7216 | 0.68664 | 0.59052 | 0.71411 | 0.61798 | 0.068665 | -0.041199 | 3.7491 | 122.0718 | 0.082397 | 122.3419 | 0.11444 | 122.3145 | -122.2916 | -122.3511 | -0.009156 | 122.0444 | -0.050354 | 38.8046
4675.25 | 122.4243 | -0.086975 | 122.113 | -0.18898 | -0.04303 | -0.00018577 | 0.018664 | -0.0046911 | -0.011598 | -0.0028005 | 0.0082703 | 0.014069 | 0.064277 | 0.040005 | -0.018156 | 0.029117 | 0.00040169 | -0.11444 | -0.050354 | -0.082397 | -0.018311 | 0.11444 | -0.027466 | 0.068665 | 38.9374 | 122.0947 | -0.1236 | 122.0444 | 3.7949 | 0.6134 | 0.6958 | 0.004578 | -122.1634 | -122.1313 | 0.20142 | 0.15564 | 0.059509 | 0.15106 | 0.054931 | -0.036621 | -0.01831 | -0.068664 | 3.8818 | 0.78278 | 0.70038 | 0.8194 | 0.737 | 0.19684 | 0.064086 | 3.9185 | 122.168 | 0.032043 | 122.2183 | 0.036621 | 122.1817 | -122.1954 | -122.2366 | 0.068664 | 122.1313 | -0.027466 | 39.0244
4676.9688 | 122.3373 | -0.091553 | 122.1497 | -0.15083 | -0.042176 | 0.00045503 | 0.022082 | 0.0019311 | -0.011384 | -0.0021597 | -0.031403 | 0.014497 | 0.066841 | 0.051755 | -0.019865 | 0.029758 | 0.0012561 | -0.12817 | -0.064087 | -0.059509 | -0.068665 | 0.041199 | -0.09613 | 0.004578 | 38.9191 | 122.1176 | -0.11902 | 121.9803 | 3.7765 | 0.55389 | 0.66376 | 0.032044 | -122.2137 | -122.2183 | 0.13275 | 0.096131 | -0.004577 | 0.064087 | -0.036621 | -0.027466 | -0.032043 | -0.16937 | 3.8681 | 0.75531 | 0.64545 | 0.78278 | 0.67291 | 0.10071 | -0.009156 | 3.8956 | 122.0993 | -0.004578 | 122.2366 | 0.027466 | 122.2092 | -122.2092 | -122.2687 | 0.022888 | 122.0718 | -0.036621 | 39.0106
4678.7344 | 122.3419 | -0.091553 | 122.1405 | -0.21187 | -0.04303 | 0.002164 | 0.019946 | -0.00041873 | -0.010102 | -0.0025869 | -0.031403 | 0.014069 | 0.067909 | 0.047055 | -0.018583 | 0.029117 | 0.00018809 | -0.14191 | -0.045776 | -0.07782 | -0.068665 | 0.032043 | -0.091553 | 0.022888 | 38.9374 | 122.0993 | -0.1236 | 121.9757 | 3.8132 | 0.55389 | 0.6546 | 0.013733 | -122.1863 | -122.2092 | 0.1236 | 0.11444 | 0 | 0.10071 | -0.013733 | -0.032043 | -0.041199 | -0.16479 | 3.9047 | 0.74616 | 0.64545 | 0.7782 | 0.67749 | 0.10986 | 0.009155 | 3.9368 | 122.0993 | 0.032044 | 122.2229 | 0.045777 | 122.1909 | -122.2183 | -122.2641 | 0.022888 | 122.0673 | -0.050354 | 39.0289
4680.5 | 122.3145 | -0.10529 | 122.1634 | -0.16609 | -0.042389 | 0.00045503 | 0.022723 | 0.0038537 | -0.011598 | -0.0053641 | -0.14127 | 0.016846 | 0.068122 | 0.054745 | -0.018797 | 0.029971 | 0.0014697 | -0.1236 | -0.027466 | -0.10071 | -0.068665 | 0.022888 | -0.1236 | -0.022888 | 39.0152 | 122.1588 | -0.14648 | 121.962 | 3.8773 | 0.52185 | 0.64545 | 0.004578 | -122.1909 | -122.2321 | 0.12817 | 0.082398 | -0.01831 | 0.07782 | -0.022888 | -0.041198 | -0.004578 | -0.20142 | 3.9825 | 0.75073 | 0.62714 | 0.79193 | 0.66833 | 0.1236 | 0.032043 | 4.0237 | 122.1085 | 0.073242 | 122.3053 | 0.07782 | 122.2641 | -122.2641 | -122.3099 | 0.036621 | 122.0673 | -0.01831 | 39.1205
4682.2812 | 122.3969 | -0.073242 | 122.1313 | -0.23476 | -0.041535 | 0.00045503 | 0.023364 | 0.0034265 | -0.010957 | -0.0030141 | -0.10464 | 0.01471 | 0.064491 | 0.050473 | -0.019865 | 0.030612 | 0.00040169 | -0.10986 | -0.059509 | -0.050354 | -0.013733 | 0.073242 | -0.068665 | 0.027466 | 39.1388 | 122.0947 | -0.11444 | 122.049 | 3.9917 | 0.60883 | 0.737 | 0.022888 | -122.1909 | -122.1451 | 0.14648 | 0.10071 | 0.004577 | 0.07782 | -0.018311 | -0.041199 | -0.036621 | -0.082398 | 4.0649 | 0.81024 | 0.68207 | 0.85144 | 0.72327 | 0.1236 | 0.036621 | 4.1061 | 122.1634 | -0.009155 | 122.2092 | 0.013733 | 122.168 | -122.1817 | -122.2458 | 0.059509 | 122.1222 | -0.036621 | 39.212
4684.0469 | 122.406 | -0.091553 | 122.1359 | -0.22713 | -0.042389 | 0.0028048 | 0.021014 | -0.00020513 | -0.011811 | -0.0034415 | -0.086334 | 0.015992 | 0.066841 | 0.056668 | -0.019438 | 0.028903 | -0.0015209 | -0.068665 | -0.054932 | -0.064087 | -0.004578 | 0.082397 | -0.064087 | 0.032043 | 39.1891 | 122.0856 | -0.10529 | 122.0306 | 4.0512 | 0.62256 | 0.737 | 0.027466 | -122.1909 | -122.1405 | 0.17395 | 0.1236 | 0.027466 | 0.09613 | 0 | -0.013733 | -0.050354 | -0.10528 | 4.1428 | 0.82855 | 0.71411 | 0.84229 | 0.72784 | 0.14648 | 0.059509 | 4.1565 | 122.1359 | 0.009155 | 122.1909 | 0.036621 | 122.1771 | -122.2 | -122.2412 | 0.086975 | 122.1222 | 0.022888 | 39.2807
4685.7656 | 122.3465 | -0.09613 | 122.1405 | -0.17372 | -0.042389 | 0.00066863 | 0.018451 | -0.0021277 | -0.012239 | -0.0053641 | -0.074127 | 0.016419 | 0.070472 | 0.048123 | -0.019651 | 0.030399 | -0.0013073 | -0.10986 | -0.054932 | -0.07782 | -0.036621 | 0.09613 | -0.086975 | 0.027466 | 39.2212 | 122.081 | -0.10529 | 121.994 | 4.0604 | 0.59967 | 0.6958 | 0.01831 | -122.1954 | -122.1771 | 0.19226 | 0.1236 | 0.009155 | 0.10529 | -0.009155 | -0.009156 | -0.059509 | -0.14648 | 4.1565 | 0.79193 | 0.6958 | 0.80109 | 0.70496 | 0.17395 | 0.041199 | 4.1657 | 122.0993 | 0.022888 | 122.1863 | 0.041198 | 122.1771 | -122.2183 | -122.2458 | 0.059509 | 122.0901 | -0.013733 | 39.3173
4687.5469 | 122.3465 | -0.11902 | 122.1359 | -0.17372 | -0.040894 | 0.0013094 | 0.022296 | 0.00086307 | -0.012879 | -0.0021597 | -0.049713 | 0.014069 | 0.065986 | 0.044064 | -0.019224 | 0.028049 | -0.0040845 | -0.15564 | -0.054932 | -0.054932 | -0.045776 | 0.036621 | -0.09613 | 0.013733 | 39.2258 | 122.0947 | -0.11444 | 121.9757 | 4.1107 | 0.58594 | 0.69122 | 0.064087 | -122.1909 | -122.1817 | 0.15564 | 0.13275 | 0.022889 | 0.068665 | -0.041198 | 0.004578 | -0.041198 | -0.16022 | 4.2297 | 0.81024 | 0.70496 | 0.80566 | 0.70038 | 0.091553 | 0.009156 | 4.2252 | 122.0901 | 0 | 122.2092 | 0.064087 | 122.2137 | -122.1909 | -122.2504 | 0.073243 | 122.0947 | -0.036621 | 39.3448
4689.3125 | 122.2504 | -0.1236 | 122.1451 | -0.15846 | -0.04068 | 0.0010958 | 0.022509 | 0.0032129 | -0.01352 | -0.0045095 | -0.14127 | 0.017274 | 0.065772 | 0.05795 | -0.018369 | 0.031894 | -0.0030163 | -0.13275 | -0.027466 | -0.09613 | -0.091553 | -0.009155 | -0.16479 | -0.064087 | 39.2212 | 122.1313 | -0.13733 | 121.9254 | 4.0741 | 0.48065 | 0.62714 | 0.027466 | -122.1725 | -122.2366 | 0.11444 | 0.059509 | -0.041199 | 0.032043 | -0.068665 | -0.013733 | -0.013733 | -0.21973 | 4.1977 | 0.75073 | 0.60425 | 0.76447 | 0.61798 | 0.086975 | 0.004577 | 4.2114 | 122.0627 | 0.068664 | 122.2687 | 0.09613 | 122.2549 | -122.2412 | -122.2824 | 0.032043 | 122.049 | -0.009155 | 39.3448
4691.0156 | 122.3099 | -0.12817 | 122.1588 | -0.13557 | -0.040253 | 0.00024143 | 0.023578 | -0.0036231 | -0.013307 | -0.0049367 | -0.12296 | 0.014283 | 0.065345 | 0.055813 | -0.020292 | 0.030612 | 0.00040169 | -0.12817 | -0.009155 | -0.086975 | -0.082397 | 0.022888 | -0.11902 | -0.032043 | 39.2853 | 122.1268 | -0.11444 | 121.9711 | 4.1977 | 0.56763 | 0.69122 | 0.041199 | -122.168 | -122.2412 | 0.15106 | 0.096131 | 0.009155 | 0.054932 | -0.032044 | 0.013733 | -0.032043 | -0.18768 | 4.3259 | 0.8194 | 0.6958 | 0.80566 | 0.68207 | 0.10986 | 0.004578 | 4.3121 | 122.0856 | 0.07782 | 122.2412 | 0.11902 | 122.2549 | -122.2458 | -122.2733 | 0.045777 | 122.0993 | 0 | 39.4135
4692.7812 | 122.3648 | -0.10986 | 122.1313 | -0.2195 | -0.043457 | 0.0013094 | 0.018237 | -0.00041873 | -0.012025 | -0.0036551 | -0.0069885 | 0.014283 | 0.066413 | 0.0462 | -0.018369 | 0.030612 | -0.00045291 | -0.14191 | -0.064087 | -0.068665 | -0.050354 | 0.045776 | -0.073242 | 0.018311 | 39.2624 | 122.0947 | -0.1236 | 121.9894 | 4.2892 | 0.68207 | 0.74616 | 0.041198 | -122.1954 | -122.1817 | 0.15564 | 0.12817 | 0.036621 | 0.086976 | -0.004577 | -0.013733 | -0.036621 | -0.14191 | 4.3991 | 0.85602 | 0.79193 | 0.86975 | 0.80566 | 0.11444 | 0.018311 | 4.4128 | 122.113 | 0.004578 | 122.2183 | 0.045776 | 122.2046 | -122.2 | -122.2549 | 0.059509 | 122.0993 | -0.032044 | 39.3723
4694.5469 | 122.2366 | -0.14191 | 122.1497 | -0.17372 | -0.039826 | 0.0019504 | 0.024218 | 0.0017175 | -0.009675 | -0.0030141 | -0.12601 | 0.016846 | 0.06385 | 0.04855 | -0.018369 | 0.031894 | -0.0038709 | -0.16022 | -0.022888 | -0.10529 | -0.14191 | -0.073242 | -0.21515 | -0.09613 | 39.1663 | 122.1497 | -0.17395 | 121.8933 | 4.1794 | 0.50354 | 0.63171 | 0.036621 | -122.1725 | -122.2916 | 0.068665 | 0.045777 | -0.073242 | 0.009156 | -0.10986 | -0.032043 | 0 | -0.25635 | 4.3213 | 0.77362 | 0.64545 | 0.80566 | 0.67749 | 0.032044 | -0.036621 | 4.3533 | 122.0673 | 0.082398 | 122.3236 | 0.11902 | 122.2916 | -122.2549 | -122.3236 | 0 | 122.0352 | -0.01831 | 39.3082
4696.3125 | 122.3007 | -0.1236 | 122.1451 | -0.12794 | -0.040467 | -0.00018577 | 0.021228 | -0.0021277 | -0.012666 | -0.0049367 | -0.11685 | 0.01471 | 0.065986 | 0.049618 | -0.017515 | 0.032108 | -0.0028027 | -0.15106 | -0.018311 | -0.082397 | -0.10071 | -0.004578 | -0.1236 | -0.022888 | 39.2715 | 122.1268 | -0.14191 | 121.9345 | 4.3076 | 0.5722 | 0.68207 | 0.041199 | -122.1634 | -122.2458 | 0.11902 | 0.10071 | 0 | 0.059509 | -0.041199 | -0.018311 | -0.018311 | -0.21057 | 4.4312 | 0.80566 | 0.6958 | 0.82398 | 0.71411 | 0.077819 | -0.018311 | 4.4495 | 122.0764 | 0.064086 | 122.2687 | 0.10528 | 122.2504 | -122.2275 | -122.287 | 0.022888 | 122.0581 | -0.027466 | 39.3951
4698.0781 | 122.2641 | -0.14191 | 122.1588 | -0.12794 | -0.044739 | -0.00039957 | 0.021869 | -0.0017005 | -0.013734 | -0.0015189 | -0.06192 | 0.016846 | 0.065986 | 0.051968 | -0.01901 | 0.030612 | -0.00088011 | -0.1831 | -0.018311 | -0.10071 | -0.13275 | -0.032043 | -0.13275 | -0.054932 | 39.2487 | 122.1497 | -0.15106 | 121.8933 | 4.303 | 0.53558 | 0.65002 | 0.041199 | -122.1771 | -122.2916 | 0.10986 | 0.086975 | 0.009156 | 0.045776 | -0.032043 | -0.009155 | -0.009155 | -0.2655 | 4.4449 | 0.79193 | 0.67749 | 0.80109 | 0.68665 | 0.068665 | -0.032043 | 4.454 | 122.0444 | 0.082397 | 122.3007 | 0.1236 | 122.2916 | -122.2595 | -122.3099 | 0.009156 | 122.0352 | -0.041198 | 39.3906
4699.7812 | 122.3465 | -0.10071 | 122.113 | -0.18135 | -0.04303 | 0.00024143 | 0.019732 | 0.0010767 | -0.01117 | -0.0028005 | -0.025299 | 0.016846 | 0.066627 | 0.04321 | -0.017088 | 0.029758 | -0.0019483 | -0.12817 | -0.045776 | -0.064087 | -0.004578 | 0.10071 | -0.036621 | 0.059509 | 39.537 | 122.0856 | -0.12817 | 121.9711 | 4.4632 | 0.69122 | 0.75531 | 0.036621 | -122.1588 | -122.1176 | 0.20142 | 0.16022 | 0.064087 | 0.1236 | 0.027466 | -0.027466 | -0.027466 | -0.14191 | 4.5639 | 0.85602 | 0.79193 | 0.88348 | 0.8194 | 0.1648 | 0.059509 | 4.5914 | 122.0993 | 0.018311 | 122.2137 | 0.054932 | 122.1863 | -122.1771 | -122.2412 | 0.09613 | 122.0718 | -0.027466 | 39.6378
4701.5469 | 122.374 | -0.091553 | 122.1085 | -0.20424 | -0.038971 | 0.0028048 | 0.022509 | -0.0019141 | -0.01053 | -0.0062185 | -0.10464 | 0.015992 | 0.066627 | 0.055173 | -0.020719 | 0.030612 | -0.0010937 | -0.1236 | -0.027466 | -0.068665 | -0.036621 | 0.059509 | -0.10986 | 0.018311 | 39.6011 | 122.1039 | -0.12817 | 122.0215 | 4.5181 | 0.69122 | 0.81482 | 0.022888 | -122.1359 | -122.1451 | 0.15106 | 0.10986 | -0.01831 | 0.086976 | -0.041198 | -0.036621 | -0.004577 | -0.086975 | 4.6097 | 0.90637 | 0.78278 | 0.94299 | 0.8194 | 0.12817 | 0.032044 | 4.6463 | 122.1497 | 0.041199 | 122.2321 | 0.064087 | 122.1954 | -122.1771 | -122.2366 | 0.054932 | 122.113 | -0.032043 | 39.6927
4703.3125 | 122.2458 | -0.14191 | 122.1817 | -0.19661 | -0.040894 | 0.00088223 | 0.02315 | 0.0027857 | -0.011384 | -0.0045095 | -0.12906 | 0.015351 | 0.065772 | 0.048764 | -0.018369 | 0.032748 | 0.00082889 | -0.15106 | -0.027466 | -0.11444 | -0.10986 | -0.027466 | -0.17395 | -0.068665 | 39.4867 | 122.1405 | -0.16937 | 121.9116 | 4.4357 | 0.55847 | 0.67749 | 0.027466 | -122.2092 | -122.2916 | 0.11444 | 0.073242 | -0.032043 | 0.045776 | -0.059509 | -0.027466 | -0.041199 | -0.27008 | 4.5776 | 0.8194 | 0.70038 | 0.84686 | 0.72784 | 0.086975 | 0.004578 | 4.6051 | 122.081 | 0.086975 | 122.3099 | 0.11444 | 122.2824 | -122.2961 | -122.3511 | 0.032044 | 122.0535 | -0.009155 | 39.6286
4705.0781 | 122.3053 | -0.11444 | 122.1451 | -0.16609 | -0.04068 | 0.002164 | 0.023364 | 0.0044947 | -0.01053 | -0.0053641 | -0.092438 | 0.015992 | 0.066627 | 0.048764 | -0.016233 | 0.032108 | -0.00045291 | -0.1236 | -0.018311 | -0.10071 | -0.09613 | 0.032043 | -0.10529 | -0.009155 | 39.5645 | 122.1222 | -0.13733 | 121.9437 | 4.541 | 0.61798 | 0.737 | 0.013733 | -122.1634 | -122.2412 | 0.14648 | 0.10529 | 0.009155 | 0.091553 | -0.004578 | -0.022888 | -0.022889 | -0.20142 | 4.6555 | 0.85144 | 0.73242 | 0.87433 | 0.75531 | 0.13275 | 0.004578 | 4.6783 | 122.081 | 0.082397 | 122.2595 | 0.09613 | 122.2366 | -122.2458 | -122.2824 | 0.018311 | 122.0581 | -0.009155 | 39.679
4706.7812 | 122.3511 | -0.086975 | 122.1268 | -0.2729 | -0.040894 | 0.0019504 | 0.019091 | 0.0036401 | -0.010316 | -0.0045095 | -0.0069885 | 0.016419 | 0.067909 | 0.040646 | -0.019224 | 0.031467 | -0.0028027 | -0.10986 | -0.091553 | -0.059509 | -0.013733 | 0.09613 | -0.07782 | 0.045776 | 39.6469 | 122.0764 | -0.11902 | 121.994 | 4.6417 | 0.71411 | 0.81482 | 0.027466 | -122.2183 | -122.1405 | 0.1831 | 0.13275 | 0.009155 | 0.10528 | -0.018311 | -0.032044 | -0.050354 | -0.13275 | 4.7287 | 0.90179 | 0.80109 | 0.93384 | 0.83313 | 0.15564 | 0.045776 | 4.7607 | 122.113 | -0.032044 | 122.1954 | -0.004578 | 122.1634 | -122.1863 | -122.2458 | 0.073242 | 122.081 | -0.022888 | 39.7339
4708.5469 | 122.3145 | -0.11444 | 122.113 | -0.15083 | -0.040039 | 0.00066863 | 0.021228 | 0.0019311 | -0.009675 | -0.0068593 | -0.1077 | 0.01941 | 0.067481 | 0.051114 | -0.017515 | 0.031039 | -0.00066651 | -0.16022 | -0.032043 | -0.10986 | -0.11444 | -0.032043 | -0.17395 | -0.064087 | 39.5096 | 122.1085 | -0.15106 | 121.9482 | 4.5914 | 0.62256 | 0.77362 | 0.004578 | -122.1451 | -122.2275 | 0.082398 | 0.050354 | -0.059509 | 0.045776 | -0.064087 | -0.036621 | -0.004578 | -0.1648 | 4.7058 | 0.88806 | 0.737 | 0.92468 | 0.77362 | 0.07782 | -0.004578 | 4.7424 | 122.0993 | 0.07782 | 122.2595 | 0.082398 | 122.2229 | -122.2229 | -122.2641 | 0 | 122.0627 | -0.045776 | 39.624
4710.25 | 122.287 | -0.13275 | 122.1497 | -0.16609 | -0.04068 | -0.00061317 | 0.02315 | -0.0014867 | -0.01117 | -0.0047231 | -0.086334 | 0.015778 | 0.06855 | 0.049405 | -0.019651 | 0.031894 | -0.0019483 | -0.15106 | -0.004578 | -0.10071 | -0.13275 | -0.036621 | -0.14191 | -0.036621 | 39.4226 | 122.113 | -0.14191 | 121.9116 | 4.6417 | 0.62256 | 0.74616 | 0.032043 | -122.1542 | -122.2824 | 0.09613 | 0.09613 | -0.009156 | 0.064087 | -0.041199 | -0.009156 | -0.036621 | -0.23804 | 4.7745 | 0.87891 | 0.75531 | 0.88806 | 0.76447 | 0.064087 | -0.032043 | 4.7836 | 122.0535 | 0.09613 | 122.2549 | 0.12817 | 122.2458 | -122.2504 | -122.2916 | 0 | 122.0444 | -0.018311 | 39.5554
4712.0312 | 122.3694 | -0.086975 | 122.1176 | -0.19661 | -0.039826 | 0.003232 | 0.019519 | -0.0019141 | -0.010743 | -0.0023733 | -0.040558 | 0.015778 | 0.067054 | 0.045346 | -0.017515 | 0.031039 | -2.571e-05 | -0.091553 | -0.059509 | -0.059509 | 0 | 0.10071 | -0.064087 | 0.054932 | 39.5874 | 122.0856 | -0.1236 | 122.0078 | 4.8065 | 0.74616 | 0.8606 | 0.027466 | -122.1771 | -122.1176 | 0.18768 | 0.14191 | 0.022888 | 0.11444 | -0.004578 | -0.036621 | -0.032044 | -0.10986 | 4.8935 | 0.94757 | 0.83313 | 0.98419 | 0.86975 | 0.16022 | 0.059509 | 4.9301 | 122.1313 | 0 | 122.2092 | 0.027466 | 122.1725 | -122.1771 | -122.2412 | 0.086975 | 122.0947 | -0.004578 | 39.6744
4713.7812 | 122.3785 | -0.11444 | 122.1039 | -0.21187 | -0.04303 | 0.00066863 | 0.018878 | -0.0017005 | -0.01352 | -0.0030141 | -0.0039367 | 0.018342 | 0.070259 | 0.047055 | -0.017942 | 0.030399 | 0.0027515 | -0.13275 | -0.045776 | -0.07782 | -0.022888 | 0.082397 | -0.027466 | 0.068665 | 39.5279 | 122.0673 | -0.1236 | 122.0032 | 4.8569 | 0.78278 | 0.86975 | 0.036621 | -122.1497 | -122.1268 | 0.19684 | 0.18311 | 0.086975 | 0.14649 | 0.050354 | -0.009155 | -0.036621 | -0.10071 | 4.9713 | 0.98419 | 0.89722 | 0.99335 | 0.90637 | 0.16022 | 0.054932 | 4.9805 | 122.1268 | 0.032044 | 122.1909 | 0.068665 | 122.1817 | -122.1817 | -122.2275 | 0.091553 | 122.1176 | -0.01831 | 39.6423
4715.5469 | 122.2549 | -0.13275 | 122.1359 | -0.15083 | -0.042389 | -0.00018577 | 0.02315 | 8.47e-06 | -0.011811 | -0.0047231 | -0.09549 | 0.019196 | 0.069404 | 0.052609 | -0.019438 | 0.031253 | -0.0023755 | -0.17853 | -0.027466 | -0.10071 | -0.14191 | -0.041199 | -0.14191 | -0.064087 | 39.386 | 122.1405 | -0.15106 | 121.8704 | 4.7424 | 0.61798 | 0.737 | 0.032043 | -122.1634 | -122.2778 | 0.091552 | 0.068664 | -0.009156 | 0.036621 | -0.041199 | -0.018311 | 0.004578 | -0.2655 | 4.8752 | 0.86975 | 0.75073 | 0.88806 | 0.76904 | 0.059509 | -0.041199 | 4.8935 | 122.0215 | 0.073242 | 122.2916 | 0.10529 | 122.2733 | -122.2366 | -122.287 | -0.009156 | 122.0032 | -0.045777 | 39.5187
4717.3438 | 122.3328 | -0.1236 | 122.1176 | -0.18135 | -0.042816 | 0.00066863 | 0.019946 | -0.00020513 | -0.012025 | -0.0036551 | -0.0008851 | 0.017487 | 0.067054 | 0.046414 | -0.017942 | 0.033817 | 0.0012561 | -0.14191 | -0.050354 | -0.064087 | -0.068665 | 0.041199 | -0.086975 | 0.013733 | 39.505 | 122.0581 | -0.14648 | 121.9437 | 4.8477 | 0.72784 | 0.84686 | 0.059509 | -122.168 | -122.1863 | 0.16479 | 0.13733 | 0.036621 | 0.07782 | -0.022888 | -0.022888 | -0.05951 | -0.17395 | 4.9713 | 0.97046 | 0.85144 | 0.99335 | 0.87433 | 0.10529 | -0.004578 | 4.9942 | 122.0901 | 0.013733 | 122.2046 | 0.073242 | 122.1817 | -122.1817 | -122.2641 | 0.054931 | 122.0673 | -0.018311 | 39.6286
4719.1094 | 122.2961 | -0.12817 | 122.113 | -0.15846 | -0.042816 | 0.0023776 | 0.023364 | -0.0012731 | -0.01352 | -0.0042959 | -0.1138 | 0.018128 | 0.066627 | 0.051541 | -0.020078 | 0.031894 | 0.00061529 | -0.12817 | -0.036621 | -0.091553 | -0.064087 | 0.022888 | -0.11444 | -0.013733 | 39.418 | 122.113 | -0.13733 | 121.9528 | 4.8798 | 0.6958 | 0.82398 | 0.036621 | -122.1497 | -122.1771 | 0.15106 | 0.11444 | 0.013733 | 0.07782 | -0.022888 | -0.009155 | 0 | -0.16022 | 5.0079 | 0.95215 | 0.82398 | 0.9613 | 0.83313 | 0.11444 | 0.027466 | 5.0171 | 122.0901 | 0.054932 | 122.2504 | 0.091553 | 122.2412 | -122.2046 | -122.2504 | 0.064087 | 122.081 | 0 | 39.5462
4720.8125 | 122.2366 | -0.14648 | 122.1451 | -0.12032 | -0.043244 | -0.0010404 | 0.021014 | -0.0027685 | -0.013093 | -0.0036551 | -0.052765 | 0.016419 | 0.071327 | 0.0462 | -0.016233 | 0.029544 | 0.0027515 | -0.16937 | -0.009155 | -0.10986 | -0.10986 | -0.032043 | -0.13275 | -0.045776 | 39.3402 | 122.1222 | -0.16937 | 121.8613 | 4.8614 | 0.66376 | 0.78278 | 0.036621 | -122.1542 | -122.2549 | 0.11444 | 0.10071 | 0.013733 | 0.064087 | -0.022888 | -0.022889 | -0.022889 | -0.28381 | 5.0079 | 0.92926 | 0.81024 | 0.95215 | 0.83313 | 0.07782 | 0 | 5.0308 | 122.0306 | 0.10071 | 122.2916 | 0.13733 | 122.2687 | -122.2549 | -122.3145 | 0.036621 | 122.0078 | -0.022889 | 39.4867
4722.6094 | 122.3648 | -0.10529 | 122.1176 | -0.13557 | -0.042176 | 2.7834e-05 | 0.019732 | -0.0019141 | -0.012666 | -0.0049367 | 0.0021667 | 0.018769 | 0.0662 | 0.042996 | -0.018156 | 0.029544 | 0.00061529 | -0.13733 | -0.054932 | -0.073242 | -0.050354 | 0.07782 | -0.045776 | 0.050354 | 39.3082 | 122.0718 | -0.12817 | 121.9986 | 5.0308 | 0.8194 | 0.93384 | 0.032044 | -122.1725 | -122.168 | 0.18311 | 0.15564 | 0.05951 | 0.1236 | 0.027466 | -0.022888 | -0.045777 | -0.11902 | 5.1361 | 1.0391 | 0.92468 | 1.062 | 0.94757 | 0.15106 | 0.022888 | 5.159 | 122.1268 | 0.01831 | 122.2 | 0.050354 | 122.1771 | -122.1909 | -122.2458 | 0.054932 | 122.1039 | -0.032043 | 39.4135
4724.3125 | 122.3785 | -0.10071 | 122.0901 | -0.10506 | -0.044098 | 0.0010958 | 0.018023 | -0.0051183 | -0.013093 | -0.0053641 | -0.016144 | 0.017274 | 0.06855 | 0.053036 | -0.019438 | 0.02933 | 0.0018969 | -0.12817 | -0.054932 | -0.073242 | -0.036621 | 0.086975 | -0.064087 | 0.050354 | 39.3173 | 122.0581 | -0.13275 | 121.9849 | 5.0766 | 0.8194 | 0.94757 | 0.027466 | -122.1451 | -122.1268 | 0.18768 | 0.15106 | 0.036621 | 0.1236 | 0.009155 | -0.032043 | -0.032044 | -0.10529 | 5.1773 | 1.0483 | 0.92011 | 1.0803 | 0.95215 | 0.16022 | 0.036621 | 5.2093 | 122.1176 | 0.01831 | 122.1909 | 0.045776 | 122.1588 | -122.1634 | -122.2229 | 0.064087 | 122.0856 | -0.027466 | 39.418
4726.0781 | 122.2916 | -0.12817 | 122.113 | -0.13557 | -0.040253 | 0.0023776 | 0.022509 | 0.0027857 | -0.010957 | -0.0057913 | -0.1199 | 0.017914 | 0.069404 | 0.045346 | -0.019865 | 0.03168 | -0.0028027 | -0.1236 | -0.013733 | -0.09613 | -0.07782 | 0.009155 | -0.11444 | -0.027466 | 39.2395 | 122.1039 | -0.14191 | 121.9254 | 5.0446 | 0.72784 | 0.87433 | 0.032044 | -122.1268 | -122.1909 | 0.13733 | 0.10071 | 0.013733 | 0.068664 | -0.018311 | -0.013733 | -0.009155 | -0.18768 | 5.1727 | 1.0025 | 0.85602 | 1.0162 | 0.86975 | 0.10528 | 0.01831 | 5.1865 | 122.0673 | 0.082397 | 122.2458 | 0.11444 | 122.2321 | -122.2092 | -122.2549 | 0.050354 | 122.0535 | 0.004578 | 39.3677
4727.8594 | 122.2412 | -0.15106 | 122.1542 | -0.15083 | -0.043671 | -0.00039957 | 0.02016 | -0.0012731 | -0.012239 | -0.0025869 | -0.077179 | 0.018342 | 0.068763 | 0.048764 | -0.017942 | 0.029758 | -0.0028027 | -0.18768 | -0.027466 | -0.10071 | -0.13733 | -0.045776 | -0.15564 | -0.045776 | 39.1663 | 122.1039 | -0.16022 | 121.8658 | 5.0354 | 0.70038 | 0.8606 | 0.050354 | -122.1817 | -122.2916 | 0.10529 | 0.10529 | -0.004578 | 0.054932 | -0.054932 | -0.009155 | -0.050354 | -0.28839 | 5.1865 | 1.0117 | 0.85144 | 1.0208 | 0.86059 | 0.054932 | -0.036621 | 5.1956 | 122.0261 | 0.073242 | 122.2641 | 0.1236 | 122.2549 | -122.2549 | -122.3145 | 0.013733 | 122.0169 | -0.036621 | 39.3173
4729.6406 | 122.3236 | -0.10071 | 122.049 | -0.1432 | -0.038544 | 0.00045503 | 0.019519 | 8.47e-06 | -0.012239 | -0.0032277 | -0.040558 | 0.016846 | 0.0662 | 0.052182 | -0.017729 | 0.031039 | -0.0017347 | -0.11902 | -0.064087 | -0.045776 | -0.013733 | 0.10071 | -0.07782 | 0.050354 | 39.299 | 122.0718 | -0.11444 | 121.9711 | 5.1773 | 0.80109 | 0.9613 | 0.054932 | -122.113 | -122.0627 | 0.20142 | 0.15106 | 0.022888 | 0.09613 | -0.032044 | -0.013733 | 0.022888 | -0.07782 | 5.278 | 1.062 | 0.90179 | 1.0757 | 0.91553 | 0.14648 | 0.032043 | 5.2917 | 122.0856 | -0.018311 | 122.1863 | 0.036621 | 122.1725 | -122.0947 | -122.1634 | 0.086975 | 122.0718 | -0.018311 | 39.3997
4731.4062 | 122.3053 | -0.1236 | 122.0856 | -0.21187 | -0.040894 | 0.0028048 | 0.023578 | 0.0038537 | -0.010957 | -0.0049367 | -0.12601 | 0.017701 | 0.067481 | 0.05325 | -0.018583 | 0.032108 | 0.00018809 | -0.16022 | -0.022888 | -0.09613 | -0.10071 | -0.036621 | -0.17853 | -0.054932 | 39.1525 | 122.0993 | -0.13733 | 121.9528 | 5.1773 | 0.77362 | 0.94299 | 0.027466 | -122.1085 | -122.1863 | 0.086975 | 0.068664 | -0.054932 | 0.041198 | -0.082398 | -0.013733 | 0.013733 | -0.13275 | 5.3009 | 1.0666 | 0.89722 | 1.0803 | 0.91095 | 0.059509 | -0.004578 | 5.3146 | 122.0901 | 0.073242 | 122.2366 | 0.10071 | 122.2229 | -122.1817 | -122.2229 | 0.022888 | 122.0764 | -0.036621 | 39.2761
4733.1094 | 122.3099 | -0.10071 | 122.113 | -0.18135 | -0.042816 | 0.00088223 | 0.019091 | 0.00043587 | -0.012879 | -0.00045074 | -0.040558 | 0.018128 | 0.067909 | 0.053464 | -0.018797 | 0.028049 | 0.0010425 | -0.15106 | -0.041199 | -0.073242 | -0.068665 | 0.027466 | -0.086975 | 0.004578 | 39.1205 | 122.0535 | -0.13733 | 121.9254 | 5.2505 | 0.80109 | 0.95215 | 0.027466 | -122.1542 | -122.1817 | 0.12817 | 0.10529 | 0.013733 | 0.07782 | -0.013733 | -0.036621 | -0.059509 | -0.18768 | 5.3513 | 1.0529 | 0.90179 | 1.0895 | 0.93841 | 0.10071 | 0.004577 | 5.3879 | 122.0627 | 0.032043 | 122.1909 | 0.059509 | 122.1542 | -122.1863 | -122.2504 | 0.032043 | 122.0261 | -0.050354 | 39.2212
4734.8125 | 122.3007 | -0.11444 | 122.0764 | -0.16609 | -0.041962 | -0.00082677 | 0.019305 | -0.0017005 | -0.012239 | -0.0045095 | -0.055817 | 0.018555 | 0.067695 | 0.045132 | -0.019651 | 0.029758 | 0.0021107 | -0.13733 | -0.050354 | -0.068665 | -0.045776 | 0.073242 | -0.091553 | 0.013733 | 39.0976 | 122.0718 | -0.13275 | 121.9528 | 5.2963 | 0.81482 | 0.97961 | 0.045776 | -122.1268 | -122.1222 | 0.18768 | 0.12817 | 0.022888 | 0.082398 | -0.022888 | -0.01831 | -0.004578 | -0.1236 | 5.4108 | 1.0941 | 0.92926 | 1.1124 | 0.94757 | 0.14191 | 0.022889 | 5.4291 | 122.0856 | 0.018311 | 122.2046 | 0.064087 | 122.1863 | -122.1451 | -122.2092 | 0.068665 | 122.0673 | -0.022888 | 39.212
4736.5625 | 122.2824 | -0.1236 | 122.113 | -0.097427 | -0.043671 | 0.00088223 | 0.020373 | 0.00064947 | -0.014588 | -0.0049367 | -0.055817 | 0.018983 | 0.068336 | 0.052182 | -0.018583 | 0.030612 | -0.00023931 | -0.10986 | -0.050354 | -0.054932 | -0.022888 | 0.073242 | -0.059509 | 0.041199 | 39.0656 | 122.0627 | -0.11444 | 121.9208 | 5.3375 | 0.81482 | 0.97504 | 0.068664 | -122.1634 | -122.1359 | 0.19684 | 0.16479 | 0.064087 | 0.096131 | -0.004577 | 0.009155 | -0.050354 | -0.19226 | 5.4611 | 1.0986 | 0.93841 | 1.0895 | 0.92926 | 0.12817 | 0.032044 | 5.452 | 122.0352 | 0.004578 | 122.1771 | 0.073242 | 122.1863 | -122.168 | -122.2275 | 0.10071 | 122.0444 | 0.013733 | 39.1891
4738.3281 | 122.3648 | -0.09613 | 122.0673 | -0.18898 | -0.042389 | 0.00088223 | 0.0208 | -0.0038367 | -0.010957 | -0.0030141 | -0.031403 | 0.017914 | 0.06855 | 0.051968 | -0.020078 | 0.030612 | 0.00040169 | -0.086975 | -0.054932 | -0.073242 | 0.009155 | 0.12817 | 0.009155 | 0.068665 | 39.061 | 122.0352 | -0.11902 | 121.9757 | 5.4657 | 0.91553 | 1.0529 | 0.022888 | -122.1222 | -122.0581 | 0.2243 | 0.16479 | 0.10528 | 0.14191 | 0.082397 | -0.022889 | -0.032044 | -0.091553 | 5.5618 | 1.149 | 1.0117 | 1.1719 | 1.0345 | 0.20142 | 0.082397 | 5.5847 | 122.0947 | 0.01831 | 122.1542 | 0.041198 | 122.1313 | -122.1405 | -122.1863 | 0.10528 | 122.0718 | 0.009155 | 39.1571
4740.0312 | 122.3648 | -0.10986 | 122.0856 | -0.1432 | -0.045594 | -0.0010404 | 0.021228 | -0.0027685 | -0.013093 | -0.0057913 | -0.016144 | 0.018128 | 0.067054 | 0.049191 | -0.020078 | 0.030826 | 0.0036059 | -0.10986 | -0.064087 | -0.073242 | 0.018311 | 0.11444 | -0.022888 | 0.059509 | 39.006 | 122.0581 | -0.12817 | 121.9849 | 5.5115 | 0.92926 | 1.062 | 0.036621 | -122.1497 | -122.0673 | 0.2243 | 0.16937 | 0.086975 | 0.13275 | 0.050354 | -0.018311 | -0.027466 | -0.10071 | 5.6213 | 1.1719 | 1.0391 | 1.1902 | 1.0574 | 0.18768 | 0.091553 | 5.6396 | 122.113 | 0.009155 | 122.1863 | 0.045776 | 122.168 | -122.1588 | -122.2137 | 0.12817 | 122.0947 | 0 | 39.1159
4741.7812 | 122.2641 | -0.14191 | 122.113 | -0.12794 | -0.042389 | 0.00088223 | 0.024005 | 0.0015039 | -0.013947 | -0.0038687 | -0.1077 | 0.020692 | 0.066627 | 0.057522 | -0.019651 | 0.030826 | 0.0033923 | -0.15106 | -0.032043 | -0.10986 | -0.11444 | -0.045776 | -0.14191 | -0.064087 | 38.8138 | 122.1039 | -0.15564 | 121.8887 | 5.4291 | 0.78278 | 0.97504 | 0.032044 | -122.1451 | -122.2275 | 0.096131 | 0.07782 | 0 | 0.045776 | -0.032044 | -0.013733 | -0.009155 | -0.2243 | 5.571 | 1.1169 | 0.92468 | 1.1307 | 0.93842 | 0.064087 | -0.004578 | 5.5847 | 122.0444 | 0.07782 | 122.2595 | 0.10986 | 122.2458 | -122.2229 | -122.2687 | 0.027466 | 122.0306 | -0.009155 | 38.9557
4743.4844 | 122.2549 | -0.13275 | 122.1313 | -0.17372 | -0.041535 | -0.0021084 | 0.022723 | 0.0010767 | -0.013307 | -0.0034415 | -0.092438 | 0.020051 | 0.067268 | 0.047909 | -0.017729 | 0.032962 | 0.00018809 | -0.14191 | -0.022888 | -0.086975 | -0.1236 | -0.041199 | -0.13733 | -0.041199 | 38.7497 | 122.1039 | -0.13275 | 121.8887 | 5.5023 | 0.81482 | 1.0025 | 0.045776 | -122.1542 | -122.2549 | 0.091552 | 0.091552 | -0.004578 | 0.045776 | -0.050354 | 0 | -0.027466 | -0.24262 | 5.6351 | 1.1353 | 0.94757 | 1.1353 | 0.94757 | 0.045776 | -0.036621 | 5.6351 | 122.0215 | 0.064087 | 122.2366 | 0.10986 | 122.2366 | -122.2183 | -122.2641 | 0.009155 | 122.0215 | -0.009156 | 38.8824
4745.25 | 122.2229 | -0.15106 | 122.081 | -0.16609 | -0.040253 | 2.7834e-05 | 0.021655 | 0.0027857 | -0.01053 | -0.0060049 | -0.12296 | 0.020692 | 0.071754 | 0.057522 | -0.017729 | 0.033389 | -0.00088011 | -0.16479 | -0.018311 | -0.10986 | -0.14191 | -0.068665 | -0.20142 | -0.068665 | 38.6581 | 122.081 | -0.16937 | 121.8658 | 5.4794 | 0.78735 | 0.95215 | 0.041199 | -122.0993 | -122.2229 | 0.082397 | 0.082397 | -0.050354 | 0.041198 | -0.091553 | -0.018311 | 0 | -0.21515 | 5.6305 | 1.1032 | 0.93842 | 1.1215 | 0.95673 | 0.041198 | -0.032044 | 5.6488 | 122.0352 | 0.091552 | 122.2504 | 0.13275 | 122.2321 | -122.1909 | -122.2504 | 0.009155 | 122.0169 | -0.013733 | 38.8092
4747.0156 | 122.319 | -0.09613 | 122.0535 | -0.26527 | -0.040467 | 0.0013094 | 0.019946 | 0.0015039 | -0.011598 | -0.0051505 | -0.040558 | 0.018983 | 0.067481 | 0.053036 | -0.017942 | 0.032535 | -0.00088011 | -0.10071 | -0.082397 | -0.054932 | -0.013733 | 0.10071 | -0.059509 | 0.045776 | 38.736 | 122.0306 | -0.1236 | 121.962 | 5.6534 | 0.95673 | 1.0757 | 0.041198 | -122.1359 | -122.0673 | 0.19684 | 0.14191 | 0.036621 | 0.10071 | -0.004577 | -0.027466 | -0.022888 | -0.091553 | 5.7495 | 1.1719 | 1.0529 | 1.1993 | 1.0803 | 0.15564 | 0.041199 | 5.777 | 122.0856 | -0.027465 | 122.1542 | 0.013733 | 122.1268 | -122.1085 | -122.1771 | 0.082397 | 122.0581 | -0.004578 | 38.8321
4748.7969 | 122.2595 | -0.14191 | 122.0993 | -0.16609 | -0.042603 | 0.002164 | 0.021441 | 0.0015039 | -0.012452 | -0.0032277 | -0.1138 | 0.020692 | 0.070259 | 0.051755 | -0.018156 | 0.033817 | 0.0012561 | -0.11902 | -0.036621 | -0.086975 | -0.064087 | 0.036621 | -0.10986 | -0.009155 | 38.5895 | 122.0856 | -0.13733 | 121.9162 | 5.6534 | 0.86517 | 1.03 | 0.054932 | -122.1359 | -122.1634 | 0.17853 | 0.13275 | 0.032044 | 0.07782 | -0.022888 | 0.004578 | -0.013733 | -0.1831 | 5.7953 | 1.1719 | 1.0071 | 1.1673 | 1.0025 | 0.1236 | 0.022888 | 5.7907 | 122.0535 | 0.050354 | 122.2229 | 0.10529 | 122.2275 | -122.1863 | -122.2366 | 0.07782 | 122.0581 | 0.022888 | 38.7314
4750.5 | 122.2275 | -0.15564 | 122.1359 | -0.15083 | -0.043457 | -0.0016812 | 0.019946 | 0.0029993 | -0.013307 | -0.0045095 | -0.092438 | 0.019837 | 0.06855 | 0.053036 | -0.018156 | 0.032321 | -2.571e-05 | -0.1831 | -0.004578 | -0.09613 | -0.14648 | -0.054932 | -0.14648 | -0.054932 | 38.4842 | 122.0993 | -0.16022 | 121.8292 | 5.658 | 0.82855 | 1.0025 | 0.05951 | -122.1405 | -122.2824 | 0.10071 | 0.10071 | 0.009156 | 0.041198 | -0.050354 | -0.004577 | -0.036621 | -0.3067 | 5.8136 | 1.1581 | 0.98419 | 1.1627 | 0.98877 | 0.041198 | -0.050354 | 5.8182 | 121.9894 | 0.091552 | 122.2595 | 0.15106 | 122.2549 | -122.2321 | -122.2961 | 0.009156 | 121.9849 | -0.027465 | 38.6398
4752.2656 | 122.2961 | -0.1236 | 122.0856 | -0.18898 | -0.042816 | 0.0013094 | 0.019946 | 0.0010767 | -0.011384 | -0.0055777 | -0.037506 | 0.018769 | 0.068977 | 0.047268 | -0.018583 | 0.031253 | 0.0012561 | -0.15106 | -0.059509 | -0.073242 | -0.073242 | 0.027466 | -0.091553 | -0.004578 | 38.3926 | 122.0261 | -0.1236 | 121.907 | 5.7678 | 0.92468 | 1.0666 | 0.050354 | -122.1451 | -122.1588 | 0.15106 | 0.11902 | 0.032043 | 0.068664 | -0.018311 | 0 | -0.059509 | -0.17853 | 5.8914 | 1.1902 | 1.0483 | 1.1902 | 1.0483 | 0.10071 | 0 | 5.8914 | 122.0306 | 0.013733 | 122.1497 | 0.064087 | 122.1497 | -122.1588 | -122.2092 | 0.050354 | 122.0306 | -0.027466 | 38.5162
4754.0312 | 122.2961 | -0.11902 | 122.0947 | -0.13557 | -0.041535 | 0.00045503 | 0.019946 | 0.00086307 | -0.012666 | -0.0030141 | -0.046661 | 0.020264 | 0.069618 | 0.048977 | -0.019224 | 0.03403 | 0.0021107 | -0.10071 | -0.064087 | -0.073242 | -0.013733 | 0.086975 | -0.041199 | 0.054932 | 38.3286 | 122.0398 | -0.13733 | 121.9208 | 5.8548 | 0.96588 | 1.1307 | 0.045777 | -122.1588 | -122.1085 | 0.20599 | 0.17395 | 0.07782 | 0.12817 | 0.032043 | -0.01831 | -0.054932 | -0.17395 | 5.9738 | 1.2497 | 1.0849 | 1.268 | 1.1032 | 0.16022 | 0.059509 | 5.9921 | 122.0581 | 0.009155 | 122.1771 | 0.054932 | 122.1588 | -122.168 | -122.2321 | 0.10529 | 122.0398 | 0.018311 | 38.4476
4755.7344 | 122.2916 | -0.10986 | 122.0535 | -0.2195 | -0.040467 | 0.0017368 | 0.0208 | -0.0014867 | -0.012239 | -0.0049367 | -0.080231 | 0.019837 | 0.070045 | 0.056454 | -0.019865 | 0.032321 | -0.00023931 | -0.13733 | -0.059509 | -0.064087 | -0.054932 | 0.064087 | -0.10529 | 0.018311 | 38.2416 | 122.0398 | -0.14191 | 121.9162 | 5.8685 | 0.95215 | 1.1124 | 0.045776 | -122.113 | -122.1085 | 0.17395 | 0.12817 | 0.004577 | 0.082398 | -0.041199 | -0.032044 | -0.013733 | -0.13733 | 5.9784 | 1.2222 | 1.062 | 1.2543 | 1.0941 | 0.12817 | 0.009155 | 6.0104 | 122.0581 | 0.004578 | 122.1817 | 0.050354 | 122.1497 | -122.1176 | -122.1954 | 0.054931 | 122.0261 | -0.027466 | 38.3514
4757.5 | 122.2137 | -0.14191 | 122.0856 | -0.11269 | -0.043457 | -0.00061317 | 0.0208 | -0.0021277 | -0.015016 | -0.0030141 | -0.074127 | 0.020051 | 0.067695 | 0.05325 | -0.018156 | 0.032321 | 0.0016833 | -0.14648 | -0.036621 | -0.082397 | -0.09613 | -0.004578 | -0.14191 | -0.018311 | 38.0447 | 122.0764 | -0.15106 | 121.8384 | 5.8548 | 0.90637 | 1.0208 | 0.05951 | -122.1222 | -122.1817 | 0.13733 | 0.1236 | 0 | 0.064086 | -0.05951 | -0.009155 | -0.009155 | -0.24719 | 5.9967 | 1.1627 | 1.0483 | 1.1719 | 1.0574 | 0.077819 | -0.013733 | 6.0059 | 121.9894 | 0.045776 | 122.2275 | 0.10529 | 122.2183 | -122.168 | -122.2366 | 0.045777 | 121.9803 | -0.004577 | 38.1866
4759.25 | 122.2229 | -0.14648 | 122.0764 | -0.10506 | -0.044312 | 0.00045503 | 0.021655 | 0.0012903 | -0.011384 | -0.0051505 | -0.11075 | 0.021119 | 0.068977 | 0.048337 | -0.018369 | 0.032748 | 0.0044605 | -0.19226 | -0.004578 | -0.11444 | -0.1236 | -0.059509 | -0.13733 | -0.054932 | 37.9166 | 122.0993 | -0.16479 | 121.8567 | 5.9189 | 0.91553 | 1.0666 | 0.032043 | -122.081 | -122.2 | 0.086975 | 0.091552 | 0.009155 | 0.059509 | -0.022888 | -0.018311 | 0.022888 | -0.21973 | 6.0654 | 1.2131 | 1.062 | 1.2314 | 1.0803 | 0.054932 | -0.009155 | 6.0837 | 122.0215 | 0.10986 | 122.2641 | 0.14191 | 122.2458 | -122.1909 | -122.2412 | 0.022888 | 122.0032 | -0.045777 | 38.063
4761.0156 | 122.3099 | -0.13275 | 122.0306 | -0.15846 | -0.041535 | 0.0017368 | 0.0208 | -0.0031957 | -0.0098886 | -0.0036551 | -0.028351 | 0.020264 | 0.06919 | 0.050686 | -0.018156 | 0.02933 | 0.0018969 | -0.15106 | -0.054932 | -0.073242 | -0.050354 | 0.064087 | -0.073242 | 0.045776 | 37.8891 | 122.0123 | -0.14191 | 121.9162 | 6.0745 | 1.0574 | 1.1765 | 0.059509 | -122.0856 | -122.081 | 0.19684 | 0.17853 | 0.059509 | 0.11902 | 0 | -0.009156 | -0.018311 | -0.11444 | 6.2073 | 1.3092 | 1.1902 | 1.3184 | 1.1993 | 0.13733 | 0.022888 | 6.2164 | 122.0581 | 0.01831 | 122.1542 | 0.077819 | 122.1451 | -122.1039 | -122.1725 | 0.082397 | 122.049 | -0.018311 | 38.0219
4762.7969 | 122.1909 | -0.15106 | 122.0581 | -0.19661 | -0.039826 | 0.0010958 | 0.02315 | 0.0023585 | -0.008607 | -0.0028005 | -0.15347 | 0.021332 | 0.06919 | 0.054104 | -0.019224 | 0.033389 | 0.0018969 | -0.15564 | -0.013733 | -0.09613 | -0.14648 | -0.064087 | -0.20142 | -0.082397 | 37.6968 | 122.0535 | -0.17395 | 121.8384 | 6.0013 | 0.90637 | 1.1124 | 0.054932 | -122.0718 | -122.2046 | 0.086975 | 0.068665 | -0.050354 | 0.013733 | -0.10529 | -0.022888 | -0.004577 | -0.21973 | 6.1523 | 1.2634 | 1.0574 | 1.2863 | 1.0803 | 0.032043 | -0.050354 | 6.1752 | 122.0123 | 0.082397 | 122.2275 | 0.13733 | 122.2046 | -122.1542 | -122.2321 | 0.004578 | 121.9894 | -0.004578 | 37.8479
4764.5625 | 122.2916 | -0.1236 | 122.0352 | -0.16609 | -0.041748 | 0.0017368 | 0.019305 | 0.0021447 | -0.011811 | -0.0057913 | -0.034454 | 0.01941 | 0.070045 | 0.053036 | -0.017942 | 0.030612 | 0.0010425 | -0.10529 | -0.064087 | -0.059509 | -0.004578 | 0.10529 | -0.032043 | 0.054932 | 37.8021 | 122.0215 | -0.13275 | 121.9116 | 6.2073 | 1.0803 | 1.2131 | 0.064087 | -122.0993 | -122.0398 | 0.22888 | 0.17853 | 0.091553 | 0.11444 | 0.027466 | -0.009155 | -0.013733 | -0.1236 | 6.3309 | 1.3367 | 1.2039 | 1.3458 | 1.2131 | 0.16479 | 0.054931 | 6.34 | 122.0444 | -0.004578 | 122.1542 | 0.059509 | 122.1451 | -122.0947 | -122.168 | 0.11902 | 122.0352 | 0.01831 | 37.9257
4766.2656 | 117.9977 | -0.10986 | 117.8375 | -0.16609 | -0.039612 | 0.0030184 | 0.023791 | 0.00022207 | -0.0094614 | -0.0060049 | -0.13211 | 0.020051 | 0.065559 | 0.052609 | -0.019438 | 0.034457 | 0.0023243 | -0.16937 | -0.036621 | -0.10529 | -0.11444 | -0.022888 | -0.17853 | -0.050354 | 36.2503 | 117.897 | -0.16479 | 117.7185 | 5.9738 | 0.95673 | 1.1307 | 0.004577 | -117.8741 | -117.952 | 0.086975 | 0.059509 | -0.068665 | 0.054932 | -0.073242 | -0.054932 | 0.05951 | -0.11902 | 6.0837 | 1.2405 | 1.0666 | 1.2955 | 1.1215 | 0.082398 | -0.009155 | 6.1386 | 117.8833 | 0.068665 | 118.0618 | 0.073242 | 118.0069 | -117.9428 | -118.0023 | -0.004578 | 117.8284 | -0.05951 | 36.3602
4768.0312 | 122.1313 | -0.15564 | 122.049 | -0.18898 | -0.038758 | 0.0036594 | 0.022723 | 0.0021447 | -0.013307 | -0.0023733 | -0.13516 | 0.022614 | 0.069618 | 0.053464 | -0.020292 | 0.033603 | 0.0014697 | -0.16022 | -0.013733 | -0.09613 | -0.15106 | -0.07782 | -0.21515 | -0.082397 | 37.3672 | 122.0444 | -0.16479 | 121.7834 | 6.1844 | 0.95673 | 1.1307 | 0.05951 | -122.0627 | -122.2 | 0.07782 | 0.073243 | -0.059509 | 0.013733 | -0.11902 | -0.009155 | -0.004577 | -0.2655 | 6.34 | 1.2863 | 1.1124 | 1.2955 | 1.1215 | 0.01831 | -0.054932 | 6.3492 | 121.9482 | 0.082397 | 122.2092 | 0.14191 | 122.2 | -122.1451 | -122.2137 | 0.004578 | 121.9391 | -0.004577 | 37.5229
4769.8125 | 122.1725 | -0.16022 | 122.0673 | -0.18898 | -0.038971 | 0.002164 | 0.022723 | 0.00022207 | -0.010102 | -0.0064321 | -0.12601 | 0.023896 | 0.072181 | 0.050046 | -0.01602 | 0.033817 | 0.0012561 | -0.15564 | -0.027466 | -0.10071 | -0.15106 | -0.073242 | -0.21515 | -0.082397 | 37.2986 | 122.0215 | -0.16022 | 121.7972 | 6.2485 | 0.97961 | 1.181 | 0.059509 | -122.0947 | -122.2183 | 0.086975 | 0.07782 | -0.054932 | 0.018311 | -0.11444 | 0 | -0.045777 | -0.27008 | 6.4087 | 1.3412 | 1.1398 | 1.3412 | 1.1398 | 0.027466 | -0.050354 | 6.4087 | 121.9574 | 0.073242 | 122.1817 | 0.13275 | 122.1817 | -122.168 | -122.2275 | 0.009155 | 121.9574 | 0.004577 | 37.4588
4771.5156 | 122.2137 | -0.13275 | 122.0718 | -0.1432 | -0.041962 | 0.0019504 | 0.017169 | 8.47e-06 | -0.011598 | -0.0045095 | -0.04361 | 0.020905 | 0.068977 | 0.058804 | -0.017942 | 0.032535 | 0.0040333 | -0.10986 | -0.064087 | -0.059509 | -0.032043 | 0.091553 | -0.041199 | 0.036621 | 37.2711 | 121.9986 | -0.14648 | 121.8475 | 6.4545 | 1.1124 | 1.2497 | 0.073242 | -122.1359 | -122.1039 | 0.2243 | 0.16937 | 0.091552 | 0.09613 | 0.01831 | -0.013733 | -0.073242 | -0.2243 | 6.5872 | 1.3824 | 1.2451 | 1.3962 | 1.2589 | 0.15106 | 0.027466 | 6.601 | 121.994 | -0.004578 | 122.1451 | 0.068664 | 122.1313 | -122.1313 | -122.2183 | 0.10071 | 121.9803 | 0.022888 | 37.4039
4773.2812 | 122.2504 | -0.11902 | 122.0306 | -0.20424 | -0.041748 | 0.00066863 | 0.020373 | -0.0040503 | -0.008607 | -0.0085683 | -0.071076 | 0.021546 | 0.072181 | 0.050686 | -0.017088 | 0.033817 | 0.0025379 | -0.12817 | -0.059509 | -0.059509 | -0.022888 | 0.09613 | -0.073242 | 0.032043 | 37.1933 | 121.9849 | -0.1236 | 121.8796 | 6.5002 | 1.1307 | 1.3046 | 0.05951 | -122.0901 | -122.0535 | 0.21515 | 0.15106 | 0.045777 | 0.091552 | -0.013733 | -0.004577 | -0.045777 | -0.15106 | 6.6193 | 1.4236 | 1.2497 | 1.4282 | 1.2543 | 0.15564 | 0.036621 | 6.6238 | 122.0032 | 0 | 122.1085 | 0.05951 | 122.1039 | -122.0901 | -122.1542 | 0.096131 | 121.9986 | -0.009155 | 37.3123
4775.0625 | 122.1405 | -0.14191 | 122.0306 | -0.15083 | -0.041321 | -0.00018577 | 0.02315 | -0.0010595 | -0.010102 | -0.0042959 | -0.13516 | 0.022828 | 0.071113 | 0.054959 | -0.019651 | 0.037021 | 0.0036059 | -0.13275 | -0.050354 | -0.068665 | -0.091553 | -0.018311 | -0.15564 | -0.068665 | 37.0605 | 122.0169 | -0.16937 | 121.7926 | 6.4819 | 1.0529 | 1.2131 | 0.073242 | -122.081 | -122.1222 | 0.1236 | 0.073242 | -0.013733 | 0 | -0.086975 | -0.027466 | -0.013733 | -0.23804 | 6.6238 | 1.355 | 1.1948 | 1.3824 | 1.2222 | 0.050354 | -0.022888 | 6.6513 | 121.962 | 0.018311 | 122.1863 | 0.091553 | 122.1588 | -122.0993 | -122.2 | 0.050354 | 121.9345 | 0.009156 | 37.2025
4776.7656 | 122.1634 | -0.13733 | 122.0261 | -0.10506 | -0.041962 | -0.00018577 | 0.021441 | -0.0010595 | -0.013307 | -0.0045095 | -0.092438 | 0.022828 | 0.07154 | 0.051327 | -0.017515 | 0.034885 | 0.0023243 | -0.17853 | -0.032043 | -0.086975 | -0.14191 | -0.045776 | -0.15564 | -0.054932 | 36.882 | 122.0078 | -0.16479 | 121.7743 | 6.5689 | 1.0986 | 1.236 | 0.050354 | -122.0581 | -122.168 | 0.091553 | 0.082397 | -0.018311 | 0.032043 | -0.068665 | -0.027466 | -0.018311 | -0.25177 | 6.7062 | 1.3733 | 1.236 | 1.4008 | 1.2634 | 0.041199 | -0.054932 | 6.7337 | 121.9391 | 0.054932 | 122.1725 | 0.10529 | 122.1451 | -122.113 | -122.1909 | -0.004578 | 121.9116 | -0.041199 | 37.0193
4778.5312 | 122.1771 | -0.1236 | 121.9345 | -0.15846 | -0.042176 | 0.00066863 | 0.019091 | 0.0010767 | -0.012879 | -0.0047231 | -0.0069885 | 0.020051 | 0.070045 | 0.052609 | -0.016874 | 0.032748 | 0.0068103 | -0.14648 | -0.045776 | -0.082397 | -0.07782 | 0.045776 | -0.086975 | 0.022888 | 36.8637 | 121.8887 | -0.13275 | 121.7697 | 6.7383 | 1.2039 | 1.3184 | 0.041199 | -121.9803 | -122.0123 | 0.16937 | 0.14648 | 0.036621 | 0.10528 | -0.004578 | -0.009155 | -0.045776 | -0.1648 | 6.8619 | 1.442 | 1.3275 | 1.4511 | 1.3367 | 0.12817 | 0.004577 | 6.871 | 121.9025 | 0.036621 | 122.0215 | 0.07782 | 122.0123 | -122.0169 | -122.0673 | 0.045776 | 121.8933 | -0.022888 | 36.9873
4780.2344 | 122.2458 | -0.10986 | 121.9528 | -0.12794 | -0.042389 | 0.001523 | 0.021869 | -0.0021277 | -0.011811 | -0.0055777 | -0.092438 | 0.021546 | 0.071113 | 0.056454 | -0.019438 | 0.034885 | -0.00088011 | -0.10529 | -0.054932 | -0.073242 | -0.045776 | 0.073242 | -0.091553 | 0.032043 | 36.8317 | 121.9345 | -0.13275 | 121.875 | 6.7795 | 1.2314 | 1.3824 | 0.036621 | -122.0078 | -121.9986 | 0.18311 | 0.14191 | 0.01831 | 0.10529 | -0.018311 | -0.022888 | -0.018311 | -0.07782 | 6.8893 | 1.4923 | 1.3412 | 1.5152 | 1.3641 | 0.14648 | 0.027466 | 6.9122 | 122.0078 | 0.01831 | 122.0673 | 0.054931 | 122.0444 | -122.0261 | -122.0856 | 0.064087 | 121.9849 | 0.004577 | 36.9415
4782 | 122.1222 | -0.15564 | 121.994 | -0.11269 | -0.043244 | 0.0019504 | 0.0208 | -0.0025549 | -0.012239 | -0.0013051 | -0.068024 | 0.02475 | 0.068336 | 0.052609 | -0.017515 | 0.034457 | 0.0027515 | -0.18768 | -0.027466 | -0.1236 | -0.14191 | -0.036621 | -0.14191 | -0.045776 | 36.6623 | 121.962 | -0.17853 | 121.7102 | 6.7749 | 1.1444 | 1.2634 | 0.032044 | -122.0215 | -122.1359 | 0.11902 | 0.10986 | 0.013733 | 0.07782 | -0.018311 | -0.022888 | -0.032044 | -0.28381 | 6.9305 | 1.4191 | 1.3 | 1.442 | 1.3229 | 0.086975 | -0.018311 | 6.9534 | 121.8887 | 0.09613 | 122.1405 | 0.12817 | 122.1176 | -122.1176 | -122.1725 | 0.013733 | 121.8658 | -0.032043 | 36.8179
4783.7656 | 122.113 | -0.14191 | 121.9391 | -0.15846 | -0.042176 | 0.001523 | 0.022082 | -0.0012731 | -0.01352 | -0.0051505 | -0.10159 | 0.021973 | 0.071113 | 0.060086 | -0.017729 | 0.033817 | 0.0036059 | -0.13275 | -0.022888 | -0.10529 | -0.073242 | 0.004578 | -0.11444 | -0.022888 | 36.6852 | 121.9299 | -0.16022 | 121.7239 | 6.8481 | 1.1993 | 1.3229 | 0.036621 | -121.962 | -122.0123 | 0.14649 | 0.11902 | 0.027466 | 0.082398 | -0.009155 | -0.01831 | -0.009155 | -0.21515 | 6.9901 | 1.4648 | 1.3412 | 1.4832 | 1.3596 | 0.10986 | 0.032044 | 7.0084 | 121.8842 | 0.082398 | 122.0901 | 0.11902 | 122.0718 | -122.0444 | -122.0993 | 0.068665 | 121.8658 | 0.009156 | 36.8271
4785.4531 | 122.1222 | -0.11444 | 121.8704 | -0.22713 | -0.041107 | 0.0013094 | 0.024005 | 8.47e-06 | -0.01117 | -0.0038687 | -0.068024 | 0.02475 | 0.06919 | 0.053891 | -0.019224 | 0.035739 | 0.0044605 | -0.11902 | -0.068665 | -0.068665 | -0.027466 | 0.091553 | -0.068665 | 0.027466 | 36.6302 | 121.8384 | -0.13275 | 121.7239 | 6.9534 | 1.2817 | 1.4008 | 0.045776 | -121.9391 | -121.8979 | 0.20599 | 0.14191 | 0.045776 | 0.096131 | 0 | -0.01831 | -0.032043 | -0.14648 | 7.0679 | 1.5152 | 1.3962 | 1.5335 | 1.4145 | 0.16022 | 0.041199 | 7.0862 | 121.8567 | 0 | 121.9711 | 0.045776 | 121.9528 | -121.9391 | -122.0032 | 0.086975 | 121.8384 | -0.004578 | 36.7447
4787.2188 | 121.9391 | -0.1236 | 121.788 | -0.15846 | -0.039826 | 0.00024143 | 0.02315 | 0.0059901 | -0.012025 | -0.0040823 | -0.13516 | 0.024964 | 0.071754 | 0.05325 | -0.018797 | 0.036594 | 0.0016833 | -0.12817 | -0.041199 | -0.091553 | -0.073242 | 0.013733 | -0.1236 | -0.027466 | 36.4609 | 121.7926 | -0.16479 | 121.582 | 6.9672 | 1.1902 | 1.3321 | 0.032043 | -121.8292 | -121.8613 | 0.13733 | 0.09613 | 0 | 0.064087 | -0.032043 | -0.041199 | 0.004578 | -0.20599 | 7.0908 | 1.4557 | 1.3138 | 1.4969 | 1.355 | 0.10529 | 0.018311 | 7.132 | 121.7468 | 0.050354 | 121.9574 | 0.082397 | 121.9162 | -121.8796 | -121.9528 | 0.050354 | 121.7056 | -0.004578 | 36.5845
4788.9219 | 121.9254 | -0.086975 | 121.7377 | -0.20424 | -0.042389 | 0.0030184 | 0.018451 | 0.0010767 | -0.0090342 | -0.0047231 | -0.046661 | 0.02411 | 0.068763 | 0.049191 | -0.017515 | 0.033176 | 0.0042469 | -0.1236 | -0.07782 | -0.054932 | -0.018311 | 0.10071 | -0.068665 | 0.045776 | 36.4792 | 121.7102 | -0.11902 | 121.6187 | 7.077 | 1.3184 | 1.4648 | 0.032043 | -121.8155 | -121.756 | 0.18768 | 0.13275 | 0.01831 | 0.10071 | -0.013733 | -0.032044 | -0.027466 | -0.11902 | 7.164 | 1.5518 | 1.4053 | 1.5839 | 1.4374 | 0.15564 | 0.036621 | 7.196 | 121.7377 | -0.022888 | 121.8292 | 0.009155 | 121.7972 | -121.7926 | -121.8567 | 0.068664 | 121.7056 | -0.036621 | 36.5662
4790.6875 | 121.8384 | -0.091553 | 121.55 | -0.15846 | -0.043244 | 0.00024143 | 0.019091 | 0.0023585 | -0.012879 | -0.0019461 | -0.022247 | 0.023041 | 0.069831 | 0.048337 | -0.018797 | 0.03403 | 0.0016833 | -0.11444 | -0.045776 | -0.086975 | 0 | 0.11444 | -0.009155 | 0.054932 | 36.3098 | 121.5271 | -0.13275 | 121.4218 | 7.1503 | 1.387 | 1.4465 | 0.004578 | -121.5958 | -121.55 | 0.20599 | 0.14649 | 0.082398 | 0.14191 | 0.07782 | -0.041198 | -0.022888 | -0.12817 | 7.2418 | 1.5381 | 1.4786 | 1.5793 | 1.5198 | 0.20142 | 0.086975 | 7.283 | 121.5546 | 0.041199 | 121.6599 | 0.045777 | 121.6187 | -121.637 | -121.6827 | 0.091553 | 121.5134 | -0.022888 | 36.4014
4792.4062 | 121.7102 | -0.13733 | 121.4676 | -0.18898 | -0.039398 | 0.00024143 | 0.023364 | -0.0019141 | -0.010743 | -0.0017325 | -0.12296 | 0.025178 | 0.071327 | 0.047696 | -0.019651 | 0.035312 | 0.0029651 | -0.17853 | -0.009155 | -0.11444 | -0.14648 | -0.054932 | -0.18768 | -0.064087 | 36.0992 | 121.4813 | -0.15564 | 121.2479 | 7.077 | 1.2177 | 1.4053 | 0.022888 | -121.4767 | -121.6141 | 0.082397 | 0.073242 | -0.050354 | 0.050354 | -0.073242 | -0.018311 | 0.013733 | -0.21973 | 7.2144 | 1.5427 | 1.355 | 1.561 | 1.3733 | 0.059509 | -0.032043 | 7.2327 | 121.4035 | 0.10529 | 121.637 | 0.12817 | 121.6187 | -121.582 | -121.6232 | -0.009155 | 121.3852 | -0.041199 | 36.2366
4794.1719 | 121.8613 | -0.14648 | 121.6736 | -0.10506 | -0.041107 | 0.00024143 | 0.0208 | 0.00086307 | -0.012025 | -0.0021597 | -0.10159 | 0.023682 | 0.071754 | 0.060299 | -0.019651 | 0.035953 | 0.0036059 | -0.16022 | -0.018311 | -0.086975 | -0.091553 | -0.013733 | -0.1236 | -0.032043 | 36.1771 | 121.6324 | -0.15106 | 121.4539 | 7.2327 | 1.3367 | 1.4236 | 0.059509 | -121.6919 | -121.7651 | 0.13275 | 0.11444 | 0.022888 | 0.054932 | -0.036621 | -0.004578 | -0.041199 | -0.21973 | 7.3792 | 1.5701 | 1.4832 | 1.5747 | 1.4877 | 0.073242 | -0.004578 | 7.3837 | 121.6049 | 0.068664 | 121.7834 | 0.12817 | 121.7789 | -121.7606 | -121.8246 | 0.054931 | 121.6003 | -0.013733 | 36.3235
4795.9375 | 121.9162 | -0.082397 | 121.7102 | -0.17372 | -0.041962 | 0.003232 | 0.019946 | -0.0038367 | -0.011811 | -0.0045095 | -0.01004 | 0.024537 | 0.071113 | 0.051541 | -0.019651 | 0.036807 | 0.0016833 | -0.15106 | -0.036621 | -0.064087 | -0.073242 | 0.027466 | -0.086975 | 0.027466 | 36.2228 | 121.6873 | -0.11444 | 121.5454 | 7.3792 | 1.4008 | 1.506 | 0.01831 | -121.7468 | -121.7834 | 0.10986 | 0.10986 | -0.004578 | 0.091553 | -0.022888 | -0.032044 | -0.022888 | -0.16479 | 7.4615 | 1.5884 | 1.4832 | 1.6205 | 1.5152 | 0.091553 | -0.009155 | 7.4936 | 121.6599 | 0.027466 | 121.8018 | 0.045776 | 121.7697 | -121.7743 | -121.8246 | 0.009155 | 121.6278 | -0.068665 | 36.3052
4797.6406 | 121.962 | -0.11902 | 121.8109 | -0.15846 | -0.042389 | 0.00024143 | 0.022723 | -0.00063233 | -0.011811 | -0.0023733 | -0.092438 | 0.027314 | 0.070472 | 0.051968 | -0.019224 | 0.034671 | 0.0012561 | -0.15106 | -0.004578 | -0.09613 | -0.13275 | -0.018311 | -0.12817 | -0.036621 | 36.0901 | 121.8063 | -0.13733 | 121.6049 | 7.4387 | 1.3687 | 1.4923 | 0.022889 | -121.8155 | -121.9437 | 0.10071 | 0.082398 | -0.009155 | 0.059509 | -0.032044 | -0.01831 | -0.004578 | -0.20599 | 7.5577 | 1.6113 | 1.4877 | 1.6296 | 1.506 | 0.077819 | -0.036621 | 7.576 | 121.7422 | 0.091552 | 121.9437 | 0.11444 | 121.9254 | -121.907 | -121.9482 | -0.013732 | 121.7239 | -0.032043 | 36.2091
4799.4219 | 122.081 | -0.073242 | 121.8246 | -0.20424 | -0.041107 | -0.00018577 | 0.024432 | 0.0012903 | -0.010102 | -0.0038687 | -0.080231 | 0.025605 | 0.068977 | 0.060086 | -0.01901 | 0.036166 | 0.0031787 | -0.082397 | -0.050354 | -0.045776 | 0 | 0.10529 | -0.064087 | 0.045776 | 36.1221 | 121.8201 | -0.091553 | 121.7239 | 7.6355 | 1.5289 | 1.6159 | 0.027466 | -121.875 | -121.8246 | 0.17853 | 0.11902 | 0.009155 | 0.091552 | -0.018311 | -0.018311 | -0.004578 | -0.10071 | 7.7087 | 1.6891 | 1.6022 | 1.7075 | 1.6205 | 0.15106 | 0.045776 | 7.7271 | 121.8155 | -0.004578 | 121.9116 | 0.022888 | 121.8933 | -121.8704 | -121.9162 | 0.073242 | 121.7972 | -0.009155 | 36.1954
4801.1719 | 122.0581 | -0.07782 | 121.8338 | -0.24239 | -0.04068 | 0.0025912 | 0.0208 | 0.0017175 | -0.011598 | -0.0021597 | -0.055817 | 0.025819 | 0.070899 | 0.051541 | -0.020719 | 0.037448 | 0.0021107 | -0.091553 | -0.059509 | -0.054932 | -0.004578 | 0.11444 | -0.050354 | 0.054932 | 36.0214 | 121.8018 | -0.10071 | 121.7239 | 7.6813 | 1.5198 | 1.593 | 0.022888 | -121.8933 | -121.8384 | 0.19226 | 0.13275 | 0.027466 | 0.10986 | 0.004578 | -0.022888 | -0.032043 | -0.10986 | 7.7591 | 1.6708 | 1.5976 | 1.6937 | 1.6205 | 0.16937 | 0.050354 | 7.782 | 121.8246 | -0.004577 | 121.9025 | 0.018311 | 121.8796 | -121.8887 | -121.9345 | 0.073242 | 121.8018 | -0.013733 | 36.0992
4802.9375 | 122.113 | -0.082397 | 121.8704 | -0.15083 | -0.044098 | 0.0010958 | 0.021441 | -0.0017005 | -0.010957 | -0.0047231 | -0.025299 | 0.024323 | 0.07389 | 0.054318 | -0.020506 | 0.036594 | 0.0078785 | -0.14648 | -0.041199 | -0.07782 | -0.041199 | 0.054932 | -0.059509 | 0.054932 | 35.8978 | 121.8384 | -0.091553 | 121.7239 | 7.7683 | 1.593 | 1.6205 | 0.004577 | -121.9116 | -121.9116 | 0.13733 | 0.13733 | 0.022888 | 0.13275 | 0.018311 | -0.009156 | -0.032043 | -0.14648 | 7.8506 | 1.7029 | 1.6754 | 1.712 | 1.6846 | 0.13275 | 0.036621 | 7.8598 | 121.8155 | 0.036621 | 121.9299 | 0.041198 | 121.9208 | -121.9482 | -121.962 | 0.041198 | 121.8063 | -0.064087 | 35.9802
4804.7031 | 122.1176 | -0.07782 | 121.8933 | -0.15846 | -0.039612 | 0.0013094 | 0.025073 | 0.0019311 | -0.009675 | -0.0034415 | -0.086334 | 0.026887 | 0.071327 | 0.056241 | -0.020078 | 0.035953 | 0.0033923 | -0.13733 | -0.009155 | -0.10071 | -0.068665 | 0.036621 | -0.10529 | 0.013733 | 35.8612 | 121.8704 | -0.10986 | 121.756 | 7.8232 | 1.5564 | 1.6708 | -0.022888 | -121.9025 | -121.962 | 0.11444 | 0.091553 | -0.027466 | 0.11444 | -0.004578 | -0.032043 | -0.022889 | -0.13733 | 7.901 | 1.7487 | 1.6342 | 1.7807 | 1.6663 | 0.13733 | 0.032043 | 7.933 | 121.8658 | 0.091553 | 121.9803 | 0.068665 | 121.9482 | -121.994 | -122.0032 | 0.009155 | 121.8338 | -0.059509 | 35.939
4806.4062 | 122.0261 | -0.10071 | 121.9208 | -0.15846 | -0.040253 | 0.0013094 | 0.024005 | -0.00084593 | -0.012239 | -0.0066457 | -0.1199 | 0.027741 | 0.071967 | 0.066067 | -0.02136 | 0.035098 | 0.0023243 | -0.11902 | -0.004578 | -0.082397 | -0.054932 | 0.013733 | -0.11444 | -0.009155 | 35.7101 | 121.907 | -0.13275 | 121.701 | 7.8094 | 1.6022 | 1.6022 | 0.018311 | -121.9254 | -121.9757 | 0.11444 | 0.091553 | -0.013733 | 0.073242 | -0.032044 | -0.032043 | -0.013733 | -0.21973 | 7.9102 | 1.7029 | 1.7029 | 1.7349 | 1.7349 | 0.09613 | 0.027465 | 7.9422 | 121.8338 | 0.077819 | 122.0398 | 0.09613 | 122.0078 | -122.0032 | -122.0535 | 0.045776 | 121.8018 | -0.018311 | 35.8109
4808.1875 | 122.0123 | -0.1236 | 121.9391 | -0.15846 | -0.043244 | -0.0023222 | 0.021655 | -0.00020513 | -0.011811 | -0.0042959 | -0.055817 | 0.028382 | 0.071113 | 0.061795 | -0.017729 | 0.035739 | 0.0042469 | -0.17395 | -0.009155 | -0.086975 | -0.14648 | -0.013733 | -0.13275 | -0.036621 | 35.6049 | 121.9299 | -0.12817 | 121.6644 | 7.8644 | 1.5244 | 1.5518 | 0.036621 | -121.9482 | -122.0856 | 0.10986 | 0.086975 | -0.009155 | 0.050354 | -0.045776 | -0.004578 | -0.009155 | -0.27466 | 7.988 | 1.6754 | 1.6479 | 1.68 | 1.6525 | 0.073242 | -0.059509 | 7.9926 | 121.7926 | 0.07782 | 122.0581 | 0.11444 | 122.0535 | -122.0261 | -122.0673 | -0.022888 | 121.788 | -0.050354 | 35.7285
4809.9062 | 122.0764 | -0.10071 | 121.9299 | -0.18898 | -0.043457 | 0.00088223 | 0.02315 | 0.0036401 | -0.011598 | -0.0025869 | -0.089386 | 0.028809 | 0.072181 | 0.053036 | -0.016874 | 0.037448 | 0.0046741 | -0.13275 | -0.004578 | -0.091553 | -0.07782 | 0.009155 | -0.10529 | -0.022888 | 35.6277 | 121.9299 | -0.13733 | 121.7239 | 7.9514 | 1.6159 | 1.6296 | 0.009155 | -121.9345 | -122.0078 | 0.10986 | 0.07782 | -0.004578 | 0.068665 | -0.013733 | -0.036621 | 0 | -0.20599 | 8.0521 | 1.7303 | 1.7166 | 1.767 | 1.7532 | 0.10071 | 0.013733 | 8.0887 | 121.8613 | 0.086975 | 122.0673 | 0.09613 | 122.0306 | -122.0215 | -122.0673 | 0.022888 | 121.8246 | -0.032043 | 35.7285
4811.6719 | 122.1222 | -0.082397 | 121.9299 | -0.20424 | -0.041748 | 0.00024143 | 0.018878 | 0.00064947 | -0.012239 | -0.0070731 | -0.0039367 | 0.027528 | 0.072608 | 0.057309 | -0.016233 | 0.034885 | 0.0053149 | -0.13275 | -0.032043 | -0.068665 | -0.059509 | 0.041199 | -0.09613 | 0.027466 | 35.5911 | 121.8979 | -0.10529 | 121.7468 | 7.9834 | 1.6571 | 1.6937 | 0.013732 | -121.962 | -121.9894 | 0.1236 | 0.10986 | -0.013733 | 0.096131 | -0.027465 | -0.022889 | -0.032044 | -0.18311 | 8.0658 | 1.7761 | 1.7395 | 1.799 | 1.7624 | 0.10986 | 0.009156 | 8.0887 | 121.8521 | 0.036622 | 122.0032 | 0.050354 | 121.9803 | -121.9986 | -122.0352 | 0.022888 | 121.8292 | -0.050354 | 35.6735
4813.375 | 122.0535 | -0.1236 | 121.9666 | -0.16609 | -0.042389 | -0.001254 | 0.02016 | 0.00022207 | -0.012666 | -0.0051505 | -0.074127 | 0.027528 | 0.071967 | 0.0509 | -0.017729 | 0.037021 | 0.0033923 | -0.17853 | -0.004578 | -0.082397 | -0.13733 | -0.022888 | -0.14191 | -0.027466 | 35.4584 | 121.9666 | -0.13733 | 121.6782 | 8.0383 | 1.5884 | 1.6067 | 0.041199 | -121.9711 | -122.1039 | 0.10071 | 0.09613 | -0.018311 | 0.054931 | -0.05951 | -0.013733 | 0 | -0.28839 | 8.1619 | 1.7303 | 1.712 | 1.7441 | 1.7258 | 0.059509 | -0.054932 | 8.1757 | 121.8155 | 0.077819 | 122.1039 | 0.11902 | 122.0901 | -122.049 | -122.1039 | -0.013733 | 121.8018 | -0.054932 | 35.582
4815.1406 | 122.2 | -0.082397 | 121.9208 | -0.15846 | -0.042389 | 0.00088223 | 0.018237 | 0.0012903 | -0.010743 | -0.0060049 | -0.025299 | 0.026032 | 0.072395 | 0.046841 | -0.019224 | 0.036166 | 0.0016833 | -0.091553 | -0.059509 | -0.064087 | 0.004578 | 0.15106 | -0.004578 | 0.073242 | 35.614 | 121.8979 | -0.09613 | 121.8155 | 8.2993 | 1.7578 | 1.7624 | 0.01831 | -121.9803 | -121.9162 | 0.23346 | 0.15564 | 0.077819 | 0.13733 | 0.059509 | -0.013733 | -0.022888 | -0.10529 | 8.3817 | 1.8448 | 1.8402 | 1.8585 | 1.8539 | 0.21515 | 0.068665 | 8.3954 | 121.9116 | 0.004578 | 121.994 | 0.022888 | 121.9803 | -121.9849 | -122.0169 | 0.086975 | 121.8979 | -0.009156 | 35.6964
4816.9062 | 122.081 | -0.10986 | 122.0032 | -0.10506 | -0.042389 | 2.7834e-05 | 0.020373 | -0.0036231 | -0.013947 | -0.0036551 | -0.064972 | 0.026673 | 0.071754 | 0.055386 | -0.018797 | 0.036807 | 0.0063831 | -0.11444 | -0.032043 | -0.09613 | -0.07782 | 0.022888 | -0.11902 | 0.004578 | 35.4858 | 121.9345 | -0.12817 | 121.6873 | 8.1848 | 1.6159 | 1.6296 | 0.013733 | -122.0352 | -122.081 | 0.13275 | 0.11444 | -0.009156 | 0.10071 | -0.022889 | -0.018311 | -0.068665 | -0.31586 | 8.2947 | 1.7395 | 1.7258 | 1.7578 | 1.7441 | 0.11902 | 0.01831 | 8.313 | 121.8155 | 0.064087 | 122.0627 | 0.07782 | 122.0444 | -122.0993 | -122.1313 | 0.032043 | 121.7972 | -0.004578 | 35.5957
4818.6875 | 122.0856 | -0.10986 | 121.9849 | -0.13557 | -0.043885 | 0.0013094 | 0.022082 | -0.0059729 | -0.012452 | -0.0042959 | -0.11075 | 0.028809 | 0.072608 | 0.059445 | -0.019224 | 0.036594 | 0.0038195 | -0.17395 | -0.009155 | -0.10529 | -0.13733 | -0.041199 | -0.15106 | -0.045776 | 35.3027 | 121.9803 | -0.13733 | 121.6965 | 8.2535 | 1.6479 | 1.6891 | 0.004577 | -121.994 | -122.1222 | 0.068664 | 0.064087 | -0.041199 | 0.05951 | -0.045776 | -0.027466 | -0.004577 | -0.28839 | 8.3633 | 1.799 | 1.7578 | 1.8265 | 1.7853 | 0.064087 | -0.032043 | 8.3908 | 121.8338 | 0.096131 | 122.1176 | 0.10071 | 122.0901 | -122.0901 | -122.1222 | -0.027466 | 121.8063 | -0.064087 | 35.4126
4820.4688 | 122.2183 | -0.07782 | 121.9482 | -0.1432 | -0.04538 | -0.00018577 | 0.017169 | -0.0014867 | -0.014161 | -0.0028005 | -0.019196 | 0.027955 | 0.073249 | 0.0509 | -0.019224 | 0.036166 | 0.0012561 | -0.091553 | -0.064087 | -0.054932 | 0 | 0.1236 | -0.022888 | 0.082397 | 35.3851 | 121.9208 | -0.09613 | 121.8384 | 8.4549 | 1.8585 | 1.8219 | 0.022888 | -122.0123 | -121.9482 | 0.20142 | 0.16022 | 0.054932 | 0.13733 | 0.032044 | -0.01831 | -0.027466 | -0.10986 | 8.5327 | 1.8997 | 1.9363 | 1.918 | 1.9547 | 0.17853 | 0.054932 | 8.551 | 121.9345 | -0.009155 | 122.0169 | 0.013733 | 121.9986 | -122.0032 | -122.0444 | 0.07782 | 121.9162 | -0.013733 | 35.463
4822.1875 | 122.1039 | -0.1236 | 121.9757 | -0.12032 | -0.041321 | 0.00088223 | 0.021014 | 0.00064947 | -0.01117 | -0.0038687 | -0.1077 | 0.028809 | 0.07154 | 0.059659 | -0.018369 | 0.039371 | 0.0089465 | -0.15106 | -0.013733 | -0.091553 | -0.1236 | -0.041199 | -0.17853 | -0.064087 | 35.3027 | 121.9666 | -0.1236 | 121.7422 | 8.4595 | 1.6891 | 1.7395 | 0.032043 | -121.9894 | -122.0993 | 0.082397 | 0.059509 | -0.054932 | 0.027466 | -0.086975 | 0 | -0.009155 | -0.23346 | 8.5831 | 1.8631 | 1.8127 | 1.8631 | 1.8127 | 0.050354 | -0.032043 | 8.5831 | 121.8658 | 0.07782 | 122.0901 | 0.10986 | 122.0901 | -122.0673 | -122.0993 | 0 | 121.8658 | -0.027466 | 35.4263
4823.9688 | 122.2092 | -0.07782 | 121.9437 | -0.12794 | -0.044098 | 0.00088223 | 0.019091 | -0.0036231 | -0.011598 | -0.0040823 | -0.031403 | 0.029237 | 0.072181 | 0.05325 | -0.018156 | 0.039371 | 0.0033923 | -0.09613 | -0.054932 | -0.054932 | 0.013733 | 0.12817 | 0 | 0.086975 | 35.3348 | 121.9299 | -0.073242 | 121.8246 | 8.6563 | 1.7578 | 1.8631 | 0.022888 | -121.9986 | -121.9299 | 0.20599 | 0.16479 | 0.07782 | 0.14191 | 0.054932 | 0.004578 | -0.013733 | -0.11902 | 8.7341 | 1.9409 | 1.8356 | 1.9363 | 1.8311 | 0.18311 | 0.068665 | 8.7296 | 121.8979 | 0 | 122.0032 | 0.022888 | 122.0078 | -121.9986 | -122.0169 | 0.091553 | 121.9025 | -0.01831 | 35.4126
4825.6719 | 122.1588 | -0.07782 | 121.962 | -0.18135 | -0.041535 | 0.0010958 | 0.019519 | -0.0019141 | -0.0094614 | -0.0023733 | -0.055817 | 0.028168 | 0.070899 | 0.059659 | -0.017301 | 0.035526 | 0.0072375 | -0.11902 | -0.054932 | -0.041199 | -0.050354 | 0.059509 | -0.086975 | 0.022888 | 35.2432 | 121.9528 | -0.11444 | 121.8109 | 8.6151 | 1.918 | 1.8402 | 0.036621 | -122.0169 | -122.0123 | 0.13733 | 0.10071 | -0.009155 | 0.064087 | -0.045776 | -0.036621 | -0.009155 | -0.15106 | 8.6929 | 1.918 | 1.9958 | 1.9547 | 2.0325 | 0.10071 | -0.009155 | 8.7296 | 121.9254 | -0.013733 | 122.0673 | 0.022888 | 122.0306 | -122.0032 | -122.0764 | 0.027466 | 121.8887 | -0.041199 | 35.321
4827.4375 | 122.1176 | -0.11444 | 121.9849 | -0.1432 | -0.042603 | 2.7834e-05 | 0.021655 | 8.47e-06 | -0.011598 | -0.0051505 | -0.074127 | 0.030091 | 0.071754 | 0.062222 | -0.019438 | 0.039371 | 0.0046741 | -0.10529 | -0.027466 | -0.068665 | -0.041199 | 0.073242 | -0.054932 | 0.027466 | 35.1013 | 121.9757 | -0.10529 | 121.7422 | 8.6014 | 1.8631 | 1.8127 | 0.045776 | -122.0123 | -122.0261 | 0.18768 | 0.14191 | 0.059509 | 0.096131 | 0.013733 | 0.009155 | -0.009155 | -0.24261 | 8.7158 | 1.9272 | 1.9775 | 1.918 | 1.9684 | 0.14191 | 0.027466 | 8.7067 | 121.8475 | 0.041199 | 122.081 | 0.086975 | 122.0901 | -122.0535 | -122.0901 | 0.073242 | 121.8567 | 0.009155 | 35.2158
4829.2188 | 122.2412 | -0.07782 | 121.9757 | -0.17372 | -0.040894 | 0.00066863 | 0.018023 | -0.0019141 | -0.01117 | -0.0038687 | -0.040558 | 0.027741 | 0.071967 | 0.059018 | -0.020506 | 0.036807 | 0.010442 | -0.091553 | -0.059509 | -0.068665 | 0.009155 | 0.13733 | -0.027466 | 0.07782 | 35.1883 | 121.9482 | -0.10071 | 121.8521 | 8.7936 | 1.9592 | 1.9363 | 0.009155 | -122.0352 | -121.9666 | 0.21515 | 0.15564 | 0.050354 | 0.14649 | 0.041199 | -0.022888 | -0.027466 | -0.1236 | 8.8715 | 2.0142 | 2.037 | 2.037 | 2.0599 | 0.20599 | 0.07782 | 8.8943 | 121.9528 | 0.009156 | 122.0489 | 0.018311 | 122.0261 | -122.0444 | -122.0764 | 0.086975 | 121.9299 | -0.013733 | 35.2661
4830.9844 | 122.1359 | -0.10071 | 121.994 | -0.19661 | -0.040039 | 0.00066863 | 0.024646 | 0.0023585 | -0.010743 | -0.0028005 | -0.14737 | 0.030518 | 0.074317 | 0.061795 | -0.019438 | 0.037235 | 0.0027515 | -0.14648 | -0.022888 | -0.07782 | -0.11444 | -0.032043 | -0.16479 | -0.050354 | 34.9915 | 121.9757 | -0.11444 | 121.8109 | 8.8303 | 1.9089 | 1.8814 | 0.022888 | -122.0169 | -122.1085 | 0.068665 | 0.050354 | -0.064087 | 0.027466 | -0.086975 | -0.013733 | -0.018311 | -0.18311 | 8.931 | 1.9821 | 2.0096 | 1.9959 | 2.0233 | 0.045777 | -0.036621 | 8.9447 | 121.9254 | 0.054932 | 122.0901 | 0.07782 | 122.0764 | -122.0718 | -122.1085 | -0.013733 | 121.9116 | -0.045776 | 35.0922
4832.6875 | 122.1359 | -0.10071 | 122.0032 | -0.17372 | -0.040467 | 0.0010958 | 0.02315 | 0.0038537 | -0.010957 | -0.0038687 | -0.12906 | 0.030946 | 0.072608 | 0.06564 | -0.020078 | 0.037235 | 0.0040333 | -0.10986 | -0.009155 | -0.086975 | -0.068665 | 0.027466 | -0.09613 | -0.013733 | 35.0739 | 122.0123 | -0.10071 | 121.7834 | 8.8715 | 1.8997 | 1.9135 | 0.013733 | -122.0123 | -122.0718 | 0.12817 | 0.086975 | 0.004578 | 0.073242 | -0.009155 | 0 | 0.009155 | -0.21973 | 8.9722 | 2.0142 | 2.0004 | 2.0142 | 2.0004 | 0.11444 | 0.01831 | 8.9722 | 121.8842 | 0.07782 | 122.113 | 0.091553 | 122.113 | -122.0901 | -122.1039 | 0.032043 | 121.8842 | -0.009155 | 35.1746
4834.4688 | 122.1542 | -0.09613 | 121.9894 | -0.16609 | -0.04068 | 0.00088223 | 0.024859 | 0.0010767 | -0.010743 | -0.0030141 | -0.1199 | 0.029664 | 0.07154 | 0.061581 | -0.018583 | 0.041293 | 0.010228 | -0.14191 | 0 | -0.10071 | -0.10071 | -0.036621 | -0.16937 | -0.045776 | 35.0052 | 121.9757 | -0.11444 | 121.7926 | 8.9264 | 1.8997 | 1.9501 | -0.004578 | -121.9894 | -122.0901 | 0.059509 | 0.050354 | -0.073243 | 0.054932 | -0.068665 | -0.018311 | -0.013733 | -0.19684 | 9.0225 | 2.0462 | 1.9958 | 2.0645 | 2.0142 | 0.064087 | 0 | 9.0408 | 121.907 | 0.10071 | 122.0901 | 0.09613 | 122.0718 | -122.0901 | -122.1039 | -0.004578 | 121.8887 | -0.045777 | 35.1013
4836.1562 | 122.1085 | -0.13275 | 122.049 | -0.17372 | -0.043457 | 0.00066863 | 0.021228 | -0.00041873 | -0.013307 | -0.0051505 | -0.098541 | 0.032227 | 0.072822 | 0.060086 | -0.018369 | 0.038943 | 0.0059559 | -0.16022 | -0.009155 | -0.10529 | -0.14191 | -0.041199 | -0.13733 | -0.045776 | 35.0052 | 121.994 | -0.14191 | 121.7377 | 9.0363 | 1.9684 | 1.9043 | 0.027465 | -122.0581 | -122.1909 | 0.091552 | 0.086975 | -0.004578 | 0.05951 | -0.032043 | -0.009156 | -0.054931 | -0.31128 | 9.169 | 2.037 | 2.1011 | 2.0462 | 2.1103 | 0.064087 | -0.036621 | 9.1782 | 121.8796 | 0.096131 | 122.1359 | 0.1236 | 122.1268 | -122.1542 | -122.1909 | -0.009156 | 121.8704 | -0.027466 | 35.1379
4837.9219 | 122.1085 | -0.11444 | 122.0215 | -0.15846 | -0.040253 | 0.0023776 | 0.022937 | 0.0021447 | -0.013307 | -0.0055777 | -0.1199 | 0.032868 | 0.074317 | 0.062222 | -0.017515 | 0.040012 | 0.0085193 | -0.11902 | -0.013733 | -0.10071 | -0.086975 | 0.004578 | -0.14648 | -0.045776 | 35.0464 | 122.0123 | -0.11902 | 121.7697 | 9.0866 | 1.9089 | 1.973 | 0.013733 | -122.0352 | -122.1085 | 0.11902 | 0.068665 | -0.032043 | 0.054932 | -0.045776 | -0.004578 | -0.009155 | -0.25177 | 9.201 | 2.0874 | 2.0233 | 2.092 | 2.0279 | 0.10529 | 0.013733 | 9.2056 | 121.8887 | 0.086975 | 122.1313 | 0.10071 | 122.1268 | -122.1222 | -122.1405 | 0.027466 | 121.8842 | -0.004578 | 35.1608
4839.6875 | 122.1085 | -0.12817 | 122.0398 | -0.082169 | -0.041535 | 0.0017368 | 0.019305 | 0.0012903 | -0.011384 | -0.0066457 | -0.046661 | 0.032227 | 0.075599 | 0.054532 | -0.018797 | 0.038516 | 0.0093737 | -0.15564 | -0.022888 | -0.073242 | -0.11902 | -0.004578 | -0.11902 | -0.032043 | 35.0739 | 121.9894 | -0.14648 | 121.7377 | 9.2011 | 2.0142 | 1.9501 | 0.054932 | -122.0627 | -122.1588 | 0.1236 | 0.096131 | 0.009155 | 0.041199 | -0.045777 | -0.01831 | -0.050354 | -0.30212 | 9.3292 | 2.0782 | 2.1423 | 2.0966 | 2.1606 | 0.068664 | -0.045777 | 9.3475 | 121.8842 | 0.050354 | 122.1359 | 0.10529 | 122.1176 | -122.113 | -122.1863 | 0.009155 | 121.8658 | -0.027466 | 35.202
4841.3906 | 122.1359 | -0.09613 | 122.0123 | -0.16609 | -0.041748 | 0.001523 | 0.023578 | -0.0012731 | -0.010957 | -0.0030141 | -0.12296 | 0.033723 | 0.075385 | 0.054745 | -0.017301 | 0.040439 | 0.0040333 | -0.16479 | -0.013733 | -0.07782 | -0.13275 | -0.036621 | -0.16479 | -0.064087 | 35.1105 | 121.9986 | -0.13275 | 121.7743 | 9.256 | 1.8951 | 2.005 | 0.01831 | -122.0261 | -122.1451 | 0.059509 | 0.032043 | -0.068665 | 0.013733 | -0.086975 | -0.036621 | -0.013733 | -0.23804 | 9.3521 | 2.1011 | 1.9913 | 2.1378 | 2.0279 | 0.041199 | -0.054931 | 9.3887 | 121.907 | 0.064087 | 122.1313 | 0.082397 | 122.0947 | -122.0901 | -122.1451 | -0.036621 | 121.8704 | -0.068665 | 35.2066
4843.1562 | 122.2 | -0.09613 | 121.9711 | -0.17372 | -0.040894 | -0.0016812 | 0.0208 | -0.0021277 | -0.0092478 | -0.0040823 | -0.031403 | 0.033082 | 0.074317 | 0.057309 | -0.017942 | 0.039798 | 0.0087329 | -0.13733 | -0.054932 | -0.059509 | -0.068665 | 0.041199 | -0.09613 | 0.018311 | 35.1562 | 121.9757 | -0.11444 | 121.8155 | 9.3704 | 2.092 | 2.0645 | 0.036621 | -122.0261 | -122.0398 | 0.13733 | 0.11444 | 0 | 0.07782 | -0.036621 | -0.018311 | 0.004578 | -0.15564 | 9.4666 | 2.1606 | 2.1881 | 2.179 | 2.2064 | 0.10071 | -0.009156 | 9.4849 | 121.9299 | 0.004577 | 122.0901 | 0.041198 | 122.0718 | -122.0306 | -122.0856 | 0.027465 | 121.9116 | -0.041199 | 35.2524
4844.8594 | 122.1725 | -0.086975 | 122.0078 | -0.18898 | -0.042389 | 0.002164 | 0.0208 | -0.0010595 | -0.012239 | -0.0023733 | -0.04361 | 0.030946 | 0.074745 | 0.056881 | -0.017729 | 0.040012 | 0.0055285 | -0.09613 | -0.036621 | -0.059509 | -0.013733 | 0.086975 | -0.036621 | 0.045776 | 34.5337 | 121.9711 | -0.10986 | 121.8109 | 9.2468 | 2.0874 | 2.0737 | 0.027466 | -122.0444 | -122.0215 | 0.17395 | 0.13275 | 0.050354 | 0.10528 | 0.022888 | -0.022888 | -0.036621 | -0.19684 | 9.3338 | 2.1606 | 2.1744 | 2.1835 | 2.1973 | 0.14648 | 0.045776 | 9.3567 | 121.9208 | 0.022888 | 122.081 | 0.050354 | 122.0581 | -122.0673 | -122.1176 | 0.073242 | 121.8979 | -0.009155 | 34.6207
4846.625 | 122.2412 | -0.064087 | 121.9803 | -0.19661 | -0.04068 | 0.00066863 | 0.022082 | 0.0025721 | -0.010743 | -0.0051505 | -0.10464 | 0.0318 | 0.071754 | 0.058377 | -0.01901 | 0.039157 | 0.0038195 | -0.10529 | -0.054932 | -0.073242 | -0.036621 | 0.068665 | -0.073242 | 0.036621 | 34.4696 | 121.9757 | -0.07782 | 121.8704 | 9.3567 | 2.1103 | 2.1744 | -0.009155 | -122.0352 | -122.0169 | 0.13275 | 0.10071 | -0.009155 | 0.10986 | 0 | -0.013733 | -0.004578 | -0.10986 | 9.4208 | 2.2385 | 2.1744 | 2.2522 | 2.1881 | 0.14191 | 0.036621 | 9.4345 | 121.9482 | 0.01831 | 122.0535 | 0.009155 | 122.0398 | -122.0535 | -122.0581 | 0.027466 | 121.9345 | -0.041199 | 34.5337
4848.3906 | 122.2458 | -0.07782 | 122.0078 | -0.10506 | -0.044953 | 0.00066863 | 0.017382 | 0.00022207 | -0.010102 | -0.0053641 | -0.031403 | 0.033082 | 0.073463 | 0.0509 | -0.018156 | 0.040439 | 0.0044605 | -0.086975 | -0.050354 | -0.045776 | 0.018311 | 0.15564 | 0 | 0.10529 | 34.5383 | 121.9711 | -0.11444 | 121.875 | 9.3842 | 2.2156 | 2.211 | 0.032044 | -122.0581 | -121.9894 | 0.23346 | 0.18311 | 0.07782 | 0.15106 | 0.045776 | -0.036621 | -0.036621 | -0.13275 | 9.462 | 2.2888 | 2.2934 | 2.3254 | 2.33 | 0.20142 | 0.064087 | 9.4986 | 121.9894 | -0.004578 | 122.0856 | 0.027466 | 122.049 | -122.0535 | -122.1222 | 0.096131 | 121.9528 | -0.009155 | 34.6161
4850.1562 | 122.1588 | -0.09613 | 122.0444 | -0.17372 | -0.041321 | 0.00045503 | 0.021228 | 0.0027857 | -0.010743 | -0.0075003 | -0.12601 | 0.033295 | 0.072822 | 0.068417 | -0.017942 | 0.040225 | 0.012151 | -0.1236 | -0.013733 | -0.091553 | -0.054932 | 0.045776 | -0.10986 | -0.013733 | 34.4376 | 122.0215 | -0.11444 | 121.8155 | 9.3933 | 2.1011 | 2.1194 | 0.004577 | -122.0581 | -122.0993 | 0.14191 | 0.082397 | -0.013733 | 0.07782 | -0.01831 | -0.018311 | -0.022889 | -0.22888 | 9.4894 | 2.2156 | 2.1973 | 2.2339 | 2.2156 | 0.13733 | 0.036621 | 9.5078 | 121.9299 | 0.07782 | 122.1359 | 0.082397 | 122.1176 | -122.1359 | -122.1588 | 0.041198 | 121.9116 | -0.027466 | 34.5337
4851.8594 | 122.1634 | -0.1236 | 122.0398 | -0.1432 | -0.042603 | 0.00066863 | 0.021655 | -0.0014867 | -0.01352 | -0.0042959 | -0.10159 | 0.033295 | 0.07389 | 0.06094 | -0.022428 | 0.041507 | 0.0089465 | -0.15564 | 0.009155 | -0.10529 | -0.1236 | -0.041199 | -0.1236 | -0.045776 | 34.4559 | 122.0215 | -0.13275 | 121.7651 | 9.4574 | 2.092 | 2.1103 | 0.01831 | -122.0306 | -122.1634 | 0.082397 | 0.07782 | 0 | 0.05951 | -0.01831 | -0.009155 | -0.018311 | -0.27466 | 9.581 | 2.2339 | 2.2156 | 2.243 | 2.2247 | 0.064087 | -0.01831 | 9.5901 | 121.8979 | 0.11444 | 122.1542 | 0.13275 | 122.1451 | -122.1451 | -122.1725 | 0 | 121.8887 | -0.032044 | 34.5795
4853.625 | 122.1497 | -0.10071 | 122.0215 | -0.1432 | -0.038758 | 0.001523 | 0.022937 | -0.0012731 | -0.01053 | -0.0064321 | -0.11685 | 0.033723 | 0.075599 | 0.057736 | -0.018797 | 0.041721 | 0.010869 | -0.15564 | 0 | -0.09613 | -0.14191 | -0.050354 | -0.16937 | -0.045776 | 34.4147 | 122.0078 | -0.13275 | 121.7789 | 9.5947 | 2.1103 | 2.1423 | 0.004578 | -122.0215 | -122.1634 | 0.050354 | 0.054932 | -0.068665 | 0.050354 | -0.073243 | -0.032043 | -0.013733 | -0.24261 | 9.6954 | 2.243 | 2.211 | 2.2751 | 2.243 | 0.045776 | -0.045777 | 9.7275 | 121.9116 | 0.09613 | 122.1405 | 0.10071 | 122.1085 | -122.1176 | -122.1542 | -0.041199 | 121.8796 | -0.054932 | 34.5154
4855.3438 | 122.2092 | -0.07782 | 122.0306 | -0.18135 | -0.040253 | 0.002164 | 0.02016 | -0.0012731 | -0.01053 | -0.0042959 | -0.055817 | 0.032868 | 0.072608 | 0.052609 | -0.018797 | 0.040012 | 0.0080921 | -0.09613 | -0.045776 | -0.036621 | -0.004578 | 0.11902 | -0.059509 | 0.059509 | 34.639 | 121.9711 | -0.09613 | 121.8658 | 9.8007 | 2.2568 | 2.2751 | 0.041199 | -122.0764 | -122.0352 | 0.19684 | 0.13733 | 0.018311 | 0.09613 | -0.022888 | -0.01831 | -0.05951 | -0.1648 | 9.8785 | 2.3529 | 2.3346 | 2.3712 | 2.3529 | 0.15564 | 0.032043 | 9.8969 | 121.962 | -0.009155 | 122.0673 | 0.032044 | 122.049 | -122.0673 | -122.1268 | 0.073242 | 121.9437 | -0.01831 | 34.7168
4857.125 | 122.1268 | -0.1236 | 122.0215 | -0.1432 | -0.03833 | 0.0019504 | 0.022723 | -0.0023413 | -0.011598 | -0.0055777 | -0.12296 | 0.034363 | 0.075172 | 0.06329 | -0.018369 | 0.043002 | 0.0070239 | -0.13275 | -0.018311 | -0.068665 | -0.082397 | 0.022888 | -0.1236 | -0.027466 | 34.584 | 122.0215 | -0.11902 | 121.7926 | 9.7687 | 2.1469 | 2.1881 | 0.054931 | -122.0398 | -122.1039 | 0.14648 | 0.09613 | 0 | 0.041199 | -0.054931 | 0.004577 | 0 | -0.22888 | 9.8923 | 2.3117 | 2.2705 | 2.3071 | 2.2659 | 0.091553 | -0.013732 | 9.8877 | 121.9116 | 0.050354 | 122.1405 | 0.10528 | 122.1451 | -122.0901 | -122.1405 | 0.041199 | 121.9162 | -0.009155 | 34.7076
4858.8281 | 122.1222 | -0.11902 | 122.0444 | -0.17372 | -0.041962 | 0.001523 | 0.022296 | -0.0031957 | -0.011384 | -0.0066457 | -0.13516 | 0.033295 | 0.07389 | 0.059445 | -0.018369 | 0.040866 | 0.0087329 | -0.16479 | -0.018311 | -0.082397 | -0.11444 | -0.041199 | -0.17395 | -0.064087 | 34.4879 | 122.0352 | -0.1236 | 121.756 | 9.8328 | 2.1469 | 2.1835 | 0.036622 | -122.0627 | -122.1588 | 0.07782 | 0.054932 | -0.054931 | 0.01831 | -0.091553 | -0.004577 | -0.009156 | -0.28839 | 9.9518 | 2.3026 | 2.2659 | 2.3071 | 2.2705 | 0.041198 | -0.032044 | 9.9564 | 121.8796 | 0.064086 | 122.1588 | 0.10071 | 122.1542 | -122.1268 | -122.168 | 0.004578 | 121.875 | -0.045776 | 34.6069
4860.5938 | 122.1085 | -0.10986 | 122.0627 | -0.16609 | -0.042176 | 0.0034456 | 0.022937 | 0.0034265 | -0.012452 | -0.0055777 | -0.12906 | 0.034791 | 0.074317 | 0.062222 | -0.019224 | 0.04108 | 0.010228 | -0.15106 | -0.004578 | -0.068665 | -0.11902 | -0.050354 | -0.18768 | -0.059509 | 34.5932 | 122.049 | -0.14648 | 121.7743 | 10.0021 | 2.1286 | 2.2247 | 0.041198 | -122.0673 | -122.1817 | 0.059509 | 0.050354 | -0.07782 | 0.009156 | -0.11902 | -0.036621 | -0.013733 | -0.28839 | 10.112 | 2.3346 | 2.2385 | 2.3712 | 2.2751 | 0.018311 | -0.050354 | 10.1486 | 121.9208 | 0.064087 | 122.1954 | 0.10529 | 122.1588 | -122.1313 | -122.2092 | -0.009156 | 121.8842 | -0.041199 | 34.7031
4862.3594 | 122.2458 | -0.073242 | 121.9894 | -0.20424 | -0.04068 | 0.0025912 | 0.019946 | 0.0025721 | -0.010957 | -0.0034415 | -0.034454 | 0.03415 | 0.07624 | 0.058163 | -0.01901 | 0.040225 | 0.011296 | -0.07782 | -0.054932 | -0.036621 | 0 | 0.11902 | -0.041199 | 0.045776 | 34.7351 | 122.0078 | -0.091553 | 121.8842 | 10.144 | 2.3895 | 2.417 | 0.036621 | -122.0444 | -121.9894 | 0.19226 | 0.11902 | 0.032043 | 0.082397 | -0.004578 | -0.018311 | 0.01831 | -0.10529 | 10.2173 | 2.4902 | 2.4628 | 2.5085 | 2.4811 | 0.15564 | 0.036621 | 10.2356 | 121.9757 | -0.018311 | 122.0993 | 0.01831 | 122.081 | -122.0261 | -122.081 | 0.073242 | 121.9574 | -0.004578 | 34.8083
4864.0781 | 122.2366 | -0.091553 | 122.0261 | -0.17372 | -0.043885 | 0.00024143 | 0.019305 | 8.47e-06 | -0.011811 | -0.0055777 | -0.022247 | 0.034363 | 0.076026 | 0.061795 | -0.018156 | 0.042575 | 0.010228 | -0.15106 | -0.036621 | -0.073242 | -0.050354 | 0.050354 | -0.082397 | 0.032043 | 34.7214 | 121.9894 | -0.10071 | 121.8521 | 10.2173 | 2.3575 | 2.3483 | 0.018311 | -122.0627 | -122.0764 | 0.14191 | 0.1236 | 0.009156 | 0.10529 | -0.009155 | -0.009155 | -0.036621 | -0.17395 | 10.3088 | 2.4399 | 2.449 | 2.449 | 2.4582 | 0.1236 | 0.022888 | 10.318 | 121.9528 | 0.036621 | 122.0901 | 0.054932 | 122.081 | -122.0993 | -122.1268 | 0.041199 | 121.9437 | -0.059509 | 34.8129
4865.8438 | 122.1497 | -0.10071 | 122.0764 | -0.20424 | -0.039612 | 0.0013094 | 0.023578 | 0.00064947 | -0.012666 | -0.0053641 | -0.1138 | 0.0365 | 0.075172 | 0.06799 | -0.020078 | 0.041721 | 0.011296 | -0.15564 | -0.022888 | -0.07782 | -0.14191 | -0.050354 | -0.17395 | -0.068665 | 34.671 | 122.0123 | -0.14648 | 121.7926 | 10.231 | 2.2156 | 2.3483 | 0.022888 | -122.0993 | -122.2183 | 0.050354 | 0.032043 | -0.073242 | 0.009155 | -0.09613 | -0.045776 | -0.064087 | -0.28381 | 10.3317 | 2.449 | 2.3163 | 2.4948 | 2.3621 | 0.027466 | -0.064087 | 10.3775 | 121.9391 | 0.054932 | 122.1588 | 0.07782 | 122.113 | -122.1542 | -122.2229 | -0.041199 | 121.8933 | -0.054932 | 34.7717
4867.6094 | 122.2458 | -0.068665 | 122.0444 | -0.17372 | -0.044953 | 0.00066863 | 0.019732 | -0.0023413 | -0.012025 | -0.0047231 | -0.025299 | 0.035004 | 0.074958 | 0.055173 | -0.017515 | 0.039798 | 0.012364 | -0.13733 | -0.036621 | -0.059509 | -0.059509 | 0.073242 | -0.059509 | 0.054932 | 34.8358 | 121.9894 | -0.09613 | 121.8796 | 10.4553 | 2.417 | 2.4582 | 0.009156 | -122.081 | -122.1039 | 0.14191 | 0.1236 | 0.009156 | 0.11444 | 0 | -0.027465 | -0.054932 | -0.16479 | 10.524 | 2.5269 | 2.4857 | 2.5543 | 2.5131 | 0.13275 | 0 | 10.5515 | 121.9757 | 0.022888 | 122.0856 | 0.032044 | 122.0581 | -122.1039 | -122.1405 | 0.009156 | 121.9482 | -0.068664 | 34.9045
4869.3281 | 122.2275 | -0.068665 | 122.0032 | -0.1432 | -0.041107 | 0.0017368 | 0.019091 | -0.00084593 | -0.012452 | -0.0051505 | -0.06192 | 0.035218 | 0.073463 | 0.05795 | -0.021147 | 0.040866 | 0.0089465 | -0.09613 | -0.050354 | -0.041199 | -0.004578 | 0.10071 | -0.050354 | 0.054932 | 34.9182 | 121.9803 | -0.10071 | 121.8796 | 10.524 | 2.4307 | 2.4719 | 0.027466 | -122.0535 | -122.0078 | 0.16937 | 0.1236 | 0.018311 | 0.096131 | -0.009155 | -0.032043 | -0.022888 | -0.1236 | 10.5927 | 2.5406 | 2.4994 | 2.5726 | 2.5314 | 0.14191 | 0.036621 | 10.6247 | 121.9803 | -0.009155 | 122.081 | 0.018311 | 122.049 | -122.0444 | -122.1039 | 0.064087 | 121.9482 | -0.027465 | 34.9869
4871.0938 | 122.1817 | -0.10071 | 122.0764 | -0.12032 | -0.041748 | 0.00024143 | 0.0208 | 0.0012903 | -0.01117 | -0.0038687 | -0.14737 | 0.037568 | 0.075813 | 0.06564 | -0.020719 | 0.043002 | 0.013005 | -0.11444 | -0.036621 | -0.073242 | -0.050354 | 0.032043 | -0.10071 | -0.004578 | 34.8816 | 122.0215 | -0.10986 | 121.8155 | 10.5286 | 2.4124 | 2.4307 | 0.027466 | -122.113 | -122.1268 | 0.13275 | 0.09613 | 0 | 0.068664 | -0.027466 | -0.009155 | -0.054932 | -0.26093 | 10.6293 | 2.5314 | 2.5131 | 2.5406 | 2.5223 | 0.10529 | 0.022888 | 10.6384 | 121.9254 | 0.036621 | 122.1313 | 0.064087 | 122.1222 | -122.1497 | -122.1863 | 0.050354 | 121.9162 | -0.013733 | 34.9823
4872.7969 | 122.1725 | -0.11444 | 122.049 | -0.1432 | -0.041107 | 0.0017368 | 0.022082 | 0.0034265 | -0.012666 | -0.0047231 | -0.1199 | 0.037995 | 0.07624 | 0.062222 | -0.020506 | 0.040012 | 0.014073 | -0.1236 | -0.004578 | -0.082397 | -0.086975 | 0.013733 | -0.11444 | -0.009155 | 34.8633 | 122.0261 | -0.10986 | 121.8384 | 10.6155 | 2.3895 | 2.449 | 0.032044 | -122.0535 | -122.1359 | 0.12817 | 0.10529 | 0 | 0.073242 | -0.032044 | 0.004578 | -0.022888 | -0.21057 | 10.73 | 2.5635 | 2.504 | 2.5589 | 2.4994 | 0.09613 | -0.004578 | 10.7254 | 121.9482 | 0.077819 | 122.1359 | 0.10986 | 122.1405 | -122.1313 | -122.1588 | 0.027466 | 121.9528 | -0.009155 | 34.9777
4874.5781 | 122.2641 | -0.091553 | 122.0078 | -0.18898 | -0.042176 | 0.001523 | 0.019519 | -0.0023413 | -0.011598 | -0.0030141 | -0.0039367 | 0.036927 | 0.074745 | 0.062649 | -0.017942 | 0.041507 | 0.011083 | -0.14648 | -0.045776 | -0.050354 | -0.054932 | 0.068665 | -0.059509 | 0.045776 | 34.8999 | 122.0123 | -0.11444 | 121.8842 | 10.8398 | 2.5269 | 2.5452 | 0.041199 | -122.0535 | -122.0627 | 0.16022 | 0.13733 | 0.032044 | 0.09613 | -0.009155 | -0.022888 | 0.004578 | -0.1236 | 10.9314 | 2.6367 | 2.6184 | 2.6596 | 2.6413 | 0.11902 | -0.004578 | 10.9543 | 121.9986 | 0.004578 | 122.1268 | 0.045777 | 122.1039 | -122.0581 | -122.1222 | 0.036621 | 121.9757 | -0.054931 | 34.9915
4876.3438 | 122.2275 | -0.082397 | 121.9986 | -0.21187 | -0.04068 | 0.00066863 | 0.0208 | -0.0012731 | -0.009675 | -0.0049367 | -0.055817 | 0.037141 | 0.078376 | 0.066922 | -0.017515 | 0.042789 | 0.011724 | -0.086975 | -0.041199 | -0.050354 | -0.009155 | 0.10986 | -0.059509 | 0.054932 | 35.0647 | 121.9666 | -0.09613 | 121.8933 | 10.9543 | 2.536 | 2.5726 | 0.032043 | -122.0398 | -122.0078 | 0.19226 | 0.13733 | 0.022888 | 0.10529 | -0.009155 | -0.013733 | -0.032043 | -0.10529 | 11.0367 | 2.655 | 2.6184 | 2.6688 | 2.6321 | 0.16022 | 0.041199 | 11.0504 | 121.9894 | 0.009155 | 122.0627 | 0.041198 | 122.049 | -122.049 | -122.0947 | 0.073242 | 121.9757 | -0.004578 | 35.1471
4878.1094 | 122.2229 | -0.09613 | 122.049 | -0.17372 | -0.042603 | 0.00088223 | 0.021228 | -0.0012731 | -0.012879 | -0.0062185 | -0.068024 | 0.037141 | 0.076454 | 0.067563 | -0.019438 | 0.043857 | 0.010655 | -0.10071 | -0.050354 | -0.054932 | -0.018311 | 0.09613 | -0.018311 | 0.064087 | 35.0555 | 122.0078 | -0.10071 | 121.8704 | 11.0367 | 2.5223 | 2.5085 | 0.041198 | -122.0993 | -122.0673 | 0.19226 | 0.16022 | 0.077819 | 0.11902 | 0.036621 | -0.004578 | -0.041199 | -0.17853 | 11.1328 | 2.6047 | 2.6184 | 2.6093 | 2.623 | 0.15106 | 0.036621 | 11.1374 | 121.9711 | 0.004578 | 122.1085 | 0.045776 | 122.1039 | -122.1039 | -122.1497 | 0.077819 | 121.9666 | -0.004578 | 35.1517
4879.8125 | 122.2229 | -0.10986 | 122.0306 | -0.16609 | -0.043244 | 2.7834e-05 | 0.019946 | -0.0027685 | -0.010743 | -0.0055777 | -0.058869 | 0.039063 | 0.077522 | 0.060513 | -0.017942 | 0.04108 | 0.012151 | -0.11444 | -0.045776 | -0.054932 | -0.032043 | 0.10071 | -0.027466 | 0.064087 | 35.0601 | 122.0352 | -0.10071 | 121.8475 | 11.1191 | 2.5314 | 2.5818 | 0.054931 | -122.0764 | -122.0627 | 0.21057 | 0.17395 | 0.082397 | 0.11902 | 0.027466 | 0.009155 | 0.004577 | -0.18311 | 11.2289 | 2.6916 | 2.6413 | 2.6825 | 2.6321 | 0.15564 | 0.022889 | 11.2198 | 121.9482 | 0.009156 | 122.1359 | 0.064087 | 122.1451 | -122.0856 | -122.1313 | 0.07782 | 121.9574 | -0.004578 | 35.17
4881.5781 | 122.1863 | -0.091553 | 122.0535 | -0.18898 | -0.039398 | 0.00024143 | 0.022082 | 0.0034265 | -0.011811 | -0.0025869 | -0.12296 | 0.038636 | 0.075813 | 0.065426 | -0.020078 | 0.041507 | 0.0074511 | -0.11902 | -0.022888 | -0.082397 | -0.054932 | 0.027466 | -0.10986 | -0.004578 | 35.0464 | 122.0444 | -0.14191 | 121.8384 | 11.2061 | 2.4811 | 2.5589 | 0.009156 | -122.0764 | -122.1085 | 0.11902 | 0.086975 | -0.01831 | 0.077819 | -0.027466 | -0.050354 | -0.009155 | -0.21515 | 11.2976 | 2.6505 | 2.5726 | 2.7008 | 2.623 | 0.10986 | 0.027465 | 11.348 | 121.9803 | 0.059509 | 122.1863 | 0.068665 | 122.1359 | -122.1359 | -122.1954 | 0.036621 | 121.9299 | -0.027466 | 35.1379
4883.3281 | 122.2458 | -0.09613 | 122.0261 | -0.2195 | -0.042176 | 0.00024143 | 0.020373 | 0.00043587 | -0.01117 | -0.0019461 | -0.1077 | 0.040772 | 0.076881 | 0.060086 | -0.021574 | 0.044284 | 0.0091601 | -0.16479 | -0.022888 | -0.091553 | -0.10071 | 0.013733 | -0.15106 | -0.027466 | 35.0739 | 121.9803 | -0.10986 | 121.8979 | 11.3022 | 2.5497 | 2.5589 | 0.004577 | -122.0489 | -122.1268 | 0.10986 | 0.068664 | -0.054932 | 0.064087 | -0.059509 | -0.013733 | -0.045776 | -0.12817 | 11.3983 | 2.655 | 2.6459 | 2.6688 | 2.6596 | 0.10529 | -0.009155 | 11.412 | 122.0078 | 0.068665 | 122.0901 | 0.073242 | 122.0764 | -122.1176 | -122.1359 | -0.004578 | 121.994 | -0.068665 | 35.17
4885.0469 | 122.2275 | -0.068665 | 122.0352 | -0.15083 | -0.042603 | -0.00082677 | 0.02016 | -0.0036231 | -0.01117 | -0.0057913 | -0.06192 | 0.040131 | 0.077949 | 0.061581 | -0.01901 | 0.041934 | 0.010869 | -0.15106 | -0.050354 | -0.059509 | -0.045776 | 0.059509 | -0.091553 | 0.032043 | 35.0647 | 121.9986 | -0.10529 | 121.8567 | 11.4075 | 2.5772 | 2.623 | 0.009156 | -122.0856 | -122.081 | 0.12817 | 0.10071 | -0.022888 | 0.091552 | -0.032044 | -0.036621 | -0.036621 | -0.17853 | 11.4761 | 2.6917 | 2.6459 | 2.7283 | 2.6825 | 0.11902 | 0.013733 | 11.5128 | 121.962 | 0.009155 | 122.1039 | 0.018311 | 122.0673 | -122.0947 | -122.1405 | 0.022889 | 121.9254 | -0.082397 | 35.1334
4886.8125 | 122.2 | -0.11902 | 122.0764 | -0.11269 | -0.041535 | 0.00024143 | 0.022937 | 0.0012903 | -0.011598 | -0.0049367 | -0.12906 | 0.03949 | 0.077949 | 0.063717 | -0.018583 | 0.043002 | 0.0091601 | -0.10986 | -0.004578 | -0.086975 | -0.064087 | 0.027466 | -0.10071 | -0.013733 | 35.1334 | 122.0444 | -0.10529 | 121.8384 | 11.5311 | 2.5543 | 2.6779 | 0.032044 | -122.081 | -122.1405 | 0.14649 | 0.10529 | 0.018311 | 0.073242 | -0.013733 | 0.013733 | -0.032043 | -0.23804 | 11.6501 | 2.7969 | 2.6733 | 2.7832 | 2.6596 | 0.11444 | 0.022888 | 11.6364 | 121.9437 | 0.082397 | 122.1497 | 0.11444 | 122.1634 | -122.1634 | -122.1817 | 0.054932 | 121.9574 | 0.009156 | 35.2524
4888.5781 | 122.1542 | -0.11444 | 122.0718 | -0.097427 | -0.043671 | 2.7834e-05 | 0.018878 | -0.00020513 | -0.010743 | -0.0032277 | -0.09549 | 0.040131 | 0.07859 | 0.059872 | -0.017515 | 0.041293 | 0.011724 | -0.16479 | -0.013733 | -0.09613 | -0.13275 | -0.032043 | -0.15564 | -0.050354 | 35.0693 | 122.0398 | -0.14648 | 121.7926 | 11.5631 | 2.5269 | 2.5681 | 0.018311 | -122.0856 | -122.2046 | 0.082398 | 0.064087 | -0.041199 | 0.045776 | -0.05951 | -0.032043 | -0.032043 | -0.27923 | 11.6776 | 2.6825 | 2.6413 | 2.7145 | 2.6733 | 0.064087 | -0.036621 | 11.7096 | 121.9391 | 0.082397 | 122.1863 | 0.10071 | 122.1542 | -122.168 | -122.2183 | -0.01831 | 121.907 | -0.050354 | 35.1837
4890.2812 | 122.168 | -0.12817 | 122.0535 | -0.10506 | -0.042603 | -0.00061317 | 0.021228 | -0.0029821 | -0.010316 | -0.0028005 | -0.10159 | 0.039277 | 0.077094 | 0.064358 | -0.01901 | 0.04343 | 0.010655 | -0.16937 | -0.018311 | -0.091553 | -0.12817 | -0.036621 | -0.14191 | -0.050354 | 35.1746 | 122.0352 | -0.14191 | 121.7789 | 11.6501 | 2.5497 | 2.6093 | 0.036621 | -122.0718 | -122.1817 | 0.091553 | 0.07782 | -0.013733 | 0.041199 | -0.050354 | -0.013733 | -0.018311 | -0.27466 | 11.7783 | 2.7374 | 2.6779 | 2.7512 | 2.6917 | 0.054932 | -0.036621 | 11.792 | 121.9208 | 0.073242 | 122.1771 | 0.10986 | 122.1634 | -122.1451 | -122.1954 | 0 | 121.907 | -0.041199 | 35.3027
4892.0469 | 122.2641 | -0.064087 | 122.0169 | -0.21187 | -0.037262 | 0.0023776 | 0.0208 | -0.0029821 | -0.0092478 | -0.0042959 | -0.10159 | 0.039063 | 0.076667 | 0.059445 | -0.019865 | 0.041934 | 0.0098011 | -0.059509 | -0.068665 | -0.054932 | 0 | 0.10986 | -0.064087 | 0.045776 | 35.3943 | 121.994 | -0.073242 | 121.9299 | 11.7966 | 2.7054 | 2.6047 | 0.009155 | -122.0856 | -122.0169 | 0.17395 | 0.10986 | 0 | 0.10071 | -0.009155 | -0.009155 | -0.022888 | -0.086975 | 11.8607 | 2.6688 | 2.7695 | 2.6779 | 2.7786 | 0.16479 | 0.054932 | 11.8698 | 122.0032 | -0.013733 | 122.0673 | -0.004578 | 122.0581 | -122.0718 | -122.0901 | 0.064087 | 121.994 | 0.004578 | 35.4584
4893.75 | 122.1588 | -0.1236 | 122.0718 | -0.089798 | -0.042389 | -0.00039957 | 0.021655 | 0.0021447 | -0.012666 | -0.0023733 | -0.068024 | 0.04184 | 0.077949 | 0.063504 | -0.019438 | 0.042789 | 0.012792 | -0.17853 | 0.009155 | -0.09613 | -0.1236 | -0.041199 | -0.14648 | -0.045776 | 35.2707 | 122.0306 | -0.13275 | 121.7926 | 11.8011 | 2.5955 | 2.6505 | 0.027466 | -122.0627 | -122.1954 | 0.082397 | 0.07782 | -0.022888 | 0.050354 | -0.050354 | -0.009155 | -0.041198 | -0.27923 | 11.9247 | 2.774 | 2.7191 | 2.7832 | 2.7283 | 0.054931 | -0.027466 | 11.9339 | 121.9254 | 0.10528 | 122.1634 | 0.13275 | 122.1542 | -122.168 | -122.2046 | 0 | 121.9162 | -0.054932 | 35.3943
4895.5312 | 122.1497 | -0.13275 | 122.0673 | -0.082169 | -0.044312 | -0.00061317 | 0.019946 | 0.00064947 | -0.011811 | -0.0060049 | -0.080231 | 0.040131 | 0.079872 | 0.060513 | -0.01901 | 0.043216 | 0.013646 | -0.17395 | -0.009155 | -0.09613 | -0.12817 | -0.022888 | -0.1236 | -0.036621 | 35.3165 | 122.049 | -0.1236 | 121.788 | 11.7783 | 2.6047 | 2.6871 | 0.036621 | -122.0764 | -122.1954 | 0.10986 | 0.09613 | 0.009155 | 0.059509 | -0.027466 | 0.009155 | -0.018311 | -0.27924 | 11.911 | 2.8198 | 2.7374 | 2.8107 | 2.7283 | 0.073242 | -0.032044 | 11.9019 | 121.9116 | 0.086975 | 122.1725 | 0.1236 | 122.1817 | -122.1634 | -122.1909 | 0.004577 | 121.9208 | -0.041199 | 35.4492
4897.2969 | 122.1542 | -0.11444 | 122.0581 | -0.15083 | -0.041535 | -0.00082677 | 0.021441 | -0.0040503 | -0.015016 | -0.0030141 | -0.083283 | 0.041413 | 0.07859 | 0.060086 | -0.017729 | 0.043002 | 0.012151 | -0.16479 | -0.009155 | -0.09613 | -0.13275 | -0.013733 | -0.14191 | -0.032043 | 35.3485 | 122.0535 | -0.14648 | 121.7834 | 11.879 | 2.6367 | 2.7008 | 0.018311 | -122.0673 | -122.1909 | 0.10071 | 0.082398 | -0.027466 | 0.064087 | -0.045777 | -0.032043 | -0.004577 | -0.27466 | 11.9934 | 2.8152 | 2.7512 | 2.8473 | 2.7832 | 0.082397 | -0.036621 | 12.0255 | 121.9299 | 0.086975 | 122.2 | 0.10529 | 122.168 | -122.1542 | -122.2046 | -0.01831 | 121.8979 | -0.050354 | 35.463
4899.0625 | 122.1588 | -0.13733 | 122.0856 | -0.16609 | -0.039185 | 0.00066863 | 0.021441 | 0.0019311 | -0.0092478 | -0.0049367 | -0.12296 | 0.042908 | 0.078376 | 0.07034 | -0.017942 | 0.04407 | 0.016851 | -0.14191 | 0 | -0.10986 | -0.14648 | -0.059509 | -0.19226 | -0.064087 | 35.3806 | 122.0398 | -0.13275 | 121.8018 | 11.9751 | 2.6184 | 2.7054 | 0.027466 | -122.0856 | -122.2321 | 0.07782 | 0.073242 | -0.054932 | 0.045776 | -0.082398 | 0.004578 | -0.045776 | -0.28381 | 12.1124 | 2.8427 | 2.7557 | 2.8381 | 2.7512 | 0.050354 | -0.036621 | 12.1078 | 121.9345 | 0.10986 | 122.1725 | 0.13733 | 122.1771 | -122.1954 | -122.2183 | -0.009155 | 121.9391 | -0.004578 | 35.5179
4900.8281 | 122.1771 | -0.11444 | 122.0535 | -0.10506 | -0.042603 | -0.00018577 | 0.020587 | -0.00041873 | -0.013307 | -0.0060049 | -0.10464 | 0.044404 | 0.080085 | 0.064358 | -0.018797 | 0.043216 | 0.0085193 | -0.15564 | 0.009155 | -0.07782 | -0.11902 | -0.027466 | -0.13275 | -0.041199 | 35.3256 | 122.0261 | -0.14648 | 121.7972 | 11.9339 | 2.6871 | 2.7328 | 0.036621 | -122.0444 | -122.1725 | 0.086975 | 0.073242 | -0.01831 | 0.036621 | -0.054931 | -0.032043 | -0.027466 | -0.25635 | 12.0483 | 2.8473 | 2.8015 | 2.8793 | 2.8336 | 0.050354 | -0.041199 | 12.0804 | 121.9437 | 0.086975 | 122.1725 | 0.1236 | 122.1405 | -122.1313 | -122.2 | -0.004578 | 121.9116 | -0.041199 | 35.4401
4902.5938 | 122.2412 | -0.073242 | 122.049 | -0.22713 | -0.042816 | 0.0013094 | 0.019519 | -0.0017005 | -0.012239 | -0.0040823 | -0.034454 | 0.04184 | 0.079444 | 0.062649 | -0.019224 | 0.043643 | 0.012151 | -0.14191 | -0.045776 | -0.054932 | -0.050354 | 0.073242 | -0.091553 | 0.018311 | 35.5865 | 122.0078 | -0.10071 | 121.8704 | 12.0712 | 2.8336 | 2.8198 | 0.01831 | -122.0947 | -122.0993 | 0.14648 | 0.091553 | -0.018311 | 0.073243 | -0.036621 | -0.027466 | -0.041199 | -0.17853 | 12.1445 | 2.8931 | 2.9068 | 2.9205 | 2.9343 | 0.12817 | 0.004578 | 12.1719 | 121.9711 | 0.009156 | 122.1085 | 0.027466 | 122.081 | -122.1039 | -122.1497 | 0.022888 | 121.9437 | -0.068665 | 35.6598
4904.3125 | 122.2412 | -0.064087 | 122.0215 | -0.18898 | -0.041107 | 0.00066863 | 0.018664 | -0.00063233 | -0.012879 | -0.0040823 | -0.037506 | 0.041627 | 0.077949 | 0.066708 | -0.019224 | 0.043643 | 0.012578 | -0.13733 | -0.041199 | -0.073242 | -0.045776 | 0.054932 | -0.091553 | 0.022888 | 35.5499 | 121.9986 | -0.11902 | 121.8658 | 12.1399 | 2.8336 | 2.8885 | -0.009155 | -122.0627 | -122.0673 | 0.11902 | 0.086975 | -0.027466 | 0.09613 | -0.018311 | -0.054932 | -0.022888 | -0.15564 | 12.204 | 2.9526 | 2.8976 | 3.0075 | 2.9526 | 0.12817 | 0.027466 | 12.2589 | 121.9849 | 0.032043 | 122.1176 | 0.022888 | 122.0627 | -122.0947 | -122.1405 | 0.018311 | 121.9299 | -0.073242 | 35.614
4906.0781 | 122.287 | -0.064087 | 122.0398 | -0.16609 | -0.040467 | 0.0013094 | 0.021441 | 0.0027857 | -0.0094614 | -0.0038687 | -0.10464 | 0.043549 | 0.079444 | 0.065854 | -0.020292 | 0.04407 | 0.010015 | -0.10071 | -0.045776 | -0.045776 | -0.004578 | 0.091553 | -0.064087 | 0.041199 | 35.6644 | 121.9986 | -0.091553 | 121.9345 | 12.1902 | 2.8793 | 2.9709 | 0.018311 | -122.0856 | -122.0444 | 0.15564 | 0.10529 | 0 | 0.086975 | -0.018311 | -0.027466 | -0.041199 | -0.10529 | 12.2543 | 3.035 | 2.9434 | 3.0624 | 2.9709 | 0.13733 | 0.041198 | 12.2818 | 122.0261 | 0 | 122.0901 | 0.018311 | 122.0627 | -122.0856 | -122.1313 | 0.059509 | 121.9986 | -0.036621 | 35.7285
4907.8438 | 122.1634 | -0.13275 | 122.081 | -0.082169 | -0.041535 | 0.0030184 | 0.020373 | 0.00064947 | -0.01352 | -0.0021597 | -0.089386 | 0.044404 | 0.07859 | 0.064786 | -0.019438 | 0.044711 | 0.015782 | -0.17395 | 0 | -0.11444 | -0.14191 | -0.032043 | -0.13733 | -0.036621 | 35.5865 | 122.0398 | -0.13275 | 121.7926 | 12.1033 | 2.8107 | 2.7924 | 0.01831 | -122.081 | -122.2229 | 0.10071 | 0.09613 | -0.004578 | 0.07782 | -0.022888 | 0 | -0.041199 | -0.28839 | 12.236 | 2.9251 | 2.9434 | 2.9251 | 2.9434 | 0.082398 | -0.027466 | 12.236 | 121.9254 | 0.11444 | 122.1725 | 0.13275 | 122.1725 | -122.1954 | -122.2137 | -0.009156 | 121.9254 | -0.041199 | 35.7193
4909.625 | 122.2366 | -0.086975 | 122.0261 | -0.21187 | -0.042603 | 0.0010958 | 0.021869 | -0.0044775 | -0.010316 | -0.0040823 | -0.049713 | 0.042908 | 0.077522 | 0.064572 | -0.016447 | 0.043002 | 0.013433 | -0.13733 | -0.045776 | -0.064087 | -0.073242 | 0.022888 | -0.091553 | 0.013733 | 35.6827 | 122.0078 | -0.12817 | 121.8475 | 12.2223 | 2.8564 | 2.9388 | 0.022888 | -122.0718 | -122.0993 | 0.10986 | 0.10071 | -0.004578 | 0.07782 | -0.027466 | -0.041199 | -0.018311 | -0.17853 | 12.3093 | 3.0258 | 2.9434 | 3.067 | 2.9846 | 0.086975 | -0.009155 | 12.3505 | 121.9757 | 0.018311 | 122.1359 | 0.041199 | 122.0947 | -122.0901 | -122.1542 | 0.013733 | 121.9345 | -0.050354 | 35.7697
4911.3438 | 122.2549 | -0.068665 | 122.0123 | -0.25764 | -0.040253 | 0.0013094 | 0.019519 | -0.0014867 | -0.010743 | -0.0040823 | -0.083283 | 0.041199 | 0.076667 | 0.066708 | -0.019438 | 0.045352 | 0.015355 | -0.086975 | -0.054932 | -0.050354 | -0.022888 | 0.10986 | -0.054932 | 0.045776 | 35.7925 | 122.0078 | -0.10529 | 121.907 | 12.4649 | 2.948 | 3.0396 | 0.018311 | -122.0673 | -122.0352 | 0.17853 | 0.11444 | 0.013733 | 0.09613 | -0.004578 | -0.036621 | -0.004578 | -0.10529 | 12.5336 | 3.1082 | 3.0167 | 3.1448 | 3.0533 | 0.16022 | 0.027466 | 12.5702 | 122.0123 | -0.004578 | 122.113 | 0.013733 | 122.0764 | -122.0627 | -122.1176 | 0.045777 | 121.9757 | -0.01831 | 35.8612
4913.1094 | 122.1634 | -0.11444 | 122.0673 | -0.16609 | -0.039826 | 0.0013094 | 0.021014 | 0.0015039 | -0.009675 | -0.0051505 | -0.15652 | 0.042908 | 0.078376 | 0.063717 | -0.020506 | 0.042575 | 0.013005 | -0.13733 | -0.013733 | -0.091553 | -0.13275 | -0.064087 | -0.18768 | -0.07782 | 35.6689 | 122.049 | -0.11902 | 121.8201 | 12.4603 | 2.8427 | 2.9297 | 0.022888 | -122.081 | -122.2 | 0.050354 | 0.036621 | -0.073242 | 0.013733 | -0.09613 | -0.004578 | -0.018311 | -0.24719 | 12.5748 | 3.0441 | 2.9572 | 3.0487 | 2.9617 | 0.027466 | -0.041198 | 12.5793 | 121.9391 | 0.07782 | 122.168 | 0.10071 | 122.1634 | -122.1588 | -122.1863 | -0.01831 | 121.9345 | -0.022888 | 35.7834
4914.875 | 122.1817 | -0.10071 | 122.049 | -0.20424 | -0.040253 | 0.00045503 | 0.022937 | 0.0017175 | -0.0098886 | -0.0055777 | -0.14127 | 0.046326 | 0.081153 | 0.067563 | -0.01901 | 0.044498 | 0.017705 | -0.17395 | -0.009155 | -0.091553 | -0.13733 | -0.036621 | -0.18768 | -0.059509 | 35.7285 | 122.049 | -0.13733 | 121.8018 | 12.5244 | 2.8473 | 2.9572 | 0.009155 | -122.0581 | -122.1863 | 0.064087 | 0.041199 | -0.086975 | 0.032044 | -0.09613 | -0.036621 | 0 | -0.24719 | 12.6251 | 3.0579 | 2.948 | 3.0945 | 2.9846 | 0.054932 | -0.045776 | 12.6617 | 121.9391 | 0.082398 | 122.1863 | 0.091553 | 122.1497 | -122.1405 | -122.1863 | -0.036621 | 121.9025 | -0.073242 | 35.8292
4916.6562 | 122.2 | -0.11902 | 122.0856 | -0.1432 | -0.042176 | 0.0030184 | 0.020587 | 0.0032129 | -0.013947 | -0.0057913 | -0.12296 | 0.045899 | 0.079658 | 0.069058 | -0.019865 | 0.04343 | 0.01621 | -0.11444 | 0 | -0.07782 | -0.064087 | 0.036621 | -0.10529 | -0.004578 | 35.8109 | 122.0718 | -0.11444 | 121.8658 | 12.6389 | 2.9205 | 3.0533 | 0.041199 | -122.0856 | -122.1497 | 0.15564 | 0.11444 | 0.013733 | 0.073242 | -0.027466 | 0.004578 | -0.013733 | -0.21973 | 12.7579 | 3.1723 | 3.0396 | 3.1677 | 3.035 | 0.11444 | 0.013733 | 12.7533 | 121.9803 | 0.07782 | 122.1863 | 0.11902 | 122.1909 | -122.1634 | -122.2 | 0.054932 | 121.9849 | 0.004578 | 35.9299
4918.3594 | 122.2366 | -0.09613 | 122.0352 | -0.21187 | -0.041321 | 0.00088223 | 0.01781 | 0.00064947 | -0.013307 | -0.0066457 | -0.052765 | 0.042695 | 0.080299 | 0.065213 | -0.019438 | 0.045352 | 0.012151 | -0.13275 | -0.045776 | -0.050354 | -0.068665 | 0.050354 | -0.091553 | 0.022888 | 35.8109 | 122.0261 | -0.11902 | 121.8658 | 12.6801 | 2.98 | 3.1494 | 0.045776 | -122.081 | -122.1039 | 0.14648 | 0.11902 | 0.004577 | 0.073242 | -0.041199 | -0.022889 | -0.009155 | -0.16937 | 12.7762 | 3.2455 | 3.0762 | 3.2684 | 3.0991 | 0.10071 | -0.018311 | 12.7991 | 121.9849 | 0.004578 | 122.1451 | 0.050354 | 122.1222 | -122.0856 | -122.1542 | 0.027465 | 121.962 | -0.036621 | 35.907
4920.125 | 122.1405 | -0.12817 | 122.0673 | -0.2195 | -0.039398 | 0.00066863 | 0.022296 | 0.0019311 | -0.011811 | -0.0036551 | -0.15652 | 0.044404 | 0.079872 | 0.06564 | -0.018369 | 0.046848 | 0.01386 | -0.13733 | 0 | -0.10529 | -0.13733 | -0.064087 | -0.19684 | -0.073242 | 35.8063 | 122.0673 | -0.13275 | 121.8018 | 12.6709 | 2.8839 | 3.0396 | 0.022888 | -122.0673 | -122.2046 | 0.064087 | 0.054932 | -0.068664 | 0.032044 | -0.091552 | -0.004577 | 0 | -0.2655 | 12.7991 | 3.1677 | 3.0121 | 3.1723 | 3.0167 | 0.041199 | -0.032043 | 12.8036 | 121.9345 | 0.10529 | 122.2 | 0.12817 | 122.1954 | -122.1725 | -122.2 | -0.009155 | 121.9299 | -0.009155 | 35.9344
4921.8281 | 122.2321 | -0.073242 | 122.0444 | -0.20424 | -0.042603 | 0.00066863 | 0.018878 | -0.0046911 | -0.01117 | -0.0032277 | -0.055817 | 0.045258 | 0.081367 | 0.059445 | -0.018583 | 0.042789 | 0.016637 | -0.12817 | -0.045776 | -0.054932 | -0.064087 | 0.050354 | -0.07782 | 0.018311 | 35.9436 | 122.0261 | -0.091553 | 121.8704 | 12.8677 | 3.0167 | 3.1586 | 0.01831 | -122.0901 | -122.1085 | 0.1236 | 0.091553 | -0.004578 | 0.073243 | -0.022888 | -0.018311 | -0.018311 | -0.17395 | 12.941 | 3.2318 | 3.0899 | 3.2501 | 3.1082 | 0.10529 | -0.009155 | 12.9593 | 121.962 | 0.009156 | 122.1176 | 0.027466 | 122.0993 | -122.0993 | -122.1359 | 0.009155 | 121.9437 | -0.054932 | 36.0168
4923.5938 | 122.168 | -0.10529 | 122.0764 | -0.15846 | -0.040253 | -0.001254 | 0.022937 | 0.0021447 | -0.011811 | -0.0053641 | -0.16263 | 0.047394 | 0.078163 | 0.067135 | -0.01901 | 0.045352 | 0.014714 | -0.10986 | -0.009155 | -0.054932 | -0.073242 | 0.027466 | -0.11902 | -0.032043 | 35.8383 | 122.0398 | -0.10529 | 121.843 | 12.9593 | 2.9205 | 3.1219 | 0.050354 | -122.0856 | -122.1497 | 0.13275 | 0.073243 | -0.013733 | 0.022889 | -0.064087 | 0 | -0.036621 | -0.23346 | 13.0646 | 3.2272 | 3.0258 | 3.2272 | 3.0258 | 0.082398 | -0.01831 | 13.0646 | 121.9482 | 0.045777 | 122.1451 | 0.096131 | 122.1451 | -122.1313 | -122.1817 | 0.032044 | 121.9482 | -0.004577 | 35.9436
4925.3594 | 122.168 | -0.10529 | 122.0947 | -0.12032 | -0.041107 | 0.00045503 | 0.022296 | 0.0015039 | -0.011384 | -0.0055777 | -0.098541 | 0.047394 | 0.08094 | 0.070126 | -0.018369 | 0.046207 | 0.017278 | -0.15564 | -0.009155 | -0.10071 | -0.11902 | -0.027466 | -0.13733 | -0.036621 | 35.7971 | 122.0398 | -0.11902 | 121.8018 | 13.1378 | 2.916 | 3.0716 | 0.004578 | -122.1039 | -122.2137 | 0.07782 | 0.068665 | -0.032043 | 0.064087 | -0.036621 | -0.013733 | -0.054932 | -0.29297 | 13.2431 | 3.1769 | 3.0212 | 3.1906 | 3.035 | 0.073242 | -0.018311 | 13.2568 | 121.9208 | 0.091553 | 122.1588 | 0.096131 | 122.1451 | -122.1954 | -122.2137 | -0.013733 | 121.907 | -0.050354 | 35.9024
4927.0625 | 122.2641 | -0.07782 | 122.049 | -0.15846 | -0.044312 | 0.00066863 | 0.019091 | -0.00041873 | -0.013307 | -0.0057913 | -0.016144 | 0.04654 | 0.08094 | 0.051968 | -0.020506 | 0.043216 | 0.013005 | -0.082397 | -0.045776 | -0.050354 | -0.004578 | 0.11444 | -0.018311 | 0.068665 | 35.9436 | 122.0215 | -0.10071 | 121.907 | 13.266 | 3.1036 | 3.2181 | 0.027466 | -122.0947 | -122.0535 | 0.19226 | 0.14649 | 0.059509 | 0.11902 | 0.032043 | -0.022888 | -0.027466 | -0.14191 | 13.3438 | 3.2959 | 3.1815 | 3.3188 | 3.2043 | 0.16479 | 0.045776 | 13.3667 | 122.0078 | 0.004578 | 122.1222 | 0.032044 | 122.0993 | -122.0993 | -122.1497 | 0.073242 | 121.9849 | -0.004577 | 36.0214
4928.8281 | 122.1542 | -0.12817 | 122.0947 | -0.18135 | -0.039826 | 0.00066863 | 0.022082 | 0.0012903 | -0.010743 | -0.0057913 | -0.15958 | 0.047181 | 0.078803 | 0.060299 | -0.019651 | 0.04407 | 0.017064 | -0.16937 | 0.004578 | -0.10071 | -0.13733 | -0.036621 | -0.18768 | -0.059509 | 35.8017 | 122.0581 | -0.13275 | 121.8246 | 13.1287 | 2.916 | 3.154 | 0.027466 | -122.0901 | -122.2321 | 0.091553 | 0.068665 | -0.059509 | 0.041199 | -0.086975 | -0.004577 | -0.036622 | -0.27008 | 13.2568 | 3.2822 | 3.0441 | 3.2867 | 3.0487 | 0.064087 | -0.036621 | 13.2614 | 121.9574 | 0.10529 | 122.1909 | 0.13275 | 122.1863 | -122.1954 | -122.2275 | -0.009155 | 121.9528 | -0.041199 | 35.9299
4930.6094 | 122.2 | -0.13275 | 122.0901 | -0.089798 | -0.041748 | -0.001254 | 0.021869 | 0.0010767 | -0.012452 | -0.0045095 | -0.10464 | 0.046967 | 0.081367 | 0.065426 | -0.018156 | 0.045352 | 0.01151 | -0.17395 | 0 | -0.11902 | -0.13733 | -0.045776 | -0.13733 | -0.045776 | 35.8337 | 122.0718 | -0.11902 | 121.8201 | 13.2294 | 2.9755 | 3.2089 | 0.013732 | -122.0901 | -122.2275 | 0.086975 | 0.086975 | -0.004578 | 0.073243 | -0.01831 | 0.013732 | -0.018311 | -0.27008 | 13.3621 | 3.3417 | 3.1082 | 3.3279 | 3.0945 | 0.073243 | -0.01831 | 13.3484 | 121.9391 | 0.11902 | 122.1909 | 0.13275 | 122.2046 | -122.2092 | -122.2092 | -0.004578 | 121.9528 | -0.041199 | 35.9665
4932.375 | 122.2275 | -0.082397 | 122.0398 | -0.18898 | -0.041535 | 0.00088223 | 0.01781 | 8.47e-06 | -0.014802 | -0.0038687 | -0.028351 | 0.045258 | 0.079658 | 0.064358 | -0.016874 | 0.045139 | 0.015782 | -0.13275 | -0.032043 | -0.059509 | -0.054932 | 0.032043 | -0.091553 | 0.032043 | 35.9756 | 122.0123 | -0.09613 | 121.875 | 13.3575 | 3.0258 | 3.2867 | 0.022888 | -122.0718 | -122.0947 | 0.11444 | 0.11444 | -0.009156 | 0.091552 | -0.032044 | -0.013733 | -0.027466 | -0.16479 | 13.4399 | 3.3691 | 3.1082 | 3.3829 | 3.1219 | 0.091552 | 0.004577 | 13.4537 | 121.9711 | 0.027466 | 122.1085 | 0.050354 | 122.0947 | -122.0993 | -122.1359 | 0.027465 | 121.9574 | -0.050354 | 36.058
4934.0781 | 122.2412 | -0.07782 | 122.0581 | -0.18135 | -0.041962 | 0.0013094 | 0.021869 | -0.00084593 | -0.010743 | -0.0025869 | -0.071076 | 0.047181 | 0.081367 | 0.063077 | -0.019438 | 0.045566 | 0.017064 | -0.09613 | -0.059509 | -0.050354 | -0.013733 | 0.09613 | -0.073242 | 0.045776 | 35.9802 | 121.9986 | -0.082397 | 121.9025 | 13.5086 | 3.0716 | 3.3051 | 0.027466 | -122.1176 | -122.0718 | 0.17395 | 0.1236 | 0.004578 | 0.09613 | -0.022888 | -0.004577 | -0.059509 | -0.15564 | 13.5864 | 3.3829 | 3.1494 | 3.3875 | 3.154 | 0.14648 | 0.036621 | 13.591 | 121.9849 | -0.009155 | 122.081 | 0.018311 | 122.0764 | -122.1085 | -122.1405 | 0.064087 | 121.9803 | -0.01831 | 36.058
4935.8438 | 122.2549 | -0.086975 | 122.0535 | -0.24239 | -0.04068 | 0.00024143 | 0.019946 | 0.0034265 | -0.010957 | -0.0042959 | -0.071076 | 0.04654 | 0.081581 | 0.063077 | -0.017942 | 0.044925 | 0.015569 | -0.10071 | -0.041199 | -0.036621 | -0.013733 | 0.09613 | -0.073242 | 0.045776 | 35.8566 | 121.994 | -0.10986 | 121.8796 | 13.6826 | 3.067 | 3.3279 | 0.050354 | -122.0947 | -122.0673 | 0.1831 | 0.13275 | 0.013733 | 0.082397 | -0.036621 | -0.022888 | -0.059509 | -0.17395 | 13.7695 | 3.4149 | 3.154 | 3.4378 | 3.1769 | 0.13275 | 0.022888 | 13.7924 | 121.9894 | -0.004578 | 122.1039 | 0.045776 | 122.081 | -122.0901 | -122.1634 | 0.073242 | 121.9666 | -0.013733 | 35.9436
4937.5469 | 122.2137 | -0.10071 | 122.0764 | -0.12794 | -0.04303 | 0.00066863 | 0.021869 | -0.00020513 | -0.010743 | -0.0038687 | -0.13211 | 0.046754 | 0.081581 | 0.076321 | -0.022215 | 0.045352 | 0.015569 | -0.12817 | -0.009155 | -0.091553 | -0.09613 | 0.004578 | -0.11902 | -0.013733 | 35.6644 | 122.0673 | -0.11444 | 121.8567 | 13.71 | 3.0075 | 3.3417 | 0.009155 | -122.0856 | -122.1725 | 0.10529 | 0.086975 | -0.018311 | 0.07782 | -0.027466 | -0.013733 | -0.009155 | -0.21973 | 13.8107 | 3.4424 | 3.1082 | 3.4561 | 3.1219 | 0.096131 | -0.004577 | 13.8245 | 121.9711 | 0.082398 | 122.1817 | 0.091553 | 122.168 | -122.168 | -122.1909 | 0.004578 | 121.9574 | -0.027466 | 35.7651
4939.3281 | 122.2687 | -0.091553 | 122.0398 | -0.1432 | -0.042816 | 0.0019504 | 0.019519 | -0.0014867 | -0.010957 | -0.0025869 | -0.031403 | 0.046326 | 0.08094 | 0.059659 | -0.020078 | 0.04407 | 0.015569 | -0.14648 | -0.027466 | -0.07782 | -0.064087 | 0.073242 | -0.07782 | 0.041199 | 35.4721 | 122.0261 | -0.10529 | 121.8887 | 13.8794 | 3.0853 | 3.3875 | 0.013733 | -122.0673 | -122.1039 | 0.16479 | 0.13275 | 0.013733 | 0.11902 | 0 | -0.013733 | -0.013733 | -0.15106 | 13.9709 | 3.479 | 3.1769 | 3.4927 | 3.1906 | 0.15106 | 0.013733 | 13.9847 | 121.994 | 0.050354 | 122.1313 | 0.064087 | 122.1176 | -122.1176 | -122.1451 | 0.027466 | 121.9803 | -0.054931 | 35.5637
4941.0312 | 122.2824 | -0.082397 | 122.0352 | -0.20424 | -0.044098 | 0.00066863 | 0.02016 | -0.0055457 | -0.013307 | -0.0045095 | -0.040558 | 0.048676 | 0.080726 | 0.064786 | -0.018156 | 0.043857 | 0.013646 | -0.11902 | -0.045776 | -0.068665 | -0.013733 | 0.091553 | -0.032043 | 0.07782 | 35.2753 | 121.9894 | -0.10071 | 121.9254 | 13.8886 | 3.154 | 3.4195 | 0.013732 | -122.081 | -122.049 | 0.17395 | 0.16022 | 0.050354 | 0.14649 | 0.036622 | -0.018311 | -0.045776 | -0.10986 | 13.9709 | 3.5019 | 3.2364 | 3.5202 | 3.2547 | 0.16022 | 0.054932 | 13.9893 | 122.0261 | 0.022889 | 122.0901 | 0.036621 | 122.0718 | -122.1039 | -122.1359 | 0.068664 | 122.0078 | -0.036622 | 35.3577
4942.7344 | 122.2504 | -0.068665 | 122.0123 | -0.18135 | -0.042389 | 0.0010958 | 0.022937 | -0.00041873 | -0.012239 | -0.0036551 | -0.09549 | 0.045899 | 0.080299 | 0.067349 | -0.020719 | 0.045779 | 0.018346 | -0.091553 | -0.032043 | -0.041199 | -0.004578 | 0.10071 | -0.064087 | 0.050354 | 34.3918 | 121.9849 | -0.10529 | 121.9116 | 13.9252 | 3.0716 | 3.4012 | 0.027466 | -122.0444 | -122.0169 | 0.16937 | 0.11902 | 0.004578 | 0.091553 | -0.022888 | -0.036621 | -0.027466 | -0.10071 | 13.9938 | 3.4698 | 3.1403 | 3.5065 | 3.1769 | 0.14191 | 0.036621 | 14.0305 | 122.0169 | 0.009156 | 122.0901 | 0.036622 | 122.0535 | -122.0535 | -122.1176 | 0.064087 | 121.9803 | -0.022888 | 34.4605
4944.5 | 122.1954 | -0.10986 | 122.0673 | -0.12032 | -0.041962 | -0.0010404 | 0.021869 | -0.0044775 | -0.012452 | -0.0030141 | -0.15652 | 0.049317 | 0.080299 | 0.068631 | -0.021787 | 0.047061 | 0.012578 | -0.15106 | 0 | -0.10071 | -0.10986 | -0.041199 | -0.13275 | -0.027466 | 33.989 | 122.0306 | -0.13275 | 121.8201 | 13.9435 | 3.0121 | 3.4287 | 0.009155 | -122.0673 | -122.1771 | 0.068664 | 0.082397 | -0.022888 | 0.073242 | -0.032043 | -0.022888 | -0.036621 | -0.24719 | 14.0533 | 3.5385 | 3.1219 | 3.5614 | 3.1448 | 0.059509 | -0.009155 | 14.0762 | 121.9528 | 0.10071 | 122.1634 | 0.10986 | 122.1405 | -122.168 | -122.2 | 0 | 121.9299 | -0.041199 | 34.0988
4946.2188 | 122.2046 | -0.10986 | 122.049 | -0.15083 | -0.041321 | 0.0023776 | 0.024646 | 0.0015039 | -0.01053 | -0.00066434 | -0.16263 | 0.050385 | 0.08094 | 0.076748 | -0.020719 | 0.046207 | 0.011296 | -0.11902 | -0.004578 | -0.082397 | -0.050354 | 0.027466 | -0.10529 | -0.009155 | 34.0897 | 122.0352 | -0.11444 | 121.8796 | 14.1953 | 3.0441 | 3.4882 | 0.027466 | -122.0535 | -122.0993 | 0.13733 | 0.10071 | 0.004577 | 0.073242 | -0.022889 | -0.004578 | -0.013733 | -0.16937 | 14.3051 | 3.598 | 3.154 | 3.6026 | 3.1586 | 0.10986 | 0.032043 | 14.3097 | 121.994 | 0.077819 | 122.1497 | 0.10529 | 122.1451 | -122.1313 | -122.1634 | 0.059509 | 121.9894 | -0.009156 | 34.1995
4947.9844 | 122.2687 | -0.091553 | 122.0169 | -0.16609 | -0.042603 | -0.00018577 | 0.01781 | -0.0014867 | -0.013307 | -0.0062185 | -0.028351 | 0.049317 | 0.082008 | 0.064358 | -0.017088 | 0.044498 | 0.018132 | -0.14191 | -0.022888 | -0.064087 | -0.064087 | 0.050354 | -0.073242 | 0.041199 | 33.9432 | 122.0123 | -0.1236 | 121.9025 | 14.4012 | 3.1769 | 3.5797 | 0.027466 | -122.0398 | -122.081 | 0.14191 | 0.13275 | 0.018311 | 0.10529 | -0.009155 | -0.032043 | -0.004578 | -0.11444 | 14.4928 | 3.6713 | 3.2684 | 3.7033 | 3.3005 | 0.11444 | 0 | 14.5248 | 122.0261 | 0.041199 | 122.1359 | 0.068665 | 122.1039 | -122.081 | -122.1405 | 0.027466 | 121.994 | -0.050354 | 34.0347
4949.75 | 122.1725 | -0.11444 | 122.081 | -0.13557 | -0.043671 | 0.00024143 | 0.020587 | 0.00022207 | -0.010957 | -0.0049367 | -0.12296 | 0.049958 | 0.083717 | 0.064786 | -0.020506 | 0.04642 | 0.017919 | -0.16479 | 0 | -0.09613 | -0.1236 | -0.036621 | -0.15106 | -0.036621 | 33.8242 | 122.0444 | -0.14648 | 121.8155 | 14.4104 | 3.0441 | 3.511 | 0.018311 | -122.081 | -122.2046 | 0.07782 | 0.07782 | -0.036621 | 0.059509 | -0.054932 | -0.032043 | -0.036621 | -0.2655 | 14.5248 | 3.6255 | 3.1586 | 3.6575 | 3.1906 | 0.059509 | -0.027466 | 14.5569 | 121.962 | 0.09613 | 122.1909 | 0.11444 | 122.1588 | -122.1771 | -122.2275 | -0.009155 | 121.9299 | -0.050354 | 33.9386
4951.4531 | 122.1588 | -0.1236 | 122.0718 | -0.16609 | -0.042389 | 0.00024143 | 0.021869 | -0.0012731 | -0.012239 | -0.0049367 | -0.089386 | 0.049531 | 0.082862 | 0.062863 | -0.018156 | 0.046848 | 0.014928 | -0.15106 | -0.009155 | -0.073242 | -0.11444 | -0.009155 | -0.1236 | -0.036621 | 33.934 | 122.0627 | -0.1236 | 121.8063 | 14.7034 | 3.1265 | 3.5202 | 0.050354 | -122.081 | -122.1863 | 0.11444 | 0.086975 | 0 | 0.036621 | -0.050354 | 0 | -0.009155 | -0.2655 | 14.827 | 3.6438 | 3.2501 | 3.6438 | 3.2501 | 0.064087 | -0.041199 | 14.827 | 121.9299 | 0.064087 | 122.1863 | 0.11444 | 122.1863 | -122.1451 | -122.1954 | 0.009155 | 121.9299 | -0.027466 | 34.0576
4953.2031 | 122.2046 | -0.10071 | 122.0581 | -0.18135 | -0.041748 | 0.0010958 | 0.022509 | 0.0055627 | -0.010743 | -0.0047231 | -0.13516 | 0.050385 | 0.08094 | 0.070553 | -0.017729 | 0.047061 | 0.01621 | -0.13275 | -0.004578 | -0.086975 | -0.11444 | -0.013733 | -0.11444 | -0.022888 | 34.0805 | 122.0673 | -0.1236 | 121.8521 | 14.8865 | 3.0945 | 3.4561 | 0.013733 | -122.0627 | -122.1725 | 0.086975 | 0.07782 | -0.013733 | 0.064087 | -0.027466 | -0.022888 | 0.009156 | -0.20599 | 14.9872 | 3.5568 | 3.1952 | 3.5797 | 3.2181 | 0.073242 | -0.027466 | 15.0101 | 121.9757 | 0.082397 | 122.1909 | 0.09613 | 122.168 | -122.1451 | -122.1817 | -0.013733 | 121.9528 | -0.032043 | 34.1812
4954.9062 | 122.1588 | -0.1236 | 122.0856 | -0.15083 | -0.043244 | 0.00088223 | 0.02016 | 0.0021447 | -0.013307 | -0.0060049 | -0.068024 | 0.049744 | 0.081367 | 0.066281 | -0.017942 | 0.045779 | 0.020909 | -0.13733 | 0 | -0.091553 | -0.1236 | -0.018311 | -0.13733 | -0.032043 | 33.9111 | 122.081 | -0.14191 | 121.8018 | 15.0055 | 3.1128 | 3.598 | 0.032043 | -122.0856 | -122.2092 | 0.10528 | 0.091553 | -0.013733 | 0.05951 | -0.045776 | -0.018311 | -0.004577 | -0.28381 | 15.1291 | 3.7216 | 3.2364 | 3.7399 | 3.2547 | 0.073242 | -0.032043 | 15.1474 | 121.9437 | 0.091553 | 122.2229 | 0.1236 | 122.2046 | -122.1771 | -122.2275 | 0 | 121.9254 | -0.013733 | 34.0347
4956.6719 | 122.1588 | -0.10986 | 122.0718 | -0.13557 | -0.040894 | -0.0010404 | 0.02016 | 0.00086307 | -0.011598 | -0.0053641 | -0.15652 | 0.05359 | 0.081581 | 0.069485 | -0.019438 | 0.047488 | 0.019628 | -0.1236 | -0.018311 | -0.09613 | -0.091553 | 0.018311 | -0.13275 | -0.022888 | 33.8654 | 122.0581 | -0.11444 | 121.8384 | 15.0925 | 3.1311 | 3.685 | 0.013733 | -122.0901 | -122.1634 | 0.12817 | 0.086975 | -0.022888 | 0.073242 | -0.036621 | -0.004578 | -0.013733 | -0.23346 | 15.2023 | 3.7949 | 3.241 | 3.7994 | 3.2455 | 0.11444 | 0.004577 | 15.2069 | 121.9528 | 0.077819 | 122.1725 | 0.091552 | 122.168 | -122.168 | -122.1863 | 0.01831 | 121.9482 | -0.013733 | 33.9752
4958.4375 | 122.1954 | -0.1236 | 122.0581 | -0.10506 | -0.043457 | -0.0018948 | 0.019732 | -0.0010595 | -0.012239 | -0.0055777 | -0.092438 | 0.053162 | 0.082649 | 0.074185 | -0.016874 | 0.046634 | 0.016423 | -0.16022 | 0.004578 | -0.086975 | -0.11444 | -0.027466 | -0.13733 | -0.032043 | 33.6136 | 122.0535 | -0.1236 | 121.843 | 15.3397 | 3.1311 | 3.6987 | 0.036621 | -122.0535 | -122.1725 | 0.09613 | 0.091553 | -0.013733 | 0.054932 | -0.050354 | 0 | -0.004577 | -0.21515 | 15.4633 | 3.8223 | 3.2547 | 3.8223 | 3.2547 | 0.059509 | -0.027466 | 15.4633 | 121.9666 | 0.091553 | 122.1771 | 0.12817 | 122.1771 | -122.1451 | -122.1817 | 0.009155 | 121.9666 | -0.036621 | 33.7372
4960.2031 | 122.2321 | -0.086975 | 122.0352 | -0.20424 | -0.040894 | -0.00082677 | 0.017382 | -0.00084593 | -0.010102 | -0.0045095 | -0.040558 | 0.053376 | 0.084144 | 0.069058 | -0.017301 | 0.043643 | 0.0192 | -0.086975 | -0.041199 | -0.050354 | -0.022888 | 0.11902 | -0.036621 | 0.059509 | 33.4717 | 122.0032 | -0.086975 | 121.8887 | 15.6372 | 3.1998 | 3.6438 | 0.036621 | -122.0764 | -122.0581 | 0.20599 | 0.14648 | 0.050354 | 0.10986 | 0.013733 | 0 | -0.032043 | -0.14648 | 15.7242 | 3.7308 | 3.2867 | 3.7308 | 3.2867 | 0.16937 | 0.027466 | 15.7242 | 121.9757 | 0.009155 | 122.0901 | 0.045776 | 122.0901 | -122.0856 | -122.1222 | 0.064087 | 121.9757 | 0 | 33.5587
4961.9062 | 122.2046 | -0.10986 | 122.049 | -0.15846 | -0.041535 | 2.7834e-05 | 0.0208 | 0.0047083 | -0.01053 | -0.0030141 | -0.12296 | 0.051453 | 0.085212 | 0.07333 | -0.019224 | 0.04877 | 0.017491 | -0.11444 | -0.009155 | -0.10071 | -0.07782 | 0.027466 | -0.10986 | 0 | 33.316 | 122.0673 | -0.11444 | 121.875 | 15.7379 | 3.2501 | 3.7674 | 0.009155 | -122.0581 | -122.1268 | 0.13733 | 0.10986 | 0 | 0.10071 | -0.009155 | -0.004578 | 0.018311 | -0.17395 | 15.8478 | 3.8773 | 3.36 | 3.8818 | 3.3646 | 0.12817 | 0.022888 | 15.8524 | 121.9894 | 0.091553 | 122.1817 | 0.10071 | 122.1771 | -122.1497 | -122.1634 | 0.032043 | 121.9849 | -0.004578 | 33.4259
4963.6719 | 122.2046 | -0.10529 | 122.0673 | -0.16609 | -0.040253 | 0.001523 | 0.022723 | -0.0025549 | -0.012025 | -0.0034415 | -0.12906 | 0.057221 | 0.086067 | 0.071835 | -0.021147 | 0.047488 | 0.017278 | -0.10986 | 0 | -0.082397 | -0.068665 | 0.032043 | -0.091553 | -0.018311 | 31.4117 | 122.049 | -0.09613 | 121.8842 | 15.9348 | 3.273 | 3.7445 | 0.022889 | -122.0673 | -122.1359 | 0.13733 | 0.086975 | 0.013733 | 0.064086 | -0.009156 | 0.009156 | -0.018311 | -0.18311 | 16.04 | 3.8498 | 3.3783 | 3.8406 | 3.3691 | 0.11444 | 0.013732 | 16.0309 | 121.9803 | 0.082397 | 122.1451 | 0.10529 | 122.1542 | -122.1497 | -122.1634 | 0.036621 | 121.9894 | -0.004577 | 31.517
4965.3594 | 122.2504 | -0.091553 | 122.0261 | -0.2195 | -0.041962 | 0.003873 | 0.019091 | 0.00022207 | -0.01053 | -0.0047231 | -0.037506 | 0.069825 | 0.099952 | 0.071621 | -0.018583 | 0.048557 | 0.023259 | -0.13275 | -0.050354 | -0.045776 | -0.068665 | 0.050354 | -0.086975 | 0.032043 | 32.1808 | 122.0123 | -0.10986 | 121.8613 | 40.8142 | 3.3371 | 4.5959 | 0.045777 | -122.0764 | -122.0947 | 0.14191 | 0.1236 | 0.004578 | 0.077819 | -0.041199 | -0.01831 | -0.013733 | -0.16479 | 40.9058 | 4.6875 | 3.4287 | 4.7058 | 3.447 | 0.09613 | -0.022889 | 40.9241 | 121.9711 | -0.004578 | 122.1222 | 0.041199 | 122.1039 | -122.0718 | -122.1359 | 0.022888 | 121.9528 | -0.041198 | 32.2723
4967.1406 | 122.2 | -0.11444 | 122.0352 | -0.12794 | -0.042816 | 0.0030184 | 0.022723 | -0.0040503 | -0.010957 | -0.0030141 | -0.14127 | 0.13135 | 0.15037 | 0.069699 | -0.020078 | 0.04877 | 0.024968 | -0.16022 | -0.013733 | -0.10529 | -0.11444 | -0.018311 | -0.11902 | -0.018311 | 32.6157 | 122.0444 | -0.11444 | 121.8338 | 119.7372 | 3.2089 | 5.0812 | 0.009155 | -122.049 | -122.1497 | 0.09613 | 0.09613 | -0.004578 | 0.086975 | -0.013733 | 0 | 0.009156 | -0.20142 | 119.8517 | 5.1956 | 3.3234 | 5.1956 | 3.3234 | 0.086975 | -0.009155 | 119.8517 | 121.9482 | 0.091553 | 122.1588 | 0.10071 | 122.1588 | -122.1405 | -122.1497 | 0 | 121.9482 | -0.045776 | 32.7301
4968.9062 | 122.2687 | -0.068665 | 122.0123 | -0.21187 | -0.04068 | 0.0023776 | 0.019519 | 0.00086307 | -0.010316 | -0.0066457 | -0.15042 | 0.1384 | 0.15549 | 0.067563 | -0.019224 | 0.047488 | 0.027532 | -0.086975 | -0.036621 | -0.054932 | -0.009155 | 0.091553 | -0.064087 | 0.045776 | 30.7114 | 121.994 | -0.082397 | 121.9345 | 120.7489 | 3.3966 | 5.2551 | 0.013733 | -122.0489 | -122.0215 | 0.16022 | 0.11444 | 0.004578 | 0.10071 | -0.009155 | -0.013732 | -0.01831 | -0.07782 | 120.8176 | 5.3238 | 3.4653 | 5.3375 | 3.479 | 0.14649 | 0.045777 | 120.8313 | 122.0169 | 0.018311 | 122.0764 | 0.032044 | 122.0627 | -122.0673 | -122.0947 | 0.05951 | 122.0032 | -0.01831 | 30.78
4970.6094 | 122.2778 | -0.068665 | 122.0215 | -0.21187 | -0.040039 | -0.00018577 | 0.02315 | -0.0051183 | -0.01053 | -0.0034415 | -0.14127 | 0.14075 | 0.15913 | 0.066708 | -0.019438 | 0.047702 | 0.027318 | -0.09613 | -0.041199 | -0.059509 | -0.013733 | 0.091553 | -0.054932 | 0.050354 | 30.5511 | 121.9757 | -0.082397 | 121.9208 | 122.0352 | 3.4103 | 5.2505 | 0.009156 | -122.0627 | -122.0352 | 0.16022 | 0.11902 | 0.013733 | 0.10986 | 0.004577 | -0.013732 | -0.045776 | -0.10071 | 122.1039 | 5.3192 | 3.479 | 5.3329 | 3.4927 | 0.15106 | 0.045776 | 122.1176 | 122.0032 | 0.01831 | 122.0581 | 0.027466 | 122.0444 | -122.081 | -122.1039 | 0.054932 | 121.9894 | -0.027465 | 30.6198
4972.375 | 122.2961 | -0.073242 | 122.0032 | -0.13557 | -0.042603 | 0.0023776 | 0.018451 | -0.0010595 | -0.011384 | -0.0055777 | -0.18399 | 0.4473 | 0.36335 | 0.063504 | -0.018156 | 0.046848 | 0.12516 | -0.10071 | -0.041199 | -0.068665 | 0.009155 | 0.14191 | 0.004578 | 0.09613 | 24.3439 | 121.9299 | -0.07782 | 121.9299 | 121.9757 | 2.6505 | 13.8657 | 0.004577 | -122.0444 | -121.994 | 0.21515 | 0.16937 | 0.07782 | 0.16479 | 0.073243 | -0.004578 | -0.073242 | -0.073242 | 122.0489 | 13.9389 | 2.7237 | 13.9435 | 2.7283 | 0.21057 | 0.07782 | 122.0535 | 122.0078 | 0.027466 | 122.0078 | 0.032043 | 122.0032 | -122.0718 | -122.081 | 0.082397 | 122.0032 | -0.027466 | 24.4171
4974.1406 | 122.1313 | -0.11444 | 122.0215 | -0.18135 | -0.041321 | 0.001523 | 0.022082 | 0.0032129 | -0.011598 | -0.0055777 | -0.092438 | 0.024964 | 0.015785 | -0.0080601 | -0.019865 | 0.028476 | 0.00018809 | -0.14648 | -0.018311 | -0.086975 | -0.13733 | -0.032043 | -0.16937 | -0.059509 | 2.9297 | 3.1952 | 2.8931 | 2.9755 | 3.0304 | 2.948 | 3.067 | 0.027466 | -122.0398 | -122.1588 | 0.082398 | 0.054932 | -0.054932 | 0.027466 | -0.082398 | 3.0075 | -118.8263 | -119.046 | 3.1448 | 3.1815 | 3.0624 | 0.17395 | 0.054932 | 0.054932 | -0.050354 | 0.13733 | 0.082398 | 0.068664 | 0.30212 | 0.09613 | 3.3096 | -122.1085 | -119.1284 | -0.022888 | 3.0899 | -0.032043 | 3.0441
4975.9062 | 122.2549 | -0.064087 | 122.0032 | -0.2195 | -0.040039 | 2.7834e-05 | 0.019519 | 0.0025721 | -0.011384 | -0.0038687 | -0.058869 | 0.024323 | 0.01493 | -0.0076327 | -0.020078 | 0.027835 | -0.0051525 | -0.073242 | -0.045776 | -0.054932 | -0.004578 | 0.09613 | -0.054932 | 0.045776 | 3.0029 | 3.0624 | 2.8381 | 3.0075 | 3.0899 | 2.9984 | 3.0624 | 0.009155 | -122.049 | -122.0078 | 0.16022 | 0.10986 | 0.009155 | 0.10071 | 0 | 2.9022 | -118.9407 | -118.9957 | 3.154 | 3.1265 | 3.0624 | 0.2243 | 0.16022 | 0.15106 | 0.050354 | 0.25177 | 0.16937 | 0.009156 | 0.2243 | 0.018311 | 3.1265 | -122.0581 | -119.165 | 0.059509 | 3.0716 | -0.009155 | 3.067
4977.6875 | 122.1771 | -0.091553 | 122.0444 | -0.18135 | -0.042603 | 0.0019504 | 0.021014 | 0.0025721 | -0.012452 | -0.0045095 | -0.092438 | 0.024323 | 0.016426 | -0.011264 | -0.019224 | 0.027621 | -0.0042981 | -0.12817 | -0.004578 | -0.082397 | -0.059509 | 0.050354 | -0.09613 | 0.004578 | 2.9114 | 3.0808 | 2.8244 | 2.9114 | 3.0075 | 2.9114 | 2.9938 | 0.009156 | -122.049 | -122.1039 | 0.14191 | 0.096131 | -0.004577 | 0.086975 | -0.013733 | 2.916 | -118.9636 | -119.133 | 3.0991 | 3.0853 | 3.0029 | 0.16937 | 0.086975 | 0.13275 | 0.022888 | 0.1831 | 0.086975 | 0.077819 | 0.25635 | 0.086975 | 3.1723 | -122.1268 | -119.22 | 0.032044 | 3.0029 | -0.036621 | 3.0029
4979.4531 | 122.2504 | -0.068665 | 122.0078 | -0.22713 | -0.042176 | 0.0040866 | 0.0208 | 0.0025721 | -0.012879 | -0.0064321 | -0.058869 | 0.022401 | 0.015144 | -0.016605 | -0.017942 | 0.025272 | -0.0040845 | -0.091553 | -0.027466 | -0.054932 | 0 | 0.11444 | -0.068665 | 0.054932 | 2.9846 | 3.0396 | 2.8061 | 2.9434 | 3.0533 | 2.9617 | 3.0212 | 0.013733 | -122.0352 | -122.0078 | 0.18311 | 0.1236 | 0 | 0.10986 | -0.013733 | 2.8748 | -118.9682 | -119.0643 | 3.1219 | 3.0899 | 3.0304 | 0.21515 | 0.15564 | 0.16937 | 0.054932 | 0.24719 | 0.13733 | 0.027466 | 0.23346 | 0.041199 | 3.1082 | -122.0627 | -119.2017 | 0.068665 | 3.0121 | -0.022888 | 3.0533
4981.1562 | 122.1451 | -0.11444 | 122.0856 | -0.19661 | -0.039826 | 0.001523 | 0.022509 | -0.0025549 | -0.011811 | -0.0030141 | -0.1077 | 0.021332 | 0.016212 | -0.0095553 | -0.018369 | 0.028476 | -0.00088011 | -0.16022 | 0.013733 | -0.10071 | -0.14191 | -0.07782 | -0.18768 | -0.07782 | 2.7695 | 3.0808 | 2.7649 | 2.8519 | 2.8976 | 2.829 | 2.9251 | 0.013733 | -122.0718 | -122.2275 | 0.036621 | 0.036621 | -0.073242 | 0.022888 | -0.086975 | 2.8793 | -119.0048 | -119.2337 | 3.0121 | 3.0396 | 2.9434 | 0.16022 | 0.064086 | 0.022888 | -0.041199 | 0.13275 | 0.086975 | 0.11444 | 0.31586 | 0.12817 | 3.1952 | -122.1863 | -119.3207 | -0.027466 | 2.9663 | -0.045776 | 2.8839
4982.8594 | 122.2229 | -0.086975 | 122.0581 | -0.21187 | -0.040894 | 0.001523 | 0.021655 | -0.0010595 | -0.011384 | -0.0089957 | -0.10464 | 0.025391 | 0.016212 | -0.0069919 | -0.018797 | 0.026767 | -0.0017347 | -0.15106 | -0.018311 | -0.068665 | -0.10529 | -0.009155 | -0.16479 | -0.041199 | 2.9434 | 3.1357 | 2.8702 | 2.9709 | 3.0396 | 2.98 | 3.067 | 0.01831 | -122.0764 | -122.1634 | 0.07782 | 0.045776 | -0.07782 | 0.027466 | -0.09613 | 2.9572 | -118.9224 | -119.0872 | 3.1265 | 3.154 | 3.067 | 0.19684 | 0.10986 | 0.05951 | -0.036621 | 0.16937 | 0.10071 | 0.050354 | 0.2655 | 0.068664 | 3.2227 | -122.1268 | -119.1879 | -0.018311 | 3.0579 | -0.064087 | 3.0304
4984.625 | 122.1771 | -0.1236 | 122.0535 | -0.20424 | -0.041107 | 0.00066863 | 0.022296 | 0.0021447 | -0.013307 | -0.0015189 | -0.064972 | 0.023682 | 0.014717 | -0.015323 | -0.019224 | 0.028049 | -0.0042981 | -0.14648 | 0 | -0.09613 | -0.13733 | -0.045776 | -0.19226 | -0.073242 | 2.9434 | 3.2043 | 2.9068 | 2.9755 | 3.035 | 2.9572 | 3.067 | 0.027466 | -122.0535 | -122.1909 | 0.07782 | 0.050354 | -0.068665 | 0.022888 | -0.096131 | 3.0304 | -118.8492 | -119.0781 | 3.1586 | 3.1906 | 3.0807 | 0.16022 | 0.050354 | 0.050354 | -0.041199 | 0.12817 | 0.068665 | 0.09613 | 0.29755 | 0.1236 | 3.3279 | -122.1497 | -119.1467 | -0.013733 | 3.0991 | -0.022888 | 3.067
4986.3125 | 122.287 | -0.068665 | 122.0444 | -0.15846 | -0.042176 | -0.0021084 | 0.019946 | -0.00041873 | -0.011598 | -0.0049367 | -0.0039367 | 0.022401 | 0.013648 | -0.010837 | -0.019224 | 0.025699 | -0.0042981 | -0.091553 | -0.022888 | -0.059509 | 0.004578 | 0.13275 | -0.009155 | 0.082397 | 3.154 | 3.2227 | 2.9984 | 3.1219 | 3.2547 | 3.186 | 3.1952 | 0.009156 | -122.0673 | -122.0398 | 0.20142 | 0.15106 | 0.05951 | 0.14191 | 0.050354 | 3.067 | -118.8217 | -118.9224 | 3.3234 | 3.2639 | 3.2547 | 0.19684 | 0.18768 | 0.19226 | 0.064087 | 0.25635 | 0.1236 | 0.036621 | 0.2243 | 0.045777 | 3.2913 | -122.1039 | -119.046 | 0.073243 | 3.1906 | -0.022888 | 3.2227
4988.0938 | 122.1634 | -0.11444 | 122.1313 | -0.17372 | -0.042816 | 0.00066863 | 0.020587 | -0.00063233 | -0.014375 | -0.0042959 | -0.06192 | 0.021973 | 0.014717 | -0.013828 | -0.020078 | 0.025485 | -0.0034435 | -0.16937 | 0 | -0.091553 | -0.11902 | -0.022888 | -0.1236 | -0.041199 | 3.0167 | 3.2822 | 2.9938 | 3.0487 | 3.1494 | 3.0808 | 3.1265 | 0.022888 | -122.1313 | -122.2504 | 0.091553 | 0.073242 | -0.009155 | 0.050354 | -0.032043 | 3.1082 | -118.8492 | -119.0826 | 3.2639 | 3.241 | 3.1952 | 0.13275 | 0.086976 | 0.068665 | -0.027466 | 0.15564 | 0.054932 | 0.091553 | 0.28839 | 0.11444 | 3.3966 | -122.2229 | -119.1376 | -0.004578 | 3.1631 | -0.054932 | 3.1311
4989.8594 | 122.1725 | -0.10986 | 122.0856 | -0.18135 | -0.038758 | 0.00024143 | 0.022723 | 0.0012903 | -0.010316 | -0.0049367 | -0.10464 | 0.025391 | 0.015571 | -0.011051 | -0.019438 | 0.026767 | -0.0025891 | -0.13733 | -0.009155 | -0.068665 | -0.10986 | -0.036621 | -0.17853 | -0.064087 | 3.0121 | 3.2867 | 3.0029 | 3.0304 | 3.1219 | 3.0258 | 3.1357 | 0.041198 | -122.0947 | -122.1954 | 0.073242 | 0.045776 | -0.068665 | 0.004578 | -0.10986 | 3.1128 | -118.7988 | -119.0552 | 3.2318 | 3.2455 | 3.1357 | 0.13275 | 0.022888 | 0.032044 | -0.041198 | 0.11902 | 0.027466 | 0.05951 | 0.28381 | 0.10071 | 3.3966 | -122.1542 | -119.0826 | 0 | 3.1403 | -0.027466 | 3.1219
4991.5469 | 122.1954 | -0.10986 | 122.0901 | -0.15083 | -0.042389 | 0.00088223 | 0.022509 | -0.0023413 | -0.010102 | -0.0028005 | -0.074127 | 0.024323 | 0.016426 | -0.015323 | -0.019224 | 0.027621 | -0.0021619 | -0.15106 | 0 | -0.086975 | -0.13275 | -0.036621 | -0.18768 | -0.045776 | 3.035 | 3.273 | 2.98 | 3.0624 | 3.1311 | 3.0441 | 3.1448 | 0.022888 | -122.0901 | -122.2229 | 0.073242 | 0.064087 | -0.07782 | 0.041199 | -0.10071 | 3.0899 | -118.8171 | -119.0277 | 3.241 | 3.2547 | 3.154 | 0.16479 | 0.064086 | 0.050354 | -0.045776 | 0.15106 | 0.082397 | 0.086975 | 0.29297 | 0.10986 | 3.3829 | -122.1771 | -119.1101 | -0.022888 | 3.1723 | -0.041199 | 3.1448
4993.3125 | 122.3236 | -0.086975 | 122.0535 | -0.12032 | -0.041535 | 0.00024143 | 0.019732 | -0.0031957 | -0.012239 | -0.0034415 | 0.0052185 | 0.022401 | 0.014503 | -0.011478 | -0.017729 | 0.024631 | -0.0010937 | -0.09613 | -0.041199 | -0.064087 | -0.009155 | 0.13275 | -0.004578 | 0.086975 | 3.2547 | 3.2455 | 3.0579 | 3.1906 | 3.3234 | 3.273 | 3.2684 | 0.022888 | -122.0947 | -122.0627 | 0.21973 | 0.17395 | 0.082397 | 0.15106 | 0.059509 | 3.1448 | -118.808 | -118.8629 | 3.4103 | 3.3554 | 3.36 | 0.21057 | 0.21515 | 0.19684 | 0.054932 | 0.2655 | 0.13275 | 0.022888 | 0.18768 | 0.045776 | 3.3325 | -122.1176 | -118.9957 | 0.07782 | 3.2776 | -0.009155 | 3.3417
4995.0781 | 122.2687 | -0.073242 | 122.0398 | -0.28816 | -0.040467 | 0.003232 | 0.017596 | 0.0015039 | -0.009675 | -0.0068593 | -0.025299 | 0.020905 | 0.015144 | -0.017032 | -0.019651 | 0.026126 | -0.00045291 | -0.086975 | -0.050354 | -0.045776 | 0 | 0.10986 | -0.050354 | 0.054932 | 3.1815 | 3.2318 | 3.0258 | 3.1494 | 3.2272 | 3.1677 | 3.2227 | 0.027466 | -122.0901 | -122.0398 | 0.18311 | 0.12817 | 0.022888 | 0.10071 | -0.004578 | 3.0991 | -118.808 | -118.8904 | 3.3005 | 3.2959 | 3.241 | 0.19684 | 0.14191 | 0.15564 | 0.045776 | 0.20142 | 0.1236 | -0.004578 | 0.20599 | 0.022888 | 3.3051 | -122.0856 | -119.014 | 0.073242 | 3.2227 | -0.013733 | 3.2547
4996.8438 | 122.319 | -0.059509 | 122.049 | -0.21187 | -0.041321 | 0.0030184 | 0.021655 | 8.47e-06 | -0.011811 | -0.0049367 | -0.055817 | 0.02176 | 0.015571 | -0.011264 | -0.020506 | 0.026126 | -0.0025891 | -0.064087 | -0.036621 | -0.036621 | -0.009155 | 0.11444 | -0.059509 | 0.050354 | 3.1998 | 3.2501 | 3.0258 | 3.1952 | 3.2913 | 3.1952 | 3.2455 | 0.022888 | -122.0856 | -122.0581 | 0.17395 | 0.10986 | 0 | 0.086975 | -0.022888 | 3.0853 | -118.7988 | -118.8538 | 3.3508 | 3.3051 | 3.2547 | 0.21973 | 0.16937 | 0.15106 | 0.027466 | 0.2655 | 0.16937 | 0 | 0.2243 | 0.022888 | 3.3096 | -122.0856 | -119.0231 | 0.050354 | 3.2547 | -0.004578 | 3.2593
4998.6094 | 122.168 | -0.12817 | 122.1039 | -0.18898 | -0.039612 | 0.0019504 | 0.022509 | 0.0025721 | -0.011811 | -0.0038687 | -0.1199 | 0.023255 | 0.015998 | -0.014041 | -0.02136 | 0.025272 | -0.0017347 | -0.15106 | -0.022888 | -0.10986 | -0.10986 | -0.054932 | -0.17853 | -0.059509 | 3.0716 | 3.3279 | 3.0441 | 3.0808 | 3.1677 | 3.0945 | 3.186 | 0.018311 | -122.1268 | -122.2137 | 0.073242 | 0.068665 | -0.050354 | 0.050354 | -0.068665 | 3.1723 | -118.7759 | -119.0231 | 3.2959 | 3.3142 | 3.2227 | 0.14191 | 0.050354 | 0.054931 | 0 | 0.1236 | 0.036622 | 0.086975 | 0.28381 | 0.10529 | 3.4561 | -122.2137 | -119.0598 | 0.018311 | 3.2089 | -0.022888 | 3.1998
5000.3125 | 122.2916 | -0.086975 | 122.0856 | -0.15083 | -0.042389 | -0.0014676 | 0.019091 | -0.0012731 | -0.012452 | -0.0066457 | 0.0052185 | 0.021546 | 0.013648 | -0.018741 | -0.01901 | 0.02399 | -0.0079297 | -0.09613 | -0.050354 | -0.032043 | 0.009155 | 0.13275 | -0.013733 | 0.082397 | 3.2364 | 3.2867 | 3.0853 | 3.1998 | 3.3051 | 3.2547 | 3.2684 | 0.054932 | -122.1359 | -122.0764 | 0.21973 | 0.16937 | 0.073242 | 0.11444 | 0.01831 | 3.1723 | -118.7988 | -118.8858 | 3.392 | 3.3554 | 3.3417 | 0.18311 | 0.16937 | 0.16479 | 0.041198 | 0.21973 | 0.11444 | -0.018311 | 0.20142 | 0.036621 | 3.3737 | -122.1176 | -119.0002 | 0.09613 | 3.2867 | -0.009155 | 3.3234
5002.0938 | 122.2549 | -0.091553 | 122.0764 | -0.15846 | -0.042176 | -0.00018577 | 0.018878 | 0.0012903 | -0.010743 | -0.0062185 | -0.0008851 | 0.02176 | 0.016639 | -0.01276 | -0.017942 | 0.02634 | -0.0049389 | -0.13275 | -0.032043 | -0.064087 | -0.059509 | 0.041199 | -0.091553 | 0.018311 | 3.1219 | 3.2822 | 3.0441 | 3.1311 | 3.2364 | 3.1677 | 3.2318 | 0.027466 | -122.1085 | -122.1359 | 0.13275 | 0.10986 | 0 | 0.082398 | -0.027466 | 3.1357 | -118.7942 | -118.9453 | 3.3279 | 3.3234 | 3.2593 | 0.18768 | 0.1236 | 0.10529 | 0.004578 | 0.19226 | 0.086976 | 0.032044 | 0.23804 | 0.05951 | 3.3737 | -122.1405 | -119.0323 | 0.032044 | 3.2227 | -0.041198 | 3.2135
5003.8594 | 122.2412 | -0.10986 | 122.1085 | -0.17372 | -0.040894 | 0.00066863 | 0.021869 | 0.0021447 | -0.011384 | -0.0028005 | -0.083283 | 0.023041 | 0.01493 | -0.014041 | -0.021574 | 0.02634 | -0.0013073 | -0.09613 | -0.018311 | -0.082397 | -0.059509 | 0.018311 | -0.091553 | 0.004578 | 3.2181 | 3.3554 | 3.0945 | 3.1906 | 3.2822 | 3.2089 | 3.273 | 0.027466 | -122.1268 | -122.168 | 0.12817 | 0.11444 | 0.01831 | 0.086975 | -0.009156 | 3.2043 | -118.7531 | -118.9178 | 3.392 | 3.3829 | 3.3188 | 0.17853 | 0.11444 | 0.10071 | 0.022888 | 0.18768 | 0.096131 | 0.064086 | 0.26093 | 0.091552 | 3.4653 | -122.1909 | -119.014 | 0.050354 | 3.3005 | 0.013733 | 3.3279
5005.5625 | 122.1771 | -0.1236 | 122.113 | -0.13557 | -0.042603 | -0.0014676 | 0.019946 | -0.0049047 | -0.01352 | -0.0036551 | -0.04361 | 0.023255 | 0.015144 | -0.012119 | -0.019865 | 0.02634 | -0.0042981 | -0.13733 | -0.018311 | -0.091553 | -0.11444 | 0 | -0.13275 | -0.018311 | 3.1128 | 3.3508 | 3.0533 | 3.1082 | 3.2089 | 3.1631 | 3.1952 | 0.032043 | -122.1313 | -122.2275 | 0.1236 | 0.10528 | -0.009155 | 0.073242 | -0.041198 | 3.1769 | -118.7622 | -119.0048 | 3.3325 | 3.3188 | 3.2867 | 0.14191 | 0.10986 | 0.091553 | -0.022888 | 0.15564 | 0.054931 | 0.073242 | 0.29755 | 0.10528 | 3.4744 | -122.2046 | -119.0598 | 0.009155 | 3.2318 | -0.013733 | 3.2364
5007.3438 | 122.3236 | -0.064087 | 122.0627 | -0.15083 | -0.042816 | 2.7834e-05 | 0.018878 | -0.0042639 | -0.01053 | -0.0055777 | -0.013092 | 0.021119 | 0.013648 | -0.015109 | -0.018797 | 0.027194 | -0.0032299 | -0.091553 | -0.050354 | -0.050354 | 0.018311 | 0.16022 | 0.013733 | 0.10529 | 3.3234 | 3.3463 | 3.154 | 3.2822 | 3.4012 | 3.3508 | 3.36 | 0.013733 | -122.113 | -122.0444 | 0.2243 | 0.16937 | 0.07782 | 0.15564 | 0.064087 | 3.2181 | -118.7164 | -118.7805 | 3.4653 | 3.4241 | 3.4149 | 0.20599 | 0.19684 | 0.21057 | 0.068665 | 0.24719 | 0.12817 | 0 | 0.19226 | 0.013733 | 3.4103 | -122.113 | -118.9087 | 0.082398 | 3.3463 | -0.027466 | 3.3875
5009.0469 | 122.3236 | -0.07782 | 122.0673 | -0.19661 | -0.041962 | -0.001254 | 0.018878 | 0.00064947 | -0.013093 | -0.0034415 | -0.0008851 | 0.025391 | 0.014289 | -0.021518 | -0.019224 | 0.026767 | -0.0049389 | -0.11902 | -0.032043 | -0.068665 | -0.036621 | 0.082397 | -0.054932 | 0.054932 | 3.2364 | 3.3279 | 3.1128 | 3.2593 | 3.3691 | 3.3142 | 3.3508 | 0.009155 | -122.0993 | -122.1039 | 0.16022 | 0.13275 | 0.022888 | 0.1236 | 0.013733 | 3.1906 | -118.7393 | -118.808 | 3.447 | 3.4287 | 3.392 | 0.23804 | 0.20142 | 0.15106 | 0.032044 | 0.25635 | 0.14648 | 0.036622 | 0.21515 | 0.045777 | 3.4058 | -122.1359 | -118.9545 | 0.041199 | 3.3371 | -0.041199 | 3.3142
5010.75 | 122.2137 | -0.10529 | 122.0718 | -0.18135 | -0.040253 | 0.0010958 | 0.021869 | 0.0010767 | -0.011598 | -0.0045095 | -0.11075 | 0.023682 | 0.016426 | -0.0093417 | -0.019224 | 0.027621 | -0.0038709 | -0.13733 | 0.004578 | -0.09613 | -0.13275 | -0.036621 | -0.16937 | -0.054932 | 3.2181 | 3.4149 | 3.154 | 3.2318 | 3.3142 | 3.2364 | 3.3188 | 0.009156 | -122.0673 | -122.2046 | 0.068665 | 0.050354 | -0.064087 | 0.041198 | -0.073243 | 3.2593 | -118.6569 | -118.84 | 3.4195 | 3.4241 | 3.3417 | 0.16479 | 0.082397 | 0.059509 | -0.036621 | 0.16022 | 0.07782 | 0.10071 | 0.26092 | 0.10986 | 3.5202 | -122.168 | -118.9178 | -0.027465 | 3.3371 | -0.032043 | 3.3234
5012.5312 | 122.1909 | -0.11444 | 122.0627 | -0.15846 | -0.039398 | 0.0017368 | 0.021014 | -0.00063233 | -0.012239 | -0.0040823 | -0.13516 | 0.023682 | 0.015144 | -0.0080601 | -0.018797 | 0.027194 | -0.0015209 | -0.10529 | -0.009155 | -0.073242 | -0.068665 | 0.018311 | -0.13733 | -0.018311 | 3.2455 | 3.4332 | 3.154 | 3.2318 | 3.3096 | 3.2181 | 3.3051 | 0.041199 | -122.0718 | -122.1313 | 0.13275 | 0.09613 | -0.022888 | 0.054931 | -0.064087 | 3.2684 | -118.6295 | -118.8309 | 3.4241 | 3.4195 | 3.3325 | 0.15106 | 0.064087 | 0.091553 | 0.004577 | 0.15564 | 0.07782 | 0.064087 | 0.27924 | 0.10529 | 3.5477 | -122.1359 | -118.9087 | 0.045776 | 3.3463 | 0.009155 | 3.36
5014.2969 | 122.2137 | -0.10071 | 122.0993 | -0.15846 | -0.043244 | 0.002164 | 0.019091 | -0.0023413 | -0.012025 | -0.0047231 | -0.025299 | 0.021119 | 0.013648 | -0.0093417 | -0.019438 | 0.026126 | -0.0049389 | -0.10529 | -0.045776 | -0.064087 | -0.041199 | 0.082397 | -0.064087 | 0.032043 | 3.2822 | 3.4424 | 3.186 | 3.2455 | 3.3508 | 3.2913 | 3.3463 | 0.036621 | -122.1451 | -122.1405 | 0.18311 | 0.13275 | 0.036621 | 0.09613 | 0 | 3.2867 | -118.6569 | -118.8538 | 3.4515 | 3.447 | 3.392 | 0.16022 | 0.10529 | 0.14648 | 0.022888 | 0.1648 | 0.059509 | 0.018311 | 0.25635 | 0.054932 | 3.5431 | -122.1634 | -118.9133 | 0.059509 | 3.3463 | -0.004578 | 3.3829
5016.0625 | 122.2687 | -0.073242 | 122.0581 | -0.15846 | -0.041748 | 0.0013094 | 0.019519 | 0.0025721 | -0.01352 | -0.0032277 | -0.022247 | 0.02176 | 0.012794 | -0.017032 | -0.021147 | 0.026767 | 0.00040169 | -0.12817 | -0.018311 | -0.050354 | -0.032043 | 0.054932 | -0.091553 | 0.022888 | 3.2867 | 3.3966 | 3.1769 | 3.2913 | 3.3875 | 3.3234 | 3.3783 | 0.022888 | -122.0764 | -122.0901 | 0.12817 | 0.09613 | -0.018311 | 0.073242 | -0.041199 | 3.2501 | -118.6615 | -118.7668 | 3.4607 | 3.4515 | 3.3966 | 0.20142 | 0.14648 | 0.10529 | 0.018311 | 0.21057 | 0.11444 | 0.032043 | 0.21973 | 0.054931 | 3.4698 | -122.1085 | -118.8812 | 0.041199 | 3.3646 | -0.054932 | 3.36
5017.8281 | 122.3007 | -0.068665 | 122.0627 | -0.22713 | -0.041321 | 0.0010958 | 0.019305 | 0.00086307 | -0.012025 | -0.0036551 | -0.034454 | 0.023041 | 0.016639 | -0.0080601 | -0.017729 | 0.025699 | -0.0019483 | -0.086975 | -0.032043 | -0.050354 | 0.004578 | 0.10986 | -0.041199 | 0.059509 | 3.4058 | 3.4332 | 3.2272 | 3.3737 | 3.4653 | 3.3783 | 3.4241 | 0.018311 | -122.0947 | -122.0581 | 0.17853 | 0.12817 | 0.027466 | 0.10986 | 0.009155 | 3.2959 | -118.6295 | -118.689 | 3.5339 | 3.4927 | 3.447 | 0.19684 | 0.15106 | 0.16022 | 0.054932 | 0.23804 | 0.14648 | 0.018311 | 0.20599 | 0.036622 | 3.5019 | -122.113 | -118.8354 | 0.073243 | 3.4424 | -0.01831 | 3.4744
5019.5938 | 122.2 | -0.1236 | 122.113 | -0.15083 | -0.044098 | -0.001254 | 0.018878 | -0.0034095 | -0.014588 | -0.0051505 | -0.074127 | 0.02411 | 0.014717 | -0.021091 | -0.019438 | 0.023776 | -0.0023755 | -0.17853 | 0.004578 | -0.09613 | -0.13275 | -0.027466 | -0.14191 | -0.018311 | 3.1998 | 3.4424 | 3.1631 | 3.2272 | 3.3279 | 3.2501 | 3.3142 | 0.027466 | -122.1085 | -122.2458 | 0.09613 | 0.10528 | -0.018311 | 0.077819 | -0.045777 | 3.2867 | -118.6707 | -118.8858 | 3.4515 | 3.4378 | 3.3737 | 0.15106 | 0.086975 | 0.068664 | -0.036621 | 0.1648 | 0.064087 | 0.10071 | 0.27924 | 0.12817 | 3.566 | -122.2092 | -118.9499 | -0.009155 | 3.3508 | -0.054932 | 3.3234
5021.2969 | 122.3236 | -0.082397 | 122.0947 | -0.21187 | -0.04068 | -0.0010404 | 0.0208 | 8.47e-06 | -0.013734 | -0.0057913 | 0.0082703 | 0.020905 | 0.014289 | -0.012973 | -0.018583 | 0.026126 | -0.0042981 | -0.13275 | -0.027466 | -0.054932 | -0.036621 | 0.064087 | -0.073242 | 0.064087 | 3.3234 | 3.4058 | 3.1723 | 3.3234 | 3.4241 | 3.3646 | 3.4012 | 0.027465 | -122.1222 | -122.1313 | 0.14648 | 0.14648 | 0.009155 | 0.11902 | -0.01831 | 3.2547 | -118.689 | -118.7714 | 3.5065 | 3.4836 | 3.447 | 0.22888 | 0.19226 | 0.11902 | 0.018311 | 0.25177 | 0.15106 | 0.027466 | 0.23346 | 0.054931 | 3.4882 | -122.1497 | -118.9224 | 0.045776 | 3.4058 | -0.050354 | 3.4058
5023.0625 | 122.3053 | -0.07782 | 122.0444 | -0.18135 | -0.043244 | 0.00045503 | 0.021014 | -0.00041873 | -0.012879 | -0.0072867 | -0.01004 | 0.023041 | 0.014289 | -0.015323 | -0.019224 | 0.024631 | -0.0062207 | -0.13733 | -0.041199 | -0.059509 | -0.041199 | 0.059509 | -0.054932 | 0.045776 | 3.2822 | 3.3875 | 3.1631 | 3.2913 | 3.4058 | 3.3417 | 3.392 | 0.018311 | -122.0856 | -122.0856 | 0.13733 | 0.1236 | 0.022888 | 0.10528 | 0.004577 | 3.241 | -118.6569 | -118.7531 | 3.4836 | 3.4698 | 3.4195 | 0.22888 | 0.17853 | 0.11902 | 0.01831 | 0.24262 | 0.12817 | 0.01831 | 0.2243 | 0.036621 | 3.4653 | -122.1039 | -118.8812 | 0.036621 | 3.3691 | -0.059509 | 3.36
5024.8438 | 122.3053 | -0.068665 | 122.0764 | -0.22713 | -0.042603 | 0.00045503 | 0.019946 | -0.0010595 | -0.012239 | -0.0042959 | -0.019196 | 0.023469 | 0.014289 | -0.014896 | -0.018369 | 0.025485 | -0.0070751 | -0.14191 | -0.036621 | -0.059509 | -0.041199 | 0.068665 | -0.064087 | 0.050354 | 3.273 | 3.3783 | 3.1586 | 3.2867 | 3.392 | 3.3371 | 3.3783 | 0.009156 | -122.113 | -122.1176 | 0.13733 | 0.11902 | 0.004578 | 0.10986 | -0.004578 | 3.2272 | -118.6981 | -118.7897 | 3.4607 | 3.447 | 3.4058 | 0.21973 | 0.17853 | 0.12817 | 0.01831 | 0.23346 | 0.12817 | 0.022888 | 0.21973 | 0.032044 | 3.447 | -122.1359 | -118.9178 | 0.027466 | 3.3554 | -0.073242 | 3.3417
5026.5469 | 122.3282 | -0.082397 | 122.0764 | -0.13557 | -0.043885 | 0.00024143 | 0.021869 | -0.0078955 | -0.013093 | -0.0045095 | -0.037506 | 0.024964 | 0.014289 | -0.011264 | -0.020719 | 0.025485 | -2.571e-05 | -0.10529 | -0.027466 | -0.068665 | -0.018311 | 0.073242 | -0.036621 | 0.07782 | 3.3966 | 3.4653 | 3.2318 | 3.4012 | 3.5156 | 3.447 | 3.4698 | 0.013732 | -122.1039 | -122.0947 | 0.15564 | 0.16022 | 0.045776 | 0.14649 | 0.032044 | 3.3142 | -118.6111 | -118.6752 | 3.598 | 3.5522 | 3.5294 | 0.23804 | 0.21515 | 0.14191 | 0.050354 | 0.28381 | 0.16937 | 0.041199 | 0.23346 | 0.054931 | 3.5477 | -122.1451 | -118.8446 | 0.064086 | 3.4836 | -0.022889 | 3.479
5028.3125 | 122.3282 | -0.073242 | 122.0856 | -0.17372 | -0.042176 | 0.0010958 | 0.02016 | -0.0027685 | -0.013093 | -0.0030141 | -0.040558 | 0.021973 | 0.013862 | -0.01276 | -0.019651 | 0.025699 | -0.00066651 | -0.09613 | -0.050354 | -0.059509 | 0.022888 | 0.14648 | 0.009155 | 0.091553 | 3.4653 | 3.4561 | 3.2547 | 3.392 | 3.5156 | 3.4561 | 3.4698 | 0.013733 | -122.1359 | -122.0627 | 0.21973 | 0.16479 | 0.082397 | 0.15106 | 0.068664 | 3.3279 | -118.6295 | -118.6935 | 3.5889 | 3.5431 | 3.5294 | 0.21515 | 0.20142 | 0.20599 | 0.082397 | 0.26092 | 0.13733 | 0.009155 | 0.20142 | 0.022888 | 3.5294 | -122.1451 | -118.8309 | 0.09613 | 3.4653 | -0.022888 | 3.5385
5030.0781 | 122.2778 | -0.082397 | 122.0352 | -0.17372 | -0.040253 | 0.0010958 | 0.018878 | -0.0036231 | -0.010743 | -0.0057913 | -0.06192 | 0.022828 | 0.012794 | -0.011905 | -0.021147 | 0.025272 | -0.0057935 | -0.086975 | -0.041199 | -0.050354 | 0.013733 | 0.10529 | -0.054932 | 0.054932 | 3.3783 | 3.4332 | 3.2181 | 3.3646 | 3.447 | 3.3691 | 3.4332 | 0.032043 | -122.0764 | -122.0215 | 0.18768 | 0.13733 | 0.027465 | 0.10529 | -0.004578 | 3.3005 | -118.602 | -118.6707 | 3.5294 | 3.5156 | 3.4515 | 0.21515 | 0.15106 | 0.15564 | 0.064087 | 0.22888 | 0.14648 | 0.009155 | 0.21515 | 0.041198 | 3.5156 | -122.0856 | -118.8171 | 0.09613 | 3.447 | -0.004578 | 3.4607
5031.7812 | 122.3328 | -0.082397 | 122.0764 | -0.16609 | -0.042389 | -0.0023222 | 0.019946 | -0.0017005 | -0.014802 | -0.0025869 | -0.016144 | 0.023896 | 0.014503 | -0.013187 | -0.019865 | 0.024631 | -0.0051525 | -0.11444 | -0.036621 | -0.064087 | 0.004578 | 0.1236 | -0.022888 | 0.086975 | 3.3966 | 3.4241 | 3.2181 | 3.3783 | 3.4973 | 3.4378 | 3.4378 | 0.01831 | -122.113 | -122.0718 | 0.20599 | 0.16937 | 0.059509 | 0.15106 | 0.041199 | 3.3005 | -118.6523 | -118.6981 | 3.5797 | 3.5202 | 3.5202 | 0.21973 | 0.21973 | 0.18768 | 0.068665 | 0.27923 | 0.16022 | 0.027466 | 0.20599 | 0.045776 | 3.5065 | -122.1405 | -118.8583 | 0.086975 | 3.4607 | -0.032044 | 3.479
5033.5469 | 122.3145 | -0.07782 | 122.0764 | -0.19661 | -0.039185 | 2.7834e-05 | 0.021655 | -0.0019141 | -0.0098886 | -0.0034415 | -0.089386 | 0.02176 | 0.014076 | -0.013187 | -0.020933 | 0.028903 | -0.0045117 | -0.068665 | -0.050354 | -0.045776 | 0.009155 | 0.11444 | -0.050354 | 0.054932 | 3.4195 | 3.4378 | 3.2501 | 3.4012 | 3.4836 | 3.3966 | 3.4607 | 0.032044 | -122.1268 | -122.0673 | 0.19226 | 0.13275 | 0.027466 | 0.10071 | -0.004578 | 3.3279 | -118.6386 | -118.6752 | 3.5614 | 3.5385 | 3.4744 | 0.21057 | 0.14648 | 0.16022 | 0.054931 | 0.23346 | 0.15106 | -0.004578 | 0.18768 | 0.027466 | 3.5156 | -122.1222 | -118.8263 | 0.086975 | 3.479 | 0.009155 | 3.4973
5035.2969 | 122.319 | -0.07782 | 122.0764 | -0.18898 | -0.04303 | -0.00039957 | 0.02016 | -0.0029821 | -0.012025 | -0.0049367 | -0.034454 | 0.023682 | 0.015357 | -0.013828 | -0.020506 | 0.026126 | -0.0019483 | -0.11902 | -0.032043 | -0.064087 | -0.036621 | 0.068665 | -0.050354 | 0.054932 | 3.3737 | 3.4515 | 3.2318 | 3.3737 | 3.4927 | 3.4195 | 3.4698 | 0.013733 | -122.1085 | -122.113 | 0.14649 | 0.13275 | 0.027466 | 0.11902 | 0.013733 | 3.3096 | -118.6249 | -118.7027 | 3.5706 | 3.5477 | 3.4973 | 0.23804 | 0.18768 | 0.13275 | 0.027466 | 0.26092 | 0.14191 | 0.032044 | 0.21973 | 0.045777 | 3.5294 | -122.1405 | -118.8446 | 0.041199 | 3.4515 | -0.041199 | 3.4515
5037.0781 | 122.3282 | -0.082397 | 122.0718 | -0.19661 | -0.042176 | 0.00024143 | 0.020587 | 0.00064947 | -0.012239 | -0.0025869 | -0.028351 | 0.023682 | 0.012153 | -0.014469 | -0.018156 | 0.02634 | 0.00018809 | -0.11444 | -0.036621 | -0.07782 | -0.018311 | 0.082397 | -0.027466 | 0.068665 | 3.3966 | 3.4561 | 3.2181 | 3.3829 | 3.5065 | 3.4332 | 3.4698 | 0.004577 | -122.1085 | -122.0901 | 0.16479 | 0.15106 | 0.054931 | 0.14649 | 0.050354 | 3.3005 | -118.6157 | -118.689 | 3.5889 | 3.5522 | 3.5156 | 0.25177 | 0.21515 | 0.16022 | 0.059509 | 0.28839 | 0.1648 | 0.041199 | 0.23804 | 0.045776 | 3.5385 | -122.1497 | -118.8538 | 0.064086 | 3.4653 | -0.032044 | 3.479
5038.7969 | 122.1909 | -0.1236 | 122.0901 | -0.16609 | -0.043885 | -0.001254 | 0.022082 | -0.0027685 | -0.013307 | -0.0042959 | -0.10159 | 0.020905 | 0.015357 | -0.014682 | -0.019865 | 0.027194 | -0.0066479 | -0.16022 | -0.018311 | -0.091553 | -0.11444 | -0.041199 | -0.13275 | -0.036621 | 3.2593 | 3.5019 | 3.2089 | 3.2593 | 3.3646 | 3.2913 | 3.3554 | 0.032043 | -122.1085 | -122.2046 | 0.082397 | 0.086975 | -0.009155 | 0.054932 | -0.041198 | 3.3325 | -118.5883 | -118.8309 | 3.4882 | 3.479 | 3.4149 | 0.14649 | 0.082398 | 0.050354 | -0.022888 | 0.15564 | 0.050354 | 0.073242 | 0.29297 | 0.10528 | 3.6255 | -122.1817 | -118.8812 | 0.009155 | 3.3829 | -0.036621 | 3.3829
5040.5625 | 122.3236 | -0.064087 | 122.081 | -0.22713 | -0.041535 | 0.00024143 | 0.022723 | -0.0038367 | -0.010102 | -0.0070731 | -0.1138 | 0.022187 | 0.014289 | -0.0089145 | -0.018583 | 0.025272 | -0.0021619 | -0.10529 | -0.036621 | -0.064087 | -0.004578 | 0.07782 | -0.068665 | 0.045776 | 3.4058 | 3.4424 | 3.2364 | 3.3966 | 3.4882 | 3.4103 | 3.4698 | 0 | -122.1176 | -122.0856 | 0.14191 | 0.10986 | -0.004578 | 0.10986 | -0.004578 | 3.3005 | -118.6386 | -118.6844 | 3.5522 | 3.5339 | 3.4744 | 0.23346 | 0.17395 | 0.14191 | 0.059509 | 0.25177 | 0.16022 | 0.027466 | 0.20599 | 0.027466 | 3.5065 | -122.1451 | -118.8446 | 0.059509 | 3.4607 | -0.041199 | 3.4698
5042.3281 | 122.2046 | -0.13275 | 122.1039 | -0.15083 | -0.041107 | -0.001254 | 0.022509 | 0.00043587 | -0.011384 | -0.0045095 | -0.10159 | 0.023896 | 0.014289 | -0.0061375 | -0.020078 | 0.02634 | -0.0038709 | -0.17395 | 0 | -0.10071 | -0.12817 | -0.041199 | -0.14191 | -0.027466 | 3.3279 | 3.5614 | 3.2776 | 3.3463 | 3.4424 | 3.3875 | 3.4378 | 0.032043 | -122.1039 | -122.2321 | 0.091552 | 0.10529 | -0.009156 | 0.073242 | -0.041199 | 3.4103 | -118.5425 | -118.7576 | 3.5751 | 3.5706 | 3.5202 | 0.16022 | 0.10986 | 0.059509 | -0.027466 | 0.16479 | 0.068664 | 0.10071 | 0.28381 | 0.13275 | 3.6942 | -122.2046 | -118.8263 | 0.004577 | 3.479 | -0.041199 | 3.4607
5044.1094 | 122.2778 | -0.054932 | 122.0901 | -0.20424 | -0.040467 | 0.00088223 | 0.020587 | -0.0021277 | -0.010957 | -0.0070731 | -0.052765 | 0.023041 | 0.013862 | -0.0134 | -0.018797 | 0.026767 | -0.0015209 | -0.09613 | -0.027466 | -0.050354 | -0.018311 | 0.11902 | -0.054932 | 0.050354 | 3.4424 | 3.479 | 3.2867 | 3.4012 | 3.5019 | 3.447 | 3.4653 | 0.004578 | -122.1176 | -122.1085 | 0.17395 | 0.10529 | 0 | 0.10071 | -0.004578 | 3.3417 | -118.6111 | -118.689 | 3.5568 | 3.5202 | 3.5019 | 0.17853 | 0.16022 | 0.16937 | 0.032043 | 0.21515 | 0.11444 | 0.022888 | 0.19226 | 0.027466 | 3.5339 | -122.1405 | -118.8034 | 0.036621 | 3.4561 | -0.041198 | 3.4973
5045.8125 | 122.3145 | -0.059509 | 122.0581 | -0.16609 | -0.039826 | 0.0028048 | 0.020373 | -0.0010595 | -0.013093 | -0.0038687 | -0.068024 | 0.02176 | 0.017066 | -0.0033603 | -0.019651 | 0.027408 | -0.0019483 | -0.07782 | -0.041199 | -0.032043 | 0.018311 | 0.1236 | -0.041199 | 0.054932 | 3.4653 | 3.4653 | 3.2913 | 3.447 | 3.5431 | 3.4698 | 3.5156 | 0.027466 | -122.0993 | -122.0398 | 0.1831 | 0.11444 | 0.01831 | 0.086975 | -0.009156 | 3.3508 | -118.5928 | -118.6111 | 3.6026 | 3.5751 | 3.5294 | 0.2243 | 0.17853 | 0.15564 | 0.050354 | 0.25177 | 0.15564 | -0.009156 | 0.17395 | 0.01831 | 3.5248 | -122.0901 | -118.7668 | 0.07782 | 3.5065 | -0.018311 | 3.5248
5047.5781 | 122.2778 | -0.082397 | 122.0856 | -0.19661 | -0.038971 | -0.0018948 | 0.020373 | -0.00020513 | -0.01117 | -0.0062185 | -0.064972 | 0.020692 | 0.015571 | -0.0089145 | -0.018369 | 0.02634 | -0.0021619 | -0.11444 | -0.050354 | -0.041199 | -0.032043 | 0.086975 | -0.086975 | 0.036621 | 3.4149 | 3.4882 | 3.2822 | 3.3875 | 3.4744 | 3.4378 | 3.4744 | 0.041198 | -122.1359 | -122.1176 | 0.16937 | 0.11902 | -0.004578 | 0.07782 | -0.045776 | 3.3646 | -118.5974 | -118.6981 | 3.5568 | 3.5568 | 3.5202 | 0.19226 | 0.15564 | 0.12817 | 0.009156 | 0.19226 | 0.10528 | -0.009155 | 0.20599 | 0.032043 | 3.5706 | -122.1268 | -118.8034 | 0.050354 | 3.4698 | -0.032044 | 3.4973
5049.2812 | 122.2733 | -0.086975 | 122.0764 | -0.18135 | -0.039185 | -0.0021084 | 0.018878 | -0.0023413 | -0.012452 | -0.0040823 | -0.068024 | 0.022187 | 0.011512 | -0.014682 | -0.017088 | 0.027621 | -0.0034435 | -0.11444 | -0.041199 | -0.059509 | -0.041199 | 0.082397 | -0.091553 | 0.036621 | 3.3646 | 3.447 | 3.2547 | 3.3829 | 3.4607 | 3.4103 | 3.4332 | 0.027466 | -122.1176 | -122.1176 | 0.16937 | 0.1236 | -0.004578 | 0.09613 | -0.032044 | 3.3417 | -118.6295 | -118.6935 | 3.5477 | 3.5202 | 3.4973 | 0.17853 | 0.15564 | 0.14191 | 0.01831 | 0.20599 | 0.12817 | 0.01831 | 0.19226 | 0.045776 | 3.5339 | -122.1359 | -118.8217 | 0.045776 | 3.4698 | -0.027466 | 3.4515
5051.0469 | 122.2229 | -0.1236 | 122.113 | -0.18135 | -0.042389 | -0.001254 | 0.021441 | 0.00064947 | -0.013093 | -0.0060049 | -0.064972 | 0.023255 | 0.013862 | -0.010623 | -0.01901 | 0.025699 | -0.0057935 | -0.10529 | -0.050354 | -0.059509 | -0.036621 | 0.054932 | -0.064087 | 0.027466 | 3.3463 | 3.4973 | 3.2318 | 3.3005 | 3.4332 | 3.3646 | 3.3875 | 0.064087 | -122.1634 | -122.1497 | 0.17853 | 0.15106 | 0.059509 | 0.086975 | -0.004578 | 3.3554 | -118.6157 | -118.8126 | 3.5568 | 3.511 | 3.4882 | 0.15564 | 0.13275 | 0.11444 | 0.022888 | 0.20142 | 0.068664 | 0.009155 | 0.2655 | 0.073242 | 3.6209 | -122.1725 | -118.8812 | 0.086975 | 3.4241 | 0.01831 | 3.4698
5052.8281 | 122.2412 | -0.11444 | 122.1085 | -0.17372 | -0.041107 | 0.00066863 | 0.023791 | 0.0051355 | -0.010743 | -0.0042959 | -0.12296 | 0.022614 | 0.013008 | -0.011264 | -0.018797 | 0.029971 | -0.0017347 | -0.10986 | 0 | -0.086975 | -0.059509 | 0.036621 | -0.10071 | -0.009155 | 3.3966 | 3.5156 | 3.2593 | 3.3875 | 3.4698 | 3.4103 | 3.4561 | 0.027466 | -122.1085 | -122.168 | 0.15106 | 0.10529 | 0.013733 | 0.07782 | -0.013733 | 3.3737 | -118.5928 | -118.721 | 3.5843 | 3.5706 | 3.5248 | 0.19684 | 0.15106 | 0.1236 | 0.027466 | 0.21057 | 0.12817 | 0.086975 | 0.25635 | 0.11444 | 3.6301 | -122.1954 | -118.8492 | 0.054932 | 3.5019 | 0.004578 | 3.511
5054.6094 | 122.2458 | -0.11902 | 122.1085 | -0.089798 | -0.04303 | 0.00066863 | 0.023791 | -0.0036231 | -0.012879 | -0.0040823 | -0.098541 | 0.024323 | 0.017921 | -0.014041 | -0.015592 | 0.029971 | -0.0030163 | -0.14648 | 0.009155 | -0.091553 | -0.09613 | -0.009155 | -0.11902 | -0.027466 | 3.3051 | 3.5156 | 3.241 | 3.3417 | 3.4378 | 3.3554 | 3.4378 | 0.027466 | -122.0993 | -122.2046 | 0.10986 | 0.091553 | 0 | 0.064087 | -0.027466 | 3.36 | -118.5928 | -118.7668 | 3.5568 | 3.5568 | 3.4744 | 0.19684 | 0.11444 | 0.082398 | -0.004577 | 0.19684 | 0.10071 | 0.10071 | 0.27466 | 0.12817 | 3.6346 | -122.2 | -118.8675 | 0.022889 | 3.4607 | -0.027465 | 3.4241
5056.3125 | 122.3007 | -0.054932 | 122.0581 | -0.19661 | -0.041107 | -0.00082677 | 0.016528 | 0.0017175 | -0.012879 | -0.0038687 | -0.016144 | 0.023255 | 0.013648 | -0.019168 | -0.016874 | 0.025699 | -0.0021619 | -0.12817 | -0.018311 | -0.059509 | -0.050354 | 0.064087 | -0.073242 | 0.041199 | 3.3371 | 3.4653 | 3.2364 | 3.3646 | 3.4744 | 3.4332 | 3.4653 | -0.004577 | -122.0764 | -122.1085 | 0.11902 | 0.096131 | -0.01831 | 0.10071 | -0.013733 | 3.2913 | -118.5928 | -118.6935 | 3.5294 | 3.5202 | 3.4882 | 0.22888 | 0.19684 | 0.1236 | 0.009155 | 0.23804 | 0.12817 | 0.041198 | 0.22888 | 0.036621 | 3.5202 | -122.1176 | -118.8217 | 0.004578 | 3.4195 | -0.073242 | 3.392
5058.0781 | 122.2824 | -0.068665 | 122.0627 | -0.21187 | -0.040467 | 0.00088223 | 0.01781 | -0.00063233 | -0.01053 | -0.0049367 | -0.028351 | 0.022828 | 0.016426 | -0.0097689 | -0.018369 | 0.026553 | -2.571e-05 | -0.11444 | -0.032043 | -0.041199 | -0.036621 | 0.059509 | -0.091553 | 0.022888 | 3.3417 | 3.4515 | 3.2364 | 3.3508 | 3.4378 | 3.392 | 3.4149 | 0.027466 | -122.0947 | -122.0993 | 0.12817 | 0.091553 | -0.022888 | 0.064087 | -0.050354 | 3.3051 | -118.6111 | -118.7119 | 3.5065 | 3.4836 | 3.4607 | 0.17853 | 0.15564 | 0.10071 | 0.004578 | 0.20142 | 0.11444 | 0.009156 | 0.21515 | 0.036622 | 3.5202 | -122.1039 | -118.8263 | 0.032044 | 3.4195 | -0.045776 | 3.4103
5059.8438 | 122.1863 | -0.1236 | 122.0947 | -0.12794 | -0.042389 | -0.0023222 | 0.021014 | -0.0031957 | -0.013947 | -0.0055777 | -0.058869 | 0.023896 | 0.015571 | -0.0082737 | -0.019865 | 0.028262 | -0.0032299 | -0.16022 | 0 | -0.091553 | -0.11444 | -0.013733 | -0.13733 | -0.032043 | 3.2501 | 3.4515 | 3.1815 | 3.2227 | 3.3417 | 3.2959 | 3.3279 | 0.032043 | -122.0947 | -122.2092 | 0.10986 | 0.091553 | -0.013733 | 0.05951 | -0.045776 | 3.3051 | -118.6432 | -118.8721 | 3.4653 | 3.4515 | 3.4195 | 0.14648 | 0.11444 | 0.07782 | -0.022888 | 0.16022 | 0.041198 | 0.091553 | 0.27008 | 0.1236 | 3.5751 | -122.1863 | -118.9133 | 0.009155 | 3.3463 | -0.036621 | 3.3737
5061.6094 | 122.3053 | -0.073242 | 122.0856 | -0.23476 | -0.040467 | 0.0025912 | 0.0208 | 0.0027857 | -0.01053 | -0.0051505 | -0.1077 | 0.023469 | 0.014717 | -0.0065647 | -0.02136 | 0.026553 | -0.0045117 | -0.12817 | -0.022888 | -0.091553 | -0.054932 | 0.050354 | -0.09613 | 0.018311 | 3.3371 | 3.4149 | 3.1952 | 3.3508 | 3.4287 | 3.3691 | 3.4332 | -0.018311 | -122.1085 | -122.1405 | 0.1236 | 0.091553 | -0.022888 | 0.10986 | -0.004577 | 3.2684 | -118.6707 | -118.7347 | 3.5019 | 3.5065 | 3.4424 | 0.23804 | 0.17395 | 0.14191 | 0.036621 | 0.23346 | 0.15564 | 0.068665 | 0.21973 | 0.050354 | 3.4882 | -122.1771 | -118.8904 | 0.01831 | 3.4241 | -0.054932 | 3.4103
5063.375 | 122.3328 | -0.073242 | 122.0856 | -0.24239 | -0.040253 | 0.0034456 | 0.021655 | -0.00084593 | -0.0081796 | -0.0013051 | -0.074127 | 0.021119 | 0.01728 | -0.012546 | -0.018797 | 0.027408 | -0.0049389 | -0.073242 | -0.045776 | -0.050354 | 0.018311 | 0.10529 | -0.068665 | 0.054932 | 3.3966 | 3.3966 | 3.2318 | 3.3737 | 3.4653 | 3.4103 | 3.4515 | 0.022888 | -122.1313 | -122.0673 | 0.17853 | 0.12817 | 0.004577 | 0.10529 | -0.018311 | 3.3051 | -118.689 | -118.7119 | 3.5385 | 3.5248 | 3.4836 | 0.21973 | 0.17853 | 0.15564 | 0.068665 | 0.23346 | 0.14191 | 0.004578 | 0.16479 | 0.027466 | 3.4698 | -122.1359 | -118.8538 | 0.091553 | 3.447 | 0 | 3.4698
5065.0781 | 122.2229 | -0.1236 | 122.0947 | -0.13557 | -0.040894 | 0.0017368 | 0.022509 | -0.00084593 | -0.012025 | -0.0064321 | -0.14432 | 0.025178 | 0.014717 | -0.0084873 | -0.018797 | 0.027621 | -0.0028027 | -0.16479 | 0.004578 | -0.082397 | -0.13275 | -0.045776 | -0.16937 | -0.059509 | 3.2043 | 3.3966 | 3.1403 | 3.2455 | 3.3005 | 3.2364 | 3.3142 | 0.041199 | -122.0901 | -122.2275 | 0.07782 | 0.064087 | -0.045777 | 0.022888 | -0.086976 | 3.2639 | -118.6981 | -118.8492 | 3.4241 | 3.4378 | 3.36 | 0.17395 | 0.09613 | 0.036621 | -0.050354 | 0.16022 | 0.10529 | 0.086975 | 0.25635 | 0.12817 | 3.5202 | -122.1771 | -118.9545 | -0.009155 | 3.3691 | -0.041199 | 3.3279
5066.8281 | 122.3099 | -0.054932 | 122.081 | -0.21187 | -0.041962 | 0.00066863 | 0.017169 | -0.0014867 | -0.011811 | -0.0057913 | -0.0008851 | 0.021332 | 0.01493 | -0.017032 | -0.020292 | 0.025272 | -0.0019483 | -0.10071 | -0.013733 | -0.054932 | 0.004578 | 0.15106 | -0.004578 | 0.082397 | 3.3737 | 3.3691 | 3.1815 | 3.3234 | 3.4561 | 3.4058 | 3.4058 | 0 | -122.0947 | -122.0764 | 0.20599 | 0.13733 | 0.050354 | 0.13733 | 0.050354 | 3.2364 | -118.7119 | -118.7576 | 3.511 | 3.4607 | 3.4607 | 0.2243 | 0.2243 | 0.20599 | 0.05951 | 0.27466 | 0.14191 | 0.041199 | 0.18768 | 0.041199 | 3.4241 | -122.1359 | -118.8995 | 0.05951 | 3.3783 | -0.045776 | 3.4287
5068.6094 | 122.3145 | -0.068665 | 122.0993 | -0.1432 | -0.041321 | -0.0021084 | 0.019946 | 0.0017175 | -0.012239 | -0.0049367 | -0.019196 | 0.023469 | 0.01493 | -0.010196 | -0.01901 | 0.026767 | -0.0049389 | -0.09613 | -0.050354 | -0.036621 | 0.009155 | 0.15106 | -0.004578 | 0.086975 | 3.3417 | 3.3737 | 3.1723 | 3.3051 | 3.4378 | 3.392 | 3.392 | 0.032044 | -122.1497 | -122.0901 | 0.21973 | 0.15564 | 0.064087 | 0.1236 | 0.032043 | 3.241 | -118.7256 | -118.7943 | 3.5065 | 3.4607 | 3.4607 | 0.21973 | 0.21973 | 0.18768 | 0.045776 | 0.2655 | 0.13275 | -0.013733 | 0.20142 | 0.018311 | 3.4424 | -122.1359 | -118.927 | 0.07782 | 3.3737 | -0.027465 | 3.4103
5070.3125 | 122.3007 | -0.068665 | 122.081 | -0.15846 | -0.038117 | 0.0017368 | 0.0208 | -0.0017005 | -0.0094614 | -0.0049367 | -0.083283 | 0.024537 | 0.015571 | -0.013187 | -0.018583 | 0.028903 | -0.00066651 | -0.10529 | -0.041199 | -0.064087 | -0.027466 | 0.07782 | -0.086975 | 0.050354 | 3.3371 | 3.3783 | 3.1906 | 3.3371 | 3.4149 | 3.3508 | 3.4012 | 0.004578 | -122.1222 | -122.1085 | 0.14649 | 0.11902 | -0.01831 | 0.11444 | -0.022888 | 3.2593 | -118.7027 | -118.7439 | 3.4836 | 3.4698 | 3.4195 | 0.21057 | 0.16022 | 0.14191 | 0.036621 | 0.2243 | 0.14648 | 0.022888 | 0.18768 | 0.027466 | 3.447 | -122.1451 | -118.8904 | 0.041199 | 3.4058 | -0.036621 | 3.4058
5072.0938 | 122.2641 | -0.086975 | 122.113 | -0.20424 | -0.04068 | -0.00018577 | 0.022082 | 0.00086307 | -0.01053 | -0.0040823 | -0.11075 | 0.024323 | 0.015785 | -0.010837 | -0.019438 | 0.027408 | 0.00018809 | -0.14648 | -0.004578 | -0.073242 | -0.10986 | -0.004578 | -0.14648 | -0.032043 | 3.2364 | 3.3783 | 3.154 | 3.2776 | 3.3463 | 3.2776 | 3.3417 | 0.013733 | -122.1176 | -122.2229 | 0.082397 | 0.054932 | -0.059509 | 0.041199 | -0.073242 | 3.241 | -118.7347 | -118.8354 | 3.4332 | 3.4286 | 3.3646 | 0.18768 | 0.1236 | 0.068664 | -0.036621 | 0.19226 | 0.1236 | 0.068664 | 0.2243 | 0.082397 | 3.4653 | -122.1863 | -118.959 | -0.022888 | 3.3646 | -0.059509 | 3.3234
5073.7969 | 122.2778 | -0.086975 | 122.0901 | -0.20424 | -0.040253 | 0.0010958 | 0.02016 | -0.0036231 | -0.0094614 | -0.0045095 | -0.04361 | 0.02176 | 0.015144 | -0.0134 | -0.017942 | 0.025912 | -0.0045117 | -0.13733 | -0.027466 | -0.054932 | -0.064087 | 0.054932 | -0.091553 | 0.022888 | 3.2089 | 3.3279 | 3.1265 | 3.241 | 3.3279 | 3.2639 | 3.3096 | 0.032043 | -122.1176 | -122.1542 | 0.14191 | 0.10986 | -0.004578 | 0.07782 | -0.036621 | 3.2135 | -118.7622 | -118.8492 | 3.4149 | 3.3966 | 3.3508 | 0.1831 | 0.13733 | 0.10986 | -0.009155 | 0.20142 | 0.11444 | 0.027466 | 0.20142 | 0.059509 | 3.4149 | -122.1451 | -118.9636 | 0.022888 | 3.3279 | -0.050354 | 3.2959
5075.5469 | 122.3099 | -0.082397 | 122.0581 | -0.16609 | -0.04068 | -0.0018948 | 0.018664 | -0.0036231 | -0.010102 | -0.0032277 | -0.016144 | 0.022401 | 0.016426 | -0.01276 | -0.019224 | 0.025272 | -0.0077161 | -0.11902 | -0.041199 | -0.07782 | -0.036621 | 0.064087 | -0.059509 | 0.050354 | 3.2227 | 3.3142 | 3.0991 | 3.2547 | 3.3508 | 3.2913 | 3.3279 | 0.004577 | -122.0993 | -122.0947 | 0.14648 | 0.13275 | 0.022888 | 0.12817 | 0.018311 | 3.1815 | -118.7439 | -118.8034 | 3.4332 | 3.4103 | 3.3737 | 0.22888 | 0.19226 | 0.14191 | 0.041199 | 0.25177 | 0.15564 | 0.036621 | 0.21515 | 0.041198 | 3.3966 | -122.1359 | -118.959 | 0.045776 | 3.3371 | -0.036622 | 3.3051
5077.3125 | 122.2092 | -0.11902 | 122.1222 | -0.12794 | -0.043885 | 0.0023776 | 0.022082 | 0.00043587 | -0.01352 | -0.0049367 | -0.071076 | 0.023255 | 0.016426 | -0.0061375 | -0.018583 | 0.025699 | -0.00066651 | -0.17395 | 0.027466 | -0.10529 | -0.13733 | -0.036621 | -0.12817 | -0.041199 | 3.0945 | 3.3325 | 3.0533 | 3.1174 | 3.1998 | 3.1311 | 3.2089 | 0.013733 | -122.0947 | -122.2595 | 0.082398 | 0.07782 | -0.009155 | 0.064087 | -0.022888 | 3.1723 | -118.7897 | -119.0048 | 3.3188 | 3.3279 | 3.2501 | 0.15564 | 0.07782 | 0.068665 | -0.032043 | 0.14648 | 0.064087 | 0.13275 | 0.27924 | 0.14649 | 3.4515 | -122.2275 | -119.0689 | -0.01831 | 3.2364 | -0.054931 | 3.2135
5079.0312 | 122.2046 | -0.10986 | 122.1313 | -0.13557 | -0.043671 | -0.0018948 | 0.019946 | 0.00064947 | -0.012025 | -0.0028005 | -0.092438 | 0.023896 | 0.01493 | -0.0097689 | -0.020078 | 0.025912 | -0.0021619 | -0.16022 | -0.009155 | -0.10071 | -0.1236 | -0.041199 | -0.14191 | -0.036621 | 3.0808 | 3.3234 | 3.0396 | 3.1082 | 3.1998 | 3.1403 | 3.1998 | 0.009155 | -122.1405 | -122.2549 | 0.068664 | 0.073242 | -0.032044 | 0.064087 | -0.041199 | 3.1494 | -118.808 | -119.0231 | 3.3096 | 3.3096 | 3.2501 | 0.16022 | 0.10071 | 0.059509 | -0.022888 | 0.16022 | 0.068664 | 0.091553 | 0.28381 | 0.10071 | 3.4332 | -122.2321 | -119.0918 | -0.013733 | 3.2181 | -0.050354 | 3.1906
5080.7969 | 122.3236 | -0.064087 | 122.0627 | -0.21187 | -0.04068 | 0.002164 | 0.021228 | 8.47e-06 | -0.012239 | -0.0062185 | -0.074127 | 0.023469 | 0.013648 | -0.014255 | -0.01901 | 0.027408 | -0.0036573 | -0.068665 | -0.018311 | -0.041199 | 0.004578 | 0.10986 | -0.045776 | 0.059509 | 3.2181 | 3.2501 | 3.0624 | 3.2181 | 3.3096 | 3.241 | 3.2959 | 0.022888 | -122.081 | -122.0581 | 0.17395 | 0.1236 | 0.018311 | 0.10071 | -0.004577 | 3.1265 | -118.8126 | -118.8446 | 3.3737 | 3.36 | 3.3051 | 0.23346 | 0.17853 | 0.15106 | 0.045777 | 0.24719 | 0.15564 | 0.022888 | 0.18768 | 0.045776 | 3.3142 | -122.1039 | -119.0002 | 0.068665 | 3.2822 | -0.004578 | 3.2822
5082.5625 | 122.2137 | -0.10986 | 122.0901 | -0.16609 | -0.039612 | 0.0030184 | 0.021869 | 0.0023585 | -0.01117 | -0.0057913 | -0.080231 | 0.022614 | 0.012794 | -0.0061375 | -0.020933 | 0.026981 | -0.0028027 | -0.14648 | 0.018311 | -0.11444 | -0.11902 | -0.022888 | -0.18768 | -0.050354 | 2.916 | 3.1952 | 2.9388 | 3.0304 | 3.0808 | 3.0075 | 3.1036 | -0.004578 | -122.0718 | -122.2092 | 0.086975 | 0.059509 | -0.07782 | 0.064087 | -0.073242 | 3.0487 | -118.895 | -119.0598 | 3.1906 | 3.2135 | 3.1174 | 0.1648 | 0.068664 | 0.091553 | -0.004578 | 0.14191 | 0.091553 | 0.13275 | 0.25635 | 0.12817 | 3.3051 | -122.2046 | -119.1513 | -0.009156 | 3.1403 | -0.036621 | 3.0258
5084.3281 | 122.3328 | -0.082397 | 122.0581 | -0.17372 | -0.041748 | 0.002164 | 0.018451 | 0.0023585 | -0.012025 | -0.0049367 | 0.017425 | 0.023041 | 0.016212 | -0.014041 | -0.01901 | 0.025058 | -0.0051525 | -0.12817 | -0.022888 | -0.068665 | -0.027466 | 0.082397 | -0.054932 | 0.054932 | 3.0304 | 3.1906 | 3.0075 | 3.154 | 3.2593 | 3.1906 | 3.2318 | 0.013732 | -122.081 | -122.0856 | 0.16479 | 0.13733 | 0.027465 | 0.1236 | 0.013733 | 3.0899 | -118.8675 | -118.9041 | 3.3417 | 3.3142 | 3.273 | 0.22431 | 0.18311 | 0.15106 | 0.041199 | 0.25177 | 0.14649 | 0.045777 | 0.18311 | 0.059509 | 3.273 | -122.1268 | -119.0506 | 0.054931 | 3.2364 | -0.045777 | 3.1128
5086.0312 | 122.1954 | -0.1236 | 122.0764 | -0.16609 | -0.038971 | -0.00018577 | 0.024005 | 8.47e-06 | -0.010957 | -0.0057913 | -0.1199 | 0.02411 | 0.016426 | -0.0050693 | -0.020719 | 0.030185 | -0.0025891 | -0.15564 | -0.004578 | -0.091553 | -0.12817 | -0.068665 | -0.20142 | -0.050354 | 2.8427 | 3.2043 | 2.9205 | 2.9984 | 3.0579 | 2.9938 | 3.0991 | 0.032043 | -122.081 | -122.2046 | 0.054931 | 0.073242 | -0.07782 | 0.041199 | -0.10986 | 3.0441 | -118.8721 | -119.0781 | 3.1815 | 3.2227 | 3.1174 | 0.17853 | 0.073242 | 0.022888 | -0.036621 | 0.13733 | 0.07782 | 0.086975 | 0.28381 | 0.11902 | 3.3279 | -122.168 | -119.1559 | -0.004578 | 3.1219 | -0.032044 | 2.9663
5087.7969 | 122.3099 | -0.086975 | 122.0947 | -0.2195 | -0.044525 | -0.00082677 | 0.021014 | -0.0023413 | -0.009675 | -0.0047231 | -0.013092 | 0.023682 | 0.014717 | -0.015537 | -0.019224 | 0.023776 | -0.0028027 | -0.1236 | -0.022888 | -0.059509 | -0.050354 | 0.07782 | -0.054932 | 0.045776 | 2.9572 | 3.1677 | 2.9663 | 3.0853 | 3.1952 | 3.1677 | 3.1906 | 0.027466 | -122.1176 | -122.1451 | 0.16479 | 0.13275 | 0.032043 | 0.10528 | 0.004577 | 3.0533 | -118.927 | -119.0094 | 3.2822 | 3.2776 | 3.2547 | 0.2243 | 0.20142 | 0.13733 | 0.009155 | 0.22888 | 0.11902 | 0.036621 | 0.20142 | 0.064087 | 3.2547 | -122.1542 | -119.1284 | 0.036621 | 3.1723 | -0.036621 | 3.0441
5089.5781 | 122.3236 | -0.068665 | 122.0718 | -0.097427 | -0.042389 | 0.00024143 | 0.01781 | 0.0027857 | -0.012879 | -0.0019461 | -0.0039367 | 0.020692 | 0.01493 | -0.014041 | -0.01901 | 0.027621 | -0.0070751 | -0.082397 | -0.036621 | -0.054932 | 0.036621 | 0.16022 | 0 | 0.091553 | 3.0899 | 3.1128 | 2.9205 | 3.0716 | 3.1952 | 3.1265 | 3.1357 | 0.013733 | -122.1085 | -122.0352 | 0.22888 | 0.16022 | 0.068665 | 0.14649 | 0.054932 | 2.9892 | -118.959 | -119.0002 | 3.2639 | 3.2043 | 3.1952 | 0.21515 | 0.20599 | 0.21515 | 0.091553 | 0.27466 | 0.15106 | 0.018311 | 0.19226 | 0.032044 | 3.1815 | -122.1268 | -119.1513 | 0.10529 | 3.1403 | -0.013732 | 3.1586
5091.3438 | 122.2595 | -0.10071 | 122.1176 | -0.18898 | -0.038971 | 0.00088223 | 0.023364 | 0.0010767 | -0.009675 | -0.0081411 | -0.11075 | 0.022614 | 0.013862 | -0.010196 | -0.020292 | 0.02869 | -0.0015209 | -0.14648 | -0.004578 | -0.068665 | -0.11444 | -0.022888 | -0.14648 | -0.036621 | 2.9617 | 3.1219 | 2.8793 | 2.9984 | 3.0716 | 2.9938 | 3.067 | 0.032043 | -122.1222 | -122.2321 | 0.07782 | 0.064087 | -0.045776 | 0.032044 | -0.077819 | 2.98 | -118.9957 | -119.1193 | 3.1723 | 3.1677 | 3.0945 | 0.18768 | 0.11444 | 0.045777 | -0.045776 | 0.19226 | 0.11902 | 0.064087 | 0.24262 | 0.09613 | 3.2227 | -122.1863 | -119.2383 | -0.013733 | 3.0991 | -0.045776 | 3.0624
5093.0469 | 122.2 | -0.10986 | 122.1268 | -0.15846 | -0.039612 | 0.0023776 | 0.022509 | 0.0012903 | -0.010957 | -0.0036551 | -0.10159 | 0.026246 | 0.013221 | -0.012332 | -0.020292 | 0.027835 | -0.0030163 | -0.1236 | -0.009155 | -0.073242 | -0.073242 | 0 | -0.1236 | -0.032043 | 2.9709 | 3.1403 | 2.9022 | 2.9755 | 3.0441 | 2.948 | 3.0487 | 0.036621 | -122.1359 | -122.2 | 0.10986 | 0.07782 | -0.013733 | 0.041199 | -0.050354 | 3.0121 | -118.9865 | -119.1513 | 3.154 | 3.1586 | 3.0579 | 0.14648 | 0.045776 | 0.073242 | 0 | 0.14191 | 0.073242 | 0.064087 | 0.23804 | 0.10071 | 3.2501 | -122.2 | -119.2245 | 0.036621 | 3.0853 | -0.013733 | 3.0807
5094.8281 | 122.2275 | -0.10529 | 122.113 | -0.11269 | -0.041962 | 0.001523 | 0.021869 | -0.00084593 | -0.010316 | -0.0036551 | -0.080231 | 0.023682 | 0.013435 | -0.0063511 | -0.019224 | 0.02869 | -0.00066651 | -0.13275 | 0.018311 | -0.086975 | -0.10071 | -0.022888 | -0.1236 | -0.027466 | 2.916 | 3.1219 | 2.861 | 2.9526 | 3.0624 | 2.9617 | 3.0487 | 0.018311 | -122.0947 | -122.2137 | 0.082398 | 0.07782 | -0.01831 | 0.059509 | -0.036621 | 2.9663 | -118.9911 | -119.1605 | 3.1677 | 3.154 | 3.067 | 0.18768 | 0.10071 | 0.064087 | -0.013733 | 0.20142 | 0.091553 | 0.10529 | 0.26093 | 0.1236 | 3.2272 | -122.2 | -119.252 | 0.004578 | 3.0579 | -0.027465 | 3.0212
5096.6094 | 122.2092 | -0.13275 | 122.1085 | -0.18135 | -0.041107 | -0.00018577 | 0.019732 | -0.00063233 | -0.013093 | -0.0057913 | 0.0082703 | 0.022187 | 0.01728 | -0.014469 | -0.018583 | 0.025058 | -0.0030163 | -0.1236 | -0.032043 | -0.068665 | -0.059509 | 0.068665 | -0.068665 | 0.032043 | 2.948 | 3.0808 | 2.8748 | 2.916 | 3.035 | 2.9572 | 2.9984 | 0.064086 | -122.1405 | -122.168 | 0.20142 | 0.16479 | 0.064086 | 0.10071 | 0 | 3.0075 | -119.0277 | -119.1925 | 3.1677 | 3.1311 | 3.0899 | 0.1236 | 0.082397 | 0.13733 | 0.009156 | 0.16022 | 0.041199 | 0.036622 | 0.20599 | 0.10071 | 3.2135 | -122.1771 | -119.2337 | 0.073242 | 3.0487 | 0.009155 | 3.0807
5098.375 | 122.3053 | -0.068665 | 122.0718 | -0.16609 | -0.040894 | 0.0023776 | 0.021014 | 0.0015039 | -0.010743 | -0.0047231 | -0.046661 | 0.023896 | 0.014076 | -0.016605 | -0.018583 | 0.027194 | -0.0013073 | -0.07782 | -0.036621 | -0.045776 | 0.004578 | 0.11902 | -0.036621 | 0.054932 | 3.0258 | 3.0487 | 2.8885 | 3.0258 | 3.1128 | 3.035 | 3.0762 | 0.022889 | -122.1085 | -122.0673 | 0.18768 | 0.1236 | 0.032044 | 0.10071 | 0.009155 | 2.9572 | -119.0231 | -119.046 | 3.1815 | 3.1448 | 3.1036 | 0.18768 | 0.14648 | 0.16479 | 0.050354 | 0.2243 | 0.13733 | 0.009155 | 0.16022 | 0.032044 | 3.1174 | -122.1176 | -119.1833 | 0.073243 | 3.0945 | -0.009155 | 3.0945
5100.0781 | 122.2778 | -0.091553 | 122.0856 | -0.18898 | -0.040894 | 0.00024143 | 0.021228 | -0.0010595 | -0.011811 | -0.0051505 | -0.013092 | 0.023255 | 0.014289 | -0.010837 | -0.017301 | 0.027194 | -0.0032299 | -0.12817 | -0.036621 | -0.045776 | -0.045776 | 0.059509 | -0.082397 | 0.018311 | 2.9343 | 3.067 | 2.8427 | 2.9297 | 3.0487 | 2.9709 | 3.0258 | 0.045777 | -122.1222 | -122.1313 | 0.15106 | 0.10986 | 0.009156 | 0.064087 | -0.036621 | 2.9343 | -119.0186 | -119.1559 | 3.1403 | 3.1174 | 3.0624 | 0.18311 | 0.12817 | 0.10528 | 0 | 0.20599 | 0.086975 | 0.009155 | 0.2243 | 0.054932 | 3.1586 | -122.1313 | -119.2429 | 0.045777 | 3.0212 | -0.036621 | 3.0258
5101.8438 | 122.2183 | -0.10529 | 122.1176 | -0.1432 | -0.042603 | 0.001523 | 0.0208 | -0.00041873 | -0.013093 | -0.0038687 | -0.064972 | 0.02411 | 0.015357 | -0.0052829 | -0.019438 | 0.027194 | -0.0032299 | -0.14191 | 0.009155 | -0.10986 | -0.1236 | -0.022888 | -0.12817 | -0.032043 | 2.71 | 3.1036 | 2.8336 | 2.916 | 3.0075 | 2.9297 | 2.9984 | -0.004577 | -122.1085 | -122.2412 | 0.082398 | 0.073243 | -0.022888 | 0.07782 | -0.018311 | 2.9388 | -119.014 | -119.2017 | 3.1128 | 3.1036 | 3.035 | 0.1648 | 0.09613 | 0.086975 | -0.013733 | 0.17395 | 0.082398 | 0.11902 | 0.27008 | 0.11444 | 3.2089 | -122.2275 | -119.2841 | -0.01831 | 3.0212 | -0.036621 | 2.8152
5103.625 | 122.2733 | -0.09613 | 122.0627 | -0.19661 | -0.042816 | 0.0017368 | 0.019946 | -0.0010595 | -0.012879 | -0.0045095 | 0.026581 | 0.02176 | 0.016853 | -0.012546 | -0.018797 | 0.025058 | -0.0017347 | -0.12817 | -0.027466 | -0.064087 | -0.064087 | 0.045776 | -0.073242 | 0.027466 | 2.7283 | 2.9984 | 2.8061 | 2.9068 | 3.0121 | 2.9434 | 2.9938 | 0.032043 | -122.0901 | -122.1268 | 0.14191 | 0.1236 | 0.022888 | 0.091553 | -0.009155 | 2.9022 | -119.0643 | -119.1559 | 3.1082 | 3.0899 | 3.0396 | 0.18768 | 0.13733 | 0.10986 | 0 | 0.20599 | 0.10071 | 0.036621 | 0.19226 | 0.068664 | 3.0945 | -122.1268 | -119.2566 | 0.032043 | 3.0029 | -0.032044 | 2.8244
5105.3281 | 122.2366 | -0.10071 | 122.0856 | -0.15083 | -0.040467 | 0.0017368 | 0.021655 | 0.00086307 | -0.010102 | -0.0057913 | -0.089386 | 0.024537 | 0.01258 | -0.011051 | -0.019651 | 0.025272 | -0.0038709 | -0.15564 | 0.013733 | -0.09613 | -0.10071 | -0.018311 | -0.16022 | -0.032043 | 2.6596 | 3.0212 | 2.7786 | 2.8839 | 2.9434 | 2.8564 | 2.9617 | 0.004578 | -122.0718 | -122.1863 | 0.082397 | 0.068665 | -0.059509 | 0.064087 | -0.064087 | 2.8793 | -119.0643 | -119.2017 | 3.0441 | 3.0624 | 2.9572 | 0.18311 | 0.07782 | 0.077819 | -0.004578 | 0.1648 | 0.10529 | 0.10986 | 0.24262 | 0.11444 | 3.1219 | -122.1817 | -119.3069 | 0 | 2.9846 | -0.054932 | 2.7603
5107.0938 | 122.1634 | -0.1236 | 122.113 | -0.18898 | -0.039612 | 0.00045503 | 0.021655 | 8.47e-06 | -0.012666 | -0.0042959 | -0.10159 | 0.024323 | 0.014717 | -0.0076327 | -0.019224 | 0.028049 | -0.0051525 | -0.14191 | -0.018311 | -0.091553 | -0.1236 | -0.041199 | -0.18768 | -0.073242 | 2.5681 | 3.0075 | 2.7374 | 2.7786 | 2.8564 | 2.7786 | 2.8748 | 0.032043 | -122.1313 | -122.2366 | 0.082397 | 0.050354 | -0.064087 | 0.018311 | -0.09613 | 2.861 | -119.1055 | -119.3344 | 2.98 | 2.9984 | 2.9022 | 0.13733 | 0.041198 | 0.050354 | -0.032043 | 0.11902 | 0.041198 | 0.073242 | 0.27008 | 0.10528 | 3.1311 | -122.2046 | -119.3756 | 0 | 2.9022 | -0.018311 | 2.6917
5108.8594 | 122.2961 | -0.064087 | 122.0535 | -0.18135 | -0.042176 | 0.003232 | 0.016528 | -0.0049047 | -0.010957 | -0.0030141 | -0.013092 | 0.022187 | 0.015144 | -0.01041 | -0.019224 | 0.025699 | -0.0055799 | -0.09613 | -0.041199 | -0.054932 | 0.009155 | 0.1236 | -0.018311 | 0.064087 | 2.742 | 2.9892 | 2.8015 | 2.9068 | 3.0396 | 2.98 | 2.98 | 0.009155 | -122.0947 | -122.0444 | 0.18768 | 0.12817 | 0.045776 | 0.11902 | 0.036621 | 2.8656 | -119.0643 | -119.1467 | 3.1036 | 3.0441 | 3.0441 | 0.17853 | 0.17853 | 0.17853 | 0.064087 | 0.23804 | 0.10528 | 0.013733 | 0.18768 | 0.022888 | 3.0533 | -122.1085 | -119.252 | 0.073242 | 2.9709 | -0.032043 | 2.8061
5110.6406 | 122.2687 | -0.086975 | 122.0581 | -0.19661 | -0.04303 | 0.00024143 | 0.018237 | -0.00041873 | -0.01117 | -0.0036551 | -0.016144 | 0.023255 | 0.01493 | -0.013614 | -0.018156 | 0.026126 | -0.00045291 | -0.13275 | -0.022888 | -0.050354 | -0.059509 | 0.036621 | -0.091553 | 0.022888 | 2.6276 | 2.9526 | 2.7512 | 2.8427 | 2.9343 | 2.8976 | 2.9434 | 0.036621 | -122.081 | -122.1176 | 0.1236 | 0.10986 | -0.004578 | 0.073242 | -0.041199 | 2.8381 | -119.1055 | -119.2154 | 3.0212 | 3.0304 | 2.9846 | 0.19226 | 0.14648 | 0.086975 | -0.009155 | 0.1831 | 0.091552 | 0.027466 | 0.20142 | 0.064087 | 3.0396 | -122.1085 | -119.3069 | 0.027466 | 2.9297 | -0.045776 | 2.7145
5112.4062 | 122.2412 | -0.10071 | 122.081 | -0.19661 | -0.039826 | 0.00045503 | 0.021655 | -0.00084593 | -0.010957 | -0.0049367 | -0.068024 | 0.023682 | 0.013435 | -0.0095553 | -0.020292 | 0.025699 | -2.571e-05 | -0.12817 | -0.013733 | -0.10071 | -0.073242 | 0.036621 | -0.10986 | 0.004578 | 2.6871 | 2.9022 | 2.6779 | 2.7786 | 2.8519 | 2.774 | 2.8427 | 0 | -122.0947 | -122.1542 | 0.13733 | 0.10529 | -0.009155 | 0.10529 | -0.009155 | 2.7786 | -119.1788 | -119.3024 | 2.9526 | 2.9434 | 2.8748 | 0.1648 | 0.096131 | 0.13733 | 0.027466 | 0.17395 | 0.10071 | 0.086975 | 0.22431 | 0.086975 | 3.0029 | -122.1817 | -119.4031 | 0.027466 | 2.8793 | -0.027466 | 2.7878
5114.1094 | 122.2687 | -0.086975 | 122.0673 | -0.19661 | -0.04303 | 0.0010958 | 0.018878 | 0.0025721 | -0.013093 | -0.0068593 | -0.016144 | 0.023682 | 0.014717 | -0.0134 | -0.019865 | 0.025485 | -0.0019483 | -0.11444 | -0.045776 | -0.054932 | -0.032043 | 0.091553 | -0.07782 | 0.041199 | 2.6917 | 2.7969 | 2.6047 | 2.7191 | 2.8107 | 2.7512 | 2.7832 | 0.032043 | -122.113 | -122.0993 | 0.17853 | 0.12817 | 0.009155 | 0.096131 | -0.022888 | 2.6916 | -119.2703 | -119.3481 | 2.8976 | 2.8702 | 2.8381 | 0.17853 | 0.14649 | 0.14649 | 0.022889 | 0.20599 | 0.11444 | 0.009156 | 0.19226 | 0.041199 | 2.8839 | -122.1222 | -119.4626 | 0.054932 | 2.8061 | -0.027466 | 2.7786
5115.875 | 122.2046 | -0.11444 | 122.0947 | -0.17372 | -0.04068 | 0.00088223 | 0.025714 | 0.0015039 | -0.011811 | -0.0053641 | -0.11685 | 0.025605 | 0.015144 | -0.014255 | -0.020719 | 0.027621 | -0.0019483 | -0.15564 | 0 | -0.09613 | -0.12817 | -0.041199 | -0.17395 | -0.059509 | 2.4811 | 2.742 | 2.4719 | 2.5269 | 2.6001 | 2.5452 | 2.623 | 0.018311 | -122.0947 | -122.2229 | 0.073242 | 0.054932 | -0.059509 | 0.036621 | -0.07782 | 2.5864 | -119.3527 | -119.5679 | 2.7145 | 2.7374 | 2.6596 | 0.15106 | 0.073242 | 0.054931 | -0.032044 | 0.12817 | 0.054931 | 0.09613 | 0.27008 | 0.11444 | 2.8564 | -122.1909 | -119.6228 | -0.013733 | 2.6413 | -0.041199 | 2.5955
5117.6406 | 122.2046 | -0.11902 | 122.1039 | -0.20424 | -0.040253 | 0.00045503 | 0.023364 | 0.00086307 | -0.009675 | -0.0038687 | -0.092438 | 0.023469 | 0.015785 | -0.0069919 | -0.020292 | 0.025058 | -0.0028027 | -0.16937 | 0.009155 | -0.082397 | -0.11902 | -0.045776 | -0.17395 | -0.036621 | 2.4719 | 2.6779 | 2.4216 | 2.5131 | 2.5818 | 2.5131 | 2.6001 | 0.036622 | -122.0947 | -122.2229 | 0.073243 | 0.082398 | -0.054931 | 0.045776 | -0.091553 | 2.5406 | -119.426 | -119.5908 | 2.7008 | 2.7191 | 2.6321 | 0.17853 | 0.091553 | 0.036621 | -0.036622 | 0.16022 | 0.091553 | 0.091552 | 0.25635 | 0.12817 | 2.7969 | -122.1863 | -119.6823 | 0 | 2.6321 | -0.050354 | 2.5909
5119.3594 | 122.3053 | -0.073242 | 122.0627 | -0.20424 | -0.046021 | 0.00024143 | 0.019946 | 0.0023585 | -0.011598 | -0.0060049 | 0.023529 | 0.023682 | 0.015144 | -0.0181 | -0.017088 | 0.027408 | -0.0010937 | -0.14191 | -0.022888 | -0.073242 | -0.041199 | 0.082397 | -0.050354 | 0.045776 | 2.4902 | 2.6138 | 2.4124 | 2.5085 | 2.6367 | 2.5909 | 2.6184 | 0 | -122.0856 | -122.1039 | 0.15564 | 0.11902 | 0.022888 | 0.11902 | 0.022888 | 2.4857 | -119.4489 | -119.5541 | 2.71 | 2.6917 | 2.6642 | 0.20599 | 0.17853 | 0.15564 | 0.032043 | 0.2243 | 0.09613 | 0.050354 | 0.20142 | 0.050354 | 2.6871 | -122.1359 | -119.6503 | 0.032043 | 2.5818 | -0.068665 | 2.5635
5121.125 | 122.2733 | -0.091553 | 122.0581 | -0.18135 | -0.039826 | 0.00088223 | 0.020587 | 0.00064947 | -0.012666 | -0.0047231 | -0.04361 | 0.021332 | 0.016212 | -0.011692 | -0.020292 | 0.027835 | -0.0060071 | -0.091553 | -0.032043 | -0.050354 | 0.013733 | 0.11902 | -0.059509 | 0.050354 | 2.4719 | 2.5497 | 2.3712 | 2.4994 | 2.5909 | 2.5177 | 2.5726 | 0.041199 | -122.0901 | -122.0444 | 0.21057 | 0.14191 | 0.032044 | 0.10071 | -0.009155 | 2.4628 | -119.5084 | -119.5587 | 2.6825 | 2.6642 | 2.6093 | 0.20142 | 0.14648 | 0.16937 | 0.064087 | 0.21973 | 0.12817 | 0.018311 | 0.17853 | 0.05951 | 2.6413 | -122.1085 | -119.6869 | 0.10529 | 2.5909 | 0 | 2.5635
5122.8281 | 122.3145 | -0.082397 | 122.0444 | -0.22713 | -0.037476 | 0.0025912 | 0.0208 | 0.00086307 | -0.012025 | -0.0030141 | -0.071076 | 0.02176 | 0.014717 | -0.015537 | -0.020506 | 0.028476 | -0.0025891 | -0.073242 | -0.032043 | -0.054932 | -0.004578 | 0.10071 | -0.050354 | 0.064087 | 2.4536 | 2.4811 | 2.3071 | 2.449 | 2.5223 | 2.4628 | 2.5269 | 0.027465 | -122.0764 | -122.049 | 0.18311 | 0.14648 | 0.032043 | 0.11902 | 0.004578 | 2.3895 | -119.5633 | -119.5953 | 2.6047 | 2.6093 | 2.5452 | 0.21973 | 0.15564 | 0.15564 | 0.050354 | 0.21515 | 0.14191 | 0.022889 | 0.17395 | 0.050354 | 2.5635 | -122.0993 | -119.7372 | 0.077819 | 2.5314 | 0.009155 | 2.536
5124.5938 | 122.2092 | -0.11902 | 122.0856 | -0.15846 | -0.041107 | 0.001523 | 0.022723 | 0.00064947 | -0.012452 | -0.0062185 | -0.089386 | 0.02411 | 0.014289 | -0.016178 | -0.017942 | 0.02869 | -0.0040845 | -0.16022 | 0.009155 | -0.091553 | -0.1236 | -0.041199 | -0.1831 | -0.059509 | 2.2797 | 2.4948 | 2.2385 | 2.3026 | 2.3758 | 2.3026 | 2.3941 | 0.027466 | -122.0764 | -122.2092 | 0.07782 | 0.05951 | -0.064086 | 0.032044 | -0.091552 | 2.3575 | -119.5908 | -119.783 | 2.4948 | 2.5131 | 2.4216 | 0.15564 | 0.064087 | 0.050354 | -0.032043 | 0.13733 | 0.064087 | 0.10071 | 0.25635 | 0.12817 | 2.6138 | -122.1771 | -119.8471 | -0.004577 | 2.4216 | -0.041198 | 2.3987
5126.3594 | 122.1725 | -0.12817 | 122.1176 | -0.1432 | -0.041535 | -0.0018948 | 0.019946 | -0.0010595 | -0.014161 | -0.0023733 | -0.049713 | 0.023896 | 0.016426 | -0.0074191 | -0.01901 | 0.025272 | -0.0036573 | -0.16479 | 0 | -0.10071 | -0.10071 | -0.018311 | -0.11444 | -0.022888 | 2.2751 | 2.4811 | 2.2522 | 2.2659 | 2.3895 | 2.33 | 2.3804 | 0.027466 | -122.1176 | -122.2183 | 0.10986 | 0.10529 | 0.013733 | 0.07782 | -0.013733 | 2.3804 | -119.6365 | -119.8517 | 2.5177 | 2.5085 | 2.4582 | 0.12817 | 0.07782 | 0.082397 | 0 | 0.13733 | 0.013733 | 0.10071 | 0.22888 | 0.12817 | 2.6093 | -122.2183 | -119.8654 | 0.027466 | 2.3941 | -0.036621 | 2.4033
5128.0625 | 122.2916 | -0.068665 | 122.0673 | -0.16609 | -0.043244 | 2.7834e-05 | 0.021869 | 8.47e-06 | -0.011811 | -0.0049367 | -0.01004 | 0.022401 | 0.014076 | -0.011051 | -0.018369 | 0.026553 | -0.0034435 | -0.13733 | -0.013733 | -0.054932 | -0.050354 | 0.059509 | -0.07782 | 0.032043 | 2.3346 | 2.4353 | 2.243 | 2.3666 | 2.4811 | 2.4261 | 2.4445 | 0.013733 | -122.081 | -122.1176 | 0.12817 | 0.10071 | -0.009155 | 0.086975 | -0.022888 | 2.3117 | -119.632 | -119.7006 | 2.5497 | 2.5131 | 2.4948 | 0.20142 | 0.1831 | 0.11444 | 0.004578 | 0.23804 | 0.1236 | 0.041199 | 0.19226 | 0.054932 | 2.504 | -122.1222 | -119.8242 | 0.018311 | 2.4353 | -0.068664 | 2.4033
5129.7812 | 122.168 | -0.11444 | 122.0856 | -0.20424 | -0.038544 | -0.001254 | 0.021014 | 0.0012903 | -0.009675 | -0.0045095 | -0.1138 | 0.025605 | 0.015785 | -0.0097689 | -0.020719 | 0.027621 | -0.0025891 | -0.16022 | 0 | -0.09613 | -0.12817 | -0.059509 | -0.18768 | -0.054932 | 2.2293 | 2.4536 | 2.2018 | 2.2614 | 2.3254 | 2.2568 | 2.3529 | 0.018311 | -122.0856 | -122.2137 | 0.054932 | 0.059509 | -0.073242 | 0.041198 | -0.091553 | 2.3163 | -119.632 | -119.8242 | 2.4399 | 2.4673 | 2.3712 | 0.15106 | 0.054932 | 0.036621 | -0.032044 | 0.1236 | 0.05951 | 0.09613 | 0.25177 | 0.11444 | 2.5681 | -122.1817 | -119.8837 | -0.013733 | 2.3758 | -0.045776 | 2.3438
5131.5469 | 122.1817 | -0.10986 | 122.0901 | -0.12794 | -0.040467 | 0.00066863 | 0.021228 | 0.0029993 | -0.0094614 | -0.0017325 | -0.11075 | 0.024323 | 0.014076 | -0.01276 | -0.017942 | 0.026981 | 0.0016833 | -0.15564 | -0.013733 | -0.09613 | -0.1236 | -0.059509 | -0.18768 | -0.059509 | 2.1515 | 2.3895 | 2.124 | 2.2018 | 2.2522 | 2.1744 | 2.2888 | 0.013733 | -122.1039 | -122.2137 | 0.050354 | 0.050354 | -0.07782 | 0.036621 | -0.091553 | 2.2339 | -119.7006 | -119.8883 | 2.3621 | 2.3987 | 2.2842 | 0.16479 | 0.050354 | 0.036621 | -0.027466 | 0.12817 | 0.07782 | 0.082397 | 0.2655 | 0.09613 | 2.4994 | -122.1863 | -119.9661 | -0.013733 | 2.3117 | -0.045777 | 2.2614
5133.3281 | 122.1863 | -0.1236 | 122.113 | -0.10506 | -0.044312 | -0.00061317 | 0.018664 | 0.0010767 | -0.014161 | -0.0051505 | -0.046661 | 0.023896 | 0.014717 | -0.011478 | -0.019438 | 0.027408 | -0.0055799 | -0.17853 | 0.018311 | -0.09613 | -0.1236 | -0.027466 | -0.13275 | -0.036621 | 2.1103 | 2.3254 | 2.0691 | 2.1103 | 2.2156 | 2.1652 | 2.2247 | 0.027466 | -122.0947 | -122.2366 | 0.09613 | 0.086975 | -0.009155 | 0.059509 | -0.036621 | 2.1927 | -119.7876 | -120.0027 | 2.3392 | 2.3483 | 2.2888 | 0.15564 | 0.09613 | 0.068664 | -0.027466 | 0.14648 | 0.041199 | 0.11444 | 0.25635 | 0.14191 | 2.449 | -122.2092 | -120.0439 | 0 | 2.2339 | -0.054932 | 2.2339
5135.1094 | 122.3053 | -0.082397 | 122.081 | -0.13557 | -0.042176 | 2.7834e-05 | 0.018237 | -0.0034095 | -0.014161 | -0.0051505 | -0.0069885 | 0.023896 | 0.013862 | -0.019168 | -0.020292 | 0.026767 | -0.0066479 | -0.091553 | -0.027466 | -0.045776 | 0 | 0.14648 | 0 | 0.082397 | 2.3254 | 2.3392 | 2.1652 | 2.2797 | 2.417 | 2.3483 | 2.3666 | 0.036621 | -122.1085 | -122.081 | 0.22888 | 0.16479 | 0.082397 | 0.12817 | 0.045776 | 2.2476 | -119.7418 | -119.8013 | 2.4994 | 2.449 | 2.4307 | 0.20142 | 0.18311 | 0.19226 | 0.045776 | 0.25177 | 0.11444 | 0.01831 | 0.17395 | 0.054931 | 2.4216 | -122.1268 | -119.9158 | 0.082397 | 2.3621 | -0.009156 | 2.4078
5136.8281 | 122.287 | -0.064087 | 122.0627 | -0.13557 | -0.043671 | 0.0019504 | 0.018664 | -0.0029821 | -0.012239 | -0.0042959 | -0.019196 | 0.024537 | 0.014289 | -0.018741 | -0.020078 | 0.02399 | -0.0051525 | -0.091553 | -0.041199 | -0.041199 | 0.013733 | 0.12817 | 0 | 0.082397 | 2.2522 | 2.2614 | 2.1103 | 2.2064 | 2.3392 | 2.2797 | 2.3026 | 0.022888 | -122.1039 | -122.049 | 0.19226 | 0.14648 | 0.064087 | 0.1236 | 0.041199 | 2.1744 | -119.8013 | -119.8563 | 2.4033 | 2.3666 | 2.3438 | 0.19226 | 0.16937 | 0.16937 | 0.054932 | 0.22888 | 0.09613 | 0 | 0.15106 | 0.022888 | 2.3254 | -122.1039 | -119.9524 | 0.07782 | 2.2705 | -0.027466 | 2.3163
5138.5938 | 122.3007 | -0.050354 | 122.0627 | -0.21187 | -0.038117 | 0.00024143 | 0.021441 | 0.0051355 | -0.010743 | -0.00087794 | -0.086334 | 0.020692 | 0.016212 | -0.0078463 | -0.018369 | 0.025485 | -0.0062207 | -0.13275 | -0.013733 | -0.07782 | -0.032043 | 0.064087 | -0.068665 | 0.041199 | 2.2064 | 2.2476 | 2.0508 | 2.2018 | 2.2888 | 2.2064 | 2.2842 | -0.027466 | -122.0764 | -122.0947 | 0.11444 | 0.091553 | -0.018311 | 0.11902 | 0.009155 | 2.1011 | -119.8151 | -119.8608 | 2.3392 | 2.3346 | 2.2568 | 0.23346 | 0.15564 | 0.14191 | 0.045777 | 0.23804 | 0.15106 | 0.064087 | 0.19684 | 0.036621 | 2.298 | -122.1405 | -120.0119 | 0.018311 | 2.2522 | -0.082397 | 2.2568
5140.3594 | 122.2824 | -0.086975 | 122.0581 | -0.18898 | -0.040467 | 0.0025912 | 0.019732 | -0.00084593 | -0.01117 | -0.0042959 | -0.022247 | 0.022187 | 0.015144 | -0.017887 | -0.020292 | 0.026553 | -0.0025891 | -0.12817 | -0.027466 | -0.073242 | -0.041199 | 0.045776 | -0.068665 | 0.027466 | 2.1469 | 2.2522 | 2.0554 | 2.1423 | 2.2705 | 2.211 | 2.243 | 0.013733 | -122.0856 | -122.0993 | 0.13275 | 0.11444 | 0.01831 | 0.10071 | 0.004577 | 2.1423 | -119.8059 | -119.9158 | 2.3575 | 2.33 | 2.298 | 0.18768 | 0.15564 | 0.11902 | 0.032043 | 0.21515 | 0.086975 | 0.045776 | 0.19684 | 0.059509 | 2.3392 | -122.1313 | -120.0027 | 0.045776 | 2.2293 | -0.041199 | 2.2339
5142.0625 | 122.2824 | -0.073242 | 122.0673 | -0.18135 | -0.042389 | 2.7834e-05 | 0.019519 | 0.00064947 | -0.012239 | -0.0047231 | -0.034454 | 0.022614 | 0.015785 | -0.012546 | -0.020292 | 0.025485 | -0.00088011 | -0.09613 | -0.022888 | -0.064087 | 0.004578 | 0.10986 | -0.018311 | 0.082397 | 2.1744 | 2.2202 | 2.0462 | 2.1515 | 2.2842 | 2.2156 | 2.2385 | 0.009155 | -122.0901 | -122.0627 | 0.18311 | 0.15564 | 0.054931 | 0.14648 | 0.045776 | 2.1194 | -119.8471 | -119.9158 | 2.3575 | 2.3117 | 2.2888 | 0.19226 | 0.16937 | 0.17395 | 0.068665 | 0.23804 | 0.10529 | 0.041199 | 0.17395 | 0.050354 | 2.2934 | -122.1313 | -120.0211 | 0.07782 | 2.2247 | -0.022888 | 2.2476
5143.8281 | 122.168 | -0.11444 | 122.1039 | -0.17372 | -0.039398 | 0.00066863 | 0.023791 | 0.0012903 | -0.011598 | -0.0064321 | -0.13821 | 0.024323 | 0.014076 | -0.010837 | -0.020078 | 0.027835 | -0.0028027 | -0.10986 | -0.004578 | -0.073242 | -0.082397 | 0.004578 | -0.16937 | -0.036621 | 2.0416 | 2.2247 | 1.9867 | 2.0233 | 2.0874 | 2.0279 | 2.1011 | 0.041199 | -122.1085 | -122.1863 | 0.11902 | 0.07782 | -0.054932 | 0.036621 | -0.096131 | 2.1011 | -119.8792 | -120.0806 | 2.2018 | 2.2156 | 2.1423 | 0.11444 | 0.041199 | 0.07782 | -0.009155 | 0.10071 | 0.036621 | 0.068664 | 0.23804 | 0.10986 | 2.3392 | -122.1771 | -120.1172 | 0.032044 | 2.1378 | 0.004578 | 2.1561
5145.6094 | 122.2092 | -0.12817 | 122.1268 | -0.13557 | -0.040894 | -0.00018577 | 0.022937 | -0.00084593 | -0.013947 | -0.0053641 | -0.071076 | 0.025391 | 0.015571 | -0.013187 | -0.019438 | 0.025272 | -0.00023931 | -0.16479 | 0.018311 | -0.10529 | -0.11444 | -0.027466 | -0.14191 | -0.027466 | 1.9363 | 2.1561 | 1.9089 | 1.9592 | 2.0554 | 2.0142 | 2.0691 | 0.022888 | -122.1085 | -122.2412 | 0.10071 | 0.10071 | -0.013733 | 0.07782 | -0.036621 | 2.037 | -119.9707 | -120.1675 | 2.1835 | 2.1973 | 2.1423 | 0.16022 | 0.10528 | 0.07782 | -0.009155 | 0.14648 | 0.050354 | 0.1236 | 0.24719 | 0.14649 | 2.2842 | -122.2321 | -120.2179 | 0.013733 | 2.0874 | -0.036621 | 2.0645
5147.3281 | 122.2733 | -0.091553 | 122.0718 | -0.20424 | -0.041962 | -0.0025358 | 0.018451 | -0.0025549 | -0.012239 | -0.0049367 | -0.016144 | 0.023896 | 0.014717 | -0.019382 | -0.019224 | 0.02634 | -0.00066651 | -0.09613 | -0.032043 | -0.054932 | 0.013733 | 0.11444 | -0.032043 | 0.068665 | 2.0599 | 2.1057 | 1.9135 | 2.0279 | 2.1515 | 2.092 | 2.1149 | 0.036621 | -122.1039 | -122.0581 | 0.20599 | 0.16022 | 0.05951 | 0.1236 | 0.022889 | 2.005 | -119.9661 | -120.0439 | 2.243 | 2.2064 | 2.1835 | 0.20142 | 0.17853 | 0.16937 | 0.068665 | 0.23804 | 0.11444 | 0.022889 | 0.19226 | 0.05951 | 2.1973 | -122.1268 | -120.1584 | 0.10529 | 2.1194 | -0.004577 | 2.1515
5149.0938 | 122.2458 | -0.082397 | 122.0764 | -0.15846 | -0.042603 | 0.00024143 | 0.019946 | -0.0010595 | -0.01352 | -0.0038687 | -0.031403 | 0.023041 | 0.015357 | -0.012973 | -0.018583 | 0.023776 | -0.0013073 | -0.13275 | -0.027466 | -0.064087 | -0.054932 | 0.059509 | -0.082397 | 0.022888 | 1.9638 | 2.0828 | 1.9135 | 1.9913 | 2.0737 | 2.0233 | 2.0737 | 0.01831 | -122.1039 | -122.1313 | 0.14191 | 0.10528 | 0 | 0.086975 | -0.01831 | 1.9958 | -119.9936 | -120.0851 | 2.1561 | 2.1561 | 2.1057 | 0.16022 | 0.10986 | 0.1236 | 0.009155 | 0.16022 | 0.07782 | 0.036621 | 0.16937 | 0.054931 | 2.1652 | -122.1405 | -120.163 | 0.027465 | 2.0737 | -0.050354 | 2.0462
5150.8594 | 122.2183 | -0.10529 | 122.1039 | -0.12032 | -0.04303 | -0.0018948 | 0.021014 | 0.0034265 | -0.012239 | -0.0042959 | -0.10464 | 0.023469 | 0.016426 | -0.0097689 | -0.021574 | 0.028049 | -0.0036573 | -0.13275 | 0.004578 | -0.086975 | -0.082397 | -0.013733 | -0.11444 | -0.018311 | 1.9501 | 2.1149 | 1.8631 | 1.9592 | 2.0737 | 1.9867 | 2.0462 | 0.018311 | -122.0993 | -122.1863 | 0.091553 | 0.086975 | -0.009155 | 0.068664 | -0.027466 | 1.9684 | -119.989 | -120.1447 | 2.179 | 2.1515 | 2.092 | 0.18311 | 0.1236 | 0.073242 | 0.004578 | 0.21057 | 0.096131 | 0.091553 | 0.25177 | 0.10986 | 2.2202 | -122.1909 | -120.2408 | 0.022889 | 2.0645 | -0.027465 | 2.0554
5152.6406 | 122.2504 | -0.086975 | 122.0627 | -0.15846 | -0.040894 | -0.0023222 | 0.02016 | 0.0010767 | -0.011811 | -0.0053641 | -0.016144 | 0.022187 | 0.014076 | -0.018955 | -0.018369 | 0.026126 | -0.0047253 | -0.13733 | -0.027466 | -0.054932 | -0.050354 | 0.050354 | -0.07782 | 0.027466 | 2.0096 | 2.1149 | 1.9089 | 1.9913 | 2.0828 | 2.0416 | 2.0874 | 0.032043 | -122.0901 | -122.113 | 0.13733 | 0.11444 | 0.009155 | 0.082398 | -0.022888 | 1.9959 | -119.9478 | -120.0714 | 2.1698 | 2.1744 | 2.1286 | 0.17853 | 0.13275 | 0.10529 | 0.004578 | 0.17395 | 0.082397 | 0.027466 | 0.20599 | 0.059509 | 2.2018 | -122.1176 | -120.1538 | 0.036621 | 2.0782 | -0.050354 | 2.0966
5154.4219 | 122.3053 | -0.07782 | 122.0581 | -0.1432 | -0.043457 | 0.00024143 | 0.019305 | -0.0027685 | -0.013093 | -0.0094229 | -0.013092 | 0.021973 | 0.015357 | -0.016818 | -0.019651 | 0.028476 | -0.0025891 | -0.091553 | -0.036621 | -0.050354 | 0.027466 | 0.13733 | -0.004578 | 0.10071 | 2.0782 | 2.0782 | 1.8997 | 2.0187 | 2.1469 | 2.0874 | 2.1057 | 0.027466 | -122.0947 | -122.0306 | 0.21515 | 0.17853 | 0.073242 | 0.15106 | 0.045776 | 1.9775 | -119.9799 | -120.0394 | 2.2247 | 2.1835 | 2.1652 | 0.20599 | 0.18768 | 0.18768 | 0.07782 | 0.24719 | 0.11902 | 0.013733 | 0.17853 | 0.041199 | 2.1561 | -122.1085 | -120.1584 | 0.10529 | 2.0966 | -0.013733 | 2.1561
5156.125 | 122.2641 | -0.073242 | 122.0673 | -0.25002 | -0.042389 | -0.001254 | 0.020587 | -0.0019141 | -0.013093 | -0.0051505 | -0.016144 | 0.02411 | 0.015357 | -0.015537 | -0.017729 | 0.026981 | -0.0015209 | -0.13275 | -0.018311 | -0.054932 | -0.064087 | 0.041199 | -0.09613 | 0.018311 | 1.9409 | 2.0599 | 1.8585 | 1.9455 | 2.0554 | 2.0004 | 2.0325 | 0.01831 | -122.0856 | -122.1313 | 0.11444 | 0.091553 | -0.022888 | 0.073243 | -0.041198 | 1.9318 | -120.0073 | -120.1218 | 2.1286 | 2.1057 | 2.0737 | 0.17395 | 0.14191 | 0.096131 | -0.009155 | 0.19684 | 0.086975 | 0.036621 | 0.20142 | 0.054931 | 2.1332 | -122.1222 | -120.2087 | 0.009155 | 2.0187 | -0.059509 | 2.0142
5157.8906 | 122.1588 | -0.12817 | 122.1085 | -0.22713 | -0.041107 | 0.0013094 | 0.021869 | 0.00064947 | -0.012879 | -0.0085683 | -0.12906 | 0.024964 | 0.016639 | -0.014255 | -0.020506 | 0.027408 | -0.0032299 | -0.13733 | 0.004578 | -0.082397 | -0.11902 | -0.041199 | -0.17395 | -0.059509 | 1.8631 | 2.1286 | 1.8723 | 1.9089 | 1.9775 | 1.9043 | 1.9958 | 0.045777 | -122.1039 | -122.2275 | 0.086975 | 0.068665 | -0.045776 | 0.022888 | -0.091553 | 2.0004 | -119.9799 | -120.1996 | 2.1057 | 2.124 | 2.0325 | 0.1236 | 0.032044 | 0.041198 | -0.036622 | 0.10529 | 0.036622 | 0.086975 | 0.25635 | 0.13275 | 2.2568 | -122.1909 | -120.2362 | 0.009155 | 2.037 | -0.009155 | 1.9913
5159.6562 | 122.2824 | -0.064087 | 122.0398 | -0.23476 | -0.037476 | 0.00066863 | 0.020587 | -0.0017005 | -0.011598 | -0.0057913 | -0.037506 | 0.02176 | 0.014289 | -0.014041 | -0.01901 | 0.025485 | -0.0034435 | -0.07782 | -0.041199 | -0.054932 | 0.013733 | 0.13275 | -0.036621 | 0.054932 | 2.0187 | 2.0233 | 1.8539 | 1.9913 | 2.092 | 2.0142 | 2.0554 | 0.009155 | -122.081 | -122.0261 | 0.19684 | 0.11902 | 0.027466 | 0.10986 | 0.018311 | 1.918 | -120.0165 | -120.0485 | 2.1561 | 2.1194 | 2.0782 | 0.20142 | 0.16022 | 0.18768 | 0.068665 | 0.23804 | 0.13733 | 0.013733 | 0.16937 | 0.022888 | 2.0874 | -122.0947 | -120.1859 | 0.07782 | 2.0554 | -0.013733 | 2.0828
5161.4219 | 122.3053 | -0.054932 | 122.0398 | -0.15846 | -0.043457 | 0.00066863 | 0.018664 | 0.0015039 | -0.01352 | -0.0036551 | -0.013092 | 0.021973 | 0.015571 | -0.018741 | -0.018797 | 0.025272 | -0.0045117 | -0.091553 | -0.045776 | -0.045776 | 0.013733 | 0.14648 | -0.004578 | 0.09613 | 1.9821 | 1.9821 | 1.8311 | 1.9592 | 2.092 | 2.0416 | 2.0416 | 0.009156 | -122.0856 | -122.0261 | 0.20142 | 0.15106 | 0.050354 | 0.14191 | 0.041198 | 1.886 | -120.0577 | -120.0806 | 2.1469 | 2.0966 | 2.0966 | 0.21057 | 0.21057 | 0.19226 | 0.059509 | 0.26092 | 0.12817 | 0 | 0.15106 | 0.009156 | 2.037 | -122.0856 | -120.2087 | 0.068665 | 2.0142 | -0.036621 | 2.037
5163.125 | 122.2366 | -0.086975 | 122.0627 | -0.16609 | -0.040253 | 2.7834e-05 | 0.02016 | -0.0027685 | -0.011384 | -0.0049367 | -0.034454 | 0.022401 | 0.016212 | -0.01575 | -0.020078 | 0.027621 | -0.0019483 | -0.1236 | -0.036621 | -0.041199 | -0.036621 | 0.054932 | -0.082397 | 0.018311 | 1.8951 | 2.0096 | 1.8127 | 1.9043 | 1.9913 | 1.9318 | 1.9913 | 0.045776 | -122.0993 | -122.0993 | 0.14191 | 0.10529 | 0.004578 | 0.05951 | -0.041198 | 1.8997 | -120.0531 | -120.1584 | 2.0782 | 2.0782 | 2.0187 | 0.17853 | 0.11902 | 0.096131 | 0.004578 | 0.17853 | 0.091553 | 0.004578 | 0.19684 | 0.050354 | 2.0966 | -122.1039 | -120.2499 | 0.050354 | 1.9913 | -0.036621 | 1.9821
5164.8906 | 122.2595 | -0.064087 | 122.0535 | -0.16609 | -0.042389 | 0.00024143 | 0.019732 | -0.0010595 | -0.015229 | -0.0055777 | -0.028351 | 0.023682 | 0.015571 | -0.017246 | -0.019438 | 0.026767 | -0.0032299 | -0.1236 | -0.032043 | -0.064087 | -0.045776 | 0.041199 | -0.09613 | 0.032043 | 1.8951 | 2.0187 | 1.8311 | 1.9089 | 2.0142 | 1.9547 | 2.005 | 0 | -122.0856 | -122.0993 | 0.10529 | 0.09613 | -0.032043 | 0.09613 | -0.032043 | 1.8951 | -120.0348 | -120.1447 | 2.0782 | 2.0691 | 2.0187 | 0.17395 | 0.1236 | 0.10529 | 0.018311 | 0.1831 | 0.07782 | 0.032044 | 0.18768 | 0.032044 | 2.0828 | -122.1176 | -120.2225 | 0.018311 | 1.973 | -0.059509 | 1.9592
5166.6562 | 122.3007 | -0.073242 | 122.0535 | -0.21187 | -0.037689 | 0.00088223 | 0.023364 | 0.0015039 | -0.011384 | -0.0045095 | -0.092438 | 0.022187 | 0.015357 | -0.010623 | -0.019651 | 0.027194 | -0.0049389 | -0.050354 | -0.059509 | -0.041199 | 0.022888 | 0.12817 | -0.054932 | 0.054932 | 1.9638 | 1.9592 | 1.8127 | 1.9363 | 2.037 | 1.9547 | 2.005 | 0.032043 | -122.113 | -122.0306 | 0.20142 | 0.12817 | 0.01831 | 0.096131 | -0.013733 | 1.886 | -120.0943 | -120.1172 | 2.1103 | 2.0782 | 2.0279 | 0.19226 | 0.14191 | 0.16937 | 0.064087 | 0.2243 | 0.1236 | -0.01831 | 0.14649 | 0.013733 | 2.0325 | -122.0947 | -120.2408 | 0.09613 | 2.0096 | 0.022888 | 2.037
5168.4219 | 122.2961 | -0.07782 | 122.0444 | -0.2195 | -0.043457 | 0.00088223 | 0.0208 | -0.0034095 | -0.014588 | -0.0081411 | -0.031403 | 0.022828 | 0.013221 | -0.0072055 | -0.019224 | 0.027194 | -0.0042981 | -0.091553 | -0.041199 | -0.041199 | 0.018311 | 0.14191 | -0.009155 | 0.091553 | 1.973 | 1.9547 | 1.7807 | 1.9226 | 2.0416 | 1.9913 | 1.9913 | 0.036621 | -122.0856 | -122.0261 | 0.21973 | 0.16937 | 0.068665 | 0.13275 | 0.032044 | 1.8585 | -120.0897 | -120.1218 | 2.1194 | 2.0691 | 2.0691 | 0.21057 | 0.21057 | 0.18311 | 0.05951 | 0.26092 | 0.14191 | 0 | 0.17395 | 0.036621 | 2.0325 | -122.0856 | -120.2637 | 0.096131 | 2.0004 | -0.013733 | 2.0508
5170.1406 | 122.1863 | -0.10986 | 122.0718 | -0.18135 | -0.040894 | -0.0018948 | 0.020373 | -0.0012731 | -0.011811 | -0.0032277 | -0.10159 | 0.02475 | 0.013862 | -0.011905 | -0.018583 | 0.028262 | -0.0047253 | -0.16479 | 0.027466 | -0.09613 | -0.11444 | -0.032043 | -0.13275 | -0.013733 | 1.7624 | 1.9821 | 1.7395 | 1.7807 | 1.886 | 1.8219 | 1.8951 | 0.013733 | -122.0444 | -122.1863 | 0.07782 | 0.09613 | -0.022888 | 0.082397 | -0.036621 | 1.8494 | -120.0897 | -120.2911 | 1.9958 | 2.005 | 1.9318 | 0.15564 | 0.082397 | 0.064087 | -0.018311 | 0.14648 | 0.041199 | 0.1236 | 0.24261 | 0.13733 | 2.092 | -122.168 | -120.3323 | -0.004578 | 1.8906 | -0.054932 | 1.8723
5171.9219 | 122.2687 | -0.064087 | 122.0627 | -0.18898 | -0.042176 | 0.00045503 | 0.019732 | 0.0015039 | -0.01117 | -0.0045095 | -0.028351 | 0.02475 | 0.01258 | -0.010196 | -0.019651 | 0.025699 | -0.0023755 | -0.13275 | -0.018311 | -0.054932 | -0.054932 | 0.064087 | -0.073242 | 0.045776 | 1.8173 | 1.9318 | 1.7441 | 1.8539 | 1.9592 | 1.8997 | 1.9272 | 0.009155 | -122.081 | -122.1176 | 0.12817 | 0.10986 | -0.009155 | 0.10071 | -0.01831 | 1.8082 | -120.1309 | -120.2087 | 2.0233 | 1.9913 | 1.9638 | 0.1831 | 0.15564 | 0.11902 | 0 | 0.21515 | 0.10986 | 0.036621 | 0.18768 | 0.045776 | 1.9958 | -122.1176 | -120.3186 | 0.009155 | 1.918 | -0.068664 | 1.8814
5173.6875 | 122.2504 | -0.059509 | 122.0535 | -0.21187 | -0.041107 | 0.0023776 | 0.019305 | 0.0021447 | -0.012452 | -0.0045095 | -0.034454 | 0.023682 | 0.012794 | -0.014469 | -0.019438 | 0.026553 | 0.0025379 | -0.09613 | -0.027466 | -0.027466 | -0.027466 | 0.086975 | -0.068665 | 0.050354 | 1.8677 | 1.9318 | 1.7624 | 1.8494 | 1.9363 | 1.8951 | 1.9272 | 0.032043 | -122.081 | -122.081 | 0.14648 | 0.10986 | -0.009156 | 0.07782 | -0.041199 | 1.8219 | -120.1218 | -120.2042 | 1.9958 | 1.9867 | 1.9547 | 0.1648 | 0.13275 | 0.11444 | 0 | 0.17395 | 0.086975 | 0 | 0.16937 | 0.032043 | 1.9913 | -122.081 | -120.2911 | 0.032043 | 1.9089 | -0.036621 | 1.9272
5175.4531 | 122.1451 | -0.10529 | 122.081 | -0.18898 | -0.04068 | 0.00088223 | 0.023364 | 0.00043587 | -0.012452 | -0.0013051 | -0.14737 | 0.023682 | 0.013008 | -0.0076327 | -0.021574 | 0.025485 | -0.0060071 | -0.14191 | 0.009155 | -0.082397 | -0.14191 | -0.068665 | -0.18768 | -0.054932 | 1.7303 | 1.9684 | 1.712 | 1.7853 | 1.8265 | 1.7532 | 1.8494 | 0.022889 | -122.0718 | -122.2229 | 0.036621 | 0.050354 | -0.082397 | 0.027465 | -0.10529 | 1.8173 | -120.1126 | -120.2957 | 1.9318 | 1.9547 | 1.8585 | 0.13733 | 0.041199 | 0.013732 | -0.05951 | 0.11444 | 0.073242 | 0.091552 | 0.25635 | 0.11444 | 2.0737 | -122.1634 | -120.369 | -0.036621 | 1.8906 | -0.036621 | 1.8356
5177.1562 | 122.2275 | -0.07782 | 122.0627 | -0.17372 | -0.040039 | 0.00045503 | 0.019091 | 8.47e-06 | -0.010957 | -0.0051505 | -0.040558 | 0.025391 | 0.014503 | -0.019382 | -0.020078 | 0.026126 | -0.0028027 | -0.10529 | -0.004578 | -0.068665 | -0.022888 | 0.073242 | -0.073242 | 0.050354 | 1.8082 | 1.886 | 1.7029 | 1.8082 | 1.8997 | 1.8448 | 1.8723 | 0.009155 | -122.0673 | -122.0856 | 0.15106 | 0.12817 | 0.004578 | 0.11902 | -0.004577 | 1.7807 | -120.1767 | -120.2545 | 1.9775 | 1.9501 | 1.9226 | 0.16937 | 0.14191 | 0.14191 | 0.045777 | 0.19684 | 0.10529 | 0.064087 | 0.1831 | 0.073242 | 1.9638 | -122.1313 | -120.3598 | 0.054932 | 1.886 | -0.027466 | 1.886
5178.9219 | 122.1817 | -0.09613 | 122.0535 | -0.21187 | -0.042389 | 0.0013094 | 0.017382 | -0.0012731 | -0.013307 | -0.0070731 | -0.031403 | 0.02176 | 0.013221 | -0.013187 | -0.019865 | 0.026767 | -0.0057935 | -0.086975 | -0.022888 | -0.054932 | -0.022888 | 0.091553 | -0.050354 | 0.041199 | 1.8082 | 1.918 | 1.7303 | 1.7715 | 1.8631 | 1.799 | 1.8494 | 0.041198 | -122.0764 | -122.0764 | 0.18768 | 0.13733 | 0.045776 | 0.096131 | 0.004578 | 1.8265 | -120.1355 | -120.282 | 1.9592 | 1.9455 | 1.8951 | 0.11902 | 0.068664 | 0.14649 | 0.032044 | 0.13275 | 0.041198 | 0.032044 | 0.18768 | 0.073242 | 2.0142 | -122.1085 | -120.3232 | 0.073242 | 1.8677 | 0.009155 | 1.9043
5180.7031 | 122.2458 | -0.064087 | 122.0581 | -0.1432 | -0.044312 | -0.0016812 | 0.018878 | -0.0014867 | -0.012239 | -0.0062185 | -0.019196 | 0.021119 | 0.014289 | -0.018527 | -0.018156 | 0.027621 | -0.00066651 | -0.11444 | 0.004578 | -0.050354 | -0.032043 | 0.068665 | -0.050354 | 0.054932 | 1.8082 | 1.8951 | 1.7075 | 1.8219 | 1.9272 | 1.8677 | 1.8997 | 0.013733 | -122.0535 | -122.0901 | 0.13275 | 0.11902 | 0.013733 | 0.10529 | 0 | 1.7715 | -120.163 | -120.2362 | 1.9913 | 1.9638 | 1.9318 | 0.19226 | 0.16022 | 0.11902 | 0.018311 | 0.21973 | 0.11444 | 0.054932 | 0.18768 | 0.068665 | 1.9592 | -122.1085 | -120.3506 | 0.032044 | 1.886 | -0.050354 | 1.8723
5182.4219 | 122.2961 | -0.064087 | 122.0261 | -0.18135 | -0.042389 | 0.00066863 | 0.018664 | 0.0012903 | -0.013307 | -0.0021597 | -0.022247 | 0.023682 | 0.013221 | -0.016818 | -0.01901 | 0.025699 | -0.0040845 | -0.082397 | -0.036621 | -0.041199 | 0.041199 | 0.16022 | 0.013733 | 0.09613 | 1.8768 | 1.8631 | 1.712 | 1.8494 | 1.9775 | 1.9043 | 1.9043 | 0.022888 | -122.0627 | -121.9849 | 0.2243 | 0.16022 | 0.07782 | 0.13733 | 0.054932 | 1.7761 | -120.163 | -120.1767 | 2.0416 | 1.9684 | 1.9684 | 0.19226 | 0.19226 | 0.20142 | 0.082398 | 0.2655 | 0.13733 | 0.004578 | 0.15106 | 0.027466 | 1.9272 | -122.0673 | -120.314 | 0.10529 | 1.9135 | -0.01831 | 1.9409
5184.1875 | 122.1725 | -0.09613 | 122.0627 | -0.15846 | -0.040467 | 0.00045503 | 0.022082 | 0.0017175 | -0.012239 | -0.0042959 | -0.13516 | 0.024537 | 0.014289 | -0.0059237 | -0.020933 | 0.027835 | -0.0036573 | -0.091553 | 0.009155 | -0.059509 | -0.064087 | 0.050354 | -0.10071 | -0.009155 | 1.7395 | 1.886 | 1.6525 | 1.7212 | 1.7899 | 1.712 | 1.799 | 0.036621 | -122.0535 | -122.1268 | 0.14648 | 0.086975 | -0.004578 | 0.050354 | -0.041199 | 1.7487 | -120.1767 | -120.3415 | 1.886 | 1.8951 | 1.8082 | 0.14648 | 0.059509 | 0.10986 | -0.004578 | 0.13733 | 0.068664 | 0.068664 | 0.23346 | 0.10528 | 1.9821 | -122.1222 | -120.4102 | 0.032043 | 1.8173 | 0.004577 | 1.8356
5185.9531 | 122.1451 | -0.13733 | 122.0444 | -0.18135 | -0.041107 | 2.7834e-05 | 0.019732 | -0.0019141 | -0.013093 | -0.0053641 | -0.046661 | 0.022828 | 0.015571 | -0.0063511 | -0.019438 | 0.026767 | -0.0019483 | -0.1236 | 0.018311 | -0.059509 | -0.086975 | 0.032043 | -0.10071 | 0 | 1.6617 | 1.8494 | 1.5976 | 1.6525 | 1.7578 | 1.6937 | 1.7349 | 0.07782 | -122.0261 | -122.1313 | 0.16937 | 0.13733 | 0.036621 | 0.059509 | -0.041199 | 1.7349 | -120.195 | -120.3918 | 1.8951 | 1.8723 | 1.8311 | 0.13733 | 0.096131 | 0.091552 | -0.027466 | 0.16022 | 0.054932 | 0.07782 | 0.25177 | 0.15564 | 1.9867 | -122.1039 | -120.4468 | 0.050354 | 1.7899 | 0.013733 | 1.799
5187.7188 | 122.1542 | -0.09613 | 122.0306 | -0.19661 | -0.040467 | -0.00018577 | 0.023791 | 0.0034265 | -0.012879 | -0.0038687 | -0.1077 | 0.025178 | 0.016853 | -0.0046421 | -0.019651 | 0.027194 | -0.0017347 | -0.14191 | 0.032043 | -0.073242 | -0.11444 | -0.032043 | -0.16022 | -0.045776 | 1.6708 | 1.8631 | 1.6159 | 1.7029 | 1.7624 | 1.6937 | 1.7761 | 0.022888 | -121.9986 | -122.1451 | 0.064087 | 0.050354 | -0.064087 | 0.027466 | -0.086975 | 1.712 | -120.1675 | -120.3278 | 1.8585 | 1.8723 | 1.7899 | 0.16022 | 0.07782 | 0.041199 | -0.041199 | 0.14648 | 0.086975 | 0.10529 | 0.24719 | 0.12817 | 1.9592 | -122.1039 | -120.4147 | -0.018311 | 1.799 | -0.045777 | 1.767
5189.4219 | 122.1222 | -0.13275 | 122.0535 | -0.16609 | -0.043244 | 0.002164 | 0.019732 | 0.0015039 | -0.014588 | -0.0042959 | -0.049713 | 0.023896 | 0.015357 | -0.015537 | -0.017942 | 0.026981 | -0.0049389 | -0.15564 | 0.022888 | -0.082397 | -0.10529 | -0.004578 | -0.11444 | -0.018311 | 1.6342 | 1.8585 | 1.6113 | 1.6296 | 1.7578 | 1.6983 | 1.7441 | 0.050354 | -122.0306 | -122.1588 | 0.12817 | 0.11444 | 0.01831 | 0.064086 | -0.032044 | 1.7441 | -120.195 | -120.4239 | 1.8906 | 1.8768 | 1.8311 | 0.13275 | 0.086975 | 0.077819 | -0.022889 | 0.14648 | 0.018311 | 0.10528 | 0.24719 | 0.15564 | 1.9913 | -122.1359 | -120.4422 | 0.027465 | 1.7624 | -0.022889 | 1.767
5191.2031 | 122.2366 | -0.054932 | 122.0169 | -0.15083 | -0.04303 | -0.00082677 | 0.0208 | -0.0019141 | -0.010316 | -0.0057913 | 0.0082703 | 0.023255 | 0.015785 | -0.018955 | -0.018797 | 0.025485 | -0.0036573 | -0.12817 | -0.027466 | -0.045776 | -0.045776 | 0.07782 | -0.050354 | 0.059509 | 1.6891 | 1.767 | 1.5884 | 1.6891 | 1.8082 | 1.7441 | 1.7761 | 0.009156 | -122.0444 | -122.0627 | 0.13275 | 0.11444 | 0.004578 | 0.10528 | -0.004578 | 1.6434 | -120.2499 | -120.3278 | 1.8631 | 1.8311 | 1.799 | 0.18768 | 0.15564 | 0.1236 | 0 | 0.21973 | 0.10071 | 0.01831 | 0.17853 | 0.027466 | 1.8219 | -122.0627 | -120.4285 | 0.009156 | 1.7441 | -0.073242 | 1.7441
5192.9688 | 122.1313 | -0.1236 | 122.0444 | -0.17372 | -0.039612 | 0.00066863 | 0.023578 | 0.0051355 | -0.01053 | -0.0034415 | -0.12296 | 0.024964 | 0.015144 | -0.0093417 | -0.02136 | 0.02869 | -0.0036573 | -0.14648 | 0.013733 | -0.082397 | -0.10529 | -0.050354 | -0.17395 | -0.050354 | 1.593 | 1.7944 | 1.5839 | 1.6388 | 1.6754 | 1.6205 | 1.7303 | 0.041199 | -122.0306 | -122.1497 | 0.073242 | 0.073242 | -0.050354 | 0.032043 | -0.091553 | 1.7075 | -120.2499 | -120.4056 | 1.799 | 1.8539 | 1.7441 | 0.14648 | 0.036621 | 0.032043 | -0.022889 | 0.091553 | 0.054932 | 0.09613 | 0.21057 | 0.13733 | 1.918 | -122.1268 | -120.4605 | 0.01831 | 1.7624 | -0.022888 | 1.7166
5194.7344 | 122.2641 | -0.068665 | 122.0078 | -0.15083 | -0.043457 | -0.00082677 | 0.019732 | -0.0017005 | -0.012666 | -0.0072867 | 0.017425 | 0.02411 | 0.014076 | -0.02045 | -0.020506 | 0.025912 | -0.0042981 | -0.11444 | -0.018311 | -0.050354 | -0.004578 | 0.13275 | -0.004578 | 0.09613 | 1.7166 | 1.7349 | 1.5656 | 1.6937 | 1.8127 | 1.7715 | 1.7807 | 0.018311 | -122.0261 | -122.0123 | 0.20142 | 0.16479 | 0.064087 | 0.14648 | 0.045776 | 1.6342 | -120.2728 | -120.314 | 1.8814 | 1.8494 | 1.8402 | 0.21515 | 0.20599 | 0.18311 | 0.045776 | 0.24719 | 0.12817 | 0.032043 | 0.16937 | 0.050354 | 1.8036 | -122.0581 | -120.4422 | 0.064087 | 1.7624 | -0.045776 | 1.7853
5196.4531 | 122.1405 | -0.10986 | 122.0535 | -0.18135 | -0.041962 | 2.7834e-05 | 0.020373 | -0.0029821 | -0.012879 | -0.0051505 | -0.04361 | 0.022401 | 0.015571 | -0.0134 | -0.017088 | 0.02869 | -0.0055799 | -0.13733 | -0.009155 | -0.091553 | -0.082397 | 0.004578 | -0.10986 | -0.018311 | 1.561 | 1.7624 | 1.5244 | 1.5518 | 1.6754 | 1.6113 | 1.6479 | 0.01831 | -122.0627 | -122.1359 | 0.11444 | 0.091552 | 0 | 0.073242 | -0.01831 | 1.6342 | -120.2911 | -120.5017 | 1.7853 | 1.7578 | 1.7212 | 0.1236 | 0.086975 | 0.096131 | 0.009156 | 0.15106 | 0.027466 | 0.082398 | 0.23804 | 0.10071 | 1.8723 | -122.1451 | -120.5292 | 0.027466 | 1.6617 | -0.027466 | 1.6708
5198.2188 | 122.1909 | -0.082397 | 122.0215 | -0.17372 | -0.041321 | 0.00066863 | 0.018664 | 0.0017175 | -0.0083932 | -0.0057913 | 0.0052185 | 0.02176 | 0.016639 | -0.023014 | -0.020933 | 0.027194 | -0.0038709 | -0.1236 | 0 | -0.054932 | -0.054932 | 0.050354 | -0.086975 | 0.036621 | 1.6388 | 1.7441 | 1.561 | 1.6525 | 1.7487 | 1.6937 | 1.7441 | 0.027465 | -122.0215 | -122.0764 | 0.13275 | 0.11902 | -0.004578 | 0.091553 | -0.032043 | 1.6434 | -120.2774 | -120.369 | 1.8311 | 1.8265 | 1.7761 | 0.18311 | 0.13275 | 0.10529 | 0 | 0.18768 | 0.091553 | 0.054932 | 0.18311 | 0.082397 | 1.8265 | -122.0764 | -120.4605 | 0.027465 | 1.7349 | -0.041199 | 1.7212
5199.9844 | 122.2504 | -0.045776 | 122.0306 | -0.19661 | -0.040253 | 0.0028048 | 0.02016 | 0.00086307 | -0.014161 | -0.0057913 | -0.016144 | 0.023255 | 0.013862 | -0.0069919 | -0.019865 | 0.02399 | -0.0019483 | -0.054932 | -0.022888 | -0.041199 | 0.036621 | 0.15106 | 0.022888 | 0.10529 | 1.7303 | 1.7349 | 1.561 | 1.6846 | 1.8219 | 1.7441 | 1.7578 | 0.004577 | -122.0535 | -121.994 | 0.19684 | 0.15106 | 0.068664 | 0.14649 | 0.064087 | 1.6068 | -120.2957 | -120.3461 | 1.8677 | 1.8036 | 1.7899 | 0.19684 | 0.18311 | 0.19226 | 0.07782 | 0.26092 | 0.1236 | 0.018311 | 0.17395 | 0.022888 | 1.7807 | -122.0718 | -120.4697 | 0.082397 | 1.7303 | -0.009156 | 1.7761
5201.7031 | 122.2504 | -0.064087 | 121.9986 | -0.17372 | -0.042816 | -0.00061317 | 0.020373 | -0.0010595 | -0.012239 | -0.0028005 | -0.0039367 | 0.02411 | 0.014717 | -0.013614 | -0.022001 | 0.024204 | 0.0016833 | -0.082397 | -0.036621 | -0.041199 | 0.027466 | 0.14648 | 0 | 0.10071 | 1.68 | 1.6937 | 1.5244 | 1.6479 | 1.7487 | 1.6983 | 1.7166 | 0.022888 | -122.0352 | -121.9711 | 0.21057 | 0.1648 | 0.064087 | 0.14191 | 0.041199 | 1.5884 | -120.3049 | -120.3506 | 1.8127 | 1.7807 | 1.7624 | 0.19226 | 0.17395 | 0.18768 | 0.068665 | 0.2243 | 0.1236 | 0.004578 | 0.16937 | 0.027466 | 1.7578 | -122.0398 | -120.4742 | 0.091553 | 1.712 | -0.01831 | 1.7441
5203.4688 | 122.1451 | -0.10529 | 122.0627 | -0.19661 | -0.040039 | -0.0010404 | 0.022509 | 0.00086307 | -0.01053 | -0.0068593 | -0.14432 | 0.023255 | 0.017494 | -0.0082737 | -0.020292 | 0.027194 | -0.0038709 | -0.13275 | 0.022888 | -0.073242 | -0.09613 | -0.018311 | -0.15564 | -0.045776 | 1.5335 | 1.712 | 1.4923 | 1.5518 | 1.6067 | 1.5427 | 1.6342 | 0.032044 | -122.0398 | -122.1588 | 0.086975 | 0.05951 | -0.050354 | 0.027466 | -0.082398 | 1.5976 | -120.3506 | -120.5109 | 1.712 | 1.7395 | 1.648 | 0.14191 | 0.050354 | 0.054931 | -0.022888 | 0.11444 | 0.059509 | 0.09613 | 0.21973 | 0.12817 | 1.8173 | -122.1359 | -120.5704 | 0.009156 | 1.6571 | -0.027465 | 1.6388
5205.1719 | 122.2183 | -0.068665 | 122.0215 | -0.18898 | -0.038758 | -0.001254 | 0.023364 | 0.00086307 | -0.010743 | -0.0057913 | -0.080231 | 0.024537 | 0.015357 | -0.0084873 | -0.020292 | 0.027621 | -0.0021619 | -0.11902 | 0.013733 | -0.050354 | -0.045776 | 0.050354 | -0.09613 | 0.027466 | 1.6159 | 1.6754 | 1.4969 | 1.6342 | 1.7029 | 1.6434 | 1.7075 | 0.018311 | -122.0078 | -122.0673 | 0.11902 | 0.096131 | -0.027465 | 0.07782 | -0.045776 | 1.5656 | -120.3461 | -120.3873 | 1.7715 | 1.7761 | 1.712 | 0.21057 | 0.14648 | 0.10071 | 0.004578 | 0.20599 | 0.13733 | 0.064087 | 0.17853 | 0.082398 | 1.7441 | -122.0718 | -120.5246 | 0.022889 | 1.7029 | -0.050354 | 1.6846
5206.9375 | 122.2504 | -0.045776 | 121.9986 | -0.19661 | -0.041535 | 0.001523 | 0.022723 | 0.0021447 | -0.01053 | -0.0010915 | -0.092438 | 0.024323 | 0.014717 | -0.0093417 | -0.017942 | 0.026981 | -0.0042981 | -0.086975 | -0.004578 | -0.036621 | 0 | 0.091553 | -0.07782 | 0.059509 | 1.6251 | 1.6479 | 1.4877 | 1.6296 | 1.6937 | 1.6205 | 1.7075 | 0.009155 | -122.0032 | -121.9986 | 0.13733 | 0.10528 | -0.032044 | 0.09613 | -0.041199 | 1.5335 | -120.3506 | -120.369 | 1.7395 | 1.7532 | 1.6663 | 0.21973 | 0.13275 | 0.12817 | 0.036621 | 0.20599 | 0.14191 | 0.032043 | 0.16022 | 0.041198 | 1.6937 | -122.0352 | -120.5109 | 0.045776 | 1.6754 | -0.041199 | 1.6708
5208.7031 | 122.2412 | -0.064087 | 122.0261 | -0.11269 | -0.044312 | 0.00066863 | 0.019091 | -0.00084593 | -0.015229 | -0.0032277 | -0.025299 | 0.023469 | 0.013008 | -0.015537 | -0.018369 | 0.026553 | -0.0032299 | -0.073242 | -0.013733 | -0.045776 | 0.036621 | 0.15564 | 0.018311 | 0.10071 | 1.6342 | 1.6251 | 1.4694 | 1.593 | 1.7349 | 1.6663 | 1.68 | 0.018311 | -122.0398 | -121.9894 | 0.21973 | 0.1648 | 0.082398 | 0.14648 | 0.064087 | 1.5335 | -120.401 | -120.433 | 1.799 | 1.7441 | 1.7303 | 0.21057 | 0.19684 | 0.20142 | 0.082397 | 0.2655 | 0.1236 | 0.032043 | 0.15564 | 0.050354 | 1.6891 | -122.0718 | -120.5566 | 0.10071 | 1.6571 | -0.009155 | 1.6983
5210.5781 | 122.2 | -0.073242 | 121.9711 | -0.18898 | -0.039398 | 0.00024143 | 0.021441 | -0.0010595 | -0.013307 | -0.0034415 | -0.052765 | 0.023682 | 0.015144 | -0.012973 | -0.019865 | 0.025058 | -0.0019483 | -0.082397 | -0.027466 | -0.045776 | 0.009155 | 0.11444 | -0.050354 | 0.064087 | 1.5976 | 1.6159 | 1.4603 | 1.5701 | 1.6525 | 1.5976 | 1.6296 | 0.027466 | -121.9986 | -121.962 | 0.18768 | 0.13733 | 0.022888 | 0.10986 | -0.004578 | 1.5335 | -120.3552 | -120.401 | 1.7258 | 1.7029 | 1.6708 | 0.16937 | 0.13733 | 0.16022 | 0.054931 | 0.19226 | 0.10986 | 0.01831 | 0.15564 | 0.045776 | 1.6891 | -122.0169 | -120.5109 | 0.082397 | 1.6434 | -0.009155 | 1.6708
5212.375 | 122.0993 | -0.11902 | 122.0169 | -0.1432 | -0.041107 | -0.0021084 | 0.021655 | -0.0034095 | -0.014802 | -0.0045095 | -0.06192 | 0.02411 | 0.017921 | -0.010623 | -0.017942 | 0.024204 | -0.0036573 | -0.14648 | 0.004578 | -0.064087 | -0.086975 | 0.004578 | -0.11444 | -0.004578 | 1.4191 | 1.6251 | 1.3916 | 1.4282 | 1.5198 | 1.4694 | 1.5152 | 0.054932 | -122.0123 | -122.1039 | 0.1236 | 0.11444 | 0.004578 | 0.059509 | -0.050354 | 1.5106 | -120.3918 | -120.5887 | 1.6388 | 1.6342 | 1.5884 | 0.1236 | 0.077819 | 0.068665 | -0.022888 | 0.12817 | 0.036621 | 0.068665 | 0.23346 | 0.1236 | 1.7441 | -122.081 | -120.6253 | 0.032044 | 1.5472 | -0.027465 | 1.5381
5214.0938 | 122.0947 | -0.11444 | 122.0306 | -0.11269 | -0.042389 | -0.0023222 | 0.02016 | -0.0010595 | -0.012239 | -0.0038687 | -0.064972 | 0.024323 | 0.015998 | -0.011905 | -0.017301 | 0.026553 | -0.0036573 | -0.16022 | 0.027466 | -0.086975 | -0.09613 | 0.004578 | -0.1236 | -0.022888 | 1.4282 | 1.6251 | 1.3824 | 1.4008 | 1.4969 | 1.4465 | 1.5106 | 0.027466 | -122.0032 | -122.1268 | 0.11902 | 0.091553 | -0.009155 | 0.064087 | -0.036621 | 1.4969 | -120.4056 | -120.6299 | 1.6113 | 1.6251 | 1.561 | 0.12817 | 0.064087 | 0.091553 | -0.009155 | 0.11444 | 0.018311 | 0.11444 | 0.24262 | 0.14191 | 1.7395 | -122.1176 | -120.6482 | 0.018311 | 1.5152 | -0.045776 | 1.5427
5215.7969 | 122.1405 | -0.07782 | 122.0169 | -0.12794 | -0.041748 | -0.00018577 | 0.021441 | 0.0025721 | -0.012025 | -0.0034415 | -0.09549 | 0.023682 | 0.015357 | -0.011264 | -0.020506 | 0.027408 | -0.0072889 | -0.10529 | 0.013733 | -0.064087 | -0.041199 | 0.050354 | -0.10071 | 0.018311 | 1.7258 | 1.8356 | 1.6388 | 1.7258 | 1.8173 | 1.7441 | 1.7899 | 0.013733 | -122.0032 | -122.0581 | 0.12817 | 0.096131 | -0.022888 | 0.082398 | -0.036621 | 1.7166 | -120.1813 | -120.2911 | 1.8951 | 1.8677 | 1.8219 | 0.15106 | 0.10529 | 0.11444 | 0.022888 | 0.17853 | 0.086975 | 0.07782 | 0.19684 | 0.091553 | 1.9135 | -122.081 | -120.3781 | 0.036621 | 1.8036 | -0.027466 | 1.8036
5217.5312 | 122.1863 | -0.059509 | 121.9711 | -0.19661 | -0.040467 | 0.0010958 | 0.019091 | -0.0019141 | -0.011384 | -0.0034415 | 0.0021667 | 0.023896 | 0.017494 | -0.012973 | -0.018369 | 0.026767 | -0.0017347 | -0.13275 | 0.004578 | -0.041199 | -0.045776 | 0.082397 | -0.064087 | 0.050354 | 1.6937 | 1.7899 | 1.5839 | 1.7212 | 1.8127 | 1.7807 | 1.8082 | 0.01831 | -121.9666 | -122.0169 | 0.14191 | 0.10986 | -0.004578 | 0.091553 | -0.022888 | 1.6434 | -120.1813 | -120.2499 | 1.8723 | 1.8677 | 1.8402 | 0.2243 | 0.19684 | 0.1236 | -0.004577 | 0.22888 | 0.13733 | 0.045777 | 0.20599 | 0.064087 | 1.8494 | -122.0123 | -120.3873 | 0.013733 | 1.7807 | -0.073242 | 1.7532
5219.3594 | 122.2275 | -0.073242 | 121.9574 | -0.20424 | -0.040894 | 0.0017368 | 0.02016 | -0.00084593 | -0.010743 | -0.0032277 | -0.055817 | 0.022614 | 0.015144 | -0.012973 | -0.021147 | 0.027408 | -0.0057935 | -0.10071 | -0.004578 | -0.041199 | -0.004578 | 0.086975 | -0.091553 | 0.054932 | 1.6617 | 1.7166 | 1.5564 | 1.68 | 1.7532 | 1.6891 | 1.7578 | 0.032043 | -121.962 | -121.962 | 0.16022 | 0.12817 | -0.018311 | 0.096131 | -0.050354 | 1.6296 | -120.2408 | -120.2774 | 1.8265 | 1.8311 | 1.7624 | 0.20142 | 0.13275 | 0.12817 | 0.036621 | 0.19684 | 0.1236 | 0.036621 | 0.16022 | 0.068664 | 1.7899 | -121.9986 | -120.401 | 0.068664 | 1.7532 | -0.027466 | 1.7349
5221.1094 | 122.1451 | -0.064087 | 121.994 | -0.16609 | -0.041321 | 0.0010958 | 0.018664 | 8.47e-06 | -0.014161 | -0.0030141 | -0.031403 | 0.021119 | 0.014289 | -0.0074191 | -0.019224 | 0.02634 | -0.0066479 | -0.10071 | -0.009155 | -0.045776 | 0 | 0.10986 | -0.013733 | 0.073242 | 1.7258 | 1.7853 | 1.5976 | 1.68 | 1.799 | 1.7258 | 1.767 | 0.018311 | -122.0032 | -121.994 | 0.17395 | 0.13733 | 0.050354 | 0.11902 | 0.032043 | 1.6617 | -120.2087 | -120.314 | 1.8631 | 1.8311 | 1.7899 | 0.16937 | 0.12817 | 0.15564 | 0.045776 | 0.20142 | 0.082398 | 0.036621 | 0.18768 | 0.054932 | 1.8494 | -122.0398 | -120.3964 | 0.064087 | 1.7441 | -0.036621 | 1.7899
5222.875 | 122.0947 | -0.10529 | 122.0123 | -0.18898 | -0.039185 | -0.00061317 | 0.022296 | 0.0034265 | -0.013093 | -0.0032277 | -0.10159 | 0.024323 | 0.014503 | -0.0025059 | -0.018156 | 0.027621 | -0.0042981 | -0.10529 | 0.022888 | -0.068665 | -0.054932 | 0.045776 | -0.09613 | 0.009155 | 1.7303 | 1.8494 | 1.6434 | 1.7029 | 1.7807 | 1.712 | 1.7899 | 0.036621 | -121.9894 | -122.0673 | 0.15106 | 0.11444 | 0.009156 | 0.07782 | -0.027465 | 1.7487 | -120.163 | -120.3094 | 1.886 | 1.8951 | 1.8173 | 0.14648 | 0.068664 | 0.11444 | 0.013733 | 0.13733 | 0.059509 | 0.091553 | 0.20599 | 0.12817 | 1.9547 | -122.081 | -120.369 | 0.050354 | 1.8082 | 0 | 1.8356
5224.7031 | 122.1634 | -0.091553 | 121.9574 | -0.24239 | -0.04068 | 0.0013094 | 0.018664 | 0.0040675 | -0.012666 | -0.0057913 | 0.0082703 | 0.021546 | 0.015357 | -0.011905 | -0.017088 | 0.026126 | -0.0028027 | -0.13275 | -0.022888 | -0.032043 | -0.032043 | 0.068665 | -0.059509 | 0.045776 | 1.6983 | 1.7853 | 1.6067 | 1.6937 | 1.7944 | 1.7441 | 1.7899 | 0.05951 | -121.9803 | -121.9894 | 0.16022 | 0.13733 | 0.032044 | 0.077819 | -0.027466 | 1.6983 | -120.1721 | -120.2637 | 1.886 | 1.8814 | 1.8356 | 0.18311 | 0.13733 | 0.10071 | 0 | 0.18768 | 0.086976 | 0.009155 | 0.17853 | 0.068665 | 1.8768 | -121.9894 | -120.3506 | 0.05951 | 1.7853 | -0.041198 | 1.7899
5226.5 | 122.0764 | -0.11444 | 121.9711 | -0.16609 | -0.04068 | -0.0010404 | 0.021441 | -0.0021277 | -0.012239 | -0.0051505 | -0.055817 | 0.022828 | 0.015357 | -0.0080601 | -0.01901 | 0.026767 | -0.0028027 | -0.16479 | 0.018311 | -0.10071 | -0.12817 | -0.018311 | -0.12817 | -0.027466 | 1.5701 | 1.7807 | 1.5381 | 1.5976 | 1.6846 | 1.6296 | 1.7075 | 0.013733 | -121.9528 | -122.0993 | 0.09613 | 0.086975 | -0.013733 | 0.073242 | -0.027466 | 1.6525 | -120.1904 | -120.3735 | 1.799 | 1.8219 | 1.7441 | 0.16937 | 0.091553 | 0.082397 | -0.027466 | 0.14648 | 0.059509 | 0.11902 | 0.24262 | 0.13275 | 1.8951 | -122.0718 | -120.433 | -0.013733 | 1.712 | -0.050354 | 1.6846
5228.2969 | 121.0098 | -0.064087 | 120.7901 | -0.15846 | -0.041107 | 0.0034456 | 0.02016 | -0.0012731 | -0.012239 | -0.0051505 | 0.0052185 | 0.023255 | 0.015144 | -0.016391 | -0.019224 | 0.026553 | -0.0034435 | -0.1236 | -0.027466 | -0.064087 | -0.032043 | 0.059509 | -0.068665 | 0.032043 | 1.6479 | 1.7624 | 1.5701 | 1.6571 | 1.7487 | 1.7029 | 1.7532 | 0 | -120.8176 | -120.8221 | 0.1236 | 0.09613 | -0.004578 | 0.09613 | -0.004578 | 1.6342 | -119.0277 | -119.133 | 1.8127 | 1.8173 | 1.767 | 0.18311 | 0.13275 | 0.1236 | 0.032044 | 0.17853 | 0.086975 | 0.036621 | 0.19226 | 0.036621 | 1.8265 | -120.8542 | -119.22 | 0.032044 | 1.7212 | -0.059509 | 1.712
5230.0156 | 121.8475 | -0.073242 | 121.6461 | -0.18898 | -0.03833 | 0.00045503 | 0.0208 | -0.00084593 | -0.011384 | -0.0055777 | -0.037506 | 0.023469 | 0.01493 | -0.013614 | -0.020078 | 0.026126 | -0.0038709 | -0.086975 | -0.022888 | -0.036621 | -0.004578 | 0.11444 | -0.064087 | 0.073242 | 1.6754 | 1.712 | 1.5244 | 1.6388 | 1.7395 | 1.6708 | 1.7166 | 0.036621 | -121.669 | -121.6507 | 0.18768 | 0.14648 | 0.009155 | 0.10986 | -0.027466 | 1.5976 | -119.9341 | -120.0073 | 1.8127 | 1.7899 | 1.7441 | 0.19226 | 0.14648 | 0.15106 | 0.032043 | 0.21515 | 0.11444 | 0.013733 | 0.18768 | 0.050354 | 1.7853 | -121.6827 | -120.1218 | 0.068664 | 1.712 | -0.013733 | 1.7487
5231.8125 | 121.9482 | -0.07782 | 121.7194 | -0.2195 | -0.040894 | 0.002164 | 0.019732 | -0.0019141 | -0.010743 | -0.0053641 | -0.049713 | 0.021973 | 0.015357 | -0.015323 | -0.020933 | 0.025699 | -0.00023931 | -0.082397 | -0.022888 | -0.041199 | 0.009155 | 0.12817 | -0.032043 | 0.064087 | 1.6891 | 1.712 | 1.5335 | 1.6434 | 1.7303 | 1.6708 | 1.7303 | 0.036621 | -121.7422 | -121.7102 | 0.20599 | 0.14191 | 0.045777 | 0.10529 | 0.009156 | 1.6113 | -120.0073 | -120.076 | 1.8082 | 1.8082 | 1.7487 | 0.19684 | 0.13733 | 0.16937 | 0.050354 | 0.19684 | 0.10986 | 0.018311 | 0.17853 | 0.054932 | 1.7899 | -121.7606 | -120.1859 | 0.086975 | 1.7212 | -0.004577 | 1.767
5233.6094 | 121.9254 | -0.11444 | 121.6095 | -0.20424 | -0.042176 | 0.00045503 | 0.0208 | -0.00041873 | -0.012879 | -0.00023714 | -0.01004 | 0.02411 | 0.014717 | -0.011905 | -0.018583 | 0.025912 | -0.0055799 | -0.10986 | -0.036621 | -0.050354 | -0.009155 | 0.11444 | -0.022888 | 0.07782 | 1.68 | 1.6983 | 1.5244 | 1.6617 | 1.767 | 1.712 | 1.7487 | 0.064087 | -121.6461 | -121.6187 | 0.22888 | 0.19226 | 0.091553 | 0.12817 | 0.027466 | 1.6388 | -119.9112 | -119.9478 | 1.8814 | 1.8631 | 1.8265 | 0.2243 | 0.18768 | 0.16479 | 0.041199 | 0.24262 | 0.13733 | 0.013733 | 0.17395 | 0.07782 | 1.8127 | -121.6599 | -120.0851 | 0.10529 | 1.7761 | 0.004578 | 1.7944
5235.375 | 121.8475 | -0.13275 | 121.6599 | -0.097427 | -0.04303 | 0.0028048 | 0.022723 | -0.0034095 | -0.012025 | -0.0023733 | -0.12601 | 0.025605 | 0.014076 | -0.0063511 | -0.020933 | 0.026553 | -0.0057935 | -0.11444 | 0 | -0.086975 | -0.054932 | 0.022888 | -0.10071 | -0.009155 | 1.5427 | 1.6846 | 1.4923 | 1.5472 | 1.6388 | 1.5793 | 1.6388 | 0.045776 | -121.6599 | -121.7148 | 0.15564 | 0.1236 | 0.032043 | 0.07782 | -0.013733 | 1.6251 | -119.9753 | -120.1126 | 1.7715 | 1.7715 | 1.712 | 0.14648 | 0.086975 | 0.10986 | 0.032043 | 0.14648 | 0.054931 | 0.086975 | 0.19226 | 0.13275 | 1.8173 | -121.7468 | -120.1675 | 0.077819 | 1.68 | 0.01831 | 1.6754
5237.125 | 121.8246 | -0.10986 | 121.7194 | -0.13557 | -0.04303 | -0.00082677 | 0.022082 | -0.00084593 | -0.014375 | -0.0025869 | -0.058869 | 0.02176 | 0.015571 | -0.0035739 | -0.019865 | 0.025058 | -0.0045117 | -0.17395 | 0.009155 | -0.086975 | -0.10986 | -0.009155 | -0.11444 | -0.004578 | 1.4786 | 1.7029 | 1.4832 | 1.4877 | 1.6022 | 1.5472 | 1.5976 | 0.022888 | -121.7102 | -121.8292 | 0.10071 | 0.10529 | -0.004578 | 0.082397 | -0.027466 | 1.593 | -120.0165 | -120.2316 | 1.712 | 1.7075 | 1.6571 | 0.11444 | 0.064087 | 0.07782 | -0.022888 | 0.11902 | 0.004578 | 0.09613 | 0.21973 | 0.11902 | 1.8127 | -121.8063 | -120.2362 | 0 | 1.5976 | -0.064087 | 1.5884
5238.9688 | 121.962 | -0.086975 | 121.6965 | -0.20424 | -0.039826 | 0.00088223 | 0.021655 | 0.00043587 | -0.010957 | -0.0049367 | -0.052765 | 0.023041 | 0.014503 | -0.015323 | -0.017729 | 0.027408 | -0.0040845 | -0.068665 | -0.013733 | -0.018311 | 0.018311 | 0.13275 | -0.050354 | 0.073242 | 1.6205 | 1.6205 | 1.474 | 1.6113 | 1.6846 | 1.6159 | 1.6617 | 0.068664 | -121.7102 | -121.6782 | 0.21973 | 0.16022 | 0.036621 | 0.091553 | -0.032043 | 1.561 | -120.076 | -120.0851 | 1.7715 | 1.7487 | 1.7029 | 0.18768 | 0.14191 | 0.15106 | 0.036622 | 0.21057 | 0.13733 | 0.004578 | 0.14648 | 0.073242 | 1.7075 | -121.7148 | -120.2225 | 0.10529 | 1.6983 | 0.01831 | 1.7075
5240.7031 | 121.8201 | -0.31586 | 121.5317 | -0.18135 | -0.041535 | 0.0017368 | 0.019946 | 0.0023585 | -0.012452 | -0.0034415 | -0.086334 | 0.023255 | 0.015144 | -0.013828 | -0.019224 | 0.025912 | -0.0019483 | -0.18768 | -0.036621 | -0.1236 | -0.14648 | -0.064087 | -0.16937 | -0.073242 | 1.4603 | 1.6525 | 1.4282 | 1.4648 | 1.5884 | 1.5244 | 1.5747 | 0.19226 | -121.5683 | -121.6782 | 0.25177 | 0.24261 | 0.14648 | 0.050354 | -0.045777 | 1.7441 | -119.8791 | -120.0668 | 1.9043 | 1.8906 | 1.8402 | 0.14648 | 0.09613 | 0.059509 | -0.022888 | 0.16022 | 0.036621 | 0.086975 | 0.2243 | 0.27924 | 1.9684 | -121.6553 | -120.1035 | 0.16937 | 1.7807 | 0.12817 | 1.7761
5242.4219 | 117.0181 | -0.1236 | 116.7114 | -0.21187 | -0.042603 | 0.00024143 | 0.018237 | -0.00084593 | -0.012879 | -0.0042959 | -0.0008851 | 0.023255 | 0.012367 | -0.013187 | -0.017729 | 0.027621 | -0.0047253 | -0.09613 | -0.041199 | -0.068665 | 0.018311 | 0.13733 | 0.004578 | 0.07782 | 1.5335 | 1.5381 | 1.387 | 1.5015 | 1.6296 | 1.561 | 1.5747 | 0.054931 | -116.7526 | -116.6931 | 0.26093 | 0.20142 | 0.12817 | 0.14649 | 0.073243 | 1.5106 | -115.1733 | -115.21 | 1.7532 | 1.6983 | 1.6846 | 0.18768 | 0.17395 | 0.20599 | 0.086976 | 0.24262 | 0.11444 | 0.027466 | 0.15106 | 0.082397 | 1.6617 | -116.7801 | -115.3244 | 0.14191 | 1.6251 | 0.027466 | 1.6571
5244.1719 | 121.5591 | -0.07782 | 121.3577 | -0.19661 | -0.040253 | -0.001254 | 0.021228 | -0.0019141 | -0.0098886 | -0.0051505 | -0.034454 | 0.023041 | 0.014076 | -0.016391 | -0.020506 | 0.027194 | -0.0025891 | -0.086975 | -0.018311 | -0.027466 | -0.022888 | 0.09613 | -0.073242 | 0.050354 | 1.5198 | 1.5884 | 1.4099 | 1.4969 | 1.5839 | 1.5381 | 1.5884 | 0.050354 | -121.376 | -121.3806 | 0.17395 | 0.12817 | 0.004578 | 0.07782 | -0.045776 | 1.4877 | -119.7693 | -119.8608 | 1.6617 | 1.6663 | 1.6159 | 0.17853 | 0.12817 | 0.1236 | 0.004578 | 0.17395 | 0.086975 | 0.009155 | 0.17853 | 0.059509 | 1.6663 | -121.3852 | -119.9478 | 0.054932 | 1.5747 | -0.009155 | 1.5976
5245.9062 | 121.6873 | -0.068665 | 121.463 | -0.21187 | -0.044098 | -0.00018577 | 0.018664 | -0.0019141 | -0.012452 | -0.0045095 | -0.01004 | 0.023469 | 0.014289 | -0.012119 | -0.019224 | 0.024417 | -0.0045117 | -0.07782 | -0.013733 | -0.022888 | 0.041199 | 0.16937 | 0.018311 | 0.1236 | 1.6067 | 1.5884 | 1.442 | 1.5564 | 1.6891 | 1.6296 | 1.6296 | 0.045777 | -121.4767 | -121.4218 | 0.23804 | 0.19226 | 0.086976 | 0.14648 | 0.041199 | 1.5106 | -119.8746 | -119.9066 | 1.7578 | 1.6983 | 1.6983 | 0.18768 | 0.18768 | 0.19226 | 0.064087 | 0.24719 | 0.11444 | 0.009155 | 0.14648 | 0.054932 | 1.6571 | -121.4859 | -120.0211 | 0.10986 | 1.6251 | -0.009155 | 1.6754
5247.625 | 121.6141 | -0.10986 | 121.5637 | -0.12794 | -0.044312 | 0.00088223 | 0.021228 | 0.00064947 | -0.012025 | -0.0042959 | -0.086334 | 0.023682 | 0.014503 | -0.01041 | -0.019438 | 0.026553 | -0.0049389 | -0.14191 | 0.004578 | -0.073242 | -0.10071 | -0.022888 | -0.1236 | -0.022888 | 1.3733 | 1.5839 | 1.355 | 1.4053 | 1.5152 | 1.4694 | 1.5198 | 0.036621 | -121.5591 | -121.6644 | 0.086975 | 0.086975 | -0.013733 | 0.050354 | -0.050354 | 1.4648 | -119.9799 | -120.1584 | 1.6251 | 1.6296 | 1.5793 | 0.1648 | 0.11444 | 0.050354 | -0.027466 | 0.16022 | 0.050354 | 0.07782 | 0.22888 | 0.11444 | 1.6937 | -121.637 | -120.2087 | 0.009155 | 1.5152 | -0.032044 | 1.4832
5249.3594 | 121.7239 | -0.064087 | 121.5271 | -0.22713 | -0.040253 | 0.00024143 | 0.021228 | 0.0019311 | -0.012879 | -0.0064321 | -0.074127 | 0.023255 | 0.015785 | -0.016178 | -0.019651 | 0.027835 | 0.00040169 | -0.064087 | -0.009155 | -0.064087 | 0.009155 | 0.09613 | -0.050354 | 0.054932 | 1.5427 | 1.5701 | 1.4099 | 1.5518 | 1.6159 | 1.5289 | 1.6388 | 0 | -121.5363 | -121.5179 | 0.16022 | 0.11902 | 0.013733 | 0.11902 | 0.013733 | 1.474 | -119.957 | -119.9753 | 1.68 | 1.7029 | 1.593 | 0.22888 | 0.11902 | 0.16022 | 0.073242 | 0.20599 | 0.14191 | 0.054932 | 0.16022 | 0.054932 | 1.6342 | -121.5912 | -120.1172 | 0.073242 | 1.6159 | 0 | 1.6068
5251.1562 | 121.7239 | -0.059509 | 121.6141 | -0.17372 | -0.042176 | -0.0010404 | 0.021014 | -0.00063233 | -0.012025 | -0.0040823 | 0.014374 | 0.020264 | 0.017494 | -0.017032 | -0.019651 | 0.025699 | -0.0075025 | -0.1236 | -0.018311 | -0.032043 | -0.050354 | 0.059509 | -0.07782 | 0.050354 | 0.022888 | 0.1236 | -0.054932 | 0.027466 | 0.14191 | 0.091553 | 0.13275 | 0.027466 | -121.6324 | -121.6644 | 0.11902 | 0.10986 | -0.018311 | 0.082397 | -0.045777 | 0.004577 | -121.4905 | -121.5866 | 0.20142 | 0.19226 | 0.15106 | 0.18768 | 0.14649 | 0.091552 | -0.018311 | 0.19684 | 0.082398 | 0.013732 | 0.17853 | 0.041198 | 0.1831 | -121.6461 | -121.669 | 0.009155 | 0.086975 | -0.064087 | 0.082397
5252.8594 | 121.7651 | -0.054932 | 121.637 | -0.18135 | -0.038758 | -0.001254 | 0.021014 | 0.0047083 | -0.011598 | -0.0036551 | -0.1077 | 0.023255 | 0.014503 | -0.01276 | -0.021787 | 0.026981 | -0.0021619 | -0.09613 | 0.009155 | -0.059509 | -0.036621 | 0.054932 | -0.091553 | 0.009155 | 0.032043 | 0.16022 | -0.045776 | 0.018311 | 0.10986 | 0.045776 | 0.10986 | -0.004577 | -121.6278 | -121.6736 | 0.10986 | 0.064087 | -0.036621 | 0.068664 | -0.032044 | 0.009156 | -121.4767 | -121.6187 | 0.16479 | 0.16479 | 0.10071 | 0.15564 | 0.091552 | 0.11444 | 0.022888 | 0.15564 | 0.064087 | 0.068664 | 0.20599 | 0.064087 | 0.21515 | -121.6965 | -121.6827 | 0.018311 | 0.073243 | -0.041198 | 0.086975
5254.5625 | 121.7743 | -0.064087 | 121.6187 | -0.22713 | -0.041107 | 0.0019504 | 0.019519 | 0.00043587 | -0.011384 | -0.0040823 | -0.037506 | 0.023255 | 0.015571 | -0.0089145 | -0.017301 | 0.028262 | -0.0015209 | -0.09613 | -0.004578 | -0.041199 | 0 | 0.11444 | -0.041199 | 0.064087 | 0.064087 | 0.11902 | -0.027466 | 0.041199 | 0.13275 | 0.082397 | 0.13733 | 0.022888 | -121.6232 | -121.6187 | 0.17853 | 0.12817 | 0.022888 | 0.10529 | 0 | 0.036621 | -121.4996 | -121.5775 | 0.19684 | 0.20142 | 0.14648 | 0.16479 | 0.10986 | 0.15564 | 0.041199 | 0.16022 | 0.068665 | 0.036621 | 0.14649 | 0.059509 | 0.18311 | -121.6599 | -121.6461 | 0.064087 | 0.10529 | -0.032043 | 0.12817
5256.3281 | 121.7606 | -0.068665 | 121.5729 | -0.18898 | -0.039612 | -0.00018577 | 0.021228 | -0.0012731 | -0.011384 | -0.0066457 | -0.040558 | 0.022828 | 0.014289 | -0.017459 | -0.019224 | 0.025699 | -0.00088011 | -0.082397 | -0.027466 | -0.036621 | 0.018311 | 0.13733 | -0.041199 | 0.054932 | 0.10071 | 0.12817 | -0.027466 | 0.073242 | 0.16022 | 0.09613 | 0.16022 | 0.032044 | -121.6003 | -121.5546 | 0.20599 | 0.1236 | 0.027466 | 0.091553 | -0.004578 | 0.041199 | -121.4447 | -121.4996 | 0.22888 | 0.22888 | 0.16479 | 0.18768 | 0.1236 | 0.17395 | 0.054932 | 0.18768 | 0.10071 | 0.009155 | 0.15564 | 0.041199 | 0.19684 | -121.6095 | -121.6003 | 0.086976 | 0.14191 | -0.013732 | 0.16937
5258.1094 | 121.7789 | -0.10986 | 121.6461 | -0.18135 | -0.040253 | 0.0010958 | 0.023578 | -0.0019141 | -0.012452 | -0.0023733 | -0.10464 | 0.023896 | 0.014289 | -0.0087009 | -0.019438 | 0.02869 | -0.0017347 | -0.09613 | 0.009155 | -0.082397 | -0.050354 | 0.041199 | -0.086975 | 0.004578 | 0.009155 | 0.14648 | -0.064087 | 0.018311 | 0.091553 | 0.018311 | 0.086975 | 0.027466 | -121.637 | -121.6965 | 0.15106 | 0.11444 | 0.022888 | 0.086975 | -0.004578 | 0.045776 | -121.4996 | -121.6278 | 0.20142 | 0.19684 | 0.12817 | 0.15106 | 0.082398 | 0.1236 | 0.032043 | 0.15564 | 0.082398 | 0.091552 | 0.21057 | 0.11902 | 0.25635 | -121.7285 | -121.7102 | 0.059509 | 0.12817 | 0.013733 | 0.11902
5259.875 | 121.8018 | -0.09613 | 121.6461 | -0.1432 | -0.040894 | 0.001523 | 0.021228 | -0.0010595 | -0.012239 | -0.0062185 | -0.086334 | 0.02411 | 0.015357 | -0.010623 | -0.018583 | 0.027621 | 0.0018969 | -0.10529 | 0 | -0.073242 | -0.054932 | 0.041199 | -0.09613 | 0.013733 | 0.022888 | 0.16479 | -0.064087 | 0.027466 | 0.11444 | 0.050354 | 0.11444 | 0.022888 | -121.6461 | -121.701 | 0.13733 | 0.10986 | 0 | 0.086975 | -0.022888 | 0.032043 | -121.4813 | -121.6187 | 0.21057 | 0.21057 | 0.14648 | 0.17853 | 0.11444 | 0.11444 | 0.01831 | 0.17853 | 0.091553 | 0.073242 | 0.22888 | 0.09613 | 0.26092 | -121.7194 | -121.7102 | 0.041198 | 0.1236 | -0.009156 | 0.11902
5261.6562 | 121.756 | -0.11902 | 121.6278 | -0.15083 | -0.043457 | -0.0023222 | 0.019091 | -0.0034095 | -0.012452 | -0.0036551 | -0.025299 | 0.022187 | 0.013862 | -0.0099827 | -0.017942 | 0.027194 | -0.0013073 | -0.09613 | -0.022888 | -0.059509 | -0.013733 | 0.10986 | -0.018311 | 0.054932 | 0.036621 | 0.13275 | -0.041199 | -0.009155 | 0.11444 | 0.073242 | 0.09613 | 0.05951 | -121.6507 | -121.6415 | 0.22888 | 0.17395 | 0.10071 | 0.11444 | 0.041198 | 0.07782 | -121.4951 | -121.637 | 0.23346 | 0.21515 | 0.19226 | 0.13733 | 0.11444 | 0.16937 | 0.045776 | 0.15564 | 0.032044 | 0.036621 | 0.17395 | 0.096131 | 0.25177 | -121.6873 | -121.669 | 0.10529 | 0.10986 | 0.022889 | 0.15564
5263.4062 | 121.7056 | -0.12817 | 121.6324 | -0.12032 | -0.038971 | -0.00039957 | 0.020587 | -0.00084593 | -0.01117 | -0.0040823 | -0.1199 | 0.02411 | 0.01493 | -0.0050693 | -0.019438 | 0.028262 | -0.0032299 | -0.14648 | 0.013733 | -0.073242 | -0.10529 | -0.054932 | -0.16022 | -0.073242 | -0.09613 | 0.16022 | -0.073242 | -0.050354 | 0.018311 | -0.054932 | 0.036621 | 0.054932 | -121.6187 | -121.7377 | 0.073242 | 0.054932 | -0.032043 | 0 | -0.086975 | 0.054932 | -121.4722 | -121.6827 | 0.14649 | 0.1648 | 0.073242 | 0.10986 | 0.01831 | 0.01831 | -0.032044 | 0.091553 | 0.022888 | 0.086975 | 0.23346 | 0.14191 | 0.28839 | -121.7056 | -121.7056 | 0.022888 | 0.07782 | -0.01831 | 0.032044
5265.1719 | 121.7285 | -0.56763 | 121.0464 | -0.13557 | -0.041535 | 0.00045503 | 0.018023 | 0.0029993 | -0.010743 | -0.0036551 | -0.0069885 | 0.02411 | 0.015571 | -0.015537 | -0.018369 | 0.024631 | -0.0021619 | -0.19684 | -0.13733 | -0.13733 | -0.10986 | 0.013733 | -0.1236 | -0.032043 | 0.036621 | 0.1236 | -0.027466 | 0.018311 | 0.16022 | 0.10071 | 0.11902 | 0.4303 | -121.1838 | -121.1563 | 0.58136 | 0.53558 | 0.44403 | 0.10529 | 0.013733 | 0.54016 | -120.9229 | -121.0281 | 0.72784 | 0.68665 | 0.66834 | 0.14649 | 0.12817 | 0.15106 | 0.027466 | 0.18768 | 0.045777 | 0 | 0.15106 | 0.4303 | 0.69122 | -121.1838 | -121.0739 | 0.45776 | 0.58594 | 0.37079 | 0.60425
5266.9219 | 121.7331 | -0.18768 | 121.5042 | -0.16609 | -0.041107 | 0.00045503 | 0.021869 | 0.0032129 | -0.01352 | -0.0034415 | -0.086334 | 0.025605 | 0.014289 | -0.0095553 | -0.019865 | 0.027621 | -0.0040845 | -0.12817 | -0.009155 | -0.082397 | -0.082397 | 0.018311 | -0.11444 | -0.027466 | 0 | 0.16022 | -0.054932 | 0 | 0.082397 | 0.013733 | 0.09613 | 0.10529 | -121.5134 | -121.5866 | 0.20599 | 0.16022 | 0.073242 | 0.054931 | -0.032044 | 0.13275 | -121.344 | -121.5042 | 0.27008 | 0.28381 | 0.20142 | 0.15106 | 0.068665 | 0.10071 | 0 | 0.13733 | 0.054932 | 0.073242 | 0.21515 | 0.17853 | 0.3479 | -121.5866 | -121.5591 | 0.10529 | 0.18768 | 0.059509 | 0.18768
5268.625 | 121.3028 | -0.10529 | 121.2067 | -0.15083 | -0.041535 | 2.7834e-05 | 0.021014 | -0.0019141 | -0.013947 | -0.0051505 | -0.080231 | 0.023255 | 0.015785 | -0.010623 | -0.020078 | 0.027408 | -0.0032299 | -0.10071 | -0.004578 | -0.054932 | -0.054932 | 0.032043 | -0.11444 | 0 | 0.018311 | 0.12817 | -0.073242 | -0.013733 | 0.073242 | 0.004578 | 0.086975 | 0.050354 | -121.2112 | -121.2616 | 0.13733 | 0.10529 | -0.009155 | 0.054932 | -0.059509 | 0.032044 | -121.0785 | -121.2204 | 0.17853 | 0.19226 | 0.10986 | 0.16022 | 0.07782 | 0.086975 | 0 | 0.14648 | 0.059509 | 0.050354 | 0.20142 | 0.10071 | 0.23346 | -121.2616 | -121.2799 | 0.050354 | 0.091553 | 0.004578 | 0.1236
5270.375 | 121.4859 | -0.068665 | 121.2936 | -0.2729 | -0.041535 | 0.002164 | 0.017382 | -0.0021277 | -0.0098886 | -0.0049367 | -0.022247 | 0.021546 | 0.013008 | -0.01276 | -0.016447 | 0.025912 | -0.0032299 | -0.10071 | -0.027466 | -0.036621 | -0.013733 | 0.10986 | -0.054932 | 0.068665 | 0.086975 | 0.09613 | -0.050354 | 0.036621 | 0.14191 | 0.086975 | 0.13275 | 0.032044 | -121.3211 | -121.3074 | 0.17853 | 0.13733 | 0.013733 | 0.10529 | -0.018311 | 0.018311 | -121.1975 | -121.257 | 0.21057 | 0.20142 | 0.15564 | 0.18311 | 0.13733 | 0.14648 | 0.022888 | 0.19226 | 0.086975 | 0.009155 | 0.14648 | 0.041199 | 0.16479 | -121.3303 | -121.344 | 0.054932 | 0.10529 | -0.032043 | 0.15564
5272.1562 | 121.582 | -0.054932 | 121.3669 | -0.18135 | -0.041535 | 0.003232 | 0.019519 | 8.47e-06 | -0.01352 | -0.0068593 | -0.040558 | 0.023896 | 0.015144 | -0.015323 | -0.020292 | 0.026553 | -0.0021619 | -0.064087 | -0.013733 | -0.036621 | 0.004578 | 0.1236 | -0.036621 | 0.064087 | 0.1236 | 0.11444 | -0.032043 | 0.091553 | 0.17853 | 0.12817 | 0.16937 | 0.018311 | -121.3806 | -121.3623 | 0.17853 | 0.11902 | 0.018311 | 0.10071 | 0 | 0.022889 | -121.2524 | -121.2753 | 0.23346 | 0.22431 | 0.18311 | 0.20142 | 0.16022 | 0.16022 | 0.041199 | 0.21057 | 0.1236 | 0.022888 | 0.14648 | 0.041199 | 0.16937 | -121.4035 | -121.3989 | 0.05951 | 0.14649 | -0.009155 | 0.17853
5273.8594 | 121.5317 | -0.082397 | 121.4584 | -0.12794 | -0.037903 | 0.0017368 | 0.0208 | 0.0040675 | -0.012239 | -0.0053641 | -0.11685 | 0.023896 | 0.014717 | -0.0080601 | -0.020933 | 0.028049 | -0.0045117 | -0.086975 | 0.041199 | -0.064087 | -0.050354 | 0.059509 | -0.086975 | 0.009155 | 0.032043 | 0.15106 | -0.059509 | 0.009155 | 0.11902 | 0.050354 | 0.11444 | 0.01831 | -121.4172 | -121.5088 | 0.14191 | 0.091552 | -0.004578 | 0.073242 | -0.022888 | 0.022888 | -121.3074 | -121.4493 | 0.20142 | 0.19684 | 0.13275 | 0.17395 | 0.10986 | 0.1236 | 0.013733 | 0.17853 | 0.068664 | 0.10529 | 0.21057 | 0.1236 | 0.23346 | -121.5225 | -121.5179 | 0.032043 | 0.091552 | -0.004578 | 0.11444
5275.625 | 120.9915 | -0.068665 | 120.7993 | -0.2195 | -0.041535 | 0.00024143 | 0.019519 | -0.0061865 | -0.0098886 | -0.0032277 | 0.0052185 | 0.023041 | 0.012367 | -0.015964 | -0.017942 | 0.025912 | -0.0013073 | -0.1236 | -0.018311 | -0.041199 | -0.045776 | 0.045776 | -0.073242 | 0.045776 | 0.018311 | 0.10986 | -0.045776 | 0.018311 | 0.1236 | 0.059509 | 0.10986 | 0.027466 | -120.8176 | -120.845 | 0.11444 | 0.11444 | -0.004577 | 0.086975 | -0.032043 | 0.022889 | -120.6894 | -120.7809 | 0.19226 | 0.17853 | 0.12817 | 0.15564 | 0.10528 | 0.086975 | -0.004577 | 0.16937 | 0.064087 | 0.022888 | 0.15564 | 0.050354 | 0.17853 | -120.8405 | -120.845 | 0.022889 | 0.086976 | -0.054931 | 0.086976
5277.3906 | 121.1334 | -0.15564 | 120.9229 | -0.21187 | -0.040253 | 0.0019504 | 0.019732 | 8.47e-06 | -0.011384 | -0.0064321 | -0.083283 | 0.02411 | 0.017707 | -0.0134 | -0.020078 | 0.029758 | 0.0014697 | -0.16479 | 0.004578 | -0.091553 | -0.12817 | -0.054932 | -0.16937 | -0.045776 | -0.068665 | 0.16937 | -0.073242 | -0.054932 | 0.013733 | -0.022888 | 0.054932 | 0.064087 | -120.9183 | -121.051 | 0.10071 | 0.10986 | -0.013733 | 0.045777 | -0.07782 | 0.082398 | -120.7535 | -120.9778 | 0.16937 | 0.21057 | 0.13275 | 0.12817 | 0.050354 | 0.036621 | -0.036621 | 0.086975 | 0.01831 | 0.096131 | 0.24261 | 0.16022 | 0.32501 | -121.0144 | -120.9961 | 0.027466 | 0.10071 | -0.009155 | 0.086975
5279.0938 | 121.1975 | -0.2655 | 120.8359 | -0.21187 | -0.040467 | 0.00024143 | 0.022937 | 0.0015039 | -0.013734 | -0.0053641 | -0.074127 | 0.020051 | 0.016212 | -0.017032 | -0.019651 | 0.027621 | -0.00088011 | -0.18768 | -0.022888 | -0.1236 | -0.14648 | -0.036621 | -0.19226 | -0.059509 | -0.027466 | 0.14648 | -0.054932 | 0.018311 | 0.07782 | 0.013733 | 0.11444 | 0.14191 | -120.8588 | -120.9824 | 0.22888 | 0.20599 | 0.073242 | 0.064087 | -0.068665 | 0.21057 | -120.6894 | -120.8176 | 0.34332 | 0.37994 | 0.27924 | 0.16937 | 0.068665 | 0.086975 | -0.022888 | 0.13275 | 0.073243 | 0.10071 | 0.20142 | 0.24261 | 0.41199 | -120.9595 | -120.8908 | 0.11902 | 0.28381 | 0.07782 | 0.23804
5280.7812 | 121.2387 | -0.36163 | 120.7535 | -0.21187 | -0.041107 | 0.0017368 | 0.017382 | -0.0021277 | -0.011598 | -0.0032277 | -0.0008851 | 0.023469 | 0.013648 | -0.015537 | -0.017301 | 0.027621 | -0.0047253 | -0.17853 | -0.068665 | -0.09613 | -0.11902 | 0.004578 | -0.13275 | -0.013733 | 0.009155 | 0.11444 | -0.032043 | 0.022888 | 0.12817 | 0.082397 | 0.11444 | 0.2655 | -120.8221 | -120.8725 | 0.36621 | 0.3479 | 0.22888 | 0.082397 | -0.036621 | 0.32959 | -120.639 | -120.7306 | 0.48981 | 0.47607 | 0.44403 | 0.14648 | 0.11444 | 0.10071 | -0.022889 | 0.16022 | 0.054931 | 0.027465 | 0.14648 | 0.29297 | 0.47607 | -120.8496 | -120.7855 | 0.24261 | 0.38452 | 0.1831 | 0.37079
5282.5469 | 121.1792 | -0.37537 | 120.7901 | -0.12032 | -0.039612 | 2.7834e-05 | 0.0208 | 0.0057763 | -0.010957 | -0.0015189 | -0.092438 | 0.022401 | 0.016212 | -0.010196 | -0.019865 | 0.027621 | -0.0036573 | -0.16022 | -0.064087 | -0.14191 | -0.11444 | -0.013733 | -0.14648 | -0.068665 | 0.022888 | 0.13733 | -0.041199 | 0.004578 | 0.10529 | 0.054932 | 0.10071 | 0.23346 | -120.8542 | -120.9045 | 0.36163 | 0.3067 | 0.22888 | 0.073242 | -0.004577 | 0.33417 | -120.6528 | -120.7855 | 0.48065 | 0.47607 | 0.4303 | 0.14191 | 0.096131 | 0.12817 | 0.027466 | 0.14649 | 0.045777 | 0.07782 | 0.17853 | 0.31128 | 0.5127 | -120.932 | -120.8313 | 0.26092 | 0.37994 | 0.21515 | 0.39825
5284.3125 | 117.7002 | -0.17853 | 117.4805 | -0.15083 | -0.039185 | 0.0013094 | 0.0208 | 0.0057763 | -0.012879 | -0.0064321 | -0.1077 | 0.024323 | 0.01493 | -0.012119 | -0.020933 | 0.027408 | -0.0047253 | -0.1236 | -0.027466 | -0.09613 | -0.068665 | 0.032043 | -0.10529 | -0.022888 | 0.027466 | 0.15564 | -0.045776 | 0 | 0.09613 | 0.036621 | 0.10071 | 0.082398 | -117.5079 | -117.5491 | 0.21057 | 0.15564 | 0.073242 | 0.073242 | -0.009156 | 0.13275 | -117.3248 | -117.4805 | 0.27466 | 0.27924 | 0.21515 | 0.14648 | 0.082397 | 0.12817 | 0.027465 | 0.14191 | 0.045776 | 0.068664 | 0.20142 | 0.15106 | 0.33417 | -117.5766 | -117.5262 | 0.10986 | 0.17853 | 0.054932 | 0.20599
5286.0781 | 120.9686 | -0.10529 | 120.7718 | -0.2195 | -0.039826 | 0.00024143 | 0.01781 | -0.00041873 | -0.011811 | -0.0057913 | -0.01004 | 0.02411 | 0.016426 | -0.016178 | -0.018797 | 0.024844 | -0.0038709 | -0.09613 | -0.022888 | -0.064087 | -0.022888 | 0.10529 | -0.064087 | 0.050354 | 0.054932 | 0.11444 | -0.045776 | 0.041199 | 0.13733 | 0.073242 | 0.11902 | 0.041199 | -120.7947 | -120.7947 | 0.21057 | 0.15564 | 0.041199 | 0.11444 | 0 | 0.05951 | -120.6573 | -120.7306 | 0.24262 | 0.22431 | 0.17853 | 0.16479 | 0.11902 | 0.16937 | 0.041199 | 0.18311 | 0.086975 | 0.041199 | 0.16022 | 0.082398 | 0.21973 | -120.8359 | -120.8176 | 0.082398 | 0.14649 | 0.009156 | 0.16022
5287.7812 | 121.2158 | -0.31128 | 120.5795 | -0.20424 | -0.039826 | 0.0010958 | 0.018237 | 0.00064947 | -0.009675 | -0.0060049 | -0.028351 | 0.02176 | 0.015357 | -0.011051 | -0.020933 | 0.027408 | 0.00061529 | -0.14648 | -0.082397 | -0.09613 | -0.059509 | 0.064087 | -0.10071 | 0.013733 | 0.086975 | 0.10986 | -0.036621 | 0.041199 | 0.13275 | 0.09613 | 0.1236 | 0.21515 | -120.6619 | -120.639 | 0.37537 | 0.32501 | 0.21057 | 0.10986 | -0.004578 | 0.27466 | -120.4697 | -120.5383 | 0.44403 | 0.43487 | 0.40741 | 0.16022 | 0.13275 | 0.16022 | 0.036621 | 0.16937 | 0.07782 | 0.013733 | 0.14648 | 0.22888 | 0.42114 | -120.6757 | -120.6161 | 0.25177 | 0.35248 | 0.16479 | 0.39825
5289.5312 | 121.1746 | -0.20599 | 120.7489 | -0.23476 | -0.039826 | 0.0028048 | 0.020587 | 0.00086307 | -0.0094614 | -0.0049367 | -0.052765 | 0.020905 | 0.014289 | -0.0080601 | -0.020078 | 0.02634 | -0.0045117 | -0.10071 | -0.059509 | -0.054932 | 0 | 0.082397 | -0.073242 | 0.050354 | 0.10529 | 0.10071 | -0.050354 | 0.10071 | 0.17853 | 0.11444 | 0.16022 | 0.15106 | -120.8084 | -120.7489 | 0.28839 | 0.25635 | 0.13275 | 0.10529 | -0.01831 | 0.15564 | -120.6482 | -120.6482 | 0.38452 | 0.36621 | 0.32044 | 0.21057 | 0.16479 | 0.13733 | 0.054932 | 0.22888 | 0.15106 | -0.004577 | 0.15106 | 0.14649 | 0.3067 | -120.8038 | -120.7993 | 0.20599 | 0.3067 | 0.10529 | 0.31128
5291.2812 | 121.1014 | -0.21057 | 120.8359 | -0.18135 | -0.040894 | -0.0014676 | 0.01781 | 0.00022207 | -0.013307 | -0.0034415 | -0.0008851 | 0.022614 | 0.015571 | -0.012332 | -0.01901 | 0.026126 | 0.0012561 | -0.11444 | -0.032043 | -0.07782 | -0.027466 | 0.068665 | -0.041199 | 0.032043 | 0.027466 | 0.15106 | -0.050354 | -0.009155 | 0.10529 | 0.045776 | 0.086975 | 0.13275 | -120.8679 | -120.8633 | 0.27924 | 0.24261 | 0.16937 | 0.10986 | 0.036621 | 0.16022 | -120.6848 | -120.845 | 0.31586 | 0.29755 | 0.25635 | 0.13733 | 0.09613 | 0.14649 | 0.050354 | 0.15564 | 0.041199 | 0.045777 | 0.20142 | 0.17853 | 0.36163 | -120.9137 | -120.8862 | 0.18311 | 0.20142 | 0.09613 | 0.23804
5292.9844 | 121.1517 | -0.20142 | 120.9 | -0.18898 | -0.041321 | 0.00045503 | 0.017382 | -0.0010595 | -0.01587 | -0.0038687 | -0.013092 | 0.023255 | 0.014289 | -0.0022921 | -0.019651 | 0.025912 | -0.0025891 | -0.09613 | -0.036621 | -0.07782 | -0.027466 | 0.07782 | -0.027466 | 0.041199 | 0.041199 | 0.1236 | -0.050354 | 0.018311 | 0.1236 | 0.07782 | 0.09613 | 0.1236 | -120.9366 | -120.9274 | 0.27924 | 0.24262 | 0.17395 | 0.11902 | 0.050354 | 0.15106 | -120.7764 | -120.8817 | 0.32501 | 0.29755 | 0.27924 | 0.14648 | 0.12817 | 0.15564 | 0.050354 | 0.17395 | 0.068665 | 0.041199 | 0.17395 | 0.1648 | 0.32501 | -120.9778 | -120.9503 | 0.17395 | 0.21973 | 0.10529 | 0.24262
5294.7344 | 121.2387 | -0.1831 | 120.8771 | -0.12794 | -0.044312 | 0.00024143 | 0.018451 | 0.00022207 | -0.013093 | -0.0045095 | 0.0021667 | 0.024323 | 0.016212 | -0.0099827 | -0.019438 | 0.024204 | -0.0045117 | -0.10529 | -0.064087 | -0.086975 | 0.009155 | 0.12817 | -0.022888 | 0.064087 | 0.10986 | 0.10529 | -0.036621 | 0.068665 | 0.20142 | 0.14191 | 0.17395 | 0.09613 | -120.9412 | -120.8679 | 0.31128 | 0.24719 | 0.16022 | 0.15106 | 0.064087 | 0.14648 | -120.7718 | -120.8084 | 0.38452 | 0.35706 | 0.32501 | 0.21057 | 0.17853 | 0.21515 | 0.09613 | 0.23804 | 0.10529 | 0.022888 | 0.14191 | 0.11902 | 0.28839 | -120.9641 | -120.9137 | 0.19226 | 0.25177 | 0.077819 | 0.29297
5296.5 | 121.1472 | -0.21057 | 120.9412 | -0.15083 | -0.040467 | 0.0019504 | 0.021655 | -0.0038367 | -0.010957 | -0.0032277 | -0.13211 | 0.022187 | 0.013862 | -0.0072055 | -0.019224 | 0.025272 | -0.0017347 | -0.15564 | 0.004578 | -0.091553 | -0.1236 | -0.054932 | -0.20599 | -0.082397 | -0.09613 | 0.14191 | -0.073242 | -0.068665 | 0.009155 | -0.059509 | 0.050354 | 0.11902 | -120.9366 | -121.0648 | 0.15564 | 0.12817 | 0.004577 | 0.009156 | -0.11444 | 0.13733 | -120.7993 | -121.0098 | 0.21973 | 0.26093 | 0.15106 | 0.1236 | 0.013733 | 0.036621 | -0.032043 | 0.082397 | 0.004577 | 0.096131 | 0.21515 | 0.21515 | 0.35248 | -121.0327 | -121.0144 | 0.086975 | 0.14191 | 0.054931 | 0.11444
5298.2188 | 121.1426 | -0.42114 | 120.7077 | -0.15846 | -0.040894 | 0.002164 | 0.0208 | -0.0019141 | -0.010957 | -0.0045095 | -0.086334 | 0.02475 | 0.01493 | -0.016391 | -0.020506 | 0.02634 | -0.0034435 | -0.20142 | -0.027466 | -0.15106 | -0.18768 | -0.091553 | -0.23804 | -0.10529 | -0.059509 | 0.15106 | -0.07782 | -0.018311 | 0.032043 | -0.013733 | 0.054932 | 0.27008 | -120.7352 | -120.8954 | 0.32959 | 0.31586 | 0.18311 | 0.045776 | -0.086975 | 0.34332 | -120.5566 | -120.726 | 0.45319 | 0.47607 | 0.40741 | 0.13275 | 0.064087 | 0.059509 | -0.036621 | 0.10986 | 0.059509 | 0.1236 | 0.22888 | 0.39368 | 0.5722 | -120.8588 | -120.7855 | 0.23346 | 0.40283 | 0.21973 | 0.36163
5299.9844 | 121.1975 | -0.48981 | 120.5246 | -0.17372 | -0.042603 | 0.00045503 | 0.021655 | 0.00022207 | -0.010957 | -0.0042959 | -0.071076 | 0.025178 | 0.016639 | -0.019168 | -0.019438 | 0.028049 | -0.00066651 | -0.21057 | -0.09613 | -0.16479 | -0.12817 | -0.036621 | -0.17853 | -0.054932 | 0.041199 | 0.10986 | -0.036621 | 0.082397 | 0.14648 | 0.091553 | 0.16022 | 0.32501 | -120.6207 | -120.6528 | 0.45319 | 0.43488 | 0.31128 | 0.10986 | -0.013733 | 0.45319 | -120.4147 | -120.4422 | 0.63629 | 0.65002 | 0.58136 | 0.19684 | 0.12817 | 0.12817 | 0.036621 | 0.18311 | 0.11902 | 0.068665 | 0.14648 | 0.39368 | 0.59967 | -120.6894 | -120.5612 | 0.36163 | 0.5722 | 0.27924 | 0.53101
5301.75 | 121.0968 | -0.46234 | 120.6299 | -0.12794 | -0.041962 | 0.0013094 | 0.016955 | -0.0021277 | -0.012452 | -0.0051505 | -0.022247 | 0.023041 | 0.01258 | -0.013614 | -0.018369 | 0.02869 | -0.0023755 | -0.17395 | -0.09613 | -0.12817 | -0.11444 | 0.009155 | -0.10986 | -0.032043 | 0.013733 | 0.13733 | -0.073242 | -0.027466 | 0.09613 | 0.018311 | 0.068665 | 0.33417 | -120.726 | -120.7443 | 0.4715 | 0.4303 | 0.35248 | 0.096131 | 0.018311 | 0.3891 | -120.4926 | -120.6573 | 0.55847 | 0.53101 | 0.48065 | 0.14191 | 0.091553 | 0.13733 | 0.013733 | 0.16937 | 0.045776 | 0.032044 | 0.21057 | 0.36621 | 0.59967 | -120.7581 | -120.7031 | 0.3479 | 0.43488 | 0.28839 | 0.47607
5303.4531 | 121.1472 | -0.59967 | 120.3598 | -0.20424 | -0.03833 | 0.00088223 | 0.02016 | -0.0017005 | -0.01117 | -0.0042959 | -0.077179 | 0.022401 | 0.014289 | -0.0074191 | -0.021147 | 0.028476 | -0.0045117 | -0.20142 | -0.12817 | -0.17853 | -0.11902 | -0.018311 | -0.17395 | -0.064087 | 0.068665 | 0.10529 | -0.041199 | 0.082397 | 0.17853 | 0.09613 | 0.16022 | 0.42114 | -120.488 | -120.4788 | 0.58136 | 0.53558 | 0.42572 | 0.11444 | 0.004578 | 0.55847 | -120.2545 | -120.2774 | 0.7782 | 0.75989 | 0.6958 | 0.20142 | 0.13733 | 0.16022 | 0.059509 | 0.21973 | 0.1236 | 0.050354 | 0.14649 | 0.4715 | 0.70496 | -120.5383 | -120.401 | 0.48065 | 0.68207 | 0.39825 | 0.66834
5305.2188 | 120.9457 | -1.1581 | 119.6732 | -0.15083 | -0.041962 | -0.00082677 | 0.018237 | -0.0051183 | -0.010743 | -0.0049367 | -0.025299 | 0.023469 | 0.015357 | -0.018741 | -0.020078 | 0.025272 | 0.00018809 | -0.36621 | -0.26093 | -0.29297 | -0.28381 | -0.17395 | -0.32959 | -0.21057 | -0.009155 | 0.10986 | -0.068665 | 0.013733 | 0.10986 | 0.054932 | 0.11444 | 0.86517 | -119.9341 | -119.957 | 0.98419 | 0.94757 | 0.82855 | 0.082398 | -0.036621 | 1.0895 | -119.5633 | -119.6594 | 1.268 | 1.2726 | 1.2131 | 0.18311 | 0.1236 | 0.11902 | 0.009156 | 0.17853 | 0.082398 | 0.032044 | 0.17853 | 0.89722 | 1.268 | -119.9661 | -119.7418 | 0.87433 | 1.1719 | 0.79193 | 1.149
5306.9375 | 120.7901 | -120.0302 | 0.36163 | -0.17372 | -0.039185 | 0.0047274 | 0.02016 | 0.0010767 | -0.011811 | -0.0021597 | -0.052765 | 0.024323 | 0.012794 | -0.015964 | -0.020506 | 0.025912 | -0.0068615 | -0.07782 | -0.027466 | -0.004578 | 0.018311 | 0.11902 | -0.027466 | 0.082397 | 0.10071 | 0.10529 | -0.032043 | 0.10071 | 0.17395 | 0.1236 | 0.16937 | 120.0256 | -0.3891 | -0.34332 | 120.1492 | 120.1126 | 120.0027 | 0.086975 | -0.022888 | 119.9982 | -0.25635 | -0.26092 | 120.2042 | 120.1996 | 120.1538 | 0.20142 | 0.15564 | 0.1236 | 0.022889 | 0.20599 | 0.13275 | -0.022888 | 0.13733 | 120.0027 | 120.1355 | -0.36621 | -0.39368 | 120.0485 | 120.1309 | 119.9524 | 120.1309
5308.7031 | 120.8908 | -120.3094 | 0.40741 | -0.2195 | -0.040039 | 0.001523 | 0.024005 | 0.0010767 | -0.014161 | -0.0036551 | -0.10159 | 0.024537 | 0.015571 | -0.0099827 | -0.019438 | 0.027621 | -0.0042981 | -0.13733 | 0.009155 | -0.07782 | -0.10986 | -0.032043 | -0.14648 | -0.036621 | -0.045776 | 0.15106 | -0.059509 | -0.004578 | 0.022888 | -0.004578 | 0.068665 | 120.2316 | -0.39825 | -0.51727 | 120.2774 | 120.2728 | 120.163 | 0.041199 | -0.068664 | 120.2499 | -0.25635 | -0.41199 | 120.3323 | 120.3781 | 120.3049 | 0.12817 | 0.054931 | 0.045777 | -0.032043 | 0.082397 | 0.054931 | 0.086975 | 0.21057 | 120.3186 | 120.4605 | -0.48523 | -0.46692 | 120.1996 | 120.3049 | 120.1721 | 120.2637
5310.4688 | 120.8038 | -120.1492 | 0.4303 | -0.25764 | -0.038544 | 0.002164 | 0.022509 | 0.0040675 | -0.01352 | -0.0047231 | -0.031403 | 0.021332 | 0.01493 | -0.0061375 | -0.018797 | 0.026553 | -0.0042981 | -0.059509 | -0.018311 | -0.018311 | 0.036621 | 0.13275 | -0.036621 | 0.082397 | 0.10986 | 0.1236 | -0.022888 | 0.091553 | 0.18768 | 0.11902 | 0.16937 | 120.1309 | -0.44861 | -0.39368 | 120.282 | 120.2316 | 120.1126 | 0.10071 | -0.01831 | 120.1263 | -0.3067 | -0.33875 | 120.3369 | 120.3186 | 120.2682 | 0.19226 | 0.14191 | 0.15106 | 0.054932 | 0.21057 | 0.11444 | 0 | 0.14648 | 120.1309 | 120.2728 | -0.44861 | -0.45319 | 120.1859 | 120.2408 | 120.0897 | 120.2591
5312.2344 | 120.9503 | -120.2499 | 0.4715 | -0.18135 | -0.043671 | 0.00045503 | 0.018237 | -0.0038367 | -0.013307 | -0.0038687 | -0.0069885 | 0.022401 | 0.012153 | -0.010837 | -0.019865 | 0.023776 | -0.0051525 | -0.13733 | -0.018311 | -0.064087 | -0.045776 | 0.082397 | -0.050354 | 0.064087 | 0.045776 | 0.11902 | -0.027466 | 0.059509 | 0.16022 | 0.11444 | 0.16022 | 120.1859 | -0.48981 | -0.51727 | 120.3323 | 120.314 | 120.1996 | 0.12817 | 0.013733 | 120.2225 | -0.35248 | -0.41199 | 120.4102 | 120.4102 | 120.3644 | 0.18768 | 0.14191 | 0.14648 | 0.018311 | 0.18768 | 0.086975 | 0.045776 | 0.14649 | 120.2316 | 120.369 | -0.53558 | -0.49896 | 120.2042 | 120.3094 | 120.1126 | 120.2957
5313.9375 | 121.0007 | -120.2591 | 0.50354 | -0.18898 | -0.040467 | 0.00088223 | 0.022509 | -0.0012731 | -0.013307 | -0.0038687 | -0.037506 | 0.023041 | 0.01258 | -0.017032 | -0.020719 | 0.026981 | -0.0040845 | -0.068665 | -0.018311 | -0.018311 | 0.013733 | 0.14191 | -0.036621 | 0.07782 | 0.11444 | 0.11444 | -0.027466 | 0.091553 | 0.16479 | 0.10071 | 0.16022 | 120.2408 | -0.52185 | -0.48981 | 120.401 | 120.3369 | 120.2225 | 0.096131 | -0.01831 | 120.2316 | -0.3891 | -0.41199 | 120.4239 | 120.4193 | 120.3598 | 0.18768 | 0.12817 | 0.16022 | 0.032044 | 0.19226 | 0.11902 | 0 | 0.14191 | 120.2408 | 120.3735 | -0.52185 | -0.53101 | 120.2728 | 120.3506 | 120.1904 | 120.3735
5315.6875 | 121.1105 | -120.3094 | 0.50812 | -0.21187 | -0.039398 | 0.0017368 | 0.020373 | -0.00084593 | -0.013734 | -0.0019461 | -0.071076 | 0.021332 | 0.012367 | -0.013614 | -0.020292 | 0.027835 | -0.0034435 | -0.054932 | -0.018311 | -0.041199 | 0.018311 | 0.1236 | -0.041199 | 0.073242 | 0.10986 | 0.10986 | -0.041199 | 0.11902 | 0.18768 | 0.11444 | 0.16937 | 120.2682 | -0.52643 | -0.48981 | 120.433 | 120.3827 | 120.2682 | 0.11444 | 0 | 120.2682 | -0.39825 | -0.3891 | 120.4971 | 120.4788 | 120.4239 | 0.21057 | 0.15564 | 0.16479 | 0.05951 | 0.22888 | 0.16022 | 0.022888 | 0.15106 | 120.2911 | 120.4193 | -0.54932 | -0.54932 | 120.3278 | 120.4285 | 120.2545 | 120.4193
5317.4375 | 121.1105 | -120.3461 | 0.49439 | -0.17372 | -0.040467 | 0.0013094 | 0.018023 | 0.00043587 | -0.012666 | -0.0055777 | -0.025299 | 0.02176 | 0.012367 | -0.011905 | -0.017729 | 0.025272 | -0.00023931 | -0.059509 | -0.009155 | -0.022888 | 0.009155 | 0.13733 | -0.036621 | 0.082397 | 0.10986 | 0.1236 | -0.027466 | 0.068665 | 0.14648 | 0.10071 | 0.13275 | 120.3232 | -0.50354 | -0.48523 | 120.4834 | 120.4285 | 120.3094 | 0.10528 | -0.013733 | 120.3186 | -0.37079 | -0.42572 | 120.4926 | 120.4788 | 120.4468 | 0.16022 | 0.12817 | 0.16022 | 0.032043 | 0.17395 | 0.096131 | 0.013733 | 0.15106 | 120.3369 | 120.4697 | -0.51727 | -0.52185 | 120.3552 | 120.4147 | 120.2866 | 120.4559
5319.1562 | 121.0876 | -120.3827 | 0.52643 | -0.11269 | -0.042816 | -0.00018577 | 0.02016 | -0.0023413 | -0.013307 | -0.0028005 | -0.025299 | 0.022401 | 0.011512 | -0.013614 | -0.018583 | 0.025699 | -0.0083569 | -0.082397 | -0.018311 | -0.036621 | 0.041199 | 0.17853 | 0.009155 | 0.10529 | 0.13275 | 0.10986 | -0.027466 | 0.086975 | 0.2243 | 0.14191 | 0.18768 | 120.3461 | -0.54474 | -0.48523 | 120.5612 | 120.488 | 120.3918 | 0.14191 | 0.045776 | 120.3552 | -0.41657 | -0.43945 | 120.607 | 120.5704 | 120.5246 | 0.21515 | 0.16937 | 0.21515 | 0.07782 | 0.25177 | 0.11444 | 0.01831 | 0.13733 | 120.3644 | 120.4926 | -0.56305 | -0.55389 | 120.4239 | 120.4697 | 120.3003 | 120.5154
5320.8594 | 120.6253 | -3.2364 | 117.3248 | -0.19661 | -0.041962 | -0.0027494 | 0.018878 | -0.0021277 | -0.011598 | -0.0055777 | -0.049713 | 0.022187 | 0.016639 | -0.012119 | -0.018797 | 0.029971 | -0.0010937 | -0.073242 | -0.022888 | -0.036621 | -0.009155 | 0.07782 | -0.073242 | 0.050354 | 0.045776 | 0.10986 | -0.036621 | 0.036621 | 0.11902 | 0.068665 | 0.1236 | 3.1998 | -117.3477 | -117.334 | 3.3142 | 3.2867 | 3.1631 | 0.086975 | -0.036621 | 3.1998 | -117.215 | -117.2882 | 3.3554 | 3.36 | 3.3051 | 0.16022 | 0.10529 | 0.11444 | 0.027466 | 0.15564 | 0.073242 | 0.013733 | 0.14648 | 3.2135 | 3.3463 | -117.3614 | -117.3614 | 3.2272 | 3.273 | 3.1631 | 3.2822
5322.625 | 120.7352 | -104.9927 | 15.2435 | -0.18135 | -0.04303 | -0.00061317 | 0.018664 | -0.0021277 | -0.012452 | -0.0062185 | -0.013092 | 0.023682 | 0.011512 | -0.014041 | -0.022001 | 0.025485 | -0.0062207 | -0.068665 | -0.004578 | -0.018311 | 0.068665 | 0.19684 | 0.027466 | 0.10986 | 0.11902 | 0.11444 | -0.022888 | 0.09613 | 0.19684 | 0.14191 | 0.16479 | 104.9744 | -15.2481 | -15.1749 | 105.1895 | 105.1025 | 105.0201 | 0.12817 | 0.045777 | 104.9698 | -15.1291 | -15.1474 | 105.1895 | 105.1575 | 105.1346 | 0.18768 | 0.16479 | 0.21515 | 0.086976 | 0.21973 | 0.11902 | 0.013733 | 0.13733 | 104.9881 | 105.1071 | -15.2618 | -15.2664 | 105.0613 | 105.0888 | 104.924 | 105.1117
5324.3906 | 120.9045 | -105.2948 | 15.1932 | -0.15083 | -0.040253 | -0.00018577 | 0.020587 | -0.0031957 | -0.010316 | -0.0040823 | -0.022247 | 0.022401 | 0.013435 | -0.011905 | -0.017515 | 0.026126 | -0.0047253 | -0.10529 | -0.004578 | -0.050354 | -0.027466 | 0.045776 | -0.073242 | 0.045776 | 0.004578 | 0.12817 | -0.036621 | 0.036621 | 0.12817 | 0.068665 | 0.1236 | 105.2444 | -15.1978 | -15.2206 | 105.3406 | 105.3406 | 105.2216 | 0.09613 | -0.022888 | 105.2582 | -15.065 | -15.1566 | 105.423 | 105.4184 | 105.3635 | 0.16022 | 0.10529 | 0.09613 | 0.022888 | 0.1648 | 0.073242 | 0.045776 | 0.1648 | 105.2902 | 105.423 | -15.2435 | -15.2298 | 105.2673 | 105.3314 | 105.1895 | 105.2994
5326.1562 | 116.4551 | -80.4382 | 35.1379 | -0.15083 | -0.041962 | -0.0016812 | 0.019305 | 0.00022207 | -0.015656 | -0.0019461 | -0.0008851 | 0.021973 | 0.013862 | -0.011905 | -0.018369 | 0.025912 | -0.0034435 | -0.068665 | -0.027466 | -0.032043 | 0.041199 | 0.13275 | 0 | 0.091553 | 0.10529 | 0.13733 | -0.013733 | 0.073242 | 0.1831 | 0.11902 | 0.14191 | 80.4062 | -35.1654 | -35.0967 | 80.571 | 80.5298 | 80.4382 | 0.1236 | 0.032043 | 80.4245 | -35.0006 | -35.0647 | 80.6213 | 80.5801 | 80.5573 | 0.15564 | 0.13275 | 0.16479 | 0.073242 | 0.19684 | 0.086975 | 0.004577 | 0.15106 | 80.4108 | 80.5756 | -35.17 | -35.1517 | 80.4794 | 80.5115 | 80.3696 | 80.5435
5327.8594 | 120.726 | -105.2124 | 15.0101 | -0.15083 | -0.04303 | 0.00045503 | 0.019091 | -0.0042639 | -0.012239 | -0.0047231 | -0.028351 | 0.022401 | 0.011726 | -0.0063511 | -0.019651 | 0.025058 | -0.0064343 | -0.082397 | -0.009155 | -0.036621 | 0.054932 | 0.17395 | 0.022888 | 0.10986 | 0.10071 | 0.11444 | -0.027466 | 0.10986 | 0.19684 | 0.15564 | 0.15106 | 105.1758 | -15.0192 | -14.9551 | 105.3864 | 105.3223 | 105.2353 | 0.14648 | 0.059509 | 105.1849 | -14.8956 | -14.9002 | 105.4092 | 105.3635 | 105.368 | 0.17853 | 0.18311 | 0.21057 | 0.091553 | 0.2243 | 0.13733 | 0.027466 | 0.14191 | 105.2032 | 105.3268 | -15.0467 | -15.0375 | 105.2673 | 105.3223 | 105.13 | 105.3131
5329.6094 | 120.7489 | -105.3772 | 15.1245 | -0.17372 | -0.038117 | 0.00024143 | 0.019946 | -0.00084593 | -0.015229 | -0.0038687 | -0.068024 | 0.023896 | 0.015785 | -0.011692 | -0.018156 | 0.024631 | -0.0023755 | -0.086975 | -0.004578 | -0.036621 | -0.022888 | 0.064087 | -0.041199 | 0.036621 | -0.018311 | 0.15106 | -0.032043 | 0.009155 | 0.059509 | 0.004578 | 0.073242 | 105.3406 | -15.1291 | -15.1474 | 105.4413 | 105.4138 | 105.336 | 0.073242 | -0.004578 | 105.3452 | -14.9734 | -15.1154 | 105.4367 | 105.4504 | 105.3818 | 0.10529 | 0.036621 | 0.10071 | 0.013733 | 0.091552 | 0.041198 | 0.032043 | 0.18311 | 105.3726 | 105.5283 | -15.1611 | -15.1566 | 105.3543 | 105.3864 | 105.2902 | 105.3589
5331.3125 | 120.8359 | -105.9631 | 14.6622 | -0.1432 | -0.039612 | -0.00018577 | 0.022509 | -0.00084593 | -0.013307 | -0.0055777 | -0.13821 | 0.023896 | 0.013008 | -0.0097689 | -0.018797 | 0.027408 | -0.00088011 | -0.091553 | 0.013733 | -0.041199 | -0.036621 | 0.050354 | -0.11444 | -0.004578 | 0.004578 | 0.15564 | -0.059509 | 0.013733 | 0.068665 | -0.022888 | 0.059509 | 105.9219 | -14.6484 | -14.6988 | 106.0135 | 105.9586 | 105.8487 | 0.036621 | -0.073242 | 105.9036 | -14.5065 | -14.6484 | 106.0318 | 106.0226 | 105.9402 | 0.11902 | 0.036621 | 0.091553 | 0.004578 | 0.12817 | 0.073242 | 0.054932 | 0.21515 | 105.9769 | 106.1188 | -14.7034 | -14.7217 | 105.9265 | 105.9769 | 105.8716 | 105.9677
5333.0938 | 120.9091 | -105.661 | 15.0146 | -0.17372 | -0.041107 | 0.002164 | 0.022509 | 0.0036401 | -0.010316 | -0.0049367 | -0.1199 | 0.02411 | 0.015785 | -0.014896 | -0.01901 | 0.025272 | -0.0064343 | -0.07782 | 0.032043 | -0.068665 | -0.036621 | 0.050354 | -0.086975 | 0.009155 | 0.036621 | 0.13733 | -0.045776 | 0.032043 | 0.091553 | 0.022888 | 0.09613 | 105.5923 | -14.9826 | -15.0513 | 105.7114 | 105.6702 | 105.574 | 0.07782 | -0.01831 | 105.6152 | -14.8773 | -14.9826 | 105.7526 | 105.7571 | 105.6839 | 0.14191 | 0.068664 | 0.11902 | 0.032044 | 0.13733 | 0.077819 | 0.10071 | 0.18311 | 105.6931 | 105.7983 | -15.0833 | -15.0604 | 105.6244 | 105.6931 | 105.5832 | 105.6976
5334.7969 | 120.9961 | -105.1209 | 15.6006 | -0.1432 | -0.042603 | -0.001254 | 0.016742 | 0.0034265 | -0.014161 | -0.0019461 | -0.019196 | 0.021332 | 0.012153 | -0.015323 | -0.020506 | 0.027408 | -0.0038709 | -0.059509 | -0.004578 | -0.036621 | 0.032043 | 0.15106 | 0 | 0.086975 | 0.10071 | 0.11902 | -0.027466 | 0.059509 | 0.19226 | 0.11902 | 0.15106 | 105.0842 | -15.6052 | -15.5685 | 105.2719 | 105.2078 | 105.1209 | 0.1236 | 0.036621 | 105.0934 | -15.4816 | -15.5411 | 105.3131 | 105.2719 | 105.2399 | 0.17853 | 0.14649 | 0.18768 | 0.068664 | 0.21973 | 0.086975 | 0.032043 | 0.14649 | 105.1163 | 105.2399 | -15.6372 | -15.6281 | 105.1529 | 105.1804 | 105.0613 | 105.2216
5336.5469 | 120.5658 | -105.5054 | 14.6805 | -0.12794 | -0.041321 | 0.0025912 | 0.018878 | 8.47e-06 | -0.012239 | -0.0070731 | -0.040558 | 0.020905 | 0.014076 | -0.014469 | -0.015806 | 0.025485 | -0.00088011 | -0.086975 | 0.009155 | -0.041199 | -0.018311 | 0.10071 | -0.032043 | 0.050354 | 0.041199 | 0.13275 | -0.045776 | -0.013733 | 0.10071 | 0.041199 | 0.054932 | 105.4642 | -14.6713 | -14.6988 | 105.6061 | 105.5557 | 105.4733 | 0.091553 | 0.009156 | 105.4596 | -14.5477 | -14.6942 | 105.6061 | 105.5603 | 105.5466 | 0.10071 | 0.086975 | 0.14191 | 0.022888 | 0.14648 | 0.032043 | 0.050354 | 0.17853 | 105.5145 | 105.6381 | -14.7217 | -14.7263 | 105.4871 | 105.4916 | 105.4184 | 105.5466
5338.3125 | 120.9229 | -106.0272 | 14.534 | -0.18898 | -0.041321 | 0.00066863 | 0.02315 | -0.0017005 | -0.010102 | -0.0053641 | -0.098541 | 0.023041 | 0.01493 | -0.015537 | -0.02136 | 0.028903 | -0.0017347 | -0.14648 | 0.009155 | -0.064087 | -0.086975 | 0.009155 | -0.15106 | -0.027466 | -0.009155 | 0.14648 | -0.050354 | 0.036621 | 0.091553 | 0.027466 | 0.091553 | 105.9631 | -14.5248 | -14.621 | 106.0364 | 105.9998 | 105.8762 | 0.036621 | -0.086975 | 105.9769 | -14.3875 | -14.4974 | 106.1188 | 106.1188 | 106.0547 | 0.14191 | 0.07782 | 0.073242 | -0.022888 | 0.14191 | 0.086975 | 0.073242 | 0.19684 | 106.0364 | 106.1737 | -14.5981 | -14.5844 | 105.9402 | 106.0638 | 105.8807 | 106.0181
5340.0312 | 120.9457 | -106.2653 | 14.4424 | -0.17372 | -0.039826 | 0.0023776 | 0.022296 | -0.00041873 | -0.015229 | -0.0040823 | -0.10464 | 0.025819 | 0.014076 | -0.013828 | -0.01901 | 0.027621 | -0.0032299 | -0.12817 | 0.045776 | -0.07782 | -0.11444 | -0.022888 | -0.16022 | -0.054932 | -0.068665 | 0.15106 | -0.068665 | -0.013733 | 0.032043 | -0.018311 | 0.07782 | 106.1874 | -14.3967 | -14.5569 | 106.2424 | 106.2103 | 106.105 | 0.022888 | -0.082397 | 106.1966 | -14.2914 | -14.4562 | 106.2973 | 106.3431 | 106.2469 | 0.14649 | 0.050354 | 0.054932 | -0.036621 | 0.10071 | 0.054932 | 0.1236 | 0.21973 | 106.311 | 106.4163 | -14.5203 | -14.5111 | 106.1508 | 106.2515 | 106.1371 | 106.1966
5341.7969 | 120.9641 | -106.1874 | 14.6027 | -0.1432 | -0.038758 | 0.00024143 | 0.023364 | 0.0042811 | -0.01117 | -0.0040823 | -0.11075 | 0.023896 | 0.014717 | -0.014682 | -0.018369 | 0.028262 | -0.00066651 | -0.12817 | 0.045776 | -0.059509 | -0.11902 | -0.050354 | -0.16937 | -0.036621 | -0.064087 | 0.15564 | -0.073242 | -0.013733 | 0.022888 | -0.036621 | 0.064087 | 106.1279 | -14.5569 | -14.7217 | 106.1371 | 106.1508 | 106.0181 | 0.022888 | -0.10986 | 106.1142 | -14.447 | -14.6164 | 106.2103 | 106.2515 | 106.1508 | 0.13733 | 0.036621 | 0.009155 | -0.05951 | 0.09613 | 0.059509 | 0.10528 | 0.22888 | 106.2332 | 106.3431 | -14.6622 | -14.6759 | 106.0684 | 106.1737 | 106.0593 | 106.1234
5343.5625 | 120.9961 | -106.2241 | 14.6484 | -0.15846 | -0.041962 | 0.00045503 | 0.019519 | 0.0010767 | -0.013947 | -0.0047231 | -0.049713 | 0.022187 | 0.013435 | -0.015537 | -0.020078 | 0.026767 | -0.00045291 | -0.16022 | 0.027466 | -0.07782 | -0.10071 | 0 | -0.10529 | -0.009155 | -0.054932 | 0.15106 | -0.059509 | -0.045776 | 0.054932 | -0.004578 | 0.064087 | 106.1462 | -14.621 | -14.7491 | 106.2241 | 106.2149 | 106.1188 | 0.068665 | -0.027466 | 106.1646 | -14.4974 | -14.6942 | 106.279 | 106.2881 | 106.2195 | 0.1236 | 0.054931 | 0.07782 | -0.022888 | 0.11444 | 0.013733 | 0.10529 | 0.21057 | 106.2515 | 106.3751 | -14.7263 | -14.7079 | 106.1234 | 106.1783 | 106.0638 | 106.1691
5345.3281 | 120.3827 | -5.1956 | 115.7547 | -0.13557 | -0.034699 | 0.001523 | 0.02315 | -0.00063233 | -0.010957 | -0.0038687 | -0.12296 | 0.022828 | 0.014076 | -0.014682 | -0.017942 | 0.026767 | 0.0010425 | -0.13733 | 0.036621 | -0.082397 | -0.1236 | -0.032043 | -0.16022 | -0.050354 | -0.064087 | 0.15106 | -0.068665 | -0.004578 | 0.018311 | -0.041199 | 0.054932 | 5.1132 | -115.7181 | -115.8783 | 5.1636 | 5.1453 | 5.0354 | 0.032043 | -0.07782 | 5.127 | -115.6036 | -115.7593 | 5.2139 | 5.2505 | 5.1544 | 0.1236 | 0.027466 | 0.050354 | -0.041199 | 0.086976 | 0.064087 | 0.11902 | 0.21973 | 5.2322 | 5.3467 | -115.8371 | -115.8234 | 5.072 | 5.191 | 5.0583 | 5.1315
5347.0312 | 120.4788 | -4.8203 | 116.1438 | -0.15083 | -0.043244 | -0.00082677 | 0.021228 | 0.0036401 | -0.012879 | -0.0055777 | -0.092438 | 0.02475 | 0.013435 | -0.014041 | -0.018797 | 0.028476 | 0.00061529 | -0.09613 | 0.013733 | -0.050354 | -0.041199 | 0.054932 | -0.082397 | -0.004578 | 0.032043 | 0.14191 | -0.045776 | 0.059509 | 0.10071 | 0.054932 | 0.10071 | 4.7699 | -116.1301 | -116.185 | 4.8752 | 4.8157 | 4.7379 | 0.045776 | -0.032043 | 4.7745 | -116.0019 | -116.0843 | 4.921 | 4.921 | 4.8752 | 0.14648 | 0.10071 | 0.10529 | 0.009155 | 0.14648 | 0.10528 | 0.064087 | 0.18768 | 4.834 | 4.9622 | -116.1942 | -116.1896 | 4.7791 | 4.8798 | 4.7241 | 4.8523
5348.7969 | 120.9641 | -4.5547 | 116.4825 | -0.097427 | -0.041535 | -0.0023222 | 0.017382 | 0.00043587 | -0.013947 | -0.0038687 | -0.037506 | 0.023469 | 0.014503 | -0.015109 | -0.01901 | 0.025699 | -0.0066479 | -0.13275 | 0.022888 | -0.086975 | -0.09613 | 0.027466 | -0.10071 | 0 | -0.059509 | 0.14648 | -0.082397 | -0.036621 | 0.064087 | 0.013733 | 0.045776 | 4.4678 | -116.4597 | -116.5787 | 4.5822 | 4.5547 | 4.454 | 0.086975 | -0.013733 | 4.4724 | -116.3361 | -116.5192 | 4.6188 | 4.6005 | 4.5685 | 0.12817 | 0.09613 | 0.11444 | -0.009155 | 0.14648 | 0.045776 | 0.10986 | 0.22888 | 4.5776 | 4.7012 | -116.5695 | -116.5649 | 4.4586 | 4.5181 | 4.422 | 4.4952
5350.4844 | 120.3003 | -2.7786 | 118.2083 | -0.18135 | -0.039185 | 0.001523 | 0.020373 | 0.00022207 | -0.0090342 | -0.0040823 | -0.11075 | 0.023041 | 0.01493 | -0.016605 | -0.019224 | 0.030826 | -0.0032299 | -0.10529 | 0.018311 | -0.068665 | -0.086975 | 0 | -0.16479 | -0.027466 | -0.050354 | 0.16022 | -0.064087 | -0.050354 | 0.059509 | -0.036621 | 0.041199 | 2.71 | -118.19 | -118.2953 | 2.7786 | 2.7512 | 2.6138 | 0.041199 | -0.09613 | 2.7145 | -118.0481 | -118.2587 | 2.8381 | 2.8198 | 2.742 | 0.10529 | 0.027466 | 0.068665 | -0.01831 | 0.1236 | 0.013733 | 0.086976 | 0.2243 | 2.7969 | 2.9388 | -118.277 | -118.2724 | 2.6917 | 2.7283 | 2.6733 | 2.7283
5352.2344 | 121.0098 | -2.7008 | 118.3182 | -0.13557 | -0.040894 | 0.0017368 | 0.018451 | 0.0040675 | -0.011811 | -0.0064321 | -0.089386 | 0.021546 | 0.01493 | -0.0099827 | -0.018797 | 0.02634 | 0.00018809 | -0.082397 | 0.022888 | -0.073242 | -0.054932 | 0.059509 | -0.091553 | 0 | 0.018311 | 0.13733 | -0.073242 | 0 | 0.086975 | 0.004578 | 0.10071 | 2.6276 | -118.2953 | -118.3731 | 2.7603 | 2.7008 | 2.6093 | 0.073242 | -0.018311 | 2.6276 | -118.1808 | -118.3182 | 2.7878 | 2.8015 | 2.7054 | 0.17395 | 0.07782 | 0.13275 | 0.01831 | 0.16022 | 0.073242 | 0.09613 | 0.21057 | 2.7237 | 2.8381 | -118.3914 | -118.3914 | 2.6459 | 2.7008 | 2.6184 | 2.7191
5354 | 120.607 | -71.5073 | 47.7448 | -0.20424 | -0.041962 | 0.00045503 | 0.019091 | 0.0027857 | -0.009675 | -0.0064321 | -0.016144 | 0.023255 | 0.015571 | -0.014255 | -0.017729 | 0.026126 | -0.0019483 | -0.068665 | -0.009155 | -0.041199 | 0.013733 | 0.13733 | -0.032043 | 0.073242 | 0.10529 | 0.10529 | -0.041199 | 0.073242 | 0.14648 | 0.1236 | 0.14648 | 71.4661 | -47.7539 | -47.731 | 71.6446 | 71.5805 | 71.4752 | 0.11444 | 0.009156 | 71.4661 | -47.6395 | -47.6715 | 71.6537 | 71.6537 | 71.6309 | 0.18768 | 0.16479 | 0.17853 | 0.054932 | 0.18768 | 0.11444 | 0.032044 | 0.14649 | 71.4981 | 71.6125 | -47.7859 | -47.7859 | 71.521 | 71.5805 | 71.4386 | 71.6125
5355.7031 | 120.8588 | -7.1228 | 113.5712 | -0.12032 | -0.04303 | -0.0031766 | 0.016742 | -0.0057593 | -0.011384 | -0.0075003 | 0.017425 | 0.022614 | 0.017066 | -0.011692 | -0.01901 | 0.027194 | -0.0025891 | -0.059509 | -0.013733 | -0.041199 | 0.032043 | 0.1831 | 0.018311 | 0.13275 | 0.11444 | 0.1236 | -0.032043 | 0.07782 | 0.21515 | 0.15106 | 0.16022 | 7.0816 | -113.5849 | -113.5391 | 7.3059 | 7.2556 | 7.1411 | 0.17395 | 0.05951 | 7.0908 | -113.4476 | -113.4933 | 7.338 | 7.283 | 7.2739 | 0.19226 | 0.18311 | 0.2243 | 0.073242 | 0.24719 | 0.10986 | 0.027466 | 0.15564 | 7.1091 | 7.2464 | -113.6124 | -113.6032 | 7.1548 | 7.2006 | 7.0633 | 7.2372
5357.4688 | 120.8862 | -6.546 | 114.2395 | -0.20424 | -0.04068 | 0.00088223 | 0.018451 | 0.0032129 | -0.012666 | -0.0060049 | -0.01004 | 0.023469 | 0.015571 | -0.013187 | -0.017088 | 0.026981 | -0.0019483 | -0.091553 | -0.018311 | -0.036621 | -0.013733 | 0.10071 | -0.059509 | 0.059509 | 0.050354 | 0.11902 | -0.045776 | 0.018311 | 0.1236 | 0.09613 | 0.1236 | 6.5094 | -114.2578 | -114.2532 | 6.6467 | 6.6055 | 6.4865 | 0.09613 | -0.022888 | 6.5002 | -114.1205 | -114.2212 | 6.6696 | 6.6696 | 6.6422 | 0.16937 | 0.14191 | 0.13733 | 0.022888 | 0.16937 | 0.064087 | 0.01831 | 0.16479 | 6.5277 | 6.665 | -114.2761 | -114.2853 | 6.5323 | 6.5643 | 6.4545 | 6.5964
5359.2344 | 120.8862 | -5.7175 | 115.21 | -0.089798 | -0.041748 | -0.00018577 | 0.018451 | -0.0025549 | -0.012452 | -0.0070731 | -0.058869 | 0.024537 | 0.014503 | -0.013614 | -0.019865 | 0.025272 | -0.0010937 | -0.14648 | 0.027466 | -0.086975 | -0.09613 | -0.004578 | -0.1236 | -0.013733 | -0.054932 | 0.15564 | -0.086975 | -0.064087 | 0.073242 | 0.009155 | 0.059509 | 5.6305 | -115.1825 | -115.3061 | 5.7129 | 5.7037 | 5.5939 | 0.073242 | -0.036621 | 5.6305 | -115.0543 | -115.274 | 5.7907 | 5.777 | 5.7266 | 0.14648 | 0.09613 | 0.082397 | -0.009155 | 0.16022 | 0.022888 | 0.11444 | 0.24261 | 5.7449 | 5.8731 | -115.2969 | -115.2969 | 5.6213 | 5.6534 | 5.571 | 5.6625
5360.9375 | 121.0236 | -4.7653 | 116.1163 | -0.19661 | -0.039185 | 0.0017368 | 0.018878 | 0.00064947 | -0.011384 | -0.0032277 | -0.01004 | 0.022401 | 0.01728 | -0.010623 | -0.019438 | 0.026126 | -0.0051525 | -0.07782 | -0.018311 | -0.041199 | 0.018311 | 0.13733 | -0.041199 | 0.073242 | 0.10529 | 0.10986 | -0.045776 | 0.050354 | 0.15106 | 0.09613 | 0.14191 | 4.7241 | -116.1346 | -116.098 | 4.9026 | 4.8386 | 4.7241 | 0.11444 | 0 | 4.7195 | -116.0065 | -116.066 | 4.9164 | 4.9072 | 4.8614 | 0.18768 | 0.14191 | 0.17853 | 0.05951 | 0.19684 | 0.09613 | 0.022888 | 0.15564 | 4.747 | 4.8752 | -116.1575 | -116.1621 | 4.7836 | 4.8157 | 4.6875 | 4.8706
5362.7031 | 121.0098 | -4.7333 | 116.2628 | -0.20424 | -0.03833 | 0.001523 | 0.022723 | -0.0012731 | -0.011598 | -0.0057913 | -0.11685 | 0.023255 | 0.017066 | -0.0057101 | -0.020292 | 0.027621 | -0.0019483 | -0.12817 | 0.018311 | -0.073242 | -0.10529 | -0.009155 | -0.14191 | -0.013733 | -0.032043 | 0.14648 | -0.073242 | -0.036621 | 0.059509 | 0.004578 | 0.09613 | 4.66 | -116.2445 | -116.3681 | 4.7241 | 4.7195 | 4.5914 | 0.059509 | -0.068665 | 4.66 | -116.1163 | -116.2994 | 4.7928 | 4.8294 | 4.7379 | 0.16937 | 0.07782 | 0.064087 | -0.032044 | 0.13275 | 0.036621 | 0.091553 | 0.21973 | 4.7516 | 4.8798 | -116.3361 | -116.3361 | 4.628 | 4.6967 | 4.6051 | 4.7012
5364.4688 | 121.0602 | -4.6829 | 116.2949 | -0.18898 | -0.040467 | 0.00024143 | 0.022509 | 0.0055627 | -0.012452 | -0.0060049 | -0.1077 | 0.023469 | 0.014717 | -0.018314 | -0.019865 | 0.026981 | -0.0034435 | -0.086975 | 0.013733 | -0.086975 | -0.045776 | 0.059509 | -0.082397 | 0.004578 | 0.018311 | 0.16022 | -0.045776 | -0.004578 | 0.10529 | 0.054932 | 0.10986 | 4.5959 | -116.2811 | -116.3406 | 4.7424 | 4.6875 | 4.6005 | 0.091553 | 0.004578 | 4.6371 | -116.1346 | -116.2994 | 4.7882 | 4.7928 | 4.7379 | 0.15564 | 0.10071 | 0.14648 | 0.041199 | 0.15106 | 0.041198 | 0.10071 | 0.20599 | 4.6967 | 4.8431 | -116.3818 | -116.3406 | 4.6371 | 4.6783 | 4.5959 | 4.7012
5366.2344 | 121.0739 | -4.715 | 116.3177 | -0.16609 | -0.042389 | 0.00045503 | 0.019519 | 0.0023585 | -0.011811 | -0.0036551 | -0.10464 | 0.024323 | 0.017066 | -0.010837 | -0.019224 | 0.028903 | -0.0042981 | -0.13275 | 0.036621 | -0.07782 | -0.091553 | -0.009155 | -0.16022 | -0.032043 | -0.036621 | 0.13733 | -0.068665 | -0.032043 | 0.068665 | 0 | 0.09613 | 4.6371 | -116.2811 | -116.4093 | 4.7058 | 4.6829 | 4.5547 | 0.045777 | -0.082397 | 4.6463 | -116.1804 | -116.3498 | 4.7836 | 4.8111 | 4.715 | 0.16479 | 0.068665 | 0.068665 | -0.013733 | 0.13733 | 0.036622 | 0.11444 | 0.20599 | 4.7516 | 4.8523 | -116.3956 | -116.3864 | 4.6234 | 4.6829 | 4.5822 | 4.6783
5367.9375 | 121.0693 | -4.4632 | 116.6428 | -0.13557 | -0.042389 | -0.0021084 | 0.017596 | 0.00043587 | -0.012879 | -0.0051505 | -0.037506 | 0.024323 | 0.018562 | -0.019809 | -0.019438 | 0.027835 | -0.0042981 | -0.14648 | 0.045776 | -0.091553 | -0.10529 | -0.013733 | -0.10986 | -0.018311 | -0.064087 | 0.16479 | -0.07782 | -0.059509 | 0.054932 | 0.004578 | 0.064087 | 4.3716 | -116.597 | -116.748 | 4.4495 | 4.4449 | 4.3533 | 0.073242 | -0.01831 | 4.3854 | -116.478 | -116.7023 | 4.5181 | 4.5273 | 4.4678 | 0.14191 | 0.082398 | 0.07782 | -0.013733 | 0.13275 | 0.018311 | 0.13733 | 0.24261 | 4.509 | 4.628 | -116.7343 | -116.7206 | 4.3579 | 4.4037 | 4.3167 | 4.3991
5369.7031 | 121.1884 | -4.3488 | 116.6611 | -0.15846 | -0.04068 | 0.001523 | 0.018664 | -0.0034095 | -0.010102 | -0.0051505 | -0.037506 | 0.023255 | 0.014717 | -0.015323 | -0.019224 | 0.025272 | -0.0045117 | -0.068665 | -0.013733 | -0.036621 | 0.018311 | 0.15106 | -0.022888 | 0.068665 | 0.09613 | 0.10071 | -0.027466 | 0.054932 | 0.16479 | 0.10986 | 0.14648 | 4.3121 | -116.6748 | -116.6428 | 4.4998 | 4.4174 | 4.3259 | 0.10529 | 0.013733 | 4.3213 | -116.5604 | -116.6061 | 4.5135 | 4.4952 | 4.4586 | 0.17395 | 0.13733 | 0.18768 | 0.054932 | 0.19226 | 0.082398 | 0.022888 | 0.12817 | 4.335 | 4.4495 | -116.6977 | -116.6885 | 4.3671 | 4.4037 | 4.2801 | 4.4449
5371.4062 | 121.2204 | -4.4861 | 116.5924 | -0.17372 | -0.041535 | 0.00088223 | 0.018664 | -0.0014867 | -0.012452 | -0.0034415 | 0.0021667 | 0.023682 | 0.013221 | -0.016391 | -0.01901 | 0.026126 | -0.0079297 | -0.11902 | 0.009155 | -0.045776 | -0.036621 | 0.073242 | -0.07782 | 0.041199 | 0 | 0.11444 | -0.050354 | 0.004578 | 0.13275 | 0.086975 | 0.14191 | 4.4403 | -116.5833 | -116.629 | 4.5593 | 4.5273 | 4.4083 | 0.086975 | -0.032044 | 4.4357 | -116.478 | -116.5878 | 4.6188 | 4.628 | 4.5731 | 0.19226 | 0.13733 | 0.11902 | 0.009155 | 0.18311 | 0.054932 | 0.054931 | 0.16479 | 4.4952 | 4.6005 | -116.6382 | -116.6428 | 4.4495 | 4.4907 | 4.3671 | 4.4861
5373.1719 | 121.1746 | -4.5502 | 116.6382 | -0.17372 | -0.041535 | 0.0010958 | 0.022296 | 0.0025721 | -0.012239 | -0.0053641 | -0.12601 | 0.023682 | 0.013648 | -0.0089145 | -0.019438 | 0.027194 | 0.00082889 | -0.082397 | 0.022888 | -0.068665 | -0.027466 | 0.054932 | -0.082397 | 0.004578 | 0.004578 | 0.13275 | -0.045776 | -0.009155 | 0.068665 | 0.018311 | 0.09613 | 4.4815 | -116.6153 | -116.6656 | 4.6051 | 4.5547 | 4.4678 | 0.073243 | -0.013732 | 4.5044 | -116.5054 | -116.6473 | 4.6188 | 4.6463 | 4.5685 | 0.14191 | 0.064087 | 0.1236 | 0.041199 | 0.11444 | 0.036621 | 0.091553 | 0.17853 | 4.5731 | 4.6829 | -116.7068 | -116.684 | 4.5227 | 4.541 | 4.4678 | 4.5547
5374.875 | 121.1334 | -4.4449 | 116.6885 | -0.16609 | -0.039826 | 0.0013094 | 0.020373 | 0.0034265 | -0.011598 | -0.0047231 | -0.1138 | 0.023896 | 0.017707 | -0.01575 | -0.019865 | 0.025912 | -0.0015209 | -0.15106 | 0.036621 | -0.073242 | -0.11444 | -0.045776 | -0.1831 | -0.036621 | -0.082397 | 0.16022 | -0.086975 | -0.054932 | 0.013733 | -0.022888 | 0.068665 | 4.3716 | -116.6519 | -116.803 | 4.3991 | 4.4083 | 4.2618 | 0.036621 | -0.10986 | 4.3579 | -116.5283 | -116.7435 | 4.4586 | 4.5136 | 4.422 | 0.15564 | 0.064087 | 0.027466 | -0.041199 | 0.10071 | 0.032043 | 0.10986 | 0.24719 | 4.4815 | 4.6051 | -116.7618 | -116.7755 | 4.3304 | 4.39 | 4.2938 | 4.3625
5376.6406 | 121.1792 | -3.8635 | 117.3157 | -0.16609 | -0.037689 | 0.0019504 | 0.019946 | 0.0036401 | -0.01053 | -0.0060049 | -0.092438 | 0.023255 | 0.015144 | -0.0084873 | -0.018156 | 0.025058 | -0.0013073 | -0.12817 | 0.013733 | -0.068665 | -0.09613 | -0.041199 | -0.16022 | -0.064087 | -0.091553 | 0.16479 | -0.07782 | -0.068665 | 0.004578 | -0.032043 | 0.068665 | 3.7949 | -117.3019 | -117.4118 | 3.8223 | 3.7994 | 3.7033 | 0.004578 | -0.091552 | 3.7857 | -117.1509 | -117.3843 | 3.8681 | 3.9322 | 3.8315 | 0.14649 | 0.045777 | 0.027466 | -0.027465 | 0.082398 | 0.009155 | 0.082398 | 0.24261 | 3.8773 | 4.0283 | -117.3843 | -117.3935 | 3.7674 | 3.7949 | 3.7354 | 3.772
5378.3906 | 120.4285 | -82.1915 | 38.1546 | -0.097427 | -0.041748 | 0.00045503 | 0.018237 | -0.0017005 | -0.012452 | -0.0057913 | -0.022247 | 0.023255 | 0.014717 | -0.011478 | -0.015592 | 0.024631 | 0.0042469 | -0.18768 | 0.045776 | -0.068665 | -0.11444 | 0 | -0.09613 | -0.022888 | -0.07782 | 0.15106 | -0.064087 | -0.064087 | 0.050354 | 0.009155 | 0.068665 | 82.1228 | -38.1088 | -38.269 | 82.1915 | 82.1686 | 82.0953 | 0.045777 | -0.027465 | 82.1274 | -38.0035 | -38.2187 | 82.2418 | 82.2601 | 82.2006 | 0.13275 | 0.073242 | 0.068665 | -0.045776 | 0.11444 | 0 | 0.11444 | 0.21515 | 82.2372 | 82.3425 | -38.2233 | -38.2187 | 82.077 | 82.1274 | 82.0038 | 82.1136
5380.1719 | 120.2316 | -10.7208 | 109.7992 | -0.16609 | -0.038971 | -0.00039957 | 0.021655 | 0.0053491 | -0.010743 | -0.0051505 | -0.10159 | 0.023255 | 0.016426 | -0.017032 | -0.019865 | 0.027194 | -0.0042981 | -0.11902 | 0.009155 | -0.086975 | -0.09613 | -0.004578 | -0.13733 | -0.036621 | -0.064087 | 0.15106 | -0.073242 | -0.064087 | 0.022888 | -0.022888 | 0.059509 | 10.6338 | -109.79 | -109.8953 | 10.7162 | 10.6842 | 10.5835 | 0.050354 | -0.050354 | 10.6476 | -109.6481 | -109.8633 | 10.7437 | 10.7803 | 10.6979 | 0.13275 | 0.050354 | 0.082397 | -0.009155 | 0.09613 | 0.009155 | 0.09613 | 0.2243 | 10.73 | 10.8719 | -109.8862 | -109.8724 | 10.6247 | 10.6567 | 10.6018 | 10.6567
5381.8594 | 120.9732 | -111.0214 | 9.4254 | -0.16609 | -0.044098 | 0.0010958 | 0.018451 | -0.0019141 | -0.013734 | -0.0051505 | 0.047943 | 0.022401 | 0.015144 | -0.015537 | -0.018583 | 0.02399 | -0.00066651 | -0.10529 | -0.013733 | -0.036621 | 0.032043 | 0.16022 | 0.041199 | 0.10986 | 0.09613 | 0.10529 | -0.013733 | 0.073242 | 0.21057 | 0.15106 | 0.16937 | 110.9848 | -9.4391 | -9.3933 | 111.1816 | 111.1313 | 111.0626 | 0.14648 | 0.07782 | 111.0077 | -9.3201 | -9.3521 | 111.232 | 111.1908 | 111.1725 | 0.18311 | 0.16479 | 0.19684 | 0.068664 | 0.2243 | 0.086975 | 0.022888 | 0.11902 | 111.0077 | 111.1267 | -9.462 | -9.4391 | 111.0535 | 111.0947 | 110.9161 | 111.1176
5383.6094 | 121.0144 | -119.1605 | 1.4923 | -0.17372 | -0.041107 | 0.0013094 | 0.019732 | 0.0015039 | -0.014375 | -0.0040823 | 0.023529 | 0.022614 | 0.015144 | -0.017459 | -0.01901 | 0.025058 | -0.00023931 | -0.13275 | 0.004578 | -0.045776 | -0.045776 | 0.068665 | -0.050354 | 0.059509 | 0.013733 | 0.11902 | -0.045776 | 0.018311 | 0.10986 | 0.068665 | 0.1236 | 119.1147 | -1.4877 | -1.5381 | 119.2291 | 119.22 | 119.1101 | 0.10528 | -0.004578 | 119.1147 | -1.3733 | -1.474 | 119.2703 | 119.2841 | 119.2291 | 0.16937 | 0.11444 | 0.11444 | 0 | 0.15564 | 0.064087 | 0.050354 | 0.16479 | 119.165 | 119.2795 | -1.5381 | -1.5381 | 119.1147 | 119.1788 | 119.0277 | 119.1742
5385.375 | 121.1014 | -119.696 | 0.99792 | -0.23476 | -0.039398 | 0.002164 | 0.0208 | -0.00063233 | -0.013307 | -0.0028005 | -0.034454 | 0.021973 | 0.011299 | -0.0099827 | -0.021787 | 0.026553 | -0.0079297 | -0.059509 | 0 | -0.032043 | 0.013733 | 0.10986 | -0.022888 | 0.07782 | 0.10986 | 0.10986 | -0.022888 | 0.1236 | 0.16937 | 0.1236 | 0.17395 | 119.664 | -0.99792 | -0.98419 | 119.8059 | 119.7739 | 119.6732 | 0.10986 | 0.009155 | 119.6732 | -0.88806 | -0.87433 | 119.8654 | 119.87 | 119.8196 | 0.19684 | 0.14648 | 0.14191 | 0.045776 | 0.19226 | 0.14648 | 0.032043 | 0.13275 | 119.696 | 119.8059 | -1.03 | -1.0208 | 119.7098 | 119.8196 | 119.6365 | 119.8059
5387.125 | 120.9961 | -0.40741 | 120.5566 | -0.20424 | -0.04303 | -0.0010404 | 0.02016 | -0.00063233 | -0.012879 | -0.0025869 | -0.0008851 | 0.022187 | 0.014076 | -0.011478 | -0.018583 | 0.025485 | -0.0028027 | -0.10529 | -0.004578 | -0.032043 | -0.041199 | 0.073242 | -0.07782 | 0.032043 | 0.027466 | 0.10071 | -0.045776 | 0.041199 | 0.11902 | 0.068665 | 0.1236 | 0.37537 | -120.5612 | -120.5978 | 0.48065 | 0.43945 | 0.32959 | 0.064086 | -0.045777 | 0.36163 | -120.4559 | -120.5154 | 0.52643 | 0.53101 | 0.47608 | 0.16937 | 0.11444 | 0.10529 | -0.009156 | 0.16479 | 0.086975 | 0.027465 | 0.14648 | 0.40283 | 0.50812 | -120.5887 | -120.6024 | 0.36621 | 0.44861 | 0.30212 | 0.43488
5388.8281 | 121.0556 | -0.3891 | 120.575 | -0.15083 | -0.040039 | -0.00082677 | 0.021014 | 8.47e-06 | -0.010743 | -0.0021597 | -0.022247 | 0.021546 | 0.014503 | -0.018527 | -0.019438 | 0.024417 | -0.0053661 | -0.10529 | -0.013733 | -0.027466 | -0.027466 | 0.086975 | -0.068665 | 0.050354 | 0.018311 | 0.10986 | -0.059509 | 0.045776 | 0.11444 | 0.064087 | 0.12817 | 0.36163 | -120.5887 | -120.6024 | 0.47607 | 0.43945 | 0.32043 | 0.07782 | -0.041199 | 0.32959 | -120.4651 | -120.5292 | 0.50354 | 0.51727 | 0.45319 | 0.18768 | 0.1236 | 0.11444 | 0 | 0.17395 | 0.10528 | 0.013733 | 0.16937 | 0.37537 | 0.49896 | -120.6024 | -120.6345 | 0.36163 | 0.43487 | 0.28381 | 0.40741
5390.5781 | 121.1151 | -0.38452 | 120.6436 | -0.1432 | -0.042389 | 0.00066863 | 0.019946 | 0.0010767 | -0.012025 | -0.0036551 | -0.037506 | 0.021332 | 0.014503 | -0.0087009 | -0.020506 | 0.02634 | -0.0028027 | -0.064087 | -0.027466 | -0.027466 | 0.032043 | 0.14191 | -0.004578 | 0.091553 | 0.091553 | 0.12817 | -0.032043 | 0.064087 | 0.17853 | 0.12817 | 0.13275 | 0.35706 | -120.6711 | -120.6116 | 0.52643 | 0.47607 | 0.37994 | 0.11902 | 0.022888 | 0.35248 | -120.5154 | -120.5795 | 0.56305 | 0.51727 | 0.5127 | 0.16479 | 0.16022 | 0.16937 | 0.059509 | 0.21057 | 0.09613 | 0 | 0.16022 | 0.35706 | 0.5127 | -120.6711 | -120.6757 | 0.41656 | 0.44861 | 0.32043 | 0.47607
5392.3281 | 121.1426 | -0.38452 | 120.6619 | -0.20424 | -0.042603 | -0.00082677 | 0.0208 | 0.0032129 | -0.014375 | -0.0049367 | -0.025299 | 0.022401 | 0.014503 | -0.013828 | -0.019224 | 0.02634 | -0.0066479 | -0.10071 | -0.013733 | -0.036621 | -0.045776 | 0.059509 | -0.068665 | 0.045776 | 0.036621 | 0.13275 | -0.050354 | 0.036621 | 0.14191 | 0.09613 | 0.1236 | 0.3479 | -120.6757 | -120.7077 | 0.44403 | 0.4303 | 0.31586 | 0.082397 | -0.032044 | 0.33417 | -120.5292 | -120.6253 | 0.52643 | 0.50812 | 0.48065 | 0.17395 | 0.14648 | 0.09613 | -0.009155 | 0.19226 | 0.086975 | 0.022888 | 0.18311 | 0.37079 | 0.51727 | -120.6985 | -120.7123 | 0.33875 | 0.42114 | 0.28381 | 0.42114
5394.0312 | 121.0922 | -0.4303 | 120.7169 | -0.1432 | -0.042176 | 2.7834e-05 | 0.019305 | 0.0015039 | -0.012025 | -0.0015189 | -0.046661 | 0.023041 | 0.01493 | -0.0080601 | -0.017942 | 0.025272 | -0.0040845 | -0.07782 | 0 | -0.054932 | -0.032043 | 0.073242 | -0.054932 | 0.041199 | -0.018311 | 0.12817 | -0.068665 | -0.027466 | 0.07782 | 0.018311 | 0.073242 | 0.37537 | -120.7169 | -120.7489 | 0.50354 | 0.4715 | 0.37537 | 0.096131 | 0 | 0.36163 | -120.5887 | -120.7443 | 0.50812 | 0.50354 | 0.44861 | 0.14191 | 0.086976 | 0.12817 | 0.022889 | 0.14649 | 0.041199 | 0.054932 | 0.19684 | 0.4303 | 0.55847 | -120.7718 | -120.7855 | 0.39826 | 0.40283 | 0.35248 | 0.41199
5395.7812 | 121.2067 | -0.36621 | 120.7031 | -0.18135 | -0.041962 | -0.00018577 | 0.019946 | -0.0017005 | -0.011811 | -0.0042959 | -0.028351 | 0.020905 | 0.015144 | -0.0067783 | -0.019438 | 0.027194 | -0.0038709 | -0.064087 | -0.013733 | -0.045776 | 0.041199 | 0.14191 | -0.004578 | 0.086975 | 0.086975 | 0.11902 | -0.045776 | 0.050354 | 0.18768 | 0.11902 | 0.15564 | 0.32044 | -120.7169 | -120.6619 | 0.50812 | 0.45319 | 0.36163 | 0.13275 | 0.041198 | 0.32044 | -120.5841 | -120.6528 | 0.55389 | 0.52185 | 0.48523 | 0.20142 | 0.16479 | 0.18768 | 0.086975 | 0.23346 | 0.09613 | 0.032043 | 0.16479 | 0.35248 | 0.48523 | -120.7489 | -120.7489 | 0.40741 | 0.41657 | 0.30212 | 0.45319
5397.5312 | 121.1563 | -0.41657 | 120.7535 | -0.12032 | -0.041107 | -0.001254 | 0.018878 | -0.00041873 | -0.012666 | -0.0045095 | -0.049713 | 0.022614 | 0.014076 | -0.01575 | -0.018583 | 0.025272 | -0.0045117 | -0.10071 | -0.009155 | -0.050354 | -0.041199 | 0.073242 | -0.050354 | 0.045776 | 0 | 0.14191 | -0.054932 | -0.041199 | 0.11902 | 0.027466 | 0.054932 | 0.36621 | -120.7626 | -120.7947 | 0.48981 | 0.46234 | 0.36621 | 0.09613 | 0 | 0.36163 | -120.6116 | -120.7947 | 0.53558 | 0.4715 | 0.44403 | 0.10986 | 0.082398 | 0.1236 | 0.009155 | 0.17395 | 0.013733 | 0.041199 | 0.19684 | 0.40741 | 0.55847 | -120.8038 | -120.8084 | 0.37537 | 0.37537 | 0.31586 | 0.41657
5399.2969 | 120.3506 | -0.37079 | 119.8334 | -0.19661 | -0.042176 | -0.00082677 | 0.022296 | 0.00086307 | -0.010316 | -0.0036551 | -0.080231 | 0.026032 | 0.014289 | -0.011478 | -0.020292 | 0.027621 | -0.0023755 | -0.1236 | 0.009155 | -0.068665 | -0.045776 | 0.032043 | -0.11902 | 0.009155 | 0.022888 | 0.10986 | -0.068665 | 0.068665 | 0.14191 | 0.068665 | 0.14191 | 0.30212 | -119.8242 | -119.8792 | 0.40283 | 0.37994 | 0.25177 | 0.07782 | -0.050354 | 0.30212 | -119.7235 | -119.7647 | 0.5127 | 0.5127 | 0.43945 | 0.21057 | 0.13733 | 0.10071 | 0.022889 | 0.21057 | 0.13733 | 0.07782 | 0.17853 | 0.37994 | 0.48065 | -119.902 | -119.902 | 0.32501 | 0.43945 | 0.24719 | 0.39368
5401 | 120.6802 | -0.38452 | 120.2637 | -0.16609 | -0.038758 | -0.00082677 | 0.0208 | -0.00020513 | -0.01117 | -0.0057913 | -0.1077 | 0.023041 | 0.014289 | -0.016178 | -0.020292 | 0.028262 | -0.0010937 | -0.082397 | 0.013733 | -0.068665 | -0.054932 | 0.041199 | -0.082397 | 0.004578 | 0.009155 | 0.14648 | -0.045776 | 0.013733 | 0.10986 | 0.050354 | 0.10529 | 0.31586 | -120.2499 | -120.3186 | 0.42572 | 0.3891 | 0.30212 | 0.073243 | -0.013732 | 0.33875 | -120.1172 | -120.2499 | 0.49438 | 0.48981 | 0.43488 | 0.15106 | 0.09613 | 0.10986 | 0.013733 | 0.15564 | 0.059509 | 0.082398 | 0.19226 | 0.39825 | 0.531 | -120.3323 | -120.3094 | 0.32959 | 0.39825 | 0.30212 | 0.39368
5402.7656 | 120.7993 | -0.40283 | 120.3781 | -0.10506 | -0.040894 | 0.00024143 | 0.0208 | 0.00043587 | -0.010743 | -0.0053641 | -0.10159 | 0.025391 | 0.015571 | -0.0095553 | -0.019865 | 0.026767 | -0.0047253 | -0.10071 | 0.022888 | -0.073242 | -0.045776 | 0.054932 | -0.09613 | 0.009155 | 0.018311 | 0.13733 | -0.059509 | 0.009155 | 0.1236 | 0.054932 | 0.11444 | 0.32959 | -120.3552 | -120.4239 | 0.45776 | 0.41199 | 0.3067 | 0.082397 | -0.022888 | 0.34332 | -120.2408 | -120.369 | 0.52643 | 0.51727 | 0.45776 | 0.17395 | 0.11444 | 0.12817 | 0.027466 | 0.1831 | 0.068664 | 0.09613 | 0.19684 | 0.42572 | 0.54016 | -120.4514 | -120.4376 | 0.35706 | 0.41199 | 0.30212 | 0.42114
5404.5312 | 120.8725 | -0.39825 | 120.4559 | -0.16609 | -0.042176 | -0.001254 | 0.018664 | -0.0019141 | -0.012239 | -0.0068593 | -0.01004 | 0.02411 | 0.014503 | -0.0228 | -0.018583 | 0.027194 | -0.0013073 | -0.064087 | -0.009155 | -0.068665 | -0.009155 | 0.10529 | -0.009155 | 0.068665 | 0.032043 | 0.1236 | -0.050354 | -0.009155 | 0.1236 | 0.068665 | 0.10529 | 0.32959 | -120.4651 | -120.4651 | 0.50354 | 0.46692 | 0.3891 | 0.13733 | 0.05951 | 0.3479 | -120.3323 | -120.4651 | 0.52185 | 0.50354 | 0.46692 | 0.15564 | 0.11902 | 0.17395 | 0.05951 | 0.17395 | 0.041199 | 0.05951 | 0.17395 | 0.3891 | 0.52185 | -120.5246 | -120.5063 | 0.3891 | 0.3891 | 0.33417 | 0.4303
5406.2969 | 120.8633 | -0.41657 | 120.5246 | -0.1432 | -0.036835 | 0.0019504 | 0.023364 | -0.0025549 | -0.010743 | -0.0075003 | -0.1138 | 0.022614 | 0.012794 | -0.0134 | -0.020719 | 0.029758 | -0.0040845 | -0.14191 | 0.032043 | -0.064087 | -0.10986 | -0.027466 | -0.18768 | -0.068665 | -0.09613 | 0.14648 | -0.064087 | -0.050354 | 0.022888 | -0.045776 | 0.064087 | 0.35248 | -120.4926 | -120.6345 | 0.3891 | 0.3479 | 0.22888 | -0.004578 | -0.1236 | 0.35248 | -120.3781 | -120.575 | 0.43945 | 0.48065 | 0.37079 | 0.12817 | 0.018311 | 0.036621 | -0.045776 | 0.086975 | 0.013733 | 0.09613 | 0.21057 | 0.44861 | 0.56305 | -120.5887 | -120.5887 | 0.3067 | 0.36621 | 0.27466 | 0.32044
5408.0469 | 120.9778 | -0.37994 | 120.5658 | -0.12794 | -0.038758 | 0.00024143 | 0.019305 | 0.00022207 | -0.01117 | -0.0023733 | -0.089386 | 0.022401 | 0.013862 | -0.015323 | -0.018583 | 0.026767 | -0.0021619 | -0.10071 | 0.022888 | -0.07782 | -0.022888 | 0.064087 | -0.07782 | 0.018311 | 0.022888 | 0.1236 | -0.068665 | 0.013733 | 0.11902 | 0.059509 | 0.10986 | 0.30212 | -120.5429 | -120.5887 | 0.44403 | 0.39826 | 0.30212 | 0.096131 | 0 | 0.31128 | -120.4422 | -120.5521 | 0.49896 | 0.48981 | 0.43945 | 0.17853 | 0.12817 | 0.14191 | 0.054932 | 0.18768 | 0.082398 | 0.10071 | 0.19226 | 0.40283 | 0.50354 | -120.6436 | -120.6345 | 0.35706 | 0.39368 | 0.27924 | 0.40283
5409.75 | 121.0876 | -0.36163 | 120.6116 | -0.13557 | -0.043457 | 0.00024143 | 0.01546 | -0.00020513 | -0.012452 | -0.0045095 | 0.0021667 | 0.019623 | 0.015785 | -0.01575 | -0.017515 | 0.028049 | -0.0030163 | -0.07782 | -0.009155 | -0.027466 | 0.022888 | 0.12817 | -0.009155 | 0.086975 | 0.082397 | 0.11902 | -0.050354 | 0.022888 | 0.18768 | 0.13275 | 0.14191 | 0.33417 | -120.6207 | -120.5887 | 0.48981 | 0.44861 | 0.35248 | 0.11444 | 0.018311 | 0.31128 | -120.4926 | -120.5887 | 0.54932 | 0.50354 | 0.49438 | 0.19226 | 0.18311 | 0.15564 | 0.050354 | 0.23804 | 0.073242 | 0.018311 | 0.16937 | 0.35248 | 0.48065 | -120.639 | -120.6619 | 0.38452 | 0.38452 | 0.28381 | 0.44403
5411.5156 | 121.1288 | -0.3891 | 120.6436 | -0.19661 | -0.041107 | 0.0019504 | 0.019305 | 0.0029993 | -0.010316 | -0.0040823 | -0.037506 | 0.023896 | 0.015998 | -0.011692 | -0.017515 | 0.026767 | -0.0023755 | -0.086975 | -0.022888 | -0.041199 | 0 | 0.10071 | -0.054932 | 0.054932 | 0.054932 | 0.10986 | -0.054932 | 0.027466 | 0.14191 | 0.082397 | 0.10986 | 0.3479 | -120.6665 | -120.6436 | 0.48981 | 0.44403 | 0.33417 | 0.096131 | -0.013733 | 0.33417 | -120.5338 | -120.6161 | 0.53101 | 0.49896 | 0.4715 | 0.16479 | 0.13733 | 0.14191 | 0.041199 | 0.19684 | 0.082398 | 0.018311 | 0.16479 | 0.36621 | 0.49896 | -120.6848 | -120.6985 | 0.3891 | 0.41656 | 0.30212 | 0.44403
5413.2812 | 121.2204 | -0.35706 | 120.6573 | -0.089798 | -0.041962 | 2.7834e-05 | 0.017169 | -0.0019141 | -0.010957 | -0.0055777 | -0.0069885 | 0.020478 | 0.014503 | -0.011478 | -0.019865 | 0.024844 | -0.0060071 | -0.082397 | -0.018311 | -0.050354 | 0.027466 | 0.15106 | 0.013733 | 0.11444 | 0.12817 | 0.10986 | -0.045776 | 0.07782 | 0.21057 | 0.16479 | 0.16937 | 0.3067 | -120.6757 | -120.6299 | 0.50812 | 0.4715 | 0.37079 | 0.16479 | 0.064087 | 0.31128 | -120.5475 | -120.5795 | 0.56763 | 0.52643 | 0.52185 | 0.21515 | 0.21057 | 0.20142 | 0.07782 | 0.25635 | 0.1236 | 0.032043 | 0.15564 | 0.33874 | 0.46692 | -120.7077 | -120.7031 | 0.38452 | 0.43488 | 0.27466 | 0.48523
5415 | 121.1334 | -0.40741 | 120.7443 | -0.089798 | -0.04068 | -0.00039957 | 0.020373 | 0.00043587 | -0.014802 | -0.0045095 | -0.052765 | 0.024537 | 0.015571 | -0.010196 | -0.02136 | 0.028903 | -0.0070751 | -0.12817 | 0.013733 | -0.09613 | -0.086975 | -0.013733 | -0.13275 | -0.013733 | -0.054932 | 0.14191 | -0.07782 | -0.041199 | 0.073242 | 0.013733 | 0.086975 | 0.31128 | -120.7306 | -120.8313 | 0.39368 | 0.39368 | 0.27466 | 0.082397 | -0.036621 | 0.32959 | -120.6024 | -120.7855 | 0.48065 | 0.49438 | 0.42114 | 0.16479 | 0.091553 | 0.082397 | 0.009155 | 0.15106 | 0.036621 | 0.10986 | 0.21973 | 0.42114 | 0.54932 | -120.8405 | -120.8221 | 0.32044 | 0.36621 | 0.27924 | 0.35248
5416.75 | 121.1746 | -0.39825 | 120.7123 | -0.10506 | -0.042816 | -0.001254 | 0.020587 | 0.0010767 | -0.013307 | -0.0021597 | -0.092438 | 0.023041 | 0.015357 | -0.0082737 | -0.019651 | 0.027408 | -0.0015209 | -0.13275 | 0.018311 | -0.07782 | -0.073242 | 0.004578 | -0.10071 | -0.004578 | -0.018311 | 0.15564 | -0.059509 | -0.009155 | 0.10071 | 0.045776 | 0.091553 | 0.32043 | -120.694 | -120.7855 | 0.40283 | 0.39368 | 0.29755 | 0.073242 | -0.022888 | 0.33875 | -120.5566 | -120.7214 | 0.49896 | 0.48981 | 0.44403 | 0.15106 | 0.10528 | 0.082398 | 0.004578 | 0.16022 | 0.050354 | 0.096131 | 0.21515 | 0.41657 | 0.55389 | -120.7901 | -120.7718 | 0.32501 | 0.3891 | 0.2655 | 0.37994
5418.5 | 121.2341 | -0.39825 | 120.7535 | -0.16609 | -0.040894 | 2.7834e-05 | 0.022296 | 0.00043587 | -0.011811 | -0.0015189 | -0.074127 | 0.024323 | 0.016212 | -0.012332 | -0.019865 | 0.027408 | -0.0036573 | -0.10986 | 0.027466 | -0.073242 | -0.068665 | 0.022888 | -0.12817 | -0.009155 | 0.027466 | 0.14191 | -0.054932 | 0.054932 | 0.13733 | 0.064087 | 0.13733 | 0.32501 | -120.726 | -120.8221 | 0.42114 | 0.3891 | 0.27008 | 0.064087 | -0.054932 | 0.34332 | -120.6116 | -120.6985 | 0.53558 | 0.53558 | 0.46234 | 0.19226 | 0.11902 | 0.09613 | 0.004577 | 0.19226 | 0.10986 | 0.10071 | 0.19684 | 0.42572 | 0.54016 | -120.8267 | -120.8084 | 0.32959 | 0.45319 | 0.28839 | 0.42572
5420.2812 | 121.2708 | -0.37079 | 120.7352 | -0.19661 | -0.038758 | 0.0013094 | 0.018878 | 0.0021447 | -0.010316 | -0.0070731 | -0.055817 | 0.021973 | 0.015571 | -0.017459 | -0.018797 | 0.024204 | -0.0010937 | -0.07782 | -0.013733 | -0.032043 | 0.022888 | 0.13275 | -0.032043 | 0.068665 | 0.091553 | 0.091553 | -0.036621 | 0.068665 | 0.16937 | 0.11444 | 0.15564 | 0.33875 | -120.7489 | -120.7123 | 0.50354 | 0.43945 | 0.33875 | 0.10071 | 0 | 0.33417 | -120.6436 | -120.6665 | 0.54016 | 0.52643 | 0.48523 | 0.19226 | 0.15106 | 0.16479 | 0.054931 | 0.20599 | 0.10529 | 0.01831 | 0.12817 | 0.35706 | 0.46234 | -120.7672 | -120.7718 | 0.39368 | 0.43945 | 0.29297 | 0.46234
5422.0469 | 121.225 | -0.40283 | 120.7947 | -0.13557 | -0.041107 | -0.00039957 | 0.018878 | -0.0019141 | -0.012452 | -0.0034415 | 0.0052185 | 0.021332 | 0.01493 | -0.018527 | -0.017088 | 0.02634 | -0.0051525 | -0.073242 | -0.032043 | -0.041199 | -0.022888 | 0.091553 | -0.032043 | 0.059509 | 0.022888 | 0.13733 | -0.045776 | -0.018311 | 0.09613 | 0.036621 | 0.082397 | 0.36163 | -120.8267 | -120.8176 | 0.49439 | 0.46234 | 0.37079 | 0.10071 | 0.009156 | 0.35706 | -120.6573 | -120.813 | 0.49896 | 0.48523 | 0.43945 | 0.12817 | 0.082397 | 0.13275 | 0.018311 | 0.14191 | 0.027465 | 0.009156 | 0.18311 | 0.37079 | 0.54016 | -120.8359 | -120.8405 | 0.37994 | 0.38452 | 0.32959 | 0.42572
5423.75 | 121.312 | -0.3891 | 120.7764 | -0.20424 | -0.040467 | -0.00061317 | 0.02315 | 0.0023585 | -0.010316 | -0.0064321 | -0.10464 | 0.023255 | 0.01493 | -0.0097689 | -0.022428 | 0.026767 | -0.0025891 | -0.12817 | 0.013733 | -0.073242 | -0.068665 | 0.022888 | -0.11902 | -0.004578 | 0.004578 | 0.13733 | -0.036621 | 0.045776 | 0.13275 | 0.073242 | 0.14648 | 0.31586 | -120.7626 | -120.845 | 0.41199 | 0.38452 | 0.27008 | 0.068664 | -0.045777 | 0.35248 | -120.639 | -120.7306 | 0.52185 | 0.53558 | 0.46234 | 0.18311 | 0.10986 | 0.09613 | 0.004577 | 0.16937 | 0.082397 | 0.086975 | 0.17395 | 0.40283 | 0.52643 | -120.8496 | -120.813 | 0.32043 | 0.43487 | 0.26092 | 0.39368
5425.5156 | 121.3531 | -0.37079 | 120.7855 | -0.24239 | -0.04068 | 0.00045503 | 0.02016 | -0.0021277 | -0.012239 | -0.0057913 | -0.055817 | 0.023041 | 0.016853 | -0.016178 | -0.020292 | 0.027194 | 0.00018809 | -0.050354 | -0.022888 | -0.018311 | 0.036621 | 0.13275 | -0.036621 | 0.086975 | 0.09613 | 0.10071 | -0.041199 | 0.086975 | 0.17853 | 0.11902 | 0.16937 | 0.35248 | -120.8084 | -120.7489 | 0.50354 | 0.45776 | 0.33417 | 0.10529 | -0.01831 | 0.32959 | -120.6848 | -120.6985 | 0.54932 | 0.54016 | 0.48981 | 0.21057 | 0.16022 | 0.15106 | 0.054932 | 0.21973 | 0.12817 | -0.004577 | 0.14191 | 0.3479 | 0.4715 | -120.8038 | -120.8267 | 0.40741 | 0.45776 | 0.32043 | 0.46692
5427.2812 | 121.2479 | -0.4303 | 120.8405 | -0.21187 | -0.042176 | -0.0023222 | 0.018023 | -0.0044775 | -0.013093 | -0.0055777 | -0.031403 | 0.023041 | 0.014717 | -0.015323 | -0.019438 | 0.025272 | -0.0047253 | -0.13733 | 0.027466 | -0.07782 | -0.091553 | 0.022888 | -0.10529 | 0 | -0.045776 | 0.13733 | -0.082397 | -0.050354 | 0.073242 | 0.013733 | 0.050354 | 0.35248 | -120.813 | -120.932 | 0.45319 | 0.4303 | 0.32501 | 0.07782 | -0.027466 | 0.3479 | -120.7031 | -120.8908 | 0.50354 | 0.48065 | 0.44403 | 0.13275 | 0.09613 | 0.10071 | -0.013733 | 0.15564 | 0.032043 | 0.10529 | 0.21973 | 0.45776 | 0.56763 | -120.9183 | -120.9229 | 0.33875 | 0.37994 | 0.29297 | 0.38452
5429.0312 | 121.3028 | -0.42114 | 120.8633 | -0.12794 | -0.04068 | -0.0023222 | 0.0208 | 0.0012903 | -0.013307 | -0.0049367 | -0.098541 | 0.024964 | 0.016639 | -0.0074191 | -0.018583 | 0.026767 | -0.0028027 | -0.10529 | 0.027466 | -0.068665 | -0.054932 | 0.022888 | -0.091553 | 0.009155 | -0.004578 | 0.14648 | -0.059509 | 0.004578 | 0.10529 | 0.032043 | 0.10529 | 0.35248 | -120.8359 | -120.9183 | 0.44403 | 0.4303 | 0.32959 | 0.07782 | -0.022888 | 0.36163 | -120.7169 | -120.8588 | 0.52643 | 0.52643 | 0.45319 | 0.16479 | 0.091552 | 0.091553 | 0.013733 | 0.16479 | 0.064087 | 0.096131 | 0.20599 | 0.44861 | 0.56763 | -120.932 | -120.9229 | 0.36621 | 0.42572 | 0.31586 | 0.41656
5430.7344 | 121.3348 | -0.4303 | 120.8817 | -0.11269 | -0.042389 | 0.00066863 | 0.021228 | -0.00041873 | -0.012025 | -0.0051505 | -0.077179 | 0.022828 | 0.015571 | -0.0134 | -0.019865 | 0.026126 | -0.010066 | -0.12817 | 0.018311 | -0.086975 | -0.082397 | -0.009155 | -0.09613 | -0.022888 | -0.036621 | 0.15106 | -0.073242 | -0.022888 | 0.086975 | 0.018311 | 0.09613 | 0.34332 | -120.8633 | -120.9641 | 0.42114 | 0.40741 | 0.33417 | 0.064087 | -0.009155 | 0.35706 | -120.7306 | -120.9045 | 0.51727 | 0.52643 | 0.44861 | 0.16937 | 0.091553 | 0.07782 | 0.004578 | 0.16022 | 0.050354 | 0.10529 | 0.2243 | 0.44861 | 0.58136 | -120.9686 | -120.9549 | 0.3479 | 0.40741 | 0.30212 | 0.39368
5432.4844 | 121.344 | -0.42572 | 120.8908 | -0.12794 | -0.040467 | 0.0013094 | 0.019946 | -0.00020513 | -0.01117 | -0.0075003 | -0.064972 | 0.023255 | 0.01728 | -0.011905 | -0.01666 | 0.026767 | -0.0049389 | -0.11444 | 0.022888 | -0.07782 | -0.073242 | 0.018311 | -0.10071 | 0.004578 | -0.013733 | 0.15106 | -0.054932 | -0.004578 | 0.10529 | 0.041199 | 0.09613 | 0.3479 | -120.8679 | -120.9641 | 0.44403 | 0.4303 | 0.32501 | 0.082398 | -0.022888 | 0.37079 | -120.7397 | -120.8954 | 0.53101 | 0.52185 | 0.46692 | 0.15106 | 0.096131 | 0.096131 | 0.004578 | 0.16022 | 0.050354 | 0.10071 | 0.20599 | 0.44861 | 0.57678 | -120.9686 | -120.9457 | 0.35248 | 0.42114 | 0.31128 | 0.41199
5434.1875 | 121.4035 | -0.39825 | 120.8862 | -0.18898 | -0.042603 | 0.00088223 | 0.019732 | -0.0038367 | -0.011811 | -0.0040823 | -0.013092 | 0.023255 | 0.015785 | -0.016391 | -0.018156 | 0.026553 | -0.0025891 | -0.10529 | -0.027466 | -0.036621 | -0.018311 | 0.09613 | -0.059509 | 0.041199 | 0.022888 | 0.11444 | -0.050354 | 0.013733 | 0.12817 | 0.07782 | 0.11902 | 0.36163 | -120.9137 | -120.9045 | 0.49438 | 0.43945 | 0.33875 | 0.07782 | -0.022888 | 0.3479 | -120.7718 | -120.8725 | 0.52643 | 0.51727 | 0.47607 | 0.16937 | 0.12817 | 0.13275 | 0.01831 | 0.17853 | 0.064087 | 0.009155 | 0.16479 | 0.37079 | 0.5127 | -120.9229 | -120.9366 | 0.37994 | 0.41199 | 0.29297 | 0.42114
5435.9531 | 121.4035 | -0.44403 | 120.8633 | -0.15083 | -0.039612 | 2.7834e-05 | 0.021441 | -0.0017005 | -0.0092478 | -0.0057913 | -0.098541 | 0.025819 | 0.013221 | -0.0097689 | -0.021574 | 0.025912 | -0.0036573 | -0.14191 | 0.018311 | -0.068665 | -0.086975 | 0.004578 | -0.14648 | -0.036621 | -0.013733 | 0.12817 | -0.045776 | 0.013733 | 0.086975 | 0.050354 | 0.1236 | 0.37537 | -120.845 | -120.9503 | 0.44861 | 0.40741 | 0.29755 | 0.032044 | -0.077819 | 0.39826 | -120.7352 | -120.8496 | 0.53101 | 0.56763 | 0.49439 | 0.16937 | 0.09613 | 0.073243 | -0.01831 | 0.13275 | 0.059509 | 0.086976 | 0.17395 | 0.46234 | 0.57221 | -120.932 | -120.9091 | 0.35706 | 0.45776 | 0.30212 | 0.4303
5437.7188 | 121.3852 | -0.44403 | 120.9366 | -0.15083 | -0.042816 | 0.0017368 | 0.01781 | -0.0044775 | -0.011811 | -0.0055777 | -0.025299 | 0.020905 | 0.013862 | -0.014255 | -0.017301 | 0.023563 | -0.0055799 | -0.086975 | -0.013733 | -0.032043 | -0.018311 | 0.10529 | -0.027466 | 0.064087 | 0.032043 | 0.13733 | -0.036621 | -0.018311 | 0.09613 | 0.050354 | 0.091553 | 0.41199 | -120.9503 | -120.9549 | 0.54932 | 0.50812 | 0.41657 | 0.09613 | 0.004577 | 0.40741 | -120.7993 | -120.9549 | 0.54016 | 0.53558 | 0.49439 | 0.12817 | 0.086975 | 0.13733 | 0.013732 | 0.13275 | 0.01831 | 0.01831 | 0.17395 | 0.4303 | 0.58136 | -120.9686 | -120.9732 | 0.42572 | 0.42572 | 0.35706 | 0.47607
5439.4062 | 121.4172 | -0.43945 | 120.9412 | -0.13557 | -0.040253 | 0.0010958 | 0.022937 | -0.00020513 | -0.012025 | -0.0057913 | -0.09549 | 0.026459 | 0.015571 | -0.0072055 | -0.021147 | 0.026126 | -0.0036573 | -0.091553 | 0.022888 | -0.07782 | -0.018311 | 0.064087 | -0.082397 | 0.022888 | 0.022888 | 0.12817 | -0.054932 | 0.018311 | 0.11444 | 0.054932 | 0.10986 | 0.36163 | -120.9183 | -120.9595 | 0.50354 | 0.46234 | 0.35706 | 0.10071 | -0.004577 | 0.38452 | -120.813 | -120.9229 | 0.55389 | 0.54932 | 0.49438 | 0.16479 | 0.10986 | 0.14191 | 0.059509 | 0.16937 | 0.073243 | 0.10071 | 0.18311 | 0.46234 | 0.56763 | -121.019 | -120.9961 | 0.42114 | 0.45776 | 0.3479 | 0.46234
5441.1719 | 121.4539 | -0.41199 | 120.9457 | -0.22713 | -0.040894 | 0.0013094 | 0.019519 | -0.00084593 | -0.012666 | -0.0060049 | -0.031403 | 0.02411 | 0.013648 | -0.020664 | -0.019438 | 0.025272 | 0.0012561 | -0.082397 | -0.018311 | -0.027466 | -0.004578 | 0.12817 | -0.059509 | 0.054932 | 0.068665 | 0.091553 | -0.027466 | 0.045776 | 0.14648 | 0.086975 | 0.12817 | 0.38452 | -120.9641 | -120.9503 | 0.54016 | 0.46692 | 0.35248 | 0.082398 | -0.032043 | 0.38452 | -120.8542 | -120.9 | 0.55847 | 0.54016 | 0.49896 | 0.15564 | 0.11444 | 0.15564 | 0.022888 | 0.17395 | 0.073242 | 0.009155 | 0.11902 | 0.39368 | 0.50354 | -120.9732 | -120.9732 | 0.40741 | 0.45776 | 0.32959 | 0.48065
5442.9375 | 121.3989 | -0.44861 | 120.9686 | -0.12794 | -0.039826 | -0.0010404 | 0.022296 | 0.00022207 | -0.010957 | -0.0053641 | -0.089386 | 0.024537 | 0.017921 | -0.013187 | -0.019651 | 0.02634 | -0.0025891 | -0.12817 | 0.022888 | -0.073242 | -0.10071 | -0.041199 | -0.17395 | -0.036621 | -0.059509 | 0.14648 | -0.068665 | -0.045776 | 0.036621 | -0.032043 | 0.064087 | 0.37537 | -120.9457 | -121.0693 | 0.40741 | 0.41199 | 0.27466 | 0.036621 | -0.10071 | 0.37994 | -120.8221 | -121.0144 | 0.48523 | 0.5127 | 0.41657 | 0.13275 | 0.036622 | 0.032043 | -0.027466 | 0.10529 | 0.022889 | 0.09613 | 0.21515 | 0.4715 | 0.59509 | -121.0419 | -121.0373 | 0.3479 | 0.40283 | 0.32043 | 0.3891
5444.7188 | 121.4264 | -0.45776 | 120.9732 | -0.17372 | -0.038971 | 0.00088223 | 0.021441 | 0.0044947 | -0.0090342 | -0.0070731 | -0.083283 | 0.023896 | 0.017494 | -0.01041 | -0.019224 | 0.025272 | 0.00082889 | -0.13275 | 0.036621 | -0.086975 | -0.10986 | -0.027466 | -0.16479 | -0.041199 | -0.054932 | 0.14191 | -0.059509 | -0.022888 | 0.032043 | -0.018311 | 0.068665 | 0.37079 | -120.9366 | -121.0831 | 0.4303 | 0.41657 | 0.29297 | 0.045776 | -0.07782 | 0.39826 | -120.8313 | -120.9961 | 0.48981 | 0.52643 | 0.43945 | 0.12817 | 0.041198 | 0.059509 | -0.022888 | 0.091552 | 0.036621 | 0.1236 | 0.20142 | 0.49439 | 0.59967 | -121.0602 | -121.0327 | 0.3479 | 0.43488 | 0.32501 | 0.40283
5446.4844 | 121.5546 | -0.40283 | 120.9549 | -0.23476 | -0.039185 | 0.00088223 | 0.019732 | -0.0014867 | -0.010743 | -0.0030141 | -0.046661 | 0.023469 | 0.015785 | -0.014469 | -0.017301 | 0.025699 | -0.0064343 | -0.054932 | 0 | -0.059509 | 0.018311 | 0.11444 | -0.036621 | 0.059509 | 0.091553 | 0.09613 | -0.032043 | 0.09613 | 0.17395 | 0.10529 | 0.1831 | 0.34332 | -120.9549 | -120.9366 | 0.51727 | 0.46234 | 0.36621 | 0.11902 | 0.022888 | 0.37079 | -120.8588 | -120.8588 | 0.57678 | 0.58594 | 0.50812 | 0.21515 | 0.13733 | 0.17395 | 0.07782 | 0.20599 | 0.12817 | 0.059509 | 0.12817 | 0.40283 | 0.49896 | -121.0144 | -120.9869 | 0.42114 | 0.49896 | 0.3479 | 0.49439
5448.1875 | 120.5429 | -119.2291 | 0.86517 | -0.23476 | -0.041107 | 0.004941 | 0.020373 | 8.47e-06 | -0.01352 | -0.0032277 | -0.052765 | 0.023255 | 0.015144 | -0.016605 | -0.019438 | 0.027408 | -0.0055799 | -0.13275 | 0.004578 | -0.050354 | -0.004578 | 0.086975 | -0.059509 | 0.041199 | 0.082397 | 0.10986 | -0.022888 | 0.07782 | 0.16022 | 0.11444 | 0.17853 | 119.1788 | -0.86059 | -0.86975 | 119.3161 | 119.2703 | 119.1696 | 0.091553 | -0.009155 | 119.2062 | -0.75531 | -0.78735 | 119.3893 | 119.4077 | 119.3436 | 0.20142 | 0.13733 | 0.13733 | 0.045776 | 0.1831 | 0.10071 | 0.054932 | 0.13275 | 119.2337 | 119.339 | -0.91553 | -0.88806 | 119.2245 | 119.3069 | 119.0964 | 119.3115
5449.8906 | 121.0876 | -120.1447 | 0.72784 | -0.15083 | -0.040467 | 0.0013094 | 0.022509 | 0.0036401 | -0.013734 | -0.0038687 | -0.055817 | 0.024323 | 0.014717 | -0.014041 | -0.019224 | 0.025699 | -0.0017347 | -0.13275 | 0.027466 | -0.091553 | -0.11444 | -0.004578 | -0.15564 | -0.027466 | -0.054932 | 0.15106 | -0.07782 | -0.018311 | 0.032043 | -0.013733 | 0.07782 | 120.0531 | -0.70038 | -0.84229 | 120.1401 | 120.1172 | 119.989 | 0.064087 | -0.064087 | 120.0668 | -0.57678 | -0.74616 | 120.1767 | 120.2225 | 120.1309 | 0.15564 | 0.064087 | 0.086975 | -0.022888 | 0.10986 | 0.059509 | 0.11902 | 0.22888 | 120.1721 | 120.2957 | -0.8194 | -0.80566 | 120.0302 | 120.1263 | 120.0119 | 120.0897
5451.6406 | 121.1792 | -120.369 | 0.6546 | -0.13557 | -0.042389 | -0.00018577 | 0.018878 | 0.00086307 | -0.013734 | -0.0028005 | -0.022247 | 0.020478 | 0.015144 | -0.013828 | -0.017729 | 0.026767 | -2.571e-05 | -0.10986 | 0.004578 | -0.041199 | -0.064087 | 0.059509 | -0.073242 | 0.036621 | -0.022888 | 0.13733 | -0.041199 | -0.018311 | 0.059509 | 0.022888 | 0.059509 | 120.3278 | -0.65002 | -0.71869 | 120.4285 | 120.4056 | 120.2957 | 0.07782 | -0.032043 | 120.3278 | -0.51727 | -0.67291 | 120.4285 | 120.4285 | 120.3918 | 0.10071 | 0.064087 | 0.10071 | -0.022888 | 0.10071 | 0.022888 | 0.045777 | 0.17853 | 120.3735 | 120.5063 | -0.6958 | -0.6958 | 120.3049 | 120.3506 | 120.2591 | 120.3461
5453.4062 | 121.3577 | -120.4102 | 0.6134 | -0.22713 | -0.036835 | 0.00066863 | 0.019519 | -0.0014867 | -0.012452 | -0.0049367 | -0.025299 | 0.02176 | 0.01493 | -0.010196 | -0.020506 | 0.027835 | -0.0083569 | -0.054932 | -0.013733 | -0.032043 | 0.032043 | 0.14191 | -0.032043 | 0.068665 | 0.12817 | 0.082397 | -0.018311 | 0.10071 | 0.16479 | 0.11444 | 0.16937 | 120.3781 | -0.62714 | -0.58136 | 120.5521 | 120.4788 | 120.3781 | 0.10071 | 0 | 120.3918 | -0.53101 | -0.5127 | 120.575 | 120.5795 | 120.5246 | 0.18768 | 0.13275 | 0.17395 | 0.064086 | 0.18311 | 0.11902 | 0.01831 | 0.10071 | 120.3964 | 120.4926 | -0.64545 | -0.63171 | 120.4422 | 120.5109 | 120.3552 | 120.5383
5455.1875 | 121.3806 | -120.1218 | 0.9613 | -0.18135 | -0.042816 | 2.7834e-05 | 0.020373 | -0.0019141 | -0.011811 | -0.0062185 | 0.023529 | 0.022187 | 0.012153 | -0.01575 | -0.019865 | 0.025272 | -0.0032299 | -0.11902 | 0 | -0.054932 | -0.032043 | 0.082397 | -0.054932 | 0.073242 | 0.036621 | 0.12817 | -0.036621 | 0.07782 | 0.15106 | 0.11444 | 0.15106 | 120.0668 | -0.9613 | -0.99335 | 120.2042 | 120.195 | 120.0668 | 0.12817 | 0 | 120.0851 | -0.83313 | -0.88348 | 120.2728 | 120.2728 | 120.2362 | 0.18768 | 0.15106 | 0.13733 | 0.022889 | 0.18768 | 0.11444 | 0.054932 | 0.1648 | 120.1218 | 120.2499 | -1.0162 | -0.99793 | 120.0897 | 120.1996 | 120.0027 | 120.1584
5456.8906 | 121.2982 | -120.1035 | 1.0574 | -0.13557 | -0.038544 | 0.00024143 | 0.024005 | 0.0025721 | -0.013947 | -0.0021597 | -0.074127 | 0.023682 | 0.013221 | -0.010196 | -0.01901 | 0.027408 | -0.0023755 | -0.14191 | 0.027466 | -0.068665 | -0.11902 | -0.032043 | -0.16022 | -0.041199 | -0.064087 | 0.15564 | -0.064087 | -0.004578 | 0.027466 | -0.022888 | 0.073242 | 120.0348 | -1.03 | -1.1765 | 120.0714 | 120.0623 | 119.9432 | 0.027466 | -0.091552 | 120.0394 | -0.90179 | -1.062 | 120.1309 | 120.1767 | 120.0806 | 0.13733 | 0.041199 | 0.036622 | -0.050354 | 0.091553 | 0.059509 | 0.096131 | 0.21973 | 120.1309 | 120.2591 | -1.1261 | -1.1215 | 119.9844 | 120.0989 | 119.9615 | 120.0394
5458.6406 | 121.4447 | -120.4834 | 0.66834 | -0.19661 | -0.04068 | 0.00024143 | 0.021869 | 0.00043587 | -0.010316 | -0.0028005 | -0.040558 | 0.023469 | 0.014289 | -0.0069919 | -0.019651 | 0.028903 | -0.0021619 | -0.086975 | 0.004578 | -0.045776 | -0.009155 | 0.09613 | -0.050354 | 0.059509 | 0.086975 | 0.11444 | -0.041199 | 0.11444 | 0.15106 | 0.091553 | 0.17395 | 120.4376 | -0.66376 | -0.67749 | 120.5795 | 120.5429 | 120.433 | 0.10528 | -0.004578 | 120.4422 | -0.55389 | -0.55389 | 120.6345 | 120.6573 | 120.575 | 0.21515 | 0.13275 | 0.14191 | 0.036621 | 0.19226 | 0.15564 | 0.050354 | 0.15564 | 120.488 | 120.5978 | -0.71411 | -0.70953 | 120.4742 | 120.5978 | 120.3964 | 120.5704
5460.3438 | 121.3852 | -120.5658 | 0.69122 | -0.15846 | -0.040894 | 0.00066863 | 0.018878 | 0.0012903 | -0.014161 | -0.0064321 | 0.011322 | 0.022401 | 0.014717 | -0.0076327 | -0.016233 | 0.02399 | -0.0055799 | -0.073242 | 0 | -0.036621 | -0.013733 | 0.10529 | -0.022888 | 0.054932 | 0.027466 | 0.13275 | -0.045776 | 0.013733 | 0.10986 | 0.045776 | 0.07782 | 120.5292 | -0.69122 | -0.70496 | 120.6711 | 120.6207 | 120.5429 | 0.091553 | 0.013733 | 120.52 | -0.55847 | -0.67749 | 120.6757 | 120.6436 | 120.6116 | 0.1236 | 0.091552 | 0.14191 | 0.022888 | 0.15564 | 0.059509 | 0.036621 | 0.17853 | 120.5658 | 120.6985 | -0.72784 | -0.737 | 120.5521 | 120.5795 | 120.4926 | 120.5933
5462.125 | 121.4676 | -120.5429 | 0.66376 | -0.13557 | -0.041321 | 2.7834e-05 | 0.019732 | 0.0015039 | -0.012025 | -0.0062185 | 0.014374 | 0.021332 | 0.013862 | -0.0074191 | -0.019651 | 0.028476 | -0.0023755 | -0.12817 | -0.013733 | -0.050354 | -0.036621 | 0.054932 | -0.059509 | 0.041199 | 0.027466 | 0.11444 | -0.045776 | 0.045776 | 0.14191 | 0.10071 | 0.1236 | 120.4926 | -0.67749 | -0.70038 | 120.5978 | 120.5841 | 120.4834 | 0.091553 | -0.009155 | 120.4971 | -0.54932 | -0.61798 | 120.6848 | 120.6665 | 120.6436 | 0.16937 | 0.14648 | 0.10529 | 0.013733 | 0.18768 | 0.091552 | 0.036621 | 0.16022 | 120.5292 | 120.6573 | -0.71411 | -0.70953 | 120.5063 | 120.5887 | 120.4147 | 120.5704
5463.8281 | 121.4081 | -120.5338 | 0.737 | -0.19661 | -0.038971 | 0.0025912 | 0.021441 | 0.0010767 | -0.013093 | -0.0040823 | -0.1138 | 0.023041 | 0.014717 | -0.0091281 | -0.019865 | 0.026767 | -0.0053661 | -0.086975 | 0.036621 | -0.050354 | -0.073242 | 0.041199 | -0.10986 | 0.004578 | -0.004578 | 0.14648 | -0.045776 | 0.004578 | 0.045776 | -0.022888 | 0.064087 | 120.4834 | -0.70038 | -0.81024 | 120.575 | 120.5383 | 120.4239 | 0.054932 | -0.059509 | 120.488 | -0.59052 | -0.73242 | 120.5795 | 120.5978 | 120.5109 | 0.10986 | 0.022888 | 0.091553 | -0.022888 | 0.091552 | 0.050354 | 0.086975 | 0.19226 | 120.5704 | 120.6802 | -0.78735 | -0.78278 | 120.4605 | 120.5383 | 120.4468 | 120.5292
5465.5938 | 121.5271 | -120.6116 | 0.61798 | -0.19661 | -0.040894 | 2.7834e-05 | 0.0208 | 0.0010767 | -0.0092478 | -0.0055777 | -0.055817 | 0.023041 | 0.014076 | -0.014682 | -0.018369 | 0.025699 | -0.0032299 | -0.045776 | -0.027466 | -0.032043 | 0.032043 | 0.13275 | -0.036621 | 0.073242 | 0.10529 | 0.10529 | -0.032043 | 0.10071 | 0.17395 | 0.11902 | 0.16022 | 120.5795 | -0.64545 | -0.58594 | 120.7443 | 120.6848 | 120.575 | 0.10529 | -0.004578 | 120.5795 | -0.5127 | -0.51727 | 120.7855 | 120.7718 | 120.7306 | 0.19226 | 0.15106 | 0.16479 | 0.064086 | 0.20599 | 0.13275 | 0.004577 | 0.13733 | 120.5841 | 120.7169 | -0.65002 | -0.65002 | 120.6436 | 120.7123 | 120.5658 | 120.7169
5467.2969 | 121.4722 | -120.6345 | 0.65002 | -0.12794 | -0.041748 | 0.00045503 | 0.019091 | -0.0034095 | -0.012666 | -0.0030141 | -0.025299 | 0.021119 | 0.014289 | -0.015964 | -0.018797 | 0.025058 | -0.0032299 | -0.073242 | 0.004578 | -0.041199 | -0.004578 | 0.10071 | -0.013733 | 0.073242 | 0.050354 | 0.11902 | -0.050354 | 0.022888 | 0.11444 | 0.059509 | 0.10529 | 120.5933 | -0.64545 | -0.6546 | 120.7352 | 120.7077 | 120.6207 | 0.11444 | 0.027466 | 120.5841 | -0.53101 | -0.62714 | 120.7489 | 120.7397 | 120.694 | 0.15564 | 0.10986 | 0.14191 | 0.036621 | 0.16479 | 0.073242 | 0.045777 | 0.16937 | 120.639 | 120.7535 | -0.69122 | -0.70038 | 120.6299 | 120.6573 | 120.5612 | 120.6848
5469.0625 | 120.9915 | -102.8915 | 17.5964 | -0.24239 | -0.040894 | 0.001523 | 0.021014 | 0.0012903 | -0.011384 | -0.0047231 | -0.037506 | 0.022828 | 0.014717 | -0.018955 | -0.020078 | 0.024204 | 0.00040169 | -0.059509 | -0.013733 | -0.022888 | 0.013733 | 0.14191 | -0.027466 | 0.073242 | 0.10071 | 0.10071 | -0.027466 | 0.082397 | 0.15564 | 0.09613 | 0.16479 | 102.8687 | -17.6102 | -17.5827 | 103.0334 | 102.9648 | 102.8641 | 0.09613 | -0.004578 | 102.8641 | -17.4957 | -17.514 | 103.0472 | 103.0563 | 102.9877 | 0.19226 | 0.1236 | 0.16479 | 0.036621 | 0.18311 | 0.10986 | 0.009155 | 0.12817 | 102.8778 | 102.9922 | -17.6193 | -17.6239 | 102.9053 | 102.9739 | 102.832 | 102.9922
5470.8281 | 121.2891 | -105.1987 | 15.7516 | -0.15846 | -0.040039 | 0.00066863 | 0.021228 | 0.0034265 | -0.0083932 | -0.0066457 | -0.1077 | 0.024964 | 0.011726 | -0.0072055 | -0.018797 | 0.026981 | -0.0028027 | -0.082397 | -0.009155 | -0.073242 | -0.045776 | 0.045776 | -0.10071 | 0 | 0.013733 | 0.13733 | -0.041199 | 0.027466 | 0.07782 | 0.013733 | 0.082397 | 105.1254 | -15.7608 | -15.7974 | 105.2444 | 105.1987 | 105.098 | 0.073242 | -0.027466 | 105.1575 | -15.6143 | -15.7242 | 105.2765 | 105.2811 | 105.2124 | 0.1236 | 0.054932 | 0.11902 | 0.027466 | 0.11902 | 0.068665 | 0.064087 | 0.17853 | 105.1895 | 105.336 | -15.8249 | -15.7928 | 105.1529 | 105.2261 | 105.1163 | 105.2124
5472.5938 | 121.3943 | -104.6906 | 16.3239 | -0.1432 | -0.043671 | -0.0016812 | 0.017596 | 0.0017175 | -0.012879 | -0.0021597 | 0.020477 | 0.02176 | 0.011512 | -0.01276 | -0.016874 | 0.026767 | 0.00061529 | -0.11902 | -0.004578 | -0.032043 | -0.036621 | 0.059509 | -0.082397 | 0.036621 | 0.004578 | 0.10986 | -0.045776 | 0.032043 | 0.1236 | 0.073242 | 0.11902 | 104.6585 | -16.3284 | -16.3605 | 104.7501 | 104.7272 | 104.6082 | 0.068664 | -0.050354 | 104.6448 | -16.214 | -16.2918 | 104.8141 | 104.8096 | 104.7638 | 0.16479 | 0.11902 | 0.091552 | -0.004578 | 0.16937 | 0.077819 | 0.027465 | 0.15564 | 104.686 | 104.8004 | -16.3559 | -16.3696 | 104.6539 | 104.7226 | 104.5715 | 104.6951
5474.3594 | 121.4813 | -104.1275 | 16.9373 | -0.18898 | -0.043671 | 2.7834e-05 | 0.02016 | 0.0029993 | -0.013093 | -0.0068593 | 0.0021667 | 0.023255 | 0.014289 | -0.011264 | -0.018797 | 0.026767 | -0.0042981 | -0.10071 | -0.004578 | -0.045776 | -0.009155 | 0.09613 | -0.036621 | 0.073242 | 0.054932 | 0.10986 | -0.045776 | 0.073242 | 0.18768 | 0.11902 | 0.17395 | 104.0817 | -16.9418 | -16.9464 | 104.2236 | 104.2007 | 104.0909 | 0.11902 | 0.009155 | 104.0817 | -16.8274 | -16.864 | 104.3152 | 104.3015 | 104.2465 | 0.21973 | 0.16479 | 0.14191 | 0.036621 | 0.23346 | 0.11902 | 0.041198 | 0.15564 | 104.1229 | 104.2374 | -16.983 | -16.983 | 104.1183 | 104.2007 | 104.0268 | 104.1824
5476.125 | 121.4035 | -104.6173 | 16.571 | -0.11269 | -0.040467 | -0.0014676 | 0.021014 | 0.0049219 | -0.014375 | -0.0047231 | -0.080231 | 0.024323 | 0.014289 | -0.0029331 | -0.01901 | 0.025912 | -0.0040845 | -0.15564 | 0.022888 | -0.082397 | -0.10071 | -0.009155 | -0.12817 | -0.018311 | -0.054932 | 0.16022 | -0.064087 | -0.013733 | 0.07782 | 0.013733 | 0.073242 | 104.5349 | -16.5482 | -16.6718 | 104.6082 | 104.599 | 104.4891 | 0.064086 | -0.045777 | 104.5532 | -16.4108 | -16.5848 | 104.6951 | 104.6906 | 104.631 | 0.13733 | 0.07782 | 0.073242 | -0.018311 | 0.14191 | 0.050354 | 0.10528 | 0.2243 | 104.6402 | 104.7775 | -16.6534 | -16.6351 | 104.5166 | 104.6036 | 104.4617 | 104.5624
5477.8438 | 121.5225 | -105.0659 | 16.0629 | -0.16609 | -0.043885 | 0.00088223 | 0.016955 | -0.0023413 | -0.013307 | -2.3544e-05 | -0.016144 | 0.022828 | 0.013648 | -0.0087009 | -0.018797 | 0.025912 | -0.0070751 | -0.068665 | -0.018311 | -0.036621 | 0.036621 | 0.14648 | 0.009155 | 0.09613 | 0.091553 | 0.10529 | -0.032043 | 0.082397 | 0.1831 | 0.13275 | 0.15106 | 105.0293 | -16.0812 | -16.0263 | 105.2124 | 105.162 | 105.0751 | 0.13275 | 0.045776 | 105.0339 | -15.9576 | -15.9805 | 105.249 | 105.217 | 105.1987 | 0.18311 | 0.16479 | 0.18311 | 0.073242 | 0.21515 | 0.11444 | 0.01831 | 0.13733 | 105.0476 | 105.1712 | -16.0995 | -16.095 | 105.1025 | 105.1483 | 104.9973 | 105.1575
5479.6094 | 121.5637 | -105.5923 | 15.6006 | -0.18135 | -0.043244 | -0.0010404 | 0.018237 | -0.0014867 | -0.010743 | -0.0025869 | -0.013092 | 0.021332 | 0.015144 | -0.014041 | -0.019438 | 0.02634 | -0.0023755 | -0.10071 | 0.004578 | -0.050354 | -0.009155 | 0.10529 | -0.018311 | 0.086975 | 0.086975 | 0.10986 | -0.032043 | 0.082397 | 0.18768 | 0.13733 | 0.16022 | 105.542 | -15.596 | -15.6097 | 105.6976 | 105.6793 | 105.574 | 0.13733 | 0.032043 | 105.5603 | -15.4907 | -15.5182 | 105.78 | 105.7526 | 105.7297 | 0.19226 | 0.16937 | 0.15564 | 0.041199 | 0.21973 | 0.11444 | 0.054932 | 0.14191 | 105.5969 | 105.7022 | -15.6509 | -15.6326 | 105.5832 | 105.6747 | 105.4916 | 105.6793
5481.375 | 121.463 | -104.9561 | 16.3055 | -0.12794 | -0.040467 | -0.0023222 | 0.018451 | 8.47e-06 | -0.014161 | -0.0051505 | -0.049713 | 0.023041 | 0.013008 | -0.014041 | -0.018583 | 0.027194 | -0.0045117 | -0.064087 | 0.009155 | -0.045776 | -0.018311 | 0.068665 | -0.041199 | 0.054932 | 0.027466 | 0.12817 | -0.045776 | -0.009155 | 0.07782 | 0.036621 | 0.07782 | 104.9103 | -16.2964 | -16.3239 | 105.0247 | 105.011 | 104.9149 | 0.10071 | 0.004577 | 104.9103 | -16.1774 | -16.3147 | 105.0339 | 105.0339 | 104.9927 | 0.1236 | 0.082397 | 0.11444 | 0.027465 | 0.1236 | 0.036621 | 0.054931 | 0.17395 | 104.9652 | 105.0842 | -16.3513 | -16.3513 | 104.9377 | 104.9469 | 104.892 | 104.9835
5483.1562 | 121.582 | -104.1 | 17.1249 | -0.1432 | -0.042816 | -0.0014676 | 0.019305 | -0.00063233 | -0.01352 | -0.0077139 | -0.040558 | 0.021119 | 0.012367 | -0.015537 | -0.020078 | 0.026553 | -0.0057935 | -0.073242 | 0.004578 | -0.041199 | 0.032043 | 0.15106 | 0.013733 | 0.10071 | 0.11902 | 0.11902 | -0.032043 | 0.09613 | 0.21057 | 0.13733 | 0.16022 | 104.0588 | -17.1204 | -17.0929 | 104.2511 | 104.2007 | 104.1138 | 0.14191 | 0.054932 | 104.068 | -17.0059 | -17.0288 | 104.3106 | 104.2603 | 104.2374 | 0.19226 | 0.16937 | 0.19226 | 0.073242 | 0.24261 | 0.12817 | 0.045777 | 0.15106 | 104.1046 | 104.2191 | -17.1661 | -17.157 | 104.1321 | 104.1962 | 104.0268 | 104.2191
5484.8594 | 121.55 | -102.626 | 18.5852 | -0.19661 | -0.040467 | 0.0017368 | 0.021014 | -0.0014867 | -0.012239 | -0.0038687 | -0.06192 | 0.021119 | 0.014076 | -0.01575 | -0.021787 | 0.025485 | -0.0036573 | -0.059509 | -0.022888 | -0.022888 | 0.027466 | 0.1236 | -0.041199 | 0.07782 | 0.086975 | 0.11444 | -0.022888 | 0.059509 | 0.14648 | 0.091553 | 0.12817 | 102.6031 | -18.6081 | -18.5577 | 102.7496 | 102.7039 | 102.5848 | 0.10071 | -0.018311 | 102.6031 | -18.4708 | -18.5257 | 102.7725 | 102.7542 | 102.7176 | 0.15106 | 0.11444 | 0.14648 | 0.050354 | 0.16937 | 0.082397 | 0 | 0.13733 | 102.6031 | 102.7405 | -18.6081 | -18.6081 | 102.6535 | 102.6855 | 102.5665 | 102.713
5486.625 | 121.2021 | -16.9327 | 104.5166 | -0.15846 | -0.041748 | -0.0038174 | 0.019305 | -0.0055457 | -0.013307 | -0.0023733 | -0.06192 | 0.02176 | 0.014076 | -0.012119 | -0.02136 | 0.026126 | -0.0028027 | -0.054932 | -0.018311 | -0.045776 | -0.027466 | 0.073242 | -0.054932 | 0.041199 | -0.009155 | 0.14191 | -0.059509 | -0.018311 | 0.07782 | 0.018311 | 0.068665 | 16.8869 | -104.5349 | -104.5441 | 17.0059 | 16.9739 | 16.8777 | 0.086975 | -0.009156 | 16.8732 | -104.3747 | -104.5349 | 17.0105 | 17.0013 | 16.951 | 0.12817 | 0.07782 | 0.11902 | 0.01831 | 0.13733 | 0.041198 | 0.027465 | 0.20142 | 16.9144 | 17.0746 | -104.5624 | -104.5761 | 16.9052 | 16.9144 | 16.8777 | 16.9235
5488.3906 | 120.9183 | -10.6064 | 110.8383 | -0.17372 | -0.039185 | 2.7834e-05 | 0.02315 | -0.0017005 | -0.010743 | -0.0092093 | -0.16568 | 0.023255 | 0.01728 | -0.0046421 | -0.020292 | 0.028476 | -0.0042981 | -0.07782 | 0.018311 | -0.064087 | -0.036621 | 0.050354 | -0.10986 | 0.013733 | 0.018311 | 0.13733 | -0.07782 | -0.004578 | 0.09613 | 0.004578 | 0.086975 | 10.5423 | -110.82 | -110.8749 | 10.6567 | 10.6201 | 10.4965 | 0.07782 | -0.045776 | 10.5286 | -110.701 | -110.8429 | 10.7025 | 10.6934 | 10.611 | 0.16479 | 0.082398 | 0.11444 | 0.027466 | 0.17395 | 0.073242 | 0.082398 | 0.21515 | 10.6247 | 10.7437 | -110.9024 | -110.9161 | 10.5698 | 10.6018 | 10.5286 | 10.6247
5490.1562 | 121.3394 | -9.4849 | 111.9278 | -0.18135 | -0.040253 | -0.00039957 | 0.022296 | 0.00064947 | -0.010102 | -0.0040823 | -0.11685 | 0.021332 | 0.01728 | -0.01041 | -0.017942 | 0.027408 | -0.00045291 | -0.07782 | 0.009155 | -0.082397 | -0.036621 | 0.059509 | -0.09613 | 0 | 0.013733 | 0.14191 | -0.059509 | -0.013733 | 0.10071 | 0.036621 | 0.086975 | 9.4025 | -111.9186 | -111.9644 | 9.5444 | 9.4849 | 9.3887 | 0.082397 | -0.013733 | 9.4254 | -111.7859 | -111.9415 | 9.5856 | 9.5718 | 9.5215 | 0.14648 | 0.09613 | 0.14191 | 0.045776 | 0.16022 | 0.045776 | 0.091552 | 0.20142 | 9.494 | 9.6268 | -112.0102 | -111.9873 | 9.4482 | 9.4711 | 9.407 | 9.4986
5491.8594 | 121.4996 | -9.0775 | 112.3718 | -0.11269 | -0.040467 | 0.00045503 | 0.021014 | 0.0051355 | -0.013093 | -0.0060049 | -0.12296 | 0.02475 | 0.01728 | -0.011051 | -0.019438 | 0.026126 | -0.0036573 | -0.09613 | 0.018311 | -0.07782 | -0.027466 | 0.045776 | -0.073242 | 0.009155 | 0.050354 | 0.13733 | -0.059509 | 0.009155 | 0.1236 | 0.059509 | 0.10071 | 8.9996 | -112.3535 | -112.3993 | 9.1232 | 9.0866 | 9.0042 | 0.086975 | 0.004578 | 9.0179 | -112.2345 | -112.3627 | 9.201 | 9.1782 | 9.137 | 0.16022 | 0.11902 | 0.1236 | 0.050354 | 0.1831 | 0.068664 | 0.096131 | 0.19684 | 9.0958 | 9.2148 | -112.4496 | -112.4313 | 9.05 | 9.0866 | 8.9813 | 9.1278
5493.6094 | 121.4722 | -8.7891 | 112.6785 | -0.13557 | -0.042603 | -0.0016812 | 0.018237 | 0.00064947 | -0.012452 | -0.0068593 | -0.06192 | 0.023896 | 0.016212 | -0.0228 | -0.017515 | 0.027408 | -0.0019483 | -0.16022 | 0.027466 | -0.082397 | -0.10986 | -0.004578 | -0.13275 | -0.009155 | -0.059509 | 0.15564 | -0.068665 | -0.07782 | 0.073242 | 0.004578 | 0.050354 | 8.7067 | -112.6511 | -112.7884 | 8.7845 | 8.7799 | 8.6563 | 0.073242 | -0.050354 | 8.7204 | -112.5229 | -112.7563 | 8.8623 | 8.8394 | 8.7936 | 0.11902 | 0.073243 | 0.077819 | -0.027466 | 0.14191 | -0.009155 | 0.10986 | 0.22431 | 8.8165 | 8.9447 | -112.7609 | -112.7472 | 8.6792 | 8.7112 | 8.6288 | 8.7296
5495.3906 | 121.5958 | -9.4711 | 111.9598 | -0.17372 | -0.04068 | 0.0036594 | 0.018023 | 0.0027857 | -0.0094614 | -0.0040823 | -0.046661 | 0.021546 | 0.018348 | -0.014682 | -0.021574 | 0.026767 | -0.0055799 | -0.054932 | 0 | -0.013733 | 0.022888 | 0.14191 | -0.032043 | 0.068665 | 0.10986 | 0.10071 | -0.032043 | 0.073242 | 0.19684 | 0.11902 | 0.16479 | 9.4574 | -111.9598 | -111.937 | 9.613 | 9.5398 | 9.4391 | 0.082398 | -0.01831 | 9.4391 | -111.8591 | -111.8866 | 9.668 | 9.6359 | 9.5901 | 0.19684 | 0.15106 | 0.15564 | 0.036621 | 0.22888 | 0.10529 | 0.013733 | 0.13275 | 9.4711 | 9.5718 | -111.9736 | -111.9919 | 9.494 | 9.5444 | 9.4162 | 9.581
5497.0938 | 121.5912 | -8.8028 | 112.619 | -0.21187 | -0.040039 | 0.0010958 | 0.021655 | -0.0021277 | -0.011811 | -0.0040823 | -0.1077 | 0.02176 | 0.015357 | -0.0134 | -0.020933 | 0.028262 | -0.0034435 | -0.1236 | 0.027466 | -0.045776 | -0.050354 | 0.045776 | -0.10986 | 0.009155 | 0.032043 | 0.11444 | -0.050354 | 0.041199 | 0.15564 | 0.064087 | 0.14648 | 8.757 | -112.5916 | -112.6694 | 8.8486 | 8.8119 | 8.6929 | 0.054931 | -0.064087 | 8.7524 | -112.5046 | -112.5778 | 8.9584 | 8.9493 | 8.8669 | 0.19684 | 0.11444 | 0.091552 | -0.004578 | 0.20599 | 0.091553 | 0.073242 | 0.16479 | 8.8303 | 8.9172 | -112.6648 | -112.6694 | 8.7524 | 8.844 | 8.6792 | 8.8348
5498.8594 | 121.582 | -8.67 | 112.793 | -0.17372 | -0.040253 | -0.00039957 | 0.019519 | 0.00086307 | -0.010316 | -0.0053641 | -0.022247 | 0.024537 | 0.01493 | -0.016605 | -0.018797 | 0.025272 | -0.0040845 | -0.10986 | -0.004578 | -0.027466 | -0.009155 | 0.10986 | -0.059509 | 0.045776 | 0.050354 | 0.09613 | -0.050354 | 0.004578 | 0.14191 | 0.086975 | 0.12817 | 8.6426 | -112.7975 | -112.8021 | 8.7799 | 8.7158 | 8.6105 | 0.073242 | -0.032043 | 8.6197 | -112.6968 | -112.7884 | 8.812 | 8.7982 | 8.757 | 0.17853 | 0.13733 | 0.13733 | 0.018311 | 0.19226 | 0.054932 | 0.022888 | 0.14648 | 8.6655 | 8.7662 | -112.8204 | -112.8433 | 8.6609 | 8.6746 | 8.5602 | 8.7204
5500.625 | 121.6507 | -8.4274 | 113.0127 | -0.1432 | -0.041535 | 0.00088223 | 0.020587 | 0.0034265 | -0.012452 | -0.0053641 | -0.077179 | 0.022614 | 0.015998 | -0.01041 | -0.019651 | 0.025272 | -0.0032299 | -0.068665 | -0.022888 | -0.041199 | 0.013733 | 0.11902 | -0.050354 | 0.07782 | 0.082397 | 0.10071 | -0.027466 | 0.073242 | 0.18768 | 0.13733 | 0.1831 | 8.3862 | -113.0356 | -112.999 | 8.5464 | 8.5052 | 8.3771 | 0.11902 | -0.009155 | 8.4 | -112.912 | -112.9395 | 8.6151 | 8.6105 | 8.5648 | 0.21057 | 0.16479 | 0.16022 | 0.054932 | 0.21515 | 0.10071 | 0.018311 | 0.12817 | 8.4045 | 8.5281 | -113.0539 | -113.0402 | 8.4412 | 8.5007 | 8.3588 | 8.5098
5502.3906 | 121.6324 | -8.4503 | 112.999 | -0.18135 | -0.040894 | -0.00018577 | 0.019305 | -0.00063233 | -0.01053 | -0.0047231 | -0.031403 | 0.02176 | 0.015785 | -0.0099827 | -0.020292 | 0.026767 | -0.0021619 | -0.091553 | 0 | -0.059509 | 0.018311 | 0.11902 | -0.068665 | 0.045776 | 0.07782 | 0.11902 | -0.032043 | 0.009155 | 0.13275 | 0.091553 | 0.14648 | 8.3908 | -112.999 | -112.9807 | 8.5693 | 8.4961 | 8.3817 | 0.10528 | -0.009156 | 8.4183 | -112.8799 | -112.9898 | 8.5831 | 8.5968 | 8.5419 | 0.17853 | 0.1236 | 0.17853 | 0.07782 | 0.16479 | 0.041198 | 0.059509 | 0.15106 | 8.4503 | 8.5693 | -113.0585 | -113.031 | 8.4686 | 8.4595 | 8.3588 | 8.5281
5504.1562 | 121.582 | -8.1894 | 113.3469 | -0.12794 | -0.041107 | -0.00061317 | 0.018451 | -0.00084593 | -0.013307 | -0.0042959 | -0.09549 | 0.022828 | 0.015144 | -0.0093417 | -0.020292 | 0.025058 | -0.0023755 | -0.14191 | 0.036621 | -0.082397 | -0.09613 | -0.009155 | -0.11902 | -0.013733 | -0.068665 | 0.14191 | -0.068665 | -0.050354 | 0.050354 | 0.009155 | 0.07782 | 8.107 | -113.3102 | -113.443 | 8.1802 | 8.1757 | 8.0704 | 0.068664 | -0.036622 | 8.1207 | -113.205 | -113.3972 | 8.2397 | 8.2672 | 8.1985 | 0.14649 | 0.07782 | 0.073242 | -0.013733 | 0.11902 | 0.018311 | 0.11902 | 0.21057 | 8.226 | 8.3313 | -113.4293 | -113.4155 | 8.0933 | 8.139 | 8.0475 | 8.1207
5505.8594 | 121.7056 | -8.1345 | 113.3194 | -0.17372 | -0.042816 | -0.00082677 | 0.019091 | -0.0023413 | -0.014161 | -0.0028005 | -0.016144 | 0.022401 | 0.016426 | -0.016178 | -0.019224 | 0.026126 | -0.0038709 | -0.11444 | 0.004578 | -0.059509 | 0.013733 | 0.11444 | -0.018311 | 0.082397 | 0.054932 | 0.10986 | -0.041199 | 0.050354 | 0.20599 | 0.16022 | 0.18768 | 8.075 | -113.3148 | -113.3057 | 8.2489 | 8.2169 | 8.1161 | 0.14191 | 0.041198 | 8.0933 | -113.2095 | -113.269 | 8.3405 | 8.3221 | 8.2947 | 0.22888 | 0.20142 | 0.17395 | 0.073242 | 0.24719 | 0.091553 | 0.064087 | 0.15106 | 8.139 | 8.2443 | -113.3789 | -113.3606 | 8.1482 | 8.1848 | 8.02 | 8.1894
5507.625 | 121.5958 | -7.9376 | 113.5849 | -0.20424 | -0.039398 | 0.0010958 | 0.021228 | 0.00086307 | -0.009675 | -0.0068593 | -0.13211 | 0.024323 | 0.01493 | -0.011264 | -0.020719 | 0.027408 | -0.0047253 | -0.12817 | 0.004578 | -0.07782 | -0.10529 | -0.032043 | -0.16937 | -0.050354 | -0.068665 | 0.13275 | -0.07782 | -0.050354 | 0.027466 | -0.018311 | 0.073242 | 7.8598 | -113.5803 | -113.6902 | 7.9056 | 7.8873 | 7.7682 | 0.027466 | -0.091553 | 7.8598 | -113.4521 | -113.6353 | 7.9651 | 8.0109 | 7.9193 | 0.15106 | 0.059509 | 0.045777 | -0.027466 | 0.10529 | 0.027466 | 0.082398 | 0.21057 | 7.9422 | 8.0704 | -113.6627 | -113.6627 | 7.8323 | 7.8873 | 7.8094 | 7.869
5509.3281 | 121.6095 | -7.8049 | 113.7497 | -0.18135 | -0.041535 | -0.00018577 | 0.016528 | -0.0081091 | -0.013307 | -0.0040823 | -0.037506 | 0.023041 | 0.016426 | -0.019809 | -0.019865 | 0.024631 | -0.0021619 | -0.07782 | -0.004578 | -0.054932 | -0.022888 | 0.091553 | -0.027466 | 0.064087 | 0.009155 | 0.12817 | -0.045776 | -0.013733 | 0.10986 | 0.045776 | 0.091553 | 7.7499 | -113.7543 | -113.7726 | 7.8964 | 7.869 | 7.7774 | 0.11902 | 0.027466 | 7.7591 | -113.6215 | -113.7634 | 7.9147 | 7.8964 | 7.8506 | 0.13733 | 0.091552 | 0.14649 | 0.032044 | 0.15564 | 0.032043 | 0.050354 | 0.17395 | 7.8003 | 7.933 | -113.8046 | -113.7955 | 7.782 | 7.7911 | 7.7271 | 7.814
5511.1094 | 121.6003 | -7.7408 | 113.8687 | -0.15083 | -0.039612 | -0.00082677 | 0.017382 | -0.0010595 | -0.011811 | -0.0042959 | -0.052765 | 0.022828 | 0.013008 | -0.017246 | -0.022001 | 0.024844 | -0.0079297 | -0.10529 | 0.009155 | -0.068665 | -0.059509 | 0.032043 | -0.07782 | 0.013733 | -0.041199 | 0.13733 | -0.064087 | -0.054932 | 0.07782 | 0.022888 | 0.068665 | 7.6721 | -113.8596 | -113.9282 | 7.7728 | 7.7545 | 7.663 | 0.082398 | -0.009155 | 7.6767 | -113.7314 | -113.9236 | 7.8186 | 7.8094 | 7.7637 | 0.13275 | 0.086975 | 0.10071 | 0.009156 | 0.14191 | 0.009155 | 0.07782 | 0.20142 | 7.7499 | 7.8781 | -113.9374 | -113.9328 | 7.6813 | 7.6859 | 7.6355 | 7.6996
5512.8125 | 121.7514 | -7.6859 | 113.7955 | -0.16609 | -0.041962 | 2.7834e-05 | 0.017382 | -0.0049047 | -0.012239 | -0.0021597 | -0.013092 | 0.023896 | 0.014503 | -0.012332 | -0.019865 | 0.025699 | -0.0045117 | -0.10529 | -0.004578 | -0.054932 | 0.027466 | 0.13275 | -0.004578 | 0.10071 | 0.09613 | 0.09613 | -0.050354 | 0.091553 | 0.19684 | 0.15564 | 0.1831 | 7.6309 | -113.8 | -113.768 | 7.8186 | 7.7866 | 7.6813 | 0.15564 | 0.050354 | 7.6355 | -113.6993 | -113.7039 | 7.8827 | 7.869 | 7.8415 | 0.23346 | 0.20599 | 0.18768 | 0.082398 | 0.24719 | 0.14191 | 0.050354 | 0.14648 | 7.6813 | 7.782 | -113.8504 | -113.8458 | 7.7133 | 7.7774 | 7.5806 | 7.782
5514.5781 | 121.6324 | -7.5943 | 114.0335 | -0.16609 | -0.040894 | 0.00066863 | 0.019732 | 0.0010767 | -0.014161 | -0.0092093 | -0.064972 | 0.02411 | 0.015998 | -0.0134 | -0.019865 | 0.026767 | -0.00088011 | -0.11444 | 0.013733 | -0.064087 | -0.073242 | 0.045776 | -0.10529 | 0 | -0.036621 | 0.14191 | -0.059509 | -0.068665 | 0.068665 | 0 | 0.050354 | 7.5302 | -114.0198 | -114.1067 | 7.6401 | 7.5943 | 7.489 | 0.064087 | -0.041199 | 7.5348 | -113.8916 | -114.1022 | 7.663 | 7.6447 | 7.5943 | 0.10986 | 0.059509 | 0.10986 | -0.009155 | 0.12817 | -0.009156 | 0.07782 | 0.20142 | 7.608 | 7.7362 | -114.0976 | -114.093 | 7.5211 | 7.5256 | 7.4799 | 7.5577
5516.3438 | 121.637 | -7.4799 | 114.1113 | -0.15846 | -0.039826 | 0.00024143 | 0.023791 | -0.00020513 | -0.013307 | -0.0064321 | -0.13211 | 0.02411 | 0.013862 | -0.010196 | -0.020719 | 0.027621 | -2.571e-05 | -0.091553 | 0.009155 | -0.064087 | -0.064087 | 0.027466 | -0.12817 | -0.032043 | -0.013733 | 0.14191 | -0.054932 | -0.041199 | 0.045776 | -0.022888 | 0.064087 | 7.4158 | -114.1022 | -114.1754 | 7.5073 | 7.4478 | 7.3517 | 0.032044 | -0.064087 | 7.4249 | -113.9694 | -114.1525 | 7.5256 | 7.5439 | 7.457 | 0.11902 | 0.032044 | 0.091553 | 0 | 0.10071 | 0.013733 | 0.073242 | 0.19684 | 7.489 | 7.6218 | -114.1754 | -114.1663 | 7.4158 | 7.4387 | 7.3883 | 7.4661
5518.1094 | 121.6965 | -7.4158 | 114.1251 | -0.16609 | -0.040039 | -0.0025358 | 0.019305 | -0.0012731 | -0.011811 | -0.0032277 | -0.0039367 | 0.023255 | 0.015571 | -0.010623 | -0.017515 | 0.025272 | -0.0025891 | -0.082397 | -0.022888 | -0.045776 | 0 | 0.10529 | -0.009155 | 0.086975 | 0.050354 | 0.11902 | -0.054932 | 0.009155 | 0.14648 | 0.068665 | 0.09613 | 7.37 | -114.1479 | -114.1251 | 7.5211 | 7.5027 | 7.4066 | 0.13275 | 0.036621 | 7.3608 | -114.006 | -114.1159 | 7.5623 | 7.5119 | 7.4844 | 0.15106 | 0.1236 | 0.15106 | 0.045776 | 0.20142 | 0.064087 | 0.022888 | 0.17395 | 7.3929 | 7.5348 | -114.1708 | -114.18 | 7.4158 | 7.4249 | 7.3334 | 7.4661
5519.875 | 121.6919 | -7.3975 | 114.2075 | -0.15846 | -0.043457 | -0.00082677 | 0.018237 | 8.47e-06 | -0.014161 | -0.0032277 | -0.028351 | 0.023469 | 0.01493 | -0.010837 | -0.018156 | 0.024844 | -0.0083569 | -0.07782 | -0.009155 | -0.041199 | 0.004578 | 0.10986 | -0.022888 | 0.059509 | 0.032043 | 0.10986 | -0.050354 | -0.009155 | 0.13275 | 0.068665 | 0.11444 | 7.3563 | -114.2166 | -114.2029 | 7.5073 | 7.457 | 7.3746 | 0.10071 | 0.018311 | 7.3471 | -114.0976 | -114.2166 | 7.5302 | 7.5119 | 7.4661 | 0.16479 | 0.11902 | 0.15106 | 0.045777 | 0.18311 | 0.041199 | 0.032044 | 0.16022 | 7.3883 | 7.5073 | -114.2487 | -114.2578 | 7.402 | 7.3883 | 7.3196 | 7.4295
5521.6562 | 121.0968 | -5.0446 | 115.9241 | -0.2195 | -0.042389 | 0.00024143 | 0.0208 | -0.0019141 | -0.01117 | -0.0028005 | -0.025299 | 0.024323 | 0.015144 | -0.011905 | -0.019865 | 0.026553 | -0.0038709 | -0.068665 | -0.004578 | -0.032043 | 0.022888 | 0.11902 | -0.050354 | 0.068665 | 0.07782 | 0.09613 | -0.032043 | 0.050354 | 0.15106 | 0.086975 | 0.13275 | 5.0125 | -115.9286 | -115.9012 | 5.1636 | 5.1132 | 4.9942 | 0.10071 | -0.018311 | 5.0125 | -115.8279 | -115.8737 | 5.1956 | 5.1773 | 5.1315 | 0.16479 | 0.11902 | 0.15106 | 0.054931 | 0.18311 | 0.082397 | 0.027465 | 0.12817 | 5.04 | 5.1407 | -115.9561 | -115.9561 | 5.0674 | 5.0949 | 4.9759 | 5.1224
5523.4219 | 121.3486 | -3.772 | 117.4118 | -0.2195 | -0.039826 | 0.00045503 | 0.019732 | 0.0012903 | -0.011811 | -0.0047231 | -0.040558 | 0.022614 | 0.017066 | -0.016178 | -0.020506 | 0.027408 | -0.0060071 | -0.054932 | -0.009155 | -0.018311 | 0.036621 | 0.1236 | -0.041199 | 0.082397 | 0.10529 | 0.10071 | -0.013733 | 0.082397 | 0.17395 | 0.10529 | 0.16479 | 3.7537 | -117.421 | -117.3752 | 3.8956 | 3.8544 | 3.7308 | 0.10071 | -0.022888 | 3.7582 | -117.3111 | -117.3294 | 3.9459 | 3.9368 | 3.8773 | 0.17853 | 0.11902 | 0.14191 | 0.054932 | 0.18768 | 0.09613 | 0.009156 | 0.11444 | 3.7628 | 3.8727 | -117.4301 | -117.4255 | 3.8086 | 3.8544 | 3.717 | 3.8773
5525.1875 | 121.3577 | -3.7537 | 117.5858 | -0.15846 | -0.038544 | 0.00024143 | 0.022937 | 0.00043587 | -0.012025 | -0.0068593 | -0.11075 | 0.025391 | 0.015144 | -0.0067783 | -0.018156 | 0.027194 | 0.00040169 | -0.086975 | 0.032043 | -0.059509 | -0.009155 | 0.059509 | -0.082397 | 0.018311 | 0.018311 | 0.11902 | -0.059509 | 0.013733 | 0.10071 | 0.022888 | 0.11902 | 3.6942 | -117.5537 | -117.5949 | 3.8132 | 3.772 | 3.6713 | 0.07782 | -0.022888 | 3.6942 | -117.4667 | -117.572 | 3.8544 | 3.8727 | 3.7765 | 0.17853 | 0.082397 | 0.11902 | 0.050354 | 0.16022 | 0.073242 | 0.091552 | 0.17853 | 3.7857 | 3.8727 | -117.6453 | -117.6453 | 3.7445 | 3.7674 | 3.6667 | 3.772
5526.9531 | 121.4584 | -4.2709 | 117.0731 | -0.15846 | -0.040253 | 0.00066863 | 0.018878 | 0.0032129 | -0.011384 | -0.0057913 | -0.019196 | 0.023255 | 0.016639 | -0.012119 | -0.018583 | 0.026553 | -0.0038709 | -0.10529 | -0.004578 | -0.027466 | -0.018311 | 0.07782 | -0.068665 | 0.068665 | 0.018311 | 0.10529 | -0.054932 | 0.004578 | 0.13275 | 0.086975 | 0.1236 | 4.2435 | -117.0776 | -117.0914 | 4.3488 | 4.3396 | 4.2023 | 0.096131 | -0.041199 | 4.216 | -116.9678 | -117.0685 | 4.4037 | 4.3945 | 4.3579 | 0.17853 | 0.14191 | 0.10529 | 0.009155 | 0.18768 | 0.05951 | 0.022888 | 0.16022 | 4.2664 | 4.3762 | -117.1005 | -117.128 | 4.2526 | 4.2755 | 4.1656 | 4.2892
5528.6562 | 121.4035 | -4.0237 | 117.4393 | -0.1432 | -0.040039 | 2.7834e-05 | 0.023578 | 0.0049219 | -0.01053 | -0.0038687 | -0.11075 | 0.023682 | 0.015571 | -0.0084873 | -0.019865 | 0.028049 | -0.0034435 | -0.11444 | 0.022888 | -0.068665 | -0.082397 | 0.018311 | -0.14191 | -0.032043 | -0.041199 | 0.14191 | -0.054932 | -0.050354 | 0.045776 | -0.036621 | 0.064087 | 3.9551 | -117.4164 | -117.5217 | 4.0421 | 3.9917 | 3.8818 | 0.036622 | -0.073242 | 3.9688 | -117.2974 | -117.4896 | 4.0695 | 4.0878 | 3.9871 | 0.11902 | 0.018311 | 0.086976 | -0.013732 | 0.10071 | 0.004578 | 0.091553 | 0.19684 | 4.0466 | 4.1656 | -117.5079 | -117.4942 | 3.9413 | 3.9734 | 3.9093 | 3.9825
5530.4062 | 121.5454 | -3.7949 | 117.5949 | -0.18135 | -0.041748 | 0.00088223 | 0.020587 | -0.00063233 | -0.011598 | -0.0062185 | -0.089386 | 0.023469 | 0.014717 | -0.014469 | -0.020078 | 0.027408 | -0.0040845 | -0.13733 | 0.027466 | -0.068665 | -0.059509 | 0.050354 | -0.10986 | 0.013733 | 0.013733 | 0.10986 | -0.050354 | 0.059509 | 0.14648 | 0.091553 | 0.15106 | 3.7262 | -117.5674 | -117.6544 | 3.8452 | 3.8086 | 3.685 | 0.082398 | -0.041198 | 3.7445 | -117.485 | -117.5354 | 3.9413 | 3.9459 | 3.8864 | 0.20142 | 0.14191 | 0.11902 | 0.009156 | 0.19684 | 0.10986 | 0.096131 | 0.16022 | 3.8223 | 3.9047 | -117.6636 | -117.6453 | 3.7354 | 3.8544 | 3.6575 | 3.8086
5532.1719 | 121.6278 | -3.392 | 118.0161 | -0.16609 | -0.044953 | 0.0010958 | 0.018451 | -0.0044775 | -0.012025 | -0.0062185 | 0.026581 | 0.023896 | 0.014717 | -0.017887 | -0.019865 | 0.024844 | -0.0038709 | -0.073242 | 0.009155 | -0.032043 | 0.036621 | 0.17853 | 0.022888 | 0.10529 | 0.11902 | 0.11444 | -0.041199 | 0.068665 | 0.21515 | 0.16937 | 0.15564 | 3.36 | -118.0069 | -117.9794 | 3.5706 | 3.4973 | 3.4149 | 0.13733 | 0.054931 | 3.3508 | -117.9016 | -117.9474 | 3.6072 | 3.5477 | 3.5614 | 0.19684 | 0.21057 | 0.21057 | 0.068664 | 0.25635 | 0.10986 | 0.041198 | 0.15564 | 3.4012 | 3.5065 | -118.0481 | -118.0573 | 3.4286 | 3.4607 | 3.3188 | 3.511
5533.9375 | 121.5454 | -3.3829 | 118.1213 | -0.12032 | -0.042603 | -0.00039957 | 0.021869 | -0.0012731 | -0.012025 | -0.0053641 | -0.089386 | 0.02475 | 0.015571 | -0.0097689 | -0.01901 | 0.029971 | -0.0034435 | -0.11902 | 0.018311 | -0.073242 | -0.086975 | -0.004578 | -0.091553 | -0.004578 | -0.027466 | 0.14191 | -0.07782 | -0.013733 | 0.09613 | 0.036621 | 0.091553 | 3.3096 | -118.103 | -118.2083 | 3.3783 | 3.3783 | 3.2913 | 0.068664 | -0.018311 | 3.3051 | -117.9794 | -118.1351 | 3.479 | 3.4744 | 3.4195 | 0.16937 | 0.11444 | 0.068664 | -0.013733 | 0.17395 | 0.064087 | 0.091553 | 0.21973 | 3.4012 | 3.5248 | -118.1946 | -118.1992 | 3.2959 | 3.3691 | 3.2639 | 3.3554
5535.6875 | 121.5088 | -3.2913 | 118.2678 | -0.13557 | -0.040039 | 0.0019504 | 0.022082 | 0.0017175 | -0.01352 | -0.0047231 | -0.1077 | 0.024537 | 0.01728 | -0.012332 | -0.019438 | 0.024844 | -0.0013073 | -0.11902 | 0.009155 | -0.073242 | -0.07782 | 0.022888 | -0.12817 | -0.022888 | -0.022888 | 0.13733 | -0.059509 | -0.041199 | 0.045776 | -0.013733 | 0.050354 | 3.2181 | -118.2587 | -118.3456 | 3.3142 | 3.2684 | 3.1631 | 0.050354 | -0.054932 | 3.2318 | -118.1305 | -118.309 | 3.3371 | 3.3417 | 3.2776 | 0.10986 | 0.045776 | 0.09613 | -0.004578 | 0.10528 | 0.01831 | 0.082397 | 0.19684 | 3.3005 | 3.4286 | -118.3411 | -118.3273 | 3.2135 | 3.2501 | 3.1723 | 3.2684
5537.3906 | 121.637 | -3.2364 | 118.277 | -0.16609 | -0.041107 | 0.0013094 | 0.016101 | -0.0017005 | -0.012666 | -0.0066457 | -0.0069885 | 0.024537 | 0.015785 | -0.0181 | -0.019438 | 0.02399 | -0.0028027 | -0.073242 | -0.013733 | -0.041199 | 0.018311 | 0.13275 | -0.004578 | 0.091553 | 0.068665 | 0.10529 | -0.045776 | 0.036621 | 0.16937 | 0.11444 | 0.14191 | 3.1952 | -118.2907 | -118.2587 | 3.3691 | 3.3279 | 3.2318 | 0.13275 | 0.036621 | 3.1906 | -118.1717 | -118.2404 | 3.4058 | 3.3783 | 3.3508 | 0.18768 | 0.16022 | 0.17395 | 0.05951 | 0.21515 | 0.082397 | 0.027466 | 0.15106 | 3.2227 | 3.3417 | -118.3182 | -118.3228 | 3.2547 | 3.273 | 3.1631 | 3.3051
5539.1562 | 121.5637 | -3.1952 | 118.3502 | -0.16609 | -0.038117 | -0.00018577 | 0.021869 | -0.00041873 | -0.01352 | -0.0032277 | -0.12601 | 0.023896 | 0.014717 | -0.0052829 | -0.019865 | 0.025485 | -0.0055799 | -0.12817 | 0.022888 | -0.082397 | -0.10071 | -0.041199 | -0.1831 | -0.045776 | -0.086975 | 0.14191 | -0.082397 | -0.045776 | 0.036621 | -0.018311 | 0.082397 | 3.1128 | -118.3273 | -118.4509 | 3.154 | 3.1494 | 3.0121 | 0.036621 | -0.10071 | 3.1128 | -118.2083 | -118.396 | 3.2318 | 3.2776 | 3.1769 | 0.16479 | 0.064086 | 0.041198 | -0.018311 | 0.11902 | 0.036621 | 0.10528 | 0.2243 | 3.2181 | 3.3371 | -118.4326 | -118.4326 | 3.0945 | 3.1494 | 3.067 | 3.1082
5540.8594 | 121.7239 | -3.1448 | 118.3456 | -0.18135 | -0.042389 | 0.00088223 | 0.01781 | 0.0017175 | -0.012025 | -0.0079275 | -0.013092 | 0.022401 | 0.015144 | -0.017459 | -0.017729 | 0.024417 | -0.0040845 | -0.07782 | -0.022888 | -0.041199 | 0.027466 | 0.17395 | 0.027466 | 0.11902 | 0.12817 | 0.086975 | -0.027466 | 0.064087 | 0.19684 | 0.15564 | 0.15106 | 3.1036 | -118.3685 | -118.3182 | 3.3188 | 3.2639 | 3.1723 | 0.16022 | 0.068665 | 3.1174 | -118.2587 | -118.2816 | 3.3417 | 3.2959 | 3.3005 | 0.17853 | 0.18311 | 0.21515 | 0.068665 | 0.2243 | 0.091553 | 0.018311 | 0.11444 | 3.1219 | 3.2318 | -118.3868 | -118.3731 | 3.1723 | 3.2089 | 3.067 | 3.273
5542.6562 | 121.6599 | -3.3646 | 118.19 | -0.15846 | -0.039826 | 0.00088223 | 0.022082 | 0.0012903 | -0.0098886 | -0.0068593 | -0.083283 | 0.024964 | 0.01493 | -0.0099827 | -0.019865 | 0.026126 | -0.0010937 | -0.1236 | 0 | -0.064087 | -0.068665 | 0.013733 | -0.13733 | -0.013733 | 0.004578 | 0.13275 | -0.07782 | 0.018311 | 0.091553 | 0.041199 | 0.10986 | 3.3005 | -118.19 | -118.2587 | 3.3783 | 3.3508 | 3.2272 | 0.050354 | -0.073242 | 3.2867 | -118.0573 | -118.1717 | 3.4561 | 3.4744 | 3.4058 | 0.18768 | 0.11902 | 0.07782 | -0.004578 | 0.16937 | 0.096131 | 0.064087 | 0.21057 | 3.3646 | 3.4973 | -118.2541 | -118.2678 | 3.2959 | 3.3829 | 3.241 | 3.3691
5544.3594 | 121.6232 | -3.4012 | 118.2083 | -0.15083 | -0.041535 | -0.0027494 | 0.017596 | -0.0019141 | -0.010316 | -0.0060049 | -0.0069885 | 0.024537 | 0.015998 | -0.017673 | -0.019224 | 0.025699 | -0.0030163 | -0.15564 | 0.004578 | -0.091553 | -0.09613 | 0.009155 | -0.09613 | -0.004578 | -0.07782 | 0.13275 | -0.09613 | -0.068665 | 0.045776 | 0.009155 | 0.054932 | 3.3096 | -118.2037 | -118.3044 | 3.4103 | 3.3966 | 3.3051 | 0.086975 | -0.004577 | 3.3051 | -118.0756 | -118.277 | 3.447 | 3.4561 | 3.4103 | 0.15106 | 0.10528 | 0.10071 | -0.004577 | 0.14191 | 0.027465 | 0.096131 | 0.22888 | 3.4058 | 3.5339 | -118.2999 | -118.3044 | 3.3051 | 3.3325 | 3.2455 | 3.3234
5546.125 | 121.6415 | -3.392 | 118.2404 | -0.12032 | -0.039185 | 2.7834e-05 | 0.019519 | -0.0010595 | -0.011811 | -0.0057913 | -0.089386 | 0.023682 | 0.015144 | -0.017032 | -0.02136 | 0.02634 | -0.010066 | -0.086975 | 0.027466 | -0.059509 | -0.041199 | 0.050354 | -0.091553 | 0.032043 | 0.032043 | 0.11902 | -0.054932 | 0 | 0.086975 | 0.018311 | 0.10529 | 3.3325 | -118.2129 | -118.2816 | 3.4424 | 3.4241 | 3.3005 | 0.091552 | -0.032044 | 3.3371 | -118.1213 | -118.2404 | 3.479 | 3.4973 | 3.4103 | 0.16022 | 0.073243 | 0.10986 | 0.01831 | 0.14191 | 0.054932 | 0.086975 | 0.17395 | 3.4195 | 3.511 | -118.2999 | -118.2953 | 3.3508 | 3.392 | 3.3051 | 3.4241
5547.8906 | 121.6919 | -3.392 | 118.2312 | -0.18135 | -0.039826 | 0.0017368 | 0.022296 | -0.0038367 | -0.013093 | -0.0042959 | -0.071076 | 0.021973 | 0.014289 | -0.0095553 | -0.019865 | 0.025058 | -0.00066651 | -0.09613 | 0.022888 | -0.073242 | -0.045776 | 0.054932 | -0.07782 | 0.013733 | 0.009155 | 0.13275 | -0.054932 | -0.004578 | 0.10986 | 0.064087 | 0.1236 | 3.3188 | -118.2083 | -118.277 | 3.447 | 3.4058 | 3.3142 | 0.086975 | -0.004578 | 3.3371 | -118.0984 | -118.2358 | 3.5019 | 3.5156 | 3.4561 | 0.17853 | 0.11902 | 0.12817 | 0.027466 | 0.16479 | 0.050354 | 0.09613 | 0.18768 | 3.4149 | 3.5248 | -118.3044 | -118.2861 | 3.3463 | 3.3875 | 3.2959 | 3.4012
5549.6406 | 121.6507 | -3.3966 | 118.2541 | -0.13557 | -0.040253 | -0.00018577 | 0.02016 | 0.0021447 | -0.011598 | -0.0021597 | -0.074127 | 0.026459 | 0.014503 | -0.0084873 | -0.018583 | 0.025485 | -0.0025891 | -0.10986 | 0.022888 | -0.054932 | -0.050354 | 0.027466 | -0.10071 | -0.013733 | -0.009155 | 0.13275 | -0.059509 | -0.032043 | 0.054932 | -0.004578 | 0.07782 | 3.3417 | -118.2312 | -118.3044 | 3.4241 | 3.3829 | 3.2959 | 0.041199 | -0.045776 | 3.3371 | -118.1213 | -118.2861 | 3.4515 | 3.4744 | 3.392 | 0.13733 | 0.054931 | 0.082398 | 0.004578 | 0.11444 | 0.027466 | 0.07782 | 0.19226 | 3.4195 | 3.5294 | -118.309 | -118.3136 | 3.3463 | 3.3646 | 3.2867 | 3.3875
5551.4062 | 121.7926 | -3.3325 | 118.2587 | -0.2195 | -0.037262 | 0.0028048 | 0.018664 | 8.47e-06 | -0.012239 | -0.0023733 | -0.01004 | 0.023255 | 0.016212 | -0.014682 | -0.018369 | 0.025912 | -0.0055799 | -0.050354 | -0.013733 | -0.018311 | 0.027466 | 0.14191 | -0.036621 | 0.07782 | 0.10986 | 0.091553 | -0.041199 | 0.091553 | 0.1831 | 0.12817 | 0.15564 | 3.3142 | -118.2724 | -118.2312 | 3.4744 | 3.4103 | 3.2959 | 0.096131 | -0.01831 | 3.2913 | -118.1671 | -118.1671 | 3.5156 | 3.4882 | 3.4607 | 0.19684 | 0.16937 | 0.16022 | 0.045777 | 0.2243 | 0.13275 | 0.004578 | 0.13275 | 3.3188 | 3.4241 | -118.277 | -118.2999 | 3.36 | 3.4241 | 3.2822 | 3.4424
5553.1875 | 121.6827 | -3.3737 | 118.2953 | -0.17372 | -0.041321 | 0.001523 | 0.02315 | -0.0012731 | -0.012879 | -0.0030141 | -0.086334 | 0.022187 | 0.015357 | -0.010837 | -0.021147 | 0.028903 | -0.0077161 | -0.13275 | 0.022888 | -0.07782 | -0.10071 | -0.022888 | -0.13733 | -0.032043 | -0.054932 | 0.12817 | -0.082397 | -0.054932 | 0.045776 | -0.022888 | 0.073242 | 3.2959 | -118.2724 | -118.396 | 3.3508 | 3.3417 | 3.2364 | 0.045777 | -0.059509 | 3.2913 | -118.1671 | -118.3502 | 3.4195 | 3.447 | 3.3508 | 0.15564 | 0.059509 | 0.054932 | -0.022888 | 0.12817 | 0.027465 | 0.10071 | 0.21057 | 3.3966 | 3.5019 | -118.3731 | -118.3777 | 3.273 | 3.3188 | 3.241 | 3.3188
5554.9531 | 121.7834 | -3.2135 | 118.364 | -0.1432 | -0.042176 | 0.00088223 | 0.019519 | 0.00022207 | -0.01053 | -0.0038687 | 0.0021667 | 0.02176 | 0.01728 | -0.018741 | -0.02136 | 0.026553 | -0.0047253 | -0.073242 | -0.013733 | -0.036621 | 0.036621 | 0.14648 | 0.009155 | 0.09613 | 0.082397 | 0.09613 | -0.036621 | 0.059509 | 0.18768 | 0.1236 | 0.17395 | 3.1769 | -118.3777 | -118.3273 | 3.36 | 3.3096 | 3.2227 | 0.13275 | 0.045776 | 3.1769 | -118.2678 | -118.3044 | 3.4012 | 3.3875 | 3.3371 | 0.21057 | 0.16022 | 0.18311 | 0.073242 | 0.2243 | 0.09613 | 0.022888 | 0.13275 | 3.1998 | 3.3096 | -118.4006 | -118.4006 | 3.2501 | 3.273 | 3.1403 | 3.2959
5556.6562 | 121.6827 | -3.2547 | 118.4189 | -0.12032 | -0.041748 | 0.00024143 | 0.020373 | -0.0010595 | -0.015016 | -0.0053641 | -0.016144 | 0.023682 | 0.014289 | -0.015109 | -0.018583 | 0.025485 | -0.0045117 | -0.11902 | 0.027466 | -0.059509 | -0.091553 | 0.032043 | -0.10071 | 0.009155 | -0.054932 | 0.13733 | -0.082397 | -0.073242 | 0.041199 | 0.009155 | 0.064087 | 3.1952 | -118.3914 | -118.5104 | 3.2867 | 3.2639 | 3.154 | 0.068664 | -0.041199 | 3.1723 | -118.2816 | -118.4921 | 3.2959 | 3.3188 | 3.2639 | 0.14648 | 0.091552 | 0.091552 | -0.032044 | 0.1236 | 0.009155 | 0.086975 | 0.21973 | 3.2822 | 3.392 | -118.4784 | -118.5013 | 3.1631 | 3.1815 | 3.1357 | 3.1998
5558.4062 | 121.6599 | -3.1998 | 118.5059 | -0.20424 | -0.038758 | 0.0013094 | 0.022082 | 0.0025721 | -0.015229 | -0.0021597 | -0.092438 | 0.024537 | 0.015144 | -0.0076327 | -0.021787 | 0.026767 | -2.571e-05 | -0.13275 | 0.027466 | -0.07782 | -0.11444 | -0.045776 | -0.16937 | -0.054932 | -0.091553 | 0.13733 | -0.068665 | -0.064087 | 0.004578 | -0.045776 | 0.036621 | 3.1219 | -118.4784 | -118.6203 | 3.154 | 3.1448 | 3.0304 | 0.022888 | -0.091553 | 3.1311 | -118.3685 | -118.5699 | 3.2043 | 3.2364 | 3.154 | 0.10529 | 0.022889 | 0.032044 | -0.036621 | 0.073243 | 0.004578 | 0.10529 | 0.20599 | 3.2272 | 3.3371 | -118.5837 | -118.5745 | 3.0853 | 3.1357 | 3.067 | 3.1082
5560.1719 | 121.7422 | -3.1631 | 118.515 | -0.15083 | -0.042389 | -0.00018577 | 0.020373 | -0.00041873 | -0.011811 | -0.0062185 | -0.052765 | 0.024537 | 0.016853 | -0.016178 | -0.017729 | 0.02634 | -0.0049389 | -0.13275 | 0.036621 | -0.073242 | -0.082397 | 0.018311 | -0.09613 | -0.004578 | -0.018311 | 0.1236 | -0.07782 | -0.009155 | 0.086975 | 0.018311 | 0.10986 | 3.0899 | -118.4784 | -118.5974 | 3.1815 | 3.1586 | 3.067 | 0.068664 | -0.022888 | 3.0853 | -118.3914 | -118.5242 | 3.2501 | 3.273 | 3.1815 | 0.18768 | 0.096131 | 0.091553 | -0.009155 | 0.16479 | 0.068665 | 0.10986 | 0.20142 | 3.1998 | 3.2867 | -118.5883 | -118.5928 | 3.0808 | 3.154 | 3.0304 | 3.1448
5561.875 | 121.7194 | -3.1998 | 118.5287 | -0.19661 | -0.042389 | -0.0018948 | 0.01781 | 0.00022207 | -0.012879 | -0.0040823 | -0.01004 | 0.022828 | 0.016212 | -0.017887 | -0.018583 | 0.025699 | -0.0017347 | -0.10071 | 0.013733 | -0.073242 | -0.045776 | 0.068665 | -0.064087 | 0.041199 | -0.045776 | 0.12817 | -0.050354 | -0.064087 | 0.068665 | 0.022888 | 0.054932 | 3.1265 | -118.515 | -118.5745 | 3.2684 | 3.241 | 3.1357 | 0.11444 | 0.009155 | 3.1494 | -118.4006 | -118.5928 | 3.2684 | 3.2547 | 3.2227 | 0.10529 | 0.073242 | 0.14191 | 0.027466 | 0.11902 | -0.013733 | 0.086975 | 0.17853 | 3.2135 | 3.3279 | -118.602 | -118.5791 | 3.154 | 3.1357 | 3.0991 | 3.154
5563.625 | 121.7056 | -3.1311 | 118.5791 | -0.1432 | -0.04303 | -0.00018577 | 0.019305 | 8.47e-06 | -0.015016 | -0.0062185 | -0.0039367 | 0.023255 | 0.01493 | -0.014469 | -0.018797 | 0.025912 | -0.0038709 | -0.13275 | 0.018311 | -0.068665 | -0.082397 | 0.013733 | -0.10071 | 0 | -0.054932 | 0.14191 | -0.068665 | -0.059509 | 0.054932 | 0.013733 | 0.050354 | 3.0624 | -118.5608 | -118.6615 | 3.1448 | 3.1311 | 3.0304 | 0.068665 | -0.032043 | 3.0624 | -118.4372 | -118.6386 | 3.186 | 3.1815 | 3.1448 | 0.11902 | 0.082398 | 0.082398 | -0.013732 | 0.1236 | 0.009156 | 0.086976 | 0.21057 | 3.1494 | 3.273 | -118.6478 | -118.6478 | 3.0487 | 3.0716 | 2.9984 | 3.0762
5565.3438 | 121.8155 | -3.0991 | 118.5699 | -0.20424 | -0.038758 | 0.0010958 | 0.0208 | -0.0010595 | -0.010102 | -0.0042959 | -0.064972 | 0.023041 | 0.015357 | -0.015537 | -0.019865 | 0.02634 | -0.0010937 | -0.12817 | 0.022888 | -0.07782 | -0.073242 | 0.032043 | -0.12817 | -0.004578 | 0.022888 | 0.12817 | -0.054932 | 0.036621 | 0.10986 | 0.054932 | 0.14191 | 3.0212 | -118.5471 | -118.6432 | 3.1311 | 3.0945 | 2.9709 | 0.073242 | -0.050354 | 3.0441 | -118.4418 | -118.5333 | 3.2089 | 3.241 | 3.154 | 0.19684 | 0.10986 | 0.10986 | 0.004578 | 0.16479 | 0.091553 | 0.10071 | 0.18311 | 3.1219 | 3.2272 | -118.6478 | -118.6249 | 3.0258 | 3.1357 | 2.9709 | 3.1219
5567.1094 | 121.756 | -3.1128 | 118.6066 | -0.13557 | -0.041107 | -0.001254 | 0.017382 | -0.00063233 | -0.01053 | -0.0062185 | 0.011322 | 0.023041 | 0.015571 | -0.015323 | -0.019651 | 0.025272 | -0.0025891 | -0.07782 | -0.004578 | -0.054932 | -0.009155 | 0.091553 | -0.022888 | 0.045776 | 0.018311 | 0.11902 | -0.064087 | -0.013733 | 0.091553 | 0.032043 | 0.082397 | 3.0579 | -118.6111 | -118.6157 | 3.2043 | 3.1586 | 3.0899 | 0.10071 | 0.032044 | 3.0487 | -118.4875 | -118.6203 | 3.2043 | 3.1952 | 3.1448 | 0.14648 | 0.09613 | 0.14649 | 0.045777 | 0.15564 | 0.050354 | 0.050354 | 0.18311 | 3.1082 | 3.2318 | -118.6615 | -118.6707 | 3.1036 | 3.0991 | 3.035 | 3.1311
5568.8594 | 121.7743 | -3.0991 | 118.6203 | -0.13557 | -0.042176 | -0.00082677 | 0.019732 | -0.0012731 | -0.012025 | -0.0055777 | -0.040558 | 0.022828 | 0.015357 | -0.0061375 | -0.021147 | 0.026553 | -0.0021619 | -0.13275 | 0.032043 | -0.07782 | -0.10071 | -0.022888 | -0.10529 | 0 | -0.059509 | 0.14191 | -0.050354 | -0.054932 | 0.054932 | 0.018311 | 0.068665 | 3.0212 | -118.5883 | -118.721 | 3.0762 | 3.0991 | 2.9938 | 0.07782 | -0.027466 | 3.0487 | -118.4784 | -118.6752 | 3.154 | 3.1677 | 3.1174 | 0.11902 | 0.068665 | 0.054932 | -0.022888 | 0.10529 | -0.004578 | 0.10986 | 0.19226 | 3.1311 | 3.241 | -118.6981 | -118.6707 | 2.9984 | 3.0441 | 2.9663 | 3.0396
5570.625 | 121.788 | -3.1219 | 118.5928 | -0.18135 | -0.040039 | -0.00018577 | 0.023791 | 0.00086307 | -0.011598 | -0.0060049 | -0.06192 | 0.024964 | 0.018562 | -0.016178 | -0.019438 | 0.025272 | -0.0036573 | -0.12817 | 0.027466 | -0.07782 | -0.10529 | 0 | -0.14191 | -0.013733 | -0.032043 | 0.14648 | -0.07782 | 0 | 0.068665 | 0.018311 | 0.07782 | 3.0441 | -118.5654 | -118.6981 | 3.1219 | 3.1082 | 2.98 | 0.064087 | -0.064087 | 3.0441 | -118.4463 | -118.5928 | 3.1906 | 3.1998 | 3.1403 | 0.15564 | 0.096131 | 0.07782 | -0.027466 | 0.14649 | 0.07782 | 0.10529 | 0.2243 | 3.1494 | 3.2684 | -118.6707 | -118.6707 | 3.0167 | 3.1219 | 2.9938 | 3.0899
5572.3281 | 121.8842 | -3.1952 | 118.4738 | -0.097427 | -0.043885 | -0.001254 | 0.019519 | 0.0015039 | -0.011811 | -0.0028005 | 0.0082703 | 0.023255 | 0.016212 | -0.018741 | -0.018583 | 0.027194 | -0.0030163 | -0.059509 | 0 | -0.050354 | 0.022888 | 0.15564 | 0.004578 | 0.091553 | 0.10529 | 0.10071 | -0.045776 | 0.059509 | 0.18768 | 0.13733 | 0.15106 | 3.1448 | -118.4738 | -118.4509 | 3.3508 | 3.2867 | 3.1998 | 0.14191 | 0.054932 | 3.1494 | -118.3731 | -118.4143 | 3.3829 | 3.3463 | 3.3325 | 0.19684 | 0.18311 | 0.20599 | 0.073242 | 0.23346 | 0.10528 | 0.050354 | 0.14648 | 3.1952 | 3.2959 | -118.5242 | -118.5196 | 3.2181 | 3.2547 | 3.1357 | 3.3005
5574.1094 | 121.8246 | -3.2272 | 118.4921 | -0.18135 | -0.038758 | 2.7834e-05 | 0.02315 | 0.00022207 | -0.013093 | -0.0023733 | -0.092438 | 0.023469 | 0.016426 | -0.012973 | -0.020292 | 0.027194 | -0.0017347 | -0.13275 | 0.041199 | -0.068665 | -0.07782 | 0.013733 | -0.14191 | -0.018311 | -0.018311 | 0.11902 | -0.054932 | 0.013733 | 0.073242 | 0.018311 | 0.11444 | 3.1586 | -118.4509 | -118.5699 | 3.241 | 3.2089 | 3.0853 | 0.050354 | -0.073242 | 3.1723 | -118.3731 | -118.4784 | 3.3005 | 3.3417 | 3.2455 | 0.16937 | 0.073243 | 0.082398 | -0.009155 | 0.12817 | 0.068665 | 0.10986 | 0.17395 | 3.2684 | 3.3463 | -118.5608 | -118.5471 | 3.1494 | 3.241 | 3.0945 | 3.2089
5575.8125 | 121.7697 | -3.2318 | 118.5471 | -0.15083 | -0.043457 | -0.00061317 | 0.0208 | -0.0021277 | -0.011811 | -0.0070731 | -0.034454 | 0.023896 | 0.015571 | -0.014896 | -0.020933 | 0.025699 | -0.0015209 | -0.16022 | 0.027466 | -0.086975 | -0.10529 | -0.004578 | -0.11444 | -0.009155 | -0.068665 | 0.14191 | -0.064087 | -0.059509 | 0.045776 | 0.009155 | 0.054932 | 3.1448 | -118.5196 | -118.6523 | 3.2272 | 3.2227 | 3.1174 | 0.07782 | -0.027466 | 3.1677 | -118.4052 | -118.6066 | 3.2776 | 3.2867 | 3.241 | 0.11902 | 0.073242 | 0.082397 | -0.018311 | 0.10986 | 0.004578 | 0.11444 | 0.20599 | 3.2593 | 3.3737 | -118.634 | -118.6111 | 3.1265 | 3.1723 | 3.0716 | 3.1631
5577.5781 | 121.8567 | -3.1815 | 118.4921 | -0.21187 | -0.039185 | 0.00088223 | 0.017169 | 0.00043587 | -0.01117 | -0.0045095 | -0.022247 | 0.022614 | 0.014717 | -0.014682 | -0.019438 | 0.027408 | -0.0053661 | -0.082397 | 0.004578 | -0.018311 | 0.018311 | 0.13275 | -0.050354 | 0.064087 | 0.07782 | 0.086975 | -0.032043 | 0.032043 | 0.12817 | 0.082397 | 0.13733 | 3.1631 | -118.4875 | -118.4738 | 3.3142 | 3.2455 | 3.1311 | 0.082398 | -0.032043 | 3.1494 | -118.4052 | -118.4601 | 3.3096 | 3.3188 | 3.2639 | 0.16937 | 0.11444 | 0.15106 | 0.036622 | 0.16022 | 0.064086 | 0.022889 | 0.11902 | 3.186 | 3.2684 | -118.5104 | -118.5242 | 3.1998 | 3.2135 | 3.0991 | 3.2593
5579.2812 | 121.8246 | -3.2043 | 118.5242 | -0.21187 | -0.040039 | -0.00039957 | 0.021228 | 0.00043587 | -0.012666 | -0.0015189 | -0.09549 | 0.023682 | 0.014717 | -0.016605 | -0.022215 | 0.027621 | -0.0053661 | -0.091553 | 0.013733 | -0.073242 | -0.036621 | 0.050354 | -0.086975 | 0.027466 | 0.045776 | 0.13733 | -0.073242 | 0.004578 | 0.09613 | 0.036621 | 0.10071 | 3.1311 | -118.5104 | -118.5608 | 3.2547 | 3.2318 | 3.1174 | 0.10071 | -0.013733 | 3.1311 | -118.3868 | -118.5196 | 3.3005 | 3.3051 | 3.241 | 0.17395 | 0.10986 | 0.1236 | 0.036621 | 0.16937 | 0.07782 | 0.086975 | 0.21057 | 3.2181 | 3.3417 | -118.5974 | -118.5974 | 3.1677 | 3.2089 | 3.1128 | 3.2501
5581.0312 | 121.8979 | -3.1815 | 118.5379 | -0.22713 | -0.038758 | 0.001523 | 0.02315 | 8.47e-06 | -0.011811 | -0.0045095 | -0.071076 | 0.022614 | 0.016639 | -0.011264 | -0.021147 | 0.026553 | -0.0049389 | -0.1236 | 0.027466 | -0.068665 | -0.032043 | 0.045776 | -0.11444 | 0.018311 | 0.045776 | 0.09613 | -0.054932 | 0.050354 | 0.13733 | 0.07782 | 0.16479 | 3.1128 | -118.5104 | -118.5699 | 3.2272 | 3.1998 | 3.067 | 0.086976 | -0.045776 | 3.1265 | -118.4418 | -118.4875 | 3.3188 | 3.3463 | 3.2593 | 0.21973 | 0.13275 | 0.11444 | 0.036622 | 0.19226 | 0.10529 | 0.096131 | 0.15106 | 3.2089 | 3.2776 | -118.6066 | -118.5928 | 3.1494 | 3.2318 | 3.0579 | 3.2272
5582.7969 | 121.843 | -3.2135 | 118.5471 | -0.16609 | -0.041535 | 0.001523 | 0.019946 | 0.0019311 | -0.0092478 | -0.0045095 | -0.086334 | 0.02411 | 0.016853 | -0.0087009 | -0.020078 | 0.025058 | -0.00023931 | -0.10986 | 0.018311 | -0.073242 | -0.032043 | 0.068665 | -0.086975 | 0.032043 | 0.022888 | 0.11444 | -0.054932 | 0.018311 | 0.10986 | 0.050354 | 0.11444 | 3.1403 | -118.5287 | -118.5791 | 3.2822 | 3.2455 | 3.1265 | 0.10529 | -0.013733 | 3.1586 | -118.4326 | -118.5287 | 3.3234 | 3.3279 | 3.2639 | 0.16937 | 0.10529 | 0.14191 | 0.041199 | 0.16479 | 0.073243 | 0.091553 | 0.16937 | 3.2318 | 3.3279 | -118.6203 | -118.602 | 3.1815 | 3.2318 | 3.1036 | 3.2364
5584.5625 | 121.8933 | -3.1952 | 118.5699 | -0.17372 | -0.041321 | 2.7834e-05 | 0.018664 | -0.0014867 | -0.012666 | -0.0053641 | 0.011322 | 0.021332 | 0.01493 | -0.0099827 | -0.019651 | 0.025912 | -0.0021619 | -0.11902 | 0 | -0.054932 | -0.045776 | 0.059509 | -0.064087 | 0.036621 | 0.009155 | 0.10529 | -0.068665 | 0.018311 | 0.13733 | 0.082397 | 0.11902 | 3.1403 | -118.5699 | -118.6157 | 3.2547 | 3.2318 | 3.1311 | 0.091553 | -0.009155 | 3.1265 | -118.4647 | -118.5516 | 3.3325 | 3.3142 | 3.2776 | 0.18768 | 0.15106 | 0.11444 | 0.009156 | 0.20599 | 0.086976 | 0.054932 | 0.17395 | 3.1952 | 3.3005 | -118.6249 | -118.6386 | 3.1494 | 3.2135 | 3.0762 | 3.2043
5586.2656 | 121.8018 | -3.1952 | 118.5928 | -0.17372 | -0.040039 | -0.00018577 | 0.022082 | -0.0014867 | -0.012666 | -0.0064321 | -0.1077 | 0.023255 | 0.014289 | -0.011478 | -0.021147 | 0.026126 | -0.0042981 | -0.13733 | 0.036621 | -0.091553 | -0.10529 | -0.045776 | -0.16479 | -0.036621 | -0.064087 | 0.11902 | -0.068665 | -0.032043 | 0.027466 | -0.041199 | 0.054932 | 3.1036 | -118.5562 | -118.6981 | 3.1494 | 3.1586 | 3.0304 | 0.054932 | -0.073242 | 3.1265 | -118.4738 | -118.6249 | 3.2227 | 3.2501 | 3.154 | 0.1236 | 0.027466 | 0.045777 | -0.013733 | 0.096131 | 0.036622 | 0.12817 | 0.18768 | 3.2318 | 3.3142 | -118.6844 | -118.6615 | 3.0899 | 3.1631 | 3.0579 | 3.1311
5588.0312 | 121.8521 | -3.2135 | 118.5837 | -0.19661 | -0.041962 | -0.0014676 | 0.019946 | -0.0012731 | -0.010957 | -0.0036551 | -0.028351 | 0.021973 | 0.016639 | -0.014469 | -0.018156 | 0.022922 | -2.571e-05 | -0.07782 | 0.004578 | -0.045776 | -0.009155 | 0.10986 | -0.032043 | 0.064087 | 0.036621 | 0.086975 | -0.064087 | -0.018311 | 0.11444 | 0.059509 | 0.10529 | 3.1677 | -118.5791 | -118.5928 | 3.3234 | 3.2776 | 3.1815 | 0.10986 | 0.013733 | 3.1494 | -118.4967 | -118.602 | 3.3279 | 3.3188 | 3.273 | 0.16937 | 0.1236 | 0.15564 | 0.036621 | 0.17853 | 0.045776 | 0.050354 | 0.15106 | 3.2181 | 3.3005 | -118.6295 | -118.6478 | 3.2043 | 3.1952 | 3.1357 | 3.2501
5589.7969 | 121.9437 | -3.1906 | 118.5379 | -0.25002 | -0.039398 | 0.001523 | 0.020373 | 0.00086307 | -0.011384 | -0.0040823 | -0.052765 | 0.02475 | 0.013435 | -0.010623 | -0.022215 | 0.027408 | -0.0019483 | -0.036621 | -0.013733 | -0.027466 | 0.032043 | 0.11902 | -0.041199 | 0.064087 | 0.09613 | 0.082397 | -0.032043 | 0.07782 | 0.19226 | 0.11902 | 0.16022 | 3.1631 | -118.5516 | -118.5059 | 3.3096 | 3.2547 | 3.1494 | 0.091553 | -0.013733 | 3.1586 | -118.4555 | -118.4601 | 3.3829 | 3.3508 | 3.3096 | 0.19226 | 0.15106 | 0.14649 | 0.059509 | 0.2243 | 0.10986 | 0.013733 | 0.11444 | 3.1769 | 3.273 | -118.5654 | -118.5699 | 3.2227 | 3.2684 | 3.154 | 3.2867
5591.5 | 121.9208 | -3.2227 | 118.5425 | -0.19661 | -0.042816 | 0.00024143 | 0.019732 | 0.00022207 | -0.01352 | -0.0079275 | -0.0039367 | 0.023041 | 0.014076 | -0.017246 | -0.019865 | 0.024631 | -0.0055799 | -0.11444 | -0.004578 | -0.050354 | -0.054932 | 0.059509 | -0.050354 | 0.054932 | 0.009155 | 0.091553 | -0.036621 | 0.018311 | 0.13733 | 0.09613 | 0.12817 | 3.1723 | -118.5471 | -118.5974 | 3.2822 | 3.2776 | 3.1723 | 0.10529 | 0 | 3.186 | -118.4509 | -118.5242 | 3.36 | 3.3508 | 3.3188 | 0.1648 | 0.13275 | 0.10986 | -0.004578 | 0.17395 | 0.054932 | 0.045776 | 0.12817 | 3.2181 | 3.3142 | -118.5928 | -118.5791 | 3.1677 | 3.241 | 3.1082 | 3.2318
5593.2656 | 121.8567 | -3.273 | 118.5333 | -0.18135 | -0.03833 | 0.0013094 | 0.019519 | -0.0021277 | -0.012452 | -0.0042959 | -0.1138 | 0.023469 | 0.018562 | -0.01041 | -0.019865 | 0.026981 | -0.00045291 | -0.14648 | 0.036621 | -0.073242 | -0.09613 | -0.009155 | -0.15106 | -0.027466 | -0.064087 | 0.11444 | -0.059509 | -0.022888 | 0.050354 | -0.009155 | 0.07782 | 3.1998 | -118.4967 | -118.6295 | 3.2639 | 3.2455 | 3.1219 | 0.045776 | -0.07782 | 3.2135 | -118.4189 | -118.5562 | 3.3234 | 3.3508 | 3.2639 | 0.13733 | 0.050354 | 0.064087 | -0.022888 | 0.10986 | 0.036621 | 0.10986 | 0.17395 | 3.3096 | 3.3875 | -118.6066 | -118.5928 | 3.1769 | 3.2501 | 3.1265 | 3.2089
5595.0312 | 121.9666 | -3.2684 | 118.4875 | -0.1432 | -0.042389 | -0.00018577 | 0.018878 | -0.0049047 | -0.013307 | -0.0017325 | 0.0082703 | 0.02176 | 0.015357 | -0.016391 | -0.02136 | 0.02399 | -0.0053661 | -0.073242 | -0.013733 | -0.045776 | 0.045776 | 0.17395 | 0.009155 | 0.09613 | 0.10986 | 0.07782 | -0.041199 | 0.064087 | 0.20142 | 0.16022 | 0.16022 | 3.2227 | -118.5013 | -118.4418 | 3.4424 | 3.3646 | 3.2776 | 0.14191 | 0.054931 | 3.2272 | -118.4097 | -118.4235 | 3.4698 | 3.4286 | 3.4286 | 0.20142 | 0.20142 | 0.21973 | 0.091552 | 0.24262 | 0.10529 | 0.032043 | 0.11902 | 3.2547 | 3.3463 | -118.5333 | -118.5287 | 3.3142 | 3.3325 | 3.1952 | 3.3783
5596.7812 | 121.8887 | -3.3875 | 118.4555 | -0.1432 | -0.043457 | -0.0021084 | 0.021655 | 0.00064947 | -0.013093 | -0.0021597 | -0.064972 | 0.023896 | 0.015144 | -0.011478 | -0.020506 | 0.026553 | -0.0028027 | -0.13275 | 0.022888 | -0.073242 | -0.091553 | -0.022888 | -0.1236 | -0.009155 | -0.054932 | 0.13275 | -0.082397 | -0.027466 | 0.07782 | 0.032043 | 0.09613 | 3.3142 | -118.4326 | -118.5471 | 3.3646 | 3.3783 | 3.2639 | 0.064087 | -0.050354 | 3.3051 | -118.3228 | -118.483 | 3.4653 | 3.4836 | 3.4195 | 0.17853 | 0.11444 | 0.050354 | -0.018311 | 0.16022 | 0.054931 | 0.09613 | 0.21515 | 3.4103 | 3.5202 | -118.5287 | -118.5379 | 3.2959 | 3.36 | 3.2547 | 3.3325
5598.5469 | 121.8796 | -3.392 | 118.4555 | -0.089798 | -0.040039 | -0.00039957 | 0.0208 | -0.0021277 | -0.012452 | -0.0023733 | -0.074127 | 0.02176 | 0.015357 | -0.015964 | -0.020078 | 0.026981 | -0.0013073 | -0.14191 | 0.054932 | -0.091553 | -0.10529 | -0.013733 | -0.10986 | -0.013733 | -0.07782 | 0.14191 | -0.086975 | -0.054932 | 0.073242 | 0 | 0.068665 | 3.3005 | -118.4006 | -118.5608 | 3.3783 | 3.3783 | 3.2822 | 0.07782 | -0.01831 | 3.3051 | -118.3136 | -118.5104 | 3.4653 | 3.4607 | 3.392 | 0.15564 | 0.086975 | 0.07782 | -0.013733 | 0.16022 | 0.032043 | 0.14649 | 0.22888 | 3.447 | 3.5339 | -118.5471 | -118.5425 | 3.2867 | 3.3371 | 3.2501 | 3.3142
5600.3125 | 121.843 | -3.4058 | 118.4555 | -0.13557 | -0.040467 | 0.0017368 | 0.02016 | 0.0010767 | -0.01352 | -0.0040823 | -0.11075 | 0.025178 | 0.015998 | -0.01575 | -0.019224 | 0.02634 | -0.00023931 | -0.13275 | 0.027466 | -0.082397 | -0.09613 | -0.009155 | -0.15106 | -0.045776 | -0.082397 | 0.14191 | -0.068665 | -0.064087 | 0.018311 | -0.045776 | 0.054932 | 3.3234 | -118.428 | -118.5516 | 3.3966 | 3.36 | 3.2547 | 0.036621 | -0.068665 | 3.3371 | -118.3136 | -118.5196 | 3.4241 | 3.4607 | 3.36 | 0.1236 | 0.022889 | 0.073242 | -0.013733 | 0.086976 | 0.004578 | 0.10986 | 0.21057 | 3.4332 | 3.5477 | -118.5379 | -118.5242 | 3.3096 | 3.3417 | 3.273 | 3.3234
5602.0156 | 121.8567 | -3.3829 | 118.483 | -0.11269 | -0.041107 | 0.0010958 | 0.018664 | -0.00084593 | -0.011384 | -0.0040823 | -0.040558 | 0.021973 | 0.014503 | -0.0181 | -0.018583 | 0.025699 | -0.0015209 | -0.10071 | 0.027466 | -0.059509 | -0.054932 | 0.068665 | -0.064087 | 0.036621 | -0.013733 | 0.12817 | -0.068665 | -0.045776 | 0.068665 | 0.022888 | 0.050354 | 3.3234 | -118.4555 | -118.5379 | 3.4515 | 3.4195 | 3.3188 | 0.09613 | -0.004578 | 3.3142 | -118.3548 | -118.5287 | 3.4515 | 3.4332 | 3.4058 | 0.11902 | 0.091553 | 0.12817 | 0.004577 | 0.13733 | 0.022889 | 0.086975 | 0.19684 | 3.4103 | 3.511 | -118.5425 | -118.5516 | 3.3279 | 3.3371 | 3.2822 | 3.3691
5603.7812 | 121.9437 | -3.3188 | 118.4509 | -0.20424 | -0.040039 | 0.00045503 | 0.021441 | -0.00063233 | -0.01053 | -0.0053641 | -0.077179 | 0.02411 | 0.015144 | -0.012332 | -0.021574 | 0.027194 | -0.0034435 | -0.14191 | 0.027466 | -0.073242 | -0.086975 | 0 | -0.13275 | -0.013733 | 0 | 0.13275 | -0.054932 | 0.018311 | 0.10529 | 0.054932 | 0.11902 | 3.2455 | -118.4235 | -118.5379 | 3.3188 | 3.3051 | 3.186 | 0.059509 | -0.059509 | 3.2639 | -118.3182 | -118.4326 | 3.4241 | 3.4378 | 3.3737 | 0.17395 | 0.10986 | 0.073242 | -0.013733 | 0.16022 | 0.073243 | 0.10071 | 0.18768 | 3.3463 | 3.4515 | -118.5242 | -118.5059 | 3.2318 | 3.3371 | 3.1769 | 3.3188
5605.4844 | 121.9986 | -3.3096 | 118.5013 | -0.16609 | -0.041321 | 0.00066863 | 0.019519 | -0.0023413 | -0.011384 | -0.0047231 | 0.014374 | 0.023255 | 0.013648 | -0.014041 | -0.022001 | 0.024417 | -0.00088011 | -0.11444 | 0.013733 | -0.064087 | -0.022888 | 0.11902 | -0.004578 | 0.086975 | 0.091553 | 0.091553 | -0.032043 | 0.059509 | 0.1831 | 0.13733 | 0.16022 | 3.2455 | -118.4875 | -118.5242 | 3.4287 | 3.3966 | 3.3051 | 0.15106 | 0.059509 | 3.2776 | -118.4097 | -118.4418 | 3.4927 | 3.4698 | 3.447 | 0.19226 | 0.16937 | 0.18311 | 0.041199 | 0.21515 | 0.091552 | 0.07782 | 0.1236 | 3.3234 | 3.4012 | -118.5654 | -118.5333 | 3.2867 | 3.3691 | 3.1952 | 3.4012
5607.25 | 121.9208 | -3.3234 | 118.5196 | -0.1432 | -0.04303 | -0.00082677 | 0.018664 | 0.00064947 | -0.012452 | -0.0013051 | -0.0008851 | 0.023896 | 0.018562 | -0.014469 | -0.01901 | 0.024844 | -0.0040845 | -0.073242 | 0 | -0.045776 | 0.013733 | 0.11444 | -0.022888 | 0.07782 | 0.050354 | 0.091553 | -0.041199 | -0.004578 | 0.12817 | 0.064087 | 0.10529 | 3.2776 | -118.5196 | -118.5059 | 3.4378 | 3.4012 | 3.3005 | 0.1236 | 0.022888 | 3.2822 | -118.428 | -118.5242 | 3.4515 | 3.4287 | 3.3875 | 0.14649 | 0.10529 | 0.16022 | 0.059509 | 0.16937 | 0.036621 | 0.045776 | 0.13275 | 3.3234 | 3.4149 | -118.5654 | -118.5608 | 3.3371 | 3.3188 | 3.2501 | 3.3737
5609.0156 | 122.0032 | -3.3051 | 118.5104 | -0.15846 | -0.042389 | -0.00039957 | 0.019519 | 8.47e-06 | -0.012452 | -0.0013051 | -0.016144 | 0.023469 | 0.014076 | -0.0048557 | -0.019438 | 0.027408 | -0.0021619 | -0.073242 | -0.018311 | -0.032043 | 0.036621 | 0.15564 | 0.009155 | 0.09613 | 0.09613 | 0.10529 | -0.032043 | 0.073242 | 0.17853 | 0.13733 | 0.15564 | 3.273 | -118.5287 | -118.4738 | 3.4607 | 3.4012 | 3.3142 | 0.12817 | 0.041198 | 3.273 | -118.4052 | -118.4372 | 3.4836 | 3.4607 | 3.4424 | 0.18768 | 0.16937 | 0.18768 | 0.068664 | 0.21057 | 0.10529 | 0.013732 | 0.13733 | 3.2867 | 3.4103 | -118.5425 | -118.5425 | 3.3417 | 3.3783 | 3.2318 | 3.4012
5610.7188 | 122.0215 | -3.3005 | 118.5196 | -0.23476 | -0.041107 | 0.0030184 | 0.019732 | -0.00084593 | -0.01053 | -0.0045095 | -0.086334 | 0.023682 | 0.013008 | -0.014469 | -0.018583 | 0.026981 | -0.0083569 | -0.050354 | -0.004578 | -0.022888 | 0.018311 | 0.13733 | -0.036621 | 0.068665 | 0.10529 | 0.10071 | -0.013733 | 0.09613 | 0.1831 | 0.11902 | 0.17395 | 3.2776 | -118.5242 | -118.5013 | 3.4378 | 3.3691 | 3.2639 | 0.091553 | -0.013733 | 3.2867 | -118.4189 | -118.4235 | 3.4836 | 3.4744 | 3.4195 | 0.18768 | 0.13275 | 0.16022 | 0.041199 | 0.19684 | 0.10986 | 0.01831 | 0.11444 | 3.2959 | 3.4012 | -118.5425 | -118.5333 | 3.3188 | 3.3966 | 3.2501 | 3.4058
5612.4844 | 121.9757 | -3.3508 | 118.4647 | -0.17372 | -0.039398 | -0.0027494 | 0.019732 | -0.0010595 | -0.012666 | -0.0053641 | -0.022247 | 0.023041 | 0.015998 | -0.019809 | -0.019438 | 0.027408 | -0.0023755 | -0.073242 | -0.009155 | -0.041199 | 0.022888 | 0.13275 | -0.041199 | 0.082397 | 0.07782 | 0.086975 | -0.036621 | 0.036621 | 0.13733 | 0.07782 | 0.13733 | 3.3096 | -118.4738 | -118.4418 | 3.4836 | 3.4332 | 3.3096 | 0.1236 | 0 | 3.3142 | -118.3777 | -118.428 | 3.4882 | 3.4882 | 3.4287 | 0.17395 | 0.11444 | 0.17395 | 0.064087 | 0.17395 | 0.073242 | 0.032044 | 0.1236 | 3.3417 | 3.4378 | -118.5059 | -118.5013 | 3.3737 | 3.3875 | 3.2776 | 3.4287
5614.1875 | 121.962 | -3.4378 | 118.3823 | -0.20424 | -0.041107 | 0.0028048 | 0.021441 | -0.00063233 | -0.011384 | -0.0062185 | -0.049713 | 0.021973 | 0.013862 | -0.0134 | -0.021574 | 0.028262 | -0.0077161 | -0.07782 | -0.004578 | -0.027466 | 0.013733 | 0.14191 | -0.059509 | 0.068665 | 0.09613 | 0.10071 | -0.041199 | 0.050354 | 0.13275 | 0.082397 | 0.12817 | 3.4103 | -118.3868 | -118.3685 | 3.5797 | 3.5065 | 3.3783 | 0.096131 | -0.032043 | 3.3966 | -118.2816 | -118.3319 | 3.5706 | 3.566 | 3.5202 | 0.16937 | 0.1236 | 0.16937 | 0.041199 | 0.17395 | 0.091553 | 0.022888 | 0.14191 | 3.4332 | 3.5385 | -118.4097 | -118.4235 | 3.4515 | 3.4882 | 3.36 | 3.5339
5615.9531 | 121.9849 | -3.4195 | 118.4189 | -0.15846 | -0.039185 | 0.00088223 | 0.016528 | 0.00064947 | -0.013734 | -0.0021597 | -0.025299 | 0.021973 | 0.015785 | -0.0091281 | -0.019651 | 0.026126 | -0.0057935 | -0.073242 | 0 | -0.032043 | 0.032043 | 0.12817 | 0.004578 | 0.09613 | 0.059509 | 0.086975 | -0.045776 | 0.041199 | 0.16022 | 0.11902 | 0.12817 | 3.3875 | -118.4189 | -118.3868 | 3.5477 | 3.5156 | 3.4241 | 0.12817 | 0.036621 | 3.3737 | -118.3319 | -118.3777 | 3.5797 | 3.5477 | 3.5385 | 0.17395 | 0.16479 | 0.16022 | 0.064086 | 0.20599 | 0.086975 | 0.032043 | 0.13275 | 3.4195 | 3.5065 | -118.4509 | -118.4647 | 3.4515 | 3.4607 | 3.3463 | 3.479
5617.6719 | 122.0581 | -3.479 | 118.3319 | -0.15083 | -0.043244 | -0.0014676 | 0.020373 | -0.0031957 | -0.012879 | -0.0030141 | -0.028351 | 0.023682 | 0.014717 | -0.0089145 | -0.019438 | 0.027408 | -0.00066651 | -0.082397 | 0.004578 | -0.036621 | 0.027466 | 0.14191 | 0.013733 | 0.10986 | 0.10986 | 0.10071 | -0.041199 | 0.07782 | 0.20599 | 0.16022 | 0.16479 | 3.4424 | -118.3273 | -118.3044 | 3.6209 | 3.5889 | 3.4927 | 0.14648 | 0.050354 | 3.4378 | -118.2312 | -118.2541 | 3.685 | 3.6438 | 3.6392 | 0.20599 | 0.20142 | 0.17853 | 0.064087 | 0.24719 | 0.11902 | 0.041199 | 0.14191 | 3.4836 | 3.5797 | -118.3685 | -118.3731 | 3.5065 | 3.5568 | 3.3966 | 3.5889
5619.4375 | 122.0535 | -3.479 | 118.3685 | -0.089798 | -0.041748 | -0.0010404 | 0.020373 | -0.0034095 | -0.011598 | -0.0040823 | -0.028351 | 0.020051 | 0.013648 | -0.016605 | -0.01901 | 0.025272 | -0.0049389 | -0.07782 | -0.013733 | -0.036621 | 0.050354 | 0.16022 | 0.018311 | 0.11444 | 0.13733 | 0.07782 | -0.045776 | 0.073242 | 0.21057 | 0.15106 | 0.17395 | 3.4424 | -118.3823 | -118.3182 | 3.6392 | 3.5934 | 3.4973 | 0.15106 | 0.054932 | 3.4332 | -118.2907 | -118.2953 | 3.6896 | 3.653 | 3.6301 | 0.21973 | 0.19684 | 0.19684 | 0.086975 | 0.25635 | 0.11902 | 0.022888 | 0.1236 | 3.4653 | 3.5568 | -118.4052 | -118.4143 | 3.5294 | 3.5522 | 3.4012 | 3.6163
5621.1406 | 121.9437 | -3.4973 | 118.3914 | -0.13557 | -0.04068 | 0.00045503 | 0.021869 | -0.0017005 | -0.01053 | -0.0070731 | -0.1138 | 0.02411 | 0.016639 | -0.011905 | -0.020719 | 0.025272 | -0.0021619 | -0.12817 | 0.054932 | -0.07782 | -0.10071 | -0.013733 | -0.14191 | -0.032043 | -0.050354 | 0.1236 | -0.068665 | -0.018311 | 0.041199 | -0.018311 | 0.073242 | 3.4195 | -118.3365 | -118.4921 | 3.4836 | 3.4653 | 3.3554 | 0.045777 | -0.064087 | 3.4286 | -118.2678 | -118.4097 | 3.5385 | 3.5706 | 3.479 | 0.14191 | 0.050354 | 0.064087 | -0.022888 | 0.10986 | 0.050354 | 0.13275 | 0.19226 | 3.5522 | 3.6209 | -118.4692 | -118.4601 | 3.3966 | 3.479 | 3.3691 | 3.447
5622.9062 | 121.9116 | -3.511 | 118.4235 | -0.12794 | -0.038758 | 0.001523 | 0.022296 | 0.0021447 | -0.010743 | -0.0032277 | -0.13211 | 0.023041 | 0.014289 | -0.0093417 | -0.019865 | 0.02933 | -0.0036573 | -0.1236 | 0.036621 | -0.073242 | -0.091553 | -0.018311 | -0.16479 | -0.054932 | -0.073242 | 0.13275 | -0.082397 | -0.054932 | 0.032043 | -0.041199 | 0.059509 | 3.4378 | -118.3868 | -118.515 | 3.4927 | 3.4561 | 3.3463 | 0.01831 | -0.091553 | 3.4287 | -118.2907 | -118.4784 | 3.5431 | 3.5706 | 3.4698 | 0.14191 | 0.041198 | 0.054931 | -0.018311 | 0.11444 | 0.027465 | 0.10986 | 0.21515 | 3.5477 | 3.6438 | -118.4967 | -118.5059 | 3.4195 | 3.4561 | 3.3875 | 3.4378
5624.6719 | 121.9025 | -3.4744 | 118.428 | -0.15846 | -0.039612 | 0.00066863 | 0.021869 | -0.00020513 | -0.012452 | -0.0045095 | -0.1199 | 0.023255 | 0.01493 | -0.0097689 | -0.018797 | 0.026553 | -0.00088011 | -0.14648 | 0.036621 | -0.086975 | -0.10986 | -0.050354 | -0.16937 | -0.045776 | -0.10529 | 0.13733 | -0.07782 | -0.050354 | 0.027466 | -0.027466 | 0.045776 | 3.3875 | -118.3914 | -118.5379 | 3.4241 | 3.4286 | 3.3051 | 0.041199 | -0.082398 | 3.3966 | -118.2907 | -118.4784 | 3.5019 | 3.5202 | 3.447 | 0.1236 | 0.050354 | 0.036621 | -0.022888 | 0.10529 | 0.027466 | 0.1236 | 0.21515 | 3.511 | 3.6118 | -118.515 | -118.5059 | 3.3646 | 3.4241 | 3.3279 | 3.3691
5626.4375 | 122.0764 | -3.4195 | 118.4235 | -0.17372 | -0.040253 | -0.00018577 | 0.018878 | -0.0027685 | -0.013307 | -0.0049367 | 0.0021667 | 0.02411 | 0.015144 | -0.012973 | -0.017301 | 0.024417 | -0.0066479 | -0.082397 | -0.013733 | -0.064087 | 0.032043 | 0.16479 | 0.018311 | 0.11444 | 0.11902 | 0.07782 | -0.054932 | 0.091553 | 0.21973 | 0.15106 | 0.17395 | 3.3554 | -118.4372 | -118.3914 | 3.5843 | 3.5339 | 3.4378 | 0.17853 | 0.082398 | 3.3646 | -118.3456 | -118.3319 | 3.6392 | 3.5934 | 3.5706 | 0.22888 | 0.20599 | 0.22888 | 0.09613 | 0.27466 | 0.14649 | 0.050354 | 0.13275 | 3.4058 | 3.4973 | -118.4875 | -118.4784 | 3.4515 | 3.511 | 3.3371 | 3.5385
5628.1562 | 121.907 | -3.4744 | 118.4601 | -0.18135 | -0.041107 | 0.0019504 | 0.022937 | 0.00043587 | -0.010957 | -0.0062185 | -0.1199 | 0.023896 | 0.017066 | -0.016605 | -0.018797 | 0.026767 | -0.0053661 | -0.14191 | 0.032043 | -0.091553 | -0.10986 | -0.059509 | -0.16479 | -0.041199 | -0.073242 | 0.11902 | -0.068665 | -0.036621 | 0.032043 | -0.041199 | 0.059509 | 3.3829 | -118.428 | -118.5699 | 3.4149 | 3.4332 | 3.3096 | 0.050354 | -0.073242 | 3.4058 | -118.3411 | -118.4967 | 3.5065 | 3.5339 | 3.4332 | 0.12817 | 0.027466 | 0.032044 | -0.01831 | 0.10071 | 0.032044 | 0.1236 | 0.18768 | 3.5065 | 3.5934 | -118.5516 | -118.5287 | 3.3646 | 3.4378 | 3.3325 | 3.4012
5629.9219 | 122.0627 | -3.4195 | 118.4372 | -0.17372 | -0.041107 | -0.00061317 | 0.016955 | -0.0010595 | -0.012239 | -0.0087819 | 0.0082703 | 0.023469 | 0.016212 | -0.014255 | -0.019651 | 0.024631 | -0.0038709 | -0.09613 | 0.004578 | -0.045776 | 0.018311 | 0.1236 | -0.013733 | 0.09613 | 0.073242 | 0.091553 | -0.041199 | 0.064087 | 0.19684 | 0.14191 | 0.16479 | 3.3737 | -118.4326 | -118.4189 | 3.5431 | 3.5156 | 3.4058 | 0.14191 | 0.032043 | 3.3783 | -118.3456 | -118.3731 | 3.6163 | 3.5843 | 3.5614 | 0.20599 | 0.18311 | 0.16937 | 0.064087 | 0.23804 | 0.10529 | 0.050354 | 0.13275 | 3.4241 | 3.511 | -118.483 | -118.4784 | 3.4378 | 3.4836 | 3.3234 | 3.4927
5631.625 | 121.9894 | -3.4378 | 118.4647 | -0.17372 | -0.038971 | 0.0028048 | 0.020373 | -0.0014867 | -0.01117 | -0.0028005 | -0.11075 | 0.023041 | 0.013862 | -0.011051 | -0.020078 | 0.026981 | -0.0021619 | -0.09613 | 0.027466 | -0.068665 | -0.036621 | 0.059509 | -0.073242 | 0.027466 | 0.018311 | 0.10529 | -0.050354 | 0.004578 | 0.091553 | 0.050354 | 0.09613 | 3.3691 | -118.4372 | -118.5013 | 3.4973 | 3.4653 | 3.3646 | 0.096131 | -0.004577 | 3.3875 | -118.3594 | -118.4601 | 3.5294 | 3.5339 | 3.4882 | 0.14648 | 0.10071 | 0.12817 | 0.032044 | 0.14191 | 0.054932 | 0.096131 | 0.15564 | 3.4653 | 3.5431 | -118.5333 | -118.515 | 3.4012 | 3.4424 | 3.3417 | 3.4561
5633.3906 | 122.0261 | -3.4149 | 118.4235 | -0.18135 | -0.038971 | 0.0013094 | 0.019732 | -0.0017005 | -0.009675 | -0.0045095 | -0.031403 | 0.022187 | 0.015357 | -0.015109 | -0.020078 | 0.024417 | -0.0034435 | -0.086975 | -0.004578 | -0.032043 | 0.013733 | 0.13733 | -0.036621 | 0.07782 | 0.082397 | 0.091553 | -0.050354 | 0.054932 | 0.13275 | 0.082397 | 0.1236 | 3.3829 | -118.428 | -118.4097 | 3.5522 | 3.4927 | 3.3783 | 0.10986 | -0.004578 | 3.3646 | -118.3319 | -118.3685 | 3.5477 | 3.5385 | 3.4973 | 0.17395 | 0.13275 | 0.16937 | 0.045776 | 0.18311 | 0.10529 | 0.027465 | 0.14191 | 3.4103 | 3.5065 | -118.4555 | -118.4738 | 3.4287 | 3.4698 | 3.3279 | 3.4973
5635.1562 | 122.0764 | -3.392 | 118.4326 | -0.24239 | -0.040253 | 0.00024143 | 0.022509 | 0.0025721 | -0.01053 | -0.0030141 | -0.092438 | 0.022614 | 0.015144 | -0.010837 | -0.02136 | 0.02634 | -0.0064343 | -0.09613 | 0.004578 | -0.041199 | -0.004578 | 0.10071 | -0.086975 | 0.050354 | 0.07782 | 0.10071 | -0.050354 | 0.086975 | 0.15564 | 0.09613 | 0.17395 | 3.3508 | -118.428 | -118.4372 | 3.4927 | 3.4424 | 3.3051 | 0.091553 | -0.045776 | 3.3417 | -118.3319 | -118.3456 | 3.5477 | 3.566 | 3.4882 | 0.2243 | 0.14648 | 0.14191 | 0.036621 | 0.20599 | 0.13733 | 0.045777 | 0.15106 | 3.3966 | 3.4927 | -118.4738 | -118.483 | 3.3875 | 3.479 | 3.2959 | 3.4698
5636.8594 | 121.9986 | -3.4653 | 118.4601 | -0.1432 | -0.042389 | -0.0014676 | 0.019519 | -0.0029821 | -0.015016 | -0.0030141 | -0.025299 | 0.022828 | 0.014503 | -0.018741 | -0.022001 | 0.026553 | -0.0070751 | -0.07782 | 0.004578 | -0.022888 | 0.004578 | 0.13275 | -0.004578 | 0.064087 | 0.032043 | 0.10529 | -0.064087 | 0 | 0.13733 | 0.07782 | 0.10529 | 3.4424 | -118.4555 | -118.4555 | 3.598 | 3.5294 | 3.4607 | 0.086975 | 0.01831 | 3.4012 | -118.3548 | -118.4601 | 3.6026 | 3.5706 | 3.5431 | 0.16937 | 0.14191 | 0.15564 | 0.027466 | 0.20142 | 0.064087 | 0.027466 | 0.16937 | 3.4698 | 3.5706 | -118.483 | -118.5242 | 3.4698 | 3.4653 | 3.3875 | 3.4973
5638.6406 | 121.9986 | -3.4515 | 118.4509 | -0.19661 | -0.042389 | -0.00061317 | 0.018023 | -0.0010595 | -0.012666 | -0.0032277 | -0.049713 | 0.022828 | 0.016853 | -0.015537 | -0.021147 | 0.025058 | -0.0019483 | -0.091553 | -0.013733 | -0.050354 | -0.013733 | 0.10071 | -0.022888 | 0.068665 | 0.032043 | 0.11902 | -0.050354 | 0 | 0.11444 | 0.059509 | 0.09613 | 3.4012 | -118.4647 | -118.4647 | 3.5522 | 3.5202 | 3.4287 | 0.11902 | 0.027466 | 3.4012 | -118.3319 | -118.4509 | 3.566 | 3.5477 | 3.511 | 0.14648 | 0.10986 | 0.15106 | 0.036621 | 0.16479 | 0.050354 | 0.036621 | 0.16937 | 3.4378 | 3.5706 | -118.5013 | -118.5013 | 3.4378 | 3.4515 | 3.36 | 3.4836
5640.4219 | 122.0535 | -3.4607 | 118.428 | -0.21187 | -0.041107 | 0.00045503 | 0.018664 | -0.0019141 | -0.012879 | -0.0047231 | -0.022247 | 0.021973 | 0.016426 | -0.017459 | -0.018156 | 0.026553 | -0.0013073 | -0.11902 | 0.004578 | -0.059509 | -0.045776 | 0.068665 | -0.068665 | 0.045776 | 0.018311 | 0.10071 | -0.073242 | 0.022888 | 0.11902 | 0.068665 | 0.11444 | 3.4012 | -118.4235 | -118.4738 | 3.5294 | 3.5065 | 3.392 | 0.10528 | -0.009156 | 3.3875 | -118.3273 | -118.4052 | 3.5797 | 3.5751 | 3.5294 | 0.18768 | 0.14191 | 0.12817 | 0.013733 | 0.19226 | 0.09613 | 0.064087 | 0.17395 | 3.4653 | 3.5614 | -118.4875 | -118.5013 | 3.4149 | 3.4836 | 3.3417 | 3.479
5642.1875 | 122.0901 | -3.4378 | 118.4555 | -0.12794 | -0.043457 | 2.7834e-05 | 0.017596 | -0.0025549 | -0.010957 | -0.0032277 | -0.034454 | 0.021546 | 0.015998 | -0.012119 | -0.022001 | 0.025272 | -0.0053661 | -0.07782 | -0.009155 | -0.041199 | 0.036621 | 0.15564 | 0.022888 | 0.11902 | 0.10071 | 0.07782 | -0.036621 | 0.068665 | 0.20599 | 0.13275 | 0.14191 | 3.3966 | -118.4647 | -118.4189 | 3.5934 | 3.5568 | 3.4607 | 0.16022 | 0.064087 | 3.4012 | -118.3777 | -118.3868 | 3.6438 | 3.5797 | 3.5706 | 0.17853 | 0.16937 | 0.19684 | 0.07782 | 0.24262 | 0.10529 | 0.032044 | 0.11444 | 3.4287 | 3.5156 | -118.4967 | -118.4921 | 3.4744 | 3.5065 | 3.36 | 3.5385
5643.9062 | 122.0444 | -3.4424 | 118.4692 | -0.19661 | -0.042176 | 0.00024143 | 0.019519 | -0.0044775 | -0.012239 | -0.0049367 | -0.037506 | 0.022614 | 0.012367 | -0.011264 | -0.01901 | 0.025058 | -0.0034435 | -0.10986 | 0.004578 | -0.041199 | -0.018311 | 0.068665 | -0.073242 | 0.041199 | 0.013733 | 0.086975 | -0.068665 | 0.018311 | 0.10529 | 0.054932 | 0.11902 | 3.4012 | -118.4647 | -118.4875 | 3.511 | 3.4836 | 3.3691 | 0.082398 | -0.032043 | 3.3737 | -118.3823 | -118.4509 | 3.5477 | 3.5614 | 3.4973 | 0.18768 | 0.1236 | 0.10986 | 0.022888 | 0.17395 | 0.086976 | 0.045777 | 0.15564 | 3.447 | 3.5294 | -118.5104 | -118.5379 | 3.4241 | 3.4607 | 3.3325 | 3.4561
5645.6719 | 121.9757 | -3.4653 | 118.5059 | -0.13557 | -0.043244 | -0.0021084 | 0.019519 | -0.00084593 | -0.014161 | -0.0087819 | -0.064972 | 0.023041 | 0.01728 | -0.0087009 | -0.020933 | 0.026553 | -0.00088011 | -0.12817 | 0.013733 | -0.073242 | -0.073242 | 0.022888 | -0.091553 | 0.004578 | -0.059509 | 0.13733 | -0.068665 | -0.054932 | 0.064087 | 0.013733 | 0.045776 | 3.392 | -118.4921 | -118.5791 | 3.4882 | 3.4698 | 3.3737 | 0.07782 | -0.018311 | 3.3966 | -118.3685 | -118.5608 | 3.5294 | 3.511 | 3.479 | 0.11444 | 0.082398 | 0.09613 | 0 | 0.13275 | 0.013733 | 0.086975 | 0.20599 | 3.479 | 3.6026 | -118.5791 | -118.5745 | 3.392 | 3.4103 | 3.3371 | 3.4058
5647.4375 | 121.994 | -3.4561 | 118.483 | -0.18135 | -0.039185 | -0.00061317 | 0.019305 | 0.0025721 | -0.013734 | -0.0030141 | -0.1138 | 0.025819 | 0.01493 | -0.0082737 | -0.020719 | 0.025699 | -0.0053661 | -0.10071 | 0.018311 | -0.068665 | -0.032043 | 0.045776 | -0.10529 | 0 | 0 | 0.13275 | -0.059509 | 0 | 0.068665 | 0.004578 | 0.073242 | 3.3875 | -118.4647 | -118.515 | 3.5019 | 3.4561 | 3.3508 | 0.068665 | -0.036621 | 3.3966 | -118.3502 | -118.483 | 3.5248 | 3.5294 | 3.4607 | 0.13275 | 0.064087 | 0.11444 | 0.036622 | 0.12817 | 0.059509 | 0.086976 | 0.19226 | 3.4744 | 3.5889 | -118.5516 | -118.5425 | 3.4241 | 3.4561 | 3.3554 | 3.4561
5649.1406 | 122.1039 | -3.4241 | 118.4555 | -0.16609 | -0.039185 | 0.00066863 | 0.022082 | 0.0010767 | -0.010957 | -0.0066457 | -0.06192 | 0.021973 | 0.016212 | -0.0134 | -0.020078 | 0.027621 | -0.0062207 | -0.068665 | 0.004578 | -0.041199 | 0.009155 | 0.10986 | -0.036621 | 0.068665 | 0.082397 | 0.09613 | -0.045776 | 0.09613 | 0.16937 | 0.091553 | 0.17853 | 3.3829 | -118.4509 | -118.4463 | 3.5339 | 3.4927 | 3.3875 | 0.10986 | 0.004578 | 3.3783 | -118.3594 | -118.3594 | 3.5934 | 3.6026 | 3.5156 | 0.2243 | 0.13733 | 0.15106 | 0.050354 | 0.21515 | 0.14191 | 0.045777 | 0.14191 | 3.4286 | 3.5202 | -118.4967 | -118.5013 | 3.4332 | 3.5202 | 3.3554 | 3.5065
5650.9062 | 122.0627 | -3.4149 | 118.4692 | -0.19661 | -0.040039 | 0.0017368 | 0.019946 | -0.0014867 | -0.011811 | -0.0062185 | -0.013092 | 0.020905 | 0.015571 | -0.013187 | -0.018583 | 0.025485 | -0.0049389 | -0.1236 | -0.013733 | -0.032043 | -0.041199 | 0.082397 | -0.073242 | 0.050354 | 0.022888 | 0.091553 | -0.050354 | 0.027466 | 0.12817 | 0.07782 | 0.11902 | 3.3829 | -118.483 | -118.5104 | 3.4973 | 3.4653 | 3.3417 | 0.082397 | -0.041199 | 3.3646 | -118.3777 | -118.4418 | 3.5431 | 3.5339 | 3.4927 | 0.16937 | 0.12817 | 0.11444 | -0.009156 | 0.17853 | 0.07782 | 0.01831 | 0.14191 | 3.4012 | 3.5065 | -118.5013 | -118.5196 | 3.3737 | 3.4424 | 3.2913 | 3.4378
5652.6094 | 121.9849 | -3.5065 | 118.5013 | -0.17372 | -0.039826 | 0.00066863 | 0.023578 | 8.47e-06 | -0.011598 | -0.0057913 | -0.11075 | 0.026673 | 0.015571 | -0.0050693 | -0.020719 | 0.028476 | -0.0049389 | -0.12817 | 0.027466 | -0.086975 | -0.09613 | -0.045776 | -0.17395 | -0.041199 | -0.073242 | 0.11902 | -0.086975 | -0.045776 | 0.013733 | -0.027466 | 0.064087 | 3.4195 | -118.4738 | -118.5974 | 3.4607 | 3.4653 | 3.3325 | 0.045776 | -0.086975 | 3.4195 | -118.3823 | -118.5471 | 3.5202 | 3.5706 | 3.479 | 0.15106 | 0.059509 | 0.041199 | -0.009155 | 0.10071 | 0.041199 | 0.11444 | 0.20599 | 3.5339 | 3.6255 | -118.5883 | -118.5883 | 3.4103 | 3.4607 | 3.3783 | 3.4332
5654.375 | 122.0901 | -3.4241 | 118.5287 | -0.21187 | -0.041962 | 0.0013094 | 0.020373 | 0.00022207 | -0.010743 | -0.0038687 | -0.01004 | 0.023896 | 0.013435 | -0.013614 | -0.019438 | 0.025058 | -0.0042981 | -0.10986 | 0.009155 | -0.050354 | -0.032043 | 0.064087 | -0.082397 | 0.050354 | 0 | 0.09613 | -0.059509 | 0.009155 | 0.12817 | 0.054932 | 0.11902 | 3.3737 | -118.5196 | -118.5608 | 3.4882 | 3.4744 | 3.3417 | 0.10071 | -0.032043 | 3.3646 | -118.4326 | -118.5196 | 3.5522 | 3.5431 | 3.479 | 0.17853 | 0.11444 | 0.11444 | 0.018311 | 0.18768 | 0.068664 | 0.059509 | 0.15564 | 3.4332 | 3.5202 | -118.5791 | -118.5883 | 3.392 | 3.4332 | 3.3142 | 3.4241
5656.125 | 122.0718 | -3.4149 | 118.5013 | -0.28053 | -0.040894 | 0.0010958 | 0.019091 | 0.00022207 | -0.01053 | -0.0053641 | -0.046661 | 0.023682 | 0.014717 | -0.015537 | -0.020719 | 0.02634 | -0.0025891 | -0.086975 | 0 | -0.036621 | 0.004578 | 0.13733 | -0.036621 | 0.068665 | 0.068665 | 0.091553 | -0.059509 | 0.036621 | 0.14191 | 0.091553 | 0.12817 | 3.3783 | -118.5013 | -118.4967 | 3.5522 | 3.4836 | 3.3783 | 0.10529 | 0 | 3.3554 | -118.4097 | -118.4647 | 3.5568 | 3.5431 | 3.5065 | 0.18768 | 0.15106 | 0.17395 | 0.041199 | 0.20142 | 0.09613 | 0.036621 | 0.15106 | 3.4149 | 3.5065 | -118.5379 | -118.5608 | 3.4195 | 3.4515 | 3.3279 | 3.4836
5657.8906 | 122.113 | -3.3875 | 118.5287 | -0.20424 | -0.041321 | 0.00045503 | 0.020373 | -0.0029821 | -0.011811 | -0.0060049 | -0.028351 | 0.02176 | 0.012153 | -0.0095553 | -0.021147 | 0.02399 | -0.0047253 | -0.091553 | -0.032043 | -0.036621 | 0.036621 | 0.15106 | 0.004578 | 0.10529 | 0.086975 | 0.10529 | -0.068665 | 0.064087 | 0.1831 | 0.13275 | 0.14191 | 3.3508 | -118.5608 | -118.4921 | 3.5385 | 3.4927 | 3.392 | 0.14191 | 0.041199 | 3.3188 | -118.4235 | -118.4647 | 3.5706 | 3.5294 | 3.5202 | 0.21057 | 0.20142 | 0.18768 | 0.073242 | 0.25177 | 0.13275 | 0.004578 | 0.17395 | 3.3554 | 3.4927 | -118.5654 | -118.5974 | 3.4241 | 3.4515 | 3.2959 | 3.4744
5659.6562 | 121.9986 | -3.392 | 118.5883 | -0.1432 | -0.037689 | -0.00082677 | 0.021869 | -0.00041873 | -0.010957 | -0.0038687 | -0.13516 | 0.022828 | 0.015571 | -0.0072055 | -0.021147 | 0.028049 | -0.0060071 | -0.13275 | 0.041199 | -0.07782 | -0.10529 | -0.059509 | -0.16479 | -0.059509 | -0.11444 | 0.11902 | -0.086975 | -0.041199 | 0.027466 | -0.050354 | 0.059509 | 3.3142 | -118.5471 | -118.6935 | 3.3325 | 3.3325 | 3.2272 | 0.018311 | -0.086975 | 3.3051 | -118.4692 | -118.6295 | 3.4195 | 3.4515 | 3.3417 | 0.14648 | 0.036621 | 0.018311 | -0.027466 | 0.11444 | 0.045776 | 0.11902 | 0.20599 | 3.4332 | 3.511 | -118.6661 | -118.6752 | 3.2867 | 3.3508 | 3.2593 | 3.2776
5661.3594 | 122.049 | -3.3875 | 118.5791 | -0.16609 | -0.041748 | -0.0014676 | 0.019091 | -0.0012731 | -0.012879 | -0.0068593 | -0.031403 | 0.023469 | 0.014503 | -0.016605 | -0.018369 | 0.025699 | -0.0019483 | -0.091553 | -0.009155 | -0.045776 | -0.004578 | 0.10986 | -0.022888 | 0.068665 | 0.036621 | 0.09613 | -0.064087 | 0 | 0.11902 | 0.07782 | 0.10071 | 3.3417 | -118.5883 | -118.5837 | 3.4973 | 3.4561 | 3.3646 | 0.11444 | 0.022888 | 3.3234 | -118.483 | -118.5791 | 3.5065 | 3.4882 | 3.4653 | 0.1648 | 0.14191 | 0.15564 | 0.041198 | 0.18311 | 0.064087 | 0.036621 | 0.16022 | 3.3783 | 3.4836 | -118.6249 | -118.6432 | 3.3829 | 3.3875 | 3.2959 | 3.4241
5663.1406 | 122.1268 | -3.3325 | 118.5699 | -0.19661 | -0.038117 | 0.0010958 | 0.019519 | 0.00022207 | -0.013093 | -0.0049367 | -0.077179 | 0.023041 | 0.012367 | -0.011051 | -0.019438 | 0.026553 | -0.0042981 | -0.059509 | 0.004578 | -0.036621 | 0.036621 | 0.1236 | -0.045776 | 0.073242 | 0.091553 | 0.07782 | -0.036621 | 0.082397 | 0.17395 | 0.11902 | 0.16937 | 3.2959 | -118.5654 | -118.5333 | 3.4561 | 3.4058 | 3.2867 | 0.10986 | -0.009155 | 3.2959 | -118.4921 | -118.4875 | 3.5065 | 3.5019 | 3.4515 | 0.20599 | 0.15564 | 0.16022 | 0.073242 | 0.21057 | 0.11902 | 0.041199 | 0.11444 | 3.3371 | 3.4103 | -118.6066 | -118.6066 | 3.3691 | 3.4149 | 3.273 | 3.4241
5664.9219 | 122.1634 | -3.3096 | 118.6111 | -0.20424 | -0.042389 | 0.00024143 | 0.016742 | -0.00020513 | -0.01117 | -0.0060049 | -0.0069885 | 0.020692 | 0.014289 | -0.017459 | -0.018369 | 0.02399 | -0.0025891 | -0.09613 | -0.013733 | -0.045776 | 0.013733 | 0.14191 | 0.009155 | 0.11444 | 0.10071 | 0.09613 | -0.050354 | 0.086975 | 0.21057 | 0.15564 | 0.15564 | 3.2639 | -118.6249 | -118.5974 | 3.4515 | 3.4241 | 3.3188 | 0.16022 | 0.054931 | 3.2593 | -118.515 | -118.5242 | 3.5202 | 3.4653 | 3.4653 | 0.20599 | 0.20599 | 0.18768 | 0.059509 | 0.26093 | 0.13733 | 0.032043 | 0.14648 | 3.2959 | 3.4058 | -118.6569 | -118.6615 | 3.3234 | 3.3966 | 3.2135 | 3.4103
5666.6406 | 122.1588 | -3.3051 | 118.6386 | -0.19661 | -0.037689 | 0.00045503 | 0.019946 | 0.0064173 | -0.009675 | -0.0068593 | -0.083283 | 0.025391 | 0.015998 | -0.013828 | -0.020506 | 0.027194 | -0.0066479 | -0.050354 | -0.022888 | -0.050354 | 0.018311 | 0.11444 | -0.036621 | 0.068665 | 0.10071 | 0.082397 | -0.027466 | 0.082397 | 0.17395 | 0.10529 | 0.16022 | 3.2547 | -118.6615 | -118.6203 | 3.4195 | 3.3737 | 3.2684 | 0.11902 | 0.013733 | 3.2776 | -118.5562 | -118.5562 | 3.479 | 3.4653 | 3.4103 | 0.18768 | 0.13275 | 0.16479 | 0.068665 | 0.20142 | 0.10986 | 0.027466 | 0.10986 | 3.2822 | 3.3875 | -118.689 | -118.6661 | 3.3234 | 3.3875 | 3.2547 | 3.4058
5668.4062 | 122.1359 | -3.2913 | 118.6478 | -0.15846 | -0.041535 | 0.00024143 | 0.019946 | -0.0046911 | -0.01053 | -0.0047231 | -0.037506 | 0.021546 | 0.015357 | -0.01041 | -0.017515 | 0.023776 | 0.0012561 | -0.11444 | 0.009155 | -0.050354 | -0.027466 | 0.054932 | -0.054932 | 0.054932 | 0.027466 | 0.10529 | -0.059509 | 0.032043 | 0.14648 | 0.086975 | 0.13733 | 3.241 | -118.6386 | -118.6752 | 3.3463 | 3.3463 | 3.2364 | 0.10529 | -0.004578 | 3.2318 | -118.5425 | -118.6157 | 3.4378 | 3.4286 | 3.3783 | 0.19684 | 0.14648 | 0.10529 | 0.022888 | 0.20599 | 0.091552 | 0.059509 | 0.16479 | 3.3005 | 3.3966 | -118.6981 | -118.7073 | 3.2639 | 3.3234 | 3.1769 | 3.3188
5670.1719 | 122.0261 | -3.4103 | 118.6249 | -0.17372 | -0.042816 | -0.00061317 | 0.019519 | -0.0023413 | -0.012666 | -0.0055777 | -0.06192 | 0.022187 | 0.015571 | -0.015323 | -0.021787 | 0.02634 | -0.0034435 | -0.15106 | 0.041199 | -0.082397 | -0.086975 | 0 | -0.10986 | -0.009155 | -0.064087 | 0.14648 | -0.07782 | -0.064087 | 0.050354 | 0 | 0.054932 | 3.3279 | -118.5837 | -118.7119 | 3.4103 | 3.4012 | 3.3005 | 0.073242 | -0.027466 | 3.3325 | -118.4784 | -118.689 | 3.4607 | 3.4653 | 3.4103 | 0.13275 | 0.07782 | 0.082397 | -0.004578 | 0.12817 | 0.013733 | 0.1236 | 0.2243 | 3.4515 | 3.5568 | -118.7073 | -118.7027 | 3.3234 | 3.3463 | 3.2593 | 3.3463
5671.9219 | 122.0444 | -3.3463 | 118.6935 | -0.13557 | -0.040894 | -0.001254 | 0.018237 | -0.00020513 | -0.011598 | -0.0045095 | -0.064972 | 0.023255 | 0.014076 | -0.0080601 | -0.018583 | 0.027408 | -0.0023755 | -0.091553 | 0.022888 | -0.064087 | -0.045776 | 0.041199 | -0.068665 | 0.018311 | -0.032043 | 0.1236 | -0.073242 | -0.036621 | 0.073242 | 0.004578 | 0.054932 | 3.2822 | -118.6707 | -118.7393 | 3.3875 | 3.3646 | 3.2776 | 0.082398 | -0.004578 | 3.273 | -118.5699 | -118.7302 | 3.4195 | 3.4012 | 3.3508 | 0.12817 | 0.07782 | 0.10529 | 0.018311 | 0.14648 | 0.036621 | 0.086975 | 0.19684 | 3.3691 | 3.4698 | -118.7576 | -118.7668 | 3.3005 | 3.3096 | 3.2547 | 3.3142
5673.625 | 122.081 | -3.3279 | 118.6386 | -0.20424 | -0.039826 | -0.0010404 | 0.022937 | -0.00084593 | -0.012452 | -0.0070731 | -0.10464 | 0.021973 | 0.01493 | -0.0076327 | -0.02136 | 0.027621 | -0.0028027 | -0.13733 | 0.032043 | -0.082397 | -0.091553 | 0 | -0.15564 | -0.018311 | -0.041199 | 0.086975 | -0.064087 | 0.004578 | 0.07782 | 0.009155 | 0.09613 | 3.2455 | -118.6066 | -118.7302 | 3.3279 | 3.3096 | 3.1723 | 0.064086 | -0.073243 | 3.2639 | -118.5516 | -118.634 | 3.4058 | 3.4241 | 3.3371 | 0.16022 | 0.073242 | 0.082397 | -0.009156 | 0.14191 | 0.068665 | 0.11444 | 0.15106 | 3.36 | 3.4149 | -118.721 | -118.7027 | 3.2364 | 3.3325 | 3.1906 | 3.2867
5675.3906 | 122.1588 | -3.3188 | 118.6478 | -0.16609 | -0.041748 | 0.00066863 | 0.020373 | 0.00022207 | -0.013093 | -0.0075003 | -0.025299 | 0.02176 | 0.015571 | -0.010196 | -0.019224 | 0.026553 | -0.00066651 | -0.082397 | -0.018311 | -0.054932 | 0.032043 | 0.14648 | 0.009155 | 0.10071 | 0.091553 | 0.10071 | -0.032043 | 0.068665 | 0.18768 | 0.14191 | 0.14648 | 3.2639 | -118.6661 | -118.6157 | 3.4653 | 3.4195 | 3.3279 | 0.15564 | 0.064087 | 3.2867 | -118.5471 | -118.5791 | 3.5065 | 3.4653 | 3.4607 | 0.17853 | 0.17395 | 0.20142 | 0.086975 | 0.21973 | 0.10071 | 0.036621 | 0.13275 | 3.3005 | 3.4195 | -118.7027 | -118.6798 | 3.3508 | 3.3875 | 3.2364 | 3.4103
5677.1406 | 122.0444 | -3.2135 | 118.8217 | -0.15083 | -0.042389 | -0.00061317 | 0.018451 | -0.0031957 | -0.01352 | -0.0023733 | -0.04361 | 0.021973 | 0.01728 | -0.0095553 | -0.020078 | 0.02634 | -0.0023755 | -0.086975 | 0.004578 | -0.054932 | -0.032043 | 0.073242 | -0.054932 | 0.022888 | -0.032043 | 0.11902 | -0.068665 | -0.045776 | 0.082397 | 0.013733 | 0.059509 | 3.1586 | -118.8171 | -118.8538 | 3.2867 | 3.2364 | 3.1586 | 0.07782 | 0 | 3.1448 | -118.7027 | -118.8675 | 3.2959 | 3.273 | 3.2272 | 0.12817 | 0.082398 | 0.12817 | 0.022889 | 0.15106 | 0.022889 | 0.05951 | 0.18768 | 3.2181 | 3.3325 | -118.8766 | -118.8904 | 3.1815 | 3.1677 | 3.1265 | 3.1815
5678.9062 | 122.1634 | -3.1677 | 118.7805 | -0.20424 | -0.040039 | 0.0030184 | 0.023578 | -0.0040503 | -0.012452 | -0.0062185 | -0.074127 | 0.023469 | 0.015357 | -0.013614 | -0.020933 | 0.02634 | -0.0036573 | -0.068665 | 0 | -0.050354 | 0.018311 | 0.11902 | -0.045776 | 0.064087 | 0.07782 | 0.09613 | -0.041199 | 0.091553 | 0.16479 | 0.10071 | 0.1831 | 3.1174 | -118.7805 | -118.7622 | 3.2867 | 3.2318 | 3.1219 | 0.11444 | 0.004578 | 3.1265 | -118.6844 | -118.689 | 3.3325 | 3.3508 | 3.2684 | 0.2243 | 0.14191 | 0.16937 | 0.068665 | 0.20599 | 0.13275 | 0.050354 | 0.13733 | 3.1677 | 3.2639 | -118.8309 | -118.8217 | 3.186 | 3.2593 | 3.0991 | 3.2455
5680.6719 | 122.081 | -3.2227 | 118.8034 | -0.11269 | -0.038758 | 2.7834e-05 | 0.022723 | 0.0027857 | -0.012666 | -0.0045095 | -0.11075 | 0.024323 | 0.01493 | -0.01276 | -0.019438 | 0.02933 | -0.0021619 | -0.12817 | 0.018311 | -0.054932 | -0.045776 | 0.022888 | -0.086975 | 0.013733 | -0.022888 | 0.1236 | -0.073242 | 0.009155 | 0.10071 | 0.045776 | 0.10071 | 3.1677 | -118.7851 | -118.8492 | 3.2455 | 3.2364 | 3.1357 | 0.068665 | -0.032043 | 3.1494 | -118.6798 | -118.7943 | 3.3234 | 3.3234 | 3.2684 | 0.17395 | 0.11902 | 0.07782 | 0.009156 | 0.17395 | 0.082397 | 0.073243 | 0.19684 | 3.241 | 3.3463 | -118.8583 | -118.8766 | 3.1769 | 3.2318 | 3.0945 | 3.1998
5682.4375 | 122.1176 | -3.2043 | 118.7988 | -0.17372 | -0.040467 | 0.00024143 | 0.023364 | -0.00020513 | -0.012879 | -0.0057913 | -0.10464 | 0.022401 | 0.015144 | -0.0099827 | -0.019224 | 0.026981 | -0.0060071 | -0.12817 | 0.022888 | -0.064087 | -0.082397 | 0 | -0.15106 | -0.013733 | -0.009155 | 0.10529 | -0.07782 | 0.022888 | 0.09613 | 0.022888 | 0.10071 | 3.1403 | -118.7759 | -118.8812 | 3.2043 | 3.1906 | 3.0533 | 0.050354 | -0.086975 | 3.1265 | -118.6935 | -118.7759 | 3.3005 | 3.3051 | 3.2272 | 0.17853 | 0.10071 | 0.064087 | -0.01831 | 0.17395 | 0.10071 | 0.086975 | 0.18311 | 3.2272 | 3.3096 | -118.8629 | -118.8766 | 3.1219 | 3.2272 | 3.0762 | 3.1952
5684.1562 | 122.0947 | -3.2318 | 118.8171 | -0.18898 | -0.04303 | 0.00045503 | 0.018878 | -0.0021277 | -0.01352 | -0.0072867 | -0.0039367 | 0.02475 | 0.014076 | -0.021305 | -0.018156 | 0.024204 | -0.0079297 | -0.07782 | 0.004578 | -0.036621 | 0 | 0.10071 | -0.018311 | 0.068665 | 0.004578 | 0.10071 | -0.068665 | -0.027466 | 0.09613 | 0.050354 | 0.10071 | 3.1952 | -118.8126 | -118.8171 | 3.3325 | 3.3005 | 3.2135 | 0.10529 | 0.01831 | 3.1631 | -118.7164 | -118.8446 | 3.3279 | 3.3325 | 3.2822 | 0.16937 | 0.11902 | 0.13733 | 0.036621 | 0.16479 | 0.041199 | 0.041199 | 0.16937 | 3.2364 | 3.3325 | -118.8538 | -118.8858 | 3.2318 | 3.2043 | 3.154 | 3.2364
5685.9062 | 122.0993 | -3.2181 | 118.8263 | -0.17372 | -0.040467 | -0.0010404 | 0.02315 | 0.0044947 | -0.013734 | -0.0070731 | -0.10464 | 0.022614 | 0.015144 | -0.0080601 | -0.018797 | 0.025912 | -0.0045117 | -0.082397 | 0.013733 | -0.068665 | -0.036621 | 0.068665 | -0.07782 | 0.013733 | 0.027466 | 0.10986 | -0.054932 | -0.004578 | 0.09613 | 0.018311 | 0.10529 | 3.1494 | -118.8126 | -118.8629 | 3.2867 | 3.2318 | 3.1403 | 0.082398 | -0.009155 | 3.1631 | -118.7164 | -118.8309 | 3.3142 | 3.3234 | 3.2364 | 0.16022 | 0.073243 | 0.13733 | 0.032044 | 0.15106 | 0.050354 | 0.082398 | 0.16479 | 3.2318 | 3.3279 | -118.895 | -118.8812 | 3.1815 | 3.2135 | 3.1357 | 3.2455
5687.6719 | 122.1451 | -3.1906 | 118.8217 | -0.19661 | -0.042603 | -0.0014676 | 0.01781 | -0.0046911 | -0.01117 | -0.0072867 | 0.0021667 | 0.023896 | 0.016426 | -0.014041 | -0.016874 | 0.02399 | -0.0038709 | -0.11902 | 0 | -0.050354 | -0.032043 | 0.073242 | -0.068665 | 0.045776 | 0.004578 | 0.091553 | -0.059509 | 0.004578 | 0.11902 | 0.064087 | 0.11444 | 3.1403 | -118.8217 | -118.8538 | 3.2639 | 3.2364 | 3.1219 | 0.09613 | -0.018311 | 3.1311 | -118.7302 | -118.8171 | 3.3096 | 3.3051 | 3.2547 | 0.17395 | 0.1236 | 0.1236 | 0.018311 | 0.17853 | 0.064087 | 0.050354 | 0.15106 | 3.1906 | 3.2822 | -118.8721 | -118.8812 | 3.1586 | 3.1952 | 3.0716 | 3.1952
5689.375 | 122.1222 | -3.1815 | 118.8309 | -0.18898 | -0.039185 | 0.0017368 | 0.019946 | 0.0027857 | -0.010102 | -0.0051505 | -0.09549 | 0.022614 | 0.016639 | -0.015109 | -0.01901 | 0.026767 | -2.571e-05 | -0.13275 | 0.032043 | -0.068665 | -0.07782 | 0.013733 | -0.12817 | -0.013733 | -0.004578 | 0.10986 | -0.059509 | 0.018311 | 0.10529 | 0.032043 | 0.11902 | 3.1128 | -118.7988 | -118.9087 | 3.1952 | 3.1677 | 3.0533 | 0.054932 | -0.059509 | 3.1219 | -118.721 | -118.8126 | 3.2867 | 3.3005 | 3.2135 | 0.17853 | 0.091552 | 0.082398 | -0.009155 | 0.16479 | 0.07782 | 0.10071 | 0.16937 | 3.2135 | 3.2913 | -118.8995 | -118.8904 | 3.1036 | 3.1998 | 3.0487 | 3.1769
5691.1406 | 122.1222 | -3.3005 | 118.7759 | -0.18135 | -0.040894 | 0.00045503 | 0.019519 | 0.0055627 | -0.012879 | -0.0051505 | -0.10464 | 0.024964 | 0.01728 | -0.011264 | -0.020078 | 0.025485 | -0.0017347 | -0.091553 | 0.022888 | -0.064087 | -0.022888 | 0.064087 | -0.07782 | 0.013733 | 0.013733 | 0.13733 | -0.064087 | 0.004578 | 0.10529 | 0.054932 | 0.10986 | 3.2364 | -118.7531 | -118.7988 | 3.3646 | 3.3142 | 3.2227 | 0.07782 | -0.013733 | 3.2364 | -118.6386 | -118.7714 | 3.4058 | 3.4103 | 3.3554 | 0.17395 | 0.11902 | 0.12817 | 0.041199 | 0.16937 | 0.068665 | 0.086975 | 0.20142 | 3.3234 | 3.4378 | -118.84 | -118.84 | 3.2776 | 3.3051 | 3.2089 | 3.3142
5692.8438 | 122.081 | -3.2867 | 118.7897 | -0.12032 | -0.041321 | -0.0025358 | 0.018878 | -0.0025549 | -0.012879 | -0.0051505 | -0.06192 | 0.022401 | 0.016212 | -0.015109 | -0.019438 | 0.025485 | 0.0012561 | -0.15564 | 0.041199 | -0.086975 | -0.1236 | -0.013733 | -0.11444 | -0.013733 | -0.068665 | 0.1236 | -0.091553 | -0.059509 | 0.054932 | -0.009155 | 0.059509 | 3.1998 | -118.7485 | -118.9133 | 3.273 | 3.273 | 3.1723 | 0.073242 | -0.027466 | 3.1952 | -118.6661 | -118.8492 | 3.3417 | 3.3463 | 3.2776 | 0.15106 | 0.082398 | 0.073242 | -0.036621 | 0.14649 | 0.032044 | 0.12817 | 0.21515 | 3.3279 | 3.4103 | -118.8766 | -118.8812 | 3.1631 | 3.2272 | 3.1311 | 3.2181
5694.6094 | 122.1542 | -3.2272 | 118.7988 | -0.18898 | -0.041107 | -0.0018948 | 0.018451 | -0.00041873 | -0.013307 | -0.0087819 | 0.011322 | 0.023469 | 0.015571 | -0.010623 | -0.021574 | 0.024204 | -0.0021619 | -0.11444 | 0.004578 | -0.050354 | -0.045776 | 0.068665 | -0.07782 | 0.027466 | 0 | 0.086975 | -0.054932 | 0.004578 | 0.11444 | 0.068665 | 0.11902 | 3.1769 | -118.7943 | -118.8446 | 3.2959 | 3.2547 | 3.1494 | 0.07782 | -0.027466 | 3.1723 | -118.7119 | -118.7943 | 3.3417 | 3.3463 | 3.2959 | 0.17395 | 0.1236 | 0.11902 | 0.004578 | 0.16937 | 0.05951 | 0.054932 | 0.14191 | 3.2318 | 3.3142 | -118.8492 | -118.8538 | 3.1815 | 3.2318 | 3.1128 | 3.2272
5696.375 | 122.1588 | -3.2181 | 118.8263 | -0.15846 | -0.040894 | 0.00066863 | 0.017596 | -0.0031957 | -0.011811 | -0.0057913 | -0.04361 | 0.02176 | 0.012153 | -0.016818 | -0.018156 | 0.024844 | -0.0045117 | -0.09613 | -0.009155 | -0.036621 | -0.009155 | 0.10529 | -0.068665 | 0.068665 | 0.013733 | 0.091553 | -0.054932 | 0.022888 | 0.13275 | 0.064087 | 0.11902 | 3.1815 | -118.8354 | -118.8354 | 3.3234 | 3.2867 | 3.1494 | 0.10529 | -0.032044 | 3.1631 | -118.7347 | -118.8034 | 3.3508 | 3.3371 | 3.2822 | 0.17395 | 0.11902 | 0.14191 | 0.027466 | 0.18768 | 0.07782 | 0.027466 | 0.14649 | 3.2089 | 3.3096 | -118.8629 | -118.8812 | 3.2089 | 3.241 | 3.1219 | 3.2318
5698.1562 | 122.2229 | -3.1906 | 118.8126 | -0.2195 | -0.038117 | 0.00088223 | 0.021441 | 0.0019311 | -0.011384 | -0.0028005 | -0.055817 | 0.023255 | 0.015144 | -0.0074191 | -0.02136 | 0.026981 | -0.0028027 | -0.050354 | -0.004578 | -0.022888 | 0.036621 | 0.1236 | -0.036621 | 0.068665 | 0.086975 | 0.086975 | -0.041199 | 0.07782 | 0.1831 | 0.09613 | 0.16937 | 3.1677 | -118.8171 | -118.7759 | 3.3142 | 3.2593 | 3.154 | 0.091553 | -0.013733 | 3.1494 | -118.7256 | -118.7347 | 3.3737 | 3.36 | 3.2867 | 0.21057 | 0.13733 | 0.14648 | 0.059509 | 0.2243 | 0.11902 | 0.01831 | 0.12817 | 3.186 | 3.2776 | -118.8354 | -118.8538 | 3.2272 | 3.2684 | 3.1403 | 3.2776
5699.875 | 122.1085 | -3.2364 | 118.8538 | -0.15083 | -0.040467 | 2.7834e-05 | 0.021655 | -0.00041873 | -0.011811 | -0.0057913 | -0.092438 | 0.023682 | 0.013862 | -0.017887 | -0.020719 | 0.028262 | -0.0034435 | -0.12817 | 0.027466 | -0.073242 | -0.10986 | -0.027466 | -0.15564 | -0.032043 | -0.064087 | 0.1236 | -0.082397 | -0.041199 | 0.036621 | -0.022888 | 0.073242 | 3.1631 | -118.8263 | -118.9636 | 3.2089 | 3.2043 | 3.0807 | 0.041199 | -0.082398 | 3.154 | -118.7302 | -118.895 | 3.273 | 3.3096 | 3.2135 | 0.15564 | 0.059509 | 0.045776 | -0.036621 | 0.11902 | 0.041198 | 0.10071 | 0.20599 | 3.2639 | 3.36 | -118.927 | -118.9362 | 3.1265 | 3.1952 | 3.1082 | 3.1723
5701.6406 | 122.2275 | -3.1128 | 118.9041 | -0.1432 | -0.042816 | 2.7834e-05 | 0.018878 | -0.0010595 | -0.012025 | -0.0053641 | -0.01004 | 0.021546 | 0.014717 | -0.0095553 | -0.01901 | 0.025058 | -0.0030163 | -0.09613 | -0.013733 | -0.050354 | 0 | 0.10529 | -0.013733 | 0.091553 | 0.082397 | 0.086975 | -0.041199 | 0.054932 | 0.19226 | 0.13275 | 0.16479 | 3.0624 | -118.9178 | -118.9041 | 3.2181 | 3.2043 | 3.0991 | 0.14191 | 0.036621 | 3.0716 | -118.8171 | -118.8492 | 3.3051 | 3.2776 | 3.2455 | 0.20599 | 0.17395 | 0.15564 | 0.050354 | 0.23346 | 0.096131 | 0.036621 | 0.12817 | 3.0991 | 3.1998 | -118.9545 | -118.9453 | 3.1128 | 3.1677 | 3.0167 | 3.1952
5703.4062 | 122.1405 | -3.1815 | 118.8721 | -0.18135 | -0.039612 | -0.00018577 | 0.021014 | 0.00022207 | -0.015016 | -0.0057913 | -0.1077 | 0.025178 | 0.014503 | -0.010196 | -0.019651 | 0.027408 | -0.0028027 | -0.091553 | 0.032043 | -0.064087 | -0.041199 | 0.050354 | -0.082397 | 0.013733 | 0.027466 | 0.091553 | -0.068665 | 0.009155 | 0.10529 | 0.041199 | 0.10986 | 3.1174 | -118.84 | -118.9133 | 3.2318 | 3.1952 | 3.0991 | 0.07782 | -0.01831 | 3.1128 | -118.7805 | -118.8629 | 3.2867 | 3.2913 | 3.2227 | 0.17853 | 0.10986 | 0.11444 | 0.022888 | 0.17395 | 0.07782 | 0.09613 | 0.16022 | 3.2135 | 3.273 | -118.9362 | -118.9407 | 3.1403 | 3.1906 | 3.0899 | 3.2089
5705.1094 | 122.081 | -3.1586 | 118.9453 | -0.2195 | -0.041748 | 0.00045503 | 0.021441 | 0.0027857 | -0.012239 | -0.0060049 | -0.11075 | 0.023896 | 0.014503 | -0.0057101 | -0.020506 | 0.026767 | -0.0021619 | -0.11444 | 0.041199 | -0.068665 | -0.073242 | 0.022888 | -0.11902 | -0.009155 | -0.027466 | 0.14191 | -0.059509 | -0.036621 | 0.032043 | -0.041199 | 0.045776 | 3.0899 | -118.9041 | -119.0186 | 3.1815 | 3.1494 | 3.0395 | 0.05951 | -0.050354 | 3.0991 | -118.8034 | -118.9819 | 3.1906 | 3.2043 | 3.1174 | 0.10528 | 0.01831 | 0.091553 | -0.004577 | 0.091552 | 0.022888 | 0.10986 | 0.20142 | 3.1998 | 3.3005 | -119.014 | -119.0048 | 3.0853 | 3.1219 | 3.0441 | 3.1311
5706.875 | 122.1497 | -3.1586 | 118.9133 | -0.22713 | -0.039826 | 0.0030184 | 0.021441 | 8.47e-06 | -0.011598 | -0.0055777 | -0.074127 | 0.023255 | 0.017921 | -0.011051 | -0.020506 | 0.028049 | -0.0045117 | -0.13733 | 0.018311 | -0.068665 | -0.082397 | 0.009155 | -0.15564 | -0.022888 | -0.022888 | 0.11902 | -0.07782 | 0 | 0.073242 | 0.022888 | 0.10529 | 3.0899 | -118.895 | -118.9957 | 3.1677 | 3.1357 | 3.0029 | 0.045777 | -0.086975 | 3.0807 | -118.7943 | -118.9133 | 3.2318 | 3.2639 | 3.1815 | 0.18311 | 0.10071 | 0.07782 | -0.013732 | 0.15106 | 0.07782 | 0.086976 | 0.19684 | 3.1769 | 3.2776 | -118.9819 | -118.9911 | 3.0762 | 3.1586 | 3.0212 | 3.1357
5708.5781 | 122.0993 | -3.1677 | 118.927 | -0.13557 | -0.042603 | -0.0031766 | 0.019091 | 0.0032129 | -0.013093 | -0.0053641 | -0.052765 | 0.023469 | 0.015357 | -0.016818 | -0.020078 | 0.025699 | -0.0032299 | -0.14648 | 0.018311 | -0.07782 | -0.10529 | -0.009155 | -0.10529 | -0.009155 | -0.073242 | 0.1236 | -0.07782 | -0.082397 | 0.045776 | -0.009155 | 0.045776 | 3.0899 | -118.9087 | -119.0323 | 3.1586 | 3.1586 | 3.0624 | 0.068665 | -0.027466 | 3.0899 | -118.8034 | -119.0094 | 3.2135 | 3.2135 | 3.1586 | 0.1236 | 0.068665 | 0.068665 | -0.027466 | 0.1236 | -0.004577 | 0.096131 | 0.20142 | 3.186 | 3.2913 | -119.0048 | -119.0048 | 3.0624 | 3.0853 | 3.0212 | 3.0945
5710.3438 | 122.1039 | -3.1586 | 118.9362 | -0.13557 | -0.041535 | -0.00039957 | 0.021869 | 0.0015039 | -0.013947 | -0.0045095 | -0.12296 | 0.023682 | 0.015785 | -0.0082737 | -0.019438 | 0.026981 | -0.0060071 | -0.13733 | 0.032043 | -0.082397 | -0.10529 | -0.027466 | -0.16479 | -0.036621 | -0.09613 | 0.12817 | -0.073242 | -0.045776 | 0.018311 | -0.032043 | 0.059509 | 3.0762 | -118.9041 | -119.0414 | 3.1311 | 3.1219 | 2.9938 | 0.045776 | -0.082398 | 3.0853 | -118.808 | -118.9819 | 3.1769 | 3.2181 | 3.1265 | 0.13275 | 0.041199 | 0.054931 | -0.022889 | 0.091553 | 0.027466 | 0.11444 | 0.20142 | 3.1906 | 3.2867 | -119.0186 | -119.0094 | 3.0533 | 3.1128 | 3.0212 | 3.0624
5712.0469 | 122.1542 | -3.1769 | 118.9041 | -0.21187 | -0.040894 | 0.0013094 | 0.017596 | -0.0021277 | -0.012239 | -0.0040823 | -0.0008851 | 0.023682 | 0.015785 | -0.0093417 | -0.019438 | 0.025485 | -0.0057935 | -0.082397 | -0.004578 | -0.054932 | -0.013733 | 0.10529 | -0.018311 | 0.068665 | 0.032043 | 0.10986 | -0.059509 | -0.022888 | 0.11444 | 0.045776 | 0.07782 | 3.1219 | -118.9087 | -118.9178 | 3.2822 | 3.2455 | 3.1586 | 0.1236 | 0.036621 | 3.1174 | -118.7943 | -118.927 | 3.2913 | 3.2547 | 3.2227 | 0.13733 | 0.10528 | 0.16022 | 0.041199 | 0.17395 | 0.036621 | 0.050354 | 0.16937 | 3.1723 | 3.2867 | -118.959 | -118.9636 | 3.1631 | 3.154 | 3.0945 | 3.2089
5713.7969 | 122.1085 | -3.2043 | 118.8995 | -0.13557 | -0.040467 | 0.00024143 | 0.021869 | -0.00020513 | -0.012239 | -0.0042959 | -0.11075 | 0.023255 | 0.014717 | -0.01041 | -0.019438 | 0.026126 | -0.0019483 | -0.091553 | 0.032043 | -0.064087 | -0.041199 | 0.054932 | -0.10529 | 0 | 0 | 0.12817 | -0.086975 | -0.022888 | 0.064087 | -0.004578 | 0.068665 | 3.1403 | -118.8675 | -118.9407 | 3.2593 | 3.2043 | 3.0991 | 0.064087 | -0.041199 | 3.1174 | -118.7714 | -118.9224 | 3.2684 | 3.273 | 3.1998 | 0.15564 | 0.082397 | 0.11902 | 0.022888 | 0.15106 | 0.064087 | 0.09613 | 0.21515 | 3.2364 | 3.3325 | -118.9636 | -118.9865 | 3.1631 | 3.1815 | 3.1128 | 3.2043
5715.5781 | 122.1588 | -3.2364 | 118.84 | -0.20424 | -0.039398 | 0.0010958 | 0.020373 | 0.0044947 | -0.010743 | -0.0042959 | -0.074127 | 0.023469 | 0.015571 | -0.011264 | -0.019865 | 0.025485 | -0.0047253 | -0.10071 | 0.032043 | -0.073242 | -0.050354 | 0.064087 | -0.064087 | 0.036621 | 0.022888 | 0.1236 | -0.07782 | 0.004578 | 0.086975 | 0.050354 | 0.10986 | 3.1631 | -118.808 | -118.8904 | 3.3005 | 3.273 | 3.1723 | 0.10986 | 0.009155 | 3.1586 | -118.7164 | -118.8354 | 3.3234 | 3.3463 | 3.2867 | 0.18768 | 0.12817 | 0.13733 | 0.022888 | 0.16479 | 0.082398 | 0.10529 | 0.20142 | 3.2684 | 3.36 | -118.9133 | -118.9178 | 3.186 | 3.241 | 3.1357 | 3.2593
5717.2812 | 122.2229 | -3.2089 | 118.8217 | -0.18135 | -0.038544 | 2.7834e-05 | 0.019732 | 0.00086307 | -0.012025 | -0.0047231 | -0.055817 | 0.02475 | 0.012794 | -0.011692 | -0.020719 | 0.025699 | 0.0010425 | -0.10071 | 0.018311 | -0.041199 | -0.004578 | 0.086975 | -0.054932 | 0.041199 | 0.059509 | 0.091553 | -0.050354 | 0.050354 | 0.16479 | 0.10071 | 0.16479 | 3.1677 | -118.8034 | -118.8263 | 3.2959 | 3.2501 | 3.154 | 0.082398 | -0.013733 | 3.1586 | -118.7302 | -118.7714 | 3.3737 | 3.3737 | 3.3096 | 0.21515 | 0.15106 | 0.12817 | 0.036621 | 0.21515 | 0.10071 | 0.05951 | 0.14191 | 3.2272 | 3.3005 | -118.8629 | -118.8721 | 3.2043 | 3.2593 | 3.1082 | 3.2684
5719.0469 | 122.2458 | -3.2181 | 118.8263 | -0.12032 | -0.041962 | -0.00039957 | 0.017382 | 0.0015039 | -0.010102 | -0.0028005 | 0.029632 | 0.023682 | 0.013862 | -0.015323 | -0.018797 | 0.024631 | -0.0049389 | -0.10071 | 0.013733 | -0.054932 | 0 | 0.10986 | -0.009155 | 0.10986 | 0.07782 | 0.07782 | -0.054932 | 0.045776 | 0.18768 | 0.12817 | 0.15564 | 3.1631 | -118.8126 | -118.8263 | 3.3279 | 3.3279 | 3.2089 | 0.16479 | 0.045777 | 3.1631 | -118.7485 | -118.7805 | 3.4058 | 3.3737 | 3.3463 | 0.21057 | 0.18311 | 0.16479 | 0.054932 | 0.24261 | 0.10071 | 0.068665 | 0.13275 | 3.2318 | 3.2959 | -118.8812 | -118.8812 | 3.2181 | 3.2639 | 3.1174 | 3.2959
5720.75 | 122.2321 | -3.2135 | 118.84 | -0.15083 | -0.04068 | 2.7834e-05 | 0.017169 | -0.0042639 | -0.01352 | -0.0040823 | -0.0069885 | 0.021546 | 0.015571 | -0.017246 | -0.020933 | 0.023563 | -0.0036573 | -0.068665 | -0.009155 | -0.045776 | 0.018311 | 0.14648 | -0.009155 | 0.09613 | 0.068665 | 0.07782 | -0.054932 | 0.045776 | 0.16022 | 0.11902 | 0.13733 | 3.1677 | -118.8492 | -118.8217 | 3.36 | 3.3096 | 3.2043 | 0.14191 | 0.036621 | 3.1586 | -118.7622 | -118.7943 | 3.3737 | 3.3508 | 3.3325 | 0.19226 | 0.17395 | 0.19226 | 0.064087 | 0.21515 | 0.10071 | 0.036621 | 0.13275 | 3.2043 | 3.2913 | -118.8858 | -118.895 | 3.2318 | 3.2593 | 3.1448 | 3.2822
5722.5156 | 121.3577 | -39.6149 | 80.8685 | -0.18135 | -0.040894 | 0.0013094 | 0.022082 | -0.00020513 | -0.012666 | -0.0053641 | -0.052765 | 0.023255 | 0.013862 | -0.012119 | -0.02136 | 0.029971 | -0.00066651 | -0.11902 | 0.004578 | -0.059509 | -0.018311 | 0.068665 | -0.054932 | 0.054932 | 0.064087 | 0.09613 | -0.059509 | 0.068665 | 0.14191 | 0.10071 | 0.16937 | 39.5554 | -80.864 | -80.8868 | 39.6835 | 39.6698 | 39.5599 | 0.11444 | 0.004577 | 39.5554 | -80.7724 | -80.7999 | 39.7568 | 39.7842 | 39.7156 | 0.22888 | 0.16022 | 0.12817 | 0.041198 | 0.20142 | 0.12817 | 0.064087 | 0.15564 | 39.6194 | 39.711 | -80.928 | -80.928 | 39.5966 | 39.6835 | 39.4958 | 39.679
5724.2188 | 120.7123 | -11.6592 | 109.7397 | -0.11269 | -0.039185 | -0.0023222 | 0.019305 | 0.00086307 | -0.013734 | -0.0051505 | -0.083283 | 0.022401 | 0.016639 | -0.0087009 | -0.020506 | 0.027194 | -0.0025891 | -0.082397 | 0.018311 | -0.091553 | -0.073242 | 0.022888 | -0.091553 | 0.013733 | -0.004578 | 0.11902 | -0.064087 | 0.004578 | 0.091553 | 0.045776 | 0.07782 | 11.5677 | -109.7214 | -109.8129 | 11.6821 | 11.673 | 11.5677 | 0.10529 | 0 | 11.5952 | -109.6207 | -109.7351 | 11.7508 | 11.7371 | 11.705 | 0.14191 | 0.10986 | 0.11444 | 0.018311 | 0.15564 | 0.068665 | 0.10986 | 0.18311 | 11.6776 | 11.7783 | -109.8312 | -109.8038 | 11.586 | 11.6638 | 11.5768 | 11.6547
5725.9844 | 121.6049 | -10.3317 | 111.1633 | -0.13557 | -0.040467 | -0.0036038 | 0.016528 | 0.00022207 | -0.015443 | -0.0049367 | 0.0052185 | 0.022614 | 0.014717 | -0.017673 | -0.021147 | 0.023563 | -0.0025891 | -0.064087 | 0.004578 | -0.054932 | -0.013733 | 0.10071 | -0.018311 | 0.073242 | 0.013733 | 0.11444 | -0.064087 | -0.018311 | 0.09613 | 0.059509 | 0.09613 | 10.2768 | -111.1588 | -111.1771 | 10.4324 | 10.405 | 10.3134 | 0.12817 | 0.036621 | 10.2676 | -111.0489 | -111.1816 | 10.4279 | 10.4279 | 10.3912 | 0.16022 | 0.1236 | 0.15564 | 0.041199 | 0.16022 | 0.045776 | 0.05951 | 0.17853 | 10.3363 | 10.4462 | -111.2183 | -111.2274 | 10.318 | 10.3134 | 10.2676 | 10.3455
5727.6875 | 121.6049 | -9.819 | 111.6074 | -0.16609 | -0.039185 | -0.00061317 | 0.019732 | -0.00041873 | -0.011598 | -0.0066457 | 0.0082703 | 0.023469 | 0.015785 | -0.013187 | -0.01901 | 0.025058 | -0.0051525 | -0.11902 | 0 | -0.050354 | -0.045776 | 0.050354 | -0.07782 | 0.050354 | -0.013733 | 0.09613 | -0.050354 | -0.009155 | 0.12817 | 0.059509 | 0.10071 | 9.7687 | -111.6074 | -111.6531 | 9.8694 | 9.8694 | 9.7412 | 0.10071 | -0.027466 | 9.7687 | -111.5112 | -111.6165 | 9.9472 | 9.9197 | 9.8785 | 0.15106 | 0.10986 | 0.10071 | 0.004578 | 0.17853 | 0.041199 | 0.050354 | 0.14648 | 9.819 | 9.9152 | -111.6577 | -111.6577 | 9.7733 | 9.8099 | 9.7 | 9.8053
5729.4531 | 121.7377 | -11.0046 | 110.5453 | -0.2195 | -0.040039 | 0.00045503 | 0.018664 | -0.0019141 | -0.012879 | -0.0049367 | 0.0052185 | 0.023682 | 0.015357 | -0.016605 | -0.020292 | 0.025272 | -0.0017347 | -0.10986 | 0.013733 | -0.050354 | -0.027466 | 0.07782 | -0.041199 | 0.073242 | 0.018311 | 0.10986 | -0.064087 | 0.022888 | 0.16937 | 0.10986 | 0.15106 | 10.9543 | -110.5316 | -110.5728 | 11.0825 | 11.0779 | 10.9634 | 0.1236 | 0.009155 | 10.9406 | -110.4355 | -110.5225 | 11.174 | 11.1557 | 11.1145 | 0.21515 | 0.17395 | 0.12817 | 0.022888 | 0.23346 | 0.086975 | 0.064087 | 0.17395 | 11.0184 | 11.1145 | -110.5957 | -110.6094 | 10.9772 | 11.0275 | 10.8948 | 11.0229
5731.1562 | 121.0922 | -19.6152 | 102.475 | -0.1432 | -0.038971 | 0.00088223 | 0.021228 | 0.0023585 | -0.011384 | -0.0030141 | -0.083283 | 0.023041 | 0.015785 | -0.0063511 | -0.020933 | 0.024631 | -0.0013073 | -0.12817 | 0.036621 | -0.073242 | -0.09613 | -0.050354 | -0.17395 | -0.050354 | -0.10071 | 0.13275 | -0.082397 | -0.068665 | 0.013733 | -0.059509 | 0.041199 | 19.5419 | -102.4384 | -102.5711 | 19.5648 | 19.5648 | 19.4412 | 0.022888 | -0.10071 | 19.5328 | -102.3422 | -102.5436 | 19.6289 | 19.6564 | 19.5557 | 0.1236 | 0.022888 | 0.022888 | -0.022888 | 0.09613 | 0.013732 | 0.10986 | 0.21515 | 19.6518 | 19.7479 | -102.5482 | -102.5574 | 19.519 | 19.5465 | 19.487 | 19.5145
5732.9219 | 121.3989 | -14.2914 | 107.4371 | -0.16609 | -0.041962 | -0.00082677 | 0.018664 | -0.00063233 | -0.01352 | -0.0042959 | -0.025299 | 0.022187 | 0.018134 | -0.021518 | -0.021147 | 0.026553 | -0.0047253 | -0.10986 | 0.013733 | -0.041199 | -0.068665 | 0.036621 | -0.09613 | 0.013733 | -0.050354 | 0.1236 | -0.068665 | -0.068665 | 0.068665 | 0 | 0.059509 | 14.2502 | -107.4234 | -107.5058 | 14.328 | 14.3051 | 14.1953 | 0.054932 | -0.054931 | 14.2227 | -107.3135 | -107.5058 | 14.36 | 14.3509 | 14.2914 | 0.12817 | 0.068665 | 0.07782 | -0.027466 | 0.13733 | 0 | 0.054932 | 0.19226 | 14.3051 | 14.415 | -107.4783 | -107.5058 | 14.2227 | 14.2227 | 14.1815 | 14.241
5734.6406 | 121.8246 | -10.3226 | 111.3007 | -0.13557 | -0.040467 | -0.00039957 | 0.016955 | 0.00064947 | -0.012025 | -0.0060049 | 0.0052185 | 0.022401 | 0.016639 | -0.015109 | -0.017729 | 0.02399 | -0.0025891 | -0.07782 | -0.004578 | -0.054932 | 0.009155 | 0.14191 | 0.004578 | 0.1236 | 0.1236 | 0.086975 | -0.054932 | 0.050354 | 0.21057 | 0.14191 | 0.16937 | 10.2676 | -111.3052 | -111.2915 | 10.4645 | 10.4462 | 10.3271 | 0.17853 | 0.05951 | 10.2676 | -111.2137 | -111.2503 | 10.5331 | 10.4919 | 10.4645 | 0.22431 | 0.19684 | 0.19684 | 0.064087 | 0.2655 | 0.10529 | 0.050354 | 0.14191 | 10.318 | 10.4095 | -111.3556 | -111.3556 | 10.3317 | 10.3729 | 10.2448 | 10.4462
5736.4062 | 121.669 | -10.5698 | 111.1084 | -0.18135 | -0.03833 | 0.00066863 | 0.020587 | 0.0017175 | -0.012879 | -0.0072867 | -0.1077 | 0.02475 | 0.015998 | -0.0134 | -0.019651 | 0.026553 | -0.0055799 | -0.07782 | 0.027466 | -0.086975 | -0.054932 | 0.032043 | -0.1236 | -0.009155 | -0.036621 | 0.1236 | -0.073242 | -0.036621 | 0.050354 | -0.027466 | 0.045776 | 10.4828 | -111.0809 | -111.1633 | 10.6018 | 10.5606 | 10.4462 | 0.07782 | -0.036621 | 10.4965 | -110.9848 | -111.145 | 10.6201 | 10.6155 | 10.5423 | 0.11902 | 0.045776 | 0.11902 | 0.032043 | 0.1236 | 0.036621 | 0.11444 | 0.19684 | 10.5972 | 10.6934 | -111.1954 | -111.1816 | 10.5148 | 10.5331 | 10.4919 | 10.5331
5738.1719 | 121.843 | -25.6531 | 95.9244 | -0.17372 | -0.043244 | 2.7834e-05 | 0.017169 | -0.00020513 | -0.011384 | -0.0066457 | 0.0082703 | 0.02475 | 0.018989 | -0.017032 | -0.018583 | 0.02634 | -0.0047253 | -0.10986 | 0.004578 | -0.050354 | -0.027466 | 0.086975 | -0.036621 | 0.059509 | 0.027466 | 0.09613 | -0.054932 | 0.036621 | 0.1831 | 0.1236 | 0.15564 | 25.6027 | -95.9198 | -95.9518 | 25.7401 | 25.7126 | 25.6165 | 0.10986 | 0.013733 | 25.5981 | -95.8282 | -95.8878 | 25.8362 | 25.8087 | 25.7767 | 0.21057 | 0.17853 | 0.13733 | 0.022888 | 0.23804 | 0.091553 | 0.054932 | 0.15106 | 25.6577 | 25.7492 | -95.9747 | -95.9793 | 25.6256 | 25.6897 | 25.5432 | 25.6805
5739.9375 | 121.7972 | -26.0422 | 95.549 | -0.19661 | -0.039612 | -0.0014676 | 0.018878 | -0.00063233 | -0.011384 | -0.0047231 | -0.06192 | 0.02411 | 0.016212 | -0.011905 | -0.021787 | 0.028049 | -0.0068615 | -0.036621 | -0.004578 | -0.045776 | 0.022888 | 0.10986 | -0.036621 | 0.064087 | 0.10071 | 0.086975 | -0.041199 | 0.07782 | 0.16937 | 0.10986 | 0.16479 | 25.9964 | -95.5536 | -95.5261 | 26.152 | 26.1063 | 26.0056 | 0.10986 | 0.009155 | 26.001 | -95.462 | -95.4712 | 26.2115 | 26.207 | 26.152 | 0.20599 | 0.15106 | 0.15564 | 0.068664 | 0.21057 | 0.11902 | 0.041198 | 0.12817 | 26.0376 | 26.1291 | -95.5948 | -95.5902 | 26.0651 | 26.12 | 26.0056 | 26.1429
5741.7031 | 121.8613 | -17.7017 | 103.9856 | -0.19661 | -0.041962 | 0.00066863 | 0.018878 | -0.0023413 | -0.012239 | -0.0040823 | 0.017425 | 0.022828 | 0.015571 | -0.012332 | -0.021574 | 0.024204 | -0.0040845 | -0.086975 | -0.004578 | -0.041199 | 0.009155 | 0.13275 | -0.013733 | 0.082397 | 0.086975 | 0.091553 | -0.045776 | 0.059509 | 0.19684 | 0.12817 | 0.15564 | 17.6605 | -103.9902 | -103.9764 | 17.8345 | 17.7841 | 17.688 | 0.1236 | 0.027466 | 17.6559 | -103.894 | -103.9261 | 17.8986 | 17.8574 | 17.8299 | 0.20142 | 0.17395 | 0.17395 | 0.050354 | 0.24261 | 0.10528 | 0.036621 | 0.13733 | 17.6971 | 17.7933 | -104.0268 | -104.0314 | 17.7109 | 17.7612 | 17.6147 | 17.7887
5743.4062 | 121.17 | -13.9389 | 107.7942 | -0.29579 | 0.044128 | -0.0038174 | 0.021228 | 0.0036401 | -0.011598 | -0.0077139 | -0.12906 | 0.023469 | 0.015998 | -0.0134 | -0.021147 | 0.028049 | -0.0032299 | -0.082397 | 0.032043 | -0.073242 | -0.022888 | 0.050354 | -0.09613 | 0.013733 | 0.022888 | 0.10529 | -0.068665 | 0.009155 | 0.054932 | 0.013733 | 0.082397 | 13.8657 | -107.7621 | -107.8171 | 13.9893 | 13.9526 | 13.8428 | 0.086975 | -0.022888 | 13.8702 | -107.6889 | -107.785 | 13.9938 | 14.0213 | 13.9526 | 0.15106 | 0.082398 | 0.1236 | 0.050354 | 0.1236 | 0.07782 | 0.10529 | 0.17395 | 13.9709 | 14.0442 | -107.8674 | -107.8629 | 13.916 | 13.9481 | 13.8565 | 13.9618
5745.2188 | 121.7148 | -14.2181 | 107.5424 | -0.13557 | -0.041748 | -0.0085172 | 0.0208 | 0.0032129 | -0.012025 | -0.0062185 | -0.10464 | 0.023896 | 0.018134 | -0.016605 | -0.019438 | 0.025912 | -0.0028027 | -0.12817 | 0.013733 | -0.07782 | -0.10071 | -0.041199 | -0.15564 | -0.036621 | -0.07782 | 0.12817 | -0.086975 | -0.032043 | 0.022888 | -0.032043 | 0.045776 | 14.1403 | -107.5287 | -107.6431 | 14.1769 | 14.1815 | 14.0625 | 0.041199 | -0.07782 | 14.1312 | -107.4142 | -107.5745 | 14.241 | 14.2639 | 14.1861 | 0.13275 | 0.054932 | 0.036621 | -0.022888 | 0.10986 | 0.054932 | 0.091553 | 0.21515 | 14.2319 | 14.3463 | -107.6202 | -107.6294 | 14.1174 | 14.1861 | 14.09 | 14.1403
5746.9375 | 121.9391 | -17.6514 | 103.8437 | -0.22713 | -0.039398 | -0.00061317 | 0.019519 | -0.0029821 | -0.011598 | -0.0045095 | -0.068024 | 0.023896 | 0.017494 | -0.010623 | -0.02136 | 0.026553 | -0.00066651 | -0.054932 | 0 | -0.054932 | 0.022888 | 0.11902 | -0.036621 | 0.059509 | 0.082397 | 0.09613 | -0.059509 | 0.09613 | 0.16479 | 0.10071 | 0.17395 | 17.5964 | -103.8437 | -103.8208 | 17.7704 | 17.7109 | 17.6147 | 0.11444 | 0.018311 | 17.5919 | -103.7476 | -103.7476 | 17.8162 | 17.8253 | 17.7521 | 0.23346 | 0.16022 | 0.17395 | 0.07782 | 0.2243 | 0.15564 | 0.054932 | 0.15564 | 17.6514 | 17.7475 | -103.8986 | -103.9032 | 17.6743 | 17.7475 | 17.5964 | 17.7338
5748.7031 | 121.9482 | -23.5886 | 98.0621 | -0.15846 | -0.041748 | -0.00061317 | 0.018451 | -0.0044775 | -0.011384 | -0.0049367 | 0.0052185 | 0.022401 | 0.015571 | -0.0134 | -0.019651 | 0.023563 | -0.00088011 | -0.073242 | 0.013733 | -0.059509 | 0.036621 | 0.16937 | 0.032043 | 0.1236 | 0.13275 | 0.086975 | -0.036621 | 0.07782 | 0.21515 | 0.16022 | 0.17853 | 23.5291 | -98.0484 | -98.0255 | 23.7579 | 23.7122 | 23.6206 | 0.1831 | 0.091552 | 23.5519 | -97.9752 | -97.9843 | 23.8037 | 23.7671 | 23.7488 | 0.21515 | 0.19684 | 0.22888 | 0.09613 | 0.25177 | 0.11444 | 0.073242 | 0.1236 | 23.6023 | 23.6755 | -98.1216 | -98.0988 | 23.6252 | 23.6664 | 23.5153 | 23.7213
5750.4375 | 121.9025 | -31.1234 | 90.5319 | -0.18135 | -0.039185 | 0.00045503 | 0.018237 | -0.0017005 | -0.012239 | -0.0036551 | -0.016144 | 0.023896 | 0.015357 | -0.011264 | -0.023069 | 0.02634 | -0.0051525 | -0.13275 | 0.004578 | -0.050354 | -0.009155 | 0.07782 | -0.064087 | 0.036621 | 0.009155 | 0.10529 | -0.045776 | 0.009155 | 0.1236 | 0.059509 | 0.10529 | 31.073 | -90.5273 | -90.5411 | 31.2012 | 31.16 | 31.0593 | 0.086975 | -0.013733 | 31.0776 | -90.4266 | -90.5228 | 31.2469 | 31.2286 | 31.1829 | 0.15106 | 0.10528 | 0.12817 | 0.041199 | 0.16937 | 0.054931 | 0.054932 | 0.15106 | 31.1279 | 31.2286 | -90.5823 | -90.5777 | 31.1142 | 31.1325 | 30.9906 | 31.1325
5752.2031 | 121.9025 | -28.0289 | 93.6356 | -0.20424 | -0.042389 | 0.00024143 | 0.01781 | -0.0025549 | -0.012666 | -0.0053641 | -0.013092 | 0.024964 | 0.017066 | -0.012119 | -0.020506 | 0.025058 | 0.00082889 | -0.1236 | 0.013733 | -0.045776 | -0.041199 | 0.068665 | -0.064087 | 0.050354 | 0.018311 | 0.091553 | -0.059509 | 0.009155 | 0.13733 | 0.086975 | 0.1236 | 27.9831 | -93.6218 | -93.6768 | 28.0975 | 28.0792 | 27.9648 | 0.09613 | -0.018311 | 27.9694 | -93.544 | -93.6264 | 28.1662 | 28.1525 | 28.1158 | 0.1831 | 0.14648 | 0.11444 | 0.004577 | 0.19684 | 0.068664 | 0.059509 | 0.15106 | 28.0426 | 28.1204 | -93.6813 | -93.6951 | 27.9877 | 28.038 | 27.9053 | 28.0472
5753.9688 | 121.9391 | -28.2669 | 93.4708 | -0.19661 | -0.043671 | -0.00082677 | 0.018023 | 0.0027857 | -0.014161 | -0.0066457 | -0.0039367 | 0.02411 | 0.014289 | -0.012119 | -0.018583 | 0.024844 | -0.0070751 | -0.068665 | -0.013733 | -0.041199 | 0.032043 | 0.16937 | 0.018311 | 0.11902 | 0.10986 | 0.086975 | -0.045776 | 0.054932 | 0.20599 | 0.13733 | 0.14648 | 28.2257 | -93.4845 | -93.4387 | 28.4363 | 28.3859 | 28.2852 | 0.16022 | 0.05951 | 28.2211 | -93.3838 | -93.4158 | 28.4729 | 28.4134 | 28.4042 | 0.19226 | 0.18311 | 0.21057 | 0.073242 | 0.25177 | 0.10071 | 0.027466 | 0.13275 | 28.2532 | 28.3539 | -93.512 | -93.5165 | 28.299 | 28.3218 | 28.1982 | 28.3768
5755.75 | 121.312 | -43.7119 | 84.6542 | -0.1432 | -0.037689 | 0.00088223 | 0.021228 | 0.00043587 | -0.01117 | -0.0036551 | -0.077179 | 0.02411 | 0.015144 | -0.01276 | 4.6134 | 0.0116 | -0.0060071 | -0.036621 | 0 | -0.054932 | 0.032043 | 0.1236 | -0.027466 | 0.068665 | 0.073242 | 0.10986 | -0.032043 | 0.091553 | 4.8981 | 0.15106 | 0.36163 | 43.6569 | -84.6542 | -84.6222 | 43.8354 | 43.7805 | 43.6844 | 0.1236 | 0.027466 | 43.6798 | -84.5444 | -84.5627 | 48.6099 | 44.0735 | 43.8629 | 0.39368 | 0.18311 | 0.17853 | 0.086975 | 4.9301 | 0.1236 | 0.054932 | 0.14191 | 43.7119 | 43.8217 | -84.7092 | -84.6863 | 43.7439 | 43.8034 | 43.6752 | 43.7851
5757.5156 | 122.0856 | -118.364 | 3.2272 | -0.16609 | -0.040253 | 0.00024143 | 0.016314 | 0.00086307 | -0.012239 | -0.0051505 | 0.038788 | 0.023041 | 0.015998 | -0.018741 | -0.02136 | 0.025699 | -0.0042981 | -0.10071 | 0.009155 | 0.009155 | -0.013733 | 0.082397 | -0.068665 | -0.027466 | 0.068665 | -0.004578 | 0.23804 | 0.032043 | 0.12817 | 0.068665 | 0.13275 | 118.3731 | -3.2181 | -3.241 | 118.4463 | 118.3365 | 118.2953 | -0.036621 | -0.07782 | 118.602 | -3.2318 | -3.1952 | 118.4921 | 118.4967 | 118.4326 | -0.10529 | -0.16937 | 0.073242 | -0.022888 | -0.10986 | -0.20599 | 0 | -0.24261 | 118.3731 | 118.3594 | -3.2181 | -2.9892 | 118.3502 | 118.396 | 118.2632 | 118.4326
5759.2812 | 122.1497 | -119.6915 | 1.9913 | -0.1432 | -0.038971 | 0.0010958 | 0.01781 | -0.0025549 | -0.012025 | -0.0072867 | 0.054047 | 0.021332 | 0.01493 | -0.017673 | -0.018797 | 0.025272 | -0.0019483 | -0.086975 | -0.009155 | -0.045776 | 0.022888 | 0.17853 | 0.032043 | 0.091553 | 0.11902 | 0.086975 | 0.022888 | 0.07782 | 0.1831 | 0.13275 | 0.15564 | 119.6457 | -2.0004 | -1.9684 | 119.87 | 119.783 | 119.7235 | 0.13733 | 0.077819 | 119.7144 | -1.9043 | -1.9135 | 119.8746 | 119.8471 | 119.8242 | 0.13275 | 0.10986 | 0.2243 | 0.068664 | 0.16022 | 0.054932 | 0.036621 | 0.064087 | 119.6823 | 119.7784 | -2.037 | -1.9684 | 119.7144 | 119.7693 | 119.6045 | 119.8105
5760.9844 | 122.0627 | -118.0298 | 3.6758 | -0.12794 | -0.043457 | -0.0014676 | 0.01781 | -0.0019141 | -0.011384 | -0.0053641 | -0.052765 | 0.023896 | 0.015571 | -0.017673 | -0.01901 | 0.024631 | -0.0030163 | -0.16022 | 0.018311 | 0.10071 | -0.10986 | -0.21057 | -0.40283 | -0.32044 | -0.073242 | 0.11902 | 0.29297 | -0.032043 | 0.018311 | -0.29755 | -0.22888 | 118.1305 | -3.6575 | -3.7857 | 117.8192 | 117.7094 | 117.627 | -0.42114 | -0.50354 | 118.3228 | -3.5568 | -3.7079 | 118.0481 | 117.8009 | 117.7322 | -0.52185 | -0.59051 | -0.31128 | -0.21057 | -0.27466 | -0.32501 | -0.082397 | -0.17395 | 118.0481 | 118.1488 | -3.5751 | -3.3829 | 117.9199 | 117.9977 | 117.8696 | 117.9565
5762.75 | 122.1451 | -118.428 | 3.2547 | -0.18898 | -0.041107 | 0.0036594 | 0.019732 | -0.0017005 | -0.009675 | -0.0036551 | 0.0052185 | 0.021332 | 0.013648 | -0.01041 | -0.020078 | 0.026126 | 0.00082889 | -0.059509 | 0.018311 | -0.041199 | 0.018311 | 0.1236 | -0.041199 | -0.036621 | 0.09613 | 0.068665 | -0.022888 | 0.10986 | 0.13275 | 0.10986 | 0.15564 | 118.3868 | -3.2364 | -3.2364 | 118.5516 | 118.3914 | 118.3868 | 0.004578 | 0 | 118.4052 | -3.186 | -3.1448 | 118.5608 | 118.5837 | 118.5379 | 0.17853 | 0.13275 | 0.16479 | 0.05951 | 0.15564 | 0.13275 | 0.05951 | 0.091553 | 118.4464 | 118.4967 | -3.2959 | -3.2776 | 118.4464 | 118.5379 | 118.3685 | 118.5242
5764.5156 | 122.0123 | -118.7027 | 3.1357 | -0.1432 | -0.041535 | -0.00082677 | 0.02016 | -0.00084593 | -0.013307 | -0.0049367 | 0.0082703 | 0.023255 | 0.017066 | -0.017887 | -0.018369 | 0.025912 | -0.0032299 | -0.14191 | 0.027466 | -0.07782 | -0.086975 | 0.004578 | -0.17395 | -0.20142 | -0.050354 | 0.13275 | -0.054932 | -0.032043 | 0.027466 | -0.013733 | -0.11444 | 118.6249 | -3.1082 | -3.2227 | 118.7073 | 118.5013 | 118.5287 | -0.1236 | -0.09613 | 118.6478 | -3.0029 | -3.1677 | 118.7302 | 118.5883 | 118.689 | -0.059509 | 0.041199 | 0.082398 | -0.009155 | 0.082398 | 0.022889 | 0.10529 | 0.18768 | 118.7302 | 118.8354 | -3.2135 | -3.1906 | 118.6157 | 118.6707 | 118.5608 | 118.6523
5766.2812 | 122.168 | -120.6299 | 1.0986 | -0.10506 | -0.041535 | -0.00061317 | 0.018664 | -0.0012731 | -0.010957 | -0.0051505 | 0.050995 | 0.022187 | 0.016212 | -0.025791 | -0.020506 | 0.025912 | -0.0030163 | -0.11444 | 0.018311 | -0.050354 | -0.036621 | 0.07782 | -0.036621 | 0.059509 | 0.032043 | 0.091553 | -0.045776 | 0.07782 | 0.10529 | 0.086975 | 0.13733 | 120.5795 | -1.0803 | -1.1353 | 120.7077 | 120.6894 | 120.5933 | 0.10986 | 0.013733 | 120.5841 | -1.0071 | -1.0208 | 120.7352 | 120.7672 | 120.7169 | 0.18311 | 0.13275 | 0.12817 | 0.013733 | 0.15106 | 0.1236 | 0.068665 | 0.13733 | 120.6482 | 120.7214 | -1.149 | -1.1444 | 120.5933 | 120.7077 | 120.5154 | 120.6619
5767.9844 | 122.0627 | -120.6985 | 1.1444 | -0.20424 | 0.040069 | 0.11432 | 0.012256 | 0.044442 | 0.054198 | 0.048255 | -0.48611 | 0.037568 | 0.023475 | -0.020877 | 0.19739 | 0.042361 | -0.019465 | -0.068665 | 0.036621 | -0.064087 | -0.032043 | -0.082397 | -0.41199 | -0.12817 | 0.013733 | 0.13275 | -0.050354 | 0.036621 | 0.027466 | -0.041199 | -0.30212 | 120.6345 | -1.1078 | -1.1765 | 120.6162 | 120.5704 | 120.2866 | -0.064087 | -0.3479 | 120.6482 | -1.0117 | -1.1078 | 120.726 | 120.3964 | 120.6573 | -0.25177 | 0.009155 | -0.01831 | 0.032044 | 0.07782 | 0.086975 | 0.10071 | 0.18311 | 120.7352 | 120.8313 | -1.2085 | -1.1948 | 120.6665 | 120.7352 | 120.6299 | 120.7123
5769.75 | 122.0261 | -120.7077 | 1.181 | -0.18898 | -0.048798 | -0.014285 | 0.019732 | -0.0111 | -0.030183 | -0.02459 | -0.31522 | 0.010438 | 0.012153 | -0.017032 | -0.017515 | 0.021854 | -0.0060071 | -0.13275 | 0.041199 | -0.07782 | -0.09613 | -0.054932 | -0.28839 | -0.39368 | -0.073242 | 0.1236 | -0.07782 | 0.013733 | -0.004578 | -0.059509 | -0.041199 | 120.6299 | -1.1398 | -1.2772 | 120.6528 | 120.314 | 120.4193 | -0.31586 | -0.21057 | 120.6299 | -1.0574 | -1.1673 | 120.7031 | 120.6665 | 120.6482 | 0.036621 | 0.018311 | 0.022888 | -0.01831 | 0.073242 | 0.091553 | 0.11902 | 0.20142 | 120.7489 | 120.8313 | -1.2589 | -1.2589 | 120.6116 | 120.7214 | 120.575 | 120.6345
5771.5156 | 122.1085 | -120.7077 | 1.149 | -0.17372 | -0.043244 | -0.00061317 | 0.018878 | 0.0019311 | -0.012879 | -0.0036551 | 0.011322 | 0.020905 | 0.01493 | -0.019596 | -0.019438 | 0.025699 | -0.0025891 | -0.082397 | 0.013733 | -0.050354 | 0.027466 | 0.13733 | 0 | 0.09613 | 0.054932 | 0.091553 | -0.064087 | 0.059509 | 0.13275 | 0.082397 | 0.11902 | 120.6573 | -1.1353 | -1.1215 | 120.845 | 120.8038 | 120.7077 | 0.14648 | 0.050354 | 120.6436 | -1.0574 | -1.0895 | 120.8405 | 120.8267 | 120.7901 | 0.18311 | 0.14648 | 0.18768 | 0.07782 | 0.19684 | 0.1236 | 0.064087 | 0.15564 | 120.7214 | 120.7993 | -1.1993 | -1.2131 | 120.7352 | 120.7672 | 120.6253 | 120.7626
5773.2188 | 122.0993 | -120.5795 | 1.1673 | -0.17372 | -0.043244 | -0.0016812 | 0.018451 | -0.00063233 | -0.011598 | -0.0034415 | 0.032684 | 0.023682 | 0.014503 | -0.01041 | -0.01901 | 0.027194 | -0.0032299 | -0.068665 | -0.004578 | -0.036621 | 0.041199 | 0.15564 | 0.027466 | 0.11902 | 0.13733 | 0.082397 | -0.045776 | 0.086975 | 0.19684 | 0.12817 | 0.15106 | 120.5429 | -1.1719 | -1.1261 | 120.7352 | 120.6985 | 120.607 | 0.15564 | 0.064087 | 120.5338 | -1.0849 | -1.0803 | 120.7764 | 120.7306 | 120.7077 | 0.19684 | 0.17395 | 0.19226 | 0.07782 | 0.24261 | 0.13275 | 0.032043 | 0.12817 | 120.575 | 120.6619 | -1.2039 | -1.2131 | 120.6207 | 120.6665 | 120.5109 | 120.7169
5774.9844 | 122.0352 | -120.3964 | 1.4923 | -0.12794 | -0.051789 | -0.01578 | 0.015033 | -0.020499 | -0.021424 | 0.040351 | -0.48306 | 0.038209 | 0.0027536 | -0.025791 | -0.029691 | 0.042361 | -0.016475 | -0.086975 | 0.050354 | -0.073242 | -0.036621 | 0.054932 | -0.1236 | -0.22888 | 0.022888 | 0.1236 | -0.068665 | 0.045776 | 0.073242 | 0.009155 | 0.073242 | 120.3232 | -1.442 | -1.5289 | 120.4514 | 120.1675 | 120.2728 | -0.15564 | -0.050354 | 120.3278 | -1.3687 | -1.4465 | 120.4697 | 120.4697 | 120.4056 | 0.14191 | 0.07782 | 0.12817 | 0.036621 | 0.14191 | 0.11444 | 0.1236 | 0.19226 | 120.4468 | 120.52 | -1.5656 | -1.561 | 120.3598 | 120.4422 | 120.3094 | 120.4193
5776.75 | 122.1359 | -120.2637 | 1.5884 | -0.15846 | -0.042816 | -0.0016812 | 0.018023 | -0.0038367 | -0.01117 | -0.0053641 | 0.038788 | 0.020692 | 0.014717 | -0.015109 | -0.020933 | 0.023349 | -0.0036573 | -0.059509 | -0.004578 | -0.032043 | 0.036621 | 0.15564 | 0.027466 | 0.10986 | 0.10986 | 0.091553 | -0.045776 | 0.082397 | 0.19226 | 0.13275 | 0.14648 | 120.2316 | -1.593 | -1.5518 | 120.4193 | 120.3735 | 120.2911 | 0.14191 | 0.059509 | 120.2179 | -1.4969 | -1.506 | 120.4559 | 120.4102 | 120.3964 | 0.19226 | 0.17853 | 0.18768 | 0.068664 | 0.23804 | 0.12817 | 0.027465 | 0.13733 | 120.2591 | 120.3552 | -1.6205 | -1.6342 | 120.3003 | 120.3461 | 120.2042 | 120.3735
5778.5156 | 121.9986 | -120.1721 | 1.7441 | -0.1432 | -0.043457 | 0.0064364 | 0.021869 | -0.0070409 | -0.02826 | -0.021813 | -0.18094 | 0.0063787 | 0.010444 | -0.011905 | -0.016233 | 0.017581 | -0.0047253 | -0.12817 | 0.059509 | -0.082397 | -0.10986 | -0.050354 | -0.17853 | -0.13275 | -0.10071 | 0.1236 | -0.07782 | -0.018311 | 0.022888 | -0.045776 | 0.054932 | 120.0897 | -1.6846 | -1.8539 | 120.1218 | 120.0394 | 119.9936 | -0.050354 | -0.096131 | 120.0943 | -1.6205 | -1.7624 | 120.195 | 120.2271 | 120.1263 | 0.13275 | 0.032044 | 0.032043 | -0.027466 | 0.10071 | 0.059509 | 0.14191 | 0.20142 | 120.2316 | 120.2957 | -1.8265 | -1.8219 | 120.0623 | 120.1538 | 120.0439 | 120.0714
5780.2812 | 122.049 | -120.1263 | 1.7853 | -0.097427 | -0.039398 | -0.00061317 | 0.021014 | -0.00084593 | -0.0094614 | -0.0051505 | -0.13211 | 0.022614 | 0.014717 | -0.0095553 | -0.019438 | 0.02634 | -0.0028027 | -0.13275 | 0.041199 | -0.073242 | -0.10529 | -0.027466 | -0.10986 | -0.022888 | -0.054932 | 0.1236 | -0.07782 | -0.027466 | 0.082397 | -0.004578 | 0.050354 | 120.0531 | -1.7441 | -1.8906 | 120.0989 | 120.1035 | 120.0165 | 0.050354 | -0.036621 | 120.0485 | -1.6617 | -1.8127 | 120.2087 | 120.1767 | 120.1218 | 0.12817 | 0.073242 | 0.045776 | -0.032044 | 0.16022 | 0.050354 | 0.11444 | 0.20142 | 120.1675 | 120.2499 | -1.8585 | -1.8631 | 120.0211 | 120.0989 | 119.9936 | 120.0714
5781.9844 | 122.2412 | -117.0593 | 4.6097 | -0.17372 | -0.040039 | 0.0019504 | 0.021869 | 0.0021447 | -0.011598 | -0.0057913 | -0.058869 | 0.02176 | 0.015357 | -0.016391 | -0.020933 | 0.02869 | 0.0012561 | -0.10986 | 0.022888 | -0.045776 | 0 | 0.09613 | -0.07782 | 0.059509 | 0.073242 | 0.09613 | -0.050354 | 0.10071 | 0.15564 | 0.086975 | 0.16022 | 117.0135 | -4.5868 | -4.6097 | 117.1555 | 117.1188 | 116.9815 | 0.10528 | -0.032044 | 117.009 | -4.5136 | -4.509 | 117.215 | 117.2195 | 117.1463 | 0.21057 | 0.13733 | 0.14191 | 0.045776 | 0.20599 | 0.15106 | 0.068664 | 0.14648 | 117.0822 | 117.1555 | -4.6555 | -4.66 | 117.0593 | 117.16 | 116.9495 | 117.1326
5783.75 | 122.1725 | -116.6382 | 5.1407 | -0.18135 | -0.039398 | -0.00018577 | 0.021655 | 0.0019311 | -0.011811 | -0.0045095 | -0.016144 | 0.022614 | 0.013648 | -0.012973 | -0.017301 | 0.025058 | -0.0032299 | -0.10986 | -0.009155 | -0.022888 | -0.027466 | 0.086975 | -0.054932 | 0.050354 | 0.022888 | 0.091553 | -0.059509 | 0.054932 | 0.13275 | 0.054932 | 0.10071 | 116.6153 | -5.1498 | -5.1682 | 116.7252 | 116.6885 | 116.5833 | 0.073242 | -0.032044 | 116.5787 | -5.0491 | -5.0858 | 116.7709 | 116.7389 | 116.6931 | 0.16022 | 0.11444 | 0.10986 | -0.004578 | 0.19226 | 0.11444 | 0.013733 | 0.15106 | 116.629 | 116.7297 | -5.1636 | -5.2002 | 116.6107 | 116.6931 | 116.5283 | 116.6611
5785.5156 | 122.1542 | -119.0323 | 2.8152 | -0.18135 | -0.038971 | -0.0072354 | 0.021655 | -0.013023 | -0.022492 | -0.014764 | -0.49222 | 0.037568 | 0.005958 | -0.019809 | -0.032469 | 0.041934 | -0.018611 | -0.07782 | 0.032043 | -0.064087 | -0.018311 | 0.064087 | -0.082397 | -0.073242 | 0.050354 | 0.10071 | -0.064087 | 0.050354 | 0.091553 | 0.036621 | 0.091553 | 118.9682 | -2.7832 | -2.8336 | 119.0964 | 118.959 | 118.9499 | -0.009155 | -0.01831 | 118.9682 | -2.7145 | -2.7649 | 119.1238 | 119.1238 | 119.0689 | 0.15564 | 0.10071 | 0.12817 | 0.045776 | 0.15564 | 0.11444 | 0.09613 | 0.1648 | 119.0643 | 119.133 | -2.8793 | -2.8793 | 119.014 | 119.0826 | 118.9545 | 119.0826
5787.2812 | 122.1497 | -119.7464 | 2.1286 | -0.18135 | -0.041748 | -0.00082677 | 0.018451 | -0.00041873 | -0.012666 | -0.0045095 | -0.0008851 | 0.022187 | 0.01493 | -0.016178 | -0.018797 | 0.024204 | -0.0025891 | -0.11902 | 0 | -0.045776 | -0.041199 | 0.07782 | -0.064087 | 0.050354 | 0.018311 | 0.091553 | -0.050354 | 0.041199 | 0.11444 | 0.054932 | 0.11444 | 119.7006 | -2.1286 | -2.1698 | 119.8242 | 119.7968 | 119.6823 | 0.09613 | -0.018311 | 119.696 | -2.037 | -2.0874 | 119.8608 | 119.8608 | 119.8013 | 0.16479 | 0.10529 | 0.1236 | 0.004577 | 0.16479 | 0.091553 | 0.045776 | 0.14191 | 119.7464 | 119.838 | -2.1744 | -2.179 | 119.7052 | 119.7876 | 119.6274 | 119.7647
5789 | 122.1222 | -119.7876 | 2.1286 | -0.18135 | -0.038971 | 0.0013094 | 0.021441 | -0.0023413 | -0.01352 | -0.016473 | -0.23282 | 0.01236 | 0.011299 | -0.018527 | -0.023283 | 0.0098908 | -0.0094251 | -0.09613 | 0.027466 | -0.073242 | -0.045776 | 0.054932 | -0.068665 | 0.013733 | 0.013733 | 0.13275 | -0.054932 | 0.041199 | 0.10071 | 0.041199 | 0.082397 | 119.7144 | -2.1011 | -2.1744 | 119.8425 | 119.8013 | 119.7189 | 0.086975 | 0.004577 | 119.7327 | -1.9959 | -2.0874 | 119.8883 | 119.87 | 119.8288 | 0.13733 | 0.096131 | 0.12817 | 0.027466 | 0.15564 | 0.096131 | 0.10071 | 0.18768 | 119.8151 | 119.9203 | -2.2018 | -2.1835 | 119.7418 | 119.8288 | 119.6915 | 119.8013
5790.7656 | 122.2687 | -119.2108 | 2.6093 | -0.18135 | -0.042603 | -0.00061317 | 0.019946 | 0.00064947 | -0.013093 | -0.0017325 | 0.011322 | 0.02176 | 0.013435 | -0.016605 | -0.019224 | 0.024844 | -0.0036573 | -0.13275 | 0.018311 | -0.050354 | -0.045776 | 0.064087 | -0.059509 | 0.068665 | -0.009155 | 0.091553 | -0.064087 | 0.064087 | 0.11902 | 0.054932 | 0.1236 | 119.1605 | -2.5909 | -2.655 | 119.2749 | 119.2795 | 119.1513 | 0.11902 | -0.009155 | 119.1467 | -2.5177 | -2.5452 | 119.3298 | 119.3344 | 119.2657 | 0.18768 | 0.11902 | 0.11444 | 0.004578 | 0.18311 | 0.12817 | 0.068665 | 0.15564 | 119.2291 | 119.3024 | -2.6596 | -2.6733 | 119.165 | 119.2749 | 119.0781 | 119.2017
5792.5312 | 122.2458 | -119.3893 | 2.4307 | -0.20424 | -0.039185 | 0.0017368 | 0.023791 | 0.00022207 | -0.01352 | -0.0019461 | -0.06192 | 0.023041 | 0.012153 | -0.014255 | -0.019224 | 0.024204 | -0.00066651 | -0.059509 | 0.004578 | -0.027466 | 0.027466 | 0.12817 | -0.027466 | 0.082397 | 0.091553 | 0.07782 | -0.027466 | 0.13275 | 0.16937 | 0.09613 | 0.16479 | 119.3619 | -2.4261 | -2.4033 | 119.5175 | 119.4717 | 119.3619 | 0.10986 | 0 | 119.3619 | -2.3529 | -2.298 | 119.5587 | 119.5541 | 119.4855 | 0.19226 | 0.1236 | 0.15564 | 0.054932 | 0.19684 | 0.16022 | 0.032044 | 0.10529 | 119.3939 | 119.4672 | -2.4582 | -2.4582 | 119.4168 | 119.5221 | 119.3298 | 119.4809
5794.2344 | 122.1588 | -119.5129 | 2.3849 | -0.17372 | -0.040253 | 0.0019504 | 0.021869 | -0.014091 | -0.012879 | -0.018822 | -0.19315 | 0.031159 | 0.010658 | -0.026859 | -0.035887 | 0.042148 | -0.023311 | -0.086975 | 0.045776 | -0.068665 | -0.041199 | 0.059509 | -0.07782 | -0.009155 | 0.036621 | 0.11902 | -0.059509 | 0.059509 | 0.09613 | 0.032043 | 0.086975 | 119.4443 | -2.3392 | -2.4261 | 119.5724 | 119.5038 | 119.4351 | 0.05951 | -0.009155 | 119.4534 | -2.2659 | -2.3254 | 119.6091 | 119.5999 | 119.545 | 0.14648 | 0.091552 | 0.12817 | 0.027466 | 0.15564 | 0.11902 | 0.11444 | 0.17853 | 119.5587 | 119.632 | -2.4536 | -2.4445 | 119.4717 | 119.5724 | 119.426 | 119.5496
5796 | 122.0947 | -119.9387 | 2.0142 | -0.10506 | -0.042816 | -0.00018577 | 0.019519 | -0.0040503 | -0.01053 | -0.0047231 | -0.040558 | 0.023896 | 0.014076 | -0.010837 | -0.017942 | 0.026553 | -0.0036573 | -0.16479 | 0.054932 | -0.09613 | -0.10071 | 0.004578 | -0.10986 | 0 | -0.068665 | 0.13275 | -0.086975 | -0.036621 | 0.050354 | -0.009155 | 0.036621 | 119.8425 | -1.9592 | -2.1149 | 119.9432 | 119.9387 | 119.8288 | 0.09613 | -0.013733 | 119.8517 | -1.8814 | -2.0508 | 119.989 | 119.9753 | 119.9295 | 0.1236 | 0.07782 | 0.10071 | -0.004578 | 0.13733 | 0.050354 | 0.15106 | 0.21973 | 119.9936 | 120.0714 | -2.1103 | -2.1011 | 119.838 | 119.902 | 119.7739 | 119.87
5797.7031 | 122.0947 | -120.5154 | 1.4648 | -0.13557 | -0.041962 | -0.0018948 | 0.018664 | 0.00022207 | -0.015016 | -0.0040823 | -0.040558 | 0.022614 | 0.014289 | -0.019809 | -0.021574 | 0.024417 | -0.0053661 | -0.15564 | 0.036621 | -0.086975 | -0.10986 | 0.004578 | -0.10071 | 0 | -0.073242 | 0.14191 | -0.068665 | -0.045776 | 0.041199 | -0.009155 | 0.041199 | 120.4285 | -1.4282 | -1.5747 | 120.52 | 120.5154 | 120.4147 | 0.086975 | -0.013733 | 120.4468 | -1.3229 | -1.5106 | 120.5566 | 120.5566 | 120.5063 | 0.10986 | 0.05951 | 0.091553 | -0.022888 | 0.10986 | 0.022889 | 0.1236 | 0.21057 | 120.5521 | 120.6573 | -1.5518 | -1.5335 | 120.4056 | 120.4697 | 120.3598 | 120.4422
5799.4531 | 122.1817 | -117.3981 | 4.5181 | -0.13557 | -0.042176 | 0.00066863 | 0.018451 | -0.0012731 | -0.015016 | -0.0023733 | 0.0052185 | 0.022401 | 0.015144 | -0.0095553 | -0.01901 | 0.024631 | -0.0023755 | -0.064087 | 0 | -0.041199 | 0.032043 | 0.14648 | 0.004578 | 0.10986 | 0.086975 | 0.082397 | -0.041199 | 0.07782 | 0.18768 | 0.14191 | 0.15106 | 117.3569 | -4.5181 | -4.4861 | 117.5446 | 117.5079 | 117.4026 | 0.15106 | 0.045777 | 117.3569 | -4.4357 | -4.4403 | 117.5858 | 117.5491 | 117.54 | 0.19226 | 0.18311 | 0.18768 | 0.073242 | 0.22888 | 0.11902 | 0.041199 | 0.1236 | 117.3981 | 117.4805 | -4.5593 | -4.5593 | 117.4301 | 117.4759 | 117.334 | 117.485
5801.1562 | 122.1954 | -120.5887 | 1.2909 | -0.05928 | -0.039612 | -0.0036038 | 0.023364 | -0.0036231 | -0.01117 | -0.0081411 | -0.17178 | 0.018769 | 0.0083078 | -0.013828 | -0.025419 | 0.043643 | -0.016902 | -0.082397 | 0.036621 | -0.068665 | -0.041199 | 0.073242 | -0.07782 | 0.013733 | 0.027466 | 0.11902 | -0.068665 | 0.054932 | 0.11444 | 0.036621 | 0.09613 | 120.52 | -1.2543 | -1.3321 | 120.6619 | 120.6024 | 120.5109 | 0.082398 | -0.009155 | 120.52 | -1.1719 | -1.236 | 120.7031 | 120.6848 | 120.6253 | 0.16479 | 0.10529 | 0.14191 | 0.027466 | 0.18311 | 0.1236 | 0.10529 | 0.18768 | 120.6253 | 120.7077 | -1.3596 | -1.3596 | 120.5475 | 120.6436 | 120.5063 | 120.6162
5802.9219 | 122.1451 | -120.8221 | 1.1261 | -0.12794 | -0.038971 | -0.0027494 | 0.021228 | -0.0012731 | -0.015016 | -0.0040823 | -0.058869 | 0.024323 | 0.014717 | -0.016178 | -0.018797 | 0.025912 | -0.0010937 | -0.15564 | 0.045776 | -0.09613 | -0.1236 | 0 | -0.1236 | -0.009155 | -0.059509 | 0.13733 | -0.07782 | -0.013733 | 0.045776 | 0 | 0.045776 | 120.726 | -1.0803 | -1.2497 | 120.8221 | 120.813 | 120.6985 | 0.086975 | -0.027466 | 120.7443 | -0.98877 | -1.1398 | 120.8679 | 120.8679 | 120.8221 | 0.1236 | 0.07782 | 0.09613 | -0.027466 | 0.1236 | 0.064087 | 0.14191 | 0.21515 | 120.8679 | 120.9595 | -1.2222 | -1.2039 | 120.6985 | 120.8084 | 120.6665 | 120.7626
5804.6875 | 122.1725 | -120.9091 | 1.0712 | -0.11269 | -0.037903 | -0.00061317 | 0.021655 | -0.0042639 | -0.012879 | -0.0038687 | -0.22366 | 0.016206 | 0.013648 | -0.011051 | -0.017301 | 0.018436 | -0.0098523 | -0.11444 | 0.027466 | -0.082397 | -0.064087 | 0.050354 | -0.07782 | 0.018311 | -0.004578 | 0.11444 | -0.082397 | 0.036621 | 0.091553 | 0.027466 | 0.09613 | 120.8267 | -1.0437 | -1.1353 | 120.9595 | 120.9274 | 120.8313 | 0.10071 | 0.004577 | 120.8267 | -0.95673 | -1.0345 | 121.0007 | 121.0052 | 120.9366 | 0.17853 | 0.10986 | 0.13275 | 0.01831 | 0.17395 | 0.11902 | 0.10986 | 0.19684 | 120.9366 | 121.0236 | -1.1536 | -1.1536 | 120.845 | 120.9457 | 120.7947 | 120.9045
5806.3906 | 122.0901 | -120.0531 | 1.9455 | -0.15846 | -0.038758 | 0.0010958 | 0.021014 | 0.0010767 | -0.013093 | -0.0077139 | -0.16263 | 0.023041 | 0.013862 | -0.010837 | -0.018583 | 0.028049 | 0.0029651 | -0.14648 | 0.036621 | -0.082397 | -0.1236 | -0.064087 | -0.18768 | -0.036621 | -0.082397 | 0.1236 | -0.07782 | -0.013733 | 0.013733 | -0.050354 | 0.050354 | 119.9707 | -1.9089 | -2.0691 | 119.989 | 120.0165 | 119.8654 | 0.045776 | -0.10529 | 119.9753 | -1.8219 | -1.9592 | 120.0668 | 120.1035 | 120.0027 | 0.12817 | 0.027466 | 0.01831 | -0.041199 | 0.091553 | 0.064087 | 0.11902 | 0.20142 | 120.0897 | 120.1767 | -2.0279 | -2.0233 | 119.9295 | 120.0394 | 119.9066 | 119.9707
5808.1719 | 122.1863 | -118.895 | 3.1952 | -0.18898 | -0.040467 | -0.0033902 | 0.017382 | -0.00063233 | -0.013307 | -0.0053641 | 0.0021667 | 0.02176 | 0.015998 | -0.012119 | -0.018156 | 0.025058 | -0.0013073 | -0.11902 | 0 | -0.050354 | -0.050354 | 0.073242 | -0.068665 | 0.041199 | 0 | 0.10529 | -0.050354 | 0.036621 | 0.12817 | 0.064087 | 0.11444 | 118.8446 | -3.1952 | -3.2455 | 118.9682 | 118.9362 | 118.8263 | 0.091553 | -0.018311 | 118.8446 | -3.0899 | -3.1586 | 119.0231 | 119.0094 | 118.959 | 0.16479 | 0.11444 | 0.1236 | 0 | 0.17853 | 0.086975 | 0.050354 | 0.15564 | 118.895 | 119.0002 | -3.2455 | -3.2455 | 118.8446 | 118.9316 | 118.7759 | 118.895
5809.875 | 122.2549 | -120.8817 | 1.03 | -0.17372 | -0.042603 | 0.00088223 | 0.017596 | 0.0019311 | -0.012452 | -0.0057913 | 0.014374 | 0.023682 | 0.014717 | -0.019596 | -0.019651 | 0.024417 | -0.0034435 | -0.073242 | 0.013733 | -0.032043 | 0.004578 | 0.13733 | 0.022888 | 0.10986 | 0.086975 | 0.086975 | -0.045776 | 0.10071 | 0.19226 | 0.15106 | 0.17853 | 120.8496 | -1.0162 | -1.0254 | 121.019 | 120.9915 | 120.9045 | 0.14191 | 0.054931 | 120.8359 | -0.94299 | -0.92926 | 121.0739 | 121.0602 | 121.0327 | 0.2243 | 0.19684 | 0.16937 | 0.036621 | 0.23804 | 0.14648 | 0.045776 | 0.13275 | 120.8954 | 120.9686 | -1.062 | -1.0757 | 120.8862 | 120.9824 | 120.8084 | 120.9686
5811.6406 | 122.1039 | -120.9045 | 1.0849 | -0.11269 | -0.03833 | 0.0013094 | 0.021655 | 0.0042811 | -0.013307 | -0.0030141 | -0.15042 | 0.022828 | 0.015144 | -0.013187 | -0.019651 | 0.029544 | -0.0038709 | -0.13275 | 0.036621 | -0.068665 | -0.09613 | -0.045776 | -0.16479 | -0.050354 | -0.068665 | 0.10986 | -0.086975 | -0.013733 | 0.027466 | -0.045776 | 0.045776 | 120.8359 | -1.0483 | -1.181 | 120.8588 | 120.8542 | 120.7397 | 0.018311 | -0.09613 | 120.8176 | -0.97504 | -1.0986 | 120.932 | 120.9503 | 120.8588 | 0.13275 | 0.041199 | 0.022889 | -0.027465 | 0.11444 | 0.073242 | 0.10529 | 0.19684 | 120.9412 | 121.0144 | -1.1536 | -1.1719 | 120.8084 | 120.8908 | 120.7718 | 120.8359
5813.3281 | 122.1542 | -120.8221 | 1.1627 | -0.13557 | -0.041535 | -0.0016812 | 0.0208 | -0.0019141 | -0.013734 | -0.0072867 | -0.052765 | 0.02176 | 0.017921 | -0.015964 | -0.018156 | 0.025699 | -0.0023755 | -0.15564 | 0.045776 | -0.091553 | -0.11444 | -0.004578 | -0.11444 | -0.004578 | -0.068665 | 0.14648 | -0.082397 | -0.054932 | 0.050354 | -0.022888 | 0.045776 | 120.7306 | -1.1169 | -1.2772 | 120.8176 | 120.8176 | 120.7077 | 0.086975 | -0.022888 | 120.7397 | -1.0162 | -1.2177 | 120.8725 | 120.8679 | 120.7993 | 0.12817 | 0.059509 | 0.086975 | -0.022888 | 0.13275 | 0.027465 | 0.13733 | 0.22888 | 120.8679 | 120.9686 | -1.2543 | -1.2451 | 120.7077 | 120.7672 | 120.6665 | 120.7535
5815.1094 | 122.1542 | -120.8267 | 1.1581 | -0.15846 | -0.039612 | -0.007449 | 0.022937 | 0.00064947 | -0.012239 | -0.0028005 | -0.10464 | 0.021973 | 0.014503 | -0.013187 | -0.017942 | 0.026553 | -0.00088011 | -0.12817 | 0.050354 | -0.091553 | -0.10529 | -0.027466 | -0.16479 | -0.036621 | -0.050354 | 0.13733 | -0.10071 | -0.022888 | 0.041199 | -0.013733 | 0.054932 | 120.7352 | -1.1078 | -1.2634 | 120.7993 | 120.7901 | 120.6619 | 0.054932 | -0.073242 | 120.726 | -1.0208 | -1.181 | 120.8679 | 120.8817 | 120.813 | 0.15564 | 0.086975 | 0.064087 | -0.013733 | 0.14191 | 0.07782 | 0.14191 | 0.23804 | 120.8771 | 120.9641 | -1.2497 | -1.2589 | 120.7214 | 120.8038 | 120.6985 | 120.7764
5816.8281 | 122.1268 | -120.8588 | 1.1307 | -0.18135 | -0.036408 | -0.00082677 | 0.021441 | 0.0010767 | -0.009675 | -0.0055777 | -0.13211 | 0.023041 | 0.013435 | -0.010196 | -0.018797 | 0.026126 | -0.0032299 | -0.14648 | 0.041199 | -0.07782 | -0.11902 | -0.032043 | -0.15106 | -0.054932 | -0.07782 | 0.12817 | -0.091553 | -0.022888 | 0.018311 | -0.036621 | 0.059509 | 120.7809 | -1.0895 | -1.2497 | 120.8267 | 120.8038 | 120.7077 | 0.022888 | -0.073242 | 120.7672 | -1.0025 | -1.1536 | 120.8771 | 120.9183 | 120.8221 | 0.15106 | 0.054932 | 0.045777 | -0.041199 | 0.10986 | 0.068665 | 0.11902 | 0.21973 | 120.9 | 120.9869 | -1.2085 | -1.2222 | 120.7397 | 120.8359 | 120.7123 | 120.7809
5818.5938 | 122.1451 | -120.9366 | 1.0529 | -0.18135 | -0.038544 | 0.0013094 | 0.019305 | 0.0029993 | -0.012025 | -0.0051505 | -0.09549 | 0.022401 | 0.013435 | -0.0093417 | -0.016874 | 0.025699 | -0.0030163 | -0.13733 | 0.036621 | -0.073242 | -0.11444 | -0.027466 | -0.15564 | -0.036621 | -0.068665 | 0.10529 | -0.068665 | -0.018311 | 0.050354 | -0.022888 | 0.068665 | 120.8633 | -1.0162 | -1.1673 | 120.9091 | 120.9 | 120.7809 | 0.036621 | -0.082398 | 120.8679 | -0.94757 | -1.0712 | 120.9869 | 121.0052 | 120.9137 | 0.13733 | 0.045777 | 0.045776 | -0.041199 | 0.11902 | 0.050354 | 0.10986 | 0.17395 | 120.9732 | 121.0419 | -1.1261 | -1.1215 | 120.8221 | 120.9183 | 120.7993 | 120.8679
5820.2969 | 122.1725 | -120.9366 | 1.0666 | -0.089798 | -0.039185 | 0.00088223 | 0.019946 | 0.0023585 | -0.0088206 | -0.0010915 | -0.11075 | 0.022828 | 0.015571 | -0.0054965 | -0.018583 | 0.019931 | -0.0094251 | -0.091553 | 0.041199 | -0.073242 | -0.041199 | 0.059509 | -0.07782 | 0.032043 | 0.022888 | 0.1236 | -0.073242 | 0.027466 | 0.10071 | 0.022888 | 0.10071 | 120.8633 | -1.0254 | -1.1078 | 120.9961 | 120.9686 | 120.8588 | 0.10529 | -0.004578 | 120.8633 | -0.94299 | -1.0391 | 121.0373 | 121.0373 | 120.9595 | 0.17395 | 0.09613 | 0.13275 | 0.032043 | 0.17395 | 0.10071 | 0.11444 | 0.19684 | 120.9778 | 121.0602 | -1.1398 | -1.1398 | 120.8954 | 120.9641 | 120.845 | 120.9595
5822.0625 | 122.2549 | -120.9274 | 1.0208 | -0.15846 | -0.041962 | 2.7834e-05 | 0.016742 | 0.0023585 | -0.011598 | -0.0036551 | 0.0021667 | 0.023469 | 0.014503 | -0.015323 | -0.018369 | 0.027194 | -0.0040845 | -0.07782 | 0.004578 | -0.050354 | 0.013733 | 0.16479 | 0.018311 | 0.11444 | 0.091553 | 0.073242 | -0.050354 | 0.073242 | 0.19684 | 0.14648 | 0.16022 | 120.8771 | -1.0162 | -1.0071 | 121.0922 | 121.0419 | 120.9457 | 0.16479 | 0.068665 | 120.8771 | -0.94757 | -0.94757 | 121.1243 | 121.0876 | 121.0739 | 0.21057 | 0.19684 | 0.21515 | 0.064087 | 0.24719 | 0.1236 | 0.054932 | 0.1236 | 120.932 | 121.0007 | -1.0712 | -1.0712 | 120.9412 | 121.0007 | 120.8496 | 121.019
5823.75 | 122.2504 | -120.8496 | 1.0712 | -0.2195 | -0.040039 | 0.0010958 | 0.02016 | -0.0023413 | -0.0088206 | -0.0047231 | -0.064972 | 0.023682 | 0.012367 | -0.012973 | -0.020506 | 0.026126 | -0.0045117 | -0.059509 | 0.004578 | -0.045776 | 0.009155 | 0.11444 | -0.041199 | 0.068665 | 0.082397 | 0.086975 | -0.064087 | 0.10986 | 0.16937 | 0.1236 | 0.17395 | 120.8038 | -1.0666 | -1.062 | 120.9641 | 120.9183 | 120.8084 | 0.11444 | 0.004577 | 120.7855 | -0.98419 | -0.9613 | 121.019 | 121.0236 | 120.9732 | 0.23804 | 0.18768 | 0.16022 | 0.054931 | 0.23346 | 0.17395 | 0.050354 | 0.15106 | 120.8542 | 120.9366 | -1.1169 | -1.1353 | 120.8588 | 120.9595 | 120.7901 | 120.932
5825.5156 | 122.168 | -120.9 | 1.1124 | -0.15083 | -0.040039 | 0.002164 | 0.019946 | 0.0015039 | -0.012452 | -0.0030141 | -0.089386 | 0.023682 | 0.014289 | -0.011051 | -0.018583 | 0.024844 | 0.0010425 | -0.086975 | 0.054932 | -0.073242 | -0.050354 | 0.041199 | -0.07782 | 0.027466 | 0.027466 | 0.11444 | -0.07782 | 0.018311 | 0.10529 | 0.045776 | 0.09613 | 120.8267 | -1.0574 | -1.1627 | 120.9412 | 120.9274 | 120.8221 | 0.10071 | -0.004578 | 120.8221 | -0.99792 | -1.0941 | 121.0052 | 120.9961 | 120.9457 | 0.17395 | 0.1236 | 0.11444 | 0.022888 | 0.18311 | 0.096131 | 0.12817 | 0.19226 | 120.9549 | 121.0144 | -1.1856 | -1.1902 | 120.8496 | 120.9183 | 120.813 | 120.9274
5827.2812 | 122.1817 | -120.8862 | 1.1078 | -0.11269 | -0.040894 | 0.00088223 | 0.018664 | 0.0029993 | -0.013307 | -0.0055777 | -0.040558 | 0.023469 | 0.015998 | -0.0054965 | -0.019865 | 0.026767 | 0.00018809 | -0.12817 | 0.054932 | -0.07782 | -0.10071 | 0 | -0.10529 | -0.004578 | -0.050354 | 0.10529 | -0.086975 | 0 | 0.09613 | 0.022888 | 0.07782 | 120.8084 | -1.0529 | -1.2085 | 120.8862 | 120.8817 | 120.7809 | 0.073242 | -0.027466 | 120.7993 | -1.0025 | -1.1078 | 120.9824 | 120.9641 | 120.9091 | 0.16479 | 0.10986 | 0.07782 | -0.022888 | 0.1831 | 0.086975 | 0.13275 | 0.19226 | 120.9412 | 120.9915 | -1.1856 | -1.1948 | 120.7855 | 120.8862 | 120.7581 | 120.8359
5829.0469 | 122.1909 | -120.9137 | 1.1078 | -0.1432 | -0.040467 | -0.00039957 | 0.019732 | 0.0019311 | -0.014161 | -0.0066457 | -0.09549 | 0.023041 | 0.012794 | -0.0095553 | -0.017729 | 0.026553 | -0.0040845 | -0.082397 | 0.032043 | -0.059509 | -0.041199 | 0.059509 | -0.068665 | 0.018311 | 0.013733 | 0.11444 | -0.059509 | 0.013733 | 0.10529 | 0.059509 | 0.11444 | 120.8542 | -1.0757 | -1.149 | 120.9732 | 120.932 | 120.845 | 0.07782 | -0.009156 | 120.8542 | -0.99335 | -1.0941 | 121.019 | 121.0281 | 120.9732 | 0.17395 | 0.11902 | 0.11902 | 0.01831 | 0.16479 | 0.073242 | 0.091552 | 0.17395 | 120.9457 | 121.0281 | -1.1673 | -1.1673 | 120.8725 | 120.9274 | 120.8313 | 120.9274
5830.75 | 122.1451 | -120.9229 | 1.1398 | -0.17372 | -0.039826 | -0.00082677 | 0.019732 | -0.00041873 | -0.012239 | -0.0015189 | -0.0008851 | 0.022187 | 0.014289 | -0.014896 | -0.01901 | 0.025699 | -0.0015209 | -0.091553 | 0.004578 | -0.050354 | -0.050354 | 0.07782 | -0.036621 | 0.059509 | 0.004578 | 0.09613 | -0.068665 | -0.045776 | 0.07782 | 0.027466 | 0.064087 | 120.8725 | -1.1353 | -1.1902 | 121.0007 | 120.9824 | 120.8862 | 0.10986 | 0.013733 | 120.8542 | -1.0437 | -1.1856 | 121.0007 | 120.9869 | 120.9503 | 0.13275 | 0.096131 | 0.12817 | 0 | 0.14649 | 0.022889 | 0.054932 | 0.16479 | 120.9274 | 121.019 | -1.1902 | -1.2085 | 120.8725 | 120.8771 | 120.8313 | 120.9274
5832.5312 | 122.2733 | -120.8954 | 1.062 | -0.22713 | -0.041535 | 0.0010958 | 0.01781 | 0.0021447 | -0.011384 | -0.0038687 | -0.016144 | 0.02176 | 0.01493 | -0.011478 | -0.021147 | 0.02634 | -0.0066479 | -0.10529 | 0.018311 | -0.054932 | -0.036621 | 0.07782 | -0.036621 | 0.068665 | 0.045776 | 0.086975 | -0.064087 | 0.045776 | 0.17395 | 0.11902 | 0.14648 | 120.8405 | -1.0437 | -1.0986 | 120.9732 | 120.9641 | 120.8588 | 0.1236 | 0.018311 | 120.8313 | -0.97504 | -1.0162 | 121.0693 | 121.0419 | 121.0144 | 0.21057 | 0.18311 | 0.13275 | 0.018311 | 0.23804 | 0.10986 | 0.073243 | 0.15106 | 120.9137 | 120.9824 | -1.1169 | -1.1261 | 120.8588 | 120.9412 | 120.7901 | 120.9412
5834.2969 | 122.1863 | -120.9457 | 1.1032 | -0.1432 | -0.041535 | -0.00061317 | 0.022082 | 0.0029993 | -0.012666 | -0.0025869 | -0.064972 | 0.022828 | 0.014289 | -0.0067783 | -0.021147 | 0.025912 | -0.0045117 | -0.12817 | 0.032043 | -0.07782 | -0.082397 | 0.004578 | -0.091553 | -0.004578 | -0.050354 | 0.12817 | -0.07782 | -0.013733 | 0.091553 | 0.036621 | 0.10529 | 120.8679 | -1.0712 | -1.1856 | 120.9503 | 120.9412 | 120.8542 | 0.073242 | -0.013733 | 120.8679 | -0.97504 | -1.1169 | 121.0373 | 121.051 | 120.9824 | 0.18311 | 0.11444 | 0.082398 | -0.004577 | 0.16937 | 0.064087 | 0.10986 | 0.20599 | 120.9778 | 121.0739 | -1.181 | -1.181 | 120.8633 | 120.932 | 120.8176 | 120.8954
5836.0625 | 122.2321 | -120.9183 | 1.0391 | -0.15083 | -0.040467 | 0.00045503 | 0.018664 | -0.0025549 | -0.012666 | -0.0068593 | -0.0008851 | 0.021332 | 0.017066 | -0.0091281 | -0.018369 | 0.025272 | 0.0010425 | -0.11444 | 0.004578 | -0.050354 | -0.032043 | 0.07782 | -0.064087 | 0.045776 | 0.013733 | 0.10071 | -0.064087 | 0.018311 | 0.1236 | 0.064087 | 0.11444 | 120.8679 | -1.0345 | -1.0712 | 120.9961 | 120.9641 | 120.8542 | 0.09613 | -0.013733 | 120.8542 | -0.93842 | -1.0208 | 121.0419 | 121.0327 | 120.9824 | 0.17853 | 0.12817 | 0.12817 | 0.018311 | 0.18768 | 0.082398 | 0.054932 | 0.1648 | 120.9229 | 121.019 | -1.0895 | -1.1032 | 120.8862 | 120.9366 | 120.8038 | 120.932
5837.8438 | 122.2778 | -120.9412 | 1.0483 | -0.17372 | -0.042389 | -0.0023222 | 0.01781 | 0.0019311 | -0.013734 | -0.0049367 | -0.01004 | 0.021973 | 0.014503 | -0.017246 | -0.019865 | 0.023776 | -0.0013073 | -0.059509 | 0 | -0.045776 | 0.032043 | 0.15564 | 0.022888 | 0.10071 | 0.10071 | 0.073242 | -0.050354 | 0.082397 | 0.18768 | 0.16022 | 0.16022 | 120.8954 | -1.0483 | -1.0162 | 121.0968 | 121.0419 | 120.9641 | 0.14648 | 0.068664 | 120.8908 | -0.97504 | -0.96588 | 121.1288 | 121.1014 | 121.1014 | 0.21057 | 0.21057 | 0.20142 | 0.077819 | 0.23804 | 0.13275 | 0.045776 | 0.1236 | 120.9412 | 121.0144 | -1.0941 | -1.0986 | 120.9732 | 121.0236 | 120.8817 | 121.0419
5839.6094 | 122.1909 | -120.9641 | 1.0574 | -0.17372 | -0.039185 | 0.001523 | 0.023578 | 0.0034265 | -0.011384 | -0.0030141 | -0.1138 | 0.021332 | 0.015144 | -0.0091281 | -0.019651 | 0.026553 | -0.0010937 | -0.11902 | 0.036621 | -0.07782 | -0.086975 | -0.013733 | -0.15106 | -0.041199 | -0.036621 | 0.11444 | -0.068665 | -0.022888 | 0.045776 | 0 | 0.091553 | 120.8862 | -1.0208 | -1.1444 | 120.9503 | 120.9229 | 120.813 | 0.036621 | -0.073242 | 120.8954 | -0.94299 | -1.0803 | 121.0098 | 121.0556 | 120.9641 | 0.16022 | 0.068665 | 0.064087 | -0.009155 | 0.11444 | 0.045777 | 0.11444 | 0.18311 | 121.0007 | 121.0785 | -1.1353 | -1.1261 | 120.8771 | 120.9412 | 120.845 | 120.9274
5841.3125 | 122.1863 | -120.9824 | 1.0666 | -0.13557 | -0.041107 | -0.00018577 | 0.020587 | -0.0025549 | -0.013307 | -0.0019461 | -0.068024 | 0.023896 | 0.015144 | -0.0099827 | -0.020078 | 0.028049 | -0.0036573 | -0.14191 | 0.054932 | -0.086975 | -0.086975 | -0.009155 | -0.10071 | -0.009155 | -0.054932 | 0.13275 | -0.073242 | -0.022888 | 0.082397 | 0.018311 | 0.073242 | 120.8954 | -1.0117 | -1.1536 | 120.9732 | 120.9732 | 120.8817 | 0.07782 | -0.013733 | 120.9091 | -0.93384 | -1.0895 | 121.0648 | 121.0556 | 121.0007 | 0.14648 | 0.091553 | 0.07782 | 0 | 0.15564 | 0.050354 | 0.14191 | 0.20599 | 121.0373 | 121.1151 | -1.1536 | -1.1398 | 120.8954 | 120.9595 | 120.8405 | 120.9274
5843.1094 | 122.2733 | -120.9412 | 1.0483 | -0.1432 | -0.04068 | 0.00024143 | 0.015887 | -0.0012731 | -0.011598 | -0.0064321 | -0.028351 | 0.022614 | 0.013221 | -0.020023 | -0.020933 | 0.026126 | -0.0025891 | -0.073242 | 0.004578 | -0.045776 | 0.027466 | 0.14648 | 0.004578 | 0.10986 | 0.068665 | 0.09613 | -0.050354 | 0.050354 | 0.16937 | 0.1236 | 0.15564 | 120.8954 | -1.0437 | -1.0208 | 121.0876 | 121.051 | 120.9457 | 0.15564 | 0.050354 | 120.8908 | -0.95215 | -0.99792 | 121.1105 | 121.0968 | 121.0648 | 0.20599 | 0.17395 | 0.19226 | 0.073242 | 0.21973 | 0.10071 | 0.050354 | 0.14648 | 120.9457 | 121.0373 | -1.0941 | -1.0986 | 120.9686 | 120.9915 | 120.8679 | 121.0098
5844.875 | 122.2916 | -120.9641 | 1.0345 | -0.13557 | -0.040253 | -0.0014676 | 0.018664 | 0.00022207 | -0.012452 | -0.0066457 | -0.0069885 | 0.023896 | 0.014076 | -0.022373 | -0.020292 | 0.023349 | -0.00023931 | -0.050354 | -0.004578 | -0.032043 | 0.027466 | 0.16479 | 0.022888 | 0.10529 | 0.10071 | 0.073242 | -0.041199 | 0.059509 | 0.19226 | 0.16479 | 0.15564 | 120.932 | -1.0391 | -1.0071 | 121.1288 | 121.0693 | 120.9869 | 0.13733 | 0.054931 | 120.9229 | -0.9613 | -0.97504 | 121.1563 | 121.1197 | 121.1288 | 0.19684 | 0.20599 | 0.19684 | 0.059509 | 0.23346 | 0.10071 | 0.027465 | 0.11444 | 120.9595 | 121.0373 | -1.0666 | -1.0757 | 120.9915 | 121.0236 | 120.9137 | 121.0648
5846.6562 | 122.168 | -120.9915 | 1.0849 | -0.18898 | -0.039612 | -0.0010404 | 0.0208 | 0.0021447 | -0.012239 | -0.0040823 | -0.14127 | 0.025178 | 0.014289 | -0.01041 | -0.020506 | 0.027835 | -0.0019483 | -0.11902 | 0.036621 | -0.059509 | -0.09613 | -0.022888 | -0.14648 | -0.036621 | -0.082397 | 0.13275 | -0.073242 | -0.054932 | 0.018311 | -0.045776 | 0.050354 | 120.932 | -1.0483 | -1.181 | 120.9686 | 120.9549 | 120.845 | 0.022888 | -0.086975 | 120.9183 | -0.95215 | -1.1398 | 121.0098 | 121.0419 | 120.9457 | 0.1236 | 0.027466 | 0.036621 | -0.036621 | 0.091553 | 0.01831 | 0.09613 | 0.20599 | 121.0281 | 121.1243 | -1.1444 | -1.1581 | 120.8954 | 120.9366 | 120.8725 | 120.9091
5848.3594 | 122.2275 | -120.9824 | 1.0803 | -0.15846 | -0.04068 | -0.00061317 | 0.022296 | 0.0015039 | -0.010957 | -0.0030141 | -0.092438 | 0.023469 | 0.014717 | -0.015537 | -0.022215 | 0.027621 | -0.0064343 | -0.10071 | 0.036621 | -0.068665 | -0.041199 | 0.064087 | -0.086975 | 0.013733 | 0.022888 | 0.11902 | -0.064087 | 0.013733 | 0.10986 | 0.027466 | 0.10986 | 120.9137 | -1.0437 | -1.1215 | 121.0464 | 120.9961 | 120.8954 | 0.082398 | -0.01831 | 120.9183 | -0.9613 | -1.0666 | 121.0922 | 121.0922 | 121.0098 | 0.17395 | 0.091553 | 0.13275 | 0.027466 | 0.17395 | 0.07782 | 0.10529 | 0.18311 | 121.019 | 121.1014 | -1.149 | -1.1444 | 120.9412 | 120.9961 | 120.8817 | 121.0052
5850.0625 | 122.1817 | -121.0098 | 1.0895 | -0.1432 | -0.040039 | 2.7834e-05 | 0.016955 | -0.0038367 | -0.012666 | -0.0047231 | -0.013092 | 0.023682 | 0.016212 | -0.018741 | -0.01901 | 0.025058 | -0.0051525 | -0.10071 | 0.018311 | -0.054932 | -0.073242 | 0.032043 | -0.09613 | 0.022888 | -0.041199 | 0.11444 | -0.064087 | -0.050354 | 0.059509 | 0.009155 | 0.041199 | 120.9549 | -1.0712 | -1.1627 | 121.0419 | 121.0327 | 120.9137 | 0.07782 | -0.041198 | 120.9457 | -0.97504 | -1.1398 | 121.0693 | 121.051 | 121.019 | 0.10529 | 0.073242 | 0.086975 | -0.01831 | 0.1236 | 0.013733 | 0.073243 | 0.17853 | 121.0281 | 121.1243 | -1.1444 | -1.1536 | 120.9366 | 120.9595 | 120.9091 | 120.9686
5851.7812 | 122.2321 | -120.9641 | 1.0986 | -0.1432 | -0.038544 | 0.00066863 | 0.018664 | 0.0027857 | -0.012025 | -0.0047231 | -0.1138 | 0.024964 | 0.013862 | -0.0069919 | -0.018583 | 0.029117 | -0.0051525 | -0.082397 | 0.036621 | -0.064087 | -0.036621 | 0.064087 | -0.073242 | 0.032043 | 0.022888 | 0.11902 | -0.054932 | 0 | 0.12817 | 0.054932 | 0.10529 | 120.9 | -1.062 | -1.1353 | 121.0281 | 120.9961 | 120.8908 | 0.09613 | -0.009155 | 120.9091 | -0.97961 | -1.0986 | 121.0922 | 121.0693 | 121.019 | 0.16022 | 0.10986 | 0.12817 | 0.027466 | 0.18311 | 0.054932 | 0.10071 | 0.17395 | 121.0007 | 121.0831 | -1.1627 | -1.1536 | 120.9274 | 120.9641 | 120.8817 | 120.9869
5853.5312 | 122.3145 | -120.9137 | 1.0941 | -0.19661 | -0.037903 | 0.0013094 | 0.019305 | -0.00041873 | -0.010743 | -0.0047231 | -0.055817 | 0.021973 | 0.015144 | -0.012119 | -0.019438 | 0.026553 | -0.0010937 | -0.050354 | 0.004578 | -0.050354 | 0.018311 | 0.13275 | -0.036621 | 0.068665 | 0.10529 | 0.091553 | -0.059509 | 0.086975 | 0.18768 | 0.11444 | 0.17853 | 120.8633 | -1.0895 | -1.0757 | 121.0464 | 120.9824 | 120.8771 | 0.11902 | 0.013733 | 120.8542 | -1.0025 | -1.0071 | 121.1014 | 121.0922 | 121.0281 | 0.23804 | 0.17395 | 0.18311 | 0.068665 | 0.24719 | 0.14648 | 0.054932 | 0.15106 | 120.9183 | 121.0052 | -1.1444 | -1.1536 | 120.932 | 121.0007 | 120.8633 | 121.019
5855.2344 | 122.1725 | -120.9778 | 1.1398 | -0.13557 | -0.041962 | -0.00082677 | 0.021014 | 0.0019311 | -0.012025 | -0.0062185 | -0.058869 | 0.022614 | 0.013862 | -0.017887 | -0.021787 | 0.024844 | -0.00066651 | -0.14191 | 0.032043 | -0.082397 | -0.11444 | 0.009155 | -0.10986 | 0 | -0.059509 | 0.11444 | -0.082397 | -0.064087 | 0.054932 | 0.009155 | 0.045776 | 120.8954 | -1.1078 | -1.2543 | 120.9869 | 120.9778 | 120.8679 | 0.082397 | -0.027466 | 120.8954 | -1.0254 | -1.2039 | 121.0327 | 121.0236 | 120.9869 | 0.12817 | 0.091552 | 0.091552 | -0.032044 | 0.13733 | 0.01831 | 0.11444 | 0.19684 | 121.0098 | 121.0922 | -1.2222 | -1.2222 | 120.8633 | 120.9137 | 120.8359 | 120.9183
5856.9375 | 122.2504 | -120.932 | 1.1215 | -0.15846 | -0.040467 | -0.00082677 | 0.018237 | -0.0027685 | -0.014375 | -0.0047231 | -0.0008851 | 0.022187 | 0.014289 | -0.018314 | -0.019865 | 0.023563 | -0.00088011 | -0.07782 | 0.009155 | -0.036621 | 0 | 0.09613 | -0.009155 | 0.07782 | 0.036621 | 0.07782 | -0.041199 | 0 | 0.12817 | 0.064087 | 0.10071 | 120.8954 | -1.1124 | -1.1215 | 121.0281 | 121.0098 | 120.9229 | 0.11444 | 0.027466 | 120.8908 | -1.0437 | -1.1215 | 121.0602 | 121.0327 | 120.9961 | 0.14191 | 0.10529 | 0.13275 | 0.036621 | 0.16937 | 0.041199 | 0.045776 | 0.11902 | 120.9412 | 121.0098 | -1.1581 | -1.1627 | 120.932 | 120.932 | 120.8542 | 120.9686
5858.6719 | 122.3145 | -120.8908 | 1.1078 | -0.2195 | -0.037689 | 0.0019504 | 0.018664 | -0.0021277 | -0.0098886 | -0.00045074 | -0.046661 | 0.022187 | 0.016212 | -0.015323 | -0.019651 | 0.026981 | -0.0023755 | -0.064087 | -0.009155 | -0.036621 | 0.032043 | 0.12817 | -0.018311 | 0.07782 | 0.09613 | 0.086975 | -0.054932 | 0.082397 | 0.16022 | 0.11444 | 0.15106 | 120.8542 | -1.1169 | -1.0757 | 121.019 | 120.9686 | 120.8725 | 0.11444 | 0.01831 | 120.8359 | -1.0208 | -1.0254 | 121.051 | 121.0419 | 121.0052 | 0.20599 | 0.16937 | 0.1648 | 0.068664 | 0.21515 | 0.13733 | 0.027466 | 0.14191 | 120.8817 | 120.9778 | -1.1444 | -1.1627 | 120.9229 | 120.9732 | 120.8267 | 120.9869
5860.3594 | 122.2504 | -120.9137 | 1.1536 | -0.18898 | -0.038971 | 0.00045503 | 0.021014 | 0.0017175 | -0.01352 | -0.0057913 | -0.11075 | 0.026246 | 0.012367 | -0.011051 | -0.019438 | 0.027194 | -0.0015209 | -0.10529 | 0.022888 | -0.068665 | -0.036621 | 0.059509 | -0.064087 | 0.022888 | 0.018311 | 0.11444 | -0.073242 | 0.018311 | 0.10986 | 0.050354 | 0.09613 | 120.845 | -1.1307 | -1.1902 | 120.9732 | 120.9366 | 120.8496 | 0.091553 | 0.004578 | 120.8405 | -1.0391 | -1.1353 | 121.0236 | 121.0098 | 120.9641 | 0.16937 | 0.1236 | 0.12817 | 0.032044 | 0.18311 | 0.091553 | 0.091553 | 0.18768 | 120.9366 | 121.0281 | -1.2222 | -1.2268 | 120.8771 | 120.932 | 120.8084 | 120.932
5862.0781 | 122.2275 | -120.9091 | 1.1993 | -0.097427 | -0.040253 | -0.00061317 | 0.02016 | 0.0017175 | -0.014588 | -0.0055777 | -0.064972 | 0.024964 | 0.016212 | -0.015964 | -0.020506 | 0.024631 | -0.0034435 | -0.13275 | 0.059509 | -0.073242 | -0.10529 | -0.018311 | -0.10986 | -0.004578 | -0.068665 | 0.1236 | -0.064087 | -0.032043 | 0.059509 | 0.018311 | 0.073242 | 120.8359 | -1.1398 | -1.3046 | 120.8908 | 120.9045 | 120.7993 | 0.068664 | -0.036621 | 120.845 | -1.0757 | -1.2314 | 120.9686 | 120.9824 | 120.9274 | 0.13733 | 0.082398 | 0.054931 | -0.032044 | 0.1236 | 0.032044 | 0.13275 | 0.18768 | 120.9686 | 121.0327 | -1.2726 | -1.2634 | 120.8038 | 120.8771 | 120.7764 | 120.8405
5863.7812 | 122.2733 | -120.7855 | 1.2314 | -0.18898 | -0.040894 | 0.0025912 | 0.018451 | -0.00084593 | -0.012666 | -0.0066457 | -0.034454 | 0.023469 | 0.013221 | -0.01575 | -0.01901 | 0.025699 | -0.00023931 | -0.073242 | -0.004578 | -0.036621 | 0 | 0.11902 | -0.050354 | 0.073242 | 0.059509 | 0.073242 | -0.041199 | 0.032043 | 0.11902 | 0.07782 | 0.11902 | 120.7489 | -1.236 | -1.2314 | 120.9045 | 120.8588 | 120.7352 | 0.10986 | -0.013733 | 120.7443 | -1.1581 | -1.1993 | 120.9045 | 120.9045 | 120.8633 | 0.16022 | 0.11902 | 0.15564 | 0.036621 | 0.16022 | 0.073242 | 0.032043 | 0.11444 | 120.7809 | 120.8588 | -1.268 | -1.2726 | 120.7855 | 120.8176 | 120.7123 | 120.845
5865.5938 | 122.3099 | -120.7489 | 1.2543 | -0.24239 | -0.040894 | 0.0017368 | 0.017382 | 0.0049219 | -0.010316 | -0.0042959 | -0.04361 | 0.022187 | 0.013435 | -0.017459 | -0.020078 | 0.025699 | -0.0023755 | -0.073242 | 0 | -0.032043 | 0.022888 | 0.14191 | -0.022888 | 0.082397 | 0.10071 | 0.082397 | -0.045776 | 0.073242 | 0.16937 | 0.10529 | 0.16937 | 120.7169 | -1.2543 | -1.2314 | 120.8908 | 120.8313 | 120.726 | 0.11444 | 0.009155 | 120.7031 | -1.1719 | -1.181 | 120.9183 | 120.9183 | 120.8542 | 0.21515 | 0.15106 | 0.17395 | 0.054931 | 0.21515 | 0.11902 | 0.032043 | 0.12817 | 120.7489 | 120.8313 | -1.2863 | -1.3 | 120.7718 | 120.8221 | 120.6757 | 120.8496
5867.2969 | 122.2321 | -120.7764 | 1.3458 | -0.12032 | -0.041107 | -0.0014676 | 0.0208 | -0.0017005 | -0.012452 | -0.0042959 | -0.071076 | 0.023682 | 0.015785 | -0.01276 | -0.019865 | 0.025058 | -0.0049389 | -0.14648 | 0.032043 | -0.086975 | -0.09613 | -0.013733 | -0.11902 | -0.013733 | -0.059509 | 0.1236 | -0.07782 | -0.050354 | 0.073242 | 0.013733 | 0.07782 | 120.6894 | -1.3138 | -1.442 | 120.7626 | 120.7626 | 120.6573 | 0.073242 | -0.032044 | 120.6985 | -1.2222 | -1.3962 | 120.8496 | 120.8542 | 120.7901 | 0.15564 | 0.091553 | 0.073242 | -0.009155 | 0.15106 | 0.027466 | 0.11902 | 0.20142 | 120.8084 | 120.9 | -1.4328 | -1.4236 | 120.6802 | 120.726 | 120.6299 | 120.7169
5869 | 122.3419 | -120.7031 | 1.3321 | -0.13557 | -0.041962 | -0.001254 | 0.017382 | 8.47e-06 | -0.012879 | -0.0068593 | -0.013092 | 0.022614 | 0.014076 | -0.013614 | -0.022215 | 0.024844 | -0.0010937 | -0.082397 | 0.004578 | -0.045776 | 0.022888 | 0.15106 | 0.013733 | 0.1236 | 0.10986 | 0.07782 | -0.050354 | 0.091553 | 0.20142 | 0.16479 | 0.16022 | 120.6573 | -1.3275 | -1.3092 | 120.8542 | 120.8267 | 120.7169 | 0.16937 | 0.059509 | 120.6528 | -1.2543 | -1.2405 | 120.9045 | 120.8633 | 120.8679 | 0.21057 | 0.21515 | 0.19684 | 0.068664 | 0.25177 | 0.14191 | 0.050354 | 0.12817 | 120.7077 | 120.7809 | -1.3779 | -1.3824 | 120.726 | 120.7947 | 120.6207 | 120.813
5870.7031 | 122.3328 | -120.6619 | 1.355 | -0.17372 | -0.038117 | 0.0013094 | 0.019519 | 0.00022207 | -0.012239 | -0.0034415 | -0.083283 | 0.023041 | 0.012794 | -0.0099827 | -0.02136 | 0.027621 | -0.0019483 | -0.059509 | 0 | -0.045776 | 0.013733 | 0.10529 | -0.027466 | 0.07782 | 0.082397 | 0.091553 | -0.036621 | 0.09613 | 0.16479 | 0.10529 | 0.17395 | 120.6161 | -1.355 | -1.3412 | 120.7672 | 120.7397 | 120.6345 | 0.1236 | 0.01831 | 120.6253 | -1.2634 | -1.2589 | 120.8267 | 120.8359 | 120.7672 | 0.21057 | 0.14191 | 0.15106 | 0.059509 | 0.20142 | 0.13275 | 0.045776 | 0.12817 | 120.6619 | 120.7535 | -1.4008 | -1.3916 | 120.6757 | 120.7581 | 120.6024 | 120.7443
5872.3906 | 122.2687 | -120.6802 | 1.4191 | -0.12794 | -0.040894 | 2.7834e-05 | 0.019519 | -0.00020513 | -0.016084 | -0.0042959 | -0.098541 | 0.022401 | 0.015998 | -0.011905 | -0.01901 | 0.028903 | -0.0038709 | -0.11902 | 0.032043 | -0.073242 | -0.064087 | -0.004578 | -0.10071 | 0.004578 | -0.022888 | 0.11444 | -0.086975 | 0 | 0.09613 | 0.032043 | 0.09613 | 120.607 | -1.387 | -1.4832 | 120.6757 | 120.6848 | 120.5795 | 0.07782 | -0.027466 | 120.5933 | -1.3046 | -1.4191 | 120.7764 | 120.7764 | 120.7123 | 0.1831 | 0.11902 | 0.068664 | 0.009155 | 0.1831 | 0.086975 | 0.10529 | 0.20142 | 120.7123 | 120.7947 | -1.4923 | -1.506 | 120.6162 | 120.6802 | 120.5612 | 120.6573
5874.1406 | 122.2229 | -120.7581 | 1.355 | -0.18898 | -0.039612 | 0.0028048 | 0.021228 | 0.0040675 | -0.012025 | -0.0036551 | -0.12906 | 0.024964 | 0.016212 | -0.012546 | -0.020506 | 0.027621 | -0.0034435 | -0.13275 | 0.041199 | -0.07782 | -0.10071 | -0.032043 | -0.16479 | -0.036621 | -0.086975 | 0.12817 | -0.07782 | -0.041199 | 0.022888 | -0.032043 | 0.064087 | 120.6802 | -1.3138 | -1.4557 | 120.726 | 120.7214 | 120.5933 | 0.041199 | -0.086975 | 120.6802 | -1.2268 | -1.3962 | 120.7809 | 120.8221 | 120.726 | 0.14191 | 0.045777 | 0.045777 | -0.022888 | 0.10071 | 0.036621 | 0.11902 | 0.20599 | 120.7993 | 120.8862 | -1.4328 | -1.4328 | 120.6573 | 120.7169 | 120.6253 | 120.6711
5875.8594 | 122.3328 | -120.7718 | 1.2863 | -0.19661 | -0.041321 | -0.0016812 | 0.016955 | -0.0038367 | -0.012452 | -0.0032277 | 0.0082703 | 0.020051 | 0.015144 | -0.014896 | -0.017088 | 0.025272 | -0.0045117 | -0.082397 | 0.004578 | -0.032043 | 0.022888 | 0.15106 | 0.013733 | 0.10071 | 0.086975 | 0.068665 | -0.054932 | 0.064087 | 0.19226 | 0.12817 | 0.14648 | 120.7397 | -1.2817 | -1.2634 | 120.9229 | 120.8725 | 120.7855 | 0.13275 | 0.045776 | 120.7169 | -1.2177 | -1.2222 | 120.9641 | 120.9183 | 120.9 | 0.20142 | 0.18311 | 0.18311 | 0.054931 | 0.24719 | 0.11902 | 0.036621 | 0.1236 | 120.7764 | 120.8405 | -1.3184 | -1.3412 | 120.7947 | 120.8359 | 120.6894 | 120.8588
5877.625 | 122.3099 | -120.7672 | 1.3 | -0.15083 | -0.038117 | 0.0010958 | 0.018664 | -0.00041873 | -0.011384 | -0.0042959 | -0.046661 | 0.022828 | 0.015998 | -0.015537 | -0.018797 | 0.026126 | -0.0047253 | -0.09613 | 0.004578 | -0.032043 | 0.009155 | 0.10986 | -0.064087 | 0.064087 | 0.054932 | 0.073242 | -0.045776 | 0.018311 | 0.1236 | 0.086975 | 0.12817 | 120.7352 | -1.2955 | -1.2909 | 120.8771 | 120.8313 | 120.7031 | 0.09613 | -0.032044 | 120.7214 | -1.2268 | -1.2817 | 120.8908 | 120.8954 | 120.8542 | 0.17395 | 0.13275 | 0.14191 | 0.041198 | 0.16937 | 0.064087 | 0.036621 | 0.11902 | 120.7718 | 120.8405 | -1.3321 | -1.3458 | 120.7764 | 120.7855 | 120.6711 | 120.8221
5879.3438 | 122.2641 | -120.8221 | 1.2772 | -0.11269 | -0.039826 | 2.7834e-05 | 0.021441 | -0.0014867 | -0.013734 | -0.0034415 | -0.1138 | 0.023469 | 0.015357 | -0.014682 | -0.022001 | 0.02634 | -0.00045291 | -0.09613 | 0.027466 | -0.07782 | -0.022888 | 0.064087 | -0.073242 | 0.032043 | 0.022888 | 0.10529 | -0.064087 | 0.013733 | 0.091553 | 0.018311 | 0.091553 | 120.7443 | -1.2497 | -1.3 | 120.8862 | 120.8542 | 120.7489 | 0.10986 | 0.004578 | 120.7581 | -1.1719 | -1.2634 | 120.9137 | 120.9137 | 120.8405 | 0.15564 | 0.082398 | 0.14191 | 0.054932 | 0.15564 | 0.07782 | 0.10529 | 0.16937 | 120.8496 | 120.9274 | -1.355 | -1.3412 | 120.7993 | 120.8359 | 120.726 | 120.845
5881.0781 | 122.319 | -120.7947 | 1.268 | -0.15083 | -0.039826 | 0.0010958 | 0.019091 | -0.00020513 | -0.01352 | -0.0057913 | 0.0052185 | 0.023896 | 0.013862 | -0.0134 | -0.018369 | 0.026767 | -0.0019483 | -0.11444 | 0.009155 | -0.054932 | -0.041199 | 0.068665 | -0.054932 | 0.041199 | 0.022888 | 0.11444 | -0.050354 | 0.032043 | 0.13733 | 0.10071 | 0.12817 | 120.7397 | -1.2589 | -1.3092 | 120.8633 | 120.8359 | 120.7397 | 0.096131 | 0 | 120.7443 | -1.1536 | -1.236 | 120.932 | 120.9229 | 120.8954 | 0.17853 | 0.15106 | 0.1236 | 0.013733 | 0.18768 | 0.082397 | 0.064087 | 0.16479 | 120.8038 | 120.9091 | -1.3229 | -1.3184 | 120.7535 | 120.8267 | 120.6802 | 120.8176
5882.7969 | 122.2321 | -120.8588 | 1.2955 | -0.1432 | -0.037903 | 0.00066863 | 0.019305 | -0.00063233 | -0.012239 | -0.0021597 | -0.1138 | 0.023682 | 0.016212 | -0.0067783 | -0.020292 | 0.026981 | -0.0042981 | -0.10529 | 0.036621 | -0.073242 | -0.064087 | 0.018311 | -0.12817 | -0.004578 | -0.032043 | 0.1236 | -0.073242 | -0.050354 | 0.041199 | -0.045776 | 0.045776 | 120.7855 | -1.2589 | -1.3596 | 120.8771 | 120.8542 | 120.7306 | 0.068664 | -0.054932 | 120.7855 | -1.1719 | -1.3458 | 120.9 | 120.9045 | 120.813 | 0.11902 | 0.027466 | 0.091553 | 0.009155 | 0.11444 | 0.022888 | 0.10986 | 0.19684 | 120.8954 | 120.9824 | -1.3687 | -1.3687 | 120.7947 | 120.8084 | 120.7535 | 120.8267
5884.5 | 122.3557 | -120.7993 | 1.2497 | -0.2195 | -0.040467 | -0.00039957 | 0.017169 | -0.0059729 | -0.014375 | -0.0066457 | -0.019196 | 0.022401 | 0.015998 | -0.017032 | -0.021574 | 0.025699 | -0.0042981 | -0.073242 | -0.004578 | -0.041199 | 0.036621 | 0.16022 | 0.004578 | 0.10071 | 0.091553 | 0.091553 | -0.050354 | 0.073242 | 0.21057 | 0.1236 | 0.16022 | 120.7581 | -1.2543 | -1.2131 | 120.9595 | 120.9 | 120.8038 | 0.14191 | 0.045777 | 120.7489 | -1.1581 | -1.1765 | 121.0098 | 120.9595 | 120.9229 | 0.21057 | 0.17395 | 0.20142 | 0.07782 | 0.26093 | 0.1236 | 0.036621 | 0.14191 | 120.7947 | 120.8908 | -1.2909 | -1.3 | 120.8359 | 120.8725 | 120.726 | 120.8908
5886.25 | 122.2824 | -120.8496 | 1.2863 | -0.15846 | -0.039826 | 2.7834e-05 | 0.022723 | 0.0017175 | -0.012452 | -0.0049367 | -0.06192 | 0.02176 | 0.015571 | -0.0091281 | -0.018369 | 0.027621 | -0.0055799 | -0.10986 | 0.045776 | -0.09613 | -0.073242 | 0.004578 | -0.091553 | 0.004578 | -0.036621 | 0.12817 | -0.07782 | -0.027466 | 0.09613 | 0.022888 | 0.10071 | 120.7535 | -1.2405 | -1.3596 | 120.8542 | 120.8542 | 120.7581 | 0.10071 | 0.004577 | 120.7718 | -1.1581 | -1.3138 | 120.9457 | 120.9503 | 120.8725 | 0.17853 | 0.10071 | 0.10071 | 0.022888 | 0.17395 | 0.050354 | 0.14191 | 0.20599 | 120.8954 | 120.9778 | -1.3824 | -1.3641 | 120.7764 | 120.8221 | 120.7397 | 120.813
5887.9844 | 122.2549 | -120.8405 | 1.2817 | -0.12794 | -0.039398 | 0.00024143 | 0.018451 | 0.00022207 | -0.012879 | -0.0038687 | -0.034454 | 0.024323 | 0.014076 | -0.010196 | -0.018797 | 0.026981 | -2.571e-05 | -0.086975 | 0.018311 | -0.068665 | -0.050354 | 0.036621 | -0.068665 | 0.027466 | -0.036621 | 0.10071 | -0.07782 | -0.041199 | 0.082397 | 0.027466 | 0.054932 | 120.7718 | -1.2634 | -1.3321 | 120.8771 | 120.8679 | 120.7718 | 0.096131 | 0 | 120.7626 | -1.181 | -1.3229 | 120.9229 | 120.8954 | 120.8679 | 0.13275 | 0.10529 | 0.10529 | 0.018311 | 0.16022 | 0.036621 | 0.086976 | 0.17853 | 120.8588 | 120.9412 | -1.3504 | -1.3596 | 120.7901 | 120.7993 | 120.7535 | 120.8038
5889.7344 | 122.319 | -120.8633 | 1.2405 | -0.21187 | -0.039398 | 0.0013094 | 0.019091 | -0.00063233 | -0.012239 | -0.0064321 | -0.040558 | 0.02176 | 0.01493 | -0.016605 | -0.019224 | 0.025272 | -0.0025891 | -0.10986 | 0.018311 | -0.041199 | -0.022888 | 0.073242 | -0.064087 | 0.041199 | 0.018311 | 0.086975 | -0.045776 | 0.004578 | 0.11444 | 0.068665 | 0.11444 | 120.8221 | -1.2222 | -1.2634 | 120.9366 | 120.9045 | 120.7993 | 0.082398 | -0.022888 | 120.8176 | -1.1536 | -1.236 | 120.9778 | 120.9778 | 120.932 | 0.16022 | 0.11444 | 0.11444 | 0.018311 | 0.16022 | 0.050354 | 0.05951 | 0.13275 | 120.8817 | 120.9503 | -1.2817 | -1.2863 | 120.8405 | 120.8679 | 120.7535 | 120.8817
5891.4219 | 122.2458 | -120.8725 | 1.2589 | -0.12032 | -0.041107 | -0.0021084 | 0.0208 | -0.00063233 | -0.011598 | -0.0032277 | -0.089386 | 0.023255 | 0.016639 | -0.016605 | -0.019651 | 0.02634 | -0.0017347 | -0.13275 | 0.045776 | -0.091553 | -0.10071 | -0.009155 | -0.11902 | -0.018311 | -0.059509 | 0.13275 | -0.091553 | -0.050354 | 0.059509 | 0.004578 | 0.059509 | 120.7809 | -1.2131 | -1.3596 | 120.8633 | 120.8542 | 120.7535 | 0.073242 | -0.027466 | 120.7809 | -1.1261 | -1.3092 | 120.932 | 120.932 | 120.8771 | 0.15106 | 0.096131 | 0.082398 | -0.009155 | 0.15106 | 0.041199 | 0.13733 | 0.2243 | 120.9183 | 121.0052 | -1.3504 | -1.3504 | 120.7718 | 120.8221 | 120.7397 | 120.813
5893.125 | 122.3419 | -120.9045 | 1.2039 | -0.18135 | -0.040467 | 0.00088223 | 0.017382 | -0.00020513 | -0.013093 | -0.0049367 | -0.013092 | 0.023682 | 0.014717 | -0.0134 | -0.020292 | 0.024204 | -0.0042981 | -0.10529 | -0.009155 | -0.036621 | -0.045776 | 0.059509 | -0.059509 | 0.050354 | -0.009155 | 0.091553 | -0.073242 | 0.018311 | 0.12817 | 0.064087 | 0.11902 | 120.8679 | -1.2131 | -1.2497 | 120.9641 | 120.9549 | 120.845 | 0.086975 | -0.022888 | 120.8313 | -1.1124 | -1.1856 | 121.0327 | 121.0236 | 120.9686 | 0.19226 | 0.13733 | 0.09613 | -0.009155 | 0.20142 | 0.091553 | 0.027466 | 0.16479 | 120.8954 | 120.9961 | -1.2405 | -1.2772 | 120.8588 | 120.9229 | 120.7993 | 120.8954
5894.8281 | 122.2412 | -120.7672 | 1.3824 | -0.18135 | -0.038544 | 0.0010958 | 0.021869 | 0.0029993 | -0.012879 | -0.0038687 | -0.12906 | 0.023682 | 0.015357 | -0.01041 | -0.019224 | 0.027194 | -0.0023755 | -0.1236 | 0.064087 | -0.068665 | -0.10986 | -0.050354 | -0.16479 | -0.045776 | -0.10986 | 0.13275 | -0.086975 | -0.041199 | 0.022888 | -0.022888 | 0.059509 | 120.6985 | -1.3184 | -1.4923 | 120.7169 | 120.7214 | 120.6024 | 0.022889 | -0.09613 | 120.6802 | -1.2497 | -1.4236 | 120.7901 | 120.8267 | 120.7443 | 0.14648 | 0.064087 | 0.018311 | -0.041198 | 0.10986 | 0.045776 | 0.13275 | 0.21973 | 120.8313 | 120.9 | -1.4511 | -1.4694 | 120.6573 | 120.726 | 120.6436 | 120.6573
5896.5938 | 122.3969 | -120.6802 | 1.3733 | -0.23476 | -0.039826 | -0.0010404 | 0.019519 | 0.0036401 | -0.01117 | -0.0055777 | -0.058869 | 0.021973 | 0.015998 | -0.015537 | -0.019438 | 0.02634 | -0.0010937 | -0.041199 | 0 | -0.041199 | 0.018311 | 0.12817 | -0.041199 | 0.059509 | 0.091553 | 0.086975 | -0.045776 | 0.09613 | 0.16022 | 0.10986 | 0.17395 | 120.639 | -1.3733 | -1.355 | 120.8084 | 120.7397 | 120.639 | 0.10071 | 0 | 120.6345 | -1.2863 | -1.2772 | 120.8405 | 120.8542 | 120.7901 | 0.21973 | 0.15564 | 0.16937 | 0.05951 | 0.20599 | 0.14191 | 0.041199 | 0.13275 | 120.6802 | 120.7672 | -1.4145 | -1.4191 | 120.6985 | 120.7764 | 120.639 | 120.7718
5898.3125 | 122.3007 | -119.5999 | 2.536 | -0.12032 | -0.039612 | -0.0010404 | 0.021228 | -0.0012731 | -0.01352 | -0.0064321 | -0.092438 | 0.021973 | 0.015357 | -0.0078463 | -0.020506 | 0.025485 | -0.0055799 | -0.10071 | 0.064087 | -0.064087 | -0.045776 | 0.045776 | -0.07782 | 0.022888 | 0.004578 | 0.11444 | -0.082397 | 0.004578 | 0.10986 | 0.032043 | 0.09613 | 119.5358 | -2.4719 | -2.5818 | 119.6457 | 119.6228 | 119.5221 | 0.086975 | -0.013733 | 119.5175 | -2.4216 | -2.5314 | 119.7098 | 119.696 | 119.632 | 0.17853 | 0.11444 | 0.10986 | 0.018311 | 0.19226 | 0.086975 | 0.12817 | 0.19684 | 119.664 | 119.7144 | -2.6001 | -2.6184 | 119.5541 | 119.6045 | 119.4992 | 119.6045
5900.0469 | 122.3877 | -120.7947 | 1.2772 | -0.2195 | -0.038758 | 0.0023776 | 0.021228 | 0.00043587 | -0.010743 | -0.0060049 | -0.06192 | 0.024964 | 0.015571 | -0.01041 | -0.01901 | 0.027621 | -0.00045291 | -0.10071 | 0.009155 | -0.068665 | -0.018311 | 0.09613 | -0.036621 | 0.059509 | 0.059509 | 0.09613 | -0.059509 | 0.086975 | 0.16479 | 0.09613 | 0.17395 | 120.726 | -1.268 | -1.2955 | 120.8908 | 120.8542 | 120.7581 | 0.12817 | 0.032044 | 120.7352 | -1.181 | -1.1902 | 120.9595 | 120.9686 | 120.8908 | 0.23346 | 0.15564 | 0.16479 | 0.050354 | 0.2243 | 0.14648 | 0.07782 | 0.15564 | 120.8038 | 120.8908 | -1.3458 | -1.3367 | 120.7764 | 120.8817 | 120.694 | 120.8542
5901.7812 | 122.4014 | -120.7855 | 1.3229 | -0.18135 | -0.042176 | -0.0021084 | 0.018664 | 0.00064947 | -0.015016 | -0.0045095 | 0.0021667 | 0.021973 | 0.014717 | -0.013828 | -0.02136 | 0.024844 | -0.0030163 | -0.068665 | -0.022888 | -0.045776 | 0.027466 | 0.16937 | 0.018311 | 0.10986 | 0.09613 | 0.09613 | -0.050354 | 0.064087 | 0.19684 | 0.14648 | 0.15564 | 120.7397 | -1.3458 | -1.2955 | 120.9549 | 120.8954 | 120.8038 | 0.15564 | 0.064087 | 120.7352 | -1.2268 | -1.2589 | 120.9824 | 120.9412 | 120.932 | 0.20599 | 0.19684 | 0.21515 | 0.073242 | 0.24719 | 0.11444 | 0.022888 | 0.14648 | 120.7626 | 120.8817 | -1.3687 | -1.3733 | 120.813 | 120.8496 | 120.7169 | 120.8817
5903.5156 | 122.2687 | -120.8038 | 1.355 | -0.15083 | -0.04068 | -0.0023222 | 0.018664 | 0.00043587 | -0.010957 | -0.0075003 | -0.06192 | 0.025178 | 0.016639 | -0.011905 | -0.018583 | 0.025272 | -0.0057935 | -0.15106 | 0.036621 | -0.07782 | -0.10071 | 0.009155 | -0.09613 | 0 | -0.073242 | 0.10529 | -0.059509 | -0.073242 | 0.036621 | -0.013733 | 0.050354 | 120.726 | -1.3184 | -1.4557 | 120.813 | 120.8038 | 120.7077 | 0.07782 | -0.01831 | 120.7443 | -1.2497 | -1.4282 | 120.8405 | 120.8542 | 120.7901 | 0.10986 | 0.045776 | 0.086975 | -0.022888 | 0.09613 | -0.013733 | 0.11444 | 0.16479 | 120.8405 | 120.9091 | -1.4328 | -1.4145 | 120.7031 | 120.7306 | 120.6528 | 120.7306
5905.25 | 122.2733 | -120.8221 | 1.3687 | -0.082169 | -0.040039 | -0.0021084 | 0.019732 | 0.0019311 | -0.010957 | -0.0036551 | -0.068024 | 0.024323 | 0.015357 | -0.010623 | -0.020719 | 0.025699 | -0.0040845 | -0.13733 | 0.059509 | -0.073242 | -0.10986 | -0.004578 | -0.10529 | -0.009155 | -0.07782 | 0.1236 | -0.086975 | -0.054932 | 0.041199 | 0 | 0.073242 | 120.7489 | -1.3092 | -1.4786 | 120.8176 | 120.813 | 120.7169 | 0.064087 | -0.032044 | 120.7352 | -1.2451 | -1.4236 | 120.8633 | 120.8954 | 120.8221 | 0.16022 | 0.086975 | 0.068664 | -0.036621 | 0.12817 | 0.032043 | 0.13275 | 0.21057 | 120.8817 | 120.9457 | -1.442 | -1.4557 | 120.7123 | 120.7672 | 120.6848 | 120.7443
5906.9844 | 122.374 | -120.7489 | 1.3641 | -0.13557 | -0.041962 | -0.00039957 | 0.018023 | -0.0012731 | -0.014802 | -0.0049367 | 0.0052185 | 0.023682 | 0.01493 | -0.0134 | -0.019224 | 0.025485 | -0.0019483 | -0.073242 | -0.009155 | -0.050354 | 0.032043 | 0.14648 | 0.009155 | 0.10071 | 0.086975 | 0.073242 | -0.059509 | 0.054932 | 0.17853 | 0.11902 | 0.15564 | 120.6985 | -1.3733 | -1.3321 | 120.8954 | 120.8496 | 120.7581 | 0.15106 | 0.059509 | 120.6894 | -1.2909 | -1.3092 | 120.9274 | 120.9045 | 120.8679 | 0.21515 | 0.17853 | 0.19684 | 0.082397 | 0.23804 | 0.11444 | 0.041199 | 0.13275 | 120.7397 | 120.8221 | -1.4145 | -1.4236 | 120.7809 | 120.8038 | 120.6757 | 120.8359
5908.7188 | 122.3419 | -120.7489 | 1.3824 | -0.097427 | -0.040467 | -0.00082677 | 0.019946 | -0.0017005 | -0.010316 | -0.0030141 | -0.086334 | 0.023682 | 0.011939 | -0.011478 | -0.019438 | 0.026126 | -0.0051525 | -0.11444 | 0.041199 | -0.07782 | -0.07782 | 0 | -0.11444 | -0.004578 | -0.050354 | 0.1236 | -0.086975 | -0.009155 | 0.091553 | 0.018311 | 0.091553 | 120.6711 | -1.3412 | -1.4603 | 120.7489 | 120.7443 | 120.6345 | 0.073242 | -0.036621 | 120.6619 | -1.2589 | -1.3916 | 120.8405 | 120.8405 | 120.7672 | 0.17853 | 0.10529 | 0.07782 | 0 | 0.17853 | 0.07782 | 0.11902 | 0.21057 | 120.7901 | 120.8725 | -1.4603 | -1.4694 | 120.6711 | 120.7397 | 120.6345 | 120.6985
5910.4688 | 122.287 | -120.7489 | 1.4191 | -0.13557 | -0.040894 | -0.00082677 | 0.018878 | -0.0040503 | -0.012239 | -0.0060049 | -0.034454 | 0.022187 | 0.013862 | -0.017887 | -0.020719 | 0.025699 | -0.0036573 | -0.10529 | 0.013733 | -0.068665 | -0.059509 | 0.050354 | -0.073242 | 0.009155 | -0.045776 | 0.10529 | -0.086975 | -0.064087 | 0.073242 | 0.013733 | 0.068665 | 120.6802 | -1.4053 | -1.4786 | 120.7993 | 120.7581 | 120.6757 | 0.07782 | -0.004577 | 120.6619 | -1.3138 | -1.4832 | 120.8221 | 120.8176 | 120.7626 | 0.15564 | 0.10071 | 0.11902 | 0.009156 | 0.16022 | 0.022888 | 0.082398 | 0.19226 | 120.7626 | 120.8542 | -1.4877 | -1.506 | 120.6894 | 120.6848 | 120.6436 | 120.7031
5912.1875 | 122.3969 | -120.6848 | 1.4328 | -0.18898 | -0.040253 | 0.0017368 | 0.019732 | -0.00063233 | -0.010316 | -0.0049367 | -0.049713 | 0.024964 | 0.015357 | -0.0134 | -0.018797 | 0.026553 | -0.0051525 | -0.045776 | 0 | -0.036621 | 0.041199 | 0.14191 | -0.022888 | 0.064087 | 0.07782 | 0.064087 | -0.032043 | 0.091553 | 0.17395 | 0.10986 | 0.17853 | 120.6482 | -1.4328 | -1.3916 | 120.8267 | 120.7489 | 120.6619 | 0.10071 | 0.013733 | 120.6528 | -1.3687 | -1.3412 | 120.8588 | 120.8633 | 120.7947 | 0.21057 | 0.14191 | 0.17853 | 0.07782 | 0.20599 | 0.1236 | 0.036621 | 0.09613 | 120.6848 | 120.7489 | -1.4694 | -1.4648 | 120.726 | 120.7764 | 120.639 | 120.7626
5913.9062 | 122.2824 | -120.7123 | 1.4694 | -0.13557 | -0.04068 | -0.0025358 | 0.019946 | 0.0027857 | -0.016297 | -0.0023733 | -0.077179 | 0.024323 | 0.015998 | -0.0087009 | -0.020506 | 0.027835 | -0.0036573 | -0.15106 | 0.041199 | -0.10071 | -0.10071 | 0 | -0.11902 | 0 | -0.068665 | 0.10986 | -0.091553 | -0.041199 | 0.050354 | -0.004578 | 0.068665 | 120.6116 | -1.4282 | -1.5701 | 120.7123 | 120.7123 | 120.5933 | 0.10071 | -0.018311 | 120.6207 | -1.3596 | -1.5106 | 120.7626 | 120.7809 | 120.7077 | 0.16022 | 0.086975 | 0.10071 | 0 | 0.14191 | 0.050354 | 0.14191 | 0.20142 | 120.7535 | 120.8221 | -1.5701 | -1.561 | 120.6116 | 120.6711 | 120.5612 | 120.6436
5915.6406 | 122.3007 | -120.6802 | 1.4877 | -0.15846 | -0.040894 | -0.0021084 | 0.019305 | -0.0014867 | -0.01117 | -0.0045095 | -0.028351 | 0.02411 | 0.015571 | -0.0089145 | -0.020506 | 0.024417 | -0.0023755 | -0.086975 | 0.004578 | -0.068665 | -0.032043 | 0.068665 | -0.059509 | 0.041199 | -0.027466 | 0.11902 | -0.073242 | -0.032043 | 0.07782 | 0 | 0.054932 | 120.6116 | -1.4832 | -1.5198 | 120.7489 | 120.7214 | 120.6207 | 0.10986 | 0.009156 | 120.607 | -1.3687 | -1.5198 | 120.7581 | 120.7352 | 120.6802 | 0.12817 | 0.073242 | 0.13733 | 0.036622 | 0.15106 | 0.041199 | 0.073243 | 0.19226 | 120.6848 | 120.7993 | -1.5564 | -1.561 | 120.6482 | 120.6482 | 120.5933 | 120.6528
5917.375 | 122.3969 | -120.6116 | 1.474 | -0.18898 | -0.037476 | 0.00066863 | 0.019091 | -0.0012731 | -0.012025 | -0.0019461 | -0.064972 | 0.02176 | 0.013862 | -0.013828 | -0.019438 | 0.024844 | -0.0038709 | -0.036621 | 0 | -0.036621 | 0.041199 | 0.13275 | -0.022888 | 0.07782 | 0.10071 | 0.068665 | -0.059509 | 0.07782 | 0.17395 | 0.10986 | 0.16022 | 120.575 | -1.474 | -1.4328 | 120.7443 | 120.6894 | 120.5887 | 0.11444 | 0.013733 | 120.5521 | -1.4053 | -1.3962 | 120.7855 | 120.7718 | 120.7214 | 0.21973 | 0.16937 | 0.16937 | 0.07782 | 0.23346 | 0.13733 | 0.036621 | 0.12817 | 120.6116 | 120.6802 | -1.5106 | -1.5335 | 120.6528 | 120.6894 | 120.575 | 120.7123
5919.1094 | 122.4472 | -120.607 | 1.4969 | -0.18898 | -0.044098 | 2.7834e-05 | 0.016314 | -0.0025549 | -0.012879 | -0.0055777 | -0.0039367 | 0.023682 | 0.018989 | -0.014469 | -0.019224 | 0.026126 | -0.00088011 | -0.082397 | 0 | -0.045776 | 0.027466 | 0.16937 | 0.027466 | 0.1236 | 0.13275 | 0.086975 | -0.054932 | 0.082397 | 0.21057 | 0.16937 | 0.16479 | 120.5612 | -1.4969 | -1.4694 | 120.7764 | 120.7306 | 120.6345 | 0.16937 | 0.073242 | 120.5521 | -1.4099 | -1.4145 | 120.8176 | 120.7718 | 120.7764 | 0.21973 | 0.22431 | 0.21515 | 0.073242 | 0.2655 | 0.13733 | 0.045776 | 0.14191 | 120.607 | 120.694 | -1.5427 | -1.5518 | 120.6345 | 120.6894 | 120.5246 | 120.7397
5920.8438 | 122.4289 | -120.5795 | 1.5106 | -0.16609 | -0.037689 | -0.00018577 | 0.021228 | 0.0087671 | -0.010957 | -0.0060049 | -0.080231 | 0.023041 | 0.015357 | -0.012332 | -0.020506 | 0.025058 | -0.0017347 | -0.073242 | 0.004578 | -0.054932 | 0.013733 | 0.10071 | -0.041199 | 0.068665 | 0.073242 | 0.082397 | -0.041199 | 0.086975 | 0.16022 | 0.10529 | 0.16937 | 120.5246 | -1.506 | -1.4969 | 120.6802 | 120.6482 | 120.5383 | 0.1236 | 0.013733 | 120.5383 | -1.4282 | -1.4236 | 120.7397 | 120.7489 | 120.6848 | 0.21057 | 0.14649 | 0.15564 | 0.068665 | 0.20142 | 0.12817 | 0.05951 | 0.1236 | 120.5841 | 120.6619 | -1.5656 | -1.5518 | 120.5933 | 120.6665 | 120.5063 | 120.6528
5922.625 | 122.4106 | -120.5612 | 1.561 | -0.16609 | -0.041107 | 0.0010958 | 0.022937 | 8.47e-06 | -0.01053 | -0.0051505 | -0.083283 | 0.023896 | 0.016426 | -0.017887 | -0.021574 | 0.026981 | -0.00066651 | -0.11902 | 0.036621 | -0.054932 | -0.032043 | 0.059509 | -0.091553 | 0.027466 | 0.054932 | 0.10529 | -0.054932 | 0.068665 | 0.15106 | 0.086975 | 0.17395 | 120.5063 | -1.5244 | -1.593 | 120.6207 | 120.5887 | 120.4697 | 0.082398 | -0.036621 | 120.5063 | -1.4557 | -1.4923 | 120.7123 | 120.7352 | 120.6482 | 0.22888 | 0.14191 | 0.11444 | 0.022889 | 0.20599 | 0.1236 | 0.091553 | 0.16022 | 120.5978 | 120.6665 | -1.6159 | -1.6159 | 120.5292 | 120.6299 | 120.4422 | 120.6161
5924.3438 | 122.4152 | -120.575 | 1.5289 | -0.23476 | -0.037262 | 0.0025912 | 0.020587 | 0.0010767 | -0.012452 | -0.0040823 | -0.058869 | 0.022187 | 0.014717 | -0.021091 | -0.020933 | 0.026981 | -0.0053661 | -0.059509 | -0.004578 | -0.045776 | 0.027466 | 0.13733 | -0.036621 | 0.07782 | 0.11444 | 0.086975 | -0.068665 | 0.086975 | 0.1831 | 0.1236 | 0.16022 | 120.5292 | -1.5335 | -1.5015 | 120.7123 | 120.6528 | 120.5383 | 0.1236 | 0.009155 | 120.5063 | -1.442 | -1.442 | 120.7581 | 120.7352 | 120.6985 | 0.22888 | 0.19226 | 0.18311 | 0.073242 | 0.25177 | 0.15564 | 0.041198 | 0.15564 | 120.5704 | 120.6619 | -1.5747 | -1.5976 | 120.6024 | 120.6619 | 120.5154 | 120.6894
5926.0781 | 122.2961 | -120.5246 | 1.6663 | -0.05928 | -0.039398 | -0.0025358 | 0.018878 | 0.00022207 | -0.013307 | -0.0075003 | -0.074127 | 0.023041 | 0.013648 | -0.012546 | -0.01901 | 0.025912 | -0.0051525 | -0.14648 | 0.054932 | -0.10071 | -0.10071 | -0.009155 | -0.11444 | -0.004578 | -0.073242 | 0.1236 | -0.07782 | -0.050354 | 0.045776 | -0.018311 | 0.059509 | 120.4239 | -1.6113 | -1.767 | 120.5154 | 120.52 | 120.4102 | 0.09613 | -0.013733 | 120.4468 | -1.5427 | -1.7166 | 120.5704 | 120.5841 | 120.5063 | 0.13733 | 0.059509 | 0.091553 | 0 | 0.1236 | 0.027466 | 0.15564 | 0.20142 | 120.5795 | 120.6482 | -1.767 | -1.7441 | 120.4239 | 120.4742 | 120.3781 | 120.4514
5927.7812 | 122.3969 | -120.0714 | 2.0691 | -0.18898 | -0.040039 | -0.001254 | 0.019091 | 0.0017175 | -0.011811 | -0.0047231 | 0.0082703 | 0.022828 | 0.014289 | -0.020236 | -0.016874 | 0.026767 | -0.0040845 | -0.11902 | 0.013733 | -0.022888 | -0.032043 | 0.054932 | -0.041199 | 0.064087 | 0.009155 | 0.082397 | -0.068665 | 0.009155 | 0.10986 | 0.059509 | 0.11444 | 120.0485 | -2.0554 | -2.1011 | 120.1263 | 120.1355 | 120.0302 | 0.086975 | -0.018311 | 120.0027 | -1.9867 | -2.0599 | 120.1813 | 120.1859 | 120.1309 | 0.18311 | 0.12817 | 0.07782 | -0.009155 | 0.17853 | 0.07782 | 0.036621 | 0.15106 | 120.0851 | 120.1538 | -2.092 | -2.1378 | 120.0394 | 120.0806 | 119.9524 | 120.0806
5929.5 | 122.438 | -120.1813 | 1.9089 | -0.17372 | -0.040467 | 0.0017368 | 0.021441 | -0.0014867 | -0.012239 | -0.0053641 | -0.074127 | 0.024537 | 0.011726 | -0.011264 | -0.021147 | 0.026981 | -0.0047253 | -0.050354 | 0.004578 | -0.041199 | 0.022888 | 0.12817 | -0.032043 | 0.073242 | 0.086975 | 0.064087 | -0.054932 | 0.086975 | 0.16937 | 0.10986 | 0.16479 | 120.1401 | -1.9043 | -1.886 | 120.3094 | 120.2545 | 120.1492 | 0.11444 | 0.009156 | 120.1263 | -1.8448 | -1.8219 | 120.3506 | 120.3461 | 120.2911 | 0.21973 | 0.16479 | 0.16937 | 0.064087 | 0.22431 | 0.14191 | 0.045777 | 0.11902 | 120.1859 | 120.2454 | -1.9501 | -1.9638 | 120.2042 | 120.2682 | 120.1309 | 120.2682
5931.2031 | 122.3373 | -120.0439 | 2.1332 | -0.1432 | -0.041535 | 0.00045503 | 0.021228 | -0.0021277 | -0.013947 | -0.0042959 | -0.098541 | 0.02475 | 0.016853 | -0.0084873 | -0.019651 | 0.024204 | -0.0013073 | -0.14191 | 0.036621 | -0.10529 | -0.07782 | 0 | -0.11902 | -0.013733 | -0.064087 | 0.13275 | -0.073242 | -0.036621 | 0.059509 | 0.018311 | 0.068665 | 119.9387 | -2.0966 | -2.211 | 120.0439 | 120.0302 | 119.9249 | 0.091553 | -0.013733 | 119.9707 | -2.0004 | -2.1698 | 120.1035 | 120.1126 | 120.0623 | 0.14191 | 0.091553 | 0.10529 | 0.027466 | 0.13275 | 0.036621 | 0.14191 | 0.20599 | 120.0806 | 120.1767 | -2.2385 | -2.2064 | 119.9661 | 120.0073 | 119.902 | 119.9799
5932.9375 | 122.4426 | -120.2591 | 1.886 | -0.20424 | -0.043885 | -0.00039957 | 0.016528 | 0.0017175 | -0.012452 | -0.0032277 | 0.011322 | 0.022614 | 0.015785 | -0.014469 | -0.019438 | 0.025699 | -0.00023931 | -0.068665 | -0.022888 | -0.027466 | 0.032043 | 0.16937 | 0.027466 | 0.10071 | 0.09613 | 0.082397 | -0.054932 | 0.068665 | 0.18768 | 0.13275 | 0.15564 | 120.2316 | -1.9089 | -1.8539 | 120.4285 | 120.3598 | 120.2866 | 0.12817 | 0.054932 | 120.2042 | -1.8036 | -1.8173 | 120.4468 | 120.4147 | 120.3918 | 0.21057 | 0.18768 | 0.19684 | 0.059509 | 0.24261 | 0.1236 | 0.004578 | 0.13733 | 120.2362 | 120.3415 | -1.9135 | -1.9409 | 120.2911 | 120.3278 | 120.1904 | 120.3552
5934.6875 | 122.3602 | -120.3598 | 1.8356 | -0.089798 | -0.038544 | -0.0025358 | 0.021869 | 0.0012903 | -0.01117 | -0.0060049 | -0.11075 | 0.026459 | 0.015785 | -0.0097689 | -0.019651 | 0.028049 | -0.0023755 | -0.082397 | 0.045776 | -0.068665 | -0.036621 | 0.07782 | -0.073242 | 0.036621 | 0.036621 | 0.10986 | -0.073242 | 0.009155 | 0.09613 | 0.022888 | 0.091553 | 120.2911 | -1.7899 | -1.8723 | 120.4376 | 120.3964 | 120.2866 | 0.10529 | -0.004577 | 120.2866 | -1.7258 | -1.8265 | 120.4559 | 120.4514 | 120.3827 | 0.16479 | 0.09613 | 0.14649 | 0.032044 | 0.16937 | 0.082397 | 0.11444 | 0.18311 | 120.4056 | 120.4697 | -1.9043 | -1.9089 | 120.3232 | 120.369 | 120.2774 | 120.3964
5936.4219 | 122.3282 | -120.108 | 2.0828 | -0.16609 | -0.040253 | -0.00039957 | 0.022082 | -0.0019141 | -0.011811 | -0.0060049 | -0.10464 | 0.021546 | 0.016212 | -0.0084873 | -0.020933 | 0.027621 | -0.0025891 | -0.11444 | 0.041199 | -0.073242 | -0.082397 | 0.013733 | -0.14648 | -0.041199 | -0.073242 | 0.12817 | -0.064087 | -0.032043 | 0.032043 | -0.045776 | 0.045776 | 120.0348 | -2.0416 | -2.1652 | 120.1218 | 120.0668 | 119.9615 | 0.032043 | -0.073242 | 120.0439 | -1.9547 | -2.1149 | 120.1401 | 120.1538 | 120.0623 | 0.10986 | 0.018311 | 0.086975 | -0.009155 | 0.09613 | 0.032044 | 0.11444 | 0.19226 | 120.1492 | 120.2362 | -2.1561 | -2.1469 | 120.0256 | 120.076 | 119.9936 | 120.0348
5938.1406 | 122.3419 | -120.0989 | 2.092 | -0.18898 | -0.038758 | 0.00088223 | 0.020373 | 0.0032129 | -0.013947 | -0.0053641 | -0.089386 | 0.02411 | 0.017066 | -0.015537 | -0.020506 | 0.026553 | -0.00045291 | -0.082397 | 0.022888 | -0.073242 | -0.050354 | 0.059509 | -0.086975 | 0.013733 | 0.009155 | 0.1236 | -0.059509 | -0.013733 | 0.086975 | 0.009155 | 0.09613 | 120.0256 | -2.0691 | -2.1423 | 120.1584 | 120.1126 | 120.0119 | 0.086975 | -0.013733 | 120.0394 | -1.9684 | -2.1057 | 120.1859 | 120.195 | 120.108 | 0.15564 | 0.068664 | 0.13275 | 0.022888 | 0.14648 | 0.045776 | 0.09613 | 0.1831 | 120.1218 | 120.2225 | -2.1652 | -2.1515 | 120.0485 | 120.0851 | 120.0165 | 120.108
5939.8906 | 122.2733 | -119.4855 | 2.6917 | -0.15846 | -0.038758 | 0.0019504 | 0.020587 | 0.00022207 | -0.01053 | -0.0023733 | -0.1077 | 0.02475 | 0.016426 | -0.012546 | -0.019224 | 0.025058 | -0.0025891 | -0.13733 | 0.064087 | -0.10071 | -0.11444 | -0.027466 | -0.16937 | -0.041199 | -0.10986 | 0.11902 | -0.082397 | -0.041199 | 0.027466 | -0.050354 | 0.054932 | 119.3848 | -2.6276 | -2.8061 | 119.458 | 119.4443 | 119.3161 | 0.059509 | -0.068665 | 119.4031 | -2.5726 | -2.7328 | 119.5129 | 119.5404 | 119.4351 | 0.13733 | 0.032043 | 0.073242 | -0.013733 | 0.10986 | 0.041198 | 0.1648 | 0.20142 | 119.5496 | 119.6045 | -2.7924 | -2.774 | 119.371 | 119.4443 | 119.3481 | 119.3756
5941.6406 | 122.3969 | -118.2266 | 3.8864 | -0.19661 | -0.039826 | -0.00039957 | 0.01781 | -0.0012731 | -0.013734 | -0.0051505 | -0.0069885 | 0.023041 | 0.015357 | -0.019596 | -0.017729 | 0.024631 | -0.0049389 | -0.07782 | 0.009155 | -0.041199 | -0.009155 | 0.13733 | -0.045776 | 0.082397 | 0.073242 | 0.086975 | -0.064087 | 0.041199 | 0.13275 | 0.073242 | 0.1236 | 118.1854 | -3.8773 | -3.8956 | 118.364 | 118.309 | 118.1808 | 0.1236 | -0.004577 | 118.1625 | -3.7994 | -3.8452 | 118.3594 | 118.3502 | 118.2999 | 0.18768 | 0.13733 | 0.17853 | 0.032044 | 0.19684 | 0.10529 | 0.050354 | 0.15106 | 118.2358 | 118.3136 | -3.9276 | -3.9505 | 118.2175 | 118.2678 | 118.1488 | 118.2999
5943.3594 | 122.3511 | -119.5633 | 2.6184 | -0.11269 | -0.041107 | -0.00082677 | 0.020373 | -0.0010595 | -0.014588 | -0.0028005 | -0.077179 | 0.023896 | 0.012367 | -0.01276 | -0.020506 | 0.026553 | -0.0040845 | -0.13275 | 0.054932 | -0.068665 | -0.073242 | 0.022888 | -0.07782 | 0.004578 | -0.013733 | 0.11902 | -0.082397 | 0 | 0.10529 | 0.041199 | 0.10529 | 119.4946 | -2.5635 | -2.6917 | 119.5862 | 119.5679 | 119.4855 | 0.073243 | -0.009155 | 119.4809 | -2.4994 | -2.6184 | 119.6686 | 119.6686 | 119.6045 | 0.18768 | 0.1236 | 0.091553 | -0.004577 | 0.18768 | 0.082397 | 0.1236 | 0.20142 | 119.6182 | 119.6823 | -2.6871 | -2.7008 | 119.4901 | 119.5633 | 119.4305 | 119.5496
5945.0625 | 122.4106 | -120.5154 | 1.6571 | -0.22713 | -0.038758 | -0.0018948 | 0.016955 | -0.00020513 | -0.012452 | -0.0070731 | -0.013092 | 0.024537 | 0.015144 | -0.015323 | -0.019224 | 0.025272 | -0.0042981 | -0.10986 | 0 | -0.036621 | -0.041199 | 0.073242 | -0.064087 | 0.045776 | 0.004578 | 0.10071 | -0.050354 | 0.009155 | 0.12817 | 0.086975 | 0.11444 | 120.4788 | -1.6571 | -1.6983 | 120.5887 | 120.5612 | 120.4514 | 0.082397 | -0.027466 | 120.4651 | -1.5564 | -1.6479 | 120.6436 | 120.6299 | 120.6024 | 0.16479 | 0.13733 | 0.10986 | -0.004578 | 0.17853 | 0.059509 | 0.036621 | 0.15106 | 120.5154 | 120.6161 | -1.6937 | -1.7075 | 120.4742 | 120.5246 | 120.4056 | 120.52
5946.7812 | 122.3465 | -120.3278 | 1.8356 | -0.24239 | -0.039185 | -0.00018577 | 0.021228 | 0.0032129 | -0.013947 | -0.0053641 | -0.092438 | 0.024964 | 0.016639 | -0.011905 | -0.020292 | 0.026126 | -0.0017347 | -0.13275 | 0.036621 | -0.073242 | -0.10986 | -0.022888 | -0.14648 | -0.013733 | -0.050354 | 0.11902 | -0.082397 | -0.036621 | 0.036621 | -0.013733 | 0.082397 | 120.2545 | -1.799 | -1.9455 | 120.3049 | 120.314 | 120.1813 | 0.059509 | -0.073242 | 120.2454 | -1.7166 | -1.8723 | 120.3644 | 120.4102 | 120.314 | 0.16479 | 0.068664 | 0.050354 | -0.036621 | 0.11902 | 0.045776 | 0.10986 | 0.20142 | 120.3644 | 120.4468 | -1.9089 | -1.918 | 120.2179 | 120.2911 | 120.195 | 120.2774
5948.5781 | 122.4197 | -120.6253 | 1.5381 | -0.21187 | -0.040894 | -0.001254 | 0.017169 | 0.0015039 | -0.011384 | -0.0057913 | 0.0021667 | 0.022614 | 0.013648 | -0.014682 | -0.019438 | 0.023349 | 0.00082889 | -0.11444 | 0.018311 | -0.054932 | -0.045776 | 0.059509 | -0.054932 | 0.054932 | -0.004578 | 0.091553 | -0.050354 | 0.022888 | 0.14648 | 0.07782 | 0.13275 | 120.5704 | -1.5198 | -1.5839 | 120.6848 | 120.6802 | 120.5704 | 0.10986 | 0 | 120.575 | -1.4465 | -1.5152 | 120.7718 | 120.7581 | 120.7031 | 0.18311 | 0.12817 | 0.11444 | 0.009156 | 0.19684 | 0.073242 | 0.073243 | 0.14191 | 120.6436 | 120.7169 | -1.593 | -1.5884 | 120.5795 | 120.6482 | 120.5109 | 120.6207
5950.2969 | 122.4426 | -120.5887 | 1.5518 | -0.19661 | -0.041962 | -0.00018577 | 0.0208 | 0.0015039 | -0.01352 | -0.0040823 | -0.083283 | 0.024537 | 0.015785 | -0.012973 | -0.02136 | 0.025699 | -0.0049389 | -0.10986 | 0.022888 | -0.059509 | -0.004578 | 0.082397 | -0.054932 | 0.068665 | 0.064087 | 0.086975 | -0.036621 | 0.07782 | 0.15106 | 0.091553 | 0.15106 | 120.5292 | -1.5289 | -1.5564 | 120.6711 | 120.6573 | 120.5338 | 0.12817 | 0.004577 | 120.5521 | -1.4648 | -1.474 | 120.7397 | 120.7397 | 120.6802 | 0.18768 | 0.12817 | 0.14191 | 0.054931 | 0.18768 | 0.11444 | 0.082397 | 0.1236 | 120.6116 | 120.6757 | -1.6113 | -1.5884 | 120.5841 | 120.6665 | 120.4788 | 120.6528
5952.0781 | 122.4701 | -120.4605 | 1.6479 | -0.26527 | -0.040039 | 0.00088223 | 0.021014 | 0.00043587 | -0.012025 | -0.0057913 | -0.034454 | 0.021973 | 0.014503 | -0.013614 | -0.020506 | 0.026553 | -0.0030163 | -0.064087 | 0.009155 | -0.036621 | 0.032043 | 0.13733 | -0.041199 | 0.082397 | 0.10986 | 0.082397 | -0.032043 | 0.07782 | 0.17853 | 0.11444 | 0.15564 | 120.4239 | -1.6388 | -1.6159 | 120.5978 | 120.5429 | 120.4193 | 0.11902 | -0.004578 | 120.4285 | -1.5656 | -1.5701 | 120.639 | 120.6162 | 120.575 | 0.18768 | 0.14648 | 0.17395 | 0.068664 | 0.21057 | 0.10986 | 0.045776 | 0.11444 | 120.4697 | 120.5429 | -1.6846 | -1.68 | 120.4926 | 120.5383 | 120.3964 | 120.5704
5953.7812 | 122.3419 | -120.5154 | 1.7075 | -0.15846 | -0.03833 | -0.0016812 | 0.019732 | -0.0049047 | -0.01352 | -0.0040823 | -0.064972 | 0.02411 | 0.01493 | -0.014896 | -0.019651 | 0.025485 | -0.0021619 | -0.15106 | 0.045776 | -0.07782 | -0.10529 | 0 | -0.11444 | -0.004578 | -0.073242 | 0.11902 | -0.09613 | -0.050354 | 0.045776 | 0.013733 | 0.064087 | 120.4376 | -1.6617 | -1.8127 | 120.5154 | 120.5109 | 120.401 | 0.073242 | -0.036621 | 120.4193 | -1.5884 | -1.7578 | 120.5612 | 120.5795 | 120.5292 | 0.16022 | 0.10986 | 0.07782 | -0.027466 | 0.14191 | 0.045776 | 0.1236 | 0.21515 | 120.5612 | 120.6345 | -1.7853 | -1.8036 | 120.4102 | 120.4651 | 120.3644 | 120.4422
5955.5156 | 122.3602 | -120.4559 | 1.7578 | -0.18135 | -0.03833 | 0.00045503 | 0.021228 | 0.0017175 | -0.01117 | -0.0055777 | -0.11075 | 0.02475 | 0.014076 | -0.010837 | -0.020078 | 0.025485 | -0.0051525 | -0.13275 | 0.054932 | -0.091553 | -0.10529 | -0.004578 | -0.15564 | -0.004578 | -0.050354 | 0.1236 | -0.068665 | -0.004578 | 0.041199 | -0.013733 | 0.07782 | 120.3644 | -1.7029 | -1.8631 | 120.4514 | 120.4514 | 120.3003 | 0.086975 | -0.064087 | 120.3873 | -1.6342 | -1.7624 | 120.4971 | 120.5338 | 120.4422 | 0.14649 | 0.054932 | 0.086975 | -0.013733 | 0.10986 | 0.064087 | 0.14649 | 0.19226 | 120.5109 | 120.5795 | -1.8494 | -1.8265 | 120.3506 | 120.4514 | 120.3232 | 120.4056
5957.2188 | 122.374 | -120.4239 | 1.799 | -0.1432 | -0.044312 | 0.00024143 | 0.018451 | -0.0019141 | -0.015016 | -0.0015189 | -0.06192 | 0.026032 | 0.014289 | -0.011264 | -0.020078 | 0.026981 | -0.0053661 | -0.14191 | 0.036621 | -0.086975 | -0.091553 | 0 | -0.091553 | -0.009155 | -0.059509 | 0.11902 | -0.07782 | -0.022888 | 0.07782 | 0.027466 | 0.086975 | 120.3369 | -1.7624 | -1.8906 | 120.4239 | 120.4147 | 120.3323 | 0.07782 | -0.004578 | 120.3461 | -1.68 | -1.8219 | 120.5017 | 120.5109 | 120.4514 | 0.16479 | 0.10529 | 0.086975 | -0.004578 | 0.15564 | 0.054932 | 0.1236 | 0.19684 | 120.4605 | 120.5429 | -1.886 | -1.8768 | 120.3323 | 120.401 | 120.282 | 120.3644
5958.9219 | 122.4655 | -120.314 | 1.886 | -0.12794 | -0.041107 | -0.0021084 | 0.018664 | 0.0019311 | -0.011384 | -0.0036551 | -0.0008851 | 0.022614 | 0.017494 | -0.020664 | -0.019865 | 0.023349 | -2.571e-05 | -0.068665 | 0.004578 | -0.050354 | 0.032043 | 0.15106 | 0.018311 | 0.10529 | 0.086975 | 0.07782 | -0.059509 | 0.050354 | 0.1831 | 0.13275 | 0.15106 | 120.2637 | -1.8814 | -1.8539 | 120.4651 | 120.4193 | 120.3323 | 0.15564 | 0.068665 | 120.2545 | -1.8082 | -1.8356 | 120.4971 | 120.4651 | 120.4468 | 0.21057 | 0.19226 | 0.20142 | 0.082397 | 0.24261 | 0.10986 | 0.054932 | 0.13733 | 120.3186 | 120.3918 | -1.9363 | -1.9455 | 120.3461 | 120.3644 | 120.2454 | 120.401
5960.6406 | 122.3511 | -119.8654 | 2.3987 | -0.11269 | -0.04068 | -0.0010404 | 0.019519 | 0.0025721 | -0.012025 | -0.0062185 | -0.064972 | 0.024537 | 0.015144 | -0.014682 | -0.019224 | 0.027408 | -0.0045117 | -0.14191 | 0.041199 | -0.10071 | -0.09613 | -0.018311 | -0.12817 | -0.004578 | -0.064087 | 0.10986 | -0.086975 | -0.041199 | 0.045776 | 0 | 0.064087 | 119.7647 | -2.3575 | -2.4948 | 119.8471 | 119.8608 | 119.7372 | 0.09613 | -0.027466 | 119.7784 | -2.2888 | -2.4399 | 119.9112 | 119.9295 | 119.8654 | 0.15106 | 0.086975 | 0.082397 | 0.004578 | 0.13275 | 0.045776 | 0.14191 | 0.19684 | 119.9066 | 119.9753 | -2.4994 | -2.4857 | 119.7693 | 119.8242 | 119.7235 | 119.8013
5962.3438 | 122.4564 | -120.0943 | 2.0645 | -0.18898 | -0.040894 | -0.00082677 | 0.019091 | 0.00086307 | -0.011598 | -0.0066457 | -0.071076 | 0.022614 | 0.014503 | -0.0080601 | -0.018583 | 0.026126 | -0.0019483 | -0.10986 | 0.036621 | -0.07782 | -0.036621 | 0.064087 | -0.09613 | 0.032043 | 0.041199 | 0.086975 | -0.041199 | 0.064087 | 0.15106 | 0.07782 | 0.16022 | 120.0165 | -2.0279 | -2.1011 | 120.1584 | 120.1263 | 119.9982 | 0.10986 | -0.01831 | 120.0531 | -1.9775 | -2.0004 | 120.2454 | 120.2545 | 120.1721 | 0.20142 | 0.11902 | 0.14191 | 0.041199 | 0.19226 | 0.10529 | 0.11444 | 0.12817 | 120.1309 | 120.1813 | -2.1423 | -2.1057 | 120.0577 | 120.1584 | 119.9844 | 120.1355
5964.0469 | 122.3969 | -119.5267 | 2.6962 | -0.20424 | -0.04068 | -0.00082677 | 0.02016 | 0.00086307 | -0.012239 | -0.0025869 | -0.068024 | 0.024537 | 0.017066 | -0.018955 | -0.020506 | 0.024631 | -0.0032299 | -0.09613 | 0.041199 | -0.073242 | -0.064087 | 0.041199 | -0.082397 | 0.009155 | -0.004578 | 0.10986 | -0.086975 | 0 | 0.082397 | 0.027466 | 0.10071 | 119.4534 | -2.655 | -2.7603 | 119.5679 | 119.5358 | 119.4443 | 0.082397 | -0.009155 | 119.4397 | -2.5864 | -2.6962 | 119.6091 | 119.6274 | 119.5541 | 0.18768 | 0.11444 | 0.11444 | 0.009155 | 0.16937 | 0.086975 | 0.11444 | 0.19684 | 119.5679 | 119.6365 | -2.7695 | -2.7832 | 119.4626 | 119.5267 | 119.4305 | 119.5221
5965.75 | 122.4838 | -119.0643 | 3.0716 | -0.18898 | -0.042603 | -0.00082677 | 0.017169 | -0.0014867 | -0.013734 | -0.0047231 | 0.023529 | 0.023041 | 0.016853 | -0.0181 | -0.017942 | 0.025485 | -0.0053661 | -0.064087 | 0 | -0.027466 | 0.027466 | 0.17395 | 0.027466 | 0.1236 | 0.10529 | 0.068665 | -0.036621 | 0.068665 | 0.19684 | 0.15106 | 0.16937 | 119.0369 | -3.0716 | -3.0441 | 119.2383 | 119.1879 | 119.0918 | 0.15106 | 0.054932 | 119.0277 | -3.0029 | -3.0029 | 119.2612 | 119.2337 | 119.2154 | 0.20599 | 0.18768 | 0.20142 | 0.054932 | 0.23346 | 0.10529 | 0.027466 | 0.10529 | 119.0643 | 119.133 | -3.0991 | -3.1082 | 119.0918 | 119.133 | 119.0002 | 119.1696
5967.5469 | 122.4335 | -119.0598 | 3.1265 | -0.22713 | -0.039398 | -0.00039957 | 0.020373 | -0.0031957 | -0.013307 | -0.0045095 | -0.064972 | 0.021973 | 0.015785 | -0.015964 | -0.020506 | 0.026553 | -0.00045291 | -0.13275 | 0.036621 | -0.086975 | -0.045776 | 0.032043 | -0.12817 | 0.004578 | 0.004578 | 0.10071 | -0.054932 | 0.032043 | 0.1236 | 0.068665 | 0.13733 | 118.9728 | -3.0899 | -3.1723 | 119.0918 | 119.0643 | 118.9316 | 0.091553 | -0.041199 | 119.0048 | -3.0258 | -3.0945 | 119.1833 | 119.1971 | 119.1284 | 0.19226 | 0.1236 | 0.11902 | 0.041199 | 0.17853 | 0.086975 | 0.1236 | 0.15564 | 119.0964 | 119.1605 | -3.2135 | -3.1815 | 119.014 | 119.0918 | 118.927 | 119.0643
5969.2812 | 122.4472 | -118.1213 | 4.01 | -0.23476 | -0.040253 | 2.7834e-05 | 0.016955 | 0.0012903 | -0.010957 | -0.0062185 | -0.022247 | 0.023041 | 0.015357 | -0.01575 | -0.018156 | 0.025912 | -0.0060071 | -0.073242 | -0.004578 | -0.018311 | 0.022888 | 0.14191 | -0.018311 | 0.07782 | 0.09613 | 0.082397 | -0.045776 | 0.064087 | 0.15564 | 0.091553 | 0.14648 | 118.103 | -4.0146 | -3.9871 | 118.2632 | 118.1992 | 118.103 | 0.096131 | 0 | 118.0756 | -3.9276 | -3.9459 | 118.277 | 118.2678 | 118.2129 | 0.19226 | 0.13733 | 0.16022 | 0.041199 | 0.20142 | 0.10986 | 0.013733 | 0.12817 | 118.1168 | 118.2037 | -4.0283 | -4.0558 | 118.1442 | 118.1854 | 118.0481 | 118.2175
5970.9844 | 122.3694 | -120.2179 | 2.0096 | -0.15846 | -0.040253 | -0.00082677 | 0.021869 | -0.0029821 | -0.015229 | -0.0062185 | -0.077179 | 0.022828 | 0.014503 | -0.012546 | -0.020719 | 0.025699 | -0.0028027 | -0.13733 | 0.059509 | -0.086975 | -0.086975 | -0.022888 | -0.1236 | 0 | -0.064087 | 0.1236 | -0.09613 | -0.050354 | 0.068665 | 0.009155 | 0.068665 | 120.1309 | -1.9501 | -2.0966 | 120.195 | 120.2179 | 120.0943 | 0.086975 | -0.036621 | 120.1218 | -1.886 | -2.0599 | 120.2866 | 120.2866 | 120.2271 | 0.16479 | 0.10528 | 0.064087 | 0 | 0.16479 | 0.045776 | 0.14648 | 0.21973 | 120.2774 | 120.3415 | -2.0966 | -2.1057 | 120.1309 | 120.1675 | 120.0806 | 120.1538
5972.7188 | 122.4838 | -120.1355 | 2.0142 | -0.23476 | -0.042176 | -0.0018948 | 0.016955 | -0.0055457 | -0.011811 | -0.0047231 | 0.0021667 | 0.022828 | 0.016212 | -0.018527 | -0.018583 | 0.024631 | -0.0010937 | -0.09613 | 0.004578 | -0.036621 | -0.004578 | 0.13275 | -0.004578 | 0.11902 | 0.073242 | 0.091553 | -0.068665 | 0.068665 | 0.19684 | 0.16937 | 0.16479 | 120.0989 | -2.0096 | -2.0187 | 120.2682 | 120.2545 | 120.1309 | 0.15564 | 0.032043 | 120.0668 | -1.9226 | -1.9455 | 120.3323 | 120.3003 | 120.3049 | 0.23346 | 0.23804 | 0.16937 | 0.032043 | 0.2655 | 0.13733 | 0.041199 | 0.16022 | 120.1401 | 120.2271 | -2.0508 | -2.0828 | 120.1309 | 120.2042 | 120.0394 | 120.2087
5974.4219 | 122.3923 | -119.6732 | 2.5131 | -0.18135 | -0.039185 | -0.00082677 | 0.022296 | -0.0021277 | -0.012452 | -0.0070731 | -0.1199 | 0.024537 | 0.016426 | -0.01276 | -0.020292 | 0.024844 | -0.0019483 | -0.086975 | 0.041199 | -0.064087 | -0.027466 | 0.059509 | -0.086975 | 0.032043 | 0.013733 | 0.10986 | -0.059509 | 0 | 0.10071 | 0.032043 | 0.091553 | 119.6091 | -2.4719 | -2.5406 | 119.7327 | 119.7052 | 119.5862 | 0.09613 | -0.022888 | 119.6136 | -2.4033 | -2.5131 | 119.7739 | 119.7647 | 119.7052 | 0.15106 | 0.091552 | 0.1236 | 0.036621 | 0.16022 | 0.059509 | 0.10529 | 0.16937 | 119.7144 | 119.783 | -2.5772 | -2.5726 | 119.6457 | 119.6732 | 119.5862 | 119.6869
5976.125 | 122.3694 | -119.1238 | 3.1174 | -0.089798 | -0.041321 | -0.0021084 | 0.021014 | -0.00020513 | -0.012239 | -0.0049367 | -0.077179 | 0.025178 | 0.015357 | -0.0095553 | -0.018797 | 0.024844 | -0.0032299 | -0.14648 | 0.045776 | -0.07782 | -0.11444 | -0.009155 | -0.11444 | -0.004578 | -0.07782 | 0.11444 | -0.091553 | -0.068665 | 0.045776 | 0 | 0.059509 | 119.046 | -3.0716 | -3.2318 | 119.1147 | 119.1193 | 119.0094 | 0.073242 | -0.036621 | 119.0323 | -3.0029 | -3.186 | 119.1696 | 119.1833 | 119.1238 | 0.15106 | 0.091553 | 0.068665 | -0.036621 | 0.13733 | 0.022888 | 0.1236 | 0.20599 | 119.1696 | 119.2383 | -3.1952 | -3.2089 | 119.0094 | 119.0552 | 118.9774 | 119.046
5977.8594 | 122.3648 | -119.9295 | 2.2888 | -0.097427 | -0.040253 | -0.0027494 | 0.018878 | 0.0025721 | -0.010957 | -0.0042959 | -0.031403 | 0.020692 | 0.016212 | -0.014041 | -0.017729 | 0.02634 | -0.0030163 | -0.16022 | 0.059509 | -0.082397 | -0.10529 | -0.004578 | -0.11902 | -0.018311 | -0.091553 | 0.10529 | -0.07782 | -0.045776 | 0.041199 | -0.004578 | 0.059509 | 119.8471 | -2.2293 | -2.3941 | 119.9249 | 119.9112 | 119.8105 | 0.064086 | -0.036622 | 119.8517 | -2.1835 | -2.3346 | 119.9707 | 119.989 | 119.9249 | 0.13733 | 0.073242 | 0.077819 | -0.022889 | 0.11902 | 0.032044 | 0.14191 | 0.18311 | 119.989 | 120.0348 | -2.3712 | -2.3666 | 119.8242 | 119.8837 | 119.7693 | 119.838
5979.5625 | 122.3648 | -119.4763 | 2.7603 | -0.15846 | -0.040039 | -0.00018577 | 0.021441 | 0.0029993 | -0.011384 | -0.0038687 | -0.092438 | 0.02475 | 0.014289 | -0.017459 | -0.019224 | 0.027194 | -0.0023755 | -0.13275 | 0.041199 | -0.068665 | -0.11444 | -0.036621 | -0.16022 | -0.050354 | -0.064087 | 0.11444 | -0.09613 | -0.041199 | 0.032043 | -0.041199 | 0.064087 | 119.4077 | -2.7191 | -2.8748 | 119.4397 | 119.426 | 119.3161 | 0.018311 | -0.091552 | 119.3802 | -2.6459 | -2.8015 | 119.5084 | 119.5404 | 119.4351 | 0.16022 | 0.054931 | 0.032044 | -0.045776 | 0.12817 | 0.054931 | 0.10986 | 0.21057 | 119.5175 | 119.5908 | -2.829 | -2.8564 | 119.3619 | 119.4351 | 119.3436 | 119.4122
5981.2812 | 122.3602 | -119.1284 | 3.1265 | -0.10506 | -0.041107 | -0.00061317 | 0.016955 | -0.00084593 | -0.011384 | -0.0032277 | -0.022247 | 0.022614 | 0.014289 | -0.014041 | -0.020292 | 0.02634 | 0.00040169 | -0.14191 | 0.022888 | -0.068665 | -0.09613 | 0.032043 | -0.09613 | -0.004578 | -0.059509 | 0.10529 | -0.09613 | -0.068665 | 0.050354 | 0 | 0.050354 | 119.0598 | -3.1036 | -3.2227 | 119.1605 | 119.1238 | 119.0323 | 0.064087 | -0.027465 | 119.0323 | -3.0212 | -3.1952 | 119.1788 | 119.1788 | 119.1284 | 0.14648 | 0.09613 | 0.10071 | -0.027465 | 0.14648 | 0.027465 | 0.091553 | 0.20142 | 119.1513 | 119.2337 | -3.1952 | -3.2227 | 119.0323 | 119.0598 | 118.9865 | 119.0689
5982.9844 | 122.4701 | -119.3069 | 2.8336 | -0.19661 | -0.036621 | -0.00039957 | 0.019732 | 0.0029993 | -0.01053 | -0.0066457 | -0.049713 | 0.021332 | 0.014289 | -0.014682 | -0.020078 | 0.025912 | -0.0032299 | -0.064087 | 0.013733 | -0.045776 | 0.018311 | 0.10529 | -0.032043 | 0.059509 | 0.064087 | 0.091553 | -0.054932 | 0.091553 | 0.18768 | 0.09613 | 0.17395 | 119.2612 | -2.8198 | -2.8152 | 119.4122 | 119.3665 | 119.2749 | 0.10528 | 0.013733 | 119.252 | -2.742 | -2.742 | 119.4946 | 119.4809 | 119.4031 | 0.22888 | 0.15106 | 0.15106 | 0.064087 | 0.24261 | 0.14649 | 0.059509 | 0.14649 | 119.3207 | 119.3985 | -2.8793 | -2.8885 | 119.3253 | 119.3985 | 119.2429 | 119.371
5984.7188 | 122.4838 | -119.2703 | 2.9022 | -0.23476 | -0.040253 | 0.0019504 | 0.021441 | 0.0051355 | -0.009675 | -0.0045095 | -0.04361 | 0.02411 | 0.013008 | -0.017246 | -0.021574 | 0.025699 | -0.0021619 | -0.059509 | -0.013733 | -0.013733 | 0.018311 | 0.14191 | -0.032043 | 0.07782 | 0.10529 | 0.082397 | -0.045776 | 0.07782 | 0.15564 | 0.1236 | 0.15106 | 119.2566 | -2.916 | -2.8839 | 119.4122 | 119.3481 | 119.2383 | 0.091553 | -0.01831 | 119.2245 | -2.8198 | -2.8244 | 119.426 | 119.4214 | 119.3939 | 0.19684 | 0.16937 | 0.15564 | 0.032044 | 0.20142 | 0.1236 | 0 | 0.12817 | 119.2566 | 119.3527 | -2.916 | -2.948 | 119.2886 | 119.3481 | 119.2108 | 119.3756
5986.4219 | 122.4014 | -119.5175 | 2.7191 | -0.097427 | -0.041107 | -0.0010404 | 0.02016 | 0.0023585 | -0.012239 | -0.0062185 | -0.089386 | 0.023469 | 0.014503 | -0.014682 | -0.02136 | 0.026981 | -0.0017347 | -0.1236 | 0.059509 | -0.068665 | -0.073242 | 0 | -0.09613 | -0.004578 | -0.027466 | 0.1236 | -0.068665 | -0.018311 | 0.082397 | 0.036621 | 0.082397 | 119.4489 | -2.6596 | -2.7924 | 119.5175 | 119.5129 | 119.4214 | 0.064087 | -0.027465 | 119.4489 | -2.5955 | -2.7374 | 119.5999 | 119.5999 | 119.5541 | 0.15106 | 0.10529 | 0.068665 | -0.004577 | 0.15106 | 0.050354 | 0.12817 | 0.19226 | 119.577 | 119.6411 | -2.7878 | -2.7878 | 119.4443 | 119.4992 | 119.3939 | 119.4901
5988.1562 | 122.5113 | -119.6091 | 2.5772 | -0.17372 | -0.042176 | -0.00082677 | 0.018023 | -0.0055457 | -0.012452 | -0.0062185 | -0.0008851 | 0.02411 | 0.015998 | -0.017246 | -0.01901 | 0.02399 | -0.0023755 | -0.082397 | 0 | -0.027466 | 0.027466 | 0.16937 | 0.027466 | 0.11902 | 0.11444 | 0.086975 | -0.041199 | 0.064087 | 0.21057 | 0.16022 | 0.17395 | 119.5816 | -2.5772 | -2.5497 | 119.7784 | 119.7281 | 119.6365 | 0.14649 | 0.054932 | 119.5679 | -2.4902 | -2.5131 | 119.8196 | 119.783 | 119.7693 | 0.21515 | 0.20142 | 0.19684 | 0.054932 | 0.25177 | 0.10529 | 0.027466 | 0.12817 | 119.6091 | 119.696 | -2.6047 | -2.6184 | 119.6365 | 119.6732 | 119.5267 | 119.7235
5989.8594 | 122.374 | -117.4393 | 4.7333 | -0.15846 | -0.037903 | -0.00018577 | 0.021869 | 0.0012903 | -0.012025 | -0.0057913 | -0.1077 | 0.023469 | 0.013435 | -0.010623 | -0.021787 | 0.026126 | -0.0060071 | -0.086975 | 0.036621 | -0.054932 | -0.059509 | 0.050354 | -0.10986 | 0 | -0.009155 | 0.10529 | -0.07782 | -0.027466 | 0.068665 | -0.009155 | 0.073242 | 117.3843 | -4.6967 | -4.7928 | 117.4896 | 117.4393 | 117.3294 | 0.054932 | -0.054931 | 117.3614 | -4.628 | -4.7607 | 117.5079 | 117.5125 | 117.4301 | 0.15106 | 0.068665 | 0.10529 | -0.004577 | 0.14649 | 0.050354 | 0.091553 | 0.18311 | 117.4759 | 117.5446 | -4.7882 | -4.8111 | 117.3798 | 117.4118 | 117.3523 | 117.4301
5991.6094 | 122.438 | -119.3802 | 2.7695 | -0.26527 | -0.036835 | 0.00024143 | 0.019519 | 0.00022207 | -0.011384 | -0.0047231 | -0.034454 | 0.022187 | 0.015571 | -0.016605 | -0.018797 | 0.025485 | -0.0064343 | -0.050354 | 0.013733 | -0.027466 | 0.032043 | 0.13733 | -0.036621 | 0.082397 | 0.09613 | 0.054932 | -0.050354 | 0.07782 | 0.16479 | 0.11444 | 0.15106 | 119.3527 | -2.7557 | -2.7374 | 119.5175 | 119.4626 | 119.3436 | 0.10986 | -0.009155 | 119.3298 | -2.7145 | -2.6917 | 119.545 | 119.5312 | 119.4946 | 0.20142 | 0.16479 | 0.16479 | 0.059509 | 0.21515 | 0.12817 | 0.041199 | 0.10529 | 119.3939 | 119.4351 | -2.7969 | -2.8198 | 119.4122 | 119.458 | 119.3298 | 119.4763
5993.2969 | 122.4152 | -119.5541 | 2.6871 | -0.12794 | -0.03833 | -0.0010404 | 0.021655 | -0.00063233 | -0.011598 | -0.0075003 | -0.11075 | 0.022614 | 0.014717 | -0.012119 | -0.019438 | 0.028262 | -0.0062207 | -0.10529 | 0.041199 | -0.082397 | -0.050354 | 0.050354 | -0.07782 | 0.018311 | -0.009155 | 0.10071 | -0.07782 | 0 | 0.091553 | 0.041199 | 0.11444 | 119.4717 | -2.6459 | -2.7374 | 119.6045 | 119.5724 | 119.4763 | 0.10071 | 0.004577 | 119.4763 | -2.5864 | -2.6871 | 119.6457 | 119.6686 | 119.5953 | 0.19226 | 0.11902 | 0.13275 | 0.032043 | 0.16937 | 0.07782 | 0.1236 | 0.17853 | 119.5953 | 119.6548 | -2.7695 | -2.7649 | 119.5038 | 119.5541 | 119.4489 | 119.545
5995.0312 | 122.3557 | -119.5908 | 2.6779 | -0.17372 | -0.037262 | 0.00045503 | 0.0208 | 8.47e-06 | -0.010102 | -0.0032277 | -0.10159 | 0.022187 | 0.016853 | -0.011264 | -0.020292 | 0.025912 | -0.0040845 | -0.13275 | 0.041199 | -0.086975 | -0.1236 | -0.041199 | -0.16479 | -0.064087 | -0.11902 | 0.1236 | -0.082397 | -0.064087 | 0.027466 | -0.036621 | 0.054932 | 119.5038 | -2.6367 | -2.8015 | 119.5496 | 119.5267 | 119.426 | 0.022888 | -0.07782 | 119.5084 | -2.5543 | -2.742 | 119.6182 | 119.6457 | 119.5541 | 0.13733 | 0.045776 | 0.045776 | -0.036621 | 0.10986 | 0.01831 | 0.12817 | 0.20599 | 119.632 | 119.7144 | -2.7649 | -2.7603 | 119.4672 | 119.5267 | 119.458 | 119.4717
5996.7812 | 122.3831 | -119.2841 | 2.98 | -0.10506 | -0.039398 | -0.001254 | 0.020373 | 0.00086307 | -0.012452 | -0.0049367 | -0.10464 | 0.023255 | 0.015144 | -0.01041 | -0.02136 | 0.027194 | -0.00088011 | -0.11444 | 0.045776 | -0.068665 | -0.10529 | 0 | -0.14191 | -0.041199 | -0.064087 | 0.1236 | -0.07782 | -0.050354 | 0.022888 | -0.027466 | 0.050354 | 119.2154 | -2.9343 | -3.0853 | 119.2841 | 119.2429 | 119.1422 | 0.027466 | -0.073242 | 119.2062 | -2.8564 | -3.0304 | 119.3069 | 119.3344 | 119.2566 | 0.12817 | 0.050354 | 0.068665 | -0.036621 | 0.10071 | 0.027466 | 0.11444 | 0.20142 | 119.3298 | 119.4077 | -3.0487 | -3.0579 | 119.1788 | 119.2337 | 119.1696 | 119.22
5998.4844 | 122.406 | -119.5633 | 2.6642 | -0.16609 | -0.040894 | -0.00061317 | 0.016742 | 0.0021447 | -0.015229 | -0.0075003 | -0.01004 | 0.024537 | 0.016426 | -0.01276 | -0.017515 | 0.024844 | -0.0036573 | -0.07782 | 0.004578 | -0.036621 | -0.013733 | 0.10529 | -0.022888 | 0.059509 | 0.009155 | 0.11444 | -0.064087 | -0.036621 | 0.09613 | 0.036621 | 0.059509 | 119.5267 | -2.6596 | -2.6779 | 119.6686 | 119.6228 | 119.5404 | 0.09613 | 0.013733 | 119.4992 | -2.5497 | -2.7008 | 119.6594 | 119.6228 | 119.5999 | 0.1236 | 0.10071 | 0.14191 | 0.022888 | 0.16022 | 0.027466 | 0.041199 | 0.17853 | 119.5679 | 119.6777 | -2.7008 | -2.7283 | 119.5496 | 119.5267 | 119.4855 | 119.5724
6000.1875 | 122.4792 | -119.8196 | 2.3483 | -0.2729 | -0.040894 | 0.0013094 | 0.018664 | 0.0021447 | -0.011811 | -0.0081411 | -0.0069885 | 0.021973 | 0.015571 | -0.014896 | -0.020933 | 0.025272 | -0.0040845 | -0.059509 | -0.018311 | -0.036621 | 0.027466 | 0.13733 | -0.032043 | 0.086975 | 0.09613 | 0.082397 | -0.059509 | 0.068665 | 0.16937 | 0.09613 | 0.16022 | 119.783 | -2.3666 | -2.3209 | 119.957 | 119.9066 | 119.7876 | 0.1236 | 0.004578 | 119.7601 | -2.2659 | -2.2797 | 119.989 | 119.9799 | 119.9158 | 0.21973 | 0.15564 | 0.17395 | 0.064087 | 0.22888 | 0.12817 | 0.01831 | 0.14191 | 119.8013 | 119.902 | -2.3849 | -2.4078 | 119.8471 | 119.8883 | 119.7601 | 119.9158
6001.8906 | 122.4152 | -120.0119 | 2.2705 | -0.12794 | -0.040253 | 2.7834e-05 | 0.019946 | 0.0057763 | -0.014802 | -0.0025869 | -0.06192 | 0.024323 | 0.012794 | -0.015537 | -0.020506 | 0.026126 | -0.0013073 | -0.12817 | 0.032043 | -0.09613 | -0.10986 | -0.009155 | -0.11444 | -0.009155 | -0.064087 | 0.11444 | -0.086975 | -0.045776 | 0.054932 | 0.009155 | 0.068665 | 119.9158 | -2.2385 | -2.3804 | 120.0027 | 120.0027 | 119.8975 | 0.086975 | -0.018311 | 119.9249 | -2.1561 | -2.3163 | 120.0668 | 120.0806 | 120.0211 | 0.15564 | 0.09613 | 0.086975 | -0.013733 | 0.14191 | 0.041199 | 0.12817 | 0.20142 | 120.0439 | 120.1263 | -2.3666 | -2.3575 | 119.902 | 119.9661 | 119.8837 | 119.9478
6003.6406 | 122.3877 | -119.8563 | 2.4307 | -0.15846 | -0.042603 | -0.00061317 | 0.01781 | -0.0027685 | -0.014161 | -0.0075003 | -0.049713 | 0.022401 | 0.015571 | -0.020877 | -0.021574 | 0.025699 | -0.00045291 | -0.12817 | 0.036621 | -0.073242 | -0.082397 | 0.045776 | -0.073242 | 0.009155 | -0.050354 | 0.11444 | -0.082397 | -0.068665 | 0.059509 | 0.013733 | 0.032043 | 119.783 | -2.3941 | -2.5131 | 119.902 | 119.8654 | 119.783 | 0.082397 | 0 | 119.7739 | -2.3163 | -2.4994 | 119.9158 | 119.8883 | 119.87 | 0.11444 | 0.09613 | 0.11902 | -0.009155 | 0.14191 | 0.013732 | 0.10986 | 0.19684 | 119.8929 | 119.9707 | -2.504 | -2.5131 | 119.7739 | 119.7876 | 119.7281 | 119.8059
6005.3438 | 122.4655 | -119.4122 | 2.7969 | -0.15083 | -0.042389 | 2.7834e-05 | 0.018023 | -0.0053321 | -0.012879 | -0.0066457 | 0.0082703 | 0.023469 | 0.015998 | -0.013614 | -0.019224 | 0.022495 | -0.0072889 | -0.11902 | 0.018311 | -0.032043 | -0.054932 | 0.059509 | -0.07782 | 0.050354 | 0.009155 | 0.10071 | -0.064087 | 0.027466 | 0.11902 | 0.07782 | 0.12817 | 119.3802 | -2.7786 | -2.8519 | 119.4717 | 119.4626 | 119.3344 | 0.082397 | -0.045777 | 119.3481 | -2.6962 | -2.7695 | 119.5312 | 119.5404 | 119.4901 | 0.19226 | 0.14191 | 0.091552 | -0.022889 | 0.18311 | 0.091553 | 0.050354 | 0.1648 | 119.4305 | 119.5129 | -2.829 | -2.861 | 119.3573 | 119.4397 | 119.2932 | 119.4214
6007.0469 | 122.4335 | -119.5496 | 2.7237 | -0.18135 | -0.037476 | 0.0023776 | 0.021441 | 0.0023585 | -0.009675 | -0.0081411 | -0.10159 | 0.026032 | 0.01493 | -0.014041 | -0.020719 | 0.024417 | -0.0021619 | -0.1236 | 0.059509 | -0.07782 | -0.09613 | -0.013733 | -0.14191 | -0.032043 | -0.036621 | 0.10071 | -0.073242 | -0.022888 | 0.050354 | -0.022888 | 0.068665 | 119.4717 | -2.6642 | -2.8198 | 119.5358 | 119.5175 | 119.4077 | 0.045777 | -0.064087 | 119.4763 | -2.623 | -2.7466 | 119.5999 | 119.6182 | 119.5267 | 0.14191 | 0.050354 | 0.064087 | -0.01831 | 0.1236 | 0.050354 | 0.13733 | 0.17395 | 119.6091 | 119.6503 | -2.8015 | -2.7969 | 119.4534 | 119.5267 | 119.426 | 119.5129
6008.75 | 122.438 | -119.7418 | 2.449 | -0.13557 | -0.041321 | -0.00018577 | 0.019732 | 0.00022207 | -0.013093 | -0.0062185 | -0.10464 | 0.023255 | 0.014717 | -0.014682 | -0.017301 | 0.028262 | -0.00045291 | -0.091553 | 0.036621 | -0.064087 | -0.032043 | 0.064087 | -0.07782 | 0.022888 | 0.027466 | 0.10071 | -0.082397 | 0.009155 | 0.10986 | 0.064087 | 0.10529 | 119.6777 | -2.4124 | -2.4811 | 119.8059 | 119.7647 | 119.664 | 0.086975 | -0.013733 | 119.6594 | -2.3483 | -2.4399 | 119.8517 | 119.8471 | 119.8059 | 0.18768 | 0.14648 | 0.12817 | 0.032044 | 0.19226 | 0.091552 | 0.10071 | 0.18311 | 119.7784 | 119.8425 | -2.5131 | -2.5314 | 119.7098 | 119.751 | 119.6503 | 119.7693
6010.4844 | 122.4243 | -119.8334 | 2.3941 | -0.13557 | -0.039826 | 0.00066863 | 0.021655 | 0.0032129 | -0.012452 | -0.0042959 | -0.086334 | 0.023682 | 0.013648 | -0.0042147 | -0.020078 | 0.025485 | -0.0017347 | -0.09613 | 0.054932 | -0.059509 | -0.059509 | 0.041199 | -0.082397 | 0.013733 | -0.004578 | 0.11902 | -0.073242 | 0.013733 | 0.10986 | 0.050354 | 0.07782 | 119.7739 | -2.3392 | -2.4536 | 119.8746 | 119.8471 | 119.751 | 0.073242 | -0.022888 | 119.7601 | -2.2751 | -2.3804 | 119.9432 | 119.9112 | 119.8837 | 0.15106 | 0.1236 | 0.10071 | 0 | 0.18311 | 0.086975 | 0.11444 | 0.19226 | 119.8883 | 119.9524 | -2.4536 | -2.4673 | 119.7739 | 119.8471 | 119.7372 | 119.8288
6012.1875 | 122.5204 | -120.0302 | 2.1835 | -0.15846 | -0.041321 | 0.00024143 | 0.01781 | -0.0017005 | -0.0094614 | -0.0025869 | 0.041839 | 0.021973 | 0.018134 | -0.0181 | -0.018797 | 0.024417 | -0.0025891 | -0.10529 | 0.013733 | -0.059509 | -0.013733 | 0.1236 | -0.004578 | 0.082397 | 0.050354 | 0.07782 | -0.059509 | 0.064087 | 0.18768 | 0.13733 | 0.17395 | 119.9707 | -2.1698 | -2.1973 | 120.1538 | 120.1126 | 120.0256 | 0.14191 | 0.054931 | 119.9707 | -2.1057 | -2.1194 | 120.2179 | 120.2042 | 120.1675 | 0.23346 | 0.19684 | 0.1831 | 0.045776 | 0.24719 | 0.1236 | 0.073242 | 0.13733 | 120.0439 | 120.108 | -2.243 | -2.243 | 120.0165 | 120.0943 | 119.9249 | 120.0806
6013.8906 | 122.4152 | -119.9799 | 2.3071 | -0.19661 | -0.039612 | 0.0017368 | 0.0208 | 0.0023585 | -0.0088206 | -0.0034415 | -0.089386 | 0.024323 | 0.014503 | -0.0087009 | -0.020506 | 0.026981 | -0.0021619 | -0.13733 | 0.036621 | -0.086975 | -0.10529 | -0.018311 | -0.16022 | -0.027466 | -0.059509 | 0.10986 | -0.09613 | -0.036621 | 0.032043 | -0.027466 | 0.064087 | 119.8929 | -2.2705 | -2.4124 | 119.9615 | 119.9524 | 119.8196 | 0.059509 | -0.073242 | 119.8837 | -2.1973 | -2.3438 | 120.0119 | 120.0439 | 119.9524 | 0.16022 | 0.068664 | 0.068664 | -0.018311 | 0.12817 | 0.059509 | 0.1236 | 0.20599 | 120.0165 | 120.0897 | -2.3941 | -2.4033 | 119.8746 | 119.9432 | 119.8425 | 119.9203
6015.6406 | 122.438 | -119.8059 | 2.3895 | -0.15846 | -0.040894 | 0.0010958 | 0.016955 | 0.0027857 | -0.010957 | -0.0077139 | -0.013092 | 0.020264 | 0.014289 | -0.013187 | -0.020719 | 0.023776 | -0.0032299 | -0.11902 | 0.009155 | -0.045776 | -0.032043 | 0.073242 | -0.073242 | 0.059509 | 0.013733 | 0.086975 | -0.064087 | 0.009155 | 0.10529 | 0.068665 | 0.1236 | 119.7601 | -2.3804 | -2.4216 | 119.8791 | 119.8654 | 119.7327 | 0.10528 | -0.027466 | 119.7418 | -2.3026 | -2.3804 | 119.9112 | 119.9295 | 119.8746 | 0.18768 | 0.13275 | 0.11902 | 0.013733 | 0.16937 | 0.073242 | 0.054931 | 0.15106 | 119.8151 | 119.8929 | -2.4353 | -2.4536 | 119.7739 | 119.8151 | 119.6869 | 119.8196
6017.3438 | 122.438 | -119.9432 | 2.3346 | -0.1432 | -0.041748 | -0.001254 | 0.021441 | 0.0051355 | -0.01352 | -0.0032277 | -0.06192 | 0.024323 | 0.015998 | -0.0087009 | -0.019865 | 0.02399 | -2.571e-05 | -0.13275 | 0.032043 | -0.091553 | -0.086975 | 0 | -0.10071 | -0.004578 | -0.054932 | 0.12817 | -0.082397 | -0.022888 | 0.07782 | 0.027466 | 0.086975 | 119.8517 | -2.3026 | -2.4216 | 119.9432 | 119.9387 | 119.8425 | 0.086975 | -0.009155 | 119.8608 | -2.2064 | -2.3575 | 120.0211 | 120.0302 | 119.9707 | 0.16937 | 0.10986 | 0.091553 | 0.004578 | 0.16022 | 0.059509 | 0.1236 | 0.21057 | 119.9753 | 120.0714 | -2.4261 | -2.417 | 119.8563 | 119.9203 | 119.8105 | 119.8883
6019.0781 | 122.5571 | -119.9112 | 2.3026 | -0.18135 | -0.043244 | -0.0025358 | 0.018451 | -0.0017005 | -0.014161 | -0.0038687 | 0.0021667 | 0.022828 | 0.01493 | -0.014255 | -0.020933 | 0.024204 | -0.0045117 | -0.073242 | 0.009155 | -0.050354 | 0.018311 | 0.15106 | 0.009155 | 0.11444 | 0.11902 | 0.068665 | -0.059509 | 0.086975 | 0.21515 | 0.15106 | 0.16479 | 119.8608 | -2.2934 | -2.2842 | 120.0623 | 120.0256 | 119.9203 | 0.16479 | 0.059509 | 119.8517 | -2.2339 | -2.2156 | 120.1263 | 120.076 | 120.0623 | 0.2243 | 0.21057 | 0.20142 | 0.068665 | 0.27466 | 0.14648 | 0.059509 | 0.12817 | 119.9203 | 119.9799 | -2.3529 | -2.3621 | 119.9295 | 119.9982 | 119.838 | 120.0302
6020.7812 | 122.525 | -119.8791 | 2.3712 | -0.15846 | -0.040467 | 0.0010958 | 0.019091 | -0.0036231 | -0.011811 | -0.0053641 | -0.013092 | 0.02176 | 0.01493 | -0.013614 | -0.020292 | 0.024631 | -0.0030163 | -0.086975 | 0.009155 | -0.054932 | 0.004578 | 0.11902 | -0.022888 | 0.10071 | 0.064087 | 0.086975 | -0.064087 | 0.054932 | 0.18768 | 0.13733 | 0.16479 | 119.8242 | -2.3621 | -2.3666 | 119.9982 | 119.9799 | 119.8563 | 0.15564 | 0.032044 | 119.8151 | -2.2842 | -2.3163 | 120.0668 | 120.0439 | 120.0165 | 0.22888 | 0.20142 | 0.17395 | 0.05951 | 0.25177 | 0.11902 | 0.064087 | 0.15106 | 119.8883 | 119.9661 | -2.4261 | -2.4353 | 119.8837 | 119.9341 | 119.7922 | 119.9432
6022.4844 | 122.406 | -119.8151 | 2.4857 | -0.1432 | -0.037262 | 0.00024143 | 0.022509 | 0.0055627 | -0.010316 | -0.0060049 | -0.12906 | 0.023255 | 0.013008 | -0.013614 | -0.021147 | 0.026553 | -0.0060071 | -0.13733 | 0.050354 | -0.09613 | -0.10529 | -0.036621 | -0.15564 | -0.027466 | -0.082397 | 0.12817 | -0.086975 | -0.045776 | 0.018311 | -0.036621 | 0.045776 | 119.7189 | -2.4353 | -2.5909 | 119.7784 | 119.7876 | 119.6594 | 0.068664 | -0.05951 | 119.7281 | -2.3575 | -2.5314 | 119.8334 | 119.8608 | 119.7784 | 0.13275 | 0.050354 | 0.059509 | -0.009156 | 0.10529 | 0.041199 | 0.14648 | 0.21515 | 119.8654 | 119.9432 | -2.5818 | -2.5726 | 119.7098 | 119.7693 | 119.6777 | 119.7327
6024.2188 | 122.4472 | -120.1401 | 2.1103 | -0.18898 | -0.037689 | -0.001254 | 0.021014 | -0.0010595 | -0.010957 | -0.0053641 | -0.11075 | 0.025819 | 0.017921 | -0.015537 | -0.01901 | 0.02634 | -0.0032299 | -0.13733 | 0.045776 | -0.086975 | -0.09613 | -0.004578 | -0.14648 | -0.027466 | -0.050354 | 0.10071 | -0.068665 | 0.009155 | 0.064087 | 0.013733 | 0.082397 | 120.0531 | -2.0645 | -2.2064 | 120.1355 | 120.1126 | 119.9936 | 0.059509 | -0.059509 | 120.0714 | -2.0096 | -2.1011 | 120.2042 | 120.2225 | 120.1538 | 0.15106 | 0.082398 | 0.082397 | -0.009155 | 0.13275 | 0.07782 | 0.13275 | 0.16937 | 120.1859 | 120.2408 | -2.1973 | -2.179 | 120.0439 | 120.1492 | 120.0027 | 120.0897
6025.9219 | 122.5067 | -119.9295 | 2.2751 | -0.21187 | -0.04068 | -0.00061317 | 0.019091 | 0.00022207 | -0.012025 | -0.0042959 | -0.04361 | 0.02411 | 0.014076 | -0.013828 | -0.021574 | 0.026553 | -0.0053661 | -0.068665 | -0.009155 | -0.032043 | 0.022888 | 0.14191 | -0.036621 | 0.091553 | 0.10071 | 0.07782 | -0.045776 | 0.064087 | 0.17395 | 0.10986 | 0.14648 | 119.8975 | -2.2842 | -2.2522 | 120.0714 | 120.0211 | 119.8929 | 0.1236 | -0.004578 | 119.8837 | -2.1973 | -2.211 | 120.1035 | 120.076 | 120.0394 | 0.19226 | 0.15564 | 0.17395 | 0.054931 | 0.21973 | 0.10986 | 0.022888 | 0.1236 | 119.9203 | 120.0073 | -2.3071 | -2.3209 | 119.9524 | 119.9936 | 119.8608 | 120.0302
6027.625 | 122.5159 | -119.7784 | 2.449 | -0.12794 | -0.041321 | -0.00061317 | 0.018237 | 0.00043587 | -0.012025 | -0.0038687 | -0.031403 | 0.023469 | 0.015571 | -0.011264 | -0.02136 | 0.022495 | -0.0062207 | -0.054932 | 0 | -0.032043 | 0.022888 | 0.13275 | 0.013733 | 0.082397 | 0.073242 | 0.091553 | -0.050354 | 0.041199 | 0.1831 | 0.13275 | 0.13275 | 119.7464 | -2.449 | -2.4261 | 119.9112 | 119.8608 | 119.7922 | 0.11444 | 0.045776 | 119.7281 | -2.3575 | -2.4078 | 119.9615 | 119.9112 | 119.9112 | 0.18311 | 0.18311 | 0.16479 | 0.054931 | 0.23346 | 0.091553 | 0.032043 | 0.14191 | 119.7784 | 119.87 | -2.4811 | -2.4994 | 119.8013 | 119.8196 | 119.7235 | 119.8517
6029.3438 | 122.3969 | -119.6548 | 2.6505 | -0.12032 | -0.040894 | -0.0018948 | 0.02016 | -0.0053321 | -0.015016 | -0.0025869 | -0.068024 | 0.024323 | 0.016853 | -0.0089145 | -0.020506 | 0.026981 | -0.0053661 | -0.14191 | 0.041199 | -0.086975 | -0.09613 | -0.004578 | -0.11444 | -0.009155 | -0.082397 | 0.11444 | -0.086975 | -0.073242 | 0.041199 | 0 | 0.041199 | 119.5679 | -2.6093 | -2.7466 | 119.6503 | 119.6457 | 119.5404 | 0.07782 | -0.027466 | 119.5679 | -2.536 | -2.7237 | 119.696 | 119.696 | 119.6548 | 0.12817 | 0.086975 | 0.082397 | -0.009155 | 0.12817 | 0.013733 | 0.12817 | 0.20142 | 119.696 | 119.7693 | -2.7374 | -2.7374 | 119.5587 | 119.5816 | 119.5129 | 119.5724
6031.0781 | 122.4335 | -119.5633 | 2.7191 | -0.18135 | -0.043671 | -0.00061317 | 0.020373 | 0.00064947 | -0.010743 | -0.0038687 | -0.068024 | 0.023041 | 0.013008 | -0.011692 | -0.019438 | 0.027835 | -0.0049389 | -0.12817 | 0.032043 | -0.082397 | -0.10529 | -0.009155 | -0.10986 | -0.013733 | -0.068665 | 0.10986 | -0.059509 | -0.045776 | 0.054932 | 0.009155 | 0.082397 | 119.4809 | -2.6871 | -2.8244 | 119.5541 | 119.5496 | 119.4534 | 0.068664 | -0.027466 | 119.5038 | -2.6093 | -2.7649 | 119.6182 | 119.6457 | 119.5724 | 0.14191 | 0.068664 | 0.073242 | -0.022889 | 0.11444 | 0.013733 | 0.11444 | 0.16937 | 119.5953 | 119.6732 | -2.8015 | -2.7786 | 119.458 | 119.5175 | 119.4351 | 119.4946
6032.7969 | 122.3831 | -119.4168 | 2.8931 | -0.15083 | -0.042389 | -0.0016812 | 0.018878 | -0.0012731 | -0.011811 | -0.0021597 | -0.046661 | 0.022614 | 0.017066 | -0.014255 | -0.019438 | 0.024631 | -0.0051525 | -0.14191 | 0.045776 | -0.091553 | -0.10986 | -0.009155 | -0.10529 | -0.009155 | -0.07782 | 0.13275 | -0.091553 | -0.073242 | 0.050354 | 0.004578 | 0.036621 | 119.3253 | -2.8473 | -3.0029 | 119.4077 | 119.4077 | 119.3115 | 0.082398 | -0.013733 | 119.3253 | -2.7603 | -2.9663 | 119.4672 | 119.4534 | 119.4214 | 0.12817 | 0.096131 | 0.082398 | -0.01831 | 0.14191 | 0.018311 | 0.13733 | 0.2243 | 119.4626 | 119.5496 | -2.9846 | -2.9846 | 119.3069 | 119.3436 | 119.2749 | 119.339
6034.5625 | 122.4197 | -120.3781 | 1.9135 | -0.20424 | -0.04303 | -0.0014676 | 0.018878 | -0.0049047 | -0.014802 | -0.0045095 | -0.055817 | 0.022614 | 0.016639 | -0.01276 | -0.019651 | 0.025272 | -0.0032299 | -0.15106 | 0.050354 | -0.07782 | -0.10529 | 0.004578 | -0.10529 | 0 | -0.082397 | 0.11444 | -0.07782 | -0.059509 | 0.041199 | -0.004578 | 0.041199 | 120.3003 | -1.8631 | -2.0187 | 120.3827 | 120.3781 | 120.2728 | 0.07782 | -0.027466 | 120.3003 | -1.799 | -1.973 | 120.4193 | 120.4193 | 120.3735 | 0.11902 | 0.073242 | 0.082398 | -0.027466 | 0.11902 | 0.018311 | 0.12817 | 0.19226 | 120.4285 | 120.4926 | -1.9913 | -1.9913 | 120.2728 | 120.3186 | 120.2271 | 120.2957
6036.2656 | 122.493 | -120.2408 | 2.0142 | -0.18135 | -0.040894 | 2.7834e-05 | 0.018023 | -0.0044775 | -0.013093 | -0.0042959 | 0.020477 | 0.023255 | 0.013862 | -0.0181 | -0.01901 | 0.026553 | -0.0068615 | -0.10986 | 0.009155 | -0.045776 | -0.036621 | 0.059509 | -0.068665 | 0.041199 | -0.004578 | 0.091553 | -0.054932 | 0.004578 | 0.11902 | 0.068665 | 0.11444 | 120.195 | -2.005 | -2.0508 | 120.3003 | 120.282 | 120.1721 | 0.086975 | -0.022889 | 120.1859 | -1.9226 | -2.0096 | 120.3598 | 120.3552 | 120.3094 | 0.16937 | 0.1236 | 0.10528 | 0.009155 | 0.17395 | 0.05951 | 0.054931 | 0.14649 | 120.2499 | 120.3323 | -2.0599 | -2.0691 | 120.2042 | 120.2454 | 120.1309 | 120.2362
6037.9688 | 122.4518 | -120.2591 | 2.0325 | -0.15846 | -0.038971 | -0.00018577 | 0.020373 | 0.0021447 | -0.011384 | -0.0042959 | -0.086334 | 0.023469 | 0.015785 | -0.0091281 | -0.019865 | 0.028476 | -0.0051525 | -0.064087 | 0.045776 | -0.059509 | -0.032043 | 0.068665 | -0.07782 | 0.022888 | 0.013733 | 0.11444 | -0.068665 | -0.013733 | 0.09613 | 0.032043 | 0.086975 | 120.1996 | -1.9867 | -2.0645 | 120.3278 | 120.282 | 120.1813 | 0.082397 | -0.018311 | 120.1904 | -1.918 | -2.0462 | 120.3552 | 120.3461 | 120.2911 | 0.15564 | 0.10071 | 0.12817 | 0.027466 | 0.16479 | 0.054932 | 0.10528 | 0.18311 | 120.3049 | 120.3735 | -2.092 | -2.1011 | 120.2271 | 120.2454 | 120.195 | 120.2728
6039.7031 | 122.4335 | -120.2728 | 2.0325 | -0.10506 | -0.037262 | -0.0018948 | 0.019732 | 0.00064947 | -0.010957 | -0.0057913 | -0.11685 | 0.024537 | 0.014717 | -0.011264 | -0.019438 | 0.025272 | -0.0036573 | -0.07782 | 0.045776 | -0.064087 | -0.036621 | 0.036621 | -0.09613 | 0 | -0.013733 | 0.1236 | -0.086975 | -0.013733 | 0.059509 | -0.004578 | 0.07782 | 120.2087 | -1.9867 | -2.0691 | 120.3094 | 120.2728 | 120.1767 | 0.064087 | -0.032043 | 120.1859 | -1.9089 | -2.0462 | 120.3323 | 120.3506 | 120.2682 | 0.16479 | 0.082397 | 0.10071 | 0.027466 | 0.14648 | 0.073242 | 0.10986 | 0.21057 | 120.3186 | 120.3964 | -2.0966 | -2.1194 | 120.2362 | 120.2591 | 120.195 | 120.2591
6041.4062 | 122.4976 | -120.108 | 2.1378 | -0.2195 | -0.039612 | 0.00088223 | 0.017169 | 0.00043587 | -0.012879 | -0.0072867 | -0.0008851 | 0.022614 | 0.012153 | -0.015537 | -0.020292 | 0.025912 | -0.0036573 | -0.11444 | 0.004578 | -0.050354 | -0.050354 | 0.086975 | -0.064087 | 0.059509 | 0.013733 | 0.09613 | -0.059509 | -0.004578 | 0.12817 | 0.068665 | 0.10986 | 120.0577 | -2.1332 | -2.1881 | 120.195 | 120.1675 | 120.0439 | 0.10986 | -0.013733 | 120.0485 | -2.0416 | -2.1423 | 120.2362 | 120.2179 | 120.1767 | 0.16937 | 0.12817 | 0.13733 | 0 | 0.18768 | 0.054931 | 0.054932 | 0.15564 | 120.1126 | 120.2042 | -2.1881 | -2.1973 | 120.0577 | 120.1035 | 119.9936 | 120.1218
6043.1406 | 122.438 | -120.108 | 2.179 | -0.2195 | -0.039398 | 0.00024143 | 0.0208 | -0.00041873 | -0.01053 | -0.0040823 | -0.1077 | 0.026459 | 0.015144 | -0.0099827 | -0.020292 | 0.026126 | -0.0036573 | -0.13733 | 0.054932 | -0.091553 | -0.10529 | -0.032043 | -0.16937 | -0.032043 | -0.054932 | 0.11444 | -0.068665 | -0.050354 | 0.036621 | -0.022888 | 0.068665 | 120.0165 | -2.124 | -2.2842 | 120.076 | 120.076 | 119.9387 | 0.05951 | -0.07782 | 120.0394 | -2.0645 | -2.2293 | 120.1447 | 120.1767 | 120.0851 | 0.13733 | 0.045777 | 0.05951 | -0.013733 | 0.10529 | 0.018311 | 0.14649 | 0.18311 | 120.163 | 120.2225 | -2.2705 | -2.2476 | 120.0027 | 120.0577 | 119.9707 | 120.0531
6044.8438 | 122.4609 | -119.9707 | 2.3254 | -0.13557 | -0.038758 | 0.00066863 | 0.022723 | -0.0023413 | -0.01352 | -0.0070731 | -0.09549 | 0.022614 | 0.016853 | -0.010196 | -0.018797 | 0.025699 | -0.0015209 | -0.091553 | 0.032043 | -0.059509 | -0.041199 | 0.068665 | -0.068665 | 0.032043 | 0.022888 | 0.10986 | -0.054932 | 0.004578 | 0.10529 | 0.032043 | 0.10529 | 119.9112 | -2.2934 | -2.3666 | 120.0394 | 120.0027 | 119.902 | 0.091552 | -0.009156 | 119.9158 | -2.2156 | -2.3209 | 120.076 | 120.076 | 120.0027 | 0.16022 | 0.086975 | 0.12817 | 0.01831 | 0.16022 | 0.05951 | 0.091552 | 0.16479 | 120.0027 | 120.0806 | -2.3849 | -2.3804 | 119.9295 | 119.9753 | 119.8791 | 119.9936
6046.5469 | 122.5571 | -119.9158 | 2.33 | -0.12032 | -0.041107 | 0.00045503 | 0.016314 | 0.0017175 | -0.011384 | -0.0066457 | 0.0052185 | 0.02176 | 0.014289 | -0.015109 | -0.019865 | 0.024631 | 0.00082889 | -0.050354 | 0.009155 | -0.036621 | 0.018311 | 0.16937 | 0.009155 | 0.10071 | 0.10529 | 0.07782 | -0.032043 | 0.064087 | 0.19226 | 0.14648 | 0.15564 | 119.8792 | -2.3209 | -2.3117 | 120.0851 | 120.0165 | 119.9249 | 0.13733 | 0.045776 | 119.8837 | -2.2522 | -2.2659 | 120.108 | 120.0714 | 120.0623 | 0.18768 | 0.17853 | 0.20599 | 0.054932 | 0.2243 | 0.09613 | 0.045776 | 0.10986 | 119.9249 | 119.9936 | -2.3666 | -2.3621 | 119.9341 | 119.9799 | 119.8654 | 120.0211
6048.2656 | 122.5662 | -119.7601 | 2.4902 | -0.19661 | -0.041748 | -0.0014676 | 0.016101 | -0.0023413 | -0.012025 | -0.0051505 | -0.013092 | 0.022401 | 0.016212 | -0.015323 | -0.01901 | 0.023776 | -0.0017347 | -0.11444 | 0.004578 | -0.050354 | -0.027466 | 0.091553 | -0.050354 | 0.073242 | 0.041199 | 0.068665 | -0.050354 | 0.045776 | 0.16479 | 0.11444 | 0.15564 | 119.7098 | -2.4857 | -2.5177 | 119.8517 | 119.8334 | 119.7098 | 0.1236 | 0 | 119.7098 | -2.4216 | -2.4445 | 119.9249 | 119.9158 | 119.8746 | 0.20599 | 0.16479 | 0.14191 | 0.022888 | 0.21515 | 0.09613 | 0.054932 | 0.11902 | 119.7647 | 119.8288 | -2.5406 | -2.5406 | 119.7327 | 119.8059 | 119.6457 | 119.8013
6049.9688 | 122.4243 | -120.2225 | 2.0828 | -0.17372 | -0.037689 | 0.00066863 | 0.022082 | -0.00084593 | -0.0092478 | -0.0075003 | -0.11075 | 0.024964 | 0.017494 | -0.0084873 | -0.019651 | 0.026981 | -0.0025891 | -0.14648 | 0.045776 | -0.082397 | -0.10529 | -0.036621 | -0.15564 | -0.050354 | -0.086975 | 0.11902 | -0.073242 | -0.045776 | 0.018311 | -0.045776 | 0.059509 | 120.1401 | -2.037 | -2.1881 | 120.1859 | 120.1721 | 120.0668 | 0.032043 | -0.073243 | 120.1492 | -1.9638 | -2.1286 | 120.2408 | 120.282 | 120.1767 | 0.13275 | 0.027466 | 0.045776 | -0.022889 | 0.091553 | 0.027466 | 0.12817 | 0.19226 | 120.2682 | 120.3415 | -2.1652 | -2.1561 | 120.1172 | 120.1767 | 120.076 | 120.1355
6051.6719 | 122.4518 | -120.076 | 2.2339 | -0.12032 | -0.04068 | -0.0010404 | 0.017382 | -0.0031957 | -0.01352 | -0.0036551 | -0.071076 | 0.025178 | 0.015998 | -0.013187 | -0.018369 | 0.025699 | -0.0032299 | -0.13275 | 0.050354 | -0.073242 | -0.10529 | -0.013733 | -0.11444 | 0.009155 | -0.07782 | 0.11902 | -0.082397 | -0.027466 | 0.07782 | 0.022888 | 0.086975 | 120.0027 | -2.1835 | -2.3392 | 120.0623 | 120.0851 | 119.9615 | 0.082397 | -0.041199 | 119.9936 | -2.1149 | -2.2614 | 120.1538 | 120.163 | 120.0989 | 0.16937 | 0.10528 | 0.059509 | -0.032044 | 0.16022 | 0.054931 | 0.1236 | 0.20142 | 120.1263 | 120.195 | -2.3071 | -2.3163 | 119.9707 | 120.0485 | 119.9432 | 119.9982
6053.3906 | 122.4472 | -119.8837 | 2.3849 | -0.17372 | -0.040894 | 0.0023776 | 0.02016 | 0.0010767 | -0.010957 | -0.0019461 | -0.089386 | 0.025819 | 0.015357 | -0.011692 | -0.020292 | 0.026981 | -0.0062207 | -0.14191 | 0.041199 | -0.082397 | -0.09613 | 0 | -0.15106 | -0.027466 | -0.064087 | 0.10529 | -0.082397 | -0.027466 | 0.045776 | -0.009155 | 0.064087 | 119.8013 | -2.3438 | -2.4811 | 119.8837 | 119.8563 | 119.7327 | 0.054931 | -0.068665 | 119.8013 | -2.2797 | -2.4124 | 119.9295 | 119.9478 | 119.8746 | 0.14648 | 0.073242 | 0.082397 | -0.013733 | 0.12817 | 0.054931 | 0.1236 | 0.18768 | 119.9249 | 119.989 | -2.4673 | -2.4673 | 119.7876 | 119.8563 | 119.7418 | 119.8196
6055.0938 | 122.4289 | -119.9387 | 2.3804 | -0.11269 | -0.044098 | -0.001254 | 0.018237 | -0.0042639 | -0.013734 | -0.0064321 | -0.055817 | 0.023682 | 0.015571 | -0.012332 | -0.02136 | 0.02634 | -0.00066651 | -0.16022 | 0.059509 | -0.086975 | -0.10986 | 0 | -0.1236 | -0.004578 | -0.073242 | 0.1236 | -0.091553 | -0.059509 | 0.032043 | -0.013733 | 0.054932 | 119.8517 | -2.3209 | -2.4902 | 119.9387 | 119.9341 | 119.8151 | 0.082397 | -0.036621 | 119.8471 | -2.2568 | -2.4399 | 119.9707 | 119.9936 | 119.9249 | 0.14649 | 0.07782 | 0.086975 | -0.022888 | 0.1236 | 0.032044 | 0.14648 | 0.21515 | 119.9982 | 120.0623 | -2.4673 | -2.4719 | 119.8288 | 119.8792 | 119.7784 | 119.8654
6056.8125 | 122.5754 | -119.6045 | 2.6276 | -0.1432 | -0.04068 | -0.00018577 | 0.016742 | 0.00043587 | -0.011811 | -0.0060049 | 0.0052185 | 0.02411 | 0.01493 | -0.018314 | -0.020933 | 0.025485 | -0.0042981 | -0.082397 | 0.009155 | -0.041199 | 0.013733 | 0.16022 | 0.013733 | 0.12817 | 0.10071 | 0.073242 | -0.054932 | 0.068665 | 0.21057 | 0.15564 | 0.16937 | 119.5633 | -2.6184 | -2.6138 | 119.7647 | 119.7327 | 119.6182 | 0.16937 | 0.054932 | 119.5496 | -2.5543 | -2.5589 | 119.8151 | 119.7739 | 119.7601 | 0.22431 | 0.21057 | 0.20142 | 0.054932 | 0.2655 | 0.1236 | 0.050354 | 0.12817 | 119.6136 | 119.6777 | -2.6688 | -2.6825 | 119.6182 | 119.6732 | 119.5221 | 119.7052
6058.5781 | 122.4197 | -119.5862 | 2.7649 | -0.18898 | -0.040253 | -0.00039957 | 0.017382 | -0.0019141 | -0.011598 | -0.0070731 | -0.037506 | 0.022828 | 0.01493 | -0.011692 | -0.020078 | 0.026767 | -0.0030163 | -0.1236 | 0.032043 | -0.082397 | -0.086975 | 0.009155 | -0.10529 | 0.004578 | -0.059509 | 0.11902 | -0.086975 | -0.073242 | 0.054932 | -0.004578 | 0.041199 | 119.5038 | -2.7329 | -2.8519 | 119.5953 | 119.5908 | 119.4809 | 0.086975 | -0.022889 | 119.4992 | -2.6459 | -2.8381 | 119.6411 | 119.6274 | 119.5816 | 0.12817 | 0.082397 | 0.091552 | -0.004578 | 0.14191 | 0.013733 | 0.11444 | 0.20599 | 119.6182 | 119.7052 | -2.8473 | -2.8519 | 119.4992 | 119.5129 | 119.4626 | 119.5267
6060.2812 | 122.493 | -119.3069 | 2.9388 | -0.2195 | -0.040467 | -0.00082677 | 0.020373 | 0.00064947 | -0.010316 | -0.0064321 | -0.0069885 | 0.023682 | 0.014289 | -0.021091 | -0.019438 | 0.025485 | -0.0023755 | -0.10986 | 0 | -0.045776 | -0.036621 | 0.064087 | -0.068665 | 0.050354 | 0.009155 | 0.082397 | -0.045776 | 0.013733 | 0.11444 | 0.059509 | 0.11902 | 119.2612 | -2.9388 | -2.9755 | 119.371 | 119.3573 | 119.2383 | 0.09613 | -0.022889 | 119.2612 | -2.8564 | -2.9251 | 119.4214 | 119.426 | 119.3665 | 0.16479 | 0.10528 | 0.10986 | 0.009155 | 0.16022 | 0.059509 | 0.045776 | 0.12817 | 119.3069 | 119.3893 | -2.9846 | -2.9846 | 119.2703 | 119.3207 | 119.1971 | 119.3161
6062 | 122.5067 | -119.8105 | 2.449 | -0.17372 | -0.040894 | -0.0023222 | 0.018664 | -0.00063233 | -0.007966 | -0.0062185 | -0.025299 | 0.025178 | 0.013648 | -0.024295 | -0.020506 | 0.025699 | -0.0055799 | -0.12817 | 0.022888 | -0.041199 | -0.027466 | 0.07782 | -0.068665 | 0.054932 | 0.004578 | 0.082397 | -0.059509 | 0 | 0.11444 | 0.082397 | 0.11902 | 119.7693 | -2.4261 | -2.4765 | 119.8883 | 119.8654 | 119.7418 | 0.096131 | -0.027466 | 119.751 | -2.3666 | -2.449 | 119.9249 | 119.9295 | 119.8929 | 0.17853 | 0.14191 | 0.11902 | 0.013733 | 0.17395 | 0.059509 | 0.064087 | 0.14191 | 119.8334 | 119.8929 | -2.4902 | -2.5085 | 119.783 | 119.8105 | 119.6823 | 119.8151
6063.6875 | 122.4243 | -119.6915 | 2.623 | -0.18898 | -0.039398 | 0.001523 | 0.024432 | 0.0029993 | -0.011598 | -0.0055777 | -0.13211 | 0.025178 | 0.011939 | -0.016605 | -0.02136 | 0.027194 | -0.0064343 | -0.10529 | 0.041199 | -0.073242 | -0.086975 | -0.018311 | -0.15564 | -0.036621 | -0.086975 | 0.1236 | -0.086975 | -0.054932 | 0.004578 | -0.054932 | 0.036621 | 119.6182 | -2.5818 | -2.71 | 119.6732 | 119.6548 | 119.5358 | 0.036621 | -0.082398 | 119.6045 | -2.4994 | -2.6779 | 119.696 | 119.7281 | 119.6365 | 0.1236 | 0.032043 | 0.054931 | -0.013733 | 0.091553 | 0.032043 | 0.11444 | 0.21057 | 119.7327 | 119.8151 | -2.6962 | -2.71 | 119.6045 | 119.6365 | 119.5862 | 119.6045
6065.3906 | 122.5204 | -119.8196 | 2.4719 | -0.16609 | -0.038971 | 0.00066863 | 0.017596 | 0.00043587 | -0.012666 | -0.0047231 | -0.019196 | 0.02475 | 0.013648 | -0.018314 | -0.019651 | 0.025485 | -0.0028027 | -0.10986 | 0 | -0.036621 | -0.009155 | 0.10529 | -0.064087 | 0.059509 | 0.032043 | 0.07782 | -0.041199 | 0.027466 | 0.10986 | 0.073242 | 0.10986 | 119.783 | -2.4719 | -2.4811 | 119.9249 | 119.8792 | 119.7556 | 0.09613 | -0.027466 | 119.7784 | -2.3941 | -2.4445 | 119.9295 | 119.9295 | 119.8929 | 0.15106 | 0.11444 | 0.14191 | 0.027466 | 0.15106 | 0.068665 | 0.036621 | 0.11902 | 119.8196 | 119.8975 | -2.5085 | -2.5131 | 119.8105 | 119.8471 | 119.7098 | 119.8517
6067.0938 | 122.4472 | -119.5038 | 2.7969 | -0.18135 | -0.038544 | 0.00045503 | 0.020587 | -0.00063233 | -0.011811 | -0.0028005 | -0.11075 | 0.02475 | 0.016212 | -0.011051 | -0.018797 | 0.026126 | -0.0045117 | -0.13733 | 0.050354 | -0.091553 | -0.10071 | -0.027466 | -0.16022 | -0.032043 | -0.068665 | 0.10529 | -0.07782 | -0.045776 | 0.041199 | -0.032043 | 0.059509 | 119.4122 | -2.7466 | -2.8976 | 119.4763 | 119.4717 | 119.3436 | 0.05951 | -0.068664 | 119.426 | -2.6917 | -2.8427 | 119.545 | 119.5633 | 119.4717 | 0.13733 | 0.045777 | 0.064087 | -0.009155 | 0.11902 | 0.032044 | 0.14191 | 0.18311 | 119.5541 | 119.6091 | -2.8885 | -2.8748 | 119.4031 | 119.458 | 119.3665 | 119.4351
6068.7969 | 122.4518 | -119.8563 | 2.4399 | -0.1432 | -0.044098 | -0.0016812 | 0.017382 | -0.0021277 | -0.014161 | -0.0066457 | -0.028351 | 0.023041 | 0.01493 | -0.012119 | -0.019438 | 0.025272 | -0.0070751 | -0.091553 | 0.036621 | -0.068665 | -0.073242 | 0.054932 | -0.073242 | 0.018311 | -0.032043 | 0.10071 | -0.07782 | -0.054932 | 0.064087 | 0.018311 | 0.054932 | 119.7876 | -2.4033 | -2.5131 | 119.9112 | 119.8746 | 119.783 | 0.086976 | -0.004577 | 119.7784 | -2.3392 | -2.4948 | 119.9203 | 119.9112 | 119.8746 | 0.13275 | 0.096131 | 0.1236 | -0.004577 | 0.14191 | 0.022888 | 0.10529 | 0.17853 | 119.8929 | 119.957 | -2.5085 | -2.5177 | 119.783 | 119.8013 | 119.7647 | 119.8242
6070.5625 | 122.5113 | -119.4672 | 2.8152 | -0.18135 | -0.040894 | 0.00024143 | 0.019091 | -0.00041873 | -0.012666 | -0.0057913 | -0.013092 | 0.022187 | 0.013221 | -0.0035739 | -0.019224 | 0.025699 | -0.0030163 | -0.073242 | -0.004578 | -0.032043 | 0.013733 | 0.13733 | -0.013733 | 0.091553 | 0.050354 | 0.091553 | -0.050354 | 0.022888 | 0.13733 | 0.09613 | 0.10986 | 119.4351 | -2.8198 | -2.8015 | 119.6045 | 119.5587 | 119.4534 | 0.1236 | 0.01831 | 119.4168 | -2.7237 | -2.7924 | 119.6045 | 119.577 | 119.5633 | 0.16022 | 0.14648 | 0.16937 | 0.045776 | 0.18768 | 0.073242 | 0.027465 | 0.14191 | 119.4626 | 119.5587 | -2.8473 | -2.8656 | 119.4809 | 119.4901 | 119.3939 | 119.5175
6072.2656 | 122.5159 | -119.9936 | 2.2659 | -0.25002 | -0.039826 | 0.0013094 | 0.018237 | 0.00064947 | -0.012452 | -0.0047231 | -0.04361 | 0.023041 | 0.013435 | -0.012546 | -0.019224 | 0.024204 | -0.0028027 | -0.086975 | 0 | -0.032043 | 0.009155 | 0.1236 | -0.050354 | 0.059509 | 0.059509 | 0.07782 | -0.045776 | 0.032043 | 0.13275 | 0.082397 | 0.11902 | 119.9615 | -2.2659 | -2.2568 | 120.1172 | 120.0531 | 119.9432 | 0.091552 | -0.018311 | 119.9478 | -2.1881 | -2.2339 | 120.1263 | 120.1126 | 120.076 | 0.16479 | 0.12817 | 0.15564 | 0.041198 | 0.17853 | 0.077819 | 0.032043 | 0.1236 | 119.9936 | 120.0714 | -2.298 | -2.3117 | 120.0027 | 120.0256 | 119.9066 | 120.0531
6073.9688 | 122.5204 | -119.7739 | 2.5131 | -0.18135 | -0.039398 | 0.00088223 | 0.021441 | -0.00084593 | -0.012666 | -0.0028005 | -0.089386 | 0.022401 | 0.016426 | -0.0057101 | -0.020506 | 0.025272 | -0.0062207 | -0.11902 | 0.054932 | -0.054932 | -0.059509 | 0.013733 | -0.11902 | 0.013733 | -0.004578 | 0.10529 | -0.068665 | 0.045776 | 0.11902 | 0.054932 | 0.11444 | 119.7189 | -2.4582 | -2.5726 | 119.7876 | 119.7876 | 119.6548 | 0.068665 | -0.064087 | 119.7052 | -2.4078 | -2.4673 | 119.8929 | 119.8883 | 119.8288 | 0.18311 | 0.1236 | 0.068665 | -0.004577 | 0.18768 | 0.11444 | 0.10986 | 0.17395 | 119.8288 | 119.8792 | -2.5681 | -2.5818 | 119.7144 | 119.8196 | 119.6548 | 119.7693
6075.6719 | 122.493 | -119.6045 | 2.7191 | -0.15846 | -0.039612 | 0.00024143 | 0.019305 | 0.0027857 | -0.013093 | -0.0060049 | -0.11685 | 0.023469 | 0.014717 | -0.0042147 | -0.020933 | 0.026767 | -0.0013073 | -0.10529 | 0.032043 | -0.073242 | -0.054932 | 0.013733 | -0.086975 | 0.018311 | -0.004578 | 0.10529 | -0.07782 | 0.004578 | 0.10071 | 0.027466 | 0.10071 | 119.5312 | -2.6871 | -2.774 | 119.6182 | 119.6228 | 119.5175 | 0.091553 | -0.013733 | 119.5267 | -2.6138 | -2.7145 | 119.7052 | 119.7052 | 119.632 | 0.17853 | 0.10529 | 0.086975 | 0.01831 | 0.17853 | 0.082398 | 0.10529 | 0.18311 | 119.6365 | 119.7098 | -2.7924 | -2.7969 | 119.5496 | 119.6091 | 119.4992 | 119.5999
6077.3906 | 122.493 | -119.4855 | 2.8152 | -0.17372 | -0.039826 | 0.00045503 | 0.018878 | 0.0015039 | -0.010743 | -0.0036551 | -0.1077 | 0.022187 | 0.013648 | -0.0069919 | -0.020078 | 0.025912 | -0.0034435 | -0.07782 | 0.036621 | -0.054932 | -0.036621 | 0.059509 | -0.07782 | 0.036621 | 0.032043 | 0.10529 | -0.073242 | 0.013733 | 0.11902 | 0.050354 | 0.091553 | 119.4305 | -2.7786 | -2.8519 | 119.545 | 119.5221 | 119.4077 | 0.091553 | -0.022888 | 119.4122 | -2.71 | -2.8015 | 119.6045 | 119.577 | 119.5358 | 0.16479 | 0.1236 | 0.11444 | 0.018311 | 0.19226 | 0.086975 | 0.091553 | 0.17853 | 119.5221 | 119.5908 | -2.8702 | -2.8885 | 119.4489 | 119.4992 | 119.4077 | 119.5175
6079.1094 | 122.4243 | -119.8425 | 2.4948 | -0.18135 | -0.036408 | 0.00088223 | 0.019519 | 0.0040675 | -0.013093 | -0.0034415 | -0.10464 | 0.020478 | 0.013221 | -0.0097689 | -0.017942 | 0.025485 | -0.00066651 | -0.1236 | 0.041199 | -0.07782 | -0.10071 | -0.032043 | -0.16937 | -0.054932 | -0.091553 | 0.12817 | -0.073242 | -0.064087 | 0.004578 | -0.054932 | 0.041199 | 119.7647 | -2.4536 | -2.5955 | 119.8105 | 119.7876 | 119.6732 | 0.022888 | -0.091553 | 119.7693 | -2.3666 | -2.5589 | 119.8471 | 119.8837 | 119.7876 | 0.11444 | 0.01831 | 0.045777 | -0.022888 | 0.07782 | 0.009155 | 0.11902 | 0.20142 | 119.8837 | 119.9707 | -2.5726 | -2.5681 | 119.7418 | 119.7784 | 119.7189 | 119.751
6080.8125 | 122.438 | -120.369 | 1.9958 | -0.074539 | -0.041535 | 0.00024143 | 0.016101 | -0.0012731 | -0.013734 | -0.0064321 | -0.049713 | 0.025819 | 0.015144 | -0.016605 | -0.017301 | 0.024844 | 0.0014697 | -0.14191 | 0.059509 | -0.091553 | -0.10529 | 0.004578 | -0.10529 | -0.009155 | -0.082397 | 0.11902 | -0.086975 | -0.068665 | 0.054932 | -0.009155 | 0.045776 | 120.2774 | -1.9363 | -2.1011 | 120.3735 | 120.3598 | 120.2637 | 0.082398 | -0.013733 | 120.282 | -1.8768 | -2.0645 | 120.4239 | 120.4147 | 120.3598 | 0.13275 | 0.07782 | 0.096131 | -0.013733 | 0.14191 | 0.01831 | 0.15106 | 0.20599 | 120.4285 | 120.488 | -2.0874 | -2.0828 | 120.2637 | 120.3003 | 120.2271 | 120.2866
6082.5156 | 122.5525 | -119.751 | 2.5223 | -0.23476 | -0.041748 | -0.00039957 | 0.017382 | 0.0010767 | -0.013947 | -0.0040823 | 0.026581 | 0.022401 | 0.014076 | -0.0093417 | -0.018156 | 0.024844 | -0.0057935 | -0.12817 | 0.022888 | -0.036621 | -0.036621 | 0.082397 | -0.045776 | 0.073242 | 0.032043 | 0.073242 | -0.059509 | 0.045776 | 0.15106 | 0.1236 | 0.14648 | 119.7144 | -2.4994 | -2.5589 | 119.8334 | 119.8242 | 119.7052 | 0.10986 | -0.009155 | 119.6915 | -2.449 | -2.4765 | 119.902 | 119.8975 | 119.8746 | 0.20599 | 0.1831 | 0.11902 | 0 | 0.21057 | 0.10528 | 0.059509 | 0.13275 | 119.7739 | 119.8242 | -2.5589 | -2.5818 | 119.7144 | 119.7968 | 119.6228 | 119.783
6084.2188 | 122.4472 | -119.8563 | 2.4948 | -0.12794 | -0.042389 | -0.00018577 | 0.016742 | 0.0025721 | -0.013307 | -0.0042959 | -0.04361 | 0.02411 | 0.01728 | -0.012332 | -0.019865 | 0.02634 | -0.0032299 | -0.14191 | 0.064087 | -0.082397 | -0.09613 | 0.009155 | -0.10986 | 0 | -0.059509 | 0.12817 | -0.068665 | -0.07782 | 0.041199 | -0.009155 | 0.050354 | 119.7739 | -2.4307 | -2.5909 | 119.8654 | 119.8563 | 119.7464 | 0.082397 | -0.027466 | 119.7876 | -2.3666 | -2.5726 | 119.8975 | 119.9066 | 119.8471 | 0.11902 | 0.05951 | 0.091552 | -0.013733 | 0.10986 | -0.009155 | 0.14648 | 0.19684 | 119.9203 | 119.9844 | -2.5772 | -2.5635 | 119.7601 | 119.7784 | 119.7144 | 119.7968
6085.9375 | 122.4655 | -119.8471 | 2.4994 | -0.13557 | -0.039398 | -0.00018577 | 0.02016 | 0.0029993 | -0.013093 | -0.0032277 | -0.10159 | 0.023041 | 0.015571 | -0.0042147 | -0.021147 | 0.027621 | -0.0015209 | -0.086975 | 0.032043 | -0.054932 | -0.059509 | 0.027466 | -0.11444 | -0.027466 | -0.018311 | 0.09613 | -0.07782 | -0.032043 | 0.036621 | -0.018311 | 0.059509 | 119.7922 | -2.4673 | -2.5589 | 119.8746 | 119.8196 | 119.7327 | 0.027466 | -0.059509 | 119.7693 | -2.4033 | -2.5314 | 119.8837 | 119.9066 | 119.8288 | 0.13733 | 0.059509 | 0.082398 | -0.004577 | 0.11444 | 0.045777 | 0.086975 | 0.17395 | 119.8791 | 119.9432 | -2.5543 | -2.5772 | 119.7876 | 119.8151 | 119.7601 | 119.8288
6087.6562 | 122.5662 | -119.6869 | 2.536 | -0.26527 | -0.038758 | -0.00039957 | 0.01781 | -0.00041873 | -0.01117 | -0.0064321 | -0.04361 | 0.023255 | 0.013221 | -0.019168 | -0.020292 | 0.02634 | -0.0015209 | -0.054932 | 0.009155 | -0.032043 | 0.032043 | 0.15106 | -0.045776 | 0.091553 | 0.091553 | 0.07782 | -0.036621 | 0.064087 | 0.16479 | 0.10529 | 0.15106 | 119.6548 | -2.5269 | -2.504 | 119.838 | 119.7784 | 119.6411 | 0.1236 | -0.013733 | 119.6503 | -2.4582 | -2.4719 | 119.8517 | 119.838 | 119.7922 | 0.18768 | 0.14191 | 0.18311 | 0.064086 | 0.20142 | 0.10071 | 0.041198 | 0.11444 | 119.696 | 119.7647 | -2.5681 | -2.5726 | 119.7189 | 119.751 | 119.632 | 119.7784
6089.3594 | 122.5708 | -119.6732 | 2.5955 | -0.11269 | -0.04068 | -0.0018948 | 0.015887 | -0.0023413 | -0.012025 | -0.00087794 | -0.0039367 | 0.022401 | 0.012367 | -0.01276 | -0.01901 | 0.026981 | -0.0042981 | -0.064087 | 0 | -0.036621 | 0.032043 | 0.15106 | 0.004578 | 0.10529 | 0.082397 | 0.068665 | -0.050354 | 0.036621 | 0.17853 | 0.11902 | 0.14191 | 119.6365 | -2.5955 | -2.5635 | 119.8242 | 119.7784 | 119.6777 | 0.14191 | 0.041199 | 119.6228 | -2.5269 | -2.5589 | 119.8517 | 119.8151 | 119.7922 | 0.19226 | 0.16937 | 0.18768 | 0.068664 | 0.22888 | 0.086975 | 0.036621 | 0.11902 | 119.6732 | 119.7418 | -2.6321 | -2.6459 | 119.7052 | 119.7098 | 119.6091 | 119.7556
6091.0625 | 122.5616 | -119.3985 | 2.8427 | -0.26527 | -0.037049 | -0.00039957 | 0.01781 | -0.00041873 | -0.012239 | -0.0060049 | -0.034454 | 0.021332 | 0.016426 | -0.013187 | -0.021147 | 0.025912 | -0.0013073 | -0.059509 | 0.009155 | -0.045776 | 0.027466 | 0.14191 | -0.027466 | 0.07782 | 0.086975 | 0.068665 | -0.050354 | 0.059509 | 0.15564 | 0.091553 | 0.14191 | 119.3527 | -2.8336 | -2.8152 | 119.5404 | 119.4763 | 119.371 | 0.1236 | 0.01831 | 119.3481 | -2.774 | -2.7832 | 119.5541 | 119.5404 | 119.4901 | 0.19226 | 0.14191 | 0.18768 | 0.073242 | 0.20599 | 0.10986 | 0.054931 | 0.11902 | 119.4077 | 119.4672 | -2.8885 | -2.8931 | 119.426 | 119.458 | 119.339 | 119.4855
6092.7656 | 122.5067 | -119.8013 | 2.4948 | -0.13557 | -0.037689 | -0.0010404 | 0.021014 | -0.0031957 | -0.013307 | -0.0045095 | -0.09549 | 0.025178 | 0.014717 | -0.012332 | -0.021787 | 0.026981 | -0.0030163 | -0.09613 | 0.045776 | -0.082397 | -0.050354 | 0.059509 | -0.09613 | 0.009155 | 0.013733 | 0.10986 | -0.068665 | 0.009155 | 0.09613 | 0.041199 | 0.09613 | 119.7189 | -2.449 | -2.5452 | 119.8608 | 119.8105 | 119.7052 | 0.091552 | -0.013733 | 119.7327 | -2.3849 | -2.4857 | 119.8975 | 119.8975 | 119.8425 | 0.16479 | 0.10986 | 0.14191 | 0.032043 | 0.16479 | 0.07782 | 0.12817 | 0.17853 | 119.8471 | 119.9112 | -2.5772 | -2.5635 | 119.751 | 119.8105 | 119.7052 | 119.8151
6094.4844 | 122.4564 | -119.7922 | 2.5589 | -0.20424 | -0.037262 | 0.0017368 | 0.022509 | 0.0036401 | -0.013093 | -0.0051505 | -0.11075 | 0.022828 | 0.016212 | -0.015323 | -0.019651 | 0.027621 | -0.0032299 | -0.09613 | 0.041199 | -0.064087 | -0.068665 | 0.018311 | -0.12817 | -0.004578 | -0.045776 | 0.11902 | -0.091553 | -0.032043 | 0.027466 | -0.027466 | 0.045776 | 119.7281 | -2.5177 | -2.6276 | 119.8105 | 119.7876 | 119.664 | 0.059509 | -0.064087 | 119.7006 | -2.4399 | -2.5909 | 119.8196 | 119.838 | 119.7647 | 0.13733 | 0.064087 | 0.082398 | -0.004578 | 0.11902 | 0.05951 | 0.10529 | 0.21057 | 119.8334 | 119.9112 | -2.623 | -2.6505 | 119.7235 | 119.7601 | 119.696 | 119.7464
6096.1875 | 121.8338 | -118.9362 | 2.1286 | -0.1432 | -0.04068 | 0.0017368 | 0.016955 | -0.0042639 | -0.014161 | -0.0034415 | 0.014374 | 0.023255 | 0.015785 | -0.0065647 | -0.019651 | 0.024417 | -0.00023931 | -0.07782 | 0.013733 | -0.032043 | 0.032043 | 0.15564 | 0.009155 | 0.091553 | 0.10071 | 0.07782 | -0.054932 | 0.068665 | 0.18768 | 0.14191 | 0.14191 | 118.9041 | -2.1149 | -2.0966 | 119.0918 | 119.0277 | 118.9453 | 0.1236 | 0.041198 | 118.8812 | -2.0508 | -2.0599 | 119.1238 | 119.0781 | 119.0781 | 0.19684 | 0.19684 | 0.18768 | 0.064086 | 0.24261 | 0.1236 | 0.045776 | 0.13275 | 118.9499 | 119.014 | -2.1606 | -2.1835 | 118.9682 | 119.0048 | 118.8583 | 119.0369
6097.8906 | 122.0901 | -108.9157 | 12.8677 | -0.12794 | -0.043457 | 0.0010958 | 0.018878 | -0.0023413 | -0.015443 | -0.0051505 | -0.040558 | 0.023255 | 0.013221 | -0.014469 | -0.018583 | 0.023349 | -0.0038709 | -0.14191 | 0.009155 | -0.068665 | -0.064087 | 0.041199 | -0.10071 | 0.022888 | -0.059509 | 0.086975 | -0.07782 | -0.036621 | 0.045776 | 0.018311 | 0.045776 | 108.847 | -12.8586 | -12.9318 | 108.9569 | 108.9386 | 108.815 | 0.091553 | -0.032043 | 108.8379 | -12.7808 | -12.9044 | 108.9615 | 108.9615 | 108.934 | 0.1236 | 0.096131 | 0.10986 | 0.004578 | 0.1236 | 0.041199 | 0.07782 | 0.16479 | 108.9249 | 109.0027 | -12.9364 | -12.9456 | 108.8516 | 108.8791 | 108.7738 | 108.8562
6099.6406 | 122.3145 | -120.4788 | 1.3779 | -0.22713 | -0.037903 | 0.0017368 | 0.020587 | -0.00063233 | -0.013093 | -2.3544e-05 | -0.04361 | 0.024537 | 0.011512 | -0.016391 | -0.02136 | 0.025699 | -0.0019483 | -0.054932 | -0.004578 | -0.032043 | 0.027466 | 0.15106 | -0.027466 | 0.082397 | 0.10071 | 0.064087 | -0.027466 | 0.10529 | 0.16022 | 0.10071 | 0.15564 | 120.4468 | -1.3824 | -1.3504 | 120.6299 | 120.5612 | 120.4514 | 0.11444 | 0.004577 | 120.4514 | -1.3138 | -1.2726 | 120.639 | 120.6345 | 120.5795 | 0.18311 | 0.12817 | 0.18311 | 0.059509 | 0.18768 | 0.13275 | 0.027465 | 0.091553 | 120.4742 | 120.5429 | -1.4099 | -1.4053 | 120.5063 | 120.5841 | 120.4239 | 120.5795
6101.3438 | 122.2183 | -120.5612 | 1.4374 | -0.15083 | -0.039612 | 0.0023776 | 0.022937 | 0.00086307 | -0.013093 | -0.0034415 | -0.11685 | 0.023469 | 0.013648 | -0.0072055 | -0.019651 | 0.025912 | -0.0019483 | -0.10986 | 0.059509 | -0.073242 | -0.059509 | 0.013733 | -0.11902 | -0.004578 | -0.036621 | 0.10986 | -0.068665 | -0.018311 | 0.018311 | -0.032043 | 0.068665 | 120.488 | -1.3779 | -1.4969 | 120.575 | 120.5566 | 120.4422 | 0.068664 | -0.045777 | 120.4926 | -1.3275 | -1.4557 | 120.5795 | 120.6299 | 120.5292 | 0.13733 | 0.036622 | 0.086975 | 0.013733 | 0.086976 | 0.050354 | 0.13275 | 0.17853 | 120.6207 | 120.6711 | -1.5106 | -1.506 | 120.5017 | 120.5429 | 120.4514 | 120.5246
6103.0625 | 122.2458 | -120.6345 | 1.442 | -0.15083 | -0.041535 | -0.00061317 | 0.020373 | -0.0034095 | -0.013734 | -0.0028005 | -0.016144 | 0.021332 | 0.013862 | -0.0054965 | -0.019865 | 0.025272 | -0.0047253 | -0.11444 | 0.018311 | -0.054932 | -0.064087 | 0.054932 | -0.068665 | 0.027466 | -0.036621 | 0.10986 | -0.054932 | -0.036621 | 0.054932 | 0.009155 | 0.054932 | 120.5795 | -1.4236 | -1.506 | 120.6894 | 120.6619 | 120.5658 | 0.082398 | -0.013733 | 120.5795 | -1.3321 | -1.4786 | 120.6894 | 120.6894 | 120.6436 | 0.10986 | 0.064087 | 0.10986 | -0.009155 | 0.10986 | 0.018311 | 0.073243 | 0.16479 | 120.6528 | 120.7443 | -1.4969 | -1.4969 | 120.5704 | 120.5978 | 120.52 | 120.5978
6104.7656 | 122.3694 | -120.6024 | 1.442 | -0.18898 | -0.041962 | -0.00039957 | 0.017169 | -0.0034095 | -0.011598 | -0.0017325 | 0.026581 | 0.02411 | 0.014717 | -0.012332 | -0.019224 | 0.024631 | -0.00088011 | -0.091553 | 0.022888 | -0.045776 | -0.036621 | 0.086975 | -0.050354 | 0.07782 | 0.041199 | 0.086975 | -0.054932 | 0.059509 | 0.14648 | 0.10529 | 0.14191 | 120.5566 | -1.4191 | -1.4786 | 120.6894 | 120.6802 | 120.5521 | 0.1236 | -0.004578 | 120.5475 | -1.355 | -1.3824 | 120.7489 | 120.7443 | 120.7077 | 0.19684 | 0.16022 | 0.13275 | 0.009155 | 0.20142 | 0.11444 | 0.068664 | 0.14191 | 120.6253 | 120.6894 | -1.4877 | -1.4969 | 120.5658 | 120.6619 | 120.5109 | 120.6436
6106.5 | 122.2916 | -118.5791 | 3.5202 | -0.074539 | -0.039185 | 2.7834e-05 | 0.021014 | 0.00064947 | -0.012239 | -0.0053641 | -0.074127 | 0.023896 | 0.014503 | -0.011051 | -0.022215 | 0.02634 | -0.0057935 | -0.10986 | 0.054932 | -0.07782 | -0.082397 | 0.004578 | -0.086975 | 0.004578 | -0.027466 | 0.11444 | -0.054932 | 0.004578 | 0.091553 | 0.027466 | 0.09613 | 118.5013 | -3.4653 | -3.6026 | 118.5837 | 118.5837 | 118.4921 | 0.082398 | -0.009155 | 118.5242 | -3.4058 | -3.5156 | 118.6707 | 118.6752 | 118.6066 | 0.15106 | 0.082398 | 0.082398 | -0.004577 | 0.14649 | 0.05951 | 0.13275 | 0.16937 | 118.634 | 118.6935 | -3.598 | -3.5751 | 118.4967 | 118.5837 | 118.4692 | 118.5516
6108.2031 | 122.3602 | -94.3588 | 27.5116 | -0.18898 | -0.040253 | -0.002963 | 0.018664 | -0.0081091 | -0.012879 | -0.0049367 | 0.0021667 | 0.021332 | 0.013862 | -0.017887 | -0.019865 | 0.025485 | -0.0064343 | -0.10986 | 0.004578 | -0.059509 | -0.041199 | 0.059509 | -0.07782 | 0.050354 | -0.004578 | 0.082397 | -0.059509 | 0.032043 | 0.1236 | 0.073242 | 0.11444 | 94.2993 | -27.507 | -27.5528 | 94.4183 | 94.4092 | 94.281 | 0.10986 | -0.018311 | 94.2993 | -27.4292 | -27.4796 | 94.4824 | 94.4733 | 94.4321 | 0.17395 | 0.13275 | 0.11902 | 0.01831 | 0.1831 | 0.091552 | 0.064087 | 0.14191 | 94.3634 | 94.4412 | -27.5711 | -27.5711 | 94.3176 | 94.3909 | 94.249 | 94.3542
6109.9219 | 122.3419 | -120.6253 | 1.4923 | -0.15083 | -0.040467 | -0.00018577 | 0.01781 | -0.0029821 | -0.013307 | -0.0070731 | -0.046661 | 0.023041 | 0.013435 | -0.0069919 | -0.021147 | 0.025699 | -0.0013073 | -0.14648 | 0.050354 | -0.064087 | -0.082397 | 0.004578 | -0.10529 | -0.004578 | -0.054932 | 0.10986 | -0.10071 | -0.045776 | 0.022888 | 0 | 0.036621 | 120.5612 | -1.442 | -1.5747 | 120.6299 | 120.6207 | 120.52 | 0.059509 | -0.041199 | 120.5246 | -1.3824 | -1.5381 | 120.6482 | 120.6619 | 120.6253 | 0.13733 | 0.10071 | 0.068665 | -0.01831 | 0.1236 | 0.054932 | 0.11444 | 0.21057 | 120.6757 | 120.7352 | -1.5564 | -1.593 | 120.5429 | 120.5795 | 120.4788 | 120.5704
6111.6406 | 122.3511 | -113.7634 | 8.2535 | -0.22713 | -0.038117 | -0.0023222 | 0.022082 | -0.0019141 | -0.010957 | -0.0021597 | -0.098541 | 0.02411 | 0.015357 | -0.013614 | -0.018369 | 0.02634 | -0.0036573 | -0.12817 | 0.050354 | -0.059509 | -0.10071 | -0.013733 | -0.14648 | -0.022888 | -0.050354 | 0.10986 | -0.082397 | 0.009155 | 0.027466 | -0.022888 | 0.07782 | 113.7039 | -8.2031 | -8.3542 | 113.7497 | 113.7405 | 113.6169 | 0.036621 | -0.086975 | 113.681 | -8.1436 | -8.2443 | 113.7909 | 113.8412 | 113.7405 | 0.16022 | 0.059509 | 0.045776 | -0.041199 | 0.10986 | 0.091552 | 0.10986 | 0.19226 | 113.8138 | 113.8733 | -8.313 | -8.3359 | 113.6627 | 113.7726 | 113.6353 | 113.7131
6113.3438 | 122.3465 | -120.6207 | 1.5198 | -0.074539 | -0.041962 | -0.002963 | 0.018878 | 0.00043587 | -0.014161 | -0.0032277 | -0.086334 | 0.024964 | 0.016212 | -0.011051 | -0.018156 | 0.027194 | -0.0023755 | -0.14648 | 0.059509 | -0.10529 | -0.091553 | -0.018311 | -0.10986 | -0.013733 | -0.073242 | 0.10529 | -0.082397 | -0.013733 | 0.045776 | -0.004578 | 0.059509 | 120.5154 | -1.4603 | -1.6113 | 120.6024 | 120.607 | 120.5109 | 0.091553 | -0.004577 | 120.5383 | -1.4145 | -1.5335 | 120.6665 | 120.6802 | 120.6162 | 0.14191 | 0.077819 | 0.086975 | 0.013733 | 0.12817 | 0.068664 | 0.16479 | 0.18768 | 120.6802 | 120.726 | -1.6251 | -1.6022 | 120.5292 | 120.607 | 120.4742 | 120.5475
6115.0469 | 122.438 | -120.5933 | 1.5198 | -0.12794 | -0.04068 | 0.00024143 | 0.018023 | -0.00020513 | -0.014375 | -0.0015189 | -0.022247 | 0.022614 | 0.017494 | -0.014896 | -0.01901 | 0.026126 | -0.0023755 | -0.059509 | 0.004578 | -0.041199 | 0.045776 | 0.16022 | 0.022888 | 0.091553 | 0.082397 | 0.082397 | -0.045776 | 0.082397 | 0.17395 | 0.13275 | 0.13733 | 120.5521 | -1.5152 | -1.474 | 120.7535 | 120.6848 | 120.6161 | 0.13275 | 0.064087 | 120.5475 | -1.4374 | -1.4374 | 120.7672 | 120.7306 | 120.726 | 0.18311 | 0.17853 | 0.20142 | 0.086975 | 0.21973 | 0.12817 | 0.045777 | 0.12817 | 120.5978 | 120.6757 | -1.561 | -1.5656 | 120.639 | 120.6757 | 120.5338 | 120.6757
6116.75 | 122.3877 | -120.5704 | 1.5564 | -0.13557 | -0.03833 | 0.00024143 | 0.018451 | -0.0012731 | -0.013093 | -0.0075003 | -0.028351 | 0.020905 | 0.013008 | -0.014041 | -0.019224 | 0.026126 | -0.0062207 | -0.10529 | 0.018311 | -0.050354 | -0.050354 | 0.050354 | -0.073242 | 0.045776 | -0.004578 | 0.091553 | -0.045776 | 0.045776 | 0.1236 | 0.068665 | 0.11444 | 120.52 | -1.5381 | -1.6067 | 120.6207 | 120.6162 | 120.4971 | 0.09613 | -0.022888 | 120.5246 | -1.4648 | -1.5106 | 120.694 | 120.6848 | 120.639 | 0.16022 | 0.11444 | 0.10071 | 0 | 0.16937 | 0.091552 | 0.068665 | 0.13733 | 120.5887 | 120.6619 | -1.6067 | -1.6022 | 120.52 | 120.6162 | 120.4651 | 120.5658
6118.4688 | 122.406 | -120.5475 | 1.5381 | -0.18135 | -0.03833 | 0.002164 | 0.022082 | -0.0031957 | -0.011811 | -0.0042959 | -0.089386 | 0.025605 | 0.015144 | -0.0091281 | -0.018156 | 0.026981 | -0.00088011 | -0.11444 | 0.018311 | -0.068665 | -0.032043 | 0.045776 | -0.086975 | 0.022888 | 0.027466 | 0.09613 | -0.064087 | 0.091553 | 0.14191 | 0.07782 | 0.15106 | 120.4788 | -1.5198 | -1.5701 | 120.5933 | 120.5704 | 120.4605 | 0.091553 | -0.01831 | 120.4834 | -1.442 | -1.4465 | 120.6894 | 120.6985 | 120.6253 | 0.21515 | 0.14191 | 0.11444 | 0.036622 | 0.20599 | 0.15564 | 0.086976 | 0.16022 | 120.5658 | 120.6436 | -1.6068 | -1.6022 | 120.5154 | 120.639 | 120.433 | 120.575
6120.1719 | 122.3236 | -120.5933 | 1.5793 | -0.13557 | -0.040894 | -0.0010404 | 0.022509 | 0.0015039 | -0.011384 | -0.0042959 | -0.098541 | 0.023041 | 0.014076 | -0.014896 | -0.019865 | 0.028262 | -0.0085705 | -0.13733 | 0.068665 | -0.064087 | -0.10071 | -0.013733 | -0.11444 | -0.009155 | -0.064087 | 0.10529 | -0.07782 | -0.004578 | 0.068665 | 0.009155 | 0.07782 | 120.5292 | -1.5106 | -1.68 | 120.5795 | 120.5841 | 120.4788 | 0.054932 | -0.050354 | 120.5154 | -1.474 | -1.5839 | 120.6619 | 120.6711 | 120.6024 | 0.15564 | 0.086975 | 0.050354 | -0.036621 | 0.14649 | 0.073242 | 0.13275 | 0.18311 | 120.6619 | 120.6985 | -1.6434 | -1.6571 | 120.4926 | 120.5887 | 120.4559 | 120.5292
6121.8906 | 122.438 | -120.5475 | 1.5656 | -0.20424 | -0.04068 | 0.00024143 | 0.021441 | 0.0015039 | -0.012025 | -0.0070731 | -0.049713 | 0.023469 | 0.011085 | -0.015537 | -0.020933 | 0.025912 | -0.0013073 | -0.064087 | 0.013733 | -0.050354 | 0.004578 | 0.11902 | -0.045776 | 0.07782 | 0.073242 | 0.068665 | -0.045776 | 0.10071 | 0.16937 | 0.10986 | 0.16937 | 120.4971 | -1.5518 | -1.561 | 120.6665 | 120.6253 | 120.5017 | 0.12817 | 0.004578 | 120.5017 | -1.4969 | -1.4648 | 120.7169 | 120.7169 | 120.6573 | 0.21515 | 0.15564 | 0.16937 | 0.054932 | 0.21515 | 0.14648 | 0.064087 | 0.11444 | 120.5612 | 120.6161 | -1.6159 | -1.6113 | 120.5521 | 120.6482 | 120.4834 | 120.6207
6123.6406 | 122.3877 | -120.2682 | 1.8951 | -0.1432 | -0.037476 | 0.0010958 | 0.018023 | 0.0021447 | -0.012025 | -0.0053641 | -0.052765 | 0.023469 | 0.014503 | -0.016605 | -0.019438 | 0.025058 | -0.0038709 | -0.10071 | -0.004578 | -0.041199 | -0.013733 | 0.09613 | -0.068665 | 0.054932 | 0.022888 | 0.07782 | -0.045776 | 0.041199 | 0.11444 | 0.059509 | 0.11444 | 120.2271 | -1.8997 | -1.9089 | 120.3644 | 120.3232 | 120.1996 | 0.096131 | -0.027466 | 120.2225 | -1.8173 | -1.8539 | 120.3827 | 120.3827 | 120.3278 | 0.16022 | 0.10528 | 0.13733 | 0.027466 | 0.16022 | 0.086975 | 0.036621 | 0.1236 | 120.2637 | 120.3461 | -1.9363 | -1.9409 | 120.2545 | 120.3094 | 120.1675 | 120.2911
6125.3281 | 122.3053 | -120.2911 | 1.9226 | -0.19661 | -0.040894 | 0.00088223 | 0.022296 | 0.0029993 | -0.012239 | -0.0023733 | -0.12296 | 0.024964 | 0.013862 | -0.014682 | -0.022428 | 0.027621 | -0.0021619 | -0.13275 | 0.045776 | -0.082397 | -0.10529 | -0.022888 | -0.17395 | -0.045776 | -0.10529 | 0.11902 | -0.073242 | -0.050354 | 0.004578 | -0.073242 | 0.045776 | 120.2087 | -1.8768 | -2.0279 | 120.2683 | 120.2454 | 120.1172 | 0.036621 | -0.091553 | 120.2179 | -1.8036 | -1.973 | 120.2957 | 120.3369 | 120.2179 | 0.11902 | 0 | 0.059509 | -0.022889 | 0.07782 | 0.022888 | 0.12817 | 0.19226 | 120.3369 | 120.4102 | -2.005 | -1.9958 | 120.1859 | 120.2408 | 120.1584 | 120.1859
6127.0312 | 122.4197 | -120.2728 | 1.8768 | -0.15846 | -0.040894 | -0.00061317 | 0.019732 | -0.0038367 | -0.015229 | -0.0042959 | -0.0039367 | 0.021546 | 0.013435 | -0.024082 | -0.021574 | 0.02399 | -0.0042981 | -0.068665 | -0.004578 | -0.045776 | 0.036621 | 0.15564 | 0.004578 | 0.10986 | 0.09613 | 0.082397 | -0.054932 | 0.07782 | 0.19684 | 0.12817 | 0.13275 | 120.2271 | -1.8814 | -1.8402 | 120.4285 | 120.3827 | 120.2774 | 0.15564 | 0.050354 | 120.2179 | -1.7944 | -1.799 | 120.4697 | 120.4056 | 120.401 | 0.18768 | 0.18311 | 0.20142 | 0.082397 | 0.25177 | 0.13275 | 0.041198 | 0.13733 | 120.2682 | 120.3552 | -1.9226 | -1.9318 | 120.3094 | 120.3506 | 120.2042 | 120.369
6128.75 | 122.3053 | -120.3003 | 1.9089 | -0.21187 | -0.038544 | 0.0010958 | 0.0208 | 0.0055627 | -0.012452 | -0.0062185 | -0.12296 | 0.02411 | 0.013008 | -0.012119 | -0.020078 | 0.027835 | -0.0040845 | -0.14191 | 0.041199 | -0.07782 | -0.14191 | -0.059509 | -0.17853 | -0.050354 | -0.07782 | 0.10529 | -0.086975 | -0.032043 | 0.027466 | -0.032043 | 0.059509 | 120.2225 | -1.8677 | -2.0508 | 120.2408 | 120.2499 | 120.1218 | 0.027466 | -0.10071 | 120.2133 | -1.8036 | -1.9409 | 120.3278 | 120.3598 | 120.2682 | 0.14648 | 0.054932 | 0.018311 | -0.064087 | 0.11444 | 0.054932 | 0.11902 | 0.19226 | 120.3415 | 120.4056 | -1.9867 | -1.9959 | 120.1584 | 120.2682 | 120.1584 | 120.2225
6130.4531 | 122.4609 | -120.4559 | 1.6891 | -0.2195 | -0.038971 | -0.0036038 | 0.017169 | -0.0021277 | -0.011384 | -0.0066457 | -0.0069885 | 0.020905 | 0.01493 | -0.014896 | -0.018369 | 0.025699 | -0.00088011 | -0.068665 | -0.009155 | -0.045776 | 0.027466 | 0.17853 | 0.018311 | 0.10529 | 0.10071 | 0.07782 | -0.054932 | 0.068665 | 0.20599 | 0.14648 | 0.14648 | 120.4102 | -1.6983 | -1.6617 | 120.6345 | 120.5612 | 120.4742 | 0.15106 | 0.064087 | 120.401 | -1.6113 | -1.6205 | 120.6619 | 120.6024 | 120.6024 | 0.20142 | 0.20142 | 0.2243 | 0.073242 | 0.26093 | 0.1236 | 0.036621 | 0.13275 | 120.4468 | 120.5338 | -1.7349 | -1.7441 | 120.4834 | 120.5246 | 120.3873 | 120.5566
6132.1562 | 122.2824 | -120.4147 | 1.7807 | -0.15846 | -0.038971 | 0.0010958 | 0.021441 | 0.0053491 | -0.011384 | -0.0057913 | -0.10464 | 0.023682 | 0.016212 | -0.017032 | -0.018369 | 0.026767 | -0.0049389 | -0.11902 | 0.059509 | -0.07782 | -0.1236 | -0.041199 | -0.17853 | -0.041199 | -0.07782 | 0.10071 | -0.10071 | -0.032043 | 0.013733 | -0.036621 | 0.054932 | 120.3369 | -1.7212 | -1.9043 | 120.3735 | 120.3735 | 120.2362 | 0.036621 | -0.10071 | 120.314 | -1.68 | -1.8127 | 120.4285 | 120.4697 | 120.3781 | 0.15564 | 0.064087 | 0.036621 | -0.045776 | 0.11444 | 0.068665 | 0.13733 | 0.20142 | 120.4742 | 120.5154 | -1.8585 | -1.8814 | 120.2911 | 120.3827 | 120.2957 | 120.3369
6133.8906 | 122.3236 | -120.282 | 1.9363 | -0.24239 | -0.03833 | -0.00082677 | 0.019732 | -0.0010595 | -0.010102 | -0.0045095 | -0.1138 | 0.024964 | 0.014076 | -0.0074191 | -0.020933 | 0.02634 | -0.0053661 | -0.13733 | 0.054932 | -0.059509 | -0.11902 | -0.022888 | -0.15564 | -0.032043 | -0.059509 | 0.10071 | -0.086975 | -0.036621 | 0.018311 | -0.022888 | 0.059509 | 120.2225 | -1.8814 | -2.0554 | 120.2591 | 120.2499 | 120.1263 | 0.027466 | -0.096131 | 120.195 | -1.8356 | -1.973 | 120.3003 | 120.3415 | 120.2591 | 0.14648 | 0.064087 | 0.036621 | -0.05951 | 0.10529 | 0.050354 | 0.11444 | 0.18768 | 120.3369 | 120.3827 | -1.9958 | -2.0233 | 120.163 | 120.2454 | 120.1447 | 120.2225
6135.6406 | 122.3785 | -120.4971 | 1.6937 | -0.15083 | -0.043244 | -0.00039957 | 0.019305 | -0.0017005 | -0.011811 | -0.0042959 | -0.092438 | 0.023469 | 0.015571 | -0.0076327 | -0.021787 | 0.026767 | -0.0068615 | -0.12817 | 0.032043 | -0.07782 | -0.07782 | 0.013733 | -0.091553 | 0.004578 | -0.036621 | 0.10986 | -0.086975 | 0 | 0.09613 | 0.041199 | 0.086975 | 120.4193 | -1.6617 | -1.7715 | 120.5109 | 120.5017 | 120.4056 | 0.082398 | -0.013733 | 120.4102 | -1.5839 | -1.6937 | 120.5933 | 120.5841 | 120.5383 | 0.17395 | 0.12817 | 0.091553 | 0 | 0.1831 | 0.086975 | 0.10986 | 0.19684 | 120.5292 | 120.607 | -1.7715 | -1.7807 | 120.4193 | 120.4971 | 120.369 | 120.4605
6137.3906 | 122.3785 | -120.5017 | 1.7029 | -0.17372 | -0.038544 | -0.0018948 | 0.02016 | 0.00043587 | -0.014375 | -0.0032277 | -0.083283 | 0.022401 | 0.015998 | -0.011905 | -0.018583 | 0.026126 | -0.0025891 | -0.1236 | 0.073242 | -0.073242 | -0.10529 | 0 | -0.10071 | -0.004578 | -0.064087 | 0.10071 | -0.10071 | -0.032043 | 0.091553 | 0.022888 | 0.082397 | 120.4285 | -1.6296 | -1.8082 | 120.5017 | 120.4971 | 120.401 | 0.068664 | -0.027466 | 120.401 | -1.6022 | -1.7349 | 120.5933 | 120.5841 | 120.5246 | 0.18311 | 0.1236 | 0.073242 | -0.032044 | 0.19226 | 0.068665 | 0.14648 | 0.20142 | 120.575 | 120.6024 | -1.7761 | -1.8036 | 120.3964 | 120.4697 | 120.3781 | 120.4376
6139.0938 | 122.3877 | -98.2086 | 23.9227 | -0.17372 | -0.039185 | -0.0010404 | 0.016742 | -0.0027685 | -0.0098886 | -0.0045095 | 0.0021667 | 0.021119 | 0.015571 | -0.0134 | -0.020506 | 0.025272 | -0.0042981 | -0.10071 | 0.013733 | -0.050354 | -0.004578 | 0.10986 | -0.018311 | 0.10529 | 0.064087 | 0.07782 | -0.064087 | 0.064087 | 0.19226 | 0.14191 | 0.16937 | 98.1583 | -23.909 | -23.9273 | 98.3185 | 98.3139 | 98.1903 | 0.15564 | 0.032043 | 98.1445 | -23.8449 | -23.8586 | 98.4009 | 98.378 | 98.3505 | 0.23346 | 0.20599 | 0.16022 | 0.045776 | 0.25635 | 0.12817 | 0.064087 | 0.14191 | 98.2224 | 98.2864 | -23.9731 | -23.9868 | 98.204 | 98.2727 | 98.1079 | 98.2727
6140.7969 | 122.3877 | -120.5704 | 1.6022 | -0.21187 | -0.037476 | -0.00061317 | 0.020587 | 0.0021447 | -0.010743 | -0.0053641 | -0.11075 | 0.021119 | 0.015998 | -0.0080601 | -0.021574 | 0.026126 | -0.0025891 | -0.13733 | 0.041199 | -0.07782 | -0.10986 | -0.045776 | -0.17395 | -0.041199 | -0.07782 | 0.11444 | -0.091553 | -0.036621 | 0.013733 | -0.036621 | 0.064087 | 120.4926 | -1.561 | -1.712 | 120.5246 | 120.5292 | 120.3964 | 0.036621 | -0.09613 | 120.4788 | -1.4877 | -1.6388 | 120.5841 | 120.6345 | 120.5338 | 0.15564 | 0.054932 | 0.032044 | -0.032043 | 0.10529 | 0.054932 | 0.11902 | 0.20599 | 120.6116 | 120.6848 | -1.68 | -1.6937 | 120.4605 | 120.5338 | 120.433 | 120.4926
6142.5625 | 122.5113 | -120.5658 | 1.5701 | -0.19661 | -0.03833 | -0.00018577 | 0.018664 | 0.0027857 | -0.01117 | -0.0055777 | -0.080231 | 0.02176 | 0.015571 | -0.018741 | -0.019224 | 0.02869 | -0.0028027 | -0.082397 | 0.018311 | -0.059509 | -0.013733 | 0.10071 | -0.054932 | 0.064087 | 0.068665 | 0.086975 | -0.064087 | 0.07782 | 0.14648 | 0.091553 | 0.16937 | 120.5063 | -1.5518 | -1.5839 | 120.6665 | 120.6299 | 120.5109 | 0.1236 | 0.004577 | 120.5017 | -1.4832 | -1.4923 | 120.7123 | 120.7352 | 120.6573 | 0.23346 | 0.15564 | 0.16022 | 0.045776 | 0.21057 | 0.14191 | 0.07782 | 0.15106 | 120.5841 | 120.6528 | -1.6296 | -1.6342 | 120.5521 | 120.6436 | 120.4834 | 120.6345
6144.2656 | 122.4335 | -120.6162 | 1.5884 | -0.1432 | -0.039185 | -0.00061317 | 0.019946 | -0.0010595 | -0.010316 | -0.0040823 | -0.10159 | 0.025605 | 0.016212 | -0.011478 | -0.019438 | 0.025272 | -0.0032299 | -0.09613 | 0.041199 | -0.073242 | -0.050354 | 0.045776 | -0.082397 | 0.018311 | 0.013733 | 0.10071 | -0.07782 | 0.013733 | 0.10529 | 0.036621 | 0.091553 | 120.5429 | -1.5472 | -1.6388 | 120.6619 | 120.6345 | 120.5338 | 0.091553 | -0.009155 | 120.5383 | -1.4877 | -1.5747 | 120.7214 | 120.7077 | 120.6528 | 0.16937 | 0.11444 | 0.11902 | 0.022888 | 0.18311 | 0.091553 | 0.11444 | 0.17853 | 120.6573 | 120.7169 | -1.6617 | -1.6663 | 120.5658 | 120.6299 | 120.52 | 120.6299
6145.9844 | 122.4747 | -120.6024 | 1.5656 | -0.25002 | -0.038544 | -0.00082677 | 0.01781 | -0.00020513 | -0.01117 | -0.0049367 | -0.037506 | 0.022187 | 0.015998 | -0.01575 | -0.019865 | 0.024631 | 0.0018969 | -0.064087 | 0.004578 | -0.036621 | 0.018311 | 0.14191 | -0.018311 | 0.082397 | 0.082397 | 0.091553 | -0.054932 | 0.073242 | 0.15564 | 0.091553 | 0.14191 | 120.5658 | -1.561 | -1.5472 | 120.7443 | 120.6848 | 120.5841 | 0.11902 | 0.01831 | 120.5475 | -1.474 | -1.4923 | 120.7581 | 120.7443 | 120.694 | 0.19684 | 0.14649 | 0.17853 | 0.054932 | 0.21057 | 0.12817 | 0.041199 | 0.14649 | 120.607 | 120.694 | -1.6022 | -1.6205 | 120.6207 | 120.6757 | 120.5383 | 120.6848
6147.6875 | 121.7834 | -107.7026 | 13.9664 | -0.17372 | -0.037049 | 2.7834e-05 | 0.019946 | 0.0034265 | -0.0094614 | -0.0032277 | -0.12601 | 0.023469 | 0.013221 | -0.0069919 | -0.020078 | 0.026767 | -0.0015209 | -0.12817 | 0.036621 | -0.091553 | -0.10071 | -0.032043 | -0.15564 | -0.045776 | -0.10071 | 0.10986 | -0.10529 | -0.068665 | 0.013733 | -0.036621 | 0.054932 | 107.6111 | -13.9297 | -14.0671 | 107.6706 | 107.6569 | 107.547 | 0.045777 | -0.064087 | 107.5974 | -13.8565 | -14.035 | 107.7164 | 107.7576 | 107.666 | 0.16022 | 0.068665 | 0.05951 | -0.009155 | 0.11902 | 0.036621 | 0.12817 | 0.21515 | 107.7393 | 107.8125 | -14.0579 | -14.0717 | 107.6019 | 107.634 | 107.5745 | 107.6019
6149.375 | 122.0261 | -65.5151 | 56.1584 | -0.16609 | -0.041962 | -0.0010404 | 0.016528 | -0.00041873 | -0.012025 | -0.0055777 | -0.034454 | 0.023682 | 0.015785 | -0.011051 | -0.020078 | 0.023349 | -0.0032299 | -0.064087 | 0.009155 | -0.045776 | 0.004578 | 0.13733 | -0.009155 | 0.082397 | 0.050354 | 0.07782 | -0.045776 | 0.004578 | 0.1236 | 0.082397 | 0.10071 | 65.4694 | -56.1493 | -56.1539 | 65.6525 | 65.5975 | 65.506 | 0.12817 | 0.036621 | 65.4694 | -56.0806 | -56.1539 | 65.6387 | 65.6158 | 65.5975 | 0.14648 | 0.12817 | 0.18311 | 0.050354 | 0.16937 | 0.050354 | 0.054931 | 0.1236 | 65.5243 | 65.593 | -56.2042 | -56.2042 | 65.5197 | 65.5197 | 65.451 | 65.5655
6151.0938 | 121.7606 | -12.0712 | 109.8953 | -0.15846 | -0.038971 | -0.00018577 | 0.020587 | 0.00086307 | -0.012452 | -0.0055777 | -0.1077 | 0.024323 | 0.016426 | -0.011905 | -0.020933 | 0.026126 | -0.0030163 | -0.11902 | 0.054932 | -0.082397 | -0.10529 | -0.013733 | -0.14191 | -0.018311 | -0.068665 | 0.10529 | -0.086975 | -0.036621 | 0.036621 | -0.018311 | 0.064087 | 11.9888 | -109.8404 | -110.0006 | 12.0575 | 12.0529 | 11.9293 | 0.064086 | -0.05951 | 11.9843 | -109.79 | -109.9319 | 12.1078 | 12.1353 | 12.0529 | 0.15106 | 0.068664 | 0.068664 | -0.022889 | 0.1236 | 0.050354 | 0.13733 | 0.19226 | 12.1262 | 12.1765 | -109.9777 | -109.9823 | 11.9659 | 12.0346 | 11.9522 | 12.0026
6152.8125 | 122.1039 | -10.112 | 111.113 | -0.15083 | -0.040467 | 0.0010958 | 0.016528 | 0.0019311 | -0.011598 | -0.0070731 | -0.01004 | 0.021973 | 0.015571 | -0.021518 | -0.019438 | 0.024844 | -0.0015209 | -0.068665 | -0.004578 | -0.054932 | 0.045776 | 0.17853 | 0.032043 | 0.12817 | 0.10071 | 0.073242 | -0.004578 | 0.059509 | 0.20599 | 0.13275 | 0.14648 | 10.0571 | -111.1176 | -111.0672 | 10.2905 | 10.2402 | 10.144 | 0.18311 | 0.086975 | 10.1074 | -111.0397 | -111.0535 | 10.318 | 10.2585 | 10.2448 | 0.15106 | 0.13733 | 0.23346 | 0.10071 | 0.21057 | 0.064087 | 0.050354 | 0.07782 | 10.1074 | 10.1852 | -111.1679 | -111.1176 | 10.1578 | 10.1715 | 10.0433 | 10.2127
6154.5 | 108.0002 | -12.1902 | 95.6268 | -0.70015 | -0.050507 | -0.0044584 | 0.001788 | -0.0017005 | -0.015016 | -0.0083547 | -0.17178 | 0.019837 | 0.015785 | -0.013614 | -0.019438 | 0.027408 | -0.0015209 | -0.23346 | -0.1831 | -0.086975 | -0.18768 | 0.086975 | 0.082397 | 0.091553 | -0.21973 | 0.091553 | -0.09613 | -0.33417 | -0.10071 | -0.15106 | -0.050354 | 12.1033 | -95.8099 | -95.8145 | 12.2772 | 12.2818 | 12.2726 | 0.17853 | 0.16937 | 12.0941 | -95.5353 | -95.961 | 12.0895 | 12.1399 | 12.0392 | 0.045776 | -0.054932 | 0.17395 | -0.10071 | -0.004578 | -0.23804 | -0.09613 | 0.18768 | 12.0071 | 12.2818 | -95.7138 | -95.723 | 12.0026 | 11.8561 | 11.9568 | 11.9705
6156.2031 | 91.2827 | -13.2202 | 80.8228 | -0.69252 | -0.041321 | 0.00024143 | 0.012469 | -0.0036231 | -0.012239 | -0.0047231 | -0.083283 | 0.021546 | 0.011726 | -0.018527 | -0.016874 | 0.026553 | -0.0034435 | -0.52185 | 0.004578 | -0.086975 | -0.32501 | 0.09613 | 0.086975 | 0.10071 | -0.15564 | 0.091553 | -0.091553 | -0.15106 | 0.091553 | 0.091553 | 0.09613 | 13.1332 | -80.8182 | -81.1478 | 13.3163 | 13.3209 | 13.3072 | 0.18768 | 0.17395 | 13.1287 | -80.7312 | -80.9738 | 13.3118 | 13.3163 | 13.3118 | 0.18768 | 0.18311 | 0.1831 | -0.23804 | 0.18311 | -0.059509 | 0.091553 | 0.18311 | 13.2248 | 13.3118 | -80.9097 | -80.9143 | 12.8952 | 13.0692 | 12.6984 | 13.0646
6157.9062 | 121.7468 | -12.1857 | 109.584 | -0.28816 | -0.041535 | -0.001254 | 0.018237 | -0.0014867 | -0.011598 | -0.0045095 | 0.026581 | 0.021119 | 0.016212 | -0.013614 | -0.020078 | 0.025058 | 0.0014697 | -0.10071 | 0.018311 | 0.25177 | -0.045776 | 0 | -0.20599 | -0.13275 | 0.032043 | -0.25177 | 0.13733 | 0.027466 | 0.082397 | 0.018311 | 0.054932 | 12.4374 | -109.5657 | -109.6298 | 12.1857 | 12.0529 | 11.9797 | -0.38452 | -0.45776 | 12.323 | -109.8358 | -109.5566 | 12.2681 | 12.2406 | 12.204 | -0.082397 | -0.11902 | -0.25177 | -0.29755 | -0.054932 | -0.10986 | -0.23346 | -0.3891 | 12.204 | 11.9339 | -109.3323 | -109.4467 | 12.1399 | 12.2131 | 12.085 | 12.2177
6159.6094 | 122.3373 | -107.1671 | 14.653 | -0.21187 | -0.038971 | 0.0017368 | 0.017382 | -0.0027685 | -0.01352 | -0.0030141 | 0.041839 | 0.022614 | 0.015357 | -0.011051 | -0.019224 | 0.02399 | -0.0045117 | -0.09613 | 0 | 0.21515 | 0 | -0.041199 | -0.21057 | -0.14648 | 0.045776 | -0.16479 | 0.041199 | -0.009155 | -0.059509 | -0.1236 | -0.10986 | 107.3822 | -14.653 | -14.653 | 107.1259 | 107.0206 | 106.9565 | -0.36163 | -0.42572 | 107.2083 | -14.8178 | -14.6622 | 107.1075 | 107.0572 | 107.0435 | -0.15106 | -0.16479 | -0.25635 | -0.21515 | -0.10071 | -0.050354 | -0.21515 | -0.20599 | 107.1671 | 107.0023 | -14.4379 | -14.6118 | 107.1671 | 107.1579 | 107.0709 | 107.2128
6161.3281 | 122.3373 | -113.0447 | 8.8852 | -0.13557 | -0.040039 | -0.00082677 | 0.014605 | 0.046151 | -0.015656 | -0.015191 | -0.48611 | 0.037568 | 0.013648 | 0.026761 | 0.26105 | 0.041934 | 0.030736 | -0.11444 | 0.054932 | -0.068665 | -0.35706 | 0.09613 | 0.082397 | 0.091553 | 0.009155 | 0.004578 | 0.29755 | 0.004578 | 0.027466 | 0.09613 | 0.082397 | 112.9761 | -8.8303 | -9.2422 | 113.1409 | 113.1363 | 113.1271 | 0.16022 | 0.15106 | 113.3423 | -8.8806 | -8.8806 | 113.0722 | 113.1271 | 113.1409 | -0.21515 | -0.20142 | 0.16479 | -0.28839 | -0.27008 | -0.29297 | 0.1236 | -0.29297 | 113.0997 | 113.0493 | -8.9539 | -8.5876 | 112.6877 | 113.0493 | 112.9303 | 113.0539
6163.0312 | 122.3557 | -105.954 | 15.889 | -0.089798 | -0.042389 | 0.0013094 | 0.018664 | -0.0046911 | -0.013734 | -0.0023733 | 0.050995 | 0.021973 | 0.013008 | -0.015964 | -0.019651 | 0.025699 | -0.0066479 | -0.068665 | 0.013733 | -0.050354 | 0.013733 | 0.17395 | 0.027466 | 0.059509 | 0.13275 | 0.086975 | -0.054932 | 0.07782 | 0.17395 | 0.13733 | 0.16479 | 105.9036 | -15.8752 | -15.8752 | 106.1279 | 106.0135 | 105.9814 | 0.10986 | 0.07782 | 105.899 | -15.802 | -15.8112 | 106.1279 | 106.1188 | 106.0913 | 0.21973 | 0.19226 | 0.2243 | 0.064087 | 0.22888 | 0.13275 | 0.064087 | 0.14191 | 105.9677 | 106.041 | -15.9393 | -15.9439 | 105.9677 | 106.0318 | 105.8853 | 106.0867
6164.7656 | 122.2824 | -121.0556 | 0.94757 | -0.16609 | -0.039612 | 0.0019504 | 0.020587 | -0.0036231 | -0.010102 | -0.0047231 | -0.17789 | 0.020692 | 0.01493 | -0.0134 | -0.019438 | 0.025058 | -0.0030163 | -0.14191 | 0.050354 | -0.082397 | -0.11444 | -0.1831 | -0.41657 | -0.30212 | -0.045776 | 0.10529 | -0.082397 | -0.009155 | 0.013733 | -0.16937 | -0.21515 | 120.9732 | -0.89722 | -1.062 | 120.8725 | 120.7535 | 120.639 | -0.21973 | -0.33417 | 120.9732 | -0.84229 | -0.95673 | 121.0693 | 120.8405 | 120.8862 | -0.13275 | -0.086976 | -0.10071 | -0.032044 | 0.09613 | 0.073242 | 0.13275 | 0.18768 | 121.106 | 121.1609 | -1.03 | -1.03 | 120.9412 | 121.0464 | 120.9137 | 121.0098
6166.5312 | 122.2504 | -115.8966 | 6.0974 | -0.20424 | -0.039185 | -0.00082677 | 0.017382 | -0.00020513 | -0.013093 | -0.0064321 | 0.020477 | 0.021973 | 0.014503 | -0.015964 | -0.018797 | 0.025485 | 0.00018809 | -0.10071 | 0.013733 | -0.045776 | -0.050354 | 0.086975 | -0.073242 | 0.041199 | 0.027466 | 0.07782 | -0.041199 | 0.032043 | 0.09613 | 0.059509 | 0.10529 | 115.8508 | -6.0837 | -6.1478 | 115.9836 | 115.9378 | 115.8234 | 0.086975 | -0.027466 | 115.8554 | -6.0196 | -6.0654 | 115.9927 | 116.0019 | 115.9561 | 0.14649 | 0.10071 | 0.13275 | -0.004578 | 0.13733 | 0.073242 | 0.059509 | 0.11902 | 115.9103 | 115.9744 | -6.1432 | -6.1386 | 115.8463 | 115.9286 | 115.7959 | 115.9241
6168.2344 | 122.1954 | -112.4634 | 9.4894 | -0.18135 | -0.038758 | -0.00018577 | 0.019946 | -0.013663 | -0.016084 | -0.010064 | -0.48917 | 0.037995 | 0.008735 | -0.014255 | -0.030973 | 0.036594 | -0.014979 | -0.073242 | 0.054932 | -0.064087 | -0.036621 | -0.07782 | -0.39368 | -0.050354 | 0.027466 | 0.10986 | -0.068665 | 0.022888 | 0.091553 | -0.15106 | -0.073242 | 112.3993 | -9.4345 | -9.5261 | 112.3856 | 112.413 | 112.0697 | 0.013733 | -0.32959 | 112.3947 | -9.3796 | -9.4666 | 112.5549 | 112.3901 | 112.3123 | -0.004577 | -0.082397 | -0.013733 | 0.027466 | 0.16022 | 0.091553 | 0.11902 | 0.17853 | 112.5183 | 112.5732 | -9.5535 | -9.5581 | 112.4268 | 112.4863 | 112.3901 | 112.4908
6169.9375 | 122.3419 | -121.1243 | 0.88348 | -0.15083 | -0.040467 | -0.001254 | 0.018451 | 0.00022207 | -0.012666 | -0.0036551 | 0.020477 | 0.022187 | 0.014289 | -0.0095553 | -0.019438 | 0.025272 | -0.0053661 | -0.07782 | 0.004578 | -0.050354 | 0.018311 | 0.15106 | 0.018311 | 0.10986 | 0.10071 | 0.082397 | -0.050354 | 0.068665 | 0.16937 | 0.11902 | 0.16022 | 121.0739 | -0.87891 | -0.86517 | 121.2753 | 121.2341 | 121.1426 | 0.16022 | 0.068665 | 121.0739 | -0.80109 | -0.81482 | 121.2936 | 121.2845 | 121.2433 | 0.21057 | 0.16937 | 0.20142 | 0.068665 | 0.21973 | 0.11902 | 0.054932 | 0.13275 | 121.1288 | 121.2067 | -0.93384 | -0.93384 | 121.1426 | 121.1929 | 121.0464 | 121.225
6171.6562 | 122.2183 | -121.1838 | 0.90637 | -0.12032 | -0.041962 | -0.001254 | 0.020587 | -0.0023413 | -0.013307 | -0.0040823 | -0.025299 | 0.023041 | 0.014717 | -0.01041 | -0.019224 | 0.025058 | -0.0057935 | -0.13733 | 0.045776 | -0.09613 | -0.09613 | -0.004578 | -0.11902 | -0.11902 | -0.068665 | 0.10986 | -0.07782 | -0.059509 | 0.036621 | -0.018311 | -0.022888 | 121.0876 | -0.8606 | -1.0025 | 121.1792 | 121.0648 | 121.0648 | -0.022889 | -0.022889 | 121.106 | -0.79651 | -0.96588 | 121.2204 | 121.1609 | 121.1655 | 0.054932 | 0.059509 | 0.091552 | 0 | 0.11444 | 0.018311 | 0.14191 | 0.18768 | 121.2296 | 121.2936 | -1.0025 | -0.98419 | 121.0876 | 121.1243 | 121.0464 | 121.1151
6173.3438 | 122.3236 | -121.1792 | 0.85602 | -0.2195 | -0.040039 | 0.0013094 | 0.018451 | -0.00084593 | -0.012239 | -0.0062185 | -0.0069885 | 0.02411 | 0.013435 | -0.022373 | -0.019224 | 0.027408 | -0.0028027 | -0.068665 | 0.009155 | -0.050354 | 0.004578 | 0.14191 | -0.018311 | 0.082397 | 0.086975 | 0.068665 | -0.045776 | 0.068665 | 0.14648 | 0.091553 | 0.13275 | 121.1288 | -0.84686 | -0.85144 | 121.3211 | 121.2616 | 121.1609 | 0.13275 | 0.032043 | 121.1334 | -0.78735 | -0.78735 | 121.3257 | 121.3119 | 121.2708 | 0.17853 | 0.13733 | 0.19226 | 0.054932 | 0.19226 | 0.11444 | 0.059509 | 0.11444 | 121.1884 | 121.2479 | -0.90637 | -0.90179 | 121.1838 | 121.2479 | 121.1105 | 121.2662
6175.0625 | 122.3236 | -121.1929 | 0.8606 | -0.16609 | -0.037689 | 0.0010958 | 0.020373 | 8.47e-06 | -0.010957 | -0.0066457 | -0.01004 | 0.022828 | 0.015144 | -0.018527 | -0.020078 | 0.027194 | -0.0034435 | -0.07782 | 0 | -0.054932 | -0.004578 | 0.12817 | -0.045776 | 0.082397 | 0.073242 | 0.082397 | -0.036621 | 0.045776 | 0.11902 | 0.068665 | 0.11444 | 121.138 | -0.8606 | -0.86517 | 121.3211 | 121.2753 | 121.1472 | 0.13733 | 0.009156 | 121.1563 | -0.7782 | -0.81482 | 121.312 | 121.3074 | 121.2616 | 0.15106 | 0.10529 | 0.18311 | 0.050354 | 0.15564 | 0.082397 | 0.054932 | 0.11902 | 121.1929 | 121.2753 | -0.91553 | -0.89722 | 121.1884 | 121.2387 | 121.1151 | 121.2662
6176.7656 | 122.3053 | -121.1884 | 0.86975 | -0.19661 | -0.039398 | -0.0010404 | 0.021228 | 0.00022207 | -0.012452 | -0.0055777 | -0.14432 | 0.023469 | 0.012153 | -0.0076327 | -0.020292 | 0.026767 | -0.0028027 | -0.12817 | 0.036621 | -0.091553 | -0.09613 | -0.004578 | -0.14191 | -0.050354 | -0.009155 | 0.10071 | -0.073242 | 0.018311 | 0.068665 | 0.018311 | 0.086975 | 121.0968 | -0.83313 | -0.96588 | 121.1838 | 121.138 | 121.0464 | 0.041199 | -0.050354 | 121.1151 | -0.76904 | -0.85144 | 121.257 | 121.2753 | 121.2067 | 0.16022 | 0.091553 | 0.086975 | -0.004577 | 0.14191 | 0.091553 | 0.12817 | 0.17395 | 121.225 | 121.2891 | -0.9613 | -0.94299 | 121.0922 | 121.2067 | 121.0602 | 121.1792
6178.4688 | 122.2549 | -121.1975 | 0.91095 | -0.074539 | -0.039826 | -0.0023222 | 0.018878 | -0.0025549 | -0.011598 | -0.0042959 | -0.052765 | 0.024537 | 0.015571 | -0.02045 | -0.019224 | 0.026553 | -0.0049389 | -0.16479 | 0.045776 | -0.091553 | -0.10529 | -0.018311 | -0.11902 | -0.009155 | -0.082397 | 0.12817 | -0.091553 | -0.059509 | 0.027466 | -0.013733 | 0.045776 | 121.106 | -0.86517 | -1.0162 | 121.1792 | 121.1884 | 121.0785 | 0.082398 | -0.027466 | 121.106 | -0.78278 | -0.97046 | 121.225 | 121.2433 | 121.1838 | 0.13733 | 0.07782 | 0.073242 | -0.013733 | 0.11902 | 0.032044 | 0.13733 | 0.21973 | 121.2433 | 121.3257 | -1.0025 | -1.0025 | 121.0922 | 121.138 | 121.0327 | 121.1151
6180.1719 | 122.3602 | -121.1975 | 0.89264 | -0.18898 | -0.039398 | -0.0014676 | 0.017596 | 0.00043587 | -0.010743 | -0.0047231 | 0.0082703 | 0.022187 | 0.014289 | -0.018314 | -0.019224 | 0.024417 | -2.571e-05 | -0.10986 | -0.004578 | -0.059509 | -0.036621 | 0.064087 | -0.050354 | 0.064087 | 0.018311 | 0.082397 | -0.054932 | 0.045776 | 0.14191 | 0.091553 | 0.11902 | 121.138 | -0.89722 | -0.92926 | 121.2616 | 121.2616 | 121.1472 | 0.1236 | 0.009155 | 121.1426 | -0.81024 | -0.84686 | 121.3394 | 121.3165 | 121.2891 | 0.17395 | 0.14649 | 0.1236 | 0.022888 | 0.19684 | 0.10071 | 0.054931 | 0.13733 | 121.1929 | 121.2799 | -0.95215 | -0.94757 | 121.1609 | 121.2433 | 121.0876 | 121.2158
6181.8906 | 122.3785 | -121.1746 | 0.86975 | -0.2195 | -0.041962 | -0.0027494 | 0.016955 | 0.0021447 | -0.013947 | -0.0060049 | 0.0021667 | 0.022614 | 0.012153 | -0.011051 | -0.019438 | 0.027835 | -0.0047253 | -0.11444 | 0.027466 | -0.054932 | -0.009155 | 0.091553 | -0.018311 | 0.086975 | 0.045776 | 0.082397 | -0.045776 | 0.086975 | 0.17395 | 0.11902 | 0.16022 | 121.1197 | -0.84229 | -0.87891 | 121.2662 | 121.2616 | 121.1563 | 0.14191 | 0.036621 | 121.1288 | -0.78735 | -0.78278 | 121.3486 | 121.3348 | 121.2936 | 0.20599 | 0.16479 | 0.14649 | 0.045777 | 0.21973 | 0.13275 | 0.082398 | 0.12817 | 121.2021 | 121.257 | -0.92468 | -0.91553 | 121.1655 | 121.2616 | 121.0602 | 121.2204
6183.6406 | 122.3328 | -121.2067 | 0.86975 | -0.20424 | -0.039398 | 2.7834e-05 | 0.020373 | 0.0044947 | -0.01117 | -0.0055777 | -0.13211 | 0.021973 | 0.015571 | -0.011692 | -0.019438 | 0.027835 | -0.0040845 | -0.11902 | 0.045776 | -0.086975 | -0.059509 | 0.013733 | -0.14191 | 0.004578 | -0.009155 | 0.09613 | -0.068665 | 0.045776 | 0.09613 | 0.027466 | 0.10986 | 121.1197 | -0.82398 | -0.92926 | 121.2204 | 121.2112 | 121.0648 | 0.091553 | -0.054932 | 121.138 | -0.77362 | -0.82398 | 121.3028 | 121.3165 | 121.2341 | 0.17853 | 0.096131 | 0.10071 | 0.027466 | 0.16479 | 0.11444 | 0.13275 | 0.16479 | 121.2524 | 121.3028 | -0.95673 | -0.93842 | 121.1472 | 121.2524 | 121.0876 | 121.1975
6185.3906 | 122.2961 | -121.2479 | 0.87891 | -0.18135 | -0.040253 | -0.0078764 | 0.020587 | -0.0078955 | -0.02292 | -0.012627 | -0.15652 | 0.017701 | 0.00254 | -0.011905 | -0.020933 | 0.0081818 | -0.0079297 | -0.07782 | 0.041199 | -0.07782 | -0.027466 | 0.068665 | -0.086975 | 0.032043 | 0.027466 | 0.10986 | -0.059509 | 0.013733 | 0.09613 | 0.027466 | 0.082397 | 121.17 | -0.83771 | -0.90637 | 121.3165 | 121.2799 | 121.1609 | 0.10986 | -0.009155 | 121.1884 | -0.76904 | -0.86517 | 121.344 | 121.3303 | 121.2753 | 0.14191 | 0.086975 | 0.14649 | 0.050354 | 0.15564 | 0.073242 | 0.11902 | 0.16937 | 121.2891 | 121.3577 | -0.95673 | -0.93841 | 121.2204 | 121.2616 | 121.17 | 121.2753
6187.0938 | 122.3785 | -121.225 | 0.86975 | -0.15846 | -0.041962 | -0.00018577 | 0.017169 | -0.0025549 | -0.012452 | -0.0062185 | -0.028351 | 0.020692 | 0.014289 | -0.011478 | -0.020506 | 0.026553 | -0.0070751 | -0.07782 | 0.004578 | -0.064087 | 0.027466 | 0.17395 | 0.009155 | 0.10529 | 0.10071 | 0.064087 | -0.054932 | 0.073242 | 0.19684 | 0.13733 | 0.14648 | 121.1609 | -0.86517 | -0.84229 | 121.3989 | 121.3303 | 121.2341 | 0.16937 | 0.073242 | 121.17 | -0.80566 | -0.79651 | 121.4218 | 121.3715 | 121.3623 | 0.20142 | 0.19226 | 0.23804 | 0.091553 | 0.25177 | 0.12817 | 0.068665 | 0.11902 | 121.2296 | 121.2891 | -0.93384 | -0.92468 | 121.2524 | 121.2982 | 121.1472 | 121.3257
6188.7969 | 122.3785 | -121.225 | 0.86517 | -0.17372 | -0.040467 | 0.0010958 | 0.019732 | 0.0015039 | -0.013307 | -0.0042959 | -0.092438 | 0.022828 | 0.016212 | -0.013614 | -0.019651 | 0.027835 | -0.0042981 | -0.086975 | 0.022888 | -0.064087 | 0.013733 | 0.10986 | -0.054932 | 0.059509 | 0.082397 | 0.07782 | -0.059509 | 0.07782 | 0.16022 | 0.09613 | 0.16479 | 121.1609 | -0.84228 | -0.85144 | 121.3348 | 121.2845 | 121.17 | 0.1236 | 0.009155 | 121.1655 | -0.78735 | -0.78735 | 121.3852 | 121.3898 | 121.3211 | 0.2243 | 0.15564 | 0.17395 | 0.07782 | 0.21973 | 0.13733 | 0.086975 | 0.13733 | 121.2479 | 121.3028 | -0.92926 | -0.92468 | 121.2387 | 121.3028 | 121.138 | 121.3074
6190.5625 | 122.3419 | -121.2341 | 0.87891 | -0.17372 | -0.040253 | -0.0016812 | 0.018237 | -0.00084593 | -0.014375 | -0.0075003 | -0.022247 | 0.021332 | 0.014076 | -0.013187 | -0.022215 | 0.024204 | -0.0017347 | -0.11444 | 0.009155 | -0.041199 | -0.027466 | 0.09613 | -0.054932 | 0.045776 | 0.013733 | 0.073242 | -0.064087 | 0.036621 | 0.1236 | 0.068665 | 0.10529 | 121.1929 | -0.86975 | -0.90637 | 121.3303 | 121.2799 | 121.1792 | 0.086975 | -0.013733 | 121.17 | -0.80566 | -0.84228 | 121.3577 | 121.3394 | 121.3028 | 0.16937 | 0.13275 | 0.13733 | 0.013733 | 0.18768 | 0.10071 | 0.050354 | 0.13733 | 121.2433 | 121.3074 | -0.9201 | -0.94299 | 121.2067 | 121.2708 | 121.1197 | 121.2479
6192.2656 | 122.2504 | -121.2479 | 0.89722 | -0.2195 | -0.044739 | -0.010013 | 0.019091 | -0.0089637 | -0.019715 | -0.010491 | -0.33658 | 0.0080877 | 0.010444 | -0.014255 | -0.01901 | 0.020145 | 0.00040169 | -0.11902 | 0.050354 | -0.073242 | -0.091553 | -0.036621 | -0.16479 | -0.036621 | -0.082397 | 0.12817 | -0.07782 | -0.045776 | 0.013733 | -0.054932 | 0.041199 | 121.1746 | -0.84686 | -0.98877 | 121.2112 | 121.2112 | 121.0831 | 0.036621 | -0.091553 | 121.17 | -0.76904 | -0.94299 | 121.2616 | 121.2891 | 121.1929 | 0.11902 | 0.022888 | 0.036621 | -0.018311 | 0.091553 | 0.032044 | 0.1236 | 0.20599 | 121.2982 | 121.376 | -0.97046 | -0.97504 | 121.1563 | 121.2021 | 121.1288 | 121.1655
6193.9844 | 122.3785 | -121.2204 | 0.85602 | -0.15846 | -0.03833 | -0.001254 | 0.019519 | 0.0059901 | -0.009675 | -0.0047231 | -0.09549 | 0.021546 | 0.01493 | -0.015109 | -0.020506 | 0.027835 | -0.0015209 | -0.10071 | 0.036621 | -0.064087 | -0.027466 | 0.068665 | -0.09613 | 0.036621 | 0.073242 | 0.082397 | -0.054932 | 0.059509 | 0.14648 | 0.091553 | 0.15106 | 121.1563 | -0.8194 | -0.88348 | 121.2891 | 121.257 | 121.1243 | 0.10071 | -0.032043 | 121.1655 | -0.77362 | -0.79651 | 121.3669 | 121.3715 | 121.312 | 0.20599 | 0.14649 | 0.13275 | 0.036621 | 0.20142 | 0.11444 | 0.10071 | 0.13733 | 121.257 | 121.3028 | -0.9201 | -0.91095 | 121.1929 | 121.2799 | 121.1197 | 121.2936
6195.6875 | 122.319 | -121.2662 | 0.88806 | -0.17372 | -0.042176 | 0.00066863 | 0.019732 | 0.0040675 | -0.01053 | -0.0045095 | -0.19009 | 0.01471 | 0.015144 | -0.011692 | -0.021787 | 0.024631 | -0.0015209 | -0.09613 | 0.045776 | -0.082397 | -0.045776 | 0.045776 | -0.07782 | 0.018311 | 0.013733 | 0.09613 | -0.07782 | 0 | 0.10529 | 0.041199 | 0.10071 | 121.1838 | -0.84229 | -0.93384 | 121.312 | 121.2845 | 121.1884 | 0.10071 | 0.004577 | 121.1884 | -0.79193 | -0.88806 | 121.3715 | 121.3669 | 121.3074 | 0.17853 | 0.11902 | 0.12817 | 0.036621 | 0.18311 | 0.07782 | 0.12817 | 0.17395 | 121.312 | 121.3623 | -0.97046 | -0.96588 | 121.2204 | 121.2662 | 121.17 | 121.2799
6197.4219 | 122.3969 | -121.2662 | 0.8606 | -0.15846 | -0.041107 | -0.001254 | 0.014819 | -0.0021277 | -0.012239 | -0.0030141 | 0.011322 | 0.022401 | 0.014503 | -0.019168 | -0.01666 | 0.025272 | -0.0049389 | -0.068665 | 0.018311 | -0.045776 | 0.027466 | 0.16022 | 0.022888 | 0.10986 | 0.10986 | 0.086975 | -0.059509 | 0.064087 | 0.20599 | 0.13733 | 0.15106 | 121.2204 | -0.84229 | -0.83313 | 121.4264 | 121.376 | 121.2891 | 0.15564 | 0.068664 | 121.2067 | -0.77362 | -0.79651 | 121.4722 | 121.4172 | 121.4035 | 0.21057 | 0.19684 | 0.20599 | 0.073242 | 0.2655 | 0.1236 | 0.064087 | 0.14648 | 121.2845 | 121.3531 | -0.90637 | -0.92011 | 121.2936 | 121.3303 | 121.1975 | 121.376
6199.1406 | 122.2824 | -121.2067 | 0.94757 | -0.16609 | -0.045166 | -0.012149 | 0.021869 | -0.0072547 | -0.02292 | -0.017113 | -0.24808 | 0.0097967 | 0.0083078 | -0.014255 | -0.017301 | 0.017581 | -0.0023755 | -0.082397 | 0.059509 | -0.059509 | -0.050354 | 0.041199 | -0.10529 | 0.004578 | -0.009155 | 0.11902 | -0.068665 | -0.013733 | 0.059509 | -0.004578 | 0.059509 | 121.1472 | -0.88806 | -0.99793 | 121.2479 | 121.2112 | 121.1014 | 0.064087 | -0.045777 | 121.138 | -0.82855 | -0.9613 | 121.2662 | 121.2662 | 121.2021 | 0.12817 | 0.064087 | 0.10071 | 0.009155 | 0.12817 | 0.054932 | 0.11902 | 0.18768 | 121.2662 | 121.3257 | -1.0071 | -1.0162 | 121.1563 | 121.1929 | 121.1243 | 121.1975
6200.8438 | 122.2778 | -121.2708 | 0.92926 | -0.1432 | -0.044312 | 0.00045503 | 0.02016 | -0.0027685 | -0.012879 | -0.0036551 | -0.064972 | 0.022614 | 0.012794 | -0.0097689 | -0.019438 | 0.02399 | -0.0025891 | -0.13733 | 0.036621 | -0.10529 | -0.10986 | -0.013733 | -0.1236 | -0.013733 | -0.068665 | 0.1236 | -0.091553 | -0.07782 | 0.045776 | -0.018311 | 0.059509 | 121.1655 | -0.89264 | -1.0391 | 121.257 | 121.257 | 121.1472 | 0.091553 | -0.01831 | 121.1792 | -0.80566 | -1.0071 | 121.3165 | 121.3303 | 121.2524 | 0.15106 | 0.073242 | 0.091553 | -0.004577 | 0.13733 | 0.013733 | 0.14191 | 0.21515 | 121.3074 | 121.3943 | -1.0345 | -1.0208 | 121.1609 | 121.1929 | 121.1334 | 121.2021
6202.5469 | 122.2916 | -121.2708 | 0.9201 | -0.15083 | -0.04068 | -0.0040312 | 0.019946 | -0.0021277 | -0.014375 | -0.0047231 | -0.040558 | 0.023041 | 0.015998 | -0.012973 | -0.018583 | 0.025699 | -0.0013073 | -0.16479 | 0.041199 | -0.086975 | -0.082397 | 0.004578 | -0.10071 | 0 | -0.064087 | 0.11902 | -0.086975 | -0.068665 | 0.041199 | 0.004578 | 0.041199 | 121.1838 | -0.87891 | -1.0025 | 121.2753 | 121.2708 | 121.17 | 0.086975 | -0.013733 | 121.1838 | -0.80109 | -0.98877 | 121.312 | 121.312 | 121.2753 | 0.12817 | 0.091553 | 0.091553 | 0.004578 | 0.12817 | 0.01831 | 0.12817 | 0.20599 | 121.312 | 121.3898 | -1.0071 | -1.0071 | 121.1884 | 121.2021 | 121.106 | 121.2067
6204.2812 | 122.2504 | -121.2662 | 0.9201 | -0.18898 | -0.041321 | -0.0095854 | 0.019519 | 0.0038537 | -0.019074 | -0.0030141 | -0.10159 | 0.023682 | 0.015357 | -0.011264 | -0.020719 | 0.027194 | 0.0014697 | -0.12817 | 0.059509 | -0.07782 | -0.10986 | -0.045776 | -0.16022 | -0.050354 | -0.09613 | 0.1236 | -0.082397 | -0.050354 | 0.027466 | -0.032043 | 0.054932 | 121.1884 | -0.8606 | -1.03 | 121.2204 | 121.2158 | 121.106 | 0.027466 | -0.082397 | 121.1838 | -0.79651 | -0.97046 | 121.2936 | 121.3211 | 121.2341 | 0.13733 | 0.050354 | 0.032044 | -0.032043 | 0.10986 | 0.032043 | 0.13733 | 0.20599 | 121.3257 | 121.3898 | -0.99792 | -1.0025 | 121.1563 | 121.2158 | 121.138 | 121.17
6206.0156 | 122.2961 | -121.2524 | 0.92926 | -0.13557 | -0.041748 | -0.00039957 | 0.017169 | -0.0023413 | -0.013093 | -0.0025869 | -0.055817 | 0.025391 | 0.015144 | -0.013187 | -0.018156 | 0.023776 | -0.0023755 | -0.16479 | 0.054932 | -0.082397 | -0.10986 | -0.018311 | -0.10986 | -0.009155 | -0.082397 | 0.11902 | -0.09613 | -0.054932 | 0.050354 | 0.009155 | 0.064087 | 121.17 | -0.87433 | -1.0391 | 121.2341 | 121.2433 | 121.1426 | 0.073242 | -0.027466 | 121.1563 | -0.81024 | -0.98419 | 121.3028 | 121.3165 | 121.2616 | 0.16022 | 0.10528 | 0.064086 | -0.027466 | 0.14648 | 0.041198 | 0.13733 | 0.21515 | 121.3074 | 121.3715 | -1.0117 | -1.0254 | 121.1426 | 121.1975 | 121.0876 | 121.17
6207.7188 | 122.4014 | -121.225 | 0.89264 | -0.1432 | -0.041535 | -0.00061317 | 0.016528 | -0.00041873 | -0.012452 | -0.0040823 | -0.01004 | 0.023255 | 0.014717 | -0.020877 | -0.020719 | 0.022495 | -0.0017347 | -0.09613 | 0.022888 | -0.054932 | 0.004578 | 0.12817 | 0 | 0.11902 | 0.10071 | 0.07782 | -0.059509 | 0.07782 | 0.20142 | 0.15564 | 0.16937 | 121.17 | -0.86975 | -0.88806 | 121.3531 | 121.344 | 121.225 | 0.17395 | 0.054932 | 121.1655 | -0.81482 | -0.81482 | 121.4264 | 121.3943 | 121.3806 | 0.22888 | 0.21515 | 0.18311 | 0.05951 | 0.26093 | 0.13733 | 0.07782 | 0.13733 | 121.2479 | 121.3028 | -0.94757 | -0.95215 | 121.2296 | 121.3028 | 121.1288 | 121.3257
6209.4219 | 122.2824 | -121.2708 | 0.93842 | -0.12794 | -0.039185 | -0.00018577 | 0.022296 | -0.0034095 | -0.014161 | -0.0075003 | -0.12906 | 0.023041 | 0.015357 | -0.013828 | -0.020078 | 0.026553 | -0.0021619 | -0.10986 | 0.050354 | -0.082397 | -0.086975 | 0 | -0.15106 | -0.036621 | -0.054932 | 0.1236 | -0.073242 | -0.045776 | 0.022888 | -0.036621 | 0.054932 | 121.1884 | -0.88806 | -1.0254 | 121.2708 | 121.2341 | 121.1197 | 0.045776 | -0.068665 | 121.1975 | -0.81482 | -0.98419 | 121.2936 | 121.3257 | 121.2341 | 0.12817 | 0.036621 | 0.082397 | -0.004578 | 0.09613 | 0.027466 | 0.13275 | 0.19684 | 121.3211 | 121.3943 | -1.0208 | -1.0117 | 121.1838 | 121.225 | 121.1609 | 121.2158
6211.1562 | 122.3923 | -121.2662 | 0.87891 | -0.18135 | -0.04068 | 0.0023776 | 0.017169 | 0.00064947 | -0.011598 | -0.0047231 | -0.049713 | 0.021546 | 0.016212 | -0.018955 | -0.019438 | 0.024844 | -0.00045291 | -0.07782 | 0.004578 | -0.022888 | 0.013733 | 0.13733 | -0.045776 | 0.086975 | 0.073242 | 0.07782 | -0.073242 | 0.041199 | 0.13275 | 0.082397 | 0.12817 | 121.2433 | -0.87433 | -0.86517 | 121.4035 | 121.3531 | 121.2204 | 0.10986 | -0.022888 | 121.1929 | -0.80109 | -0.83771 | 121.3989 | 121.3943 | 121.3486 | 0.20142 | 0.15564 | 0.16022 | 0.036621 | 0.20599 | 0.11444 | 0.027466 | 0.15106 | 121.2708 | 121.344 | -0.90179 | -0.95215 | 121.2799 | 121.3074 | 121.1884 | 121.3394
6212.8594 | 122.3465 | -121.2753 | 0.90179 | -0.1432 | -0.039185 | 0.00024143 | 0.019946 | 0.0023585 | -0.014161 | -0.0034415 | -0.089386 | 0.023041 | 0.016853 | -0.014041 | -0.019865 | 0.025912 | -0.00045291 | -0.12817 | 0.054932 | -0.07782 | -0.054932 | 0.013733 | -0.091553 | 0.009155 | -0.022888 | 0.1236 | -0.09613 | -0.018311 | 0.10071 | 0.036621 | 0.091553 | 121.1975 | -0.84686 | -0.95673 | 121.2891 | 121.2845 | 121.1838 | 0.086975 | -0.013733 | 121.1792 | -0.7782 | -0.9201 | 121.376 | 121.3669 | 121.312 | 0.18768 | 0.13275 | 0.091553 | 0.022888 | 0.19684 | 0.077819 | 0.13275 | 0.21973 | 121.3303 | 121.3989 | -0.97961 | -0.99792 | 121.2204 | 121.257 | 121.1472 | 121.2524
6214.6094 | 122.3099 | -121.2753 | 0.89722 | -0.15083 | -0.038971 | -0.0089444 | 0.021014 | -0.00041873 | -0.017579 | -0.010705 | -0.1199 | 0.02411 | 0.01258 | -0.010623 | -0.01901 | 0.02634 | -2.571e-05 | -0.10529 | 0.045776 | -0.073242 | -0.064087 | 0.022888 | -0.14648 | -0.013733 | -0.041199 | 0.10529 | -0.073242 | -0.045776 | 0.036621 | -0.032043 | 0.054932 | 121.2021 | -0.85144 | -0.9613 | 121.2982 | 121.2616 | 121.1288 | 0.059509 | -0.073242 | 121.2021 | -0.79193 | -0.94299 | 121.312 | 121.3303 | 121.2433 | 0.12817 | 0.041199 | 0.09613 | 0.009155 | 0.10986 | 0.027466 | 0.11902 | 0.17853 | 121.3211 | 121.3806 | -0.97046 | -0.97046 | 121.2112 | 121.2296 | 121.17 | 121.2341
6216.3125 | 122.3969 | -121.225 | 0.90179 | -0.25002 | -0.040894 | -0.0018948 | 0.015674 | -0.0014867 | -0.009675 | -0.0064321 | -0.0039367 | 0.022614 | 0.014289 | -0.014682 | -0.018156 | 0.023563 | -0.0045117 | -0.1236 | 0.009155 | -0.041199 | -0.045776 | 0.068665 | -0.068665 | 0.054932 | -0.004578 | 0.082397 | -0.064087 | 0.018311 | 0.13275 | 0.082397 | 0.11902 | 121.1838 | -0.89264 | -0.94757 | 121.2936 | 121.2799 | 121.1563 | 0.096131 | -0.027466 | 121.1609 | -0.8194 | -0.88348 | 121.3577 | 121.344 | 121.3074 | 0.18311 | 0.14648 | 0.10986 | -0.004577 | 0.19684 | 0.082398 | 0.050354 | 0.14648 | 121.2341 | 121.3074 | -0.94299 | -0.96588 | 121.1792 | 121.2433 | 121.1014 | 121.2204
6218.0469 | 122.3236 | -121.2753 | 0.91095 | -0.17372 | -0.038544 | -0.00018577 | 0.021014 | -0.0023413 | -0.010316 | -0.0057913 | -0.11685 | 0.024323 | 0.01493 | -0.0076327 | -0.021574 | 0.026553 | -0.0030163 | -0.1236 | 0.050354 | -0.073242 | -0.10986 | -0.022888 | -0.15106 | -0.027466 | -0.054932 | 0.10986 | -0.07782 | -0.022888 | 0.036621 | -0.022888 | 0.064087 | 121.2021 | -0.8606 | -1.0208 | 121.2524 | 121.2479 | 121.1243 | 0.045776 | -0.07782 | 121.1975 | -0.80109 | -0.93384 | 121.312 | 121.3394 | 121.2524 | 0.14191 | 0.054932 | 0.050354 | -0.036621 | 0.11444 | 0.054932 | 0.1236 | 0.18768 | 121.3257 | 121.3852 | -0.98419 | -0.98877 | 121.1655 | 121.2524 | 121.1517 | 121.2204
6219.7656 | 122.2961 | -121.2891 | 0.9201 | -0.21187 | -0.038971 | -0.0053128 | 0.0208 | -0.00020513 | -0.016938 | -0.0062185 | -0.10159 | 0.023041 | 0.015144 | -0.016605 | -0.02136 | 0.025699 | 0.00082889 | -0.12817 | 0.045776 | -0.073242 | -0.10986 | -0.041199 | -0.17853 | -0.050354 | -0.086975 | 0.10529 | -0.082397 | -0.07782 | 0.004578 | -0.041199 | 0.050354 | 121.2158 | -0.87433 | -1.03 | 121.2479 | 121.2387 | 121.1105 | 0.022888 | -0.10529 | 121.2067 | -0.81482 | -0.99792 | 121.2936 | 121.3394 | 121.2479 | 0.13275 | 0.041198 | 0.032043 | -0.036621 | 0.086975 | 0.004577 | 0.11902 | 0.18768 | 121.3348 | 121.3943 | -0.99335 | -1.0025 | 121.1792 | 121.2112 | 121.1609 | 121.2021
6221.4688 | 122.3923 | -121.257 | 0.90179 | -0.25764 | -0.04068 | 0.00066863 | 0.017169 | 0.0032129 | -0.012452 | -0.0060049 | -0.019196 | 0.022614 | 0.014076 | -0.014255 | -0.01901 | 0.025058 | -0.0021619 | -0.10529 | 0.009155 | -0.032043 | -0.027466 | 0.10071 | -0.064087 | 0.059509 | 0.018311 | 0.086975 | -0.068665 | 0.009155 | 0.10986 | 0.068665 | 0.10986 | 121.225 | -0.89264 | -0.92926 | 121.3577 | 121.3165 | 121.1929 | 0.091552 | -0.032044 | 121.1884 | -0.81482 | -0.89264 | 121.3669 | 121.3669 | 121.3257 | 0.17853 | 0.13733 | 0.13275 | 0.004577 | 0.17853 | 0.07782 | 0.041198 | 0.15564 | 121.2662 | 121.344 | -0.93384 | -0.97046 | 121.2296 | 121.2662 | 121.1517 | 121.2753
6223.1719 | 122.319 | -121.2936 | 0.94757 | -0.1432 | -0.041321 | -0.0031766 | 0.019305 | -0.0019141 | -0.013093 | -0.0057913 | -0.04361 | 0.023255 | 0.014503 | -0.011905 | -0.021574 | 0.026126 | -0.0040845 | -0.15564 | 0.059509 | -0.086975 | -0.10986 | 0.004578 | -0.09613 | 0.004578 | -0.082397 | 0.1236 | -0.091553 | -0.07782 | 0.041199 | 0.004578 | 0.050354 | 121.2067 | -0.88806 | -1.0574 | 121.2982 | 121.2982 | 121.1975 | 0.091553 | -0.009155 | 121.2021 | -0.82398 | -1.0254 | 121.3348 | 121.344 | 121.2982 | 0.14191 | 0.096131 | 0.091553 | -0.022888 | 0.13275 | 0.013733 | 0.14648 | 0.21515 | 121.3531 | 121.4172 | -1.0345 | -1.0391 | 121.1838 | 121.2158 | 121.138 | 121.2112
6224.9062 | 122.4243 | -121.2662 | 0.89264 | -0.17372 | -0.040467 | -0.0027494 | 0.016742 | -0.0027685 | -0.011811 | -0.0057913 | -0.0069885 | 0.025391 | 0.014717 | -0.0181 | -0.020292 | 0.023776 | -0.0075025 | -0.10071 | 0.018311 | -0.059509 | -0.041199 | 0.068665 | -0.073242 | 0.068665 | 0.018311 | 0.091553 | -0.068665 | 0.018311 | 0.13275 | 0.10529 | 0.1236 | 121.2067 | -0.87433 | -0.93384 | 121.3348 | 121.3348 | 121.1929 | 0.12817 | -0.013733 | 121.1975 | -0.80109 | -0.87433 | 121.3989 | 121.3898 | 121.3715 | 0.19226 | 0.17395 | 0.12817 | 0.01831 | 0.20142 | 0.086976 | 0.07782 | 0.16022 | 121.2845 | 121.3577 | -0.95215 | -0.9613 | 121.225 | 121.2845 | 121.1655 | 121.2845
6226.6094 | 122.3465 | -121.3211 | 0.89722 | -0.17372 | -0.040253 | -0.00018577 | 0.022296 | 0.0015039 | -0.009675 | -0.0032277 | -0.10464 | 0.024964 | 0.013648 | -0.0093417 | -0.022428 | 0.025485 | -0.0040845 | -0.14191 | 0.032043 | -0.073242 | -0.10529 | -0.022888 | -0.14191 | -0.032043 | -0.059509 | 0.11444 | -0.091553 | -0.027466 | 0.032043 | -0.022888 | 0.086975 | 121.2479 | -0.86517 | -1.0025 | 121.2982 | 121.2891 | 121.1792 | 0.041199 | -0.068665 | 121.2296 | -0.78278 | -0.92468 | 121.3531 | 121.4081 | 121.2982 | 0.17853 | 0.068665 | 0.050354 | -0.032044 | 0.1236 | 0.064087 | 0.10529 | 0.20599 | 121.3531 | 121.4355 | -0.97046 | -0.98877 | 121.2158 | 121.2936 | 121.1792 | 121.2616
6228.2969 | 122.3648 | -121.2799 | 0.90179 | -0.17372 | -0.041535 | 0.00024143 | 0.01781 | -0.0014867 | -0.012239 | -0.0053641 | -0.0008851 | 0.021973 | 0.014717 | -0.014896 | -0.020292 | 0.025485 | -0.0023755 | -0.068665 | 0.013733 | -0.050354 | -0.009155 | 0.10529 | -0.018311 | 0.064087 | 0.036621 | 0.091553 | -0.064087 | -0.018311 | 0.10986 | 0.059509 | 0.091553 | 121.2296 | -0.88806 | -0.91095 | 121.3852 | 121.344 | 121.2616 | 0.11444 | 0.032043 | 121.2158 | -0.81024 | -0.9201 | 121.3898 | 121.3715 | 121.3394 | 0.15564 | 0.1236 | 0.15564 | 0.041199 | 0.17395 | 0.045776 | 0.064087 | 0.15564 | 121.2936 | 121.3715 | -0.95215 | -0.96588 | 121.2708 | 121.2616 | 121.2112 | 121.3165
6230.0156 | 122.319 | -121.3074 | 0.90179 | -0.19661 | -0.039612 | -0.0048856 | 0.022723 | -0.00041873 | -0.019929 | -0.010064 | -0.12296 | 0.021973 | 0.016639 | -0.014469 | -0.021574 | 0.023349 | -0.0045117 | -0.10071 | 0.045776 | -0.07782 | -0.073242 | 0 | -0.14648 | -0.054932 | -0.064087 | 0.11902 | -0.073242 | -0.054932 | 0.041199 | -0.041199 | 0.045776 | 121.2296 | -0.85602 | -0.97504 | 121.3074 | 121.2524 | 121.1609 | 0.022888 | -0.068664 | 121.2341 | -0.78277 | -0.95673 | 121.3486 | 121.3531 | 121.2662 | 0.11902 | 0.032043 | 0.07782 | 0.004578 | 0.11444 | 0.01831 | 0.1236 | 0.19226 | 121.3531 | 121.4264 | -0.97961 | -0.97504 | 121.2341 | 121.2524 | 121.2067 | 121.2433
6231.7188 | 122.3648 | -121.3028 | 0.90179 | -0.082169 | -0.041962 | -0.00061317 | 0.019305 | -0.0012731 | -0.014161 | -0.0034415 | -0.06192 | 0.023896 | 0.014717 | -0.0080601 | -0.019865 | 0.025485 | -0.0062207 | -0.14191 | 0.059509 | -0.082397 | -0.09613 | 0 | -0.10529 | 0 | -0.073242 | 0.13275 | -0.09613 | -0.054932 | 0.054932 | 0.009155 | 0.073242 | 121.2204 | -0.84228 | -0.99792 | 121.3028 | 121.3028 | 121.1975 | 0.082397 | -0.022889 | 121.2067 | -0.76904 | -0.95673 | 121.3577 | 121.376 | 121.312 | 0.16937 | 0.10528 | 0.082397 | -0.013733 | 0.15106 | 0.041198 | 0.14191 | 0.22888 | 121.3623 | 121.4355 | -0.98419 | -0.99792 | 121.2067 | 121.2479 | 121.1609 | 121.2296
6233.4062 | 122.4426 | -121.2616 | 0.87433 | -0.17372 | -0.037689 | 0.001523 | 0.019732 | 0.00064947 | -0.010957 | -0.0060049 | -0.055817 | 0.023896 | 0.013435 | -0.0080601 | -0.020292 | 0.028049 | -0.0015209 | -0.064087 | 0.013733 | -0.041199 | 0.018311 | 0.12817 | -0.041199 | 0.073242 | 0.073242 | 0.073242 | -0.041199 | 0.086975 | 0.16937 | 0.10071 | 0.1831 | 121.2204 | -0.8606 | -0.85602 | 121.3898 | 121.3348 | 121.2204 | 0.11444 | 0 | 121.2204 | -0.80109 | -0.78735 | 121.431 | 121.4447 | 121.3623 | 0.2243 | 0.14191 | 0.16937 | 0.05951 | 0.21057 | 0.12817 | 0.054932 | 0.11444 | 121.2753 | 121.3348 | -0.91553 | -0.91553 | 121.2799 | 121.3486 | 121.1975 | 121.3348
6235.1406 | 122.3785 | -121.312 | 0.90179 | -0.097427 | -0.040894 | -0.0018948 | 0.021441 | -0.0010595 | -0.011384 | -0.0047231 | -0.092438 | 0.02176 | 0.013221 | -0.012119 | -0.01901 | 0.025912 | -0.0036573 | -0.09613 | 0.041199 | -0.082397 | -0.041199 | 0.064087 | -0.09613 | 0.027466 | 0.013733 | 0.10071 | -0.064087 | 0 | 0.10986 | 0.027466 | 0.10071 | 121.2296 | -0.86059 | -0.94299 | 121.376 | 121.3394 | 121.2158 | 0.10986 | -0.013733 | 121.2479 | -0.80109 | -0.90179 | 121.4218 | 121.4127 | 121.3394 | 0.1648 | 0.091553 | 0.14648 | 0.041198 | 0.17395 | 0.064087 | 0.1236 | 0.1648 | 121.3531 | 121.4127 | -0.98419 | -0.96588 | 121.2708 | 121.312 | 121.2158 | 121.3257
6236.8438 | 122.438 | -121.2616 | 0.88348 | -0.11269 | -0.04303 | -0.0014676 | 0.018023 | -0.0023413 | -0.011811 | -0.0055777 | -0.019196 | 0.021546 | 0.015357 | -0.010837 | -0.020933 | 0.026126 | -0.00045291 | -0.082397 | 0.013733 | -0.041199 | 0.036621 | 0.13733 | 0.013733 | 0.09613 | 0.059509 | 0.086975 | -0.059509 | 0.022888 | 0.15106 | 0.11902 | 0.12817 | 121.2204 | -0.86975 | -0.84686 | 121.3989 | 121.3577 | 121.2753 | 0.13733 | 0.054932 | 121.2021 | -0.79651 | -0.8606 | 121.4127 | 121.3898 | 121.3806 | 0.18768 | 0.17853 | 0.17853 | 0.07782 | 0.21057 | 0.082397 | 0.054932 | 0.14648 | 121.2753 | 121.3486 | -0.92468 | -0.94299 | 121.2982 | 121.2845 | 121.1792 | 121.3211
6238.6094 | 122.4426 | -121.2708 | 0.88806 | -0.1432 | -0.039185 | -0.00082677 | 0.017596 | -0.0025549 | -0.013307 | -0.0047231 | -0.01004 | 0.023469 | 0.013435 | -0.017673 | -0.020078 | 0.024417 | -0.0028027 | -0.073242 | -0.004578 | -0.045776 | 0.009155 | 0.13275 | 0.013733 | 0.10071 | 0.059509 | 0.068665 | -0.059509 | 0.045776 | 0.16479 | 0.12817 | 0.14648 | 121.225 | -0.89264 | -0.87891 | 121.4035 | 121.3715 | 121.2845 | 0.14648 | 0.059509 | 121.2112 | -0.8194 | -0.84229 | 121.4355 | 121.4172 | 121.3989 | 0.20599 | 0.18768 | 0.17853 | 0.054931 | 0.2243 | 0.10528 | 0.041198 | 0.12817 | 121.2662 | 121.3394 | -0.93384 | -0.94757 | 121.2799 | 121.3165 | 121.1975 | 121.3303
6240.2969 | 122.4152 | -121.312 | 0.90179 | -0.20424 | -0.041321 | -0.0023222 | 0.018451 | -0.0019141 | -0.013093 | -0.0034415 | -0.028351 | 0.023896 | 0.014076 | -0.020664 | -0.020719 | 0.025272 | -0.0038709 | -0.068665 | 0.018311 | -0.050354 | 0.018311 | 0.12817 | 0.009155 | 0.082397 | 0.059509 | 0.091553 | -0.041199 | 0.022888 | 0.14648 | 0.10071 | 0.13275 | 121.2616 | -0.88348 | -0.88348 | 121.4401 | 121.3943 | 121.3211 | 0.13275 | 0.059509 | 121.2708 | -0.81024 | -0.87891 | 121.4584 | 121.4447 | 121.4127 | 0.17395 | 0.14191 | 0.17853 | 0.068665 | 0.18768 | 0.064087 | 0.068665 | 0.13275 | 121.3303 | 121.4035 | -0.95215 | -0.94299 | 121.3303 | 121.3348 | 121.2433 | 121.3715
6242.0625 | 122.406 | -121.3257 | 0.87433 | -0.24239 | -0.03833 | 0.00045503 | 0.018878 | 0.0029993 | -0.0098886 | -0.0013051 | -0.098541 | 0.021546 | 0.014289 | -0.0093417 | -0.022215 | 0.024204 | -0.0047253 | -0.13733 | 0.059509 | -0.064087 | -0.082397 | 0.004578 | -0.13733 | -0.018311 | -0.018311 | 0.09613 | -0.064087 | 0.009155 | 0.09613 | 0.041199 | 0.11902 | 121.2616 | -0.81482 | -0.95673 | 121.3303 | 121.3074 | 121.1884 | 0.045776 | -0.073242 | 121.2616 | -0.7782 | -0.86517 | 121.4218 | 121.4447 | 121.3669 | 0.18311 | 0.10529 | 0.068665 | -0.01831 | 0.16022 | 0.073242 | 0.1236 | 0.16022 | 121.3852 | 121.4218 | -0.93842 | -0.93842 | 121.2433 | 121.3348 | 121.1884 | 121.3074
6243.7656 | 122.3648 | -121.3623 | 0.89722 | -0.1432 | -0.038971 | 0.00088223 | 0.019305 | -0.00084593 | -0.014375 | -0.0036551 | -0.04361 | 0.022828 | 0.012153 | -0.0084873 | -0.020506 | 0.026981 | -0.00066651 | -0.15106 | 0.041199 | -0.073242 | -0.10986 | 0.009155 | -0.10986 | 0 | -0.064087 | 0.10986 | -0.09613 | -0.068665 | 0.050354 | 0 | 0.045776 | 121.2891 | -0.85602 | -1.0071 | 121.3715 | 121.3623 | 121.2524 | 0.073242 | -0.036621 | 121.2662 | -0.78735 | -0.96588 | 121.4127 | 121.4081 | 121.3623 | 0.14191 | 0.09613 | 0.082397 | -0.036621 | 0.14648 | 0.027465 | 0.11444 | 0.20599 | 121.4035 | 121.4722 | -0.97046 | -0.99335 | 121.2524 | 121.2936 | 121.2112 | 121.2982
6245.5 | 122.3328 | -121.3394 | 0.90179 | -0.2195 | -0.037903 | 0.0013094 | 0.021441 | 0.0064173 | -0.010957 | -0.0019461 | -0.1077 | 0.026673 | 0.014717 | -0.0093417 | -0.019865 | 0.027621 | -0.0068615 | -0.13733 | 0.050354 | -0.073242 | -0.10986 | -0.041199 | -0.16937 | -0.054932 | -0.10071 | 0.12817 | -0.091553 | -0.032043 | 0.027466 | -0.027466 | 0.059509 | 121.2662 | -0.85144 | -1.0117 | 121.2982 | 121.2845 | 121.17 | 0.01831 | -0.096131 | 121.2479 | -0.77362 | -0.93384 | 121.3669 | 121.3989 | 121.312 | 0.15106 | 0.064087 | 0.032043 | -0.036621 | 0.11902 | 0.05951 | 0.1236 | 0.21973 | 121.3898 | 121.4676 | -0.97504 | -0.99335 | 121.2296 | 121.3074 | 121.2021 | 121.2387
6247.2188 | 122.4792 | -121.3348 | 0.85602 | -0.15083 | -0.039826 | -0.0018948 | 0.019732 | -0.0019141 | -0.012452 | -0.0042959 | 0.0082703 | 0.022614 | 0.01493 | -0.017246 | -0.018156 | 0.023776 | -0.0045117 | -0.09613 | 0.018311 | -0.045776 | -0.013733 | 0.10986 | -0.009155 | 0.086975 | 0.073242 | 0.068665 | -0.050354 | 0.054932 | 0.1831 | 0.15106 | 0.16937 | 121.2891 | -0.83771 | -0.86975 | 121.4447 | 121.4218 | 121.3257 | 0.13275 | 0.036621 | 121.2845 | -0.78735 | -0.80109 | 121.5179 | 121.5042 | 121.4859 | 0.21973 | 0.20142 | 0.15564 | 0.032043 | 0.23346 | 0.10529 | 0.064087 | 0.11902 | 121.3531 | 121.4035 | -0.90179 | -0.90637 | 121.3211 | 121.3898 | 121.2387 | 121.4081
6248.9219 | 122.3923 | -121.3165 | 0.87891 | -0.12794 | -0.03833 | 0.0013094 | 0.019305 | 0.0019311 | -0.012666 | -0.0013051 | -0.10464 | 0.023896 | 0.015998 | -0.019382 | -0.018156 | 0.019077 | -0.0066479 | -0.086975 | 0.045776 | -0.07782 | -0.032043 | 0.073242 | -0.07782 | 0.013733 | 0.018311 | 0.091553 | -0.064087 | 0.004578 | 0.086975 | 0.022888 | 0.086975 | 121.2387 | -0.83313 | -0.91095 | 121.3898 | 121.3303 | 121.2387 | 0.091553 | 0 | 121.2524 | -0.78735 | -0.87433 | 121.4035 | 121.4035 | 121.3394 | 0.15106 | 0.086975 | 0.15106 | 0.045777 | 0.15106 | 0.068665 | 0.1236 | 0.15564 | 121.3623 | 121.4081 | -0.95673 | -0.94299 | 121.2845 | 121.3211 | 121.2296 | 121.3348
6250.6562 | 122.406 | -121.3531 | 0.89722 | -0.12032 | -0.040894 | -0.00082677 | 0.0208 | 0.0057763 | -0.011811 | -0.0062185 | -0.083283 | 0.02176 | 0.016212 | -0.013828 | -0.020292 | 0.02634 | -0.0055799 | -0.12817 | 0.050354 | -0.086975 | -0.091553 | 0.009155 | -0.09613 | 0 | -0.064087 | 0.13275 | -0.064087 | -0.013733 | 0.07782 | 0.018311 | 0.091553 | 121.2662 | -0.84686 | -0.98877 | 121.3623 | 121.3531 | 121.257 | 0.086975 | -0.009155 | 121.2891 | -0.76447 | -0.91095 | 121.431 | 121.4447 | 121.3715 | 0.15564 | 0.082398 | 0.09613 | -0.004578 | 0.14191 | 0.050354 | 0.13733 | 0.19684 | 121.4035 | 121.4859 | -0.98419 | -0.9613 | 121.2616 | 121.3394 | 121.225 | 121.2891
6252.3438 | 122.4472 | -121.312 | 0.86975 | -0.19661 | -0.039398 | 0.0017368 | 0.016955 | -0.00084593 | -0.009675 | -0.0049367 | -0.034454 | 0.022828 | 0.014717 | -0.014255 | -0.018156 | 0.023776 | -2.571e-05 | -0.068665 | 0.004578 | -0.036621 | 0.009155 | 0.14191 | -0.027466 | 0.082397 | 0.082397 | 0.068665 | -0.041199 | 0.054932 | 0.14648 | 0.086975 | 0.13275 | 121.2753 | -0.86517 | -0.8606 | 121.4539 | 121.3943 | 121.2845 | 0.11902 | 0.009155 | 121.2708 | -0.80109 | -0.81482 | 121.4584 | 121.4447 | 121.3989 | 0.17395 | 0.12817 | 0.17853 | 0.045776 | 0.18768 | 0.096131 | 0.041199 | 0.10986 | 121.3165 | 121.3806 | -0.90637 | -0.91095 | 121.3211 | 121.3669 | 121.2433 | 121.3943
6254.0469 | 122.3648 | -121.3531 | 0.89722 | -0.20424 | -0.038971 | 2.7834e-05 | 0.018451 | 0.0019311 | -0.012452 | -0.0023733 | -0.092438 | 0.02411 | 0.015144 | -0.0033603 | -0.019438 | 0.02399 | -0.0010937 | -0.13275 | 0.050354 | -0.082397 | -0.11902 | -0.027466 | -0.15106 | -0.032043 | -0.07782 | 0.10986 | -0.07782 | -0.036621 | 0.018311 | -0.022888 | 0.054932 | 121.2708 | -0.84686 | -1.0162 | 121.3257 | 121.3211 | 121.2021 | 0.050354 | -0.068665 | 121.2753 | -0.78735 | -0.93384 | 121.3715 | 121.4081 | 121.3303 | 0.13275 | 0.054932 | 0.054931 | -0.036622 | 0.096131 | 0.041199 | 0.13275 | 0.18768 | 121.4035 | 121.463 | -0.97961 | -0.97504 | 121.2341 | 121.3165 | 121.2204 | 121.2753
6255.7656 | 122.4792 | -121.3165 | 0.86975 | -0.23476 | -0.040253 | 0.00045503 | 0.019305 | 0.0034265 | -0.0090342 | -0.0077139 | -0.049713 | 0.021119 | 0.015998 | -0.012119 | -0.019865 | 0.025272 | -0.0042981 | -0.10071 | 0.027466 | -0.068665 | 0 | 0.09613 | -0.050354 | 0.073242 | 0.050354 | 0.09613 | -0.032043 | 0.064087 | 0.16022 | 0.091553 | 0.16022 | 121.2479 | -0.84229 | -0.86975 | 121.4127 | 121.3898 | 121.2662 | 0.14191 | 0.018311 | 121.2845 | -0.77362 | -0.80566 | 121.4767 | 121.4767 | 121.4081 | 0.19226 | 0.1236 | 0.16479 | 0.068665 | 0.19226 | 0.09613 | 0.096131 | 0.12817 | 121.344 | 121.4127 | -0.93842 | -0.90179 | 121.3165 | 121.3806 | 121.2158 | 121.3669
6257.4688 | 122.3831 | -121.344 | 0.8606 | -0.10506 | -0.039185 | -0.0059538 | 0.020373 | 0.0034265 | -0.014375 | -0.0066457 | -0.10464 | 0.023041 | 0.016426 | -0.0059237 | -0.020933 | 0.024204 | -0.0032299 | -0.07782 | 0.022888 | -0.07782 | -0.027466 | 0.068665 | -0.09613 | 0.022888 | 0.032043 | 0.10529 | -0.073242 | 0 | 0.086975 | 0.022888 | 0.10529 | 121.2662 | -0.83771 | -0.88806 | 121.4127 | 121.3669 | 121.2479 | 0.10071 | -0.01831 | 121.2708 | -0.75531 | -0.8606 | 121.431 | 121.4493 | 121.3669 | 0.17853 | 0.09613 | 0.14649 | 0.050354 | 0.16022 | 0.073242 | 0.10071 | 0.17853 | 121.3669 | 121.4493 | -0.93842 | -0.93384 | 121.3165 | 121.344 | 121.2662 | 121.376
6259.1719 | 122.493 | -121.3303 | 0.86975 | -0.12032 | -0.039826 | -0.00061317 | 0.015674 | -0.0061865 | -0.012452 | -0.0060049 | -0.0039367 | 0.022828 | 0.014717 | -0.0095553 | -0.020292 | 0.025912 | 0.00061529 | -0.064087 | 0 | -0.041199 | 0.036621 | 0.15564 | 0.004578 | 0.11444 | 0.086975 | 0.07782 | -0.050354 | 0.054932 | 0.17395 | 0.13275 | 0.15564 | 121.2891 | -0.86975 | -0.83313 | 121.4859 | 121.4447 | 121.3348 | 0.15564 | 0.045777 | 121.2799 | -0.79193 | -0.81482 | 121.5042 | 121.4859 | 121.463 | 0.20599 | 0.18311 | 0.19684 | 0.07782 | 0.2243 | 0.10529 | 0.041199 | 0.12817 | 121.3303 | 121.4081 | -0.91095 | -0.92011 | 121.3669 | 121.3852 | 121.2662 | 121.4172
6260.8906 | 122.5159 | -121.3303 | 0.8606 | -0.16609 | -0.041535 | -0.001254 | 0.017169 | -0.0017005 | -0.011598 | -0.0032277 | -0.01004 | 0.021973 | 0.01493 | -0.011264 | -0.022428 | 0.025485 | -0.0015209 | -0.07782 | 0.009155 | -0.054932 | 0.036621 | 0.16937 | 0.022888 | 0.09613 | 0.10529 | 0.073242 | -0.059509 | 0.059509 | 0.18768 | 0.13733 | 0.14191 | 121.2753 | -0.85144 | -0.82398 | 121.4996 | 121.4264 | 121.3531 | 0.15106 | 0.07782 | 121.2708 | -0.78735 | -0.80109 | 121.5179 | 121.4722 | 121.4676 | 0.20142 | 0.19684 | 0.22431 | 0.091553 | 0.24719 | 0.11902 | 0.064087 | 0.13275 | 121.3394 | 121.4035 | -0.91553 | -0.92011 | 121.3669 | 121.3898 | 121.2524 | 121.4355
6262.5781 | 122.5113 | -121.3165 | 0.8606 | -0.19661 | -0.037689 | 0.00066863 | 0.019732 | 0.0017175 | -0.015016 | -0.0036551 | -0.037506 | 0.024537 | 0.014717 | -0.0054965 | -0.021574 | 0.026126 | 0.00018809 | -0.050354 | -0.004578 | -0.041199 | 0.022888 | 0.14191 | -0.032043 | 0.07782 | 0.091553 | 0.064087 | -0.036621 | 0.091553 | 0.16022 | 0.10529 | 0.16937 | 121.2753 | -0.86517 | -0.83771 | 121.4584 | 121.3943 | 121.2845 | 0.11902 | 0.009156 | 121.2799 | -0.79651 | -0.76904 | 121.4767 | 121.4859 | 121.4218 | 0.20599 | 0.14191 | 0.18311 | 0.064087 | 0.19684 | 0.12817 | 0.036621 | 0.10071 | 121.312 | 121.3806 | -0.9018 | -0.89722 | 121.3394 | 121.4081 | 121.2662 | 121.4081
6264.2812 | 122.4106 | -121.376 | 0.87891 | -0.15846 | -0.041535 | -0.002963 | 0.019946 | 0.00064947 | -0.01352 | -0.0030141 | -0.077179 | 0.023469 | 0.014076 | -0.012332 | -0.020078 | 0.027835 | -0.0092115 | -0.15106 | 0.050354 | -0.082397 | -0.09613 | -0.013733 | -0.10529 | 0 | -0.064087 | 0.11902 | -0.073242 | -0.045776 | 0.059509 | 0.004578 | 0.068665 | 121.2936 | -0.82855 | -0.97504 | 121.3623 | 121.376 | 121.2708 | 0.082397 | -0.022889 | 121.3028 | -0.75989 | -0.92468 | 121.4355 | 121.4447 | 121.3806 | 0.14191 | 0.07782 | 0.068664 | -0.013733 | 0.13275 | 0.027466 | 0.13275 | 0.19226 | 121.4264 | 121.4951 | -0.9613 | -0.95215 | 121.2799 | 121.3303 | 121.225 | 121.312
6266.0156 | 122.5067 | -121.3669 | 0.84686 | -0.16609 | -0.041535 | 0.00024143 | 0.017382 | -0.0031957 | -0.012025 | -0.0034415 | -0.0039367 | 0.021119 | 0.015571 | -0.019809 | -0.019865 | 0.024844 | -2.571e-05 | -0.091553 | 0.004578 | -0.041199 | 0.054932 | 0.19684 | 0.022888 | 0.11444 | 0.086975 | 0.073242 | -0.045776 | 0.054932 | 0.18768 | 0.14648 | 0.15564 | 121.3257 | -0.84229 | -0.79193 | 121.5637 | 121.4813 | 121.3898 | 0.15564 | 0.064087 | 121.3211 | -0.77362 | -0.79193 | 121.5546 | 121.5225 | 121.5134 | 0.20142 | 0.19226 | 0.23804 | 0.096131 | 0.23346 | 0.10071 | 0.045777 | 0.11902 | 121.3715 | 121.4401 | -0.88806 | -0.89264 | 121.4218 | 121.4218 | 121.2753 | 121.4539
6267.7188 | 122.4655 | -121.3669 | 0.85602 | -0.21187 | -0.03833 | 0.0017368 | 0.018023 | -0.0014867 | -0.011384 | -0.0055777 | -0.028351 | 0.02475 | 0.014076 | -0.017673 | -0.020292 | 0.023776 | -0.0049389 | -0.09613 | 0.009155 | -0.041199 | 0 | 0.1236 | -0.036621 | 0.082397 | 0.050354 | 0.064087 | -0.045776 | 0.027466 | 0.13275 | 0.073242 | 0.11902 | 121.3257 | -0.84686 | -0.85602 | 121.4905 | 121.4493 | 121.3303 | 0.1236 | 0.004578 | 121.3211 | -0.79193 | -0.82855 | 121.4996 | 121.4859 | 121.4401 | 0.16479 | 0.11902 | 0.16479 | 0.041199 | 0.17853 | 0.073242 | 0.050354 | 0.10986 | 121.376 | 121.431 | -0.89722 | -0.90179 | 121.3669 | 121.3943 | 121.2708 | 121.4172
6269.4219 | 122.5021 | -121.3486 | 0.83313 | -0.23476 | -0.039398 | 0.00024143 | 0.021869 | -0.00041873 | -0.010316 | -0.00087794 | -0.098541 | 0.021973 | 0.015571 | -0.012119 | -0.01901 | 0.027194 | -0.0017347 | -0.10986 | 0.036621 | -0.064087 | -0.045776 | 0.045776 | -0.09613 | 0.018311 | 0.045776 | 0.10071 | -0.064087 | 0.054932 | 0.14191 | 0.086975 | 0.16479 | 121.2845 | -0.79651 | -0.87891 | 121.3943 | 121.3669 | 121.2524 | 0.082398 | -0.032043 | 121.2845 | -0.73242 | -0.7782 | 121.4905 | 121.5134 | 121.4355 | 0.22888 | 0.15106 | 0.10986 | 0.018311 | 0.20599 | 0.11902 | 0.10071 | 0.1648 | 121.3852 | 121.4493 | -0.89722 | -0.89722 | 121.3028 | 121.4035 | 121.2387 | 121.3943
6271.1406 | 122.4289 | -121.3531 | 0.87433 | -0.15083 | -0.037689 | 0.0010958 | 0.018664 | 0.0010767 | -0.013307 | -0.0057913 | -0.098541 | 0.023041 | 0.013648 | -0.013187 | -0.020506 | 0.023563 | -0.0034435 | -0.1236 | 0.045776 | -0.082397 | -0.064087 | 0.022888 | -0.091553 | 0.018311 | -0.027466 | 0.10529 | -0.082397 | -0.004578 | 0.10529 | 0.032043 | 0.10986 | 121.2708 | -0.82855 | -0.93842 | 121.376 | 121.3715 | 121.2616 | 0.10071 | -0.009156 | 121.2708 | -0.76904 | -0.87891 | 121.4584 | 121.463 | 121.3852 | 0.19226 | 0.11444 | 0.10528 | 0.01831 | 0.18768 | 0.077819 | 0.12817 | 0.18768 | 121.3989 | 121.4584 | -0.95673 | -0.95673 | 121.2891 | 121.3486 | 121.2296 | 121.3257
6272.8438 | 122.4747 | -121.3531 | 0.85602 | -0.16609 | -0.04068 | -0.0014676 | 0.016742 | -0.00041873 | -0.012666 | -0.0068593 | 0.0052185 | 0.024323 | 0.014503 | -0.016818 | -0.019224 | 0.023135 | -0.0021619 | -0.11444 | 0.009155 | -0.050354 | -0.036621 | 0.07782 | -0.059509 | 0.050354 | 0.009155 | 0.086975 | -0.054932 | 0.032043 | 0.14191 | 0.07782 | 0.11444 | 121.3028 | -0.84686 | -0.89264 | 121.431 | 121.4035 | 121.2936 | 0.10071 | -0.009155 | 121.2982 | -0.76904 | -0.82397 | 121.4951 | 121.4676 | 121.431 | 0.16937 | 0.13275 | 0.12817 | 0.013733 | 0.19684 | 0.086975 | 0.059509 | 0.14191 | 121.3623 | 121.4401 | -0.90637 | -0.91095 | 121.3165 | 121.3852 | 121.2387 | 121.3623
6274.5469 | 122.5021 | -121.3348 | 0.86517 | -0.23476 | -0.03833 | 0.00088223 | 0.018878 | 0.0021447 | -0.011811 | -0.0066457 | -0.083283 | 0.022614 | 0.015785 | -0.012546 | -0.019224 | 0.025699 | -0.0032299 | -0.10071 | 0.013733 | -0.064087 | -0.004578 | 0.10986 | -0.082397 | 0.068665 | 0.073242 | 0.073242 | -0.050354 | 0.068665 | 0.15106 | 0.09613 | 0.16937 | 121.2708 | -0.85144 | -0.86975 | 121.4447 | 121.4035 | 121.2524 | 0.13275 | -0.01831 | 121.2845 | -0.79193 | -0.79651 | 121.4859 | 121.5042 | 121.431 | 0.21973 | 0.14648 | 0.17395 | 0.059509 | 0.20142 | 0.11902 | 0.07782 | 0.1236 | 121.3486 | 121.4081 | -0.92926 | -0.91553 | 121.3303 | 121.4035 | 121.2341 | 121.4081
6276.2812 | 122.5159 | -121.3486 | 0.85602 | -0.2195 | -0.037049 | -0.00061317 | 0.020587 | 0.0021447 | -0.010743 | -0.0032277 | -0.037506 | 0.024323 | 0.017707 | -0.018314 | -0.017729 | 0.026553 | -0.0032299 | -0.059509 | 0.009155 | -0.036621 | 0.022888 | 0.1236 | -0.018311 | 0.10071 | 0.073242 | 0.064087 | -0.045776 | 0.073242 | 0.16479 | 0.10529 | 0.16937 | 121.312 | -0.84686 | -0.83313 | 121.4722 | 121.4493 | 121.3303 | 0.13733 | 0.01831 | 121.3028 | -0.79193 | -0.78278 | 121.5134 | 121.5179 | 121.4539 | 0.21515 | 0.15106 | 0.16022 | 0.059509 | 0.21057 | 0.11902 | 0.045776 | 0.10986 | 121.3577 | 121.4127 | -0.89264 | -0.90179 | 121.3715 | 121.4218 | 121.2891 | 121.4218
6277.9844 | 122.3511 | -121.3898 | 0.89264 | -0.15846 | -0.038971 | 0.0013094 | 0.022509 | 0.00022207 | -0.010743 | -0.0034415 | -0.13211 | 0.024323 | 0.015357 | -0.0076327 | -0.020078 | 0.026553 | -0.0049389 | -0.14648 | 0.045776 | -0.082397 | -0.10529 | -0.036621 | -0.16479 | -0.032043 | -0.09613 | 0.11902 | -0.09613 | -0.054932 | 0.018311 | -0.041199 | 0.054932 | 121.3074 | -0.84686 | -0.99792 | 121.3531 | 121.3577 | 121.225 | 0.050354 | -0.082398 | 121.2936 | -0.77362 | -0.94757 | 121.4081 | 121.4447 | 121.3486 | 0.15106 | 0.054931 | 0.045776 | -0.022889 | 0.11444 | 0.041198 | 0.12817 | 0.21515 | 121.4355 | 121.5088 | -0.97504 | -0.98877 | 121.2845 | 121.3348 | 121.2433 | 121.2936
6279.7031 | 122.5342 | -121.3715 | 0.83771 | -0.12794 | -0.041962 | 0.0013094 | 0.017596 | 0.0012903 | -0.013734 | -0.0042959 | -0.019196 | 0.022187 | 0.016853 | -0.011478 | -0.018583 | 0.025485 | -0.0055799 | -0.086975 | 0.009155 | -0.041199 | 0.032043 | 0.16937 | 0.022888 | 0.1236 | 0.10529 | 0.07782 | -0.068665 | 0.086975 | 0.20142 | 0.15564 | 0.16937 | 121.3303 | -0.82855 | -0.80566 | 121.5408 | 121.4951 | 121.3943 | 0.16479 | 0.064087 | 121.3028 | -0.75989 | -0.75073 | 121.5729 | 121.5408 | 121.5271 | 0.23804 | 0.22431 | 0.21057 | 0.073242 | 0.27008 | 0.15564 | 0.050354 | 0.14649 | 121.3806 | 121.4493 | -0.87891 | -0.90637 | 121.4035 | 121.4584 | 121.2845 | 121.4767
6281.4062 | 122.4335 | -121.4035 | 0.89264 | -0.15846 | -0.038544 | -0.0016812 | 0.020373 | 0.0032129 | -0.011598 | -0.0045095 | -0.064972 | 0.02411 | 0.015357 | -0.0065647 | -0.020078 | 0.026981 | -0.0038709 | -0.12817 | 0.059509 | -0.091553 | -0.07782 | -0.004578 | -0.09613 | -0.004578 | -0.054932 | 0.10986 | -0.09613 | -0.032043 | 0.073242 | 0.009155 | 0.082397 | 121.3119 | -0.83313 | -0.97046 | 121.3989 | 121.3989 | 121.3074 | 0.086975 | -0.004577 | 121.3074 | -0.78278 | -0.92468 | 121.4767 | 121.4859 | 121.4127 | 0.17853 | 0.10528 | 0.086975 | 0.013733 | 0.16937 | 0.064087 | 0.15106 | 0.20599 | 121.463 | 121.5134 | -0.98419 | -0.98877 | 121.3257 | 121.3715 | 121.2753 | 121.3486
6283.1406 | 122.5113 | -121.3531 | 0.84228 | -0.1432 | -0.042176 | -0.0016812 | 0.016314 | -0.0044775 | -0.013093 | -0.0028005 | -0.016144 | 0.022401 | 0.01493 | -0.023441 | -0.019224 | 0.025485 | -0.0021619 | -0.11444 | 0.032043 | -0.073242 | 0.004578 | 0.1236 | -0.018311 | 0.09613 | 0.059509 | 0.082397 | -0.045776 | 0.064087 | 0.19226 | 0.14191 | 0.16479 | 121.2799 | -0.81024 | -0.83771 | 121.4767 | 121.4493 | 121.3348 | 0.16937 | 0.054931 | 121.3074 | -0.75989 | -0.7782 | 121.5454 | 121.5179 | 121.4951 | 0.21057 | 0.18768 | 0.19684 | 0.07782 | 0.23804 | 0.10986 | 0.10529 | 0.12817 | 121.3852 | 121.4355 | -0.91553 | -0.88806 | 121.3577 | 121.4172 | 121.2387 | 121.4127
6284.8438 | 122.3694 | -121.3898 | 0.87891 | -0.16609 | -0.036835 | -0.00082677 | 0.0208 | -0.00084593 | -0.011811 | -0.0045095 | -0.12601 | 0.021546 | 0.015144 | -0.012546 | -0.020078 | 0.025485 | 0.0018969 | -0.13275 | 0.064087 | -0.07782 | -0.11444 | -0.041199 | -0.16022 | -0.045776 | -0.10529 | 0.10986 | -0.10071 | -0.041199 | 0.022888 | -0.027466 | 0.050354 | 121.312 | -0.81482 | -0.99335 | 121.3486 | 121.344 | 121.2296 | 0.032044 | -0.082397 | 121.2891 | -0.76904 | -0.9201 | 121.4127 | 121.4401 | 121.3623 | 0.15106 | 0.073242 | 0.036621 | -0.036621 | 0.1236 | 0.059509 | 0.14191 | 0.21057 | 121.4539 | 121.4996 | -0.95673 | -0.97961 | 121.2753 | 121.3486 | 121.257 | 121.2845
6286.5625 | 122.4747 | -121.3577 | 0.86517 | -0.2195 | -0.038971 | -0.00082677 | 0.016314 | 0.0010767 | -0.012239 | -0.0066457 | -0.019196 | 0.02176 | 0.015998 | -0.016605 | -0.018583 | 0.024631 | -0.0032299 | -0.1236 | 0.022888 | -0.050354 | -0.032043 | 0.068665 | -0.059509 | 0.059509 | 0 | 0.082397 | -0.059509 | 0 | 0.10071 | 0.07782 | 0.10986 | 121.3074 | -0.84228 | -0.89722 | 121.4264 | 121.4172 | 121.2982 | 0.10986 | -0.009155 | 121.2982 | -0.78278 | -0.86517 | 121.4584 | 121.4676 | 121.4355 | 0.16937 | 0.13733 | 0.11902 | 0.018311 | 0.16022 | 0.059509 | 0.073242 | 0.14191 | 121.3806 | 121.4401 | -0.91553 | -0.92468 | 121.3257 | 121.3577 | 121.2341 | 121.3577
6288.2656 | 122.4518 | -121.3943 | 0.8194 | -0.18898 | -0.042389 | -0.0025358 | 0.017596 | -0.0019141 | -0.013947 | -0.0047231 | -0.040558 | 0.021546 | 0.016853 | -0.012332 | -0.020506 | 0.026553 | -0.0015209 | -0.086975 | 0.018311 | -0.041199 | 0 | 0.11444 | -0.004578 | 0.07782 | 0.032043 | 0.082397 | -0.054932 | 0.013733 | 0.12817 | 0.07782 | 0.10529 | 121.3531 | -0.80109 | -0.8194 | 121.5088 | 121.4722 | 121.3898 | 0.11902 | 0.036621 | 121.3394 | -0.737 | -0.80566 | 121.5225 | 121.4996 | 121.4722 | 0.16022 | 0.13275 | 0.15564 | 0.041199 | 0.18311 | 0.068665 | 0.05951 | 0.13733 | 121.4127 | 121.4767 | -0.8606 | -0.87433 | 121.3943 | 121.4081 | 121.3074 | 121.4264
6289.9688 | 122.4655 | -121.4035 | 0.85144 | -0.12794 | -0.039826 | 0.00066863 | 0.018878 | 0.0017175 | -0.011598 | -0.0055777 | -0.01004 | 0.023682 | 0.014503 | -0.017032 | -0.022215 | 0.025272 | -0.0010937 | -0.10986 | 0.032043 | -0.064087 | -0.036621 | 0.073242 | -0.068665 | 0.054932 | -0.004578 | 0.086975 | -0.059509 | 0.004578 | 0.11444 | 0.064087 | 0.1236 | 121.3394 | -0.8194 | -0.88806 | 121.4767 | 121.4584 | 121.3348 | 0.11902 | -0.004578 | 121.344 | -0.76446 | -0.84686 | 121.5179 | 121.5271 | 121.4676 | 0.1831 | 0.1236 | 0.13733 | 0.027466 | 0.17395 | 0.064087 | 0.09613 | 0.14648 | 121.4355 | 121.4905 | -0.91553 | -0.91095 | 121.3669 | 121.4081 | 121.2936 | 121.3989
6291.6875 | 122.493 | -121.4218 | 0.82855 | -0.16609 | -0.037689 | 2.7834e-05 | 0.022937 | -0.0025549 | -0.012239 | -0.0051505 | -0.1077 | 0.023469 | 0.016212 | -0.0089145 | -0.023069 | 0.026981 | -0.0049389 | -0.1236 | 0.018311 | -0.054932 | -0.050354 | 0.032043 | -0.10986 | 0.013733 | 0.018311 | 0.086975 | -0.050354 | 0.064087 | 0.11902 | 0.082397 | 0.14648 | 121.3669 | -0.81024 | -0.87891 | 121.4539 | 121.4355 | 121.312 | 0.068665 | -0.054931 | 121.3715 | -0.74158 | -0.76446 | 121.5408 | 121.5683 | 121.5042 | 0.19684 | 0.13275 | 0.086975 | 0.004578 | 0.16937 | 0.11444 | 0.073243 | 0.13733 | 121.4401 | 121.5088 | -0.88348 | -0.87891 | 121.3715 | 121.4859 | 121.2982 | 121.4401
6293.3906 | 122.5204 | -121.3943 | 0.82398 | -0.15846 | -0.039612 | -0.0014676 | 0.017382 | 0.0019311 | -0.012879 | -0.0066457 | -0.031403 | 0.023255 | 0.016212 | -0.016391 | -0.021147 | 0.025058 | -0.0068615 | -0.068665 | 0.004578 | -0.041199 | 0.045776 | 0.15106 | 0.018311 | 0.11444 | 0.07782 | 0.059509 | -0.041199 | 0.054932 | 0.1831 | 0.1236 | 0.16022 | 121.3531 | -0.8194 | -0.7782 | 121.5454 | 121.5088 | 121.4127 | 0.15564 | 0.05951 | 121.3531 | -0.76447 | -0.76904 | 121.5775 | 121.5546 | 121.5179 | 0.20142 | 0.16479 | 0.19226 | 0.086975 | 0.2243 | 0.096131 | 0.045777 | 0.10071 | 121.3989 | 121.4539 | -0.86517 | -0.86517 | 121.4401 | 121.4493 | 121.3257 | 121.4722
6295.1406 | 122.4426 | -121.4355 | 0.84686 | -0.17372 | -0.040467 | -0.0021084 | 0.021014 | 0.0015039 | -0.013307 | -0.0013051 | -0.12906 | 0.024323 | 0.014076 | -0.013187 | -0.017729 | 0.019717 | -0.0045117 | -0.10071 | 0.045776 | -0.068665 | -0.032043 | 0.059509 | -0.09613 | 0.022888 | 0.009155 | 0.091553 | -0.068665 | -0.004578 | 0.086975 | 0.027466 | 0.09613 | 121.3669 | -0.80109 | -0.87891 | 121.4951 | 121.4584 | 121.3394 | 0.091553 | -0.027465 | 121.3669 | -0.75531 | -0.85144 | 121.5225 | 121.5317 | 121.463 | 0.16479 | 0.096131 | 0.12817 | 0.036622 | 0.15564 | 0.064087 | 0.11444 | 0.16022 | 121.4813 | 121.5271 | -0.91553 | -0.91553 | 121.4035 | 121.431 | 121.3348 | 121.4447
6296.8438 | 122.4243 | -121.4401 | 0.83771 | -0.12032 | -0.041535 | 0.0010958 | 0.01781 | -0.0025549 | -0.013093 | -0.0066457 | -0.034454 | 0.023041 | 0.013862 | -0.0134 | -0.018156 | 0.025485 | -0.0030163 | -0.07782 | 0.004578 | -0.054932 | -0.013733 | 0.09613 | -0.036621 | 0.059509 | -0.013733 | 0.11444 | -0.07782 | -0.032043 | 0.091553 | 0.013733 | 0.059509 | 121.3852 | -0.83313 | -0.85144 | 121.5363 | 121.4996 | 121.4035 | 0.11444 | 0.018311 | 121.3623 | -0.72327 | -0.86975 | 121.5317 | 121.4996 | 121.4539 | 0.13733 | 0.091553 | 0.15106 | 0.041199 | 0.16937 | 0.045777 | 0.05951 | 0.19226 | 121.4447 | 121.5546 | -0.89264 | -0.91553 | 121.4264 | 121.4081 | 121.3623 | 121.4264
6298.5625 | 122.5204 | -121.3989 | 0.82398 | -0.20424 | -0.036408 | -0.001254 | 0.016528 | -0.0029821 | -0.01053 | -0.0060049 | -0.031403 | 0.023255 | 0.012794 | -0.018741 | -0.020078 | 0.024417 | -0.0051525 | -0.068665 | 0.009155 | -0.027466 | 0.027466 | 0.14648 | -0.027466 | 0.064087 | 0.09613 | 0.07782 | -0.050354 | 0.068665 | 0.16022 | 0.09613 | 0.16022 | 121.3715 | -0.81482 | -0.79651 | 121.5454 | 121.463 | 121.3715 | 0.091553 | 0 | 121.3486 | -0.74616 | -0.75531 | 121.5591 | 121.5591 | 121.4951 | 0.21057 | 0.14648 | 0.17395 | 0.054932 | 0.21057 | 0.11902 | 0.036621 | 0.12817 | 121.4081 | 121.4767 | -0.85144 | -0.87433 | 121.4264 | 121.4676 | 121.3303 | 121.4951
6300.2656 | 122.4518 | -121.4447 | 0.85602 | -0.097427 | -0.038544 | -0.00061317 | 0.019519 | -0.00020513 | -0.01117 | -0.0042959 | -0.1077 | 0.024323 | 0.017921 | -0.0003695 | -0.019224 | 0.027621 | -0.0045117 | -0.11902 | 0.059509 | -0.073242 | -0.059509 | 0.018311 | -0.091553 | 0.004578 | -0.027466 | 0.11902 | -0.07782 | 0 | 0.10529 | 0.045776 | 0.091553 | 121.3715 | -0.79651 | -0.91553 | 121.463 | 121.4493 | 121.3531 | 0.07782 | -0.018311 | 121.3669 | -0.737 | -0.85602 | 121.55 | 121.5363 | 121.4905 | 0.16937 | 0.1236 | 0.091553 | 0.013733 | 0.18311 | 0.07782 | 0.13275 | 0.19684 | 121.5042 | 121.5637 | -0.92926 | -0.93384 | 121.3852 | 121.4447 | 121.3257 | 121.4172
6302 | 122.493 | -121.4401 | 0.83771 | -0.18135 | -0.039612 | -0.0014676 | 0.018023 | 0.00086307 | -0.011598 | -0.0062185 | -0.025299 | 0.023469 | 0.01493 | -0.0091281 | -0.019865 | 0.025912 | -0.00088011 | -0.10986 | 0.022888 | -0.045776 | -0.018311 | 0.11444 | -0.068665 | 0.059509 | 0.032043 | 0.07782 | -0.068665 | 0.027466 | 0.1236 | 0.064087 | 0.12817 | 121.3943 | -0.81482 | -0.85602 | 121.5546 | 121.4996 | 121.3715 | 0.10528 | -0.022889 | 121.3715 | -0.75989 | -0.81024 | 121.5637 | 121.5683 | 121.5042 | 0.19684 | 0.13275 | 0.16022 | 0.027465 | 0.19226 | 0.096131 | 0.068664 | 0.14649 | 121.463 | 121.5179 | -0.88348 | -0.90637 | 121.4218 | 121.4676 | 121.3303 | 121.4722
6303.7344 | 122.4152 | -121.4813 | 0.88348 | -0.13557 | -0.041748 | -0.0014676 | 0.018664 | -0.0021277 | -0.014161 | -0.0057913 | -0.074127 | 0.022614 | 0.014503 | -0.010837 | -0.019438 | 0.025272 | -0.0036573 | -0.15106 | 0.059509 | -0.086975 | -0.10986 | -0.022888 | -0.11902 | -0.009155 | -0.07782 | 0.11902 | -0.082397 | -0.054932 | 0.054932 | -0.009155 | 0.064087 | 121.3943 | -0.82398 | -0.99335 | 121.4584 | 121.4722 | 121.3623 | 0.07782 | -0.032044 | 121.3989 | -0.76447 | -0.93842 | 121.5363 | 121.5454 | 121.4722 | 0.14648 | 0.073242 | 0.064087 | -0.022888 | 0.13733 | 0.027465 | 0.14648 | 0.20142 | 121.5408 | 121.6003 | -0.97046 | -0.96588 | 121.3715 | 121.4264 | 121.3303 | 121.4035
6305.4375 | 122.4609 | -121.4493 | 0.8194 | -0.15083 | -0.038971 | 2.7834e-05 | 0.019946 | 0.0042811 | -0.010102 | -0.0051505 | -0.1077 | 0.023041 | 0.015144 | -0.014469 | -0.019224 | 0.02634 | -0.0032299 | -0.12817 | 0.045776 | -0.086975 | -0.09613 | 0.009155 | -0.12817 | -0.004578 | -0.022888 | 0.10986 | -0.086975 | 0.013733 | 0.07782 | 0.032043 | 0.09613 | 121.3623 | -0.77362 | -0.91553 | 121.4584 | 121.4447 | 121.3211 | 0.082397 | -0.041199 | 121.3623 | -0.70953 | -0.80566 | 121.5271 | 121.5454 | 121.4813 | 0.1831 | 0.11902 | 0.09613 | -0.009155 | 0.16479 | 0.10071 | 0.13275 | 0.19684 | 121.4951 | 121.5591 | -0.90637 | -0.90637 | 121.3531 | 121.463 | 121.3211 | 121.4264
6307.1406 | 122.4518 | -121.4447 | 0.82398 | -0.15846 | -0.038544 | -0.00061317 | 0.019946 | 0.0034265 | -0.011811 | -0.0055777 | -0.1077 | 0.023896 | 0.015144 | -0.011692 | -0.019224 | 0.026981 | -0.0040845 | -0.09613 | 0.054932 | -0.068665 | -0.032043 | 0.054932 | -0.086975 | 0.027466 | 0.013733 | 0.11444 | -0.068665 | -0.004578 | 0.091553 | 0.041199 | 0.10071 | 121.376 | -0.76904 | -0.85602 | 121.4996 | 121.4722 | 121.3577 | 0.096131 | -0.01831 | 121.376 | -0.70953 | -0.82855 | 121.5363 | 121.5454 | 121.4859 | 0.16937 | 0.10986 | 0.1236 | 0.036622 | 0.16022 | 0.064087 | 0.1236 | 0.18311 | 121.4996 | 121.5591 | -0.89264 | -0.89264 | 121.4127 | 121.4401 | 121.3486 | 121.4584
6308.8594 | 122.4197 | -121.4722 | 0.82855 | -0.18898 | -0.038544 | 0.001523 | 0.020587 | -0.0017005 | -0.012666 | -0.0032277 | -0.10464 | 0.023896 | 0.016426 | -0.0134 | -0.018797 | 0.02634 | -0.0021619 | -0.13275 | 0.059509 | -0.068665 | -0.11444 | -0.032043 | -0.16022 | -0.041199 | -0.086975 | 0.1236 | -0.086975 | -0.041199 | 0.032043 | -0.032043 | 0.068665 | 121.4035 | -0.76904 | -0.94299 | 121.4401 | 121.431 | 121.312 | 0.027466 | -0.091552 | 121.3852 | -0.70496 | -0.86975 | 121.5042 | 121.5408 | 121.4401 | 0.15564 | 0.054932 | 0.036622 | -0.045776 | 0.11902 | 0.045776 | 0.12817 | 0.21057 | 121.5317 | 121.5958 | -0.89722 | -0.91553 | 121.3577 | 121.431 | 121.3394 | 121.3852
6310.6094 | 122.4289 | -121.4676 | 0.85144 | -0.12032 | -0.041962 | -0.0010404 | 0.016314 | 0.00043587 | -0.01352 | -0.0053641 | -0.013092 | 0.023041 | 0.015144 | -0.017673 | -0.01901 | 0.024844 | -0.0013073 | -0.086975 | 0.004578 | -0.045776 | -0.045776 | 0.082397 | -0.032043 | 0.045776 | -0.018311 | 0.09613 | -0.073242 | -0.059509 | 0.068665 | 0.009155 | 0.059509 | 121.4218 | -0.84686 | -0.89722 | 121.55 | 121.5134 | 121.4355 | 0.091552 | 0.013733 | 121.3943 | -0.75531 | -0.91095 | 121.5363 | 121.5271 | 121.4767 | 0.13275 | 0.082397 | 0.12817 | 0 | 0.14191 | 0.013733 | 0.050354 | 0.16937 | 121.4722 | 121.5637 | -0.89722 | -0.92468 | 121.4218 | 121.4081 | 121.3806 | 121.4493
6312.2969 | 122.5296 | -121.4355 | 0.82398 | -0.20424 | -0.037049 | 0.001523 | 0.017596 | -0.0046911 | -0.01117 | -0.0042959 | -0.037506 | 0.022828 | 0.015571 | -0.017032 | -0.021147 | 0.026981 | -0.0066479 | -0.054932 | 0.018311 | -0.059509 | 0.032043 | 0.14648 | -0.022888 | 0.082397 | 0.091553 | 0.082397 | -0.036621 | 0.064087 | 0.16479 | 0.10071 | 0.15106 | 121.376 | -0.80566 | -0.79193 | 121.582 | 121.5179 | 121.4127 | 0.14191 | 0.036621 | 121.3989 | -0.74158 | -0.75989 | 121.6003 | 121.5866 | 121.5363 | 0.18768 | 0.13733 | 0.20599 | 0.091552 | 0.20142 | 0.10071 | 0.07782 | 0.11902 | 121.4539 | 121.5179 | -0.88348 | -0.8606 | 121.4676 | 121.4996 | 121.3806 | 121.5271
6314 | 122.5662 | -121.4218 | 0.80109 | -0.19661 | -0.041321 | -0.001254 | 0.018237 | 0.0012903 | -0.011598 | -0.0075003 | 0.011322 | 0.022828 | 0.013435 | -0.0134 | -0.019651 | 0.024844 | -0.0087841 | -0.10986 | 0.018311 | -0.064087 | -0.032043 | 0.091553 | -0.036621 | 0.050354 | 0.027466 | 0.086975 | -0.068665 | 0.036621 | 0.14648 | 0.11444 | 0.15106 | 121.3577 | -0.78277 | -0.83313 | 121.5134 | 121.4722 | 121.3852 | 0.11444 | 0.027466 | 121.3531 | -0.71411 | -0.76446 | 121.5683 | 121.5729 | 121.5363 | 0.21973 | 0.18311 | 0.15564 | 0.032044 | 0.21515 | 0.10529 | 0.082398 | 0.15564 | 121.4401 | 121.5088 | -0.86517 | -0.86975 | 121.3898 | 121.4584 | 121.312 | 121.4493
6315.7031 | 122.4335 | -121.4722 | 0.81482 | -0.16609 | -0.037049 | 0.0017368 | 0.021441 | -0.0019141 | -0.011384 | -0.0042959 | -0.11685 | 0.023255 | 0.014717 | -0.01276 | -0.020292 | 0.026981 | -0.00066651 | -0.086975 | 0.041199 | -0.082397 | -0.036621 | 0.045776 | -0.086975 | 0.013733 | 0 | 0.10529 | -0.082397 | -0.013733 | 0.059509 | 0 | 0.091553 | 121.3898 | -0.77362 | -0.85144 | 121.5179 | 121.4859 | 121.3852 | 0.09613 | -0.004578 | 121.3898 | -0.70953 | -0.82855 | 121.5317 | 121.5637 | 121.4722 | 0.17395 | 0.082397 | 0.12817 | 0.045776 | 0.14191 | 0.068664 | 0.1236 | 0.18768 | 121.5134 | 121.5775 | -0.89722 | -0.89722 | 121.4355 | 121.4584 | 121.3852 | 121.4722
6317.4062 | 122.3969 | -121.4493 | 0.84228 | -0.23476 | -0.039612 | 0.00045503 | 0.021014 | 0.00043587 | -0.012239 | -0.0042959 | -0.11075 | 0.024537 | 0.01258 | -0.0078463 | -0.018369 | 0.025272 | -0.0034435 | -0.13275 | 0.041199 | -0.073242 | -0.09613 | -0.027466 | -0.16479 | -0.036621 | -0.09613 | 0.10986 | -0.086975 | -0.068665 | 0.013733 | -0.054932 | 0.050354 | 121.376 | -0.80109 | -0.93841 | 121.4218 | 121.4127 | 121.2845 | 0.036621 | -0.091553 | 121.3623 | -0.73242 | -0.91095 | 121.463 | 121.4996 | 121.3943 | 0.13733 | 0.032043 | 0.045776 | -0.022888 | 0.10071 | 0.01831 | 0.11444 | 0.19684 | 121.4905 | 121.5591 | -0.91553 | -0.92926 | 121.3531 | 121.3806 | 121.3165 | 121.3531
6319.125 | 122.5525 | -121.4539 | 0.82398 | -0.17372 | -0.042176 | -0.00061317 | 0.015887 | 0.0012903 | -0.01117 | -0.0064321 | 0.0021667 | 0.022401 | 0.017066 | -0.016818 | -0.020292 | 0.024631 | -0.0036573 | -0.073242 | 0.004578 | -0.045776 | 0.027466 | 0.17395 | 0.018311 | 0.10529 | 0.10071 | 0.059509 | -0.064087 | 0.050354 | 0.19226 | 0.13733 | 0.15106 | 121.4081 | -0.8194 | -0.79651 | 121.6278 | 121.5591 | 121.4722 | 0.15106 | 0.064087 | 121.3898 | -0.76447 | -0.77362 | 121.6461 | 121.6049 | 121.5912 | 0.21515 | 0.20142 | 0.21973 | 0.073242 | 0.25635 | 0.11444 | 0.050354 | 0.1236 | 121.4584 | 121.5134 | -0.86975 | -0.88806 | 121.4813 | 121.5042 | 121.3806 | 121.5546
6320.8281 | 122.5433 | -121.4172 | 0.78278 | -0.21187 | -0.037903 | 0.0010958 | 0.019091 | 0.0017175 | -0.010743 | -0.0040823 | -0.064972 | 0.022187 | 0.014289 | -0.012332 | -0.021574 | 0.026126 | -0.0042981 | -0.050354 | 0.027466 | -0.027466 | 0.032043 | 0.14191 | -0.045776 | 0.086975 | 0.10071 | 0.068665 | -0.045776 | 0.091553 | 0.17395 | 0.10986 | 0.16937 | 121.3898 | -0.75531 | -0.75073 | 121.5591 | 121.5042 | 121.3715 | 0.11444 | -0.01831 | 121.3715 | -0.71411 | -0.69122 | 121.5912 | 121.5866 | 121.5271 | 0.21515 | 0.15564 | 0.16937 | 0.059509 | 0.21973 | 0.13733 | 0.054932 | 0.11444 | 121.4447 | 121.4859 | -0.81024 | -0.82855 | 121.4493 | 121.5088 | 121.3669 | 121.5179
6322.5469 | 122.4564 | -121.4905 | 0.8194 | -0.18135 | -0.041962 | -0.0016812 | 0.022937 | 0.0047083 | -0.012025 | -0.0032277 | -0.1077 | 0.023469 | 0.015571 | -0.011478 | -0.021787 | 0.024844 | -0.0049389 | -0.10071 | 0.036621 | -0.068665 | -0.036621 | 0.068665 | -0.082397 | 0.036621 | 0.018311 | 0.11444 | -0.064087 | 0.022888 | 0.086975 | 0.041199 | 0.07782 | 121.4218 | -0.78278 | -0.85602 | 121.5591 | 121.5271 | 121.4081 | 0.10529 | -0.013732 | 121.4264 | -0.70496 | -0.79651 | 121.5775 | 121.5683 | 121.5317 | 0.14191 | 0.10529 | 0.13733 | 0.032044 | 0.15106 | 0.086975 | 0.10529 | 0.17853 | 121.5271 | 121.6049 | -0.88806 | -0.88348 | 121.4539 | 121.5134 | 121.3898 | 121.5088
6324.25 | 122.5662 | -121.4584 | 0.81024 | -0.15846 | -0.041107 | -0.0025358 | 0.018023 | 0.0010767 | -0.011811 | -0.0042959 | 0.0082703 | 0.021973 | 0.015785 | -0.012973 | -0.022642 | 0.024204 | -0.0070751 | -0.073242 | 0.009155 | -0.050354 | 0.013733 | 0.15106 | 0.027466 | 0.11902 | 0.10071 | 0.068665 | -0.050354 | 0.073242 | 0.20142 | 0.15106 | 0.16022 | 121.4081 | -0.80109 | -0.79651 | 121.6095 | 121.5775 | 121.4859 | 0.16937 | 0.07782 | 121.4081 | -0.74158 | -0.737 | 121.6599 | 121.6187 | 121.6095 | 0.21057 | 0.20142 | 0.20142 | 0.064087 | 0.25177 | 0.1236 | 0.059509 | 0.11902 | 121.4676 | 121.5271 | -0.8606 | -0.8606 | 121.4722 | 121.5317 | 121.3852 | 121.5591
6325.9531 | 122.5342 | -121.4676 | 0.78278 | -0.25002 | -0.038544 | 0.00066863 | 0.017596 | 0.0021447 | -0.011598 | -0.0062185 | -0.040558 | 0.022828 | 0.016212 | -0.014255 | -0.022215 | 0.025912 | -0.0025891 | -0.064087 | -0.004578 | -0.032043 | 0.022888 | 0.15106 | -0.022888 | 0.086975 | 0.07782 | 0.064087 | -0.059509 | 0.073242 | 0.16022 | 0.091553 | 0.16022 | 121.4355 | -0.78735 | -0.75989 | 121.6187 | 121.5546 | 121.4447 | 0.11902 | 0.009155 | 121.4081 | -0.71869 | -0.70953 | 121.6278 | 121.6278 | 121.5591 | 0.21973 | 0.15106 | 0.18311 | 0.054931 | 0.21973 | 0.13275 | 0.027465 | 0.1236 | 121.463 | 121.5317 | -0.81482 | -0.84229 | 121.4905 | 121.5408 | 121.4035 | 121.5454
6327.6562 | 122.58 | -121.4355 | 0.80109 | -0.17372 | -0.04068 | -0.00061317 | 0.018023 | -0.0027685 | -0.012879 | -0.0053641 | -0.01004 | 0.023682 | 0.013221 | -0.011692 | -0.018583 | 0.025485 | -0.0045117 | -0.068665 | 0.009155 | -0.054932 | 0.018311 | 0.16022 | 0.018311 | 0.1236 | 0.11444 | 0.07782 | -0.050354 | 0.082397 | 0.21057 | 0.14648 | 0.18768 | 121.3806 | -0.79193 | -0.78277 | 121.5958 | 121.5591 | 121.4539 | 0.17853 | 0.073243 | 121.3852 | -0.72327 | -0.71869 | 121.6461 | 121.6232 | 121.582 | 0.23804 | 0.19684 | 0.21515 | 0.073243 | 0.26093 | 0.13275 | 0.064087 | 0.12817 | 121.4447 | 121.5134 | -0.85602 | -0.85144 | 121.4539 | 121.5179 | 121.3669 | 121.55
6329.3906 | 122.5662 | -121.463 | 0.80109 | -0.18135 | -0.041107 | -0.00082677 | 0.017169 | 8.47e-06 | -0.012239 | -0.0055777 | -0.019196 | 0.023255 | 0.013435 | -0.020877 | -0.022001 | 0.024417 | -0.0036573 | -0.09613 | 0.013733 | -0.050354 | 0.009155 | 0.13733 | 0.009155 | 0.11444 | 0.09613 | 0.07782 | -0.054932 | 0.073242 | 0.19226 | 0.13733 | 0.16022 | 121.4127 | -0.78735 | -0.79193 | 121.6003 | 121.5775 | 121.4722 | 0.16479 | 0.059509 | 121.4081 | -0.72327 | -0.72784 | 121.6553 | 121.6232 | 121.6003 | 0.21515 | 0.19226 | 0.18768 | 0.059509 | 0.24719 | 0.12817 | 0.064087 | 0.13275 | 121.4767 | 121.5408 | -0.85144 | -0.85602 | 121.4722 | 121.5363 | 121.3669 | 121.5591
6331.0938 | 122.5067 | -121.4584 | 0.81482 | -0.22713 | -0.03833 | 2.7834e-05 | 0.017596 | -0.0038367 | -0.011811 | -0.0049367 | -0.037506 | 0.023896 | 0.015785 | -0.013614 | -0.019865 | 0.024844 | -0.0038709 | -0.10986 | 0.027466 | -0.064087 | -0.036621 | 0.073242 | -0.07782 | 0.054932 | 0.018311 | 0.073242 | -0.059509 | 0.013733 | 0.10986 | 0.059509 | 0.09613 | 121.3943 | -0.78735 | -0.85144 | 121.5317 | 121.5134 | 121.3806 | 0.11902 | -0.013733 | 121.3989 | -0.74158 | -0.80109 | 121.5683 | 121.5546 | 121.5179 | 0.15564 | 0.11902 | 0.13733 | 0.027466 | 0.16937 | 0.073242 | 0.091553 | 0.13275 | 121.4859 | 121.5317 | -0.87891 | -0.87433 | 121.4218 | 121.4722 | 121.3486 | 121.4767
6332.7969 | 122.4243 | -121.4859 | 0.83771 | -0.17372 | -0.036835 | 0.00045503 | 0.020587 | -0.00063233 | -0.010743 | -0.0023733 | -0.15042 | 0.024964 | 0.012367 | -0.011051 | -0.021147 | 0.025912 | -0.0040845 | -0.14191 | 0.054932 | -0.082397 | -0.09613 | -0.045776 | -0.17395 | -0.068665 | -0.10529 | 0.11902 | -0.07782 | -0.036621 | 0.013733 | -0.032043 | 0.050354 | 121.4035 | -0.78278 | -0.93384 | 121.4401 | 121.4172 | 121.312 | 0.013732 | -0.091553 | 121.4081 | -0.71869 | -0.87433 | 121.4996 | 121.5363 | 121.4539 | 0.12817 | 0.045777 | 0.036621 | -0.013733 | 0.091553 | 0.041199 | 0.13733 | 0.19684 | 121.5408 | 121.6049 | -0.9201 | -0.91553 | 121.3898 | 121.4493 | 121.344 | 121.3806
6334.5156 | 122.5571 | -121.4493 | 0.80109 | -0.20424 | -0.037262 | 0.00045503 | 0.019732 | -0.0031957 | -0.011811 | -0.0034415 | -0.071076 | 0.022614 | 0.014289 | -0.01575 | -0.019865 | 0.026126 | -0.0034435 | -0.036621 | 0.022888 | -0.027466 | 0.027466 | 0.15106 | -0.032043 | 0.07782 | 0.10529 | 0.050354 | -0.041199 | 0.082397 | 0.16479 | 0.10529 | 0.16022 | 121.4218 | -0.7782 | -0.77362 | 121.6003 | 121.5271 | 121.4172 | 0.10529 | -0.004577 | 121.4081 | -0.75073 | -0.71869 | 121.6141 | 121.6095 | 121.5546 | 0.20142 | 0.14649 | 0.17853 | 0.054932 | 0.20599 | 0.1236 | 0.050354 | 0.091553 | 121.4722 | 121.4996 | -0.82855 | -0.84228 | 121.4767 | 121.5317 | 121.4127 | 121.5546
6336.2188 | 122.4289 | -121.4813 | 0.81024 | -0.2195 | -0.037903 | 0.0013094 | 0.022296 | -0.0014867 | -0.01117 | -0.0025869 | -0.12296 | 0.022828 | 0.014717 | -0.0078463 | -0.019651 | 0.025058 | -0.0040845 | -0.14648 | 0.054932 | -0.086975 | -0.10986 | -0.027466 | -0.17853 | -0.041199 | -0.091553 | 0.11444 | -0.068665 | -0.059509 | 0.013733 | -0.036621 | 0.050354 | 121.3943 | -0.75531 | -0.92011 | 121.4539 | 121.4401 | 121.3028 | 0.045776 | -0.091553 | 121.4127 | -0.6958 | -0.86975 | 121.4951 | 121.5317 | 121.4447 | 0.11902 | 0.032044 | 0.059509 | -0.022888 | 0.082398 | 0.009156 | 0.14191 | 0.18311 | 121.5363 | 121.5958 | -0.89722 | -0.87891 | 121.3715 | 121.4218 | 121.3348 | 121.3898
6337.9375 | 122.3969 | -121.4996 | 0.82855 | -0.17372 | -0.037689 | 0.00066863 | 0.020373 | 0.0015039 | -0.012025 | -0.0030141 | -0.12296 | 0.022614 | 0.014289 | -0.011264 | -0.01901 | 0.025699 | -0.0015209 | -0.13733 | 0.059509 | -0.07782 | -0.10071 | -0.027466 | -0.16479 | -0.041199 | -0.091553 | 0.11902 | -0.086975 | -0.045776 | 0.032043 | -0.050354 | 0.059509 | 121.4218 | -0.76904 | -0.92926 | 121.4722 | 121.4584 | 121.3348 | 0.036621 | -0.086975 | 121.4127 | -0.70953 | -0.87433 | 121.5317 | 121.5591 | 121.4493 | 0.14648 | 0.036621 | 0.050354 | -0.022888 | 0.11902 | 0.041199 | 0.13733 | 0.20599 | 121.5591 | 121.6187 | -0.90637 | -0.91553 | 121.3989 | 121.4539 | 121.3623 | 121.4081
6339.6562 | 122.5388 | -121.4767 | 0.7782 | -0.19661 | -0.040894 | 0.002164 | 0.019519 | -0.00063233 | -0.010316 | -0.0034415 | -0.080231 | 0.024323 | 0.015998 | -0.0091281 | -0.019865 | 0.026981 | 0.00082889 | -0.11902 | 0.045776 | -0.059509 | -0.041199 | 0.059509 | -0.09613 | 0.022888 | 0.045776 | 0.086975 | -0.050354 | 0.059509 | 0.13733 | 0.07782 | 0.15106 | 121.4172 | -0.73242 | -0.8194 | 121.5363 | 121.4996 | 121.3806 | 0.082397 | -0.036621 | 121.4264 | -0.69122 | -0.71869 | 121.6141 | 121.6278 | 121.5546 | 0.20142 | 0.12817 | 0.11902 | 0.01831 | 0.18768 | 0.10986 | 0.10528 | 0.13733 | 121.5225 | 121.5637 | -0.83771 | -0.82855 | 121.4355 | 121.5363 | 121.3577 | 121.5225
6341.3594 | 122.4747 | -121.5179 | 0.80566 | -0.12032 | -0.040253 | -0.00061317 | 0.020373 | 0.0049219 | -0.012025 | -0.0032277 | -0.1138 | 0.02176 | 0.015357 | -0.0095553 | -0.020506 | 0.025699 | -0.00045291 | -0.10071 | 0.041199 | -0.082397 | -0.041199 | 0.064087 | -0.07782 | 0.032043 | 0.004578 | 0.11444 | -0.064087 | -0.009155 | 0.068665 | 0 | 0.086975 | 121.4355 | -0.76447 | -0.84686 | 121.582 | 121.55 | 121.4401 | 0.11444 | 0.004577 | 121.4539 | -0.69122 | -0.81482 | 121.5866 | 121.6049 | 121.5179 | 0.15106 | 0.064087 | 0.14648 | 0.041198 | 0.13275 | 0.054932 | 0.1236 | 0.17853 | 121.5591 | 121.6324 | -0.88806 | -0.86975 | 121.4767 | 121.5088 | 121.4172 | 121.5225
6343.0625 | 122.5845 | -121.4722 | 0.80109 | -0.16609 | -0.041962 | -0.0021084 | 0.015674 | 0.0010767 | -0.01352 | -0.0032277 | -0.0008851 | 0.020905 | 0.013435 | -0.016818 | -0.020719 | 0.026126 | -0.00088011 | -0.059509 | 0.009155 | -0.050354 | 0.027466 | 0.1831 | 0.027466 | 0.1236 | 0.09613 | 0.091553 | -0.050354 | 0.068665 | 0.1831 | 0.15564 | 0.15106 | 121.4218 | -0.79193 | -0.77362 | 121.6553 | 121.5958 | 121.4996 | 0.17395 | 0.07782 | 121.4218 | -0.70953 | -0.73242 | 121.6553 | 121.6232 | 121.6278 | 0.20142 | 0.20599 | 0.23346 | 0.07782 | 0.23346 | 0.11902 | 0.059509 | 0.14191 | 121.4813 | 121.5637 | -0.85144 | -0.85144 | 121.4996 | 121.5408 | 121.4127 | 121.5683
6344.7656 | 122.5296 | -121.4722 | 0.78278 | -0.16609 | -0.039612 | -0.00082677 | 0.019732 | 0.00064947 | -0.011598 | -0.0036551 | -0.049713 | 0.021332 | 0.013435 | -0.01276 | -0.019651 | 0.028476 | -0.0051525 | -0.068665 | 0.013733 | -0.041199 | 0 | 0.13275 | -0.045776 | 0.068665 | 0.082397 | 0.07782 | -0.045776 | 0.045776 | 0.13275 | 0.086975 | 0.13275 | 121.431 | -0.76904 | -0.78278 | 121.6049 | 121.5408 | 121.4264 | 0.10986 | -0.004577 | 121.4264 | -0.70496 | -0.737 | 121.6049 | 121.6049 | 121.5591 | 0.17853 | 0.13275 | 0.17395 | 0.041199 | 0.17853 | 0.091552 | 0.054932 | 0.1236 | 121.4859 | 121.55 | -0.82398 | -0.82855 | 121.4722 | 121.5179 | 121.4035 | 121.5546
6346.5 | 122.5708 | -121.4767 | 0.80566 | -0.19661 | -0.040039 | 2.7834e-05 | 0.017382 | -0.0010595 | -0.013947 | -0.0077139 | -0.0008851 | 0.021973 | 0.013008 | -0.021305 | -0.021147 | 0.024417 | -0.00045291 | -0.082397 | 0.013733 | -0.054932 | 0.041199 | 0.18768 | 0.032043 | 0.12817 | 0.12817 | 0.086975 | -0.036621 | 0.073242 | 0.1831 | 0.15106 | 0.15106 | 121.4218 | -0.79193 | -0.76447 | 121.6644 | 121.6049 | 121.5088 | 0.18311 | 0.086975 | 121.4401 | -0.71869 | -0.73242 | 121.6599 | 121.6278 | 121.6278 | 0.18768 | 0.18768 | 0.24261 | 0.096131 | 0.21973 | 0.10986 | 0.068665 | 0.1236 | 121.4905 | 121.5637 | -0.8606 | -0.84229 | 121.5179 | 121.55 | 121.3943 | 121.6049
6348.2188 | 122.4655 | -121.5042 | 0.8194 | -0.15846 | -0.038117 | -0.0016812 | 0.0208 | 0.0021447 | -0.01053 | -0.0034415 | -0.11685 | 0.02475 | 0.01493 | -0.012546 | -0.021147 | 0.026126 | -0.0047253 | -0.07782 | 0.050354 | -0.054932 | -0.022888 | 0.068665 | -0.068665 | 0.013733 | 0.027466 | 0.11902 | -0.082397 | 0.009155 | 0.073242 | 0.022888 | 0.086975 | 121.4493 | -0.76904 | -0.84229 | 121.5729 | 121.5179 | 121.4355 | 0.068665 | -0.013733 | 121.4218 | -0.70038 | -0.81024 | 121.5775 | 121.5912 | 121.5271 | 0.16937 | 0.10528 | 0.1236 | 0.032044 | 0.15564 | 0.091552 | 0.10529 | 0.20142 | 121.5546 | 121.6232 | -0.87433 | -0.90179 | 121.4813 | 121.5134 | 121.4264 | 121.5317
6349.9219 | 122.5662 | -121.4722 | 0.80109 | -0.12032 | -0.041962 | 2.7834e-05 | 0.016528 | -0.0049047 | -0.012452 | -0.0038687 | -0.0008851 | 0.022401 | 0.014076 | -0.016605 | -0.019651 | 0.02399 | -0.0015209 | -0.07782 | 0.004578 | -0.027466 | 0.032043 | 0.16479 | 0.013733 | 0.11444 | 0.086975 | 0.091553 | -0.045776 | 0.054932 | 0.18768 | 0.13733 | 0.15564 | 121.4447 | -0.79651 | -0.76904 | 121.637 | 121.5866 | 121.4859 | 0.14191 | 0.041199 | 121.4264 | -0.70953 | -0.74615 | 121.6599 | 121.6278 | 121.6095 | 0.20142 | 0.18311 | 0.19226 | 0.059509 | 0.23346 | 0.10071 | 0.032044 | 0.13733 | 121.4767 | 121.5637 | -0.82855 | -0.84686 | 121.5042 | 121.5271 | 121.3943 | 121.5591
6351.6406 | 122.4884 | -121.5088 | 0.82398 | -0.12032 | -0.041962 | -0.00082677 | 0.021441 | -0.00041873 | -0.011384 | -0.0066457 | -0.086334 | 0.023041 | 0.01493 | -0.011264 | -0.019651 | 0.025912 | -0.0049389 | -0.091553 | 0.050354 | -0.059509 | -0.041199 | 0.050354 | -0.086975 | 0.022888 | -0.004578 | 0.12817 | -0.086975 | -0.004578 | 0.10529 | 0.036621 | 0.10529 | 121.4493 | -0.77362 | -0.86517 | 121.5591 | 121.5317 | 121.4218 | 0.082397 | -0.027466 | 121.4218 | -0.6958 | -0.82855 | 121.6141 | 121.6141 | 121.5454 | 0.19226 | 0.1236 | 0.10986 | 0.01831 | 0.19226 | 0.082397 | 0.10986 | 0.21515 | 121.5591 | 121.637 | -0.88348 | -0.91095 | 121.4676 | 121.5042 | 121.4172 | 121.5042
6353.3438 | 122.5662 | -121.4767 | 0.81482 | -0.18898 | -0.041321 | -0.0021084 | 0.016955 | 0.0012903 | -0.014802 | -0.0060049 | -0.016144 | 0.021973 | 0.016639 | -0.010837 | -0.020506 | 0.024844 | -0.0068615 | -0.073242 | 0.009155 | -0.050354 | 0.018311 | 0.16022 | 0.009155 | 0.091553 | 0.07782 | 0.07782 | -0.059509 | 0.054932 | 0.17853 | 0.1236 | 0.16022 | 121.4264 | -0.80566 | -0.79651 | 121.637 | 121.5683 | 121.4859 | 0.14191 | 0.059509 | 121.4172 | -0.737 | -0.75989 | 121.6553 | 121.637 | 121.6003 | 0.21973 | 0.1831 | 0.21057 | 0.068665 | 0.23804 | 0.11444 | 0.059509 | 0.13733 | 121.4859 | 121.5546 | -0.86517 | -0.87433 | 121.4951 | 121.5317 | 121.4035 | 121.5546
6355.0469 | 122.5433 | -121.4584 | 0.79651 | -0.2195 | -0.03833 | 0.003232 | 0.016742 | -0.0017005 | -0.011811 | -0.0019461 | -0.025299 | 0.022828 | 0.013008 | -0.014041 | -0.022428 | 0.026767 | -0.0068615 | -0.054932 | 0.022888 | -0.032043 | 0.036621 | 0.12817 | -0.027466 | 0.091553 | 0.10529 | 0.082397 | -0.045776 | 0.068665 | 0.17395 | 0.10529 | 0.16479 | 121.4264 | -0.77362 | -0.75989 | 121.5866 | 121.55 | 121.431 | 0.1236 | 0.004577 | 121.4127 | -0.71411 | -0.72784 | 121.6324 | 121.6232 | 121.5637 | 0.21057 | 0.15106 | 0.16022 | 0.068664 | 0.21973 | 0.11444 | 0.054931 | 0.12817 | 121.4813 | 121.5408 | -0.82855 | -0.84229 | 121.4951 | 121.5271 | 121.4035 | 121.5637
6356.7812 | 122.4518 | -121.5408 | 0.8194 | -0.11269 | -0.041321 | -0.0021084 | 0.01781 | -0.0021277 | -0.013734 | -0.0047231 | -0.046661 | 0.023682 | 0.014717 | -0.013187 | -0.020933 | 0.026126 | -0.0070751 | -0.10986 | 0.032043 | -0.054932 | -0.064087 | 0.054932 | -0.086975 | 0.013733 | -0.032043 | 0.11902 | -0.086975 | -0.045776 | 0.054932 | 0.004578 | 0.064087 | 121.4859 | -0.78735 | -0.88348 | 121.5958 | 121.5546 | 121.4539 | 0.068665 | -0.032043 | 121.4539 | -0.70038 | -0.86517 | 121.5958 | 121.6049 | 121.5454 | 0.15106 | 0.091553 | 0.10986 | -0.009155 | 0.14191 | 0.041199 | 0.086975 | 0.20599 | 121.5729 | 121.6599 | -0.87433 | -0.90637 | 121.4767 | 121.4951 | 121.431 | 121.5088
6358.5312 | 122.58 | -121.4722 | 0.77362 | -0.23476 | -0.038117 | 2.7834e-05 | 0.02016 | 0.0012903 | -0.01117 | -0.0081411 | -0.074127 | 0.022401 | 0.016212 | -0.019596 | -0.020933 | 0.02634 | -0.0079297 | -0.032043 | 0.004578 | -0.045776 | 0.013733 | 0.12817 | -0.032043 | 0.07782 | 0.10986 | 0.082397 | -0.054932 | 0.07782 | 0.16022 | 0.09613 | 0.17853 | 121.4264 | -0.76904 | -0.75989 | 121.6003 | 121.55 | 121.4401 | 0.1236 | 0.013733 | 121.4172 | -0.69122 | -0.6958 | 121.6324 | 121.6507 | 121.5683 | 0.23346 | 0.15106 | 0.17395 | 0.059509 | 0.21515 | 0.13275 | 0.050354 | 0.13733 | 121.4767 | 121.5546 | -0.8194 | -0.82855 | 121.4859 | 121.55 | 121.4401 | 121.582
6360.2344 | 122.4564 | -121.5317 | 0.81482 | -0.17372 | -0.039185 | 0.0010958 | 0.021228 | 0.0029993 | -0.01352 | -0.0051505 | -0.14127 | 0.023469 | 0.014289 | -0.017459 | -0.020506 | 0.027408 | -0.0034435 | -0.086975 | 0.050354 | -0.073242 | -0.054932 | 0.050354 | -0.091553 | 0.004578 | 0 | 0.10071 | -0.064087 | -0.022888 | 0.059509 | -0.036621 | 0.059509 | 121.4584 | -0.76446 | -0.86975 | 121.582 | 121.5363 | 121.4401 | 0.07782 | -0.018311 | 121.4676 | -0.71411 | -0.83771 | 121.5912 | 121.5912 | 121.4951 | 0.1236 | 0.027466 | 0.1236 | 0.01831 | 0.1236 | 0.041199 | 0.1236 | 0.1648 | 121.582 | 121.6324 | -0.88806 | -0.87891 | 121.4767 | 121.5088 | 121.4447 | 121.5317
6361.9531 | 122.5845 | -121.4859 | 0.80109 | -0.21187 | -0.041962 | -0.0016812 | 0.016101 | 0.0015039 | -0.012666 | -0.0053641 | 0.017425 | 0.022614 | 0.015571 | -0.015109 | -0.021147 | 0.025058 | -0.0051525 | -0.086975 | 0.009155 | -0.045776 | 0.027466 | 0.16022 | 0.018311 | 0.11902 | 0.082397 | 0.073242 | -0.054932 | 0.050354 | 0.19684 | 0.14191 | 0.16022 | 121.4401 | -0.79193 | -0.77362 | 121.6461 | 121.6049 | 121.5042 | 0.16479 | 0.064087 | 121.431 | -0.72784 | -0.75073 | 121.6827 | 121.6461 | 121.6278 | 0.21515 | 0.19684 | 0.20599 | 0.073242 | 0.25177 | 0.10529 | 0.054931 | 0.12817 | 121.4951 | 121.5591 | -0.84686 | -0.85602 | 121.5134 | 121.5363 | 121.3989 | 121.5683
6363.6719 | 122.5067 | -121.5271 | 0.82398 | -0.15083 | -0.040253 | -0.00018577 | 0.020373 | 0.0040675 | -0.013947 | -0.0055777 | -0.11075 | 0.023682 | 0.016212 | -0.010623 | -0.020078 | 0.025485 | -0.0017347 | -0.11444 | 0.045776 | -0.059509 | -0.064087 | 0.027466 | -0.082397 | 0.013733 | -0.004578 | 0.10529 | -0.073242 | 0 | 0.10529 | 0.041199 | 0.09613 | 121.4676 | -0.7782 | -0.88806 | 121.5546 | 121.5408 | 121.4447 | 0.073242 | -0.022888 | 121.4539 | -0.71869 | -0.82398 | 121.6324 | 121.6232 | 121.5683 | 0.16937 | 0.11444 | 0.086975 | -0.004578 | 0.17853 | 0.073242 | 0.10528 | 0.17853 | 121.5729 | 121.6324 | -0.88348 | -0.89722 | 121.463 | 121.5271 | 121.4127 | 121.5225
6365.375 | 122.5433 | -121.5179 | 0.78735 | -0.19661 | -0.03833 | -0.001254 | 0.018878 | -0.00063233 | -0.012239 | -0.0042959 | 0.0052185 | 0.023682 | 0.016426 | -0.014041 | -0.020292 | 0.025272 | -0.0028027 | -0.10986 | 0.009155 | -0.059509 | -0.045776 | 0.059509 | -0.068665 | 0.045776 | 0.009155 | 0.10529 | -0.068665 | 0 | 0.12817 | 0.086975 | 0.11444 | 121.4584 | -0.7782 | -0.83313 | 121.5775 | 121.5637 | 121.4493 | 0.10528 | -0.009156 | 121.4493 | -0.68207 | -0.78735 | 121.6461 | 121.6324 | 121.6049 | 0.18311 | 0.15564 | 0.11902 | 0.013733 | 0.19684 | 0.068665 | 0.068664 | 0.17395 | 121.5271 | 121.6232 | -0.84686 | -0.85602 | 121.4722 | 121.5179 | 121.4081 | 121.5271
6367.1094 | 122.5021 | -121.5225 | 0.80566 | -0.12794 | -0.039398 | -0.001254 | 0.016955 | 0.00064947 | -0.012239 | -0.0049367 | -0.071076 | 0.023255 | 0.014717 | -0.0059237 | -0.019865 | 0.026767 | -0.0042981 | -0.11902 | 0.036621 | -0.073242 | -0.054932 | 0.022888 | -0.082397 | 0.018311 | -0.022888 | 0.11902 | -0.068665 | -0.009155 | 0.10071 | 0.032043 | 0.09613 | 121.4493 | -0.76904 | -0.8606 | 121.5454 | 121.5408 | 121.4401 | 0.091553 | -0.009155 | 121.4539 | -0.68665 | -0.81482 | 121.6232 | 121.6187 | 121.5546 | 0.16479 | 0.10071 | 0.09613 | 0.01831 | 0.16937 | 0.05951 | 0.10986 | 0.18768 | 121.5591 | 121.6415 | -0.87891 | -0.87433 | 121.4676 | 121.5134 | 121.4035 | 121.4996
6368.8125 | 122.4884 | -121.5317 | 0.81482 | -0.17372 | -0.038544 | -0.0018948 | 0.016955 | -0.0014867 | -0.012239 | -0.0049367 | -0.019196 | 0.023682 | 0.016212 | -0.014469 | -0.017942 | 0.02634 | -0.0081433 | -0.07782 | 0.032043 | -0.064087 | -0.018311 | 0.10071 | -0.045776 | 0.064087 | 0.018311 | 0.09613 | -0.07782 | -0.032043 | 0.091553 | 0.022888 | 0.086975 | 121.4676 | -0.78278 | -0.83313 | 121.6324 | 121.5958 | 121.4859 | 0.12817 | 0.018311 | 121.4539 | -0.71869 | -0.84686 | 121.6232 | 121.6187 | 121.5546 | 0.16479 | 0.10071 | 0.1648 | 0.045776 | 0.16937 | 0.045777 | 0.09613 | 0.17395 | 121.5637 | 121.6278 | -0.87891 | -0.89264 | 121.5134 | 121.4996 | 121.4539 | 121.55
6370.5625 | 122.4884 | -121.5408 | 0.82398 | -0.097427 | -0.041321 | -0.0018948 | 0.019946 | 0.0042811 | -0.014588 | -0.0049367 | -0.080231 | 0.024323 | 0.015571 | -0.0084873 | -0.020506 | 0.025699 | -0.0038709 | -0.13733 | 0.068665 | -0.09613 | -0.10071 | -0.009155 | -0.12817 | -0.009155 | -0.086975 | 0.1236 | -0.09613 | -0.045776 | 0.059509 | 0.004578 | 0.073242 | 121.4447 | -0.75531 | -0.92468 | 121.5317 | 121.5317 | 121.4127 | 0.086975 | -0.032044 | 121.4447 | -0.70038 | -0.86975 | 121.6003 | 121.6141 | 121.5454 | 0.16937 | 0.10071 | 0.086975 | -0.004578 | 0.15564 | 0.050354 | 0.16479 | 0.21973 | 121.6095 | 121.6644 | -0.9201 | -0.9201 | 121.4401 | 121.4951 | 121.4035 | 121.4539
6372.2656 | 122.493 | -121.5454 | 0.81024 | -0.19661 | -0.039826 | -0.0021084 | 0.019519 | 0.00086307 | -0.012239 | -0.0051505 | -0.092438 | 0.021546 | 0.014503 | -0.0046421 | -0.019651 | 0.027194 | -0.0040845 | -0.11902 | 0.045776 | -0.086975 | -0.059509 | 0.032043 | -0.082397 | 0.013733 | -0.009155 | 0.10529 | -0.073242 | -0.009155 | 0.10529 | 0.032043 | 0.09613 | 121.4584 | -0.76447 | -0.86975 | 121.5775 | 121.5591 | 121.463 | 0.10071 | 0.004578 | 121.4722 | -0.70496 | -0.8194 | 121.6507 | 121.6415 | 121.5775 | 0.16937 | 0.10529 | 0.11902 | 0.027466 | 0.17853 | 0.064087 | 0.13275 | 0.17853 | 121.5912 | 121.6507 | -0.89722 | -0.88348 | 121.4859 | 121.5363 | 121.4264 | 121.5363
6373.9688 | 122.6028 | -121.4996 | 0.76446 | -0.12794 | -0.040467 | -0.00061317 | 0.01781 | -0.0042639 | -0.011384 | -0.0060049 | 0.020477 | 0.020905 | 0.015357 | -0.011692 | -0.019865 | 0.024417 | -0.0051525 | -0.10529 | 0.013733 | -0.045776 | -0.004578 | 0.13733 | -0.013733 | 0.10986 | 0.09613 | 0.09613 | -0.054932 | 0.068665 | 0.19684 | 0.14191 | 0.16479 | 121.4539 | -0.75073 | -0.76904 | 121.637 | 121.6095 | 121.4859 | 0.15564 | 0.032043 | 121.4447 | -0.66833 | -0.6958 | 121.6965 | 121.6644 | 121.6415 | 0.21973 | 0.19684 | 0.18311 | 0.041198 | 0.25177 | 0.1236 | 0.059509 | 0.15106 | 121.5134 | 121.5958 | -0.81024 | -0.8194 | 121.4951 | 121.5683 | 121.3943 | 121.5958
6375.6719 | 122.5891 | -121.4859 | 0.78735 | -0.2195 | -0.041107 | 2.7834e-05 | 0.019091 | -0.0010595 | -0.011384 | -0.0021597 | -0.089386 | 0.025605 | 0.014503 | -0.017459 | -0.019438 | 0.025912 | -0.0064343 | -0.091553 | 0.018311 | -0.054932 | 0.004578 | 0.11444 | -0.054932 | 0.073242 | 0.068665 | 0.07782 | -0.045776 | 0.07782 | 0.16479 | 0.09613 | 0.16479 | 121.431 | -0.76904 | -0.78278 | 121.6003 | 121.5591 | 121.431 | 0.12817 | 0 | 121.4401 | -0.70953 | -0.70953 | 121.6507 | 121.6507 | 121.582 | 0.21057 | 0.14191 | 0.16937 | 0.05951 | 0.21057 | 0.1236 | 0.073243 | 0.1236 | 121.5042 | 121.5637 | -0.84229 | -0.83313 | 121.4905 | 121.5637 | 121.3943 | 121.5546
6377.375 | 122.58 | -121.5042 | 0.78735 | -0.16609 | -0.039826 | -0.0038174 | 0.017596 | 0.00043587 | -0.012025 | -0.0040823 | -0.025299 | 0.022401 | 0.012153 | -0.011692 | -0.019865 | 0.023776 | -0.0030163 | -0.068665 | 0.009155 | -0.050354 | 0.027466 | 0.12817 | 0.009155 | 0.091553 | 0.07782 | 0.073242 | -0.073242 | 0.050354 | 0.16937 | 0.12817 | 0.14191 | 121.4539 | -0.7782 | -0.75989 | 121.6324 | 121.5958 | 121.5134 | 0.14191 | 0.059509 | 121.431 | -0.71411 | -0.737 | 121.6736 | 121.6461 | 121.6324 | 0.21515 | 0.20142 | 0.17853 | 0.07782 | 0.24261 | 0.1236 | 0.059509 | 0.14648 | 121.5134 | 121.5775 | -0.83771 | -0.8606 | 121.5317 | 121.5546 | 121.4355 | 121.582
6379.125 | 122.493 | -121.5408 | 0.80109 | -0.089798 | -0.04068 | -0.0023222 | 0.016955 | -0.0051183 | -0.012666 | -0.0055777 | -0.037506 | 0.02411 | 0.01493 | -0.015323 | -0.019224 | 0.022922 | -0.0051525 | -0.082397 | 0.022888 | -0.045776 | -0.018311 | 0.09613 | -0.036621 | 0.064087 | 0 | 0.091553 | -0.073242 | -0.036621 | 0.086975 | 0.018311 | 0.073242 | 121.4951 | -0.7782 | -0.8194 | 121.637 | 121.6049 | 121.5042 | 0.10986 | 0.009155 | 121.4676 | -0.70953 | -0.83771 | 121.6278 | 121.6141 | 121.5591 | 0.14648 | 0.091553 | 0.14191 | 0.027465 | 0.16022 | 0.036621 | 0.068664 | 0.16479 | 121.5637 | 121.6324 | -0.84686 | -0.87433 | 121.5225 | 121.5042 | 121.4584 | 121.5408
6380.8281 | 122.5983 | -121.5042 | 0.7782 | -0.20424 | -0.04068 | -0.0040312 | 0.017596 | -0.0010595 | -0.01352 | -0.0042959 | 0.0021667 | 0.023469 | 0.015785 | -0.010196 | -0.022001 | 0.024844 | -0.0019483 | -0.10071 | 0.027466 | -0.050354 | -0.009155 | 0.10529 | -0.022888 | 0.086975 | 0.050354 | 0.091553 | -0.050354 | 0.050354 | 0.16479 | 0.13275 | 0.15564 | 121.4539 | -0.75073 | -0.78735 | 121.6095 | 121.5912 | 121.4813 | 0.13733 | 0.027466 | 121.4539 | -0.68664 | -0.72784 | 121.669 | 121.6599 | 121.637 | 0.20599 | 0.18311 | 0.15564 | 0.041199 | 0.21515 | 0.10071 | 0.07782 | 0.14191 | 121.5317 | 121.5958 | -0.82855 | -0.82855 | 121.4951 | 121.5546 | 121.4035 | 121.5546
6382.5938 | 122.5754 | -121.5454 | 0.79193 | -0.1432 | -0.040467 | -0.00082677 | 0.01781 | -0.0014867 | -0.011811 | -0.0062185 | -0.040558 | 0.020264 | 0.015357 | -0.014896 | -0.021147 | 0.026767 | -0.0019483 | -0.073242 | 0 | -0.032043 | 0.032043 | 0.13733 | 0.004578 | 0.10986 | 0.073242 | 0.086975 | -0.054932 | 0.045776 | 0.17395 | 0.11444 | 0.14191 | 121.5134 | -0.79193 | -0.75989 | 121.6827 | 121.6553 | 121.55 | 0.14191 | 0.036621 | 121.4905 | -0.70496 | -0.74616 | 121.7194 | 121.6873 | 121.6599 | 0.19684 | 0.16937 | 0.16937 | 0.064086 | 0.22888 | 0.10071 | 0.032043 | 0.14191 | 121.5454 | 121.6324 | -0.82397 | -0.84686 | 121.5775 | 121.5912 | 121.4722 | 121.6187
6384.3438 | 122.5479 | -121.5363 | 0.78278 | -0.16609 | -0.039398 | -0.00039957 | 0.01781 | -0.0040503 | -0.012452 | -0.0057913 | -0.016144 | 0.023255 | 0.014289 | -0.016818 | -0.022856 | 0.026126 | -0.0023755 | -0.10986 | 0.032043 | -0.064087 | -0.036621 | 0.073242 | -0.059509 | 0.050354 | 0.009155 | 0.09613 | -0.068665 | 0.013733 | 0.13275 | 0.07782 | 0.13275 | 121.4722 | -0.75073 | -0.8194 | 121.6095 | 121.5866 | 121.4767 | 0.11444 | 0.004578 | 121.4676 | -0.68665 | -0.76904 | 121.669 | 121.669 | 121.6141 | 0.20142 | 0.14649 | 0.13733 | 0.027466 | 0.20142 | 0.082398 | 0.09613 | 0.16479 | 121.5683 | 121.6324 | -0.84686 | -0.85144 | 121.4996 | 121.55 | 121.4264 | 121.5454
6386.0469 | 122.5845 | -121.4996 | 0.76904 | -0.20424 | -0.038117 | 0.00045503 | 0.019519 | 0.0019311 | -0.011811 | -0.0045095 | -0.06192 | 0.023896 | 0.014076 | -0.014469 | -0.020719 | 0.026981 | -0.0036573 | -0.036621 | 0.004578 | -0.036621 | 0.041199 | 0.13733 | -0.036621 | 0.091553 | 0.09613 | 0.073242 | -0.050354 | 0.082397 | 0.17853 | 0.10986 | 0.15106 | 121.463 | -0.76447 | -0.72784 | 121.637 | 121.5912 | 121.463 | 0.12817 | 0 | 121.4493 | -0.6958 | -0.68665 | 121.6782 | 121.6507 | 121.6095 | 0.20142 | 0.16022 | 0.17395 | 0.07782 | 0.22888 | 0.13275 | 0.041199 | 0.1236 | 121.5042 | 121.5729 | -0.80566 | -0.8194 | 121.5408 | 121.582 | 121.463 | 121.5958
6387.7344 | 122.5845 | -121.5363 | 0.78278 | -0.21187 | -0.039612 | -0.00082677 | 0.018451 | -0.0017005 | -0.012666 | -0.0028005 | -0.028351 | 0.021973 | 0.015357 | -0.01575 | -0.022001 | 0.025699 | -0.0062207 | -0.073242 | 0.004578 | -0.041199 | 0.036621 | 0.14191 | 0 | 0.10071 | 0.082397 | 0.082397 | -0.036621 | 0.059509 | 0.17853 | 0.13275 | 0.14648 | 121.4951 | -0.7782 | -0.74616 | 121.6782 | 121.637 | 121.5363 | 0.14191 | 0.041199 | 121.4996 | -0.70038 | -0.72327 | 121.7148 | 121.6827 | 121.669 | 0.18311 | 0.16937 | 0.18311 | 0.07782 | 0.21515 | 0.09613 | 0.045777 | 0.11902 | 121.5408 | 121.6187 | -0.82398 | -0.8194 | 121.5729 | 121.5958 | 121.463 | 121.6187
6389.4531 | 122.58 | -121.5179 | 0.76904 | -0.18135 | -0.040039 | 2.7834e-05 | 0.021228 | -0.0014867 | -0.01117 | -0.0032277 | -0.092438 | 0.020692 | 0.014503 | -0.017459 | -0.02136 | 0.025485 | -0.0045117 | -0.09613 | 0.032043 | -0.064087 | -0.018311 | 0.073242 | -0.082397 | 0.032043 | 0.050354 | 0.07782 | -0.054932 | 0.068665 | 0.15564 | 0.082397 | 0.15106 | 121.4539 | -0.737 | -0.78735 | 121.5912 | 121.55 | 121.4355 | 0.09613 | -0.01831 | 121.463 | -0.69122 | -0.70038 | 121.6736 | 121.669 | 121.6003 | 0.20599 | 0.13733 | 0.13733 | 0.045776 | 0.21057 | 0.1236 | 0.09613 | 0.13275 | 121.55 | 121.5958 | -0.83313 | -0.82398 | 121.4996 | 121.5866 | 121.4218 | 121.5683
6391.1719 | 122.5204 | -121.5454 | 0.78735 | -0.21187 | -0.039185 | -0.0021084 | 0.021228 | 0.0012903 | -0.013734 | -0.0075003 | -0.11685 | 0.02411 | 0.013862 | -0.0093417 | -0.020078 | 0.026767 | -0.0040845 | -0.10529 | 0.050354 | -0.07782 | -0.027466 | 0.082397 | -0.07782 | 0.036621 | 0.022888 | 0.11444 | -0.082397 | 0.013733 | 0.09613 | 0.036621 | 0.09613 | 121.4676 | -0.737 | -0.81482 | 121.6278 | 121.582 | 121.4676 | 0.11444 | 0 | 121.463 | -0.67291 | -0.77362 | 121.6415 | 121.6415 | 121.582 | 0.17853 | 0.11902 | 0.16022 | 0.050354 | 0.17853 | 0.09613 | 0.12817 | 0.19684 | 121.5958 | 121.6599 | -0.86517 | -0.86975 | 121.5179 | 121.5591 | 121.4401 | 121.5683
6392.875 | 122.5983 | -121.4905 | 0.7782 | -0.1432 | -0.041107 | -0.0016812 | 0.015246 | -0.0036231 | -0.011811 | -0.0034415 | -0.013092 | 0.023896 | 0.013221 | -0.01575 | -0.020933 | 0.023776 | -0.0053661 | -0.064087 | 0.013733 | -0.032043 | 0.036621 | 0.1831 | 0.009155 | 0.13733 | 0.13275 | 0.073242 | -0.054932 | 0.064087 | 0.20599 | 0.15106 | 0.15564 | 121.4584 | -0.76446 | -0.74158 | 121.6736 | 121.6278 | 121.4996 | 0.16937 | 0.041198 | 121.4355 | -0.70496 | -0.71411 | 121.6965 | 121.6461 | 121.6415 | 0.21057 | 0.20599 | 0.21515 | 0.068664 | 0.26093 | 0.11902 | 0.045776 | 0.12817 | 121.5042 | 121.5637 | -0.81024 | -0.83313 | 121.5271 | 121.5546 | 121.4264 | 121.6232
6394.5938 | 122.5571 | -121.5225 | 0.79651 | -0.22713 | -0.040467 | 0.00045503 | 0.015674 | -0.0019141 | -0.011811 | -0.0066457 | -0.028351 | 0.022614 | 0.016212 | -0.0078463 | -0.021147 | 0.024204 | -0.0042981 | -0.091553 | 0.009155 | -0.059509 | -0.013733 | 0.10529 | -0.064087 | 0.054932 | 0.032043 | 0.082397 | -0.059509 | 0.032043 | 0.1236 | 0.054932 | 0.11444 | 121.463 | -0.78735 | -0.81024 | 121.6278 | 121.5775 | 121.4584 | 0.11444 | -0.004578 | 121.463 | -0.71411 | -0.76447 | 121.6461 | 121.637 | 121.5775 | 0.17395 | 0.11444 | 0.16479 | 0.045776 | 0.1831 | 0.091552 | 0.068664 | 0.14191 | 121.5317 | 121.6049 | -0.85602 | -0.85602 | 121.5088 | 121.5546 | 121.431 | 121.5546
6396.2969 | 122.5983 | -121.5042 | 0.7782 | -0.17372 | -0.037476 | -0.0014676 | 0.019946 | 0.0025721 | -0.010102 | -0.0034415 | -0.11075 | 0.022614 | 0.015357 | -0.013614 | -0.021787 | 0.025699 | -0.0025891 | -0.082397 | 0.036621 | -0.064087 | 0.009155 | 0.091553 | -0.050354 | 0.082397 | 0.07782 | 0.068665 | -0.054932 | 0.068665 | 0.16479 | 0.091553 | 0.17395 | 121.4401 | -0.74158 | -0.76904 | 121.5958 | 121.5866 | 121.4539 | 0.14648 | 0.013733 | 121.4493 | -0.70953 | -0.70953 | 121.669 | 121.6782 | 121.5958 | 0.22888 | 0.14649 | 0.15564 | 0.073242 | 0.21973 | 0.1236 | 0.10071 | 0.1236 | 121.5408 | 121.5729 | -0.84228 | -0.83313 | 121.5134 | 121.5729 | 121.4218 | 121.582
6398.0156 | 122.5983 | -121.5225 | 0.78735 | -0.15083 | -0.039612 | -0.001254 | 0.018023 | 0.00064947 | -0.011811 | -0.0055777 | -0.034454 | 0.022614 | 0.013221 | -0.014896 | -0.020719 | 0.023776 | -0.0064343 | -0.054932 | 0 | -0.045776 | 0.050354 | 0.17853 | 0.027466 | 0.12817 | 0.10986 | 0.073242 | -0.07782 | 0.068665 | 0.20142 | 0.15106 | 0.15106 | 121.4767 | -0.78735 | -0.737 | 121.701 | 121.6507 | 121.55 | 0.17395 | 0.073242 | 121.4447 | -0.71411 | -0.71869 | 121.7239 | 121.6736 | 121.6736 | 0.22888 | 0.22888 | 0.2243 | 0.09613 | 0.27924 | 0.14649 | 0.045776 | 0.15106 | 121.5225 | 121.5958 | -0.83313 | -0.86517 | 121.5729 | 121.5912 | 121.4676 | 121.6324
6399.7188 | 122.5479 | -121.5271 | 0.7782 | -0.21187 | -0.039826 | 0.002164 | 0.018023 | 0.0017175 | -0.011811 | -0.0066457 | -0.055817 | 0.025178 | 0.015357 | -0.0067783 | -0.019651 | 0.023776 | -0.0025891 | -0.09613 | 0.004578 | -0.041199 | -0.004578 | 0.10529 | -0.059509 | 0.064087 | 0.036621 | 0.073242 | -0.068665 | 0.041199 | 0.1236 | 0.073242 | 0.11444 | 121.4859 | -0.77362 | -0.78278 | 121.6324 | 121.5912 | 121.4676 | 0.10529 | -0.01831 | 121.4584 | -0.70496 | -0.737 | 121.6507 | 121.6415 | 121.6003 | 0.18311 | 0.14191 | 0.14649 | 0.036621 | 0.19226 | 0.10986 | 0.045777 | 0.14191 | 121.5317 | 121.6003 | -0.8194 | -0.84686 | 121.5225 | 121.5683 | 121.431 | 121.5637
6401.4375 | 122.6166 | -121.5225 | 0.77362 | -0.15083 | -0.040467 | -0.00018577 | 0.016955 | -0.0031957 | -0.012239 | -0.0036551 | -0.04361 | 0.022828 | 0.013008 | -0.015109 | -0.022001 | 0.025912 | -0.0045117 | -0.068665 | 0.009155 | -0.064087 | 0.041199 | 0.15106 | 0.018311 | 0.11902 | 0.12817 | 0.059509 | -0.041199 | 0.086975 | 0.21057 | 0.15564 | 0.17395 | 121.4584 | -0.76447 | -0.73242 | 121.6736 | 121.6415 | 121.5408 | 0.18311 | 0.082398 | 121.4813 | -0.71411 | -0.68665 | 121.7331 | 121.6965 | 121.6782 | 0.21515 | 0.19684 | 0.21515 | 0.10529 | 0.25177 | 0.12817 | 0.073242 | 0.10071 | 121.5317 | 121.582 | -0.83771 | -0.81482 | 121.5637 | 121.6095 | 121.4539 | 121.6507
6403.1406 | 122.5708 | -121.5179 | 0.78278 | -0.16609 | -0.038758 | -0.00018577 | 0.020373 | -0.00084593 | -0.012666 | -0.0053641 | -0.1199 | 0.02411 | 0.01493 | -0.0076327 | -0.02136 | 0.025699 | 0.0014697 | -0.11902 | 0.045776 | -0.07782 | -0.041199 | 0.045776 | -0.10986 | 0.018311 | 0.022888 | 0.091553 | -0.073242 | 0.054932 | 0.13275 | 0.082397 | 0.15564 | 121.4401 | -0.737 | -0.82398 | 121.5637 | 121.5363 | 121.4081 | 0.096131 | -0.032043 | 121.4447 | -0.69122 | -0.72784 | 121.6507 | 121.6736 | 121.6003 | 0.22888 | 0.15564 | 0.1236 | 0.036621 | 0.20599 | 0.12817 | 0.1236 | 0.16479 | 121.5637 | 121.6095 | -0.8606 | -0.85602 | 121.4767 | 121.5729 | 121.3989 | 121.5408
6404.8438 | 122.5571 | -121.5363 | 0.79193 | -0.19661 | -0.04068 | -0.0016812 | 0.016101 | 0.0010767 | -0.0098886 | -0.0045095 | -0.040558 | 0.02176 | 0.015571 | -0.014469 | -0.018369 | 0.025699 | -0.0040845 | -0.10529 | 0.018311 | -0.050354 | -0.022888 | 0.07782 | -0.059509 | 0.064087 | 0 | 0.09613 | -0.073242 | 0.009155 | 0.11902 | 0.059509 | 0.10529 | 121.4859 | -0.77362 | -0.81482 | 121.6141 | 121.6003 | 121.4767 | 0.11444 | -0.009155 | 121.463 | -0.6958 | -0.78278 | 121.6553 | 121.6415 | 121.5958 | 0.17853 | 0.13275 | 0.12817 | 0.027466 | 0.19226 | 0.082397 | 0.068665 | 0.16937 | 121.5546 | 121.6324 | -0.84229 | -0.86517 | 121.5134 | 121.5454 | 121.431 | 121.5363
6406.6094 | 122.5479 | -121.5363 | 0.80109 | -0.19661 | -0.040039 | -0.0010404 | 0.018023 | -0.0055457 | -0.011598 | -0.0081411 | -0.025299 | 0.023469 | 0.016853 | -0.010623 | -0.019224 | 0.025485 | -0.00088011 | -0.11902 | 0.009155 | -0.054932 | -0.022888 | 0.068665 | -0.064087 | 0.045776 | 0.004578 | 0.082397 | -0.054932 | 0.022888 | 0.10986 | 0.064087 | 0.10986 | 121.4813 | -0.79193 | -0.82397 | 121.6049 | 121.582 | 121.4722 | 0.10071 | -0.009155 | 121.4813 | -0.71869 | -0.7782 | 121.6461 | 121.6461 | 121.6003 | 0.16479 | 0.11902 | 0.1236 | 0.032044 | 0.16479 | 0.07782 | 0.064087 | 0.13733 | 121.5454 | 121.6187 | -0.85602 | -0.85602 | 121.5134 | 121.5591 | 121.4172 | 121.5408
6408.3594 | 122.525 | -121.5591 | 0.80109 | -0.15846 | -0.037689 | 0.00024143 | 0.022723 | 0.0029993 | -0.014375 | -0.0038687 | -0.12601 | 0.022614 | 0.014076 | -0.0076327 | -0.02136 | 0.026553 | -0.0068615 | -0.086975 | 0.045776 | -0.064087 | -0.022888 | 0.068665 | -0.07782 | 0.027466 | 0.022888 | 0.1236 | -0.064087 | 0.018311 | 0.11902 | 0.036621 | 0.10986 | 121.4951 | -0.75531 | -0.82397 | 121.6278 | 121.5866 | 121.4813 | 0.091553 | -0.013733 | 121.4951 | -0.67749 | -0.78277 | 121.6782 | 121.669 | 121.5958 | 0.17395 | 0.10071 | 0.13275 | 0.041199 | 0.18311 | 0.082398 | 0.10986 | 0.18768 | 121.6049 | 121.6827 | -0.86517 | -0.86517 | 121.5363 | 121.5775 | 121.4722 | 121.582
6410.0625 | 122.5662 | -121.5683 | 0.78735 | -0.15083 | -0.039612 | -0.00082677 | 0.017169 | 0.0040675 | -0.011384 | -0.0034415 | -0.037506 | 0.022401 | 0.012794 | -0.012119 | -0.019438 | 0.023776 | -0.00066651 | -0.086975 | 0.009155 | -0.027466 | -0.009155 | 0.10529 | -0.050354 | 0.059509 | 0.050354 | 0.091553 | -0.059509 | 0.027466 | 0.10986 | 0.064087 | 0.12817 | 121.5408 | -0.7782 | -0.79651 | 121.6736 | 121.6278 | 121.5179 | 0.086975 | -0.022888 | 121.5088 | -0.6958 | -0.75989 | 121.6782 | 121.6965 | 121.6324 | 0.18768 | 0.1236 | 0.13275 | 0.018311 | 0.16937 | 0.086975 | 0.036621 | 0.15106 | 121.5775 | 121.6599 | -0.81482 | -0.84686 | 121.5591 | 121.5958 | 121.4813 | 121.6187
6411.7656 | 122.5342 | -121.5454 | 0.79651 | -0.16609 | -0.040253 | 0.00045503 | 0.021441 | 0.0029993 | -0.01117 | -0.0051505 | -0.12296 | 0.022614 | 0.015144 | -0.0078463 | -0.021574 | 0.028903 | -2.571e-05 | -0.13275 | 0.041199 | -0.07782 | -0.07782 | -0.009155 | -0.14648 | -0.013733 | -0.027466 | 0.10529 | -0.07782 | 0.022888 | 0.082397 | 0.018311 | 0.10071 | 121.4676 | -0.75531 | -0.87433 | 121.5363 | 121.5317 | 121.3989 | 0.064087 | -0.068664 | 121.4676 | -0.69122 | -0.77362 | 121.6278 | 121.6461 | 121.5637 | 0.17853 | 0.096131 | 0.068665 | 0 | 0.16022 | 0.10071 | 0.11902 | 0.18311 | 121.5866 | 121.6507 | -0.87433 | -0.87433 | 121.4676 | 121.5683 | 121.4127 | 121.5179
6413.4688 | 122.5754 | -121.5179 | 0.78278 | -0.24239 | -0.037476 | 0.00024143 | 0.017382 | -0.0031957 | -0.01117 | -0.0055777 | -0.04361 | 0.02411 | 0.016853 | -0.020236 | -0.020292 | 0.028262 | -0.0042981 | -0.07782 | 0.004578 | -0.032043 | 0.032043 | 0.14191 | -0.004578 | 0.07782 | 0.091553 | 0.091553 | -0.045776 | 0.064087 | 0.16022 | 0.10529 | 0.14648 | 121.4859 | -0.7782 | -0.75073 | 121.6599 | 121.5958 | 121.5134 | 0.10986 | 0.027465 | 121.4722 | -0.69122 | -0.71869 | 121.6782 | 121.6644 | 121.6232 | 0.19226 | 0.15106 | 0.17395 | 0.064086 | 0.20599 | 0.10986 | 0.036621 | 0.13733 | 121.5225 | 121.6095 | -0.81482 | -0.82855 | 121.55 | 121.582 | 121.4401 | 121.6095
6415.1719 | 122.4976 | -121.5591 | 0.8194 | -0.18135 | -0.038117 | 2.7834e-05 | 0.022082 | 0.0021447 | -0.012025 | -0.0036551 | -0.12296 | 0.024323 | 0.014289 | -0.016818 | -0.019651 | 0.025699 | -0.0038709 | -0.13275 | 0.041199 | -0.07782 | -0.10529 | -0.013733 | -0.15106 | -0.027466 | -0.054932 | 0.10529 | -0.086975 | -0.036621 | 0.027466 | -0.027466 | 0.064087 | 121.4813 | -0.7782 | -0.92468 | 121.5454 | 121.5317 | 121.4081 | 0.050354 | -0.073242 | 121.4722 | -0.71411 | -0.85602 | 121.5866 | 121.6232 | 121.5317 | 0.15106 | 0.059509 | 0.064087 | -0.027466 | 0.11444 | 0.050354 | 0.11902 | 0.19226 | 121.6003 | 121.6644 | -0.89722 | -0.90637 | 121.4539 | 121.5225 | 121.4264 | 121.5042
6416.875 | 122.5204 | -121.5775 | 0.81024 | -0.12794 | -0.041107 | -0.0016812 | 0.018237 | 0.0025721 | -0.013307 | -0.0066457 | -0.083283 | 0.022828 | 0.014289 | -0.014896 | -0.020933 | 0.026553 | -0.0019483 | -0.14648 | 0.041199 | -0.091553 | -0.086975 | 0.004578 | -0.10071 | 0 | -0.045776 | 0.10529 | -0.082397 | -0.018311 | 0.082397 | 0.032043 | 0.086975 | 121.4859 | -0.76904 | -0.89722 | 121.582 | 121.5775 | 121.4767 | 0.091553 | -0.009155 | 121.4951 | -0.70496 | -0.82855 | 121.6599 | 121.6644 | 121.6095 | 0.16937 | 0.11444 | 0.096131 | 0.004578 | 0.16479 | 0.064086 | 0.13275 | 0.18768 | 121.6187 | 121.6827 | -0.9018 | -0.89264 | 121.4905 | 121.5591 | 121.431 | 121.5317
6418.5938 | 122.6166 | -121.5225 | 0.78735 | -0.15846 | -0.042176 | -0.0016812 | 0.01781 | -0.0034095 | -0.014161 | -0.0051505 | -0.022247 | 0.021546 | 0.017066 | -0.012973 | -0.018797 | 0.024417 | -0.0010937 | -0.086975 | -0.004578 | -0.054932 | 0.013733 | 0.14648 | -0.004578 | 0.1236 | 0.10986 | 0.059509 | -0.059509 | 0.086975 | 0.20599 | 0.15106 | 0.17853 | 121.4676 | -0.79193 | -0.77362 | 121.669 | 121.6461 | 121.5179 | 0.17853 | 0.050354 | 121.463 | -0.72784 | -0.70038 | 121.7285 | 121.701 | 121.6736 | 0.23804 | 0.21057 | 0.20142 | 0.068665 | 0.2655 | 0.14648 | 0.050354 | 0.11902 | 121.5179 | 121.582 | -0.84229 | -0.84686 | 121.5363 | 121.6095 | 121.4355 | 121.6324
6420.2969 | 122.6166 | -121.5179 | 0.76904 | -0.18898 | -0.040039 | -0.00061317 | 0.019091 | 0.00022207 | -0.012666 | -0.0051505 | -0.071076 | 0.022187 | 0.015571 | -0.012546 | -0.020292 | 0.027621 | -0.0015209 | -0.054932 | 0.013733 | -0.045776 | 0.018311 | 0.11902 | -0.032043 | 0.082397 | 0.082397 | 0.086975 | -0.041199 | 0.091553 | 0.17395 | 0.10986 | 0.19226 | 121.4722 | -0.75531 | -0.75073 | 121.637 | 121.6003 | 121.4859 | 0.12817 | 0.013733 | 121.4767 | -0.68207 | -0.67749 | 121.6919 | 121.7102 | 121.6278 | 0.23346 | 0.15106 | 0.16479 | 0.064087 | 0.21515 | 0.13275 | 0.059509 | 0.12817 | 121.5317 | 121.6049 | -0.81482 | -0.81024 | 121.5363 | 121.6095 | 121.463 | 121.6003
6422 | 122.5342 | -121.5591 | 0.80566 | -0.15083 | -0.036621 | -0.0016812 | 0.019946 | 0.0025721 | -0.014161 | -0.0049367 | -0.083283 | 0.023896 | 0.016639 | -0.014041 | -0.020506 | 0.025912 | -0.0062207 | -0.11902 | 0.054932 | -0.068665 | -0.082397 | 0.022888 | -0.086975 | -0.009155 | -0.018311 | 0.11902 | -0.086975 | -0.009155 | 0.09613 | 0.050354 | 0.091553 | 121.4905 | -0.75073 | -0.88806 | 121.582 | 121.55 | 121.4722 | 0.05951 | -0.01831 | 121.4722 | -0.68665 | -0.81482 | 121.6553 | 121.6507 | 121.6095 | 0.17853 | 0.13733 | 0.091553 | -0.013732 | 0.1831 | 0.07782 | 0.1236 | 0.20599 | 121.6141 | 121.6782 | -0.87433 | -0.89264 | 121.4767 | 121.55 | 121.4401 | 121.5408
6423.7031 | 122.6212 | -121.5454 | 0.76446 | -0.12032 | -0.039826 | -0.0016812 | 0.019305 | 0.0034265 | -0.014161 | -0.0030141 | -0.022247 | 0.020905 | 0.015998 | -0.015323 | -0.019865 | 0.024631 | -0.0028027 | -0.07782 | 0 | -0.027466 | 0.036621 | 0.16479 | 0.009155 | 0.11902 | 0.07782 | 0.059509 | -0.050354 | 0.054932 | 0.18768 | 0.13733 | 0.15564 | 121.5179 | -0.76446 | -0.72784 | 121.7102 | 121.6644 | 121.5546 | 0.14649 | 0.036621 | 121.4951 | -0.70496 | -0.70953 | 121.7331 | 121.7011 | 121.6827 | 0.20599 | 0.18768 | 0.19226 | 0.064087 | 0.23804 | 0.10529 | 0.027466 | 0.10986 | 121.5454 | 121.6049 | -0.79193 | -0.81482 | 121.582 | 121.6003 | 121.4676 | 121.6232
6425.4062 | 122.493 | -121.55 | 0.82855 | -0.19661 | -0.036835 | -0.00082677 | 0.021228 | -0.00084593 | -0.012879 | -0.0034415 | -0.12906 | 0.023896 | 0.015357 | -0.0097689 | -0.020506 | 0.026553 | -0.00045291 | -0.1236 | 0.054932 | -0.068665 | -0.10071 | -0.018311 | -0.15106 | -0.059509 | -0.073242 | 0.11902 | -0.086975 | -0.054932 | 0.022888 | -0.032043 | 0.045776 | 121.4813 | -0.77362 | -0.92926 | 121.5317 | 121.4905 | 121.3989 | 0.009156 | -0.082397 | 121.463 | -0.70953 | -0.88348 | 121.5729 | 121.5958 | 121.5179 | 0.13275 | 0.054932 | 0.050354 | -0.032043 | 0.10986 | 0.032043 | 0.1236 | 0.20599 | 121.6049 | 121.669 | -0.89722 | -0.91553 | 121.4493 | 121.4951 | 121.4264 | 121.4767
6427.1094 | 122.5388 | -121.5363 | 0.82398 | -0.12794 | -0.043244 | -0.002963 | 0.020587 | 0.0023585 | -0.015229 | -0.0042959 | -0.09549 | 0.024537 | 0.015785 | -0.018314 | -0.020078 | 0.026126 | -0.00066651 | -0.13275 | 0.045776 | -0.07782 | -0.073242 | 0.027466 | -0.068665 | 0 | -0.036621 | 0.10529 | -0.082397 | 0 | 0.10071 | 0.041199 | 0.091553 | 121.4584 | -0.7782 | -0.89722 | 121.5637 | 121.5363 | 121.4676 | 0.07782 | 0.009155 | 121.4539 | -0.71869 | -0.82398 | 121.637 | 121.6278 | 121.5775 | 0.17395 | 0.1236 | 0.10529 | 0.004578 | 0.18311 | 0.082397 | 0.1236 | 0.18768 | 121.582 | 121.6415 | -0.9018 | -0.90637 | 121.463 | 121.5363 | 121.4035 | 121.4996
6428.8125 | 122.5616 | -121.5271 | 0.81024 | -0.17372 | -0.039826 | -0.0010404 | 0.016955 | 0.0027857 | -0.013307 | -0.0017325 | -0.0008851 | 0.022828 | 0.01493 | -0.014041 | -0.018583 | 0.025699 | -0.0019483 | -0.068665 | 0.013733 | -0.041199 | -0.004578 | 0.13275 | 0 | 0.082397 | 0.041199 | 0.082397 | -0.050354 | 0.013733 | 0.12817 | 0.082397 | 0.10986 | 121.4859 | -0.79651 | -0.81482 | 121.6599 | 121.6095 | 121.5271 | 0.1236 | 0.041199 | 121.4767 | -0.72785 | -0.79651 | 121.6553 | 121.637 | 121.6095 | 0.16022 | 0.13275 | 0.17395 | 0.036621 | 0.17853 | 0.064087 | 0.054932 | 0.13275 | 121.5408 | 121.6095 | -0.85144 | -0.8606 | 121.5225 | 121.5408 | 121.4584 | 121.5683
6430.5625 | 122.5433 | -121.5408 | 0.82855 | -0.082169 | -0.041535 | -0.001254 | 0.018664 | -0.00041873 | -0.011598 | -0.0021597 | -0.06192 | 0.023682 | 0.014076 | -0.013614 | -0.01901 | 0.026981 | -0.0055799 | -0.12817 | 0.050354 | -0.07782 | -0.10986 | 0.018311 | -0.10071 | -0.013733 | -0.064087 | 0.1236 | -0.086975 | -0.018311 | 0.073242 | 0.018311 | 0.091553 | 121.463 | -0.7782 | -0.93841 | 121.5591 | 121.5271 | 121.4401 | 0.064087 | -0.022888 | 121.4539 | -0.70496 | -0.84686 | 121.6141 | 121.6324 | 121.5591 | 0.17853 | 0.10529 | 0.096131 | -0.032043 | 0.16022 | 0.068664 | 0.12817 | 0.21057 | 121.5912 | 121.6644 | -0.90637 | -0.91553 | 121.431 | 121.5225 | 121.4127 | 121.4767
6432.2656 | 122.5708 | -121.5363 | 0.79651 | -0.18898 | -0.041962 | -0.0018948 | 0.016955 | -0.0027685 | -0.011384 | -0.0028005 | -0.013092 | 0.02411 | 0.014503 | -0.010837 | -0.01901 | 0.025699 | -0.0034435 | -0.10986 | 0.032043 | -0.050354 | -0.041199 | 0.068665 | -0.082397 | 0.050354 | -0.004578 | 0.068665 | -0.064087 | 0.018311 | 0.11444 | 0.068665 | 0.10071 | 121.4859 | -0.76447 | -0.83771 | 121.6049 | 121.5866 | 121.4539 | 0.10071 | -0.032043 | 121.4722 | -0.72784 | -0.7782 | 121.6507 | 121.637 | 121.6049 | 0.1648 | 0.13275 | 0.11902 | 0.009155 | 0.17853 | 0.082398 | 0.082397 | 0.13275 | 121.5683 | 121.6049 | -0.84686 | -0.8606 | 121.4951 | 121.5546 | 121.4264 | 121.5317
6433.9688 | 122.5845 | -121.5134 | 0.80566 | -0.1432 | -0.038544 | -0.00039957 | 0.021228 | 0.0025721 | -0.012239 | -0.0064321 | -0.074127 | 0.023682 | 0.018348 | -0.0089145 | -0.020719 | 0.025912 | -0.0015209 | -0.1236 | 0.059509 | -0.064087 | -0.059509 | 0.036621 | -0.11902 | 0 | 0.022888 | 0.10529 | -0.07782 | 0.036621 | 0.1236 | 0.091553 | 0.13733 | 121.4493 | -0.74616 | -0.86517 | 121.55 | 121.5134 | 121.3943 | 0.064087 | -0.054932 | 121.4355 | -0.70038 | -0.76904 | 121.637 | 121.6507 | 121.6049 | 0.21515 | 0.16937 | 0.10071 | 0.004578 | 0.20142 | 0.11444 | 0.1236 | 0.18311 | 121.5729 | 121.6187 | -0.86975 | -0.88348 | 121.4539 | 121.55 | 121.3898 | 121.5363
6435.6875 | 122.5388 | -121.5271 | 0.82398 | -0.18898 | -0.039398 | -0.001254 | 0.020373 | 0.0055627 | -0.012879 | -0.0032277 | -0.11685 | 0.023469 | 0.017066 | -0.011692 | -0.019438 | 0.026126 | -0.0038709 | -0.091553 | 0.041199 | -0.086975 | -0.041199 | 0.068665 | -0.07782 | 0.027466 | 0.032043 | 0.10529 | -0.059509 | 0 | 0.10529 | 0.045776 | 0.11902 | 121.4401 | -0.78278 | -0.86517 | 121.5958 | 121.5546 | 121.4493 | 0.11444 | 0.009155 | 121.4676 | -0.71869 | -0.82398 | 121.6324 | 121.6461 | 121.5729 | 0.17853 | 0.10528 | 0.15564 | 0.045776 | 0.16479 | 0.059509 | 0.12817 | 0.16479 | 121.5683 | 121.6324 | -0.91095 | -0.88348 | 121.4859 | 121.5271 | 121.4355 | 121.5591
6437.3906 | 122.6303 | -121.5042 | 0.78735 | -0.17372 | -0.041962 | -0.0031766 | 0.016314 | -0.0040503 | -0.012666 | -0.0034415 | 0.014374 | 0.02176 | 0.015357 | -0.015964 | -0.019865 | 0.024417 | -0.0030163 | -0.10529 | 0.027466 | -0.054932 | -0.009155 | 0.11902 | -0.018311 | 0.10529 | 0.059509 | 0.073242 | -0.050354 | 0.059509 | 0.17853 | 0.13733 | 0.16937 | 121.4493 | -0.75989 | -0.79651 | 121.6232 | 121.6095 | 121.4859 | 0.16022 | 0.036621 | 121.4539 | -0.71411 | -0.72784 | 121.6827 | 121.6736 | 121.6415 | 0.21973 | 0.18768 | 0.17395 | 0.045777 | 0.22888 | 0.10986 | 0.082398 | 0.1236 | 121.5317 | 121.5775 | -0.84229 | -0.83771 | 121.4951 | 121.5637 | 121.3989 | 121.5637
6439.1406 | 122.5021 | -121.5591 | 0.81482 | -0.18898 | -0.038544 | -0.0023222 | 0.021228 | 0.00086307 | -0.013307 | -0.0053641 | -0.1199 | 0.024537 | 0.013862 | -0.01041 | -0.018156 | 0.027408 | -0.0047253 | -0.1236 | 0.068665 | -0.07782 | -0.10529 | -0.045776 | -0.16479 | -0.027466 | -0.082397 | 0.10529 | -0.091553 | -0.041199 | 0.032043 | -0.036621 | 0.068665 | 121.4813 | -0.74615 | -0.9201 | 121.5134 | 121.5317 | 121.3943 | 0.050354 | -0.086975 | 121.4676 | -0.70953 | -0.85602 | 121.5912 | 121.6278 | 121.5225 | 0.16022 | 0.054932 | 0.032044 | -0.027466 | 0.1236 | 0.050354 | 0.14649 | 0.19684 | 121.6278 | 121.6644 | -0.89264 | -0.90637 | 121.4539 | 121.5179 | 121.4355 | 121.4767
6440.8438 | 122.5067 | -121.5775 | 0.81482 | -0.097427 | -0.042389 | 0.00024143 | 0.016314 | -0.0027685 | -0.013093 | -0.0083547 | -0.0039367 | 0.023041 | 0.015571 | -0.014255 | -0.019651 | 0.024204 | -0.0015209 | -0.10529 | 0.013733 | -0.054932 | -0.073242 | 0.036621 | -0.082397 | 0.022888 | -0.036621 | 0.11444 | -0.082397 | -0.041199 | 0.068665 | 0.027466 | 0.059509 | 121.5225 | -0.80109 | -0.88806 | 121.6141 | 121.6003 | 121.4951 | 0.07782 | -0.027465 | 121.4951 | -0.70038 | -0.85602 | 121.6461 | 121.637 | 121.6049 | 0.14191 | 0.10986 | 0.091553 | -0.01831 | 0.15106 | 0.041198 | 0.068665 | 0.19684 | 121.5912 | 121.6919 | -0.86975 | -0.89722 | 121.5042 | 121.5363 | 121.4722 | 121.5408
6442.5625 | 122.493 | -121.5729 | 0.82398 | -0.18898 | -0.038117 | 0.00045503 | 0.019305 | -0.00041873 | -0.011384 | -0.0060049 | -0.1199 | 0.022828 | 0.015785 | -0.010623 | -0.020506 | 0.025912 | -0.0030163 | -0.11902 | 0.050354 | -0.073242 | -0.086975 | -0.027466 | -0.14648 | -0.036621 | -0.086975 | 0.11444 | -0.082397 | -0.050354 | 0.022888 | -0.041199 | 0.041199 | 121.4996 | -0.77362 | -0.91095 | 121.5454 | 121.5363 | 121.4264 | 0.036621 | -0.073242 | 121.4905 | -0.70953 | -0.87433 | 121.5958 | 121.6141 | 121.5317 | 0.1236 | 0.041198 | 0.045776 | -0.013733 | 0.10528 | 0.032043 | 0.1236 | 0.19684 | 121.6232 | 121.6873 | -0.89722 | -0.90637 | 121.4859 | 121.5225 | 121.4539 | 121.4859
6444.2656 | 122.5067 | -121.5866 | 0.83771 | -0.12032 | -0.042816 | -0.0016812 | 0.019091 | 0.0034265 | -0.011811 | -0.0081411 | -0.040558 | 0.023041 | 0.015144 | -0.0099827 | -0.018369 | 0.025699 | -2.571e-05 | -0.15106 | 0.068665 | -0.091553 | -0.10986 | -0.004578 | -0.11444 | 0 | -0.07782 | 0.11902 | -0.068665 | -0.068665 | 0.050354 | 0.009155 | 0.045776 | 121.4951 | -0.76904 | -0.94757 | 121.582 | 121.5866 | 121.4722 | 0.091553 | -0.022888 | 121.5179 | -0.71869 | -0.90637 | 121.637 | 121.6324 | 121.5958 | 0.11444 | 0.07782 | 0.086975 | -0.01831 | 0.11902 | 0 | 0.16022 | 0.18768 | 121.6553 | 121.7056 | -0.92926 | -0.90637 | 121.4767 | 121.5179 | 121.4355 | 121.5088
6445.9844 | 122.6257 | -121.5225 | 0.79193 | -0.19661 | -0.040253 | -0.00061317 | 0.018878 | 0.0023585 | -0.010957 | -0.0047231 | -0.06192 | 0.023469 | 0.014503 | -0.010623 | -0.020292 | 0.026553 | -0.0021619 | -0.073242 | 0.018311 | -0.059509 | 0 | 0.10529 | -0.050354 | 0.07782 | 0.086975 | 0.068665 | -0.050354 | 0.07782 | 0.15564 | 0.086975 | 0.17395 | 121.463 | -0.77362 | -0.79193 | 121.6278 | 121.6003 | 121.4722 | 0.13733 | 0.009155 | 121.4722 | -0.72327 | -0.71411 | 121.6782 | 121.6965 | 121.6095 | 0.2243 | 0.13733 | 0.16479 | 0.059509 | 0.20599 | 0.12817 | 0.07782 | 0.11902 | 121.5408 | 121.5912 | -0.85144 | -0.84229 | 121.5225 | 121.6003 | 121.4493 | 121.6095
6447.7031 | 122.6212 | -121.4996 | 0.79651 | -0.18135 | -0.040039 | 2.7834e-05 | 0.020587 | 0.0019311 | -0.013093 | -0.0042959 | -0.06192 | 0.024323 | 0.014717 | -0.014682 | -0.020078 | 0.02634 | -0.0045117 | -0.082397 | 0.022888 | -0.050354 | 0.013733 | 0.10529 | -0.050354 | 0.059509 | 0.073242 | 0.064087 | -0.045776 | 0.068665 | 0.15564 | 0.091553 | 0.17395 | 121.4493 | -0.77362 | -0.78278 | 121.6049 | 121.5591 | 121.4493 | 0.10986 | 0 | 121.4539 | -0.73242 | -0.72784 | 121.6553 | 121.6736 | 121.5912 | 0.21973 | 0.13733 | 0.15564 | 0.064087 | 0.20142 | 0.11444 | 0.073242 | 0.10986 | 121.5225 | 121.5637 | -0.84686 | -0.84229 | 121.5134 | 121.5683 | 121.4172 | 121.5729
6449.4062 | 122.58 | -121.5363 | 0.80566 | -0.2195 | -0.040039 | 0.00024143 | 0.016314 | 0.00022207 | -0.012452 | -0.0038687 | -0.028351 | 0.022187 | 0.015785 | -0.016605 | -0.021147 | 0.025058 | -0.0017347 | -0.09613 | 0.004578 | -0.050354 | -0.041199 | 0.091553 | -0.064087 | 0.059509 | 0.022888 | 0.09613 | -0.064087 | 0.018311 | 0.12817 | 0.068665 | 0.1236 | 121.4859 | -0.80109 | -0.84686 | 121.6278 | 121.5958 | 121.4722 | 0.10986 | -0.013733 | 121.4722 | -0.70953 | -0.78735 | 121.6644 | 121.6599 | 121.6049 | 0.18768 | 0.13275 | 0.14191 | 0.009155 | 0.19226 | 0.082398 | 0.054932 | 0.16022 | 121.5408 | 121.6324 | -0.85602 | -0.86975 | 121.4951 | 121.5546 | 121.4401 | 121.5591
6451.1094 | 122.644 | -121.4996 | 0.79651 | -0.20424 | -0.038544 | -0.00039957 | 0.018237 | 0.00064947 | -0.010957 | -0.0066457 | -0.064972 | 0.023896 | 0.014076 | -0.0087009 | -0.021147 | 0.02634 | -0.0045117 | -0.050354 | 0.027466 | -0.054932 | 0 | 0.12817 | -0.050354 | 0.082397 | 0.082397 | 0.064087 | -0.027466 | 0.082397 | 0.17395 | 0.09613 | 0.1831 | 121.4447 | -0.76904 | -0.79651 | 121.6278 | 121.582 | 121.4493 | 0.13733 | 0.004578 | 121.4722 | -0.73242 | -0.71411 | 121.6736 | 121.6827 | 121.5958 | 0.21057 | 0.1236 | 0.18311 | 0.054932 | 0.20142 | 0.10986 | 0.082398 | 0.091553 | 121.5271 | 121.5637 | -0.85144 | -0.82398 | 121.4996 | 121.582 | 121.4493 | 121.582
6452.8125 | 122.5388 | -121.5729 | 0.84686 | -0.1432 | -0.041535 | -0.0010404 | 0.018878 | -0.0025549 | -0.012239 | -0.0083547 | -0.071076 | 0.021546 | 0.016426 | -0.011905 | -0.021147 | 0.025912 | -0.0028027 | -0.1236 | 0.064087 | -0.086975 | -0.086975 | -0.009155 | -0.11444 | 0.004578 | -0.064087 | 0.11902 | -0.073242 | -0.050354 | 0.045776 | 0.027466 | 0.091553 | 121.4859 | -0.78278 | -0.93384 | 121.5637 | 121.5775 | 121.4584 | 0.091553 | -0.027466 | 121.4996 | -0.72784 | -0.89722 | 121.6187 | 121.6644 | 121.6003 | 0.16479 | 0.10071 | 0.07782 | 0 | 0.11902 | 0.022888 | 0.15106 | 0.19226 | 121.637 | 121.6919 | -0.93384 | -0.92011 | 121.4859 | 121.5225 | 121.4493 | 121.5088
6454.5312 | 122.5571 | -121.5729 | 0.79651 | -0.12032 | -0.039612 | -0.00039957 | 0.020373 | 0.0021447 | -0.01352 | -0.0040823 | -0.10159 | 0.023041 | 0.01493 | -0.013828 | -0.021147 | 0.025485 | -0.0010937 | -0.082397 | 0.045776 | -0.064087 | -0.045776 | 0.064087 | -0.064087 | 0.018311 | 0.013733 | 0.11902 | -0.068665 | 0.004578 | 0.10529 | 0.045776 | 0.10986 | 121.5088 | -0.75073 | -0.84229 | 121.637 | 121.5912 | 121.5088 | 0.082398 | 0 | 121.5042 | -0.67749 | -0.79193 | 121.6782 | 121.6827 | 121.6187 | 0.17853 | 0.11444 | 0.12817 | 0.018311 | 0.17395 | 0.073243 | 0.10986 | 0.18768 | 121.6187 | 121.6919 | -0.8606 | -0.86517 | 121.5271 | 121.5775 | 121.4905 | 121.5866
6456.2812 | 122.5204 | -121.5454 | 0.83771 | -0.17372 | -0.03833 | -0.0018948 | 0.018664 | 0.0029993 | -0.014161 | -0.0055777 | -0.055817 | 0.022828 | 0.014289 | -0.013187 | -0.019438 | 0.024844 | -0.00045291 | -0.13275 | 0.045776 | -0.10071 | -0.10071 | -0.009155 | -0.11444 | -0.009155 | -0.059509 | 0.1236 | -0.09613 | -0.036621 | 0.068665 | 0.004578 | 0.073242 | 121.4447 | -0.79193 | -0.93842 | 121.5363 | 121.5363 | 121.431 | 0.091553 | -0.013733 | 121.4493 | -0.71411 | -0.87433 | 121.6141 | 121.6187 | 121.55 | 0.16937 | 0.10071 | 0.091553 | 0 | 0.16479 | 0.059509 | 0.14648 | 0.21973 | 121.5912 | 121.669 | -0.93842 | -0.93384 | 121.4447 | 121.5088 | 121.4127 | 121.4859
6458.0469 | 122.5113 | -121.5775 | 0.83771 | -0.20424 | -0.04068 | -0.0016812 | 0.017382 | -0.0023413 | -0.014161 | -0.0055777 | -0.013092 | 0.023255 | 0.014076 | -0.015109 | -0.018583 | 0.025272 | -0.0013073 | -0.091553 | 0.041199 | -0.064087 | -0.054932 | 0.068665 | -0.059509 | 0.032043 | -0.022888 | 0.10071 | -0.082397 | -0.045776 | 0.091553 | 0.018311 | 0.059509 | 121.5134 | -0.79651 | -0.89264 | 121.6461 | 121.6095 | 121.5179 | 0.09613 | 0.004578 | 121.4951 | -0.737 | -0.88348 | 121.669 | 121.637 | 121.5958 | 0.14191 | 0.10071 | 0.13275 | 0.009155 | 0.17395 | 0.036621 | 0.10529 | 0.18311 | 121.6187 | 121.6782 | -0.9018 | -0.9201 | 121.5225 | 121.5317 | 121.4859 | 121.5546
6459.75 | 122.644 | -121.5134 | 0.80109 | -0.15846 | -0.042603 | -0.0018948 | 0.017596 | -0.0036231 | -0.012879 | -0.0070731 | 0.023529 | 0.021119 | 0.016426 | -0.014255 | -0.020506 | 0.023563 | -0.0070751 | -0.10529 | 0.027466 | -0.068665 | -0.013733 | 0.091553 | -0.022888 | 0.082397 | 0.045776 | 0.07782 | -0.059509 | 0.059509 | 0.18768 | 0.14191 | 0.16479 | 121.4447 | -0.77362 | -0.81482 | 121.6049 | 121.5958 | 121.4905 | 0.15106 | 0.045777 | 121.4539 | -0.72327 | -0.74158 | 121.7011 | 121.6782 | 121.6553 | 0.2243 | 0.20142 | 0.16022 | 0.054932 | 0.24719 | 0.11902 | 0.096131 | 0.13733 | 121.5408 | 121.5912 | -0.86975 | -0.86059 | 121.4996 | 121.5729 | 121.4081 | 121.5591
6461.4531 | 122.5113 | -121.5591 | 0.85144 | -0.16609 | -0.041107 | 2.7834e-05 | 0.016101 | 8.47e-06 | -0.01117 | -0.0021597 | -0.034454 | 0.023896 | 0.015144 | -0.017673 | -0.02136 | 0.026126 | -0.0028027 | -0.12817 | 0.045776 | -0.073242 | -0.09613 | 0.022888 | -0.091553 | 0.022888 | -0.054932 | 0.11444 | -0.068665 | -0.073242 | 0.064087 | -0.004578 | 0.045776 | 121.4859 | -0.80566 | -0.94757 | 121.582 | 121.582 | 121.4676 | 0.09613 | -0.018311 | 121.4905 | -0.737 | -0.92468 | 121.6232 | 121.6049 | 121.5546 | 0.11444 | 0.064087 | 0.09613 | -0.022888 | 0.13275 | -0.004577 | 0.11902 | 0.18311 | 121.6049 | 121.6736 | -0.92468 | -0.9201 | 121.463 | 121.4859 | 121.431 | 121.5042
6463.1562 | 122.6669 | -121.5271 | 0.80566 | -0.12032 | -0.040467 | -0.0016812 | 0.018237 | 0.0021447 | -0.013734 | -0.0049367 | 0.026581 | 0.023041 | 0.015144 | -0.010837 | -0.021574 | 0.023135 | -0.0062207 | -0.064087 | 0.004578 | -0.045776 | 0.018311 | 0.16479 | 0.018311 | 0.13733 | 0.10986 | 0.086975 | -0.054932 | 0.073242 | 0.21057 | 0.15106 | 0.16022 | 121.4813 | -0.80109 | -0.78735 | 121.6919 | 121.6644 | 121.5454 | 0.18311 | 0.064087 | 121.4722 | -0.71869 | -0.73242 | 121.7377 | 121.6873 | 121.6782 | 0.21515 | 0.20599 | 0.21057 | 0.064087 | 0.2655 | 0.12817 | 0.050354 | 0.14191 | 121.5317 | 121.6141 | -0.85144 | -0.8606 | 121.5454 | 121.6003 | 121.463 | 121.637
6464.8594 | 122.5891 | -121.5363 | 0.80566 | -0.2195 | -0.040039 | 0.00066863 | 0.018023 | 0.0017175 | -0.010957 | -0.0045095 | -0.025299 | 0.023896 | 0.013862 | -0.013828 | -0.020292 | 0.025485 | -0.0028027 | -0.068665 | 0.004578 | -0.041199 | 0.004578 | 0.14191 | -0.054932 | 0.073242 | 0.09613 | 0.07782 | -0.032043 | 0.050354 | 0.15106 | 0.091553 | 0.14191 | 121.4951 | -0.80109 | -0.80109 | 121.6782 | 121.6095 | 121.4813 | 0.11444 | -0.013733 | 121.5042 | -0.72784 | -0.75531 | 121.6873 | 121.6782 | 121.6278 | 0.17395 | 0.1236 | 0.18311 | 0.045777 | 0.18311 | 0.082397 | 0.045777 | 0.10986 | 121.5408 | 121.6141 | -0.84686 | -0.83771 | 121.5408 | 121.5866 | 121.4676 | 121.6324
6466.6094 | 122.5525 | -121.6095 | 0.79193 | -0.15083 | -0.040467 | 0.00088223 | 0.0208 | -0.0025549 | -0.012879 | -0.0034415 | -0.13211 | 0.022614 | 0.014717 | -0.011051 | -0.020933 | 0.026126 | -0.00066651 | -0.091553 | 0.064087 | -0.068665 | -0.041199 | 0.059509 | -0.073242 | 0.013733 | 0.022888 | 0.11902 | -0.045776 | 0.009155 | 0.10529 | 0.022888 | 0.09613 | 121.5408 | -0.72784 | -0.83313 | 121.669 | 121.6232 | 121.5363 | 0.082398 | -0.004577 | 121.5637 | -0.67291 | -0.78278 | 121.7148 | 121.7056 | 121.6324 | 0.14191 | 0.068664 | 0.12817 | 0.027466 | 0.15106 | 0.054931 | 0.13275 | 0.16479 | 121.6736 | 121.7285 | -0.8606 | -0.83771 | 121.5683 | 121.6187 | 121.5179 | 121.6324
6468.2969 | 122.644 | -121.5775 | 0.75531 | -0.18135 | -0.040253 | -0.002963 | 0.016528 | 0.0012903 | -0.012025 | -0.0047231 | -0.0008851 | 0.022614 | 0.014717 | -0.013614 | -0.021147 | 0.024204 | -0.0036573 | -0.073242 | 0 | -0.054932 | 0.041199 | 0.18768 | 0.027466 | 0.12817 | 0.10071 | 0.082397 | -0.045776 | 0.064087 | 0.21515 | 0.14648 | 0.15564 | 121.5225 | -0.75531 | -0.71411 | 121.7651 | 121.7056 | 121.6049 | 0.18311 | 0.082398 | 121.5317 | -0.67291 | -0.69122 | 121.7926 | 121.7331 | 121.7239 | 0.20142 | 0.19226 | 0.24261 | 0.096131 | 0.26093 | 0.10986 | 0.054932 | 0.12817 | 121.5775 | 121.6599 | -0.81024 | -0.80109 | 121.6187 | 121.6415 | 121.5042 | 121.6782
6470 | 122.5891 | -121.5958 | 0.75989 | -0.15083 | -0.041535 | -0.0010404 | 0.016955 | -0.0012731 | -0.01053 | -0.0025869 | -0.028351 | 0.021546 | 0.013648 | -0.015964 | -0.020506 | 0.026126 | -0.0060071 | -0.11902 | 0.036621 | -0.045776 | -0.041199 | 0.064087 | -0.082397 | 0.045776 | -0.013733 | 0.086975 | -0.054932 | 0.013733 | 0.11902 | 0.064087 | 0.11444 | 121.55 | -0.72327 | -0.80109 | 121.6599 | 121.6415 | 121.5134 | 0.091552 | -0.036621 | 121.5408 | -0.67291 | -0.74616 | 121.7148 | 121.7102 | 121.6599 | 0.16937 | 0.11902 | 0.10986 | 0.004577 | 0.17395 | 0.068665 | 0.082397 | 0.14191 | 121.6324 | 121.6827 | -0.80566 | -0.81482 | 121.5546 | 121.6095 | 121.4767 | 121.582
6471.7188 | 122.525 | -121.6232 | 0.78278 | -0.23476 | -0.038544 | -0.00061317 | 0.021869 | 0.0023585 | -0.012239 | -0.0040823 | -0.12906 | 0.024537 | 0.016212 | -0.0069919 | -0.020719 | 0.027194 | -0.0030163 | -0.11902 | 0.054932 | -0.086975 | -0.09613 | -0.050354 | -0.16022 | -0.032043 | -0.054932 | 0.13733 | -0.086975 | -0.036621 | 0.032043 | -0.032043 | 0.059509 | 121.5363 | -0.72784 | -0.87891 | 121.5729 | 121.5912 | 121.463 | 0.054932 | -0.073242 | 121.5363 | -0.64545 | -0.8194 | 121.6553 | 121.6827 | 121.5912 | 0.14648 | 0.054932 | 0.036621 | -0.009155 | 0.11902 | 0.050354 | 0.14191 | 0.2243 | 121.6782 | 121.7606 | -0.86975 | -0.86975 | 121.5271 | 121.5866 | 121.5042 | 121.5683
6473.4219 | 122.5021 | -121.6278 | 0.78278 | -0.1432 | -0.043244 | -0.0016812 | 0.018237 | 0.0029993 | -0.01352 | -0.0066457 | -0.080231 | 0.023682 | 0.013221 | -0.01276 | -0.021147 | 0.025058 | 0.00061529 | -0.15564 | 0.068665 | -0.07782 | -0.091553 | -0.009155 | -0.10986 | -0.013733 | -0.082397 | 0.12817 | -0.086975 | -0.054932 | 0.045776 | 0 | 0.059509 | 121.55 | -0.71411 | -0.87433 | 121.6187 | 121.6141 | 121.5179 | 0.064087 | -0.032043 | 121.5408 | -0.6546 | -0.83771 | 121.6736 | 121.6873 | 121.6278 | 0.14648 | 0.086975 | 0.068665 | -0.013733 | 0.13275 | 0.032043 | 0.14649 | 0.21515 | 121.6965 | 121.756 | -0.8606 | -0.86975 | 121.5363 | 121.5729 | 121.4722 | 121.5454
6475.125 | 122.5891 | -121.5866 | 0.77362 | -0.13557 | -0.039398 | -0.0016812 | 0.01546 | -0.00020513 | -0.013307 | -0.0042959 | 0.0021667 | 0.022828 | 0.013008 | -0.015964 | -0.020292 | 0.025912 | -0.0028027 | -0.082397 | -0.004578 | -0.054932 | 0.009155 | 0.1236 | 0.004578 | 0.091553 | 0.050354 | 0.07782 | -0.059509 | 0.027466 | 0.15106 | 0.086975 | 0.11444 | 121.5317 | -0.7782 | -0.76447 | 121.7102 | 121.6782 | 121.5912 | 0.14649 | 0.05951 | 121.5271 | -0.6958 | -0.74616 | 121.7377 | 121.701 | 121.6736 | 0.17395 | 0.14648 | 0.17853 | 0.064087 | 0.21057 | 0.086975 | 0.050354 | 0.13733 | 121.582 | 121.6644 | -0.82855 | -0.83313 | 121.5958 | 121.6141 | 121.5042 | 121.637
6476.8281 | 122.6166 | -121.5912 | 0.75989 | -0.17372 | -0.040253 | 0.00024143 | 0.020587 | -0.0014867 | -0.013307 | -0.0045095 | 0.011322 | 0.02411 | 0.013862 | -0.015109 | -0.019651 | 0.025272 | -0.0075025 | -0.1236 | 0.009155 | -0.050354 | -0.032043 | 0.064087 | -0.064087 | 0.054932 | -0.009155 | 0.082397 | -0.059509 | 0.013733 | 0.15106 | 0.091553 | 0.12817 | 121.5408 | -0.75073 | -0.79193 | 121.6553 | 121.6461 | 121.5271 | 0.10529 | -0.013733 | 121.5317 | -0.67749 | -0.74616 | 121.7422 | 121.7194 | 121.6827 | 0.18768 | 0.15106 | 0.11444 | 0.018311 | 0.21057 | 0.073242 | 0.059509 | 0.14191 | 121.6003 | 121.6736 | -0.81024 | -0.8194 | 121.5591 | 121.6049 | 121.4676 | 121.582
6478.5938 | 122.644 | -121.5866 | 0.74158 | -0.13557 | -0.040467 | -0.0023222 | 0.018237 | -0.0055457 | -0.014375 | -0.0068593 | -0.025299 | 0.021119 | 0.016212 | -0.0181 | -0.023069 | 0.025272 | -0.0064343 | -0.07782 | 0.013733 | -0.054932 | 0.064087 | 0.19684 | 0.013733 | 0.11444 | 0.10529 | 0.064087 | -0.041199 | 0.073242 | 0.20599 | 0.15106 | 0.16022 | 121.5317 | -0.72784 | -0.67749 | 121.7834 | 121.701 | 121.6003 | 0.16937 | 0.068665 | 121.5454 | -0.67749 | -0.66834 | 121.7926 | 121.7468 | 121.7377 | 0.20142 | 0.19226 | 0.25177 | 0.11902 | 0.24719 | 0.11444 | 0.068665 | 0.10529 | 121.6003 | 121.6507 | -0.79651 | -0.78278 | 121.6507 | 121.6599 | 121.5088 | 121.6919
6480.2969 | 122.612 | -121.5546 | 0.75989 | -0.22713 | -0.038758 | -0.00082677 | 0.019946 | -0.0023413 | -0.013093 | -0.0045095 | -0.049713 | 0.021546 | 0.014076 | -0.014469 | -0.022856 | 0.02634 | -0.0013073 | -0.068665 | 0.013733 | -0.032043 | 0.032043 | 0.12817 | -0.027466 | 0.086975 | 0.10529 | 0.07782 | -0.050354 | 0.064087 | 0.15564 | 0.10071 | 0.14648 | 121.5225 | -0.74616 | -0.72784 | 121.6827 | 121.6415 | 121.5271 | 0.11902 | 0.004577 | 121.5042 | -0.68207 | -0.6958 | 121.7102 | 121.701 | 121.6553 | 0.19684 | 0.15106 | 0.16022 | 0.064086 | 0.20599 | 0.11444 | 0.045776 | 0.12817 | 121.5683 | 121.6324 | -0.79193 | -0.81024 | 121.5866 | 121.6187 | 121.4859 | 121.6599
6482 | 122.5662 | -121.6095 | 0.75531 | -0.17372 | -0.039826 | 0.00045503 | 0.0208 | -0.00041873 | -0.014802 | -0.0060049 | -0.10159 | 0.024323 | 0.015785 | -0.013187 | -0.020506 | 0.025912 | -0.0032299 | -0.082397 | 0.045776 | -0.09613 | -0.041199 | 0.045776 | -0.068665 | 0.027466 | 0.027466 | 0.10986 | -0.064087 | 0.013733 | 0.10529 | 0.036621 | 0.11444 | 121.5134 | -0.70953 | -0.79651 | 121.6553 | 121.637 | 121.5408 | 0.1236 | 0.027465 | 121.5454 | -0.64545 | -0.74158 | 121.7148 | 121.7239 | 121.6461 | 0.17853 | 0.10071 | 0.14191 | 0.054931 | 0.16937 | 0.07782 | 0.14191 | 0.17395 | 121.6553 | 121.7194 | -0.85144 | -0.8194 | 121.5683 | 121.6232 | 121.5271 | 121.637
6483.75 | 122.5754 | -121.6232 | 0.75989 | -0.074539 | -0.037262 | 2.7834e-05 | 0.019946 | 0.0036401 | -0.015656 | -0.0066457 | -0.09549 | 0.023255 | 0.016212 | -0.010196 | -0.019438 | 0.027621 | -0.0021619 | -0.13275 | 0.041199 | -0.073242 | -0.07782 | 0.009155 | -0.15106 | -0.018311 | -0.041199 | 0.09613 | -0.086975 | 0.009155 | 0.073242 | -0.004578 | 0.091553 | 121.55 | -0.71869 | -0.83771 | 121.6324 | 121.6049 | 121.4722 | 0.054931 | -0.07782 | 121.5363 | -0.66376 | -0.75073 | 121.6965 | 121.7148 | 121.6187 | 0.17853 | 0.082397 | 0.082397 | -0.004578 | 0.16022 | 0.09613 | 0.11444 | 0.1831 | 121.6644 | 121.7194 | -0.83313 | -0.84686 | 121.5454 | 121.6324 | 121.4905 | 121.582
6485.4531 | 122.5662 | -121.6049 | 0.75989 | -0.097427 | -0.04068 | -0.0036038 | 0.019732 | 0.0010767 | -0.01352 | -0.0042959 | -0.11075 | 0.023896 | 0.014289 | -0.011905 | -0.018583 | 0.025485 | 0.0023243 | -0.09613 | 0.045776 | -0.073242 | -0.036621 | 0.064087 | -0.07782 | 0.018311 | 0.027466 | 0.10986 | -0.064087 | 0.013733 | 0.11444 | 0.041199 | 0.10529 | 121.5317 | -0.71411 | -0.79651 | 121.669 | 121.6232 | 121.5271 | 0.091553 | -0.004578 | 121.5408 | -0.65002 | -0.74616 | 121.7194 | 121.7102 | 121.6461 | 0.16937 | 0.10529 | 0.13733 | 0.036621 | 0.17853 | 0.07782 | 0.11902 | 0.17395 | 121.6507 | 121.7148 | -0.83313 | -0.82398 | 121.5683 | 121.6187 | 121.5088 | 121.6324
6487.1562 | 122.5296 | -121.6507 | 0.7782 | -0.15083 | -0.040467 | -0.0042448 | 0.018237 | 0.0040675 | -0.014802 | -0.0017325 | -0.074127 | 0.024537 | 0.015144 | -0.0091281 | -0.019224 | 0.026981 | -0.0047253 | -0.13733 | 0.059509 | -0.07782 | -0.10529 | 0 | -0.10986 | -0.013733 | -0.086975 | 0.13275 | -0.086975 | -0.050354 | 0.068665 | -0.004578 | 0.064087 | 121.5729 | -0.71869 | -0.88348 | 121.6507 | 121.637 | 121.5408 | 0.064087 | -0.032043 | 121.5637 | -0.64545 | -0.82855 | 121.7194 | 121.7148 | 121.6461 | 0.15106 | 0.082397 | 0.07782 | -0.027466 | 0.15564 | 0.036621 | 0.13733 | 0.21973 | 121.7102 | 121.7834 | -0.85602 | -0.86517 | 121.5454 | 121.6003 | 121.5134 | 121.5637
6488.8594 | 122.6395 | -121.6278 | 0.74158 | -0.17372 | -0.041107 | 0.0017368 | 0.01546 | -0.0023413 | -0.011811 | -0.0060049 | 0.0052185 | 0.022187 | 0.014503 | -0.020664 | -0.019438 | 0.024417 | -0.0019483 | -0.1236 | 0.009155 | -0.064087 | -0.036621 | 0.07782 | -0.068665 | 0.054932 | 0.027466 | 0.09613 | -0.054932 | 0.045776 | 0.15564 | 0.11444 | 0.12817 | 121.5637 | -0.73242 | -0.7782 | 121.7056 | 121.6827 | 121.5591 | 0.11902 | -0.004578 | 121.5729 | -0.64545 | -0.6958 | 121.7834 | 121.756 | 121.7422 | 0.18311 | 0.16937 | 0.14191 | 0.027466 | 0.21057 | 0.10071 | 0.073242 | 0.15106 | 121.637 | 121.7239 | -0.80566 | -0.79651 | 121.5912 | 121.6736 | 121.5042 | 121.6553
6490.625 | 122.6395 | -121.5912 | 0.75073 | -0.23476 | -0.040039 | -0.00039957 | 0.018237 | 0.0021447 | -0.01053 | -0.0060049 | -0.040558 | 0.022401 | 0.015357 | -0.011478 | -0.021147 | 0.024631 | -0.0017347 | -0.059509 | 0.009155 | -0.050354 | 0.036621 | 0.13275 | -0.027466 | 0.073242 | 0.11444 | 0.068665 | -0.041199 | 0.082397 | 0.17395 | 0.11444 | 0.16937 | 121.5408 | -0.74158 | -0.71411 | 121.7239 | 121.6644 | 121.5637 | 0.1236 | 0.022888 | 121.55 | -0.68207 | -0.66833 | 121.7651 | 121.7606 | 121.7056 | 0.21057 | 0.15564 | 0.18311 | 0.086975 | 0.21515 | 0.1236 | 0.059509 | 0.10986 | 121.6003 | 121.6599 | -0.80109 | -0.79193 | 121.6278 | 121.6736 | 121.5317 | 121.7056
6492.3281 | 122.5296 | -121.6507 | 0.75531 | -0.074539 | -0.042816 | -0.0042448 | 0.019519 | 0.0042811 | -0.012239 | -0.0047231 | -0.086334 | 0.024323 | 0.013648 | -0.014682 | -0.021147 | 0.025272 | -0.0010937 | -0.13733 | 0.054932 | -0.082397 | -0.11444 | -0.018311 | -0.1236 | -0.004578 | -0.073242 | 0.12817 | -0.082397 | -0.050354 | 0.045776 | 0.004578 | 0.068665 | 121.5683 | -0.70038 | -0.86975 | 121.6324 | 121.6461 | 121.5271 | 0.077819 | -0.041199 | 121.5683 | -0.62714 | -0.80566 | 121.6965 | 121.7194 | 121.6553 | 0.15106 | 0.086975 | 0.064086 | -0.032044 | 0.12817 | 0.032043 | 0.13733 | 0.21057 | 121.7056 | 121.7789 | -0.83771 | -0.83771 | 121.5363 | 121.6003 | 121.5134 | 121.5775
6494.0312 | 122.6578 | -121.6095 | 0.71869 | -0.19661 | -0.042603 | -0.0025358 | 0.016528 | -0.0034095 | -0.012666 | -0.0070731 | -0.0039367 | 0.024537 | 0.015998 | -0.015537 | -0.018797 | 0.025699 | -0.0066479 | -0.073242 | 0 | -0.036621 | 0.036621 | 0.17395 | 0.027466 | 0.11444 | 0.10071 | 0.073242 | -0.045776 | 0.059509 | 0.21515 | 0.15106 | 0.15564 | 121.5729 | -0.71869 | -0.68207 | 121.7834 | 121.7239 | 121.637 | 0.15106 | 0.064087 | 121.5637 | -0.64545 | -0.65918 | 121.8246 | 121.7651 | 121.7606 | 0.20142 | 0.19684 | 0.21057 | 0.073242 | 0.26093 | 0.10528 | 0.036621 | 0.11902 | 121.6095 | 121.6827 | -0.75531 | -0.76447 | 121.6461 | 121.669 | 121.5363 | 121.7102
6495.7344 | 122.6303 | -121.6187 | 0.73242 | -0.26527 | -0.038544 | 2.7834e-05 | 0.016101 | 0.00043587 | -0.014375 | -0.0057913 | -0.052765 | 0.023041 | 0.015785 | -0.017032 | -0.02136 | 0.023349 | -0.0047253 | -0.054932 | 0.018311 | -0.018311 | 0.004578 | 0.13275 | -0.032043 | 0.086975 | 0.10986 | 0.082397 | -0.050354 | 0.073242 | 0.15564 | 0.10986 | 0.14648 | 121.6003 | -0.71411 | -0.72784 | 121.7514 | 121.7056 | 121.5866 | 0.10529 | -0.013732 | 121.5683 | -0.65003 | -0.65918 | 121.7743 | 121.7651 | 121.7285 | 0.19684 | 0.16022 | 0.15106 | 0.022889 | 0.20599 | 0.1236 | 0.036622 | 0.13275 | 121.637 | 121.701 | -0.75073 | -0.78278 | 121.6232 | 121.6919 | 121.5637 | 121.7285
6497.4375 | 122.5296 | -121.6461 | 0.76446 | -0.17372 | -0.037903 | -0.00039957 | 0.02016 | 0.0047083 | -0.011811 | -0.0068593 | -0.10464 | 0.02411 | 0.014289 | -0.0134 | -0.019651 | 0.023563 | -0.0053661 | -0.091553 | 0.041199 | -0.07782 | -0.054932 | 0.041199 | -0.09613 | 0.009155 | -0.009155 | 0.11444 | -0.07782 | -0.022888 | 0.068665 | -0.013733 | 0.064087 | 121.5683 | -0.72327 | -0.8194 | 121.6873 | 121.6553 | 121.55 | 0.086975 | -0.01831 | 121.5683 | -0.65002 | -0.78735 | 121.7148 | 121.7102 | 121.6324 | 0.14191 | 0.064087 | 0.11902 | 0.022888 | 0.14649 | 0.054932 | 0.11902 | 0.19226 | 121.6873 | 121.7606 | -0.84228 | -0.84228 | 121.5912 | 121.6232 | 121.5546 | 121.637
6499.1875 | 122.5479 | -121.6324 | 0.77362 | -0.20424 | -0.038117 | 0.00045503 | 0.019519 | 0.0010767 | -0.012025 | -0.0075003 | -0.1077 | 0.026459 | 0.013008 | -0.0069919 | -0.018583 | 0.026126 | -0.0028027 | -0.12817 | 0.050354 | -0.07782 | -0.10529 | -0.022888 | -0.15564 | -0.032043 | -0.054932 | 0.11902 | -0.07782 | -0.027466 | 0.041199 | -0.013733 | 0.068665 | 121.5546 | -0.72327 | -0.87891 | 121.6095 | 121.6003 | 121.4767 | 0.045777 | -0.07782 | 121.5546 | -0.6546 | -0.80109 | 121.6736 | 121.701 | 121.6187 | 0.14649 | 0.064087 | 0.054932 | -0.027466 | 0.11902 | 0.050354 | 0.12817 | 0.19684 | 121.6827 | 121.7514 | -0.85144 | -0.85144 | 121.5271 | 121.6049 | 121.5042 | 121.5775
6500.8906 | 122.58 | -121.6553 | 0.75531 | -0.12794 | -0.040039 | -0.0014676 | 0.018664 | 8.47e-06 | -0.012666 | -0.0064321 | -0.074127 | 0.023682 | 0.01493 | -0.011478 | -0.019438 | 0.025272 | -0.0015209 | -0.09613 | 0.041199 | -0.09613 | -0.041199 | 0.059509 | -0.086975 | 0.022888 | 0.032043 | 0.10071 | -0.073242 | 0.013733 | 0.10071 | 0.032043 | 0.10071 | 121.5591 | -0.71411 | -0.79651 | 121.7148 | 121.6782 | 121.5683 | 0.11902 | 0.009155 | 121.582 | -0.6546 | -0.74158 | 121.756 | 121.756 | 121.6873 | 0.17395 | 0.10529 | 0.15564 | 0.054931 | 0.17395 | 0.086975 | 0.13733 | 0.17395 | 121.6965 | 121.756 | -0.85144 | -0.82855 | 121.6141 | 121.669 | 121.5591 | 121.6873
6502.6406 | 122.6715 | -121.6461 | 0.72327 | -0.18898 | -0.040253 | -0.0010404 | 0.014392 | 0.00043587 | -0.01117 | -0.0051505 | 0.0052185 | 0.022401 | 0.014076 | -0.014469 | -0.020292 | 0.024204 | -0.0023755 | -0.054932 | -0.004578 | -0.027466 | 0.045776 | 0.17395 | 0.027466 | 0.13275 | 0.10986 | 0.064087 | -0.032043 | 0.064087 | 0.21973 | 0.13733 | 0.15106 | 121.6187 | -0.72784 | -0.67749 | 121.8201 | 121.7789 | 121.6736 | 0.16022 | 0.054932 | 121.6141 | -0.65918 | -0.65918 | 121.8658 | 121.7972 | 121.7834 | 0.18311 | 0.16937 | 0.20142 | 0.073242 | 0.25177 | 0.09613 | 0.022888 | 0.09613 | 121.6415 | 121.7102 | -0.75073 | -0.75531 | 121.6919 | 121.7102 | 121.5912 | 121.756
6504.3281 | 122.6532 | -121.637 | 0.72784 | -0.20424 | -0.041535 | 0.00088223 | 0.015887 | 0.0027857 | -0.013093 | -0.0036551 | 0.0021667 | 0.023896 | 0.014289 | -0.012119 | -0.020292 | 0.02634 | -0.0034435 | -0.073242 | 0.018311 | -0.045776 | 0.018311 | 0.15564 | 0.018311 | 0.11444 | 0.12817 | 0.073242 | -0.050354 | 0.07782 | 0.21057 | 0.15564 | 0.17395 | 121.5912 | -0.70953 | -0.70953 | 121.7926 | 121.7514 | 121.6553 | 0.16022 | 0.064087 | 121.5866 | -0.6546 | -0.65002 | 121.8475 | 121.8109 | 121.7926 | 0.2243 | 0.20599 | 0.20142 | 0.064087 | 0.26093 | 0.12817 | 0.064087 | 0.1236 | 121.6553 | 121.7102 | -0.77362 | -0.7782 | 121.6553 | 121.7148 | 121.5637 | 121.7651
6506.0469 | 122.6212 | -121.6324 | 0.72327 | -0.20424 | -0.039826 | -0.0016812 | 0.016742 | 0.0023585 | -0.012239 | -0.0053641 | -0.028351 | 0.022401 | 0.013435 | -0.0093417 | -0.020292 | 0.024417 | -0.0064343 | -0.086975 | 0.013733 | -0.027466 | 0.004578 | 0.12817 | -0.054932 | 0.064087 | 0.054932 | 0.068665 | -0.054932 | 0.045776 | 0.14191 | 0.07782 | 0.11444 | 121.6049 | -0.70953 | -0.71869 | 121.7606 | 121.6965 | 121.5775 | 0.091553 | -0.027466 | 121.5775 | -0.6546 | -0.67749 | 121.7743 | 121.7468 | 121.7102 | 0.16937 | 0.13275 | 0.15564 | 0.032044 | 0.19684 | 0.10071 | 0.041199 | 0.1236 | 121.6461 | 121.701 | -0.75073 | -0.7782 | 121.637 | 121.6782 | 121.5454 | 121.6873
6507.75 | 122.6349 | -121.6095 | 0.72327 | -0.22713 | -0.042176 | -0.001254 | 0.020587 | 0.0027857 | -0.010316 | -0.0057913 | -0.04361 | 0.022614 | 0.015357 | -0.01041 | -0.021574 | 0.025699 | -0.0040845 | -0.064087 | 0.013733 | -0.041199 | 0.022888 | 0.13733 | -0.036621 | 0.07782 | 0.086975 | 0.068665 | -0.059509 | 0.073242 | 0.16022 | 0.09613 | 0.13733 | 121.5683 | -0.70953 | -0.70038 | 121.7468 | 121.6873 | 121.5729 | 0.11902 | 0.004578 | 121.55 | -0.6546 | -0.65002 | 121.7697 | 121.7468 | 121.7056 | 0.19684 | 0.15564 | 0.17853 | 0.064087 | 0.21973 | 0.13275 | 0.054932 | 0.12817 | 121.6232 | 121.6782 | -0.76447 | -0.78278 | 121.6324 | 121.6827 | 121.5454 | 121.6965
6509.4688 | 122.6486 | -121.6278 | 0.72784 | -0.13557 | -0.040467 | -0.00061317 | 0.022082 | -0.0017005 | -0.010743 | -0.0062185 | -0.11075 | 0.023041 | 0.01493 | -0.0082737 | -0.021147 | 0.025912 | -0.0028027 | -0.11444 | 0.054932 | -0.07782 | -0.036621 | 0.041199 | -0.10529 | 0.022888 | 0.036621 | 0.086975 | -0.064087 | 0.054932 | 0.15106 | 0.07782 | 0.15106 | 121.55 | -0.67291 | -0.76447 | 121.669 | 121.6507 | 121.5225 | 0.10071 | -0.027466 | 121.5637 | -0.64087 | -0.67291 | 121.7789 | 121.7789 | 121.7056 | 0.21515 | 0.14191 | 0.11902 | 0.041199 | 0.21515 | 0.11902 | 0.13275 | 0.15106 | 121.6827 | 121.7148 | -0.80566 | -0.79193 | 121.5912 | 121.6827 | 121.5134 | 121.6644
6511.1875 | 122.58 | -121.6507 | 0.75531 | -0.15846 | -0.040894 | -0.0014676 | 0.019946 | 0.0012903 | -0.011384 | -0.0047231 | -0.11685 | 0.024537 | 0.016212 | -0.014682 | -0.021574 | 0.026767 | -0.0028027 | -0.11444 | 0.064087 | -0.082397 | -0.073242 | 0.013733 | -0.086975 | 0 | -0.032043 | 0.11902 | -0.07782 | -0.004578 | 0.086975 | 0.036621 | 0.10529 | 121.5683 | -0.69122 | -0.82855 | 121.6644 | 121.6507 | 121.5637 | 0.082397 | -0.004578 | 121.5729 | -0.63629 | -0.75989 | 121.7377 | 121.756 | 121.6873 | 0.18311 | 0.11444 | 0.09613 | 0.009155 | 0.16479 | 0.073242 | 0.14648 | 0.19684 | 121.7148 | 121.7697 | -0.83771 | -0.83313 | 121.5775 | 121.6461 | 121.5363 | 121.6187
6512.8906 | 122.5388 | -121.669 | 0.75989 | -0.19661 | -0.042176 | -0.00018577 | 0.016528 | -0.0017005 | -0.012025 | -0.0036551 | -0.040558 | 0.021546 | 0.016853 | -0.014896 | -0.020292 | 0.024631 | -0.0015209 | -0.10986 | 0.050354 | -0.054932 | -0.068665 | 0.036621 | -0.091553 | 0.009155 | -0.045776 | 0.1236 | -0.073242 | -0.059509 | 0.073242 | 0.022888 | 0.041199 | 121.6141 | -0.70953 | -0.82855 | 121.7056 | 121.6782 | 121.5775 | 0.064087 | -0.036621 | 121.5958 | -0.63629 | -0.8194 | 121.7422 | 121.7102 | 121.6919 | 0.11444 | 0.09613 | 0.091553 | -0.013733 | 0.14648 | 0.013733 | 0.10529 | 0.19684 | 121.7194 | 121.7926 | -0.81482 | -0.83313 | 121.6003 | 121.6095 | 121.5591 | 121.6232
6514.6406 | 122.5296 | -121.6782 | 0.75989 | -0.18898 | -0.039612 | -0.00018577 | 0.021228 | -0.0019141 | -0.0090342 | -0.0064321 | -0.098541 | 0.022614 | 0.013862 | -0.013828 | -0.019865 | 0.023135 | -0.0036573 | -0.10986 | 0.045776 | -0.082397 | -0.10071 | -0.027466 | -0.16937 | -0.041199 | -0.068665 | 0.11902 | -0.068665 | -0.027466 | 0.050354 | -0.018311 | 0.059509 | 121.5958 | -0.71411 | -0.8606 | 121.6507 | 121.637 | 121.5088 | 0.041198 | -0.086976 | 121.6095 | -0.64087 | -0.78735 | 121.7285 | 121.7377 | 121.6599 | 0.12817 | 0.050354 | 0.054931 | -0.018311 | 0.11902 | 0.041199 | 0.12817 | 0.18768 | 121.7239 | 121.7972 | -0.84228 | -0.82855 | 121.5775 | 121.6507 | 121.5683 | 121.6095
6516.3438 | 122.6395 | -121.6278 | 0.71869 | -0.20424 | -0.03833 | 0.0017368 | 0.01781 | 0.00064947 | -0.011384 | -0.0049367 | -0.077179 | 0.023255 | 0.01493 | -0.0084873 | -0.019224 | 0.026981 | -0.0015209 | -0.10529 | 0.041199 | -0.064087 | -0.022888 | 0.091553 | -0.064087 | 0.054932 | 0.059509 | 0.068665 | -0.045776 | 0.073242 | 0.16479 | 0.10986 | 0.16937 | 121.5637 | -0.67749 | -0.74158 | 121.7194 | 121.6827 | 121.5637 | 0.11902 | 0 | 121.582 | -0.65002 | -0.64545 | 121.7926 | 121.7972 | 121.7377 | 0.21515 | 0.15564 | 0.15564 | 0.041199 | 0.21057 | 0.11902 | 0.10529 | 0.11444 | 121.669 | 121.6965 | -0.78278 | -0.76447 | 121.6049 | 121.701 | 121.5225 | 121.6873
6518.0469 | 122.5388 | -121.6644 | 0.78735 | -0.22713 | -0.036835 | 0.0010958 | 0.018878 | 0.0021447 | -0.012879 | -0.0025869 | -0.11685 | 0.023682 | 0.015998 | -0.015323 | -0.020078 | 0.025272 | -0.0023755 | -0.10071 | 0.045776 | -0.073242 | -0.082397 | 0.013733 | -0.13275 | -0.027466 | -0.036621 | 0.1236 | -0.082397 | -0.045776 | 0.041199 | -0.027466 | 0.050354 | 121.5912 | -0.74158 | -0.86975 | 121.6782 | 121.637 | 121.5317 | 0.045776 | -0.059509 | 121.582 | -0.66376 | -0.83313 | 121.7056 | 121.7148 | 121.637 | 0.13275 | 0.054931 | 0.086975 | -0.009155 | 0.1236 | 0.036621 | 0.11902 | 0.20599 | 121.7102 | 121.788 | -0.8606 | -0.86975 | 121.582 | 121.6187 | 121.5637 | 121.6278
6519.7656 | 122.6212 | -121.6415 | 0.72784 | -0.15846 | -0.041748 | 2.7834e-05 | 0.016955 | -0.0014867 | -0.010743 | -0.0040823 | -0.0039367 | 0.021546 | 0.013648 | -0.019596 | -0.019651 | 0.027408 | -0.0019483 | -0.11444 | 0.013733 | -0.045776 | -0.041199 | 0.068665 | -0.068665 | 0.050354 | -0.009155 | 0.07782 | -0.068665 | 0.018311 | 0.1236 | 0.073242 | 0.11444 | 121.5958 | -0.71411 | -0.76904 | 121.7102 | 121.6919 | 121.5729 | 0.09613 | -0.022889 | 121.5729 | -0.65002 | -0.70953 | 121.7651 | 121.756 | 121.7148 | 0.18311 | 0.14191 | 0.11444 | 0.004577 | 0.19226 | 0.086976 | 0.059509 | 0.14649 | 121.6553 | 121.7194 | -0.77362 | -0.79651 | 121.6003 | 121.6599 | 121.5271 | 121.6324
6521.4688 | 122.5891 | -121.6827 | 0.74158 | -0.15846 | -0.042176 | -0.00018577 | 0.019732 | 0.0012903 | -0.010743 | -0.0064321 | -0.1077 | 0.025178 | 0.015785 | -0.016605 | -0.020292 | 0.024204 | -0.0017347 | -0.082397 | 0.045776 | -0.082397 | -0.032043 | 0.064087 | -0.064087 | 0.022888 | 0.022888 | 0.11444 | -0.059509 | 0 | 0.10071 | 0.050354 | 0.09613 | 121.6003 | -0.6958 | -0.77362 | 121.7468 | 121.7056 | 121.6187 | 0.10528 | 0.01831 | 121.6232 | -0.62714 | -0.74158 | 121.7834 | 121.7789 | 121.7331 | 0.15564 | 0.10986 | 0.14648 | 0.050354 | 0.16022 | 0.059509 | 0.12817 | 0.17395 | 121.7285 | 121.7972 | -0.82397 | -0.80109 | 121.6507 | 121.6827 | 121.6003 | 121.7056
6523.1719 | 122.5388 | -121.6827 | 0.75989 | -0.15846 | -0.041321 | 2.7834e-05 | 0.016314 | -0.00084593 | -0.012666 | -0.0066457 | -0.031403 | 0.022187 | 0.012153 | -0.017032 | -0.019224 | 0.024204 | -0.0010937 | -0.10071 | 0.032043 | -0.054932 | -0.054932 | 0.045776 | -0.073242 | 0.018311 | -0.032043 | 0.11902 | -0.07782 | -0.054932 | 0.064087 | 0.013733 | 0.064087 | 121.6278 | -0.72784 | -0.81482 | 121.7285 | 121.701 | 121.6095 | 0.073243 | -0.01831 | 121.6049 | -0.64087 | -0.81482 | 121.7468 | 121.7468 | 121.6965 | 0.14191 | 0.091553 | 0.10071 | 0 | 0.14191 | 0.022888 | 0.086975 | 0.19684 | 121.7148 | 121.8018 | -0.81482 | -0.83771 | 121.6278 | 121.6278 | 121.582 | 121.6507
6524.9062 | 122.5754 | -121.6965 | 0.75531 | -0.13557 | -0.039185 | 0.00024143 | 0.019946 | 0.0025721 | -0.015229 | -0.0057913 | -0.071076 | 0.023041 | 0.012794 | -0.014469 | -0.020933 | 0.026767 | -0.0019483 | -0.11902 | 0.064087 | -0.09613 | -0.068665 | -0.009155 | -0.091553 | 0.013733 | -0.022888 | 0.11902 | -0.064087 | -0.022888 | 0.086975 | 0.027466 | 0.082397 | 121.6003 | -0.69122 | -0.82398 | 121.6873 | 121.7102 | 121.6049 | 0.10986 | 0.004577 | 121.6324 | -0.63629 | -0.7782 | 121.7834 | 121.7789 | 121.7239 | 0.14648 | 0.091553 | 0.086975 | 0.027465 | 0.15106 | 0.041199 | 0.16022 | 0.18311 | 121.7606 | 121.8155 | -0.85144 | -0.8194 | 121.6278 | 121.6736 | 121.5775 | 121.6736
6526.6094 | 122.5616 | -121.6827 | 0.75531 | -0.13557 | -0.038758 | -0.0038174 | 0.018451 | 0.00022207 | -0.014375 | -0.0036551 | -0.086334 | 0.023469 | 0.016212 | -0.011051 | -0.02136 | 0.025699 | -0.0070751 | -0.13275 | 0.050354 | -0.086975 | -0.09613 | -0.004578 | -0.091553 | 0.004578 | -0.059509 | 0.1236 | -0.086975 | -0.036621 | 0.082397 | 0.027466 | 0.086975 | 121.5958 | -0.70496 | -0.85144 | 121.6782 | 121.6873 | 121.5912 | 0.091553 | -0.004578 | 121.5958 | -0.63171 | -0.79193 | 121.7651 | 121.7697 | 121.7102 | 0.17395 | 0.11444 | 0.082397 | -0.009155 | 0.16937 | 0.050354 | 0.13733 | 0.21057 | 121.7331 | 121.8063 | -0.84229 | -0.84229 | 121.5866 | 121.6461 | 121.55 | 121.6232
6528.3281 | 122.6395 | -121.6278 | 0.71869 | -0.21187 | -0.037262 | -0.0016812 | 0.017169 | -0.0027685 | -0.0088206 | -0.0049367 | -0.022247 | 0.021119 | 0.015571 | -0.013828 | -0.018583 | 0.025058 | -0.0049389 | -0.068665 | 0.018311 | -0.022888 | 0.018311 | 0.14648 | -0.027466 | 0.073242 | 0.09613 | 0.082397 | -0.041199 | 0.059509 | 0.14648 | 0.09613 | 0.13275 | 121.6049 | -0.70038 | -0.70038 | 121.7743 | 121.701 | 121.6003 | 0.09613 | -0.004578 | 121.5866 | -0.63629 | -0.65918 | 121.7743 | 121.7606 | 121.7239 | 0.17395 | 0.13733 | 0.16937 | 0.041199 | 0.18768 | 0.10071 | 0.041199 | 0.1236 | 121.6461 | 121.7102 | -0.74158 | -0.75989 | 121.6461 | 121.6873 | 121.5591 | 121.7239
6530.0781 | 122.5342 | -121.6461 | 0.74616 | -0.15083 | -0.037689 | -0.0010404 | 0.02016 | -0.0012731 | -0.0098886 | -0.0047231 | -0.098541 | 0.023255 | 0.014289 | -0.0050693 | -0.019651 | 0.02399 | -0.0028027 | -0.13733 | 0.050354 | -0.086975 | -0.11444 | -0.041199 | -0.17853 | -0.041199 | -0.11444 | 0.12817 | -0.07782 | -0.050354 | 0.018311 | -0.041199 | 0.064087 | 121.5591 | -0.6958 | -0.8606 | 121.6049 | 121.6049 | 121.4676 | 0.045776 | -0.091553 | 121.5683 | -0.61798 | -0.79651 | 121.6644 | 121.7102 | 121.6049 | 0.14191 | 0.036621 | 0.045776 | -0.027466 | 0.096131 | 0.027466 | 0.13733 | 0.20599 | 121.6965 | 121.7743 | -0.83313 | -0.82398 | 121.5317 | 121.5958 | 121.5088 | 121.5317
6531.7812 | 122.5662 | -121.7056 | 0.75073 | -0.15083 | -0.039826 | -0.00082677 | 0.018664 | 0.00086307 | -0.01352 | -0.0032277 | -0.028351 | 0.022401 | 0.014076 | -0.011264 | -0.01901 | 0.025912 | 0.0031787 | -0.10986 | 0.027466 | -0.07782 | -0.059509 | 0.041199 | -0.07782 | 0.018311 | -0.041199 | 0.11444 | -0.073242 | -0.054932 | 0.059509 | 0.022888 | 0.054932 | 121.6278 | -0.72327 | -0.81024 | 121.7468 | 121.7239 | 121.6278 | 0.096131 | 0 | 121.6324 | -0.63629 | -0.80566 | 121.7651 | 121.7606 | 121.7285 | 0.12817 | 0.09613 | 0.11902 | 0.018311 | 0.13275 | 0.01831 | 0.10529 | 0.18768 | 121.7331 | 121.8201 | -0.82855 | -0.82397 | 121.6461 | 121.6507 | 121.5958 | 121.6644
6533.5469 | 122.6532 | -121.6507 | 0.70038 | -0.20424 | -0.038971 | 0.00024143 | 0.016101 | 0.00086307 | -0.011811 | -0.0042959 | -0.064972 | 0.02411 | 0.014076 | -0.021518 | -0.019224 | 0.025699 | -0.0017347 | -0.064087 | -0.004578 | -0.004578 | 0.013733 | 0.15106 | -0.027466 | 0.07782 | 0.09613 | 0.068665 | -0.054932 | 0.068665 | 0.16479 | 0.10986 | 0.16022 | 121.6461 | -0.70496 | -0.68664 | 121.8018 | 121.7285 | 121.6232 | 0.082398 | -0.022888 | 121.5958 | -0.63171 | -0.63171 | 121.8155 | 121.8109 | 121.7606 | 0.21515 | 0.16479 | 0.15564 | 0.018311 | 0.21973 | 0.1236 | 0 | 0.1236 | 121.6461 | 121.7194 | -0.70496 | -0.75531 | 121.6644 | 121.7194 | 121.5866 | 121.7468
6535.2969 | 122.6761 | -121.6278 | 0.70953 | -0.18135 | -0.042176 | -0.0027494 | 0.015674 | -0.0025549 | -0.012025 | -0.0057913 | 0.0082703 | 0.023682 | 0.016639 | -0.014041 | -0.02136 | 0.024844 | -0.0028027 | -0.10986 | 0.032043 | -0.054932 | -0.004578 | 0.12817 | -0.004578 | 0.11444 | 0.073242 | 0.068665 | -0.045776 | 0.064087 | 0.18768 | 0.14191 | 0.17853 | 121.5729 | -0.67749 | -0.71411 | 121.756 | 121.7422 | 121.6232 | 0.16937 | 0.050354 | 121.582 | -0.64087 | -0.64545 | 121.8155 | 121.8063 | 121.7697 | 0.2243 | 0.18768 | 0.18311 | 0.050354 | 0.23346 | 0.10986 | 0.086975 | 0.11444 | 121.6599 | 121.6965 | -0.76447 | -0.75531 | 121.6232 | 121.6919 | 121.5179 | 121.701
6537.0312 | 122.6669 | -121.6507 | 0.69122 | -0.19661 | -0.038758 | 0.00045503 | 0.018451 | 0.0012903 | -0.01117 | -0.0028005 | -0.080231 | 0.02475 | 0.015357 | -0.011051 | -0.021787 | 0.028049 | -0.00066651 | -0.050354 | 0.013733 | -0.036621 | 0.009155 | 0.1236 | -0.018311 | 0.082397 | 0.091553 | 0.073242 | -0.064087 | 0.086975 | 0.16937 | 0.11902 | 0.16937 | 121.6141 | -0.67749 | -0.68207 | 121.7743 | 121.7331 | 121.6324 | 0.11902 | 0.01831 | 121.5866 | -0.61798 | -0.60425 | 121.8201 | 121.8201 | 121.7697 | 0.23346 | 0.18311 | 0.16022 | 0.045776 | 0.23346 | 0.15106 | 0.050354 | 0.13733 | 121.6644 | 121.7239 | -0.72784 | -0.75531 | 121.6599 | 121.7377 | 121.6003 | 121.7422
6538.7344 | 122.5845 | -121.6919 | 0.75531 | -0.18135 | -0.039826 | 0.00066863 | 0.021014 | 0.0049219 | -0.009675 | -0.0062185 | -0.098541 | 0.024537 | 0.015571 | -0.0074191 | -0.021574 | 0.024417 | -0.0062207 | -0.086975 | 0.041199 | -0.068665 | -0.032043 | 0.068665 | -0.07782 | 0.032043 | 0.027466 | 0.10529 | -0.054932 | 0.009155 | 0.091553 | 0.027466 | 0.10529 | 121.6232 | -0.71411 | -0.78735 | 121.7606 | 121.7239 | 121.6141 | 0.10071 | -0.009155 | 121.637 | -0.65002 | -0.74616 | 121.7834 | 121.7972 | 121.7194 | 0.16022 | 0.082398 | 0.13733 | 0.036622 | 0.14649 | 0.064087 | 0.10986 | 0.16022 | 121.7331 | 121.7972 | -0.82398 | -0.81024 | 121.6599 | 121.7011 | 121.6049 | 121.7194
6540.4688 | 122.6578 | -121.6507 | 0.72784 | -0.15846 | -0.04068 | -0.0025358 | 0.017382 | 0.00022207 | -0.012452 | -0.0072867 | -0.028351 | 0.023896 | 0.017066 | -0.018314 | -0.020719 | 0.024631 | -0.0057935 | -0.07782 | 0.013733 | -0.054932 | 0.054932 | 0.16479 | 0.004578 | 0.11444 | 0.091553 | 0.082397 | -0.045776 | 0.050354 | 0.18768 | 0.12817 | 0.14648 | 121.5958 | -0.71411 | -0.67291 | 121.8155 | 121.7651 | 121.6553 | 0.16937 | 0.05951 | 121.6049 | -0.64545 | -0.67749 | 121.8384 | 121.7972 | 121.7789 | 0.19226 | 0.17395 | 0.21973 | 0.10986 | 0.23346 | 0.09613 | 0.068665 | 0.12817 | 121.6644 | 121.7331 | -0.78278 | -0.77362 | 121.7056 | 121.701 | 121.5729 | 121.7422
6542.1719 | 122.7081 | -121.6415 | 0.73242 | -0.15083 | -0.039185 | 0.00024143 | 0.017169 | 0.00022207 | -0.013947 | -0.0045095 | -0.0039367 | 0.021546 | 0.014717 | -0.011692 | -0.020078 | 0.023563 | -0.0045117 | -0.064087 | 0.013733 | -0.064087 | 0.022888 | 0.17395 | 0.013733 | 0.13733 | 0.12817 | 0.068665 | -0.036621 | 0.091553 | 0.21515 | 0.15106 | 0.15106 | 121.5775 | -0.71869 | -0.70953 | 121.8155 | 121.7789 | 121.6553 | 0.20142 | 0.07782 | 121.6049 | -0.66376 | -0.64087 | 121.8567 | 121.7926 | 121.7926 | 0.18768 | 0.18768 | 0.23804 | 0.086975 | 0.25177 | 0.12817 | 0.07782 | 0.10529 | 121.6553 | 121.7102 | -0.79651 | -0.76904 | 121.6644 | 121.7331 | 121.5775 | 121.7697
6543.875 | 122.6715 | -121.6507 | 0.70038 | -0.2195 | -0.035981 | 0.00066863 | 0.0208 | 0.00043587 | -0.012239 | -0.0051505 | -0.071076 | 0.022401 | 0.014503 | -0.012119 | -0.020506 | 0.025912 | -0.0047253 | -0.10071 | 0.036621 | -0.07782 | -0.027466 | 0.07782 | -0.07782 | 0.045776 | 0.059509 | 0.086975 | -0.059509 | 0.064087 | 0.14648 | 0.10071 | 0.16022 | 121.5729 | -0.66376 | -0.72784 | 121.7285 | 121.6965 | 121.5729 | 0.1236 | 0 | 121.5912 | -0.6134 | -0.63629 | 121.7972 | 121.8109 | 121.7514 | 0.21973 | 0.16022 | 0.15564 | 0.050354 | 0.20599 | 0.1236 | 0.11444 | 0.14648 | 121.6873 | 121.7377 | -0.7782 | -0.75989 | 121.6232 | 121.7148 | 121.55 | 121.7102
6545.5781 | 122.5525 | -121.7102 | 0.74158 | -0.13557 | -0.039398 | -0.0027494 | 0.019305 | -0.0019141 | -0.015016 | -0.0053641 | -0.064972 | 0.026246 | 0.015357 | -0.0091281 | -0.018797 | 0.024631 | 0.00061529 | -0.14648 | 0.050354 | -0.09613 | -0.10071 | -0.018311 | -0.10986 | -0.009155 | -0.07782 | 0.1236 | -0.082397 | -0.054932 | 0.054932 | 0 | 0.059509 | 121.6141 | -0.69122 | -0.84229 | 121.6919 | 121.701 | 121.6003 | 0.086975 | -0.013733 | 121.6278 | -0.61798 | -0.79651 | 121.7651 | 121.7697 | 121.7102 | 0.14191 | 0.082397 | 0.077819 | -0.004578 | 0.13733 | 0.027465 | 0.14648 | 0.20599 | 121.7606 | 121.8338 | -0.83771 | -0.82397 | 121.6095 | 121.6553 | 121.5637 | 121.6324
6547.2812 | 122.5616 | -121.6965 | 0.72784 | -0.2195 | -0.038971 | -0.00039957 | 0.021441 | 0.0051355 | -0.010102 | -0.0040823 | -0.080231 | 0.025178 | 0.015357 | -0.014255 | -0.021147 | 0.025485 | -0.0047253 | -0.14191 | 0.050354 | -0.086975 | -0.10529 | -0.013733 | -0.15106 | -0.032043 | -0.032043 | 0.10529 | -0.09613 | -0.041199 | 0.050354 | -0.009155 | 0.086975 | 121.6095 | -0.67749 | -0.83313 | 121.6827 | 121.6644 | 121.5454 | 0.054932 | -0.064087 | 121.6003 | -0.62256 | -0.76904 | 121.7468 | 121.7834 | 121.6873 | 0.1831 | 0.086975 | 0.073242 | -0.018311 | 0.14648 | 0.054931 | 0.13733 | 0.20142 | 121.7468 | 121.8018 | -0.81482 | -0.82397 | 121.5912 | 121.6553 | 121.5546 | 121.6644
6548.9844 | 122.58 | -121.701 | 0.72327 | -0.082169 | -0.039826 | -0.00061317 | 0.020587 | 0.0047083 | -0.011384 | -0.0036551 | -0.1077 | 0.023469 | 0.015571 | -0.014041 | -0.020719 | 0.025912 | -0.0025891 | -0.086975 | 0.050354 | -0.059509 | -0.045776 | 0.064087 | -0.091553 | 0.027466 | 0.009155 | 0.09613 | -0.068665 | 0.004578 | 0.086975 | 0.018311 | 0.09613 | 121.6415 | -0.67291 | -0.76904 | 121.7651 | 121.7285 | 121.6095 | 0.086975 | -0.032044 | 121.6324 | -0.62714 | -0.71869 | 121.788 | 121.7972 | 121.7194 | 0.16479 | 0.086976 | 0.1236 | 0.013733 | 0.15564 | 0.073243 | 0.10986 | 0.16479 | 121.7514 | 121.7972 | -0.78278 | -0.79193 | 121.6553 | 121.7056 | 121.6141 | 121.7102
6550.7188 | 122.6669 | -121.6507 | 0.70953 | -0.18135 | -0.037689 | 0.00045503 | 0.018023 | 0.00043587 | -0.012239 | -0.0057913 | -0.049713 | 0.022614 | 0.015571 | -0.014682 | -0.020933 | 0.021854 | -0.0042981 | -0.059509 | 0.022888 | -0.032043 | 0.018311 | 0.14648 | -0.027466 | 0.086975 | 0.09613 | 0.050354 | -0.041199 | 0.091553 | 0.17395 | 0.1236 | 0.15564 | 121.6187 | -0.68665 | -0.69122 | 121.7972 | 121.7377 | 121.6232 | 0.11902 | 0.004577 | 121.6095 | -0.65918 | -0.61798 | 121.8246 | 121.8063 | 121.7743 | 0.19684 | 0.16479 | 0.17853 | 0.050354 | 0.21515 | 0.13275 | 0.054931 | 0.091553 | 121.6736 | 121.701 | -0.74158 | -0.75073 | 121.669 | 121.7422 | 121.5912 | 121.7468
6552.4062 | 122.5937 | -121.6873 | 0.70496 | -0.17372 | -0.040039 | -0.0016812 | 0.019519 | -0.0034095 | -0.014375 | -0.0028005 | -0.083283 | 0.022614 | 0.015785 | -0.0025059 | -0.019224 | 0.025485 | -0.0025891 | -0.12817 | 0.054932 | -0.086975 | -0.068665 | 0.009155 | -0.086975 | 0.013733 | -0.041199 | 0.10071 | -0.073242 | -0.018311 | 0.09613 | 0.036621 | 0.10071 | 121.6003 | -0.65002 | -0.77362 | 121.6965 | 121.701 | 121.6003 | 0.10071 | 0 | 121.6141 | -0.60425 | -0.72327 | 121.7834 | 121.788 | 121.7239 | 0.17395 | 0.10986 | 0.09613 | 0.01831 | 0.16937 | 0.054931 | 0.14191 | 0.17395 | 121.7422 | 121.788 | -0.79193 | -0.7782 | 121.6187 | 121.669 | 121.5591 | 121.6461
6554.1094 | 122.5662 | -121.7239 | 0.72327 | -0.18135 | -0.040467 | -0.0031766 | 0.018237 | -0.0023413 | -0.012879 | -0.0053641 | -0.034454 | 0.022614 | 0.015571 | -0.018314 | -0.018583 | 0.024204 | -0.0047253 | -0.12817 | 0.022888 | -0.073242 | -0.10071 | 0.018311 | -0.086975 | 0.004578 | -0.050354 | 0.10986 | -0.091553 | -0.059509 | 0.059509 | -0.004578 | 0.059509 | 121.6507 | -0.70038 | -0.82398 | 121.7422 | 121.7285 | 121.637 | 0.07782 | -0.013733 | 121.6324 | -0.6134 | -0.78278 | 121.7834 | 121.7834 | 121.7194 | 0.15106 | 0.086975 | 0.091553 | -0.027466 | 0.15106 | 0.032044 | 0.09613 | 0.20142 | 121.7468 | 121.8338 | -0.79651 | -0.81482 | 121.6232 | 121.6644 | 121.5958 | 121.6736
6555.8125 | 122.6212 | -121.6782 | 0.71869 | -0.2195 | -0.040039 | 0.00066863 | 0.018023 | -0.0034095 | -0.012879 | -0.0017325 | -0.013092 | 0.023469 | 0.016426 | -0.019168 | -0.020719 | 0.024844 | -0.0010937 | -0.11444 | 0.009155 | -0.045776 | -0.013733 | 0.10071 | -0.068665 | 0.054932 | 0.027466 | 0.068665 | -0.059509 | 0.018311 | 0.14191 | 0.068665 | 0.1236 | 121.6324 | -0.70953 | -0.73242 | 121.7789 | 121.7331 | 121.6095 | 0.10071 | -0.022889 | 121.6187 | -0.65002 | -0.70038 | 121.8201 | 121.8018 | 121.7468 | 0.1831 | 0.12817 | 0.14648 | 0.032043 | 0.20142 | 0.07782 | 0.054931 | 0.12817 | 121.6873 | 121.7468 | -0.76447 | -0.7782 | 121.6644 | 121.6965 | 121.5637 | 121.7056
6557.5156 | 122.6852 | -121.6644 | 0.71869 | -0.18898 | -0.03833 | -0.0021084 | 0.017169 | 0.0010767 | -0.011384 | -0.0051505 | -0.058869 | 0.021119 | 0.014289 | -0.018741 | -0.022001 | 0.026126 | -0.0053661 | -0.059509 | 0.027466 | -0.054932 | 0.013733 | 0.12817 | -0.032043 | 0.073242 | 0.09613 | 0.091553 | -0.041199 | 0.07782 | 0.16479 | 0.10529 | 0.17853 | 121.6095 | -0.69122 | -0.70496 | 121.7926 | 121.7377 | 121.6324 | 0.12817 | 0.022889 | 121.6232 | -0.62714 | -0.64087 | 121.8292 | 121.843 | 121.7697 | 0.21973 | 0.14649 | 0.18311 | 0.068665 | 0.20599 | 0.11902 | 0.082398 | 0.13275 | 121.6919 | 121.756 | -0.77362 | -0.75989 | 121.6782 | 121.7422 | 121.6049 | 121.7606
6559.2344 | 122.6807 | -121.669 | 0.68665 | -0.19661 | -0.036194 | 0.00045503 | 0.019091 | 0.0042811 | -0.013093 | -0.0034415 | -0.077179 | 0.022401 | 0.01493 | -0.013614 | -0.020078 | 0.026553 | -0.0030163 | -0.050354 | 0.027466 | -0.045776 | 0.022888 | 0.11444 | -0.022888 | 0.064087 | 0.091553 | 0.073242 | -0.041199 | 0.091553 | 0.17853 | 0.10986 | 0.17395 | 121.6232 | -0.65918 | -0.66376 | 121.7834 | 121.7331 | 121.6461 | 0.10986 | 0.022888 | 121.6278 | -0.6134 | -0.59509 | 121.8475 | 121.843 | 121.7789 | 0.21515 | 0.15106 | 0.16022 | 0.068664 | 0.21973 | 0.13275 | 0.073242 | 0.11444 | 121.6965 | 121.7422 | -0.73242 | -0.72784 | 121.6919 | 121.7606 | 121.6187 | 121.7606
6560.9375 | 122.6578 | -121.6873 | 0.71869 | -0.15846 | -0.039185 | -0.001254 | 0.016528 | -0.0019141 | -0.01352 | -0.0032277 | -0.025299 | 0.019837 | 0.014717 | -0.018314 | -0.022642 | 0.025699 | -0.0025891 | -0.068665 | -0.004578 | -0.045776 | 0.032043 | 0.13733 | 0 | 0.086975 | 0.068665 | 0.07782 | -0.041199 | 0.027466 | 0.15564 | 0.12817 | 0.13275 | 121.6415 | -0.72327 | -0.68665 | 121.8246 | 121.7743 | 121.6873 | 0.13275 | 0.045776 | 121.6461 | -0.64087 | -0.69122 | 121.843 | 121.8201 | 121.8155 | 0.17395 | 0.16937 | 0.18311 | 0.077819 | 0.19684 | 0.068665 | 0.041198 | 0.11902 | 121.6827 | 121.7651 | -0.76447 | -0.75989 | 121.7194 | 121.7148 | 121.6187 | 121.756
6562.6406 | 122.6852 | -121.637 | 0.70496 | -0.19661 | -0.040039 | -0.00018577 | 0.016314 | -0.0038367 | -0.012666 | -0.0023733 | -0.0069885 | 0.021546 | 0.018348 | -0.0097689 | -0.023924 | 0.024844 | -0.00045291 | -0.064087 | 0.018311 | -0.054932 | 0.036621 | 0.17395 | 0.022888 | 0.13275 | 0.13275 | 0.07782 | -0.036621 | 0.068665 | 0.20599 | 0.15564 | 0.16022 | 121.582 | -0.68665 | -0.66834 | 121.8109 | 121.7697 | 121.6599 | 0.18768 | 0.07782 | 121.6003 | -0.62714 | -0.63629 | 121.843 | 121.7972 | 121.7926 | 0.19684 | 0.19226 | 0.22888 | 0.091553 | 0.24262 | 0.10529 | 0.073243 | 0.11444 | 121.6553 | 121.7148 | -0.75989 | -0.74158 | 121.6736 | 121.7056 | 121.5729 | 121.7697
6564.3281 | 122.6761 | -121.6736 | 0.70038 | -0.18898 | -0.038971 | 0.00024143 | 0.019732 | -0.00020513 | -0.012025 | -0.0068593 | -0.055817 | 0.02176 | 0.01493 | -0.01575 | -0.020292 | 0.025058 | -0.0040845 | -0.064087 | 0.022888 | -0.050354 | 0.018311 | 0.12817 | -0.041199 | 0.073242 | 0.086975 | 0.073242 | -0.045776 | 0.082397 | 0.16479 | 0.1236 | 0.17853 | 121.6232 | -0.67749 | -0.68207 | 121.8018 | 121.7468 | 121.6324 | 0.1236 | 0.009155 | 121.6278 | -0.62714 | -0.61798 | 121.8384 | 121.8521 | 121.7972 | 0.2243 | 0.16937 | 0.17853 | 0.068665 | 0.21057 | 0.12817 | 0.073242 | 0.11902 | 121.6965 | 121.7468 | -0.75073 | -0.74615 | 121.6919 | 121.756 | 121.6095 | 121.7606
6566.0938 | 122.6669 | -121.6782 | 0.70038 | -0.17372 | -0.041748 | -0.00039957 | 0.015887 | -0.00084593 | -0.013947 | -0.0028005 | -0.022247 | 0.023255 | 0.015998 | -0.015964 | -0.020078 | 0.025058 | -0.0062207 | -0.10986 | 0.041199 | -0.054932 | -0.041199 | 0.073242 | -0.054932 | 0.059509 | 0.027466 | 0.091553 | -0.064087 | 0.032043 | 0.16022 | 0.11444 | 0.14191 | 121.6232 | -0.65918 | -0.74158 | 121.7514 | 121.7377 | 121.6232 | 0.11444 | 0 | 121.6141 | -0.60882 | -0.66833 | 121.8384 | 121.8201 | 121.7926 | 0.20599 | 0.17853 | 0.12817 | 0.013733 | 0.2243 | 0.09613 | 0.096131 | 0.15564 | 121.7194 | 121.7697 | -0.75531 | -0.76446 | 121.637 | 121.7102 | 121.5683 | 121.7056
6567.7969 | 122.6807 | -121.6736 | 0.70496 | -0.20424 | -0.037689 | 0.00066863 | 0.019732 | 0.0010767 | -0.012025 | -0.0045095 | -0.083283 | 0.021332 | 0.01493 | -0.0093417 | -0.020719 | 0.024844 | -0.00023931 | -0.045776 | 0.022888 | -0.059509 | 0.027466 | 0.12817 | -0.045776 | 0.07782 | 0.10986 | 0.07782 | -0.041199 | 0.10071 | 0.18768 | 0.11902 | 0.15564 | 121.6141 | -0.68207 | -0.67749 | 121.8018 | 121.7514 | 121.6278 | 0.13733 | 0.013733 | 121.6324 | -0.62714 | -0.60425 | 121.8613 | 121.8292 | 121.7926 | 0.19684 | 0.16022 | 0.18768 | 0.086975 | 0.22888 | 0.14191 | 0.082397 | 0.11902 | 121.6965 | 121.7514 | -0.76447 | -0.74616 | 121.7011 | 121.7743 | 121.6278 | 121.7834
6569.5156 | 122.6761 | -121.6782 | 0.68207 | -0.2195 | -0.040467 | -0.00039957 | 0.01546 | -0.0029821 | -0.010957 | -0.0047231 | -0.0039367 | 0.022401 | 0.016853 | -0.013614 | -0.020933 | 0.022922 | -0.0068615 | -0.10986 | 0.013733 | -0.054932 | 0 | 0.10071 | -0.027466 | 0.09613 | 0.07782 | 0.082397 | -0.054932 | 0.059509 | 0.17853 | 0.13275 | 0.15106 | 121.6232 | -0.66834 | -0.68207 | 121.7789 | 121.7743 | 121.6507 | 0.15106 | 0.027466 | 121.6232 | -0.59967 | -0.62256 | 121.8567 | 121.8292 | 121.8109 | 0.20599 | 0.18768 | 0.15564 | 0.054932 | 0.23346 | 0.11444 | 0.068665 | 0.13733 | 121.6919 | 121.7606 | -0.737 | -0.737 | 121.6782 | 121.7377 | 121.5683 | 121.756
6571.2188 | 122.6486 | -121.6873 | 0.70953 | -0.20424 | -0.037903 | -0.00082677 | 0.0208 | -0.0042639 | -0.010957 | -0.0062185 | -0.13211 | 0.025391 | 0.012367 | -0.012332 | -0.022856 | 0.02634 | -0.0051525 | -0.13275 | 0.036621 | -0.091553 | -0.059509 | 0.013733 | -0.11902 | -0.009155 | 0 | 0.10986 | -0.059509 | 0.032043 | 0.11444 | 0.064087 | 0.14191 | 121.5958 | -0.67291 | -0.76904 | 121.701 | 121.6782 | 121.5683 | 0.082398 | -0.027466 | 121.6278 | -0.59967 | -0.67749 | 121.8018 | 121.8292 | 121.7514 | 0.20142 | 0.1236 | 0.10529 | 0.032044 | 0.17395 | 0.091552 | 0.12817 | 0.16937 | 121.7239 | 121.7972 | -0.80109 | -0.76904 | 121.6278 | 121.7194 | 121.5546 | 121.6873
6572.9375 | 122.6944 | -121.6553 | 0.70496 | -0.16609 | -0.041962 | -0.0023222 | 0.016101 | -0.0017005 | -0.012666 | -0.0040823 | -0.04361 | 0.024964 | 0.014503 | -0.011264 | -0.020506 | 0.025058 | -0.0038709 | -0.082397 | 0.041199 | -0.054932 | 0.027466 | 0.16937 | 0.004578 | 0.10986 | 0.09613 | 0.082397 | -0.054932 | 0.073242 | 0.20142 | 0.14191 | 0.14191 | 121.6003 | -0.66376 | -0.67749 | 121.8246 | 121.7651 | 121.6599 | 0.16479 | 0.05951 | 121.6003 | -0.62256 | -0.63171 | 121.8567 | 121.7972 | 121.7972 | 0.19684 | 0.19684 | 0.22431 | 0.082398 | 0.25635 | 0.12817 | 0.096131 | 0.13733 | 121.6965 | 121.7377 | -0.75989 | -0.75989 | 121.6827 | 121.7285 | 121.5729 | 121.7514
6574.6719 | 122.5525 | -121.7102 | 0.73242 | -0.13557 | -0.037262 | -0.00082677 | 0.020587 | 0.0038537 | -0.01053 | -0.0047231 | -0.12906 | 0.020692 | 0.017066 | -0.01575 | -0.020292 | 0.025699 | -0.0019483 | -0.13733 | 0.050354 | -0.09613 | -0.10529 | -0.036621 | -0.16937 | -0.027466 | -0.064087 | 0.13275 | -0.07782 | -0.041199 | 0.036621 | -0.032043 | 0.054932 | 121.6141 | -0.68207 | -0.83771 | 121.6736 | 121.6827 | 121.5408 | 0.068664 | -0.073243 | 121.6324 | -0.59967 | -0.77362 | 121.7468 | 121.7651 | 121.6782 | 0.13275 | 0.045777 | 0.059509 | -0.009156 | 0.11444 | 0.036621 | 0.14648 | 0.21057 | 121.7606 | 121.843 | -0.82855 | -0.81024 | 121.6049 | 121.669 | 121.5729 | 121.6461
6576.375 | 122.5891 | -121.7194 | 0.72784 | -0.1432 | -0.038544 | 2.7834e-05 | 0.022296 | 0.00086307 | -0.012452 | -0.0038687 | -0.13211 | 0.024537 | 0.014717 | -0.011051 | -0.020078 | 0.025699 | -0.0013073 | -0.10071 | 0.045776 | -0.068665 | -0.041199 | 0.064087 | -0.064087 | 0.022888 | 0.022888 | 0.10986 | -0.068665 | 0 | 0.10986 | 0.036621 | 0.10071 | 121.6507 | -0.68207 | -0.76904 | 121.7834 | 121.7422 | 121.6553 | 0.091553 | 0.004578 | 121.6507 | -0.61798 | -0.72784 | 121.8292 | 121.8201 | 121.756 | 0.16937 | 0.10529 | 0.13275 | 0.027466 | 0.17853 | 0.068665 | 0.11444 | 0.17853 | 121.7651 | 121.8292 | -0.79651 | -0.79651 | 121.6782 | 121.7194 | 121.6187 | 121.7422
6578.0781 | 122.5571 | -121.7606 | 0.73242 | -0.15083 | -0.042176 | -0.0018948 | 0.016528 | -0.0031957 | -0.010957 | -0.0051505 | -0.064972 | 0.021546 | 0.015571 | -0.014255 | -0.019438 | 0.025485 | -0.0049389 | -0.15106 | 0.059509 | -0.086975 | -0.10071 | 0.009155 | -0.11902 | 0 | -0.059509 | 0.11902 | -0.09613 | -0.068665 | 0.064087 | 0.004578 | 0.054932 | 121.6736 | -0.67291 | -0.83313 | 121.7697 | 121.7606 | 121.6415 | 0.086975 | -0.032044 | 121.6644 | -0.6134 | -0.80109 | 121.8246 | 121.8155 | 121.7651 | 0.15106 | 0.10071 | 0.09613 | -0.013733 | 0.16022 | 0.027465 | 0.14648 | 0.21515 | 121.8201 | 121.8796 | -0.8194 | -0.82855 | 121.6599 | 121.6919 | 121.6095 | 121.701
6579.7812 | 122.6303 | -121.7102 | 0.68665 | -0.21187 | -0.044312 | 0.00024143 | 0.016528 | 0.0027857 | -0.013307 | -0.0038687 | -0.013092 | 0.022828 | 0.014717 | -0.02045 | -0.018797 | 0.024631 | -0.0060071 | -0.10986 | 0.032043 | -0.050354 | -0.050354 | 0.073242 | -0.07782 | 0.054932 | -0.009155 | 0.091553 | -0.073242 | 0.009155 | 0.14191 | 0.091553 | 0.11444 | 121.6599 | -0.6546 | -0.737 | 121.7834 | 121.7651 | 121.6324 | 0.10529 | -0.027466 | 121.637 | -0.59509 | -0.67749 | 121.8521 | 121.8246 | 121.8018 | 0.18768 | 0.16479 | 0.1236 | 0 | 0.21515 | 0.082397 | 0.082397 | 0.16479 | 121.7422 | 121.8018 | -0.737 | -0.75989 | 121.6599 | 121.7194 | 121.6003 | 121.701
6581.4844 | 122.5845 | -121.7194 | 0.72784 | -0.20424 | -0.039185 | -0.001254 | 0.020587 | 0.0015039 | -0.011811 | -0.0077139 | -0.1077 | 0.023041 | 0.016853 | -0.013187 | -0.02136 | 0.026767 | -0.0038709 | -0.12817 | 0.068665 | -0.064087 | -0.11444 | -0.018311 | -0.15106 | -0.032043 | -0.064087 | 0.11902 | -0.064087 | -0.027466 | 0.045776 | -0.013733 | 0.054932 | 121.6553 | -0.65918 | -0.84229 | 121.701 | 121.6873 | 121.5683 | 0.032044 | -0.086975 | 121.6553 | -0.60883 | -0.75531 | 121.7651 | 121.7743 | 121.7056 | 0.11902 | 0.050354 | 0.045776 | -0.050354 | 0.10986 | 0.036621 | 0.13275 | 0.18311 | 121.788 | 121.8384 | -0.79193 | -0.79193 | 121.6049 | 121.6919 | 121.5912 | 121.6553
6583.1875 | 122.6715 | -121.6644 | 0.69122 | -0.19661 | -0.036621 | 2.7834e-05 | 0.019519 | 0.0036401 | -0.011811 | -0.0028005 | -0.083283 | 0.022401 | 0.013435 | -0.017246 | -0.019651 | 0.027621 | -0.0062207 | -0.073242 | 0.032043 | -0.073242 | 0.009155 | 0.10986 | -0.041199 | 0.059509 | 0.073242 | 0.082397 | -0.045776 | 0.086975 | 0.17395 | 0.10071 | 0.17395 | 121.5912 | -0.65918 | -0.68207 | 121.7743 | 121.7239 | 121.6232 | 0.13275 | 0.032043 | 121.6187 | -0.60883 | -0.60425 | 121.8384 | 121.8384 | 121.7651 | 0.21973 | 0.14648 | 0.18311 | 0.082397 | 0.21973 | 0.13275 | 0.10529 | 0.12817 | 121.6965 | 121.7468 | -0.76447 | -0.737 | 121.6736 | 121.7514 | 121.5912 | 121.7377
6584.8906 | 122.5525 | -121.7422 | 0.72327 | -0.12794 | -0.03833 | 2.7834e-05 | 0.02016 | 0.0012903 | -0.014802 | -0.0028005 | -0.12601 | 0.023041 | 0.014289 | -0.0044285 | -0.020719 | 0.025912 | -0.0021619 | -0.11444 | 0.064087 | -0.073242 | -0.10071 | -0.027466 | -0.16479 | -0.059509 | -0.10529 | 0.11902 | -0.082397 | -0.059509 | 0.013733 | -0.054932 | 0.041199 | 121.669 | -0.65918 | -0.82398 | 121.7148 | 121.6827 | 121.5775 | 0.013733 | -0.091553 | 121.6599 | -0.60425 | -0.78278 | 121.756 | 121.7834 | 121.6873 | 0.1236 | 0.027465 | 0.045776 | -0.027466 | 0.09613 | 0.022888 | 0.13733 | 0.20142 | 121.8063 | 121.8613 | -0.79651 | -0.80566 | 121.6415 | 121.6827 | 121.6278 | 121.637
6586.625 | 122.6028 | -121.7056 | 0.73242 | -0.13557 | -0.038544 | -0.00018577 | 0.018878 | 0.00064947 | -0.01053 | -0.0036551 | -0.077179 | 0.022187 | 0.016426 | -0.0099827 | -0.019224 | 0.02634 | -0.0040845 | -0.10529 | 0.045776 | -0.064087 | -0.059509 | 0.041199 | -0.064087 | 0.018311 | -0.004578 | 0.10529 | -0.082397 | -0.009155 | 0.10986 | 0.036621 | 0.10529 | 121.6415 | -0.68665 | -0.79193 | 121.7468 | 121.7239 | 121.6415 | 0.082398 | 0 | 121.6232 | -0.62714 | -0.74158 | 121.8155 | 121.8109 | 121.7422 | 0.18768 | 0.11902 | 0.10529 | 0.004578 | 0.19226 | 0.073242 | 0.10986 | 0.18768 | 121.7514 | 121.8109 | -0.79651 | -0.81482 | 121.6461 | 121.6965 | 121.6003 | 121.701
6588.3281 | 122.7036 | -121.701 | 0.66834 | -0.1432 | -0.041535 | -0.00082677 | 0.01546 | 0.0012903 | -0.01117 | -0.0049367 | -0.0039367 | 0.022614 | 0.015785 | -0.01575 | -0.018583 | 0.024417 | -0.0017347 | -0.10071 | 0.027466 | -0.07782 | -0.013733 | 0.12817 | -0.004578 | 0.10529 | 0.086975 | 0.068665 | -0.064087 | 0.059509 | 0.20142 | 0.14648 | 0.16479 | 121.6232 | -0.64087 | -0.68207 | 121.8292 | 121.8063 | 121.6965 | 0.18311 | 0.073242 | 121.637 | -0.59967 | -0.60883 | 121.9025 | 121.8658 | 121.8475 | 0.22888 | 0.21057 | 0.20599 | 0.064087 | 0.2655 | 0.1236 | 0.10529 | 0.13275 | 121.7285 | 121.7697 | -0.74616 | -0.73242 | 121.6873 | 121.7606 | 121.6003 | 121.788
6590.0312 | 122.6532 | -121.6782 | 0.69122 | -0.2729 | -0.03833 | -0.001254 | 0.015674 | 0.00064947 | -0.010316 | -0.0010915 | -0.052765 | 0.023682 | 0.015144 | -0.013828 | -0.019438 | 0.02634 | -0.0028027 | -0.073242 | 0.013733 | -0.036621 | 0.013733 | 0.14191 | -0.032043 | 0.068665 | 0.086975 | 0.068665 | -0.054932 | 0.07782 | 0.15106 | 0.10071 | 0.15106 | 121.6415 | -0.67749 | -0.67749 | 121.8201 | 121.7468 | 121.6461 | 0.10529 | 0.004578 | 121.6232 | -0.62256 | -0.6134 | 121.8292 | 121.8292 | 121.7789 | 0.20599 | 0.15564 | 0.17853 | 0.050354 | 0.20599 | 0.13275 | 0.050354 | 0.1236 | 121.6919 | 121.7468 | -0.72784 | -0.74616 | 121.6919 | 121.756 | 121.6049 | 121.7651
6591.7344 | 122.6898 | -121.6782 | 0.6958 | -0.23476 | -0.036621 | 0.002164 | 0.019519 | 0.0017175 | -0.012666 | -0.0047231 | -0.052765 | 0.022187 | 0.013862 | -0.014682 | -0.021147 | 0.025912 | -0.0021619 | -0.054932 | 0.027466 | -0.041199 | 0.022888 | 0.11444 | -0.041199 | 0.07782 | 0.086975 | 0.07782 | -0.045776 | 0.082397 | 0.17395 | 0.11444 | 0.16022 | 121.637 | -0.66834 | -0.67291 | 121.7926 | 121.756 | 121.637 | 0.11902 | 0 | 121.6324 | -0.61798 | -0.6134 | 121.8521 | 121.8384 | 121.7926 | 0.20599 | 0.16022 | 0.15564 | 0.064087 | 0.21973 | 0.12817 | 0.068665 | 0.1236 | 121.7056 | 121.756 | -0.737 | -0.74158 | 121.701 | 121.7606 | 121.6232 | 121.7651
6593.4531 | 122.6715 | -121.6965 | 0.70038 | -0.15846 | -0.043244 | -0.0016812 | 0.019091 | -0.0027685 | -0.013307 | -0.0077139 | -0.022247 | 0.021973 | 0.014289 | -0.015964 | -0.01901 | 0.025058 | -0.0051525 | -0.091553 | 0.032043 | -0.054932 | 0.045776 | 0.15564 | 0.018311 | 0.10986 | 0.082397 | 0.073242 | -0.054932 | 0.064087 | 0.20142 | 0.13275 | 0.16479 | 121.6415 | -0.66833 | -0.6546 | 121.8521 | 121.8063 | 121.7148 | 0.16479 | 0.073243 | 121.6415 | -0.62714 | -0.63629 | 121.8979 | 121.8613 | 121.8292 | 0.21973 | 0.18768 | 0.21057 | 0.10071 | 0.25635 | 0.11902 | 0.086975 | 0.12817 | 121.7285 | 121.7697 | -0.75531 | -0.75531 | 121.7422 | 121.7606 | 121.6049 | 121.7789
6595.1562 | 122.6852 | -121.701 | 0.68665 | -0.21187 | -0.039612 | -0.0018948 | 0.017169 | -0.0031957 | -0.012025 | -0.0062185 | -0.01004 | 0.023469 | 0.015357 | -0.017246 | -0.019865 | 0.022708 | -0.00045291 | -0.11444 | 0.041199 | -0.068665 | -0.032043 | 0.068665 | -0.054932 | 0.064087 | 0.022888 | 0.082397 | -0.064087 | 0.041199 | 0.15106 | 0.11444 | 0.15106 | 121.6324 | -0.64545 | -0.71869 | 121.7697 | 121.7651 | 121.6461 | 0.13275 | 0.013733 | 121.637 | -0.60425 | -0.64545 | 121.8521 | 121.8521 | 121.8155 | 0.21515 | 0.17853 | 0.13733 | 0.036622 | 0.21515 | 0.10529 | 0.10986 | 0.14648 | 121.7422 | 121.7834 | -0.75531 | -0.75073 | 121.669 | 121.7422 | 121.5866 | 121.7239
6596.8594 | 122.6898 | -121.6827 | 0.6958 | -0.22713 | -0.039398 | -0.0010404 | 0.019519 | 0.0010767 | -0.012452 | -0.0036551 | -0.071076 | 0.021546 | 0.016212 | -0.015964 | -0.020933 | 0.024417 | -0.0019483 | -0.059509 | 0 | -0.045776 | 0.027466 | 0.11902 | -0.041199 | 0.086975 | 0.10071 | 0.064087 | -0.032043 | 0.091553 | 0.16479 | 0.11444 | 0.17395 | 121.637 | -0.6958 | -0.66834 | 121.8018 | 121.7697 | 121.6415 | 0.13275 | 0.004577 | 121.6507 | -0.63171 | -0.60425 | 121.8475 | 121.8567 | 121.7972 | 0.20599 | 0.14648 | 0.16479 | 0.073242 | 0.19684 | 0.1236 | 0.045776 | 0.09613 | 121.6827 | 121.7468 | -0.74158 | -0.72784 | 121.7102 | 121.7743 | 121.6232 | 121.7834
6598.6094 | 122.5845 | -121.7377 | 0.73242 | -0.19661 | -0.040253 | -0.00018577 | 0.017596 | 0.00043587 | -0.01352 | -0.0032277 | -0.034454 | 0.023041 | 0.014076 | -0.019168 | -0.021147 | 0.023349 | -0.0062207 | -0.082397 | 0.022888 | -0.050354 | -0.022888 | 0.086975 | -0.027466 | 0.050354 | 0.013733 | 0.09613 | -0.073242 | -0.022888 | 0.091553 | 0.013733 | 0.082397 | 121.6873 | -0.70953 | -0.75531 | 121.8246 | 121.788 | 121.7102 | 0.10071 | 0.022888 | 121.6644 | -0.63629 | -0.75531 | 121.8292 | 121.8201 | 121.7514 | 0.15564 | 0.086975 | 0.13733 | 0.027466 | 0.16479 | 0.050354 | 0.073242 | 0.16937 | 121.7606 | 121.8338 | -0.78278 | -0.80566 | 121.7148 | 121.7148 | 121.6553 | 121.7514
6600.3125 | 122.7036 | -121.6919 | 0.67291 | -0.15846 | -0.038117 | 0.00088223 | 0.019946 | 0.0019311 | -0.011384 | -0.0060049 | -0.086334 | 0.022187 | 0.013221 | -0.017246 | -0.020078 | 0.025058 | -0.0036573 | -0.09613 | 0.032043 | -0.045776 | 0 | 0.091553 | -0.091553 | 0.07782 | 0.073242 | 0.07782 | -0.045776 | 0.073242 | 0.16022 | 0.09613 | 0.16479 | 121.6461 | -0.64087 | -0.67291 | 121.7834 | 121.7697 | 121.6003 | 0.1236 | -0.045777 | 121.6461 | -0.59509 | -0.59967 | 121.8521 | 121.8567 | 121.788 | 0.21057 | 0.14191 | 0.13733 | 0.045776 | 0.20599 | 0.11902 | 0.077819 | 0.1236 | 121.7239 | 121.7697 | -0.71869 | -0.71869 | 121.6919 | 121.7651 | 121.5958 | 121.7651
6602.0156 | 122.6898 | -121.6553 | 0.67291 | -0.19661 | -0.039398 | -0.00082677 | 0.018451 | 0.0023585 | -0.012666 | -0.0049367 | -0.089386 | 0.023469 | 0.016212 | -0.013614 | -0.020719 | 0.025272 | -0.0045117 | -0.050354 | 0.018311 | -0.041199 | 0.027466 | 0.13733 | -0.036621 | 0.073242 | 0.09613 | 0.068665 | -0.054932 | 0.082397 | 0.1831 | 0.1236 | 0.17395 | 121.6141 | -0.6546 | -0.64545 | 121.7926 | 121.7285 | 121.6187 | 0.11444 | 0.004578 | 121.6003 | -0.60425 | -0.59052 | 121.8384 | 121.8292 | 121.7789 | 0.22888 | 0.17853 | 0.17853 | 0.068665 | 0.23804 | 0.13733 | 0.05951 | 0.1236 | 121.6736 | 121.7239 | -0.71411 | -0.72784 | 121.6827 | 121.7377 | 121.6049 | 121.7514
6603.7188 | 122.5937 | -121.7422 | 0.72327 | -0.17372 | -0.039398 | -0.00039957 | 0.021014 | 0.0019311 | -0.012452 | -0.0068593 | -0.098541 | 0.024323 | 0.016426 | -0.013614 | -0.020292 | 0.028049 | -0.00066651 | -0.1236 | 0.059509 | -0.07782 | -0.10986 | -0.032043 | -0.14648 | -0.018311 | -0.050354 | 0.10986 | -0.082397 | -0.036621 | 0.041199 | -0.013733 | 0.064087 | 121.6644 | -0.66376 | -0.83313 | 121.7102 | 121.7239 | 121.5958 | 0.059509 | -0.068664 | 121.6599 | -0.6134 | -0.75989 | 121.7834 | 121.8063 | 121.7285 | 0.14648 | 0.068664 | 0.045777 | -0.032043 | 0.1236 | 0.045776 | 0.13733 | 0.19226 | 121.8018 | 121.8521 | -0.80109 | -0.80566 | 121.6324 | 121.7056 | 121.6187 | 121.6919
6605.4062 | 122.6532 | -121.6873 | 0.69122 | -0.20424 | -0.040253 | 2.7834e-05 | 0.019946 | 0.0012903 | -0.012239 | -0.0045095 | -0.098541 | 0.021332 | 0.015144 | -0.012546 | -0.020719 | 0.026126 | -0.00066651 | -0.11902 | 0.045776 | -0.086975 | -0.064087 | 0.018311 | -0.11902 | 0.013733 | 0.022888 | 0.09613 | -0.073242 | 0.041199 | 0.11444 | 0.064087 | 0.14191 | 121.6003 | -0.64545 | -0.75531 | 121.7056 | 121.701 | 121.5683 | 0.10071 | -0.032044 | 121.6141 | -0.59509 | -0.65002 | 121.8018 | 121.8292 | 121.7514 | 0.21515 | 0.13733 | 0.10529 | 0.022888 | 0.18768 | 0.11444 | 0.13275 | 0.16937 | 121.7331 | 121.7834 | -0.7782 | -0.76447 | 121.6232 | 121.7285 | 121.5683 | 121.7102
6607.1406 | 122.6166 | -121.7377 | 0.71869 | -0.16609 | -0.039612 | 0.00045503 | 0.018237 | 0.0023585 | -0.01053 | -0.0040823 | -0.092438 | 0.02411 | 0.014717 | -0.012546 | -0.020292 | 0.025058 | -0.0062207 | -0.086975 | 0.059509 | -0.082397 | -0.059509 | 0.068665 | -0.07782 | 0.018311 | 0.022888 | 0.11902 | -0.073242 | 0.009155 | 0.11444 | 0.050354 | 0.10986 | 121.6553 | -0.65918 | -0.7782 | 121.8063 | 121.756 | 121.6599 | 0.10071 | 0.004577 | 121.6644 | -0.59967 | -0.70953 | 121.8521 | 121.8475 | 121.788 | 0.18311 | 0.1236 | 0.15106 | 0.022888 | 0.18768 | 0.082397 | 0.14191 | 0.19226 | 121.7972 | 121.8567 | -0.80109 | -0.79193 | 121.6782 | 121.7468 | 121.6507 | 121.7606
6608.8438 | 122.5662 | -121.7377 | 0.73242 | -0.12794 | -0.041962 | -0.0010404 | 0.017596 | 0.0040675 | -0.012879 | -0.0055777 | -0.049713 | 0.022614 | 0.015785 | -0.01276 | -0.020719 | 0.025912 | -0.0057935 | -0.15106 | 0.059509 | -0.091553 | -0.10986 | 0 | -0.1236 | -0.004578 | -0.068665 | 0.11902 | -0.07782 | -0.064087 | 0.054932 | 0.013733 | 0.064087 | 121.6461 | -0.67291 | -0.84229 | 121.7377 | 121.7331 | 121.6141 | 0.086975 | -0.032043 | 121.6599 | -0.6134 | -0.79651 | 121.7926 | 121.8018 | 121.7514 | 0.14191 | 0.091553 | 0.091553 | -0.01831 | 0.13275 | 0.013733 | 0.15106 | 0.19684 | 121.7972 | 121.8567 | -0.82398 | -0.81024 | 121.6278 | 121.6736 | 121.5866 | 121.669
6610.6094 | 122.5983 | -121.7239 | 0.70496 | -0.15846 | -0.038758 | -0.00061317 | 0.019305 | 0.0047083 | -0.010743 | -0.0042959 | -0.077179 | 0.022828 | 0.017494 | -0.0063511 | -0.020719 | 0.026126 | -0.00045291 | -0.13733 | 0.045776 | -0.073242 | -0.11902 | -0.004578 | -0.14648 | -0.022888 | -0.054932 | 0.11444 | -0.086975 | -0.022888 | 0.059509 | -0.004578 | 0.07782 | 121.6507 | -0.65918 | -0.82398 | 121.7194 | 121.7011 | 121.5775 | 0.050354 | -0.073242 | 121.637 | -0.59052 | -0.72784 | 121.7834 | 121.8018 | 121.7194 | 0.16479 | 0.082397 | 0.068664 | -0.045777 | 0.14648 | 0.064087 | 0.11902 | 0.20142 | 121.7697 | 121.8384 | -0.7782 | -0.79193 | 121.6049 | 121.7011 | 121.5866 | 121.669
6612.3281 | 122.6898 | -121.6873 | 0.69122 | -0.16609 | -0.040039 | 0.00088223 | 0.020373 | -0.0012731 | -0.011384 | -0.0038687 | -0.052765 | 0.022401 | 0.015357 | -0.013614 | -0.019865 | 0.027408 | -0.0017347 | -0.091553 | 0.032043 | -0.073242 | -0.022888 | 0.086975 | -0.082397 | 0.045776 | 0.059509 | 0.086975 | -0.045776 | 0.068665 | 0.16022 | 0.10071 | 0.16937 | 121.6141 | -0.65918 | -0.71411 | 121.7743 | 121.7331 | 121.6049 | 0.11902 | -0.009155 | 121.6415 | -0.60425 | -0.62256 | 121.8475 | 121.8567 | 121.788 | 0.21515 | 0.14648 | 0.16022 | 0.050354 | 0.20599 | 0.11444 | 0.10529 | 0.13275 | 121.7194 | 121.7743 | -0.76447 | -0.737 | 121.6644 | 121.756 | 121.5958 | 121.7468
6614.0781 | 122.5937 | -121.7422 | 0.72327 | -0.13557 | -0.038117 | -0.00039957 | 0.018451 | 0.00064947 | -0.013734 | -0.0042959 | -0.077179 | 0.02475 | 0.016212 | -0.012332 | -0.017942 | 0.025485 | 0.00018809 | -0.14191 | 0.059509 | -0.10071 | -0.10529 | 0.004578 | -0.091553 | -0.004578 | -0.064087 | 0.11444 | -0.09613 | -0.041199 | 0.07782 | 0.036621 | 0.10071 | 121.6415 | -0.66376 | -0.82855 | 121.7468 | 121.7377 | 121.6507 | 0.09613 | 0.009155 | 121.6461 | -0.60883 | -0.76447 | 121.8201 | 121.843 | 121.7789 | 0.19684 | 0.13275 | 0.10529 | -0.004578 | 0.17395 | 0.054931 | 0.16022 | 0.21057 | 121.8018 | 121.8567 | -0.82398 | -0.8194 | 121.637 | 121.701 | 121.6003 | 121.6782
6615.7812 | 122.6944 | -121.6919 | 0.70038 | -0.13557 | -0.041962 | -0.001254 | 0.018237 | -0.0025549 | -0.015016 | -0.0017325 | 0.0021667 | 0.02411 | 0.015785 | -0.018314 | -0.020719 | 0.023776 | -0.0051525 | -0.073242 | 0 | -0.054932 | 0.009155 | 0.16937 | 0.009155 | 0.1236 | 0.09613 | 0.068665 | -0.054932 | 0.064087 | 0.20599 | 0.15106 | 0.16022 | 121.637 | -0.70038 | -0.69122 | 121.8613 | 121.8155 | 121.7011 | 0.17853 | 0.064087 | 121.637 | -0.63171 | -0.63629 | 121.8979 | 121.8521 | 121.843 | 0.21515 | 0.20599 | 0.22431 | 0.064087 | 0.26093 | 0.11902 | 0.054932 | 0.1236 | 121.6919 | 121.7606 | -0.75531 | -0.75531 | 121.7011 | 121.756 | 121.6187 | 121.788
6617.5156 | 122.6624 | -121.7148 | 0.70496 | -0.22713 | -0.040894 | 0.0017368 | 0.017169 | -0.00084593 | -0.012666 | -0.0070731 | -0.037506 | 0.022401 | 0.014076 | -0.017673 | -0.020933 | 0.023563 | -0.0036573 | -0.086975 | 0.013733 | -0.036621 | -0.009155 | 0.11444 | -0.068665 | 0.064087 | 0.041199 | 0.091553 | -0.050354 | 0.027466 | 0.12817 | 0.07782 | 0.13275 | 121.6782 | -0.69122 | -0.71411 | 121.8292 | 121.7789 | 121.6461 | 0.10071 | -0.032044 | 121.6644 | -0.6134 | -0.67749 | 121.843 | 121.8475 | 121.7926 | 0.18311 | 0.12817 | 0.15106 | 0.027466 | 0.17853 | 0.07782 | 0.050354 | 0.14191 | 121.7285 | 121.8063 | -0.74158 | -0.75531 | 121.7056 | 121.7422 | 121.6278 | 121.756
6619.2188 | 122.6349 | -121.7239 | 0.72784 | -0.18135 | -0.03833 | -0.00018577 | 0.02016 | 0.0029993 | -0.011811 | -0.0042959 | -0.10464 | 0.022828 | 0.015144 | -0.0059237 | -0.020506 | 0.024844 | -0.0055799 | -0.1236 | 0.036621 | -0.064087 | -0.10071 | 0 | -0.13733 | -0.018311 | -0.022888 | 0.1236 | -0.073242 | 0.013733 | 0.082397 | 0.013733 | 0.10071 | 121.6599 | -0.69122 | -0.82855 | 121.7239 | 121.7056 | 121.5866 | 0.045776 | -0.073242 | 121.6507 | -0.60425 | -0.71411 | 121.8063 | 121.8246 | 121.7377 | 0.17395 | 0.086975 | 0.064087 | -0.036621 | 0.15564 | 0.086975 | 0.10071 | 0.19684 | 121.7606 | 121.8475 | -0.79193 | -0.80109 | 121.6232 | 121.7377 | 121.6003 | 121.7011
6620.9219 | 122.5983 | -121.7422 | 0.73242 | -0.082169 | -0.038117 | -0.00039957 | 0.021014 | 0.00043587 | -0.013307 | -0.0075003 | -0.1138 | 0.022187 | 0.014503 | -0.01575 | -0.023924 | 0.02634 | -0.0062207 | -0.068665 | 0.032043 | -0.045776 | -0.041199 | 0.059509 | -0.073242 | 0.013733 | 0.009155 | 0.11902 | -0.073242 | -0.009155 | 0.082397 | 0.009155 | 0.086975 | 121.6965 | -0.70038 | -0.77362 | 121.8018 | 121.756 | 121.669 | 0.059509 | -0.027466 | 121.669 | -0.6134 | -0.74158 | 121.8246 | 121.8292 | 121.7514 | 0.16022 | 0.082397 | 0.10528 | 0.004577 | 0.15564 | 0.064087 | 0.077819 | 0.19226 | 121.7743 | 121.8613 | -0.7782 | -0.80566 | 121.701 | 121.7331 | 121.6736 | 121.7514
6622.6562 | 122.6166 | -121.7102 | 0.73242 | -0.17372 | -0.039185 | 2.7834e-05 | 0.019732 | -0.0029821 | -0.012025 | -0.0072867 | -0.089386 | 0.022187 | 0.01493 | -0.0063511 | -0.022001 | 0.024631 | -0.0025891 | -0.091553 | 0.050354 | -0.054932 | -0.032043 | 0.050354 | -0.07782 | 0.027466 | 0.018311 | 0.10529 | -0.064087 | 0.022888 | 0.10529 | 0.050354 | 0.10986 | 121.6553 | -0.68207 | -0.76447 | 121.7606 | 121.7377 | 121.6324 | 0.082398 | -0.022888 | 121.6461 | -0.62714 | -0.70953 | 121.8155 | 121.8201 | 121.7606 | 0.17395 | 0.11444 | 0.10529 | 0.022889 | 0.16937 | 0.086975 | 0.10529 | 0.16937 | 121.7606 | 121.8155 | -0.78735 | -0.79651 | 121.6782 | 121.7331 | 121.6187 | 121.7285
6624.3594 | 122.5845 | -121.7468 | 0.73242 | -0.097427 | -0.040253 | -0.0023222 | 0.018664 | -0.0021277 | -0.01352 | -0.0055777 | -0.040558 | 0.022614 | 0.018348 | -0.011051 | -0.020292 | 0.023349 | -0.0045117 | -0.16937 | 0.059509 | -0.086975 | -0.11902 | -0.004578 | -0.10986 | -0.004578 | -0.082397 | 0.11444 | -0.091553 | -0.054932 | 0.041199 | 0.004578 | 0.059509 | 121.6599 | -0.67291 | -0.85144 | 121.7422 | 121.7422 | 121.637 | 0.082397 | -0.022888 | 121.6553 | -0.61798 | -0.78735 | 121.788 | 121.8063 | 121.7514 | 0.15106 | 0.096131 | 0.082397 | -0.032044 | 0.13275 | 0.036621 | 0.14648 | 0.20599 | 121.8063 | 121.8613 | -0.8194 | -0.82398 | 121.6278 | 121.6919 | 121.5775 | 121.6644
6626.0625 | 122.6852 | -121.7056 | 0.70496 | -0.19661 | -0.042816 | -0.0014676 | 0.016101 | -0.0029821 | -0.012239 | -0.0049367 | 0.014374 | 0.023682 | 0.014289 | -0.016818 | -0.017729 | 0.025485 | -0.0051525 | -0.1236 | 0.022888 | -0.054932 | -0.045776 | 0.091553 | -0.064087 | 0.064087 | 0.013733 | 0.086975 | -0.050354 | 0.041199 | 0.14191 | 0.09613 | 0.15106 | 121.6507 | -0.68207 | -0.75073 | 121.7972 | 121.7697 | 121.6415 | 0.11902 | -0.009155 | 121.6553 | -0.61798 | -0.66376 | 121.8475 | 121.8567 | 121.8018 | 0.20142 | 0.14648 | 0.14649 | 0.009156 | 0.19226 | 0.091553 | 0.07782 | 0.13733 | 121.7285 | 121.7926 | -0.75989 | -0.75531 | 121.6599 | 121.7468 | 121.582 | 121.7194
6627.7812 | 122.699 | -121.6919 | 0.69122 | -0.20424 | -0.038544 | -0.00061317 | 0.017596 | 0.0010767 | -0.012452 | -0.0064321 | -0.046661 | 0.024964 | 0.012153 | -0.011051 | -0.020506 | 0.026767 | -0.0013073 | -0.07782 | 0.027466 | -0.064087 | 0.013733 | 0.12817 | -0.036621 | 0.073242 | 0.082397 | 0.086975 | -0.054932 | 0.07782 | 0.16937 | 0.10529 | 0.17395 | 121.6278 | -0.66376 | -0.67749 | 121.8201 | 121.7651 | 121.6553 | 0.13733 | 0.027466 | 121.637 | -0.60425 | -0.6134 | 121.8613 | 121.8658 | 121.7972 | 0.22888 | 0.16022 | 0.19226 | 0.07782 | 0.22431 | 0.13275 | 0.091553 | 0.14191 | 121.7194 | 121.7789 | -0.75531 | -0.74616 | 121.7056 | 121.7697 | 121.6141 | 121.7743
6629.5469 | 122.5937 | -121.7239 | 0.72784 | -0.15846 | -0.038544 | 0.00088223 | 0.018023 | 0.0023585 | -0.01117 | -0.0055777 | -0.10464 | 0.024964 | 0.016426 | -0.012973 | -0.020292 | 0.02634 | 0.00018809 | -0.12817 | 0.059509 | -0.082397 | -0.11444 | -0.032043 | -0.16022 | -0.032043 | -0.068665 | 0.10529 | -0.09613 | -0.036621 | 0.032043 | -0.013733 | 0.068665 | 121.6415 | -0.66834 | -0.84229 | 121.6919 | 121.6919 | 121.5637 | 0.050354 | -0.07782 | 121.6278 | -0.62256 | -0.76447 | 121.756 | 121.7926 | 121.7102 | 0.16479 | 0.082397 | 0.050354 | -0.032044 | 0.12817 | 0.059509 | 0.14191 | 0.20142 | 121.7834 | 121.8292 | -0.81024 | -0.82397 | 121.6095 | 121.6873 | 121.5958 | 121.6553
6631.2656 | 122.699 | -121.6782 | 0.70953 | -0.19661 | -0.039612 | -0.0018948 | 0.01781 | -0.0012731 | -0.015016 | -0.0068593 | 0.0052185 | 0.022828 | 0.01493 | -0.015537 | -0.01901 | 0.023776 | -0.0036573 | -0.068665 | 0.027466 | -0.045776 | 0.009155 | 0.16479 | 0.027466 | 0.13275 | 0.091553 | 0.07782 | -0.041199 | 0.073242 | 0.20142 | 0.16022 | 0.16022 | 121.6324 | -0.68207 | -0.70038 | 121.843 | 121.8109 | 121.7056 | 0.17853 | 0.073242 | 121.637 | -0.63171 | -0.63629 | 121.8796 | 121.8384 | 121.8384 | 0.20142 | 0.20142 | 0.21057 | 0.054931 | 0.24262 | 0.11444 | 0.073242 | 0.11902 | 121.7056 | 121.756 | -0.75531 | -0.75073 | 121.6873 | 121.7514 | 121.6095 | 121.7697
6633.0312 | 122.5891 | -121.7285 | 0.72327 | -0.15846 | -0.037903 | 0.0010958 | 0.018451 | 0.0038537 | -0.013307 | -0.0042959 | -0.089386 | 0.023041 | 0.015571 | -0.011264 | -0.01901 | 0.023349 | -0.0042981 | -0.11902 | 0.050354 | -0.07782 | -0.09613 | -0.032043 | -0.14648 | -0.036621 | -0.059509 | 0.10986 | -0.10071 | -0.054932 | 0.032043 | -0.027466 | 0.07782 | 121.6507 | -0.67291 | -0.8194 | 121.6965 | 121.6919 | 121.582 | 0.041199 | -0.068664 | 121.6278 | -0.6134 | -0.7782 | 121.7606 | 121.8063 | 121.701 | 0.17853 | 0.073242 | 0.045777 | -0.01831 | 0.13275 | 0.045776 | 0.12817 | 0.21057 | 121.7789 | 121.8384 | -0.80109 | -0.82398 | 121.6324 | 121.6736 | 121.6095 | 121.669
6634.7344 | 122.5845 | -121.7468 | 0.72784 | -0.13557 | -0.037049 | -0.0010404 | 0.02016 | 0.0027857 | -0.014375 | -0.0049367 | -0.10464 | 0.024323 | 0.015144 | -0.011264 | -0.022001 | 0.025912 | -0.0013073 | -0.082397 | 0.059509 | -0.068665 | -0.054932 | 0.064087 | -0.07782 | 0.018311 | -0.004578 | 0.086975 | -0.064087 | -0.009155 | 0.07782 | 0.009155 | 0.082397 | 121.6782 | -0.66834 | -0.78278 | 121.8109 | 121.7651 | 121.669 | 0.086976 | -0.009155 | 121.6827 | -0.64087 | -0.737 | 121.8246 | 121.8292 | 121.756 | 0.14648 | 0.073242 | 0.13275 | 0.013733 | 0.14191 | 0.054932 | 0.12817 | 0.15106 | 121.8063 | 121.8338 | -0.79651 | -0.79193 | 121.6919 | 121.7377 | 121.6644 | 121.7422
6636.4531 | 122.5891 | -121.7285 | 0.73242 | -0.18135 | -0.04068 | -0.0016812 | 0.016528 | 0.00086307 | -0.015443 | -0.0038687 | -0.016144 | 0.022614 | 0.017066 | -0.010623 | -0.019438 | 0.024417 | -0.0070751 | -0.10529 | 0.022888 | -0.050354 | -0.036621 | 0.073242 | -0.064087 | 0.041199 | -0.027466 | 0.10529 | -0.09613 | -0.054932 | 0.086975 | 0.013733 | 0.064087 | 121.6782 | -0.70953 | -0.76904 | 121.8018 | 121.7697 | 121.6644 | 0.091553 | -0.013733 | 121.6324 | -0.62714 | -0.78735 | 121.8155 | 121.7926 | 121.7422 | 0.16022 | 0.10986 | 0.1236 | 0.013733 | 0.1831 | 0.041198 | 0.073242 | 0.20142 | 121.7514 | 121.8338 | -0.78278 | -0.82855 | 121.6919 | 121.6736 | 121.6232 | 121.701
6638.1562 | 122.7173 | -121.6919 | 0.70038 | -0.18898 | -0.041107 | -0.0025358 | 0.017169 | 0.0017175 | -0.011598 | -0.0042959 | -0.01004 | 0.020264 | 0.014076 | -0.020236 | -0.020506 | 0.023135 | -0.0036573 | -0.059509 | 0.004578 | -0.032043 | 0.018311 | 0.14648 | 0.013733 | 0.10071 | 0.082397 | 0.086975 | -0.054932 | 0.054932 | 0.17853 | 0.12817 | 0.16022 | 121.6599 | -0.6958 | -0.68207 | 121.8384 | 121.7926 | 121.7056 | 0.13275 | 0.045776 | 121.637 | -0.6134 | -0.64545 | 121.8704 | 121.8521 | 121.8201 | 0.21515 | 0.18311 | 0.17853 | 0.050354 | 0.23346 | 0.10986 | 0.036621 | 0.14191 | 121.6965 | 121.7789 | -0.73242 | -0.75531 | 121.7102 | 121.7468 | 121.6324 | 121.7743
6639.8594 | 122.731 | -121.7102 | 0.68665 | -0.16609 | -0.041107 | -0.0025358 | 0.014819 | -0.0023413 | -0.011384 | -0.0047231 | -0.013092 | 0.023469 | 0.01493 | -0.0228 | -0.019651 | 0.024631 | -0.0021619 | -0.059509 | 0.018311 | -0.050354 | 0.018311 | 0.16937 | 0.009155 | 0.13733 | 0.11444 | 0.086975 | -0.045776 | 0.07782 | 0.19684 | 0.14648 | 0.16479 | 121.6599 | -0.66834 | -0.66834 | 121.8796 | 121.8475 | 121.7194 | 0.18768 | 0.059509 | 121.6644 | -0.59967 | -0.60883 | 121.907 | 121.875 | 121.8567 | 0.21057 | 0.19226 | 0.21973 | 0.068665 | 0.24261 | 0.1236 | 0.068665 | 0.13275 | 121.7285 | 121.7972 | -0.737 | -0.73242 | 121.7285 | 121.788 | 121.6507 | 121.8246
6641.6094 | 122.5845 | -121.7239 | 0.74158 | -0.20424 | -0.041107 | -0.0033902 | 0.016955 | -0.00020513 | -0.011811 | -0.0057913 | -0.037506 | 0.022828 | 0.015144 | -0.017459 | -0.020506 | 0.022281 | -0.0036573 | -0.1236 | 0.059509 | -0.059509 | -0.07782 | 0.027466 | -0.091553 | 0.009155 | -0.050354 | 0.10071 | -0.07782 | -0.059509 | 0.059509 | 0.018311 | 0.050354 | 121.6644 | -0.68207 | -0.8194 | 121.7514 | 121.7331 | 121.6324 | 0.068664 | -0.032044 | 121.6461 | -0.64087 | -0.80109 | 121.7834 | 121.7743 | 121.7422 | 0.12817 | 0.096131 | 0.086975 | -0.018311 | 0.13733 | 0.018311 | 0.11902 | 0.17853 | 121.7834 | 121.8246 | -0.80109 | -0.8194 | 121.6461 | 121.6644 | 121.6003 | 121.6736
6643.3125 | 122.6944 | -121.7102 | 0.69122 | -0.22713 | -0.042603 | -0.0021084 | 0.016742 | 0.00064947 | -0.014375 | -0.0055777 | -0.0069885 | 0.023896 | 0.015357 | -0.014041 | -0.022215 | 0.02399 | -0.0040845 | -0.10986 | 0.032043 | -0.054932 | -0.027466 | 0.082397 | -0.045776 | 0.07782 | 0.041199 | 0.086975 | -0.059509 | 0.036621 | 0.16022 | 0.1236 | 0.14648 | 121.6553 | -0.65918 | -0.71869 | 121.7926 | 121.788 | 121.6644 | 0.13275 | 0.009156 | 121.6507 | -0.60425 | -0.6546 | 121.8704 | 121.8567 | 121.8338 | 0.20599 | 0.1831 | 0.13733 | 0.027466 | 0.21973 | 0.09613 | 0.086975 | 0.14648 | 121.7422 | 121.7972 | -0.74616 | -0.75073 | 121.6827 | 121.7468 | 121.6003 | 121.7514
6645.0938 | 122.58 | -121.7468 | 0.74616 | -0.16609 | -0.041107 | -0.0023222 | 0.016955 | 0.0017175 | -0.013307 | -0.0055777 | -0.049713 | 0.025391 | 0.01493 | -0.016391 | -0.020078 | 0.022922 | -0.0055799 | -0.14648 | 0.041199 | -0.086975 | -0.082397 | 0.013733 | -0.10986 | 0.018311 | -0.050354 | 0.10071 | -0.082397 | -0.064087 | 0.054932 | 0.009155 | 0.050354 | 121.6599 | -0.70496 | -0.82855 | 121.7606 | 121.7651 | 121.637 | 0.10529 | -0.022888 | 121.6644 | -0.64545 | -0.81024 | 121.8018 | 121.7972 | 121.756 | 0.13275 | 0.091552 | 0.10071 | 0.004578 | 0.13733 | 0.01831 | 0.12817 | 0.18311 | 121.788 | 121.8475 | -0.83313 | -0.82855 | 121.6644 | 121.6827 | 121.6003 | 121.6965
6646.7969 | 122.6715 | -121.7194 | 0.68207 | -0.17372 | -0.040894 | -0.0016812 | 0.019732 | -0.0025549 | -0.013093 | -0.0053641 | -0.031403 | 0.021973 | 0.014503 | -0.017459 | -0.019865 | 0.025699 | 0.00040169 | -0.10986 | 0.022888 | -0.064087 | -0.036621 | 0.068665 | -0.091553 | 0.054932 | 0.004578 | 0.09613 | -0.045776 | 0.004578 | 0.1236 | 0.059509 | 0.10071 | 121.6553 | -0.65918 | -0.71869 | 121.788 | 121.7743 | 121.6278 | 0.11902 | -0.027466 | 121.6736 | -0.58594 | -0.67749 | 121.843 | 121.8201 | 121.7789 | 0.14648 | 0.10528 | 0.13275 | 0.027466 | 0.16937 | 0.050354 | 0.086975 | 0.14191 | 121.7422 | 121.8155 | -0.74616 | -0.72784 | 121.6827 | 121.7239 | 121.6095 | 121.7239
6648.5156 | 122.6303 | -121.7285 | 0.72784 | -0.082169 | -0.039185 | -0.00061317 | 0.021014 | 0.00022207 | -0.012025 | -0.0049367 | -0.11075 | 0.022614 | 0.013435 | -0.0067783 | -0.022001 | 0.025485 | -0.0034435 | -0.091553 | 0.059509 | -0.073242 | -0.032043 | 0.054932 | -0.086975 | 0.009155 | 0.013733 | 0.11444 | -0.059509 | 0.004578 | 0.10529 | 0.032043 | 0.10071 | 121.6553 | -0.66834 | -0.75989 | 121.7834 | 121.7377 | 121.6415 | 0.082397 | -0.013733 | 121.669 | -0.6134 | -0.72327 | 121.8338 | 121.8292 | 121.7606 | 0.16022 | 0.091552 | 0.12817 | 0.041199 | 0.16479 | 0.064087 | 0.13275 | 0.17395 | 121.788 | 121.843 | -0.80109 | -0.78735 | 121.6965 | 121.7331 | 121.637 | 121.7422
6650.2188 | 122.7036 | -121.7239 | 0.70496 | -0.12794 | -0.041535 | -0.0014676 | 0.015033 | -0.0036231 | -0.013947 | -0.0060049 | -0.016144 | 0.022187 | 0.014076 | -0.016391 | -0.020933 | 0.022495 | -0.0013073 | -0.086975 | 0.009155 | -0.059509 | 0.036621 | 0.16022 | 0.018311 | 0.11444 | 0.11444 | 0.082397 | -0.045776 | 0.07782 | 0.20142 | 0.14648 | 0.15564 | 121.6644 | -0.6958 | -0.66834 | 121.8842 | 121.8384 | 121.7422 | 0.17395 | 0.07782 | 121.6782 | -0.62256 | -0.62714 | 121.9254 | 121.8796 | 121.8704 | 0.20142 | 0.19226 | 0.21973 | 0.09613 | 0.24719 | 0.1236 | 0.068664 | 0.12817 | 121.7331 | 121.8063 | -0.76447 | -0.75073 | 121.7606 | 121.8018 | 121.637 | 121.8384
6651.9375 | 122.7219 | -121.701 | 0.66834 | -0.20424 | -0.038758 | 0.0019504 | 0.018451 | 0.0025721 | -0.010957 | -0.0034415 | -0.083283 | 0.021973 | 0.012367 | -0.014255 | -0.022428 | 0.025272 | -0.0015209 | -0.041199 | 0.018311 | -0.045776 | 0.018311 | 0.10986 | -0.041199 | 0.091553 | 0.10071 | 0.07782 | -0.054932 | 0.082397 | 0.1831 | 0.10986 | 0.19226 | 121.6553 | -0.65002 | -0.65002 | 121.8109 | 121.7926 | 121.6599 | 0.13733 | 0.004577 | 121.6461 | -0.59052 | -0.58594 | 121.8842 | 121.8933 | 121.8109 | 0.24719 | 0.16479 | 0.15564 | 0.064087 | 0.23804 | 0.13733 | 0.064087 | 0.13275 | 121.7194 | 121.7789 | -0.71411 | -0.72327 | 121.7194 | 121.7834 | 121.6599 | 121.8018
6653.7031 | 122.7173 | -121.7331 | 0.68207 | -0.23476 | -0.041107 | -0.0014676 | 0.016528 | 0.00022207 | -0.012879 | -0.0045095 | -0.034454 | 0.023255 | 0.014503 | -0.018314 | -0.021147 | 0.025058 | -0.0017347 | -0.10071 | 0.018311 | -0.054932 | -0.009155 | 0.091553 | -0.032043 | 0.082397 | 0.045776 | 0.073242 | -0.068665 | 0.054932 | 0.18768 | 0.13275 | 0.15106 | 121.6782 | -0.66376 | -0.69122 | 121.8246 | 121.8155 | 121.701 | 0.13733 | 0.022889 | 121.6644 | -0.60883 | -0.62714 | 121.9208 | 121.8842 | 121.8658 | 0.21973 | 0.20142 | 0.14649 | 0.045777 | 0.25635 | 0.1236 | 0.073243 | 0.14191 | 121.7514 | 121.8063 | -0.737 | -0.75073 | 121.7239 | 121.788 | 121.6324 | 121.7789
6655.4062 | 122.6852 | -121.7102 | 0.70038 | -0.21187 | -0.040467 | -0.00061317 | 0.018023 | 0.0025721 | -0.011598 | -0.0045095 | -0.034454 | 0.023469 | 0.016426 | -0.015109 | -0.020292 | 0.02399 | -0.0040845 | -0.11444 | 0.018311 | -0.054932 | -0.022888 | 0.073242 | -0.032043 | 0.068665 | 0.027466 | 0.082397 | -0.036621 | 0.032043 | 0.15564 | 0.13275 | 0.14648 | 121.6553 | -0.68207 | -0.72327 | 121.7834 | 121.7789 | 121.6782 | 0.1236 | 0.022889 | 121.6736 | -0.61798 | -0.66833 | 121.8658 | 121.8567 | 121.843 | 0.18311 | 0.16937 | 0.12817 | 0.032044 | 0.19226 | 0.068664 | 0.073243 | 0.11902 | 121.7285 | 121.7926 | -0.75531 | -0.737 | 121.6873 | 121.7422 | 121.5958 | 121.7377
6657.1094 | 122.6898 | -121.7285 | 0.70953 | -0.18898 | -0.041962 | -0.0048856 | 0.01781 | -0.0027685 | -0.012452 | -0.0072867 | -0.04361 | 0.021332 | 0.014289 | -0.017032 | -0.020719 | 0.023563 | -0.0047253 | -0.11444 | 0.032043 | -0.050354 | -0.027466 | 0.082397 | -0.064087 | 0.054932 | 0.022888 | 0.082397 | -0.059509 | 0.036621 | 0.15106 | 0.10986 | 0.14191 | 121.6782 | -0.67749 | -0.737 | 121.8109 | 121.7834 | 121.6644 | 0.10529 | -0.013733 | 121.669 | -0.62714 | -0.67291 | 121.8796 | 121.8704 | 121.8384 | 0.20142 | 0.16937 | 0.13275 | 0.022888 | 0.21057 | 0.09613 | 0.082397 | 0.14191 | 121.7606 | 121.8109 | -0.75989 | -0.76904 | 121.701 | 121.7651 | 121.6141 | 121.7514
6658.8125 | 122.6212 | -121.7422 | 0.71411 | -0.17372 | -0.04068 | -0.0025358 | 0.019519 | 0.0017175 | -0.012879 | -0.0055777 | -0.098541 | 0.022828 | 0.015357 | -0.0080601 | -0.023283 | 0.025699 | -0.0036573 | -0.11902 | 0.054932 | -0.086975 | -0.041199 | 0.041199 | -0.086975 | 0.018311 | 0.004578 | 0.11902 | -0.068665 | 0.004578 | 0.10986 | 0.041199 | 0.10071 | 121.6553 | -0.65918 | -0.75531 | 121.7834 | 121.7606 | 121.6553 | 0.10529 | 0 | 121.6736 | -0.59509 | -0.70953 | 121.8521 | 121.843 | 121.7834 | 0.16937 | 0.10986 | 0.12817 | 0.045776 | 0.17853 | 0.073243 | 0.14191 | 0.18768 | 121.7972 | 121.8613 | -0.80109 | -0.78278 | 121.701 | 121.7468 | 121.6232 | 121.7468
6660.5625 | 122.5891 | -121.7468 | 0.70496 | -0.17372 | -0.039398 | -0.001254 | 0.021014 | 0.0036401 | -0.01053 | -0.0038687 | -0.13516 | 0.02475 | 0.015357 | -0.0035739 | -0.021574 | 0.024204 | -0.0021619 | -0.1236 | 0.068665 | -0.07782 | -0.09613 | -0.041199 | -0.16479 | -0.032043 | -0.050354 | 0.11444 | -0.086975 | -0.041199 | 0.027466 | -0.018311 | 0.073242 | 121.669 | -0.63629 | -0.80109 | 121.7056 | 121.7148 | 121.582 | 0.045777 | -0.086975 | 121.6599 | -0.59052 | -0.74616 | 121.7743 | 121.8201 | 121.7285 | 0.16022 | 0.068664 | 0.036621 | -0.01831 | 0.11444 | 0.045776 | 0.14649 | 0.20142 | 121.8155 | 121.8613 | -0.78278 | -0.79193 | 121.6507 | 121.7056 | 121.6232 | 121.6965
6662.2656 | 122.699 | -121.7102 | 0.66834 | -0.21187 | -0.040467 | 0.0013094 | 0.020373 | -0.0010595 | -0.012025 | -0.0092093 | -0.074127 | 0.02411 | 0.013008 | -0.012119 | -0.020078 | 0.02634 | -0.0045117 | -0.07782 | 0.013733 | -0.045776 | 0.009155 | 0.10529 | -0.064087 | 0.059509 | 0.082397 | 0.086975 | -0.054932 | 0.082397 | 0.16937 | 0.10529 | 0.16479 | 121.6644 | -0.6546 | -0.65918 | 121.8155 | 121.7697 | 121.6461 | 0.10528 | -0.018311 | 121.6553 | -0.58136 | -0.58594 | 121.8796 | 121.875 | 121.8155 | 0.21973 | 0.16022 | 0.15106 | 0.054931 | 0.22431 | 0.13733 | 0.059509 | 0.14191 | 121.7239 | 121.7972 | -0.71411 | -0.72327 | 121.7194 | 121.7926 | 121.6324 | 121.7926
6664.0781 | 122.6028 | -121.7468 | 0.73242 | -0.12794 | -0.041107 | -0.0016812 | 0.018878 | -0.00041873 | -0.012025 | -0.0032277 | -0.077179 | 0.025391 | 0.016426 | -0.01276 | -0.020292 | 0.025485 | -0.0028027 | -0.13733 | 0.050354 | -0.082397 | -0.091553 | -0.013733 | -0.11444 | -0.013733 | -0.068665 | 0.10986 | -0.086975 | -0.050354 | 0.073242 | 0.009155 | 0.068665 | 121.6644 | -0.68207 | -0.82398 | 121.7331 | 121.7331 | 121.6324 | 0.068664 | -0.032044 | 121.6599 | -0.62256 | -0.78278 | 121.8201 | 121.8155 | 121.756 | 0.15564 | 0.09613 | 0.068664 | -0.009156 | 0.16022 | 0.036621 | 0.13275 | 0.19684 | 121.7972 | 121.8567 | -0.81482 | -0.8194 | 121.6553 | 121.6965 | 121.6095 | 121.6782
6665.8438 | 122.699 | -121.7422 | 0.66376 | -0.2195 | -0.039185 | -0.0010404 | 0.015887 | 0.0015039 | -0.011384 | -0.0040823 | -0.064972 | 0.022187 | 0.013648 | -0.013614 | -0.020719 | 0.02933 | -0.0064343 | -0.073242 | 0.004578 | -0.036621 | 0.022888 | 0.14648 | -0.032043 | 0.07782 | 0.091553 | 0.07782 | -0.041199 | 0.073242 | 0.17395 | 0.10986 | 0.15564 | 121.7056 | -0.65918 | -0.64087 | 121.8887 | 121.8201 | 121.7102 | 0.11444 | 0.004578 | 121.701 | -0.58594 | -0.59052 | 121.9162 | 121.8979 | 121.8521 | 0.19684 | 0.15106 | 0.18311 | 0.059509 | 0.21515 | 0.11444 | 0.041199 | 0.11902 | 121.7468 | 121.8201 | -0.70038 | -0.70496 | 121.7651 | 121.8155 | 121.669 | 121.8338
6667.625 | 122.6349 | -121.7606 | 0.72784 | -0.15083 | -0.040253 | -0.0027494 | 0.019305 | 0.0023585 | -0.012666 | -0.0083547 | -0.080231 | 0.023682 | 0.013435 | -0.015964 | -0.022001 | 0.025912 | -0.0028027 | -0.11444 | 0.059509 | -0.07782 | -0.064087 | 0.027466 | -0.10071 | 0.018311 | -0.018311 | 0.13275 | -0.082397 | 0 | 0.10986 | 0.036621 | 0.10529 | 121.6827 | -0.66834 | -0.79193 | 121.788 | 121.7789 | 121.6599 | 0.096131 | -0.022888 | 121.6782 | -0.59509 | -0.72784 | 121.8704 | 121.8658 | 121.7972 | 0.18768 | 0.11902 | 0.10529 | 0.013733 | 0.19226 | 0.082397 | 0.13733 | 0.21515 | 121.8201 | 121.8933 | -0.80566 | -0.81024 | 121.6965 | 121.7606 | 121.6461 | 121.7422
6669.4062 | 122.5891 | -121.7651 | 0.71869 | -0.15846 | -0.039398 | -0.00018577 | 0.017382 | -0.0021277 | -0.010957 | -0.0070731 | -0.12296 | 0.024964 | 0.015785 | -0.0078463 | -0.019224 | 0.025912 | -0.0017347 | -0.10071 | 0.045776 | -0.086975 | -0.07782 | 0.018311 | -0.14648 | -0.027466 | -0.022888 | 0.10986 | -0.068665 | -0.041199 | 0.045776 | -0.022888 | 0.041199 | 121.6782 | -0.67291 | -0.79651 | 121.7834 | 121.7377 | 121.6187 | 0.059509 | -0.059509 | 121.6965 | -0.60883 | -0.75989 | 121.8109 | 121.8063 | 121.7422 | 0.10986 | 0.045777 | 0.10529 | 0.009155 | 0.11444 | 0.027466 | 0.13275 | 0.17853 | 121.8109 | 121.875 | -0.80566 | -0.78735 | 121.6873 | 121.7239 | 121.6644 | 121.7422
6671.1094 | 122.6166 | -121.7377 | 0.74616 | -0.11269 | -0.04068 | -0.0010404 | 0.018451 | 0.0010767 | -0.010957 | -0.0066457 | -0.055817 | 0.023896 | 0.015144 | -0.014469 | -0.019438 | 0.025058 | -0.0042981 | -0.1236 | 0.064087 | -0.07782 | -0.086975 | -0.009155 | -0.10071 | -0.004578 | -0.068665 | 0.10529 | -0.082397 | -0.022888 | 0.082397 | 0.013733 | 0.07782 | 121.6599 | -0.68207 | -0.83313 | 121.7285 | 121.7331 | 121.637 | 0.073242 | -0.022888 | 121.6553 | -0.64087 | -0.76904 | 121.8201 | 121.8155 | 121.7514 | 0.16022 | 0.09613 | 0.068665 | -0.009155 | 0.16479 | 0.059509 | 0.14191 | 0.18768 | 121.8018 | 121.843 | -0.82398 | -0.82855 | 121.6507 | 121.7148 | 121.6141 | 121.669
6672.875 | 122.7173 | -121.6965 | 0.6958 | -0.20424 | -0.036835 | 0.00066863 | 0.018237 | 0.0038537 | -0.0092478 | -0.0057913 | -0.068024 | 0.023255 | 0.014289 | -0.0087009 | -0.020719 | 0.025912 | -0.0042981 | -0.045776 | -0.004578 | -0.032043 | 0.013733 | 0.14191 | -0.022888 | 0.082397 | 0.091553 | 0.073242 | -0.041199 | 0.082397 | 0.17853 | 0.11444 | 0.16022 | 121.6644 | -0.70038 | -0.68207 | 121.8384 | 121.7789 | 121.6736 | 0.11444 | 0.009155 | 121.6553 | -0.62256 | -0.6134 | 121.875 | 121.8567 | 121.8109 | 0.20142 | 0.15564 | 0.17395 | 0.045776 | 0.21973 | 0.1236 | 0.027465 | 0.11444 | 121.6919 | 121.7697 | -0.72784 | -0.737 | 121.7102 | 121.7789 | 121.6507 | 121.788
6674.6719 | 122.6303 | -121.7514 | 0.72327 | -0.15083 | -0.037262 | 0.001523 | 0.02016 | -0.00020513 | -0.013307 | -0.0040823 | -0.083283 | 0.022614 | 0.015571 | -0.020236 | -0.020078 | 0.025699 | -0.0025891 | -0.13275 | 0.073242 | -0.07782 | -0.091553 | 0.004578 | -0.15106 | -0.009155 | -0.045776 | 0.10529 | -0.091553 | -0.018311 | 0.050354 | 0.004578 | 0.09613 | 121.6736 | -0.65002 | -0.81482 | 121.756 | 121.7422 | 121.6003 | 0.068665 | -0.073242 | 121.6599 | -0.61798 | -0.74158 | 121.8018 | 121.8475 | 121.756 | 0.18768 | 0.096131 | 0.082398 | -0.013733 | 0.14191 | 0.073242 | 0.15106 | 0.19684 | 121.8246 | 121.8567 | -0.80109 | -0.81482 | 121.6599 | 121.7331 | 121.6187 | 121.7056
6676.3906 | 122.6486 | -121.7331 | 0.70953 | -0.1432 | -0.037049 | 0.00045503 | 0.021655 | 0.0053491 | -0.012666 | -0.0057913 | -0.10159 | 0.023041 | 0.015998 | -0.016178 | -0.018797 | 0.026126 | -0.0040845 | -0.11902 | 0.064087 | -0.07782 | -0.091553 | 0 | -0.13275 | -0.013733 | -0.013733 | 0.10071 | -0.064087 | 0.004578 | 0.082397 | 0.027466 | 0.10986 | 121.6553 | -0.64545 | -0.80109 | 121.7331 | 121.7194 | 121.6003 | 0.064087 | -0.054931 | 121.669 | -0.60883 | -0.70496 | 121.8155 | 121.843 | 121.7606 | 0.17395 | 0.091553 | 0.07782 | -0.013733 | 0.14648 | 0.068665 | 0.14191 | 0.1648 | 121.7972 | 121.8338 | -0.78735 | -0.77362 | 121.6415 | 121.7377 | 121.6141 | 121.7194
6678.1562 | 122.6212 | -121.7239 | 0.74158 | -0.21187 | -0.042389 | -0.001254 | 0.015887 | -0.0025549 | -0.011384 | -0.0034415 | -0.028351 | 0.024537 | 0.015357 | -0.014896 | -0.020506 | 0.025058 | -0.0036573 | -0.10529 | 0.009155 | -0.068665 | -0.059509 | 0.059509 | -0.073242 | 0.027466 | -0.041199 | 0.11444 | -0.07782 | -0.050354 | 0.073242 | 0.004578 | 0.068665 | 121.6553 | -0.73242 | -0.80109 | 121.7834 | 121.7514 | 121.6507 | 0.096131 | -0.004577 | 121.6461 | -0.62714 | -0.79193 | 121.7972 | 121.7926 | 121.7285 | 0.14649 | 0.082398 | 0.12817 | 0.009156 | 0.15106 | 0.027466 | 0.07782 | 0.19226 | 121.7331 | 121.8384 | -0.81024 | -0.8194 | 121.6644 | 121.6736 | 121.6187 | 121.6827
6679.9219 | 122.5891 | -121.7789 | 0.737 | -0.15083 | -0.039612 | -0.0018948 | 0.018451 | 0.00043587 | -0.014588 | -0.0057913 | -0.034454 | 0.025178 | 0.015571 | -0.0134 | -0.020292 | 0.023563 | -0.0021619 | -0.15564 | 0.073242 | -0.091553 | -0.11902 | -0.013733 | -0.11444 | -0.009155 | -0.082397 | 0.11444 | -0.091553 | -0.054932 | 0.054932 | 0.009155 | 0.045776 | 121.6873 | -0.66376 | -0.85602 | 121.7651 | 121.7697 | 121.6644 | 0.082398 | -0.022888 | 121.6873 | -0.62256 | -0.79193 | 121.8338 | 121.8246 | 121.788 | 0.13733 | 0.10071 | 0.07782 | -0.027466 | 0.14649 | 0.036621 | 0.16479 | 0.20599 | 121.8521 | 121.8933 | -0.82855 | -0.82855 | 121.6599 | 121.7239 | 121.6232 | 121.6965
6681.7031 | 122.6257 | -121.7468 | 0.73242 | -0.10506 | -0.037689 | -0.0014676 | 0.018237 | -0.0014867 | -0.012239 | -0.0019461 | -0.046661 | 0.025391 | 0.016853 | -0.0091281 | -0.019865 | 0.025912 | -2.571e-05 | -0.11902 | 0.045776 | -0.082397 | -0.10529 | -0.004578 | -0.10986 | -0.004578 | -0.054932 | 0.12817 | -0.082397 | -0.036621 | 0.073242 | 0.041199 | 0.082397 | 121.6644 | -0.68665 | -0.83771 | 121.7422 | 121.7422 | 121.637 | 0.077819 | -0.027466 | 121.6644 | -0.60425 | -0.76904 | 121.8201 | 121.8292 | 121.788 | 0.16479 | 0.1236 | 0.077819 | -0.022889 | 0.15564 | 0.045776 | 0.12817 | 0.21057 | 121.7926 | 121.875 | -0.81482 | -0.81482 | 121.6415 | 121.7102 | 121.6278 | 121.6919
6683.4688 | 122.6898 | -121.7194 | 0.70953 | -0.23476 | -0.038971 | 0.00045503 | 0.018023 | -0.0027685 | -0.011811 | -0.0064321 | -0.01004 | 0.023469 | 0.015998 | -0.018527 | -0.019224 | 0.024844 | -0.0060071 | -0.073242 | 0.009155 | -0.041199 | -0.018311 | 0.10986 | -0.054932 | 0.059509 | 0.054932 | 0.086975 | -0.059509 | 0.036621 | 0.1236 | 0.082397 | 0.11902 | 121.6782 | -0.70038 | -0.72784 | 121.8292 | 121.7789 | 121.6644 | 0.10071 | -0.013733 | 121.6599 | -0.62256 | -0.67291 | 121.843 | 121.8384 | 121.8018 | 0.17853 | 0.14191 | 0.15106 | 0.022888 | 0.1831 | 0.09613 | 0.050354 | 0.14648 | 121.7285 | 121.8063 | -0.75073 | -0.76904 | 121.701 | 121.756 | 121.6461 | 121.7743
6685.1719 | 122.6532 | -121.7422 | 0.70496 | -0.20424 | -0.038758 | -0.00018577 | 0.01546 | -0.0019141 | -0.012666 | -0.0045095 | -0.028351 | 0.020692 | 0.015785 | -0.013614 | -0.019438 | 0.022708 | -0.0028027 | -0.07782 | 0.004578 | -0.050354 | 0.013733 | 0.13733 | -0.004578 | 0.09613 | 0.07782 | 0.091553 | -0.045776 | 0.022888 | 0.16022 | 0.10071 | 0.11444 | 121.6919 | -0.70038 | -0.69122 | 121.8796 | 121.8384 | 121.7377 | 0.14648 | 0.045776 | 121.6965 | -0.6134 | -0.68207 | 121.9025 | 121.8567 | 121.843 | 0.16022 | 0.14648 | 0.18768 | 0.064087 | 0.20599 | 0.068664 | 0.054932 | 0.13733 | 121.7468 | 121.8338 | -0.75531 | -0.75073 | 121.756 | 121.7651 | 121.6644 | 121.8201
6686.9375 | 122.6486 | -121.7285 | 0.71869 | -0.17372 | -0.040467 | -0.00039957 | 0.01781 | 0.0036401 | -0.013734 | -0.0057913 | -0.022247 | 0.022187 | 0.013648 | -0.015323 | -0.019865 | 0.023135 | -0.0030163 | -0.086975 | 0.027466 | -0.059509 | 0 | 0.11444 | -0.013733 | 0.07782 | 0.041199 | 0.09613 | -0.045776 | 0.004578 | 0.1236 | 0.068665 | 0.10986 | 121.669 | -0.69122 | -0.71869 | 121.843 | 121.8063 | 121.7148 | 0.13733 | 0.045776 | 121.6827 | -0.62256 | -0.71411 | 121.8521 | 121.8384 | 121.7972 | 0.15564 | 0.11444 | 0.17395 | 0.059509 | 0.16937 | 0.050354 | 0.086975 | 0.14191 | 121.756 | 121.8246 | -0.7782 | -0.76447 | 121.7285 | 121.7331 | 121.6415 | 121.7697
6688.7031 | 122.6852 | -121.6965 | 0.70038 | -0.25002 | -0.037476 | -0.00018577 | 0.019091 | -0.0025549 | -0.011384 | -0.0055777 | -0.049713 | 0.022187 | 0.017066 | -0.017246 | -0.020292 | 0.025699 | -0.0030163 | -0.068665 | 0.009155 | -0.045776 | 0.013733 | 0.14648 | -0.022888 | 0.082397 | 0.10071 | 0.073242 | -0.032043 | 0.054932 | 0.16479 | 0.082397 | 0.13733 | 121.6507 | -0.69122 | -0.68664 | 121.843 | 121.7789 | 121.6736 | 0.12817 | 0.022888 | 121.6644 | -0.62714 | -0.64545 | 121.8613 | 121.8338 | 121.7789 | 0.16937 | 0.11444 | 0.19226 | 0.059509 | 0.19684 | 0.086975 | 0.054931 | 0.10529 | 121.7056 | 121.7697 | -0.74615 | -0.73242 | 121.7102 | 121.7514 | 121.6278 | 121.7972
6690.4062 | 122.6578 | -121.7285 | 0.71869 | -0.18135 | -0.041321 | -0.001254 | 0.014819 | -0.0038367 | -0.014588 | -0.0040823 | -0.022247 | 0.020692 | 0.016426 | -0.015109 | -0.020719 | 0.024844 | -0.00023931 | -0.064087 | 0.027466 | -0.050354 | 0.022888 | 0.1236 | -0.009155 | 0.073242 | 0.050354 | 0.09613 | -0.059509 | 0.018311 | 0.13733 | 0.073242 | 0.11902 | 121.6782 | -0.69122 | -0.6958 | 121.8521 | 121.8018 | 121.7194 | 0.1236 | 0.041199 | 121.669 | -0.62256 | -0.70038 | 121.8658 | 121.8475 | 121.8018 | 0.17853 | 0.13275 | 0.17395 | 0.073242 | 0.19684 | 0.07782 | 0.07782 | 0.15564 | 121.756 | 121.8246 | -0.76904 | -0.7782 | 121.7514 | 121.7468 | 121.6644 | 121.7789
6692.1719 | 122.7219 | -121.7285 | 0.70496 | -0.16609 | -0.040894 | -0.0010404 | 0.018023 | -0.0031957 | -0.015229 | -0.0045095 | -0.025299 | 0.020905 | 0.012794 | -0.014682 | -0.020933 | 0.026126 | -0.0051525 | -0.082397 | 0.004578 | -0.054932 | 0.036621 | 0.15564 | 0.022888 | 0.11902 | 0.10071 | 0.07782 | -0.050354 | 0.064087 | 0.1831 | 0.12817 | 0.15564 | 121.6736 | -0.70038 | -0.66834 | 121.8842 | 121.8475 | 121.7514 | 0.17395 | 0.07782 | 121.6782 | -0.62714 | -0.64087 | 121.9116 | 121.8842 | 121.8567 | 0.20599 | 0.17853 | 0.21057 | 0.091553 | 0.23346 | 0.11444 | 0.05951 | 0.12817 | 121.7331 | 121.8063 | -0.75989 | -0.75531 | 121.7651 | 121.7926 | 121.6461 | 121.8292
6693.9375 | 122.5891 | -121.7651 | 0.73242 | -0.17372 | -0.036835 | -0.00018577 | 0.019519 | 0.0038537 | -0.012879 | -0.0057913 | -0.1077 | 0.024323 | 0.01493 | -0.014469 | -0.021574 | 0.025699 | -0.0030163 | -0.11902 | 0.064087 | -0.086975 | -0.09613 | -0.013733 | -0.15564 | -0.032043 | -0.059509 | 0.10986 | -0.086975 | -0.059509 | 0.013733 | -0.032043 | 0.050354 | 121.6782 | -0.66834 | -0.82855 | 121.7514 | 121.7331 | 121.6095 | 0.054932 | -0.068665 | 121.6782 | -0.62256 | -0.79193 | 121.7789 | 121.8155 | 121.7331 | 0.13733 | 0.054932 | 0.073242 | -0.009155 | 0.10071 | 0.027466 | 0.15106 | 0.19684 | 121.8292 | 121.875 | -0.8194 | -0.8194 | 121.669 | 121.7056 | 121.6461 | 121.7056
6695.7188 | 122.7127 | -121.7056 | 0.67749 | -0.17372 | -0.036835 | -0.0014676 | 0.01781 | -0.0034095 | -0.011384 | -0.0049367 | -0.077179 | 0.022401 | 0.015785 | -0.01276 | -0.020719 | 0.024844 | -0.00023931 | -0.10986 | 0.050354 | -0.054932 | -0.009155 | 0.086975 | -0.064087 | 0.054932 | 0.054932 | 0.086975 | -0.032043 | 0.068665 | 0.16022 | 0.09613 | 0.16022 | 121.6507 | -0.62714 | -0.68665 | 121.7926 | 121.7606 | 121.6415 | 0.10986 | -0.009155 | 121.6736 | -0.59052 | -0.60883 | 121.8658 | 121.8658 | 121.8018 | 0.19226 | 0.12817 | 0.14191 | 0.045777 | 0.19226 | 0.10071 | 0.10529 | 0.11902 | 121.756 | 121.7926 | -0.73242 | -0.70953 | 121.6965 | 121.7743 | 121.5958 | 121.7606
6697.4062 | 122.6578 | -121.7422 | 0.71411 | -0.12794 | -0.039612 | -0.00061317 | 0.020587 | -0.0025549 | -0.014588 | -0.0045095 | -0.092438 | 0.023896 | 0.014503 | -0.0093417 | -0.019438 | 0.025058 | -0.0030163 | -0.10071 | 0.045776 | -0.086975 | -0.050354 | 0.059509 | -0.064087 | 0.022888 | 0.013733 | 0.11444 | -0.068665 | 0.018311 | 0.10529 | 0.045776 | 0.10529 | 121.6553 | -0.66834 | -0.76447 | 121.8018 | 121.7651 | 121.6782 | 0.10986 | 0.022888 | 121.6736 | -0.59967 | -0.6958 | 121.8475 | 121.8475 | 121.788 | 0.17395 | 0.11444 | 0.14648 | 0.036621 | 0.17395 | 0.086976 | 0.13275 | 0.18311 | 121.788 | 121.8567 | -0.80109 | -0.78278 | 121.6919 | 121.7606 | 121.6415 | 121.756
6699.1719 | 122.6898 | -121.7239 | 0.68207 | -0.18898 | -0.037049 | -0.0014676 | 0.019519 | 0.0038537 | -0.010316 | -0.0068593 | -0.086334 | 0.023896 | 0.016426 | -0.012332 | -0.020292 | 0.024844 | -0.0023755 | -0.10529 | 0.054932 | -0.07782 | -0.064087 | 0.032043 | -0.11444 | 0.004578 | 0.018311 | 0.09613 | -0.054932 | 0.050354 | 0.13733 | 0.086975 | 0.15564 | 121.6461 | -0.62714 | -0.74616 | 121.756 | 121.7285 | 121.6095 | 0.082398 | -0.036621 | 121.669 | -0.58594 | -0.63171 | 121.8613 | 121.8796 | 121.8109 | 0.21057 | 0.14191 | 0.10986 | 0.013733 | 0.19226 | 0.10529 | 0.13275 | 0.15106 | 121.7789 | 121.8201 | -0.75989 | -0.737 | 121.6599 | 121.7743 | 121.6187 | 121.7422
6700.9531 | 122.6578 | -121.7377 | 0.72327 | -0.15083 | -0.040467 | -0.00061317 | 0.02016 | 0.0032129 | -0.013093 | -0.0055777 | -0.086334 | 0.023041 | 0.015571 | -0.013614 | -0.018156 | 0.02399 | -0.0070751 | -0.082397 | 0.045776 | -0.073242 | -0.050354 | 0.054932 | -0.086975 | 0.013733 | 0.022888 | 0.10529 | -0.068665 | 0.004578 | 0.10529 | 0.050354 | 0.10529 | 121.6644 | -0.67749 | -0.77362 | 121.7926 | 121.7514 | 121.6507 | 0.086975 | -0.013733 | 121.669 | -0.61798 | -0.71869 | 121.843 | 121.843 | 121.788 | 0.17395 | 0.11902 | 0.12817 | 0.022888 | 0.17395 | 0.073243 | 0.11902 | 0.17395 | 121.7834 | 121.843 | -0.79651 | -0.79193 | 121.6873 | 121.7422 | 121.6553 | 121.7606
6702.7188 | 122.7219 | -121.7148 | 0.70496 | -0.18898 | -0.039612 | -0.00018577 | 0.016955 | -0.0025549 | -0.01352 | -0.0051505 | 0.0021667 | 0.021973 | 0.015571 | -0.012546 | -0.019224 | 0.025058 | -0.0040845 | -0.10986 | 0.027466 | -0.068665 | -0.045776 | 0.082397 | -0.050354 | 0.064087 | 0.032043 | 0.086975 | -0.041199 | 0.022888 | 0.16022 | 0.10529 | 0.14648 | 121.6461 | -0.67749 | -0.75073 | 121.7972 | 121.7789 | 121.6644 | 0.13275 | 0.018311 | 121.6736 | -0.61798 | -0.68207 | 121.875 | 121.8613 | 121.8201 | 0.18768 | 0.14649 | 0.15106 | 0.022889 | 0.20142 | 0.064087 | 0.096131 | 0.12817 | 121.7422 | 121.8018 | -0.77362 | -0.74616 | 121.669 | 121.7377 | 121.6049 | 121.7468
6704.4219 | 122.7219 | -121.7102 | 0.69122 | -0.15846 | -0.041321 | -0.0014676 | 0.015246 | -0.0012731 | -0.012666 | -0.0030141 | -0.013092 | 0.020051 | 0.013221 | -0.021091 | -0.019651 | 0.02399 | -0.0053661 | -0.082397 | 0.013733 | -0.073242 | 0.045776 | 0.14648 | 0 | 0.10529 | 0.082397 | 0.086975 | -0.041199 | 0.068665 | 0.17395 | 0.15106 | 0.15564 | 121.637 | -0.67749 | -0.64545 | 121.8567 | 121.8155 | 121.7102 | 0.17853 | 0.073242 | 121.669 | -0.60425 | -0.62256 | 121.8842 | 121.8658 | 121.8613 | 0.19684 | 0.19226 | 0.21973 | 0.11902 | 0.21515 | 0.10986 | 0.086975 | 0.12817 | 121.7239 | 121.7972 | -0.76447 | -0.73242 | 121.756 | 121.7789 | 121.6278 | 121.7926
6706.1875 | 122.7219 | -121.7422 | 0.6958 | -0.12032 | -0.042816 | -0.0025358 | 0.016314 | -0.0014867 | -0.014375 | -0.0023733 | -0.0008851 | 0.022828 | 0.015785 | -0.014682 | -0.021787 | 0.024204 | -0.00088011 | -0.091553 | -0.004578 | -0.050354 | 0.027466 | 0.15106 | 0.018311 | 0.1236 | 0.082397 | 0.073242 | -0.027466 | 0.068665 | 0.17853 | 0.13733 | 0.16022 | 121.6919 | -0.70038 | -0.66834 | 121.8933 | 121.8658 | 121.7606 | 0.17395 | 0.068665 | 121.7148 | -0.62256 | -0.62714 | 121.9208 | 121.9025 | 121.8796 | 0.18768 | 0.16479 | 0.20142 | 0.07782 | 0.20599 | 0.096131 | 0.045776 | 0.10071 | 121.7377 | 121.8155 | -0.74616 | -0.72327 | 121.7697 | 121.8109 | 121.6507 | 121.8246
6707.8906 | 122.6898 | -121.7514 | 0.71411 | -0.16609 | -0.040253 | -0.0036038 | 0.015246 | -0.0025549 | -0.014161 | -0.0049367 | -0.037506 | 0.023469 | 0.015144 | -0.020023 | -0.020933 | 0.025058 | -0.0025891 | -0.073242 | 0.022888 | -0.054932 | 0.009155 | 0.13733 | -0.013733 | 0.086975 | 0.07782 | 0.10071 | -0.045776 | 0.022888 | 0.15564 | 0.10986 | 0.12817 | 121.6965 | -0.69122 | -0.70496 | 121.8887 | 121.8384 | 121.7377 | 0.14191 | 0.041199 | 121.7056 | -0.6134 | -0.69122 | 121.907 | 121.8796 | 121.8613 | 0.17395 | 0.15564 | 0.19226 | 0.064087 | 0.20142 | 0.068664 | 0.07782 | 0.14648 | 121.7743 | 121.8521 | -0.76904 | -0.75989 | 121.7606 | 121.7743 | 121.6782 | 121.8292
6709.6719 | 122.6028 | -121.8018 | 0.73242 | -0.16609 | -0.040894 | -0.0010404 | 0.016955 | 8.47e-06 | -0.013734 | -0.0049367 | -0.052765 | 0.023041 | 0.013435 | -0.0181 | -0.020506 | 0.025058 | -0.0010937 | -0.13275 | 0.059509 | -0.091553 | -0.09613 | 0.004578 | -0.10071 | 0 | -0.054932 | 0.13275 | -0.082397 | -0.068665 | 0.054932 | 0 | 0.054932 | 121.7102 | -0.67291 | -0.82855 | 121.8063 | 121.8018 | 121.7011 | 0.091553 | -0.009155 | 121.7194 | -0.59967 | -0.80109 | 121.8567 | 121.8567 | 121.8018 | 0.13733 | 0.082397 | 0.096131 | -0.004577 | 0.13733 | 0.013732 | 0.15106 | 0.21515 | 121.8613 | 121.9345 | -0.82398 | -0.81482 | 121.7056 | 121.7331 | 121.669 | 121.7468
6711.4375 | 122.5983 | -121.7972 | 0.71411 | -0.18135 | -0.037049 | -0.0014676 | 0.021869 | -0.00041873 | -0.012666 | -0.0045095 | -0.10159 | 0.022828 | 0.017066 | -0.014682 | -0.020933 | 0.025058 | -0.0040845 | -0.10529 | 0.064087 | -0.082397 | -0.091553 | 0 | -0.15564 | -0.027466 | -0.045776 | 0.10986 | -0.064087 | -0.050354 | 0.036621 | -0.041199 | 0.045776 | 121.7148 | -0.65002 | -0.80566 | 121.7972 | 121.7697 | 121.6415 | 0.054931 | -0.073243 | 121.7331 | -0.60425 | -0.76447 | 121.8338 | 121.843 | 121.756 | 0.10986 | 0.022888 | 0.082397 | -0.009156 | 0.10071 | 0.013733 | 0.14648 | 0.17395 | 121.8613 | 121.907 | -0.79651 | -0.7782 | 121.7056 | 121.7468 | 121.6919 | 121.7514
6713.1562 | 122.5891 | -121.7743 | 0.70038 | -0.18135 | -0.037689 | -0.0010404 | 0.021869 | 0.0049219 | -0.010316 | -0.0079275 | -0.1138 | 0.023682 | 0.017707 | -0.011051 | -0.020506 | 0.025272 | -0.0060071 | -0.15106 | 0.050354 | -0.091553 | -0.1236 | -0.036621 | -0.16937 | -0.050354 | -0.059509 | 0.1236 | -0.068665 | -0.041199 | 0.027466 | -0.041199 | 0.050354 | 121.6827 | -0.65002 | -0.82397 | 121.7377 | 121.7239 | 121.6049 | 0.041199 | -0.07782 | 121.7056 | -0.57678 | -0.74158 | 121.8018 | 121.8246 | 121.7331 | 0.11902 | 0.027466 | 0.054932 | -0.032043 | 0.096131 | 0.027466 | 0.14191 | 0.19226 | 121.8246 | 121.8979 | -0.79193 | -0.76904 | 121.6507 | 121.7331 | 121.6232 | 121.7148
6714.9375 | 122.6532 | -121.756 | 0.72784 | -0.13557 | -0.039398 | -0.00082677 | 0.019305 | 0.00064947 | -0.012879 | -0.0025869 | -0.086334 | 0.023041 | 0.014503 | -0.017459 | -0.019865 | 0.025699 | -0.0032299 | -0.10529 | 0.054932 | -0.07782 | -0.068665 | 0.027466 | -0.068665 | 0.009155 | -0.013733 | 0.10071 | -0.068665 | -0.009155 | 0.10986 | 0.036621 | 0.086975 | 121.6782 | -0.67291 | -0.79651 | 121.7834 | 121.7651 | 121.6873 | 0.086975 | 0.009155 | 121.6873 | -0.62714 | -0.737 | 121.8658 | 121.843 | 121.7926 | 0.15564 | 0.10529 | 0.10529 | 0.009155 | 0.17853 | 0.05951 | 0.13275 | 0.16937 | 121.8109 | 121.8567 | -0.80566 | -0.79651 | 121.6873 | 121.7468 | 121.6507 | 121.7422
6716.7031 | 122.7402 | -121.7422 | 0.68665 | -0.16609 | -0.038117 | -0.0010404 | 0.014178 | -0.00063233 | -0.012239 | -0.0051505 | 0.0021667 | 0.023682 | 0.013862 | -0.016818 | -0.020506 | 0.023776 | -0.0057935 | -0.10071 | 0.032043 | -0.073242 | -0.004578 | 0.11902 | -0.022888 | 0.091553 | 0.064087 | 0.073242 | -0.082397 | 0.064087 | 0.19226 | 0.13733 | 0.16479 | 121.669 | -0.6546 | -0.69122 | 121.8613 | 121.8338 | 121.7194 | 0.16479 | 0.050354 | 121.6599 | -0.6134 | -0.62256 | 121.9345 | 121.907 | 121.8796 | 0.24719 | 0.21973 | 0.19226 | 0.068664 | 0.27466 | 0.14648 | 0.10529 | 0.15564 | 121.7743 | 121.8155 | -0.75989 | -0.76904 | 121.7377 | 121.8063 | 121.6415 | 121.8063
6718.4688 | 122.731 | -121.7102 | 0.68207 | -0.18135 | -0.037689 | 0.00045503 | 0.019519 | 0.0021447 | -0.011384 | -0.0053641 | -0.049713 | 0.023041 | 0.013862 | -0.016605 | -0.018583 | 0.025058 | -0.00088011 | -0.045776 | 0.009155 | -0.027466 | 0.027466 | 0.14648 | -0.036621 | 0.082397 | 0.10986 | 0.073242 | -0.059509 | 0.09613 | 0.17853 | 0.1236 | 0.16937 | 121.6827 | -0.67291 | -0.6546 | 121.8567 | 121.7926 | 121.6736 | 0.10986 | -0.009155 | 121.6507 | -0.60883 | -0.58594 | 121.8887 | 121.8796 | 121.8338 | 0.22888 | 0.1831 | 0.17395 | 0.054932 | 0.23804 | 0.15564 | 0.036621 | 0.13275 | 121.7194 | 121.7834 | -0.70953 | -0.74158 | 121.7377 | 121.8063 | 121.6644 | 121.8201
6720.1719 | 122.7448 | -121.7285 | 0.68665 | -0.15846 | -0.04068 | -0.0027494 | 0.016528 | 0.0017175 | -0.01053 | -0.0032277 | 0.0082703 | 0.023041 | 0.014717 | -0.011905 | -0.02136 | 0.024204 | -0.0010937 | -0.07782 | 0.013733 | -0.054932 | 0.036621 | 0.16479 | 0.013733 | 0.1236 | 0.12817 | 0.068665 | -0.054932 | 0.082397 | 0.20599 | 0.15106 | 0.17853 | 121.6736 | -0.67291 | -0.65002 | 121.8933 | 121.8521 | 121.7422 | 0.17853 | 0.068665 | 121.6736 | -0.61798 | -0.60425 | 121.9345 | 121.907 | 121.8796 | 0.23346 | 0.20599 | 0.21973 | 0.091553 | 0.26093 | 0.13733 | 0.068665 | 0.1236 | 121.7422 | 121.7972 | -0.74158 | -0.74158 | 121.7651 | 121.8109 | 121.6507 | 121.8567

## Thermal Data
Fire Time | A Position - Middle | C Position - 3' | C Position - Middle | C Position - 7'
-0.824 | 14.5974 | 14.8155 | 15.217 | 14.7636
0.176 | 14.6021 | 14.8133 | 15.2177 | 14.7621
1.176 | 14.6035 | 14.8153 | 15.2295 | 14.7704
2.176 | 14.5998 | 14.8219 | 15.2306 | 14.7688
3.176 | 15.8467 | 14.8449 | 15.2605 | 14.772
4.176 | 24.1941 | 15.0865 | 15.6375 | 14.8511
5.176 | 75.6817 | 17.0404 | 16.5021 | 15.0298
6.176 | 125.1002 | 17.1355 | 17.1838 | 15.4326
7.176 | 171.0603 | 19.4733 | 17.8887 | 19.9381
8.176 | 235.8329 | 27.3443 | 21.3964 | 27.038
9.176 | 272.7015 | 36.5192 | 29.2955 | 34.5256
10.176 | 292.705 | 43.646 | 38.575 | 44.6374
11.176 | 331.7906 | 54.2249 | 51.3933 | 57.4371
12.176 | 363.0439 | 65.0258 | 59.1359 | 69.3152
13.176 | 401.9252 | 73.2157 | 67.3005 | 76.2894
14.176 | 445.7763 | 82.0107 | 75.619 | 82.6338
15.176 | 470.2591 | 92.0344 | 86.3722 | 92.8463
16.176 | 499.3719 | 102.1046 | 96.6951 | 103.0482
17.176 | 534.0854 | 113.1665 | 104.3465 | 108.9498
18.176 | 547.0071 | 118.6469 | 112.204 | 115.6768
19.176 | 572.4352 | 125.1636 | 119.6569 | 120.9223
20.1917 | 592.3685 | 134.0076 | 126.1685 | 125.6585
21.176 | 601.55 | 139.8919 | 131.2133 | 133.7241
22.176 | 575.231 | 145.3035 | 138.2293 | 138.1772
23.176 | 544.5007 | 149.1843 | 141.461 | 141.0954
24.176 | 517.2794 | 150.9171 | 144.2963 | 144.4401
25.176 | 491.4691 | 151.807 | 145.8702 | 145.8694
26.176 | 467.2013 | 152.7257 | 147.4288 | 146.7956
27.176 | 445.4239 | 153.3878 | 148.0748 | 147.721
28.176 | 424.6221 | 153.2801 | 148.2715 | 148.7052
29.176 | 406.1741 | 152.703 | 149.2095 | 148.5611
30.176 | 390.3865 | 152.3785 | 148.5297 | 147.9382
31.176 | 375.0042 | 151.6781 | 148.1499 | 147.2675
32.176 | 360.4217 | 150.7961 | 146.292 | 146.6413
33.176 | 347.2752 | 148.6524 | 144.2532 | 144.7196
34.176 | 333.4999 | 146.4223 | 141.8555 | 142.6447
35.176 | 321.9357 | 144.3374 | 140.1622 | 140.5785
36.176 | 312.365 | 142.1792 | 138.3048 | 138.8582
37.176 | 301.4327 | 140.2902 | 136.7304 | 137.0759
38.176 | 290.4635 | 138.0443 | 135.2438 | 135.4835
39.176 | 281.7924 | 135.7828 | 133.784 | 133.5436
40.176 | 274.6901 | 134.1038 | 132.6276 | 131.9602
41.176 | 266.4722 | 132.311 | 131.2477 | 130.4699
42.176 | 257.3537 | 130.7781 | 129.6788 | 129.0076
43.176 | 250.505 | 129.2509 | 128.4101 | 127.4901
44.176 | 243.4414 | 127.8137 | 126.8604 | 126.0263
45.176 | 237.0907 | 126.4274 | 125.4756 | 124.1803
46.176 | 231.8668 | 124.9631 | 124.4018 | 122.6545
47.176 | 228.3067 | 123.4459 | 123.2894 | 121.3199
48.176 | 223.9734 | 122.0972 | 122.1394 | 120.2212
49.176 | 219.7054 | 120.8513 | 120.8443 | 119.0656
50.1917 | 215.0432 | 119.5549 | 119.6484 | 117.7605
51.176 | 210.4843 | 118.4544 | 118.4221 | 116.5569
52.176 | 206.8332 | 117.363 | 117.36 | 115.5967
53.176 | 202.5424 | 116.4616 | 116.168 | 114.6527
54.176 | 199.1132 | 115.3869 | 115.3233 | 113.5497
55.176 | 196.5114 | 114.3322 | 114.2107 | 112.3155
56.176 | 192.8739 | 113.2627 | 113.2474 | 111.5217
57.176 | 189.543 | 112.0633 | 112.2799 | 110.6162
58.176 | 185.9531 | 111.1648 | 111.4688 | 109.835
59.176 | 183.3884 | 110.4569 | 110.601 | 108.9996
60.176 | 181.613 | 109.5897 | 109.8781 | 107.897
61.176 | 179.3229 | 108.8386 | 109.2119 | 106.676
62.176 | 176.8805 | 108.14 | 108.477 | 105.8627
63.176 | 174.467 | 107.4701 | 107.8894 | 105.0678
64.176 | 172.7977 | 106.68 | 107.1313 | 104.3515
65.176 | 170.9575 | 105.9426 | 106.4504 | 103.6831
66.176 | 169.9712 | 105.2966 | 105.8253 | 102.9659
67.176 | 169.0198 | 104.7378 | 105.3187 | 102.3051
68.176 | 167.9003 | 104.1551 | 104.827 | 101.6494
69.176 | 167.7536 | 103.4865 | 104.2659 | 100.9606
70.176 | 167.716 | 102.9911 | 103.7387 | 100.3378
71.176 | 167.1633 | 102.8075 | 103.2863 | 99.7587
72.176 | 167.6075 | 102.2784 | 102.9495 | 99.226
73.176 | 168.3032 | 102.4921 | 103.461 | 99.0804
74.176 | 168.0317 | 102.1755 | 102.8802 | 98.3759
75.176 | 167.8261 | 102.0219 | 102.8294 | 98.3868
76.176 | 169.1113 | 102.5577 | 103.2778 | 98.4692
77.176 | 168.5801 | 102.8549 | 102.9452 | 98.4295
78.176 | 168.8154 | 103.0423 | 102.886 | 98.2959
79.176 | 168.408 | 103.2239 | 102.9364 | 98.1595
80.176 | 168.0698 | 102.7727 | 102.8393 | 98.2887
81.176 | 167.8955 | 102.7581 | 102.8396 | 98.4608
82.176 | 167.2181 | 102.8772 | 102.835 | 98.5076
83.176 | 169.0081 | 103.0808 | 102.7806 | 98.318
84.176 | 168.11 | 103.2395 | 102.9721 | 98.0826
85.176 | 168.0089 | 103.2357 | 102.9727 | 98.1662
86.176 | 168.1319 | 103.2965 | 103.2332 | 98.2492
87.176 | 167.9652 | 103.7014 | 103.4062 | 98.5452
88.176 | 168.5189 | 103.6907 | 103.62 | 98.6627
89.176 | 168.0579 | 103.9863 | 103.8232 | 99.9172
90.176 | 170.0289 | 103.9334 | 104.0561 | 100.398
91.176 | 172.7381 | 103.9869 | 104.1832 | 100.5865
92.176 | 175.029 | 104.1902 | 104.5961 | 100.5207
93.176 | 176.8192 | 104.6738 | 104.9811 | 100.6892
94.176 | 177.2703 | 105.3986 | 105.3875 | 101.1293
95.176 | 178.0541 | 105.5994 | 105.8231 | 101.7823
96.176 | 182.9193 | 105.9798 | 106.1945 | 102.0094
97.176 | 184.3078 | 106.91 | 106.528 | 102.4996
98.176 | 185.1999 | 107.1072 | 106.869 | 103.3059
99.176 | 185.6368 | 107.5063 | 107.4466 | 104.0495
100.176 | 187.648 | 107.7947 | 108.0942 | 104.405
101.176 | 191.4394 | 108.6375 | 108.8132 | 105.0246
102.176 | 195.5721 | 109.6365 | 109.5085 | 105.3947
103.176 | 197.2138 | 110.1191 | 110.3241 | 106.0488
104.176 | 197.9922 | 111.1618 | 110.6981 | 106.1346
105.176 | 199.9803 | 111.3521 | 111.1452 | 106.3835
106.176 | 201.7736 | 111.8079 | 111.982 | 106.9105
107.176 | 203.3357 | 112.9482 | 112.5558 | 107.2175
108.176 | 202.6431 | 113.4956 | 113.458 | 107.6425
109.176 | 203.5792 | 113.8256 | 113.9367 | 108.0969
110.176 | 203.3548 | 114.7881 | 114.4041 | 108.6997
111.176 | 204.3948 | 114.5777 | 114.955 | 109.1292
112.176 | 203.6665 | 115.3614 | 115.7301 | 109.2483
113.176 | 204.1564 | 116.4522 | 116.4097 | 109.7951
114.176 | 203.379 | 116.2417 | 116.907 | 110.0101
115.176 | 206.3786 | 116.6154 | 117.2732 | 110.4469
116.176 | 203.9346 | 117.6394 | 117.8143 | 110.9511
117.176 | 202.4652 | 118.9587 | 118.1259 | 111.0487
118.176 | 201.6092 | 119.4345 | 118.4425 | 111.711
119.176 | 200.8861 | 119.466 | 118.9097 | 111.7784
120.176 | 201.2786 | 119.5956 | 119.2682 | 112.5309
121.176 | 201.3081 | 119.6735 | 119.6511 | 113.2617
122.176 | 200.512 | 119.7413 | 119.8241 | 113.7381
123.176 | 199.5924 | 119.763 | 119.8397 | 114.1107
124.176 | 197.415 | 119.597 | 119.887 | 114.2818
125.176 | 196.66 | 119.7898 | 120.2368 | 114.8901
126.176 | 196.1483 | 119.9772 | 120.1987 | 114.6244
127.176 | 196.0408 | 119.95 | 120.1095 | 115.2169
128.176 | 194.841 | 120.0138 | 120.1686 | 114.7567
129.176 | 194.1698 | 119.943 | 120.5253 | 114.8656
130.176 | 193.8522 | 120.1014 | 120.6021 | 115.4795
131.176 | 194.0384 | 120.2143 | 120.7794 | 115.3684
132.176 | 193.6364 | 120.3879 | 121.2664 | 115.4517
133.176 | 193.2731 | 120.5982 | 121.3823 | 115.3372
134.176 | 192.8322 | 120.8619 | 121.2546 | 115.2288
135.176 | 193.6136 | 121.0698 | 121.194 | 115.1104
136.176 | 195.2143 | 121.1859 | 121.2515 | 115.0147
137.176 | 195.1866 | 121.4062 | 121.7358 | 115.3371
138.176 | 194.3946 | 121.9442 | 121.5511 | 115.3313
139.176 | 193.9043 | 121.9363 | 121.7118 | 115.3249
140.176 | 193.3676 | 122.2202 | 121.6666 | 115.2232
141.176 | 192.5621 | 122.5427 | 121.7314 | 115.2551
142.176 | 190.5677 | 122.7991 | 121.4575 | 115.458
143.176 | 189.8709 | 123.2665 | 121.233 | 115.448
144.176 | 189.3413 | 123.2706 | 121.2286 | 115.3966
145.176 | 188.3774 | 123.8849 | 121.3356 | 115.2839
146.176 | 186.5467 | 123.8509 | 121.3968 | 115.4373
147.176 | 184.7447 | 123.8377 | 121.326 | 115.3562
148.176 | 183.2552 | 124.37 | 121.4092 | 115.7358
149.176 | 181.877 | 124.4584 | 121.364 | 115.9125
150.176 | 179.7803 | 124.7408 | 121.487 | 116.1752
151.176 | 178.8665 | 124.4435 | 121.5393 | 116.4315
152.176 | 178.8875 | 124.4445 | 121.6135 | 116.9064
153.176 | 179.5321 | 124.2044 | 121.5871 | 116.7816
154.176 | 179.2533 | 123.915 | 121.5191 | 117.0069
155.176 | 178.4886 | 123.8004 | 121.9411 | 117.2803
156.176 | 178.0174 | 124.123 | 122.06 | 117.366
157.176 | 178.2354 | 124.1737 | 121.9276 | 117.454
158.176 | 178.9041 | 123.6704 | 121.745 | 117.3438
159.176 | 181.1594 | 123.3329 | 121.9266 | 117.4568
160.176 | 182.095 | 123.2183 | 122.0295 | 117.3624
161.176 | 182.8672 | 123.1253 | 122.332 | 117.4204
162.176 | 183.8417 | 122.9381 | 122.4008 | 117.3448
163.176 | 184.4135 | 122.893 | 122.4358 | 117.4344
164.176 | 185.2967 | 123.0403 | 122.5352 | 117.6488
165.176 | 184.1036 | 123.6688 | 122.6321 | 117.556
166.176 | 182.7196 | 124.2153 | 122.6897 | 117.7303
167.176 | 182.2494 | 124.2177 | 122.6806 | 117.5377
168.176 | 182.0087 | 124.9099 | 123.1286 | 118.3335
169.176 | 181.7288 | 125.032 | 123.3814 | 118.6363
170.176 | 182.1133 | 125.1716 | 123.6755 | 118.3629
171.176 | 181.6552 | 125.448 | 123.799 | 118.199
172.176 | 181.3283 | 125.5315 | 124.1867 | 118.3612
173.176 | 181.641 | 125.4659 | 124.1762 | 118.3446
174.176 | 181.525 | 125.4173 | 124.1482 | 118.7576
175.176 | 181.5872 | 125.4644 | 124.1462 | 119.2468
176.176 | 180.2342 | 125.6608 | 124.4142 | 119.3169
177.176 | 179.8338 | 126.0685 | 124.6016 | 119.8788
178.176 | 178.768 | 126.2607 | 124.7665 | 119.6085
179.176 | 177.2469 | 126.1364 | 124.9118 | 119.7034
180.176 | 176.3778 | 126.262 | 124.9775 | 119.9095
181.176 | 176.0532 | 126.2082 | 125.0461 | 120.1459
182.176 | 176.718 | 126.2755 | 125.132 | 120.5675
183.176 | 176.5472 | 125.8976 | 125.0104 | 120.8604
184.176 | 177.4263 | 125.529 | 125.0103 | 121.2309
185.176 | 176.7752 | 125.5764 | 125.0111 | 121.5321
186.176 | 177.214 | 125.5258 | 125.1596 | 122.0071
187.176 | 177.3372 | 125.6985 | 125.045 | 122.161
188.176 | 176.5929 | 126.1722 | 125.121 | 122.2842
189.176 | 177.1552 | 126.3217 | 124.9431 | 122.525
190.176 | 176.7722 | 126.8145 | 125.0107 | 122.7097
191.176 | 176.2661 | 127.039 | 125.1507 | 122.6583
192.176 | 176.2988 | 127.3777 | 125.2023 | 122.5222
193.176 | 176.4797 | 127.647 | 125.3522 | 122.1945
194.176 | 180.5747 | 127.7147 | 125.3938 | 122.731
195.176 | 180.9709 | 127.9578 | 125.4521 | 122.7348
196.176 | 181.0967 | 128.241 | 125.7744 | 122.7336
197.176 | 181.0319 | 128.3211 | 125.9713 | 122.7681
198.176 | 180.4158 | 128.3184 | 126.268 | 122.8944
199.176 | 180.5533 | 128.8579 | 126.5189 | 122.8003
200.1917 | 182.9309 | 128.3263 | 126.6676 | 123.0289
201.176 | 183.6228 | 128.6423 | 127.0767 | 123.1543
202.176 | 183.4819 | 128.6202 | 127.2347 | 123.4209
203.176 | 184.1455 | 128.8334 | 127.207 | 123.6735
204.176 | 186.3758 | 129.6249 | 127.1821 | 124.4856
205.176 | 186.5494 | 129.8594 | 127.3952 | 124.5956
206.176 | 188.2468 | 130.2755 | 127.7718 | 125.1093
207.176 | 188.2043 | 130.4236 | 128.1209 | 125.5551
208.176 | 188.7156 | 130.5743 | 128.4479 | 126.0532
209.176 | 188.5034 | 130.7996 | 128.8824 | 126.2371
210.176 | 188.4163 | 130.9432 | 129.0894 | 126.2472
211.176 | 189.5974 | 130.6789 | 129.3312 | 126.4426
212.176 | 192.4238 | 130.5131 | 129.5701 | 127.0772
213.176 | 192.5362 | 130.6929 | 129.7388 | 127.2119
214.176 | 191.7959 | 131.0885 | 129.8467 | 127.0974
215.176 | 191.0976 | 131.4598 | 129.8057 | 126.8785
216.176 | 192.0032 | 132.2916 | 129.9075 | 126.5484
217.176 | 190.436 | 132.3071 | 130.215 | 126.9786
218.176 | 190.18 | 132.6786 | 130.4455 | 126.6046
219.176 | 190.0977 | 132.6638 | 130.6581 | 127.2603
220.176 | 190.5381 | 132.7902 | 130.919 | 127.5848
221.176 | 193.3239 | 132.9892 | 131.0826 | 127.717
222.176 | 195.4017 | 133.0442 | 131.3704 | 127.4312
223.176 | 196.2621 | 133.0415 | 131.6525 | 127.615
224.176 | 196.6068 | 134.0483 | 131.806 | 128.006
225.176 | 197.5989 | 134.4948 | 132.19 | 128.8623
226.176 | 197.2192 | 134.5567 | 132.8852 | 129.7853
227.176 | 196.3667 | 135.1574 | 133.2164 | 130.9058
228.176 | 195.5817 | 135.6657 | 133.9124 | 131.1443
229.176 | 194.923 | 135.6983 | 133.9912 | 131.0526
230.176 | 193.9742 | 135.8632 | 134.2068 | 131.3163
231.176 | 193.5343 | 136.1446 | 134.64 | 131.7922
232.176 | 192.9048 | 136.7506 | 134.9003 | 131.4013
233.176 | 192.8061 | 136.9849 | 135.0361 | 131.5857
234.176 | 193.4086 | 137.7036 | 136.0176 | 131.7095
235.176 | 191.5031 | 137.8509 | 135.6662 | 131.4917
236.176 | 192.4609 | 137.5614 | 135.8115 | 131.908
237.176 | 192.6156 | 137.1459 | 136.1162 | 131.7801
238.176 | 193.2115 | 137.0149 | 136.4477 | 131.9195
239.176 | 193.2144 | 137.0037 | 136.7813 | 132.5474
240.176 | 192.1352 | 137.2491 | 136.9263 | 133.1112
241.176 | 190.8415 | 137.5853 | 137.7789 | 133.0914
242.176 | 189.535 | 138.1081 | 138.3024 | 132.6731
243.176 | 187.724 | 138.116 | 138.7752 | 132.6782
244.176 | 187.7378 | 138.4476 | 138.4978 | 133.1831
245.176 | 187.3969 | 138.4146 | 138.351 | 133.0527
246.176 | 186.9679 | 138.5293 | 138.514 | 132.953
247.176 | 186.817 | 139.0734 | 138.6804 | 132.9001
248.176 | 186.2548 | 139.5804 | 138.6559 | 133.1786
249.176 | 186.5773 | 139.6798 | 138.5524 | 133.2545
250.176 | 187.033 | 139.2748 | 138.7274 | 133.14
251.176 | 187.466 | 139.1421 | 138.9562 | 133.1895
252.176 | 187.5512 | 139.4349 | 139.0024 | 133.955
253.176 | 188.5882 | 139.8943 | 139.2609 | 134.0727
254.176 | 189.4786 | 140.0142 | 139.2974 | 133.976
255.176 | 190.0354 | 140.0472 | 139.3659 | 133.7839
256.176 | 190.9036 | 140.1088 | 139.3436 | 133.6864
257.176 | 190.7433 | 140.2944 | 139.5278 | 133.8031
258.176 | 190.2056 | 140.1672 | 139.9267 | 133.96
259.176 | 190.8595 | 141.1637 | 140.2343 | 134.107
260.176 | 190.9334 | 141.0346 | 140.4313 | 133.7982
261.176 | 191.1686 | 141.0415 | 140.5922 | 133.6619
262.176 | 190.5994 | 141.4832 | 140.7024 | 133.7732
263.176 | 191.9353 | 141.9721 | 140.8295 | 133.8788
264.176 | 193.3936 | 141.7797 | 141.0299 | 133.53
265.176 | 196.2832 | 141.4918 | 141.0228 | 133.7418
266.176 | 197.0326 | 141.6606 | 141.1515 | 134.1604
267.176 | 196.8013 | 141.9941 | 141.2436 | 134.7148
268.176 | 197.8077 | 142.2723 | 141.1762 | 134.6208
269.176 | 197.7064 | 142.1438 | 141.0629 | 134.3028
270.176 | 197.3804 | 141.9843 | 141.0083 | 134.4487
271.176 | 197.9867 | 142.1192 | 140.9036 | 134.2757
272.176 | 197.4424 | 142.0174 | 141.1293 | 134.3694
273.176 | 199.6293 | 142.0161 | 141.0707 | 134.3719
274.176 | 199.321 | 142.2586 | 141.1085 | 134.4896
275.176 | 198.1087 | 142.1882 | 141.2951 | 134.6382
276.176 | 197.5141 | 142.3781 | 141.4066 | 135.1688
277.176 | 197.3728 | 143.7882 | 141.5813 | 134.837
278.176 | 197.969 | 143.8936 | 141.8363 | 134.9149
279.176 | 197.8692 | 143.9346 | 141.9839 | 135.1879
280.176 | 198.4718 | 144.6423 | 142.0237 | 134.7322
281.176 | 198.9301 | 143.9759 | 142.1812 | 134.9887
282.176 | 200.0151 | 144.2966 | 142.4742 | 136.135
283.176 | 199.55 | 143.9441 | 142.2837 | 135.8113
284.176 | 200.153 | 143.7722 | 142.2281 | 135.5448
285.176 | 201.1756 | 143.5713 | 142.6887 | 135.6037
286.176 | 201.5907 | 143.5577 | 142.6593 | 135.6772
287.176 | 202.5111 | 143.5716 | 142.642 | 135.5725
288.176 | 203.8544 | 143.3947 | 142.8979 | 135.7527
289.176 | 204.5104 | 143.1854 | 143.1352 | 136.4237
290.176 | 206.6885 | 143.4265 | 143.3835 | 136.8475
291.176 | 208.2661 | 144.3675 | 143.7713 | 137.4669
292.176 | 208.9959 | 144.4782 | 143.8153 | 137.4898
293.176 | 208.3704 | 145.8137 | 144.0054 | 137.6591
294.176 | 207.5615 | 145.8361 | 144.634 | 138.2466
295.176 | 206.4902 | 145.7867 | 144.9823 | 138.9443
296.176 | 205.919 | 146.8351 | 145.3525 | 139.1435
297.176 | 205.628 | 146.7536 | 145.9254 | 139.6895
298.176 | 204.727 | 146.6895 | 146.3246 | 139.7383
299.176 | 205.5194 | 147.2506 | 146.4629 | 139.6553
300.176 | 205.0129 | 147.6024 | 146.3944 | 140.0794
301.176 | 203.6735 | 147.6801 | 146.5186 | 140.7461
302.176 | 203.4294 | 148.3504 | 146.826 | 140.6278
303.176 | 203.449 | 148.0542 | 146.8374 | 140.7603
304.176 | 202.6173 | 148.5753 | 147.8987 | 141.0809
305.176 | 201.99 | 149.024 | 147.9996 | 140.8966
306.176 | 201.8814 | 148.6669 | 148.0064 | 140.7663
307.176 | 204.9336 | 149.323 | 148.0142 | 140.616
308.176 | 206.421 | 150.1139 | 147.9812 | 140.9996
309.176 | 206.2464 | 149.5909 | 148.1809 | 141.8892
310.176 | 207.0483 | 149.2137 | 148.2739 | 142.0976
311.176 | 205.4129 | 149.1643 | 148.2849 | 142.0928
312.176 | 206.1935 | 149.0338 | 148.3014 | 142.2623
313.176 | 207.2889 | 148.4469 | 148.2327 | 142.347
314.176 | 207.3605 | 148.311 | 148.2206 | 142.1255
315.176 | 205.5355 | 148.1536 | 148.147 | 141.8306
316.176 | 205.8308 | 148.7368 | 148.1268 | 142.6026
317.176 | 203.6703 | 148.8989 | 148.1386 | 142.4944
318.176 | 202.8263 | 149.2424 | 148.7315 | 142.62
319.176 | 202.7207 | 150.8941 | 149.9311 | 143.0149
320.176 | 201.1533 | 150.6053 | 149.674 | 142.9049
321.176 | 200.0682 | 150.697 | 149.8724 | 142.5285
322.176 | 197.8847 | 150.3656 | 150.4232 | 142.935
323.176 | 196.1902 | 150.0426 | 150.5161 | 142.7628
324.176 | 195.39 | 149.8643 | 150.4037 | 142.7041
325.176 | 194.514 | 150.233 | 150.2733 | 142.4006
326.176 | 193.8863 | 150.1517 | 150.219 | 143.2539
327.176 | 193.5485 | 150.2556 | 150.4122 | 142.9864
328.176 | 192.2553 | 150.2415 | 150.401 | 142.8353
329.176 | 191.9887 | 150.6234 | 150.2091 | 142.5842
330.176 | 191.6605 | 149.6252 | 150.3685 | 142.5873
331.176 | 191.9088 | 149.1244 | 150.2889 | 142.6367
332.176 | 191.5413 | 148.9789 | 150.3487 | 142.5421
333.176 | 192.4124 | 148.8837 | 150.3527 | 142.5057
334.176 | 193.7372 | 149.0934 | 150.4557 | 142.0764
335.176 | 193.173 | 148.6812 | 150.0091 | 141.755
336.176 | 193.1751 | 148.742 | 149.7453 | 141.4356
337.176 | 193.9417 | 148.8457 | 149.5398 | 141.1763
338.176 | 194.5263 | 149.3696 | 149.2513 | 141.0356
339.176 | 194.1948 | 148.9771 | 148.9388 | 140.8935
340.176 | 193.2552 | 149.0235 | 148.6397 | 140.4856
341.176 | 192.2033 | 148.4088 | 148.6358 | 140.4073
342.176 | 192.4267 | 148.0152 | 148.5475 | 140.6447
343.176 | 192.2341 | 147.3174 | 148.6612 | 140.7402
344.176 | 192.125 | 147.689 | 149.1235 | 141.0696
345.176 | 193.8586 | 148.4097 | 149.2643 | 141.1239
346.176 | 194.7611 | 148.338 | 149.2897 | 141.6637
347.176 | 196.1836 | 148.5102 | 149.1466 | 142.0323
348.176 | 196.733 | 149.2791 | 149.227 | 141.9107
349.176 | 197.1922 | 149.0861 | 149.3295 | 141.6932
350.176 | 198.1945 | 148.9328 | 149.5558 | 141.8447
351.176 | 200.0714 | 149.1671 | 149.5491 | 142.0325
352.176 | 200.8463 | 150.0738 | 149.8886 | 142.3424
353.176 | 200.924 | 150.6067 | 150.0981 | 142.7089
354.176 | 201.1545 | 150.6506 | 150.2872 | 142.9557
355.176 | 200.8101 | 150.8139 | 150.5912 | 142.9846
356.176 | 199.7026 | 151.5776 | 151.0321 | 143.1873
357.176 | 198.2972 | 151.2831 | 151.3708 | 143.3539
358.176 | 197.4508 | 150.9137 | 151.3118 | 143.6111
359.176 | 197.7134 | 151.4897 | 151.5056 | 143.8117
360.176 | 197.4927 | 152.4805 | 151.7395 | 143.6127
361.176 | 195.7968 | 152.9677 | 151.7852 | 142.9101
362.176 | 194.5712 | 152.4704 | 151.7273 | 142.8072
363.176 | 194.327 | 152.2 | 151.7309 | 143.3015
364.176 | 193.351 | 151.8821 | 151.4394 | 143.2921
365.176 | 194.1039 | 151.5384 | 151.1541 | 144.5325
366.176 | 194.1109 | 150.9288 | 150.9127 | 144.1901
367.176 | 193.5112 | 150.7892 | 150.8914 | 144.0253
368.176 | 193.4633 | 150.1831 | 150.7704 | 143.8515
369.176 | 193.4273 | 150.6006 | 150.7195 | 144.0881
370.176 | 194.3835 | 150.4084 | 150.8694 | 144.5558
371.176 | 195.9764 | 150.0667 | 150.8476 | 144.3808
372.176 | 197.1772 | 149.8895 | 150.8781 | 144.1236
373.176 | 199.4737 | 150.1643 | 150.9843 | 144.1293
374.176 | 199.6877 | 150.3456 | 151.1291 | 144.2828
375.176 | 199.7299 | 151.0057 | 151.5858 | 144.2984
376.176 | 200.027 | 151.8007 | 152.267 | 145.1603
377.176 | 200.1556 | 151.7322 | 152.7533 | 145.5862
378.176 | 200.1882 | 152.0984 | 153.574 | 146.0319
379.176 | 200.731 | 152.6791 | 153.7897 | 146.2815
380.176 | 201.8937 | 152.9605 | 153.9194 | 146.3695
381.176 | 203.2421 | 153.3128 | 154.1974 | 146.1565
382.176 | 203.3942 | 153.5116 | 154.4465 | 146.2119
383.176 | 203.7056 | 153.3263 | 154.651 | 146.1472
384.176 | 202.8631 | 154.3664 | 154.5501 | 145.87
385.176 | 202.3739 | 154.0587 | 154.2222 | 145.7184
386.176 | 201.2026 | 154.0722 | 154.1099 | 145.9274
387.176 | 200.6527 | 154.0921 | 153.8881 | 146.0485
388.176 | 200.5346 | 153.7933 | 154.0192 | 145.9621
389.176 | 201.2899 | 153.6593 | 153.9062 | 145.9327
390.176 | 202.6472 | 153.4945 | 153.9566 | 145.9538
391.176 | 202.4221 | 153.161 | 153.7995 | 146.0181
392.176 | 202.1748 | 153.4161 | 153.6943 | 146.1365
393.176 | 202.7681 | 153.7472 | 154.1887 | 147.7437
394.176 | 204.34 | 153.1447 | 154.2844 | 147.6101
395.176 | 204.5987 | 152.6582 | 154.332 | 147.9343
396.176 | 205.3363 | 153.3542 | 154.8277 | 148.0261
397.176 | 206.1207 | 153.5054 | 154.7497 | 148.3035
398.176 | 206.766 | 153.4812 | 155.0877 | 148.1892
399.176 | 206.8225 | 153.8852 | 155.5536 | 148.2229
400.176 | 206.3617 | 154.3546 | 155.8951 | 148.4673
401.176 | 206.0014 | 154.8828 | 156.0962 | 148.3956
402.176 | 204.9856 | 154.6166 | 156.3344 | 148.2882
403.176 | 203.3994 | 154.2828 | 156.7053 | 148.2252
404.176 | 203.9902 | 154.684 | 156.947 | 148.8811
405.176 | 203.9516 | 155.1608 | 156.9285 | 149.1601
406.176 | 203.0786 | 155.1767 | 156.8561 | 149.2276
407.176 | 202.7179 | 155.1827 | 156.8091 | 149.1965
408.176 | 202.8919 | 154.5332 | 156.7301 | 148.9769
409.176 | 201.8255 | 154.2098 | 156.4524 | 148.7123
410.176 | 201.9599 | 153.7511 | 156.1655 | 148.505
411.176 | 200.8472 | 154.2491 | 155.9866 | 148.6175
412.176 | 200.9629 | 155.0691 | 155.9025 | 148.6301
413.176 | 199.5043 | 154.9641 | 155.9778 | 148.4623
414.176 | 199.489 | 154.6311 | 155.8076 | 148.3346
415.176 | 199.7342 | 154.7627 | 156.1092 | 148.289
416.176 | 199.3393 | 154.7833 | 156.0047 | 148.0872
417.1917 | 199.3649 | 154.5897 | 155.8111 | 148.0828
418.176 | 200.8913 | 154.1594 | 156.1532 | 147.986
419.176 | 199.785 | 153.6485 | 155.7177 | 147.8647
420.1917 | 199.978 | 153.29 | 155.5792 | 147.8404
421.176 | 200.1941 | 153.7013 | 155.4674 | 147.6882
422.176 | 200.4056 | 153.8398 | 155.4109 | 147.9581
423.1917 | 200.9264 | 153.8859 | 155.3523 | 147.8762
424.1917 | 201.7606 | 154.2588 | 155.6319 | 147.8532
425.176 | 202.3414 | 153.6093 | 155.8202 | 147.9823
426.176 | 203.0875 | 153.238 | 155.8996 | 147.9703
427.176 | 203.6091 | 152.7623 | 155.9293 | 148.5372
428.176 | 203.1853 | 153.2155 | 156.1372 | 148.2064
429.176 | 203.8614 | 153.4007 | 155.9646 | 147.9949
430.176 | 204.0243 | 153.213 | 156.19 | 148.0827
431.176 | 203.9333 | 153.7365 | 156.1108 | 148.0048
432.176 | 205.2377 | 153.8357 | 156.0388 | 148.2098
433.176 | 205.9782 | 153.9384 | 156.0384 | 148.1576
434.176 | 207.7349 | 153.8592 | 156.4855 | 148.2063
435.176 | 208.798 | 154.0119 | 156.3605 | 148.0159
436.176 | 209.236 | 154.2311 | 156.2273 | 148.1466
437.1917 | 209.2603 | 153.8656 | 156.1329 | 148.7007
438.176 | 208.0715 | 153.9691 | 156.1715 | 148.8737
439.176 | 209.171 | 153.3437 | 156.3062 | 148.7708
440.176 | 210.465 | 153.087 | 156.354 | 148.7946
441.176 | 212.2561 | 152.7368 | 156.3408 | 149.0116
442.176 | 211.4059 | 153.1838 | 156.3669 | 149.3344
443.176 | 210.3582 | 153.4162 | 156.4113 | 149.8597
444.176 | 210.3486 | 153.7957 | 156.3735 | 150.2203
445.176 | 210.8734 | 153.9895 | 156.2318 | 150.0945
446.176 | 211.3944 | 153.2768 | 156.0423 | 149.9366
447.176 | 212.0186 | 152.8911 | 155.8651 | 149.7385
448.176 | 211.3277 | 152.9658 | 155.8844 | 150.2193
449.176 | 211.1933 | 153.1462 | 155.8214 | 149.7553
450.176 | 210.6357 | 152.9384 | 155.8066 | 150.6329
451.176 | 210.4012 | 153.2891 | 155.6675 | 150.4594
452.176 | 210.6398 | 153.1349 | 155.6425 | 150.5366
453.176 | 211.4551 | 153.3086 | 155.4506 | 150.1936
454.176 | 211.6709 | 153.1001 | 155.0673 | 149.777
455.176 | 212.419 | 153.0731 | 155.0051 | 149.6024
456.176 | 210.7527 | 153.0066 | 154.7632 | 149.4353
457.176 | 211.0848 | 153.2209 | 154.7537 | 149.2344
458.176 | 210.4951 | 153.4528 | 154.7142 | 149.1199
459.176 | 209.4204 | 153.7606 | 154.7189 | 148.9244
460.176 | 208.398 | 153.5505 | 154.7213 | 148.7985
461.176 | 208.4824 | 153.1925 | 154.744 | 148.8029
462.176 | 207.6763 | 153.3848 | 155.0165 | 148.7945
463.176 | 208.0331 | 153.4686 | 155.2659 | 148.8991
464.176 | 208.0549 | 153.5814 | 155.1502 | 149.1896
465.176 | 208.7116 | 154.169 | 154.8865 | 149.0813
466.176 | 207.8613 | 154.9968 | 154.9671 | 148.8349
467.176 | 210.512 | 155.4355 | 154.924 | 148.8987
468.176 | 212.7835 | 155.4734 | 154.9726 | 149.3085
469.176 | 213.56 | 155.9283 | 154.9141 | 149.3389
470.176 | 214.2305 | 156.5493 | 154.8329 | 149.0148
471.176 | 213.9423 | 156.0493 | 154.9345 | 149.0591
472.176 | 213.3243 | 156.1566 | 155.0074 | 149.2375
473.176 | 211.4722 | 156.0916 | 155.1794 | 149.3604
474.176 | 210.2412 | 156.2015 | 155.3608 | 149.3618
475.1917 | 208.9941 | 156.6257 | 155.1076 | 149.4851
476.176 | 208.7877 | 156.4521 | 155.1539 | 149.619
477.176 | 208.9649 | 156.7174 | 155.3997 | 149.7738
478.176 | 208.4553 | 157.1367 | 155.7 | 149.8684
479.176 | 208.2795 | 157.2401 | 155.4562 | 149.8193
480.1917 | 207.6481 | 156.7937 | 155.4918 | 149.8072
481.1917 | 207.1827 | 156.1255 | 155.2928 | 149.6773
482.176 | 206.4887 | 155.8034 | 155.1405 | 149.5845
483.176 | 205.8888 | 155.6073 | 155.0839 | 149.6915
484.176 | 207.3727 | 155.3064 | 154.9169 | 149.63
485.176 | 206.817 | 155.3774 | 154.7225 | 149.9085
486.176 | 206.6904 | 155.4652 | 154.459 | 150.0413
487.176 | 207.5693 | 155.146 | 154.6719 | 150.0452
488.176 | 207.6317 | 155.0542 | 154.5884 | 150.0722
489.176 | 208.5675 | 154.639 | 154.5508 | 150.0121
490.176 | 209.0575 | 154.3185 | 154.5435 | 150.0607
491.176 | 209.1361 | 154.5928 | 154.6223 | 150.161
492.176 | 208.4935 | 154.6233 | 155.2586 | 150.2768
493.176 | 208.1133 | 154.5918 | 155.1678 | 150.2043
494.176 | 207.3976 | 154.5131 | 155.0841 | 150.2309
495.176 | 207.5931 | 154.2951 | 154.8828 | 150.0508
496.176 | 206.0171 | 154.2866 | 154.671 | 150.1371
497.176 | 205.7172 | 154.7628 | 154.1611 | 150.1745
498.176 | 205.1101 | 154.4542 | 153.9693 | 150.1501
499.176 | 205.7086 | 153.9226 | 153.7092 | 149.827
500.176 | 205.3856 | 153.6086 | 153.5052 | 149.8784
501.176 | 204.9014 | 153.4663 | 153.3503 | 149.777
502.176 | 204.2346 | 153.7681 | 153.4121 | 149.4002
503.176 | 204.4906 | 154.0293 | 153.346 | 149.0956
504.176 | 203.0529 | 154.0496 | 153.2062 | 148.9131
505.176 | 203.4184 | 153.8476 | 153.0175 | 149.0058
506.176 | 204.9845 | 153.8749 | 152.7878 | 149.0369
507.176 | 205.5333 | 154.0347 | 152.6596 | 149.1594
508.176 | 205.7951 | 154.1228 | 152.683 | 149.4081
509.176 | 205.315 | 154.0026 | 152.7691 | 149.5315
510.176 | 205.2711 | 154.1261 | 152.9338 | 149.7101
511.176 | 205.1537 | 153.7242 | 153.1211 | 149.9314
512.176 | 205.9806 | 153.7008 | 153.2971 | 149.7463
513.176 | 205.5094 | 154.2708 | 153.4065 | 149.6722
514.176 | 205.5406 | 154.4768 | 153.5319 | 149.7857
515.176 | 204.9609 | 154.4475 | 153.7045 | 149.6063
516.176 | 205.1312 | 154.1395 | 153.7833 | 149.7505
517.176 | 203.6555 | 154.141 | 153.8075 | 149.6811
518.176 | 204.0153 | 154.3464 | 153.8979 | 149.5802
519.176 | 204.1567 | 154.3956 | 154.1572 | 149.8922
520.176 | 204.6754 | 154.4328 | 154.2041 | 149.8429
521.176 | 203.5468 | 154.3377 | 154.3052 | 149.9661
522.176 | 202.6379 | 154.224 | 154.243 | 149.6704
523.176 | 202.1863 | 154.8887 | 154.3166 | 150.0996
524.176 | 201.153 | 155.3028 | 154.3764 | 150.1894
525.176 | 201.2196 | 155.0978 | 154.4265 | 150.0361
526.176 | 201.0544 | 155.2538 | 154.8034 | 150.0485
527.176 | 201.6568 | 155.0056 | 155.0937 | 150.1327
528.176 | 201.2802 | 155.6418 | 155.3321 | 149.8613
529.176 | 200.6023 | 155.7874 | 155.9293 | 150.6334
530.176 | 198.7806 | 155.8301 | 156.8131 | 150.9809
531.176 | 199.6468 | 156.3419 | 157.5113 | 151.4106
532.176 | 199.7492 | 156.5813 | 157.8349 | 151.9036
533.176 | 199.5208 | 158.3001 | 158.4736 | 153.0384
534.176 | 198.4262 | 158.2099 | 158.7381 | 153.4881
535.176 | 198.2394 | 158.3009 | 158.6414 | 153.3977
536.176 | 197.8252 | 158.0283 | 158.7952 | 153.4312
537.176 | 197.3051 | 158.1515 | 159.1153 | 153.2592
538.176 | 196.7986 | 158.2351 | 159.514 | 153.0822
539.176 | 196.5188 | 157.9133 | 159.4364 | 152.7867
540.176 | 195.9334 | 157.8956 | 159.2585 | 152.4979
541.176 | 196.4188 | 157.977 | 159.0528 | 152.4473
542.176 | 196.3452 | 157.9928 | 158.8263 | 152.2783
543.176 | 199.0416 | 157.862 | 158.2882 | 152.2141
544.176 | 200.1515 | 158.0781 | 157.8463 | 152.5556
545.176 | 201.4024 | 158.0076 | 157.6114 | 152.6849
546.176 | 201.8702 | 157.9162 | 157.6326 | 152.7388
547.176 | 201.652 | 157.9169 | 157.6323 | 152.9764
548.176 | 200.1149 | 157.6585 | 157.716 | 152.611
549.176 | 200.0354 | 157.7425 | 157.7575 | 152.5691
550.176 | 200.3872 | 157.6758 | 157.8904 | 153.4831
551.176 | 200.6955 | 157.2499 | 158.4736 | 153.1841
552.176 | 200.8988 | 157.3852 | 158.7533 | 153.0058
553.176 | 201.2242 | 157.2372 | 158.6003 | 152.8395
554.176 | 201.2687 | 157.1046 | 158.551 | 152.7345
555.176 | 201.4417 | 157.6142 | 158.3406 | 152.5518
556.176 | 201.557 | 157.3794 | 158.1609 | 152.4902
557.176 | 202.5337 | 157.84 | 158.2123 | 152.6084
558.176 | 202.1329 | 157.7311 | 158.2917 | 152.7273
559.176 | 201.3969 | 157.8446 | 158.1558 | 152.9647
560.176 | 202.4273 | 158.4939 | 158.1461 | 153.7261
561.176 | 203.2429 | 159.076 | 158.1441 | 153.6886
562.176 | 203.5096 | 158.7861 | 158.4236 | 153.2563
563.176 | 204.2562 | 158.6556 | 158.5628 | 152.9398
564.176 | 204.2914 | 159.3668 | 158.753 | 153.172
565.176 | 204.1636 | 159.1778 | 158.833 | 153.0023
566.176 | 204.4564 | 158.981 | 159.0889 | 153.1209
567.176 | 204.6064 | 158.9262 | 159.8441 | 152.949
568.176 | 205.5885 | 159.3468 | 159.9695 | 152.8813
569.176 | 204.9615 | 158.9306 | 160.3772 | 153.1885
570.176 | 204.9731 | 160.0851 | 160.3497 | 153.6691
571.176 | 205.1719 | 159.6701 | 160.1317 | 153.424
572.176 | 205.0046 | 159.8261 | 159.91 | 153.3248
573.176 | 205.6014 | 159.388 | 159.6839 | 153.1763
574.176 | 203.9764 | 159.7573 | 159.6067 | 153.2783
575.176 | 203.4301 | 159.897 | 159.484 | 153.492
576.176 | 203.8007 | 160.0856 | 159.3224 | 153.3668
577.176 | 204.6774 | 160.2317 | 159.4752 | 153.2882
578.176 | 204.2243 | 159.9901 | 159.625 | 153.1389
579.176 | 203.7835 | 159.3832 | 159.5381 | 153.0296
580.176 | 203.8657 | 158.9136 | 159.507 | 152.804
581.176 | 203.9115 | 159.0897 | 159.392 | 152.8133
582.176 | 203.9192 | 158.8269 | 159.1791 | 152.6312
583.176 | 204.6366 | 158.3397 | 158.8703 | 152.6967
584.176 | 205.8455 | 158.6032 | 158.8169 | 152.3749
585.176 | 205.4888 | 157.8327 | 158.6552 | 152.401
586.176 | 205.5218 | 157.2635 | 158.5366 | 152.6269
587.176 | 204.4211 | 158.4026 | 158.6407 | 152.4434
588.176 | 203.8992 | 158.1217 | 158.6005 | 152.4464
589.176 | 203.6011 | 157.9339 | 158.4504 | 152.6971
590.176 | 203.0925 | 157.9752 | 158.4861 | 152.8751
591.176 | 204.0897 | 157.5094 | 158.5516 | 152.9223
592.176 | 205.6761 | 157.1644 | 158.4017 | 152.7994
593.176 | 205.0071 | 156.978 | 158.7705 | 152.6771
594.176 | 204.4272 | 157.373 | 159.1848 | 152.7924
595.176 | 205.4098 | 158.6004 | 159.1465 | 152.6066
596.176 | 205.3365 | 159.0629 | 159.1363 | 152.573
597.176 | 204.0232 | 159.6987 | 159.098 | 152.6771
598.176 | 203.354 | 160.0709 | 159.0877 | 152.4877
599.176 | 203.6946 | 160.1437 | 158.891 | 152.1527
600.176 | 203.5834 | 160.4144 | 159.2126 | 152.2275
601.176 | 203.5589 | 159.9885 | 159.3394 | 152.3047
602.176 | 202.6261 | 159.6864 | 159.7527 | 152.5903
603.176 | 202.4323 | 159.7259 | 159.7715 | 153.0576
604.176 | 201.2356 | 159.3086 | 160.0433 | 153.023
605.176 | 201.0236 | 159.4848 | 160.1889 | 153.1909
606.176 | 201.0951 | 159.4402 | 160.2165 | 153.6726
607.176 | 201.0864 | 159.7006 | 160.2067 | 154.2451
608.176 | 200.386 | 159.3604 | 160.0903 | 154.1154
609.176 | 200.3766 | 159.2695 | 159.9783 | 153.976
610.176 | 200.5255 | 159.3792 | 159.7027 | 153.8167
611.176 | 200.7784 | 159.0292 | 159.4844 | 153.8042
612.176 | 200.3604 | 158.7874 | 159.3741 | 153.5022
613.176 | 200.3914 | 158.5369 | 159.3901 | 153.3805
614.176 | 200.3075 | 158.1451 | 159.3656 | 153.3565
615.176 | 200.501 | 158.2293 | 159.4327 | 153.3578
616.176 | 200.0202 | 157.9566 | 159.2889 | 153.5193
617.176 | 200.0928 | 158.4853 | 159.428 | 154.0989
618.176 | 200.1277 | 158.34 | 159.4027 | 154.2908
619.176 | 200.2673 | 158.5394 | 159.7265 | 154.4985
620.176 | 200.6903 | 158.0901 | 159.8303 | 154.0489
621.176 | 200.8191 | 158.2609 | 160.0894 | 153.904
622.176 | 200.6793 | 159.4968 | 159.9565 | 153.8788
623.176 | 200.514 | 160.1036 | 160.0028 | 153.9374
624.176 | 199.7258 | 160.3712 | 160.1204 | 153.9687
625.176 | 199.6712 | 160.9256 | 160.8115 | 154.4411
626.176 | 200.0508 | 161.2587 | 161.1089 | 154.5788
627.176 | 200.4927 | 161.0921 | 161.2434 | 154.5603
628.176 | 201.3527 | 161.1558 | 161.6191 | 154.4252
629.176 | 201.9175 | 161.5496 | 161.6129 | 154.8026
630.176 | 201.7325 | 161.0868 | 161.781 | 155.3047
631.176 | 201.6259 | 161.2956 | 161.9627 | 155.1269
632.176 | 201.5436 | 160.9364 | 162.0159 | 155.165
633.176 | 200.5757 | 161.1004 | 161.9564 | 155.161
634.176 | 201.3224 | 161.3983 | 161.8985 | 155.3574
635.176 | 202.0429 | 161.3836 | 161.7168 | 155.134
636.176 | 202.3967 | 161.473 | 161.952 | 155.1523
637.176 | 202.2661 | 161.8348 | 162.0115 | 155.1218
638.176 | 202.0135 | 161.7709 | 162.1952 | 155.3011
639.176 | 201.4112 | 162.5329 | 162.194 | 154.9974
640.176 | 201.8468 | 163.4446 | 162.3032 | 155.0548
641.176 | 202.0967 | 163.8007 | 162.3782 | 155.1432
642.176 | 202.1897 | 163.5873 | 162.1943 | 155.063
643.176 | 200.9758 | 163.6756 | 162.1653 | 155.0578
644.176 | 199.7403 | 163.1628 | 162.2208 | 155.5964
645.1917 | 200.2462 | 163.5117 | 162.18 | 155.3609
646.176 | 199.6618 | 163.2479 | 162.4029 | 155.217
647.176 | 199.6344 | 162.6477 | 162.7022 | 154.9412
648.176 | 199.4052 | 163.6341 | 163.5756 | 154.5536
649.176 | 199.825 | 164.0076 | 163.6205 | 154.5039
650.176 | 201.3278 | 163.6698 | 164.0377 | 154.9777
651.176 | 202.9416 | 163.4389 | 163.8477 | 155.041
652.176 | 203.7388 | 163.0916 | 163.835 | 155.3095
653.176 | 203.645 | 163.7006 | 163.7713 | 156.3055
654.176 | 203.7069 | 163.4501 | 164.1744 | 156.3219
655.176 | 204.7728 | 163.5525 | 164.4121 | 156.3318
656.176 | 205.2312 | 163.3991 | 164.3453 | 156.9105
657.176 | 205.5538 | 163.44 | 165.2084 | 157.234
658.176 | 206.363 | 163.206 | 165.0962 | 157.1617
659.176 | 207.6497 | 162.6988 | 165.3356 | 157.0154
660.176 | 208.1207 | 162.3529 | 165.2958 | 156.9942
661.176 | 210.0719 | 162.4047 | 165.499 | 156.9799
662.176 | 210.1512 | 163.3213 | 165.8114 | 156.7404
663.176 | 209.2668 | 163.2219 | 166.7315 | 156.7295
664.176 | 209.0077 | 163.0665 | 166.7036 | 156.7378
665.176 | 209.0274 | 163.3893 | 166.9376 | 156.9522
666.176 | 209.93 | 163.7872 | 166.9357 | 157.0021
667.176 | 209.7606 | 164.0055 | 166.8384 | 157.3638
668.176 | 209.2705 | 163.3948 | 166.4447 | 157.2569
669.176 | 210.027 | 163.0794 | 166.3967 | 157.5874
670.176 | 209.7899 | 163.0836 | 166.314 | 157.4759
671.176 | 210.4643 | 163.1309 | 166.0658 | 157.3323
672.176 | 211.2587 | 163.2138 | 165.8493 | 157.0816
673.176 | 211.0551 | 163.1718 | 165.6539 | 156.9225
674.176 | 211.6346 | 162.9925 | 165.4419 | 156.9017
675.176 | 212.3083 | 162.9935 | 165.4044 | 157.2111
676.176 | 211.4809 | 162.9216 | 165.36 | 157.2201
677.176 | 211.6892 | 162.8868 | 165.2431 | 157.3248
678.176 | 212.6686 | 162.7054 | 164.8633 | 157.5185
679.176 | 211.4925 | 162.6982 | 165.0972 | 158.0479
680.176 | 211.5063 | 163.1971 | 165.2122 | 158.465
681.176 | 212.2312 | 163.0763 | 165.1851 | 158.8221
682.176 | 211.517 | 162.6587 | 165.4766 | 158.8883
683.176 | 211.1978 | 162.7706 | 165.331 | 159.0294
684.176 | 211.7626 | 162.8433 | 165.4921 | 159.0324
685.176 | 212.383 | 162.5025 | 165.6441 | 158.9251
686.176 | 212.0082 | 163.1449 | 165.5047 | 158.9601
687.176 | 212.2459 | 163.7101 | 166.079 | 159.4064
688.176 | 212.7383 | 163.7829 | 166.7176 | 159.3976
689.176 | 213.4308 | 164.1015 | 166.8714 | 159.4506
690.176 | 215.2139 | 164.1271 | 167.2193 | 159.6257
691.176 | 215.1833 | 163.8014 | 167.7562 | 159.6417
692.176 | 215.9937 | 164.1348 | 167.8348 | 159.8121
693.176 | 216.1485 | 164.3658 | 168.1944 | 160.1376
694.176 | 216.5831 | 164.5098 | 167.6427 | 160.2758
695.176 | 216.0987 | 164.2888 | 167.4539 | 160.1689
696.176 | 215.3522 | 164.5312 | 167.2409 | 159.9707
697.176 | 216.0127 | 164.3935 | 167.0333 | 159.9829
698.176 | 217.5665 | 164.3093 | 167.2139 | 160.2384
699.176 | 218.305 | 163.9887 | 167.0536 | 160.3025
700.176 | 218.1974 | 164.4992 | 166.8705 | 160.562
701.176 | 219.4156 | 164.0225 | 166.7264 | 160.5492
702.176 | 218.9788 | 163.5149 | 166.5213 | 160.5584
703.176 | 218.6483 | 163.2339 | 166.3925 | 160.2668
704.176 | 220.4092 | 163.3955 | 166.2481 | 160.0883
705.176 | 219.838 | 163.3706 | 166.0959 | 159.973
706.176 | 219.4835 | 163.2051 | 166.2646 | 159.8497
707.176 | 218.5678 | 163.5456 | 166.2706 | 159.4826
708.176 | 220.9624 | 163.4644 | 166.4863 | 159.5001
709.176 | 221.6485 | 163.1456 | 166.5999 | 159.5175
710.176 | 222.0268 | 163.2826 | 166.618 | 159.7073
711.176 | 221.355 | 162.9486 | 166.616 | 159.7931
712.176 | 221.1324 | 162.8533 | 166.5662 | 160.0003
713.176 | 220.7606 | 162.6934 | 166.4447 | 160.0479
714.176 | 220.9456 | 162.7307 | 166.3159 | 160.2811
715.176 | 221.0052 | 162.5612 | 166.2945 | 160.1216
716.176 | 221.6978 | 162.4309 | 166.3169 | 160.0108
717.176 | 220.7541 | 162.5461 | 166.3429 | 160.1006
718.176 | 220.5095 | 162.5155 | 166.4423 | 160.2424
719.176 | 220.792 | 162.8096 | 166.9789 | 160.1381
720.176 | 222.3077 | 162.4386 | 167.1375 | 160.1425
721.176 | 222.7505 | 162.9259 | 167.1949 | 160.4446
722.176 | 223.2908 | 163.1897 | 167.1894 | 160.4376
723.176 | 223.7599 | 163.2487 | 167.2546 | 160.6277
724.176 | 223.2692 | 163.1549 | 167.1284 | 161.0325
725.176 | 222.8913 | 163.0638 | 167.0429 | 160.7371
726.176 | 222.467 | 162.9671 | 167.0564 | 161.0081
727.176 | 223.2738 | 162.7356 | 166.9396 | 161.3839
728.176 | 224.0057 | 162.4555 | 166.7494 | 161.4851
729.176 | 226.5447 | 162.3775 | 166.6787 | 161.8266
730.176 | 228.7428 | 162.0403 | 166.6784 | 162.0482
731.176 | 227.4905 | 162.313 | 166.9627 | 162.1562
732.176 | 226.7867 | 162.5977 | 167.0359 | 162.1658
733.176 | 227.244 | 162.5448 | 167.123 | 162.0465
734.176 | 227.0619 | 162.5861 | 167.2939 | 162.2622
735.176 | 225.2495 | 162.3634 | 167.5577 | 162.3774
736.176 | 225.3478 | 162.3836 | 167.622 | 162.0835
737.176 | 225.3933 | 162.3405 | 167.5674 | 161.9126
738.176 | 225.8039 | 162.13 | 167.4777 | 161.7768
739.176 | 228.0223 | 162.9308 | 167.6121 | 161.9939
740.176 | 228.2245 | 163.373 | 167.8025 | 162.0439
741.176 | 228.8153 | 163.8552 | 168.002 | 162.1019
742.176 | 231.8751 | 163.9101 | 168.35 | 162.418
743.176 | 233.8231 | 163.9525 | 168.4237 | 162.2404
744.176 | 234.5533 | 163.8722 | 168.4402 | 161.6887
745.176 | 238.0389 | 164.2733 | 168.5256 | 161.5891
746.176 | 241.1744 | 164.9411 | 168.5319 | 161.732
747.176 | 242.6079 | 165.2086 | 168.6605 | 161.8897
748.176 | 243.5787 | 164.8475 | 168.7016 | 161.7256
749.176 | 244.8934 | 164.955 | 168.836 | 161.7492
750.176 | 244.579 | 164.8007 | 168.9723 | 161.7625
751.176 | 245.1372 | 164.7793 | 169.1377 | 161.6862
752.176 | 245.4679 | 164.8145 | 169.3575 | 161.5289
753.176 | 248.3411 | 165.19 | 169.7096 | 161.9268
754.176 | 250.4539 | 165.3979 | 170.3543 | 162.1806
755.176 | 251.1277 | 166.1535 | 170.3408 | 162.6868
756.176 | 251.0289 | 165.8461 | 170.7941 | 163.2914
757.176 | 250.5443 | 165.5892 | 170.9053 | 163.0045
758.176 | 249.418 | 165.2883 | 171.0941 | 162.9738
759.176 | 249.1836 | 165.5871 | 171.4321 | 163.3313
760.176 | 248.8143 | 165.4629 | 171.4163 | 163.5314
761.176 | 247.6712 | 165.2851 | 171.5676 | 163.7573
762.176 | 248.5879 | 164.7871 | 171.5307 | 163.8202
763.176 | 247.058 | 164.5027 | 171.3946 | 163.698
764.176 | 247.5385 | 164.688 | 171.1559 | 163.4552
765.176 | 249.0363 | 164.5069 | 170.9393 | 163.4847
766.176 | 250.431 | 164.1649 | 170.765 | 163.289
767.176 | 253.2409 | 164.0895 | 170.5056 | 163.1206
768.176 | 252.728 | 164.5464 | 170.19 | 163.4364
769.176 | 251.961 | 165.0342 | 170.1274 | 163.7316
770.176 | 251.2532 | 165.518 | 170.0424 | 163.6315
771.176 | 250.1438 | 165.3775 | 169.9854 | 163.6233
772.176 | 252.7585 | 165.7162 | 170.0282 | 163.4621
773.176 | 257.4405 | 165.591 | 170.1505 | 163.4671
774.176 | 257.2446 | 165.5992 | 170.2383 | 163.1469
775.176 | 259.2421 | 165.4371 | 170.2813 | 163.021
776.176 | 261.2196 | 165.6409 | 170.4669 | 163.0898
777.176 | 264.0516 | 166.1735 | 170.6756 | 163.1528
778.176 | 263.788 | 166.2846 | 170.9191 | 163.2746
779.176 | 264.0956 | 165.8887 | 170.9897 | 163.2021
780.176 | 264.0712 | 165.4915 | 170.8054 | 163.4483
781.176 | 264.5986 | 165.3672 | 171.2022 | 163.6466
782.176 | 265.3907 | 165.3292 | 171.6807 | 163.7607
783.176 | 265.7121 | 165.7799 | 171.5744 | 164.0145
784.176 | 269.9923 | 166.2387 | 171.4721 | 164.4714
785.176 | 268.1533 | 166.2169 | 171.5588 | 164.3289
786.176 | 273.144 | 166.1163 | 171.5482 | 164.0666
787.176 | 273.9289 | 166.3681 | 171.5628 | 164.4222
788.176 | 273.6785 | 166.2611 | 171.5815 | 164.5397
789.176 | 272.0569 | 166.1668 | 172.0843 | 164.7598
790.176 | 271.0115 | 166.0379 | 171.8828 | 164.3696
791.176 | 269.7414 | 166.0756 | 171.7882 | 164.2385
792.176 | 270.6111 | 166.2533 | 171.5397 | 164.271
793.176 | 269.2597 | 166.0727 | 171.473 | 164.3537
794.176 | 269.6048 | 165.9501 | 171.2233 | 164.2538
795.176 | 279.4741 | 166.0787 | 171.077 | 164.5328
796.176 | 278.8211 | 166.1639 | 171.0364 | 164.1916
797.176 | 279.735 | 166.5744 | 171.0951 | 164.3035
798.176 | 278.9942 | 166.9788 | 171.2433 | 164.308
799.176 | 281.6911 | 167.1088 | 171.4965 | 164.1598
800.176 | 281.7653 | 167.6591 | 171.6599 | 164.1956
801.176 | 279.9611 | 167.904 | 172.0651 | 163.8309
802.176 | 280.8793 | 168.0887 | 172.2471 | 163.9502
803.176 | 280.1945 | 168.0791 | 172.1352 | 163.8428
804.176 | 291.0026 | 167.8634 | 172.1268 | 163.721
805.176 | 288.2245 | 168.0249 | 172.0781 | 163.4967
806.176 | 288.6007 | 168.0467 | 172.1772 | 163.7109
807.176 | 290.1155 | 167.9351 | 172.0209 | 163.7184
808.176 | 296.9772 | 167.6095 | 171.9062 | 164.014
809.176 | 297.9569 | 167.4006 | 171.8681 | 164.0738
810.176 | 297.6464 | 167.5611 | 171.9291 | 164.7159
811.176 | 296.8037 | 167.8959 | 171.6758 | 165.2087
812.176 | 297.0759 | 168.1005 | 171.8165 | 165.4698
813.176 | 301.6123 | 168.4494 | 172.1831 | 165.4761
814.176 | 299.093 | 168.4444 | 172.2404 | 165.4675
815.176 | 298.0629 | 168.9126 | 172.5631 | 165.8282
816.176 | 296.9343 | 168.5383 | 172.6365 | 165.7338
817.176 | 295.1933 | 168.9081 | 172.9329 | 165.751
818.176 | 292.6753 | 168.8304 | 173.1656 | 166.059
819.176 | 291.7421 | 168.9231 | 173.284 | 165.9996
820.176 | 293.0156 | 169.0468 | 173.5974 | 166.201
821.176 | 292.2771 | 169.1116 | 173.8793 | 166.2665
822.176 | 293.3278 | 168.9648 | 174.1857 | 166.322
823.176 | 293.9974 | 168.9084 | 174.3953 | 166.5209
824.176 | 295.3899 | 169.3755 | 174.3924 | 166.7495
825.176 | 295.9602 | 169.2499 | 174.424 | 166.8014
826.176 | 295.0873 | 170.6664 | 174.468 | 167.384
827.176 | 294.7248 | 170.5335 | 174.5256 | 167.2509
828.176 | 295.0225 | 170.7302 | 174.5766 | 167.5339
829.176 | 293.5584 | 170.7173 | 174.9491 | 168.0529
830.176 | 296.2844 | 170.9115 | 175.6001 | 167.8841
831.176 | 296.8405 | 171.7863 | 175.89 | 167.8559
832.176 | 300.495 | 172.6441 | 176.3065 | 168.5298
833.176 | 315.8577 | 173.1444 | 176.3417 | 169.0431
834.176 | 314.0716 | 173.9915 | 176.5012 | 168.9817
835.176 | 315.7991 | 174.3385 | 176.5093 | 169.5834
836.176 | 315.002 | 175.025 | 176.6825 | 169.4694
837.176 | 313.8625 | 174.7484 | 176.915 | 169.9254
838.176 | 313.8015 | 174.5952 | 177.0847 | 170.7266
839.176 | 331.4882 | 174.335 | 177.1117 | 170.794
840.176 | 338.795 | 174.2018 | 177.4036 | 170.6332
841.176 | 337.5711 | 174.1056 | 177.9264 | 170.7948
842.176 | 338.73 | 174.2557 | 178.3509 | 170.8545
843.176 | 337.1154 | 175.0028 | 178.7982 | 171.1422
844.176 | 333.5741 | 174.4492 | 179.0386 | 171.2459
845.176 | 331.0322 | 174.6076 | 178.9914 | 171.5604
846.176 | 326.3064 | 175.1696 | 179.0693 | 171.6042
847.176 | 326.8376 | 175.4758 | 179.0762 | 172.2321
848.176 | 326.7711 | 175.759 | 179.2786 | 171.9679
849.176 | 324.6374 | 176.0246 | 179.3656 | 172.3613
850.176 | 324.5352 | 175.2233 | 179.3084 | 172.1443
851.176 | 327.5093 | 174.8317 | 179.2221 | 172.3049
852.176 | 327.7788 | 174.6689 | 179.121 | 172.9723
853.176 | 328.3375 | 174.332 | 179.9277 | 172.8027
854.176 | 324.6051 | 174.592 | 179.7297 | 172.513
855.176 | 325.3001 | 174.8707 | 179.5836 | 172.2348
856.176 | 324.2615 | 175.2919 | 179.4126 | 172.6105
857.176 | 320.4439 | 175.05 | 179.5165 | 172.91
858.176 | 319.241 | 175.2754 | 179.5607 | 172.7273
859.176 | 319.1553 | 175.2333 | 179.4649 | 172.3862
860.176 | 318.2383 | 175.1364 | 179.4242 | 172.2875
861.176 | 316.5945 | 175.3663 | 179.0981 | 171.9217
862.176 | 317.309 | 175.1759 | 178.995 | 171.9097
863.176 | 315.8979 | 175.1079 | 178.8208 | 171.9813
864.176 | 318.0176 | 174.9432 | 178.9264 | 171.7224
865.176 | 314.1307 | 175.0064 | 179.0485 | 171.7887
866.176 | 312.2237 | 175.1743 | 179.3911 | 172.3121
867.176 | 313.4308 | 174.7248 | 179.385 | 172.2452
868.176 | 310.9181 | 174.7567 | 179.3359 | 172.0691
869.176 | 310.2669 | 174.5459 | 179.3588 | 172.1931
870.176 | 321.3947 | 174.5945 | 179.6125 | 172.0813
871.176 | 328.8581 | 174.3162 | 179.7468 | 172.2298
872.176 | 335.222 | 174.4856 | 179.9581 | 172.084
873.176 | 335.6205 | 174.5312 | 180.1287 | 171.9677
874.176 | 333.9058 | 174.3337 | 180.2038 | 172.1097
875.176 | 332.1583 | 174.4377 | 180.3238 | 171.9921
876.176 | 331.4405 | 174.4037 | 180.2552 | 171.7082
877.176 | 340.9681 | 174.8145 | 180.4232 | 171.9457
878.176 | 358.7184 | 174.8455 | 180.5777 | 172.001
879.176 | 357.0236 | 174.7366 | 180.6566 | 171.7347
880.176 | 378.2223 | 175.2191 | 180.5817 | 171.7973
881.176 | 404.0492 | 175.3204 | 180.5299 | 173.258
882.176 | 397.0972 | 175.1985 | 180.6427 | 173.6348
883.176 | 397.9135 | 175.2883 | 180.4863 | 173.6456
884.176 | 390.8807 | 175.7517 | 180.9366 | 174.1943
885.176 | 385.5566 | 175.5583 | 180.9203 | 174.0697
886.176 | 382.5598 | 175.4564 | 180.9096 | 174.5313
887.176 | 377.5299 | 175.2791 | 181.0269 | 174.3545
888.176 | 373.597 | 175.2515 | 180.8248 | 173.989
889.176 | 369.2846 | 174.822 | 180.6571 | 173.9705
890.176 | 366.0399 | 174.7949 | 180.6063 | 173.742
891.176 | 360.9454 | 175.068 | 181.0328 | 174.4995
892.176 | 357.7613 | 174.87 | 181.3396 | 174.3491
893.176 | 356.9121 | 175.3614 | 181.6344 | 174.1328
894.176 | 373.4078 | 175.2907 | 181.9674 | 173.9626
895.176 | 398.0729 | 175.4586 | 182.1166 | 174.0285
896.176 | 391.5936 | 175.3282 | 182.2966 | 173.8206
897.176 | 387.2933 | 175.9971 | 182.2867 | 173.5457
898.176 | 378.6103 | 176.4258 | 182.1877 | 173.3909
899.176 | 371.5306 | 175.9546 | 182.0005 | 173.8094
900.176 | 365.7232 | 175.8895 | 181.9532 | 174.1123
901.176 | 363.1544 | 176.1736 | 182.0139 | 173.9798
902.176 | 359.0868 | 176.2605 | 182.2438 | 174.0546
903.176 | 359.3156 | 175.9112 | 182.804 | 174.5654
904.176 | 353.9544 | 175.5526 | 182.953 | 175.2516
905.176 | 350.9853 | 175.762 | 183.0919 | 175.626
906.176 | 346.362 | 175.5535 | 182.9128 | 175.8883
907.176 | 343.9774 | 175.4598 | 182.7029 | 175.7937
908.176 | 341.6469 | 175.5382 | 182.7253 | 175.7989
909.176 | 339.2048 | 175.9253 | 182.4931 | 175.8659
910.176 | 337.8255 | 175.7512 | 182.6489 | 175.8032
911.176 | 335.581 | 175.8811 | 182.7464 | 175.7251
912.176 | 335.5164 | 176.3326 | 182.7221 | 176.2524
913.176 | 334.5879 | 176.7505 | 182.6849 | 176.2381
914.176 | 334.9116 | 176.7237 | 182.5719 | 176.2907
915.176 | 350.134 | 176.6981 | 182.6124 | 176.5233
916.176 | 346.2533 | 176.8768 | 183.1961 | 176.5531
917.176 | 357.2419 | 176.9167 | 183.5434 | 176.7792
918.176 | 375.8783 | 176.8837 | 183.6469 | 176.9665
919.176 | 382.5152 | 177.4394 | 184.0031 | 177.1212
920.176 | 399.4424 | 177.9657 | 184.4003 | 177.2122
921.176 | 419.2622 | 177.9977 | 184.6628 | 177.6153
922.176 | 428.2665 | 179.1824 | 184.7303 | 177.8615
923.176 | 437.9577 | 179.9148 | 184.9982 | 178.2222
924.176 | 435.3609 | 179.7352 | 185.1744 | 177.9147
925.176 | 435.1673 | 180.3308 | 185.0097 | 178.1264
926.176 | 443.7116 | 180.7595 | 184.8968 | 178.4446
927.176 | 442.0158 | 180.2872 | 184.8608 | 178.303
928.176 | 455.246 | 179.9663 | 184.8149 | 178.1625
929.176 | 478.2569 | 181.2732 | 184.8457 | 178.0279
930.176 | 462.7465 | 180.3379 | 184.8262 | 178.1531
931.176 | 456.8328 | 180.4594 | 184.8906 | 178.023
932.176 | 448.0476 | 180.0129 | 185.165 | 178.1597
933.176 | 445.7201 | 180.2237 | 185.3162 | 178.2058
934.176 | 451.7837 | 180.8973 | 185.8735 | 177.7959
935.176 | 468.7457 | 181.2687 | 185.969 | 178.3095
936.176 | 495.1582 | 180.727 | 185.9604 | 178.3411
937.176 | 518.5931 | 181.2829 | 186.1775 | 178.4037
938.176 | 537.3453 | 181.3038 | 186.4475 | 178.8781
939.176 | 542.7801 | 181.123 | 186.5013 | 178.9958
940.176 | 549.2046 | 180.9544 | 186.7255 | 179.2184
941.176 | 548.7039 | 180.954 | 186.8659 | 179.2815
942.176 | 532.7144 | 181.1308 | 187.0024 | 179.3776
943.176 | 523.4486 | 181.1356 | 187.248 | 179.8407
944.176 | 512.2714 | 181.3931 | 187.4292 | 180.3468
945.176 | 502 | 182.5329 | 187.4942 | 180.2053
946.176 | 489.0372 | 182.7122 | 187.3797 | 179.8805
947.176 | 484.4985 | 182.6327 | 187.5298 | 179.7782
948.176 | 489.7995 | 182.4054 | 187.5598 | 179.7167
949.176 | 494.2476 | 182.6479 | 187.6162 | 179.6048
950.176 | 518.7165 | 182.9369 | 187.8221 | 180.0803
951.176 | 534.9965 | 182.7282 | 187.9883 | 179.9894
952.176 | 525.1842 | 182.8608 | 188.1219 | 180.2168
953.176 | 522.3724 | 182.7811 | 188.3025 | 180.3608
954.176 | 512.3835 | 182.4858 | 188.1372 | 180.0804
955.176 | 505.366 | 183.3037 | 188.1032 | 180.039
956.176 | 501.3473 | 183.0812 | 188.0568 | 179.9362
957.176 | 487.9709 | 183.0528 | 187.9883 | 180.568
958.176 | 480.5015 | 182.6593 | 187.5672 | 180.7266
959.176 | 482.7203 | 182.844 | 187.1665 | 180.2657
960.176 | 473.5844 | 182.5349 | 186.8361 | 180.315
961.176 | 478.4207 | 182.3617 | 186.4655 | 179.9391
962.176 | 485.3836 | 182.4358 | 186.322 | 179.7645
963.176 | 501.7514 | 182.6712 | 186.382 | 179.8221
964.176 | 513.2772 | 182.8604 | 186.2564 | 179.8865
965.176 | 530.7187 | 183.1127 | 186.161 | 180.0212
966.176 | 539.8841 | 183.0319 | 186.1928 | 180.0731
967.176 | 539.1615 | 183.1404 | 186.2104 | 180.3764
968.176 | 537.5175 | 184.0419 | 186.3456 | 180.6649
969.176 | 526.9025 | 183.8164 | 186.06 | 180.6303
970.176 | 546.5093 | 183.8258 | 185.9214 | 180.5604
971.176 | 535.5806 | 183.6434 | 185.8195 | 180.4241
972.176 | 524.7639 | 183.888 | 185.5565 | 180.5499
973.176 | 513.1374 | 183.8213 | 185.3367 | 180.0449
974.176 | 535.9858 | 184.2592 | 185.5878 | 179.9165
975.176 | 556.5954 | 183.8224 | 185.4527 | 179.9854
976.176 | 561.9221 | 183.7509 | 185.4088 | 180.2309
977.176 | 584.882 | 183.8852 | 185.3436 | 179.9141
978.176 | 576.4172 | 183.7062 | 185.3183 | 179.8305
979.176 | 570.0001 | 183.5934 | 185.2442 | 179.9206
980.176 | 555.9503 | 183.2319 | 185.152 | 180.4192
981.176 | 543.4826 | 183.39 | 185.1026 | 180.6278
982.176 | 543.5168 | 183.9512 | 185.2829 | 181.3338
983.176 | 534.7777 | 183.9249 | 185.5084 | 181.7023
984.176 | 528.2109 | 183.9583 | 185.778 | 182.5087
985.176 | 535.8865 | 183.9621 | 185.9119 | 182.5345
986.176 | 523.53 | 183.7862 | 186.13 | 182.4444
987.176 | 530.2208 | 184.194 | 186.2755 | 182.5303
988.176 | 532.3907 | 184.035 | 186.4402 | 182.382
989.176 | 535.1802 | 183.838 | 186.7097 | 182.3427
990.176 | 555.843 | 183.5183 | 187.0384 | 182.5371
991.176 | 541.112 | 183.3768 | 187.2353 | 182.418
992.176 | 537.456 | 183.4753 | 188.0411 | 182.496
993.176 | 535.0589 | 184.0437 | 188.4578 | 182.5194
994.176 | 548.8992 | 184.3061 | 188.6593 | 182.4892
995.176 | 568.3097 | 184.3596 | 188.7326 | 182.6673
996.176 | 564.6162 | 184.6395 | 188.7663 | 183.5029
997.176 | 562.0483 | 184.7095 | 188.8267 | 185.3942
998.176 | 551.2777 | 185.3293 | 188.7079 | 185.2348
999.176 | 551.6039 | 185.9682 | 188.8955 | 185.881
1000.176 | 565.6723 | 185.5721 | 189.1652 | 186.2996
1001.176 | 572.5467 | 185.5689 | 189.0682 | 186.1935
1002.176 | 589.9196 | 186.0267 | 188.969 | 186.4018
1003.176 | 574.4508 | 185.7296 | 188.8041 | 186.9215
1004.176 | 574.1518 | 185.8803 | 188.8897 | 186.9754
1005.176 | 569.0689 | 186.4417 | 189.0678 | 186.8126
1006.176 | 571.6308 | 186.452 | 189.1833 | 186.8969
1007.176 | 566.6745 | 186.7338 | 189.3248 | 186.8835
1008.176 | 563.137 | 186.9511 | 189.4006 | 186.6879
1009.176 | 578.4577 | 186.9719 | 189.341 | 187.0024
1010.176 | 568.0853 | 187.2555 | 189.6925 | 186.93
1011.176 | 565.5672 | 187.5217 | 189.6404 | 186.6258
1012.176 | 563.6667 | 187.1694 | 189.5688 | 186.3235
1013.176 | 551.4355 | 187.2431 | 189.5914 | 186.1626
1014.176 | 544.6465 | 186.983 | 189.4846 | 186.1103
1015.176 | 537.7632 | 186.6954 | 189.402 | 186.1953
1016.176 | 550.704 | 186.7965 | 189.2491 | 186.1646
1017.176 | 560.3245 | 186.9763 | 189.1124 | 186.0126
1018.176 | 583.1111 | 186.7029 | 188.9002 | 186.0087
1019.176 | 594.0034 | 186.8613 | 188.8605 | 185.8437
1020.176 | 602.2729 | 186.707 | 189.1844 | 185.7394
1021.176 | 613.0569 | 187.1591 | 189.4609 | 185.6416
1022.176 | 613.3662 | 187.3585 | 189.6493 | 186.3308
1023.176 | 636.3173 | 187.7762 | 189.8663 | 186.5345
1024.176 | 628.1849 | 187.9137 | 190.044 | 186.5942
1025.176 | 622.7385 | 187.994 | 190.0378 | 186.4365
1026.176 | 615.6026 | 188.3696 | 190.2255 | 186.483
1027.176 | 607.0089 | 188.3144 | 190.3822 | 186.305
1028.176 | 596.9384 | 188.6957 | 190.6511 | 185.9498
1029.176 | 612.053 | 188.7822 | 190.97 | 185.8843
1030.176 | 608.0907 | 188.6054 | 191.1318 | 186.0814
1031.176 | 612.9777 | 188.8878 | 191.351 | 186.8816
1032.176 | 611.677 | 189.001 | 191.3704 | 187.1942
1033.176 | 631.3281 | 188.8369 | 191.5606 | 187.6982
1034.176 | 638.8735 | 188.4931 | 191.4782 | 188.0307
1035.176 | 624.8328 | 188.6875 | 191.7804 | 187.8596
1036.176 | 623.3714 | 188.7846 | 191.7584 | 187.9823
1037.176 | 616.043 | 188.7469 | 191.8775 | 187.9654
1038.176 | 610.8168 | 189.0292 | 191.9944 | 188.0594
1039.176 | 594.9634 | 189.7025 | 192.0639 | 187.7534
1040.176 | 613.8119 | 189.2797 | 192.5304 | 187.7275
1041.176 | 608.9136 | 189.3846 | 193.0321 | 187.5851
1042.176 | 602.7266 | 189.1458 | 193.3177 | 187.6167
1043.176 | 599.669 | 189.1751 | 193.5911 | 187.5376
1044.176 | 594.8407 | 189.5476 | 193.5908 | 187.8236
1045.176 | 595.8228 | 189.6631 | 193.6155 | 187.9898
1046.176 | 597.8087 | 189.5011 | 193.6523 | 187.9688
1047.176 | 589.3007 | 189.5482 | 193.753 | 187.5931
1048.176 | 606.0739 | 189.473 | 193.9252 | 187.4606
1049.176 | 604.7413 | 189.9285 | 194.0883 | 187.3125
1050.176 | 594.4195 | 190.1602 | 193.8287 | 187.7272
1051.176 | 592.6513 | 190.3335 | 193.4326 | 187.9999
1052.176 | 581.9035 | 190.2751 | 193.2716 | 187.9773
1053.176 | 586.8519 | 190.6358 | 193.1104 | 187.6585
1054.176 | 571.1653 | 190.7723 | 193.2848 | 187.4765
1055.176 | 574.2184 | 191.0165 | 193.9238 | 187.4332
1056.176 | 569.3973 | 191.3355 | 194.206 | 187.3176
1057.176 | 575.249 | 191.9195 | 194.6949 | 187.607
1058.176 | 569.0622 | 192.5786 | 194.7639 | 187.7637
1059.176 | 570.6842 | 192.6513 | 194.7854 | 187.6202
1060.176 | 582.9943 | 192.4652 | 194.7501 | 187.5069
1061.176 | 584.2474 | 192.4593 | 194.809 | 187.4009
1062.176 | 595.6895 | 192.5065 | 194.8055 | 187.546
1063.176 | 601.4226 | 192.0041 | 194.7182 | 187.4771
1064.176 | 602.6316 | 191.6372 | 194.6083 | 187.4032
1065.176 | 616.5371 | 191.1965 | 194.3075 | 188.1895
1066.176 | 614.8186 | 191.1523 | 194.2092 | 188.0802
1067.176 | 633.778 | 191.3335 | 194.0864 | 188.2777
1068.176 | 620.2299 | 191.3533 | 194.0045 | 187.9451
1069.176 | 602.5866 | 190.9744 | 193.9156 | 187.9454
1070.176 | 609.6107 | 190.5783 | 193.8724 | 188.0149
1071.1917 | 606.7282 | 190.2857 | 193.7954 | 187.981
1072.176 | 593.6877 | 190.561 | 193.769 | 188.0117
1073.176 | 599.3681 | 190.868 | 193.6451 | 187.6258
1074.176 | 608.291 | 190.8824 | 193.5095 | 187.8372
1075.176 | 613.8956 | 190.6507 | 193.399 | 187.6519
1076.176 | 602.8776 | 190.0487 | 193.2733 | 187.6961
1077.176 | 609.2392 | 189.9078 | 193.1498 | 187.9564
1078.176 | 626.7133 | 189.8124 | 193.1134 | 188.051
1079.176 | 631.2364 | 189.4413 | 193.0157 | 187.9942
1080.176 | 632.5094 | 189.5397 | 192.7536 | 188.4018
1081.176 | 640.4515 | 189.4505 | 192.5488 | 188.1061
1082.176 | 642.2065 | 189.0777 | 192.2512 | 188.1213
1083.176 | 652.3172 | 188.7667 | 191.9412 | 187.9756
1084.176 | 649.7289 | 188.6826 | 191.8342 | 187.9526
1085.176 | 634.8742 | 188.6435 | 191.8464 | 187.8605
1086.176 | 627.3594 | 188.9294 | 191.9265 | 187.8227
1087.176 | 611.3159 | 188.8082 | 192.0557 | 187.8629
1088.176 | 607.9886 | 188.7041 | 192.1637 | 188.4884
1089.176 | 612.5158 | 189.498 | 192.2169 | 189.0591
1090.176 | 607.5924 | 190.0892 | 192.372 | 189.1045
1091.176 | 618.9925 | 190.1532 | 192.6217 | 188.8592
1092.176 | 627.8637 | 190.4435 | 192.8294 | 188.7686
1093.176 | 645.4225 | 190.5898 | 193.177 | 188.7856
1094.176 | 651.9357 | 190.7343 | 193.4356 | 188.5232
1095.176 | 640.9611 | 190.7953 | 193.6664 | 188.5827
1096.176 | 637.1065 | 190.8821 | 194.0339 | 188.7466
1097.176 | 641.7691 | 190.8249 | 194.2538 | 188.7568
1098.176 | 641.6014 | 190.7417 | 194.7047 | 188.9497
1099.176 | 652.367 | 190.644 | 194.8506 | 188.7904
1100.176 | 662.22 | 190.9716 | 194.7395 | 188.4882
1101.1917 | 665.2093 | 191.6846 | 194.7382 | 188.4812
1102.176 | 669.4627 | 191.5228 | 194.8303 | 188.4224
1103.176 | 675.7148 | 191.4039 | 195.075 | 188.6089
1104.176 | 672.2127 | 193.1173 | 195.4566 | 189.4609
1105.176 | 681.6229 | 192.8591 | 195.6815 | 190.0084
1106.176 | 662.7682 | 192.8168 | 196.0557 | 190.2343
1107.176 | 651.6127 | 193.6676 | 196.1881 | 190.6825
1108.176 | 656.9892 | 194.5217 | 196.5723 | 191.1621
1109.176 | 656.5274 | 194.115 | 196.9883 | 191.7494
1110.176 | 648.5611 | 194.808 | 197.3192 | 192.0915
1111.176 | 653.1215 | 194.7155 | 197.5038 | 192.3283
1112.176 | 652.0842 | 194.6878 | 197.4971 | 192.5629
1113.176 | 652.5089 | 194.6502 | 197.449 | 192.4331
1114.176 | 632.4449 | 194.7044 | 197.3074 | 192.1517
1115.176 | 619.5229 | 194.9513 | 197.4681 | 191.6293
1116.176 | 620.2662 | 195.3541 | 197.2589 | 191.4714
1117.176 | 611.995 | 194.9689 | 197.1125 | 192.1524
1118.176 | 601.1235 | 195.1147 | 196.9162 | 192.8537
1119.176 | 612.7104 | 195.5871 | 196.8746 | 193.5474
1120.176 | 604.7182 | 195.5532 | 196.8615 | 193.8915
1121.176 | 610.3895 | 195.7998 | 196.9143 | 193.8127
1122.176 | 612.339 | 195.8705 | 196.9877 | 193.7088
1123.176 | 603.1526 | 196.0379 | 197.2035 | 193.8846
1124.176 | 611.2578 | 196.0182 | 196.9293 | 193.3084
1125.176 | 606.6089 | 196.025 | 196.8674 | 193.1125
1126.176 | 600.7793 | 195.6781 | 196.8044 | 192.985
1127.176 | 613.7342 | 195.6899 | 196.7793 | 193.3236
1128.176 | 630.0666 | 195.7553 | 196.9309 | 193.2515
1129.176 | 633.2371 | 195.7521 | 196.9289 | 192.9012
1130.176 | 635.2841 | 196.2006 | 197.0237 | 192.6684
1131.176 | 647.0766 | 196.4178 | 197.1433 | 193.3958
1132.176 | 642.3743 | 196.6726 | 197.0928 | 193.4338
1133.176 | 644.4833 | 196.6321 | 196.8421 | 193.2291
1134.176 | 637.1836 | 196.5709 | 196.7626 | 193.1661
1135.176 | 644.9541 | 196.5786 | 196.7311 | 193.2061
1136.176 | 639.1762 | 196.4788 | 196.6952 | 193.2846
1137.176 | 637.8471 | 196.6705 | 196.6474 | 193.3645
1138.176 | 647.2961 | 197.1244 | 196.6295 | 193.3169
1139.176 | 651.4503 | 197.3379 | 196.8791 | 192.8442
1140.176 | 662.7268 | 197.4044 | 197.1672 | 193.4748
1141.176 | 668.9093 | 197.4692 | 197.349 | 193.5406
1142.176 | 680.9947 | 198.0323 | 197.7431 | 194.3716
1143.176 | 672.696 | 198.5212 | 199.1812 | 194.8249
1144.176 | 665.657 | 199.0658 | 199.6409 | 195.0538
1145.176 | 651.8 | 199.055 | 199.7972 | 194.8443
1146.176 | 651.8232 | 199.2794 | 200.0624 | 195.1516
1147.176 | 640.3603 | 199.7878 | 200.1847 | 195.3938
1148.176 | 624.4537 | 199.9873 | 200.4731 | 195.6909
1149.176 | 614.6127 | 199.581 | 200.6209 | 196.2325
1150.176 | 617.3315 | 199.5603 | 200.8469 | 196.1435
1151.176 | 612.5322 | 199.3883 | 200.9466 | 196.9637
1152.176 | 628.8949 | 199.7275 | 201.2498 | 196.8331
1153.176 | 633.6359 | 199.9422 | 201.4966 | 196.9256
1154.176 | 627.9031 | 199.5252 | 201.4899 | 196.9516
1155.176 | 631.9097 | 199.3816 | 201.3814 | 196.8904
1156.176 | 618.1239 | 199.2332 | 201.2881 | 197.0576
1157.176 | 626.9358 | 199.0466 | 201.3218 | 196.947
1158.176 | 632.6465 | 199.1044 | 201.1968 | 196.5553
1159.176 | 631.9244 | 198.7891 | 201.1368 | 196.4466
1160.176 | 613.6494 | 198.4868 | 201.0241 | 196.4634
1161.176 | 623.8884 | 198.3266 | 200.8382 | 195.9464
1162.176 | 621.1942 | 198.4598 | 200.6735 | 196.0446
1163.176 | 607.4915 | 198.2823 | 200.5769 | 195.7778
1164.176 | 605.114 | 198.4992 | 200.6204 | 195.6686
1165.176 | 602.319 | 198.7355 | 200.6966 | 195.8869
1166.176 | 608.5943 | 198.7286 | 200.5911 | 195.6827
1167.176 | 612.6607 | 198.7872 | 200.8564 | 195.445
1168.176 | 626.229 | 198.9656 | 201.0261 | 195.2517
1169.176 | 630.5502 | 199.0114 | 201.2204 | 195.7653
1170.176 | 628.9679 | 199.1885 | 201.6193 | 196.0329
1171.176 | 611.3616 | 199.4802 | 202.3115 | 195.8464
1172.176 | 599.0612 | 199.3686 | 203.0593 | 195.5974
1173.176 | 616.83 | 200.0472 | 203.5473 | 195.9393
1174.176 | 597.9484 | 199.9215 | 203.954 | 196.104
1175.176 | 609.7799 | 199.9705 | 203.961 | 196.3269
1176.176 | 617.5239 | 200.1306 | 204.3916 | 196.8501
1177.176 | 618.153 | 200.0704 | 204.3774 | 196.7428
1178.176 | 628.7123 | 199.8589 | 204.5065 | 196.6994
1179.176 | 635.3515 | 199.8002 | 204.6856 | 196.8317
1180.176 | 618.5491 | 199.633 | 204.7843 | 197.4061
1181.176 | 617.3102 | 199.6843 | 204.696 | 197.1478
1182.176 | 614.3182 | 199.6332 | 204.4399 | 196.8395
1183.176 | 607.5303 | 199.6888 | 204.3033 | 196.7421
1184.176 | 619.7466 | 199.7305 | 204.407 | 196.8352
1185.176 | 625.5436 | 200.3805 | 204.6342 | 197.1806
1186.176 | 635.482 | 200.3885 | 204.9908 | 197.2978
1187.176 | 646.9571 | 200.6528 | 205.1569 | 196.9934
1188.176 | 630.6666 | 200.9291 | 205.2028 | 197.3699
1189.176 | 625.0693 | 200.9809 | 205.3762 | 197.3203
1190.176 | 636.5315 | 200.9837 | 205.4774 | 197.7005
1191.1917 | 632.5043 | 200.6073 | 205.4487 | 198.2569
1192.176 | 628.4869 | 200.3184 | 205.35 | 198.0719
1193.176 | 643.2455 | 200.6877 | 205.0714 | 198.1388
1194.176 | 624.1449 | 200.7292 | 205.0874 | 198.0811
1195.176 | 621.7528 | 200.7373 | 205.0114 | 198.1811
1196.176 | 619.7253 | 200.4313 | 205.026 | 197.8836
1197.176 | 606.6833 | 200.2553 | 204.8845 | 198.3032
1198.176 | 605.1368 | 200.079 | 204.6049 | 198.1971
1199.176 | 608.279 | 200.052 | 204.3824 | 198.3311
1200.176 | 620.8356 | 199.9183 | 204.1937 | 198.0545
1201.176 | 630.6764 | 199.9059 | 204.0994 | 197.7493
1202.176 | 636.1923 | 199.6745 | 204.0304 | 197.4374
1203.176 | 643.5692 | 199.8038 | 203.6647 | 197.2859
1204.176 | 624.6197 | 199.7978 | 203.3641 | 196.9136
1205.176 | 616.4788 | 199.9104 | 203.1566 | 196.773
1206.176 | 611.837 | 200.311 | 202.9382 | 196.7367
1207.176 | 610.4146 | 200.0768 | 202.6669 | 196.9987
1208.176 | 600.8525 | 200.1397 | 202.7632 | 196.77
1209.176 | 581.9261 | 200.0849 | 202.777 | 196.5713
1210.176 | 570.5391 | 200.7627 | 202.687 | 196.2545
1211.176 | 574.7804 | 200.7341 | 202.3965 | 196.2017
1212.176 | 587.911 | 200.9999 | 202.2078 | 196.3704
1213.176 | 572.7245 | 201.1675 | 202.2047 | 196.4172
1214.176 | 552.4719 | 201.4596 | 202.1415 | 196.5164
1215.176 | 534.6785 | 201.4563 | 202.2109 | 196.7166
1216.176 | 520.4252 | 202.2917 | 202.2327 | 196.612
1217.176 | 505.5691 | 202.6011 | 202.1481 | 196.9425
1218.176 | 489.7671 | 202.5514 | 202.0615 | 197.5295
1219.176 | 480.7038 | 202.7634 | 202.2034 | 197.3888
1220.176 | 481.4543 | 203.0234 | 202.1663 | 197.2
1221.176 | 503.881 | 203.2445 | 202.5747 | 197.2484
1222.176 | 505.2652 | 204.018 | 202.3716 | 197.2642
1223.176 | 499.7295 | 204.6031 | 202.2148 | 197.3186
1224.176 | 497.4765 | 205.1171 | 202.4305 | 197.7392
1225.176 | 503.4625 | 205.2226 | 202.3861 | 197.3945
1226.176 | 491.0365 | 205.5301 | 202.2753 | 197.6476
1227.176 | 479.6416 | 205.7157 | 202.1555 | 197.7901
1228.176 | 491.8458 | 205.7532 | 202.0713 | 197.5865
1229.176 | 503.0373 | 205.8865 | 202.1835 | 197.4447
1230.176 | 532.2708 | 205.5712 | 202.3522 | 197.7291
1231.176 | 550.2257 | 205.5408 | 202.4809 | 198.0348
1232.176 | 534.2854 | 205.4693 | 202.5863 | 198.9457
1233.176 | 516.5736 | 205.1309 | 202.8329 | 199.2489
1234.176 | 502.1486 | 205.5448 | 203.3606 | 199.21
1235.176 | 488.0059 | 205.4311 | 203.4692 | 198.9271
1236.176 | 478.1522 | 204.8244 | 203.6302 | 198.8857
1237.176 | 470.4278 | 204.5102 | 203.7696 | 198.6832
1238.176 | 459.1492 | 204.7938 | 203.7097 | 198.556
1239.176 | 449.4575 | 204.6875 | 203.8748 | 198.69
1240.176 | 445.5889 | 204.4467 | 203.8426 | 198.7241
1241.176 | 440.1441 | 204.3065 | 203.7002 | 198.6698
1242.176 | 434.1594 | 203.9947 | 203.6354 | 198.4938
1243.176 | 430.607 | 204.1425 | 203.5178 | 198.1964
1244.176 | 423.932 | 204.2879 | 203.3107 | 198.1006
1245.176 | 416.7095 | 204.4581 | 203.276 | 198.2066
1246.176 | 411.5066 | 204.6404 | 203.1943 | 198.597
1247.176 | 410.8823 | 204.7585 | 203.2588 | 198.808
1248.176 | 433.5904 | 204.8662 | 203.3859 | 199.1981
1249.176 | 432.8993 | 204.5994 | 203.4521 | 199.1997
1250.176 | 429.3841 | 205.0134 | 203.6994 | 199.083
1251.176 | 445.9059 | 205.2349 | 203.9191 | 199.5732
1252.176 | 457.3036 | 205.6787 | 204.1131 | 199.9394
1253.176 | 472.796 | 205.7886 | 203.9202 | 199.6542
1254.176 | 490.7862 | 205.982 | 204.0086 | 200.1761
1255.176 | 495.2904 | 206.0397 | 203.9384 | 199.792
1256.176 | 491.6399 | 206.1648 | 204.0305 | 199.8922
1257.176 | 476.9189 | 206.3415 | 203.7635 | 199.7172
1258.176 | 463.6925 | 206.1088 | 203.7986 | 199.6155
1259.176 | 453.566 | 206.2097 | 203.7502 | 199.3627
1260.176 | 444.4761 | 206.2608 | 203.7753 | 199.6685
1261.176 | 440.3858 | 206.0001 | 203.7959 | 200.1024
1262.176 | 432.1665 | 205.6708 | 203.9999 | 199.9066
1263.176 | 427.3239 | 205.326 | 204.3077 | 199.9492
1264.176 | 422.9458 | 205.1089 | 204.4882 | 200.0411
1265.176 | 418.3101 | 204.8397 | 204.486 | 199.9252
1266.176 | 417.0741 | 204.9528 | 204.6215 | 200.0815
1267.176 | 415.9502 | 204.8386 | 204.8605 | 200.0252
1268.176 | 424.6876 | 205.6344 | 204.8756 | 200.1656
1269.176 | 432.5007 | 205.4918 | 205.0546 | 200.2767
1270.176 | 427.9583 | 205.4991 | 205.0817 | 200.3865
1271.176 | 427.2339 | 205.3989 | 205.376 | 200.5954
1272.176 | 426.6522 | 205.1951 | 205.3016 | 201.1082
1273.176 | 424.9004 | 205.1091 | 205.2184 | 200.9491
1274.176 | 447.5522 | 204.9744 | 205.2459 | 201.4908
1275.176 | 439.2237 | 204.9526 | 205.3993 | 201.5732
1276.176 | 433.6279 | 204.9737 | 205.2881 | 201.2871
1277.176 | 428.4237 | 205.1572 | 205.9939 | 200.9451
1278.176 | 421.0844 | 204.9949 | 205.93 | 200.64
1279.176 | 420.1791 | 204.8222 | 205.8176 | 200.61
1280.176 | 418.5816 | 205.097 | 205.6591 | 200.4274
1281.176 | 414.14 | 205.333 | 205.6312 | 200.3341
1282.176 | 413.8051 | 205.4783 | 205.4052 | 200.2676
1283.176 | 410.2385 | 205.5715 | 205.376 | 200.1971
1284.176 | 409.9945 | 205.5033 | 205.2668 | 200.6182
1285.176 | 407.571 | 205.6218 | 205.3699 | 200.0639
1286.176 | 403.1723 | 205.6556 | 205.3776 | 199.8454
1287.176 | 396.4853 | 205.6027 | 205.2898 | 200.8248
1288.176 | 393.9341 | 205.6072 | 205.3748 | 200.5926
1289.176 | 402.0469 | 205.3172 | 205.3934 | 200.1774
1290.176 | 422.5457 | 205.2349 | 205.3152 | 199.8872
1291.176 | 440.5146 | 205.0829 | 205.3368 | 200.1174
1292.176 | 457.6262 | 204.9471 | 205.2894 | 200.1927
1293.176 | 446.4807 | 204.9746 | 205.1833 | 200.3404
1294.176 | 470.7911 | 204.983 | 205.0295 | 200.603
1295.176 | 478.3494 | 204.8521 | 204.8147 | 200.6193
1296.176 | 488.861 | 204.8833 | 204.6146 | 201.2095
1297.176 | 506.0498 | 204.8216 | 204.4705 | 201.3188
1298.176 | 543.2959 | 204.9927 | 204.6624 | 201.1612
1299.176 | 553.263 | 204.9925 | 204.6 | 201.192
1300.176 | 546.0087 | 204.6333 | 204.5395 | 201.7108
1301.176 | 531.2749 | 204.4755 | 204.3617 | 201.8622
1302.176 | 512.0015 | 204.548 | 204.3425 | 201.4777
1303.176 | 495.6509 | 204.3676 | 204.2928 | 201.4062
1304.176 | 483.3709 | 204.5423 | 204.2422 | 201.6405
1305.176 | 483.8799 | 204.513 | 203.9878 | 201.7168
1306.176 | 476.1427 | 204.8275 | 203.7305 | 201.905
1307.176 | 468.5677 | 204.9048 | 203.4916 | 201.8927
1308.176 | 460.8424 | 204.895 | 203.5748 | 201.5842
1309.176 | 453.4671 | 205.0841 | 203.6708 | 201.7215
1310.176 | 445.086 | 204.9266 | 203.6002 | 201.723
1311.176 | 439.7065 | 204.5446 | 203.5605 | 201.6974
1312.176 | 442.4226 | 204.4969 | 203.7072 | 201.9601
1313.176 | 438.1804 | 204.7897 | 203.7756 | 202.318
1314.176 | 430.671 | 204.807 | 203.705 | 202.4459
1315.176 | 425.1747 | 204.9295 | 203.9376 | 202.6906
1316.176 | 422.1593 | 204.9647 | 204.0683 | 203.0874
1317.176 | 421.1879 | 204.8144 | 204.4319 | 203.1146
1318.176 | 421.6915 | 204.9664 | 204.3802 | 202.7246
1319.176 | 418.59 | 205.0465 | 204.5837 | 202.3235
1320.176 | 416.5723 | 205.5938 | 204.5113 | 202.1949
1321.176 | 414.7172 | 206.4028 | 204.3698 | 202.9094
1322.176 | 410.6534 | 206.8492 | 204.1945 | 203.6066
1323.176 | 405.1825 | 206.4449 | 204.3374 | 203.4507
1324.176 | 401.1465 | 206.3962 | 204.4237 | 203.4863
1325.176 | 397.9295 | 206.8527 | 204.4511 | 203.745
1326.176 | 393.9615 | 206.9667 | 204.5195 | 204.0795
1327.176 | 388.3571 | 206.9594 | 204.5608 | 204.0989
1328.176 | 383.4559 | 206.925 | 204.6273 | 204.0773
1329.176 | 382.3431 | 206.9048 | 204.5815 | 204.4375
1330.176 | 379.3051 | 207.0872 | 204.4809 | 204.8657
1331.176 | 379.0598 | 207.1121 | 204.5275 | 205.1337
1332.176 | 377.5827 | 207.0831 | 204.2357 | 204.8342
1333.176 | 375.9298 | 207.0987 | 204.1806 | 204.9442
1334.176 | 369.3824 | 206.7143 | 203.9713 | 205.0177
1335.176 | 364.4768 | 206.8086 | 203.9075 | 204.9429
1336.176 | 358.9002 | 206.9743 | 203.7939 | 204.927
1337.176 | 356.33 | 207.3597 | 203.7265 | 205.0355
1338.176 | 353.3114 | 207.5257 | 203.5289 | 205.3201
1339.176 | 349.7535 | 207.6714 | 203.4855 | 205.1621
1340.176 | 347.9488 | 207.8276 | 203.4301 | 205.0872
1341.176 | 347.227 | 208.1053 | 203.7247 | 204.8175
1342.176 | 351.0509 | 208.6804 | 203.9103 | 204.619
1343.176 | 348.7167 | 208.8844 | 204.272 | 204.4597
1344.176 | 346.5127 | 208.9248 | 204.5597 | 204.6684
1345.176 | 346.6786 | 208.9099 | 204.47 | 205.0885
1346.176 | 346.953 | 209.0229 | 204.7396 | 205.3844
1347.176 | 347.6106 | 209.5057 | 204.7601 | 205.6015
1348.176 | 347.9499 | 209.4976 | 204.7467 | 205.788
1349.176 | 347.9902 | 209.4419 | 204.9775 | 205.5435
1350.176 | 344.1883 | 209.718 | 205.071 | 205.3232
1351.176 | 343.7558 | 210.0137 | 205.1421 | 205.2913
1352.176 | 345.3114 | 210.4355 | 205.063 | 205.514
1353.176 | 358.2184 | 210.5849 | 205.2962 | 205.468
1354.176 | 358.8108 | 210.9061 | 205.5904 | 205.2208
1355.176 | 356.3947 | 210.7498 | 205.6454 | 205.4483
1356.176 | 356.5407 | 211.0902 | 205.7757 | 205.9539
1357.176 | 353.7519 | 210.8784 | 206.0037 | 205.5273
1358.176 | 353.0519 | 210.9077 | 206.1816 | 205.772
1359.176 | 356.0807 | 210.7276 | 206.0728 | 205.3784
1360.176 | 372.384 | 210.8318 | 206.1473 | 205.1795
1361.176 | 374.3394 | 210.7277 | 206.065 | 204.7592
1362.176 | 374.5317 | 210.5936 | 206.1968 | 204.2305
1363.176 | 373.8712 | 210.1476 | 206.1406 | 203.8242
1364.176 | 398.2802 | 209.711 | 206.1097 | 203.9151
1365.176 | 415.8781 | 209.4415 | 206.3469 | 203.6422
1366.176 | 413.4698 | 209.3109 | 206.6427 | 203.3045
1367.176 | 442.651 | 209.2447 | 206.707 | 203.6563
1368.176 | 446.3614 | 209.0082 | 206.7995 | 203.2831
1369.176 | 464.2499 | 208.7836 | 207.0859 | 203.1242
1370.176 | 456.7611 | 208.7126 | 207.5558 | 203.4585
1371.176 | 446.2689 | 208.4616 | 207.4826 | 203.8088
1372.176 | 441.3869 | 208.3526 | 207.4992 | 203.3747
1373.176 | 433.5528 | 208.3902 | 207.5248 | 203.2425
1374.176 | 426.3765 | 208.3619 | 207.4833 | 202.806
1375.176 | 422.8749 | 208.1875 | 207.5458 | 202.8786
1376.176 | 416.6961 | 208.4286 | 207.8566 | 203.3545
1377.176 | 411.6622 | 208.6137 | 208.177 | 203.0937
1378.176 | 411.8291 | 208.6586 | 208.8003 | 203.009
1379.176 | 409.2875 | 208.6152 | 209.2309 | 203.0694
1380.176 | 405.9953 | 208.6789 | 209.5927 | 203.2479
1381.176 | 402.8371 | 208.4053 | 209.9148 | 203.0869
1382.176 | 420.744 | 208.5004 | 210.1403 | 203.0451
1383.176 | 432.2797 | 208.5531 | 210.2567 | 203.1231
1384.176 | 436.9804 | 208.3014 | 210.3487 | 203.3297
1385.176 | 432.0905 | 208.6168 | 210.2412 | 203.4696
1386.176 | 430.1328 | 208.6534 | 210.2068 | 203.7248
1387.176 | 425.5276 | 208.7836 | 210.2565 | 204.0363
1388.176 | 425.5483 | 208.7019 | 210.2551 | 203.9603
1389.176 | 423.6261 | 208.1373 | 210.2752 | 203.7642
1390.176 | 439.2473 | 207.9568 | 210.2219 | 203.9475
1391.176 | 459.6969 | 208.0806 | 210.2414 | 203.8703
1392.176 | 461.4206 | 208.0931 | 210.5518 | 204.6667
1393.176 | 465.8394 | 208.363 | 210.7607 | 204.2525
1394.176 | 459.5791 | 208.049 | 211.3118 | 204.9228
1395.176 | 450.3595 | 208.5028 | 211.8472 | 205.5123
1396.176 | 441.1436 | 208.3474 | 212.2265 | 205.3903
1397.176 | 435.8517 | 208.7756 | 212.5604 | 205.3639
1398.176 | 433.2701 | 208.305 | 212.829 | 205.2128
1399.176 | 439.4408 | 208.4851 | 213.0551 | 205.0672
1400.176 | 438.0932 | 208.6918 | 213.2665 | 205.5064
1401.176 | 432.3306 | 208.8044 | 213.6676 | 205.4302
1402.176 | 427.671 | 208.9999 | 213.8771 | 205.2444
1403.176 | 422.9695 | 209.2628 | 214.1142 | 205.0757
1404.176 | 420.843 | 209.2911 | 214.2601 | 205.1343
1405.176 | 434.7223 | 209.4878 | 214.1531 | 205.3012
1406.176 | 439.9227 | 209.2541 | 214.2771 | 205.4237
1407.176 | 439.9261 | 209.2844 | 214.0552 | 206.1132
1408.176 | 434.6951 | 209.1666 | 214.2054 | 206.2752
1409.176 | 444.7459 | 208.9975 | 214.1323 | 206.2353
1410.176 | 442.3053 | 209.0737 | 214.0603 | 206.0268
1411.176 | 464.3118 | 209.1629 | 214.1114 | 205.7178
1412.176 | 457.1762 | 208.8332 | 214.1285 | 206.1821
1413.176 | 469.5432 | 208.7611 | 213.9643 | 206.3834
1414.176 | 465.5561 | 208.5545 | 213.7949 | 206.4036
1415.176 | 494.9122 | 208.8295 | 213.6658 | 206.8482
1416.176 | 503.4507 | 208.948 | 213.7135 | 207.2581
1417.176 | 528.2432 | 209.1826 | 213.6814 | 206.8155
1418.176 | 541.3959 | 209.5619 | 214.0969 | 206.4865
1419.176 | 525.6961 | 209.7664 | 214.0723 | 206.7666
1420.176 | 512.3457 | 209.8422 | 214.1353 | 207.0974
1421.176 | 500.2102 | 209.9683 | 214.2442 | 206.7185
1422.176 | 500.871 | 209.8906 | 214.1857 | 206.9147
1423.176 | 508.2826 | 209.6631 | 214.1416 | 206.7193
1424.176 | 508.0322 | 209.6502 | 214.5242 | 206.7662
1425.176 | 520.8635 | 209.5117 | 214.725 | 206.851
1426.176 | 510.6172 | 209.717 | 214.8001 | 206.7269
1427.176 | 498.4191 | 209.7406 | 214.918 | 206.3768
1428.176 | 488.7159 | 209.6028 | 214.9065 | 206.7261
1429.176 | 477.3508 | 209.3177 | 214.9932 | 207.2361
1430.176 | 469.5222 | 209.4116 | 215.2124 | 207.3346
1431.176 | 458.6015 | 209.1365 | 215.1352 | 206.9109
1432.176 | 452.0662 | 208.9977 | 215.2019 | 206.5325
1433.176 | 444.8507 | 208.7784 | 214.9844 | 206.2578
1434.176 | 437.1043 | 208.7177 | 214.7429 | 206.2341
1435.176 | 431.0208 | 208.4528 | 214.3773 | 206.1392
1436.176 | 424.0823 | 208.4884 | 214.0349 | 206.084
1437.176 | 422.4693 | 208.3024 | 213.9419 | 206.2962
1438.176 | 417.5417 | 208.4157 | 213.8127 | 206.0031
1439.176 | 412.096 | 208.3215 | 213.7203 | 205.9222
1440.176 | 407.3409 | 208.4186 | 213.6094 | 205.5665
1441.176 | 402.3491 | 208.5531 | 213.5237 | 205.5438
1442.1917 | 396.6549 | 208.5718 | 213.4557 | 205.4078
1443.176 | 393.6948 | 208.5661 | 213.282 | 205.3832
1444.176 | 390.4581 | 208.6308 | 213.1792 | 205.2835
1445.176 | 393.2275 | 208.6786 | 212.9757 | 205.1025
1446.176 | 394.7926 | 208.6802 | 212.8382 | 205.2475
1447.176 | 394.8521 | 208.8694 | 212.4694 | 205.3506
1448.176 | 395.3324 | 208.9233 | 212.2519 | 205.071
1449.176 | 396.327 | 208.916 | 212.2588 | 205.2995
1450.176 | 397.5896 | 208.7432 | 212.3393 | 205.0516
1451.176 | 400.2781 | 208.7246 | 212.7009 | 205.4647
1452.176 | 412.894 | 208.6247 | 212.9173 | 205.9705
1453.176 | 422.6006 | 208.5443 | 213.1137 | 206.0225
1454.176 | 417.8229 | 208.5737 | 213.2235 | 206.1282
1455.176 | 413.3806 | 208.6653 | 213.2462 | 205.8982
1456.176 | 409.6513 | 208.4487 | 213.294 | 205.8515
1457.176 | 411.4059 | 208.3694 | 213.2034 | 206.1167
1458.176 | 407.2953 | 208.4512 | 213.1736 | 205.9434
1459.176 | 405.8308 | 208.3943 | 212.9817 | 205.3534
1460.176 | 412.026 | 208.1519 | 212.8723 | 205.0389
1461.176 | 412.2646 | 208.5387 | 212.7529 | 204.8892
1462.176 | 420.3912 | 208.7134 | 212.8138 | 204.9076
1463.176 | 427.008 | 208.5968 | 212.7327 | 205.0808
1464.176 | 421.4861 | 208.6555 | 212.7262 | 205.2001
1465.176 | 416.1799 | 209.1913 | 212.7724 | 205.1225
1466.176 | 412.1791 | 209.5841 | 212.8359 | 205.3471
1467.176 | 407.5239 | 209.7784 | 212.9435 | 205.3616
1468.176 | 406.9496 | 209.8002 | 213.0249 | 205.2511
1469.176 | 412.7431 | 209.6808 | 213.1867 | 204.8333
1470.176 | 410.3643 | 209.8251 | 213.2115 | 204.8041
1471.176 | 406.3087 | 209.7374 | 213.0674 | 204.9468
1472.176 | 406.2101 | 209.7808 | 212.9216 | 205.1073
1473.176 | 411.9023 | 209.5864 | 212.8424 | 205.1826
1474.176 | 455.1593 | 209.6844 | 212.9965 | 205.5886
1475.176 | 446.5442 | 209.6087 | 212.9517 | 205.7796
1476.176 | 442.513 | 209.6264 | 212.8495 | 205.7661
1477.176 | 438.6185 | 209.8563 | 212.7852 | 206.2864
1478.176 | 432.1446 | 210.1525 | 212.7096 | 206.7041
1479.176 | 428.7845 | 210.0608 | 212.7556 | 206.9826
1480.176 | 445.88 | 210.1887 | 212.7341 | 207.6494
1481.176 | 439.8202 | 210.2007 | 212.8864 | 207.9217
1482.176 | 447.4137 | 210.3859 | 213.9337 | 208.2771
1483.176 | 449.8715 | 210.7153 | 214.201 | 208.5358
1484.176 | 448.4758 | 210.7121 | 214.4288 | 208.6886
1485.176 | 454.0509 | 210.6397 | 214.6865 | 208.659
1486.176 | 466.6364 | 210.9749 | 214.5962 | 208.663
1487.176 | 493.2439 | 210.7529 | 214.6729 | 208.2589
1488.176 | 499.0593 | 210.8393 | 214.8764 | 208.4175
1489.176 | 497.7383 | 210.9471 | 215.2129 | 208.4305
1490.176 | 500.6403 | 211.5937 | 215.2767 | 208.6846
1491.176 | 522.3805 | 211.9021 | 215.4415 | 208.7962
1492.176 | 525.7906 | 212.3107 | 215.7597 | 209.315
1493.176 | 511.8632 | 212.7352 | 215.8731 | 209.251
1494.176 | 500.6266 | 212.9344 | 216.1184 | 209.2367
1495.176 | 494.435 | 213.2114 | 216.2507 | 209.356
1496.176 | 488.767 | 213.14 | 216.2962 | 209.0824
1497.176 | 483.304 | 212.826 | 216.2092 | 209.1446
1498.176 | 481.5986 | 212.7376 | 216.0729 | 209.2863
1499.176 | 472.6187 | 213.749 | 216.0024 | 208.9724
1500.176 | 468.4615 | 213.522 | 215.805 | 208.7265
1501.176 | 461.291 | 213.5491 | 215.6776 | 208.6331
1502.176 | 460.0076 | 213.1228 | 215.6088 | 208.3207
1503.176 | 458.9798 | 213.0341 | 215.6857 | 208.0878
1504.176 | 468.7103 | 213.0145 | 215.8771 | 208.0901
1505.176 | 463.6277 | 212.969 | 215.8237 | 208.3259
1506.176 | 459.7854 | 212.8738 | 215.8787 | 208.5882
1507.176 | 454.7014 | 213.1201 | 215.9813 | 208.5439
1508.176 | 447.8814 | 213.251 | 216.1414 | 208.7636
1509.176 | 444.1526 | 213.3495 | 216.3857 | 208.4297
1510.176 | 459.8213 | 213.5634 | 216.697 | 208.342
1511.176 | 483.5105 | 213.4681 | 216.6436 | 208.5966
1512.176 | 484.3156 | 213.6989 | 216.4312 | 208.4505
1513.176 | 518.184 | 214.0135 | 216.7693 | 208.4066
1514.176 | 531.3597 | 214.2134 | 216.785 | 208.7554
1515.176 | 540.7074 | 214.372 | 217.1078 | 208.9922
1516.176 | 530.9698 | 215.2011 | 217.395 | 210.1177
1517.176 | 522.911 | 215.4909 | 217.6494 | 209.7877
1518.176 | 522.7925 | 215.7451 | 217.8636 | 210.5236
1519.176 | 513.9029 | 215.5643 | 218.2472 | 210.6292
1520.176 | 521.7473 | 215.6782 | 218.4071 | 210.6803
1521.176 | 516.4468 | 215.571 | 218.7336 | 211.4127
1522.176 | 506.5031 | 215.3213 | 218.6569 | 211.5504
1523.176 | 499.4322 | 215.1306 | 218.6784 | 211.5062
1524.176 | 519.4976 | 214.9867 | 218.612 | 211.8475
1525.176 | 552.7637 | 215.0916 | 218.4481 | 211.8736
1526.176 | 547.8194 | 214.8514 | 218.2948 | 211.7649
1527.176 | 538.7766 | 214.9448 | 218.0975 | 211.7406
1528.176 | 527.1252 | 214.733 | 218.0486 | 211.7256
1529.176 | 519.4339 | 214.8342 | 218.1846 | 211.7044
1530.176 | 513.4757 | 215.0728 | 218.1533 | 211.6952
1531.176 | 508.89 | 215.3791 | 218.139 | 211.8165
1532.176 | 505.4053 | 215.6994 | 218.4983 | 211.8144
1533.176 | 500.2151 | 215.7947 | 218.2887 | 211.9084
1534.176 | 497.0864 | 215.9001 | 218.225 | 211.9259
1535.176 | 500.8423 | 215.7888 | 218.0872 | 212.1915
1536.176 | 492.4713 | 215.4419 | 218.0577 | 212.2424
1537.176 | 500.7264 | 215.5762 | 217.9778 | 212.4442
1538.176 | 497.1595 | 215.7876 | 217.8284 | 212.8807
1539.176 | 490.7419 | 215.7548 | 217.8583 | 213.1104
1540.176 | 483.4585 | 215.775 | 217.9283 | 212.7277
1541.176 | 475.6772 | 215.4304 | 217.8788 | 212.3206
1542.176 | 468.7284 | 215.7424 | 217.5423 | 211.98
1543.176 | 462.2465 | 215.7034 | 217.2857 | 211.9776
1544.176 | 457.6137 | 216.1104 | 217.216 | 212.2074
1545.176 | 449.1902 | 216.1012 | 217.2629 | 212.6519
1546.176 | 444.995 | 216.3224 | 217.1584 | 213.0387
1547.176 | 446.8781 | 216.6019 | 217.0957 | 213.0674
1548.176 | 440.4833 | 216.5419 | 216.9872 | 213.5723
1549.176 | 446.1746 | 217.1152 | 217.005 | 213.8168
1550.176 | 445.5766 | 217.48 | 216.954 | 214.2303
1551.176 | 441.5246 | 217.4788 | 217.4916 | 214.8018
1552.176 | 445.9611 | 217.372 | 217.4516 | 215.0427
1553.176 | 444.8238 | 217.1043 | 217.4748 | 215.1049
1554.176 | 446.0545 | 217.1137 | 217.5876 | 215.8351
1555.176 | 451.9471 | 217.3759 | 217.6855 | 216.0255
1556.176 | 457.6679 | 217.7252 | 217.6649 | 215.8509
1557.176 | 455.6525 | 218.1598 | 217.9404 | 216.2424
1558.176 | 451.9254 | 218.1758 | 218.1614 | 216.1903
1559.1917 | 450.5219 | 218.1496 | 218.2719 | 215.9423
1560.176 | 450.3528 | 218.0431 | 218.3099 | 215.5885
1561.176 | 447.3662 | 217.5082 | 218.3878 | 215.0661
1562.176 | 443.4145 | 217.8957 | 218.3786 | 214.5391
1563.176 | 440.7003 | 217.7712 | 218.2304 | 214.4307
1564.176 | 435.8771 | 217.883 | 217.9949 | 214.0813
1565.176 | 434.349 | 218.0451 | 217.5962 | 213.6592
1566.176 | 429.9399 | 217.8395 | 217.3262 | 213.8554
1567.176 | 432.3606 | 217.396 | 217.7204 | 214.0295
1568.176 | 446.1211 | 217.1702 | 217.6748 | 213.8628
1569.176 | 453.7724 | 217.156 | 217.6857 | 213.7748
1570.176 | 474.85 | 217.4128 | 218.2531 | 214.0026
1571.176 | 467.801 | 217.3527 | 218.2122 | 213.8964
1572.176 | 477.4375 | 217.453 | 218.4853 | 213.8875
1573.176 | 490.4662 | 217.6547 | 218.6898 | 214.2742
1574.176 | 483.4352 | 217.3673 | 218.9975 | 214.7803
1575.176 | 475.6184 | 217.3296 | 219.2752 | 214.4144
1576.176 | 471.8087 | 217.5432 | 219.393 | 214.3794
1577.176 | 462.8672 | 218.061 | 219.478 | 214.4971
1578.176 | 463.6279 | 218.4461 | 219.5867 | 214.4294
1579.176 | 469.6927 | 218.7166 | 219.4936 | 214.6747
1580.176 | 466.0129 | 218.4985 | 219.3906 | 214.489
1581.176 | 470.8549 | 218.0842 | 219.2395 | 214.2124
1582.176 | 470.9398 | 218.1327 | 219.0848 | 213.678
1583.176 | 463.3421 | 218.2388 | 218.977 | 213.58
1584.176 | 458.7569 | 218.1026 | 218.8432 | 213.6245
1585.176 | 466.0042 | 217.5238 | 218.8834 | 213.8131
1586.176 | 462.0106 | 217.406 | 218.757 | 214.0354
1587.176 | 463.8873 | 217.3611 | 218.7461 | 213.9923
1588.176 | 466.9269 | 217.3796 | 218.7603 | 214.4286
1589.176 | 484.2535 | 217.4493 | 218.8695 | 214.875
1590.176 | 486.6824 | 217.5142 | 219.0995 | 214.7127
1591.176 | 485.8549 | 217.6174 | 219.2886 | 215.0186
1592.176 | 482.4075 | 217.5401 | 219.2884 | 215.5206
1593.176 | 476.4254 | 217.7941 | 219.5921 | 215.3754
1594.176 | 478.2971 | 218.1324 | 219.7997 | 215.4091
1595.176 | 475.6478 | 218.1457 | 219.9252 | 215.4039
1596.176 | 501.5052 | 218.3166 | 219.8825 | 215.2066
1597.176 | 492.2402 | 218.8836 | 219.8754 | 215.4923
1598.176 | 485.4954 | 218.9993 | 220.2672 | 215.2048
1599.176 | 481.8082 | 219.1256 | 220.3529 | 215.5946
1600.176 | 484.9898 | 219.0116 | 220.2699 | 215.8046
1601.176 | 483.6691 | 218.9819 | 220.2146 | 216.0971
1602.176 | 480.9664 | 219.215 | 220.2196 | 216.1548
1603.176 | 480.8781 | 219.1758 | 220.2234 | 216.5623
1604.176 | 474.0335 | 219.1435 | 220.2144 | 216.8415
1605.176 | 473.2391 | 219.2356 | 220.3705 | 216.9242
1606.176 | 465.8612 | 219.1565 | 220.3716 | 216.6376
1607.176 | 455.0782 | 218.9757 | 220.2061 | 216.5374
1608.176 | 451.4292 | 219.4418 | 220.0571 | 216.4476
1609.176 | 452.9186 | 219.8329 | 219.8692 | 216.6695
1610.176 | 454.6258 | 219.9714 | 219.9539 | 216.9518
1611.176 | 452.7218 | 219.7006 | 220.1572 | 216.6925
1612.176 | 450.9359 | 219.6174 | 220.1411 | 216.4497
1613.176 | 448.9239 | 219.9325 | 220.3645 | 216.5746
1614.176 | 457.1678 | 220.1156 | 220.5426 | 216.6972
1615.176 | 469.2907 | 220.4437 | 220.888 | 217.1572
1616.176 | 475.7895 | 220.6077 | 220.912 | 217.3449
1617.176 | 475.5856 | 220.8733 | 220.9443 | 217.9472
1618.176 | 477.8678 | 220.9969 | 220.9516 | 218.2806
1619.176 | 474.5851 | 220.9734 | 220.676 | 217.8828
1620.176 | 467.9108 | 221.2047 | 220.7994 | 218.1659
1621.176 | 470.7259 | 221.4437 | 221.1331 | 218.1909
1622.176 | 479.927 | 221.6389 | 221.9548 | 218.2061
1623.176 | 484.2318 | 221.4189 | 221.9141 | 218.8026
1624.176 | 482.1028 | 220.9595 | 222.5198 | 218.2646
1625.176 | 478.3838 | 221.0134 | 222.5711 | 217.9552
1626.176 | 475.9873 | 220.9816 | 222.6113 | 217.5661
1627.176 | 471.327 | 220.7239 | 222.5382 | 217.384
1628.176 | 470.508 | 221.0364 | 222.5666 | 217.0965
1629.176 | 464.5219 | 220.6701 | 222.6376 | 217.0601
1630.176 | 468.2499 | 220.5288 | 222.6474 | 217.1155
1631.176 | 458.6676 | 220.4305 | 222.4823 | 217.1076
1632.176 | 456.7739 | 220.7397 | 222.3416 | 216.8865
1633.176 | 457.1703 | 220.9564 | 222.1201 | 216.6992
1634.176 | 452.7602 | 220.7914 | 222.0993 | 217.2407
1635.176 | 449.4323 | 221.0514 | 222.0085 | 217.6474
1636.176 | 443.6065 | 221.0911 | 221.9109 | 217.4328
1637.176 | 445.6603 | 221.4721 | 221.7105 | 217.2926
1638.176 | 439.4722 | 221.6642 | 221.5217 | 217.0207
1639.176 | 438.0991 | 222.0081 | 221.3786 | 216.7691
1640.176 | 434.3067 | 222.1334 | 221.4937 | 216.844
1641.176 | 431.5983 | 222.7751 | 221.5963 | 216.8694
1642.176 | 432.0868 | 223.0819 | 221.7994 | 216.9309
1643.176 | 433.9301 | 223.7739 | 221.7918 | 216.95
1644.176 | 433.8501 | 224.2979 | 222.3127 | 217.1897
1645.176 | 431.1775 | 224.7643 | 222.2819 | 217.6949
1646.176 | 428.7862 | 225.0058 | 222.1175 | 217.858
1647.176 | 427.0435 | 225.1973 | 221.9364 | 217.7355
1648.176 | 423.9441 | 225.2333 | 222.0496 | 217.784
1649.176 | 425.7864 | 225.1733 | 222.0687 | 217.7962
1650.176 | 428.5026 | 224.9257 | 221.946 | 217.6622
1651.176 | 427.6996 | 224.9145 | 221.8406 | 217.535
1652.176 | 426.2416 | 224.8912 | 221.8873 | 217.3485
1653.176 | 424.3642 | 224.77 | 221.9478 | 217.8049
1654.176 | 425.8266 | 224.3 | 221.8705 | 218.3704
1655.176 | 427.67 | 224.1615 | 221.772 | 218.0432
1656.176 | 431.7473 | 224.2181 | 221.8725 | 218.0273
1657.176 | 432.4738 | 224.3434 | 222.0136 | 218.0669
1658.176 | 435.8827 | 224.4635 | 222.0366 | 218.0028
1659.176 | 440.9879 | 224.428 | 221.9695 | 218.3564
1660.176 | 445.8864 | 224.4801 | 221.8206 | 218.3085
1661.176 | 449.3773 | 224.2725 | 221.6078 | 218.362
1662.176 | 448.4696 | 224.4482 | 221.6046 | 218.1446
1663.176 | 446.9182 | 224.3585 | 221.5895 | 218.3456
1664.176 | 447.336 | 224.2598 | 221.7464 | 218.8817
1665.176 | 445.3305 | 224.0682 | 222.0806 | 218.645
1666.176 | 445.3783 | 224.0294 | 222.4068 | 219.1852
1667.176 | 454.1077 | 223.8802 | 222.7018 | 219.0104
1668.176 | 465.3426 | 224.1241 | 222.966 | 218.9323
1669.176 | 462.7458 | 224.359 | 223.1513 | 218.771
1670.176 | 458.8869 | 224.1926 | 223.3792 | 218.7014
1671.176 | 468.3332 | 223.9604 | 223.6429 | 218.4394
1672.176 | 463.6915 | 224.1503 | 223.8062 | 218.4715
1673.176 | 459.4387 | 224.9515 | 224.0859 | 219.1186
1674.176 | 458.6221 | 224.4632 | 224.5355 | 219.4245
1675.176 | 458.2317 | 224.4168 | 224.9998 | 219.5867
1676.176 | 464.0434 | 223.9513 | 225.3554 | 220.0226
1677.176 | 462.2117 | 223.847 | 226.0509 | 219.72
1678.176 | 481.3838 | 223.8654 | 225.8085 | 219.6662
1679.176 | 504.6574 | 223.6429 | 225.5261 | 220.0151
1680.176 | 499.8218 | 223.2849 | 225.3329 | 219.6924
1681.176 | 503.5684 | 223.0336 | 225.0996 | 219.9608
1682.176 | 505.152 | 223.2609 | 224.8949 | 219.8685
1683.176 | 498.6384 | 223.1324 | 224.7027 | 219.3875
1684.176 | 493.7144 | 222.6913 | 224.5971 | 219.8621
1685.176 | 489.3676 | 222.7722 | 224.8397 | 220.0883
1686.176 | 516.6055 | 222.7353 | 224.737 | 220.0694
1687.176 | 515.0618 | 222.68 | 224.7447 | 219.8994
1688.176 | 518.5951 | 222.5882 | 224.7781 | 219.8682
1689.176 | 512.8412 | 222.7862 | 224.9731 | 219.7766
1690.176 | 506.4347 | 222.6614 | 224.9894 | 219.4936
1691.176 | 499.4578 | 222.834 | 224.9922 | 219.2228
1692.176 | 493.3696 | 223.2342 | 224.9348 | 219.2728
1693.176 | 486.0954 | 222.7532 | 224.9041 | 218.926
1694.176 | 482.1855 | 222.3826 | 224.8166 | 218.6999
1695.176 | 477.3425 | 222.3441 | 224.5548 | 218.8867
1696.176 | 474.0971 | 222.3079 | 224.5221 | 218.8499
1697.176 | 471.6467 | 222.4243 | 224.3151 | 218.7398
1698.176 | 477.3394 | 222.8832 | 224.2343 | 218.7633
1699.176 | 479.4178 | 223.1663 | 224.3298 | 218.5833
1700.176 | 478.0699 | 223.1425 | 224.299 | 218.7538
1701.176 | 473.0679 | 222.988 | 224.5977 | 218.683
1702.176 | 472.9391 | 223.2827 | 224.6172 | 218.7814
1703.176 | 484.4725 | 223.2517 | 224.7239 | 219.0177
1704.176 | 495.9514 | 223.3041 | 224.8152 | 219.0014
1705.176 | 491.7232 | 223.3714 | 225.0717 | 219.1849
1706.176 | 489.0888 | 223.3035 | 225.044 | 219.2918
1707.176 | 487.5722 | 223.1681 | 225.0729 | 219.3131
1708.176 | 480.0703 | 223.3084 | 225.2815 | 219.4716
1709.176 | 479.1845 | 223.2655 | 225.6971 | 219.6592
1710.176 | 473.7889 | 222.8117 | 225.7299 | 219.5489
1711.176 | 468.532 | 222.8158 | 225.7063 | 219.3413
1712.176 | 463.4093 | 222.8587 | 225.745 | 219.1974
1713.176 | 467.3122 | 222.6783 | 225.5761 | 218.9643
1714.176 | 474.3523 | 222.3649 | 225.4307 | 219.1236
1715.176 | 488.2574 | 222.4115 | 225.4189 | 218.9064
1716.176 | 516.9414 | 222.2352 | 225.4901 | 219.3752
1717.176 | 515.5188 | 222.2748 | 225.535 | 219.4561
1718.176 | 508.5318 | 222.4992 | 225.4808 | 219.449
1719.176 | 501.0254 | 222.6649 | 225.3746 | 219.4567
1720.176 | 500.7481 | 222.8844 | 225.2084 | 219.4589
1721.176 | 496.8514 | 222.8434 | 225.1909 | 219.3459
1722.176 | 492.248 | 222.4285 | 225.1749 | 219.2606
1723.176 | 499.2783 | 222.4656 | 225.055 | 219.1824
1724.176 | 501.0801 | 222.4073 | 224.9394 | 219.1266
1725.176 | 505.0024 | 222.5143 | 224.8056 | 218.9078
1726.176 | 499.1872 | 222.267 | 224.7412 | 218.6789
1727.176 | 492.3341 | 222.1495 | 224.6053 | 218.7637
1728.176 | 485.7011 | 222.2231 | 224.3865 | 218.5957
1729.176 | 487.4974 | 222.284 | 224.1176 | 218.1987
1730.176 | 487.5872 | 222.2374 | 223.9177 | 218.0845
1731.176 | 485.8096 | 222.4259 | 223.821 | 218.6853
1732.176 | 479.5445 | 222.724 | 223.6628 | 218.5171
1733.176 | 477.9866 | 223.0818 | 223.5572 | 218.222
1734.176 | 478.7542 | 223.4218 | 223.3351 | 218.2841
1735.176 | 475.5857 | 223.5426 | 223.0976 | 218.5524
1736.176 | 471.9821 | 223.9497 | 222.9174 | 218.7847
1737.176 | 473.3156 | 224.2308 | 222.811 | 218.7116
1738.176 | 471.3128 | 224.5113 | 222.907 | 218.9257
1739.176 | 471.2363 | 224.5305 | 223.0007 | 218.8947
1740.176 | 474.3823 | 224.5728 | 223.1288 | 218.9509
1741.176 | 469.7824 | 224.3173 | 223.0545 | 219.1665
1742.176 | 464.6271 | 224.203 | 222.8477 | 219.1994
1743.176 | 462.9202 | 224.1836 | 222.6631 | 218.9613
1744.176 | 459.4028 | 224.0132 | 222.7517 | 218.5897
1745.176 | 451.4362 | 223.6767 | 222.6464 | 218.2178
1746.176 | 451.3264 | 223.437 | 222.6378 | 218.5179
1747.176 | 449.38 | 223.5233 | 222.8307 | 218.0484
1748.176 | 450.5619 | 223.4615 | 222.8277 | 217.872
1749.176 | 451.6659 | 223.5759 | 222.8227 | 217.4337
1750.176 | 456.9716 | 224.0121 | 222.7786 | 217.2078
1751.176 | 455.1592 | 223.6607 | 222.7022 | 216.8668
1752.176 | 448.6069 | 223.9573 | 222.7896 | 216.8566
1753.176 | 445.5651 | 224.1771 | 222.6845 | 216.961
1754.176 | 451.3529 | 224.2579 | 222.5691 | 217.0468
1755.176 | 445.8436 | 224.1723 | 222.7141 | 217.2577
1756.176 | 444.4649 | 224.4369 | 222.8525 | 217.2548
1757.176 | 439.5234 | 224.4593 | 223.0044 | 217.1915
1758.176 | 437.0599 | 224.9534 | 223.0491 | 217.52
1759.176 | 438.6778 | 224.9375 | 222.9921 | 217.7595
1760.176 | 440.8439 | 224.7971 | 222.9931 | 217.5437
1761.176 | 439.0116 | 224.6429 | 223.1268 | 217.7126
1762.176 | 436.7328 | 224.5773 | 223.2596 | 217.9765
1763.176 | 432.0013 | 224.3482 | 223.1471 | 217.9566
1764.176 | 428.8619 | 224.0795 | 222.9787 | 218.127
1765.176 | 424.0667 | 223.7554 | 222.8029 | 217.958
1766.176 | 425.1334 | 223.6891 | 222.6398 | 217.6678
1767.176 | 430.2265 | 223.22 | 222.5142 | 217.3948
1768.176 | 433.8984 | 223.0239 | 222.3588 | 216.9047
1769.176 | 434.3241 | 223.0801 | 222.2151 | 216.333
1770.176 | 435.4694 | 222.5194 | 222.1171 | 216.4161
1771.176 | 433.0772 | 222.3716 | 222.2083 | 217.0601
1772.176 | 432.0481 | 223.5106 | 222.1846 | 216.6876
1773.176 | 430.6808 | 223.356 | 222.2732 | 216.2731
1774.176 | 428.916 | 223.193 | 222.2053 | 215.9149
1775.176 | 430.327 | 222.8499 | 222.3421 | 216.0585
1776.176 | 432.6982 | 222.8176 | 222.6031 | 216.1528
1777.176 | 434.751 | 222.7111 | 222.7655 | 216.4165
1778.176 | 433.165 | 222.4717 | 222.9703 | 216.2386
1779.176 | 434.8469 | 222.3484 | 223.0603 | 216.6443
1780.176 | 432.1797 | 222.8617 | 223.157 | 216.729
1781.176 | 429.3872 | 223.0229 | 223.7944 | 217.3009
1782.176 | 425.4282 | 222.6017 | 223.9804 | 218.0365
1783.176 | 421.2875 | 222.4173 | 224.1491 | 217.9878
1784.176 | 418.6641 | 222.606 | 224.2657 | 217.8878
1785.176 | 421.1048 | 223.0791 | 224.3865 | 217.5921
1786.176 | 418.1175 | 223.0562 | 224.6031 | 218.1553
1787.176 | 422.498 | 223.2381 | 224.8148 | 218.2174
1788.176 | 426.218 | 223.5656 | 224.9992 | 218.3109
1789.176 | 425.818 | 223.3511 | 225.2707 | 218.3062
1790.176 | 428.2136 | 223.6657 | 225.3112 | 218.9262
1791.176 | 446.3073 | 223.2581 | 225.568 | 218.4982
1792.176 | 449.5472 | 223.1872 | 225.5372 | 218.316
1793.176 | 446.4953 | 222.8651 | 225.5235 | 218.1039
1794.176 | 446.3116 | 222.9256 | 225.4741 | 218.1475
1795.176 | 440.1918 | 222.9851 | 225.3594 | 218.4301
1796.176 | 433.3809 | 222.883 | 225.1825 | 218.1499
1797.176 | 431.0441 | 222.9784 | 225.2087 | 218.2153
1798.176 | 431.1193 | 223.0547 | 224.9738 | 218.06
1799.176 | 429.6359 | 223.1994 | 224.6751 | 218.5374
1800.176 | 428.6048 | 222.7227 | 224.4278 | 218.568
1801.176 | 430.1438 | 222.3477 | 224.1085 | 218.5781
1802.1917 | 430.0562 | 222.3115 | 223.8758 | 218.5648
1803.176 | 428.9159 | 222.2749 | 223.8037 | 218.4738
1804.176 | 429.0758 | 222.2797 | 223.823 | 218.4503
1805.176 | 428.5474 | 222.1189 | 223.7812 | 218.2411
1806.176 | 430.3191 | 221.9507 | 223.732 | 218.1037
1807.176 | 444.2719 | 222.0388 | 223.7147 | 218.1081
1808.176 | 442.9004 | 221.9211 | 223.7006 | 218.1019
1809.176 | 437.2495 | 221.7878 | 223.7915 | 218.2312
1810.176 | 439.2963 | 221.3555 | 223.8377 | 218.77
1811.176 | 440.9326 | 221.2749 | 223.8368 | 218.5953
1812.176 | 444.5448 | 221.6447 | 223.7127 | 218.644
1813.176 | 442.3831 | 222.225 | 223.9044 | 218.9861
1814.176 | 442.7276 | 222.8187 | 223.8753 | 219.2412
1815.176 | 439.4314 | 222.9096 | 224.019 | 219.4381
1816.176 | 466.9838 | 222.9461 | 224.0467 | 219.2657
1817.176 | 489.3973 | 223.1709 | 223.7717 | 219.3774
1818.176 | 513.566 | 223.2912 | 223.537 | 219.5696
1819.176 | 510.6466 | 223.4539 | 223.3587 | 219.5263
1820.176 | 522.1484 | 223.2547 | 223.3024 | 219.3834
1821.176 | 533.9109 | 223.3691 | 223.1347 | 219.2637
1822.176 | 551.7871 | 223.4062 | 223.0829 | 219.2676
1823.176 | 556.5862 | 223.4827 | 223.0357 | 219.3839
1824.176 | 566.2385 | 223.4471 | 222.8958 | 219.6082
1825.176 | 584.0543 | 223.4357 | 222.7385 | 219.5978
1826.176 | 593.7438 | 223.5754 | 222.6027 | 219.6966
1827.176 | 585.6536 | 223.7982 | 222.6655 | 219.7878
1828.176 | 575.8909 | 223.9876 | 222.5872 | 219.7124
1829.176 | 559.4682 | 223.5312 | 222.4816 | 219.4887
1830.176 | 551.155 | 223.2669 | 222.4935 | 219.1075
1831.176 | 577.5185 | 223.4328 | 222.5817 | 218.9645
1832.176 | 591.1785 | 223.8566 | 222.7647 | 219.0843
1833.176 | 603.3995 | 224.22 | 222.8261 | 219.0125
1834.176 | 613.7075 | 223.9264 | 223.0641 | 218.6956
1835.176 | 623.5158 | 223.7225 | 223.1848 | 218.7313
1836.176 | 606.1786 | 223.6895 | 223.427 | 218.8426
1837.176 | 601.8467 | 223.2051 | 223.7248 | 218.726
1838.176 | 594.2728 | 222.6719 | 223.6159 | 218.7439
1839.176 | 598.1195 | 222.3922 | 223.5163 | 218.4051
1840.176 | 592.7986 | 222.2588 | 223.6912 | 218.5408
1841.176 | 591.0893 | 222.2389 | 223.6161 | 218.4463
1842.176 | 591.8318 | 222.1473 | 223.4895 | 218.3892
1843.176 | 599.2523 | 222.0015 | 223.3509 | 218.139
1844.176 | 580.0008 | 221.5069 | 223.1314 | 217.8343
1845.176 | 561.6945 | 221.1787 | 222.8304 | 217.5136
1846.176 | 544.5005 | 220.7947 | 222.6486 | 217.3946
1847.176 | 529.7969 | 220.7573 | 222.3988 | 217.1724
1848.176 | 521.9383 | 220.6645 | 222.2784 | 216.9246
1849.176 | 516.5469 | 221.0618 | 222.0564 | 216.9132
1850.176 | 515.143 | 220.9488 | 221.9947 | 216.7964
1851.176 | 514.1976 | 221.0423 | 221.823 | 216.712
1852.176 | 532.4486 | 221.0556 | 221.6794 | 216.5767
1853.176 | 524.5765 | 221.1897 | 221.919 | 216.7856
1854.176 | 520.2734 | 221.2324 | 222.1705 | 217.027
1855.176 | 516.7531 | 221.1695 | 222.4495 | 216.9989
1856.176 | 506.855 | 220.9853 | 222.5499 | 217.0087
1857.176 | 499.7182 | 221.2368 | 222.6299 | 216.9763
1858.176 | 493.318 | 221.2891 | 222.72 | 217.1467
1859.176 | 483.5838 | 221.2051 | 222.7108 | 217.3268
1860.176 | 478.7424 | 220.7534 | 222.8574 | 217.2934
1861.176 | 472.8085 | 220.5375 | 222.8963 | 217.3765
1862.176 | 463.7782 | 220.7011 | 222.8573 | 217.5
1863.176 | 455.4037 | 220.9147 | 223.1502 | 217.845
1864.176 | 453.0154 | 220.5982 | 223.3788 | 217.6556
1865.176 | 451.8895 | 220.3634 | 223.4405 | 217.6419
1866.176 | 451.8806 | 220.457 | 223.4545 | 217.7992
1867.176 | 450.8642 | 220.346 | 223.4454 | 217.4924
1868.176 | 444.7807 | 220.5335 | 223.4935 | 217.4872
1869.176 | 438.9631 | 220.7036 | 223.4633 | 217.7274
1870.176 | 439.5339 | 220.7836 | 223.5074 | 217.6555
1871.176 | 441.204 | 220.8537 | 223.6665 | 217.6195
1872.176 | 433.2488 | 220.9936 | 223.7451 | 217.4864
1873.176 | 426.0514 | 221.3528 | 223.6491 | 217.3419
1874.176 | 424.7058 | 221.6951 | 223.6539 | 217.2949
1875.176 | 427.5772 | 221.5995 | 223.5055 | 217.2662
1876.176 | 448.5985 | 221.8892 | 223.3905 | 217.5027
1877.176 | 458.854 | 222.1357 | 223.0906 | 217.2218
1878.176 | 462.4164 | 222.4246 | 222.9568 | 216.9443
1879.176 | 466.2121 | 222.4796 | 222.8982 | 216.6017
1880.176 | 471.1216 | 222.4503 | 222.7855 | 216.3589
1881.176 | 475.1649 | 222.758 | 222.6592 | 216.5289
1882.176 | 482.7267 | 223.2019 | 222.4621 | 217.0113
1883.176 | 485.3348 | 223.342 | 222.4261 | 216.9988
1884.176 | 490.1569 | 223.2326 | 222.522 | 217.3851
1885.176 | 507.7999 | 223.1157 | 222.3529 | 217.2021
1886.176 | 511.3302 | 223.5822 | 222.3345 | 217.2403
1887.176 | 522.41 | 223.9883 | 222.3406 | 216.8163
1888.176 | 527.2266 | 224.2255 | 222.2323 | 216.6568
1889.176 | 535.2865 | 224.4289 | 222.1511 | 217.0197
1890.176 | 531.2561 | 224.1217 | 222.1808 | 217.1865
1891.176 | 529.8692 | 223.8935 | 221.965 | 217.1983
1892.176 | 530.6803 | 224.1241 | 221.7784 | 217.3965
1893.176 | 531.4143 | 224.0364 | 221.6236 | 217.4751
1894.176 | 534.5632 | 224.1351 | 221.5801 | 217.4016
1895.176 | 541.0905 | 224.1029 | 221.5182 | 217.5144
1896.176 | 547.031 | 224.3392 | 221.3767 | 217.6808
1897.176 | 548.7746 | 224.3492 | 221.3021 | 217.6186
1898.176 | 552.3864 | 224.6691 | 221.3487 | 217.7893
1899.176 | 550.7086 | 224.7469 | 221.2852 | 217.9929
1900.176 | 553.8749 | 224.5674 | 221.234 | 217.7716
1901.176 | 556.1824 | 224.4731 | 221.173 | 218.5716
1902.176 | 567.9744 | 224.453 | 221.0542 | 218.3883
1903.176 | 572.1969 | 224.5102 | 221.1976 | 218.2907
1904.176 | 568.7124 | 224.8713 | 221.2198 | 218.5971
1905.176 | 573.2797 | 225.0962 | 221.4748 | 218.264
1906.176 | 574.8195 | 224.8308 | 221.8643 | 218.3138
1907.176 | 567.9365 | 224.423 | 221.9138 | 218.065
1908.176 | 574.6837 | 224.1486 | 221.9751 | 217.8581
1909.176 | 582.2827 | 223.8933 | 221.8864 | 217.6609
1910.176 | 579.389 | 223.9593 | 221.716 | 217.6712
1911.176 | 587.8485 | 223.6494 | 221.6549 | 217.5074
1912.176 | 584.5604 | 223.4691 | 221.5539 | 217.502
1913.176 | 583.495 | 223.3059 | 221.3885 | 217.4807
1914.176 | 577.0908 | 223.5084 | 221.2695 | 217.5503
1915.176 | 585.158 | 223.5876 | 221.178 | 217.614
1916.176 | 588.6963 | 223.8806 | 221.2144 | 217.7451
1917.176 | 592.4273 | 224.1953 | 221.3989 | 217.9121
1918.176 | 600.3871 | 224.3954 | 221.558 | 217.8897
1919.176 | 602.126 | 224.3655 | 221.7611 | 217.9867
1920.176 | 605.1041 | 224.3396 | 221.988 | 218.09
1921.176 | 622.602 | 224.4173 | 222.1034 | 218.2909
1922.1917 | 633.7462 | 224.1317 | 222.1432 | 218.3703
1923.176 | 631.0565 | 224.2809 | 222.2474 | 218.4351
1924.176 | 637.1443 | 224.0111 | 222.2418 | 218.4197
1925.176 | 643.7632 | 224.1495 | 222.1766 | 218.6907
1926.176 | 645.0746 | 223.6247 | 222.0442 | 218.6701
1927.176 | 652.8183 | 223.4031 | 221.936 | 218.7292
1928.176 | 658.8727 | 223.5697 | 221.8336 | 218.6599
1929.176 | 667.8165 | 223.589 | 221.8877 | 218.7388
1930.176 | 658.7386 | 223.5782 | 222.0235 | 218.8362
1931.176 | 661.5066 | 223.4887 | 222.0257 | 218.6288
1932.176 | 663.1898 | 223.1509 | 221.9077 | 218.6113
1933.176 | 657.9561 | 223.0028 | 221.8099 | 218.3956
1934.176 | 650.8949 | 222.8773 | 221.7811 | 218.4185
1935.176 | 650.2717 | 222.6883 | 221.6536 | 218.2975
1936.176 | 646.7157 | 222.7667 | 221.5426 | 218.3044
1937.176 | 653.7755 | 222.7589 | 221.7295 | 218.3998
1938.176 | 657.7328 | 222.9429 | 221.8087 | 218.5302
1939.176 | 659.8416 | 223.1287 | 221.7013 | 218.4364
1940.176 | 659.3758 | 223.4822 | 221.5304 | 218.3624
1941.176 | 643.2755 | 223.707 | 221.3103 | 218.1672
1942.176 | 638.4249 | 223.733 | 221.2815 | 218.0776
1943.176 | 642.6288 | 223.8088 | 221.1784 | 218.3262
1944.176 | 634.074 | 223.7537 | 221.0615 | 218.5287
1945.176 | 640.0621 | 223.7701 | 220.9524 | 218.7725
1946.176 | 640.1764 | 223.9073 | 221.0405 | 218.6989
1947.176 | 641.6021 | 224.0001 | 221.1851 | 218.673
1948.176 | 640.5696 | 223.9354 | 221.2298 | 218.7076
1949.176 | 648.3788 | 223.9571 | 221.2181 | 218.7519
1950.176 | 652.6963 | 223.8855 | 221.1771 | 219.2244
1951.176 | 663.5142 | 223.8363 | 221.171 | 218.8208
1952.176 | 667.957 | 223.8524 | 221.2002 | 218.5912
1953.176 | 651.67 | 223.6023 | 221.2575 | 219.0558
1954.176 | 647.5011 | 223.6934 | 221.3156 | 219.6446
1955.176 | 641.3882 | 223.677 | 221.3661 | 219.4928
1956.176 | 640.8453 | 223.9441 | 221.3987 | 219.4047
1957.176 | 645.5181 | 224.013 | 221.3943 | 219.5325
1958.176 | 643.1618 | 224.5883 | 221.4012 | 219.5292
1959.176 | 651.7273 | 224.9193 | 221.3914 | 219.3356
1960.176 | 652.1724 | 225.4153 | 221.4744 | 219.1631
1961.176 | 652.8172 | 225.4586 | 221.5922 | 219.1615
1962.176 | 662.7534 | 225.4159 | 221.59 | 219.4055
1963.176 | 661.9264 | 225.1093 | 221.6496 | 219.6993
1964.176 | 663.0024 | 225.2841 | 221.8081 | 220.1007
1965.176 | 659.0671 | 225.8174 | 221.9026 | 219.8813
1966.176 | 660.7134 | 225.9901 | 221.8622 | 219.9975
1967.176 | 655.3218 | 225.8215 | 221.9485 | 220.0478
1968.176 | 665.933 | 225.6984 | 222.0891 | 220.2567
1969.176 | 666.762 | 225.6474 | 221.9961 | 220.3741
1970.176 | 669.4154 | 225.6908 | 221.9272 | 220.158
1971.176 | 663.0493 | 225.6172 | 221.958 | 220.2963
1972.176 | 662.5473 | 225.5427 | 221.8882 | 220.203
1973.176 | 657.9086 | 225.4261 | 221.7776 | 219.9351
1974.176 | 654.7797 | 225.4147 | 221.844 | 220.0389
1975.176 | 650.4172 | 225.4734 | 221.9321 | 220.0212
1976.176 | 651.7546 | 225.7059 | 221.8882 | 219.9839
1977.176 | 651.5915 | 225.8014 | 221.8001 | 219.8179
1978.176 | 645.3307 | 225.7011 | 221.7397 | 219.5518
1979.176 | 649.3292 | 225.9212 | 221.7131 | 219.5
1980.176 | 653.6937 | 226.1517 | 221.8597 | 219.5096
1981.176 | 654.0374 | 226.1239 | 221.9815 | 219.4571
1982.176 | 655.6377 | 226.1097 | 221.8565 | 219.3058
1983.176 | 647.9637 | 226.0258 | 221.8842 | 219.1937
1984.176 | 640.3921 | 225.9039 | 221.842 | 219.0344
1985.176 | 638.0044 | 225.7344 | 221.838 | 218.7493
1986.176 | 642.2115 | 225.4361 | 222.1314 | 218.44
1987.176 | 640.5999 | 225.5106 | 222.0806 | 218.1722
1988.176 | 645.08 | 225.1894 | 222.0293 | 217.8687
1989.176 | 644.4538 | 225.0813 | 222.0387 | 217.7615
1990.176 | 644.8657 | 224.4528 | 221.9308 | 217.4973
1991.176 | 639.7878 | 224.1139 | 221.7384 | 217.4466
1992.176 | 626.6783 | 223.7814 | 221.7582 | 217.3536
1993.176 | 622.3661 | 223.6875 | 221.6337 | 217.2013
1994.176 | 616.4523 | 223.3719 | 221.4274 | 217.3634
1995.176 | 614.9892 | 223.0402 | 221.253 | 217.1985
1996.176 | 622.4894 | 223.0382 | 221.167 | 217.3905
1997.176 | 633.8452 | 223.3707 | 221.1993 | 217.8665
1998.176 | 641.9582 | 222.9956 | 221.2587 | 218.0079
1999.176 | 640.2833 | 223.094 | 221.839 | 218.3739
2000.176 | 632.8622 | 222.9376 | 221.972 | 218.2713
2001.176 | 633.4379 | 222.946 | 222.0386 | 219.1372
2002.176 | 624.1352 | 223.0844 | 222.2704 | 219.4866
2003.176 | 631.8113 | 223.192 | 222.9192 | 219.3691
2004.176 | 626.3034 | 223.2122 | 222.8616 | 219.4771
2005.176 | 616.4551 | 223.2172 | 222.9338 | 219.505
2006.176 | 624.2892 | 223.2748 | 222.9137 | 219.5264
2007.176 | 632.401 | 223.1961 | 223.0496 | 219.5901
2008.176 | 635.8473 | 223.1737 | 223.1095 | 219.3315
2009.176 | 631.2989 | 223.2956 | 223.2662 | 219.3684
2010.176 | 627.5752 | 223.4802 | 223.2658 | 219.2625
2011.176 | 618.4868 | 223.447 | 223.1688 | 219.1022
2012.176 | 634.362 | 223.3425 | 223.2648 | 219.0322
2013.176 | 634.1846 | 223.3102 | 223.2047 | 218.8754
2014.176 | 645.346 | 223.2191 | 223.2018 | 218.7549
2015.176 | 642.868 | 223.0914 | 223.2422 | 218.5655
2016.176 | 640.0118 | 222.9078 | 222.9901 | 218.4203
2017.176 | 644.9495 | 222.892 | 222.8766 | 218.541
2018.176 | 650.8534 | 222.6633 | 222.7695 | 218.6987
2019.176 | 634.0726 | 222.3917 | 222.7478 | 218.8864
2020.176 | 632.6273 | 222.1318 | 222.6622 | 218.8799
2021.176 | 629.38 | 221.8674 | 222.5991 | 219.0231
2022.176 | 639.4547 | 221.8742 | 222.5414 | 219.154
2023.176 | 632.0323 | 221.5647 | 222.4043 | 219.2997
2024.176 | 640.8314 | 221.8102 | 222.3639 | 219.4653
2025.176 | 655.1677 | 222.0847 | 222.1775 | 219.3492
2026.176 | 644.2861 | 222.4527 | 221.9954 | 219.5009
2027.176 | 653.5681 | 222.7318 | 222.0147 | 219.585
2028.176 | 641.2179 | 222.7451 | 222.2034 | 219.821
2029.176 | 649.1215 | 222.6611 | 222.2377 | 220.0034
2030.176 | 655.315 | 222.8137 | 222.4178 | 220.0175
2031.176 | 657.3821 | 223.2423 | 222.4812 | 220.1451
2032.176 | 657.2493 | 223.3872 | 222.4514 | 220.1321
2033.176 | 664.6809 | 223.741 | 222.422 | 219.9374
2034.176 | 657.7642 | 223.9072 | 222.3555 | 220.0164
2035.176 | 653.6844 | 224.1725 | 222.6989 | 220.2404
2036.176 | 651.5213 | 224.3626 | 222.929 | 219.958
2037.176 | 654.3578 | 224.7184 | 222.913 | 220.0339
2038.176 | 629.9818 | 225.2575 | 222.7791 | 220.0486
2039.176 | 622.8606 | 225.1062 | 222.405 | 219.8946
2040.176 | 630.9205 | 225.3357 | 222.3621 | 219.5817
2041.176 | 620.089 | 225.3711 | 222.1531 | 219.4287
2042.176 | 617.6658 | 225.4097 | 222.1889 | 219.518
2043.176 | 622.5584 | 225.42 | 222.0904 | 219.6254
2044.176 | 618.8103 | 225.3237 | 222.2029 | 219.6355
2045.176 | 601.125 | 225.3174 | 222.1964 | 219.7166
2046.176 | 594.6102 | 225.2836 | 222.0782 | 219.7247
2047.176 | 586.9943 | 225.3013 | 222.0281 | 219.4552
2048.176 | 588.6394 | 225.369 | 222.0005 | 219.3823
2049.176 | 586.8538 | 225.3676 | 221.868 | 219.7403
2050.176 | 585.3655 | 225.3978 | 221.8384 | 219.92
2051.176 | 602.7795 | 225.4898 | 221.7203 | 219.9872
2052.176 | 598.1165 | 225.3846 | 221.8342 | 219.8349
2053.176 | 604.7554 | 225.5218 | 221.8348 | 219.6245
2054.176 | 599.5925 | 225.77 | 221.8749 | 219.6402
2055.176 | 602.0196 | 225.6329 | 222.0131 | 220.0152
2056.176 | 589.4075 | 225.6899 | 222.1152 | 220.0747
2057.176 | 587.3743 | 225.5505 | 222.0408 | 220.3735
2058.176 | 573.1935 | 225.3737 | 222.0711 | 220.668
2059.176 | 560.1897 | 225.2955 | 222.0357 | 220.6895
2060.176 | 573.6349 | 225.0655 | 221.8569 | 220.6753
2061.176 | 560.4375 | 224.6679 | 221.8921 | 220.9178
2062.1917 | 581.1977 | 224.6797 | 221.9596 | 221.2426
2063.176 | 572.2598 | 224.6204 | 221.7562 | 221.2568
2064.176 | 567.185 | 224.5756 | 221.7075 | 221.3433
2065.176 | 570.388 | 224.8328 | 221.5182 | 221.4254
2066.176 | 582.584 | 224.9348 | 221.5226 | 221.2443
2067.176 | 589.1351 | 224.8359 | 221.255 | 221.2693
2068.176 | 593.3921 | 224.6294 | 221.0638 | 221.0432
2069.176 | 608.6974 | 224.6781 | 220.9846 | 220.7421
2070.176 | 607.9897 | 224.5022 | 220.89 | 220.6449
2071.176 | 620.1699 | 224.7506 | 220.8496 | 220.7423
2072.176 | 619.374 | 224.8877 | 220.9224 | 220.6502
2073.176 | 607.0148 | 225.1079 | 221.1678 | 220.782
2074.176 | 593.6767 | 225.0194 | 221.2674 | 221.296
2075.176 | 588.6208 | 224.9964 | 221.3808 | 221.1898
2076.176 | 576.8834 | 224.6964 | 221.3707 | 221.1988
2077.176 | 568.6179 | 224.8701 | 221.4157 | 221.4609
2078.176 | 559.3368 | 224.6289 | 221.4703 | 221.3044
2079.176 | 571.0538 | 225.2263 | 221.5695 | 221.2065
2080.176 | 569.7355 | 225.138 | 221.5145 | 221.0226
2081.176 | 589.6492 | 225.0103 | 221.8671 | 221.0159
2082.176 | 593.4646 | 225.0508 | 221.8439 | 220.7955
2083.176 | 583.7749 | 225.1785 | 221.7201 | 220.5661
2084.176 | 565.9208 | 225.0843 | 221.6735 | 220.7648
2085.176 | 568.3688 | 225.2567 | 221.6901 | 221.2291
2086.176 | 584.2755 | 225.2409 | 221.7539 | 221.2299
2087.176 | 573.361 | 225.2781 | 221.9249 | 220.9571
2088.176 | 559.5812 | 225.2066 | 221.8668 | 220.6315
2089.176 | 548.5026 | 225.1867 | 221.7981 | 220.4664
2090.176 | 550.3305 | 225.2415 | 222.0635 | 220.1349
2091.176 | 549.6712 | 225.2631 | 222.2759 | 220.0143
2092.176 | 546.6028 | 225.198 | 222.4654 | 219.7993
2093.176 | 536.6645 | 224.7973 | 222.4491 | 219.4377
2094.176 | 526.3849 | 224.6268 | 222.554 | 219.3566
2095.176 | 516.9676 | 224.5305 | 222.6728 | 219.2054
2096.176 | 511.3096 | 224.6298 | 222.7914 | 219.4348
2097.176 | 518.0121 | 224.6682 | 223.0738 | 219.4486
2098.176 | 513.556 | 224.6839 | 223.4372 | 219.6958
2099.176 | 526.6623 | 224.7051 | 223.524 | 219.8063
2100.176 | 534.784 | 224.7578 | 223.612 | 219.7174
2101.176 | 534.0867 | 224.8926 | 223.9867 | 220.034
2102.176 | 539.8831 | 225.0357 | 224.3253 | 220.1259
2103.176 | 539.6498 | 225.3235 | 225.022 | 220.6293
2104.176 | 529.3771 | 225.2588 | 225.1527 | 220.796
2105.176 | 529.8293 | 225.166 | 225.2594 | 220.8742
2106.176 | 533.4209 | 225.1353 | 225.3116 | 221.0079
2107.176 | 541.9018 | 225.0348 | 225.2167 | 221.1577
2108.176 | 532.7396 | 225.1799 | 225.1297 | 221.9236
2109.176 | 523.2906 | 225.1866 | 225.0634 | 221.8386
2110.176 | 533.1807 | 225.3372 | 224.9774 | 221.9258
2111.176 | 538.78 | 225.4167 | 224.8223 | 221.476
2112.176 | 535.9502 | 225.4541 | 224.7255 | 221.1376
2113.176 | 533.8514 | 225.7287 | 224.4944 | 221.3354
2114.176 | 523.9929 | 225.4728 | 224.4076 | 221.5637
2115.176 | 523.4239 | 225.6247 | 224.417 | 221.5036
2116.176 | 535.9051 | 225.5773 | 224.4174 | 221.43
2117.176 | 541.717 | 225.6352 | 224.3858 | 221.1798
2118.176 | 554.7914 | 225.2919 | 224.5159 | 220.8938
2119.176 | 564.0506 | 225.3058 | 224.4775 | 220.7874
2120.176 | 564.7117 | 225.3081 | 224.3857 | 220.9015
2121.176 | 552.9265 | 224.949 | 224.168 | 220.8825
2122.176 | 544.8639 | 224.8116 | 223.9848 | 220.7865
2123.176 | 539.0742 | 224.7175 | 223.8421 | 220.5905
2124.176 | 540.7185 | 224.6951 | 223.8664 | 220.2007
2125.176 | 549.723 | 224.7421 | 223.5963 | 219.8763
2126.176 | 543.4776 | 224.9024 | 223.4171 | 219.5867
2127.176 | 535.376 | 225.1993 | 223.3487 | 219.6425
2128.176 | 527.4392 | 225.0792 | 223.3802 | 219.7785
2129.176 | 523.5499 | 224.9079 | 223.4319 | 219.8464
2130.176 | 532.8154 | 224.7792 | 223.5486 | 219.8682
2131.176 | 536.6539 | 224.5352 | 223.7491 | 219.7378
2132.176 | 531.1091 | 224.4776 | 224.0758 | 219.5726
2133.176 | 535.6659 | 224.4583 | 224.1764 | 219.4161
2134.176 | 535.2021 | 224.3155 | 224.3674 | 219.2298
2135.176 | 528.3004 | 224.272 | 224.4814 | 218.9578
2136.176 | 542.9453 | 224.3524 | 224.4733 | 218.9904
2137.176 | 526.4844 | 224.3699 | 224.4486 | 218.9592
2138.176 | 533.6016 | 224.7697 | 224.4153 | 219.1184
2139.176 | 540.4848 | 225.1155 | 224.4272 | 219.0791
2140.176 | 548.9484 | 224.938 | 224.5304 | 219.5583
2141.176 | 539.9666 | 225.4053 | 224.8599 | 219.7484
2142.176 | 541.4442 | 225.4299 | 224.9548 | 219.5575
2143.176 | 534.4417 | 225.775 | 225.0186 | 219.6893
2144.176 | 544.2872 | 225.7332 | 225.3479 | 219.5496
2145.176 | 566.0351 | 225.8175 | 225.0414 | 219.6066
2146.176 | 548.6005 | 225.9267 | 224.806 | 219.8316
2147.176 | 540.6795 | 226.0026 | 224.5174 | 219.9298
2148.176 | 538.0061 | 225.8431 | 224.3836 | 220.018
2149.176 | 521.3047 | 225.7207 | 224.4368 | 220.0349
2150.176 | 517.4641 | 225.6476 | 224.2892 | 219.9265
2151.176 | 532.2794 | 225.6011 | 224.1211 | 220.0657
2152.176 | 527.5404 | 225.4934 | 223.8821 | 220.1694
2153.176 | 519.1631 | 225.5288 | 223.6962 | 220.0127
2154.176 | 526.5262 | 225.4196 | 223.563 | 219.7969
2155.176 | 526.5153 | 225.3559 | 223.3995 | 219.692
2156.176 | 518.9956 | 225.2408 | 223.3966 | 219.7909
2157.176 | 525.7831 | 225.1638 | 223.1963 | 219.7561
2158.176 | 530.0681 | 224.9428 | 223.0705 | 219.555
2159.176 | 520.6666 | 224.7195 | 223.0784 | 219.4535
2160.176 | 538.8595 | 224.4838 | 222.9338 | 219.4259
2161.176 | 549.2605 | 224.3791 | 222.7001 | 219.4365
2162.176 | 534.8997 | 224.1117 | 222.5854 | 219.7814
2163.176 | 538.9707 | 223.9149 | 222.5113 | 219.8112
2164.176 | 558.7117 | 223.9313 | 222.6662 | 219.9121
2165.176 | 554.4616 | 223.9146 | 222.709 | 220.0167
2166.176 | 550.4152 | 224.219 | 222.8998 | 220.4778
2167.176 | 577.4243 | 224.0852 | 223.2435 | 221.0438
2168.176 | 570.0197 | 224.5359 | 223.4714 | 221.3822
2169.176 | 573.4067 | 223.8532 | 223.5259 | 221.29
2170.176 | 574.1751 | 223.8108 | 223.5589 | 221.3106
2171.176 | 557.2593 | 223.8107 | 223.6221 | 221.3957
2172.176 | 571.2026 | 223.4738 | 223.6608 | 221.1244
2173.176 | 553.0591 | 223.2228 | 223.9158 | 220.7467
2174.176 | 561.7529 | 223.2252 | 223.8322 | 220.5359
2175.176 | 563.2883 | 223.3561 | 223.7467 | 220.5315
2176.176 | 559.5061 | 223.612 | 223.9211 | 220.5225
2177.176 | 581.8436 | 223.6452 | 223.9473 | 220.4239
2178.176 | 565.6711 | 223.8691 | 224.4704 | 220.6083
2179.176 | 559.7564 | 223.6714 | 224.3427 | 220.8878
2180.176 | 545.2756 | 223.6831 | 224.3792 | 221.2333
2181.176 | 544.9534 | 223.5359 | 224.4432 | 221.6959
2182.176 | 531.4271 | 223.8543 | 224.4126 | 221.994
2183.176 | 522.547 | 223.6548 | 224.388 | 222.0483
2184.176 | 520.0506 | 223.4428 | 224.4598 | 221.9194
2185.176 | 504.6205 | 223.1162 | 224.0341 | 221.6917
2186.176 | 498.37 | 223.1687 | 223.8891 | 221.5871
2187.176 | 490.5714 | 223.1039 | 223.7517 | 221.283
2188.176 | 486.8571 | 223.1074 | 223.7262 | 221.0378
2189.176 | 481.7914 | 222.7311 | 223.5688 | 220.8972
2190.176 | 474.9101 | 222.4873 | 223.6348 | 220.9757
2191.176 | 469.0452 | 222.4843 | 223.9507 | 221.1081
2192.176 | 459.813 | 222.4866 | 224.0463 | 221.2987
2193.176 | 456.2689 | 222.5218 | 223.9697 | 221.6239
2194.176 | 449.9058 | 222.2743 | 223.7849 | 221.2389
2195.176 | 454.3959 | 222.0438 | 223.6742 | 220.9389
2196.176 | 465.0764 | 222.0855 | 223.3476 | 220.8991
2197.176 | 460.3845 | 222.2816 | 223.0983 | 220.7907
2198.176 | 475.1671 | 222.2554 | 222.9851 | 220.5663
2199.176 | 469.5245 | 222.2199 | 222.9314 | 220.4864
2200.176 | 465.6917 | 222.2893 | 223.0619 | 220.4574
2201.176 | 468.2661 | 222.5066 | 222.9892 | 220.593
2202.176 | 464.3777 | 222.565 | 222.9279 | 220.5403
2203.176 | 456.3791 | 222.5532 | 222.8865 | 220.6081
2204.176 | 467.0726 | 222.7049 | 222.8242 | 220.7761
2205.176 | 470.5542 | 222.7879 | 222.6876 | 220.9362
2206.176 | 470.2003 | 222.5915 | 222.6176 | 220.9677
2207.176 | 484.1544 | 222.4241 | 222.4768 | 220.9508
2208.176 | 487.6102 | 222.419 | 222.271 | 220.8339
2209.176 | 504.854 | 222.441 | 222.1048 | 220.957
2210.176 | 525.7865 | 222.4816 | 221.8946 | 220.894
2211.176 | 532.7659 | 222.6144 | 221.6426 | 220.7187
2212.1917 | 534.275 | 222.526 | 221.4031 | 220.4952
2213.176 | 547.8501 | 222.4667 | 221.3734 | 220.3846
2214.176 | 558.6954 | 222.5678 | 221.2165 | 220.0766
2215.176 | 579.6491 | 222.6503 | 221.0972 | 219.7358
2216.176 | 564.4766 | 222.9441 | 221.1199 | 219.6025
2217.176 | 545.4692 | 223.1937 | 221.399 | 219.5132
2218.176 | 530.7046 | 223.3913 | 221.5002 | 219.4089
2219.176 | 534.0303 | 223.3227 | 221.4754 | 219.5342
2220.176 | 534.2236 | 223.4702 | 221.3567 | 219.8946
2221.176 | 539.8962 | 223.5817 | 221.2999 | 219.8014
2222.176 | 568.6158 | 223.7463 | 221.2559 | 219.4123
2223.176 | 570.6576 | 223.9656 | 221.3729 | 219.4738
2224.176 | 559.4271 | 224.1552 | 221.1759 | 218.944
2225.176 | 569.2966 | 224.4381 | 221.082 | 218.6432
2226.176 | 569.6429 | 224.5051 | 220.9567 | 218.6944
2227.176 | 550.9778 | 224.5591 | 220.79 | 218.7756
2228.176 | 550.6557 | 224.5957 | 220.8318 | 218.6641
2229.176 | 574.9305 | 224.7234 | 220.7707 | 219.1378
2230.176 | 568.5718 | 224.4729 | 220.9373 | 219.127
2231.176 | 551.2399 | 224.3691 | 220.9046 | 219.2652
2232.176 | 555.4503 | 224.4125 | 220.8866 | 219.4335
2233.176 | 560.7459 | 224.2935 | 220.7789 | 219.2885
2234.176 | 545.4855 | 224.097 | 220.6926 | 219.2891
2235.176 | 529.241 | 224.3358 | 220.7351 | 219.2991
2236.176 | 518.9956 | 224.3993 | 220.6928 | 219.3358
2237.176 | 505.3236 | 224.2376 | 220.5668 | 219.1368
2238.176 | 500.9327 | 224.039 | 220.5658 | 218.9249
2239.176 | 495.5075 | 223.979 | 220.5107 | 218.9182
2240.176 | 524.5946 | 223.9326 | 220.3691 | 218.8005
2241.176 | 514.2308 | 223.6354 | 220.2789 | 218.4716
2242.176 | 503.8893 | 223.4559 | 220.1771 | 218.3677
2243.176 | 520.0868 | 223.418 | 220.3847 | 218.5067
2244.176 | 517.6971 | 223.5922 | 220.781 | 218.9376
2245.176 | 525.7212 | 223.6058 | 220.7097 | 219.0341
2246.176 | 509.7909 | 223.5508 | 220.7033 | 218.9232
2247.176 | 498.6189 | 223.4388 | 220.8208 | 218.9095
2248.176 | 490.3652 | 223.5723 | 220.9278 | 218.8372
2249.176 | 482.9729 | 223.8863 | 220.909 | 219.1715
2250.176 | 475.9612 | 223.8338 | 220.9125 | 219.4061
2251.176 | 497.2456 | 223.9315 | 221.0106 | 219.7789
2252.176 | 495.2184 | 223.8597 | 221.2027 | 219.974
2253.176 | 514.0196 | 223.9781 | 221.4391 | 220.0691
2254.176 | 504.0012 | 223.9126 | 221.4084 | 220.0164
2255.176 | 517.6467 | 223.7423 | 221.1926 | 219.8946
2256.176 | 530.9802 | 223.844 | 220.9126 | 219.6764
2257.176 | 538.5554 | 224.1238 | 220.8292 | 219.4842
2258.176 | 533.6545 | 224.0392 | 220.6475 | 219.2957
2259.176 | 526.1703 | 224.0188 | 220.6141 | 219.1506
2260.176 | 513.6889 | 223.8441 | 220.6311 | 219.0148
2261.176 | 512.219 | 223.7283 | 220.5235 | 218.9655
2262.176 | 505.5056 | 223.6506 | 220.3995 | 218.9503
2263.176 | 524.9477 | 223.7319 | 220.3751 | 218.8473
2264.176 | 532.9072 | 223.6019 | 220.3548 | 218.6971
2265.176 | 524.5323 | 223.4918 | 220.2125 | 218.4269
2266.176 | 534.6624 | 223.425 | 220.3788 | 218.3182
2267.176 | 537.4921 | 223.7009 | 220.2712 | 218.7688
2268.176 | 535.2937 | 223.8717 | 220.2346 | 219.0075
2269.176 | 533.4887 | 223.8537 | 220.297 | 219.0246
2270.176 | 537.5927 | 224.047 | 220.7813 | 219.2976
2271.176 | 529.0245 | 224.125 | 220.8542 | 219.0586
2272.1917 | 511.5845 | 224.0379 | 220.9195 | 219.1149
2273.176 | 501.2755 | 223.8596 | 221.0129 | 218.9648
2274.176 | 489.7253 | 223.6976 | 221.0969 | 218.8936
2275.176 | 479.3201 | 223.4523 | 220.9228 | 218.7492
2276.176 | 466.715 | 223.0565 | 220.7338 | 218.7334
2277.176 | 457.0854 | 222.7551 | 220.5569 | 218.6214
2278.176 | 451.0521 | 222.5584 | 220.3123 | 218.359
2279.176 | 445.0056 | 222.4446 | 220.1295 | 218.3577
2280.176 | 444.4942 | 222.3123 | 220.0331 | 218.1327
2281.176 | 456.1846 | 222.2113 | 219.8687 | 217.8371
2282.176 | 465.6165 | 222.1782 | 219.9392 | 217.7625
2283.176 | 484.957 | 222.3574 | 219.9041 | 217.8438
2284.176 | 488.1872 | 222.521 | 220.0695 | 217.7093
2285.176 | 482.9372 | 222.7935 | 220.3766 | 217.6372
2286.176 | 482.2606 | 222.6822 | 220.8148 | 217.5038
2287.176 | 491.777 | 222.8106 | 220.7339 | 217.3586
2288.176 | 487.3949 | 222.6565 | 220.615 | 217.0215
2289.176 | 476.7733 | 222.5408 | 220.5209 | 216.7707
2290.176 | 483.0715 | 222.4733 | 220.3907 | 216.6078
2291.176 | 470.5921 | 222.3339 | 220.4333 | 216.3722
2292.176 | 479.4225 | 222.5143 | 220.4799 | 216.2083
2293.176 | 480.5577 | 222.3306 | 220.4109 | 215.8773
2294.176 | 482.8913 | 222.2028 | 220.2915 | 215.9856
2295.176 | 490.1743 | 222.2276 | 220.3016 | 215.8841
2296.176 | 498.0022 | 222.1754 | 220.2772 | 215.9287
2297.176 | 494.7511 | 222.3265 | 220.2808 | 215.9438
2298.176 | 504.4123 | 222.2276 | 220.3004 | 215.885
2299.176 | 504.5778 | 222.2824 | 220.226 | 215.8948
2300.176 | 519.2671 | 222.3187 | 220.4288 | 216.1412
2301.176 | 549.5577 | 222.3417 | 220.5019 | 216.1622
2302.176 | 545.0543 | 222.6426 | 220.4915 | 216.3454
2303.176 | 542.4412 | 222.935 | 220.4328 | 216.6262
2304.176 | 538.3912 | 223.1541 | 220.2768 | 216.813
2305.176 | 541.3068 | 223.2823 | 220.1181 | 217.0475
2306.176 | 529.8122 | 223.2141 | 219.9917 | 217.4901
2307.176 | 513.6181 | 223.3757 | 220.0118 | 217.4855
2308.176 | 498.8276 | 223.3927 | 220.2267 | 217.6289
2309.176 | 488.606 | 223.2979 | 220.3436 | 217.8724
2310.176 | 491.1409 | 223.6895 | 220.5795 | 217.905
2311.176 | 479.3564 | 223.5998 | 220.5128 | 218.1954
2312.176 | 469.9489 | 223.6051 | 220.5383 | 218.0762
2313.176 | 464.0571 | 223.6937 | 220.5619 | 218.1436
2314.176 | 460.7889 | 223.7183 | 220.4866 | 218.0284
2315.176 | 465.5437 | 223.7834 | 220.4053 | 217.9355
2316.176 | 466.216 | 223.6468 | 220.3563 | 217.7658
2317.176 | 484.1946 | 223.4789 | 220.2892 | 217.6132
2318.176 | 506.1645 | 223.6642 | 220.3218 | 217.6971
2319.176 | 503.0602 | 223.7337 | 220.2871 | 217.9291
2320.176 | 508.3248 | 224.0337 | 220.4815 | 217.8726
2321.176 | 508.7675 | 224.1592 | 220.4825 | 217.8886
2322.176 | 510.2259 | 223.8637 | 220.3203 | 218.1236
2323.176 | 529.7007 | 223.5943 | 220.3732 | 218.3917
2324.176 | 527.3819 | 223.512 | 220.3248 | 218.2408
2325.176 | 532.8699 | 223.2283 | 220.2571 | 218.2607
2326.176 | 538.9841 | 223.0965 | 220.2153 | 218.4118
2327.176 | 532.7495 | 223.23 | 220.1421 | 218.4629
2328.176 | 530.4579 | 223.4003 | 220.1515 | 218.4787
2329.176 | 530.6333 | 223.3921 | 220.1768 | 218.3995
2330.176 | 538.4529 | 223.287 | 220.2611 | 218.4174
2331.176 | 550.2543 | 223.4806 | 220.1399 | 218.4599
2332.176 | 553.0898 | 223.5693 | 220.0611 | 218.4201
2333.176 | 545.9876 | 223.4145 | 219.9842 | 218.0994
2334.176 | 534.6844 | 223.1619 | 220.0261 | 218.1646
2335.176 | 523.6384 | 222.9924 | 220.1168 | 218.0538
2336.176 | 519.4612 | 222.9372 | 220.0632 | 217.8463
2337.176 | 531.7035 | 222.982 | 220.0991 | 217.8509
2338.176 | 548.4359 | 222.8694 | 219.9349 | 218.0765
2339.176 | 542.416 | 222.7317 | 219.8918 | 218.3085
2340.176 | 553.6503 | 222.4358 | 219.7442 | 218.3959
2341.176 | 540.0257 | 222.1072 | 219.6069 | 218.3267
2342.176 | 547.1829 | 221.7958 | 219.4693 | 218.3293
2343.176 | 537.9452 | 221.695 | 219.4081 | 218.2511
2344.176 | 541.6511 | 221.5053 | 219.4244 | 218.0901
2345.176 | 539.0582 | 221.4602 | 219.3128 | 217.8248
2346.1917 | 537.169 | 221.5161 | 219.187 | 217.6128
2347.1917 | 543.4873 | 221.5315 | 219.0151 | 217.4297
2348.176 | 539.9276 | 221.3929 | 218.9443 | 217.7113
2349.176 | 525.2452 | 221.5103 | 219.0423 | 217.6669
2350.176 | 514.4628 | 221.7262 | 219.297 | 217.5601
2351.176 | 519.2544 | 221.9514 | 219.4252 | 217.565
2352.176 | 535.8307 | 222.195 | 219.5385 | 217.6461
2353.176 | 523.6486 | 222.292 | 219.5731 | 217.7528
2354.176 | 521.8864 | 222.2695 | 219.706 | 217.539
2355.176 | 514.2277 | 222.254 | 219.673 | 217.6304
2356.176 | 513.5936 | 222.0721 | 219.5733 | 217.8047
2357.176 | 523.0062 | 222.0638 | 219.4796 | 218.0558
2358.176 | 517.5636 | 221.8874 | 219.5327 | 218.0482
2359.176 | 522.9658 | 221.8849 | 219.5181 | 218.2275
2360.176 | 512.0763 | 221.6896 | 219.4678 | 218.2086
2361.176 | 503.6534 | 221.7664 | 219.3859 | 218.3551
2362.176 | 512.5149 | 221.7762 | 219.2588 | 218.4169
2363.176 | 526.7446 | 221.7652 | 219.3824 | 218.4615
2364.176 | 519.4922 | 221.7362 | 219.3947 | 218.4774
2365.176 | 533.0007 | 221.5832 | 219.4369 | 218.2954
2366.176 | 521.6562 | 221.4318 | 219.5713 | 218.5819
2367.176 | 512.6991 | 221.3013 | 219.6251 | 218.5097
2368.176 | 502.9602 | 221.4351 | 219.7248 | 218.7151
2369.176 | 498.4876 | 221.3143 | 219.6658 | 218.6568
2370.176 | 494.1241 | 221.2894 | 219.662 | 218.7758
2371.176 | 487.8838 | 221.5006 | 219.6183 | 218.7132
2372.176 | 495.2124 | 221.68 | 219.6778 | 218.5612
2373.176 | 491.8752 | 221.7865 | 219.6906 | 218.4066
2374.176 | 495.8199 | 221.7216 | 219.7457 | 218.277
2375.176 | 492.8794 | 221.5358 | 219.7793 | 218.1218
2376.176 | 490.7061 | 221.186 | 219.8313 | 218.0656
2377.176 | 490.4511 | 221.3101 | 220.0399 | 218.3228
2378.176 | 491.3729 | 221.4407 | 220.1905 | 218.1479
2379.176 | 508.1009 | 221.7085 | 220.2198 | 218.0196
2380.176 | 506.3738 | 221.6122 | 220.3208 | 218.1421
2381.176 | 513.4888 | 221.178 | 220.4047 | 218.1511
2382.176 | 513.6025 | 221.203 | 220.4407 | 218.263
2383.176 | 529.4827 | 221.3569 | 220.5203 | 218.5076
2384.176 | 528.3019 | 221.1469 | 220.627 | 218.4026
2385.176 | 537.9595 | 221.0568 | 220.7326 | 218.5681
2386.176 | 550.1919 | 220.8947 | 220.7081 | 218.5607
2387.176 | 553.6846 | 220.2692 | 220.6355 | 218.4291
2388.176 | 544.9673 | 220.4248 | 220.5885 | 218.6181
2389.176 | 550.0794 | 220.353 | 220.5665 | 218.3893
2390.176 | 551.9181 | 220.329 | 220.6806 | 218.2619
2391.176 | 550.9243 | 220.5102 | 220.78 | 218.1076
2392.176 | 533.5602 | 220.2781 | 220.7321 | 218.2079
2393.176 | 534.8623 | 220.357 | 220.7297 | 218.749
2394.176 | 548.385 | 220.4847 | 220.6838 | 218.9131
2395.176 | 543.5945 | 220.5493 | 220.7213 | 218.8987
2396.176 | 548.7556 | 220.8055 | 220.7818 | 219.1188
2397.176 | 545.1718 | 221.1018 | 220.7365 | 219.2691
2398.176 | 548.0188 | 221.0143 | 220.8167 | 219.6298
2399.176 | 546.6967 | 221.15 | 220.8858 | 219.5545
2400.176 | 534.5494 | 221.3111 | 220.8441 | 219.5332
2401.176 | 536.1467 | 221.578 | 220.9887 | 219.7693
2402.176 | 558.0973 | 221.6419 | 220.8483 | 219.9182
2403.176 | 554.179 | 221.7135 | 220.9077 | 220.0429
2404.176 | 544.9684 | 221.4447 | 220.7088 | 220.1882
2405.176 | 551.343 | 221.3755 | 220.6445 | 220.3796
2406.176 | 565.9748 | 221.482 | 220.4927 | 220.0629
2407.176 | 558.2195 | 221.504 | 220.3098 | 219.7014
2408.176 | 563.9913 | 221.3222 | 220.1265 | 219.4684
2409.176 | 569.7852 | 220.8719 | 219.9318 | 219.2459
2410.176 | 568.968 | 220.7822 | 219.7284 | 219.1088
2411.176 | 576.3206 | 220.6569 | 219.5207 | 218.928
2412.176 | 569.916 | 220.6292 | 219.2775 | 218.9191
2413.176 | 571.3693 | 220.6757 | 219.1252 | 219.016
2414.176 | 563.2398 | 220.83 | 219.0731 | 218.956
2415.176 | 542.4394 | 220.86 | 219.0309 | 219.289
2416.176 | 568.531 | 220.9081 | 219.15 | 219.3134
2417.176 | 561.2475 | 220.881 | 219.1606 | 219.7308
2418.176 | 553.7402 | 220.8801 | 219.362 | 219.7419
2419.176 | 568.3167 | 220.8328 | 219.2961 | 219.5568
2420.176 | 562.8723 | 220.8304 | 219.2301 | 219.4994
2421.176 | 542.615 | 220.9611 | 219.1011 | 219.3375
2422.176 | 529.4222 | 221.155 | 219.0361 | 219.3281
2423.176 | 529.2328 | 221.3782 | 218.8855 | 219.1064
2424.176 | 528.6639 | 221.389 | 218.8917 | 219.091
2425.176 | 536.2725 | 221.5025 | 218.9863 | 218.9628
2426.176 | 530.878 | 221.5712 | 219.0309 | 219.268
2427.176 | 528.3336 | 221.6827 | 219.1074 | 219.4374
2428.176 | 523.6444 | 221.8701 | 219.1551 | 219.8001
2429.176 | 529.2522 | 221.8102 | 219.2039 | 219.9379
2430.176 | 527.2812 | 221.7801 | 219.3962 | 219.7613
2431.176 | 520.1812 | 221.8723 | 219.4601 | 219.6349
2432.176 | 523.7012 | 222.1865 | 219.571 | 219.5733
2433.176 | 524.1968 | 222.138 | 219.5365 | 219.5046
2434.176 | 527.3453 | 222.1904 | 219.4999 | 219.4561
2435.176 | 526.5086 | 222.2451 | 219.4265 | 219.218
2436.176 | 519.895 | 222.2715 | 219.6608 | 219.0357
2437.176 | 516.0833 | 222.3351 | 219.5757 | 219.0289
2438.176 | 507.8968 | 222.4234 | 219.6534 | 218.7144
2439.176 | 499.4551 | 222.1847 | 219.9958 | 218.4694
2440.176 | 488.4708 | 222.0332 | 219.9698 | 218.5589
2441.176 | 506.4167 | 221.991 | 219.7856 | 218.6206
2442.176 | 498.1533 | 221.7291 | 219.6339 | 218.4978
2443.176 | 509.8946 | 221.5244 | 220.0932 | 218.393
2444.176 | 509.9439 | 221.5855 | 220.1325 | 218.3447
2445.176 | 510.9072 | 221.5527 | 220.1651 | 218.4719
2446.176 | 522.051 | 221.379 | 220.0044 | 218.625
2447.176 | 525.5681 | 221.3836 | 219.8532 | 218.5743
2448.176 | 541.3415 | 221.0802 | 219.6781 | 218.5366
2449.176 | 535.3758 | 220.7436 | 219.5904 | 218.3678
2450.176 | 537.2792 | 220.5324 | 219.4493 | 218.5315
2451.176 | 546.9857 | 220.5227 | 219.3153 | 218.5575
2452.176 | 547.3897 | 220.6537 | 219.1808 | 218.5473
2453.176 | 544.1345 | 220.7207 | 218.9971 | 218.5752
2454.176 | 533.8252 | 220.7895 | 218.9557 | 218.4064
2455.176 | 527.8583 | 220.9665 | 219.19 | 218.1452
2456.176 | 522.1998 | 221.1449 | 219.2368 | 218.051
2457.176 | 518.4373 | 221.5385 | 219.2436 | 218.344
2458.176 | 523.1035 | 221.6309 | 219.3861 | 218.3249
2459.176 | 537.6351 | 221.7675 | 219.6778 | 218.3643
2460.176 | 549.7336 | 221.9973 | 219.7352 | 218.4792
2461.176 | 542.8289 | 222.3512 | 219.7456 | 218.7171
2462.176 | 543.0468 | 222.5211 | 220.1033 | 218.8251
2463.176 | 552.0592 | 222.8994 | 220.3903 | 218.7925
2464.176 | 536.7481 | 222.8079 | 220.5984 | 218.8402
2465.176 | 540.8906 | 222.8413 | 220.7715 | 219.1828
2466.176 | 534.5671 | 223.1546 | 220.6156 | 219.438
2467.176 | 532.9994 | 223.3507 | 220.5452 | 219.7975
2468.176 | 536.4611 | 223.2815 | 220.5839 | 219.965
2469.176 | 535.3433 | 223.1062 | 220.5323 | 219.8498
2470.176 | 530.8792 | 223.0364 | 220.4271 | 219.622
2471.176 | 527.8645 | 223.1627 | 220.3841 | 219.4969
2472.176 | 525.8337 | 223.0878 | 220.3376 | 219.5671
2473.176 | 541.9388 | 223.028 | 220.2846 | 219.4353
2474.176 | 545.6482 | 222.9773 | 220.129 | 219.4778
2475.176 | 544.5853 | 222.7813 | 220.0875 | 219.8845
2476.176 | 546.5048 | 222.7615 | 220.0393 | 219.8381
2477.176 | 537.1865 | 222.7796 | 219.9283 | 219.4945
2478.176 | 534.6277 | 222.7338 | 219.887 | 219.2883
2479.176 | 527.3446 | 222.5249 | 219.6774 | 219.2463
2480.176 | 532.7974 | 222.2893 | 219.4701 | 219.3655
2481.176 | 538.9662 | 222.2452 | 219.345 | 219.243
2482.176 | 544.1484 | 222.1349 | 219.2323 | 219.0996
2483.176 | 546.8873 | 222.1193 | 219.1421 | 218.817
2484.176 | 540.9746 | 222.3472 | 219.0574 | 219.1048
2485.176 | 534.7441 | 222.4318 | 219.028 | 219.1248
2486.176 | 535.2266 | 222.672 | 219.0459 | 219.1443
2487.176 | 539.087 | 222.7241 | 219.1625 | 219.3339
2488.176 | 543.0732 | 222.6562 | 219.2635 | 219.3181
2489.176 | 535.5047 | 222.6243 | 219.3084 | 219.1518
2490.176 | 546.8856 | 222.6059 | 219.3911 | 219.1756
2491.176 | 550.9648 | 222.4793 | 219.482 | 219.3323
2492.176 | 551.0567 | 222.2613 | 219.4631 | 219.4576
2493.176 | 542.8589 | 222.1302 | 219.4653 | 219.3619
2494.176 | 541.2869 | 222.1606 | 219.4049 | 219.1201
2495.176 | 546.0693 | 222.2005 | 219.3895 | 219.2004
2496.176 | 540.109 | 222.3048 | 219.323 | 219.3176
2497.176 | 544.7159 | 222.4652 | 219.2582 | 219.1568
2498.176 | 547.9287 | 222.4035 | 219.1489 | 218.985
2499.176 | 537.4046 | 222.3172 | 219.2543 | 219.0112
2500.176 | 537.2266 | 222.2149 | 219.3892 | 219.1407
2501.176 | 534.3399 | 221.9269 | 219.3712 | 218.9273
2502.176 | 544.5124 | 221.6858 | 219.557 | 218.7251
2503.176 | 530.9253 | 221.2861 | 219.7691 | 218.6495
2504.176 | 523.8664 | 221.4362 | 219.6348 | 218.5616
2505.176 | 516.952 | 221.015 | 219.4915 | 218.5483
2506.176 | 531.4955 | 220.905 | 219.4749 | 218.2786
2507.176 | 520.1927 | 220.9058 | 219.4536 | 218.4167
2508.176 | 510.6588 | 220.8716 | 219.4356 | 218.272
2509.176 | 506.9133 | 220.9699 | 219.3847 | 218.4839
2510.176 | 495.6454 | 220.9989 | 219.4485 | 218.4605
2511.176 | 487.5669 | 221.0082 | 219.4565 | 218.5577
2512.176 | 487.0423 | 221.0462 | 219.476 | 218.3414
2513.176 | 501.6656 | 221.1167 | 219.433 | 218.0609
2514.176 | 496.2668 | 221.1961 | 219.2752 | 218.0592
2515.176 | 493.2056 | 221.1927 | 219.1688 | 218.0046
2516.176 | 502.1813 | 221.0213 | 219.1943 | 218.0643
2517.176 | 500.8029 | 221.0758 | 219.2858 | 218.012
2518.176 | 502.3593 | 221.0245 | 219.3636 | 218.0634
2519.176 | 506.712 | 221.1829 | 219.4095 | 218.1103
2520.176 | 498.1644 | 221.2631 | 219.5657 | 217.8662
2521.176 | 495.6502 | 221.1434 | 219.572 | 217.988
2522.176 | 489.2768 | 221.1499 | 219.6568 | 218.2338
2523.176 | 485.366 | 221.0576 | 219.8589 | 218.2516
2524.176 | 496.8401 | 220.9538 | 219.7738 | 218.0828
2525.176 | 489.4512 | 220.7606 | 219.7384 | 218.0561
2526.176 | 493.7113 | 220.5859 | 219.6656 | 217.9835
2527.176 | 489.8198 | 220.4528 | 219.6374 | 217.9391
2528.176 | 489.6616 | 220.6016 | 219.5757 | 217.9487
2529.176 | 483.8484 | 220.5012 | 219.518 | 217.762
2530.176 | 478.0041 | 220.3955 | 219.4977 | 217.6599
2531.176 | 473.0172 | 220.4755 | 219.6122 | 217.6063
2532.176 | 472.447 | 220.1003 | 219.5959 | 217.7183
2533.176 | 478.1494 | 219.9123 | 219.6449 | 218.0464
2534.176 | 496.4042 | 220.0316 | 219.7735 | 218.0776
2535.176 | 496.7777 | 219.9949 | 219.7956 | 217.9978
2536.176 | 490.3231 | 219.8271 | 219.9299 | 217.983
2537.176 | 498.9113 | 219.864 | 220.0088 | 218.0903
2538.176 | 500.6245 | 219.8653 | 220.2865 | 218.0761
2539.176 | 498.7411 | 220.3169 | 220.6265 | 218.0641
2540.176 | 492.2413 | 220.1257 | 221.0053 | 218.2256
2541.176 | 492.9942 | 220.0456 | 221.146 | 218.1143
2542.176 | 493.4349 | 220.1944 | 221.4233 | 218.0462
2543.176 | 493.7873 | 220.1096 | 221.4476 | 217.9701
2544.176 | 501.4675 | 220.003 | 221.6506 | 217.8727
2545.176 | 501.3018 | 219.6619 | 221.7425 | 217.8288
2546.176 | 508.8185 | 219.7395 | 221.7211 | 217.7671
2547.176 | 515.0288 | 219.8117 | 221.7146 | 218.0365
2548.176 | 515.1925 | 219.7838 | 221.8832 | 218.2303
2549.176 | 507.1578 | 219.9081 | 222.0107 | 218.055
2550.176 | 508.7238 | 220.0809 | 222.0562 | 218.0423
2551.176 | 507.8531 | 220.1885 | 222.0224 | 217.9975
2552.176 | 507.9691 | 219.8146 | 222.0004 | 217.9078
2553.176 | 502.5241 | 219.5772 | 221.9012 | 218.102
2554.176 | 497.5257 | 219.2752 | 221.9323 | 218.056
2555.176 | 502.8674 | 219.4314 | 221.9036 | 218.2082
2556.176 | 505.7747 | 219.4487 | 221.8343 | 218.1666
2557.176 | 505.9549 | 219.4043 | 221.7558 | 218.1787
2558.176 | 501.256 | 219.7347 | 221.7426 | 218.0791
2559.176 | 507.6 | 220.0411 | 221.78 | 218.1476
2560.176 | 502.3309 | 220.8393 | 221.9475 | 218.3916
2561.176 | 509.1768 | 221.1106 | 222.0907 | 218.1809
2562.176 | 505.6295 | 221.1677 | 221.9939 | 218.0958
2563.176 | 508.8555 | 221.1941 | 221.9615 | 218.3769
2564.176 | 505.9602 | 221.1692 | 222.0537 | 218.3064
2565.176 | 509.0768 | 221.1158 | 222.0933 | 218.2066
2566.176 | 510.613 | 221.0694 | 222.1041 | 218.1727
2567.176 | 520.2291 | 221.2197 | 222.058 | 218.0826
2568.176 | 511.7008 | 221.2605 | 222.0708 | 218.1955
2569.176 | 520.539 | 221.1218 | 222.1268 | 218.2446
2570.176 | 517.7093 | 221.2408 | 222.1057 | 218.172
2571.176 | 504.2473 | 221.3766 | 222.158 | 218.1609
2572.176 | 491.6875 | 221.4376 | 222.2293 | 218.3034
2573.176 | 483.0413 | 221.5419 | 222.2277 | 218.5371
2574.176 | 478.3244 | 221.232 | 222.3112 | 218.9854
2575.176 | 485.3542 | 221.2722 | 222.4578 | 218.9763
2576.176 | 496.7906 | 221.2792 | 222.6347 | 219.0578
2577.176 | 493.2287 | 221.2382 | 222.7602 | 219.0576
2578.176 | 503.3451 | 220.8792 | 222.7641 | 219.1083
2579.176 | 510.3165 | 220.9393 | 222.7583 | 218.9968
2580.176 | 506.6842 | 220.8036 | 222.8192 | 218.9256
2581.176 | 512.6229 | 220.8903 | 222.866 | 218.8865
2582.176 | 527.7518 | 220.7021 | 222.7052 | 218.7271
2583.176 | 525.264 | 220.3772 | 222.652 | 218.5952
2584.176 | 528.425 | 220.5757 | 222.6111 | 218.6563
2585.176 | 528.4713 | 220.6703 | 222.5388 | 218.5143
2586.176 | 526.1879 | 220.6067 | 222.5115 | 218.4331
2587.176 | 515.8009 | 220.3553 | 222.5642 | 218.5243
2588.176 | 507.1628 | 220.3714 | 222.5392 | 218.5711
2589.176 | 506.9072 | 220.3814 | 222.4709 | 218.6216
2590.176 | 511.3376 | 220.3082 | 222.4785 | 218.7807
2591.176 | 505.4792 | 220.3944 | 222.5335 | 219.1647
2592.176 | 501.2197 | 220.5694 | 222.551 | 219.222
2593.176 | 504.7299 | 220.5669 | 222.5511 | 219.6164
2594.176 | 498.2803 | 220.7146 | 222.5602 | 219.5848
2595.176 | 501.3446 | 220.8837 | 222.6224 | 219.7122
2596.176 | 501.9498 | 221.0677 | 222.6635 | 219.3843
2597.176 | 506.5714 | 221.302 | 222.6917 | 219.188
2598.176 | 508.8495 | 221.5666 | 222.7497 | 219.1737
2599.176 | 509.7914 | 221.6262 | 222.8022 | 219.4038
2600.176 | 508.7068 | 221.3626 | 222.724 | 219.6982
2601.176 | 507.9567 | 221.3171 | 222.5717 | 219.5015
2602.176 | 511.9294 | 221.0566 | 222.4189 | 219.405
2603.176 | 504.1165 | 220.9381 | 222.368 | 219.1212
2604.176 | 508.3265 | 220.6379 | 222.297 | 218.9779
2605.176 | 502.3452 | 220.6586 | 222.3049 | 218.6688
2606.176 | 494.1047 | 220.6692 | 222.3456 | 218.4536
2607.176 | 507.7304 | 220.5788 | 222.3115 | 218.3403
2608.176 | 507.361 | 220.4252 | 222.2269 | 218.3193
2609.176 | 512.7729 | 220.3388 | 222.1048 | 218.1858
2610.176 | 512.0302 | 220.0232 | 221.965 | 218.0664
2611.176 | 516.5654 | 220.0279 | 221.8207 | 217.8513
2612.176 | 518.0181 | 219.8791 | 221.6498 | 217.574
2613.176 | 512.6705 | 219.9789 | 221.6275 | 217.4374
2614.176 | 510.8739 | 219.956 | 221.5885 | 217.3746
2615.176 | 513.5468 | 219.837 | 221.4327 | 217.2473
2616.176 | 517.4167 | 219.7131 | 221.3542 | 217.5088
2617.176 | 507.0607 | 219.8571 | 221.1753 | 217.7741
2618.176 | 504.4905 | 219.8088 | 221.0896 | 217.8516
2619.176 | 497.6085 | 219.8583 | 220.9173 | 217.8879
2620.176 | 495.0463 | 219.824 | 220.8007 | 217.7963
2621.176 | 496.2717 | 219.7706 | 220.744 | 217.9179
2622.176 | 502.072 | 219.9299 | 220.5939 | 218.2155
2623.176 | 504.0867 | 219.8991 | 220.3978 | 218.6376
2624.176 | 500.0153 | 220.0038 | 220.3988 | 218.7449
2625.176 | 494.5487 | 220.0004 | 220.4586 | 218.8166
2626.176 | 494.9262 | 219.9862 | 220.5936 | 218.7046
2627.176 | 488.3048 | 219.8294 | 220.6626 | 218.6448
2628.176 | 492.7602 | 219.8562 | 220.7753 | 218.8537
2629.176 | 487.8252 | 219.7463 | 220.9199 | 218.7993
2630.176 | 485.0694 | 219.6051 | 220.9954 | 218.7656
2631.176 | 480.1597 | 220.1646 | 221.0706 | 219.0087
2632.176 | 476.4282 | 219.904 | 221.293 | 218.9538
2633.176 | 473.087 | 219.8672 | 221.4864 | 218.7972
2634.176 | 476.0924 | 219.8623 | 221.7315 | 219.0265
2635.176 | 476.1172 | 220.1011 | 221.8359 | 219.0679
2636.176 | 487.3243 | 220.1883 | 221.9764 | 219.091
2637.176 | 492.5832 | 220.1268 | 222.0703 | 219.1983
2638.176 | 492.1484 | 220.2945 | 222.2248 | 219.1017
2639.176 | 490.4646 | 220.2592 | 222.3095 | 219.1056
2640.176 | 483.7074 | 220.3571 | 222.3893 | 218.9397
2641.176 | 477.2812 | 220.3198 | 222.6157 | 218.9269
2642.176 | 481.7486 | 220.2246 | 222.6852 | 218.8398
2643.176 | 485.6906 | 220.2262 | 222.7634 | 218.9233
2644.176 | 486.8106 | 220.4377 | 222.9435 | 219.0479
2645.176 | 483.5797 | 220.4399 | 222.8512 | 218.9426
2646.176 | 487.2774 | 220.5648 | 222.8325 | 219.0184
2647.176 | 479.2915 | 220.5645 | 222.7817 | 219.2283
2648.176 | 472.3848 | 220.4955 | 222.7021 | 219.3914
2649.176 | 471.6909 | 220.6968 | 222.6282 | 219.3229
2650.176 | 464.0765 | 220.8711 | 222.4118 | 219.4055
2651.176 | 482.9742 | 220.9285 | 222.2122 | 219.7169
2652.176 | 478.9097 | 221.1864 | 222.2386 | 219.8709
2653.176 | 478.3742 | 221.3666 | 222.1902 | 219.9344
2654.176 | 476.7392 | 221.5235 | 222.072 | 219.8877
2655.176 | 474.9913 | 221.2097 | 222.039 | 220.0593
2656.176 | 481.8047 | 221.1428 | 221.8825 | 220.15
2657.176 | 481.703 | 221.1093 | 221.9052 | 220.2126
2658.176 | 484.3462 | 221.1156 | 221.6756 | 220.2977
2659.176 | 479.2218 | 221.1649 | 221.488 | 220.2946
2660.176 | 473.7759 | 221.1913 | 221.4167 | 220.1563
2661.176 | 471.7806 | 221.0494 | 221.3383 | 220.2267
2662.176 | 466.8816 | 221.0996 | 221.2689 | 220.462
2663.176 | 462.7586 | 221.014 | 221.2467 | 220.2859
2664.176 | 473.0794 | 220.8956 | 221.3306 | 220.1882
2665.176 | 479.3898 | 221.0735 | 221.4672 | 220.271
2666.176 | 482.3125 | 220.9029 | 221.3754 | 220.3112
2667.176 | 478.7729 | 220.8311 | 221.3946 | 220.0699
2668.176 | 478.2031 | 220.7264 | 221.3804 | 220.0618
2669.176 | 473.5395 | 220.7524 | 221.2956 | 220.2585
2670.176 | 468.6181 | 220.5179 | 221.1785 | 220.3563
2671.176 | 471.4809 | 220.4911 | 221.1055 | 220.2037
2672.176 | 478.6309 | 220.4991 | 220.8996 | 219.9732
2673.176 | 481.3054 | 220.4204 | 220.8114 | 219.998
2674.176 | 475.3669 | 220.4656 | 220.6758 | 219.963
2675.176 | 467.8883 | 220.2476 | 220.7138 | 220.0112
2676.176 | 466.646 | 220.3715 | 220.5281 | 220.3437
2677.176 | 463.3985 | 220.3218 | 220.4111 | 220.4298
2678.176 | 462.0593 | 220.1642 | 220.4235 | 220.6038
2679.176 | 457.0251 | 220.1148 | 220.4097 | 220.6791
2680.176 | 452.6544 | 219.8814 | 220.3267 | 220.6361
2681.176 | 449.0808 | 219.8462 | 220.3457 | 220.7061
2682.176 | 446.3011 | 219.6071 | 220.1087 | 220.4657
2683.176 | 449.394 | 219.4364 | 219.9112 | 220.4064
2684.176 | 454.2802 | 219.417 | 219.6404 | 220.4976
2685.176 | 453.4473 | 219.4082 | 219.4374 | 220.4949
2686.176 | 453.0285 | 219.5103 | 219.293 | 220.5472
2687.176 | 451.2661 | 219.6463 | 219.2049 | 220.5785
2688.176 | 450.755 | 219.8214 | 219.1592 | 220.3519
2689.176 | 456.7299 | 219.8549 | 219.1214 | 220.3198
2690.176 | 453.0672 | 220.1498 | 219.1694 | 220.0341
2691.176 | 447.1757 | 220.0739 | 219.1345 | 219.9266
2692.176 | 442.2913 | 220.2512 | 219.0288 | 219.7178
2693.176 | 441.7404 | 220.3656 | 218.936 | 219.457
2694.176 | 448.5256 | 220.3398 | 218.9059 | 219.3858
2695.176 | 448.7361 | 220.4143 | 218.8625 | 219.4001
2696.176 | 445.8995 | 220.3678 | 218.8513 | 219.2882
2697.176 | 459.7404 | 220.342 | 218.8469 | 219.4049
2698.176 | 458.7695 | 220.3263 | 218.8233 | 219.2615
2699.176 | 461.4021 | 220.2506 | 218.8532 | 219.1705
2700.176 | 463.3637 | 220.0454 | 218.7887 | 219.1342
2701.176 | 478.9698 | 220.0444 | 219.0448 | 219.2534
2702.176 | 486.9371 | 220.2649 | 219.4523 | 219.1504
2703.176 | 487.0622 | 220.219 | 219.4292 | 219.5021
2704.176 | 484.5424 | 220.3426 | 219.3606 | 219.3355
2705.176 | 488.7049 | 220.5016 | 219.2313 | 219.2602
2706.176 | 480.9933 | 220.6805 | 219.2375 | 219.194
2707.176 | 479.9565 | 220.6583 | 219.0283 | 219.1669
2708.176 | 479.9595 | 220.9532 | 219.0053 | 219.0112
2709.176 | 483.7856 | 221.1063 | 218.9568 | 218.8971
2710.176 | 496.5425 | 221.0821 | 219.1236 | 218.7688
2711.176 | 501.4954 | 220.9022 | 219.0285 | 218.7359
2712.176 | 500.7814 | 221.0391 | 218.9536 | 218.9841
2713.176 | 503.5171 | 221.0789 | 218.9168 | 219.0817
2714.176 | 506.7824 | 221.0301 | 218.823 | 218.83
2715.176 | 508.1891 | 220.6515 | 218.7597 | 218.6403
2716.176 | 509.5909 | 220.5423 | 218.7926 | 218.3733
2717.176 | 503.6625 | 220.5262 | 218.8163 | 218.2441
2718.176 | 500.4958 | 220.545 | 218.8677 | 218.2716
2719.176 | 509.3022 | 220.5095 | 218.8322 | 218.3438
2720.176 | 518.9768 | 220.2666 | 218.8716 | 218.2322
2721.176 | 515.0558 | 220.3227 | 218.9928 | 218.1965
2722.176 | 510.3677 | 220.322 | 219.0015 | 218.0651
2723.176 | 505.2816 | 220.2208 | 219.0878 | 218.1154
2724.176 | 502.9262 | 220.336 | 218.9546 | 218.1414
2725.176 | 497.5943 | 220.5692 | 218.9769 | 218.2283
2726.176 | 490.6309 | 220.7516 | 219.0094 | 218.3979
2727.176 | 485.7281 | 220.8729 | 219.0813 | 218.8051
2728.176 | 499.1178 | 221.2501 | 219.1164 | 219.1424
2729.176 | 494.4289 | 221.2648 | 219.1339 | 218.8547
2730.176 | 493.3077 | 221.0496 | 219.1222 | 218.6663
2731.176 | 492.03 | 220.7693 | 219.1998 | 218.6991
2732.176 | 491.7182 | 220.6916 | 219.1705 | 218.7113
2733.176 | 486.2157 | 220.5674 | 219.0847 | 218.6934
2734.176 | 491.2316 | 220.419 | 219.0934 | 218.6835
2735.176 | 493.2415 | 220.3073 | 219.0471 | 218.5545
2736.176 | 493.2655 | 220.1782 | 219.0915 | 218.4579
2737.176 | 489.4832 | 220.1232 | 219.1752 | 218.7129
2738.176 | 489.8123 | 219.9838 | 219.103 | 218.7276
2739.176 | 484.0238 | 219.9431 | 219.0773 | 218.7811
2740.176 | 483.9492 | 219.8738 | 219.1289 | 218.7955
2741.176 | 481.9269 | 219.6937 | 219.2198 | 218.7929
2742.176 | 484.6386 | 219.7881 | 219.2096 | 218.8813
2743.176 | 479.2649 | 219.5815 | 219.2042 | 218.9843
2744.176 | 480.6289 | 219.5093 | 219.1793 | 218.8908
2745.176 | 480.2312 | 219.2268 | 219.1893 | 218.7403
2746.176 | 486.2279 | 219.3331 | 219.2185 | 218.4893
2747.176 | 497.4891 | 219.4856 | 219.2391 | 218.4322
2748.176 | 506.7288 | 219.6753 | 219.2588 | 218.3564
2749.176 | 499.3299 | 219.9168 | 219.2522 | 218.5273
2750.176 | 499.7088 | 219.9839 | 219.273 | 218.6199
2751.176 | 493.5589 | 220.1393 | 219.3064 | 218.5531
2752.176 | 487.9905 | 220.0906 | 219.3715 | 218.4705
2753.176 | 484.5908 | 220.3354 | 219.328 | 218.4415
2754.176 | 485.0158 | 220.4667 | 219.3364 | 218.3036
2755.176 | 492.027 | 220.5439 | 219.3735 | 218.2393
2756.176 | 498.5881 | 220.53 | 219.2929 | 217.9623
2757.176 | 492.6061 | 220.4687 | 219.1669 | 217.6741
2758.176 | 489.8361 | 220.2816 | 219.1477 | 217.6095
2759.176 | 493.3915 | 220.1209 | 219.1495 | 217.7256
2760.176 | 491.2122 | 220.0871 | 219.2877 | 217.6787
2761.176 | 485.4285 | 220.1305 | 219.5068 | 217.9751
2762.176 | 490.6299 | 220.2045 | 219.4505 | 218.0606
2763.176 | 490.8625 | 220.1705 | 219.298 | 218.0752
2764.176 | 488.0124 | 220.3202 | 219.3096 | 218.2918
2765.176 | 489.9749 | 220.4015 | 219.3333 | 218.4603
2766.176 | 492.2001 | 220.5404 | 219.5058 | 218.7808
2767.176 | 489.4803 | 220.568 | 219.6078 | 218.9219
2768.176 | 491.197 | 220.758 | 219.6126 | 218.9297
2769.176 | 488.2331 | 220.8767 | 219.5743 | 218.8961
2770.176 | 482.0766 | 221.0065 | 219.567 | 218.7988
2771.176 | 482.4583 | 221.1048 | 219.6098 | 218.6665
2772.176 | 483.0395 | 221.359 | 219.7002 | 218.8222
2773.176 | 479.8667 | 221.5892 | 219.7705 | 219.0208
2774.176 | 478.1026 | 221.6067 | 219.8296 | 218.9484
2775.176 | 476.2121 | 221.7649 | 219.9056 | 219.045
2776.176 | 474.9009 | 221.9283 | 219.8866 | 219.0287
2777.176 | 474.4982 | 221.8803 | 219.8253 | 219.1713
2778.176 | 481.4455 | 221.9459 | 219.7735 | 219.5735
2779.176 | 478.6151 | 222.1438 | 219.9051 | 220.0297
2780.176 | 474.0849 | 222.1236 | 220.104 | 219.8359
2781.176 | 471.1187 | 222.0134 | 220.2309 | 220.2023
2782.176 | 465.7644 | 222.0985 | 220.3126 | 220.1965
2783.176 | 460.7687 | 222.1674 | 220.4618 | 220.0557
2784.176 | 465.2952 | 222.3368 | 220.6213 | 220.1721
2785.176 | 468.752 | 222.6999 | 220.8442 | 220.135
2786.176 | 468.4832 | 223.2035 | 221.2231 | 219.9797
2787.176 | 467.5146 | 223.8026 | 221.5433 | 220.2678
2788.176 | 465.1541 | 223.4922 | 222.096 | 220.236
2789.176 | 463.6268 | 223.4967 | 222.3589 | 220.4762
2790.176 | 468.6923 | 223.546 | 222.7348 | 221.7148
2791.176 | 468.8393 | 223.341 | 223.0237 | 221.8179
2792.176 | 469.1718 | 223.3876 | 223.2196 | 222.0605
2793.176 | 470.1694 | 223.1515 | 223.4289 | 222.01
2794.176 | 476.9562 | 223.4515 | 223.5522 | 221.77
2795.176 | 485.0486 | 223.396 | 223.5951 | 221.4452
2796.176 | 483.8474 | 223.1965 | 223.7852 | 221.2979
2797.176 | 483.6169 | 223.3385 | 223.7677 | 221.3306
2798.176 | 480.9154 | 222.9079 | 223.7691 | 221.1609
2799.176 | 484.2 | 222.7508 | 223.7292 | 221.1164
2800.176 | 490.5824 | 222.7892 | 223.8059 | 220.9565
2801.176 | 490.7278 | 222.9553 | 223.9094 | 220.8859
2802.176 | 485.8956 | 222.9077 | 223.8425 | 220.7344
2803.176 | 490.7821 | 222.979 | 223.7782 | 220.5372
2804.176 | 489.2676 | 223.0764 | 223.736 | 220.2708
2805.176 | 494.6017 | 222.968 | 223.757 | 220.2411
2806.176 | 498.5177 | 222.9048 | 223.5173 | 220.3388
2807.176 | 498.2327 | 222.9018 | 223.3823 | 220.3196
2808.176 | 497.5507 | 222.8459 | 223.2375 | 220.3165
2809.176 | 495.1285 | 222.7205 | 223.028 | 220.3452
2810.176 | 497.4318 | 222.6785 | 222.7897 | 220.4341
2811.176 | 496.0807 | 222.5918 | 222.7303 | 220.5333
2812.176 | 498.0183 | 222.7164 | 222.7314 | 220.5676
2813.176 | 503.0572 | 222.7382 | 222.6586 | 220.663
2814.176 | 498.4802 | 222.7295 | 222.8556 | 220.6708
2815.176 | 495.8468 | 222.8659 | 222.8206 | 220.7948
2816.176 | 495.2631 | 222.8835 | 222.8306 | 220.7713
2817.176 | 497.426 | 222.8991 | 223.0096 | 220.7464
2818.176 | 494.5135 | 222.9024 | 222.8576 | 220.6177
2819.176 | 487.7226 | 222.8381 | 222.8128 | 220.5432
2820.176 | 483.222 | 222.8929 | 222.7604 | 220.5693
2821.176 | 489.4482 | 223.0039 | 222.7889 | 220.6638
2822.176 | 483.4109 | 223.2217 | 222.8762 | 220.8065
2823.176 | 481.2321 | 223.3107 | 222.85 | 220.8033
2824.176 | 483.3503 | 223.1267 | 222.9347 | 220.8261
2825.176 | 484.4158 | 223.1698 | 223.0319 | 220.959
2826.176 | 480.4879 | 223.1068 | 222.9663 | 220.9771
2827.176 | 480.4411 | 223.2553 | 222.9356 | 220.8672
2828.176 | 483.0098 | 223.4136 | 223.1534 | 221.0406
2829.176 | 486.4889 | 223.5582 | 223.2284 | 221.0895
2830.176 | 490.4401 | 223.4754 | 223.3581 | 220.8564
2831.176 | 490.6949 | 223.4821 | 223.4229 | 220.678
2832.176 | 489.7666 | 223.4849 | 223.5605 | 220.55
2833.176 | 486.9082 | 223.2328 | 223.7397 | 220.4054
2834.176 | 485.817 | 223.3964 | 223.778 | 220.2834
2835.176 | 482.1196 | 223.5707 | 223.8916 | 220.2359
2836.176 | 491.9087 | 223.4084 | 224.1437 | 220.281
2837.176 | 493.038 | 223.3855 | 224.114 | 220.5473
2838.176 | 492.3296 | 223.3321 | 224.0803 | 220.5411
2839.176 | 504.3495 | 223.3181 | 224.0667 | 220.5467
2840.176 | 522.1846 | 223.4327 | 224.1173 | 220.9038
2841.176 | 519.5045 | 223.6824 | 224.0448 | 220.7706
2842.176 | 519.7851 | 223.7751 | 223.9 | 220.4866
2843.176 | 520.228 | 223.7507 | 223.9614 | 220.3098
2844.176 | 521.0541 | 223.6954 | 223.945 | 220.1467
2845.176 | 512.3709 | 223.6438 | 223.8804 | 220.0449
2846.176 | 505.6484 | 223.498 | 223.761 | 219.9681
2847.176 | 503.3613 | 223.421 | 223.7727 | 219.9315
2848.176 | 497.9455 | 223.4845 | 223.6376 | 220.117
2849.176 | 498.1667 | 223.4168 | 223.4969 | 220.1691
2850.176 | 502.1218 | 223.1981 | 223.2889 | 220.2596
2851.176 | 494.1639 | 223.0735 | 223.0595 | 220.0966
2852.176 | 494.3179 | 223.0814 | 222.9115 | 220.0245
2853.176 | 500.633 | 223.0016 | 222.8096 | 219.8195
2854.176 | 493.6112 | 223.1188 | 222.7787 | 219.7451
2855.176 | 485.2782 | 223.205 | 222.6943 | 219.7346
2856.176 | 479.3878 | 223.1705 | 222.7028 | 219.6879
2857.176 | 473.8053 | 223.1569 | 222.7602 | 219.7258
2858.176 | 473.6149 | 223.132 | 222.6424 | 220.1315
2859.176 | 471.9715 | 222.9015 | 222.6448 | 220.311
2860.176 | 472.2805 | 222.7259 | 222.6396 | 220.4572
2861.176 | 471.1773 | 222.9143 | 222.5979 | 220.6126
2862.176 | 467.4163 | 222.8725 | 222.6032 | 220.8453
2863.176 | 469.1858 | 222.8943 | 222.6215 | 221.2318
2864.176 | 472.9446 | 222.6685 | 222.5481 | 221.1073
2865.176 | 471.7894 | 222.6929 | 222.6742 | 221.0257
2866.176 | 467.6095 | 222.7524 | 222.7029 | 220.889
2867.176 | 466.9798 | 222.6017 | 222.7184 | 220.7508
2868.176 | 466.5623 | 222.7623 | 222.7676 | 220.6308
2869.176 | 464.266 | 222.761 | 222.8266 | 220.5331
2870.176 | 462.6113 | 222.6786 | 222.9853 | 220.5933
2871.176 | 460.8048 | 222.6647 | 223.0744 | 220.4674
2872.176 | 460.3047 | 222.6274 | 223.2584 | 220.4006
2873.176 | 460.5647 | 222.5805 | 223.5073 | 220.4417
2874.176 | 458.0501 | 222.4951 | 223.8376 | 220.6472
2875.176 | 454.3181 | 222.3411 | 224.0755 | 221.0482
2876.176 | 452.9718 | 222.2697 | 224.2804 | 221.4762
2877.176 | 450.4196 | 222.2143 | 224.4191 | 221.6715
2878.176 | 449.7897 | 222.1665 | 224.5732 | 221.6268
2879.176 | 457.958 | 221.8505 | 224.5951 | 221.6833
2880.176 | 456.4246 | 221.8337 | 224.7519 | 221.6065
2881.176 | 456.0213 | 221.8224 | 224.6976 | 221.6296
2882.176 | 457.7932 | 221.9683 | 224.7285 | 221.8166
2883.176 | 456.7474 | 221.9362 | 224.5682 | 221.742
2884.176 | 457.0043 | 221.9099 | 224.5381 | 221.6478
2885.176 | 459.0704 | 221.8719 | 224.2419 | 221.3477
2886.176 | 459.6514 | 221.8824 | 224.0273 | 221.0976
2887.176 | 455.8191 | 221.9855 | 223.9529 | 220.9413
2888.176 | 453.2691 | 221.9988 | 223.7617 | 220.7363
2889.176 | 451.7282 | 221.9715 | 223.4922 | 220.623
2890.176 | 454.5988 | 221.7933 | 223.3959 | 220.4917
2891.176 | 453.7742 | 221.8304 | 223.2049 | 220.5015
2892.176 | 452.3414 | 221.5803 | 222.9912 | 220.6319
2893.176 | 453.7839 | 221.3485 | 223.1207 | 220.8107
2894.176 | 455.2022 | 221.3952 | 223.3423 | 220.847
2895.176 | 461.2931 | 221.522 | 223.5359 | 221.0498
2896.176 | 464.399 | 221.4525 | 223.7676 | 221.2704
2897.176 | 468.097 | 221.8547 | 224.0086 | 221.2325
2898.176 | 481.4351 | 221.6485 | 224.2481 | 221.3595
2899.176 | 482.4038 | 221.5437 | 224.3599 | 221.4902
2900.176 | 492.45 | 221.4468 | 224.4664 | 221.5456
2901.176 | 493.6466 | 221.4191 | 224.5079 | 221.4807
2902.176 | 496.938 | 221.594 | 224.598 | 221.3864
2903.176 | 497.2029 | 221.9088 | 224.678 | 221.5478
2904.176 | 492.2876 | 222.1039 | 224.7755 | 221.957
2905.176 | 492.3379 | 222.2515 | 224.764 | 222.2481
2906.176 | 490.4293 | 222.6519 | 224.729 | 222.4218
2907.176 | 491.7603 | 222.6288 | 224.7175 | 222.2169
2908.176 | 487.5029 | 222.6375 | 224.8688 | 222.0719
2909.176 | 480.0221 | 222.7148 | 224.6772 | 222.1187
2910.176 | 475.1991 | 222.8683 | 224.5833 | 222.2358
2911.176 | 470.218 | 222.8741 | 224.4621 | 222.2435
2912.176 | 462.7756 | 222.9108 | 224.2875 | 222.3082
2913.176 | 458.3682 | 222.8165 | 224.1489 | 222.2907
2914.176 | 454.9847 | 222.7311 | 223.9953 | 222.224
2915.176 | 458.64 | 222.5779 | 223.976 | 222.3906
2916.176 | 462.2424 | 222.5261 | 223.8961 | 222.3367
2917.176 | 461.5412 | 222.4693 | 223.8834 | 222.2305
2918.176 | 465.7394 | 222.7026 | 223.769 | 222.2519
2919.176 | 470.8993 | 222.6018 | 223.6831 | 222.1553
2920.176 | 468.9551 | 222.6664 | 223.7915 | 222.2292
2921.176 | 469.974 | 222.7054 | 223.854 | 222.0474
2922.176 | 469.468 | 222.8727 | 223.8022 | 221.8205
2923.176 | 465.6886 | 222.8859 | 223.6796 | 221.7109
2924.176 | 466.9885 | 222.7352 | 223.7299 | 221.9021
2925.176 | 464.5653 | 222.6079 | 223.7638 | 221.6369
2926.176 | 464.6132 | 222.519 | 223.7548 | 221.5812
2927.176 | 466.9614 | 222.5015 | 223.5781 | 221.6161
2928.176 | 470.0901 | 222.6104 | 223.3871 | 221.5097
2929.176 | 482.475 | 222.7337 | 223.2889 | 221.301
2930.176 | 486.292 | 222.8366 | 223.1879 | 221.203
2931.176 | 491.6666 | 222.7556 | 223.1742 | 221.0111
2932.176 | 489.8106 | 222.8552 | 222.9844 | 221.0202
2933.176 | 488.0493 | 222.7171 | 222.8598 | 220.9299
2934.176 | 492.3751 | 222.8055 | 223.0101 | 220.9087
2935.176 | 490.3397 | 223.0791 | 223.115 | 220.841
2936.176 | 485.907 | 223.172 | 223.0196 | 220.8181
2937.176 | 489.2137 | 223.3631 | 223.1337 | 220.9828
2938.176 | 489.6784 | 223.4011 | 223.0888 | 221.2558
2939.176 | 490.5599 | 223.2947 | 223.0425 | 221.3661
2940.176 | 488.0799 | 223.2598 | 223.0008 | 221.5044
2941.176 | 482.8934 | 223.3014 | 223.0505 | 221.6948
2942.176 | 476.374 | 223.364 | 223.0088 | 221.8357
2943.176 | 472.9765 | 223.4303 | 223.1468 | 221.8755
2944.176 | 470.3655 | 223.3078 | 223.0019 | 222.0689
2945.176 | 469.8958 | 223.1365 | 222.942 | 222.1285
2946.176 | 470.4232 | 223.0782 | 223.1178 | 222.1756
2947.176 | 468.4329 | 222.8707 | 222.9559 | 222.3165
2948.176 | 463.4336 | 222.8533 | 222.7939 | 222.1254
2949.176 | 461.7035 | 222.9331 | 222.6637 | 222.0976
2950.176 | 460.0783 | 222.8277 | 222.6783 | 222.27
2951.176 | 461.4314 | 223.0124 | 222.7325 | 222.2637
2952.176 | 460.178 | 223.1565 | 222.7941 | 222.3057
2953.176 | 456.7679 | 223.3143 | 222.8488 | 222.2442
2954.176 | 453.9075 | 223.5612 | 222.8006 | 222.3295
2955.176 | 448.7667 | 223.585 | 222.8671 | 222.4307
2956.176 | 446.8975 | 223.7227 | 222.9103 | 222.3595
2957.176 | 445.8151 | 223.8285 | 222.8713 | 222.3424
2958.176 | 445.312 | 223.9308 | 222.8041 | 222.255
2959.176 | 441.4728 | 223.8098 | 222.8113 | 222.3744
2960.176 | 438.2868 | 223.7575 | 222.7266 | 222.4079
2961.176 | 436.9964 | 223.7615 | 222.6234 | 222.5208
2962.176 | 442.0759 | 223.6913 | 222.4992 | 222.4849
2963.176 | 445.2101 | 223.4498 | 222.4221 | 222.4904
2964.176 | 452.6601 | 223.2506 | 222.3802 | 222.3844
2965.176 | 449.7523 | 223.0933 | 222.5206 | 222.4319
2966.176 | 449.6724 | 222.8864 | 222.426 | 222.5351
2967.176 | 447.4988 | 222.7975 | 222.3239 | 222.45
2968.176 | 453.6365 | 222.9588 | 222.287 | 222.2084
2969.176 | 451.9187 | 222.9606 | 222.2817 | 222.0535
2970.176 | 449.9636 | 223.0325 | 222.1715 | 222.2587
2971.176 | 451.7642 | 222.8961 | 222.569 | 222.182
2972.176 | 452.0679 | 222.7364 | 222.4797 | 222.0585
2973.176 | 450.9896 | 222.8907 | 222.3353 | 221.924
2974.176 | 448.4098 | 222.7434 | 222.2057 | 221.9213
2975.1917 | 444.6591 | 222.5542 | 222.1474 | 221.8164
2976.1917 | 442.4914 | 222.488 | 222.1521 | 221.7793
2977.176 | 445.0304 | 222.5849 | 222.2262 | 221.7596
2978.176 | 450.6535 | 222.5281 | 222.2481 | 221.9838
2979.176 | 455.4901 | 222.5663 | 222.2852 | 222.1283
2980.176 | 458.3311 | 222.7617 | 222.1757 | 222.2778
2981.176 | 457.6121 | 222.8549 | 222.1537 | 222.4206
2982.176 | 456.7649 | 222.7558 | 222.3517 | 222.3431
2983.1917 | 455.6685 | 222.8234 | 222.2964 | 222.1676
2984.1917 | 453.9036 | 222.7825 | 222.2982 | 222.0081
2985.1917 | 455.3914 | 222.6656 | 222.3743 | 221.9494
2986.176 | 452.0721 | 222.4483 | 222.2615 | 221.9533
2987.176 | 450.2718 | 222.284 | 222.3077 | 221.8527
2988.176 | 443.2725 | 222.2205 | 222.3217 | 221.7078
2989.176 | 443.042 | 222.3292 | 222.2254 | 221.6053
2990.176 | 442.2153 | 222.373 | 222.2242 | 221.568
2991.176 | 438.0688 | 222.5462 | 222.3257 | 221.4798
2992.176 | 433.9673 | 222.7114 | 222.3426 | 221.3159
2993.176 | 430.0475 | 222.7807 | 222.2981 | 221.2552
2994.176 | 428.8001 | 223.0838 | 222.5189 | 221.2551
2995.176 | 428.7446 | 222.8727 | 222.5086 | 221.2218
2996.176 | 429.8872 | 222.8963 | 223.0433 | 221.272
2997.176 | 431.4944 | 223.0277 | 223.0701 | 221.3634
2998.176 | 438.263 | 223.1796 | 223.1293 | 221.5849
2999.176 | 437.3484 | 223.1753 | 223.1846 | 221.6414
3000.176 | 455.3192 | 223.478 | 223.2351 | 221.8492
3001.176 | 455.4385 | 223.4384 | 223.4039 | 221.8426
3002.176 | 454.8987 | 223.4674 | 223.5731 | 221.7625
3003.176 | 455.8367 | 223.5603 | 223.6705 | 221.7641
3004.176 | 454.3771 | 223.651 | 223.875 | 222.0798
3005.176 | 453.3932 | 223.6685 | 223.9484 | 221.9073
3006.176 | 455.8443 | 223.7903 | 224.2683 | 221.8888
3007.176 | 454.0992 | 223.8543 | 224.6238 | 221.8359
3008.176 | 457.3024 | 223.8637 | 224.9391 | 221.7908
3009.176 | 459.0954 | 223.8463 | 225.3063 | 221.8627
3010.176 | 458.8301 | 223.6385 | 225.3764 | 221.9207
3011.176 | 461.5709 | 223.3715 | 225.4493 | 222.1082
3012.176 | 461.9413 | 223.1337 | 225.4701 | 222.0858
3013.176 | 461.4937 | 223.0312 | 225.3714 | 222.109
3014.176 | 458.1349 | 223.137 | 225.3552 | 222.3417
3015.176 | 456.2341 | 223.1875 | 225.2504 | 222.0599
3016.176 | 454.8563 | 222.9837 | 225.2117 | 221.8484
3017.176 | 454.9635 | 222.7214 | 225.1682 | 222.0307
3018.176 | 456.4521 | 222.3483 | 225.1004 | 221.8853
3019.176 | 455.8423 | 222.2047 | 225.0013 | 222.0457
3020.176 | 456.0571 | 222.0739 | 224.9479 | 221.9583
3021.176 | 455.4364 | 222.2171 | 225.0073 | 221.8935
3022.176 | 453.3492 | 222.2032 | 224.9626 | 221.6986
3023.176 | 450.2386 | 222.2143 | 224.9576 | 221.5771
3024.176 | 449.3263 | 222.0927 | 224.916 | 221.5107
3025.176 | 448.3195 | 222.2707 | 225.0177 | 221.6824
3026.176 | 449.7659 | 222.3076 | 224.8798 | 221.8311
3027.176 | 448.6553 | 222.3608 | 224.7482 | 221.754
3028.176 | 446.5697 | 222.3859 | 224.7102 | 221.6975
3029.176 | 446.3414 | 222.3135 | 224.4863 | 221.5046
3030.176 | 453.2297 | 222.4691 | 224.2099 | 221.5088
3031.176 | 453.6746 | 222.4827 | 223.992 | 221.4379
3032.176 | 459.588 | 222.3876 | 223.8432 | 221.2725
3033.176 | 465.3308 | 222.1824 | 223.6892 | 220.9833
3034.176 | 463.9218 | 222.0744 | 223.5441 | 220.9683
3035.176 | 461.8416 | 222.0176 | 223.4252 | 220.9136
3036.176 | 461.1969 | 221.9253 | 223.3237 | 221.054
3037.176 | 459.5188 | 222.0793 | 223.2755 | 221.3955
3038.176 | 458.5198 | 222.3173 | 223.1005 | 221.4339
3039.176 | 459.9952 | 222.3517 | 223.0434 | 221.3447
3040.176 | 462.0045 | 222.3764 | 223.1279 | 221.6115
3041.176 | 459.511 | 222.4879 | 223.0238 | 221.7732
3042.176 | 461.5636 | 222.7113 | 222.9069 | 221.6923
3043.176 | 460.6567 | 222.7663 | 222.9012 | 221.6787
3044.176 | 456.3207 | 222.8467 | 223.1779 | 221.7279
3045.176 | 453.7937 | 223.1584 | 223.1958 | 221.7615
3046.176 | 450.9132 | 223.1613 | 223.1442 | 221.7149
3047.176 | 447.9602 | 223.1393 | 223.007 | 221.6392
3048.176 | 445.5956 | 223.0412 | 222.9249 | 221.6011
3049.176 | 443.1676 | 222.8527 | 222.7899 | 221.5282
3050.176 | 440.8103 | 222.6411 | 222.6345 | 221.6839
3051.176 | 441.4885 | 222.7537 | 222.5686 | 221.5528
3052.176 | 444.6845 | 222.6921 | 222.4788 | 221.5386
3053.176 | 444.4556 | 222.85 | 222.4734 | 221.61
3054.176 | 442.6744 | 222.7977 | 222.5564 | 221.6245
3055.176 | 439.1024 | 222.6799 | 222.6541 | 221.7991
3056.176 | 438.5326 | 222.5528 | 222.6481 | 222.0085
3057.176 | 444.2738 | 222.2972 | 222.8688 | 222.0702
3058.176 | 449.5605 | 222.114 | 222.6994 | 222.1369
3059.176 | 448.7334 | 222.1636 | 222.6556 | 222.193
3060.176 | 445.3749 | 222.1604 | 222.5665 | 222.2151
3061.176 | 443.2543 | 222.2219 | 222.4936 | 222.148
3062.176 | 444.6236 | 222.1844 | 222.7462 | 222.1477
3063.176 | 446.0636 | 222.1931 | 222.7974 | 222.3678
3064.176 | 449.2415 | 222.0931 | 222.8074 | 222.684
3065.176 | 452.5609 | 222.0938 | 222.7998 | 222.6031
3066.176 | 454.8624 | 222.1536 | 222.8866 | 222.6003
3067.176 | 458.0357 | 222.117 | 223.0437 | 222.5678
3068.176 | 458.4671 | 222.1531 | 223.2172 | 222.5263
3069.176 | 454.6212 | 222.1225 | 223.335 | 222.3932
3070.176 | 455.8864 | 221.939 | 223.331 | 222.3534
3071.176 | 454.3526 | 221.849 | 223.3392 | 222.3234
3072.176 | 454.34 | 221.7973 | 223.2996 | 222.2667
3073.176 | 451.301 | 221.6752 | 223.1207 | 222.1332
3074.176 | 449.8547 | 221.6158 | 223.1227 | 222.0275
3075.176 | 456.3307 | 221.6261 | 223.1275 | 222.0974
3076.176 | 460.5608 | 221.6457 | 223.2453 | 222.122
3077.176 | 461.6672 | 221.4702 | 223.3035 | 221.996
3078.176 | 465.8555 | 221.5414 | 223.4107 | 221.922
3079.176 | 468.8276 | 221.5347 | 223.4886 | 221.8646
3080.176 | 471.1906 | 221.9437 | 223.7365 | 221.8363
3081.176 | 469.9178 | 222.3898 | 223.8821 | 221.7695
3082.176 | 467.9765 | 222.5217 | 223.9556 | 221.8285
3083.176 | 466.1332 | 222.7078 | 223.9332 | 221.7981
3084.176 | 469.1885 | 223.0542 | 224.0278 | 221.8222
3085.176 | 468.8101 | 223.3248 | 224.036 | 221.8465
3086.176 | 476.3668 | 223.0416 | 224.0166 | 221.7982
3087.176 | 473.9101 | 222.9674 | 224.1296 | 221.9199
3088.176 | 470.5475 | 222.8586 | 224.34 | 221.8674
3089.176 | 467.2999 | 222.9231 | 224.5464 | 222.0461
3090.176 | 463.8371 | 222.9866 | 224.7382 | 222.251
3091.176 | 462.0429 | 223.1729 | 224.8349 | 222.213
3092.176 | 457.8478 | 223.0048 | 224.9552 | 222.3453
3093.176 | 457.3482 | 222.8666 | 224.9528 | 222.397
3094.176 | 455.0631 | 222.9557 | 224.9667 | 222.386
3095.176 | 459.3291 | 222.9206 | 224.8227 | 222.3633
3096.176 | 459.193 | 222.9763 | 224.7218 | 222.4114
3097.176 | 457.4418 | 222.8912 | 224.5536 | 222.4823
3098.176 | 454.2996 | 222.9542 | 224.5239 | 222.7951
3099.176 | 455.3627 | 223.0067 | 224.4804 | 222.7916
3100.176 | 456.0662 | 223.0572 | 224.4631 | 222.7674
3101.176 | 456.6831 | 222.9994 | 224.4125 | 222.8599
3102.176 | 458.9461 | 222.9606 | 224.3865 | 222.6966
3103.176 | 460.9318 | 223.0851 | 224.3188 | 222.8331
3104.176 | 459.6232 | 222.9885 | 224.1073 | 222.9752
3105.176 | 457.7885 | 222.919 | 223.9743 | 222.9692
3106.176 | 461.1338 | 223.0777 | 223.9005 | 223.0627
3107.176 | 461.7452 | 223.1502 | 223.8909 | 223.1652
3108.176 | 465.4401 | 223.2458 | 223.8553 | 223.3381
3109.176 | 473.9062 | 223.1757 | 223.8596 | 223.3097
3110.176 | 475.5584 | 223.1665 | 223.7874 | 223.4579
3111.176 | 477.8679 | 223.2081 | 223.7537 | 223.3815
3112.176 | 471.7896 | 223.4315 | 223.6542 | 223.3064
3113.176 | 469.1276 | 223.5652 | 223.5771 | 223.1341
3114.176 | 465.4209 | 223.3892 | 223.4928 | 223.0057
3115.176 | 467.5742 | 223.3274 | 223.5386 | 223.0885
3116.176 | 466.7118 | 223.1008 | 223.4632 | 223.245
3117.176 | 464.5407 | 223.168 | 223.4368 | 223.3132
3118.176 | 462.7758 | 223.0632 | 223.5951 | 223.2826
3119.176 | 460.1952 | 223.0587 | 223.3939 | 223.3084
3120.176 | 458.6849 | 222.9487 | 223.2713 | 223.2898
3121.176 | 456.9079 | 223.1039 | 223.2094 | 223.4366
3122.176 | 457.4581 | 223.1837 | 223.0514 | 223.2717
3123.176 | 458.9987 | 223.1199 | 222.9933 | 223.0478
3124.176 | 453.4609 | 223.0344 | 223.0536 | 223.203
3125.176 | 450.5027 | 223.0857 | 223.0848 | 223.1794
3126.176 | 449.2063 | 223.1177 | 223.1232 | 223.1701
3127.176 | 448.786 | 223.2158 | 223.1364 | 223.2012
3128.176 | 447.4191 | 223.1864 | 223.0224 | 223.0727
3129.176 | 447.1414 | 223.1779 | 222.9755 | 223.0534
3130.176 | 447.1128 | 223.0688 | 222.8647 | 223.1257
3131.176 | 448.0182 | 223.2405 | 222.6378 | 222.7723
3132.176 | 446.1362 | 223.4004 | 222.4772 | 222.8801
3133.176 | 446.5454 | 223.4612 | 222.3337 | 223.0585
3134.176 | 444.0931 | 223.2419 | 222.2592 | 223.0936
3135.176 | 441.4357 | 223.0616 | 222.2331 | 223.0334
3136.176 | 443.7482 | 223.0689 | 222.2295 | 223.0881
3137.176 | 444.9716 | 222.8192 | 222.2361 | 222.8499
3138.176 | 447.5475 | 222.8339 | 222.1915 | 222.8331
3139.176 | 445.2101 | 222.8566 | 222.1667 | 222.7602
3140.176 | 442.8901 | 222.9781 | 222.2205 | 222.9584
3141.176 | 440.8172 | 222.6763 | 222.1626 | 222.9505
3142.176 | 442.0432 | 222.6218 | 222.0943 | 222.84
3143.1917 | 440.8245 | 222.6925 | 222.1307 | 222.9203
3144.176 | 442.6107 | 222.5812 | 222.1196 | 222.9927
3145.176 | 439.5558 | 222.5332 | 222.1046 | 223.1654
3146.176 | 434.9603 | 222.5962 | 222.0368 | 223.1237
3147.176 | 430.4368 | 222.5298 | 222.0367 | 223.0678
3148.176 | 431.7391 | 222.5152 | 221.9668 | 222.9544
3149.176 | 433.621 | 222.5386 | 221.9089 | 222.9534
3150.176 | 432.1352 | 222.437 | 221.8115 | 222.9826
3151.176 | 435.3061 | 222.2579 | 221.8304 | 222.9626
3152.176 | 438.9316 | 222.2778 | 221.8795 | 222.7115
3153.176 | 439.9651 | 222.1266 | 221.8554 | 222.5723
3154.176 | 441.1585 | 222.0248 | 221.704 | 222.3764
3155.176 | 442.3631 | 222.1608 | 221.6129 | 222.2905
3156.176 | 446.6586 | 222.1209 | 221.6214 | 222.1182
3157.176 | 446.4291 | 222.1224 | 221.4818 | 222.1513
3158.176 | 444.9655 | 222.1808 | 221.3838 | 222.2807
3159.176 | 442.9762 | 222.1278 | 221.251 | 221.9591
3160.176 | 443.0519 | 221.9499 | 221.1868 | 221.6798
3161.176 | 442.0773 | 221.8429 | 221.2242 | 221.4809
3162.176 | 442.51 | 221.9678 | 221.1981 | 221.2958
3163.176 | 439.4412 | 222.123 | 221.257 | 221.6454
3164.176 | 437.3063 | 222.1624 | 221.245 | 221.5394
3165.176 | 437.2005 | 222.2829 | 221.3038 | 221.4706
3166.176 | 434.769 | 222.2689 | 221.485 | 221.6348
3167.176 | 432.5877 | 222.3063 | 221.5694 | 221.8541
3168.176 | 429.1324 | 222.3402 | 221.5075 | 221.7885
3169.176 | 430.5879 | 222.3019 | 221.4794 | 221.7262
3170.176 | 429.7731 | 222.2626 | 221.3329 | 221.731
3171.176 | 432.2315 | 222.1912 | 221.2764 | 221.707
3172.176 | 432.6958 | 222.2382 | 221.2639 | 221.4954
3173.1917 | 434.8673 | 222.1814 | 221.2369 | 221.2742
3174.176 | 440.1737 | 222.1372 | 221.2209 | 221.2019
3175.176 | 440.2638 | 222.3514 | 221.3629 | 221.2125
3176.176 | 443.5151 | 222.5146 | 221.358 | 221.2665
3177.176 | 443.4296 | 222.7205 | 221.3482 | 221.347
3178.176 | 441.7066 | 222.7337 | 221.2184 | 221.4025
3179.176 | 438.674 | 222.7045 | 221.1557 | 221.5452
3180.176 | 435.4341 | 222.6389 | 221.0664 | 221.5296
3181.176 | 430.6882 | 222.4818 | 220.9797 | 221.5115
3182.176 | 427.0243 | 222.2206 | 220.966 | 221.5282
3183.176 | 425.3508 | 222.0411 | 220.8196 | 221.7025
3184.176 | 423.9974 | 221.931 | 220.8121 | 221.7548
3185.176 | 422.816 | 221.8763 | 220.7322 | 221.6357
3186.176 | 424.9792 | 221.8243 | 220.6892 | 221.676
3187.176 | 427.8917 | 221.6951 | 220.6383 | 221.4322
3188.176 | 428.4046 | 221.4017 | 220.6746 | 221.3648
3189.176 | 431.6661 | 221.2216 | 220.6194 | 221.4076
3190.176 | 431.9021 | 221.1408 | 220.5521 | 221.2998
3191.176 | 436.6238 | 221.1837 | 220.5441 | 221.1209
3192.176 | 440.8235 | 221.5701 | 220.4269 | 221.0438
3193.176 | 442.109 | 221.6748 | 220.4135 | 220.9749
3194.176 | 444.866 | 221.9141 | 220.4626 | 221.0221
3195.176 | 445.5306 | 222.0107 | 220.2732 | 220.7887
3196.176 | 449.5884 | 222.0059 | 220.3292 | 220.6853
3197.176 | 454.0834 | 222.2441 | 220.2744 | 220.761
3198.176 | 453.0177 | 222.3049 | 220.2169 | 220.6962
3199.176 | 451.1795 | 222.41 | 220.3494 | 220.7983
3200.176 | 453.4161 | 222.3571 | 220.4153 | 221.1026
3201.176 | 451.9316 | 222.3897 | 220.4327 | 221.2522
3202.176 | 453.8822 | 222.3019 | 220.403 | 221.1604
3203.1917 | 453.7913 | 222.2555 | 220.3896 | 221.3194
3204.176 | 450.192 | 222.3416 | 220.392 | 221.5783
3205.176 | 448.5319 | 222.4929 | 220.3105 | 221.4986
3206.176 | 445.0059 | 222.5468 | 220.2474 | 221.3451
3207.176 | 442.8371 | 222.485 | 220.3737 | 221.072
3208.176 | 439.8577 | 222.3396 | 220.3212 | 220.9843
3209.176 | 441.6076 | 222.1058 | 220.251 | 220.8488
3210.176 | 440.7811 | 222.0639 | 220.2218 | 220.5289
3211.176 | 439.4703 | 221.8897 | 220.1965 | 220.4097
3212.176 | 436.6173 | 221.5952 | 220.1113 | 220.3568
3213.176 | 436.1398 | 221.3818 | 220.0423 | 220.4806
3214.176 | 433.8213 | 221.352 | 220.0543 | 220.6521
3215.176 | 432.1387 | 221.2456 | 219.9614 | 220.5979
3216.176 | 432.7156 | 221.1443 | 219.8332 | 220.7101
3217.176 | 431.4475 | 221.1923 | 219.689 | 220.9111
3218.176 | 436.2179 | 220.8836 | 219.589 | 220.9779
3219.176 | 438.1992 | 220.6758 | 219.5875 | 221.0593
3220.176 | 439.3376 | 220.3612 | 219.5887 | 220.8274
3221.176 | 439.27 | 220.3752 | 219.658 | 220.8348
3222.176 | 437.2005 | 220.477 | 219.5873 | 220.8747
3223.176 | 435.0515 | 220.8693 | 219.5615 | 221.0325
3224.176 | 432.3459 | 220.9886 | 219.5851 | 221.1102
3225.176 | 431.4915 | 221.0052 | 219.7244 | 221.0932
3226.2229 | 430.6644 | 220.9365 | 219.9995 | 220.9867
3227.176 | 430.8366 | 220.836 | 220.1455 | 220.7893
3228.176 | 430.0826 | 220.7457 | 220.2777 | 220.6011
3229.176 | 424.2246 | 220.5782 | 220.3465 | 220.4427
3230.176 | 424.4636 | 220.6583 | 220.3454 | 220.2601
3231.176 | 423.4925 | 220.728 | 220.2839 | 220.0747
3232.176 | 423.1168 | 220.722 | 220.192 | 220.0105
3233.1917 | 422.1389 | 220.4467 | 220.2946 | 220.0698
3234.176 | 418.2484 | 220.5999 | 220.3876 | 220.051
3235.176 | 415.695 | 220.7951 | 220.4779 | 220.1243
3236.176 | 415.0723 | 220.8856 | 220.6475 | 220.5084
3237.176 | 415.2326 | 221.0297 | 220.764 | 220.4349
3238.176 | 417.8067 | 221.1519 | 220.979 | 220.556
3239.176 | 413.7345 | 221.3611 | 221.1764 | 220.507
3240.176 | 409.5593 | 221.3897 | 221.3345 | 220.8403
3241.176 | 411.9878 | 221.878 | 221.3931 | 221.0299
3242.176 | 412.0991 | 221.9538 | 221.9972 | 221.2429
3243.176 | 412.7288 | 221.9726 | 222.1628 | 221.752
3244.176 | 409.759 | 222.3626 | 222.3109 | 221.6545
3245.176 | 407.9418 | 222.5844 | 222.6209 | 221.9614
3246.176 | 408.0427 | 222.4628 | 222.987 | 221.9866
3247.176 | 411.8686 | 222.6244 | 223.5004 | 222.0332
3248.176 | 411.3034 | 222.7697 | 223.9344 | 221.9364
3249.176 | 414.0128 | 222.6431 | 224.4182 | 222.3209
3250.176 | 415.2938 | 222.9716 | 224.7585 | 222.4743
3251.176 | 412.9511 | 222.9001 | 225.0827 | 222.6919
3252.176 | 413.0384 | 222.8793 | 225.5573 | 222.9401
3253.176 | 413.7866 | 223.0608 | 225.9603 | 223.1414
3254.176 | 412.5945 | 223.6325 | 226.0842 | 223.6976
3255.176 | 412.0864 | 223.4376 | 226.2816 | 223.6272
3256.176 | 413.484 | 223.4227 | 226.3612 | 223.5803
3257.176 | 412.5051 | 223.5082 | 226.6745 | 223.7523
3258.176 | 408.3503 | 223.4528 | 226.6703 | 223.6616
3259.176 | 404.82 | 223.318 | 226.5802 | 223.5893
3260.176 | 403.1024 | 223.4261 | 226.6226 | 223.6977
3261.176 | 401.4682 | 223.2902 | 226.5647 | 223.7251
3262.176 | 402.301 | 223.5409 | 226.7188 | 223.7506
3263.176 | 406.0059 | 223.5411 | 226.7867 | 223.7814
3264.176 | 407.6281 | 223.3967 | 226.8844 | 224.0622
3265.176 | 409.7531 | 223.1816 | 226.9219 | 224.2102
3266.176 | 411.0651 | 223.0062 | 227.0727 | 224.3389
3267.176 | 410.9452 | 223.063 | 227.3097 | 224.1409
3268.176 | 410.6168 | 223.1313 | 227.3254 | 224.1569
3269.176 | 408.6895 | 222.9693 | 227.3336 | 224.1771
3270.176 | 404.2331 | 222.9254 | 227.377 | 224.0652
3271.1917 | 406.8227 | 222.8165 | 227.4989 | 223.8722
3272.176 | 407.6976 | 222.7888 | 227.519 | 223.9634
3273.176 | 410.481 | 222.7296 | 227.4111 | 223.8559
3274.1917 | 412.7064 | 222.6994 | 227.3171 | 223.985
3275.1917 | 417.6005 | 222.644 | 227.2971 | 224.0337
3276.176 | 421.7512 | 222.5626 | 227.239 | 223.9494
3277.176 | 423.2678 | 222.4943 | 227.2886 | 223.9358
3278.176 | 426.2969 | 222.4018 | 227.3437 | 223.9612
3279.176 | 427.7809 | 222.5383 | 227.299 | 224.0282
3280.176 | 432.1214 | 222.8877 | 227.44 | 224.4535
3281.176 | 434.3361 | 222.9817 | 227.4186 | 224.3416
3282.176 | 433.027 | 222.9839 | 227.4277 | 224.4795
3283.176 | 435.2902 | 222.8412 | 227.3914 | 224.3341
3284.176 | 437.4359 | 222.6893 | 227.3198 | 224.3814
3285.176 | 435.9269 | 222.7698 | 227.1505 | 224.2275
3286.176 | 435.0154 | 222.7352 | 227.0224 | 223.9923
3287.176 | 430.5115 | 222.8726 | 226.9272 | 223.896
3288.176 | 429.7691 | 223.1293 | 226.8427 | 223.7355
3289.176 | 431.2433 | 223.0388 | 226.7215 | 223.6926
3290.176 | 431.0302 | 223.1594 | 226.8088 | 223.7798
3291.176 | 434.4997 | 223.2055 | 226.7881 | 223.7928
3292.176 | 438.8865 | 223.1254 | 226.6707 | 223.6145
3293.1917 | 441.9679 | 222.9704 | 226.6099 | 223.4517
3294.176 | 443.3318 | 223.1321 | 226.609 | 223.3313
3295.176 | 442.4675 | 222.9855 | 226.5057 | 223.4308
3296.176 | 445.1705 | 223.0001 | 226.556 | 223.5433
3297.176 | 444.8776 | 222.9466 | 226.5831 | 223.6415
3298.176 | 444.1202 | 222.9809 | 226.5297 | 223.557
3299.176 | 442.6468 | 223.0055 | 226.4505 | 223.4393
3300.176 | 443.0834 | 223.0417 | 226.3139 | 223.2128
3301.176 | 445.8345 | 223.057 | 226.1509 | 223.0738
3302.176 | 447.9229 | 222.9158 | 225.9064 | 223.0647
3303.176 | 451.1271 | 223.1012 | 225.7336 | 222.9473
3304.176 | 449.9544 | 223.2725 | 225.6355 | 222.8808
3305.176 | 451.0538 | 223.3925 | 225.4835 | 222.8882
3306.176 | 445.8557 | 223.5283 | 225.3672 | 223.0412
3307.176 | 439.331 | 223.5557 | 225.2843 | 222.9868
3308.176 | 436.3968 | 223.5432 | 225.243 | 223.1239
3309.176 | 435.1536 | 223.2686 | 225.0949 | 223.1777
3310.176 | 432.1915 | 223.3145 | 224.9106 | 223.1603
3311.176 | 432.8339 | 223.2544 | 224.7292 | 223.1808
3312.176 | 431.6876 | 223.2747 | 224.6836 | 223.1507
3313.176 | 439.8425 | 223.5665 | 224.804 | 223.427
3314.176 | 443.9632 | 223.7808 | 224.9638 | 223.5369
3315.176 | 450.073 | 224.0107 | 225.2532 | 223.9952
3316.176 | 454.7311 | 224.3163 | 225.4119 | 224.1814
3317.176 | 456.4248 | 224.775 | 225.5257 | 224.4346
3318.176 | 459.4165 | 225.2212 | 225.7013 | 224.8676
3319.176 | 463.3578 | 225.4065 | 226.1643 | 225.313
3320.176 | 469.2205 | 225.7302 | 226.6382 | 226.1466
3321.176 | 471.5064 | 225.8937 | 227.2228 | 227.1227
3322.176 | 471.8367 | 226.2382 | 227.7758 | 227.7027
3323.176 | 469.9471 | 226.8119 | 228.362 | 228.5168
3324.176 | 465.1764 | 227.4921 | 228.8784 | 229.0818
3325.176 | 459.9743 | 228.1909 | 229.3775 | 229.3942
3326.176 | 456.4379 | 228.9502 | 229.9094 | 230.3478
3327.176 | 460.283 | 229.3509 | 230.4296 | 230.9549
3328.176 | 456.7777 | 229.6673 | 231.1278 | 231.0365
3329.176 | 451.082 | 229.9956 | 231.7119 | 231.2834
3330.176 | 449.005 | 231.0645 | 232.1977 | 231.8906
3331.176 | 449.5015 | 231.8449 | 233.1476 | 232.392
3332.176 | 448.9192 | 232.6514 | 233.8612 | 232.7559
3333.176 | 447.4288 | 233.2205 | 234.4756 | 232.8539
3334.176 | 448.1939 | 233.6581 | 234.9382 | 232.9619
3335.176 | 446.1402 | 234.1707 | 235.4202 | 232.9199
3336.176 | 445.6126 | 234.5312 | 235.8713 | 232.9424
3337.176 | 443.6626 | 234.8851 | 236.5334 | 233.1062
3338.176 | 447.2091 | 235.3516 | 237.2531 | 233.5288
3339.176 | 447.6848 | 236.2442 | 237.6652 | 234.5008
3340.176 | 444.3162 | 236.6903 | 238.1369 | 234.6674
3341.176 | 443.9985 | 237.1287 | 238.6344 | 234.7316
3342.176 | 446.2838 | 237.4172 | 238.9322 | 235.0379
3343.176 | 445.9862 | 237.8514 | 239.1226 | 235.7147
3344.176 | 448.9305 | 237.7375 | 239.1993 | 236.1118
3345.176 | 450.3157 | 238.0306 | 239.3815 | 236.4069
3346.176 | 451.9505 | 238.1954 | 239.4894 | 236.7537
3347.176 | 447.8766 | 238.8037 | 239.7133 | 236.8222
3348.176 | 449.8574 | 239.0671 | 240.0567 | 237.0203
3349.176 | 451.8674 | 239.3938 | 240.4918 | 237.2333
3350.176 | 454.5371 | 239.2422 | 240.5303 | 237.1499
3351.176 | 451.4364 | 239.2428 | 240.6637 | 237.0866
3352.176 | 450.309 | 239.5316 | 240.8364 | 237.1587
3353.176 | 451.7313 | 239.676 | 241.4452 | 237.3222
3354.176 | 450.1041 | 239.935 | 241.7626 | 237.5549
3355.176 | 447.5675 | 240.3078 | 242.1505 | 237.8884
3356.176 | 447.5102 | 240.7514 | 242.8473 | 238.2562
3357.176 | 450.5167 | 240.8891 | 243.0268 | 238.4815
3358.176 | 452.9648 | 241.1353 | 243.7769 | 238.5946
3359.176 | 450.3172 | 241.6401 | 244.1474 | 238.881
3360.176 | 452.068 | 241.9335 | 244.33 | 239.0502
3361.176 | 450.7758 | 242.4268 | 244.7175 | 239.2107
3362.176 | 449.8043 | 242.7901 | 245.11 | 239.051
3363.176 | 450.5397 | 242.8259 | 245.551 | 239.1442
3364.176 | 449.224 | 243.2993 | 245.9606 | 239.0145
3365.176 | 448.0571 | 243.5742 | 246.1461 | 239.3227
3366.176 | 450.4243 | 243.5132 | 246.3748 | 239.3723
3367.176 | 448.4925 | 243.4556 | 246.5574 | 239.6474
3368.176 | 447.2853 | 243.7177 | 246.8351 | 239.6524
3369.176 | 451.3733 | 243.8665 | 247.057 | 239.7924
3370.176 | 455.0836 | 243.8426 | 247.3217 | 239.8775
3371.176 | 458.0913 | 244.0602 | 247.5699 | 239.8559
3372.176 | 457.5114 | 244.4818 | 247.9117 | 240.0725
3373.176 | 457.809 | 244.8711 | 247.9797 | 240.0938
3374.176 | 454.5861 | 244.965 | 248.0826 | 240.6416
3375.176 | 452.7944 | 244.9695 | 248.1545 | 241.3849
3376.176 | 455.5789 | 244.8858 | 248.2394 | 242.1516
3377.176 | 454.1358 | 244.8218 | 248.1804 | 242.6792
3378.176 | 459.111 | 244.9655 | 248.2366 | 242.8603
3379.176 | 465.882 | 244.8477 | 248.0462 | 242.876
3380.176 | 472.6181 | 245.1875 | 248.1773 | 243.2369
3381.176 | 473.4412 | 245.4518 | 248.1179 | 243.577
3382.176 | 478.0274 | 245.8227 | 248.3418 | 244.1968
3383.176 | 480.5503 | 246.365 | 248.7783 | 244.8788
3384.176 | 481.8141 | 246.9562 | 249.1881 | 245.1028
3385.176 | 484.0181 | 246.9802 | 249.5131 | 245.7612
3386.176 | 488.0171 | 247.0578 | 250.0406 | 246.3357
3387.176 | 488.8899 | 247.5732 | 250.2493 | 246.7508
3388.176 | 486.0651 | 248.0549 | 250.2693 | 247.2533
3389.176 | 482.6937 | 248.6596 | 250.3727 | 247.6337
3390.176 | 482.6056 | 249.3564 | 250.5159 | 248.6031
3391.176 | 481.919 | 249.8207 | 250.9331 | 249.0603
3392.176 | 484.2637 | 250.3729 | 251.4236 | 249.7482
3393.176 | 483.3297 | 250.6137 | 251.8379 | 249.9265
3394.176 | 483.3564 | 251.2314 | 252.4687 | 250.5196
3395.176 | 487.3451 | 251.9331 | 252.937 | 251.5648
3396.176 | 488.3002 | 252.774 | 253.2169 | 252.1724
3397.176 | 494.3332 | 253.2034 | 253.2831 | 252.7221
3398.176 | 503.6868 | 253.8312 | 253.8302 | 253.4809
3399.176 | 508.4405 | 254.8171 | 254.9847 | 253.7037
3400.176 | 511.7594 | 255.6132 | 255.2573 | 254.1398
3401.176 | 518.9405 | 256.6121 | 255.7886 | 255.1426
3402.176 | 523.2163 | 257.7306 | 256.3063 | 256.2145
3403.176 | 529.5435 | 258.3662 | 256.7816 | 257.4443
3404.176 | 535.2816 | 258.6054 | 256.9761 | 257.7003
3405.176 | 543.6322 | 259.0583 | 257.4102 | 258.3144
3406.176 | 552.6559 | 259.6066 | 257.6695 | 258.803
3407.176 | 550.6952 | 260.2038 | 258.6261 | 259.5695
3408.176 | 549.7894 | 260.7972 | 259.1113 | 260.2484
3409.176 | 545.5634 | 261.6268 | 259.5708 | 261.1998
3410.176 | 535.6743 | 261.9552 | 259.7592 | 261.7698
3411.176 | 529.7068 | 262.531 | 260.0582 | 262.5755
3412.176 | 526.9814 | 262.6624 | 260.6669 | 262.8411
3413.176 | 526.5889 | 263.0108 | 260.8156 | 262.7387
3414.176 | 521.5406 | 264.106 | 261.2134 | 262.3762
3415.176 | 519.1545 | 264.0447 | 261.6516 | 262.3395
3416.176 | 516.0524 | 264.7512 | 261.9956 | 262.2096
3417.176 | 515.6262 | 265.0656 | 262.2488 | 262.0225
3418.176 | 509.2109 | 266.095 | 262.3356 | 262.1558
3419.176 | 510.425 | 266.5703 | 262.6083 | 262.3618
3420.176 | 515.9613 | 266.6599 | 262.629 | 262.5235
3421.176 | 516.5772 | 266.6053 | 262.6738 | 262.2417
3422.176 | 512.0662 | 266.7278 | 262.7332 | 262.1601
3423.176 | 511.8571 | 266.8987 | 262.9717 | 262.6699
3424.176 | 517.5469 | 267.2528 | 262.8011 | 263.5119
3425.176 | 518.0375 | 267.1721 | 262.9163 | 263.8519
3426.176 | 516.2718 | 266.9899 | 262.8364 | 263.8306
3427.176 | 509.2691 | 266.8899 | 262.7999 | 264.2066
3428.176 | 507.1651 | 266.6943 | 262.9006 | 264.4789
3429.176 | 508.7218 | 267.1227 | 262.8823 | 264.3414
3430.176 | 518.0169 | 267.2337 | 263.0965 | 264.6762
3431.176 | 514.44 | 267.7136 | 263.3667 | 265.0097
3432.176 | 516.0379 | 267.9653 | 263.5023 | 265.7255
3433.176 | 523.666 | 268.4669 | 263.7934 | 265.727
3434.176 | 527.3687 | 268.7975 | 264.2388 | 265.9563
3435.176 | 530.9598 | 269.2721 | 264.3874 | 266.1791
3436.176 | 539.1517 | 269.0113 | 264.7215 | 266.2974
3437.176 | 545.2278 | 269.0464 | 265.0093 | 266.5754
3438.176 | 544.7512 | 268.4807 | 265.0271 | 266.7434
3439.176 | 534.8615 | 268.9709 | 264.9388 | 266.4724
3440.176 | 539.323 | 269.1078 | 264.7264 | 266.0745
3441.176 | 543.179 | 269.5315 | 264.7069 | 266.1251
3442.176 | 544.2889 | 269.9064 | 264.7129 | 266.6431
3443.176 | 549.6032 | 269.3004 | 265.0625 | 266.8104
3444.176 | 557.5768 | 269.9608 | 265.2474 | 266.88
3445.176 | 560.023 | 270.5605 | 265.6071 | 267.227
3446.176 | 564.7127 | 271.779 | 266.542 | 267.3704
3447.176 | 567.9285 | 271.882 | 266.6606 | 267.7491
3448.176 | 573.9517 | 271.697 | 266.6538 | 268.2179
3449.176 | 571.2406 | 271.5523 | 266.649 | 268.3668
3450.176 | 581.1242 | 271.7151 | 266.7424 | 268.587
3451.176 | 570.4111 | 272.1063 | 266.817 | 268.5016
3452.176 | 567.8349 | 271.8376 | 267.2282 | 268.8425
3453.176 | 558.3191 | 271.6524 | 267.3402 | 269.1254
3454.176 | 550.0676 | 271.5096 | 267.509 | 269.4598
3455.176 | 556.2397 | 271.9942 | 268.2932 | 269.9043
3456.1917 | 557.1061 | 272.6963 | 268.9285 | 270.105
3457.1917 | 561.5197 | 273.3131 | 269.0683 | 270.0329
3458.1917 | 563.8733 | 274.0418 | 269.1451 | 270.1169
3459.176 | 565.0163 | 274.1297 | 269.1635 | 269.9929
3460.176 | 569.0101 | 274.6257 | 269.1537 | 270.6825
3461.176 | 570.5545 | 275.0358 | 269.1072 | 271.2036
3462.176 | 563.3382 | 274.5571 | 269.0908 | 270.8612
3463.176 | 552.0774 | 274.8053 | 269.5497 | 270.9278
3464.176 | 542.7962 | 275.6793 | 269.6504 | 270.8394
3465.176 | 535.5691 | 276.0859 | 270.0156 | 270.5161
3466.176 | 535.6316 | 276.9513 | 270.2065 | 270.6593
3467.176 | 541.2918 | 277.4394 | 270.4191 | 270.7917
3468.176 | 545.2028 | 278.3905 | 271.0201 | 271.2101
3469.176 | 552.483 | 278.591 | 271.2678 | 271.4505
3470.176 | 554.7865 | 279.0858 | 271.4075 | 271.7817
3471.176 | 554.0156 | 279.2916 | 271.2592 | 272.1338
3472.176 | 554.8122 | 278.9415 | 271.3106 | 272.4408
3473.176 | 555.8821 | 278.9385 | 271.1439 | 272.9236
3474.176 | 560.2772 | 279.0349 | 271.5701 | 272.9011
3475.176 | 556.6518 | 278.8181 | 271.9689 | 273.4364
3476.176 | 559.0417 | 279.2135 | 272.5092 | 274.4656
3477.176 | 562.4386 | 279.7914 | 272.7981 | 274.9967
3478.176 | 558.996 | 280.2775 | 273.2758 | 274.808
3479.176 | 558.5261 | 280.5394 | 273.6102 | 275.0081
3480.176 | 555.5615 | 280.5226 | 274.0247 | 275.1296
3481.176 | 556.3254 | 280.7809 | 275.0922 | 275.4287
3482.176 | 555.7378 | 280.8561 | 274.9722 | 276.0963
3483.176 | 556.9754 | 281.0179 | 275.2671 | 276.0977
3484.176 | 558.3018 | 281.0223 | 276.0834 | 276.1192
3485.176 | 563.7892 | 281.2952 | 275.7062 | 276.1111
3486.176 | 568.5965 | 281.0535 | 275.5672 | 276.415
3487.176 | 565.5648 | 281.2457 | 275.4128 | 276.2559
3488.176 | 568.4823 | 281.5324 | 275.435 | 276.4243
3489.176 | 567.444 | 281.5878 | 275.7294 | 276.1534
3490.176 | 559.4268 | 282.3357 | 275.8566 | 275.8847
3491.176 | 553.1519 | 282.0244 | 275.9342 | 275.8716
3492.176 | 555.2176 | 282.0421 | 276.1449 | 275.8879
3493.176 | 554.1172 | 282.0347 | 276.2792 | 276.0912
3494.176 | 554.6567 | 281.8661 | 276.1278 | 276.2238
3495.176 | 551.5352 | 281.9666 | 276.0964 | 276.5062
3496.176 | 546.1607 | 282.6457 | 276.2893 | 276.9326
3497.176 | 540.7484 | 282.8114 | 276.0407 | 277.9797
3498.176 | 549.7473 | 283.3574 | 276.2097 | 278.926
3499.176 | 559.961 | 283.9865 | 276.3938 | 279.2069
3500.176 | 565.9235 | 284.4682 | 276.7634 | 278.9088
3501.176 | 562.9686 | 284.8328 | 276.9642 | 278.6012
3502.176 | 555.9279 | 284.9451 | 277.4176 | 278.9255
3503.176 | 555.2959 | 285.0875 | 277.5743 | 279.3593
3504.176 | 558.818 | 285.0056 | 277.8082 | 279.8556
3505.176 | 560.0342 | 285.3118 | 277.7729 | 280.099
3506.176 | 556.7988 | 285.1226 | 277.8432 | 280.1334
3507.176 | 559.0658 | 285.603 | 277.9905 | 280.4187
3508.176 | 560.4985 | 285.2313 | 278.2799 | 280.7285
3509.176 | 562.5195 | 285.2366 | 278.3871 | 280.9686
3510.176 | 572.7119 | 285.5486 | 278.3874 | 281.1187
3511.176 | 577.4072 | 285.4728 | 278.4555 | 281.5925
3512.176 | 577.044 | 285.2614 | 278.5562 | 282.3359
3513.176 | 574.5133 | 285.8461 | 279.0953 | 282.3018
3514.176 | 569.465 | 286.0581 | 279.4943 | 282.1497
3515.176 | 568.8791 | 286.1149 | 279.4918 | 282.079
3516.176 | 571.4347 | 286.283 | 279.5504 | 282.1622
3517.176 | 579.0682 | 286.2145 | 279.4368 | 282.4783
3518.176 | 576.1048 | 286.2843 | 279.3225 | 282.5668
3519.176 | 574.5271 | 286.5871 | 279.3125 | 283.6141
3520.176 | 578.3817 | 286.9315 | 279.4502 | 283.645
3521.176 | 576.041 | 287.3244 | 279.4794 | 283.7752
3522.176 | 577.6378 | 287.3823 | 280.0641 | 283.7948
3523.176 | 579.7021 | 287.964 | 280.0849 | 283.8839
3524.176 | 578.1573 | 288.1743 | 280.4793 | 284.2995
3525.176 | 575.4511 | 288.0818 | 280.6325 | 284.633
3526.176 | 579.5454 | 288.1105 | 280.6241 | 285.0515
3527.176 | 575.4918 | 287.9964 | 281.0392 | 284.9698
3528.176 | 572.5328 | 288.975 | 281.1482 | 284.901
3529.176 | 571.223 | 288.4145 | 281.1702 | 285.0129
3530.176 | 565.8329 | 288.9187 | 281.151 | 285.3
3531.176 | 563.6533 | 289.0836 | 281.1034 | 285.4086
3532.176 | 563.9589 | 289.3556 | 281.095 | 285.2596
3533.176 | 572.043 | 289.7189 | 281.0841 | 285.3327
3534.176 | 577.2665 | 289.8266 | 281.1498 | 284.9747
3535.176 | 586.008 | 290.2152 | 281.2152 | 285.123
3536.176 | 590.3935 | 290.2528 | 281.6772 | 285.3214
3537.176 | 595.8855 | 290.2668 | 281.6783 | 285.0468
3538.176 | 603.4255 | 290.23 | 281.8047 | 285.1716
3539.176 | 609.1777 | 290.6495 | 281.7582 | 286.3162
3540.176 | 617.588 | 290.9593 | 281.6689 | 286.3922
3541.176 | 626.5941 | 291.2137 | 282.8544 | 287.1123
3542.176 | 631.7518 | 291.3637 | 282.8717 | 287.0886
3543.176 | 627.5463 | 291.3462 | 283.0083 | 287.3795
3544.176 | 631.7291 | 291.3366 | 282.8649 | 287.6614
3545.176 | 636.0894 | 291.0933 | 282.9024 | 287.9618
3546.176 | 642.4957 | 291.428 | 283.3228 | 287.8703
3547.176 | 649.9311 | 291.5181 | 283.399 | 287.548
3548.176 | 647.5706 | 291.2745 | 283.9653 | 287.8998
3549.176 | 649.3011 | 291.1952 | 283.8985 | 287.7353
3550.176 | 652.844 | 291.4151 | 283.8411 | 288.0166
3551.176 | 647.0606 | 291.5401 | 283.7234 | 287.8355
3552.176 | 649.3729 | 291.2245 | 284.0262 | 288.1098
3553.176 | 648.7918 | 291.8788 | 284.8743 | 288.2078
3554.176 | 639.2814 | 292.1588 | 284.8702 | 288.0147
3555.176 | 634.1031 | 292.9682 | 284.845 | 287.1232
3556.176 | 630.1263 | 293.2172 | 284.9976 | 286.8355
3557.176 | 621.7983 | 293.6195 | 284.6475 | 286.3809
3558.176 | 615.8483 | 293.6888 | 285.0307 | 286.2155
3559.176 | 615.6076 | 293.994 | 285.2377 | 285.6579
3560.176 | 608.653 | 294.0728 | 285.4413 | 285.7276
3561.176 | 606.6615 | 294.6359 | 285.4514 | 286.2558
3562.176 | 620.9905 | 294.8171 | 285.779 | 287.1242
3563.176 | 626.7736 | 295.175 | 286.1884 | 287.9225
3564.176 | 629.8305 | 295.5036 | 287.3665 | 288.0611
3565.176 | 629.064 | 295.5398 | 287.2481 | 288.5058
3566.176 | 626.2553 | 295.4193 | 287.0746 | 288.0909
3567.176 | 623.2088 | 295.4562 | 287.0857 | 287.6234
3568.176 | 628.4706 | 295.9723 | 287.4391 | 287.68
3569.176 | 629.9773 | 296.4375 | 287.4225 | 288.0547
3570.176 | 636.9881 | 296.5504 | 287.1745 | 287.888
3571.176 | 636.0538 | 296.2885 | 287.2437 | 287.8496
3572.176 | 643.0372 | 296.6943 | 287.8339 | 288.3779
3573.176 | 644.4463 | 296.7013 | 288.3039 | 288.2972
3574.176 | 645.5608 | 296.6841 | 288.647 | 288.6474
3575.176 | 642.2507 | 296.8601 | 289.0443 | 288.5891
3576.176 | 642.5365 | 297.0955 | 289.0429 | 289.1261
3577.176 | 639.2716 | 296.8495 | 289.6411 | 289.6357
3578.176 | 640.7694 | 297.0082 | 289.9941 | 289.9731
3579.176 | 641.8917 | 296.6655 | 289.8331 | 290.6376
3580.176 | 636.8936 | 296.5438 | 289.8219 | 291.6092
3581.176 | 635.6275 | 296.5853 | 290.9126 | 292.0856
3582.176 | 642.6266 | 296.652 | 290.8343 | 292.1563
3583.176 | 644.6901 | 297.0025 | 290.7922 | 292.6848
3584.176 | 647.9028 | 297.1923 | 291.175 | 293.0357
3585.176 | 650.4435 | 297.297 | 291.2321 | 293.1825
3586.176 | 652.7264 | 297.6307 | 291.4166 | 293.4128
3587.176 | 654.8689 | 297.8958 | 291.863 | 293.4264
3588.176 | 652.2655 | 297.8449 | 292.3857 | 293.1698
3589.176 | 645.8408 | 297.1243 | 292.4187 | 293.0699
3590.176 | 646.363 | 297.4886 | 292.4782 | 293.368
3591.176 | 647.784 | 297.6833 | 293.334 | 293.3629
3592.176 | 651.804 | 298.1914 | 293.7622 | 294.0215
3593.176 | 649.6042 | 298.8918 | 294.3359 | 294.0005
3594.176 | 656.0771 | 299.244 | 294.132 | 294.0856
3595.176 | 653.2323 | 299.6693 | 294.4282 | 293.6982
3596.176 | 648.3688 | 299.9639 | 294.5642 | 293.8742
3597.176 | 659.6072 | 300.483 | 295.2173 | 293.7831
3598.176 | 661.4834 | 301.0382 | 295.5919 | 293.7763
3599.176 | 660.1586 | 301.8275 | 295.7037 | 293.4965
3600.176 | 667.5772 | 302.5991 | 296.8028 | 293.8463
3601.176 | 679.133 | 303.2027 | 296.4902 | 294.4455
3602.176 | 685.7969 | 304.472 | 296.3234 | 294.8381
3603.176 | 679.2024 | 305.196 | 296.976 | 295.4799
3604.176 | 675.8097 | 306.3755 | 297.1896 | 295.6124
3605.176 | 674.9487 | 306.8698 | 297.4505 | 295.7514
3606.176 | 677.7551 | 307.9367 | 297.6122 | 296.023
3607.176 | 684.183 | 308.128 | 299.0474 | 296.3221
3608.176 | 684.5391 | 308.5629 | 299.3403 | 297.2752
3609.176 | 686.9945 | 308.3838 | 299.7455 | 297.7469
3610.176 | 690.2229 | 308.6045 | 300.1728 | 298.1774
3611.176 | 686.244 | 308.7048 | 300.7165 | 298.1445
3612.176 | 683.6614 | 309.5341 | 301.1621 | 298.7324
3613.176 | 680.5941 | 309.7866 | 301.555 | 298.9085
3614.176 | 683.218 | 310.1157 | 301.7487 | 299.189
3615.176 | 685.5392 | 310.2263 | 301.4695 | 299.1357
3616.176 | 687.0467 | 310.428 | 301.313 | 299.2969
3617.176 | 684.5477 | 310.2504 | 301.1028 | 299.7702
3618.176 | 686.4781 | 310.1081 | 300.7996 | 300.3325
3619.176 | 687.4744 | 309.8543 | 300.6685 | 300.522
3620.176 | 688.7481 | 309.906 | 300.78 | 300.5496
3621.176 | 686.5886 | 309.8158 | 300.462 | 300.1486
3622.176 | 686.6961 | 310.4249 | 300.4254 | 300.6428
3623.176 | 684.1115 | 311.0613 | 301.5569 | 301.0134
3624.176 | 681.5268 | 311.0823 | 301.6545 | 302.0171
3625.176 | 675.7183 | 311.3625 | 301.706 | 303.0134
3626.176 | 672.4226 | 311.6408 | 301.5766 | 303.8162
3627.176 | 674.8701 | 311.8674 | 302.1274 | 304.0759
3628.176 | 663.0319 | 311.6929 | 301.9546 | 303.6214
3629.176 | 665.3275 | 311.5894 | 302.0317 | 303.2095
3630.176 | 668.4974 | 312.9355 | 302.3538 | 303.1184
3631.176 | 673.0116 | 313.617 | 302.7271 | 303.0279
3632.176 | 679.1265 | 314.1261 | 302.7693 | 303.2543
3633.176 | 682.5138 | 314.3836 | 303.0497 | 303.4603
3634.176 | 685.8839 | 314.4329 | 303.7498 | 304.0542
3635.176 | 684.4462 | 314.2502 | 303.9518 | 304.5853
3636.176 | 682.1312 | 314.3395 | 303.8069 | 303.8067
3637.176 | 680.7715 | 314.6093 | 304.0053 | 304.0528
3638.176 | 679.3949 | 314.8888 | 304.4461 | 303.9837
3639.176 | 669.0628 | 315.9416 | 304.599 | 304.3723
3640.176 | 656.8006 | 316.3782 | 304.8766 | 304.7647
3641.176 | 653.7539 | 317.1304 | 305.53 | 304.5261
3642.176 | 648.3697 | 317.9207 | 306.217 | 305.5317
3643.176 | 644.3329 | 318.0081 | 306.6106 | 305.5068
3644.176 | 646.5713 | 317.9551 | 307.0579 | 305.1364
3645.176 | 644.3288 | 318.1839 | 307.4326 | 304.8854
3646.176 | 645.5414 | 318.3354 | 308.1522 | 304.8891
3647.176 | 647.3367 | 319.5686 | 308.5489 | 305.0264
3648.176 | 649.5877 | 320.3926 | 308.8328 | 305.9656
3649.176 | 656.3356 | 320.8394 | 309.2517 | 306.2151
3650.176 | 660.9691 | 321.3407 | 309.9546 | 306.4613
3651.176 | 669.4203 | 321.6078 | 310.1795 | 306.1269
3652.176 | 672.613 | 322.0792 | 310.571 | 306.69
3653.176 | 678.1177 | 321.7284 | 311.0118 | 307.263
3654.176 | 675.4389 | 321.79 | 311.649 | 307.756
3655.176 | 673.4284 | 321.7543 | 312.391 | 307.7909
3656.176 | 672.7856 | 321.8486 | 312.9486 | 308.3565
3657.176 | 677.6663 | 321.7249 | 313.8249 | 308.4855
3658.176 | 676.6416 | 321.8656 | 314.3508 | 308.3205
3659.176 | 675.988 | 322.453 | 314.938 | 308.7774
3660.176 | 678.4002 | 322.697 | 315.1273 | 309.5349
3661.176 | 679.3904 | 322.7144 | 315.3448 | 310.276
3662.176 | 679.8613 | 322.6508 | 315.4554 | 310.4393
3663.176 | 677.4421 | 322.8336 | 315.9997 | 310.7627
3664.176 | 672.1321 | 323.3013 | 316.1867 | 311.4083
3665.176 | 675.7945 | 323.6426 | 316.1101 | 311.9842
3666.176 | 679.3566 | 324.0313 | 316.4109 | 311.8944
3667.176 | 681.6804 | 324.5262 | 316.7038 | 311.6387
3668.176 | 681.2254 | 325.3258 | 316.7718 | 312.1468
3669.176 | 683.3739 | 325.8613 | 317.2248 | 312.1047
3670.176 | 682.9477 | 326.6278 | 317.4676 | 311.6413
3671.176 | 685.378 | 326.5724 | 317.591 | 311.7464
3672.176 | 684.3721 | 326.5906 | 317.6777 | 311.6537
3673.176 | 682.1433 | 326.5592 | 318.1002 | 312.5621
3674.176 | 680.6471 | 326.9878 | 318.0265 | 312.8969
3675.176 | 682.1498 | 327.2097 | 318.2976 | 313.3614
3676.176 | 679.7554 | 327.4678 | 318.4079 | 313.286
3677.176 | 676.9818 | 328.0962 | 318.5662 | 314.3485
3678.176 | 677.494 | 328.2185 | 318.7526 | 314.5781
3679.176 | 680.5161 | 328.7366 | 319.6751 | 314.7287
3680.176 | 685.0867 | 328.7019 | 319.5406 | 315.053
3681.176 | 687.6066 | 328.4935 | 319.5814 | 315.0492
3682.176 | 684.6992 | 328.4108 | 320.2084 | 314.8922
3683.176 | 687.8409 | 328.7301 | 320.3811 | 314.9192
3684.176 | 689.6752 | 329.5844 | 320.422 | 314.7709
3685.176 | 690.8511 | 329.9185 | 320.4804 | 314.9383
3686.176 | 691.0044 | 330.1355 | 320.7719 | 315.4949
3687.176 | 692.0949 | 330.5048 | 321.3052 | 316.1995
3688.176 | 692.2877 | 330.5346 | 321.6082 | 316.6866
3689.176 | 691.2859 | 330.9119 | 322.1501 | 317.1547
3690.176 | 692.3371 | 331.8635 | 322.3471 | 316.9945
3691.176 | 694.4028 | 332.5968 | 323.0758 | 317.5624
3692.176 | 691.2119 | 333.2191 | 323.4403 | 318.2132
3693.176 | 697.9077 | 333.175 | 323.8258 | 318.5142
3694.176 | 699.9272 | 333.2676 | 324.1734 | 318.7308
3695.176 | 698.6779 | 333.6087 | 324.4003 | 319.2941
3696.176 | 695.7232 | 334.3329 | 324.643 | 319.6949
3697.176 | 694.8068 | 334.1904 | 324.7704 | 319.7243
3698.176 | 689.3297 | 334.5314 | 324.8848 | 319.666
3699.176 | 684.433 | 334.7259 | 325.3443 | 319.8933
3700.176 | 682.0156 | 334.9407 | 325.8333 | 319.7339
3701.176 | 685.9544 | 335.6747 | 326.1722 | 320.1269
3702.176 | 687.4207 | 336.0371 | 326.2851 | 320.8331
3703.176 | 691.0705 | 336.5292 | 326.316 | 321.5046
3704.176 | 692.6586 | 336.8279 | 326.4682 | 322.2003
3705.176 | 690.8837 | 337.0388 | 326.1617 | 323.2756
3706.176 | 692.6512 | 337.2912 | 326.2734 | 323.4286
3707.176 | 691.0038 | 337.2367 | 326.7181 | 323.2615
3708.176 | 692.6683 | 337.7685 | 327.1846 | 323.7014
3709.176 | 693.9676 | 338.6088 | 327.4826 | 324.2059
3710.176 | 694.5404 | 339.1398 | 328.1334 | 324.3126
3711.176 | 693.4275 | 339.0888 | 328.6768 | 324.6818
3712.176 | 691.579 | 339.154 | 329.1768 | 325.4151
3713.176 | 681.0506 | 339.3004 | 330.3644 | 326.1301
3714.176 | 680.709 | 339.7019 | 330.7814 | 326.4032
3715.176 | 679.0515 | 340.7294 | 331.8684 | 326.6762
3716.176 | 681.0319 | 340.8119 | 332.209 | 327.0529
3717.176 | 683.8445 | 341.0102 | 332.2188 | 327.6779
3718.176 | 683.4068 | 341.3489 | 332.5277 | 328.0556
3719.176 | 682.3178 | 342.046 | 332.3462 | 328.3414
3720.176 | 685.739 | 342.6458 | 332.2979 | 329.1502
3721.176 | 685.0002 | 343.3348 | 332.3671 | 329.0747
3722.176 | 686.7272 | 343.5349 | 333.1129 | 330.0572
3723.176 | 692.2784 | 344.1535 | 333.7071 | 330.6925
3724.176 | 699.6752 | 344.3022 | 334.4148 | 330.9163
3725.176 | 702.6076 | 344.8383 | 335.2055 | 331.1768
3726.176 | 702.8294 | 345.0422 | 335.727 | 330.9649
3727.176 | 699.6125 | 345.3351 | 336.2814 | 331.0437
3728.176 | 694.5832 | 345.5947 | 336.8007 | 331.7856
3729.176 | 694.443 | 345.8531 | 337.4 | 332.213
3730.176 | 690.6312 | 345.8703 | 338.1149 | 333.3573
3731.176 | 687.893 | 345.8619 | 338.3256 | 333.2003
3732.176 | 688.8211 | 346.1491 | 338.4939 | 332.5919
3733.176 | 692.3305 | 346.707 | 338.633 | 332.9684
3734.176 | 694.18 | 347.6632 | 339.188 | 333.1929
3735.176 | 692.1112 | 347.816 | 339.8463 | 333.3971
3736.176 | 691.5464 | 348.2213 | 340.4873 | 334.0258
3737.176 | 688.7829 | 349.3638 | 341.748 | 334.3188
3738.176 | 686.9418 | 351.3095 | 342.4895 | 335.57
3739.176 | 687.0855 | 352.729 | 343.2491 | 335.7525
3740.176 | 686.4442 | 353.212 | 343.8129 | 336.2531
3741.176 | 686.229 | 353.7981 | 344.2636 | 336.3043
3742.176 | 690.9745 | 353.9309 | 344.6217 | 336.1508
3743.176 | 695.5706 | 354.4201 | 344.9205 | 336.8546
3744.176 | 691.4949 | 354.5985 | 345.7434 | 337.0014
3745.176 | 688.1403 | 354.6451 | 345.8472 | 337.411
3746.176 | 684.6536 | 354.8584 | 345.9749 | 338.3546
3747.176 | 676.1793 | 354.6573 | 346.11 | 339.1253
3748.176 | 673.2374 | 355.0606 | 346.4217 | 338.7527
3749.176 | 675.9857 | 355.0126 | 346.9844 | 340.4005
3750.176 | 680.2348 | 355.3524 | 347.3735 | 341.0649
3751.176 | 681.765 | 355.6162 | 347.7139 | 340.6867
3752.176 | 680.8528 | 356.0873 | 348.8375 | 340.433
3753.176 | 683.3837 | 356.1843 | 349.0798 | 341.0763
3754.176 | 686.9875 | 356.6748 | 349.5875 | 341.2659
3755.176 | 689.6965 | 357.4158 | 349.991 | 341.1863
3756.176 | 685.4636 | 357.9113 | 350.3695 | 342.0433
3757.176 | 687.4189 | 359.021 | 350.9313 | 343.261
3758.176 | 688.9285 | 359.8859 | 352.2576 | 343.5362
3759.176 | 690.3345 | 359.7407 | 352.8093 | 343.4687
3760.176 | 689.3874 | 360.2486 | 352.5804 | 343.4418
3761.176 | 686.105 | 359.8197 | 352.2575 | 342.6651
3762.176 | 680.851 | 359.388 | 351.684 | 342.0891
3763.176 | 680.0373 | 359.5134 | 351.5906 | 341.8333
3764.176 | 677.6666 | 359.4263 | 351.4541 | 341.9375
3765.176 | 678.0228 | 359.9142 | 351.3478 | 341.0337
3766.176 | 682.8352 | 359.7073 | 351.5343 | 340.3783
3767.176 | 684.6739 | 359.842 | 351.5968 | 340.3612
3768.176 | 689.2044 | 360.0175 | 351.812 | 340.7417
3769.176 | 689.7135 | 360.2686 | 352.0457 | 341.3864
3770.176 | 689.3784 | 359.819 | 352.2643 | 341.3809
3771.176 | 693.7775 | 359.8747 | 352.3303 | 341.2585
3772.176 | 696.5174 | 360.2139 | 352.4102 | 341.0129
3773.176 | 697.3092 | 360.3995 | 353.1036 | 341.7165
3774.176 | 698.3422 | 360.1908 | 353.6525 | 342.4414
3775.176 | 700.1919 | 360.1188 | 353.6646 | 342.9295
3776.176 | 700.5297 | 360.0509 | 353.7484 | 343.1882
3777.176 | 696.4197 | 359.6259 | 353.7754 | 342.8688
3778.176 | 694.2175 | 359.7724 | 354.0059 | 342.9492
3779.176 | 690.8736 | 359.6632 | 353.9087 | 343.5371
3780.176 | 687.5605 | 359.6906 | 354.1036 | 344.3871
3781.176 | 684.9381 | 359.6466 | 354.341 | 344.6417
3782.176 | 684.308 | 359.2989 | 354.1732 | 344.9587
3783.176 | 681.7561 | 359.0611 | 353.7802 | 345.1101
3784.176 | 684.0159 | 359.0168 | 353.5498 | 344.7902
3785.176 | 682.1743 | 359.2001 | 353.5897 | 344.8929
3786.176 | 683.6322 | 359.0986 | 353.893 | 344.5113
3787.176 | 683.4465 | 359.1765 | 354.7069 | 344.5717
3788.176 | 685.0844 | 359.3685 | 355.1373 | 344.397
3789.176 | 689.6793 | 359.6687 | 355.6899 | 344.3528
3790.176 | 689.3512 | 359.6059 | 355.7903 | 344.7261
3791.176 | 689.3305 | 359.8043 | 356.3711 | 345.1203
3792.176 | 690.4488 | 360.6765 | 356.7494 | 344.8254
3793.176 | 691.2893 | 361.073 | 357.0047 | 344.6801
3794.176 | 695.2471 | 361.4973 | 357.3235 | 345.213
3795.176 | 695.0385 | 362.232 | 357.3653 | 345.696
3796.176 | 694.491 | 362.3839 | 357.2017 | 345.8134
3797.176 | 694.6183 | 362.2775 | 357.1702 | 345.259
3798.176 | 693.3684 | 362.5757 | 356.9645 | 344.9918
3799.176 | 692.2901 | 362.7595 | 357.0291 | 345.1575
3800.176 | 690.4434 | 362.6356 | 356.7789 | 344.8168
3801.176 | 688.8584 | 362.5515 | 356.5457 | 345.2506
3802.176 | 691.2743 | 362.7376 | 356.3519 | 346.4077
3803.176 | 694.5358 | 363.3108 | 357.0548 | 346.9519
3804.176 | 695.6911 | 363.5724 | 357.5362 | 347.3957
3805.176 | 695.8008 | 363.9327 | 357.978 | 348.4029
3806.176 | 694.7199 | 364.2808 | 358.352 | 348.3991
3807.176 | 695.5973 | 365.1776 | 359.0977 | 348.5894
3808.176 | 693.4702 | 365.417 | 359.5294 | 349.3185
3809.176 | 690.9426 | 365.5531 | 359.4426 | 349.2314
3810.176 | 687.2547 | 365.6161 | 359.197 | 349.4382
3811.176 | 686.2407 | 365.8814 | 359.1473 | 349.148
3812.176 | 682.2638 | 365.8718 | 359.1491 | 349.5624
3813.176 | 686.6981 | 366.0296 | 359.3471 | 349.5189
3814.176 | 694.5686 | 366.0532 | 359.7361 | 350.4685
3815.176 | 694.7736 | 366.7994 | 360.2225 | 351.3866
3816.176 | 698.5174 | 367.3103 | 360.4489 | 351.5596
3817.176 | 699.5951 | 367.7994 | 360.7813 | 351.2602
3818.176 | 697.1645 | 367.9319 | 361.0375 | 350.876
3819.176 | 694.2749 | 368.6061 | 361.002 | 350.2877
3820.176 | 692.6189 | 369.0621 | 361.3126 | 350.0322
3821.176 | 691.7478 | 368.8892 | 361.5965 | 349.6384
3822.176 | 693.5593 | 368.7799 | 361.5302 | 349.1717
3823.176 | 694.4248 | 368.8353 | 361.6934 | 348.9778
3824.176 | 691.7411 | 368.88 | 361.7772 | 348.6038
3825.176 | 691.2795 | 368.9749 | 361.8717 | 348.7705
3826.176 | 689.864 | 369.4448 | 361.7519 | 348.8025
3827.176 | 685.985 | 369.5957 | 362.0261 | 349.4104
3828.176 | 686.7013 | 369.8979 | 362.5124 | 349.9294
3829.176 | 688.8367 | 369.7578 | 362.3283 | 350.3192
3830.176 | 690.0952 | 369.566 | 362.1293 | 350.2836
3831.176 | 689.4437 | 369.5299 | 362.3628 | 350.606
3832.176 | 687.4076 | 370.2504 | 362.8345 | 352.09
3833.176 | 687.0846 | 370.6344 | 363.85 | 352.2423
3834.176 | 691.0629 | 370.6935 | 363.7852 | 352.0565
3835.176 | 692.1977 | 371.0357 | 363.7704 | 352.4172
3836.176 | 687.2385 | 370.8639 | 363.4587 | 352.132
3837.176 | 685.3789 | 371.2089 | 363.0444 | 352.0417
3838.176 | 694.7241 | 371.5512 | 362.9972 | 352.0773
3839.176 | 703.5081 | 372.3746 | 363.121 | 351.9371
3840.176 | 702.6586 | 372.1712 | 363.5028 | 351.4319
3841.176 | 698.7183 | 371.726 | 363.7052 | 351.9072
3842.176 | 696.8062 | 371.5105 | 363.5049 | 352.3772
3843.176 | 695.1836 | 371.5232 | 363.4463 | 352.3388
3844.176 | 695.1152 | 372.0495 | 363.1524 | 352.0022
3845.176 | 698.4077 | 372.5234 | 363.1349 | 351.9412
3846.176 | 693.7243 | 373.6761 | 363.1191 | 351.6333
3847.176 | 693.7753 | 374.2487 | 363.3274 | 351.9484
3848.176 | 693.1105 | 374.4366 | 363.6221 | 352.9294
3849.176 | 689.9662 | 374.5631 | 363.9612 | 353.1562
3850.176 | 688.5353 | 375.1419 | 364.6045 | 353.9889
3851.176 | 685.7447 | 375.8569 | 365.1723 | 354.6535
3852.176 | 683.8938 | 375.6682 | 365.7904 | 354.9718
3853.176 | 682.5279 | 376.0907 | 366.6681 | 355.258
3854.176 | 682.0843 | 376.5057 | 367.1152 | 355.3356
3855.176 | 686.1288 | 376.6501 | 367.3545 | 355.66
3856.176 | 687.1405 | 377.5479 | 369.1018 | 356.0203
3857.176 | 682.9765 | 377.3258 | 369.1656 | 356.5914
3858.176 | 680.0651 | 377.3256 | 368.8685 | 357.3379
3859.176 | 681.8031 | 377.8671 | 368.7804 | 358.0875
3860.176 | 683.8615 | 377.9913 | 369.2102 | 358.1401
3861.176 | 684.9162 | 378.1424 | 369.2448 | 358.4311
3862.176 | 685.6226 | 378.2322 | 369.1972 | 358.4769
3863.176 | 688.8855 | 378.4052 | 369.1979 | 358.6743
3864.176 | 687.547 | 378.2099 | 369.1941 | 358.7467
3865.176 | 688.2856 | 377.846 | 369.3326 | 358.4938
3866.176 | 686.1871 | 377.8633 | 369.369 | 358.5512
3867.176 | 685.7274 | 378.0272 | 369.2972 | 358.6833
3868.176 | 687.487 | 378.1065 | 369.2322 | 358.4267
3869.176 | 684.7344 | 377.8367 | 369.2152 | 358.833
3870.176 | 682.5089 | 377.9722 | 369.3239 | 359.4483
3871.176 | 679.8739 | 377.9568 | 369.382 | 360.5007
3872.176 | 680.291 | 378.018 | 369.5139 | 360.0827
3873.176 | 685.2507 | 378.3854 | 369.5896 | 360.2679
3874.176 | 688.3569 | 378.6319 | 369.7143 | 360.0649
3875.176 | 687.9659 | 378.7471 | 369.6265 | 360.7016
3876.176 | 684.335 | 379.0803 | 369.6919 | 360.2629
3877.176 | 682.0726 | 379.4141 | 369.9512 | 360.8051
3878.176 | 682.4267 | 379.4379 | 370.1548 | 361.2535
3879.176 | 682.8153 | 379.9585 | 370.6096 | 361.8011
3880.176 | 680.8071 | 380.0019 | 371.0804 | 361.7258
3881.176 | 675.9576 | 380.4085 | 371.4435 | 361.6417
3882.176 | 674.1086 | 381.5346 | 371.5382 | 361.9013
3883.176 | 671.348 | 381.7196 | 371.7276 | 361.6846
3884.176 | 671.0598 | 382.1008 | 371.9837 | 362.0205
3885.176 | 674.5443 | 382.5333 | 372.5579 | 362.5546
3886.176 | 671.1722 | 382.8242 | 373.0374 | 363.0476
3887.176 | 671.9416 | 383.2446 | 373.3789 | 363.5741
3888.176 | 674.3475 | 383.5105 | 373.4056 | 364.8951
3889.176 | 673.2197 | 384.3332 | 373.0262 | 364.9203
3890.176 | 669.0271 | 385.3827 | 373.3624 | 365.6275
3891.176 | 667.1104 | 385.8649 | 373.7676 | 365.5662
3892.176 | 667.9281 | 386.3637 | 374.1791 | 366.106
3893.176 | 669.0205 | 387.2248 | 374.3877 | 365.8304
3894.176 | 667.3593 | 386.8815 | 375.7815 | 365.9059
3895.176 | 669.3625 | 386.9537 | 376.0463 | 365.5953
3896.176 | 670.1006 | 387.3075 | 376.1085 | 366.0629
3897.176 | 671.4938 | 387.4928 | 376.348 | 365.8946
3898.176 | 672.2819 | 387.5855 | 376.3958 | 366.0388
3899.176 | 675.2564 | 387.3036 | 376.254 | 365.9329
3900.176 | 678.6795 | 387.5478 | 376.2473 | 365.8939
3901.176 | 681.7127 | 388.0771 | 376.6353 | 366.0048
3902.176 | 680.6528 | 388.3445 | 376.9338 | 366.3884
3903.176 | 679.158 | 388.7666 | 377.37 | 367.1265
3904.176 | 675.2932 | 389.2299 | 377.6922 | 367.6168
3905.176 | 674.506 | 389.4629 | 377.5477 | 367.7759
3906.176 | 674.2782 | 389.2692 | 377.6678 | 367.9519
3907.176 | 674.9772 | 390.7372 | 378.297 | 368.5522
3908.176 | 676.2704 | 391.0106 | 378.6276 | 368.878
3909.176 | 678.1588 | 391.0447 | 378.7998 | 369.3276
3910.176 | 676.3299 | 390.9053 | 378.8827 | 369.9811
3911.176 | 676.1056 | 391.0351 | 379.3886 | 370.9418
3912.176 | 675.6151 | 391.5243 | 379.6552 | 371.3778
3913.176 | 674.6462 | 391.489 | 379.6878 | 371.407
3914.176 | 673.1276 | 391.691 | 379.8113 | 371.4165
3915.176 | 672.1049 | 391.8051 | 380.3564 | 371.9346
3916.176 | 671.4765 | 392.7307 | 380.9699 | 372.5225
3917.176 | 669.569 | 393.4355 | 381.3568 | 373.3558
3918.176 | 665.3973 | 394.3576 | 382.2308 | 373.8084
3919.176 | 662.9224 | 394.7976 | 383.0208 | 374.5706
3920.176 | 659.1177 | 395.8597 | 384.1251 | 375.2393
3921.176 | 654.6324 | 396.5322 | 385.0264 | 375.5805
3922.176 | 651.0967 | 397.3493 | 385.9775 | 376.4883
3923.176 | 649.1538 | 397.9389 | 386.6959 | 376.1399
3924.176 | 643.1085 | 398.8173 | 387.0867 | 376.5316
3925.176 | 641.0913 | 399.4572 | 387.5709 | 377.0034
3926.176 | 640.297 | 399.9203 | 387.9008 | 376.8978
3927.176 | 638.5706 | 400.3363 | 388.3522 | 377.7597
3928.176 | 637.9032 | 401.1374 | 389.111 | 378.3442
3929.176 | 636.3062 | 401.9369 | 389.6586 | 379.1231
3930.176 | 635.9774 | 401.8376 | 390.2649 | 379.0814
3931.176 | 635.6762 | 401.8856 | 390.8855 | 379.0893
3932.176 | 636.2616 | 401.5524 | 390.9727 | 379.4933
3933.176 | 637.387 | 401.2009 | 391.1383 | 379.5603
3934.176 | 638.2327 | 401.582 | 391.3899 | 380.4371
3935.176 | 638.8518 | 401.8621 | 391.6893 | 380.5215
3936.176 | 637.246 | 402.6992 | 391.9572 | 380.0382
3937.176 | 639.6101 | 403.8452 | 392.4437 | 380.215
3938.176 | 640.7484 | 405.3875 | 393.4428 | 380.1769
3939.176 | 644.571 | 405.7175 | 394.487 | 380.7263
3940.176 | 646.3756 | 405.3815 | 395.1163 | 381.6127
3941.176 | 647.7865 | 404.9693 | 395.5 | 381.5109
3942.176 | 648.1817 | 404.9043 | 395.571 | 381.5001
3943.176 | 648.5306 | 404.9857 | 395.5343 | 381.4972
3944.176 | 646.4039 | 405.3055 | 395.3902 | 382.1565
3945.176 | 648.7985 | 405.4331 | 395.6695 | 383.4243
3946.176 | 651.188 | 406.2656 | 396.268 | 383.4548
3947.176 | 651.8303 | 407.2567 | 396.614 | 383.7171
3948.176 | 653.5035 | 407.4642 | 396.563 | 383.1971
3949.176 | 654.0062 | 407.9205 | 396.6895 | 383.4871
3950.176 | 650.6468 | 408.9792 | 396.9102 | 383.5175
3951.176 | 649.6417 | 409.2254 | 397.4314 | 383.9157
3952.176 | 651.3505 | 409.2303 | 398.1991 | 384.2537
3953.176 | 649.5742 | 408.8891 | 398.4957 | 384.6462
3954.176 | 650.1397 | 409.3998 | 399.1775 | 384.9602
3955.176 | 649.5194 | 409.542 | 399.2024 | 385.1752
3956.176 | 649.6478 | 409.8297 | 399.4143 | 385.4935
3957.176 | 650.3195 | 409.3083 | 399.5644 | 385.6026
3958.176 | 654.5826 | 409.0382 | 399.4968 | 385.2511
3959.176 | 659.3596 | 409.3312 | 399.494 | 384.8183
3960.176 | 665.9939 | 410.1271 | 399.8947 | 385.1007
3961.176 | 668.7658 | 410.0521 | 400.4899 | 385.6586
3962.176 | 669.3331 | 409.8586 | 400.5457 | 385.4058
3963.176 | 668.6744 | 409.7382 | 400.5189 | 385.4034
3964.176 | 669.1812 | 409.3832 | 400.6203 | 386.5396
3965.176 | 664.1272 | 409.357 | 400.5986 | 386.8831
3966.176 | 660.9994 | 409.1348 | 400.5114 | 386.5459
3967.176 | 656.3229 | 408.8654 | 400.4238 | 387.0285
3968.176 | 655.3709 | 408.6719 | 400.4475 | 386.7599
3969.176 | 655.3197 | 408.5389 | 400.1937 | 386.8198
3970.176 | 654.8853 | 408.004 | 400.0584 | 386.4774
3971.176 | 655.4057 | 407.4655 | 399.9115 | 386.0651
3972.176 | 656.3442 | 407.4324 | 399.8079 | 387.753
3973.176 | 654.8831 | 407.5758 | 399.8791 | 387.9621
3974.176 | 653.4829 | 407.5573 | 399.6737 | 387.5596
3975.176 | 654.6304 | 407.654 | 401.1653 | 386.8799
3976.176 | 654.1069 | 408.3122 | 400.878 | 386.3404
3977.176 | 659.5791 | 409.011 | 400.823 | 386.112
3978.176 | 662.7953 | 409.1761 | 400.6315 | 386.2155
3979.176 | 668.3079 | 409.0257 | 400.4652 | 386.2961
3980.176 | 668.9236 | 409.2215 | 400.2556 | 386.6966
3981.176 | 669.2199 | 408.9919 | 399.9502 | 386.6109
3982.176 | 667.256 | 409.3401 | 399.8337 | 387.0822
3983.176 | 668.7824 | 409.5464 | 399.5221 | 387.2445
3984.176 | 667.0474 | 409.8962 | 399.4173 | 387.5164
3985.176 | 665.2717 | 409.9567 | 399.1201 | 388.7187
3986.176 | 660.9115 | 409.4245 | 398.863 | 388.2698
3987.176 | 661.0382 | 409.0323 | 398.8112 | 388.6084
3988.176 | 660.5507 | 408.7297 | 399.0934 | 388.6944
3989.176 | 662.1252 | 409.1043 | 399.133 | 388.5731
3990.176 | 662.3381 | 409.2896 | 399.2524 | 388.1677
3991.176 | 667.3044 | 409.2207 | 399.525 | 387.9687
3992.176 | 668.2077 | 409.2026 | 399.67 | 388.0765
3993.176 | 672.2847 | 409.4227 | 399.7072 | 387.503
3994.176 | 671.937 | 410.0573 | 399.8369 | 386.8844
3995.176 | 670.4406 | 410.5148 | 399.5759 | 386.419
3996.176 | 668.7398 | 410.9248 | 399.5037 | 386.1207
3997.176 | 664.9834 | 410.6834 | 399.119 | 385.6371
3998.176 | 664.2907 | 410.5675 | 398.9404 | 385.1135
3999.176 | 665.3691 | 410.4098 | 398.9704 | 384.7447
4000.176 | 668.623 | 410.2814 | 398.8881 | 385.107
4001.176 | 666.6642 | 410.3435 | 398.9858 | 386.3888
4002.176 | 661.4457 | 410.6293 | 399.315 | 387.1718
4003.176 | 660.5808 | 411.6344 | 399.6115 | 387.3704
4004.176 | 661.7065 | 411.7483 | 400.018 | 387.9137
4005.176 | 662.3944 | 411.7081 | 400.0217 | 387.9258
4006.176 | 662.9876 | 411.8498 | 399.9852 | 387.6838
4007.176 | 661.3292 | 411.1103 | 400.0298 | 388.2485
4008.176 | 660.9462 | 410.9098 | 400.057 | 388.0006
4009.176 | 661.6595 | 411.5571 | 400.7743 | 387.7441
4010.176 | 662.2349 | 411.9876 | 401.3339 | 387.9142
4011.176 | 656.3863 | 411.9507 | 401.4033 | 388.5759
4012.176 | 657.977 | 411.5017 | 401.537 | 388.9348
4013.176 | 657.2654 | 411.1042 | 401.5642 | 388.9645
4014.176 | 658.384 | 410.5788 | 401.4498 | 388.7511
4015.176 | 654.6372 | 410.1094 | 401.5592 | 388.8044
4016.176 | 653.5001 | 410.2469 | 401.7588 | 388.6036
4017.176 | 653.1868 | 410.7697 | 401.8552 | 388.474
4018.176 | 651.8547 | 411.237 | 402.0438 | 388.5865
4019.176 | 649.8052 | 411.6731 | 402.5298 | 388.6959
4020.176 | 657.461 | 411.8424 | 402.8729 | 388.7627
4021.176 | 666.1744 | 412.2124 | 403.3427 | 389.205
4022.176 | 673.5593 | 413.1793 | 404.7724 | 389.3753
4023.176 | 680.7776 | 413.892 | 407.2364 | 389.8962
4024.176 | 680.8119 | 414.85 | 408.3883 | 391.3082
4025.176 | 676.45 | 415.6389 | 408.8211 | 392.6346
4026.176 | 676.7324 | 416.1325 | 409.098 | 393.4671
4027.176 | 682.959 | 416.318 | 409.1725 | 393.5073
4028.176 | 685.9134 | 416.5813 | 409.2216 | 393.2273
4029.176 | 687.378 | 417.0915 | 409.0466 | 393.3654
4030.176 | 685.7136 | 417.286 | 408.967 | 393.6421
4031.176 | 690.0167 | 417.2422 | 408.9263 | 393.4581
4032.176 | 687.7044 | 417.1723 | 408.6997 | 394.2781
4033.176 | 687.0726 | 416.9022 | 408.3904 | 394.0976
4034.176 | 686.3301 | 417.7884 | 408.209 | 393.9245
4035.176 | 685.4105 | 418.3717 | 408.3841 | 393.5374
4036.176 | 684.6696 | 418.9303 | 408.5498 | 393.0419
4037.176 | 689.6641 | 419.2962 | 408.7515 | 393.0818
4038.176 | 689.7823 | 420.2977 | 408.6836 | 393.0893
4039.176 | 686.2128 | 420.5344 | 408.7307 | 392.5431
4040.176 | 680.052 | 420.4439 | 408.4235 | 392.3874
4041.176 | 675.8506 | 420.2703 | 407.9997 | 392.0423
4042.176 | 680.3752 | 420.0398 | 407.5924 | 392.157
4043.176 | 678.672 | 420.3156 | 407.1692 | 391.7374
4044.176 | 676.9263 | 420.3891 | 407.0073 | 391.7307
4045.176 | 679.8132 | 420.1481 | 406.8998 | 391.6416
4046.176 | 678.2604 | 420.1814 | 407.1992 | 391.5968
4047.176 | 678.7173 | 419.8277 | 407.6448 | 391.8382
4048.176 | 682.0259 | 419.2819 | 407.7356 | 391.512
4049.176 | 681.2838 | 419.3223 | 407.5872 | 391.254
4050.176 | 677.6822 | 419.0709 | 407.5907 | 390.586
4051.176 | 678.1904 | 419.3562 | 407.3761 | 390.2858
4052.176 | 678.671 | 419.286 | 407.2162 | 391.7318
4053.176 | 674.3196 | 419.6839 | 407.3612 | 391.9131
4054.176 | 669.7891 | 420.5726 | 408.0371 | 392.2681
4055.176 | 662.1493 | 421.1185 | 409.1666 | 393.5914
4056.176 | 662.4892 | 421.7334 | 410.1066 | 394.3426
4057.176 | 658.8987 | 421.9588 | 410.8625 | 394.8781
4058.176 | 657.5678 | 422.3208 | 411.3063 | 394.9477
4059.176 | 663.073 | 422.5762 | 411.6659 | 395.7291
4060.176 | 665.4485 | 422.8439 | 412.1151 | 396.2431
4061.176 | 671.5872 | 422.7713 | 412.0976 | 396.6949
4062.176 | 672.7145 | 422.5497 | 412.2689 | 396.8336
4063.176 | 669.5218 | 422.6398 | 412.2069 | 397.2987
4064.176 | 670.6574 | 422.8279 | 412.1741 | 397.3177
4065.176 | 670.2109 | 422.6439 | 412.2422 | 397.6077
4066.176 | 667.7211 | 422.4372 | 412.0272 | 397.976
4067.176 | 666 | 422.15 | 412.2641 | 398.109
4068.176 | 664.0888 | 422.5677 | 412.4224 | 397.7514
4069.176 | 667.7804 | 422.2668 | 412.126 | 398.6781
4070.176 | 668.2636 | 422.299 | 411.8498 | 398.5121
4071.176 | 668.9514 | 422.4875 | 412.1442 | 397.9453
4072.176 | 669.8556 | 422.2763 | 412.014 | 397.3557
4073.176 | 670.7786 | 422.0778 | 411.9812 | 397.0674
4074.176 | 670.1771 | 422.091 | 411.7019 | 397.0232
4075.176 | 669.4944 | 422.2007 | 411.8544 | 396.8766
4076.176 | 669.8788 | 422.534 | 411.937 | 396.3947
4077.176 | 671.0697 | 422.8282 | 411.7994 | 396.0114
4078.176 | 670.7572 | 422.4275 | 411.4423 | 396.9877
4079.176 | 671.4096 | 422.1274 | 411.3674 | 397.1977
4080.176 | 669.542 | 422.0819 | 412.0883 | 397.368
4081.176 | 671.0172 | 422.4712 | 412.393 | 397.7847
4082.176 | 671.0298 | 422.854 | 412.5951 | 397.6634
4083.176 | 669.9573 | 423.1703 | 412.2238 | 397.6435
4084.176 | 667.6755 | 423.2349 | 411.9992 | 397.1906
4085.176 | 665.4668 | 423.1777 | 411.7281 | 397.066
4086.176 | 665.4093 | 422.8155 | 411.3073 | 397.2254
4087.176 | 662.1108 | 422.7834 | 411.2853 | 397.2626
4088.176 | 661.3034 | 422.5286 | 411.0986 | 397.4656
4089.176 | 661.7028 | 422.6842 | 411.3325 | 397.4738
4090.176 | 659.9209 | 423.2998 | 411.3766 | 397.2714
4091.176 | 661.7567 | 424.0843 | 411.5961 | 397.295
4092.176 | 664.2628 | 425.0525 | 411.946 | 397.4491
4093.176 | 664.9735 | 425.3493 | 412.592 | 398.0035
4094.176 | 666.6993 | 425.865 | 412.5062 | 397.8483
4095.176 | 669.3315 | 426.6579 | 412.7382 | 397.7491
4096.176 | 670.8744 | 426.4409 | 412.879 | 398.2924
4097.176 | 672.5025 | 425.9644 | 412.8137 | 398.2911
4098.176 | 673.5943 | 426.071 | 412.7339 | 398.2111
4099.176 | 673.6596 | 426.1241 | 413.2703 | 398.1026
4100.176 | 673.8576 | 425.9916 | 413.8171 | 398.4657
4101.176 | 674.9449 | 425.6783 | 413.7898 | 398.6879
4102.176 | 676.9039 | 425.5162 | 413.4545 | 398.4963
4103.176 | 680.3239 | 425.0517 | 413.4899 | 398.2723
4104.176 | 682.5993 | 424.703 | 413.9479 | 397.985
4105.176 | 685.8099 | 424.9662 | 414.544 | 398.0064
4106.176 | 685.3004 | 425.0361 | 414.9854 | 398.1903
4107.176 | 683.5933 | 424.6598 | 415.0855 | 398.7847
4108.176 | 683.5752 | 424.45 | 415.011 | 398.8689
4109.176 | 685.1682 | 424.6179 | 414.7956 | 398.5872
4110.176 | 683.9391 | 424.9632 | 415.1117 | 398.3952
4111.176 | 683.9923 | 425.5003 | 415.5003 | 399.1722
4112.176 | 683.8153 | 426.0127 | 416.0221 | 399.3339
4113.176 | 684.479 | 426.3667 | 416.146 | 399.9101
4114.176 | 682.504 | 426.7285 | 416.4944 | 400.6787
4115.176 | 679.7628 | 426.8594 | 416.7124 | 400.5372
4116.176 | 678.0478 | 427.2157 | 416.5524 | 400.5373
4117.176 | 676.2296 | 427.4279 | 416.4905 | 400.7153
4118.176 | 673.8494 | 427.6358 | 416.3195 | 400.896
4119.176 | 671.1137 | 428.0979 | 416.3839 | 401.0169
4120.176 | 667.5815 | 428.7516 | 416.2966 | 400.9002
4121.176 | 663.9861 | 429.5568 | 416.2525 | 401.4645
4122.176 | 660.1886 | 430.7845 | 416.3436 | 402.2965
4123.176 | 658.7508 | 431.5113 | 416.7323 | 403.403
4124.176 | 657.9688 | 431.6032 | 416.9302 | 403.6836
4125.176 | 657.8799 | 431.1286 | 416.5302 | 405.0827
4126.176 | 656.7352 | 431.0766 | 415.9028 | 405.4444
4127.176 | 657.1587 | 431.331 | 415.652 | 405.0992
4128.176 | 655.8959 | 431.6183 | 415.692 | 406.0637
4129.176 | 654.9213 | 431.9291 | 416.1644 | 407.2138
4130.176 | 655.9457 | 432.3997 | 416.6478 | 407.531
4131.176 | 657.8267 | 432.8286 | 417.2493 | 408.2149
4132.176 | 657.6278 | 433.1467 | 417.4403 | 407.9889
4133.176 | 660.1107 | 433.7932 | 417.661 | 408.2482
4134.176 | 661.0387 | 433.6676 | 417.8695 | 408.7037
4135.176 | 658.3285 | 433.6252 | 417.9678 | 408.3704
4136.176 | 658.9858 | 433.8281 | 417.6131 | 408.1668
4137.176 | 659.8219 | 434.1998 | 417.7074 | 408.744
4138.176 | 661.9155 | 434.7987 | 417.5568 | 408.3525
4139.176 | 664.0154 | 435.8804 | 417.6174 | 408.4038
4140.176 | 665.9052 | 435.5758 | 417.6233 | 409.0897
4141.176 | 668.8466 | 435.5139 | 417.6013 | 409.0911
4142.176 | 672.8255 | 435.0701 | 417.5449 | 410.2994
4143.176 | 675.5509 | 434.976 | 417.73 | 409.8965
4144.176 | 680.8168 | 435.7822 | 417.8613 | 410.0125
4145.176 | 685.648 | 435.414 | 418.2595 | 409.829
4146.176 | 691.3484 | 435.3366 | 418.8487 | 409.2792
4147.176 | 696.3857 | 436.2419 | 419.9453 | 410.3262
4148.176 | 699.8684 | 436.2945 | 420.5133 | 410.307
4149.176 | 703.7198 | 436.254 | 420.4821 | 410.3126
4150.176 | 707.6745 | 436.2083 | 420.6719 | 410.2121
4151.176 | 710.0716 | 436.3199 | 421.0769 | 409.83
4152.176 | 716.0848 | 436.5834 | 421.6089 | 409.4102
4153.176 | 720.8937 | 436.1536 | 422.1221 | 409.809
4154.176 | 723.5337 | 436.0978 | 422.534 | 409.8466
4155.176 | 725.0408 | 435.5904 | 422.8921 | 410.1615
4156.176 | 724.8604 | 435.4085 | 422.9875 | 410.8972
4157.176 | 722.74 | 435.1552 | 422.7529 | 411.2543
4158.176 | 721.0114 | 435.033 | 422.5846 | 411.966
4159.176 | 717.221 | 434.9926 | 422.5884 | 412.1401
4160.176 | 715.2437 | 434.6789 | 422.4276 | 412.4339
4161.176 | 713.5294 | 434.2305 | 422.1906 | 412.503
4162.176 | 710.7693 | 434.6348 | 422.3146 | 413.1304
4163.176 | 706.4603 | 434.6617 | 422.4277 | 413.9644
4164.176 | 703.6043 | 434.9059 | 422.646 | 414.4354
4165.176 | 701.639 | 435.2132 | 422.6156 | 415.9841
4166.176 | 700.1087 | 434.9741 | 422.7512 | 417.044
4167.176 | 699.0381 | 434.7358 | 423.4328 | 417.1103
4168.176 | 698.8414 | 434.7268 | 423.7454 | 417.1375
4169.176 | 695.4378 | 434.67 | 423.9969 | 416.8615
4170.176 | 693.4891 | 434.7497 | 424.1951 | 416.4989
4171.176 | 694.6874 | 434.5711 | 424.3881 | 416.2071
4172.176 | 695.4342 | 434.7961 | 424.5416 | 415.8469
4173.176 | 696.5292 | 434.8269 | 424.6818 | 415.834
4174.176 | 697.607 | 434.8221 | 424.5749 | 415.8378
4175.176 | 699.576 | 435.1332 | 424.2984 | 415.9253
4176.176 | 703.1965 | 435.4601 | 424.4737 | 415.8181
4177.176 | 704.7337 | 435.5543 | 424.9895 | 415.6136
4178.176 | 704.1045 | 435.8186 | 425.5475 | 415.921
4179.176 | 703.2429 | 436.0968 | 426.4172 | 416.9477
4180.176 | 699.318 | 436.6636 | 426.9498 | 417.9102
4181.176 | 697.6289 | 436.8668 | 427.223 | 418.1836
4182.176 | 697.1758 | 436.9326 | 427.2868 | 418.4395
4183.176 | 694.8478 | 436.7461 | 428.4421 | 418.1976
4184.176 | 691.5932 | 436.8672 | 429.9038 | 418.4673
4185.176 | 690.0111 | 437.0792 | 429.8373 | 418.5068
4186.176 | 688.08 | 436.9792 | 429.6617 | 418.3847
4187.176 | 687.5821 | 437.1769 | 429.8455 | 418.2994
4188.176 | 684.9924 | 437.4709 | 429.5606 | 418.7305
4189.176 | 679.3843 | 437.7014 | 429.6541 | 418.7379
4190.176 | 675.1399 | 437.7582 | 429.7263 | 418.6416
4191.176 | 672.8183 | 438.3005 | 430.127 | 418.4664
4192.176 | 672.0711 | 438.5379 | 430.3706 | 418.624
4193.176 | 671.2654 | 439.0065 | 430.6555 | 418.4597
4194.176 | 668.5651 | 439.4078 | 430.687 | 418.7389
4195.176 | 666.3093 | 439.6539 | 430.4689 | 419.3155
4196.176 | 665.5184 | 439.4783 | 430.6024 | 419.7812
4197.176 | 665.1227 | 439.584 | 430.4093 | 419.7533
4198.176 | 667.3534 | 439.7587 | 430.3548 | 420.8508
4199.176 | 668.7325 | 440.2216 | 430.3324 | 420.7
4200.176 | 667.9567 | 440.5728 | 430.6311 | 420.5766
4201.176 | 667.8698 | 440.9442 | 431.241 | 420.2831
4202.176 | 670.1067 | 441.1679 | 431.5832 | 420.4303
4203.1917 | 672.7377 | 441.1935 | 431.5818 | 419.8193
4204.176 | 674.4138 | 441.4158 | 432.402 | 419.4268
4205.176 | 675.0353 | 441.5838 | 432.4107 | 419.0852
4206.176 | 676.7593 | 441.7366 | 432.8694 | 419.5475
4207.176 | 677.5538 | 441.8291 | 433.0845 | 420.0373
4208.176 | 678.6748 | 442.1577 | 432.9458 | 420.218
4209.176 | 679.4436 | 441.9549 | 432.9078 | 421.056
4210.176 | 679.1508 | 442.0016 | 433.3556 | 422.1157
4211.176 | 676.3026 | 442.166 | 433.6515 | 422.18
4212.176 | 674.7726 | 442.9087 | 434.259 | 422.3737
4213.176 | 674.4865 | 443.8136 | 434.6948 | 423.0125
4214.176 | 673.7555 | 445.0016 | 434.9573 | 423.7464
4215.176 | 671.1397 | 445.1928 | 434.7532 | 424.6493
4216.176 | 668.0285 | 445.3215 | 434.7939 | 425.0172
4217.176 | 665.774 | 445.5792 | 434.7639 | 424.8082
4218.176 | 664.2165 | 446.3708 | 434.9941 | 424.9633
4219.176 | 662.5715 | 446.7394 | 434.826 | 425.0178
4220.176 | 662.093 | 447.3528 | 435.345 | 424.7474
4221.176 | 668.7113 | 447.129 | 435.2284 | 425.5482
4222.176 | 673.9534 | 447.1876 | 435.2842 | 425.4377
4223.176 | 677.1538 | 447.5729 | 435.359 | 425.5451
4224.176 | 678.6305 | 448.1073 | 435.3081 | 425.5363
4225.176 | 678.5408 | 448.418 | 435.3083 | 425.6258
4226.176 | 679.1516 | 448.8979 | 435.4873 | 425.9649
4227.176 | 676.151 | 449.7784 | 435.7737 | 426.2011
4228.176 | 673.9825 | 450.5254 | 436.6615 | 427.0758
4229.176 | 670.6393 | 450.5507 | 437.0645 | 427.0131
4230.176 | 669.9459 | 450.173 | 437.4631 | 427.3561
4231.176 | 668.9561 | 449.913 | 437.4342 | 428.6332
4232.176 | 668.1623 | 449.7941 | 437.7138 | 428.4405
4233.176 | 670.4159 | 449.5915 | 437.7093 | 428.5813
4234.176 | 670.2467 | 449.8036 | 437.4247 | 428.4237
4235.176 | 672.9367 | 449.7702 | 437.3521 | 428.2493
4236.176 | 674.7048 | 449.8976 | 437.2381 | 428.4107
4237.176 | 675.3514 | 450.5663 | 437.0088 | 428.2561
4238.176 | 675.0056 | 450.762 | 437.2554 | 428.6095
4239.176 | 675.7668 | 450.5199 | 437.7634 | 430.0539
4240.176 | 678.0973 | 450.8305 | 438.25 | 430.084
4241.176 | 679.6857 | 450.6382 | 438.5882 | 430.4717
4242.176 | 680.791 | 450.45 | 438.5867 | 430.1832
4243.176 | 680.3318 | 450.0967 | 438.382 | 430.1988
4244.176 | 680.1428 | 449.4521 | 438.7623 | 429.7433
4245.176 | 680.4888 | 448.9036 | 438.5106 | 429.8618
4246.176 | 681.1859 | 448.8301 | 438.2175 | 429.2993
4247.176 | 681.2481 | 449.4049 | 438.2684 | 429.617
4248.176 | 683.4175 | 449.5896 | 438.2941 | 429.4221
4249.176 | 684.4754 | 449.8302 | 438.1445 | 429.0601
4250.176 | 682.7474 | 450.4172 | 438.0512 | 428.8152
4251.176 | 681.848 | 451.1971 | 438.9328 | 428.4846
4252.176 | 679.272 | 451.6153 | 439.1537 | 429.0701
4253.176 | 680.8529 | 451.9814 | 439.2587 | 429.2911
4254.176 | 682.2244 | 451.7242 | 439.2143 | 429.5823
4255.176 | 682.007 | 451.4916 | 439.3151 | 429.5108
4256.176 | 682.5755 | 451.7939 | 439.105 | 430.158
4257.176 | 681.9852 | 451.7132 | 438.9107 | 430.0424
4258.176 | 682.3741 | 451.6861 | 439.031 | 429.5169
4259.176 | 682.711 | 452.082 | 438.8325 | 430.5733
4260.176 | 679.0632 | 453.8748 | 439.1255 | 431.1288
4261.176 | 676.7825 | 454.5115 | 440.2965 | 431.288
4262.1917 | 675.8293 | 455.7792 | 441.3486 | 431.3587
4263.1917 | 673.2295 | 456.4266 | 442.5678 | 432.9085
4264.176 | 672.3944 | 457.3286 | 443.3456 | 433.277
4265.176 | 671.3004 | 458.6499 | 444.233 | 434.2922
4266.176 | 668.3835 | 458.8844 | 444.8164 | 435.0004
4267.176 | 666.635 | 458.7886 | 444.9589 | 435.5334
4268.176 | 665.2264 | 458.6699 | 445.0104 | 435.1674
4269.176 | 664.9083 | 458.7008 | 445.048 | 435.7487
4270.176 | 667.314 | 458.3739 | 445.5641 | 435.518
4271.176 | 668.2089 | 458.6843 | 445.703 | 435.7017
4272.176 | 666.9142 | 459.2655 | 445.8319 | 435.4767
4273.176 | 666.4171 | 459.4717 | 445.8642 | 435.2418
4274.176 | 665.8785 | 459.7893 | 445.9708 | 435.5395
4275.176 | 670.1119 | 460.1113 | 445.7499 | 435.3727
4276.176 | 678.3413 | 460.7006 | 445.5299 | 434.8206
4277.176 | 679.2173 | 461.2125 | 445.3938 | 434.5084
4278.176 | 678.6742 | 461.494 | 445.3619 | 434.3851
4279.176 | 680.588 | 461.547 | 445.3669 | 434.5334
4280.176 | 684.259 | 461.7723 | 445.8957 | 434.3123
4281.176 | 686.6697 | 461.5111 | 445.8692 | 434.7533
4282.176 | 687.2686 | 461.9919 | 446.1114 | 434.9359
4283.176 | 688.3454 | 462.861 | 446.1349 | 434.995
4284.176 | 686.9749 | 463.5617 | 446.2522 | 435.3671
4285.176 | 687.1892 | 463.803 | 446.6872 | 435.8314
4286.176 | 687.7401 | 463.6413 | 446.7381 | 435.4165
4287.176 | 687.3457 | 463.8108 | 446.4159 | 435.6063
4288.176 | 684.2424 | 464.4939 | 446.1932 | 435.6913
4289.176 | 683.4264 | 464.2569 | 446.7066 | 436.0578
4290.176 | 682.2855 | 464.6049 | 446.9022 | 436.2888
4291.176 | 678.8655 | 465.1735 | 446.9359 | 436.3511
4292.176 | 676.743 | 466.1744 | 446.7319 | 437.1994
4293.176 | 675.4926 | 466.879 | 447.1689 | 437.7886
4294.176 | 681.11 | 467.222 | 447.2848 | 438.7415
4295.176 | 682.6866 | 467.5346 | 448.053 | 439.1226
4296.176 | 679.4852 | 467.6426 | 448.7883 | 439.7163
4297.176 | 677.6422 | 467.8584 | 449.8353 | 439.5136
4298.176 | 675.6363 | 467.9221 | 450.6074 | 439.7707
4299.176 | 674.524 | 467.5135 | 450.9006 | 440.633
4300.176 | 675.2553 | 466.6889 | 450.7496 | 440.5798
4301.176 | 676.2078 | 466.458 | 450.5765 | 440.6736
4302.176 | 677.6799 | 466.4255 | 451.5583 | 440.4358
4303.176 | 681.2793 | 467.209 | 452.1491 | 440.0244
4304.176 | 682.9552 | 467.1757 | 452.1219 | 439.4069
4305.176 | 684.0696 | 467.5127 | 452.3485 | 439.3906
4306.176 | 684.1801 | 468.1551 | 452.5824 | 438.9626
4307.176 | 685.4537 | 468.0485 | 452.4747 | 439.7629
4308.176 | 685.6114 | 468.368 | 452.4339 | 439.9281
4309.176 | 683.0987 | 468.9808 | 452.739 | 440.0005
4310.176 | 680.9711 | 469.3265 | 453.1438 | 439.4457
4311.176 | 677.7249 | 469.524 | 453.4168 | 439.8706
4312.176 | 674.994 | 468.9774 | 453.4181 | 439.8436
4313.176 | 674.0101 | 468.8641 | 453.3403 | 439.9736
4314.176 | 675.7105 | 469.2788 | 453.1648 | 439.7233
4315.176 | 680.5647 | 469.5329 | 453.2678 | 439.6516
4316.176 | 681.5022 | 470.0374 | 453.3549 | 439.2827
4317.176 | 682.2807 | 470.3275 | 453.3022 | 439.1958
4318.176 | 682.5749 | 470.5111 | 453.2966 | 439.0937
4319.176 | 684.942 | 470.8917 | 453.4927 | 439.8228
4320.176 | 684.5552 | 471.473 | 454.0866 | 440.0254
4321.176 | 683.1666 | 471.9455 | 454.5116 | 440.3738
4322.176 | 681.6419 | 472.886 | 454.3819 | 440.9209
4323.176 | 683.2269 | 474.056 | 454.1001 | 441.9586
4324.176 | 685.0837 | 474.3441 | 454.3767 | 441.738
4325.176 | 685.123 | 474.5838 | 454.328 | 441.8949
4326.176 | 683.4807 | 474.8261 | 454.7086 | 441.883
4327.176 | 681.166 | 475.0514 | 455.3901 | 442.0526
4328.176 | 679.0682 | 475.0211 | 455.8902 | 442.0115
4329.176 | 677.7976 | 474.983 | 455.8095 | 442.8551
4330.176 | 679.0778 | 474.8878 | 455.5909 | 442.8599
4331.176 | 680.035 | 475.0892 | 455.0154 | 442.793
4332.176 | 682.5416 | 474.8749 | 454.5889 | 442.2667
4333.176 | 682.0417 | 475.6179 | 454.428 | 441.5925
4334.176 | 682.5947 | 475.5731 | 454.4216 | 441.402
4335.176 | 688.2048 | 475.7425 | 454.7342 | 441.7012
4336.176 | 688.8333 | 475.7271 | 455.298 | 443.2282
4337.176 | 684.8567 | 476.2271 | 455.9642 | 443.587
4338.176 | 679.409 | 477.7899 | 456.7387 | 444.0833
4339.176 | 672.9866 | 478.2568 | 457.5856 | 444.8857
4340.176 | 673.3033 | 479.0989 | 458.0607 | 445.3369
4341.176 | 680.0613 | 479.4365 | 458.736 | 445.6706
4342.176 | 680.87 | 479.8946 | 458.7536 | 445.6594
4343.176 | 682.5142 | 480.2274 | 459.3303 | 446.0403
4344.176 | 684.9196 | 479.9531 | 459.3555 | 446.5088
4345.176 | 684.7091 | 479.878 | 459.6427 | 446.487
4346.176 | 682.3806 | 481.1799 | 459.3639 | 447.723
4347.176 | 681.7986 | 480.8309 | 459.597 | 447.7851
4348.176 | 679.3628 | 480.6425 | 459.758 | 448.3382
4349.176 | 678.0267 | 480.9468 | 459.7278 | 447.9523
4350.176 | 678.6308 | 480.7869 | 459.9929 | 448.1126
4351.176 | 681.6496 | 481.429 | 460.7044 | 447.7825
4352.176 | 684.5574 | 481.379 | 461.0384 | 447.6126
4353.176 | 685.031 | 480.9074 | 461.2895 | 447.4371
4354.176 | 686.7891 | 480.346 | 461.1732 | 446.8526
4355.176 | 689.318 | 480.3835 | 461.1243 | 446.3938
4356.176 | 691.8833 | 481.0201 | 461.4381 | 446.4301
4357.176 | 694.4914 | 480.8325 | 461.457 | 445.8669
4358.176 | 694.6419 | 480.6721 | 461.9921 | 445.4788
4359.176 | 696.9711 | 480.474 | 462.0699 | 445.7102
4360.176 | 696.5353 | 480.6169 | 461.7466 | 445.8416
4361.176 | 696.8952 | 480.7765 | 462.3116 | 446.6102
4362.176 | 696.1997 | 481.1766 | 463.3742 | 447.9908
4363.176 | 696.563 | 480.5845 | 463.5238 | 448.8062
4364.176 | 697.4161 | 480.137 | 463.4463 | 449.4913
4365.176 | 698.7438 | 479.5984 | 463.1697 | 449.7632
4366.176 | 699.8691 | 479.4847 | 462.6244 | 449.7474
4367.176 | 699.6087 | 479.6101 | 462.3821 | 449.7276
4368.176 | 698.8122 | 480.1795 | 462.1564 | 449.5626
4369.176 | 697.078 | 480.4558 | 461.8959 | 449.6421
4370.176 | 696.1604 | 481.2838 | 462.1144 | 450.1458
4371.176 | 694.3327 | 481.2399 | 462.7376 | 450.5878
4372.176 | 692.6438 | 481.2942 | 463.2999 | 451.1623
4373.176 | 690.1364 | 481.0764 | 463.3608 | 451.5641
4374.176 | 689.0463 | 480.8098 | 463.4959 | 452.116
4375.176 | 685.7553 | 480.5919 | 463.4567 | 452.3197
4376.176 | 686.006 | 480.1217 | 463.379 | 452.1541
4377.176 | 683.8113 | 479.3582 | 463.3234 | 451.8288
4378.176 | 681.812 | 478.8294 | 463.3873 | 452.679
4379.176 | 679.9937 | 478.9282 | 463.5782 | 452.5677
4380.176 | 681.9408 | 479.6233 | 464.112 | 453.0014
4381.176 | 679.9129 | 480.3916 | 464.4085 | 453.387
4382.176 | 677.3988 | 480.9449 | 464.9783 | 453.1983
4383.176 | 674.0471 | 481.7208 | 465.5188 | 453.5475
4384.176 | 673.1062 | 482.2792 | 466.0504 | 453.4626
4385.176 | 669.1139 | 482.6772 | 466.2547 | 453.835
4386.176 | 665.6387 | 482.199 | 466.234 | 454.0901
4387.176 | 667.093 | 481.7353 | 466.2033 | 453.4007
4388.176 | 671.2123 | 481.6767 | 466.0463 | 453.0754
4389.176 | 673.3959 | 481.5841 | 465.7847 | 452.8774
4390.176 | 672.9908 | 481.9798 | 465.4892 | 453.0696
4391.176 | 675.1207 | 482.1473 | 465.1093 | 453.206
4392.176 | 676.3053 | 482.0378 | 464.9703 | 453.1301
4393.176 | 677.6525 | 481.8807 | 465.0832 | 453.0292
4394.176 | 678.4923 | 482.5562 | 465.4652 | 453.0208
4395.176 | 676.6462 | 482.6455 | 466.1381 | 453.2952
4396.176 | 673.1132 | 483.2912 | 466.5439 | 453.9944
4397.176 | 670.1692 | 484.6627 | 467.1485 | 454.7259
4398.176 | 668.8646 | 484.8827 | 467.3509 | 455.2806
4399.176 | 666.0104 | 484.2399 | 467.2109 | 454.8986
4400.176 | 666.9954 | 483.6491 | 466.9363 | 455.7265
4401.176 | 668.0428 | 483.5902 | 466.5372 | 456.3523
4402.176 | 669.5971 | 484.44 | 466.7455 | 456.276
4403.176 | 669.3446 | 485.164 | 467.0456 | 457.4574
4404.176 | 669.5359 | 485.5881 | 467.6341 | 457.8443
4405.176 | 670.3434 | 485.7393 | 468.183 | 458.4825
4406.176 | 671.8391 | 486.9506 | 468.3138 | 458.2721
4407.176 | 670.6567 | 487.4429 | 469.2556 | 458.9355
4408.176 | 668.0564 | 488.5168 | 469.9434 | 459.8565
4409.176 | 666.8104 | 488.5726 | 470.0092 | 460.0909
4410.176 | 668.328 | 489.0586 | 469.678 | 460.0895
4411.176 | 672.1294 | 489.1462 | 469.9592 | 459.5407
4412.176 | 671.6328 | 489.54 | 470.4445 | 460.1438
4413.176 | 670.4926 | 489.8732 | 470.9874 | 459.9497
4414.176 | 668.7833 | 490.1286 | 471.6472 | 460.597
4415.176 | 669.6046 | 490.4461 | 472.1264 | 460.2821
4416.176 | 668.9721 | 490.7468 | 472.5198 | 461.3925
4417.176 | 666.0742 | 491.4796 | 472.7856 | 461.6483
4418.176 | 665.4561 | 491.4236 | 472.7203 | 462.2674
4419.176 | 661.8317 | 492.1838 | 473.5679 | 462.9027
4420.176 | 659.8477 | 493.3897 | 473.6988 | 464.1236
4421.176 | 657.2696 | 494.8323 | 474.0539 | 464.2789
4422.176 | 657.5508 | 494.9229 | 474.1989 | 464.9697
4423.176 | 655.9282 | 494.7163 | 474.0655 | 465.1878
4424.176 | 655.8387 | 493.9305 | 474.1231 | 465.499
4425.176 | 655.0702 | 493.7018 | 474.4739 | 466.8141
4426.176 | 654.2193 | 493.6662 | 474.6014 | 466.5818
4427.176 | 654.8837 | 494.2663 | 474.53 | 466.1899
4428.176 | 655.942 | 494.776 | 474.3377 | 465.8958
4429.176 | 661.2859 | 494.7926 | 474.0643 | 465.1937
4430.176 | 664.3418 | 494.4757 | 473.475 | 464.5911
4431.176 | 666.8136 | 494.9015 | 472.9857 | 464.0812
4432.176 | 667.832 | 495.3282 | 472.6602 | 463.4163
4433.176 | 668.3499 | 495.9645 | 472.7172 | 462.8124
4434.1917 | 668.1083 | 495.4547 | 473.014 | 463.7652
4435.176 | 667.4986 | 495.0479 | 473.2484 | 463.7381
4436.176 | 667.4732 | 494.9453 | 473.5251 | 464.9764
4437.176 | 668.0101 | 494.8385 | 473.6421 | 465.0001
4438.176 | 668.4349 | 494.8813 | 473.9574 | 464.7963
4439.176 | 670.3276 | 495.0318 | 474.3647 | 465.0695
4440.176 | 672.1997 | 495.1717 | 474.5557 | 466.2587
4441.176 | 671.9999 | 495.1112 | 474.9286 | 466.3185
4442.176 | 669.7527 | 495.0159 | 475.2384 | 466.2454
4443.176 | 672.8446 | 494.6515 | 475.3874 | 465.9615
4444.176 | 677.2682 | 493.9439 | 475.4478 | 466.6278
4445.176 | 679.8271 | 493.7303 | 475.4292 | 466.4161
4446.176 | 679.8207 | 494.1847 | 475.9292 | 466.6848
4447.176 | 679.7114 | 494.0314 | 476.055 | 466.805
4448.176 | 679.8271 | 493.6868 | 476.1357 | 467.0681
4449.176 | 679.819 | 493.4888 | 476.1533 | 468.0194
4450.176 | 680.9752 | 493.6559 | 476.1974 | 468.354
4451.176 | 680.5717 | 493.6886 | 476.3593 | 468.0184
4452.176 | 682.1434 | 493.8139 | 476.2725 | 468.8212
4453.176 | 684.4826 | 494.3763 | 477.0949 | 468.5139
4454.176 | 685.4653 | 494.9145 | 477.9938 | 469.2053
4455.176 | 686.3572 | 494.9982 | 478.2896 | 469.3809
4456.176 | 687.3499 | 495.6173 | 478.4318 | 470.0693
4457.176 | 689.3952 | 496.0014 | 478.6591 | 470.6025
4458.176 | 691.4245 | 495.8699 | 479.3385 | 470.9846
4459.176 | 691.0191 | 495.5363 | 480.2367 | 471.1662
4460.176 | 688.1101 | 495.7121 | 480.4711 | 470.9353
4461.176 | 682.8239 | 495.8924 | 480.3568 | 471.0997
4462.176 | 679.8646 | 496.8351 | 480.2404 | 471.223
4463.176 | 678.1792 | 496.5903 | 480.1129 | 471.365
4464.176 | 677.16 | 496.0386 | 479.8502 | 471.3986
4465.176 | 673.9588 | 495.6661 | 479.3766 | 471.3928
4466.176 | 671.6939 | 494.9642 | 478.9805 | 471.1264
4467.176 | 668.3086 | 494.2129 | 478.979 | 470.9718
4468.176 | 665.3027 | 493.5796 | 479.038 | 471.5427
4469.176 | 663.8211 | 493.7205 | 479.2889 | 471.3701
4470.176 | 661.6259 | 493.9262 | 479.1335 | 472.4554
4471.176 | 663.34 | 493.4826 | 478.8444 | 471.8803
4472.176 | 663.5409 | 494.0739 | 478.5648 | 471.4667
4473.176 | 663.8497 | 495.3466 | 478.4753 | 471.0374
4474.176 | 665.2386 | 496.7881 | 478.2399 | 470.6546
4475.176 | 664.8503 | 496.7026 | 478.5987 | 470.2199
4476.176 | 663.3775 | 497.0655 | 479.5084 | 471.058
4477.176 | 662.9174 | 497.7041 | 479.3789 | 470.833
4478.1917 | 661.3469 | 497.5374 | 479.5323 | 471.0958
4479.176 | 660.7246 | 497.8967 | 479.7265 | 470.6811
4480.176 | 658.9341 | 498.9383 | 479.6137 | 470.4316
4481.176 | 656.1785 | 499.7086 | 479.7981 | 470.8397
4482.176 | 652.7947 | 500.1871 | 481.0002 | 471.1637
4483.176 | 654.7027 | 500.46 | 481.5423 | 471.3473
4484.176 | 659.1989 | 500.5349 | 482.948 | 471.6204
4485.176 | 659.6474 | 500.3735 | 482.8679 | 472.3052
4486.176 | 663.0655 | 500.249 | 482.8895 | 473.1572
4487.176 | 665.0019 | 499.8991 | 482.893 | 473.5126
4488.176 | 664.9189 | 500.0597 | 483.3223 | 473.1083
4489.176 | 662.5377 | 500.6582 | 483.4198 | 473.0462
4490.176 | 663.7837 | 501.2908 | 483.8497 | 473.1354
4491.176 | 665.3974 | 501.2157 | 484.7353 | 473.853
4492.176 | 668.0572 | 502.2552 | 485.0304 | 474.4681
4493.176 | 673.1374 | 503.1063 | 485.0893 | 474.88
4494.176 | 674.3074 | 503.2404 | 485.0934 | 475.2279
4495.176 | 674.887 | 503.1587 | 485.0943 | 476.5219
4496.176 | 675.9109 | 503.2286 | 485.1913 | 476.8567
4497.176 | 679.6402 | 503.3871 | 485.5413 | 476.95
4498.176 | 679.5254 | 503.8285 | 485.4592 | 477.0129
4499.176 | 677.6247 | 504.4334 | 485.6718 | 477.2059
4500.176 | 675.7016 | 505.1806 | 485.5719 | 476.8821
4501.176 | 674.7392 | 505.3149 | 485.5117 | 476.8164
4502.176 | 673.4319 | 504.8779 | 485.475 | 476.5315
4503.176 | 671.8413 | 504.3978 | 485.5973 | 476.8275
4504.176 | 667.5659 | 503.7179 | 485.0028 | 477.0527
4505.176 | 665.7685 | 503.7442 | 485.1727 | 476.7314
4506.176 | 662.8736 | 503.5405 | 485.4556 | 476.7564
4507.176 | 662.1981 | 502.4432 | 485.4199 | 476.6929
4508.176 | 661.2636 | 502.2243 | 485.4044 | 476.3751
4509.176 | 658.0169 | 502.1703 | 484.9305 | 476.1394
4510.176 | 656.1794 | 502.2312 | 484.8949 | 476.4392
4511.176 | 655.3236 | 501.3545 | 485.9987 | 476.368
4512.176 | 660.207 | 500.6077 | 485.7696 | 476.5856
4513.176 | 662.2232 | 500.1077 | 485.1171 | 476.6928
4514.176 | 661.1873 | 500.2959 | 484.49 | 475.9226
4515.176 | 659.393 | 500.039 | 484.0759 | 475.4931
4516.176 | 659.8423 | 500.2777 | 483.8676 | 475.1782
4517.176 | 662.1658 | 500.3796 | 483.8425 | 475.2372
4518.176 | 664.4281 | 500.418 | 483.6519 | 475.2703
4519.176 | 665.8988 | 500.6262 | 483.5644 | 475.2827
4520.176 | 668.695 | 500.6798 | 483.5906 | 475.5458
4521.176 | 671.6291 | 500.8335 | 483.4566 | 475.8967
4522.176 | 671.5966 | 501.5849 | 483.7177 | 475.3452
4523.176 | 674.8229 | 501.8397 | 484.3212 | 474.9563
4524.176 | 673.9737 | 502.0489 | 484.6174 | 474.8695
4525.176 | 672.696 | 501.4355 | 484.6948 | 475.3058
4526.176 | 674.4682 | 501.2191 | 484.5097 | 475.9706
4527.176 | 674.8178 | 501.5756 | 484.3966 | 476.0676
4528.176 | 676.4117 | 501.9763 | 484.9069 | 475.6973
4529.176 | 676.9248 | 502.2674 | 485.1915 | 475.2637
4530.176 | 679.3896 | 502.5138 | 484.7711 | 475.421
4531.176 | 681.0387 | 502.1056 | 484.4632 | 476.1256
4532.176 | 681.0405 | 501.4102 | 484.3292 | 476.0585
4533.176 | 680.3609 | 500.8637 | 483.9689 | 475.7509
4534.176 | 683.1507 | 500.3389 | 483.8994 | 475.6593
4535.176 | 685.6898 | 500.4435 | 484.0806 | 475.8577
4536.176 | 687.3962 | 500.8392 | 484.2906 | 476.6793
4537.176 | 690.2367 | 501.0607 | 484.7213 | 477.259
4538.176 | 690.9055 | 501.6357 | 484.9135 | 478.045
4539.176 | 690.9172 | 501.7961 | 485.3101 | 478.1169
4540.176 | 690.0375 | 502.1613 | 485.5282 | 477.5646
4541.176 | 688.7499 | 502.7744 | 486.0348 | 478.0601
4542.176 | 686.4187 | 502.977 | 486.5666 | 479.6451
4543.176 | 686.8255 | 502.8995 | 486.6892 | 479.5662
4544.176 | 687.094 | 503.1903 | 486.4701 | 479.4585
4545.176 | 687.1976 | 503.9985 | 486.802 | 479.3691
4546.176 | 686.1145 | 504.7711 | 487.2786 | 479.3324
4547.176 | 686.6114 | 505.9792 | 487.469 | 479.7134
4548.176 | 685.7992 | 507.0881 | 487.8113 | 479.9416
4549.176 | 685.0348 | 507.4795 | 488.186 | 480.2762
4550.176 | 678.6251 | 508.6017 | 488.7263 | 480.3637
4551.176 | 672.9928 | 509.4219 | 489.229 | 480.0924
4552.176 | 671.4428 | 510.0474 | 489.5182 | 480.4112
4553.176 | 667.7043 | 511.0224 | 489.7624 | 481.1975
4554.176 | 664.4037 | 511.7673 | 489.9962 | 481.8258
4555.176 | 661.1215 | 511.1979 | 491.1156 | 482.4307
4556.176 | 659.6587 | 511.4987 | 490.9048 | 483.2824
4557.176 | 657.8711 | 511.5285 | 490.8786 | 483.7541
4558.176 | 659.4696 | 511.7234 | 491.0183 | 484.3124
4559.176 | 662.0951 | 512.072 | 490.9179 | 484.4017
4560.176 | 658.872 | 512.7927 | 491.7033 | 484.5847
4561.176 | 655.4693 | 513.9635 | 491.7978 | 484.5864
4562.176 | 655.3363 | 514.5587 | 491.9718 | 485.1381
4563.1917 | 656.4245 | 514.661 | 492.3228 | 485.4347
4564.176 | 656.4257 | 514.6303 | 492.0988 | 486.3723
4565.176 | 654.977 | 514.8041 | 491.7451 | 486.2295
4566.176 | 658.6678 | 515.3833 | 491.8572 | 486.642
4567.176 | 660.5529 | 515.6002 | 491.7354 | 486.5669
4568.176 | 662.2456 | 515.9623 | 491.8512 | 487.0969
4569.176 | 660.5235 | 516.1783 | 491.9767 | 487.2504
4570.176 | 660.573 | 516.5635 | 491.9462 | 487.7257
4571.176 | 660.0205 | 516.8147 | 492.1428 | 487.7283
4572.176 | 657.6867 | 516.6496 | 492.3938 | 487.514
4573.176 | 656.2005 | 516.8114 | 492.5052 | 487.2619
4574.176 | 651.9951 | 516.1296 | 492.524 | 486.6237
4575.176 | 650.6965 | 515.3279 | 492.3696 | 486.7872
4576.176 | 656.0466 | 515.0885 | 491.9311 | 486.6464
4577.176 | 654.366 | 515.3038 | 491.7608 | 486.0899
4578.176 | 657.0241 | 515.4683 | 491.5195 | 485.9306
4579.176 | 656.4805 | 515.558 | 491.5218 | 485.6974
4580.176 | 658.5414 | 515.2684 | 491.4651 | 485.2398
4581.176 | 659.2327 | 514.4013 | 491.2534 | 484.9565
4582.176 | 661.0573 | 514.0996 | 491.1929 | 484.5224
4583.176 | 660.4259 | 514.108 | 490.9477 | 484.6247
4584.176 | 663.9343 | 514.1468 | 490.8191 | 484.9044
4585.176 | 658.9472 | 515.1556 | 491.0695 | 484.7182
4586.176 | 659.7708 | 516.336 | 491.4775 | 484.3694
4587.176 | 661.948 | 516.6498 | 491.5712 | 483.9622
4588.176 | 660.5552 | 516.8879 | 491.5871 | 483.8993
4589.176 | 663.3294 | 517.4503 | 492.4915 | 483.6736
4590.176 | 671.2399 | 517.5926 | 492.4483 | 483.8805
4591.176 | 672.3677 | 517.2372 | 492.5089 | 483.7164
4592.176 | 669.163 | 516.9384 | 492.0296 | 483.6354
4593.176 | 669.8739 | 516.8336 | 491.6896 | 483.6943
4594.176 | 668.233 | 516.8451 | 491.9816 | 484.1701
4595.176 | 674.1646 | 516.3989 | 492.1119 | 484.0498
4596.176 | 673.4298 | 516.6738 | 492.1055 | 484.3197
4597.176 | 674.65 | 517.0165 | 491.9742 | 484.1212
4598.176 | 671.4868 | 517.5549 | 492.34 | 483.7597
4599.176 | 668.4241 | 517.7901 | 491.9744 | 483.1804
4600.176 | 671.4773 | 517.3933 | 491.8395 | 483.0767
4601.176 | 670.9669 | 517.2663 | 492.168 | 483.7927
4602.176 | 672.9004 | 517.2045 | 491.829 | 483.6226
4603.176 | 674.5492 | 516.2924 | 491.7689 | 483.2149
4604.176 | 673.3828 | 516.0994 | 492.066 | 483.1081
4605.176 | 676.68 | 515.8536 | 492.0262 | 482.8793
4606.176 | 674.5171 | 515.5983 | 491.6109 | 483.9818
4607.176 | 676.7318 | 516.7355 | 492.2073 | 483.4966
4608.176 | 678.9902 | 516.5429 | 492.4104 | 483.0022
4609.176 | 677.7218 | 516.2397 | 492.5665 | 483.0245
4610.176 | 677.4278 | 516.2314 | 492.8957 | 483.737
4611.176 | 673.4783 | 516.9745 | 493.0172 | 483.3964
4612.176 | 678.2384 | 517.4841 | 493.2072 | 483.2006
4613.176 | 675.3 | 517.609 | 493.6735 | 482.772
4614.176 | 675.279 | 517.6102 | 493.6761 | 482.5075
4615.176 | 675.8475 | 517.1793 | 493.6393 | 483.6528
4616.176 | 673.5454 | 516.8038 | 493.4449 | 483.482
4617.176 | 669.5141 | 517.3693 | 493.3025 | 483.0062
4618.176 | 666.85 | 516.8173 | 493.2919 | 482.6213
4619.176 | 662.4061 | 516.8273 | 493.2998 | 482.9972
4620.176 | 663.021 | 517.1789 | 493.1378 | 482.7623
4621.176 | 666.9497 | 517.2582 | 492.7561 | 482.5323
4622.176 | 666.824 | 517.6562 | 492.306 | 482.2438
4623.1917 | 669.177 | 517.7537 | 492.2303 | 482.5843
4624.176 | 670.49 | 518.3297 | 492.3627 | 483.6954
4625.176 | 666.7885 | 518.9735 | 492.6207 | 484.4604
4626.176 | 667.6619 | 520.3794 | 493.0037 | 484.4622
4627.176 | 665.5918 | 521.0288 | 493.5509 | 484.531
4628.176 | 665.4459 | 520.9764 | 493.6811 | 484.6278
4629.176 | 665.5343 | 520.997 | 493.8362 | 484.8524
4630.176 | 663.5752 | 521.0798 | 494.8869 | 485.0502
4631.176 | 666.1266 | 521.9385 | 494.9429 | 485.4616
4632.176 | 665.2338 | 521.5505 | 495.0086 | 485.5893
4633.176 | 666.9593 | 521.5123 | 495.015 | 486.1677
4634.176 | 669.0771 | 521.3656 | 495.3066 | 486.3774
4635.176 | 670.6624 | 521.7412 | 495.501 | 486.0512
4636.176 | 671.5596 | 522.102 | 495.5741 | 485.98
4637.176 | 668.9316 | 522.7223 | 495.5998 | 486.4514
4638.176 | 669.2602 | 522.864 | 496.0446 | 487.006
4639.176 | 669.3593 | 524.0604 | 496.8936 | 487.7048
4640.176 | 667.6623 | 524.6088 | 497.9978 | 487.7401
4641.176 | 668.0457 | 525.6005 | 498.0768 | 487.5148
4642.176 | 668.2784 | 526.269 | 497.7144 | 487.1631
4643.176 | 665.3343 | 525.4604 | 497.4125 | 487.7433
4644.176 | 666.2804 | 525.3617 | 497.4157 | 488.618
4645.176 | 660.8396 | 526.1412 | 497.466 | 489.3151
4646.176 | 660.8745 | 526.3987 | 497.4619 | 489.0672
4647.176 | 662.8858 | 526.1043 | 497.8026 | 488.3069
4648.176 | 668.425 | 526.224 | 497.9043 | 489.75
4649.176 | 668.1786 | 526.9382 | 498.1201 | 489.849
4650.176 | 662.8375 | 527.4842 | 498.549 | 489.4113
4651.176 | 662.0572 | 527.2364 | 498.7656 | 489.1239
4652.176 | 659.2982 | 526.8428 | 498.5602 | 488.6006
4653.176 | 661.7284 | 527.3134 | 498.1061 | 489.2068
4654.176 | 660.5121 | 529.1571 | 497.948 | 488.8206
4655.176 | 664.0748 | 529.0777 | 498.5245 | 488.4957
4656.176 | 663.0224 | 528.2109 | 498.8286 | 489.0994
4657.176 | 660.8518 | 527.6813 | 498.5234 | 489.5394
4658.176 | 664.7608 | 526.6865 | 498.4471 | 489.6732
4659.176 | 662.8275 | 526.8223 | 497.8659 | 489.8794
4660.176 | 663.0498 | 526.1325 | 497.5462 | 489.9191
4661.176 | 662.2412 | 525.9903 | 497.2609 | 490.0011
4662.176 | 660.8381 | 527.3572 | 497.3009 | 489.9256
4663.176 | 654.5864 | 529.5 | 497.2359 | 489.4442
4664.176 | 650.7269 | 529.7824 | 497.1888 | 489.495
4665.176 | 651.3701 | 529.8056 | 497.1197 | 490.0649
4666.176 | 650.0807 | 529.1414 | 498.2235 | 490.2303
4667.176 | 658.0725 | 529.9817 | 498.633 | 489.794
4668.176 | 658.4041 | 530.7 | 498.8857 | 489.9083
4669.176 | 664.4661 | 530.6312 | 498.9384 | 490.1433
4670.176 | 667.828 | 530.8446 | 498.7471 | 490.337
4671.176 | 668.3863 | 531.535 | 499.4993 | 490.3869
4672.176 | 670.1478 | 531.475 | 499.7803 | 490.1703
4673.176 | 668.6482 | 531.6623 | 500.1369 | 490.9222
4674.176 | 664.1345 | 531.6929 | 500.6969 | 491.6881
4675.176 | 659.4641 | 532.1535 | 501.3604 | 492.2463
4676.176 | 655.8308 | 532.2844 | 501.5725 | 493.1542
4677.176 | 649.4273 | 532.6051 | 502.1554 | 493.5047
4678.176 | 647.1838 | 533.1509 | 502.8422 | 493.4067
4679.176 | 646.7647 | 533.4113 | 502.5883 | 493.2953
4680.176 | 649.8506 | 533.7601 | 502.8824 | 493.3539
4681.176 | 645.715 | 533.1195 | 502.7948 | 492.9951
4682.176 | 645.0763 | 532.2857 | 502.6551 | 493.2973
4683.176 | 645.4611 | 531.4604 | 502.2686 | 493.3447
4684.176 | 646.2321 | 531.623 | 502.046 | 493.2656
4685.176 | 644.7784 | 531.3867 | 501.5419 | 493.0869
4686.176 | 644.3539 | 532.0352 | 501.3004 | 492.8928
4687.176 | 641.1411 | 533.3192 | 501.2646 | 492.7429
4688.176 | 641.8216 | 534.529 | 501.6759 | 492.9213
4689.176 | 640.6619 | 535.6052 | 502.2302 | 492.5175
4690.176 | 637.9946 | 536.2061 | 502.7299 | 492.4537
4691.176 | 640.689 | 537.5001 | 502.6445 | 491.8889
4692.176 | 637.863 | 537.2599 | 502.7036 | 491.6582
4693.176 | 637.0289 | 538.2395 | 502.9116 | 493.7471
4694.176 | 634.4387 | 540.5769 | 503.0446 | 493.7297
4695.176 | 628.8662 | 539.5609 | 503.017 | 493.3901
4696.176 | 630.3931 | 539.397 | 503.9908 | 493.1291
4697.176 | 631.3877 | 540.3796 | 504.4488 | 493.4457
4698.176 | 630.709 | 540.1623 | 505.0009 | 493.6681
4699.176 | 631.3802 | 540.0931 | 504.954 | 493.8331
4700.176 | 631.5396 | 539.3485 | 504.7958 | 493.1163
4701.176 | 639.0409 | 539.1612 | 504.3792 | 492.8217
4702.176 | 642.5868 | 539.75 | 504.0407 | 492.3833
4703.176 | 642.2304 | 540.0635 | 503.9091 | 492.5346
4704.176 | 642.5982 | 539.6486 | 503.9978 | 492.1208
4705.176 | 644.6086 | 539.2294 | 503.7453 | 492.2716
4706.176 | 644.5022 | 540.5539 | 503.5481 | 492.5701
4707.176 | 644.3066 | 541.1567 | 503.3988 | 492.0988
4708.176 | 643.2721 | 541.3608 | 504.2136 | 492.4878
4709.176 | 645.4803 | 541.9024 | 505.3032 | 492.5635
4710.176 | 639.6933 | 541.102 | 505.3248 | 492.8085
4711.176 | 641.0138 | 541.4511 | 505.4716 | 492.971
4712.176 | 643.3249 | 541.7821 | 505.6653 | 492.9081
4713.176 | 645.0728 | 541.8685 | 506.4135 | 493.277
4714.176 | 643.07 | 541.2548 | 506.2836 | 493.3017
4715.176 | 643.8888 | 541.407 | 506.2989 | 494.4178
4716.176 | 641.5982 | 541.0287 | 506.3732 | 495.4918
4717.176 | 642.6171 | 541.1017 | 506.029 | 495.3099
4718.176 | 643.7618 | 541.3725 | 505.671 | 495.0353
4719.176 | 640.7129 | 541.4502 | 505.4322 | 494.5844
4720.176 | 644.4653 | 541.4872 | 504.9799 | 494.5771
4721.176 | 642.6991 | 540.4573 | 504.6414 | 494.6944
4722.176 | 642.7983 | 541.0052 | 504.8534 | 494.1724
4723.176 | 642.5384 | 540.6312 | 505.3908 | 493.6815
4724.176 | 642.0466 | 539.7352 | 505.3442 | 494.0575
4725.176 | 639.1498 | 539.0028 | 504.9208 | 494.1644
4726.176 | 639.3802 | 539.6495 | 504.9162 | 493.8606
4727.176 | 640.001 | 541.1452 | 504.5204 | 493.7756
4728.176 | 640.5151 | 540.1739 | 504.6828 | 493.7794
4729.176 | 639.1109 | 540.0053 | 504.8054 | 494.2245
4730.176 | 636.7235 | 541.0512 | 504.6188 | 493.7747
4731.176 | 640.197 | 541.9588 | 504.367 | 494.5267
4732.176 | 640.4251 | 541.9767 | 504.617 | 494.4835
4733.176 | 641.0571 | 543.178 | 505.0135 | 494.896
4734.176 | 642.0927 | 543.5918 | 505.4567 | 494.58
4735.176 | 644.6187 | 543.2643 | 505.3771 | 495.2181
4736.176 | 641.8817 | 543.7651 | 505.3601 | 495.673
4737.176 | 643.1907 | 544.9983 | 505.79 | 495.762
4738.176 | 644.6065 | 546.5113 | 506.4147 | 495.7994
4739.176 | 649.5581 | 547.5576 | 506.3892 | 495.8733
4740.176 | 652.0941 | 547.3892 | 506.5101 | 495.8746
4741.176 | 663.7227 | 546.7479 | 506.2664 | 495.4282
4742.176 | 668.7025 | 547.2095 | 506.1625 | 495.4877
4743.176 | 666.8068 | 546.6554 | 505.8134 | 495.4652
4744.176 | 671.1248 | 546.7916 | 506.1036 | 496.0984
4745.176 | 664.4023 | 545.9494 | 506.2322 | 496.3943
4746.176 | 662.0484 | 545.6702 | 506.508 | 497.0769
4747.176 | 659.2642 | 546.4198 | 506.8068 | 496.9268
4748.176 | 662.0616 | 546.2993 | 506.557 | 497.1863
4749.176 | 662.465 | 546.8469 | 506.9032 | 497.1919
4750.176 | 662.3186 | 546.647 | 507.1752 | 497.0229
4751.176 | 659.187 | 546.3105 | 507.447 | 496.8857
4752.176 | 658.0469 | 546.024 | 507.4955 | 497.5157
4753.176 | 655.7968 | 547.089 | 507.6674 | 497.6542
4754.176 | 659.2808 | 547.3374 | 507.4416 | 497.1701
4755.176 | 659.6161 | 546.6281 | 507.5184 | 496.6898
4756.176 | 659.3972 | 546.9413 | 507.4831 | 495.9467
4757.176 | 662.4526 | 546.7075 | 507.0885 | 495.7382
4758.176 | 662.0191 | 546.5821 | 506.7964 | 495.5434
4759.176 | 660.1551 | 545.8585 | 506.6201 | 495.8038
4760.176 | 658.2904 | 545.0666 | 507.4416 | 495.4234
4761.176 | 658.8876 | 544.1379 | 508.3361 | 495.4567
4762.176 | 659.2429 | 544.4108 | 508.7261 | 495.6438
4763.176 | 658.7772 | 544.2036 | 509.9039 | 495.2724
4764.176 | 659.183 | 545.1605 | 510.484 | 495.1678
4765.176 | 661.4877 | 545.1949 | 511.5285 | 494.7913
4766.176 | 659.1228 | 545.5861 | 512.7413 | 494.2049
4767.176 | 660.5451 | 546.8213 | 513.0018 | 493.6784
4768.176 | 666.2428 | 546.5865 | 515.2877 | 494.3005
4769.176 | 670.3095 | 546.101 | 516.5343 | 493.9226
4770.176 | 673.0824 | 545.125 | 517.112 | 493.793
4771.176 | 675.1513 | 544.1266 | 517.1684 | 494.0511
4772.176 | 674.497 | 544.0206 | 517.4035 | 494.4097
4773.176 | 672.9361 | 542.5614 | 518.2534 | 494.6371
4774.176 | 671.2247 | 541.5044 | 518.3558 | 494.0635
4775.176 | 669.6798 | 541.9902 | 518.1871 | 494.1127
4776.176 | 669.32 | 541.5038 | 517.7248 | 493.7509
4777.176 | 665.5786 | 541.4973 | 518.101 | 493.4465
4778.176 | 664.6114 | 541.5036 | 518.6145 | 494.4126
4779.176 | 662.4592 | 541.7885 | 520.2033 | 494.175
4780.176 | 665.3476 | 541.4631 | 520.2944 | 493.6975
4781.176 | 669.0389 | 542.5428 | 519.5289 | 494.0893
4782.176 | 670.5565 | 543.3538 | 519.4337 | 493.9836
4783.176 | 668.4751 | 544.6621 | 519.9058 | 494.1919
4784.176 | 671.6278 | 544.487 | 519.4743 | 494.5765
4785.176 | 673.0723 | 545.058 | 519.0198 | 494.6186
4786.176 | 676.6254 | 545.911 | 518.4503 | 494.4963
4787.176 | 681.2327 | 546.3831 | 517.9956 | 494.5633
4788.176 | 682.8138 | 545.6169 | 517.3401 | 494.386
4789.176 | 678.1985 | 544.7053 | 516.3697 | 494.1851
4790.176 | 676.0314 | 545.5383 | 515.3122 | 494.7021
4791.176 | 672.519 | 544.9301 | 514.609 | 494.8013
4792.176 | 666.8471 | 544.8187 | 514.043 | 495.4674
4793.176 | 665.3141 | 544.2685 | 513.6662 | 495.6724
4794.176 | 667.6815 | 544.35 | 513.2079 | 495.3687
4795.176 | 665.8152 | 544.8885 | 512.9723 | 494.7736
4796.176 | 667.0172 | 545.4368 | 513.0778 | 494.5559
4797.176 | 666.615 | 545.5032 | 513.2358 | 495.1448
4798.176 | 668.9325 | 544.9254 | 513.5932 | 495.2767
4799.176 | 670.3013 | 544.0161 | 514.1634 | 496.0329
4800.176 | 671.745 | 543.0398 | 515.0677 | 496.0949
4801.176 | 670.1582 | 542.6769 | 514.8765 | 496.3022
4802.176 | 667.6018 | 541.959 | 515.1084 | 496.125
4803.176 | 666.5367 | 542.0603 | 515.7887 | 495.6762
4804.176 | 667.6702 | 544.0657 | 516.6274 | 495.3813
4805.176 | 672.8548 | 545.0345 | 519.7866 | 495.4745
4806.176 | 671.722 | 545.821 | 522.4576 | 495.4315
4807.176 | 676.6415 | 546.6432 | 524.8929 | 495.2101
4808.176 | 676.4364 | 547.3498 | 526.8745 | 495.2816
4809.176 | 678.7824 | 548.088 | 527.4662 | 495.6991
4810.176 | 678.1108 | 549.1581 | 527.3883 | 496.2766
4811.176 | 677.6583 | 548.8871 | 528.0474 | 496.5641
4812.176 | 674.9562 | 548.8952 | 528.6692 | 497.8847
4813.176 | 674.9166 | 548.4449 | 527.9193 | 498.059
4814.176 | 671.9602 | 548.0309 | 527.1034 | 498.6918
4815.176 | 668.2892 | 547.6212 | 526.6361 | 498.6323
4816.176 | 665.864 | 547.0826 | 525.8159 | 498.5349
4817.176 | 664.9494 | 546.0577 | 526.3923 | 498.2683
4818.176 | 661.9014 | 546.4164 | 526.2064 | 498.437
4819.176 | 659.6064 | 547.7479 | 525.4097 | 497.9815
4820.176 | 658.5355 | 549.2192 | 524.0064 | 498.2084
4821.176 | 659.6784 | 548.9876 | 523.2911 | 498.9595
4822.176 | 658.2801 | 547.8206 | 522.6745 | 499.384
4823.176 | 656.8426 | 548.1981 | 522.692 | 499.963
4824.176 | 656.3766 | 549.1938 | 522.8465 | 500.0666
4825.176 | 657.8325 | 549.593 | 522.7487 | 499.9543
4826.176 | 661.1247 | 549.6105 | 522.1436 | 499.9901
4827.176 | 668.1386 | 548.842 | 521.5425 | 499.8828
4828.176 | 676.6792 | 549.2801 | 520.7423 | 500.0408
4829.176 | 674.851 | 548.7313 | 520.4751 | 499.9211
4830.176 | 674.7269 | 549.1187 | 520.3507 | 500.6226
4831.176 | 672.306 | 548.5717 | 520.8403 | 500.5855
4832.176 | 669.4701 | 548.089 | 521.2249 | 500.7832
4833.176 | 666.8837 | 547.7873 | 521.4055 | 501.5542
4834.176 | 667.6493 | 547.5591 | 521.5242 | 501.2578
4835.176 | 665.4826 | 547.3758 | 521.2847 | 501.57
4836.176 | 663.8714 | 547.5017 | 520.6537 | 502.1647
4837.176 | 663.1651 | 547.0965 | 520.4337 | 502.6166
4838.176 | 668.237 | 546.9822 | 520.2917 | 503.0656
4839.176 | 672.6586 | 547.1082 | 519.7488 | 503.1177
4840.176 | 672.1365 | 547.0875 | 519.3728 | 503.3857
4841.176 | 673.5247 | 547.9821 | 518.666 | 503.0475
4842.176 | 674.432 | 548.4555 | 518.2731 | 503.0954
4843.176 | 673.04 | 547.8561 | 517.8366 | 504.4228
4844.176 | 671.2468 | 547.4663 | 517.3183 | 504.1888
4845.176 | 667.3143 | 547.8331 | 516.9176 | 503.6285
4846.176 | 667.1482 | 546.8678 | 516.3678 | 502.8462
4847.176 | 666.3521 | 546.0637 | 517.2496 | 502.1903
4848.176 | 671.7911 | 545.4847 | 518.0891 | 501.4589
4849.176 | 676.637 | 545.258 | 518.7366 | 501.5932
4850.176 | 672.9942 | 544.2148 | 518.758 | 501.5306
4851.176 | 675.2827 | 543.4846 | 519.7479 | 502.3187
4852.176 | 672.2708 | 544.0387 | 519.4823 | 502.5559
4853.176 | 670.3291 | 545.0575 | 519.6102 | 502.2104
4854.176 | 668.3325 | 546.6367 | 519.6288 | 502.4575
4855.176 | 667.682 | 546.9232 | 520.1805 | 502.555
4856.176 | 668.8042 | 546.4829 | 521.4636 | 502.0603
4857.176 | 670.8693 | 547.2567 | 522.5543 | 502.12
4858.176 | 670.4309 | 547.1488 | 522.8444 | 502.3979
4859.176 | 670.0838 | 547.9284 | 522.4824 | 502.1504
4860.176 | 666.9547 | 547.7727 | 521.8328 | 502.0773
4861.176 | 663.0101 | 547.9128 | 520.9632 | 502.3312
4862.176 | 660.1562 | 548.1376 | 520.8052 | 502.429
4863.176 | 658.0322 | 547.8815 | 520.4973 | 502.4767
4864.176 | 656.6972 | 546.7876 | 520.0267 | 502.4478
4865.176 | 655.8172 | 546.753 | 520.5821 | 502.3751
4866.176 | 655.5713 | 547.0395 | 520.8177 | 502.2886
4867.176 | 651.8376 | 547.8268 | 520.7552 | 502.2081
4868.176 | 655.7565 | 547.109 | 521.445 | 502.2978
4869.176 | 656.7333 | 546.928 | 522.2099 | 502.859
4870.176 | 658.3646 | 546.4076 | 521.3889 | 502.9045
4871.176 | 665.291 | 546.0864 | 521.188 | 502.5887
4872.176 | 665.9205 | 547.3049 | 520.5709 | 502.2983
4873.176 | 667.5181 | 548.8226 | 520.4836 | 501.9582
4874.176 | 666.16 | 548.064 | 519.9915 | 501.6232
4875.176 | 664.977 | 548.0805 | 519.7329 | 501.5669
4876.176 | 663.2871 | 548.0481 | 519.4435 | 502.5033
4877.176 | 661.3567 | 547.1145 | 519.5307 | 502.3217
4878.176 | 658.6704 | 546.8203 | 519.2921 | 502.2689
4879.176 | 656.3945 | 547.1912 | 518.9713 | 502.3843
4880.176 | 653.752 | 547.9888 | 518.8931 | 503.2024
4881.176 | 653.0554 | 547.9902 | 519.5346 | 503.3536
4882.176 | 654.4547 | 546.8568 | 520.1762 | 503.0233
4883.176 | 653.9023 | 546.3652 | 520.3286 | 503.9188
4884.176 | 652.8218 | 546.2965 | 520.3037 | 504.0189
4885.176 | 651.1985 | 546.7062 | 520.4708 | 504.2
4886.176 | 649.9416 | 547.073 | 521.0246 | 504.469
4887.176 | 650.3077 | 547.394 | 521.6646 | 504.3289
4888.176 | 652.4141 | 547.4217 | 522.1859 | 503.9569
4889.176 | 651.764 | 546.5201 | 521.8988 | 504.0388
4890.176 | 650.6936 | 546.0187 | 522.8141 | 504.2682
4891.176 | 651.0547 | 546.3521 | 522.897 | 504.422
4892.176 | 652.6396 | 546.2404 | 522.5401 | 504.9499
4893.176 | 653.1928 | 546.4107 | 522.0059 | 504.8237
4894.176 | 651.2518 | 545.46 | 521.1421 | 504.6097
4895.176 | 648.9515 | 544.9803 | 520.62 | 505.0333
4896.176 | 648.2945 | 546.1377 | 520.4107 | 505.0057
4897.176 | 648.2391 | 546.4659 | 520.4422 | 504.9284
4898.176 | 648.1614 | 547.007 | 520.1868 | 505.2892
4899.176 | 646.8358 | 547.0668 | 520.0321 | 505.4255
4900.176 | 646.0671 | 547.2951 | 519.9171 | 505.3657
4901.176 | 646.538 | 546.7316 | 519.6033 | 505.4481
4902.176 | 647.5305 | 545.801 | 519.7167 | 505.5011
4903.176 | 647.6681 | 546.7195 | 519.9453 | 506.0264
4904.176 | 647.5026 | 547.9607 | 520.7155 | 506.2791
4905.176 | 646.8597 | 548.0011 | 521.5605 | 506.6825
4906.176 | 646.6741 | 548.654 | 521.7247 | 507.5343
4907.176 | 646.6442 | 548.5581 | 521.9062 | 507.8483
4908.176 | 649.6703 | 548.3131 | 522.0759 | 508.2096
4909.176 | 650.6336 | 548.0431 | 521.8834 | 508.2671
4910.176 | 648.9857 | 549.4153 | 521.6989 | 508.2172
4911.176 | 647.458 | 549.516 | 522.3116 | 508.2084
4912.176 | 648.7238 | 549.551 | 522.7264 | 508.208
4913.176 | 652.7845 | 549.0704 | 522.6748 | 508.4466
4914.176 | 653.8314 | 548.3839 | 522.9311 | 508.8088
4915.176 | 654.9788 | 548.17 | 522.4845 | 508.4029
4916.176 | 656.5283 | 549.1561 | 521.8153 | 508.3365
4917.176 | 659.2157 | 550.1297 | 521.0111 | 508.1687
4918.176 | 662.5676 | 549.26 | 520.2314 | 508.2511
4919.176 | 664.1762 | 548.2789 | 519.547 | 508.2323
4920.176 | 663.693 | 548.1371 | 519.6236 | 508.3026
4921.176 | 661.5882 | 548.7212 | 519.9728 | 508.8057
4922.176 | 660.5283 | 547.9619 | 520.4741 | 508.5973
4923.176 | 660.0686 | 547.3543 | 520.4896 | 508.7622
4924.176 | 661.679 | 546.5101 | 520.7026 | 508.5647
4925.176 | 661.6909 | 545.4722 | 520.2533 | 508.9624
4926.176 | 660.5446 | 545.0704 | 519.6295 | 508.8567
4927.176 | 661.2414 | 545.8815 | 519.8213 | 508.6132
4928.176 | 665.3776 | 545.7378 | 520.1799 | 508.5494
4929.176 | 666.3017 | 544.2998 | 520.2991 | 508.7258
4930.176 | 669.1455 | 544.3153 | 519.915 | 508.1538
4931.176 | 669.0752 | 544.5407 | 519.9469 | 507.9461
4932.176 | 666.6972 | 545.6661 | 521.0311 | 507.8596
4933.176 | 665.9431 | 545.9924 | 522.0126 | 507.5986
4934.176 | 665.6697 | 546.1743 | 522.1452 | 507.3431
4935.176 | 663.8364 | 546.1762 | 521.8253 | 506.9582
4936.176 | 664.8415 | 545.6438 | 521.3927 | 506.8478
4937.176 | 665.7431 | 544.7682 | 520.9963 | 506.9006
4938.176 | 666.5116 | 544.5323 | 520.9341 | 507.4179
4939.176 | 667.8192 | 545.0161 | 520.8764 | 507.3417
4940.176 | 668.5838 | 544.9486 | 520.5924 | 507.3238
4941.176 | 667.5415 | 545.3302 | 520.7481 | 507.3934
4942.176 | 671.7753 | 544.7168 | 522.3477 | 507.0619
4943.176 | 676.7937 | 544.0141 | 524.1305 | 507.313
4944.176 | 678.3288 | 543.5979 | 525.5894 | 507.3964
4945.176 | 678.8097 | 543.4568 | 526.9543 | 507.57
4946.176 | 677.5649 | 544.4105 | 527.297 | 508.2844
4947.176 | 675.4254 | 543.7944 | 527.7966 | 508.4333
4948.176 | 679.8225 | 543.1208 | 527.5513 | 508.528
4949.176 | 682.5667 | 542.3882 | 527.9124 | 508.675
4950.176 | 683.4683 | 542.8226 | 527.3679 | 508.3469
4951.176 | 684.637 | 542.6532 | 526.4771 | 508.0315
4952.176 | 684.6462 | 542.4207 | 525.8863 | 507.7119
4953.176 | 686.4413 | 542.2224 | 526.6222 | 507.5272
4954.176 | 688.9338 | 541.5453 | 527.7977 | 506.9133
4955.176 | 688.6436 | 541.1301 | 528.4458 | 506.2311
4956.176 | 688.5383 | 540.9855 | 529.6787 | 505.9982
4957.176 | 688.3568 | 542.0333 | 531.7253 | 506.134
4958.176 | 687.1448 | 543.4613 | 533.7812 | 506.9438
4959.176 | 687.1304 | 544.0067 | 534.7928 | 507.0521
4960.176 | 686.0032 | 543.9367 | 534.8244 | 506.8587
4961.176 | 686.4269 | 544.4658 | 535.9785 | 507.2646
4962.176 | 683.0014 | 545.7964 | 536.6311 | 508.2483
4963.176 | 680.8717 | 545.4127 | 537.0847 | 508.2104
4964.176 | 677.9345 | 544.5805 | 537.7916 | 508.2689
4965.176 | 677.0418 | 544 | 537.2804 | 508.2966
4966.176 | 675.4404 | 544.1504 | 538.195 | 508.2173
4967.176 | 675.9382 | 544.3427 | 540.284 | 508.0749
4968.176 | 676.7887 | 543.4391 | 540.7371 | 508.0431
4969.176 | 673.1796 | 543.6838 | 540.7241 | 508.2516
4970.176 | 669.9309 | 544.1173 | 540.9001 | 508.2848
4971.176 | 667.0522 | 542.4864 | 540.5847 | 508.299
4972.176 | 665.5225 | 542.8707 | 540.0827 | 509.416
4973.176 | 662.4525 | 542.1415 | 539.4043 | 509.5205
4974.176 | 662.2503 | 541.7021 | 538.4753 | 509.3233
4975.176 | 663.7903 | 542.1499 | 537.8003 | 508.8993
4976.176 | 663.3262 | 542.8544 | 537.5924 | 508.5825
4977.176 | 660.8914 | 543.8657 | 536.8435 | 508.257
4978.176 | 657.9375 | 544.5104 | 536.3431 | 508.0668
4979.176 | 656.7351 | 542.9008 | 536.8548 | 508.5436
4980.176 | 655.4229 | 542.5899 | 536.2666 | 508.3355
4981.176 | 656.4741 | 542.9071 | 536.3354 | 508.1894
4982.176 | 655.0146 | 543.2998 | 536.6109 | 508.5282
4983.176 | 651.378 | 544.272 | 536.6545 | 508.3103
4984.176 | 650.9474 | 544.9228 | 535.5166 | 508.2948
4985.176 | 649.26 | 545.259 | 534.3504 | 508.1803
4986.176 | 650.5864 | 544.8461 | 533.1471 | 508.1743
4987.176 | 650.059 | 543.9138 | 532.2658 | 508.4145
4988.176 | 651.2792 | 543.6609 | 531.961 | 508.4618
4989.176 | 651.8075 | 543.7963 | 532.4411 | 508.5529
4990.176 | 654.2498 | 543.9547 | 532.7649 | 509.2371
4991.176 | 651.801 | 544.9733 | 532.6358 | 509.1283
4992.176 | 653.2676 | 545.5264 | 532.4255 | 509.7322
4993.176 | 652.2372 | 546.0184 | 534.3106 | 509.6672
4994.176 | 652.7299 | 545.4969 | 535.8655 | 509.8471
4995.176 | 653.4338 | 545.2024 | 535.5481 | 509.8526
4996.176 | 654.8108 | 544.7396 | 534.6378 | 510.177
4997.176 | 657.8972 | 544.3436 | 533.8066 | 510.2538
4998.176 | 658.9874 | 544.9891 | 533.3299 | 511.0513
4999.176 | 660.829 | 544.7592 | 533.1911 | 510.794
5000.176 | 664.586 | 545.4845 | 532.342 | 510.7693
5001.176 | 668.1509 | 545.2347 | 531.4859 | 510.8207
5002.176 | 670.3559 | 545.2855 | 530.9891 | 510.7963
5003.176 | 669.2393 | 545.3631 | 531.0181 | 510.6374
5004.176 | 664.412 | 545.2418 | 531.829 | 510.7752
5005.176 | 661.6868 | 543.9648 | 532.5828 | 510.5318
5006.176 | 662.5151 | 542.6838 | 533.049 | 510.3183
5007.176 | 662.1539 | 541.3408 | 532.4284 | 510.4052
5008.176 | 658.7384 | 540.5229 | 532.448 | 510.1096
5009.176 | 657.8137 | 540.9431 | 532.6728 | 510.6482
5010.176 | 657.6699 | 540.7934 | 533.45 | 510.4896
5011.176 | 656.2736 | 541.191 | 534.6829 | 511.1523
5012.176 | 655.2147 | 541.6291 | 535.5855 | 511.2379
5013.176 | 654.0178 | 540.9126 | 536.6304 | 511.2092
5014.176 | 653.5914 | 542.3584 | 537.3575 | 510.9444
5015.176 | 653.0421 | 542.9656 | 537.2534 | 510.8056
5016.176 | 651.1079 | 543.6527 | 536.4723 | 510.3468
5017.176 | 649.9611 | 543.4153 | 535.177 | 509.8638
5018.176 | 649.1786 | 543.3952 | 533.9169 | 509.8242
5019.176 | 649.9188 | 544.1744 | 532.6926 | 509.7371
5020.176 | 650.7476 | 543.9272 | 532.083 | 509.9601
5021.176 | 654.3224 | 543.5452 | 531.4531 | 509.9808
5022.176 | 654.1506 | 544.1122 | 530.4869 | 510.1341
5023.176 | 653.0452 | 544.9152 | 529.785 | 510.1943
5024.176 | 654.732 | 545.42 | 529.7582 | 509.8624
5025.176 | 654.9598 | 545.38 | 529.5526 | 509.805
5026.176 | 656.2346 | 544.7924 | 528.9384 | 510.537
5027.176 | 654.2223 | 544.4161 | 528.4368 | 510.6971
5028.176 | 653.5507 | 544.706 | 527.6328 | 510.9534
5029.176 | 653.0242 | 544.2361 | 526.8434 | 511.0902
5030.176 | 653.9382 | 543.6798 | 526.6292 | 511.4034
5031.176 | 654.3807 | 543.2901 | 526.3005 | 512.0398
5032.176 | 652.747 | 542.5713 | 525.9815 | 512.9892
5033.176 | 654.1796 | 542.6473 | 526.0523 | 512.9581
5034.176 | 654.4103 | 542.7434 | 525.9843 | 512.7639
5035.176 | 654.8849 | 542.5113 | 525.9929 | 513.4054
5036.176 | 656.218 | 542.4537 | 526.2121 | 513.795
5037.176 | 656.4968 | 541.912 | 526.4247 | 515.0726
5038.176 | 656.8577 | 541.4961 | 526.4041 | 515.1587
5039.176 | 661.3801 | 540.8583 | 525.9499 | 515.0256
5040.176 | 667.0944 | 539.8701 | 525.158 | 514.6477
5041.176 | 669.4843 | 539.478 | 524.7021 | 513.9903
5042.176 | 671.4042 | 540.7008 | 524.8315 | 513.3948
5043.176 | 671.4843 | 541.0528 | 524.6632 | 512.5065
5044.176 | 672.9418 | 540.7908 | 524.2861 | 512.0425
5045.176 | 671.2546 | 540.3802 | 524.102 | 511.7462
5046.176 | 670.6397 | 539.9791 | 524.3831 | 512.4051
5047.176 | 667.1947 | 540.5994 | 524.9275 | 512.7422
5048.176 | 664.0184 | 539.9243 | 525.9317 | 512.4843
5049.176 | 664.3273 | 539.401 | 526.2322 | 512.0857
5050.176 | 664.4329 | 539.7303 | 527.0226 | 511.6059
5051.176 | 667.0694 | 539.6291 | 527.8735 | 511.0858
5052.176 | 668.922 | 539.6888 | 529.0138 | 511.4401
5053.176 | 669.8 | 540.4451 | 529.423 | 511.7139
5054.176 | 669.6891 | 541.0078 | 529.4994 | 512.5892
5055.176 | 667.9022 | 541.3388 | 529.5436 | 512.6382
5056.176 | 665.3201 | 541.1266 | 529.751 | 512.4872
5057.176 | 670.4463 | 542.2276 | 530.4418 | 513.0733
5058.176 | 673.4849 | 541.4484 | 531.6296 | 513.6525
5059.176 | 671.9954 | 541.2685 | 531.9932 | 513.7942
5060.176 | 672.6766 | 541.6723 | 532.4701 | 513.5482
5061.176 | 673.0035 | 541.5716 | 533.2934 | 513.332
5062.176 | 673.8167 | 540.4346 | 534.2396 | 513.3876
5063.176 | 673.0676 | 539.6138 | 534.8344 | 512.8151
5064.176 | 671.1174 | 539.6845 | 536.1827 | 512.0673
5065.176 | 671.8044 | 539.1654 | 536.8976 | 511.7693
5066.176 | 672.7856 | 538.7992 | 536.5226 | 511.7144
5067.176 | 674.3683 | 538.5159 | 536.5864 | 511.6538
5068.176 | 673.8625 | 538.2909 | 536.6955 | 512.2067
5069.176 | 672.7019 | 538.2789 | 537.3107 | 513.0678
5070.176 | 671.937 | 537.3734 | 536.6261 | 513.4168
5071.176 | 670.3573 | 535.9308 | 535.7176 | 513.0285
5072.176 | 670.6191 | 534.8333 | 535.4779 | 513.4968
5073.176 | 672.3783 | 535.1539 | 535.3656 | 513.1765
5074.176 | 673.0643 | 535.3404 | 536.5929 | 513.2338
5075.176 | 670.9336 | 536.079 | 537.6248 | 512.9138
5076.176 | 673.6808 | 535.7534 | 538.0216 | 512.5272
5077.176 | 672.3654 | 535.2242 | 537.5495 | 511.9503
5078.176 | 677.229 | 534.5968 | 536.2282 | 511.8783
5079.176 | 677.0526 | 535.6282 | 536.3694 | 511.3677
5080.176 | 676.4939 | 536.6216 | 536.0429 | 511.1354
5081.176 | 676.4409 | 536.5912 | 535.0056 | 511.0256
5082.176 | 675.0165 | 536.3086 | 534.6293 | 510.8363
5083.176 | 671.1715 | 536.1207 | 534.2917 | 510.948
5084.176 | 670.5682 | 536.4339 | 534.088 | 510.9868
5085.176 | 668.6057 | 536.7813 | 534.0178 | 511.4166
5086.176 | 665.1164 | 536.7486 | 534.0651 | 511.4756
5087.176 | 662.288 | 537.0272 | 534.0818 | 511.2512
5088.176 | 660.0401 | 537.1442 | 534.0043 | 511.0151
5089.176 | 654.3469 | 536.5935 | 534.9026 | 511.17
5090.176 | 656.9232 | 536.7187 | 535.1628 | 510.9625
5091.176 | 655.0723 | 537.8072 | 535.4657 | 511.1259
5092.176 | 652.4681 | 537.5654 | 535.0408 | 510.9308
5093.176 | 648.6637 | 536.9397 | 534.2492 | 510.6899
5094.176 | 650.9895 | 538.8207 | 533.3758 | 510.6949
5095.176 | 654.1395 | 538.4577 | 532.2578 | 510.2256
5096.176 | 653.5348 | 538.7892 | 530.9855 | 510.0481
5097.176 | 651.5751 | 539.7656 | 530.3368 | 510.1371
5098.176 | 646.8079 | 538.8461 | 531.0986 | 510.0905
5099.176 | 653.8128 | 537.8261 | 531.693 | 509.992
5100.176 | 654.2901 | 536.9418 | 531.595 | 509.9851
5101.176 | 655.798 | 536.0928 | 530.4749 | 510.07
5102.176 | 650.118 | 535.5593 | 529.7701 | 510.4374
5103.176 | 651.23 | 536.0831 | 530.0115 | 510.4311
5104.176 | 649.1258 | 535.1386 | 529.7717 | 510.7492
5105.176 | 653.5295 | 535.1732 | 530.1476 | 511.0173
5106.176 | 652.379 | 537.4183 | 530.8031 | 511.3972
5107.176 | 652.9945 | 537.4555 | 530.5843 | 512.0269
5108.176 | 651.8113 | 537.5977 | 530.2977 | 511.873
5109.176 | 651.3629 | 538.4415 | 529.9272 | 511.7956
5110.176 | 651.882 | 539.752 | 530.4443 | 511.7577
5111.176 | 648.4303 | 540.1924 | 530.2982 | 512.0285
5112.176 | 654.8657 | 540.423 | 530.7106 | 512.7027
5113.176 | 649.8461 | 540.7759 | 531.3255 | 513.2151
5114.176 | 650.5147 | 541.7039 | 531.0059 | 513.7103
5115.176 | 648.3936 | 544.2584 | 531.1945 | 513.4473
5116.176 | 656.8081 | 544.4139 | 532.1117 | 513.9881
5117.176 | 653.7192 | 543.7748 | 532.1853 | 514.3799
5118.176 | 654.2033 | 543.1163 | 532.1352 | 514.599
5119.176 | 650.0285 | 543.0032 | 532.0441 | 514.7431
5120.176 | 649.9105 | 542.6739 | 531.5114 | 514.4626
5121.176 | 642.0324 | 542.0065 | 530.8706 | 513.8566
5122.176 | 646.818 | 541.9136 | 530.415 | 513.4413
5123.176 | 642.2625 | 541.3527 | 530.0537 | 513.0895
5124.176 | 644.8727 | 541.1192 | 529.6809 | 512.8831
5125.176 | 643.5291 | 542.5058 | 529.1288 | 513.0025
5126.176 | 641.9028 | 543.2321 | 528.5865 | 513.0892
5127.176 | 635.3584 | 542.4601 | 527.9831 | 512.8798
5128.176 | 640.467 | 542.6593 | 527.3758 | 512.6003
5129.1917 | 641.8741 | 542.029 | 527.345 | 512.1186
5130.176 | 642.0982 | 542.5221 | 527.4964 | 511.8953
5131.176 | 640.7695 | 543.7083 | 527.3337 | 511.9957
5132.176 | 639.4828 | 544.3568 | 526.6333 | 511.7259
5133.176 | 637.1485 | 543.3419 | 526.0071 | 511.6616
5134.1917 | 638.9726 | 541.7811 | 525.3806 | 511.9315
5135.1917 | 641.777 | 540.6768 | 524.9546 | 511.6885
5136.176 | 642.235 | 540.5331 | 524.579 | 511.2316
5137.176 | 641.4176 | 540.7782 | 524.3792 | 511.0828
5138.176 | 635.4993 | 540.328 | 524.2307 | 510.5887
5139.176 | 637.6497 | 542.5941 | 523.856 | 510.546
5140.176 | 636.8898 | 547.0972 | 524.03 | 510.3211
5141.176 | 634.2575 | 546.1765 | 525.085 | 510.1967
5142.176 | 631.7561 | 545.1687 | 525.3337 | 510.4275
5143.176 | 635.8713 | 545.2777 | 525.8226 | 510.3383
5144.176 | 635.5948 | 545.5852 | 525.6064 | 510.8262
5145.176 | 631.9938 | 545.4252 | 524.9971 | 510.5869
5146.176 | 639.5353 | 544.5716 | 524.3333 | 510.3643
5147.176 | 644.5835 | 542.9062 | 523.5482 | 510.2981
5148.176 | 644.3662 | 542.6675 | 523.0066 | 511.266
5149.176 | 647.749 | 542.4794 | 522.5169 | 511.484
5150.176 | 646.6749 | 542.8849 | 522.1251 | 511.4056
5151.176 | 648.1842 | 542.9183 | 521.4781 | 511.1944
5152.176 | 648.8233 | 542.2674 | 521.8621 | 510.7987
5153.176 | 646.8086 | 541.529 | 522.4768 | 510.7969
5154.176 | 649.4415 | 540.7046 | 522.1828 | 510.5062
5155.176 | 649.4386 | 540.0734 | 522.237 | 510.3972
5156.176 | 656.9837 | 539.4171 | 522.3278 | 510.095
5157.176 | 658.0693 | 538.6508 | 522.4905 | 510.085
5158.176 | 655.8099 | 538.0668 | 521.9384 | 509.9374
5159.176 | 657.7397 | 537.7653 | 521.492 | 509.8355
5160.176 | 656.9985 | 537.5716 | 521.2728 | 509.7443
5161.176 | 657.8279 | 537.306 | 521.5048 | 510.0414
5162.176 | 654.0199 | 537.6393 | 521.9244 | 509.8094
5163.176 | 662.573 | 539.1079 | 523.3829 | 510.3459
5164.176 | 664.6971 | 542.7589 | 524.6607 | 510.7449
5165.176 | 663.9509 | 542.4106 | 525.8261 | 511.5762
5166.176 | 664.6462 | 542.5012 | 526.8797 | 511.835
5167.176 | 668.8419 | 542.6744 | 528.1043 | 511.6975
5168.176 | 670.6781 | 542.3557 | 529.2222 | 511.6018
5169.176 | 667.9836 | 542.3155 | 529.7828 | 511.1788
5170.176 | 667.2814 | 541.9903 | 529.7187 | 510.8915
5171.176 | 672.5283 | 541.8961 | 529.2215 | 510.7322
5172.176 | 671.4746 | 541.1243 | 528.7233 | 510.6186
5173.176 | 666.9653 | 541.1783 | 528.4847 | 510.9082
5174.176 | 671.6066 | 540.0951 | 529.5443 | 511.1045
5175.176 | 676.8772 | 540.0925 | 530.051 | 511.843
5176.176 | 678.8772 | 540.6448 | 530.3333 | 512.2341
5177.176 | 681.1141 | 540.5037 | 530.3338 | 512.2357
5178.176 | 681.5573 | 540.3394 | 530.5008 | 512.4279
5179.176 | 681.2431 | 539.773 | 531.1556 | 513.2182
5180.176 | 679.4916 | 539.3091 | 532.2241 | 513.4383
5181.176 | 678.3311 | 539.0136 | 532.2089 | 513.2291
5182.176 | 678.269 | 537.4928 | 530.9833 | 512.4366
5183.176 | 677.7349 | 537.5268 | 531.4408 | 512.7335
5184.176 | 675.6982 | 536.1099 | 530.9867 | 512.9673
5185.176 | 676.5986 | 535.6036 | 530.6687 | 512.9685
5186.176 | 675.1117 | 534.7182 | 532.3323 | 512.6489
5187.176 | 676.5062 | 534.6354 | 533.766 | 512.4216
5188.176 | 673.5567 | 535.0446 | 535.7536 | 512.6603
5189.176 | 674.1495 | 535.7762 | 536.0385 | 512.095
5190.176 | 673.2721 | 535.7545 | 537.6122 | 511.4817
5191.176 | 673.7048 | 536.8586 | 538.9879 | 511.6048
5192.176 | 674.2874 | 537.1292 | 539.9416 | 512.0655
5193.176 | 675.4781 | 537.1024 | 540.0005 | 511.8504
5194.176 | 681.0122 | 536.6614 | 539.0608 | 511.8958
5195.176 | 678.233 | 536.9234 | 539.0675 | 512.2777
5196.176 | 680.3225 | 536.8367 | 539.2379 | 513.6124
5197.176 | 674.3512 | 537.8168 | 539.7156 | 513.4362
5198.176 | 677.1329 | 536.8565 | 540.5657 | 514.2246
5199.176 | 677.2096 | 536.0542 | 541.3485 | 514.7735
5200.176 | 678.8156 | 536.2256 | 542.0125 | 514.3034
5201.176 | 675.6086 | 535.5522 | 541.2941 | 513.8978
5202.176 | 673.7243 | 535.1561 | 540.4087 | 513.3792
5203.176 | 675.5304 | 535.0124 | 540.5962 | 512.5908
5204.176 | 674.9637 | 535.2835 | 541.4896 | 512.0349
5205.176 | 673.2929 | 535.5993 | 542.3028 | 512.0805
5206.176 | 672.7118 | 535.6008 | 543.7775 | 511.8834
5207.176 | 672.8568 | 535.5728 | 544.1686 | 511.9127
5208.176 | 671.5001 | 535.6914 | 543.5141 | 512.6888
5209.176 | 671.9882 | 535.3108 | 541.4693 | 513.1983
5210.176 | 670.0682 | 534.6458 | 539.7985 | 513.1073
5211.176 | 667.2044 | 533.8944 | 538.6756 | 512.6637
5212.176 | 667.308 | 533.9554 | 538.0393 | 512.3979
5213.176 | 665.1018 | 533.7379 | 538.0558 | 512.3623
5214.176 | 664.9964 | 533.7391 | 537.9529 | 512.0969
5215.176 | 664.2619 | 534.0016 | 537.7486 | 511.5719
5216.176 | 661.5701 | 534.0131 | 538.8068 | 511.2885
5217.176 | 660.3972 | 533.0312 | 538.139 | 511.2345
5218.176 | 660.6188 | 532.2146 | 537.3356 | 511.1652
5219.176 | 658.8028 | 531.337 | 536.9391 | 511.0783
5220.176 | 655.6827 | 531.1937 | 536.4743 | 510.9702
5221.176 | 655.8547 | 531.1911 | 536.6766 | 510.3992
5222.176 | 653.8506 | 530.9426 | 536.1135 | 509.9221
5223.176 | 649.4701 | 530.4424 | 535.3435 | 509.7813
5224.176 | 645.5935 | 529.6974 | 534.4365 | 509.8062
5225.176 | 644.5701 | 529.6418 | 534.0575 | 509.6004
5226.176 | 642.8505 | 529.7371 | 533.4409 | 510.1433
5227.176 | 641.4504 | 528.942 | 532.3693 | 510.0799
5228.176 | 641.9489 | 529.0936 | 531.1576 | 509.9525
5229.176 | 646.2071 | 528.9486 | 531.6154 | 509.3887
5230.176 | 646.9088 | 528.7763 | 532.0096 | 509.0058
5231.176 | 647.2406 | 528.7836 | 532.1407 | 509.1224
5232.176 | 646.5077 | 529.8405 | 533.1723 | 509.5238
5233.176 | 645.3782 | 531.3232 | 533.4994 | 509.9803
5234.176 | 642.7908 | 530.7792 | 533.2586 | 510.3388
5235.176 | 640.5272 | 531.2105 | 534.0964 | 510.2193
5236.176 | 641.3926 | 531.8035 | 534.9773 | 510.1812
5237.176 | 640.2841 | 531.6929 | 535.9845 | 509.9343
5238.176 | 638.7696 | 531.0757 | 537.2937 | 509.3333
5239.176 | 636.9989 | 530.3731 | 537.5546 | 509.301
5240.176 | 633.8726 | 530.1998 | 536.8297 | 509.4698
5241.176 | 630.9396 | 529.8745 | 536.6536 | 509.7304
5242.176 | 628.2541 | 529.4672 | 536.3473 | 510.2063
5243.176 | 629.0088 | 528.6022 | 535.1713 | 510.4901
5244.176 | 629.2729 | 528.2958 | 534.428 | 510.3723
5245.176 | 628.9532 | 528.5771 | 533.7151 | 510.0777
5246.176 | 628.4434 | 528.1326 | 533.2461 | 509.3829
5247.176 | 632.2396 | 528.2955 | 532.3063 | 508.9745
5248.176 | 634.8226 | 527.9427 | 531.868 | 508.5896
5249.176 | 634.7284 | 528.0855 | 531.5421 | 508.402
5250.176 | 636.2188 | 528.9428 | 532.0239 | 508.3806
5251.176 | 637.0064 | 529.2654 | 532.455 | 508.205
5252.176 | 636.8218 | 530.4999 | 533.0971 | 508.4957
5253.176 | 634.5334 | 531.6379 | 532.693 | 508.9336
5254.176 | 632.1941 | 531.7989 | 532.9827 | 509.329
5255.176 | 631.2751 | 531.9228 | 533.1147 | 509.403
5256.176 | 630.4751 | 531.3141 | 532.5189 | 509.3303
5257.176 | 630.1458 | 530.9022 | 531.7964 | 509.4862
5258.176 | 630.016 | 531.0003 | 531.8361 | 510.0198
5259.176 | 632.5078 | 530.2825 | 531.0978 | 510.2891
5260.176 | 632.4558 | 529.6511 | 531.1148 | 510.316
5261.176 | 631.8358 | 529.2356 | 531.3594 | 509.8775
5262.176 | 631.5447 | 529.1636 | 530.5071 | 509.8553
5263.176 | 633.1445 | 528.9237 | 530.9054 | 509.6637
5264.176 | 632.3748 | 528.3074 | 531.7482 | 509.2706
5265.176 | 632.1782 | 527.9345 | 532.3565 | 509.6451
5266.176 | 634.3018 | 526.9376 | 532.3021 | 509.6139
5267.176 | 635.2251 | 526.3129 | 531.5652 | 509.4698
5268.176 | 635.2696 | 526.5289 | 532.0117 | 509.0402
5269.176 | 637.3751 | 526.0704 | 532.6798 | 508.3718
5270.176 | 638.5727 | 526.0848 | 533.9601 | 507.9826
5271.176 | 642.0988 | 526.4956 | 535.0013 | 507.8896
5272.176 | 645.3111 | 527.5577 | 535.3739 | 507.6429
5273.176 | 645.5535 | 529.9637 | 535.7398 | 507.4053
5274.176 | 648.2441 | 530.4535 | 536.001 | 507.172
5275.176 | 651.0132 | 531.8457 | 535.0067 | 506.9198
5276.176 | 654.2203 | 530.9127 | 534.9956 | 507.1865
5277.176 | 655.6836 | 530.3219 | 535.2784 | 507.3867
5278.176 | 657.3918 | 529.9591 | 535.1845 | 507.0648
5279.176 | 659.9581 | 529.5867 | 535.8391 | 507.0644
5280.176 | 659.4906 | 529.051 | 534.6038 | 506.5755
5281.176 | 659.8472 | 528.8789 | 533.4341 | 505.9147
5282.176 | 665.0326 | 528.8947 | 533.1868 | 505.6836
5283.176 | 664.4799 | 528.9617 | 531.988 | 506.0901
5284.176 | 664.0852 | 528.5714 | 531.0849 | 506.2838
5285.176 | 663.2453 | 528.0746 | 530.5316 | 506.448
5286.176 | 660.6091 | 528.3679 | 530.6809 | 506.4479
5287.176 | 658.1577 | 528.2591 | 529.5226 | 506.5668
5288.176 | 657.5555 | 527.7676 | 528.4538 | 506.6343
5289.176 | 656.13 | 526.9199 | 527.7337 | 506.9042
5290.176 | 660.0656 | 526.7656 | 527.7979 | 507.4275
5291.176 | 661.6949 | 526.1341 | 526.9614 | 507.4933
5292.176 | 660.844 | 525.2139 | 527.3393 | 507.3159
5293.176 | 661.5282 | 524.9037 | 527.2275 | 507.0568
5294.176 | 662.3711 | 526.2783 | 527.1414 | 506.6954
5295.176 | 660.3385 | 525.5123 | 527.0124 | 506.1916
5296.176 | 657.8642 | 525.1526 | 527.6315 | 505.9685
5297.176 | 654.8318 | 527.06 | 528.3298 | 505.5437
5298.176 | 654.1337 | 526.7666 | 529.3303 | 505.5041
5299.176 | 655.3998 | 526.9801 | 529.149 | 505.3582
5300.176 | 655.9664 | 527.3226 | 529.3829 | 505.1111
5301.176 | 659.5196 | 527.7514 | 529.4603 | 505.6178
5302.176 | 656.8061 | 527.7301 | 529.1747 | 506.1878
5303.176 | 656.2125 | 527.4489 | 528.9296 | 506.2558
5304.176 | 656.1987 | 527.4354 | 529.4361 | 505.8451
5305.1917 | 661.2054 | 528.7398 | 530.7562 | 505.1395
5306.176 | 660.7048 | 529.5474 | 530.8951 | 504.8922
5307.176 | 661.3678 | 529.2386 | 530.8248 | 505.0055
5308.176 | 661.6301 | 528.7621 | 531.2427 | 504.3232
5309.176 | 663.222 | 528.023 | 530.9888 | 503.6237
5310.176 | 666.5722 | 527.7256 | 530.0159 | 503.3942
5311.176 | 671.6184 | 526.6806 | 529.5732 | 504.1363
5312.176 | 675.7963 | 526.8462 | 530.5159 | 504.8954
5313.176 | 680.9082 | 527.3816 | 531.942 | 505.016
5314.176 | 684.649 | 526.6897 | 531.0525 | 506.2477
5315.176 | 686.31 | 526.3576 | 530.0431 | 507.111
5316.176 | 685.904 | 526.1661 | 530.0714 | 508.0833
5317.176 | 685.5268 | 525.406 | 529.4414 | 507.7592
5318.176 | 687.4219 | 524.8098 | 529.4576 | 508.1079
5319.176 | 689.9153 | 524.6902 | 529.9122 | 508.876
5320.176 | 687.7374 | 524.4508 | 529.368 | 509.6083
5321.176 | 691.2276 | 523.8995 | 528.2829 | 509.2371
5322.176 | 695.0467 | 524.9109 | 527.6534 | 508.6298
5323.176 | 697.7807 | 526.6861 | 528.5875 | 508.6452
5324.176 | 698.7105 | 527.0045 | 528.2284 | 508.5227
5325.176 | 700.237 | 525.4061 | 526.7627 | 508.1156
5326.176 | 700.049 | 523.8281 | 526.5045 | 507.6744
5327.176 | 699.2153 | 522.9533 | 527.4545 | 507.8802
5328.176 | 700.1601 | 522.5685 | 527.3458 | 507.5999
5329.176 | 698.703 | 521.4911 | 527.0419 | 506.9374
5330.176 | 699.3639 | 520.568 | 528.1132 | 506.6598
5331.176 | 700.6871 | 521.9532 | 527.9909 | 506.5015
5332.176 | 700.3514 | 521.2876 | 527.7577 | 506.2989
5333.176 | 703.1493 | 520.3332 | 529.0207 | 505.7103
5334.176 | 704.7368 | 521.1544 | 529.1288 | 505.7457
5335.1917 | 709.6684 | 520.7725 | 529.1902 | 506.1161
5336.176 | 712.4251 | 520.84 | 529.1355 | 507.0788
5337.176 | 715.96 | 520.9444 | 528.0787 | 508.1818
5338.176 | 718.8792 | 521.9206 | 527.6649 | 507.7247
5339.176 | 720.5001 | 521.0553 | 527.0187 | 507.6497
5340.176 | 723.9776 | 520.7172 | 526.4873 | 508.6203
5341.176 | 723.4844 | 520.292 | 526.1785 | 509.3656
5342.176 | 722.5947 | 520.5341 | 525.8388 | 509.2685
5343.176 | 724.2014 | 521.0043 | 525.7699 | 508.6992
5344.176 | 724.3049 | 520.854 | 526.1409 | 508.1103
5345.176 | 722.5927 | 520.7535 | 525.6701 | 507.6435
5346.176 | 718.1902 | 521.4852 | 524.9204 | 507.1041
5347.176 | 716.1762 | 521.6671 | 523.9527 | 506.5454
5348.176 | 714.4476 | 521.2388 | 523.4367 | 506.4816
5349.176 | 713.8325 | 522.5933 | 524.9788 | 506.3638
5350.176 | 712.9235 | 522.2408 | 524.8226 | 505.8495
5351.176 | 714.0822 | 521.8245 | 524.6251 | 505.473
5352.176 | 716.5945 | 521.4554 | 524.9038 | 505.9327
5353.176 | 715.4571 | 520.514 | 524.6934 | 507.8034
5354.176 | 713.8985 | 520.2881 | 524.1917 | 508.5223
5355.176 | 710.8484 | 520.2334 | 524.1106 | 508.9943
5356.176 | 709.3062 | 520.7365 | 524.0336 | 509.0259
5357.176 | 706.4333 | 520.6346 | 524.0978 | 508.1411
5358.176 | 703.6212 | 521.0619 | 524.5147 | 507.4175
5359.176 | 704.8436 | 521.5252 | 524.911 | 506.9389
5360.176 | 704.0262 | 521.0491 | 524.9787 | 506.5256
5361.176 | 703.7796 | 520.5252 | 524.6714 | 506.6726
5362.176 | 698.3795 | 520.47 | 524.0656 | 508.0091
5363.176 | 692.5253 | 520.0854 | 522.8523 | 509.0578
5364.176 | 686.4629 | 520.1251 | 521.6453 | 510.0973
5365.176 | 680.1889 | 520.3263 | 521.3351 | 510.0147
5366.176 | 676.9008 | 519.4977 | 521.2081 | 509.1613
5367.176 | 673.0248 | 518.4179 | 522.1915 | 508.2583
5368.176 | 667.6463 | 517.8795 | 522.8915 | 507.4046
5369.176 | 663.6774 | 517.4739 | 522.2352 | 506.8743
5370.176 | 659.7985 | 516.9777 | 522.216 | 507.1761
5371.176 | 657.0321 | 517.0941 | 522.5986 | 506.8592
5372.176 | 654.7789 | 516.9463 | 522.3929 | 507.153
5373.176 | 652.9249 | 517.1846 | 522.9118 | 506.8083
5374.176 | 652.442 | 517.3248 | 522.8301 | 506.5349
5375.176 | 652.5617 | 516.9825 | 523.8605 | 506.4992
5376.176 | 651.7446 | 517.0626 | 525.28 | 506.3396
5377.176 | 651.8157 | 517.4629 | 526.7071 | 505.9704
5378.176 | 650.8923 | 517.7665 | 528.1961 | 506.2193
5379.176 | 650.4761 | 518.4114 | 527.8 | 505.6386
5380.176 | 651.7073 | 518.3442 | 527.8607 | 505.3304
5381.176 | 652.814 | 518.8486 | 527.6501 | 506.0149
5382.176 | 652.7336 | 518.9863 | 527.4273 | 506.1176
5383.176 | 654.0404 | 518.541 | 526.8256 | 505.5625
5384.176 | 655.5149 | 518.3799 | 526.697 | 505.6172
5385.176 | 658.0727 | 518.4664 | 526.7794 | 506.1727
5386.176 | 658.9063 | 518.1697 | 526.6824 | 505.8604
5387.176 | 658.8952 | 517.9645 | 526.2033 | 505.2179
5388.176 | 657.1128 | 517.8491 | 526.6211 | 504.9347
5389.176 | 655.5322 | 517.4581 | 526.5185 | 505.1328
5390.176 | 654.4296 | 516.8824 | 526.3515 | 505.3768
5391.176 | 653.3557 | 516.1669 | 526.5924 | 505.1371
5392.176 | 651.1719 | 516.2477 | 526.209 | 504.5497
5393.176 | 650.3747 | 516.1458 | 525.568 | 504.3941
5394.176 | 650.3992 | 516.0898 | 525.348 | 504.2189
5395.1917 | 649.1511 | 516.0421 | 525.7174 | 504.7722
5396.176 | 648.1002 | 515.1911 | 526.0247 | 504.7969
5397.176 | 648.6888 | 514.8205 | 526.1169 | 505.1383
5398.176 | 648.5759 | 515.0268 | 526.2505 | 504.7612
5399.176 | 647.6076 | 515.0015 | 525.6543 | 505.0272
5400.176 | 645.7463 | 515.8313 | 524.9314 | 504.3128
5401.176 | 643.0176 | 516.4816 | 526.2536 | 503.8161
5402.176 | 640.397 | 517.0884 | 527.6065 | 503.3405
5403.176 | 639.5257 | 517.1742 | 527.9163 | 502.8803
5404.176 | 641.0205 | 517.0263 | 528.7358 | 502.2184
5405.176 | 644.3846 | 516.783 | 528.1737 | 502.0727
5406.176 | 645.0889 | 516.9308 | 527.7161 | 503.0209
5407.176 | 644.5343 | 517.1302 | 527.411 | 504.1488
5408.176 | 645.1828 | 517.299 | 527.2138 | 504.5241
5409.176 | 644.7316 | 517.7398 | 526.8702 | 504.3794
5410.176 | 645.0624 | 517.7982 | 525.9802 | 504.3921
5411.176 | 644.6402 | 517.5173 | 525.4456 | 504.4094
5412.176 | 644.4623 | 517.7185 | 525.4347 | 504.2335
5413.176 | 642.927 | 517.44 | 525.2033 | 503.9423
5414.176 | 642.3652 | 516.9505 | 525.5001 | 503.8195
5415.176 | 642.8637 | 516.2427 | 524.9733 | 503.7575
5416.176 | 645.4358 | 515.1744 | 525.6941 | 503.1933
5417.176 | 644.0723 | 514.1592 | 525.2037 | 503.4348
5418.176 | 642.8287 | 514.3901 | 524.5536 | 503.399
5419.176 | 641.0973 | 514.7003 | 524.0355 | 503.3274
5420.176 | 640.2762 | 514.5151 | 523.6314 | 503.1149
5421.176 | 641.8106 | 514.1291 | 523.2372 | 502.7261
5422.176 | 644.1508 | 513.8466 | 522.9835 | 502.5609
5423.176 | 645.5326 | 513.4681 | 521.843 | 502.6144
5424.176 | 647.5607 | 512.8637 | 521.4686 | 503.0093
5425.1917 | 655.6838 | 512.6228 | 522.3422 | 503.2535
5426.176 | 657.3394 | 512.5905 | 523.1723 | 503.3365
5427.176 | 657.5232 | 512.4096 | 523.4986 | 503.3107
5428.176 | 657.3854 | 512.566 | 522.4794 | 503.0893
5429.176 | 654.6957 | 512.4875 | 521.3752 | 502.7547
5430.176 | 655.5813 | 512.408 | 520.6581 | 502.1504
5431.176 | 654.6326 | 511.8616 | 520.66 | 501.4848
5432.176 | 655.8973 | 511.5348 | 521.3216 | 501.6561
5433.176 | 655.8172 | 511.6488 | 520.1674 | 501.2806
5434.176 | 657.9412 | 511.624 | 519.2587 | 500.5972
5435.176 | 660.9237 | 511.9568 | 519.7884 | 500.3236
5436.176 | 665.5278 | 513.3235 | 519.797 | 500.2415
5437.176 | 671.9391 | 513.5644 | 519.6694 | 499.9656
5438.176 | 673.9651 | 513.9906 | 519.0811 | 499.459
5439.176 | 675.2165 | 514.125 | 518.1041 | 499.8229
5440.176 | 678.8196 | 513.9592 | 517.4688 | 500.4753
5441.176 | 684.3345 | 514.2046 | 517.4356 | 500.3212
5442.176 | 686.4935 | 514.1367 | 518.1072 | 500.4032
5443.176 | 691.668 | 514.042 | 518.5924 | 500.3593
5444.176 | 696.9574 | 514.5553 | 518.8142 | 500.5298
5445.176 | 699.287 | 514.4057 | 518.63 | 501.3963
5446.176 | 703.2137 | 515.179 | 518.6488 | 501.4
5447.176 | 707.9156 | 515.1862 | 518.8663 | 501.9189
5448.176 | 713.0852 | 515.6275 | 520.6369 | 502.128
5449.176 | 715.7581 | 516.0857 | 521.3314 | 502.932
5450.176 | 715.8279 | 515.8157 | 521.8216 | 504.0649
5451.176 | 713.9731 | 515.487 | 521.1052 | 504.0182
5452.176 | 712.441 | 515.469 | 520.0867 | 504.4569
5453.176 | 710.0495 | 515.0392 | 519.1739 | 503.8249
5454.176 | 707.9893 | 515.2297 | 518.2108 | 503.6826
5455.176 | 708.8117 | 514.9796 | 517.1632 | 503.4839
5456.176 | 710.4765 | 514.8485 | 517.6821 | 503.0475
5457.176 | 709.8042 | 513.9581 | 517.2618 | 502.8576
5458.176 | 709.8439 | 513.205 | 516.9898 | 502.4508
5459.176 | 708.7403 | 512.6428 | 516.8496 | 501.9682
5460.176 | 707.9903 | 512.2264 | 517.512 | 502.0457
5461.176 | 705.6626 | 511.7412 | 517.1743 | 502.3357
5462.176 | 705.4192 | 511.0692 | 516.9232 | 503.0917
5463.176 | 705.9105 | 511.0588 | 516.8458 | 503.73
5464.176 | 703.725 | 511.5155 | 516.6939 | 503.2494
5465.176 | 701.4221 | 511.2147 | 516.26 | 503.6208
5466.176 | 699.0818 | 510.8155 | 515.4094 | 503.2433
5467.176 | 697.623 | 510.451 | 514.6718 | 502.6862
5468.176 | 695.7193 | 510.1688 | 514.4384 | 502.1128
5469.176 | 694.8658 | 510.4038 | 514.3041 | 502.0816
5470.176 | 693.9033 | 510.3498 | 514.0998 | 501.4503
5471.176 | 693.4755 | 509.3624 | 512.8402 | 501.0922
5472.176 | 692.4809 | 508.1325 | 511.6096 | 501.3846
5473.176 | 690.8797 | 508.028 | 510.9416 | 501.1646
5474.176 | 691.7715 | 507.601 | 510.7318 | 500.4809
5475.176 | 693.8131 | 507.0943 | 510.9671 | 500.0408
5476.176 | 695.118 | 506.5562 | 511.6831 | 499.9765
5477.176 | 695.9543 | 506.2091 | 511.2782 | 499.9974
5478.176 | 697.0137 | 506.0451 | 511.271 | 500.235
5479.176 | 696.9262 | 505.9713 | 512.5628 | 500.0257
5480.176 | 697.1451 | 505.9628 | 512.35 | 499.2939
5481.176 | 696.0604 | 506.1403 | 512.2904 | 498.8878
5482.176 | 694.8254 | 506.5829 | 513.2143 | 498.4195
5483.176 | 693.2938 | 507.336 | 514.2681 | 498.574
5484.176 | 690.1969 | 507.4701 | 515.6012 | 498.7317
5485.176 | 691.0863 | 507.9972 | 515.8921 | 499.2838
5486.176 | 689.1258 | 508.7918 | 515.9088 | 499.3867
5487.176 | 687.5032 | 508.9569 | 515.4506 | 498.9492
5488.176 | 688.548 | 508.9819 | 515.4711 | 498.5635
5489.176 | 686.8344 | 509.3532 | 515.4687 | 498.2585
5490.176 | 688.5548 | 509.4671 | 516.0454 | 498.3655
5491.176 | 688.5444 | 509.4084 | 516.1956 | 499.0659
5492.176 | 687.7772 | 508.7931 | 515.77 | 498.8833
5493.176 | 686.7446 | 508.5406 | 515.269 | 498.7541
5494.176 | 684.3257 | 508.8824 | 516.0794 | 498.5054
5495.176 | 684.8082 | 508.7943 | 516.9303 | 499.365
5496.176 | 685.9982 | 508.7986 | 518.1649 | 500.1209
5497.176 | 684.9853 | 508.3738 | 518.5826 | 499.832
5498.176 | 681.6974 | 508.5444 | 517.869 | 499.3402
5499.176 | 678.3415 | 509.0999 | 516.4259 | 498.9743
5500.176 | 677.1817 | 508.7579 | 514.9701 | 498.0618
5501.176 | 675.276 | 508.6967 | 513.9139 | 497.9339
5502.176 | 672.4983 | 508.5552 | 513.478 | 497.9871
5503.176 | 669.8879 | 508.7323 | 513.7282 | 497.7039
5504.176 | 669.4048 | 509.0825 | 513.0111 | 497.6607
5505.176 | 668.5641 | 509.0509 | 512.4116 | 497.4444
5506.176 | 667.3782 | 508.752 | 513.1684 | 496.9995
5507.176 | 667.7855 | 508.8772 | 513.5924 | 496.721
5508.176 | 671.8008 | 508.1135 | 512.9363 | 496.566
5509.176 | 672.1857 | 507.6055 | 513.1611 | 496.8064
5510.176 | 670.2344 | 507.2121 | 512.913 | 497.1384
5511.176 | 667.8492 | 507.3081 | 511.837 | 496.9012
5512.176 | 666.4721 | 506.8074 | 510.9162 | 496.4746
5513.176 | 665.3395 | 506.3181 | 510.1769 | 496.5455
5514.176 | 665.1669 | 505.473 | 510.0082 | 497.1372
5515.176 | 664.035 | 505.0951 | 510.1534 | 498.5699
5516.176 | 661.5316 | 505.0836 | 510.2215 | 498.7661
5517.176 | 661.1944 | 504.7021 | 511.1196 | 498.3692
5518.176 | 664.1873 | 504.3576 | 511.1726 | 497.7425
5519.176 | 667.3536 | 504.2743 | 511.4599 | 497.5821
5520.176 | 669.6231 | 504.3964 | 511.9664 | 497.596
5521.176 | 670.5806 | 504.5773 | 512.5208 | 497.6836
5522.176 | 672.6933 | 505.089 | 512.3737 | 497.2275
5523.176 | 675.6691 | 506.0768 | 512.6701 | 497.0213
5524.176 | 679.0552 | 506.7182 | 513.0133 | 496.775
5525.176 | 680.6662 | 506.6999 | 514.0653 | 496.254
5526.176 | 683.133 | 506.2487 | 514.0945 | 495.8268
5527.176 | 690.5079 | 506.0546 | 514.7197 | 495.8793
5528.176 | 693.2032 | 506.4453 | 514.7927 | 496.2128
5529.176 | 694.7502 | 506.8326 | 514.3462 | 498.0895
5530.176 | 696.5383 | 506.7203 | 514.7903 | 498.6681
5531.176 | 698.4323 | 507.0535 | 514.2516 | 498.8275
5532.176 | 700.5865 | 507.369 | 513.6959 | 498.7988
5533.176 | 699.8197 | 507.3995 | 515.0962 | 499.8914
5534.176 | 697.7099 | 507.4296 | 515.0243 | 500.2308
5535.176 | 695.3794 | 508.0403 | 515.4156 | 500.0277
5536.176 | 694.5743 | 508.7544 | 514.5273 | 499.5422
5537.176 | 695.4905 | 509.4169 | 513.4635 | 498.6629
5538.176 | 695.2103 | 509.2887 | 512.5176 | 497.9541
5539.176 | 694.5317 | 509.6461 | 512.2187 | 497.4534
5540.176 | 694.3251 | 509.7091 | 512.2162 | 496.9615
5541.176 | 691.3603 | 509.4189 | 512.4715 | 496.5539
5542.176 | 689.7634 | 509.2105 | 512.4113 | 496.4231
5543.176 | 689.7212 | 509.4913 | 514.367 | 496.0781
5544.176 | 688.2982 | 509.9226 | 516.2046 | 496.4708
5545.176 | 685.9153 | 510.1951 | 515.9318 | 496.8248
5546.176 | 683.9744 | 511.21 | 515.2462 | 496.7084
5547.176 | 681.7225 | 511.5727 | 515.2897 | 496.3261
5548.176 | 680.8314 | 511.7268 | 515.033 | 496.5794
5549.176 | 680.6036 | 512.0529 | 514.7233 | 497.1554
5550.176 | 678.5969 | 511.9181 | 515.8917 | 497.0217
5551.176 | 677.8539 | 512.0552 | 516.5272 | 497.0126
5552.176 | 676.8255 | 512.6159 | 516.7564 | 497.5978
5553.176 | 675.2766 | 513.2815 | 517.2091 | 496.9648
5554.176 | 672.868 | 513.9567 | 516.4778 | 496.2396
5555.176 | 672.0109 | 513.9062 | 516.9542 | 495.4901
5556.176 | 671.9956 | 514.2059 | 517.8762 | 494.9115
5557.176 | 672.1117 | 514.7811 | 517.4373 | 494.5189
5558.176 | 671.3728 | 513.8917 | 517.6283 | 494.2601
5559.176 | 669.7739 | 513.7828 | 517.3695 | 493.6554
5560.176 | 666.3281 | 513.3411 | 516.8269 | 493.3094
5561.176 | 666.1386 | 513.1956 | 516.1598 | 494.1177
5562.176 | 666.361 | 513.9391 | 516.1364 | 494.6779
5563.176 | 665.208 | 514.3003 | 515.8831 | 496.3687
5564.176 | 662.267 | 513.8829 | 515.12 | 495.7979
5565.176 | 658.6643 | 513.0083 | 513.8004 | 495.0983
5566.176 | 656.8265 | 512.5476 | 512.7359 | 495.1094
5567.176 | 655.2363 | 511.694 | 511.7321 | 495.0897
5568.176 | 655.0399 | 510.2438 | 510.8228 | 495.0028
5569.176 | 655.7542 | 509.2364 | 509.7454 | 494.7517
5570.176 | 654.7783 | 508.8788 | 509.3663 | 494.6239
5571.176 | 653.8993 | 508.9402 | 509.5234 | 494.1597
5572.176 | 652.5065 | 508.95 | 508.9209 | 493.7497
5573.176 | 650.8056 | 508.9711 | 508.0649 | 493.7213
5574.176 | 648.5265 | 508.3521 | 507.4215 | 493.6178
5575.176 | 648.1703 | 507.6562 | 506.9197 | 494.0718
5576.176 | 647.3737 | 507.8692 | 506.5268 | 494.2938
5577.176 | 646.6783 | 507.9566 | 506.8453 | 494.2997
5578.176 | 646.1422 | 507.735 | 507.3042 | 494.0114
5579.176 | 646.5864 | 507.6484 | 507.6814 | 493.881
5580.176 | 648.9682 | 507.8996 | 507.596 | 494.1518
5581.176 | 652.5947 | 507.9754 | 508.0821 | 494.382
5582.176 | 657.6707 | 507.8857 | 509.164 | 494.2502
5583.176 | 657.3851 | 508.3852 | 510.4235 | 494.8123
5584.176 | 656.7162 | 508.4962 | 511.1799 | 494.8091
5585.176 | 654.4201 | 508.204 | 511.6846 | 495.059
5586.176 | 653.8155 | 508.0485 | 511.5515 | 495.4979
5587.176 | 653.0114 | 509.4531 | 511.3192 | 496.2597
5588.176 | 654.0703 | 510.538 | 512.3337 | 495.9787
5589.176 | 655.815 | 510.7922 | 513.3291 | 496.1159
5590.176 | 656.3612 | 511.0149 | 512.8961 | 495.9631
5591.176 | 655.158 | 511.2911 | 512.6213 | 495.5365
5592.176 | 653.3871 | 511.9584 | 512.2564 | 495.3695
5593.176 | 652.8023 | 513.0975 | 513.9248 | 494.9718
5594.176 | 652.9151 | 514.3164 | 515.7103 | 495.641
5595.176 | 652.534 | 514.6401 | 515.8374 | 496.4041
5596.176 | 654.1899 | 515.086 | 515.8717 | 495.976
5597.176 | 655.105 | 515.8346 | 515.3766 | 495.7467
5598.176 | 655.5925 | 516.1019 | 514.5428 | 495.0863
5599.176 | 653.8861 | 516.2888 | 514.3393 | 494.8309
5600.176 | 652.2428 | 515.3093 | 513.843 | 494.4721
5601.176 | 650.5959 | 514.2972 | 513.234 | 494.5636
5602.176 | 649.1539 | 513.082 | 512.8913 | 494.85
5603.176 | 646.3864 | 511.852 | 512.9416 | 495.5003
5604.176 | 644.1023 | 510.367 | 512.2044 | 495.072
5605.176 | 641.9865 | 509.5098 | 512.3193 | 494.5809
5606.176 | 641.0441 | 508.6311 | 512.8709 | 494.4554
5607.176 | 641.8126 | 507.828 | 513.4196 | 493.9394
5608.176 | 639.8742 | 506.9744 | 513.5352 | 493.521
5609.176 | 640.4342 | 506.46 | 514.3724 | 493.3583
5610.176 | 641.5502 | 506.1376 | 514.8376 | 494.1238
5611.176 | 642.1753 | 506.7514 | 515.3547 | 494.6108
5612.176 | 643.6438 | 507.4029 | 514.6819 | 494.2952
5613.176 | 645.6883 | 507.6509 | 514.1368 | 493.8662
5614.176 | 648.7183 | 507.9444 | 514.4563 | 493.704
5615.176 | 650.2826 | 508.4237 | 513.5142 | 493.4725
5616.176 | 652.6337 | 508.6224 | 513.3952 | 492.9906
5617.176 | 658.4196 | 509.336 | 513.1449 | 492.8253
5618.176 | 664.6485 | 509.4569 | 513.8989 | 492.8076
5619.176 | 666.3466 | 509.2423 | 514.4381 | 492.5574
5620.176 | 668.2907 | 510.0683 | 513.7678 | 492.2094
5621.176 | 668.7969 | 510.9332 | 513.1294 | 491.8326
5622.176 | 670.3478 | 511.7096 | 512.9337 | 491.6381
5623.176 | 674.9293 | 511.9238 | 512.6958 | 491.6624
5624.176 | 677.9477 | 512.781 | 512.4555 | 491.8444
5625.176 | 681.3678 | 512.4701 | 512.3101 | 492.3504
5626.176 | 681.7209 | 512.2441 | 512.0368 | 492.8888
5627.2073 | 680.8862 | 511.9229 | 511.8518 | 493.4404
5628.176 | 680.2103 | 511.7821 | 511.7155 | 493.6704
5629.176 | 678.6854 | 511.6887 | 511.3395 | 493.4828
5630.176 | 681.4593 | 512.4553 | 511.4108 | 493.5657
5631.176 | 681.6943 | 513.0893 | 511.4259 | 493.7642
5632.176 | 681.98 | 512.7943 | 511.1626 | 494.2414
5633.176 | 681.5128 | 512.5803 | 510.8924 | 494.7407
5634.176 | 679.7398 | 512.7972 | 510.7703 | 494.9573
5635.176 | 679.2631 | 513.4724 | 510.8494 | 495.6385
5636.176 | 678.8354 | 514.0436 | 511.0205 | 495.8917
5637.176 | 676.4076 | 513.9424 | 510.8921 | 496.3759
5638.176 | 674.1696 | 513.4277 | 510.0604 | 496.8156
5639.176 | 671.1581 | 513.2474 | 509.4496 | 496.2834
5640.176 | 670.4568 | 513.0938 | 509.1533 | 496.6676
5641.176 | 670.2219 | 513.3769 | 509.3419 | 496.3689
5642.176 | 669.3942 | 513.4068 | 509.6512 | 496.6975
5643.176 | 668.7626 | 514.7287 | 510.211 | 498.2452
5644.176 | 669.128 | 515.0139 | 510.7178 | 498.1284
5645.176 | 673.161 | 514.3998 | 510.1137 | 497.4679
5646.176 | 673.7622 | 513.6109 | 509.4965 | 497.0603
5647.176 | 673.6608 | 513.5788 | 509.2024 | 497.1262
5648.176 | 674.4416 | 513.1545 | 509.3421 | 497.5483
5649.176 | 675.1444 | 513.0824 | 509.009 | 497.7298
5650.176 | 675.4995 | 512.8866 | 508.702 | 496.985
5651.176 | 674.6371 | 512.4925 | 509.0982 | 496.479
5652.176 | 677.5246 | 512.5294 | 509.0334 | 496.244
5653.176 | 682.163 | 513.0758 | 508.9981 | 496.491
5654.176 | 688.2137 | 512.725 | 508.5213 | 497.1574
5655.176 | 692.8093 | 512.1348 | 508.3338 | 498.0042
5656.176 | 696.6612 | 513.0796 | 508.173 | 498.1809
5657.176 | 696.1027 | 512.9792 | 508.0179 | 498.6323
5658.176 | 694.4352 | 513.0024 | 507.9194 | 499.3052
5659.176 | 692.3385 | 513.0193 | 508.8307 | 499.0069
5660.176 | 693.6622 | 512.6894 | 508.9586 | 499.1073
5661.176 | 697.352 | 512.608 | 510.4633 | 498.3718
5662.176 | 701.668 | 512.0737 | 510.8436 | 497.7011
5663.176 | 701.3977 | 511.7245 | 510.1476 | 496.8171
5664.176 | 699.0155 | 511.4714 | 510.7966 | 496.1514
5665.176 | 696.7986 | 511.6781 | 510.9424 | 496.4012
5666.176 | 693.4221 | 513.0124 | 511.0118 | 496.7602
5667.176 | 691.1518 | 513.1323 | 510.9624 | 497.2993
5668.176 | 694.2964 | 513.058 | 511.1841 | 497.0268
5669.176 | 698.4006 | 513.3418 | 511.1318 | 496.6769
5670.176 | 700.5425 | 512.8767 | 511.3457 | 496.3063
5671.176 | 702.3469 | 512.832 | 510.8109 | 495.8984
5672.176 | 703.7523 | 512.4285 | 510.7995 | 496.3644
5673.176 | 704.2461 | 512.3439 | 511.2762 | 496.5701
5674.176 | 702.0109 | 512.2246 | 512.1585 | 496.3067
5675.176 | 700.5596 | 512.4378 | 512.529 | 497.084
5676.176 | 699.5058 | 512.7464 | 513.6968 | 498.1535
5677.176 | 703.4409 | 512.3943 | 514.232 | 499.2822
5678.176 | 704.9581 | 512.3009 | 513.9929 | 499.8911
5679.176 | 703.0322 | 512.674 | 513.8333 | 500.6645
5680.176 | 699.8999 | 512.8965 | 513.9637 | 500.5167
5681.176 | 696.927 | 514.1787 | 515.7635 | 500.9126
5682.176 | 693.7279 | 514.3035 | 515.4654 | 500.7223
5683.176 | 690.2699 | 514.8458 | 515.1676 | 499.9727
5684.176 | 688.6875 | 514.3855 | 515.3523 | 499.61
5685.176 | 686.2715 | 514.5461 | 516.0992 | 499.1558
5686.176 | 686.1046 | 514.5463 | 516.7695 | 498.7839
5687.176 | 686.3164 | 515.2385 | 518.5548 | 498.6524
5688.176 | 685.6764 | 515.4987 | 518.5714 | 498.8007
5689.176 | 690.8252 | 515.5667 | 518.5813 | 499.9565
5690.176 | 692.2849 | 514.7424 | 518.4569 | 500.32
5691.176 | 692.4253 | 515.0631 | 518.5835 | 500.8792
5692.176 | 690.6268 | 514.9783 | 518.6719 | 501.3509
5693.176 | 687.2358 | 515.0337 | 518.068 | 502.1518
5694.176 | 684.4055 | 515.0696 | 517.5198 | 501.9944
5695.176 | 683.1808 | 514.8786 | 517.1479 | 501.4457
5696.176 | 682.754 | 515.0258 | 516.6815 | 501.7936
5697.176 | 685.9797 | 514.9995 | 516.2091 | 501.9251
5698.176 | 686.8993 | 515.2586 | 515.7886 | 501.4261
5699.176 | 684.1466 | 515.3037 | 516.6407 | 500.847
5700.176 | 680.8721 | 515.0769 | 516.1434 | 500.8369
5701.176 | 682.4155 | 515.503 | 516.001 | 500.2278
5702.176 | 686.7644 | 515.3403 | 516.3482 | 500.3121
5703.176 | 684.9715 | 515.3271 | 517.624 | 500.0124
5704.176 | 681.4182 | 515.4253 | 517.8821 | 499.6236
5705.176 | 680.6131 | 515.1383 | 517.0418 | 499.0286
5706.176 | 678.2941 | 515.1812 | 516.3746 | 499.0034
5707.176 | 676.6327 | 515.8966 | 516.1384 | 499.4376
5708.176 | 675.1015 | 516.5333 | 515.9869 | 500.0522
5709.176 | 673.9009 | 516.9672 | 515.7725 | 500.1919
5710.176 | 673.1953 | 516.5792 | 515.2047 | 501.1654
5711.176 | 670.2594 | 516.4162 | 515.2454 | 500.8474
5712.176 | 667.881 | 517.1811 | 514.9519 | 500.5696
5713.176 | 663.8789 | 517.9337 | 514.4758 | 500.9406
5714.176 | 661.0121 | 518.1892 | 513.8439 | 501.4392
5715.176 | 658.4878 | 517.6389 | 513.0541 | 500.1772
5716.176 | 657.2951 | 517.1093 | 512.32 | 500.2268
5717.176 | 668.0082 | 517.0588 | 512.0922 | 500.5561
5718.176 | 672.8208 | 516.4784 | 512.3407 | 500.918
5719.176 | 672.1578 | 516.3993 | 511.7065 | 500.3404
5720.176 | 668.9385 | 515.1254 | 510.9565 | 500.1384
5721.176 | 665.279 | 514.1191 | 510.3378 | 499.7542
5722.176 | 661.4328 | 513.5789 | 509.7528 | 499.6053
5723.176 | 660.9114 | 512.9794 | 509.4198 | 499.3917
5724.176 | 661.4528 | 512.3173 | 509.4246 | 499.2535
5725.176 | 661.5957 | 511.7131 | 509.1247 | 499.7372
5726.176 | 660.7692 | 511.4836 | 508.631 | 499.2492
5727.176 | 659.5867 | 511.4657 | 508.4859 | 498.2543
5728.176 | 658.5279 | 511.8967 | 509.0993 | 497.6604
5729.176 | 658.5324 | 511.2447 | 509.4238 | 497.3658
5730.176 | 663.1257 | 510.5362 | 510.3098 | 497.9473
5731.176 | 665.0366 | 509.9963 | 510.1838 | 497.4255
5732.176 | 666.0656 | 509.9564 | 509.6909 | 496.5082
5733.176 | 666.1439 | 509.6746 | 508.838 | 496.7042
5734.176 | 668.4064 | 509.2183 | 508.102 | 496.3212
5735.176 | 672.3344 | 508.5952 | 508.332 | 496.0995
5736.176 | 673.954 | 508.5069 | 507.9521 | 496.3151
5737.176 | 678.5473 | 508.0246 | 507.6654 | 495.568
5738.176 | 680.0414 | 507.7766 | 507.5268 | 495.8306
5739.176 | 683.5017 | 507.9388 | 508.4685 | 495.9692
5740.176 | 690.5801 | 507.5012 | 508.2503 | 495.0501
5741.176 | 695.2252 | 507.2443 | 508.4556 | 494.5469
5742.176 | 695.7866 | 507.7577 | 508.0259 | 494.2441
5743.176 | 692.9419 | 508.6659 | 508.0226 | 494.5191
5744.176 | 690.5594 | 508.6752 | 507.9488 | 494.6586
5745.176 | 690.6314 | 509.7546 | 507.5624 | 494.6239
5746.176 | 692.004 | 509.4487 | 507.5964 | 494.7909
5747.176 | 691.4277 | 509.3923 | 507.7199 | 494.6793
5748.176 | 693.4645 | 509.2633 | 507.7415 | 494.7792
5749.176 | 693.5244 | 508.909 | 507.9172 | 496.004
5750.176 | 695.5699 | 508.9166 | 508.548 | 495.9229
5751.176 | 696.6091 | 508.96 | 508.7162 | 497.4264
5752.176 | 693.5728 | 509.307 | 509.2382 | 497.9736
5753.176 | 687.8515 | 509.7348 | 519.2326 | 497.9356
5754.176 | 684.773 | 510.4887 | 532.3321 | 498.2427
5755.176 | 682.7341 | 510.9185 | 533.006 | 503.0366
5756.176 | 678.2367 | 510.9155 | 531.9195 | 515.9333
5757.176 | 675.8709 | 511.4787 | 531.6159 | 521.1523
5758.176 | 672.6641 | 512.4222 | 531.9556 | 525.2329
5759.176 | 669.9965 | 513.146 | 531.4872 | 527.1513
5760.176 | 668.5683 | 513.2055 | 530.4066 | 528.1549
5761.176 | 665.0015 | 513.0982 | 528.7166 | 528.4425
5762.176 | 664.8702 | 512.9105 | 527.4372 | 527.7294
5763.176 | 668.2639 | 512.1913 | 525.6861 | 527.5463
5764.176 | 673.6919 | 511.3124 | 524.1514 | 528.0292
5765.176 | 675.4134 | 510.8499 | 522.8753 | 530.426
5766.176 | 676.2637 | 509.7568 | 521.2541 | 530.0555
5767.176 | 681.0586 | 508.9875 | 519.5989 | 529.6834
5768.176 | 689.929 | 508.1581 | 518.2546 | 528.5091
5769.176 | 695.259 | 507.8399 | 517.4047 | 526.4891
5770.176 | 694.6524 | 507.6353 | 516.6445 | 524.3092
5771.176 | 691.6789 | 506.7916 | 515.9283 | 522.0378
5772.176 | 689.6038 | 506.5633 | 516.5105 | 519.9868
5773.176 | 688.7296 | 509.8026 | 517.6891 | 518.2511
5774.176 | 690.6257 | 511.6179 | 521.9135 | 517.4142
5775.176 | 695.5342 | 513.7007 | 525.9542 | 515.9431
5776.176 | 702.5712 | 514.5793 | 528.4578 | 514.4395
5777.176 | 702.8053 | 515.2337 | 529.3013 | 513.7232
5778.176 | 701.8969 | 516.7037 | 530.2274 | 512.6555
5779.176 | 698.5631 | 517.2775 | 531.2649 | 512.4681
5780.176 | 694.389 | 517.1403 | 535.4828 | 512.0242
5781.176 | 696.1001 | 518.5706 | 546.8104 | 511.4147
5782.176 | 695.2696 | 518.7223 | 547.2666 | 510.975
5783.176 | 693.0655 | 518.8035 | 545.5955 | 510.7804
5784.176 | 690.851 | 518.505 | 544.1238 | 510.3179
5785.176 | 690.1448 | 517.7706 | 541.4528 | 509.86
5786.176 | 690.414 | 517.5084 | 539.2767 | 509.3398
5787.176 | 691.726 | 517.1212 | 536.6014 | 508.8902
5788.176 | 688.2556 | 516.6991 | 534.1241 | 508.6112
5789.176 | 686.1987 | 516.4917 | 531.9341 | 507.107
5790.176 | 684.8264 | 516.2981 | 530.0534 | 505.8656
5791.176 | 682.0029 | 515.6503 | 528.5313 | 505.2398
5792.176 | 680.2457 | 516.0297 | 527.0233 | 505.0443
5793.176 | 680.1941 | 516.2039 | 525.7188 | 504.748
5794.176 | 683.7064 | 515.3902 | 524.53 | 504.3627
5795.176 | 681.5995 | 514.6804 | 523.3946 | 503.8197
5796.176 | 676.5451 | 514.284 | 521.9809 | 503.1442
5797.176 | 673.142 | 513.7137 | 520.5441 | 503.6523
5798.176 | 673.2732 | 513.2011 | 519.443 | 503.0875
5799.176 | 672.6291 | 513.2909 | 518.8257 | 502.9215
5800.176 | 671.3123 | 513.4768 | 518.0873 | 502.6121
5801.176 | 669.9155 | 514.1721 | 517.7934 | 502.6023
5802.176 | 666.3088 | 514.3709 | 517.8283 | 502.7257
5803.176 | 664.7704 | 514.297 | 518.1266 | 502.118
5804.176 | 663.4052 | 514.4196 | 517.1305 | 501.9494
5805.176 | 661.7199 | 514.7269 | 515.9603 | 501.9005
5806.176 | 661.0633 | 515.1857 | 515.2281 | 501.0557
5807.176 | 660.8133 | 515.3344 | 515.3517 | 500.0823
5808.176 | 663.5796 | 515.2059 | 515.0056 | 499.9026
5809.176 | 664.7636 | 514.8624 | 514.4949 | 499.8755
5810.176 | 668.3643 | 514.2557 | 514.5534 | 499.3738
5811.176 | 670.4115 | 513.5961 | 514.2552 | 500.0481
5812.176 | 673.3221 | 513.0228 | 513.441 | 500.0422
5813.176 | 675.4205 | 512.185 | 513.0578 | 499.9458
5814.176 | 674.5436 | 511.1962 | 512.6356 | 499.7605
5815.176 | 672.5883 | 510.38 | 511.6003 | 498.7214
5816.176 | 669.8413 | 509.7499 | 510.2959 | 497.8891
5817.176 | 667.0167 | 509.7828 | 509.2985 | 497.051
5818.176 | 664.4821 | 509.2903 | 509.6511 | 497.2348
5819.176 | 664.3647 | 508.5737 | 509.3165 | 496.7899
5820.176 | 665.5723 | 508.4739 | 508.9648 | 496.1986
5821.176 | 666.447 | 508.2554 | 508.4895 | 495.9049
5822.176 | 665.2176 | 507.903 | 508.3366 | 495.7598
5823.176 | 662.1198 | 507.4346 | 507.4175 | 495.4337
5824.176 | 659.5962 | 507.1554 | 506.9399 | 495.074
5825.176 | 655.7873 | 506.2068 | 506.1189 | 494.9352
5826.176 | 651.8502 | 505.0957 | 505.6334 | 494.5879
5827.176 | 649.3954 | 504.1283 | 504.9367 | 495.1876
5828.176 | 647.15 | 502.8713 | 504.1436 | 496.2067
5829.176 | 643.0677 | 501.9587 | 503.7058 | 496.2942
5830.176 | 639.4739 | 501.179 | 502.9704 | 496.047
5831.176 | 636.0655 | 500.7675 | 502.4967 | 495.9463
5832.176 | 635.3501 | 500.398 | 502.0821 | 495.2436
5833.176 | 634.1749 | 500.134 | 501.7383 | 494.6389
5834.176 | 634.7433 | 499.699 | 501.5466 | 494.2773
5835.176 | 635.3681 | 499.2138 | 502.8496 | 493.8235
5836.176 | 634.4011 | 498.7939 | 502.8798 | 493.4034
5837.176 | 632.3109 | 498.6454 | 503.703 | 493.2852
5838.176 | 629.1172 | 498.1471 | 503.4287 | 492.6697
5839.176 | 631.5687 | 497.8752 | 503.1078 | 491.9622
5840.176 | 632.9041 | 497.6234 | 503.2111 | 491.5041
5841.176 | 633.6545 | 497.4172 | 503.1246 | 490.7525
5842.176 | 631.8257 | 497.2646 | 502.5368 | 490.1048
5843.176 | 632.1811 | 497.366 | 501.6158 | 489.5124
5844.176 | 633.0254 | 497.2613 | 500.2892 | 489.0902
5845.176 | 635.563 | 497.0431 | 500.7865 | 490.0923
5846.176 | 636.6833 | 496.7875 | 501.4399 | 491.3071
5847.176 | 638.5086 | 496.759 | 500.8562 | 490.7309
5848.176 | 638.5486 | 496.6714 | 500.7656 | 489.9188
5849.176 | 639.8035 | 497.7252 | 502.1209 | 489.428
5850.176 | 641.958 | 498.5067 | 501.8571 | 489.2126
5851.176 | 650.5859 | 499.1099 | 501.924 | 488.7765
5852.176 | 657.3074 | 499.3075 | 501.6852 | 489.2272
5853.176 | 660.1081 | 499.3325 | 501.2356 | 489.3864
5854.176 | 661.8498 | 499.3875 | 501.0994 | 489.7764
5855.176 | 661.4701 | 499.4279 | 501.0396 | 490.0033
5856.176 | 663.7214 | 499.8987 | 500.999 | 489.9335
5857.176 | 664.9451 | 500.3288 | 501.0193 | 489.7121
5858.176 | 666.6862 | 501.1241 | 500.7982 | 489.5197
5859.176 | 669.0692 | 501.6468 | 500.7533 | 490.0939
5860.176 | 675.9345 | 501.9719 | 502.39 | 490.3475
5861.176 | 681.2804 | 501.9538 | 503.0326 | 491.3629
5862.176 | 683.1993 | 502.1958 | 503.1587 | 491.3457
5863.176 | 686.5561 | 502.2107 | 503.1349 | 491.548
5864.176 | 692.9847 | 502.7819 | 503.3798 | 491.635
5865.176 | 696.6978 | 502.5172 | 503.4559 | 491.8791
5866.176 | 695.6906 | 503.0483 | 503.7287 | 492.0908
5867.176 | 695.3086 | 503.422 | 503.9762 | 492.1677
5868.176 | 693.5301 | 503.5881 | 503.8267 | 491.8739
5869.176 | 695.9214 | 503.8535 | 503.0789 | 492.1588
5870.176 | 693.2245 | 503.5473 | 502.3039 | 491.9333
5871.176 | 695.7402 | 503.4093 | 501.985 | 491.9697
5872.176 | 699.752 | 503.1911 | 501.7353 | 491.7158
5873.176 | 701.0481 | 502.792 | 501.4282 | 491.867
5874.176 | 705.2484 | 502.4363 | 501.5799 | 492.0101
5875.176 | 709.3296 | 502.4468 | 501.3085 | 491.2859
5876.176 | 715.4943 | 502.1036 | 501.2076 | 490.7815
5877.176 | 718.4908 | 501.7839 | 501.3021 | 490.4557
5878.176 | 716.7711 | 501.1496 | 501.4091 | 490.8862
5879.176 | 724.6708 | 500.7896 | 500.9517 | 491.2668
5880.176 | 727.9863 | 501.3905 | 500.6714 | 491.1223
5881.176 | 732.3225 | 501.0992 | 500.4375 | 490.7266
5882.176 | 727.8643 | 500.7581 | 499.8924 | 490.7948
5883.176 | 719.0878 | 500.5606 | 499.6381 | 490.5938
5884.176 | 725.3265 | 500.2862 | 500.0157 | 490.574
5885.176 | 727.742 | 500.0633 | 499.9494 | 490.2844
5886.176 | 726.9144 | 499.7582 | 500.2486 | 489.825
5887.176 | 723.6731 | 499.6369 | 500.1991 | 489.4877
5888.176 | 719.8682 | 499.2802 | 499.8766 | 488.9009
5889.176 | 717.019 | 499.1076 | 499.3194 | 488.4441
5890.176 | 716.8458 | 499.0021 | 499.2548 | 488.0653
5891.176 | 721.5884 | 498.827 | 500.0705 | 487.6306
5892.176 | 724.8391 | 498.3962 | 499.7046 | 487.4402
5893.176 | 727.6225 | 498.19 | 499.4978 | 487.4596
5894.176 | 729.7167 | 498.0471 | 499.4694 | 487.2727
5895.176 | 727.3655 | 497.911 | 499.0986 | 487.8799
5896.176 | 722.847 | 497.7436 | 498.7606 | 487.9304
5897.176 | 721.9546 | 497.4503 | 497.9165 | 487.8154
5898.176 | 719.9596 | 497.1352 | 497.5723 | 487.8153
5899.176 | 715.9276 | 497.0306 | 497.1321 | 487.8479
5900.176 | 711.7308 | 496.5154 | 496.8449 | 487.8882
5901.176 | 706.419 | 496.2164 | 496.3041 | 488.006
5902.176 | 700.847 | 496.1705 | 496.4987 | 488.0444
5903.176 | 697.7841 | 496.3437 | 496.6133 | 487.9529
5904.176 | 700.0747 | 496.5532 | 496.6053 | 488.4817
5905.176 | 702.3536 | 496.7311 | 496.6247 | 488.3622
5906.176 | 698.8569 | 496.6812 | 496.5316 | 488.1812
5907.176 | 691.9083 | 496.9478 | 496.228 | 487.9033
5908.176 | 685.6503 | 497.1202 | 496.417 | 487.7386
5909.176 | 680.4187 | 496.8836 | 496.8349 | 487.17
5910.176 | 675.3114 | 496.4361 | 496.6475 | 486.9589
5911.176 | 672.2633 | 496.8168 | 496.816 | 486.2913
5912.176 | 671.6712 | 496.9751 | 496.0988 | 485.5832
5913.176 | 669.68 | 497.1263 | 495.3994 | 485.191
5914.176 | 667.9948 | 497.6776 | 495.3398 | 485.3202
5915.176 | 667.2135 | 497.9698 | 495.8417 | 484.8108
5916.176 | 665.1658 | 498.1792 | 496.0325 | 484.8978
5917.176 | 662.8838 | 498.5305 | 496.2468 | 485.0048
5918.176 | 660.0172 | 498.4086 | 496.2916 | 484.9268
5919.176 | 658.9825 | 498.3168 | 496.0492 | 484.4902
5920.176 | 656.7233 | 498.1863 | 496.5803 | 483.9931
5921.176 | 656.5429 | 497.5324 | 496.9038 | 484.538
5922.176 | 656.6433 | 497.5849 | 497.0631 | 484.5806
5923.176 | 654.2095 | 497.9282 | 497.5323 | 485.4543
5924.176 | 651.0966 | 498.347 | 497.744 | 485.8245
5925.176 | 650.2492 | 499.3183 | 497.9684 | 485.8175
5926.176 | 651.7751 | 500.0435 | 499.2567 | 486.3057
5927.176 | 653.9872 | 500.4086 | 499.8259 | 485.9235
5928.176 | 655.84 | 500.5452 | 499.9607 | 486.3818
5929.176 | 656.3316 | 500.5229 | 500.151 | 486.6346
5930.176 | 660.1162 | 500.4265 | 500.4319 | 487.5377
5931.176 | 661.914 | 500.3879 | 501.3125 | 488.172
5932.176 | 665.4721 | 500.1732 | 501.5638 | 488.5816
5933.176 | 669.3526 | 500.0558 | 501.3506 | 488.5557
5934.176 | 673.4307 | 499.9699 | 501.3397 | 488.6263
5935.176 | 678.8817 | 500.0245 | 500.9149 | 488.8559
5936.176 | 684.8912 | 499.8566 | 500.5059 | 488.6951
5937.176 | 686.7581 | 499.9827 | 500.0229 | 487.947
5938.176 | 692.0325 | 499.4911 | 500.055 | 487.4259
5939.176 | 702.3795 | 498.6342 | 499.3914 | 486.8444
5940.176 | 712.9266 | 498.1091 | 499.7172 | 486.3503
5941.176 | 715.4722 | 497.7488 | 499.7059 | 485.8848
5942.176 | 714.8679 | 497.1554 | 499.8834 | 485.7699
5943.176 | 720.2564 | 496.814 | 499.7287 | 485.6777
5944.176 | 720.0965 | 496.6974 | 498.8846 | 485.5955
5945.176 | 719.5379 | 496.3836 | 498.3671 | 485.1282
5946.176 | 720.4177 | 496.0714 | 498.553 | 485.19
5947.176 | 716.8915 | 496.3299 | 498.5792 | 485.306
5948.176 | 722.7368 | 496.3561 | 499.0223 | 484.864
5949.176 | 727.9084 | 496.2086 | 498.344 | 485.179
5950.176 | 726.2565 | 496.3049 | 498.6696 | 486.1768
5951.176 | 720.2626 | 496.7037 | 499.0056 | 486.4736
5952.176 | 714.7364 | 497.1097 | 499.4511 | 487.036
5953.176 | 712.3755 | 497.1134 | 499.7166 | 487.9357
5954.176 | 710.7292 | 497.4851 | 499.9647 | 488.1268
5955.176 | 705.3066 | 497.7792 | 500.0403 | 488.3385
5956.176 | 701.1588 | 497.9255 | 499.9634 | 488.7719
5957.176 | 699.0183 | 497.5686 | 500.0029 | 488.6164
5958.176 | 705.9171 | 497.157 | 499.5875 | 488.49
5959.176 | 710.6627 | 496.8569 | 498.9079 | 488.3246
5960.176 | 718.0255 | 496.1949 | 498.5035 | 488.0466
5961.176 | 718.1288 | 496.1164 | 498.1037 | 488.8255
5962.176 | 712.8396 | 495.8999 | 497.5042 | 488.5858
5963.176 | 720.1154 | 496.3533 | 496.7844 | 488.1893
5964.176 | 728.7826 | 496.3051 | 496.2228 | 488.0714
5965.176 | 726.7826 | 496.1635 | 496.2049 | 487.7078
5966.176 | 723.1626 | 496.0836 | 496.2952 | 487.2948
5967.176 | 720.5022 | 496.0818 | 496.1727 | 486.9758
5968.176 | 717.095 | 496.2844 | 495.7989 | 486.8301
5969.176 | 713.6455 | 496.1771 | 495.6876 | 486.9614
5970.176 | 717.5142 | 495.9394 | 495.769 | 487.2687
5971.176 | 716.6633 | 495.9221 | 495.6662 | 487.6208
5972.176 | 716.7864 | 495.7453 | 495.646 | 487.7347
5973.176 | 712.3349 | 495.5409 | 495.366 | 487.8941
5974.176 | 708.2797 | 495.3431 | 495.0225 | 487.6671
5975.176 | 712.592 | 495.3639 | 495.2107 | 487.1428
5976.176 | 711.7216 | 495.863 | 495.4815 | 486.7656
5977.176 | 714.226 | 496.178 | 495.3656 | 486.5206
5978.176 | 718.0368 | 496.1988 | 495.1161 | 486.1405
5979.176 | 719.0731 | 496.1485 | 495.1103 | 486.6194
5980.176 | 715.5967 | 495.8802 | 495.2468 | 486.4493
5981.176 | 715.8702 | 495.6015 | 495.1363 | 487.0716
5982.176 | 714.1438 | 495.3288 | 494.7382 | 487.0024
5983.176 | 716.0139 | 494.9528 | 494.6882 | 487.0454
5984.176 | 718.5647 | 495.0217 | 494.5611 | 487.5975
5985.176 | 720.4641 | 495.0333 | 494.5175 | 488.3985
5986.176 | 722.8267 | 494.8945 | 494.6765 | 488.9828
5987.176 | 726.3841 | 494.5988 | 495.177 | 489.1678
5988.176 | 725.1723 | 494.4434 | 495.4112 | 488.6668
5989.176 | 723.4991 | 494.1826 | 495.3818 | 488.3731
5990.176 | 725.0451 | 494.0839 | 495.2571 | 487.73
5991.176 | 722.7833 | 493.7911 | 495.2314 | 488.1319
5992.176 | 729.3093 | 493.2141 | 494.739 | 488.0066
5993.176 | 729.0687 | 493.228 | 494.5301 | 488.038
5994.176 | 726.6884 | 492.8957 | 494.3532 | 488.0473
5995.176 | 730.5872 | 492.4711 | 493.9693 | 487.8627
5996.176 | 735.1898 | 492.0951 | 493.9313 | 487.051
5997.176 | 740.6547 | 491.5018 | 493.3883 | 486.6992
5998.176 | 749.126 | 490.9499 | 492.9382 | 486.9067
5999.176 | 748.8951 | 490.8981 | 493.2088 | 486.6591
6000.1917 | 742.2006 | 491.5186 | 493.5354 | 486.2717
6001.176 | 736.6583 | 491.5604 | 493.4639 | 486.3031
6002.176 | 737.2868 | 491.6828 | 493.6645 | 485.976
6003.176 | 732.7838 | 491.7193 | 494.046 | 485.6637
6004.176 | 727.6522 | 491.9289 | 494.0372 | 485.2496
6005.176 | 721.2995 | 492.0749 | 494.273 | 484.8988
6006.176 | 718.1177 | 491.8448 | 494.2599 | 484.3829
6007.176 | 712.2218 | 492.0975 | 494.553 | 484.1107
6008.176 | 710.9297 | 492.401 | 494.8777 | 484.1965
6009.176 | 712.212 | 492.6025 | 495.2941 | 484.4245
6010.176 | 713.8792 | 492.3779 | 495.8813 | 484.9586
6011.176 | 713.3477 | 492.4221 | 495.8604 | 485.2013
6012.176 | 716.6688 | 492.1077 | 495.7326 | 485.2278
6013.176 | 720.28 | 491.8046 | 495.6358 | 485.5801
6014.176 | 726.5534 | 491.6056 | 495.4133 | 486.3043
6015.176 | 733.7685 | 491.4459 | 495.5427 | 486.6959
6016.176 | 738.9846 | 491.0218 | 495.4448 | 486.5634
6017.176 | 741.6801 | 490.5209 | 495.3133 | 486.7602
6018.176 | 739.8411 | 490.1183 | 495.1298 | 487.3042
6019.176 | 739.2428 | 489.7851 | 494.6229 | 487.3368
6020.176 | 734.5123 | 489.6484 | 494.5728 | 486.7944
6021.176 | 729.8309 | 489.9686 | 494.7411 | 486.2551
6022.176 | 725.0738 | 490.3795 | 496.0271 | 486.7814
6023.176 | 720.9731 | 490.8185 | 496.58 | 487.1903
6024.176 | 715.3296 | 491.1597 | 497.6212 | 487.2104
6025.176 | 711.5832 | 491.3555 | 497.9762 | 487.2793
6026.176 | 711.3028 | 491.2961 | 497.7318 | 486.3368
6027.176 | 711.406 | 491.0368 | 497.5533 | 485.4884
6028.176 | 711.8511 | 490.957 | 497.6894 | 485.2687
6029.176 | 711.5388 | 490.9809 | 497.7364 | 485.4145
6030.176 | 717.3466 | 490.9211 | 498.3281 | 485.0791
6031.176 | 721.6367 | 490.7316 | 498.2508 | 485.2939
6032.176 | 719.338 | 490.4108 | 497.9069 | 485.3909
6033.176 | 715.7092 | 490.4177 | 498.064 | 486.7967
6034.176 | 711.2956 | 490.5546 | 497.5172 | 486.8822
6035.176 | 711.527 | 490.474 | 497.169 | 487.1187
6036.176 | 712.724 | 490.4643 | 496.7586 | 487.3447
6037.176 | 710.8614 | 490.9407 | 496.7103 | 487.4293
6038.176 | 707.5486 | 491.1751 | 496.6658 | 487.7539
6039.176 | 703.4679 | 490.9871 | 496.3746 | 487.4906
6040.176 | 701.1176 | 490.6216 | 496.1166 | 487.3059
6041.176 | 703.7794 | 490.278 | 495.6242 | 487.0149
6042.176 | 708.2703 | 489.5114 | 494.9474 | 486.3854
6043.176 | 709.0692 | 489.2577 | 494.4145 | 485.8025
6044.176 | 712.6325 | 488.9992 | 494.0262 | 485.224
6045.176 | 719.0052 | 489.0234 | 493.5471 | 484.5742
6046.176 | 719.6264 | 488.6935 | 492.867 | 483.8872
6047.176 | 723.6175 | 488.4592 | 492.7352 | 483.3985
6048.176 | 726.3444 | 488.5482 | 493.2234 | 483.0892
6049.176 | 727.2464 | 488.4069 | 493.2327 | 482.9946
6050.176 | 724.1194 | 488.4033 | 492.851 | 482.4779
6051.176 | 721.0562 | 488.4601 | 492.3589 | 481.9909
6052.176 | 725.679 | 488.145 | 492.0944 | 482.0402
6053.176 | 731.1296 | 488.113 | 492.3725 | 482.1132
6054.176 | 734.7954 | 487.943 | 492.3966 | 481.9699
6055.176 | 736.5558 | 487.677 | 492.1786 | 481.8525
6056.176 | 730.8454 | 487.5363 | 492.0481 | 482.8892
6057.176 | 730.4657 | 487.2864 | 491.5058 | 482.5746
6058.176 | 737.9477 | 487.0846 | 491.0811 | 482.2554
6059.176 | 740.9015 | 486.5938 | 490.7051 | 482.0423
6060.176 | 737.0318 | 486.2675 | 490.0588 | 481.6921
6061.176 | 732.8339 | 485.7372 | 489.6779 | 481.5795
6062.176 | 737.6205 | 485.2265 | 488.7628 | 481.2495
6063.176 | 739.392 | 484.9283 | 488.803 | 481.3863
6064.176 | 734.1828 | 484.7963 | 489.4901 | 482.2133
6065.176 | 727.4637 | 485.1171 | 489.9129 | 483.0423
6066.176 | 721.8469 | 485.6603 | 491.0231 | 482.754
6067.176 | 716.1723 | 486.2395 | 490.9611 | 482.785
6068.176 | 709.2818 | 486.2487 | 490.8002 | 483.1395
6069.176 | 702.7235 | 486.2344 | 490.6056 | 482.9782
6070.176 | 697.6846 | 486.6916 | 490.4242 | 482.4462
6071.176 | 694.8673 | 487.6735 | 490.202 | 481.9698
6072.176 | 693.5572 | 488.105 | 490.296 | 481.1537
6073.176 | 694.527 | 488.2111 | 490.2788 | 480.273
6074.176 | 693.9512 | 488.0848 | 490.4692 | 479.5811
6075.176 | 702.7544 | 487.9304 | 490.404 | 478.9532
6076.176 | 710.4071 | 487.754 | 490.0494 | 478.3636
6077.176 | 713.3398 | 487.4263 | 490.0358 | 478.2561
6078.176 | 710.3695 | 487.0157 | 489.8706 | 478.4527
6079.176 | 707.4133 | 486.9232 | 489.7912 | 479.2268
6080.176 | 712.6658 | 487.2696 | 489.473 | 479.2197
6081.176 | 711.9412 | 487.6379 | 489.4341 | 480.4462
6082.176 | 714.1889 | 487.6169 | 489.4952 | 479.7897
6083.176 | 710.7877 | 487.4669 | 489.3307 | 479.7289
6084.176 | 706.5104 | 487.1273 | 489.2297 | 479.3705
6085.176 | 700.7062 | 487.0594 | 488.9328 | 479.3616
6086.176 | 702.6646 | 486.9852 | 488.8545 | 479.2163
6087.176 | 707.165 | 486.7751 | 488.9579 | 479.0693
6088.176 | 704.856 | 486.5597 | 488.5731 | 479.1916
6089.176 | 703.778 | 486.5112 | 488.4414 | 478.8756
6090.176 | 711.5789 | 486.7217 | 488.4374 | 478.6046
6091.176 | 720.2311 | 486.6853 | 488.529 | 478.6943
6092.176 | 727.0737 | 486.599 | 488.5399 | 479.4031
6093.176 | 730.1053 | 486.607 | 488.5962 | 480.288
6094.176 | 728.3136 | 486.6841 | 488.8988 | 480.1638
6095.176 | 724.4832 | 486.6167 | 489.06 | 480.0166
6096.176 | 721.9139 | 486.7476 | 488.9593 | 480.0956
6097.176 | 717.8919 | 487.2724 | 489.1371 | 480.2343
6098.176 | 714.5865 | 487.1138 | 488.9613 | 479.9065
6099.176 | 710.9356 | 487.3075 | 488.9223 | 479.4644
6100.176 | 709.1675 | 487.3678 | 488.6259 | 478.8219
6101.176 | 706.1449 | 487.6106 | 488.4577 | 478.3883
6102.176 | 704.6069 | 487.8281 | 488.8913 | 478.0378
6103.176 | 702.8958 | 487.7051 | 488.9338 | 478.0142
6104.176 | 700.0325 | 487.8421 | 489.1021 | 477.7546
6105.176 | 696.7165 | 488.1319 | 489.3367 | 477.3218
6106.176 | 694.1517 | 488.151 | 490.1349 | 477.158
6107.176 | 691.4585 | 488.5766 | 490.3152 | 476.8992
6108.176 | 690.841 | 488.5213 | 490.0698 | 476.5892
6109.176 | 689.8721 | 488.3547 | 489.9344 | 476.5665
6110.176 | 692.7078 | 488.167 | 489.5115 | 476.3658
6111.176 | 691.8335 | 487.6514 | 489.2762 | 476.0695
6112.176 | 689.4767 | 487.6218 | 488.9319 | 476.1301
6113.176 | 689.9391 | 487.7022 | 488.8786 | 476.3801
6114.176 | 695.0936 | 487.5743 | 489.0615 | 476.4445
6115.176 | 694.9048 | 487.2825 | 489.2358 | 476.9558
6116.176 | 696.4514 | 486.6751 | 488.8445 | 476.9712
6117.176 | 696.1848 | 486.4489 | 488.5549 | 477.1475
6118.176 | 692.9338 | 486.1696 | 488.4028 | 477.3608
6119.176 | 693.9832 | 485.7754 | 488.2841 | 478.5784
6120.176 | 695.0382 | 485.5474 | 487.7548 | 478.1122
6121.176 | 690.6908 | 485.5514 | 487.3586 | 477.5204
6122.176 | 688.6651 | 485.3508 | 486.7354 | 477.2538
6123.176 | 693.8867 | 485.2801 | 486.5124 | 476.8817
6124.176 | 696.9097 | 484.8382 | 486.0122 | 476.5447
6125.176 | 700.7414 | 484.4966 | 485.7032 | 476.1855
6126.176 | 701.0938 | 483.9234 | 485.2636 | 476.2645
6127.176 | 700.6432 | 483.2777 | 484.7915 | 475.8223
6128.176 | 703.755 | 482.6108 | 484.0489 | 475.2544
6129.176 | 703.3329 | 482.0848 | 483.6466 | 474.7453
6130.176 | 706.5262 | 481.4281 | 483.405 | 474.4207
6131.176 | 708.2514 | 481.1812 | 483.1463 | 474.2089
6132.176 | 714.2929 | 481.4442 | 482.7405 | 474.1256
6133.176 | 718.269 | 481.1645 | 482.4951 | 473.8743
6134.176 | 714.14 | 480.771 | 482.4178 | 473.9293
6135.176 | 711.3221 | 480.7016 | 481.953 | 473.7698
6136.176 | 708.1015 | 480.9131 | 481.698 | 473.2519
6137.1917 | 703.2463 | 481.1051 | 481.4817 | 472.8524
6138.176 | 705.9057 | 481.1879 | 481.2214 | 472.6593
6139.176 | 715.7439 | 481.7429 | 480.9313 | 472.3046
6140.176 | 718.9008 | 482.4688 | 480.6154 | 472.7376
6141.176 | 715.4747 | 482.208 | 480.4582 | 472.8192
6142.176 | 712.7531 | 481.861 | 480.6437 | 472.7248
6143.176 | 708.0553 | 481.7066 | 480.3777 | 472.5768
6144.176 | 701.4508 | 481.6017 | 480.3218 | 472.8242
6145.176 | 695.9332 | 481.3381 | 480.4062 | 472.9203
6146.176 | 692.6526 | 481.5364 | 480.2372 | 472.8262
6147.176 | 692.0954 | 481.5176 | 480.0945 | 472.9775
6148.176 | 693.1578 | 481.8598 | 479.9953 | 473.2113
6149.176 | 694.5955 | 481.9312 | 480.0025 | 473.1869
6150.176 | 694.64 | 481.8878 | 480.0962 | 473.1926
6151.176 | 695.0141 | 481.9108 | 481.3813 | 473.0423
6152.176 | 692.6671 | 481.9724 | 481.4536 | 473.0918
6153.176 | 689.8553 | 482.4017 | 482.2135 | 473.3959
6154.176 | 687.8422 | 482.9109 | 482.5405 | 473.7421
6155.176 | 687.5383 | 483.5262 | 483.6349 | 474.1538
6156.176 | 684.8471 | 484.8153 | 484.7113 | 474.851
6157.176 | 687.0065 | 484.6639 | 485.1587 | 475.4628
6158.176 | 689.0132 | 484.6484 | 485.1745 | 475.7013
6159.176 | 688.8052 | 484.696 | 485.1512 | 475.557
6160.176 | 690.6397 | 484.5203 | 485.423 | 475.4626
6161.176 | 692.0059 | 485.1208 | 486.1649 | 475.3402
6162.176 | 689.3501 | 485.4807 | 486.0366 | 475.3249
6163.176 | 686.325 | 485.8415 | 486.0246 | 475.3814
6164.176 | 683.0934 | 486.7398 | 486.0484 | 475.359
6165.176 | 683.6073 | 486.8144 | 485.9765 | 475.0313
6166.176 | 682.1162 | 486.8456 | 485.9616 | 475.03
6167.176 | 683.7593 | 487.1618 | 486.0585 | 475.8011
6168.176 | 685.216 | 487.8516 | 485.8806 | 476.1044
6169.176 | 685.4799 | 487.6222 | 485.7847 | 476.9606
6170.176 | 688.5798 | 487.2771 | 485.3194 | 477.7154
6171.176 | 691.8351 | 486.9919 | 485.0568 | 477.5996
6172.176 | 694.056 | 486.834 | 485.1613 | 477.4035
6173.176 | 695.0656 | 486.8509 | 485.2309 | 477.0841
6174.176 | 692.88 | 486.8021 | 484.6052 | 476.1277
6175.176 | 693.667 | 486.3974 | 484.1617 | 475.5793
6176.176 | 695.2645 | 487.0912 | 483.8819 | 475.0875
6177.176 | 693.6892 | 487.409 | 483.6763 | 474.7838
6178.176 | 690.4995 | 487.7859 | 483.7723 | 474.6086
6179.176 | 689.6884 | 488.7057 | 484.5841 | 474.4334
6180.176 | 687.0617 | 489.2339 | 484.9721 | 474.3624
6181.176 | 682.486 | 489.5005 | 485.6095 | 474.4537
6182.176 | 685.6315 | 489.2962 | 485.7402 | 474.4296
6183.176 | 687.218 | 489.0024 | 486.0233 | 474.4835
6184.176 | 689.4391 | 488.7168 | 486.1121 | 474.3328
6185.176 | 687.5163 | 488.1179 | 485.8774 | 474.8773
6186.176 | 685.574 | 487.5618 | 485.3135 | 475.1642
6187.176 | 682.519 | 487.5856 | 485.3385 | 474.8962
6188.176 | 678.5197 | 487.5277 | 484.7868 | 474.6071
6189.176 | 676.8506 | 487.7604 | 484.4805 | 474.4692
6190.176 | 678.8563 | 487.5972 | 484.0896 | 474.463
6191.176 | 685.5503 | 487.5603 | 484.0428 | 474.3236
6192.176 | 691.3355 | 486.9296 | 483.7081 | 473.992
6193.176 | 698.8651 | 486.3147 | 483.3584 | 473.8991
6194.176 | 700.6739 | 486.0626 | 483.006 | 473.8198
6195.176 | 696.1642 | 485.4162 | 482.395 | 473.4965
6196.176 | 692.7913 | 484.9865 | 481.7393 | 473.6206
6197.176 | 691.3774 | 484.4819 | 480.805 | 473.9016
6198.176 | 692.1324 | 484.2417 | 480.4638 | 473.5173
6199.176 | 693.0333 | 484.1893 | 480.3101 | 472.9277
6200.176 | 692.9568 | 484.5391 | 480.0652 | 472.1284
6201.176 | 690.4891 | 484.6225 | 480.1252 | 471.714
6202.176 | 692.2743 | 484.5883 | 480.165 | 471.6394
6203.176 | 694.107 | 485.3208 | 480.6492 | 471.1985
6204.176 | 695.2652 | 485.0551 | 480.4839 | 471.4052
6205.176 | 694.9599 | 484.3205 | 480.0704 | 471.1962
6206.176 | 691.4584 | 483.8213 | 479.995 | 471.4202
6207.176 | 692.7725 | 483.4035 | 481.2096 | 471.4718
6208.176 | 691.5891 | 483.1986 | 481.9294 | 471.168
6209.176 | 693.2598 | 483.2827 | 482.068 | 471.3944
6210.176 | 697.4433 | 483.4288 | 482.0063 | 471.6024
6211.176 | 699.8461 | 483.4657 | 481.7559 | 471.7223
6212.176 | 695.5059 | 482.8111 | 481.3147 | 471.4876
6213.176 | 693.5529 | 482.4448 | 480.996 | 470.9417
6214.176 | 689.5891 | 481.9053 | 480.5684 | 470.845
6215.176 | 687.1239 | 481.7109 | 480.0634 | 470.5364
6216.176 | 685.9373 | 481.5838 | 479.904 | 470.3481
6217.176 | 687.7305 | 482.0866 | 479.8696 | 470.5134
6218.176 | 684.6841 | 482.976 | 479.8972 | 470.4464
6219.176 | 682.7715 | 483.7603 | 480.2556 | 470.4139
6220.176 | 684.199 | 484.1571 | 480.573 | 470.1585
6221.176 | 685.5987 | 484.0929 | 480.932 | 470.1663
6222.176 | 691.3285 | 483.6794 | 481.26 | 470.3764
6223.176 | 690.0992 | 483.221 | 481.7554 | 471.1084
6224.176 | 685.7636 | 482.6518 | 481.609 | 471.2185
6225.176 | 684.8735 | 482.119 | 481.2663 | 471.0847
6226.176 | 687.9941 | 482.3591 | 480.5878 | 470.8225
6227.2073 | 688.1762 | 482.3143 | 480.0426 | 470.6503
6228.176 | 687.1615 | 482.9327 | 479.8604 | 470.164
6229.176 | 685.5504 | 483.4636 | 480.1702 | 470.1852
6230.176 | 684.4529 | 483.5555 | 480.7154 | 469.9641
6231.176 | 687.942 | 484.3502 | 481.0514 | 469.7192
6232.176 | 692.7311 | 484.0253 | 480.8402 | 469.7776
6233.176 | 690.3031 | 483.5414 | 480.7665 | 469.8004
6234.176 | 688.278 | 483.6807 | 480.5004 | 470.0634
6235.176 | 692.6562 | 483.3727 | 480.1764 | 470.4314
6236.176 | 703.2933 | 483.1512 | 479.6443 | 470.3023
6237.176 | 708.685 | 482.6801 | 479.4268 | 470.4006
6238.176 | 703.8371 | 482.1566 | 479.2054 | 470.1802
6239.176 | 699.5968 | 481.6671 | 479.007 | 469.794
6240.176 | 698.0152 | 482.1466 | 479.031 | 469.3649
6241.176 | 698.5931 | 482.277 | 479.4097 | 469.3674
6242.176 | 699.6284 | 482.158 | 479.6034 | 469.9652
6243.176 | 696.1882 | 481.7094 | 479.4881 | 470.2821
6244.176 | 691.4749 | 481.4368 | 479.321 | 469.8867
6245.176 | 687.0854 | 481.1887 | 479.2675 | 469.5348
6246.176 | 684.6674 | 481.3294 | 479.3044 | 469.3288
6247.176 | 688.2116 | 482.0305 | 479.4463 | 469.2076
6248.176 | 693.4029 | 481.8905 | 479.3628 | 468.9734
6249.176 | 698.5692 | 481.5726 | 478.9552 | 468.8907
6250.176 | 697.0638 | 481.3416 | 479.2233 | 469.0019
6251.176 | 691.5535 | 481.1121 | 479.292 | 469.2254
6252.176 | 686.9505 | 480.8029 | 479.1369 | 469.5824
6253.176 | 683.4024 | 480.4895 | 478.8198 | 469.7073
6254.176 | 678.3523 | 480.6904 | 478.286 | 469.0809
6255.176 | 677.9648 | 480.6164 | 477.8229 | 468.4999
6256.176 | 682.9288 | 481.0091 | 477.4665 | 468.2104
6257.176 | 682.1413 | 481.0836 | 477.6521 | 468.5367
6258.176 | 685.3079 | 481.1818 | 478.0405 | 468.5734
6259.176 | 685.7863 | 481.3184 | 478.193 | 468.8549
6260.176 | 686.5286 | 481.3035 | 478.879 | 469.1127
6261.176 | 686.4493 | 481.0322 | 478.9668 | 469.3174
6262.176 | 683.0546 | 480.7167 | 479.0294 | 469.6713
6263.176 | 684.8127 | 480.4255 | 478.9462 | 469.8169
6264.176 | 686.7618 | 480.343 | 478.7759 | 470.0446
6265.176 | 692.0204 | 480.0092 | 478.8642 | 470.1157
6266.176 | 694.4943 | 480.0817 | 478.6056 | 469.7846
6267.176 | 695.1596 | 479.7827 | 478.637 | 469.4707
6268.176 | 690.9633 | 479.5922 | 478.5985 | 469.5577
6269.176 | 686.5468 | 479.7581 | 478.6667 | 469.6554
6270.176 | 681.5472 | 479.8378 | 478.764 | 469.9146
6271.176 | 679.8328 | 480.4329 | 478.6315 | 469.6576
6272.176 | 682.1352 | 481.413 | 478.2414 | 469.6318
6273.176 | 681.5462 | 481.3613 | 478.2965 | 469.1705
6274.176 | 680.8095 | 481.7075 | 478.5102 | 468.8283
6275.176 | 678.7387 | 481.6798 | 478.9103 | 468.2235
6276.176 | 678.8207 | 481.7935 | 479.219 | 468.2582
6277.176 | 677.6231 | 481.8907 | 479.5246 | 468.3071
6278.176 | 675.3812 | 481.8695 | 479.6475 | 468.3791
6279.176 | 680.5356 | 482.0704 | 479.5757 | 468.502
6280.176 | 691.5334 | 481.6241 | 479.4007 | 469.2787
6281.176 | 700.6395 | 481.3361 | 479.1504 | 468.8998
6282.176 | 705.1269 | 480.9783 | 479.1525 | 469.3099
6283.176 | 705.1083 | 480.3713 | 478.9905 | 469.4216
6284.176 | 705.1822 | 480.1473 | 478.8006 | 469.4238
6285.176 | 704.6726 | 479.8882 | 478.8702 | 469.2716
6286.176 | 703.3533 | 480.0427 | 478.9101 | 469.1444
6287.176 | 705.6513 | 480.5606 | 478.9601 | 468.8327
6288.176 | 702.8115 | 480.9032 | 479.3824 | 468.8082
6289.176 | 698.5366 | 481.2363 | 479.6002 | 468.7234
6290.176 | 695.352 | 481.4333 | 479.6965 | 469.0229
6291.176 | 695.4359 | 481.5259 | 479.7973 | 469.4257
6292.176 | 692.4124 | 481.5435 | 480.0073 | 469.5195
6293.176 | 690.0874 | 481.5156 | 480.1851 | 469.5395
6294.176 | 685.6471 | 481.2329 | 480.0966 | 469.6981
6295.176 | 683.6211 | 481.2866 | 479.9837 | 471.1272
6296.1917 | 682.5885 | 481.8719 | 480.2304 | 471.8204
6297.176 | 677.9486 | 482.4563 | 480.3675 | 471.7315
6298.176 | 675.7517 | 482.9672 | 480.2319 | 471.3423
6299.176 | 676.0641 | 482.3423 | 479.8637 | 470.5723
6300.176 | 679.5624 | 482.3443 | 479.453 | 470.1829
6301.176 | 681.7779 | 482.2178 | 479.4923 | 470.0528
6302.176 | 683.9142 | 482.2251 | 479.5508 | 469.5598
6303.176 | 689.6246 | 482.1191 | 479.3204 | 469.111
6304.176 | 699.0525 | 481.647 | 479.0985 | 469.7236
6305.176 | 706.6419 | 481.0863 | 478.879 | 469.777
6306.176 | 706.2096 | 480.5625 | 478.5282 | 469.4364
6307.176 | 702.6009 | 480.0563 | 478.2338 | 469.0428
6308.176 | 703.2027 | 479.8608 | 478.0955 | 468.8236
6309.176 | 700.377 | 479.89 | 478.0621 | 468.6444
6310.176 | 696.219 | 480.3708 | 478.0222 | 468.8693
6311.176 | 691.1266 | 480.9167 | 477.8882 | 468.6986
6312.176 | 685.4511 | 480.8934 | 477.9302 | 468.508
6313.176 | 681.2012 | 481.2224 | 477.8295 | 468.2462
6314.176 | 678.4438 | 481.9295 | 478.0682 | 467.8655
6315.176 | 688.0749 | 482.3247 | 478.3638 | 467.7609
6316.176 | 693.6094 | 482.2896 | 478.6269 | 467.5261
6317.176 | 692.5549 | 482.2151 | 478.8967 | 467.3492
6318.176 | 694.8726 | 481.9081 | 478.7741 | 467.2647
6319.176 | 695.3801 | 481.4745 | 478.7513 | 467.3784
6320.176 | 691.3727 | 481.4563 | 478.8662 | 467.4949
6321.176 | 687.3945 | 481.3691 | 478.8782 | 467.553
6322.176 | 683.2855 | 482.8167 | 479.0379 | 467.6899
6323.176 | 681.3871 | 483.3369 | 479.0349 | 467.6243
6324.176 | 682.5762 | 483.0246 | 479.076 | 467.5994
6325.176 | 682.6132 | 482.3666 | 478.7955 | 467.4603
6326.1917 | 682.2675 | 481.9268 | 478.5176 | 467.4435
6327.176 | 680.3178 | 481.8548 | 478.2829 | 467.7806
6328.176 | 678.6695 | 481.8201 | 478.3007 | 467.7528
6329.176 | 685.804 | 481.8098 | 478.6436 | 467.4248
6330.176 | 690.2843 | 481.3604 | 478.6215 | 467.2456
6331.176 | 697.0515 | 480.8168 | 478.2897 | 467.0755
6332.176 | 701.4956 | 480.3784 | 478.1583 | 467.1383
6333.176 | 708.9781 | 479.8554 | 477.9929 | 467.0914
6334.176 | 714.3959 | 479.323 | 477.6598 | 466.4812
6335.176 | 714.3349 | 478.7429 | 477.0951 | 466.248
6336.176 | 719.2517 | 478.2472 | 476.3245 | 465.8242
6337.176 | 719.0703 | 477.4511 | 476.2095 | 465.6339
6338.176 | 714.1721 | 477.2571 | 475.95 | 465.4416
6339.176 | 707.7638 | 477.4935 | 475.988 | 465.1678
6340.176 | 702.0464 | 477.6113 | 475.5785 | 464.9972
6341.176 | 694.6245 | 477.4312 | 475.3403 | 464.6545
6342.176 | 686.9273 | 477.376 | 474.9419 | 464.3628
6343.176 | 682.6837 | 477.9966 | 474.7198 | 463.8503
6344.176 | 681.0745 | 477.6251 | 474.3272 | 463.4869
6345.176 | 679.1571 | 477.4479 | 473.806 | 463.4438
6346.176 | 676.139 | 477.3218 | 473.6144 | 463.3033
6347.176 | 675.4545 | 476.9939 | 473.273 | 462.787
6348.176 | 674.3936 | 476.774 | 473.113 | 462.4509
6349.176 | 673.7159 | 476.7211 | 472.9777 | 462.3484
6350.176 | 672.2401 | 476.8824 | 472.963 | 462.3505
6351.176 | 671.4288 | 476.855 | 473.045 | 462.4552
6352.176 | 668.692 | 476.8361 | 472.9608 | 462.1377
6353.176 | 666.7843 | 476.384 | 472.5141 | 462.0024
6354.176 | 664.0537 | 475.8943 | 472.0584 | 461.5347
6355.176 | 660.8946 | 475.3633 | 471.4437 | 461.1652
6356.176 | 660.7776 | 475.0537 | 471.0164 | 461.4583
6357.176 | 667.0363 | 474.7414 | 470.5593 | 461.9801
6358.176 | 668.0648 | 474.5445 | 470.3409 | 461.989
6359.176 | 668.7483 | 474.7395 | 470.0549 | 461.682
6360.176 | 672.5218 | 474.8271 | 469.8794 | 461.6354
6361.176 | 677.6452 | 475.6168 | 469.8346 | 461.4282
6362.176 | 675.8823 | 475.6795 | 469.9269 | 461.6014
6363.176 | 673.8767 | 475.3035 | 469.5151 | 461.4538
6364.176 | 670.8619 | 475.2143 | 469.2961 | 461.5856
6365.176 | 666.665 | 476.2334 | 469.1314 | 461.6717
6366.176 | 666.1622 | 476.4277 | 469.5292 | 461.5141
6367.176 | 668.5535 | 476.6138 | 470.1084 | 461.6103
6368.176 | 668.6412 | 477.001 | 470.7343 | 462.1672
6369.176 | 667.6705 | 477.1206 | 471.2862 | 463.5217
6370.176 | 667.0973 | 477.5239 | 471.7331 | 464.2467
6371.176 | 669.8062 | 477.7504 | 471.993 | 464.4585
6372.176 | 672.5901 | 477.5643 | 471.9639 | 464.8553
6373.176 | 670.1182 | 477.2208 | 471.9404 | 464.9306
6374.176 | 669.111 | 477.0317 | 471.9477 | 465.5231
6375.176 | 675.5599 | 477.0626 | 471.8668 | 465.3065
6376.176 | 680.7343 | 477.5625 | 471.7713 | 465.0807
6377.176 | 682.0715 | 477.4992 | 471.8307 | 464.7151
6378.176 | 683.1254 | 477.8684 | 471.9517 | 464.4705
6379.176 | 682.1248 | 477.8183 | 472.2659 | 464.1064
6380.176 | 682.6616 | 478.0616 | 472.2821 | 463.668
6381.176 | 693.7112 | 478.1548 | 472.2999 | 463.5111
6382.176 | 702.2912 | 477.9644 | 472.1052 | 463.7284
6383.176 | 700.9166 | 477.2664 | 471.7025 | 463.5277
6384.176 | 701.0762 | 476.6382 | 471.3945 | 463.469
6385.176 | 704.6999 | 476.6341 | 470.9377 | 463.2455
6386.176 | 701.7746 | 476.2947 | 471.1848 | 463.1973
6387.176 | 708.8965 | 477.8816 | 471.4789 | 463.5009
6388.176 | 711.7938 | 477.5221 | 471.3503 | 463.4345
6389.176 | 712.5864 | 476.7866 | 471.125 | 463.0485
6390.176 | 708.342 | 476.1757 | 470.7906 | 462.6917
6391.176 | 702.525 | 476.3884 | 470.6814 | 462.5973
6392.176 | 698.4852 | 476.3619 | 470.7079 | 462.0358
6393.176 | 695.0354 | 476.6178 | 470.8469 | 461.6581
6394.176 | 690.3048 | 476.6265 | 471.1323 | 461.4164
6395.176 | 686.1426 | 476.8752 | 471.2911 | 461.0109
6396.176 | 684.1529 | 477.1221 | 471.3375 | 460.9307
6397.176 | 681.73 | 477.5016 | 471.3523 | 460.8919
6398.176 | 679.5617 | 477.8309 | 471.3627 | 461.1212
6399.176 | 678.8974 | 478.0896 | 471.4771 | 461.495
6400.176 | 678.9584 | 477.8913 | 471.4805 | 461.9031
6401.176 | 677.6913 | 477.7271 | 471.4685 | 462.1412
6402.176 | 675.5253 | 477.3196 | 471.6868 | 462.4188
6403.176 | 673.3631 | 477.3148 | 471.9197 | 462.4253
6404.176 | 673.4924 | 477.2382 | 471.9502 | 462.2238
6405.176 | 673.6048 | 476.9644 | 471.9845 | 462.4849
6406.176 | 671.7549 | 476.5409 | 472.0687 | 462.5907
6407.176 | 672.1974 | 476.2341 | 471.9289 | 462.4156
6408.176 | 683.2895 | 476.0616 | 471.5519 | 462.1456
6409.176 | 693.7372 | 475.905 | 471.2578 | 462.007
6410.176 | 701.3821 | 476.5558 | 470.9754 | 461.8774
6411.176 | 713.3321 | 475.9132 | 470.6522 | 461.77
6412.176 | 720.3386 | 475.2688 | 470.2228 | 461.4642
6413.176 | 724.7287 | 474.7252 | 469.7943 | 461.2374
6414.176 | 723.0299 | 474.7072 | 469.4473 | 460.7639
6415.176 | 717.1594 | 474.7816 | 469.0855 | 460.5681
6416.176 | 714.4763 | 475.2784 | 468.9281 | 460.3024
6417.176 | 711.2389 | 475.3964 | 469.2353 | 460.572
6418.176 | 708.4831 | 475.7865 | 469.5816 | 460.9701
6419.176 | 705.3609 | 475.5613 | 469.74 | 460.9139
6420.176 | 703.1019 | 475.3294 | 469.7902 | 460.9448
6421.176 | 702.4753 | 475.0828 | 469.7117 | 460.7994
6422.176 | 698.9917 | 474.7628 | 469.9199 | 460.5552
6423.176 | 696.0265 | 474.4244 | 469.8652 | 460.4836
6424.176 | 693.3743 | 474.7314 | 469.7989 | 460.2141
6425.176 | 691.9283 | 474.9893 | 469.6647 | 460.0268
6426.176 | 690.0019 | 475.3023 | 469.4651 | 459.8666
6427.176 | 690.1621 | 475.5709 | 469.4044 | 459.9532
6428.176 | 687.7213 | 476.0098 | 469.3636 | 460.1897
6429.176 | 686.2226 | 476.735 | 469.3969 | 460.6326
6430.176 | 691.4316 | 476.688 | 469.4175 | 460.94
6431.176 | 690.3671 | 476.502 | 469.3802 | 461.3594
6432.176 | 687.1355 | 476.7722 | 469.5849 | 461.4371
6433.176 | 687.4815 | 476.7719 | 469.6769 | 461.525
6434.176 | 688.4912 | 476.9587 | 469.8031 | 461.6671
6435.176 | 693.8778 | 476.7933 | 470.0855 | 462.9919
6436.176 | 695.9294 | 476.5578 | 470.4221 | 463.2202
6437.176 | 695.4717 | 477.0226 | 470.4701 | 463.0937
6438.176 | 696.7212 | 477.0305 | 470.2652 | 462.8567
6439.176 | 698.2884 | 476.7856 | 470.2833 | 462.56
6440.176 | 694.4405 | 476.9393 | 470.4303 | 462.3033
6441.176 | 690.6793 | 476.6624 | 470.5007 | 462.0885
6442.176 | 689.3589 | 476.674 | 470.6018 | 462.5537
6443.176 | 687.7925 | 476.784 | 470.6016 | 462.1724
6444.176 | 696.1125 | 476.5045 | 470.5405 | 461.8724
6445.176 | 694.6739 | 476.4794 | 470.3718 | 461.4345
6446.176 | 691.9997 | 476.0989 | 470.2456 | 460.8623
6447.176 | 691.4735 | 475.8028 | 470.2947 | 460.4956
6448.176 | 689.3212 | 475.7837 | 470.3191 | 460.4263
6449.176 | 689.2611 | 475.4823 | 470.2915 | 460.1909
6450.176 | 693.3429 | 475.4052 | 470.2326 | 460.7505
6451.176 | 693.3315 | 475.103 | 470.3015 | 460.7175
6452.176 | 691.4416 | 474.7666 | 470.3277 | 460.8086
6453.176 | 691.2634 | 475.7484 | 470.0286 | 460.8729
6454.176 | 698.1332 | 475.621 | 469.7202 | 460.8638
6455.176 | 696.4032 | 475.1743 | 469.4594 | 460.6927
6456.176 | 693.1589 | 474.9074 | 469.2043 | 460.3957
6457.176 | 690.8696 | 474.4426 | 468.9941 | 460.0359
6458.176 | 691.7168 | 474.4514 | 468.7432 | 459.8837
6459.176 | 700.9675 | 474.3447 | 468.3689 | 459.6278
6460.176 | 701.6565 | 474.6042 | 468.1744 | 459.1211
6461.176 | 698.6555 | 475.1394 | 468.0611 | 458.8202
6462.176 | 692.7602 | 475.7282 | 468.1076 | 458.5602
6463.176 | 689.1545 | 475.5449 | 468.864 | 458.0769
6464.176 | 689.6783 | 475.1686 | 468.7053 | 457.8291
6465.176 | 691.0693 | 475.335 | 468.7451 | 457.8211
6466.176 | 687.1412 | 475.1664 | 468.7521 | 458.0113
6467.176 | 688.0568 | 474.8809 | 468.6724 | 457.974
6468.176 | 687.932 | 475.0854 | 468.7599 | 457.8176
6469.176 | 685.0128 | 475.5004 | 468.8403 | 457.8965
6470.176 | 681.3772 | 475.2849 | 468.9621 | 457.9629
6471.176 | 678.7541 | 475.0602 | 469.308 | 458.1376
6472.176 | 676.2322 | 474.9562 | 469.6345 | 458.2579
6473.176 | 672.7808 | 474.7515 | 469.5224 | 458.961
6474.176 | 669.1991 | 474.7328 | 469.625 | 458.7828
6475.176 | 666.4371 | 474.766 | 469.5297 | 458.7182
6476.1917 | 666.597 | 475.2691 | 469.8444 | 458.6457
6477.176 | 662.6368 | 476.0215 | 469.8831 | 458.8293
6478.176 | 659.9629 | 476.0642 | 470.0012 | 459.0026
6479.176 | 662.4631 | 476.0579 | 470.1433 | 458.9618
6480.176 | 662.0486 | 475.8349 | 469.7368 | 458.9324
6481.176 | 664.6486 | 475.6728 | 469.6931 | 458.7676
6482.176 | 666.531 | 475.3509 | 469.6825 | 458.7215
6483.176 | 667.0185 | 475.1242 | 469.5724 | 458.6213
6484.176 | 670.0158 | 474.7689 | 469.4854 | 458.4301
6485.176 | 670.4789 | 475.1594 | 469.3071 | 458.3361
6486.176 | 669.9752 | 475.3626 | 469.331 | 458.1934
6487.176 | 667.9256 | 475.6202 | 469.4986 | 458.3936
6488.176 | 666.2406 | 475.7179 | 469.5509 | 458.4879
6489.176 | 665.1439 | 476.1002 | 469.9234 | 458.9517
6490.176 | 665.8813 | 476.1579 | 470.3342 | 459.1034
6491.176 | 668.5756 | 476.0113 | 470.4374 | 459.2473
6492.176 | 666.8965 | 475.8401 | 470.4002 | 459.2684
6493.176 | 666.0543 | 475.4275 | 470.2032 | 458.9937
6494.176 | 667.219 | 475.1665 | 469.7883 | 458.7688
6495.176 | 669.561 | 474.9139 | 469.3951 | 458.3303
6496.176 | 667.812 | 474.4916 | 469.0059 | 458.2606
6497.176 | 666.3833 | 474.892 | 468.921 | 458.085
6498.176 | 665.2345 | 475.2523 | 468.7818 | 458.1778
6499.176 | 664.1912 | 475.8083 | 469.1134 | 458.0372
6500.176 | 664.5079 | 475.6125 | 469.285 | 458.2226
6501.176 | 666.7232 | 475.2821 | 469.3418 | 458.1418
6502.176 | 669.3816 | 474.7929 | 469.1752 | 457.8221
6503.176 | 670.8664 | 474.4784 | 469.0016 | 457.4785
6504.176 | 671.5979 | 474.59 | 469.0905 | 457.2722
6505.176 | 671.4859 | 474.4271 | 468.9308 | 457.6922
6506.176 | 670.6335 | 474.6972 | 468.8545 | 457.2681
6507.176 | 669.876 | 474.3373 | 468.6688 | 456.9215
6508.176 | 673.8874 | 474.4218 | 468.6059 | 456.874
6509.176 | 674.5208 | 474.8004 | 468.7643 | 456.8969
6510.176 | 674.8414 | 474.6436 | 468.9159 | 457.0241
6511.176 | 674.2083 | 474.6824 | 469.1125 | 456.8908
6512.176 | 672.0249 | 474.9708 | 469.2024 | 456.7439
6513.176 | 671.6168 | 474.5683 | 469.0437 | 456.8986
6514.176 | 668.9267 | 474.7199 | 469.2335 | 457.2205
6515.176 | 666.0094 | 474.7744 | 469.2148 | 457.6038
6516.176 | 664.8151 | 475.0764 | 469.0468 | 457.3504
6517.176 | 662.9126 | 475.5251 | 468.9943 | 457.2008
6518.176 | 660.6528 | 475.8779 | 469.0558 | 457.5242
6519.176 | 662.9107 | 475.6902 | 468.8018 | 457.2185
6520.176 | 661.1748 | 475.6404 | 468.5751 | 457.1556
6521.176 | 661.3687 | 475.2779 | 468.2847 | 457.4981
6522.176 | 660.8436 | 474.7397 | 467.9056 | 457.3829
6523.176 | 659.5543 | 474.524 | 467.5808 | 457.1148
6524.176 | 659.4682 | 474.4235 | 467.3184 | 456.9226
6525.176 | 659.7735 | 474.8414 | 467.454 | 456.4665
6526.176 | 660.2631 | 475.4072 | 467.4093 | 456.2749
6527.176 | 658.7203 | 475.6933 | 467.7244 | 456.1652
6528.176 | 658.1257 | 475.6202 | 467.9301 | 456.0126
6529.176 | 656.1623 | 475.8029 | 468.2775 | 456.1179
6530.176 | 654.1042 | 475.7278 | 468.8297 | 456.2094
6531.176 | 653.1599 | 475.4225 | 469.1357 | 457.045
6532.176 | 650.0102 | 475.5938 | 469.338 | 457.3873
6533.176 | 649.9423 | 475.4515 | 469.566 | 457.7272
6534.176 | 650.0986 | 475.3933 | 469.6034 | 457.7107
6535.176 | 650.9124 | 475.1031 | 469.5509 | 457.7215
6536.176 | 651.1095 | 475.1572 | 469.6254 | 457.8452
6537.176 | 649.2631 | 475.4751 | 469.5748 | 458.171
6538.176 | 649.8351 | 475.8733 | 469.7272 | 458.31
6539.176 | 648.749 | 476.3877 | 470.0203 | 458.2992
6540.176 | 647.517 | 476.7133 | 470.5489 | 458.2683
6541.176 | 648.0603 | 476.8214 | 470.759 | 457.9488
6542.176 | 649.138 | 476.511 | 470.616 | 457.6265
6543.176 | 650.3577 | 476.0416 | 470.5007 | 457.7459
6544.176 | 649.1824 | 475.9512 | 470.564 | 457.8315
6545.176 | 650.9646 | 475.9975 | 470.5103 | 457.5257
6546.176 | 652.5212 | 476.2469 | 470.8059 | 457.5212
6547.176 | 652.4531 | 476.461 | 470.9918 | 457.3984
6548.176 | 651.0947 | 476.2191 | 471.0232 | 457.4167
6549.176 | 649.6315 | 475.8205 | 470.8571 | 457.5384
6550.176 | 649.0056 | 475.3295 | 470.8846 | 457.6846
6551.176 | 649.3884 | 475.9159 | 470.94 | 458.0227
6552.176 | 649.285 | 475.8978 | 470.9176 | 458.1501
6553.176 | 648.5144 | 476.0662 | 471.057 | 458.0219
6554.176 | 648.0253 | 476.3204 | 471.3378 | 458.0024
6555.176 | 645.4429 | 476.0482 | 471.5077 | 457.7637
6556.176 | 644.3165 | 475.811 | 471.3933 | 457.2982
6557.176 | 645.9642 | 475.6619 | 471.3521 | 457.1219
6558.176 | 654.879 | 475.6103 | 471.2112 | 457.1972
6559.176 | 658.545 | 475.3837 | 470.9559 | 457.0097
6560.176 | 661.0838 | 475.1051 | 470.6908 | 457.1489
6561.176 | 660.9183 | 475.2147 | 470.8057 | 457.4079
6562.176 | 659.5287 | 475.2246 | 471.05 | 457.6911
6563.176 | 658.8253 | 475.2844 | 471.0669 | 457.9568
6564.176 | 657.0979 | 475.0529 | 471.0109 | 457.9412
6565.176 | 654.0881 | 475.1996 | 470.9726 | 458.0325
6566.176 | 651.9647 | 475.1131 | 470.9862 | 457.7639
6567.176 | 651.3427 | 475.1544 | 470.9198 | 457.5937
6568.176 | 652.2648 | 475.423 | 470.9104 | 457.4223
6569.176 | 653.9685 | 475.4638 | 470.8829 | 457.5361
6570.176 | 651.9543 | 475.3104 | 471.0123 | 457.8104
6571.176 | 649.8313 | 475.0016 | 470.8752 | 457.7121
6572.176 | 653.4988 | 474.74 | 470.5162 | 457.3446
6573.176 | 658.207 | 474.5729 | 470.3302 | 457.1049
6574.176 | 658.4624 | 474.6077 | 470.2691 | 456.603
6575.176 | 657.686 | 475.0967 | 469.9918 | 456.4951
6576.176 | 657.4161 | 475.3133 | 470.0385 | 456.368
6577.176 | 655.9255 | 475.7587 | 470.6476 | 456.0842
6578.176 | 654.8531 | 476.3484 | 471.1493 | 456.0618
6579.176 | 654.9256 | 476.547 | 471.4923 | 456.1806
6580.176 | 655.4337 | 476.3286 | 471.6063 | 456.1687
6581.176 | 655.8257 | 476.1013 | 471.6454 | 456.1501
6582.176 | 654.6012 | 476.1076 | 471.8057 | 456.2119
6583.176 | 652.9244 | 475.9255 | 471.6596 | 456.3275
6584.176 | 652.8861 | 475.7425 | 471.5957 | 456.4271
6585.176 | 654.5435 | 476.0024 | 471.5466 | 456.3915
6586.176 | 652.8767 | 475.6429 | 471.4418 | 456.2916
6587.176 | 654.8079 | 475.2046 | 471.0059 | 456.2972
6588.176 | 663.5694 | 474.806 | 470.7499 | 456.2672
6589.176 | 669.7435 | 475.3518 | 470.5675 | 456.1285
6590.176 | 671.1278 | 474.7302 | 470.1836 | 456.0144
6591.176 | 669.2462 | 474.1119 | 469.625 | 455.8056
6592.176 | 664.9037 | 473.6663 | 469.1089 | 455.4974
6593.176 | 662.031 | 473.2928 | 468.5183 | 455.1044
6594.176 | 661.4028 | 474.0039 | 468.1194 | 454.6148
6595.176 | 658.0396 | 473.456 | 467.5036 | 454.5882
6596.176 | 656.299 | 472.514 | 466.9366 | 454.2891
6597.176 | 659.8578 | 472.0312 | 466.4107 | 453.8621
6598.176 | 659.1343 | 471.9562 | 466.1711 | 453.7108
6599.176 | 655.9542 | 471.9353 | 466.0199 | 453.2502
6600.176 | 653.5548 | 471.9886 | 466.2175 | 453.4014
6601.176 | 651.1602 | 472.1156 | 466.1385 | 453.7793
6602.176 | 648.1758 | 472.2066 | 466.2085 | 453.9649
6603.176 | 647.5756 | 472.1016 | 466.2582 | 453.9086
6604.176 | 647.1636 | 471.9548 | 466.1074 | 453.7781
6605.176 | 643.5351 | 471.3713 | 465.8612 | 453.4696
6606.176 | 639.1223 | 470.7904 | 465.1448 | 453.1314
6607.176 | 637.0419 | 470.4602 | 464.8828 | 452.978
6608.176 | 636.4614 | 470.2174 | 464.5495 | 452.8507
6609.176 | 638.2901 | 470.4882 | 464.652 | 452.3038
6610.176 | 650.0032 | 470.6311 | 464.6173 | 452.3106
6611.176 | 650.9141 | 470.6609 | 464.6009 | 452.3627
6612.176 | 649.6612 | 470.853 | 464.6563 | 452.5472
6613.176 | 647.3562 | 470.8738 | 464.6946 | 452.4447
6614.176 | 646.409 | 470.8616 | 464.735 | 452.4732
6615.176 | 645.2987 | 471.1291 | 465.1073 | 452.7968
6616.176 | 643.9555 | 471.6925 | 465.1575 | 452.817
6617.176 | 642.6386 | 471.7884 | 465.2063 | 452.6803
6618.176 | 642.9713 | 472.2116 | 465.4111 | 453.0175
6619.176 | 649.3381 | 472.3615 | 465.5561 | 453.0111
6620.176 | 651.9056 | 472.1824 | 465.6436 | 452.8039
6621.176 | 651.5759 | 471.6865 | 465.5215 | 452.5635
6622.176 | 654.2554 | 471.0268 | 465.3378 | 452.4557
6623.176 | 658.3377 | 471.0226 | 465.161 | 452.1786
6624.176 | 659.9972 | 471.1826 | 465.2167 | 451.9944
6625.176 | 662.759 | 470.699 | 465.0327 | 451.9779
6626.176 | 670.7515 | 470.4181 | 465.0317 | 452.2219
6627.176 | 682.1402 | 470.666 | 465.6742 | 452.1459
6628.176 | 691.5038 | 470.3648 | 465.4644 | 452.1835
6629.176 | 695.2776 | 469.9076 | 465.039 | 452.2932
6630.176 | 693.2155 | 469.34 | 464.6849 | 452.3161
6631.176 | 691.3893 | 468.9737 | 464.3763 | 452.4856
6632.176 | 692.2065 | 469.1036 | 464.2033 | 452.9742
6633.176 | 695.1867 | 468.4891 | 463.7499 | 452.9505
6634.176 | 689.7914 | 467.8395 | 463.1644 | 452.6707
6635.176 | 684.6234 | 467.3867 | 462.6854 | 452.1729
6636.176 | 682.8704 | 466.9998 | 462.2932 | 452.5112
6637.176 | 685.921 | 466.8097 | 462.116 | 452.7983
6638.176 | 685.0773 | 467.008 | 462.0723 | 452.7501
6639.176 | 681.79 | 466.9031 | 461.9946 | 452.6687
6640.176 | 676.9277 | 467.0275 | 462.0024 | 452.4794
6641.176 | 671.9903 | 467.4126 | 461.964 | 452.3197
6642.176 | 667.8117 | 467.7455 | 461.9258 | 452.336
6643.176 | 663.0035 | 467.7834 | 461.7928 | 452.0107
6644.176 | 659.5362 | 467.837 | 461.8762 | 451.8038
6645.176 | 657.661 | 468.254 | 461.8514 | 451.6244
6646.176 | 659.0938 | 468.3293 | 462.0446 | 451.6547
6647.176 | 665.5757 | 468.6776 | 462.581 | 452.2347
6648.176 | 677.0674 | 468.5054 | 462.8285 | 452.251
6649.176 | 675.6384 | 468.0824 | 463.0197 | 452.257
6650.176 | 672.491 | 467.4499 | 462.7413 | 452.1746
6651.176 | 670.3721 | 466.8687 | 462.5887 | 451.9405
6652.176 | 667.4613 | 466.9873 | 462.4226 | 451.7311
6653.176 | 665.6626 | 467.1182 | 462.4703 | 451.8985
6654.176 | 663.9218 | 467.2683 | 462.1245 | 451.7234
6655.176 | 668.1293 | 467.6542 | 462.2896 | 451.4535
6656.176 | 666.3826 | 468.3403 | 462.4089 | 451.3795
6657.176 | 664.3366 | 469.041 | 462.4966 | 451.2503
6658.176 | 663.205 | 469.2299 | 462.9084 | 451.1451
6659.176 | 661.5491 | 469.5547 | 463.3847 | 451.1999
6660.176 | 661.9895 | 469.4784 | 463.7108 | 451.3809
6661.176 | 664.0776 | 469.2869 | 463.9764 | 451.4225
6662.176 | 669.4755 | 469.1723 | 463.9929 | 451.5035
6663.176 | 668.2944 | 468.9252 | 463.8928 | 451.4722
6664.176 | 665.2894 | 468.784 | 463.7329 | 451.2112
6665.176 | 664.6579 | 468.7304 | 463.4261 | 451.0412
6666.176 | 664.7811 | 469.0077 | 463.336 | 450.9753
6667.176 | 663.9742 | 469.2981 | 464.3727 | 450.6447
6668.176 | 664.4305 | 469.3153 | 464.7199 | 450.524
6669.176 | 670.2589 | 469.1335 | 464.6596 | 450.3578
6670.176 | 681.331 | 469.1328 | 464.6202 | 450.1974
6671.176 | 687.9841 | 468.6161 | 464.3971 | 450.1734
6672.176 | 688.0089 | 468.3133 | 464.1758 | 450.2919
6673.176 | 687.421 | 468.2086 | 463.8826 | 450.5677
6674.176 | 686.0022 | 467.9061 | 463.4791 | 450.444
6675.176 | 687.2973 | 467.7217 | 463.0291 | 450.2995
6676.176 | 684.9458 | 467.2589 | 462.7212 | 450.1843
6677.176 | 681.9164 | 467.3559 | 462.7315 | 450.0241
6678.176 | 680.0204 | 467.0269 | 462.2394 | 449.6505
6679.176 | 684.8863 | 466.6354 | 461.8155 | 449.2897
6680.176 | 685.6541 | 466.1258 | 461.3672 | 449.6982
6681.176 | 683.6915 | 465.8284 | 461.145 | 450.1347
6682.176 | 680.8696 | 465.7211 | 460.9291 | 450.4826
6683.176 | 678.8815 | 465.5625 | 460.5839 | 450.3126
6684.176 | 676.5118 | 465.2874 | 460.4325 | 450.0434
6685.176 | 675.7023 | 466.0344 | 460.3355 | 450.2433
6686.176 | 675.0941 | 466.7472 | 460.5759 | 450.2466
6687.176 | 680.2764 | 466.6944 | 460.53 | 450.1786
6688.176 | 679.566 | 466.7045 | 460.4577 | 450.2827
6689.176 | 678.9788 | 466.7511 | 460.6439 | 450.3618
6690.176 | 676.2853 | 466.8821 | 460.6339 | 450.3683
6691.176 | 678.0173 | 466.8188 | 460.8046 | 450.1902
6692.176 | 683.0496 | 466.6526 | 460.883 | 449.9246
6693.176 | 680.9173 | 466.3546 | 460.6957 | 449.8263
6694.176 | 677.3633 | 465.9787 | 460.5059 | 449.7087
6695.176 | 676.0931 | 466.1636 | 460.464 | 449.6823
6696.176 | 679.9891 | 466.1401 | 460.3661 | 449.8399
6697.176 | 684.2286 | 466.1656 | 460.3733 | 450.1928
6698.176 | 680.8756 | 466.4905 | 460.2132 | 449.9908
6699.176 | 677.1564 | 467.2017 | 460.1915 | 449.7598
6700.176 | 676.7398 | 466.7773 | 460.0604 | 449.8261
6701.176 | 676.2318 | 466.511 | 459.8422 | 449.923
6702.176 | 674.0709 | 466.1033 | 459.5828 | 449.7019
6703.176 | 672.5105 | 465.9796 | 459.1939 | 449.3677
6704.176 | 670.4134 | 465.6802 | 458.8902 | 449.0974
6705.176 | 671.6717 | 465.6373 | 458.6661 | 448.7853
6706.176 | 671.4857 | 465.8826 | 458.513 | 449.2267
6707.176 | 673.8053 | 466.4752 | 458.6406 | 449.6294
6708.176 | 672.2456 | 466.7882 | 459.0758 | 450.0807
6709.176 | 669.3607 | 467.0629 | 459.7872 | 450.3329
6710.176 | 666.5498 | 467.2172 | 460.2988 | 450.3404
6711.176 | 664.3721 | 467.3924 | 460.6796 | 450.2947
6712.176 | 668.9616 | 467.3698 | 460.6229 | 450.1277
6713.176 | 675.2214 | 467.1937 | 460.6127 | 450.0853
6714.176 | 682.3945 | 467.0993 | 460.3603 | 449.9529
6715.176 | 681.5696 | 466.5406 | 460.1946 | 449.9172
6716.1917 | 679.4858 | 467.2907 | 460.463 | 449.9072
6717.176 | 677.38 | 467.784 | 460.8796 | 449.9948
6718.176 | 674.834 | 468.2801 | 461.1833 | 450.3216
6719.176 | 671.2735 | 468.632 | 461.8106 | 450.4594
6720.176 | 667.5494 | 468.6176 | 462.0559 | 450.3829