## Test Conditions
DESIREE-FIRE Intermediate Scale Test 4 - Circuit Simulator Data Only
Test Date: | 2009-11-12
DCSim DAQ Start Time | 10:31
DCSim Time for Synchronization | 10:32
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 10:31
Fire Time | 11:20
Offset | 0:49 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2940 | seconds
Heat Source Offset | 0:49 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2935 | seconds
Heat Source Stop Time | 13:12
Test Duration | 1:52 | hour:minutes:seconds
| 6720 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
SOV 2 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the air temperature 3', 5', and 7' down the cable tray located in C-Position. These are labeled as "C-Position - 3'", "C-Position - Middle", " C-Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.90625 | 121.8338 | -61.2488 | 60.3333 | -0.010149 | -0.016991 | 0.0082416 | 0.059214 | -0.0063096 | 0.053676 | -0.013887 | -0.0016258 | -0.0033587 | 0.06061 | 0.023166 | 0.054311 | -61.2761 | 0.038035 | -61.1971 | 60.2213 | 59.9476 | 60.0026 | -61.2146 | -61.1843 | 0.073618 | -61.2966 | 60.0307 | 60.1628 | 60.1752 | -61.328 | 0.034184 | -0.11195 | -0.027317 | 0.05165 | 0.017466 | -0.38561 | -0.33064 | -0.07921 | -0.30251 | 0.064527 | -0.047816 | 0.031394 | -0.17044 | -0.15809 | 121.4701 | 121.1964 | 121.2514 | 61.2868 | -121.5478 | 121.2795 | 121.4116 | 121.4239 | 61.3224 | -121.6612
0.78125 | 121.9116 | -61.1664 | 60.3561 | 0.0051128 | -0.016991 | 0.008669 | 0.059427 | -0.0067368 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.061037 | 0.02338 | 0.054524 | -61.2807 | 0.038035 | -61.1971 | 60.2259 | 59.9385 | 60.0026 | -61.2146 | -61.1888 | 0.073618 | -61.2829 | 60.0307 | 60.1537 | 60.1797 | -61.3326 | -0.048213 | -0.13026 | -0.11429 | -0.030747 | 0.017466 | -0.41766 | -0.35353 | -0.16619 | -0.32539 | -0.022449 | -0.11648 | 0.049709 | -0.20249 | -0.1764 | 121.3923 | 121.1049 | 121.169 | 61.2044 | -121.5707 | 121.1971 | 121.32 | 121.3461 | 61.24 | -121.6887
2.5312 | 121.9208 | -61.2762 | 60.2692 | -0.01778 | -0.017205 | 0.008669 | 0.059427 | -0.0067368 | 0.053249 | -0.021518 | -0.0009848 | -0.0033587 | 0.06061 | 0.023166 | 0.054738 | -61.2669 | 0.038035 | -61.2017 | 60.2259 | 59.9476 | 60.0072 | -61.2238 | -61.1888 | 0.073618 | -61.2874 | 60.0262 | 60.1628 | 60.1843 | -61.328 | 0.052493 | -0.043286 | 0.009306 | 0.074538 | 0.022045 | -0.32153 | -0.26197 | -0.051744 | -0.243 | 0.087414 | -0.011193 | 0.040551 | -0.10636 | -0.084841 | 121.5021 | 121.2239 | 121.2834 | 61.3143 | -121.4929 | 121.3024 | 121.4391 | 121.4606 | 61.3499 | -121.5972
4.2188 | 121.9208 | -61.171 | 60.3882 | -0.0025182 | -0.017205 | 0.0082416 | 0.059214 | -0.0067368 | 0.053463 | -0.013887 | -0.0011986 | -0.0031451 | 0.06061 | 0.023166 | 0.054311 | -61.2807 | 0.038035 | -61.2017 | 60.2305 | 59.9431 | 60.0072 | -61.2146 | -61.1843 | 0.078197 | -61.292 | 60.0307 | 60.1628 | 60.1706 | -61.3326 | -0.043636 | -0.15773 | -0.10971 | -0.030748 | 0.012888 | -0.44512 | -0.38099 | -0.16161 | -0.35744 | -0.013293 | -0.12106 | 0.040551 | -0.22538 | -0.2176 | 121.4014 | 121.114 | 121.1782 | 61.209 | -121.6028 | 121.2017 | 121.3338 | 121.3415 | 61.2492 | -121.7208
5.9688 | 121.7697 | -61.3037 | 60.3195 | -0.01778 | -0.016991 | 0.008028 | 0.059214 | -0.0065232 | 0.053463 | -0.021518 | -0.0014122 | -0.0029313 | 0.060824 | 0.023166 | 0.054311 | -61.2761 | 0.038035 | -61.2063 | 60.2213 | 59.9431 | 59.998 | -61.2146 | -61.1934 | 0.078197 | -61.2874 | 60.0307 | 60.1628 | 60.1843 | -61.3326 | 0.089116 | -0.098218 | 0.027615 | 0.097426 | 0.00831 | -0.37646 | -0.32148 | -0.028857 | -0.28877 | 0.1103 | 0.016273 | 0.04513 | -0.15671 | -0.1352 | 121.525 | 121.2468 | 121.3017 | 61.3417 | -121.5341 | 121.3345 | 121.4665 | 121.488 | 61.3819 | -121.6521
7.7188 | 121.8796 | -61.2167 | 60.3149 | -0.01778 | -0.016991 | 0.008669 | 0.059214 | -0.0063096 | 0.053676 | -0.0062567 | -0.0014122 | -0.0035723 | 0.061037 | 0.023594 | 0.054524 | -61.2853 | 0.033457 | -61.2063 | 60.2213 | 59.9476 | 60.0026 | -61.21 | -61.1888 | 0.06904 | -61.2874 | 60.0262 | 60.172 | 60.1752 | -61.3371 | 0.00672 | -0.09364 | -0.068516 | 0.010451 | 0.003731 | -0.3673 | -0.31233 | -0.12041 | -0.28877 | 0.027905 | -0.070702 | 0.049708 | -0.14298 | -0.13978 | 121.438 | 121.1644 | 121.2194 | 61.2502 | -121.525 | 121.2429 | 121.3887 | 121.3919 | 61.2858 | -121.6521
9.3906 | 121.9299 | -61.1526 | 60.3745 | -0.0025182 | -0.017205 | 0.0084552 | 0.059214 | -0.0065232 | 0.053463 | -0.013887 | -0.0016258 | -0.0029313 | 0.060824 | 0.023166 | 0.054524 | -61.2715 | 0.042614 | -61.1971 | 60.2167 | 59.9431 | 60.0072 | -61.2192 | -61.1934 | 0.078197 | -61.2874 | 60.0353 | 60.172 | 60.1569 | -61.3326 | -0.066524 | -0.15773 | -0.11887 | -0.04448 | 0.022044 | -0.43139 | -0.36726 | -0.17992 | -0.33913 | -0.040761 | -0.13479 | 0.04513 | -0.20249 | -0.2176 | 121.3694 | 121.0957 | 121.1598 | 61.1953 | -121.5936 | 121.188 | 121.3246 | 121.3095 | 61.2308 | -121.707
11.1406 | 121.8979 | -61.2808 | 60.2463 | -0.0025182 | -0.016991 | 0.0084552 | 0.059427 | -0.0067368 | 0.05389 | -0.013887 | -0.0011986 | -0.0033587 | 0.06061 | 0.023166 | 0.054097 | -61.2761 | 0.038035 | -61.1971 | 60.2305 | 59.9476 | 60.0072 | -61.2146 | -61.1888 | 0.06904 | -61.2874 | 60.0307 | 60.172 | 60.1843 | -61.3371 | 0.066228 | -0.015819 | 0.004727 | 0.083694 | 0.017466 | -0.29864 | -0.23908 | -0.056323 | -0.21553 | 0.091992 | -0.006615 | 0.049708 | -0.074312 | -0.061953 | 121.5113 | 121.2285 | 121.288 | 61.3189 | -121.4609 | 121.3116 | 121.4528 | 121.4651 | 61.3499 | -121.5834
12.8281 | 121.8842 | -61.235 | 60.3378 | -0.0025182 | -0.016991 | 0.0084552 | 0.059214 | -0.0065232 | 0.053463 | -0.013887 | -0.0016258 | -0.0029313 | 0.060824 | 0.022953 | 0.054311 | -61.2715 | 0.038035 | -61.2017 | 60.2259 | 59.9476 | 59.998 | -61.2192 | -61.1888 | 0.082776 | -61.2874 | 60.0353 | 60.1674 | 60.1843 | -61.3326 | 0.015873 | -0.11195 | -0.036471 | 0.033339 | 0.017466 | -0.39019 | -0.33979 | -0.097522 | -0.30251 | 0.046215 | -0.052392 | 0.04513 | -0.17044 | -0.15351 | 121.4609 | 121.1827 | 121.2331 | 61.2731 | -121.557 | 121.2704 | 121.4024 | 121.4194 | 61.3178 | -121.6704
14.5625 | 121.8658 | -61.2076 | 60.347 | -0.010149 | -0.017632 | 0.0084552 | 0.059214 | -0.0065232 | 0.05389 | -0.013887 | -0.0016258 | -0.0027177 | 0.061037 | 0.023594 | 0.054311 | -61.2807 | 0.033457 | -61.2063 | 60.2259 | 59.9476 | 60.0026 | -61.21 | -61.1934 | 0.078197 | -61.2966 | 60.0307 | 60.1628 | 60.1752 | -61.3326 | -0.002435 | -0.12111 | -0.073093 | 0.001296 | 0.003731 | -0.39935 | -0.34437 | -0.12499 | -0.31624 | 0.014171 | -0.089014 | 0.035973 | -0.18418 | -0.17182 | 121.4335 | 121.1552 | 121.2102 | 61.241 | -121.557 | 121.2383 | 121.3704 | 121.3827 | 61.2858 | -121.6796
16.2969 | 121.8246 | -61.29 | 60.3012 | -0.010149 | -0.017419 | 0.008669 | 0.059 | -0.0065232 | 0.054104 | -0.013887 | -0.0014122 | -0.0031451 | 0.06061 | 0.023166 | 0.054738 | -61.2761 | 0.042614 | -61.2017 | 60.2259 | 59.9522 | 60.0072 | -61.2146 | -61.1888 | 0.073618 | -61.2874 | 60.0262 | 60.1628 | 60.1843 | -61.3326 | 0.075383 | -0.075329 | 0.013882 | 0.088271 | 0.012888 | -0.34899 | -0.29401 | -0.04259 | -0.27504 | 0.10115 | 0.00254 | 0.04513 | -0.1384 | -0.11688 | 121.5159 | 121.2422 | 121.2972 | 61.3326 | -121.5158 | 121.3161 | 121.4528 | 121.4743 | 61.3636 | -121.6338
18.0625 | 121.8979 | -61.2167 | 60.3424 | -0.0025182 | -0.016778 | 0.0084552 | 0.059214 | -0.0067368 | 0.053676 | -0.029148 | -0.0014122 | -0.0031451 | 0.060824 | 0.022953 | 0.054524 | -61.2807 | 0.038035 | -61.1971 | 60.235 | 59.9522 | 60.0026 | -61.2146 | -61.1843 | 0.073618 | -61.2966 | 60.0262 | 60.1674 | 60.1797 | -61.3371 | 0.002141 | -0.10737 | -0.063938 | 0.019607 | 0.017466 | -0.39019 | -0.33979 | -0.12041 | -0.31624 | 0.032484 | -0.079859 | 0.040551 | -0.17502 | -0.16266 | 121.4518 | 121.169 | 121.2194 | 61.2548 | -121.557 | 121.2429 | 121.3841 | 121.3965 | 61.2904 | -121.6796
19.7344 | 121.8384 | -61.2717 | 60.3058 | -0.010149 | -0.017632 | 0.0084552 | 0.059214 | -0.0067368 | 0.053676 | -0.0062567 | -0.0011986 | -0.0031451 | 0.06061 | 0.023594 | 0.054311 | -61.2807 | 0.038035 | -61.2017 | 60.2305 | 59.9568 | 60.0072 | -61.2192 | -61.1843 | 0.06904 | -61.2783 | 60.0307 | 60.1674 | 60.1752 | -61.3326 | 0.052494 | -0.075328 | -0.009007 | 0.06996 | 0.017466 | -0.34899 | -0.29859 | -0.060901 | -0.27504 | 0.087415 | -0.006614 | 0.054287 | -0.1384 | -0.13062 | 121.5021 | 121.2285 | 121.2789 | 61.3097 | -121.525 | 121.3024 | 121.4391 | 121.4468 | 61.3407 | -121.6384
21.4688 | 121.8842 | -61.203 | 60.3699 | -0.010149 | -0.017419 | 0.0084552 | 0.059 | -0.0065232 | 0.053676 | -0.021518 | -0.0014122 | -0.0033587 | 0.060824 | 0.023594 | 0.053883 | -61.2807 | 0.038035 | -61.2109 | 60.2167 | 59.9431 | 59.998 | -61.2192 | -61.1888 | 0.064461 | -61.292 | 60.0262 | 60.1628 | 60.1752 | -61.3326 | -0.01617 | -0.15315 | -0.077671 | -0.007861 | 0.008309 | -0.42681 | -0.37184 | -0.12956 | -0.34371 | 0.014172 | -0.089014 | 0.040551 | -0.20707 | -0.19471 | 121.4197 | 121.1461 | 121.201 | 61.241 | -121.589 | 121.2292 | 121.3658 | 121.3782 | 61.2675 | -121.7024
23.2344 | 121.7926 | -61.3266 | 60.3195 | -0.010149 | -0.017419 | 0.008669 | 0.059214 | -0.0065232 | 0.053249 | -0.0062567 | -0.0014122 | -0.0035723 | 0.060824 | 0.023594 | 0.054311 | -61.2715 | 0.033457 | -61.2063 | 60.2305 | 59.9522 | 60.0072 | -61.2283 | -61.1888 | 0.06904 | -61.292 | 60.0307 | 60.1674 | 60.1797 | -61.3326 | 0.098268 | -0.089061 | 0.055082 | 0.12031 | 0.022046 | -0.3673 | -0.31233 | -0.005969 | -0.28877 | 0.13777 | 0.034582 | 0.040551 | -0.15213 | -0.13977 | 121.5571 | 121.2788 | 121.3338 | 61.3601 | -121.5478 | 121.3573 | 121.494 | 121.5063 | 61.3956 | -121.6521
24.9688 | 121.7926 | -61.3266 | 60.3012 | -0.010149 | -0.017419 | 0.008669 | 0.059427 | -0.0065232 | 0.053676 | -0.021518 | -0.0014122 | -0.0035723 | 0.060824 | 0.023807 | 0.054311 | -61.2761 | 0.042614 | -61.2109 | 60.2213 | 59.9522 | 60.0026 | -61.2146 | -61.1934 | 0.078197 | -61.292 | 60.0353 | 60.1628 | 60.1843 | -61.3371 | 0.112 | -0.079907 | 0.050503 | 0.11574 | 0.003731 | -0.34899 | -0.29859 | -0.010547 | -0.26588 | 0.13319 | 0.034582 | 0.045129 | -0.1384 | -0.11688 | 121.5479 | 121.2788 | 121.3292 | 61.3692 | -121.5158 | 121.3619 | 121.4894 | 121.5109 | 61.4048 | -121.6384
26.7031 | 121.7834 | -61.3129 | 60.3149 | -0.0025182 | -0.017419 | 0.0084552 | 0.059214 | -0.0069506 | 0.05389 | -0.013887 | -0.0014122 | -0.0033587 | 0.061037 | 0.023166 | 0.054097 | -61.2761 | 0.038035 | -61.2109 | 60.2305 | 59.9568 | 60.0164 | -61.2192 | -61.1934 | 0.078197 | -61.292 | 60.0307 | 60.1628 | 60.1935 | -61.3326 | 0.093693 | -0.084483 | 0.03677 | 0.102 | 0.008309 | -0.35814 | -0.29859 | -0.019702 | -0.28419 | 0.11946 | 0.020849 | 0.040551 | -0.15213 | -0.12146 | 121.5433 | 121.2697 | 121.3292 | 61.3509 | -121.5341 | 121.3436 | 121.4757 | 121.5063 | 61.3911 | -121.6475
28.4531 | 121.907 | -61.2717 | 60.2829 | -0.010149 | -0.017632 | 0.0088826 | 0.059214 | -0.0065232 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.060824 | 0.023594 | 0.054311 | -61.2715 | 0.038035 | -61.2017 | 60.2305 | 59.9476 | 60.0072 | -61.2146 | -61.1888 | 0.073618 | -61.2874 | 60.0307 | 60.1628 | 60.1752 | -61.3326 | 0.057072 | -0.05244 | 0.00015 | 0.06996 | 0.012888 | -0.33526 | -0.2757 | -0.060901 | -0.25215 | 0.082836 | -0.015771 | 0.04513 | -0.12009 | -0.10773 | 121.5021 | 121.2193 | 121.2789 | 61.3097 | -121.4975 | 121.3024 | 121.4345 | 121.4468 | 61.3453 | -121.6155
30.2031 | 121.8887 | -61.2396 | 60.347 | -0.010149 | -0.017205 | 0.0084552 | 0.059214 | -0.0067368 | 0.053463 | -0.021518 | -0.0016258 | -0.0033587 | 0.060824 | 0.023166 | 0.054311 | -61.2807 | 0.038035 | -61.2017 | 60.2259 | 59.9476 | 60.0026 | -61.2192 | -61.1888 | 0.064461 | -61.3058 | 60.0399 | 60.1537 | 60.1752 | -61.3371 | 0.020451 | -0.12111 | -0.04105 | 0.037917 | 0.017466 | -0.39935 | -0.34437 | -0.097522 | -0.30708 | 0.050793 | -0.066129 | 0.031393 | -0.19333 | -0.17182 | 121.4655 | 121.1873 | 121.2422 | 61.2777 | -121.5662 | 121.2795 | 121.3933 | 121.4148 | 61.3041 | -121.6841
31.8906 | 121.8521 | -61.2579 | 60.3378 | -0.0025182 | -0.017419 | 0.0084552 | 0.059 | -0.0065232 | 0.053676 | -0.029148 | -0.0016258 | -0.0031451 | 0.061037 | 0.023166 | 0.054097 | -61.2715 | 0.038035 | -61.2109 | 60.2213 | 59.9522 | 60.0118 | -61.2192 | -61.1934 | 0.064461 | -61.2874 | 60.0353 | 60.1582 | 60.1797 | -61.3371 | 0.038762 | -0.11653 | -0.013582 | 0.047071 | 0.008309 | -0.38561 | -0.32606 | -0.079211 | -0.30251 | 0.064525 | -0.029503 | 0.049708 | -0.1796 | -0.15808 | 121.4792 | 121.2102 | 121.2697 | 61.296 | -121.557 | 121.2933 | 121.4162 | 121.4377 | 61.3224 | -121.675
33.6406 | 121.8979 | -61.2625 | 60.2921 | -0.0025182 | -0.017419 | 0.008669 | 0.059214 | -0.0069506 | 0.05389 | -0.0062567 | -0.0009848 | -0.0033587 | 0.060824 | 0.02338 | 0.054524 | -61.2761 | 0.033457 | -61.2109 | 60.2213 | 59.9476 | 60.0072 | -61.2283 | -61.1843 | 0.073618 | -61.2874 | 60.0262 | 60.1582 | 60.1752 | -61.3371 | 0.034181 | -0.070752 | -0.013584 | 0.051648 | 0.017467 | -0.34441 | -0.28486 | -0.074634 | -0.26589 | 0.07826 | -0.024926 | 0.049708 | -0.13382 | -0.11689 | 121.4838 | 121.2102 | 121.2697 | 61.296 | -121.5204 | 121.2887 | 121.4207 | 121.4377 | 61.3361 | -121.6292
35.3281 | 121.907 | -61.1984 | 60.3607 | -0.010149 | -0.017419 | 0.008669 | 0.059214 | -0.0067368 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.061037 | 0.02338 | 0.054311 | -61.2807 | 0.047193 | -61.2109 | 60.2259 | 59.9522 | 60.0026 | -61.2146 | -61.1888 | 0.06904 | -61.2874 | 60.0307 | 60.1628 | 60.1797 | -61.3371 | -0.01617 | -0.13484 | -0.082249 | -0.012439 | 0.003731 | -0.4085 | -0.3581 | -0.13872 | -0.32997 | 0.009594 | -0.089013 | 0.049708 | -0.19791 | -0.18097 | 121.4243 | 121.1506 | 121.201 | 61.2456 | -121.5753 | 121.2292 | 121.3612 | 121.3782 | 61.2675 | -121.6979
37.0625 | 121.8887 | -61.203 | 60.3516 | -0.010149 | -0.017632 | 0.0084552 | 0.059214 | -0.0067368 | 0.05389 | -0.021518 | -0.0016258 | -0.0031451 | 0.06061 | 0.023594 | 0.054097 | -61.2807 | 0.038035 | -61.2063 | 60.2213 | 59.9385 | 60.0118 | -61.2192 | -61.1888 | 0.06904 | -61.292 | 60.0353 | 60.1582 | 60.1752 | -61.3326 | -0.01617 | -0.13026 | -0.077671 | -0.003282 | 0.012888 | -0.41308 | -0.33979 | -0.12956 | -0.31624 | 0.014172 | -0.089014 | 0.040551 | -0.19333 | -0.1764 | 121.4243 | 121.1415 | 121.2148 | 61.241 | -121.5707 | 121.2383 | 121.3612 | 121.3782 | 61.272 | -121.6841
38.8125 | 121.8475 | -61.2579 | 60.347 | -0.010149 | -0.017632 | 0.008669 | 0.059 | -0.0069506 | 0.053249 | -0.0062567 | -0.0018394 | -0.0035723 | 0.06061 | 0.02338 | 0.054097 | -61.2761 | 0.038035 | -61.2017 | 60.235 | 59.9476 | 60.0118 | -61.2192 | -61.1934 | 0.078197 | -61.2874 | 60.0307 | 60.1674 | 60.1797 | -61.3371 | 0.038762 | -0.11195 | -0.018161 | 0.056228 | 0.017466 | -0.39935 | -0.33521 | -0.079211 | -0.31624 | 0.064525 | -0.029503 | 0.049708 | -0.1796 | -0.16724 | 121.493 | 121.2056 | 121.2697 | 61.296 | -121.5662 | 121.2887 | 121.4253 | 121.4377 | 61.3361 | -121.6841
40.5625 | 121.7834 | -61.2442 | 60.4019 | -0.0025182 | -0.017632 | 0.0082416 | 0.059214 | -0.0067368 | 0.05389 | -0.0062567 | -0.0016258 | -0.0033587 | 0.06061 | 0.023594 | 0.054097 | -61.2761 | 0.028878 | -61.2063 | 60.2213 | 59.9476 | 60.0118 | -61.21 | -61.1888 | 0.06904 | -61.292 | 60.0307 | 60.1674 | 60.1797 | -61.3371 | 0.034186 | -0.18062 | -0.031894 | 0.037917 | 0.003731 | -0.45428 | -0.39014 | -0.092944 | -0.37117 | 0.055371 | -0.047815 | 0.045129 | -0.23453 | -0.22217 | 121.4655 | 121.1918 | 121.256 | 61.2731 | -121.6119 | 121.2749 | 121.4116 | 121.4239 | 61.3132 | -121.7391
42.25 | 121.788 | -61.2991 | 60.2783 | 0.0051128 | -0.017632 | 0.008669 | 0.059214 | -0.0067368 | 0.053463 | -0.013887 | -0.0016258 | -0.0031451 | 0.061037 | 0.023594 | 0.054097 | -61.2807 | 0.038035 | -61.2017 | 60.2305 | 59.9614 | 60.0026 | -61.2192 | -61.1797 | 0.078197 | -61.292 | 60.0353 | 60.1582 | 60.1797 | -61.3371 | 0.07996 | -0.047862 | 0.018459 | 0.097426 | 0.017466 | -0.31694 | -0.27571 | -0.038013 | -0.243 | 0.11946 | 0.007116 | 0.045129 | -0.12009 | -0.098575 | 121.5296 | 121.2605 | 121.3017 | 61.3372 | -121.4975 | 121.3345 | 121.4574 | 121.4789 | 61.3773 | -121.6155
44 | 121.907 | -61.1938 | 60.3836 | -0.0025182 | -0.017846 | 0.0084552 | 0.059 | -0.0069506 | 0.053676 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060824 | 0.023594 | 0.054311 | -61.2715 | 0.038035 | -61.2017 | 60.2305 | 59.9476 | 60.0026 | -61.2146 | -61.1888 | 0.06904 | -61.292 | 60.0353 | 60.1582 | 60.1752 | -61.3371 | -0.020747 | -0.15315 | -0.077669 | -0.007859 | 0.012888 | -0.43597 | -0.38099 | -0.1433 | -0.34828 | 0.005017 | -0.098169 | 0.045129 | -0.22538 | -0.20844 | 121.4243 | 121.1415 | 121.1965 | 61.2319 | -121.5982 | 121.2292 | 121.3521 | 121.369 | 61.2629 | -121.7208
45.7344 | 121.9116 | -61.1755 | 60.3516 | 0.0051128 | -0.017419 | 0.0088826 | 0.059 | -0.0069506 | 0.05389 | -0.021518 | -0.0016258 | -0.0029313 | 0.060824 | 0.023166 | 0.054097 | -61.2807 | 0.038035 | -61.2063 | 60.2396 | 59.9522 | 60.0072 | -61.2146 | -61.1888 | 0.06904 | -61.292 | 60.0353 | 60.1674 | 60.1843 | -61.3371 | -0.039058 | -0.11195 | -0.10514 | -0.030748 | 0.00831 | -0.39934 | -0.34437 | -0.16161 | -0.31624 | -0.013294 | -0.11648 | 0.045129 | -0.18418 | -0.16724 | 121.4152 | 121.1278 | 121.1827 | 61.2136 | -121.5662 | 121.2109 | 121.3429 | 121.3599 | 61.2446 | -121.6887
47.4062 | 121.9162 | -61.1847 | 60.347 | -0.010149 | -0.017632 | 0.0084552 | 0.059214 | -0.0069506 | 0.053676 | -0.0062567 | -0.0011986 | -0.0029313 | 0.06061 | 0.023594 | 0.05367 | -61.2761 | 0.033457 | -61.2063 | 60.2213 | 59.9522 | 60.0026 | -61.2192 | -61.1934 | 0.073618 | -61.2874 | 60.0353 | 60.1628 | 60.1797 | -61.3371 | -0.034481 | -0.12568 | -0.091404 | -0.021593 | 0.012888 | -0.39477 | -0.34437 | -0.15245 | -0.31166 | -0.008718 | -0.10275 | 0.049708 | -0.18418 | -0.16724 | 121.406 | 121.1369 | 121.1873 | 61.2181 | -121.5662 | 121.22 | 121.3475 | 121.3644 | 61.2583 | -121.6841
49.1406 | 121.8338 | -61.2625 | 60.3195 | -0.010149 | -0.017419 | 0.008669 | 0.059 | -0.0065232 | 0.05389 | -0.021518 | -0.0014122 | -0.0035723 | 0.061037 | 0.023594 | 0.053883 | -61.2807 | 0.038035 | -61.1971 | 60.2259 | 59.9568 | 60.0118 | -61.2238 | -61.1888 | 0.073618 | -61.2874 | 60.0353 | 60.1674 | 60.1752 | -61.3371 | 0.03876 | -0.09364 | -0.018162 | 0.065383 | 0.026623 | -0.36272 | -0.30775 | -0.074634 | -0.28419 | 0.073681 | -0.024926 | 0.049708 | -0.15213 | -0.14435 | 121.4884 | 121.2193 | 121.2743 | 61.3005 | -121.5433 | 121.2978 | 121.4299 | 121.4377 | 61.3361 | -121.6567
50.8281 | 121.9162 | -61.1801 | 60.379 | 0.0051128 | -0.017846 | 0.0088826 | 0.059 | -0.0069506 | 0.053249 | -0.0062567 | -0.0016258 | -0.0029313 | 0.06061 | 0.023807 | 0.054311 | -61.2807 | 0.033457 | -61.2063 | 60.2213 | 59.9568 | 60.0164 | -61.2192 | -61.1843 | 0.073618 | -61.2874 | 60.0307 | 60.1582 | 60.1752 | -61.3417 | -0.039058 | -0.15773 | -0.10056 | -0.02617 | 0.012888 | -0.42223 | -0.36268 | -0.16161 | -0.34828 | -0.004137 | -0.10732 | 0.054287 | -0.2208 | -0.20386 | 121.4014 | 121.1369 | 121.1965 | 61.2136 | -121.5982 | 121.2109 | 121.3383 | 121.3553 | 61.2537 | -121.7208
52.5781 | 121.9345 | -61.1618 | 60.379 | -0.010149 | -0.017846 | 0.008669 | 0.059 | -0.0067368 | 0.053676 | -0.0062567 | -0.0014122 | -0.0029313 | 0.06061 | 0.023807 | 0.054311 | -61.2807 | 0.033457 | -61.2063 | 60.2259 | 59.9568 | 60.0118 | -61.2192 | -61.1934 | 0.073618 | -61.2874 | 60.0307 | 60.1674 | 60.1797 | -61.3326 | -0.057369 | -0.15315 | -0.11887 | -0.044481 | 0.012888 | -0.42223 | -0.36726 | -0.17076 | -0.34828 | -0.031606 | -0.12563 | 0.04513 | -0.21164 | -0.19928 | 121.3877 | 121.1186 | 121.1736 | 61.1953 | -121.5982 | 121.1925 | 121.3292 | 121.3415 | 61.2354 | -121.7116
54.3281 | 121.843 | -61.2579 | 60.3378 | 0.0051128 | -0.017846 | 0.008669 | 0.059 | -0.0069506 | 0.053463 | -0.0062567 | -0.0011986 | -0.0031451 | 0.060824 | 0.02338 | 0.054097 | -61.2761 | 0.038035 | -61.2017 | 60.2305 | 59.9568 | 60.0118 | -61.2192 | -61.1888 | 0.078197 | -61.292 | 60.0307 | 60.1674 | 60.1889 | -61.3371 | 0.038762 | -0.10737 | -0.018161 | 0.056228 | 0.017466 | -0.38103 | -0.32606 | -0.079211 | -0.30708 | 0.069104 | -0.034082 | 0.045129 | -0.17044 | -0.14893 | 121.4884 | 121.2147 | 121.2697 | 61.296 | -121.557 | 121.2887 | 121.4253 | 121.4468 | 61.3361 | -121.675
56.0625 | 121.9254 | -61.2488 | 60.2554 | -0.01778 | -0.017632 | 0.0088826 | 0.059214 | -0.0067368 | 0.053463 | -0.013887 | -0.002053 | -0.0031451 | 0.061037 | 0.023594 | 0.054311 | -61.2761 | 0.042614 | -61.2063 | 60.2259 | 59.9568 | 60.0118 | -61.2146 | -61.1843 | 0.073618 | -61.2874 | 60.0399 | 60.1674 | 60.1248 | -61.3326 | 0.034184 | -0.029553 | -0.027317 | 0.042494 | 0.00831 | -0.29863 | -0.24366 | -0.083789 | -0.21553 | 0.064527 | -0.038659 | 0.04513 | -0.088046 | -0.13063 | 121.4747 | 121.2056 | 121.2606 | 61.2914 | -121.47 | 121.2887 | 121.4162 | 121.3736 | 61.3224 | -121.588
57.8125 | 121.9162 | -61.171 | 60.3561 | -0.01778 | -0.017846 | 0.008669 | 0.058573 | -0.0067368 | 0.053463 | -0.013887 | -0.0011986 | -0.0031451 | 0.061037 | 0.02338 | 0.054311 | -61.2807 | 0.042614 | -61.2063 | 60.2305 | 59.9476 | 60.0118 | -61.2192 | -61.1934 | 0.073618 | -61.292 | 60.0307 | 60.172 | 60.1202 | -61.3371 | -0.048214 | -0.12568 | -0.10971 | -0.035326 | 0.012888 | -0.4085 | -0.34437 | -0.16619 | -0.32539 | -0.022451 | -0.12106 | 0.045129 | -0.18418 | -0.23592 | 121.4014 | 121.1186 | 121.1827 | 61.2136 | -121.5753 | 121.2017 | 121.3429 | 121.2912 | 61.2446 | -121.6933
59.5625 | 121.8063 | -61.2762 | 60.3195 | -0.010149 | -0.017632 | 0.008669 | 0.059 | -0.0069506 | 0.053463 | -0.0062567 | -0.0014122 | -0.0029313 | 0.06061 | 0.023594 | 0.054311 | -61.2715 | 0.038035 | -61.2017 | 60.235 | 59.9614 | 60.0164 | -61.2238 | -61.1888 | 0.073618 | -61.2874 | 60.0491 | 60.172 | 60.1431 | -61.3417 | 0.052493 | -0.084483 | 0.004728 | 0.074538 | 0.022045 | -0.35814 | -0.30317 | -0.06548 | -0.27046 | 0.087414 | -0.011193 | 0.054287 | -0.14755 | -0.1764 | 121.5113 | 121.2376 | 121.2926 | 61.3143 | -121.5433 | 121.3253 | 121.4482 | 121.4194 | 61.3499 | -121.6612
61.2344 | 121.8979 | -61.2122 | 60.3561 | -0.010149 | -0.017846 | 0.0084552 | 0.058786 | -0.0065232 | 0.05389 | -0.0062567 | -0.0016258 | -0.0031451 | 0.061037 | 0.023807 | 0.054524 | -61.2807 | 0.033457 | -61.1971 | 60.2259 | 59.9568 | 60.0026 | -61.2192 | -61.1888 | 0.06904 | -61.2874 | 60.0353 | 60.1582 | 60.1797 | -61.3417 | -0.007015 | -0.13026 | -0.068516 | 0.015029 | 0.022044 | -0.39934 | -0.35353 | -0.12957 | -0.32082 | 0.023327 | -0.07528 | 0.054287 | -0.19791 | -0.1764 | 121.438 | 121.169 | 121.2148 | 61.2456 | -121.5753 | 121.2475 | 121.3704 | 121.3919 | 61.2812 | -121.6979
62.9844 | 121.9208 | -61.1435 | 60.3699 | 0.0051128 | -0.017846 | 0.0088826 | 0.059 | -0.0065232 | 0.053676 | 0.0013733 | -0.0016258 | -0.0033587 | 0.06061 | 0.023594 | 0.054524 | -61.2807 | 0.033457 | -61.1926 | 60.2259 | 59.9476 | 60.0072 | -61.2238 | -61.1888 | 0.06904 | -61.2966 | 60.0445 | 60.172 | 60.1752 | -61.3417 | -0.080258 | -0.14399 | -0.13718 | -0.049057 | 0.031201 | -0.42223 | -0.36268 | -0.19823 | -0.32539 | -0.045337 | -0.1531 | 0.04513 | -0.19791 | -0.19471 | 121.3694 | 121.0911 | 121.1507 | 61.177 | -121.5936 | 121.188 | 121.3155 | 121.3187 | 61.2125 | -121.7116
64.7344 | 121.7972 | -61.2213 | 60.4202 | -0.010149 | -0.017632 | 0.0088826 | 0.058786 | -0.0069506 | 0.05389 | -0.0062567 | -0.0014122 | -0.0031451 | 0.061037 | 0.023594 | 0.053883 | -61.2761 | 0.033457 | -61.2063 | 60.2213 | 59.9522 | 60.0118 | -61.2192 | -61.1934 | 0.073618 | -61.2874 | 60.0399 | 60.1628 | 60.1431 | -61.3417 | 0.00214 | -0.19893 | -0.054783 | 0.015028 | 0.012888 | -0.46801 | -0.40845 | -0.12041 | -0.38032 | 0.027903 | -0.066125 | 0.054287 | -0.25742 | -0.27711 | 121.4426 | 121.1735 | 121.2331 | 61.2548 | -121.6394 | 121.2612 | 121.3841 | 121.3644 | 61.2949 | -121.762
66.4219 | 121.7834 | -61.322 | 60.3104 | -0.010149 | -0.017846 | 0.008669 | 0.058786 | -0.0067368 | 0.053463 | -0.021518 | -0.0016258 | -0.0031451 | 0.060396 | 0.023807 | 0.054311 | -61.2761 | 0.033457 | -61.2154 | 60.2305 | 59.9568 | 60.0118 | -61.2238 | -61.1888 | 0.064461 | -61.292 | 60.0307 | 60.1674 | 60.1614 | -61.3371 | 0.098269 | -0.079906 | 0.045925 | 0.10658 | 0.00831 | -0.35357 | -0.29859 | -0.015125 | -0.27962 | 0.13319 | 0.030004 | 0.045129 | -0.14298 | -0.14893 | 121.5525 | 121.2788 | 121.3338 | 61.3555 | -121.5341 | 121.3528 | 121.4894 | 121.4835 | 61.3865 | -121.6475
68.1719 | 121.8201 | -61.2808 | 60.3241 | -0.0025182 | -0.017846 | 0.008669 | 0.058786 | -0.0069506 | 0.05389 | -0.0062567 | -0.0014122 | -0.0031451 | 0.06061 | 0.023807 | 0.054097 | -61.2807 | 0.038035 | -61.2017 | 60.235 | 59.9614 | 60.0118 | -61.2238 | -61.1888 | 0.073618 | -61.2874 | 60.0307 | 60.1628 | 60.1523 | -61.3417 | 0.057071 | -0.089061 | 0.000149 | 0.079116 | 0.022045 | -0.36272 | -0.31232 | -0.060902 | -0.29335 | 0.091992 | -0.006615 | 0.054287 | -0.16129 | -0.17182 | 121.5159 | 121.2422 | 121.2926 | 61.3189 | -121.5478 | 121.3116 | 121.4436 | 121.4331 | 61.3544 | -121.6658
69.9219 | 121.9162 | -61.1755 | 60.3378 | -0.010149 | -0.01806 | 0.0084552 | 0.058786 | -0.0067368 | 0.053676 | -0.013887 | -0.0014122 | -0.0033587 | 0.060396 | 0.023594 | 0.054097 | -61.2853 | 0.038035 | -61.1971 | 60.2259 | 59.9476 | 60.0118 | -61.2146 | -61.1934 | 0.06904 | -61.292 | 60.0399 | 60.1674 | 60.1385 | -61.3463 | -0.039058 | -0.11195 | -0.10972 | -0.021592 | 0.017466 | -0.39019 | -0.32606 | -0.17077 | -0.29793 | -0.017873 | -0.11648 | 0.054287 | -0.17044 | -0.19929 | 121.4014 | 121.1232 | 121.1873 | 61.2136 | -121.5524 | 121.2154 | 121.3429 | 121.3141 | 61.2446 | -121.6841
71.5938 | 121.875 | -61.2122 | 60.3287 | -0.0025182 | -0.01806 | 0.008669 | 0.059 | -0.0069506 | 0.053676 | -0.021518 | -0.0016258 | -0.0029313 | 0.061037 | 0.023594 | 0.054097 | -61.2853 | 0.033457 | -61.2017 | 60.2305 | 59.9522 | 60.0072 | -61.2192 | -61.1888 | 0.073618 | -61.2874 | 60.0399 | 60.1765 | 60.1385 | -61.3417 | -0.007015 | -0.098216 | -0.073094 | 0.010451 | 0.017466 | -0.37646 | -0.32148 | -0.12957 | -0.28877 | 0.023327 | -0.07528 | 0.054287 | -0.15213 | -0.19014 | 121.4426 | 121.1644 | 121.2194 | 61.2456 | -121.5478 | 121.2521 | 121.3887 | 121.3507 | 61.2858 | -121.6704
73.3438 | 121.9299 | -61.2808 | 60.2783 | -0.010149 | -0.01806 | 0.0084552 | 0.059 | -0.0067368 | 0.053463 | -0.021518 | -0.0018394 | -0.0031451 | 0.06061 | 0.023807 | 0.054097 | -61.2761 | 0.047193 | -61.2063 | 60.235 | 59.9522 | 60.0164 | -61.2146 | -61.1934 | 0.078197 | -61.2874 | 60.0399 | 60.172 | 60.1797 | -61.3371 | 0.066228 | -0.043284 | 0.004727 | 0.074538 | 0.00831 | -0.3261 | -0.26197 | -0.056323 | -0.23842 | 0.087413 | -0.006615 | 0.049708 | -0.10636 | -0.098575 | 121.5159 | 121.233 | 121.2972 | 61.328 | -121.4929 | 121.3207 | 121.4528 | 121.4606 | 61.359 | -121.6155
75.0938 | 121.8292 | -61.2762 | 60.3333 | 0.0051128 | -0.017632 | 0.0082416 | 0.059 | -0.0067368 | 0.053463 | -0.013887 | -0.0014122 | -0.0029313 | 0.060824 | 0.023594 | 0.054524 | -61.2807 | 0.042614 | -61.2063 | 60.2259 | 59.9614 | 60.0164 | -61.2192 | -61.1888 | 0.082776 | -61.2783 | 60.0307 | 60.1674 | 60.1202 | -61.3417 | 0.057072 | -0.10737 | -0.004429 | 0.06996 | 0.012888 | -0.37188 | -0.3169 | -0.06548 | -0.30251 | 0.087414 | -0.002036 | 0.063444 | -0.16587 | -0.21303 | 121.5021 | 121.2376 | 121.2926 | 61.3189 | -121.5524 | 121.307 | 121.4436 | 121.3965 | 61.359 | -121.675
76.7812 | 121.9025 | -61.2213 | 60.3012 | -0.0025182 | -0.01806 | 0.008669 | 0.059 | -0.0067368 | 0.053676 | -0.021518 | -0.0014122 | -0.0031451 | 0.060824 | 0.023807 | 0.054311 | -61.2715 | 0.038035 | -61.2063 | 60.2259 | 59.9522 | 60.0164 | -61.2146 | -61.1888 | 0.078197 | -61.2874 | 60.0399 | 60.1628 | 60.134 | -61.3417 | 0.006718 | -0.075329 | -0.050204 | 0.015028 | 0.00831 | -0.34899 | -0.28486 | -0.12041 | -0.26131 | 0.032482 | -0.066125 | 0.054287 | -0.1384 | -0.16725 | 121.4472 | 121.1735 | 121.2377 | 61.2593 | -121.5158 | 121.2612 | 121.3841 | 121.3553 | 61.2995 | -121.6429
78.5312 | 121.9574 | -61.1572 | 60.3561 | -0.0025182 | -0.017846 | 0.0084552 | 0.059214 | -0.0071642 | 0.053676 | -0.0062567 | -0.0016258 | -0.0033587 | 0.060824 | 0.023594 | 0.054097 | -61.2807 | 0.028878 | -61.2017 | 60.2305 | 59.9568 | 60.0118 | -61.2192 | -61.198 | 0.06904 | -61.292 | 60.0307 | 60.1674 | 60.1202 | -61.3371 | -0.061946 | -0.12568 | -0.12345 | -0.04448 | 0.017466 | -0.39934 | -0.34437 | -0.17992 | -0.32539 | -0.040761 | -0.13479 | 0.045129 | -0.18875 | -0.23592 | 121.3877 | 121.114 | 121.169 | 61.1861 | -121.5753 | 121.188 | 121.3246 | 121.2775 | 61.2263 | -121.6933
80.2656 | 121.8979 | -61.2579 | 60.26 | -0.0025182 | -0.01806 | 0.0084552 | 0.059 | -0.0065232 | 0.053676 | 0.0013733 | -0.0011986 | -0.0031451 | 0.060824 | 0.024235 | 0.054097 | -61.2715 | 0.038035 | -61.2063 | 60.235 | 59.9568 | 60.0164 | -61.2283 | -61.1843 | 0.078197 | -61.2829 | 60.0445 | 60.172 | 60.1797 | -61.3417 | 0.029604 | -0.024974 | -0.013582 | 0.05165 | 0.022046 | -0.30321 | -0.24366 | -0.08379 | -0.21553 | 0.073683 | -0.024924 | 0.058866 | -0.088045 | -0.080265 | 121.493 | 121.2147 | 121.2743 | 61.296 | -121.4883 | 121.3024 | 121.4299 | 121.4377 | 61.3361 | -121.6017
81.9531 | 121.9528 | -61.1893 | 60.3653 | -0.010149 | -0.017846 | 0.0082416 | 0.058786 | -0.0067368 | 0.053463 | -0.0062567 | -0.0016258 | -0.0035723 | 0.06061 | 0.023807 | 0.054097 | -61.2715 | 0.038035 | -61.2063 | 60.2259 | 59.9522 | 60.0118 | -61.2238 | -61.1934 | 0.06904 | -61.3012 | 60.0353 | 60.172 | 60.1431 | -61.3326 | -0.034482 | -0.13942 | -0.082247 | -0.017015 | 0.017467 | -0.41308 | -0.35352 | -0.1433 | -0.32997 | -0.00414 | -0.1119 | 0.031394 | -0.19333 | -0.22218 | 121.4151 | 121.1415 | 121.201 | 61.2273 | -121.589 | 121.2246 | 121.3612 | 121.3324 | 61.2583 | -121.6979
83.7031 | 121.7789 | -61.3083 | 60.3012 | -0.0025182 | -0.01806 | 0.0084552 | 0.059 | -0.0067368 | 0.053463 | -0.021518 | -0.0014122 | -0.0033587 | 0.060396 | 0.024021 | 0.054097 | -61.2761 | 0.038035 | -61.2017 | 60.2259 | 59.9614 | 60.0255 | -61.2283 | -61.1934 | 0.073618 | -61.2874 | 60.0399 | 60.172 | 60.1935 | -61.3326 | 0.079958 | -0.075329 | 0.032193 | 0.10658 | 0.026624 | -0.33983 | -0.2757 | -0.024279 | -0.26131 | 0.11488 | 0.020851 | 0.04513 | -0.12924 | -0.10773 | 121.5342 | 121.2697 | 121.3338 | 61.3463 | -121.5295 | 121.3482 | 121.4803 | 121.5018 | 61.3819 | -121.6338
85.4375 | 121.8384 | -61.2488 | 60.3699 | -0.010149 | -0.018273 | 0.0084552 | 0.059 | -0.0069506 | 0.053676 | -0.013887 | -0.0014122 | -0.0031451 | 0.06061 | 0.023807 | 0.054311 | -61.2761 | 0.042614 | -61.2063 | 60.2305 | 59.9568 | 60.0164 | -61.2146 | -61.1888 | 0.06904 | -61.2874 | 60.0353 | 60.172 | 60.1477 | -61.3417 | 0.034184 | -0.13941 | -0.027317 | 0.042494 | 0.00831 | -0.41308 | -0.35352 | -0.092946 | -0.33455 | 0.059948 | -0.038659 | 0.054287 | -0.19791 | -0.22218 | 121.4792 | 121.2056 | 121.2651 | 61.2914 | -121.5845 | 121.2841 | 121.4207 | 121.3965 | 61.3178 | -121.7116
87.125 | 121.8109 | -61.3083 | 60.3058 | 0.0051128 | -0.017846 | 0.0082416 | 0.059 | -0.0071642 | 0.053463 | 0.0013733 | -0.0014122 | -0.0031451 | 0.06061 | 0.024021 | 0.054311 | -61.2807 | 0.042614 | -61.2154 | 60.2396 | 59.9614 | 60.0209 | -61.21 | -61.1888 | 0.073618 | -61.2829 | 60.0399 | 60.1674 | 60.1248 | -61.3463 | 0.098273 | -0.066171 | 0.027615 | 0.092847 | -0.005426 | -0.34441 | -0.28486 | -0.038015 | -0.26588 | 0.11946 | 0.02543 | 0.063445 | -0.1384 | -0.18098 | 121.5479 | 121.2697 | 121.3292 | 61.3509 | -121.5158 | 121.3482 | 121.4757 | 121.4331 | 61.3819 | -121.6521
88.875 | 121.8887 | -61.2762 | 60.2692 | -0.0025182 | -0.01806 | 0.0084552 | 0.059214 | -0.0069506 | 0.053463 | -0.021518 | -0.0018394 | -0.0031451 | 0.06061 | 0.024021 | 0.053883 | -61.2807 | 0.042614 | -61.2063 | 60.235 | 59.9614 | 60.0164 | -61.2192 | -61.1843 | 0.078197 | -61.292 | 60.0353 | 60.1674 | 60.1843 | -61.3326 | 0.057072 | -0.034129 | -0.004429 | 0.06996 | 0.012888 | -0.30779 | -0.25281 | -0.056323 | -0.23384 | 0.091993 | -0.015772 | 0.040551 | -0.10178 | -0.084841 | 121.5113 | 121.2376 | 121.2926 | 61.3189 | -121.4883 | 121.3116 | 121.4436 | 121.4606 | 61.3544 | -121.6017
90.625 | 121.8475 | -61.1847 | 60.4019 | -0.0025182 | -0.018273 | 0.0084552 | 0.059 | -0.0071642 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.06061 | 0.023807 | 0.054097 | -61.2853 | 0.038035 | -61.2063 | 60.235 | 59.9568 | 60.0164 | -61.2192 | -61.198 | 0.06904 | -61.292 | 60.0399 | 60.172 | 60.1248 | -61.3371 | -0.034481 | -0.16688 | -0.10056 | -0.021593 | 0.012888 | -0.44512 | -0.38557 | -0.15245 | -0.36201 | -0.013296 | -0.10733 | 0.045129 | -0.22995 | -0.27711 | 121.4197 | 121.1415 | 121.201 | 61.2227 | -121.6211 | 121.2246 | 121.3567 | 121.3095 | 61.2537 | -121.7391
92.2969 | 121.9208 | -61.1984 | 60.3653 | -0.0025182 | -0.018273 | 0.008669 | 0.059 | -0.0071642 | 0.053249 | -0.0062567 | -0.0014122 | -0.0029313 | 0.061037 | 0.023807 | 0.054097 | -61.2761 | 0.042614 | -61.2017 | 60.2305 | 59.9522 | 60.0164 | -61.2238 | -61.1888 | 0.073618 | -61.2966 | 60.0399 | 60.1674 | 60.1248 | -61.3417 | -0.025327 | -0.13484 | -0.077671 | -0.003282 | 0.022045 | -0.41308 | -0.34894 | -0.1433 | -0.32539 | 0.009594 | -0.09817 | 0.04513 | -0.19791 | -0.24049 | 121.4289 | 121.1506 | 121.2148 | 61.241 | -121.589 | 121.2383 | 121.3658 | 121.3232 | 61.272 | -121.707
94.0312 | 121.8155 | -61.2854 | 60.3195 | -0.010149 | -0.018273 | 0.0084552 | 0.058786 | -0.0073778 | 0.053676 | -0.021518 | -0.0014122 | -0.0033587 | 0.060824 | 0.024021 | 0.054311 | -61.2807 | 0.033457 | -61.2109 | 60.235 | 59.9522 | 60.0164 | -61.2192 | -61.1843 | 0.078197 | -61.2829 | 60.0399 | 60.172 | 60.1843 | -61.3509 | 0.066227 | -0.084483 | 0.004726 | 0.074536 | 0.008309 | -0.3673 | -0.30317 | -0.065483 | -0.27962 | 0.10115 | 0.002541 | 0.068024 | -0.14755 | -0.1352 | 121.5204 | 121.2376 | 121.3018 | 61.3189 | -121.5387 | 121.3253 | 121.4574 | 121.4697 | 61.3636 | -121.6704
95.7188 | 121.9116 | -61.1801 | 60.3653 | 0.0051128 | -0.01806 | 0.0088826 | 0.059214 | -0.0069506 | 0.053463 | -0.0062567 | -0.0016258 | -0.0031451 | 0.060824 | 0.024235 | 0.054311 | -61.2853 | 0.038035 | -61.2063 | 60.2305 | 59.9568 | 60.0118 | -61.2146 | -61.1934 | 0.06904 | -61.2966 | 60.0399 | 60.172 | 60.1706 | -61.3463 | -0.03448 | -0.13484 | -0.10514 | -0.02617 | 0.00831 | -0.4085 | -0.35352 | -0.16619 | -0.32539 | -0.013295 | -0.11648 | 0.049709 | -0.19333 | -0.19471 | 121.4106 | 121.1369 | 121.1919 | 61.2182 | -121.5799 | 121.22 | 121.3521 | 121.3507 | 61.2492 | -121.7116
97.4531 | 121.9299 | -61.2534 | 60.2737 | -0.01778 | -0.018273 | 0.008669 | 0.058786 | -0.0071642 | 0.053463 | -0.021518 | -0.0018394 | -0.0031451 | 0.060824 | 0.023807 | 0.054097 | -61.2761 | 0.042614 | -61.1971 | 60.235 | 59.9568 | 60.0164 | -61.2283 | -61.1934 | 0.078197 | -61.292 | 60.0491 | 60.1674 | 60.134 | -61.3509 | 0.025026 | -0.038707 | -0.022739 | 0.056228 | 0.031202 | -0.31695 | -0.25739 | -0.097526 | -0.22468 | 0.059947 | -0.03866 | 0.058866 | -0.10636 | -0.13978 | 121.4884 | 121.2102 | 121.2697 | 61.296 | -121.5021 | 121.3024 | 121.4207 | 121.3873 | 61.3316 | -121.6246
99.2031 | 121.7834 | -61.2305 | 60.4111 | -0.010149 | -0.018701 | 0.0084552 | 0.058573 | -0.0071642 | 0.053249 | -0.021518 | -0.0014122 | -0.0031451 | 0.060824 | 0.024021 | 0.054524 | -61.2761 | 0.042614 | -61.2017 | 60.2259 | 59.9614 | 60.0164 | -61.2192 | -61.1888 | 0.078197 | -61.292 | 60.0445 | 60.1674 | 60.1706 | -61.3509 | 0.011296 | -0.18519 | -0.045627 | 0.028762 | 0.017466 | -0.4497 | -0.39472 | -0.12041 | -0.36659 | 0.041638 | -0.061548 | 0.058866 | -0.24369 | -0.24048 | 121.4563 | 121.1918 | 121.2468 | 61.2731 | -121.6302 | 121.2749 | 121.3979 | 121.4011 | 61.3087 | -121.762
100.8906 | 121.8567 | -61.2488 | 60.3653 | -0.0025182 | -0.018273 | 0.0090964 | 0.059 | -0.0067368 | 0.053249 | -0.013887 | -0.0014122 | -0.0029313 | 0.060824 | 0.024235 | 0.054311 | -61.2761 | 0.033457 | -61.2063 | 60.2305 | 59.966 | 60.0255 | -61.2238 | -61.1888 | 0.078197 | -61.2966 | 60.0353 | 60.1674 | 60.1843 | -61.3371 | 0.025027 | -0.13484 | -0.027317 | 0.042494 | 0.017467 | -0.39934 | -0.33979 | -0.088367 | -0.32997 | 0.059948 | -0.047816 | 0.040551 | -0.19791 | -0.18097 | 121.4792 | 121.2147 | 121.2743 | 61.2822 | -121.589 | 121.2841 | 121.4162 | 121.4331 | 61.327 | -121.7024
102.6406 | 121.8063 | -61.2442 | 60.379 | -0.0025182 | -0.018487 | 0.008669 | 0.058786 | -0.0067368 | 0.05389 | -0.013887 | -0.0014122 | -0.0029313 | 0.06061 | 0.024235 | 0.054097 | -61.2761 | 0.033457 | -61.2017 | 60.2259 | 59.9568 | 60.0164 | -61.2192 | -61.1888 | 0.073618 | -61.2966 | 60.0353 | 60.1674 | 60.1797 | -61.3417 | 0.025029 | -0.15315 | -0.031894 | 0.042495 | 0.017466 | -0.42223 | -0.36268 | -0.097523 | -0.3437 | 0.055371 | -0.052393 | 0.04513 | -0.21164 | -0.19928 | 121.4701 | 121.201 | 121.2606 | 61.2777 | -121.5982 | 121.2795 | 121.4116 | 121.4239 | 61.3178 | -121.7208
104.3906 | 121.9254 | -61.2671 | 60.2509 | -0.0025182 | -0.018487 | 0.0084552 | 0.058573 | -0.0071642 | 0.053463 | -0.013887 | -0.0011986 | -0.0031451 | 0.06061 | 0.023807 | 0.054097 | -61.2761 | 0.042614 | -61.2109 | 60.235 | 59.9568 | 60.0164 | -61.2283 | -61.1934 | 0.082776 | -61.2874 | 60.0399 | 60.172 | 60.166 | -61.3509 | 0.038759 | -0.015818 | -0.009006 | 0.056226 | 0.017467 | -0.29406 | -0.2345 | -0.083793 | -0.21095 | 0.07368 | -0.020348 | 0.063445 | -0.078889 | -0.084845 | 121.5021 | 121.2239 | 121.2834 | 61.3097 | -121.4792 | 121.307 | 121.4391 | 121.4331 | 61.3499 | -121.6017
106.0625 | 121.9391 | -61.1847 | 60.3653 | 0.0051128 | -0.018487 | 0.0084552 | 0.059 | -0.0069506 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.060824 | 0.024021 | 0.054311 | -61.2761 | 0.038035 | -61.2063 | 60.2305 | 59.9522 | 60.0209 | -61.2283 | -61.1934 | 0.06904 | -61.2966 | 60.0399 | 60.1765 | 60.1294 | -61.3463 | -0.043639 | -0.13484 | -0.091404 | -0.021593 | 0.022046 | -0.41308 | -0.34437 | -0.16161 | -0.32539 | -0.008718 | -0.1119 | 0.049709 | -0.18875 | -0.23592 | 121.4151 | 121.1369 | 121.2056 | 61.2227 | -121.5936 | 121.2246 | 121.3612 | 121.3141 | 61.2537 | -121.7116
107.7969 | 121.8338 | -61.2579 | 60.3836 | -0.0025182 | -0.018273 | 0.0088826 | 0.058786 | -0.0069506 | 0.053463 | -0.021518 | -0.0016258 | -0.0031451 | 0.060824 | 0.024021 | 0.053883 | -61.2853 | 0.042614 | -61.2063 | 60.2305 | 59.966 | 60.0118 | -61.2238 | -61.1934 | 0.082776 | -61.292 | 60.0399 | 60.1765 | 60.1706 | -61.3463 | 0.034183 | -0.15315 | -0.027317 | 0.05165 | 0.017467 | -0.41765 | -0.37183 | -0.088369 | -0.3437 | 0.064525 | -0.034082 | 0.054287 | -0.20706 | -0.21302 | 121.4884 | 121.2239 | 121.2697 | 61.3005 | -121.6074 | 121.2978 | 121.4345 | 121.4285 | 61.3407 | -121.7299
109.5625 | 121.8567 | -61.2579 | 60.3149 | -0.0025182 | -0.018273 | 0.008669 | 0.059 | -0.0069506 | 0.05389 | -0.021518 | -0.0016258 | -0.0033587 | 0.060396 | 0.024021 | 0.053883 | -61.2761 | 0.038035 | -61.2109 | 60.2259 | 59.966 | 60.0209 | -61.2238 | -61.1888 | 0.073618 | -61.2874 | 60.0307 | 60.172 | 60.1889 | -61.3463 | 0.034183 | -0.089062 | -0.018161 | 0.047071 | 0.012888 | -0.34899 | -0.29401 | -0.088369 | -0.28419 | 0.069104 | -0.029503 | 0.058866 | -0.14298 | -0.12604 | 121.4838 | 121.2239 | 121.2789 | 61.296 | -121.5387 | 121.2887 | 121.4299 | 121.4468 | 61.3316 | -121.6612
111.2344 | 121.8384 | -61.3037 | 60.2829 | -0.0025182 | -0.018487 | 0.008669 | 0.058786 | -0.0069506 | 0.053676 | -0.013887 | -0.0011986 | -0.0033587 | 0.060824 | 0.024021 | 0.054097 | -61.2715 | 0.038035 | -61.2109 | 60.235 | 59.9568 | 60.0255 | -61.2283 | -61.1888 | 0.082776 | -61.292 | 60.0491 | 60.172 | 60.1843 | -61.3509 | 0.07538 | -0.047862 | 0.032194 | 0.092847 | 0.017467 | -0.3261 | -0.25739 | -0.047172 | -0.23384 | 0.11488 | 0.011694 | 0.058866 | -0.11093 | -0.098574 | 121.5387 | 121.2605 | 121.3292 | 61.3417 | -121.5112 | 121.3528 | 121.4757 | 121.488 | 61.3865 | -121.6338
112.9844 | 121.8384 | -61.2305 | 60.3882 | -0.0025182 | -0.018487 | 0.008669 | 0.058786 | -0.0071642 | 0.053676 | -0.021518 | -0.0014122 | -0.0029313 | 0.061037 | 0.024021 | 0.054311 | -61.2807 | 0.038035 | -61.2063 | 60.2396 | 59.9568 | 60.0164 | -61.2238 | -61.1934 | 0.06904 | -61.2829 | 60.0307 | 60.1628 | 60.1477 | -61.3463 | 0.006717 | -0.14857 | -0.050205 | 0.024184 | 0.017467 | -0.43139 | -0.37183 | -0.11584 | -0.35744 | 0.037059 | -0.05239 | 0.063445 | -0.22538 | -0.24049 | 121.4701 | 121.1873 | 121.2468 | 61.2685 | -121.6119 | 121.2612 | 121.3933 | 121.3782 | 61.2995 | -121.7345
114.7188 | 121.843 | -61.2625 | 60.3836 | -0.0025182 | -0.018701 | 0.0088826 | 0.058786 | -0.0067368 | 0.053249 | 0.0013733 | -0.0016258 | -0.0033587 | 0.060824 | 0.024021 | 0.053883 | -61.2761 | 0.047193 | -61.2017 | 60.235 | 59.9568 | 60.0209 | -61.2238 | -61.1934 | 0.073618 | -61.292 | 60.0399 | 60.172 | 60.1752 | -61.3463 | 0.03876 | -0.14857 | -0.013584 | 0.060805 | 0.022045 | -0.42681 | -0.36268 | -0.083792 | -0.3437 | 0.069102 | -0.029505 | 0.054287 | -0.21164 | -0.20844 | 121.4975 | 121.2193 | 121.2834 | 61.3097 | -121.6074 | 121.3024 | 121.4345 | 121.4377 | 61.3361 | -121.7299
116.4531 | 121.8201 | -61.2671 | 60.3241 | -0.010149 | -0.018487 | 0.008669 | 0.059 | -0.0067368 | 0.053676 | -0.021518 | -0.0018394 | -0.0031451 | 0.060824 | 0.024235 | 0.053883 | -61.2807 | 0.038035 | -61.2154 | 60.2259 | 59.9705 | 60.0255 | -61.2238 | -61.1843 | 0.078197 | -61.2874 | 60.0353 | 60.1765 | 60.1477 | -61.3463 | 0.043338 | -0.098218 | -0.013584 | 0.051648 | 0.00831 | -0.35356 | -0.29859 | -0.079214 | -0.28877 | 0.082838 | -0.020348 | 0.058866 | -0.14755 | -0.1764 | 121.493 | 121.2376 | 121.2926 | 61.3051 | -121.5478 | 121.3024 | 121.4436 | 121.4148 | 61.3453 | -121.6704
118.2031 | 121.9208 | -61.2579 | 60.2737 | -0.010149 | -0.018487 | 0.008669 | 0.059214 | -0.0069506 | 0.053676 | -0.013887 | -0.0014122 | -0.0031451 | 0.060824 | 0.024235 | 0.054311 | -61.2761 | 0.038035 | -61.2017 | 60.2396 | 59.9568 | 60.0301 | -61.2283 | -61.1934 | 0.073618 | -61.2874 | 60.0445 | 60.1765 | 60.1614 | -61.3417 | 0.029604 | -0.034128 | -0.018161 | 0.056228 | 0.026624 | -0.31695 | -0.24366 | -0.08379 | -0.22926 | 0.064525 | -0.029503 | 0.054287 | -0.097199 | -0.11231 | 121.4976 | 121.2147 | 121.288 | 61.296 | -121.5021 | 121.3024 | 121.4345 | 121.4194 | 61.3316 | -121.6155
119.8906 | 121.7972 | -61.2122 | 60.4065 | -0.0025182 | -0.018487 | 0.0088826 | 0.059 | -0.0067368 | 0.053676 | -0.0062567 | -0.0016258 | -0.0035723 | 0.06061 | 0.024021 | 0.054311 | -61.2807 | 0.038035 | -61.2063 | 60.2305 | 59.966 | 60.0209 | -61.2238 | -61.198 | 0.06904 | -61.292 | 60.0307 | 60.172 | 60.1797 | -61.3509 | -0.011594 | -0.17604 | -0.068516 | 0.005873 | 0.017467 | -0.44054 | -0.38556 | -0.13873 | -0.37575 | 0.01417 | -0.079859 | 0.058866 | -0.23453 | -0.22675 | 121.4426 | 121.1781 | 121.2331 | 61.2502 | -121.6302 | 121.2429 | 121.3841 | 121.3919 | 61.2812 | -121.7574
121.6406 | 121.8796 | -61.2167 | 60.3561 | -0.025411 | -0.018914 | 0.0084552 | 0.059214 | -0.0071642 | 0.053676 | -0.013887 | -0.0014122 | -0.0033587 | 0.06061 | 0.024235 | 0.053883 | -61.2807 | 0.033457 | -61.2109 | 60.2259 | 59.9614 | 60.0164 | -61.2238 | -61.1888 | 0.073618 | -61.2966 | 60.0353 | 60.1674 | 60.1752 | -61.3463 | -0.007016 | -0.13026 | -0.063938 | 0.005872 | 0.012888 | -0.39476 | -0.33979 | -0.12957 | -0.32082 | 0.027905 | -0.079859 | 0.049709 | -0.18875 | -0.18097 | 121.4426 | 121.1781 | 121.2331 | 61.2502 | -121.5799 | 121.2521 | 121.3841 | 121.3919 | 61.2904 | -121.7024
123.3906 | 121.9025 | -61.203 | 60.3653 | -0.01778 | -0.018701 | 0.008669 | 0.058786 | -0.0067368 | 0.05389 | -0.013887 | -0.0016258 | -0.0033587 | 0.06061 | 0.024662 | 0.053883 | -61.2761 | 0.042614 | -61.2109 | 60.235 | 59.9568 | 60.0255 | -61.2192 | -61.198 | 0.078197 | -61.3012 | 60.0399 | 60.1765 | 60.1523 | -61.3463 | -0.01617 | -0.13026 | -0.073093 | -0.007861 | 0.008309 | -0.4085 | -0.33979 | -0.1433 | -0.32539 | 0.005015 | -0.098171 | 0.04513 | -0.18875 | -0.21302 | 121.438 | 121.1598 | 121.2285 | 61.2456 | -121.5845 | 121.2429 | 121.3795 | 121.3553 | 61.2812 | -121.7116
125.0781 | 121.8796 | -61.2167 | 60.3424 | -0.0025182 | -0.018487 | 0.008669 | 0.058573 | -0.0071642 | 0.053249 | -0.013887 | -0.0018394 | -0.0035723 | 0.06061 | 0.024235 | 0.054524 | -61.2761 | 0.038035 | -61.2063 | 60.235 | 59.966 | 60.0255 | -61.2238 | -61.1888 | 0.078197 | -61.2966 | 60.0399 | 60.172 | 60.1752 | -61.3509 | -0.007016 | -0.10737 | -0.05936 | 0.010451 | 0.017467 | -0.37645 | -0.3169 | -0.13415 | -0.3025 | 0.027905 | -0.079859 | 0.054288 | -0.17044 | -0.16724 | 121.4518 | 121.1827 | 121.2422 | 61.2548 | -121.5662 | 121.2566 | 121.3887 | 121.3919 | 61.2949 | -121.6933
126.8125 | 121.8887 | -61.1847 | 60.4111 | -0.0025182 | -0.018914 | 0.0084552 | 0.058786 | -0.0067368 | 0.05389 | -0.021518 | -0.0016258 | -0.0031451 | 0.060824 | 0.024448 | 0.053883 | -61.2853 | 0.033457 | -61.2063 | 60.235 | 59.9614 | 60.0209 | -61.2146 | -61.1934 | 0.073618 | -61.2874 | 60.0307 | 60.1674 | 60.1431 | -61.3417 | -0.029903 | -0.17604 | -0.10056 | -0.021593 | 0.00831 | -0.4497 | -0.39014 | -0.15703 | -0.38033 | -0.008718 | -0.10275 | 0.054287 | -0.24369 | -0.26796 | 121.4197 | 121.1461 | 121.2056 | 61.2181 | -121.6257 | 121.2154 | 121.3521 | 121.3278 | 61.2583 | -121.7528
128.5625 | 121.8201 | -61.2808 | 60.3333 | -0.0025182 | -0.018914 | 0.0084552 | 0.058573 | -0.0071642 | 0.053676 | -0.021518 | -0.002053 | -0.0029313 | 0.061037 | 0.024235 | 0.053883 | -61.2761 | 0.038035 | -61.2063 | 60.2305 | 59.9705 | 60.0255 | -61.2192 | -61.1888 | 0.06904 | -61.2966 | 60.0353 | 60.1811 | 60.1569 | -61.3509 | 0.06165 | -0.10279 | 0.004727 | 0.074538 | 0.012888 | -0.36272 | -0.30774 | -0.07006 | -0.29793 | 0.091992 | -0.015772 | 0.054288 | -0.15213 | -0.1764 | 121.5113 | 121.2514 | 121.3063 | 61.3189 | -121.5524 | 121.3161 | 121.4619 | 121.4377 | 61.3499 | -121.6841
130.3125 | 121.8887 | -61.2305 | 60.2921 | -0.010149 | -0.018701 | 0.0084552 | 0.058786 | -0.0067368 | 0.053676 | -0.021518 | -0.0016258 | -0.0029313 | 0.06061 | 0.024662 | 0.054311 | -61.2853 | 0.042614 | -61.2154 | 60.235 | 59.9614 | 60.0209 | -61.2238 | -61.1934 | 0.073618 | -61.292 | 60.0399 | 60.1765 | 60.1294 | -61.3509 | 0.006717 | -0.057017 | -0.054783 | 0.015027 | 0.00831 | -0.33068 | -0.27112 | -0.12041 | -0.25215 | 0.037059 | -0.061548 | 0.058866 | -0.11551 | -0.16267 | 121.4655 | 121.1918 | 121.2514 | 61.2731 | -121.5158 | 121.2704 | 121.407 | 121.3598 | 61.3041 | -121.6429
131.9844 | 121.875 | -61.1893 | 60.4156 | -0.010149 | -0.018487 | 0.0084552 | 0.058786 | -0.0071642 | 0.05389 | -0.013887 | -0.0011986 | -0.0031451 | 0.060396 | 0.024235 | 0.054311 | -61.2807 | 0.028878 | -61.2109 | 60.2305 | 59.9614 | 60.0164 | -61.2192 | -61.198 | 0.073618 | -61.292 | 60.0353 | 60.1765 | 60.0836 | -61.3509 | -0.029903 | -0.18519 | -0.091404 | -0.021594 | 0.008309 | -0.45427 | -0.3993 | -0.16161 | -0.38032 | -0.008718 | -0.10275 | 0.058866 | -0.23911 | -0.33206 | 121.4197 | 121.1506 | 121.2056 | 61.2181 | -121.6348 | 121.2246 | 121.3658 | 121.2729 | 61.2629 | -121.7665
133.7188 | 121.8292 | -61.2396 | 60.3699 | -0.0025182 | -0.019128 | 0.008669 | 0.058573 | -0.0069506 | 0.053676 | -0.013887 | -0.0018394 | -0.0033587 | 0.060396 | 0.024235 | 0.054097 | -61.2761 | 0.033457 | -61.2063 | 60.2259 | 59.966 | 60.0209 | -61.2146 | -61.1934 | 0.073618 | -61.292 | 60.0445 | 60.1765 | 60.1797 | -61.3555 | 0.025029 | -0.14399 | -0.036472 | 0.033339 | 0.00831 | -0.40392 | -0.34894 | -0.11584 | -0.32539 | 0.046214 | -0.052393 | 0.063445 | -0.19333 | -0.19013 | 121.4655 | 121.2056 | 121.2606 | 61.2731 | -121.5845 | 121.2841 | 121.4162 | 121.4194 | 61.3132 | -121.7253
135.3906 | 121.9345 | -61.2579 | 60.2692 | 0.0051128 | -0.018914 | 0.0084552 | 0.058786 | -0.0071642 | 0.05389 | -0.013887 | -0.0016258 | -0.0029313 | 0.060824 | 0.024235 | 0.054311 | -61.2807 | 0.042614 | -61.2109 | 60.235 | 59.9568 | 60.0209 | -61.2192 | -61.2026 | 0.078197 | -61.292 | 60.0399 | 60.1674 | 60.1477 | -61.3463 | 0.038762 | -0.034129 | -0.022739 | 0.047071 | 0.008309 | -0.31237 | -0.24824 | -0.088369 | -0.22926 | 0.055368 | -0.034082 | 0.054287 | -0.10178 | -0.12147 | 121.493 | 121.2147 | 121.2789 | 61.3005 | -121.4883 | 121.2978 | 121.4253 | 121.4056 | 61.3361 | -121.6155
137.1406 | 121.9208 | -61.2442 | 60.3149 | -0.010149 | -0.019128 | 0.008669 | 0.058786 | -0.0069506 | 0.053463 | -0.013887 | -0.0014122 | -0.0033587 | 0.06061 | 0.024448 | 0.054097 | -61.2761 | 0.038035 | -61.2109 | 60.2396 | 59.9614 | 60.0164 | -61.2192 | -61.1934 | 0.06904 | -61.2966 | 60.0399 | 60.1811 | 60.1385 | -61.3463 | 0.025029 | -0.075326 | -0.031894 | 0.033338 | 0.008309 | -0.35356 | -0.29859 | -0.1021 | -0.27504 | 0.050792 | -0.052393 | 0.049709 | -0.13382 | -0.1764 | 121.4838 | 121.2056 | 121.2606 | 61.2822 | -121.5341 | 121.2841 | 121.4253 | 121.3827 | 61.3132 | -121.6612
138.8281 | 121.8155 | -61.2762 | 60.3882 | -0.0025182 | -0.019128 | 0.0088826 | 0.059 | -0.0071642 | 0.05389 | -0.013887 | -0.0016258 | -0.0029313 | 0.06061 | 0.024448 | 0.054097 | -61.2807 | 0.033457 | -61.2154 | 60.235 | 59.966 | 60.0118 | -61.2192 | -61.2026 | 0.078197 | -61.292 | 60.0399 | 60.172 | 60.1843 | -61.3463 | 0.057072 | -0.15315 | -0.004429 | 0.060803 | 0.003731 | -0.42223 | -0.37641 | -0.070059 | -0.34828 | 0.073678 | -0.015772 | 0.054287 | -0.21622 | -0.20386 | 121.5113 | 121.2422 | 121.288 | 61.3097 | -121.6074 | 121.3161 | 121.4482 | 121.4606 | 61.3544 | -121.7345
140.5938 | 121.9254 | -61.1847 | 60.3607 | -0.0025182 | -0.018914 | 0.0088826 | 0.058786 | -0.0067368 | 0.053249 | -0.013887 | -0.0016258 | -0.0033587 | 0.06061 | 0.024662 | 0.054097 | -61.2761 | 0.038035 | -61.2063 | 60.2305 | 59.9614 | 60.0209 | -61.2238 | -61.198 | 0.073618 | -61.292 | 60.0399 | 60.1765 | 60.1797 | -61.3463 | -0.03906 | -0.13026 | -0.091404 | -0.021593 | 0.017467 | -0.39934 | -0.33979 | -0.16161 | -0.32081 | -0.013296 | -0.10733 | 0.054287 | -0.18417 | -0.18097 | 121.4151 | 121.1461 | 121.2056 | 61.2227 | -121.5845 | 121.2246 | 121.3612 | 121.3644 | 61.2583 | -121.707
142.3281 | 121.8887 | -61.2488 | 60.347 | -0.010149 | -0.018701 | 0.0084552 | 0.059 | -0.0067368 | 0.053463 | -0.029148 | -0.0014122 | -0.0031451 | 0.060824 | 0.024662 | 0.053883 | -61.2853 | 0.033457 | -61.2109 | 60.2305 | 59.9568 | 60.0164 | -61.2146 | -61.198 | 0.06904 | -61.2874 | 60.0445 | 60.1674 | 60.1889 | -61.3463 | 0.034184 | -0.11653 | -0.036473 | 0.037915 | 0.003731 | -0.39019 | -0.33063 | -0.097525 | -0.3025 | 0.050791 | -0.038659 | 0.058866 | -0.1796 | -0.15808 | 121.4792 | 121.2056 | 121.2651 | 61.2822 | -121.5616 | 121.2933 | 121.4162 | 121.4377 | 61.3178 | -121.6933
144.0156 | 121.9208 | -61.1938 | 60.3928 | 0.0051128 | -0.018701 | 0.0090964 | 0.058786 | -0.0067368 | 0.053463 | -0.021518 | -0.0018394 | -0.0035723 | 0.060396 | 0.024448 | 0.054311 | -61.2853 | 0.042614 | -61.2017 | 60.2305 | 59.966 | 60.0164 | -61.2192 | -61.1934 | 0.06904 | -61.2966 | 60.0445 | 60.172 | 60.1843 | -61.3509 | -0.025325 | -0.1623 | -0.091404 | -0.007859 | 0.017466 | -0.42681 | -0.37641 | -0.15704 | -0.34828 | 0.000438 | -0.10275 | 0.054288 | -0.2208 | -0.20844 | 121.4243 | 121.1598 | 121.2102 | 61.2365 | -121.6119 | 121.2383 | 121.3658 | 121.3782 | 61.2629 | -121.7436
145.7656 | 121.8933 | -61.2213 | 60.3287 | -0.010149 | -0.018701 | 0.0090964 | 0.058786 | -0.0069506 | 0.053463 | -0.0062567 | -0.0016258 | -0.0031451 | 0.060824 | 0.024448 | 0.054097 | -61.2807 | 0.038035 | -61.2063 | 60.2259 | 59.9568 | 60.0255 | -61.2192 | -61.1934 | 0.073618 | -61.2874 | 60.0353 | 60.1765 | 60.1706 | -61.36 | 0.00214 | -0.1028 | -0.059361 | 0.015028 | 0.012888 | -0.37188 | -0.30317 | -0.13873 | -0.29335 | 0.027903 | -0.066125 | 0.072603 | -0.15213 | -0.15809 | 121.4472 | 121.1781 | 121.2468 | 61.2593 | -121.5478 | 121.2566 | 121.3979 | 121.3919 | 61.2949 | -121.6887
147.4375 | 121.9345 | -61.1847 | 60.3195 | -0.0025182 | -0.018701 | 0.0084552 | 0.058786 | -0.0071642 | 0.053676 | -0.013887 | -0.0018394 | -0.0033587 | 0.06061 | 0.024662 | 0.05367 | -61.2807 | 0.042614 | -61.2109 | 60.2259 | 59.9614 | 60.0301 | -61.2238 | -61.1934 | 0.073618 | -61.2966 | 60.0445 | 60.172 | 60.1202 | -61.3463 | -0.03906 | -0.09364 | -0.095982 | -0.026172 | 0.012888 | -0.35814 | -0.28943 | -0.16161 | -0.27504 | -0.008718 | -0.1119 | 0.049709 | -0.14755 | -0.1993 | 121.4106 | 121.1461 | 121.2148 | 61.2273 | -121.5433 | 121.2292 | 121.3567 | 121.3049 | 61.2583 | -121.6658
149.1719 | 121.8704 | -61.2259 | 60.3287 | -0.010149 | -0.019128 | 0.008669 | 0.058573 | -0.0069506 | 0.053676 | -0.021518 | -0.0014122 | -0.0035723 | 0.06061 | 0.024662 | 0.054097 | -61.2807 | 0.042614 | -61.2017 | 60.2305 | 59.966 | 60.0255 | -61.2238 | -61.198 | 0.073618 | -61.2966 | 60.0399 | 60.1857 | 60.166 | -61.3509 | 0.002139 | -0.098216 | -0.054783 | 0.024184 | 0.022045 | -0.36272 | -0.30317 | -0.12499 | -0.28877 | 0.027903 | -0.070704 | 0.054288 | -0.14297 | -0.16266 | 121.4563 | 121.1918 | 121.2514 | 61.2685 | -121.5524 | 121.2658 | 121.4116 | 121.3919 | 61.2995 | -121.6796
150.9375 | 121.7926 | -61.3266 | 60.3241 | -0.010149 | -0.018914 | 0.008669 | 0.058786 | -0.0071642 | 0.053463 | -0.013887 | -0.0014122 | -0.0031451 | 0.060824 | 0.024876 | 0.05367 | -61.2761 | 0.042614 | -61.2063 | 60.235 | 59.9705 | 60.0209 | -61.2238 | -61.1934 | 0.073618 | -61.2874 | 60.0353 | 60.172 | 60.1614 | -61.3509 | 0.10285 | -0.089061 | 0.050503 | 0.12031 | 0.017467 | -0.35356 | -0.30317 | -0.024284 | -0.28877 | 0.13319 | 0.039161 | 0.063445 | -0.15213 | -0.16267 | 121.5616 | 121.2971 | 121.3475 | 61.3692 | -121.5478 | 121.3619 | 121.4986 | 121.488 | 61.4002 | -121.675
152.6875 | 121.8155 | -61.2854 | 60.3058 | 0.020375 | -0.018914 | 0.0082416 | 0.058786 | -0.0073778 | 0.053463 | -0.0062567 | -0.0018394 | -0.0033587 | 0.060824 | 0.024448 | 0.054311 | -61.2853 | 0.042614 | -61.2017 | 60.2305 | 59.9705 | 60.0209 | -61.2238 | -61.198 | 0.078197 | -61.2874 | 60.0491 | 60.1765 | 60.1706 | -61.3463 | 0.061648 | -0.075328 | 0.000148 | 0.083693 | 0.022045 | -0.33525 | -0.28486 | -0.060904 | -0.25673 | 0.087412 | -0.002038 | 0.058866 | -0.12924 | -0.1352 | 121.5159 | 121.2559 | 121.3063 | 61.328 | -121.5295 | 121.3345 | 121.4619 | 121.456 | 61.3636 | -121.6521
154.4219 | 121.7926 | -61.3037 | 60.3012 | 0.0051128 | -0.018914 | 0.0088826 | 0.058786 | -0.0071642 | 0.053676 | -0.021518 | -0.0016258 | -0.0031451 | 0.060396 | 0.024448 | 0.054097 | -61.2761 | 0.038035 | -61.2063 | 60.2396 | 59.966 | 60.0209 | -61.2329 | -61.1934 | 0.073618 | -61.2966 | 60.0399 | 60.1765 | 60.1614 | -61.3417 | 0.070801 | -0.061593 | 0.027615 | 0.097426 | 0.026625 | -0.33525 | -0.28028 | -0.038014 | -0.26131 | 0.1103 | 0.007116 | 0.04513 | -0.12466 | -0.13978 | 121.5433 | 121.2697 | 121.3246 | 61.3417 | -121.5341 | 121.3436 | 121.4803 | 121.4651 | 61.3773 | -121.6429
156.125 | 121.9025 | -61.203 | 60.3607 | -0.010149 | -0.019128 | 0.0088826 | 0.058359 | -0.0071642 | 0.053463 | -0.013887 | -0.0018394 | -0.0035723 | 0.06061 | 0.024876 | 0.054097 | -61.2807 | 0.038035 | -61.2063 | 60.235 | 59.9705 | 60.0164 | -61.2192 | -61.198 | 0.073618 | -61.2874 | 60.0445 | 60.172 | 60.1294 | -61.3555 | -0.01617 | -0.12568 | -0.077671 | -0.003282 | 0.012888 | -0.39018 | -0.34437 | -0.15246 | -0.31624 | 0.005015 | -0.084435 | 0.068024 | -0.18875 | -0.23134 | 121.438 | 121.1735 | 121.2194 | 61.241 | -121.5799 | 121.2475 | 121.375 | 121.3324 | 61.2766 | -121.7162
157.8125 | 121.8796 | -61.2213 | 60.3241 | -0.0025182 | -0.019128 | 0.008669 | 0.058573 | -0.0071642 | 0.053463 | -0.013887 | -0.0016258 | -0.0031451 | 0.060824 | 0.025089 | 0.05367 | -61.2761 | 0.042614 | -61.2063 | 60.2305 | 59.9568 | 60.0255 | -61.2192 | -61.198 | 0.078197 | -61.292 | 60.0399 | 60.1811 | 60.1843 | -61.3463 | 0.00214 | -0.093639 | -0.054783 | 0.015028 | 0.012888 | -0.3673 | -0.29859 | -0.12499 | -0.28419 | 0.023325 | -0.070704 | 0.054287 | -0.14297 | -0.13977 | 121.4518 | 121.1781 | 121.2468 | 61.2639 | -121.5433 | 121.2612 | 121.4024 | 121.4056 | 61.2995 | -121.6704
159.5469 | 121.8063 | -61.235 | 60.3836 | -0.0025182 | -0.019128 | 0.008669 | 0.058786 | -0.0071642 | 0.053676 | -0.0062567 | -0.0016258 | -0.0033587 | 0.060396 | 0.024876 | 0.054311 | -61.2807 | 0.033457 | -61.1971 | 60.235 | 59.9614 | 60.0255 | -61.2283 | -61.1934 | 0.073618 | -61.2966 | 60.0445 | 60.1765 | 60.1752 | -61.3555 | 0.006715 | -0.14857 | -0.045628 | 0.037917 | 0.031202 | -0.42223 | -0.3581 | -0.12042 | -0.33913 | 0.041636 | -0.061549 | 0.058867 | -0.20706 | -0.20844 | 121.4701 | 121.1964 | 121.2606 | 61.2685 | -121.6119 | 121.2795 | 121.4116 | 121.4102 | 61.3087 | -121.7391
161.3125 | 121.907 | -61.203 | 60.379 | -0.010149 | -0.019342 | 0.0084552 | 0.058786 | -0.0071642 | 0.053035 | -0.029148 | -0.0016258 | -0.0035723 | 0.06061 | 0.024662 | 0.05367 | -61.2807 | 0.033457 | -61.2017 | 60.2305 | 59.9568 | 60.0209 | -61.2192 | -61.198 | 0.073618 | -61.2874 | 60.0353 | 60.1765 | 60.166 | -61.3555 | -0.01617 | -0.14857 | -0.077671 | 0.001296 | 0.017466 | -0.42223 | -0.3581 | -0.15246 | -0.3437 | 0.005015 | -0.084435 | 0.068024 | -0.20248 | -0.21302 | 121.4335 | 121.1598 | 121.2239 | 61.2365 | -121.5982 | 121.2383 | 121.3795 | 121.369 | 61.2766 | -121.7345
163 | 121.7743 | -61.3174 | 60.2875 | -0.010149 | -0.019128 | 0.0088826 | 0.058786 | -0.0071642 | 0.053249 | -0.013887 | -0.0018394 | -0.0033587 | 0.06061 | 0.024448 | 0.053883 | -61.2761 | 0.038035 | -61.2063 | 60.2305 | 59.9751 | 60.0301 | -61.2238 | -61.1888 | 0.073618 | -61.2874 | 60.0399 | 60.1674 | 60.1889 | -61.3509 | 0.093692 | -0.057018 | 0.041348 | 0.11116 | 0.017467 | -0.31236 | -0.25739 | -0.033439 | -0.24757 | 0.12861 | 0.030006 | 0.063445 | -0.12009 | -0.098574 | 121.5479 | 121.2926 | 121.3475 | 61.3555 | -121.5112 | 121.3573 | 121.4848 | 121.5063 | 61.3911 | -121.6384
164.75 | 121.9528 | -61.1755 | 60.3836 | -0.010149 | -0.019342 | 0.0088826 | 0.058786 | -0.0071642 | 0.053463 | -0.021518 | -0.0014122 | -0.0031451 | 0.060824 | 0.024662 | 0.053883 | -61.2715 | 0.042614 | -61.2063 | 60.235 | 59.9614 | 60.0164 | -61.2329 | -61.1934 | 0.078197 | -61.292 | 60.0491 | 60.1765 | 60.1797 | -61.36 | -0.057373 | -0.14857 | -0.09598 | -0.030748 | 0.026625 | -0.42223 | -0.36726 | -0.1845 | -0.33455 | -0.017873 | -0.11648 | 0.068024 | -0.20706 | -0.20386 | 121.4106 | 121.1369 | 121.1919 | 61.2182 | -121.6165 | 121.2246 | 121.3521 | 121.3553 | 61.2537 | -121.7436
166.4844 | 121.875 | -61.2305 | 60.3561 | 0.0051128 | -0.019342 | 0.008669 | 0.058786 | -0.0067368 | 0.053463 | -0.013887 | -0.0014122 | -0.0033587 | 0.06061 | 0.024448 | 0.053883 | -61.2761 | 0.038035 | -61.2063 | 60.235 | 59.966 | 60.0209 | -61.2283 | -61.1934 | 0.078197 | -61.292 | 60.0445 | 60.1765 | 60.1797 | -61.36 | 0.002138 | -0.1211 | -0.045627 | 0.024184 | 0.022046 | -0.39019 | -0.33521 | -0.12957 | -0.31166 | 0.037059 | -0.061548 | 0.068024 | -0.1796 | -0.1764 | 121.4655 | 121.1964 | 121.2514 | 61.2685 | -121.5845 | 121.2749 | 121.407 | 121.4102 | 61.3087 | -121.7162
168.2188 | 121.8933 | -61.235 | 60.3378 | -0.010149 | -0.018914 | 0.0088826 | 0.058359 | -0.0071642 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.060824 | 0.024448 | 0.054097 | -61.2807 | 0.038035 | -61.2017 | 60.235 | 59.9568 | 60.0255 | -61.2192 | -61.1934 | 0.073618 | -61.2874 | 60.0445 | 60.1674 | 60.1431 | -61.3509 | 0.015873 | -0.10279 | -0.045628 | 0.033339 | 0.017466 | -0.38103 | -0.31232 | -0.11584 | -0.29335 | 0.041636 | -0.052392 | 0.063445 | -0.17044 | -0.19471 | 121.4701 | 121.1918 | 121.2606 | 61.2731 | -121.557 | 121.2795 | 121.4024 | 121.3782 | 61.3087 | -121.6887
169.9062 | 121.7697 | -61.3174 | 60.3012 | -0.0025182 | -0.019128 | 0.0084552 | 0.058786 | -0.0075914 | 0.053249 | -0.0062567 | -0.0018394 | -0.0027177 | 0.060183 | 0.024662 | 0.053883 | -61.2761 | 0.033457 | -61.2017 | 60.2396 | 59.9705 | 60.0301 | -61.2283 | -61.198 | 0.078197 | -61.2966 | 60.0399 | 60.172 | 60.1523 | -61.3463 | 0.089113 | -0.061593 | 0.041348 | 0.11574 | 0.026624 | -0.33067 | -0.27112 | -0.02886 | -0.26131 | 0.11946 | 0.020849 | 0.049709 | -0.12924 | -0.14894 | 121.5571 | 121.288 | 121.3475 | 61.3509 | -121.5295 | 121.3573 | 121.4894 | 121.4697 | 61.3956 | -121.6475
171.6562 | 121.9208 | -61.2946 | 60.2417 | -0.025411 | -0.019128 | 0.0088826 | 0.058573 | -0.0069506 | 0.053463 | -0.013887 | -0.0018394 | -0.0033587 | 0.06061 | 0.024662 | 0.054097 | -61.2761 | 0.042614 | -61.2109 | 60.235 | 59.9568 | 60.0209 | -61.2146 | -61.198 | 0.073618 | -61.2966 | 60.0399 | 60.172 | 60.1294 | -61.3555 | 0.079961 | -0.006663 | 0.01846 | 0.083692 | 0.003731 | -0.2849 | -0.22077 | -0.060906 | -0.2018 | 0.096568 | -0.002039 | 0.058867 | -0.069734 | -0.11232 | 121.5296 | 121.2514 | 121.3155 | 61.3372 | -121.4563 | 121.3345 | 121.4665 | 121.4239 | 61.3682 | -121.5972
173.4062 | 121.8796 | -61.2259 | 60.3516 | -0.01778 | -0.019555 | 0.0082416 | 0.058359 | -0.0071642 | 0.053463 | -0.013887 | -0.0016258 | -0.0031451 | 0.060824 | 0.024662 | 0.053883 | -61.2807 | 0.038035 | -61.2063 | 60.235 | 59.966 | 60.0301 | -61.2238 | -61.1934 | 0.078197 | -61.292 | 60.0399 | 60.1765 | 60.1614 | -61.36 | 0.002139 | -0.11653 | -0.054783 | 0.019606 | 0.017467 | -0.38561 | -0.32147 | -0.13415 | -0.31166 | 0.032481 | -0.066126 | 0.068024 | -0.17502 | -0.19013 | 121.4609 | 121.1918 | 121.256 | 61.2639 | -121.5753 | 121.2658 | 121.4024 | 121.3873 | 61.3041 | -121.7116
175.1562 | 121.8658 | -61.2122 | 60.4019 | -0.010149 | -0.019128 | 0.0088826 | 0.058573 | -0.0071642 | 0.053463 | -0.021518 | -0.0014122 | -0.0027177 | 0.06061 | 0.024662 | 0.054311 | -61.2853 | 0.042614 | -61.2063 | 60.2305 | 59.966 | 60.0255 | -61.2283 | -61.1934 | 0.082776 | -61.3058 | 60.0399 | 60.1765 | 60.1706 | -61.36 | -0.016173 | -0.17146 | -0.073094 | 0.005873 | 0.022046 | -0.43596 | -0.37641 | -0.14788 | -0.36201 | 0.018748 | -0.093595 | 0.054288 | -0.22537 | -0.23133 | 121.4426 | 121.1781 | 121.2377 | 61.2548 | -121.6302 | 121.2521 | 121.3887 | 121.3827 | 61.2949 | -121.762
176.8281 | 121.9208 | -61.2442 | 60.3012 | -0.0025182 | -0.019769 | 0.008669 | 0.058573 | -0.0071642 | 0.053676 | -0.029148 | -0.002053 | -0.0031451 | 0.060824 | 0.025089 | 0.054311 | -61.2761 | 0.042614 | -61.1926 | 60.2396 | 59.9705 | 60.0209 | -61.2192 | -61.1888 | 0.078197 | -61.3012 | 60.0445 | 60.1765 | 60.166 | -61.3555 | 0.025029 | -0.061593 | -0.031894 | 0.051651 | 0.026622 | -0.33067 | -0.28028 | -0.11126 | -0.25673 | 0.055371 | -0.056972 | 0.054288 | -0.12466 | -0.1352 | 121.4838 | 121.2147 | 121.2651 | 61.2868 | -121.5204 | 121.2887 | 121.4207 | 121.4102 | 61.3224 | -121.6567
178.5625 | 121.9116 | -61.2671 | 60.2829 | -0.010149 | -0.019342 | 0.0084552 | 0.058786 | -0.0071642 | 0.053463 | -0.013887 | -0.0018394 | -0.0031451 | 0.060824 | 0.024876 | 0.054311 | -61.2715 | 0.042614 | -61.2063 | 60.235 | 59.9705 | 60.0209 | -61.2238 | -61.2026 | 0.078197 | -61.292 | 60.0445 | 60.1811 | 60.1569 | -61.36 | 0.043338 | -0.047862 | -0.004427 | 0.060805 | 0.017467 | -0.31236 | -0.26197 | -0.092951 | -0.23842 | 0.064523 | -0.024927 | 0.068024 | -0.10178 | -0.12605 | 121.5021 | 121.2376 | 121.288 | 61.3097 | -121.5067 | 121.3116 | 121.4482 | 121.4239 | 61.3453 | -121.6429
180.2344 | 121.9162 | -61.1847 | 60.3745 | -0.010149 | -0.019769 | 0.0084552 | 0.058359 | -0.0071642 | 0.05389 | -0.021518 | -0.0016258 | -0.0033587 | 0.060824 | 0.024448 | 0.054097 | -61.2807 | 0.033457 | -61.2154 | 60.235 | 59.966 | 60.0209 | -61.2238 | -61.1934 | 0.073618 | -61.2874 | 60.0445 | 60.172 | 60.1569 | -61.3646 | -0.03906 | -0.13941 | -0.095982 | -0.03075 | 0.00831 | -0.4085 | -0.35352 | -0.17993 | -0.32997 | -0.008718 | -0.10275 | 0.077181 | -0.20249 | -0.2176 | 121.4197 | 121.1506 | 121.2056 | 61.2181 | -121.5982 | 121.2292 | 121.3567 | 121.3415 | 61.2583 | -121.7391
181.9844 | 121.8384 | -61.2854 | 60.3653 | 0.0051128 | -0.019342 | 0.0088826 | 0.058359 | -0.0071642 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.060824 | 0.025089 | 0.053883 | -61.2761 | 0.042614 | -61.2063 | 60.2305 | 59.966 | 60.0301 | -61.2238 | -61.1934 | 0.078197 | -61.2966 | 60.0353 | 60.1811 | 60.1843 | -61.36 | 0.061648 | -0.13484 | 0.009304 | 0.079115 | 0.017467 | -0.39934 | -0.33521 | -0.074641 | -0.32997 | 0.09199 | -0.011195 | 0.063446 | -0.18417 | -0.18097 | 121.5159 | 121.2514 | 121.3155 | 61.328 | -121.589 | 121.3207 | 121.4665 | 121.4697 | 61.3636 | -121.7253
183.7188 | 121.9482 | -61.1893 | 60.3516 | -0.010149 | -0.019555 | 0.0090964 | 0.058786 | -0.0071642 | 0.053463 | -0.013887 | -0.002053 | -0.0031451 | 0.06061 | 0.025089 | 0.053883 | -61.2807 | 0.042614 | -61.2063 | 60.235 | 59.9614 | 60.0255 | -61.2192 | -61.1934 | 0.06904 | -61.2966 | 60.0399 | 60.1811 | 60.1569 | -61.36 | -0.029903 | -0.11653 | -0.091404 | -0.017015 | 0.012888 | -0.39019 | -0.32605 | -0.17077 | -0.31166 | -0.00414 | -0.10733 | 0.063446 | -0.17044 | -0.19471 | 121.4243 | 121.1506 | 121.2148 | 61.2319 | -121.5707 | 121.2292 | 121.3704 | 121.3461 | 61.2583 | -121.7116
185.4531 | 121.788 | -61.2305 | 60.4477 | -0.010149 | -0.019342 | 0.0084552 | 0.058359 | -0.0071642 | 0.053463 | -0.0062567 | -0.0014122 | -0.0029313 | 0.061037 | 0.025089 | 0.053883 | -61.2807 | 0.033457 | -61.2017 | 60.2259 | 59.9705 | 60.0255 | -61.2192 | -61.1934 | 0.06904 | -61.292 | 60.0399 | 60.1811 | 60.1156 | -61.36 | 0.011296 | -0.22181 | -0.050205 | 0.028762 | 0.017466 | -0.47716 | -0.42218 | -0.12957 | -0.40779 | 0.037059 | -0.061548 | 0.068024 | -0.26657 | -0.33205 | 121.4563 | 121.201 | 121.256 | 61.2639 | -121.6669 | 121.2704 | 121.4116 | 121.3461 | 61.2995 | -121.8077
187.1406 | 121.8796 | -61.2305 | 60.3195 | -0.0025182 | -0.019128 | 0.0084552 | 0.058786 | -0.0071642 | 0.053249 | -0.029148 | -0.002053 | -0.0031451 | 0.060824 | 0.024662 | 0.053883 | -61.2853 | 0.038035 | -61.2017 | 60.235 | 59.9614 | 60.0255 | -61.2283 | -61.1934 | 0.078197 | -61.292 | 60.0445 | 60.1811 | 60.1889 | -61.3692 | 0.002138 | -0.084483 | -0.054783 | 0.028762 | 0.026624 | -0.35814 | -0.29401 | -0.13873 | -0.27504 | 0.037059 | -0.061548 | 0.077181 | -0.1384 | -0.13062 | 121.4655 | 121.1918 | 121.256 | 61.2685 | -121.5478 | 121.2749 | 121.4116 | 121.4194 | 61.3087 | -121.6887
188.8906 | 121.8887 | -61.2305 | 60.3287 | -0.010149 | -0.019342 | 0.0088826 | 0.058573 | -0.0073778 | 0.053463 | -0.013887 | -0.0016258 | -0.0029313 | 0.06061 | 0.025303 | 0.054097 | -61.2761 | 0.042614 | -61.2017 | 60.2442 | 59.966 | 60.0255 | -61.2238 | -61.1888 | 0.078197 | -61.292 | 60.0399 | 60.1765 | 60.1752 | -61.36 | 0.006717 | -0.084481 | -0.045627 | 0.028762 | 0.022045 | -0.36272 | -0.30317 | -0.12957 | -0.28877 | 0.041638 | -0.061548 | 0.068024 | -0.15213 | -0.15351 | 121.4747 | 121.1964 | 121.256 | 61.2731 | -121.5524 | 121.2704 | 121.407 | 121.4056 | 61.3087 | -121.6887
190.5781 | 121.8109 | -61.2488 | 60.3973 | -0.0025182 | -0.019555 | 0.0084552 | 0.058573 | -0.0073778 | 0.053249 | 0.0013733 | -0.0016258 | -0.0031451 | 0.06061 | 0.024662 | 0.054311 | -61.2807 | 0.047193 | -61.2017 | 60.2396 | 59.9797 | 60.0301 | -61.2329 | -61.1934 | 0.073618 | -61.292 | 60.0445 | 60.1765 | 60.1889 | -61.3646 | 0.015869 | -0.15772 | -0.031895 | 0.047072 | 0.031203 | -0.41765 | -0.36725 | -0.11584 | -0.35286 | 0.055369 | -0.043238 | 0.072602 | -0.2208 | -0.20844 | 121.4884 | 121.2285 | 121.2789 | 61.296 | -121.6302 | 121.2933 | 121.4253 | 121.4377 | 61.3224 | -121.762
192.3281 | 121.8018 | -61.2259 | 60.4019 | -0.0025182 | -0.019555 | 0.0088826 | 0.058573 | -0.0069506 | 0.053676 | 0.0013733 | -0.0016258 | -0.0031451 | 0.060396 | 0.024876 | 0.053883 | -61.2807 | 0.038035 | -61.1971 | 60.2305 | 59.9705 | 60.0255 | -61.2238 | -61.1934 | 0.078197 | -61.3012 | 60.0491 | 60.1765 | 60.166 | -61.3646 | 0.002139 | -0.17146 | -0.054783 | 0.028762 | 0.026623 | -0.43138 | -0.37641 | -0.13873 | -0.35286 | 0.032481 | -0.075283 | 0.063445 | -0.22537 | -0.23591 | 121.4563 | 121.1964 | 121.2514 | 61.2639 | -121.6257 | 121.2749 | 121.4024 | 121.3919 | 61.3041 | -121.7665
194.0781 | 121.8979 | -61.2076 | 60.3653 | -0.0025182 | -0.019769 | 0.0090964 | 0.058359 | -0.0071642 | 0.053249 | -0.013887 | -0.0016258 | -0.0035723 | 0.06061 | 0.024876 | 0.053456 | -61.2761 | 0.033457 | -61.1971 | 60.2305 | 59.9614 | 60.0255 | -61.2238 | -61.198 | 0.06904 | -61.2966 | 60.0445 | 60.1765 | 60.1797 | -61.3646 | -0.016171 | -0.13484 | -0.068515 | 0.010452 | 0.026623 | -0.40392 | -0.33979 | -0.15704 | -0.32081 | 0.009593 | -0.089014 | 0.068024 | -0.18875 | -0.18555 | 121.438 | 121.169 | 121.2331 | 61.241 | -121.589 | 121.2521 | 121.3841 | 121.3873 | 61.2766 | -121.7299
195.8281 | 121.8063 | -61.2991 | 60.3287 | -0.010149 | -0.019769 | 0.008669 | 0.058359 | -0.0071642 | 0.053676 | -0.0062567 | -0.0018394 | -0.0031451 | 0.06061 | 0.025303 | 0.054097 | -61.2761 | 0.042614 | -61.2063 | 60.2396 | 59.9751 | 60.0209 | -61.2283 | -61.1934 | 0.073618 | -61.2966 | 60.0445 | 60.1811 | 60.1706 | -61.3738 | 0.070802 | -0.089059 | 0.023037 | 0.092848 | 0.022046 | -0.35356 | -0.30774 | -0.074644 | -0.28419 | 0.10572 | 0.002538 | 0.077182 | -0.14755 | -0.15809 | 121.5387 | 121.2742 | 121.3201 | 61.3417 | -121.557 | 121.3436 | 121.4803 | 121.4697 | 61.3728 | -121.7025
197.5625 | 121.875 | -61.2122 | 60.3195 | -0.010149 | -0.019769 | 0.0084552 | 0.058573 | -0.0075914 | 0.053249 | -0.036779 | -0.0018394 | -0.0029313 | 0.060396 | 0.024876 | 0.053883 | -61.2807 | 0.038035 | -61.2063 | 60.2305 | 59.966 | 60.0301 | -61.2238 | -61.1843 | 0.073618 | -61.2874 | 60.0445 | 60.172 | 60.1385 | -61.3646 | -0.011594 | -0.089061 | -0.068516 | 0.005873 | 0.017467 | -0.35356 | -0.28943 | -0.15246 | -0.27504 | 0.027906 | -0.07528 | 0.077181 | -0.14755 | -0.18098 | 121.4426 | 121.1781 | 121.2422 | 61.2502 | -121.5433 | 121.2566 | 121.3841 | 121.3507 | 61.2858 | -121.6841
199.2344 | 121.8292 | -61.2122 | 60.4065 | 0.0051128 | -0.019342 | 0.008669 | 0.058145 | -0.0073778 | 0.053463 | -0.013887 | -0.002053 | -0.0031451 | 0.060396 | 0.024448 | 0.053883 | -61.2807 | 0.042614 | -61.2017 | 60.2305 | 59.9705 | 60.0301 | -61.2192 | -61.2026 | 0.073618 | -61.292 | 60.0399 | 60.172 | 60.1843 | -61.3738 | -0.007015 | -0.17604 | -0.068516 | 0.010451 | 0.017466 | -0.43596 | -0.37641 | -0.16162 | -0.36659 | 0.009591 | -0.079859 | 0.08176 | -0.23453 | -0.22217 | 121.4426 | 121.1827 | 121.2422 | 61.2548 | -121.6257 | 121.2521 | 121.3841 | 121.3965 | 61.2858 | -121.7803
200.9844 | 121.8384 | -61.2625 | 60.3745 | 0.0051128 | -0.019983 | 0.008669 | 0.058573 | -0.0073778 | 0.053463 | -0.013887 | -0.002053 | -0.0035723 | 0.06061 | 0.025089 | 0.054097 | -61.2807 | 0.033457 | -61.2063 | 60.235 | 59.9751 | 60.0301 | -61.2283 | -61.1934 | 0.078197 | -61.292 | 60.0399 | 60.172 | 60.1843 | -61.3738 | 0.034181 | -0.13941 | -0.018162 | 0.056227 | 0.022046 | -0.39934 | -0.34436 | -0.11126 | -0.33455 | 0.069102 | -0.029505 | 0.08176 | -0.20249 | -0.19013 | 121.4975 | 121.2376 | 121.2926 | 61.296 | -121.6028 | 121.3024 | 121.4345 | 121.4468 | 61.3407 | -121.7482
202.7344 | 121.843 | -61.2671 | 60.347 | -0.0025182 | -0.019983 | 0.0088826 | 0.059 | -0.0071642 | 0.05389 | -0.029148 | -0.0018394 | -0.0029313 | 0.06061 | 0.024876 | 0.053883 | -61.2807 | 0.042614 | -61.2109 | 60.235 | 59.9705 | 60.0255 | -61.2283 | -61.1934 | 0.073618 | -61.292 | 60.0445 | 60.172 | 60.1569 | -61.3692 | 0.038759 | -0.11195 | -0.013584 | 0.056226 | 0.017467 | -0.37645 | -0.32148 | -0.10211 | -0.3025 | 0.07368 | -0.024927 | 0.077181 | -0.17502 | -0.19013 | 121.5021 | 121.2376 | 121.2926 | 61.3097 | -121.5753 | 121.3116 | 121.4391 | 121.4239 | 61.3407 | -121.7162
204.4219 | 121.9254 | -61.29 | 60.2509 | -0.0025182 | -0.019555 | 0.0090964 | 0.058573 | -0.0073778 | 0.053676 | -0.021518 | -0.0016258 | -0.0031451 | 0.06061 | 0.025303 | 0.053883 | -61.2761 | 0.042614 | -61.2063 | 60.2396 | 59.9705 | 60.0347 | -61.2238 | -61.1934 | 0.073618 | -61.2874 | 60.0307 | 60.1765 | 60.1935 | -61.3692 | 0.066226 | -0.011239 | 0.013882 | 0.083693 | 0.017467 | -0.28032 | -0.21619 | -0.07922 | -0.22011 | 0.096568 | 0.00254 | 0.08176 | -0.07431 | -0.057373 | 121.5296 | 121.2605 | 121.3246 | 61.3326 | -121.4746 | 121.3207 | 121.4665 | 121.4835 | 61.3636 | -121.6201
206.1875 | 121.8018 | -61.3037 | 60.3333 | -0.0025182 | -0.019769 | 0.0088826 | 0.058786 | -0.0078052 | 0.053676 | -0.013887 | -0.0014122 | -0.0027177 | 0.06061 | 0.025303 | 0.054097 | -61.2761 | 0.042614 | -61.2109 | 60.235 | 59.9705 | 60.0301 | -61.2283 | -61.1934 | 0.073618 | -61.2874 | 60.0491 | 60.1765 | 60.1843 | -61.3646 | 0.07538 | -0.098216 | 0.027615 | 0.092847 | 0.017467 | -0.36272 | -0.30316 | -0.060908 | -0.28419 | 0.1103 | 0.016273 | 0.077181 | -0.15671 | -0.14893 | 121.5387 | 121.2742 | 121.3338 | 61.3463 | -121.5616 | 121.3528 | 121.4803 | 121.488 | 61.3773 | -121.6979
207.9375 | 121.8109 | -61.3037 | 60.3104 | -0.01778 | -0.019769 | 0.0088826 | 0.058359 | -0.0071642 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.060396 | 0.024876 | 0.053883 | -61.2853 | 0.042614 | -61.2063 | 60.2396 | 59.9705 | 60.0347 | -61.2238 | -61.198 | 0.073618 | -61.292 | 60.0399 | 60.1765 | 60.1477 | -61.3646 | 0.079959 | -0.070749 | 0.018459 | 0.097426 | 0.017467 | -0.33983 | -0.2757 | -0.060908 | -0.27046 | 0.10572 | 0.011694 | 0.072602 | -0.13382 | -0.16267 | 121.5433 | 121.2742 | 121.3384 | 61.3463 | -121.5341 | 121.3436 | 121.4803 | 121.4514 | 61.3773 | -121.675
209.6719 | 121.8063 | -61.2305 | 60.4202 | -0.010149 | -0.019983 | 0.0088826 | 0.058359 | -0.0073778 | 0.053463 | 0.0013733 | -0.002053 | -0.0031451 | 0.06061 | 0.025089 | 0.05367 | -61.2853 | 0.038035 | -61.2063 | 60.235 | 59.9751 | 60.0347 | -61.2283 | -61.1888 | 0.082776 | -61.2874 | 60.0491 | 60.1765 | 60.166 | -61.3738 | 0.002138 | -0.18519 | -0.054783 | 0.024184 | 0.022046 | -0.44511 | -0.38556 | -0.14331 | -0.37117 | 0.041638 | -0.056969 | 0.086339 | -0.24368 | -0.25422 | 121.4655 | 121.2056 | 121.2651 | 61.2685 | -121.6486 | 121.2795 | 121.407 | 121.3965 | 61.3132 | -121.794
211.3594 | 121.9345 | -61.2625 | 60.2646 | -0.0025182 | -0.019342 | 0.0088826 | 0.058359 | -0.0075914 | 0.053676 | -0.013887 | -0.0016258 | -0.0031451 | 0.060396 | 0.025303 | 0.053456 | -61.2761 | 0.038035 | -61.2063 | 60.2396 | 59.9705 | 60.0301 | -61.2329 | -61.198 | 0.078197 | -61.292 | 60.0445 | 60.1765 | 60.166 | -61.3692 | 0.029602 | -0.024972 | -0.013584 | 0.056227 | 0.026625 | -0.29405 | -0.2345 | -0.10669 | -0.22011 | 0.064524 | -0.029505 | 0.077181 | -0.088043 | -0.098578 | 121.5021 | 121.233 | 121.2926 | 61.3005 | -121.4975 | 121.307 | 121.4391 | 121.4285 | 61.3407 | -121.6338
213.125 | 121.8201 | -61.3129 | 60.2966 | -0.010149 | -0.019983 | 0.0088826 | 0.058359 | -0.0075914 | 0.053463 | -0.021518 | -0.0018394 | -0.0031451 | 0.06061 | 0.025089 | 0.053883 | -61.2715 | 0.042614 | -61.2017 | 60.235 | 59.9751 | 60.0347 | -61.2283 | -61.1934 | 0.06904 | -61.3012 | 60.0399 | 60.1811 | 60.1889 | -61.3738 | 0.084535 | -0.061595 | 0.041349 | 0.11116 | 0.026624 | -0.32152 | -0.26196 | -0.060911 | -0.25673 | 0.11946 | 0.011692 | 0.072603 | -0.11551 | -0.10773 | 121.5479 | 121.288 | 121.3475 | 61.3555 | -121.525 | 121.3528 | 121.494 | 121.5018 | 61.3819 | -121.6704
214.8125 | 121.8887 | -61.2396 | 60.3333 | -0.0025182 | -0.019769 | 0.0090964 | 0.058573 | -0.0069506 | 0.053463 | -0.021518 | -0.0018394 | -0.0031451 | 0.060396 | 0.025303 | 0.053883 | -61.2761 | 0.033457 | -61.2063 | 60.2396 | 59.9751 | 60.0347 | -61.2238 | -61.1934 | 0.073618 | -61.3012 | 60.0445 | 60.1857 | 60.1752 | -61.3692 | 0.015872 | -0.093637 | -0.036472 | 0.033339 | 0.017467 | -0.35814 | -0.29859 | -0.12957 | -0.28877 | 0.046214 | -0.06155 | 0.068024 | -0.14755 | -0.15809 | 121.4792 | 121.2147 | 121.2743 | 61.2731 | -121.557 | 121.2841 | 121.4253 | 121.4148 | 61.3132 | -121.7024
216.5625 | 121.8155 | -61.2991 | 60.3241 | -0.0025182 | -0.019769 | 0.008669 | 0.058573 | -0.0073778 | 0.053463 | -0.013887 | -0.0018394 | -0.0031451 | 0.060396 | 0.025303 | 0.053883 | -61.2715 | 0.042614 | -61.2017 | 60.2396 | 59.9705 | 60.0347 | -61.2329 | -61.1934 | 0.078197 | -61.2874 | 60.0445 | 60.1857 | 60.1614 | -61.3738 | 0.066223 | -0.084482 | 0.027616 | 0.097426 | 0.031203 | -0.35356 | -0.28943 | -0.074644 | -0.27962 | 0.10572 | 0.011695 | 0.086339 | -0.1384 | -0.16267 | 121.5387 | 121.2697 | 121.3338 | 61.3417 | -121.557 | 121.3436 | 121.4848 | 121.4606 | 61.3773 | -121.6979
218.25 | 121.8201 | -61.1847 | 60.3973 | 0.0051128 | -0.019983 | 0.0088826 | 0.058573 | -0.0073778 | 0.053249 | -0.0062567 | -0.0018394 | -0.0033587 | 0.060824 | 0.025089 | 0.05367 | -61.2807 | 0.028878 | -61.2154 | 60.2396 | 59.9705 | 60.0347 | -61.2238 | -61.198 | 0.078197 | -61.292 | 60.0491 | 60.1811 | 60.1477 | -61.3692 | -0.03906 | -0.15772 | -0.095982 | -0.03075 | 0.00831 | -0.42681 | -0.36267 | -0.18451 | -0.34828 | -0.013296 | -0.10733 | 0.077181 | -0.21622 | -0.24964 | 121.4243 | 121.1552 | 121.2194 | 61.2136 | -121.6211 | 121.2338 | 121.3658 | 121.3324 | 61.2629 | -121.7665
219.9844 | 121.8933 | -61.2213 | 60.3699 | -0.010149 | -0.019769 | 0.0088826 | 0.058359 | -0.0073778 | 0.053676 | -0.021518 | -0.0014122 | -0.0031451 | 0.06061 | 0.025089 | 0.054097 | -61.2807 | 0.028878 | -61.2063 | 60.2305 | 59.9705 | 60.0255 | -61.2283 | -61.1934 | 0.06904 | -61.2874 | 60.0399 | 60.1857 | 60.1156 | -61.3738 | -0.007018 | -0.13941 | -0.059361 | 0.015028 | 0.022046 | -0.39934 | -0.34436 | -0.15246 | -0.32997 | 0.027903 | -0.066125 | 0.086339 | -0.18417 | -0.25423 | 121.4518 | 121.1918 | 121.2468 | 61.2502 | -121.5982 | 121.2612 | 121.407 | 121.337 | 61.2904 | -121.7437
221.7344 | 121.8979 | -61.1984 | 60.4202 | 0.0051128 | -0.019983 | 0.0088826 | 0.058786 | -0.0078052 | 0.053463 | -0.013887 | -0.0016258 | -0.0031451 | 0.060824 | 0.025089 | 0.053883 | -61.2761 | 0.028878 | -61.2063 | 60.235 | 59.9705 | 60.0347 | -61.2283 | -61.198 | 0.073618 | -61.2966 | 60.0445 | 60.1903 | 60.1752 | -61.3738 | -0.029906 | -0.18519 | -0.077671 | -0.00786 | 0.022046 | -0.44969 | -0.38556 | -0.17535 | -0.37575 | 0.000437 | -0.09817 | 0.077182 | -0.22995 | -0.24506 | 121.4335 | 121.169 | 121.2331 | 61.2273 | -121.6486 | 121.2429 | 121.3887 | 121.3736 | 61.272 | -121.794
223.4844 | 121.7834 | -61.3266 | 60.3104 | -0.0025182 | -0.019983 | 0.008669 | 0.058786 | -0.0071642 | 0.053249 | -0.013887 | -0.0018394 | -0.0029313 | 0.06061 | 0.025089 | 0.053883 | -61.2669 | 0.033457 | -61.2154 | 60.2396 | 59.9797 | 60.0301 | -61.2283 | -61.198 | 0.078197 | -61.292 | 60.0491 | 60.1857 | 60.1706 | -61.3738 | 0.098268 | -0.070749 | 0.05966 | 0.11116 | 0.012889 | -0.33067 | -0.28028 | -0.047178 | -0.26131 | 0.12861 | 0.034582 | 0.08176 | -0.12466 | -0.13978 | 121.5662 | 121.3063 | 121.3567 | 61.3601 | -121.5387 | 121.3757 | 121.5123 | 121.4972 | 61.4048 | -121.6841
225.2188 | 121.9345 | -61.2854 | 60.2737 | -0.010149 | -0.019983 | 0.008669 | 0.058573 | -0.0071642 | 0.053463 | -0.021518 | -0.0014122 | -0.0031451 | 0.06061 | 0.025089 | 0.054311 | -61.2761 | 0.038035 | -61.2017 | 60.235 | 59.966 | 60.0301 | -61.2329 | -61.1888 | 0.078197 | -61.3012 | 60.0399 | 60.1811 | 60.1614 | -61.3738 | 0.05249 | -0.038707 | 0.009304 | 0.083693 | 0.031203 | -0.30779 | -0.24366 | -0.088377 | -0.23384 | 0.096569 | -0.015774 | 0.072603 | -0.092621 | -0.11231 | 121.5204 | 121.2514 | 121.3155 | 61.3234 | -121.5067 | 121.3253 | 121.4665 | 121.4468 | 61.3636 | -121.6475
226.9062 | 121.9299 | -61.2625 | 60.2783 | -0.0025182 | -0.020196 | 0.0084552 | 0.059 | -0.0073778 | 0.053676 | -0.013887 | -0.0018394 | -0.0033587 | 0.060396 | 0.025303 | 0.053883 | -61.2761 | 0.038035 | -61.2017 | 60.2396 | 59.9614 | 60.0347 | -61.2283 | -61.198 | 0.06904 | -61.2966 | 60.0399 | 60.1765 | 60.1752 | -61.3692 | 0.034181 | -0.038705 | -0.013584 | 0.060805 | 0.026624 | -0.31694 | -0.24365 | -0.10669 | -0.23842 | 0.064524 | -0.034083 | 0.072603 | -0.10178 | -0.10315 | 121.5021 | 121.2239 | 121.2972 | 61.3005 | -121.5067 | 121.3024 | 121.4391 | 121.4377 | 61.3316 | -121.6475
228.6406 | 121.7926 | -61.2991 | 60.3424 | -0.01778 | -0.020196 | 0.0090964 | 0.058145 | -0.0073778 | 0.053463 | -0.013887 | -0.0018394 | -0.0029313 | 0.060396 | 0.02573 | 0.05367 | -61.2761 | 0.042614 | -61.2017 | 60.2442 | 59.9705 | 60.0347 | -61.2238 | -61.198 | 0.078197 | -61.2874 | 60.0445 | 60.1765 | 60.1797 | -61.3738 | 0.075381 | -0.098214 | 0.023037 | 0.097426 | 0.022045 | -0.37187 | -0.30774 | -0.074644 | -0.29793 | 0.10114 | 0.011695 | 0.086339 | -0.16586 | -0.16266 | 121.5433 | 121.2697 | 121.3338 | 61.3417 | -121.5662 | 121.3436 | 121.4757 | 121.4789 | 61.3773 | -121.7162
230.3125 | 121.8521 | -61.2579 | 60.3287 | 0.0051128 | -0.020196 | 0.0088826 | 0.058573 | -0.0075914 | 0.053463 | -0.0062567 | -0.0018394 | -0.0029313 | 0.060396 | 0.025089 | 0.053883 | -61.2761 | 0.033457 | -61.2063 | 60.2442 | 59.9705 | 60.0392 | -61.2283 | -61.1934 | 0.078197 | -61.292 | 60.0491 | 60.1857 | 60.166 | -61.3784 | 0.029604 | -0.084481 | -0.018161 | 0.05165 | 0.022046 | -0.35814 | -0.28943 | -0.12042 | -0.27961 | 0.064525 | -0.034082 | 0.086339 | -0.14297 | -0.16266 | 121.5021 | 121.2285 | 121.2972 | 61.2914 | -121.557 | 121.307 | 121.4436 | 121.4239 | 61.3361 | -121.707
232.0625 | 121.8887 | -61.203 | 60.4111 | -0.0025182 | -0.019983 | 0.0088826 | 0.058359 | -0.0071642 | 0.053463 | -0.021518 | -0.002053 | -0.0031451 | 0.060824 | 0.025517 | 0.053883 | -61.2761 | 0.038035 | -61.2109 | 60.2305 | 59.9705 | 60.0347 | -61.2329 | -61.2026 | 0.078197 | -61.3012 | 60.0491 | 60.1811 | 60.1752 | -61.3829 | -0.029907 | -0.18061 | -0.073093 | -0.007861 | 0.022046 | -0.44054 | -0.37641 | -0.17993 | -0.36201 | 0.000436 | -0.098171 | 0.081761 | -0.22995 | -0.23591 | 121.4335 | 121.1735 | 121.2377 | 61.241 | -121.644 | 121.2521 | 121.3841 | 121.3782 | 61.2812 | -121.794
233.7969 | 121.9208 | -61.1847 | 60.3836 | -0.010149 | -0.02041 | 0.0090964 | 0.058573 | -0.0073778 | 0.053249 | -0.021518 | -0.0018394 | -0.0031451 | 0.06061 | 0.025303 | 0.05367 | -61.2761 | 0.033457 | -61.2154 | 60.2396 | 59.9797 | 60.0301 | -61.2375 | -61.2026 | 0.06904 | -61.2966 | 60.0536 | 60.1765 | 60.1889 | -61.3738 | -0.052797 | -0.14399 | -0.091404 | -0.03075 | 0.022047 | -0.40391 | -0.35352 | -0.18908 | -0.32997 | -0.017875 | -0.1119 | 0.077182 | -0.20706 | -0.1947 | 121.4243 | 121.1644 | 121.2148 | 61.2181 | -121.6211 | 121.2383 | 121.3612 | 121.3736 | 61.2537 | -121.7574
235.4688 | 121.8887 | -61.2259 | 60.347 | -0.010149 | -0.019983 | 0.0090964 | 0.058786 | -0.0075914 | 0.05389 | -0.021518 | -0.002053 | -0.0031451 | 0.060183 | 0.025517 | 0.05367 | -61.2807 | 0.038035 | -61.2063 | 60.2396 | 59.9751 | 60.0347 | -61.2329 | -61.198 | 0.06904 | -61.2966 | 60.0445 | 60.1811 | 60.1797 | -61.3646 | -0.007019 | -0.10737 | -0.054783 | 0.019606 | 0.026625 | -0.37187 | -0.31232 | -0.13873 | -0.3025 | 0.027903 | -0.070704 | 0.068024 | -0.16586 | -0.16724 | 121.4655 | 121.201 | 121.2606 | 61.2639 | -121.5799 | 121.2704 | 121.407 | 121.4056 | 61.2949 | -121.7116
237.2188 | 121.8567 | -61.2534 | 60.3149 | -0.01778 | -0.020196 | 0.0088826 | 0.058573 | -0.0073778 | 0.053463 | -0.013887 | -0.0018394 | -0.0031451 | 0.060396 | 0.025517 | 0.05367 | -61.2807 | 0.033457 | -61.2109 | 60.2396 | 59.9797 | 60.0301 | -61.2283 | -61.198 | 0.078197 | -61.2966 | 60.0399 | 60.1765 | 60.1935 | -61.3738 | 0.025026 | -0.075326 | -0.027317 | 0.042493 | 0.017467 | -0.33525 | -0.28485 | -0.12042 | -0.27504 | 0.055369 | -0.043238 | 0.077182 | -0.1384 | -0.12146 | 121.493 | 121.233 | 121.2834 | 61.2868 | -121.5433 | 121.2933 | 121.4299 | 121.4468 | 61.3316 | -121.6887
238.8906 | 121.8842 | -61.2396 | 60.3333 | -0.0025182 | -0.020196 | 0.0088826 | 0.058573 | -0.0069506 | 0.053249 | -0.0062567 | -0.0018394 | -0.0033587 | 0.060396 | 0.025303 | 0.053456 | -61.2807 | 0.033457 | -61.2109 | 60.235 | 59.966 | 60.0347 | -61.2283 | -61.198 | 0.078197 | -61.2966 | 60.0445 | 60.1765 | 60.1614 | -61.3692 | 0.011293 | -0.098216 | -0.04105 | 0.02876 | 0.017467 | -0.3673 | -0.29859 | -0.12957 | -0.28877 | 0.041636 | -0.056971 | 0.072603 | -0.15671 | -0.17182 | 121.4747 | 121.2056 | 121.2743 | 61.2731 | -121.5616 | 121.2841 | 121.4162 | 121.4011 | 61.3178 | -121.7024
240.6406 | 121.8658 | -61.1984 | 60.4019 | 0.0051128 | -0.020196 | 0.0090964 | 0.058359 | -0.0073778 | 0.053676 | -0.0062567 | -0.0014122 | -0.0035723 | 0.06061 | 0.025303 | 0.053883 | -61.2853 | 0.038035 | -61.2109 | 60.235 | 59.9705 | 60.0392 | -61.2283 | -61.1934 | 0.078197 | -61.2966 | 60.0491 | 60.1765 | 60.1889 | -61.3738 | -0.029906 | -0.16688 | -0.086827 | -0.012439 | 0.017467 | -0.43138 | -0.36267 | -0.17535 | -0.35286 | 0.005015 | -0.09817 | 0.077182 | -0.22537 | -0.21301 | 121.4335 | 121.169 | 121.2377 | 61.2365 | -121.6302 | 121.2475 | 121.375 | 121.3873 | 61.2766 | -121.7757
242.375 | 121.9254 | -61.1755 | 60.3699 | -0.010149 | -0.02041 | 0.0088826 | 0.058573 | -0.0073778 | 0.053463 | -0.0062567 | -0.0016258 | -0.0035723 | 0.06061 | 0.025303 | 0.053883 | -61.2898 | 0.033457 | -61.2063 | 60.2396 | 59.9751 | 60.0347 | -61.2283 | -61.198 | 0.078197 | -61.292 | 60.0491 | 60.1765 | 60.1614 | -61.3646 | -0.052794 | -0.13026 | -0.11429 | -0.030748 | 0.022046 | -0.39476 | -0.33521 | -0.18908 | -0.32081 | -0.022451 | -0.11648 | 0.072602 | -0.19333 | -0.20844 | 121.4152 | 121.1506 | 121.2102 | 61.209 | -121.5982 | 121.2246 | 121.3521 | 121.337 | 61.2537 | -121.7345
244.1094 | 121.9208 | -61.1801 | 60.379 | 0.0051128 | -0.020196 | 0.0088826 | 0.058359 | -0.0073778 | 0.053676 | -0.013887 | -0.002053 | -0.0033587 | 0.06061 | 0.025517 | 0.05367 | -61.2761 | 0.038035 | -61.2063 | 60.2396 | 59.9751 | 60.0301 | -61.2283 | -61.2026 | 0.073618 | -61.2966 | 60.0445 | 60.1811 | 60.1752 | -61.3692 | -0.048216 | -0.13941 | -0.095981 | -0.02617 | 0.022046 | -0.40391 | -0.34894 | -0.18908 | -0.33455 | -0.022452 | -0.11648 | 0.072603 | -0.19791 | -0.20386 | 121.4197 | 121.1552 | 121.2102 | 61.2182 | -121.6074 | 121.2246 | 121.3612 | 121.3553 | 61.2537 | -121.7482
245.7969 | 121.9391 | -61.2488 | 60.2875 | -0.0025182 | -0.020196 | 0.008669 | 0.058359 | -0.0075914 | 0.053463 | -0.021518 | -0.002053 | -0.0031451 | 0.060396 | 0.025303 | 0.05367 | -61.2853 | 0.038035 | -61.2063 | 60.2442 | 59.9751 | 60.0392 | -61.2329 | -61.1934 | 0.078197 | -61.2966 | 60.0445 | 60.1765 | 60.1706 | -61.3646 | 0.015869 | -0.043283 | -0.036473 | 0.042494 | 0.026625 | -0.31236 | -0.24823 | -0.11584 | -0.243 | 0.055369 | -0.047816 | 0.068024 | -0.11093 | -0.11689 | 121.493 | 121.2239 | 121.288 | 61.2868 | -121.5204 | 121.2933 | 121.4253 | 121.4194 | 61.327 | -121.6521
247.5469 | 121.8063 | -61.203 | 60.4294 | -0.010149 | -0.02041 | 0.0088826 | 0.058359 | -0.0073778 | 0.053249 | -0.0062567 | -0.002053 | -0.0029313 | 0.060824 | 0.025517 | 0.053883 | -61.2807 | 0.033457 | -61.2109 | 60.2396 | 59.9843 | 60.0347 | -61.2329 | -61.2026 | 0.06904 | -61.292 | 60.0445 | 60.1811 | 60.1752 | -61.3646 | -0.029907 | -0.18977 | -0.077671 | -0.007861 | 0.022046 | -0.44511 | -0.39472 | -0.16162 | -0.3849 | 0.000436 | -0.089014 | 0.072602 | -0.24826 | -0.25422 | 121.4426 | 121.1873 | 121.2377 | 61.2365 | -121.6623 | 121.2475 | 121.3841 | 121.3782 | 61.272 | -121.794
249.2812 | 121.8292 | -61.2396 | 60.3882 | 0.012744 | -0.02041 | 0.0090964 | 0.058573 | -0.0071642 | 0.053676 | -0.0062567 | -0.0018394 | -0.0031451 | 0.06061 | 0.025089 | 0.05367 | -61.2761 | 0.033457 | -61.2109 | 60.235 | 59.9797 | 60.0438 | -61.2192 | -61.1934 | 0.078197 | -61.2966 | 60.0491 | 60.1765 | 60.166 | -61.3646 | 0.020451 | -0.15315 | -0.036472 | 0.02876 | 0.008309 | -0.40849 | -0.34436 | -0.12499 | -0.33913 | 0.046214 | -0.056971 | 0.068024 | -0.21164 | -0.22218 | 121.4747 | 121.2193 | 121.2834 | 61.2731 | -121.6074 | 121.2887 | 121.4162 | 121.4056 | 61.3178 | -121.7528
250.9688 | 121.843 | -61.2671 | 60.3561 | -0.010149 | -0.02041 | 0.0088826 | 0.058145 | -0.0071642 | 0.053249 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.025303 | 0.053883 | -61.2761 | 0.038035 | -61.2063 | 60.2396 | 59.9843 | 60.0347 | -61.2283 | -61.1934 | 0.078197 | -61.2874 | 60.0491 | 60.1811 | 60.1843 | -61.36 | 0.038759 | -0.11653 | -0.009006 | 0.060805 | 0.022046 | -0.37187 | -0.32147 | -0.092951 | -0.30708 | 0.07368 | -0.020348 | 0.072603 | -0.17502 | -0.17182 | 121.5067 | 121.2514 | 121.3018 | 61.3051 | -121.5845 | 121.3161 | 121.4482 | 121.4514 | 61.3453 | -121.7162
252.7031 | 121.8979 | -61.235 | 60.3516 | -0.010149 | -0.02041 | 0.008669 | 0.058573 | -0.0075914 | 0.053249 | -0.021518 | -0.0016258 | -0.0029313 | 0.059969 | 0.025089 | 0.053883 | -61.2807 | 0.033457 | -61.2109 | 60.2442 | 59.9705 | 60.0301 | -61.2283 | -61.2026 | 0.073618 | -61.2966 | 60.0491 | 60.1765 | 60.1935 | -61.36 | 0.006715 | -0.10737 | -0.045628 | 0.024182 | 0.017467 | -0.38103 | -0.32147 | -0.125 | -0.3025 | 0.032479 | -0.061549 | 0.063446 | -0.17502 | -0.15808 | 121.4792 | 121.2056 | 121.2651 | 61.2685 | -121.5799 | 121.2841 | 121.4116 | 121.4285 | 61.3087 | -121.7116
254.375 | 121.9574 | -61.1526 | 60.379 | -0.0025182 | -0.020624 | 0.0090964 | 0.058359 | -0.0073778 | 0.053463 | -0.013887 | -0.002053 | -0.0029313 | 0.06061 | 0.025517 | 0.05367 | -61.2807 | 0.038035 | -61.2063 | 60.2396 | 59.9705 | 60.0392 | -61.2329 | -61.1934 | 0.073618 | -61.2966 | 60.0491 | 60.1811 | 60.1889 | -61.3646 | -0.080261 | -0.13941 | -0.12803 | -0.053636 | 0.026625 | -0.40849 | -0.33978 | -0.21197 | -0.32997 | -0.040761 | -0.14395 | 0.068024 | -0.19791 | -0.19013 | 121.3923 | 121.1232 | 121.1919 | 61.1907 | -121.6119 | 121.2017 | 121.3338 | 121.3416 | 61.2263 | -121.7436
256.125 | 121.907 | -61.2625 | 60.2692 | -0.010149 | -0.020196 | 0.0090964 | 0.058786 | -0.0073778 | 0.053249 | -0.013887 | -0.0018394 | -0.0029313 | 0.06061 | 0.025089 | 0.053883 | -61.2761 | 0.038035 | -61.2109 | 60.2396 | 59.966 | 60.0438 | -61.2238 | -61.198 | 0.073618 | -61.2966 | 60.0399 | 60.1811 | 60.1981 | -61.3646 | 0.03876 | -0.02955 | -0.013584 | 0.051648 | 0.012888 | -0.30321 | -0.22534 | -0.10211 | -0.22926 | 0.064524 | -0.034083 | 0.068024 | -0.088043 | -0.071106 | 121.5021 | 121.2285 | 121.3063 | 61.3005 | -121.4929 | 121.3024 | 121.4436 | 121.4606 | 61.3361 | -121.6338
257.7969 | 121.8292 | -61.2396 | 60.3882 | -0.010149 | -0.02041 | 0.0088826 | 0.058359 | -0.0073778 | 0.053249 | -0.021518 | -0.0016258 | -0.0029313 | 0.06061 | 0.025517 | 0.053883 | -61.2807 | 0.028878 | -61.2109 | 60.2305 | 59.9751 | 60.0301 | -61.2283 | -61.198 | 0.078197 | -61.292 | 60.0491 | 60.1857 | 60.1752 | -61.36 | 0.011293 | -0.15773 | -0.04105 | 0.02876 | 0.017467 | -0.41307 | -0.3581 | -0.12042 | -0.33913 | 0.041636 | -0.052393 | 0.068024 | -0.20248 | -0.21302 | 121.4701 | 121.2147 | 121.2697 | 61.2685 | -121.6165 | 121.2887 | 121.4253 | 121.4148 | 61.3178 | -121.7482
259.5312 | 121.962 | -61.171 | 60.3882 | -0.010149 | -0.02041 | 0.008669 | 0.058145 | -0.0073778 | 0.053249 | -0.0062567 | -0.0016258 | -0.0031451 | 0.060824 | 0.02573 | 0.053456 | -61.2807 | 0.028878 | -61.2109 | 60.2396 | 59.9705 | 60.0347 | -61.2283 | -61.198 | 0.06904 | -61.2966 | 60.0491 | 60.1765 | 60.1981 | -61.3646 | -0.057372 | -0.14857 | -0.10971 | -0.039905 | 0.017467 | -0.41765 | -0.35352 | -0.19366 | -0.33913 | -0.027029 | -0.12564 | 0.068024 | -0.21164 | -0.19013 | 121.4106 | 121.1415 | 121.2056 | 61.1998 | -121.6165 | 121.22 | 121.3475 | 121.369 | 61.24 | -121.7528
261.2812 | 121.907 | -61.2717 | 60.2692 | -0.010149 | -0.02041 | 0.0088826 | 0.058359 | -0.0075914 | 0.053676 | -0.021518 | -0.0018394 | -0.0035723 | 0.060396 | 0.025517 | 0.053883 | -61.2761 | 0.042614 | -61.2063 | 60.2442 | 59.9797 | 60.0392 | -61.2283 | -61.2026 | 0.078197 | -61.292 | 60.0445 | 60.1811 | 60.1981 | -61.36 | 0.043336 | -0.024972 | -0.004429 | 0.065382 | 0.022046 | -0.28947 | -0.22992 | -0.088374 | -0.22468 | 0.0691 | -0.02035 | 0.068024 | -0.088043 | -0.071106 | 121.5159 | 121.2514 | 121.3109 | 61.3143 | -121.4975 | 121.3161 | 121.4528 | 121.4697 | 61.3499 | -121.6292
262.9688 | 121.9437 | -61.1572 | 60.3836 | -0.0025182 | -0.02041 | 0.0088826 | 0.058359 | -0.0073778 | 0.053035 | -0.021518 | -0.002053 | -0.0031451 | 0.060396 | 0.025303 | 0.053456 | -61.2715 | 0.033457 | -61.2109 | 60.2396 | 59.9705 | 60.0392 | -61.2283 | -61.198 | 0.078197 | -61.3058 | 60.0536 | 60.1811 | 60.1889 | -61.3692 | -0.071104 | -0.14399 | -0.11429 | -0.053637 | 0.017467 | -0.41307 | -0.34436 | -0.21197 | -0.32997 | -0.040761 | -0.14853 | 0.063445 | -0.20248 | -0.1947 | 121.3968 | 121.1278 | 121.1965 | 61.1907 | -121.6119 | 121.2109 | 121.3383 | 121.3461 | 61.2354 | -121.7528
264.7188 | 121.9299 | -61.171 | 60.3836 | -0.010149 | -0.020196 | 0.0090964 | 0.058573 | -0.0073778 | 0.053249 | -0.013887 | -0.0014122 | -0.0031451 | 0.06061 | 0.025303 | 0.053883 | -61.2853 | 0.033457 | -61.2154 | 60.2396 | 59.9797 | 60.0392 | -61.2283 | -61.198 | 0.073618 | -61.292 | 60.0399 | 60.1765 | 60.1981 | -61.36 | -0.057372 | -0.14399 | -0.11429 | -0.044483 | 0.012889 | -0.40391 | -0.34436 | -0.18908 | -0.3437 | -0.027029 | -0.12106 | 0.068024 | -0.20706 | -0.18555 | 121.4106 | 121.1507 | 121.2102 | 61.2044 | -121.6119 | 121.2109 | 121.3475 | 121.369 | 61.2446 | -121.7436
266.4062 | 121.8979 | -61.2259 | 60.347 | -0.01778 | -0.020624 | 0.0088826 | 0.058573 | -0.0073778 | 0.053035 | -0.013887 | -0.002053 | -0.0035723 | 0.060396 | 0.025517 | 0.053883 | -61.2761 | 0.0243 | -61.2109 | 60.2396 | 59.9797 | 60.0392 | -61.2421 | -61.198 | 0.06904 | -61.292 | 60.0491 | 60.1811 | 60.1935 | -61.36 | -0.016177 | -0.10737 | -0.050205 | 0.015027 | 0.031204 | -0.36729 | -0.30774 | -0.13415 | -0.29793 | 0.027903 | -0.066126 | 0.068024 | -0.16586 | -0.1535 | 121.4655 | 121.2056 | 121.2651 | 61.2502 | -121.5891 | 121.2749 | 121.407 | 121.4194 | 61.2949 | -121.707
268.1562 | 121.843 | -61.2259 | 60.3973 | -0.010149 | -0.020837 | 0.0090964 | 0.058573 | -0.0073778 | 0.053249 | -0.021518 | -0.0022666 | -0.0035723 | 0.060824 | 0.025517 | 0.05367 | -61.2807 | 0.033457 | -61.2109 | 60.2442 | 59.9705 | 60.0392 | -61.2283 | -61.198 | 0.078197 | -61.2966 | 60.0491 | 60.1903 | 60.1843 | -61.3646 | -0.00244 | -0.15315 | -0.054783 | 0.015027 | 0.017467 | -0.42681 | -0.3581 | -0.13873 | -0.34828 | 0.027903 | -0.070704 | 0.068024 | -0.20706 | -0.21302 | 121.4701 | 121.1964 | 121.2651 | 61.2593 | -121.6257 | 121.2749 | 121.4162 | 121.4102 | 61.3041 | -121.762
269.9062 | 121.8246 | -61.2122 | 60.3836 | -0.010149 | -0.02041 | 0.0088826 | 0.058573 | -0.0075914 | 0.053249 | -0.0062567 | -0.0018394 | -0.0033587 | 0.06061 | 0.02573 | 0.053456 | -61.2807 | 0.028878 | -61.2109 | 60.2396 | 59.9797 | 60.0392 | -61.2329 | -61.198 | 0.06904 | -61.292 | 60.0491 | 60.1765 | 60.1889 | -61.36 | -0.020752 | -0.14399 | -0.068516 | 0.001294 | 0.022046 | -0.40391 | -0.34436 | -0.14788 | -0.33455 | 0.01417 | -0.079859 | 0.068024 | -0.20706 | -0.1947 | 121.4518 | 121.1919 | 121.2514 | 61.241 | -121.6165 | 121.2612 | 121.3887 | 121.4011 | 61.2812 | -121.7436
271.5938 | 121.9254 | -61.2717 | 60.2921 | 0.0051128 | -0.020624 | 0.0088826 | 0.058359 | -0.0071642 | 0.053463 | -0.021518 | -0.0018394 | -0.0031451 | 0.060183 | 0.025517 | 0.05367 | -61.2807 | 0.033457 | -61.2109 | 60.2396 | 59.9843 | 60.0438 | -61.2283 | -61.1934 | 0.073618 | -61.292 | 60.0491 | 60.1811 | 60.1935 | -61.36 | 0.043336 | -0.052438 | -0.009007 | 0.060803 | 0.017467 | -0.30778 | -0.24823 | -0.088374 | -0.24299 | 0.078257 | -0.02035 | 0.068024 | -0.11093 | -0.098572 | 121.5113 | 121.2559 | 121.3155 | 61.3051 | -121.5204 | 121.3207 | 121.4528 | 121.4651 | 61.3453 | -121.6521
273.3281 | 121.8475 | -61.2625 | 60.3149 | -0.010149 | -0.021051 | 0.0090964 | 0.058573 | -0.0075914 | 0.053249 | -0.013887 | -0.0016258 | -0.0035723 | 0.060396 | 0.02573 | 0.053883 | -61.2761 | 0.038035 | -61.2109 | 60.2396 | 59.9797 | 60.0392 | -61.2283 | -61.198 | 0.073618 | -61.2966 | 60.0491 | 60.1811 | 60.1935 | -61.3692 | 0.034181 | -0.075326 | -0.013584 | 0.051648 | 0.017467 | -0.33525 | -0.2757 | -0.10669 | -0.26588 | 0.064524 | -0.034083 | 0.072603 | -0.13382 | -0.12146 | 121.5021 | 121.2422 | 121.3018 | 61.3005 | -121.5433 | 121.3116 | 121.4436 | 121.456 | 61.3361 | -121.6841
275.0781 | 121.8796 | -61.2305 | 60.3241 | -0.010149 | -0.020624 | 0.0088826 | 0.058359 | -0.0073778 | 0.053249 | -0.021518 | -0.002053 | -0.0031451 | 0.06061 | 0.02573 | 0.054097 | -61.2807 | 0.038035 | -61.2154 | 60.2396 | 59.9705 | 60.0392 | -61.2283 | -61.198 | 0.073618 | -61.2966 | 60.0445 | 60.1811 | 60.1935 | -61.3555 | 0.002138 | -0.084482 | -0.050205 | 0.015027 | 0.012889 | -0.35356 | -0.28485 | -0.12499 | -0.27962 | 0.032481 | -0.066126 | 0.058867 | -0.14297 | -0.13062 | 121.4701 | 121.201 | 121.2697 | 61.2685 | -121.5524 | 121.2749 | 121.4116 | 121.4239 | 61.3041 | -121.6796
276.8125 | 121.8384 | -61.2534 | 60.347 | 0.0051128 | -0.020837 | 0.0090964 | 0.058573 | -0.0073778 | 0.053249 | 0.0013733 | -0.0016258 | -0.0033587 | 0.060396 | 0.02573 | 0.053242 | -61.2807 | 0.033457 | -61.2109 | 60.2442 | 59.9797 | 60.0438 | -61.2329 | -61.2026 | 0.073618 | -61.2874 | 60.0536 | 60.1765 | 60.1889 | -61.3646 | 0.020447 | -0.10279 | -0.027317 | 0.042493 | 0.022046 | -0.36729 | -0.30316 | -0.11126 | -0.29335 | 0.05079 | -0.034081 | 0.077181 | -0.17044 | -0.15808 | 121.4976 | 121.233 | 121.2972 | 61.2868 | -121.5799 | 121.307 | 121.4299 | 121.4423 | 61.327 | -121.7116
278.5625 | 121.8155 | -61.2213 | 60.4111 | -0.010149 | -0.020624 | 0.0088826 | 0.058573 | -0.0071642 | 0.053249 | -0.013887 | -0.0018394 | -0.0031451 | 0.060824 | 0.025944 | 0.05367 | -61.2807 | 0.028878 | -61.2154 | 60.2442 | 59.9843 | 60.0392 | -61.2283 | -61.1934 | 0.06904 | -61.292 | 60.0399 | 60.1857 | 60.166 | -61.36 | -0.007018 | -0.16688 | -0.059361 | 0.005871 | 0.012889 | -0.4268 | -0.37183 | -0.13873 | -0.37117 | 0.027903 | -0.070704 | 0.068024 | -0.22537 | -0.24506 | 121.4655 | 121.2056 | 121.2606 | 61.2502 | -121.6394 | 121.2612 | 121.407 | 121.3873 | 61.2904 | -121.7711
280.2969 | 121.8338 | -61.2396 | 60.379 | -0.010149 | -0.02041 | 0.0088826 | 0.058573 | -0.0073778 | 0.053249 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060824 | 0.02573 | 0.053883 | -61.2761 | 0.033457 | -61.2154 | 60.2442 | 59.9751 | 60.0392 | -61.2283 | -61.198 | 0.06904 | -61.292 | 60.0491 | 60.1811 | 60.1431 | -61.36 | 0.011293 | -0.13483 | -0.036472 | 0.024182 | 0.012889 | -0.40391 | -0.33978 | -0.12042 | -0.32997 | 0.041636 | -0.052393 | 0.068024 | -0.19791 | -0.23591 | 121.4838 | 121.2147 | 121.2789 | 61.2731 | -121.6074 | 121.2887 | 121.4207 | 121.3827 | 61.3087 | -121.7391
282.0469 | 121.8384 | -61.2579 | 60.3241 | -0.010149 | -0.02041 | 0.0088826 | 0.058359 | -0.0073778 | 0.053249 | -0.0062567 | -0.0018394 | -0.0029313 | 0.060396 | 0.025944 | 0.05367 | -61.2853 | 0.028878 | -61.2109 | 60.2442 | 59.9751 | 60.0484 | -61.2283 | -61.1934 | 0.06904 | -61.2966 | 60.0491 | 60.1765 | 60.2026 | -61.36 | 0.029604 | -0.079904 | -0.027317 | 0.047071 | 0.017467 | -0.34898 | -0.2757 | -0.10211 | -0.27504 | 0.064525 | -0.03866 | 0.063446 | -0.14755 | -0.12146 | 121.5021 | 121.233 | 121.3063 | 61.2868 | -121.5524 | 121.307 | 121.4345 | 121.4606 | 61.327 | -121.6841
283.7344 | 121.9208 | -61.2625 | 60.3058 | -0.01778 | -0.020624 | 0.008669 | 0.058359 | -0.0071642 | 0.053463 | -0.013887 | -0.002053 | -0.0035723 | 0.060824 | 0.025944 | 0.053883 | -61.2853 | 0.028878 | -61.2109 | 60.2488 | 59.9797 | 60.0438 | -61.2329 | -61.1934 | 0.073618 | -61.2874 | 60.0536 | 60.1811 | 60.1752 | -61.3555 | 0.029602 | -0.057015 | -0.02274 | 0.051648 | 0.022046 | -0.32609 | -0.26196 | -0.09295 | -0.25215 | 0.069102 | -0.024926 | 0.068024 | -0.12466 | -0.13062 | 121.5113 | 121.2422 | 121.3063 | 61.2914 | -121.5387 | 121.3161 | 121.4436 | 121.4377 | 61.3361 | -121.6612
285.4844 | 121.875 | -61.2488 | 60.3378 | -0.010149 | -0.020837 | 0.0090964 | 0.058359 | -0.0075914 | 0.053249 | -0.021518 | -0.0016258 | -0.0031451 | 0.060183 | 0.025517 | 0.053456 | -61.2853 | 0.038035 | -61.2154 | 60.2488 | 59.9751 | 60.0392 | -61.2283 | -61.1934 | 0.073618 | -61.2874 | 60.0445 | 60.1811 | 60.1752 | -61.3555 | 0.020448 | -0.089059 | -0.036473 | 0.033337 | 0.012889 | -0.36272 | -0.29859 | -0.10668 | -0.29335 | 0.055369 | -0.038659 | 0.068024 | -0.15671 | -0.16266 | 121.4975 | 121.2239 | 121.288 | 61.2868 | -121.5662 | 121.2933 | 121.4299 | 121.4239 | 61.3224 | -121.6933
287.1719 | 121.9437 | -61.2579 | 60.2646 | -0.010149 | -0.020837 | 0.008669 | 0.058359 | -0.0075914 | 0.053676 | -0.013887 | -0.0022666 | -0.0033587 | 0.060396 | 0.02573 | 0.053456 | -61.2853 | 0.042614 | -61.2154 | 60.2488 | 59.9843 | 60.0484 | -61.2329 | -61.198 | 0.078197 | -61.2829 | 60.0491 | 60.1857 | 60.1156 | -61.3646 | 0.025025 | -0.015816 | -0.027317 | 0.042493 | 0.017468 | -0.28032 | -0.21619 | -0.10668 | -0.21553 | 0.059947 | -0.024924 | 0.08176 | -0.078886 | -0.14894 | 121.5067 | 121.2422 | 121.3063 | 61.3005 | -121.4975 | 121.307 | 121.4436 | 121.3736 | 61.3361 | -121.6292
288.9219 | 121.9482 | -61.1938 | 60.3836 | -0.0025182 | -0.020624 | 0.0090964 | 0.058359 | -0.0071642 | 0.053035 | -0.013887 | -0.0018394 | -0.0031451 | 0.06061 | 0.025517 | 0.053883 | -61.2853 | 0.042614 | -61.22 | 60.235 | 59.9751 | 60.0438 | -61.2238 | -61.198 | 0.078197 | -61.292 | 60.0445 | 60.1811 | 60.1981 | -61.36 | -0.029904 | -0.14857 | -0.091404 | -0.026172 | 0.003732 | -0.40849 | -0.33978 | -0.16619 | -0.33913 | -0.00414 | -0.098169 | 0.068024 | -0.20248 | -0.18555 | 121.4289 | 121.169 | 121.2377 | 61.2365 | -121.6074 | 121.2383 | 121.375 | 121.3919 | 61.272 | -121.7436
290.6719 | 121.8155 | -61.2305 | 60.4202 | -0.010149 | -0.021051 | 0.008669 | 0.058359 | -0.0075914 | 0.053463 | -0.0062567 | -0.0018394 | -0.0033587 | 0.06061 | 0.02573 | 0.05367 | -61.2807 | 0.033457 | -61.2154 | 60.2442 | 59.9705 | 60.0347 | -61.2329 | -61.198 | 0.073618 | -61.292 | 60.0491 | 60.1765 | 60.1889 | -61.3646 | -0.002441 | -0.17603 | -0.050205 | 0.015027 | 0.017468 | -0.44969 | -0.38556 | -0.13415 | -0.37117 | 0.032481 | -0.061548 | 0.072602 | -0.24368 | -0.23132 | 121.4747 | 121.201 | 121.2651 | 61.2639 | -121.6531 | 121.2795 | 121.407 | 121.4194 | 61.3041 | -121.7848
292.3594 | 121.9162 | -61.171 | 60.4019 | -0.010149 | -0.020624 | 0.008669 | 0.058359 | -0.0073778 | 0.053249 | -0.021518 | -0.0014122 | -0.0029313 | 0.060183 | 0.026158 | 0.053883 | -61.2853 | 0.033457 | -61.2154 | 60.2396 | 59.9797 | 60.0392 | -61.2329 | -61.198 | 0.06904 | -61.2966 | 60.0445 | 60.1903 | 60.1935 | -61.3555 | -0.061951 | -0.1623 | -0.11429 | -0.044483 | 0.017468 | -0.42222 | -0.36267 | -0.1845 | -0.35744 | -0.027029 | -0.12564 | 0.058867 | -0.21164 | -0.20844 | 121.4106 | 121.1507 | 121.2102 | 61.2044 | -121.6348 | 121.2154 | 121.3612 | 121.3644 | 61.24 | -121.7574
294.1094 | 121.8704 | -61.2717 | 60.3516 | -0.010149 | -0.020837 | 0.0090964 | 0.058359 | -0.0071642 | 0.053035 | -0.013887 | -0.002053 | -0.0031451 | 0.06061 | 0.02573 | 0.05367 | -61.2761 | 0.038035 | -61.2154 | 60.2396 | 59.9843 | 60.0484 | -61.2283 | -61.2026 | 0.073618 | -61.3012 | 60.0445 | 60.1857 | 60.1889 | -61.3692 | 0.043336 | -0.11195 | -0.004429 | 0.056225 | 0.012889 | -0.36729 | -0.30316 | -0.097531 | -0.30708 | 0.0691 | -0.029507 | 0.068024 | -0.16586 | -0.16266 | 121.5113 | 121.2559 | 121.3201 | 61.3097 | -121.5799 | 121.3161 | 121.4574 | 121.4606 | 61.3453 | -121.7208
295.7969 | 121.9574 | -61.1755 | 60.3653 | -0.010149 | -0.020624 | 0.0088826 | 0.058786 | -0.0071642 | 0.053035 | -0.013887 | -0.002053 | -0.0031451 | 0.06061 | 0.025944 | 0.053883 | -61.2807 | 0.038035 | -61.2109 | 60.2396 | 59.9705 | 60.0438 | -61.2329 | -61.198 | 0.06904 | -61.2966 | 60.0445 | 60.1903 | 60.1889 | -61.3555 | -0.057373 | -0.12568 | -0.10514 | -0.035327 | 0.022046 | -0.39476 | -0.32147 | -0.17993 | -0.32081 | -0.022451 | -0.12106 | 0.058867 | -0.17502 | -0.17639 | 121.4152 | 121.1461 | 121.2194 | 61.2136 | -121.5982 | 121.22 | 121.3658 | 121.3644 | 61.2446 | -121.7208
297.5312 | 121.9025 | -61.235 | 60.3378 | -0.010149 | -0.020837 | 0.0088826 | 0.058359 | -0.0078052 | 0.053249 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.02573 | 0.053883 | -61.2807 | 0.042614 | -61.2154 | 60.2442 | 59.9797 | 60.0438 | -61.2329 | -61.1888 | 0.073618 | -61.2966 | 60.0445 | 60.1857 | 60.1523 | -61.3646 | 0.002136 | -0.093637 | -0.045628 | 0.019604 | 0.017468 | -0.35814 | -0.29401 | -0.12957 | -0.29335 | 0.046215 | -0.061549 | 0.068024 | -0.15213 | -0.18556 | 121.4792 | 121.2147 | 121.2789 | 61.2777 | -121.5707 | 121.2795 | 121.4207 | 121.3873 | 61.3087 | -121.7024
299.2812 | 121.8338 | -61.2854 | 60.3973 | -0.010149 | -0.020837 | 0.0090964 | 0.058359 | -0.0073778 | 0.052822 | -0.0062567 | -0.0016258 | -0.0029313 | 0.06061 | 0.025944 | 0.053883 | -61.2761 | 0.038035 | -61.2154 | 60.2396 | 59.9797 | 60.0438 | -61.2421 | -61.2026 | 0.073618 | -61.2966 | 60.0491 | 60.1857 | 60.1752 | -61.3646 | 0.043332 | -0.15772 | 0.009304 | 0.069958 | 0.026626 | -0.41765 | -0.35352 | -0.079219 | -0.34828 | 0.082833 | -0.011195 | 0.068024 | -0.21164 | -0.22217 | 121.525 | 121.2651 | 121.3292 | 61.3234 | -121.6394 | 121.3345 | 121.4711 | 121.4606 | 61.359 | -121.762
300.9688 | 121.9299 | -61.1618 | 60.379 | -0.0025182 | -0.021051 | 0.0084552 | 0.058786 | -0.0078052 | 0.052822 | -0.021518 | -0.0018394 | -0.0031451 | 0.06061 | 0.02573 | 0.05367 | -61.2807 | 0.033457 | -61.2154 | 60.2442 | 59.9797 | 60.0392 | -61.2329 | -61.2026 | 0.082776 | -61.2966 | 60.0536 | 60.1857 | 60.166 | -61.3646 | -0.071106 | -0.13483 | -0.11887 | -0.053638 | 0.017468 | -0.39934 | -0.33978 | -0.20282 | -0.32539 | -0.040763 | -0.13479 | 0.068024 | -0.19333 | -0.21302 | 121.406 | 121.1415 | 121.201 | 61.1953 | -121.6119 | 121.2154 | 121.3475 | 121.3278 | 61.2446 | -121.7436
302.7188 | 121.8201 | -61.2946 | 60.3287 | -0.010149 | -0.020837 | 0.008669 | 0.058359 | -0.0075914 | 0.053035 | -0.021518 | -0.0016258 | -0.0027177 | 0.060396 | 0.02573 | 0.05367 | -61.2807 | 0.042614 | -61.2109 | 60.2488 | 59.9888 | 60.0438 | -61.2329 | -61.2026 | 0.06904 | -61.2966 | 60.0491 | 60.1811 | 60.1843 | -61.36 | 0.061646 | -0.079903 | 0.013882 | 0.083692 | 0.022046 | -0.33982 | -0.28485 | -0.065485 | -0.27961 | 0.091989 | -0.002039 | 0.063446 | -0.14755 | -0.14435 | 121.5433 | 121.2834 | 121.3384 | 61.3372 | -121.5616 | 121.3436 | 121.4757 | 121.4789 | 61.3636 | -121.6887
304.4531 | 121.9162 | -61.235 | 60.3333 | -0.010149 | -0.021051 | 0.008669 | 0.058359 | -0.0075914 | 0.053035 | -0.013887 | -0.0016258 | -0.0031451 | 0.060396 | 0.025944 | 0.053456 | -61.2807 | 0.033457 | -61.22 | 60.2396 | 59.9751 | 60.0438 | -61.2283 | -61.198 | 0.078197 | -61.292 | 60.0491 | 60.1811 | 60.1797 | -61.36 | 0.006715 | -0.093637 | -0.045628 | 0.015026 | 0.008311 | -0.35814 | -0.28943 | -0.125 | -0.28419 | 0.037058 | -0.056971 | 0.068024 | -0.15213 | -0.15351 | 121.4747 | 121.2102 | 121.2789 | 61.2685 | -121.5616 | 121.2841 | 121.4162 | 121.4148 | 61.3132 | -121.6933
306.2031 | 121.9208 | -61.2808 | 60.3149 | -0.010149 | -0.020837 | 0.0088826 | 0.058145 | -0.0075914 | 0.053035 | -0.029148 | -0.0016258 | -0.0031451 | 0.060396 | 0.025517 | 0.05367 | -61.2761 | 0.038035 | -61.2154 | 60.2442 | 59.9751 | 60.0438 | -61.2375 | -61.198 | 0.073618 | -61.3012 | 60.0445 | 60.1857 | 60.1889 | -61.36 | 0.043334 | -0.070748 | 0.004727 | 0.065381 | 0.022047 | -0.33983 | -0.27112 | -0.079218 | -0.27046 | 0.082835 | -0.020351 | 0.058867 | -0.12924 | -0.12604 | 121.525 | 121.2559 | 121.3246 | 61.3189 | -121.5524 | 121.3253 | 121.4665 | 121.4697 | 61.3544 | -121.675
307.9375 | 121.8613 | -61.2579 | 60.3378 | -0.0025182 | -0.021265 | 0.0082416 | 0.058786 | -0.0075914 | 0.052822 | -0.0062567 | -0.0018394 | -0.0029313 | 0.060824 | 0.02573 | 0.053456 | -61.2807 | 0.038035 | -61.2154 | 60.235 | 59.9888 | 60.0484 | -61.2375 | -61.198 | 0.073618 | -61.292 | 60.0491 | 60.1857 | 60.1935 | -61.3692 | 0.020446 | -0.10279 | -0.022739 | 0.042493 | 0.022047 | -0.34898 | -0.28943 | -0.11126 | -0.28877 | 0.059947 | -0.034082 | 0.077181 | -0.15213 | -0.14435 | 121.493 | 121.2468 | 121.3063 | 61.296 | -121.5753 | 121.307 | 121.4436 | 121.4514 | 61.3316 | -121.707
309.625 | 121.8109 | -61.3129 | 60.2875 | -0.01778 | -0.021051 | 0.008669 | 0.058573 | -0.0078052 | 0.053249 | -0.013887 | -0.0016258 | -0.0031451 | 0.060183 | 0.02573 | 0.053456 | -61.2715 | 0.028878 | -61.2154 | 60.2396 | 59.9843 | 60.0484 | -61.2421 | -61.1934 | 0.078197 | -61.2829 | 60.0536 | 60.1857 | 60.2026 | -61.3646 | 0.070798 | -0.047861 | 0.041349 | 0.097424 | 0.026626 | -0.30321 | -0.23907 | -0.051753 | -0.23384 | 0.11946 | 0.030007 | 0.08176 | -0.10177 | -0.084838 | 121.5525 | 121.2971 | 121.3613 | 61.3417 | -121.5295 | 121.3665 | 121.4986 | 121.5155 | 61.3911 | -121.6521
311.3594 | 121.8201 | -61.2534 | 60.379 | -0.010149 | -0.021265 | 0.008669 | 0.058359 | -0.0075914 | 0.053035 | -0.0062567 | -0.0016258 | -0.0027177 | 0.060396 | 0.02573 | 0.05367 | -61.2853 | 0.042614 | -61.22 | 60.2442 | 59.9797 | 60.0392 | -61.2283 | -61.2026 | 0.073618 | -61.2874 | 60.0491 | 60.1857 | 60.1843 | -61.3692 | 0.025026 | -0.13483 | -0.031895 | 0.033337 | 0.008311 | -0.39934 | -0.33978 | -0.11584 | -0.32997 | 0.05079 | -0.034081 | 0.08176 | -0.19333 | -0.1947 | 121.4976 | 121.233 | 121.2926 | 61.296 | -121.6074 | 121.3024 | 121.4391 | 121.4377 | 61.327 | -121.7482
313.1094 | 121.9437 | -61.1801 | 60.379 | -0.01778 | -0.021051 | 0.0090964 | 0.058786 | -0.0073778 | 0.053035 | -0.021518 | -0.0016258 | -0.0035723 | 0.060396 | 0.025944 | 0.05367 | -61.2807 | 0.038035 | -61.2154 | 60.2396 | 59.9797 | 60.053 | -61.2329 | -61.1934 | 0.078197 | -61.2966 | 60.0445 | 60.1903 | 60.1935 | -61.3646 | -0.052795 | -0.13941 | -0.10056 | -0.035327 | 0.017468 | -0.39934 | -0.32605 | -0.1845 | -0.33455 | -0.013295 | -0.11648 | 0.068024 | -0.18875 | -0.18555 | 121.4197 | 121.1598 | 121.2331 | 61.2182 | -121.6119 | 121.2246 | 121.3704 | 121.3736 | 61.2583 | -121.7436
314.7812 | 121.8201 | -61.2991 | 60.3195 | -0.010149 | -0.021051 | 0.0088826 | 0.058573 | -0.0075914 | 0.053035 | -0.013887 | -0.002053 | -0.0029313 | 0.060396 | 0.02573 | 0.053456 | -61.2853 | 0.042614 | -61.22 | 60.2442 | 59.9843 | 60.0438 | -61.2375 | -61.198 | 0.073618 | -61.2966 | 60.0491 | 60.1857 | 60.1981 | -61.3646 | 0.061644 | -0.075326 | 0.013881 | 0.079113 | 0.017469 | -0.33525 | -0.2757 | -0.065486 | -0.27046 | 0.10114 | 0.002538 | 0.068024 | -0.13382 | -0.12146 | 121.5433 | 121.2834 | 121.343 | 61.3417 | -121.557 | 121.3482 | 121.4848 | 121.4972 | 61.3728 | -121.6841
316.5312 | 121.9666 | -61.1755 | 60.3882 | -0.0025182 | -0.021051 | 0.008669 | 0.057932 | -0.0071642 | 0.052608 | -0.013887 | -0.0016258 | -0.0031451 | 0.060396 | 0.025944 | 0.05367 | -61.2807 | 0.042614 | -61.2154 | 60.2488 | 59.9797 | 60.0438 | -61.2375 | -61.1934 | 0.073618 | -61.3012 | 60.0491 | 60.1857 | 60.1889 | -61.3692 | -0.061952 | -0.13941 | -0.10514 | -0.039905 | 0.022047 | -0.40849 | -0.34436 | -0.19366 | -0.33913 | -0.017873 | -0.12564 | 0.068024 | -0.20248 | -0.19928 | 121.4243 | 121.1552 | 121.2194 | 61.2182 | -121.6257 | 121.2246 | 121.3612 | 121.3644 | 61.2492 | -121.7574
318.2969 | 121.9391 | -61.2534 | 60.2783 | -0.010149 | -0.021051 | 0.008669 | 0.058573 | -0.0075914 | 0.053249 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060396 | 0.025944 | 0.05367 | -61.2853 | 0.038035 | -61.2109 | 60.2396 | 59.9843 | 60.0484 | -61.2329 | -61.198 | 0.078197 | -61.2966 | 60.0491 | 60.1949 | 60.1935 | -61.3646 | 0.020447 | -0.038705 | -0.031895 | 0.042493 | 0.022046 | -0.29405 | -0.22992 | -0.11126 | -0.22926 | 0.055369 | -0.043238 | 0.068024 | -0.083462 | -0.084839 | 121.493 | 121.2376 | 121.3018 | 61.2914 | -121.5112 | 121.3024 | 121.4482 | 121.4468 | 61.3316 | -121.6429
319.9844 | 121.8292 | -61.2122 | 60.4111 | -0.010149 | -0.021051 | 0.008669 | 0.058359 | -0.0075914 | 0.052822 | -0.013887 | -0.0018394 | -0.0031451 | 0.060183 | 0.025944 | 0.05367 | -61.2853 | 0.038035 | -61.22 | 60.2442 | 59.9843 | 60.0484 | -61.2329 | -61.198 | 0.073618 | -61.3012 | 60.0445 | 60.1811 | 60.1797 | -61.3692 | -0.020752 | -0.16688 | -0.073094 | -0.007862 | 0.01289 | -0.4268 | -0.36267 | -0.15704 | -0.36659 | 0.01417 | -0.089016 | 0.068024 | -0.22995 | -0.23133 | 121.4564 | 121.1964 | 121.2606 | 61.2502 | -121.644 | 121.2566 | 121.3933 | 121.3919 | 61.2858 | -121.7803
321.7344 | 121.9025 | -61.1847 | 60.4065 | -0.0025182 | -0.021265 | 0.008669 | 0.058573 | -0.0075914 | 0.053035 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060396 | 0.026158 | 0.053456 | -61.2853 | 0.038035 | -61.2154 | 60.2442 | 59.9751 | 60.0438 | -61.2421 | -61.2026 | 0.073618 | -61.2966 | 60.0445 | 60.1903 | 60.1889 | -61.3692 | -0.057376 | -0.1623 | -0.10056 | -0.03075 | 0.026626 | -0.43138 | -0.36267 | -0.18451 | -0.36201 | -0.017875 | -0.1119 | 0.072603 | -0.21622 | -0.21759 | 121.4289 | 121.1598 | 121.2285 | 61.2227 | -121.6486 | 121.2292 | 121.375 | 121.3736 | 61.2583 | -121.7757
323.5 | 121.9162 | -61.1847 | 60.3699 | -0.0025182 | -0.021265 | 0.008669 | 0.058573 | -0.0073778 | 0.053035 | -0.021518 | -0.002053 | -0.0033587 | 0.06061 | 0.026158 | 0.053456 | -61.2761 | 0.042614 | -61.2246 | 60.2442 | 59.9751 | 60.0438 | -61.2329 | -61.198 | 0.073618 | -61.2966 | 60.0491 | 60.1903 | 60.1843 | -61.3646 | -0.048218 | -0.12568 | -0.091404 | -0.039906 | 0.008312 | -0.39476 | -0.32605 | -0.17993 | -0.32081 | -0.013296 | -0.1119 | 0.068024 | -0.17959 | -0.18555 | 121.4289 | 121.1598 | 121.2285 | 61.2273 | -121.6028 | 121.2338 | 121.375 | 121.369 | 61.2583 | -121.7345
325.25 | 121.907 | -61.2762 | 60.2783 | -0.01778 | -0.021051 | 0.00931 | 0.058359 | -0.0078052 | 0.053035 | -0.021518 | -0.0022666 | -0.0029313 | 0.060396 | 0.025944 | 0.05367 | -61.2853 | 0.047193 | -61.22 | 60.2442 | 59.9843 | 60.0438 | -61.2283 | -61.2026 | 0.078197 | -61.2966 | 60.0536 | 60.1811 | 60.1706 | -61.36 | 0.047914 | -0.034127 | -0.009007 | 0.056225 | 0.008311 | -0.29405 | -0.2345 | -0.083796 | -0.22468 | 0.073678 | -0.02035 | 0.063446 | -0.097198 | -0.10773 | 121.5204 | 121.2605 | 121.3201 | 61.3234 | -121.5067 | 121.3299 | 121.4574 | 121.4468 | 61.3544 | -121.6384
326.9375 | 121.8567 | -61.2442 | 60.3928 | 0.0051128 | -0.021265 | 0.0090964 | 0.058786 | -0.0071642 | 0.053035 | -0.013887 | -0.0016258 | -0.0031451 | 0.06061 | 0.025944 | 0.053883 | -61.2853 | 0.042614 | -61.22 | 60.2396 | 59.9797 | 60.0438 | -61.2329 | -61.1934 | 0.073618 | -61.2966 | 60.0445 | 60.1903 | 60.1935 | -61.3692 | 0.011292 | -0.15315 | -0.04105 | 0.024182 | 0.01289 | -0.41307 | -0.34894 | -0.125 | -0.34828 | 0.050792 | -0.052393 | 0.072603 | -0.20248 | -0.19928 | 121.4838 | 121.2239 | 121.288 | 61.2868 | -121.6257 | 121.2887 | 121.4345 | 121.4377 | 61.3178 | -121.762
328.6875 | 121.843 | -61.3083 | 60.3287 | -0.0025182 | -0.020837 | 0.0088826 | 0.058573 | -0.0075914 | 0.053035 | -0.021518 | -0.002053 | -0.0031451 | 0.060396 | 0.026158 | 0.053456 | -61.2807 | 0.038035 | -61.2246 | 60.2488 | 59.9888 | 60.0438 | -61.2329 | -61.1934 | 0.078197 | -61.2966 | 60.0445 | 60.1994 | 60.1981 | -61.3646 | 0.075379 | -0.079903 | 0.027615 | 0.083691 | 0.008312 | -0.33982 | -0.28485 | -0.05633 | -0.28419 | 0.11488 | 0.011694 | 0.068024 | -0.12924 | -0.13061 | 121.5571 | 121.2971 | 121.3521 | 61.3463 | -121.5616 | 121.3528 | 121.5077 | 121.5063 | 61.3865 | -121.6933
330.4375 | 121.9391 | -61.1847 | 60.4019 | -0.0025182 | -0.021051 | 0.0090964 | 0.058145 | -0.0080188 | 0.052822 | -0.013887 | -0.0016258 | -0.0029313 | 0.06061 | 0.026158 | 0.05367 | -61.2807 | 0.042614 | -61.2246 | 60.2488 | 59.9797 | 60.0438 | -61.2329 | -61.2026 | 0.073618 | -61.2966 | 60.0491 | 60.1857 | 60.1981 | -61.3692 | -0.048218 | -0.15315 | -0.095982 | -0.039906 | 0.008312 | -0.42222 | -0.35809 | -0.18451 | -0.35286 | -0.017875 | -0.1119 | 0.072603 | -0.21622 | -0.20386 | 121.4335 | 121.1644 | 121.2285 | 61.2273 | -121.6348 | 121.2338 | 121.3704 | 121.3828 | 61.2583 | -121.7711
332.1875 | 121.8292 | -61.2946 | 60.3104 | -0.0025182 | -0.021265 | 0.008669 | 0.058573 | -0.0073778 | 0.053035 | -0.013887 | -0.002053 | -0.0031451 | 0.060183 | 0.025944 | 0.05367 | -61.2807 | 0.047193 | -61.22 | 60.2442 | 59.9843 | 60.0576 | -61.2421 | -61.2071 | 0.064461 | -61.292 | 60.0491 | 60.1903 | 60.1981 | -61.3646 | 0.052488 | -0.066171 | 0.013882 | 0.074536 | 0.022048 | -0.32609 | -0.25281 | -0.070063 | -0.26131 | 0.08741 | 0.002539 | 0.072602 | -0.12009 | -0.1123 | 121.5387 | 121.2788 | 121.3521 | 61.3417 | -121.5524 | 121.3436 | 121.4848 | 121.4926 | 61.359 | -121.675
333.875 | 121.8613 | -61.2396 | 60.3653 | -0.0025182 | -0.021479 | 0.0090964 | 0.058786 | -0.0071642 | 0.053035 | -0.0062567 | -0.002053 | -0.0031451 | 0.060183 | 0.025944 | 0.05367 | -61.2807 | 0.038035 | -61.2109 | 60.2442 | 59.9843 | 60.0438 | -61.2421 | -61.2026 | 0.082776 | -61.2966 | 60.0491 | 60.1949 | 60.1752 | -61.3738 | -0.002444 | -0.1211 | -0.04105 | 0.02876 | 0.031204 | -0.38103 | -0.32147 | -0.13415 | -0.31624 | 0.037057 | -0.056971 | 0.077182 | -0.17044 | -0.19013 | 121.4838 | 121.2239 | 121.2834 | 61.2777 | -121.6074 | 121.2887 | 121.4345 | 121.4148 | 61.3224 | -121.7391
335.6094 | 121.7972 | -61.3129 | 60.3241 | -0.0025182 | -0.021265 | 0.0088826 | 0.058573 | -0.0078052 | 0.053035 | -0.0062567 | -0.0014122 | -0.0031451 | 0.060183 | 0.025944 | 0.053883 | -61.2807 | 0.042614 | -61.22 | 60.2488 | 59.9888 | 60.0484 | -61.2375 | -61.2026 | 0.078197 | -61.292 | 60.0445 | 60.1857 | 60.1569 | -61.36 | 0.075377 | -0.075326 | 0.032192 | 0.092846 | 0.017469 | -0.33525 | -0.2757 | -0.047175 | -0.27962 | 0.1103 | 0.020849 | 0.068024 | -0.1384 | -0.16725 | 121.5616 | 121.3017 | 121.3613 | 61.3555 | -121.5616 | 121.3573 | 121.4986 | 121.4697 | 61.3911 | -121.6841
337.3594 | 121.8521 | -61.2396 | 60.4111 | -0.010149 | -0.021265 | 0.0088826 | 0.058573 | -0.0075914 | 0.052608 | -0.021518 | -0.0022666 | -0.0031451 | 0.060183 | 0.026371 | 0.053883 | -61.2853 | 0.038035 | -61.2154 | 60.2442 | 59.9888 | 60.0484 | -61.2329 | -61.198 | 0.073618 | -61.2966 | 60.0582 | 60.1857 | 60.1935 | -61.36 | 0.006714 | -0.16688 | -0.045628 | 0.024182 | 0.017468 | -0.42222 | -0.36267 | -0.12042 | -0.35286 | 0.041636 | -0.056971 | 0.063446 | -0.22537 | -0.21759 | 121.4838 | 121.2285 | 121.288 | 61.2777 | -121.644 | 121.2978 | 121.4253 | 121.4331 | 61.3132 | -121.7711
339.1094 | 121.9162 | -61.2167 | 60.3653 | -0.010149 | -0.021265 | 0.0088826 | 0.058573 | -0.0078052 | 0.052822 | -0.021518 | -0.0016258 | -0.0029313 | 0.060183 | 0.025944 | 0.053456 | -61.2761 | 0.033457 | -61.22 | 60.2396 | 59.9797 | 60.0438 | -61.2375 | -61.2026 | 0.073618 | -61.3012 | 60.0491 | 60.1903 | 60.2026 | -61.3738 | -0.020753 | -0.12568 | -0.05936 | -0.003284 | 0.017469 | -0.3856 | -0.32147 | -0.15704 | -0.31624 | 0.014169 | -0.084438 | 0.072603 | -0.17502 | -0.16266 | 121.4564 | 121.1964 | 121.2606 | 61.2502 | -121.6028 | 121.2658 | 121.407 | 121.4194 | 61.2904 | -121.7391
340.7969 | 121.9299 | -61.2808 | 60.2783 | -0.010149 | -0.021479 | 0.0088826 | 0.058359 | -0.0075914 | 0.053249 | -0.013887 | -0.002053 | -0.0031451 | 0.060396 | 0.026158 | 0.053242 | -61.2807 | 0.047193 | -61.2154 | 60.2442 | 59.9797 | 60.0438 | -61.2238 | -61.198 | 0.073618 | -61.292 | 60.0536 | 60.1949 | 60.1981 | -61.3692 | 0.057071 | -0.034127 | 0.000149 | 0.065381 | 0.00831 | -0.29863 | -0.2345 | -0.088375 | -0.22468 | 0.082835 | -0.011194 | 0.077181 | -0.083462 | -0.080261 | 121.525 | 121.2605 | 121.3246 | 61.328 | -121.5021 | 121.3345 | 121.4757 | 121.4789 | 61.3544 | -121.6475
342.5469 | 121.7972 | -61.2259 | 60.4065 | -0.0025182 | -0.021051 | 0.0088826 | 0.058359 | -0.0075914 | 0.052608 | -0.013887 | -0.002053 | -0.0033587 | 0.059969 | 0.026585 | 0.053456 | -61.2807 | 0.038035 | -61.2154 | 60.2533 | 59.9797 | 60.0484 | -61.2375 | -61.198 | 0.073618 | -61.2966 | 60.0491 | 60.1903 | 60.1752 | -61.3646 | -0.011598 | -0.15314 | -0.054783 | 0.010449 | 0.022047 | -0.4268 | -0.35809 | -0.13873 | -0.35744 | 0.027903 | -0.070704 | 0.068024 | -0.21622 | -0.23133 | 121.4792 | 121.2056 | 121.2743 | 61.2639 | -121.644 | 121.2749 | 121.4162 | 121.4011 | 61.2995 | -121.7711
344.2969 | 121.907 | -61.2076 | 60.3928 | 0.0051128 | -0.021051 | 0.00931 | 0.058359 | -0.0073778 | 0.053035 | -0.021518 | -0.002053 | -0.0035723 | 0.060396 | 0.026158 | 0.053456 | -61.2807 | 0.038035 | -61.2154 | 60.2488 | 60.0026 | 60.0621 | -61.2329 | -61.2026 | 0.073618 | -61.3058 | 60.0536 | 60.1903 | 60.1981 | -61.3692 | -0.025329 | -0.14399 | -0.073093 | -0.007861 | 0.017468 | -0.39017 | -0.33062 | -0.16162 | -0.33912 | 0.005014 | -0.098172 | 0.063445 | -0.20248 | -0.1947 | 121.4564 | 121.2102 | 121.2697 | 61.2456 | -121.6257 | 121.2612 | 121.3979 | 121.4056 | 61.2812 | -121.762
345.9844 | 121.8384 | -61.3312 | 60.3149 | -0.010149 | -0.021479 | 0.0090964 | 0.058145 | -0.0078052 | 0.053035 | -0.0062567 | -0.0016258 | -0.0029313 | 0.06061 | 0.026158 | 0.054097 | -61.2807 | 0.042614 | -61.22 | 60.2533 | 59.9888 | 60.0576 | -61.2329 | -61.198 | 0.078197 | -61.2966 | 60.0536 | 60.1949 | 60.2026 | -61.3738 | 0.098267 | -0.061591 | 0.050503 | 0.11116 | 0.01289 | -0.32609 | -0.25738 | -0.0426 | -0.2613 | 0.13319 | 0.034582 | 0.077182 | -0.12008 | -0.1123 | 121.5845 | 121.32 | 121.3887 | 61.3738 | -121.5479 | 121.3848 | 121.526 | 121.5338 | 61.4094 | -121.6887
347.7344 | 121.8933 | -61.2396 | 60.3241 | -0.025411 | -0.021692 | 0.008669 | 0.058145 | -0.0075914 | 0.052608 | -0.029148 | -0.002053 | -0.0033587 | 0.060396 | 0.026585 | 0.05367 | -61.2807 | 0.042614 | -61.2109 | 60.2442 | 59.9843 | 60.0438 | -61.2238 | -61.1888 | 0.082776 | -61.2966 | 60.0491 | 60.1903 | 60.1889 | -61.3646 | 0.015872 | -0.079904 | -0.04105 | 0.02876 | 0.012888 | -0.33983 | -0.28027 | -0.12499 | -0.27504 | 0.050793 | -0.056971 | 0.068024 | -0.13382 | -0.1352 | 121.4838 | 121.2239 | 121.2834 | 61.2822 | -121.5478 | 121.2887 | 121.4299 | 121.4285 | 61.3224 | -121.6887
349.4688 | 121.9528 | -61.1755 | 60.3607 | 0.0051128 | -0.020837 | 0.0088826 | 0.058573 | -0.0078052 | 0.053249 | -0.013887 | -0.002053 | -0.0031451 | 0.06061 | 0.026158 | 0.053456 | -61.2761 | 0.042614 | -61.2154 | 60.2396 | 59.9797 | 60.0484 | -61.2329 | -61.2117 | 0.073618 | -61.3012 | 60.0491 | 60.1903 | 60.1981 | -61.36 | -0.057373 | -0.1211 | -0.10056 | -0.039905 | 0.017468 | -0.38103 | -0.31232 | -0.1845 | -0.31166 | -0.036187 | -0.12564 | 0.058867 | -0.17044 | -0.16266 | 121.4152 | 121.1552 | 121.2239 | 61.2182 | -121.5936 | 121.2246 | 121.3658 | 121.3736 | 61.2492 | -121.7208
351.1562 | 121.8842 | -61.2442 | 60.3516 | -0.010149 | -0.021692 | 0.0084552 | 0.058145 | -0.0075914 | 0.052608 | -0.013887 | -0.0018394 | -0.0029313 | 0.06061 | 0.025944 | 0.053456 | -61.2761 | 0.042614 | -61.2154 | 60.2488 | 59.9751 | 60.053 | -61.2329 | -61.2117 | 0.06904 | -61.2966 | 60.0582 | 60.1857 | 60.1981 | -61.3692 | 0.011292 | -0.10279 | -0.031894 | 0.02876 | 0.017468 | -0.37645 | -0.29858 | -0.125 | -0.29335 | 0.032478 | -0.052393 | 0.072603 | -0.16586 | -0.1535 | 121.493 | 121.2193 | 121.2972 | 61.2868 | -121.5845 | 121.3024 | 121.4299 | 121.4423 | 61.3132 | -121.7208
352.8438 | 121.907 | -61.2488 | 60.3333 | -0.01778 | -0.021906 | 0.0088826 | 0.058573 | -0.0075914 | 0.053035 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.026158 | 0.053456 | -61.2761 | 0.038035 | -61.2154 | 60.2396 | 59.9797 | 60.0576 | -61.2329 | -61.198 | 0.073618 | -61.2966 | 60.0536 | 60.1903 | 60.1935 | -61.3646 | 0.015869 | -0.093637 | -0.027317 | 0.033337 | 0.017468 | -0.35356 | -0.27569 | -0.11584 | -0.27961 | 0.050791 | -0.047816 | 0.068024 | -0.14297 | -0.13977 | 121.4884 | 121.2285 | 121.3063 | 61.2868 | -121.5662 | 121.3024 | 121.4391 | 121.4423 | 61.3224 | -121.6979
354.5938 | 121.8246 | -61.3129 | 60.3195 | -0.010149 | -0.021692 | 0.0088826 | 0.058573 | -0.0073778 | 0.052822 | -0.021518 | -0.002053 | -0.0031451 | 0.06061 | 0.026158 | 0.05367 | -61.2853 | 0.038035 | -61.2109 | 60.2442 | 59.9888 | 60.0484 | -61.2283 | -61.198 | 0.06904 | -61.292 | 60.0491 | 60.1949 | 60.1935 | -61.3692 | 0.084535 | -0.075326 | 0.027614 | 0.102 | 0.017467 | -0.33067 | -0.27112 | -0.056332 | -0.27046 | 0.11488 | 0.020849 | 0.077181 | -0.12466 | -0.12604 | 121.5571 | 121.3017 | 121.3613 | 61.3509 | -121.5478 | 121.3619 | 121.5077 | 121.5063 | 61.3819 | -121.6887
356.3125 | 121.9528 | -61.1755 | 60.3882 | -0.010149 | -0.021479 | 0.0088826 | 0.058359 | -0.0075914 | 0.053035 | -0.013887 | -0.0016258 | -0.0029313 | 0.060396 | 0.026371 | 0.05367 | -61.2761 | 0.042614 | -61.2154 | 60.2488 | 59.9797 | 60.053 | -61.2421 | -61.2026 | 0.073618 | -61.3058 | 60.0536 | 60.1949 | 60.1981 | -61.3646 | -0.066531 | -0.13941 | -0.10056 | -0.039905 | 0.026626 | -0.40849 | -0.3352 | -0.18908 | -0.33455 | -0.02703 | -0.13022 | 0.058866 | -0.19333 | -0.19013 | 121.4243 | 121.1552 | 121.2285 | 61.2182 | -121.6303 | 121.2292 | 121.3704 | 121.3736 | 61.2492 | -121.7528
358 | 121.9299 | -61.203 | 60.3607 | -0.01778 | -0.021479 | 0.0088826 | 0.058573 | -0.0075914 | 0.052822 | -0.013887 | -0.0016258 | -0.0031451 | 0.060396 | 0.026371 | 0.053456 | -61.2853 | 0.038035 | -61.22 | 60.2488 | 59.9843 | 60.0484 | -61.2375 | -61.2071 | 0.078197 | -61.2966 | 60.0536 | 60.1903 | 60.1981 | -61.3646 | -0.034486 | -0.11195 | -0.082249 | -0.017017 | 0.017469 | -0.37645 | -0.31232 | -0.16162 | -0.30708 | -0.004143 | -0.093592 | 0.068024 | -0.17044 | -0.16266 | 121.4518 | 121.1873 | 121.2514 | 61.241 | -121.5982 | 121.2566 | 121.3933 | 121.4011 | 61.2812 | -121.7253
359.7344 | 121.9437 | -61.1801 | 60.3882 | -0.0025182 | -0.021906 | 0.0088826 | 0.058573 | -0.0071642 | 0.052822 | -0.021518 | -0.0018394 | -0.0031451 | 0.060183 | 0.026158 | 0.053456 | -61.2853 | 0.047193 | -61.2154 | 60.235 | 59.9797 | 60.053 | -61.2375 | -61.2117 | 0.073618 | -61.2966 | 60.0536 | 60.1903 | 60.1981 | -61.36 | -0.057374 | -0.15315 | -0.10514 | -0.035327 | 0.022047 | -0.40849 | -0.3352 | -0.17993 | -0.33455 | -0.031609 | -0.11648 | 0.063446 | -0.19791 | -0.19013 | 121.4152 | 121.1598 | 121.2331 | 61.2273 | -121.6257 | 121.2338 | 121.3704 | 121.3782 | 61.2537 | -121.7482
361.4062 | 121.9574 | -61.203 | 60.3607 | -0.0025182 | -0.021479 | 0.0088826 | 0.058145 | -0.0078052 | 0.053035 | -0.013887 | -0.0018394 | -0.0033587 | 0.06061 | 0.026158 | 0.05367 | -61.2853 | 0.038035 | -61.2154 | 60.2488 | 60.0026 | 60.0484 | -61.2421 | -61.2071 | 0.073618 | -61.2966 | 60.0536 | 60.1903 | 60.2026 | -61.3829 | -0.039065 | -0.11195 | -0.082249 | -0.012439 | 0.026626 | -0.35813 | -0.31232 | -0.17993 | -0.30708 | -0.004143 | -0.093592 | 0.08634 | -0.17044 | -0.15808 | 121.4518 | 121.2056 | 121.2514 | 61.241 | -121.6028 | 121.2566 | 121.3933 | 121.4056 | 61.2766 | -121.7437
363.1719 | 121.8338 | -61.29 | 60.3104 | -0.0025182 | -0.021479 | 0.0088826 | 0.058573 | -0.0078052 | 0.052394 | -0.021518 | -0.0018394 | -0.0033587 | 0.06061 | 0.026371 | 0.053456 | -61.2807 | 0.042614 | -61.2109 | 60.2488 | 59.9843 | 60.0484 | -61.2375 | -61.2026 | 0.078197 | -61.2966 | 60.0491 | 60.1903 | 60.2072 | -61.3692 | 0.052489 | -0.061593 | 0.009304 | 0.079114 | 0.026625 | -0.32609 | -0.26196 | -0.07922 | -0.26131 | 0.087411 | -0.006617 | 0.072603 | -0.12009 | -0.10315 | 121.5387 | 121.2742 | 121.3384 | 61.3326 | -121.5479 | 121.339 | 121.4803 | 121.4972 | 61.3682 | -121.6796
364.9219 | 121.9254 | -61.171 | 60.3653 | -0.0025182 | -0.021479 | 0.0088826 | 0.058359 | -0.0075914 | 0.053035 | -0.021518 | -0.002053 | -0.0033587 | 0.060396 | 0.026371 | 0.053242 | -61.2853 | 0.047193 | -61.2154 | 60.2488 | 59.9797 | 60.0484 | -61.2375 | -61.2026 | 0.06904 | -61.3058 | 60.0628 | 60.1949 | 60.1935 | -61.3692 | -0.06653 | -0.11652 | -0.11429 | -0.044483 | 0.022047 | -0.3856 | -0.31689 | -0.19824 | -0.3025 | -0.031608 | -0.13479 | 0.063445 | -0.17044 | -0.17181 | 121.4197 | 121.1507 | 121.2194 | 61.2182 | -121.6028 | 121.2338 | 121.3658 | 121.3644 | 61.24 | -121.7345
366.6094 | 121.9162 | -61.1893 | 60.3699 | -0.0025182 | -0.021692 | 0.0088826 | 0.058573 | -0.0075914 | 0.052822 | -0.021518 | -0.0016258 | -0.0029313 | 0.06061 | 0.026799 | 0.053456 | -61.2807 | 0.042614 | -61.22 | 60.2442 | 59.9888 | 60.053 | -61.2421 | -61.2071 | 0.078197 | -61.2966 | 60.0491 | 60.204 | 60.1843 | -61.3738 | -0.052798 | -0.12568 | -0.091404 | -0.03075 | 0.022048 | -0.38102 | -0.31689 | -0.18451 | -0.32081 | -0.017876 | -0.10733 | 0.077182 | -0.16586 | -0.18555 | 121.4335 | 121.1781 | 121.2422 | 61.2319 | -121.6119 | 121.2383 | 121.3933 | 121.3736 | 61.2675 | -121.7437
368.375 | 121.8933 | -61.2396 | 60.3561 | -0.01778 | -0.021692 | 0.008669 | 0.058359 | -0.0075914 | 0.052822 | -0.0062567 | -0.002053 | -0.0031451 | 0.060396 | 0.026799 | 0.053242 | -61.2807 | 0.038035 | -61.22 | 60.2442 | 59.9705 | 60.053 | -61.2329 | -61.198 | 0.082776 | -61.2966 | 60.0582 | 60.1949 | 60.1889 | -61.3646 | 0.006714 | -0.11195 | -0.04105 | 0.019604 | 0.01289 | -0.38561 | -0.30316 | -0.12499 | -0.29792 | 0.041636 | -0.056971 | 0.068024 | -0.16128 | -0.16724 | 121.4838 | 121.2102 | 121.2926 | 61.2777 | -121.5891 | 121.2978 | 121.4345 | 121.4285 | 61.3224 | -121.7208
370.0625 | 121.9391 | -61.1664 | 60.3516 | -0.0025182 | -0.021906 | 0.0088826 | 0.058786 | -0.0071642 | 0.052822 | -0.0062567 | -0.0016258 | -0.0035723 | 0.060396 | 0.026371 | 0.05367 | -61.2807 | 0.038035 | -61.2154 | 60.2488 | 59.9843 | 60.053 | -61.2375 | -61.2026 | 0.073618 | -61.292 | 60.0582 | 60.1857 | 60.1797 | -61.3692 | -0.071107 | -0.10279 | -0.11429 | -0.04906 | 0.022047 | -0.36729 | -0.29858 | -0.20282 | -0.29335 | -0.036185 | -0.12564 | 0.077181 | -0.16586 | -0.17182 | 121.4152 | 121.1507 | 121.2194 | 61.2044 | -121.5891 | 121.2246 | 121.3521 | 121.3461 | 61.24 | -121.7208
371.8125 | 121.8201 | -61.235 | 60.4477 | -0.0025182 | -0.021906 | 0.0090964 | 0.058573 | -0.0075914 | 0.053035 | -0.013887 | -0.0018394 | -0.0031451 | 0.060396 | 0.026585 | 0.053242 | -61.2898 | 0.047193 | -61.2154 | 60.2442 | 59.998 | 60.0576 | -61.2421 | -61.2071 | 0.078197 | -61.2966 | 60.0582 | 60.1994 | 60.2026 | -61.3692 | -0.007022 | -0.2035 | -0.054785 | 0.019604 | 0.026626 | -0.44969 | -0.39013 | -0.13415 | -0.38948 | 0.0279 | -0.061549 | 0.072603 | -0.24826 | -0.24506 | 121.4792 | 121.2331 | 121.2926 | 61.2822 | -121.6898 | 121.2933 | 121.4345 | 121.4377 | 61.3132 | -121.8169
373.5938 | 121.8796 | -61.2122 | 60.3745 | -0.0025182 | -0.021906 | 0.008669 | 0.058573 | -0.0078052 | 0.052822 | -0.013887 | -0.0016258 | -0.0033587 | 0.060183 | 0.026371 | 0.05367 | -61.2807 | 0.042614 | -61.2109 | 60.2442 | 59.9751 | 60.053 | -61.2329 | -61.2071 | 0.078197 | -61.2966 | 60.0536 | 60.1949 | 60.2026 | -61.3692 | -0.020752 | -0.13026 | -0.068516 | 0.001294 | 0.022046 | -0.39934 | -0.32147 | -0.15704 | -0.32081 | 0.005012 | -0.084437 | 0.072603 | -0.17959 | -0.17181 | 121.4564 | 121.1873 | 121.2651 | 61.2548 | -121.6074 | 121.2658 | 121.407 | 121.4148 | 61.2904 | -121.7436
375.3438 | 121.8613 | -61.2808 | 60.3241 | -0.0025182 | -0.021906 | 0.0088826 | 0.058359 | -0.0078052 | 0.052822 | -0.013887 | -0.002053 | -0.0033587 | 0.06061 | 0.026585 | 0.05367 | -61.2807 | 0.038035 | -61.2154 | 60.2488 | 59.9934 | 60.053 | -61.2375 | -61.198 | 0.073618 | -61.292 | 60.0536 | 60.204 | 60.2026 | -61.3692 | 0.043334 | -0.075326 | 0.000149 | 0.065381 | 0.022047 | -0.33067 | -0.27112 | -0.088375 | -0.27046 | 0.082835 | -0.011194 | 0.077181 | -0.12008 | -0.12146 | 121.5296 | 121.2743 | 121.3338 | 61.3189 | -121.5616 | 121.3345 | 121.4848 | 121.4835 | 61.3544 | -121.6933
377.0156 | 121.8109 | -61.2854 | 60.3241 | -0.0025182 | -0.02212 | 0.0090964 | 0.058786 | -0.0078052 | 0.052608 | -0.021518 | -0.0014122 | -0.0033587 | 0.059969 | 0.026371 | 0.053242 | -61.2715 | 0.038035 | -61.22 | 60.2442 | 59.9888 | 60.053 | -61.2375 | -61.2117 | 0.078197 | -61.2966 | 60.0536 | 60.1994 | 60.2072 | -61.3692 | 0.047911 | -0.079904 | 0.013883 | 0.06538 | 0.017469 | -0.33525 | -0.27112 | -0.083798 | -0.27046 | 0.073676 | -0.011195 | 0.072603 | -0.12466 | -0.11688 | 121.5296 | 121.2742 | 121.3384 | 61.3234 | -121.5616 | 121.339 | 121.4848 | 121.4926 | 61.3636 | -121.6933
378.7812 | 121.9345 | -61.1755 | 60.3607 | -0.010149 | -0.021906 | 0.0088826 | 0.058359 | -0.0078052 | 0.052608 | -0.021518 | -0.002053 | -0.0029313 | 0.06061 | 0.026371 | 0.053456 | -61.2807 | 0.042614 | -61.2154 | 60.2442 | 59.9934 | 60.0576 | -61.2329 | -61.2071 | 0.078197 | -61.292 | 60.0536 | 60.1949 | 60.2026 | -61.3646 | -0.057373 | -0.11652 | -0.10514 | -0.039905 | 0.017468 | -0.36729 | -0.30316 | -0.18908 | -0.30708 | -0.031609 | -0.11648 | 0.072602 | -0.16586 | -0.15808 | 121.4197 | 121.169 | 121.2331 | 61.2182 | -121.5936 | 121.2292 | 121.3704 | 121.3782 | 61.2537 | -121.7253
380.4688 | 121.7926 | -61.3266 | 60.3195 | -0.0025182 | -0.022333 | 0.0088826 | 0.058359 | -0.0082324 | 0.052822 | -0.0062567 | -0.002053 | -0.0031451 | 0.060396 | 0.026799 | 0.05367 | -61.2807 | 0.042614 | -61.2154 | 60.2488 | 59.9888 | 60.0576 | -61.2421 | -61.2071 | 0.078197 | -61.3058 | 60.0491 | 60.1949 | 60.2072 | -61.36 | 0.084531 | -0.070748 | 0.045925 | 0.11116 | 0.026626 | -0.33067 | -0.26196 | -0.033442 | -0.27046 | 0.11945 | 0.020846 | 0.054288 | -0.12466 | -0.1123 | 121.5754 | 121.3154 | 121.3842 | 61.3692 | -121.5616 | 121.3757 | 121.5215 | 121.5338 | 61.4048 | -121.6796
382.2188 | 121.8979 | -61.2213 | 60.3607 | -0.0025182 | -0.02212 | 0.0084552 | 0.058573 | -0.0075914 | 0.052822 | -0.013887 | -0.002053 | -0.0031451 | 0.06061 | 0.026371 | 0.053456 | -61.2761 | 0.042614 | -61.2154 | 60.2442 | 59.9843 | 60.0576 | -61.2421 | -61.198 | 0.073618 | -61.2966 | 60.0536 | 60.1949 | 60.2026 | -61.3692 | -0.020755 | -0.11652 | -0.054783 | 0.005871 | 0.026626 | -0.37645 | -0.30316 | -0.14788 | -0.30708 | 0.023325 | -0.075282 | 0.072603 | -0.16586 | -0.15808 | 121.4655 | 121.2056 | 121.2789 | 61.2639 | -121.6028 | 121.275 | 121.4162 | 121.424 | 61.2949 | -121.7299
383.9688 | 121.9025 | -61.2167 | 60.3653 | -0.01778 | -0.021906 | 0.008669 | 0.058359 | -0.0073778 | 0.052608 | -0.021518 | -0.002053 | -0.0029313 | 0.060396 | 0.026585 | 0.053242 | -61.2807 | 0.038035 | -61.2154 | 60.2488 | 59.9843 | 60.053 | -61.2375 | -61.2071 | 0.073618 | -61.3012 | 60.0582 | 60.1994 | 60.1935 | -61.3692 | -0.020753 | -0.11652 | -0.063938 | 0.001294 | 0.022047 | -0.38103 | -0.31232 | -0.15246 | -0.30708 | 0.00959 | -0.084438 | 0.068024 | -0.16586 | -0.17181 | 121.4655 | 121.201 | 121.2697 | 61.2548 | -121.6028 | 121.275 | 121.4162 | 121.4102 | 61.2904 | -121.7345
385.6406 | 121.8613 | -61.2488 | 60.347 | -0.0025182 | -0.021906 | 0.008669 | 0.058573 | -0.0078052 | 0.052608 | -0.0062567 | -0.0018394 | -0.0033587 | 0.060396 | 0.026799 | 0.05367 | -61.2853 | 0.047193 | -61.22 | 60.2488 | 59.9888 | 60.053 | -61.2375 | -61.198 | 0.078197 | -61.2966 | 60.0582 | 60.1994 | 60.1797 | -61.3692 | 0.01129 | -0.098214 | -0.036473 | 0.028759 | 0.017469 | -0.35814 | -0.294 | -0.12042 | -0.28877 | 0.050791 | -0.047816 | 0.072603 | -0.14755 | -0.16724 | 121.4975 | 121.2376 | 121.3018 | 61.296 | -121.5845 | 121.307 | 121.4482 | 121.4285 | 61.327 | -121.7162
387.375 | 121.8018 | -61.322 | 60.3149 | -0.0025182 | -0.021906 | 0.0088826 | 0.058786 | -0.0080188 | 0.052822 | -0.021518 | -0.0018394 | -0.0033587 | 0.060183 | 0.026371 | 0.053242 | -61.2715 | 0.042614 | -61.2109 | 60.2442 | 60.0072 | 60.0576 | -61.2421 | -61.2026 | 0.082776 | -61.2966 | 60.0536 | 60.1949 | 60.2026 | -61.3646 | 0.079953 | -0.070748 | 0.050504 | 0.11116 | 0.031204 | -0.30778 | -0.25738 | -0.042598 | -0.2613 | 0.11945 | 0.025426 | 0.068024 | -0.12008 | -0.1123 | 121.5662 | 121.3292 | 121.3796 | 61.3646 | -121.557 | 121.3757 | 121.5169 | 121.5247 | 61.4048 | -121.6796
389.125 | 121.8338 | -61.2396 | 60.3836 | -0.010149 | -0.02212 | 0.0088826 | 0.059 | -0.0075914 | 0.052822 | -0.029148 | -0.0016258 | -0.0029313 | 0.06061 | 0.026585 | 0.053456 | -61.2807 | 0.042614 | -61.2154 | 60.2488 | 60.0072 | 60.053 | -61.2375 | -61.2026 | 0.06904 | -61.2966 | 60.0582 | 60.1994 | 60.2026 | -61.3692 | 0.002135 | -0.13484 | -0.04105 | 0.024182 | 0.022047 | -0.37644 | -0.33063 | -0.12957 | -0.32539 | 0.037057 | -0.056971 | 0.072603 | -0.18417 | -0.18097 | 121.4884 | 121.2468 | 121.2926 | 61.2822 | -121.6211 | 121.2978 | 121.4391 | 121.4423 | 61.3087 | -121.7528
390.8594 | 121.8201 | -61.2946 | 60.3058 | -0.01778 | -0.02212 | 0.008669 | 0.058573 | -0.0075914 | 0.052608 | -0.0062567 | -0.0018394 | -0.0033587 | 0.060396 | 0.026585 | 0.053242 | -61.2761 | 0.042614 | -61.2109 | 60.2442 | 60.0026 | 60.0576 | -61.2375 | -61.198 | 0.082776 | -61.292 | 60.0491 | 60.1994 | 60.2026 | -61.3646 | 0.057067 | -0.061593 | 0.01846 | 0.083692 | 0.026625 | -0.3032 | -0.24823 | -0.070063 | -0.25673 | 0.096568 | 0.002539 | 0.072602 | -0.10635 | -0.10315 | 121.5387 | 121.2971 | 121.3521 | 61.3372 | -121.5433 | 121.3436 | 121.494 | 121.4972 | 61.3773 | -121.6704
392.6094 | 121.9391 | -61.1893 | 60.347 | -0.01778 | -0.02212 | 0.008669 | 0.058145 | -0.0075914 | 0.052822 | -0.021518 | -0.0016258 | -0.0033587 | 0.06061 | 0.026585 | 0.053242 | -61.2807 | 0.047193 | -61.2154 | 60.2488 | 59.9843 | 60.0576 | -61.2375 | -61.2071 | 0.078197 | -61.2966 | 60.0582 | 60.1994 | 60.1981 | -61.3738 | -0.048219 | -0.098214 | -0.091404 | -0.026172 | 0.022047 | -0.36271 | -0.28943 | -0.18451 | -0.28877 | -0.017876 | -0.10733 | 0.077182 | -0.14755 | -0.14893 | 121.438 | 121.1735 | 121.2468 | 61.2365 | -121.5845 | 121.2475 | 121.3887 | 121.3873 | 61.2675 | -121.7208
394.2969 | 121.9025 | -61.235 | 60.347 | -0.0025182 | -0.022333 | 0.0090964 | 0.058359 | -0.0078052 | 0.052608 | -0.021518 | -0.0016258 | -0.0033587 | 0.06061 | 0.026799 | 0.053456 | -61.2807 | 0.047193 | -61.22 | 60.2396 | 59.9797 | 60.0576 | -61.2329 | -61.2071 | 0.078197 | -61.2966 | 60.0628 | 60.1949 | 60.2026 | -61.3692 | 0.002136 | -0.10737 | -0.045628 | 0.015026 | 0.01289 | -0.36729 | -0.28943 | -0.13415 | -0.28419 | 0.0279 | -0.061549 | 0.072603 | -0.15213 | -0.14435 | 121.4747 | 121.2147 | 121.2926 | 61.2822 | -121.5799 | 121.2978 | 121.4299 | 121.4377 | 61.3132 | -121.7162
395.9844 | 121.8109 | -61.3129 | 60.3333 | -0.010149 | -0.022761 | 0.0090964 | 0.058573 | -0.0075914 | 0.052822 | 0.0013733 | -0.0018394 | -0.0031451 | 0.060396 | 0.026585 | 0.053456 | -61.2853 | 0.042614 | -61.2154 | 60.2533 | 59.9934 | 60.0576 | -61.2329 | -61.2026 | 0.073618 | -61.2966 | 60.0582 | 60.1949 | 60.1797 | -61.3692 | 0.079956 | -0.079902 | 0.027614 | 0.097424 | 0.017468 | -0.33982 | -0.27569 | -0.056332 | -0.27504 | 0.1103 | 0.016271 | 0.072603 | -0.13839 | -0.15351 | 121.5662 | 121.3063 | 121.3704 | 61.3555 | -121.5662 | 121.3711 | 121.5077 | 121.4926 | 61.3865 | -121.7024
397.7344 | 121.788 | -61.3129 | 60.3241 | -0.0025182 | -0.02212 | 0.0090964 | 0.058359 | -0.0075914 | 0.052822 | 0.0013733 | -0.0018394 | -0.0031451 | 0.060183 | 0.026585 | 0.053242 | -61.2715 | 0.038035 | -61.2154 | 60.2533 | 59.9843 | 60.0621 | -61.2375 | -61.2071 | 0.082776 | -61.3012 | 60.0491 | 60.1949 | 60.1797 | -61.3692 | 0.075377 | -0.070747 | 0.041349 | 0.097424 | 0.022047 | -0.33983 | -0.26196 | -0.056332 | -0.27504 | 0.10572 | 0.011692 | 0.068024 | -0.12924 | -0.14435 | 121.5662 | 121.2971 | 121.375 | 61.3509 | -121.5616 | 121.3619 | 121.5077 | 121.4926 | 61.3956 | -121.6933
399.5 | 121.8475 | -61.2854 | 60.3516 | -0.010149 | -0.021692 | 0.0088826 | 0.058359 | -0.0078052 | 0.052822 | -0.013887 | -0.002053 | -0.0033587 | 0.06061 | 0.026585 | 0.053456 | -61.2761 | 0.042614 | -61.2154 | 60.2533 | 60.0072 | 60.0576 | -61.2375 | -61.2071 | 0.06904 | -61.292 | 60.0536 | 60.204 | 60.1797 | -61.3646 | 0.047911 | -0.098212 | 0.009304 | 0.069958 | 0.022047 | -0.3444 | -0.294 | -0.079219 | -0.29792 | 0.078254 | -0.006617 | 0.072602 | -0.14755 | -0.17182 | 121.5387 | 121.2926 | 121.343 | 61.328 | -121.5891 | 121.339 | 121.4894 | 121.4651 | 61.3544 | -121.7162
401.1875 | 121.8338 | -61.3037 | 60.3195 | -0.010149 | -0.022333 | 0.0088826 | 0.058573 | -0.0078052 | 0.052608 | -0.021518 | -0.002053 | -0.0031451 | 0.060183 | 0.026371 | 0.053456 | -61.2853 | 0.033457 | -61.22 | 60.2533 | 60.0117 | 60.0576 | -61.2375 | -61.198 | 0.073618 | -61.292 | 60.0536 | 60.1949 | 60.2072 | -61.3692 | 0.066222 | -0.066169 | 0.018459 | 0.083691 | 0.017469 | -0.30777 | -0.26196 | -0.065487 | -0.26588 | 0.10572 | 0.011694 | 0.077181 | -0.12466 | -0.1123 | 121.5571 | 121.3155 | 121.3613 | 61.3372 | -121.557 | 121.3573 | 121.4986 | 121.5109 | 61.3773 | -121.6887
402.9531 | 121.8704 | -61.2808 | 60.3104 | 0.0051128 | -0.02212 | 0.00931 | 0.058786 | -0.0073778 | 0.052822 | -0.013887 | -0.0016258 | -0.0033587 | 0.060183 | 0.027226 | 0.053456 | -61.2807 | 0.038035 | -61.22 | 60.2442 | 59.9888 | 60.0621 | -61.2421 | -61.2071 | 0.078197 | -61.3012 | 60.0536 | 60.204 | 60.2026 | -61.3692 | 0.038755 | -0.066171 | 0.000149 | 0.060803 | 0.022048 | -0.32151 | -0.24823 | -0.088375 | -0.25673 | 0.073677 | -0.020351 | 0.068024 | -0.10635 | -0.10773 | 121.525 | 121.2697 | 121.343 | 61.3189 | -121.5524 | 121.3345 | 121.4848 | 121.4835 | 61.359 | -121.6796
404.7031 | 121.8613 | -61.2762 | 60.3653 | -0.010149 | -0.02212 | 0.0088826 | 0.058573 | -0.0080188 | 0.052822 | -0.021518 | -0.002053 | -0.0029313 | 0.060183 | 0.026799 | 0.053456 | -61.2715 | 0.038035 | -61.22 | 60.2442 | 60.0255 | 60.0621 | -61.2466 | -61.2026 | 0.078197 | -61.2966 | 60.0536 | 60.204 | 60.1981 | -61.3692 | 0.029598 | -0.1211 | 0.004728 | 0.056225 | 0.026627 | -0.33981 | -0.30316 | -0.092953 | -0.31166 | 0.073678 | -0.02035 | 0.072603 | -0.16128 | -0.16724 | 121.5204 | 121.3017 | 121.3384 | 61.3143 | -121.6119 | 121.3299 | 121.4803 | 121.4743 | 61.3544 | -121.7345
406.3906 | 121.7972 | -61.3129 | 60.3516 | -0.010149 | -0.022333 | 0.0090964 | 0.058573 | -0.0078052 | 0.052822 | -0.021518 | -0.0018394 | -0.0031451 | 0.060396 | 0.026585 | 0.053456 | -61.2853 | 0.0243 | -61.22 | 60.2488 | 59.9888 | 60.0576 | -61.2421 | -61.2071 | 0.078197 | -61.292 | 60.0582 | 60.1994 | 60.2072 | -61.3692 | 0.070798 | -0.10279 | 0.027614 | 0.092846 | 0.022048 | -0.36271 | -0.294 | -0.056332 | -0.29335 | 0.10572 | 0.020849 | 0.077181 | -0.15212 | -0.14435 | 121.5616 | 121.3017 | 121.3704 | 61.3372 | -121.5936 | 121.3711 | 121.5123 | 121.5201 | 61.3911 | -121.7208
408.1562 | 121.8475 | -61.2808 | 60.3561 | -0.010149 | -0.022333 | 0.00931 | 0.058573 | -0.0073778 | 0.053249 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.027226 | 0.053242 | -61.2761 | 0.0243 | -61.2109 | 60.2488 | 60.0255 | 60.0621 | -61.2421 | -61.198 | 0.078197 | -61.2966 | 60.0536 | 60.204 | 60.2118 | -61.3646 | 0.038755 | -0.10737 | 0.004727 | 0.069959 | 0.031204 | -0.33066 | -0.294 | -0.083796 | -0.3025 | 0.082835 | -0.015772 | 0.068024 | -0.15213 | -0.14435 | 121.5296 | 121.3063 | 121.343 | 61.3051 | -121.5982 | 121.3345 | 121.4848 | 121.4926 | 61.359 | -121.7208
410.125 | 121.8979 | -61.235 | 60.3607 | -0.010149 | -0.02212 | 0.0090964 | 0.058359 | -0.0075914 | 0.052608 | -0.013887 | -0.002053 | -0.0029313 | 0.060396 | 0.026799 | 0.05367 | -61.2761 | 0.028878 | -61.2154 | 60.2488 | 60.0163 | 60.0576 | -61.2421 | -61.2026 | 0.082776 | -61.3012 | 60.0582 | 60.204 | 60.1889 | -61.3738 | -0.007022 | -0.11195 | -0.04105 | 0.019604 | 0.026626 | -0.34439 | -0.30316 | -0.13873 | -0.3025 | 0.032479 | -0.066128 | 0.072603 | -0.1567 | -0.17182 | 121.4838 | 121.2514 | 121.2926 | 61.2639 | -121.6028 | 121.2933 | 121.4391 | 121.4239 | 61.3178 | -121.7345
413.9219 | 121.8567 | -61.1938 | 60.3928 | -0.010149 | -0.022333 | 0.0088826 | 0.058359 | -0.0080188 | 0.052608 | -0.013887 | -0.0014122 | -0.0033587 | 0.060396 | 0.027012 | 0.053456 | -61.2807 | 0.028878 | -61.2154 | 60.2442 | 59.9934 | 60.0576 | -61.2466 | -61.2026 | 0.073618 | -61.3012 | 60.0582 | 60.204 | 60.2072 | -61.3784 | -0.052799 | -0.14857 | -0.086826 | -0.021594 | 0.031205 | -0.39933 | -0.3352 | -0.18451 | -0.33454 | -0.008719 | -0.10733 | 0.077182 | -0.18875 | -0.18554 | 121.438 | 121.1873 | 121.2514 | 61.2227 | -121.6394 | 121.2521 | 121.3979 | 121.4011 | 61.2675 | -121.7711
417.2656 | 121.8979 | -61.2305 | 60.3516 | -0.01778 | -0.022547 | 0.0084552 | 0.058359 | -0.0078052 | 0.053035 | -0.013887 | -0.0018394 | -0.0029313 | 0.060396 | 0.027012 | 0.053456 | -61.2853 | 0.028878 | -61.2246 | 60.2442 | 59.9934 | 60.0576 | -61.2421 | -61.2026 | 0.078197 | -61.2966 | 60.0582 | 60.1994 | 60.1981 | -61.3738 | -0.011599 | -0.10737 | -0.054783 | 0.005871 | 0.01747 | -0.35813 | -0.294 | -0.14331 | -0.29335 | 0.027902 | -0.066126 | 0.077182 | -0.15212 | -0.1535 | 121.4747 | 121.2239 | 121.288 | 61.2593 | -121.5936 | 121.2887 | 121.4299 | 121.4285 | 61.3087 | -121.7253
422.9375 | 121.9299 | -61.1755 | 60.3973 | -0.0025182 | -0.022547 | 0.008669 | 0.058573 | -0.0078052 | 0.052394 | -0.013887 | -0.0018394 | -0.0031451 | 0.060396 | 0.027012 | 0.053242 | -61.2853 | 0.0243 | -61.22 | 60.2488 | 59.9934 | 60.0621 | -61.2421 | -61.2071 | 0.073618 | -61.3012 | 60.0582 | 60.204 | 60.2026 | -61.3692 | -0.066531 | -0.14857 | -0.10972 | -0.044483 | 0.022048 | -0.40391 | -0.3352 | -0.19366 | -0.33912 | -0.031609 | -0.12564 | 0.068024 | -0.19332 | -0.1947 | 121.4243 | 121.169 | 121.2377 | 61.1998 | -121.6394 | 121.2338 | 121.3796 | 121.3782 | 61.2492 | -121.7665
424.7031 | 121.8063 | -61.235 | 60.434 | -0.0025182 | -0.022761 | 0.0088826 | 0.058359 | -0.0080188 | 0.052822 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060396 | 0.027012 | 0.053456 | -61.2853 | 0.033457 | -61.2109 | 60.2488 | 59.9934 | 60.053 | -61.2421 | -61.2026 | 0.073618 | -61.3012 | 60.0582 | 60.1994 | 60.2072 | -61.3738 | -0.007022 | -0.18519 | -0.050206 | 0.024182 | 0.031204 | -0.44053 | -0.38098 | -0.13873 | -0.37574 | 0.032479 | -0.066128 | 0.072603 | -0.23452 | -0.22674 | 121.4838 | 121.2285 | 121.288 | 61.2685 | -121.676 | 121.2933 | 121.4345 | 121.4423 | 61.3087 | -121.8077
426.4531 | 121.907 | -61.235 | 60.347 | -0.0025182 | -0.022333 | 0.0088826 | 0.058145 | -0.0080188 | 0.052608 | -0.021518 | -0.0014122 | -0.0033587 | 0.060183 | 0.026799 | 0.053456 | -61.2807 | 0.028878 | -61.22 | 60.2533 | 59.9934 | 60.0576 | -61.2375 | -61.2071 | 0.06904 | -61.292 | 60.0582 | 60.1994 | 60.2072 | -61.3646 | -0.002443 | -0.093635 | -0.045628 | 0.015026 | 0.017469 | -0.35356 | -0.28943 | -0.12957 | -0.28877 | 0.0279 | -0.056971 | 0.072602 | -0.14755 | -0.13977 | 121.4884 | 121.2285 | 121.2926 | 61.2639 | -121.5845 | 121.2933 | 121.4345 | 121.4423 | 61.3041 | -121.7116
428.2031 | 121.843 | -61.3129 | 60.347 | -0.010149 | -0.02212 | 0.0090964 | 0.058359 | -0.0078052 | 0.052608 | -0.013887 | -0.002053 | -0.0031451 | 0.060183 | 0.026799 | 0.05367 | -61.2761 | 0.033457 | -61.22 | 60.2533 | 59.9934 | 60.0667 | -61.2466 | -61.2026 | 0.073618 | -61.2966 | 60.0628 | 60.204 | 60.2118 | -61.3692 | 0.066219 | -0.093635 | 0.03677 | 0.092846 | 0.026627 | -0.35356 | -0.28027 | -0.056332 | -0.28419 | 0.1103 | 0.016271 | 0.072603 | -0.14297 | -0.13519 | 121.5662 | 121.3063 | 121.3796 | 61.3463 | -121.5936 | 121.3757 | 121.5169 | 121.5247 | 61.3865 | -121.7162
429.9375 | 121.9482 | -61.1984 | 60.3516 | -0.0025182 | -0.022547 | 0.00931 | 0.058359 | -0.0078052 | 0.052394 | -0.021518 | -0.0016258 | -0.0029313 | 0.060824 | 0.026799 | 0.053456 | -61.2807 | 0.033457 | -61.2246 | 60.2442 | 59.998 | 60.0621 | -61.2375 | -61.2071 | 0.073618 | -61.2966 | 60.0674 | 60.204 | 60.2118 | -61.3738 | -0.039064 | -0.10737 | -0.082249 | -0.026173 | 0.012891 | -0.35356 | -0.28943 | -0.17535 | -0.28419 | -0.008721 | -0.09817 | 0.077182 | -0.14755 | -0.13977 | 121.4426 | 121.1964 | 121.2606 | 61.2319 | -121.5891 | 121.2658 | 121.4024 | 121.4102 | 61.272 | -121.7253
431.6094 | 121.8338 | -61.2259 | 60.3973 | -0.0025182 | -0.022547 | 0.008669 | 0.058573 | -0.0075914 | 0.053035 | -0.0062567 | -0.0018394 | -0.0033587 | 0.060183 | 0.027012 | 0.05367 | -61.2853 | 0.0243 | -61.22 | 60.2533 | 59.998 | 60.0576 | -61.2421 | -61.2117 | 0.078197 | -61.292 | 60.0582 | 60.2086 | 60.2026 | -61.3692 | -0.016177 | -0.14399 | -0.059361 | 0.005871 | 0.022048 | -0.39933 | -0.33978 | -0.14331 | -0.33912 | 0.014167 | -0.066126 | 0.077181 | -0.18875 | -0.1947 | 121.4792 | 121.2239 | 121.2834 | 61.2502 | -121.6394 | 121.2841 | 121.4345 | 121.4285 | 61.3041 | -121.7665
433.3594 | 121.9254 | -61.2762 | 60.2783 | -0.01778 | -0.022761 | 0.0090964 | 0.058359 | -0.0080188 | 0.052822 | -0.021518 | -0.002053 | -0.0033587 | 0.059969 | 0.026799 | 0.053456 | -61.2761 | 0.028878 | -61.2154 | 60.2488 | 59.9934 | 60.0667 | -61.2375 | -61.2026 | 0.087354 | -61.2966 | 60.0628 | 60.1949 | 60.2072 | -61.3692 | 0.038756 | -0.029549 | 0.000149 | 0.060803 | 0.022047 | -0.28489 | -0.2116 | -0.092953 | -0.21552 | 0.073678 | -0.02035 | 0.072603 | -0.083462 | -0.071103 | 121.525 | 121.2697 | 121.343 | 61.3051 | -121.5158 | 121.339 | 121.4711 | 121.4835 | 61.3636 | -121.6475
435.0312 | 121.8521 | -61.2671 | 60.347 | -0.010149 | -0.022547 | 0.0088826 | 0.058145 | -0.0075914 | 0.053035 | 0.0013733 | -0.002053 | -0.0031451 | 0.060396 | 0.027226 | 0.053029 | -61.2807 | 0.028878 | -61.2154 | 60.2488 | 60.0026 | 60.0667 | -61.2421 | -61.2071 | 0.073618 | -61.3012 | 60.0491 | 60.2086 | 60.2118 | -61.3738 | 0.025022 | -0.098214 | -0.013584 | 0.051648 | 0.026626 | -0.3444 | -0.28027 | -0.10669 | -0.29793 | 0.059944 | -0.034084 | 0.072603 | -0.13839 | -0.13519 | 121.5159 | 121.2697 | 121.3338 | 61.296 | -121.5891 | 121.3161 | 121.4757 | 121.4789 | 61.3407 | -121.7208
436.7188 | 121.9528 | -61.2625 | 60.2692 | -0.01778 | -0.022761 | 0.0090964 | 0.058573 | -0.0080188 | 0.052822 | -0.013887 | -0.0018394 | -0.0033587 | 0.060396 | 0.026799 | 0.053456 | -61.2807 | 0.033457 | -61.2109 | 60.2442 | 60.0117 | 60.0621 | -61.2421 | -61.2026 | 0.073618 | -61.2966 | 60.0536 | 60.204 | 60.221 | -61.3692 | 0.020444 | -0.024972 | -0.018162 | 0.051648 | 0.031204 | -0.25742 | -0.20703 | -0.10669 | -0.21553 | 0.059945 | -0.034083 | 0.072603 | -0.06515 | -0.048213 | 121.5067 | 121.2743 | 121.3246 | 61.296 | -121.5112 | 121.3161 | 121.4665 | 121.4835 | 61.3361 | -121.6384
438.4688 | 121.9025 | -61.2213 | 60.3516 | -0.0025182 | -0.022761 | 0.008669 | 0.058145 | -0.0073778 | 0.052608 | -0.013887 | -0.0016258 | -0.0031451 | 0.060396 | 0.027226 | 0.053456 | -61.2807 | 0.028878 | -61.2154 | 60.2488 | 59.9934 | 60.0621 | -61.2421 | -61.2026 | 0.078197 | -61.3058 | 60.0582 | 60.2086 | 60.2164 | -61.3738 | -0.020755 | -0.10279 | -0.059361 | 0.005871 | 0.026626 | -0.35813 | -0.28943 | -0.15246 | -0.29335 | 0.018746 | -0.08444 | 0.068024 | -0.14297 | -0.13519 | 121.4701 | 121.2147 | 121.2835 | 61.2502 | -121.5936 | 121.2795 | 121.4299 | 121.4377 | 61.2995 | -121.7253
440.1719 | 121.9254 | -61.2534 | 60.3058 | -0.010149 | -0.022547 | 0.0088826 | 0.058359 | -0.0078052 | 0.052608 | -0.021518 | -0.0018394 | -0.0031451 | 0.060183 | 0.027226 | 0.053029 | -61.2761 | 0.028878 | -61.22 | 60.2579 | 60.0026 | 60.0621 | -61.2466 | -61.2071 | 0.078197 | -61.3012 | 60.0628 | 60.204 | 60.2164 | -61.3692 | 0.00671 | -0.047858 | -0.022739 | 0.033337 | 0.026627 | -0.3032 | -0.24365 | -0.11584 | -0.24299 | 0.046211 | -0.047817 | 0.068024 | -0.10177 | -0.089412 | 121.5113 | 121.2559 | 121.3155 | 61.2822 | -121.5524 | 121.3162 | 121.4574 | 121.4697 | 61.3316 | -121.675
441.9062 | 121.9482 | -61.2671 | 60.2829 | -0.01778 | -0.022974 | 0.008669 | 0.058359 | -0.0080188 | 0.052822 | -0.021518 | -0.002053 | -0.0031451 | 0.06061 | 0.027012 | 0.05367 | -61.2807 | 0.028878 | -61.22 | 60.2533 | 60.0255 | 60.0667 | -61.2421 | -61.2071 | 0.078197 | -61.3058 | 60.0582 | 60.2132 | 60.2118 | -61.3738 | 0.025022 | -0.029548 | -0.013584 | 0.04707 | 0.022048 | -0.25742 | -0.21618 | -0.10669 | -0.22468 | 0.059944 | -0.038663 | 0.068024 | -0.069726 | -0.071103 | 121.5204 | 121.2926 | 121.3338 | 61.296 | -121.525 | 121.3253 | 121.4803 | 121.4789 | 61.3453 | -121.6567
443.5781 | 121.8796 | -61.2167 | 60.3973 | -0.0025182 | -0.022974 | 0.0088826 | 0.058145 | -0.0080188 | 0.052608 | -0.021518 | -0.002053 | -0.0029313 | 0.060183 | 0.027226 | 0.053456 | -61.2898 | 0.0243 | -61.2246 | 60.2579 | 60.0026 | 60.0621 | -61.2375 | -61.2071 | 0.078197 | -61.3058 | 60.0674 | 60.204 | 60.2072 | -61.3738 | -0.020753 | -0.13941 | -0.073095 | -0.007862 | 0.012891 | -0.39475 | -0.3352 | -0.15704 | -0.32997 | 0.00959 | -0.089017 | 0.068024 | -0.19332 | -0.19012 | 121.4747 | 121.2193 | 121.2789 | 61.241 | -121.6348 | 121.2841 | 121.4208 | 121.424 | 61.2949 | -121.7711
445.3125 | 121.9116 | -61.1938 | 60.4019 | -0.010149 | -0.022761 | 0.0088826 | 0.058359 | -0.0078052 | 0.053035 | -0.021518 | -0.0018394 | -0.0033587 | 0.060183 | 0.027226 | 0.053242 | -61.2761 | 0.028878 | -61.2246 | 60.2442 | 59.998 | 60.0667 | -61.2375 | -61.2071 | 0.082776 | -61.3012 | 60.0536 | 60.2178 | 60.2118 | -61.3784 | -0.043641 | -0.15772 | -0.082248 | -0.03075 | 0.012891 | -0.40391 | -0.3352 | -0.18451 | -0.34828 | -0.013298 | -0.10733 | 0.077182 | -0.18417 | -0.19012 | 121.438 | 121.1919 | 121.2606 | 61.2227 | -121.6394 | 121.2475 | 121.4116 | 121.4056 | 61.2766 | -121.7803
446.9844 | 121.8292 | -61.2854 | 60.3104 | 0.0051128 | -0.022974 | 0.0090964 | 0.058359 | -0.0080188 | 0.053035 | -0.0062567 | -0.002053 | -0.0029313 | 0.060824 | 0.027012 | 0.053029 | -61.2807 | 0.028878 | -61.22 | 60.2488 | 60.0117 | 60.0667 | -61.2466 | -61.1934 | 0.082776 | -61.2966 | 60.0628 | 60.204 | 60.2072 | -61.3646 | 0.038753 | -0.061593 | 0.004726 | 0.06538 | 0.026627 | -0.29862 | -0.24365 | -0.079219 | -0.24757 | 0.09199 | -0.011195 | 0.068024 | -0.10635 | -0.10315 | 121.5342 | 121.2971 | 121.3521 | 61.3143 | -121.557 | 121.3482 | 121.4894 | 121.4926 | 61.3682 | -121.675
448.7344 | 121.7972 | -61.3449 | 60.3012 | -0.010149 | -0.022761 | 0.00931 | 0.058573 | -0.0080188 | 0.052822 | -0.013887 | -0.002053 | -0.0033587 | 0.060183 | 0.026799 | 0.053242 | -61.2761 | 0.028878 | -61.22 | 60.2488 | 60.0301 | 60.0576 | -61.2466 | -61.2026 | 0.082776 | -61.3012 | 60.0628 | 60.1994 | 60.2164 | -61.3784 | 0.098263 | -0.052437 | 0.068814 | 0.12489 | 0.026627 | -0.27115 | -0.24365 | -0.033446 | -0.23841 | 0.14234 | 0.043736 | 0.077182 | -0.10177 | -0.084834 | 121.5937 | 121.375 | 121.4025 | 61.3738 | -121.5479 | 121.4077 | 121.5443 | 121.5613 | 61.4277 | -121.6796
450.5 | 121.8567 | -61.2534 | 60.347 | -0.0025182 | -0.022974 | 0.0088826 | 0.058359 | -0.0080188 | 0.053249 | -0.021518 | -0.0018394 | -0.0027177 | 0.060396 | 0.027012 | 0.053242 | -61.2761 | 0.0243 | -61.22 | 60.2533 | 60.0026 | 60.0667 | -61.2421 | -61.2026 | 0.082776 | -61.2966 | 60.0536 | 60.1994 | 60.2118 | -61.3738 | 0.011289 | -0.093635 | -0.022739 | 0.033337 | 0.022048 | -0.3444 | -0.28027 | -0.12042 | -0.29335 | 0.05079 | -0.043238 | 0.077182 | -0.14755 | -0.13519 | 121.5067 | 121.2559 | 121.3201 | 61.2777 | -121.5891 | 121.307 | 121.4528 | 121.4652 | 61.3361 | -121.7208
452.1719 | 121.9345 | -61.2946 | 60.26 | -0.01778 | -0.022761 | 0.0088826 | 0.058786 | -0.0075914 | 0.052608 | -0.013887 | -0.0016258 | -0.0029313 | 0.060183 | 0.027226 | 0.053456 | -61.2807 | 0.028878 | -61.2109 | 60.2533 | 60.0072 | 60.0713 | -61.2421 | -61.198 | 0.082776 | -61.3012 | 60.0582 | 60.204 | 60.2072 | -61.3738 | 0.052488 | -0.00666 | 0.013882 | 0.083692 | 0.031204 | -0.25285 | -0.18872 | -0.079221 | -0.20179 | 0.096568 | -0.006618 | 0.072603 | -0.055995 | -0.052793 | 121.5479 | 121.3017 | 121.3658 | 61.3234 | -121.5021 | 121.3528 | 121.4986 | 121.5018 | 61.3773 | -121.6338
453.9062 | 121.8018 | -61.3266 | 60.3058 | -0.010149 | -0.022761 | 0.0090964 | 0.058573 | -0.0080188 | 0.052822 | -0.013887 | -0.0018394 | -0.0029313 | 0.06061 | 0.027226 | 0.053029 | -61.2715 | 0.0243 | -61.22 | 60.2579 | 60.0346 | 60.0713 | -61.2466 | -61.198 | 0.082776 | -61.292 | 60.0582 | 60.2132 | 60.2118 | -61.3738 | 0.079952 | -0.047858 | 0.055082 | 0.10658 | 0.026627 | -0.27115 | -0.23449 | -0.047178 | -0.24757 | 0.12861 | 0.034582 | 0.08176 | -0.092614 | -0.093991 | 121.5845 | 121.3612 | 121.3979 | 61.3509 | -121.5524 | 121.3848 | 121.5398 | 121.5384 | 61.4094 | -121.6796
455.6562 | 121.9116 | -61.2213 | 60.3653 | -0.0025182 | -0.023188 | 0.0088826 | 0.058573 | -0.0080188 | 0.052822 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.027226 | 0.053456 | -61.2715 | 0.038035 | -61.2246 | 60.2442 | 59.998 | 60.0713 | -61.2466 | -61.2026 | 0.078197 | -61.292 | 60.0674 | 60.204 | 60.2072 | -61.3738 | -0.025334 | -0.1211 | -0.050204 | -0.003285 | 0.022049 | -0.36729 | -0.294 | -0.15246 | -0.29792 | 0.018746 | -0.070704 | 0.08176 | -0.16128 | -0.15808 | 121.4655 | 121.2193 | 121.2926 | 61.2593 | -121.6119 | 121.2887 | 121.4253 | 121.4285 | 61.2995 | -121.7391
457.4062 | 121.8613 | -61.2808 | 60.3516 | -0.010149 | -0.022974 | 0.008669 | 0.058359 | -0.0080188 | 0.052822 | -0.021518 | -0.002053 | -0.0031451 | 0.060183 | 0.027226 | 0.05367 | -61.2761 | 0.033457 | -61.22 | 60.2625 | 60.0117 | 60.0667 | -61.2421 | -61.2026 | 0.082776 | -61.3012 | 60.0628 | 60.2132 | 60.2118 | -61.3646 | 0.038755 | -0.089056 | 0.004727 | 0.060803 | 0.022048 | -0.33982 | -0.28485 | -0.083796 | -0.28877 | 0.078256 | -0.020351 | 0.063445 | -0.13839 | -0.13977 | 121.5433 | 121.2926 | 121.3475 | 61.3143 | -121.5936 | 121.3436 | 121.494 | 121.4926 | 61.3636 | -121.7162
459.1562 | 121.9666 | -61.1801 | 60.3928 | -0.0025182 | -0.022974 | 0.0088826 | 0.058573 | -0.0075914 | 0.052822 | -0.013887 | -0.0018394 | -0.0029313 | 0.060183 | 0.027226 | 0.053242 | -61.2761 | 0.033457 | -61.2246 | 60.2533 | 60.0438 | 60.0759 | -61.2421 | -61.2071 | 0.073618 | -61.3012 | 60.0582 | 60.2086 | 60.2164 | -61.3738 | -0.061953 | -0.13941 | -0.095981 | -0.044483 | 0.01747 | -0.34896 | -0.31689 | -0.19366 | -0.33454 | -0.027031 | -0.12106 | 0.072603 | -0.18417 | -0.17639 | 121.4335 | 121.2239 | 121.256 | 61.2136 | -121.6348 | 121.2383 | 121.3887 | 121.3965 | 61.2537 | -121.7665
460.8438 | 121.8201 | -61.3037 | 60.3287 | -0.0025182 | -0.022761 | 0.0084552 | 0.058573 | -0.0080188 | 0.052822 | -0.013887 | -0.0018394 | -0.0031451 | 0.060396 | 0.027012 | 0.053242 | -61.2761 | 0.0243 | -61.2292 | 60.2579 | 60.0301 | 60.0667 | -61.2421 | -61.2071 | 0.082776 | -61.2966 | 60.0674 | 60.2132 | 60.2164 | -61.3692 | 0.061643 | -0.070746 | 0.027615 | 0.074534 | 0.012891 | -0.29861 | -0.26196 | -0.065487 | -0.2613 | 0.096565 | 0.007116 | 0.072603 | -0.1155 | -0.1123 | 121.5616 | 121.3338 | 121.3704 | 61.328 | -121.5707 | 121.3711 | 121.5169 | 121.5201 | 61.3865 | -121.6979
462.5938 | 121.9391 | -61.2671 | 60.2875 | -0.0025182 | -0.023188 | 0.0090964 | 0.058573 | -0.0080188 | 0.052608 | -0.013887 | -0.002053 | -0.0031451 | 0.060396 | 0.027012 | 0.053029 | -61.2807 | 0.033457 | -61.2154 | 60.2625 | 60.0575 | 60.0805 | -61.2375 | -61.2026 | 0.082776 | -61.3012 | 60.0536 | 60.2086 | 60.221 | -61.3646 | 0.029601 | -0.02497 | -0.013584 | 0.051648 | 0.022047 | -0.22994 | -0.20702 | -0.097529 | -0.23384 | 0.064523 | -0.034084 | 0.063445 | -0.078882 | -0.066524 | 121.5296 | 121.3246 | 121.3475 | 61.3005 | -121.525 | 121.3207 | 121.4757 | 121.488 | 61.3499 | -121.6521
464.2656 | 121.8567 | -61.203 | 60.4294 | -0.0025182 | -0.022547 | 0.0088826 | 0.058145 | -0.0082324 | 0.052608 | -0.021518 | -0.0022666 | -0.0029313 | 0.059969 | 0.027226 | 0.053242 | -61.2853 | 0.019721 | -61.22 | 60.2488 | 60.0026 | 60.0667 | -61.2421 | -61.2071 | 0.082776 | -61.3058 | 60.0582 | 60.2086 | 60.2118 | -61.3692 | -0.039065 | -0.18061 | -0.082249 | -0.017017 | 0.022048 | -0.4268 | -0.36267 | -0.16619 | -0.37117 | -0.004143 | -0.10275 | 0.063445 | -0.22079 | -0.21759 | 121.4518 | 121.2056 | 121.2697 | 61.2227 | -121.6714 | 121.2612 | 121.4116 | 121.4148 | 61.2858 | -121.7986
466.0156 | 121.8658 | -61.3083 | 60.2966 | -0.010149 | -0.023402 | 0.008669 | 0.058786 | -0.0080188 | 0.052394 | -0.021518 | -0.0018394 | -0.0031451 | 0.060183 | 0.027226 | 0.053242 | -61.2807 | 0.033457 | -61.22 | 60.2488 | 60.0117 | 60.0713 | -61.2466 | -61.1934 | 0.087354 | -61.292 | 60.0582 | 60.2086 | 60.2164 | -61.3784 | 0.061642 | -0.04786 | 0.027615 | 0.088269 | 0.026627 | -0.28489 | -0.22534 | -0.070067 | -0.23841 | 0.11488 | 0.016272 | 0.086339 | -0.088037 | -0.080257 | 121.5571 | 121.32 | 121.3796 | 61.3417 | -121.5433 | 121.3665 | 121.5169 | 121.5247 | 61.3956 | -121.675
467.7031 | 121.9437 | -61.1618 | 60.379 | -0.0025182 | -0.022974 | 0.00931 | 0.058145 | -0.0080188 | 0.052822 | -0.021518 | -0.0018394 | -0.0029313 | 0.060183 | 0.02744 | 0.053456 | -61.2761 | 0.033457 | -61.22 | 60.2488 | 60.0255 | 60.0667 | -61.2421 | -61.2071 | 0.078197 | -61.2966 | 60.0536 | 60.2086 | 60.2072 | -61.3738 | -0.080264 | -0.13026 | -0.11429 | -0.058216 | 0.022048 | -0.35355 | -0.31231 | -0.21197 | -0.32539 | -0.045342 | -0.13479 | 0.077182 | -0.17043 | -0.17181 | 121.4106 | 121.1873 | 121.2285 | 61.1953 | -121.6211 | 121.2154 | 121.3704 | 121.369 | 61.24 | -121.7528
469.4531 | 121.9574 | -61.2762 | 60.2875 | -0.010149 | -0.023188 | 0.0088826 | 0.058359 | -0.0078052 | 0.052822 | -0.021518 | -0.0022666 | -0.0031451 | 0.06061 | 0.02744 | 0.053456 | -61.2761 | 0.033457 | -61.2246 | 60.2488 | 60.0301 | 60.0621 | -61.2421 | -61.2026 | 0.082776 | -61.292 | 60.0582 | 60.2086 | 60.2072 | -61.3738 | 0.034177 | -0.038705 | 0.000149 | 0.051647 | 0.01747 | -0.25742 | -0.22534 | -0.097532 | -0.22926 | 0.073678 | -0.015772 | 0.08176 | -0.078882 | -0.080259 | 121.525 | 121.3063 | 121.3384 | 61.3097 | -121.5295 | 121.3345 | 121.4848 | 121.4835 | 61.359 | -121.6613
471.2031 | 121.907 | -61.2259 | 60.3561 | -0.0025182 | -0.023402 | 0.0088826 | 0.058359 | -0.0080188 | 0.052822 | -0.021518 | -0.0018394 | -0.0029313 | 0.060183 | 0.027226 | 0.053242 | -61.2761 | 0.0243 | -61.22 | 60.2579 | 60.0255 | 60.0759 | -61.2375 | -61.2026 | 0.087354 | -61.2874 | 60.0628 | 60.2132 | 60.2118 | -61.3738 | -0.011598 | -0.098212 | -0.050205 | 0.005871 | 0.017469 | -0.33066 | -0.28027 | -0.14789 | -0.29335 | 0.023324 | -0.061547 | 0.086339 | -0.14297 | -0.14435 | 121.4838 | 121.2514 | 121.3018 | 61.2502 | -121.5936 | 121.2887 | 121.4391 | 121.4377 | 61.3132 | -121.7299
472.9375 | 121.9345 | -61.2625 | 60.2966 | -0.01778 | -0.023188 | 0.0088826 | 0.058145 | -0.0080188 | 0.053035 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.027653 | 0.053029 | -61.2853 | 0.028878 | -61.2246 | 60.2625 | 60.0758 | 60.0713 | -61.2421 | -61.2071 | 0.087354 | -61.2966 | 60.0674 | 60.2086 | 60.2118 | -61.3738 | 0.020444 | -0.034125 | -0.02274 | 0.037914 | 0.01747 | -0.22078 | -0.22534 | -0.11126 | -0.22926 | 0.055366 | -0.034083 | 0.077182 | -0.088037 | -0.084836 | 121.525 | 121.3384 | 121.3338 | 61.2914 | -121.5387 | 121.3299 | 121.4711 | 121.4743 | 61.3499 | -121.6704
474.6719 | 121.9208 | -61.29 | 60.3104 | -0.010149 | -0.023188 | 0.0090964 | 0.058145 | -0.0080188 | 0.052608 | -0.021518 | -0.0016258 | -0.0029313 | 0.060183 | 0.027012 | 0.053456 | -61.2807 | 0.038035 | -61.2292 | 60.2579 | 60.0667 | 60.0621 | -61.2512 | -61.198 | 0.078197 | -61.3012 | 60.0628 | 60.2086 | 60.2118 | -61.3692 | 0.038752 | -0.052436 | 0.009304 | 0.060801 | 0.022049 | -0.24367 | -0.24823 | -0.07922 | -0.24757 | 0.09199 | -0.011196 | 0.068024 | -0.10177 | -0.098569 | 121.5479 | 121.3567 | 121.3521 | 61.328 | -121.5616 | 121.3528 | 121.4986 | 121.5018 | 61.3682 | -121.6796
476.3594 | 121.8567 | -61.2579 | 60.347 | -0.0025182 | -0.022974 | 0.0088826 | 0.058145 | -0.0084462 | 0.052822 | -0.0062567 | -0.002053 | -0.0035723 | 0.060183 | 0.027226 | 0.053456 | -61.2853 | 0.0243 | -61.2246 | 60.2533 | 60.0484 | 60.0713 | -61.2375 | -61.198 | 0.087354 | -61.3012 | 60.0674 | 60.2086 | 60.2118 | -61.3738 | 0.020446 | -0.093635 | -0.027317 | 0.033337 | 0.012891 | -0.29861 | -0.27569 | -0.11584 | -0.27961 | 0.059947 | -0.043239 | 0.072603 | -0.13839 | -0.13519 | 121.5113 | 121.3063 | 121.3292 | 61.2822 | -121.5845 | 121.3253 | 121.4665 | 121.4697 | 61.3453 | -121.7208
478.1094 | 121.8109 | -61.322 | 60.3287 | -0.010149 | -0.023402 | 0.0088826 | 0.058145 | -0.0086598 | 0.052822 | -0.013887 | -0.0018394 | -0.0031451 | 0.059969 | 0.027226 | 0.053029 | -61.2853 | 0.038035 | -61.2154 | 60.2625 | 60.0713 | 60.0759 | -61.2421 | -61.2026 | 0.078197 | -61.2966 | 60.0674 | 60.1994 | 60.2164 | -61.3784 | 0.079953 | -0.066168 | 0.036769 | 0.10658 | 0.026626 | -0.2574 | -0.2528 | -0.056335 | -0.2613 | 0.11945 | 0.025426 | 0.081761 | -0.12924 | -0.1123 | 121.5845 | 121.3933 | 121.3979 | 61.3601 | -121.5707 | 121.3894 | 121.5215 | 121.5384 | 61.4002 | -121.707
479.8594 | 121.9528 | -61.1755 | 60.3928 | -0.01778 | -0.023402 | 0.008669 | 0.058359 | -0.0080188 | 0.052608 | -0.013887 | -0.0018394 | -0.0033587 | 0.060183 | 0.02744 | 0.053242 | -61.2853 | 0.028878 | -61.22 | 60.2488 | 60.0484 | 60.0621 | -61.2466 | -61.2117 | 0.082776 | -61.3012 | 60.0628 | 60.2086 | 60.2072 | -61.3784 | -0.07111 | -0.14399 | -0.10972 | -0.044483 | 0.026627 | -0.34439 | -0.33062 | -0.20282 | -0.32997 | -0.036187 | -0.12564 | 0.077182 | -0.18417 | -0.18554 | 121.4243 | 121.2239 | 121.2377 | 61.2044 | -121.6394 | 121.2383 | 121.3841 | 121.3828 | 61.2583 | -121.7711
481.5469 | 121.9254 | -61.2579 | 60.2875 | -0.010149 | -0.023188 | 0.0090964 | 0.058359 | -0.0080188 | 0.052822 | -0.029148 | -0.0018394 | -0.0031451 | 0.060183 | 0.02744 | 0.053242 | -61.2807 | 0.028878 | -61.22 | 60.2533 | 60.0575 | 60.0759 | -61.2512 | -61.2117 | 0.087354 | -61.3012 | 60.0491 | 60.204 | 60.2118 | -61.3784 | 0.006709 | -0.034126 | -0.022739 | 0.037915 | 0.031206 | -0.22994 | -0.2116 | -0.12042 | -0.23842 | 0.046211 | -0.043239 | 0.077182 | -0.083461 | -0.075681 | 121.5113 | 121.3155 | 121.3338 | 61.2868 | -121.5387 | 121.307 | 121.462 | 121.4697 | 61.3453 | -121.6658
483.2969 | 121.8338 | -61.3083 | 60.3104 | -0.010149 | -0.023402 | 0.00931 | 0.058359 | -0.0082324 | 0.052608 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.027653 | 0.053242 | -61.2761 | 0.033457 | -61.22 | 60.2533 | 60.0621 | 60.0667 | -61.2466 | -61.2026 | 0.087354 | -61.2966 | 60.0628 | 60.2086 | 60.2118 | -61.3738 | 0.061642 | -0.057014 | 0.032193 | 0.088269 | 0.026627 | -0.24825 | -0.24365 | -0.065488 | -0.24757 | 0.10572 | 0.011694 | 0.077182 | -0.10177 | -0.098569 | 121.5616 | 121.3704 | 121.375 | 61.3417 | -121.557 | 121.3711 | 121.5169 | 121.5201 | 61.3956 | -121.6841
485.0469 | 121.8613 | -61.2488 | 60.3836 | 0.0051128 | -0.023402 | 0.0088826 | 0.058145 | -0.0078052 | 0.052822 | -0.029148 | -0.002053 | -0.0031451 | 0.060183 | 0.02744 | 0.053029 | -61.2853 | 0.033457 | -61.2292 | 60.2579 | 60.0484 | 60.0713 | -61.2466 | -61.2026 | 0.082776 | -61.3012 | 60.0582 | 60.204 | 60.2072 | -61.3738 | 0.002132 | -0.12568 | -0.036473 | 0.019602 | 0.01747 | -0.33523 | -0.31231 | -0.125 | -0.32539 | 0.046212 | -0.052395 | 0.072603 | -0.17959 | -0.17639 | 121.5067 | 121.2972 | 121.3201 | 61.2822 | -121.6303 | 121.307 | 121.4528 | 121.456 | 61.3316 | -121.7574
486.7344 | 121.9437 | -61.1618 | 60.4019 | -0.0025182 | -0.023402 | 0.0090964 | 0.058786 | -0.0080188 | 0.052608 | -0.013887 | -0.0016258 | -0.0029313 | 0.059755 | 0.027012 | 0.053242 | -61.2853 | 0.033457 | -61.2292 | 60.2488 | 60.0575 | 60.0759 | -61.2421 | -61.2071 | 0.078197 | -61.3012 | 60.0536 | 60.2132 | 60.2072 | -61.3784 | -0.080264 | -0.15315 | -0.12345 | -0.067373 | 0.012891 | -0.34438 | -0.32604 | -0.21655 | -0.34828 | -0.045342 | -0.13937 | 0.077182 | -0.18874 | -0.1947 | 121.4106 | 121.2193 | 121.2377 | 61.1953 | -121.644 | 121.2154 | 121.375 | 121.369 | 61.24 | -121.7803
488.4844 | 121.8109 | -61.2396 | 60.434 | -0.01778 | -0.023188 | 0.0090964 | 0.058359 | -0.0080188 | 0.052608 | -0.013887 | -0.002053 | -0.0029313 | 0.060183 | 0.027226 | 0.053242 | -61.2807 | 0.0243 | -61.22 | 60.2533 | 60.1033 | 60.0759 | -61.2421 | -61.2026 | 0.082776 | -61.2966 | 60.0582 | 60.2086 | 60.2072 | -61.3829 | -0.002444 | -0.18061 | -0.04105 | 0.019604 | 0.022048 | -0.33064 | -0.35809 | -0.14331 | -0.37574 | 0.037057 | -0.056971 | 0.08634 | -0.22537 | -0.22674 | 121.493 | 121.3429 | 121.3155 | 61.2639 | -121.676 | 121.2978 | 121.4482 | 121.4468 | 61.3224 | -121.8169
490.25 | 121.9345 | -61.1938 | 60.4202 | -0.0025182 | -0.023615 | 0.008669 | 0.058359 | -0.0082324 | 0.052822 | -0.0062567 | -0.002053 | -0.0031451 | 0.060396 | 0.027653 | 0.053242 | -61.2807 | 0.028878 | -61.22 | 60.2533 | 60.0575 | 60.0713 | -61.2375 | -61.2071 | 0.091933 | -61.3012 | 60.0628 | 60.2132 | 60.2072 | -61.3692 | -0.043641 | -0.16688 | -0.086826 | -0.026172 | 0.017469 | -0.36269 | -0.34893 | -0.17535 | -0.35743 | -0.013298 | -0.10733 | 0.068024 | -0.20705 | -0.21301 | 121.4472 | 121.2514 | 121.2651 | 61.2227 | -121.6577 | 121.2566 | 121.407 | 121.4011 | 61.2858 | -121.7894
492 | 121.8613 | -61.2076 | 60.4248 | -0.0025182 | -0.023829 | 0.0088826 | 0.058359 | -0.0082324 | 0.052822 | -0.0062567 | -0.002053 | -0.0033587 | 0.060183 | 0.027653 | 0.053242 | -61.2898 | 0.0243 | -61.2154 | 60.2579 | 60.1216 | 60.0713 | -61.2466 | -61.2026 | 0.082776 | -61.2966 | 60.0628 | 60.2178 | 60.2072 | -61.3738 | -0.039066 | -0.16688 | -0.08225 | -0.007861 | 0.031205 | -0.30317 | -0.35351 | -0.1662 | -0.36201 | 0.005014 | -0.089014 | 0.077182 | -0.20705 | -0.21759 | 121.4655 | 121.3292 | 121.2789 | 61.2319 | -121.6715 | 121.2704 | 121.4253 | 121.4148 | 61.2904 | -121.7986
493.75 | 121.8384 | -61.2122 | 60.3973 | -0.0025182 | -0.023402 | 0.0090964 | 0.058573 | -0.0078052 | 0.053035 | -0.013887 | -0.002053 | -0.0031451 | 0.060183 | 0.027867 | 0.052601 | -61.2898 | 0.028878 | -61.2246 | 60.2579 | 60.1125 | 60.0713 | -61.2466 | -61.2071 | 0.082776 | -61.292 | 60.0536 | 60.204 | 60.2164 | -61.3784 | -0.034489 | -0.13941 | -0.077673 | -0.01244 | 0.022049 | -0.28486 | -0.32605 | -0.1662 | -0.3437 | 0.005012 | -0.079859 | 0.086339 | -0.19332 | -0.18097 | 121.4701 | 121.3246 | 121.2835 | 61.241 | -121.644 | 121.2658 | 121.4162 | 121.4285 | 61.2949 | -121.7757
495.5 | 121.8109 | -61.3449 | 60.3058 | -0.010149 | -0.023615 | 0.008669 | 0.057932 | -0.0080188 | 0.052822 | -0.021518 | -0.002053 | -0.0031451 | 0.060396 | 0.027226 | 0.053456 | -61.2761 | 0.033457 | -61.2292 | 60.2625 | 60.1079 | 60.0667 | -61.2512 | -61.1934 | 0.082776 | -61.3012 | 60.0628 | 60.2132 | 60.2164 | -61.3829 | 0.093684 | -0.04328 | 0.068814 | 0.11573 | 0.022049 | -0.19788 | -0.23907 | -0.038025 | -0.24299 | 0.1515 | 0.043736 | 0.081761 | -0.092614 | -0.089412 | 121.6074 | 121.4528 | 121.4116 | 61.3784 | -121.557 | 121.4077 | 121.5581 | 121.5613 | 61.4277 | -121.6887
497.1875 | 121.8658 | -61.2671 | 60.347 | -0.0025182 | -0.023615 | 0.0088826 | 0.058145 | -0.0080188 | 0.053035 | -0.0062567 | -0.0018394 | -0.0027177 | 0.060396 | 0.027653 | 0.053242 | -61.2761 | 0.033457 | -61.2246 | 60.2579 | 60.1171 | 60.0667 | -61.2512 | -61.2071 | 0.087354 | -61.2966 | 60.0628 | 60.2132 | 60.2255 | -61.3784 | 0.015864 | -0.089057 | -0.009006 | 0.042492 | 0.026628 | -0.22993 | -0.28027 | -0.11127 | -0.28419 | 0.059944 | -0.029505 | 0.081761 | -0.13381 | -0.12145 | 121.525 | 121.3841 | 121.3338 | 61.3005 | -121.5982 | 121.3299 | 121.4803 | 121.4926 | 61.3544 | -121.7253
498.9219 | 121.8109 | -61.2213 | 60.3973 | -0.0025182 | -0.023829 | 0.0088826 | 0.058145 | -0.0080188 | 0.052822 | -0.0062567 | -0.0016258 | -0.0031451 | 0.059969 | 0.027867 | 0.053029 | -61.2761 | 0.028878 | -61.2292 | 60.2488 | 60.1216 | 60.0713 | -61.2421 | -61.2071 | 0.082776 | -61.292 | 60.0582 | 60.2132 | 60.2164 | -61.3875 | -0.020755 | -0.14857 | -0.054783 | -0.007864 | 0.012891 | -0.2757 | -0.32605 | -0.1662 | -0.33912 | 0.014167 | -0.070704 | 0.095496 | -0.18417 | -0.18097 | 121.4701 | 121.343 | 121.2926 | 61.2502 | -121.6394 | 121.2795 | 121.4345 | 121.4377 | 61.3041 | -121.7849
500.6719 | 121.9528 | -61.1847 | 60.3699 | -0.0025182 | -0.023829 | 0.0090964 | 0.057932 | -0.0073778 | 0.052822 | -0.013887 | -0.002053 | -0.0031451 | 0.060183 | 0.027653 | 0.053029 | -61.2853 | 0.028878 | -61.22 | 60.2533 | 60.085 | 60.0713 | -61.2466 | -61.2071 | 0.082776 | -61.3058 | 60.0536 | 60.2086 | 60.2118 | -61.3692 | -0.061955 | -0.11652 | -0.10056 | -0.035328 | 0.026627 | -0.28487 | -0.29858 | -0.18451 | -0.31623 | -0.022454 | -0.12106 | 0.063445 | -0.16128 | -0.15808 | 121.438 | 121.2697 | 121.256 | 61.2136 | -121.6165 | 121.2383 | 121.3933 | 121.3965 | 61.2675 | -121.7391
502.3594 | 121.8887 | -61.2396 | 60.3561 | -0.0025182 | -0.023402 | 0.0088826 | 0.058145 | -0.0080188 | 0.052608 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.02744 | 0.053242 | -61.2853 | 0.033457 | -61.2292 | 60.2579 | 60.085 | 60.0805 | -61.2375 | -61.2071 | 0.082776 | -61.2966 | 60.0582 | 60.2132 | 60.2118 | -61.3784 | 0.002135 | -0.098212 | -0.045628 | 0.010447 | 0.008312 | -0.27113 | -0.27569 | -0.13873 | -0.29792 | 0.032478 | -0.056971 | 0.081761 | -0.14297 | -0.14435 | 121.4976 | 121.3246 | 121.3201 | 61.2731 | -121.5936 | 121.2978 | 121.4528 | 121.4514 | 61.3224 | -121.7345
504.125 | 121.7926 | -61.3037 | 60.3333 | -0.010149 | -0.023615 | 0.00931 | 0.058359 | -0.0078052 | 0.053035 | 0.0013733 | -0.0018394 | -0.0029313 | 0.060183 | 0.027226 | 0.052815 | -61.2853 | 0.033457 | -61.2246 | 60.2579 | 60.1033 | 60.0759 | -61.2466 | -61.2026 | 0.082776 | -61.2966 | 60.0582 | 60.2132 | 60.2164 | -61.3784 | 0.057064 | -0.075324 | 0.018459 | 0.079113 | 0.022049 | -0.22993 | -0.25738 | -0.074645 | -0.27504 | 0.10114 | 0.007116 | 0.081761 | -0.12008 | -0.11688 | 121.5616 | 121.407 | 121.3796 | 61.3372 | -121.5799 | 121.3619 | 121.5169 | 121.5201 | 61.3865 | -121.7116
505.8125 | 121.9025 | -61.2259 | 60.3607 | -0.0025182 | -0.023615 | 0.0090964 | 0.058145 | -0.0080188 | 0.052394 | -0.021518 | -0.0022666 | -0.0031451 | 0.060396 | 0.027867 | 0.053242 | -61.2853 | 0.033457 | -61.2338 | 60.2533 | 60.0758 | 60.0713 | -61.2512 | -61.2117 | 0.087354 | -61.3058 | 60.0582 | 60.2086 | 60.2072 | -61.3738 | -0.025335 | -0.10737 | -0.059361 | -0.007864 | 0.017471 | -0.28487 | -0.28942 | -0.14789 | -0.3025 | 0.014167 | -0.079862 | 0.068024 | -0.15212 | -0.1535 | 121.4792 | 121.3017 | 121.2972 | 61.2593 | -121.6119 | 121.2841 | 121.4345 | 121.4331 | 61.3132 | -121.7345
507.5625 | 121.8109 | -61.3403 | 60.3287 | -0.01778 | -0.023829 | 0.0088826 | 0.058145 | -0.0080188 | 0.052608 | -0.021518 | -0.0018394 | -0.0035723 | 0.059969 | 0.027653 | 0.053029 | -61.2807 | 0.042614 | -61.2154 | 60.2533 | 60.0987 | 60.0759 | -61.2466 | -61.2026 | 0.087354 | -61.3012 | 60.0582 | 60.2132 | 60.2164 | -61.3738 | 0.093685 | -0.075324 | 0.059658 | 0.12489 | 0.031205 | -0.22993 | -0.2528 | -0.033445 | -0.27046 | 0.13776 | 0.039158 | 0.072603 | -0.1155 | -0.1123 | 121.5937 | 121.4391 | 121.4162 | 61.3829 | -121.5753 | 121.3985 | 121.5535 | 121.5567 | 61.4277 | -121.7025
509.2344 | 121.962 | -61.1618 | 60.3882 | -0.010149 | -0.023615 | 0.0088826 | 0.058145 | -0.0078052 | 0.052608 | -0.0062567 | -0.0016258 | -0.0029313 | 0.059969 | 0.027653 | 0.053242 | -61.2715 | 0.033457 | -61.2246 | 60.2533 | 60.0667 | 60.0713 | -61.2466 | -61.2071 | 0.078197 | -61.3012 | 60.0628 | 60.204 | 60.2118 | -61.3784 | -0.084843 | -0.13483 | -0.10971 | -0.062794 | 0.022049 | -0.32149 | -0.31689 | -0.21655 | -0.32539 | -0.045342 | -0.13937 | 0.077182 | -0.18417 | -0.17639 | 121.4152 | 121.2285 | 121.2331 | 61.1953 | -121.6348 | 121.2246 | 121.3658 | 121.3736 | 61.24 | -121.7665
510.9844 | 121.8475 | -61.2579 | 60.3699 | -0.0025182 | -0.023829 | 0.0088826 | 0.057932 | -0.0080188 | 0.052608 | -0.021518 | -0.0022666 | -0.0031451 | 0.060396 | 0.027653 | 0.053242 | -61.2807 | 0.033457 | -61.2246 | 60.2579 | 60.1079 | 60.0713 | -61.2558 | -61.2026 | 0.087354 | -61.2966 | 60.0674 | 60.2086 | 60.221 | -61.3784 | 0.00213 | -0.11194 | -0.022739 | 0.033337 | 0.031207 | -0.26197 | -0.29858 | -0.12042 | -0.3025 | 0.055368 | -0.03866 | 0.081761 | -0.16128 | -0.14892 | 121.5159 | 121.3658 | 121.3292 | 61.2914 | -121.6257 | 121.3253 | 121.4665 | 121.4789 | 61.3453 | -121.7482
512.75 | 121.8155 | -61.2305 | 60.4111 | -0.0025182 | -0.023829 | 0.0090964 | 0.058145 | -0.0080188 | 0.052608 | -0.021518 | -0.002053 | -0.0029313 | 0.059969 | 0.028081 | 0.053029 | -61.2807 | 0.033457 | -61.2246 | 60.2579 | 60.0667 | 60.0713 | -61.2421 | -61.2071 | 0.082776 | -61.3103 | 60.0628 | 60.204 | 60.2118 | -61.3784 | -0.011599 | -0.15314 | -0.050205 | 0.005871 | 0.01747 | -0.34438 | -0.33978 | -0.14789 | -0.34828 | 0.023323 | -0.079863 | 0.068024 | -0.20706 | -0.19928 | 121.4884 | 121.2972 | 121.3018 | 61.2639 | -121.6531 | 121.2933 | 121.4345 | 121.4423 | 61.3132 | -121.7894
514.4375 | 121.8292 | -61.3174 | 60.3104 | -0.010149 | -0.023615 | 0.0088826 | 0.058359 | -0.0080188 | 0.052608 | -0.021518 | -0.0016258 | -0.0031451 | 0.060183 | 0.027653 | 0.053242 | -61.2761 | 0.033457 | -61.22 | 60.2625 | 60.0987 | 60.0713 | -61.2558 | -61.2163 | 0.091933 | -61.3012 | 60.0628 | 60.2086 | 60.2164 | -61.3784 | 0.061639 | -0.047858 | 0.041348 | 0.097424 | 0.035785 | -0.21162 | -0.23907 | -0.060912 | -0.24757 | 0.10114 | 0.01627 | 0.077182 | -0.10177 | -0.09399 | 121.5799 | 121.4162 | 121.3887 | 61.3509 | -121.5662 | 121.3802 | 121.526 | 121.5338 | 61.4094 | -121.6887
516.1875 | 121.8658 | -61.3037 | 60.2737 | -0.0025182 | -0.024043 | 0.0090964 | 0.058359 | -0.0080188 | 0.052822 | -0.013887 | -0.0018394 | -0.0031451 | 0.060396 | 0.027867 | 0.053242 | -61.2853 | 0.038035 | -61.2246 | 60.2579 | 60.0667 | 60.0759 | -61.2512 | -61.198 | 0.091933 | -61.2966 | 60.0674 | 60.2132 | 60.2118 | -61.3738 | 0.052485 | -0.015815 | 0.018459 | 0.079113 | 0.026628 | -0.20705 | -0.19787 | -0.070066 | -0.20637 | 0.10572 | 0.007116 | 0.077182 | -0.060571 | -0.061948 | 121.5616 | 121.3704 | 121.3796 | 61.3417 | -121.525 | 121.3711 | 121.5169 | 121.5155 | 61.3956 | -121.6475
517.9375 | 121.9391 | -61.2579 | 60.2692 | -0.0025182 | -0.024043 | 0.0088826 | 0.058145 | -0.0078052 | 0.052394 | -0.013887 | -0.002053 | -0.0031451 | 0.060183 | 0.02744 | 0.053242 | -61.2807 | 0.033457 | -61.2246 | 60.2533 | 60.0896 | 60.0759 | -61.2466 | -61.2026 | 0.082776 | -61.3012 | 60.0628 | 60.2132 | 60.2118 | -61.3738 | 0.011288 | -0.015815 | -0.022739 | 0.033337 | 0.022049 | -0.17958 | -0.19329 | -0.11584 | -0.20637 | 0.055368 | -0.043239 | 0.072603 | -0.055993 | -0.05737 | 121.5113 | 121.3475 | 121.3338 | 61.2914 | -121.5158 | 121.3207 | 121.4711 | 121.4697 | 61.3407 | -121.6429
519.6875 | 121.8613 | -61.2808 | 60.3607 | -0.0025182 | -0.023829 | 0.0088826 | 0.058359 | -0.0080188 | 0.052822 | -0.013887 | -0.0014122 | -0.0031451 | 0.059969 | 0.027867 | 0.053029 | -61.2853 | 0.038035 | -61.2246 | 60.2579 | 60.0987 | 60.0759 | -61.2558 | -61.2071 | 0.078197 | -61.3058 | 60.0582 | 60.2086 | 60.2118 | -61.3738 | 0.025018 | -0.10279 | -0.004429 | 0.056225 | 0.031207 | -0.26197 | -0.28484 | -0.092954 | -0.3025 | 0.073677 | -0.02493 | 0.068024 | -0.15212 | -0.14892 | 121.5388 | 121.3796 | 121.3567 | 61.3189 | -121.6165 | 121.339 | 121.4894 | 121.4926 | 61.359 | -121.7345
521.375 | 121.9299 | -61.2213 | 60.379 | -0.010149 | -0.024043 | 0.0088826 | 0.058145 | -0.0080188 | 0.053035 | 0.0013733 | -0.0018394 | -0.0031451 | 0.060183 | 0.027653 | 0.053242 | -61.2853 | 0.0243 | -61.2292 | 60.2533 | 60.0621 | 60.0713 | -61.2466 | -61.198 | 0.087354 | -61.2966 | 60.0582 | 60.204 | 60.2072 | -61.3784 | -0.025334 | -0.12568 | -0.063939 | -0.007864 | 0.01747 | -0.31692 | -0.30773 | -0.15704 | -0.32081 | 0.023325 | -0.075282 | 0.081761 | -0.17501 | -0.17181 | 121.4747 | 121.2834 | 121.2926 | 61.2456 | -121.6257 | 121.2795 | 121.4253 | 121.4285 | 61.3087 | -121.7574
523.125 | 121.8658 | -61.2762 | 60.347 | -0.0025182 | -0.024043 | 0.0088826 | 0.058359 | -0.0080188 | 0.053035 | -0.013887 | -0.0018394 | -0.0029313 | 0.060396 | 0.028081 | 0.053029 | -61.2807 | 0.028878 | -61.2246 | 60.2533 | 60.1125 | 60.0713 | -61.2466 | -61.2071 | 0.073618 | -61.3058 | 60.0674 | 60.204 | 60.221 | -61.3738 | 0.029598 | -0.093635 | -0.004429 | 0.051647 | 0.022049 | -0.2345 | -0.27569 | -0.097532 | -0.27961 | 0.069099 | -0.029508 | 0.068024 | -0.14297 | -0.12603 | 121.5296 | 121.3887 | 121.3475 | 61.3051 | -121.5936 | 121.3436 | 121.4803 | 121.4972 | 61.3499 | -121.7208
524.8125 | 121.9528 | -61.171 | 60.4065 | 0.0051128 | -0.024043 | 0.008669 | 0.058359 | -0.0080188 | 0.052822 | -0.021518 | -0.002053 | -0.0027177 | 0.060183 | 0.027653 | 0.053456 | -61.2807 | 0.028878 | -61.2246 | 60.2533 | 60.1171 | 60.0805 | -61.2512 | -61.2026 | 0.078197 | -61.2966 | 60.0582 | 60.204 | 60.2118 | -61.3738 | -0.080267 | -0.15314 | -0.10971 | -0.053639 | 0.026628 | -0.28944 | -0.32604 | -0.20282 | -0.34828 | -0.031608 | -0.12564 | 0.077182 | -0.20248 | -0.1947 | 121.4243 | 121.288 | 121.2514 | 61.1998 | -121.6577 | 121.2292 | 121.375 | 121.3828 | 61.2492 | -121.7803
526.5625 | 121.8018 | -61.2991 | 60.3195 | -0.010149 | -0.024043 | 0.0090964 | 0.058573 | -0.0080188 | 0.053035 | -0.021518 | -0.002053 | -0.0027177 | 0.060396 | 0.027867 | 0.053242 | -61.2761 | 0.038035 | -61.2246 | 60.2625 | 60.0987 | 60.085 | -61.2512 | -61.2071 | 0.087354 | -61.2966 | 60.072 | 60.2132 | 60.221 | -61.3829 | 0.047907 | -0.057013 | 0.023037 | 0.074535 | 0.026628 | -0.22077 | -0.23449 | -0.083802 | -0.24757 | 0.091987 | 0.002538 | 0.08634 | -0.10635 | -0.098567 | 121.5616 | 121.3979 | 121.3842 | 61.3372 | -121.5707 | 121.3711 | 121.5123 | 121.5201 | 61.3865 | -121.7025
528.2969 | 121.9345 | -61.2717 | 60.26 | -0.01778 | -0.024043 | 0.0088826 | 0.058359 | -0.0082324 | 0.053035 | -0.0062567 | -0.0018394 | -0.0029313 | 0.060396 | 0.028081 | 0.053242 | -61.2898 | 0.038035 | -61.2246 | 60.2625 | 60.1308 | 60.0713 | -61.2466 | -61.2026 | 0.087354 | -61.2966 | 60.0628 | 60.2086 | 60.221 | -61.3738 | 0.02502 | 0.002496 | -0.018164 | 0.047069 | 0.022049 | -0.12921 | -0.18872 | -0.10211 | -0.19721 | 0.0691 | -0.024928 | 0.077182 | -0.051416 | -0.039058 | 121.5342 | 121.4025 | 121.343 | 61.3097 | -121.5067 | 121.3345 | 121.4803 | 121.4926 | 61.359 | -121.6338
529.9688 | 121.8292 | -61.2305 | 60.4431 | -0.0025182 | -0.024043 | 0.0088826 | 0.058145 | -0.0078052 | 0.052822 | -0.013887 | -0.0018394 | -0.0035723 | 0.059969 | 0.028081 | 0.053029 | -61.2853 | 0.028878 | -61.22 | 60.2533 | 60.1262 | 60.0759 | -61.2512 | -61.2071 | 0.078197 | -61.2966 | 60.0674 | 60.1994 | 60.2118 | -61.3829 | -0.020757 | -0.18977 | -0.054783 | 0.010449 | 0.031206 | -0.3169 | -0.36724 | -0.15247 | -0.37574 | 0.023323 | -0.066126 | 0.08634 | -0.24368 | -0.23132 | 121.4838 | 121.3567 | 121.3063 | 61.2593 | -121.6943 | 121.2978 | 121.4299 | 121.4423 | 61.3087 | -121.8261
531.7188 | 121.8979 | -61.2259 | 60.3516 | -0.0025182 | -0.023829 | 0.0088826 | 0.057932 | -0.0080188 | 0.052394 | -0.021518 | -0.0022666 | -0.0029313 | 0.060396 | 0.027867 | 0.053242 | -61.2853 | 0.033457 | -61.2246 | 60.2579 | 60.1125 | 60.0759 | -61.2421 | -61.2026 | 0.096512 | -61.3012 | 60.0674 | 60.2086 | 60.2118 | -61.3646 | -0.016177 | -0.093634 | -0.059361 | 0.001293 | 0.01747 | -0.23908 | -0.27569 | -0.13873 | -0.28419 | 0.023324 | -0.075283 | 0.063445 | -0.14297 | -0.13977 | 121.4838 | 121.3384 | 121.3018 | 61.2593 | -121.5936 | 121.2933 | 121.4345 | 121.4377 | 61.3224 | -121.7162
533.4531 | 121.9254 | -61.3037 | 60.2829 | -0.0025182 | -0.023829 | 0.008669 | 0.058359 | -0.0080188 | 0.052608 | -0.021518 | -0.002053 | -0.0031451 | 0.059755 | 0.027653 | 0.053029 | -61.2807 | 0.038035 | -61.2292 | 60.2533 | 60.1216 | 60.0713 | -61.2466 | -61.2071 | 0.082776 | -61.3103 | 60.0628 | 60.2086 | 60.2164 | -61.3738 | 0.057064 | -0.029548 | 0.023037 | 0.074534 | 0.01747 | -0.16126 | -0.2116 | -0.070066 | -0.2201 | 0.096565 | -0.006621 | 0.063445 | -0.074304 | -0.066524 | 121.5571 | 121.4253 | 121.375 | 61.3417 | -121.5295 | 121.3665 | 121.5123 | 121.5201 | 61.3865 | -121.6567
535.2031 | 121.8658 | -61.2671 | 60.347 | 0.0051128 | -0.024043 | 0.0090964 | 0.058573 | -0.0080188 | 0.052822 | -0.013887 | -0.0018394 | -0.0031451 | 0.060183 | 0.027867 | 0.053029 | -61.2807 | 0.038035 | -61.2338 | 60.2579 | 60.0758 | 60.0759 | -61.2466 | -61.2071 | 0.078197 | -61.292 | 60.0628 | 60.204 | 60.2164 | -61.3784 | 0.020443 | -0.089057 | -0.013584 | 0.033335 | 0.012892 | -0.27114 | -0.27111 | -0.11127 | -0.28419 | 0.059944 | -0.024927 | 0.086339 | -0.14297 | -0.13061 | 121.525 | 121.3429 | 121.343 | 61.3051 | -121.5936 | 121.3299 | 121.4711 | 121.4835 | 61.3453 | -121.7253
536.8906 | 121.9162 | -61.1847 | 60.3973 | -0.0025182 | -0.024043 | 0.008669 | 0.058359 | -0.0080188 | 0.052822 | -0.013887 | -0.0016258 | -0.0033587 | 0.06061 | 0.027653 | 0.053242 | -61.2807 | 0.033457 | -61.2246 | 60.2488 | 60.1125 | 60.0805 | -61.2466 | -61.2026 | 0.078197 | -61.3058 | 60.0628 | 60.204 | 60.2072 | -61.3875 | -0.061955 | -0.14857 | -0.095982 | -0.039906 | 0.022049 | -0.28486 | -0.31689 | -0.20282 | -0.33454 | -0.017875 | -0.12106 | 0.08176 | -0.19332 | -0.19012 | 121.4335 | 121.2972 | 121.2651 | 61.2181 | -121.644 | 121.2475 | 121.3887 | 121.3919 | 61.2629 | -121.7849
538.6406 | 121.9437 | -61.1847 | 60.4156 | -0.01778 | -0.024043 | 0.008669 | 0.058145 | -0.0080188 | 0.052608 | -0.013887 | -0.0018394 | -0.0029313 | 0.060183 | 0.028081 | 0.053242 | -61.2807 | 0.038035 | -61.2246 | 60.2533 | 60.1171 | 60.0805 | -61.2421 | -61.2163 | 0.082776 | -61.3012 | 60.0628 | 60.2086 | 60.2164 | -61.3738 | -0.057376 | -0.1623 | -0.095982 | -0.039906 | 0.01747 | -0.29859 | -0.3352 | -0.18908 | -0.35285 | -0.031611 | -0.11648 | 0.072603 | -0.20706 | -0.19928 | 121.438 | 121.3018 | 121.2651 | 61.2227 | -121.6577 | 121.2475 | 121.3933 | 121.4011 | 61.2675 | -121.7894
540.3906 | 121.8979 | -61.1938 | 60.4156 | -0.0025182 | -0.023829 | 0.008669 | 0.058145 | -0.0080188 | 0.052822 | -0.013887 | -0.002053 | -0.0031451 | 0.059969 | 0.028081 | 0.053242 | -61.2853 | 0.033457 | -61.2246 | 60.2533 | 60.0987 | 60.0759 | -61.2466 | -61.2026 | 0.078197 | -61.2966 | 60.0536 | 60.2086 | 60.2118 | -61.3784 | -0.052799 | -0.1623 | -0.091404 | -0.03075 | 0.022049 | -0.3169 | -0.33978 | -0.18451 | -0.36201 | -0.008719 | -0.10275 | 0.081761 | -0.20706 | -0.20385 | 121.4472 | 121.2926 | 121.2697 | 61.2273 | -121.6623 | 121.2475 | 121.4024 | 121.4056 | 61.272 | -121.794
542.0938 | 121.9528 | -61.1938 | 60.3928 | -0.010149 | -0.024043 | 0.0088826 | 0.057932 | -0.0082324 | 0.052822 | -0.013887 | -0.0018394 | -0.0031451 | 0.059969 | 0.027867 | 0.053242 | -61.2807 | 0.038035 | -61.2109 | 60.2533 | 60.1171 | 60.0805 | -61.2421 | -61.2026 | 0.078197 | -61.3058 | 60.0674 | 60.2132 | 60.221 | -61.3738 | -0.04822 | -0.13941 | -0.086826 | -0.017016 | 0.031204 | -0.2757 | -0.31231 | -0.17993 | -0.32539 | -0.008719 | -0.11191 | 0.068024 | -0.17959 | -0.17181 | 121.4472 | 121.3109 | 121.2743 | 61.2319 | -121.6348 | 121.2612 | 121.407 | 121.4148 | 61.272 | -121.7665
543.8438 | 121.8201 | -61.2167 | 60.3928 | 0.0051128 | -0.024256 | 0.0090964 | 0.058573 | -0.0082324 | 0.052822 | -0.013887 | -0.0018394 | -0.0029313 | 0.060396 | 0.027653 | 0.053029 | -61.2853 | 0.028878 | -61.22 | 60.2625 | 60.1216 | 60.0759 | -61.2421 | -61.2071 | 0.078197 | -61.2966 | 60.0582 | 60.2086 | 60.2164 | -61.3829 | -0.025332 | -0.13025 | -0.068516 | -0.003284 | 0.022048 | -0.27112 | -0.31689 | -0.1662 | -0.33454 | 0.00959 | -0.079859 | 0.08634 | -0.18417 | -0.17639 | 121.4792 | 121.3384 | 121.2926 | 61.2456 | -121.6348 | 121.275 | 121.4253 | 121.4331 | 61.2949 | -121.7757
545.5938 | 121.7926 | -61.3037 | 60.3012 | 0.0051128 | -0.024256 | 0.0088826 | 0.058359 | -0.0084462 | 0.052608 | -0.013887 | -0.0018394 | -0.0029313 | 0.060183 | 0.028081 | 0.052815 | -61.2807 | 0.033457 | -61.2246 | 60.2625 | 60.1354 | 60.0713 | -61.2421 | -61.2071 | 0.091933 | -61.292 | 60.0628 | 60.204 | 60.221 | -61.3738 | 0.061643 | -0.038702 | 0.023037 | 0.079113 | 0.01747 | -0.16583 | -0.22991 | -0.070066 | -0.23841 | 0.096565 | 0.011694 | 0.08176 | -0.097193 | -0.080256 | 121.5662 | 121.4391 | 121.375 | 61.3372 | -121.5433 | 121.3665 | 121.5077 | 121.5247 | 61.3956 | -121.675
547.3438 | 121.8567 | -61.2854 | 60.3378 | -0.0025182 | -0.024256 | 0.0084552 | 0.058359 | -0.0082324 | 0.053035 | -0.0062567 | -0.0018394 | -0.0027177 | 0.059969 | 0.028081 | 0.053029 | -61.2807 | 0.033457 | -61.22 | 60.2625 | 60.1216 | 60.085 | -61.2512 | -61.2026 | 0.082776 | -61.3012 | 60.0628 | 60.2086 | 60.2164 | -61.3738 | 0.034174 | -0.075324 | 0.004726 | 0.06538 | 0.031206 | -0.21619 | -0.2528 | -0.088377 | -0.27503 | 0.082833 | -0.015774 | 0.072603 | -0.12924 | -0.12146 | 121.5479 | 121.407 | 121.3704 | 61.3189 | -121.5891 | 121.3482 | 121.494 | 121.5018 | 61.3682 | -121.7116
549.0938 | 121.9391 | -61.2579 | 60.26 | -0.01778 | -0.02447 | 0.0084552 | 0.058573 | -0.0078052 | 0.052608 | -0.013887 | -0.002053 | -0.0031451 | 0.06061 | 0.028295 | 0.053456 | -61.2898 | 0.038035 | -61.22 | 60.2533 | 60.1262 | 60.085 | -61.2512 | -61.2026 | 0.087354 | -61.3058 | 60.0628 | 60.2086 | 60.2118 | -61.3692 | 0.006709 | -0.00666 | -0.031896 | 0.037915 | 0.031206 | -0.13379 | -0.17498 | -0.11126 | -0.19721 | 0.055368 | -0.047818 | 0.063445 | -0.051416 | -0.048215 | 121.5113 | 121.3842 | 121.343 | 61.296 | -121.5112 | 121.3207 | 121.4665 | 121.4697 | 61.3453 | -121.6292
550.7656 | 121.9437 | -61.1755 | 60.4111 | -0.010149 | -0.024256 | 0.008669 | 0.057932 | -0.0082324 | 0.052822 | -0.013887 | -0.002053 | -0.0033587 | 0.060396 | 0.028081 | 0.053242 | -61.2807 | 0.028878 | -61.2154 | 60.2579 | 60.1262 | 60.0896 | -61.2466 | -61.2071 | 0.073618 | -61.3012 | 60.0628 | 60.204 | 60.2072 | -61.3829 | -0.07111 | -0.15314 | -0.10514 | -0.039905 | 0.031205 | -0.28486 | -0.32146 | -0.2074 | -0.34828 | -0.031609 | -0.12564 | 0.081761 | -0.20706 | -0.20385 | 121.4335 | 121.3018 | 121.2651 | 61.2044 | -121.6577 | 121.2383 | 121.3796 | 121.3828 | 61.2492 | -121.794
552.5156 | 121.8521 | -61.29 | 60.3195 | -0.0025182 | -0.024684 | 0.008669 | 0.058573 | -0.0080188 | 0.052394 | -0.021518 | -0.0018394 | -0.0029313 | 0.060183 | 0.027867 | 0.053242 | -61.2853 | 0.038035 | -61.2246 | 60.2533 | 60.1262 | 60.085 | -61.2375 | -61.2026 | 0.082776 | -61.3012 | 60.0674 | 60.1994 | 60.221 | -61.3692 | 0.052489 | -0.066169 | 0.004726 | 0.06538 | 0.012891 | -0.1933 | -0.23449 | -0.07922 | -0.25215 | 0.087411 | -0.011196 | 0.068024 | -0.12008 | -0.098567 | 121.5433 | 121.4162 | 121.375 | 61.328 | -121.557 | 121.3574 | 121.4894 | 121.5109 | 61.3728 | -121.6887
554.2656 | 121.8109 | -61.322 | 60.3333 | -0.010149 | -0.024256 | 0.008669 | 0.058359 | -0.0080188 | 0.052181 | -0.013887 | -0.002053 | -0.0029313 | 0.060183 | 0.028081 | 0.053242 | -61.2761 | 0.038035 | -61.2154 | 60.2671 | 60.14 | 60.085 | -61.2512 | -61.2071 | 0.078197 | -61.3012 | 60.072 | 60.2086 | 60.2164 | -61.3738 | 0.070795 | -0.066167 | 0.045925 | 0.10658 | 0.035784 | -0.1933 | -0.24822 | -0.051756 | -0.2613 | 0.11487 | 0.020847 | 0.072603 | -0.12466 | -0.11688 | 121.5891 | 121.462 | 121.4071 | 61.3601 | -121.5845 | 121.394 | 121.5306 | 121.5384 | 61.4002 | -121.707
555.9531 | 121.9437 | -61.2534 | 60.2737 | -0.010149 | -0.024256 | 0.0084552 | 0.057932 | -0.0080188 | 0.052608 | -0.021518 | -0.0022666 | -0.0029313 | 0.060183 | 0.028081 | 0.053029 | -61.2853 | 0.038035 | -61.2109 | 60.2579 | 60.1308 | 60.0805 | -61.2512 | -61.2026 | 0.082776 | -61.3012 | 60.0628 | 60.2086 | 60.2255 | -61.3784 | 0.002131 | -0.015815 | -0.031895 | 0.042493 | 0.040362 | -0.14295 | -0.19329 | -0.125 | -0.21095 | 0.05079 | -0.047817 | 0.077182 | -0.065149 | -0.048212 | 121.5113 | 121.3842 | 121.3338 | 61.2914 | -121.525 | 121.3162 | 121.462 | 121.4789 | 61.3361 | -121.6521
557.7031 | 121.9116 | -61.2579 | 60.347 | -0.010149 | -0.02447 | 0.0090964 | 0.058573 | -0.0078052 | 0.052608 | -0.021518 | -0.0018394 | -0.0031451 | 0.060396 | 0.028081 | 0.052815 | -61.2761 | 0.0243 | -61.2154 | 60.2579 | 60.1308 | 60.0759 | -61.2421 | -61.198 | 0.078197 | -61.3012 | 60.0628 | 60.2178 | 60.2118 | -61.3784 | 0.015867 | -0.089057 | -0.018161 | 0.042493 | 0.026626 | -0.21619 | -0.27111 | -0.12042 | -0.28419 | 0.059947 | -0.043239 | 0.077182 | -0.12923 | -0.13519 | 121.5159 | 121.3887 | 121.3338 | 61.2822 | -121.5891 | 121.3207 | 121.4757 | 121.4697 | 61.3361 | -121.7253
559.3906 | 121.962 | -61.1664 | 60.3607 | -0.010149 | -0.024256 | 0.0088826 | 0.058359 | -0.0082324 | 0.052608 | -0.0062567 | -0.002053 | -0.0031451 | 0.060183 | 0.028081 | 0.053029 | -61.2853 | 0.028878 | -61.22 | 60.2579 | 60.1308 | 60.0805 | -61.2512 | -61.2117 | 0.082776 | -61.3058 | 60.0674 | 60.2132 | 60.2164 | -61.3738 | -0.084844 | -0.10279 | -0.11887 | -0.053638 | 0.031206 | -0.22992 | -0.28027 | -0.20739 | -0.29334 | -0.045342 | -0.13937 | 0.068024 | -0.14755 | -0.14434 | 121.4243 | 121.2972 | 121.2468 | 61.1953 | -121.6119 | 121.2338 | 121.3796 | 121.3828 | 61.2492 | -121.7345
561.1406 | 121.8796 | -61.2534 | 60.3561 | -0.0025182 | -0.024684 | 0.0084552 | 0.058145 | -0.0082324 | 0.052608 | -0.0062567 | -0.0016258 | -0.0035723 | 0.059755 | 0.028081 | 0.053242 | -61.2807 | 0.033457 | -61.22 | 60.2625 | 60.1216 | 60.0805 | -61.2421 | -61.2117 | 0.073618 | -61.3012 | 60.0628 | 60.2086 | 60.221 | -61.3784 | 0.011289 | -0.093634 | -0.027317 | 0.033337 | 0.022048 | -0.2345 | -0.27569 | -0.125 | -0.29335 | 0.041633 | -0.047817 | 0.077182 | -0.14755 | -0.13519 | 121.5159 | 121.375 | 121.3338 | 61.2868 | -121.5982 | 121.3162 | 121.462 | 121.4743 | 61.327 | -121.7345
562.875 | 121.8018 | -61.3083 | 60.3104 | -0.0025182 | -0.024256 | 0.0088826 | 0.058359 | -0.0080188 | 0.052608 | 0.0013733 | -0.002053 | -0.0029313 | 0.060396 | 0.028081 | 0.053029 | -61.2853 | 0.038035 | -61.22 | 60.2625 | 60.1308 | 60.0805 | -61.2421 | -61.2071 | 0.082776 | -61.3012 | 60.0674 | 60.2132 | 60.2164 | -61.3784 | 0.066221 | -0.047858 | 0.023037 | 0.088269 | 0.022048 | -0.17957 | -0.22991 | -0.070067 | -0.24299 | 0.10114 | 0.007115 | 0.077182 | -0.097192 | -0.09399 | 121.5708 | 121.4391 | 121.3887 | 61.3463 | -121.5524 | 121.3757 | 121.5215 | 121.5247 | 61.3911 | -121.6887
564.625 | 121.8292 | -61.3174 | 60.3195 | -0.0025182 | -0.02447 | 0.008669 | 0.057932 | -0.0082324 | 0.052822 | -0.013887 | -0.0016258 | -0.0031451 | 0.060183 | 0.028081 | 0.053242 | -61.2761 | 0.028878 | -61.2154 | 60.2671 | 60.1308 | 60.0896 | -61.2604 | -61.2026 | 0.082776 | -61.2966 | 60.0674 | 60.2178 | 60.221 | -61.3784 | 0.05706 | -0.052434 | 0.041348 | 0.102 | 0.044942 | -0.18872 | -0.22991 | -0.060912 | -0.25215 | 0.11488 | 0.020849 | 0.081761 | -0.10177 | -0.098567 | 121.5845 | 121.4482 | 121.4071 | 61.3463 | -121.5799 | 121.3848 | 121.5352 | 121.5384 | 61.4002 | -121.6979
566.375 | 121.9528 | -61.1893 | 60.3607 | -0.010149 | -0.024684 | 0.0090964 | 0.058145 | -0.0082324 | 0.052608 | -0.0062567 | -0.002053 | -0.0031451 | 0.060183 | 0.028295 | 0.053029 | -61.2898 | 0.033457 | -61.2109 | 60.2533 | 60.1262 | 60.0759 | -61.2375 | -61.2026 | 0.078197 | -61.3058 | 60.0765 | 60.2132 | 60.2118 | -61.3784 | -0.048219 | -0.10737 | -0.10056 | -0.021594 | 0.026625 | -0.2345 | -0.28484 | -0.18909 | -0.28419 | -0.013297 | -0.11648 | 0.072603 | -0.14755 | -0.14892 | 121.4426 | 121.3155 | 121.2651 | 61.2227 | -121.5982 | 121.2658 | 121.4024 | 121.4011 | 61.2675 | -121.7391
568.0625 | 121.8292 | -61.3174 | 60.3287 | -0.010149 | -0.024043 | 0.008669 | 0.057932 | -0.0078052 | 0.053035 | -0.021518 | -0.0022666 | -0.0033587 | 0.059755 | 0.028081 | 0.052815 | -61.2807 | 0.033457 | -61.22 | 60.2671 | 60.1308 | 60.0805 | -61.2558 | -61.2117 | 0.073618 | -61.2966 | 60.072 | 60.2178 | 60.221 | -61.3784 | 0.061639 | -0.061589 | 0.03677 | 0.097424 | 0.035785 | -0.19788 | -0.24822 | -0.060912 | -0.25672 | 0.10572 | 0.020849 | 0.081761 | -0.11092 | -0.10772 | 121.5845 | 121.4482 | 121.3979 | 61.3509 | -121.5845 | 121.3894 | 121.5352 | 121.5384 | 61.3911 | -121.707
569.75 | 121.8384 | -61.2442 | 60.4111 | 0.0051128 | -0.024897 | 0.0088826 | 0.058145 | -0.0084462 | 0.052608 | -0.013887 | -0.0016258 | -0.0031451 | 0.060396 | 0.028295 | 0.053029 | -61.2715 | 0.038035 | -61.2154 | 60.2625 | 60.1216 | 60.0805 | -61.2466 | -61.2117 | 0.078197 | -61.2966 | 60.072 | 60.2132 | 60.2164 | -61.3829 | -0.002445 | -0.14857 | -0.027315 | 0.02876 | 0.031205 | -0.28943 | -0.33062 | -0.13873 | -0.33912 | 0.032478 | -0.052393 | 0.08634 | -0.1979 | -0.1947 | 121.5067 | 121.3658 | 121.3247 | 61.2822 | -121.6577 | 121.3162 | 121.4574 | 121.4606 | 61.3224 | -121.794
571.5 | 121.8292 | -61.2991 | 60.2966 | -0.0025182 | -0.02447 | 0.0088826 | 0.058359 | -0.0082324 | 0.052394 | -0.021518 | -0.0016258 | -0.0031451 | 0.059969 | 0.027867 | 0.053242 | -61.2761 | 0.033457 | -61.22 | 60.2625 | 60.1216 | 60.0805 | -61.2512 | -61.2071 | 0.082776 | -61.3012 | 60.072 | 60.204 | 60.221 | -61.3784 | 0.047907 | -0.034125 | 0.023037 | 0.079113 | 0.031206 | -0.17499 | -0.21618 | -0.079223 | -0.22468 | 0.091987 | -0.002041 | 0.077182 | -0.092616 | -0.075679 | 121.5616 | 121.4208 | 121.3796 | 61.3326 | -121.5479 | 121.3711 | 121.5031 | 121.5201 | 61.3819 | -121.675
573.25 | 121.8567 | -61.3266 | 60.2783 | -0.010149 | -0.02447 | 0.0088826 | 0.058145 | -0.0082324 | 0.052608 | -0.013887 | -0.0018394 | -0.0029313 | 0.06061 | 0.028081 | 0.053456 | -61.2807 | 0.028878 | -61.2246 | 60.2625 | 60.1262 | 60.0805 | -61.2466 | -61.2071 | 0.087354 | -61.2966 | 60.0674 | 60.2132 | 60.2164 | -61.3784 | 0.079952 | -0.015814 | 0.045925 | 0.102 | 0.022049 | -0.1521 | -0.19787 | -0.051757 | -0.21095 | 0.11945 | 0.030004 | 0.081761 | -0.065148 | -0.061946 | 121.5891 | 121.4528 | 121.4071 | 61.3555 | -121.525 | 121.394 | 121.5398 | 121.543 | 61.414 | -121.6567
575 | 121.9391 | -61.171 | 60.3699 | -0.0025182 | -0.024256 | 0.0088826 | 0.058359 | -0.0084462 | 0.052822 | -0.021518 | -0.0016258 | -0.0033587 | 0.060396 | 0.028081 | 0.053029 | -61.2761 | 0.028878 | -61.2246 | 60.2579 | 60.1308 | 60.0805 | -61.2466 | -61.2071 | 0.073618 | -61.3058 | 60.0674 | 60.2132 | 60.2164 | -61.3829 | -0.075688 | -0.11194 | -0.10514 | -0.053639 | 0.022049 | -0.23908 | -0.28942 | -0.21198 | -0.3025 | -0.036187 | -0.13479 | 0.077182 | -0.1567 | -0.1535 | 121.4289 | 121.3018 | 121.2514 | 61.1998 | -121.6165 | 121.2383 | 121.3841 | 121.3873 | 61.2446 | -121.7528
576.75 | 121.8521 | -61.2534 | 60.3699 | -0.010149 | -0.024256 | 0.0088826 | 0.058145 | -0.0082324 | 0.052608 | -0.0062567 | -0.002053 | -0.0031451 | 0.060183 | 0.028508 | 0.053242 | -61.2807 | 0.033457 | -61.22 | 60.2579 | 60.1308 | 60.085 | -61.2421 | -61.2026 | 0.078197 | -61.3012 | 60.072 | 60.2086 | 60.2164 | -61.3784 | 0.011289 | -0.11194 | -0.027317 | 0.033337 | 0.022048 | -0.23908 | -0.28484 | -0.125 | -0.29792 | 0.05079 | -0.047817 | 0.077182 | -0.16128 | -0.1535 | 121.5113 | 121.3842 | 121.3384 | 61.2868 | -121.6119 | 121.3253 | 121.462 | 121.4697 | 61.3316 | -121.7482
578.4375 | 121.8933 | -61.2213 | 60.3653 | -0.010149 | -0.024897 | 0.0088826 | 0.058145 | -0.0080188 | 0.052394 | -0.0062567 | -0.0018394 | -0.0029313 | 0.060183 | 0.028081 | 0.053029 | -61.2853 | 0.033457 | -61.2246 | 60.2579 | 60.1262 | 60.0805 | -61.2466 | -61.2026 | 0.087354 | -61.3058 | 60.0674 | 60.2178 | 60.221 | -61.3829 | -0.025334 | -0.10737 | -0.063939 | -0.003285 | 0.022049 | -0.23908 | -0.28484 | -0.16162 | -0.29792 | 0.018746 | -0.08444 | 0.077182 | -0.14754 | -0.14434 | 121.4792 | 121.3475 | 121.3018 | 61.2548 | -121.6119 | 121.2887 | 121.4391 | 121.4423 | 61.3087 | -121.7482
580.1875 | 121.8704 | -61.2625 | 60.3653 | -0.0025182 | -0.024684 | 0.008669 | 0.058145 | -0.0082324 | 0.052822 | -0.013887 | -0.002053 | -0.0031451 | 0.060396 | 0.028508 | 0.053242 | -61.2807 | 0.0243 | -61.22 | 60.2533 | 60.1216 | 60.0805 | -61.2421 | -61.2026 | 0.082776 | -61.3058 | 60.0628 | 60.2132 | 60.2118 | -61.3738 | 0.020444 | -0.11195 | -0.018162 | 0.042492 | 0.022048 | -0.24366 | -0.28484 | -0.11126 | -0.3025 | 0.059945 | -0.043241 | 0.068024 | -0.15212 | -0.1535 | 121.5159 | 121.3842 | 121.343 | 61.2868 | -121.6074 | 121.3253 | 121.4757 | 121.4743 | 61.3453 | -121.7391
581.9375 | 121.843 | -61.3174 | 60.3104 | 0.0051128 | -0.024897 | 0.0088826 | 0.058145 | -0.0082324 | 0.052608 | -0.021518 | -0.002053 | -0.0029313 | 0.060183 | 0.028081 | 0.053029 | -61.2807 | 0.028878 | -61.22 | 60.2671 | 60.1216 | 60.085 | -61.2512 | -61.2071 | 0.087354 | -61.2966 | 60.072 | 60.2178 | 60.2164 | -61.3738 | 0.066218 | -0.043279 | 0.03677 | 0.097424 | 0.031206 | -0.18873 | -0.22533 | -0.056333 | -0.23841 | 0.1103 | 0.020849 | 0.077182 | -0.092613 | -0.09399 | 121.5845 | 121.4391 | 121.4025 | 61.3463 | -121.5616 | 121.3894 | 121.5352 | 121.5338 | 61.4048 | -121.6841
583.6875 | 121.8658 | -61.2122 | 60.4065 | -0.0025182 | -0.025111 | 0.0088826 | 0.058145 | -0.0082324 | 0.052608 | -0.021518 | -0.002053 | -0.0035723 | 0.059969 | 0.028295 | 0.052815 | -61.2807 | 0.038035 | -61.2246 | 60.2579 | 60.1262 | 60.0805 | -61.2512 | -61.2071 | 0.078197 | -61.3058 | 60.0674 | 60.2132 | 60.2118 | -61.3784 | -0.039068 | -0.14857 | -0.068516 | -0.01244 | 0.026628 | -0.28028 | -0.32604 | -0.1662 | -0.33912 | 0.005012 | -0.093595 | 0.072603 | -0.19332 | -0.1947 | 121.4701 | 121.3384 | 121.2926 | 61.2502 | -121.6577 | 121.2795 | 121.4253 | 121.424 | 61.2904 | -121.7849
585.3594 | 121.8292 | -61.2991 | 60.2921 | -0.010149 | -0.024684 | 0.008669 | 0.058359 | -0.0080188 | 0.052608 | -0.013887 | -0.0018394 | -0.0029313 | 0.060183 | 0.028508 | 0.053029 | -61.2853 | 0.033457 | -61.2154 | 60.2533 | 60.1262 | 60.085 | -61.2512 | -61.2071 | 0.082776 | -61.292 | 60.0674 | 60.2086 | 60.221 | -61.3784 | 0.047907 | -0.038703 | 0.013881 | 0.083691 | 0.035784 | -0.16584 | -0.20702 | -0.079223 | -0.22468 | 0.091987 | 0.007116 | 0.086339 | -0.083459 | -0.071101 | 121.5525 | 121.4253 | 121.3842 | 61.3326 | -121.5433 | 121.3665 | 121.5077 | 121.5201 | 61.3819 | -121.6704
587.1094 | 121.9299 | -61.203 | 60.3745 | -0.010149 | -0.02447 | 0.0088826 | 0.058359 | -0.0084462 | 0.052608 | -0.013887 | -0.0016258 | -0.0029313 | 0.060183 | 0.028081 | 0.053456 | -61.2761 | 0.033457 | -61.2154 | 60.2625 | 60.1216 | 60.085 | -61.2421 | -61.2117 | 0.078197 | -61.2966 | 60.0674 | 60.2178 | 60.2164 | -61.3784 | -0.039065 | -0.11194 | -0.073093 | -0.012439 | 0.026626 | -0.25281 | -0.28942 | -0.17535 | -0.30708 | -0.008721 | -0.093592 | 0.081761 | -0.1567 | -0.15808 | 121.4655 | 121.3246 | 121.288 | 61.2365 | -121.6165 | 121.2704 | 121.4208 | 121.4194 | 61.2812 | -121.7528
588.8438 | 121.9391 | -61.2717 | 60.2966 | -0.010149 | -0.024897 | 0.008669 | 0.058359 | -0.0082324 | 0.052608 | -0.029148 | -0.0018394 | -0.0031451 | 0.060183 | 0.028722 | 0.053029 | -61.2807 | 0.042614 | -61.2154 | 60.2625 | 60.1308 | 60.085 | -61.2466 | -61.198 | 0.078197 | -61.3012 | 60.072 | 60.2178 | 60.221 | -61.3784 | 0.02502 | -0.034125 | -0.009007 | 0.056225 | 0.031205 | -0.16584 | -0.2116 | -0.10669 | -0.22468 | 0.073679 | -0.029507 | 0.077182 | -0.07888 | -0.075679 | 121.5342 | 121.4025 | 121.3567 | 61.3143 | -121.5433 | 121.3436 | 121.4894 | 121.4926 | 61.3499 | -121.675
590.5781 | 121.962 | -61.1847 | 60.3745 | -0.01778 | -0.024897 | 0.0090964 | 0.058359 | -0.0082324 | 0.052608 | 0.0013733 | -0.002053 | -0.0031451 | 0.060396 | 0.028508 | 0.052815 | -61.2898 | 0.028878 | -61.2154 | 60.2579 | 60.1308 | 60.0805 | -61.2466 | -61.2071 | 0.082776 | -61.3012 | 60.072 | 60.2178 | 60.221 | -61.3784 | -0.061955 | -0.11652 | -0.10514 | -0.03075 | 0.031205 | -0.24366 | -0.294 | -0.19366 | -0.3025 | -0.022454 | -0.11648 | 0.077182 | -0.1567 | -0.1535 | 121.4426 | 121.3155 | 121.2651 | 61.2136 | -121.6211 | 121.2566 | 121.4024 | 121.4056 | 61.2675 | -121.7528
592.3281 | 121.9574 | -61.2579 | 60.2783 | -0.010149 | -0.02447 | 0.0090964 | 0.058359 | -0.0080188 | 0.052608 | -0.029148 | -0.0016258 | -0.0033587 | 0.059969 | 0.028508 | 0.053242 | -61.2853 | 0.033457 | -61.2154 | 60.2625 | 60.1354 | 60.0805 | -61.2512 | -61.2071 | 0.082776 | -61.3012 | 60.072 | 60.2086 | 60.221 | -61.3829 | 0.006709 | -0.015814 | -0.027317 | 0.042493 | 0.035784 | -0.14294 | -0.19787 | -0.125 | -0.20637 | 0.050789 | -0.043239 | 0.081761 | -0.069726 | -0.057368 | 121.5204 | 121.3933 | 121.3384 | 61.2914 | -121.5295 | 121.3299 | 121.4665 | 121.4789 | 61.3407 | -121.6613
594 | 121.8384 | -61.2122 | 60.434 | -0.0025182 | -0.024684 | 0.008669 | 0.058359 | -0.0080188 | 0.052822 | -0.013887 | -0.0018394 | -0.0031451 | 0.059969 | 0.028722 | 0.052815 | -61.2807 | 0.033457 | -61.2292 | 60.2625 | 60.1216 | 60.0942 | -61.2421 | -61.2117 | 0.078197 | -61.3058 | 60.0674 | 60.2178 | 60.2118 | -61.3784 | -0.02991 | -0.17145 | -0.068516 | -0.017019 | 0.012891 | -0.31232 | -0.33977 | -0.1662 | -0.36659 | 0.000434 | -0.093595 | 0.072603 | -0.21621 | -0.22216 | 121.4747 | 121.3338 | 121.3063 | 61.2456 | -121.676 | 121.2795 | 121.4299 | 121.424 | 61.2904 | -121.8123
595.7344 | 121.8613 | -61.2671 | 60.3836 | 0.0051128 | -0.024684 | 0.0090964 | 0.057932 | -0.0084462 | 0.052394 | -0.021518 | -0.0018394 | -0.0031451 | 0.060183 | 0.028722 | 0.052601 | -61.2807 | 0.028878 | -61.2154 | 60.2579 | 60.1262 | 60.085 | -61.2466 | -61.2026 | 0.082776 | -61.2966 | 60.0674 | 60.2132 | 60.2255 | -61.3784 | 0.020443 | -0.12568 | -0.013584 | 0.051648 | 0.031205 | -0.25739 | -0.29858 | -0.11127 | -0.31623 | 0.064523 | -0.029505 | 0.081761 | -0.17043 | -0.15808 | 121.525 | 121.3933 | 121.3521 | 61.296 | -121.6303 | 121.3345 | 121.4803 | 121.4926 | 61.3499 | -121.762
597.4219 | 121.8704 | -61.2671 | 60.3653 | -0.0025182 | -0.025325 | 0.0088826 | 0.058145 | -0.0080188 | 0.052608 | -0.021518 | -0.0022666 | -0.0033587 | 0.060183 | 0.028722 | 0.052815 | -61.2807 | 0.033457 | -61.2246 | 60.2625 | 60.1216 | 60.0713 | -61.2466 | -61.2026 | 0.078197 | -61.3012 | 60.0582 | 60.2132 | 60.2255 | -61.3784 | 0.020443 | -0.10279 | -0.013584 | 0.042492 | 0.022049 | -0.24366 | -0.294 | -0.11127 | -0.30708 | 0.064523 | -0.034084 | 0.077182 | -0.15212 | -0.13976 | 121.5296 | 121.3887 | 121.3384 | 61.3005 | -121.6119 | 121.3253 | 121.4803 | 121.4926 | 61.3453 | -121.7437
599.1562 | 121.8018 | -61.3312 | 60.3149 | -0.010149 | -0.025325 | 0.0084552 | 0.058359 | -0.0084462 | 0.052181 | -0.013887 | -0.002053 | -0.0031451 | 0.059969 | 0.028722 | 0.053029 | -61.2761 | 0.042614 | -61.22 | 60.2579 | 60.1308 | 60.0942 | -61.2512 | -61.2071 | 0.078197 | -61.2966 | 60.0674 | 60.204 | 60.2255 | -61.3829 | 0.079951 | -0.057013 | 0.055081 | 0.11116 | 0.031206 | -0.18415 | -0.22075 | -0.051758 | -0.24757 | 0.12403 | 0.034582 | 0.08634 | -0.11093 | -0.08941 | 121.5891 | 121.462 | 121.4254 | 61.3738 | -121.5662 | 121.3986 | 121.5352 | 121.5567 | 61.4094 | -121.6979
600.9062 | 121.8842 | -61.2213 | 60.3516 | -0.010149 | -0.025111 | 0.0090964 | 0.058145 | -0.0086598 | 0.052181 | -0.013887 | -0.0018394 | -0.0031451 | 0.059969 | 0.028508 | 0.053242 | -61.2761 | 0.042614 | -61.22 | 60.2579 | 60.1216 | 60.0805 | -61.2421 | -61.2071 | 0.078197 | -61.3012 | 60.0628 | 60.2132 | 60.2164 | -61.3829 | -0.020755 | -0.093634 | -0.054783 | 0.001293 | 0.022048 | -0.22992 | -0.27111 | -0.16162 | -0.28877 | 0.014167 | -0.079861 | 0.081761 | -0.13839 | -0.13519 | 121.4792 | 121.343 | 121.3018 | 61.2639 | -121.5936 | 121.2841 | 121.4345 | 121.4377 | 61.2995 | -121.7345
602.5938 | 121.8796 | -61.2396 | 60.4111 | -0.0025182 | -0.025325 | 0.0088826 | 0.058359 | -0.0084462 | 0.052608 | -0.013887 | -0.0016258 | -0.0031451 | 0.059969 | 0.028508 | 0.052815 | -61.2853 | 0.038035 | -61.2246 | 60.2625 | 60.1354 | 60.0805 | -61.2512 | -61.2026 | 0.073618 | -61.3012 | 60.0674 | 60.2086 | 60.221 | -61.3784 | -0.011602 | -0.14857 | -0.045628 | 0.015026 | 0.026628 | -0.2757 | -0.33062 | -0.13873 | -0.3437 | 0.037057 | -0.06155 | 0.077182 | -0.20248 | -0.19012 | 121.5021 | 121.375 | 121.3201 | 61.2777 | -121.6623 | 121.307 | 121.4482 | 121.4606 | 61.3132 | -121.7894
604.3281 | 121.9162 | -61.2076 | 60.379 | -0.010149 | -0.024897 | 0.0088826 | 0.058359 | -0.0084462 | 0.052608 | -0.013887 | -0.0018394 | -0.0029313 | 0.059969 | 0.028508 | 0.052815 | -61.2761 | 0.038035 | -61.2246 | 60.2717 | 60.1308 | 60.085 | -61.2466 | -61.2071 | 0.078197 | -61.3103 | 60.072 | 60.2132 | 60.2164 | -61.3738 | -0.039066 | -0.10737 | -0.068515 | -0.017017 | 0.022049 | -0.24823 | -0.294 | -0.1662 | -0.30708 | 0.000435 | -0.10275 | 0.063445 | -0.16586 | -0.16265 | 121.4792 | 121.3384 | 121.2926 | 61.2456 | -121.6257 | 121.2795 | 121.4208 | 121.424 | 61.2858 | -121.7528
606 | 121.8201 | -61.2442 | 60.434 | -0.010149 | -0.025111 | 0.0088826 | 0.058145 | -0.0084462 | 0.052608 | -0.013887 | -0.0018394 | -0.0035723 | 0.059969 | 0.028508 | 0.052815 | -61.2807 | 0.033457 | -61.2109 | 60.2625 | 60.1262 | 60.085 | -61.2512 | -61.2071 | 0.06904 | -61.3012 | 60.0628 | 60.204 | 60.2164 | -61.3784 | -0.007024 | -0.17145 | -0.036472 | 0.033338 | 0.040362 | -0.30774 | -0.34893 | -0.13415 | -0.37116 | 0.037056 | -0.056972 | 0.077182 | -0.22995 | -0.21759 | 121.5067 | 121.3704 | 121.3292 | 61.2777 | -121.6852 | 121.307 | 121.4482 | 121.4606 | 61.3132 | -121.8123
607.75 | 121.9528 | -61.2579 | 60.2829 | -0.0025182 | -0.025111 | 0.0088826 | 0.058359 | -0.0084462 | 0.052394 | -0.021518 | -0.0022666 | -0.0029313 | 0.060183 | 0.028508 | 0.052601 | -61.2761 | 0.042614 | -61.22 | 60.2579 | 60.1262 | 60.0896 | -61.2512 | -61.2117 | 0.087354 | -61.3103 | 60.072 | 60.2086 | 60.2164 | -61.3875 | 0.006709 | -0.02497 | -0.018161 | 0.037915 | 0.031206 | -0.15668 | -0.19329 | -0.12958 | -0.21095 | 0.046211 | -0.052397 | 0.077181 | -0.074304 | -0.066524 | 121.5159 | 121.3842 | 121.3475 | 61.3005 | -121.5341 | 121.3299 | 121.4665 | 121.4743 | 61.3453 | -121.6704
609.5 | 121.9299 | -61.2717 | 60.3012 | -0.0025182 | -0.025325 | 0.0088826 | 0.058359 | -0.0084462 | 0.052608 | -0.0062567 | -0.002053 | -0.0029313 | 0.060183 | 0.028508 | 0.052815 | -61.2807 | 0.038035 | -61.2338 | 60.2579 | 60.1354 | 60.085 | -61.2466 | -61.2026 | 0.082776 | -61.3058 | 60.072 | 60.2132 | 60.2255 | -61.3875 | 0.02502 | -0.04328 | -0.009007 | 0.037912 | 0.012892 | -0.16583 | -0.21618 | -0.11585 | -0.22926 | 0.0691 | -0.034086 | 0.08176 | -0.088036 | -0.075677 | 121.5296 | 121.407 | 121.3567 | 61.3097 | -121.5479 | 121.3436 | 121.4848 | 121.4972 | 61.3544 | -121.6887
611.1875 | 121.8109 | -61.3266 | 60.3058 | -0.010149 | -0.025111 | 0.0088826 | 0.058573 | -0.0084462 | 0.052608 | -0.021518 | -0.0014122 | -0.0033587 | 0.060183 | 0.028508 | 0.052815 | -61.2807 | 0.042614 | -61.2292 | 60.2671 | 60.1308 | 60.0896 | -61.2512 | -61.2026 | 0.078197 | -61.3012 | 60.0628 | 60.204 | 60.221 | -61.3738 | 0.075373 | -0.038701 | 0.045925 | 0.097422 | 0.022049 | -0.17499 | -0.21618 | -0.047178 | -0.24299 | 0.12403 | 0.025425 | 0.072603 | -0.10177 | -0.084834 | 121.5937 | 121.4574 | 121.4162 | 61.3692 | -121.557 | 121.3894 | 121.5306 | 121.5476 | 61.4048 | -121.6796
612.9375 | 121.907 | -61.2259 | 60.3745 | -0.0025182 | -0.025325 | 0.008669 | 0.058145 | -0.0084462 | 0.052394 | -0.0062567 | -0.0016258 | -0.0031451 | 0.059969 | 0.028936 | 0.052815 | -61.2807 | 0.038035 | -61.2246 | 60.2671 | 60.1308 | 60.0896 | -61.2512 | -61.198 | 0.078197 | -61.3058 | 60.072 | 60.2086 | 60.2164 | -61.3829 | -0.025335 | -0.10737 | -0.054783 | 0.001293 | 0.026628 | -0.24366 | -0.28484 | -0.15704 | -0.3025 | 0.027903 | -0.079862 | 0.077182 | -0.16586 | -0.15808 | 121.493 | 121.3567 | 121.3155 | 61.2639 | -121.6257 | 121.2978 | 121.4345 | 121.4423 | 61.3041 | -121.7574
614.6875 | 121.875 | -61.2076 | 60.4065 | -0.0025182 | -0.025111 | 0.0088826 | 0.058359 | -0.0082324 | 0.052394 | -0.0062567 | -0.002053 | -0.0031451 | 0.059755 | 0.028722 | 0.052815 | -61.2761 | 0.038035 | -61.2292 | 60.2625 | 60.1262 | 60.0896 | -61.2512 | -61.2026 | 0.082776 | -61.3058 | 60.072 | 60.2178 | 60.2118 | -61.3784 | -0.043645 | -0.14399 | -0.068515 | -0.021596 | 0.022049 | -0.28028 | -0.31688 | -0.17077 | -0.33454 | 0.005014 | -0.098172 | 0.072603 | -0.18874 | -0.1947 | 121.4701 | 121.3338 | 121.2972 | 61.2456 | -121.6577 | 121.2795 | 121.4253 | 121.4194 | 61.2904 | -121.7849
616.375 | 121.8658 | -61.3129 | 60.2783 | -0.0025182 | -0.025325 | 0.0090964 | 0.058145 | -0.0084462 | 0.052608 | -0.021518 | -0.0018394 | -0.0027177 | 0.060183 | 0.028722 | 0.052601 | -61.2761 | 0.042614 | -61.2246 | 60.2625 | 60.1262 | 60.0942 | -61.2512 | -61.2026 | 0.078197 | -61.3012 | 60.0765 | 60.2132 | 60.221 | -61.3784 | 0.06164 | -0.015814 | 0.03677 | 0.088268 | 0.026628 | -0.1521 | -0.18413 | -0.06549 | -0.20179 | 0.1103 | 0.011692 | 0.077182 | -0.065148 | -0.057368 | 121.5754 | 121.4391 | 121.4071 | 61.3555 | -121.5295 | 121.3894 | 121.526 | 121.5338 | 61.3911 | -121.6567
618.125 | 121.9345 | -61.1755 | 60.3836 | -0.0025182 | -0.025111 | 0.008669 | 0.058359 | -0.0084462 | 0.052608 | -0.013887 | -0.002053 | -0.0029313 | 0.060183 | 0.028936 | 0.052601 | -61.2715 | 0.038035 | -61.2292 | 60.2579 | 60.1308 | 60.0896 | -61.2558 | -61.2117 | 0.078197 | -61.3058 | 60.0628 | 60.2132 | 60.2164 | -61.3829 | -0.080268 | -0.12568 | -0.09598 | -0.05364 | 0.026628 | -0.25281 | -0.294 | -0.2074 | -0.32081 | -0.036187 | -0.13022 | 0.077182 | -0.17043 | -0.16723 | 121.4335 | 121.3063 | 121.2651 | 61.2136 | -121.6394 | 121.2383 | 121.3887 | 121.3919 | 61.2537 | -121.7665
619.8125 | 121.907 | -61.2213 | 60.3516 | -0.0025182 | -0.025111 | 0.0090964 | 0.058359 | -0.0082324 | 0.052394 | -0.013887 | -0.002053 | -0.0031451 | 0.059969 | 0.028722 | 0.052601 | -61.2853 | 0.042614 | -61.2292 | 60.2625 | 60.1354 | 60.085 | -61.2512 | -61.2026 | 0.082776 | -61.3012 | 60.0674 | 60.2132 | 60.221 | -61.3829 | -0.029913 | -0.089056 | -0.063939 | -0.007864 | 0.022049 | -0.21619 | -0.26653 | -0.16162 | -0.28419 | 0.018746 | -0.079861 | 0.081761 | -0.13839 | -0.13061 | 121.4838 | 121.3567 | 121.3063 | 61.2639 | -121.6028 | 121.2887 | 121.4345 | 121.4423 | 61.3041 | -121.7345
621.5625 | 121.8018 | -61.3449 | 60.3149 | -0.0025182 | -0.025111 | 0.0090964 | 0.057932 | -0.0080188 | 0.052394 | -0.013887 | -0.0016258 | -0.0031451 | 0.059969 | 0.028508 | 0.052601 | -61.2853 | 0.028878 | -61.2292 | 60.2671 | 60.1354 | 60.0896 | -61.2466 | -61.2117 | 0.078197 | -61.2966 | 60.072 | 60.2132 | 60.2255 | -61.3784 | 0.098263 | -0.047856 | 0.059658 | 0.11573 | 0.01747 | -0.17957 | -0.22533 | -0.033446 | -0.24299 | 0.13319 | 0.048315 | 0.081761 | -0.10177 | -0.08941 | 121.612 | 121.4803 | 121.4345 | 61.3738 | -121.5616 | 121.4169 | 121.5581 | 121.5704 | 61.4231 | -121.6933
623.25 | 121.7972 | -61.3358 | 60.3149 | -0.010149 | -0.025111 | 0.0090964 | 0.057932 | -0.0084462 | 0.052394 | -0.021518 | -0.002053 | -0.0031451 | 0.060183 | 0.028936 | 0.052815 | -61.2761 | 0.042614 | -61.2338 | 60.2671 | 60.14 | 60.0896 | -61.2421 | -61.2026 | 0.082776 | -61.3012 | 60.0674 | 60.2178 | 60.2255 | -61.3875 | 0.093686 | -0.047856 | 0.059658 | 0.102 | 0.008313 | -0.17499 | -0.22533 | -0.051759 | -0.24757 | 0.13319 | 0.03458 | 0.086339 | -0.09719 | -0.08941 | 121.6028 | 121.4757 | 121.4254 | 61.3784 | -121.557 | 121.4031 | 121.5535 | 121.5613 | 61.4185 | -121.7025
624.9375 | 121.962 | -61.203 | 60.3836 | -0.010149 | -0.025538 | 0.0090964 | 0.058145 | -0.0084462 | 0.052394 | -0.021518 | -0.0016258 | -0.0033587 | 0.059969 | 0.028936 | 0.053029 | -61.2853 | 0.042614 | -61.2338 | 60.2625 | 60.1216 | 60.0896 | -61.2421 | -61.2071 | 0.082776 | -61.3012 | 60.072 | 60.2132 | 60.2164 | -61.3784 | -0.039065 | -0.1211 | -0.082249 | -0.030752 | 0.008313 | -0.26197 | -0.294 | -0.17535 | -0.31165 | -0.004143 | -0.098171 | 0.077182 | -0.17043 | -0.16723 | 121.4655 | 121.3246 | 121.2926 | 61.2456 | -121.6257 | 121.275 | 121.4162 | 121.4194 | 61.2858 | -121.762
626.6875 | 121.9391 | -61.1893 | 60.3928 | -0.010149 | -0.025538 | 0.0088826 | 0.058359 | -0.0088734 | 0.052608 | -0.013887 | -0.0018394 | -0.0031451 | 0.060183 | 0.028936 | 0.052815 | -61.2853 | 0.042614 | -61.2338 | 60.2625 | 60.1308 | 60.0896 | -61.2512 | -61.2071 | 0.073618 | -61.3058 | 60.0674 | 60.2086 | 60.2255 | -61.3829 | -0.061956 | -0.13025 | -0.095982 | -0.044485 | 0.017471 | -0.26197 | -0.30315 | -0.19367 | -0.32539 | -0.017876 | -0.11648 | 0.077182 | -0.18417 | -0.16723 | 121.4518 | 121.3201 | 121.2789 | 61.2319 | -121.644 | 121.2566 | 121.3979 | 121.4148 | 61.2629 | -121.7757
628.375 | 121.9208 | -61.2488 | 60.3241 | -0.010149 | -0.025325 | 0.0088826 | 0.058359 | -0.0084462 | 0.052608 | -0.013887 | -0.0016258 | -0.0033587 | 0.059969 | 0.028722 | 0.052388 | -61.2807 | 0.042614 | -61.2292 | 60.2579 | 60.1354 | 60.0942 | -61.2512 | -61.2026 | 0.078197 | -61.3058 | 60.072 | 60.2086 | 60.2255 | -61.3784 | -0.002447 | -0.066169 | -0.031895 | 0.019602 | 0.022049 | -0.18872 | -0.22991 | -0.12958 | -0.25214 | 0.046212 | -0.056974 | 0.072603 | -0.1155 | -0.098566 | 121.5067 | 121.3842 | 121.343 | 61.2914 | -121.5753 | 121.3207 | 121.4574 | 121.4743 | 61.327 | -121.7025
630.125 | 121.9482 | -61.171 | 60.3836 | -0.0025182 | -0.025325 | 0.008669 | 0.058145 | -0.0084462 | 0.052608 | -0.021518 | -0.0016258 | -0.0029313 | 0.060396 | 0.029149 | 0.053029 | -61.2761 | 0.038035 | -61.2338 | 60.2579 | 60.14 | 60.0942 | -61.2466 | -61.2117 | 0.073618 | -61.3103 | 60.0674 | 60.2178 | 60.221 | -61.3738 | -0.075688 | -0.12568 | -0.10514 | -0.062796 | 0.012892 | -0.24365 | -0.28942 | -0.20282 | -0.31623 | -0.040765 | -0.13937 | 0.063445 | -0.16586 | -0.16265 | 121.4289 | 121.3109 | 121.2651 | 61.209 | -121.6303 | 121.2383 | 121.3887 | 121.3919 | 61.2446 | -121.7574
631.8125 | 121.8109 | -61.322 | 60.3378 | -0.0025182 | -0.025325 | 0.008669 | 0.058145 | -0.0082324 | 0.052394 | -0.021518 | -0.002053 | -0.0031451 | 0.060183 | 0.028936 | 0.053242 | -61.2807 | 0.042614 | -61.2292 | 60.2625 | 60.1308 | 60.0896 | -61.2512 | -61.2026 | 0.082776 | -61.3058 | 60.072 | 60.2132 | 60.221 | -61.3875 | 0.070795 | -0.075324 | 0.041347 | 0.092844 | 0.022049 | -0.20703 | -0.24822 | -0.065492 | -0.26588 | 0.11945 | 0.016268 | 0.08176 | -0.12466 | -0.11688 | 121.5845 | 121.4528 | 121.4116 | 61.3646 | -121.5891 | 121.394 | 121.5352 | 121.543 | 61.4048 | -121.7253
633.5625 | 121.8155 | -61.3174 | 60.3378 | -0.0025182 | -0.025111 | 0.0088826 | 0.057932 | -0.0084462 | 0.052181 | -0.021518 | -0.0018394 | -0.0031451 | 0.06061 | 0.028508 | 0.053029 | -61.2761 | 0.047193 | -61.2292 | 60.2625 | 60.1354 | 60.0988 | -61.2558 | -61.2071 | 0.073618 | -61.3012 | 60.072 | 60.2132 | 60.2347 | -61.3829 | 0.061639 | -0.075324 | 0.041348 | 0.088267 | 0.026628 | -0.20245 | -0.23906 | -0.065491 | -0.26588 | 0.1103 | 0.01627 | 0.081761 | -0.12466 | -0.10314 | 121.5799 | 121.4528 | 121.4162 | 61.3646 | -121.5936 | 121.3894 | 121.5306 | 121.5521 | 61.3911 | -121.7208
635.25 | 121.8933 | -61.235 | 60.3699 | -0.010149 | -0.025538 | 0.008669 | 0.058145 | -0.0082324 | 0.052181 | -0.013887 | -0.0018394 | -0.0027177 | 0.060396 | 0.028508 | 0.053029 | -61.2807 | 0.038035 | -61.2246 | 60.2579 | 60.1354 | 60.085 | -61.2512 | -61.2117 | 0.06904 | -61.3012 | 60.0765 | 60.2178 | 60.221 | -61.3829 | -0.01618 | -0.11194 | -0.045628 | 0.010448 | 0.026628 | -0.2345 | -0.28484 | -0.14789 | -0.29334 | 0.023322 | -0.066128 | 0.081761 | -0.15212 | -0.14892 | 121.493 | 121.3704 | 121.3201 | 61.2731 | -121.6211 | 121.3116 | 121.4528 | 121.456 | 61.3041 | -121.7528
637 | 121.9116 | -61.2488 | 60.3104 | -0.010149 | -0.025538 | 0.008669 | 0.058359 | -0.0084462 | 0.052394 | -0.013887 | -0.0018394 | -0.0029313 | 0.059755 | 0.028508 | 0.052815 | -61.2807 | 0.05635 | -61.2338 | 60.2671 | 60.1308 | 60.0896 | -61.2421 | -61.2026 | 0.078197 | -61.3012 | 60.0628 | 60.2178 | 60.221 | -61.3829 | 0.006711 | -0.043279 | -0.031895 | 0.015024 | 0.008313 | -0.17957 | -0.22075 | -0.13416 | -0.24757 | 0.046212 | -0.052395 | 0.081761 | -0.092613 | -0.089412 | 121.5159 | 121.3796 | 121.3384 | 61.3051 | -121.5524 | 121.3116 | 121.4665 | 121.4697 | 61.327 | -121.6933
638.7656 | 121.875 | -61.2854 | 60.347 | 0.0051128 | -0.025325 | 0.0088826 | 0.058145 | -0.0086598 | 0.052822 | -0.021518 | -0.0018394 | -0.0033587 | 0.060183 | 0.028936 | 0.053029 | -61.2807 | 0.042614 | -61.2338 | 60.2625 | 60.1308 | 60.085 | -61.2512 | -61.2026 | 0.073618 | -61.3012 | 60.072 | 60.2132 | 60.2164 | -61.3829 | 0.034174 | -0.084479 | 0.004726 | 0.051645 | 0.017471 | -0.21619 | -0.26195 | -0.097535 | -0.27503 | 0.082833 | -0.015774 | 0.081761 | -0.13381 | -0.13061 | 121.5479 | 121.4162 | 121.3704 | 61.328 | -121.5982 | 121.3574 | 121.4986 | 121.5018 | 61.359 | -121.7299
640.4375 | 121.9345 | -61.2762 | 60.2783 | -0.025411 | -0.024897 | 0.0090964 | 0.058359 | -0.0084462 | 0.052181 | -0.021518 | -0.002053 | -0.0029313 | 0.060183 | 0.029149 | 0.053029 | -61.2807 | 0.042614 | -61.2292 | 60.2625 | 60.1354 | 60.0942 | -61.2558 | -61.2071 | 0.078197 | -61.3058 | 60.072 | 60.2086 | 60.2255 | -61.3875 | 0.02044 | -0.015814 | -0.004429 | 0.047068 | 0.026628 | -0.14294 | -0.18413 | -0.11127 | -0.20637 | 0.069099 | -0.029508 | 0.08176 | -0.069726 | -0.052789 | 121.5388 | 121.4116 | 121.3704 | 61.3189 | -121.5341 | 121.3482 | 121.4848 | 121.5018 | 61.3544 | -121.6658
642.1875 | 121.907 | -61.2213 | 60.3241 | -0.0025182 | -0.025538 | 0.0084552 | 0.058145 | -0.0084462 | 0.052181 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.028722 | 0.052601 | -61.2853 | 0.042614 | -61.2338 | 60.2579 | 60.14 | 60.0988 | -61.2466 | -61.2071 | 0.073618 | -61.3012 | 60.072 | 60.2086 | 60.2164 | -61.3784 | -0.025334 | -0.066169 | -0.063939 | -0.012442 | 0.012892 | -0.18414 | -0.22533 | -0.15704 | -0.25214 | 0.014167 | -0.079861 | 0.077182 | -0.1155 | -0.10772 | 121.4792 | 121.3613 | 121.3201 | 61.2639 | -121.5707 | 121.2933 | 121.4299 | 121.4377 | 61.2949 | -121.7025
643.875 | 121.8796 | -61.2854 | 60.3836 | -0.010149 | -0.025538 | 0.0088826 | 0.058359 | -0.0084462 | 0.052608 | -0.021518 | -0.0016258 | -0.0033587 | 0.060396 | 0.029149 | 0.053029 | -61.2807 | 0.047193 | -61.2292 | 60.2625 | 60.1354 | 60.0896 | -61.2604 | -61.2026 | 0.06904 | -61.3058 | 60.0628 | 60.2132 | 60.2255 | -61.3875 | 0.025016 | -0.1211 | 0.004726 | 0.056223 | 0.031207 | -0.24823 | -0.294 | -0.10211 | -0.32081 | 0.082833 | -0.020353 | 0.08176 | -0.17043 | -0.15808 | 121.5479 | 121.4208 | 121.375 | 61.3326 | -121.644 | 121.3482 | 121.4986 | 121.5109 | 61.3544 | -121.7711
645.625 | 121.8338 | -61.2534 | 60.3973 | -0.01778 | -0.025966 | 0.0090964 | 0.058145 | -0.0084462 | 0.052608 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.029149 | 0.052388 | -61.2761 | 0.042614 | -61.2292 | 60.2671 | 60.14 | 60.0896 | -61.2466 | -61.2026 | 0.073618 | -61.3012 | 60.0674 | 60.204 | 60.2255 | -61.3784 | 0.00671 | -0.13025 | -0.022739 | 0.02418 | 0.01747 | -0.25738 | -0.30773 | -0.125 | -0.32997 | 0.05079 | -0.047817 | 0.077182 | -0.19332 | -0.17181 | 121.5204 | 121.3933 | 121.343 | 61.296 | -121.644 | 121.3207 | 121.4574 | 121.4789 | 61.327 | -121.7757
647.3125 | 121.8887 | -61.2122 | 60.4202 | -0.010149 | -0.025752 | 0.0090964 | 0.058359 | -0.0086598 | 0.052394 | -0.0062567 | -0.002053 | -0.0031451 | 0.059969 | 0.028936 | 0.052601 | -61.2807 | 0.038035 | -61.2246 | 60.2579 | 60.1308 | 60.0942 | -61.2512 | -61.2163 | 0.073618 | -61.3012 | 60.072 | 60.2132 | 60.2164 | -61.3829 | -0.039068 | -0.1623 | -0.068516 | -0.01244 | 0.026628 | -0.28943 | -0.32604 | -0.17078 | -0.34827 | -0.004145 | -0.089016 | 0.081761 | -0.20705 | -0.20385 | 121.4701 | 121.343 | 121.3063 | 61.2502 | -121.6715 | 121.2841 | 121.4253 | 121.4285 | 61.2858 | -121.8032
649.0625 | 121.7926 | -61.3266 | 60.3012 | 0.0051128 | -0.025325 | 0.0088826 | 0.057932 | -0.0090872 | 0.052181 | -0.0062567 | -0.0018394 | -0.0031451 | 0.059969 | 0.028936 | 0.053029 | -61.2761 | 0.042614 | -61.2338 | 60.2671 | 60.14 | 60.0896 | -61.2512 | -61.2071 | 0.073618 | -61.3012 | 60.0674 | 60.2086 | 60.2255 | -61.3875 | 0.075373 | -0.034123 | 0.050503 | 0.092844 | 0.017471 | -0.16125 | -0.2116 | -0.060914 | -0.23383 | 0.11945 | 0.025425 | 0.086339 | -0.092614 | -0.075677 | 121.5937 | 121.4666 | 121.4162 | 61.3692 | -121.5524 | 121.394 | 121.5352 | 121.5521 | 61.4002 | -121.6887
650.8125 | 121.8018 | -61.2991 | 60.3287 | -0.0025182 | -0.025325 | 0.0088826 | 0.058573 | -0.0086598 | 0.052608 | 0.0013733 | -0.002053 | -0.0029313 | 0.060183 | 0.028722 | 0.052601 | -61.2853 | 0.047193 | -61.2292 | 60.2671 | 60.1354 | 60.0942 | -61.2512 | -61.2071 | 0.073618 | -61.3012 | 60.0628 | 60.2132 | 60.2255 | -61.3875 | 0.047907 | -0.061589 | 0.013881 | 0.069956 | 0.022049 | -0.1933 | -0.23449 | -0.08838 | -0.26588 | 0.091987 | -0.002041 | 0.086339 | -0.1155 | -0.10314 | 121.5662 | 121.4345 | 121.3933 | 61.3463 | -121.5799 | 121.3619 | 121.5123 | 121.5247 | 61.3728 | -121.7162
652.5156 | 121.9025 | -61.2305 | 60.347 | -0.010149 | -0.025752 | 0.0090964 | 0.057932 | -0.0082324 | 0.052394 | -0.013887 | -0.0016258 | -0.0033587 | 0.059969 | 0.029363 | 0.052815 | -61.2761 | 0.042614 | -61.2338 | 60.2671 | 60.1354 | 60.0942 | -61.2512 | -61.2026 | 0.064461 | -61.2966 | 60.072 | 60.2178 | 60.221 | -61.3829 | -0.020757 | -0.0799 | -0.045627 | -0.003286 | 0.017471 | -0.21161 | -0.2528 | -0.15247 | -0.27503 | 0.027902 | -0.066126 | 0.08634 | -0.12923 | -0.12603 | 121.4976 | 121.3658 | 121.3247 | 61.2731 | -121.5982 | 121.3024 | 121.4482 | 121.4514 | 61.2949 | -121.7299
654.25 | 121.962 | -61.1984 | 60.3973 | -0.010149 | -0.025538 | 0.0088826 | 0.058359 | -0.0082324 | 0.052394 | -0.013887 | -0.0016258 | -0.0029313 | 0.059969 | 0.028936 | 0.052601 | -61.2853 | 0.042614 | -61.2383 | 60.2625 | 60.1354 | 60.1033 | -61.2466 | -61.2071 | 0.073618 | -61.3058 | 60.072 | 60.2086 | 60.2301 | -61.3875 | -0.048222 | -0.13483 | -0.086827 | -0.039908 | 0.008314 | -0.26196 | -0.29399 | -0.18909 | -0.32539 | -0.008721 | -0.10733 | 0.08176 | -0.18875 | -0.16723 | 121.4609 | 121.3338 | 121.3018 | 61.241 | -121.644 | 121.2704 | 121.407 | 121.4285 | 61.272 | -121.7849
655.9219 | 121.8567 | -61.2579 | 60.3424 | -0.010149 | -0.025538 | 0.008669 | 0.058359 | -0.0086598 | 0.052394 | 0.0013733 | -0.0016258 | -0.0031451 | 0.059969 | 0.029149 | 0.052815 | -61.2761 | 0.051771 | -61.2429 | 60.2671 | 60.1308 | 60.0896 | -61.2558 | -61.2071 | 0.064461 | -61.2966 | 60.0674 | 60.2132 | 60.2255 | -61.3784 | 0.00213 | -0.075322 | -0.018161 | 0.015023 | 0.012893 | -0.21161 | -0.2528 | -0.12042 | -0.27503 | 0.050789 | -0.03866 | 0.081761 | -0.12924 | -0.11688 | 121.525 | 121.3887 | 121.3475 | 61.3097 | -121.5982 | 121.3253 | 121.4711 | 121.4835 | 61.3224 | -121.7208
657.6562 | 121.7972 | -61.3174 | 60.3149 | -0.010149 | -0.025538 | 0.0088826 | 0.058145 | -0.0086598 | 0.052608 | -0.021518 | -0.002053 | -0.0029313 | 0.060183 | 0.029149 | 0.052601 | -61.2761 | 0.042614 | -61.2292 | 60.2671 | 60.1445 | 60.0988 | -61.2512 | -61.2071 | 0.073618 | -61.2966 | 60.0674 | 60.2178 | 60.221 | -61.3829 | 0.066218 | -0.047856 | 0.041348 | 0.088267 | 0.022049 | -0.17041 | -0.21617 | -0.065491 | -0.24757 | 0.1103 | 0.020849 | 0.08634 | -0.09719 | -0.093989 | 121.5845 | 121.462 | 121.4162 | 61.3601 | -121.5662 | 121.3848 | 121.5352 | 121.5384 | 61.3911 | -121.6979
659.3438 | 121.8933 | -61.2442 | 60.3745 | -0.01778 | -0.025966 | 0.0088826 | 0.058359 | -0.0084462 | 0.052608 | -0.029148 | -0.002053 | -0.0031451 | 0.059542 | 0.028936 | 0.052601 | -61.2853 | 0.042614 | -61.2292 | 60.2625 | 60.1354 | 60.0988 | -61.2558 | -61.2117 | 0.073618 | -61.3103 | 60.072 | 60.2086 | 60.2255 | -61.3829 | -0.011603 | -0.11194 | -0.04105 | 0.015025 | 0.026628 | -0.23908 | -0.27569 | -0.13873 | -0.3025 | 0.032478 | -0.06613 | 0.072603 | -0.16586 | -0.14892 | 121.5067 | 121.3796 | 121.343 | 61.2868 | -121.6303 | 121.3162 | 121.4528 | 121.4697 | 61.3178 | -121.7574
661.0781 | 121.9162 | -61.2488 | 60.3745 | -0.01778 | -0.025966 | 0.0088826 | 0.058359 | -0.0082324 | 0.052181 | -0.013887 | -0.0016258 | -0.0033587 | 0.059969 | 0.028936 | 0.052815 | -61.2853 | 0.038035 | -61.2292 | 60.2671 | 60.14 | 60.0942 | -61.2421 | -61.2117 | 0.078197 | -61.3012 | 60.0674 | 60.2132 | 60.2255 | -61.3875 | 0.006711 | -0.10737 | -0.036473 | 0.019602 | 0.012891 | -0.2345 | -0.28026 | -0.13873 | -0.30708 | 0.037055 | -0.052395 | 0.086339 | -0.16128 | -0.14892 | 121.5159 | 121.3887 | 121.343 | 61.2868 | -121.6165 | 121.3162 | 121.462 | 121.4743 | 61.327 | -121.762
662.8438 | 121.8246 | -61.3358 | 60.3058 | -0.010149 | -0.025752 | 0.008669 | 0.058573 | -0.0088734 | 0.052608 | -0.013887 | -0.002053 | -0.0033587 | 0.059969 | 0.028722 | 0.052815 | -61.2853 | 0.038035 | -61.2383 | 60.2579 | 60.14 | 60.0988 | -61.2558 | -61.2117 | 0.073618 | -61.3058 | 60.072 | 60.2086 | 60.2255 | -61.3875 | 0.079949 | -0.047858 | 0.050502 | 0.097421 | 0.017472 | -0.16583 | -0.20702 | -0.051759 | -0.23383 | 0.12403 | 0.030001 | 0.08176 | -0.097192 | -0.080255 | 121.5937 | 121.4757 | 121.4345 | 61.3738 | -121.5616 | 121.4077 | 121.5443 | 121.5613 | 61.4094 | -121.6933
664.5156 | 121.962 | -61.2122 | 60.4019 | -0.010149 | -0.026179 | 0.0088826 | 0.057718 | -0.0086598 | 0.052181 | -0.013887 | -0.0016258 | -0.0033587 | 0.060183 | 0.029149 | 0.052815 | -61.2761 | 0.038035 | -61.2338 | 60.2671 | 60.14 | 60.0942 | -61.2466 | -61.2117 | 0.078197 | -61.3103 | 60.0628 | 60.2178 | 60.2164 | -61.3829 | -0.034489 | -0.13483 | -0.063938 | -0.021597 | 0.012892 | -0.26196 | -0.30773 | -0.17078 | -0.33912 | 0.000434 | -0.098174 | 0.072603 | -0.18417 | -0.18554 | 121.4792 | 121.3521 | 121.3063 | 61.2502 | -121.6486 | 121.275 | 121.4299 | 121.4285 | 61.2904 | -121.7849
666.25 | 121.8842 | -61.203 | 60.4019 | -0.010149 | -0.025966 | 0.008669 | 0.058359 | -0.0086598 | 0.052181 | -0.0062567 | -0.002053 | -0.0031451 | 0.060183 | 0.029149 | 0.052601 | -61.2898 | 0.033457 | -61.2383 | 60.2625 | 60.1354 | 60.085 | -61.2512 | -61.2026 | 0.06904 | -61.3058 | 60.0674 | 60.2178 | 60.2164 | -61.3921 | -0.048223 | -0.13941 | -0.086828 | -0.03533 | 0.012893 | -0.26654 | -0.31689 | -0.18909 | -0.33454 | 0.000436 | -0.10275 | 0.086339 | -0.18417 | -0.18554 | 121.4655 | 121.3384 | 121.288 | 61.2365 | -121.6531 | 121.2704 | 121.4208 | 121.4194 | 61.272 | -121.794
667.9375 | 121.8384 | -61.235 | 60.3928 | -0.010149 | -0.026179 | 0.0088826 | 0.058145 | -0.0086598 | 0.052181 | -0.013887 | -0.0018394 | -0.0031451 | 0.060183 | 0.029363 | 0.053029 | -61.2761 | 0.038035 | -61.2383 | 60.2671 | 60.14 | 60.0942 | -61.2558 | -61.2117 | 0.073618 | -61.3058 | 60.0674 | 60.2178 | 60.2255 | -61.3829 | -0.020759 | -0.12568 | -0.04105 | -0.003287 | 0.017472 | -0.25281 | -0.29857 | -0.14789 | -0.32539 | 0.023322 | -0.070707 | 0.077182 | -0.17501 | -0.16723 | 121.5021 | 121.375 | 121.3292 | 61.2731 | -121.6486 | 121.3024 | 121.4528 | 121.4606 | 61.3087 | -121.7757
669.6719 | 121.8704 | -61.2625 | 60.3607 | 0.0051128 | -0.026179 | 0.0088826 | 0.058573 | -0.0086598 | 0.052394 | -0.013887 | -0.0016258 | -0.0029313 | 0.060396 | 0.029149 | 0.052601 | -61.2898 | 0.028878 | -61.2338 | 60.2625 | 60.1354 | 60.085 | -61.2558 | -61.2026 | 0.06904 | -61.3012 | 60.0674 | 60.2223 | 60.2301 | -61.3875 | 0.006707 | -0.098212 | -0.027319 | 0.028757 | 0.02205 | -0.22534 | -0.27569 | -0.125 | -0.29334 | 0.059945 | -0.038662 | 0.086339 | -0.13839 | -0.13061 | 121.525 | 121.3979 | 121.3475 | 61.2914 | -121.6165 | 121.3299 | 121.4848 | 121.4926 | 61.3316 | -121.7482
671.3438 | 121.9482 | -61.2671 | 60.2737 | -0.01778 | -0.025966 | 0.0088826 | 0.058359 | -0.0090872 | 0.052394 | -0.021518 | -0.0016258 | -0.0033587 | 0.060396 | 0.029577 | 0.052388 | -61.2853 | 0.038035 | -61.2292 | 60.2579 | 60.14 | 60.0988 | -61.2466 | -61.2071 | 0.06904 | -61.3012 | 60.072 | 60.2132 | 60.2347 | -61.3875 | 0.020443 | -0.015815 | -0.018162 | 0.037913 | 0.01747 | -0.13379 | -0.17498 | -0.12042 | -0.20179 | 0.059944 | -0.034084 | 0.086339 | -0.060571 | -0.039055 | 121.525 | 121.407 | 121.3659 | 61.3051 | -121.5204 | 121.339 | 121.4803 | 121.5018 | 61.3361 | -121.6613
673.0938 | 121.9528 | -61.2717 | 60.26 | -0.010149 | -0.025966 | 0.0088826 | 0.058573 | -0.0084462 | 0.051967 | -0.021518 | -0.0016258 | -0.0029313 | 0.059969 | 0.029577 | 0.052815 | -61.2807 | 0.038035 | -61.2338 | 60.2671 | 60.14 | 60.0988 | -61.2512 | -61.2071 | 0.073618 | -61.3058 | 60.0674 | 60.2223 | 60.221 | -61.3875 | 0.020441 | 0.007075 | -0.009007 | 0.037912 | 0.017471 | -0.12006 | -0.16124 | -0.11585 | -0.19264 | 0.064521 | -0.034086 | 0.08176 | -0.03768 | -0.039058 | 121.5388 | 121.4116 | 121.3704 | 61.3097 | -121.5112 | 121.339 | 121.494 | 121.4926 | 61.3453 | -121.6475
674.7812 | 121.8521 | -61.2625 | 60.3333 | 0.0051128 | -0.025966 | 0.0088826 | 0.057932 | -0.0086598 | 0.052394 | -0.021518 | -0.0018394 | -0.0033587 | 0.060183 | 0.029149 | 0.052815 | -61.2807 | 0.042614 | -61.2383 | 60.2671 | 60.14 | 60.1033 | -61.2558 | -61.198 | 0.06904 | -61.3058 | 60.072 | 60.2223 | 60.221 | -61.3829 | 0.006707 | -0.066167 | -0.018162 | 0.024179 | 0.017472 | -0.1933 | -0.22991 | -0.12042 | -0.2613 | 0.064524 | -0.043241 | 0.077182 | -0.11092 | -0.1123 | 121.5296 | 121.4025 | 121.3659 | 61.3051 | -121.5891 | 121.3345 | 121.4848 | 121.4835 | 61.3316 | -121.7162
676.5312 | 121.9437 | -61.2808 | 60.2829 | -0.010149 | -0.025966 | 0.0088826 | 0.058359 | -0.0088734 | 0.052181 | -0.013887 | -0.0018394 | -0.0029313 | 0.060183 | 0.029363 | 0.052815 | -61.2853 | 0.042614 | -61.2383 | 60.2579 | 60.1354 | 60.0988 | -61.2466 | -61.2117 | 0.078197 | -61.3012 | 60.0628 | 60.2223 | 60.221 | -61.3829 | 0.034176 | -0.02497 | -0.004429 | 0.04249 | 0.008314 | -0.14752 | -0.18413 | -0.10211 | -0.2201 | 0.069099 | -0.020351 | 0.081761 | -0.060568 | -0.061946 | 121.5388 | 121.4162 | 121.3796 | 61.3234 | -121.5295 | 121.3436 | 121.5032 | 121.5018 | 61.359 | -121.6658
678.2812 | 121.9437 | -61.2534 | 60.3058 | -0.01778 | -0.026179 | 0.0088826 | 0.057932 | -0.0086598 | 0.052394 | -0.021518 | -0.0018394 | -0.0031451 | 0.059755 | 0.029363 | 0.052388 | -61.2807 | 0.038035 | -61.2292 | 60.2671 | 60.14 | 60.085 | -61.2466 | -61.2163 | 0.06904 | -61.3058 | 60.072 | 60.2269 | 60.221 | -61.3829 | 0.00671 | -0.038701 | -0.027317 | 0.02418 | 0.01747 | -0.16583 | -0.22076 | -0.12958 | -0.23383 | 0.037054 | -0.052396 | 0.077182 | -0.078878 | -0.084834 | 121.5204 | 121.3933 | 121.3384 | 61.2914 | -121.5524 | 121.3253 | 121.4803 | 121.4743 | 61.3224 | -121.6887
680.0312 | 121.8521 | -61.2213 | 60.4431 | -0.0025182 | -0.025966 | 0.0088826 | 0.058359 | -0.0086598 | 0.052181 | -0.013887 | -0.0018394 | -0.0029313 | 0.059969 | 0.029363 | 0.052601 | -61.2807 | 0.038035 | -61.2383 | 60.2625 | 60.1445 | 60.0942 | -61.2558 | -61.2026 | 0.064461 | -61.3058 | 60.0674 | 60.2178 | 60.2255 | -61.3829 | -0.034492 | -0.18061 | -0.059361 | -0.01702 | 0.017472 | -0.29858 | -0.34893 | -0.16162 | -0.37574 | 0.018746 | -0.08444 | 0.077182 | -0.22536 | -0.21758 | 121.4838 | 121.3658 | 121.3155 | 61.2593 | -121.6989 | 121.2887 | 121.4391 | 121.4468 | 61.2858 | -121.8261
681.7188 | 121.8155 | -61.3266 | 60.3195 | -0.0025182 | -0.026179 | 0.0090964 | 0.057932 | -0.0088734 | 0.052181 | -0.021518 | -0.0018394 | -0.0033587 | 0.059969 | 0.029577 | 0.052601 | -61.2807 | 0.033457 | -61.2383 | 60.2671 | 60.1354 | 60.0942 | -61.2512 | -61.2071 | 0.064461 | -61.3058 | 60.0765 | 60.2178 | 60.2255 | -61.3829 | 0.075373 | -0.052434 | 0.045925 | 0.088266 | 0.012893 | -0.18414 | -0.22533 | -0.056336 | -0.24299 | 0.11945 | 0.020846 | 0.077182 | -0.10177 | -0.093988 | 121.5937 | 121.462 | 121.4208 | 61.3601 | -121.5707 | 121.4031 | 121.5444 | 121.5521 | 61.3911 | -121.7025
683.4688 | 121.8338 | -61.3129 | 60.3012 | -0.0025182 | -0.025966 | 0.008669 | 0.058145 | -0.0086598 | 0.052181 | -0.013887 | -0.0016258 | -0.0031451 | 0.059969 | 0.029149 | 0.053029 | -61.2807 | 0.042614 | -61.2383 | 60.2671 | 60.1445 | 60.0988 | -61.2466 | -61.2071 | 0.078197 | -61.3012 | 60.0674 | 60.2223 | 60.2301 | -61.3875 | 0.066219 | -0.034123 | 0.032192 | 0.074533 | 0.008314 | -0.15667 | -0.20244 | -0.074647 | -0.23383 | 0.10572 | 0.011692 | 0.086339 | -0.078878 | -0.071098 | 121.58 | 121.4574 | 121.4116 | 61.3555 | -121.5479 | 121.3802 | 121.5352 | 121.543 | 61.3911 | -121.6887
685.2344 | 121.8246 | -61.2488 | 60.4202 | -0.0025182 | -0.026179 | 0.0088826 | 0.058359 | -0.0088734 | 0.052181 | -0.0062567 | -0.0014122 | -0.0029313 | 0.059969 | 0.029363 | 0.052601 | -61.2761 | 0.042614 | -61.2383 | 60.2671 | 60.14 | 60.0896 | -61.2558 | -61.2071 | 0.064461 | -61.3103 | 60.0628 | 60.204 | 60.2301 | -61.3921 | -0.007026 | -0.15314 | -0.027317 | 0.010446 | 0.017472 | -0.28027 | -0.33062 | -0.14331 | -0.35743 | 0.041633 | -0.061553 | 0.08176 | -0.21621 | -0.19012 | 121.5159 | 121.3887 | 121.3384 | 61.2914 | -121.676 | 121.3116 | 121.4528 | 121.4789 | 61.3132 | -121.8123
686.9844 | 121.9345 | -61.2854 | 60.3058 | -0.01778 | -0.025966 | 0.0088826 | 0.058573 | -0.0086598 | 0.052608 | -0.021518 | -0.0018394 | -0.0033587 | 0.059969 | 0.029149 | 0.053029 | -61.2807 | 0.047193 | -61.2338 | 60.2625 | 60.14 | 60.1033 | -61.2512 | -61.2163 | 0.06904 | -61.3012 | 60.072 | 60.2269 | 60.221 | -61.3921 | 0.034174 | -0.04328 | 0.004726 | 0.051645 | 0.017471 | -0.16583 | -0.20244 | -0.10669 | -0.23383 | 0.069097 | -0.015774 | 0.090918 | -0.078878 | -0.084834 | 121.5479 | 121.4254 | 121.3887 | 61.3326 | -121.557 | 121.3574 | 121.5123 | 121.5064 | 61.3544 | -121.6979
688.6719 | 121.8246 | -61.3174 | 60.3241 | -0.010149 | -0.025966 | 0.0088826 | 0.058145 | -0.0084462 | 0.052181 | -0.021518 | -0.0018394 | -0.0033587 | 0.059969 | 0.029149 | 0.052601 | -61.2853 | 0.042614 | -61.2475 | 60.2671 | 60.14 | 60.0988 | -61.2512 | -61.2071 | 0.073618 | -61.3058 | 60.0674 | 60.2223 | 60.2347 | -61.3829 | 0.066218 | -0.057012 | 0.032192 | 0.069954 | 0.003736 | -0.18414 | -0.22533 | -0.065491 | -0.25672 | 0.1103 | 0.011691 | 0.077182 | -0.10177 | -0.089409 | 121.5845 | 121.4574 | 121.4162 | 61.3601 | -121.5753 | 121.3848 | 121.5398 | 121.5521 | 61.3911 | -121.707
690.4062 | 121.875 | -61.2717 | 60.3287 | -0.010149 | -0.026179 | 0.008669 | 0.058359 | -0.0088734 | 0.052181 | -0.0062567 | -0.0018394 | -0.0033587 | 0.060183 | 0.029577 | 0.052601 | -61.2761 | 0.033457 | -61.2338 | 60.2625 | 60.14 | 60.0988 | -61.2512 | -61.2117 | 0.073618 | -61.3012 | 60.0674 | 60.2269 | 60.2255 | -61.3875 | 0.020441 | -0.066168 | -0.004429 | 0.037912 | 0.017471 | -0.18872 | -0.22991 | -0.11585 | -0.2613 | 0.059943 | -0.029507 | 0.086339 | -0.10177 | -0.10314 | 121.5342 | 121.4116 | 121.3704 | 61.3051 | -121.5799 | 121.339 | 121.4986 | 121.4972 | 61.3453 | -121.7162
692.1562 | 121.8567 | -61.3312 | 60.2966 | -0.01778 | -0.026179 | 0.0090964 | 0.057932 | -0.0088734 | 0.052394 | -0.029148 | -0.0016258 | -0.0029313 | 0.060183 | 0.029577 | 0.052601 | -61.2898 | 0.042614 | -61.2292 | 60.2671 | 60.1491 | 60.1033 | -61.2512 | -61.2163 | 0.078197 | -61.3149 | 60.072 | 60.2178 | 60.2301 | -61.3829 | 0.079951 | -0.029546 | 0.041346 | 0.102 | 0.022049 | -0.14752 | -0.19329 | -0.051758 | -0.22468 | 0.11487 | 0.016267 | 0.068025 | -0.07888 | -0.066521 | 121.5983 | 121.4803 | 121.4345 | 61.3738 | -121.5479 | 121.4031 | 121.5489 | 121.5613 | 61.4094 | -121.6796
693.8438 | 121.7972 | -61.3129 | 60.3195 | -0.0025182 | -0.026179 | 0.0090964 | 0.058145 | -0.0082324 | 0.052181 | -0.021518 | -0.0018394 | -0.0029313 | 0.060183 | 0.028936 | 0.052815 | -61.2898 | 0.042614 | -61.2338 | 60.2625 | 60.1445 | 60.1033 | -61.2466 | -61.2117 | 0.06904 | -61.2966 | 60.0628 | 60.2178 | 60.2347 | -61.3784 | 0.066219 | -0.057013 | 0.023035 | 0.079111 | 0.012892 | -0.17499 | -0.21617 | -0.06549 | -0.25672 | 0.10114 | 0.016271 | 0.081761 | -0.10177 | -0.084831 | 121.5754 | 121.4574 | 121.4162 | 61.3555 | -121.5662 | 121.3757 | 121.5306 | 121.5476 | 61.3819 | -121.6979
695.5781 | 121.8109 | -61.2213 | 60.4202 | -0.01778 | -0.025966 | 0.0090964 | 0.058359 | -0.0086598 | 0.052181 | 0.0013733 | -0.0018394 | -0.0033587 | 0.060183 | 0.029363 | 0.052815 | -61.2853 | 0.042614 | -61.2338 | 60.2533 | 60.1445 | 60.0988 | -61.2558 | -61.2117 | 0.06904 | -61.3058 | 60.0628 | 60.2269 | 60.221 | -61.3921 | -0.034492 | -0.16688 | -0.063939 | -0.012442 | 0.02205 | -0.27569 | -0.32146 | -0.17078 | -0.35743 | 0.009589 | -0.08444 | 0.086339 | -0.19332 | -0.19928 | 121.4747 | 121.3658 | 121.3201 | 61.2639 | -121.676 | 121.2841 | 121.4482 | 121.4423 | 61.2904 | -121.8123
697.3125 | 121.875 | -61.203 | 60.4202 | -0.0025182 | -0.026393 | 0.0088826 | 0.058359 | -0.0088734 | 0.052181 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.029363 | 0.052601 | -61.2807 | 0.038035 | -61.2338 | 60.2671 | 60.1354 | 60.0988 | -61.2558 | -61.2117 | 0.06904 | -61.3058 | 60.072 | 60.2178 | 60.221 | -61.3875 | -0.052802 | -0.15314 | -0.077671 | -0.030752 | 0.02205 | -0.28485 | -0.32146 | -0.18451 | -0.34827 | -0.008721 | -0.10275 | 0.08176 | -0.20248 | -0.19928 | 121.4701 | 121.3384 | 121.3018 | 61.241 | -121.676 | 121.275 | 121.4208 | 121.424 | 61.272 | -121.8077
699.0781 | 121.9574 | -61.1755 | 60.3973 | -0.0025182 | -0.026393 | 0.008669 | 0.058145 | -0.0088734 | 0.051967 | -0.0062567 | -0.0014122 | -0.0031451 | 0.060183 | 0.029577 | 0.052601 | -61.2853 | 0.042614 | -61.2246 | 60.2625 | 60.1354 | 60.1033 | -61.2512 | -61.2071 | 0.06904 | -61.3058 | 60.072 | 60.2178 | 60.2301 | -61.3921 | -0.075689 | -0.13483 | -0.10972 | -0.049061 | 0.026628 | -0.26196 | -0.29399 | -0.21655 | -0.32539 | -0.031609 | -0.13022 | 0.086339 | -0.17959 | -0.16723 | 121.438 | 121.3109 | 121.2789 | 61.2182 | -121.6486 | 121.2475 | 121.3933 | 121.4056 | 61.2446 | -121.7894
700.7656 | 121.8063 | -61.3083 | 60.3287 | -0.010149 | -0.026393 | 0.0090964 | 0.058359 | -0.0088734 | 0.052181 | -0.029148 | -0.0016258 | -0.0029313 | 0.060396 | 0.029363 | 0.052601 | -61.2807 | 0.042614 | -61.2338 | 60.2671 | 60.14 | 60.1033 | -61.2558 | -61.2071 | 0.06904 | -61.3058 | 60.072 | 60.2132 | 60.221 | -61.3875 | 0.052484 | -0.061589 | 0.027615 | 0.074534 | 0.02205 | -0.18872 | -0.22533 | -0.079224 | -0.25672 | 0.10114 | 0.002536 | 0.08176 | -0.1155 | -0.10772 | 121.5754 | 121.4482 | 121.4116 | 61.3509 | -121.5845 | 121.3802 | 121.5215 | 121.5292 | 61.3773 | -121.7162
702.5 | 121.9528 | -61.2717 | 60.2966 | -0.010149 | -0.026607 | 0.0088826 | 0.058145 | -0.0084462 | 0.051967 | -0.013887 | -0.0016258 | -0.0031451 | 0.059969 | 0.029577 | 0.052815 | -61.2853 | 0.042614 | -61.2246 | 60.2717 | 60.1445 | 60.1033 | -61.2512 | -61.2117 | 0.082776 | -61.2966 | 60.072 | 60.2178 | 60.2255 | -61.3921 | 0.020441 | -0.024968 | -0.013585 | 0.047069 | 0.026628 | -0.1521 | -0.19329 | -0.12042 | -0.22468 | 0.059943 | -0.024928 | 0.095497 | -0.07888 | -0.0711 | 121.5433 | 121.4162 | 121.375 | 61.3143 | -121.5479 | 121.3436 | 121.4894 | 121.4972 | 61.3544 | -121.6887
704.25 | 121.9666 | -61.2991 | 60.2875 | -0.01778 | -0.025966 | 0.0090964 | 0.058573 | -0.0082324 | 0.052181 | -0.021518 | -0.002053 | -0.0031451 | 0.060183 | 0.02979 | 0.052601 | -61.2807 | 0.042614 | -61.2338 | 60.2625 | 60.1491 | 60.0988 | -61.2466 | -61.2026 | 0.06904 | -61.292 | 60.0765 | 60.2132 | 60.2255 | -61.3921 | 0.052486 | -0.02497 | 0.018459 | 0.065378 | 0.012892 | -0.13836 | -0.18871 | -0.092959 | -0.21095 | 0.096566 | 0.007116 | 0.10007 | -0.074304 | -0.061945 | 121.5616 | 121.4482 | 121.3979 | 61.3417 | -121.5341 | 121.3757 | 121.5123 | 121.5247 | 61.3682 | -121.6796
705.9219 | 121.8933 | -61.1664 | 60.4065 | -0.0025182 | -0.026393 | 0.0088826 | 0.058145 | -0.0086598 | 0.052181 | -0.013887 | -0.0018394 | -0.0029313 | 0.060396 | 0.029363 | 0.052174 | -61.2807 | 0.042614 | -61.2383 | 60.2625 | 60.1491 | 60.0988 | -61.2512 | -61.2071 | 0.064461 | -61.3012 | 60.072 | 60.2178 | 60.2301 | -61.3921 | -0.084844 | -0.14399 | -0.11429 | -0.071951 | 0.012893 | -0.25738 | -0.30773 | -0.22571 | -0.33454 | -0.040764 | -0.13479 | 0.090918 | -0.18874 | -0.17638 | 121.4289 | 121.3155 | 121.2651 | 61.209 | -121.6577 | 121.2383 | 121.3841 | 121.3965 | 61.2308 | -121.7986
707.6719 | 121.962 | -61.1847 | 60.3882 | -0.025411 | -0.026393 | 0.008669 | 0.057932 | -0.0086598 | 0.052394 | -0.021518 | -0.0018394 | -0.0031451 | 0.060396 | 0.029363 | 0.052388 | -61.2761 | 0.042614 | -61.2246 | 60.2671 | 60.1354 | 60.1125 | -61.2512 | -61.2163 | 0.073618 | -61.3103 | 60.072 | 60.2178 | 60.2255 | -61.3921 | -0.066534 | -0.1211 | -0.091404 | -0.039906 | 0.026628 | -0.25281 | -0.27568 | -0.2074 | -0.31623 | -0.031611 | -0.12564 | 0.08176 | -0.17043 | -0.16265 | 121.4518 | 121.3201 | 121.2972 | 61.2273 | -121.6394 | 121.2566 | 121.4024 | 121.4102 | 61.2583 | -121.7803
709.4219 | 121.843 | -61.235 | 60.3973 | -0.0025182 | -0.026393 | 0.008669 | 0.058573 | -0.0088734 | 0.052394 | -0.021518 | -0.0018394 | -0.0033587 | 0.060396 | 0.029363 | 0.052601 | -61.2898 | 0.042614 | -61.22 | 60.2762 | 60.1491 | 60.1033 | -61.2558 | -61.2163 | 0.06904 | -61.3103 | 60.0765 | 60.2178 | 60.2347 | -61.3875 | -0.020759 | -0.1211 | -0.054785 | 0.015026 | 0.035785 | -0.24823 | -0.29399 | -0.15247 | -0.32081 | 0.018743 | -0.075286 | 0.077181 | -0.17959 | -0.16265 | 121.5113 | 121.3842 | 121.3384 | 61.2777 | -121.6531 | 121.3116 | 121.4528 | 121.4697 | 61.3041 | -121.7849
711.1719 | 121.8796 | -61.2625 | 60.347 | -0.010149 | -0.025966 | 0.0090964 | 0.058359 | -0.0086598 | 0.052394 | -0.013887 | -0.0022666 | -0.0029313 | 0.059969 | 0.029577 | 0.052601 | -61.2807 | 0.038035 | -61.2292 | 60.2762 | 60.1354 | 60.1033 | -61.2558 | -61.2117 | 0.059882 | -61.3058 | 60.0765 | 60.2269 | 60.2347 | -61.3875 | 0.006707 | -0.070743 | -0.018162 | 0.033335 | 0.026628 | -0.21161 | -0.24364 | -0.125 | -0.27045 | 0.050788 | -0.043241 | 0.08176 | -0.12008 | -0.1123 | 121.5388 | 121.3979 | 121.3659 | 61.3005 | -121.6028 | 121.339 | 121.4894 | 121.4972 | 61.3224 | -121.7345
712.8594 | 121.8292 | -61.2396 | 60.4294 | -0.0025182 | -0.026607 | 0.008669 | 0.058145 | -0.0088734 | 0.052394 | -0.013887 | -0.002053 | -0.0031451 | 0.059969 | 0.029577 | 0.052601 | -61.2807 | 0.038035 | -61.2292 | 60.2625 | 60.14 | 60.1033 | -61.2512 | -61.2117 | 0.073618 | -61.3012 | 60.0765 | 60.2223 | 60.2255 | -61.3829 | -0.011602 | -0.16688 | -0.04105 | 0.010447 | 0.022049 | -0.28943 | -0.32604 | -0.14331 | -0.35285 | 0.0279 | -0.06155 | 0.081761 | -0.20705 | -0.20385 | 121.5021 | 121.3796 | 121.343 | 61.2777 | -121.6806 | 121.3162 | 121.462 | 121.4652 | 61.3132 | -121.8123
714.6094 | 121.9437 | -61.235 | 60.2966 | -0.01778 | -0.026607 | 0.0090964 | 0.058573 | -0.0084462 | 0.052394 | -0.013887 | -0.002053 | -0.0033587 | 0.060183 | 0.02979 | 0.052388 | -61.2853 | 0.047193 | -61.2338 | 60.2671 | 60.1491 | 60.0988 | -61.2558 | -61.2071 | 0.06904 | -61.3012 | 60.072 | 60.2269 | 60.2255 | -61.3967 | -0.020759 | -0.029546 | -0.050206 | 0.001291 | 0.02205 | -0.14752 | -0.19787 | -0.16163 | -0.22468 | 0.0279 | -0.066128 | 0.095497 | -0.069723 | -0.0711 | 121.5021 | 121.3842 | 121.3338 | 61.2822 | -121.5524 | 121.307 | 121.462 | 121.4606 | 61.3041 | -121.6933
716.3594 | 121.8246 | -61.2167 | 60.4156 | -0.0025182 | -0.026179 | 0.0090964 | 0.058359 | -0.0084462 | 0.052181 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.029577 | 0.052601 | -61.2853 | 0.047193 | -61.2246 | 60.2671 | 60.1537 | 60.1033 | -61.2512 | -61.2163 | 0.06904 | -61.3012 | 60.072 | 60.2178 | 60.2301 | -61.3829 | -0.03449 | -0.14856 | -0.068516 | -0.007862 | 0.026628 | -0.26196 | -0.3123 | -0.1662 | -0.3437 | 0.000433 | -0.084438 | 0.081761 | -0.1979 | -0.18554 | 121.4838 | 121.3704 | 121.3201 | 61.2639 | -121.6669 | 121.2887 | 121.4345 | 121.4468 | 61.2858 | -121.7986
718.0938 | 121.8018 | -61.3358 | 60.3012 | 0.0051128 | -0.02682 | 0.0090964 | 0.057932 | -0.0090872 | 0.052394 | -0.013887 | -0.0024804 | -0.0031451 | 0.060183 | 0.029577 | 0.052601 | -61.2807 | 0.042614 | -61.2246 | 60.2671 | 60.1491 | 60.0988 | -61.2604 | -61.2117 | 0.06904 | -61.3058 | 60.0765 | 60.2269 | 60.2255 | -61.3967 | 0.07537 | -0.034123 | 0.05508 | 0.11116 | 0.035786 | -0.1521 | -0.20244 | -0.060917 | -0.22468 | 0.12403 | 0.030001 | 0.090918 | -0.0743 | -0.075677 | 121.6028 | 121.4849 | 121.4345 | 61.3784 | -121.5616 | 121.4123 | 121.5627 | 121.5613 | 61.4048 | -121.6979
719.7812 | 121.8521 | -61.2167 | 60.434 | -0.010149 | -0.026607 | 0.0088826 | 0.058359 | -0.0088734 | 0.052394 | -0.013887 | -0.0014122 | -0.0029313 | 0.059755 | 0.029577 | 0.052388 | -61.2853 | 0.042614 | -61.2246 | 60.2671 | 60.1491 | 60.1033 | -61.2512 | -61.2071 | 0.06904 | -61.3058 | 60.0674 | 60.2269 | 60.2255 | -61.3967 | -0.03449 | -0.16687 | -0.068516 | -0.007862 | 0.026628 | -0.28485 | -0.33062 | -0.17994 | -0.36659 | 0.00959 | -0.089017 | 0.090918 | -0.20705 | -0.20843 | 121.4838 | 121.3658 | 121.3201 | 61.2593 | -121.6852 | 121.2841 | 121.4436 | 121.4423 | 61.2858 | -121.8306
721.5156 | 121.9025 | -61.2488 | 60.3653 | -0.010149 | -0.02682 | 0.00931 | 0.058359 | -0.0088734 | 0.052394 | -0.021518 | -0.002053 | -0.0029313 | 0.059969 | 0.029577 | 0.052815 | -61.2853 | 0.042614 | -61.2338 | 60.2625 | 60.1445 | 60.1079 | -61.2512 | -61.2117 | 0.073618 | -61.3058 | 60.0674 | 60.2178 | 60.2347 | -61.3921 | -0.002447 | -0.10279 | -0.036473 | 0.015024 | 0.017471 | -0.22076 | -0.25737 | -0.14331 | -0.29792 | 0.037055 | -0.056974 | 0.086339 | -0.14754 | -0.13061 | 121.5113 | 121.3933 | 121.3567 | 61.2914 | -121.6165 | 121.3162 | 121.4665 | 121.4835 | 61.3224 | -121.7574
723.2656 | 121.8979 | -61.2167 | 60.3607 | -0.010149 | -0.026393 | 0.0088826 | 0.058573 | -0.0088734 | 0.052181 | -0.013887 | -0.0016258 | -0.0029313 | 0.059755 | 0.030004 | 0.052601 | -61.2807 | 0.038035 | -61.2292 | 60.2717 | 60.1491 | 60.1033 | -61.2604 | -61.2117 | 0.073618 | -61.3058 | 60.0628 | 60.2223 | 60.2164 | -61.3921 | -0.043648 | -0.089055 | -0.063938 | -0.012441 | 0.031207 | -0.21161 | -0.25737 | -0.17536 | -0.29792 | 0.005012 | -0.089017 | 0.086339 | -0.13839 | -0.14434 | 121.4884 | 121.3658 | 121.3201 | 61.2548 | -121.6211 | 121.2795 | 121.4391 | 121.4331 | 61.2904 | -121.7528
724.9531 | 121.8155 | -61.3449 | 60.3149 | -0.01778 | -0.026393 | 0.0088826 | 0.058359 | -0.0086598 | 0.052181 | -0.013887 | -0.002053 | -0.0029313 | 0.059969 | 0.029577 | 0.052601 | -61.2761 | 0.047193 | -61.2246 | 60.2671 | 60.1445 | 60.1079 | -61.2558 | -61.2117 | 0.073618 | -61.3058 | 60.072 | 60.2178 | 60.2255 | -61.3875 | 0.089105 | -0.047856 | 0.068814 | 0.12031 | 0.031207 | -0.17041 | -0.20702 | -0.042603 | -0.24299 | 0.13319 | 0.039157 | 0.08176 | -0.09719 | -0.08941 | 121.612 | 121.4894 | 121.4528 | 61.3921 | -121.5707 | 121.4169 | 121.5627 | 121.5704 | 61.4185 | -121.7025
726.7031 | 121.962 | -61.2717 | 60.2737 | -0.01778 | -0.026607 | 0.0090964 | 0.058359 | -0.0086598 | 0.051967 | -0.021518 | -0.002053 | -0.0029313 | 0.059969 | 0.029577 | 0.052601 | -61.2853 | 0.042614 | -61.2246 | 60.2671 | 60.1491 | 60.1033 | -61.2558 | -61.2071 | 0.073618 | -61.3012 | 60.072 | 60.2178 | 60.2255 | -61.3967 | 0.015862 | -0.006658 | -0.013585 | 0.047069 | 0.031207 | -0.12463 | -0.1704 | -0.125 | -0.20179 | 0.064521 | -0.029507 | 0.095497 | -0.055992 | -0.048212 | 121.5388 | 121.4208 | 121.375 | 61.3143 | -121.5295 | 121.3436 | 121.4894 | 121.4972 | 61.3453 | -121.6704
728.4531 | 121.8338 | -61.3083 | 60.3104 | -0.010149 | -0.026607 | 0.0088826 | 0.058359 | -0.0086598 | 0.052181 | -0.029148 | -0.002053 | -0.0031451 | 0.059969 | 0.029363 | 0.052601 | -61.2807 | 0.042614 | -61.2246 | 60.2717 | 60.1491 | 60.0988 | -61.2512 | -61.2071 | 0.06904 | -61.3012 | 60.072 | 60.2269 | 60.2301 | -61.3921 | 0.057063 | -0.038701 | 0.027615 | 0.083691 | 0.026628 | -0.16125 | -0.2116 | -0.083803 | -0.23841 | 0.10114 | 0.007115 | 0.090918 | -0.083456 | -0.080254 | 121.58 | 121.4574 | 121.4071 | 61.3509 | -121.5616 | 121.3802 | 121.5352 | 121.5384 | 61.3773 | -121.7025
730.1562 | 121.8292 | -61.3174 | 60.3378 | -0.0025182 | -0.026607 | 0.0090964 | 0.058359 | -0.0088734 | 0.051753 | -0.013887 | -0.0018394 | -0.0033587 | 0.059755 | 0.030004 | 0.052174 | -61.2807 | 0.047193 | -61.2338 | 60.2671 | 60.1445 | 60.1033 | -61.2512 | -61.2117 | 0.073618 | -61.3058 | 60.072 | 60.2178 | 60.2255 | -61.3921 | 0.066218 | -0.070745 | 0.03677 | 0.083689 | 0.017471 | -0.1933 | -0.23448 | -0.074648 | -0.26588 | 0.10572 | 0.011691 | 0.086339 | -0.12008 | -0.1123 | 121.5845 | 121.462 | 121.4208 | 61.3646 | -121.5891 | 121.3894 | 121.5352 | 121.543 | 61.3911 | -121.7299
731.8906 | 121.843 | -61.3037 | 60.3058 | -0.0025182 | -0.027034 | 0.008669 | 0.058359 | -0.0090872 | 0.052181 | -0.0062567 | -0.0016258 | -0.0033587 | 0.060183 | 0.029577 | 0.052601 | -61.2761 | 0.042614 | -61.2246 | 60.2671 | 60.1491 | 60.1171 | -61.2512 | -61.2117 | 0.073618 | -61.3103 | 60.0811 | 60.2223 | 60.2301 | -61.3875 | 0.052485 | -0.038701 | 0.027615 | 0.079113 | 0.026628 | -0.15667 | -0.18871 | -0.083802 | -0.22468 | 0.091987 | -0.006621 | 0.077181 | -0.083456 | -0.075676 | 121.5708 | 121.4528 | 121.4208 | 61.3463 | -121.557 | 121.3848 | 121.526 | 121.5338 | 61.3773 | -121.6933
733.6406 | 121.9254 | -61.235 | 60.3424 | -0.01778 | -0.02682 | 0.0088826 | 0.057718 | -0.0088734 | 0.052181 | -0.013887 | -0.0018394 | -0.0035723 | 0.060183 | 0.029577 | 0.052601 | -61.2853 | 0.038035 | -61.2292 | 60.2671 | 60.1445 | 60.0942 | -61.2512 | -61.2117 | 0.06904 | -61.3058 | 60.0765 | 60.2132 | 60.2255 | -61.3921 | -0.01618 | -0.075322 | -0.050206 | 0.005869 | 0.022049 | -0.19787 | -0.24822 | -0.15705 | -0.26588 | 0.023322 | -0.070707 | 0.086339 | -0.12924 | -0.11688 | 121.5021 | 121.3796 | 121.3292 | 61.2731 | -121.5936 | 121.3116 | 121.4482 | 121.4606 | 61.3041 | -121.7345
735.3906 | 121.907 | -61.2305 | 60.379 | -0.01778 | -0.02682 | 0.008669 | 0.058145 | -0.0084462 | 0.052394 | -0.021518 | -0.0018394 | -0.0031451 | 0.060183 | 0.02979 | 0.052815 | -61.2807 | 0.042614 | -61.2246 | 60.2671 | 60.1491 | 60.1079 | -61.2466 | -61.2163 | 0.073618 | -61.3103 | 60.0811 | 60.2178 | 60.2301 | -61.3921 | -0.016178 | -0.11194 | -0.050205 | 0.005871 | 0.022049 | -0.22992 | -0.2711 | -0.16162 | -0.29792 | 0.014166 | -0.079863 | 0.08176 | -0.16128 | -0.14892 | 121.4976 | 121.3796 | 121.3384 | 61.2731 | -121.6257 | 121.3116 | 121.4482 | 121.4606 | 61.3041 | -121.7711
737.1406 | 121.875 | -61.2762 | 60.347 | -0.010149 | -0.026393 | 0.008669 | 0.058145 | -0.0088734 | 0.052181 | -0.013887 | -0.0022666 | -0.0029313 | 0.060183 | 0.02979 | 0.052601 | -61.2853 | 0.042614 | -61.2246 | 60.2717 | 60.1537 | 60.1033 | -61.2558 | -61.2163 | 0.073618 | -61.3058 | 60.0765 | 60.2223 | 60.2301 | -61.3921 | 0.02044 | -0.075322 | -0.009007 | 0.051647 | 0.031207 | -0.19329 | -0.24364 | -0.11585 | -0.27045 | 0.059942 | -0.029508 | 0.086339 | -0.12465 | -0.11687 | 121.5479 | 121.4299 | 121.3796 | 61.3189 | -121.6028 | 121.3528 | 121.4986 | 121.5064 | 61.3499 | -121.7391
738.8281 | 121.9345 | -61.2442 | 60.3012 | -0.010149 | -0.027034 | 0.0088826 | 0.057718 | -0.0088734 | 0.052181 | -0.021518 | -0.0018394 | -0.0031451 | 0.059755 | 0.029577 | 0.053029 | -61.2807 | 0.038035 | -61.2246 | 60.2625 | 60.1491 | 60.1079 | -61.2558 | -61.2117 | 0.073618 | -61.3058 | 60.072 | 60.2178 | 60.2301 | -61.3921 | -0.011603 | -0.038702 | -0.036472 | 0.019604 | 0.031207 | -0.1521 | -0.19329 | -0.14789 | -0.22926 | 0.032478 | -0.061551 | 0.086339 | -0.083457 | -0.071098 | 121.5067 | 121.3933 | 121.3521 | 61.2822 | -121.557 | 121.3162 | 121.462 | 121.4743 | 61.3178 | -121.6933
740.5625 | 121.9116 | -61.2305 | 60.3424 | -0.01778 | -0.027248 | 0.0090964 | 0.058573 | -0.0084462 | 0.052394 | -0.013887 | -0.002053 | -0.0029313 | 0.060183 | 0.030004 | 0.052601 | -61.2807 | 0.051771 | -61.2246 | 60.2717 | 60.1491 | 60.1079 | -61.2558 | -61.2071 | 0.078197 | -61.3058 | 60.0811 | 60.2269 | 60.2301 | -61.3921 | -0.025336 | -0.070744 | -0.050205 | 0.005871 | 0.031207 | -0.19329 | -0.23448 | -0.16162 | -0.2613 | 0.023323 | -0.075284 | 0.086339 | -0.1155 | -0.1123 | 121.5021 | 121.3796 | 121.3384 | 61.2822 | -121.5982 | 121.3116 | 121.4574 | 121.4606 | 61.3087 | -121.7345
742.2969 | 121.9299 | -61.29 | 60.2829 | -0.0025182 | -0.027248 | 0.0088826 | 0.057932 | -0.0090872 | 0.051967 | -0.013887 | -0.0018394 | -0.0033587 | 0.059755 | 0.030004 | 0.052601 | -61.2853 | 0.047193 | -61.2246 | 60.2671 | 60.1445 | 60.1079 | -61.2558 | -61.2117 | 0.078197 | -61.3058 | 60.072 | 60.2223 | 60.2301 | -61.3875 | 0.034173 | -0.015813 | 0.004726 | 0.06538 | 0.031207 | -0.13837 | -0.17498 | -0.097535 | -0.21095 | 0.078254 | -0.015775 | 0.08176 | -0.060568 | -0.052788 | 121.5571 | 121.4345 | 121.3979 | 61.3372 | -121.5387 | 121.3619 | 121.5123 | 121.5201 | 61.3682 | -121.6704
743.9844 | 121.8658 | -61.29 | 60.347 | -0.010149 | -0.027461 | 0.008669 | 0.058359 | -0.0086598 | 0.051967 | -0.0062567 | -0.0022666 | -0.0033587 | 0.060183 | 0.02979 | 0.052388 | -61.2807 | 0.042614 | -61.2246 | 60.2671 | 60.1583 | 60.1079 | -61.2558 | -61.2117 | 0.073618 | -61.3058 | 60.0765 | 60.2223 | 60.2301 | -61.3875 | 0.034173 | -0.0799 | 0.009304 | 0.06538 | 0.031207 | -0.18871 | -0.23906 | -0.097535 | -0.27045 | 0.078254 | -0.015775 | 0.08176 | -0.12465 | -0.11687 | 121.5571 | 121.4482 | 121.3979 | 61.3326 | -121.6028 | 121.3665 | 121.5123 | 121.5201 | 61.3636 | -121.7345
745.7344 | 121.8567 | -61.2167 | 60.4202 | -0.0025182 | -0.02682 | 0.0088826 | 0.057718 | -0.0090872 | 0.052181 | -0.0062567 | -0.0018394 | -0.0033587 | 0.059969 | 0.029577 | 0.052815 | -61.2853 | 0.051771 | -61.2246 | 60.2671 | 60.1445 | 60.0988 | -61.2512 | -61.2071 | 0.06904 | -61.3058 | 60.072 | 60.2223 | 60.2301 | -61.3921 | -0.03449 | -0.15314 | -0.068516 | -0.007862 | 0.026628 | -0.27569 | -0.32146 | -0.17536 | -0.34827 | 0.00959 | -0.089017 | 0.086339 | -0.1979 | -0.19012 | 121.4838 | 121.3613 | 121.3155 | 61.2685 | -121.6715 | 121.2887 | 121.4391 | 121.4468 | 61.2858 | -121.8123
747.4844 | 121.8475 | -61.2991 | 60.3333 | -0.010149 | -0.02682 | 0.0088826 | 0.057932 | -0.0088734 | 0.051967 | -0.021518 | -0.0016258 | -0.0031451 | 0.059755 | 0.030004 | 0.052601 | -61.2853 | 0.047193 | -61.2338 | 60.2671 | 60.1583 | 60.1079 | -61.2604 | -61.2071 | 0.078197 | -61.3058 | 60.0765 | 60.2223 | 60.2301 | -61.3875 | 0.038749 | -0.066167 | 0.013881 | 0.065378 | 0.026629 | -0.17498 | -0.22533 | -0.08838 | -0.25672 | 0.091987 | -0.00662 | 0.08176 | -0.11092 | -0.10314 | 121.5662 | 121.4574 | 121.4071 | 61.3463 | -121.5936 | 121.3757 | 121.5215 | 121.5292 | 61.3773 | -121.7208
749.1719 | 121.8613 | -61.2671 | 60.347 | -0.010149 | -0.02682 | 0.0088826 | 0.058359 | -0.0086598 | 0.051967 | -0.021518 | -0.002053 | -0.0029313 | 0.060396 | 0.030004 | 0.052601 | -61.2761 | 0.038035 | -61.2246 | 60.2671 | 60.1491 | 60.1079 | -61.2558 | -61.2071 | 0.073618 | -61.3012 | 60.0765 | 60.2132 | 60.221 | -61.3921 | 0.011285 | -0.0799 | -0.009006 | 0.042492 | 0.031207 | -0.19787 | -0.23906 | -0.125 | -0.27045 | 0.059944 | -0.034084 | 0.090918 | -0.13381 | -0.12603 | 121.5342 | 121.4162 | 121.375 | 61.3051 | -121.6028 | 121.3436 | 121.4803 | 121.488 | 61.3407 | -121.7391
750.9219 | 121.8475 | -61.322 | 60.3241 | -0.010149 | -0.027034 | 0.0090964 | 0.058359 | -0.0088734 | 0.051967 | -0.013887 | -0.0018394 | -0.0031451 | 0.059969 | 0.02979 | 0.052815 | -61.2807 | 0.047193 | -61.2246 | 60.2717 | 60.1445 | 60.1079 | -61.2558 | -61.2117 | 0.06904 | -61.3058 | 60.0857 | 60.2178 | 60.2301 | -61.3921 | 0.066216 | -0.052434 | 0.041347 | 0.097423 | 0.031207 | -0.17956 | -0.21617 | -0.070071 | -0.23841 | 0.1103 | 0.016268 | 0.086339 | -0.10635 | -0.093987 | 121.5937 | 121.4666 | 121.4299 | 61.3692 | -121.5799 | 121.4077 | 121.5398 | 121.5521 | 61.3911 | -121.7162
752.6719 | 121.9437 | -61.2762 | 60.2875 | 0.0051128 | -0.027248 | 0.0088826 | 0.057932 | -0.0090872 | 0.051967 | -0.029148 | -0.0018394 | -0.0029313 | 0.059542 | 0.02979 | 0.052174 | -61.2853 | 0.047193 | -61.2292 | 60.2808 | 60.1491 | 60.1033 | -61.2512 | -61.2071 | 0.06904 | -61.3012 | 60.072 | 60.2178 | 60.2301 | -61.3967 | 0.025019 | -0.006656 | -0.009007 | 0.047068 | 0.022049 | -0.13836 | -0.18413 | -0.12043 | -0.21552 | 0.069099 | -0.024929 | 0.095497 | -0.069725 | -0.057366 | 121.5571 | 121.4254 | 121.3796 | 61.3234 | -121.5387 | 121.3482 | 121.494 | 121.5064 | 61.3453 | -121.6841
754.3594 | 121.8933 | -61.29 | 60.3516 | -0.010149 | -0.027461 | 0.0090964 | 0.057932 | -0.0088734 | 0.052181 | -0.013887 | -0.002053 | -0.0029313 | 0.059969 | 0.02979 | 0.052815 | -61.2853 | 0.038035 | -61.2338 | 60.2625 | 60.1537 | 60.1079 | -61.2604 | -61.2071 | 0.073618 | -61.3103 | 60.072 | 60.2223 | 60.2347 | -61.3829 | 0.029594 | -0.089056 | 0.004726 | 0.056223 | 0.026629 | -0.19787 | -0.24364 | -0.092957 | -0.27961 | 0.082832 | -0.020354 | 0.072603 | -0.12923 | -0.11687 | 121.5525 | 121.4437 | 121.3979 | 61.328 | -121.6119 | 121.3619 | 121.5123 | 121.5247 | 61.3636 | -121.7345
756.0938 | 121.9482 | -61.203 | 60.3882 | -0.0025182 | -0.027248 | 0.008669 | 0.058145 | -0.0088734 | 0.052181 | -0.013887 | -0.002053 | -0.0029313 | 0.059755 | 0.030004 | 0.052388 | -61.2898 | 0.042614 | -61.22 | 60.2717 | 60.1537 | 60.1125 | -61.2512 | -61.2071 | 0.073618 | -61.3058 | 60.072 | 60.2223 | 60.2301 | -61.4012 | -0.048223 | -0.11652 | -0.086828 | -0.017017 | 0.031206 | -0.23449 | -0.27568 | -0.19825 | -0.31623 | -0.004143 | -0.10275 | 0.095497 | -0.16585 | -0.15807 | 121.4747 | 121.3567 | 121.3155 | 61.2456 | -121.6394 | 121.275 | 121.4253 | 121.4331 | 61.2766 | -121.7894
757.8594 | 121.9666 | -61.2808 | 60.2783 | -0.0025182 | -0.027461 | 0.0090964 | 0.058145 | -0.0088734 | 0.051967 | -0.021518 | -0.002053 | -0.0033587 | 0.059755 | 0.030004 | 0.052388 | -61.2807 | 0.042614 | -61.2338 | 60.2717 | 60.1583 | 60.1125 | -61.2512 | -61.2163 | 0.082776 | -61.2966 | 60.0811 | 60.2223 | 60.2301 | -61.3921 | 0.029597 | -0.006657 | 0.000149 | 0.047068 | 0.017471 | -0.12005 | -0.16582 | -0.11127 | -0.19721 | 0.06452 | -0.015772 | 0.095497 | -0.05599 | -0.04821 | 121.5525 | 121.4391 | 121.3933 | 61.3234 | -121.5295 | 121.3619 | 121.5032 | 121.5109 | 61.3636 | -121.6704
759.5469 | 121.9574 | -61.2762 | 60.2783 | -0.010149 | -0.027248 | 0.0088826 | 0.058145 | -0.0088734 | 0.052394 | -0.013887 | -0.002053 | -0.0029313 | 0.059969 | 0.02979 | 0.052388 | -61.2807 | 0.042614 | -61.2429 | 60.2717 | 60.1445 | 60.1033 | -61.2512 | -61.2071 | 0.078197 | -61.2966 | 60.0811 | 60.2269 | 60.2347 | -61.3921 | 0.025019 | -0.006657 | -0.004429 | 0.033333 | 0.008314 | -0.13379 | -0.17498 | -0.11585 | -0.19721 | 0.069099 | -0.02035 | 0.095497 | -0.051412 | -0.043632 | 121.5479 | 121.4208 | 121.3796 | 61.3189 | -121.5295 | 121.3574 | 121.5032 | 121.5109 | 61.3544 | -121.6704
761.2812 | 121.9437 | -61.2946 | 60.2875 | -0.010149 | -0.027034 | 0.0088826 | 0.058145 | -0.0086598 | 0.052394 | -0.013887 | -0.002053 | -0.0033587 | 0.059969 | 0.030004 | 0.052601 | -61.2807 | 0.047193 | -61.2246 | 60.2671 | 60.1583 | 60.1079 | -61.2512 | -61.2117 | 0.078197 | -61.3058 | 60.0765 | 60.2132 | 60.2301 | -61.3921 | 0.04333 | -0.020391 | 0.013882 | 0.069958 | 0.026628 | -0.12921 | -0.17955 | -0.097536 | -0.21095 | 0.082832 | -0.011197 | 0.086339 | -0.074304 | -0.057366 | 121.5616 | 121.4528 | 121.4025 | 61.3417 | -121.5387 | 121.3711 | 121.5077 | 121.5247 | 61.3728 | -121.6796
763.0469 | 121.9711 | -61.2122 | 60.3699 | -0.0025182 | -0.027461 | 0.0090964 | 0.057932 | -0.0088734 | 0.051967 | -0.013887 | -0.0016258 | -0.0031451 | 0.059755 | 0.030218 | 0.052601 | -61.2807 | 0.042614 | -61.2383 | 60.2671 | 60.1537 | 60.1171 | -61.2558 | -61.2117 | 0.073618 | -61.3103 | 60.072 | 60.2223 | 60.2255 | -61.4012 | -0.043647 | -0.10279 | -0.068516 | -0.026175 | 0.017472 | -0.21618 | -0.25279 | -0.18909 | -0.29792 | 0.000434 | -0.098174 | 0.090918 | -0.14754 | -0.14434 | 121.4792 | 121.3658 | 121.3292 | 61.2548 | -121.6257 | 121.2841 | 121.4345 | 121.4377 | 61.2858 | -121.7711
764.7344 | 121.9299 | -61.1847 | 60.3882 | -0.01778 | -0.027034 | 0.0090964 | 0.058145 | -0.0088734 | 0.051967 | -0.021518 | -0.0016258 | -0.0031451 | 0.059969 | 0.030004 | 0.052815 | -61.2898 | 0.042614 | -61.2429 | 60.2579 | 60.1491 | 60.1079 | -61.2604 | -61.2071 | 0.078197 | -61.3058 | 60.0765 | 60.2178 | 60.2347 | -61.3921 | -0.075692 | -0.13026 | -0.10514 | -0.05822 | 0.017472 | -0.23907 | -0.28026 | -0.2074 | -0.31165 | -0.022454 | -0.12106 | 0.086339 | -0.17043 | -0.1535 | 121.4426 | 121.3338 | 121.2926 | 61.2273 | -121.6486 | 121.2612 | 121.4024 | 121.4194 | 61.2629 | -121.7803
766.4688 | 121.9299 | -61.2076 | 60.3745 | -0.010149 | -0.027248 | 0.008669 | 0.058359 | -0.0086598 | 0.052181 | -0.021518 | -0.0016258 | -0.0029313 | 0.060183 | 0.030218 | 0.052815 | -61.2898 | 0.042614 | -61.2338 | 60.2671 | 60.1537 | 60.1079 | -61.2512 | -61.2163 | 0.073618 | -61.3058 | 60.072 | 60.2269 | 60.221 | -61.3967 | -0.043645 | -0.10737 | -0.08225 | -0.026174 | 0.017471 | -0.22076 | -0.26653 | -0.18909 | -0.3025 | -0.008722 | -0.098172 | 0.090918 | -0.14754 | -0.1535 | 121.4747 | 121.3613 | 121.3155 | 61.2502 | -121.6257 | 121.2795 | 121.4345 | 121.4285 | 61.2812 | -121.7711
768.2031 | 121.907 | -61.203 | 60.4111 | -0.0025182 | -0.027248 | 0.00931 | 0.058145 | -0.0086598 | 0.052181 | -0.0062567 | -0.0018394 | -0.0029313 | 0.059969 | 0.030218 | 0.052388 | -61.2853 | 0.038035 | -61.2383 | 60.2579 | 60.1491 | 60.1079 | -61.2558 | -61.198 | 0.064461 | -61.3103 | 60.0811 | 60.2223 | 60.2255 | -61.3967 | -0.052802 | -0.15314 | -0.082249 | -0.03533 | 0.017472 | -0.26196 | -0.30315 | -0.19367 | -0.32996 | 0.005015 | -0.10733 | 0.086339 | -0.18874 | -0.18554 | 121.4609 | 121.3521 | 121.3109 | 61.241 | -121.6669 | 121.2841 | 121.4253 | 121.4285 | 61.2675 | -121.8077
769.9531 | 121.9254 | -61.2488 | 60.3241 | -0.01778 | -0.027461 | 0.00931 | 0.058145 | -0.0088734 | 0.051753 | -0.036779 | -0.0022666 | -0.0033587 | 0.059755 | 0.030004 | 0.052174 | -61.2807 | 0.038035 | -61.2383 | 60.2717 | 60.1537 | 60.1079 | -61.2604 | -61.2163 | 0.073618 | -61.3012 | 60.072 | 60.2361 | 60.2255 | -61.3967 | -0.011605 | -0.052434 | -0.031895 | 0.010446 | 0.022051 | -0.17041 | -0.21617 | -0.14789 | -0.25214 | 0.032476 | -0.052395 | 0.095497 | -0.088032 | -0.098566 | 121.5204 | 121.4025 | 121.3567 | 61.2868 | -121.5845 | 121.3207 | 121.4848 | 121.4743 | 61.3224 | -121.7208
771.625 | 121.9666 | -61.2625 | 60.3012 | -0.010149 | -0.027248 | 0.00931 | 0.057932 | -0.0088734 | 0.052181 | -0.0062567 | -0.0018394 | -0.0031451 | 0.059755 | 0.030004 | 0.052601 | -61.2807 | 0.042614 | -61.2338 | 60.2717 | 60.1583 | 60.1125 | -61.2558 | -61.2071 | 0.073618 | -61.3103 | 60.0765 | 60.2269 | 60.2347 | -61.3921 | 0.006707 | -0.029545 | -0.018162 | 0.028757 | 0.02205 | -0.14294 | -0.18871 | -0.12958 | -0.22468 | 0.055366 | -0.04782 | 0.08176 | -0.0743 | -0.06652 | 121.5342 | 121.4208 | 121.375 | 61.3051 | -121.557 | 121.339 | 121.4894 | 121.4972 | 61.3361 | -121.6933
773.375 | 121.9437 | -61.2762 | 60.3012 | -0.01778 | -0.027248 | 0.0088826 | 0.058145 | -0.0088734 | 0.051967 | -0.0062567 | -0.0018394 | -0.0029313 | 0.059755 | 0.030004 | 0.052601 | -61.2807 | 0.038035 | -61.2383 | 60.2671 | 60.1491 | 60.1079 | -61.2512 | -61.2117 | 0.073618 | -61.3058 | 60.0765 | 60.2269 | 60.2255 | -61.3921 | 0.025019 | -0.034123 | -0.004429 | 0.037912 | 0.012893 | -0.1521 | -0.19329 | -0.11585 | -0.22468 | 0.064521 | -0.029508 | 0.086339 | -0.0743 | -0.075677 | 121.5433 | 121.4254 | 121.3842 | 61.3143 | -121.5524 | 121.3528 | 121.5032 | 121.5018 | 61.3499 | -121.6933
775.125 | 121.8887 | -61.2488 | 60.3516 | -0.0025182 | -0.027248 | 0.0090964 | 0.058359 | -0.0088734 | 0.051967 | -0.013887 | -0.0018394 | -0.0029313 | 0.059969 | 0.030218 | 0.052174 | -61.2807 | 0.042614 | -61.2292 | 60.2717 | 60.1674 | 60.1125 | -61.2604 | -61.2117 | 0.06904 | -61.3058 | 60.0765 | 60.2223 | 60.2347 | -61.4012 | -0.011605 | -0.079899 | -0.031895 | 0.019602 | 0.031207 | -0.18413 | -0.23906 | -0.15247 | -0.27503 | 0.037055 | -0.056974 | 0.095497 | -0.12923 | -0.11687 | 121.5204 | 121.4162 | 121.3613 | 61.2914 | -121.6119 | 121.3253 | 121.4711 | 121.4835 | 61.3178 | -121.7528
776.8125 | 121.9162 | -61.2305 | 60.3378 | -0.010149 | -0.027461 | 0.0090964 | 0.057932 | -0.0088734 | 0.052181 | -0.013887 | -0.0016258 | -0.0027177 | 0.060183 | 0.030004 | 0.052174 | -61.2761 | 0.042614 | -61.2383 | 60.2717 | 60.1583 | 60.1079 | -61.2512 | -61.2071 | 0.073618 | -61.3058 | 60.0765 | 60.2178 | 60.2301 | -61.3921 | -0.020757 | -0.066167 | -0.045627 | -0.007864 | 0.012893 | -0.17956 | -0.22991 | -0.16162 | -0.2613 | 0.023323 | -0.075284 | 0.086339 | -0.12008 | -0.10772 | 121.5021 | 121.3887 | 121.3384 | 61.2731 | -121.5891 | 121.307 | 121.4482 | 121.4606 | 61.3041 | -121.7299
778.5625 | 121.9162 | -61.2488 | 60.3699 | -0.025411 | -0.027248 | 0.0088826 | 0.057932 | -0.0086598 | 0.051967 | -0.021518 | -0.0018394 | -0.0031451 | 0.060183 | 0.030004 | 0.052601 | -61.2853 | 0.028878 | -61.2383 | 60.2625 | 60.1583 | 60.1079 | -61.2558 | -61.2071 | 0.064461 | -61.3012 | 60.0765 | 60.2269 | 60.2301 | -61.3967 | -0.007026 | -0.10737 | -0.036473 | 0.010446 | 0.017472 | -0.2116 | -0.26195 | -0.14789 | -0.29334 | 0.041633 | -0.052395 | 0.095497 | -0.14296 | -0.13976 | 121.5113 | 121.407 | 121.3567 | 61.2777 | -121.6257 | 121.3253 | 121.4757 | 121.4789 | 61.3132 | -121.7665
780.3281 | 121.8475 | -61.2946 | 60.3241 | -0.0025182 | -0.027248 | 0.0088826 | 0.058145 | -0.0088734 | 0.051967 | -0.0062567 | -0.002053 | -0.0029313 | 0.059969 | 0.030218 | 0.052601 | -61.2807 | 0.033457 | -61.2383 | 60.2671 | 60.1674 | 60.1079 | -61.2558 | -61.2071 | 0.078197 | -61.3058 | 60.072 | 60.2223 | 60.2301 | -61.3875 | 0.038751 | -0.057012 | 0.013882 | 0.056223 | 0.017472 | -0.15667 | -0.21617 | -0.092957 | -0.25214 | 0.08741 | -0.011197 | 0.08176 | -0.10177 | -0.093987 | 121.5616 | 121.462 | 121.4025 | 61.328 | -121.5799 | 121.3665 | 121.5169 | 121.5247 | 61.3728 | -121.7116
782.0156 | 121.9208 | -61.2442 | 60.3333 | -0.0025182 | -0.027461 | 0.008669 | 0.058145 | -0.0093008 | 0.052181 | -0.013887 | -0.0016258 | -0.0031451 | 0.060183 | 0.030218 | 0.052388 | -61.2853 | 0.038035 | -61.2383 | 60.2717 | 60.1628 | 60.1125 | -61.2558 | -61.2163 | 0.073618 | -61.3103 | 60.0674 | 60.2269 | 60.2255 | -61.3921 | -0.011603 | -0.061589 | -0.04105 | 0.005869 | 0.017472 | -0.1704 | -0.22075 | -0.14789 | -0.26588 | 0.027899 | -0.06613 | 0.08176 | -0.10634 | -0.10772 | 121.5159 | 121.4071 | 121.3567 | 61.2822 | -121.5891 | 121.3116 | 121.4711 | 121.4697 | 61.3178 | -121.7253
783.7656 | 121.9162 | -61.2488 | 60.3607 | -0.010149 | -0.027461 | 0.0095236 | 0.057932 | -0.0086598 | 0.052181 | -0.0062567 | -0.0018394 | -0.0031451 | 0.059755 | 0.030218 | 0.052388 | -61.2807 | 0.028878 | -61.2429 | 60.2762 | 60.1537 | 60.1125 | -61.2558 | -61.2117 | 0.078197 | -61.3058 | 60.0765 | 60.2223 | 60.2255 | -61.4012 | -0.007026 | -0.084476 | -0.031895 | 0.005867 | 0.012893 | -0.20703 | -0.24822 | -0.15247 | -0.28419 | 0.037055 | -0.056974 | 0.095497 | -0.13839 | -0.13519 | 121.525 | 121.4025 | 121.3613 | 61.2777 | -121.6165 | 121.3253 | 121.4711 | 121.4743 | 61.327 | -121.762
785.5156 | 121.9482 | -61.1664 | 60.3973 | -0.010149 | -0.027461 | 0.0090964 | 0.057932 | -0.0088734 | 0.051753 | -0.013887 | -0.0016258 | -0.0029313 | 0.060183 | 0.030645 | 0.052388 | -61.2853 | 0.033457 | -61.2429 | 60.2671 | 60.1491 | 60.1125 | -61.2558 | -61.2209 | 0.06904 | -61.3103 | 60.0765 | 60.2269 | 60.2255 | -61.3921 | -0.089423 | -0.13025 | -0.11887 | -0.07653 | 0.012893 | -0.24823 | -0.28484 | -0.22571 | -0.32081 | -0.0545 | -0.14395 | 0.08176 | -0.17043 | -0.17181 | 121.4335 | 121.3155 | 121.2789 | 61.1998 | -121.6531 | 121.2429 | 121.3933 | 121.3919 | 61.2354 | -121.7894
787.2031 | 121.8246 | -61.2488 | 60.4202 | -0.010149 | -0.027461 | 0.008669 | 0.057932 | -0.0084462 | 0.051753 | -0.0062567 | -0.0018394 | -0.0031451 | 0.060183 | 0.030431 | 0.052174 | -61.2898 | 0.028878 | -61.2429 | 60.2671 | 60.1491 | 60.1125 | -61.2604 | -61.2163 | 0.06904 | -61.3058 | 60.0765 | 60.2269 | 60.221 | -61.3967 | -0.011605 | -0.15314 | -0.041052 | 0.005867 | 0.017472 | -0.27111 | -0.30772 | -0.14789 | -0.3437 | 0.032476 | -0.056974 | 0.090918 | -0.19332 | -0.19928 | 121.5159 | 121.3979 | 121.3613 | 61.2777 | -121.6806 | 121.3253 | 121.4757 | 121.4697 | 61.3178 | -121.8169
788.9688 | 121.8933 | -61.2534 | 60.347 | -0.01778 | -0.027675 | 0.0090964 | 0.057932 | -0.0088734 | 0.051753 | -0.021518 | -0.0022666 | -0.0031451 | 0.059969 | 0.030218 | 0.05196 | -61.2807 | 0.038035 | -61.2429 | 60.2671 | 60.1537 | 60.1125 | -61.2558 | -61.2071 | 0.073618 | -61.3058 | 60.0811 | 60.2269 | 60.2347 | -61.3921 | -0.002448 | -0.0799 | -0.027317 | 0.010445 | 0.012893 | -0.19329 | -0.23448 | -0.13873 | -0.26588 | 0.046211 | -0.052396 | 0.086339 | -0.12008 | -0.1123 | 121.5204 | 121.407 | 121.3659 | 61.2914 | -121.6028 | 121.3345 | 121.4803 | 121.488 | 61.327 | -121.7391
790.7188 | 121.8933 | -61.2167 | 60.3561 | -0.025411 | -0.027675 | 0.0090964 | 0.057932 | -0.0090872 | 0.051753 | -0.013887 | -0.002053 | -0.0031451 | 0.059755 | 0.030431 | 0.052388 | -61.2853 | 0.033457 | -61.2429 | 60.2717 | 60.1537 | 60.1125 | -61.2604 | -61.2117 | 0.06904 | -61.3058 | 60.0765 | 60.2178 | 60.2347 | -61.3921 | -0.043648 | -0.084477 | -0.068516 | -0.026176 | 0.017472 | -0.20245 | -0.24364 | -0.17536 | -0.27961 | 0.005012 | -0.089017 | 0.086339 | -0.13839 | -0.12145 | 121.4884 | 121.3704 | 121.3292 | 61.2502 | -121.6165 | 121.2933 | 121.4345 | 121.4514 | 61.2858 | -121.7482
792.4062 | 121.9482 | -61.2808 | 60.2783 | -0.01778 | -0.027248 | 0.00931 | 0.058145 | -0.0088734 | 0.051967 | -0.0062567 | -0.0018394 | -0.0029313 | 0.059755 | 0.030218 | 0.052174 | -61.2853 | 0.042614 | -61.2383 | 60.2717 | 60.1674 | 60.1171 | -61.2512 | -61.2117 | 0.078197 | -61.3058 | 60.072 | 60.2315 | 60.2255 | -61.3921 | 0.029597 | -0.006657 | -0.004429 | 0.04249 | 0.012893 | -0.11089 | -0.16124 | -0.11127 | -0.20637 | 0.069099 | -0.02493 | 0.086339 | -0.046833 | -0.052789 | 121.5525 | 121.4483 | 121.3979 | 61.3234 | -121.5295 | 121.3528 | 121.5123 | 121.5064 | 61.359 | -121.6704
794.1562 | 121.8658 | -61.2167 | 60.4111 | 0.0051128 | -0.027461 | 0.0090964 | 0.058145 | -0.0088734 | 0.051967 | -0.0062567 | -0.0016258 | -0.0031451 | 0.059969 | 0.030218 | 0.052601 | -61.2853 | 0.033457 | -61.2429 | 60.2671 | 60.1537 | 60.1125 | -61.2604 | -61.2163 | 0.06904 | -61.3012 | 60.072 | 60.2315 | 60.2301 | -61.3967 | -0.043648 | -0.14399 | -0.068516 | -0.026176 | 0.017472 | -0.25738 | -0.29857 | -0.17994 | -0.33912 | 0.000433 | -0.084438 | 0.095497 | -0.17958 | -0.18096 | 121.4838 | 121.3704 | 121.3292 | 61.2502 | -121.6715 | 121.2887 | 121.4482 | 121.4468 | 61.2858 | -121.8077
795.9062 | 121.8338 | -61.2259 | 60.4202 | -0.010149 | -0.027675 | 0.0090964 | 0.058145 | -0.0088734 | 0.051753 | -0.0062567 | -0.0022666 | -0.0033587 | 0.060183 | 0.030645 | 0.052174 | -61.2807 | 0.033457 | -61.2383 | 60.2717 | 60.1583 | 60.1033 | -61.2604 | -61.2163 | 0.06904 | -61.3012 | 60.072 | 60.2269 | 60.2347 | -61.3921 | -0.034493 | -0.14856 | -0.054783 | -0.012442 | 0.022051 | -0.26196 | -0.31688 | -0.1662 | -0.34827 | 0.009588 | -0.075283 | 0.090918 | -0.19332 | -0.18554 | 121.4976 | 121.3842 | 121.3292 | 61.2593 | -121.6806 | 121.2978 | 121.4528 | 121.4606 | 61.2949 | -121.8123
797.5938 | 121.8979 | -61.3129 | 60.2829 | -0.010149 | -0.027675 | 0.0088826 | 0.058359 | -0.0086598 | 0.051753 | -0.0062567 | -0.0014122 | -0.0029313 | 0.060183 | 0.030218 | 0.052388 | -61.2853 | 0.038035 | -61.2429 | 60.2717 | 60.1628 | 60.1171 | -61.2512 | -61.2071 | 0.082776 | -61.2966 | 60.0811 | 60.2315 | 60.2347 | -61.3967 | 0.06164 | -0.011235 | 0.027614 | 0.069954 | 0.008314 | -0.12005 | -0.16582 | -0.083805 | -0.20179 | 0.10572 | 0.016271 | 0.10008 | -0.051411 | -0.04821 | 121.5845 | 121.4757 | 121.4299 | 61.3509 | -121.5341 | 121.394 | 121.5444 | 121.5476 | 61.3956 | -121.6796
799.3438 | 121.8704 | -61.2167 | 60.4019 | -0.010149 | -0.027675 | 0.00931 | 0.057932 | -0.0093008 | 0.051967 | -0.013887 | -0.002053 | -0.0031451 | 0.060183 | 0.030218 | 0.052174 | -61.2807 | 0.038035 | -61.2475 | 60.2717 | 60.1583 | 60.1079 | -61.2558 | -61.2163 | 0.078197 | -61.3012 | 60.0765 | 60.2223 | 60.2255 | -61.3921 | -0.039069 | -0.13025 | -0.063938 | -0.030754 | 0.008315 | -0.24365 | -0.29399 | -0.17536 | -0.32539 | 0.000433 | -0.084438 | 0.090918 | -0.17959 | -0.17639 | 121.4884 | 121.375 | 121.3247 | 61.2548 | -121.6577 | 121.2933 | 121.4391 | 121.4423 | 61.2949 | -121.794
801.0781 | 121.8613 | -61.2442 | 60.3836 | -0.0025182 | -0.027889 | 0.0088826 | 0.058145 | -0.0086598 | 0.052181 | -0.021518 | -0.002053 | -0.0031451 | 0.059969 | 0.030218 | 0.052174 | -61.2761 | 0.033457 | -61.2429 | 60.2717 | 60.1583 | 60.1171 | -61.265 | -61.2071 | 0.06904 | -61.3058 | 60.072 | 60.2178 | 60.2255 | -61.3921 | -0.020761 | -0.11194 | -0.031894 | 0.00129 | 0.022051 | -0.22534 | -0.26653 | -0.14789 | -0.31165 | 0.037056 | -0.061551 | 0.086339 | -0.16586 | -0.15808 | 121.5159 | 121.4025 | 121.3613 | 61.2777 | -121.6486 | 121.3162 | 121.462 | 121.4697 | 61.3132 | -121.7757
802.8125 | 121.8155 | -61.3403 | 60.3195 | -0.010149 | -0.027675 | 0.0088826 | 0.057718 | -0.0086598 | 0.051967 | -0.013887 | -0.002053 | -0.0029313 | 0.059969 | 0.030218 | 0.052388 | -61.2761 | 0.033457 | -61.2338 | 60.2762 | 60.1583 | 60.1171 | -61.2558 | -61.2117 | 0.073618 | -61.3012 | 60.0765 | 60.2269 | 60.2347 | -61.3967 | 0.084527 | -0.043277 | 0.064236 | 0.10658 | 0.02205 | -0.16125 | -0.20244 | -0.056339 | -0.24299 | 0.12861 | 0.039158 | 0.095497 | -0.092611 | -0.084831 | 121.6166 | 121.4986 | 121.4574 | 61.3738 | -121.5753 | 121.4169 | 121.5672 | 121.575 | 61.4139 | -121.7162
804.5625 | 121.8155 | -61.3129 | 60.3424 | -0.010149 | -0.027889 | 0.0088826 | 0.057932 | -0.0090872 | 0.051967 | -0.021518 | -0.002053 | -0.0029313 | 0.060183 | 0.030645 | 0.052388 | -61.2853 | 0.038035 | -61.2429 | 60.2671 | 60.1628 | 60.1217 | -61.2558 | -61.2071 | 0.073618 | -61.3058 | 60.072 | 60.2223 | 60.2301 | -61.3875 | 0.057061 | -0.075322 | 0.027614 | 0.069954 | 0.012893 | -0.17956 | -0.22075 | -0.074647 | -0.27045 | 0.10572 | 0.007113 | 0.08176 | -0.12008 | -0.1123 | 121.58 | 121.4757 | 121.4345 | 61.3509 | -121.5982 | 121.3848 | 121.5352 | 121.543 | 61.3865 | -121.7299
806.2344 | 121.962 | -61.2762 | 60.2966 | -0.0025182 | -0.027675 | 0.0088826 | 0.057932 | -0.0088734 | 0.052181 | -0.021518 | -0.0018394 | -0.0031451 | 0.059755 | 0.030431 | 0.052388 | -61.2807 | 0.042614 | -61.2338 | 60.2717 | 60.1491 | 60.1079 | -61.2558 | -61.2117 | 0.073618 | -61.3103 | 60.072 | 60.2223 | 60.2301 | -61.3921 | 0.02044 | -0.024968 | -0.004429 | 0.04249 | 0.02205 | -0.14752 | -0.18871 | -0.11585 | -0.22468 | 0.064521 | -0.034087 | 0.08176 | -0.074301 | -0.066521 | 121.5479 | 121.4254 | 121.3842 | 61.3189 | -121.5524 | 121.3482 | 121.4986 | 121.5064 | 61.3499 | -121.6887
807.9219 | 121.8613 | -61.2762 | 60.3424 | -0.0025182 | -0.027675 | 0.008669 | 0.057932 | -0.0093008 | 0.051753 | -0.021518 | -0.002053 | -0.0027177 | 0.060183 | 0.030431 | 0.052388 | -61.2853 | 0.033457 | -61.2429 | 60.2717 | 60.1537 | 60.1125 | -61.2512 | -61.2209 | 0.073618 | -61.3058 | 60.0811 | 60.2315 | 60.2347 | -61.3875 | 0.025019 | -0.070744 | -0.009007 | 0.033333 | 0.008314 | -0.18872 | -0.22991 | -0.11127 | -0.2613 | 0.055363 | -0.029508 | 0.08176 | -0.11092 | -0.10772 | 121.5479 | 121.4299 | 121.3887 | 61.3097 | -121.5936 | 121.3574 | 121.5077 | 121.5109 | 61.3499 | -121.7299
809.6719 | 121.843 | -61.2488 | 60.434 | -0.010149 | -0.027889 | 0.0090964 | 0.057504 | -0.0088734 | 0.051753 | -0.0062567 | -0.0016258 | -0.0029313 | 0.060183 | 0.030431 | 0.052174 | -61.2898 | 0.042614 | -61.2429 | 60.2671 | 60.1537 | 60.1079 | -61.2512 | -61.2117 | 0.078197 | -61.3058 | 60.0674 | 60.2269 | 60.2347 | -61.3967 | -0.002447 | -0.16687 | -0.041052 | 0.005867 | 0.008314 | -0.28027 | -0.32604 | -0.14789 | -0.36659 | 0.037055 | -0.056974 | 0.090918 | -0.20705 | -0.19927 | 121.5159 | 121.4025 | 121.3567 | 61.2914 | -121.6852 | 121.3162 | 121.4757 | 121.4835 | 61.327 | -121.8306
811.3438 | 121.8384 | -61.235 | 60.4294 | -0.010149 | -0.028102 | 0.008669 | 0.058145 | -0.0088734 | 0.051967 | -0.013887 | -0.0018394 | -0.0029313 | 0.059969 | 0.030218 | 0.052388 | -61.2853 | 0.038035 | -61.2429 | 60.2671 | 60.1628 | 60.1125 | -61.2558 | -61.2071 | 0.073618 | -61.3103 | 60.0765 | 60.2269 | 60.2301 | -61.4012 | -0.020759 | -0.1623 | -0.050206 | -0.007866 | 0.012893 | -0.26653 | -0.31688 | -0.1662 | -0.35285 | 0.0279 | -0.075286 | 0.090918 | -0.20247 | -0.19927 | 121.5021 | 121.3979 | 121.3475 | 61.2731 | -121.6852 | 121.3116 | 121.462 | 121.4652 | 61.3087 | -121.8306
813.1094 | 121.9528 | -61.2808 | 60.26 | -0.010149 | -0.027889 | 0.0088826 | 0.058145 | -0.0090872 | 0.051967 | -0.021518 | -0.0018394 | -0.0031451 | 0.059969 | 0.030431 | 0.052174 | -61.2807 | 0.042614 | -61.2383 | 60.2671 | 60.1583 | 60.1171 | -61.2558 | -61.2071 | 0.073618 | -61.3058 | 60.0765 | 60.2223 | 60.2255 | -61.4012 | 0.025018 | 0.007075 | 0.000149 | 0.04249 | 0.017472 | -0.10174 | -0.14293 | -0.12043 | -0.18348 | 0.073677 | -0.02493 | 0.095497 | -0.03768 | -0.034479 | 121.5479 | 121.4391 | 121.3979 | 61.3234 | -121.5158 | 121.3574 | 121.5032 | 121.5064 | 61.3544 | -121.6613
814.7969 | 121.9528 | -61.2625 | 60.2829 | -0.010149 | -0.027889 | 0.0088826 | 0.058145 | -0.0090872 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.059969 | 0.030645 | 0.05196 | -61.2761 | 0.033457 | -61.2338 | 60.2717 | 60.1628 | 60.1217 | -61.2558 | -61.2117 | 0.073618 | -61.3103 | 60.0765 | 60.2269 | 60.2347 | -61.3967 | 0.006707 | -0.011235 | -0.013584 | 0.028757 | 0.02205 | -0.12005 | -0.16124 | -0.13416 | -0.20637 | 0.050788 | -0.04782 | 0.086339 | -0.05599 | -0.04821 | 121.5342 | 121.4254 | 121.3842 | 61.296 | -121.5387 | 121.339 | 121.4894 | 121.4972 | 61.3361 | -121.6796
816.5312 | 121.9116 | -61.2808 | 60.2966 | -0.010149 | -0.027889 | 0.0088826 | 0.058145 | -0.0090872 | 0.051967 | -0.021518 | -0.0022666 | -0.0031451 | 0.059755 | 0.030431 | 0.052174 | -61.2853 | 0.042614 | -61.2338 | 60.2717 | 60.1583 | 60.1125 | -61.2558 | -61.2071 | 0.073618 | -61.3012 | 60.072 | 60.2269 | 60.2301 | -61.3921 | 0.025018 | -0.024968 | -0.004429 | 0.047068 | 0.02205 | -0.13836 | -0.18413 | -0.11127 | -0.22468 | 0.073677 | -0.020351 | 0.090918 | -0.069723 | -0.066521 | 121.5525 | 121.4391 | 121.3933 | 61.3234 | -121.5524 | 121.3528 | 121.5077 | 121.5109 | 61.3544 | -121.6887
818.2656 | 121.9574 | -61.2808 | 60.2875 | -0.01778 | -0.027889 | 0.0090964 | 0.057932 | -0.0090872 | 0.051967 | -0.021518 | -0.0022666 | -0.0033587 | 0.059969 | 0.030218 | 0.052174 | -61.2807 | 0.047193 | -61.2429 | 60.2671 | 60.1583 | 60.1171 | -61.2558 | -61.2163 | 0.073618 | -61.3058 | 60.0765 | 60.2269 | 60.2393 | -61.3921 | 0.025018 | -0.020391 | 0.000149 | 0.037911 | 0.012893 | -0.12921 | -0.1704 | -0.11127 | -0.21095 | 0.06452 | -0.02493 | 0.086339 | -0.060568 | -0.048209 | 121.5479 | 121.4391 | 121.3979 | 61.328 | -121.5433 | 121.3574 | 121.5077 | 121.5201 | 61.3544 | -121.6796
820.0156 | 121.8704 | -61.3129 | 60.3104 | -0.010149 | -0.028102 | 0.0088826 | 0.057932 | -0.0090872 | 0.051753 | -0.021518 | -0.0016258 | -0.0031451 | 0.059969 | 0.030645 | 0.052174 | -61.2807 | 0.047193 | -61.2292 | 60.2671 | 60.1537 | 60.1171 | -61.265 | -61.2163 | 0.078197 | -61.3058 | 60.0765 | 60.2178 | 60.2393 | -61.3921 | 0.047903 | -0.043279 | 0.032192 | 0.083689 | 0.035786 | -0.15667 | -0.19328 | -0.079226 | -0.23383 | 0.096563 | 0.007113 | 0.086339 | -0.092613 | -0.071097 | 121.58 | 121.4666 | 121.4299 | 61.3601 | -121.5753 | 121.3894 | 121.5306 | 121.5521 | 61.3911 | -121.7025
821.75 | 121.8979 | -61.2991 | 60.2921 | -0.01778 | -0.027889 | 0.0088826 | 0.057932 | -0.0093008 | 0.051753 | -0.021518 | -0.0018394 | -0.0029313 | 0.059969 | 0.030645 | 0.052388 | -61.2761 | 0.038035 | -61.2429 | 60.2762 | 60.1491 | 60.1308 | -61.2558 | -61.2071 | 0.073618 | -61.3012 | 60.0765 | 60.2269 | 60.2301 | -61.4012 | 0.043328 | -0.015811 | 0.023037 | 0.056221 | 0.012893 | -0.14294 | -0.16124 | -0.10212 | -0.21552 | 0.091987 | -0.002041 | 0.10008 | -0.065145 | -0.061943 | 121.5754 | 121.4482 | 121.4299 | 61.3372 | -121.5479 | 121.3757 | 121.526 | 121.5292 | 61.3728 | -121.6933
823.4844 | 121.9345 | -61.2213 | 60.3745 | -0.0025182 | -0.028102 | 0.0088826 | 0.058359 | -0.0086598 | 0.051753 | -0.021518 | -0.002053 | -0.0029313 | 0.059755 | 0.030859 | 0.052388 | -61.2807 | 0.038035 | -61.2383 | 60.2762 | 60.1628 | 60.1171 | -61.2558 | -61.2071 | 0.078197 | -61.3012 | 60.072 | 60.2269 | 60.2393 | -61.4012 | -0.034492 | -0.098209 | -0.059361 | -0.01702 | 0.017472 | -0.2116 | -0.25737 | -0.17994 | -0.3025 | 0.014167 | -0.079861 | 0.10008 | -0.14754 | -0.13518 | 121.4976 | 121.3842 | 121.3384 | 61.2593 | -121.6303 | 121.2933 | 121.4482 | 121.4606 | 61.2995 | -121.7757
825.2344 | 121.8704 | -61.2625 | 60.3928 | -0.0025182 | -0.027889 | 0.0090964 | 0.058359 | -0.0088734 | 0.051753 | -0.021518 | -0.0018394 | -0.0033587 | 0.059755 | 0.030431 | 0.05196 | -61.2853 | 0.042614 | -61.2383 | 60.2762 | 60.1583 | 60.1217 | -61.2558 | -61.2163 | 0.078197 | -61.3058 | 60.072 | 60.2269 | 60.2347 | -61.4012 | 0.006707 | -0.11652 | -0.02274 | 0.024179 | 0.017472 | -0.23449 | -0.2711 | -0.13874 | -0.32081 | 0.046209 | -0.043241 | 0.095497 | -0.16585 | -0.15807 | 121.5388 | 121.4208 | 121.3842 | 61.3051 | -121.6486 | 121.3345 | 121.4894 | 121.4972 | 61.3407 | -121.794
826.9219 | 121.9116 | -61.2442 | 60.347 | -0.01778 | -0.028102 | 0.0088826 | 0.058145 | -0.0093008 | 0.051326 | -0.013887 | -0.0018394 | -0.0031451 | 0.060183 | 0.030218 | 0.051747 | -61.2761 | 0.042614 | -61.2383 | 60.2717 | 60.1628 | 60.1171 | -61.2558 | -61.2117 | 0.078197 | -61.3103 | 60.0765 | 60.2223 | 60.2301 | -61.3967 | -0.011603 | -0.075322 | -0.031894 | 0.005869 | 0.017472 | -0.18414 | -0.2299 | -0.15247 | -0.27045 | 0.032478 | -0.06613 | 0.086339 | -0.12465 | -0.11687 | 121.5159 | 121.4071 | 121.3613 | 61.2868 | -121.6028 | 121.3207 | 121.4665 | 121.4743 | 61.3224 | -121.7437
828.6562 | 121.8979 | -61.2167 | 60.3882 | -0.010149 | -0.028102 | 0.0088826 | 0.058145 | -0.0090872 | 0.051753 | -0.013887 | -0.0018394 | -0.0031451 | 0.059969 | 0.030645 | 0.052174 | -61.2898 | 0.047193 | -61.2383 | 60.2762 | 60.1628 | 60.1171 | -61.2558 | -61.2163 | 0.078197 | -61.3103 | 60.0765 | 60.2223 | 60.2347 | -61.3967 | -0.039069 | -0.11194 | -0.073095 | -0.021597 | 0.017472 | -0.22534 | -0.2711 | -0.17994 | -0.31165 | 0.000433 | -0.093596 | 0.086339 | -0.16585 | -0.1535 | 121.493 | 121.3796 | 121.3338 | 61.2639 | -121.644 | 121.2933 | 121.4391 | 121.4514 | 61.2949 | -121.7849
830.4062 | 121.9299 | -61.29 | 60.2875 | -0.0025182 | -0.028102 | 0.0090964 | 0.057932 | -0.0088734 | 0.05154 | -0.021518 | -0.002053 | -0.0029313 | 0.059969 | 0.030431 | 0.052174 | -61.2807 | 0.047193 | -61.2338 | 60.2762 | 60.1628 | 60.1171 | -61.2604 | -61.2117 | 0.073618 | -61.3103 | 60.0765 | 60.2361 | 60.2347 | -61.3875 | 0.029594 | -0.011234 | 0.009304 | 0.056223 | 0.026629 | -0.12463 | -0.1704 | -0.097535 | -0.21095 | 0.078254 | -0.020354 | 0.077181 | -0.051411 | -0.052788 | 121.5662 | 121.4528 | 121.4071 | 61.3372 | -121.5479 | 121.3665 | 121.526 | 121.5247 | 61.3636 | -121.675
832.1562 | 121.962 | -61.2946 | 60.2875 | -0.010149 | -0.028316 | 0.0090964 | 0.057932 | -0.0086598 | 0.051326 | -0.021518 | -0.0016258 | -0.0031451 | 0.060183 | 0.030431 | 0.05196 | -61.2853 | 0.042614 | -61.2338 | 60.2717 | 60.1674 | 60.1171 | -61.2604 | -61.2117 | 0.078197 | -61.3058 | 60.0765 | 60.2315 | 60.2347 | -61.3967 | 0.034172 | -0.015813 | 0.009304 | 0.060801 | 0.026629 | -0.12005 | -0.1704 | -0.10211 | -0.21095 | 0.082832 | -0.011197 | 0.090918 | -0.055989 | -0.052788 | 121.5662 | 121.462 | 121.4116 | 61.3372 | -121.5479 | 121.3711 | 121.526 | 121.5292 | 61.3728 | -121.6841
833.8438 | 121.8475 | -61.29 | 60.3333 | 0.0051128 | -0.028102 | 0.0088826 | 0.057932 | -0.0090872 | 0.051753 | -0.021518 | -0.002053 | -0.0029313 | 0.059542 | 0.030431 | 0.052174 | -61.2853 | 0.047193 | -61.2338 | 60.2717 | 60.1537 | 60.1262 | -61.2558 | -61.2163 | 0.073618 | -61.3058 | 60.0811 | 60.2315 | 60.2347 | -61.4012 | 0.034173 | -0.061589 | 0.004726 | 0.056223 | 0.02205 | -0.17956 | -0.20701 | -0.11127 | -0.25214 | 0.073675 | -0.015775 | 0.095497 | -0.10177 | -0.098564 | 121.5616 | 121.4437 | 121.4162 | 61.3372 | -121.5891 | 121.3711 | 121.5215 | 121.5247 | 61.3636 | -121.7345
835.5938 | 121.8292 | -61.2167 | 60.4385 | -0.01778 | -0.028316 | 0.0088826 | 0.058145 | -0.0090872 | 0.051753 | -0.0062567 | -0.0018394 | -0.0027177 | 0.060183 | 0.030645 | 0.052174 | -61.2853 | 0.047193 | -61.2383 | 60.2808 | 60.1628 | 60.1125 | -61.2604 | -61.2163 | 0.078197 | -61.3103 | 60.0765 | 60.2269 | 60.2255 | -61.3967 | -0.043648 | -0.15772 | -0.068516 | -0.021597 | 0.022051 | -0.27569 | -0.32604 | -0.17994 | -0.36201 | 0.000433 | -0.093596 | 0.086339 | -0.21163 | -0.21301 | 121.4976 | 121.3796 | 121.3292 | 61.2639 | -121.6989 | 121.2933 | 121.4436 | 121.4423 | 61.2949 | -121.8352
837.3281 | 121.8933 | -61.2625 | 60.3424 | -0.0025182 | -0.028316 | 0.0088826 | 0.057932 | -0.0088734 | 0.05154 | -0.021518 | -0.002053 | -0.0033587 | 0.059542 | 0.030431 | 0.052174 | -61.2807 | 0.051771 | -61.2383 | 60.2717 | 60.1583 | 60.1262 | -61.2466 | -61.2163 | 0.078197 | -61.3012 | 60.0765 | 60.2315 | 60.2393 | -61.3967 | 0.015865 | -0.070744 | -0.018162 | 0.024179 | 0.008314 | -0.18414 | -0.21617 | -0.13416 | -0.26588 | 0.046209 | -0.038662 | 0.095497 | -0.11092 | -0.10314 | 121.5342 | 121.4208 | 121.3888 | 61.3143 | -121.5891 | 121.339 | 121.494 | 121.5018 | 61.3407 | -121.7391
839.0781 | 121.907 | -61.2534 | 60.3424 | -0.010149 | -0.028316 | 0.0088826 | 0.058145 | -0.0088734 | 0.051326 | -0.013887 | -0.002053 | -0.0031451 | 0.059755 | 0.030431 | 0.05196 | -61.2807 | 0.042614 | -61.2338 | 60.2671 | 60.1583 | 60.1171 | -61.2604 | -61.2117 | 0.073618 | -61.3058 | 60.0811 | 60.2269 | 60.2301 | -61.3921 | -0.007027 | -0.075322 | -0.027317 | 0.019602 | 0.026629 | -0.18414 | -0.22533 | -0.13873 | -0.2613 | 0.041633 | -0.052396 | 0.086339 | -0.1155 | -0.1123 | 121.5204 | 121.4116 | 121.3704 | 61.296 | -121.6028 | 121.3345 | 121.4803 | 121.4835 | 61.327 | -121.7345
840.7656 | 121.9116 | -61.2167 | 60.3607 | 0.0051128 | -0.028316 | 0.0090964 | 0.058145 | -0.0086598 | 0.051753 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059969 | 0.030431 | 0.051747 | -61.2807 | 0.047193 | -61.2338 | 60.2762 | 60.1583 | 60.1217 | -61.2604 | -61.2163 | 0.073618 | -61.3058 | 60.0765 | 60.2315 | 60.2347 | -61.3967 | -0.043648 | -0.084476 | -0.063938 | -0.017019 | 0.026629 | -0.20245 | -0.23906 | -0.17994 | -0.28419 | 0.000433 | -0.089017 | 0.090918 | -0.12923 | -0.12603 | 121.493 | 121.375 | 121.3384 | 61.2639 | -121.6211 | 121.2933 | 121.4482 | 121.4514 | 61.2904 | -121.7574
842.5156 | 121.9437 | -61.1984 | 60.4065 | -0.0025182 | -0.028316 | 0.0088826 | 0.058145 | -0.0090872 | 0.051326 | 0.0013733 | -0.0018394 | -0.0035723 | 0.059969 | 0.030859 | 0.052174 | -61.2853 | 0.038035 | -61.2292 | 60.2717 | 60.1628 | 60.1125 | -61.2558 | -61.2117 | 0.078197 | -61.3058 | 60.072 | 60.2269 | 60.2301 | -61.4012 | -0.05738 | -0.13483 | -0.086827 | -0.030752 | 0.026628 | -0.24365 | -0.29399 | -0.20282 | -0.33454 | -0.013299 | -0.10733 | 0.095497 | -0.17959 | -0.17638 | 121.4701 | 121.3613 | 121.3109 | 61.2365 | -121.6623 | 121.2704 | 121.4253 | 121.4285 | 61.2766 | -121.8077
844.2656 | 121.8704 | -61.3174 | 60.3287 | -0.010149 | -0.028316 | 0.0088826 | 0.058145 | -0.0093008 | 0.051753 | -0.013887 | -0.0018394 | -0.0029313 | 0.059755 | 0.030859 | 0.05196 | -61.2807 | 0.042614 | -61.2383 | 60.2717 | 60.1583 | 60.1171 | -61.2512 | -61.2117 | 0.078197 | -61.3012 | 60.0811 | 60.2223 | 60.2255 | -61.3967 | 0.066218 | -0.057011 | 0.03677 | 0.079111 | 0.012893 | -0.1704 | -0.21159 | -0.079227 | -0.24757 | 0.10572 | 0.01627 | 0.095497 | -0.10634 | -0.10314 | 121.5891 | 121.4757 | 121.4345 | 61.3601 | -121.5799 | 121.3986 | 121.5398 | 121.543 | 61.3956 | -121.7253
845.9531 | 121.9803 | -61.1893 | 60.3745 | 0.0051128 | -0.028316 | 0.0090964 | 0.058145 | -0.0090872 | 0.051326 | -0.013887 | -0.002053 | -0.0031451 | 0.059755 | 0.031072 | 0.051747 | -61.2898 | 0.047193 | -61.2338 | 60.2717 | 60.1583 | 60.1125 | -61.2558 | -61.2163 | 0.06904 | -61.3103 | 60.0765 | 60.2223 | 60.2301 | -61.4012 | -0.066535 | -0.10279 | -0.10056 | -0.044485 | 0.02205 | -0.21618 | -0.26195 | -0.21198 | -0.29792 | -0.027033 | -0.12106 | 0.090918 | -0.15212 | -0.14434 | 121.4609 | 121.3475 | 121.3018 | 61.2365 | -121.6303 | 121.2658 | 121.4116 | 121.4194 | 61.2583 | -121.7757
847.7031 | 121.8475 | -61.3037 | 60.3378 | -0.010149 | -0.02853 | 0.0088826 | 0.057718 | -0.0090872 | 0.05154 | -0.0062567 | -0.002053 | -0.0029313 | 0.059969 | 0.030645 | 0.05196 | -61.2898 | 0.042614 | -61.2292 | 60.2808 | 60.1583 | 60.1217 | -61.2604 | -61.2163 | 0.078197 | -61.3058 | 60.0811 | 60.2315 | 60.2438 | -61.3967 | 0.043327 | -0.05701 | 0.01388 | 0.074534 | 0.031207 | -0.17956 | -0.21617 | -0.09296 | -0.25672 | 0.087408 | -0.002042 | 0.090918 | -0.10634 | -0.093985 | 121.5845 | 121.462 | 121.4254 | 61.3463 | -121.5982 | 121.3848 | 121.5352 | 121.5476 | 61.3819 | -121.7345
849.4531 | 121.8338 | -61.3312 | 60.3378 | -0.010149 | -0.028316 | 0.0090964 | 0.057932 | -0.0090872 | 0.051326 | -0.021518 | -0.002053 | -0.0031451 | 0.059755 | 0.030645 | 0.051747 | -61.2807 | 0.042614 | -61.2338 | 60.2762 | 60.1583 | 60.1125 | -61.2604 | -61.2163 | 0.078197 | -61.3012 | 60.072 | 60.2315 | 60.2393 | -61.3967 | 0.070793 | -0.061588 | 0.050503 | 0.097422 | 0.026629 | -0.17956 | -0.22533 | -0.065494 | -0.26588 | 0.11487 | 0.030003 | 0.095497 | -0.10634 | -0.098563 | 121.6074 | 121.4894 | 121.4437 | 61.3738 | -121.5982 | 121.4031 | 121.5627 | 121.5704 | 61.4094 | -121.7345
851.2188 | 121.8796 | -61.2534 | 60.3607 | -0.01778 | -0.028102 | 0.00931 | 0.057932 | -0.0088734 | 0.05154 | -0.0062567 | -0.002053 | -0.0029313 | 0.059755 | 0.030645 | 0.05196 | -61.2853 | 0.047193 | -61.2383 | 60.2717 | 60.1674 | 60.1171 | -61.2604 | -61.2163 | 0.078197 | -61.3058 | 60.072 | 60.2315 | 60.2347 | -61.3967 | -0.007027 | -0.089055 | -0.031895 | 0.015024 | 0.022051 | -0.19329 | -0.24364 | -0.14331 | -0.28877 | 0.037054 | -0.052396 | 0.090918 | -0.12923 | -0.12603 | 121.525 | 121.4208 | 121.3704 | 61.3006 | -121.6211 | 121.3253 | 121.4848 | 121.488 | 61.3316 | -121.7574
852.9688 | 121.9437 | -61.2488 | 60.2829 | -0.0025182 | -0.028316 | 0.0090964 | 0.057718 | -0.0093008 | 0.051326 | -0.021518 | -0.002053 | -0.0031451 | 0.059755 | 0.030859 | 0.05196 | -61.2853 | 0.042614 | -61.2383 | 60.2717 | 60.1628 | 60.1217 | -61.265 | -61.2117 | 0.078197 | -61.3103 | 60.0674 | 60.2269 | 60.2255 | -61.3967 | -0.016184 | -0.011235 | -0.036473 | 0.010446 | 0.02663 | -0.12005 | -0.16124 | -0.14789 | -0.21552 | 0.037055 | -0.061553 | 0.086339 | -0.05599 | -0.057367 | 121.5204 | 121.4116 | 121.3704 | 61.2914 | -121.5479 | 121.3162 | 121.4757 | 121.4743 | 61.327 | -121.6796
854.6406 | 121.8704 | -61.2534 | 60.3699 | -0.0025182 | -0.028316 | 0.0090964 | 0.057932 | -0.0090872 | 0.051753 | -0.021518 | -0.002053 | -0.0031451 | 0.059542 | 0.030859 | 0.051747 | -61.2853 | 0.047193 | -61.2383 | 60.2762 | 60.1583 | 60.1171 | -61.2604 | -61.2163 | 0.082776 | -61.3012 | 60.0765 | 60.2361 | 60.2393 | -61.3967 | -0.007027 | -0.093631 | -0.031895 | 0.015024 | 0.022051 | -0.2116 | -0.25279 | -0.14331 | -0.29334 | 0.037054 | -0.047817 | 0.095497 | -0.13381 | -0.13061 | 121.5296 | 121.4116 | 121.3704 | 61.3006 | -121.6303 | 121.3299 | 121.4894 | 121.4926 | 61.3361 | -121.7665
856.3906 | 121.9299 | -61.2076 | 60.4202 | -0.0025182 | -0.028743 | 0.0088826 | 0.058145 | -0.0090872 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.060183 | 0.030859 | 0.051747 | -61.2853 | 0.038035 | -61.2383 | 60.2762 | 60.1583 | 60.1171 | -61.2558 | -61.2163 | 0.082776 | -61.3058 | 60.0811 | 60.2269 | 60.2347 | -61.4012 | -0.048224 | -0.14398 | -0.077671 | -0.030752 | 0.017472 | -0.26196 | -0.30315 | -0.19367 | -0.33912 | -0.008722 | -0.098172 | 0.095497 | -0.19332 | -0.18554 | 121.4838 | 121.3659 | 121.3247 | 61.2456 | -121.676 | 121.2887 | 121.4345 | 121.4423 | 61.2904 | -121.8215
858.1406 | 121.8796 | -61.2671 | 60.3928 | -0.01778 | -0.028316 | 0.0088826 | 0.057932 | -0.0090872 | 0.05154 | -0.021518 | -0.002053 | -0.0033587 | 0.059542 | 0.030645 | 0.051747 | -61.2853 | 0.038035 | -61.2338 | 60.2717 | 60.1537 | 60.1217 | -61.2604 | -61.2209 | 0.082776 | -61.3103 | 60.0765 | 60.2223 | 60.2393 | -61.4012 | 0.006706 | -0.1211 | -0.018162 | 0.033335 | 0.026629 | -0.23907 | -0.2711 | -0.13416 | -0.31623 | 0.046208 | -0.043242 | 0.090918 | -0.17043 | -0.15349 | 121.5388 | 121.4208 | 121.3887 | 61.3051 | -121.6531 | 121.3436 | 121.4894 | 121.5064 | 61.3499 | -121.794
859.8281 | 121.962 | -61.1984 | 60.3882 | -0.010149 | -0.028102 | 0.0088826 | 0.057932 | -0.0088734 | 0.051967 | -0.021518 | -0.0024804 | -0.0033587 | 0.059969 | 0.031072 | 0.052174 | -61.2807 | 0.038035 | -61.2521 | 60.2671 | 60.1628 | 60.1171 | -61.2558 | -61.2163 | 0.078197 | -61.3058 | 60.072 | 60.2361 | 60.2301 | -61.4012 | -0.05738 | -0.1211 | -0.082249 | -0.053643 | 0.003737 | -0.22534 | -0.2711 | -0.20282 | -0.31623 | -0.017878 | -0.10733 | 0.095497 | -0.15212 | -0.15807 | 121.4655 | 121.3613 | 121.3155 | 61.2365 | -121.644 | 121.2704 | 121.4345 | 121.4285 | 61.2766 | -121.7894
861.5781 | 121.8246 | -61.2213 | 60.4202 | -0.010149 | -0.028102 | 0.00931 | 0.058145 | -0.0090872 | 0.05154 | -0.0062567 | -0.0022666 | -0.0031451 | 0.060183 | 0.030859 | 0.052601 | -61.2853 | 0.042614 | -61.2521 | 60.2671 | 60.1583 | 60.1217 | -61.2604 | -61.2117 | 0.078197 | -61.3103 | 60.0765 | 60.2269 | 60.2347 | -61.4012 | -0.039071 | -0.15314 | -0.063939 | -0.030755 | 0.008316 | -0.26196 | -0.29857 | -0.17994 | -0.3437 | 0.009589 | -0.089019 | 0.090918 | -0.19332 | -0.18554 | 121.4884 | 121.3796 | 121.343 | 61.2639 | -121.6806 | 121.2978 | 121.4482 | 121.456 | 61.2995 | -121.8215
863.3125 | 121.9437 | -61.1755 | 60.3745 | -0.010149 | -0.028316 | 0.0090964 | 0.058145 | -0.0090872 | 0.05154 | -0.013887 | -0.0016258 | -0.0031451 | 0.059755 | 0.030859 | 0.051747 | -61.2853 | 0.047193 | -61.2383 | 60.2762 | 60.1583 | 60.1125 | -61.2558 | -61.2163 | 0.073618 | -61.3058 | 60.0811 | 60.2315 | 60.2347 | -61.4012 | -0.080268 | -0.098209 | -0.10972 | -0.062796 | 0.017472 | -0.21618 | -0.26195 | -0.22571 | -0.29334 | -0.040766 | -0.13022 | 0.095497 | -0.14296 | -0.13976 | 121.4518 | 121.3338 | 121.288 | 61.2227 | -121.6303 | 121.2566 | 121.407 | 121.4102 | 61.2492 | -121.7757
865.0781 | 121.843 | -61.235 | 60.4019 | -0.010149 | -0.02853 | 0.0090964 | 0.057932 | -0.0086598 | 0.051326 | -0.029148 | -0.0018394 | -0.0035723 | 0.059755 | 0.030645 | 0.05196 | -61.2807 | 0.038035 | -61.2429 | 60.2762 | 60.1583 | 60.1217 | -61.265 | -61.2163 | 0.082776 | -61.3012 | 60.072 | 60.2178 | 60.2347 | -61.3967 | -0.029917 | -0.12567 | -0.045628 | -0.007866 | 0.022051 | -0.24365 | -0.28026 | -0.16163 | -0.32996 | 0.018743 | -0.066128 | 0.095497 | -0.18417 | -0.16723 | 121.5113 | 121.3933 | 121.3567 | 61.2731 | -121.6669 | 121.307 | 121.4528 | 121.4697 | 61.3178 | -121.7986
866.75 | 121.9574 | -61.203 | 60.3745 | -0.010149 | -0.028743 | 0.00931 | 0.057718 | -0.0088734 | 0.051326 | -0.013887 | -0.002053 | -0.0033587 | 0.059755 | 0.030859 | 0.05196 | -61.2853 | 0.033457 | -61.2383 | 60.2717 | 60.1583 | 60.1217 | -61.2512 | -61.2117 | 0.078197 | -61.3103 | 60.0811 | 60.2361 | 60.2393 | -61.4058 | -0.048223 | -0.10279 | -0.082249 | -0.03533 | 0.012893 | -0.21618 | -0.25279 | -0.20283 | -0.29334 | -0.008721 | -0.10733 | 0.095497 | -0.13839 | -0.13518 | 121.4747 | 121.3613 | 121.3247 | 61.2365 | -121.6257 | 121.2841 | 121.4391 | 121.4423 | 61.2812 | -121.7803
868.5 | 121.875 | -61.2534 | 60.3745 | -0.01778 | -0.028743 | 0.0088826 | 0.057504 | -0.0093008 | 0.051753 | -0.013887 | -0.002053 | -0.0029313 | 0.059755 | 0.031072 | 0.051747 | -61.2898 | 0.047193 | -61.2521 | 60.2717 | 60.1491 | 60.1171 | -61.2604 | -61.2163 | 0.078197 | -61.3058 | 60.0765 | 60.2223 | 60.2347 | -61.4012 | -0.007027 | -0.10279 | -0.036474 | 0.001289 | 0.008316 | -0.22534 | -0.25737 | -0.14789 | -0.29792 | 0.037054 | -0.052396 | 0.095497 | -0.15212 | -0.13976 | 121.525 | 121.4025 | 121.3704 | 61.3006 | -121.6348 | 121.3299 | 121.4757 | 121.488 | 61.3316 | -121.7757
870.2656 | 121.9574 | -61.1847 | 60.3745 | -0.010149 | -0.02853 | 0.0090964 | 0.058359 | -0.0093008 | 0.051112 | -0.013887 | -0.002053 | -0.0029313 | 0.059755 | 0.030645 | 0.05196 | -61.2807 | 0.038035 | -61.2475 | 60.2717 | 60.1628 | 60.1217 | -61.2604 | -61.2163 | 0.078197 | -61.3149 | 60.0811 | 60.2269 | 60.2301 | -61.4012 | -0.075692 | -0.10279 | -0.095982 | -0.062798 | 0.012894 | -0.2116 | -0.25279 | -0.21656 | -0.29334 | -0.031611 | -0.13022 | 0.08634 | -0.14754 | -0.14434 | 121.4564 | 121.3475 | 121.3064 | 61.2227 | -121.6348 | 121.2658 | 121.4116 | 121.4148 | 61.2629 | -121.7757
871.9531 | 121.8887 | -61.2854 | 60.347 | -0.010149 | -0.02853 | 0.0090964 | 0.057932 | -0.0093008 | 0.05154 | -0.0062567 | -0.0022666 | -0.0033587 | 0.059755 | 0.031072 | 0.052174 | -61.2853 | 0.042614 | -61.2475 | 60.2762 | 60.1583 | 60.1217 | -61.265 | -61.2209 | 0.082776 | -61.3103 | 60.072 | 60.2269 | 60.2393 | -61.3967 | 0.020437 | -0.070743 | 0.000148 | 0.03791 | 0.017473 | -0.18871 | -0.22533 | -0.11127 | -0.27503 | 0.064518 | -0.024932 | 0.086339 | -0.12008 | -0.10772 | 121.5616 | 121.4437 | 121.4071 | 61.328 | -121.6119 | 121.3574 | 121.5123 | 121.5247 | 61.3682 | -121.7437
873.7031 | 121.9711 | -61.2808 | 60.2875 | -0.01778 | -0.028743 | 0.0090964 | 0.057932 | -0.0093008 | 0.05154 | -0.021518 | -0.002053 | -0.0037859 | 0.059755 | 0.031072 | 0.05196 | -61.2807 | 0.033457 | -61.2429 | 60.2762 | 60.1628 | 60.1217 | -61.2558 | -61.2255 | 0.082776 | -61.3012 | 60.0811 | 60.2315 | 60.2301 | -61.4012 | 0.025018 | -0.011234 | 0.000149 | 0.037911 | 0.012893 | -0.12463 | -0.16582 | -0.12043 | -0.20637 | 0.055362 | -0.020351 | 0.10008 | -0.055989 | -0.057366 | 121.5571 | 121.4437 | 121.4025 | 61.3143 | -121.5433 | 121.3619 | 121.5123 | 121.5109 | 61.3636 | -121.6887
875.4531 | 121.8384 | -61.203 | 60.4294 | -0.010149 | -0.02853 | 0.0088826 | 0.057932 | -0.0093008 | 0.051326 | -0.013887 | -0.0022666 | -0.0033587 | 0.059755 | 0.031286 | 0.05196 | -61.2898 | 0.038035 | -61.2429 | 60.2671 | 60.1583 | 60.1262 | -61.2558 | -61.2117 | 0.078197 | -61.3058 | 60.0811 | 60.2315 | 60.2347 | -61.4012 | -0.052802 | -0.1623 | -0.086828 | -0.039909 | 0.012893 | -0.27111 | -0.30314 | -0.19825 | -0.34827 | -0.008721 | -0.10275 | 0.095497 | -0.19789 | -0.19469 | 121.4701 | 121.3613 | 121.3292 | 61.241 | -121.6852 | 121.2841 | 121.4345 | 121.4377 | 61.2812 | -121.8306
877.2031 | 121.9803 | -61.1847 | 60.3928 | -0.01778 | -0.028743 | 0.00931 | 0.057932 | -0.0090872 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059755 | 0.030859 | 0.05196 | -61.2853 | 0.033457 | -61.2475 | 60.2717 | 60.1674 | 60.1217 | -61.2604 | -61.2163 | 0.078197 | -61.3058 | 60.0765 | 60.2315 | 60.2301 | -61.4012 | -0.075692 | -0.1211 | -0.10056 | -0.062798 | 0.012894 | -0.22533 | -0.2711 | -0.21656 | -0.31623 | -0.031611 | -0.12106 | 0.095497 | -0.16127 | -0.16265 | 121.4564 | 121.3521 | 121.3064 | 61.2181 | -121.6531 | 121.2612 | 121.4162 | 121.4148 | 61.2629 | -121.794
878.9531 | 121.9345 | -61.2488 | 60.347 | -0.0025182 | -0.028743 | 0.0088826 | 0.057718 | -0.0088734 | 0.051326 | -0.021518 | -0.0018394 | -0.0035723 | 0.059969 | 0.031072 | 0.052174 | -61.2853 | 0.038035 | -61.2429 | 60.2717 | 60.1628 | 60.1217 | -61.2558 | -61.2071 | 0.078197 | -61.3103 | 60.0948 | 60.2315 | 60.2255 | -61.4058 | -0.007026 | -0.075322 | -0.036473 | 0.005867 | 0.012893 | -0.18414 | -0.22533 | -0.15705 | -0.25214 | 0.041633 | -0.061553 | 0.095497 | -0.1155 | -0.12145 | 121.5204 | 121.4116 | 121.3704 | 61.2868 | -121.6028 | 121.3436 | 121.4803 | 121.4743 | 61.327 | -121.7528
880.6406 | 121.8338 | -61.203 | 60.4248 | 0.0051128 | -0.02853 | 0.00931 | 0.057932 | -0.0090872 | 0.051326 | -0.0062567 | -0.0022666 | -0.0029313 | 0.059755 | 0.031072 | 0.05196 | -61.2853 | 0.033457 | -61.2475 | 60.2762 | 60.1537 | 60.1217 | -61.2558 | -61.2209 | 0.087354 | -61.3058 | 60.0765 | 60.2315 | 60.2301 | -61.3967 | -0.052802 | -0.14856 | -0.082249 | -0.044487 | 0.008315 | -0.27111 | -0.30315 | -0.19367 | -0.34828 | -0.017879 | -0.10275 | 0.090918 | -0.19332 | -0.19469 | 121.4792 | 121.3567 | 121.3247 | 61.2365 | -121.6806 | 121.2795 | 121.4345 | 121.4331 | 61.2904 | -121.8215
882.375 | 121.8292 | -61.2625 | 60.4111 | -0.010149 | -0.028957 | 0.0090964 | 0.057932 | -0.0090872 | 0.05154 | -0.021518 | -0.0022666 | -0.0033587 | 0.059755 | 0.030645 | 0.051747 | -61.2853 | 0.038035 | -61.2383 | 60.2671 | 60.1628 | 60.1217 | -61.265 | -61.2163 | 0.087354 | -61.3058 | 60.0857 | 60.2315 | 60.2301 | -61.4012 | -0.002451 | -0.14399 | -0.02274 | 0.024179 | 0.02663 | -0.24822 | -0.28941 | -0.13874 | -0.32538 | 0.046209 | -0.043241 | 0.095497 | -0.17958 | -0.18096 | 121.5296 | 121.4254 | 121.3842 | 61.3005 | -121.676 | 121.3482 | 121.494 | 121.4926 | 61.3499 | -121.8123
884.125 | 121.8338 | -61.2396 | 60.4294 | -0.010149 | -0.028957 | 0.00931 | 0.057932 | -0.0090872 | 0.05154 | -0.021518 | -0.0018394 | -0.0035723 | 0.059755 | 0.030859 | 0.05196 | -61.2853 | 0.038035 | -61.2429 | 60.2717 | 60.1628 | 60.1171 | -61.2604 | -61.2163 | 0.078197 | -61.3058 | 60.0811 | 60.2315 | 60.2347 | -61.4012 | -0.02076 | -0.15772 | -0.045628 | -0.003288 | 0.017472 | -0.26653 | -0.3123 | -0.16163 | -0.34827 | 0.023321 | -0.066129 | 0.095497 | -0.19789 | -0.19469 | 121.5113 | 121.4025 | 121.3567 | 61.2777 | -121.6898 | 121.3207 | 121.4711 | 121.4743 | 61.3178 | -121.8306
885.8125 | 121.8842 | -61.2808 | 60.3424 | -0.010149 | -0.02853 | 0.0088826 | 0.057932 | -0.0088734 | 0.051753 | -0.013887 | -0.002053 | -0.0031451 | 0.059755 | 0.031286 | 0.05196 | -61.2807 | 0.038035 | -61.2429 | 60.2717 | 60.1674 | 60.1217 | -61.2604 | -61.2209 | 0.078197 | -61.3012 | 60.0811 | 60.2315 | 60.2438 | -61.4104 | 0.020439 | -0.070744 | 0.000149 | 0.037911 | 0.017472 | -0.17498 | -0.22075 | -0.12958 | -0.2613 | 0.059941 | -0.020351 | 0.10923 | -0.11092 | -0.098562 | 121.5525 | 121.4483 | 121.4025 | 61.3189 | -121.6028 | 121.3619 | 121.5123 | 121.5247 | 61.359 | -121.7528
887.5469 | 121.8018 | -61.2991 | 60.3607 | -0.0025182 | -0.028957 | 0.00931 | 0.058145 | -0.0090872 | 0.051326 | -0.013887 | -0.0018394 | -0.0031451 | 0.059542 | 0.0315 | 0.051747 | -61.2807 | 0.038035 | -61.2429 | 60.2762 | 60.1674 | 60.1262 | -61.2604 | -61.2163 | 0.082776 | -61.2966 | 60.0811 | 60.2361 | 60.2347 | -61.4104 | 0.038749 | -0.084476 | 0.018459 | 0.056221 | 0.017472 | -0.19329 | -0.23448 | -0.11127 | -0.27961 | 0.08283 | 0.002538 | 0.11381 | -0.12465 | -0.12603 | 121.5754 | 121.4666 | 121.4254 | 61.3372 | -121.6211 | 121.3802 | 121.5352 | 121.5338 | 61.3819 | -121.7711
889.2969 | 121.8979 | -61.235 | 60.3699 | -0.010149 | -0.028957 | 0.00931 | 0.057932 | -0.0090872 | 0.051753 | -0.013887 | -0.002053 | -0.0029313 | 0.059542 | 0.031286 | 0.05196 | -61.2761 | 0.038035 | -61.2429 | 60.2717 | 60.1583 | 60.1262 | -61.2604 | -61.2163 | 0.078197 | -61.3103 | 60.0857 | 60.2269 | 60.2301 | -61.4012 | -0.025338 | -0.09821 | -0.04105 | -0.007866 | 0.017472 | -0.2116 | -0.24363 | -0.1662 | -0.28419 | 0.018743 | -0.075286 | 0.090918 | -0.14296 | -0.13976 | 121.5067 | 121.3933 | 121.3613 | 61.2731 | -121.6303 | 121.3207 | 121.462 | 121.4652 | 61.3132 | -121.7711
890.9844 | 121.9711 | -61.1938 | 60.3973 | -0.0025182 | -0.028743 | 0.0090964 | 0.057932 | -0.0090872 | 0.052181 | -0.0062567 | -0.0022666 | -0.0029313 | 0.059755 | 0.030859 | 0.051747 | -61.2898 | 0.038035 | -61.2383 | 60.2717 | 60.1628 | 60.1171 | -61.265 | -61.2209 | 0.078197 | -61.3058 | 60.0857 | 60.2315 | 60.2255 | -61.4012 | -0.071115 | -0.12568 | -0.095983 | -0.044485 | 0.02663 | -0.23449 | -0.28026 | -0.2074 | -0.31165 | -0.027034 | -0.11191 | 0.095497 | -0.16585 | -0.17181 | 121.4655 | 121.3567 | 121.3109 | 61.2319 | -121.6623 | 121.2795 | 121.4253 | 121.4194 | 61.272 | -121.7986
892.7188 | 121.9254 | -61.2167 | 60.3745 | -0.01778 | -0.028957 | 0.0090964 | 0.057932 | -0.0093008 | 0.051753 | -0.013887 | -0.0016258 | -0.0031451 | 0.059969 | 0.031286 | 0.051747 | -61.2853 | 0.047193 | -61.2383 | 60.2671 | 60.1628 | 60.1217 | -61.2604 | -61.2117 | 0.078197 | -61.3058 | 60.0765 | 60.2315 | 60.2393 | -61.4104 | -0.043648 | -0.10737 | -0.068516 | -0.021597 | 0.022051 | -0.2116 | -0.25279 | -0.19367 | -0.29792 | 0.005012 | -0.089017 | 0.10465 | -0.14296 | -0.13518 | 121.4838 | 121.3796 | 121.3384 | 61.2639 | -121.6348 | 121.2933 | 121.4482 | 121.456 | 61.2949 | -121.7849
894.4688 | 121.8384 | -61.2534 | 60.3973 | -0.010149 | -0.028957 | 0.0088826 | 0.057932 | -0.0090872 | 0.051753 | -0.013887 | -0.0018394 | -0.0027177 | 0.059969 | 0.031286 | 0.052174 | -61.2807 | 0.038035 | -61.2383 | 60.2671 | 60.1628 | 60.1217 | -61.2558 | -61.2163 | 0.078197 | -61.3012 | 60.0765 | 60.2269 | 60.2301 | -61.4058 | -0.002448 | -0.13025 | -0.027317 | 0.015024 | 0.017472 | -0.23449 | -0.27568 | -0.15247 | -0.32081 | 0.037054 | -0.047817 | 0.10465 | -0.17043 | -0.16723 | 121.5204 | 121.4162 | 121.375 | 61.2914 | -121.6531 | 121.3299 | 121.4803 | 121.4835 | 61.3316 | -121.8032
896.2344 | 121.8567 | -61.322 | 60.3012 | -0.010149 | -0.029171 | 0.0088826 | 0.058145 | -0.0090872 | 0.051753 | -0.0062567 | -0.002053 | -0.0029313 | 0.059755 | 0.0315 | 0.05196 | -61.2853 | 0.042614 | -61.2429 | 60.2808 | 60.1628 | 60.1171 | -61.2604 | -61.2209 | 0.078197 | -61.3103 | 60.0765 | 60.2315 | 60.2393 | -61.4058 | 0.061637 | -0.020388 | 0.036769 | 0.079109 | 0.017472 | -0.13836 | -0.18413 | -0.083808 | -0.22468 | 0.10114 | 0.011689 | 0.095497 | -0.069721 | -0.061941 | 121.6028 | 121.4849 | 121.4391 | 61.3646 | -121.5616 | 121.3986 | 121.5535 | 121.5613 | 61.4002 | -121.707
897.9062 | 121.843 | -61.2396 | 60.434 | -0.01778 | -0.028743 | 0.0090964 | 0.057718 | -0.0093008 | 0.051753 | -0.013887 | -0.0018394 | -0.0035723 | 0.059969 | 0.031072 | 0.05196 | -61.2807 | 0.042614 | -61.2475 | 60.2762 | 60.1628 | 60.1217 | -61.265 | -61.2163 | 0.082776 | -61.3058 | 60.0765 | 60.2315 | 60.2301 | -61.4104 | -0.025339 | -0.15772 | -0.04105 | -0.007866 | 0.017473 | -0.27111 | -0.3123 | -0.17078 | -0.35743 | 0.023321 | -0.066129 | 0.10465 | -0.20247 | -0.20385 | 121.5159 | 121.4025 | 121.3613 | 61.2822 | -121.6989 | 121.3162 | 121.4711 | 121.4697 | 61.3224 | -121.8444
899.6406 | 121.8613 | -61.2442 | 60.4248 | -0.0025182 | -0.028957 | 0.0088826 | 0.057718 | -0.0093008 | 0.051753 | -0.0062567 | -0.002053 | -0.0033587 | 0.059542 | 0.031286 | 0.052174 | -61.2807 | 0.038035 | -61.2429 | 60.2762 | 60.1674 | 60.1354 | -61.265 | -61.2209 | 0.082776 | -61.3058 | 60.0765 | 60.2361 | 60.2347 | -61.3967 | -0.020761 | -0.14856 | -0.036472 | 0.00129 | 0.022051 | -0.25738 | -0.28941 | -0.15247 | -0.34828 | 0.02332 | -0.061551 | 0.090918 | -0.18874 | -0.19012 | 121.5204 | 121.4116 | 121.3796 | 61.2822 | -121.6898 | 121.3207 | 121.4803 | 121.4789 | 61.327 | -121.8215
901.3906 | 121.8292 | -61.2442 | 60.4202 | 0.0051128 | -0.028957 | 0.0090964 | 0.057504 | -0.0088734 | 0.051753 | -0.013887 | -0.0018394 | -0.0031451 | 0.059755 | 0.031072 | 0.05196 | -61.2898 | 0.038035 | -61.2429 | 60.2717 | 60.1674 | 60.1262 | -61.2604 | -61.2117 | 0.078197 | -61.3149 | 60.0811 | 60.2406 | 60.2393 | -61.4104 | -0.016182 | -0.14856 | -0.045629 | 0.00129 | 0.017472 | -0.2528 | -0.29399 | -0.16621 | -0.33912 | 0.032478 | -0.070708 | 0.095498 | -0.17958 | -0.18096 | 121.5159 | 121.4116 | 121.3704 | 61.2822 | -121.6806 | 121.3253 | 121.4848 | 121.4835 | 61.3224 | -121.8306
903.0781 | 121.9116 | -61.235 | 60.3607 | -0.010149 | -0.029171 | 0.0088826 | 0.058145 | -0.0090872 | 0.051753 | -0.013887 | -0.0022666 | -0.0029313 | 0.059969 | 0.031286 | 0.05196 | -61.2853 | 0.047193 | -61.2475 | 60.2717 | 60.1674 | 60.1308 | -61.2558 | -61.2117 | 0.078197 | -61.3103 | 60.0765 | 60.2361 | 60.2347 | -61.4012 | -0.020759 | -0.089055 | -0.050206 | -0.012444 | 0.008315 | -0.19329 | -0.2299 | -0.1662 | -0.28419 | 0.023322 | -0.075286 | 0.090918 | -0.12465 | -0.12603 | 121.5067 | 121.4025 | 121.3659 | 61.2822 | -121.6165 | 121.3116 | 121.4711 | 121.4697 | 61.3132 | -121.762
904.8281 | 121.8842 | -61.2717 | 60.3287 | -0.0025182 | -0.028957 | 0.0088826 | 0.057718 | -0.0090872 | 0.051753 | -0.0062567 | -0.0022666 | -0.0029313 | 0.059755 | 0.031072 | 0.051747 | -61.2853 | 0.042614 | -61.2429 | 60.2717 | 60.1674 | 60.1217 | -61.265 | -61.2117 | 0.078197 | -61.3058 | 60.0811 | 60.2406 | 60.2393 | -61.4058 | 0.006704 | -0.057011 | -0.013585 | 0.028755 | 0.022051 | -0.16125 | -0.20701 | -0.13416 | -0.24757 | 0.059943 | -0.034086 | 0.10008 | -0.08803 | -0.089407 | 121.5433 | 121.4391 | 121.3933 | 61.3143 | -121.5936 | 121.3528 | 121.5123 | 121.5109 | 61.3499 | -121.7345
906.5781 | 121.8521 | -61.235 | 60.4248 | -0.025411 | -0.028957 | 0.0088826 | 0.057718 | -0.0090872 | 0.051753 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.031072 | 0.05196 | -61.2807 | 0.038035 | -61.2429 | 60.2762 | 60.1628 | 60.1217 | -61.2604 | -61.2117 | 0.078197 | -61.3103 | 60.0811 | 60.2361 | 60.2301 | -61.4104 | -0.025338 | -0.14856 | -0.045628 | -0.007866 | 0.017472 | -0.26196 | -0.30315 | -0.17536 | -0.3437 | 0.023322 | -0.075286 | 0.10008 | -0.18874 | -0.19469 | 121.5113 | 121.3979 | 121.3567 | 61.2731 | -121.6852 | 121.3162 | 121.4711 | 121.4652 | 61.3132 | -121.8352
908.3281 | 121.8567 | -61.3312 | 60.3149 | 0.0051128 | -0.028957 | 0.0095236 | 0.058145 | -0.0090872 | 0.051753 | -0.021518 | -0.002053 | -0.0029313 | 0.059969 | 0.030645 | 0.05196 | -61.2807 | 0.047193 | -61.2475 | 60.2762 | 60.1628 | 60.1262 | -61.2558 | -61.2071 | 0.082776 | -61.3058 | 60.0765 | 60.2406 | 60.2301 | -61.4058 | 0.075372 | -0.038699 | 0.050503 | 0.083687 | 0.008315 | -0.15209 | -0.1887 | -0.074652 | -0.23841 | 0.12403 | 0.025424 | 0.10008 | -0.074297 | -0.084831 | 121.6074 | 121.494 | 121.4574 | 61.3784 | -121.5707 | 121.4077 | 121.5718 | 121.5613 | 61.414 | -121.7208
910.0312 | 121.9299 | -61.1938 | 60.3928 | 0.0051128 | -0.029171 | 0.00931 | 0.057932 | -0.0090872 | 0.05154 | -0.021518 | -0.002053 | -0.0033587 | 0.059328 | 0.031072 | 0.052174 | -61.2853 | 0.038035 | -61.2475 | 60.2762 | 60.1674 | 60.1262 | -61.2604 | -61.2117 | 0.073618 | -61.3103 | 60.0811 | 60.2361 | 60.2301 | -61.3967 | -0.066536 | -0.11652 | -0.091404 | -0.053642 | 0.012894 | -0.22533 | -0.26652 | -0.20282 | -0.31165 | -0.017876 | -0.11648 | 0.086339 | -0.1567 | -0.16265 | 121.4701 | 121.3613 | 121.3201 | 61.2319 | -121.6531 | 121.275 | 121.4299 | 121.424 | 61.2675 | -121.7894
911.7812 | 121.8567 | -61.2946 | 60.3333 | -0.010149 | -0.029171 | 0.0090964 | 0.057932 | -0.0093008 | 0.05154 | -0.0062567 | -0.002053 | -0.0031451 | 0.059969 | 0.0315 | 0.051747 | -61.2807 | 0.047193 | -61.2383 | 60.2762 | 60.1628 | 60.1217 | -61.2604 | -61.2071 | 0.073618 | -61.2966 | 60.0765 | 60.2452 | 60.2393 | -61.4058 | 0.034172 | -0.05701 | 0.013882 | 0.056223 | 0.022051 | -0.1704 | -0.21159 | -0.11127 | -0.25672 | 0.08741 | -0.002039 | 0.10923 | -0.088029 | -0.093985 | 121.5708 | 121.4574 | 121.4162 | 61.3417 | -121.5936 | 121.3711 | 121.5398 | 121.5338 | 61.3682 | -121.7391
913.5156 | 121.9116 | -61.2396 | 60.3287 | -0.01778 | -0.029384 | 0.0090964 | 0.057932 | -0.0090872 | 0.05154 | -0.013887 | -0.002053 | -0.0029313 | 0.059969 | 0.031072 | 0.051747 | -61.2853 | 0.038035 | -61.2429 | 60.2762 | 60.1628 | 60.1217 | -61.2604 | -61.2163 | 0.078197 | -61.3149 | 60.0811 | 60.2406 | 60.2347 | -61.4058 | -0.02076 | -0.052432 | -0.045628 | -0.003288 | 0.017472 | -0.16582 | -0.20701 | -0.1662 | -0.24757 | 0.023321 | -0.075286 | 0.090919 | -0.08803 | -0.093986 | 121.5159 | 121.4025 | 121.3613 | 61.2777 | -121.5891 | 121.3207 | 121.4803 | 121.4743 | 61.3178 | -121.7345
915.25 | 121.9849 | -61.1618 | 60.379 | -0.0025182 | -0.029171 | 0.0090964 | 0.057932 | -0.0088734 | 0.051753 | -0.029148 | -0.0022666 | -0.0029313 | 0.059755 | 0.031286 | 0.051747 | -61.2807 | 0.042614 | -61.2429 | 60.2762 | 60.1628 | 60.1171 | -61.265 | -61.2163 | 0.073618 | -61.3012 | 60.0811 | 60.2452 | 60.2393 | -61.4104 | -0.10316 | -0.10279 | -0.11887 | -0.081108 | 0.022051 | -0.21618 | -0.26195 | -0.2486 | -0.29792 | -0.054499 | -0.13937 | 0.10923 | -0.1338 | -0.13976 | 121.438 | 121.3247 | 121.2789 | 61.2044 | -121.644 | 121.2429 | 121.407 | 121.4011 | 61.2354 | -121.7894
916.9375 | 121.8384 | -61.2213 | 60.4294 | -0.0025182 | -0.029171 | 0.0095236 | 0.057718 | -0.0090872 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059755 | 0.031286 | 0.05196 | -61.2898 | 0.042614 | -61.2475 | 60.2762 | 60.1583 | 60.1262 | -61.2558 | -61.2163 | 0.078197 | -61.3103 | 60.0811 | 60.2406 | 60.2393 | -61.4058 | -0.034492 | -0.15314 | -0.068518 | -0.026177 | 0.008315 | -0.27111 | -0.30314 | -0.18452 | -0.34827 | 0.00501 | -0.089019 | 0.095497 | -0.18874 | -0.19011 | 121.4976 | 121.3796 | 121.3476 | 61.2639 | -121.6852 | 121.3024 | 121.462 | 121.4606 | 61.2995 | -121.8352
918.625 | 121.9482 | -61.2808 | 60.2829 | -0.0025182 | -0.029384 | 0.00931 | 0.057932 | -0.0090872 | 0.051753 | -0.021518 | -0.002053 | -0.0033587 | 0.059755 | 0.031286 | 0.05196 | -61.2807 | 0.051771 | -61.2475 | 60.2808 | 60.1628 | 60.1308 | -61.265 | -61.2163 | 0.082776 | -61.3012 | 60.0765 | 60.2406 | 60.2393 | -61.4058 | 0.01586 | -0.002078 | 0.000149 | 0.033333 | 0.017473 | -0.12005 | -0.15208 | -0.12501 | -0.20637 | 0.06452 | -0.020351 | 0.10465 | -0.042254 | -0.043631 | 121.5616 | 121.4437 | 121.4116 | 61.3326 | -121.5479 | 121.3574 | 121.5215 | 121.5201 | 61.3636 | -121.6887
920.375 | 121.9666 | -61.2625 | 60.3104 | -0.010149 | -0.029384 | 0.0088826 | 0.057932 | -0.0090872 | 0.051753 | -0.021518 | -0.0022666 | -0.0033587 | 0.059755 | 0.0315 | 0.051747 | -61.2807 | 0.042614 | -61.2429 | 60.2808 | 60.1628 | 60.1308 | -61.265 | -61.2071 | 0.082776 | -61.3058 | 60.0857 | 60.2361 | 60.2393 | -61.4012 | -0.002451 | -0.029544 | -0.018162 | 0.0196 | 0.022051 | -0.14751 | -0.17955 | -0.13874 | -0.22468 | 0.055366 | -0.043241 | 0.095497 | -0.074299 | -0.071097 | 121.5433 | 121.4254 | 121.3933 | 61.3051 | -121.5753 | 121.3482 | 121.4986 | 121.5018 | 61.3453 | -121.7116
922.125 | 121.8796 | -61.2854 | 60.3836 | -0.0025182 | -0.029384 | 0.0088826 | 0.057718 | -0.0090872 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059755 | 0.031713 | 0.05196 | -61.2807 | 0.038035 | -61.2429 | 60.2717 | 60.1674 | 60.1262 | -61.265 | -61.2209 | 0.073618 | -61.3058 | 60.0811 | 60.2452 | 60.2393 | -61.3967 | 0.020437 | -0.11194 | 0.004726 | 0.042488 | 0.022051 | -0.21618 | -0.25737 | -0.11127 | -0.3025 | 0.064518 | -0.020353 | 0.090918 | -0.13838 | -0.14434 | 121.5571 | 121.4528 | 121.4116 | 61.3234 | -121.6486 | 121.3665 | 121.5306 | 121.5247 | 61.359 | -121.7803
923.7969 | 121.9574 | -61.29 | 60.2921 | -0.0025182 | -0.029384 | 0.0088826 | 0.057718 | -0.0090872 | 0.051753 | -0.021518 | -0.002053 | -0.0033587 | 0.059755 | 0.031713 | 0.051747 | -61.2853 | 0.047193 | -61.2475 | 60.2808 | 60.1628 | 60.1217 | -61.2604 | -61.2117 | 0.078197 | -61.3058 | 60.0857 | 60.2406 | 60.2301 | -61.4012 | 0.029594 | -0.011233 | 0.004726 | 0.042488 | 0.012894 | -0.1292 | -0.17039 | -0.11127 | -0.20637 | 0.078254 | -0.015775 | 0.095497 | -0.051409 | -0.061943 | 121.5708 | 121.4528 | 121.4116 | 61.3372 | -121.5524 | 121.3757 | 121.5306 | 121.5201 | 61.3682 | -121.6933
925.5469 | 121.9299 | -61.1755 | 60.4202 | -0.010149 | -0.029384 | 0.0088826 | 0.057504 | -0.0090872 | 0.05154 | -0.0062567 | -0.0022666 | -0.0033587 | 0.059542 | 0.0315 | 0.05196 | -61.2898 | 0.038035 | -61.2429 | 60.2671 | 60.1628 | 60.1262 | -61.265 | -61.2117 | 0.073618 | -61.3149 | 60.0765 | 60.2315 | 60.2347 | -61.3967 | -0.089426 | -0.15314 | -0.11429 | -0.067375 | 0.022051 | -0.25738 | -0.29399 | -0.22113 | -0.3437 | -0.036187 | -0.13937 | 0.081761 | -0.18874 | -0.18554 | 121.4426 | 121.3384 | 121.3018 | 61.2136 | -121.6852 | 121.2521 | 121.407 | 121.4102 | 61.2492 | -121.8169
927.2969 | 121.9345 | -61.235 | 60.3836 | -0.010149 | -0.029384 | 0.0088826 | 0.057718 | -0.0090872 | 0.05154 | -0.013887 | -0.002053 | -0.0029313 | 0.059755 | 0.0315 | 0.051533 | -61.2898 | 0.042614 | -61.2429 | 60.2717 | 60.1628 | 60.1308 | -61.265 | -61.2163 | 0.073618 | -61.3103 | 60.0811 | 60.2452 | 60.2393 | -61.4104 | -0.029917 | -0.11194 | -0.054785 | -0.007866 | 0.022051 | -0.22076 | -0.25279 | -0.17536 | -0.3025 | 0.018743 | -0.075286 | 0.10008 | -0.13838 | -0.14434 | 121.5067 | 121.3979 | 121.3659 | 61.2777 | -121.6486 | 121.3162 | 121.4803 | 121.4743 | 61.3087 | -121.794
928.9844 | 121.8292 | -61.3358 | 60.3104 | -0.010149 | -0.029384 | 0.00931 | 0.057718 | -0.0090872 | 0.051753 | -0.029148 | -0.0016258 | -0.0031451 | 0.059542 | 0.031713 | 0.051747 | -61.2761 | 0.047193 | -61.2338 | 60.2717 | 60.1674 | 60.1262 | -61.265 | -61.2117 | 0.078197 | -61.3012 | 60.0811 | 60.2452 | 60.2393 | -61.4058 | 0.070791 | -0.038701 | 0.059658 | 0.102 | 0.031208 | -0.14294 | -0.18413 | -0.070075 | -0.22926 | 0.12403 | 0.03458 | 0.10465 | -0.065141 | -0.071097 | 121.6074 | 121.5032 | 121.462 | 61.3829 | -121.5753 | 121.4169 | 121.581 | 121.575 | 61.414 | -121.7162
930.7344 | 121.9254 | -61.2122 | 60.3607 | -0.0025182 | -0.029598 | 0.0090964 | 0.057932 | -0.0093008 | 0.051753 | -0.021518 | -0.0022666 | -0.0029313 | 0.059542 | 0.0315 | 0.05196 | -61.2853 | 0.047193 | -61.2429 | 60.2717 | 60.1674 | 60.1354 | -61.2604 | -61.2163 | 0.078197 | -61.3103 | 60.0811 | 60.2406 | 60.2347 | -61.4104 | -0.048226 | -0.089055 | -0.073094 | -0.030754 | 0.017472 | -0.19329 | -0.22532 | -0.19825 | -0.27961 | -0.004145 | -0.098174 | 0.10008 | -0.12007 | -0.12603 | 121.4838 | 121.3796 | 121.3476 | 61.2594 | -121.6211 | 121.2933 | 121.4528 | 121.4468 | 61.2904 | -121.7711
932.4844 | 121.9711 | -61.1938 | 60.4019 | -0.010149 | -0.029384 | 0.0088826 | 0.058145 | -0.0090872 | 0.051753 | -0.013887 | -0.0024804 | -0.0031451 | 0.059755 | 0.031713 | 0.051533 | -61.2807 | 0.042614 | -61.2475 | 60.2808 | 60.1674 | 60.1308 | -61.2558 | -61.2071 | 0.06904 | -61.3149 | 60.0811 | 60.2361 | 60.253 | -61.4058 | -0.061957 | -0.1211 | -0.086826 | -0.053642 | 0.008315 | -0.23449 | -0.2711 | -0.21198 | -0.32081 | -0.013298 | -0.12106 | 0.090919 | -0.16585 | -0.14891 | 121.4747 | 121.3613 | 121.3247 | 61.2365 | -121.6577 | 121.275 | 121.4299 | 121.4469 | 61.2629 | -121.8077
934.1719 | 121.8155 | -61.3495 | 60.3195 | -0.01778 | -0.029171 | 0.00931 | 0.057718 | -0.0090872 | 0.051753 | -0.013887 | -0.0022666 | -0.0033587 | 0.059542 | 0.0315 | 0.051747 | -61.2853 | 0.038035 | -61.2475 | 60.2808 | 60.1766 | 60.1262 | -61.265 | -61.2117 | 0.073618 | -61.3058 | 60.0857 | 60.2406 | 60.2438 | -61.4058 | 0.084524 | -0.038699 | 0.064235 | 0.102 | 0.017473 | -0.14293 | -0.19328 | -0.056342 | -0.23383 | 0.13776 | 0.043734 | 0.10008 | -0.078875 | -0.075674 | 121.6303 | 121.5261 | 121.4757 | 61.3875 | -121.5845 | 121.4352 | 121.5901 | 121.5933 | 61.4231 | -121.7253
935.875 | 121.8292 | -61.3083 | 60.3149 | -0.010149 | -0.029171 | 0.0090964 | 0.057718 | -0.0093008 | 0.05154 | -0.013887 | -0.0018394 | -0.0029313 | 0.059542 | 0.031286 | 0.051747 | -61.2853 | 0.042614 | -61.2429 | 60.2808 | 60.1674 | 60.1262 | -61.2558 | -61.2163 | 0.078197 | -61.3103 | 60.0811 | 60.2406 | 60.2347 | -61.4012 | 0.052484 | -0.034121 | 0.023037 | 0.065377 | 0.012893 | -0.14751 | -0.1887 | -0.092961 | -0.23383 | 0.091986 | -0.002043 | 0.090918 | -0.074297 | -0.080253 | 121.5891 | 121.4757 | 121.4345 | 61.3509 | -121.5707 | 121.3894 | 121.5489 | 121.543 | 61.3865 | -121.7162
937.6094 | 121.8658 | -61.2854 | 60.3424 | -0.0025182 | -0.029171 | 0.0090964 | 0.057718 | -0.0093008 | 0.051326 | -0.021518 | -0.0022666 | -0.0029313 | 0.059969 | 0.0315 | 0.05196 | -61.2807 | 0.047193 | -61.2429 | 60.2762 | 60.1766 | 60.1262 | -61.265 | -61.2117 | 0.078197 | -61.3149 | 60.0811 | 60.2361 | 60.2393 | -61.4058 | 0.020437 | -0.066165 | 0.004726 | 0.042488 | 0.022051 | -0.16582 | -0.21617 | -0.12043 | -0.2613 | 0.073676 | -0.02951 | 0.090919 | -0.10634 | -0.10314 | 121.5616 | 121.462 | 121.4116 | 61.3326 | -121.6074 | 121.3665 | 121.5215 | 121.5247 | 61.3636 | -121.7482
939.3438 | 121.8521 | -61.2946 | 60.3378 | -0.0025182 | -0.029384 | 0.00931 | 0.057932 | -0.0095144 | 0.051326 | -0.021518 | -0.002053 | -0.0031451 | 0.060183 | 0.031286 | 0.051747 | -61.2715 | 0.047193 | -61.2475 | 60.2808 | 60.1674 | 60.1354 | -61.2604 | -61.2117 | 0.073618 | -61.3149 | 60.0811 | 60.2361 | 60.2484 | -61.4012 | 0.034172 | -0.05701 | 0.023039 | 0.047066 | 0.012894 | -0.1704 | -0.20243 | -0.10669 | -0.25672 | 0.082832 | -0.020354 | 0.08634 | -0.10176 | -0.089406 | 121.5754 | 121.462 | 121.43 | 61.3417 | -121.5982 | 121.3757 | 121.5306 | 121.543 | 61.3682 | -121.7391
941.1094 | 121.9299 | -61.2808 | 60.3424 | -0.01778 | -0.029598 | 0.00931 | 0.057932 | -0.0090872 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059969 | 0.031286 | 0.052388 | -61.2898 | 0.047193 | -61.2521 | 60.2808 | 60.172 | 60.1308 | -61.2604 | -61.2163 | 0.073618 | -61.3058 | 60.0811 | 60.2406 | 60.2393 | -61.4104 | 0.020439 | -0.061587 | -0.009008 | 0.028755 | 0.008316 | -0.1704 | -0.21159 | -0.12958 | -0.2613 | 0.06452 | -0.02493 | 0.10465 | -0.10176 | -0.10314 | 121.5616 | 121.4528 | 121.4116 | 61.328 | -121.6028 | 121.3619 | 121.5215 | 121.5201 | 61.3544 | -121.7528
942.7969 | 121.9666 | -61.2122 | 60.3653 | -0.01778 | -0.029598 | 0.0090964 | 0.057932 | -0.0095144 | 0.051753 | -0.013887 | -0.0016258 | -0.0031451 | 0.060183 | 0.0315 | 0.052174 | -61.2853 | 0.042614 | -61.2521 | 60.2762 | 60.1628 | 60.1262 | -61.2695 | -61.2163 | 0.073618 | -61.3103 | 60.0857 | 60.2361 | 60.2393 | -61.4012 | -0.057384 | -0.089053 | -0.073094 | -0.03991 | 0.017474 | -0.20245 | -0.23906 | -0.18909 | -0.27961 | -0.004145 | -0.098174 | 0.090918 | -0.12923 | -0.12603 | 121.4884 | 121.375 | 121.3384 | 61.2548 | -121.6348 | 121.2978 | 121.4482 | 121.4514 | 61.2858 | -121.7665
944.5312 | 121.9711 | -61.1938 | 60.4156 | -0.010149 | -0.029598 | 0.0090964 | 0.057932 | -0.0093008 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059755 | 0.031713 | 0.05196 | -61.2807 | 0.033457 | -61.2429 | 60.2808 | 60.1674 | 60.1262 | -61.2604 | -61.2071 | 0.073618 | -61.3058 | 60.0857 | 60.2406 | 60.2347 | -61.4058 | -0.066536 | -0.13483 | -0.086826 | -0.049064 | 0.017472 | -0.24822 | -0.28941 | -0.21198 | -0.32996 | -0.013298 | -0.11191 | 0.10008 | -0.175 | -0.18096 | 121.4747 | 121.3613 | 121.3201 | 61.2273 | -121.676 | 121.2795 | 121.4345 | 121.4285 | 61.2675 | -121.8215
946.2344 | 121.9345 | -61.1984 | 60.4065 | -0.01778 | -0.029812 | 0.00931 | 0.058145 | -0.0090872 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.0315 | 0.05196 | -61.2807 | 0.038035 | -61.2475 | 60.2808 | 60.1674 | 60.1308 | -61.265 | -61.2163 | 0.078197 | -61.3012 | 60.0765 | 60.2406 | 60.2393 | -61.4058 | -0.066538 | -0.12567 | -0.082249 | -0.049065 | 0.017473 | -0.23907 | -0.27568 | -0.2074 | -0.32996 | -0.017878 | -0.10275 | 0.10465 | -0.16585 | -0.16723 | 121.4792 | 121.3659 | 121.3292 | 61.2365 | -121.6715 | 121.275 | 121.4391 | 121.4377 | 61.2766 | -121.8123
947.9688 | 121.8567 | -61.2305 | 60.4156 | -0.010149 | -0.029812 | 0.0088826 | 0.057291 | -0.0093008 | 0.05154 | -0.013887 | -0.0018394 | -0.0035723 | 0.059755 | 0.031286 | 0.051747 | -61.2853 | 0.042614 | -61.2475 | 60.2808 | 60.1674 | 60.1262 | -61.2604 | -61.2209 | 0.078197 | -61.3149 | 60.0857 | 60.2361 | 60.2393 | -61.4104 | -0.029915 | -0.13483 | -0.054783 | -0.017021 | 0.012894 | -0.24822 | -0.28941 | -0.17994 | -0.32996 | 0.009587 | -0.084441 | 0.095498 | -0.17958 | -0.17638 | 121.5113 | 121.3979 | 121.3567 | 61.2731 | -121.676 | 121.3162 | 121.4665 | 121.4697 | 61.3087 | -121.8261
949.7188 | 121.8796 | -61.2717 | 60.3516 | -0.010149 | -0.029598 | 0.0090964 | 0.057718 | -0.0093008 | 0.051326 | -0.021518 | -0.0022666 | -0.0029313 | 0.059755 | 0.031927 | 0.05196 | -61.2761 | 0.047193 | -61.2475 | 60.2762 | 60.172 | 60.1354 | -61.2741 | -61.2071 | 0.087354 | -61.3058 | 60.0857 | 60.2361 | 60.2438 | -61.4058 | -0.002454 | -0.07532 | -0.004429 | 0.024177 | 0.026631 | -0.17956 | -0.21617 | -0.13416 | -0.26588 | 0.064521 | -0.034086 | 0.10008 | -0.1155 | -0.10772 | 121.5479 | 121.4437 | 121.4071 | 61.3189 | -121.6257 | 121.3574 | 121.5077 | 121.5155 | 61.359 | -121.7574
951.4062 | 121.8979 | -61.1938 | 60.4202 | 0.0051128 | -0.029598 | 0.0095236 | 0.057932 | -0.0093008 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.059755 | 0.0315 | 0.052174 | -61.2853 | 0.042614 | -61.2475 | 60.2854 | 60.1674 | 60.1308 | -61.2558 | -61.2163 | 0.078197 | -61.3103 | 60.0857 | 60.2406 | 60.2301 | -61.4058 | -0.061957 | -0.13483 | -0.091404 | -0.053642 | 0.008315 | -0.2528 | -0.28941 | -0.21198 | -0.33454 | -0.022455 | -0.11648 | 0.095497 | -0.17958 | -0.19012 | 121.4792 | 121.3613 | 121.3247 | 61.2365 | -121.676 | 121.2795 | 121.4345 | 121.424 | 61.272 | -121.8261
953.1562 | 121.8887 | -61.3083 | 60.2966 | -0.0025182 | -0.029598 | 0.0090964 | 0.057932 | -0.0093008 | 0.051326 | -0.013887 | -0.002053 | -0.0031451 | 0.059969 | 0.031072 | 0.051747 | -61.2853 | 0.047193 | -61.2521 | 60.2808 | 60.172 | 60.1354 | -61.265 | -61.2209 | 0.073618 | -61.3058 | 60.0857 | 60.2406 | 60.2393 | -61.4104 | 0.043326 | -0.015811 | 0.023037 | 0.056221 | 0.012895 | -0.12462 | -0.16124 | -0.10212 | -0.21094 | 0.087407 | 0.002536 | 0.10465 | -0.055987 | -0.057364 | 121.5891 | 121.4803 | 121.4437 | 61.3555 | -121.5616 | 121.394 | 121.5489 | 121.5476 | 61.3819 | -121.707
954.8438 | 121.8658 | -61.2305 | 60.4111 | -0.01778 | -0.030025 | 0.00931 | 0.057932 | -0.0093008 | 0.051326 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.0315 | 0.051533 | -61.2807 | 0.047193 | -61.2429 | 60.2762 | 60.172 | 60.14 | -61.2695 | -61.2071 | 0.06904 | -61.3149 | 60.0857 | 60.2361 | 60.2484 | -61.4058 | -0.039073 | -0.13483 | -0.050205 | -0.012443 | 0.02663 | -0.23907 | -0.2711 | -0.17536 | -0.32538 | 0.023323 | -0.084441 | 0.090919 | -0.17501 | -0.16265 | 121.5067 | 121.4025 | 121.3704 | 61.2777 | -121.6806 | 121.3162 | 121.4665 | 121.4789 | 61.2995 | -121.8169
956.5938 | 121.9482 | -61.1893 | 60.4202 | -0.0025182 | -0.029598 | 0.0088826 | 0.057932 | -0.0093008 | 0.051753 | -0.0062567 | -0.0018394 | -0.0033587 | 0.059755 | 0.031927 | 0.05196 | -61.2898 | 0.042614 | -61.2383 | 60.2808 | 60.1674 | 60.1308 | -61.2604 | -61.2117 | 0.073618 | -61.3103 | 60.0857 | 60.2406 | 60.2393 | -61.4104 | -0.071114 | -0.13941 | -0.10056 | -0.049063 | 0.022051 | -0.2528 | -0.28941 | -0.22114 | -0.33454 | -0.022454 | -0.12106 | 0.10008 | -0.17958 | -0.18096 | 121.4701 | 121.3567 | 121.3201 | 61.2319 | -121.6806 | 121.275 | 121.4299 | 121.4285 | 61.2629 | -121.8306
958.2812 | 121.8567 | -61.322 | 60.3424 | -0.0025182 | -0.029598 | 0.0095236 | 0.057718 | -0.0095144 | 0.051326 | -0.021518 | -0.002053 | -0.0027177 | 0.059969 | 0.031927 | 0.05196 | -61.2807 | 0.047193 | -61.2429 | 60.2762 | 60.172 | 60.14 | -61.2558 | -61.2071 | 0.078197 | -61.3012 | 60.0903 | 60.2452 | 60.2438 | -61.4058 | 0.066216 | -0.066165 | 0.041347 | 0.079109 | 0.012893 | -0.1704 | -0.20243 | -0.083808 | -0.25214 | 0.11487 | 0.020847 | 0.10465 | -0.097184 | -0.098562 | 121.5983 | 121.494 | 121.462 | 61.3692 | -121.5982 | 121.4123 | 121.5672 | 121.5659 | 61.4002 | -121.7482
960.0312 | 121.9666 | -61.1893 | 60.379 | 0.0051128 | -0.029812 | 0.0090964 | 0.057718 | -0.0090872 | 0.051753 | -0.021518 | -0.0018394 | -0.0031451 | 0.059542 | 0.031927 | 0.05196 | -61.2853 | 0.042614 | -61.2521 | 60.2808 | 60.1674 | 60.1354 | -61.265 | -61.2071 | 0.078197 | -61.3149 | 60.0811 | 60.2361 | 60.2393 | -61.4104 | -0.075693 | -0.098208 | -0.095982 | -0.062798 | 0.012895 | -0.2116 | -0.24363 | -0.22114 | -0.29792 | -0.017876 | -0.12564 | 0.095498 | -0.14296 | -0.13976 | 121.4701 | 121.3567 | 121.3247 | 61.2319 | -121.644 | 121.2704 | 121.4253 | 121.4285 | 61.2675 | -121.7894
961.7344 | 121.8521 | -61.3083 | 60.3424 | -0.010149 | -0.029598 | 0.0088826 | 0.057932 | -0.0090872 | 0.051753 | -0.021518 | -0.0022666 | -0.0029313 | 0.059542 | 0.031713 | 0.05196 | -61.2853 | 0.047193 | -61.2475 | 60.2808 | 60.172 | 60.1354 | -61.2695 | -61.2071 | 0.078197 | -61.3103 | 60.0857 | 60.2406 | 60.2438 | -61.4012 | 0.038747 | -0.061587 | 0.023037 | 0.060799 | 0.022052 | -0.1704 | -0.20701 | -0.092961 | -0.25672 | 0.10114 | -0.002043 | 0.090918 | -0.10176 | -0.098562 | 121.5891 | 121.4803 | 121.4437 | 61.3555 | -121.6119 | 121.394 | 121.5489 | 121.5521 | 61.3865 | -121.7437
963.4688 | 121.8613 | -61.3037 | 60.3516 | -0.010149 | -0.029598 | 0.0090964 | 0.057718 | -0.0088734 | 0.05154 | -0.029148 | -0.002053 | -0.0031451 | 0.059969 | 0.0315 | 0.051747 | -61.2853 | 0.047193 | -61.2475 | 60.2762 | 60.1674 | 60.1354 | -61.2695 | -61.2071 | 0.073618 | -61.3058 | 60.0765 | 60.2452 | 60.2438 | -61.3967 | 0.034169 | -0.07532 | 0.018459 | 0.056221 | 0.022052 | -0.18413 | -0.21617 | -0.09296 | -0.27503 | 0.096565 | -0.002042 | 0.090918 | -0.10634 | -0.10772 | 121.58 | 121.4711 | 121.4391 | 61.3509 | -121.6211 | 121.3802 | 121.5489 | 121.5476 | 61.3773 | -121.7482
965.2188 | 121.8521 | -61.2305 | 60.4477 | -0.010149 | -0.030025 | 0.0090964 | 0.057504 | -0.0090872 | 0.051967 | -0.0062567 | -0.002053 | -0.0029313 | 0.059542 | 0.032141 | 0.051533 | -61.2898 | 0.047193 | -61.2521 | 60.2808 | 60.1674 | 60.1354 | -61.2604 | -61.2071 | 0.082776 | -61.2966 | 60.0811 | 60.2361 | 60.2347 | -61.4058 | -0.029915 | -0.16687 | -0.059362 | -0.021599 | 0.008316 | -0.28027 | -0.3123 | -0.17536 | -0.36658 | 0.023323 | -0.066126 | 0.10923 | -0.21163 | -0.21301 | 121.5113 | 121.3979 | 121.3659 | 61.2777 | -121.7081 | 121.3116 | 121.4665 | 121.4652 | 61.3132 | -121.8535
966.9062 | 121.907 | -61.2259 | 60.3699 | -0.01778 | -0.030025 | 0.00931 | 0.057504 | -0.0093008 | 0.051326 | -0.0062567 | -0.0018394 | -0.0027177 | 0.059542 | 0.0315 | 0.05196 | -61.2853 | 0.047193 | -61.2475 | 60.2808 | 60.1674 | 60.1354 | -61.2604 | -61.2163 | 0.073618 | -61.3103 | 60.0948 | 60.2361 | 60.2393 | -61.3967 | -0.034493 | -0.089053 | -0.059361 | -0.021599 | 0.012894 | -0.20245 | -0.23448 | -0.17078 | -0.27503 | 0.009588 | -0.084441 | 0.086339 | -0.13381 | -0.13061 | 121.5067 | 121.3933 | 121.3613 | 61.2731 | -121.6303 | 121.3207 | 121.462 | 121.4652 | 61.2995 | -121.7665
968.6562 | 121.9666 | -61.1938 | 60.4019 | -0.010149 | -0.029812 | 0.0088826 | 0.057504 | -0.0093008 | 0.05154 | -0.013887 | -0.0018394 | -0.0031451 | 0.059755 | 0.031713 | 0.051747 | -61.2807 | 0.047193 | -61.2475 | 60.2762 | 60.1674 | 60.1354 | -61.2695 | -61.2117 | 0.082776 | -61.3058 | 60.0765 | 60.2406 | 60.2438 | -61.4058 | -0.075694 | -0.12567 | -0.086826 | -0.053642 | 0.022052 | -0.23449 | -0.26652 | -0.21198 | -0.32539 | -0.017876 | -0.11191 | 0.10008 | -0.16127 | -0.15807 | 121.4701 | 121.3613 | 121.3292 | 61.241 | -121.6715 | 121.2704 | 121.4345 | 121.4377 | 61.2766 | -121.8077
970.3438 | 121.8887 | -61.3037 | 60.2692 | 0.0051128 | -0.029812 | 0.00931 | 0.057932 | -0.0088734 | 0.05154 | 0.0013733 | -0.0022666 | -0.0031451 | 0.059969 | 0.031927 | 0.051747 | -61.2853 | 0.05635 | -61.2429 | 60.2854 | 60.1628 | 60.14 | -61.2604 | -61.2117 | 0.078197 | -61.3103 | 60.0857 | 60.2361 | 60.2438 | -61.3967 | 0.043327 | 0.016233 | 0.018459 | 0.060799 | 0.017472 | -0.10632 | -0.12919 | -0.09296 | -0.18348 | 0.091987 | -0.006621 | 0.086339 | -0.0331 | -0.02532 | 121.5891 | 121.4666 | 121.4437 | 61.3601 | -121.5295 | 121.3894 | 121.5398 | 121.5476 | 61.3819 | -121.6658
972.0781 | 121.9116 | -61.2396 | 60.3699 | -0.010149 | -0.029812 | 0.0090964 | 0.057932 | -0.0095144 | 0.05154 | -0.0062567 | -0.0024804 | -0.0033587 | 0.059542 | 0.031927 | 0.052174 | -61.2853 | 0.05635 | -61.2475 | 60.2762 | 60.1628 | 60.1354 | -61.2604 | -61.2117 | 0.078197 | -61.3012 | 60.0857 | 60.2406 | 60.2438 | -61.4012 | -0.02076 | -0.093631 | -0.045628 | -0.007866 | 0.012894 | -0.20702 | -0.23448 | -0.16163 | -0.28419 | 0.0279 | -0.06155 | 0.10008 | -0.12923 | -0.12603 | 121.5159 | 121.4025 | 121.375 | 61.296 | -121.6303 | 121.3253 | 121.4803 | 121.4835 | 61.3178 | -121.7711
973.8125 | 121.9803 | -61.2076 | 60.3836 | -0.010149 | -0.030239 | 0.0088826 | 0.057718 | -0.0093008 | 0.051753 | -0.013887 | -0.0022666 | -0.0029313 | 0.059755 | 0.031927 | 0.05196 | -61.2853 | 0.042614 | -61.2475 | 60.2854 | 60.172 | 60.1308 | -61.2604 | -61.2117 | 0.078197 | -61.3058 | 60.0903 | 60.2452 | 60.2438 | -61.4058 | -0.052803 | -0.098208 | -0.077671 | -0.039909 | 0.012894 | -0.2116 | -0.25279 | -0.19825 | -0.29334 | -0.004143 | -0.098172 | 0.10008 | -0.13838 | -0.13976 | 121.493 | 121.3796 | 121.3384 | 61.2502 | -121.644 | 121.2978 | 121.4528 | 121.4514 | 61.2858 | -121.7894
975.5625 | 121.8521 | -61.2442 | 60.4111 | -0.0025182 | -0.030025 | 0.008669 | 0.058145 | -0.0093008 | 0.05154 | -0.0062567 | -0.002053 | -0.0029313 | 0.059542 | 0.031713 | 0.052174 | -61.2853 | 0.042614 | -61.2475 | 60.2808 | 60.1766 | 60.1308 | -61.2695 | -61.2117 | 0.078197 | -61.3103 | 60.0811 | 60.2452 | 60.2438 | -61.4058 | -0.02534 | -0.13025 | -0.04105 | -0.003288 | 0.022052 | -0.23449 | -0.28026 | -0.16163 | -0.32996 | 0.032478 | -0.06613 | 0.095497 | -0.16585 | -0.16723 | 121.525 | 121.4208 | 121.375 | 61.2868 | -121.6806 | 121.3253 | 121.4894 | 121.488 | 61.3224 | -121.8169
977.25 | 121.875 | -61.2076 | 60.4156 | 0.0051128 | -0.029812 | 0.008669 | 0.057718 | -0.0093008 | 0.051326 | -0.013887 | -0.0022666 | -0.0031451 | 0.059328 | 0.031713 | 0.05196 | -61.2853 | 0.042614 | -61.2429 | 60.2808 | 60.172 | 60.14 | -61.265 | -61.2209 | 0.073618 | -61.3012 | 60.0811 | 60.2406 | 60.2347 | -61.3967 | -0.057382 | -0.13483 | -0.077671 | -0.035331 | 0.022051 | -0.24364 | -0.27568 | -0.18909 | -0.33454 | -0.013301 | -0.093593 | 0.095497 | -0.175 | -0.18096 | 121.4884 | 121.3796 | 121.3476 | 61.2502 | -121.6806 | 121.2887 | 121.4482 | 121.4423 | 61.2812 | -121.8123
979 | 121.8246 | -61.3129 | 60.3424 | -0.0025182 | -0.030025 | 0.0090964 | 0.057504 | -0.0093008 | 0.051326 | -0.029148 | -0.0022666 | -0.0031451 | 0.059755 | 0.031927 | 0.052174 | -61.2853 | 0.047193 | -61.2521 | 60.29 | 60.1766 | 60.14 | -61.265 | -61.2117 | 0.073618 | -61.3103 | 60.0948 | 60.2406 | 60.2438 | -61.4058 | 0.047903 | -0.05243 | 0.027614 | 0.060798 | 0.012895 | -0.16582 | -0.20243 | -0.092963 | -0.24756 | 0.10114 | 0.002534 | 0.095497 | -0.10176 | -0.098562 | 121.6028 | 121.4895 | 121.4528 | 61.3601 | -121.6074 | 121.4077 | 121.5535 | 121.5567 | 61.3865 | -121.7482
980.75 | 121.9711 | -61.2808 | 60.2737 | -0.0025182 | -0.029812 | 0.0088826 | 0.057932 | -0.0093008 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.031927 | 0.051747 | -61.2807 | 0.047193 | -61.2475 | 60.2808 | 60.172 | 60.1354 | -61.2604 | -61.2163 | 0.078197 | -61.3058 | 60.0857 | 60.2406 | 60.2393 | -61.4104 | 0.020439 | 0.007077 | 0.000149 | 0.033333 | 0.012894 | -0.10174 | -0.13835 | -0.12958 | -0.18806 | 0.06452 | -0.02493 | 0.10465 | -0.033099 | -0.034476 | 121.5616 | 121.4528 | 121.4162 | 61.328 | -121.5341 | 121.3665 | 121.5215 | 121.5201 | 61.359 | -121.6842
982.4375 | 121.9391 | -61.2946 | 60.2966 | -0.010149 | -0.030239 | 0.00931 | 0.057718 | -0.0095144 | 0.051967 | -0.021518 | -0.002053 | -0.0029313 | 0.059969 | 0.031713 | 0.051747 | -61.2807 | 0.042614 | -61.2475 | 60.2762 | 60.1674 | 60.1354 | -61.2695 | -61.2163 | 0.087354 | -61.3058 | 60.0857 | 60.2452 | 60.2347 | -61.4058 | 0.025014 | -0.020389 | 0.013882 | 0.047066 | 0.022052 | -0.1292 | -0.16124 | -0.11127 | -0.21094 | 0.078253 | -0.011197 | 0.10008 | -0.051408 | -0.061943 | 121.5708 | 121.462 | 121.43 | 61.3372 | -121.5662 | 121.3802 | 121.5398 | 121.5292 | 61.3819 | -121.7025
984.1875 | 121.9482 | -61.2671 | 60.2875 | -0.0025182 | -0.029812 | 0.0090964 | 0.057932 | -0.0093008 | 0.051326 | -0.013887 | -0.0024804 | -0.0029313 | 0.059755 | 0.032141 | 0.051747 | -61.2853 | 0.047193 | -61.2475 | 60.2808 | 60.172 | 60.14 | -61.265 | -61.2117 | 0.082776 | -61.3058 | 60.0903 | 60.2498 | 60.2347 | -61.4058 | 0.002127 | -0.006656 | -0.018162 | 0.0196 | 0.017473 | -0.11547 | -0.1475 | -0.13874 | -0.19721 | 0.055366 | -0.038663 | 0.10008 | -0.037675 | -0.052788 | 121.5479 | 121.4391 | 121.4071 | 61.3143 | -121.5524 | 121.3574 | 121.5169 | 121.5018 | 61.3499 | -121.6933
985.9375 | 121.8384 | -61.3312 | 60.3149 | -0.0025182 | -0.029812 | 0.008669 | 0.057932 | -0.0095144 | 0.05154 | 0.0013733 | -0.002053 | -0.0029313 | 0.059969 | 0.032141 | 0.051747 | -61.2807 | 0.042614 | -61.2475 | 60.2854 | 60.1766 | 60.1446 | -61.2604 | -61.2071 | 0.073618 | -61.3058 | 60.0857 | 60.2406 | 60.2393 | -61.4058 | 0.070793 | -0.029543 | 0.050503 | 0.083687 | 0.012894 | -0.13836 | -0.17039 | -0.074652 | -0.22925 | 0.12403 | 0.025424 | 0.10008 | -0.074297 | -0.075674 | 121.6166 | 121.5078 | 121.4757 | 61.3738 | -121.5753 | 121.4169 | 121.5718 | 121.5704 | 61.4048 | -121.7208
987.625 | 121.8384 | -61.2259 | 60.4065 | -0.01778 | -0.029812 | 0.0090964 | 0.057932 | -0.0093008 | 0.051326 | -0.021518 | -0.0024804 | -0.0033587 | 0.059755 | 0.031927 | 0.051533 | -61.2807 | 0.038035 | -61.2566 | 60.2854 | 60.172 | 60.1354 | -61.265 | -61.2163 | 0.073618 | -61.3012 | 60.0857 | 60.2452 | 60.2393 | -61.4012 | -0.039072 | -0.1211 | -0.054783 | -0.030755 | 0.008317 | -0.23449 | -0.2711 | -0.17536 | -0.32081 | 0.009588 | -0.075283 | 0.10008 | -0.16127 | -0.16723 | 121.5113 | 121.3979 | 121.3613 | 61.2639 | -121.6715 | 121.3116 | 121.4711 | 121.4652 | 61.2995 | -121.8077
989.375 | 121.8567 | -61.235 | 60.4385 | -0.010149 | -0.030025 | 0.0090964 | 0.057718 | -0.0095144 | 0.05154 | 0.0013733 | -0.002053 | -0.0031451 | 0.059755 | 0.031927 | 0.05196 | -61.2807 | 0.042614 | -61.2521 | 60.2717 | 60.172 | 60.1354 | -61.265 | -61.2117 | 0.073618 | -61.3103 | 60.0948 | 60.2498 | 60.2347 | -61.3967 | -0.029917 | -0.16688 | -0.045628 | -0.017022 | 0.012895 | -0.26653 | -0.30314 | -0.16163 | -0.34369 | 0.023322 | -0.075286 | 0.086339 | -0.18874 | -0.20385 | 121.5067 | 121.4071 | 121.3704 | 61.2777 | -121.7035 | 121.3299 | 121.4848 | 121.4697 | 61.3087 | -121.8352
991.125 | 121.8292 | -61.235 | 60.434 | -0.010149 | -0.030239 | 0.0090964 | 0.057504 | -0.0095144 | 0.051326 | -0.013887 | -0.0022666 | -0.0031451 | 0.059969 | 0.032141 | 0.051747 | -61.2807 | 0.038035 | -61.2475 | 60.2717 | 60.172 | 60.1354 | -61.265 | -61.2117 | 0.073618 | -61.3012 | 60.0857 | 60.2452 | 60.2347 | -61.4058 | -0.029917 | -0.1623 | -0.045628 | -0.012444 | 0.017473 | -0.26195 | -0.29856 | -0.17078 | -0.34827 | 0.023322 | -0.066128 | 0.10465 | -0.18874 | -0.19927 | 121.5067 | 121.4071 | 121.3704 | 61.2731 | -121.6989 | 121.3207 | 121.4803 | 121.4697 | 61.3087 | -121.8398
992.875 | 121.8521 | -61.3495 | 60.3104 | -0.01778 | -0.030025 | 0.00931 | 0.057932 | -0.0093008 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059542 | 0.031927 | 0.051533 | -61.2853 | 0.047193 | -61.2566 | 60.29 | 60.1766 | 60.1308 | -61.2604 | -61.2071 | 0.078197 | -61.3058 | 60.0811 | 60.2544 | 60.2484 | -61.4012 | 0.089103 | -0.020387 | 0.064235 | 0.092841 | 0.003738 | -0.13378 | -0.17955 | -0.051763 | -0.22926 | 0.14234 | 0.043734 | 0.095497 | -0.055984 | -0.06194 | 121.6395 | 121.5261 | 121.4803 | 61.3967 | -121.5707 | 121.4306 | 121.6039 | 121.5979 | 61.4277 | -121.7116
994.625 | 121.8613 | -61.2762 | 60.4248 | -0.010149 | -0.030239 | 0.00931 | 0.057718 | -0.0090872 | 0.05154 | -0.013887 | -0.0022666 | -0.0029313 | 0.059542 | 0.032354 | 0.05196 | -61.2853 | 0.042614 | -61.2429 | 60.2808 | 60.172 | 60.1308 | -61.265 | -61.2163 | 0.082776 | -61.3103 | 60.0811 | 60.2406 | 60.2484 | -61.4104 | 0.011282 | -0.14399 | -0.009007 | 0.033333 | 0.022051 | -0.2528 | -0.29399 | -0.13416 | -0.3437 | 0.059942 | -0.034087 | 0.10008 | -0.18416 | -0.17638 | 121.5571 | 121.4483 | 121.4071 | 61.3189 | -121.6898 | 121.3574 | 121.5169 | 121.5247 | 61.359 | -121.8352
996.3125 | 121.8521 | -61.322 | 60.3378 | -0.010149 | -0.030239 | 0.0090964 | 0.057504 | -0.0095144 | 0.05154 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059755 | 0.031927 | 0.05196 | -61.2807 | 0.047193 | -61.2475 | 60.29 | 60.172 | 60.14 | -61.265 | -61.2071 | 0.082776 | -61.3103 | 60.0903 | 60.2452 | 60.2438 | -61.4012 | 0.057058 | -0.047853 | 0.041347 | 0.074531 | 0.017473 | -0.16582 | -0.19786 | -0.079229 | -0.24756 | 0.11487 | 0.011689 | 0.090918 | -0.092607 | -0.093985 | 121.612 | 121.494 | 121.462 | 61.3692 | -121.6028 | 121.4123 | 121.5672 | 121.5659 | 61.4048 | -121.7391
998.0625 | 121.9574 | -61.2259 | 60.3928 | -0.0025182 | -0.030239 | 0.0088826 | 0.057718 | -0.0093008 | 0.05154 | -0.021518 | -0.0018394 | -0.0031451 | 0.059969 | 0.032141 | 0.05196 | -61.2898 | 0.042614 | -61.2566 | 60.2808 | 60.172 | 60.1308 | -61.2695 | -61.2071 | 0.073618 | -61.3058 | 60.0903 | 60.2498 | 60.2484 | -61.4012 | -0.043651 | -0.11194 | -0.06394 | -0.030755 | 0.012896 | -0.22075 | -0.26194 | -0.17536 | -0.3025 | 0.018745 | -0.079862 | 0.095497 | -0.14296 | -0.14434 | 121.5067 | 121.3979 | 121.3567 | 61.2685 | -121.6623 | 121.3162 | 121.4757 | 121.4743 | 61.2995 | -121.794
999.8125 | 121.8842 | -61.2946 | 60.3516 | -0.0025182 | -0.030239 | 0.0090964 | 0.057718 | -0.0090872 | 0.05154 | -0.0062567 | -0.002053 | -0.0031451 | 0.059755 | 0.031927 | 0.051747 | -61.2853 | 0.042614 | -61.2429 | 60.2854 | 60.1766 | 60.14 | -61.2741 | -61.2071 | 0.06904 | -61.3058 | 60.0811 | 60.2498 | 60.2484 | -61.4104 | 0.020435 | -0.066164 | 0.009304 | 0.051644 | 0.031209 | -0.17498 | -0.21159 | -0.11585 | -0.27045 | 0.08741 | -0.011197 | 0.10465 | -0.10176 | -0.10314 | 121.58 | 121.4711 | 121.4345 | 61.3372 | -121.6257 | 121.3757 | 121.5444 | 121.543 | 61.3636 | -121.762
1001.5625 | 121.9345 | -61.2396 | 60.3882 | -0.010149 | -0.030453 | 0.0090964 | 0.057504 | -0.0093008 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.031713 | 0.05196 | -61.2715 | 0.038035 | -61.2429 | 60.2808 | 60.172 | 60.14 | -61.2695 | -61.2163 | 0.078197 | -61.3058 | 60.0857 | 60.2544 | 60.2347 | -61.415 | -0.029918 | -0.10736 | -0.031893 | -0.003288 | 0.02663 | -0.21618 | -0.24821 | -0.17536 | -0.3025 | 0.023321 | -0.066129 | 0.10923 | -0.1338 | -0.1535 | 121.5204 | 121.4116 | 121.3796 | 61.2777 | -121.6577 | 121.3253 | 121.494 | 121.4743 | 61.3178 | -121.8032
1003.25 | 121.9574 | -61.2579 | 60.2966 | -0.01778 | -0.030453 | 0.0088826 | 0.057718 | -0.0093008 | 0.051326 | -0.0062567 | -0.0022666 | -0.0027177 | 0.059969 | 0.032141 | 0.051747 | -61.2898 | 0.042614 | -61.2429 | 60.2808 | 60.172 | 60.1446 | -61.2604 | -61.2117 | 0.078197 | -61.3012 | 60.0948 | 60.2452 | 60.2393 | -61.4058 | -0.002449 | -0.015811 | -0.031896 | 0.015023 | 0.017472 | -0.12462 | -0.15208 | -0.14789 | -0.20179 | 0.046211 | -0.043239 | 0.10465 | -0.051408 | -0.057364 | 121.5388 | 121.4299 | 121.4025 | 61.3005 | -121.557 | 121.3528 | 121.5032 | 121.4972 | 61.3361 | -121.7025
1005 | 121.9803 | -61.1801 | 60.4111 | -0.010149 | -0.030239 | 0.00931 | 0.057932 | -0.0093008 | 0.05154 | -0.013887 | -0.0024804 | -0.0029313 | 0.059755 | 0.031927 | 0.051747 | -61.2807 | 0.038035 | -61.2383 | 60.2808 | 60.172 | 60.1354 | -61.2695 | -61.2163 | 0.06904 | -61.3103 | 60.0811 | 60.2498 | 60.2484 | -61.4104 | -0.089427 | -0.13025 | -0.10056 | -0.058218 | 0.031209 | -0.23907 | -0.27568 | -0.23029 | -0.32996 | -0.036188 | -0.13022 | 0.10008 | -0.16127 | -0.16265 | 121.4609 | 121.3521 | 121.3155 | 61.2182 | -121.6806 | 121.2612 | 121.4299 | 121.4285 | 61.2492 | -121.8215
1006.7344 | 121.8658 | -61.203 | 60.4294 | -0.0025182 | -0.030666 | 0.00931 | 0.057504 | -0.0095144 | 0.051753 | -0.0062567 | -0.002053 | -0.0031451 | 0.059755 | 0.031927 | 0.051747 | -61.2853 | 0.047193 | -61.2475 | 60.2808 | 60.1766 | 60.1308 | -61.2695 | -61.2209 | 0.078197 | -61.3058 | 60.0903 | 60.2498 | 60.2393 | -61.4058 | -0.066539 | -0.14856 | -0.082249 | -0.044487 | 0.022052 | -0.2528 | -0.29857 | -0.20283 | -0.33912 | -0.017879 | -0.10275 | 0.10008 | -0.17958 | -0.19011 | 121.4838 | 121.3796 | 121.3338 | 61.2502 | -121.6989 | 121.2933 | 121.4528 | 121.4423 | 61.2812 | -121.8352
1008.4844 | 121.9162 | -61.2122 | 60.4294 | -0.0025182 | -0.030239 | 0.0088826 | 0.058145 | -0.0095144 | 0.051326 | -0.021518 | -0.002053 | -0.0031451 | 0.059542 | 0.032141 | 0.05196 | -61.2898 | 0.042614 | -61.2475 | 60.2854 | 60.1766 | 60.14 | -61.2695 | -61.2163 | 0.073618 | -61.3103 | 60.0903 | 60.2406 | 60.2438 | -61.4058 | -0.057384 | -0.14398 | -0.077673 | -0.035332 | 0.022052 | -0.2528 | -0.28941 | -0.19367 | -0.33912 | -0.004145 | -0.098174 | 0.095497 | -0.18874 | -0.18554 | 121.4976 | 121.3887 | 121.3521 | 61.2548 | -121.6989 | 121.3024 | 121.4528 | 121.456 | 61.2858 | -121.8352
1010.1562 | 121.9803 | -61.2717 | 60.2921 | -0.010149 | -0.030239 | 0.0090964 | 0.057718 | -0.0093008 | 0.051326 | -0.029148 | -0.002053 | -0.0029313 | 0.059755 | 0.031927 | 0.05196 | -61.2807 | 0.047193 | -61.2566 | 60.2808 | 60.1766 | 60.14 | -61.265 | -61.2117 | 0.078197 | -61.3103 | 60.0903 | 60.2452 | 60.2438 | -61.4104 | 0.006704 | -0.011233 | -0.009007 | 0.015021 | 0.008317 | -0.11547 | -0.15208 | -0.13874 | -0.20179 | 0.059943 | -0.038665 | 0.10008 | -0.04683 | -0.048208 | 121.5525 | 121.4483 | 121.4116 | 61.3189 | -121.557 | 121.3619 | 121.5169 | 121.5155 | 61.3499 | -121.7025
1011.9062 | 121.9299 | -61.2442 | 60.3607 | -0.010149 | -0.030453 | 0.0090964 | 0.057504 | -0.0095144 | 0.05154 | -0.029148 | -0.0022666 | -0.0031451 | 0.059755 | 0.032141 | 0.05196 | -61.2853 | 0.047193 | -61.2475 | 60.2854 | 60.1674 | 60.14 | -61.265 | -61.2163 | 0.087354 | -61.3103 | 60.0857 | 60.2452 | 60.2438 | -61.4058 | -0.020761 | -0.07532 | -0.04105 | -0.003288 | 0.017473 | -0.19329 | -0.22075 | -0.16163 | -0.27503 | 0.027899 | -0.06613 | 0.095497 | -0.11549 | -0.11687 | 121.5296 | 121.4116 | 121.3842 | 61.2914 | -121.6257 | 121.3299 | 121.4894 | 121.488 | 61.3316 | -121.7665
1013.5781 | 121.9482 | -61.2122 | 60.4156 | -0.010149 | -0.030453 | 0.0090964 | 0.057718 | -0.0095144 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.031927 | 0.05196 | -61.2807 | 0.042614 | -61.2475 | 60.2808 | 60.1766 | 60.1354 | -61.2604 | -61.2117 | 0.073618 | -61.3058 | 60.0903 | 60.2498 | 60.2393 | -61.4058 | -0.048226 | -0.13483 | -0.068516 | -0.035332 | 0.012894 | -0.23906 | -0.28025 | -0.19367 | -0.32538 | 0.000434 | -0.093595 | 0.10008 | -0.16585 | -0.17638 | 121.493 | 121.3887 | 121.3476 | 61.2548 | -121.676 | 121.3024 | 121.462 | 121.4514 | 61.2858 | -121.8215
1015.3125 | 122.0032 | -61.1938 | 60.4111 | -0.01778 | -0.030666 | 0.0090964 | 0.057932 | -0.0093008 | 0.05154 | -0.0062567 | -0.002694 | -0.0031451 | 0.059328 | 0.032141 | 0.05196 | -61.2853 | 0.038035 | -61.2475 | 60.2762 | 60.1628 | 60.14 | -61.2695 | -61.2163 | 0.078197 | -61.3058 | 60.0903 | 60.2406 | 60.2438 | -61.4104 | -0.075694 | -0.13483 | -0.091404 | -0.053642 | 0.022052 | -0.24822 | -0.2711 | -0.21656 | -0.32081 | -0.022455 | -0.11191 | 0.10465 | -0.17043 | -0.16723 | 121.4701 | 121.3567 | 121.3338 | 61.2319 | -121.6806 | 121.2841 | 121.4345 | 121.4377 | 61.272 | -121.8215
1017.0625 | 121.9482 | -61.2762 | 60.3104 | -0.01778 | -0.030666 | 0.0088826 | 0.057504 | -0.0093008 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059542 | 0.032354 | 0.052388 | -61.2853 | 0.038035 | -61.2475 | 60.2808 | 60.1766 | 60.1308 | -61.265 | -61.2026 | 0.078197 | -61.3103 | 60.0857 | 60.2406 | 60.2393 | -61.4058 | 0.011282 | -0.029544 | -0.009007 | 0.028755 | 0.017473 | -0.13378 | -0.17955 | -0.12958 | -0.22468 | 0.073678 | -0.034087 | 0.095497 | -0.06972 | -0.071097 | 121.5571 | 121.4528 | 121.4071 | 61.3143 | -121.5753 | 121.3619 | 121.5169 | 121.5155 | 61.3544 | -121.7162
1018.7344 | 121.8338 | -61.3449 | 60.3424 | -0.010149 | -0.030453 | 0.008669 | 0.057504 | -0.0095144 | 0.051112 | -0.021518 | -0.0022666 | -0.0033587 | 0.059542 | 0.032141 | 0.05196 | -61.2853 | 0.042614 | -61.2475 | 60.2808 | 60.172 | 60.1308 | -61.265 | -61.2071 | 0.082776 | -61.3058 | 60.0948 | 60.2361 | 60.2484 | -61.4058 | 0.079947 | -0.061587 | 0.059658 | 0.09742 | 0.017473 | -0.1704 | -0.21159 | -0.060919 | -0.24756 | 0.13776 | 0.039157 | 0.10008 | -0.10634 | -0.093983 | 121.6257 | 121.5169 | 121.4757 | 61.3875 | -121.6074 | 121.4398 | 121.581 | 121.5933 | 61.4277 | -121.7482
1020.4844 | 121.9116 | -61.235 | 60.3745 | -0.01778 | -0.030453 | 0.0090964 | 0.057718 | -0.0097282 | 0.05154 | -0.029148 | -0.0024804 | -0.0029313 | 0.059542 | 0.032141 | 0.052174 | -61.2807 | 0.038035 | -61.2475 | 60.2808 | 60.1766 | 60.14 | -61.2695 | -61.2163 | 0.078197 | -61.3103 | 60.0765 | 60.2452 | 60.2484 | -61.4058 | -0.034496 | -0.093631 | -0.045628 | -0.012444 | 0.022052 | -0.19787 | -0.23448 | -0.17078 | -0.29792 | 0.018743 | -0.075286 | 0.095497 | -0.12923 | -0.12603 | 121.5159 | 121.4116 | 121.375 | 61.2731 | -121.644 | 121.3116 | 121.4803 | 121.4835 | 61.3132 | -121.7803
1022.25 | 121.8887 | -61.3266 | 60.3104 | -0.0025182 | -0.030453 | 0.0090964 | 0.057504 | -0.0095144 | 0.051326 | -0.013887 | -0.002053 | -0.0029313 | 0.059542 | 0.032354 | 0.052174 | -61.2898 | 0.042614 | -61.2475 | 60.29 | 60.1812 | 60.1446 | -61.265 | -61.2071 | 0.073618 | -61.3058 | 60.0948 | 60.2498 | 60.2438 | -61.4058 | 0.061636 | -0.020387 | 0.036768 | 0.079109 | 0.017473 | -0.1292 | -0.16581 | -0.07923 | -0.21552 | 0.11945 | 0.020846 | 0.10008 | -0.060563 | -0.066519 | 121.6166 | 121.5078 | 121.4712 | 61.3692 | -121.5753 | 121.4214 | 121.5764 | 121.5704 | 61.4002 | -121.7162
1023.9375 | 121.8842 | -61.2762 | 60.3516 | -0.01778 | -0.030025 | 0.0088826 | 0.057504 | -0.0093008 | 0.051326 | -0.013887 | -0.0022666 | -0.0033587 | 0.059969 | 0.031713 | 0.05196 | -61.2898 | 0.042614 | -61.2475 | 60.2854 | 60.1812 | 60.1491 | -61.265 | -61.2163 | 0.078197 | -61.3058 | 60.0903 | 60.2498 | 60.2438 | -61.4058 | 0.011282 | -0.066164 | -0.013586 | 0.028755 | 0.017473 | -0.1704 | -0.20243 | -0.12958 | -0.2613 | 0.059942 | -0.029508 | 0.10008 | -0.10176 | -0.10772 | 121.5616 | 121.4574 | 121.4254 | 61.3189 | -121.6165 | 121.3665 | 121.526 | 121.5201 | 61.3544 | -121.7574
1025.6719 | 121.8613 | -61.322 | 60.3195 | -0.010149 | -0.030453 | 0.0088826 | 0.057718 | -0.0093008 | 0.05154 | -0.021518 | -0.0024804 | -0.0029313 | 0.059755 | 0.032141 | 0.052174 | -61.2761 | 0.047193 | -61.2475 | 60.29 | 60.1766 | 60.1446 | -61.265 | -61.2071 | 0.087354 | -61.3058 | 60.0903 | 60.2452 | 60.2438 | -61.4058 | 0.057058 | -0.029542 | 0.045925 | 0.074531 | 0.017473 | -0.14293 | -0.17497 | -0.083808 | -0.22925 | 0.11487 | 0.016268 | 0.10008 | -0.074296 | -0.075674 | 121.612 | 121.4986 | 121.4666 | 61.3692 | -121.5845 | 121.4123 | 121.5672 | 121.5659 | 61.4094 | -121.7253
1027.4219 | 121.8292 | -61.2213 | 60.4385 | -0.01778 | -0.030453 | 0.0088826 | 0.057932 | -0.0095144 | 0.051326 | -0.021518 | -0.002053 | -0.0031451 | 0.059969 | 0.032568 | 0.051533 | -61.2807 | 0.033457 | -61.2475 | 60.2854 | 60.1766 | 60.14 | -61.265 | -61.2026 | 0.073618 | -61.3058 | 60.0857 | 60.2452 | 60.2393 | -61.4104 | -0.04365 | -0.15314 | -0.059361 | -0.026177 | 0.017473 | -0.26195 | -0.29857 | -0.18909 | -0.35285 | 0.018746 | -0.08444 | 0.10465 | -0.19331 | -0.19927 | 121.5067 | 121.3979 | 121.3613 | 61.2548 | -121.7035 | 121.307 | 121.4665 | 121.4606 | 61.2949 | -121.8489
1029.1875 | 121.8796 | -61.2717 | 60.3516 | -0.0025182 | -0.030666 | 0.0090964 | 0.057932 | -0.0099418 | 0.05154 | -0.021518 | -0.002053 | -0.0029313 | 0.059542 | 0.032568 | 0.052174 | -61.2898 | 0.038035 | -61.2475 | 60.2808 | 60.1766 | 60.1446 | -61.2695 | -61.2163 | 0.078197 | -61.3103 | 60.0857 | 60.2498 | 60.2347 | -61.4012 | 0.002125 | -0.070742 | -0.018164 | 0.024177 | 0.022052 | -0.17498 | -0.20701 | -0.12958 | -0.26588 | 0.055364 | -0.038665 | 0.090918 | -0.10176 | -0.11687 | 121.5525 | 121.4483 | 121.4162 | 61.3097 | -121.6211 | 121.3574 | 121.5215 | 121.5064 | 61.3499 | -121.7528
1030.875 | 121.8658 | -61.29 | 60.3653 | -0.01778 | -0.030666 | 0.0090964 | 0.057718 | -0.0095144 | 0.05154 | -0.0062567 | -0.002694 | -0.0031451 | 0.059755 | 0.032141 | 0.052174 | -61.2807 | 0.047193 | -61.2521 | 60.2808 | 60.1812 | 60.1446 | -61.265 | -61.2071 | 0.073618 | -61.3103 | 60.0903 | 60.2498 | 60.2438 | -61.4012 | 0.025015 | -0.084475 | 0.009304 | 0.03791 | 0.012895 | -0.18413 | -0.22074 | -0.11127 | -0.27503 | 0.082832 | -0.020354 | 0.090918 | -0.11549 | -0.12145 | 121.5708 | 121.4711 | 121.4345 | 61.3372 | -121.6303 | 121.3802 | 121.5398 | 121.5338 | 61.3636 | -121.7665
1032.6406 | 121.8842 | -61.2534 | 60.3745 | -0.010149 | -0.03088 | 0.0090964 | 0.057718 | -0.0093008 | 0.051326 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.032354 | 0.05196 | -61.2898 | 0.033457 | -61.2521 | 60.2808 | 60.1812 | 60.1446 | -61.2695 | -61.2163 | 0.073618 | -61.3012 | 60.0948 | 60.2498 | 60.2393 | -61.4012 | -0.016185 | -0.093631 | -0.036474 | 0.001289 | 0.017474 | -0.19329 | -0.2299 | -0.14789 | -0.27961 | 0.037054 | -0.047817 | 0.10008 | -0.12465 | -0.13518 | 121.5342 | 121.4345 | 121.3979 | 61.2868 | -121.644 | 121.3482 | 121.5032 | 121.4926 | 61.327 | -121.7757
1034.3281 | 121.907 | -61.2396 | 60.3424 | -0.010149 | -0.030453 | 0.00931 | 0.057504 | -0.0095144 | 0.051326 | -0.021518 | -0.0022666 | -0.0029313 | 0.059755 | 0.032354 | 0.05196 | -61.2807 | 0.038035 | -61.2475 | 60.2946 | 60.172 | 60.14 | -61.2695 | -61.2117 | 0.078197 | -61.3058 | 60.0903 | 60.2452 | 60.2438 | -61.4104 | -0.029918 | -0.047852 | -0.04105 | -0.007866 | 0.022052 | -0.1704 | -0.20243 | -0.17078 | -0.25214 | 0.0279 | -0.066129 | 0.10465 | -0.097184 | -0.098562 | 121.5342 | 121.4116 | 121.3796 | 61.2777 | -121.6119 | 121.3299 | 121.4848 | 121.4835 | 61.3178 | -121.7528
1036.0625 | 121.8384 | -61.2579 | 60.4156 | -0.010149 | -0.03088 | 0.0090964 | 0.057718 | -0.0093008 | 0.051326 | -0.013887 | -0.0024804 | -0.0029313 | 0.059542 | 0.032568 | 0.05196 | -61.2898 | 0.033457 | -61.2521 | 60.29 | 60.172 | 60.1446 | -61.2695 | -61.2117 | 0.078197 | -61.3012 | 60.0903 | 60.2452 | 60.2393 | -61.4058 | -0.011607 | -0.12567 | -0.031896 | 0.005867 | 0.017474 | -0.24364 | -0.2711 | -0.14789 | -0.32538 | 0.046211 | -0.043239 | 0.10465 | -0.17043 | -0.17638 | 121.5479 | 121.4299 | 121.4025 | 61.2914 | -121.6852 | 121.3482 | 121.5032 | 121.4972 | 61.3361 | -121.8215
1037.75 | 121.8796 | -61.2854 | 60.3745 | -0.010149 | -0.03088 | 0.0088826 | 0.057718 | -0.0093008 | 0.051112 | -0.013887 | -0.0022666 | -0.0031451 | 0.059328 | 0.032141 | 0.051747 | -61.2807 | 0.028878 | -61.2429 | 60.2762 | 60.1766 | 60.1446 | -61.2604 | -61.2163 | 0.073618 | -61.3058 | 60.0903 | 60.2544 | 60.2484 | -61.4058 | 0.025016 | -0.098209 | 0.004726 | 0.042488 | 0.017472 | -0.19787 | -0.2299 | -0.12043 | -0.28419 | 0.069097 | -0.020353 | 0.10008 | -0.12007 | -0.12603 | 121.5616 | 121.462 | 121.43 | 61.3143 | -121.6348 | 121.3757 | 121.5398 | 121.5338 | 61.359 | -121.7803
1039.4844 | 121.8338 | -61.3037 | 60.3104 | -0.0025182 | -0.030666 | 0.008669 | 0.057718 | -0.0095144 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059328 | 0.032354 | 0.051747 | -61.2715 | 0.042614 | -61.2429 | 60.2854 | 60.1766 | 60.14 | -61.2695 | -61.2071 | 0.078197 | -61.3058 | 60.0903 | 60.2544 | 60.2438 | -61.415 | 0.034169 | -0.024966 | 0.032194 | 0.060799 | 0.02663 | -0.13378 | -0.17039 | -0.11127 | -0.2201 | 0.096565 | -0.002042 | 0.10923 | -0.055984 | -0.066519 | 121.5891 | 121.4803 | 121.4437 | 61.3463 | -121.5799 | 121.394 | 121.5581 | 121.5476 | 61.3819 | -121.7253
1041.2344 | 121.9482 | -61.2717 | 60.3012 | -0.025411 | -0.03088 | 0.008669 | 0.057718 | -0.0095144 | 0.051112 | -0.021518 | -0.002053 | -0.0031451 | 0.059755 | 0.032141 | 0.05196 | -61.2807 | 0.047193 | -61.2521 | 60.29 | 60.1766 | 60.1446 | -61.265 | -61.2163 | 0.078197 | -61.3058 | 60.0948 | 60.2498 | 60.2393 | -61.4104 | 0.006704 | -0.011231 | -0.009007 | 0.019599 | 0.012895 | -0.12462 | -0.15666 | -0.13874 | -0.20636 | 0.055364 | -0.034086 | 0.10465 | -0.051407 | -0.061941 | 121.5616 | 121.4483 | 121.4162 | 61.3189 | -121.5662 | 121.3665 | 121.5215 | 121.5109 | 61.3499 | -121.7116
1042.9844 | 121.9574 | -61.1893 | 60.3973 | -0.010149 | -0.03088 | 0.0088826 | 0.057932 | -0.0097282 | 0.051112 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.032782 | 0.05196 | -61.2853 | 0.028878 | -61.2429 | 60.2854 | 60.1674 | 60.1446 | -61.2741 | -61.2163 | 0.078197 | -61.3103 | 60.0857 | 60.2452 | 60.2393 | -61.415 | -0.084851 | -0.11194 | -0.095982 | -0.053642 | 0.031209 | -0.22991 | -0.25279 | -0.22572 | -0.31165 | -0.027033 | -0.12106 | 0.10465 | -0.15212 | -0.15807 | 121.4747 | 121.3567 | 121.3338 | 61.2181 | -121.6715 | 121.275 | 121.4345 | 121.4285 | 61.2675 | -121.8123
1044.6719 | 121.9574 | -61.2442 | 60.3195 | -0.01778 | -0.030453 | 0.0088826 | 0.058359 | -0.0093008 | 0.051326 | -0.021518 | -0.0024804 | -0.0031451 | 0.059328 | 0.032354 | 0.05196 | -61.2807 | 0.038035 | -61.2429 | 60.2854 | 60.1812 | 60.1446 | -61.265 | -61.2163 | 0.078197 | -61.3149 | 60.0903 | 60.2452 | 60.2438 | -61.4058 | -0.020761 | -0.034121 | -0.036472 | 0.00129 | 0.022051 | -0.13835 | -0.17497 | -0.16163 | -0.22925 | 0.027899 | -0.070708 | 0.090919 | -0.074296 | -0.075674 | 121.5296 | 121.4254 | 121.3888 | 61.2822 | -121.5845 | 121.3345 | 121.4894 | 121.488 | 61.3224 | -121.7253
1046.4062 | 121.9528 | -61.2534 | 60.3104 | -0.010149 | -0.030666 | 0.00931 | 0.057504 | -0.0093008 | 0.05154 | -0.013887 | -0.0024804 | -0.0031451 | 0.059542 | 0.032568 | 0.051533 | -61.2807 | 0.038035 | -61.2475 | 60.29 | 60.1766 | 60.1491 | -61.265 | -61.2117 | 0.082776 | -61.3012 | 60.0903 | 60.259 | 60.2484 | -61.4058 | -0.011606 | -0.020387 | -0.027317 | 0.005867 | 0.017473 | -0.13378 | -0.16123 | -0.15247 | -0.2201 | 0.041633 | -0.047817 | 0.10465 | -0.051406 | -0.06194 | 121.5433 | 121.4299 | 121.4025 | 61.2914 | -121.5753 | 121.3436 | 121.5123 | 121.5018 | 61.3361 | -121.7162
1048.1562 | 121.9757 | -61.2122 | 60.3745 | -0.010149 | -0.030666 | 0.0090964 | 0.057504 | -0.0095144 | 0.051326 | -0.013887 | -0.0022666 | -0.0033587 | 0.059328 | 0.032568 | 0.051747 | -61.2807 | 0.028878 | -61.2521 | 60.2854 | 60.172 | 60.1446 | -61.265 | -61.2163 | 0.078197 | -61.3012 | 60.0903 | 60.2498 | 60.2438 | -61.4104 | -0.052805 | -0.089053 | -0.068516 | -0.03991 | 0.012895 | -0.20244 | -0.2299 | -0.19825 | -0.28419 | -0.004145 | -0.089016 | 0.10923 | -0.12465 | -0.13061 | 121.4976 | 121.3842 | 121.3567 | 61.241 | -121.6394 | 121.3024 | 121.462 | 121.456 | 61.2904 | -121.7849
1049.8281 | 121.843 | -61.322 | 60.347 | -0.010149 | -0.030666 | 0.0090964 | 0.057932 | -0.0095144 | 0.051326 | -0.021518 | -0.002053 | -0.0031451 | 0.059755 | 0.032354 | 0.05196 | -61.2761 | 0.042614 | -61.2521 | 60.2762 | 60.1766 | 60.1446 | -61.2741 | -61.2163 | 0.073618 | -61.3058 | 60.0994 | 60.2498 | 60.2484 | -61.415 | 0.0479 | -0.070743 | 0.045925 | 0.069953 | 0.022053 | -0.1704 | -0.20243 | -0.092965 | -0.24756 | 0.10572 | 0.016268 | 0.10923 | -0.097184 | -0.098561 | 121.5983 | 121.4986 | 121.4666 | 61.3646 | -121.6211 | 121.4214 | 121.5718 | 121.5704 | 61.3956 | -121.762
1051.5781 | 121.8567 | -61.3266 | 60.3424 | -0.010149 | -0.03088 | 0.0088826 | 0.057504 | -0.0097282 | 0.051112 | -0.013887 | -0.0024804 | -0.0031451 | 0.059542 | 0.032568 | 0.052174 | -61.2807 | 0.038035 | -61.2429 | 60.2946 | 60.1812 | 60.1446 | -61.2558 | -61.2071 | 0.082776 | -61.3149 | 60.0903 | 60.2452 | 60.2438 | -61.4104 | 0.070794 | -0.047852 | 0.045925 | 0.083687 | 0.012893 | -0.16124 | -0.19786 | -0.083809 | -0.25214 | 0.11945 | 0.011689 | 0.095498 | -0.097184 | -0.098562 | 121.6212 | 121.5078 | 121.4712 | 61.3646 | -121.5982 | 121.4169 | 121.5718 | 121.5704 | 61.4094 | -121.7528
1053.3281 | 121.8933 | -61.2534 | 60.3561 | -0.010149 | -0.03088 | 0.0088826 | 0.057504 | -0.0097282 | 0.051326 | -0.013887 | -0.002053 | -0.0033587 | 0.059542 | 0.032354 | 0.051747 | -61.2853 | 0.033457 | -61.2429 | 60.2946 | 60.1812 | 60.1491 | -61.2695 | -61.2163 | 0.082776 | -61.3103 | 60.0903 | 60.2452 | 60.2484 | -61.4058 | -0.016185 | -0.061585 | -0.031895 | 0.010445 | 0.02663 | -0.17498 | -0.20701 | -0.15247 | -0.26587 | 0.037054 | -0.056975 | 0.095497 | -0.11092 | -0.10772 | 121.5479 | 121.4345 | 121.4025 | 61.2868 | -121.6257 | 121.3436 | 121.4986 | 121.5018 | 61.3361 | -121.762
1055.0625 | 121.8384 | -61.2991 | 60.3424 | -0.010149 | -0.031094 | 0.0088826 | 0.057718 | -0.0095144 | 0.051326 | -0.021518 | -0.0024804 | -0.0033587 | 0.059755 | 0.032782 | 0.051533 | -61.2807 | 0.038035 | -61.2475 | 60.2854 | 60.1812 | 60.1446 | -61.2604 | -61.2163 | 0.073618 | -61.3058 | 60.0903 | 60.2498 | 60.2484 | -61.4104 | 0.038749 | -0.057009 | 0.018459 | 0.051643 | 0.012894 | -0.16124 | -0.19786 | -0.11127 | -0.25214 | 0.08283 | -0.00662 | 0.10465 | -0.092606 | -0.093983 | 121.5845 | 121.4803 | 121.4437 | 61.3372 | -121.6028 | 121.3894 | 121.5489 | 121.5476 | 61.3728 | -121.7528
1056.75 | 121.8933 | -61.29 | 60.3882 | -0.01778 | -0.031307 | 0.00931 | 0.058145 | -0.0093008 | 0.051326 | -0.021518 | -0.002053 | -0.0031451 | 0.059969 | 0.032782 | 0.05196 | -61.2853 | 0.042614 | -61.2475 | 60.2854 | 60.1812 | 60.1446 | -61.2604 | -61.2071 | 0.073618 | -61.3103 | 60.0948 | 60.2498 | 60.2484 | -61.415 | 0.029594 | -0.10279 | 0.004726 | 0.042488 | 0.012894 | -0.20702 | -0.24363 | -0.12501 | -0.29334 | 0.082832 | -0.020354 | 0.10465 | -0.13838 | -0.13976 | 121.5754 | 121.4711 | 121.4345 | 61.3326 | -121.6486 | 121.3848 | 121.5398 | 121.5384 | 61.3636 | -121.8032
1058.4844 | 121.9803 | -61.2946 | 60.2692 | -0.010149 | -0.03088 | 0.00931 | 0.057718 | -0.0095144 | 0.051326 | -0.013887 | -0.002053 | -0.0033587 | 0.059328 | 0.032354 | 0.051533 | -61.2807 | 0.038035 | -61.2475 | 60.2854 | 60.172 | 60.1491 | -61.265 | -61.2117 | 0.073618 | -61.3012 | 60.0903 | 60.2544 | 60.2484 | -61.4104 | 0.029593 | 0.016233 | 0.013882 | 0.047066 | 0.017473 | -0.097159 | -0.12003 | -0.11585 | -0.1789 | 0.082832 | -0.006618 | 0.10923 | -0.014785 | -0.020741 | 121.58 | 121.4666 | 121.4437 | 61.3326 | -121.5341 | 121.3848 | 121.5489 | 121.543 | 61.3682 | -121.6796
1060.2344 | 121.8338 | -61.2534 | 60.4294 | -0.010149 | -0.03088 | 0.0090964 | 0.057718 | -0.0099418 | 0.051326 | -0.0062567 | -0.0022666 | -0.0029313 | 0.059755 | 0.032568 | 0.05196 | -61.2807 | 0.033457 | -61.2429 | 60.29 | 60.1766 | 60.1491 | -61.2695 | -61.2071 | 0.06904 | -61.3149 | 60.0903 | 60.2498 | 60.2484 | -61.4196 | -0.016185 | -0.1394 | -0.027317 | 0.010445 | 0.02663 | -0.2528 | -0.28025 | -0.16621 | -0.33912 | 0.046211 | -0.061553 | 0.10466 | -0.17958 | -0.18096 | 121.5433 | 121.4299 | 121.4025 | 61.2868 | -121.6989 | 121.3436 | 121.5032 | 121.5018 | 61.3224 | -121.8489
1061.9844 | 121.8384 | -61.3083 | 60.347 | -0.01778 | -0.03088 | 0.0090964 | 0.057718 | -0.0093008 | 0.051112 | -0.013887 | -0.0022666 | -0.0033587 | 0.059542 | 0.032568 | 0.051747 | -61.2715 | 0.038035 | -61.2475 | 60.2946 | 60.1766 | 60.1491 | -61.265 | -61.2117 | 0.078197 | -61.3058 | 60.0857 | 60.2498 | 60.2438 | -61.4104 | 0.043326 | -0.05243 | 0.036772 | 0.060799 | 0.017473 | -0.1704 | -0.19785 | -0.10212 | -0.2613 | 0.096565 | 0.002536 | 0.10465 | -0.097184 | -0.10314 | 121.6028 | 121.4849 | 121.4574 | 61.3463 | -121.6119 | 121.394 | 121.5581 | 121.5521 | 61.3865 | -121.7574
1063.7344 | 121.9757 | -61.1755 | 60.3882 | -0.010149 | -0.03088 | 0.00931 | 0.057718 | -0.0095144 | 0.051326 | -0.013887 | -0.0022666 | -0.0027177 | 0.059755 | 0.032354 | 0.051747 | -61.2807 | 0.038035 | -61.2429 | 60.2808 | 60.1812 | 60.1491 | -61.265 | -61.2163 | 0.078197 | -61.2966 | 60.0903 | 60.2498 | 60.2393 | -61.4196 | -0.089426 | -0.10736 | -0.10514 | -0.067375 | 0.022051 | -0.20702 | -0.23905 | -0.24403 | -0.29792 | -0.040766 | -0.12106 | 0.12297 | -0.13838 | -0.14892 | 121.4564 | 121.3567 | 121.3247 | 61.2136 | -121.6531 | 121.2658 | 121.4253 | 121.4148 | 61.2537 | -121.8077
1065.4219 | 121.8933 | -61.2396 | 60.3882 | -0.0025182 | -0.031094 | 0.0090964 | 0.057504 | -0.0097282 | 0.051326 | -0.013887 | -0.0024804 | -0.0031451 | 0.059328 | 0.032995 | 0.05196 | -61.2761 | 0.033457 | -61.2521 | 60.29 | 60.1812 | 60.1491 | -61.2695 | -61.2071 | 0.073618 | -61.3058 | 60.104 | 60.2544 | 60.2438 | -61.4104 | -0.029918 | -0.098207 | -0.036472 | -0.012444 | 0.017474 | -0.20702 | -0.23905 | -0.17078 | -0.28418 | 0.032478 | -0.066129 | 0.10465 | -0.1338 | -0.14434 | 121.5296 | 121.4208 | 121.3888 | 61.2731 | -121.6577 | 121.3436 | 121.494 | 121.4835 | 61.3132 | -121.7986
1067.1719 | 121.9757 | -61.1938 | 60.3928 | -0.01778 | -0.031094 | 0.00931 | 0.057718 | -0.0097282 | 0.051326 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059542 | 0.032568 | 0.05196 | -61.2807 | 0.028878 | -61.2429 | 60.2854 | 60.1812 | 60.1491 | -61.2604 | -61.2071 | 0.073618 | -61.3058 | 60.0994 | 60.2498 | 60.2438 | -61.4104 | -0.066536 | -0.10736 | -0.086826 | -0.049064 | 0.017472 | -0.2116 | -0.24363 | -0.21656 | -0.29334 | -0.013298 | -0.11191 | 0.10465 | -0.14296 | -0.14892 | 121.4792 | 121.375 | 121.343 | 61.2227 | -121.6531 | 121.2933 | 121.4436 | 121.4377 | 61.2675 | -121.8032
1068.8594 | 121.843 | -61.2167 | 60.434 | -0.0025182 | -0.03088 | 0.0095236 | 0.057504 | -0.0095144 | 0.05154 | -0.021518 | -0.0024804 | -0.0031451 | 0.059542 | 0.032568 | 0.051533 | -61.2898 | 0.038035 | -61.2475 | 60.29 | 60.1857 | 60.1491 | -61.2695 | -61.2117 | 0.073618 | -61.3103 | 60.0857 | 60.2498 | 60.2438 | -61.4104 | -0.052806 | -0.14398 | -0.073095 | -0.030754 | 0.022052 | -0.24822 | -0.28483 | -0.19367 | -0.34827 | 0.005012 | -0.093596 | 0.10008 | -0.18416 | -0.19011 | 121.5067 | 121.4025 | 121.3659 | 61.2548 | -121.7035 | 121.3024 | 121.4665 | 121.4606 | 61.2904 | -121.8444
1070.6094 | 121.9299 | -61.2579 | 60.3058 | -0.010149 | -0.031094 | 0.00931 | 0.057718 | -0.0099418 | 0.051326 | -0.021518 | -0.0022666 | -0.0029313 | 0.059542 | 0.032782 | 0.05196 | -61.2761 | 0.038035 | -61.2475 | 60.2854 | 60.1766 | 60.1491 | -61.2695 | -61.2071 | 0.073618 | -61.3012 | 60.0903 | 60.259 | 60.2484 | -61.4104 | -0.011607 | -0.020388 | -0.018161 | 0.010445 | 0.022052 | -0.1292 | -0.15666 | -0.15247 | -0.21552 | 0.050789 | -0.043239 | 0.10923 | -0.046828 | -0.057362 | 121.5433 | 121.4345 | 121.4071 | 61.296 | -121.5753 | 121.3482 | 121.5169 | 121.5064 | 61.3316 | -121.7162
1072.3594 | 121.9803 | -61.1755 | 60.4248 | -0.01778 | -0.03088 | 0.0088826 | 0.057504 | -0.0095144 | 0.051326 | -0.013887 | -0.0022666 | -0.0029313 | 0.059755 | 0.032568 | 0.05196 | -61.2807 | 0.033457 | -61.2475 | 60.29 | 60.1766 | 60.1537 | -61.2695 | -61.2209 | 0.078197 | -61.3012 | 60.0903 | 60.2498 | 60.2438 | -61.4104 | -0.094005 | -0.13483 | -0.10514 | -0.071953 | 0.022052 | -0.24822 | -0.2711 | -0.23487 | -0.33454 | -0.045345 | -0.12564 | 0.10923 | -0.175 | -0.18096 | 121.4655 | 121.3521 | 121.3292 | 61.209 | -121.6943 | 121.2658 | 121.4253 | 121.4194 | 61.2537 | -121.8352
1074.0469 | 121.9345 | -61.1618 | 60.4294 | -0.010149 | -0.031094 | 0.0090964 | 0.057932 | -0.0097282 | 0.051326 | -0.029148 | -0.0022666 | -0.0031451 | 0.059542 | 0.032782 | 0.05196 | -61.2853 | 0.028878 | -61.2429 | 60.2854 | 60.1812 | 60.1491 | -61.265 | -61.2117 | 0.06904 | -61.3012 | 60.0903 | 60.259 | 60.2484 | -61.415 | -0.10316 | -0.14398 | -0.12345 | -0.081108 | 0.022051 | -0.24822 | -0.28025 | -0.25318 | -0.33912 | -0.04992 | -0.13937 | 0.11381 | -0.17042 | -0.18096 | 121.4472 | 121.343 | 121.3109 | 61.1907 | -121.6943 | 121.2521 | 121.4208 | 121.4102 | 61.2308 | -121.8444
1075.8125 | 121.9299 | -61.2625 | 60.3104 | -0.01778 | -0.031521 | 0.00931 | 0.057718 | -0.0095144 | 0.051326 | -0.021518 | -0.0024804 | -0.0031451 | 0.059755 | 0.032568 | 0.05196 | -61.2807 | 0.042614 | -61.2475 | 60.2946 | 60.1812 | 60.1537 | -61.265 | -61.2071 | 0.078197 | -61.3103 | 60.0994 | 60.259 | 60.2438 | -61.415 | -0.002451 | -0.015809 | -0.018162 | 0.015022 | 0.017473 | -0.1292 | -0.15666 | -0.15247 | -0.21094 | 0.055366 | -0.04782 | 0.10465 | -0.051406 | -0.066519 | 121.5571 | 121.4437 | 121.4162 | 61.3051 | -121.5753 | 121.3619 | 121.5215 | 121.5064 | 61.3407 | -121.7253
1077.5469 | 121.962 | -61.2671 | 60.2921 | -0.010149 | -0.031521 | 0.0090964 | 0.057932 | -0.0095144 | 0.05154 | -0.021518 | -0.0024804 | -0.0035723 | 0.059755 | 0.032782 | 0.05196 | -61.2853 | 0.028878 | -61.2429 | 60.2946 | 60.1812 | 60.1583 | -61.2604 | -61.2117 | 0.078197 | -61.3012 | 60.0948 | 60.2544 | 60.2438 | -61.415 | 0.006706 | 0.002502 | -0.018162 | 0.024178 | 0.017472 | -0.11089 | -0.13377 | -0.1479 | -0.19721 | 0.055366 | -0.034084 | 0.11381 | -0.037673 | -0.048208 | 121.5616 | 121.4483 | 121.4254 | 61.296 | -121.5524 | 121.3619 | 121.5215 | 121.5109 | 61.3453 | -121.707
1079.2969 | 121.8567 | -61.322 | 60.3424 | -0.010149 | -0.031094 | 0.0090964 | 0.057504 | -0.0095144 | 0.051326 | -0.013887 | -0.0022666 | -0.0029313 | 0.059969 | 0.032354 | 0.051747 | -61.2853 | 0.038035 | -61.2521 | 60.29 | 60.1857 | 60.1583 | -61.265 | -61.2071 | 0.078197 | -61.3103 | 60.0948 | 60.2498 | 60.253 | -61.415 | 0.057058 | -0.05243 | 0.036769 | 0.069953 | 0.012895 | -0.15666 | -0.18412 | -0.092965 | -0.24756 | 0.11487 | 0.011689 | 0.10465 | -0.092606 | -0.089404 | 121.612 | 121.5078 | 121.4803 | 61.3601 | -121.6074 | 121.4169 | 121.5718 | 121.575 | 61.4002 | -121.7574
1080.9844 | 121.8842 | -61.2717 | 60.3516 | 0.0051128 | -0.031094 | 0.00931 | 0.057504 | -0.0095144 | 0.051753 | -0.021518 | -0.0022666 | -0.0031451 | 0.059542 | 0.032782 | 0.05196 | -61.2853 | 0.038035 | -61.2521 | 60.2854 | 60.1903 | 60.1537 | -61.265 | -61.2071 | 0.078197 | -61.3058 | 60.104 | 60.2544 | 60.253 | -61.4104 | 0.006704 | -0.066164 | -0.013585 | 0.019599 | 0.012895 | -0.16124 | -0.19785 | -0.13874 | -0.24756 | 0.064521 | -0.034086 | 0.10465 | -0.097182 | -0.098559 | 121.5571 | 121.462 | 121.4254 | 61.3097 | -121.6165 | 121.3757 | 121.526 | 121.5247 | 61.3499 | -121.762
1082.7344 | 121.9254 | -61.2625 | 60.3699 | -0.010149 | -0.031094 | 0.0090964 | 0.057504 | -0.0097282 | 0.051753 | -0.013887 | -0.0024804 | -0.0033587 | 0.059328 | 0.033209 | 0.052174 | -61.2761 | 0.038035 | -61.2429 | 60.29 | 60.1857 | 60.1446 | -61.2695 | -61.2117 | 0.078197 | -61.3103 | 60.0857 | 60.259 | 60.2438 | -61.4012 | -0.00703 | -0.079896 | -0.013584 | 0.0196 | 0.02663 | -0.18413 | -0.22532 | -0.13874 | -0.28419 | 0.050788 | -0.04782 | 0.090918 | -0.11091 | -0.12603 | 121.5525 | 121.4483 | 121.4071 | 61.3005 | -121.6394 | 121.3482 | 121.5215 | 121.5064 | 61.3407 | -121.7711
1084.4688 | 121.9894 | -61.171 | 60.3973 | -0.010149 | -0.031521 | 0.0088826 | 0.057718 | -0.0093008 | 0.051326 | -0.029148 | -0.0022666 | -0.0031451 | 0.059755 | 0.032995 | 0.051533 | -61.2853 | 0.0243 | -61.2429 | 60.2808 | 60.1857 | 60.1491 | -61.2604 | -61.2163 | 0.06904 | -61.3058 | 60.0948 | 60.2498 | 60.2484 | -61.4058 | -0.089425 | -0.11652 | -0.11429 | -0.071953 | 0.017472 | -0.2116 | -0.24821 | -0.23487 | -0.3025 | -0.045344 | -0.13479 | 0.10008 | -0.14754 | -0.14892 | 121.4518 | 121.3567 | 121.3201 | 61.1953 | -121.6577 | 121.2658 | 121.4208 | 121.4194 | 61.24 | -121.8032
1086.2188 | 121.9666 | -61.2671 | 60.3012 | -0.025411 | -0.031307 | 0.00931 | 0.057718 | -0.0097282 | 0.05154 | -0.013887 | -0.0022666 | -0.0033587 | 0.059755 | 0.032354 | 0.05196 | -61.2853 | 0.038035 | -61.2521 | 60.29 | 60.1812 | 60.1491 | -61.2604 | -61.2071 | 0.078197 | -61.3103 | 60.0948 | 60.2498 | 60.2484 | -61.4104 | 0.006706 | -0.011231 | -0.018162 | 0.015022 | 0.008316 | -0.12004 | -0.15208 | -0.14332 | -0.20636 | 0.059944 | -0.043242 | 0.10008 | -0.051407 | -0.052784 | 121.5571 | 121.4483 | 121.4162 | 61.3051 | -121.5616 | 121.3619 | 121.5169 | 121.5155 | 61.3453 | -121.7116
1087.9062 | 121.8292 | -61.322 | 60.347 | -0.010149 | -0.031521 | 0.0088826 | 0.057504 | -0.0090872 | 0.05154 | -0.029148 | -0.0024804 | -0.0029313 | 0.059969 | 0.032782 | 0.05196 | -61.2853 | 0.042614 | -61.2429 | 60.2854 | 60.1857 | 60.1583 | -61.2695 | -61.2071 | 0.082776 | -61.3058 | 60.0948 | 60.259 | 60.2576 | -61.4058 | 0.052479 | -0.061587 | 0.036769 | 0.079109 | 0.02663 | -0.16124 | -0.1887 | -0.083808 | -0.25214 | 0.11487 | 0.016268 | 0.10008 | -0.088027 | -0.089404 | 121.6074 | 121.5078 | 121.4803 | 61.3646 | -121.6165 | 121.4169 | 121.581 | 121.5796 | 61.4048 | -121.7528
1089.6562 | 121.9666 | -61.29 | 60.3058 | -0.010149 | -0.031521 | 0.0088826 | 0.057932 | -0.0095144 | 0.051326 | -0.021518 | -0.0018394 | -0.0031451 | 0.059542 | 0.032995 | 0.05196 | -61.2761 | 0.038035 | -61.2475 | 60.29 | 60.1766 | 60.1583 | -61.2695 | -61.2026 | 0.078197 | -61.3058 | 60.0994 | 60.2635 | 60.2438 | -61.4058 | 0.020436 | -0.015809 | 0.013882 | 0.042488 | 0.022052 | -0.1292 | -0.1475 | -0.11585 | -0.20636 | 0.087411 | -0.015775 | 0.10008 | -0.042249 | -0.061941 | 121.58 | 121.4666 | 121.4483 | 61.328 | -121.5753 | 121.3894 | 121.5535 | 121.5338 | 61.3682 | -121.7116
1091.4219 | 121.8704 | -61.2991 | 60.3424 | -0.01778 | -0.031094 | 0.0088826 | 0.057932 | -0.0097282 | 0.05154 | -0.029148 | -0.002053 | -0.0029313 | 0.059542 | 0.032782 | 0.051747 | -61.2761 | 0.038035 | -61.2475 | 60.29 | 60.1766 | 60.1537 | -61.265 | -61.2071 | 0.078197 | -61.3103 | 60.0948 | 60.2681 | 60.253 | -61.4012 | 0.03417 | -0.05243 | 0.023037 | 0.051643 | 0.017473 | -0.16582 | -0.1887 | -0.10212 | -0.24756 | 0.091987 | -0.011199 | 0.090918 | -0.074291 | -0.089404 | 121.5891 | 121.4757 | 121.4528 | 61.3372 | -121.6074 | 121.394 | 121.5672 | 121.5521 | 61.3773 | -121.7437
1093.1875 | 121.8567 | -61.3129 | 60.3378 | 0.0051128 | -0.031521 | 0.0090964 | 0.057504 | -0.0097282 | 0.05154 | -0.0062567 | -0.002053 | -0.0031451 | 0.059542 | 0.032782 | 0.05196 | -61.2807 | 0.038035 | -61.2429 | 60.2946 | 60.1857 | 60.1537 | -61.265 | -61.2163 | 0.073618 | -61.3012 | 60.0903 | 60.2635 | 60.2576 | -61.4104 | 0.047903 | -0.043275 | 0.032192 | 0.069954 | 0.022051 | -0.15209 | -0.18412 | -0.097542 | -0.24756 | 0.096563 | 0.011692 | 0.10923 | -0.074293 | -0.080249 | 121.6074 | 121.4986 | 121.4666 | 61.3509 | -121.6028 | 121.4031 | 121.5764 | 121.5704 | 61.3865 | -121.7482
1094.875 | 121.9666 | -61.1801 | 60.4202 | -0.010149 | -0.031521 | 0.0090964 | 0.057718 | -0.0095144 | 0.051112 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.032568 | 0.051747 | -61.2761 | 0.038035 | -61.2338 | 60.29 | 60.1857 | 60.1537 | -61.2695 | -61.2163 | 0.078197 | -61.3058 | 60.104 | 60.2681 | 60.253 | -61.415 | -0.089427 | -0.13025 | -0.095981 | -0.05364 | 0.035787 | -0.23448 | -0.26652 | -0.23487 | -0.31623 | -0.036188 | -0.12564 | 0.10923 | -0.15211 | -0.16722 | 121.4701 | 121.3659 | 121.3338 | 61.2182 | -121.6898 | 121.2841 | 121.4482 | 121.4331 | 61.2583 | -121.8352
1096.625 | 121.9345 | -61.235 | 60.379 | -0.0025182 | -0.031521 | 0.0090964 | 0.058145 | -0.0095144 | 0.051326 | -0.013887 | -0.0022666 | -0.0033587 | 0.059328 | 0.032782 | 0.05196 | -61.2807 | 0.033457 | -61.2383 | 60.29 | 60.1766 | 60.1583 | -61.265 | -61.2071 | 0.078197 | -61.3012 | 60.104 | 60.2544 | 60.2484 | -61.4058 | -0.029917 | -0.089051 | -0.045628 | -0.003287 | 0.02663 | -0.20244 | -0.22074 | -0.17078 | -0.27503 | 0.0279 | -0.066128 | 0.10465 | -0.12465 | -0.1306 | 121.525 | 121.4116 | 121.3933 | 61.2685 | -121.644 | 121.339 | 121.4894 | 121.4835 | 61.3132 | -121.7849
1098.3281 | 121.907 | -61.2213 | 60.3836 | -0.010149 | -0.031521 | 0.0088826 | 0.057718 | -0.0099418 | 0.051112 | -0.021518 | -0.002053 | -0.0029313 | 0.059755 | 0.033209 | 0.052174 | -61.2761 | 0.033457 | -61.2338 | 60.2854 | 60.1766 | 60.1583 | -61.2558 | -61.2163 | 0.073618 | -61.3058 | 60.0903 | 60.2635 | 60.2438 | -61.4104 | -0.034492 | -0.098208 | -0.054783 | -0.012442 | 0.02205 | -0.20702 | -0.22532 | -0.18909 | -0.29334 | 0.00501 | -0.08444 | 0.10465 | -0.12007 | -0.13976 | 121.5067 | 121.3979 | 121.3796 | 61.2548 | -121.6394 | 121.3116 | 121.4848 | 121.4652 | 61.2949 | -121.794
1100.0781 | 121.8567 | -61.322 | 60.3241 | -0.0025182 | -0.031735 | 0.0090964 | 0.057718 | -0.0099418 | 0.05154 | -0.021518 | -0.0024804 | -0.0029313 | 0.059755 | 0.032782 | 0.05196 | -61.2807 | 0.033457 | -61.2429 | 60.2946 | 60.1857 | 60.1629 | -61.2695 | -61.2117 | 0.073618 | -61.3058 | 60.104 | 60.259 | 60.2484 | -61.4058 | 0.052479 | -0.029542 | 0.041347 | 0.079109 | 0.02663 | -0.13835 | -0.16123 | -0.083808 | -0.2201 | 0.1103 | 0.016268 | 0.10008 | -0.065139 | -0.075673 | 121.6166 | 121.5078 | 121.4849 | 61.3555 | -121.5936 | 121.426 | 121.581 | 121.5704 | 61.3956 | -121.7299
1101.8281 | 121.9391 | -61.2167 | 60.379 | -0.0025182 | -0.031735 | 0.0088826 | 0.057932 | -0.0095144 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.032782 | 0.051747 | -61.2807 | 0.033457 | -61.2429 | 60.29 | 60.1857 | 60.1446 | -61.2604 | -61.2163 | 0.06904 | -61.3012 | 60.0994 | 60.2635 | 60.2484 | -61.4058 | -0.043648 | -0.089051 | -0.063938 | -0.026176 | 0.017472 | -0.19328 | -0.23448 | -0.18909 | -0.2796 | 0.000433 | -0.084438 | 0.10465 | -0.11549 | -0.1306 | 121.5067 | 121.4025 | 121.3613 | 61.2502 | -121.6394 | 121.3162 | 121.4803 | 121.4652 | 61.2858 | -121.7849
1103.5781 | 121.9711 | -61.2946 | 60.2829 | -0.010149 | -0.031521 | 0.0090964 | 0.057504 | -0.0097282 | 0.051112 | -0.0062567 | -0.002053 | -0.0027177 | 0.059755 | 0.032568 | 0.051747 | -61.2853 | 0.042614 | -61.2429 | 60.2946 | 60.1812 | 60.1537 | -61.2604 | -61.2071 | 0.073618 | -61.3058 | 60.0948 | 60.2635 | 60.253 | -61.4196 | 0.034172 | 0.011657 | 0.009304 | 0.051644 | 0.017472 | -0.10173 | -0.12919 | -0.12501 | -0.18805 | 0.08741 | -0.011197 | 0.11381 | -0.019361 | -0.029895 | 121.5891 | 121.4757 | 121.4483 | 61.3372 | -121.5433 | 121.3894 | 121.5581 | 121.5476 | 61.3682 | -121.7025
1105.3281 | 121.962 | -61.203 | 60.4065 | -0.010149 | -0.031521 | 0.0090964 | 0.057718 | -0.0097282 | 0.051753 | -0.0062567 | -0.0018394 | -0.0035723 | 0.059328 | 0.032995 | 0.05196 | -61.2853 | 0.033457 | -61.2429 | 60.2946 | 60.1903 | 60.1537 | -61.265 | -61.2117 | 0.073618 | -61.3012 | 60.0994 | 60.2681 | 60.253 | -61.415 | -0.06196 | -0.11194 | -0.082249 | -0.039909 | 0.022051 | -0.21617 | -0.25279 | -0.21198 | -0.30707 | -0.008721 | -0.098171 | 0.11381 | -0.13838 | -0.15349 | 121.4976 | 121.3933 | 121.3567 | 61.2365 | -121.6715 | 121.3024 | 121.4711 | 121.456 | 61.2766 | -121.8215
1107.0156 | 121.9437 | -61.2305 | 60.3516 | -0.025411 | -0.031521 | 0.0090964 | 0.057932 | -0.0095144 | 0.051326 | -0.013887 | -0.0024804 | -0.0031451 | 0.059755 | 0.032782 | 0.051533 | -61.2807 | 0.033457 | -61.2475 | 60.2946 | 60.1766 | 60.1583 | -61.265 | -61.2209 | 0.078197 | -61.3058 | 60.0948 | 60.259 | 60.2393 | -61.4104 | -0.034494 | -0.057007 | -0.050205 | -0.017021 | 0.017473 | -0.17498 | -0.19327 | -0.17994 | -0.25672 | 0.009587 | -0.075284 | 0.10465 | -0.092604 | -0.1123 | 121.525 | 121.4071 | 121.3888 | 61.2639 | -121.6165 | 121.3253 | 121.4894 | 121.4697 | 61.3087 | -121.762
1108.7656 | 122.0032 | -61.1664 | 60.4065 | 0.0051128 | -0.031521 | 0.0088826 | 0.057932 | -0.0095144 | 0.051112 | -0.013887 | -0.002053 | -0.0029313 | 0.059755 | 0.032995 | 0.051533 | -61.2715 | 0.028878 | -61.2475 | 60.29 | 60.1812 | 60.1583 | -61.265 | -61.2163 | 0.078197 | -61.3103 | 60.0994 | 60.2635 | 60.2484 | -61.4104 | -0.098581 | -0.11652 | -0.10514 | -0.081108 | 0.017473 | -0.22533 | -0.24821 | -0.24403 | -0.30707 | -0.049921 | -0.14395 | 0.10008 | -0.14296 | -0.15807 | 121.4564 | 121.3475 | 121.3247 | 61.1953 | -121.6715 | 121.2658 | 121.4299 | 121.4148 | 61.2446 | -121.8169
1110.5 | 121.9437 | -61.1847 | 60.4019 | 0.012744 | -0.031307 | 0.00931 | 0.057718 | -0.0099418 | 0.051326 | -0.013887 | -0.0022666 | -0.0027177 | 0.059755 | 0.033209 | 0.051533 | -61.2761 | 0.038035 | -61.2475 | 60.29 | 60.1812 | 60.1537 | -61.265 | -61.2163 | 0.073618 | -61.3103 | 60.0994 | 60.2635 | 60.2484 | -61.4104 | -0.080271 | -0.11194 | -0.091404 | -0.062798 | 0.017473 | -0.22075 | -0.24821 | -0.22572 | -0.30249 | -0.031611 | -0.12564 | 0.10008 | -0.13838 | -0.15349 | 121.4747 | 121.3659 | 121.3384 | 61.2227 | -121.6669 | 121.2841 | 121.4482 | 121.4331 | 61.2583 | -121.8123
1112.1875 | 121.9574 | -61.2762 | 60.2875 | -0.010149 | -0.031735 | 0.0090964 | 0.057504 | -0.0095144 | 0.050899 | -0.029148 | -0.002053 | -0.0031451 | 0.059328 | 0.032782 | 0.05196 | -61.2761 | 0.038035 | -61.2429 | 60.29 | 60.1903 | 60.1583 | -61.2604 | -61.2071 | 0.073618 | -61.3058 | 60.0948 | 60.259 | 60.2576 | -61.4058 | 0.015861 | 0.002501 | 0.000149 | 0.033333 | 0.017472 | -0.097154 | -0.12919 | -0.12958 | -0.19263 | 0.069099 | -0.029508 | 0.10008 | -0.028518 | -0.029895 | 121.5662 | 121.4666 | 121.4345 | 61.3143 | -121.5479 | 121.3711 | 121.5352 | 121.5338 | 61.3499 | -121.6933
1113.9531 | 121.8979 | -61.2717 | 60.3378 | -0.010149 | -0.031735 | 0.00931 | 0.057718 | -0.0097282 | 0.051326 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059755 | 0.032995 | 0.051747 | -61.2807 | 0.028878 | -61.2383 | 60.29 | 60.1903 | 60.1583 | -61.2604 | -61.2071 | 0.082776 | -61.3058 | 60.0948 | 60.2498 | 60.253 | -61.415 | 0.011283 | -0.047853 | -0.009007 | 0.033334 | 0.022051 | -0.14751 | -0.17954 | -0.14332 | -0.24299 | 0.064521 | -0.034086 | 0.10923 | -0.088029 | -0.084827 | 121.5616 | 121.462 | 121.43 | 61.3005 | -121.5982 | 121.3665 | 121.5215 | 121.5247 | 61.3544 | -121.7528
1115.7031 | 121.8384 | -61.3403 | 60.3333 | -0.0025182 | -0.031735 | 0.0095236 | 0.057291 | -0.0097282 | 0.05154 | -0.021518 | -0.0024804 | -0.0029313 | 0.059969 | 0.032995 | 0.05196 | -61.2807 | 0.033457 | -61.2475 | 60.29 | 60.1857 | 60.1583 | -61.2695 | -61.2117 | 0.078197 | -61.3058 | 60.0948 | 60.2544 | 60.253 | -61.4058 | 0.07079 | -0.043275 | 0.059658 | 0.092842 | 0.022052 | -0.14751 | -0.17496 | -0.065497 | -0.23841 | 0.12861 | 0.034579 | 0.10008 | -0.078872 | -0.080249 | 121.6303 | 121.5261 | 121.4986 | 61.3738 | -121.6028 | 121.4352 | 121.5947 | 121.5933 | 61.4185 | -121.7391
1117.3906 | 121.9528 | -61.1938 | 60.3882 | -0.0025182 | -0.031735 | 0.0095236 | 0.057504 | -0.0095144 | 0.051112 | -0.013887 | -0.0018394 | -0.0029313 | 0.059755 | 0.032782 | 0.051747 | -61.2761 | 0.033457 | -61.2475 | 60.2946 | 60.1903 | 60.1583 | -61.2604 | -61.2117 | 0.078197 | -61.3058 | 60.0994 | 60.259 | 60.253 | -61.4058 | -0.066536 | -0.093629 | -0.082248 | -0.053642 | 0.012894 | -0.19786 | -0.2299 | -0.21198 | -0.28876 | -0.017876 | -0.11191 | 0.10008 | -0.12923 | -0.13518 | 121.4884 | 121.3842 | 121.3521 | 61.2273 | -121.6486 | 121.2933 | 121.4528 | 121.4469 | 61.272 | -121.794
1119.1719 | 121.8613 | -61.3129 | 60.3241 | -0.025411 | -0.031521 | 0.00931 | 0.057504 | -0.0095144 | 0.051112 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.032568 | 0.051747 | -61.2761 | 0.038035 | -61.2383 | 60.2991 | 60.1903 | 60.1583 | -61.2604 | -61.2071 | 0.073618 | -61.2966 | 60.0948 | 60.2544 | 60.253 | -61.4104 | 0.052482 | -0.024963 | 0.03677 | 0.074533 | 0.022051 | -0.13377 | -0.16581 | -0.097542 | -0.22925 | 0.10572 | 0.016271 | 0.11381 | -0.069717 | -0.071094 | 121.612 | 121.5032 | 121.4712 | 61.3509 | -121.5845 | 121.4077 | 121.5672 | 121.5659 | 61.3865 | -121.7345
1120.8594 | 121.843 | -61.3266 | 60.3378 | 0.0051128 | -0.031948 | 0.0090964 | 0.057718 | -0.0097282 | 0.051112 | -0.021518 | -0.0022666 | -0.0031451 | 0.059755 | 0.033209 | 0.05132 | -61.2807 | 0.028878 | -61.2475 | 60.2946 | 60.1903 | 60.1629 | -61.265 | -61.2117 | 0.073618 | -61.3012 | 60.0994 | 60.2544 | 60.2484 | -61.4104 | 0.061636 | -0.043275 | 0.045925 | 0.079109 | 0.017473 | -0.14751 | -0.17496 | -0.083809 | -0.23841 | 0.11488 | 0.025425 | 0.10923 | -0.08345 | -0.089406 | 121.6212 | 121.5169 | 121.4895 | 61.3555 | -121.6028 | 121.426 | 121.581 | 121.575 | 61.4002 | -121.7482
1122.5938 | 121.8338 | -61.3174 | 60.347 | -0.01778 | -0.031735 | 0.0088826 | 0.057718 | -0.0097282 | 0.051326 | -0.029148 | -0.0024804 | -0.0031451 | 0.059542 | 0.032995 | 0.051533 | -61.2715 | 0.033457 | -61.2475 | 60.2946 | 60.1903 | 60.1629 | -61.265 | -61.2117 | 0.082776 | -61.3012 | 60.0994 | 60.259 | 60.253 | -61.4058 | 0.052481 | -0.05243 | 0.045927 | 0.069954 | 0.017473 | -0.15666 | -0.18412 | -0.088385 | -0.24756 | 0.10572 | 0.01627 | 0.10465 | -0.088027 | -0.093982 | 121.612 | 121.5078 | 121.4803 | 61.3509 | -121.6119 | 121.4169 | 121.5764 | 121.5704 | 61.4002 | -121.7528
1124.3438 | 121.9208 | -61.1847 | 60.3973 | 0.0051128 | -0.031307 | 0.00931 | 0.057718 | -0.0097282 | 0.051326 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059542 | 0.032782 | 0.051747 | -61.2807 | 0.028878 | -61.2429 | 60.2991 | 60.1812 | 60.1583 | -61.2604 | -61.2117 | 0.06904 | -61.3012 | 60.0948 | 60.2635 | 60.2576 | -61.415 | -0.075692 | -0.098205 | -0.095982 | -0.05822 | 0.017472 | -0.21617 | -0.23905 | -0.23029 | -0.3025 | -0.027032 | -0.11648 | 0.11381 | -0.1338 | -0.13976 | 121.4838 | 121.3659 | 121.343 | 61.2136 | -121.6577 | 121.2795 | 121.4482 | 121.4423 | 61.2537 | -121.8123
1126.0938 | 121.8613 | -61.3358 | 60.3012 | -0.010149 | -0.031735 | 0.00931 | 0.057504 | -0.0097282 | 0.05154 | -0.0062567 | -0.002053 | -0.0031451 | 0.059755 | 0.032782 | 0.051747 | -61.2807 | 0.028878 | -61.2429 | 60.2946 | 60.1857 | 60.1629 | -61.265 | -61.2071 | 0.073618 | -61.3058 | 60.0948 | 60.259 | 60.2576 | -61.415 | 0.070791 | -0.006653 | 0.05508 | 0.092842 | 0.022051 | -0.11547 | -0.13834 | -0.079232 | -0.20636 | 0.12861 | 0.030001 | 0.10923 | -0.04225 | -0.043627 | 121.6303 | 121.5215 | 121.4986 | 61.3646 | -121.5662 | 121.4306 | 121.5947 | 121.5933 | 61.4094 | -121.7162
1127.7812 | 121.8475 | -61.2167 | 60.4294 | -0.010149 | -0.031521 | 0.00931 | 0.057718 | -0.0095144 | 0.051753 | -0.0062567 | -0.0022666 | -0.0029313 | 0.059969 | 0.033209 | 0.051533 | -61.2715 | 0.0243 | -61.2475 | 60.29 | 60.1903 | 60.1629 | -61.2558 | -61.2163 | 0.073618 | -61.3058 | 60.104 | 60.259 | 60.2576 | -61.4104 | -0.039069 | -0.1394 | -0.054781 | -0.030754 | 0.008315 | -0.23906 | -0.26652 | -0.19367 | -0.32538 | 0.000433 | -0.089017 | 0.10465 | -0.17042 | -0.1718 | 121.5067 | 121.4071 | 121.3796 | 61.241 | -121.6852 | 121.3207 | 121.4757 | 121.4743 | 61.2904 | -121.8398
1129.5469 | 121.8201 | -61.3449 | 60.3378 | 0.0051128 | -0.031735 | 0.0088826 | 0.057504 | -0.0095144 | 0.051326 | -0.021518 | -0.0022666 | -0.0033587 | 0.059542 | 0.033209 | 0.051747 | -61.2761 | 0.028878 | -61.2383 | 60.2991 | 60.1903 | 60.172 | -61.2695 | -61.2117 | 0.082776 | -61.3012 | 60.104 | 60.2544 | 60.2576 | -61.4058 | 0.075368 | -0.038696 | 0.068814 | 0.10658 | 0.031209 | -0.14751 | -0.16581 | -0.060919 | -0.23383 | 0.13319 | 0.043736 | 0.10465 | -0.08345 | -0.080249 | 121.644 | 121.5352 | 121.5169 | 61.3738 | -121.6074 | 121.4489 | 121.5993 | 121.6025 | 61.4277 | -121.7437
1131.2344 | 121.8658 | -61.2625 | 60.4248 | -0.010149 | -0.031735 | 0.00931 | 0.057718 | -0.0099418 | 0.051753 | -0.013887 | -0.0022666 | -0.0033587 | 0.059328 | 0.033423 | 0.051747 | -61.2761 | 0.028878 | -61.2429 | 60.2991 | 60.1857 | 60.1629 | -61.2604 | -61.2071 | 0.073618 | -61.2966 | 60.0948 | 60.259 | 60.2576 | -61.4104 | 0.002128 | -0.12567 | -0.013584 | 0.0196 | 0.017472 | -0.23906 | -0.26194 | -0.1479 | -0.32996 | 0.055366 | -0.034083 | 0.11381 | -0.16585 | -0.16722 | 121.5616 | 121.4483 | 121.4254 | 61.2914 | -121.6852 | 121.3574 | 121.5215 | 121.5201 | 61.3361 | -121.8352
1133 | 121.8887 | -61.2579 | 60.3699 | 0.0051128 | -0.031948 | 0.00931 | 0.057718 | -0.0099418 | 0.051326 | -0.0062567 | -0.0022666 | -0.0029313 | 0.059755 | 0.032995 | 0.051533 | -61.2761 | 0.028878 | -61.2475 | 60.29 | 60.1903 | 60.1583 | -61.2604 | -61.2071 | 0.078197 | -61.3058 | 60.104 | 60.2544 | 60.2484 | -61.4104 | -0.002449 | -0.079896 | -0.018161 | 0.010445 | 0.012894 | -0.17955 | -0.21158 | -0.15247 | -0.26587 | 0.050789 | -0.047818 | 0.10465 | -0.11549 | -0.12145 | 121.5479 | 121.4483 | 121.4162 | 61.2868 | -121.6303 | 121.3619 | 121.5123 | 121.5064 | 61.3361 | -121.7803
1134.75 | 121.8842 | -61.2854 | 60.3607 | -0.010149 | -0.031735 | 0.00931 | 0.057718 | -0.0097282 | 0.051326 | -0.021518 | -0.0022666 | -0.0029313 | 0.059542 | 0.033423 | 0.051533 | -61.2807 | 0.033457 | -61.2429 | 60.2991 | 60.1903 | 60.1674 | -61.265 | -61.2026 | 0.078197 | -61.3058 | 60.0994 | 60.2635 | 60.253 | -61.4104 | 0.020437 | -0.061584 | 0.004726 | 0.042488 | 0.022051 | -0.1704 | -0.19327 | -0.12501 | -0.26129 | 0.082833 | -0.020353 | 0.10465 | -0.097181 | -0.10771 | 121.5845 | 121.4757 | 121.4528 | 61.3189 | -121.6257 | 121.3848 | 121.5489 | 121.5384 | 61.3636 | -121.7711
1136.4531 | 121.8887 | -61.2762 | 60.4294 | -0.010149 | -0.031521 | 0.0090964 | 0.057504 | -0.0099418 | 0.05154 | -0.013887 | -0.0022666 | -0.0029313 | 0.059328 | 0.033209 | 0.051533 | -61.2761 | 0.028878 | -61.2429 | 60.2991 | 60.1903 | 60.1583 | -61.2741 | -61.2026 | 0.078197 | -61.3058 | 60.0948 | 60.259 | 60.2576 | -61.4058 | 0.002124 | -0.13025 | 0.000149 | 0.033333 | 0.031209 | -0.23906 | -0.27109 | -0.12958 | -0.33454 | 0.073678 | -0.029508 | 0.10008 | -0.17042 | -0.1718 | 121.5754 | 121.4666 | 121.4345 | 61.3051 | -121.7035 | 121.3711 | 121.5352 | 121.5338 | 61.3544 | -121.8352
1138.2031 | 121.9299 | -61.2305 | 60.3241 | -0.010149 | -0.031735 | 0.0090964 | 0.057718 | -0.0095144 | 0.051326 | -0.013887 | -0.0022666 | -0.0029313 | 0.059328 | 0.033423 | 0.05132 | -61.2761 | 0.028878 | -61.2429 | 60.2991 | 60.1903 | 60.1583 | -61.2604 | -61.2071 | 0.078197 | -61.3058 | 60.104 | 60.2635 | 60.253 | -61.415 | -0.029915 | -0.024963 | -0.045627 | -0.012443 | 0.017472 | -0.13377 | -0.16581 | -0.18452 | -0.2201 | 0.023323 | -0.075284 | 0.10923 | -0.06056 | -0.071094 | 121.5296 | 121.4208 | 121.3888 | 61.2593 | -121.5845 | 121.3345 | 121.494 | 121.4835 | 61.3087 | -121.7391
1139.8906 | 121.9254 | -61.2122 | 60.3516 | -0.010149 | -0.031948 | 0.0090964 | 0.057718 | -0.0095144 | 0.051326 | -0.0062567 | -0.002053 | -0.0031451 | 0.059328 | 0.033209 | 0.05132 | -61.2715 | 0.033457 | -61.2475 | 60.2946 | 60.1903 | 60.1674 | -61.2558 | -61.2071 | 0.078197 | -61.3058 | 60.104 | 60.2635 | 60.2622 | -61.4058 | -0.043647 | -0.057007 | -0.059359 | -0.035332 | 0.008315 | -0.16124 | -0.18412 | -0.19367 | -0.24756 | 0.005012 | -0.093595 | 0.10008 | -0.088025 | -0.089402 | 121.5067 | 121.4025 | 121.3796 | 61.2456 | -121.6074 | 121.3162 | 121.4757 | 121.4743 | 61.2904 | -121.7574
1141.6406 | 121.9711 | -61.2671 | 60.3012 | -0.0025182 | -0.031735 | 0.0095236 | 0.057718 | -0.0097282 | 0.051112 | -0.0062567 | -0.002053 | -0.0031451 | 0.059328 | 0.033209 | 0.051533 | -61.2669 | 0.0243 | -61.2383 | 60.2991 | 60.1949 | 60.1674 | -61.2558 | -61.2071 | 0.078197 | -61.3012 | 60.0948 | 60.2681 | 60.253 | -61.415 | 0.011285 | -0.002074 | 0.000151 | 0.028757 | 0.017472 | -0.10631 | -0.13376 | -0.1479 | -0.20636 | 0.059944 | -0.034084 | 0.11381 | -0.033092 | -0.048205 | 121.5662 | 121.462 | 121.4345 | 61.2914 | -121.557 | 121.3619 | 121.5352 | 121.5201 | 61.3453 | -121.7162
1143.3906 | 121.9711 | -61.2534 | 60.2829 | -0.01778 | -0.031735 | 0.0090964 | 0.057291 | -0.0095144 | 0.05154 | -0.029148 | -0.002053 | -0.0029313 | 0.059542 | 0.033423 | 0.051533 | -61.2761 | 0.028878 | -61.2383 | 60.2991 | 60.1903 | 60.1629 | -61.2604 | -61.2117 | 0.073618 | -61.3012 | 60.1132 | 60.2635 | 60.2484 | -61.4058 | -0.007027 | 0.016236 | -0.022739 | 0.015024 | 0.022051 | -0.092576 | -0.12003 | -0.15247 | -0.16974 | 0.041633 | -0.047817 | 0.10465 | -0.019361 | -0.034474 | 121.5525 | 121.4437 | 121.4162 | 61.2822 | -121.5433 | 121.3665 | 121.5169 | 121.5018 | 61.327 | -121.6887
1145.1562 | 121.8933 | -61.3037 | 60.3745 | -0.010149 | -0.031521 | 0.00931 | 0.057077 | -0.0097282 | 0.051112 | -0.021518 | -0.0022666 | -0.0031451 | 0.059542 | 0.033423 | 0.051533 | -61.2669 | 0.028878 | -61.2429 | 60.2991 | 60.1995 | 60.1629 | -61.2695 | -61.2071 | 0.078197 | -61.2966 | 60.1086 | 60.2635 | 60.253 | -61.415 | 0.034169 | -0.075317 | 0.036772 | 0.060799 | 0.02663 | -0.17497 | -0.21158 | -0.11127 | -0.26587 | 0.096565 | 0.007116 | 0.11839 | -0.11091 | -0.12145 | 121.6028 | 121.5032 | 121.4666 | 61.3326 | -121.644 | 121.4123 | 121.5672 | 121.5567 | 61.3819 | -121.7894
1146.8438 | 121.8704 | -61.2076 | 60.4385 | 0.0051128 | -0.031735 | 0.00931 | 0.057932 | -0.0095144 | 0.051112 | -0.0062567 | -0.002053 | -0.0031451 | 0.059755 | 0.033636 | 0.051106 | -61.2761 | 0.015142 | -61.2429 | 60.2946 | 60.1949 | 60.1629 | -61.265 | -61.2163 | 0.078197 | -61.3103 | 60.0994 | 60.2635 | 60.253 | -61.4104 | -0.057382 | -0.14398 | -0.068515 | -0.035331 | 0.022051 | -0.24364 | -0.27567 | -0.20283 | -0.33911 | -0.008722 | -0.10275 | 0.10008 | -0.175 | -0.18554 | 121.5021 | 121.4025 | 121.3704 | 61.2227 | -121.7035 | 121.307 | 121.4711 | 121.4606 | 61.2858 | -121.8489
1148.5938 | 121.8475 | -61.3312 | 60.3241 | -0.01778 | -0.031521 | 0.0090964 | 0.057718 | -0.0095144 | 0.051326 | -0.013887 | -0.0024804 | -0.0031451 | 0.059542 | 0.032995 | 0.050892 | -61.2715 | 0.028878 | -61.2475 | 60.2991 | 60.1995 | 60.1674 | -61.2604 | -61.198 | 0.078197 | -61.3058 | 60.104 | 60.2635 | 60.2576 | -61.4104 | 0.070793 | -0.024963 | 0.05966 | 0.083687 | 0.012894 | -0.12462 | -0.15665 | -0.079231 | -0.2201 | 0.13319 | 0.025424 | 0.10465 | -0.06056 | -0.066516 | 121.6303 | 121.5307 | 121.4986 | 61.3601 | -121.5845 | 121.4352 | 121.5947 | 121.5888 | 61.4094 | -121.7345
1150.3281 | 121.8842 | -61.2625 | 60.4019 | -0.010149 | -0.032162 | 0.0090964 | 0.057504 | -0.0095144 | 0.051112 | -0.0062567 | -0.0024804 | -0.0033587 | 0.059542 | 0.033636 | 0.05132 | -61.2715 | 0.0243 | -61.2338 | 60.29 | 60.1995 | 60.1629 | -61.265 | -61.2071 | 0.073618 | -61.3012 | 60.1132 | 60.2635 | 60.2622 | -61.4104 | -0.002451 | -0.11194 | -0.009005 | 0.028757 | 0.031208 | -0.20244 | -0.23905 | -0.1479 | -0.28876 | 0.055366 | -0.038662 | 0.10923 | -0.13838 | -0.13976 | 121.5525 | 121.462 | 121.4254 | 61.2868 | -121.6669 | 121.3757 | 121.526 | 121.5247 | 61.3361 | -121.8123
1152.0781 | 121.8475 | -61.2991 | 60.3378 | -0.010149 | -0.031948 | 0.0088826 | 0.057291 | -0.0097282 | 0.051112 | -0.013887 | -0.0022666 | -0.0031451 | 0.059755 | 0.033423 | 0.051533 | -61.2807 | 0.015142 | -61.2383 | 60.2946 | 60.1949 | 60.1583 | -61.2695 | -61.2117 | 0.078197 | -61.3012 | 60.0994 | 60.2635 | 60.2622 | -61.415 | 0.029591 | -0.043275 | 0.018459 | 0.0608 | 0.031209 | -0.14293 | -0.17954 | -0.11585 | -0.23841 | 0.087409 | -0.002041 | 0.11381 | -0.074293 | -0.07567 | 121.5937 | 121.494 | 121.4574 | 61.3143 | -121.6074 | 121.3986 | 121.5627 | 121.5613 | 61.3773 | -121.7528
1153.7656 | 121.9803 | -61.2671 | 60.2921 | -0.01778 | -0.032376 | 0.008669 | 0.057718 | -0.0097282 | 0.051112 | -0.021518 | -0.002053 | -0.0029313 | 0.059328 | 0.033209 | 0.05132 | -61.2761 | 0.019721 | -61.2475 | 60.3037 | 60.1903 | 60.1766 | -61.2604 | -61.2071 | 0.078197 | -61.3058 | 60.104 | 60.2635 | 60.253 | -61.4058 | 0.006706 | 0.011659 | -0.009006 | 0.0196 | 0.012894 | -0.10173 | -0.11545 | -0.13874 | -0.18805 | 0.059944 | -0.038663 | 0.10008 | -0.028516 | -0.03905 | 121.5708 | 121.4574 | 121.4437 | 61.2868 | -121.5524 | 121.3711 | 121.5306 | 121.5201 | 61.3453 | -121.6979
1155.5156 | 121.9208 | -61.2213 | 60.3607 | -0.010149 | -0.032162 | 0.0090964 | 0.057504 | -0.0093008 | 0.051326 | -0.013887 | -0.002053 | -0.0031451 | 0.059328 | 0.03385 | 0.051533 | -61.2669 | 0.0243 | -61.2429 | 60.2946 | 60.1903 | 60.1674 | -61.265 | -61.2117 | 0.078197 | -61.2966 | 60.0994 | 60.2727 | 60.2622 | -61.4058 | -0.04365 | -0.066163 | -0.045626 | -0.021599 | 0.022051 | -0.1704 | -0.19327 | -0.18452 | -0.26129 | 0.009589 | -0.075282 | 0.10923 | -0.088024 | -0.098558 | 121.5159 | 121.4116 | 121.3888 | 61.2456 | -121.6257 | 121.3207 | 121.494 | 121.4835 | 61.2995 | -121.7665
1157.2656 | 121.8384 | -61.3083 | 60.3745 | -0.0025182 | -0.032162 | 0.00931 | 0.057718 | -0.0097282 | 0.051112 | -0.021518 | -0.0024804 | -0.0031451 | 0.059969 | 0.033636 | 0.051533 | -61.2807 | 0.0243 | -61.2383 | 60.2991 | 60.1949 | 60.1674 | -61.2604 | -61.2071 | 0.073618 | -61.2966 | 60.0948 | 60.259 | 60.2622 | -61.4104 | 0.047905 | -0.075317 | 0.027615 | 0.069956 | 0.022051 | -0.17955 | -0.20701 | -0.10212 | -0.27961 | 0.10114 | 0.011694 | 0.11381 | -0.11549 | -0.11229 | 121.6074 | 121.5032 | 121.4757 | 61.3326 | -121.6348 | 121.4031 | 121.5672 | 121.5704 | 61.3819 | -121.7849
1159.0156 | 121.907 | -61.1938 | 60.4385 | -0.0025182 | -0.031735 | 0.00931 | 0.057718 | -0.0097282 | 0.051326 | -0.021518 | -0.0022666 | -0.0029313 | 0.059328 | 0.033636 | 0.05132 | -61.2715 | 0.015142 | -61.2383 | 60.2991 | 60.1903 | 60.172 | -61.2695 | -61.2026 | 0.078197 | -61.3012 | 60.104 | 60.2544 | 60.2622 | -61.415 | -0.075694 | -0.1394 | -0.077669 | -0.044485 | 0.031209 | -0.24822 | -0.26651 | -0.22114 | -0.33454 | -0.008719 | -0.10733 | 0.11381 | -0.18416 | -0.17638 | 121.493 | 121.3842 | 121.3659 | 61.209 | -121.7081 | 121.2978 | 121.4482 | 121.456 | 61.272 | -121.8535
1160.7031 | 121.9345 | -61.2122 | 60.3561 | -0.010149 | -0.032162 | 0.0090964 | 0.057291 | -0.0097282 | 0.05154 | -0.021518 | -0.0022666 | -0.0033587 | 0.059755 | 0.033209 | 0.05132 | -61.2807 | 0.019721 | -61.2429 | 60.2991 | 60.1949 | 60.1674 | -61.2604 | -61.2071 | 0.082776 | -61.3058 | 60.104 | 60.2681 | 60.2622 | -61.415 | -0.048226 | -0.057006 | -0.068516 | -0.030754 | 0.017472 | -0.16124 | -0.1887 | -0.20283 | -0.25214 | 0.005012 | -0.093595 | 0.10923 | -0.088024 | -0.09398 | 121.5113 | 121.4071 | 121.3796 | 61.2319 | -121.6165 | 121.3162 | 121.4803 | 121.4743 | 61.2949 | -121.7711
1162.4375 | 121.9803 | -61.1847 | 60.4019 | -0.010149 | -0.031948 | 0.0088826 | 0.057718 | -0.0097282 | 0.051326 | -0.013887 | -0.002053 | -0.0029313 | 0.059755 | 0.03385 | 0.05132 | -61.2715 | 0.015142 | -61.2338 | 60.3037 | 60.1949 | 60.1629 | -61.2695 | -61.2071 | 0.078197 | -61.3012 | 60.1086 | 60.2681 | 60.2576 | -61.4104 | -0.08485 | -0.098205 | -0.086825 | -0.049063 | 0.035787 | -0.20702 | -0.23905 | -0.22572 | -0.29334 | -0.022454 | -0.11648 | 0.10923 | -0.1338 | -0.14434 | 121.4884 | 121.3796 | 121.3476 | 61.1998 | -121.6715 | 121.2933 | 121.4528 | 121.4423 | 61.2629 | -121.8123
1164.1875 | 121.8567 | -61.2122 | 60.4431 | 0.0051128 | -0.031735 | 0.0088826 | 0.057504 | -0.0097282 | 0.05154 | -0.013887 | -0.002053 | -0.0029313 | 0.059755 | 0.033209 | 0.051533 | -61.2807 | 0.010564 | -61.2383 | 60.2946 | 60.1903 | 60.1674 | -61.265 | -61.2071 | 0.078197 | -61.3058 | 60.104 | 60.2727 | 60.2576 | -61.415 | -0.052805 | -0.14856 | -0.068516 | -0.026175 | 0.02663 | -0.25279 | -0.27567 | -0.20283 | -0.33911 | 0.005012 | -0.093595 | 0.10923 | -0.17042 | -0.18553 | 121.5067 | 121.4025 | 121.3796 | 61.2227 | -121.7081 | 121.3162 | 121.4849 | 121.4697 | 61.2904 | -121.8581
1165.875 | 121.9757 | -61.2762 | 60.2921 | -0.01778 | -0.031948 | 0.0090964 | 0.057718 | -0.0097282 | 0.051753 | -0.021518 | -0.0022666 | -0.0029313 | 0.059328 | 0.033209 | 0.05132 | -61.2715 | 0.019721 | -61.2475 | 60.2991 | 60.1995 | 60.1766 | -61.265 | -61.2071 | 0.078197 | -61.3058 | 60.0994 | 60.2727 | 60.2576 | -61.415 | 0.011282 | 0.007081 | 0.004728 | 0.028755 | 0.017473 | -0.092573 | -0.11545 | -0.13874 | -0.19263 | 0.069099 | -0.029508 | 0.10923 | -0.019359 | -0.034472 | 121.5754 | 121.4757 | 121.4528 | 61.296 | -121.557 | 121.3757 | 121.5489 | 121.5338 | 61.3544 | -121.707
1167.625 | 121.9666 | -61.2625 | 60.3287 | -0.025411 | -0.031948 | 0.0090964 | 0.057718 | -0.0099418 | 0.051967 | -0.021518 | -0.0022666 | -0.0031451 | 0.059755 | 0.033423 | 0.05132 | -61.2715 | 0.019721 | -61.2383 | 60.3037 | 60.1995 | 60.172 | -61.2604 | -61.2071 | 0.078197 | -61.3012 | 60.0994 | 60.2681 | 60.2576 | -61.4104 | 0.002128 | -0.024962 | -0.009005 | 0.024179 | 0.022051 | -0.12919 | -0.15665 | -0.1479 | -0.22925 | 0.055366 | -0.038662 | 0.10923 | -0.060558 | -0.071093 | 121.5662 | 121.462 | 121.4345 | 61.2822 | -121.5891 | 121.3619 | 121.5306 | 121.5201 | 61.3407 | -121.7391
1169.3906 | 121.8521 | -61.3129 | 60.3745 | -0.01778 | -0.031948 | 0.00931 | 0.057718 | -0.0099418 | 0.051753 | -0.013887 | -0.0022666 | -0.0031451 | 0.059969 | 0.033209 | 0.05132 | -61.2807 | 0.010564 | -61.2429 | 60.3083 | 60.1903 | 60.172 | -61.2558 | -61.2117 | 0.078197 | -61.3012 | 60.0994 | 60.2635 | 60.253 | -61.4104 | 0.057061 | -0.066161 | 0.032192 | 0.069954 | 0.012893 | -0.18413 | -0.20243 | -0.097542 | -0.27503 | 0.10114 | 0.011692 | 0.10923 | -0.11091 | -0.12145 | 121.6212 | 121.5032 | 121.4849 | 61.3234 | -121.6303 | 121.4123 | 121.5764 | 121.5659 | 61.3911 | -121.7849
1171.1406 | 121.9025 | -61.2442 | 60.4019 | -0.010149 | -0.031948 | 0.0090964 | 0.057504 | -0.0099418 | 0.051326 | -0.013887 | -0.002053 | -0.0029313 | 0.059542 | 0.033423 | 0.051106 | -61.2715 | 0.015142 | -61.2429 | 60.2991 | 60.1949 | 60.172 | -61.265 | -61.2071 | 0.064461 | -61.2966 | 60.1086 | 60.2727 | 60.253 | -61.4104 | -0.020761 | -0.10278 | -0.027315 | 0.00129 | 0.022051 | -0.20702 | -0.22989 | -0.16621 | -0.29334 | 0.037056 | -0.052393 | 0.11381 | -0.12922 | -0.14891 | 121.5433 | 121.4391 | 121.4162 | 61.2593 | -121.6669 | 121.3528 | 121.5169 | 121.4972 | 61.3087 | -121.8123
1172.8281 | 121.8933 | -61.3129 | 60.3149 | -0.025411 | -0.032162 | 0.0090964 | 0.057504 | -0.0097282 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059755 | 0.033423 | 0.051106 | -61.2715 | 0.015142 | -61.2383 | 60.2991 | 60.1949 | 60.172 | -61.2604 | -61.2026 | 0.073618 | -61.3058 | 60.104 | 60.2727 | 60.2622 | -61.4104 | 0.052482 | -0.015807 | 0.041349 | 0.074533 | 0.022051 | -0.12004 | -0.14292 | -0.097542 | -0.21094 | 0.1103 | 0.007113 | 0.10465 | -0.042247 | -0.052781 | 121.612 | 121.5078 | 121.4849 | 61.328 | -121.5753 | 121.4169 | 121.5856 | 121.575 | 61.3865 | -121.7253
1174.5781 | 121.9757 | -61.1435 | 60.4019 | -0.010149 | -0.032162 | 0.0090964 | 0.057932 | -0.0095144 | 0.05154 | -0.0062567 | -0.0022666 | -0.0033587 | 0.059755 | 0.033423 | 0.05132 | -61.2761 | 0.010564 | -61.2475 | 60.2991 | 60.1903 | 60.1766 | -61.265 | -61.2026 | 0.078197 | -61.3058 | 60.104 | 60.2681 | 60.253 | -61.4104 | -0.12147 | -0.10278 | -0.1326 | -0.104 | 0.017473 | -0.21159 | -0.22531 | -0.26691 | -0.29792 | -0.059073 | -0.16226 | 0.10465 | -0.1338 | -0.14891 | 121.4426 | 121.3338 | 121.3201 | 61.1541 | -121.6669 | 121.2475 | 121.4116 | 121.3965 | 61.2217 | -121.8123
1176.2812 | 121.9254 | -61.2167 | 60.3653 | -0.010149 | -0.031735 | 0.00931 | 0.057718 | -0.0099418 | 0.051326 | -0.013887 | -0.0022666 | -0.0031451 | 0.059328 | 0.033423 | 0.05132 | -61.2761 | 0.0243 | -61.2383 | 60.3037 | 60.1949 | 60.172 | -61.2558 | -61.2026 | 0.078197 | -61.3012 | 60.0994 | 60.2727 | 60.253 | -61.415 | -0.039069 | -0.061583 | -0.05936 | -0.021597 | 0.017472 | -0.17039 | -0.19327 | -0.19825 | -0.26587 | 0.014169 | -0.084438 | 0.11381 | -0.092601 | -0.11229 | 121.5204 | 121.4116 | 121.3888 | 61.241 | -121.6211 | 121.3162 | 121.4894 | 121.4697 | 61.2949 | -121.7803
1178.0312 | 122.0123 | -61.1984 | 60.3928 | -0.01778 | -0.032162 | 0.00931 | 0.057932 | -0.0097282 | 0.05154 | -0.013887 | -0.002053 | -0.0029313 | 0.059542 | 0.033423 | 0.051533 | -61.2715 | 0.019721 | -61.2429 | 60.3083 | 60.1949 | 60.1674 | -61.2604 | -61.2026 | 0.073618 | -61.3012 | 60.104 | 60.2681 | 60.2576 | -61.4104 | -0.061959 | -0.084471 | -0.073092 | -0.044487 | 0.017472 | -0.19786 | -0.22532 | -0.21198 | -0.28876 | -0.004142 | -0.10275 | 0.10923 | -0.12465 | -0.13518 | 121.5067 | 121.3933 | 121.3659 | 61.2181 | -121.6531 | 121.3024 | 121.4665 | 121.456 | 61.272 | -121.8032
1179.7344 | 121.8338 | -61.2259 | 60.4431 | -0.01778 | -0.032376 | 0.0090964 | 0.057718 | -0.010369 | 0.051326 | -0.029148 | -0.0024804 | -0.0031451 | 0.059328 | 0.033636 | 0.05132 | -61.2761 | 0.015142 | -61.2383 | 60.3037 | 60.1903 | 60.1766 | -61.2604 | -61.2026 | 0.078197 | -61.2966 | 60.1132 | 60.2773 | 60.2622 | -61.4104 | -0.034493 | -0.1394 | -0.050205 | -0.012442 | 0.022051 | -0.25279 | -0.26651 | -0.18452 | -0.32996 | 0.023324 | -0.070704 | 0.11381 | -0.16584 | -0.18095 | 121.5296 | 121.4162 | 121.4025 | 61.241 | -121.7035 | 121.339 | 121.5032 | 121.4881 | 61.3041 | -121.8535
1181.4844 | 121.8704 | -61.2122 | 60.4568 | -0.010149 | -0.031948 | 0.00931 | 0.057932 | -0.0099418 | 0.05154 | -0.0062567 | -0.002053 | -0.0031451 | 0.059542 | 0.033636 | 0.051533 | -61.2715 | 0.015142 | -61.2429 | 60.3083 | 60.1995 | 60.1766 | -61.265 | -61.198 | 0.087354 | -61.3012 | 60.0994 | 60.2727 | 60.2713 | -61.4104 | -0.052805 | -0.14856 | -0.059359 | -0.030754 | 0.022051 | -0.25737 | -0.28025 | -0.19825 | -0.35742 | 0.01417 | -0.089016 | 0.10923 | -0.18415 | -0.18553 | 121.5204 | 121.4116 | 121.3888 | 61.2273 | -121.7218 | 121.3116 | 121.4849 | 121.4835 | 61.2995 | -121.8673
1183.1719 | 121.9757 | -61.1847 | 60.4202 | -0.010149 | -0.032162 | 0.0090964 | 0.057504 | -0.0099418 | 0.051326 | -0.021518 | -0.002053 | -0.0027177 | 0.059328 | 0.033636 | 0.05132 | -61.2715 | 0.015142 | -61.2338 | 60.2991 | 60.1949 | 60.1812 | -61.2558 | -61.2071 | 0.082776 | -61.3012 | 60.1177 | 60.2819 | 60.2622 | -61.4058 | -0.071113 | -0.12109 | -0.086825 | -0.049063 | 0.02205 | -0.22533 | -0.23905 | -0.22114 | -0.30249 | -0.022454 | -0.11648 | 0.10465 | -0.13838 | -0.15807 | 121.4838 | 121.3796 | 121.3659 | 61.1998 | -121.676 | 121.3024 | 121.4665 | 121.4469 | 61.2675 | -121.8261
1184.9062 | 121.8796 | -61.2717 | 60.3882 | -0.010149 | -0.032162 | 0.00931 | 0.057718 | -0.010155 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.033423 | 0.05132 | -61.2669 | 0.005985 | -61.2338 | 60.3083 | 60.2086 | 60.1858 | -61.2604 | -61.2026 | 0.073618 | -61.292 | 60.104 | 60.2819 | 60.2759 | -61.4012 | 0.011283 | -0.079894 | 0.004728 | 0.037912 | 0.026629 | -0.17955 | -0.20243 | -0.12958 | -0.28418 | 0.0691 | -0.02035 | 0.10923 | -0.10633 | -0.11229 | 121.58 | 121.4803 | 121.4574 | 61.2777 | -121.6486 | 121.3757 | 121.5535 | 121.5476 | 61.3453 | -121.7894
1186.6562 | 121.9299 | -61.2122 | 60.3653 | -0.010149 | -0.032376 | 0.00931 | 0.057718 | -0.0097282 | 0.05154 | -0.029148 | -0.0022666 | -0.0031451 | 0.059755 | 0.033423 | 0.051106 | -61.2624 | 0.015142 | -61.2338 | 60.3129 | 60.2041 | 60.1766 | -61.2558 | -61.1934 | 0.078197 | -61.2874 | 60.1132 | 60.2727 | 60.2713 | -61.4058 | -0.043647 | -0.052426 | -0.050202 | -0.021597 | 0.02205 | -0.16124 | -0.18869 | -0.19367 | -0.25214 | 0.018748 | -0.07528 | 0.11839 | -0.092601 | -0.093978 | 121.525 | 121.4162 | 121.3888 | 61.2273 | -121.6211 | 121.3253 | 121.4849 | 121.4835 | 61.2904 | -121.7711
1188.3438 | 121.8246 | -61.322 | 60.3424 | -0.010149 | -0.032376 | 0.00931 | 0.057718 | -0.0099418 | 0.05154 | -0.021518 | -0.0022666 | -0.0029313 | 0.059542 | 0.033423 | 0.05132 | -61.2669 | 0.015142 | -61.2338 | 60.3174 | 60.2086 | 60.1858 | -61.2512 | -61.1934 | 0.078197 | -61.2874 | 60.1132 | 60.2819 | 60.2759 | -61.4012 | 0.070795 | -0.02496 | 0.055082 | 0.088266 | 0.017471 | -0.13377 | -0.15665 | -0.079229 | -0.22925 | 0.12861 | 0.034583 | 0.11381 | -0.060556 | -0.066511 | 121.6395 | 121.5307 | 121.5078 | 61.3372 | -121.5936 | 121.4352 | 121.6039 | 121.5979 | 61.4002 | -121.7437
1190.0938 | 121.8933 | -61.2946 | 60.347 | -0.010149 | -0.032376 | 0.0090964 | 0.057718 | -0.0097282 | 0.051326 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059542 | 0.033636 | 0.051106 | -61.2578 | 0.015142 | -61.2246 | 60.322 | 60.2086 | 60.1949 | -61.2466 | -61.1934 | 0.078197 | -61.2874 | 60.1269 | 60.2819 | 60.2759 | -61.4012 | 0.047909 | -0.02496 | 0.036774 | 0.069958 | 0.022049 | -0.13835 | -0.15207 | -0.10669 | -0.22009 | 0.10115 | 0.007118 | 0.11381 | -0.065134 | -0.071089 | 121.6166 | 121.5032 | 121.4895 | 61.3097 | -121.5936 | 121.4214 | 121.5764 | 121.5705 | 61.3728 | -121.7482
1191.7812 | 121.9757 | -61.1526 | 60.4202 | -0.010149 | -0.032376 | 0.0090964 | 0.057932 | -0.0099418 | 0.051753 | -0.021518 | -0.002053 | -0.0031451 | 0.059542 | 0.03385 | 0.051106 | -61.2532 | 0.015142 | -61.2154 | 60.322 | 60.2086 | 60.1903 | -61.2512 | -61.1888 | 0.073618 | -61.2874 | 60.1132 | 60.2819 | 60.2759 | -61.3921 | -0.098577 | -0.098202 | -0.10055 | -0.062793 | 0.035784 | -0.21159 | -0.22989 | -0.23944 | -0.30707 | -0.036182 | -0.13479 | 0.10465 | -0.13838 | -0.14433 | 121.4747 | 121.3613 | 121.343 | 61.1678 | -121.6715 | 121.2658 | 121.4345 | 121.4285 | 61.2263 | -121.8123
1193.5312 | 121.843 | -61.2122 | 60.4706 | -0.0025182 | -0.032162 | 0.0088826 | 0.057077 | -0.0097282 | 0.052181 | -0.029148 | -0.002053 | -0.0031451 | 0.059755 | 0.033209 | 0.05132 | -61.2578 | 0.010564 | -61.2246 | 60.3266 | 60.2086 | 60.1903 | -61.2466 | -61.1888 | 0.073618 | -61.2829 | 60.1269 | 60.2864 | 60.2896 | -61.3967 | -0.034489 | -0.14398 | -0.045624 | -0.01244 | 0.022049 | -0.26194 | -0.28024 | -0.18451 | -0.34369 | 0.023327 | -0.070701 | 0.11381 | -0.18415 | -0.18095 | 121.5388 | 121.4208 | 121.4025 | 61.2227 | -121.7172 | 121.3391 | 121.4986 | 121.5018 | 61.2858 | -121.8673
1195.2188 | 121.8704 | -61.1938 | 60.4614 | -0.010149 | -0.032376 | 0.00931 | 0.057291 | -0.0099418 | 0.051753 | 0.0013733 | -0.002053 | -0.0029313 | 0.059755 | 0.034064 | 0.05132 | -61.2532 | 0.015142 | -61.22 | 60.322 | 60.2086 | 60.1949 | -61.2421 | -61.1797 | 0.082776 | -61.2783 | 60.1223 | 60.2956 | 60.2851 | -61.3875 | -0.04822 | -0.1394 | -0.059356 | -0.026172 | 0.022048 | -0.25279 | -0.26651 | -0.19366 | -0.33911 | 0.014175 | -0.084433 | 0.10923 | -0.16584 | -0.17637 | 121.5159 | 121.4025 | 121.3888 | 61.209 | -121.7035 | 121.3162 | 121.4894 | 121.4789 | 61.2766 | -121.8489
1196.9688 | 121.9208 | -61.203 | 60.3973 | -0.01778 | -0.032376 | 0.00931 | 0.057718 | -0.0097282 | 0.051753 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.033423 | 0.051747 | -61.2486 | 0.019721 | -61.2154 | 60.3174 | 60.2132 | 60.1949 | -61.2421 | -61.1797 | 0.073618 | -61.2829 | 60.1406 | 60.291 | 60.2896 | -61.3921 | -0.039065 | -0.079892 | -0.045622 | -0.012439 | 0.026626 | -0.18412 | -0.20242 | -0.18909 | -0.25671 | 0.02333 | -0.079856 | 0.10923 | -0.10633 | -0.10771 | 121.5205 | 121.4162 | 121.3979 | 61.2227 | -121.6394 | 121.3436 | 121.494 | 121.4926 | 61.2766 | -121.7894
1198.6562 | 121.8567 | -61.2717 | 60.3561 | -0.0025182 | -0.032162 | 0.0090964 | 0.057504 | -0.010155 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.033423 | 0.051747 | -61.2486 | 0.019721 | -61.2109 | 60.3266 | 60.2224 | 60.1995 | -61.2421 | -61.1797 | 0.078197 | -61.2737 | 60.1406 | 60.3002 | 60.2851 | -61.3829 | 0.029599 | -0.029536 | 0.023042 | 0.060803 | 0.031204 | -0.13377 | -0.15665 | -0.11127 | -0.21551 | 0.091994 | -0.002035 | 0.10923 | -0.055974 | -0.071087 | 121.5983 | 121.494 | 121.4712 | 61.2914 | -121.5982 | 121.4123 | 121.5718 | 121.5567 | 61.3499 | -121.7391
1200.4062 | 121.8979 | -61.2579 | 60.3607 | -0.010149 | -0.032162 | 0.0090964 | 0.057504 | -0.010155 | 0.05154 | -0.013887 | -0.0024804 | -0.0033587 | 0.059755 | 0.03385 | 0.05132 | -61.2395 | 0.019721 | -61.2154 | 60.3312 | 60.227 | 60.2041 | -61.2421 | -61.1843 | 0.082776 | -61.2737 | 60.1361 | 60.3002 | 60.2942 | -61.3829 | 0.015867 | -0.029536 | 0.018467 | 0.042493 | 0.026626 | -0.13376 | -0.15664 | -0.125 | -0.22467 | 0.073683 | -0.015767 | 0.10923 | -0.060552 | -0.066508 | 121.5891 | 121.4849 | 121.462 | 61.2777 | -121.6028 | 121.394 | 121.5581 | 121.5521 | 61.3407 | -121.7437
1202.1562 | 121.907 | -61.2991 | 60.3378 | -0.025411 | -0.032376 | 0.00931 | 0.057718 | -0.0099418 | 0.05154 | -0.021518 | -0.0024804 | -0.0029313 | 0.059542 | 0.033636 | 0.05132 | -61.244 | 0.015142 | -61.22 | 60.3312 | 60.2224 | 60.2087 | -61.2329 | -61.1751 | 0.087354 | -61.2737 | 60.1361 | 60.3002 | 60.2942 | -61.3784 | 0.066223 | -0.006648 | 0.055086 | 0.079113 | 0.01289 | -0.11545 | -0.12918 | -0.079223 | -0.20178 | 0.12404 | 0.025431 | 0.10465 | -0.037664 | -0.04362 | 121.6303 | 121.5215 | 121.5078 | 61.3143 | -121.5707 | 121.4352 | 121.5993 | 121.5933 | 61.3865 | -121.7162
1203.9062 | 121.9254 | -61.1755 | 60.4065 | -0.010149 | -0.032162 | 0.0090964 | 0.057504 | -0.0097282 | 0.051753 | -0.021518 | -0.0022666 | -0.0029313 | 0.059114 | 0.033636 | 0.051533 | -61.244 | 0.015142 | -61.2063 | 60.3312 | 60.2315 | 60.1995 | -61.2329 | -61.1751 | 0.073618 | -61.2783 | 60.1361 | 60.3002 | 60.2851 | -61.3738 | -0.057373 | -0.075312 | -0.06851 | -0.030748 | 0.026625 | -0.17496 | -0.207 | -0.19824 | -0.27044 | 0.000442 | -0.10274 | 0.095496 | -0.10633 | -0.12144 | 121.5067 | 121.4071 | 121.375 | 61.1907 | -121.6394 | 121.3116 | 121.4757 | 121.4606 | 61.2492 | -121.7803
1205.6562 | 121.843 | -61.1893 | 60.4614 | -0.0025182 | -0.03259 | 0.0090964 | 0.057504 | -0.010155 | 0.05154 | -0.0062567 | -0.0022666 | -0.0033587 | 0.059542 | 0.033636 | 0.051106 | -61.244 | 0.010564 | -61.2017 | 60.322 | 60.2224 | 60.2132 | -61.2329 | -61.1797 | 0.073618 | -61.26 | 60.1406 | 60.3002 | 60.2942 | -61.3692 | -0.04364 | -0.1394 | -0.054777 | -0.012437 | 0.031203 | -0.23905 | -0.2482 | -0.17993 | -0.3208 | 0.009597 | -0.070696 | 0.10923 | -0.16126 | -0.16722 | 121.5113 | 121.4116 | 121.4025 | 61.1998 | -121.6943 | 121.3299 | 121.4894 | 121.4835 | 61.2629 | -121.8306
1207.3906 | 121.8475 | -61.29 | 60.3882 | -0.0025182 | -0.03259 | 0.0088826 | 0.057718 | -0.0097282 | 0.051967 | -0.029148 | -0.0022666 | -0.0031451 | 0.059755 | 0.033636 | 0.051533 | -61.2395 | 0.010564 | -61.2109 | 60.3358 | 60.2224 | 60.2041 | -61.2375 | -61.1751 | 0.078197 | -61.2691 | 60.1406 | 60.3002 | 60.2942 | -61.3738 | 0.052489 | -0.052423 | 0.05051 | 0.079114 | 0.026625 | -0.16581 | -0.18411 | -0.083799 | -0.24756 | 0.11488 | 0.020855 | 0.10465 | -0.088018 | -0.093974 | 121.6257 | 121.5124 | 121.4941 | 61.3005 | -121.6257 | 121.4306 | 121.5901 | 121.5842 | 61.3682 | -121.762
1209.0938 | 121.9849 | -61.1481 | 60.4477 | -0.0025182 | -0.032376 | 0.0090964 | 0.057291 | -0.0099418 | 0.051326 | -0.021518 | -0.0024804 | -0.0029313 | 0.059542 | 0.033636 | 0.051106 | -61.244 | 0.015142 | -61.2017 | 60.3312 | 60.2224 | 60.2041 | -61.2283 | -61.1751 | 0.078197 | -61.2645 | 60.1361 | 60.3047 | 60.2896 | -61.3784 | -0.08026 | -0.11651 | -0.095976 | -0.053636 | 0.026624 | -0.22532 | -0.24362 | -0.23028 | -0.31164 | -0.027024 | -0.11647 | 0.11381 | -0.14295 | -0.15806 | 121.4793 | 121.3704 | 121.3521 | 61.1632 | -121.676 | 121.2841 | 121.4528 | 121.4377 | 61.2263 | -121.826
1210.8438 | 121.9299 | -61.2762 | 60.3424 | -0.0025182 | -0.033017 | 0.0088826 | 0.057718 | -0.010155 | 0.051753 | -0.013887 | -0.0024804 | -0.0031451 | 0.059542 | 0.033636 | 0.05132 | -61.2395 | 0.0243 | -61.2017 | 60.3358 | 60.2361 | 60.2087 | -61.2329 | -61.1659 | 0.082776 | -61.26 | 60.1406 | 60.3139 | 60.2988 | -61.3829 | 0.043335 | -0.006646 | 0.036777 | 0.074538 | 0.031203 | -0.1063 | -0.13376 | -0.10669 | -0.20178 | 0.11031 | 0.016279 | 0.12297 | -0.028505 | -0.043618 | 121.612 | 121.5124 | 121.4849 | 61.3005 | -121.5753 | 121.4169 | 121.5901 | 121.575 | 61.359 | -121.7253
1212.5938 | 121.9986 | -61.1572 | 60.4294 | -0.010149 | -0.03259 | 0.0090964 | 0.057932 | -0.0099418 | 0.051753 | -0.013887 | -0.002053 | -0.0027177 | 0.059755 | 0.034064 | 0.051533 | -61.2349 | 0.015142 | -61.2063 | 60.3358 | 60.2315 | 60.2132 | -61.2329 | -61.1797 | 0.078197 | -61.2645 | 60.1315 | 60.3047 | 60.2896 | -61.3784 | -0.075683 | -0.093621 | -0.077663 | -0.049058 | 0.026625 | -0.19785 | -0.21615 | -0.22113 | -0.29791 | -0.022446 | -0.10732 | 0.11381 | -0.12464 | -0.13975 | 121.493 | 121.3888 | 121.3705 | 61.1724 | -121.6623 | 121.2887 | 121.462 | 121.4469 | 61.2354 | -121.8077
1214.3438 | 121.9482 | -61.2259 | 60.3653 | -0.010149 | -0.03259 | 0.0090964 | 0.057932 | -0.0097282 | 0.05154 | -0.021518 | -0.0024804 | -0.0029313 | 0.059542 | 0.033636 | 0.051533 | -61.244 | 0.015142 | -61.2017 | 60.3358 | 60.2315 | 60.2041 | -61.2329 | -61.1751 | 0.087354 | -61.2783 | 60.1361 | 60.3047 | 60.2942 | -61.3784 | -0.007019 | -0.029534 | -0.018156 | 0.024184 | 0.031203 | -0.13376 | -0.16122 | -0.15246 | -0.22924 | 0.050796 | -0.05239 | 0.10007 | -0.060551 | -0.071085 | 121.5617 | 121.4574 | 121.43 | 61.241 | -121.5982 | 121.3619 | 121.5306 | 121.5201 | 61.3132 | -121.7437
1216.0312 | 121.9757 | -61.2488 | 60.347 | -0.0025182 | -0.03259 | 0.00931 | 0.057718 | -0.0097282 | 0.051326 | -0.021518 | -0.0024804 | -0.0031451 | 0.059755 | 0.033636 | 0.051533 | -61.244 | 0.019721 | -61.2109 | 60.3358 | 60.2315 | 60.2087 | -61.2283 | -61.1659 | 0.087354 | -61.2645 | 60.1361 | 60.3139 | 60.2896 | -61.3784 | 0.020448 | -0.011224 | 0.004732 | 0.037915 | 0.017467 | -0.11545 | -0.13833 | -0.12958 | -0.21093 | 0.082842 | -0.015765 | 0.11381 | -0.033083 | -0.057354 | 121.5845 | 121.4803 | 121.4574 | 61.2685 | -121.5753 | 121.3848 | 121.5627 | 121.5384 | 61.3361 | -121.7253
1217.7812 | 121.875 | -61.1572 | 60.4935 | -0.0025182 | -0.03259 | 0.0095236 | 0.057504 | -0.0099418 | 0.051112 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059328 | 0.033423 | 0.051106 | -61.2349 | 0.010564 | -61.2154 | 60.3266 | 60.227 | 60.2132 | -61.2329 | -61.1705 | 0.078197 | -61.2645 | 60.1361 | 60.2956 | 60.2942 | -61.3738 | -0.075683 | -0.16686 | -0.077663 | -0.058215 | 0.017468 | -0.26652 | -0.28024 | -0.21655 | -0.35742 | -0.013289 | -0.10732 | 0.10923 | -0.19788 | -0.19926 | 121.4838 | 121.3842 | 121.3705 | 61.1678 | -121.7264 | 121.2933 | 121.4528 | 121.4514 | 61.2354 | -121.8672
1219.4844 | 121.9757 | -61.1343 | 60.4202 | -0.010149 | -0.032376 | 0.0088826 | 0.057504 | -0.0099418 | 0.051112 | -0.021518 | -0.0022666 | -0.0029313 | 0.059542 | 0.034064 | 0.05132 | -61.2395 | 0.015142 | -61.2063 | 60.3358 | 60.227 | 60.2087 | -61.2283 | -61.1751 | 0.078197 | -61.2783 | 60.1452 | 60.3002 | 60.2988 | -61.3829 | -0.093993 | -0.084466 | -0.10513 | -0.071947 | 0.022046 | -0.19327 | -0.21157 | -0.2486 | -0.27502 | -0.040757 | -0.14394 | 0.10465 | -0.12006 | -0.12144 | 121.4701 | 121.3613 | 121.343 | 61.1495 | -121.6486 | 121.2795 | 121.4345 | 121.4331 | 61.2125 | -121.8032
1221.2344 | 121.8613 | -61.2122 | 60.4568 | -0.010149 | -0.03259 | 0.0090964 | 0.057504 | -0.0099418 | 0.051326 | -0.021518 | -0.0022666 | -0.0029313 | 0.059755 | 0.033636 | 0.051747 | -61.2395 | 0.015142 | -61.2109 | 60.3312 | 60.2224 | 60.1949 | -61.2329 | -61.1751 | 0.078197 | -61.2737 | 60.1315 | 60.2956 | 60.2896 | -61.3875 | -0.020752 | -0.12567 | -0.02731 | 0.001294 | 0.022046 | -0.23447 | -0.26193 | -0.17535 | -0.32538 | 0.037063 | -0.061544 | 0.11381 | -0.16126 | -0.16722 | 121.5433 | 121.4345 | 121.4071 | 61.2273 | -121.6898 | 121.3436 | 121.5077 | 121.5018 | 61.2904 | -121.8444
1222.9844 | 121.9482 | -61.2625 | 60.3516 | -0.010149 | -0.03259 | 0.0090964 | 0.057291 | -0.0099418 | 0.05154 | -0.021518 | -0.002053 | -0.0033587 | 0.059755 | 0.033636 | 0.05132 | -61.244 | 0.019721 | -61.2109 | 60.3358 | 60.227 | 60.2041 | -61.2329 | -61.1797 | 0.091933 | -61.2691 | 60.1406 | 60.3139 | 60.2851 | -61.3875 | 0.029602 | -0.015801 | 0.018465 | 0.051648 | 0.022046 | -0.12461 | -0.14749 | -0.125 | -0.21093 | 0.082839 | -0.006611 | 0.11839 | -0.03766 | -0.066509 | 121.5983 | 121.4895 | 121.4666 | 61.2822 | -121.5845 | 121.4031 | 121.5764 | 121.5476 | 61.3544 | -121.7391
1224.7344 | 121.8475 | -61.1893 | 60.466 | -0.0025182 | -0.03259 | 0.0090964 | 0.057291 | -0.0097282 | 0.05154 | -0.0062567 | -0.0016258 | -0.0031451 | 0.059755 | 0.03385 | 0.051747 | -61.2395 | 0.005985 | -61.2109 | 60.3266 | 60.2224 | 60.2132 | -61.2466 | -61.1751 | 0.082776 | -61.2691 | 60.1269 | 60.3002 | 60.2942 | -61.3875 | -0.057377 | -0.1394 | -0.050198 | -0.021594 | 0.035783 | -0.24363 | -0.25277 | -0.19824 | -0.33911 | 0.014175 | -0.079853 | 0.11839 | -0.16584 | -0.17179 | 121.5159 | 121.4116 | 121.4025 | 61.1953 | -121.7126 | 121.3162 | 121.4894 | 121.4835 | 61.272 | -121.8535
1226.5 | 121.8384 | -61.2122 | 60.4523 | -0.0025182 | -0.033017 | 0.00931 | 0.057718 | -0.0099418 | 0.051326 | -0.021518 | -0.0022666 | -0.0027177 | 0.059755 | 0.03385 | 0.051533 | -61.244 | 0.005985 | -61.2109 | 60.3312 | 60.227 | 60.2041 | -61.2375 | -61.1797 | 0.087354 | -61.2783 | 60.1315 | 60.2956 | 60.2851 | -61.3921 | -0.025331 | -0.12109 | -0.031889 | 0.001294 | 0.026625 | -0.22532 | -0.2482 | -0.17993 | -0.3208 | 0.032485 | -0.066123 | 0.11381 | -0.15668 | -0.16722 | 121.5433 | 121.4391 | 121.4162 | 61.2181 | -121.6898 | 121.3436 | 121.5077 | 121.4972 | 61.2995 | -121.8444
1228.1875 | 121.9482 | -61.1481 | 60.4752 | -0.01778 | -0.03259 | 0.0090964 | 0.057291 | -0.0099418 | 0.05154 | -0.0062567 | -0.002053 | -0.0031451 | 0.059542 | 0.033423 | 0.051533 | -61.244 | 0.010564 | -61.22 | 60.3312 | 60.2224 | 60.1995 | -61.2329 | -61.1751 | 0.078197 | -61.2737 | 60.1269 | 60.291 | 60.2851 | -61.3875 | -0.084839 | -0.14398 | -0.095976 | -0.071949 | 0.01289 | -0.25278 | -0.27566 | -0.23944 | -0.34826 | -0.027024 | -0.12563 | 0.11381 | -0.18415 | -0.19011 | 121.4793 | 121.3704 | 121.3476 | 61.1586 | -121.7081 | 121.275 | 121.4391 | 121.4331 | 61.2263 | -121.8627
1229.9375 | 121.9345 | -61.2076 | 60.3882 | -0.010149 | -0.032803 | 0.00931 | 0.057718 | -0.0095144 | 0.051112 | -0.021518 | -0.0022666 | -0.0029313 | 0.059328 | 0.034064 | 0.05132 | -61.244 | 0.010564 | -61.2109 | 60.322 | 60.227 | 60.1995 | -61.2421 | -61.1751 | 0.087354 | -61.2783 | 60.1315 | 60.3002 | 60.2851 | -61.3921 | -0.034487 | -0.066159 | -0.036466 | -0.003283 | 0.031204 | -0.16123 | -0.18869 | -0.18451 | -0.25671 | 0.032486 | -0.0707 | 0.11381 | -0.088018 | -0.10313 | 121.5296 | 121.4345 | 121.4071 | 61.2181 | -121.6303 | 121.3391 | 121.5077 | 121.4926 | 61.2949 | -121.7803
1231.6719 | 121.9757 | -61.1481 | 60.4614 | 0.0051128 | -0.032803 | 0.00931 | 0.057504 | -0.0097282 | 0.051753 | -0.021518 | -0.0022666 | -0.0029313 | 0.059755 | 0.034064 | 0.051533 | -61.244 | 0.010564 | -61.22 | 60.3266 | 60.2224 | 60.2087 | -61.2421 | -61.1843 | 0.087354 | -61.2737 | 60.1315 | 60.2956 | 60.2805 | -61.3875 | -0.093997 | -0.13482 | -0.095976 | -0.071949 | 0.022048 | -0.23905 | -0.25277 | -0.23944 | -0.32995 | -0.036181 | -0.12563 | 0.11381 | -0.16584 | -0.18095 | 121.4747 | 121.3704 | 121.3567 | 61.1586 | -121.7035 | 121.2795 | 121.4437 | 121.4285 | 61.2354 | -121.8489
1233.3438 | 121.843 | -61.1893 | 60.4843 | -0.010149 | -0.032803 | 0.0090964 | 0.057718 | -0.0097282 | 0.051112 | -0.0062567 | -0.0024804 | -0.0029313 | 0.059755 | 0.033636 | 0.051533 | -61.2532 | 0.015142 | -61.2154 | 60.3266 | 60.2178 | 60.1995 | -61.2466 | -61.1934 | 0.082776 | -61.2829 | 60.1223 | 60.2956 | 60.2896 | -61.3921 | -0.057377 | -0.15771 | -0.063934 | -0.026172 | 0.031205 | -0.26652 | -0.28482 | -0.20282 | -0.362 | -0.00414 | -0.093589 | 0.10923 | -0.18873 | -0.19468 | 121.5159 | 121.4071 | 121.3888 | 61.2044 | -121.731 | 121.3116 | 121.4849 | 121.4789 | 61.272 | -121.8764
1235.0938 | 121.8567 | -61.2259 | 60.4614 | -0.0025182 | -0.032803 | 0.00931 | 0.057504 | -0.0097282 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059328 | 0.033636 | 0.051747 | -61.2532 | 0.005985 | -61.22 | 60.322 | 60.2132 | 60.1903 | -61.2421 | -61.1797 | 0.082776 | -61.2829 | 60.1269 | 60.2956 | 60.2805 | -61.3967 | -0.016177 | -0.1394 | -0.027313 | 0.005871 | 0.022048 | -0.24821 | -0.27109 | -0.17078 | -0.33453 | 0.046218 | -0.056968 | 0.11381 | -0.16584 | -0.18095 | 121.5479 | 121.4391 | 121.4162 | 61.2319 | -121.7035 | 121.3528 | 121.5215 | 121.5064 | 61.3087 | -121.8581
1236.7812 | 121.9025 | -61.2167 | 60.3653 | -0.0025182 | -0.033017 | 0.00931 | 0.057504 | -0.0097282 | 0.051112 | -0.029148 | -0.002694 | -0.0031451 | 0.059328 | 0.034064 | 0.05132 | -61.2486 | 0.010564 | -61.2154 | 60.322 | 60.2224 | 60.2041 | -61.2421 | -61.1888 | 0.091933 | -61.2829 | 60.1315 | 60.291 | 60.2805 | -61.3967 | -0.025332 | -0.04327 | -0.031889 | 0.001294 | 0.026626 | -0.14292 | -0.16122 | -0.17994 | -0.23382 | 0.027905 | -0.066123 | 0.11381 | -0.074286 | -0.084821 | 121.5388 | 121.4391 | 121.4208 | 61.2273 | -121.6074 | 121.3482 | 121.5077 | 121.4972 | 61.3087 | -121.762
1238.5469 | 121.8567 | -61.2991 | 60.3333 | -0.010149 | -0.033017 | 0.0090964 | 0.057504 | -0.0097282 | 0.051326 | -0.013887 | -0.002053 | -0.0029313 | 0.059328 | 0.034277 | 0.051533 | -61.244 | 0.015142 | -61.2109 | 60.322 | 60.2178 | 60.1949 | -61.2512 | -61.1843 | 0.087354 | -61.2783 | 60.1315 | 60.2956 | 60.2896 | -61.3967 | 0.047907 | -0.011227 | 0.055086 | 0.088269 | 0.040362 | -0.11546 | -0.13834 | -0.097538 | -0.20178 | 0.11488 | 0.020852 | 0.11839 | -0.037665 | -0.043621 | 121.6212 | 121.5169 | 121.494 | 61.3143 | -121.5845 | 121.4306 | 121.5947 | 121.5888 | 61.3865 | -121.7299
1240.2344 | 121.9482 | -61.2396 | 60.3561 | 0.0051128 | -0.032803 | 0.0095236 | 0.057504 | -0.0097282 | 0.051326 | -0.013887 | -0.0018394 | -0.0029313 | 0.059328 | 0.034064 | 0.051747 | -61.2486 | 0.015142 | -61.2246 | 60.322 | 60.2086 | 60.1995 | -61.2421 | -61.1888 | 0.091933 | -61.2874 | 60.1269 | 60.2864 | 60.2713 | -61.3967 | -0.002444 | -0.034115 | -0.009001 | 0.015026 | 0.01747 | -0.1475 | -0.15665 | -0.15705 | -0.22925 | 0.050793 | -0.047814 | 0.10923 | -0.06971 | -0.084823 | 121.5616 | 121.4483 | 121.4391 | 61.2548 | -121.5982 | 121.3665 | 121.5261 | 121.5109 | 61.3316 | -121.7528
1241.9844 | 121.9711 | -61.1618 | 60.4202 | -0.0025182 | -0.033017 | 0.0095236 | 0.057077 | -0.010155 | 0.051326 | -0.013887 | -0.0022666 | -0.0033587 | 0.059542 | 0.033636 | 0.051747 | -61.2578 | 0.005985 | -61.22 | 60.3174 | 60.2132 | 60.1949 | -61.2512 | -61.1843 | 0.078197 | -61.2874 | 60.1223 | 60.2864 | 60.2759 | -61.3967 | -0.089422 | -0.10278 | -0.095978 | -0.058216 | 0.031206 | -0.20701 | -0.22531 | -0.23487 | -0.29791 | -0.022448 | -0.12563 | 0.10923 | -0.1338 | -0.14433 | 121.4793 | 121.375 | 121.3567 | 61.1678 | -121.6715 | 121.2841 | 121.4482 | 121.4377 | 61.24 | -121.8169
1243.7344 | 121.8521 | -61.235 | 60.4797 | -0.010149 | -0.033444 | 0.00931 | 0.057291 | -0.0097282 | 0.05154 | -0.0062567 | -0.0022666 | -0.0027177 | 0.059755 | 0.034064 | 0.051533 | -61.2578 | 0.001407 | -61.2246 | 60.3129 | 60.2132 | 60.1949 | -61.2558 | -61.1888 | 0.082776 | -61.2874 | 60.1177 | 60.291 | 60.2759 | -61.4012 | -0.020759 | -0.16687 | -0.022736 | 0.010448 | 0.031207 | -0.26652 | -0.28482 | -0.1662 | -0.362 | 0.046215 | -0.052392 | 0.11381 | -0.18873 | -0.20384 | 121.5479 | 121.4483 | 121.43 | 61.2365 | -121.7355 | 121.3528 | 121.5261 | 121.5109 | 61.3178 | -121.881
1245.4219 | 121.8475 | -61.2808 | 60.3516 | 0.0051128 | -0.032803 | 0.0088826 | 0.057291 | -0.0099418 | 0.05154 | -0.013887 | -0.0024804 | -0.0031451 | 0.059755 | 0.034064 | 0.051747 | -61.2532 | 0.005985 | -61.22 | 60.3129 | 60.2178 | 60.1949 | -61.2512 | -61.1934 | 0.082776 | -61.2874 | 60.1223 | 60.2864 | 60.2805 | -61.3967 | 0.029597 | -0.038693 | 0.027619 | 0.060803 | 0.031206 | -0.13377 | -0.15665 | -0.11585 | -0.22925 | 0.087413 | -0.006615 | 0.10923 | -0.065132 | -0.071088 | 121.5937 | 121.4986 | 121.4757 | 61.2868 | -121.6028 | 121.4031 | 121.5673 | 121.5613 | 61.3636 | -121.7482
1247.1719 | 121.8384 | -61.3083 | 60.3653 | -0.01778 | -0.032803 | 0.0095236 | 0.057291 | -0.010155 | 0.051753 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.034064 | 0.051747 | -61.2624 | 0.005985 | -61.2292 | 60.322 | 60.2086 | 60.1949 | -61.2604 | -61.1888 | 0.087354 | -61.2874 | 60.1177 | 60.2819 | 60.2805 | -61.4012 | 0.047905 | -0.04327 | 0.045929 | 0.079112 | 0.031207 | -0.15666 | -0.17038 | -0.092961 | -0.24756 | 0.11946 | 0.020851 | 0.11381 | -0.083444 | -0.084821 | 121.6303 | 121.5169 | 121.5032 | 61.3143 | -121.6257 | 121.426 | 121.5901 | 121.5888 | 61.3956 | -121.7665
1248.9219 | 121.9345 | -61.235 | 60.3699 | -0.0025182 | -0.032803 | 0.0090964 | 0.057291 | -0.0099418 | 0.05154 | -0.013887 | -0.0024804 | -0.0027177 | 0.059755 | 0.034491 | 0.051533 | -61.2532 | 0.001407 | -61.2246 | 60.3129 | 60.2086 | 60.1858 | -61.2512 | -61.1888 | 0.087354 | -61.292 | 60.1177 | 60.2773 | 60.2713 | -61.4058 | -0.01618 | -0.057004 | -0.018158 | 0.010448 | 0.026628 | -0.16123 | -0.18411 | -0.17078 | -0.25214 | 0.046215 | -0.056971 | 0.11381 | -0.0926 | -0.098556 | 121.5479 | 121.4437 | 121.4208 | 61.2365 | -121.6211 | 121.3528 | 121.5123 | 121.5064 | 61.3224 | -121.7757
1250.6719 | 121.8155 | -61.3129 | 60.3561 | -0.010149 | -0.033017 | 0.0095236 | 0.057291 | -0.0099418 | 0.051753 | -0.021518 | -0.0024804 | -0.0031451 | 0.059542 | 0.033423 | 0.051533 | -61.2486 | 0.001407 | -61.2292 | 60.322 | 60.2086 | 60.1858 | -61.2604 | -61.1888 | 0.087354 | -61.292 | 60.1269 | 60.2819 | 60.2805 | -61.4104 | 0.052482 | -0.034115 | 0.064241 | 0.083689 | 0.031207 | -0.1475 | -0.17038 | -0.097542 | -0.22925 | 0.12403 | 0.020849 | 0.11839 | -0.074289 | -0.075666 | 121.6349 | 121.5215 | 121.4986 | 61.3143 | -121.6165 | 121.4398 | 121.5947 | 121.5933 | 61.4002 | -121.7665
1252.3594 | 121.8887 | -61.2625 | 60.3928 | -0.010149 | -0.033017 | 0.00931 | 0.057291 | -0.010369 | 0.05154 | -0.021518 | -0.0022666 | -0.0033587 | 0.059755 | 0.034491 | 0.051533 | -61.2578 | 0.001407 | -61.2246 | 60.3129 | 60.2086 | 60.1858 | -61.2558 | -61.2026 | 0.078197 | -61.2966 | 60.1132 | 60.2773 | 60.2713 | -61.415 | 0.006707 | -0.079892 | 0.00473 | 0.037914 | 0.031207 | -0.18412 | -0.207 | -0.15247 | -0.2796 | 0.059945 | -0.034083 | 0.11839 | -0.11549 | -0.12144 | 121.5754 | 121.4711 | 121.4483 | 61.2639 | -121.6486 | 121.3757 | 121.5398 | 121.5338 | 61.3407 | -121.8077
1254.1094 | 121.8887 | -61.1893 | 60.4477 | -0.01778 | -0.033017 | 0.0090964 | 0.057291 | -0.0097282 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.034064 | 0.051747 | -61.2624 | -0.003172 | -61.2292 | 60.3083 | 60.1995 | 60.1812 | -61.2604 | -61.1934 | 0.078197 | -61.292 | 60.1132 | 60.2819 | 60.2622 | -61.4012 | -0.071114 | -0.1394 | -0.07309 | -0.039907 | 0.031207 | -0.24821 | -0.26651 | -0.21198 | -0.33454 | -0.00414 | -0.10275 | 0.10923 | -0.16584 | -0.18553 | 121.4976 | 121.3888 | 121.3705 | 61.1861 | -121.7081 | 121.3024 | 121.4711 | 121.4514 | 61.2675 | -121.8489
1255.7969 | 121.8613 | -61.2213 | 60.4385 | -0.010149 | -0.033017 | 0.0090964 | 0.057504 | -0.010155 | 0.051326 | -0.029148 | -0.002053 | -0.0029313 | 0.059755 | 0.034277 | 0.051533 | -61.2624 | -0.003172 | -61.2292 | 60.3083 | 60.2086 | 60.1858 | -61.2604 | -61.1934 | 0.082776 | -61.2966 | 60.1177 | 60.2819 | 60.2759 | -61.4058 | -0.039071 | -0.13025 | -0.041047 | -0.007864 | 0.031207 | -0.2299 | -0.25278 | -0.18452 | -0.3208 | 0.027903 | -0.075282 | 0.10923 | -0.15669 | -0.16264 | 121.5296 | 121.43 | 121.4071 | 61.2181 | -121.6989 | 121.3391 | 121.5032 | 121.4972 | 61.3041 | -121.8444
1257.5469 | 121.9711 | -61.2579 | 60.2829 | -0.010149 | -0.033017 | 0.0088826 | 0.057504 | -0.010155 | 0.051326 | -0.021518 | -0.0022666 | -0.0031451 | 0.059328 | 0.034277 | 0.051533 | -61.2624 | -0.003172 | -61.2338 | 60.3083 | 60.1949 | 60.1903 | -61.2695 | -61.2026 | 0.078197 | -61.2966 | 60.1086 | 60.2727 | 60.2759 | -61.415 | -0.011607 | 0.025392 | -0.004425 | 0.02418 | 0.035787 | -0.087997 | -0.09256 | -0.15705 | -0.17432 | 0.055368 | -0.03866 | 0.11839 | -0.010204 | -0.007002 | 121.5662 | 121.4528 | 121.4483 | 61.2548 | -121.5524 | 121.3665 | 121.5306 | 121.5338 | 61.3361 | -121.6979
1259.2344 | 121.8796 | -61.2808 | 60.3607 | -0.010149 | -0.033017 | 0.0090964 | 0.057504 | -0.010155 | 0.051753 | -0.021518 | -0.0022666 | -0.0029313 | 0.059755 | 0.03385 | 0.051747 | -61.2669 | -0.003172 | -61.2383 | 60.3129 | 60.1995 | 60.1812 | -61.2558 | -61.2026 | 0.087354 | -61.3012 | 60.1132 | 60.2773 | 60.2713 | -61.4196 | 0.025018 | -0.047849 | 0.013884 | 0.04249 | 0.017472 | -0.16124 | -0.17954 | -0.13874 | -0.24756 | 0.078256 | -0.020351 | 0.11839 | -0.083445 | -0.089401 | 121.5937 | 121.4803 | 121.462 | 61.2777 | -121.6165 | 121.394 | 121.5581 | 121.5521 | 61.3682 | -121.7803
1260.9844 | 121.8933 | -61.2488 | 60.379 | -0.01778 | -0.033017 | 0.0090964 | 0.057504 | -0.0099418 | 0.051112 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059542 | 0.034277 | 0.051533 | -61.2669 | -0.012329 | -61.2338 | 60.3129 | 60.1995 | 60.1766 | -61.265 | -61.2026 | 0.087354 | -61.2966 | 60.104 | 60.2635 | 60.2622 | -61.415 | -0.016184 | -0.066159 | -0.01816 | 0.015024 | 0.031208 | -0.17955 | -0.20243 | -0.16621 | -0.27503 | 0.046212 | -0.047816 | 0.11839 | -0.11549 | -0.11687 | 121.5616 | 121.4483 | 121.4254 | 61.2364 | -121.644 | 121.3528 | 121.5123 | 121.5109 | 61.3361 | -121.794
1262.7344 | 121.9437 | -61.2534 | 60.3195 | -0.0025182 | -0.033231 | 0.0090964 | 0.057718 | -0.010155 | 0.05154 | -0.013887 | -0.002053 | -0.0031451 | 0.059114 | 0.034064 | 0.051533 | -61.2761 | -0.016908 | -61.2429 | 60.2946 | 60.1857 | 60.1766 | -61.2741 | -61.2163 | 0.091933 | -61.3058 | 60.0994 | 60.2544 | 60.253 | -61.4241 | -0.020764 | -0.024964 | -0.022739 | 0.010445 | 0.031209 | -0.13378 | -0.14292 | -0.17079 | -0.2201 | 0.037054 | -0.052396 | 0.11839 | -0.065139 | -0.066516 | 121.5479 | 121.4391 | 121.43 | 61.2364 | -121.5936 | 121.3528 | 121.5077 | 121.5064 | 61.3453 | -121.7437
1264.4219 | 121.8613 | -61.2579 | 60.4019 | 0.0051128 | -0.033444 | 0.00931 | 0.057291 | -0.010155 | 0.05154 | -0.0062567 | -0.0024804 | -0.0031451 | 0.059969 | 0.034277 | 0.051747 | -61.2761 | -0.030644 | -61.2566 | 60.29 | 60.1903 | 60.1674 | -61.2833 | -61.2209 | 0.087354 | -61.3195 | 60.0903 | 60.2498 | 60.2438 | -61.4287 | -0.025343 | -0.11194 | -0.018161 | 0.001289 | 0.026632 | -0.21159 | -0.23447 | -0.17079 | -0.31165 | 0.037053 | -0.061554 | 0.10923 | -0.15212 | -0.15807 | 121.5479 | 121.4483 | 121.4254 | 61.2273 | -121.6852 | 121.3482 | 121.5077 | 121.5018 | 61.3453 | -121.8306
1266.1875 | 121.9574 | -61.2076 | 60.3882 | -0.010149 | -0.033444 | 0.0090964 | 0.057291 | -0.0099418 | 0.051326 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.033636 | 0.051747 | -61.2761 | -0.044379 | -61.2475 | 60.2946 | 60.1812 | 60.1674 | -61.2741 | -61.2255 | 0.082776 | -61.3149 | 60.104 | 60.259 | 60.2484 | -61.4241 | -0.06654 | -0.093629 | -0.068515 | -0.039909 | 0.026631 | -0.20702 | -0.22074 | -0.21656 | -0.28418 | -0.01788 | -0.10733 | 0.10923 | -0.12923 | -0.13976 | 121.5021 | 121.3887 | 121.375 | 61.1632 | -121.6623 | 121.3116 | 121.4665 | 121.456 | 61.2904 | -121.8123
1267.9375 | 121.9574 | -61.1984 | 60.4019 | -0.010149 | -0.033231 | 0.00931 | 0.057291 | -0.0097282 | 0.05154 | -0.013887 | -0.0022666 | -0.0029313 | 0.059542 | 0.034277 | 0.05132 | -61.2853 | -0.058115 | -61.2566 | 60.2854 | 60.1812 | 60.1629 | -61.2879 | -61.2255 | 0.087354 | -61.3195 | 60.0903 | 60.2498 | 60.2484 | -61.4287 | -0.089432 | -0.11652 | -0.086827 | -0.058221 | 0.031211 | -0.22075 | -0.23905 | -0.2303 | -0.31165 | -0.027036 | -0.12106 | 0.10923 | -0.15212 | -0.15349 | 121.4838 | 121.3796 | 121.3613 | 61.1403 | -121.6898 | 121.2887 | 121.4482 | 121.4468 | 61.2858 | -121.8306
1269.6875 | 121.8567 | -61.2534 | 60.4477 | -0.010149 | -0.033017 | 0.0090964 | 0.057718 | -0.010155 | 0.051326 | -0.021518 | -0.0024804 | -0.0029313 | 0.059328 | 0.034277 | 0.051533 | -61.2807 | -0.062694 | -61.2566 | 60.2808 | 60.172 | 60.1583 | -61.2924 | -61.2392 | 0.087354 | -61.3241 | 60.0811 | 60.2406 | 60.2347 | -61.4379 | -0.039079 | -0.16687 | -0.027317 | -0.003289 | 0.03579 | -0.27569 | -0.28941 | -0.18452 | -0.36658 | 0.01416 | -0.070711 | 0.11381 | -0.20705 | -0.21301 | 121.5342 | 121.4254 | 121.4116 | 61.1907 | -121.7401 | 121.3345 | 121.494 | 121.488 | 61.3407 | -121.8856
1271.375 | 121.9025 | -61.2259 | 60.3516 | -0.01778 | -0.033017 | 0.0095236 | 0.057291 | -0.010155 | 0.05154 | -0.013887 | -0.002053 | -0.0033587 | 0.059328 | 0.034064 | 0.051533 | -61.2898 | -0.07643 | -61.2612 | 60.2808 | 60.172 | 60.1537 | -61.2879 | -61.23 | 0.082776 | -61.3241 | 60.0857 | 60.2452 | 60.2347 | -61.4425 | -0.061966 | -0.070742 | -0.06394 | -0.035334 | 0.026632 | -0.17956 | -0.19785 | -0.21657 | -0.26588 | -0.004148 | -0.098177 | 0.11839 | -0.10634 | -0.11687 | 121.5067 | 121.3979 | 121.3796 | 61.1495 | -121.6394 | 121.3116 | 121.4711 | 121.4606 | 61.3087 | -121.794
1273.125 | 121.9391 | -61.2488 | 60.3745 | 0.0051128 | -0.033017 | 0.0088826 | 0.057291 | -0.010155 | 0.05154 | -0.021518 | -0.0022666 | -0.0029313 | 0.059755 | 0.034064 | 0.05132 | -61.2898 | -0.099323 | -61.2612 | 60.2762 | 60.172 | 60.1491 | -61.3062 | -61.2392 | 0.087354 | -61.3286 | 60.0765 | 60.2361 | 60.2301 | -61.4425 | -0.057394 | -0.098209 | -0.041052 | -0.012446 | 0.044948 | -0.20244 | -0.22532 | -0.19368 | -0.29792 | 0.009582 | -0.079867 | 0.11381 | -0.13839 | -0.14434 | 121.525 | 121.4208 | 121.3979 | 61.1495 | -121.6806 | 121.3253 | 121.4848 | 121.4789 | 61.3361 | -121.8169
1274.875 | 121.9116 | -61.2213 | 60.3836 | -0.0025182 | -0.033231 | 0.00931 | 0.057504 | -0.0097282 | 0.05154 | -0.013887 | -0.0018394 | -0.0031451 | 0.059542 | 0.034277 | 0.051747 | -61.299 | -0.13137 | -61.2704 | 60.2717 | 60.1674 | 60.1491 | -61.297 | -61.2392 | 0.082776 | -61.3332 | 60.0765 | 60.2406 | 60.221 | -61.4516 | -0.075702 | -0.11194 | -0.077675 | -0.049068 | 0.026634 | -0.21618 | -0.23448 | -0.2303 | -0.30708 | -0.017884 | -0.11191 | 0.11839 | -0.14296 | -0.16265 | 121.493 | 121.3887 | 121.3704 | 61.0899 | -121.6806 | 121.2978 | 121.462 | 121.4423 | 61.3041 | -121.8352
1276.5625 | 121.962 | -61.2213 | 60.3836 | -0.010149 | -0.033444 | 0.0090964 | 0.057504 | -0.0099418 | 0.051326 | -0.021518 | -0.0024804 | -0.0029313 | 0.059755 | 0.03385 | 0.05132 | -61.299 | -0.14969 | -61.2704 | 60.2671 | 60.1583 | 60.1354 | -61.3108 | -61.2392 | 0.087354 | -61.3424 | 60.072 | 60.2315 | 60.221 | -61.4516 | -0.089439 | -0.11652 | -0.077675 | -0.049068 | 0.040371 | -0.22534 | -0.24821 | -0.2303 | -0.31165 | -0.017884 | -0.12107 | 0.10923 | -0.15212 | -0.16265 | 121.4884 | 121.3796 | 121.3567 | 61.0716 | -121.6944 | 121.2933 | 121.4528 | 121.4423 | 61.3087 | -121.8352
1278.2969 | 121.8979 | -61.29 | 60.3287 | -0.0025182 | -0.033231 | 0.0090964 | 0.057077 | -0.010155 | 0.05154 | -0.021518 | -0.002053 | -0.0031451 | 0.059542 | 0.034064 | 0.051747 | -61.3081 | -0.17716 | -61.2795 | 60.2625 | 60.1628 | 60.1446 | -61.3108 | -61.2438 | 0.087354 | -61.3378 | 60.0628 | 60.2269 | 60.2255 | -61.4654 | -0.020774 | -0.066168 | -0.018166 | 0.01044 | 0.031214 | -0.16582 | -0.18412 | -0.17538 | -0.26588 | 0.046203 | -0.047826 | 0.12755 | -0.10177 | -0.10314 | 121.5525 | 121.4528 | 121.4345 | 61.1128 | -121.6394 | 121.3528 | 121.5169 | 121.5155 | 61.3773 | -121.794
1280.0469 | 121.907 | -61.3174 | 60.3241 | -0.0025182 | -0.033231 | 0.0095236 | 0.057291 | -0.010155 | 0.051753 | -0.0062567 | -0.0016258 | -0.0029313 | 0.059328 | 0.034064 | 0.051533 | -61.299 | -0.20463 | -61.2795 | 60.2625 | 60.1583 | 60.14 | -61.3153 | -61.2529 | 0.087354 | -61.3424 | 60.0628 | 60.2178 | 60.221 | -61.4654 | 0.002113 | -0.061591 | 0.018456 | 0.037906 | 0.035793 | -0.16583 | -0.18412 | -0.14791 | -0.2613 | 0.064511 | -0.024938 | 0.12297 | -0.10635 | -0.10315 | 121.5799 | 121.4757 | 121.4574 | 61.1128 | -121.6394 | 121.3802 | 121.5352 | 121.5384 | 61.4048 | -121.7895
1281.7969 | 121.9803 | -61.2305 | 60.3333 | -0.0025182 | -0.033231 | 0.0095236 | 0.057718 | -0.010369 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.034491 | 0.051106 | -61.3081 | -0.23668 | -61.275 | 60.2579 | 60.1491 | 60.1354 | -61.3108 | -61.2484 | 0.082776 | -61.3607 | 60.0582 | 60.2223 | 60.221 | -61.4562 | -0.080283 | -0.075324 | -0.077675 | -0.044491 | 0.035792 | -0.18414 | -0.19786 | -0.22573 | -0.27504 | -0.017885 | -0.13023 | 0.095499 | -0.11092 | -0.1123 | 121.4884 | 121.3796 | 121.3659 | 60.9938 | -121.644 | 121.2887 | 121.4528 | 121.4514 | 61.3132 | -121.7894
1283.5625 | 121.8796 | -61.3678 | 60.2783 | -0.010149 | -0.033231 | 0.0095236 | 0.057718 | -0.0099418 | 0.051967 | -0.021518 | -0.0022666 | -0.0031451 | 0.059969 | 0.034491 | 0.051106 | -61.3127 | -0.27331 | -61.2841 | 60.2533 | 60.1537 | 60.1354 | -61.3245 | -61.2575 | 0.082776 | -61.3515 | 60.0491 | 60.2223 | 60.2118 | -61.4745 | 0.043309 | -0.02497 | 0.055075 | 0.083682 | 0.040373 | -0.12463 | -0.14292 | -0.10671 | -0.22926 | 0.11029 | 0.016258 | 0.12297 | -0.05599 | -0.066525 | 121.6211 | 121.5215 | 121.5032 | 61.0945 | -121.6028 | 121.4169 | 121.5901 | 121.5796 | 61.4506 | -121.7528
1285.25 | 121.9803 | -61.2946 | 60.2509 | -0.0025182 | -0.033017 | 0.00931 | 0.057504 | -0.0097282 | 0.05154 | -0.021518 | -0.0022666 | -0.0027177 | 0.059755 | 0.034064 | 0.051747 | -61.3127 | -0.32367 | -61.2795 | 60.2488 | 60.1445 | 60.1217 | -61.3245 | -61.2529 | 0.091933 | -61.3653 | 60.0491 | 60.2178 | 60.2072 | -61.4654 | -0.029933 | -0.002083 | -0.018167 | 0.015018 | 0.044951 | -0.10632 | -0.12919 | -0.1708 | -0.20179 | 0.041623 | -0.07072 | 0.10008 | -0.033103 | -0.043637 | 121.5433 | 121.4391 | 121.4162 | 60.9709 | -121.5753 | 121.3436 | 121.5123 | 121.5018 | 61.3865 | -121.7162
1287 | 121.8658 | -61.2946 | 60.3836 | 0.0051128 | -0.033231 | 0.0090964 | 0.057077 | -0.010369 | 0.051753 | -0.021518 | -0.0024804 | -0.0029313 | 0.059755 | 0.034277 | 0.051533 | -61.3173 | -0.3603 | -61.2933 | 60.2442 | 60.1354 | 60.1217 | -61.3291 | -61.2621 | 0.087354 | -61.3607 | 60.0491 | 60.2132 | 60.2118 | -61.4745 | -0.034512 | -0.13941 | -0.022745 | 0.001283 | 0.035795 | -0.24823 | -0.26195 | -0.17995 | -0.33455 | 0.032466 | -0.066141 | 0.11381 | -0.17043 | -0.17181 | 121.5387 | 121.4299 | 121.4162 | 60.9343 | -121.7127 | 121.3436 | 121.5077 | 121.5064 | 61.3819 | -121.8581
1288.6719 | 121.9254 | -61.29 | 60.3149 | -0.010149 | -0.033444 | 0.0088826 | 0.057504 | -0.010369 | 0.05154 | -0.021518 | -0.0022666 | -0.0029313 | 0.059114 | 0.034064 | 0.051533 | -61.3173 | -0.40609 | -61.2887 | 60.2396 | 60.1445 | 60.1217 | -61.3245 | -61.2575 | 0.087354 | -61.3653 | 60.0491 | 60.2086 | 60.1935 | -61.4745 | -0.034511 | -0.075326 | -0.027323 | 0.001284 | 0.035795 | -0.17041 | -0.19328 | -0.18453 | -0.26588 | 0.032466 | -0.075298 | 0.10923 | -0.10635 | -0.12146 | 121.5296 | 121.4345 | 121.4116 | 60.8839 | -121.6394 | 121.339 | 121.4986 | 121.4835 | 61.3773 | -121.7895
1290.4219 | 121.875 | -61.29 | 60.3653 | -0.01778 | -0.033231 | 0.00931 | 0.057291 | -0.010155 | 0.05154 | -0.013887 | -0.0022666 | -0.0033587 | 0.059542 | 0.034064 | 0.051747 | -61.3173 | -0.46561 | -61.2933 | 60.2396 | 60.1308 | 60.1262 | -61.3336 | -61.2667 | 0.087354 | -61.3607 | 60.0491 | 60.2132 | 60.1981 | -61.4837 | -0.043669 | -0.12568 | -0.027323 | -0.003295 | 0.040374 | -0.2345 | -0.23906 | -0.19369 | -0.31624 | 0.023309 | -0.070719 | 0.12297 | -0.15212 | -0.16724 | 121.5296 | 121.4208 | 121.4162 | 60.8244 | -121.6989 | 121.339 | 121.5032 | 121.488 | 61.3773 | -121.849
1292.1094 | 121.8887 | -61.2579 | 60.3607 | -0.0025182 | -0.033231 | 0.0095236 | 0.057504 | -0.0099418 | 0.051326 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.034064 | 0.051533 | -61.3219 | -0.52971 | -61.2933 | 60.2396 | 60.1308 | 60.1217 | -61.3291 | -61.2712 | 0.082776 | -61.3699 | 60.0536 | 60.204 | 60.1889 | -61.4791 | -0.071133 | -0.1211 | -0.063944 | -0.035338 | 0.035795 | -0.22992 | -0.23906 | -0.22115 | -0.30708 | -0.013313 | -0.11192 | 0.10923 | -0.1567 | -0.17182 | 121.4976 | 121.3887 | 121.3796 | 60.7282 | -121.6898 | 121.3116 | 121.462 | 121.4468 | 61.3407 | -121.8398
1293.8594 | 121.9803 | -61.2717 | 60.3195 | -0.010149 | -0.033444 | 0.0095236 | 0.057504 | -0.010369 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.034491 | 0.05132 | -61.3219 | -0.59381 | -61.2979 | 60.235 | 60.1262 | 60.1125 | -61.3428 | -61.2804 | 0.091933 | -61.3744 | 60.0445 | 60.1949 | 60.1843 | -61.4882 | -0.071137 | -0.084483 | -0.050212 | -0.026184 | 0.044953 | -0.1933 | -0.20702 | -0.21658 | -0.27504 | -0.008738 | -0.10277 | 0.11381 | -0.12466 | -0.1352 | 121.5067 | 121.3979 | 121.3842 | 60.6779 | -121.6623 | 121.3161 | 121.4665 | 121.456 | 61.3636 | -121.8078
1295.6094 | 121.9894 | -61.2213 | 60.3561 | -0.0025182 | -0.033872 | 0.00931 | 0.057718 | -0.010369 | 0.051326 | -0.021518 | -0.0024804 | -0.0029313 | 0.059542 | 0.034705 | 0.051533 | -61.3173 | -0.66249 | -61.2887 | 60.2305 | 60.1262 | 60.1125 | -61.3336 | -61.2712 | 0.082776 | -61.3744 | 60.0399 | 60.1949 | 60.1889 | -61.4837 | -0.11233 | -0.12568 | -0.095988 | -0.067381 | 0.044953 | -0.22992 | -0.24364 | -0.26236 | -0.31624 | -0.049935 | -0.15312 | 0.10924 | -0.16128 | -0.16724 | 121.4518 | 121.3475 | 121.3338 | 60.5588 | -121.6898 | 121.2612 | 121.4162 | 121.4102 | 61.3041 | -121.8398
1297.2812 | 121.8658 | -61.409 | 60.2463 | -0.010149 | -0.033658 | 0.0090964 | 0.057291 | -0.010155 | 0.051326 | -0.021518 | -0.0022666 | -0.0027177 | 0.059755 | 0.034277 | 0.051747 | -61.3219 | -0.73117 | -61.2933 | 60.2259 | 60.1216 | 60.1079 | -61.3428 | -61.2712 | 0.087354 | -61.3699 | 60.0399 | 60.1994 | 60.1889 | -61.4928 | 0.066193 | -0.020398 | 0.087118 | 0.11572 | 0.049531 | -0.12464 | -0.13835 | -0.083829 | -0.20637 | 0.13775 | 0.039142 | 0.12297 | -0.04684 | -0.057375 | 121.6349 | 121.5306 | 121.5169 | 60.6778 | -121.5891 | 121.4489 | 121.6084 | 121.5979 | 61.4964 | -121.7391
1299.0469 | 121.9574 | -61.3449 | 60.2051 | -0.010149 | -0.033231 | 0.0090964 | 0.057291 | -0.010369 | 0.05154 | -0.0062567 | -0.002053 | -0.0031451 | 0.059328 | 0.034705 | 0.051533 | -61.331 | -0.79527 | -61.307 | 60.2259 | 60.1171 | 60.1033 | -61.3474 | -61.285 | 0.091933 | -61.3744 | 60.0262 | 60.1949 | 60.1797 | -61.4974 | -0.002473 | 0.020801 | 0.013874 | 0.037902 | 0.040375 | -0.088019 | -0.10173 | -0.1525 | -0.17891 | 0.059926 | -0.029523 | 0.12297 | -0.01022 | -0.025333 | 121.5708 | 121.462 | 121.4483 | 60.5496 | -121.5525 | 121.3711 | 121.5398 | 121.5247 | 61.4368 | -121.7025
1300.8125 | 121.8292 | -61.3953 | 60.2966 | -0.010149 | -0.033872 | 0.0095236 | 0.057291 | -0.0099418 | 0.05154 | -0.0062567 | -0.0024804 | -0.0031451 | 0.059755 | 0.034491 | 0.051533 | -61.331 | -0.87769 | -61.307 | 60.2167 | 60.1171 | 60.0988 | -61.3565 | -61.285 | 0.087354 | -61.3836 | 60.0307 | 60.1903 | 60.1843 | -61.4928 | 0.038723 | -0.079908 | 0.064228 | 0.088256 | 0.049533 | -0.17957 | -0.19787 | -0.097562 | -0.26588 | 0.11028 | 0.011673 | 0.10923 | -0.10635 | -0.11231 | 121.612 | 121.5123 | 121.494 | 60.5176 | -121.6532 | 121.426 | 121.5855 | 121.5796 | 61.4826 | -121.7895
1302.5625 | 121.875 | -61.3541 | 60.2783 | -0.01778 | -0.033444 | 0.0090964 | 0.057291 | -0.0095144 | 0.051753 | -0.0062567 | -0.002053 | -0.0033587 | 0.059114 | 0.034491 | 0.05132 | -61.331 | -0.96468 | -61.307 | 60.2167 | 60.1125 | 60.0942 | -61.3565 | -61.2896 | 0.087354 | -61.3836 | 60.0216 | 60.1857 | 60.1797 | -61.4928 | -0.002476 | -0.061597 | 0.023029 | 0.047057 | 0.049533 | -0.16584 | -0.18413 | -0.13876 | -0.25673 | 0.064503 | -0.029526 | 0.10923 | -0.092619 | -0.098575 | 121.5708 | 121.4665 | 121.4483 | 60.3894 | -121.6349 | 121.3757 | 121.5398 | 121.5338 | 61.4414 | -121.7711
1304.25 | 121.9666 | -61.2625 | 60.3241 | -0.0025182 | -0.033444 | 0.0090964 | 0.057504 | -0.010155 | 0.051326 | -0.013887 | -0.002053 | -0.0029313 | 0.059542 | 0.034064 | 0.05132 | -61.3402 | -1.0517 | -61.307 | 60.2213 | 60.1125 | 60.0942 | -61.3565 | -61.2987 | 0.078197 | -61.3882 | 60.0216 | 60.1811 | 60.1706 | -61.5066 | -0.094029 | -0.1028 | -0.077681 | -0.044496 | 0.049533 | -0.21162 | -0.22991 | -0.24405 | -0.30251 | -0.036208 | -0.12566 | 0.11839 | -0.14297 | -0.15351 | 121.4838 | 121.375 | 121.3567 | 60.2108 | -121.6806 | 121.2841 | 121.4436 | 121.4331 | 61.3407 | -121.8307
1306 | 121.9254 | -61.3632 | 60.2325 | -0.010149 | -0.033444 | 0.00931 | 0.057291 | -0.010369 | 0.051753 | -0.013887 | -0.0024804 | -0.0029313 | 0.059328 | 0.034491 | 0.051533 | -61.3356 | -1.1432 | -61.3024 | 60.2121 | 60.1125 | 60.1033 | -61.3611 | -61.2896 | 0.087354 | -61.3973 | 60.0262 | 60.1903 | 60.1706 | -61.5066 | 0.0021 | -0.0204 | 0.027605 | 0.060791 | 0.058691 | -0.12006 | -0.1292 | -0.14334 | -0.20638 | 0.073658 | -0.034107 | 0.10924 | -0.042265 | -0.061956 | 121.5754 | 121.4757 | 121.4666 | 60.22 | -121.5937 | 121.3894 | 121.5535 | 121.5338 | 61.4506 | -121.7391
1307.75 | 121.9803 | -61.2717 | 60.3104 | -0.010149 | -0.033444 | 0.0095236 | 0.057291 | -0.010155 | 0.051753 | -0.021518 | -0.0018394 | -0.0029313 | 0.059328 | 0.034491 | 0.051533 | -61.3356 | -1.2348 | -61.307 | 60.2121 | 60.1079 | 60.0942 | -61.3565 | -61.2987 | 0.087354 | -61.3927 | 60.0216 | 60.1857 | 60.166 | -61.502 | -0.084874 | -0.09822 | -0.063948 | -0.035341 | 0.049533 | -0.20246 | -0.21618 | -0.23032 | -0.28878 | -0.027053 | -0.12108 | 0.10924 | -0.12466 | -0.14435 | 121.4838 | 121.3796 | 121.3659 | 60.0369 | -121.6669 | 121.2933 | 121.4574 | 121.4377 | 61.359 | -121.8123
1309.5 | 121.9482 | -61.3861 | 60.2097 | -0.0025182 | -0.033658 | 0.0090964 | 0.057504 | -0.0099418 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059328 | 0.034491 | 0.051533 | -61.331 | -1.3127 | -61.307 | 60.203 | 60.1079 | 60.0942 | -61.3611 | -61.2987 | 0.091933 | -61.3973 | 60.017 | 60.1765 | 60.1706 | -61.5157 | 0.024988 | -0.006669 | 0.055072 | 0.0791 | 0.054112 | -0.10176 | -0.11547 | -0.12961 | -0.19265 | 0.087388 | -0.011219 | 0.11839 | -0.033112 | -0.039068 | 121.5891 | 121.494 | 121.4803 | 60.0735 | -121.5708 | 121.4031 | 121.5627 | 121.5567 | 61.478 | -121.7254
1311.1875 | 121.9711 | -61.3678 | 60.2509 | -0.01778 | -0.033872 | 0.0088826 | 0.057077 | -0.0097282 | 0.05154 | -0.013887 | -0.0022666 | -0.0029313 | 0.059542 | 0.034491 | 0.05132 | -61.331 | -1.418 | -61.3162 | 60.2076 | 60.1033 | 60.085 | -61.3611 | -61.3033 | 0.087354 | -61.3973 | 60.0124 | 60.1765 | 60.166 | -61.5111 | 0.006678 | -0.043288 | 0.036762 | 0.051634 | 0.044956 | -0.14753 | -0.16582 | -0.14334 | -0.23842 | 0.064499 | -0.029529 | 0.11382 | -0.07431 | -0.084845 | 121.5754 | 121.4711 | 121.4528 | 59.9498 | -121.612 | 121.3802 | 121.5443 | 121.5338 | 61.4552 | -121.762
1312.9375 | 121.9254 | -61.2808 | 60.3378 | -0.010149 | -0.033658 | 0.00931 | 0.057077 | -0.0099418 | 0.051326 | -0.0062567 | -0.0022666 | -0.0029313 | 0.059328 | 0.034491 | 0.05132 | -61.3356 | -1.5233 | -61.2979 | 60.2121 | 60.1079 | 60.0942 | -61.3703 | -61.2941 | 0.082776 | -61.4065 | 60.017 | 60.1857 | 60.1752 | -61.5111 | -0.089455 | -0.12569 | -0.054792 | -0.017028 | 0.072427 | -0.22993 | -0.24364 | -0.23032 | -0.32082 | -0.013318 | -0.12566 | 0.10466 | -0.15213 | -0.16266 | 121.493 | 121.3887 | 121.375 | 59.7576 | -121.7081 | 121.2978 | 121.4665 | 121.456 | 61.3636 | -121.849
1314.625 | 121.907 | -61.3358 | 60.2829 | -0.0025182 | -0.033872 | 0.0090964 | 0.057077 | -0.0099418 | 0.05154 | -0.013887 | -0.0022666 | -0.0025041 | 0.059542 | 0.034064 | 0.051533 | -61.3265 | -1.6011 | -61.307 | 60.2167 | 60.1125 | 60.0942 | -61.3611 | -61.2987 | 0.096512 | -61.3882 | 60.017 | 60.1857 | 60.1706 | -61.5157 | -0.025366 | -0.066175 | 0.009296 | 0.028746 | 0.054112 | -0.17042 | -0.18871 | -0.17997 | -0.26589 | 0.037034 | -0.052416 | 0.12755 | -0.097197 | -0.11231 | 121.5525 | 121.4482 | 121.4299 | 59.7347 | -121.644 | 121.3528 | 121.5215 | 121.5063 | 61.4323 | -121.7986
1316.375 | 121.962 | -61.2854 | 60.3058 | -0.025411 | -0.033658 | 0.00931 | 0.057291 | -0.010155 | 0.051326 | -0.0062567 | -0.0024804 | -0.0027177 | 0.059542 | 0.034277 | 0.051106 | -61.331 | -1.6698 | -61.307 | 60.203 | 60.1033 | 60.0988 | -61.3703 | -61.3079 | 0.082776 | -61.3973 | 60.0124 | 60.1811 | 60.1706 | -61.5111 | -0.084878 | -0.1028 | -0.045636 | -0.021608 | 0.06327 | -0.20246 | -0.20702 | -0.22574 | -0.29335 | -0.022477 | -0.11193 | 0.11382 | -0.12466 | -0.1352 | 121.4884 | 121.3887 | 121.3842 | 59.6156 | -121.6761 | 121.2978 | 121.4665 | 121.456 | 61.3682 | -121.8169
1318.125 | 121.9666 | -61.3495 | 60.228 | -0.01778 | -0.033658 | 0.00931 | 0.057504 | -0.010155 | 0.051112 | -0.013887 | -0.0024804 | -0.0031451 | 0.059328 | 0.034491 | 0.051533 | -61.3219 | -1.7476 | -61.307 | 60.203 | 60.1033 | 60.0942 | -61.3657 | -61.3033 | 0.087354 | -61.4019 | 60.0124 | 60.1811 | 60.1752 | -61.5111 | -0.016212 | -0.024979 | 0.027608 | 0.042479 | 0.058691 | -0.12464 | -0.13378 | -0.16165 | -0.21553 | 0.046188 | -0.052419 | 0.10924 | -0.046844 | -0.0528 | 121.5525 | 121.4528 | 121.4437 | 59.6019 | -121.5937 | 121.3619 | 121.5306 | 121.5247 | 61.4368 | -121.7391
1319.8594 | 121.9803 | -61.2854 | 60.3012 | -0.010149 | -0.033872 | 0.0090964 | 0.057504 | -0.010155 | 0.05154 | -0.013887 | -0.0022666 | -0.0033587 | 0.059969 | 0.034277 | 0.051533 | -61.3265 | -1.8483 | -61.307 | 60.2076 | 60.1079 | 60.0896 | -61.3657 | -61.3033 | 0.087354 | -61.4019 | 60.017 | 60.1811 | 60.1706 | -61.5111 | -0.080299 | -0.093642 | -0.041058 | -0.021608 | 0.058691 | -0.19331 | -0.2116 | -0.22574 | -0.2842 | -0.017899 | -0.11651 | 0.10924 | -0.12009 | -0.13062 | 121.493 | 121.3933 | 121.375 | 59.4371 | -121.6669 | 121.3024 | 121.4665 | 121.456 | 61.3728 | -121.8124
1321.5469 | 121.8658 | -61.3083 | 60.3607 | -0.0025182 | -0.033872 | 0.0088826 | 0.057291 | -0.0099418 | 0.051753 | -0.013887 | -0.002053 | -0.0033587 | 0.059542 | 0.034918 | 0.05132 | -61.3219 | -1.9216 | -61.2933 | 60.2167 | 60.1033 | 60.0896 | -61.3611 | -61.2987 | 0.087354 | -61.3973 | 60.0124 | 60.1765 | 60.1706 | -61.5157 | -0.052831 | -0.14399 | -0.01359 | 0.015016 | 0.067847 | -0.25739 | -0.27111 | -0.20743 | -0.34829 | 0.009569 | -0.089038 | 0.11839 | -0.18417 | -0.19013 | 121.525 | 121.4116 | 121.3979 | 59.3867 | -121.7218 | 121.3207 | 121.4848 | 121.4789 | 61.3956 | -121.8764
1323.2969 | 122.0078 | -61.2762 | 60.3058 | -0.0025182 | -0.033658 | 0.00931 | 0.057077 | -0.010155 | 0.051326 | -0.0062567 | -0.0022666 | -0.0029313 | 0.059542 | 0.034277 | 0.05132 | -61.3127 | -1.9766 | -61.2933 | 60.2259 | 60.1171 | 60.0988 | -61.3657 | -61.285 | 0.091933 | -61.3927 | 60.017 | 60.1857 | 60.1752 | -61.5111 | -0.089454 | -0.079907 | -0.036478 | -0.017028 | 0.072426 | -0.18873 | -0.20702 | -0.2349 | -0.28878 | -0.008739 | -0.1165 | 0.11839 | -0.12008 | -0.13062 | 121.5021 | 121.3933 | 121.375 | 59.2997 | -121.6715 | 121.2933 | 121.4619 | 121.4514 | 61.3682 | -121.8169
1325.0312 | 121.8933 | -61.3586 | 60.2646 | -0.01778 | -0.033658 | 0.0090964 | 0.057504 | -0.010369 | 0.051326 | -0.013887 | -0.002053 | -0.0033587 | 0.059755 | 0.034705 | 0.051533 | -61.3081 | -2.0406 | -61.2795 | 60.2259 | 60.1171 | 60.1033 | -61.3657 | -61.2804 | 0.087354 | -61.3836 | 60.017 | 60.1949 | 60.1843 | -61.5066 | -0.007056 | -0.038708 | 0.050499 | 0.079105 | 0.086161 | -0.14753 | -0.16124 | -0.14792 | -0.24758 | 0.078238 | -0.024948 | 0.12297 | -0.069729 | -0.080263 | 121.5845 | 121.4757 | 121.462 | 59.318 | -121.6303 | 121.3757 | 121.5535 | 121.543 | 61.446 | -121.7712
1326.7812 | 121.9528 | -61.2946 | 60.3149 | -0.0025182 | -0.033872 | 0.00931 | 0.057077 | -0.0099418 | 0.05154 | -0.021518 | -0.0024804 | -0.0029313 | 0.059755 | 0.034491 | 0.051533 | -61.3036 | -2.091 | -61.2841 | 60.2121 | 60.1125 | 60.1033 | -61.352 | -61.285 | 0.087354 | -61.3927 | 60.0262 | 60.1857 | 60.1752 | -61.5111 | -0.057406 | -0.1028 | -0.00901 | 0.01044 | 0.067846 | -0.20246 | -0.2116 | -0.21659 | -0.28877 | 0.009572 | -0.098192 | 0.11839 | -0.12924 | -0.13978 | 121.5067 | 121.407 | 121.3979 | 59.2035 | -121.6669 | 121.3207 | 121.4803 | 121.4697 | 61.3819 | -121.8261
1328.5469 | 121.8842 | -61.3861 | 60.2921 | -0.01778 | -0.033872 | 0.0095236 | 0.057077 | -0.0099418 | 0.051112 | -0.013887 | -0.002053 | -0.0027177 | 0.059755 | 0.034705 | 0.05132 | -61.2944 | -2.1505 | -61.2841 | 60.2259 | 60.1216 | 60.1033 | -61.3565 | -61.2896 | 0.087354 | -61.3882 | 60.0262 | 60.1903 | 60.1752 | -61.5066 | 0.029567 | -0.066174 | 0.091699 | 0.10199 | 0.072425 | -0.17042 | -0.18871 | -0.12045 | -0.26589 | 0.096546 | -0.002062 | 0.11839 | -0.10177 | -0.11689 | 121.612 | 121.5077 | 121.4895 | 59.2356 | -121.6486 | 121.4123 | 121.5764 | 121.5613 | 61.4735 | -121.7986
1330.2344 | 121.9391 | -61.29 | 60.2783 | -0.0025182 | -0.033872 | 0.00931 | 0.057718 | -0.010155 | 0.051326 | -0.029148 | -0.0024804 | -0.0031451 | 0.059542 | 0.034277 | 0.051533 | -61.2853 | -2.1963 | -61.2795 | 60.2213 | 60.1262 | 60.1033 | -61.352 | -61.2941 | 0.087354 | -61.3927 | 60.0307 | 60.1949 | 60.1843 | -61.502 | -0.061984 | -0.057019 | 0.004726 | 0.01044 | 0.072424 | -0.1521 | -0.17498 | -0.21201 | -0.24757 | -0.004163 | -0.10277 | 0.10924 | -0.083462 | -0.093996 | 121.5113 | 121.4162 | 121.3933 | 59.0937 | -121.6303 | 121.3207 | 121.4848 | 121.4743 | 61.3773 | -121.7803
1331.9844 | 121.8338 | -61.3815 | 60.26 | -0.010149 | -0.033658 | 0.0090964 | 0.057291 | -0.0099418 | 0.051753 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.034491 | 0.051106 | -61.2898 | -2.2513 | -61.2704 | 60.2167 | 60.1262 | 60.1125 | -61.3565 | -61.2941 | 0.087354 | -61.3882 | 60.0307 | 60.1949 | 60.1889 | -61.502 | 0.02499 | -0.043287 | 0.0917 | 0.11115 | 0.08616 | -0.13379 | -0.14751 | -0.12045 | -0.22926 | 0.08739 | -0.006639 | 0.11381 | -0.065152 | -0.071108 | 121.5983 | 121.5077 | 121.494 | 59.1303 | -121.6166 | 121.4123 | 121.5764 | 121.5704 | 61.4689 | -121.762
1333.6719 | 121.875 | -61.3174 | 60.347 | -0.010149 | -0.033872 | 0.00931 | 0.057291 | -0.0099418 | 0.051753 | -0.013887 | -0.0022666 | -0.0029313 | 0.059542 | 0.034705 | 0.051533 | -61.2898 | -2.2696 | -61.275 | 60.2213 | 60.1171 | 60.1079 | -61.352 | -61.285 | 0.087354 | -61.3882 | 60.0262 | 60.1949 | 60.1843 | -61.5111 | -0.034518 | -0.12568 | 0.027613 | 0.042484 | 0.077002 | -0.22993 | -0.23906 | -0.1937 | -0.32082 | 0.03246 | -0.070726 | 0.12297 | -0.15213 | -0.16266 | 121.5387 | 121.4345 | 121.4254 | 59.0479 | -121.6989 | 121.3436 | 121.5123 | 121.5018 | 61.4048 | -121.8581
1335.4219 | 121.843 | -61.3129 | 60.3653 | -0.010149 | -0.033872 | 0.0095236 | 0.057291 | -0.010155 | 0.051326 | -0.021518 | -0.0024804 | -0.0029313 | 0.059542 | 0.034705 | 0.05132 | -61.2807 | -2.3062 | -61.275 | 60.2213 | 60.1171 | 60.1125 | -61.352 | -61.285 | 0.091933 | -61.3882 | 60.0262 | 60.1903 | 60.1797 | -61.4974 | -0.039096 | -0.14399 | 0.032192 | 0.037906 | 0.077002 | -0.24824 | -0.25279 | -0.18454 | -0.33913 | 0.027882 | -0.075304 | 0.10923 | -0.17502 | -0.18555 | 121.5342 | 121.4299 | 121.4254 | 59.0067 | -121.7173 | 121.339 | 121.5031 | 121.4926 | 61.4048 | -121.8627
1337.1875 | 121.9803 | -61.2305 | 60.3424 | -0.010149 | -0.034085 | 0.00931 | 0.057291 | -0.010155 | 0.05154 | -0.021518 | -0.0022666 | -0.0029313 | 0.059328 | 0.034705 | 0.051106 | -61.2853 | -2.3291 | -61.2795 | 60.2121 | 60.1079 | 60.1033 | -61.3611 | -61.285 | 0.078197 | -61.3927 | 60.0262 | 60.1857 | 60.1706 | -61.5066 | -0.13065 | -0.13026 | -0.054783 | -0.049069 | 0.081582 | -0.23451 | -0.23906 | -0.27609 | -0.31624 | -0.054515 | -0.16228 | 0.11382 | -0.15671 | -0.17182 | 121.4426 | 121.3384 | 121.3338 | 58.9014 | -121.7035 | 121.2566 | 121.4162 | 121.4011 | 61.3087 | -121.849
1338.9688 | 121.9803 | -61.3586 | 60.2417 | -0.010149 | -0.034085 | 0.00931 | 0.057504 | -0.010369 | 0.051326 | -0.013887 | -0.0022666 | -0.0029313 | 0.059328 | 0.034705 | 0.051106 | -61.2807 | -2.3749 | -61.275 | 60.2167 | 60.1171 | 60.0988 | -61.3657 | -61.3033 | 0.091933 | -61.3973 | 60.0262 | 60.1811 | 60.1797 | -61.5111 | -0.007056 | -0.024976 | 0.077969 | 0.083683 | 0.090739 | -0.12464 | -0.14293 | -0.1525 | -0.21553 | 0.055344 | -0.038684 | 0.11382 | -0.060577 | -0.061954 | 121.5754 | 121.4757 | 121.4574 | 58.9838 | -121.6074 | 121.3848 | 121.5398 | 121.5384 | 61.4506 | -121.7528
1340.7188 | 121.9025 | -61.3678 | 60.2646 | -0.0025182 | -0.034299 | 0.00931 | 0.057291 | -0.010155 | 0.05154 | -0.013887 | -0.0024804 | -0.0031451 | 0.059542 | 0.034491 | 0.05132 | -61.2807 | -2.4024 | -61.2795 | 60.2121 | 60.1125 | 60.0988 | -61.3703 | -61.2987 | 0.082776 | -61.4065 | 60.0124 | 60.172 | 60.1706 | -61.5203 | -0.00248 | -0.052443 | 0.087124 | 0.08826 | 0.09074 | -0.15211 | -0.16582 | -0.1525 | -0.25216 | 0.069078 | -0.038686 | 0.11382 | -0.092622 | -0.093999 | 121.5799 | 121.4803 | 121.4666 | 58.9654 | -121.6349 | 121.3802 | 121.5398 | 121.5384 | 61.4506 | -121.7849
1342.4062 | 121.8658 | -61.4044 | 60.2692 | -0.0025182 | -0.034085 | 0.0090964 | 0.057077 | -0.010155 | 0.05154 | -0.013887 | -0.0022666 | -0.0033587 | 0.059542 | 0.034705 | 0.05132 | -61.2853 | -2.4344 | -61.2841 | 60.2076 | 60.1033 | 60.0942 | -61.3703 | -61.3033 | 0.087354 | -61.4019 | 60.0124 | 60.172 | 60.166 | -61.5295 | 0.034141 | -0.061599 | 0.11917 | 0.1203 | 0.086162 | -0.16584 | -0.17498 | -0.12504 | -0.25673 | 0.10112 | 0.002513 | 0.12755 | -0.0972 | -0.10316 | 121.612 | 121.5077 | 121.4986 | 58.97 | -121.6394 | 121.4169 | 121.5764 | 121.5704 | 61.4918 | -121.7986
1344.1562 | 121.962 | -61.2946 | 60.3058 | -0.01778 | -0.033872 | 0.00931 | 0.057291 | -0.010155 | 0.05154 | -0.0062567 | -0.0024804 | -0.0029313 | 0.059542 | 0.034705 | 0.050679 | -61.2898 | -2.4527 | -61.2887 | 60.203 | 60.0942 | 60.0805 | -61.384 | -61.3125 | 0.082776 | -61.4065 | 59.9987 | 60.1674 | 60.1569 | -61.534 | -0.089459 | -0.1028 | 0.004725 | 0.005862 | 0.095321 | -0.21162 | -0.22533 | -0.23948 | -0.30709 | -0.0179 | -0.11193 | 0.12755 | -0.1384 | -0.14893 | 121.4975 | 121.3887 | 121.375 | 58.8418 | -121.6898 | 121.2933 | 121.4619 | 121.4514 | 61.3773 | -121.8398
1345.9062 | 121.8521 | -61.4227 | 60.2646 | 0.0051128 | -0.034085 | 0.00931 | 0.057291 | -0.0099418 | 0.051753 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059542 | 0.034491 | 0.051106 | -61.2898 | -2.4894 | -61.2933 | 60.1938 | 60.085 | 60.0759 | -61.384 | -61.3216 | 0.087354 | -61.4111 | 59.9941 | 60.1628 | 60.1569 | -61.534 | 0.038714 | -0.070756 | 0.1329 | 0.12946 | 0.090742 | -0.17958 | -0.18871 | -0.11131 | -0.27047 | 0.10112 | 0.011666 | 0.12297 | -0.10178 | -0.10773 | 121.6166 | 121.5077 | 121.4986 | 58.9334 | -121.6486 | 121.4168 | 121.5855 | 121.5796 | 61.5101 | -121.7986
1347.6562 | 121.8292 | -61.4456 | 60.2188 | -0.010149 | -0.034085 | 0.0090964 | 0.057291 | -0.0099418 | 0.051326 | -0.021518 | -0.0018394 | -0.0033587 | 0.059755 | 0.034277 | 0.05132 | -61.299 | -2.4985 | -61.2887 | 60.1893 | 60.085 | 60.0713 | -61.3932 | -61.3216 | 0.087354 | -61.4294 | 59.9804 | 60.1537 | 60.1431 | -61.5432 | 0.052445 | -0.029559 | 0.14663 | 0.15692 | 0.10448 | -0.1338 | -0.14752 | -0.097575 | -0.23843 | 0.12401 | 0.01624 | 0.11382 | -0.06516 | -0.075695 | 121.6349 | 121.5306 | 121.5169 | 58.9471 | -121.612 | 121.426 | 121.5993 | 121.5887 | 61.533 | -121.762
1349.3438 | 121.9803 | -61.2991 | 60.3012 | -0.0025182 | -0.033872 | 0.0090964 | 0.057291 | -0.0097282 | 0.051326 | -0.013887 | -0.0024804 | -0.0029313 | 0.059328 | 0.034918 | 0.050892 | -61.2853 | -2.5489 | -61.2933 | 60.1801 | 60.0942 | 60.0667 | -61.3886 | -61.3308 | 0.087354 | -61.4294 | 59.9895 | 60.1537 | 60.1477 | -61.5386 | -0.089461 | -0.12111 | 0.013881 | 0.00586 | 0.095321 | -0.20704 | -0.23449 | -0.23948 | -0.31167 | -0.031638 | -0.13025 | 0.10924 | -0.14756 | -0.15351 | 121.4792 | 121.3933 | 121.3658 | 58.7503 | -121.6898 | 121.2887 | 121.4528 | 121.4468 | 61.3865 | -121.8398
1351.1094 | 121.9391 | -61.3586 | 60.2463 | -0.025411 | -0.033872 | 0.00931 | 0.057504 | -0.0099418 | 0.051112 | -0.013887 | -0.0018394 | -0.0029313 | 0.059542 | 0.034705 | 0.051106 | -61.2853 | -2.5718 | -61.3024 | 60.1801 | 60.0758 | 60.0621 | -61.4069 | -61.3353 | 0.091933 | -61.4294 | 59.985 | 60.1582 | 60.1385 | -61.5524 | -0.048266 | -0.066182 | 0.073391 | 0.056214 | 0.10448 | -0.17043 | -0.18414 | -0.19371 | -0.26132 | 0.023293 | -0.070735 | 0.12297 | -0.088048 | -0.10774 | 121.5387 | 121.4345 | 121.4208 | 58.7869 | -121.6532 | 121.3436 | 121.5169 | 121.4972 | 61.4506 | -121.7986
1352.8594 | 121.9666 | -61.3953 | 60.1501 | -0.01778 | -0.034085 | 0.0090964 | 0.057077 | -0.010155 | 0.051326 | -0.029148 | -0.002053 | -0.0031451 | 0.059542 | 0.034491 | 0.051106 | -61.299 | -2.6313 | -61.307 | 60.1709 | 60.0621 | 60.0576 | -61.4069 | -61.3399 | 0.082776 | -61.434 | 59.9758 | 60.1445 | 60.1294 | -61.5615 | -0.011645 | 0.020793 | 0.096276 | 0.088256 | 0.099901 | -0.088034 | -0.092587 | -0.16625 | -0.17434 | 0.055336 | -0.038693 | 0.12755 | -0.005653 | -0.020766 | 121.5662 | 121.4574 | 121.4528 | 58.764 | -121.5571 | 121.3711 | 121.5398 | 121.5246 | 61.478 | -121.7117
1354.6094 | 121.8475 | -61.4639 | 60.2188 | -0.0025182 | -0.034085 | 0.00931 | 0.057504 | -0.010369 | 0.051753 | -0.0062567 | -0.0022666 | -0.0033587 | 0.059328 | 0.034918 | 0.051106 | -61.299 | -2.6817 | -61.307 | 60.1618 | 60.0713 | 60.0576 | -61.4069 | -61.3445 | 0.091933 | -61.4431 | 59.9666 | 60.1445 | 60.1294 | -61.5661 | 0.057019 | -0.057029 | 0.16494 | 0.15692 | 0.099901 | -0.14754 | -0.16125 | -0.10216 | -0.25216 | 0.11942 | 0.020814 | 0.12297 | -0.074318 | -0.089431 | 121.6257 | 121.5352 | 121.5215 | 58.7823 | -121.6257 | 121.4306 | 121.6084 | 121.5933 | 61.5559 | -121.7849
1356.2969 | 121.8933 | -61.4273 | 60.2371 | -0.010149 | -0.033658 | 0.0090964 | 0.057077 | -0.0099418 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.035132 | 0.051106 | -61.299 | -2.732 | -61.3116 | 60.1618 | 60.0575 | 60.0347 | -61.4161 | -61.3537 | 0.087354 | -61.4477 | 59.9621 | 60.1308 | 60.1156 | -61.5707 | 0.01124 | -0.07534 | 0.12832 | 0.11572 | 0.10448 | -0.17959 | -0.20246 | -0.14336 | -0.27505 | 0.073643 | -0.020386 | 0.12297 | -0.10636 | -0.12148 | 121.5891 | 121.4848 | 121.462 | 58.6953 | -121.6532 | 121.3894 | 121.5581 | 121.543 | 61.5147 | -121.8078
1358.0469 | 121.9482 | -61.409 | 60.1822 | -0.010149 | -0.034299 | 0.0095236 | 0.057291 | -0.010155 | 0.051753 | -0.013887 | -0.002053 | -0.0029313 | 0.059542 | 0.035132 | 0.050892 | -61.2944 | -2.7732 | -61.3116 | 60.1572 | 60.0575 | 60.0484 | -61.4206 | -61.3582 | 0.087354 | -61.4569 | 59.9575 | 60.1399 | 60.1202 | -61.5707 | -0.011649 | -0.024986 | 0.11459 | 0.097411 | 0.10906 | -0.12466 | -0.13379 | -0.16167 | -0.2247 | 0.050754 | -0.047853 | 0.11382 | -0.042275 | -0.061967 | 121.5662 | 121.4665 | 121.4574 | 58.6358 | -121.6028 | 121.3665 | 121.5489 | 121.5292 | 61.4964 | -121.7529
1359.7969 | 121.8521 | -61.4548 | 60.1959 | -0.0025182 | -0.034085 | 0.00931 | 0.057718 | -0.010369 | 0.05154 | -0.021518 | -0.0022666 | -0.0031451 | 0.059328 | 0.034491 | 0.050892 | -61.2898 | -2.8327 | -61.3116 | 60.1572 | 60.0575 | 60.0392 | -61.4252 | -61.3582 | 0.091933 | -61.4523 | 59.9575 | 60.1308 | 60.1202 | -61.5707 | 0.029548 | -0.038719 | 0.16494 | 0.14319 | 0.11364 | -0.13839 | -0.15668 | -0.11589 | -0.23843 | 0.09653 | 0.002501 | 0.11839 | -0.065165 | -0.0757 | 121.612 | 121.5123 | 121.494 | 58.622 | -121.6211 | 121.4123 | 121.5855 | 121.575 | 61.5467 | -121.7666
1361.5625 | 121.8613 | -61.3815 | 60.2646 | -0.010149 | -0.034513 | 0.0095236 | 0.057291 | -0.010369 | 0.05154 | -0.029148 | -0.0022666 | -0.0031451 | 0.059328 | 0.034918 | 0.05132 | -61.3081 | -2.8923 | -61.3299 | 60.1435 | 60.0392 | 60.0255 | -61.439 | -61.3674 | 0.087354 | -61.4706 | 59.9392 | 60.1079 | 60.1019 | -61.5936 | -0.057431 | -0.12112 | 0.073387 | 0.051632 | 0.10906 | -0.22537 | -0.23908 | -0.21203 | -0.32541 | 0.01413 | -0.089055 | 0.12297 | -0.15672 | -0.16268 | 121.525 | 121.4207 | 121.407 | 58.4893 | -121.7035 | 121.3207 | 121.4894 | 121.4834 | 61.4689 | -121.8581
1363.25 | 121.9894 | -61.3861 | 60.2097 | 0.0051128 | -0.034299 | 0.00931 | 0.057077 | -0.0099418 | 0.051753 | -0.029148 | -0.0022666 | -0.0031451 | 0.059542 | 0.034705 | 0.05132 | -61.3127 | -2.9609 | -61.3253 | 60.1297 | 60.0255 | 60.0118 | -61.4481 | -61.3857 | 0.087354 | -61.4797 | 59.9392 | 60.0987 | 60.0882 | -61.6027 | -0.062012 | -0.079923 | 0.073385 | 0.060787 | 0.1228 | -0.18418 | -0.19788 | -0.21661 | -0.27048 | 0.000393 | -0.093636 | 0.12297 | -0.11095 | -0.12148 | 121.5158 | 121.4116 | 121.3979 | 58.4252 | -121.6578 | 121.3253 | 121.4848 | 121.4743 | 61.4735 | -121.8124
1364.9844 | 121.843 | -61.5051 | 60.1776 | -0.0025182 | -0.034299 | 0.0095236 | 0.057291 | -0.0099418 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.034918 | 0.051106 | -61.3906 | -3.0434 | -61.4077 | 60.0382 | 59.9431 | 59.9339 | -61.5351 | -61.4727 | 0.087354 | -61.5667 | 59.8476 | 60.0071 | 59.9966 | -61.6897 | -0.029992 | -0.13945 | 0.11457 | 0.097397 | 0.12739 | -0.23455 | -0.24368 | -0.18459 | -0.33001 | 0.032416 | -0.061612 | 0.12298 | -0.17048 | -0.18101 | 121.5433 | 121.4482 | 121.4391 | 58.4618 | -121.7127 | 121.3527 | 121.5123 | 121.5017 | 61.5925 | -121.8673
1366.7344 | 121.8475 | -62.3062 | 59.3491 | -0.01778 | -0.034513 | 0.00931 | 0.057291 | -0.010155 | 0.051326 | -0.029148 | -0.0024804 | -0.0027177 | 0.059328 | 0.034918 | 0.05132 | -61.9262 | -3.1945 | -61.9525 | 59.5025 | 59.3936 | 59.3845 | -62.0937 | -61.9809 | 0.073618 | -62.1208 | 59.2982 | 59.4669 | 59.4426 | -62.2346 | 0.21247 | 0.15343 | 0.37999 | 0.35367 | 0.1412 | 0.044529 | 0.035444 | 0.071618 | -0.050874 | 0.32527 | 0.18545 | 0.11383 | 0.1178 | 0.09353 | 121.8087 | 121.6998 | 121.6907 | 59.1118 | -121.4428 | 121.6044 | 121.7731 | 121.7488 | 62.3798 | -121.5837
1368.4844 | 121.9849 | -62.8784 | 58.7448 | -0.010149 | -0.034085 | 0.00931 | 0.057291 | -0.010369 | 0.051753 | -0.021518 | -0.0024804 | -0.0031451 | 0.059542 | 0.034705 | 0.050892 | -62.0132 | -3.2952 | -62.0304 | 59.4155 | 59.3157 | 59.3112 | -62.167 | -62.0542 | 0.055303 | -62.1894 | 59.2112 | 59.389 | 59.3693 | -62.3308 | 0.71141 | 0.67069 | 0.8652 | 0.84804 | 0.13664 | 0.57093 | 0.56643 | 0.54767 | 0.46638 | 0.82421 | 0.68897 | 0.14131 | 0.64421 | 0.62452 | 122.2939 | 122.1942 | 122.1897 | 59.5832 | -120.9118 | 122.0896 | 122.2674 | 122.2477 | 62.9337 | -121.0756
1370.1719 | 121.9482 | -62.1689 | 59.4452 | -0.010149 | -0.034299 | 0.0095236 | 0.057504 | -0.0099418 | 0.05154 | -0.021518 | -0.0022666 | -0.0029313 | 0.059542 | 0.034918 | 0.051106 | -62.0224 | -3.3593 | -62.0487 | 59.388 | 59.2974 | 59.2884 | -62.1807 | -62.0817 | 0.087354 | -62.2078 | 59.1975 | 59.3616 | 59.3556 | -62.3353 | -0.011864 | -0.057156 | 0.14651 | 0.12019 | 0.13206 | -0.14776 | -0.15684 | -0.16645 | -0.24773 | 0.087205 | -0.038875 | 0.12757 | -0.083638 | -0.089594 | 121.5569 | 121.4663 | 121.4572 | 58.8096 | -121.6259 | 121.3663 | 121.5304 | 121.5245 | 62.2562 | -121.7805
1371.9219 | 121.8887 | -62.0041 | 59.6558 | -0.010149 | -0.034299 | 0.00931 | 0.057291 | -0.0097282 | 0.051112 | -0.021518 | -0.0022666 | -0.0033587 | 0.059542 | 0.034918 | 0.05132 | -61.885 | -3.4051 | -61.9205 | 59.5162 | 59.4211 | 59.4074 | -62.0617 | -61.9489 | 0.087354 | -62.0796 | 59.3348 | 59.4852 | 59.4838 | -62.2071 | -0.057607 | -0.13953 | 0.11907 | 0.083592 | 0.1412 | -0.2347 | -0.24836 | -0.20303 | -0.32095 | 0.055192 | -0.075466 | 0.12757 | -0.17059 | -0.17197 | 121.5203 | 121.4252 | 121.4115 | 58.599 | -121.7175 | 121.3389 | 121.4893 | 121.4879 | 62.0914 | -121.8629
1373.6719 | 121.8979 | -62.0087 | 59.6649 | -0.0025182 | -0.034299 | 0.00931 | 0.057718 | -0.010369 | 0.05154 | -0.013887 | -0.0024804 | -0.0029313 | 0.059542 | 0.034705 | 0.051106 | -61.8072 | -3.4692 | -61.8427 | 59.6032 | 59.4989 | 59.4944 | -61.9839 | -61.8665 | 0.082776 | -62.0017 | 59.4081 | 59.5676 | 59.5571 | -62.1247 | 0.024813 | -0.061698 | 0.20148 | 0.166 | 0.14119 | -0.16601 | -0.17053 | -0.11604 | -0.25685 | 0.14219 | 0.00695 | 0.12299 | -0.097328 | -0.10786 | 121.6119 | 121.5076 | 121.5031 | 58.5395 | -121.6488 | 121.4167 | 121.5763 | 121.5657 | 62.0914 | -121.7896
1375.3594 | 121.9711 | -62.0041 | 59.5688 | -0.01778 | -0.034299 | 0.00931 | 0.057077 | -0.010369 | 0.05154 | -0.013887 | -0.0022666 | -0.0029313 | 0.059542 | 0.034918 | 0.05132 | -61.8438 | -3.5333 | -61.8701 | 59.562 | 59.4669 | 59.4623 | -62.0113 | -61.9123 | 0.091933 | -62.0429 | 59.3714 | 59.531 | 59.5158 | -62.1659 | -0.007238 | -0.006774 | 0.16027 | 0.13395 | 0.14119 | -0.10193 | -0.10645 | -0.16182 | -0.19734 | 0.091822 | -0.038836 | 0.12299 | -0.037826 | -0.052939 | 121.5661 | 121.4709 | 121.4664 | 58.4708 | -121.5801 | 121.3755 | 121.535 | 121.5199 | 62.096 | -121.7347
1377.125 | 121.8979 | -62.1094 | 59.5322 | -0.0025182 | -0.034299 | 0.00931 | 0.057932 | -0.010155 | 0.051326 | -0.013887 | -0.0024804 | -0.0033587 | 0.059114 | 0.034918 | 0.050892 | -61.9079 | -3.6248 | -61.9434 | 59.5025 | 59.3982 | 59.3937 | -62.0846 | -61.9672 | 0.091933 | -62.1116 | 59.3073 | 59.4669 | 59.4563 | -62.2346 | 0.024785 | -0.029672 | 0.20146 | 0.16599 | 0.1412 | -0.134 | -0.1385 | -0.12522 | -0.22482 | 0.14216 | -0.002231 | 0.12299 | -0.065306 | -0.07584 | 121.6119 | 121.5075 | 121.503 | 58.4845 | -121.6168 | 121.4167 | 121.5762 | 121.5657 | 62.2013 | -121.7668
1378.8594 | 121.8475 | -62.2055 | 59.4589 | -0.01778 | -0.034513 | 0.00931 | 0.057077 | -0.010583 | 0.051326 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.035132 | 0.05132 | -61.972 | -3.7256 | -62.0212 | 59.4247 | 59.3249 | 59.3067 | -62.1624 | -62.0542 | 0.082776 | -62.1894 | 59.2249 | 59.3982 | 59.3785 | -62.3124 | 0.043073 | -0.034262 | 0.23349 | 0.18429 | 0.14121 | -0.13402 | -0.15225 | -0.10693 | -0.23399 | 0.1513 | 0.016061 | 0.12299 | -0.060742 | -0.080433 | 121.6302 | 121.5304 | 121.5122 | 58.4799 | -121.6214 | 121.4304 | 121.6037 | 121.584 | 62.2883 | -121.7714
1380.625 | 121.9757 | -62.1506 | 59.4452 | -0.010149 | -0.034299 | 0.00931 | 0.057291 | -0.010155 | 0.05154 | -0.021518 | -0.0024804 | -0.0031451 | 0.059328 | 0.035132 | 0.05132 | -62.1368 | -3.8034 | -62.1723 | 59.2507 | 59.1509 | 59.1373 | -62.3319 | -62.2099 | 0.082776 | -62.3543 | 59.0555 | 59.2334 | 59.2045 | -62.4819 | -0.18128 | -0.19451 | 0.013741 | -0.021729 | 0.15955 | -0.29428 | -0.30793 | -0.33128 | -0.38966 | -0.059309 | -0.2037 | 0.12757 | -0.21184 | -0.24069 | 121.4013 | 121.3015 | 121.2878 | 58.3472 | -121.777 | 121.2061 | 121.3839 | 121.3551 | 62.2334 | -121.927
1382.3125 | 121.9391 | -62.2925 | 59.3124 | -0.0025182 | -0.034513 | 0.00931 | 0.057291 | -0.0099418 | 0.05154 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.034918 | 0.051106 | -62.1002 | -3.895 | -62.1448 | 59.2873 | 59.1738 | 59.1739 | -62.2952 | -62.1916 | 0.078197 | -62.3268 | 59.083 | 59.2654 | 59.2366 | -62.4406 | -0.002741 | -0.025129 | 0.19227 | 0.14765 | 0.15039 | -0.13864 | -0.13855 | -0.14816 | -0.22944 | 0.10091 | -0.034325 | 0.11384 | -0.047037 | -0.075886 | 121.5798 | 121.4663 | 121.4664 | 58.3975 | -121.6077 | 121.3755 | 121.5579 | 121.529 | 62.3707 | -121.7531
1384.0625 | 121.9666 | -62.4023 | 59.1934 | -0.010149 | -0.034085 | 0.00931 | 0.057291 | -0.010155 | 0.05154 | -0.021518 | -0.002694 | -0.0031451 | 0.059755 | 0.035132 | 0.051106 | -62.2009 | -3.9957 | -62.2501 | 59.1774 | 59.0776 | 59.064 | -62.4051 | -62.2969 | 0.078197 | -62.4321 | 58.9823 | 59.1509 | 59.1267 | -62.5597 | -0.002771 | -0.015991 | 0.20141 | 0.15221 | 0.15498 | -0.11578 | -0.12942 | -0.15735 | -0.21115 | 0.10547 | -0.029771 | 0.12758 | -0.042483 | -0.066754 | 121.5798 | 121.48 | 121.4663 | 58.4066 | -121.5985 | 121.3846 | 121.5533 | 121.529 | 62.4805 | -121.7531
1385.8125 | 121.8475 | -62.5305 | 59.1751 | -0.0025182 | -0.034513 | 0.00931 | 0.057291 | -0.0099418 | 0.051753 | -0.0062567 | -0.002053 | -0.0029313 | 0.059328 | 0.034918 | 0.05132 | -62.2925 | -4.1148 | -62.3417 | 59.0767 | 58.9769 | 58.9679 | -62.4967 | -62.3976 | 0.087354 | -62.5283 | 58.8815 | 59.0502 | 59.0397 | -62.6558 | 0.033825 | -0.098406 | 0.23802 | 0.18882 | 0.15499 | -0.1982 | -0.20726 | -0.12533 | -0.29357 | 0.13291 | 0.00225 | 0.12758 | -0.1249 | -0.13544 | 121.6072 | 121.5074 | 121.4984 | 58.4158 | -121.6718 | 121.4121 | 121.5807 | 121.5702 | 62.6179 | -121.831
1387.4844 | 121.962 | -64.5035 | 57.0923 | -0.010149 | -0.034513 | 0.0095236 | 0.057504 | -0.0099418 | 0.05154 | -0.013887 | -0.0022666 | -0.0029313 | 0.059542 | 0.035132 | 0.05132 | -63.3226 | -4.4169 | -63.3764 | 58.042 | 57.9238 | 57.9377 | -63.5636 | -63.4553 | 0.018674 | -63.5859 | 57.8239 | 58.0063 | 57.9637 | -63.7227 | 0.9399 | 0.9497 | 1.1808 | 1.1271 | 0.18719 | 0.83147 | 0.84538 | 0.78077 | 0.73163 | 1.0482 | 0.91753 | 0.13676 | 0.914 | 0.87142 | 122.5455 | 122.4272 | 122.4411 | 60.0865 | -120.6559 | 122.3274 | 122.5098 | 122.4672 | 64.5222 | -120.815
1389.25 | 121.9574 | -62.677 | 58.905 | -0.010149 | -0.034299 | 0.00931 | 0.057291 | -0.010155 | 0.051967 | -0.029148 | -0.0024804 | -0.0025041 | 0.059328 | 0.034918 | 0.051533 | -62.5443 | -4.3345 | -62.6072 | 58.8066 | 58.7113 | 58.6931 | -62.7714 | -62.654 | 0.082776 | -62.7984 | 58.6114 | 58.7846 | 58.7604 | -62.9168 | -0.094427 | -0.09845 | 0.13269 | 0.069763 | 0.16419 | -0.1937 | -0.21189 | -0.23984 | -0.29362 | 0.022984 | -0.12141 | 0.11843 | -0.12038 | -0.14465 | 121.4836 | 121.3883 | 121.3701 | 58.3425 | -121.6765 | 121.2884 | 121.4616 | 121.4374 | 62.7598 | -121.8219
1391 | 121.9666 | -62.6678 | 58.9417 | 0.0051128 | -0.034726 | 0.0095236 | 0.057077 | -0.010155 | 0.05154 | -0.0062567 | -0.002053 | -0.0033587 | 0.059328 | 0.035346 | 0.051106 | -62.7366 | -4.481 | -62.8133 | 58.6006 | 58.5053 | 58.4825 | -62.9729 | -62.8555 | 0.091933 | -62.9953 | 58.4145 | 58.5832 | 58.5681 | -63.1275 | -0.30505 | -0.3411 | -0.068754 | -0.14541 | 0.15964 | -0.43637 | -0.45913 | -0.45962 | -0.52711 | -0.18763 | -0.32745 | 0.13217 | -0.35846 | -0.37357 | 121.2684 | 121.1731 | 121.1504 | 58.1868 | -121.9146 | 121.0824 | 121.251 | 121.2359 | 62.7598 | -122.0691
1392.7031 | 121.8567 | -63.2172 | 58.4564 | -0.0025182 | -0.034726 | 0.00931 | 0.057291 | -0.0099418 | 0.051326 | -0.021518 | -0.0022666 | -0.0029313 | 0.059755 | 0.034705 | 0.05132 | -63.0113 | -4.655 | -63.0696 | 58.3304 | 58.2305 | 58.2261 | -63.2568 | -63.1302 | 0.082776 | -63.2609 | 58.1352 | 58.3085 | 58.2934 | -63.4114 | -0.039632 | -0.12599 | 0.20586 | 0.14752 | 0.18715 | -0.22588 | -0.2303 | -0.19419 | -0.32117 | 0.086959 | -0.043699 | 0.15049 | -0.14795 | -0.16306 | 121.5476 | 121.4477 | 121.4433 | 58.5621 | -121.7132 | 121.3524 | 121.5256 | 121.5105 | 63.2999 | -121.8678
1394.4531 | 121.994 | -63.1302 | 58.4518 | -0.0025182 | -0.034726 | 0.0090964 | 0.057291 | -0.010155 | 0.05154 | -0.013887 | -0.0022666 | -0.0029313 | 0.059755 | 0.035132 | 0.051533 | -62.9655 | -4.7741 | -63.0422 | 58.3533 | 58.2626 | 58.2536 | -63.2202 | -63.1027 | 0.078197 | -63.238 | 58.1627 | 58.3314 | 58.3208 | -63.3656 | -0.089975 | -0.098524 | 0.16467 | 0.088012 | 0.17799 | -0.18925 | -0.19825 | -0.23538 | -0.28912 | 0.027456 | -0.10778 | 0.12759 | -0.12048 | -0.13101 | 121.4835 | 121.3928 | 121.3838 | 58.3561 | -121.672 | 121.2929 | 121.4616 | 121.451 | 63.2084 | -121.8174
1396.2031 | 121.875 | -63.3545 | 58.2458 | -0.0025182 | -0.034299 | 0.009951 | 0.057291 | -0.0099418 | 0.051753 | -0.013887 | -0.0024804 | -0.0029313 | 0.059755 | 0.034918 | 0.051106 | -63.1258 | -4.916 | -63.1978 | 58.1931 | 58.0978 | 58.0933 | -63.3896 | -63.2721 | 0.078197 | -63.3982 | 58.0071 | 58.1574 | 58.156 | -63.5396 | -0.035092 | -0.052775 | 0.22873 | 0.15666 | 0.19175 | -0.1481 | -0.15251 | -0.18507 | -0.2388 | 0.082348 | -0.043731 | 0.14133 | -0.08847 | -0.089847 | 121.5476 | 121.4522 | 121.4478 | 58.4385 | -121.6354 | 121.3615 | 121.5119 | 121.5105 | 63.4327 | -121.7854
1397.9688 | 121.843 | -65.5884 | 56.0669 | 0.0051128 | -0.03494 | 0.0095236 | 0.057291 | -0.010369 | 0.051326 | -0.013887 | -0.0022666 | -0.0031451 | 0.059755 | 0.035132 | 0.051106 | -64.8564 | -5.4609 | -64.9101 | 56.5037 | 56.3715 | 56.4038 | -65.1754 | -65.0395 | 0.000359 | -65.1473 | 56.2489 | 56.4312 | 56.4253 | -65.2932 | 0.41302 | 0.43675 | 0.73198 | 0.67827 | 0.26525 | 0.3046 | 0.33694 | 0.29513 | 0.18201 | 0.54885 | 0.44109 | 0.14596 | 0.36435 | 0.3584 | 122.092 | 121.9599 | 121.9922 | 60.1275 | -121.2423 | 121.8373 | 122.0196 | 122.0137 | 65.5887 | -121.3601
1399.6562 | 121.8796 | -63.7848 | 57.8888 | -0.010149 | -0.034726 | 0.00931 | 0.057291 | -0.010155 | 0.051753 | -0.013887 | -0.0022666 | -0.0027177 | 0.059328 | 0.035132 | 0.05132 | -63.6157 | -5.2869 | -63.7106 | 57.7032 | 57.6032 | 57.6034 | -63.8933 | -63.7895 | 0.078197 | -63.8927 | 57.4988 | 57.6675 | 57.634 | -64.0341 | -0.10847 | -0.18561 | 0.16914 | 0.074185 | 0.18266 | -0.28556 | -0.28537 | -0.24928 | -0.38996 | -0.004748 | -0.10793 | 0.14135 | -0.22133 | -0.25475 | 121.488 | 121.388 | 121.3882 | 58.4979 | -121.7821 | 121.2836 | 121.4523 | 121.4188 | 63.863 | -121.9229
1401.4062 | 121.8613 | -63.8809 | 57.7744 | -0.010149 | -0.034726 | 0.00931 | 0.057504 | -0.010155 | 0.052181 | -0.021518 | -0.0024804 | -0.0027177 | 0.059542 | 0.035346 | 0.050892 | -65.1586 | -5.7631 | -65.281 | 56.1374 | 56.051 | 56.0375 | -65.4913 | -65.3463 | 0.12398 | -65.4495 | 55.9376 | 56.097 | 56.1185 | -65.5954 | -1.6104 | -1.637 | -1.2776 | -1.4 | 0.21035 | -1.7234 | -1.7368 | -1.7145 | -1.8368 | -1.4654 | -1.5686 | 0.14596 | -1.6773 | -1.6558 | 120.0183 | 119.9319 | 119.9185 | 58.1179 | -123.2657 | 119.8185 | 119.9779 | 119.9994 | 64.0049 | -123.3698
1403.1094 | 121.9666 | -70.079 | 51.4664 | -0.0025182 | -0.034726 | 0.0095236 | 0.057504 | -0.0099418 | 0.051967 | -0.021518 | -0.0024804 | -0.0031451 | 0.059755 | 0.035132 | 0.05132 | -65.4378 | -6.0515 | -65.5465 | 55.8673 | 55.7671 | 55.7674 | -65.7477 | -65.6393 | -0.059164 | -65.7563 | 55.6445 | 55.7994 | 55.8026 | -65.9068 | 4.3313 | 4.4009 | 4.6412 | 4.5325 | 0.20124 | 4.3007 | 4.301 | 4.1722 | 4.1782 | 4.4397 | 4.3228 | 0.15055 | 4.333 | 4.3362 | 125.9463 | 125.8461 | 125.8464 | 64.0275 | -117.2141 | 125.7236 | 125.8784 | 125.8816 | 70.0199 | -117.3732
1404.8125 | 121.9849 | -64.2105 | 57.399 | -0.010149 | -0.035154 | 0.00931 | 0.057077 | -0.0099418 | 0.05154 | -0.029148 | -0.002053 | -0.0033587 | 0.059114 | 0.034918 | 0.051106 | -65.0624 | -6.0057 | -65.1848 | 56.2106 | 56.1288 | 56.1245 | -65.3814 | -65.2593 | 0.1194 | -65.3671 | 56.0383 | 56.1932 | 56.1918 | -65.513 | -1.1709 | -1.1884 | -0.85191 | -0.9743 | 0.19661 | -1.2702 | -1.2744 | -1.3025 | -1.3607 | -1.0488 | -1.1566 | 0.14596 | -1.2058 | -1.2072 | 120.4211 | 120.3393 | 120.335 | 58.2048 | -122.7804 | 120.2488 | 120.4037 | 120.4023 | 64.3299 | -122.912
1406.5625 | 121.9208 | -71.2784 | 50.3036 | -0.010149 | -0.03494 | 0.00931 | 0.056863 | -0.010155 | 0.051967 | -0.013887 | -0.002053 | -0.0031451 | 0.059755 | 0.035346 | 0.05132 | -65.8865 | -6.5231 | -65.986 | 55.4277 | 55.3 | 55.3233 | -66.2331 | -66.1247 | -0.13242 | -66.237 | 55.1592 | 55.3415 | 55.3127 | -66.4059 | 5.0453 | 5.1241 | 5.3918 | 5.2924 | 0.24709 | 4.9964 | 5.0196 | 4.8725 | 4.8556 | 5.1537 | 5.0414 | 0.16887 | 5.0379 | 5.009 | 126.7061 | 126.5784 | 126.6017 | 64.7553 | -116.5367 | 126.4376 | 126.6199 | 126.5911 | 71.146 | -116.7095
1408.3125 | 121.875 | -66.5039 | 55.2017 | -0.0025182 | -0.034726 | 0.0090964 | 0.056863 | -0.010155 | 0.051967 | -0.013887 | -0.0024804 | -0.0031451 | 0.059328 | 0.035132 | 0.05132 | -65.7492 | -6.7841 | -65.8853 | 55.501 | 55.4008 | 55.4011 | -66.1003 | -65.9827 | 0.055303 | -66.0813 | 55.3103 | 55.4514 | 55.4684 | -66.2411 | 0.4036 | 0.29926 | 0.75473 | 0.61862 | 0.21502 | 0.19905 | 0.1994 | 0.26285 | 0.1086 | 0.52117 | 0.42256 | 0.15971 | 0.2497 | 0.26664 | 122.0049 | 121.9047 | 121.905 | 59.7198 | -121.302 | 121.8142 | 121.9553 | 121.9723 | 66.5592 | -121.4428
1409.9844 | 121.9437 | -66.4627 | 55.1285 | -0.01778 | -0.03494 | 0.00931 | 0.057077 | -0.010155 | 0.05154 | -0.021518 | -0.0024804 | -0.0029313 | 0.059328 | 0.035132 | 0.050892 | -66.4543 | -7.1412 | -66.5858 | 54.8005 | 54.7002 | 54.7052 | -66.8146 | -66.7062 | 0.036989 | -66.8002 | 54.5915 | 54.7601 | 54.7541 | -66.9508 | -0.35191 | -0.32799 | 0.008456 | -0.12306 | 0.22885 | -0.42829 | -0.42331 | -0.48807 | -0.53699 | -0.24347 | -0.3375 | 0.15057 | -0.36842 | -0.37438 | 121.2632 | 121.1629 | 121.1679 | 59.3215 | -121.9431 | 121.0542 | 121.2228 | 121.2168 | 66.4997 | -122.0793
1411.7344 | 121.8842 | -66.5863 | 55.0735 | -0.0025182 | -0.03494 | 0.00931 | 0.057077 | -0.0097282 | 0.051753 | -0.013887 | -0.0022666 | -0.0033587 | 0.059542 | 0.035346 | 0.051106 | -66.2436 | -7.4938 | -66.3614 | 54.9974 | 54.8925 | 54.9112 | -66.6315 | -66.5047 | 0.018674 | -66.6079 | 54.7884 | 54.9478 | 54.9601 | -66.7676 | -0.045158 | -0.076187 | 0.34266 | 0.22487 | 0.27003 | -0.18104 | -0.16234 | -0.18132 | -0.28518 | 0.081591 | -0.021595 | 0.15972 | -0.12577 | -0.11341 | 121.5837 | 121.4788 | 121.4975 | 59.0925 | -121.705 | 121.3747 | 121.5341 | 121.5464 | 66.605 | -121.8412
1413.4375 | 121.9391 | -67.6071 | 53.9795 | -0.010149 | -0.034513 | 0.00931 | 0.057504 | -0.0097282 | 0.051753 | -0.013887 | -0.0024804 | -0.0029313 | 0.059328 | 0.035346 | 0.051533 | -65.447 | -7.535 | -65.5694 | 55.7665 | 55.6663 | 55.6667 | -65.821 | -65.6943 | 0.064461 | -65.8249 | 55.5804 | 55.7307 | 55.7248 | -65.9755 | 1.7861 | 1.787 | 2.1601 | 2.0377 | 0.25161 | 1.6869 | 1.6872 | 1.6316 | 1.601 | 1.9128 | 1.7822 | 0.15055 | 1.7512 | 1.7453 | 123.3736 | 123.2735 | 123.2738 | 60.0721 | -119.8005 | 123.1876 | 123.3378 | 123.3319 | 67.6716 | -119.955
1415.1875 | 121.8567 | -66.4124 | 55.2887 | -0.01778 | -0.03494 | 0.00931 | 0.057077 | -0.010155 | 0.051967 | -0.021518 | -0.002053 | -0.0031451 | 0.059328 | 0.035132 | 0.05132 | -66.088 | -7.9745 | -66.2058 | 55.1164 | 55.0299 | 55.0257 | -66.4666 | -66.3353 | 0.06904 | -66.4568 | 54.9349 | 55.0806 | 55.0838 | -66.6119 | -0.054267 | -0.1723 | 0.32437 | 0.20659 | 0.26085 | -0.25882 | -0.26302 | -0.19959 | -0.35382 | 0.077053 | -0.044447 | 0.15514 | -0.20814 | -0.20494 | 121.5288 | 121.4422 | 121.438 | 58.4378 | -121.7553 | 121.3472 | 121.4929 | 121.4961 | 66.4814 | -121.9006
1416.9375 | 121.9482 | -66.5817 | 54.9911 | -0.025411 | -0.034726 | 0.00931 | 0.057077 | -0.0099418 | 0.051967 | -0.029148 | -0.0024804 | -0.0027177 | 0.059328 | 0.035346 | 0.05132 | -66.5733 | -8.3362 | -66.7506 | 54.6082 | 54.517 | 54.5037 | -66.9749 | -66.8619 | 0.073618 | -66.9605 | 54.4267 | 54.5815 | 54.5755 | -67.1248 | -0.39316 | -0.38295 | 0.008436 | -0.16886 | 0.2243 | -0.47411 | -0.48744 | -0.54304 | -0.56448 | -0.28013 | -0.37873 | 0.16431 | -0.40966 | -0.41561 | 121.1899 | 121.0988 | 121.0854 | 58.2455 | -121.966 | 121.0084 | 121.1632 | 121.1573 | 66.6553 | -122.1159
1418.6875 | 121.8613 | -66.6595 | 55.0049 | -0.0025182 | -0.03494 | 0.00931 | 0.057291 | -0.0099418 | 0.052181 | -0.013887 | -0.0024804 | -0.0029313 | 0.059542 | 0.035346 | 0.051533 | -66.7106 | -8.6384 | -66.8376 | 54.48 | 54.3888 | 54.3847 | -67.1168 | -66.9763 | 0.078197 | -67.0978 | 54.2847 | 54.4487 | 54.4428 | -67.253 | -0.45728 | -0.52488 | -0.051096 | -0.17802 | 0.27926 | -0.61606 | -0.62021 | -0.59343 | -0.72015 | -0.31677 | -0.43827 | 0.15516 | -0.55617 | -0.56213 | 121.1395 | 121.0484 | 121.0442 | 58.0211 | -122.1217 | 120.9443 | 121.1083 | 121.1023 | 66.7377 | -122.2579
1420.3906 | 121.8292 | -68.1839 | 53.4714 | -0.01778 | -0.034726 | 0.0090964 | 0.057504 | -0.010369 | 0.051967 | -0.013887 | -0.0022666 | -0.0031451 | 0.059542 | 0.035132 | 0.051106 | -67.9972 | -9.2474 | -68.1332 | 53.1523 | 53.0426 | 53.0615 | -68.4356 | -68.2813 | 0.036989 | -68.4073 | 52.9615 | 53.1209 | 53.115 | -68.5854 | -0.25166 | -0.31911 | 0.18673 | 0.050675 | 0.30233 | -0.42875 | -0.40992 | -0.40152 | -0.50983 | -0.097353 | -0.22343 | 0.17808 | -0.35046 | -0.35641 | 121.3362 | 121.2265 | 121.2454 | 58.9365 | -121.9069 | 121.1454 | 121.3048 | 121.2989 | 68.2209 | -122.0568
1422.1406 | 121.8384 | -68.1015 | 53.5629 | -0.0025182 | -0.035367 | 0.0090964 | 0.057504 | -0.010155 | 0.051967 | -0.013887 | -0.002053 | -0.0035723 | 0.059328 | 0.035346 | 0.05132 | -67.727 | -9.4397 | -67.8723 | 53.4132 | 53.3265 | 53.3224 | -68.1654 | -68.0111 | 0.059882 | -68.1463 | 53.2408 | 53.3911 | 53.3714 | -68.3198 | -0.063901 | -0.14969 | 0.37446 | 0.22924 | 0.29314 | -0.23641 | -0.24049 | -0.21834 | -0.32209 | 0.090392 | -0.044844 | 0.1735 | -0.17187 | -0.19156 | 121.5147 | 121.428 | 121.4239 | 58.6618 | -121.7283 | 121.3423 | 121.4926 | 121.4729 | 68.1614 | -121.8828
1423.8281 | 121.962 | -69.5297 | 52.0203 | -0.01778 | -0.03494 | 0.00931 | 0.057291 | -0.010155 | 0.052181 | -0.021518 | -0.002053 | -0.0029313 | 0.059755 | 0.035773 | 0.051106 | -69.1509 | -10.1127 | -69.3098 | 51.9573 | 51.8704 | 51.8664 | -69.6169 | -69.4671 | 0.046146 | -69.5932 | 51.7803 | 51.9259 | 51.9291 | -69.7805 | -0.087197 | -0.062953 | 0.3788 | 0.21988 | 0.30708 | -0.14985 | -0.15382 | -0.25076 | -0.23997 | 0.062586 | -0.063494 | 0.18727 | -0.094362 | -0.091161 | 121.487 | 121.4001 | 121.3962 | 59.417 | -121.6372 | 121.31 | 121.4556 | 121.4588 | 69.5759 | -121.8007
1425.5781 | 121.907 | -69.9188 | 51.7044 | -0.0025182 | -0.035154 | 0.00931 | 0.057291 | -0.010155 | 0.051967 | 0.0013733 | -0.0022666 | -0.0029313 | 0.059328 | 0.035132 | 0.051106 | -69.4714 | -10.479 | -69.6212 | 51.6231 | 51.5499 | 51.5505 | -69.9466 | -69.7922 | 0.036989 | -69.9183 | 51.4506 | 51.6008 | 51.5949 | -70.1056 | -0.027781 | -0.081318 | 0.44741 | 0.29766 | 0.32544 | -0.15452 | -0.15389 | -0.18676 | -0.25376 | 0.1266 | 0.000517 | 0.18727 | -0.10359 | -0.10954 | 121.5419 | 121.4687 | 121.4693 | 59.4398 | -121.651 | 121.3695 | 121.5196 | 121.5137 | 69.9558 | -121.81
1427.2656 | 121.8384 | -70.2209 | 51.4343 | -0.010149 | -0.03494 | 0.00931 | 0.057291 | -0.010369 | 0.051967 | -0.013887 | -0.0022666 | -0.0031451 | 0.059114 | 0.035346 | 0.050892 | -69.856 | -10.859 | -70.0332 | 51.211 | 51.1286 | 51.1339 | -70.3587 | -70.1952 | 0.064461 | -70.3304 | 51.0432 | 51.1887 | 51.1919 | -70.5085 | -0.13776 | -0.22329 | 0.36495 | 0.18774 | 0.3255 | -0.3057 | -0.30046 | -0.28757 | -0.39117 | 0.025794 | -0.10944 | 0.17813 | -0.24558 | -0.24238 | 121.432 | 121.3496 | 121.3548 | 59.3619 | -121.793 | 121.2641 | 121.4097 | 121.4129 | 70.2854 | -121.9428
1429.0156 | 121.9254 | -70.5231 | 51.0635 | -0.010149 | -0.035154 | 0.00931 | 0.056863 | -0.010369 | 0.051967 | -0.021518 | -0.0024804 | -0.0027177 | 0.059114 | 0.035346 | 0.051106 | -69.9796 | -11.1933 | -70.1522 | 51.092 | 51.005 | 51.0102 | -70.4869 | -70.3234 | 0.041567 | -70.4632 | 50.9104 | 51.0605 | 51.0592 | -70.6459 | 0.036154 | 0.028458 | 0.54346 | 0.37082 | 0.33467 | -0.058539 | -0.053298 | -0.12281 | -0.15315 | 0.19971 | 0.059898 | 0.18271 | -0.002992 | -0.004369 | 121.6151 | 121.5281 | 121.5333 | 59.3298 | -121.5505 | 121.4335 | 121.5836 | 121.5822 | 70.5646 | -121.7094
1430.7031 | 121.9803 | -71.0678 | 50.5142 | -0.010149 | -0.034726 | 0.0095236 | 0.057291 | -0.010155 | 0.051967 | 0.0013733 | -0.0024804 | -0.0029313 | 0.059328 | 0.035346 | 0.051106 | -70.6664 | -11.6603 | -70.8527 | 50.3686 | 50.2907 | 50.296 | -71.2012 | -71.0331 | 0.046146 | -71.1591 | 50.2007 | 50.3554 | 50.3495 | -71.3556 | -0.13342 | -0.14561 | 0.40144 | 0.21509 | 0.34851 | -0.22353 | -0.21824 | -0.28779 | -0.3135 | 0.034753 | -0.091326 | 0.19646 | -0.15878 | -0.16474 | 121.4364 | 121.3585 | 121.3638 | 59.4075 | -121.7155 | 121.2685 | 121.4233 | 121.4173 | 71.114 | -121.8698
1432.4531 | 121.9482 | -72.5464 | 49.0448 | -0.01778 | -0.034726 | 0.00931 | 0.057291 | -0.010155 | 0.052181 | -0.021518 | -0.0024804 | -0.0027177 | 0.059328 | 0.035346 | 0.05132 | -72.1223 | -12.4295 | -72.3269 | 48.8761 | 48.8025 | 48.7942 | -72.6802 | -72.512 | 0.041567 | -72.6472 | 48.7081 | 48.8582 | 48.8523 | -72.8483 | -0.13384 | -0.16874 | 0.42409 | 0.21946 | 0.35329 | -0.24226 | -0.2506 | -0.30191 | -0.33667 | 0.034407 | -0.10083 | 0.20108 | -0.18656 | -0.19252 | 121.4224 | 121.3489 | 121.3406 | 60.1169 | -121.725 | 121.2545 | 121.4046 | 121.3987 | 72.588 | -121.8931
1434.1875 | 121.8384 | -71.2234 | 50.4639 | -0.010149 | -0.035154 | 0.0095236 | 0.057291 | -0.010369 | 0.052181 | -0.021518 | -0.0024804 | -0.0029313 | 0.059542 | 0.035346 | 0.050892 | -70.6893 | -12.2509 | -70.8848 | 50.3274 | 50.2403 | 50.2502 | -71.247 | -71.088 | 0.041567 | -71.2141 | 50.1504 | 50.2959 | 50.29 | -71.4151 | -0.023568 | -0.13646 | 0.53419 | 0.33868 | 0.36225 | -0.22355 | -0.21368 | -0.19167 | -0.31351 | 0.13545 | 0.009369 | 0.20104 | -0.16795 | -0.1739 | 121.5509 | 121.4638 | 121.4736 | 58.9725 | -121.7109 | 121.3738 | 121.5194 | 121.5134 | 71.265 | -121.879
1435.9375 | 121.8887 | -71.9421 | 49.7177 | 0.0051128 | -0.035367 | 0.0095236 | 0.057077 | -0.0099418 | 0.05154 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059328 | 0.035346 | 0.051106 | -70.8495 | -12.631 | -71.045 | 50.158 | 50.0663 | 50.0762 | -71.4393 | -71.2666 | 0.023253 | -71.3927 | 49.9672 | 50.1265 | 50.116 | -71.5891 | 0.50281 | 0.44029 | 1.0926 | 0.89713 | 0.39432 | 0.34861 | 0.35849 | 0.35302 | 0.2495 | 0.67557 | 0.54949 | 0.19647 | 0.4088 | 0.39827 | 122.1001 | 122.0085 | 122.0183 | 59.3112 | -121.157 | 121.9094 | 122.0686 | 122.0581 | 71.9654 | -121.3068
1437.7031 | 121.8613 | -71.4249 | 50.2121 | 0.0051128 | -0.035154 | 0.0095236 | 0.057291 | -0.010155 | 0.052394 | -0.013887 | -0.002053 | -0.0031451 | 0.059542 | 0.035559 | 0.050892 | -70.8312 | -12.956 | -71.0404 | 50.1488 | 50.0801 | 50.067 | -71.4256 | -71.2483 | 0.055303 | -71.3881 | 49.9764 | 50.1311 | 50.1251 | -71.58 | -0.00073 | -0.063249 | 0.59367 | 0.38443 | 0.38516 | -0.13204 | -0.14505 | -0.1551 | -0.23573 | 0.17661 | 0.036794 | 0.19189 | -0.081007 | -0.086963 | 121.5737 | 121.5049 | 121.4919 | 58.4688 | -121.6377 | 121.4012 | 121.556 | 121.55 | 71.4802 | -121.7921
1439.3906 | 121.843 | -71.4523 | 50.2121 | -0.010149 | -0.035154 | 0.00931 | 0.057291 | -0.010155 | 0.051753 | -0.013887 | -0.0022666 | -0.0033587 | 0.058901 | 0.035559 | 0.05132 | -70.703 | -13.2353 | -70.9168 | 50.2633 | 50.1808 | 50.1861 | -71.3065 | -71.1429 | 0.041567 | -71.2782 | 50.0908 | 50.2456 | 50.2396 | -71.4655 | 0.14579 | 0.05121 | 0.74934 | 0.53551 | 0.38973 | -0.031304 | -0.026006 | -0.013158 | -0.12127 | 0.30939 | 0.17415 | 0.18731 | 0.033458 | 0.027502 | 121.7156 | 121.6331 | 121.6384 | 58.217 | -121.5186 | 121.5432 | 121.6979 | 121.6919 | 71.4939 | -121.6776
1441.1406 | 121.8658 | -72.5784 | 49.0768 | -0.01778 | -0.03494 | 0.00931 | 0.057291 | -0.010155 | 0.051967 | -0.021518 | -0.0024804 | -0.0029313 | 0.059328 | 0.035346 | 0.051106 | -72.0216 | -13.9954 | -72.2491 | 48.9035 | 48.83 | 48.8308 | -72.6573 | -72.4845 | 0.036989 | -72.6335 | 48.7402 | 48.8811 | 48.8752 | -72.8208 | -0.078897 | -0.17332 | 0.55686 | 0.32933 | 0.40823 | -0.24683 | -0.24602 | -0.24239 | -0.33667 | 0.093922 | -0.055051 | 0.18734 | -0.19571 | -0.20167 | 121.482 | 121.4084 | 121.4093 | 58.583 | -121.7342 | 121.3186 | 121.4596 | 121.4536 | 72.6154 | -121.8977
1442.8438 | 121.9437 | -72.8165 | 48.7518 | -0.010149 | -0.03494 | 0.0095236 | 0.056863 | -0.0099418 | 0.051967 | -0.021518 | -0.0022666 | -0.0029313 | 0.059328 | 0.035773 | 0.050892 | -72.4428 | -14.4578 | -72.6749 | 48.4732 | 48.3904 | 48.3959 | -73.0969 | -72.9286 | 0.036989 | -73.0547 | 48.3006 | 48.4507 | 48.4448 | -73.2512 | -0.28044 | -0.27867 | 0.37368 | 0.14159 | 0.42203 | -0.3614 | -0.35597 | -0.43476 | -0.45119 | -0.11218 | -0.23825 | 0.19651 | -0.30109 | -0.30704 | 121.2896 | 121.2069 | 121.2123 | 58.3586 | -121.8487 | 121.1171 | 121.2672 | 121.2613 | 72.8535 | -122.0031
1444.6094 | 121.9757 | -72.7844 | 48.8113 | -0.010149 | -0.035367 | 0.00931 | 0.057291 | -0.010155 | 0.051967 | -0.013887 | -0.002694 | -0.0031451 | 0.059114 | 0.035346 | 0.051106 | -72.3558 | -14.8104 | -72.5925 | 48.5327 | 48.4545 | 48.4645 | -73.0374 | -72.86 | 0.041567 | -72.986 | 48.3602 | 48.5148 | 48.5043 | -73.1917 | -0.25295 | -0.27866 | 0.42863 | 0.19196 | 0.44491 | -0.3568 | -0.3468 | -0.40728 | -0.45118 | -0.075538 | -0.20162 | 0.20566 | -0.2965 | -0.30703 | 121.3171 | 121.239 | 121.249 | 57.9741 | -121.8487 | 121.1446 | 121.2993 | 121.2887 | 72.826 | -122.003
1446.3594 | 121.8567 | -73.1003 | 48.5596 | -0.010149 | -0.03494 | 0.00931 | 0.057291 | -0.0099418 | 0.052181 | -0.021518 | -0.0024804 | -0.0031451 | 0.059328 | 0.035559 | 0.05132 | -72.5939 | -15.227 | -72.8443 | 48.2763 | 48.1981 | 48.199 | -73.2846 | -73.1164 | 0.036989 | -73.2424 | 48.1129 | 48.2539 | 48.2571 | -73.4619 | -0.18436 | -0.28328 | 0.50641 | 0.25601 | 0.44037 | -0.36145 | -0.36059 | -0.36157 | -0.44665 | -0.016089 | -0.14217 | 0.21941 | -0.30571 | -0.30251 | 121.3766 | 121.2984 | 121.2993 | 57.8733 | -121.8442 | 121.2132 | 121.3541 | 121.3573 | 73.1373 | -122.0214
1448.0469 | 121.9757 | -73.8007 | 47.7859 | -0.010149 | -0.035154 | 0.00931 | 0.057291 | -0.010155 | 0.051967 | -0.013887 | -0.0022666 | -0.0031451 | 0.059328 | 0.035559 | 0.051106 | -73.038 | -15.7215 | -73.2884 | 47.8047 | 47.7356 | 47.7457 | -73.7517 | -73.5834 | 0.03241 | -73.7049 | 47.6459 | 47.796 | 47.7855 | -73.9197 | 0.048969 | 0.018763 | 0.76268 | 0.51229 | 0.46332 | -0.050303 | -0.040254 | -0.11908 | -0.14003 | 0.21726 | 0.09576 | 0.21484 | 0.010052 | -0.000482 | 121.6054 | 121.5363 | 121.5464 | 58.0791 | -121.5376 | 121.4466 | 121.5967 | 121.5861 | 73.8331 | -121.7057
1449.7812 | 121.9208 | -74.1531 | 47.4426 | -0.025411 | -0.035154 | 0.0095236 | 0.057077 | -0.010155 | 0.051967 | -0.021518 | -0.002694 | -0.0033587 | 0.059542 | 0.035346 | 0.050892 | -73.3997 | -16.2206 | -73.6501 | 47.4293 | 47.3556 | 47.3519 | -74.1317 | -73.9543 | 0.03241 | -74.0849 | 47.2613 | 47.4068 | 47.41 | -74.2998 | 0.021396 | -0.013342 | 0.75347 | 0.50308 | 0.48169 | -0.08703 | -0.09069 | -0.14664 | -0.18131 | 0.19886 | 0.068205 | 0.21485 | -0.035806 | -0.032604 | 121.5824 | 121.5087 | 121.5051 | 57.9326 | -121.5744 | 121.4145 | 121.56 | 121.5632 | 74.1855 | -121.7424
1451.5312 | 121.9757 | -74.8077 | 46.756 | 0.0051128 | -0.03494 | 0.00931 | 0.056863 | -0.0099418 | 0.051967 | -0.021518 | -0.0024804 | -0.0031451 | 0.059542 | 0.035559 | 0.05132 | -73.9994 | -16.8204 | -74.259 | 46.802 | 46.7283 | 46.7384 | -74.7545 | -74.577 | 0.023253 | -74.7122 | 46.6432 | 46.7796 | 46.7736 | -74.9271 | 0.053265 | 0.046065 | 0.8083 | 0.54878 | 0.49551 | -0.027697 | -0.017577 | -0.11934 | -0.11275 | 0.23076 | 0.095524 | 0.21486 | 0.023572 | 0.017616 | 121.6098 | 121.536 | 121.5461 | 57.9874 | -121.5105 | 121.451 | 121.5873 | 121.5813 | 74.831 | -121.6831
1453.2344 | 121.8292 | -75.9567 | 45.694 | -0.0025182 | -0.035154 | 0.00931 | 0.057291 | -0.010155 | 0.052394 | -0.013887 | -0.0022666 | -0.0029313 | 0.058901 | 0.035559 | 0.05132 | -75.0662 | -17.6216 | -75.3394 | 45.6987 | 45.6248 | 45.635 | -75.8763 | -75.6804 | 0.023253 | -75.8019 | 45.5398 | 45.6807 | 45.6747 | -76.0306 | 0.080415 | 0.004685 | 0.89053 | 0.61729 | 0.53687 | -0.069207 | -0.059009 | -0.073845 | -0.15416 | 0.27628 | 0.15478 | 0.22862 | -0.013282 | -0.019238 | 121.6554 | 121.5815 | 121.5917 | 58.3351 | -121.5703 | 121.4965 | 121.6374 | 121.6315 | 75.98 | -121.7245
1454.9844 | 121.9437 | -76.0483 | 45.5521 | -0.010149 | -0.035581 | 0.0095236 | 0.057291 | -0.0099418 | 0.052181 | -0.021518 | -0.002694 | -0.0031451 | 0.059542 | 0.035559 | 0.051106 | -75.3455 | -18.0383 | -75.6324 | 45.3965 | 45.3271 | 45.3374 | -76.1648 | -75.9826 | 0.018674 | -76.1041 | 45.2376 | 45.3877 | 45.3725 | -76.3236 | -0.1165 | -0.15558 | 0.7028 | 0.41583 | 0.53234 | -0.22493 | -0.21471 | -0.27534 | -0.31443 | 0.065637 | -0.055864 | 0.21947 | -0.16441 | -0.17952 | 121.4448 | 121.3754 | 121.3856 | 58.01 | -121.7168 | 121.2859 | 121.4359 | 121.4208 | 76.067 | -121.8757
1456.7344 | 121.8613 | -76.712 | 44.8975 | -0.010149 | -0.035581 | 0.00931 | 0.057291 | -0.0097282 | 0.051967 | -0.013887 | -0.002053 | -0.0029313 | 0.059328 | 0.035559 | 0.051106 | -76.0826 | -18.6518 | -76.3833 | 44.6182 | 44.5533 | 44.559 | -76.9478 | -76.7427 | 0.009516 | -76.8688 | 44.4593 | 44.6047 | 44.6033 | -77.1066 | -0.23574 | -0.27931 | 0.62943 | 0.32875 | 0.56449 | -0.34417 | -0.33847 | -0.39456 | -0.43818 | -0.030672 | -0.15675 | 0.23781 | -0.29274 | -0.29412 | 121.3302 | 121.2653 | 121.271 | 58.0602 | -121.8452 | 121.1713 | 121.3168 | 121.3154 | 76.7216 | -122.0041
1458.4688 | 121.9711 | -77.1973 | 44.3802 | -0.010149 | -0.035154 | 0.00931 | 0.057291 | -0.0097282 | 0.052394 | -0.021518 | -0.0022666 | -0.0031451 | 0.059328 | 0.035132 | 0.05132 | -76.2291 | -19.0318 | -76.5344 | 44.4579 | 44.3793 | 44.4033 | -77.1172 | -76.9167 | 0.009516 | -77.0474 | 44.2899 | 44.4399 | 44.4294 | -77.2714 | 0.080067 | 0.077724 | 0.96816 | 0.6629 | 0.58283 | -0.000892 | 0.023129 | -0.074164 | -0.090309 | 0.28057 | 0.14991 | 0.22407 | 0.059699 | 0.049164 | 121.6552 | 121.5766 | 121.6006 | 58.1654 | -121.4974 | 121.4871 | 121.6372 | 121.6266 | 77.2068 | -121.6516
1460.1719 | 121.8887 | -76.4053 | 45.2454 | -0.0025182 | -0.035154 | 0.0095236 | 0.057291 | -0.0099418 | 0.052608 | -0.0062567 | -0.0024804 | -0.0029313 | 0.059542 | 0.035773 | 0.051533 | -75.6705 | -19.16 | -75.9712 | 44.9844 | 44.9242 | 44.9299 | -76.5631 | -76.3718 | 0.036989 | -76.4933 | 44.8439 | 44.9893 | 44.9788 | -76.7357 | -0.15782 | -0.26094 | 0.73479 | 0.43409 | 0.59191 | -0.32117 | -0.31551 | -0.33038 | -0.40148 | 0.033501 | -0.087999 | 0.24238 | -0.25604 | -0.26658 | 121.3898 | 121.3295 | 121.3352 | 57.2453 | -121.8085 | 121.2492 | 121.3947 | 121.3841 | 76.4423 | -121.9811
1461.875 | 121.9254 | -78.4882 | 43.0573 | -0.0025182 | -0.035154 | 0.0090964 | 0.057291 | -0.010155 | 0.052181 | -0.021518 | -0.0024804 | -0.0031451 | 0.059328 | 0.035559 | 0.05132 | -76.4489 | -19.8606 | -76.7724 | 44.1832 | 44.1091 | 44.124 | -77.3965 | -77.1914 | 0.014095 | -77.3221 | 44.0197 | 44.1652 | 44.1546 | -77.5553 | 1.0916 | 1.126 | 2.0393 | 1.7157 | 0.62407 | 1.0519 | 1.0668 | 0.93284 | 0.9625 | 1.2967 | 1.1661 | 0.23324 | 1.1079 | 1.0974 | 122.6714 | 122.5973 | 122.6122 | 58.6276 | -120.4538 | 122.5079 | 122.6533 | 122.6428 | 78.5023 | -120.6126
1463.6406 | 121.8979 | -77.33 | 44.2841 | -0.0025182 | -0.035367 | 0.0097374 | 0.057504 | -0.0099418 | 0.052394 | -0.013887 | -0.0024804 | -0.0029313 | 0.059542 | 0.035773 | 0.050892 | -76.7144 | -20.3093 | -77.0426 | 43.8902 | 43.8207 | 43.831 | -77.6667 | -77.4707 | 0.03241 | -77.5968 | 43.7405 | 43.8813 | 43.8753 | -77.8392 | -0.33665 | -0.39387 | 0.6156 | 0.28746 | 0.62411 | -0.46339 | -0.45307 | -0.50919 | -0.5436 | -0.14071 | -0.26678 | 0.2424 | -0.40276 | -0.40872 | 121.2202 | 121.1507 | 121.161 | 57.0207 | -121.9507 | 121.0705 | 121.2113 | 121.2054 | 77.3624 | -122.1233
1465.3438 | 121.9849 | -77.9205 | 43.6203 | -0.0025182 | -0.035154 | 0.0097374 | 0.057291 | -0.0099418 | 0.052608 | -0.013887 | -0.0022666 | -0.0031451 | 0.059114 | 0.035773 | 0.050892 | -76.9891 | -20.8038 | -77.3264 | 43.5789 | 43.5139 | 43.5288 | -77.9826 | -77.7821 | 0.018674 | -77.9082 | 43.4245 | 43.57 | 43.564 | -78.146 | -0.062084 | -0.041439 | 0.93141 | 0.59412 | 0.6562 | -0.10642 | -0.091497 | -0.22545 | -0.19576 | 0.13846 | 0.012377 | 0.23783 | -0.050348 | -0.056304 | 121.4994 | 121.4344 | 121.4493 | 57.1168 | -121.6029 | 121.3451 | 121.4905 | 121.4845 | 77.9392 | -121.7663
1467.0781 | 121.8201 | -78.1082 | 43.5425 | 0.0051128 | -0.035154 | 0.00931 | 0.057077 | -0.0099418 | 0.052394 | -0.013887 | -0.0024804 | -0.0033587 | 0.059328 | 0.035773 | 0.050892 | -77.2364 | -21.2891 | -77.5874 | 43.3133 | 43.2346 | 43.2541 | -78.2619 | -78.0614 | 0.018674 | -78.1875 | 43.1453 | 43.2998 | 43.2893 | -78.4161 | -0.15372 | -0.22916 | 0.87186 | 0.52084 | 0.67456 | -0.30791 | -0.28839 | -0.30792 | -0.39722 | 0.046838 | -0.079241 | 0.22868 | -0.24266 | -0.2532 | 121.4215 | 121.3428 | 121.3623 | 56.8191 | -121.8044 | 121.2535 | 121.408 | 121.3975 | 78.1269 | -121.9586
1468.7656 | 121.9025 | -78.273 | 43.3594 | -0.010149 | -0.035367 | 0.0097374 | 0.057077 | -0.0099418 | 0.052608 | -0.013887 | -0.002694 | -0.0031451 | 0.059114 | 0.035559 | 0.051106 | -77.4332 | -21.6829 | -77.7934 | 43.0798 | 43.0102 | 43.0206 | -78.4863 | -78.2766 | 0.03241 | -78.4118 | 42.9209 | 43.0709 | 43.0695 | -78.6451 | -0.21329 | -0.27956 | 0.83978 | 0.47961 | 0.6929 | -0.34918 | -0.3388 | -0.37207 | -0.43847 | -0.003566 | -0.1388 | 0.23326 | -0.28849 | -0.28987 | 121.3528 | 121.2832 | 121.2936 | 56.5902 | -121.8457 | 121.1939 | 121.3439 | 121.3425 | 78.3054 | -122.0045
1470.4844 | 121.8246 | -78.3829 | 43.2724 | -0.0025182 | -0.035367 | 0.00931 | 0.057291 | -0.0099418 | 0.052394 | -0.021518 | -0.0024804 | -0.0031451 | 0.059542 | 0.035559 | 0.051106 | -77.36 | -22.072 | -77.7293 | 43.1302 | 43.056 | 43.0755 | -78.4497 | -78.2308 | 0.027831 | -78.366 | 42.9713 | 43.1167 | 43.1061 | -78.6084 | -0.066793 | -0.14222 | 1.0229 | 0.65357 | 0.72037 | -0.21641 | -0.19688 | -0.22557 | -0.30113 | 0.15208 | 0.016848 | 0.24242 | -0.15573 | -0.16626 | 121.5131 | 121.4389 | 121.4584 | 56.3108 | -121.7221 | 121.3541 | 121.4995 | 121.489 | 78.4107 | -121.8808
1472.2031 | 121.843 | -77.124 | 44.5541 | -0.01778 | -0.035581 | 0.0097374 | 0.057291 | -0.010155 | 0.052181 | -0.021518 | -0.0022666 | -0.0031451 | 0.059114 | 0.035987 | 0.050892 | -76.7098 | -22.1453 | -77.0975 | 43.7574 | 43.6787 | 43.7028 | -77.8178 | -77.6127 | 0.03241 | -77.7387 | 43.5848 | 43.7439 | 43.738 | -77.9811 | -0.69375 | -0.79672 | 0.41418 | 0.026526 | 0.72028 | -0.87542 | -0.85135 | -0.85712 | -0.96935 | -0.48864 | -0.61472 | 0.24241 | -0.8102 | -0.81616 | 120.8814 | 120.8027 | 120.8268 | 54.9787 | -122.3719 | 120.7088 | 120.868 | 120.862 | 77.1564 | -122.5353
1473.9219 | 121.8384 | -77.9572 | 43.6844 | 0.0051128 | -0.035367 | 0.00931 | 0.057291 | -0.0097282 | 0.052394 | -0.013887 | -0.0022666 | -0.0033587 | 0.059328 | 0.035987 | 0.050892 | -76.8289 | -22.6032 | -77.2257 | 43.5926 | 43.5276 | 43.538 | -77.9643 | -77.7638 | 0.023253 | -77.8807 | 43.4291 | 43.5837 | 43.5823 | -78.1277 | -0.007148 | -0.091791 | 1.1283 | 0.73146 | 0.73861 | -0.15677 | -0.14643 | -0.17052 | -0.25527 | 0.19339 | 0.076471 | 0.24699 | -0.1007 | -0.10208 | 121.5497 | 121.4848 | 121.4951 | 55.354 | -121.6487 | 121.3863 | 121.5408 | 121.5395 | 77.9804 | -121.8121
1475.6562 | 121.9528 | -78.1586 | 43.4052 | -0.01778 | -0.035581 | 0.0095236 | 0.057718 | -0.0099418 | 0.052394 | -0.0062567 | -0.0022666 | -0.0033587 | 0.059114 | 0.035559 | 0.050892 | -76.6412 | -22.8641 | -77.0471 | 43.762 | 43.6833 | 43.7074 | -77.8178 | -77.6127 | 0.009516 | -77.7479 | 43.5939 | 43.7439 | 43.7288 | -77.9766 | 0.34079 | 0.35685 | 1.5174 | 1.1114 | 0.77064 | 0.27815 | 0.30222 | 0.182 | 0.1888 | 0.54591 | 0.41067 | 0.22867 | 0.33879 | 0.32368 | 121.9206 | 121.8419 | 121.8659 | 55.2944 | -121.2229 | 121.7525 | 121.9025 | 121.8874 | 78.1681 | -121.3817
1477.3594 | 121.875 | -77.5452 | 44.1101 | -0.010149 | -0.035154 | 0.0097374 | 0.057291 | -0.0097282 | 0.052608 | -0.0062567 | -0.0024804 | -0.0031451 | 0.059328 | 0.035559 | 0.05132 | -76.4763 | -23.1022 | -76.8777 | 43.8902 | 43.8207 | 43.8356 | -77.6667 | -77.4707 | 0.018674 | -77.6014 | 43.7267 | 43.8767 | 43.8708 | -77.8392 | -0.1215 | -0.21992 | 1.0688 | 0.66743 | 0.78893 | -0.28944 | -0.27454 | -0.29404 | -0.38338 | 0.074443 | -0.056215 | 0.23782 | -0.23339 | -0.23934 | 121.4354 | 121.3658 | 121.3807 | 54.4429 | -121.7768 | 121.2719 | 121.4219 | 121.4159 | 77.5638 | -121.9493
1479.0625 | 121.9757 | -77.124 | 44.4626 | -0.010149 | -0.035581 | 0.00931 | 0.057291 | -0.0099418 | 0.052181 | -0.013887 | -0.0022666 | -0.0031451 | 0.059114 | 0.035773 | 0.051106 | -76.3344 | -23.2762 | -76.7495 | 44.0001 | 43.9306 | 43.9409 | -77.5659 | -77.3608 | 0.036989 | -77.4778 | 43.8412 | 43.9912 | 43.9806 | -77.7247 | -0.44191 | -0.46251 | 0.78961 | 0.37447 | 0.81639 | -0.53202 | -0.52171 | -0.60071 | -0.6214 | -0.23681 | -0.35373 | 0.24698 | -0.4714 | -0.48194 | 121.1241 | 121.0546 | 121.0649 | 53.8478 | -122.0285 | 120.9652 | 121.1152 | 121.1047 | 77.161 | -122.1873
1480.8125 | 121.8246 | -76.3412 | 45.3461 | -0.010149 | -0.035367 | 0.0097374 | 0.057504 | -0.0099418 | 0.052822 | -0.0062567 | -0.0022666 | -0.0031451 | 0.058901 | 0.035773 | 0.050892 | -74.9929 | -23.0106 | -75.4173 | 45.3232 | 45.2493 | 45.2641 | -76.2335 | -76.0467 | 0.036989 | -76.1728 | 45.1598 | 45.3098 | 45.2947 | -76.406 | 0.10778 | -0.022842 | 1.3483 | 0.92398 | 0.8162 | -0.096778 | -0.081975 | -0.064786 | -0.18628 | 0.2945 | 0.16842 | 0.23321 | -0.036248 | -0.051361 | 121.6645 | 121.5905 | 121.6053 | 53.3306 | -121.5795 | 121.501 | 121.6511 | 121.636 | 76.3782 | -121.7521
1482.5938 | 121.8796 | -76.8723 | 44.7281 | -0.0025182 | -0.035581 | 0.0095236 | 0.057291 | -0.0097282 | 0.052394 | -0.013887 | -0.002694 | -0.0029313 | 0.059328 | 0.035987 | 0.050892 | -75.5011 | -23.4868 | -75.9392 | 44.7738 | 44.7044 | 44.7192 | -76.7967 | -76.5916 | 0.046146 | -76.7223 | 44.615 | 44.7604 | 44.7544 | -76.9509 | 0.075578 | 0.045732 | 1.3711 | 0.93306 | 0.85748 | -0.023689 | -0.008848 | -0.07866 | -0.11314 | 0.28064 | 0.14998 | 0.22864 | 0.032301 | 0.026345 | 121.6461 | 121.5767 | 121.5915 | 53.3854 | -121.5248 | 121.4872 | 121.6326 | 121.6267 | 76.9184 | -121.679
1484.2969 | 121.8933 | -76.918 | 44.6777 | -0.010149 | -0.035367 | 0.00931 | 0.057504 | -0.0097282 | 0.052608 | -0.013887 | -0.002053 | -0.0031451 | 0.059328 | 0.035987 | 0.051106 | -76.0414 | -24.05 | -76.5115 | 44.1741 | 44.0954 | 44.1103 | -77.3828 | -77.1823 | 0.036989 | -77.3129 | 44.0197 | 44.1606 | 44.1501 | -77.5507 | -0.46475 | -0.50368 | 0.87663 | 0.40655 | 0.8713 | -0.58233 | -0.56745 | -0.63271 | -0.65799 | -0.26423 | -0.39489 | 0.23782 | -0.51714 | -0.52768 | 121.0921 | 121.0134 | 121.0283 | 52.868 | -122.0605 | 120.9378 | 121.0786 | 121.0681 | 76.955 | -122.2285
1486.0469 | 121.8842 | -77.3209 | 44.2841 | -0.0025182 | -0.035367 | 0.0097374 | 0.057504 | -0.0097282 | 0.052822 | -0.021518 | -0.002694 | -0.0031451 | 0.059328 | 0.035987 | 0.050892 | -75.9407 | -24.2148 | -76.4153 | 44.2381 | 44.1687 | 44.1881 | -77.3233 | -77.1227 | 0.027831 | -77.2488 | 44.0884 | 44.2293 | 44.2187 | -77.4866 | -0.002389 | -0.045909 | 1.3802 | 0.90553 | 0.90792 | -0.11539 | -0.095936 | -0.16577 | -0.19563 | 0.19812 | 0.072041 | 0.23781 | -0.054787 | -0.065321 | 121.559 | 121.4895 | 121.509 | 53.106 | -121.6073 | 121.4093 | 121.5501 | 121.5396 | 77.3487 | -121.7707
1487.7344 | 121.962 | -77.1103 | 44.4489 | -0.010149 | -0.035581 | 0.009951 | 0.057077 | -0.0099418 | 0.052608 | -0.021518 | -0.0022666 | -0.0031451 | 0.058901 | 0.035773 | 0.051106 | -75.3821 | -24.2057 | -75.8614 | 44.7647 | 44.6952 | 44.7055 | -76.7967 | -76.5916 | 0.023253 | -76.736 | 44.6012 | 44.7467 | 44.7453 | -76.9601 | 0.31362 | 0.31581 | 1.7282 | 1.2489 | 0.93531 | 0.24639 | 0.25665 | 0.15022 | 0.15236 | 0.51868 | 0.37429 | 0.22407 | 0.2978 | 0.29642 | 121.875 | 121.8055 | 121.8158 | 52.9046 | -121.2455 | 121.7115 | 121.8569 | 121.8556 | 77.1335 | -121.4089
1489.4062 | 121.8567 | -77.2797 | 44.3481 | -0.010149 | -0.035154 | 0.0097374 | 0.057504 | -0.0097282 | 0.053035 | -0.021518 | -0.0024804 | -0.0031451 | 0.059328 | 0.035987 | 0.050679 | -75.9956 | -24.6406 | -76.4932 | 44.1008 | 44.0359 | 44.0508 | -77.4606 | -77.283 | 0.036989 | -77.3862 | 43.9556 | 44.0919 | 44.086 | -77.6194 | -0.18096 | -0.24735 | 1.284 | 0.7865 | 0.96746 | -0.31227 | -0.29738 | -0.33976 | -0.3925 | -0.003333 | -0.10652 | 0.23324 | -0.25623 | -0.26219 | 121.3805 | 121.3155 | 121.3304 | 52.639 | -121.8088 | 121.2353 | 121.3716 | 121.3656 | 77.3167 | -121.9676
1491.0938 | 121.8796 | -77.0462 | 44.5908 | -0.0025182 | -0.035581 | 0.0097374 | 0.057291 | -0.010155 | 0.053035 | -0.0062567 | -0.0024804 | -0.0031451 | 0.059542 | 0.035773 | 0.050892 | -75.7072 | -24.6635 | -76.2093 | 44.3618 | 44.2877 | 44.3072 | -77.1996 | -77.0312 | 0.036989 | -77.1252 | 44.2075 | 44.3529 | 44.3469 | -77.3538 | -0.15342 | -0.22899 | 1.339 | 0.83689 | 0.99031 | -0.30304 | -0.28359 | -0.30764 | -0.38329 | 0.015037 | -0.078991 | 0.22865 | -0.23787 | -0.24382 | 121.408 | 121.3339 | 121.3534 | 52.3827 | -121.7904 | 121.2537 | 121.3991 | 121.3931 | 77.0832 | -121.9446
1492.7656 | 121.843 | -76.918 | 44.7418 | 0.0051128 | -0.035795 | 0.0097374 | 0.057291 | -0.0095144 | 0.053035 | -0.013887 | -0.0024804 | -0.0031451 | 0.059328 | 0.035987 | 0.050679 | -75.3089 | -24.7139 | -75.8293 | 44.7235 | 44.6495 | 44.6689 | -76.8379 | -76.6832 | 0.018674 | -76.7772 | 44.5554 | 44.7054 | 44.6949 | -77.015 | 0.080145 | -0.018363 | 1.6092 | 1.0887 | 1.0086 | -0.092369 | -0.072946 | -0.096987 | -0.18639 | 0.23485 | 0.14082 | 0.2378 | -0.036375 | -0.04691 | 121.6415 | 121.5675 | 121.5869 | 52.2041 | -121.5797 | 121.4735 | 121.6235 | 121.6129 | 76.9367 | -121.7568
1494.4531 | 121.962 | -75.4349 | 46.1792 | -0.010149 | -0.035367 | 0.00931 | 0.057504 | -0.0095144 | 0.053249 | -0.021518 | -0.0024804 | -0.0033587 | 0.059542 | 0.035987 | 0.050892 | -73.798 | -24.2652 | -74.3688 | 46.1611 | 46.0872 | 46.102 | -75.3909 | -75.2455 | 0.041567 | -75.3258 | 46.0022 | 46.1477 | 46.1463 | -75.5544 | 0.04393 | -0.018127 | 1.6369 | 1.066 | 1.0221 | -0.091965 | -0.077221 | -0.1195 | -0.17696 | 0.18941 | 0.10911 | 0.22861 | -0.031494 | -0.032871 | 121.5959 | 121.5221 | 121.5369 | 51.1697 | -121.5701 | 121.4371 | 121.5826 | 121.5812 | 75.4764 | -121.7336
1496.1406 | 121.875 | -72.8622 | 48.793 | -0.0025182 | -0.035367 | 0.0095236 | 0.057504 | -0.0097282 | 0.053249 | -0.013887 | -0.0022666 | -0.0029313 | 0.059114 | 0.035987 | 0.050892 | -71.2066 | -23.1343 | -71.7684 | 48.757 | 48.6835 | 48.6843 | -72.8039 | -72.6585 | 0.064461 | -72.7479 | 48.5891 | 48.7438 | 48.7378 | -72.9628 | 0.058391 | -0.036012 | 1.6556 | 1.0939 | 1.0355 | -0.10955 | -0.10872 | -0.10052 | -0.20394 | 0.20374 | 0.11429 | 0.21481 | -0.049257 | -0.055213 | 121.6193 | 121.5457 | 121.5466 | 49.728 | -121.5969 | 121.4513 | 121.606 | 121.6001 | 72.9267 | -121.7558
1497.8281 | 121.843 | -71.9238 | 49.7314 | -0.010149 | -0.035795 | 0.0095236 | 0.057504 | -0.0097282 | 0.052822 | -0.021518 | -0.0024804 | -0.0027177 | 0.059542 | 0.0362 | 0.050679 | -70.1307 | -22.7314 | -70.6971 | 49.8146 | 49.7366 | 49.7374 | -71.7599 | -71.61 | 0.055303 | -71.7086 | 49.6376 | 49.7877 | 49.7863 | -71.9051 | 0.16397 | 0.08318 | 1.7931 | 1.2268 | 1.0628 | 0.005192 | 0.005943 | 0.018771 | -0.093884 | 0.31385 | 0.21525 | 0.19647 | 0.056249 | 0.054872 | 121.7385 | 121.6605 | 121.6612 | 49.1925 | -121.4913 | 121.5614 | 121.7115 | 121.7101 | 71.9791 | -121.6365
1499.5781 | 121.8155 | -71.3562 | 50.2625 | -0.01778 | -0.035367 | 0.0097374 | 0.057504 | -0.0097282 | 0.052822 | -0.021518 | -0.0022666 | -0.0031451 | 0.059542 | 0.035773 | 0.050892 | -69.595 | -22.6306 | -70.1751 | 50.3091 | 50.2174 | 50.2273 | -71.2608 | -71.1292 | 0.059882 | -71.2187 | 50.1366 | 50.2822 | 50.2762 | -71.4197 | 0.095446 | 0.04664 | 1.7612 | 1.1811 | 1.0856 | -0.045027 | -0.035152 | -0.063501 | -0.12583 | 0.22699 | 0.13754 | 0.20104 | 0.019733 | 0.013777 | 121.6653 | 121.5736 | 121.5835 | 48.7256 | -121.5232 | 121.4928 | 121.6384 | 121.6324 | 71.4161 | -121.6822
1501.2656 | 121.8338 | -71.5988 | 50.0427 | -0.0025182 | -0.035795 | 0.0095236 | 0.057504 | -0.0097282 | 0.053249 | -0.0062567 | -0.0022666 | -0.0031451 | 0.059542 | 0.035987 | 0.051106 | -69.9613 | -23.0198 | -70.5734 | 49.8696 | 49.7962 | 49.7969 | -71.6958 | -71.5459 | 0.055303 | -71.6491 | 49.6925 | 49.8426 | 49.8458 | -71.8547 | -0.096937 | -0.17316 | 1.6375 | 1.0254 | 1.1223 | -0.24656 | -0.24582 | -0.25587 | -0.35022 | 0.052943 | -0.050242 | 0.20563 | -0.20009 | -0.19689 | 121.4684 | 121.395 | 121.3957 | 48.579 | -121.7385 | 121.2913 | 121.4415 | 121.4447 | 71.6541 | -121.8974
1503.0156 | 121.9116 | -71.1823 | 50.3998 | -0.01778 | -0.035367 | 0.0097374 | 0.057718 | -0.0097282 | 0.053249 | -0.029148 | -0.0024804 | -0.0033587 | 0.059542 | 0.035987 | 0.050892 | -69.682 | -23.029 | -70.3216 | 50.0893 | 50.0068 | 50.0075 | -71.4714 | -71.3353 | 0.064461 | -71.4339 | 49.9214 | 50.0624 | 50.0656 | -71.6349 | -0.28914 | -0.31045 | 1.5002 | 0.86061 | 1.1497 | -0.39299 | -0.39225 | -0.45266 | -0.47835 | -0.153 | -0.25161 | 0.20105 | -0.33737 | -0.33417 | 121.2716 | 121.189 | 121.1898 | 48.1533 | -121.8712 | 121.1037 | 121.2447 | 121.2479 | 71.2467 | -122.0347
1504.8281 | 121.8338 | -70.3308 | 51.3062 | -0.0025182 | -0.035154 | 0.0097374 | 0.057504 | -0.0095144 | 0.053035 | -0.021518 | -0.0022666 | -0.0033587 | 0.059328 | 0.0362 | 0.050892 | -68.4642 | -22.4704 | -69.113 | 51.2706 | 51.1927 | 51.1888 | -70.2946 | -70.1631 | 0.055303 | -70.2617 | 51.0981 | 51.2437 | 51.2377 | -70.4536 | 0.036209 | -0.035599 | 1.8666 | 1.2178 | 1.1816 | -0.11342 | -0.11735 | -0.12276 | -0.20805 | 0.16771 | 0.069102 | 0.19186 | -0.062462 | -0.068418 | 121.6014 | 121.5235 | 121.5196 | 47.8604 | -121.6008 | 121.4289 | 121.5745 | 121.5685 | 70.3861 | -121.7597
1506.5781 | 121.9208 | -69.1635 | 52.446 | -0.010149 | -0.035367 | 0.010165 | 0.057504 | -0.0097282 | 0.053035 | -0.021518 | -0.0022666 | -0.0031451 | 0.059542 | 0.035987 | 0.050679 | -67.2234 | -21.9209 | -67.886 | 52.4792 | 52.3878 | 52.3884 | -69.0766 | -68.9681 | 0.064461 | -69.0667 | 52.2977 | 52.4479 | 52.4373 | -69.2493 | 0.086905 | 0.033263 | 1.9401 | 1.2775 | 1.1906 | -0.058149 | -0.057585 | -0.08583 | -0.14832 | 0.19545 | 0.096847 | 0.18268 | 0.001879 | -0.008656 | 121.6428 | 121.5513 | 121.5519 | 47.2426 | -121.5226 | 121.4612 | 121.6114 | 121.6008 | 69.228 | -121.6953
1508.3438 | 121.9162 | -69.6991 | 51.8921 | 0.0051128 | -0.035367 | 0.0097374 | 0.057718 | -0.0097282 | 0.053249 | -0.013887 | -0.0018394 | -0.0033587 | 0.059328 | 0.035987 | 0.050892 | -67.6538 | -22.1911 | -68.3484 | 51.971 | 51.8842 | 51.8848 | -69.5894 | -69.4717 | 0.064461 | -69.5703 | 51.7895 | 51.9351 | 51.9337 | -69.7622 | 0.10965 | 0.078956 | 2.0453 | 1.3507 | 1.241 | -0.007937 | -0.007337 | -0.063073 | -0.10264 | 0.22738 | 0.12877 | 0.19185 | 0.042969 | 0.041592 | 121.6701 | 121.5832 | 121.5838 | 47.508 | -121.4815 | 121.4886 | 121.6342 | 121.6328 | 69.7636 | -121.6543
1510.0938 | 121.8979 | -69.9326 | 51.6541 | -0.01778 | -0.035154 | 0.009951 | 0.057718 | -0.0099418 | 0.053463 | -0.013887 | -0.0022666 | -0.0029313 | 0.059328 | 0.035987 | 0.051106 | -68.0201 | -22.2827 | -68.7467 | 51.5178 | 51.44 | 51.4406 | -70.0336 | -69.9113 | 0.055303 | -70.0145 | 51.3499 | 51.4864 | 51.4896 | -70.2017 | -0.10105 | -0.13627 | 1.9125 | 1.1858 | 1.2869 | -0.21406 | -0.21342 | -0.26918 | -0.30413 | 0.021283 | -0.081903 | 0.18728 | -0.1677 | -0.1645 | 121.4503 | 121.3726 | 121.3732 | 47.6499 | -121.6877 | 121.2825 | 121.4189 | 121.4221 | 69.9879 | -121.8558
1511.7812 | 121.843 | -68.6188 | 53.0273 | -0.010149 | -0.035154 | 0.009951 | 0.057504 | -0.0090872 | 0.053463 | -0.021518 | -0.0024804 | -0.0031451 | 0.059542 | 0.036414 | 0.050892 | -66.3673 | -21.4631 | -67.1123 | 53.1385 | 53.0564 | 53.0523 | -68.431 | -68.3087 | 0.064461 | -68.3936 | 52.9524 | 53.1072 | 53.1058 | -68.5854 | 0.18779 | 0.11119 | 2.2515 | 1.5065 | 1.3187 | 0.029014 | 0.024953 | 0.03336 | -0.074952 | 0.31005 | 0.22518 | 0.19182 | 0.079837 | 0.07846 | 121.7573 | 121.6751 | 121.6711 | 47.1557 | -121.4583 | 121.5712 | 121.726 | 121.7246 | 68.6832 | -121.6128
1513.5312 | 121.8979 | -67.2546 | 54.3137 | -0.010149 | -0.035367 | 0.0097374 | 0.057932 | -0.0095144 | 0.053463 | -0.021518 | -0.0022666 | -0.0031451 | 0.059328 | 0.035987 | 0.050679 | -65.3417 | -21.0098 | -66.1142 | 54.0908 | 54.0042 | 54.0001 | -67.4602 | -67.3609 | 0.078197 | -67.4504 | 53.9139 | 54.0687 | 54.0582 | -67.6284 | -0.20561 | -0.22282 | 1.9129 | 1.1404 | 1.346 | -0.30946 | -0.31359 | -0.3738 | -0.39978 | -0.10629 | -0.19574 | 0.17806 | -0.24497 | -0.25551 | 121.3455 | 121.2588 | 121.2547 | 46.2448 | -121.7739 | 121.1685 | 121.3233 | 121.3128 | 67.3328 | -121.9421
1515.2812 | 122.0078 | -83.6792 | 37.8845 | -0.010149 | -0.035367 | 0.0097374 | 0.057718 | -0.0088734 | 0.053676 | -0.021518 | -0.002694 | -0.0031451 | 0.059542 | 0.0362 | 0.05132 | -76.0322 | -26.4309 | -76.8228 | 43.1897 | 43.0514 | 43.1579 | -78.4588 | -78.2674 | -0.21026 | -78.4027 | 42.9438 | 43.135 | 43.0512 | -78.6176 | 5.2204 | 5.3052 | 7.647 | 6.8564 | 1.636 | 5.1669 | 5.2734 | 5.0616 | 5.0593 | 5.4118 | 5.2765 | 0.21495 | 5.2505 | 5.1667 | 126.8689 | 126.7306 | 126.8371 | 57.2483 | -116.3433 | 126.623 | 126.8142 | 126.7304 | 83.4689 | -116.5021
1516.9688 | 121.7743 | -82.0908 | 39.6103 | -0.010149 | -0.035581 | 0.0095236 | 0.057504 | -0.0093008 | 0.05389 | -0.013887 | -0.002694 | -0.0031451 | 0.058901 | 0.035987 | 0.051106 | -84.2825 | -30.6752 | -85.2468 | 34.6327 | 34.5896 | 34.6097 | -86.9756 | -86.6785 | 0.10567 | -86.7771 | 34.4873 | 34.6096 | 34.6632 | -87.0701 | -4.8849 | -4.9776 | -2.1917 | -3.1561 | 1.7288 | -5.0207 | -5.0006 | -4.9793 | -5.123 | -4.5877 | -4.6864 | 0.29298 | -5.0007 | -4.9471 | 116.7235 | 116.6803 | 116.7004 | 51.4155 | -126.5859 | 116.5781 | 116.7004 | 116.754 | 82.1964 | -126.6804
1518.7188 | 121.8201 | -53.4531 | 68.0649 | -0.010149 | -0.035154 | 0.010378 | 0.057718 | -0.0097282 | 0.052822 | -0.021518 | -0.0022666 | -0.0027177 | 0.059114 | 0.0362 | 0.050465 | -51.4692 | -13.8763 | -52.2237 | 68.0595 | 67.9379 | 67.9282 | -53.5312 | -53.4737 | 0.16061 | -53.5723 | 67.7867 | 67.9602 | 68.0092 | -53.6493 | -0.078095 | -0.005379 | 1.9839 | 1.2294 | 1.3075 | -0.12702 | -0.1367 | -0.19625 | -0.27816 | -0.020641 | -0.11925 | 0.077 | -0.10471 | -0.055725 | 121.5126 | 121.3909 | 121.3812 | 39.5767 | -121.596 | 121.2398 | 121.4132 | 121.4622 | 53.6137 | -121.7142
1520.4688 | 121.6736 | -64.2517 | 57.1243 | -0.010149 | -0.035367 | 0.010165 | 0.057504 | -0.0093008 | 0.053463 | -0.013887 | -0.0022666 | -0.0029313 | 0.058901 | 0.035773 | 0.050892 | -60.8503 | -18.8304 | -61.7465 | 58.2389 | 58.1893 | 58.13 | -63.2339 | -63.0569 | 0.27508 | -63.1601 | 58.0712 | 58.2077 | 58.2888 | -63.3015 | 1.0178 | 1.1145 | 3.4014 | 2.5052 | 1.4874 | 1.065 | 1.0056 | 0.95025 | 0.94682 | 1.1948 | 1.0916 | 0.14133 | 1.0834 | 1.1645 | 122.4906 | 122.441 | 122.3817 | 45.4213 | -120.3582 | 122.3229 | 122.4595 | 122.5405 | 64.5268 | -120.4258
1522.2188 | 121.4813 | -61.4685 | 60.3378 | -0.010149 | -0.035154 | 0.010592 | 0.058145 | -0.0093008 | 0.053249 | -0.013887 | -0.0022666 | -0.0029313 | 0.058901 | 0.0362 | 0.050679 | -63.1166 | -19.8789 | -64.0173 | 55.7345 | 55.7213 | 55.685 | -65.6378 | -65.4608 | 0.2705 | -65.5502 | 55.6033 | 55.7445 | 55.8163 | -65.7053 | -4.1693 | -4.6033 | -1.6481 | -2.5488 | 1.6205 | -4.6165 | -4.6528 | -4.2368 | -4.7345 | -3.9923 | -4.0817 | 0.15512 | -4.5934 | -4.5215 | 117.203 | 117.1898 | 117.1535 | 41.5896 | -125.9757 | 117.0718 | 117.213 | 117.2848 | 61.739 | -126.0432
1523.9062 | 121.5546 | -60.7315 | 60.5118 | -0.010149 | -0.035154 | 0.010592 | 0.057932 | -0.0095144 | 0.053676 | -0.013887 | -0.002053 | -0.0027177 | 0.058901 | 0.035987 | 0.050679 | -57.6546 | -16.7334 | -58.5371 | 61.137 | 61.0374 | 61.074 | -60.1752 | -60.0533 | 0.091933 | -60.1473 | 60.9373 | 61.0923 | 61.0955 | -60.2749 | 0.55633 | 0.6252 | 3.0769 | 2.1944 | 1.638 | 0.52564 | 0.56223 | 0.45665 | 0.42551 | 0.6782 | 0.58417 | 0.12752 | 0.58048 | 0.58368 | 121.8685 | 121.7689 | 121.8055 | 43.9981 | -120.687 | 121.6688 | 121.8238 | 121.827 | 60.8234 | -120.7866
1525.6406 | 121.5591 | -65.0803 | 56.0349 | -0.0025182 | -0.035367 | 0.010592 | 0.057718 | -0.0090872 | 0.05389 | -0.021518 | -0.0022666 | -0.0029313 | 0.058687 | 0.036414 | 0.050465 | -62.6405 | -19.4119 | -63.5549 | 55.9359 | 55.7854 | 55.8681 | -65.4089 | -65.2822 | -0.16448 | -65.39 | 55.6262 | 55.8269 | 55.798 | -65.5313 | -0.32863 | -0.098921 | 2.4398 | 1.5253 | 1.8539 | -0.24945 | -0.16671 | -0.45108 | -0.40862 | -0.20194 | -0.3097 | 0.14138 | -0.20798 | -0.23683 | 121.0162 | 120.8657 | 120.9484 | 45.6684 | -121.4437 | 120.7065 | 120.9071 | 120.8783 | 64.9158 | -121.5662
1527.3281 | 121.5591 | -69.7952 | 51.3474 | -0.025411 | -0.035581 | 0.010806 | 0.057932 | -0.0093008 | 0.05389 | -0.013887 | -0.0024804 | -0.0031451 | 0.058901 | 0.0362 | 0.050679 | -62.2147 | -19.2837 | -63.1841 | 56.2564 | 56.0876 | 56.1749 | -65.1067 | -64.98 | -0.086637 | -65.074 | 55.9421 | 56.1428 | 56.1002 | -65.2246 | 4.6885 | 4.9091 | 7.5806 | 6.6111 | 1.9226 | 4.7403 | 4.8276 | 4.5707 | 4.5948 | 4.8152 | 4.7212 | 0.15053 | 4.7954 | 4.7529 | 126.0516 | 125.8828 | 125.9701 | 50.5116 | -116.454 | 125.7374 | 125.938 | 125.8954 | 69.7086 | -116.5719
1529.0781 | 121.5363 | -62.1231 | 59.0286 | -0.010149 | -0.03494 | 0.011019 | 0.057932 | -0.0093008 | 0.054104 | -0.013887 | -0.002053 | -0.0025041 | 0.058687 | 0.0362 | 0.050465 | -58.3001 | -17.0768 | -59.32 | 60.0427 | 59.9339 | 59.9751 | -61.2146 | -61.0789 | 0.050725 | -61.1913 | 59.8064 | 59.9797 | 59.9783 | -61.3097 | 0.90851 | 1.0141 | 3.823 | 2.8031 | 1.8946 | 0.90528 | 0.94652 | 0.81343 | 0.77777 | 1.0442 | 0.93182 | 0.11839 | 0.95104 | 0.94966 | 122.1659 | 122.057 | 122.0983 | 45.0463 | -120.2432 | 121.9295 | 122.1028 | 122.1014 | 62.1738 | -120.3383
1530.8125 | 121.4035 | -60.1685 | 60.9695 | -0.010149 | -0.035154 | 0.010592 | 0.058359 | -0.0088734 | 0.05389 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058473 | 0.035987 | 0.050679 | -57.0411 | -16.0878 | -58.1251 | 61.1324 | 61.0786 | 61.0465 | -60.0515 | -59.9114 | 0.15604 | -60.0054 | 60.919 | 61.0877 | 61.1504 | -60.1329 | 0.11691 | 0.16286 | 3.1274 | 2.0434 | 1.9264 | 0.10909 | 0.076994 | 0.035539 | -0.050569 | 0.25709 | 0.16306 | 0.12752 | 0.11814 | 0.18087 | 121.3009 | 121.2471 | 121.215 | 44.0807 | -121.0211 | 121.0874 | 121.2561 | 121.3189 | 60.3245 | -121.1025
1532.5 | 121.5317 | -0.56763 | 120.8908 | -0.010149 | -0.034726 | 0.012301 | 0.059427 | -0.0097282 | 0.051967 | -0.013887 | -0.0018394 | -0.0022903 | 0.059328 | 0.0362 | 0.04961 | 1.3975 | 15.2848 | 0.60508 | 120.7751 | 120.5451 | 120.4585 | -0.59421 | -0.4614 | 0.59559 | -0.58748 | 120.3616 | 120.6736 | 120.6539 | -0.66324 | -0.026586 | -0.11575 | 1.9651 | 1.1727 | 1.1993 | -0.34568 | -0.43233 | -0.095613 | -0.52923 | 0.10623 | -0.019854 | 0.075759 | -0.21719 | -0.23688 | 121.3427 | 121.1128 | 121.0261 | 15.8524 | -121.485 | 120.9292 | 121.2412 | 121.2216 | 1.1632 | -121.554
1534.25 | 121.6919 | -0.51727 | 121.0373 | -0.01778 | -0.034299 | 0.012301 | 0.059641 | -0.0097282 | 0.052181 | -0.021518 | -0.0018394 | -0.0020767 | 0.059114 | 0.036414 | 0.049824 | 1.576 | 15.6373 | 0.75158 | 121.0131 | 120.7878 | 120.7057 | -0.51179 | -0.37899 | 0.46739 | -0.50049 | 120.6088 | 120.9254 | 120.8737 | -0.58082 | 0.005481 | -0.024157 | 2.0933 | 1.2689 | 1.2634 | -0.24948 | -0.33156 | -0.063548 | -0.42848 | 0.13829 | 0.016787 | 0.080335 | -0.11185 | -0.16359 | 121.5304 | 121.3051 | 121.223 | 16.1546 | -121.5491 | 121.1261 | 121.4427 | 121.391 | 0.98466 | -121.6181
1535.9375 | 121.6095 | -0.65002 | 121.019 | -0.010149 | -0.034085 | 0.012943 | 0.059427 | -0.0097282 | 0.052394 | -0.021518 | -0.0018394 | -0.0022903 | 0.059542 | 0.0362 | 0.050038 | 1.6172 | 15.9212 | 0.73785 | 120.9765 | 120.7512 | 120.6737 | -0.58505 | -0.4614 | 0.41244 | -0.58748 | 120.5768 | 120.8888 | 120.8417 | -0.65866 | 0.064969 | -0.042474 | 2.2672 | 1.3879 | 1.3229 | -0.2678 | -0.3453 | -0.008637 | -0.44222 | 0.18862 | 0.062543 | 0.07118 | -0.13017 | -0.17733 | 121.6265 | 121.4012 | 121.3237 | 16.5712 | -121.604 | 121.2268 | 121.5388 | 121.4917 | 1.0625 | -121.6776
1537.625 | 121.637 | -0.6546 | 121.0236 | -0.010149 | -0.034513 | 0.013584 | 0.060069 | -0.010155 | 0.052181 | -0.029148 | -0.002053 | -0.0022903 | 0.059114 | 0.036414 | 0.050038 | 1.7042 | 16.3104 | 0.78821 | 120.9994 | 120.7741 | 120.692 | -0.60337 | -0.47056 | 0.40329 | -0.59206 | 120.5859 | 120.9025 | 120.8645 | -0.65866 | 0.051232 | -0.02416 | 2.3588 | 1.4428 | 1.3916 | -0.24949 | -0.33157 | -0.004059 | -0.43764 | 0.18404 | 0.062542 | 0.066601 | -0.12101 | -0.15902 | 121.654 | 121.4287 | 121.3466 | 16.965 | -121.6269 | 121.2405 | 121.5572 | 121.5191 | 1.0579 | -121.6822
1539.3906 | 121.7697 | -0.65918 | 120.9549 | -0.010149 | -0.034299 | 0.019994 | 0.059641 | -0.0095144 | 0.052608 | -0.013887 | -0.0016258 | -0.0018631 | 0.059328 | 0.035987 | 0.050251 | 1.7912 | 16.9789 | 0.83857 | 120.9674 | 120.742 | 120.6645 | -0.65374 | -0.51635 | 0.38039 | -0.64701 | 120.5585 | 120.8751 | 120.8233 | -0.71361 | 0.005441 | 0.012456 | 2.4504 | 1.4978 | 1.4923 | -0.21287 | -0.29037 | -0.054427 | -0.39644 | 0.14283 | 0.012175 | 0.066602 | -0.079818 | -0.13156 | 121.6265 | 121.4012 | 121.3237 | 17.638 | -121.6086 | 121.2176 | 121.5343 | 121.4825 | 1.0396 | -121.6685
1541.1406 | 121.8292 | -5.7495 | 115.6952 | -0.010149 | -0.033872 | 0.3341 | 0.059427 | -0.0093008 | 0.053035 | -0.0062567 | -0.002053 | -0.0027177 | 0.059542 | 0.0362 | 0.050465 | -3.1168 | 16.2738 | -4.2296 | 115.5008 | 115.2885 | 115.2206 | -6.0843 | -5.9696 | 0.31629 | -6.1048 | 115.1925 | 115.4494 | 115.4068 | -6.1578 | -0.33483 | -0.19443 | 2.6327 | 1.5199 | 1.8548 | -0.40667 | -0.47463 | -0.40831 | -0.50273 | -0.22008 | -0.35532 | 0.052993 | -0.24576 | -0.28834 | 121.2503 | 121.038 | 120.9701 | 22.0233 | -121.7795 | 120.942 | 121.1989 | 121.1564 | 6.0658 | -121.853
1542.8438 | 121.8155 | -7.37 | 114.1708 | -0.010149 | -0.033872 | 0.21401 | 0.059427 | -0.0093008 | 0.053035 | -0.013887 | -0.002053 | -0.0022903 | 0.059542 | 0.035987 | 0.050038 | -0.52089 | 18.9706 | -1.6795 | 117.9365 | 117.697 | 117.6518 | -3.7033 | -3.5932 | 0.22929 | -3.7239 | 117.5733 | 117.8349 | 117.7694 | -3.818 | 3.6667 | 3.7656 | 6.8491 | 5.6905 | 2.0238 | 3.5262 | 3.481 | 3.552 | 3.4024 | 3.7768 | 3.6461 | 0.094147 | 3.664 | 3.5986 | 125.3065 | 125.067 | 125.0218 | 26.3406 | -117.8741 | 124.9433 | 125.2049 | 125.1394 | 7.5993 | -117.9889
1544.6094 | 121.6782 | -1.3962 | 120.2499 | -0.010149 | -0.033872 | 0.20162 | 0.059427 | -0.0088734 | 0.053463 | -0.0062567 | -0.002053 | -0.0018631 | 0.058901 | 0.035987 | 0.050038 | 1.8553 | 21.4201 | 0.59592 | 119.6762 | 119.492 | 119.3505 | -1.8168 | -1.7068 | 0.41244 | -1.8375 | 119.3772 | 119.6022 | 119.6329 | -1.9453 | -0.42061 | -0.57369 | 3.2515 | 1.9921 | 2.4127 | -0.75796 | -0.89948 | -0.54913 | -0.87274 | -0.31063 | -0.44129 | 0.10784 | -0.64771 | -0.61704 | 121.0724 | 120.8882 | 120.7466 | 22.8163 | -122.0667 | 120.7734 | 120.9984 | 121.0291 | 1.8086 | -122.1952
1546.3438 | 121.7422 | -1.7532 | 119.8654 | -0.010149 | -0.033872 | 0.16786 | 0.059641 | -0.0090872 | 0.053676 | -0.0062567 | -0.0018394 | -0.0022903 | 0.059114 | 0.0362 | 0.049824 | 1.9469 | 20.6646 | 0.69665 | 119.9647 | 119.7438 | 119.6526 | -1.6382 | -1.5099 | 0.35292 | -1.636 | 119.629 | 119.8769 | 119.8527 | -1.753 | 0.11503 | 0.099267 | 3.7001 | 2.4499 | 2.3349 | -0.1216 | -0.21277 | 0.000237 | -0.2364 | 0.24331 | 0.11723 | 0.11699 | 0.011525 | -0.012745 | 121.7179 | 121.4971 | 121.4059 | 22.4179 | -121.5036 | 121.3823 | 121.6302 | 121.6059 | 2.1062 | -121.6184
1548.0938 | 121.6141 | -8.812 | 113.8321 | -0.025411 | -0.033444 | 1.1957 | 0.059427 | -0.0088734 | 0.054104 | -0.021518 | -0.0016258 | -0.0022903 | 0.059114 | 0.0362 | 0.050038 | -5.5388 | 17.1803 | -7.2741 | 111.6091 | 111.401 | 111.3333 | -9.7887 | -9.7058 | 0.2934 | -9.896 | 111.406 | 111.6492 | 111.6158 | -9.8712 | -0.97674 | -2.223 | 3.2731 | 1.5378 | 2.5146 | -2.4311 | -2.4988 | -1.0593 | -2.4261 | -0.89387 | -1.084 | -0.024758 | -2.1829 | -2.2163 | 120.4211 | 120.213 | 120.1453 | 25.9923 | -123.6208 | 120.218 | 120.4611 | 120.4277 | 9.1053 | -123.7033
1549.7812 | 121.6599 | -12.0895 | 109.4421 | -0.010149 | -0.033017 | 1.5984 | 0.059427 | -0.0082324 | 0.054531 | -0.0062567 | -0.002053 | -0.0025041 | 0.059328 | 0.035987 | 0.050038 | -6.2164 | 17.8305 | -7.4252 | 110.5195 | 110.2975 | 110.2619 | -10.8144 | -10.7269 | 0.28424 | -10.9079 | 110.3484 | 110.5778 | 110.5718 | -10.8832 | 1.2752 | 1.0773 | 5.8731 | 4.6643 | 3.3891 | 0.85535 | 0.8198 | 1.2064 | 0.90627 | 1.3627 | 1.1816 | -0.024733 | 1.1357 | 1.1297 | 122.609 | 122.387 | 122.3515 | 29.92 | -120.2565 | 122.4379 | 122.6673 | 122.6614 | 12.3738 | -120.3253
1551.5156 | 121.6507 | -1.7258 | 119.7922 | -0.01778 | -0.033444 | 0.4497 | 0.059427 | -0.0084462 | 0.054745 | -0.029148 | -0.0018394 | -0.0020767 | 0.058901 | 0.035987 | 0.050038 | 1.956 | 23.7048 | -0.14576 | 118.6507 | 118.448 | 118.3523 | -2.8333 | -2.7004 | 0.40329 | -2.8265 | 118.3608 | 118.5995 | 118.5844 | -2.9114 | -1.1075 | -1.1415 | 3.6818 | 1.58 | 2.6875 | -1.3442 | -1.4398 | -1.1857 | -1.4314 | -0.97462 | -1.1007 | 0.084968 | -1.1927 | -1.2078 | 120.3765 | 120.1737 | 120.0781 | 25.4306 | -122.6255 | 120.0865 | 120.3253 | 120.3102 | 2.1291 | -122.7036
1553.2656 | 121.6049 | -0.5127 | 121.1288 | -0.0025182 | -0.033444 | 0.25226 | 0.06071 | -0.0084462 | 0.054104 | -0.021518 | -0.0022666 | -0.0025041 | 0.059114 | 0.0362 | 0.050251 | 2.7664 | 24.2955 | 0.95761 | 119.6625 | 119.4874 | 119.3459 | -1.8351 | -1.6793 | 0.41702 | -1.8283 | 119.3772 | 119.5931 | 119.6329 | -1.9087 | -1.3224 | -1.4663 | 3.2791 | 1.4703 | 2.7927 | -1.6414 | -1.783 | -1.396 | -1.7516 | -1.1666 | -1.3156 | 0.080366 | -1.5358 | -1.4959 | 120.1752 | 120.0001 | 119.8586 | 24.8082 | -122.9639 | 119.8899 | 120.1058 | 120.1456 | 0.92972 | -123.0375
1554.9688 | 121.6232 | -0.48981 | 121.1655 | -0.010149 | -0.033444 | 0.035379 | 0.062205 | -0.0090872 | 0.05389 | -0.029148 | -0.0022666 | -0.0020767 | 0.059542 | 0.0362 | 0.050251 | 3.3204 | 20.248 | 1.855 | 121.1413 | 120.9206 | 120.8339 | -0.47058 | -0.32862 | 0.34834 | -0.45012 | 120.7782 | 121.0399 | 121.0065 | -0.56708 | 0.019225 | -0.024136 | 3.8102 | 2.3448 | 2.3255 | -0.24487 | -0.33154 | -0.077278 | -0.38725 | 0.16119 | 0.039687 | 0.11696 | -0.12556 | -0.15899 | 121.6311 | 121.4104 | 121.3237 | 20.7378 | -121.636 | 121.268 | 121.5297 | 121.4963 | 0.83815 | -121.7326
1556.7188 | 121.6461 | -0.62256 | 121.0236 | -0.010149 | -0.033444 | 0.039225 | 0.061992 | -0.0090872 | 0.05389 | -0.029148 | -0.0016258 | -0.0020767 | 0.059114 | 0.0362 | 0.050251 | 3.3753 | 20.1152 | 1.855 | 121.0772 | 120.8611 | 120.7836 | -0.54384 | -0.42019 | 0.33918 | -0.53712 | 120.7324 | 120.9758 | 120.947 | -0.65866 | 0.078715 | 0.053672 | 3.9979 | 2.4775 | 2.3988 | -0.16249 | -0.24 | -0.036102 | -0.29113 | 0.20236 | 0.085443 | 0.12155 | -0.047754 | -0.076602 | 121.6998 | 121.4836 | 121.4061 | 20.7378 | -121.5674 | 121.355 | 121.5984 | 121.5695 | 0.96174 | -121.6822
1558.4844 | 121.6599 | -0.64545 | 121.0739 | -0.010149 | -0.033444 | 0.13367 | 0.06071 | -0.0080188 | 0.056027 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.035987 | 0.050038 | 5.6187 | 24.4832 | 1.5803 | 120.0242 | 119.8125 | 119.7351 | -1.5878 | -1.455 | 0.34376 | -1.5811 | 119.6931 | 119.9502 | 119.9122 | -1.6843 | -0.94239 | -1.0497 | 6.2642 | 2.2257 | 3.1681 | -1.2614 | -1.3389 | -1.0389 | -1.3808 | -0.80954 | -0.93561 | 0.10325 | -1.1237 | -1.1617 | 120.6697 | 120.4579 | 120.3805 | 25.1286 | -122.6618 | 120.3386 | 120.5956 | 120.5576 | 0.98921 | -122.7582
1560.25 | 121.6278 | -3.9688 | 117.7917 | -0.010149 | -0.033017 | 0.23752 | 0.060496 | -0.0080188 | 0.058163 | -0.013887 | -0.0016258 | -0.0022903 | 0.059755 | 0.0362 | 0.050251 | 7.592 | 25.0464 | 0.51352 | 118.6461 | 118.4022 | 118.3569 | -3.021 | -2.8835 | 0.26592 | -3.005 | 118.2921 | 118.5537 | 118.4837 | -3.1037 | 0.94777 | 0.85436 | 11.5608 | 4.4823 | 3.5346 | 0.61044 | 0.56516 | 0.86506 | 0.50035 | 1.0853 | 0.96377 | 0.098709 | 0.76198 | 0.69192 | 122.6149 | 122.371 | 122.3257 | 29.0152 | -120.8128 | 122.2609 | 122.5225 | 122.4525 | 4.2347 | -120.8955
1561.9531 | 121.6919 | -3.0029 | 118.5974 | -0.010149 | -0.033017 | 0.22598 | 0.060069 | -0.0073778 | 0.058377 | -0.0062567 | -0.002053 | -0.0018631 | 0.059114 | 0.035773 | 0.050038 | 9.4188 | 27.1937 | 1.4383 | 119.2047 | 118.9837 | 118.9109 | -2.4258 | -2.2837 | 0.30713 | -2.4098 | 118.8736 | 119.1215 | 119.0835 | -2.5039 | 0.57715 | 0.60726 | 12.4217 | 4.4413 | 3.8641 | 0.3863 | 0.3135 | 0.49901 | 0.27615 | 0.7192 | 0.59312 | 0.094116 | 0.52406 | 0.48605 | 122.2076 | 121.9866 | 121.9138 | 30.1967 | -121.0232 | 121.8765 | 122.1244 | 122.0864 | 3.3101 | -121.1013
1563.7031 | 121.7056 | -5.4016 | 116.2125 | -0.0025182 | -0.032803 | 0.49436 | 0.060282 | -0.0080188 | 0.059232 | -0.013887 | -0.0016258 | -0.0020767 | 0.059328 | 0.036628 | 0.050038 | 7.1525 | 23.0089 | -1.5055 | 116.3111 | 116.1036 | 116.031 | -5.251 | -5.1225 | 0.30713 | -5.2623 | 116.0349 | 116.269 | 116.2402 | -5.3199 | 0.15063 | 0.098668 | 12.5541 | 3.8961 | 3.7455 | -0.10889 | -0.18149 | 0.081714 | -0.17756 | 0.27908 | 0.13927 | 0.057553 | 0.05654 | 0.027691 | 121.7127 | 121.5052 | 121.4326 | 28.4105 | -121.4634 | 121.4365 | 121.6706 | 121.6418 | 5.7087 | -121.5324
1565.4688 | 121.6827 | -1.6388 | 120.0348 | -0.0025182 | -0.032803 | 0.28068 | 0.060282 | -0.0067368 | 0.059232 | -0.021518 | -0.0016258 | -0.0022903 | 0.059114 | 0.036414 | 0.050038 | 9.5195 | 24.4557 | 2.0518 | 118.5683 | 118.361 | 118.2928 | -3.0073 | -2.8744 | 0.33918 | -3.005 | 118.2646 | 118.5079 | 118.4791 | -3.0992 | -1.3685 | -1.4665 | 11.1583 | 3.6906 | 5.0591 | -1.6738 | -1.742 | -1.4604 | -1.7702 | -1.2356 | -1.3662 | 0.094131 | -1.5268 | -1.5557 | 120.2071 | 119.9998 | 119.9316 | 26.0945 | -123.0421 | 119.9034 | 120.1467 | 120.1179 | 1.978 | -123.134
1567.2188 | 121.6599 | -16.713 | 104.6539 | -0.010149 | -0.032162 | 2.4899 | 0.060923 | -0.0067368 | 0.061796 | -0.0062567 | -0.002053 | -0.0020767 | 0.059328 | 0.036414 | 0.050251 | 2.0384 | 14.8132 | -9.751 | 106.1975 | 106.0299 | 105.9947 | -15.0316 | -15.0125 | 0.21556 | -15.1753 | 106.1408 | 106.3655 | 106.3778 | -15.0865 | 1.6814 | 1.5435 | 18.7514 | 6.962 | 5.2806 | 1.376 | 1.3407 | 1.6264 | 1.4868 | 1.7004 | 1.5377 | -0.088737 | 1.7116 | 1.7239 | 122.9104 | 122.7429 | 122.7076 | 31.5261 | -119.6855 | 122.8537 | 123.0784 | 123.0908 | 16.9285 | -119.7404
1568.9688 | 121.6873 | -3.2043 | 118.4052 | 0.0051128 | -0.03259 | 0.044567 | 0.45389 | -0.0069506 | 0.060941 | -0.021518 | -0.0014122 | -0.0025041 | 0.059328 | 0.036414 | 0.049824 | 13.2601 | 26.1544 | 2.6333 | 119.0307 | 118.8189 | 118.7461 | -2.5265 | -2.389 | 0.2934 | -2.5197 | 118.7316 | 118.9841 | 118.9278 | -2.6092 | 0.67783 | 0.62554 | 16.4644 | 5.8376 | 5.1598 | 0.41372 | 0.34094 | 0.59511 | 0.32648 | 0.81531 | 0.68465 | 0.08954 | 0.57896 | 0.52264 | 122.235 | 122.0232 | 121.9504 | 29.3587 | -120.9317 | 121.936 | 122.1885 | 122.1321 | 3.4977 | -121.0144
1570.6562 | 121.6278 | -5.7999 | 115.741 | -0.010149 | -0.032803 | 0.045635 | 0.91053 | -0.0060958 | 0.062437 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.0362 | 0.050038 | 12.848 | 25.1013 | 0.72869 | 116.3935 | 116.186 | 116.1134 | -5.0449 | -4.9485 | 0.28882 | -5.0838 | 116.1494 | 116.3972 | 116.3592 | -5.1459 | 0.75494 | 0.65257 | 18.6479 | 6.5286 | 5.7736 | 0.44502 | 0.37242 | 0.65396 | 0.40839 | 0.85133 | 0.71609 | 0.062127 | 0.65624 | 0.61823 | 122.1934 | 121.9859 | 121.9133 | 30.9012 | -120.7859 | 121.9492 | 122.1971 | 122.1591 | 6.0887 | -120.8869
1572.4062 | 121.6507 | -9.1461 | 112.1933 | -0.01778 | -0.032803 | 0.04649 | 1.1753 | -0.0054548 | 0.063291 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.0362 | 0.050038 | 13.7087 | 22.3496 | 0.33038 | 114.9422 | 114.7436 | 114.6528 | -6.4369 | -6.3496 | 0.22472 | -6.4894 | 114.7117 | 114.9504 | 114.9261 | -6.5287 | 2.7092 | 2.7489 | 22.8549 | 9.4765 | 6.7673 | 2.5503 | 2.4595 | 2.6174 | 2.5184 | 2.7965 | 2.6567 | 0.039267 | 2.7571 | 2.7328 | 124.0883 | 123.8897 | 123.7989 | 31.4957 | -118.6302 | 123.8578 | 124.0965 | 124.0722 | 9.3708 | -118.722
1574.1719 | 121.5775 | -1.6708 | 119.9295 | -0.01778 | -0.03259 | 0.10675 | 0.31157 | -0.0050276 | 0.06436 | -0.021518 | -0.002053 | -0.0027177 | 0.059114 | 0.0362 | 0.050038 | 19.2806 | 26.5939 | 5.046 | 119.4702 | 119.2676 | 119.1765 | -2.0137 | -1.8854 | 0.34834 | -2.0252 | 119.1574 | 119.4008 | 119.3948 | -2.1193 | -0.34284 | -0.45929 | 20.9515 | 6.7168 | 7.0597 | -0.6619 | -0.75303 | -0.44847 | -0.77207 | -0.21454 | -0.35436 | 0.094108 | -0.52874 | -0.53469 | 121.1411 | 120.9384 | 120.8473 | 28.2648 | -121.9432 | 120.8283 | 121.0716 | 121.0656 | 2.0192 | -122.0488
1575.8594 | 121.6415 | -1.3367 | 120.2911 | -0.025411 | -0.033017 | 0.059311 | 0.21307 | -0.0046002 | 0.067137 | -0.021518 | -0.0018394 | -0.0020767 | 0.059542 | 0.0362 | 0.050038 | 24.1704 | 27.5921 | 6.5523 | 120.2989 | 120.0781 | 120.0098 | -1.3085 | -1.1528 | 0.31171 | -1.2651 | 119.9541 | 120.2203 | 120.1686 | -1.373 | 0.028145 | 0.007768 | 25.507 | 7.8889 | 7.8608 | -0.21306 | -0.28136 | -0.036287 | -0.33705 | 0.18388 | 0.07154 | 0.10783 | -0.070801 | -0.12254 | 121.6356 | 121.4147 | 121.3465 | 28.9287 | -121.5997 | 121.2908 | 121.557 | 121.5053 | 1.6484 | -121.6641
1577.6094 | 121.7194 | -1.0712 | 120.6482 | -0.025411 | -0.03259 | 0.15525 | 0.75283 | -0.0039592 | 0.067778 | -0.0062567 | -0.0016258 | -0.0020767 | 0.058901 | 0.0362 | 0.050038 | 21.6614 | 23.3798 | 3.3108 | 116.128 | 115.9525 | 115.8661 | -5.338 | -5.2049 | 0.36208 | -5.3539 | 115.8792 | 116.1179 | 116.1165 | -5.3977 | -4.2668 | -4.5202 | 22.7326 | 4.382 | 8.6488 | -4.6957 | -4.782 | -4.3266 | -4.769 | -4.1338 | -4.2828 | 0.043819 | -4.5303 | -4.5317 | 117.1992 | 117.0236 | 116.9373 | 24.4509 | -125.9862 | 116.9504 | 117.1891 | 117.1877 | 1.4332 | -126.0459
1579.3594 | 121.701 | -9.7458 | 111.7355 | -0.010149 | -0.032376 | 0.2544 | 1.1659 | -0.0037456 | 0.06906 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.036841 | 0.049824 | 20.7686 | 19.4834 | 0.454 | 112.7583 | 112.5412 | 112.4871 | -8.6669 | -8.5703 | 0.21098 | -8.7238 | 112.5461 | 112.803 | 112.7375 | -8.7311 | 1.0789 | 1.0228 | 30.5144 | 10.1998 | 9.1209 | 0.80563 | 0.7516 | 1.0147 | 0.81055 | 1.1755 | 1.0219 | 0.007267 | 1.0675 | 1.002 | 122.5041 | 122.287 | 122.2329 | 29.2291 | -120.4024 | 122.2919 | 122.5488 | 122.4833 | 9.9568 | -120.4667
1581.1094 | 121.5866 | -12.8448 | 108.4396 | -0.010149 | -0.032162 | 0.4997 | 1.4345 | -0.0037456 | 0.071197 | -0.029148 | -0.0018394 | -0.0022903 | 0.058687 | 0.036414 | 0.050038 | 22.6732 | 16.5393 | -1.3224 | 110.8262 | 110.6089 | 110.5733 | -10.4664 | -10.4109 | 0.14688 | -10.5736 | 110.646 | 110.8983 | 110.8603 | -10.5535 | 2.3785 | 2.3866 | 35.5181 | 11.5225 | 9.144 | 2.1692 | 2.1336 | 2.2914 | 2.2064 | 2.4339 | 2.2712 | -0.020163 | 2.4587 | 2.4207 | 123.6711 | 123.4537 | 123.4181 | 29.3842 | -118.906 | 123.4909 | 123.7432 | 123.7051 | 12.9917 | -118.9931
1582.7969 | 121.5088 | -13.5132 | 107.9407 | -0.01778 | -0.032803 | 1.2029 | 1.976 | -0.0031046 | 0.073547 | -0.013887 | -0.0018394 | -0.0027177 | 0.058901 | 0.036414 | 0.050038 | 22.9846 | 14.2775 | -4.5409 | 106.5088 | 106.3688 | 106.2465 | -14.3585 | -14.3715 | 0.35292 | -14.5251 | 106.5849 | 106.773 | 106.8128 | -14.4455 | -0.84528 | -1.4319 | 36.4977 | 8.9723 | 9.8176 | -1.5719 | -1.6942 | -0.9323 | -1.3558 | -0.85834 | -1.0119 | -0.079594 | -1.1677 | -1.1279 | 120.022 | 119.882 | 119.7597 | 27.7907 | -122.2991 | 120.0981 | 120.2862 | 120.326 | 13.8661 | -122.3862
1584.5469 | 121.3211 | -20.1553 | 100.9094 | -0.0025182 | -0.032162 | 2.8446 | 4.0502 | -0.0011816 | 0.076325 | -0.013887 | -0.002053 | -0.0027177 | 0.058901 | 0.036414 | 0.050251 | 14.4962 | 3.2522 | -15.2953 | 92.9018 | 92.7694 | 92.6664 | -27.3168 | -27.3339 | 0.31171 | -27.4782 | 93.4721 | 93.6507 | 93.7317 | -27.3669 | -7.1615 | -8.0076 | 34.6516 | 4.86 | 12.0215 | -8.1401 | -8.2431 | -7.2116 | -7.4373 | -7.1785 | -7.3229 | -0.11134 | -7.2587 | -7.1777 | 113.0572 | 112.9247 | 112.8217 | 23.4075 | -128.2262 | 113.6274 | 113.806 | 113.8871 | 20.467 | -128.2763
1586.2969 | 121.1426 | -17.3264 | 103.6606 | -0.01778 | -0.032376 | 1.2897 | 4.1831 | -0.00096797 | 0.07953 | -0.013887 | -0.002053 | -0.0025041 | 0.058687 | 0.036414 | 0.04961 | 29.083 | 12.7986 | -5.3055 | 102.8415 | 102.6873 | 102.579 | -17.6232 | -17.6407 | 0.2705 | -17.7989 | 103.1419 | 103.3528 | 103.3926 | -17.6919 | -0.29688 | -0.81907 | 46.4093 | 12.0209 | 12.3178 | -0.97326 | -1.0815 | -0.36551 | -0.51873 | -0.31437 | -0.4725 | -0.10699 | -0.30782 | -0.26799 | 120.1679 | 120.0137 | 119.9054 | 30.125 | -121.2838 | 120.4682 | 120.6791 | 120.719 | 17.5969 | -121.3524
1587.9844 | 121.5088 | -0.19684 | 121.2524 | -0.025411 | -0.03729 | 0.043285 | 0.027161 | -0.010796 | -0.011491 | -0.013887 | -0.002053 | -0.0020767 | 0.058901 | 0.036414 | 0.050251 | -0.021844 | 0.033457 | -0.12745 | 0.1208 | 0.12857 | 0.22438 | -0.17753 | -0.026425 | 0.38039 | -0.1525 | 120.9064 | 121.1498 | 121.1118 | -0.26488 | 0.019308 | -121.1316 | 0.17499 | 0.069393 | 0.050085 | -121.1239 | -121.0281 | -0.068045 | -0.34602 | 0.17041 | 0.044334 | 0.11238 | -0.10265 | -0.14065 | 0.31764 | 0.32541 | 0.42122 | 0.2303 | -121.43 | 121.1033 | 121.3466 | 121.3086 | 0.57723 | -121.5173
1589.7344 | 121.5546 | -0.21515 | 121.3623 | -0.010149 | -0.037718 | 0.042857 | 0.025879 | -0.010796 | -0.011277 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.036414 | 0.04961 | -0.008109 | 0.0243 | -0.12287 | 0.10707 | 0.11025 | 0.20607 | -0.18211 | -0.026425 | 0.34376 | -0.14793 | 120.9751 | 121.2322 | 121.1896 | -0.2603 | 0.03304 | -121.2552 | 0.20704 | 0.092283 | 0.059243 | -121.2521 | -121.1562 | -0.045155 | -0.38721 | 0.18872 | 0.067224 | 0.11238 | -0.1301 | -0.17268 | 0.32222 | 0.3254 | 0.42122 | 0.23945 | -121.5444 | 121.1902 | 121.4474 | 121.4048 | 0.55891 | -121.6226
1591.4219 | 121.6141 | -0.20599 | 121.3898 | 0.0051128 | -0.037718 | 0.042644 | 0.025666 | -0.01101 | -0.011705 | -0.029148 | -0.0018394 | -0.0025041 | 0.059114 | 0.036414 | 0.049824 | -0.012688 | 0.019721 | -0.12745 | 0.097912 | 0.1011 | 0.19233 | -0.19585 | -0.035582 | 0.3346 | -0.14793 | 121.0209 | 121.2551 | 121.2217 | -0.2603 | 0.010148 | -121.2919 | 0.19331 | 0.078549 | 0.068401 | -121.2887 | -121.1974 | -0.05431 | -0.36889 | 0.17041 | 0.058069 | 0.11238 | -0.13467 | -0.1681 | 0.30391 | 0.30709 | 0.39833 | 0.22571 | -121.5856 | 121.2269 | 121.4611 | 121.4277 | 0.5406 | -121.6501
1593.1562 | 121.5958 | -0.22888 | 121.376 | -0.01778 | -0.037077 | 0.042857 | 0.025238 | -0.010796 | -0.011277 | -0.013887 | -0.002053 | -0.0025041 | 0.058901 | 0.036414 | 0.049824 | -0.017266 | 0.019721 | -0.12287 | 0.088755 | 0.1011 | 0.19691 | -0.19127 | -0.040161 | 0.33918 | -0.16166 | 121.0255 | 121.2826 | 121.2446 | -0.26946 | 0.037615 | -121.2873 | 0.21162 | 0.10602 | 0.068401 | -121.2749 | -121.1791 | -0.04058 | -0.35058 | 0.18872 | 0.067221 | 0.1078 | -0.093465 | -0.13147 | 0.31764 | 0.32998 | 0.42579 | 0.2486 | -121.5673 | 121.2543 | 121.5115 | 121.4734 | 0.56807 | -121.6455
1594.9062 | 121.5866 | -0.24261 | 121.4172 | -0.01778 | -0.03729 | 0.043499 | 0.025666 | -0.010796 | -0.011918 | -0.013887 | -0.002053 | -0.0025041 | 0.059328 | 0.036414 | 0.049824 | -0.017266 | 0.0243 | -0.13202 | 0.088755 | 0.091937 | 0.19233 | -0.20958 | -0.040161 | 0.32545 | -0.17082 | 121.0438 | 121.2963 | 121.2583 | -0.27862 | 0.033032 | -121.3285 | 0.22535 | 0.11059 | 0.07756 | -121.3253 | -121.2249 | -0.036004 | -0.37346 | 0.20245 | 0.071796 | 0.1078 | -0.12093 | -0.15893 | 0.33137 | 0.33455 | 0.43495 | 0.26692 | -121.6268 | 121.2864 | 121.5389 | 121.5009 | 0.56806 | -121.6959
1596.6562 | 121.6553 | -0.23346 | 121.376 | -0.0025182 | -0.037718 | 0.043071 | 0.025452 | -0.010369 | -0.011491 | -0.013887 | -0.002053 | -0.0025041 | 0.059328 | 0.036841 | 0.049824 | -0.012688 | 0.019721 | -0.11829 | 0.084176 | 0.091937 | 0.18775 | -0.205 | -0.049318 | 0.33003 | -0.16624 | 121.0529 | 121.31 | 121.272 | -0.27862 | 0.028455 | -121.2919 | 0.22077 | 0.11517 | 0.086716 | -121.2841 | -121.1883 | -0.04516 | -0.32311 | 0.18414 | 0.067219 | 0.11238 | -0.065994 | -0.104 | 0.31764 | 0.3254 | 0.42121 | 0.25318 | -121.581 | 121.2864 | 121.5435 | 121.5055 | 0.56349 | -121.6547
1598.4062 | 121.6278 | -0.25635 | 121.4218 | -0.010149 | -0.037718 | 0.042857 | 0.025452 | -0.01101 | -0.011918 | -0.013887 | -0.0016258 | -0.0022903 | 0.059328 | 0.036628 | 0.049824 | -0.026423 | -0.048958 | -0.13202 | 0.088755 | 0.08278 | 0.18317 | -0.21416 | -0.063054 | 0.32545 | -0.17998 | 121.0621 | 121.3192 | 121.272 | -0.29236 | 0.042186 | -121.3331 | 0.22993 | 0.12433 | 0.082139 | -121.339 | -121.2386 | -0.036008 | -0.35973 | 0.19329 | 0.076372 | 0.11238 | -0.10261 | -0.14978 | 0.3451 | 0.33913 | 0.43952 | 0.20739 | -121.636 | 121.3184 | 121.5756 | 121.5284 | 0.5818 | -121.7142
1600.1562 | 121.6736 | -0.2243 | 121.431 | -0.01778 | -0.037504 | 0.043071 | 0.025666 | -0.010583 | -0.011918 | -0.013887 | -0.0018394 | -0.0020767 | 0.059328 | 0.036628 | 0.049824 | -0.021844 | 0.010564 | -0.12287 | 0.088755 | 0.091937 | 0.1786 | -0.21874 | -0.058476 | 0.32087 | -0.1754 | 121.0667 | 121.3238 | 121.2812 | -0.2832 | 0.005563 | -121.3422 | 0.20246 | 0.10144 | 0.095875 | -121.339 | -121.2524 | -0.058894 | -0.3643 | 0.16583 | 0.048906 | 0.1078 | -0.10719 | -0.14977 | 0.31306 | 0.31624 | 0.4029 | 0.23487 | -121.6497 | 121.291 | 121.5481 | 121.5055 | 0.54517 | -121.7142
1601.8438 | 121.7789 | -0.21973 | 121.376 | -0.01778 | -0.037504 | 0.042857 | 0.025666 | -0.011224 | -0.011491 | -0.021518 | -0.0022666 | -0.0022903 | 0.059114 | 0.036414 | 0.04961 | -0.021844 | -0.003172 | -0.12745 | 0.084176 | 0.08278 | 0.18317 | -0.20958 | -0.067633 | 0.32545 | -0.18913 | 121.0804 | 121.3238 | 121.2858 | -0.30151 | 0.010144 | -121.2919 | 0.19788 | 0.092282 | 0.082138 | -121.2933 | -121.1929 | -0.081786 | -0.29564 | 0.15209 | 0.030593 | 0.11238 | -0.052258 | -0.090264 | 0.3039 | 0.30251 | 0.4029 | 0.21655 | -121.5856 | 121.3001 | 121.5435 | 121.5055 | 0.54517 | -121.6776
1603.5938 | 121.6827 | -0.25635 | 121.4218 | -0.010149 | -0.03729 | 0.043071 | 0.025666 | -0.01101 | -0.011491 | -0.036779 | -0.002053 | -0.0025041 | 0.059328 | 0.036628 | 0.049824 | -0.017266 | -0.012329 | -0.12287 | 0.079598 | 0.087359 | 0.17402 | -0.21874 | -0.063054 | 0.31629 | -0.18455 | 121.085 | 121.3375 | 121.2858 | -0.29693 | 0.037607 | -121.3422 | 0.23908 | 0.13348 | 0.095875 | -121.3345 | -121.2478 | -0.040586 | -0.33683 | 0.19329 | 0.071793 | 0.11238 | -0.084298 | -0.13604 | 0.33595 | 0.34371 | 0.43036 | 0.24402 | -121.6406 | 121.3413 | 121.5939 | 121.5421 | 0.57264 | -121.7187
1605.3594 | 121.756 | -0.2243 | 121.4081 | -0.0025182 | -0.037504 | 0.043071 | 0.025452 | -0.010796 | -0.011491 | -0.021518 | -0.0018394 | -0.0022903 | 0.059114 | 0.036628 | 0.049824 | -0.021844 | -0.048958 | -0.13202 | 0.079598 | 0.091937 | 0.17402 | -0.21416 | -0.072212 | 0.32545 | -0.18455 | 121.0987 | 121.3513 | 121.2995 | -0.29236 | 0.010142 | -121.3285 | 0.20246 | 0.092281 | 0.082139 | -121.3161 | -121.2341 | -0.068052 | -0.30937 | 0.15209 | 0.039749 | 0.1078 | -0.056829 | -0.10857 | 0.3039 | 0.31624 | 0.39832 | 0.17535 | -121.6222 | 121.323 | 121.5756 | 121.5238 | 0.54975 | -121.7004
1607.1094 | 121.6736 | -0.25177 | 121.4584 | -0.010149 | -0.037718 | 0.043071 | 0.025238 | -0.01101 | -0.011705 | -0.021518 | -0.0018394 | -0.0022903 | 0.059328 | 0.036841 | 0.050251 | -0.021844 | -0.044379 | -0.11829 | 0.079598 | 0.091937 | 0.1786 | -0.21416 | -0.058476 | 0.32545 | -0.18455 | 121.0987 | 121.3604 | 121.3178 | -0.28778 | 0.037608 | -121.3788 | 0.22993 | 0.13348 | 0.095874 | -121.3665 | -121.2798 | -0.036007 | -0.35972 | 0.19329 | 0.067215 | 0.10322 | -0.098026 | -0.14061 | 0.33137 | 0.34371 | 0.43036 | 0.20739 | -121.6726 | 121.3505 | 121.6122 | 121.5696 | 0.57722 | -121.7462
1608.7969 | 121.6644 | -0.27008 | 121.463 | -0.0025182 | -0.037504 | 0.042857 | 0.025666 | -0.010796 | -0.011491 | 0.0013733 | -0.0016258 | -0.0025041 | 0.059328 | 0.036628 | 0.050038 | -0.017266 | -0.07643 | -0.12745 | 0.079598 | 0.08278 | 0.1786 | -0.21874 | -0.072212 | 0.32087 | -0.18455 | 121.1124 | 121.3558 | 121.3132 | -0.30151 | 0.05134 | -121.3834 | 0.25282 | 0.14264 | 0.091296 | -121.3802 | -121.2844 | -0.031432 | -0.35056 | 0.19787 | 0.085526 | 0.11696 | -0.10718 | -0.14977 | 0.34968 | 0.35286 | 0.44868 | 0.19365 | -121.6818 | 121.3825 | 121.6259 | 121.5833 | 0.59095 | -121.7645
1610.5469 | 121.8109 | -0.21057 | 121.4035 | -0.010149 | -0.037504 | 0.042857 | 0.025666 | -0.010583 | -0.011705 | -0.029148 | -0.002053 | -0.0022903 | 0.059328 | 0.036628 | 0.050038 | -0.026423 | -0.090166 | -0.12287 | 0.084176 | 0.08278 | 0.1786 | -0.2279 | -0.072212 | 0.32087 | -0.18913 | 121.1124 | 121.365 | 121.3178 | -0.30151 | -0.017328 | -121.3193 | 0.18415 | 0.087705 | 0.10503 | -121.3207 | -121.2249 | -0.090942 | -0.29105 | 0.13836 | 0.021437 | 0.11238 | -0.038515 | -0.085679 | 0.29475 | 0.29335 | 0.38917 | 0.12041 | -121.6314 | 121.323 | 121.5756 | 121.5284 | 0.53144 | -121.705
1612.2969 | 121.8475 | -0.21973 | 121.4172 | -0.0025182 | -0.037718 | 0.043071 | 0.025666 | -0.01101 | -0.011491 | -0.021518 | -0.002053 | -0.0020767 | 0.059542 | 0.036841 | 0.049824 | -0.021844 | -0.094744 | -0.13202 | 0.079598 | 0.078201 | 0.1786 | -0.2279 | -0.07679 | 0.32545 | -0.19829 | 121.117 | 121.365 | 121.3178 | -0.30609 | -0.008172 | -121.3376 | 0.19788 | 0.087704 | 0.095876 | -121.339 | -121.2386 | -0.086365 | -0.30021 | 0.14294 | 0.021436 | 0.1078 | -0.052248 | -0.099412 | 0.29933 | 0.29793 | 0.39832 | 0.12498 | -121.6451 | 121.3368 | 121.5847 | 121.5376 | 0.54517 | -121.7233
1614.0469 | 121.7972 | -0.23804 | 121.4401 | -0.010149 | -0.037504 | 0.042644 | 0.025666 | -0.01101 | -0.011277 | -0.013887 | -0.002053 | -0.0025041 | 0.059328 | 0.036841 | 0.049824 | -0.026423 | -0.1039 | -0.12745 | 0.07502 | 0.08278 | 0.16944 | -0.2279 | -0.081369 | 0.32545 | -0.20287 | 121.1124 | 121.3741 | 121.3224 | -0.31067 | 0.010138 | -121.3651 | 0.21161 | 0.11059 | 0.10045 | -121.3573 | -121.2707 | -0.072634 | -0.32767 | 0.15667 | 0.035167 | 0.1078 | -0.06598 | -0.11772 | 0.31306 | 0.32082 | 0.40748 | 0.13414 | -121.668 | 121.3505 | 121.6122 | 121.5604 | 0.56348 | -121.7508
1615.7344 | 121.8063 | -0.24261 | 121.4127 | -0.010149 | -0.037504 | 0.04243 | 0.025879 | -0.01101 | -0.011491 | -0.021518 | -0.0016258 | -0.0022903 | 0.059114 | 0.0362 | 0.050038 | -0.021844 | -0.12222 | -0.13202 | 0.07502 | 0.078201 | 0.16944 | -0.24163 | -0.090527 | 0.32087 | -0.20745 | 121.0941 | 121.3604 | 121.3087 | -0.32441 | 0.00098 | -121.3376 | 0.22077 | 0.11059 | 0.10961 | -121.3345 | -121.2432 | -0.081792 | -0.31852 | 0.15209 | 0.035166 | 0.11696 | -0.05225 | -0.10399 | 0.31764 | 0.32082 | 0.41205 | 0.1204 | -121.6543 | 121.3368 | 121.603 | 121.5513 | 0.56348 | -121.7371
1617.4844 | 121.701 | -0.34332 | 121.3715 | -0.010149 | -0.037718 | 0.042857 | 0.025879 | -0.010796 | -0.011705 | -0.021518 | -0.002053 | -0.0025041 | 0.059328 | 0.036841 | 0.050251 | -0.03558 | -0.16342 | -0.17323 | 0.070441 | 0.073622 | 0.16486 | -0.28742 | -0.15463 | 0.32087 | -0.26239 | 121.0529 | 121.31 | 121.2629 | -0.37477 | 0.055898 | -121.301 | 0.30774 | 0.1701 | 0.1142 | -121.2978 | -121.2066 | -0.031451 | -0.31853 | 0.18869 | 0.08093 | 0.11238 | -0.061416 | -0.10858 | 0.41376 | 0.41695 | 0.50818 | 0.1799 | -121.6589 | 121.3963 | 121.6534 | 121.6062 | 0.66419 | -121.7462
1619.2344 | 121.8109 | -0.30212 | 121.3852 | -0.0025182 | -0.037931 | 0.042857 | 0.025879 | -0.010583 | -0.011491 | -0.013887 | -0.0016258 | -0.0027177 | 0.059328 | 0.037055 | 0.049824 | -0.031001 | -0.16342 | -0.18696 | 0.070441 | 0.08278 | 0.1557 | -0.27369 | -0.13173 | 0.32087 | -0.25781 | 121.0712 | 121.3329 | 121.2812 | -0.36562 | 0.028436 | -121.3148 | 0.27112 | 0.11516 | 0.086726 | -121.3024 | -121.2295 | -0.063493 | -0.31395 | 0.17039 | 0.04431 | 0.1078 | -0.052256 | -0.104 | 0.37257 | 0.3849 | 0.45783 | 0.1387 | -121.6589 | 121.3734 | 121.6351 | 121.5833 | 0.62299 | -121.7508
1620.9219 | 121.756 | -0.33417 | 121.4035 | 0.0051128 | -0.03729 | 0.04243 | 0.025879 | -0.01101 | -0.011705 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.036628 | 0.050038 | -0.06305 | -0.18632 | -0.19612 | 0.070441 | 0.073622 | 0.16028 | -0.292 | -0.14547 | 0.31629 | -0.27613 | 121.0575 | 121.3192 | 121.272 | -0.37477 | 0.042163 | -121.3331 | 0.27112 | 0.13805 | 0.095885 | -121.3299 | -121.2432 | -0.040607 | -0.346 | 0.1887 | 0.058038 | 0.098645 | -0.084301 | -0.13147 | 0.40461 | 0.40779 | 0.49445 | 0.14785 | -121.6955 | 121.3917 | 121.6534 | 121.6062 | 0.65046 | -121.7783
1622.6719 | 121.788 | -0.33875 | 121.3806 | -0.0025182 | -0.038145 | 0.042644 | 0.025666 | -0.01101 | -0.011277 | -0.013887 | -0.0016258 | -0.0025041 | 0.059114 | 0.036841 | 0.049824 | -0.06305 | -0.19547 | -0.21901 | 0.07502 | 0.073622 | 0.16028 | -0.30116 | -0.16379 | 0.32087 | -0.28071 | 121.0484 | 121.3055 | 121.2583 | -0.38851 | 0.037584 | -121.3056 | 0.2757 | 0.11974 | 0.082151 | -121.307 | -121.2203 | -0.049766 | -0.33226 | 0.17496 | 0.058037 | 0.1078 | -0.075149 | -0.12231 | 0.41377 | 0.41237 | 0.49903 | 0.14327 | -121.6818 | 121.3871 | 121.6442 | 121.597 | 0.65961 | -121.7691
1624.4219 | 121.8246 | -0.33875 | 121.3486 | -0.0025182 | -0.037931 | 0.04243 | 0.025666 | -0.01101 | -0.011491 | -0.013887 | -0.0016258 | -0.0025041 | 0.059114 | 0.036841 | 0.049824 | -0.06305 | -0.21837 | -0.23732 | 0.065863 | 0.073622 | 0.1557 | -0.31948 | -0.17752 | 0.32545 | -0.29902 | 121.0346 | 121.2963 | 121.2446 | -0.40225 | 0.019268 | -121.2827 | 0.2757 | 0.10142 | 0.082154 | -121.275 | -121.1929 | -0.063502 | -0.31396 | 0.16122 | 0.039722 | 0.10322 | -0.052263 | -0.10401 | 0.40461 | 0.41237 | 0.49445 | 0.12038 | -121.668 | 121.3734 | 121.6351 | 121.5833 | 0.66419 | -121.7508
1626.125 | 121.8292 | -0.33875 | 121.3577 | -0.0025182 | -0.037718 | 0.042644 | 0.025452 | -0.010796 | -0.011491 | -0.013887 | -0.0018394 | -0.0020767 | 0.059542 | 0.036628 | 0.049824 | -0.067628 | -0.22752 | -0.25106 | 0.061284 | 0.078201 | 0.1557 | -0.32864 | -0.1821 | 0.33003 | -0.30818 | 121.03 | 121.2963 | 121.24 | -0.42056 | 0.01011 | -121.2964 | 0.27112 | 0.087687 | 0.077577 | -121.2795 | -121.202 | -0.081818 | -0.32769 | 0.15664 | 0.030565 | 0.11238 | -0.061418 | -0.11774 | 0.40003 | 0.41695 | 0.49445 | 0.11122 | -121.6864 | 121.3688 | 121.6351 | 121.5787 | 0.66877 | -121.7783
1627.8906 | 121.788 | -0.36163 | 121.3669 | -0.01778 | -0.037931 | 0.042644 | 0.025879 | -0.010583 | -0.011277 | -0.013887 | -0.0016258 | -0.0025041 | 0.059328 | 0.036628 | 0.050038 | -0.085942 | -0.22752 | -0.25106 | 0.065863 | 0.069043 | 0.1557 | -0.33779 | -0.1821 | 0.32087 | -0.30818 | 121.0392 | 121.2963 | 121.2491 | -0.41598 | 0.02384 | -121.301 | 0.27569 | 0.11057 | 0.086735 | -121.2978 | -121.2112 | -0.054351 | -0.32769 | 0.17953 | 0.053453 | 0.1078 | -0.070573 | -0.11774 | 0.4275 | 0.43068 | 0.51733 | 0.13411 | -121.7047 | 121.4008 | 121.6579 | 121.6108 | 0.6825 | -121.7829
1629.6406 | 121.8063 | -0.3479 | 121.3669 | -0.010149 | -0.037718 | 0.042644 | 0.025666 | -0.010796 | -0.01085 | -0.013887 | -0.0022666 | -0.0022903 | 0.059542 | 0.036841 | 0.049824 | -0.095099 | -0.2321 | -0.25106 | 0.065863 | 0.064464 | 0.15112 | -0.3149 | -0.17294 | 0.32087 | -0.29902 | 121.0484 | 121.3055 | 121.2583 | -0.39767 | 0.033002 | -121.301 | 0.2528 | 0.096842 | 0.06384 | -121.3024 | -121.2158 | -0.049768 | -0.31853 | 0.17496 | 0.048877 | 0.098645 | -0.061416 | -0.10858 | 0.41376 | 0.41236 | 0.49902 | 0.1158 | -121.6818 | 121.3963 | 121.6534 | 121.6062 | 0.66877 | -121.7645
1631.3281 | 121.8567 | -0.32959 | 121.3669 | 0.0051128 | -0.037718 | 0.042644 | 0.025879 | -0.010583 | -0.011277 | -0.0062567 | -0.0018394 | -0.0025041 | 0.059328 | 0.036841 | 0.049824 | -0.081363 | -0.2321 | -0.25564 | 0.061284 | 0.069043 | 0.14197 | -0.32864 | -0.1821 | 0.32087 | -0.29444 | 121.0575 | 121.3009 | 121.2583 | -0.41141 | 0.000955 | -121.3056 | 0.24823 | 0.073953 | 0.072998 | -121.2978 | -121.2249 | -0.081815 | -0.30937 | 0.14749 | 0.035146 | 0.11696 | -0.065995 | -0.10858 | 0.39087 | 0.39863 | 0.47156 | 0.097488 | -121.6955 | 121.3871 | 121.6305 | 121.5879 | 0.65046 | -121.7783
1633.1094 | 121.8384 | -0.3479 | 121.3531 | -0.01778 | -0.037718 | 0.042857 | 0.026307 | -0.011224 | -0.011064 | -0.021518 | -0.0018394 | -0.0022903 | 0.059328 | 0.036841 | 0.049824 | -0.10426 | -0.25042 | -0.28311 | 0.052128 | 0.064464 | 0.15112 | -0.33779 | -0.19584 | 0.32087 | -0.31734 | 121.0484 | 121.3009 | 121.2537 | -0.41598 | 0.010107 | -121.301 | 0.24365 | 0.064794 | 0.054687 | -121.2887 | -121.202 | -0.068084 | -0.3048 | 0.15206 | 0.030562 | 0.098646 | -0.052262 | -0.099425 | 0.40003 | 0.41236 | 0.49902 | 0.097483 | -121.6909 | 121.3963 | 121.6488 | 121.6016 | 0.66877 | -121.7691
1634.7969 | 121.8246 | -0.37537 | 121.3211 | -0.010149 | -0.037504 | 0.04243 | 0.025879 | -0.010796 | -0.011064 | -0.013887 | -0.0014122 | -0.0025041 | 0.058901 | 0.036628 | 0.049824 | -0.10883 | -0.28247 | -0.31515 | 0.056706 | 0.059885 | 0.14197 | -0.37442 | -0.23705 | 0.32087 | -0.35397 | 120.998 | 121.2643 | 121.2171 | -0.46177 | 0.000942 | -121.2644 | 0.26653 | 0.060212 | 0.05927 | -121.2612 | -121.1791 | -0.086406 | -0.32312 | 0.13832 | 0.021399 | 0.10781 | -0.056848 | -0.10401 | 0.43207 | 0.43525 | 0.51733 | 0.092899 | -121.6955 | 121.3734 | 121.6396 | 121.5925 | 0.69623 | -121.7829
1636.5469 | 121.8246 | -1.0345 | 120.694 | 0.0051128 | -0.037718 | 0.042216 | 0.026307 | -0.010796 | -0.0093541 | -0.013887 | -0.0018394 | -0.0018631 | 0.059114 | 0.037055 | 0.049824 | -0.27823 | -0.92347 | -0.92407 | 0.010922 | 0.009517 | 0.10534 | -1.0246 | -0.90554 | 0.31629 | -1.0225 | 120.3387 | 120.5912 | 120.5303 | -1.1303 | 0.009915 | -120.683 | 0.75631 | 0.11048 | 0.10057 | -120.6845 | -120.5886 | -0.095733 | -0.35529 | 0.12901 | 0.012087 | 0.10782 | -0.10277 | -0.16366 | 1.0455 | 1.0441 | 1.1399 | 0.11107 | -121.7186 | 121.3732 | 121.6258 | 121.5649 | 1.3508 | -121.8242
1638.2969 | 121.8796 | -0.32044 | 121.376 | -0.01778 | -0.037931 | 0.042644 | 0.025452 | -0.01101 | -0.011064 | -0.013887 | -0.0018394 | -0.0022903 | 0.059328 | 0.036841 | 0.049824 | -0.067628 | -0.20463 | -0.22817 | 0.061284 | 0.059885 | 0.1557 | -0.292 | -0.14547 | 0.31629 | -0.25781 | 121.1033 | 121.365 | 121.3178 | -0.3702 | 0.028431 | -121.3148 | 0.25281 | 0.092268 | 0.063837 | -121.3162 | -121.2203 | -0.049761 | -0.27275 | 0.17496 | 0.062621 | 0.11238 | -0.01105 | -0.058214 | 0.38172 | 0.38032 | 0.47614 | 0.1158 | -121.668 | 121.4237 | 121.6854 | 121.6383 | 0.63672 | -121.7462
1639.9844 | 121.8658 | -0.29297 | 121.3989 | -0.010149 | -0.037931 | 0.042216 | 0.025452 | -0.010583 | -0.011277 | -0.013887 | -0.0016258 | -0.0020767 | 0.059328 | 0.036841 | 0.050038 | -0.076785 | -0.20921 | -0.24648 | 0.056706 | 0.059885 | 0.15112 | -0.28742 | -0.15005 | 0.32087 | -0.26239 | 121.1033 | 121.3558 | 121.3087 | -0.3702 | 0.005544 | -121.3422 | 0.21618 | 0.046489 | 0.040945 | -121.339 | -121.2478 | -0.077227 | -0.29563 | 0.14292 | 0.030576 | 0.1078 | -0.043096 | -0.090259 | 0.34967 | 0.35285 | 0.44409 | 0.08376 | -121.6864 | 121.3963 | 121.6488 | 121.6016 | 0.61384 | -121.7691
1641.75 | 121.8887 | -0.30212 | 121.3943 | -0.01778 | -0.037931 | 0.04243 | 0.025666 | -0.010796 | -0.011064 | -0.013887 | -0.0018394 | -0.0020767 | 0.059328 | 0.036841 | 0.050038 | -0.081363 | -0.21379 | -0.2419 | 0.065863 | 0.059885 | 0.15112 | -0.292 | -0.15005 | 0.32087 | -0.27155 | 121.0987 | 121.3513 | 121.3178 | -0.37477 | 0.01012 | -121.3285 | 0.22076 | 0.060222 | 0.050102 | -121.3345 | -121.2432 | -0.07265 | -0.29563 | 0.15207 | 0.030574 | 0.10322 | -0.043096 | -0.076524 | 0.36799 | 0.36201 | 0.45325 | 0.088336 | -121.6864 | 121.4008 | 121.6534 | 121.6199 | 0.62299 | -121.7691
1643.4844 | 121.7697 | -0.36163 | 121.4493 | -0.01778 | -0.037718 | 0.04243 | 0.025879 | -0.01101 | -0.011277 | -0.021518 | -0.0022666 | -0.0020767 | 0.059328 | 0.036628 | 0.050038 | -0.085942 | -0.21837 | -0.2419 | 0.056706 | 0.059885 | 0.14197 | -0.29658 | -0.15921 | 0.32087 | -0.27613 | 121.1033 | 121.3558 | 121.3087 | -0.37935 | 0.065051 | -121.3926 | 0.27569 | 0.11973 | 0.05468 | -121.3894 | -121.3073 | -0.01772 | -0.34599 | 0.20243 | 0.085504 | 0.10322 | -0.09345 | -0.14061 | 0.41834 | 0.42152 | 0.5036 | 0.14327 | -121.7459 | 121.4649 | 121.7175 | 121.6703 | 0.6825 | -121.8286
1645.2344 | 121.8613 | -0.33875 | 121.3852 | -0.010149 | -0.038145 | 0.04243 | 0.025879 | -0.010796 | -0.01085 | -0.013887 | -0.0018394 | -0.0022903 | 0.059328 | 0.037269 | 0.049824 | -0.095099 | -0.23668 | -0.26937 | 0.056706 | 0.064464 | 0.14655 | -0.31948 | -0.1821 | 0.32087 | -0.3036 | 121.085 | 121.3421 | 121.2858 | -0.40225 | 0.019268 | -121.3285 | 0.24365 | 0.069374 | 0.050106 | -121.3207 | -121.2386 | -0.063502 | -0.30021 | 0.15664 | 0.035144 | 0.098646 | -0.043098 | -0.099419 | 0.39545 | 0.40321 | 0.48529 | 0.10206 | -121.7047 | 121.4237 | 121.6808 | 121.6245 | 0.65961 | -121.7874
1647.0312 | 121.7697 | -0.36163 | 121.4081 | -0.010149 | -0.037931 | 0.042216 | 0.025666 | -0.011224 | -0.01085 | -0.0062567 | -0.0016258 | -0.0022903 | 0.059114 | 0.036841 | 0.050038 | -0.095099 | -0.25957 | -0.28311 | 0.033814 | 0.046148 | 0.11907 | -0.33779 | -0.19126 | 0.32087 | -0.30818 | 121.0667 | 121.3284 | 121.2858 | -0.41598 | 0.02384 | -121.3743 | 0.26653 | 0.078527 | 0.054687 | -121.3619 | -121.289 | -0.054351 | -0.34142 | 0.17037 | 0.053453 | 0.1078 | -0.079722 | -0.12231 | 0.39545 | 0.40778 | 0.48071 | 0.10206 | -121.7459 | 121.4283 | 121.69 | 121.6474 | 0.6825 | -121.8241
1648.7188 | 121.8018 | -0.42572 | 121.376 | -0.01778 | -0.038145 | 0.04243 | 0.025666 | -0.010796 | -0.011064 | -0.013887 | -0.0018394 | -0.0027177 | 0.059114 | 0.036414 | 0.050251 | -0.11799 | -0.2962 | -0.32431 | 0.042971 | 0.041569 | 0.12823 | -0.36527 | -0.23247 | 0.32087 | -0.35397 | 121.0346 | 121.2872 | 121.2446 | -0.45719 | 0.060454 | -121.3331 | 0.30773 | 0.10141 | 0.040955 | -121.3345 | -121.2478 | -0.031473 | -0.34142 | 0.19325 | 0.071753 | 0.10323 | -0.088887 | -0.13147 | 0.46869 | 0.46729 | 0.55395 | 0.12952 | -121.7413 | 121.4603 | 121.7129 | 121.6703 | 0.74659 | -121.8332
1650.4688 | 121.7834 | -0.4303 | 121.3806 | -0.01778 | -0.038145 | 0.04243 | 0.025452 | -0.01101 | -0.010423 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.037055 | 0.050251 | -0.11799 | -0.29162 | -0.32889 | 0.033814 | 0.027833 | 0.12365 | -0.36527 | -0.23705 | 0.32545 | -0.34481 | 121.03 | 121.2872 | 121.2446 | -0.45719 | 0.065032 | -121.3468 | 0.31231 | 0.10141 | 0.036377 | -121.3528 | -121.257 | -0.026895 | -0.35058 | 0.19325 | 0.085488 | 0.11238 | -0.093464 | -0.13605 | 0.46411 | 0.45813 | 0.55395 | 0.13867 | -121.7459 | 121.4603 | 121.7174 | 121.6749 | 0.75575 | -121.8378
1652.2188 | 121.8567 | -0.42114 | 121.3074 | -0.010149 | -0.037931 | 0.04243 | 0.025879 | -0.010796 | -0.010423 | -0.013887 | -0.0016258 | -0.0022903 | 0.059114 | 0.037269 | 0.049397 | -0.1363 | -0.30994 | -0.33805 | 0.020079 | 0.023254 | 0.11907 | -0.38358 | -0.25078 | 0.32087 | -0.3677 | 121.0255 | 121.2688 | 121.2217 | -0.47093 | 0.037561 | -121.2873 | 0.28484 | 0.083097 | 0.045536 | -121.2841 | -121.1883 | -0.049787 | -0.28191 | 0.17036 | 0.05344 | 0.10323 | -0.038536 | -0.085699 | 0.44122 | 0.4444 | 0.54022 | 0.1112 | -121.691 | 121.4466 | 121.69 | 121.6428 | 0.74201 | -121.7783
1653.9062 | 121.8704 | -0.39825 | 121.3303 | -0.01778 | -0.038145 | 0.042216 | 0.025666 | -0.01101 | -0.01085 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.037055 | 0.049824 | -0.14088 | -0.30536 | -0.34262 | 0.015501 | 0.027833 | 0.10992 | -0.38816 | -0.25078 | 0.32087 | -0.36312 | 121.0163 | 121.278 | 121.2263 | -0.47093 | 0.010093 | -121.3148 | 0.25737 | 0.05563 | 0.045537 | -121.3024 | -121.2203 | -0.072676 | -0.31396 | 0.14747 | 0.035129 | 0.10781 | -0.052267 | -0.10401 | 0.41375 | 0.42609 | 0.50817 | 0.092894 | -121.7184 | 121.4146 | 121.6762 | 121.6245 | 0.71912 | -121.8012
1655.6719 | 121.7834 | -0.48981 | 121.344 | -0.0025182 | -0.038145 | 0.04243 | 0.025452 | -0.011224 | -0.01085 | -0.021518 | -0.0016258 | -0.0020767 | 0.059114 | 0.036841 | 0.04961 | -0.17293 | -0.34199 | -0.37925 | 0.015501 | 0.014096 | 0.10076 | -0.41106 | -0.28283 | 0.32087 | -0.40433 | 120.998 | 121.2459 | 121.2079 | -0.50298 | 0.078751 | -121.3285 | 0.31688 | 0.11056 | 0.031806 | -121.3299 | -121.2432 | -0.013174 | -0.34601 | 0.20698 | 0.085474 | 0.098648 | -0.09805 | -0.13606 | 0.50531 | 0.5039 | 0.59057 | 0.14782 | -121.755 | 121.4878 | 121.7358 | 121.6977 | 0.81068 | -121.847
1657.3594 | 121.8521 | -0.93384 | 120.7809 | -0.01778 | -0.037931 | 0.042003 | 0.02652 | -0.010796 | -0.0093541 | -0.021518 | -0.002053 | -0.0020767 | 0.059114 | 0.037055 | 0.049824 | -0.36522 | -0.8319 | -0.86455 | -0.094381 | -0.095798 | -0.009128 | -0.901 | -0.78649 | 0.32087 | -0.90341 | 120.4806 | 120.7423 | 120.6951 | -1.0021 | 0.032838 | -120.8753 | 0.56861 | 0.06929 | 0.036452 | -120.8767 | -120.7901 | -0.068234 | -0.30033 | 0.14735 | 0.030426 | 0.09866 | -0.038647 | -0.085811 | 0.83946 | 0.83804 | 0.92471 | 0.10194 | -121.6819 | 121.4145 | 121.6761 | 121.629 | 1.2547 | -121.783
1659.1094 | 121.8201 | -2.1881 | 119.5404 | -0.01778 | -0.037718 | 0.040721 | 0.026734 | -0.010796 | -0.0059355 | -0.0062567 | -0.0018394 | -0.0020767 | 0.059755 | 0.036841 | 0.049824 | -0.83222 | -1.7934 | -1.8168 | -0.28209 | -0.27896 | -0.19685 | -1.89 | -1.7755 | 0.2934 | -1.8924 | 119.4962 | 119.7533 | 119.6924 | -1.9865 | 0.29806 | -119.8225 | 1.3559 | 0.37128 | 0.073218 | -119.8194 | -119.7373 | 0.20159 | -0.044164 | 0.41262 | 0.2957 | 0.094104 | 0.21291 | 0.15201 | 1.906 | 1.9092 | 1.9913 | 0.3947 | -121.4305 | 121.6844 | 121.9414 | 121.8805 | 2.4815 | -121.5269
1660.8125 | 121.9116 | -2.2476 | 119.4489 | -0.0025182 | -0.036436 | 0.038798 | 0.027375 | -0.010796 | -0.0031579 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.037055 | 0.04961 | -0.84138 | -2.6588 | -2.6684 | -0.50644 | -0.5079 | -0.4212 | -2.8104 | -2.6546 | 0.26134 | -2.7944 | 118.6034 | 118.8651 | 118.7859 | -2.884 | -0.56279 | -119.9553 | 1.4062 | -0.42077 | 0.14202 | -119.9568 | -119.8701 | -0.63635 | -0.84542 | -0.40698 | -0.5468 | 0.089546 | -0.58378 | -0.663 | 1.7412 | 1.7397 | 1.8264 | -0.41114 | -122.2593 | 120.8511 | 121.1127 | 121.0335 | 2.509 | -122.3328
1662.5625 | 121.8658 | -0.64087 | 121.1014 | -0.025411 | -0.037931 | 0.041362 | 0.026307 | -0.01101 | -0.0095679 | -0.021518 | -0.0024804 | -0.0025041 | 0.059542 | 0.036841 | 0.04961 | -0.15462 | -0.58466 | -0.61274 | -0.06691 | -0.059167 | 0.022922 | -0.65374 | -0.53466 | 0.33003 | -0.65158 | 120.737 | 120.9895 | 120.947 | -0.75024 | -0.01287 | -121.1683 | 0.48625 | 0.028127 | 0.040997 | -121.1605 | -121.0785 | -0.10937 | -0.36437 | 0.10621 | -0.010714 | 0.098654 | -0.11184 | -0.15442 | 0.57396 | 0.5817 | 0.66379 | 0.056214 | -121.7551 | 121.3779 | 121.6304 | 121.5878 | 0.9709 | -121.8516
1664.25 | 121.8384 | -2.1286 | 119.6228 | -0.01778 | -0.037718 | 0.040934 | 0.025879 | -0.010796 | -0.0082859 | 0.0013733 | -0.002053 | -0.0022903 | 0.059328 | 0.037055 | 0.049824 | -0.2004 | -0.80901 | -0.83708 | -0.11727 | -0.11869 | -0.0366 | -0.89184 | -0.77733 | 0.2934 | -0.89426 | 120.4944 | 120.7515 | 120.6997 | -0.99749 | 1.2368 | -119.7401 | 1.9282 | 1.2915 | 0.054765 | -119.7415 | -119.6594 | 1.1311 | 0.87155 | 1.3513 | 1.2343 | 0.10324 | 1.1287 | 1.0769 | 2.0113 | 2.0099 | 2.092 | 1.3196 | -120.5146 | 122.623 | 122.8801 | 122.8283 | 2.422 | -120.6203
1666.0156 | 121.6965 | -7.7728 | 113.887 | -0.01778 | -0.030666 | 0.027259 | 0.033572 | -0.01101 | 0.016499 | -0.013887 | -0.0024804 | -0.0022903 | 0.059328 | 0.037269 | 0.049824 | -1.4732 | -7.4251 | -7.3566 | -1.3397 | -1.3779 | -1.2911 | -7.6412 | -7.5813 | 0.25219 | -7.7394 | 113.6587 | 113.9019 | 113.8593 | -7.7421 | 0.13165 | -115.2267 | 6.2996 | 0.41628 | 0.28463 | -115.2649 | -115.1782 | 0.030736 | -0.22836 | 0.19153 | 0.033401 | 0.002665 | 0.014842 | -0.027743 | 6.4331 | 6.3949 | 6.4817 | 0.34774 | -121.5282 | 121.4315 | 121.6747 | 121.6321 | 8.025 | -121.6291
1667.7656 | 121.669 | -17.7658 | 103.7201 | -0.010149 | -0.019128 | 0.002686 | 0.045111 | -0.010583 | 0.050258 | -0.013887 | -0.0018394 | -0.0027177 | 0.058901 | 0.037055 | 0.04961 | -2.3797 | -15.694 | -15.5608 | -2.2188 | -2.2708 | -2.1656 | -16.1763 | -16.1435 | 0.13314 | -16.3153 | 105.0923 | 105.3628 | 105.2836 | -16.2221 | 1.5895 | -105.9388 | 15.3861 | 2.205 | 0.61547 | -105.9909 | -105.8857 | 1.5437 | 1.3722 | 1.6223 | 1.4505 | -0.093289 | 1.6427 | 1.5635 | 15.5471 | 15.495 | 15.6002 | 2.0718 | -119.8964 | 122.8581 | 123.1286 | 123.0494 | 17.8989 | -119.9422
1669.4531 | 120.845 | -75.737 | 44.7601 | -0.0025182 | 0.033863 | -0.10308 | 0.098959 | -0.0088734 | 0.25003 | 0.0013733 | -0.0024804 | -0.0027177 | 0.057619 | 0.037482 | 0.050038 | -5.7723 | -73.3341 | -72.7939 | -5.5152 | -5.5539 | -5.4485 | -75.4779 | -75.2729 | -0.33847 | -75.399 | 44.9492 | 45.1084 | 45.1299 | -75.591 | 0.25906 | -50.2753 | 69.9647 | 2.9431 | 2.684 | -50.314 | -50.2086 | 0.146 | 0.18905 | 0.46406 | 0.33798 | 0.19198 | 0.34823 | 0.36975 | 70.2218 | 70.1831 | 70.2885 | 2.4029 | -120.2381 | 120.6862 | 120.8454 | 120.8669 | 75.3985 | -120.3511
1671.2188 | 121.4447 | -116.185 | 4.9301 | -0.010149 | 0.084931 | -0.2048 | 0.14982 | -0.0075914 | 0.4246 | -0.0062567 | -0.002694 | -0.0033587 | 0.058687 | 0.037482 | 0.050679 | -7.9882 | -110.3841 | -109.7269 | -7.4976 | -7.5045 | -7.4402 | -113.7532 | -113.496 | -0.68187 | -113.6404 | 7.0988 | 7.3074 | 7.1778 | -113.9203 | 2.4318 | -12.4277 | 108.1968 | 6.4581 | 4.0263 | -12.4346 | -12.3703 | 2.2647 | 2.1686 | 2.689 | 2.5446 | 0.27988 | 2.3773 | 2.2477 | 108.6874 | 108.6805 | 108.7448 | 5.8009 | -118.6833 | 123.2838 | 123.4924 | 123.3628 | 115.5031 | -118.8504
1672.9375 | 120.8908 | -68.1564 | 52.5558 | -0.0025182 | 0.051598 | -0.14048 | 0.11862 | 0.028731 | 0.21264 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.037269 | 0.050038 | -4.8108 | -19.5034 | -19.0541 | -4.5812 | -4.6244 | -4.5374 | -69.301 | -69.1237 | 0.23845 | -69.2178 | 51.1576 | 51.2986 | 51.3705 | -69.3775 | -1.1445 | -57.137 | 63.3456 | 49.1024 | 50.2469 | -57.1802 | -57.0932 | -1.2211 | -1.3982 | -0.9673 | -1.0613 | 0.15979 | -1.2572 | -1.1853 | 63.5752 | 63.5321 | 63.6191 | 48.653 | -121.8568 | 119.3141 | 119.4551 | 119.5269 | 68.3949 | -121.9334
1674.7031 | 120.9274 | -0.26093 | 120.9503 | -0.0025182 | -0.038145 | 0.041789 | 0.026093 | -0.01101 | -0.010209 | -0.0062567 | -0.0016258 | -0.0027177 | 0.058901 | 0.036841 | 0.049397 | -0.026423 | -0.035222 | -0.05877 | 0.061284 | 0.059885 | 0.14655 | -0.24163 | -0.099684 | 0.5086 | -0.19829 | 120.5356 | 120.8018 | 120.7547 | -0.31983 | 0.01929 | -120.889 | 0.2345 | 0.20216 | 0.18286 | -120.8904 | -120.8038 | -0.058904 | -0.41476 | 0.16124 | 0.062634 | 0.12154 | -0.1485 | -0.19566 | 0.32221 | 0.32081 | 0.40747 | 0.2257 | -121.192 | 120.7965 | 121.0627 | 121.0156 | 0.76952 | -121.2701
1676.3906 | 121.3486 | -0.1831 | 121.0236 | -0.010149 | -0.037718 | 0.041575 | 0.026093 | -0.01101 | -0.01085 | -0.0062567 | -0.0018394 | -0.0022903 | 0.058901 | 0.037055 | 0.04961 | -0.012688 | -0.007751 | -0.045036 | 0.056706 | 0.064464 | 0.14655 | -0.17753 | -0.021846 | 0.43076 | -0.14335 | 120.7004 | 120.9529 | 120.9012 | -0.25572 | 0.005575 | -120.9669 | 0.17042 | 0.13807 | 0.13249 | -120.9591 | -120.877 | -0.07262 | -0.32318 | 0.16126 | 0.039758 | 0.11238 | -0.070647 | -0.12239 | 0.23981 | 0.24757 | 0.32965 | 0.17535 | -121.2011 | 120.8835 | 121.136 | 121.0843 | 0.61386 | -121.2793
1678.1406 | 121.2845 | -0.21515 | 121.1197 | -0.01778 | -0.038145 | 0.041575 | 0.025879 | -0.01101 | -0.010423 | -0.021518 | -0.0022666 | -0.0025041 | 0.058901 | 0.037269 | 0.04961 | -0.021844 | -0.021486 | -0.045036 | 0.061284 | 0.069043 | 0.15112 | -0.18211 | -0.035582 | 0.38497 | -0.14793 | 120.7599 | 121.0079 | 120.9561 | -0.2603 | 0.03304 | -121.0584 | 0.19331 | 0.17011 | 0.13707 | -121.0506 | -120.9686 | -0.045155 | -0.35978 | 0.17957 | 0.067224 | 0.11238 | -0.11183 | -0.16358 | 0.27643 | 0.28419 | 0.36627 | 0.19366 | -121.3018 | 120.9751 | 121.223 | 121.1713 | 0.60012 | -121.38
1679.8281 | 121.344 | -0.2243 | 121.1197 | -0.010149 | -0.038145 | 0.041575 | 0.025666 | -0.01101 | -0.010209 | 0.0013733 | -0.0014122 | -0.0022903 | 0.059114 | 0.037055 | 0.04961 | -0.021844 | -0.016908 | -0.049614 | 0.056706 | 0.055306 | 0.13281 | -0.205 | -0.053897 | 0.36666 | -0.17998 | 120.7691 | 121.0307 | 120.979 | -0.26946 | 0.0193 | -121.063 | 0.20246 | 0.17469 | 0.15539 | -121.0644 | -120.9869 | -0.045158 | -0.35063 | 0.17041 | 0.044328 | 0.089486 | -0.08894 | -0.14068 | 0.28101 | 0.27961 | 0.35711 | 0.2074 | -121.3247 | 120.9934 | 121.2551 | 121.2033 | 0.59096 | -121.3892
1681.5781 | 121.4035 | -0.24261 | 121.0968 | -0.0025182 | -0.037718 | 0.041362 | 0.025666 | -0.010369 | -0.010423 | -0.0062567 | -0.0018394 | -0.0020767 | 0.059114 | 0.037055 | 0.04961 | -0.026423 | -0.016908 | -0.05877 | 0.052128 | 0.055306 | 0.13739 | -0.21416 | -0.063054 | 0.3575 | -0.18455 | 120.7874 | 121.0445 | 120.9927 | -0.29236 | 0.028453 | -121.0447 | 0.21619 | 0.18384 | 0.15539 | -121.0415 | -120.9594 | -0.049741 | -0.30942 | 0.17956 | 0.05806 | 0.1078 | -0.052317 | -0.10406 | 0.29474 | 0.29792 | 0.38 | 0.22571 | -121.311 | 121.03 | 121.2871 | 121.2354 | 0.60011 | -121.3892
1683.3281 | 121.376 | -0.26093 | 121.1472 | -0.0025182 | -0.038145 | 0.041362 | 0.025879 | -0.011224 | -0.010423 | -0.021518 | -0.0018394 | -0.0020767 | 0.059328 | 0.037696 | 0.049397 | -0.021844 | -0.026065 | -0.067927 | 0.061284 | 0.055306 | 0.13739 | -0.2279 | -0.072212 | 0.34834 | -0.19829 | 120.8011 | 121.0582 | 121.0065 | -0.30609 | 0.033026 | -121.0859 | 0.23908 | 0.193 | 0.15997 | -121.0918 | -121.0098 | -0.045167 | -0.34604 | 0.18871 | 0.062634 | 0.1078 | -0.088935 | -0.14068 | 0.32221 | 0.31623 | 0.39831 | 0.23486 | -121.3751 | 121.062 | 121.3191 | 121.2674 | 0.60927 | -121.4532
1685.0938 | 121.4035 | -0.28381 | 121.138 | -0.0025182 | -0.038145 | 0.041148 | 0.026307 | -0.010796 | -0.010209 | -0.013887 | -0.0016258 | -0.0025041 | 0.058901 | 0.036841 | 0.04961 | -0.026423 | -0.030644 | -0.05877 | 0.047549 | 0.055306 | 0.13281 | -0.24163 | -0.085948 | 0.34376 | -0.21203 | 120.8148 | 121.0674 | 121.0202 | -0.31983 | 0.042178 | -121.0905 | 0.25739 | 0.22504 | 0.18286 | -121.0827 | -121.0052 | -0.036016 | -0.32315 | 0.19786 | 0.071786 | 0.1078 | -0.070622 | -0.11779 | 0.33136 | 0.33912 | 0.41662 | 0.25317 | -121.3796 | 121.0987 | 121.3512 | 121.304 | 0.62757 | -121.4578
1686.7969 | 121.4172 | -0.32044 | 121.1426 | -0.01778 | -0.037718 | 0.041362 | 0.026093 | -0.011224 | -0.0097815 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.037269 | 0.049824 | -0.03558 | -0.062694 | -0.099975 | 0.047549 | 0.050727 | 0.12823 | -0.26453 | -0.11342 | 0.34376 | -0.22576 | 120.8148 | 121.0582 | 121.0156 | -0.33814 | 0.055905 | -121.095 | 0.28486 | 0.22046 | 0.16456 | -121.0919 | -121.0143 | -0.017709 | -0.32773 | 0.20702 | 0.094672 | 0.11238 | -0.084357 | -0.12694 | 0.36798 | 0.37116 | 0.44867 | 0.25774 | -121.4071 | 121.1353 | 121.3787 | 121.3361 | 0.6642 | -121.4807
1688.5469 | 121.4355 | -0.31128 | 121.1472 | 0.0051128 | -0.038145 | 0.041362 | 0.026307 | -0.01101 | -0.0097815 | -0.0062567 | -0.0018394 | -0.0020767 | 0.059114 | 0.037482 | 0.050038 | -0.031001 | -0.067272 | -0.099975 | 0.038393 | 0.046148 | 0.12823 | -0.27827 | -0.13173 | 0.33918 | -0.24408 | 120.8103 | 121.0582 | 121.0111 | -0.35646 | 0.033012 | -121.1088 | 0.28028 | 0.2113 | 0.17829 | -121.101 | -121.0189 | -0.04518 | -0.33689 | 0.17954 | 0.067201 | 0.11238 | -0.088935 | -0.1361 | 0.34967 | 0.35743 | 0.43951 | 0.24401 | -121.4254 | 121.1215 | 121.3695 | 121.3223 | 0.65046 | -121.5036
1690.25 | 121.5637 | -0.2655 | 121.0831 | -0.010149 | -0.037718 | 0.041362 | 0.025879 | -0.01101 | -0.0099951 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.037269 | 0.04961 | -0.076785 | -0.081008 | -0.11371 | 0.010922 | 0.000359 | 0.09618 | -0.28742 | -0.15005 | 0.33918 | -0.27155 | 120.8103 | 121.0628 | 121.0156 | -0.3702 | -0.021922 | -121.0721 | 0.18872 | 0.15179 | 0.17371 | -121.0827 | -120.9869 | -0.10469 | -0.2728 | 0.11545 | -0.006047 | 0.098646 | -0.020269 | -0.067432 | 0.27642 | 0.26586 | 0.36168 | 0.18449 | -121.3705 | 121.0758 | 121.3283 | 121.2811 | 0.60469 | -121.4533
1692.0625 | 121.582 | -0.28839 | 121.138 | -0.0025182 | -0.037718 | 0.041148 | 0.025666 | -0.010796 | -0.0093541 | -0.021518 | -0.0016258 | -0.0022903 | 0.059114 | 0.036628 | 0.049824 | -0.11341 | -0.13137 | -0.16407 | -0.044018 | -0.031693 | 0.050394 | -0.30116 | -0.15463 | 0.3346 | -0.28529 | 120.8148 | 121.072 | 121.0202 | -0.37935 | -0.01277 | -121.182 | 0.17498 | 0.12432 | 0.13709 | -121.1697 | -121.0876 | -0.090962 | -0.32315 | 0.13376 | 0.003104 | 0.094066 | -0.066043 | -0.11779 | 0.24437 | 0.2567 | 0.33879 | 0.15702 | -121.4392 | 121.1032 | 121.3603 | 121.3086 | 0.623 | -121.5174
1693.7969 | 121.5363 | -0.32501 | 121.17 | 0.0051128 | -0.037931 | 0.041575 | 0.025879 | -0.01101 | -0.0099951 | -0.0062567 | -0.002053 | -0.0027177 | 0.058901 | 0.037269 | 0.04961 | -0.1363 | -0.14053 | -0.17323 | -0.062332 | -0.063746 | 0.027501 | -0.30116 | -0.15463 | 0.32545 | -0.26239 | 120.8377 | 121.0857 | 121.0431 | -0.37935 | 0.023851 | -121.2324 | 0.18871 | 0.15179 | 0.12793 | -121.2338 | -121.1425 | -0.054341 | -0.3323 | 0.17038 | 0.062619 | 0.11696 | -0.084351 | -0.12694 | 0.26268 | 0.26127 | 0.35251 | 0.18448 | -121.4712 | 121.1628 | 121.4107 | 121.3681 | 0.65046 | -121.5494
1695.5312 | 121.582 | -0.31586 | 121.1426 | -0.01778 | -0.037718 | 0.041575 | 0.026093 | -0.01101 | -0.0091405 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.037269 | 0.049824 | -0.13173 | -0.14053 | -0.17323 | -0.057754 | -0.054588 | 0.027501 | -0.30116 | -0.15921 | 0.33003 | -0.28529 | 120.8423 | 121.0948 | 121.0431 | -0.38393 | 0.014696 | -121.2003 | 0.18413 | 0.14263 | 0.12793 | -121.1972 | -121.1151 | -0.068075 | -0.30026 | 0.15665 | 0.03057 | 0.098645 | -0.047728 | -0.09947 | 0.2581 | 0.26127 | 0.34336 | 0.17533 | -121.4437 | 121.1582 | 121.4107 | 121.359 | 0.64588 | -121.5265
1697.2812 | 121.4996 | -0.37079 | 121.1746 | -0.01778 | -0.037718 | 0.041148 | 0.025879 | -0.010583 | -0.0091405 | -0.013887 | -0.0016258 | -0.0027177 | 0.059114 | 0.037269 | 0.04961 | -0.15462 | -0.168 | -0.2007 | -0.080646 | -0.072904 | 0.004608 | -0.32864 | -0.18668 | 0.32545 | -0.29902 | 120.824 | 121.0857 | 121.034 | -0.40225 | 0.042154 | -121.2553 | 0.21617 | 0.17009 | 0.12794 | -121.2475 | -121.17 | -0.031458 | -0.35062 | 0.18411 | 0.071766 | 0.10322 | -0.088929 | -0.14067 | 0.29014 | 0.29788 | 0.3754 | 0.20279 | -121.5033 | 121.1948 | 121.4565 | 121.4047 | 0.69624 | -121.5769
1698.9844 | 121.6553 | -0.32044 | 121.1334 | -0.025411 | -0.038145 | 0.041362 | 0.025879 | -0.01101 | -0.0091405 | -0.029148 | -0.0018394 | -0.0025041 | 0.058901 | 0.037482 | 0.049824 | -0.16835 | -0.16342 | -0.20528 | -0.089802 | -0.09122 | -0.004549 | -0.33321 | -0.18668 | 0.33003 | -0.31276 | 120.824 | 121.0811 | 121.0385 | -0.41598 | -0.012779 | -121.2232 | 0.15208 | 0.11516 | 0.12794 | -121.2246 | -121.138 | -0.095549 | -0.30942 | 0.13376 | 0.007676 | 0.10323 | -0.052309 | -0.094893 | 0.23063 | 0.22922 | 0.31589 | 0.15701 | -121.4666 | 121.1444 | 121.4015 | 121.359 | 0.65046 | -121.5494
1700.7344 | 121.669 | -0.34332 | 121.1243 | -0.01778 | -0.037931 | 0.041362 | 0.026093 | -0.010796 | -0.0093541 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.037269 | 0.049824 | -0.17751 | -0.168 | -0.2007 | -0.098959 | -0.095798 | -0.009128 | -0.34237 | -0.20042 | 0.33003 | -0.32192 | 120.8332 | 121.0857 | 121.0431 | -0.42514 | 0.000951 | -121.2232 | 0.16581 | 0.14263 | 0.14168 | -121.2201 | -121.1334 | -0.081818 | -0.29111 | 0.14291 | 0.021407 | 0.10323 | -0.038575 | -0.08116 | 0.24436 | 0.24752 | 0.33419 | 0.17532 | -121.4666 | 121.1765 | 121.429 | 121.3864 | 0.67335 | -121.5494
1702.4531 | 121.637 | -0.37537 | 121.1655 | -0.010149 | -0.037931 | 0.041148 | 0.025879 | -0.010796 | -0.0091405 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.037482 | 0.049824 | -0.19124 | -0.17258 | -0.20528 | -0.11269 | -0.10496 | -0.032021 | -0.35153 | -0.22331 | 0.3346 | -0.34481 | 120.8194 | 121.0811 | 121.0294 | -0.43888 | 0.023836 | -121.2782 | 0.18412 | 0.17009 | 0.14625 | -121.2704 | -121.1975 | -0.063512 | -0.34604 | 0.15206 | 0.030556 | 0.094068 | -0.084352 | -0.13609 | 0.26267 | 0.27041 | 0.34334 | 0.20279 | -121.517 | 121.1948 | 121.4565 | 121.4047 | 0.70997 | -121.6043
1704.1875 | 121.6782 | -0.37994 | 121.138 | -0.010149 | -0.037931 | 0.040721 | 0.025879 | -0.010796 | -0.0082859 | -0.021518 | -0.0016258 | -0.0022903 | 0.059328 | 0.037482 | 0.050251 | -0.20498 | -0.18632 | -0.21443 | -0.12643 | -0.12785 | -0.041178 | -0.37442 | -0.2462 | 0.32545 | -0.36312 | 120.8057 | 121.0674 | 121.0156 | -0.45719 | 0.00552 | -121.2644 | 0.17496 | 0.16551 | 0.15999 | -121.2659 | -121.1792 | -0.077249 | -0.33231 | 0.13374 | 0.016819 | 0.094068 | -0.070622 | -0.12236 | 0.25351 | 0.25209 | 0.33877 | 0.19363 | -121.5124 | 121.1856 | 121.4473 | 121.3956 | 0.70539 | -121.5952
1705.9062 | 121.6324 | -0.43945 | 121.1105 | -0.010149 | -0.037931 | 0.040293 | 0.025879 | -0.01101 | -0.0082859 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.037482 | 0.049824 | -0.25076 | -0.22752 | -0.26479 | -0.18137 | -0.17822 | -0.091543 | -0.42021 | -0.28283 | 0.32545 | -0.40433 | 120.7828 | 121.0399 | 120.9882 | -0.50298 | 0.01924 | -121.2919 | 0.18869 | 0.17466 | 0.15542 | -121.2888 | -121.2021 | -0.063528 | -0.32774 | 0.15662 | 0.03512 | 0.098648 | -0.070628 | -0.12237 | 0.25808 | 0.26123 | 0.34791 | 0.21193 | -121.5307 | 121.2223 | 121.4794 | 121.4276 | 0.7649 | -121.6135
1707.6562 | 121.6507 | -0.48523 | 121.0648 | -0.0025182 | -0.037718 | 0.040934 | 0.026307 | -0.010796 | -0.0082859 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.037269 | 0.04961 | -0.3057 | -0.28704 | -0.31058 | -0.22258 | -0.21943 | -0.13733 | -0.45227 | -0.32862 | 0.32545 | -0.45012 | 120.7416 | 120.9987 | 120.947 | -0.54877 | 0.032963 | -121.2873 | 0.17953 | 0.17465 | 0.14169 | -121.2842 | -121.2021 | -0.06354 | -0.32317 | 0.15661 | 0.035109 | 0.098649 | -0.066059 | -0.1178 | 0.26265 | 0.2658 | 0.3479 | 0.19818 | -121.517 | 121.2268 | 121.4839 | 121.4322 | 0.81068 | -121.6135
1709.375 | 121.6553 | -0.48065 | 121.0419 | -0.01778 | -0.038145 | 0.040934 | 0.025879 | -0.010583 | -0.0080721 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.037055 | 0.04961 | -0.31944 | -0.30078 | -0.32889 | -0.24547 | -0.24232 | -0.16022 | -0.46142 | -0.3332 | 0.3346 | -0.4547 | 120.7507 | 121.0079 | 120.9561 | -0.54877 | 0.019228 | -121.2873 | 0.16121 | 0.15176 | 0.13254 | -121.2842 | -121.2021 | -0.068117 | -0.29112 | 0.14745 | 0.025953 | 0.09407 | -0.034013 | -0.085755 | 0.23518 | 0.23833 | 0.32043 | 0.17987 | -121.5033 | 121.2314 | 121.4885 | 121.4368 | 0.81526 | -121.5906
1711.1562 | 121.5912 | -0.52643 | 121.106 | -0.010149 | -0.038359 | 0.040934 | 0.026093 | -0.01101 | -0.0087131 | -0.0062567 | -0.0018394 | -0.0022903 | 0.058901 | 0.037269 | 0.049824 | -0.31486 | -0.30078 | -0.32431 | -0.24089 | -0.2469 | -0.15564 | -0.45227 | -0.32404 | 0.33003 | -0.44554 | 120.7645 | 121.0262 | 120.9699 | -0.54877 | 0.074162 | -121.3468 | 0.21157 | 0.20212 | 0.12795 | -121.3529 | -121.2616 | -0.022341 | -0.34147 | 0.20239 | 0.080887 | 0.10323 | -0.079786 | -0.13611 | 0.28554 | 0.27953 | 0.37079 | 0.22565 | -121.5582 | 121.2909 | 121.5526 | 121.4963 | 0.85645 | -121.6547
1712.9844 | 121.669 | -0.44403 | 121.106 | -0.010149 | -0.037931 | 0.040721 | 0.026307 | -0.010583 | -0.0076449 | -0.029148 | -0.0016258 | -0.0022903 | 0.059328 | 0.037055 | 0.049824 | -0.28739 | -0.26415 | -0.29226 | -0.20884 | -0.20111 | -0.12817 | -0.42937 | -0.30573 | 0.33918 | -0.42265 | 120.792 | 121.0491 | 121.0111 | -0.52587 | 0.01466 | -121.3148 | 0.15664 | 0.15177 | 0.13711 | -121.3071 | -121.2341 | -0.081844 | -0.314 | 0.13831 | 0.021383 | 0.10323 | -0.056893 | -0.094899 | 0.23519 | 0.24292 | 0.31586 | 0.17988 | -121.5353 | 121.236 | 121.4931 | 121.4551 | 0.78321 | -121.6318
1714.6875 | 121.6873 | -0.46234 | 121.0831 | -0.01778 | -0.038572 | 0.041148 | 0.025452 | -0.01101 | -0.0084995 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.037696 | 0.049824 | -0.33775 | -0.30994 | -0.3472 | -0.2592 | -0.25606 | -0.17854 | -0.44311 | -0.31488 | 0.33003 | -0.43638 | 120.792 | 121.0536 | 121.0019 | -0.52587 | 0.019233 | -121.3423 | 0.12459 | 0.11514 | 0.095906 | -121.3391 | -121.2616 | -0.063534 | -0.29111 | 0.14746 | 0.025957 | 0.089491 | -0.029426 | -0.081168 | 0.20314 | 0.20628 | 0.2838 | 0.1524 | -121.5262 | 121.2543 | 121.516 | 121.4642 | 0.79237 | -121.6089
1716.4375 | 121.7377 | -0.45319 | 121.1288 | -0.0025182 | -0.038359 | 0.041575 | 0.025666 | -0.010796 | -0.0087131 | -0.021518 | -0.002053 | -0.0025041 | 0.058901 | 0.037482 | 0.050038 | -0.3286 | -0.30078 | -0.32889 | -0.26378 | -0.25148 | -0.16938 | -0.43853 | -0.30573 | 0.32545 | -0.42723 | 120.8057 | 121.0674 | 121.0156 | -0.52587 | 0.014657 | -121.3926 | 0.12459 | 0.1243 | 0.10964 | -121.3803 | -121.2982 | -0.072689 | -0.32315 | 0.14746 | 0.025959 | 0.098648 | -0.061467 | -0.11321 | 0.1894 | 0.2017 | 0.28381 | 0.1524 | -121.5674 | 121.2589 | 121.5206 | 121.4688 | 0.77863 | -121.6547
1718.1875 | 121.6187 | -0.5127 | 121.17 | 0.0051128 | -0.038359 | 0.041362 | 0.025666 | -0.01101 | -0.0082859 | -0.029148 | -0.0016258 | -0.0018631 | 0.059542 | 0.037269 | 0.04961 | -0.33775 | -0.31452 | -0.34262 | -0.25462 | -0.25606 | -0.17396 | -0.44311 | -0.31488 | 0.32545 | -0.44096 | 120.8057 | 121.0628 | 121.0156 | -0.53045 | 0.069587 | -121.4247 | 0.17494 | 0.17007 | 0.10048 | -121.4261 | -121.344 | -0.017759 | -0.36435 | 0.19781 | 0.071732 | 0.089491 | -0.10724 | -0.15441 | 0.25807 | 0.25663 | 0.33874 | 0.19818 | -121.6132 | 121.3184 | 121.5755 | 121.5283 | 0.83814 | -121.7005
1719.8906 | 121.637 | -0.49439 | 121.1334 | -0.025411 | -0.038572 | 0.041575 | 0.025666 | -0.01101 | -0.0084995 | -0.021518 | -0.0018394 | -0.0020767 | 0.059114 | 0.037482 | 0.050038 | -0.34233 | -0.30994 | -0.3472 | -0.26378 | -0.26064 | -0.18311 | -0.44769 | -0.31488 | 0.33918 | -0.44096 | 120.8103 | 121.0628 | 121.0202 | -0.53961 | 0.046698 | -121.3972 | 0.15205 | 0.14718 | 0.10048 | -121.3941 | -121.3165 | -0.045227 | -0.32315 | 0.1795 | 0.053422 | 0.098649 | -0.070623 | -0.11321 | 0.2306 | 0.23375 | 0.31127 | 0.18445 | -121.5811 | 121.3047 | 121.5572 | 121.5146 | 0.83357 | -121.673
1721.6562 | 121.6232 | -0.49896 | 121.1472 | -0.010149 | -0.038359 | 0.041362 | 0.025666 | -0.010796 | -0.0082859 | -0.029148 | -0.002053 | -0.0020767 | 0.058901 | 0.037482 | 0.050038 | -0.35149 | -0.30994 | -0.3472 | -0.2592 | -0.25606 | -0.17854 | -0.44311 | -0.31488 | 0.3346 | -0.43638 | 120.8148 | 121.0811 | 121.0294 | -0.53961 | 0.055854 | -121.4064 | 0.14747 | 0.15176 | 0.095906 | -121.4032 | -121.3257 | -0.04065 | -0.33231 | 0.18408 | 0.062578 | 0.10323 | -0.066042 | -0.11778 | 0.23976 | 0.2429 | 0.32043 | 0.18902 | -121.5903 | 121.3138 | 121.5801 | 121.5283 | 0.83357 | -121.6868
1723.3438 | 121.6415 | -0.50812 | 121.1792 | -0.0025182 | -0.038572 | 0.042003 | 0.025666 | -0.010796 | -0.0078585 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.037482 | 0.050038 | -0.35149 | -0.30994 | -0.3472 | -0.2592 | -0.26522 | -0.17854 | -0.44311 | -0.31946 | 0.33003 | -0.43638 | 120.824 | 121.0811 | 121.0294 | -0.53503 | 0.06501 | -121.4384 | 0.15663 | 0.16092 | 0.095906 | -121.4444 | -121.3577 | -0.026915 | -0.35519 | 0.18866 | 0.071734 | 0.098649 | -0.098085 | -0.14983 | 0.24891 | 0.2429 | 0.32958 | 0.19818 | -121.6223 | 121.3321 | 121.5892 | 121.5375 | 0.83814 | -121.7142
1725.0938 | 121.6873 | -0.49439 | 121.1426 | -0.0025182 | -0.038572 | 0.041789 | 0.025666 | -0.01101 | -0.0078585 | -0.021518 | -0.0022666 | -0.0022903 | 0.059114 | 0.037482 | 0.049824 | -0.35149 | -0.32367 | -0.36551 | -0.26836 | -0.2698 | -0.19685 | -0.45685 | -0.33778 | 0.32545 | -0.45012 | 120.8286 | 121.0811 | 121.0248 | -0.54419 | 0.03754 | -121.4109 | 0.1429 | 0.12887 | 0.09133 | -121.4124 | -121.3394 | -0.049806 | -0.314 | 0.15661 | 0.044265 | 0.094071 | -0.061464 | -0.11778 | 0.22603 | 0.22459 | 0.29753 | 0.17071 | -121.5994 | 121.323 | 121.5755 | 121.5192 | 0.81983 | -121.6868
1726.8438 | 121.6827 | -0.4715 | 121.1746 | -0.0025182 | -0.038359 | 0.041575 | 0.025666 | -0.01101 | -0.0082859 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.037696 | 0.04961 | -0.34691 | -0.3191 | -0.35178 | -0.26378 | -0.26064 | -0.17396 | -0.43395 | -0.30573 | 0.3346 | -0.42723 | 120.8515 | 121.1086 | 121.066 | -0.52587 | 0.037547 | -121.4384 | 0.12459 | 0.11972 | 0.08217 | -121.4353 | -121.3486 | -0.054378 | -0.32315 | 0.16577 | 0.04427 | 0.098648 | -0.066036 | -0.10862 | 0.20772 | 0.21086 | 0.29754 | 0.1524 | -121.6086 | 121.323 | 121.5801 | 121.5375 | 0.8061 | -121.7005
1728.5938 | 121.7148 | -0.50354 | 121.1609 | -0.01778 | -0.039 | 0.041362 | 0.025452 | -0.01101 | -0.0076449 | -0.013887 | -0.0018394 | -0.0022903 | 0.059328 | 0.037482 | 0.050251 | -0.36064 | -0.34199 | -0.37925 | -0.28667 | -0.28353 | -0.20143 | -0.46142 | -0.34236 | 0.33003 | -0.45012 | 120.824 | 121.0903 | 121.0385 | -0.55793 | 0.042116 | -121.4476 | 0.14289 | 0.12429 | 0.082174 | -121.4444 | -121.3623 | -0.054387 | -0.33688 | 0.16118 | 0.05342 | 0.10781 | -0.070618 | -0.12236 | 0.21687 | 0.22001 | 0.30211 | 0.16155 | -121.6223 | 121.3275 | 121.5938 | 121.5421 | 0.83357 | -121.7188
1730.2812 | 121.6644 | -0.52185 | 121.1655 | -0.0025182 | -0.038359 | 0.042003 | 0.025452 | -0.01101 | -0.0080721 | -0.021518 | -0.0018394 | -0.0025041 | 0.059114 | 0.037696 | 0.050038 | -0.37438 | -0.35115 | -0.38383 | -0.28209 | -0.29269 | -0.20601 | -0.466 | -0.34236 | 0.33918 | -0.46386 | 120.824 | 121.0811 | 121.0294 | -0.55793 | 0.055848 | -121.4476 | 0.14747 | 0.13802 | 0.082175 | -121.4582 | -121.3715 | -0.036076 | -0.34146 | 0.17949 | 0.057995 | 0.094071 | -0.084352 | -0.13609 | 0.23976 | 0.22916 | 0.31584 | 0.1707 | -121.6315 | 121.3459 | 121.603 | 121.5512 | 0.86103 | -121.7234
1732.0312 | 121.7194 | -0.53558 | 121.1426 | -0.01778 | -0.038786 | 0.041575 | 0.025238 | -0.010796 | -0.0080721 | -0.013887 | -0.0018394 | -0.0020767 | 0.059114 | 0.037269 | 0.049397 | -0.3698 | -0.35115 | -0.37925 | -0.28667 | -0.28353 | -0.20601 | -0.47058 | -0.35151 | 0.32087 | -0.46843 | 120.8286 | 121.0857 | 121.0385 | -0.57624 | 0.065001 | -121.4293 | 0.16578 | 0.15633 | 0.091332 | -121.4261 | -121.3486 | -0.040659 | -0.314 | 0.18407 | 0.067148 | 0.10781 | -0.056885 | -0.10405 | 0.24891 | 0.25205 | 0.32958 | 0.18444 | -121.6132 | 121.3642 | 121.6213 | 121.5741 | 0.85645 | -121.7188
1733.7812 | 121.7697 | -0.52185 | 121.1472 | -0.010149 | -0.038786 | 0.042003 | 0.025238 | -0.011224 | -0.0074311 | -0.029148 | -0.0018394 | -0.0016495 | 0.059114 | 0.037482 | 0.04961 | -0.36522 | -0.35115 | -0.38383 | -0.29125 | -0.28353 | -0.20601 | -0.47516 | -0.34693 | 0.3346 | -0.46386 | 120.8332 | 121.0857 | 121.034 | -0.55793 | 0.046691 | -121.4384 | 0.15663 | 0.13802 | 0.091332 | -121.4307 | -121.3532 | -0.036076 | -0.31399 | 0.17492 | 0.057995 | 0.094071 | -0.061463 | -0.1132 | 0.2306 | 0.23832 | 0.31584 | 0.1707 | -121.6223 | 121.355 | 121.6075 | 121.5558 | 0.85646 | -121.7051
1735.4688 | 121.701 | -0.50812 | 121.1975 | -0.0025182 | -0.038572 | 0.041575 | 0.025238 | -0.011224 | -0.0076449 | -0.013887 | -0.0016258 | -0.0020767 | 0.059114 | 0.037269 | 0.049824 | -0.36064 | -0.34199 | -0.37467 | -0.28667 | -0.28811 | -0.20601 | -0.45227 | -0.32404 | 0.33003 | -0.45012 | 120.8515 | 121.1086 | 121.066 | -0.54877 | 0.055852 | -121.4842 | 0.14747 | 0.13345 | 0.077594 | -121.4856 | -121.4035 | -0.040651 | -0.34603 | 0.18408 | 0.057998 | 0.098649 | -0.088924 | -0.13151 | 0.22144 | 0.22 | 0.30211 | 0.16613 | -121.6498 | 121.3596 | 121.6167 | 121.5741 | 0.83814 | -121.7463
1737.2344 | 121.6827 | -0.50354 | 121.225 | -0.010149 | -0.038786 | 0.041789 | 0.025452 | -0.011224 | -0.0076449 | -0.029148 | -0.002053 | -0.0025041 | 0.059114 | 0.037482 | 0.049397 | -0.35607 | -0.33741 | -0.36551 | -0.27294 | -0.27438 | -0.19685 | -0.45685 | -0.31946 | 0.32545 | -0.43638 | 120.8698 | 121.1177 | 121.0752 | -0.53503 | 0.046695 | -121.4979 | 0.14747 | 0.13803 | 0.09133 | -121.4994 | -121.4218 | -0.031493 | -0.35519 | 0.18408 | 0.067156 | 0.098649 | -0.10723 | -0.14982 | 0.2306 | 0.22916 | 0.30669 | 0.16613 | -121.6818 | 121.3733 | 121.6213 | 121.5787 | 0.82899 | -121.76
1739 | 121.6919 | -0.51727 | 121.2387 | -0.010149 | -0.038786 | 0.041789 | 0.025238 | -0.010796 | -0.0074311 | 0.0013733 | -0.0018394 | -0.0022903 | 0.059328 | 0.03791 | 0.049824 | -0.34233 | -0.32367 | -0.36551 | -0.26378 | -0.25606 | -0.17854 | -0.44769 | -0.31946 | 0.3346 | -0.43638 | 120.8698 | 121.1315 | 121.0843 | -0.53961 | 0.069586 | -121.5025 | 0.17494 | 0.15176 | 0.082172 | -121.4948 | -121.4172 | -0.022339 | -0.36892 | 0.19781 | 0.080889 | 0.10323 | -0.10723 | -0.15439 | 0.25349 | 0.26121 | 0.33874 | 0.1936 | -121.6864 | 121.3871 | 121.6488 | 121.6016 | 0.85188 | -121.7783
1740.75 | 121.6919 | -0.50812 | 121.2387 | -0.010149 | -0.039213 | 0.041575 | 0.025238 | -0.010796 | -0.0074311 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.037696 | 0.049824 | -0.33775 | -0.31452 | -0.35636 | -0.25462 | -0.26064 | -0.17854 | -0.45685 | -0.31488 | 0.33003 | -0.44096 | 120.8835 | 121.1406 | 121.0797 | -0.53961 | 0.051273 | -121.4933 | 0.17036 | 0.15176 | 0.10049 | -121.4993 | -121.4172 | -0.031494 | -0.35518 | 0.19323 | 0.067155 | 0.098649 | -0.098072 | -0.15897 | 0.25349 | 0.24748 | 0.32958 | 0.1936 | -121.6956 | 121.3916 | 121.6488 | 121.5879 | 0.83814 | -121.7783
1742.4531 | 121.6873 | -0.50354 | 121.2479 | -0.0025182 | -0.038786 | 0.041789 | 0.025666 | -0.01101 | -0.0072175 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.037696 | 0.049824 | -0.33775 | -0.30994 | -0.35636 | -0.25005 | -0.26064 | -0.17854 | -0.43853 | -0.3103 | 0.3346 | -0.42723 | 120.8881 | 121.159 | 121.0981 | -0.5213 | 0.065011 | -121.4979 | 0.16579 | 0.14718 | 0.08217 | -121.5085 | -121.4264 | -0.017757 | -0.35976 | 0.19323 | 0.076313 | 0.09407 | -0.088913 | -0.14981 | 0.25349 | 0.2429 | 0.325 | 0.1936 | -121.6864 | 121.3916 | 121.6625 | 121.6016 | 0.83814 | -121.7692
1744.2031 | 121.8018 | -0.46234 | 121.2067 | -0.010149 | -0.038786 | 0.042216 | 0.024811 | -0.010796 | -0.0072175 | -0.0062567 | -0.0016258 | -0.0020767 | 0.058901 | 0.037696 | 0.049824 | -0.34691 | -0.33283 | -0.36551 | -0.2592 | -0.26064 | -0.17396 | -0.45227 | -0.30573 | 0.33003 | -0.43638 | 120.9064 | 121.159 | 121.1026 | -0.53503 | 0.010075 | -121.4659 | 0.11543 | 0.096826 | 0.086751 | -121.4673 | -121.3806 | -0.072692 | -0.30025 | 0.15662 | 0.025957 | 0.098649 | -0.047714 | -0.10403 | 0.20314 | 0.2017 | 0.28838 | 0.12951 | -121.6589 | 121.3688 | 121.6213 | 121.565 | 0.79237 | -121.7417
1745.9531 | 121.8338 | -0.43488 | 121.2112 | -0.0025182 | -0.039 | 0.042003 | 0.025238 | -0.01101 | -0.0070039 | -0.0062567 | -0.002053 | -0.0018631 | 0.059114 | 0.037696 | 0.049824 | -0.33775 | -0.3191 | -0.3472 | -0.2592 | -0.25606 | -0.16938 | -0.43853 | -0.31946 | 0.3346 | -0.43638 | 120.8973 | 121.159 | 121.1072 | -0.53503 | -0.003654 | -121.4704 | 0.097122 | 0.087673 | 0.091327 | -121.4673 | -121.3806 | -0.10016 | -0.31398 | 0.11541 | -0.001509 | 0.098649 | -0.052292 | -0.10403 | 0.17567 | 0.17881 | 0.2655 | 0.11578 | -121.6498 | 121.3321 | 121.5938 | 121.5421 | 0.76948 | -121.7463
1747.7188 | 121.7285 | -0.48065 | 121.2479 | -0.0025182 | -0.039213 | 0.042003 | 0.025452 | -0.01101 | -0.0072175 | -0.0062567 | -0.002053 | -0.0022903 | 0.058901 | 0.037269 | 0.049824 | -0.3286 | -0.30078 | -0.3472 | -0.25005 | -0.25148 | -0.17396 | -0.42479 | -0.30573 | 0.3346 | -0.42723 | 120.9156 | 121.1773 | 121.1301 | -0.53503 | 0.05586 | -121.4979 | 0.15206 | 0.13345 | 0.07759 | -121.4993 | -121.4218 | -0.054381 | -0.33229 | 0.17493 | 0.053425 | 0.10781 | -0.070599 | -0.11776 | 0.23061 | 0.22917 | 0.30669 | 0.17987 | -121.6727 | 121.3962 | 121.6579 | 121.6108 | 0.81526 | -121.7829
1749.4688 | 121.8475 | -0.43945 | 121.2067 | -0.010149 | -0.039 | 0.041789 | 0.025238 | -0.011224 | -0.0070039 | -0.021518 | -0.002053 | -0.0018631 | 0.059114 | 0.037482 | 0.04961 | -0.33317 | -0.30994 | -0.33347 | -0.2592 | -0.25606 | -0.17396 | -0.42479 | -0.30573 | 0.3346 | -0.41349 | 120.9339 | 121.1864 | 121.1438 | -0.51672 | 0.014661 | -121.4659 | 0.10628 | 0.10599 | 0.091325 | -121.4627 | -121.3806 | -0.077265 | -0.27278 | 0.13373 | 0.025963 | 0.10323 | -0.020243 | -0.062828 | 0.18025 | 0.18339 | 0.26549 | 0.12951 | -121.6315 | 121.3733 | 121.6259 | 121.5833 | 0.77406 | -121.7234
1751.1562 | 121.8475 | -0.4303 | 121.2158 | -0.0025182 | -0.038786 | 0.041575 | 0.024811 | -0.011224 | -0.0072175 | -0.029148 | -0.002053 | -0.0020767 | 0.059328 | 0.037482 | 0.049824 | -0.33775 | -0.2962 | -0.32889 | -0.25005 | -0.25148 | -0.16938 | -0.41563 | -0.28741 | 0.3346 | -0.40891 | 120.9339 | 121.1956 | 121.1393 | -0.51214 | 0.014664 | -121.4659 | 0.092545 | 0.10141 | 0.086745 | -121.4673 | -121.3852 | -0.081841 | -0.28193 | 0.14289 | 0.021386 | 0.10323 | -0.020241 | -0.076561 | 0.18025 | 0.17882 | 0.26092 | 0.1341 | -121.6315 | 121.3642 | 121.6259 | 121.5696 | 0.7649 | -121.728
1752.9219 | 121.8704 | -0.41657 | 121.2158 | -0.010149 | -0.038786 | 0.041789 | 0.025452 | -0.01101 | -0.0067901 | -0.036779 | -0.002053 | -0.0025041 | 0.059328 | 0.037269 | 0.049824 | -0.31944 | -0.28704 | -0.31515 | -0.24547 | -0.23775 | -0.15107 | -0.40648 | -0.28741 | 0.33003 | -0.40433 | 120.9614 | 121.2139 | 121.1576 | -0.50298 | 0.010088 | -121.4613 | 0.097125 | 0.10141 | 0.091323 | -121.4536 | -121.3669 | -0.086416 | -0.25446 | 0.12915 | 0.012232 | 0.098648 | -0.001926 | -0.058247 | 0.1711 | 0.17882 | 0.2655 | 0.12952 | -121.6223 | 121.3779 | 121.6305 | 121.5741 | 0.74659 | -121.7188
1754.6094 | 121.756 | -0.46234 | 121.2799 | -0.01778 | -0.039 | 0.041575 | 0.025238 | -0.01101 | -0.0067901 | -0.013887 | -0.0022666 | -0.0025041 | 0.058901 | 0.037482 | 0.04961 | -0.31944 | -0.28704 | -0.31973 | -0.24089 | -0.24232 | -0.16022 | -0.41563 | -0.28741 | 0.34376 | -0.40433 | 120.9568 | 121.2093 | 121.1622 | -0.50756 | 0.046707 | -121.5208 | 0.1429 | 0.14261 | 0.095902 | -121.5222 | -121.4401 | -0.045219 | -0.32313 | 0.17493 | 0.058008 | 0.10323 | -0.070592 | -0.11775 | 0.22145 | 0.22002 | 0.30212 | 0.1753 | -121.6955 | 121.4191 | 121.6717 | 121.6245 | 0.8061 | -121.7875
1756.3438 | 121.8246 | -0.41657 | 121.2662 | -0.01778 | -0.039427 | 0.041575 | 0.025666 | -0.01101 | -0.0063629 | -0.013887 | -0.0014122 | -0.0022903 | 0.058901 | 0.037482 | 0.050038 | -0.32402 | -0.29162 | -0.31058 | -0.23631 | -0.2469 | -0.16022 | -0.41563 | -0.28741 | 0.33918 | -0.40891 | 120.9568 | 121.2093 | 121.1576 | -0.51214 | 0.000931 | -121.5025 | 0.092547 | 0.10599 | 0.10506 | -121.5131 | -121.4264 | -0.095574 | -0.30939 | 0.12915 | 0.007653 | 0.10323 | -0.056859 | -0.1086 | 0.18025 | 0.16966 | 0.25634 | 0.12494 | -121.6818 | 121.3733 | 121.6259 | 121.5741 | 0.75575 | -121.7783
1758.125 | 121.8384 | -0.44403 | 121.3074 | -0.010149 | -0.038786 | 0.041789 | 0.025024 | -0.01101 | -0.0065765 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.037482 | 0.049824 | -0.31028 | -0.27331 | -0.29684 | -0.23173 | -0.22859 | -0.14191 | -0.4019 | -0.27368 | 0.32545 | -0.38602 | 120.9797 | 121.2459 | 121.1805 | -0.48924 | 0.042133 | -121.5391 | 0.13375 | 0.14719 | 0.10506 | -121.536 | -121.4493 | -0.045214 | -0.3277 | 0.17036 | 0.058013 | 0.10323 | -0.061429 | -0.12691 | 0.2123 | 0.21544 | 0.30212 | 0.17072 | -121.7093 | 121.4237 | 121.69 | 121.6245 | 0.76948 | -121.7966
1759.8281 | 121.8796 | -0.3891 | 121.2708 | -0.010149 | -0.039 | 0.041789 | 0.025238 | -0.011224 | -0.0061491 | -0.013887 | -0.0016258 | -0.0025041 | 0.058901 | 0.037696 | 0.04961 | -0.30113 | -0.26873 | -0.30142 | -0.22258 | -0.22401 | -0.14191 | -0.39274 | -0.25994 | 0.33918 | -0.38602 | 120.9934 | 121.2459 | 121.1896 | -0.48467 | -0.003641 | -121.4933 | 0.087973 | 0.08768 | 0.091321 | -121.4948 | -121.4127 | -0.095567 | -0.27734 | 0.12916 | 0.003081 | 0.098648 | -0.024808 | -0.081129 | 0.16652 | 0.16509 | 0.24719 | 0.12037 | -121.6635 | 121.3825 | 121.635 | 121.5787 | 0.72828 | -121.7554
1761.5625 | 121.8018 | -0.45776 | 121.312 | -0.01778 | -0.039213 | 0.042003 | 0.025238 | -0.011224 | -0.0057219 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.037696 | 0.050038 | -0.31944 | -0.27331 | -0.31058 | -0.24089 | -0.23775 | -0.15107 | -0.4019 | -0.2691 | 0.3346 | -0.39975 | 120.9797 | 121.2459 | 121.185 | -0.49382 | 0.055866 | -121.5528 | 0.13832 | 0.14719 | 0.091322 | -121.5497 | -121.463 | -0.03606 | -0.33228 | 0.18867 | 0.05801 | 0.09407 | -0.066007 | -0.12691 | 0.21688 | 0.22002 | 0.3067 | 0.18445 | -121.7138 | 121.4374 | 121.7037 | 121.6428 | 0.79237 | -121.8058
1763.25 | 121.7651 | -0.48981 | 121.3669 | -0.010149 | -0.039 | 0.041362 | 0.025024 | -0.011224 | -0.0057219 | -0.013887 | -0.0018394 | -0.0020767 | 0.059114 | 0.037696 | 0.049824 | -0.32402 | -0.28704 | -0.31515 | -0.25005 | -0.2469 | -0.1648 | -0.39732 | -0.26452 | 0.33003 | -0.3906 | 120.9934 | 121.2505 | 121.2034 | -0.48009 | 0.092488 | -121.6169 | 0.16579 | 0.17465 | 0.082165 | -121.6138 | -121.5317 | 0.00972 | -0.37347 | 0.22529 | 0.09921 | 0.08949 | -0.11636 | -0.16352 | 0.23976 | 0.2429 | 0.32501 | 0.20276 | -121.7642 | 121.4832 | 121.7403 | 121.6932 | 0.81983 | -121.847
1765 | 121.8887 | -0.38452 | 121.3211 | -0.010149 | -0.039213 | 0.041362 | 0.025452 | -0.01101 | -0.0050809 | -0.021518 | -0.0018394 | -0.0025041 | 0.059114 | 0.03791 | 0.04961 | -0.3286 | -0.30536 | -0.34262 | -0.26836 | -0.25606 | -0.17854 | -0.37442 | -0.25078 | 0.34376 | -0.36312 | 121.0209 | 121.2734 | 121.2171 | -0.47093 | 0.010097 | -121.5895 | 0.055925 | 0.041897 | 0.0318 | -121.5772 | -121.4996 | -0.086409 | -0.30023 | 0.13374 | 0.021396 | 0.10781 | -0.04769 | -0.10401 | 0.11616 | 0.12846 | 0.20599 | 0.079161 | -121.6955 | 121.4054 | 121.6579 | 121.6016 | 0.72828 | -121.792
1766.75 | 121.8796 | -0.3479 | 121.3669 | -0.010149 | -0.039213 | 0.041575 | 0.025238 | -0.01101 | -0.0055083 | -0.013887 | -0.0014122 | -0.0022903 | 0.059114 | 0.037482 | 0.049824 | -0.30113 | -0.26873 | -0.30142 | -0.22715 | -0.22859 | -0.14191 | -0.33779 | -0.20499 | 0.3346 | -0.32649 | 121.0667 | 121.3284 | 121.2675 | -0.42056 | 0.010107 | -121.594 | 0.046774 | 0.046481 | 0.036374 | -121.5955 | -121.5088 | -0.072663 | -0.30022 | 0.14291 | 0.021405 | 0.094068 | -0.038523 | -0.099422 | 0.12075 | 0.11931 | 0.20599 | 0.079169 | -121.7047 | 121.4146 | 121.6763 | 121.6154 | 0.6825 | -121.7874
1768.4375 | 121.7697 | -0.39825 | 121.4172 | -0.010149 | -0.038572 | 0.041575 | 0.025452 | -0.011224 | -0.0057219 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.037696 | 0.050038 | -0.29655 | -0.26873 | -0.306 | -0.22715 | -0.21943 | -0.14191 | -0.33321 | -0.20042 | 0.3346 | -0.31734 | 121.0712 | 121.3284 | 121.2766 | -0.42514 | 0.06504 | -121.6444 | 0.10171 | 0.092256 | 0.027216 | -121.6367 | -121.5591 | -0.026887 | -0.34599 | 0.19784 | 0.080916 | 0.1078 | -0.088877 | -0.14062 | 0.1711 | 0.17882 | 0.25635 | 0.12952 | -121.7505 | 121.4695 | 121.7266 | 121.6749 | 0.73286 | -121.8424
1770.1875 | 121.8201 | -0.36621 | 121.4401 | -0.010149 | -0.039213 | 0.041362 | 0.025452 | -0.01101 | -0.0057219 | -0.021518 | -0.002053 | -0.0018631 | 0.059114 | 0.037696 | 0.049824 | -0.28739 | -0.25042 | -0.28311 | -0.20884 | -0.20569 | -0.11901 | -0.31948 | -0.17752 | 0.33003 | -0.30818 | 121.1033 | 121.3604 | 121.2995 | -0.40225 | 0.046734 | -121.649 | 0.07882 | 0.083105 | 0.036371 | -121.6458 | -121.5591 | -0.036036 | -0.33683 | 0.18869 | 0.058031 | 0.094067 | -0.079716 | -0.14061 | 0.15737 | 0.16052 | 0.2472 | 0.11579 | -121.7596 | 121.4695 | 121.7266 | 121.6657 | 0.69624 | -121.8424
1771.9375 | 121.8475 | -0.32044 | 121.4035 | -0.010149 | -0.039 | 0.041575 | 0.025452 | -0.010796 | -0.0052945 | -0.036779 | -0.0018394 | -0.0022903 | 0.059328 | 0.038123 | 0.049824 | -0.26908 | -0.24126 | -0.27395 | -0.20426 | -0.19196 | -0.11444 | -0.30574 | -0.16836 | 0.33003 | -0.29444 | 121.117 | 121.3741 | 121.3087 | -0.39309 | 0.014695 | -121.6078 | 0.051358 | 0.046485 | 0.03179 | -121.5955 | -121.5179 | -0.072655 | -0.28647 | 0.15207 | 0.025991 | 0.098646 | -0.029358 | -0.094836 | 0.11617 | 0.12848 | 0.206 | 0.079176 | -121.7092 | 121.4375 | 121.6946 | 121.6291 | 0.65046 | -121.7966
1773.7031 | 121.8201 | -0.31586 | 121.4539 | -0.01778 | -0.039213 | 0.041362 | 0.025666 | -0.01101 | -0.0059355 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.038123 | 0.050038 | -0.25076 | -0.21837 | -0.2419 | -0.17221 | -0.17822 | -0.096121 | -0.28285 | -0.14547 | 0.33918 | -0.27155 | 121.1353 | 121.397 | 121.3407 | -0.36562 | 0.033011 | -121.6261 | 0.065093 | 0.073955 | 0.040944 | -121.6321 | -121.55 | -0.04976 | -0.31852 | 0.17039 | 0.044307 | 0.094067 | -0.056819 | -0.11314 | 0.14364 | 0.13764 | 0.21974 | 0.097491 | -121.7367 | 121.4512 | 121.7129 | 121.6566 | 0.65504 | -121.8195
1775.4375 | 121.8155 | -0.29755 | 121.4996 | -0.010149 | -0.039 | 0.041575 | 0.025452 | -0.011437 | -0.0061491 | -0.021518 | -0.0018394 | -0.0027177 | 0.058901 | 0.03791 | 0.049824 | -0.22787 | -0.20005 | -0.23275 | -0.16764 | -0.1599 | -0.082386 | -0.27827 | -0.13631 | 0.33918 | -0.25781 | 121.1628 | 121.4154 | 121.3682 | -0.35188 | 0.019279 | -121.6673 | 0.069674 | 0.064801 | 0.045522 | -121.6595 | -121.582 | -0.054334 | -0.33682 | 0.16123 | 0.039732 | 0.094066 | -0.084282 | -0.13144 | 0.12991 | 0.13764 | 0.21516 | 0.097494 | -121.7779 | 121.4604 | 121.7129 | 121.6657 | 0.63673 | -121.8515
1777.125 | 121.875 | -0.26093 | 121.4676 | -0.0025182 | -0.038359 | 0.041362 | 0.025666 | -0.011224 | -0.0061491 | -0.021518 | -0.002053 | -0.0018631 | 0.059114 | 0.037696 | 0.050038 | -0.22787 | -0.19547 | -0.21901 | -0.1539 | -0.15075 | -0.077807 | -0.25995 | -0.12716 | 0.3346 | -0.24408 | 121.1765 | 121.4291 | 121.3636 | -0.33814 | 0.000974 | -121.6215 | 0.033053 | 0.041915 | 0.040941 | -121.6183 | -121.5454 | -0.077219 | -0.29104 | 0.13377 | 0.016847 | 0.094066 | -0.038502 | -0.10398 | 0.10703 | 0.11018 | 0.18312 | 0.065452 | -121.7275 | 121.4375 | 121.69 | 121.6245 | 0.59553 | -121.8057
1778.875 | 121.8018 | -0.31586 | 121.5225 | -0.0025182 | -0.039213 | 0.041362 | 0.025238 | -0.011224 | -0.0055083 | -0.0062567 | -0.002053 | -0.0020767 | 0.058901 | 0.037696 | 0.04961 | -0.22787 | -0.1909 | -0.21901 | -0.1539 | -0.15075 | -0.073228 | -0.26453 | -0.12258 | 0.3346 | -0.24408 | 121.1811 | 121.4382 | 121.3728 | -0.33814 | 0.051327 | -121.6764 | 0.087985 | 0.096847 | 0.04552 | -121.6733 | -121.5957 | -0.022287 | -0.34139 | 0.19328 | 0.071779 | 0.094066 | -0.084277 | -0.14975 | 0.16196 | 0.16511 | 0.24263 | 0.12496 | -121.7871 | 121.497 | 121.7541 | 121.6886 | 0.65046 | -121.8607
1780.6406 | 121.9208 | -0.26093 | 121.4767 | -0.0025182 | -0.039 | 0.041148 | 0.025452 | -0.011224 | -0.0059355 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.037696 | 0.04961 | -0.21871 | -0.18632 | -0.21901 | -0.14474 | -0.15075 | -0.064071 | -0.25995 | -0.118 | 0.33003 | -0.23034 | 121.1903 | 121.4428 | 121.3865 | -0.33357 | 0.000974 | -121.6215 | 0.04221 | 0.041915 | 0.040941 | -121.6275 | -121.5408 | -0.07264 | -0.28646 | 0.14293 | 0.030583 | 0.10322 | -0.033922 | -0.090243 | 0.11618 | 0.11018 | 0.19685 | 0.074609 | -121.7367 | 121.4512 | 121.7037 | 121.6474 | 0.59095 | -121.8103
1782.3906 | 121.8979 | -0.24719 | 121.4859 | -0.010149 | -0.038786 | 0.041362 | 0.025666 | -0.011224 | -0.0057219 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.037696 | 0.049824 | -0.21414 | -0.1909 | -0.21901 | -0.14932 | -0.14159 | -0.064071 | -0.25995 | -0.11342 | 0.3346 | -0.23492 | 121.1903 | 121.4566 | 121.3911 | -0.33357 | -0.012759 | -121.6352 | 0.033055 | 0.028182 | 0.040941 | -121.6275 | -121.55 | -0.086373 | -0.29562 | 0.13377 | 0.012271 | 0.098644 | -0.029341 | -0.094819 | 0.097871 | 0.1056 | 0.18312 | 0.056297 | -121.7459 | 121.4375 | 121.7038 | 121.6383 | 0.5818 | -121.8195
1784.1406 | 121.8338 | -0.27466 | 121.5408 | 0.0051128 | -0.038572 | 0.041148 | 0.025452 | -0.011224 | -0.0059355 | -0.0062567 | -0.0016258 | -0.0022903 | 0.058901 | 0.037482 | 0.050038 | -0.20498 | -0.17716 | -0.21443 | -0.13559 | -0.14159 | -0.054914 | -0.25079 | -0.11342 | 0.3346 | -0.2395 | 121.1994 | 121.4611 | 121.4002 | -0.32441 | 0.023865 | -121.6764 | 0.069678 | 0.060226 | 0.036361 | -121.6824 | -121.5957 | -0.049749 | -0.34139 | 0.16124 | 0.035159 | 0.084908 | -0.079695 | -0.14059 | 0.13907 | 0.13307 | 0.21974 | 0.097499 | -121.7916 | 121.4741 | 121.7358 | 121.6749 | 0.60926 | -121.8652
1785.8438 | 121.7926 | -0.29755 | 121.5271 | -0.010149 | -0.038786 | 0.040934 | 0.025452 | -0.011224 | -0.0055083 | -0.013887 | -0.0016258 | -0.0022903 | 0.059114 | 0.03791 | 0.050038 | -0.20956 | -0.17258 | -0.20528 | -0.13101 | -0.13701 | -0.059493 | -0.24621 | -0.10426 | 0.3346 | -0.22576 | 121.2086 | 121.4657 | 121.4048 | -0.32441 | 0.051332 | -121.6581 | 0.087988 | 0.092271 | 0.040939 | -121.6641 | -121.5866 | -0.026861 | -0.3185 | 0.19328 | 0.071783 | 0.098644 | -0.061383 | -0.12228 | 0.16654 | 0.16054 | 0.23805 | 0.12497 | -121.7733 | 121.5061 | 121.7633 | 121.7024 | 0.63215 | -121.8515
1787.5938 | 121.9391 | -0.24719 | 121.5134 | -0.010149 | -0.039 | 0.040721 | 0.025879 | -0.011224 | -0.0052945 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.037696 | 0.04961 | -0.20498 | -0.17258 | -0.19612 | -0.12643 | -0.13243 | -0.054914 | -0.24621 | -0.099684 | 0.33918 | -0.22118 | 121.2178 | 121.4703 | 121.4094 | -0.32441 | 0.000978 | -121.6398 | 0.042212 | 0.051073 | 0.050095 | -121.6458 | -121.5683 | -0.077215 | -0.29561 | 0.14751 | 0.026007 | 0.10322 | -0.043072 | -0.10397 | 0.12076 | 0.11476 | 0.19228 | 0.074612 | -121.7596 | 121.4649 | 121.7175 | 121.6566 | 0.58638 | -121.8378
1789.3438 | 121.9025 | -0.25177 | 121.5363 | -0.010149 | -0.038786 | 0.040507 | 0.025879 | -0.01101 | -0.0052945 | -0.0062567 | -0.002053 | -0.0022903 | 0.059542 | 0.03791 | 0.049824 | -0.20956 | -0.17258 | -0.2007 | -0.12185 | -0.13243 | -0.041178 | -0.24163 | -0.095105 | 0.33918 | -0.22118 | 121.2178 | 121.4749 | 121.414 | -0.31525 | 0.010135 | -121.6581 | 0.042212 | 0.051073 | 0.040938 | -121.6687 | -121.5774 | -0.06348 | -0.3185 | 0.15666 | 0.030585 | 0.094065 | -0.061381 | -0.12228 | 0.12992 | 0.11934 | 0.21059 | 0.07919 | -121.7779 | 121.4695 | 121.7266 | 121.6657 | 0.59095 | -121.8515
1791.125 | 121.8475 | -0.27008 | 121.5546 | -0.010149 | -0.038786 | 0.040293 | 0.025879 | -0.011437 | -0.0050809 | -0.013887 | -0.0018394 | -0.0025041 | 0.059114 | 0.037696 | 0.049824 | -0.2004 | -0.168 | -0.2007 | -0.12185 | -0.12327 | -0.041178 | -0.23706 | -0.099684 | 0.3346 | -0.20745 | 121.2269 | 121.4886 | 121.4277 | -0.31525 | 0.033025 | -121.6764 | 0.069679 | 0.069384 | 0.036359 | -121.6778 | -121.5957 | -0.045169 | -0.32765 | 0.1704 | 0.062632 | 0.1078 | -0.065955 | -0.12685 | 0.14823 | 0.14681 | 0.2289 | 0.10208 | -121.7916 | 121.497 | 121.7587 | 121.6978 | 0.60469 | -121.8698
1792.8281 | 121.843 | -0.27924 | 121.5179 | -0.01778 | -0.038572 | 0.040507 | 0.026093 | -0.011437 | -0.0050809 | -0.0062567 | -0.0018394 | -0.0020767 | 0.059328 | 0.037696 | 0.050251 | -0.19582 | -0.14969 | -0.19154 | -0.12185 | -0.12327 | -0.032021 | -0.23248 | -0.099684 | 0.33003 | -0.20745 | 121.2361 | 121.4978 | 121.4277 | -0.31067 | 0.046759 | -121.6398 | 0.083413 | 0.087695 | 0.040936 | -121.6412 | -121.55 | -0.031435 | -0.28187 | 0.17955 | 0.071787 | 0.10322 | -0.020177 | -0.090233 | 0.15738 | 0.15596 | 0.24721 | 0.12955 | -121.7504 | 121.5153 | 121.777 | 121.7069 | 0.60926 | -121.8286
1794.5938 | 121.8704 | -0.27466 | 121.5866 | -0.0025182 | -0.038786 | 0.040721 | 0.025879 | -0.011224 | -0.0048673 | -0.021518 | -0.0022666 | -0.0018631 | 0.058901 | 0.038123 | 0.050251 | -0.18667 | -0.15884 | -0.18696 | -0.11727 | -0.11869 | -0.0366 | -0.22332 | -0.081369 | 0.33918 | -0.20745 | 121.2406 | 121.5115 | 121.446 | -0.30151 | 0.051338 | -121.7039 | 0.087992 | 0.087696 | 0.036358 | -121.7053 | -121.6232 | -0.026855 | -0.34596 | 0.19329 | 0.067209 | 0.094064 | -0.075106 | -0.14058 | 0.15738 | 0.15597 | 0.23806 | 0.11581 | -121.8099 | 121.5153 | 121.7862 | 121.7207 | 0.61384 | -121.8881
1796.3438 | 121.907 | -0.23346 | 121.5637 | -0.010149 | -0.038572 | 0.040293 | 0.026307 | -0.01101 | -0.0050809 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.038337 | 0.049824 | -0.19124 | -0.15427 | -0.19154 | -0.11269 | -0.11411 | -0.0366 | -0.2279 | -0.081369 | 0.33918 | -0.20745 | 121.2406 | 121.5161 | 121.4414 | -0.30151 | 0.00556 | -121.6764 | 0.042214 | 0.041918 | 0.036358 | -121.6778 | -121.6003 | -0.068054 | -0.32307 | 0.15209 | 0.02601 | 0.094064 | -0.047639 | -0.12227 | 0.12076 | 0.11935 | 0.19686 | 0.079193 | -121.7916 | 121.4741 | 121.7495 | 121.6749 | 0.57264 | -121.8652
1798.0469 | 121.9254 | -0.2243 | 121.5363 | -0.010149 | -0.038572 | 0.04008 | 0.025879 | -0.01101 | -0.0044399 | -0.021518 | -0.002053 | -0.0025041 | 0.059114 | 0.03791 | 0.050038 | -0.18667 | -0.14511 | -0.18238 | -0.11269 | -0.10953 | -0.027442 | -0.22332 | -0.07679 | 0.34834 | -0.20287 | 121.2498 | 121.5115 | 121.4506 | -0.30609 | 0.000984 | -121.6489 | 0.037638 | 0.04192 | 0.040936 | -121.6458 | -121.5637 | -0.081788 | -0.28645 | 0.14751 | 0.021434 | 0.10322 | -0.024752 | -0.085651 | 0.11161 | 0.11477 | 0.19686 | 0.079195 | -121.7596 | 121.4741 | 121.7358 | 121.6749 | 0.57265 | -121.8423
1799.7969 | 121.8246 | -0.27924 | 121.5866 | -0.025411 | -0.038572 | 0.04008 | 0.025879 | -0.011224 | -0.0046535 | -0.013887 | -0.0018394 | -0.0020767 | 0.059114 | 0.03791 | 0.050038 | -0.18667 | -0.14969 | -0.18238 | -0.10354 | -0.10953 | -0.027442 | -0.22332 | -0.072212 | 0.33918 | -0.19829 | 121.259 | 121.5207 | 121.4689 | -0.29693 | 0.055916 | -121.6901 | 0.09257 | 0.096852 | 0.040936 | -121.6961 | -121.6141 | -0.017698 | -0.32765 | 0.20702 | 0.080945 | 0.098643 | -0.065949 | -0.11769 | 0.1757 | 0.1697 | 0.25179 | 0.12955 | -121.8099 | 121.5382 | 121.7999 | 121.7482 | 0.61842 | -121.8835
1801.5469 | 121.9025 | -0.23804 | 121.5408 | -0.01778 | -0.038572 | 0.039866 | 0.025879 | -0.011224 | -0.0044399 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.03791 | 0.049824 | -0.17751 | -0.14969 | -0.17781 | -0.10354 | -0.10953 | -0.027442 | -0.21874 | -0.081369 | 0.33918 | -0.19829 | 121.2681 | 121.5207 | 121.4643 | -0.29693 | 0.019296 | -121.6444 | 0.060527 | 0.060231 | 0.040935 | -121.6504 | -121.5683 | -0.058897 | -0.27271 | 0.15667 | 0.039746 | 0.098643 | -0.020173 | -0.076493 | 0.1345 | 0.1285 | 0.2106 | 0.08835 | -121.7596 | 121.5062 | 121.7587 | 121.7024 | 0.57722 | -121.8378
1803.25 | 121.875 | -0.25177 | 121.5729 | 0.0051128 | -0.038572 | 0.039866 | 0.026093 | -0.011224 | -0.0044399 | -0.0062567 | -0.0018394 | -0.0020767 | 0.059114 | 0.038123 | 0.050251 | -0.17293 | -0.14053 | -0.17323 | -0.10354 | -0.10496 | -0.018285 | -0.21874 | -0.072212 | 0.33918 | -0.18913 | 121.2727 | 121.5298 | 121.4689 | -0.28778 | 0.033029 | -121.6764 | 0.078839 | 0.078543 | 0.045514 | -121.6778 | -121.5912 | -0.036007 | -0.30018 | 0.17956 | 0.062636 | 0.098643 | -0.043059 | -0.10396 | 0.14823 | 0.14681 | 0.23348 | 0.11124 | -121.7916 | 121.5245 | 121.7816 | 121.7207 | 0.59095 | -121.8607
1805 | 121.8979 | -0.22888 | 121.5637 | -0.0025182 | -0.038786 | 0.04008 | 0.025879 | -0.011437 | -0.0044399 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.03791 | 0.050038 | -0.16835 | -0.14053 | -0.16865 | -0.094381 | -0.10953 | -0.027442 | -0.21416 | -0.07679 | 0.33918 | -0.18913 | 121.2727 | 121.5436 | 121.4689 | -0.28778 | 0.01472 | -121.6581 | 0.060529 | 0.060233 | 0.045513 | -121.6733 | -121.5912 | -0.058895 | -0.29102 | 0.15209 | 0.039748 | 0.098643 | -0.020168 | -0.094803 | 0.1345 | 0.11935 | 0.20144 | 0.088352 | -121.7779 | 121.5016 | 121.7724 | 121.6978 | 0.56807 | -121.8515
1806.75 | 121.8887 | -0.23804 | 121.6095 | -0.010149 | -0.038572 | 0.039866 | 0.026093 | -0.01101 | -0.0042263 | -0.021518 | -0.0018394 | -0.0025041 | 0.059114 | 0.03791 | 0.050251 | -0.17293 | -0.13137 | -0.16407 | -0.094381 | -0.095798 | -0.013707 | -0.21416 | -0.072212 | 0.34376 | -0.18913 | 121.2819 | 121.5436 | 121.4827 | -0.28778 | 0.023875 | -121.7039 | 0.065106 | 0.073966 | 0.050091 | -121.7053 | -121.6232 | -0.04974 | -0.32764 | 0.16583 | 0.048903 | 0.098643 | -0.065944 | -0.12684 | 0.14366 | 0.14224 | 0.22433 | 0.10666 | -121.8237 | 121.5199 | 121.7816 | 121.7207 | 0.5818 | -121.8973
1808.4375 | 121.8887 | -0.23346 | 121.5958 | -0.010149 | -0.038359 | 0.039866 | 0.026307 | -0.01101 | -0.0044399 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.038123 | 0.04961 | -0.17293 | -0.13137 | -0.16865 | -0.098959 | -0.10038 | -0.013707 | -0.22332 | -0.063054 | 0.34376 | -0.18913 | 121.2864 | 121.5436 | 121.4872 | -0.2832 | 0.010139 | -121.6947 | 0.060528 | 0.06481 | 0.054671 | -121.6961 | -121.6095 | -0.049739 | -0.30933 | 0.17041 | 0.044325 | 0.094064 | -0.052211 | -0.10853 | 0.1345 | 0.13308 | 0.21975 | 0.10209 | -121.8191 | 121.5199 | 121.777 | 121.7207 | 0.57722 | -121.879
1810.1875 | 121.8384 | -0.24261 | 121.6232 | -0.010149 | -0.038572 | 0.039652 | 0.025879 | -0.01101 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.059114 | 0.03791 | 0.049824 | -0.17293 | -0.13137 | -0.16407 | -0.10354 | -0.095798 | -0.013707 | -0.21416 | -0.067633 | 0.33918 | -0.18455 | 121.2864 | 121.5436 | 121.4918 | -0.28778 | 0.028453 | -121.7268 | 0.069684 | 0.078544 | 0.050091 | -121.719 | -121.6369 | -0.045162 | -0.3368 | 0.17498 | 0.05806 | 0.10322 | -0.079677 | -0.13142 | 0.13908 | 0.14682 | 0.22891 | 0.11124 | -121.8374 | 121.529 | 121.7862 | 121.7344 | 0.5818 | -121.911
1811.875 | 121.8796 | -0.24261 | 121.6187 | -0.010149 | -0.038145 | 0.039439 | 0.02652 | -0.011224 | -0.0037989 | -0.013887 | -0.002053 | -0.0018631 | 0.059328 | 0.038551 | 0.050465 | -0.16835 | -0.13137 | -0.17323 | -0.10354 | -0.10038 | -0.018285 | -0.20042 | -0.067633 | 0.33918 | -0.18455 | 121.3002 | 121.5527 | 121.4918 | -0.2832 | 0.04219 | -121.7222 | 0.074262 | 0.069388 | 0.027198 | -121.719 | -121.6369 | -0.040583 | -0.31848 | 0.17498 | 0.05806 | 0.098643 | -0.065942 | -0.12684 | 0.13908 | 0.14224 | 0.22433 | 0.11124 | -121.8191 | 121.5428 | 121.7953 | 121.7344 | 0.5818 | -121.9018
1813.5781 | 121.8338 | -0.23804 | 121.6324 | -0.010149 | -0.038359 | 0.039652 | 0.026093 | -0.011437 | -0.0040125 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.038551 | 0.049824 | -0.16377 | -0.13137 | -0.15949 | -0.094381 | -0.095798 | -0.004549 | -0.205 | -0.063054 | 0.34834 | -0.17998 | 121.2956 | 121.5573 | 121.5055 | -0.27862 | 0.033033 | -121.7268 | 0.074263 | 0.078544 | 0.045511 | -121.7282 | -121.6369 | -0.040582 | -0.33679 | 0.17498 | 0.058061 | 0.098643 | -0.075096 | -0.12684 | 0.14366 | 0.14224 | 0.23349 | 0.10666 | -121.8374 | 121.5336 | 121.7953 | 121.7436 | 0.58638 | -121.911
1815.3281 | 121.962 | -0.20599 | 121.5912 | -0.0025182 | -0.038145 | 0.039225 | 0.02652 | -0.011224 | -0.0035853 | -0.013887 | -0.0016258 | -0.0022903 | 0.059328 | 0.038123 | 0.050038 | -0.16835 | -0.12679 | -0.15949 | -0.080646 | -0.095798 | -0.004549 | -0.20042 | -0.058476 | 0.34834 | -0.17998 | 121.3093 | 121.5573 | 121.501 | -0.27862 | 0.005569 | -121.6718 | 0.037641 | 0.046501 | 0.040932 | -121.687 | -121.5957 | -0.072625 | -0.28186 | 0.14752 | 0.026018 | 0.098643 | -0.033898 | -0.090219 | 0.12535 | 0.1102 | 0.20145 | 0.0792 | -121.7916 | 121.5153 | 121.7633 | 121.707 | 0.55434 | -121.8698
1817.0938 | 121.8658 | -0.23346 | 121.6232 | -0.010149 | -0.038359 | 0.039439 | 0.025879 | -0.011224 | -0.0037989 | -0.0062567 | -0.002053 | -0.0025041 | 0.058901 | 0.038123 | 0.050038 | -0.16377 | -0.12222 | -0.15491 | -0.085224 | -0.086641 | -0.004549 | -0.20042 | -0.058476 | 0.33918 | -0.1754 | 121.3047 | 121.571 | 121.5147 | -0.26946 | 0.033034 | -121.7085 | 0.069685 | 0.078545 | 0.045511 | -121.7099 | -121.6278 | -0.036003 | -0.31848 | 0.17498 | 0.058061 | 0.094064 | -0.052205 | -0.10853 | 0.14824 | 0.14682 | 0.22891 | 0.11124 | -121.8237 | 121.5382 | 121.8045 | 121.7482 | 0.57264 | -121.8927
1818.7969 | 121.9025 | -0.24261 | 121.637 | -0.01778 | -0.038145 | 0.039225 | 0.026307 | -0.011651 | -0.0033715 | -0.021518 | -0.0018394 | -0.0020767 | 0.059328 | 0.038337 | 0.050038 | -0.16377 | -0.11764 | -0.15034 | -0.085224 | -0.082062 | 0.004608 | -0.20042 | -0.049318 | 0.34834 | -0.17082 | 121.3231 | 121.5848 | 121.5193 | -0.27862 | 0.04219 | -121.7222 | 0.078841 | 0.092279 | 0.050089 | -121.719 | -121.6324 | -0.036004 | -0.3139 | 0.1933 | 0.071796 | 0.1078 | -0.052202 | -0.11768 | 0.15739 | 0.16055 | 0.24722 | 0.12498 | -121.8374 | 121.5657 | 121.8274 | 121.7619 | 0.59096 | -121.9156
1820.5469 | 121.9116 | -0.2243 | 121.637 | -0.010149 | -0.038145 | 0.039225 | 0.02652 | -0.011224 | -0.0035853 | -0.021518 | -0.0022666 | -0.0022903 | 0.058901 | 0.038337 | 0.050038 | -0.15462 | -0.11764 | -0.15949 | -0.080646 | -0.082062 | -0.004549 | -0.19127 | -0.053897 | 0.33918 | -0.17082 | 121.3231 | 121.5848 | 121.5193 | -0.26946 | 0.033037 | -121.7176 | 0.069686 | 0.064811 | 0.031774 | -121.719 | -121.6415 | -0.045158 | -0.3139 | 0.17041 | 0.053485 | 0.098643 | -0.052202 | -0.11768 | 0.14366 | 0.14224 | 0.21976 | 0.10667 | -121.8282 | 121.5474 | 121.8091 | 121.7436 | 0.56349 | -121.9064
1822.2969 | 121.875 | -0.24261 | 121.6599 | -0.0025182 | -0.038145 | 0.039225 | 0.026093 | -0.011224 | -0.0031579 | -0.0062567 | -0.0018394 | -0.0020767 | 0.059114 | 0.038337 | 0.049824 | -0.15462 | -0.11306 | -0.14576 | -0.076067 | -0.072904 | 0.013765 | -0.19585 | -0.044739 | 0.34376 | -0.17082 | 121.3276 | 121.5985 | 121.5376 | -0.25115 | 0.046769 | -121.7359 | 0.087997 | 0.096857 | 0.050088 | -121.7328 | -121.6461 | -0.008531 | -0.33221 | 0.19788 | 0.071796 | 0.080327 | -0.061355 | -0.12225 | 0.16655 | 0.16971 | 0.25638 | 0.12956 | -121.8557 | 121.5703 | 121.8411 | 121.7802 | 0.58638 | -121.911
1823.9844 | 121.962 | -0.19684 | 121.6324 | -0.010149 | -0.038145 | 0.039225 | 0.026093 | -0.01101 | -0.0035853 | -0.013887 | -0.0018394 | -0.0022903 | 0.059328 | 0.03791 | 0.050038 | -0.15004 | -0.11764 | -0.14118 | -0.076067 | -0.077483 | 0.009187 | -0.19585 | -0.044739 | 0.33918 | -0.16166 | 121.3322 | 121.5985 | 121.5422 | -0.2603 | 0.000992 | -121.7085 | 0.046799 | 0.055658 | 0.054666 | -121.7099 | -121.6232 | -0.063466 | -0.30017 | 0.1521 | 0.035177 | 0.098643 | -0.033889 | -0.090209 | 0.12077 | 0.11936 | 0.20603 | 0.079201 | -121.8282 | 121.5291 | 121.7953 | 121.739 | 0.53602 | -121.8927
1825.7344 | 121.8979 | -0.21057 | 121.6599 | -0.01778 | -0.038145 | 0.039011 | 0.02652 | -0.01101 | -0.0031579 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.038123 | 0.050251 | -0.14546 | -0.11306 | -0.14118 | -0.076067 | -0.072904 | 0.013765 | -0.19585 | -0.040161 | 0.33918 | -0.16166 | 121.3414 | 121.6077 | 121.5468 | -0.25572 | 0.014725 | -121.7359 | 0.06511 | 0.069391 | 0.054666 | -121.7328 | -121.6461 | -0.045154 | -0.31848 | 0.17041 | 0.04891 | 0.094064 | -0.052197 | -0.1131 | 0.1345 | 0.13767 | 0.22434 | 0.097512 | -121.8557 | 121.5519 | 121.8182 | 121.7573 | 0.54975 | -121.9156
1827.4844 | 121.9894 | -0.18768 | 121.6232 | -0.0025182 | -0.037931 | 0.039225 | 0.026307 | -0.011437 | -0.0035853 | -0.036779 | -0.002053 | -0.0022903 | 0.058901 | 0.038123 | 0.050251 | -0.14546 | -0.10848 | -0.14118 | -0.06691 | -0.077483 | 0.004608 | -0.18211 | -0.040161 | 0.33918 | -0.17082 | 121.346 | 121.6122 | 121.5376 | -0.25572 | 0.005574 | -121.6901 | 0.042222 | 0.046503 | 0.040929 | -121.7007 | -121.6186 | -0.068042 | -0.27728 | 0.14752 | 0.016864 | 0.084906 | -0.010998 | -0.085633 | 0.12077 | 0.1102 | 0.19229 | 0.079203 | -121.8053 | 121.5336 | 121.7999 | 121.7253 | 0.52687 | -121.879
1829.25 | 121.8521 | -0.25635 | 121.6873 | -0.010149 | -0.038145 | 0.038584 | 0.02652 | -0.011437 | -0.0031579 | -0.029148 | -0.002053 | -0.0025041 | 0.059114 | 0.038551 | 0.050038 | -0.14546 | -0.1039 | -0.14576 | -0.06691 | -0.068325 | 0.004608 | -0.17753 | -0.035582 | 0.3575 | -0.1525 | 121.3368 | 121.6077 | 121.5513 | -0.26488 | 0.078818 | -121.7542 | 0.11089 | 0.11059 | 0.031772 | -121.7556 | -121.6827 | -0.008535 | -0.35052 | 0.22077 | 0.10384 | 0.11238 | -0.079663 | -0.13598 | 0.18944 | 0.18802 | 0.26096 | 0.15245 | -121.8648 | 121.5931 | 121.864 | 121.8077 | 0.61385 | -121.9522
1830.9375 | 121.9162 | -0.21973 | 121.6599 | -0.0025182 | -0.038145 | 0.039225 | 0.02652 | -0.01101 | -0.0027305 | -0.0062567 | -0.002053 | -0.0025041 | 0.059328 | 0.038123 | 0.04961 | -0.14088 | -0.10848 | -0.14118 | -0.071489 | -0.063746 | 0.009187 | -0.19127 | -0.035582 | 0.33918 | -0.1525 | 121.346 | 121.6031 | 121.5513 | -0.2603 | 0.02846 | -121.7313 | 0.078845 | 0.078547 | 0.050087 | -121.7236 | -121.6507 | -0.040577 | -0.3139 | 0.18415 | 0.067223 | 0.1078 | -0.056776 | -0.10852 | 0.14824 | 0.15598 | 0.22891 | 0.11125 | -121.8511 | 121.5657 | 121.8228 | 121.7711 | 0.55891 | -121.9202
1832.6875 | 122.0169 | -0.17395 | 121.6324 | -0.0025182 | -0.038145 | 0.039011 | 0.026734 | -0.01101 | -0.0031579 | -0.013887 | -0.0018394 | -0.0018631 | 0.058687 | 0.038123 | 0.050038 | -0.1363 | -0.10848 | -0.1366 | -0.062332 | -0.068325 | 0.018344 | -0.17753 | -0.035582 | 0.34376 | -0.15708 | 121.3551 | 121.6168 | 121.5513 | -0.25572 | -0.00358 | -121.6947 | 0.037646 | 0.037349 | 0.040929 | -121.7007 | -121.614 | -0.081775 | -0.27728 | 0.13837 | 0.016867 | 0.098642 | -0.015574 | -0.081052 | 0.11162 | 0.10562 | 0.19229 | 0.06547 | -121.8099 | 121.5291 | 121.7908 | 121.7253 | 0.51771 | -121.8881
1834.4375 | 121.994 | -0.16479 | 121.6415 | -0.010149 | -0.038145 | 0.038584 | 0.026307 | -0.011224 | -0.0029443 | -0.029148 | -0.0018394 | -0.0018631 | 0.058901 | 0.038123 | 0.050038 | -0.14088 | -0.1039 | -0.14118 | -0.062332 | -0.059167 | 0.013765 | -0.17753 | -0.035582 | 0.34834 | -0.14793 | 121.3597 | 121.6168 | 121.5605 | -0.25115 | -0.012735 | -121.7039 | 0.023913 | 0.023615 | 0.03635 | -121.7007 | -121.6278 | -0.086351 | -0.28185 | 0.12921 | 0.01687 | 0.10322 | -0.02473 | -0.081051 | 0.10246 | 0.10563 | 0.17856 | 0.060894 | -121.8191 | 121.5245 | 121.7816 | 121.7253 | 0.51314 | -121.8927
1836.1875 | 121.9528 | -0.20599 | 121.669 | -0.010149 | -0.037931 | 0.03837 | 0.026734 | -0.011224 | -0.0025169 | -0.013887 | -0.0018394 | -0.0025041 | 0.059114 | 0.038123 | 0.050251 | -0.14546 | -0.099323 | -0.14118 | -0.071489 | -0.063746 | 0.018344 | -0.17753 | -0.026425 | 0.33918 | -0.14335 | 121.3597 | 121.6168 | 121.5559 | -0.24657 | 0.028464 | -121.7405 | 0.060533 | 0.064814 | 0.03635 | -121.7328 | -121.6507 | -0.040573 | -0.30932 | 0.17957 | 0.062647 | 0.10322 | -0.052195 | -0.11309 | 0.13451 | 0.14225 | 0.22434 | 0.10667 | -121.8465 | 121.5657 | 121.8228 | 121.7619 | 0.54518 | -121.9156
1837.875 | 121.8887 | -0.20599 | 121.6827 | -0.010149 | -0.037931 | 0.038584 | 0.02652 | -0.011437 | -0.0025169 | -0.021518 | -0.0016258 | -0.0025041 | 0.059114 | 0.038123 | 0.050251 | -0.13173 | -0.094744 | -0.13202 | -0.06691 | -0.063746 | 0.018344 | -0.18211 | -0.021846 | 0.34834 | -0.15708 | 121.3688 | 121.626 | 121.5651 | -0.25115 | 0.023885 | -121.7496 | 0.074268 | 0.073971 | 0.050086 | -121.7465 | -121.6644 | -0.045152 | -0.31389 | 0.18415 | 0.048911 | 0.094063 | -0.056771 | -0.11767 | 0.13908 | 0.14225 | 0.22434 | 0.11125 | -121.8648 | 121.5748 | 121.832 | 121.7711 | 0.55434 | -121.9339
1839.625 | 122.0215 | -0.17395 | 121.637 | -0.010149 | -0.038145 | 0.03837 | 0.026734 | -0.011224 | -0.0025169 | -0.029148 | -0.0018394 | -0.0022903 | 0.058901 | 0.038123 | 0.050038 | -0.1363 | -0.094744 | -0.12745 | -0.06691 | -0.063746 | 0.027501 | -0.17753 | -0.044739 | 0.35292 | -0.1525 | 121.3643 | 121.6214 | 121.5605 | -0.25572 | -0.00358 | -121.7039 | 0.037646 | 0.046505 | 0.050085 | -121.7007 | -121.6095 | -0.081775 | -0.2727 | 0.12921 | 0.021446 | 0.10322 | -0.015574 | -0.076473 | 0.10704 | 0.1102 | 0.20145 | 0.079206 | -121.8145 | 121.5382 | 121.7953 | 121.7344 | 0.52687 | -121.8927
1841.3594 | 121.8796 | -0.21973 | 121.6919 | -0.010149 | -0.037931 | 0.03837 | 0.02652 | -0.010796 | -0.0025169 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.038123 | 0.049824 | -0.1363 | -0.1039 | -0.12745 | -0.06691 | -0.059167 | 0.022922 | -0.17295 | -0.026425 | 0.35292 | -0.14793 | 121.3734 | 121.6397 | 121.5788 | -0.24199 | 0.046776 | -121.7588 | 0.083423 | 0.092282 | 0.045506 | -121.7511 | -121.669 | -0.022262 | -0.31847 | 0.1933 | 0.071802 | 0.094064 | -0.052191 | -0.11309 | 0.15282 | 0.16056 | 0.24265 | 0.11583 | -121.8648 | 121.5932 | 121.8594 | 121.7985 | 0.57265 | -121.9339
1843.0469 | 122.0352 | -0.17853 | 121.6599 | -0.025411 | -0.037931 | 0.03837 | 0.026734 | -0.011437 | -0.0023033 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.038123 | 0.050038 | -0.1363 | -0.090166 | -0.14118 | -0.062332 | -0.054588 | 0.022922 | -0.17295 | -0.026425 | 0.34834 | -0.14793 | 121.3734 | 121.626 | 121.5742 | -0.23741 | 0.005577 | -121.7222 | 0.042224 | 0.037348 | 0.031771 | -121.7144 | -121.6369 | -0.058882 | -0.28643 | 0.1521 | 0.030603 | 0.089485 | -0.033883 | -0.085625 | 0.1162 | 0.12394 | 0.20145 | 0.088362 | -121.8328 | 121.552 | 121.8045 | 121.7528 | 0.52687 | -121.8973
1844.75 | 122.0306 | -0.17853 | 121.6599 | -0.01778 | -0.037718 | 0.037943 | 0.026734 | -0.011224 | -0.0020895 | -0.021518 | -0.0022666 | -0.0022903 | 0.058901 | 0.038337 | 0.049824 | -0.1363 | -0.090166 | -0.13202 | -0.06691 | -0.059167 | 0.027501 | -0.16837 | -0.026425 | 0.34376 | -0.14335 | 121.378 | 121.6351 | 121.5788 | -0.23741 | 0.010155 | -121.7268 | 0.042224 | 0.046505 | 0.03635 | -121.719 | -121.6324 | -0.058882 | -0.28185 | 0.1521 | 0.035181 | 0.094063 | -0.024726 | -0.081046 | 0.11162 | 0.11936 | 0.20603 | 0.088362 | -121.8282 | 121.5565 | 121.8137 | 121.7573 | 0.52229 | -121.8973
1846.5 | 121.8933 | -0.21515 | 121.7285 | -0.010149 | -0.037718 | 0.038157 | 0.026734 | -0.011437 | -0.0020895 | -0.013887 | -0.0018394 | -0.0020767 | 0.059114 | 0.038337 | 0.049824 | -0.13173 | -0.090166 | -0.12287 | -0.057754 | -0.059167 | 0.022922 | -0.17295 | -0.031003 | 0.34376 | -0.14793 | 121.3917 | 121.6443 | 121.5834 | -0.24657 | 0.042198 | -121.7863 | 0.083423 | 0.092283 | 0.050085 | -121.7877 | -121.7056 | -0.031418 | -0.33678 | 0.18415 | 0.067224 | 0.098642 | -0.084234 | -0.14513 | 0.1574 | 0.15598 | 0.23807 | 0.12498 | -121.9015 | 121.6069 | 121.8594 | 121.7985 | 0.55891 | -121.9751
1848.2812 | 122.0123 | -0.18768 | 121.6965 | -0.01778 | -0.037718 | 0.037729 | 0.026734 | -0.011651 | -0.0016623 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.038764 | 0.049824 | -0.1363 | -0.094744 | -0.12745 | -0.057754 | -0.054588 | 0.022922 | -0.17295 | -0.031003 | 0.34834 | -0.14793 | 121.3872 | 121.6534 | 121.5788 | -0.24657 | 0.014732 | -121.7542 | 0.051379 | 0.060238 | 0.045506 | -121.7511 | -121.6736 | -0.058884 | -0.30931 | 0.15668 | 0.039758 | 0.098642 | -0.043032 | -0.11767 | 0.12993 | 0.13309 | 0.2106 | 0.092939 | -121.8694 | 121.5748 | 121.8411 | 121.7665 | 0.53602 | -121.943
1849.9688 | 121.9757 | -0.1831 | 121.6873 | -0.010149 | -0.037931 | 0.038157 | 0.026948 | -0.011437 | -0.0018759 | -0.021518 | -0.0018394 | -0.0022903 | 0.059114 | 0.038337 | 0.050038 | -0.13173 | -0.090166 | -0.12287 | -0.057754 | -0.059167 | 0.027501 | -0.17295 | -0.026425 | 0.35292 | -0.14793 | 121.3872 | 121.6489 | 121.588 | -0.24199 | 0.010154 | -121.7451 | 0.051379 | 0.060239 | 0.050085 | -121.7465 | -121.6598 | -0.058884 | -0.30016 | 0.15668 | 0.03518 | 0.094064 | -0.038456 | -0.099355 | 0.12535 | 0.12394 | 0.21061 | 0.092939 | -121.8603 | 121.5703 | 121.832 | 121.7711 | 0.53602 | -121.9293
1851.7031 | 121.8933 | -0.21515 | 121.701 | -0.010149 | -0.037718 | 0.037943 | 0.02652 | -0.011224 | -0.0020895 | -0.013887 | -0.0018394 | -0.0025041 | 0.059114 | 0.038123 | 0.049824 | -0.13173 | -0.090166 | -0.12745 | -0.053175 | -0.059167 | 0.036658 | -0.17753 | -0.021846 | 0.34376 | -0.14335 | 121.3963 | 121.658 | 121.5925 | -0.23741 | 0.037619 | -121.7542 | 0.083423 | 0.087704 | 0.050085 | -121.7602 | -121.6644 | -0.022261 | -0.30473 | 0.1933 | 0.071802 | 0.094063 | -0.043032 | -0.10851 | 0.16197 | 0.15598 | 0.25181 | 0.12498 | -121.8786 | 121.6115 | 121.8732 | 121.8077 | 0.55891 | -121.9385
1853.4531 | 121.9437 | -0.19684 | 121.6827 | -0.01778 | -0.037718 | 0.037943 | 0.027161 | -0.011224 | -0.0020895 | -0.021518 | -0.0018394 | -0.0025041 | 0.059542 | 0.038337 | 0.050465 | -0.12715 | -0.085587 | -0.12287 | -0.057754 | -0.059167 | 0.018344 | -0.17295 | -0.017267 | 0.3575 | -0.14335 | 121.3917 | 121.658 | 121.5925 | -0.23741 | 0.023887 | -121.7405 | 0.069691 | 0.073972 | 0.050085 | -121.7419 | -121.6644 | -0.040572 | -0.291 | 0.17957 | 0.053491 | 0.094063 | -0.024721 | -0.090198 | 0.13908 | 0.13767 | 0.21518 | 0.11125 | -121.8557 | 121.5886 | 121.8549 | 121.7894 | 0.55434 | -121.9201
1855.2188 | 121.9025 | -0.21515 | 121.7194 | -0.010149 | -0.037718 | 0.037943 | 0.026734 | -0.011651 | -0.0020895 | -0.0062567 | -0.0016258 | -0.0025041 | 0.058901 | 0.038337 | 0.050251 | -0.12715 | -0.085587 | -0.12287 | -0.053175 | -0.063746 | 0.03208 | -0.17753 | -0.017267 | 0.34834 | -0.14335 | 121.4009 | 121.658 | 121.5971 | -0.24657 | 0.037619 | -121.7725 | 0.088002 | 0.092283 | 0.054664 | -121.7831 | -121.6873 | -0.031418 | -0.31846 | 0.19788 | 0.071802 | 0.10322 | -0.061342 | -0.12224 | 0.16197 | 0.1514 | 0.24723 | 0.12956 | -121.8969 | 121.616 | 121.8732 | 121.8123 | 0.56349 | -121.9659
1856.9062 | 121.994 | -0.16937 | 121.6324 | -0.01778 | -0.037504 | 0.037729 | 0.026948 | -0.011865 | -0.0010213 | -0.021518 | -0.002053 | -0.0025041 | 0.059328 | 0.038551 | 0.04961 | -0.13173 | -0.094744 | -0.1366 | -0.057754 | -0.068325 | 0.027501 | -0.17295 | -0.031003 | 0.34834 | -0.1525 | 121.3688 | 121.626 | 121.5651 | -0.24657 | -0.003578 | -121.6901 | 0.037647 | 0.032772 | 0.03635 | -121.7007 | -121.6049 | -0.077194 | -0.26354 | 0.13837 | 0.016869 | 0.094063 | -0.006417 | -0.067316 | 0.11162 | 0.10105 | 0.19687 | 0.074629 | -121.8053 | 121.5382 | 121.7953 | 121.7344 | 0.51771 | -121.879
1858.6562 | 121.962 | -0.19226 | 121.5958 | -0.010149 | -0.037718 | 0.036874 | 0.026948 | -0.011437 | -0.00059393 | -0.021518 | -0.0022666 | -0.0020767 | 0.058901 | 0.038551 | 0.050038 | -0.14088 | -0.099323 | -0.13202 | -0.057754 | -0.063746 | 0.018344 | -0.17295 | -0.035582 | 0.34376 | -0.1525 | 121.3322 | 121.5893 | 121.5193 | -0.25115 | 0.01931 | -121.6535 | 0.051379 | 0.060238 | 0.040928 | -121.6595 | -121.5774 | -0.058885 | -0.26355 | 0.15668 | 0.039757 | 0.098642 | -0.006425 | -0.076481 | 0.13451 | 0.12851 | 0.2106 | 0.092938 | -121.7687 | 121.5245 | 121.7816 | 121.7115 | 0.53602 | -121.8469
1860.3906 | 121.8018 | -0.21057 | 121.6232 | -0.010149 | -0.037077 | 0.036661 | 0.027375 | -0.011224 | -0.00059393 | -0.013887 | -0.0018394 | -0.0020767 | 0.059114 | 0.038123 | 0.04961 | -0.14088 | -0.099323 | -0.12745 | -0.062332 | -0.068325 | 0.018344 | -0.18211 | -0.031003 | 0.35292 | -0.14793 | 121.3047 | 121.5573 | 121.501 | -0.25115 | 0.028462 | -121.6856 | 0.069689 | 0.083126 | 0.054664 | -121.6916 | -121.6049 | -0.040575 | -0.31848 | 0.17957 | 0.062646 | 0.10322 | -0.065941 | -0.12226 | 0.14824 | 0.14225 | 0.22892 | 0.11125 | -121.8053 | 121.5153 | 121.7679 | 121.7115 | 0.56349 | -121.8744
1862.1562 | 121.8109 | -0.21057 | 121.6324 | 0.0051128 | -0.037504 | 0.036661 | 0.027161 | -0.011224 | -0.00059393 | -0.021518 | -0.0022666 | -0.0020767 | 0.059114 | 0.038123 | 0.04961 | -0.14088 | -0.090166 | -0.13202 | -0.06691 | -0.063746 | 0.013765 | -0.17295 | -0.035582 | 0.34376 | -0.14793 | 121.2864 | 121.5527 | 121.4872 | -0.24657 | 0.03762 | -121.6993 | 0.069689 | 0.078548 | 0.040928 | -121.6961 | -121.6186 | -0.035996 | -0.34595 | 0.17499 | 0.062646 | 0.098642 | -0.079675 | -0.14515 | 0.14366 | 0.14683 | 0.22434 | 0.12041 | -121.8053 | 121.497 | 121.7633 | 121.6978 | 0.55433 | -121.879
1863.8438 | 121.9162 | -0.17395 | 121.5637 | -0.010149 | -0.037077 | 0.036233 | 0.027375 | -0.011224 | -0.00038033 | -0.029148 | -0.002053 | -0.0020767 | 0.058901 | 0.038123 | 0.049824 | -0.1363 | -0.099323 | -0.1366 | -0.062332 | -0.063746 | 0.018344 | -0.17753 | -0.035582 | 0.35292 | -0.1525 | 121.2819 | 121.5344 | 121.4643 | -0.24199 | -0.00358 | -121.6261 | 0.037646 | 0.037349 | 0.040929 | -121.6275 | -121.5454 | -0.068039 | -0.28187 | 0.13837 | 0.021446 | 0.089485 | -0.029325 | -0.099381 | 0.11162 | 0.1102 | 0.19229 | 0.074627 | -121.7413 | 121.4558 | 121.7083 | 121.6383 | 0.52687 | -121.8057
1865.5938 | 121.8521 | -0.17853 | 121.5454 | -0.010149 | -0.037718 | 0.037088 | 0.027375 | -0.011437 | -0.00059393 | -0.021518 | -0.002053 | -0.0025041 | 0.059328 | 0.038337 | 0.049824 | -0.14088 | -0.094744 | -0.1366 | -0.057754 | -0.054588 | 0.022922 | -0.16837 | -0.031003 | 0.35292 | -0.1525 | 121.2773 | 121.5344 | 121.4689 | -0.24657 | 0.010155 | -121.6032 | 0.037646 | 0.041927 | 0.031772 | -121.6 | -121.5225 | -0.068039 | -0.26813 | 0.14752 | 0.026024 | 0.094063 | -0.011014 | -0.076492 | 0.12077 | 0.12394 | 0.20145 | 0.083784 | -121.7138 | 121.4558 | 121.7129 | 121.6474 | 0.53145 | -121.792
1867.3438 | 121.8338 | -0.19226 | 121.5683 | -0.010149 | -0.03729 | 0.036874 | 0.027161 | -0.011865 | -0.00059393 | -0.013887 | -0.002053 | -0.0025041 | 0.058901 | 0.038337 | 0.049824 | -0.1363 | -0.090166 | -0.13202 | -0.062332 | -0.054588 | 0.018344 | -0.17295 | -0.031003 | 0.34834 | -0.14335 | 121.2727 | 121.5252 | 121.4506 | -0.25115 | 0.01931 | -121.6306 | 0.055957 | 0.060238 | 0.040928 | -121.6229 | -121.55 | -0.058885 | -0.2956 | 0.16126 | 0.048914 | 0.1078 | -0.043059 | -0.11769 | 0.12993 | 0.13767 | 0.2106 | 0.10209 | -121.7412 | 121.465 | 121.7175 | 121.6429 | 0.5406 | -121.8194
1869.1094 | 121.8338 | -0.18768 | 121.5637 | -0.010149 | -0.03729 | 0.036874 | 0.026948 | -0.011224 | -0.00038033 | -0.021518 | -0.0018394 | -0.0025041 | 0.059328 | 0.038337 | 0.050038 | -0.13173 | -0.099323 | -0.13202 | -0.057754 | -0.063746 | 0.027501 | -0.17295 | -0.021846 | 0.3575 | -0.14793 | 121.2498 | 121.5161 | 121.446 | -0.24199 | 0.014732 | -121.6215 | 0.055957 | 0.05566 | 0.040928 | -121.6275 | -121.5362 | -0.054306 | -0.31392 | 0.16584 | 0.039758 | 0.094064 | -0.047639 | -0.1177 | 0.12993 | 0.12394 | 0.21518 | 0.08836 | -121.7367 | 121.4375 | 121.7038 | 121.6337 | 0.54518 | -121.8057
1870.7969 | 121.7651 | -0.21057 | 121.5317 | -0.010149 | -0.03729 | 0.036447 | 0.027375 | -0.011437 | -0.00059393 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.038337 | 0.050251 | -0.1363 | -0.090166 | -0.12745 | -0.057754 | -0.063746 | 0.03208 | -0.16837 | -0.026425 | 0.3575 | -0.14335 | 121.2544 | 121.5069 | 121.4414 | -0.24657 | 0.042198 | -121.5894 | 0.074267 | 0.083126 | 0.040928 | -121.5954 | -121.4996 | -0.035996 | -0.27729 | 0.18415 | 0.067224 | 0.10322 | -0.024753 | -0.09023 | 0.15282 | 0.14683 | 0.24265 | 0.12041 | -121.7001 | 121.465 | 121.7175 | 121.652 | 0.56807 | -121.7782
1872.5469 | 121.7606 | -0.20142 | 121.5408 | -0.01778 | -0.03729 | 0.036661 | 0.027161 | -0.011437 | -0.00016673 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.038337 | 0.049397 | -0.12715 | -0.099323 | -0.12745 | -0.044018 | -0.054588 | 0.022922 | -0.17753 | -0.026425 | 0.34834 | -0.14793 | 121.2406 | 121.5023 | 121.446 | -0.24199 | 0.023886 | -121.5849 | 0.074269 | 0.073971 | 0.050085 | -121.5954 | -121.5179 | -0.040573 | -0.30019 | 0.17499 | 0.053491 | 0.094064 | -0.038487 | -0.094808 | 0.1574 | 0.14683 | 0.22434 | 0.10209 | -121.7184 | 121.4421 | 121.7038 | 121.6474 | 0.54976 | -121.7828
1874.2969 | 121.7926 | -0.2243 | 121.5317 | -0.0025182 | -0.03729 | 0.036661 | 0.027589 | -0.011437 | 4.7068e-05 | -0.013887 | -0.0022666 | -0.0020767 | 0.058901 | 0.038551 | 0.049824 | -0.12257 | -0.090166 | -0.13202 | -0.06691 | -0.054588 | 0.03208 | -0.16837 | -0.026425 | 0.35292 | -0.14793 | 121.2361 | 121.4932 | 121.4369 | -0.23741 | 0.055931 | -121.5986 | 0.10174 | 0.092281 | 0.03635 | -121.5863 | -121.4996 | -0.013106 | -0.29561 | 0.19788 | 0.076379 | 0.089485 | -0.038488 | -0.094809 | 0.15739 | 0.16972 | 0.25638 | 0.13414 | -121.7001 | 121.4604 | 121.7175 | 121.6612 | 0.57722 | -121.7691
1876 | 121.7834 | -0.20599 | 121.5729 | -0.010149 | -0.03729 | 0.037088 | 0.027375 | -0.011437 | 4.7068e-05 | -0.021518 | -0.0016258 | -0.0025041 | 0.058901 | 0.038551 | 0.049824 | -0.12257 | -0.090166 | -0.12745 | -0.057754 | -0.054588 | 0.027501 | -0.16837 | -0.017267 | 0.34834 | -0.14335 | 121.2361 | 121.4932 | 121.4277 | -0.23741 | 0.037621 | -121.6306 | 0.083425 | 0.078549 | 0.040928 | -121.6275 | -121.5454 | -0.031416 | -0.33681 | 0.18873 | 0.062647 | 0.094063 | -0.079687 | -0.14516 | 0.14824 | 0.15141 | 0.2335 | 0.11583 | -121.7412 | 121.4421 | 121.6992 | 121.6337 | 0.55434 | -121.8103
1877.75 | 121.875 | -0.19226 | 121.5225 | -0.01778 | -0.037504 | 0.036661 | 0.026948 | -0.011437 | 0.00068807 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.038337 | 0.04961 | -0.1363 | -0.094744 | -0.13202 | -0.062332 | -0.059167 | 0.018344 | -0.17295 | -0.031003 | 0.35292 | -0.1525 | 121.2315 | 121.4886 | 121.4277 | -0.24657 | 0.01931 | -121.5849 | 0.055957 | 0.060238 | 0.040928 | -121.5817 | -121.5042 | -0.054306 | -0.29103 | 0.16126 | 0.039757 | 0.094063 | -0.033912 | -0.094811 | 0.12993 | 0.13309 | 0.2106 | 0.097517 | -121.6955 | 121.4238 | 121.6809 | 121.62 | 0.54518 | -121.7691
1879.5156 | 121.7377 | -0.21057 | 121.5317 | 0.0051128 | -0.037718 | 0.036661 | 0.027161 | -0.011437 | 0.00068807 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.038123 | 0.050038 | -0.12715 | -0.094744 | -0.13202 | -0.053175 | -0.054588 | 0.027501 | -0.17753 | -0.026425 | 0.34376 | -0.14335 | 121.2269 | 121.4886 | 121.4186 | -0.25572 | 0.033041 | -121.5849 | 0.083424 | 0.078548 | 0.045507 | -121.5863 | -121.5042 | -0.045154 | -0.30477 | 0.18415 | 0.067224 | 0.11238 | -0.043067 | -0.11312 | 0.1574 | 0.15598 | 0.23807 | 0.11583 | -121.7092 | 121.4375 | 121.6992 | 121.6291 | 0.55433 | -121.7874
1881.2656 | 121.8109 | -0.1831 | 121.5271 | -0.01778 | -0.037718 | 0.036661 | 0.026948 | -0.011224 | 0.00068807 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.038123 | 0.04961 | -0.12715 | -0.094744 | -0.12287 | -0.053175 | -0.054588 | 0.022922 | -0.17295 | -0.021846 | 0.3575 | -0.14793 | 121.2223 | 121.4749 | 121.4186 | -0.24199 | 0.010154 | -121.5803 | 0.055958 | 0.060239 | 0.050085 | -121.5817 | -121.5042 | -0.058884 | -0.30477 | 0.16126 | 0.03518 | 0.094064 | -0.052226 | -0.10855 | 0.12993 | 0.12852 | 0.20603 | 0.088361 | -121.7001 | 121.4054 | 121.658 | 121.6017 | 0.5406 | -121.7691
1882.9531 | 121.843 | -0.19226 | 121.5042 | -0.0025182 | -0.037718 | 0.036874 | 0.027161 | -0.011224 | 0.00047427 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.038551 | 0.04961 | -0.13173 | -0.094744 | -0.13202 | -0.057754 | -0.054588 | 0.027501 | -0.17295 | -0.026425 | 0.35292 | -0.14793 | 121.2178 | 121.4795 | 121.4094 | -0.24657 | 0.01931 | -121.562 | 0.060535 | 0.060238 | 0.040928 | -121.5588 | -121.4767 | -0.054306 | -0.28646 | 0.16584 | 0.044336 | 0.098642 | -0.024758 | -0.094815 | 0.13451 | 0.13767 | 0.21976 | 0.097517 | -121.6772 | 121.41 | 121.6717 | 121.6017 | 0.54518 | -121.7508
1884.7031 | 121.8109 | -0.18768 | 121.4676 | -0.01778 | -0.037718 | 0.036874 | 0.027375 | -0.011437 | 0.00026067 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.038337 | 0.049824 | -0.12715 | -0.094744 | -0.13202 | -0.057754 | -0.054588 | 0.027501 | -0.16837 | -0.026425 | 0.34834 | -0.14335 | 121.2223 | 121.4703 | 121.4186 | -0.23741 | 0.01931 | -121.5253 | 0.060536 | 0.05566 | 0.03635 | -121.5222 | -121.4401 | -0.049727 | -0.24526 | 0.16126 | 0.044336 | 0.094063 | 0.002705 | -0.049036 | 0.12993 | 0.13309 | 0.21518 | 0.092939 | -121.636 | 121.41 | 121.658 | 121.6062 | 0.53602 | -121.705
1886.4531 | 121.7148 | -0.21515 | 121.5454 | -0.010149 | -0.037504 | 0.037088 | 0.027161 | -0.011651 | 0.00026067 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.038337 | 0.04961 | -0.12715 | -0.094744 | -0.12287 | -0.053175 | -0.054588 | 0.03208 | -0.16837 | -0.026425 | 0.34834 | -0.14335 | 121.2132 | 121.4703 | 121.4094 | -0.24199 | 0.046776 | -121.5986 | 0.088002 | 0.092283 | 0.045507 | -121.6 | -121.5133 | -0.02684 | -0.33223 | 0.18872 | 0.071802 | 0.098642 | -0.075115 | -0.13601 | 0.16197 | 0.16056 | 0.24723 | 0.12041 | -121.7138 | 121.4283 | 121.6854 | 121.6245 | 0.56349 | -121.7874
1888.2031 | 121.7148 | -0.23804 | 121.5134 | -0.010149 | -0.037931 | 0.037088 | 0.027161 | -0.01101 | 0.00047427 | -0.013887 | -0.002053 | -0.0025041 | 0.058901 | 0.038551 | 0.04961 | -0.13173 | -0.085587 | -0.13202 | -0.053175 | -0.054588 | 0.018344 | -0.16837 | -0.031003 | 0.34834 | -0.14335 | 121.2132 | 121.4657 | 121.414 | -0.23741 | 0.069664 | -121.5665 | 0.10631 | 0.10601 | 0.03635 | -121.568 | -121.495 | 0.000627 | -0.30019 | 0.20703 | 0.09469 | 0.094063 | -0.04765 | -0.099392 | 0.18486 | 0.18345 | 0.25638 | 0.15245 | -121.6817 | 121.4512 | 121.7038 | 121.652 | 0.58638 | -121.7508
1889.8906 | 121.7697 | -0.20142 | 121.4996 | 0.0051128 | -0.037718 | 0.036447 | 0.027375 | -0.011437 | 0.0011153 | -0.013887 | -0.0016258 | -0.0022903 | 0.058901 | 0.038551 | 0.04961 | -0.12715 | -0.094744 | -0.13202 | -0.06691 | -0.050009 | 0.022922 | -0.16837 | -0.021846 | 0.35292 | -0.14335 | 121.204 | 121.4611 | 121.4048 | -0.24657 | 0.033043 | -121.5665 | 0.074269 | 0.069393 | 0.03635 | -121.5496 | -121.4767 | -0.045151 | -0.29561 | 0.17957 | 0.058069 | 0.10322 | -0.038496 | -0.094816 | 0.13451 | 0.15141 | 0.22434 | 0.10667 | -121.668 | 121.4054 | 121.6626 | 121.6062 | 0.55434 | -121.7462
1891.6406 | 121.7194 | -0.20599 | 121.5225 | -0.010149 | -0.037718 | 0.037088 | 0.027375 | -0.011437 | 0.00068807 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.038551 | 0.04961 | -0.11799 | -0.085587 | -0.12745 | -0.053175 | -0.054588 | 0.027501 | -0.15921 | -0.021846 | 0.35292 | -0.14335 | 121.2132 | 121.4657 | 121.4094 | -0.23741 | 0.046779 | -121.5757 | 0.088003 | 0.078549 | 0.03177 | -121.5771 | -121.495 | -0.031416 | -0.30934 | 0.18415 | 0.062647 | 0.094063 | -0.056805 | -0.11313 | 0.15282 | 0.15141 | 0.2335 | 0.12041 | -121.6817 | 121.4192 | 121.6717 | 121.6154 | 0.55891 | -121.7599
1893.4062 | 121.8063 | -0.17853 | 121.4859 | -0.010149 | -0.037718 | 0.037302 | 0.026948 | -0.011437 | 0.00026067 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.038337 | 0.04961 | -0.12715 | -0.094744 | -0.12287 | -0.053175 | -0.054588 | 0.027501 | -0.16837 | -0.017267 | 0.3575 | -0.13877 | 121.2132 | 121.4611 | 121.4048 | -0.24199 | 0.010155 | -121.5391 | 0.051381 | 0.055662 | 0.045507 | -121.5405 | -121.4584 | -0.063461 | -0.27272 | 0.16126 | 0.03976 | 0.10322 | -0.024763 | -0.081083 | 0.12535 | 0.12394 | 0.20603 | 0.083784 | -121.6543 | 121.3917 | 121.6397 | 121.5833 | 0.53603 | -121.7279
1895.1562 | 121.8338 | -0.14648 | 121.4859 | -0.010149 | -0.038572 | 0.038157 | 0.026734 | -0.011437 | -0.0014487 | -0.0062567 | -0.0018394 | -0.0025041 | 0.058473 | 0.038123 | 0.049397 | -0.10426 | -0.067272 | -0.10913 | -0.034862 | -0.040851 | 0.054973 | -0.16837 | 0.001048 | 0.34834 | -0.12045 | 121.1033 | 121.365 | 121.3636 | -0.21452 | -0.021889 | -121.5208 | 0.042229 | 0.037352 | 0.059241 | -121.5268 | -121.4309 | -0.068032 | -0.38261 | 0.14753 | 0.026031 | 0.094063 | -0.12091 | -0.12229 | 0.11162 | 0.10563 | 0.20146 | 0.079212 | -121.6543 | 121.2498 | 121.5115 | 121.5101 | 0.49483 | -121.7004
1896.8438 | 121.843 | -0.16479 | 121.5454 | -0.0025182 | -0.038145 | 0.037943 | 0.02652 | -0.011437 | -0.0012349 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.038764 | 0.049824 | -0.10883 | -0.071851 | -0.10913 | -0.03944 | -0.031693 | 0.050394 | -0.15921 | -0.003531 | 0.3575 | -0.12961 | 121.2727 | 121.5298 | 121.4643 | -0.2191 | 0.00558 | -121.5849 | 0.055961 | 0.055663 | 0.050083 | -121.5771 | -121.495 | -0.0543 | -0.27271 | 0.16126 | 0.035185 | 0.089485 | -0.015593 | -0.08107 | 0.12535 | 0.1331 | 0.21519 | 0.092944 | -121.7046 | 121.4375 | 121.6946 | 121.6291 | 0.52229 | -121.7645
1898.5938 | 121.8384 | -0.19226 | 121.6141 | -0.010149 | -0.038572 | 0.037943 | 0.026734 | -0.01101 | -0.0010213 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.038337 | 0.050038 | -0.10883 | -0.07643 | -0.099975 | -0.03944 | -0.036272 | 0.045815 | -0.15464 | -0.003531 | 0.35292 | -0.12045 | 121.3047 | 121.5664 | 121.501 | -0.22367 | 0.037625 | -121.6535 | 0.083427 | 0.092286 | 0.054661 | -121.6503 | -121.5683 | -0.031412 | -0.30933 | 0.18873 | 0.071808 | 0.10322 | -0.047629 | -0.11311 | 0.15282 | 0.15599 | 0.23808 | 0.11583 | -121.7687 | 121.497 | 121.7587 | 121.6932 | 0.54518 | -121.8377
1900.3594 | 121.875 | -0.16479 | 121.637 | -0.01778 | -0.038359 | 0.037943 | 0.027161 | -0.011437 | -0.0012349 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.038764 | 0.050038 | -0.10883 | -0.071851 | -0.10913 | -0.034862 | -0.022536 | 0.054973 | -0.15464 | 0.001048 | 0.35292 | -0.11587 | 121.3231 | 121.5802 | 121.5193 | -0.22367 | 0.010159 | -121.6718 | 0.055961 | 0.055663 | 0.045504 | -121.6595 | -121.582 | -0.058878 | -0.3139 | 0.16584 | 0.048921 | 0.1078 | -0.056781 | -0.11768 | 0.12993 | 0.14226 | 0.21977 | 0.092944 | -121.7916 | 121.4879 | 121.745 | 121.6841 | 0.51772 | -121.8606
1902.1094 | 121.8796 | -0.18768 | 121.6507 | -0.010149 | -0.038572 | 0.037943 | 0.026734 | -0.011437 | -0.00080773 | -0.021518 | -0.0022666 | -0.0022903 | 0.059114 | 0.038551 | 0.049824 | -0.10426 | -0.07643 | -0.11371 | -0.034862 | -0.040851 | 0.045815 | -0.15464 | 0.001048 | 0.35292 | -0.12503 | 121.3368 | 121.5893 | 121.533 | -0.2191 | 0.033047 | -121.6856 | 0.083428 | 0.073973 | 0.040926 | -121.6915 | -121.6049 | -0.031412 | -0.3139 | 0.18873 | 0.062651 | 0.094063 | -0.061357 | -0.11768 | 0.15282 | 0.14683 | 0.2335 | 0.11125 | -121.8053 | 121.5245 | 121.777 | 121.7207 | 0.5406 | -121.8698
1903.7969 | 121.8246 | -0.17395 | 121.637 | -0.025411 | -0.038572 | 0.03837 | 0.026307 | -0.011224 | -0.00080773 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.038551 | 0.049824 | -0.10883 | -0.071851 | -0.10455 | -0.03944 | -0.036272 | 0.045815 | -0.15006 | -0.003531 | 0.3575 | -0.12503 | 121.346 | 121.5985 | 121.5422 | -0.2191 | 0.023893 | -121.6764 | 0.065116 | 0.069397 | 0.045504 | -121.6732 | -121.5911 | -0.045145 | -0.29101 | 0.17042 | 0.048918 | 0.094063 | -0.038467 | -0.094787 | 0.13451 | 0.13768 | 0.21976 | 0.1021 | -121.787 | 121.5199 | 121.7724 | 121.7161 | 0.53145 | -121.8561
1905.5469 | 121.8887 | -0.18768 | 121.6827 | -0.0025182 | -0.038359 | 0.03837 | 0.026948 | -0.011651 | -0.0012349 | -0.0062567 | -0.002053 | -0.0020767 | 0.058901 | 0.038551 | 0.050251 | -0.10883 | -0.071851 | -0.10913 | -0.03944 | -0.040851 | 0.050394 | -0.15006 | 0.005626 | 0.35292 | -0.12503 | 121.3551 | 121.6122 | 121.5513 | -0.2191 | 0.037626 | -121.7222 | 0.078849 | 0.078551 | 0.040925 | -121.7236 | -121.6323 | -0.031412 | -0.32763 | 0.19331 | 0.062651 | 0.094063 | -0.070507 | -0.13141 | 0.14824 | 0.14683 | 0.23808 | 0.11583 | -121.8328 | 121.5428 | 121.7999 | 121.739 | 0.5406 | -121.9018
1907.2969 | 121.962 | -0.15564 | 121.6644 | -0.0025182 | -0.038572 | 0.038584 | 0.026734 | -0.011224 | -0.0010213 | -0.036779 | -0.002053 | -0.0027177 | 0.058687 | 0.038764 | 0.050038 | -0.10883 | -0.062694 | -0.090818 | -0.034862 | -0.027115 | 0.050394 | -0.14548 | 0.001048 | 0.35292 | -0.12503 | 121.3643 | 121.626 | 121.5605 | -0.2191 | 0.010162 | -121.6993 | 0.046806 | 0.064822 | 0.05466 | -121.6915 | -121.614 | -0.063455 | -0.30016 | 0.15669 | 0.030608 | 0.094063 | -0.038461 | -0.10394 | 0.12078 | 0.12853 | 0.20603 | 0.092946 | -121.8099 | 121.5199 | 121.7816 | 121.7161 | 0.50856 | -121.8835
1909 | 121.9849 | -0.15564 | 121.6415 | -0.010149 | -0.038572 | 0.038157 | 0.026734 | -0.011437 | -0.00038033 | -0.021518 | -0.0018394 | -0.0020767 | 0.058901 | 0.038551 | 0.049824 | -0.10883 | -0.067272 | -0.10913 | -0.030283 | -0.040851 | 0.045815 | -0.14548 | -0.00811 | 0.35292 | -0.12045 | 121.378 | 121.6351 | 121.5696 | -0.2191 | 0.010162 | -121.6718 | 0.046806 | 0.046508 | 0.036346 | -121.6824 | -121.5957 | -0.063455 | -0.26354 | 0.14753 | 0.035187 | 0.098642 | -0.006416 | -0.071893 | 0.12536 | 0.11479 | 0.20145 | 0.088368 | -121.787 | 121.5336 | 121.7908 | 121.7253 | 0.50856 | -121.8606
1910.75 | 121.875 | -0.20142 | 121.6965 | -0.0025182 | -0.038145 | 0.037302 | 0.027161 | -0.011437 | 0.00090167 | -0.021518 | -0.002053 | -0.0025041 | 0.059114 | 0.038764 | 0.050038 | -0.11341 | -0.081008 | -0.11371 | -0.03944 | -0.04543 | 0.036658 | -0.15921 | -0.021846 | 0.36208 | -0.12961 | 121.3688 | 121.6305 | 121.5742 | -0.23283 | 0.042201 | -121.7359 | 0.088004 | 0.087706 | 0.045505 | -121.7419 | -121.6598 | -0.031415 | -0.32763 | 0.17957 | 0.071806 | 0.10322 | -0.065925 | -0.12225 | 0.16198 | 0.15599 | 0.23807 | 0.12041 | -121.8557 | 121.5703 | 121.832 | 121.7756 | 0.56349 | -121.9293
1912.5 | 121.9482 | -0.16937 | 121.6873 | -0.025411 | -0.038145 | 0.037516 | 0.026734 | -0.011224 | 0.00068807 | -0.029148 | -0.0016258 | -0.0022903 | 0.058687 | 0.038551 | 0.050038 | -0.11341 | -0.085587 | -0.11371 | -0.044018 | -0.040851 | 0.036658 | -0.15464 | -0.017267 | 0.35292 | -0.13877 | 121.378 | 121.6489 | 121.5742 | -0.22367 | 0.014737 | -121.7313 | 0.055961 | 0.055663 | 0.040926 | -121.7282 | -121.6507 | -0.0543 | -0.30931 | 0.15211 | 0.030605 | 0.084905 | -0.038456 | -0.11309 | 0.12535 | 0.12852 | 0.20603 | 0.083786 | -121.842 | 121.5474 | 121.8182 | 121.7436 | 0.52229 | -121.911
1914.25 | 121.9849 | -0.16479 | 121.6965 | -0.010149 | -0.038359 | 0.037729 | 0.026948 | -0.011437 | 0.0013291 | -0.029148 | -0.0018394 | -0.0022903 | 0.058901 | 0.038551 | 0.049824 | -0.11341 | -0.081008 | -0.11371 | -0.044018 | -0.04543 | 0.036658 | -0.14548 | -0.017267 | 0.3575 | -0.13419 | 121.3917 | 121.6534 | 121.5834 | -0.23283 | 0.019317 | -121.7405 | 0.051383 | 0.051085 | 0.031768 | -121.7419 | -121.6598 | -0.068036 | -0.30473 | 0.14753 | 0.030606 | 0.098642 | -0.043032 | -0.11309 | 0.12078 | 0.11936 | 0.20145 | 0.083787 | -121.8419 | 121.5565 | 121.8182 | 121.7482 | 0.52229 | -121.9293
1915.9375 | 121.9757 | -0.13733 | 121.6919 | -0.01778 | -0.038359 | 0.037729 | 0.027161 | -0.011224 | 0.00068807 | -0.021518 | -0.002053 | -0.0022903 | 0.058473 | 0.038551 | 0.050038 | -0.10883 | -0.081008 | -0.11371 | -0.03944 | -0.040851 | 0.036658 | -0.15464 | -0.012689 | 0.36208 | -0.12961 | 121.3917 | 121.6443 | 121.588 | -0.23283 | -0.017307 | -121.7313 | 0.028495 | 0.023619 | 0.040926 | -121.7327 | -121.6552 | -0.095502 | -0.30016 | 0.12464 | 0.007719 | 0.10322 | -0.047613 | -0.10393 | 0.097889 | 0.096478 | 0.17399 | 0.056321 | -121.8465 | 121.5291 | 121.7816 | 121.7253 | 0.49941 | -121.9247
1917.6719 | 121.9025 | -0.20599 | 121.701 | -0.01778 | -0.038359 | 0.037729 | 0.026948 | -0.011437 | 0.00090167 | -0.021518 | -0.002053 | -0.0022903 | 0.058473 | 0.038764 | 0.050038 | -0.11341 | -0.071851 | -0.10455 | -0.044018 | -0.04543 | 0.045815 | -0.15464 | -0.00811 | 0.36208 | -0.12961 | 121.3963 | 121.658 | 121.6017 | -0.22367 | 0.051358 | -121.7451 | 0.092582 | 0.10144 | 0.050083 | -121.7465 | -121.6552 | -0.017679 | -0.30473 | 0.19788 | 0.076384 | 0.094063 | -0.043032 | -0.099352 | 0.16198 | 0.16056 | 0.25181 | 0.13414 | -121.8557 | 121.6023 | 121.864 | 121.8077 | 0.56807 | -121.9247
1919.4375 | 121.8842 | -0.18768 | 121.7422 | -0.010149 | -0.038572 | 0.038157 | 0.026948 | -0.011651 | 0.0011153 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.038337 | 0.04961 | -0.11341 | -0.081008 | -0.10913 | -0.044018 | -0.04543 | 0.036658 | -0.15464 | -0.00811 | 0.34834 | -0.12961 | 121.4101 | 121.6672 | 121.6017 | -0.24199 | 0.033047 | -121.7863 | 0.074271 | 0.078551 | 0.045504 | -121.7877 | -121.7056 | -0.054306 | -0.3322 | 0.17957 | 0.058073 | 0.11238 | -0.075074 | -0.14055 | 0.14366 | 0.14225 | 0.22434 | 0.10667 | -121.8969 | 121.5977 | 121.8549 | 121.7894 | 0.53602 | -121.9842
1921.2031 | 121.9254 | -0.20142 | 121.7377 | -0.0025182 | -0.038359 | 0.037943 | 0.02652 | -0.011865 | 0.0013291 | -0.0062567 | -0.0018394 | -0.0025041 | 0.059114 | 0.039192 | 0.049824 | -0.11799 | -0.071851 | -0.11371 | -0.048597 | -0.04543 | 0.041237 | -0.16379 | -0.012689 | 0.3575 | -0.13419 | 121.4101 | 121.6672 | 121.6017 | -0.22825 | 0.037622 | -121.7863 | 0.083425 | 0.087706 | 0.050084 | -121.7831 | -121.6964 | -0.026836 | -0.32762 | 0.18873 | 0.067227 | 0.094063 | -0.070496 | -0.13597 | 0.15282 | 0.15599 | 0.24265 | 0.12957 | -121.9015 | 121.6115 | 121.8686 | 121.8031 | 0.55891 | -121.9659
1922.9062 | 121.907 | -0.21057 | 121.7697 | -0.0025182 | -0.038572 | 0.037943 | 0.02652 | -0.011651 | 0.0011153 | -0.021518 | -0.0022666 | -0.0020767 | 0.059114 | 0.038551 | 0.050251 | -0.11799 | -0.071851 | -0.10455 | -0.03944 | -0.040851 | 0.045815 | -0.15921 | -0.00811 | 0.3575 | -0.12503 | 121.4192 | 121.6763 | 121.62 | -0.22825 | 0.051356 | -121.8092 | 0.09258 | 0.10602 | 0.054662 | -121.8106 | -121.7239 | -0.017681 | -0.3505 | 0.20246 | 0.085539 | 0.10322 | -0.093381 | -0.1497 | 0.17113 | 0.16972 | 0.25639 | 0.13872 | -121.9289 | 121.6298 | 121.8869 | 121.8306 | 0.56807 | -121.998
1924.6719 | 122.0306 | -0.16479 | 121.7377 | -0.01778 | -0.038572 | 0.037729 | 0.026948 | -0.011651 | 0.0013291 | -0.0062567 | -0.0018394 | -0.0020767 | 0.058687 | 0.038978 | 0.049824 | -0.10883 | -0.07643 | -0.10913 | -0.03944 | -0.040851 | 0.045815 | -0.15921 | -0.00811 | 0.3575 | -0.13877 | 121.4192 | 121.6855 | 121.6292 | -0.22367 | 0.00558 | -121.7771 | 0.055961 | 0.055663 | 0.050083 | -121.7785 | -121.6919 | -0.058878 | -0.31846 | 0.15668 | 0.026027 | 0.084905 | -0.052181 | -0.1085 | 0.12535 | 0.12394 | 0.21061 | 0.088365 | -121.8969 | 121.584 | 121.8503 | 121.794 | 0.52229 | -121.9613
1926.4219 | 121.9391 | -0.17395 | 121.7514 | -0.010149 | -0.038786 | 0.037729 | 0.02652 | -0.011437 | 0.0011153 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.038764 | 0.049824 | -0.11341 | -0.067272 | -0.095397 | -0.034862 | -0.036272 | 0.045815 | -0.15006 | -0.00811 | 0.36208 | -0.12045 | 121.4375 | 121.6901 | 121.6292 | -0.2191 | 0.023893 | -121.7863 | 0.060538 | 0.078553 | 0.05466 | -121.7877 | -121.7056 | -0.045145 | -0.31388 | 0.16584 | 0.053497 | 0.098642 | -0.061336 | -0.12223 | 0.13909 | 0.13768 | 0.21976 | 0.10668 | -121.9015 | 121.6115 | 121.864 | 121.8031 | 0.53603 | -121.9705
1928.1719 | 121.9345 | -0.19684 | 121.7743 | -0.0025182 | -0.038572 | 0.037729 | 0.026734 | -0.011437 | 0.0013291 | -0.013887 | -0.002053 | -0.0020767 | 0.059328 | 0.038337 | 0.049824 | -0.10883 | -0.07643 | -0.095397 | -0.03944 | -0.040851 | 0.045815 | -0.15006 | -0.00811 | 0.3575 | -0.12503 | 121.4375 | 121.6992 | 121.6337 | -0.2191 | 0.046781 | -121.8137 | 0.088004 | 0.10144 | 0.05466 | -121.8151 | -121.7285 | -0.022257 | -0.33677 | 0.18873 | 0.071806 | 0.094063 | -0.075066 | -0.14054 | 0.1574 | 0.15599 | 0.24265 | 0.12041 | -121.9243 | 121.6344 | 121.8961 | 121.8306 | 0.55434 | -121.9934
1929.8594 | 121.9482 | -0.20142 | 121.7606 | -0.01778 | -0.038786 | 0.038157 | 0.02652 | -0.011651 | 0.0013291 | -0.013887 | -0.002053 | -0.0025041 | 0.059328 | 0.038764 | 0.050038 | -0.10426 | -0.07643 | -0.095397 | -0.034862 | -0.036272 | 0.045815 | -0.14548 | -0.003531 | 0.3575 | -0.12503 | 121.4421 | 121.7038 | 121.6383 | -0.2191 | 0.055938 | -121.7954 | 0.097161 | 0.10602 | 0.050081 | -121.7968 | -121.7147 | -0.017679 | -0.31846 | 0.19789 | 0.076384 | 0.094063 | -0.056755 | -0.12223 | 0.16655 | 0.16514 | 0.24723 | 0.12499 | -121.906 | 121.6435 | 121.9052 | 121.8397 | 0.55891 | -121.9797
1931.5938 | 121.9757 | -0.16937 | 121.7422 | -0.0025182 | -0.038786 | 0.038157 | 0.026734 | -0.011437 | 0.0011153 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.038337 | 0.049824 | -0.10426 | -0.071851 | -0.095397 | -0.03944 | -0.031693 | 0.054973 | -0.14548 | -0.003531 | 0.36208 | -0.12045 | 121.4421 | 121.7038 | 121.6521 | -0.2191 | 0.023895 | -121.7817 | 0.065118 | 0.073976 | 0.050081 | -121.7739 | -121.6873 | -0.049722 | -0.30015 | 0.16584 | 0.04892 | 0.098642 | -0.038445 | -0.090187 | 0.12993 | 0.13768 | 0.22435 | 0.097522 | -121.8877 | 121.6115 | 121.8732 | 121.8214 | 0.53145 | -121.9613
1933.3438 | 121.9986 | -0.16022 | 121.7468 | -0.0025182 | -0.039213 | 0.038157 | 0.02652 | -0.011437 | 0.00090167 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.038978 | 0.049824 | -0.10883 | -0.071851 | -0.095397 | -0.034862 | -0.031693 | 0.050394 | -0.15921 | 0.001048 | 0.36666 | -0.12503 | 121.4467 | 121.7084 | 121.6429 | -0.22367 | 0.001002 | -121.7817 | 0.051383 | 0.06482 | 0.063818 | -121.7785 | -121.6964 | -0.063456 | -0.30015 | 0.16126 | 0.035185 | 0.098641 | -0.038443 | -0.10392 | 0.12535 | 0.12852 | 0.21061 | 0.088366 | -121.906 | 121.6069 | 121.8686 | 121.8031 | 0.52687 | -121.9705
1935.0938 | 121.9711 | -0.1831 | 121.7651 | -0.010149 | -0.038786 | 0.038157 | 0.026734 | -0.011437 | 0.0013291 | -0.021518 | -0.0022666 | -0.0022903 | 0.059328 | 0.038764 | 0.049824 | -0.10883 | -0.067272 | -0.095397 | -0.030283 | -0.031693 | 0.041237 | -0.14548 | 0.001048 | 0.36208 | -0.12045 | 121.4513 | 121.7084 | 121.6475 | -0.2191 | 0.037627 | -121.7954 | 0.074271 | 0.087708 | 0.050081 | -121.7968 | -121.7239 | -0.03599 | -0.31388 | 0.18415 | 0.062652 | 0.098642 | -0.056754 | -0.11765 | 0.15282 | 0.15141 | 0.22434 | 0.11583 | -121.9106 | 121.6344 | 121.8915 | 121.8306 | 0.54518 | -121.9842
1936.7812 | 122.0261 | -0.16022 | 121.7651 | -0.0025182 | -0.038786 | 0.037943 | 0.02652 | -0.011651 | 0.0013291 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.038978 | 0.050038 | -0.10426 | -0.062694 | -0.090818 | -0.025705 | -0.031693 | 0.054973 | -0.15006 | 0.001048 | 0.3575 | -0.11587 | 121.4558 | 121.713 | 121.6566 | -0.21452 | 0.01016 | -121.7908 | 0.055962 | 0.069399 | 0.059239 | -121.7968 | -121.7102 | -0.054299 | -0.3093 | 0.16126 | 0.044343 | 0.098642 | -0.052176 | -0.1085 | 0.13451 | 0.12852 | 0.21519 | 0.097523 | -121.9152 | 121.6161 | 121.8732 | 121.8169 | 0.51771 | -121.9797
1938.5312 | 121.9482 | -0.19226 | 121.7789 | -0.0025182 | -0.038786 | 0.037943 | 0.026734 | -0.011651 | 0.0013291 | -0.013887 | -0.0016258 | -0.0020767 | 0.059114 | 0.038978 | 0.049824 | -0.10426 | -0.071851 | -0.099975 | -0.030283 | -0.027115 | 0.050394 | -0.15006 | -0.003531 | 0.35292 | -0.12503 | 121.4604 | 121.7175 | 121.6566 | -0.22367 | 0.042204 | -121.8092 | 0.088006 | 0.092286 | 0.050082 | -121.806 | -121.7285 | -0.031412 | -0.31846 | 0.18873 | 0.067229 | 0.098641 | -0.06133 | -0.12223 | 0.16198 | 0.16515 | 0.24265 | 0.12041 | -121.9289 | 121.6527 | 121.9098 | 121.8489 | 0.54518 | -122.0025
1940.2969 | 121.9894 | -0.17395 | 121.7606 | -0.010149 | -0.039 | 0.03837 | 0.026307 | -0.011437 | 0.0013291 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.039192 | 0.050251 | -0.10883 | -0.067272 | -0.095397 | -0.03944 | -0.022536 | 0.054973 | -0.15464 | 0.001048 | 0.36208 | -0.12503 | 121.465 | 121.7221 | 121.6612 | -0.2191 | 0.019314 | -121.8 | 0.065116 | 0.078553 | 0.059239 | -121.7831 | -121.7056 | -0.045145 | -0.29556 | 0.175 | 0.048918 | 0.094063 | -0.03844 | -0.099339 | 0.13451 | 0.15141 | 0.22892 | 0.10668 | -121.9152 | 121.6389 | 121.8961 | 121.8352 | 0.53603 | -121.9797
1941.9844 | 121.9894 | -0.19226 | 121.7651 | -0.010149 | -0.039213 | 0.038584 | 0.026307 | -0.011224 | 0.00047427 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.038978 | 0.050038 | -0.10883 | -0.07643 | -0.11371 | -0.03944 | -0.031693 | 0.050394 | -0.15921 | -0.003531 | 0.36208 | -0.12503 | 121.465 | 121.7175 | 121.6521 | -0.2191 | 0.033046 | -121.8046 | 0.083427 | 0.078551 | 0.045505 | -121.7968 | -121.7147 | -0.026834 | -0.30014 | 0.18873 | 0.067229 | 0.094063 | -0.047597 | -0.11307 | 0.15282 | 0.16057 | 0.24265 | 0.11583 | -121.9244 | 121.6573 | 121.9098 | 121.8443 | 0.55434 | -121.9842
1943.7344 | 122.0306 | -0.17853 | 121.7743 | -0.01778 | -0.039213 | 0.03837 | 0.02652 | -0.011437 | 0.0011153 | -0.013887 | -0.0018394 | -0.0020767 | 0.058687 | 0.038978 | 0.04961 | -0.10883 | -0.071851 | -0.10455 | -0.044018 | -0.04543 | 0.041237 | -0.15464 | -0.00811 | 0.36208 | -0.12503 | 121.4604 | 121.713 | 121.6612 | -0.2191 | 0.023892 | -121.8183 | 0.069694 | 0.073975 | 0.050083 | -121.8197 | -121.7331 | -0.040567 | -0.31388 | 0.17042 | 0.053496 | 0.094063 | -0.061331 | -0.11307 | 0.13451 | 0.1331 | 0.21976 | 0.10668 | -121.9289 | 121.6389 | 121.8915 | 121.8397 | 0.54061 | -121.9934
1945.4844 | 122.0581 | -0.16937 | 121.7697 | -0.010149 | -0.039427 | 0.038157 | 0.026734 | -0.011865 | 0.0013291 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.039192 | 0.04961 | -0.11799 | -0.07643 | -0.10913 | -0.034862 | -0.040851 | 0.045815 | -0.15464 | -0.012689 | 0.3575 | -0.12961 | 121.4604 | 121.7175 | 121.6704 | -0.22367 | 0.014737 | -121.8046 | 0.051382 | 0.060241 | 0.045504 | -121.8106 | -121.7239 | -0.0543 | -0.3093 | 0.15668 | 0.039763 | 0.094063 | -0.052174 | -0.099337 | 0.13451 | 0.12852 | 0.21519 | 0.092943 | -121.9243 | 121.6298 | 121.8869 | 121.8397 | 0.52687 | -121.9934
1947.2344 | 122.049 | -0.16479 | 121.7331 | -0.0025182 | -0.039213 | 0.038798 | 0.026307 | -0.011865 | 0.0011153 | -0.029148 | -0.0018394 | -0.0020767 | 0.059328 | 0.038764 | 0.049824 | -0.11799 | -0.07643 | -0.10455 | -0.044018 | -0.036272 | 0.054973 | -0.15464 | 0.001048 | 0.3575 | -0.12503 | 121.4696 | 121.7313 | 121.6612 | -0.22825 | 0.010159 | -121.7771 | 0.046804 | 0.060242 | 0.050083 | -121.7694 | -121.6781 | -0.063457 | -0.26352 | 0.16584 | 0.039763 | 0.10322 | -0.001817 | -0.071873 | 0.12078 | 0.12852 | 0.21977 | 0.088365 | -121.8877 | 121.6344 | 121.8961 | 121.826 | 0.52229 | -121.9613
1948.9844 | 121.9894 | -0.17395 | 121.7743 | -0.010149 | -0.038786 | 0.038584 | 0.026307 | -0.011437 | 0.0011153 | -0.0062567 | -0.0016258 | -0.0020767 | 0.058901 | 0.038764 | 0.049824 | -0.11341 | -0.067272 | -0.090818 | -0.03944 | -0.036272 | 0.050394 | -0.15464 | -0.00811 | 0.3575 | -0.12961 | 121.4696 | 121.7267 | 121.6704 | -0.22367 | 0.019314 | -121.8137 | 0.060538 | 0.083132 | 0.063818 | -121.8106 | -121.7239 | -0.049723 | -0.30472 | 0.16584 | 0.04434 | 0.094063 | -0.047595 | -0.10392 | 0.13451 | 0.13768 | 0.22434 | 0.10668 | -121.9289 | 121.6435 | 121.9006 | 121.8443 | 0.53145 | -121.998
1950.6875 | 122.0398 | -0.17395 | 121.7834 | -0.010149 | -0.039427 | 0.038157 | 0.026093 | -0.011651 | 0.0013291 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.038978 | 0.049824 | -0.10426 | -0.067272 | -0.10455 | -0.030283 | -0.036272 | 0.045815 | -0.15464 | -0.012689 | 0.3575 | -0.12503 | 121.4787 | 121.7359 | 121.675 | -0.22367 | 0.019314 | -121.8137 | 0.069695 | 0.069397 | 0.050083 | -121.8197 | -121.7376 | -0.049723 | -0.30472 | 0.16126 | 0.048918 | 0.098641 | -0.047593 | -0.10849 | 0.14367 | 0.13768 | 0.21976 | 0.10668 | -121.9381 | 121.6527 | 121.9098 | 121.8489 | 0.53145 | -122.0071
1952.4375 | 122.0169 | -0.16937 | 121.7834 | -0.0025182 | -0.039427 | 0.039011 | 0.026307 | -0.011224 | 0.0013291 | -0.021518 | -0.0016258 | -0.0022903 | 0.058687 | 0.038978 | 0.050038 | -0.10426 | -0.07643 | -0.099975 | -0.030283 | -0.031693 | 0.054973 | -0.15464 | 0.001048 | 0.3575 | -0.12045 | 121.4787 | 121.7359 | 121.675 | -0.22367 | 0.014737 | -121.8137 | 0.065118 | 0.069398 | 0.054661 | -121.8151 | -121.7285 | -0.0543 | -0.30472 | 0.17042 | 0.04892 | 0.10322 | -0.047593 | -0.10849 | 0.13909 | 0.13768 | 0.22435 | 0.092943 | -121.9381 | 121.6481 | 121.9052 | 121.8443 | 0.52687 | -122.0071
1954.1875 | 122.0123 | -0.16022 | 121.8063 | -0.010149 | -0.039213 | 0.038584 | 0.026307 | -0.011651 | 0.0013291 | -0.029148 | -0.0022666 | -0.0020767 | 0.059114 | 0.039192 | 0.04961 | -0.10426 | -0.062694 | -0.10455 | -0.030283 | -0.031693 | 0.045815 | -0.15006 | 0.001048 | 0.3575 | -0.12045 | 121.4833 | 121.745 | 121.6795 | -0.2191 | 0.01016 | -121.8366 | 0.055962 | 0.055664 | 0.045504 | -121.838 | -121.7605 | -0.058878 | -0.32303 | 0.16126 | 0.039764 | 0.098642 | -0.061323 | -0.1268 | 0.12993 | 0.12852 | 0.20603 | 0.097523 | -121.9564 | 121.6435 | 121.9052 | 121.8398 | 0.51771 | -122.0254
1955.8906 | 122.0947 | -0.15106 | 121.7743 | -0.010149 | -0.039 | 0.03837 | 0.026093 | -0.011224 | 0.0011153 | -0.029148 | -0.002053 | -0.0020767 | 0.058901 | 0.038978 | 0.049824 | -0.10883 | -0.067272 | -0.095397 | -0.030283 | -0.031693 | 0.050394 | -0.15006 | -0.003531 | 0.36208 | -0.11587 | 121.4833 | 121.7496 | 121.6841 | -0.2191 | 0.001005 | -121.8046 | 0.042228 | 0.055665 | 0.05466 | -121.806 | -121.7239 | -0.068033 | -0.29098 | 0.14753 | 0.035188 | 0.10322 | -0.024702 | -0.090179 | 0.12078 | 0.11937 | 0.20146 | 0.08379 | -121.9243 | 121.6344 | 121.9007 | 121.8352 | 0.51314 | -121.9934
1957.6406 | 122.0673 | -0.13733 | 121.7651 | -0.010149 | -0.039213 | 0.038584 | 0.026307 | -0.011224 | 0.0015427 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.038978 | 0.049824 | -0.10426 | -0.062694 | -0.099975 | -0.034862 | -0.036272 | 0.041237 | -0.15006 | 0.001048 | 0.36208 | -0.11587 | 121.4879 | 121.7496 | 121.6841 | -0.20994 | -0.012728 | -121.8 | 0.033074 | 0.037354 | 0.050082 | -121.8014 | -121.7239 | -0.072608 | -0.27725 | 0.13838 | 0.021455 | 0.094063 | -0.015547 | -0.081024 | 0.10247 | 0.10106 | 0.17857 | 0.074635 | -121.9152 | 121.6252 | 121.8869 | 121.8214 | 0.49941 | -121.9751
1959.4062 | 121.9666 | -0.18768 | 121.7972 | -0.010149 | -0.039427 | 0.03837 | 0.026734 | -0.011437 | 0.0015427 | -0.021518 | -0.0022666 | -0.0020767 | 0.058901 | 0.039192 | 0.049824 | -0.10426 | -0.062694 | -0.095397 | -0.025705 | -0.027115 | 0.050394 | -0.14548 | -0.00811 | 0.36208 | -0.1113 | 121.497 | 121.7587 | 121.6933 | -0.21452 | 0.042205 | -121.8229 | 0.083428 | 0.092286 | 0.050081 | -121.8243 | -121.7468 | -0.026833 | -0.30014 | 0.17957 | 0.076387 | 0.10322 | -0.038433 | -0.10391 | 0.16198 | 0.16057 | 0.23808 | 0.12499 | -121.9427 | 121.6847 | 121.9464 | 121.881 | 0.54976 | -122.0117
1961.1875 | 121.9574 | -0.17853 | 121.8201 | -0.0025182 | -0.039 | 0.03837 | 0.026307 | -0.011865 | 0.0015427 | -0.021518 | -0.0016258 | -0.0025041 | 0.059114 | 0.038978 | 0.050038 | -0.11341 | -0.067272 | -0.095397 | -0.025705 | -0.031693 | 0.054973 | -0.15006 | -0.003531 | 0.36208 | -0.12045 | 121.497 | 121.7587 | 121.6933 | -0.2191 | 0.028471 | -121.8458 | 0.065116 | 0.083131 | 0.05466 | -121.8518 | -121.7651 | -0.040567 | -0.32303 | 0.175 | 0.058075 | 0.098642 | -0.061321 | -0.1268 | 0.15282 | 0.14683 | 0.2335 | 0.11126 | -121.9701 | 121.6756 | 121.9373 | 121.8718 | 0.54061 | -122.0392
1962.875 | 121.9849 | -0.18768 | 121.8063 | -0.010149 | -0.039213 | 0.038584 | 0.026307 | -0.011437 | 0.0017563 | -0.021518 | -0.0024804 | -0.0022903 | 0.059328 | 0.038978 | 0.049824 | -0.10883 | -0.062694 | -0.095397 | -0.030283 | -0.031693 | 0.050394 | -0.14548 | 0.001048 | 0.36666 | -0.11587 | 121.5016 | 121.7587 | 121.6978 | -0.21452 | 0.042205 | -121.8366 | 0.078849 | 0.092286 | 0.050081 | -121.838 | -121.7559 | -0.026833 | -0.30471 | 0.18873 | 0.071809 | 0.098642 | -0.047588 | -0.10849 | 0.1574 | 0.15599 | 0.23808 | 0.12499 | -121.9518 | 121.6893 | 121.9464 | 121.8855 | 0.55434 | -122.0209
1964.625 | 122.0856 | -0.13275 | 121.8018 | -0.01778 | -0.038786 | 0.038157 | 0.02652 | -0.011651 | 0.0021837 | -0.013887 | -0.0022666 | -0.0020767 | 0.058901 | 0.038978 | 0.050038 | -0.10426 | -0.067272 | -0.095397 | -0.030283 | -0.031693 | 0.045815 | -0.15006 | 0.001048 | 0.36666 | -0.12045 | 121.4925 | 121.7587 | 121.6978 | -0.2191 | -0.017306 | -121.832 | 0.028496 | 0.037354 | 0.05466 | -121.8335 | -121.7559 | -0.086344 | -0.30929 | 0.1338 | 0.012298 | 0.098642 | -0.043011 | -0.10391 | 0.10247 | 0.10106 | 0.17857 | 0.065479 | -121.9518 | 121.6252 | 121.8915 | 121.8306 | 0.49941 | -122.0209
1966.375 | 121.9803 | -0.16937 | 121.8246 | -0.01778 | -0.039213 | 0.038798 | 0.026093 | -0.011437 | 0.0017563 | -0.021518 | -0.0022666 | -0.0025041 | 0.058901 | 0.039192 | 0.050038 | -0.099677 | -0.058115 | -0.099975 | -0.030283 | -0.031693 | 0.054973 | -0.14548 | 0.005626 | 0.3575 | -0.12045 | 121.5062 | 121.7587 | 121.6978 | -0.20994 | 0.023895 | -121.8549 | 0.069696 | 0.069398 | 0.045503 | -121.8563 | -121.7697 | -0.040564 | -0.31845 | 0.175 | 0.04892 | 0.089484 | -0.065899 | -0.1268 | 0.13909 | 0.13768 | 0.22435 | 0.11126 | -121.9701 | 121.6756 | 121.9281 | 121.8672 | 0.52687 | -122.0346
1968.0625 | 121.9666 | -0.15564 | 121.8338 | -0.01778 | -0.039213 | 0.03837 | 0.026307 | -0.011651 | 0.0023973 | -0.013887 | -0.0022666 | -0.0020767 | 0.059114 | 0.038764 | 0.049824 | -0.10426 | -0.067272 | -0.095397 | -0.034862 | -0.027115 | 0.054973 | -0.14548 | -0.003531 | 0.37123 | -0.12045 | 121.5062 | 121.7679 | 121.6978 | -0.2191 | 0.010162 | -121.8687 | 0.051385 | 0.060243 | 0.050081 | -121.8609 | -121.7788 | -0.063455 | -0.3276 | 0.15211 | 0.035187 | 0.098642 | -0.065896 | -0.13595 | 0.12078 | 0.12853 | 0.21061 | 0.088368 | -121.9793 | 121.6618 | 121.9235 | 121.8535 | 0.52687 | -122.0529
1969.8125 | 122.113 | -0.15106 | 121.7972 | -0.010149 | -0.039427 | 0.038157 | 0.026307 | -0.011437 | 0.0030383 | -0.0062567 | -0.002053 | -0.0022903 | 0.059328 | 0.039192 | 0.049824 | -0.10426 | -0.062694 | -0.095397 | -0.03944 | -0.031693 | 0.054973 | -0.15006 | 0.005626 | 0.36666 | -0.12045 | 121.5108 | 121.7679 | 121.7162 | -0.20994 | 0.001005 | -121.8366 | 0.046807 | 0.055665 | 0.05466 | -121.8289 | -121.7422 | -0.058875 | -0.2864 | 0.15669 | 0.030609 | 0.089484 | -0.029275 | -0.081017 | 0.11162 | 0.11937 | 0.20603 | 0.088368 | -121.9472 | 121.6618 | 121.919 | 121.8672 | 0.51772 | -122.0071
1971.5625 | 122.0993 | -0.14191 | 121.8063 | -0.025411 | -0.039213 | 0.03837 | 0.026307 | -0.011224 | 0.0019701 | -0.021518 | -0.0022666 | -0.0022903 | 0.059114 | 0.039406 | 0.04961 | -0.099677 | -0.062694 | -0.095397 | -0.030283 | -0.022536 | 0.054973 | -0.14548 | 0.005626 | 0.36666 | -0.12503 | 121.5199 | 121.7725 | 121.707 | -0.20994 | -0.003571 | -121.8366 | 0.04223 | 0.04651 | 0.050081 | -121.8289 | -121.7514 | -0.06803 | -0.2864 | 0.14753 | 0.016875 | 0.084905 | -0.033852 | -0.099329 | 0.11162 | 0.11937 | 0.19688 | 0.079213 | -121.9518 | 121.6618 | 121.9144 | 121.8489 | 0.50856 | -122.0163
1973.3125 | 122.0993 | -0.14648 | 121.8109 | -0.0025182 | -0.039641 | 0.03837 | 0.026307 | -0.011224 | 0.0021837 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.039406 | 0.050038 | -0.10883 | -0.062694 | -0.090818 | -0.025705 | -0.022536 | 0.054973 | -0.1409 | 0.005626 | 0.36208 | -0.11587 | 121.5108 | 121.7771 | 121.707 | -0.21452 | 0.005585 | -121.8366 | 0.03765 | 0.055666 | 0.050081 | -121.8334 | -121.7559 | -0.068032 | -0.30013 | 0.15211 | 0.03061 | 0.098642 | -0.033851 | -0.10391 | 0.12078 | 0.12395 | 0.20146 | 0.08379 | -121.9518 | 121.6573 | 121.9235 | 121.8535 | 0.50856 | -122.0254
1975.0156 | 122.0352 | -0.1831 | 121.8109 | 0.0051128 | -0.039213 | 0.03837 | 0.026734 | -0.011437 | 0.0023973 | -0.013887 | -0.0022666 | -0.0022903 | 0.058901 | 0.038764 | 0.049824 | -0.10883 | -0.067272 | -0.095397 | -0.025705 | -0.027115 | 0.059551 | -0.14548 | -0.003531 | 0.36208 | -0.1113 | 121.5245 | 121.7771 | 121.7116 | -0.21452 | 0.037627 | -121.8366 | 0.074271 | 0.087708 | 0.050081 | -121.838 | -121.7514 | -0.031411 | -0.2864 | 0.17957 | 0.071809 | 0.10322 | -0.033851 | -0.099329 | 0.1574 | 0.15599 | 0.24266 | 0.11583 | -121.9564 | 121.7076 | 121.9602 | 121.8947 | 0.54518 | -122.0254
1976.7656 | 121.9711 | -0.19226 | 121.8246 | -0.010149 | -0.039213 | 0.03837 | 0.02652 | -0.011651 | 0.0030383 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.038764 | 0.049824 | -0.10426 | -0.062694 | -0.099975 | -0.025705 | -0.036272 | 0.054973 | -0.15006 | 0.001048 | 0.36666 | -0.12045 | 121.5199 | 121.7725 | 121.7116 | -0.2191 | 0.042204 | -121.8504 | 0.088006 | 0.092286 | 0.050082 | -121.8609 | -121.7697 | -0.026834 | -0.30471 | 0.19331 | 0.071808 | 0.098642 | -0.052163 | -0.11306 | 0.16656 | 0.15599 | 0.24723 | 0.12957 | -121.9747 | 121.7122 | 121.9647 | 121.9038 | 0.55892 | -122.0437
1978.5312 | 122.1222 | -0.14648 | 121.7834 | -0.01778 | -0.039213 | 0.037729 | 0.02652 | -0.011437 | 0.0034657 | -0.013887 | -0.0016258 | -0.0025041 | 0.058901 | 0.039192 | 0.050038 | -0.10426 | -0.058115 | -0.08624 | -0.025705 | -0.031693 | 0.054973 | -0.15464 | 0.001048 | 0.36208 | -0.12045 | 121.5154 | 121.7771 | 121.7253 | -0.2191 | -0.008152 | -121.8092 | 0.042229 | 0.060244 | 0.068396 | -121.8151 | -121.7285 | -0.072611 | -0.26809 | 0.14753 | 0.026031 | 0.098642 | -0.006385 | -0.058127 | 0.12078 | 0.11479 | 0.20146 | 0.088369 | -121.9381 | 121.6618 | 121.9235 | 121.8718 | 0.50856 | -122.0025
1980.2812 | 122.0718 | -0.16937 | 121.8063 | -0.010149 | -0.039213 | 0.037943 | 0.026734 | -0.011651 | 0.0038929 | -0.013887 | -0.0022666 | -0.0022903 | 0.059114 | 0.038978 | 0.04961 | -0.10883 | -0.071851 | -0.095397 | -0.034862 | -0.031693 | 0.050394 | -0.15006 | -0.003531 | 0.36208 | -0.12503 | 121.5199 | 121.7816 | 121.7207 | -0.2191 | 0.019316 | -121.8412 | 0.060539 | 0.073976 | 0.05466 | -121.838 | -121.7559 | -0.049722 | -0.2864 | 0.16584 | 0.044341 | 0.094063 | -0.024695 | -0.085594 | 0.13451 | 0.13768 | 0.21977 | 0.097522 | -121.9564 | 121.6893 | 121.951 | 121.8901 | 0.53145 | -122.0254
1981.9688 | 122.1359 | -0.14191 | 121.8018 | -0.025411 | -0.039213 | 0.038157 | 0.02652 | -0.011865 | 0.0034657 | -0.021518 | -0.002053 | -0.0025041 | 0.059114 | 0.039406 | 0.049824 | -0.099677 | -0.067272 | -0.099975 | -0.030283 | -0.031693 | 0.050394 | -0.1409 | -0.003531 | 0.36666 | -0.11587 | 121.5199 | 121.7816 | 121.7116 | -0.2191 | 0.001008 | -121.832 | 0.04223 | 0.041932 | 0.040924 | -121.8335 | -121.7514 | -0.077188 | -0.28182 | 0.13838 | 0.026033 | 0.10322 | -0.020118 | -0.090174 | 0.11162 | 0.11021 | 0.1923 | 0.074635 | -121.9427 | 121.6618 | 121.9235 | 121.8535 | 0.50856 | -122.0209
1983.7188 | 121.994 | -0.19684 | 121.8567 | -0.01778 | -0.039213 | 0.037943 | 0.026307 | -0.011651 | 0.0034657 | -0.013887 | -0.002053 | -0.0020767 | 0.059328 | 0.039406 | 0.04961 | -0.099677 | -0.067272 | -0.090818 | -0.034862 | -0.027115 | 0.054973 | -0.14548 | 0.001048 | 0.36666 | -0.11587 | 121.5245 | 121.7862 | 121.7253 | -0.20994 | 0.05136 | -121.8916 | 0.097161 | 0.10602 | 0.05466 | -121.8838 | -121.8017 | -0.013099 | -0.33218 | 0.19789 | 0.080964 | 0.094063 | -0.07047 | -0.13137 | 0.16198 | 0.16972 | 0.25181 | 0.12957 | -122.0022 | 121.7214 | 121.9831 | 121.9222 | 0.56349 | -122.0666
1985.4688 | 122.1497 | -0.13733 | 121.8063 | -0.010149 | -0.039 | 0.038157 | 0.02652 | -0.011437 | 0.0036793 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.038978 | 0.049824 | -0.099677 | -0.067272 | -0.08624 | -0.025705 | -0.027115 | 0.054973 | -0.1409 | 0.001048 | 0.3575 | -0.11587 | 121.5245 | 121.7954 | 121.7253 | -0.20994 | -0.00357 | -121.832 | 0.037652 | 0.051089 | 0.054659 | -121.8334 | -121.7514 | -0.072608 | -0.28182 | 0.13838 | 0.021455 | 0.094063 | -0.010959 | -0.081015 | 0.11162 | 0.11021 | 0.1923 | 0.070057 | -121.9472 | 121.6618 | 121.9327 | 121.8626 | 0.49483 | -122.0163
1987.2188 | 121.9849 | -0.17853 | 121.875 | -0.0025182 | -0.039 | 0.037516 | 0.02652 | -0.011651 | 0.0041067 | -0.013887 | -0.0022666 | -0.0025041 | 0.059114 | 0.038764 | 0.04961 | -0.10426 | -0.062694 | -0.095397 | -0.025705 | -0.027115 | 0.050394 | -0.15464 | 0.010205 | 0.36208 | -0.12045 | 121.5291 | 121.7954 | 121.7345 | -0.22825 | 0.023892 | -121.9007 | 0.074273 | 0.083131 | 0.059239 | -121.9021 | -121.8246 | -0.049724 | -0.34591 | 0.18873 | 0.058075 | 0.1078 | -0.079624 | -0.14052 | 0.15282 | 0.15141 | 0.22892 | 0.11583 | -122.0296 | 121.7076 | 121.9739 | 121.913 | 0.54061 | -122.1033
1988.9062 | 122.0169 | -0.16022 | 121.843 | -0.01778 | -0.039427 | 0.038157 | 0.02652 | -0.011865 | 0.0036793 | -0.021518 | -0.002053 | -0.0020767 | 0.059114 | 0.038978 | 0.049824 | -0.10426 | -0.062694 | -0.090818 | -0.030283 | -0.027115 | 0.054973 | -0.14548 | 0.005626 | 0.36208 | -0.12045 | 121.5291 | 121.8 | 121.7299 | -0.21452 | 0.014739 | -121.8732 | 0.055962 | 0.069399 | 0.05466 | -121.8701 | -121.788 | -0.054299 | -0.31386 | 0.16584 | 0.039764 | 0.094063 | -0.043002 | -0.11306 | 0.12993 | 0.1331 | 0.21519 | 0.097523 | -121.9884 | 121.6893 | 121.9602 | 121.8901 | 0.52229 | -122.0575
1990.6562 | 122.0398 | -0.16022 | 121.8475 | -0.025411 | -0.039213 | 0.037943 | 0.02652 | -0.011651 | 0.0034657 | -0.021518 | -0.0016258 | -0.0025041 | 0.059328 | 0.039192 | 0.050038 | -0.099677 | -0.067272 | -0.090818 | -0.025705 | -0.027115 | 0.054973 | -0.1409 | 0.010205 | 0.37123 | -0.11587 | 121.5383 | 121.7954 | 121.7345 | -0.20536 | 0.019318 | -121.8732 | 0.06054 | 0.069399 | 0.050081 | -121.8746 | -121.7926 | -0.045141 | -0.30928 | 0.17042 | 0.044343 | 0.089484 | -0.052158 | -0.11306 | 0.13451 | 0.1331 | 0.21519 | 0.092945 | -121.9884 | 121.6985 | 121.9556 | 121.8947 | 0.53145 | -122.0529
1992.3906 | 122.1085 | -0.13733 | 121.8292 | -0.01778 | -0.039641 | 0.03837 | 0.026307 | -0.011437 | 0.0030383 | -0.021518 | -0.002053 | -0.0020767 | 0.058687 | 0.039192 | 0.050038 | -0.095099 | -0.058115 | -0.090818 | -0.030283 | -0.022536 | 0.054973 | -0.14548 | 0.001048 | 0.3575 | -0.12045 | 121.5428 | 121.8045 | 121.7345 | -0.20078 | -0.008149 | -121.8595 | 0.04223 | 0.046511 | 0.05466 | -121.8518 | -121.7743 | -0.06345 | -0.2864 | 0.13838 | 0.016876 | 0.080326 | -0.024691 | -0.094747 | 0.10705 | 0.11479 | 0.1923 | 0.079214 | -121.9747 | 121.6802 | 121.9419 | 121.8718 | 0.49483 | -122.03
1994.0781 | 122.0169 | -0.17853 | 121.8796 | -0.0025182 | -0.039213 | 0.038157 | 0.02652 | -0.011651 | 0.0023973 | -0.013887 | -0.0022666 | -0.0025041 | 0.059114 | 0.039192 | 0.04961 | -0.095099 | -0.062694 | -0.090818 | -0.021127 | -0.022536 | 0.068708 | -0.13174 | 0.014784 | 0.36666 | -0.11587 | 121.5474 | 121.8045 | 121.7482 | -0.20536 | 0.046787 | -121.9007 | 0.083429 | 0.08771 | 0.040923 | -121.9021 | -121.8109 | -0.02683 | -0.33217 | 0.19331 | 0.062654 | 0.089484 | -0.075045 | -0.13136 | 0.1574 | 0.15599 | 0.24724 | 0.11583 | -122.0113 | 121.7259 | 121.9831 | 121.9267 | 0.54518 | -122.0849
1995.7812 | 122.1542 | -0.11902 | 121.8384 | -0.010149 | -0.039427 | 0.03837 | 0.026307 | -0.011437 | 0.0019701 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.038764 | 0.050251 | -0.09052 | -0.053537 | -0.081662 | -0.01197 | -0.017957 | 0.073287 | -0.13632 | 0.023941 | 0.36208 | -0.1113 | 121.552 | 121.8228 | 121.7528 | -0.18704 | -0.017301 | -121.8503 | 0.028499 | 0.037357 | 0.054658 | -121.8563 | -121.7651 | -0.068024 | -0.28639 | 0.14296 | 0.007723 | 0.075747 | -0.015531 | -0.085587 | 0.10705 | 0.10106 | 0.19231 | 0.065482 | -121.9747 | 121.671 | 121.9419 | 121.8718 | 0.4811 | -122.0254
1997.5156 | 122.0215 | -0.17853 | 121.8887 | -0.0025182 | -0.039641 | 0.03837 | 0.02652 | -0.011437 | 0.0017563 | -0.021518 | -0.002053 | -0.0020767 | 0.059114 | 0.038551 | 0.04961 | -0.085942 | -0.048958 | -0.081662 | -0.016548 | -0.008799 | 0.06413 | -0.13632 | 0.023941 | 0.3575 | -0.10672 | 121.5611 | 121.8228 | 121.7574 | -0.20078 | 0.042208 | -121.9053 | 0.092586 | 0.096866 | 0.054658 | -121.8975 | -121.8246 | -0.022251 | -0.32759 | 0.20247 | 0.071811 | 0.094062 | -0.065885 | -0.13136 | 0.16198 | 0.16973 | 0.24266 | 0.12957 | -122.0251 | 121.7397 | 122.0014 | 121.9359 | 0.53603 | -122.0895
1999.2656 | 122.1405 | -0.1236 | 121.8475 | -0.010149 | -0.039641 | 0.038798 | 0.025879 | -0.011224 | 0.0015427 | -0.021518 | -0.0022666 | -0.0027177 | 0.058901 | 0.039192 | 0.049824 | -0.09052 | -0.048958 | -0.081662 | -0.01197 | -0.008799 | 0.073287 | -0.13174 | 0.014784 | 0.36666 | -0.097559 | 121.5657 | 121.8274 | 121.7619 | -0.1962 | -0.008145 | -121.8595 | 0.033076 | 0.041934 | 0.050079 | -121.8563 | -121.7742 | -0.072604 | -0.28181 | 0.13838 | 0.026037 | 0.098641 | -0.020108 | -0.085585 | 0.11163 | 0.1148 | 0.19688 | 0.074638 | -121.9793 | 121.6893 | 121.951 | 121.8855 | 0.49025 | -122.0437
2000.9688 | 122.1451 | -0.13733 | 121.8384 | -0.01778 | -0.039641 | 0.038584 | 0.026093 | -0.012078 | 0.0013291 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.039192 | 0.04961 | -0.076785 | -0.048958 | -0.077084 | -0.01197 | -0.008799 | 0.068708 | -0.12716 | 0.019362 | 0.36666 | -0.10672 | 121.5657 | 121.8228 | 121.7574 | -0.18704 | 0.010167 | -121.8503 | 0.060544 | 0.060245 | 0.050078 | -121.8472 | -121.7697 | -0.049714 | -0.27266 | 0.15669 | 0.030612 | 0.080326 | -0.015531 | -0.081009 | 0.12536 | 0.12853 | 0.20604 | 0.088371 | -121.9655 | 121.703 | 121.9602 | 121.8947 | 0.50399 | -122.0254
2002.7188 | 122.1588 | -0.13275 | 121.8338 | -0.0025182 | -0.039641 | 0.03837 | 0.026093 | -0.011651 | 0.0011153 | -0.029148 | -0.0018394 | -0.0022903 | 0.059114 | 0.039192 | 0.050038 | -0.081363 | -0.044379 | -0.077084 | -0.01197 | -0.008799 | 0.068708 | -0.12258 | 0.023941 | 0.37123 | -0.097559 | 121.5795 | 121.8228 | 121.7665 | -0.1962 | 0.010168 | -121.8458 | 0.051388 | 0.055667 | 0.045499 | -121.8426 | -121.7651 | -0.063449 | -0.25435 | 0.15669 | 0.035192 | 0.098641 | -0.010953 | -0.067274 | 0.12078 | 0.12395 | 0.20146 | 0.088372 | -121.9564 | 121.7122 | 121.9556 | 121.8993 | 0.50399 | -122.03
2004.4844 | 122.1497 | -0.11902 | 121.8292 | -0.010149 | -0.039427 | 0.038584 | 0.026093 | -0.011651 | 0.0015427 | -0.021518 | -0.002053 | -0.0025041 | 0.059114 | 0.039619 | 0.050038 | -0.076785 | -0.048958 | -0.077084 | -0.007391 | 0.000359 | 0.077866 | -0.118 | 0.019362 | 0.36666 | -0.088402 | 121.5795 | 121.832 | 121.7711 | -0.19162 | 0.001015 | -121.8366 | 0.042234 | 0.041935 | 0.04092 | -121.8289 | -121.7514 | -0.072603 | -0.24977 | 0.13838 | 0.030617 | 0.10322 | 0.002781 | -0.058118 | 0.11163 | 0.11938 | 0.19689 | 0.070061 | -121.9472 | 121.6985 | 121.951 | 121.8901 | 0.48567 | -122.0208
2006.25 | 122.1634 | -0.09613 | 121.8475 | -0.010149 | -0.039427 | 0.039011 | 0.026307 | -0.011437 | 0.0013291 | -0.029148 | -0.0022666 | -0.0018631 | 0.059328 | 0.039192 | 0.050251 | -0.076785 | -0.044379 | -0.072505 | -0.007391 | 0.000359 | 0.077866 | -0.13174 | 0.02852 | 0.37123 | -0.088402 | 121.584 | 121.8366 | 121.7803 | -0.18704 | -0.035611 | -121.8549 | 0.019345 | 0.023625 | 0.059236 | -121.8472 | -121.7697 | -0.090913 | -0.2635 | 0.12465 | 0.007728 | 0.098641 | -0.01095 | -0.067271 | 0.088739 | 0.096489 | 0.174 | 0.051751 | -121.9793 | 121.6802 | 121.9327 | 121.8764 | 0.46736 | -122.0346
2007.9531 | 122.0215 | -0.15564 | 121.8887 | -0.0025182 | -0.040068 | 0.038798 | 0.025879 | -0.011651 | 0.0013291 | -0.013887 | -0.002053 | -0.0020767 | 0.059328 | 0.038978 | 0.049824 | -0.076785 | -0.053537 | -0.067927 | -0.007391 | -0.008799 | 0.082444 | -0.12716 | 0.023941 | 0.36666 | -0.092981 | 121.5795 | 121.8412 | 121.7803 | -0.18704 | 0.028478 | -121.8961 | 0.078855 | 0.087713 | 0.059235 | -121.8975 | -121.8063 | -0.031403 | -0.30928 | 0.17958 | 0.062659 | 0.094062 | -0.047571 | -0.10847 | 0.14825 | 0.14684 | 0.23808 | 0.1021 | -122.0159 | 121.7351 | 121.9968 | 121.9359 | 0.5223 | -122.0758
2009.6875 | 122.1497 | -0.12817 | 121.8384 | -0.0025182 | -0.039854 | 0.038798 | 0.025879 | -0.011651 | 0.0013291 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.039406 | 0.049824 | -0.076785 | -0.044379 | -0.067927 | -0.007391 | -0.00422 | 0.077866 | -0.118 | 0.02852 | 0.36666 | -0.083823 | 121.5886 | 121.8457 | 121.7803 | -0.18704 | 0.01017 | -121.8458 | 0.051389 | 0.060247 | 0.050077 | -121.8426 | -121.7605 | -0.058869 | -0.24977 | 0.15669 | 0.044351 | 0.10322 | 0.007362 | -0.058116 | 0.12078 | 0.12395 | 0.20604 | 0.083795 | -121.9564 | 121.7168 | 121.9739 | 121.9084 | 0.49483 | -122.0254
2011.4531 | 122.1405 | -0.10529 | 121.8658 | -0.0025182 | -0.040068 | 0.038584 | 0.026093 | -0.011651 | 0.00090167 | -0.013887 | -0.002053 | -0.0020767 | 0.058901 | 0.039406 | 0.049397 | -0.081363 | -0.044379 | -0.072505 | -0.002813 | 0.000359 | 0.087023 | -0.11342 | 0.02852 | 0.36208 | -0.088402 | 121.584 | 121.8503 | 121.7848 | -0.18704 | -0.008139 | -121.8687 | 0.023923 | 0.032781 | 0.04092 | -121.8655 | -121.7788 | -0.081757 | -0.28181 | 0.13381 | 0.016884 | 0.098641 | -0.015525 | -0.081003 | 0.10247 | 0.10565 | 0.19231 | 0.060907 | -121.9793 | 121.6893 | 121.9556 | 121.8901 | 0.46736 | -122.0529
2013.1406 | 122.0535 | -0.13733 | 121.8842 | -0.0025182 | -0.040068 | 0.03837 | 0.026307 | -0.011865 | 0.0011153 | -0.021518 | -0.002053 | -0.0020767 | 0.058687 | 0.039192 | 0.049824 | -0.067628 | -0.035222 | -0.067927 | 0.001765 | -0.00422 | 0.087023 | -0.11342 | 0.023941 | 0.36666 | -0.088402 | 121.5886 | 121.8457 | 121.7894 | -0.17788 | 0.023904 | -121.8824 | 0.069701 | 0.069402 | 0.045498 | -121.8884 | -121.7971 | -0.040556 | -0.29554 | 0.16127 | 0.048927 | 0.089483 | -0.038414 | -0.094735 | 0.13909 | 0.13311 | 0.22435 | 0.10211 | -121.9976 | 121.7259 | 121.9831 | 121.9267 | 0.50399 | -122.062
2014.8906 | 122.049 | -0.14648 | 121.9208 | -0.0025182 | -0.040068 | 0.039011 | 0.026093 | -0.011651 | 0.00068807 | -0.021518 | -0.002053 | -0.0020767 | 0.059328 | 0.039406 | 0.049824 | -0.081363 | -0.039801 | -0.067927 | -0.007391 | 0.000359 | 0.082444 | -0.11342 | 0.033099 | 0.36208 | -0.088402 | 121.5978 | 121.8503 | 121.794 | -0.18246 | 0.033059 | -121.9282 | 0.065121 | 0.078557 | 0.045498 | -121.9204 | -121.8383 | -0.03598 | -0.32301 | 0.17958 | 0.058082 | 0.094062 | -0.070456 | -0.12678 | 0.13909 | 0.14684 | 0.22893 | 0.10668 | -122.0342 | 121.7443 | 121.9968 | 121.9405 | 0.50856 | -122.1032
2016.6406 | 122.1222 | -0.11902 | 121.8704 | -0.01778 | -0.039854 | 0.03837 | 0.025879 | -0.011865 | 0.00090167 | -0.013887 | -0.002053 | -0.0020767 | 0.058687 | 0.039192 | 0.049824 | -0.072207 | -0.039801 | -0.067927 | 0.001765 | 0.004938 | 0.087023 | -0.11342 | 0.02852 | 0.36666 | -0.079245 | 121.5978 | 121.8595 | 121.7894 | -0.17788 | 0.005594 | -121.8687 | 0.046812 | 0.051092 | 0.045498 | -121.8655 | -121.7834 | -0.058866 | -0.27265 | 0.14754 | 0.039774 | 0.09864 | -0.010945 | -0.081002 | 0.12078 | 0.12396 | 0.20604 | 0.079218 | -121.9838 | 121.7168 | 121.9785 | 121.9084 | 0.48567 | -122.0483
2018.3906 | 122.0947 | -0.14648 | 121.8933 | -0.010149 | -0.039854 | 0.038584 | 0.026307 | -0.011651 | 0.0011153 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.039406 | 0.050038 | -0.06305 | -0.030644 | -0.067927 | 0.010922 | 0.004938 | 0.087023 | -0.118 | 0.023941 | 0.36666 | -0.083823 | 121.6023 | 121.8686 | 121.794 | -0.17331 | 0.02848 | -121.8824 | 0.083434 | 0.078557 | 0.050077 | -121.8884 | -121.8063 | -0.026822 | -0.29096 | 0.17042 | 0.062661 | 0.089483 | -0.024677 | -0.099312 | 0.15741 | 0.15142 | 0.23351 | 0.11584 | -122.0113 | 121.7488 | 122.0151 | 121.9405 | 0.51314 | -122.0666
2020.0781 | 122.1405 | -0.13733 | 121.8887 | -0.010149 | -0.040068 | 0.038584 | 0.025879 | -0.011651 | 0.00068807 | -0.013887 | -0.0022666 | -0.0025041 | 0.059114 | 0.039192 | 0.049824 | -0.076785 | -0.030644 | -0.063349 | 0.001765 | 0.000359 | 0.087023 | -0.11342 | 0.033099 | 0.37581 | -0.088402 | 121.6023 | 121.8641 | 121.7986 | -0.18246 | 0.023904 | -121.887 | 0.060544 | 0.07398 | 0.050076 | -121.8884 | -121.8017 | -0.045135 | -0.28638 | 0.17043 | 0.048927 | 0.094062 | -0.024678 | -0.090155 | 0.13909 | 0.13769 | 0.22435 | 0.10669 | -122.0022 | 121.7397 | 122.0014 | 121.9359 | 0.51314 | -122.0712
2021.8281 | 122.1497 | -0.086975 | 121.8704 | -0.010149 | -0.039854 | 0.038798 | 0.025879 | -0.011651 | 0.00068807 | -0.029148 | -0.0022666 | -0.0022903 | 0.059114 | 0.039406 | 0.049824 | -0.072207 | -0.030644 | -0.063349 | 0.001765 | 0.000359 | 0.087023 | -0.118 | 0.037677 | 0.37123 | -0.083823 | 121.5978 | 121.8686 | 121.7986 | -0.18246 | -0.031029 | -121.8687 | 0.014768 | 0.023626 | 0.054655 | -121.8701 | -121.7834 | -0.095489 | -0.27265 | 0.12465 | 0.003152 | 0.098641 | -0.001788 | -0.071844 | 0.08874 | 0.087334 | 0.174 | 0.056331 | -121.9884 | 121.6847 | 121.9556 | 121.8856 | 0.45821 | -122.0529
2023.5781 | 122.0993 | -0.14191 | 121.9391 | -0.010149 | -0.040068 | 0.038798 | 0.026093 | -0.011651 | 0.00068807 | -0.0062567 | -0.0018394 | -0.0022903 | 0.058901 | 0.039406 | 0.04961 | -0.072207 | -0.030644 | -0.063349 | 0.010922 | 0.000359 | 0.091601 | -0.10885 | 0.033099 | 0.37123 | -0.083823 | 121.6115 | 121.8686 | 121.8032 | -0.17788 | 0.03306 | -121.9282 | 0.0697 | 0.078558 | 0.045498 | -121.9387 | -121.8475 | -0.035978 | -0.32758 | 0.17501 | 0.058084 | 0.094062 | -0.070453 | -0.13593 | 0.15283 | 0.14227 | 0.23351 | 0.11126 | -122.0479 | 121.7534 | 122.0105 | 121.9451 | 0.51314 | -122.117
2025.3281 | 122.1313 | -0.10986 | 121.8933 | 0.0051128 | -0.040282 | 0.038798 | 0.026093 | -0.011651 | 0.00090167 | -0.0062567 | -0.002053 | -0.0022903 | 0.058901 | 0.039192 | 0.049824 | -0.072207 | -0.030644 | -0.05877 | 0.006344 | 0.004938 | 0.087023 | -0.11342 | 0.037677 | 0.36666 | -0.083823 | 121.5978 | 121.8869 | 121.8077 | -0.17788 | -0.003562 | -121.887 | 0.037656 | 0.051093 | 0.054655 | -121.8884 | -121.8063 | -0.068022 | -0.29554 | 0.14754 | 0.02604 | 0.094062 | -0.006363 | -0.085576 | 0.11621 | 0.1148 | 0.19689 | 0.079219 | -122.0067 | 121.7076 | 121.9968 | 121.9176 | 0.47652 | -122.0712
2027.0938 | 122.081 | -0.14648 | 121.9345 | 0.0051128 | -0.039854 | 0.039011 | 0.025879 | -0.011865 | 0.00090167 | -0.021518 | -0.002053 | -0.0022903 | 0.059328 | 0.039192 | 0.04961 | -0.067628 | -0.035222 | -0.063349 | 0.015501 | 0.004938 | 0.091601 | -0.10885 | 0.037677 | 0.37123 | -0.079245 | 121.6161 | 121.8686 | 121.8077 | -0.17788 | 0.037637 | -121.919 | 0.078856 | 0.083135 | 0.045498 | -121.9296 | -121.8429 | -0.031401 | -0.31843 | 0.18416 | 0.067239 | 0.09864 | -0.065875 | -0.12677 | 0.16198 | 0.15142 | 0.23808 | 0.11126 | -122.0434 | 121.7626 | 122.0151 | 121.9542 | 0.51772 | -122.1124
2028.7812 | 122.049 | -0.15106 | 121.9437 | -0.010149 | -0.040068 | 0.039011 | 0.025666 | -0.011651 | 0.00090167 | -0.021518 | -0.002053 | -0.0022903 | 0.059328 | 0.039619 | 0.050038 | -0.06305 | -0.035222 | -0.05877 | 0.006344 | 0.004938 | 0.091601 | -0.118 | 0.033099 | 0.36666 | -0.079245 | 121.6207 | 121.8732 | 121.8077 | -0.17788 | 0.033058 | -121.9373 | 0.088012 | 0.092292 | 0.059234 | -121.9387 | -121.8521 | -0.026823 | -0.323 | 0.18416 | 0.071817 | 0.09864 | -0.070452 | -0.13593 | 0.15741 | 0.156 | 0.24266 | 0.11584 | -122.0617 | 121.7717 | 122.0243 | 121.9588 | 0.51772 | -122.1215
2030.5312 | 122.1771 | -0.10986 | 121.9025 | -0.0025182 | -0.040282 | 0.039011 | 0.025452 | -0.011437 | 0.00090167 | -0.029148 | -0.0022666 | -0.0022903 | 0.059114 | 0.039406 | 0.049824 | -0.072207 | -0.030644 | -0.063349 | 0.006344 | 0.009517 | 0.077866 | -0.11342 | 0.042256 | 0.38039 | -0.083823 | 121.6207 | 121.8778 | 121.8077 | -0.17331 | -0.003562 | -121.8961 | 0.037656 | 0.046514 | 0.050076 | -121.8929 | -121.8246 | -0.063443 | -0.2818 | 0.15212 | 0.02604 | 0.089483 | -0.024675 | -0.094731 | 0.11621 | 0.11938 | 0.18773 | 0.079219 | -122.0159 | 121.7305 | 121.9877 | 121.9176 | 0.49025 | -122.0758
2032.2812 | 122.0901 | -0.14648 | 121.9025 | -0.0025182 | -0.040282 | 0.038798 | 0.025879 | -0.011437 | 0.00090167 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.039619 | 0.050038 | -0.06305 | -0.030644 | -0.054192 | 0.010922 | 0.009517 | 0.09618 | -0.10885 | 0.046835 | 0.36666 | -0.079245 | 121.6207 | 121.8824 | 121.8123 | -0.17788 | 0.037637 | -121.8915 | 0.083434 | 0.092292 | 0.054655 | -121.8929 | -121.8063 | -0.031401 | -0.2818 | 0.19332 | 0.067239 | 0.09864 | -0.020096 | -0.090153 | 0.15741 | 0.156 | 0.24266 | 0.11584 | -122.0113 | 121.7671 | 122.0289 | 121.9588 | 0.51314 | -122.0804
2033.9844 | 122.1176 | -0.11902 | 121.9162 | -0.01778 | -0.040495 | 0.039011 | 0.025666 | -0.011437 | 0.00068807 | -0.013887 | -0.0018394 | -0.0020767 | 0.059114 | 0.039619 | 0.049824 | -0.06305 | -0.026065 | -0.05877 | 0.006344 | 0.004938 | 0.10076 | -0.118 | 0.042256 | 0.37123 | -0.079245 | 121.6252 | 121.8824 | 121.8169 | -0.17331 | 0.001015 | -121.9099 | 0.055969 | 0.060249 | 0.059234 | -121.9113 | -121.8154 | -0.054287 | -0.29096 | 0.16128 | 0.039774 | 0.094061 | -0.033829 | -0.099307 | 0.12536 | 0.12396 | 0.21978 | 0.092954 | -122.0342 | 121.7443 | 122.0014 | 121.9359 | 0.49025 | -122.0895
2035.75 | 122.0581 | -0.16022 | 121.9299 | -0.010149 | -0.040282 | 0.039225 | 0.025666 | -0.011224 | 0.00068807 | -0.013887 | -0.0018394 | -0.0025041 | 0.059114 | 0.039619 | 0.050038 | -0.058472 | -0.035222 | -0.05877 | 0.001765 | 0.004938 | 0.10076 | -0.11342 | 0.037677 | 0.36666 | -0.079245 | 121.6252 | 121.8869 | 121.8123 | -0.17331 | 0.046792 | -121.9282 | 0.10175 | 0.10145 | 0.054655 | -121.925 | -121.8292 | -0.013089 | -0.30469 | 0.19789 | 0.080972 | 0.094061 | -0.042984 | -0.11762 | 0.16198 | 0.16515 | 0.26098 | 0.12499 | -122.0434 | 121.7855 | 122.0472 | 121.9725 | 0.52687 | -122.1032
2037.5 | 122.1222 | -0.12817 | 121.907 | -0.010149 | -0.040282 | 0.039225 | 0.025879 | -0.011651 | 0.00068807 | -0.0062567 | -0.002053 | -0.0020767 | 0.058901 | 0.039833 | 0.049824 | -0.067628 | -0.026065 | -0.05877 | 0.010922 | 0.004938 | 0.091601 | -0.10885 | 0.042256 | 0.37581 | -0.083823 | 121.6344 | 121.8915 | 121.8169 | -0.17788 | 0.019327 | -121.8961 | 0.060546 | 0.069404 | 0.050077 | -121.9021 | -121.8154 | -0.049711 | -0.27264 | 0.17043 | 0.044351 | 0.094062 | -0.015516 | -0.090151 | 0.1391 | 0.13311 | 0.21977 | 0.10211 | -122.0159 | 121.7626 | 122.0197 | 121.9451 | 0.50399 | -122.0849
2039.25 | 122.0306 | -0.15564 | 121.9437 | -0.0025182 | -0.040495 | 0.038798 | 0.025666 | -0.011437 | 0.00068807 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.039619 | 0.049824 | -0.053893 | -0.026065 | -0.054192 | 0.006344 | 0.009517 | 0.09618 | -0.10885 | 0.042256 | 0.37123 | -0.079245 | 121.6344 | 121.8915 | 121.826 | -0.16873 | 0.046793 | -121.9373 | 0.10175 | 0.10145 | 0.054655 | -121.9341 | -121.8475 | -0.013088 | -0.30927 | 0.1979 | 0.076395 | 0.089483 | -0.052138 | -0.11762 | 0.16198 | 0.16516 | 0.25182 | 0.12957 | -122.0525 | 121.79 | 122.0472 | 121.9817 | 0.52687 | -122.1124
2040.9531 | 122.1863 | -0.11444 | 121.9254 | -0.0025182 | -0.040282 | 0.039225 | 0.025452 | -0.011651 | 0.00090167 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.039619 | 0.04961 | -0.067628 | -0.026065 | -0.05877 | 0.015501 | 0.014096 | 0.091601 | -0.10885 | 0.042256 | 0.37581 | -0.079245 | 121.6252 | 121.8915 | 121.826 | -0.17788 | 0.005594 | -121.9099 | 0.046813 | 0.055671 | 0.050077 | -121.9113 | -121.8338 | -0.063444 | -0.30011 | 0.1567 | 0.035196 | 0.09864 | -0.033827 | -0.099305 | 0.12994 | 0.12854 | 0.20604 | 0.088376 | -122.0342 | 121.7397 | 122.006 | 121.9405 | 0.49025 | -122.1032
2042.6875 | 122.0398 | -0.14648 | 121.9437 | -0.010149 | -0.040282 | 0.039225 | 0.025879 | -0.011651 | 0.00068807 | -0.013887 | -0.0022666 | -0.0022903 | 0.059114 | 0.039406 | 0.049824 | -0.06305 | -0.030644 | -0.054192 | 0.015501 | 0.009517 | 0.091601 | -0.10885 | 0.042256 | 0.37123 | -0.074666 | 121.6298 | 121.9007 | 121.8306 | -0.16873 | 0.037637 | -121.9282 | 0.083434 | 0.092292 | 0.054655 | -121.9341 | -121.8521 | -0.022244 | -0.31385 | 0.18874 | 0.071818 | 0.094062 | -0.042981 | -0.11304 | 0.16198 | 0.156 | 0.23808 | 0.11584 | -122.0525 | 121.7763 | 122.0472 | 121.9771 | 0.51772 | -122.1124
2044.4375 | 122.1039 | -0.1236 | 121.9574 | 0.0051128 | -0.040282 | 0.039011 | 0.025879 | -0.011651 | 0.00090167 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.039406 | 0.049824 | -0.067628 | -0.026065 | -0.05877 | 0.010922 | 0.014096 | 0.091601 | -0.11342 | 0.033099 | 0.38039 | -0.074666 | 121.6436 | 121.8961 | 121.8398 | -0.17788 | 0.010171 | -121.9465 | 0.055968 | 0.064826 | 0.054655 | -121.9433 | -121.8658 | -0.054289 | -0.31384 | 0.1567 | 0.04893 | 0.10322 | -0.061291 | -0.11761 | 0.13452 | 0.13769 | 0.2152 | 0.097531 | -122.0708 | 121.7672 | 122.0197 | 121.9634 | 0.50399 | -122.1353
2046.1406 | 122.1542 | -0.1236 | 121.9299 | -0.0025182 | -0.040709 | 0.039011 | 0.025666 | -0.011437 | 0.00068807 | -0.013887 | -0.002053 | -0.0020767 | 0.058901 | 0.039619 | 0.04961 | -0.06305 | -0.026065 | -0.054192 | 0.015501 | 0.014096 | 0.09618 | -0.10427 | 0.042256 | 0.37581 | -0.079245 | 121.6436 | 121.9053 | 121.8352 | -0.17331 | 0.019328 | -121.9144 | 0.060546 | 0.069404 | 0.050076 | -121.9158 | -121.8338 | -0.04971 | -0.28638 | 0.16585 | 0.044351 | 0.094061 | -0.024669 | -0.094726 | 0.1391 | 0.13769 | 0.21978 | 0.097531 | -122.0342 | 121.7672 | 122.0289 | 121.9588 | 0.49941 | -122.1032
2047.8906 | 122.1497 | -0.11444 | 121.9299 | -0.01778 | -0.040495 | 0.039011 | 0.025666 | -0.011651 | 0.00068807 | -0.021518 | -0.0018394 | -0.0020767 | 0.059114 | 0.039833 | 0.049824 | -0.058472 | -0.021486 | -0.05877 | 0.010922 | 0.014096 | 0.09618 | -0.10885 | 0.051413 | 0.37581 | -0.079245 | 121.639 | 121.9098 | 121.8398 | -0.16873 | 0.005594 | -121.919 | 0.055969 | 0.055671 | 0.050077 | -121.9158 | -121.8338 | -0.054287 | -0.29095 | 0.16585 | 0.035196 | 0.089483 | -0.020091 | -0.090147 | 0.12536 | 0.12854 | 0.21062 | 0.092955 | -122.0388 | 121.7534 | 122.0243 | 121.9542 | 0.49025 | -122.0987
2049.6406 | 122.1313 | -0.11444 | 121.9208 | -0.0025182 | -0.040709 | 0.039439 | 0.025879 | -0.011865 | 0.00068807 | -0.021518 | -0.0016258 | -0.0020767 | 0.058901 | 0.040047 | 0.049824 | -0.06305 | -0.021486 | -0.049614 | 0.010922 | 0.009517 | 0.091601 | -0.10885 | 0.042256 | 0.37581 | -0.074666 | 121.639 | 121.9053 | 121.8352 | -0.17331 | 0.005594 | -121.9099 | 0.051391 | 0.064827 | 0.059233 | -121.9113 | -121.8292 | -0.058865 | -0.2818 | 0.1567 | 0.039775 | 0.09864 | -0.015513 | -0.08557 | 0.12536 | 0.12396 | 0.20604 | 0.092955 | -122.0296 | 121.7534 | 122.0197 | 121.9496 | 0.49025 | -122.0941
2051.3906 | 122.1451 | -0.10529 | 121.9345 | -0.010149 | -0.040709 | 0.039439 | 0.025452 | -0.011865 | 0.00068807 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.039406 | 0.04961 | -0.058472 | -0.021486 | -0.045036 | 0.010922 | 0.014096 | 0.09618 | -0.10885 | 0.046835 | 0.37123 | -0.079245 | 121.6481 | 121.9144 | 121.8352 | -0.17331 | -0.003561 | -121.9236 | 0.046814 | 0.06025 | 0.063811 | -121.9204 | -121.8383 | -0.06802 | -0.28638 | 0.15212 | 0.026041 | 0.094061 | -0.020089 | -0.099303 | 0.11621 | 0.11938 | 0.20147 | 0.0838 | -122.0434 | 121.7534 | 122.0197 | 121.9405 | 0.47652 | -122.1078
2053.1406 | 122.0627 | -0.14191 | 121.9345 | -0.010149 | -0.040709 | 0.039439 | 0.025238 | -0.011437 | 0.00047427 | -0.0062567 | -0.0022666 | -0.0025041 | 0.059114 | 0.039619 | 0.049824 | -0.06305 | -0.026065 | -0.049614 | 0.015501 | 0.014096 | 0.09618 | -0.10427 | 0.046835 | 0.38039 | -0.074666 | 121.6527 | 121.9098 | 121.8398 | -0.16873 | 0.037639 | -121.919 | 0.078857 | 0.092293 | 0.054654 | -121.9204 | -121.8383 | -0.026821 | -0.2818 | 0.18874 | 0.067241 | 0.094062 | -0.024668 | -0.094724 | 0.15741 | 0.156 | 0.23809 | 0.11584 | -122.0388 | 121.7946 | 122.0517 | 121.9817 | 0.5223 | -122.1032
2054.8281 | 122.2 | -0.082397 | 121.9116 | -0.01778 | -0.040495 | 0.038798 | 0.025452 | -0.011651 | 0.00068807 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.039619 | 0.049397 | -0.058472 | -0.026065 | -0.05877 | 0.015501 | 0.014096 | 0.10076 | -0.10885 | 0.033099 | 0.37581 | -0.070087 | 121.6481 | 121.9236 | 121.8444 | -0.17331 | -0.02645 | -121.8961 | 0.023925 | 0.023627 | 0.050077 | -121.8975 | -121.8109 | -0.090909 | -0.26349 | 0.1155 | 0.01231 | 0.10322 | 0.011956 | -0.067257 | 0.097898 | 0.096493 | 0.18316 | 0.056332 | -122.0205 | 121.7305 | 122.006 | 121.9268 | 0.45821 | -122.0849
2056.5781 | 122.0993 | -0.12817 | 121.9482 | -0.0025182 | -0.040495 | 0.039011 | 0.025452 | -0.011651 | 0.00068807 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058901 | 0.039619 | 0.049824 | -0.058472 | -0.021486 | -0.054192 | 0.024657 | 0.018675 | 0.09618 | -0.10427 | 0.046835 | 0.38039 | -0.074666 | 121.6573 | 121.9144 | 121.8535 | -0.16873 | 0.023906 | -121.9236 | 0.069702 | 0.073982 | 0.050076 | -121.9296 | -121.8521 | -0.040554 | -0.29095 | 0.17501 | 0.053508 | 0.094062 | -0.033822 | -0.094721 | 0.15283 | 0.14685 | 0.22435 | 0.10669 | -122.0525 | 121.7855 | 122.0426 | 121.9817 | 0.50857 | -122.117
2058.3281 | 122.168 | -0.10986 | 121.9391 | -0.010149 | -0.040923 | 0.039225 | 0.025879 | -0.011865 | 0.00068807 | -0.029148 | -0.002053 | -0.0025041 | 0.059328 | 0.039619 | 0.049397 | -0.053893 | -0.021486 | -0.049614 | 0.020079 | 0.014096 | 0.10534 | -0.10427 | 0.046835 | 0.37123 | -0.074666 | 121.6527 | 121.9236 | 121.8444 | -0.16873 | 0.005595 | -121.919 | 0.05597 | 0.060249 | 0.054654 | -121.925 | -121.8337 | -0.058865 | -0.28638 | 0.1567 | 0.035197 | 0.094062 | -0.01551 | -0.094723 | 0.12994 | 0.12396 | 0.2152 | 0.088377 | -122.0434 | 121.7626 | 122.0334 | 121.9542 | 0.4811 | -122.1078
2060.0781 | 122.1771 | -0.1236 | 121.9391 | -0.010149 | -0.040068 | 0.039225 | 0.025452 | -0.011651 | 0.00090167 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.039619 | 0.050038 | -0.06305 | -0.030644 | -0.054192 | 0.006344 | 0.014096 | 0.09618 | -0.099689 | 0.042256 | 0.36666 | -0.074666 | 121.6573 | 121.9282 | 121.8444 | -0.17331 | 0.023907 | -121.9327 | 0.060546 | 0.069404 | 0.045497 | -121.925 | -121.8429 | -0.04971 | -0.2818 | 0.16585 | 0.04893 | 0.09864 | -0.010931 | -0.094723 | 0.12994 | 0.13769 | 0.21978 | 0.092952 | -122.0388 | 121.7809 | 122.0518 | 121.968 | 0.49025 | -122.1124
2061.7656 | 122.0993 | -0.13733 | 121.9711 | -0.010149 | -0.040495 | 0.039225 | 0.025666 | -0.011865 | 0.00068807 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.040047 | 0.049397 | -0.058472 | -0.026065 | -0.049614 | 0.015501 | 0.014096 | 0.09618 | -0.099689 | 0.046835 | 0.37123 | -0.074666 | 121.6481 | 121.9236 | 121.8489 | -0.16873 | 0.03764 | -121.9556 | 0.078857 | 0.087715 | 0.050075 | -121.957 | -121.8749 | -0.031399 | -0.323 | 0.18416 | 0.062663 | 0.094062 | -0.047553 | -0.12219 | 0.15283 | 0.15143 | 0.23351 | 0.11126 | -122.0708 | 121.7855 | 122.0609 | 121.9863 | 0.50856 | -122.1399
2063.5156 | 122.081 | -0.13733 | 121.9757 | -0.0025182 | -0.040495 | 0.039225 | 0.025238 | -0.011651 | 0.00026067 | -0.0062567 | -0.0018394 | -0.0025041 | 0.058901 | 0.039833 | 0.04961 | -0.053893 | -0.026065 | -0.049614 | 0.015501 | 0.023254 | 0.09618 | -0.10427 | 0.051413 | 0.37581 | -0.079245 | 121.6573 | 121.9236 | 121.8627 | -0.16873 | 0.033061 | -121.9602 | 0.083436 | 0.087715 | 0.054654 | -121.9525 | -121.8795 | -0.031399 | -0.31842 | 0.18874 | 0.058084 | 0.089483 | -0.052131 | -0.11303 | 0.15283 | 0.16058 | 0.23351 | 0.11126 | -122.08 | 121.7946 | 122.0609 | 122 | 0.51314 | -122.1444
2065.2656 | 122.2 | -0.082397 | 121.9437 | -0.010149 | -0.040495 | 0.039011 | 0.025452 | -0.011651 | 0.00068807 | -0.013887 | -0.002053 | -0.0020767 | 0.058901 | 0.039833 | 0.04961 | -0.058472 | -0.026065 | -0.049614 | 0.020079 | 0.018675 | 0.10076 | -0.10427 | 0.046835 | 0.38039 | -0.070087 | 121.6664 | 121.9282 | 121.8444 | -0.16415 | -0.021871 | -121.9236 | 0.023925 | 0.032783 | 0.054654 | -121.925 | -121.8429 | -0.081752 | -0.27722 | 0.12923 | 0.01231 | 0.094062 | -0.015509 | -0.099301 | 0.10248 | 0.10107 | 0.18316 | 0.056332 | -122.0479 | 121.7488 | 122.0106 | 121.9268 | 0.46279 | -122.1078
2066.9531 | 122.1634 | -0.10071 | 121.9437 | -0.010149 | -0.040495 | 0.039011 | 0.025879 | -0.011651 | 0.00047427 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.039833 | 0.049397 | -0.049315 | -0.021486 | -0.054192 | 0.015501 | 0.018675 | 0.10076 | -0.10427 | 0.051413 | 0.38039 | -0.074666 | 121.6664 | 121.9373 | 121.8535 | -0.16873 | -0.00356 | -121.9282 | 0.051393 | 0.046516 | 0.050076 | -121.925 | -121.8429 | -0.06802 | -0.27722 | 0.15212 | 0.026042 | 0.094062 | -0.006352 | -0.090144 | 0.11621 | 0.11938 | 0.20147 | 0.079222 | -122.0479 | 121.7672 | 122.038 | 121.9542 | 0.4811 | -122.1124
2068.7031 | 122.1313 | -0.11902 | 121.9391 | -0.01778 | -0.040282 | 0.039011 | 0.025666 | -0.011437 | 0.00047427 | -0.021518 | -0.0022666 | -0.0022903 | 0.058901 | 0.039833 | 0.04961 | -0.053893 | -0.026065 | -0.045036 | 0.010922 | 0.023254 | 0.09618 | -0.09511 | 0.051413 | 0.38039 | -0.074666 | 121.671 | 121.9282 | 121.8581 | -0.16873 | 0.023909 | -121.9282 | 0.065126 | 0.073983 | 0.050074 | -121.9158 | -121.8429 | -0.049709 | -0.26806 | 0.17043 | 0.044353 | 0.094062 | -0.010931 | -0.080988 | 0.12994 | 0.14227 | 0.2152 | 0.092954 | -122.0342 | 121.79 | 122.0472 | 121.9771 | 0.49941 | -122.1078
2070.3906 | 122.1176 | -0.13275 | 121.9666 | -0.01778 | -0.040282 | 0.039011 | 0.025879 | -0.011437 | 0.00047427 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.039833 | 0.04961 | -0.058472 | -0.026065 | -0.049614 | 0.020079 | 0.018675 | 0.10076 | -0.10885 | 0.046835 | 0.36666 | -0.074666 | 121.671 | 121.9327 | 121.8627 | -0.17331 | 0.023904 | -121.9465 | 0.074279 | 0.083137 | 0.059233 | -121.9479 | -121.8658 | -0.040555 | -0.29553 | 0.17959 | 0.058085 | 0.09864 | -0.033819 | -0.10388 | 0.15283 | 0.15143 | 0.23351 | 0.10669 | -122.0754 | 121.8038 | 122.0655 | 121.9954 | 0.49941 | -122.1399
2072.1406 | 122.081 | -0.14191 | 121.9849 | -0.010149 | -0.040068 | 0.039011 | 0.025666 | -0.011865 | 0.00026067 | -0.021518 | -0.0022666 | -0.0025041 | 0.059114 | 0.039833 | 0.04961 | -0.058472 | -0.035222 | -0.049614 | 0.015501 | 0.018675 | 0.10992 | -0.09511 | 0.046835 | 0.38497 | -0.070087 | 121.671 | 121.9327 | 121.8673 | -0.16415 | 0.046797 | -121.9694 | 0.083435 | 0.092293 | 0.045496 | -121.9662 | -121.8749 | -0.022242 | -0.31384 | 0.18874 | 0.07182 | 0.094062 | -0.052129 | -0.11761 | 0.15741 | 0.16058 | 0.25182 | 0.10669 | -122.08 | 121.8129 | 122.0746 | 122.0092 | 0.52688 | -122.149
2073.8281 | 122.0856 | -0.15564 | 121.9711 | -0.0025182 | -0.040709 | 0.039225 | 0.025666 | -0.011651 | 0.00068807 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.039833 | 0.049824 | -0.049315 | -0.021486 | -0.040457 | 0.015501 | 0.023254 | 0.091601 | -0.099689 | 0.055992 | 0.38039 | -0.079245 | 121.671 | 121.9327 | 121.8627 | -0.16873 | 0.055951 | -121.9556 | 0.10633 | 0.11518 | 0.059232 | -121.9479 | -121.8795 | -0.013088 | -0.3001 | 0.21163 | 0.076395 | 0.089483 | -0.038396 | -0.10845 | 0.17114 | 0.17889 | 0.24724 | 0.13415 | -122.0708 | 121.8267 | 122.0884 | 122.0183 | 0.53603 | -122.1399
2075.5625 | 122.0718 | -0.11902 | 121.9803 | -0.010149 | -0.040495 | 0.038584 | 0.025879 | -0.011865 | 0.00068807 | -0.021518 | -0.0018394 | -0.0025041 | 0.059114 | 0.039406 | 0.049397 | -0.049315 | -0.021486 | -0.049614 | 0.024657 | 0.014096 | 0.10534 | -0.099689 | 0.042256 | 0.37581 | -0.079245 | 121.6756 | 121.9327 | 121.8673 | -0.16415 | 0.01933 | -121.9556 | 0.069704 | 0.069405 | 0.050075 | -121.9662 | -121.8749 | -0.04513 | -0.30468 | 0.16128 | 0.039774 | 0.084904 | -0.047552 | -0.11303 | 0.14368 | 0.13312 | 0.22436 | 0.097533 | -122.08 | 121.7946 | 122.0518 | 121.9863 | 0.49483 | -122.1444
2077.25 | 122.168 | -0.11444 | 121.9528 | -0.010149 | -0.040495 | 0.038798 | 0.025452 | -0.011651 | 0.00047427 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.039833 | 0.04961 | -0.058472 | -0.026065 | -0.049614 | 0.020079 | 0.018675 | 0.10534 | -0.09511 | 0.051413 | 0.38039 | -0.070087 | 121.6756 | 121.9327 | 121.8673 | -0.16415 | 0.019331 | -121.9327 | 0.055969 | 0.064827 | 0.045496 | -121.9341 | -121.8475 | -0.049708 | -0.27721 | 0.16585 | 0.044354 | 0.094062 | -0.020086 | -0.085563 | 0.13452 | 0.13312 | 0.21978 | 0.088376 | -122.0479 | 121.79 | 122.0472 | 121.9817 | 0.49483 | -122.117
2078.9375 | 122.0947 | -0.12817 | 121.9711 | -0.0025182 | -0.040282 | 0.03837 | 0.025666 | -0.011865 | 0.00047427 | -0.021518 | -0.0018394 | -0.0022903 | 0.059114 | 0.039833 | 0.049397 | -0.053893 | -0.021486 | -0.045036 | 0.015501 | 0.023254 | 0.09618 | -0.099689 | 0.046835 | 0.38039 | -0.070087 | 121.6848 | 121.9373 | 121.8718 | -0.15957 | 0.028485 | -121.9556 | 0.074281 | 0.083138 | 0.054653 | -121.9479 | -121.8749 | -0.031396 | -0.28637 | 0.17501 | 0.058087 | 0.089483 | -0.033817 | -0.099295 | 0.14367 | 0.15143 | 0.22435 | 0.10669 | -122.0708 | 121.8129 | 122.0655 | 122 | 0.50857 | -122.1307
2080.6875 | 122.2092 | -0.1236 | 121.9666 | -0.0025182 | -0.040068 | 0.038584 | 0.025666 | -0.011651 | 0.00047427 | -0.021518 | -0.002053 | -0.0020767 | 0.059114 | 0.039619 | 0.04961 | -0.049315 | -0.016908 | -0.045036 | 0.020079 | 0.023254 | 0.10076 | -0.09511 | 0.055992 | 0.38497 | -0.070087 | 121.6756 | 121.9373 | 121.8673 | -0.16873 | 0.028486 | -121.9465 | 0.074281 | 0.07856 | 0.050074 | -121.9433 | -121.8658 | -0.045132 | -0.29095 | 0.17959 | 0.053509 | 0.098641 | -0.02924 | -0.099296 | 0.14367 | 0.14685 | 0.22435 | 0.10669 | -122.0617 | 121.7992 | 122.0609 | 121.9909 | 0.50857 | -122.1353
2082.3906 | 122.0718 | -0.14648 | 122.0032 | -0.010149 | -0.040495 | 0.038798 | 0.025666 | -0.011437 | 0.00068807 | -0.013887 | -0.002053 | -0.0020767 | 0.059328 | 0.039833 | 0.049824 | -0.058472 | -0.021486 | -0.045036 | 0.015501 | 0.018675 | 0.10534 | -0.09511 | 0.046835 | 0.38039 | -0.065509 | 121.6802 | 121.9419 | 121.8718 | -0.16415 | 0.051374 | -121.9877 | 0.088012 | 0.10145 | 0.050074 | -121.9845 | -121.8978 | -0.017665 | -0.32299 | 0.19332 | 0.080975 | 0.09864 | -0.061282 | -0.13134 | 0.16198 | 0.16516 | 0.25182 | 0.125 | -122.0983 | 121.8267 | 122.0884 | 122.0183 | 0.52688 | -122.1673
2084.1406 | 122.1313 | -0.12817 | 121.9894 | -0.010149 | -0.040709 | 0.038584 | 0.025666 | -0.011651 | 0.00068807 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.039833 | 0.049397 | -0.049315 | -0.026065 | -0.045036 | 0.015501 | 0.023254 | 0.10534 | -0.099689 | 0.046835 | 0.37581 | -0.074666 | 121.6756 | 121.9373 | 121.8718 | -0.16873 | 0.028485 | -121.9739 | 0.078859 | 0.083138 | 0.054653 | -121.9662 | -121.8841 | -0.040554 | -0.31384 | 0.17501 | 0.053508 | 0.094062 | -0.052128 | -0.11761 | 0.14367 | 0.15143 | 0.23351 | 0.10211 | -122.0891 | 121.8038 | 122.0655 | 122 | 0.50399 | -122.1582
2085.8281 | 122.1451 | -0.14648 | 121.9482 | -0.010149 | -0.040495 | 0.038584 | 0.025452 | -0.011437 | 0.00068807 | -0.021518 | -0.0018394 | -0.0025041 | 0.058687 | 0.039833 | 0.04961 | -0.058472 | -0.026065 | -0.049614 | 0.015501 | 0.023254 | 0.10076 | -0.10427 | 0.046835 | 0.37581 | -0.074666 | 121.6802 | 121.951 | 121.881 | -0.16873 | 0.042216 | -121.9327 | 0.088012 | 0.09687 | 0.054654 | -121.925 | -121.8475 | -0.022244 | -0.26806 | 0.19332 | 0.071818 | 0.094062 | 0.002807 | -0.06725 | 0.16198 | 0.16974 | 0.24724 | 0.12042 | -122.0525 | 121.8267 | 122.0975 | 122.0275 | 0.5223 | -122.117
2087.5781 | 122.168 | -0.082397 | 121.9482 | -0.01778 | -0.040709 | 0.038584 | 0.025666 | -0.011437 | 0.00068807 | -0.029148 | -0.002053 | -0.0027177 | 0.059114 | 0.039833 | 0.049183 | -0.049315 | -0.026065 | -0.049614 | 0.015501 | 0.023254 | 0.10534 | -0.099689 | 0.055992 | 0.38039 | -0.065509 | 121.6848 | 121.9465 | 121.8718 | -0.17788 | -0.017292 | -121.9327 | 0.033082 | 0.032783 | 0.050075 | -121.925 | -121.8429 | -0.095488 | -0.26348 | 0.13839 | 0.016888 | 0.11238 | -0.001772 | -0.076407 | 0.097898 | 0.10565 | 0.18773 | 0.056332 | -122.0479 | 121.7672 | 122.0289 | 121.9542 | 0.46279 | -122.1261
2089.2656 | 122.1863 | -0.10986 | 121.9757 | -0.010149 | -0.040495 | 0.038584 | 0.025666 | -0.011437 | 0.00047427 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.040047 | 0.049824 | -0.058472 | -0.016908 | -0.045036 | 0.020079 | 0.023254 | 0.10076 | -0.099689 | 0.060571 | 0.38039 | -0.065509 | 121.6939 | 121.9419 | 121.8718 | -0.16415 | 0.010174 | -121.9556 | 0.051391 | 0.064827 | 0.054653 | -121.9525 | -121.8749 | -0.054286 | -0.28179 | 0.17043 | 0.044354 | 0.09864 | -0.033816 | -0.10387 | 0.12994 | 0.13312 | 0.21062 | 0.092955 | -122.0754 | 121.8038 | 122.0518 | 121.9817 | 0.49025 | -122.1399
2091.0156 | 122.1451 | -0.11902 | 121.9803 | -0.0025182 | -0.040495 | 0.038584 | 0.025238 | -0.012078 | 0.00047427 | -0.0062567 | -0.002053 | -0.0022903 | 0.059114 | 0.039406 | 0.049824 | -0.058472 | -0.016908 | -0.045036 | 0.015501 | 0.014096 | 0.10076 | -0.099689 | 0.051413 | 0.38039 | -0.065509 | 121.6893 | 121.9465 | 121.8856 | -0.16873 | 0.01933 | -121.9648 | 0.060547 | 0.073983 | 0.054653 | -121.9662 | -121.8795 | -0.049709 | -0.29095 | 0.17043 | 0.05351 | 0.10322 | -0.033816 | -0.094715 | 0.13452 | 0.13312 | 0.21978 | 0.10211 | -122.08 | 121.8084 | 122.0655 | 122.0046 | 0.49941 | -122.149
2092.7656 | 122.2321 | -0.082397 | 121.9803 | -0.0025182 | -0.040495 | 0.03837 | 0.025879 | -0.011651 | 0.00068807 | -0.021518 | -0.0018394 | -0.0022903 | 0.059328 | 0.039833 | 0.04961 | -0.053893 | -0.016908 | -0.045036 | 0.029236 | 0.018675 | 0.10992 | -0.09511 | 0.055992 | 0.38039 | -0.070087 | 121.6893 | 121.9556 | 121.8902 | -0.15957 | -0.012713 | -121.9511 | 0.028504 | 0.037361 | 0.050074 | -121.9616 | -121.8704 | -0.077173 | -0.29095 | 0.13839 | 0.01231 | 0.089483 | -0.024659 | -0.090136 | 0.11163 | 0.10107 | 0.19231 | 0.065489 | -122.0754 | 121.7717 | 122.038 | 121.9725 | 0.46279 | -122.1399
2094.5312 | 122.1954 | -0.11444 | 121.9711 | -0.0025182 | -0.041136 | 0.038584 | 0.025879 | -0.011651 | 0.00068807 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.039833 | 0.049397 | -0.053893 | -0.021486 | -0.045036 | 0.015501 | 0.023254 | 0.10992 | -0.099689 | 0.060571 | 0.37581 | -0.065509 | 121.6893 | 121.9465 | 121.8856 | -0.15499 | 0.014752 | -121.9556 | 0.060548 | 0.069405 | 0.054653 | -121.9479 | -121.8612 | -0.04055 | -0.28179 | 0.17501 | 0.048932 | 0.089482 | -0.02466 | -0.085559 | 0.12994 | 0.1377 | 0.22436 | 0.092955 | -122.0708 | 121.8038 | 122.0609 | 122 | 0.49025 | -122.1261
2096.2812 | 122.1634 | -0.13733 | 121.9986 | 0.0051128 | -0.040282 | 0.038798 | 0.025879 | -0.012078 | 0.00090167 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.040047 | 0.049397 | -0.053893 | -0.021486 | -0.040457 | 0.020079 | 0.018675 | 0.10534 | -0.09511 | 0.055992 | 0.38039 | -0.065509 | 121.6848 | 121.9602 | 121.8856 | -0.15499 | 0.042219 | -121.9785 | 0.083436 | 0.096872 | 0.054653 | -121.9799 | -121.8933 | -0.017662 | -0.31383 | 0.19332 | 0.07182 | 0.089482 | -0.03839 | -0.11303 | 0.15741 | 0.156 | 0.24267 | 0.11584 | -122.0937 | 121.8221 | 122.0975 | 122.0229 | 0.51772 | -122.1536
2097.9688 | 122.2092 | -0.10986 | 121.9803 | -0.01778 | -0.040709 | 0.038584 | 0.025452 | -0.011437 | 0.00068807 | -0.029148 | -0.0018394 | -0.0025041 | 0.059114 | 0.039833 | 0.049824 | -0.049315 | -0.016908 | -0.040457 | 0.015501 | 0.023254 | 0.10992 | -0.09511 | 0.055992 | 0.38039 | -0.070087 | 121.6893 | 121.9602 | 121.8902 | -0.15957 | 0.014753 | -121.9648 | 0.060548 | 0.069406 | 0.054653 | -121.957 | -121.8704 | -0.049707 | -0.29095 | 0.16586 | 0.039776 | 0.089483 | -0.02008 | -0.090136 | 0.12536 | 0.13312 | 0.21978 | 0.092955 | -122.0754 | 121.7992 | 122.0701 | 122 | 0.49025 | -122.1399
2099.7188 | 122.1085 | -0.13733 | 122.0032 | -0.010149 | -0.040709 | 0.038584 | 0.025452 | -0.011651 | 0.00047427 | -0.013887 | -0.0024804 | -0.0022903 | 0.058901 | 0.039833 | 0.049397 | -0.053893 | -0.012329 | -0.040457 | 0.024657 | 0.023254 | 0.10534 | -0.09511 | 0.051413 | 0.38039 | -0.074666 | 121.6939 | 121.9602 | 121.8902 | -0.16415 | 0.042219 | -121.9785 | 0.083436 | 0.096872 | 0.054653 | -121.9799 | -121.8978 | -0.02682 | -0.30926 | 0.18874 | 0.062663 | 0.089483 | -0.042968 | -0.11302 | 0.16199 | 0.16058 | 0.24267 | 0.125 | -122.0983 | 121.8312 | 122.0975 | 122.0275 | 0.51772 | -122.1673
2101.4062 | 122.1497 | -0.12817 | 121.9757 | -0.01778 | -0.040709 | 0.038157 | 0.025452 | -0.011437 | 0.00068807 | -0.021518 | -0.0018394 | -0.0025041 | 0.058901 | 0.039833 | 0.04961 | -0.044736 | -0.021486 | -0.045036 | 0.015501 | 0.027833 | 0.10076 | -0.099689 | 0.055992 | 0.38039 | -0.06093 | 121.6985 | 121.9648 | 121.8902 | -0.15957 | 0.028485 | -121.9602 | 0.083438 | 0.083138 | 0.054653 | -121.9479 | -121.8749 | -0.031396 | -0.27721 | 0.18417 | 0.067244 | 0.09864 | -0.010923 | -0.085558 | 0.14367 | 0.15601 | 0.22893 | 0.10669 | -122.0754 | 121.8267 | 122.093 | 122.0183 | 0.50857 | -122.1353
2103.1719 | 122.1268 | -0.14648 | 121.9986 | 0.0051128 | -0.040495 | 0.038584 | 0.025666 | -0.011651 | 0.0011153 | -0.021518 | -0.0018394 | -0.0020767 | 0.059114 | 0.039619 | 0.049824 | -0.049315 | -0.016908 | -0.049614 | 0.024657 | 0.023254 | 0.10534 | -0.099689 | 0.055992 | 0.38039 | -0.070087 | 121.6985 | 121.9602 | 121.8902 | -0.16415 | 0.046795 | -121.9739 | 0.097169 | 0.09687 | 0.050075 | -121.9753 | -121.8933 | -0.017665 | -0.3001 | 0.20248 | 0.076397 | 0.094062 | -0.03839 | -0.10845 | 0.17114 | 0.16974 | 0.25182 | 0.12958 | -122.0983 | 121.845 | 122.1067 | 122.0366 | 0.52688 | -122.1627
2104.8594 | 122.1634 | -0.09613 | 121.9849 | -0.0025182 | -0.040709 | 0.038157 | 0.025666 | -0.011865 | 0.00090167 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.039619 | 0.049397 | -0.053893 | -0.012329 | -0.045036 | 0.020079 | 0.023254 | 0.10076 | -0.099689 | 0.055992 | 0.38955 | -0.06093 | 121.6985 | 121.9602 | 121.8993 | -0.15957 | -0.003559 | -121.9648 | 0.042237 | 0.051094 | 0.054653 | -121.9616 | -121.8841 | -0.06344 | -0.28637 | 0.15212 | 0.0352 | 0.09864 | -0.024657 | -0.085556 | 0.11621 | 0.11938 | 0.19689 | 0.083801 | -122.0846 | 121.7946 | 122.0563 | 121.9954 | 0.48568 | -122.1444
2106.6094 | 122.2321 | -0.10071 | 121.9757 | -0.010149 | -0.040923 | 0.038584 | 0.025452 | -0.011651 | 0.00047427 | -0.013887 | -0.0016258 | -0.0022903 | 0.058901 | 0.040047 | 0.049397 | -0.058472 | -0.016908 | -0.045036 | 0.020079 | 0.027833 | 0.10534 | -0.099689 | 0.051413 | 0.38039 | -0.070087 | 121.7031 | 121.9739 | 121.8947 | -0.16415 | 0.001019 | -121.9556 | 0.042236 | 0.055672 | 0.054653 | -121.9479 | -121.8704 | -0.063441 | -0.27263 | 0.15212 | 0.030621 | 0.094062 | -0.001766 | -0.08098 | 0.12079 | 0.12854 | 0.20605 | 0.0838 | -122.0754 | 121.8038 | 122.0746 | 121.9954 | 0.4811 | -122.1399
2108.3594 | 122.2275 | -0.07782 | 121.9482 | -0.010149 | -0.040923 | 0.038798 | 0.025666 | -0.011437 | 0.00068807 | -0.021518 | -0.0022666 | -0.0027177 | 0.059114 | 0.04026 | 0.049824 | -0.049315 | -0.007751 | -0.040457 | 0.020079 | 0.027833 | 0.11449 | -0.10427 | 0.060571 | 0.38497 | -0.06093 | 121.6985 | 121.9648 | 121.8993 | -0.16415 | -0.026448 | -121.9282 | 0.028505 | 0.037363 | 0.063811 | -121.9204 | -121.8337 | -0.086329 | -0.24974 | 0.13839 | 0.01689 | 0.10322 | 0.016543 | -0.048935 | 0.097899 | 0.10565 | 0.19231 | 0.070069 | -122.0525 | 121.7763 | 122.0426 | 121.9771 | 0.46279 | -122.1124
2110.125 | 122.1359 | -0.12817 | 122.0306 | -0.0025182 | -0.040923 | 0.038584 | 0.025666 | -0.011437 | 0.00068807 | -0.021518 | -0.0024804 | -0.0022903 | 0.059114 | 0.039833 | 0.049824 | -0.053893 | -0.003172 | -0.040457 | 0.029236 | 0.023254 | 0.10992 | -0.099689 | 0.06515 | 0.38955 | -0.070087 | 121.7031 | 121.9694 | 121.8993 | -0.15957 | 0.028485 | -122.0014 | 0.074281 | 0.087717 | 0.059232 | -122.0074 | -121.9207 | -0.031396 | -0.32756 | 0.19332 | 0.058087 | 0.089483 | -0.061277 | -0.13133 | 0.15741 | 0.15143 | 0.23809 | 0.125 | -122.1303 | 121.8312 | 122.0975 | 122.0275 | 0.51772 | -122.1902
2111.8281 | 122.2412 | -0.082397 | 121.9849 | -0.01778 | -0.040495 | 0.038584 | 0.025452 | -0.011865 | 0.00090167 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.040047 | 0.050038 | -0.049315 | -0.007751 | -0.035879 | 0.029236 | 0.027833 | 0.11449 | -0.09511 | 0.051413 | 0.38955 | -0.070087 | 121.7077 | 121.9831 | 121.8993 | -0.15957 | -0.012713 | -121.9556 | 0.033082 | 0.046518 | 0.059231 | -121.957 | -121.8704 | -0.077173 | -0.27721 | 0.13381 | 0.01231 | 0.089483 | -0.001764 | -0.085556 | 0.11163 | 0.11023 | 0.19689 | 0.074646 | -122.08 | 121.7901 | 122.0655 | 121.9817 | 0.47195 | -122.1444
2113.5781 | 122.2366 | -0.091553 | 121.9894 | -0.0025182 | -0.040923 | 0.038798 | 0.025452 | -0.011437 | 0.0011153 | -0.029148 | -0.002053 | -0.0020767 | 0.059114 | 0.040047 | 0.049397 | -0.049315 | -0.012329 | -0.045036 | 0.020079 | 0.027833 | 0.10992 | -0.099689 | 0.051413 | 0.38497 | -0.065509 | 121.7122 | 121.9739 | 121.8947 | -0.15957 | -0.008136 | -121.9694 | 0.042238 | 0.046517 | 0.054653 | -121.9616 | -121.8795 | -0.068017 | -0.27721 | 0.14297 | 0.026044 | 0.094061 | -0.015499 | -0.094713 | 0.11163 | 0.11939 | 0.20147 | 0.079224 | -122.0891 | 121.8038 | 122.0655 | 121.9863 | 0.47652 | -122.149
2115.3438 | 122.1176 | -0.13733 | 121.9986 | -0.010149 | -0.040495 | 0.038584 | 0.025238 | -0.012078 | 0.00068807 | -0.029148 | -0.0022666 | -0.0018631 | 0.058901 | 0.039833 | 0.049397 | -0.049315 | -0.012329 | -0.045036 | 0.020079 | 0.027833 | 0.10992 | -0.10427 | 0.055992 | 0.38955 | -0.06093 | 121.7168 | 121.9785 | 121.9085 | -0.15957 | 0.033061 | -121.9785 | 0.088014 | 0.092293 | 0.059232 | -121.9708 | -121.8887 | -0.022241 | -0.28178 | 0.19332 | 0.076399 | 0.09864 | -0.020076 | -0.090132 | 0.15741 | 0.16516 | 0.24724 | 0.125 | -122.1029 | 121.8541 | 122.1158 | 122.0458 | 0.52688 | -122.1582
2117.1094 | 122.1268 | -0.1236 | 122.049 | -0.0025182 | -0.040709 | 0.038798 | 0.025879 | -0.011865 | 0.0011153 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.039833 | 0.049183 | -0.053893 | -0.012329 | -0.035879 | 0.029236 | 0.027833 | 0.11449 | -0.090531 | 0.060571 | 0.38497 | -0.065509 | 121.7077 | 121.9831 | 121.9039 | -0.16415 | 0.033065 | -122.0197 | 0.069703 | 0.087717 | 0.054652 | -122.0211 | -121.9345 | -0.040553 | -0.3413 | 0.18417 | 0.058087 | 0.09864 | -0.065851 | -0.14507 | 0.15283 | 0.15143 | 0.23809 | 0.11127 | -122.1395 | 121.8312 | 122.1067 | 122.0275 | 0.50857 | -122.2131
2118.7969 | 122.1817 | -0.12817 | 122.0123 | -0.0025182 | -0.040709 | 0.039011 | 0.025452 | -0.011651 | 0.0011153 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.040047 | 0.049183 | -0.053893 | -0.012329 | -0.040457 | 0.024657 | 0.027833 | 0.10534 | -0.090531 | 0.060571 | 0.38039 | -0.065509 | 121.7214 | 121.9785 | 121.9085 | -0.15957 | 0.037643 | -121.9877 | 0.074281 | 0.087717 | 0.050074 | -121.9845 | -121.907 | -0.031396 | -0.29094 | 0.18874 | 0.062665 | 0.094061 | -0.033809 | -0.10386 | 0.15283 | 0.15601 | 0.23351 | 0.11585 | -122.1029 | 121.8496 | 122.1067 | 122.0366 | 0.50857 | -122.1719
2120.5469 | 122.2595 | -0.086975 | 121.9711 | -0.0025182 | -0.040495 | 0.038798 | 0.025452 | -0.011651 | 0.00090167 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.039619 | 0.04961 | -0.049315 | -0.012329 | -0.040457 | 0.024657 | 0.027833 | 0.11449 | -0.09511 | 0.055992 | 0.39413 | -0.065509 | 121.7168 | 121.9785 | 121.9039 | -0.16415 | -0.008135 | -121.9465 | 0.03766 | 0.046518 | 0.054653 | -121.9433 | -121.8566 | -0.077174 | -0.25432 | 0.14297 | 0.021466 | 0.09864 | 0.00739 | -0.067245 | 0.11163 | 0.11481 | 0.20147 | 0.074646 | -122.0662 | 121.8038 | 122.0655 | 121.9909 | 0.4811 | -122.1353
2122.3125 | 122.1451 | -0.11902 | 122.0398 | -0.010149 | -0.041136 | 0.03837 | 0.025452 | -0.011865 | 0.0011153 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.040047 | 0.049397 | -0.03558 | -0.016908 | -0.045036 | 0.029236 | 0.032411 | 0.11449 | -0.099689 | 0.055992 | 0.38039 | -0.056351 | 121.7122 | 121.9831 | 121.9085 | -0.16415 | 0.01933 | -122.0106 | 0.083439 | 0.073983 | 0.054653 | -122.0074 | -121.9253 | -0.04513 | -0.32756 | 0.17501 | 0.062668 | 0.1078 | -0.056696 | -0.13133 | 0.14825 | 0.15143 | 0.23351 | 0.10211 | -122.1395 | 121.8313 | 122.1021 | 122.0275 | 0.49941 | -122.2039
2124 | 122.2183 | -0.10986 | 121.994 | 0.0051128 | -0.040709 | 0.038584 | 0.025238 | -0.011437 | 0.0011153 | -0.0062567 | -0.002053 | -0.0020767 | 0.059114 | 0.039619 | 0.049397 | -0.044736 | -0.016908 | -0.054192 | 0.024657 | 0.023254 | 0.11907 | -0.09511 | 0.055992 | 0.38955 | -0.06093 | 121.7168 | 121.9785 | 121.9085 | -0.16415 | 0.014753 | -121.9694 | 0.065127 | 0.055671 | 0.040918 | -121.9708 | -121.8749 | -0.054286 | -0.27721 | 0.16586 | 0.048933 | 0.10322 | -0.015499 | -0.085555 | 0.13452 | 0.13312 | 0.22894 | 0.092955 | -122.0891 | 121.8267 | 122.0884 | 122.0183 | 0.49941 | -122.1582
2125.75 | 122.2366 | -0.07782 | 122.0078 | -0.01778 | -0.040923 | 0.038584 | 0.025024 | -0.011865 | 0.0011153 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.040047 | 0.049397 | -0.049315 | -0.016908 | -0.045036 | 0.033814 | 0.023254 | 0.10992 | -0.09511 | 0.055992 | 0.38955 | -0.065509 | 121.7168 | 121.9831 | 121.9176 | -0.16415 | -0.01729 | -121.9739 | 0.028505 | 0.032784 | 0.050074 | -121.9845 | -121.8978 | -0.086329 | -0.29094 | 0.13381 | 0.012311 | 0.09864 | -0.024652 | -0.09013 | 0.11163 | 0.10107 | 0.18774 | 0.060912 | -122.1029 | 121.7946 | 122.0609 | 121.9954 | 0.46737 | -122.1719
2127.5 | 122.168 | -0.14191 | 122.0398 | -0.010149 | -0.040709 | 0.038798 | 0.025452 | -0.011437 | 0.0011153 | -0.013887 | -0.0016258 | -0.0022903 | 0.058901 | 0.039833 | 0.049183 | -0.044736 | -0.007751 | -0.040457 | 0.020079 | 0.027833 | 0.10992 | -0.099689 | 0.055992 | 0.38497 | -0.056351 | 121.7168 | 121.9831 | 121.913 | -0.15957 | 0.042218 | -122.0197 | 0.097171 | 0.10145 | 0.059232 | -122.012 | -121.9299 | -0.017663 | -0.32298 | 0.1979 | 0.085556 | 0.10322 | -0.056696 | -0.12675 | 0.16199 | 0.16974 | 0.25182 | 0.13416 | -122.1395 | 121.8587 | 122.125 | 122.055 | 0.52688 | -122.1994
2129.25 | 122.2458 | -0.091553 | 122.0444 | -0.010149 | -0.040709 | 0.038584 | 0.025452 | -0.011437 | 0.00090167 | -0.021518 | -0.0018394 | -0.0020767 | 0.058901 | 0.040047 | 0.049397 | -0.044736 | -0.016908 | -0.040457 | 0.029236 | 0.03699 | 0.10992 | -0.099689 | 0.051413 | 0.38039 | -0.06093 | 121.7214 | 121.9831 | 121.913 | -0.16415 | -0.008136 | -122.0151 | 0.046817 | 0.051096 | 0.059232 | -122.0074 | -121.9345 | -0.072596 | -0.32298 | 0.14297 | 0.030623 | 0.10322 | -0.061274 | -0.13133 | 0.12079 | 0.12854 | 0.20147 | 0.074645 | -122.1441 | 121.8129 | 122.0747 | 122.0046 | 0.47195 | -122.2085
2130.9531 | 122.1451 | -0.13275 | 122.0398 | -0.01778 | -0.040709 | 0.03837 | 0.025452 | -0.011651 | 0.0011153 | -0.021518 | -0.0018394 | -0.0022903 | 0.059114 | 0.040047 | 0.04961 | -0.044736 | -0.012329 | -0.035879 | 0.024657 | 0.027833 | 0.10992 | -0.099689 | 0.051413 | 0.38497 | -0.06093 | 121.7214 | 121.9923 | 121.913 | -0.15499 | 0.033062 | -122.0151 | 0.088015 | 0.096872 | 0.06381 | -122.012 | -121.9299 | -0.02224 | -0.3184 | 0.18416 | 0.071821 | 0.094061 | -0.047539 | -0.12675 | 0.15741 | 0.16058 | 0.24267 | 0.12042 | -122.1395 | 121.8541 | 122.125 | 122.0458 | 0.51772 | -122.1948
2132.7031 | 122.1222 | -0.13733 | 122.0444 | -0.010149 | -0.041136 | 0.038584 | 0.025452 | -0.011437 | 0.0011153 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.040047 | 0.049397 | -0.044736 | -0.016908 | -0.045036 | 0.024657 | 0.032411 | 0.10992 | -0.09511 | 0.060571 | 0.38955 | -0.056351 | 121.726 | 121.9877 | 121.9222 | -0.15041 | 0.042219 | -122.0197 | 0.092593 | 0.092293 | 0.050074 | -122.012 | -121.9345 | -0.013083 | -0.3184 | 0.1979 | 0.080978 | 0.094061 | -0.056695 | -0.12217 | 0.16199 | 0.16974 | 0.24724 | 0.12042 | -122.1395 | 121.8633 | 122.125 | 122.0595 | 0.52688 | -122.1948
2134.4531 | 122.2824 | -0.086975 | 122.0123 | 0.0051128 | -0.040709 | 0.038798 | 0.025452 | -0.011437 | 0.00068807 | -0.029148 | -0.002053 | -0.0025041 | 0.058901 | 0.040047 | 0.049397 | -0.049315 | -0.012329 | -0.035879 | 0.020079 | 0.027833 | 0.11449 | -0.09511 | 0.055992 | 0.38955 | -0.065509 | 121.726 | 121.9831 | 121.9222 | -0.15957 | -0.008135 | -121.9922 | 0.03766 | 0.051096 | 0.059231 | -121.9845 | -121.8978 | -0.072595 | -0.28636 | 0.14297 | 0.021466 | 0.094061 | -0.02923 | -0.090129 | 0.10705 | 0.11481 | 0.20147 | 0.074646 | -122.1074 | 121.8129 | 122.0701 | 122.0092 | 0.47652 | -122.1719
2136.2188 | 122.1451 | -0.1236 | 122.0261 | 0.0051128 | -0.040709 | 0.038584 | 0.025238 | -0.011651 | 0.0011153 | -0.013887 | -0.0018394 | -0.0016495 | 0.059114 | 0.039833 | 0.049397 | -0.044736 | -0.016908 | -0.040457 | 0.024657 | 0.032411 | 0.11449 | -0.090531 | 0.055992 | 0.38955 | -0.056351 | 121.726 | 121.9923 | 121.9222 | -0.15499 | 0.033065 | -122.0014 | 0.07886 | 0.083139 | 0.050074 | -121.9937 | -121.9116 | -0.031395 | -0.30009 | 0.17959 | 0.067245 | 0.09864 | -0.033806 | -0.10386 | 0.14825 | 0.15601 | 0.23809 | 0.10669 | -122.1166 | 121.8496 | 122.1159 | 122.0458 | 0.51314 | -122.1811
2137.9062 | 122.2733 | -0.091553 | 121.994 | -0.01778 | -0.040923 | 0.039011 | 0.025666 | -0.011651 | 0.0011153 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.039833 | 0.049824 | -0.049315 | -0.016908 | -0.040457 | 0.029236 | 0.023254 | 0.11907 | -0.099689 | 0.051413 | 0.38955 | -0.056351 | 121.726 | 121.9968 | 121.9176 | -0.15499 | -0.008136 | -121.9648 | 0.042238 | 0.051096 | 0.059232 | -121.9708 | -121.8749 | -0.063438 | -0.26805 | 0.14297 | 0.035202 | 0.09864 | 0.002816 | -0.076398 | 0.12079 | 0.11481 | 0.21063 | 0.074645 | -122.0937 | 121.8175 | 122.0884 | 122.0092 | 0.4811 | -122.149
2139.6406 | 122.2412 | -0.10071 | 122.0123 | -0.01778 | -0.041136 | 0.038798 | 0.025452 | -0.011651 | 0.00090167 | 0.0013733 | -0.002053 | -0.0025041 | 0.058901 | 0.040047 | 0.049397 | -0.040158 | -0.012329 | -0.031301 | 0.024657 | 0.032411 | 0.10992 | -0.085952 | 0.060571 | 0.38955 | -0.065509 | 121.7305 | 121.9877 | 121.9222 | -0.15041 | 0.014756 | -121.9877 | 0.06055 | 0.069407 | 0.054651 | -121.9799 | -121.9024 | -0.049704 | -0.28178 | 0.16128 | 0.035199 | 0.084903 | -0.024651 | -0.090129 | 0.12537 | 0.13312 | 0.21062 | 0.088379 | -122.0983 | 121.8313 | 122.0884 | 122.0229 | 0.49026 | -122.1627
2141.3906 | 122.1222 | -0.14191 | 122.0398 | -0.010149 | -0.04135 | 0.038798 | 0.025666 | -0.011651 | 0.0013291 | -0.029148 | -0.002053 | -0.0022903 | 0.058687 | 0.039833 | 0.04961 | -0.040158 | -0.007751 | -0.035879 | 0.029236 | 0.027833 | 0.11449 | -0.081373 | 0.060571 | 0.38039 | -0.06093 | 121.7351 | 121.9923 | 121.9268 | -0.15957 | 0.060534 | -122.0106 | 0.10175 | 0.10603 | 0.045494 | -122.012 | -121.9253 | -0.017663 | -0.30467 | 0.20248 | 0.080977 | 0.09864 | -0.047539 | -0.11302 | 0.17114 | 0.16974 | 0.2564 | 0.13416 | -122.1212 | 121.877 | 122.1342 | 122.0687 | 0.5223 | -122.1994
2143.1562 | 122.2549 | -0.086975 | 122.0169 | -0.010149 | -0.04135 | 0.038798 | 0.025238 | -0.011865 | 0.00090167 | -0.013887 | -0.002053 | -0.0025041 | 0.059328 | 0.039833 | 0.04961 | -0.044736 | -0.012329 | -0.031301 | 0.033814 | 0.027833 | 0.10992 | -0.090531 | 0.055992 | 0.38497 | -0.051772 | 121.7214 | 122.0014 | 121.9359 | -0.15041 | -0.003556 | -121.9831 | 0.042239 | 0.055674 | 0.05923 | -121.9891 | -121.907 | -0.063437 | -0.29552 | 0.14297 | 0.035203 | 0.09864 | -0.015494 | -0.080971 | 0.12079 | 0.11481 | 0.19689 | 0.074646 | -122.1074 | 121.8084 | 122.0884 | 122.0229 | 0.47195 | -122.1673
2144.8438 | 122.2778 | -0.07782 | 122.0215 | -0.010149 | -0.041136 | 0.038798 | 0.025666 | -0.011437 | 0.00090167 | -0.0062567 | -0.002053 | -0.0027177 | 0.059114 | 0.040047 | 0.049397 | -0.044736 | -0.007751 | -0.035879 | 0.033814 | 0.032411 | 0.11907 | -0.090531 | 0.06515 | 0.39413 | -0.065509 | 121.7305 | 121.9968 | 121.9314 | -0.16415 | -0.012711 | -121.9877 | 0.033084 | 0.041941 | 0.054652 | -121.9891 | -121.9024 | -0.086329 | -0.29094 | 0.14297 | 0.012311 | 0.09864 | -0.024649 | -0.090127 | 0.11163 | 0.11023 | 0.19689 | 0.070069 | -122.112 | 121.8084 | 122.0747 | 122.0092 | 0.47195 | -122.1856
2146.6094 | 122.168 | -0.11902 | 122.0444 | -0.0025182 | -0.040923 | 0.03837 | 0.025452 | -0.011651 | 0.00090167 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.039833 | 0.048969 | -0.03558 | -0.012329 | -0.040457 | 0.024657 | 0.032411 | 0.11449 | -0.099689 | 0.060571 | 0.38955 | -0.06093 | 121.7305 | 122.0014 | 121.9268 | -0.15499 | 0.01933 | -122.0197 | 0.083439 | 0.078562 | 0.059232 | -122.012 | -121.9299 | -0.035972 | -0.31383 | 0.17959 | 0.058089 | 0.094061 | -0.04296 | -0.11759 | 0.14368 | 0.15143 | 0.23351 | 0.10669 | -122.1441 | 121.8496 | 122.1204 | 122.0458 | 0.50857 | -122.1994
2148.375 | 122.2137 | -0.086975 | 122.0398 | -0.010149 | -0.040709 | 0.039011 | 0.025024 | -0.011437 | 0.00068807 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.039833 | 0.049397 | -0.040158 | -0.012329 | -0.040457 | 0.033814 | 0.032411 | 0.11449 | -0.09511 | 0.060571 | 0.38955 | -0.065509 | 121.7397 | 121.9968 | 121.9268 | -0.15957 | -0.008135 | -122.006 | 0.046817 | 0.046518 | 0.054653 | -122.0074 | -121.9253 | -0.072595 | -0.30009 | 0.14755 | 0.021466 | 0.094061 | -0.04296 | -0.11302 | 0.12079 | 0.11939 | 0.20147 | 0.074646 | -122.1349 | 121.8267 | 122.0838 | 122.0138 | 0.47652 | -122.1994
2150.0625 | 122.2321 | -0.082397 | 121.9803 | -0.0025182 | -0.040923 | 0.039011 | 0.025666 | -0.012078 | 0.00090167 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.04026 | 0.049397 | -0.044736 | -0.007751 | -0.040457 | 0.038393 | 0.032411 | 0.11449 | -0.09511 | 0.051413 | 0.38497 | -0.06093 | 121.7351 | 122.0014 | 121.9268 | -0.15957 | -0.012713 | -121.9419 | 0.037661 | 0.04194 | 0.054653 | -121.9479 | -121.8658 | -0.077173 | -0.24516 | 0.13381 | 0.021467 | 0.09864 | 0.021127 | -0.053507 | 0.12079 | 0.11481 | 0.19689 | 0.074646 | -122.0754 | 121.8175 | 122.0838 | 122.0092 | 0.46737 | -122.1399
2151.8125 | 122.2046 | -0.10529 | 122.0261 | -0.0025182 | -0.040923 | 0.038584 | 0.025452 | -0.011651 | 0.00090167 | -0.021518 | -0.0016258 | -0.0020767 | 0.058687 | 0.040047 | 0.049397 | -0.040158 | -0.007751 | -0.035879 | 0.029236 | 0.03699 | 0.11449 | -0.09511 | 0.060571 | 0.39413 | -0.056351 | 121.7397 | 122.006 | 121.9359 | -0.15499 | 0.010176 | -121.9968 | 0.065128 | 0.069407 | 0.059231 | -121.9891 | -121.9116 | -0.049705 | -0.28636 | 0.16586 | 0.048935 | 0.09864 | -0.02007 | -0.090126 | 0.13452 | 0.14228 | 0.21978 | 0.097535 | -122.1212 | 121.845 | 122.1113 | 122.0412 | 0.49941 | -122.1811
2153.5938 | 122.2229 | -0.10071 | 122.0306 | -0.0025182 | -0.040923 | 0.038798 | 0.025238 | -0.011437 | 0.00090167 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.040047 | 0.049183 | -0.040158 | -0.012329 | -0.040457 | 0.029236 | 0.03699 | 0.11449 | -0.09511 | 0.06515 | 0.38497 | -0.06093 | 121.7443 | 122.006 | 121.9314 | -0.15499 | 0.005598 | -122.0014 | 0.06055 | 0.060251 | 0.054653 | -121.9937 | -121.9161 | -0.054283 | -0.28636 | 0.16586 | 0.039778 | 0.094061 | -0.024648 | -0.099283 | 0.12994 | 0.1377 | 0.2152 | 0.088379 | -122.1258 | 121.845 | 122.1067 | 122.0321 | 0.48568 | -122.1856
2155.2656 | 122.2321 | -0.09613 | 122.0078 | -0.01778 | -0.040923 | 0.038798 | 0.025238 | -0.011651 | 0.0011153 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.039833 | 0.049183 | -0.03558 | -0.003172 | -0.031301 | 0.033814 | 0.032411 | 0.11907 | -0.085952 | 0.06515 | 0.38497 | -0.051772 | 121.7443 | 122.0106 | 121.9359 | -0.15499 | 0.010178 | -121.9739 | 0.06055 | 0.064829 | 0.054651 | -121.9753 | -121.8887 | -0.058861 | -0.26347 | 0.16128 | 0.044358 | 0.10322 | 0.00282 | -0.071815 | 0.12994 | 0.12854 | 0.2152 | 0.092958 | -122.0937 | 121.8404 | 122.1067 | 122.0321 | 0.4811 | -122.1627
2157.0156 | 122.1771 | -0.10986 | 122.0261 | -0.010149 | -0.040923 | 0.038798 | 0.025452 | -0.011865 | 0.00090167 | -0.021518 | -0.002053 | -0.0020767 | 0.058687 | 0.04026 | 0.04961 | -0.031001 | -0.007751 | -0.026723 | 0.033814 | 0.03699 | 0.11449 | -0.09511 | 0.055992 | 0.38497 | -0.056351 | 121.7443 | 122.0106 | 121.9359 | -0.15957 | 0.014753 | -121.9922 | 0.078862 | 0.08314 | 0.068387 | -121.9891 | -121.9116 | -0.049707 | -0.28178 | 0.16586 | 0.053512 | 0.10322 | -0.015491 | -0.090126 | 0.14368 | 0.14685 | 0.22436 | 0.10211 | -122.1212 | 121.8541 | 122.1204 | 122.0458 | 0.49483 | -122.1856
2158.7188 | 122.1542 | -0.14191 | 122.0718 | -0.01778 | -0.04135 | 0.038798 | 0.025452 | -0.011651 | 0.00047427 | -0.013887 | -0.0018394 | -0.0025041 | 0.059328 | 0.040047 | 0.049397 | -0.03558 | -0.007751 | -0.031301 | 0.033814 | 0.032411 | 0.12365 | -0.085952 | 0.06515 | 0.39413 | -0.06093 | 121.7443 | 122.0014 | 121.9359 | -0.15957 | 0.055955 | -122.038 | 0.10633 | 0.11061 | 0.054651 | -122.0394 | -121.9482 | -0.017663 | -0.32756 | 0.20706 | 0.080977 | 0.09864 | -0.070425 | -0.1359 | 0.17572 | 0.17432 | 0.26556 | 0.13416 | -122.1578 | 121.8862 | 122.1433 | 122.0778 | 0.53604 | -122.2314
2160.4688 | 122.2321 | -0.082397 | 122.0352 | -0.01778 | -0.041136 | 0.038798 | 0.025238 | -0.011437 | 0.00068807 | -0.021518 | -0.002053 | -0.0018631 | 0.058901 | 0.040047 | 0.049397 | -0.044736 | -0.007751 | -0.031301 | 0.029236 | 0.03699 | 0.12365 | -0.090531 | 0.060571 | 0.38955 | -0.06093 | 121.7489 | 122.006 | 121.9451 | -0.15499 | -0.008134 | -122.006 | 0.037661 | 0.051096 | 0.05923 | -121.9982 | -121.9116 | -0.072594 | -0.28636 | 0.14297 | 0.021467 | 0.094061 | -0.029225 | -0.090124 | 0.11163 | 0.11939 | 0.20605 | 0.074646 | -122.1257 | 121.8313 | 122.0884 | 122.0275 | 0.47195 | -122.1902
2162.2344 | 122.2458 | -0.091553 | 122.0306 | -0.010149 | -0.041136 | 0.039225 | 0.025238 | -0.011865 | 0.00047427 | -0.013887 | -0.0016258 | -0.0022903 | 0.058901 | 0.04026 | 0.049397 | -0.03558 | -0.007751 | -0.031301 | 0.033814 | 0.03699 | 0.12365 | -0.085952 | 0.055992 | 0.38955 | -0.065509 | 121.7489 | 122.006 | 121.9359 | -0.15499 | 0.005601 | -121.9968 | 0.055973 | 0.060252 | 0.054651 | -121.9937 | -121.907 | -0.063438 | -0.28178 | 0.14754 | 0.026044 | 0.089482 | -0.024648 | -0.094704 | 0.12537 | 0.12854 | 0.2152 | 0.083802 | -122.1166 | 121.8404 | 122.0975 | 122.0275 | 0.4811 | -122.1856
2164 | 122.2824 | -0.07782 | 122.0398 | -0.025411 | -0.041564 | 0.038798 | 0.025238 | -0.011437 | 0.00047427 | -0.0062567 | -0.0018394 | -0.0022903 | 0.058901 | 0.039833 | 0.04961 | -0.040158 | -0.012329 | -0.035879 | 0.033814 | 0.027833 | 0.12365 | -0.090531 | 0.055992 | 0.38497 | -0.056351 | 121.7443 | 122.0106 | 121.9405 | -0.15499 | -0.012711 | -122.006 | 0.037662 | 0.041941 | 0.054652 | -122.012 | -121.9161 | -0.077171 | -0.29551 | 0.13381 | 0.021469 | 0.09864 | -0.029224 | -0.099281 | 0.11163 | 0.10565 | 0.20147 | 0.065491 | -122.1303 | 121.8221 | 122.0884 | 122.0183 | 0.46279 | -122.1948
2165.7031 | 122.2641 | -0.091553 | 122.0032 | -0.010149 | -0.041136 | 0.039011 | 0.025238 | -0.011437 | 0.00047427 | -0.029148 | -0.002053 | -0.0022903 | 0.058901 | 0.04026 | 0.04961 | -0.031001 | -0.007751 | -0.045036 | 0.033814 | 0.041569 | 0.12365 | -0.090531 | 0.060571 | 0.38955 | -0.056351 | 121.7534 | 122.006 | 121.9405 | -0.15957 | 0.001022 | -121.9694 | 0.060552 | 0.046517 | 0.045495 | -121.9616 | -121.8795 | -0.068017 | -0.24974 | 0.15212 | 0.035202 | 0.10322 | 0.002818 | -0.06266 | 0.12537 | 0.13312 | 0.2152 | 0.083802 | -122.0937 | 121.845 | 122.0975 | 122.0321 | 0.4811 | -122.1627
2167.4531 | 122.2916 | -0.068665 | 122.0078 | -0.01778 | -0.041136 | 0.038798 | 0.025238 | -0.011865 | 0.00068807 | -0.021518 | -0.002053 | -0.0027177 | 0.058687 | 0.039833 | 0.04961 | -0.040158 | -0.007751 | -0.035879 | 0.029236 | 0.041569 | 0.12365 | -0.090531 | 0.069728 | 0.39413 | -0.06093 | 121.7534 | 122.0151 | 121.9405 | -0.15041 | -0.021866 | -121.9785 | 0.028507 | 0.032786 | 0.054652 | -121.9662 | -121.8841 | -0.081747 | -0.25431 | 0.13839 | 0.007735 | 0.089482 | 0.007398 | -0.067237 | 0.097901 | 0.11023 | 0.19232 | 0.060914 | -122.0983 | 121.8221 | 122.0838 | 122.0092 | 0.46279 | -122.1582
2169.1406 | 122.1588 | -0.12817 | 122.0627 | -0.010149 | -0.041136 | 0.038584 | 0.025238 | -0.011437 | 0.00090167 | -0.013887 | -0.0022666 | -0.0018631 | 0.059114 | 0.04026 | 0.049397 | -0.03558 | -0.003172 | -0.031301 | 0.033814 | 0.03699 | 0.12365 | -0.090531 | 0.060571 | 0.38955 | -0.056351 | 121.7534 | 122.0197 | 121.9451 | -0.15041 | 0.037643 | -122.0289 | 0.092594 | 0.096873 | 0.05923 | -122.0257 | -121.939 | -0.022238 | -0.30924 | 0.18874 | 0.071823 | 0.094061 | -0.042955 | -0.11759 | 0.16199 | 0.16516 | 0.25183 | 0.125 | -122.1532 | 121.8816 | 122.1479 | 122.0733 | 0.51772 | -122.2131
2170.9062 | 122.2092 | -0.10529 | 122.081 | 0.0051128 | -0.041564 | 0.038798 | 0.025452 | -0.011651 | 0.00068807 | -0.013887 | -0.0018394 | -0.0020767 | 0.059114 | 0.039833 | 0.050038 | -0.040158 | -0.003172 | -0.035879 | 0.029236 | 0.041569 | 0.12365 | -0.085952 | 0.06515 | 0.39413 | -0.056351 | 121.7534 | 122.0106 | 121.9497 | -0.15041 | 0.019334 | -122.0518 | 0.065128 | 0.069407 | 0.050073 | -122.0394 | -121.9573 | -0.045126 | -0.32756 | 0.17044 | 0.048935 | 0.094061 | -0.070423 | -0.13132 | 0.13452 | 0.14686 | 0.22894 | 0.10211 | -122.1669 | 121.8587 | 122.1159 | 122.055 | 0.49941 | -122.2314
2172.6719 | 122.1405 | -0.1236 | 122.0764 | -0.033042 | -0.04135 | 0.039011 | 0.025452 | -0.011651 | 0.00090167 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.04026 | 0.04961 | -0.03558 | 0.005985 | -0.031301 | 0.033814 | 0.03699 | 0.12823 | -0.09511 | 0.060571 | 0.39413 | -0.056351 | 121.7626 | 122.0151 | 121.9497 | -0.15041 | 0.028486 | -122.0426 | 0.088016 | 0.092295 | 0.063809 | -122.0394 | -121.9482 | -0.026816 | -0.31382 | 0.18417 | 0.067245 | 0.094061 | -0.061267 | -0.12674 | 0.15741 | 0.16059 | 0.25183 | 0.12958 | -122.1715 | 121.8862 | 122.1387 | 122.0733 | 0.51772 | -122.2268
2174.3594 | 122.2092 | -0.091553 | 122.0581 | -0.010149 | -0.041564 | 0.039011 | 0.025024 | -0.011651 | 0.00047427 | -0.013887 | -0.002053 | -0.0027177 | 0.058901 | 0.040474 | 0.049397 | -0.03558 | -0.007751 | -0.035879 | 0.029236 | 0.03699 | 0.12365 | -0.085952 | 0.060571 | 0.39413 | -0.051772 | 121.758 | 122.0151 | 121.9634 | -0.15041 | 0.005601 | -122.0289 | 0.055973 | 0.055674 | 0.050073 | -122.0211 | -121.9345 | -0.058859 | -0.30009 | 0.15212 | 0.039781 | 0.09864 | -0.042956 | -0.094698 | 0.12079 | 0.12854 | 0.2152 | 0.083802 | -122.1441 | 121.8496 | 122.1067 | 122.055 | 0.48568 | -122.2085
2176.125 | 122.2778 | -0.064087 | 122.0261 | -0.0025182 | -0.04135 | 0.039225 | 0.024597 | -0.011865 | 0.00068807 | -0.021518 | -0.0018394 | -0.0022903 | 0.059114 | 0.04026 | 0.049397 | -0.044736 | 0.001407 | -0.035879 | 0.033814 | 0.041569 | 0.12365 | -0.081373 | 0.060571 | 0.40329 | -0.056351 | 121.7626 | 122.0151 | 121.9543 | -0.15041 | -0.017286 | -121.9922 | 0.019351 | 0.028208 | 0.045494 | -121.9845 | -121.9024 | -0.086325 | -0.26347 | 0.12466 | 0.007736 | 0.094061 | -0.010913 | -0.071812 | 0.097901 | 0.10566 | 0.18774 | 0.065494 | -122.1074 | 121.8267 | 122.0792 | 122.0183 | 0.46737 | -122.1765
2177.8906 | 122.168 | -0.12817 | 122.0581 | -0.010149 | -0.041777 | 0.039011 | 0.025238 | -0.011437 | 0.00068807 | -0.013887 | -0.0016258 | -0.0022903 | 0.058687 | 0.04026 | 0.048969 | -0.031001 | -0.003172 | -0.040457 | 0.033814 | 0.032411 | 0.11907 | -0.09511 | 0.060571 | 0.38955 | -0.056351 | 121.758 | 122.0243 | 121.9588 | -0.15041 | 0.033064 | -122.0243 | 0.097173 | 0.087717 | 0.054653 | -122.0257 | -121.939 | -0.022238 | -0.30009 | 0.18874 | 0.071823 | 0.094061 | -0.033799 | -0.099276 | 0.16199 | 0.16059 | 0.24725 | 0.125 | -122.1532 | 121.8862 | 122.1525 | 122.087 | 0.51772 | -122.2085
2179.6406 | 122.2458 | -0.09613 | 122.0352 | -0.01778 | -0.041564 | 0.039011 | 0.025024 | -0.011651 | 0.00068807 | -0.0062567 | -0.002053 | -0.0022903 | 0.058901 | 0.040047 | 0.04961 | -0.040158 | 0.001407 | -0.040457 | 0.033814 | 0.03699 | 0.12823 | -0.085952 | 0.060571 | 0.38955 | -0.051772 | 121.7626 | 122.0289 | 121.9543 | -0.15041 | 0.010178 | -122.0014 | 0.055972 | 0.055673 | 0.045495 | -121.9982 | -121.907 | -0.054282 | -0.27262 | 0.1567 | 0.044358 | 0.09864 | -0.006332 | -0.080967 | 0.12994 | 0.13312 | 0.22436 | 0.097537 | -122.1212 | 121.8587 | 122.125 | 122.0504 | 0.48568 | -122.1856
2181.3281 | 122.2549 | -0.07782 | 122.0444 | -0.010149 | -0.041564 | 0.038798 | 0.025238 | -0.011224 | 0.00068807 | -0.013887 | -0.0016258 | -0.0020767 | 0.058901 | 0.040474 | 0.048969 | -0.03558 | 0.001407 | -0.035879 | 0.038393 | 0.03699 | 0.11907 | -0.085952 | 0.060571 | 0.39871 | -0.051772 | 121.7672 | 122.0289 | 121.9497 | -0.15499 | -0.008132 | -122.006 | 0.04224 | 0.041941 | 0.050073 | -122.0074 | -121.9253 | -0.077171 | -0.2772 | 0.13839 | 0.026048 | 0.10322 | -0.015488 | -0.094701 | 0.11621 | 0.11481 | 0.19689 | 0.079227 | -122.1303 | 121.845 | 122.1067 | 122.0275 | 0.47653 | -122.1994
2183.0938 | 122.2687 | -0.073242 | 122.0673 | -0.0025182 | -0.041777 | 0.039225 | 0.025238 | -0.011651 | 0.00026067 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.039833 | 0.049183 | -0.03558 | -0.007751 | -0.026723 | 0.033814 | 0.03699 | 0.12823 | -0.085952 | 0.06515 | 0.38955 | -0.056351 | 121.7626 | 122.0243 | 121.9543 | -0.15499 | -0.01271 | -122.0334 | 0.037662 | 0.046519 | 0.059229 | -122.0303 | -121.939 | -0.081749 | -0.30466 | 0.13839 | 0.016891 | 0.09864 | -0.042955 | -0.11301 | 0.10706 | 0.11023 | 0.20147 | 0.065491 | -122.1532 | 121.8358 | 122.0975 | 122.0275 | 0.46279 | -122.2223
2184.8438 | 122.3007 | -0.068665 | 122.0123 | -0.01778 | -0.04135 | 0.039439 | 0.025024 | -0.011865 | 0.00047427 | -0.021518 | -0.0016258 | -0.0025041 | 0.059114 | 0.040474 | 0.04961 | -0.040158 | -0.003172 | -0.031301 | 0.029236 | 0.03699 | 0.12823 | -0.085952 | 0.06515 | 0.39413 | -0.06093 | 121.758 | 122.0243 | 121.9543 | -0.15041 | -0.017287 | -121.9831 | 0.028507 | 0.037364 | 0.054651 | -121.9753 | -121.8841 | -0.081747 | -0.25431 | 0.13382 | 0.007735 | 0.089482 | 0.011977 | -0.058079 | 0.097901 | 0.10565 | 0.1969 | 0.065493 | -122.0983 | 121.8267 | 122.093 | 122.0229 | 0.46279 | -122.1627
2186.6094 | 122.2916 | -0.07782 | 122.0352 | -0.025411 | -0.041564 | 0.039439 | 0.024811 | -0.011651 | 0.0011153 | -0.029148 | -0.0022666 | -0.0027177 | 0.058473 | 0.04026 | 0.04961 | -0.040158 | -0.003172 | -0.031301 | 0.042971 | 0.041569 | 0.11907 | -0.085952 | 0.06515 | 0.39413 | -0.056351 | 121.7718 | 122.0289 | 121.9588 | -0.15041 | -0.008132 | -121.9922 | 0.037662 | 0.046519 | 0.054651 | -121.9936 | -121.9161 | -0.072592 | -0.26346 | 0.14297 | 0.021469 | 0.094061 | -0.006332 | -0.076388 | 0.12079 | 0.11939 | 0.19689 | 0.074648 | -122.1212 | 121.8496 | 122.1067 | 122.0366 | 0.47195 | -122.1856
2188.2969 | 122.1588 | -0.1236 | 122.0535 | -0.0025182 | -0.041777 | 0.039225 | 0.024597 | -0.011437 | 0.00047427 | -0.029148 | -0.002053 | -0.0025041 | 0.058901 | 0.040474 | 0.04961 | -0.03558 | -0.003172 | -0.026723 | 0.038393 | 0.041569 | 0.12823 | -0.090531 | 0.06515 | 0.39871 | -0.06093 | 121.7626 | 122.0289 | 121.9634 | -0.15041 | 0.033065 | -122.0151 | 0.088016 | 0.096873 | 0.063808 | -122.012 | -121.9253 | -0.026816 | -0.29093 | 0.18875 | 0.062666 | 0.089482 | -0.024643 | -0.090121 | 0.16199 | 0.16517 | 0.25183 | 0.12042 | -122.1441 | 121.8862 | 122.1525 | 122.087 | 0.5223 | -122.2039
2190.0469 | 122.168 | -0.13275 | 122.0947 | -0.01778 | -0.04135 | 0.039011 | 0.025024 | -0.011865 | 0.00090167 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.040047 | 0.049397 | -0.03558 | -0.003172 | -0.035879 | 0.033814 | 0.041569 | 0.12823 | -0.09511 | 0.06515 | 0.38955 | -0.056351 | 121.7718 | 122.0243 | 121.968 | -0.15499 | 0.037641 | -122.0609 | 0.097171 | 0.096872 | 0.059231 | -122.0532 | -121.9665 | -0.02224 | -0.32297 | 0.1979 | 0.0764 | 0.09864 | -0.070421 | -0.12674 | 0.16657 | 0.17432 | 0.26098 | 0.12958 | -122.1898 | 121.9045 | 122.1571 | 122.1007 | 0.5223 | -122.2497
2191.7344 | 122.1817 | -0.10986 | 122.081 | -0.010149 | -0.041564 | 0.039011 | 0.024597 | -0.012078 | 0.00026067 | -0.0062567 | -0.0022666 | -0.0022903 | 0.059114 | 0.04026 | 0.049397 | -0.040158 | 0.001407 | -0.031301 | 0.038393 | 0.03699 | 0.11907 | -0.081373 | 0.06515 | 0.39871 | -0.051772 | 121.7672 | 122.0335 | 121.9634 | -0.15041 | 0.02849 | -122.0426 | 0.069705 | 0.078562 | 0.050072 | -122.044 | -121.9619 | -0.040549 | -0.31382 | 0.17501 | 0.058091 | 0.09864 | -0.04753 | -0.11759 | 0.14826 | 0.14685 | 0.22894 | 0.11127 | -122.1624 | 121.877 | 122.1433 | 122.0733 | 0.50857 | -122.2314
2193.4844 | 122.2229 | -0.10071 | 122.081 | -0.01778 | -0.041564 | 0.039225 | 0.025024 | -0.011651 | 0.00068807 | -0.029148 | -0.0018394 | -0.0022903 | 0.058901 | 0.04026 | 0.048969 | -0.03558 | 0.001407 | -0.031301 | 0.038393 | 0.041569 | 0.12365 | -0.090531 | 0.06515 | 0.39871 | -0.051772 | 121.7718 | 122.0335 | 121.9543 | -0.15957 | 0.010177 | -122.0426 | 0.065128 | 0.069407 | 0.05923 | -122.0394 | -121.9573 | -0.058862 | -0.30924 | 0.16586 | 0.048936 | 0.1078 | -0.04753 | -0.12674 | 0.1391 | 0.14228 | 0.22436 | 0.10212 | -122.1715 | 121.8725 | 122.1342 | 122.055 | 0.49941 | -122.2406
2195.2344 | 122.1725 | -0.1236 | 122.0993 | -0.0025182 | -0.041777 | 0.039225 | 0.024597 | -0.011651 | 0.00026067 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.040474 | 0.049183 | -0.03558 | -0.003172 | -0.031301 | 0.033814 | 0.03699 | 0.12365 | -0.085952 | 0.06515 | 0.39413 | -0.06093 | 121.7763 | 122.038 | 121.968 | -0.14583 | 0.037644 | -122.0655 | 0.088016 | 0.092295 | 0.054651 | -122.0623 | -121.9757 | -0.022237 | -0.32297 | 0.18875 | 0.062666 | 0.084903 | -0.061262 | -0.13132 | 0.15741 | 0.16059 | 0.24725 | 0.12042 | -122.1853 | 121.8999 | 122.1616 | 122.0916 | 0.51772 | -122.2451
2197 | 122.3053 | -0.082397 | 122.0398 | -0.010149 | -0.041777 | 0.039011 | 0.025238 | -0.011865 | 0.00090167 | -0.0062567 | -0.002053 | -0.0022903 | 0.059114 | 0.040047 | 0.049397 | -0.031001 | -0.007751 | -0.035879 | 0.038393 | 0.041569 | 0.12823 | -0.085952 | 0.069728 | 0.39413 | -0.056351 | 121.7672 | 122.0335 | 121.9588 | -0.15041 | -0.003555 | -122.0014 | 0.051396 | 0.046518 | 0.050073 | -121.9982 | -121.9116 | -0.068015 | -0.27262 | 0.15213 | 0.026046 | 0.094061 | -0.006331 | -0.080966 | 0.12079 | 0.12397 | 0.21063 | 0.074646 | -122.1257 | 121.8496 | 122.1159 | 122.0412 | 0.47652 | -122.1902
2198.7031 | 122.2321 | -0.091553 | 122.0535 | -0.0025182 | -0.041777 | 0.039225 | 0.024597 | -0.011437 | 0.00047427 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.04026 | 0.049183 | -0.040158 | 0.001407 | -0.022144 | 0.042971 | 0.041569 | 0.12365 | -0.081373 | 0.060571 | 0.38955 | -0.051772 | 121.7763 | 122.0335 | 121.9771 | -0.15957 | 0.01018 | -122.0106 | 0.051395 | 0.069409 | 0.059229 | -122.012 | -121.9299 | -0.068017 | -0.2772 | 0.15212 | 0.039781 | 0.1078 | -0.020064 | -0.076385 | 0.13452 | 0.13312 | 0.2152 | 0.09296 | -122.1349 | 121.8679 | 122.125 | 122.0687 | 0.4811 | -122.2131
2200.4688 | 122.287 | -0.054932 | 122.0306 | -0.010149 | -0.041777 | 0.039439 | 0.024811 | -0.011651 | 0.00068807 | -0.021518 | -0.0022666 | -0.0020767 | 0.059328 | 0.040688 | 0.049397 | -0.026423 | -0.003172 | -0.026723 | 0.038393 | 0.03699 | 0.13281 | -0.085952 | 0.074307 | 0.39871 | -0.051772 | 121.7718 | 122.0335 | 121.9634 | -0.15499 | -0.03102 | -121.9922 | 0.028509 | 0.028209 | 0.059229 | -121.9937 | -121.8978 | -0.10006 | -0.25889 | 0.12924 | 0.00316 | 0.10322 | 0.002824 | -0.067233 | 0.093325 | 0.091922 | 0.18774 | 0.05176 | -122.1166 | 121.8267 | 122.0884 | 122.0183 | 0.45364 | -122.1856
2202.2188 | 122.3145 | -0.073242 | 122.0398 | -0.025411 | -0.041991 | 0.039439 | 0.024811 | -0.011651 | 0.00047427 | -0.029148 | -0.0022666 | -0.0022903 | 0.058687 | 0.04026 | 0.049183 | -0.03558 | 0.001407 | -0.035879 | 0.038393 | 0.03699 | 0.12823 | -0.076794 | 0.069728 | 0.39413 | -0.051772 | 121.7809 | 122.0335 | 121.968 | -0.15499 | -0.003552 | -122.0014 | 0.037662 | 0.037363 | 0.040915 | -122.0028 | -121.9116 | -0.081749 | -0.25888 | 0.14297 | 0.02147 | 0.10322 | -0.006331 | -0.071809 | 0.11163 | 0.11023 | 0.20147 | 0.074649 | -122.1166 | 121.8542 | 122.1067 | 122.0412 | 0.46737 | -122.1948
2203.9219 | 122.1909 | -0.13733 | 122.0673 | -0.0025182 | -0.041777 | 0.039225 | 0.024597 | -0.011865 | 0.00047427 | -0.013887 | -0.0018394 | -0.0022903 | 0.058687 | 0.04026 | 0.049397 | -0.031001 | 0.001407 | -0.022144 | 0.047549 | 0.041569 | 0.12365 | -0.085952 | 0.060571 | 0.39413 | -0.06093 | 121.7718 | 122.0426 | 121.9726 | -0.15041 | 0.051377 | -122.0197 | 0.10633 | 0.11519 | 0.063808 | -122.0257 | -121.9436 | -0.013083 | -0.29551 | 0.1979 | 0.076399 | 0.089482 | -0.02464 | -0.094696 | 0.18488 | 0.1789 | 0.26098 | 0.13874 | -122.1532 | 121.9091 | 122.1799 | 122.1099 | 0.53146 | -122.2177
2205.6719 | 122.1954 | -0.11902 | 122.0993 | -0.0025182 | -0.041991 | 0.039225 | 0.024811 | -0.011437 | 0.00026067 | -0.013887 | -0.002053 | -0.0020767 | 0.058901 | 0.040474 | 0.04961 | -0.03558 | -0.003172 | -0.026723 | 0.042971 | 0.041569 | 0.12365 | -0.081373 | 0.069728 | 0.39413 | -0.047194 | 121.7809 | 122.0472 | 121.968 | -0.14583 | 0.037646 | -122.0563 | 0.083439 | 0.092296 | 0.05465 | -122.0577 | -121.9757 | -0.026814 | -0.31839 | 0.18875 | 0.071825 | 0.098639 | -0.052105 | -0.13132 | 0.16199 | 0.16059 | 0.24267 | 0.11585 | -122.1807 | 121.8999 | 122.1662 | 122.087 | 0.51315 | -122.2451
2207.3594 | 122.287 | -0.07782 | 122.0535 | -0.0025182 | -0.041777 | 0.039652 | 0.024811 | -0.011437 | 0.00026067 | -0.013887 | -0.0016258 | -0.0022903 | 0.058901 | 0.04026 | 0.049397 | -0.031001 | 0.001407 | -0.026723 | 0.038393 | 0.041569 | 0.12365 | -0.081373 | 0.069728 | 0.40329 | -0.056351 | 121.7763 | 122.0472 | 121.9771 | -0.15041 | -0.003553 | -122.0151 | 0.046819 | 0.051097 | 0.05465 | -122.012 | -121.9299 | -0.072592 | -0.2772 | 0.14755 | 0.021469 | 0.094061 | -0.006329 | -0.076385 | 0.11621 | 0.11939 | 0.20147 | 0.079227 | -122.1349 | 121.8542 | 122.125 | 122.055 | 0.48111 | -122.2039
2209.1094 | 122.2275 | -0.11444 | 122.0718 | -0.010149 | -0.041777 | 0.039225 | 0.024597 | -0.011651 | 0.00047427 | -0.021518 | -0.0018394 | -0.0025041 | 0.059114 | 0.04026 | 0.049183 | -0.031001 | 0.001407 | -0.017566 | 0.042971 | 0.041569 | 0.12823 | -0.076794 | 0.06515 | 0.40786 | -0.047194 | 121.7809 | 122.0426 | 121.9771 | -0.15041 | 0.037647 | -122.0289 | 0.08344 | 0.096875 | 0.059228 | -122.0303 | -121.9436 | -0.035971 | -0.29093 | 0.17959 | 0.067247 | 0.10322 | -0.029217 | -0.094695 | 0.15741 | 0.15601 | 0.24267 | 0.11585 | -122.1486 | 121.8954 | 122.1571 | 122.0916 | 0.52231 | -122.2223
2210.7969 | 122.1725 | -0.10529 | 122.113 | -0.0025182 | -0.042205 | 0.039866 | 0.024811 | -0.011865 | 0.00090167 | -0.013887 | -0.0016258 | -0.0022903 | 0.058687 | 0.04026 | 0.049397 | -0.031001 | -0.003172 | -0.026723 | 0.042971 | 0.03699 | 0.12365 | -0.090531 | 0.069728 | 0.40329 | -0.042615 | 121.7855 | 122.0426 | 121.9817 | -0.15041 | 0.014755 | -122.0701 | 0.074285 | 0.078563 | 0.063808 | -122.076 | -121.9894 | -0.045126 | -0.32755 | 0.17501 | 0.062671 | 0.1078 | -0.070416 | -0.13132 | 0.14826 | 0.14228 | 0.22894 | 0.10211 | -122.2036 | 121.8908 | 122.1479 | 122.087 | 0.50857 | -122.2634
2212.5469 | 122.2824 | -0.068665 | 122.081 | -0.01778 | -0.042205 | 0.039225 | 0.024811 | -0.011865 | 0.00026067 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.040047 | 0.049397 | -0.03558 | 0.010564 | -0.035879 | 0.038393 | 0.046148 | 0.13281 | -0.085952 | 0.069728 | 0.39871 | -0.051772 | 121.7809 | 122.0472 | 121.9726 | -0.15041 | -0.017287 | -122.0426 | 0.033085 | 0.032786 | 0.050073 | -122.0348 | -121.9482 | -0.081747 | -0.30008 | 0.13839 | 0.016893 | 0.09864 | -0.033795 | -0.10843 | 0.10706 | 0.11481 | 0.20147 | 0.079229 | -122.1669 | 121.8496 | 122.1159 | 122.0412 | 0.46737 | -122.2314
2214.25 | 122.1817 | -0.11902 | 122.1039 | -0.01778 | -0.041991 | 0.039439 | 0.024597 | -0.011865 | 0.00047427 | -0.029148 | -0.002053 | -0.0022903 | 0.058687 | 0.040474 | 0.04961 | -0.026423 | 0.010564 | -0.017566 | 0.038393 | 0.046148 | 0.12365 | -0.085952 | 0.06515 | 0.40329 | -0.047194 | 121.7809 | 122.0472 | 121.9771 | -0.14583 | 0.033067 | -122.0655 | 0.092596 | 0.10145 | 0.068386 | -122.0577 | -121.9802 | -0.026814 | -0.32297 | 0.18417 | 0.071825 | 0.098639 | -0.056683 | -0.12674 | 0.15741 | 0.16517 | 0.24267 | 0.12958 | -122.1898 | 121.8999 | 122.1662 | 122.0962 | 0.5223 | -122.2497
2216 | 122.2961 | -0.059509 | 122.0261 | -0.0025182 | -0.042205 | 0.039439 | 0.024383 | -0.011865 | 0.00047427 | -0.021518 | -0.0024804 | -0.0025041 | 0.059114 | 0.040047 | 0.049183 | -0.03558 | -0.007751 | -0.031301 | 0.033814 | 0.041569 | 0.12365 | -0.090531 | 0.069728 | 0.41244 | -0.051772 | 121.7855 | 122.0426 | 121.9726 | -0.15499 | -0.031022 | -121.9922 | 0.023929 | 0.028208 | 0.05923 | -121.9845 | -121.9024 | -0.095482 | -0.24057 | 0.12924 | 0.007737 | 0.10322 | 0.016559 | -0.053497 | 0.093323 | 0.10108 | 0.18316 | 0.051758 | -122.1166 | 121.845 | 122.1021 | 122.0321 | 0.47195 | -122.1811
2217.6875 | 122.2961 | -0.068665 | 122.0627 | -0.025411 | -0.042205 | 0.039652 | 0.024811 | -0.011651 | 0.00047427 | -0.0062567 | -0.0018394 | -0.0018631 | 0.058901 | 0.040047 | 0.048969 | -0.026423 | -0.003172 | -0.031301 | 0.033814 | 0.050727 | 0.13281 | -0.072215 | 0.06515 | 0.40786 | -0.051772 | 121.7855 | 122.0564 | 121.9771 | -0.14583 | -0.00355 | -122.0289 | 0.042242 | 0.037364 | 0.040914 | -122.012 | -121.9299 | -0.077168 | -0.27719 | 0.13382 | 0.016893 | 0.094061 | -0.006326 | -0.08554 | 0.10248 | 0.11939 | 0.20147 | 0.065493 | -122.1349 | 121.8542 | 122.125 | 122.0458 | 0.47653 | -122.2085
2219.4375 | 122.1817 | -0.11902 | 122.1268 | -0.01778 | -0.042418 | 0.039652 | 0.024383 | -0.011437 | 0.00026067 | -0.021518 | -0.0022666 | -0.0018631 | 0.059114 | 0.04026 | 0.04961 | -0.031001 | 0.001407 | -0.026723 | 0.033814 | 0.046148 | 0.12823 | -0.081373 | 0.069728 | 0.40786 | -0.047194 | 121.7901 | 122.0564 | 121.9863 | -0.14583 | 0.037646 | -122.093 | 0.088018 | 0.092296 | 0.05465 | -122.0806 | -121.9985 | -0.026814 | -0.3367 | 0.18875 | 0.071825 | 0.098639 | -0.070413 | -0.14047 | 0.15283 | 0.16517 | 0.24725 | 0.12043 | -122.2081 | 121.9091 | 122.1754 | 122.1053 | 0.52688 | -122.2726
2221.2031 | 122.3465 | -0.059509 | 122.049 | -0.01778 | -0.041777 | 0.039866 | 0.024811 | -0.011651 | 0.00047427 | -0.029148 | -0.002053 | -0.0018631 | 0.058901 | 0.04026 | 0.048969 | -0.031001 | -0.003172 | -0.026723 | 0.042971 | 0.041569 | 0.12823 | -0.081373 | 0.06515 | 0.40786 | -0.051772 | 121.7901 | 122.0655 | 121.9771 | -0.14583 | -0.021864 | -122.006 | 0.028508 | 0.032786 | 0.05465 | -122.0074 | -121.9207 | -0.086324 | -0.25888 | 0.12466 | 0.007737 | 0.094061 | 0.016564 | -0.071807 | 0.10248 | 0.10108 | 0.18774 | 0.056337 | -122.1303 | 121.8496 | 122.125 | 122.0367 | 0.46737 | -122.1948
2222.8906 | 122.3328 | -0.082397 | 122.0306 | -0.010149 | -0.042205 | 0.039439 | 0.024597 | -0.011224 | 0.00068807 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.04026 | 0.049397 | -0.026423 | -0.003172 | -0.022144 | 0.038393 | 0.03699 | 0.12365 | -0.085952 | 0.069728 | 0.40329 | -0.056351 | 121.7946 | 122.0564 | 121.9909 | -0.15041 | -0.003555 | -121.9922 | 0.055974 | 0.060253 | 0.063808 | -121.9937 | -121.907 | -0.068015 | -0.23599 | 0.15213 | 0.026046 | 0.094061 | 0.025717 | -0.039761 | 0.12079 | 0.11939 | 0.20605 | 0.079225 | -122.1166 | 121.877 | 122.1388 | 122.0733 | 0.48568 | -122.1811
2224.6406 | 122.3053 | -0.068665 | 122.0215 | -0.010149 | -0.042632 | 0.039439 | 0.024811 | -0.011437 | 0.00026067 | -0.0062567 | -0.002053 | -0.0027177 | 0.058901 | 0.04026 | 0.049183 | -0.031001 | 0.005985 | -0.026723 | 0.042971 | 0.041569 | 0.12365 | -0.085952 | 0.069728 | 0.39413 | -0.042615 | 121.7901 | 122.0518 | 121.9817 | -0.15041 | -0.017287 | -121.9785 | 0.037664 | 0.041942 | 0.059229 | -121.9799 | -121.8978 | -0.081747 | -0.23142 | 0.13839 | 0.02605 | 0.1078 | 0.030294 | -0.039762 | 0.11164 | 0.11023 | 0.19232 | 0.07465 | -122.1074 | 121.8587 | 122.1204 | 122.0504 | 0.46279 | -122.1719
2226.3281 | 122.1909 | -0.11902 | 122.0856 | -0.010149 | -0.042205 | 0.039652 | 0.024383 | -0.011437 | 4.7068e-05 | -0.029148 | -0.0022666 | -0.0027177 | 0.059114 | 0.040688 | 0.04961 | -0.03558 | -0.003172 | -0.022144 | 0.042971 | 0.046148 | 0.12365 | -0.085952 | 0.069728 | 0.40786 | -0.051772 | 121.7946 | 122.0472 | 121.9863 | -0.15041 | 0.033067 | -122.0426 | 0.083439 | 0.096875 | 0.063808 | -122.0394 | -121.9619 | -0.031393 | -0.29093 | 0.18875 | 0.067247 | 0.09864 | -0.038372 | -0.099271 | 0.16199 | 0.16517 | 0.24267 | 0.11585 | -122.1715 | 121.9137 | 122.1662 | 122.1053 | 0.52688 | -122.236
2228.0781 | 122.2412 | -0.10529 | 122.0856 | -0.01778 | -0.042418 | 0.039866 | 0.02417 | -0.011437 | 0.00026067 | -0.021518 | -0.0018394 | -0.0025041 | 0.058901 | 0.04026 | 0.049397 | -0.031001 | 0.001407 | -0.022144 | 0.052128 | 0.041569 | 0.12823 | -0.081373 | 0.074307 | 0.40329 | -0.042615 | 121.7855 | 122.0426 | 121.9771 | -0.14583 | 0.023913 | -122.0334 | 0.074285 | 0.083142 | 0.059229 | -122.044 | -121.9573 | -0.040547 | -0.30008 | 0.17959 | 0.062671 | 0.10322 | -0.04295 | -0.10843 | 0.15741 | 0.14686 | 0.23352 | 0.10669 | -122.1669 | 121.8908 | 122.1479 | 122.0824 | 0.50857 | -122.2314
2229.8281 | 122.1771 | -0.13275 | 122.0993 | -0.0025182 | -0.042205 | 0.039652 | 0.024383 | -0.011651 | 0.00026067 | -0.0062567 | -0.0016258 | -0.0025041 | 0.059114 | 0.040688 | 0.04961 | -0.026423 | 0.005985 | -0.022144 | 0.047549 | 0.041569 | 0.12823 | -0.085952 | 0.074307 | 0.40786 | -0.047194 | 121.7946 | 122.0564 | 121.9817 | -0.14583 | 0.046799 | -122.0518 | 0.10633 | 0.11061 | 0.063808 | -122.0577 | -121.9711 | -0.013082 | -0.30466 | 0.20706 | 0.085557 | 0.098639 | -0.042947 | -0.11758 | 0.1803 | 0.17432 | 0.26098 | 0.13874 | -122.1853 | 121.9274 | 122.1891 | 122.1145 | 0.54062 | -122.2451
2231.5625 | 122.287 | -0.086975 | 122.0673 | -0.010149 | -0.042205 | 0.039652 | 0.024597 | -0.011437 | 0.00026067 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.040688 | 0.04961 | -0.03558 | -0.003172 | -0.017566 | 0.042971 | 0.046148 | 0.12823 | -0.081373 | 0.06515 | 0.40786 | -0.051772 | 121.8038 | 122.0609 | 121.9817 | -0.14583 | 0.005602 | -122.0243 | 0.051395 | 0.069409 | 0.063807 | -122.0211 | -121.939 | -0.058858 | -0.26346 | 0.15213 | 0.035203 | 0.094061 | -0.006326 | -0.085539 | 0.12995 | 0.13312 | 0.21521 | 0.083803 | -122.1486 | 121.8908 | 122.1479 | 122.0687 | 0.49484 | -122.2131
2233.3125 | 122.1725 | -0.11444 | 122.0901 | -0.0025182 | -0.041991 | 0.039652 | 0.024383 | -0.012078 | 0.00026067 | -0.013887 | -0.0022666 | -0.0022903 | 0.058901 | 0.040474 | 0.04961 | -0.031001 | -0.003172 | -0.026723 | 0.052128 | 0.03699 | 0.12823 | -0.085952 | 0.069728 | 0.40786 | -0.047194 | 121.8038 | 122.0609 | 121.9909 | -0.15041 | 0.028489 | -122.038 | 0.08344 | 0.087718 | 0.059229 | -122.0532 | -121.9619 | -0.035971 | -0.28635 | 0.18417 | 0.067247 | 0.10322 | -0.029214 | -0.09927 | 0.16657 | 0.15143 | 0.24267 | 0.11127 | -122.1761 | 121.9182 | 122.1754 | 122.1053 | 0.52231 | -122.2406
2235 | 122.168 | -0.11444 | 122.1176 | -0.010149 | -0.042418 | 0.039439 | 0.024597 | -0.011224 | 0.00026067 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.040474 | 0.049397 | -0.026423 | 0.001407 | -0.026723 | 0.038393 | 0.046148 | 0.13739 | -0.085952 | 0.06515 | 0.40786 | -0.051772 | 121.8038 | 122.0518 | 121.9909 | -0.15041 | 0.028489 | -122.0792 | 0.088018 | 0.087718 | 0.059229 | -122.0715 | -121.9802 | -0.035971 | -0.31381 | 0.17959 | 0.062669 | 0.09864 | -0.065837 | -0.12674 | 0.15283 | 0.16059 | 0.25183 | 0.11585 | -122.2036 | 121.9182 | 122.1662 | 122.1053 | 0.52231 | -122.268
2236.7344 | 122.3419 | -0.07782 | 122.0581 | -0.010149 | -0.042418 | 0.039652 | 0.024383 | -0.011865 | 0.00026067 | -0.013887 | -0.0024804 | -0.0020767 | 0.059114 | 0.040474 | 0.04961 | -0.031001 | 0.001407 | -0.026723 | 0.047549 | 0.041569 | 0.12823 | -0.085952 | 0.06515 | 0.40786 | -0.042615 | 121.7992 | 122.0655 | 121.9863 | -0.14583 | -0.008132 | -122.0106 | 0.046819 | 0.051097 | 0.059229 | -122.0165 | -121.9299 | -0.068013 | -0.25888 | 0.14297 | 0.035205 | 0.10322 | 0.007409 | -0.071805 | 0.12537 | 0.11939 | 0.20605 | 0.079227 | -122.1441 | 121.877 | 122.1433 | 122.0641 | 0.48568 | -122.2039
2238.4375 | 122.3053 | -0.064087 | 122.0535 | -0.0025182 | -0.042205 | 0.039866 | 0.024597 | -0.011437 | 0.00026067 | -0.021518 | -0.002053 | -0.0022903 | 0.059328 | 0.040474 | 0.049397 | -0.026423 | -0.003172 | -0.022144 | 0.047549 | 0.041569 | 0.12365 | -0.081373 | 0.069728 | 0.40786 | -0.047194 | 121.7992 | 122.0564 | 121.9955 | -0.15041 | -0.017286 | -122.006 | 0.037664 | 0.041943 | 0.059229 | -122.012 | -121.9299 | -0.086325 | -0.2543 | 0.13382 | 0.016893 | 0.10322 | 0.002829 | -0.05807 | 0.11164 | 0.10566 | 0.18774 | 0.060915 | -122.1349 | 121.8633 | 122.1204 | 122.0595 | 0.47195 | -122.2039
2240.1875 | 122.2458 | -0.10986 | 122.1268 | -0.010149 | -0.042632 | 0.039866 | 0.024383 | -0.011651 | 4.7068e-05 | -0.021518 | -0.002053 | -0.0027177 | 0.058901 | 0.040474 | 0.04961 | -0.026423 | 0.001407 | -0.022144 | 0.047549 | 0.046148 | 0.12823 | -0.085952 | 0.069728 | 0.41244 | -0.042615 | 121.8038 | 122.0701 | 121.9817 | -0.14125 | 0.023911 | -122.0792 | 0.08344 | 0.087719 | 0.063808 | -122.0806 | -121.9985 | -0.031392 | -0.32297 | 0.17959 | 0.067248 | 0.09864 | -0.056678 | -0.14505 | 0.15741 | 0.15601 | 0.23809 | 0.11127 | -122.2127 | 121.9137 | 122.18 | 122.0916 | 0.52231 | -122.268
2241.9375 | 122.1817 | -0.13733 | 122.1085 | -0.010149 | -0.042418 | 0.039866 | 0.023956 | -0.011651 | -0.00016673 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.040474 | 0.049397 | -0.026423 | 0.001407 | -0.026723 | 0.038393 | 0.03699 | 0.12823 | -0.081373 | 0.069728 | 0.40786 | -0.051772 | 121.7946 | 122.0701 | 121.9863 | -0.15041 | 0.055956 | -122.0701 | 0.11091 | 0.11061 | 0.05465 | -122.0715 | -121.9802 | -0.013083 | -0.31381 | 0.20706 | 0.085557 | 0.09864 | -0.038367 | -0.12216 | 0.17572 | 0.17432 | 0.26556 | 0.13874 | -122.1898 | 121.932 | 122.2074 | 122.1236 | 0.54519 | -122.2589
2243.6406 | 122.1771 | -0.11444 | 122.1085 | -0.01778 | -0.042632 | 0.039866 | 0.024383 | -0.011651 | 0.00026067 | -0.013887 | -0.0018394 | -0.0022903 | 0.059114 | 0.040474 | 0.049183 | -0.026423 | 0.001407 | -0.022144 | 0.047549 | 0.046148 | 0.13739 | -0.081373 | 0.069728 | 0.41244 | -0.06093 | 121.7992 | 122.0655 | 121.9955 | -0.14125 | 0.033068 | -122.0609 | 0.088018 | 0.092297 | 0.059229 | -122.0623 | -121.9711 | -0.026814 | -0.30924 | 0.18417 | 0.053511 | 0.080325 | -0.042945 | -0.113 | 0.16199 | 0.16059 | 0.25183 | 0.11585 | -122.1898 | 121.9137 | 122.18 | 122.1099 | 0.52688 | -122.2497
2245.3906 | 122.3099 | -0.073242 | 122.0581 | -0.0025182 | -0.042205 | 0.039866 | 0.02417 | -0.011865 | 4.7068e-05 | -0.029148 | -0.0022666 | -0.0022903 | 0.058901 | 0.040474 | 0.049397 | -0.026423 | 0.005985 | -0.026723 | 0.038393 | 0.046148 | 0.13281 | -0.081373 | 0.074307 | 0.41244 | -0.047194 | 121.8038 | 122.0701 | 121.9909 | -0.15499 | -0.008131 | -122.0197 | 0.046819 | 0.046519 | 0.05465 | -122.012 | -121.9253 | -0.081749 | -0.2543 | 0.14755 | 0.026048 | 0.1078 | 0.011987 | -0.067226 | 0.11163 | 0.11939 | 0.20605 | 0.079227 | -122.1395 | 121.877 | 122.1433 | 122.0641 | 0.48569 | -122.2131
2247.1406 | 122.2046 | -0.13275 | 122.1085 | -0.010149 | -0.042205 | 0.039866 | 0.023956 | -0.011865 | 0.00026067 | -0.0062567 | -0.002053 | -0.0022903 | 0.058687 | 0.040688 | 0.049183 | -0.026423 | -0.003172 | -0.022144 | 0.038393 | 0.050727 | 0.12823 | -0.090531 | 0.074307 | 0.40329 | -0.047194 | 121.8084 | 122.0655 | 121.9909 | -0.14583 | 0.04222 | -122.0701 | 0.10633 | 0.11061 | 0.068387 | -122.0577 | -121.9802 | -0.013082 | -0.30008 | 0.20706 | 0.085557 | 0.098639 | -0.042945 | -0.11758 | 0.17114 | 0.18348 | 0.26098 | 0.12958 | -122.199 | 121.9411 | 122.1983 | 122.1236 | 0.53604 | -122.2543
2248.8281 | 122.319 | -0.07782 | 122.0581 | -0.025411 | -0.042418 | 0.04008 | 0.023956 | -0.011865 | -0.00016673 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.04026 | 0.049183 | -0.026423 | 0.001407 | -0.022144 | 0.047549 | 0.041569 | 0.13281 | -0.085952 | 0.069728 | 0.40786 | -0.042615 | 121.8038 | 122.0747 | 121.9955 | -0.14583 | -0.008132 | -122.0106 | 0.051397 | 0.055676 | 0.063808 | -122.0165 | -121.9253 | -0.068013 | -0.2543 | 0.14755 | 0.035205 | 0.10322 | 0.016566 | -0.062647 | 0.12537 | 0.11939 | 0.21063 | 0.079227 | -122.1441 | 121.8816 | 122.1525 | 122.0733 | 0.48568 | -122.2039
2250.5781 | 122.2092 | -0.10071 | 122.1085 | -0.010149 | -0.042632 | 0.039439 | 0.023956 | -0.011651 | -0.00016673 | -0.029148 | -0.002053 | -0.0022903 | 0.058901 | 0.040474 | 0.049397 | -0.026423 | 0.001407 | -0.012988 | 0.047549 | 0.041569 | 0.13281 | -0.081373 | 0.069728 | 0.41244 | -0.051772 | 121.8038 | 122.0747 | 122 | -0.15041 | 0.019335 | -122.0609 | 0.074285 | 0.08772 | 0.068385 | -122.0669 | -121.9757 | -0.049704 | -0.30466 | 0.17044 | 0.048936 | 0.09864 | -0.033788 | -0.10842 | 0.14826 | 0.14228 | 0.23352 | 0.10212 | -122.1898 | 121.9045 | 122.1754 | 122.1007 | 0.51315 | -122.2589
2252.2656 | 122.1817 | -0.10986 | 122.1359 | -0.025411 | -0.042418 | 0.039866 | 0.024383 | -0.011865 | -0.00016673 | -0.021518 | -0.0022666 | -0.0020767 | 0.059114 | 0.04026 | 0.049397 | -0.026423 | 0.005985 | -0.012988 | 0.042971 | 0.050727 | 0.14197 | -0.076794 | 0.069728 | 0.41702 | -0.047194 | 121.7992 | 122.0701 | 121.9955 | -0.14583 | 0.033069 | -122.093 | 0.08344 | 0.096875 | 0.063806 | -122.0852 | -121.994 | -0.03597 | -0.3367 | 0.17959 | 0.062669 | 0.098639 | -0.065833 | -0.14047 | 0.15283 | 0.16059 | 0.25183 | 0.11585 | -122.2127 | 121.9091 | 122.18 | 122.1053 | 0.52689 | -122.2818
2254.0312 | 122.1863 | -0.11444 | 122.0993 | -0.01778 | -0.042205 | 0.039866 | 0.02417 | -0.011651 | -0.00016673 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.040901 | 0.04961 | -0.031001 | 0.001407 | -0.022144 | 0.047549 | 0.041569 | 0.12365 | -0.085952 | 0.069728 | 0.40786 | -0.047194 | 121.7992 | 122.0701 | 122 | -0.14125 | 0.028489 | -122.0518 | 0.08344 | 0.092297 | 0.063808 | -122.0577 | -121.9757 | -0.026814 | -0.30008 | 0.18417 | 0.067247 | 0.094061 | -0.029212 | -0.099268 | 0.16199 | 0.15601 | 0.23809 | 0.11585 | -122.1853 | 121.9137 | 122.1845 | 122.1145 | 0.52231 | -122.2406
2255.7812 | 122.287 | -0.091553 | 122.0581 | -0.0025182 | -0.042632 | 0.039866 | 0.024383 | -0.011651 | -0.00016673 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.040474 | 0.04961 | -0.031001 | 0.001407 | -0.017566 | 0.042971 | 0.050727 | 0.13739 | -0.081373 | 0.069728 | 0.40786 | -0.051772 | 121.8084 | 122.0701 | 122 | -0.14125 | 0.01018 | -122.0151 | 0.060552 | 0.073987 | 0.063807 | -122.0074 | -121.9207 | -0.049702 | -0.24972 | 0.16128 | 0.039781 | 0.089483 | 0.011987 | -0.058069 | 0.13452 | 0.14228 | 0.22894 | 0.09296 | -122.1395 | 121.8999 | 122.1616 | 122.0916 | 0.49942 | -122.1994
2257.4688 | 122.2595 | -0.086975 | 122.0764 | -0.01778 | -0.042846 | 0.039866 | 0.023956 | -0.011651 | -0.00038033 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.04026 | 0.049397 | -0.031001 | 0.001407 | -0.022144 | 0.042971 | 0.046148 | 0.14197 | -0.085952 | 0.083464 | 0.41244 | -0.042615 | 121.8084 | 122.0747 | 121.9955 | -0.14583 | 0.001023 | -122.0334 | 0.055974 | 0.064831 | 0.063808 | -122.0303 | -121.9344 | -0.058858 | -0.26803 | 0.17044 | 0.04436 | 0.10322 | -0.001745 | -0.080958 | 0.12995 | 0.13312 | 0.22894 | 0.088382 | -122.1624 | 121.8954 | 122.1616 | 122.0824 | 0.49942 | -122.2222
2259.2344 | 122.2458 | -0.1236 | 122.1222 | -0.010149 | -0.043059 | 0.040293 | 0.023956 | -0.011651 | -0.00016673 | -0.021518 | -0.0016258 | -0.0025041 | 0.058687 | 0.040901 | 0.049397 | -0.021844 | 0.001407 | -0.017566 | 0.047549 | 0.046148 | 0.14197 | -0.076794 | 0.074307 | 0.41244 | -0.047194 | 121.813 | 122.0701 | 122.0092 | -0.13668 | 0.046802 | -122.0746 | 0.10175 | 0.10603 | 0.059228 | -122.076 | -121.9802 | -0.01308 | -0.30923 | 0.1979 | 0.076402 | 0.089482 | -0.0521 | -0.113 | 0.17114 | 0.16974 | 0.26556 | 0.125 | -122.199 | 121.9366 | 122.1937 | 122.1328 | 0.53604 | -122.2589
2260.9375 | 122.1817 | -0.1236 | 122.1176 | -0.010149 | -0.042846 | 0.04008 | 0.023956 | -0.011651 | -0.00016673 | -0.021518 | -0.002053 | -0.0020767 | 0.058473 | 0.040688 | 0.049397 | -0.017266 | 0.001407 | -0.022144 | 0.047549 | 0.046148 | 0.13281 | -0.081373 | 0.078886 | 0.41702 | -0.042615 | 121.813 | 122.0701 | 122.0046 | -0.14583 | 0.042223 | -122.0701 | 0.10633 | 0.10145 | 0.059229 | -122.0715 | -121.9848 | -0.022237 | -0.30465 | 0.20248 | 0.080981 | 0.10322 | -0.047523 | -0.113 | 0.17114 | 0.16974 | 0.2564 | 0.125 | -122.199 | 121.9366 | 122.1937 | 122.1282 | 0.54062 | -122.2634
2262.6875 | 122.2092 | -0.11444 | 122.1085 | -0.0025182 | -0.043273 | 0.039866 | 0.023956 | -0.011651 | -0.00016673 | -0.029148 | -0.0022666 | -0.0022903 | 0.058901 | 0.040688 | 0.049183 | -0.031001 | 0.005985 | -0.026723 | 0.052128 | 0.050727 | 0.12823 | -0.085952 | 0.069728 | 0.41702 | -0.047194 | 121.8084 | 122.0747 | 121.9955 | -0.15041 | 0.028489 | -122.0563 | 0.08344 | 0.087718 | 0.059229 | -122.0577 | -121.9802 | -0.035971 | -0.30008 | 0.18417 | 0.067247 | 0.10322 | -0.033788 | -0.113 | 0.16657 | 0.16517 | 0.24267 | 0.12043 | -122.1944 | 121.9228 | 122.1891 | 122.1099 | 0.53146 | -122.2589
2264.4375 | 122.1954 | -0.10986 | 122.1222 | -0.010149 | -0.043059 | 0.039866 | 0.02417 | -0.011865 | -0.00038033 | -0.013887 | -0.0018394 | -0.0022903 | 0.059328 | 0.040474 | 0.049397 | -0.031001 | 0.010564 | -0.017566 | 0.042971 | 0.050727 | 0.13281 | -0.076794 | 0.074307 | 0.41702 | -0.047194 | 121.8175 | 122.0793 | 122.0046 | -0.14125 | 0.033069 | -122.0792 | 0.078862 | 0.092297 | 0.059228 | -122.0715 | -121.9894 | -0.031392 | -0.30465 | 0.18417 | 0.062669 | 0.094061 | -0.042942 | -0.11758 | 0.15283 | 0.16059 | 0.24267 | 0.12043 | -122.199 | 121.9274 | 122.1891 | 122.1145 | 0.52689 | -122.2634
2266.1406 | 122.3236 | -0.073242 | 122.0993 | -0.010149 | -0.042846 | 0.04008 | 0.023742 | -0.011651 | 4.7068e-05 | -0.021518 | -0.002053 | -0.0025041 | 0.059114 | 0.041115 | 0.049397 | -0.03558 | 0.001407 | -0.017566 | 0.047549 | 0.055306 | 0.14197 | -0.076794 | 0.069728 | 0.41702 | -0.047194 | 121.813 | 122.0793 | 122 | -0.13668 | -0.003552 | -122.0518 | 0.037662 | 0.055676 | 0.059228 | -122.044 | -121.9573 | -0.063434 | -0.28634 | 0.14297 | 0.026048 | 0.089482 | -0.020054 | -0.099268 | 0.12079 | 0.12855 | 0.21521 | 0.074649 | -122.1761 | 121.8862 | 122.1525 | 122.0733 | 0.49026 | -122.236
2267.8906 | 122.2549 | -0.11444 | 122.1222 | -0.010149 | -0.042846 | 0.04008 | 0.023742 | -0.011865 | -0.00038033 | -0.013887 | -0.0024804 | -0.0022903 | 0.058901 | 0.040688 | 0.049397 | -0.026423 | 0.005985 | -0.022144 | 0.047549 | 0.046148 | 0.13739 | -0.076794 | 0.078886 | 0.41702 | -0.056351 | 121.8175 | 122.0701 | 122.0138 | -0.15041 | 0.037647 | -122.0746 | 0.088018 | 0.092297 | 0.05465 | -122.076 | -121.9848 | -0.035971 | -0.30465 | 0.19333 | 0.05809 | 0.094061 | -0.0521 | -0.10842 | 0.16199 | 0.16059 | 0.25183 | 0.12043 | -122.199 | 121.932 | 122.1845 | 122.1282 | 0.53146 | -122.2726
2269.6406 | 122.287 | -0.07782 | 122.0627 | -0.01778 | -0.042632 | 0.04008 | 0.023742 | -0.011651 | -0.00038033 | -0.021518 | -0.0022666 | -0.0025041 | 0.058901 | 0.040688 | 0.049183 | -0.017266 | 0.005985 | -0.017566 | 0.038393 | 0.046148 | 0.13739 | -0.081373 | 0.074307 | 0.41702 | -0.042615 | 121.813 | 122.0793 | 122.0092 | -0.14583 | -0.003553 | -122.0243 | 0.060554 | 0.060254 | 0.063807 | -122.0165 | -121.9253 | -0.068013 | -0.24972 | 0.15213 | 0.035205 | 0.10322 | 0.016567 | -0.05349 | 0.11621 | 0.12397 | 0.21521 | 0.083805 | -122.1441 | 121.8908 | 122.1571 | 122.087 | 0.49484 | -122.2085
2271.3281 | 122.3007 | -0.082397 | 122.0856 | -0.010149 | -0.042846 | 0.04008 | 0.023742 | -0.011865 | -0.00038033 | -0.013887 | -0.0016258 | -0.0025041 | 0.058687 | 0.040688 | 0.049183 | -0.031001 | 0.010564 | -0.017566 | 0.038393 | 0.050727 | 0.14197 | -0.081373 | 0.069728 | 0.41702 | -0.051772 | 121.8175 | 122.0793 | 121.9955 | -0.14583 | 0.001024 | -122.0472 | 0.051396 | 0.064831 | 0.063807 | -122.0348 | -121.9436 | -0.063436 | -0.26803 | 0.15213 | 0.030625 | 0.094061 | -0.006321 | -0.090113 | 0.12079 | 0.13312 | 0.22436 | 0.092961 | -122.1669 | 121.8999 | 122.1616 | 122.0779 | 0.49942 | -122.2314
2273.0781 | 122.2 | -0.12817 | 122.1176 | -0.010149 | -0.043059 | 0.040293 | 0.023742 | -0.011865 | -0.0018759 | -0.021518 | -0.0016258 | -0.0022903 | 0.059114 | 0.040901 | 0.049397 | -0.031001 | 0.015142 | -0.022144 | 0.052128 | 0.055306 | 0.13739 | -0.085952 | 0.06515 | 0.41244 | -0.047194 | 121.813 | 122.0884 | 121.9955 | -0.14583 | 0.042222 | -122.0655 | 0.097173 | 0.10603 | 0.063808 | -122.0623 | -121.9802 | -0.017659 | -0.30465 | 0.19332 | 0.08098 | 0.098639 | -0.029208 | -0.12216 | 0.1803 | 0.18348 | 0.26556 | 0.14332 | -122.2036 | 121.9411 | 122.2166 | 122.1236 | 0.54062 | -122.2634
2274.8438 | 122.2504 | -0.11444 | 122.1176 | 0.0051128 | -0.043273 | 0.040934 | 0.023742 | -0.012292 | -0.0035853 | -0.021518 | -0.0016258 | -0.0020767 | 0.059114 | 0.040688 | 0.049397 | -0.021844 | 0.005985 | -0.022144 | 0.047549 | 0.055306 | 0.14655 | -0.085952 | 0.06515 | 0.41244 | -0.051772 | 121.813 | 122.0793 | 122.0046 | -0.14583 | 0.028489 | -122.0701 | 0.092597 | 0.092297 | 0.063808 | -122.0623 | -121.9711 | -0.031392 | -0.30465 | 0.17959 | 0.062669 | 0.094061 | -0.038365 | -0.113 | 0.16199 | 0.16975 | 0.26099 | 0.12043 | -122.2036 | 121.9274 | 122.1937 | 122.1191 | 0.52688 | -122.2634
2276.6094 | 122.2 | -0.13733 | 122.1405 | -0.01778 | -0.043273 | 0.041148 | 0.023315 | -0.011651 | -0.0037989 | -0.013887 | -0.0018394 | -0.0020767 | 0.059114 | 0.040474 | 0.049183 | -0.021844 | 0.010564 | -0.017566 | 0.047549 | 0.059885 | 0.14197 | -0.081373 | 0.06515 | 0.41702 | -0.047194 | 121.8084 | 122.0747 | 122 | -0.15957 | 0.055956 | -122.093 | 0.11549 | 0.11976 | 0.063807 | -122.0806 | -121.9985 | -0.022241 | -0.33212 | 0.20248 | 0.090135 | 0.11238 | -0.065832 | -0.14047 | 0.18488 | 0.19721 | 0.2793 | 0.14789 | -122.2219 | 121.9457 | 122.212 | 122.1374 | 0.55435 | -122.3001
2278.375 | 122.2961 | -0.10071 | 122.081 | -0.010149 | -0.043059 | 0.040934 | 0.023529 | -0.011651 | -0.0040125 | -0.021518 | -0.002053 | -0.0020767 | 0.059328 | 0.040688 | 0.049397 | -0.012688 | 0.005985 | -0.008409 | 0.056706 | 0.055306 | 0.14655 | -0.090531 | 0.06515 | 0.41702 | -0.051772 | 121.813 | 122.0701 | 122 | -0.14583 | 0.010177 | -122.0243 | 0.08802 | 0.092299 | 0.082122 | -122.0257 | -121.9344 | -0.045125 | -0.26803 | 0.16586 | 0.048936 | 0.094061 | -0.010902 | -0.080958 | 0.15741 | 0.15601 | 0.24725 | 0.10669 | -122.1715 | 121.9137 | 122.1708 | 122.1007 | 0.51773 | -122.2268
2280.1406 | 122.2778 | -0.086975 | 122.0718 | -0.01778 | -0.043914 | 0.041148 | 0.022888 | -0.012078 | -0.0046535 | -0.029148 | -0.0016258 | -0.0025041 | 0.059114 | 0.040688 | 0.049397 | -0.021844 | 0.010564 | -0.012988 | 0.052128 | 0.059885 | 0.14197 | -0.081373 | 0.06515 | 0.41702 | -0.051772 | 121.8175 | 122.0793 | 122.0046 | -0.15957 | 0.005602 | -122.0197 | 0.065131 | 0.073987 | 0.068385 | -122.012 | -121.9299 | -0.072595 | -0.2543 | 0.15213 | 0.035203 | 0.1078 | 0.007412 | -0.067223 | 0.1391 | 0.14686 | 0.22894 | 0.097539 | -122.1532 | 121.9045 | 122.1662 | 122.0916 | 0.504 | -122.2314
2281.8281 | 122.3328 | -0.073242 | 122.0901 | -0.010149 | -0.043914 | 0.041148 | 0.023101 | -0.011651 | -0.0046535 | -0.021518 | -0.0022666 | -0.0022903 | 0.059114 | 0.041115 | 0.049183 | -0.021844 | 0.005985 | -0.008409 | 0.056706 | 0.050727 | 0.14197 | -0.090531 | 0.06515 | 0.41702 | -0.042615 | 121.813 | 122.0793 | 122 | -0.15041 | -0.017289 | -122.0334 | 0.051398 | 0.064833 | 0.082122 | -122.0394 | -121.9482 | -0.07717 | -0.27719 | 0.13839 | 0.030627 | 0.1078 | -0.010899 | -0.090113 | 0.12995 | 0.12397 | 0.21521 | 0.079227 | -122.1807 | 121.8862 | 122.1525 | 122.0733 | 0.49026 | -122.2406
2283.5781 | 122.3602 | -0.059509 | 122.0627 | -0.025411 | -0.043273 | 0.041362 | 0.023101 | -0.011651 | -0.0046535 | -0.0062567 | -0.002053 | -0.0027177 | 0.058687 | 0.041115 | 0.049183 | -0.031001 | 0.010564 | -0.008409 | 0.056706 | 0.050727 | 0.13739 | -0.085952 | 0.06515 | 0.41244 | -0.056351 | 121.8221 | 122.0884 | 122.0046 | -0.15499 | -0.026443 | -122.006 | 0.028508 | 0.0511 | 0.077543 | -122.012 | -121.9253 | -0.095482 | -0.24057 | 0.12466 | 0.003158 | 0.09864 | 0.025724 | -0.058068 | 0.11621 | 0.11024 | 0.1969 | 0.070073 | -122.1486 | 121.8816 | 122.1479 | 122.0641 | 0.47195 | -122.2177
2285.3281 | 122.3419 | -0.07782 | 122.081 | -0.0025182 | -0.043273 | 0.041148 | 0.023101 | -0.011651 | -0.0046535 | -0.021518 | -0.0016258 | -0.0022903 | 0.059114 | 0.040688 | 0.049183 | -0.021844 | 0.010564 | -0.017566 | 0.042971 | 0.055306 | 0.14197 | -0.085952 | 0.06515 | 0.42618 | -0.051772 | 121.8084 | 122.0838 | 122 | -0.15499 | -0.008132 | -122.038 | 0.055976 | 0.060254 | 0.068386 | -122.0257 | -121.939 | -0.077171 | -0.27261 | 0.14297 | 0.026048 | 0.10322 | 0.002834 | -0.080958 | 0.12079 | 0.13313 | 0.21979 | 0.088384 | -122.1669 | 121.8862 | 122.1616 | 122.0779 | 0.504 | -122.236
2287.0781 | 122.3419 | -0.10071 | 122.0856 | -0.01778 | -0.043273 | 0.041789 | 0.023101 | -0.011865 | -0.0050809 | -0.0062567 | -0.002053 | -0.0027177 | 0.058687 | 0.040688 | 0.049397 | -0.021844 | 0.010564 | -0.017566 | 0.056706 | 0.059885 | 0.14655 | -0.081373 | 0.069728 | 0.4216 | -0.051772 | 121.8175 | 122.0838 | 122.0138 | -0.14583 | 0.019335 | -122.0289 | 0.078864 | 0.083142 | 0.063807 | -122.0257 | -121.939 | -0.045125 | -0.26803 | 0.17044 | 0.048936 | 0.094061 | -0.001743 | -0.071799 | 0.15741 | 0.16059 | 0.24725 | 0.11127 | -122.1669 | 121.9182 | 122.1845 | 122.1145 | 0.52231 | -122.2314
2288.8438 | 122.2275 | -0.11444 | 122.113 | -0.010149 | -0.043487 | 0.041148 | 0.023529 | -0.011651 | -0.0046535 | -0.021518 | -0.0018394 | -0.0022903 | 0.058901 | 0.040688 | 0.049397 | -0.017266 | 0.015142 | -0.012988 | 0.056706 | 0.050727 | 0.13739 | -0.090531 | 0.06515 | 0.41702 | -0.051772 | 121.8084 | 122.093 | 122.0092 | -0.15499 | 0.02391 | -122.0563 | 0.097175 | 0.10145 | 0.077543 | -122.0623 | -121.9757 | -0.04055 | -0.30466 | 0.17959 | 0.062669 | 0.10322 | -0.020052 | -0.10384 | 0.17115 | 0.16517 | 0.25183 | 0.12958 | -122.2036 | 121.9228 | 122.2074 | 122.1236 | 0.53146 | -122.268
2290.5312 | 122.2275 | -0.10986 | 122.1268 | -0.01778 | -0.043273 | 0.041362 | 0.022888 | -0.011651 | -0.0048673 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.040901 | 0.049183 | -0.012688 | 0.010564 | -0.012988 | 0.052128 | 0.059885 | 0.14197 | -0.085952 | 0.06515 | 0.41244 | -0.047194 | 121.8221 | 122.0838 | 122.0092 | -0.15041 | 0.023911 | -122.0746 | 0.097175 | 0.096875 | 0.072964 | -122.0669 | -121.9848 | -0.040549 | -0.30465 | 0.17501 | 0.062669 | 0.10322 | -0.042942 | -0.11758 | 0.16199 | 0.16975 | 0.25183 | 0.12043 | -122.2127 | 121.932 | 122.1937 | 122.1191 | 0.52231 | -122.2772
2292.2812 | 122.319 | -0.064087 | 122.081 | -0.010149 | -0.043701 | 0.041362 | 0.023315 | -0.011865 | -0.0048673 | 0.0013733 | -0.002053 | -0.0022903 | 0.058901 | 0.040901 | 0.049183 | -0.021844 | 0.010564 | -0.012988 | 0.052128 | 0.059885 | 0.14655 | -0.090531 | 0.06515 | 0.4216 | -0.051772 | 121.8221 | 122.0793 | 122.0138 | -0.15499 | -0.026444 | -122.0289 | 0.042243 | 0.051099 | 0.077543 | -122.0211 | -121.9344 | -0.090904 | -0.25888 | 0.12924 | 0.012315 | 0.10322 | -0.001744 | -0.067222 | 0.11622 | 0.12397 | 0.21063 | 0.074651 | -122.1715 | 121.8862 | 122.1433 | 122.0779 | 0.48569 | -122.236
2294.0312 | 122.3145 | -0.086975 | 122.0901 | -0.010149 | -0.043701 | 0.041362 | 0.023529 | -0.011651 | -0.0050809 | -0.013887 | -0.002053 | -0.0025041 | 0.058901 | 0.040688 | 0.049397 | -0.021844 | 0.005985 | -0.017566 | 0.056706 | 0.055306 | 0.13739 | -0.09511 | 0.074307 | 0.41244 | -0.047194 | 121.813 | 122.0884 | 122.0092 | -0.15041 | -0.008135 | -122.0334 | 0.065131 | 0.069409 | 0.077544 | -122.0348 | -121.9528 | -0.063437 | -0.27719 | 0.16128 | 0.039781 | 0.10322 | -0.001742 | -0.080956 | 0.14368 | 0.14228 | 0.22436 | 0.09296 | -122.1853 | 121.8999 | 122.1754 | 122.0962 | 0.49942 | -122.2406
2295.7188 | 122.2229 | -0.12817 | 122.1085 | -0.0025182 | -0.043701 | 0.041575 | 0.023315 | -0.011651 | -0.0052945 | -0.013887 | -0.0014122 | -0.0025041 | 0.058901 | 0.040688 | 0.049397 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.059885 | 0.14197 | -0.085952 | 0.069728 | 0.41702 | -0.051772 | 121.8221 | 122.0884 | 122.0092 | -0.15041 | 0.042222 | -122.0518 | 0.10633 | 0.11519 | 0.072964 | -122.0486 | -121.9665 | -0.022238 | -0.28634 | 0.1979 | 0.076402 | 0.09864 | -0.020052 | -0.099266 | 0.18488 | 0.18806 | 0.27014 | 0.13874 | -122.1944 | 121.9503 | 122.2166 | 122.1374 | 0.5452 | -122.2589
2297.4688 | 122.2229 | -0.1236 | 122.1039 | -0.010149 | -0.043487 | 0.041362 | 0.023101 | -0.011865 | -0.0050809 | -0.021518 | -0.0022666 | -0.0020767 | 0.059328 | 0.040901 | 0.049397 | -0.021844 | 0.015142 | -0.012988 | 0.052128 | 0.055306 | 0.14197 | -0.09511 | 0.06515 | 0.4216 | -0.047194 | 121.8175 | 122.0884 | 122.0184 | -0.15499 | 0.028486 | -122.0518 | 0.10175 | 0.11061 | 0.082122 | -122.0486 | -121.9619 | -0.031395 | -0.28634 | 0.18875 | 0.076402 | 0.1078 | -0.015475 | -0.085531 | 0.17572 | 0.1789 | 0.26556 | 0.13874 | -122.199 | 121.9411 | 122.212 | 122.1419 | 0.5452 | -122.2589
2299.2344 | 122.2961 | -0.07782 | 122.1039 | -0.01778 | -0.043487 | 0.041575 | 0.022888 | -0.011651 | -0.0050809 | -0.021518 | -0.002053 | -0.0025041 | 0.058901 | 0.040901 | 0.049183 | -0.017266 | 0.010564 | -0.012988 | 0.056706 | 0.055306 | 0.14197 | -0.099689 | 0.060571 | 0.41702 | -0.047194 | 121.8267 | 122.0884 | 122.0046 | -0.15041 | -0.021869 | -122.0472 | 0.060554 | 0.064832 | 0.086701 | -122.0486 | -121.9619 | -0.072592 | -0.27719 | 0.13839 | 0.030626 | 0.10322 | -0.015475 | -0.099267 | 0.13453 | 0.13313 | 0.21979 | 0.088384 | -122.2036 | 121.9045 | 122.1662 | 122.0824 | 0.49484 | -122.2543
2300.9375 | 122.3145 | -0.09613 | 122.081 | -0.010149 | -0.043701 | 0.041575 | 0.022888 | -0.012292 | -0.0055083 | -0.029148 | -0.002053 | -0.0022903 | 0.059114 | 0.040688 | 0.048969 | -0.017266 | 0.010564 | -0.008409 | 0.047549 | 0.050727 | 0.14197 | -0.081373 | 0.069728 | 0.41702 | -0.051772 | 121.8221 | 122.093 | 122.0138 | -0.15041 | 0.014757 | -122.0334 | 0.078864 | 0.087721 | 0.072964 | -122.0303 | -121.939 | -0.054282 | -0.25888 | 0.16586 | 0.044358 | 0.09864 | 0.011991 | -0.067222 | 0.14368 | 0.14686 | 0.2381 | 0.10669 | -122.1624 | 121.9182 | 122.1891 | 122.1099 | 0.51315 | -122.2314
2302.6875 | 122.2092 | -0.1236 | 122.1176 | -0.010149 | -0.044128 | 0.041362 | 0.023101 | -0.011865 | -0.0052945 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.040901 | 0.049397 | -0.012688 | 0.005985 | -0.008409 | 0.052128 | 0.059885 | 0.14197 | -0.085952 | 0.069728 | 0.42618 | -0.056351 | 121.8267 | 122.093 | 122.0184 | -0.14583 | 0.037644 | -122.0655 | 0.11091 | 0.11519 | 0.077543 | -122.0577 | -121.9756 | -0.022237 | -0.29092 | 0.19332 | 0.067245 | 0.089482 | -0.02463 | -0.099264 | 0.17572 | 0.18348 | 0.26556 | 0.12958 | -122.2036 | 121.9503 | 122.2166 | 122.1419 | 0.54978 | -122.2634
2304.4531 | 122.2092 | -0.13275 | 122.1268 | -0.0025182 | -0.043701 | 0.041362 | 0.023315 | -0.011651 | -0.0052945 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.040688 | 0.049397 | -0.021844 | 0.005985 | -0.008409 | 0.061284 | 0.059885 | 0.14655 | -0.090531 | 0.069728 | 0.4216 | -0.047194 | 121.8267 | 122.093 | 122.0229 | -0.15499 | 0.04222 | -122.0655 | 0.11091 | 0.12434 | 0.082122 | -122.0669 | -121.9802 | -0.02224 | -0.30007 | 0.20248 | 0.085557 | 0.1078 | -0.033785 | -0.10384 | 0.19404 | 0.19264 | 0.2793 | 0.13874 | -122.2173 | 121.9594 | 122.2257 | 122.1557 | 0.55435 | -122.2818
2306.2031 | 122.2275 | -0.1236 | 122.1313 | -0.01778 | -0.043487 | 0.041148 | 0.022888 | -0.011865 | -0.0055083 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.041115 | 0.049397 | -0.017266 | 0.005985 | -0.012988 | 0.052128 | 0.050727 | 0.13739 | -0.085952 | 0.06515 | 0.4216 | -0.051772 | 121.8313 | 122.093 | 122.0229 | -0.15499 | 0.037644 | -122.0792 | 0.10633 | 0.11061 | 0.072964 | -122.0806 | -121.994 | -0.031395 | -0.30007 | 0.18875 | 0.071824 | 0.10322 | -0.038363 | -0.10842 | 0.17572 | 0.17432 | 0.26098 | 0.12958 | -122.2173 | 121.9549 | 122.2166 | 122.1465 | 0.5452 | -122.2863
2307.9531 | 122.2275 | -0.12817 | 122.1313 | -0.0025182 | -0.043701 | 0.041575 | 0.022674 | -0.011865 | -0.0052945 | -0.0062567 | -0.002053 | -0.0020767 | 0.059114 | 0.040901 | 0.04961 | -0.012688 | 0.005985 | -0.012988 | 0.061284 | 0.055306 | 0.14655 | -0.081373 | 0.060571 | 0.41702 | -0.047194 | 121.8313 | 122.0976 | 122.0184 | -0.14583 | 0.046801 | -122.0701 | 0.11549 | 0.11519 | 0.068385 | -122.076 | -121.9848 | -0.017659 | -0.30007 | 0.18874 | 0.08098 | 0.098639 | -0.033784 | -0.113 | 0.18946 | 0.18348 | 0.27472 | 0.13416 | -122.2127 | 121.9594 | 122.2257 | 122.1465 | 0.5452 | -122.2772
2309.6406 | 122.2504 | -0.091553 | 122.1268 | -0.01778 | -0.043701 | 0.041362 | 0.022888 | -0.011651 | -0.0050809 | -0.021518 | -0.0022666 | -0.0022903 | 0.058901 | 0.040688 | 0.049397 | -0.026423 | 0.005985 | -0.017566 | 0.052128 | 0.055306 | 0.14197 | -0.090531 | 0.074307 | 0.41244 | -0.051772 | 121.8267 | 122.0976 | 122.0184 | -0.15041 | 0.001022 | -122.0746 | 0.06513 | 0.073987 | 0.072965 | -122.0715 | -121.9848 | -0.058859 | -0.30007 | 0.16586 | 0.039781 | 0.09864 | -0.029206 | -0.10842 | 0.14368 | 0.14686 | 0.23352 | 0.097538 | -122.2173 | 121.9182 | 122.1891 | 122.1099 | 0.504 | -122.2772
2311.3906 | 122.3373 | -0.068665 | 122.0718 | -0.010149 | -0.043914 | 0.041362 | 0.023101 | -0.011865 | -0.0052945 | -0.021518 | -0.0016258 | -0.0022903 | 0.059114 | 0.040901 | 0.049183 | -0.021844 | 0.015142 | -0.008409 | 0.056706 | 0.059885 | 0.13739 | -0.085952 | 0.069728 | 0.42618 | -0.051772 | 121.8313 | 122.0976 | 122.0138 | -0.15041 | -0.017287 | -122.0151 | 0.046821 | 0.060256 | 0.077543 | -122.012 | -121.9345 | -0.081747 | -0.24056 | 0.13839 | 0.016893 | 0.09864 | 0.025726 | -0.058066 | 0.12537 | 0.12855 | 0.20605 | 0.083807 | -122.1578 | 121.8999 | 122.1662 | 122.0824 | 0.49484 | -122.2223
2313.1406 | 122.2595 | -0.09613 | 122.1313 | -0.010149 | -0.043914 | 0.041575 | 0.022888 | -0.012078 | -0.0052945 | -0.021518 | -0.002053 | -0.0022903 | 0.059328 | 0.041115 | 0.048969 | -0.021844 | 0.005985 | -0.012988 | 0.052128 | 0.059885 | 0.14655 | -0.085952 | 0.06515 | 0.4216 | -0.056351 | 121.8313 | 122.093 | 122.0275 | -0.15041 | 0.010178 | -122.0792 | 0.074286 | 0.083142 | 0.072964 | -122.0715 | -121.9848 | -0.054282 | -0.30007 | 0.16128 | 0.039779 | 0.094061 | -0.038363 | -0.10384 | 0.14826 | 0.15601 | 0.24268 | 0.10211 | -122.2173 | 121.9274 | 122.1891 | 122.1236 | 0.51773 | -122.2818
2314.8438 | 122.2229 | -0.1236 | 122.1268 | -0.0025182 | -0.043701 | 0.040934 | 0.022888 | -0.011651 | -0.0057219 | -0.013887 | -0.0022666 | -0.0020767 | 0.058687 | 0.040688 | 0.049183 | -0.021844 | 0.015142 | -0.017566 | 0.052128 | 0.055306 | 0.14197 | -0.090531 | 0.069728 | 0.4216 | -0.047194 | 121.8267 | 122.0976 | 122.0138 | -0.14583 | 0.033065 | -122.0746 | 0.10175 | 0.10603 | 0.072965 | -122.0715 | -121.9848 | -0.022237 | -0.30007 | 0.19332 | 0.076402 | 0.098639 | -0.029206 | -0.113 | 0.17572 | 0.1789 | 0.26556 | 0.13874 | -122.2173 | 121.9503 | 122.2212 | 122.1374 | 0.5452 | -122.2726
2316.5938 | 122.3557 | -0.073242 | 122.0718 | -0.0025182 | -0.043487 | 0.041362 | 0.022888 | -0.012078 | -0.0050809 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.040901 | 0.049397 | -0.021844 | 0.015142 | -0.017566 | 0.061284 | 0.059885 | 0.14197 | -0.085952 | 0.069728 | 0.41702 | -0.051772 | 121.8313 | 122.093 | 122.0275 | -0.14583 | -0.01271 | -122.0106 | 0.051398 | 0.055676 | 0.068386 | -122.012 | -121.9299 | -0.072591 | -0.24056 | 0.14297 | 0.02147 | 0.094061 | 0.021147 | -0.04433 | 0.13453 | 0.13313 | 0.21521 | 0.088384 | -122.1578 | 121.9045 | 122.1662 | 122.1007 | 0.49026 | -122.2177
2318.3438 | 122.2275 | -0.14191 | 122.1313 | -0.010149 | -0.043914 | 0.041148 | 0.022888 | -0.012078 | -0.0052945 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058901 | 0.040901 | 0.049397 | -0.021844 | 0.015142 | -0.017566 | 0.052128 | 0.059885 | 0.14655 | -0.085952 | 0.074307 | 0.4216 | -0.047194 | 121.8313 | 122.1021 | 122.0275 | -0.15957 | 0.055955 | -122.0792 | 0.12006 | 0.12434 | 0.068386 | -122.0715 | -121.9848 | -0.017663 | -0.30007 | 0.21621 | 0.094713 | 0.11238 | -0.029205 | -0.10384 | 0.19404 | 0.20179 | 0.28845 | 0.15705 | -122.2173 | 121.9732 | 122.2441 | 122.1694 | 0.56351 | -122.2909
2320.1094 | 122.2275 | -0.10529 | 122.1176 | -0.0025182 | -0.043701 | 0.041362 | 0.022674 | -0.012292 | -0.0055083 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.040688 | 0.049183 | -0.021844 | 0.010564 | -0.008409 | 0.056706 | 0.059885 | 0.14197 | -0.090531 | 0.074307 | 0.41702 | -0.047194 | 121.8313 | 122.1067 | 122.0229 | -0.15041 | 0.014755 | -122.0609 | 0.083442 | 0.096877 | 0.082122 | -122.0577 | -121.9756 | -0.045126 | -0.28634 | 0.17959 | 0.058092 | 0.10322 | -0.010894 | -0.094686 | 0.16199 | 0.16517 | 0.24725 | 0.11585 | -122.2081 | 121.9366 | 122.212 | 122.1282 | 0.52231 | -122.268
2321.8125 | 122.2687 | -0.11444 | 122.1176 | -0.010149 | -0.043914 | 0.041148 | 0.022888 | -0.012078 | -0.0052945 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.040901 | 0.049183 | -0.017266 | 0.010564 | -0.012988 | 0.056706 | 0.055306 | 0.14197 | -0.085952 | 0.06515 | 0.4216 | -0.047194 | 121.8404 | 122.1021 | 122.0229 | -0.15041 | 0.028489 | -122.0609 | 0.097175 | 0.10145 | 0.072964 | -122.0623 | -121.9756 | -0.035971 | -0.27718 | 0.17959 | 0.067247 | 0.10322 | -0.015472 | -0.094686 | 0.17115 | 0.16975 | 0.25641 | 0.12501 | -122.2036 | 121.9549 | 122.2166 | 122.1374 | 0.53604 | -122.268
2323.5625 | 122.2275 | -0.11902 | 122.1542 | -0.010149 | -0.043914 | 0.041575 | 0.022888 | -0.012078 | -0.0052945 | -0.021518 | -0.002053 | -0.0025041 | 0.058901 | 0.040901 | 0.049183 | -0.031001 | 0.001407 | -0.017566 | 0.061284 | 0.055306 | 0.14655 | -0.085952 | 0.06515 | 0.41702 | -0.051772 | 121.8359 | 122.1021 | 122.0229 | -0.15499 | 0.033067 | -122.093 | 0.088018 | 0.10145 | 0.068386 | -122.0989 | -122.0077 | -0.035972 | -0.31838 | 0.18417 | 0.067247 | 0.10322 | -0.052093 | -0.13131 | 0.1803 | 0.17433 | 0.26556 | 0.12043 | -122.2402 | 121.9549 | 122.2212 | 122.1419 | 0.53604 | -122.3092
2325.2656 | 122.3557 | -0.068665 | 122.0856 | -0.01778 | -0.044128 | 0.041575 | 0.022674 | -0.011437 | -0.0052945 | -0.021518 | -0.002053 | -0.0020767 | 0.058473 | 0.040901 | 0.049183 | -0.017266 | 0.010564 | -0.012988 | 0.056706 | 0.059885 | 0.15112 | -0.085952 | 0.074307 | 0.41702 | -0.047194 | 121.8359 | 122.1021 | 122.0184 | -0.15041 | -0.017287 | -122.0289 | 0.051399 | 0.055677 | 0.072964 | -122.0257 | -121.9344 | -0.081747 | -0.24972 | 0.14297 | 0.021471 | 0.10322 | 0.016572 | -0.06722 | 0.12537 | 0.12855 | 0.21979 | 0.079229 | -122.1715 | 121.9045 | 122.1708 | 122.087 | 0.48569 | -122.236
2327.0156 | 122.2733 | -0.1236 | 122.1405 | -0.010149 | -0.044128 | 0.041575 | 0.022888 | -0.011865 | -0.0050809 | -0.021518 | -0.0022666 | -0.0022903 | 0.059114 | 0.040901 | 0.049183 | -0.021844 | 0.010564 | -0.012988 | 0.052128 | 0.055306 | 0.15112 | -0.09511 | 0.074307 | 0.4216 | -0.051772 | 121.8404 | 122.0976 | 122.0229 | -0.14583 | 0.028486 | -122.0884 | 0.10175 | 0.11061 | 0.082122 | -122.0852 | -121.9894 | -0.022237 | -0.30007 | 0.1979 | 0.071824 | 0.094061 | -0.042939 | -0.11757 | 0.17572 | 0.1789 | 0.27472 | 0.13416 | -122.2356 | 121.964 | 122.2212 | 122.1465 | 0.5452 | -122.2863
2328.7812 | 122.2275 | -0.12817 | 122.1588 | -0.01778 | -0.044128 | 0.041575 | 0.022888 | -0.011651 | -0.0052945 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.041115 | 0.048969 | -0.021844 | 0.010564 | -0.012988 | 0.047549 | 0.055306 | 0.14197 | -0.081373 | 0.069728 | 0.4216 | -0.051772 | 121.8404 | 122.1021 | 122.0275 | -0.14583 | 0.046801 | -122.1113 | 0.10633 | 0.11519 | 0.068385 | -122.1035 | -122.0168 | -0.017659 | -0.31838 | 0.1979 | 0.076402 | 0.094061 | -0.05667 | -0.1313 | 0.17572 | 0.18348 | 0.27014 | 0.13874 | -122.2402 | 121.9686 | 122.2303 | 122.1557 | 0.54977 | -122.3046
2330.5312 | 122.2641 | -0.1236 | 122.1451 | -0.010149 | -0.044128 | 0.041575 | 0.022888 | -0.011651 | -0.0057219 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.041115 | 0.049183 | -0.026423 | 0.015142 | -0.012988 | 0.056706 | 0.059885 | 0.14655 | -0.085952 | 0.074307 | 0.4216 | -0.047194 | 121.8313 | 122.1067 | 122.0275 | -0.15041 | 0.037644 | -122.0884 | 0.097173 | 0.11061 | 0.072964 | -122.0852 | -121.9985 | -0.026816 | -0.31381 | 0.1979 | 0.076402 | 0.10322 | -0.03836 | -0.11757 | 0.1803 | 0.18348 | 0.27014 | 0.13874 | -122.231 | 121.9549 | 122.2303 | 122.1511 | 0.5452 | -122.2955
2332.2812 | 122.3007 | -0.082397 | 122.1085 | -0.010149 | -0.043914 | 0.041575 | 0.022888 | -0.011865 | -0.0052945 | -0.021518 | -0.0024804 | -0.0022903 | 0.059114 | 0.041115 | 0.049183 | -0.017266 | 0.005985 | -0.022144 | 0.061284 | 0.059885 | 0.15112 | -0.081373 | 0.06515 | 0.4216 | -0.051772 | 121.8359 | 122.1113 | 122.0275 | -0.14583 | 0.001024 | -122.0472 | 0.065131 | 0.060253 | 0.059229 | -122.0486 | -121.9573 | -0.063436 | -0.27261 | 0.14755 | 0.030625 | 0.094061 | 0.002841 | -0.080951 | 0.14368 | 0.14228 | 0.23352 | 0.088382 | -122.1898 | 121.9182 | 122.1937 | 122.1099 | 0.504 | -122.2543
2333.9688 | 122.3053 | -0.064087 | 122.113 | -0.010149 | -0.044128 | 0.041789 | 0.022247 | -0.011437 | -0.0055083 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.040688 | 0.049397 | -0.017266 | 0.010564 | -0.017566 | 0.052128 | 0.064464 | 0.14197 | -0.081373 | 0.06515 | 0.4216 | -0.038036 | 121.8404 | 122.0976 | 122.0184 | -0.14125 | -0.017286 | -122.0609 | 0.046821 | 0.046521 | 0.063807 | -122.0486 | -121.9711 | -0.077168 | -0.27261 | 0.12924 | 0.026051 | 0.10322 | -0.015473 | -0.094686 | 0.11622 | 0.12855 | 0.20605 | 0.074651 | -122.1944 | 121.9045 | 122.1617 | 122.0824 | 0.48569 | -122.2543
2335.7344 | 122.2458 | -0.12817 | 122.1588 | -0.010149 | -0.044342 | 0.041575 | 0.023101 | -0.012078 | -0.0052945 | -0.021518 | -0.002053 | -0.0025041 | 0.058687 | 0.040688 | 0.049397 | -0.021844 | 0.015142 | -0.022144 | 0.052128 | 0.059885 | 0.14197 | -0.085952 | 0.069728 | 0.41702 | -0.047194 | 121.8404 | 122.1113 | 122.0321 | -0.14583 | 0.042222 | -122.1067 | 0.10633 | 0.10603 | 0.063808 | -122.0989 | -122.0168 | -0.017659 | -0.31838 | 0.1979 | 0.08098 | 0.098639 | -0.047513 | -0.12673 | 0.1803 | 0.18806 | 0.27014 | 0.14332 | -122.2448 | 121.9686 | 122.2395 | 122.1603 | 0.5452 | -122.3046
2337.4844 | 122.2961 | -0.09613 | 122.1085 | -0.010149 | -0.044128 | 0.041362 | 0.022888 | -0.011865 | -0.0055083 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.040901 | 0.049397 | -0.021844 | 0.0243 | -0.012988 | 0.052128 | 0.059885 | 0.14655 | -0.085952 | 0.06515 | 0.4216 | -0.047194 | 121.8359 | 122.1067 | 122.0275 | -0.15499 | 0.010178 | -122.0563 | 0.074286 | 0.083142 | 0.072964 | -122.0486 | -121.9619 | -0.058861 | -0.27261 | 0.16128 | 0.048936 | 0.1078 | -0.001738 | -0.080951 | 0.14826 | 0.15601 | 0.24268 | 0.12043 | -122.1944 | 121.932 | 122.2029 | 122.1236 | 0.51773 | -122.2634
2339.2344 | 122.2412 | -0.1236 | 122.1405 | -0.0025182 | -0.043914 | 0.041789 | 0.023101 | -0.011865 | -0.0055083 | -0.029148 | -0.0018394 | -0.0020767 | 0.058901 | 0.040901 | 0.048969 | -0.021844 | 0.005985 | -0.012988 | 0.052128 | 0.055306 | 0.15112 | -0.081373 | 0.06515 | 0.4216 | -0.042615 | 121.8359 | 122.1067 | 122.0321 | -0.14583 | 0.042223 | -122.0884 | 0.10175 | 0.11061 | 0.068385 | -122.0852 | -121.9894 | -0.022237 | -0.30465 | 0.18875 | 0.080981 | 0.10322 | -0.033782 | -0.10842 | 0.17572 | 0.1789 | 0.27472 | 0.12958 | -122.2219 | 121.9594 | 122.2303 | 122.1557 | 0.5452 | -122.2863
2340.9375 | 122.2275 | -0.1236 | 122.1222 | -0.010149 | -0.044342 | 0.041575 | 0.022888 | -0.012292 | -0.0052945 | -0.013887 | -0.002053 | -0.0020767 | 0.059114 | 0.040901 | 0.049183 | -0.017266 | 0.005985 | -0.022144 | 0.052128 | 0.059885 | 0.13281 | -0.090531 | 0.069728 | 0.41702 | -0.047194 | 121.8496 | 122.1067 | 122.0275 | -0.14583 | 0.033065 | -122.0701 | 0.10633 | 0.10145 | 0.068387 | -122.0623 | -121.9894 | -0.022237 | -0.2726 | 0.19332 | 0.076402 | 0.098639 | -0.015471 | -0.094684 | 0.17572 | 0.18348 | 0.2564 | 0.12958 | -122.2127 | 121.9732 | 122.2303 | 122.1511 | 0.54062 | -122.268
2342.6875 | 122.2961 | -0.086975 | 122.1176 | -0.025411 | -0.043914 | 0.041575 | 0.022674 | -0.011865 | -0.0052945 | -0.013887 | -0.002053 | -0.0025041 | 0.058901 | 0.041329 | 0.049397 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.059885 | 0.14655 | -0.081373 | 0.06515 | 0.41702 | -0.047194 | 121.845 | 122.1159 | 122.0275 | -0.15041 | 0.005602 | -122.0609 | 0.065131 | 0.073987 | 0.068385 | -122.0577 | -121.9711 | -0.063437 | -0.27261 | 0.15213 | 0.039781 | 0.10322 | -0.001737 | -0.090107 | 0.14368 | 0.14686 | 0.23352 | 0.097539 | -122.199 | 121.932 | 122.2029 | 122.1145 | 0.504 | -122.268
2344.4375 | 122.3465 | -0.068665 | 122.081 | -0.01778 | -0.044128 | 0.041362 | 0.022888 | -0.011865 | -0.0052945 | -0.021518 | -0.002053 | -0.0020767 | 0.058901 | 0.040901 | 0.048969 | -0.021844 | 0.019721 | -0.012988 | 0.056706 | 0.064464 | 0.14197 | -0.081373 | 0.069728 | 0.4216 | -0.047194 | 121.8404 | 122.1067 | 122.0367 | -0.15041 | -0.012708 | -122.0243 | 0.046821 | 0.055677 | 0.068385 | -122.0165 | -121.939 | -0.081747 | -0.24056 | 0.13839 | 0.021471 | 0.10322 | 0.025727 | -0.044329 | 0.12537 | 0.13313 | 0.21063 | 0.088386 | -122.1624 | 121.9091 | 122.1754 | 122.1053 | 0.49026 | -122.2314
2346.2188 | 122.2733 | -0.1236 | 122.1405 | -0.025411 | -0.044128 | 0.041362 | 0.022674 | -0.011651 | -0.0052945 | -0.013887 | -0.0022666 | -0.0022903 | 0.058687 | 0.040901 | 0.048969 | -0.026423 | 0.005985 | -0.012988 | 0.056706 | 0.059885 | 0.14197 | -0.085952 | 0.074307 | 0.41702 | -0.047194 | 121.845 | 122.1205 | 122.0275 | -0.15041 | 0.037644 | -122.0838 | 0.097173 | 0.11061 | 0.072964 | -122.0806 | -121.9985 | -0.026816 | -0.29549 | 0.1979 | 0.076402 | 0.10322 | -0.020046 | -0.11299 | 0.1803 | 0.18348 | 0.26556 | 0.12958 | -122.2265 | 121.9686 | 122.2441 | 122.1511 | 0.54062 | -122.2909
2347.9062 | 122.2412 | -0.12817 | 122.113 | -0.0025182 | -0.043914 | 0.041575 | 0.022674 | -0.011651 | -0.0052945 | -0.021518 | -0.0022666 | -0.0020767 | 0.058901 | 0.041115 | 0.049183 | -0.017266 | 0.005985 | -0.017566 | 0.052128 | 0.059885 | 0.14197 | -0.081373 | 0.074307 | 0.41702 | -0.047194 | 121.845 | 122.1159 | 122.0367 | -0.14583 | 0.046801 | -122.0609 | 0.11091 | 0.11061 | 0.063807 | -122.0532 | -121.9711 | -0.017659 | -0.26803 | 0.20248 | 0.08098 | 0.098639 | 0.002841 | -0.076372 | 0.1803 | 0.18806 | 0.27014 | 0.13416 | -122.1944 | 121.9732 | 122.2441 | 122.1648 | 0.5452 | -122.2589
2349.6406 | 122.3602 | -0.054932 | 122.1222 | -0.010149 | -0.043914 | 0.041148 | 0.02246 | -0.012078 | -0.0052945 | -0.029148 | -0.002053 | -0.0025041 | 0.059114 | 0.041115 | 0.049183 | -0.026423 | 0.015142 | -0.012988 | 0.056706 | 0.059885 | 0.15112 | -0.09511 | 0.069728 | 0.42618 | -0.051772 | 121.8496 | 122.125 | 122.0275 | -0.15041 | -0.040178 | -122.0655 | 0.028509 | 0.041944 | 0.082122 | -122.0623 | -121.9711 | -0.09548 | -0.2726 | 0.12466 | 0.00316 | 0.09864 | 0.002844 | -0.094684 | 0.11164 | 0.11482 | 0.20606 | 0.070074 | -122.2173 | 121.9045 | 122.18 | 122.0824 | 0.48111 | -122.2726
2351.3906 | 122.2412 | -0.09613 | 122.1359 | -0.010149 | -0.043914 | 0.041362 | 0.022888 | -0.011651 | -0.0052945 | -0.029148 | -0.002053 | -0.0020767 | 0.058687 | 0.041115 | 0.049183 | -0.017266 | 0.005985 | -0.008409 | 0.056706 | 0.055306 | 0.14655 | -0.085952 | 0.06515 | 0.4216 | -0.042615 | 121.845 | 122.1113 | 122.0275 | -0.14583 | 0.010178 | -122.0792 | 0.078864 | 0.087721 | 0.077543 | -122.0806 | -121.9894 | -0.049703 | -0.29092 | 0.16128 | 0.053515 | 0.10322 | -0.024625 | -0.10842 | 0.15284 | 0.15144 | 0.24268 | 0.10211 | -122.2219 | 121.9411 | 122.2074 | 122.1236 | 0.51773 | -122.2818
2353.1406 | 122.3648 | -0.068665 | 122.1176 | -0.010149 | -0.043914 | 0.041148 | 0.02246 | -0.011865 | -0.0052945 | -0.013887 | -0.0018394 | -0.0025041 | 0.058473 | 0.041115 | 0.049397 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.064464 | 0.14655 | -0.085952 | 0.074307 | 0.4216 | -0.042615 | 121.8542 | 122.125 | 122.0321 | -0.15499 | -0.017287 | -122.0609 | 0.046821 | 0.055677 | 0.072964 | -122.0532 | -121.9711 | -0.086326 | -0.26345 | 0.14297 | 0.02605 | 0.11238 | 0.007421 | -0.085529 | 0.12537 | 0.13313 | 0.21521 | 0.079229 | -122.2036 | 121.9228 | 122.1937 | 122.1008 | 0.49026 | -122.2726
2354.8438 | 122.2321 | -0.1236 | 122.1497 | -0.010149 | -0.043914 | 0.041148 | 0.02246 | -0.011865 | -0.0055083 | -0.013887 | -0.002053 | -0.0022903 | 0.059328 | 0.041115 | 0.048969 | -0.017266 | 0.0243 | -0.012988 | 0.061284 | 0.050727 | 0.14197 | -0.081373 | 0.069728 | 0.41244 | -0.047194 | 121.845 | 122.1205 | 122.0412 | -0.15499 | 0.042223 | -122.0884 | 0.10633 | 0.11061 | 0.068385 | -122.0989 | -122.0077 | -0.031395 | -0.30465 | 0.19332 | 0.076402 | 0.1078 | -0.029201 | -0.10841 | 0.18488 | 0.17432 | 0.26556 | 0.1479 | -122.231 | 121.9686 | 122.2441 | 122.1648 | 0.53604 | -122.3046
2356.5938 | 122.319 | -0.07782 | 122.1176 | -0.010149 | -0.044342 | 0.041362 | 0.02246 | -0.011651 | -0.0055083 | -0.0062567 | -0.0022666 | -0.0020767 | 0.058901 | 0.041329 | 0.048969 | -0.026423 | 0.010564 | -0.017566 | 0.052128 | 0.059885 | 0.14655 | -0.081373 | 0.074307 | 0.42618 | -0.047194 | 121.8542 | 122.125 | 122.0367 | -0.14125 | -0.003553 | -122.0655 | 0.051397 | 0.060254 | 0.063807 | -122.0577 | -121.9711 | -0.063435 | -0.26345 | 0.15213 | 0.030626 | 0.094061 | 0.007421 | -0.08095 | 0.12995 | 0.1377 | 0.22437 | 0.088384 | -122.199 | 121.932 | 122.2029 | 122.1145 | 0.504 | -122.2589
2358.3594 | 122.3236 | -0.082397 | 122.1039 | -0.01778 | -0.043914 | 0.041362 | 0.022674 | -0.012078 | -0.0052945 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.041115 | 0.049183 | -0.017266 | 0.010564 | -0.017566 | 0.061284 | 0.064464 | 0.15112 | -0.081373 | 0.078886 | 0.43076 | -0.042615 | 121.845 | 122.1205 | 122.0321 | -0.14583 | 0.001024 | -122.0426 | 0.065131 | 0.064831 | 0.063807 | -122.0394 | -121.9528 | -0.063436 | -0.25887 | 0.16128 | 0.039782 | 0.10322 | 0.016575 | -0.071796 | 0.14368 | 0.14686 | 0.23352 | 0.092961 | -122.1853 | 121.9274 | 122.2029 | 122.1145 | 0.51316 | -122.2497
2360.125 | 122.3511 | -0.082397 | 122.1039 | -0.01778 | -0.044342 | 0.041789 | 0.022247 | -0.012078 | -0.0052945 | -0.021518 | -0.0022666 | -0.0020767 | 0.058901 | 0.041329 | 0.048756 | -0.012688 | 0.015142 | -0.017566 | 0.052128 | 0.059885 | 0.14197 | -0.081373 | 0.06515 | 0.41702 | -0.047194 | 121.8496 | 122.1205 | 122.0412 | -0.14125 | 0.001024 | -122.0518 | 0.069709 | 0.064831 | 0.063807 | -122.044 | -121.9619 | -0.058858 | -0.25429 | 0.14755 | 0.035203 | 0.094061 | 0.016575 | -0.062638 | 0.13453 | 0.14228 | 0.22436 | 0.097539 | -122.1853 | 121.932 | 122.2029 | 122.1236 | 0.49942 | -122.2451
2361.8125 | 122.3648 | -0.073242 | 122.1085 | -0.0025182 | -0.044342 | 0.041362 | 0.022247 | -0.011651 | -0.0052945 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.041329 | 0.048969 | -0.017266 | 0.010564 | -0.017566 | 0.061284 | 0.055306 | 0.14655 | -0.085952 | 0.074307 | 0.43076 | -0.047194 | 121.845 | 122.1159 | 122.0412 | -0.14583 | -0.01271 | -122.0472 | 0.055976 | 0.055676 | 0.068386 | -122.0532 | -121.9619 | -0.072591 | -0.26345 | 0.14755 | 0.026048 | 0.098639 | 0.007419 | -0.067215 | 0.13453 | 0.12855 | 0.21979 | 0.083806 | -122.1944 | 121.9183 | 122.1891 | 122.1145 | 0.504 | -122.2543
2363.5625 | 122.2824 | -0.091553 | 122.1634 | -0.010149 | -0.044128 | 0.041362 | 0.022674 | -0.011865 | -0.0052945 | -0.029148 | -0.0022666 | -0.0025041 | 0.059114 | 0.041329 | 0.04961 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.059885 | 0.15112 | -0.085952 | 0.069728 | 0.4216 | -0.047194 | 121.8496 | 122.1205 | 122.0412 | -0.15041 | 0.005601 | -122.1067 | 0.069709 | 0.078565 | 0.072964 | -122.1035 | -122.0123 | -0.058859 | -0.3138 | 0.16128 | 0.044359 | 0.10322 | -0.042934 | -0.12215 | 0.14826 | 0.15144 | 0.24268 | 0.10212 | -122.2493 | 121.9411 | 122.212 | 122.1328 | 0.51315 | -122.3138
2365.3281 | 122.3602 | -0.07782 | 122.1176 | 0.0051128 | -0.044128 | 0.041575 | 0.02246 | -0.011865 | -0.0050809 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.041115 | 0.049183 | -0.021844 | 0.005985 | -0.012988 | 0.056706 | 0.059885 | 0.15112 | -0.076794 | 0.06515 | 0.42618 | -0.047194 | 121.845 | 122.125 | 122.0321 | -0.15041 | 0.001026 | -122.0609 | 0.055976 | 0.064832 | 0.063806 | -122.0577 | -121.9665 | -0.072592 | -0.27261 | 0.14297 | 0.030626 | 0.10322 | 0.007421 | -0.085529 | 0.13453 | 0.1377 | 0.22894 | 0.083805 | -122.1944 | 121.9228 | 122.2029 | 122.1099 | 0.504 | -122.268
2367.0781 | 122.3694 | -0.064087 | 122.1039 | -0.01778 | -0.044555 | 0.041362 | 0.022674 | -0.011865 | -0.0052945 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.041329 | 0.048969 | -0.021844 | 0.010564 | -0.017566 | 0.061284 | 0.064464 | 0.14655 | -0.085952 | 0.074307 | 0.4216 | -0.042615 | 121.8587 | 122.125 | 122.0412 | -0.14583 | -0.021865 | -122.0426 | 0.042243 | 0.046521 | 0.068386 | -122.0394 | -121.9573 | -0.081746 | -0.24514 | 0.13839 | 0.021472 | 0.10322 | 0.021154 | -0.062638 | 0.12537 | 0.12855 | 0.21063 | 0.074651 | -122.1898 | 121.9228 | 122.1891 | 122.1053 | 0.48569 | -122.2497
2368.7812 | 122.2961 | -0.086975 | 122.1039 | -0.010149 | -0.044342 | 0.041362 | 0.02246 | -0.011651 | -0.0048673 | -0.021518 | -0.0016258 | -0.0022903 | 0.059114 | 0.041115 | 0.048969 | -0.017266 | 0.015142 | -0.022144 | 0.056706 | 0.064464 | 0.14655 | -0.085952 | 0.069728 | 0.41702 | -0.047194 | 121.8542 | 122.125 | 122.0367 | -0.14583 | 0.001023 | -122.0472 | 0.069709 | 0.064831 | 0.063808 | -122.0394 | -121.9573 | -0.058858 | -0.24972 | 0.1567 | 0.039781 | 0.098639 | 0.021154 | -0.067217 | 0.14368 | 0.15144 | 0.23352 | 0.10212 | -122.1898 | 121.9411 | 122.212 | 122.1236 | 0.504 | -122.2497
2370.5312 | 122.3465 | -0.045776 | 122.1222 | -0.01778 | -0.044342 | 0.041575 | 0.02246 | -0.012292 | -0.0052945 | -0.013887 | -0.0022666 | -0.0022903 | 0.059114 | 0.041115 | 0.049183 | -0.026423 | 0.015142 | -0.012988 | 0.047549 | 0.064464 | 0.14655 | -0.081373 | 0.069728 | 0.42618 | -0.047194 | 121.8587 | 122.1296 | 122.0458 | -0.15041 | -0.035597 | -122.0746 | 0.019353 | 0.032788 | 0.068385 | -122.0577 | -121.9756 | -0.10464 | -0.26345 | 0.1155 | -0.001418 | 0.10322 | 0.007422 | -0.07637 | 0.093325 | 0.11024 | 0.19232 | 0.060918 | -122.2036 | 121.9045 | 122.1754 | 122.0916 | 0.47195 | -122.2726
2372.2188 | 122.2641 | -0.091553 | 122.1268 | -0.0025182 | -0.044555 | 0.041362 | 0.02246 | -0.012292 | -0.0052945 | -0.021518 | -0.0018394 | -0.0025041 | 0.058901 | 0.041329 | 0.048969 | -0.021844 | 0.015142 | -0.017566 | 0.056706 | 0.064464 | 0.16028 | -0.081373 | 0.074307 | 0.4216 | -0.051772 | 121.8496 | 122.125 | 122.0367 | -0.14125 | 0.01018 | -122.0701 | 0.069709 | 0.073987 | 0.063807 | -122.0623 | -121.9665 | -0.049702 | -0.27718 | 0.16586 | 0.039781 | 0.089483 | -0.001734 | -0.090105 | 0.14826 | 0.15602 | 0.25183 | 0.10669 | -122.2081 | 121.9411 | 122.2166 | 122.1282 | 0.51315 | -122.268
2373.9688 | 122.2458 | -0.09613 | 122.168 | -0.0025182 | -0.044342 | 0.041362 | 0.022247 | -0.011865 | -0.0055083 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.041329 | 0.048969 | -0.021844 | 0.010564 | -0.012988 | 0.042971 | 0.055306 | 0.15112 | -0.081373 | 0.074307 | 0.42618 | -0.042615 | 121.8633 | 122.125 | 122.0458 | -0.14583 | 0.014757 | -122.125 | 0.074286 | 0.083142 | 0.068385 | -122.1127 | -122.0168 | -0.049703 | -0.30465 | 0.17044 | 0.053515 | 0.10322 | -0.042933 | -0.12215 | 0.1391 | 0.15144 | 0.24725 | 0.10669 | -122.2493 | 121.9595 | 122.2212 | 122.142 | 0.52231 | -122.3138
2375.7188 | 122.3465 | -0.059509 | 122.1222 | -0.01778 | -0.043914 | 0.041362 | 0.02246 | -0.011651 | -0.0052945 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.041115 | 0.048756 | -0.017266 | 0.010564 | -0.012988 | 0.056706 | 0.059885 | 0.14655 | -0.081373 | 0.074307 | 0.43076 | -0.042615 | 121.8542 | 122.1205 | 122.0504 | -0.14583 | -0.021864 | -122.0655 | 0.042243 | 0.046521 | 0.068385 | -122.0623 | -121.9756 | -0.086324 | -0.26803 | 0.13382 | 0.016894 | 0.10322 | -0.001735 | -0.071791 | 0.11621 | 0.11939 | 0.20605 | 0.070073 | -122.2036 | 121.9137 | 122.18 | 122.1099 | 0.49027 | -122.268
2377.4688 | 122.2733 | -0.091553 | 122.1497 | -0.01778 | -0.044128 | 0.041362 | 0.022674 | -0.011651 | -0.0052945 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.041329 | 0.048969 | -0.017266 | 0.005985 | -0.017566 | 0.056706 | 0.059885 | 0.15112 | -0.081373 | 0.069728 | 0.4216 | -0.042615 | 121.8587 | 122.125 | 122.0412 | -0.14125 | 0.01018 | -122.093 | 0.074287 | 0.073987 | 0.063807 | -122.0898 | -121.9985 | -0.049702 | -0.29091 | 0.16128 | 0.048938 | 0.09864 | -0.024622 | -0.10841 | 0.14826 | 0.15144 | 0.24268 | 0.097538 | -122.231 | 121.9503 | 122.2166 | 122.1328 | 0.51315 | -122.2909
2379.1562 | 122.3694 | -0.091553 | 122.0856 | -0.0025182 | -0.044342 | 0.041362 | 0.022674 | -0.011865 | -0.0052945 | -0.021518 | -0.0022666 | -0.0020767 | 0.058901 | 0.041329 | 0.048969 | -0.021844 | 0.010564 | -0.017566 | 0.056706 | 0.055306 | 0.1557 | -0.076794 | 0.074307 | 0.41702 | -0.042615 | 121.8633 | 122.125 | 122.0458 | -0.14583 | 0.014759 | -122.0289 | 0.069709 | 0.073987 | 0.059228 | -122.0303 | -121.9299 | -0.05428 | -0.22225 | 0.16586 | 0.048938 | 0.10322 | 0.039465 | -0.039749 | 0.14826 | 0.14686 | 0.24726 | 0.10212 | -122.1624 | 121.9549 | 122.2166 | 122.1374 | 0.50857 | -122.2314
2380.9219 | 122.3602 | -0.041199 | 122.1039 | -0.01778 | -0.044342 | 0.041789 | 0.02246 | -0.011865 | -0.0050809 | -0.021518 | -0.0022666 | -0.0022903 | 0.058901 | 0.040901 | 0.049397 | -0.017266 | 0.010564 | -0.012988 | 0.061284 | 0.059885 | 0.15112 | -0.081373 | 0.074307 | 0.42618 | -0.042615 | 121.8679 | 122.125 | 122.055 | -0.14583 | -0.040174 | -122.0426 | 0.023933 | 0.028211 | 0.068385 | -122.044 | -121.9528 | -0.10463 | -0.23598 | 0.11551 | -0.001416 | 0.10322 | 0.021154 | -0.048903 | 0.10248 | 0.10108 | 0.19232 | 0.051763 | -122.1853 | 121.9091 | 122.1662 | 122.0962 | 0.46738 | -122.2497
2382.6094 | 122.3694 | -0.068665 | 122.0993 | -0.010149 | -0.044342 | 0.041575 | 0.022674 | -0.011865 | -0.0055083 | -0.029148 | -0.002053 | -0.0022903 | 0.059114 | 0.041542 | 0.048969 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.059885 | 0.15112 | -0.076794 | 0.069728 | 0.4216 | -0.042615 | 121.8587 | 122.1205 | 122.0367 | -0.14583 | -0.008129 | -122.0426 | 0.046821 | 0.055677 | 0.063806 | -122.0394 | -121.9482 | -0.077168 | -0.24056 | 0.13839 | 0.02605 | 0.10322 | 0.021153 | -0.062639 | 0.12537 | 0.12855 | 0.21979 | 0.079229 | -122.1761 | 121.9274 | 122.1891 | 122.1053 | 0.49026 | -122.2451
2384.375 | 122.2733 | -0.10529 | 122.1634 | -0.010149 | -0.044342 | 0.041362 | 0.02246 | -0.011865 | -0.0052945 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.041115 | 0.04961 | -0.021844 | 0.015142 | -0.017566 | 0.056706 | 0.055306 | 0.14655 | -0.090531 | 0.074307 | 0.42618 | -0.038036 | 121.8633 | 122.125 | 122.0504 | -0.14125 | 0.014755 | -122.1067 | 0.083442 | 0.08772 | 0.072965 | -122.1081 | -122.0168 | -0.035969 | -0.30007 | 0.17959 | 0.06725 | 0.10322 | -0.038355 | -0.11299 | 0.16199 | 0.16059 | 0.25183 | 0.12043 | -122.2539 | 121.9686 | 122.2303 | 122.1557 | 0.53146 | -122.3046
2386.0938 | 122.3557 | -0.064087 | 122.1176 | -0.010149 | -0.044128 | 0.041575 | 0.02246 | -0.011865 | -0.0050809 | -0.021518 | -0.002053 | -0.0027177 | 0.058473 | 0.041115 | 0.049183 | -0.017266 | 0.015142 | -0.012988 | 0.056706 | 0.064464 | 0.14655 | -0.090531 | 0.078886 | 0.43076 | -0.042615 | 121.8633 | 122.1296 | 122.0412 | -0.15041 | -0.026444 | -122.0609 | 0.046821 | 0.051099 | 0.077543 | -122.0532 | -121.9711 | -0.086325 | -0.25429 | 0.14297 | 0.021472 | 0.1078 | 0.011999 | -0.076371 | 0.12079 | 0.12855 | 0.21063 | 0.079229 | -122.2081 | 121.9274 | 122.1937 | 122.1053 | 0.49484 | -122.268
2387.8438 | 122.2504 | -0.11902 | 122.1542 | -0.010149 | -0.044342 | 0.041575 | 0.02246 | -0.011651 | -0.0050809 | -0.029148 | -0.0022666 | -0.0022903 | 0.058901 | 0.041329 | 0.049183 | -0.017266 | 0.019721 | -0.022144 | 0.056706 | 0.055306 | 0.16028 | -0.085952 | 0.088043 | 0.42618 | -0.042615 | 121.8633 | 122.125 | 122.0504 | -0.14583 | 0.033067 | -122.0975 | 0.10175 | 0.096875 | 0.063808 | -122.0989 | -121.994 | -0.026814 | -0.29091 | 0.20706 | 0.076404 | 0.10322 | -0.0292 | -0.10384 | 0.17572 | 0.17433 | 0.2793 | 0.13874 | -122.2402 | 121.9823 | 122.2441 | 122.1694 | 0.5452 | -122.3001
2389.5938 | 122.2458 | -0.12817 | 122.1542 | -0.010149 | -0.044128 | 0.041575 | 0.022888 | -0.011865 | -0.0050809 | -0.013887 | -0.0018394 | -0.0020767 | 0.059328 | 0.041542 | 0.049183 | -0.021844 | 0.015142 | -0.017566 | 0.061284 | 0.055306 | 0.15112 | -0.076794 | 0.074307 | 0.42618 | -0.047194 | 121.8587 | 122.125 | 122.0504 | -0.14125 | 0.05138 | -122.093 | 0.10633 | 0.11061 | 0.059228 | -122.0989 | -122.0031 | -0.013081 | -0.29549 | 0.20248 | 0.08098 | 0.094061 | -0.0292 | -0.10384 | 0.18946 | 0.18348 | 0.2793 | 0.14332 | -122.231 | 121.9869 | 122.2532 | 122.1786 | 0.55435 | -122.2955
2391.2812 | 122.2366 | -0.10071 | 122.1771 | -0.01778 | -0.044342 | 0.041575 | 0.022674 | -0.012292 | -0.0052945 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.041329 | 0.049183 | -0.021844 | 0.015142 | -0.008409 | 0.056706 | 0.059885 | 0.15112 | -0.072215 | 0.074307 | 0.43534 | -0.038036 | 121.8679 | 122.1296 | 122.0596 | -0.15499 | 0.028493 | -122.1204 | 0.078864 | 0.092299 | 0.063806 | -122.1172 | -122.026 | -0.054283 | -0.30922 | 0.17502 | 0.062672 | 0.11695 | -0.04751 | -0.11757 | 0.15741 | 0.16059 | 0.25183 | 0.11585 | -122.2493 | 121.9686 | 122.2303 | 122.1603 | 0.53604 | -122.3321
2393.0312 | 122.3648 | -0.059509 | 122.1039 | -0.010149 | -0.044555 | 0.041575 | 0.02246 | -0.011651 | -0.0050809 | -0.021518 | -0.0022666 | -0.0022903 | 0.059114 | 0.041115 | 0.049183 | -0.017266 | 0.010564 | -0.012988 | 0.061284 | 0.064464 | 0.15112 | -0.076794 | 0.074307 | 0.43076 | -0.042615 | 121.8542 | 122.125 | 122.0504 | -0.15041 | -0.017285 | -122.0426 | 0.042243 | 0.046521 | 0.063806 | -122.0394 | -121.9528 | -0.090903 | -0.24972 | 0.13382 | 0.016894 | 0.1078 | 0.021154 | -0.053481 | 0.12079 | 0.12397 | 0.21063 | 0.070073 | -122.1807 | 121.9137 | 122.1845 | 122.1099 | 0.49027 | -122.2543
2394.7812 | 122.2961 | -0.07782 | 122.1497 | -0.01778 | -0.044769 | 0.040934 | 0.02246 | -0.011865 | -0.0050809 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.040901 | 0.048756 | -0.021844 | 0.010564 | -0.008409 | 0.056706 | 0.059885 | 0.15112 | -0.081373 | 0.078886 | 0.42618 | -0.033458 | 121.8633 | 122.1342 | 122.0458 | -0.15041 | -0.003553 | -122.093 | 0.055976 | 0.069411 | 0.072964 | -122.0898 | -121.9985 | -0.072592 | -0.28634 | 0.15671 | 0.044362 | 0.11695 | -0.015465 | -0.10384 | 0.13453 | 0.1377 | 0.22894 | 0.088384 | -122.231 | 121.9411 | 122.212 | 122.1236 | 0.504 | -122.3001
2396.4688 | 122.3831 | -0.054932 | 122.1039 | -0.0025182 | -0.044555 | 0.041575 | 0.022674 | -0.011865 | -0.0048673 | -0.021518 | -0.0018394 | -0.0025041 | 0.058901 | 0.041542 | 0.048969 | -0.021844 | 0.019721 | -0.012988 | 0.056706 | 0.059885 | 0.15112 | -0.076794 | 0.069728 | 0.43076 | -0.042615 | 121.8679 | 122.1296 | 122.0458 | -0.14125 | -0.021862 | -122.0472 | 0.033088 | 0.041944 | 0.063806 | -122.044 | -121.9528 | -0.086323 | -0.23598 | 0.12466 | 0.012317 | 0.09864 | 0.025732 | -0.05806 | 0.11164 | 0.11482 | 0.20606 | 0.074653 | -122.1807 | 121.9228 | 122.1845 | 122.1008 | 0.48569 | -122.2451
2398.2188 | 122.2504 | -0.1236 | 122.1588 | -0.01778 | -0.044555 | 0.041362 | 0.02246 | -0.012078 | -0.0048673 | -0.013887 | -0.0022666 | -0.0018631 | 0.058901 | 0.041329 | 0.049183 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.059885 | 0.15112 | -0.076794 | 0.083464 | 0.42618 | -0.042615 | 121.8679 | 122.1296 | 122.055 | -0.14583 | 0.046802 | -122.1021 | 0.10175 | 0.11061 | 0.063806 | -122.0989 | -122.0077 | -0.022237 | -0.29091 | 0.20706 | 0.080981 | 0.10322 | -0.029199 | -0.10383 | 0.1803 | 0.18348 | 0.27472 | 0.13416 | -122.2356 | 121.9915 | 122.2532 | 122.1786 | 0.54978 | -122.3046
2399.9688 | 122.3831 | -0.059509 | 122.1222 | -0.010149 | -0.044555 | 0.041362 | 0.022674 | -0.011865 | -0.0048673 | -0.0062567 | -0.0018394 | -0.0020767 | 0.058901 | 0.041329 | 0.049183 | -0.021844 | 0.010564 | -0.017566 | 0.056706 | 0.064464 | 0.14655 | -0.081373 | 0.078886 | 0.42618 | -0.042615 | 121.8679 | 122.1388 | 122.055 | -0.15041 | -0.021864 | -122.0655 | 0.037665 | 0.041943 | 0.063807 | -122.0577 | -121.9756 | -0.090903 | -0.25429 | 0.13839 | 0.016894 | 0.1078 | 0.016579 | -0.067213 | 0.11621 | 0.12397 | 0.20605 | 0.070073 | -122.2036 | 121.9274 | 122.1983 | 122.1145 | 0.48569 | -122.2726
2401.7188 | 122.3282 | -0.068665 | 122.1497 | -0.010149 | -0.044769 | 0.041575 | 0.022247 | -0.011651 | -0.0048673 | -0.0062567 | -0.002053 | -0.0025041 | 0.058901 | 0.041542 | 0.049183 | -0.026423 | 0.010564 | -0.012988 | 0.056706 | 0.055306 | 0.14655 | -0.081373 | 0.074307 | 0.43076 | -0.042615 | 121.8587 | 122.1433 | 122.055 | -0.14583 | -0.012708 | -122.093 | 0.042242 | 0.055677 | 0.068385 | -122.0944 | -122.0031 | -0.077168 | -0.29091 | 0.14297 | 0.02605 | 0.10322 | -0.006308 | -0.094679 | 0.12537 | 0.12397 | 0.21521 | 0.079229 | -122.231 | 121.9274 | 122.212 | 122.1236 | 0.49942 | -122.2955
2403.4219 | 122.3465 | -0.068665 | 122.1268 | -0.010149 | -0.044555 | 0.041362 | 0.022674 | -0.011437 | -0.0050809 | -0.029148 | -0.0022666 | -0.0022903 | 0.058687 | 0.041329 | 0.049183 | -0.017266 | 0.010564 | -0.017566 | 0.056706 | 0.064464 | 0.15112 | -0.076794 | 0.078886 | 0.43076 | -0.042615 | 121.8771 | 122.1388 | 122.0596 | -0.15041 | -0.008129 | -122.0701 | 0.051399 | 0.051099 | 0.059228 | -122.0623 | -121.9756 | -0.081747 | -0.24971 | 0.14755 | 0.02605 | 0.1078 | 0.012001 | -0.067212 | 0.12537 | 0.13313 | 0.21979 | 0.079229 | -122.2036 | 121.9457 | 122.2074 | 122.1282 | 0.49942 | -122.2772
2405.1719 | 122.2733 | -0.09613 | 122.1405 | -0.010149 | -0.044555 | 0.041575 | 0.02246 | -0.011865 | -0.0052945 | -0.021518 | -0.0016258 | -0.0020767 | 0.058687 | 0.041329 | 0.049183 | -0.026423 | 0.010564 | -0.012988 | 0.061284 | 0.059885 | 0.1557 | -0.076794 | 0.074307 | 0.43076 | -0.042615 | 121.8679 | 122.1296 | 122.055 | -0.15499 | 0.019336 | -122.0792 | 0.069707 | 0.083142 | 0.063806 | -122.0806 | -121.9848 | -0.058861 | -0.2726 | 0.17044 | 0.053515 | 0.11238 | -0.010889 | -0.085524 | 0.15741 | 0.15601 | 0.25183 | 0.10669 | -122.2173 | 121.964 | 122.2257 | 122.1511 | 0.52689 | -122.2955
2406.875 | 122.3877 | -0.054932 | 122.1268 | -0.01778 | -0.044555 | 0.041575 | 0.022247 | -0.011865 | -0.0048673 | -0.021518 | -0.0018394 | -0.0025041 | 0.058473 | 0.041329 | 0.049183 | -0.026423 | 0.010564 | -0.017566 | 0.056706 | 0.064464 | 0.14655 | -0.081373 | 0.078886 | 0.42618 | -0.042615 | 121.8633 | 122.1388 | 122.0504 | -0.13668 | -0.026441 | -122.0701 | 0.028509 | 0.037366 | 0.063807 | -122.0623 | -121.9802 | -0.081744 | -0.26345 | 0.13382 | 0.012317 | 0.094061 | 0.012001 | -0.076369 | 0.11164 | 0.1194 | 0.20148 | 0.065496 | -122.2081 | 121.9183 | 122.1937 | 122.1053 | 0.48111 | -122.2634
2408.625 | 122.3694 | -0.054932 | 122.1405 | 0.0051128 | -0.044769 | 0.041362 | 0.022247 | -0.011651 | -0.0050809 | -0.013887 | -0.0016258 | -0.0025041 | 0.058687 | 0.041542 | 0.049183 | -0.012688 | 0.010564 | -0.012988 | 0.056706 | 0.069043 | 0.14655 | -0.076794 | 0.078886 | 0.43534 | -0.042615 | 121.8679 | 122.1388 | 122.0504 | -0.14583 | -0.021862 | -122.0838 | 0.042244 | 0.041944 | 0.063806 | -122.0715 | -121.994 | -0.090901 | -0.2726 | 0.13382 | 0.012317 | 0.10322 | -0.001732 | -0.090102 | 0.11164 | 0.12398 | 0.20148 | 0.065496 | -122.2173 | 121.9228 | 122.1937 | 122.1053 | 0.49027 | -122.2863
2410.3125 | 122.2366 | -0.1236 | 122.1588 | -0.010149 | -0.044555 | 0.041575 | 0.022247 | -0.011651 | -0.0052945 | -0.013887 | -0.002053 | -0.0022903 | 0.059114 | 0.041756 | 0.049183 | -0.012688 | 0.010564 | -0.008409 | 0.056706 | 0.059885 | 0.14655 | -0.081373 | 0.074307 | 0.43076 | -0.038036 | 121.8725 | 122.1433 | 122.0641 | -0.15041 | 0.042223 | -122.1021 | 0.11091 | 0.11519 | 0.072964 | -122.0989 | -122.0123 | -0.026816 | -0.28633 | 0.1979 | 0.08556 | 0.11238 | -0.015463 | -0.094676 | 0.1803 | 0.18348 | 0.27014 | 0.13416 | -122.2402 | 121.9961 | 122.2669 | 122.1877 | 0.55435 | -122.3092
2412.0156 | 122.3282 | -0.073242 | 122.1313 | -0.033042 | -0.044555 | 0.041362 | 0.022247 | -0.011865 | -0.0052945 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.041115 | 0.049183 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.059885 | 0.15112 | -0.081373 | 0.074307 | 0.43076 | -0.038036 | 121.8725 | 122.1433 | 122.055 | -0.14125 | -0.008131 | -122.0746 | 0.051398 | 0.060254 | 0.068385 | -122.0715 | -121.9802 | -0.068013 | -0.25887 | 0.14755 | 0.035206 | 0.10322 | 0.012002 | -0.076369 | 0.12995 | 0.13313 | 0.22437 | 0.083806 | -122.2127 | 121.9457 | 122.2166 | 122.1282 | 0.504 | -122.2726
2413.7812 | 122.2916 | -0.09613 | 122.1771 | -0.01778 | -0.044769 | 0.041148 | 0.022674 | -0.012078 | -0.0050809 | -0.021518 | -0.0018394 | -0.0022903 | 0.058687 | 0.041542 | 0.048969 | -0.017266 | 0.015142 | -0.022144 | 0.056706 | 0.064464 | 0.15112 | -0.076794 | 0.078886 | 0.42618 | -0.038036 | 121.8679 | 122.1479 | 122.0596 | -0.14583 | 0.019336 | -122.1204 | 0.078864 | 0.073986 | 0.05465 | -122.1127 | -122.026 | -0.049703 | -0.30922 | 0.17502 | 0.058094 | 0.1078 | -0.029195 | -0.11757 | 0.15284 | 0.16059 | 0.24725 | 0.11127 | -122.2539 | 121.964 | 122.2441 | 122.1557 | 0.52231 | -122.323
2415.5625 | 122.3648 | -0.059509 | 122.1542 | -0.010149 | -0.044555 | 0.041575 | 0.02246 | -0.012292 | -0.0048673 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058687 | 0.041542 | 0.048969 | -0.012688 | 0.015142 | -0.012988 | 0.061284 | 0.073622 | 0.1557 | -0.085952 | 0.078886 | 0.43076 | -0.038036 | 121.8725 | 122.1433 | 122.0641 | -0.14125 | -0.026443 | -122.093 | 0.046821 | 0.046521 | 0.072964 | -122.0806 | -121.9985 | -0.081746 | -0.28176 | 0.13839 | 0.021473 | 0.10322 | -0.010886 | -0.090099 | 0.12079 | 0.13313 | 0.21521 | 0.074651 | -122.2402 | 121.932 | 122.2029 | 122.1236 | 0.49027 | -122.2955
2417.25 | 122.3511 | -0.064087 | 122.1451 | -0.0025182 | -0.044983 | 0.041148 | 0.02246 | -0.011865 | -0.0050809 | -0.013887 | -0.0016258 | -0.0022903 | 0.058901 | 0.041115 | 0.049183 | -0.021844 | 0.010564 | -0.008409 | 0.061284 | 0.059885 | 0.1557 | -0.081373 | 0.083464 | 0.43076 | -0.028879 | 121.8771 | 122.1388 | 122.0596 | -0.14125 | -0.017286 | -122.0838 | 0.042243 | 0.055678 | 0.072964 | -122.0852 | -121.9894 | -0.077168 | -0.26802 | 0.14755 | 0.035208 | 0.11238 | -0.00631 | -0.085523 | 0.12537 | 0.12397 | 0.21979 | 0.074651 | -122.2265 | 121.9411 | 122.2029 | 122.1236 | 0.49484 | -122.2863
2419 | 122.2504 | -0.091553 | 122.1588 | -0.01778 | -0.044769 | 0.041575 | 0.02246 | -0.012078 | -0.0052945 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.041542 | 0.048969 | -0.017266 | 0.010564 | -0.012988 | 0.056706 | 0.064464 | 0.14655 | -0.081373 | 0.074307 | 0.4216 | -0.042615 | 121.8816 | 122.1342 | 122.055 | -0.14125 | 0.01018 | -122.1021 | 0.074287 | 0.078565 | 0.068385 | -122.0943 | -122.0123 | -0.049702 | -0.27718 | 0.16586 | 0.048938 | 0.09864 | -0.02462 | -0.10383 | 0.14826 | 0.15602 | 0.2381 | 0.10212 | -122.2402 | 121.9732 | 122.2257 | 122.1465 | 0.51315 | -122.3001
2420.6875 | 122.3511 | -0.073242 | 122.1222 | -0.01778 | -0.044555 | 0.041148 | 0.02246 | -0.011865 | -0.0046535 | -0.021518 | -0.0022666 | -0.0025041 | 0.059114 | 0.041542 | 0.049183 | -0.021844 | 0.015142 | -0.008409 | 0.056706 | 0.059885 | 0.14197 | -0.081373 | 0.074307 | 0.43076 | -0.038036 | 121.8725 | 122.1479 | 122.0641 | -0.14583 | -0.008131 | -122.0655 | 0.051398 | 0.064833 | 0.072964 | -122.0623 | -121.9802 | -0.072591 | -0.24971 | 0.14755 | 0.035206 | 0.1078 | 0.025737 | -0.058055 | 0.12995 | 0.13313 | 0.21521 | 0.088384 | -122.2036 | 121.9457 | 122.2212 | 122.1374 | 0.504 | -122.268
2422.4219 | 122.287 | -0.086975 | 122.1863 | 0.0051128 | -0.044128 | 0.041362 | 0.02246 | -0.011865 | -0.0048673 | -0.013887 | -0.0022666 | -0.0025041 | 0.058901 | 0.041756 | 0.049183 | -0.017266 | 0.010564 | -0.026723 | 0.061284 | 0.064464 | 0.14655 | -0.081373 | 0.074307 | 0.43534 | -0.033458 | 121.8816 | 122.1388 | 122.0596 | -0.14125 | 0.005602 | -122.125 | 0.069709 | 0.060252 | 0.05465 | -122.1218 | -122.0397 | -0.05428 | -0.30464 | 0.16128 | 0.053517 | 0.1078 | -0.047508 | -0.12672 | 0.14826 | 0.15144 | 0.23352 | 0.097539 | -122.2677 | 121.9686 | 122.2257 | 122.1465 | 0.52231 | -122.3275
2424.1719 | 122.3557 | -0.059509 | 122.1313 | -0.0025182 | -0.044342 | 0.041148 | 0.02246 | -0.011865 | -0.0048673 | -0.029148 | -0.0022666 | -0.0025041 | 0.058901 | 0.041542 | 0.048542 | -0.031001 | 0.010564 | -0.022144 | 0.061284 | 0.064464 | 0.1557 | -0.081373 | 0.078886 | 0.43534 | -0.038036 | 121.8771 | 122.1388 | 122.0596 | -0.14583 | -0.021864 | -122.0701 | 0.028508 | 0.037365 | 0.059229 | -122.0669 | -121.9756 | -0.086324 | -0.25429 | 0.13839 | 0.021473 | 0.1078 | 0.007423 | -0.07179 | 0.12079 | 0.12397 | 0.21521 | 0.070073 | -122.2127 | 121.9366 | 122.1983 | 122.1191 | 0.49484 | -122.2772
2425.9375 | 122.2733 | -0.09613 | 122.1771 | -0.010149 | -0.044555 | 0.041362 | 0.022247 | -0.012078 | -0.0050809 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.041542 | 0.049183 | -0.026423 | 0.015142 | -0.017566 | 0.052128 | 0.059885 | 0.15112 | -0.081373 | 0.078886 | 0.41702 | -0.042615 | 121.8725 | 122.1388 | 122.0641 | -0.14125 | 0.014757 | -122.125 | 0.069707 | 0.078564 | 0.063807 | -122.1172 | -122.026 | -0.045125 | -0.30464 | 0.17502 | 0.053515 | 0.09864 | -0.038353 | -0.11299 | 0.14826 | 0.15601 | 0.24725 | 0.11127 | -122.2585 | 121.9686 | 122.2349 | 122.1603 | 0.51315 | -122.3184
2427.6875 | 122.3923 | -0.082397 | 122.1085 | -0.01778 | -0.044769 | 0.040934 | 0.022247 | -0.011865 | -0.0050809 | -0.013887 | -0.0022666 | -0.0022903 | 0.058901 | 0.041542 | 0.048969 | -0.012688 | 0.019721 | -0.022144 | 0.056706 | 0.064464 | 0.14655 | -0.076794 | 0.074307 | 0.4216 | -0.042615 | 121.8771 | 122.1433 | 122.0641 | -0.14125 | 0.005603 | -122.0518 | 0.069709 | 0.060253 | 0.05465 | -122.044 | -121.9619 | -0.058858 | -0.2314 | 0.1567 | 0.039782 | 0.09864 | 0.034891 | -0.044322 | 0.1391 | 0.14686 | 0.22894 | 0.10212 | -122.1853 | 121.9595 | 122.2257 | 122.1465 | 0.504 | -122.2497
2429.375 | 122.3877 | -0.054932 | 122.1268 | -0.010149 | -0.044983 | 0.041362 | 0.022247 | -0.011865 | -0.0050809 | -0.013887 | -0.0016258 | -0.0022903 | 0.058473 | 0.041542 | 0.049397 | -0.017266 | 0.010564 | -0.012988 | 0.061284 | 0.069043 | 0.14197 | -0.072215 | 0.078886 | 0.43076 | -0.038036 | 121.8771 | 122.1433 | 122.0641 | -0.14125 | -0.017283 | -122.0655 | 0.037666 | 0.041944 | 0.059227 | -122.0577 | -121.9848 | -0.086323 | -0.24971 | 0.13382 | 0.016896 | 0.10322 | 0.01658 | -0.062633 | 0.11622 | 0.12398 | 0.1969 | 0.065496 | -122.199 | 121.932 | 122.1983 | 122.1191 | 0.48569 | -122.268
2431.1406 | 122.3007 | -0.073242 | 122.1497 | -0.01778 | -0.044769 | 0.041362 | 0.022674 | -0.011865 | -0.0046535 | -0.013887 | -0.0022666 | -0.0020767 | 0.059114 | 0.041542 | 0.048969 | -0.021844 | 0.019721 | -0.012988 | 0.056706 | 0.073622 | 0.1557 | -0.081373 | 0.074307 | 0.43076 | -0.038036 | 121.8725 | 122.1479 | 122.0641 | -0.14583 | -0.008131 | -122.093 | 0.051398 | 0.060254 | 0.068385 | -122.076 | -121.994 | -0.072591 | -0.27718 | 0.14755 | 0.035206 | 0.1078 | -0.001729 | -0.085521 | 0.12995 | 0.14686 | 0.22894 | 0.092963 | -122.231 | 121.9457 | 122.2212 | 122.1374 | 0.504 | -122.2955
2432.875 | 122.2687 | -0.11444 | 122.1863 | -0.0025182 | -0.044769 | 0.041148 | 0.02246 | -0.012292 | -0.0048673 | -0.021518 | -0.002053 | -0.0027177 | 0.058687 | 0.041115 | 0.049397 | -0.026423 | 0.015142 | -0.008409 | 0.061284 | 0.069043 | 0.15112 | -0.085952 | 0.078886 | 0.43992 | -0.038036 | 121.8816 | 122.1479 | 122.0641 | -0.14125 | 0.028489 | -122.125 | 0.088018 | 0.10603 | 0.077543 | -122.1172 | -122.0352 | -0.026814 | -0.30464 | 0.19333 | 0.076405 | 0.10322 | -0.03835 | -0.12214 | 0.17572 | 0.18348 | 0.26556 | 0.12958 | -122.2722 | 121.9961 | 122.2624 | 122.1786 | 0.55436 | -122.3275
2434.625 | 122.2595 | -0.10986 | 122.168 | -0.010149 | -0.044555 | 0.041148 | 0.022033 | -0.011865 | -0.0046535 | -0.013887 | -0.0022666 | -0.0025041 | 0.058901 | 0.041542 | 0.048969 | -0.021844 | 0.019721 | -0.012988 | 0.056706 | 0.064464 | 0.15112 | -0.081373 | 0.078886 | 0.43534 | -0.047194 | 121.8725 | 122.1525 | 122.0687 | -0.14583 | 0.02849 | -122.1113 | 0.088019 | 0.096875 | 0.068385 | -122.1035 | -122.0168 | -0.03597 | -0.29549 | 0.18875 | 0.062669 | 0.098639 | -0.015462 | -0.099254 | 0.16657 | 0.17433 | 0.26099 | 0.12958 | -122.2493 | 121.9823 | 122.2624 | 122.1786 | 0.5452 | -122.3138
2436.375 | 122.2824 | -0.10529 | 122.1634 | -0.01778 | -0.044769 | 0.041789 | 0.022247 | -0.011865 | -0.0046535 | -0.021518 | -0.0018394 | -0.0025041 | 0.058901 | 0.041542 | 0.048756 | -0.017266 | 0.015142 | -0.017566 | 0.061284 | 0.069043 | 0.15112 | -0.085952 | 0.078886 | 0.43992 | -0.042615 | 121.8908 | 122.1525 | 122.0641 | -0.13668 | 0.019334 | -122.1021 | 0.08802 | 0.08772 | 0.068386 | -122.0943 | -122.0123 | -0.03139 | -0.2726 | 0.18417 | 0.062671 | 0.094061 | -0.010884 | -0.099254 | 0.16657 | 0.17433 | 0.25641 | 0.12043 | -122.2493 | 121.9961 | 122.2578 | 122.1694 | 0.5452 | -122.3001
2438.125 | 122.2595 | -0.10529 | 122.1634 | -0.01778 | -0.044555 | 0.041362 | 0.02246 | -0.011651 | -0.0048673 | -0.013887 | -0.0018394 | -0.0022903 | 0.058687 | 0.041542 | 0.048969 | -0.017266 | 0.010564 | -0.017566 | 0.061284 | 0.069043 | 0.1557 | -0.072215 | 0.078886 | 0.43076 | -0.038036 | 121.8771 | 122.1479 | 122.0641 | -0.13668 | 0.033071 | -122.1021 | 0.08802 | 0.08772 | 0.054649 | -122.0943 | -122.0077 | -0.03139 | -0.28633 | 0.18417 | 0.06725 | 0.09864 | -0.015462 | -0.099254 | 0.16657 | 0.17433 | 0.26099 | 0.11585 | -122.2356 | 121.9823 | 122.2532 | 122.1694 | 0.53604 | -122.3001
2439.8125 | 122.3923 | -0.050354 | 122.1497 | -0.0025182 | -0.044555 | 0.041148 | 0.021819 | -0.011437 | -0.0048673 | -0.021518 | -0.0018394 | -0.0020767 | 0.058901 | 0.041542 | 0.049183 | -0.017266 | 0.005985 | -0.012988 | 0.056706 | 0.064464 | 0.15112 | -0.072215 | 0.078886 | 0.43534 | -0.038036 | 121.8862 | 122.1525 | 122.0641 | -0.13668 | -0.021861 | -122.093 | 0.033088 | 0.037366 | 0.059227 | -122.0852 | -121.9985 | -0.086322 | -0.26344 | 0.12924 | 0.012318 | 0.09864 | 0.002849 | -0.085521 | 0.10706 | 0.11482 | 0.20148 | 0.056339 | -122.2219 | 121.9366 | 122.2029 | 122.1145 | 0.48569 | -122.2863
2441.5781 | 122.3007 | -0.10071 | 122.2046 | -0.010149 | -0.044769 | 0.041362 | 0.022247 | -0.011437 | -0.0048673 | -0.021518 | -0.0022666 | -0.0020767 | 0.058687 | 0.04197 | 0.049183 | -0.021844 | 0.015142 | -0.022144 | 0.065863 | 0.064464 | 0.15112 | -0.076794 | 0.083464 | 0.43992 | -0.038036 | 121.8862 | 122.1525 | 122.0596 | -0.14125 | 0.023914 | -122.1387 | 0.078864 | 0.078564 | 0.05465 | -122.1401 | -122.0535 | -0.040547 | -0.31837 | 0.18417 | 0.062672 | 0.10322 | -0.052083 | -0.14503 | 0.16657 | 0.16517 | 0.25183 | 0.11585 | -122.2814 | 121.9869 | 122.2532 | 122.1603 | 0.54062 | -122.3458
2443.2656 | 122.406 | -0.068665 | 122.1313 | -0.010149 | -0.044769 | 0.041148 | 0.022247 | -0.012292 | -0.0048673 | -0.013887 | -0.0022666 | -0.0022903 | 0.058901 | 0.041542 | 0.04961 | -0.021844 | 0.015142 | -0.022144 | 0.061284 | 0.064464 | 0.15112 | -0.076794 | 0.078886 | 0.43534 | -0.042615 | 121.8862 | 122.1571 | 122.055 | -0.14125 | -0.008129 | -122.0701 | 0.046821 | 0.046521 | 0.05465 | -122.0669 | -121.9802 | -0.07259 | -0.24513 | 0.14755 | 0.02605 | 0.09864 | 0.025738 | -0.076369 | 0.12995 | 0.13313 | 0.21979 | 0.083807 | -122.2081 | 121.9549 | 122.2258 | 122.1236 | 0.504 | -122.2726
2445.0156 | 122.3007 | -0.082397 | 122.1817 | -0.0025182 | -0.044555 | 0.041362 | 0.02246 | -0.012078 | -0.0048673 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.041756 | 0.049397 | -0.021844 | 0.010564 | -0.012988 | 0.047549 | 0.059885 | 0.14197 | -0.081373 | 0.078886 | 0.43076 | -0.038036 | 121.8862 | 122.1571 | 122.0596 | -0.13668 | 0.001024 | -122.1342 | 0.060553 | 0.069409 | 0.068385 | -122.1218 | -122.0397 | -0.054279 | -0.29549 | 0.16128 | 0.044361 | 0.09864 | -0.024616 | -0.12214 | 0.12995 | 0.14228 | 0.22436 | 0.092961 | -122.2631 | 121.9686 | 122.2395 | 122.142 | 0.51316 | -122.3184
2446.7812 | 122.3053 | -0.09613 | 122.1634 | -0.0025182 | -0.044983 | 0.041362 | 0.02246 | -0.011865 | -0.0046535 | -0.029148 | -0.002053 | -0.0020767 | 0.058473 | 0.041329 | 0.049183 | -0.017266 | 0.005985 | -0.017566 | 0.056706 | 0.064464 | 0.15112 | -0.076794 | 0.074307 | 0.43534 | -0.042615 | 121.8862 | 122.1525 | 122.0687 | -0.14125 | 0.019336 | -122.1067 | 0.078864 | 0.078564 | 0.059228 | -122.0989 | -122.0123 | -0.045125 | -0.27718 | 0.17044 | 0.053515 | 0.09864 | -0.010884 | -0.094676 | 0.15284 | 0.16059 | 0.24725 | 0.10211 | -122.2402 | 121.9823 | 122.2486 | 122.1648 | 0.53147 | -122.3046
2448.4844 | 122.3419 | -0.086975 | 122.1725 | -0.0025182 | -0.044983 | 0.041148 | 0.022247 | -0.011865 | -0.0048673 | -0.029148 | -0.0022666 | -0.0020767 | 0.058473 | 0.041542 | 0.048969 | -0.017266 | 0.015142 | -0.017566 | 0.056706 | 0.073622 | 0.15112 | -0.072215 | 0.078886 | 0.43534 | -0.033458 | 121.8816 | 122.1479 | 122.0596 | -0.14125 | 0.01476 | -122.1158 | 0.069709 | 0.069409 | 0.054649 | -122.0989 | -122.0214 | -0.05428 | -0.29091 | 0.16586 | 0.053517 | 0.1078 | -0.024617 | -0.11299 | 0.14368 | 0.1606 | 0.2381 | 0.10212 | -122.2448 | 121.9686 | 122.2349 | 122.1465 | 0.52231 | -122.3138
2450.2344 | 122.3236 | -0.082397 | 122.1451 | -0.01778 | -0.044769 | 0.041362 | 0.022247 | -0.012078 | -0.0046535 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.04197 | 0.048969 | -0.017266 | 0.010564 | -0.017566 | 0.061284 | 0.059885 | 0.15112 | -0.081373 | 0.078886 | 0.43534 | -0.033458 | 121.8908 | 122.1525 | 122.0733 | -0.14125 | 0.001024 | -122.0838 | 0.065131 | 0.064831 | 0.063807 | -122.0852 | -121.994 | -0.058858 | -0.25429 | 0.16128 | 0.048939 | 0.1078 | 0.007426 | -0.071787 | 0.14368 | 0.14228 | 0.23352 | 0.092961 | -122.2265 | 121.9732 | 122.2349 | 122.1557 | 0.51773 | -122.2863
2451.9844 | 122.3053 | -0.091553 | 122.1771 | -0.0025182 | -0.044769 | 0.041148 | 0.02246 | -0.012078 | -0.0050809 | -0.013887 | -0.002053 | -0.0020767 | 0.058473 | 0.041329 | 0.049183 | -0.026423 | 0.010564 | -0.012988 | 0.056706 | 0.064464 | 0.1557 | -0.076794 | 0.078886 | 0.43534 | -0.042615 | 121.8862 | 122.1525 | 122.0687 | -0.14125 | 0.014759 | -122.1204 | 0.06513 | 0.078565 | 0.063806 | -122.1127 | -122.0214 | -0.049702 | -0.29091 | 0.17044 | 0.048938 | 0.09864 | -0.024617 | -0.10841 | 0.14826 | 0.15602 | 0.24726 | 0.10212 | -122.2539 | 121.9778 | 122.2441 | 122.1603 | 0.52689 | -122.3184
2453.7344 | 122.4014 | -0.059509 | 122.1359 | -0.010149 | -0.044983 | 0.041575 | 0.02246 | -0.012078 | -0.0048673 | -0.013887 | -0.0024804 | -0.0022903 | 0.058687 | 0.04197 | 0.049183 | -0.021844 | 0.015142 | -0.012988 | 0.056706 | 0.069043 | 0.1557 | -0.076794 | 0.078886 | 0.43076 | -0.038036 | 121.8862 | 122.1571 | 122.0733 | -0.14125 | -0.017285 | -122.0792 | 0.037665 | 0.046521 | 0.063806 | -122.0669 | -121.9802 | -0.081746 | -0.24971 | 0.13839 | 0.021473 | 0.10322 | 0.021161 | -0.062631 | 0.11621 | 0.12855 | 0.21521 | 0.074651 | -122.2127 | 121.9457 | 122.2166 | 122.1328 | 0.49027 | -122.2772
2455.4219 | 122.3557 | -0.07782 | 122.1359 | -0.010149 | -0.044769 | 0.040934 | 0.02246 | -0.011865 | -0.0046535 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.041542 | 0.048969 | -0.026423 | 0.015142 | -0.017566 | 0.061284 | 0.064464 | 0.14655 | -0.076794 | 0.078886 | 0.43076 | -0.033458 | 121.8908 | 122.1525 | 122.0641 | -0.14125 | 0.001026 | -122.0746 | 0.051397 | 0.060254 | 0.059228 | -122.0715 | -121.9894 | -0.063435 | -0.24513 | 0.15671 | 0.044362 | 0.1078 | 0.016582 | -0.071788 | 0.1391 | 0.14228 | 0.22437 | 0.092962 | -122.2127 | 121.9686 | 122.2303 | 122.142 | 0.50858 | -122.2772
2457.1875 | 122.2504 | -0.10071 | 122.1863 | 0.0051128 | -0.044555 | 0.041148 | 0.02246 | -0.011651 | -0.0050809 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.041756 | 0.048969 | -0.021844 | 0.010564 | -0.012988 | 0.061284 | 0.059885 | 0.15112 | -0.085952 | 0.078886 | 0.43992 | -0.038036 | 121.8816 | 122.1433 | 122.0779 | -0.14125 | 0.014756 | -122.125 | 0.078864 | 0.08772 | 0.072964 | -122.1264 | -122.0352 | -0.040547 | -0.30464 | 0.17959 | 0.062672 | 0.10322 | -0.042929 | -0.10841 | 0.16199 | 0.16059 | 0.25183 | 0.11127 | -122.2722 | 121.9823 | 122.2441 | 122.1786 | 0.54062 | -122.3275
2458.9375 | 122.2778 | -0.10986 | 122.2046 | -0.0025182 | -0.044769 | 0.041362 | 0.022247 | -0.011651 | -0.0048673 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.04197 | 0.048969 | -0.012688 | 0.015142 | -0.017566 | 0.065863 | 0.064464 | 0.15112 | -0.076794 | 0.083464 | 0.43076 | -0.042615 | 121.8954 | 122.1617 | 122.0733 | -0.13668 | 0.033069 | -122.1387 | 0.097175 | 0.092297 | 0.059228 | -122.1401 | -122.0535 | -0.026813 | -0.30922 | 0.19333 | 0.067248 | 0.094061 | -0.042926 | -0.1313 | 0.17573 | 0.17433 | 0.26099 | 0.12501 | -122.2814 | 122.0052 | 122.2715 | 122.1832 | 0.54062 | -122.3413
2460.7031 | 122.2504 | -0.1236 | 122.1542 | -0.0025182 | -0.044555 | 0.041148 | 0.02246 | -0.011651 | -0.0046535 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058901 | 0.041542 | 0.049183 | -0.012688 | 0.015142 | -0.012988 | 0.065863 | 0.069043 | 0.15112 | -0.081373 | 0.078886 | 0.43534 | -0.033458 | 121.8954 | 122.1571 | 122.0687 | -0.14583 | 0.042223 | -122.0884 | 0.11091 | 0.11061 | 0.068385 | -122.0852 | -122.0031 | -0.022237 | -0.25886 | 0.20248 | 0.090138 | 0.11237 | 0.00285 | -0.085521 | 0.18946 | 0.19264 | 0.27472 | 0.13874 | -122.2356 | 122.019 | 122.2807 | 122.1923 | 0.55893 | -122.3001
2462.4219 | 122.2687 | -0.10986 | 122.1863 | -0.0025182 | -0.044769 | 0.041362 | 0.02246 | -0.011651 | -0.0046535 | -0.013887 | -0.002053 | -0.0025041 | 0.058687 | 0.041542 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.056706 | 0.069043 | 0.15112 | -0.076794 | 0.074307 | 0.43534 | -0.042615 | 121.8908 | 122.1571 | 122.0733 | -0.14125 | 0.033069 | -122.1296 | 0.092597 | 0.096875 | 0.063806 | -122.1172 | -122.0352 | -0.031392 | -0.29548 | 0.18417 | 0.067248 | 0.09864 | -0.029193 | -0.11298 | 0.16657 | 0.17891 | 0.26099 | 0.12501 | -122.2631 | 122.0007 | 122.2669 | 122.1832 | 0.5452 | -122.3275
2464.1719 | 122.406 | -0.054932 | 122.1863 | -0.0025182 | -0.045196 | 0.041362 | 0.02246 | -0.011865 | -0.0048673 | -0.013887 | -0.0018394 | -0.0025041 | 0.058687 | 0.041756 | 0.049397 | -0.021844 | 0.015142 | -0.012988 | 0.056706 | 0.073622 | 0.15112 | -0.072215 | 0.078886 | 0.42618 | -0.042615 | 121.8908 | 122.1525 | 122.0733 | -0.14583 | -0.017283 | -122.1296 | 0.033088 | 0.041944 | 0.059227 | -122.1127 | -122.0352 | -0.090901 | -0.29548 | 0.13382 | 0.012317 | 0.10322 | -0.033772 | -0.11298 | 0.11164 | 0.12855 | 0.20606 | 0.070074 | -122.2585 | 121.9457 | 122.2074 | 122.1282 | 0.48111 | -122.3321
2465.875 | 122.2458 | -0.10986 | 122.1771 | -0.010149 | -0.044983 | 0.041148 | 0.021819 | -0.012078 | -0.0048673 | -0.021518 | -0.0022666 | -0.0025041 | 0.058901 | 0.04197 | 0.048756 | -0.017266 | 0.019721 | -0.008409 | 0.061284 | 0.069043 | 0.1557 | -0.076794 | 0.088043 | 0.43992 | -0.038036 | 121.8908 | 122.1571 | 122.0733 | -0.14125 | 0.033069 | -122.1158 | 0.092597 | 0.10145 | 0.068385 | -122.1081 | -122.0214 | -0.031392 | -0.28633 | 0.19791 | 0.071827 | 0.10322 | -0.020038 | -0.10383 | 0.17115 | 0.17891 | 0.26556 | 0.12958 | -122.2539 | 122.0007 | 122.2669 | 122.1832 | 0.54978 | -122.3184
2467.6406 | 122.2824 | -0.086975 | 122.1909 | -0.010149 | -0.044983 | 0.041148 | 0.022247 | -0.011865 | -0.0048673 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.041756 | 0.049183 | -0.017266 | 0.010564 | -0.017566 | 0.052128 | 0.064464 | 0.1557 | -0.076794 | 0.078886 | 0.43076 | -0.028879 | 121.8908 | 122.1525 | 122.0733 | -0.14125 | 0.010181 | -122.1387 | 0.069709 | 0.069409 | 0.059228 | -122.1264 | -122.0352 | -0.05428 | -0.30006 | 0.16586 | 0.058096 | 0.11238 | -0.03835 | -0.11756 | 0.1391 | 0.15144 | 0.24268 | 0.097539 | -122.2677 | 121.9778 | 122.2395 | 122.1603 | 0.51773 | -122.3321
2469.3281 | 122.2458 | -0.10529 | 122.1725 | -0.01778 | -0.044555 | 0.041148 | 0.02246 | -0.011437 | -0.0050809 | -0.013887 | -0.002053 | -0.0020767 | 0.058687 | 0.041756 | 0.048969 | -0.012688 | 0.015142 | -0.008409 | 0.052128 | 0.064464 | 0.14655 | -0.081373 | 0.078886 | 0.43992 | -0.038036 | 121.8954 | 122.1525 | 122.0779 | -0.14125 | 0.023913 | -122.1204 | 0.092598 | 0.096877 | 0.072964 | -122.1081 | -122.026 | -0.035969 | -0.27717 | 0.18417 | 0.06725 | 0.10322 | -0.020039 | -0.094674 | 0.15741 | 0.16975 | 0.25183 | 0.12043 | -122.2539 | 122.0007 | 122.2578 | 122.1832 | 0.5452 | -122.3138
2471.0938 | 122.3419 | -0.059509 | 122.1405 | -0.0025182 | -0.044983 | 0.041362 | 0.02246 | -0.011651 | -0.0046535 | -0.013887 | -0.002053 | -0.0020767 | 0.058687 | 0.041542 | 0.048969 | -0.021844 | 0.010564 | -0.017566 | 0.061284 | 0.059885 | 0.15112 | -0.076794 | 0.083464 | 0.43534 | -0.033458 | 121.8908 | 122.1571 | 122.0733 | -0.14125 | -0.017285 | -122.0792 | 0.037665 | 0.041943 | 0.059228 | -122.0806 | -121.9894 | -0.081746 | -0.24971 | 0.14297 | 0.026051 | 0.1078 | 0.016583 | -0.067209 | 0.12079 | 0.11939 | 0.21063 | 0.070073 | -122.2173 | 121.9503 | 122.2166 | 122.1328 | 0.49484 | -122.2818
2472.8594 | 122.2916 | -0.11902 | 122.1863 | -0.0025182 | -0.045196 | 0.041362 | 0.022247 | -0.011865 | -0.0046535 | -0.029148 | -0.0018394 | -0.0025041 | 0.058687 | 0.04197 | 0.048969 | -0.012688 | 0.010564 | -0.017566 | 0.056706 | 0.069043 | 0.15112 | -0.072215 | 0.074307 | 0.43534 | -0.028879 | 121.8954 | 122.1525 | 122.0779 | -0.1321 | 0.046804 | -122.1296 | 0.10633 | 0.10145 | 0.054649 | -122.1172 | -122.0352 | -0.013078 | -0.29091 | 0.19333 | 0.09014 | 0.10322 | -0.033772 | -0.10841 | 0.17572 | 0.18806 | 0.27014 | 0.12958 | -122.2585 | 122.0144 | 122.2715 | 122.1969 | 0.55436 | -122.3184
2474.5469 | 122.2824 | -0.11902 | 122.2046 | -0.010149 | -0.044983 | 0.041362 | 0.022033 | -0.012292 | -0.0046535 | -0.021518 | -0.0022666 | -0.0027177 | 0.058687 | 0.041329 | 0.048969 | -0.012688 | 0.010564 | -0.008409 | 0.061284 | 0.073622 | 0.15112 | -0.081373 | 0.078886 | 0.43992 | -0.038036 | 121.8954 | 122.1479 | 122.0779 | -0.14125 | 0.037646 | -122.1433 | 0.10633 | 0.11061 | 0.072964 | -122.131 | -122.0535 | -0.022236 | -0.30922 | 0.1979 | 0.080983 | 0.10322 | -0.056661 | -0.12672 | 0.1803 | 0.19264 | 0.27014 | 0.12958 | -122.286 | 122.0144 | 122.2669 | 122.1969 | 0.55893 | -122.3458
2476.2969 | 122.2916 | -0.091553 | 122.1725 | -0.010149 | -0.044769 | 0.041362 | 0.022247 | -0.011865 | -0.0044399 | -0.013887 | -0.0018394 | -0.0025041 | 0.058687 | 0.041756 | 0.049183 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.064464 | 0.1557 | -0.072215 | 0.078886 | 0.43534 | -0.042615 | 121.8908 | 122.1571 | 122.0733 | -0.14125 | 0.019338 | -122.1158 | 0.069709 | 0.078565 | 0.059227 | -122.1081 | -122.0168 | -0.049702 | -0.28175 | 0.17044 | 0.048938 | 0.09864 | -0.01546 | -0.099252 | 0.14826 | 0.15602 | 0.24726 | 0.10212 | -122.2448 | 121.9823 | 122.2486 | 122.1648 | 0.52689 | -122.3138
2478.0625 | 122.2641 | -0.1236 | 122.1634 | -0.010149 | -0.044983 | 0.040934 | 0.022247 | -0.011865 | -0.0046535 | -0.013887 | -0.0022666 | -0.0020767 | 0.058687 | 0.041329 | 0.048969 | -0.021844 | 0.005985 | -0.017566 | 0.056706 | 0.064464 | 0.1557 | -0.076794 | 0.083464 | 0.43076 | -0.042615 | 121.8954 | 122.1571 | 122.0733 | -0.14125 | 0.046802 | -122.1067 | 0.10175 | 0.10603 | 0.059228 | -122.0989 | -122.0077 | -0.017659 | -0.26802 | 0.20706 | 0.080981 | 0.09864 | -0.006305 | -0.090097 | 0.1803 | 0.18806 | 0.2793 | 0.12958 | -122.2402 | 122.019 | 122.2807 | 122.1969 | 0.55435 | -122.3046
2479.8281 | 122.3511 | -0.07782 | 122.168 | -0.010149 | -0.045196 | 0.041362 | 0.022033 | -0.011865 | -0.0044399 | -0.013887 | -0.0022666 | -0.0022903 | 0.058901 | 0.04197 | 0.048756 | -0.017266 | 0.010564 | -0.012988 | 0.056706 | 0.064464 | 0.1557 | -0.072215 | 0.083464 | 0.43992 | -0.038036 | 121.9 | 122.1571 | 122.0825 | -0.13668 | 0.005605 | -122.1113 | 0.060554 | 0.064832 | 0.059227 | -122.1035 | -122.0123 | -0.058856 | -0.26802 | 0.16128 | 0.039784 | 0.09864 | -0.010883 | -0.085518 | 0.13453 | 0.14228 | 0.23352 | 0.088384 | -122.2402 | 121.9778 | 122.2349 | 122.1603 | 0.51774 | -122.3046
2481.5938 | 123.8342 | -0.09613 | 122.1542 | -0.010149 | -0.044769 | 0.041148 | 0.022247 | -0.012292 | -0.0044399 | -0.013887 | -0.002053 | -0.0025041 | 0.058901 | 0.041756 | 0.048969 | 0.019361 | 0.30359 | 0.21135 | 0.056706 | 0.069043 | 0.1557 | -0.076794 | 0.2254 | 0.4216 | 0.2779 | 121.8908 | 122.1525 | 122.0641 | -0.13668 | 0.019336 | -122.0975 | 0.11549 | 0.30748 | 0.28814 | -122.0852 | -121.9985 | -0.040546 | -0.26344 | 0.32153 | 0.37402 | 0.41457 | -0.001729 | -0.090099 | 0.15284 | 0.16517 | 0.25183 | 0.39972 | -122.231 | 121.9869 | 122.2486 | 122.1603 | 0.51773 | -122.2909
2483.2969 | 122.4976 | -0.091553 | 122.1634 | -0.0025182 | -0.045196 | 0.041575 | 0.022247 | -0.011865 | -0.0044399 | -0.0062567 | -0.0024804 | -0.0022903 | 0.058901 | 0.04197 | 0.048756 | 0.15213 | 0.010564 | -0.017566 | 0.061284 | 0.069043 | 0.1557 | -0.076794 | 0.078886 | 0.55896 | -0.001407 | 121.8908 | 122.1617 | 122.0779 | -0.14125 | 0.014759 | -122.1021 | 0.24369 | 0.073987 | 0.059228 | -122.0943 | -122.0077 | -0.049702 | -0.2726 | 0.17044 | 0.090146 | 0.13985 | -0.001727 | -0.085519 | 0.15284 | 0.1606 | 0.24726 | 0.10212 | -122.2402 | 121.9823 | 122.2532 | 122.1694 | 0.65051 | -122.3046
2485.0469 | 122.5525 | -0.068665 | 122.1588 | -0.010149 | -0.044769 | 0.041148 | 0.022247 | -0.011865 | -0.0044399 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.041756 | 0.048756 | 0.17045 | 0.010564 | -0.022144 | 0.061284 | 0.059885 | 0.14655 | -0.076794 | 0.078886 | 0.44449 | 0.13595 | 121.9 | 122.1571 | 122.0825 | -0.14125 | -0.008129 | -122.0975 | 0.23911 | 0.046521 | 0.05465 | -122.0989 | -122.0123 | -0.07259 | -0.25886 | 0.14755 | 0.20462 | 0.27721 | -0.001727 | -0.076362 | 0.12995 | 0.12855 | 0.21521 | 0.079229 | -122.2356 | 121.9686 | 122.2258 | 122.1511 | 0.51316 | -122.3001
2486.8125 | 122.4792 | -0.054932 | 122.1542 | -0.010149 | -0.044983 | 0.041148 | 0.022247 | -0.012292 | -0.0046535 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.041542 | 0.048969 | 0.36274 | 0.051771 | -0.003831 | 0.056706 | 0.064464 | 0.14197 | -0.076794 | 0.092622 | 0.47197 | -0.019721 | 121.9 | 122.1479 | 122.0687 | -0.14125 | -0.021862 | -122.0975 | 0.41767 | 0.051101 | 0.072963 | -122.0898 | -122.0123 | -0.086323 | -0.25428 | 0.14755 | 0.035211 | 0.12153 | -0.006307 | -0.085521 | 0.11164 | 0.1194 | 0.1969 | 0.1067 | -122.231 | 121.9549 | 122.2029 | 122.1236 | 0.5269 | -122.2955
2488.5 | 122.3557 | -0.09613 | 122.1863 | -0.01778 | -0.045196 | 0.041148 | 0.022247 | -0.011865 | -0.0042263 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.042183 | 0.048756 | 0.019361 | 0.015142 | -0.012988 | 0.061284 | 0.069043 | 0.15112 | -0.076794 | 0.10178 | 0.43992 | -0.028879 | 121.8908 | 122.1571 | 122.087 | -0.14583 | 0.019336 | -122.125 | 0.11549 | 0.083142 | 0.063806 | -122.1172 | -122.0352 | -0.049703 | -0.29548 | 0.19791 | 0.067251 | 0.11695 | -0.029193 | -0.099249 | 0.15741 | 0.16517 | 0.24725 | 0.11127 | -122.2631 | 121.9869 | 122.2532 | 122.1832 | 0.53604 | -122.3321
2490.25 | 122.4014 | -0.068665 | 122.1634 | -0.0025182 | -0.044983 | 0.041148 | 0.022247 | -0.011865 | -0.0042263 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.041756 | 0.048542 | 0.037675 | 0.019721 | -0.012988 | 0.056706 | 0.069043 | 0.1557 | -0.072215 | 0.083464 | 0.44449 | -0.028879 | 121.9045 | 122.1662 | 122.0825 | -0.14125 | -0.00355 | -122.1067 | 0.10634 | 0.055677 | 0.059227 | -122.0943 | -122.0077 | -0.07259 | -0.25886 | 0.15213 | 0.039786 | 0.11238 | 0.002852 | -0.08094 | 0.12537 | 0.13771 | 0.22437 | 0.088386 | -122.2356 | 121.9732 | 122.2349 | 122.1511 | 0.51316 | -122.3046
2492.0156 | 122.3511 | -0.091553 | 122.1497 | -0.010149 | -0.045196 | 0.041148 | 0.021819 | -0.011865 | -0.0046535 | -0.021518 | -0.0018394 | -0.0020767 | 0.058901 | 0.04197 | 0.049183 | -0.017266 | 0.005985 | -0.008409 | 0.056706 | 0.069043 | 0.1557 | -0.072215 | 0.083464 | 0.44449 | -0.0243 | 121.9045 | 122.1571 | 122.0779 | -0.14125 | 0.019338 | -122.093 | 0.074287 | 0.083144 | 0.063806 | -122.0806 | -121.994 | -0.049702 | -0.24513 | 0.17502 | 0.067253 | 0.11695 | 0.007428 | -0.071786 | 0.14826 | 0.1606 | 0.24726 | 0.097538 | -122.2219 | 121.9961 | 122.2486 | 122.1694 | 0.53605 | -122.2909
2493.7031 | 122.374 | -0.07782 | 122.1634 | -0.010149 | -0.044983 | 0.041362 | 0.022033 | -0.012078 | -0.0044399 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.041756 | 0.049183 | -0.017266 | 0.010564 | -0.012988 | 0.061284 | 0.073622 | 0.16028 | -0.067636 | 0.097201 | 0.45823 | -0.038036 | 121.8908 | 122.1617 | 122.0825 | -0.14583 | 0.010184 | -122.1021 | 0.060554 | 0.064832 | 0.054648 | -122.0898 | -122.0031 | -0.068013 | -0.2726 | 0.17502 | 0.039784 | 0.1078 | -0.001727 | -0.08094 | 0.1391 | 0.15144 | 0.2381 | 0.088384 | -122.231 | 121.9686 | 122.2395 | 122.1603 | 0.53605 | -122.3092
2495.4375 | 122.3923 | -0.09613 | 122.1954 | -0.0025182 | -0.045196 | 0.041148 | 0.022247 | -0.012078 | -0.0042263 | -0.021518 | -0.002053 | -0.0022903 | 0.059114 | 0.042183 | 0.048969 | 0.010204 | 0.028878 | -0.008409 | 0.065863 | 0.064464 | 0.1557 | -0.072215 | 0.083464 | 0.46281 | -0.015143 | 121.8954 | 122.1617 | 122.0825 | -0.13668 | 0.023915 | -122.1296 | 0.10633 | 0.087721 | 0.063806 | -122.131 | -122.0397 | -0.040546 | -0.30006 | 0.17959 | 0.080987 | 0.12153 | -0.033771 | -0.11298 | 0.16199 | 0.16059 | 0.25183 | 0.12501 | -122.2677 | 121.9915 | 122.2578 | 122.1786 | 0.55894 | -122.3321
2497.1875 | 122.3373 | -0.10529 | 122.2 | -0.0025182 | -0.045196 | 0.041362 | 0.02246 | -0.011865 | -0.0046535 | -0.0062567 | -0.002053 | -0.0025041 | 0.058687 | 0.041756 | 0.048969 | 0.005626 | 0.019721 | -0.008409 | 0.056706 | 0.069043 | 0.14655 | -0.081373 | 0.088043 | 0.45365 | -0.0243 | 121.8908 | 122.1571 | 122.087 | -0.13668 | 0.023913 | -122.1433 | 0.11091 | 0.096877 | 0.072964 | -122.131 | -122.0535 | -0.03139 | -0.30922 | 0.19333 | 0.080986 | 0.11238 | -0.042926 | -0.11298 | 0.16199 | 0.17433 | 0.25183 | 0.12501 | -122.2814 | 121.9961 | 122.2624 | 122.1923 | 0.55894 | -122.3367
2498.9375 | 122.4518 | -0.050354 | 122.168 | -0.010149 | -0.044983 | 0.041362 | 0.022033 | -0.012078 | -0.0042263 | -0.029148 | -0.0022666 | -0.0020767 | 0.058901 | 0.041756 | 0.048969 | 0.001048 | 0.028878 | -0.017566 | 0.065863 | 0.064464 | 0.16028 | -0.076794 | 0.088043 | 0.45823 | -0.028879 | 121.9 | 122.1662 | 122.0825 | -0.14583 | -0.02644 | -122.1021 | 0.051402 | 0.032788 | 0.059228 | -122.1035 | -122.0077 | -0.095479 | -0.26802 | 0.1384 | 0.021475 | 0.11695 | -0.001726 | -0.085518 | 0.11622 | 0.11482 | 0.21063 | 0.079232 | -122.2448 | 121.9503 | 122.2166 | 122.1328 | 0.50858 | -122.3138
2500.6406 | 122.319 | -0.10071 | 122.2321 | -0.010149 | -0.045196 | 0.041575 | 0.02246 | -0.012078 | -0.0044399 | -0.029148 | -0.0022666 | -0.0022903 | 0.059114 | 0.041756 | 0.048756 | 0.005626 | 0.028878 | -0.012988 | 0.052128 | 0.064464 | 0.15112 | -0.076794 | 0.083464 | 0.45365 | -0.019721 | 121.9 | 122.1525 | 122.0962 | -0.14125 | 0.023914 | -122.1799 | 0.10633 | 0.08772 | 0.063806 | -122.1676 | -122.0809 | -0.040547 | -0.3321 | 0.18417 | 0.080987 | 0.12153 | -0.079549 | -0.13587 | 0.15284 | 0.16517 | 0.25183 | 0.12959 | -122.3089 | 122.0007 | 122.2532 | 122.1969 | 0.55436 | -122.3733
2502.3906 | 122.3465 | -0.11444 | 122.1725 | -0.010149 | -0.045196 | 0.041362 | 0.022247 | -0.012078 | -0.0044399 | -0.021518 | -0.002053 | -0.0025041 | 0.058687 | 0.041542 | 0.048969 | 0.010204 | 0.028878 | -0.003831 | 0.056706 | 0.064464 | 0.16028 | -0.072215 | 0.078886 | 0.45365 | -0.028879 | 121.9 | 122.1617 | 122.0825 | -0.14125 | 0.042226 | -122.1158 | 0.12465 | 0.11061 | 0.068384 | -122.1081 | -122.0123 | -0.026814 | -0.27259 | 0.19333 | 0.085562 | 0.11238 | -0.010882 | -0.090095 | 0.17115 | 0.1789 | 0.27472 | 0.14332 | -122.2448 | 122.0144 | 122.2761 | 122.1969 | 0.56809 | -122.3138
2504.1406 | 122.4243 | -0.073242 | 122.1634 | -0.025411 | -0.045196 | 0.041148 | 0.022033 | -0.011865 | -0.0040125 | -0.021518 | -0.0022666 | -0.0018631 | 0.058687 | 0.04197 | 0.048542 | 0.005626 | 0.028878 | -0.017566 | 0.065863 | 0.069043 | 0.16028 | -0.072215 | 0.088043 | 0.46281 | -0.015143 | 121.9091 | 122.1662 | 122.0825 | -0.14583 | 0.001027 | -122.0975 | 0.078868 | 0.055676 | 0.054649 | -122.0943 | -122.0031 | -0.072591 | -0.25428 | 0.16129 | 0.058099 | 0.13069 | 0.002852 | -0.08094 | 0.13911 | 0.14228 | 0.23352 | 0.10212 | -122.2356 | 121.9823 | 122.2395 | 122.1557 | 0.53605 | -122.3092
2505.8906 | 122.3373 | -0.091553 | 122.1451 | -0.010149 | -0.045196 | 0.041362 | 0.022033 | -0.011651 | -0.0040125 | -0.013887 | -0.002053 | -0.0020767 | 0.058901 | 0.041542 | 0.048969 | 0.005626 | 0.0243 | -0.012988 | 0.061284 | 0.073622 | 0.15112 | -0.072215 | 0.083464 | 0.45365 | -0.028879 | 121.9045 | 122.1617 | 122.087 | -0.14125 | 0.019338 | -122.0838 | 0.097179 | 0.078565 | 0.059227 | -122.0715 | -121.994 | -0.049702 | -0.24055 | 0.17502 | 0.062674 | 0.11238 | 0.016583 | -0.058051 | 0.15284 | 0.16518 | 0.24268 | 0.11585 | -122.2173 | 121.9961 | 122.2532 | 122.1786 | 0.5452 | -122.2863
2507.6406 | 122.4014 | -0.073242 | 122.1451 | 0.0051128 | -0.04541 | 0.041148 | 0.022033 | -0.011865 | -0.0040125 | -0.021518 | -0.0022666 | -0.0025041 | 0.058901 | 0.042397 | 0.048756 | 0.001048 | 0.028878 | -0.008409 | 0.061284 | 0.078201 | 0.15112 | -0.072215 | 0.083464 | 0.45823 | -0.033458 | 121.9137 | 122.1708 | 122.087 | -0.13668 | 0.001027 | -122.0838 | 0.07429 | 0.064833 | 0.063806 | -122.0669 | -121.994 | -0.063434 | -0.2314 | 0.15671 | 0.039784 | 0.10322 | 0.025741 | -0.058051 | 0.13453 | 0.15144 | 0.22437 | 0.10212 | -122.2173 | 121.9869 | 122.2441 | 122.1603 | 0.53147 | -122.2818
2509.3906 | 122.4289 | -0.064087 | 122.1405 | 0.0051128 | -0.045196 | 0.040934 | 0.021819 | -0.011865 | -0.0037989 | -0.029148 | -0.0022666 | -0.0020767 | 0.058473 | 0.04197 | 0.048969 | 0.005626 | 0.0243 | -0.008409 | 0.065863 | 0.064464 | 0.1557 | -0.072215 | 0.083464 | 0.45365 | -0.033458 | 121.9045 | 122.1617 | 122.0962 | -0.13668 | -0.008128 | -122.0746 | 0.069713 | 0.055678 | 0.063806 | -122.076 | -121.9848 | -0.072589 | -0.23597 | 0.14755 | 0.030629 | 0.10322 | 0.021161 | -0.044316 | 0.12995 | 0.12855 | 0.21979 | 0.088387 | -122.2127 | 121.9686 | 122.2258 | 122.1603 | 0.51774 | -122.2772
2511.0938 | 122.4289 | -0.054932 | 122.1268 | -0.010149 | -0.04541 | 0.041148 | 0.021606 | -0.011865 | -0.0040125 | -0.021518 | -0.0022666 | -0.0022903 | 0.059114 | 0.04197 | 0.048969 | 0.001048 | 0.0243 | -0.008409 | 0.056706 | 0.073622 | 0.1557 | -0.076794 | 0.083464 | 0.46281 | -0.019721 | 121.9091 | 122.1571 | 122.087 | -0.14583 | -0.021862 | -122.0701 | 0.05598 | 0.046523 | 0.068385 | -122.0531 | -121.9711 | -0.090901 | -0.21766 | 0.1384 | 0.035211 | 0.12611 | 0.030316 | -0.03974 | 0.11164 | 0.12855 | 0.21063 | 0.079232 | -122.2036 | 121.964 | 122.212 | 122.142 | 0.51774 | -122.2726
2512.8594 | 122.4289 | -0.059509 | 122.1542 | -0.010149 | -0.04541 | 0.041362 | 0.022033 | -0.011865 | -0.0040125 | -0.021518 | -0.002053 | -0.0020767 | 0.058687 | 0.041542 | 0.048969 | -0.003531 | 0.0243 | -0.012988 | 0.061284 | 0.069043 | 0.15112 | -0.076794 | 0.092622 | 0.45365 | -0.019721 | 121.9045 | 122.1662 | 122.087 | -0.13668 | -0.017285 | -122.093 | 0.055978 | 0.046521 | 0.063806 | -122.0852 | -122.0031 | -0.077167 | -0.24971 | 0.15213 | 0.039788 | 0.11695 | 0.012007 | -0.067206 | 0.12079 | 0.12855 | 0.21063 | 0.083809 | -122.231 | 121.964 | 122.2258 | 122.1465 | 0.51316 | -122.2909
2514.625 | 122.2778 | -0.10986 | 122.2092 | -0.0025182 | -0.045196 | 0.041148 | 0.022033 | -0.012292 | -0.0042263 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058901 | 0.04197 | 0.048969 | 0.014783 | 0.019721 | -0.017566 | 0.056706 | 0.073622 | 0.16028 | -0.076794 | 0.12467 | 0.43992 | -0.033458 | 121.9045 | 122.1617 | 122.0962 | -0.14125 | 0.033069 | -122.1525 | 0.12465 | 0.092297 | 0.059228 | -122.1355 | -122.0489 | -0.031392 | -0.30464 | 0.23454 | 0.076405 | 0.1078 | -0.047503 | -0.11298 | 0.16657 | 0.18349 | 0.27014 | 0.12958 | -122.286 | 122.0144 | 122.2715 | 122.2061 | 0.54978 | -122.3504
2516.3125 | 122.287 | -0.10986 | 122.2046 | -0.0025182 | -0.04541 | 0.041362 | 0.022033 | -0.011651 | -0.0042263 | -0.013887 | -0.002053 | -0.0020767 | 0.058901 | 0.041756 | 0.049397 | 0.055988 | 0.038035 | -0.008409 | 0.061284 | 0.064464 | 0.16028 | -0.076794 | 0.10636 | 0.44907 | -0.033458 | 121.9 | 122.1662 | 122.087 | -0.13668 | 0.033069 | -122.1433 | 0.16585 | 0.10145 | 0.068385 | -122.1401 | -122.0443 | -0.026813 | -0.30464 | 0.21622 | 0.076405 | 0.10322 | -0.038347 | -0.11756 | 0.17115 | 0.17433 | 0.27014 | 0.1479 | -122.2814 | 122.0098 | 122.2761 | 122.1969 | 0.55894 | -122.3413
2518.0625 | 122.319 | -0.082397 | 122.1634 | -0.010149 | -0.04541 | 0.041148 | 0.02246 | -0.012506 | -0.0037989 | -0.013887 | -0.0022666 | -0.0027177 | 0.058473 | 0.04197 | 0.049183 | 0.083459 | 0.042614 | -0.008409 | 0.061284 | 0.064464 | 0.15112 | -0.081373 | 0.097201 | 0.44907 | -0.0243 | 121.9045 | 122.1662 | 122.087 | -0.14125 | 0.001024 | -122.1021 | 0.16586 | 0.073988 | 0.072964 | -122.0989 | -122.0123 | -0.058858 | -0.25886 | 0.1796 | 0.058097 | 0.11695 | 0.002852 | -0.076361 | 0.14368 | 0.14686 | 0.23352 | 0.12501 | -122.2448 | 121.9869 | 122.2486 | 122.1694 | 0.53147 | -122.3046
2519.8125 | 122.3145 | -0.086975 | 122.1863 | -0.01778 | -0.045196 | 0.040934 | 0.022033 | -0.011865 | -0.0040125 | -0.013887 | -0.0024804 | -0.0022903 | 0.058473 | 0.042397 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.061284 | 0.069043 | 0.1557 | -0.081373 | 0.078886 | 0.43992 | -0.038036 | 121.9045 | 122.1662 | 122.087 | -0.14125 | 0.005602 | -122.125 | 0.069709 | 0.073987 | 0.068385 | -122.1172 | -122.0306 | -0.05428 | -0.28175 | 0.16586 | 0.048939 | 0.10322 | -0.020036 | -0.099249 | 0.14826 | 0.15602 | 0.24268 | 0.10212 | -122.2677 | 121.9915 | 122.2532 | 122.174 | 0.52689 | -122.3275
2521.5 | 122.3282 | -0.10529 | 122.1863 | 0.0051128 | -0.04541 | 0.041148 | 0.022033 | -0.011865 | -0.0040125 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.041756 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.056706 | 0.064464 | 0.15112 | -0.076794 | 0.083464 | 0.43992 | -0.038036 | 121.9045 | 122.1708 | 122.0962 | -0.13668 | 0.028492 | -122.1296 | 0.08802 | 0.092298 | 0.063806 | -122.1218 | -122.0352 | -0.03139 | -0.28175 | 0.18875 | 0.06725 | 0.09864 | -0.015457 | -0.090092 | 0.16199 | 0.16975 | 0.25641 | 0.12043 | -122.2631 | 122.0098 | 122.2761 | 122.2015 | 0.5452 | -122.323
2523.2656 | 122.3053 | -0.11902 | 122.1771 | -0.0025182 | -0.045196 | 0.041362 | 0.022033 | -0.012078 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.058687 | 0.04197 | 0.048969 | -0.012688 | 0.015142 | -0.017566 | 0.056706 | 0.069043 | 0.1557 | -0.081373 | 0.078886 | 0.43534 | -0.033458 | 121.9091 | 122.1708 | 122.087 | -0.14125 | 0.037646 | -122.1204 | 0.10633 | 0.10145 | 0.063807 | -122.1081 | -122.0214 | -0.022236 | -0.26802 | 0.1979 | 0.085561 | 0.1078 | -0.006302 | -0.090094 | 0.17572 | 0.18806 | 0.27472 | 0.13416 | -122.2585 | 122.0281 | 122.2898 | 122.206 | 0.55436 | -122.3184
2525.0312 | 122.3785 | -0.07782 | 122.1542 | -0.0025182 | -0.045624 | 0.041575 | 0.021819 | -0.012078 | -0.0040125 | -0.029148 | -0.002053 | -0.0025041 | 0.058901 | 0.04197 | 0.049183 | -0.021844 | 0.019721 | -0.017566 | 0.056706 | 0.059885 | 0.15112 | -0.076794 | 0.078886 | 0.44449 | -0.038036 | 121.9045 | 122.1708 | 122.0916 | -0.14125 | 0.001026 | -122.0975 | 0.055976 | 0.060254 | 0.059228 | -122.0944 | -122.0031 | -0.063435 | -0.24971 | 0.15671 | 0.039784 | 0.10322 | 0.016586 | -0.062628 | 0.13453 | 0.1377 | 0.22894 | 0.097541 | -122.231 | 121.9823 | 122.2486 | 122.1694 | 0.52231 | -122.2955
2526.7812 | 122.3831 | -0.082397 | 122.1542 | -0.010149 | -0.045196 | 0.041362 | 0.022247 | -0.011865 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.058901 | 0.042611 | 0.048969 | -0.012688 | 0.015142 | -0.017566 | 0.061284 | 0.073622 | 0.1557 | -0.072215 | 0.088043 | 0.44907 | -0.033458 | 121.9137 | 122.1708 | 122.0916 | -0.14125 | 0.010182 | -122.093 | 0.069709 | 0.064831 | 0.054649 | -122.0806 | -121.9985 | -0.058858 | -0.24055 | 0.17044 | 0.048939 | 0.1078 | 0.016586 | -0.062628 | 0.14368 | 0.15602 | 0.2381 | 0.097539 | -122.2265 | 121.9961 | 122.2532 | 122.174 | 0.53147 | -122.2955
2528.4844 | 122.3145 | -0.10529 | 122.1863 | 0.0051128 | -0.045196 | 0.041148 | 0.022033 | -0.011865 | -0.0037989 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.041756 | 0.048969 | -0.021844 | 0.010564 | -0.012988 | 0.056706 | 0.073622 | 0.15112 | -0.072215 | 0.078886 | 0.43534 | -0.033458 | 121.9045 | 122.1662 | 122.0916 | -0.14125 | 0.033071 | -122.1296 | 0.083442 | 0.092298 | 0.059227 | -122.1127 | -122.0352 | -0.035969 | -0.28175 | 0.18417 | 0.071828 | 0.1078 | -0.020036 | -0.094671 | 0.16199 | 0.17891 | 0.25641 | 0.11585 | -122.2585 | 122.0098 | 122.2715 | 122.1969 | 0.54062 | -122.3275
2530.2344 | 122.3648 | -0.073242 | 122.1725 | -0.01778 | -0.04541 | 0.041148 | 0.021819 | -0.011651 | -0.0040125 | -0.029148 | -0.0024804 | -0.0022903 | 0.058901 | 0.042183 | 0.048756 | -0.021844 | 0.010564 | -0.008409 | 0.065863 | 0.069043 | 0.1557 | -0.076794 | 0.078886 | 0.44449 | -0.033458 | 121.9137 | 122.1708 | 122.0916 | -0.13668 | -0.003552 | -122.1067 | 0.051398 | 0.064833 | 0.068385 | -122.1035 | -122.0168 | -0.063434 | -0.25886 | 0.15213 | 0.039784 | 0.10322 | -0.001724 | -0.080938 | 0.13911 | 0.14228 | 0.22894 | 0.083806 | -122.2493 | 121.9869 | 122.2441 | 122.1648 | 0.51774 | -122.3092
2531.9844 | 122.3694 | -0.07782 | 122.1817 | -0.01778 | -0.044983 | 0.041362 | 0.022033 | -0.011651 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.04197 | 0.048542 | -0.021844 | 0.015142 | -0.017566 | 0.065863 | 0.064464 | 0.15112 | -0.081373 | 0.078886 | 0.44907 | -0.033458 | 121.9091 | 122.1754 | 122.0916 | -0.13668 | -0.003553 | -122.1158 | 0.055976 | 0.060254 | 0.063807 | -122.1172 | -122.0306 | -0.058856 | -0.27259 | 0.15671 | 0.044362 | 0.10322 | -0.006302 | -0.090094 | 0.14368 | 0.14228 | 0.22894 | 0.092962 | -122.2631 | 121.9869 | 122.2532 | 122.1694 | 0.52689 | -122.3184
2533.6719 | 122.2733 | -0.10529 | 122.2229 | -0.010149 | -0.04541 | 0.041148 | 0.021606 | -0.012078 | -0.0037989 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.04197 | 0.048542 | -0.017266 | 0.015142 | -0.012988 | 0.065863 | 0.069043 | 0.1557 | -0.076794 | 0.078886 | 0.44907 | -0.038036 | 121.9091 | 122.1754 | 122.0962 | -0.15041 | 0.028492 | -122.157 | 0.08802 | 0.092298 | 0.063806 | -122.1539 | -122.0672 | -0.045126 | -0.31379 | 0.18417 | 0.06725 | 0.11238 | -0.0475 | -0.12671 | 0.17115 | 0.17433 | 0.26099 | 0.12043 | -122.2997 | 122.0144 | 122.2807 | 122.2015 | 0.55436 | -122.3733
2535.4219 | 122.3877 | -0.054932 | 122.1634 | -0.010149 | -0.045624 | 0.041362 | 0.022033 | -0.012078 | -0.0037989 | -0.013887 | -0.002053 | -0.0018631 | 0.058901 | 0.042183 | 0.049183 | -0.021844 | 0.015142 | -0.022144 | 0.061284 | 0.069043 | 0.15112 | -0.081373 | 0.074307 | 0.43992 | -0.038036 | 121.9091 | 122.1708 | 122.0962 | -0.14583 | -0.026441 | -122.1021 | 0.033088 | 0.032788 | 0.059229 | -122.0943 | -122.0123 | -0.090901 | -0.25428 | 0.12924 | 0.016896 | 0.1078 | 0.007431 | -0.067204 | 0.11622 | 0.12398 | 0.20606 | 0.070074 | -122.2448 | 121.964 | 122.2258 | 122.1511 | 0.49485 | -122.3092
2537.1875 | 122.3236 | -0.091553 | 122.2046 | -0.01778 | -0.04541 | 0.041362 | 0.022033 | -0.011865 | -0.0040125 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.04197 | 0.048969 | -0.017266 | 0.015142 | -0.017566 | 0.056706 | 0.064464 | 0.15112 | -0.076794 | 0.083464 | 0.44907 | -0.028879 | 121.9137 | 122.1662 | 122.0962 | -0.14125 | 0.014759 | -122.1479 | 0.074287 | 0.073987 | 0.059228 | -122.1401 | -122.0535 | -0.049702 | -0.2909 | 0.17502 | 0.062674 | 0.11238 | -0.038347 | -0.1084 | 0.14826 | 0.15602 | 0.24268 | 0.10669 | -122.2814 | 122.0052 | 122.2578 | 122.1877 | 0.54063 | -122.3458
2538.9531 | 122.319 | -0.10986 | 122.1954 | -0.010149 | -0.04541 | 0.041148 | 0.021819 | -0.011865 | -0.0035853 | -0.013887 | -0.002053 | -0.0027177 | 0.058687 | 0.04197 | 0.049183 | -0.012688 | 0.005985 | -0.022144 | 0.065863 | 0.073622 | 0.16028 | -0.081373 | 0.088043 | 0.43992 | -0.0243 | 121.9091 | 122.18 | 122.0962 | -0.14125 | 0.02849 | -122.1296 | 0.097175 | 0.087719 | 0.059229 | -122.1218 | -122.0352 | -0.031392 | -0.28633 | 0.19791 | 0.085563 | 0.11695 | -0.015456 | -0.099248 | 0.17573 | 0.18349 | 0.27014 | 0.11585 | -122.2768 | 122.019 | 122.2898 | 122.2061 | 0.54978 | -122.3367
2540.7031 | 122.2961 | -0.10071 | 122.2 | 0.0051128 | -0.04541 | 0.041148 | 0.022033 | -0.011865 | -0.0035853 | -0.0062567 | -0.002053 | -0.0022903 | 0.058901 | 0.042183 | 0.049183 | -0.021844 | 0.019721 | -0.012988 | 0.061284 | 0.069043 | 0.1557 | -0.076794 | 0.083464 | 0.44449 | -0.033458 | 121.9091 | 122.1754 | 122.1008 | -0.13668 | 0.023914 | -122.1387 | 0.078864 | 0.08772 | 0.063806 | -122.131 | -122.0443 | -0.035968 | -0.2909 | 0.18417 | 0.06725 | 0.10322 | -0.024612 | -0.099247 | 0.16199 | 0.16975 | 0.25641 | 0.12043 | -122.2768 | 122.0098 | 122.2761 | 122.2015 | 0.5452 | -122.3367
2542.3906 | 122.3236 | -0.073242 | 122.1817 | -0.01778 | -0.045196 | 0.040934 | 0.022247 | -0.012078 | -0.0037989 | -0.013887 | -0.0022666 | -0.0022903 | 0.058687 | 0.04197 | 0.048756 | -0.017266 | 0.015142 | -0.022144 | 0.065863 | 0.069043 | 0.16028 | -0.072215 | 0.092622 | 0.45365 | -0.038036 | 121.9091 | 122.1708 | 122.0962 | -0.13668 | 0.001027 | -122.1158 | 0.055976 | 0.051098 | 0.050071 | -122.1127 | -122.0214 | -0.063434 | -0.27259 | 0.16586 | 0.035206 | 0.09864 | -0.01088 | -0.085515 | 0.13911 | 0.14228 | 0.23352 | 0.088384 | -122.2539 | 121.9823 | 122.2441 | 122.1694 | 0.52689 | -122.3184
2544.1406 | 122.3602 | -0.068665 | 122.1634 | -0.0025182 | -0.04541 | 0.041148 | 0.021606 | -0.012078 | -0.0035853 | -0.029148 | -0.0022666 | -0.0022903 | 0.058687 | 0.042183 | 0.048756 | -0.017266 | 0.015142 | -0.017566 | 0.056706 | 0.069043 | 0.16028 | -0.072215 | 0.088043 | 0.44907 | -0.033458 | 121.9137 | 122.1754 | 122.1008 | -0.13668 | -0.00355 | -122.1067 | 0.051399 | 0.051099 | 0.054649 | -122.0943 | -122.0031 | -0.068011 | -0.24971 | 0.15671 | 0.035207 | 0.10322 | 0.012009 | -0.062626 | 0.12537 | 0.13771 | 0.22895 | 0.083807 | -122.2356 | 121.9824 | 122.2441 | 122.1694 | 0.51774 | -122.3001
2545.8906 | 122.2687 | -0.091553 | 122.2137 | -0.0025182 | -0.045624 | 0.041148 | 0.022033 | -0.012078 | -0.0037989 | -0.021518 | -0.002053 | -0.0025041 | 0.058901 | 0.042183 | 0.048969 | -0.017266 | 0.019721 | -0.017566 | 0.061284 | 0.073622 | 0.1557 | -0.072215 | 0.083464 | 0.44907 | -0.033458 | 121.9091 | 122.1754 | 122.0962 | -0.15041 | 0.019338 | -122.1525 | 0.074287 | 0.073987 | 0.054649 | -122.1401 | -122.058 | -0.058859 | -0.30464 | 0.17502 | 0.058095 | 0.11695 | -0.038345 | -0.11756 | 0.15284 | 0.16518 | 0.24726 | 0.11127 | -122.286 | 122.0007 | 122.267 | 122.1877 | 0.54063 | -122.3642
2547.6406 | 122.3145 | -0.10529 | 122.168 | -0.010149 | -0.04541 | 0.040934 | 0.021819 | -0.011865 | -0.0037989 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.041756 | 0.048542 | -0.017266 | 0.015142 | -0.017566 | 0.056706 | 0.078201 | 0.16028 | -0.076794 | 0.078886 | 0.44907 | -0.038036 | 121.9137 | 122.1708 | 122.1008 | -0.14125 | 0.028492 | -122.1113 | 0.08802 | 0.08772 | 0.059228 | -122.0898 | -122.0077 | -0.035969 | -0.25428 | 0.18417 | 0.06725 | 0.10322 | 0.002853 | -0.067204 | 0.16199 | 0.18349 | 0.26557 | 0.12043 | -122.2448 | 122.019 | 122.2761 | 122.2061 | 0.55436 | -122.3092
2549.3281 | 122.3602 | -0.082397 | 122.1405 | -0.010149 | -0.04541 | 0.040934 | 0.021819 | -0.011865 | -0.0042263 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.04197 | 0.048756 | -0.017266 | 0.019721 | -0.022144 | 0.056706 | 0.069043 | 0.16486 | -0.081373 | 0.074307 | 0.45365 | -0.033458 | 121.9183 | 122.1754 | 122.0916 | -0.13668 | 0.001024 | -122.0838 | 0.065131 | 0.060253 | 0.059229 | -122.0715 | -121.9756 | -0.054279 | -0.22224 | 0.1567 | 0.048939 | 0.10322 | 0.034897 | -0.048895 | 0.1391 | 0.15144 | 0.24726 | 0.10212 | -122.2219 | 122.0007 | 122.2578 | 122.174 | 0.53605 | -122.2772
2551.0938 | 122.3557 | -0.086975 | 122.168 | -0.010149 | -0.045624 | 0.041148 | 0.022033 | -0.011865 | -0.0040125 | -0.013887 | -0.0016258 | -0.0025041 | 0.058901 | 0.042397 | 0.049183 | -0.017266 | 0.015142 | -0.017566 | 0.070441 | 0.073622 | 0.1557 | -0.076794 | 0.078886 | 0.44907 | -0.042615 | 121.9228 | 122.18 | 122.1008 | -0.14583 | 0.010181 | -122.0975 | 0.069709 | 0.069409 | 0.059228 | -122.0943 | -122.0123 | -0.058858 | -0.24513 | 0.16586 | 0.04436 | 0.10322 | 0.01201 | -0.067204 | 0.15742 | 0.1606 | 0.24268 | 0.10212 | -122.2448 | 122.0098 | 122.267 | 122.1877 | 0.53605 | -122.3138
2552.7812 | 122.2961 | -0.10071 | 122.2137 | -0.01778 | -0.045624 | 0.040934 | 0.022033 | -0.011865 | -0.0037989 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.042183 | 0.048969 | -0.012688 | 0.015142 | -0.022144 | 0.061284 | 0.064464 | 0.1557 | -0.081373 | 0.078886 | 0.44907 | -0.047194 | 121.9228 | 122.18 | 122.0962 | -0.13668 | 0.019335 | -122.1525 | 0.08802 | 0.078564 | 0.059229 | -122.1493 | -122.058 | -0.035968 | -0.2909 | 0.17959 | 0.053514 | 0.089482 | -0.033766 | -0.11756 | 0.16199 | 0.16517 | 0.25641 | 0.11585 | -122.2951 | 122.0236 | 122.2807 | 122.1969 | 0.54978 | -122.3504
2554.5312 | 122.287 | -0.10071 | 122.1909 | -0.0025182 | -0.045196 | 0.040934 | 0.021819 | -0.012078 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.042183 | 0.048969 | -0.026423 | 0.015142 | -0.017566 | 0.061284 | 0.069043 | 0.1557 | -0.076794 | 0.083464 | 0.44907 | -0.038036 | 121.9091 | 122.18 | 122.1008 | -0.14125 | 0.023914 | -122.1296 | 0.074285 | 0.083142 | 0.059228 | -122.1218 | -122.0352 | -0.040547 | -0.28175 | 0.18417 | 0.062672 | 0.10322 | -0.010878 | -0.090092 | 0.16199 | 0.16975 | 0.25641 | 0.11585 | -122.2677 | 122.0098 | 122.2807 | 122.2015 | 0.54978 | -122.3321
2556.2812 | 122.4289 | -0.059509 | 122.1542 | -0.010149 | -0.045837 | 0.040934 | 0.022033 | -0.011865 | -0.0037989 | -0.029148 | -0.0018394 | -0.0022903 | 0.058687 | 0.042183 | 0.048756 | -0.021844 | 0.015142 | -0.022144 | 0.061284 | 0.069043 | 0.16486 | -0.081373 | 0.078886 | 0.44449 | -0.028879 | 121.9274 | 122.1708 | 122.0916 | -0.13668 | -0.021864 | -122.093 | 0.037665 | 0.037365 | 0.059229 | -122.0852 | -121.9894 | -0.077167 | -0.22681 | 0.13839 | 0.03063 | 0.1078 | 0.016586 | -0.062628 | 0.12079 | 0.12855 | 0.22437 | 0.074651 | -122.2356 | 121.9869 | 122.2303 | 122.1511 | 0.504 | -122.2909
2558.0312 | 122.3099 | -0.10071 | 122.1817 | -0.0025182 | -0.045196 | 0.041148 | 0.021819 | -0.011651 | -0.0033715 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.042183 | 0.048969 | -0.008109 | 0.015142 | -0.017566 | 0.061284 | 0.064464 | 0.16028 | -0.085952 | 0.083464 | 0.45823 | -0.028879 | 121.9183 | 122.1754 | 122.0962 | -0.13668 | 0.014756 | -122.1204 | 0.092599 | 0.083142 | 0.068386 | -122.1172 | -122.0214 | -0.035968 | -0.26344 | 0.18417 | 0.071829 | 0.1078 | -0.006302 | -0.085515 | 0.16199 | 0.16517 | 0.26099 | 0.11585 | -122.2677 | 122.019 | 122.2761 | 122.1969 | 0.55894 | -122.3184
2559.7188 | 122.3419 | -0.07782 | 122.1725 | -0.01778 | -0.045624 | 0.041362 | 0.021819 | -0.011865 | -0.0037989 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.042397 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.061284 | 0.069043 | 0.1557 | -0.081373 | 0.083464 | 0.45365 | -0.033458 | 121.9091 | 122.1754 | 122.1008 | -0.14583 | -0.003553 | -122.1113 | 0.060554 | 0.064832 | 0.068385 | -122.1035 | -122.0168 | -0.068013 | -0.26344 | 0.16128 | 0.044362 | 0.11237 | 0.002854 | -0.071781 | 0.1391 | 0.14686 | 0.23352 | 0.092962 | -122.2539 | 121.9869 | 122.2532 | 122.1786 | 0.53147 | -122.3184
2561.4688 | 122.2961 | -0.09613 | 122.1954 | -0.0025182 | -0.045837 | 0.041148 | 0.021819 | -0.011865 | -0.0037989 | -0.021518 | -0.0024804 | -0.0025041 | 0.058687 | 0.042397 | 0.048969 | -0.021844 | 0.015142 | -0.022144 | 0.056706 | 0.064464 | 0.16028 | -0.072215 | 0.083464 | 0.44449 | -0.033458 | 121.9137 | 122.1846 | 122.1008 | -0.13668 | 0.023915 | -122.1387 | 0.074286 | 0.073986 | 0.050071 | -122.131 | -122.0352 | -0.040546 | -0.28175 | 0.17959 | 0.062672 | 0.10322 | -0.010878 | -0.09467 | 0.15284 | 0.16059 | 0.25641 | 0.11127 | -122.2677 | 122.0098 | 122.2807 | 122.1969 | 0.54062 | -122.3321
2563.2344 | 122.3419 | -0.082397 | 122.1725 | -0.01778 | -0.045837 | 0.041362 | 0.021819 | -0.012078 | -0.0037989 | -0.013887 | -0.0022666 | -0.0022903 | 0.058901 | 0.042183 | 0.048756 | -0.012688 | 0.015142 | -0.012988 | 0.061284 | 0.069043 | 0.16028 | -0.072215 | 0.083464 | 0.45365 | -0.033458 | 121.9137 | 122.18 | 122.1008 | -0.13668 | 0.010182 | -122.1113 | 0.069709 | 0.069409 | 0.059227 | -122.1035 | -122.0123 | -0.054279 | -0.25886 | 0.16586 | 0.048939 | 0.10322 | 0.007433 | -0.071781 | 0.14368 | 0.15144 | 0.24268 | 0.097539 | -122.2448 | 121.9961 | 122.2624 | 122.1832 | 0.53605 | -122.3092
2564.9844 | 122.2687 | -0.09613 | 122.2229 | -0.010149 | -0.045624 | 0.041362 | 0.022033 | -0.012078 | -0.0037989 | -0.013887 | -0.0018394 | -0.0020767 | 0.058687 | 0.042183 | 0.048969 | -0.017266 | 0.010564 | -0.026723 | 0.061284 | 0.069043 | 0.16028 | -0.076794 | 0.078886 | 0.45823 | -0.033458 | 121.9091 | 122.18 | 122.1053 | -0.1321 | 0.019336 | -122.1616 | 0.078864 | 0.069407 | 0.050071 | -122.1539 | -122.0626 | -0.035967 | -0.31379 | 0.17502 | 0.062672 | 0.098639 | -0.042921 | -0.11756 | 0.15741 | 0.16517 | 0.25641 | 0.10669 | -122.2997 | 122.0052 | 122.2761 | 122.2015 | 0.55436 | -122.355
2566.6719 | 122.319 | -0.082397 | 122.2137 | -0.010149 | -0.04541 | 0.041362 | 0.022033 | -0.011865 | -0.0035853 | -0.021518 | -0.0022666 | -0.0018631 | 0.058901 | 0.042183 | 0.048969 | -0.012688 | 0.015142 | -0.017566 | 0.061284 | 0.064464 | 0.16486 | -0.081373 | 0.083464 | 0.45823 | -0.028879 | 121.9137 | 122.1846 | 122.1053 | -0.13668 | 0.001024 | -122.1525 | 0.069709 | 0.064831 | 0.063807 | -122.1493 | -122.0489 | -0.054279 | -0.30006 | 0.16586 | 0.053518 | 0.1078 | -0.029188 | -0.1084 | 0.14368 | 0.14686 | 0.24726 | 0.097539 | -122.2951 | 121.9961 | 122.267 | 122.1877 | 0.54063 | -122.3504
2568.4219 | 122.4289 | -0.073242 | 122.1588 | -0.01778 | -0.04541 | 0.040934 | 0.021606 | -0.011865 | -0.0035853 | -0.013887 | -0.002053 | -0.0020767 | 0.058901 | 0.042183 | 0.048969 | -0.012688 | 0.015142 | -0.012988 | 0.065863 | 0.059885 | 0.16028 | -0.076794 | 0.083464 | 0.44449 | -0.033458 | 121.9183 | 122.1891 | 122.1008 | -0.14125 | -0.003552 | -122.093 | 0.060554 | 0.060254 | 0.063806 | -122.0989 | -121.9985 | -0.068013 | -0.24055 | 0.15671 | 0.039784 | 0.1078 | 0.030323 | -0.058048 | 0.13911 | 0.13313 | 0.23352 | 0.088384 | -122.2356 | 121.9915 | 122.2624 | 122.174 | 0.51774 | -122.3001
2570.1719 | 122.3923 | -0.07782 | 122.1817 | -0.0025182 | -0.045837 | 0.040934 | 0.022033 | -0.011865 | -0.0033715 | -0.013887 | -0.002053 | -0.0025041 | 0.059114 | 0.042824 | 0.048756 | -0.017266 | 0.019721 | -0.022144 | 0.061284 | 0.064464 | 0.16028 | -0.072215 | 0.083464 | 0.46281 | -0.038036 | 121.9183 | 122.1891 | 122.1008 | -0.13668 | 0.005605 | -122.1204 | 0.060554 | 0.055676 | 0.050071 | -122.1172 | -122.0214 | -0.058856 | -0.26344 | 0.16128 | 0.039784 | 0.09864 | 0.007434 | -0.080937 | 0.1391 | 0.14228 | 0.2381 | 0.097541 | -122.2539 | 121.9961 | 122.267 | 122.1786 | 0.54063 | -122.3184
2571.8594 | 122.3831 | -0.064087 | 122.1909 | -0.010149 | -0.045624 | 0.040934 | 0.022033 | -0.012078 | -0.0035853 | 0.0013733 | -0.0018394 | -0.0018631 | 0.058473 | 0.042397 | 0.048756 | -0.021844 | 0.019721 | -0.012988 | 0.061284 | 0.069043 | 0.16486 | -0.072215 | 0.083464 | 0.45823 | -0.033458 | 121.9183 | 122.1846 | 122.1008 | -0.14583 | -0.008128 | -122.1296 | 0.042243 | 0.051099 | 0.059227 | -122.1218 | -122.026 | -0.081746 | -0.27259 | 0.14755 | 0.030629 | 0.11237 | -0.0063 | -0.090092 | 0.12537 | 0.13313 | 0.22895 | 0.083808 | -122.2631 | 121.9824 | 122.2486 | 122.1649 | 0.52232 | -122.3367
2573.625 | 122.2687 | -0.10529 | 122.2046 | -0.010149 | -0.045624 | 0.041148 | 0.021606 | -0.012078 | -0.0033715 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.042397 | 0.048969 | -0.012688 | 0.015142 | -0.012988 | 0.065863 | 0.073622 | 0.16028 | -0.081373 | 0.088043 | 0.45365 | -0.028879 | 121.9091 | 122.1846 | 122.1008 | -0.14583 | 0.023913 | -122.1387 | 0.092598 | 0.092298 | 0.068385 | -122.131 | -122.0443 | -0.040547 | -0.29548 | 0.19333 | 0.076407 | 0.11695 | -0.020033 | -0.10383 | 0.17115 | 0.17891 | 0.26557 | 0.12043 | -122.286 | 122.0144 | 122.2898 | 122.2061 | 0.55894 | -122.3504
2575.3906 | 122.2641 | -0.10071 | 122.1909 | -0.01778 | -0.045624 | 0.040934 | 0.021819 | -0.012078 | -0.0037989 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.042183 | 0.048756 | -0.012688 | 0.015142 | -0.008409 | 0.061284 | 0.064464 | 0.16028 | -0.067636 | 0.083464 | 0.45823 | -0.033458 | 121.9183 | 122.1891 | 122.1053 | -0.13668 | 0.033072 | -122.1296 | 0.08802 | 0.092299 | 0.059227 | -122.1264 | -122.0306 | -0.035968 | -0.27259 | 0.18417 | 0.06725 | 0.10322 | -0.001721 | -0.085513 | 0.16199 | 0.16517 | 0.26099 | 0.11585 | -122.2585 | 122.019 | 122.2898 | 122.2061 | 0.55894 | -122.3275
2577.1406 | 122.287 | -0.09613 | 122.1909 | -0.010149 | -0.04541 | 0.041148 | 0.021819 | -0.011865 | -0.0033715 | -0.013887 | -0.0022666 | -0.0025041 | 0.058901 | 0.042183 | 0.048542 | -0.008109 | 0.015142 | -0.022144 | 0.056706 | 0.073622 | 0.1557 | -0.076794 | 0.088043 | 0.45365 | -0.033458 | 121.9183 | 122.18 | 122.1053 | -0.14583 | 0.019336 | -122.1342 | 0.088021 | 0.073986 | 0.05465 | -122.1172 | -122.0352 | -0.049703 | -0.27259 | 0.18417 | 0.062672 | 0.11237 | -0.010878 | -0.085513 | 0.15284 | 0.16975 | 0.25183 | 0.11127 | -122.2677 | 122.0144 | 122.2761 | 122.2015 | 0.54978 | -122.3367
2578.8594 | 122.4197 | -0.068665 | 122.1954 | -0.010149 | -0.045624 | 0.041148 | 0.022033 | -0.011651 | -0.0033715 | -0.013887 | -0.0022666 | -0.0022903 | 0.058687 | 0.042397 | 0.049183 | -0.017266 | 0.019721 | -0.017566 | 0.056706 | 0.064464 | 0.1557 | -0.072215 | 0.088043 | 0.44907 | -0.028879 | 121.9183 | 122.1891 | 122.1053 | -0.14583 | -0.00355 | -122.1387 | 0.051399 | 0.051099 | 0.054649 | -122.131 | -122.0397 | -0.077168 | -0.27717 | 0.15671 | 0.039786 | 0.11695 | -0.006299 | -0.090091 | 0.12537 | 0.13313 | 0.22437 | 0.088386 | -122.2677 | 121.9869 | 122.2578 | 122.174 | 0.51774 | -122.3413
2580.625 | 122.2916 | -0.10529 | 122.2275 | -0.010149 | -0.045624 | 0.040721 | 0.021819 | -0.012292 | -0.0035853 | -0.021518 | -0.0022666 | -0.0025041 | 0.058687 | 0.042183 | 0.048756 | -0.017266 | 0.015142 | -0.017566 | 0.061284 | 0.073622 | 0.16028 | -0.081373 | 0.083464 | 0.45823 | -0.038036 | 121.9228 | 122.1846 | 122.1053 | -0.13668 | 0.023913 | -122.1662 | 0.08802 | 0.08772 | 0.063807 | -122.1539 | -122.0672 | -0.03139 | -0.30464 | 0.18875 | 0.06725 | 0.09864 | -0.042921 | -0.12213 | 0.16657 | 0.17891 | 0.26557 | 0.12043 | -122.3089 | 122.0281 | 122.2898 | 122.2106 | 0.56352 | -122.3642
2582.3125 | 122.287 | -0.091553 | 122.2137 | -0.010149 | -0.045624 | 0.040721 | 0.021819 | -0.011865 | -0.0035853 | -0.029148 | -0.0022666 | -0.0020767 | 0.058901 | 0.042611 | 0.048969 | -0.012688 | 0.019721 | -0.017566 | 0.061284 | 0.064464 | 0.16028 | -0.072215 | 0.088043 | 0.45823 | -0.033458 | 121.9274 | 122.1846 | 122.1053 | -0.14583 | 0.019338 | -122.1525 | 0.078865 | 0.073987 | 0.054649 | -122.1493 | -122.0535 | -0.05428 | -0.28632 | 0.1796 | 0.058095 | 0.11237 | -0.029188 | -0.1084 | 0.15284 | 0.15602 | 0.25183 | 0.11127 | -122.286 | 122.019 | 122.2761 | 122.1969 | 0.54978 | -122.3596
2584.0781 | 122.2961 | -0.11444 | 122.2229 | -0.010149 | -0.046051 | 0.040934 | 0.022033 | -0.011865 | -0.0035853 | -0.021518 | -0.0022666 | -0.0020767 | 0.058901 | 0.042397 | 0.048969 | -0.017266 | 0.010564 | -0.012988 | 0.056706 | 0.073622 | 0.15112 | -0.072215 | 0.088043 | 0.45365 | -0.038036 | 121.9228 | 122.18 | 122.1099 | -0.14583 | 0.042226 | -122.1662 | 0.097175 | 0.10145 | 0.059227 | -122.1493 | -122.0718 | -0.031392 | -0.30006 | 0.20248 | 0.076405 | 0.1078 | -0.042921 | -0.11298 | 0.17115 | 0.18806 | 0.26556 | 0.12501 | -122.2951 | 122.0373 | 122.2944 | 122.2244 | 0.56809 | -122.3687
2585.8281 | 122.3282 | -0.09613 | 122.1863 | -0.010149 | -0.045837 | 0.040934 | 0.021606 | -0.011865 | -0.0035853 | -0.029148 | -0.0018394 | -0.0025041 | 0.058687 | 0.042397 | 0.048756 | -0.017266 | 0.019721 | -0.022144 | 0.056706 | 0.069043 | 0.16486 | -0.076794 | 0.088043 | 0.45823 | -0.028879 | 121.9274 | 122.1891 | 122.1099 | -0.14125 | 0.019336 | -122.1296 | 0.078864 | 0.073986 | 0.05465 | -122.1172 | -122.0214 | -0.045125 | -0.25886 | 0.18417 | 0.067251 | 0.11238 | 0.002857 | -0.076356 | 0.15284 | 0.16517 | 0.26099 | 0.11585 | -122.2631 | 122.0236 | 122.2853 | 122.2061 | 0.55436 | -122.3275
2587.5156 | 122.3648 | -0.086975 | 122.1771 | -0.01778 | -0.045837 | 0.040934 | 0.021606 | -0.012078 | -0.0037989 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.042397 | 0.048756 | -0.012688 | 0.019721 | -0.022144 | 0.065863 | 0.069043 | 0.1557 | -0.076794 | 0.083464 | 0.45823 | -0.033458 | 121.9183 | 122.18 | 122.1053 | -0.14583 | 0.010181 | -122.1113 | 0.074287 | 0.064831 | 0.05465 | -122.1081 | -122.0214 | -0.058858 | -0.25886 | 0.17044 | 0.053517 | 0.11237 | 0.002855 | -0.07178 | 0.15284 | 0.15602 | 0.24268 | 0.1067 | -122.2539 | 122.0052 | 122.267 | 122.1923 | 0.54521 | -122.323
2589.2656 | 122.3877 | -0.068665 | 122.1771 | -0.01778 | -0.046051 | 0.041148 | 0.021819 | -0.012292 | -0.0035853 | -0.0062567 | -0.002053 | -0.0020767 | 0.058901 | 0.042611 | 0.048542 | -0.017266 | 0.015142 | -0.022144 | 0.061284 | 0.073622 | 0.1557 | -0.076794 | 0.078886 | 0.45823 | -0.028879 | 121.9183 | 122.1891 | 122.1053 | -0.14125 | -0.008129 | -122.1158 | 0.051399 | 0.046521 | 0.05465 | -122.1035 | -122.0214 | -0.07259 | -0.25886 | 0.14755 | 0.039786 | 0.11238 | 0.012012 | -0.07178 | 0.12995 | 0.14229 | 0.22437 | 0.083807 | -122.2539 | 121.9869 | 122.2578 | 122.174 | 0.5269 | -122.3184
2591.0156 | 122.4289 | -0.054932 | 122.1634 | -0.010149 | -0.04541 | 0.040934 | 0.021819 | -0.012078 | -0.0031579 | -0.013887 | -0.0024804 | -0.0022903 | 0.058473 | 0.042611 | 0.048969 | -0.012688 | 0.015142 | -0.022144 | 0.061284 | 0.064464 | 0.16028 | -0.076794 | 0.083464 | 0.45823 | -0.038036 | 121.9228 | 122.1846 | 122.1053 | -0.14125 | -0.021862 | -122.1021 | 0.042244 | 0.032788 | 0.05465 | -122.0989 | -122.0031 | -0.086323 | -0.24055 | 0.1384 | 0.016896 | 0.10322 | 0.021166 | -0.058047 | 0.11622 | 0.1194 | 0.21521 | 0.070074 | -122.2402 | 121.9778 | 122.2395 | 122.1603 | 0.51316 | -122.3046
2592.7031 | 122.3465 | -0.086975 | 122.1817 | 0.0051128 | -0.04541 | 0.041148 | 0.022033 | -0.011865 | -0.0035853 | -0.013887 | -0.0018394 | -0.0025041 | 0.058901 | 0.042397 | 0.048756 | -0.021844 | 0.010564 | -0.008409 | 0.061284 | 0.073622 | 0.1557 | -0.076794 | 0.092622 | 0.46281 | -0.038036 | 121.9228 | 122.1846 | 122.1053 | -0.14125 | 0.010181 | -122.1204 | 0.065131 | 0.078566 | 0.068385 | -122.1081 | -122.026 | -0.05428 | -0.25886 | 0.1796 | 0.048939 | 0.10322 | 0.002855 | -0.076358 | 0.14826 | 0.1606 | 0.24268 | 0.097539 | -122.2585 | 122.0098 | 122.2715 | 122.1923 | 0.54978 | -122.323
2594.4688 | 122.3831 | -0.073242 | 122.1771 | -0.01778 | -0.045837 | 0.040934 | 0.022033 | -0.012078 | -0.0035853 | -0.029148 | -0.0022666 | -0.0020767 | 0.058687 | 0.042611 | 0.049183 | -0.012688 | 0.019721 | -0.017566 | 0.065863 | 0.069043 | 0.16486 | -0.072215 | 0.074307 | 0.45823 | -0.033458 | 121.9274 | 122.1891 | 122.1053 | -0.13668 | 0.001027 | -122.1113 | 0.060554 | 0.055676 | 0.054649 | -122.1081 | -122.0123 | -0.063434 | -0.2497 | 0.14755 | 0.039784 | 0.10322 | 0.012012 | -0.07178 | 0.13911 | 0.14228 | 0.2381 | 0.092963 | -122.2493 | 122.0007 | 122.2624 | 122.1786 | 0.53147 | -122.3138
2596.1562 | 122.4014 | -0.032043 | 122.1863 | -0.010149 | -0.04541 | 0.040934 | 0.021819 | -0.012292 | -0.0037989 | -0.021518 | -0.0018394 | -0.0022903 | 0.058687 | 0.042397 | 0.048542 | -0.008109 | 0.019721 | -0.012988 | 0.070441 | 0.073622 | 0.16028 | -0.072215 | 0.083464 | 0.46281 | -0.0243 | 121.9228 | 122.1891 | 122.1099 | -0.1321 | -0.040172 | -122.1158 | 0.023934 | 0.019055 | 0.059227 | -122.1127 | -122.026 | -0.10005 | -0.26344 | 0.11551 | 0.007743 | 0.1078 | 0.002857 | -0.076356 | 0.10248 | 0.10567 | 0.19232 | 0.051764 | -122.2585 | 121.9549 | 122.2212 | 122.142 | 0.49485 | -122.3184
2597.9062 | 122.2687 | -0.07782 | 122.2412 | -0.0025182 | -0.045837 | 0.040934 | 0.021819 | -0.012078 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.042611 | 0.049183 | -0.012688 | 0.015142 | -0.022144 | 0.056706 | 0.073622 | 0.16486 | -0.076794 | 0.078886 | 0.46281 | -0.033458 | 121.9228 | 122.1891 | 122.1008 | -0.14583 | 0.001026 | -122.1845 | 0.065132 | 0.055676 | 0.05465 | -122.1676 | -122.0764 | -0.068013 | -0.31837 | 0.15671 | 0.044362 | 0.11237 | -0.052075 | -0.14045 | 0.13453 | 0.15144 | 0.24268 | 0.092962 | -122.318 | 122.0007 | 122.267 | 122.1786 | 0.54063 | -122.387
2599.6562 | 122.4106 | -0.054932 | 122.168 | -0.010149 | -0.045624 | 0.041148 | 0.021819 | -0.011865 | -0.0031579 | -0.013887 | -0.002053 | -0.0025041 | 0.058687 | 0.042611 | 0.049397 | -0.012688 | 0.015142 | -0.012988 | 0.061284 | 0.078201 | 0.16486 | -0.076794 | 0.083464 | 0.46281 | -0.028879 | 121.9274 | 122.1846 | 122.1145 | -0.14583 | -0.021862 | -122.1067 | 0.042244 | 0.041944 | 0.063806 | -122.0898 | -122.0031 | -0.090901 | -0.24055 | 0.1384 | 0.026053 | 0.11695 | 0.016588 | -0.053468 | 0.11622 | 0.13313 | 0.21979 | 0.070074 | -122.2448 | 121.9824 | 122.2395 | 122.1694 | 0.51774 | -122.3138
2601.3438 | 122.2961 | -0.09613 | 122.2229 | -0.010149 | -0.045837 | 0.040934 | 0.021819 | -0.011865 | -0.0031579 | -0.021518 | -0.002053 | -0.0022903 | 0.058901 | 0.042397 | 0.048969 | -0.017266 | 0.019721 | -0.012988 | 0.061284 | 0.069043 | 0.16028 | -0.076794 | 0.078886 | 0.45823 | -0.033458 | 121.9274 | 122.1891 | 122.1053 | -0.13668 | 0.019336 | -122.1616 | 0.078864 | 0.083142 | 0.063806 | -122.1539 | -122.0626 | -0.040546 | -0.29548 | 0.17502 | 0.062672 | 0.10322 | -0.033764 | -0.11756 | 0.15741 | 0.16517 | 0.25641 | 0.11585 | -122.2997 | 122.0236 | 122.2853 | 122.2015 | 0.55436 | -122.3596
2603.1094 | 122.4106 | -0.059509 | 122.1817 | -0.010149 | -0.045624 | 0.041148 | 0.021819 | -0.012078 | -0.0031579 | -0.021518 | -0.0024804 | -0.0025041 | 0.058687 | 0.042183 | 0.048969 | -0.017266 | 0.015142 | -0.017566 | 0.061284 | 0.064464 | 0.1557 | -0.067636 | 0.078886 | 0.46281 | -0.033458 | 121.9228 | 122.1846 | 122.1008 | -0.14125 | -0.008127 | -122.1204 | 0.042243 | 0.041943 | 0.05007 | -122.1172 | -122.026 | -0.081746 | -0.25886 | 0.13839 | 0.026051 | 0.1078 | 0.002855 | -0.080937 | 0.12079 | 0.12397 | 0.21521 | 0.074651 | -122.2493 | 121.9824 | 122.2441 | 122.1603 | 0.52232 | -122.323
2604.8125 | 122.2687 | -0.10529 | 122.2183 | -0.010149 | -0.045837 | 0.040721 | 0.021819 | -0.012078 | -0.0031579 | -0.029148 | -0.002053 | -0.0027177 | 0.058687 | 0.042611 | 0.048969 | -0.017266 | 0.019721 | -0.017566 | 0.061284 | 0.069043 | 0.15112 | -0.072215 | 0.083464 | 0.45823 | -0.033458 | 121.9274 | 122.1891 | 122.1145 | -0.13668 | 0.033071 | -122.157 | 0.08802 | 0.08772 | 0.054649 | -122.1493 | -122.0672 | -0.03139 | -0.2909 | 0.18875 | 0.071828 | 0.10322 | -0.029187 | -0.10382 | 0.16657 | 0.17433 | 0.25641 | 0.12501 | -122.2905 | 122.0327 | 122.2944 | 122.2198 | 0.56352 | -122.355
2606.5625 | 122.2778 | -0.091553 | 122.2046 | -0.010149 | -0.046051 | 0.040721 | 0.021819 | -0.011865 | -0.0033715 | -0.013887 | -0.0022666 | -0.0020767 | 0.058687 | 0.042397 | 0.048756 | -0.012688 | 0.019721 | -0.017566 | 0.070441 | 0.08278 | 0.16028 | -0.067636 | 0.088043 | 0.46281 | -0.028879 | 121.9274 | 122.1846 | 122.1099 | -0.14125 | 0.023917 | -122.1341 | 0.078865 | 0.073987 | 0.05007 | -122.1218 | -122.0443 | -0.049702 | -0.27717 | 0.1796 | 0.062674 | 0.11238 | -0.020033 | -0.094667 | 0.16199 | 0.17433 | 0.25183 | 0.11127 | -122.2722 | 122.019 | 122.2761 | 122.2015 | 0.55436 | -122.3458
2608.3281 | 122.2824 | -0.10071 | 122.2 | -0.0025182 | -0.046051 | 0.040721 | 0.021606 | -0.012078 | -0.0031579 | -0.021518 | -0.0022666 | -0.0025041 | 0.058901 | 0.042611 | 0.048756 | -0.012688 | 0.0243 | -0.017566 | 0.065863 | 0.069043 | 0.16028 | -0.076794 | 0.078886 | 0.46281 | -0.033458 | 121.9274 | 122.1937 | 122.1099 | -0.13668 | 0.023914 | -122.1341 | 0.08802 | 0.083142 | 0.059228 | -122.131 | -122.0397 | -0.035968 | -0.27259 | 0.17959 | 0.06725 | 0.10322 | -0.006297 | -0.090089 | 0.16657 | 0.16975 | 0.26099 | 0.12501 | -122.2768 | 122.0281 | 122.2944 | 122.2106 | 0.56352 | -122.3367
2610.0938 | 122.3923 | -0.064087 | 122.1771 | -0.010149 | -0.045624 | 0.040721 | 0.021819 | -0.011865 | -0.0031579 | -0.021518 | -0.0022666 | -0.0025041 | 0.058687 | 0.042611 | 0.048756 | -0.008109 | 0.019721 | -0.017566 | 0.065863 | 0.059885 | 0.16486 | -0.072215 | 0.083464 | 0.45823 | -0.028879 | 121.9228 | 122.1846 | 122.1099 | -0.14125 | -0.008128 | -122.1113 | 0.055978 | 0.046521 | 0.054649 | -122.1172 | -122.0123 | -0.077168 | -0.25428 | 0.14755 | 0.035208 | 0.11238 | 0.007433 | -0.067201 | 0.12995 | 0.12397 | 0.22895 | 0.083808 | -122.2493 | 121.9869 | 122.2486 | 122.174 | 0.52232 | -122.3184
2611.875 | 122.2778 | -0.10529 | 122.2321 | -0.010149 | -0.046051 | 0.040721 | 0.021606 | -0.012292 | -0.0031579 | -0.029148 | -0.0024804 | -0.0020767 | 0.058687 | 0.042611 | 0.048969 | -0.012688 | 0.010564 | -0.017566 | 0.065863 | 0.069043 | 0.16028 | -0.076794 | 0.083464 | 0.45823 | -0.033458 | 121.932 | 122.1891 | 122.1053 | -0.14583 | 0.028492 | -122.1662 | 0.092598 | 0.08772 | 0.059228 | -122.163 | -122.0718 | -0.040547 | -0.30006 | 0.18875 | 0.071828 | 0.11237 | -0.04292 | -0.12671 | 0.17115 | 0.17433 | 0.26557 | 0.11585 | -122.3089 | 122.0373 | 122.2944 | 122.2106 | 0.56352 | -122.3779
2613.5625 | 122.3831 | -0.064087 | 122.1954 | -0.0025182 | -0.04541 | 0.040721 | 0.021819 | -0.012078 | -0.0029443 | -0.021518 | -0.0022666 | -0.0025041 | 0.058687 | 0.042397 | 0.048756 | -0.021844 | 0.0243 | -0.017566 | 0.070441 | 0.069043 | 0.1557 | -0.081373 | 0.078886 | 0.46281 | -0.033458 | 121.932 | 122.1937 | 122.1099 | -0.14125 | -0.017286 | -122.125 | 0.042243 | 0.046521 | 0.063807 | -122.1264 | -122.0397 | -0.077168 | -0.26344 | 0.14297 | 0.030629 | 0.1078 | -0.00172 | -0.085512 | 0.13453 | 0.13313 | 0.21979 | 0.088387 | -122.2768 | 121.9961 | 122.2578 | 122.174 | 0.5269 | -122.3367
2615.3281 | 122.4106 | -0.059509 | 122.1771 | 0.0051128 | -0.045624 | 0.040934 | 0.021606 | -0.012292 | -0.0029443 | -0.021518 | -0.002053 | -0.0025041 | 0.058687 | 0.042397 | 0.048969 | -0.017266 | 0.010564 | -0.017566 | 0.061284 | 0.069043 | 0.16028 | -0.081373 | 0.088043 | 0.46281 | -0.033458 | 121.932 | 122.1891 | 122.1145 | -0.14583 | -0.021864 | -122.1158 | 0.042243 | 0.041943 | 0.063807 | -122.1081 | -122.0168 | -0.086324 | -0.24512 | 0.14755 | 0.026051 | 0.11237 | 0.012012 | -0.062623 | 0.12079 | 0.12855 | 0.21979 | 0.070073 | -122.2585 | 121.9915 | 122.2486 | 122.174 | 0.52232 | -122.323
2617.0938 | 122.3236 | -0.091553 | 122.2092 | -0.01778 | -0.045624 | 0.040934 | 0.021606 | -0.011651 | -0.0033715 | -0.013887 | -0.0018394 | -0.0022903 | 0.058901 | 0.042397 | 0.048756 | -0.008109 | 0.019721 | -0.012988 | 0.056706 | 0.069043 | 0.16486 | -0.076794 | 0.078886 | 0.45823 | -0.033458 | 121.9274 | 122.1937 | 122.1191 | -0.13668 | 0.014759 | -122.1525 | 0.083444 | 0.078565 | 0.063806 | -122.1401 | -122.0443 | -0.045123 | -0.28174 | 0.17044 | 0.058095 | 0.10322 | -0.015452 | -0.090087 | 0.14826 | 0.1606 | 0.25641 | 0.11127 | -122.286 | 122.019 | 122.2853 | 122.2106 | 0.54978 | -122.3458
2618.8594 | 122.3923 | -0.07782 | 122.1909 | -0.01778 | -0.046051 | 0.041362 | 0.021819 | -0.012078 | -0.0029443 | -0.0062567 | -0.0022666 | -0.0020767 | 0.058687 | 0.042397 | 0.049183 | -0.012688 | 0.019721 | -0.012988 | 0.070441 | 0.073622 | 0.16944 | -0.072215 | 0.083464 | 0.46281 | -0.038036 | 121.932 | 122.1891 | 122.1145 | -0.14583 | 0.005605 | -122.1204 | 0.065132 | 0.064832 | 0.059227 | -122.1172 | -122.0214 | -0.068013 | -0.25886 | 0.16128 | 0.039784 | 0.1078 | -0.001721 | -0.076356 | 0.14826 | 0.15144 | 0.24726 | 0.097541 | -122.2631 | 122.0098 | 122.267 | 122.1923 | 0.54063 | -122.3367
2620.625 | 122.3969 | -0.073242 | 122.1634 | -0.01778 | -0.045624 | 0.040721 | 0.021819 | -0.012292 | -0.0031579 | -0.013887 | -0.002053 | -0.0025041 | 0.05826 | 0.042397 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.061284 | 0.078201 | 0.1557 | -0.072215 | 0.078886 | 0.45823 | -0.033458 | 121.9274 | 122.1891 | 122.1145 | -0.14125 | 0.001027 | -122.1021 | 0.055976 | 0.060254 | 0.059227 | -122.0852 | -122.0077 | -0.068013 | -0.23597 | 0.15213 | 0.039784 | 0.1078 | 0.025745 | -0.04889 | 0.13453 | 0.15144 | 0.22894 | 0.088384 | -122.2356 | 122.0007 | 122.2624 | 122.1877 | 0.53147 | -122.3046
2622.3281 | 122.4014 | -0.073242 | 122.1863 | -0.0025182 | -0.045624 | 0.041362 | 0.021606 | -0.011865 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.058901 | 0.042824 | 0.048756 | -0.017266 | 0.010564 | -0.022144 | 0.065863 | 0.078201 | 0.16486 | -0.076794 | 0.078886 | 0.46739 | -0.038036 | 121.9366 | 122.1891 | 122.1053 | -0.14125 | -0.003552 | -122.1204 | 0.055976 | 0.051098 | 0.05465 | -122.1081 | -122.0214 | -0.068013 | -0.2497 | 0.15213 | 0.035206 | 0.10322 | 0.002857 | -0.080935 | 0.13911 | 0.15144 | 0.2381 | 0.083806 | -122.2631 | 122.0098 | 122.2624 | 122.1786 | 0.54063 | -122.3275
2624.0938 | 122.3785 | -0.068665 | 122.1817 | -0.010149 | -0.045837 | 0.040934 | 0.021819 | -0.012078 | -0.0029443 | -0.013887 | -0.002053 | -0.0025041 | 0.058687 | 0.042611 | 0.048542 | -0.012688 | 0.019721 | -0.012988 | 0.061284 | 0.073622 | 0.16028 | -0.072215 | 0.088043 | 0.47197 | -0.033458 | 121.932 | 122.1891 | 122.1145 | -0.14583 | -0.00355 | -122.1204 | 0.055977 | 0.055677 | 0.059227 | -122.1081 | -122.0214 | -0.077168 | -0.2497 | 0.15671 | 0.035207 | 0.11237 | 0.007434 | -0.067201 | 0.12995 | 0.14229 | 0.22895 | 0.088386 | -122.2539 | 122.0007 | 122.2578 | 122.1832 | 0.54063 | -122.3275
2625.7812 | 122.3785 | -0.086975 | 122.2046 | -0.01778 | -0.045624 | 0.041148 | 0.022033 | -0.011865 | -0.0027305 | -0.013887 | -0.002053 | -0.0018631 | 0.058473 | 0.042611 | 0.048542 | -0.012688 | 0.019721 | -0.017566 | 0.065863 | 0.073622 | 0.17402 | -0.072215 | 0.078886 | 0.46281 | -0.038036 | 121.932 | 122.1891 | 122.1145 | -0.14125 | 0.01476 | -122.1387 | 0.074287 | 0.069409 | 0.054649 | -122.131 | -122.0306 | -0.05428 | -0.27259 | 0.16586 | 0.048939 | 0.10322 | -0.015454 | -0.090089 | 0.15284 | 0.1606 | 0.26099 | 0.1067 | -122.2768 | 122.019 | 122.2761 | 122.2015 | 0.54978 | -122.3458
2627.5312 | 122.2916 | -0.11444 | 122.2275 | -0.025411 | -0.045837 | 0.041148 | 0.021819 | -0.012078 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.058901 | 0.042611 | 0.048969 | -0.017266 | 0.019721 | -0.012988 | 0.056706 | 0.064464 | 0.16944 | -0.072215 | 0.083464 | 0.46739 | -0.028879 | 121.9366 | 122.1891 | 122.1191 | -0.14583 | 0.042226 | -122.1708 | 0.097175 | 0.10145 | 0.059227 | -122.163 | -122.058 | -0.031392 | -0.2909 | 0.1979 | 0.085562 | 0.11695 | -0.038342 | -0.1084 | 0.17115 | 0.1789 | 0.28388 | 0.13416 | -122.2997 | 122.051 | 122.3036 | 122.2335 | 0.58183 | -122.3733
2629.2344 | 122.3099 | -0.086975 | 122.2275 | -0.0025182 | -0.045837 | 0.040721 | 0.021819 | -0.012078 | -0.0031579 | -0.013887 | -0.0018394 | -0.0022903 | 0.058687 | 0.042397 | 0.048542 | -0.017266 | 0.010564 | -0.022144 | 0.061284 | 0.073622 | 0.16944 | -0.072215 | 0.078886 | 0.45823 | -0.033458 | 121.932 | 122.1891 | 122.1191 | -0.13668 | 0.01476 | -122.1662 | 0.069709 | 0.064831 | 0.050071 | -122.1539 | -122.058 | -0.049701 | -0.29548 | 0.16586 | 0.053517 | 0.10322 | -0.038342 | -0.1084 | 0.14826 | 0.1606 | 0.25641 | 0.097539 | -122.2997 | 122.019 | 122.2761 | 122.2061 | 0.54521 | -122.3642
2630.9844 | 122.3602 | -0.082397 | 122.2 | -0.010149 | -0.045837 | 0.040721 | 0.021606 | -0.012078 | -0.0031579 | -0.013887 | -0.0016258 | -0.0022903 | 0.058901 | 0.043038 | 0.048756 | -0.017266 | 0.015142 | -0.017566 | 0.061284 | 0.073622 | 0.16028 | -0.076794 | 0.078886 | 0.45823 | -0.042615 | 121.932 | 122.1937 | 122.1099 | -0.14583 | 0.005603 | -122.1387 | 0.065131 | 0.064831 | 0.059228 | -122.1264 | -122.0397 | -0.063436 | -0.26801 | 0.16128 | 0.039782 | 0.10322 | -0.006297 | -0.090089 | 0.14368 | 0.15602 | 0.24268 | 0.097539 | -122.2768 | 122.0144 | 122.2761 | 122.1923 | 0.54063 | -122.3458
2632.7344 | 122.3053 | -0.10529 | 122.2092 | -0.010149 | -0.045837 | 0.041148 | 0.021819 | -0.012292 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.042611 | 0.048542 | -0.021844 | 0.0243 | -0.008409 | 0.056706 | 0.073622 | 0.16486 | -0.067636 | 0.083464 | 0.46281 | -0.033458 | 121.932 | 122.1891 | 122.1099 | -0.13668 | 0.03765 | -122.1525 | 0.083442 | 0.096877 | 0.059227 | -122.1355 | -122.0443 | -0.03139 | -0.27717 | 0.18875 | 0.071828 | 0.10322 | -0.020031 | -0.099244 | 0.16199 | 0.17891 | 0.27015 | 0.12959 | -122.2768 | 122.0373 | 122.2944 | 122.2152 | 0.5681 | -122.3458
2634.4219 | 122.3648 | -0.064087 | 122.2 | 0.0051128 | -0.045837 | 0.041148 | 0.022033 | -0.012292 | -0.0029443 | -0.029148 | -0.0022666 | -0.0025041 | 0.058687 | 0.042397 | 0.048969 | -0.017266 | 0.015142 | -0.022144 | 0.061284 | 0.069043 | 0.16028 | -0.072215 | 0.083464 | 0.46739 | -0.033458 | 121.9366 | 122.1937 | 122.1145 | -0.13668 | -0.008128 | -122.1387 | 0.046821 | 0.041943 | 0.050071 | -122.131 | -122.0397 | -0.072589 | -0.26343 | 0.14755 | 0.030629 | 0.10322 | -0.006297 | -0.085511 | 0.12537 | 0.13313 | 0.22437 | 0.079229 | -122.2722 | 122.0007 | 122.2578 | 122.1786 | 0.53147 | -122.3367
2636.1719 | 122.3785 | -0.045776 | 122.1909 | -0.01778 | -0.045837 | 0.040934 | 0.021606 | -0.011865 | -0.0027305 | -0.029148 | -0.002053 | -0.0027177 | 0.05826 | 0.042611 | 0.048969 | -0.021844 | 0.010564 | -0.017566 | 0.061284 | 0.069043 | 0.16486 | -0.067636 | 0.078886 | 0.46281 | -0.033458 | 121.9366 | 122.1891 | 122.1099 | -0.14583 | -0.02186 | -122.1296 | 0.023932 | 0.02821 | 0.05007 | -122.1218 | -122.026 | -0.10006 | -0.25428 | 0.12466 | 0.012318 | 0.11237 | -0.001721 | -0.080934 | 0.10706 | 0.11482 | 0.21064 | 0.05634 | -122.2585 | 121.9824 | 122.2349 | 122.1557 | 0.50859 | -122.3367
2637.8594 | 122.374 | -0.07782 | 122.1909 | -0.010149 | -0.046051 | 0.041148 | 0.021819 | -0.011865 | -0.0029443 | -0.021518 | -0.002053 | -0.0020767 | 0.058473 | 0.042611 | 0.048542 | -0.012688 | 0.015142 | -0.017566 | 0.070441 | 0.069043 | 0.16028 | -0.076794 | 0.088043 | 0.46281 | -0.038036 | 121.9366 | 122.1891 | 122.1145 | -0.13668 | 0.001026 | -122.1204 | 0.065132 | 0.060254 | 0.059228 | -122.1218 | -122.0306 | -0.058856 | -0.25428 | 0.16586 | 0.039784 | 0.09864 | -0.001721 | -0.076356 | 0.14826 | 0.14686 | 0.2381 | 0.092962 | -122.2677 | 122.0144 | 122.267 | 122.1923 | 0.54063 | -122.3275
2639.625 | 122.3923 | -0.050354 | 122.2046 | -0.01778 | -0.045837 | 0.040934 | 0.022247 | -0.012078 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.042611 | 0.048328 | -0.017266 | 0.015142 | -0.022144 | 0.065863 | 0.073622 | 0.16028 | -0.072215 | 0.074307 | 0.46739 | -0.033458 | 121.932 | 122.1937 | 122.1145 | -0.1321 | -0.021861 | -122.1387 | 0.033088 | 0.02821 | 0.050071 | -122.131 | -122.0443 | -0.081743 | -0.27259 | 0.12466 | 0.016896 | 0.098639 | -0.010875 | -0.090089 | 0.11622 | 0.12398 | 0.21063 | 0.065496 | -122.2768 | 121.9824 | 122.2441 | 122.1649 | 0.51774 | -122.3367
2641.375 | 122.2824 | -0.10529 | 122.2366 | -0.010149 | -0.045837 | 0.040934 | 0.021606 | -0.011865 | -0.0031579 | -0.0062567 | -0.0024804 | -0.0022903 | 0.058687 | 0.042397 | 0.048756 | -0.017266 | 0.019721 | -0.012988 | 0.056706 | 0.08278 | 0.16944 | -0.072215 | 0.078886 | 0.47197 | -0.033458 | 121.9366 | 122.1891 | 122.1237 | -0.1321 | 0.033071 | -122.1799 | 0.08802 | 0.092298 | 0.059227 | -122.1539 | -122.0672 | -0.026811 | -0.30005 | 0.18417 | 0.071828 | 0.098639 | -0.047497 | -0.11297 | 0.16199 | 0.18807 | 0.27472 | 0.12501 | -122.3088 | 122.0419 | 122.2944 | 122.2289 | 0.57725 | -122.3687
2643.0781 | 122.4152 | -0.054932 | 122.1909 | -0.01778 | -0.045624 | 0.041148 | 0.021819 | -0.012078 | -0.0031579 | -0.021518 | -0.0018394 | -0.0022903 | 0.058473 | 0.042611 | 0.048756 | -0.012688 | 0.015142 | -0.012988 | 0.056706 | 0.073622 | 0.16486 | -0.067636 | 0.083464 | 0.45823 | -0.028879 | 121.932 | 122.1983 | 122.1145 | -0.12752 | -0.012704 | -122.1342 | 0.042244 | 0.041944 | 0.054648 | -122.1172 | -122.026 | -0.072586 | -0.25886 | 0.1384 | 0.026053 | 0.098639 | 0.007436 | -0.076356 | 0.11164 | 0.12855 | 0.21979 | 0.070074 | -122.2585 | 121.9869 | 122.2532 | 122.1694 | 0.51316 | -122.3184
2644.8438 | 122.3785 | -0.068665 | 122.2137 | -0.010149 | -0.046051 | 0.040934 | 0.021392 | -0.012292 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.042611 | 0.048542 | -0.012688 | 0.010564 | -0.017566 | 0.061284 | 0.069043 | 0.16486 | -0.081373 | 0.083464 | 0.46739 | -0.033458 | 121.932 | 122.1937 | 122.1145 | -0.1321 | -0.012708 | -122.1525 | 0.055977 | 0.051099 | 0.063807 | -122.1447 | -122.0489 | -0.063432 | -0.28175 | 0.15213 | 0.035207 | 0.098639 | -0.02003 | -0.099244 | 0.12995 | 0.13771 | 0.23352 | 0.079229 | -122.2951 | 122.0007 | 122.2624 | 122.1832 | 0.53605 | -122.3458
2646.6094 | 122.3831 | -0.07782 | 122.1954 | -0.010149 | -0.045837 | 0.040934 | 0.021606 | -0.012292 | -0.0027305 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.042397 | 0.048756 | -0.017266 | 0.019721 | -0.017566 | 0.061284 | 0.08278 | 0.16028 | -0.081373 | 0.088043 | 0.46739 | -0.033458 | 121.9366 | 122.1983 | 122.1145 | -0.13668 | -0.003553 | -122.1342 | 0.060554 | 0.060254 | 0.063807 | -122.1127 | -122.0352 | -0.058856 | -0.25886 | 0.16586 | 0.044362 | 0.10322 | 0.002858 | -0.080934 | 0.1391 | 0.1606 | 0.2381 | 0.097541 | -122.2768 | 122.0144 | 122.2761 | 122.1923 | 0.54521 | -122.3321
2648.375 | 122.2778 | -0.10986 | 122.2412 | -0.025411 | -0.046051 | 0.040934 | 0.021606 | -0.012292 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.059114 | 0.042611 | 0.048969 | -0.017266 | 0.015142 | -0.017566 | 0.070441 | 0.069043 | 0.16944 | -0.076794 | 0.088043 | 0.46739 | -0.033458 | 121.932 | 122.1937 | 122.1191 | -0.13668 | 0.033069 | -122.1708 | 0.092597 | 0.092297 | 0.059228 | -122.1722 | -122.0718 | -0.026813 | -0.30921 | 0.19791 | 0.076405 | 0.10322 | -0.047496 | -0.12213 | 0.1803 | 0.17891 | 0.2793 | 0.12501 | -122.318 | 122.0419 | 122.3036 | 122.2289 | 0.57725 | -122.3779
2650.0781 | 122.3511 | -0.073242 | 122.2046 | -0.0025182 | -0.046265 | 0.040721 | 0.021819 | -0.011865 | -0.0029443 | -0.021518 | -0.002053 | -0.0022903 | 0.058473 | 0.042611 | 0.048756 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.069043 | 0.1557 | -0.076794 | 0.092622 | 0.46739 | -0.028879 | 121.9228 | 122.1937 | 122.1191 | -0.14125 | -0.003552 | -122.1387 | 0.060554 | 0.060254 | 0.063806 | -122.1355 | -122.0489 | -0.068013 | -0.28175 | 0.16586 | 0.044363 | 0.11238 | -0.010875 | -0.08551 | 0.13911 | 0.14228 | 0.22894 | 0.092963 | -122.2814 | 121.9961 | 122.267 | 122.1923 | 0.54063 | -122.3458
2651.8281 | 122.406 | -0.050354 | 122.1588 | -0.01778 | -0.046051 | 0.041148 | 0.021819 | -0.012078 | -0.0027305 | -0.029148 | -0.0024804 | -0.0020767 | 0.058473 | 0.042183 | 0.048756 | -0.017266 | 0.019721 | -0.017566 | 0.070441 | 0.069043 | 0.16028 | -0.072215 | 0.092622 | 0.47197 | -0.028879 | 121.9366 | 122.2029 | 122.1191 | -0.14125 | -0.021861 | -122.0884 | 0.033088 | 0.032788 | 0.054649 | -122.0898 | -121.9985 | -0.090901 | -0.22223 | 0.14298 | 0.021475 | 0.11238 | 0.044059 | -0.039733 | 0.1208 | 0.1194 | 0.21063 | 0.070075 | -122.231 | 121.9869 | 122.2532 | 122.1694 | 0.52232 | -122.3001
2653.5781 | 122.2961 | -0.10071 | 122.2137 | -0.01778 | -0.045837 | 0.040507 | 0.021606 | -0.012292 | -0.0029443 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.042611 | 0.048756 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.069043 | 0.16028 | -0.072215 | 0.083464 | 0.47197 | -0.038036 | 121.9366 | 122.1937 | 122.1282 | -0.14125 | 0.028493 | -122.1479 | 0.08802 | 0.08772 | 0.059227 | -122.1447 | -122.0535 | -0.040547 | -0.27717 | 0.18417 | 0.062672 | 0.10322 | -0.02003 | -0.085508 | 0.16657 | 0.16975 | 0.26099 | 0.12043 | -122.286 | 122.0373 | 122.2944 | 122.2289 | 0.57267 | -122.355
2655.2656 | 122.374 | -0.073242 | 122.1954 | -0.025411 | -0.046051 | 0.041362 | 0.021819 | -0.012078 | -0.0029443 | -0.0062567 | -0.002053 | -0.0025041 | 0.058473 | 0.042824 | 0.048756 | -0.026423 | 0.015142 | -0.017566 | 0.07502 | 0.069043 | 0.16486 | -0.081373 | 0.078886 | 0.46739 | -0.033458 | 121.9412 | 122.1937 | 122.1099 | -0.13668 | -0.008131 | -122.1204 | 0.046819 | 0.055676 | 0.063807 | -122.1264 | -122.0306 | -0.063434 | -0.25428 | 0.15213 | 0.039784 | 0.10322 | -0.00172 | -0.085512 | 0.14826 | 0.14228 | 0.2381 | 0.088384 | -122.2768 | 122.0144 | 122.267 | 122.1832 | 0.54063 | -122.3321
2657.0156 | 122.3282 | -0.086975 | 122.2137 | -0.01778 | -0.046051 | 0.040293 | 0.022033 | -0.011865 | -0.0029443 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.042397 | 0.048969 | -0.017266 | 0.019721 | -0.022144 | 0.065863 | 0.073622 | 0.16486 | -0.076794 | 0.083464 | 0.46739 | -0.038036 | 121.9366 | 122.1891 | 122.1237 | -0.13668 | 0.010181 | -122.1479 | 0.069709 | 0.064831 | 0.05465 | -122.1401 | -122.0489 | -0.049701 | -0.27717 | 0.17044 | 0.048939 | 0.09864 | -0.024609 | -0.090087 | 0.15284 | 0.1606 | 0.25183 | 0.1067 | -122.2905 | 122.0236 | 122.2761 | 122.2106 | 0.55436 | -122.3504
2658.7031 | 122.3419 | -0.082397 | 122.1954 | -0.010149 | -0.045624 | 0.040934 | 0.021606 | -0.012292 | -0.0027305 | -0.0062567 | -0.0018394 | -0.0022903 | 0.058687 | 0.042611 | 0.048542 | -0.012688 | 0.028878 | -0.017566 | 0.061284 | 0.069043 | 0.16028 | -0.081373 | 0.083464 | 0.47197 | -0.038036 | 121.9412 | 122.1937 | 122.1191 | -0.14583 | 0.001024 | -122.1342 | 0.069709 | 0.064831 | 0.063807 | -122.1264 | -122.0352 | -0.063436 | -0.25428 | 0.16586 | 0.044361 | 0.1078 | -0.00172 | -0.076355 | 0.14368 | 0.15144 | 0.24268 | 0.11127 | -122.2768 | 122.0236 | 122.2761 | 122.2015 | 0.55436 | -122.3413
2660.4688 | 122.3969 | -0.050354 | 122.1863 | -0.010149 | -0.045837 | 0.040507 | 0.021606 | -0.011865 | -0.0029443 | -0.021518 | -0.0022666 | -0.0018631 | 0.058473 | 0.043038 | 0.048542 | -0.012688 | 0.019721 | -0.017566 | 0.065863 | 0.073622 | 0.16944 | -0.076794 | 0.083464 | 0.47197 | -0.033458 | 121.9366 | 122.1983 | 122.1237 | -0.14125 | -0.02644 | -122.1204 | 0.037666 | 0.032788 | 0.059228 | -122.1127 | -122.0168 | -0.090901 | -0.2497 | 0.13382 | 0.016896 | 0.1078 | 0.012014 | -0.062621 | 0.11622 | 0.12398 | 0.21979 | 0.070075 | -122.2631 | 121.9869 | 122.2486 | 122.174 | 0.52232 | -122.3275
2662.1562 | 122.4014 | -0.050354 | 122.2 | -0.01778 | -0.045837 | 0.040934 | 0.021606 | -0.011865 | -0.0027305 | -0.021518 | -0.002053 | -0.0020767 | 0.058473 | 0.042824 | 0.048969 | -0.012688 | 0.015142 | -0.026723 | 0.061284 | 0.069043 | 0.16486 | -0.072215 | 0.088043 | 0.47654 | -0.033458 | 121.9366 | 122.1983 | 122.1237 | -0.14125 | -0.021861 | -122.1387 | 0.037666 | 0.023631 | 0.045492 | -122.131 | -122.0352 | -0.090901 | -0.26343 | 0.1384 | 0.016896 | 0.1078 | -0.001719 | -0.076354 | 0.11164 | 0.1194 | 0.21521 | 0.065496 | -122.2722 | 121.9869 | 122.2486 | 122.174 | 0.5269 | -122.3413
2663.9219 | 122.3877 | -0.064087 | 122.2 | -0.01778 | -0.045624 | 0.040507 | 0.021392 | -0.011865 | -0.0029443 | -0.021518 | -0.0024804 | -0.0025041 | 0.058687 | 0.042824 | 0.048969 | -0.017266 | 0.0243 | -0.022144 | 0.065863 | 0.078201 | 0.16944 | -0.076794 | 0.088043 | 0.47197 | -0.033458 | 121.9366 | 122.1983 | 122.1191 | -0.14125 | -0.012707 | -122.1341 | 0.046821 | 0.041943 | 0.05465 | -122.1218 | -122.0306 | -0.077168 | -0.26343 | 0.15213 | 0.030629 | 0.1078 | -0.001719 | -0.080932 | 0.12995 | 0.14229 | 0.23353 | 0.088387 | -122.2768 | 122.0007 | 122.2624 | 122.1832 | 0.53605 | -122.3413
2665.6719 | 122.374 | -0.073242 | 122.1863 | -0.010149 | -0.046051 | 0.041148 | 0.021819 | -0.012078 | -0.0031579 | -0.036779 | -0.002053 | -0.0022903 | 0.058687 | 0.042183 | 0.048756 | -0.008109 | 0.019721 | -0.012988 | 0.070441 | 0.073622 | 0.16944 | -0.072215 | 0.078886 | 0.47197 | -0.033458 | 121.9412 | 122.2029 | 122.1191 | -0.14125 | 0.001027 | -122.1158 | 0.065133 | 0.060254 | 0.059227 | -122.1127 | -122.0168 | -0.068013 | -0.24512 | 0.15213 | 0.039784 | 0.1078 | 0.016593 | -0.067199 | 0.14368 | 0.14686 | 0.24268 | 0.092963 | -122.2585 | 122.0144 | 122.2761 | 122.1923 | 0.54521 | -122.3275
2667.3594 | 122.3969 | -0.059509 | 122.1771 | -0.01778 | -0.045837 | 0.040934 | 0.021606 | -0.012078 | -0.0027305 | -0.029148 | -0.0022666 | -0.0022903 | 0.05826 | 0.042824 | 0.048969 | -0.021844 | 0.015142 | -0.017566 | 0.065863 | 0.073622 | 0.16028 | -0.076794 | 0.083464 | 0.47197 | -0.028879 | 121.9366 | 122.2029 | 122.1282 | -0.14125 | -0.017285 | -122.1113 | 0.037665 | 0.041943 | 0.059228 | -122.1035 | -122.0168 | -0.081746 | -0.24055 | 0.14297 | 0.03063 | 0.11238 | 0.025748 | -0.048887 | 0.12537 | 0.13313 | 0.21979 | 0.074651 | -122.2539 | 121.9961 | 122.2624 | 122.1877 | 0.53148 | -122.3184
2669.1094 | 122.4335 | -0.064087 | 122.1954 | -0.0025182 | -0.046051 | 0.040934 | 0.021392 | -0.012078 | -0.0031579 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.042397 | 0.048542 | -0.021844 | 0.010564 | -0.012988 | 0.061284 | 0.069043 | 0.1557 | -0.072215 | 0.088043 | 0.46739 | -0.033458 | 121.9412 | 122.2029 | 122.1191 | -0.14125 | -0.008128 | -122.1342 | 0.042243 | 0.051099 | 0.059227 | -122.1264 | -122.0397 | -0.077168 | -0.25428 | 0.15213 | 0.030629 | 0.1078 | 0.007437 | -0.076355 | 0.12537 | 0.13313 | 0.21979 | 0.074651 | -122.2677 | 122.0052 | 122.267 | 122.1832 | 0.53147 | -122.3367
2670.8125 | 122.3785 | -0.07782 | 122.2046 | 0.0051128 | -0.045837 | 0.041148 | 0.021606 | -0.011865 | -0.0027305 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.043038 | 0.048756 | -0.021844 | 0.019721 | -0.022144 | 0.070441 | 0.069043 | 0.16028 | -0.076794 | 0.078886 | 0.47654 | -0.033458 | 121.9366 | 122.1937 | 122.1145 | -0.13668 | 0.001026 | -122.1341 | 0.055976 | 0.055676 | 0.05465 | -122.1355 | -122.0443 | -0.058856 | -0.26801 | 0.15671 | 0.044362 | 0.10322 | -0.010875 | -0.090089 | 0.14826 | 0.14686 | 0.2381 | 0.097541 | -122.2814 | 122.0144 | 122.2715 | 122.1923 | 0.55436 | -122.3413
2672.5625 | 122.3007 | -0.11902 | 122.2046 | -0.0025182 | -0.046051 | 0.040934 | 0.021606 | -0.012078 | -0.0029443 | -0.021518 | -0.0024804 | -0.0020767 | 0.058473 | 0.042611 | 0.048969 | -0.021844 | 0.019721 | -0.012988 | 0.065863 | 0.073622 | 0.16944 | -0.076794 | 0.088043 | 0.48112 | -0.028879 | 121.9412 | 122.2029 | 122.1282 | -0.14125 | 0.042225 | -122.1387 | 0.097175 | 0.10603 | 0.063806 | -122.131 | -122.0352 | -0.022236 | -0.26343 | 0.20706 | 0.09014 | 0.11238 | -0.001718 | -0.076353 | 0.18488 | 0.19264 | 0.28846 | 0.13874 | -122.2814 | 122.0602 | 122.3219 | 122.2473 | 0.60014 | -122.3458
2674.3125 | 122.3053 | -0.1236 | 122.2046 | -0.0025182 | -0.045837 | 0.040721 | 0.021606 | -0.012078 | -0.0025169 | -0.021518 | -0.0022666 | -0.0025041 | 0.058473 | 0.043038 | 0.048969 | -0.012688 | 0.015142 | -0.012988 | 0.065863 | 0.073622 | 0.1557 | -0.076794 | 0.083464 | 0.47654 | -0.038036 | 121.9366 | 122.1983 | 122.1191 | -0.14125 | 0.046802 | -122.1387 | 0.11091 | 0.11061 | 0.063806 | -122.131 | -122.0489 | -0.017659 | -0.26801 | 0.20706 | 0.08556 | 0.10322 | -0.006297 | -0.08551 | 0.18946 | 0.19722 | 0.2793 | 0.13874 | -122.2814 | 122.0602 | 122.3219 | 122.2427 | 0.60014 | -122.3458
2676.0625 | 122.4106 | -0.036621 | 122.2 | -0.01778 | -0.045837 | 0.040934 | 0.021819 | -0.012078 | -0.0027305 | -0.029148 | -0.0022666 | -0.0025041 | 0.058473 | 0.042824 | 0.048756 | -0.012688 | 0.015142 | -0.012988 | 0.065863 | 0.069043 | 0.16028 | -0.072215 | 0.083464 | 0.47654 | -0.042615 | 121.9274 | 122.2029 | 122.1237 | -0.14125 | -0.035594 | -122.1341 | 0.023933 | 0.023633 | 0.059227 | -122.131 | -122.0397 | -0.10463 | -0.27259 | 0.12008 | -0.005994 | 0.09864 | 0.00286 | -0.076354 | 0.10248 | 0.10566 | 0.1969 | 0.051763 | -122.2722 | 121.964 | 122.2395 | 122.1603 | 0.51317 | -122.3413
2677.8125 | 122.3053 | -0.10986 | 122.2321 | -0.0025182 | -0.046051 | 0.040721 | 0.021392 | -0.012506 | -0.0029443 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058687 | 0.042824 | 0.048756 | -0.012688 | 0.019721 | -0.012988 | 0.070441 | 0.064464 | 0.16486 | -0.076794 | 0.088043 | 0.47197 | -0.038036 | 121.9412 | 122.2029 | 122.1282 | -0.14125 | 0.033069 | -122.1616 | 0.097175 | 0.096875 | 0.063806 | -122.1676 | -122.0672 | -0.031392 | -0.2909 | 0.19791 | 0.071827 | 0.10322 | -0.029184 | -0.10382 | 0.1803 | 0.17433 | 0.27472 | 0.12958 | -122.3089 | 122.051 | 122.3127 | 122.2381 | 0.58183 | -122.3733
2679.5781 | 122.2824 | -0.091553 | 122.2183 | -0.01778 | -0.045837 | 0.040721 | 0.021819 | -0.012506 | -0.0029443 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.043252 | 0.049183 | -0.017266 | 0.019721 | -0.017566 | 0.065863 | 0.078201 | 0.16944 | -0.072215 | 0.088043 | 0.48112 | -0.033458 | 121.9412 | 122.1983 | 122.1237 | -0.14583 | 0.019338 | -122.1525 | 0.074287 | 0.073987 | 0.054649 | -122.1401 | -122.0489 | -0.05428 | -0.27717 | 0.1796 | 0.058095 | 0.11237 | -0.02003 | -0.094665 | 0.15742 | 0.16975 | 0.26099 | 0.11127 | -122.2905 | 122.0327 | 122.2898 | 122.2152 | 0.57268 | -122.3642
2681.2812 | 122.406 | -0.054932 | 122.1909 | -0.0025182 | -0.046265 | 0.041148 | 0.021606 | -0.012292 | -0.0025169 | -0.021518 | -0.002053 | -0.0025041 | 0.058473 | 0.043038 | 0.048756 | -0.021844 | 0.0243 | -0.008409 | 0.070441 | 0.073622 | 0.16486 | -0.076794 | 0.088043 | 0.46739 | -0.028879 | 121.9366 | 122.2029 | 122.1191 | -0.13668 | -0.021862 | -122.1204 | 0.033088 | 0.046523 | 0.068385 | -122.1172 | -122.026 | -0.081744 | -0.25428 | 0.14297 | 0.026053 | 0.1078 | 0.012015 | -0.071777 | 0.12537 | 0.12855 | 0.21979 | 0.079232 | -122.2677 | 121.9915 | 122.2578 | 122.174 | 0.52232 | -122.3275
2682.9844 | 122.3831 | -0.064087 | 122.1771 | -0.0025182 | -0.045624 | 0.040721 | 0.021178 | -0.012292 | -0.0025169 | -0.013887 | -0.0022666 | -0.0022903 | 0.058687 | 0.043252 | 0.049183 | -0.012688 | 0.015142 | -0.012988 | 0.056706 | 0.069043 | 0.16944 | -0.076794 | 0.088043 | 0.47197 | -0.038036 | 121.9412 | 122.2029 | 122.1145 | -0.13668 | -0.012707 | -122.1204 | 0.051399 | 0.051099 | 0.063806 | -122.1081 | -122.0077 | -0.072589 | -0.23597 | 0.15213 | 0.026051 | 0.09864 | 0.025748 | -0.062623 | 0.12079 | 0.13313 | 0.23353 | 0.079229 | -122.2539 | 122.0052 | 122.267 | 122.1786 | 0.53605 | -122.3138
2684.7344 | 122.2916 | -0.10071 | 122.2366 | -0.01778 | -0.046265 | 0.040934 | 0.021392 | -0.012506 | -0.0029443 | -0.021518 | -0.0022666 | -0.0025041 | 0.058901 | 0.042611 | 0.048969 | -0.017266 | 0.019721 | -0.012988 | 0.061284 | 0.069043 | 0.16944 | -0.072215 | 0.083464 | 0.47197 | -0.028879 | 121.9457 | 122.212 | 122.1191 | -0.14125 | 0.028493 | -122.1753 | 0.083442 | 0.08772 | 0.059227 | -122.1676 | -122.0672 | -0.040547 | -0.2909 | 0.18417 | 0.071829 | 0.11238 | -0.024604 | -0.11755 | 0.16199 | 0.16975 | 0.27015 | 0.12043 | -122.3088 | 122.0464 | 122.3127 | 122.2198 | 0.57267 | -122.3779
2686.4844 | 122.3785 | -0.068665 | 122.1863 | -0.01778 | -0.045624 | 0.041148 | 0.021178 | -0.012078 | -0.0025169 | -0.021518 | -0.002053 | -0.0025041 | 0.058687 | 0.042824 | 0.048328 | -0.017266 | 0.019721 | -0.012988 | 0.070441 | 0.073622 | 0.16486 | -0.076794 | 0.083464 | 0.4857 | -0.038036 | 121.9503 | 122.2074 | 122.1237 | -0.14125 | -0.008129 | -122.1158 | 0.051399 | 0.055677 | 0.063806 | -122.1127 | -122.0214 | -0.07259 | -0.23596 | 0.15213 | 0.030629 | 0.10322 | 0.021171 | -0.062621 | 0.13911 | 0.14229 | 0.23352 | 0.088386 | -122.2631 | 122.019 | 122.2761 | 122.1923 | 0.55437 | -122.3275
2688.1719 | 122.4014 | -0.059509 | 122.2046 | -0.0025182 | -0.046265 | 0.040721 | 0.021606 | -0.012292 | -0.0029443 | -0.021518 | -0.0018394 | -0.0022903 | 0.058687 | 0.043038 | 0.048756 | -0.017266 | 0.010564 | -0.012988 | 0.061284 | 0.073622 | 0.16486 | -0.081373 | 0.083464 | 0.47654 | -0.038036 | 121.9412 | 122.1983 | 122.1237 | -0.1321 | -0.021864 | -122.1433 | 0.042243 | 0.046521 | 0.068385 | -122.131 | -122.0397 | -0.072588 | -0.26343 | 0.14297 | 0.021473 | 0.094061 | -0.006297 | -0.080932 | 0.12079 | 0.13313 | 0.22437 | 0.070073 | -122.286 | 122.0007 | 122.2578 | 122.1832 | 0.53605 | -122.3367
2689.9375 | 122.3877 | -0.054932 | 122.1954 | -0.010149 | -0.046051 | 0.040721 | 0.021606 | -0.012292 | -0.0029443 | -0.021518 | -0.0022666 | -0.0020767 | 0.05826 | 0.042611 | 0.048756 | -0.021844 | 0.019721 | -0.012988 | 0.065863 | 0.078201 | 0.16028 | -0.072215 | 0.092622 | 0.48112 | -0.033458 | 121.9412 | 122.212 | 122.1282 | -0.14125 | -0.017283 | -122.1296 | 0.033088 | 0.041944 | 0.059227 | -122.1172 | -122.0352 | -0.086323 | -0.25428 | 0.14755 | 0.021474 | 0.1078 | 0.016594 | -0.067198 | 0.1208 | 0.13313 | 0.21521 | 0.074653 | -122.2677 | 121.9961 | 122.267 | 122.1832 | 0.53606 | -122.3367
2691.6875 | 122.3236 | -0.091553 | 122.2092 | -0.010149 | -0.045837 | 0.040934 | 0.021392 | -0.012292 | -0.0025169 | -0.0062567 | -0.0022666 | -0.0018631 | 0.058687 | 0.043038 | 0.048756 | -0.008109 | 0.019721 | -0.017566 | 0.065863 | 0.064464 | 0.1557 | -0.072215 | 0.083464 | 0.47197 | -0.033458 | 121.9412 | 122.2029 | 122.1191 | -0.13668 | 0.019338 | -122.1433 | 0.083444 | 0.073987 | 0.054649 | -122.1447 | -122.0535 | -0.045123 | -0.26801 | 0.17502 | 0.058095 | 0.10322 | -0.006295 | -0.090087 | 0.15742 | 0.15602 | 0.24726 | 0.11127 | -122.2814 | 122.0327 | 122.2944 | 122.2106 | 0.56352 | -122.3458
2693.375 | 122.3007 | -0.091553 | 122.2 | -0.0025182 | -0.046265 | 0.040507 | 0.021392 | -0.011865 | -0.0027305 | -0.013887 | -0.002053 | -0.0025041 | 0.058687 | 0.043038 | 0.048756 | -0.021844 | 0.0243 | -0.017566 | 0.065863 | 0.078201 | 0.16486 | -0.072215 | 0.083464 | 0.4857 | -0.033458 | 121.9457 | 122.212 | 122.1328 | -0.1321 | 0.019338 | -122.1341 | 0.069709 | 0.073987 | 0.054649 | -122.1218 | -122.0352 | -0.040544 | -0.25428 | 0.17502 | 0.058095 | 0.098639 | 0.012017 | -0.067196 | 0.15742 | 0.16975 | 0.25641 | 0.11585 | -122.2722 | 122.0373 | 122.3036 | 122.2244 | 0.57726 | -122.3321
2695.1406 | 122.287 | -0.11444 | 122.2412 | -0.010149 | -0.045837 | 0.040721 | 0.021392 | -0.011865 | -0.0025169 | -0.013887 | -0.0022666 | -0.0029313 | 0.05826 | 0.043252 | 0.048969 | -0.021844 | 0.019721 | -0.017566 | 0.065863 | 0.073622 | 0.16944 | -0.081373 | 0.088043 | 0.47197 | -0.033458 | 121.9503 | 122.2074 | 122.1282 | -0.14583 | 0.033068 | -122.1753 | 0.092597 | 0.096875 | 0.063807 | -122.1676 | -122.0718 | -0.031392 | -0.2909 | 0.20248 | 0.080983 | 0.11237 | -0.033761 | -0.11297 | 0.1803 | 0.18806 | 0.28388 | 0.13416 | -122.3226 | 122.0648 | 122.3219 | 122.2427 | 0.58641 | -122.387
2696.8281 | 122.3511 | -0.09613 | 122.2137 | -0.010149 | -0.045837 | 0.040934 | 0.021606 | -0.012078 | -0.0029443 | -0.013887 | -0.0018394 | -0.0020767 | 0.058901 | 0.043038 | 0.048542 | -0.012688 | 0.0243 | -0.022144 | 0.061284 | 0.073622 | 0.1557 | -0.076794 | 0.088043 | 0.47197 | -0.028879 | 121.9457 | 122.212 | 122.1282 | -0.14125 | 0.019336 | -122.1525 | 0.083442 | 0.073986 | 0.05465 | -122.1401 | -122.058 | -0.045125 | -0.26801 | 0.18417 | 0.067251 | 0.11238 | -0.001716 | -0.085508 | 0.15741 | 0.16975 | 0.25183 | 0.12043 | -122.2905 | 122.0419 | 122.3082 | 122.2244 | 0.5681 | -122.355
2698.5781 | 122.3877 | -0.059509 | 122.2137 | -0.010149 | -0.046265 | 0.040934 | 0.021392 | -0.012292 | -0.0027305 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.043252 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.065863 | 0.078201 | 0.16486 | -0.076794 | 0.083464 | 0.48112 | -0.033458 | 121.9457 | 122.212 | 122.1237 | -0.1321 | -0.017285 | -122.1479 | 0.042243 | 0.046521 | 0.063806 | -122.1355 | -122.0489 | -0.072588 | -0.26801 | 0.14297 | 0.026051 | 0.098639 | -0.001716 | -0.090087 | 0.12537 | 0.13771 | 0.22437 | 0.074651 | -122.2905 | 122.0052 | 122.2715 | 122.1832 | 0.54063 | -122.3458
2700.3281 | 122.3969 | -0.064087 | 122.2046 | -0.010149 | -0.045624 | 0.040721 | 0.021606 | -0.012292 | -0.0031579 | -0.029148 | -0.0022666 | -0.0020767 | 0.058687 | 0.042824 | 0.048756 | -0.012688 | 0.019721 | -0.012988 | 0.070441 | 0.073622 | 0.16486 | -0.076794 | 0.088043 | 0.47654 | -0.042615 | 121.9412 | 122.212 | 122.1191 | -0.14125 | -0.012707 | -122.1341 | 0.051399 | 0.051099 | 0.063806 | -122.131 | -122.0397 | -0.077168 | -0.26343 | 0.15213 | 0.021472 | 0.09864 | 0.007439 | -0.08551 | 0.13453 | 0.13771 | 0.22895 | 0.083808 | -122.2814 | 122.0052 | 122.2761 | 122.1832 | 0.54063 | -122.3458
2702.0938 | 122.3831 | -0.068665 | 122.1909 | -0.01778 | -0.046051 | 0.040934 | 0.021178 | -0.012078 | -0.0029443 | -0.0062567 | -0.0022666 | -0.0018631 | 0.058473 | 0.043038 | 0.048542 | -0.012688 | 0.010564 | -0.017566 | 0.070441 | 0.078201 | 0.16944 | -0.076794 | 0.088043 | 0.47197 | -0.042615 | 121.9412 | 122.212 | 122.1282 | -0.13668 | -0.008129 | -122.1204 | 0.055977 | 0.051099 | 0.059228 | -122.1127 | -122.0214 | -0.068011 | -0.2497 | 0.15671 | 0.02605 | 0.094061 | 0.021172 | -0.06262 | 0.13911 | 0.14687 | 0.2381 | 0.079229 | -122.2677 | 122.0098 | 122.2807 | 122.1969 | 0.54063 | -122.3275
2703.8594 | 122.4289 | -0.068665 | 122.1817 | -0.010149 | -0.046051 | 0.040721 | 0.021392 | -0.011865 | -0.0027305 | -0.021518 | -0.0018394 | -0.0022903 | 0.058687 | 0.043679 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.061284 | 0.078201 | 0.16486 | -0.072215 | 0.088043 | 0.48112 | -0.028879 | 121.9412 | 122.2074 | 122.1237 | -0.15041 | -0.00355 | -122.1204 | 0.051399 | 0.055677 | 0.059227 | -122.1035 | -122.0168 | -0.081747 | -0.24054 | 0.15671 | 0.039786 | 0.12153 | 0.025748 | -0.058044 | 0.12995 | 0.14687 | 0.23352 | 0.083807 | -122.2539 | 122.0098 | 122.2761 | 122.1923 | 0.54979 | -122.3321
2705.625 | 122.4289 | -0.059509 | 122.1771 | -0.010149 | -0.046265 | 0.040721 | 0.021819 | -0.012292 | -0.0027305 | -0.029148 | -0.002053 | -0.0025041 | 0.058473 | 0.042824 | 0.048756 | -0.021844 | 0.015142 | -0.012988 | 0.056706 | 0.078201 | 0.16486 | -0.081373 | 0.074307 | 0.47654 | -0.033458 | 121.9549 | 122.2074 | 122.1237 | -0.14125 | -0.021864 | -122.1204 | 0.037665 | 0.046521 | 0.068385 | -122.0989 | -122.0123 | -0.081746 | -0.22223 | 0.13382 | 0.026051 | 0.1078 | 0.030326 | -0.053466 | 0.11621 | 0.13771 | 0.22437 | 0.074651 | -122.2585 | 122.0144 | 122.267 | 122.1832 | 0.53605 | -122.3184
2707.375 | 122.3831 | -0.054932 | 122.2092 | -0.0025182 | -0.046051 | 0.040721 | 0.021606 | -0.012078 | -0.0025169 | -0.021518 | -0.0022666 | -0.0025041 | 0.058687 | 0.043038 | 0.048756 | -0.026423 | 0.019721 | -0.012988 | 0.070441 | 0.078201 | 0.16486 | -0.072215 | 0.088043 | 0.47654 | -0.028879 | 121.9457 | 122.2029 | 122.1191 | -0.14583 | -0.017283 | -122.1387 | 0.028509 | 0.041944 | 0.059227 | -122.131 | -122.0443 | -0.090901 | -0.26343 | 0.14297 | 0.026053 | 0.11695 | -0.006295 | -0.090087 | 0.12537 | 0.13313 | 0.21979 | 0.074653 | -122.2814 | 122.0007 | 122.2578 | 122.174 | 0.53148 | -122.355
2709.125 | 122.319 | -0.086975 | 122.2321 | -0.01778 | -0.046265 | 0.040721 | 0.021819 | -0.012078 | -0.0027305 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.043038 | 0.048969 | -0.017266 | 0.010564 | -0.012988 | 0.065863 | 0.073622 | 0.16486 | -0.081373 | 0.088043 | 0.48112 | -0.0243 | 121.9457 | 122.2029 | 122.1282 | -0.13668 | 0.005602 | -122.1662 | 0.069709 | 0.073987 | 0.068385 | -122.1584 | -122.0672 | -0.049701 | -0.28632 | 0.17502 | 0.062675 | 0.11238 | -0.029184 | -0.10382 | 0.15284 | 0.1606 | 0.25183 | 0.097539 | -122.3134 | 122.0327 | 122.2898 | 122.2152 | 0.5681 | -122.3687
2710.8125 | 122.4014 | -0.050354 | 122.1909 | -0.01778 | -0.046478 | 0.040721 | 0.021392 | -0.012292 | -0.0027305 | -0.029148 | -0.0024804 | -0.0022903 | 0.058687 | 0.042824 | 0.048756 | -0.017266 | 0.015142 | -0.017566 | 0.061284 | 0.078201 | 0.16028 | -0.081373 | 0.092622 | 0.47654 | -0.033458 | 121.9412 | 122.2212 | 122.1191 | -0.14583 | -0.031019 | -122.1296 | 0.033088 | 0.032788 | 0.063807 | -122.1127 | -122.0306 | -0.095479 | -0.2497 | 0.14298 | 0.016896 | 0.11237 | 0.030329 | -0.071777 | 0.11164 | 0.12856 | 0.21063 | 0.065496 | -122.2722 | 121.9915 | 122.2715 | 122.1694 | 0.5269 | -122.3367
2712.5625 | 122.2916 | -0.09613 | 122.2183 | -0.010149 | -0.046051 | 0.040721 | 0.022033 | -0.012078 | -0.0029443 | -0.021518 | -0.002053 | -0.0020767 | 0.058473 | 0.043038 | 0.048756 | -0.012688 | 0.019721 | -0.017566 | 0.065863 | 0.073622 | 0.16028 | -0.072215 | 0.083464 | 0.48112 | -0.028879 | 121.9503 | 122.2074 | 122.1282 | -0.13668 | 0.023915 | -122.1525 | 0.083442 | 0.078564 | 0.054649 | -122.1447 | -122.058 | -0.040546 | -0.26801 | 0.17959 | 0.067251 | 0.1078 | -0.010873 | -0.090086 | 0.16199 | 0.16975 | 0.25641 | 0.11585 | -122.2905 | 122.0464 | 122.3036 | 122.2244 | 0.57725 | -122.355
2714.3125 | 122.3969 | -0.050354 | 122.2183 | -0.01778 | -0.046051 | 0.040934 | 0.021819 | -0.012078 | -0.0025169 | -0.021518 | -0.0024804 | -0.0020767 | 0.058687 | 0.042824 | 0.048542 | -0.017266 | 0.0243 | -0.017566 | 0.065863 | 0.069043 | 0.17402 | -0.076794 | 0.092622 | 0.4857 | -0.038036 | 121.9457 | 122.212 | 122.1237 | -0.13668 | -0.02644 | -122.1525 | 0.033088 | 0.032788 | 0.059228 | -122.1493 | -122.0443 | -0.086322 | -0.27259 | 0.14298 | 0.012318 | 0.09864 | -0.006294 | -0.094665 | 0.11622 | 0.1194 | 0.22437 | 0.074654 | -122.2951 | 121.9961 | 122.2624 | 122.174 | 0.53606 | -122.355
2716 | 122.3145 | -0.082397 | 122.2275 | -0.010149 | -0.046265 | 0.040507 | 0.021606 | -0.011865 | -0.0025169 | -0.021518 | -0.0022666 | -0.0025041 | 0.058473 | 0.043038 | 0.048969 | -0.017266 | 0.015142 | -0.022144 | 0.065863 | 0.073622 | 0.16944 | -0.072215 | 0.088043 | 0.48112 | -0.033458 | 121.9457 | 122.2074 | 122.1282 | -0.13668 | 0.010182 | -122.1616 | 0.065131 | 0.060253 | 0.050071 | -122.1539 | -122.058 | -0.054279 | -0.28174 | 0.17044 | 0.048939 | 0.10322 | -0.020028 | -0.099241 | 0.14826 | 0.15602 | 0.25184 | 0.097539 | -122.2997 | 122.0281 | 122.2898 | 122.2106 | 0.56352 | -122.3642
2717.75 | 122.3694 | -0.082397 | 122.2 | -0.010149 | -0.046265 | 0.040507 | 0.021392 | -0.012078 | -0.0025169 | -0.021518 | -0.0024804 | -0.0022903 | 0.058901 | 0.043252 | 0.048969 | -0.017266 | 0.015142 | -0.012988 | 0.070441 | 0.078201 | 0.16486 | -0.076794 | 0.083464 | 0.48112 | -0.028879 | 121.9457 | 122.212 | 122.1237 | -0.14125 | 0.005603 | -122.1296 | 0.065131 | 0.069409 | 0.063806 | -122.1218 | -122.0352 | -0.058858 | -0.25428 | 0.16586 | 0.053518 | 0.11238 | 0.012017 | -0.076354 | 0.15284 | 0.1606 | 0.24726 | 0.097539 | -122.2768 | 122.0281 | 122.2944 | 122.2061 | 0.56352 | -122.3413
2719.4531 | 122.3785 | -0.064087 | 122.1954 | -0.01778 | -0.046051 | 0.040721 | 0.021392 | -0.012292 | -0.0025169 | -0.021518 | -0.0024804 | -0.0025041 | 0.05826 | 0.043252 | 0.048969 | -0.008109 | 0.0243 | -0.012988 | 0.065863 | 0.073622 | 0.16944 | -0.076794 | 0.083464 | 0.4857 | -0.028879 | 121.9457 | 122.2074 | 122.1237 | -0.14125 | -0.012707 | -122.1296 | 0.055978 | 0.051099 | 0.063806 | -122.1218 | -122.026 | -0.077168 | -0.2497 | 0.14755 | 0.035208 | 0.11238 | 0.012015 | -0.071777 | 0.12995 | 0.13771 | 0.23353 | 0.088387 | -122.2722 | 122.0098 | 122.2715 | 122.1877 | 0.54979 | -122.3367
2721.2188 | 122.3328 | -0.10986 | 122.2412 | -0.01778 | -0.045837 | 0.040721 | 0.021606 | -0.012292 | -0.0029443 | -0.0062567 | -0.0022666 | -0.0022903 | 0.05826 | 0.043038 | 0.048756 | -0.017266 | 0.019721 | -0.017566 | 0.070441 | 0.078201 | 0.16486 | -0.076794 | 0.078886 | 0.47654 | -0.033458 | 121.9366 | 122.212 | 122.1328 | -0.14125 | 0.033069 | -122.1708 | 0.092597 | 0.092297 | 0.059228 | -122.163 | -122.0764 | -0.031392 | -0.30463 | 0.18875 | 0.076405 | 0.1078 | -0.029182 | -0.1084 | 0.1803 | 0.18806 | 0.27472 | 0.12958 | -122.318 | 122.0464 | 122.3219 | 122.2427 | 0.58641 | -122.3825
2722.9688 | 122.4289 | -0.073242 | 122.2046 | -0.010149 | -0.046265 | 0.040934 | 0.021392 | -0.012292 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.043038 | 0.048969 | -0.017266 | 0.015142 | -0.017566 | 0.070441 | 0.073622 | 0.16486 | -0.072215 | 0.088043 | 0.47654 | -0.038036 | 121.9549 | 122.212 | 122.1374 | -0.1321 | 0.001027 | -122.1341 | 0.055976 | 0.055676 | 0.054649 | -122.131 | -122.0397 | -0.058855 | -0.2497 | 0.16129 | 0.035206 | 0.094061 | 0.007439 | -0.067196 | 0.14368 | 0.14686 | 0.2381 | 0.088384 | -122.2768 | 122.0281 | 122.2853 | 122.2106 | 0.54979 | -122.3367
2724.7344 | 122.374 | -0.059509 | 122.1863 | -0.0025182 | -0.046265 | 0.040934 | 0.021606 | -0.012292 | -0.0027305 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.043252 | 0.048756 | -0.017266 | 0.010564 | -0.012988 | 0.065863 | 0.078201 | 0.16944 | -0.076794 | 0.088043 | 0.4857 | -0.033458 | 121.9503 | 122.212 | 122.1237 | -0.14583 | -0.017285 | -122.1204 | 0.042243 | 0.046521 | 0.063806 | -122.1081 | -122.0168 | -0.086324 | -0.23596 | 0.14755 | 0.026051 | 0.11237 | 0.02575 | -0.062621 | 0.12537 | 0.13771 | 0.22895 | 0.070073 | -122.2631 | 122.0098 | 122.2715 | 122.1832 | 0.54521 | -122.3321
2726.4375 | 122.3373 | -0.10071 | 122.2412 | -0.01778 | -0.046051 | 0.040507 | 0.021819 | -0.012292 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.058901 | 0.042824 | 0.048756 | -0.017266 | 0.019721 | -0.017566 | 0.065863 | 0.069043 | 0.16028 | -0.067636 | 0.083464 | 0.48112 | -0.033458 | 121.9457 | 122.2029 | 122.1328 | -0.14125 | 0.033072 | -122.1753 | 0.083442 | 0.083142 | 0.05007 | -122.1722 | -122.0809 | -0.040547 | -0.29548 | 0.18417 | 0.06725 | 0.1078 | -0.038339 | -0.1084 | 0.16657 | 0.16975 | 0.26099 | 0.12043 | -122.3088 | 122.0464 | 122.3036 | 122.2335 | 0.58183 | -122.3825
2728.1875 | 122.4701 | -0.068665 | 122.2092 | -0.010149 | -0.046265 | 0.040721 | 0.021392 | -0.012078 | -0.0025169 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.043038 | 0.048756 | -0.017266 | 0.019721 | -0.012988 | 0.065863 | 0.073622 | 0.16944 | -0.072215 | 0.083464 | 0.48112 | -0.033458 | 121.9457 | 122.2074 | 122.1237 | -0.14125 | -0.00355 | -122.1433 | 0.051399 | 0.055677 | 0.059227 | -122.1355 | -122.0397 | -0.07259 | -0.26343 | 0.15213 | 0.035207 | 0.1078 | -0.001717 | -0.085509 | 0.13453 | 0.14229 | 0.2381 | 0.088386 | -122.2814 | 122.0144 | 122.2761 | 122.1923 | 0.54979 | -122.3504
2729.9531 | 122.4518 | -0.073242 | 122.2229 | -0.010149 | -0.046265 | 0.040934 | 0.021392 | -0.012506 | -0.0029443 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058687 | 0.043252 | 0.048969 | -0.021844 | 0.019721 | -0.017566 | 0.070441 | 0.073622 | 0.16486 | -0.076794 | 0.083464 | 0.4857 | -0.028879 | 121.9366 | 122.2029 | 122.1282 | -0.14125 | -0.003552 | -122.1525 | 0.051398 | 0.055676 | 0.059228 | -122.1493 | -122.058 | -0.068013 | -0.28632 | 0.15671 | 0.044363 | 0.11238 | -0.020028 | -0.094663 | 0.14368 | 0.14686 | 0.2381 | 0.092963 | -122.2997 | 122.0098 | 122.2761 | 122.2015 | 0.55894 | -122.3642
2731.7188 | 122.3007 | -0.09613 | 122.2412 | -0.0025182 | -0.046478 | 0.040507 | 0.021392 | -0.012292 | -0.0027305 | -0.021518 | -0.002053 | -0.0022903 | 0.058473 | 0.043252 | 0.048542 | -0.017266 | 0.019721 | -0.017566 | 0.065863 | 0.078201 | 0.16944 | -0.072215 | 0.097201 | 0.4857 | -0.033458 | 121.9549 | 122.212 | 122.1282 | -0.13668 | 0.023915 | -122.1753 | 0.078864 | 0.078564 | 0.054649 | -122.163 | -122.0718 | -0.040546 | -0.28632 | 0.19333 | 0.062672 | 0.10322 | -0.029182 | -0.11297 | 0.16199 | 0.17433 | 0.26557 | 0.11585 | -122.3134 | 122.051 | 122.3082 | 122.2244 | 0.58183 | -122.3779
2733.4062 | 122.4197 | -0.068665 | 122.1817 | -0.010149 | -0.046265 | 0.040293 | 0.021178 | -0.011865 | -0.0027305 | -0.013887 | -0.0022666 | -0.0027177 | 0.058687 | 0.042824 | 0.049183 | -0.021844 | 0.0243 | -0.012988 | 0.061284 | 0.064464 | 0.16944 | -0.072215 | 0.083464 | 0.48112 | -0.028879 | 121.9595 | 122.2166 | 122.1282 | -0.14125 | -0.00355 | -122.1204 | 0.046821 | 0.055677 | 0.059227 | -122.1172 | -122.0123 | -0.07259 | -0.22223 | 0.15213 | 0.039786 | 0.11238 | 0.034906 | -0.053465 | 0.12995 | 0.13313 | 0.2381 | 0.092965 | -122.2539 | 122.0281 | 122.2853 | 122.1969 | 0.54979 | -122.323
2735.1562 | 122.3053 | -0.10986 | 122.2458 | -0.0025182 | -0.046478 | 0.040934 | 0.021606 | -0.012506 | -0.0025169 | -0.029148 | -0.0024804 | -0.0025041 | 0.058473 | 0.043465 | 0.049183 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.078201 | 0.16944 | -0.081373 | 0.078886 | 0.47654 | -0.033458 | 121.9503 | 122.2074 | 122.1237 | -0.14583 | 0.02849 | -122.1799 | 0.097175 | 0.096875 | 0.068385 | -122.1676 | -122.0764 | -0.03597 | -0.29547 | 0.18875 | 0.076405 | 0.11237 | -0.038339 | -0.12213 | 0.17573 | 0.18806 | 0.2793 | 0.12958 | -122.3272 | 122.0602 | 122.3173 | 122.2335 | 0.58641 | -122.3916
2736.9062 | 122.3282 | -0.09613 | 122.2595 | -0.01778 | -0.046265 | 0.040507 | 0.021392 | -0.012292 | -0.0025169 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.043465 | 0.048542 | -0.017266 | 0.019721 | -0.017566 | 0.07502 | 0.073622 | 0.17402 | -0.076794 | 0.088043 | 0.48112 | -0.033458 | 121.9549 | 122.2166 | 122.1374 | -0.14125 | 0.019336 | -122.1845 | 0.078864 | 0.078564 | 0.059228 | -122.1859 | -122.0855 | -0.045125 | -0.30463 | 0.18417 | 0.062672 | 0.1078 | -0.042913 | -0.12213 | 0.17115 | 0.16975 | 0.27015 | 0.11585 | -122.3363 | 122.051 | 122.3127 | 122.2335 | 0.57725 | -122.4008
2738.6562 | 122.3465 | -0.10071 | 122.2183 | -0.0025182 | -0.046265 | 0.040721 | 0.021392 | -0.012078 | -0.0025169 | -0.013887 | -0.0024804 | -0.0018631 | 0.058687 | 0.043038 | 0.048756 | -0.017266 | 0.019721 | -0.008409 | 0.056706 | 0.073622 | 0.16028 | -0.076794 | 0.083464 | 0.4857 | -0.038036 | 121.9549 | 122.212 | 122.1328 | -0.14125 | 0.023914 | -122.1616 | 0.083442 | 0.092299 | 0.068385 | -122.1447 | -122.058 | -0.040547 | -0.26343 | 0.18417 | 0.062672 | 0.10322 | -0.006294 | -0.085507 | 0.15741 | 0.17433 | 0.26099 | 0.12043 | -122.2951 | 122.0556 | 122.3127 | 122.2335 | 0.58641 | -122.3596
2740.3438 | 122.3602 | -0.086975 | 122.1863 | -0.010149 | -0.046692 | 0.040934 | 0.021392 | -0.012078 | -0.0027305 | -0.013887 | -0.0024804 | -0.0022903 | 0.058901 | 0.043252 | 0.048756 | -0.012688 | 0.019721 | -0.008409 | 0.065863 | 0.073622 | 0.16486 | -0.072215 | 0.088043 | 0.47654 | -0.038036 | 121.9549 | 122.2212 | 122.1282 | -0.14125 | 0.01476 | -122.1204 | 0.074287 | 0.078566 | 0.063806 | -122.1127 | -122.0214 | -0.05428 | -0.23139 | 0.17502 | 0.048939 | 0.10322 | 0.034907 | -0.058042 | 0.15284 | 0.1606 | 0.25183 | 0.1067 | -122.2585 | 122.0419 | 122.3082 | 122.2152 | 0.56352 | -122.3275
2742.1094 | 122.4472 | -0.054932 | 122.1771 | -0.010149 | -0.046478 | 0.040507 | 0.021392 | -0.012078 | -0.0025169 | -0.021518 | -0.0024804 | -0.0020767 | 0.058473 | 0.043252 | 0.048969 | -0.017266 | 0.015142 | -0.012988 | 0.070441 | 0.078201 | 0.16944 | -0.067636 | 0.083464 | 0.48112 | -0.038036 | 121.9503 | 122.2212 | 122.1237 | -0.14583 | -0.012704 | -122.1067 | 0.037666 | 0.041944 | 0.054648 | -122.0989 | -122.0077 | -0.090901 | -0.22681 | 0.1384 | 0.016896 | 0.1078 | 0.044062 | -0.053466 | 0.12537 | 0.13313 | 0.22437 | 0.070074 | -122.2448 | 122.0052 | 122.2761 | 122.1786 | 0.53606 | -122.323
2743.8594 | 122.3877 | -0.064087 | 122.2092 | -0.010149 | -0.046692 | 0.04008 | 0.021178 | -0.012078 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.043252 | 0.048969 | -0.017266 | 0.010564 | -0.017566 | 0.061284 | 0.078201 | 0.16486 | -0.072215 | 0.083464 | 0.47654 | -0.028879 | 121.9595 | 122.2166 | 122.1374 | -0.14125 | -0.008128 | -122.1479 | 0.046821 | 0.046521 | 0.054649 | -122.131 | -122.0443 | -0.077168 | -0.2497 | 0.14755 | 0.035208 | 0.11238 | 0.007441 | -0.071773 | 0.12537 | 0.14229 | 0.22895 | 0.074651 | -122.2814 | 122.0236 | 122.2807 | 122.2015 | 0.54063 | -122.3504
2745.625 | 122.3419 | -0.091553 | 122.2595 | -0.0025182 | -0.046265 | 0.040721 | 0.021606 | -0.012506 | -0.0025169 | -0.021518 | -0.002053 | -0.0020767 | 0.058473 | 0.043038 | 0.048756 | -0.012688 | 0.010564 | -0.012988 | 0.070441 | 0.078201 | 0.1557 | -0.076794 | 0.078886 | 0.4857 | -0.033458 | 121.9549 | 122.2074 | 122.1328 | -0.14125 | 0.014759 | -122.1891 | 0.078865 | 0.078565 | 0.063806 | -122.1813 | -122.1038 | -0.049702 | -0.30463 | 0.17044 | 0.058095 | 0.1078 | -0.052071 | -0.12671 | 0.16199 | 0.16975 | 0.24726 | 0.10212 | -122.3363 | 122.0464 | 122.299 | 122.2244 | 0.57726 | -122.4008
2747.3125 | 122.319 | -0.10529 | 122.2595 | -0.010149 | -0.046265 | 0.040507 | 0.021392 | -0.012292 | -0.0029443 | -0.013887 | -0.002053 | -0.0022903 | 0.058901 | 0.043465 | 0.048756 | -0.017266 | 0.019721 | -0.022144 | 0.065863 | 0.073622 | 0.16944 | -0.072215 | 0.092622 | 0.48112 | -0.033458 | 121.9503 | 122.2166 | 122.1328 | -0.14125 | 0.033071 | -122.1937 | 0.08802 | 0.083142 | 0.050071 | -122.1859 | -122.0901 | -0.035969 | -0.30921 | 0.19791 | 0.071828 | 0.1078 | -0.042913 | -0.12671 | 0.17115 | 0.17891 | 0.27472 | 0.12501 | -122.3317 | 122.0556 | 122.3219 | 122.2381 | 0.58641 | -122.4008
2749.0781 | 122.3511 | -0.086975 | 122.2183 | -0.010149 | -0.046478 | 0.040934 | 0.021392 | -0.012506 | -0.0031579 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.042824 | 0.048969 | -0.021844 | 0.005985 | -0.012988 | 0.065863 | 0.073622 | 0.16486 | -0.076794 | 0.074307 | 0.4857 | -0.033458 | 121.9457 | 122.212 | 122.1374 | -0.14583 | 0.010181 | -122.1525 | 0.065131 | 0.073987 | 0.063806 | -122.1447 | -122.0535 | -0.058858 | -0.27259 | 0.16128 | 0.053517 | 0.11237 | -0.006294 | -0.080929 | 0.15284 | 0.1606 | 0.25183 | 0.09296 | -122.2951 | 122.0327 | 122.299 | 122.2244 | 0.57268 | -122.3642
2750.8438 | 122.438 | -0.045776 | 122.1909 | -0.010149 | -0.046265 | 0.040293 | 0.021178 | -0.011865 | -0.0027305 | -0.021518 | -0.0022666 | -0.0025041 | 0.058687 | 0.043252 | 0.048542 | -0.017266 | 0.0243 | -0.017566 | 0.065863 | 0.078201 | 0.16028 | -0.081373 | 0.083464 | 0.49028 | -0.028879 | 121.9503 | 122.2074 | 122.1328 | -0.13668 | -0.035597 | -122.125 | 0.02851 | 0.02821 | 0.063807 | -122.1127 | -122.0306 | -0.0909 | -0.24054 | 0.12924 | 0.016897 | 0.1078 | 0.016593 | -0.058041 | 0.11164 | 0.12398 | 0.20606 | 0.070076 | -122.2722 | 121.9961 | 122.2532 | 122.1786 | 0.53606 | -122.3275
2752.5312 | 122.3694 | -0.073242 | 122.2046 | -0.0025182 | -0.046692 | 0.040507 | 0.021606 | -0.012292 | -0.0025169 | -0.029148 | -0.0024804 | -0.0022903 | 0.058473 | 0.043252 | 0.048969 | -0.017266 | 0.015142 | -0.012988 | 0.065863 | 0.073622 | 0.16486 | -0.076794 | 0.078886 | 0.4857 | -0.033458 | 121.9503 | 122.2166 | 122.1374 | -0.14583 | -0.003552 | -122.1387 | 0.055976 | 0.060254 | 0.063806 | -122.131 | -122.0397 | -0.072591 | -0.25428 | 0.15213 | 0.039784 | 0.11237 | 0.012018 | -0.067196 | 0.13911 | 0.14686 | 0.2381 | 0.088384 | -122.2814 | 122.0236 | 122.2898 | 122.2106 | 0.55894 | -122.3504
2754.2812 | 122.3145 | -0.09613 | 122.2275 | -0.010149 | -0.046692 | 0.040293 | 0.021606 | -0.012506 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.043252 | 0.048542 | -0.012688 | 0.015142 | -0.012988 | 0.065863 | 0.073622 | 0.16944 | -0.076794 | 0.083464 | 0.4857 | -0.028879 | 121.9549 | 122.2166 | 122.1282 | -0.1321 | 0.019336 | -122.1616 | 0.083442 | 0.083142 | 0.063806 | -122.1539 | -122.058 | -0.035967 | -0.27259 | 0.17959 | 0.067251 | 0.10322 | -0.01087 | -0.099241 | 0.16199 | 0.16975 | 0.26557 | 0.11127 | -122.3043 | 122.051 | 122.3127 | 122.2244 | 0.58183 | -122.3596
2755.9844 | 122.3007 | -0.10071 | 122.2366 | -0.010149 | -0.046906 | 0.040507 | 0.021392 | -0.012078 | -0.0027305 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.043252 | 0.048328 | -0.003531 | 0.015142 | -0.017566 | 0.061284 | 0.078201 | 0.16944 | -0.072215 | 0.083464 | 0.4857 | -0.028879 | 121.9503 | 122.212 | 122.1282 | -0.14125 | 0.028493 | -122.1753 | 0.097177 | 0.083142 | 0.054649 | -122.1584 | -122.0672 | -0.040547 | -0.28632 | 0.18417 | 0.071829 | 0.11238 | -0.024604 | -0.1084 | 0.16199 | 0.17891 | 0.27015 | 0.11585 | -122.3088 | 122.051 | 122.3127 | 122.2289 | 0.58641 | -122.3779
2757.7344 | 122.3099 | -0.1236 | 122.2 | -0.0025182 | -0.046692 | 0.040721 | 0.021392 | -0.012292 | -0.0027305 | -0.013887 | -0.0022666 | -0.0027177 | 0.058687 | 0.043038 | 0.048756 | -0.012688 | 0.015142 | -0.017566 | 0.070441 | 0.08278 | 0.16486 | -0.081373 | 0.083464 | 0.49028 | -0.028879 | 121.9503 | 122.2258 | 122.1328 | -0.13668 | 0.042223 | -122.1296 | 0.11091 | 0.10603 | 0.063807 | -122.1172 | -122.0352 | -0.01308 | -0.2497 | 0.20706 | 0.094717 | 0.1078 | 0.025753 | -0.067196 | 0.19404 | 0.20638 | 0.28846 | 0.13874 | -122.2814 | 122.0739 | 122.3494 | 122.2564 | 0.61388 | -122.3367
2759.4219 | 122.4197 | -0.059509 | 122.2092 | -0.01778 | -0.046692 | 0.040721 | 0.021606 | -0.012506 | -0.0023033 | -0.021518 | -0.0024804 | -0.0022903 | 0.05826 | 0.042824 | 0.048542 | -0.017266 | 0.015142 | -0.017566 | 0.065863 | 0.073622 | 0.1786 | -0.076794 | 0.083464 | 0.4857 | -0.028879 | 121.9549 | 122.2166 | 122.1282 | -0.14583 | -0.017285 | -122.1433 | 0.042243 | 0.041943 | 0.059228 | -122.1355 | -122.0306 | -0.086324 | -0.25427 | 0.14297 | 0.03063 | 0.11695 | 0.007441 | -0.08093 | 0.12537 | 0.13313 | 0.2381 | 0.074651 | -122.286 | 122.0144 | 122.2761 | 122.1877 | 0.54521 | -122.355
2761.1875 | 122.3236 | -0.086975 | 122.2229 | -0.01778 | -0.046478 | 0.040721 | 0.020965 | -0.012292 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.043038 | 0.048756 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.073622 | 0.16944 | -0.072215 | 0.088043 | 0.4857 | -0.028879 | 121.9549 | 122.2166 | 122.1374 | -0.14583 | 0.01476 | -122.157 | 0.074287 | 0.073987 | 0.059227 | -122.1493 | -122.0535 | -0.058858 | -0.26801 | 0.17502 | 0.058096 | 0.11695 | -0.006292 | -0.085506 | 0.15284 | 0.1606 | 0.25641 | 0.1067 | -122.2951 | 122.0419 | 122.3036 | 122.2244 | 0.57268 | -122.3687
2762.9375 | 122.4243 | -0.054932 | 122.2092 | -0.01778 | -0.046692 | 0.040721 | 0.021392 | -0.012292 | -0.0027305 | -0.013887 | -0.0022666 | -0.0022903 | 0.058687 | 0.043252 | 0.048542 | -0.017266 | 0.019721 | -0.022144 | 0.065863 | 0.073622 | 0.16944 | -0.076794 | 0.078886 | 0.49028 | -0.042615 | 121.9595 | 122.2212 | 122.1328 | -0.13668 | -0.021862 | -122.1433 | 0.037666 | 0.032788 | 0.05465 | -122.1355 | -122.0397 | -0.081744 | -0.2497 | 0.13382 | 0.012317 | 0.094061 | 0.012019 | -0.076351 | 0.1208 | 0.12855 | 0.22437 | 0.074653 | -122.286 | 122.0144 | 122.2761 | 122.1877 | 0.54521 | -122.3458
2764.6875 | 122.4289 | -0.054932 | 122.1909 | -0.01778 | -0.046906 | 0.040721 | 0.021606 | -0.012506 | -0.0023033 | -0.013887 | -0.0022666 | -0.0020767 | 0.05826 | 0.043465 | 0.048542 | -0.021844 | 0.015142 | -0.012988 | 0.07502 | 0.073622 | 0.16944 | -0.076794 | 0.074307 | 0.4857 | -0.028879 | 121.9457 | 122.2212 | 122.1374 | -0.14125 | -0.021862 | -122.1158 | 0.033088 | 0.041944 | 0.063806 | -122.1172 | -122.0214 | -0.086323 | -0.24512 | 0.12924 | 0.026053 | 0.11238 | 0.030329 | -0.053463 | 0.12995 | 0.12855 | 0.22437 | 0.070074 | -122.2677 | 122.0007 | 122.2761 | 122.1923 | 0.54063 | -122.3321
2766.375 | 122.438 | -0.064087 | 122.1954 | -0.01778 | -0.046692 | 0.040721 | 0.021606 | -0.012506 | -0.0029443 | -0.013887 | -0.0022666 | -0.0020767 | 0.058473 | 0.043465 | 0.048542 | -0.017266 | 0.019721 | -0.012988 | 0.065863 | 0.073622 | 0.16486 | -0.076794 | 0.083464 | 0.49028 | -0.033458 | 121.9595 | 122.2166 | 122.1328 | -0.13668 | -0.012707 | -122.1296 | 0.046821 | 0.051099 | 0.063806 | -122.1218 | -122.0306 | -0.072589 | -0.23596 | 0.14755 | 0.030629 | 0.10322 | 0.021173 | -0.062619 | 0.12995 | 0.13771 | 0.22895 | 0.083808 | -122.2722 | 122.0236 | 122.2807 | 122.1969 | 0.55437 | -122.3321
2768.125 | 122.406 | -0.059509 | 122.2046 | -0.010149 | -0.046906 | 0.040721 | 0.021178 | -0.012506 | -0.0027305 | -0.021518 | -0.0024804 | -0.0022903 | 0.058901 | 0.043252 | 0.048328 | -0.017266 | 0.0243 | -0.017566 | 0.070441 | 0.078201 | 0.16944 | -0.081373 | 0.078886 | 0.49486 | -0.033458 | 121.9549 | 122.2212 | 122.1328 | -0.14125 | -0.021864 | -122.1341 | 0.042243 | 0.041943 | 0.063807 | -122.1264 | -122.0352 | -0.081746 | -0.2497 | 0.13839 | 0.026051 | 0.1078 | 0.016596 | -0.071774 | 0.12995 | 0.13771 | 0.22895 | 0.083809 | -122.286 | 122.0144 | 122.2807 | 122.1923 | 0.55437 | -122.3458
2769.8125 | 122.3511 | -0.091553 | 122.2504 | -0.010149 | -0.047119 | 0.040934 | 0.021392 | -0.012292 | -0.0025169 | -0.0062567 | -0.0024804 | -0.0027177 | 0.058687 | 0.043038 | 0.048542 | -0.021844 | 0.019721 | -0.012988 | 0.070441 | 0.069043 | 0.16944 | -0.072215 | 0.083464 | 0.4857 | -0.033458 | 121.9549 | 122.2212 | 122.142 | -0.14125 | 0.019338 | -122.1799 | 0.069709 | 0.078565 | 0.059227 | -122.1813 | -122.0809 | -0.049702 | -0.29547 | 0.17502 | 0.058095 | 0.1078 | -0.02918 | -0.10839 | 0.16199 | 0.1606 | 0.26099 | 0.11127 | -122.3226 | 122.0464 | 122.3127 | 122.2335 | 0.57726 | -122.3916
2771.5625 | 122.3694 | -0.068665 | 122.2137 | -0.0025182 | -0.046906 | 0.040721 | 0.021178 | -0.012292 | -0.0029443 | -0.029148 | -0.0022666 | -0.0022903 | 0.058687 | 0.043252 | 0.048756 | -0.017266 | 0.0243 | -0.017566 | 0.07502 | 0.069043 | 0.16944 | -0.076794 | 0.078886 | 0.49028 | -0.028879 | 121.9595 | 122.2212 | 122.1328 | -0.14125 | -0.008129 | -122.1387 | 0.051399 | 0.051099 | 0.059228 | -122.1447 | -122.0443 | -0.07259 | -0.25427 | 0.14755 | 0.039786 | 0.11238 | 0.007441 | -0.080929 | 0.14369 | 0.13771 | 0.2381 | 0.092965 | -122.2905 | 122.0281 | 122.2899 | 122.2015 | 0.55895 | -122.355
2773.25 | 122.3785 | -0.073242 | 122.2092 | -0.010149 | -0.046906 | 0.040507 | 0.021392 | -0.012292 | -0.0029443 | -0.029148 | -0.002053 | -0.0022903 | 0.058473 | 0.043679 | 0.048542 | -0.021844 | 0.019721 | -0.012988 | 0.079598 | 0.073622 | 0.17402 | -0.076794 | 0.083464 | 0.49028 | -0.033458 | 121.9503 | 122.2258 | 122.1374 | -0.14125 | -0.003552 | -122.1296 | 0.051398 | 0.060254 | 0.063806 | -122.1355 | -122.0352 | -0.068013 | -0.25885 | 0.15671 | 0.039784 | 0.1078 | 0.016598 | -0.071773 | 0.15284 | 0.14686 | 0.24726 | 0.092963 | -122.286 | 122.0236 | 122.299 | 122.2106 | 0.56352 | -122.3504
2775 | 122.406 | -0.064087 | 122.1863 | -0.01778 | -0.047119 | 0.040507 | 0.021606 | -0.012292 | -0.0029443 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.043038 | 0.048969 | -0.017266 | 0.019721 | -0.012988 | 0.070441 | 0.069043 | 0.16486 | -0.081373 | 0.078886 | 0.4857 | -0.042615 | 121.9595 | 122.2212 | 122.1374 | -0.1321 | -0.017286 | -122.1158 | 0.046821 | 0.051099 | 0.068385 | -122.1172 | -122.0214 | -0.06801 | -0.22681 | 0.14297 | 0.021472 | 0.089482 | 0.034907 | -0.048885 | 0.13453 | 0.13313 | 0.22895 | 0.083808 | -122.2677 | 122.0236 | 122.2853 | 122.2015 | 0.54979 | -122.3184
2776.7656 | 122.4243 | -0.068665 | 122.1909 | -0.0025182 | -0.046906 | 0.040507 | 0.021392 | -0.012506 | -0.0029443 | -0.013887 | -0.002694 | -0.0020767 | 0.058687 | 0.043465 | 0.048756 | -0.012688 | 0.019721 | -0.017566 | 0.070441 | 0.078201 | 0.16944 | -0.072215 | 0.078886 | 0.4857 | -0.033458 | 121.9503 | 122.2212 | 122.1374 | -0.14583 | -0.00355 | -122.1204 | 0.055977 | 0.051099 | 0.054649 | -122.1127 | -122.0214 | -0.077168 | -0.24054 | 0.14755 | 0.035207 | 0.11237 | 0.030329 | -0.053463 | 0.13911 | 0.14687 | 0.2381 | 0.088386 | -122.2631 | 122.019 | 122.2899 | 122.2061 | 0.55437 | -122.3367
2778.4531 | 122.3785 | -0.054932 | 122.2046 | -0.0025182 | -0.046692 | 0.040721 | 0.021819 | -0.012506 | -0.0029443 | -0.0062567 | -0.0016258 | -0.0025041 | 0.058473 | 0.043252 | 0.048328 | -0.021844 | 0.019721 | -0.022144 | 0.065863 | 0.078201 | 0.16944 | -0.072215 | 0.088043 | 0.4857 | -0.033458 | 121.9503 | 122.2166 | 122.1374 | -0.1321 | -0.017283 | -122.1387 | 0.033088 | 0.032788 | 0.050071 | -122.1264 | -122.0352 | -0.077165 | -0.25428 | 0.14297 | 0.021474 | 0.098639 | 0.012018 | -0.067196 | 0.1208 | 0.13313 | 0.22437 | 0.074653 | -122.2768 | 122.0052 | 122.2715 | 122.1923 | 0.54063 | -122.3367
2780.2031 | 122.3877 | -0.068665 | 122.2092 | -0.01778 | -0.046478 | 0.040721 | 0.021178 | -0.012506 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.043465 | 0.048542 | -0.021844 | 0.019721 | -0.017566 | 0.061284 | 0.073622 | 0.16944 | -0.076794 | 0.083464 | 0.48112 | -0.038036 | 121.9595 | 122.2166 | 122.142 | -0.14125 | -0.008129 | -122.1479 | 0.046821 | 0.051099 | 0.059228 | -122.1355 | -122.0397 | -0.07259 | -0.2497 | 0.15213 | 0.030629 | 0.10322 | 0.007441 | -0.067194 | 0.12995 | 0.14229 | 0.2381 | 0.088386 | -122.286 | 122.0281 | 122.2853 | 122.2106 | 0.54979 | -122.3504
2781.9688 | 122.3602 | -0.086975 | 122.2137 | -0.025411 | -0.046906 | 0.040721 | 0.021819 | -0.012292 | -0.0029443 | -0.013887 | -0.0022666 | -0.0025041 | 0.058687 | 0.043465 | 0.048756 | -0.021844 | 0.019721 | -0.017566 | 0.070441 | 0.078201 | 0.16944 | -0.076794 | 0.083464 | 0.48112 | -0.033458 | 121.9595 | 122.2303 | 122.1374 | -0.14125 | 0.010181 | -122.1433 | 0.065131 | 0.069409 | 0.059228 | -122.1355 | -122.0443 | -0.05428 | -0.25427 | 0.17044 | 0.053517 | 0.1078 | 0.016599 | -0.076351 | 0.15742 | 0.16518 | 0.25641 | 0.1067 | -122.2905 | 122.0464 | 122.3173 | 122.2244 | 0.5681 | -122.355
2783.7344 | 122.4289 | -0.050354 | 122.2092 | -0.01778 | -0.046692 | 0.040721 | 0.021606 | -0.012506 | -0.0027305 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058473 | 0.043465 | 0.048756 | -0.026423 | 0.019721 | -0.012988 | 0.070441 | 0.073622 | 0.16944 | -0.076794 | 0.078886 | 0.4857 | -0.033458 | 121.9549 | 122.2258 | 122.1328 | -0.13668 | -0.02644 | -122.1387 | 0.023931 | 0.037366 | 0.063806 | -122.1355 | -122.0397 | -0.086322 | -0.25427 | 0.12924 | 0.016896 | 0.10322 | 0.016598 | -0.076351 | 0.1208 | 0.12398 | 0.21979 | 0.070075 | -122.286 | 122.0052 | 122.2761 | 122.1832 | 0.53606 | -122.3458
2785.4219 | 122.3328 | -0.07782 | 122.2366 | 0.0051128 | -0.046906 | 0.040507 | 0.021606 | -0.012292 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.043038 | 0.048969 | -0.017266 | 0.019721 | -0.017566 | 0.061284 | 0.078201 | 0.17402 | -0.072215 | 0.083464 | 0.49028 | -0.028879 | 121.9549 | 122.2212 | 122.142 | -0.14125 | 0.005605 | -122.1753 | 0.060554 | 0.060254 | 0.054649 | -122.1584 | -122.0626 | -0.063435 | -0.28174 | 0.16128 | 0.048941 | 0.11238 | -0.015447 | -0.09466 | 0.1391 | 0.15602 | 0.25184 | 0.097541 | -122.3088 | 122.0327 | 122.299 | 122.2198 | 0.5681 | -122.3779
2787.1875 | 122.3145 | -0.1236 | 122.2275 | -0.0025182 | -0.046692 | 0.040507 | 0.021606 | -0.012506 | -0.0031579 | -0.013887 | -0.0022666 | -0.0025041 | 0.058473 | 0.043252 | 0.048542 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.073622 | 0.16486 | -0.081373 | 0.078886 | 0.49028 | -0.028879 | 121.9595 | 122.2212 | 122.1374 | -0.13668 | 0.042223 | -122.1616 | 0.11091 | 0.11061 | 0.068385 | -122.1539 | -122.0626 | -0.01308 | -0.26801 | 0.20248 | 0.094717 | 0.1078 | -0.006292 | -0.090084 | 0.18946 | 0.19722 | 0.28846 | 0.14332 | -122.3089 | 122.0831 | 122.3448 | 122.261 | 0.61388 | -122.3642
2788.875 | 122.3236 | -0.10071 | 122.2137 | -0.010149 | -0.047119 | 0.040721 | 0.021392 | -0.012506 | -0.0025169 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058473 | 0.043679 | 0.048756 | -0.012688 | 0.015142 | -0.017566 | 0.070441 | 0.073622 | 0.1786 | -0.085952 | 0.078886 | 0.49486 | -0.028879 | 121.9595 | 122.2212 | 122.1374 | -0.14583 | 0.014756 | -122.1433 | 0.08802 | 0.083142 | 0.068386 | -122.1401 | -122.0352 | -0.045125 | -0.25427 | 0.17959 | 0.071829 | 0.11695 | 0.007441 | -0.076351 | 0.17115 | 0.17433 | 0.2793 | 0.11585 | -122.2997 | 122.0602 | 122.3219 | 122.2381 | 0.59557 | -122.3596
2790.625 | 122.3923 | -0.059509 | 122.2137 | -0.0025182 | -0.046906 | 0.040721 | 0.021606 | -0.012292 | -0.0031579 | -0.0062567 | -0.0024804 | -0.0025041 | 0.058473 | 0.043252 | 0.048756 | -0.017266 | 0.019721 | -0.003831 | 0.065863 | 0.073622 | 0.16944 | -0.076794 | 0.088043 | 0.49028 | -0.028879 | 121.9549 | 122.2212 | 122.1466 | -0.14583 | -0.017285 | -122.1479 | 0.042243 | 0.055678 | 0.072963 | -122.1401 | -122.0443 | -0.086324 | -0.25885 | 0.14755 | 0.03063 | 0.11695 | 0.007441 | -0.067194 | 0.12537 | 0.13313 | 0.22895 | 0.07923 | -122.2905 | 122.0144 | 122.2807 | 122.2061 | 0.54979 | -122.3596
2792.3125 | 122.4197 | -0.064087 | 122.2275 | -0.010149 | -0.046478 | 0.040507 | 0.021606 | -0.012292 | -0.0029443 | -0.029148 | -0.0022666 | -0.0025041 | 0.058046 | 0.043679 | 0.048542 | -0.012688 | 0.0243 | -0.022144 | 0.070441 | 0.08278 | 0.16944 | -0.076794 | 0.088043 | 0.48112 | -0.042615 | 121.9595 | 122.2212 | 122.1374 | -0.14583 | -0.012707 | -122.157 | 0.051399 | 0.041943 | 0.05465 | -122.1447 | -122.058 | -0.081746 | -0.26801 | 0.15213 | 0.021472 | 0.10322 | -0.006292 | -0.090084 | 0.13453 | 0.14687 | 0.23353 | 0.088387 | -122.3043 | 122.0236 | 122.2853 | 122.2015 | 0.54521 | -122.3733
2794.0625 | 122.3923 | -0.064087 | 122.2183 | -0.010149 | -0.046478 | 0.040721 | 0.021178 | -0.012719 | -0.0025169 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058901 | 0.043252 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.065863 | 0.08278 | 0.16944 | -0.076794 | 0.078886 | 0.49486 | -0.038036 | 121.9549 | 122.2212 | 122.1328 | -0.14125 | -0.012707 | -122.1525 | 0.046821 | 0.051099 | 0.063806 | -122.1355 | -122.0489 | -0.077168 | -0.26343 | 0.14297 | 0.026051 | 0.10322 | 0.002863 | -0.085507 | 0.12995 | 0.14687 | 0.23353 | 0.079229 | -122.2951 | 122.019 | 122.2853 | 122.1969 | 0.55895 | -122.3596
2795.8125 | 122.438 | -0.059509 | 122.1817 | -0.01778 | -0.046906 | 0.040721 | 0.021392 | -0.012506 | -0.0027305 | -0.021518 | -0.0022666 | -0.0020767 | 0.058473 | 0.043465 | 0.048756 | -0.021844 | 0.019721 | -0.017566 | 0.065863 | 0.078201 | 0.16486 | -0.076794 | 0.088043 | 0.49486 | -0.038036 | 121.9549 | 122.2212 | 122.142 | -0.14583 | -0.017285 | -122.1158 | 0.037665 | 0.041943 | 0.059228 | -122.1035 | -122.0168 | -0.086324 | -0.22681 | 0.14755 | 0.021473 | 0.1078 | 0.039484 | -0.039729 | 0.12537 | 0.13771 | 0.22437 | 0.07923 | -122.2585 | 122.0144 | 122.2807 | 122.2015 | 0.55437 | -122.3275
2797.5 | 122.3373 | -0.09613 | 122.2229 | -0.010149 | -0.046692 | 0.040934 | 0.021606 | -0.012292 | -0.0025169 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.043465 | 0.048756 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.078201 | 0.17402 | -0.072215 | 0.083464 | 0.4857 | -0.033458 | 121.9595 | 122.2258 | 122.1466 | -0.14583 | 0.023915 | -122.157 | 0.083442 | 0.083142 | 0.059227 | -122.1447 | -122.0489 | -0.049703 | -0.26343 | 0.17959 | 0.062672 | 0.11237 | 0.002865 | -0.076349 | 0.16199 | 0.17433 | 0.27015 | 0.11585 | -122.2951 | 122.0556 | 122.3219 | 122.2427 | 0.58183 | -122.3687
2799.2656 | 122.3419 | -0.073242 | 122.2321 | -0.01778 | -0.047119 | 0.040507 | 0.021392 | -0.012506 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.043465 | 0.048542 | -0.012688 | 0.015142 | -0.017566 | 0.065863 | 0.078201 | 0.16486 | -0.076794 | 0.083464 | 0.49028 | -0.028879 | 121.9686 | 122.2303 | 122.1374 | -0.13668 | -0.003552 | -122.1662 | 0.060554 | 0.055676 | 0.059228 | -122.1539 | -122.0672 | -0.063434 | -0.26343 | 0.15671 | 0.044363 | 0.1078 | -0.001712 | -0.094662 | 0.13911 | 0.15144 | 0.2381 | 0.088384 | -122.3089 | 122.0419 | 122.3036 | 122.2106 | 0.56352 | -122.3687
2801.0312 | 122.3007 | -0.10986 | 122.2321 | -0.010149 | -0.046692 | 0.040721 | 0.021392 | -0.012719 | -0.0031579 | -0.029148 | -0.0022666 | -0.0020767 | 0.058473 | 0.043465 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.065863 | 0.069043 | 0.16486 | -0.081373 | 0.083464 | 0.49028 | -0.033458 | 121.9641 | 122.2166 | 122.142 | -0.13668 | 0.02849 | -122.1662 | 0.092597 | 0.096875 | 0.068385 | -122.163 | -122.0672 | -0.026813 | -0.26801 | 0.19333 | 0.076405 | 0.10322 | -0.015448 | -0.090083 | 0.17573 | 0.17891 | 0.27472 | 0.12501 | -122.3134 | 122.0739 | 122.3265 | 122.2518 | 0.60014 | -122.3687
2802.7812 | 122.3511 | -0.086975 | 122.2229 | -0.0025182 | -0.046906 | 0.040721 | 0.021178 | -0.012506 | -0.0027305 | -0.021518 | -0.002053 | -0.0020767 | 0.058473 | 0.043679 | 0.048756 | -0.021844 | 0.015142 | -0.022144 | 0.065863 | 0.08278 | 0.16486 | -0.067636 | 0.083464 | 0.49028 | -0.033458 | 121.9641 | 122.2212 | 122.142 | -0.14583 | 0.019339 | -122.157 | 0.065131 | 0.064831 | 0.045492 | -122.1401 | -122.058 | -0.058858 | -0.25885 | 0.17044 | 0.053517 | 0.11237 | -0.001714 | -0.080927 | 0.15284 | 0.16975 | 0.25183 | 0.10212 | -122.2905 | 122.051 | 122.3082 | 122.2289 | 0.57726 | -122.3687
2804.5312 | 122.3465 | -0.086975 | 122.2641 | -0.0025182 | -0.047119 | 0.040507 | 0.021606 | -0.012506 | -0.0029443 | -0.029148 | -0.0022666 | -0.0022903 | 0.058473 | 0.043465 | 0.048542 | -0.017266 | 0.019721 | -0.012988 | 0.065863 | 0.073622 | 0.16944 | -0.076794 | 0.083464 | 0.49028 | -0.033458 | 121.9549 | 122.2166 | 122.142 | -0.14125 | 0.010181 | -122.1982 | 0.069709 | 0.073987 | 0.063806 | -122.1905 | -122.0947 | -0.05428 | -0.30921 | 0.17044 | 0.053517 | 0.1078 | -0.047491 | -0.12213 | 0.15284 | 0.1606 | 0.25641 | 0.1067 | -122.3409 | 122.0419 | 122.3036 | 122.2289 | 0.57726 | -122.4054
2806.2969 | 122.4152 | -0.054932 | 122.1954 | -0.01778 | -0.046906 | 0.040507 | 0.021392 | -0.012506 | -0.0031579 | -0.013887 | -0.002053 | -0.0022903 | 0.05826 | 0.043679 | 0.048756 | -0.017266 | 0.0243 | -0.017566 | 0.07502 | 0.08278 | 0.16944 | -0.076794 | 0.083464 | 0.48112 | -0.038036 | 121.9641 | 122.2212 | 122.1374 | -0.14583 | -0.021862 | -122.1204 | 0.037666 | 0.037366 | 0.059228 | -122.1127 | -122.026 | -0.090901 | -0.23139 | 0.1384 | 0.016896 | 0.1078 | 0.025751 | -0.058041 | 0.12995 | 0.13771 | 0.22437 | 0.079232 | -122.2722 | 122.019 | 122.2761 | 122.1923 | 0.53606 | -122.3413
2808 | 122.3831 | -0.041199 | 122.1863 | -0.01778 | -0.047119 | 0.040721 | 0.021392 | -0.012719 | -0.0029443 | -0.013887 | -0.0022666 | -0.0027177 | 0.05826 | 0.043679 | 0.048756 | -0.017266 | 0.015142 | -0.026723 | 0.07502 | 0.08278 | 0.16944 | -0.072215 | 0.088043 | 0.49028 | -0.028879 | 121.9686 | 122.2166 | 122.142 | -0.14125 | -0.031016 | -122.1113 | 0.023933 | 0.014476 | 0.045492 | -122.1035 | -122.0168 | -0.10006 | -0.21765 | 0.12924 | 0.01232 | 0.11238 | 0.030329 | -0.044306 | 0.11622 | 0.12398 | 0.21064 | 0.056341 | -122.2585 | 122.0098 | 122.2578 | 122.1832 | 0.53148 | -122.3275
2809.6875 | 122.3145 | -0.10071 | 122.2641 | -0.01778 | -0.046906 | 0.040293 | 0.021178 | -0.012506 | -0.0025169 | 0.0013733 | -0.002053 | -0.0022903 | 0.058473 | 0.043679 | 0.048542 | -0.017266 | 0.015142 | -0.008409 | 0.070441 | 0.078201 | 0.17402 | -0.072215 | 0.083464 | 0.48112 | -0.0243 | 121.9641 | 122.212 | 122.1466 | -0.13668 | 0.028493 | -122.1937 | 0.083442 | 0.092299 | 0.063806 | -122.1859 | -122.0901 | -0.035968 | -0.30005 | 0.18417 | 0.076408 | 0.11238 | -0.05207 | -0.11755 | 0.17115 | 0.17891 | 0.27472 | 0.11585 | -122.3363 | 122.0648 | 122.3127 | 122.2473 | 0.58183 | -122.4008
2811.4375 | 122.4701 | -0.054932 | 122.2183 | -0.01778 | -0.046906 | 0.040721 | 0.021178 | -0.012719 | -0.0029443 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.043252 | 0.048542 | -0.021844 | 0.015142 | -0.017566 | 0.065863 | 0.073622 | 0.16028 | -0.072215 | 0.092622 | 0.49486 | -0.033458 | 121.9549 | 122.2303 | 122.1466 | -0.14125 | -0.017283 | -122.1525 | 0.033088 | 0.037366 | 0.054649 | -122.1447 | -122.058 | -0.086323 | -0.26343 | 0.14755 | 0.021474 | 0.1078 | 0.012021 | -0.071772 | 0.1208 | 0.12855 | 0.21521 | 0.070074 | -122.2905 | 122.0098 | 122.2853 | 122.2015 | 0.54979 | -122.3596
2813.1875 | 122.3145 | -0.09613 | 122.2321 | -0.010149 | -0.047119 | 0.040507 | 0.021606 | -0.012506 | -0.0031579 | -0.029148 | -0.0024804 | -0.0025041 | 0.058473 | 0.043465 | 0.048328 | -0.017266 | 0.015142 | -0.017566 | 0.065863 | 0.078201 | 0.16944 | -0.072215 | 0.088043 | 0.49028 | -0.028879 | 121.9641 | 122.2258 | 122.1466 | -0.14125 | 0.023915 | -122.1662 | 0.078864 | 0.078564 | 0.054649 | -122.1539 | -122.0626 | -0.045125 | -0.26801 | 0.18417 | 0.067251 | 0.11238 | -0.006291 | -0.085505 | 0.16199 | 0.17433 | 0.26557 | 0.11127 | -122.3043 | 122.0602 | 122.3219 | 122.2427 | 0.58641 | -122.3733
2814.9375 | 122.3236 | -0.091553 | 122.2458 | -0.010149 | -0.046906 | 0.040507 | 0.021819 | -0.012719 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.043465 | 0.048756 | -0.021844 | 0.019721 | -0.017566 | 0.070441 | 0.08278 | 0.16944 | -0.072215 | 0.083464 | 0.49028 | -0.033458 | 121.9641 | 122.2212 | 122.142 | -0.14125 | 0.019338 | -122.1753 | 0.069709 | 0.073987 | 0.054649 | -122.163 | -122.0764 | -0.049702 | -0.28174 | 0.17502 | 0.058095 | 0.1078 | -0.024603 | -0.10382 | 0.16199 | 0.17433 | 0.26099 | 0.11127 | -122.318 | 122.0556 | 122.3127 | 122.2335 | 0.58183 | -122.387
2816.6406 | 122.4197 | -0.054932 | 122.2046 | -0.025411 | -0.046906 | 0.040293 | 0.021392 | -0.012292 | -0.0029443 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.043465 | 0.048542 | -0.012688 | 0.015142 | -0.017566 | 0.070441 | 0.073622 | 0.16944 | -0.081373 | 0.088043 | 0.4857 | -0.033458 | 121.9595 | 122.2258 | 122.142 | -0.14583 | -0.026441 | -122.1341 | 0.042244 | 0.037366 | 0.063807 | -122.131 | -122.0352 | -0.090901 | -0.24512 | 0.14297 | 0.021474 | 0.11237 | 0.021175 | -0.062617 | 0.12537 | 0.12855 | 0.22437 | 0.070074 | -122.286 | 122.0144 | 122.2807 | 122.1969 | 0.54063 | -122.3504
2818.3906 | 122.3465 | -0.086975 | 122.2275 | -0.0025182 | -0.046906 | 0.040507 | 0.021392 | -0.012719 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.043038 | 0.048328 | -0.012688 | 0.0243 | -0.012988 | 0.061284 | 0.08278 | 0.16944 | -0.076794 | 0.088043 | 0.49944 | -0.028879 | 121.9595 | 122.2212 | 122.1466 | -0.15041 | 0.010181 | -122.1662 | 0.074287 | 0.073987 | 0.063806 | -122.1447 | -122.058 | -0.063437 | -0.26801 | 0.17502 | 0.058096 | 0.12153 | -0.006292 | -0.080927 | 0.14826 | 0.16975 | 0.25641 | 0.11127 | -122.3043 | 122.0464 | 122.3082 | 122.2335 | 0.58641 | -122.3779
2820.0938 | 122.4564 | -0.045776 | 122.2137 | -0.01778 | -0.047333 | 0.040293 | 0.021178 | -0.012292 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.043893 | 0.048542 | -0.021844 | 0.015142 | -0.017566 | 0.061284 | 0.073622 | 0.17402 | -0.072215 | 0.083464 | 0.49486 | -0.028879 | 121.9686 | 122.2212 | 122.1466 | -0.14583 | -0.026439 | -122.1525 | 0.023932 | 0.02821 | 0.054649 | -122.1401 | -122.0397 | -0.10006 | -0.24512 | 0.12924 | 0.016897 | 0.11695 | 0.007441 | -0.067194 | 0.10706 | 0.1194 | 0.21979 | 0.060918 | -122.286 | 122.0144 | 122.267 | 122.1923 | 0.54064 | -122.3596
2821.8594 | 122.3007 | -0.09613 | 122.2321 | -0.010149 | -0.046906 | 0.04008 | 0.021178 | -0.012933 | -0.0029443 | -0.013887 | -0.002053 | -0.0025041 | 0.058473 | 0.043465 | 0.048756 | -0.017266 | 0.019721 | -0.017566 | 0.065863 | 0.073622 | 0.16944 | -0.076794 | 0.092622 | 0.49486 | -0.033458 | 121.9595 | 122.2258 | 122.142 | -0.13668 | 0.019336 | -122.1662 | 0.078864 | 0.078564 | 0.059228 | -122.1584 | -122.0626 | -0.040546 | -0.27259 | 0.18875 | 0.062672 | 0.10322 | -0.006291 | -0.090083 | 0.16199 | 0.16975 | 0.26557 | 0.11585 | -122.3089 | 122.0556 | 122.3219 | 122.2381 | 0.59099 | -122.3687
2823.6094 | 122.438 | -0.050354 | 122.2137 | -0.01778 | -0.046906 | 0.040507 | 0.021178 | -0.012506 | -0.0029443 | -0.013887 | -0.0022666 | -0.0020767 | 0.058687 | 0.043679 | 0.048756 | -0.017266 | 0.028878 | -0.017566 | 0.065863 | 0.078201 | 0.16486 | -0.076794 | 0.083464 | 0.50402 | -0.033458 | 121.9641 | 122.2212 | 122.1466 | -0.14583 | -0.02644 | -122.1479 | 0.033088 | 0.032788 | 0.059228 | -122.1355 | -122.0489 | -0.095479 | -0.2497 | 0.13382 | 0.016896 | 0.11237 | 0.007441 | -0.067194 | 0.11622 | 0.12856 | 0.21521 | 0.079232 | -122.2905 | 122.0144 | 122.2715 | 122.1969 | 0.55437 | -122.3596
2825.3594 | 122.374 | -0.059509 | 122.2183 | -0.010149 | -0.047333 | 0.040507 | 0.021392 | -0.012719 | -0.0029443 | -0.013887 | -0.0022666 | -0.0025041 | 0.058687 | 0.043893 | 0.048542 | -0.017266 | 0.015142 | -0.017566 | 0.07502 | 0.08278 | 0.17402 | -0.072215 | 0.083464 | 0.49028 | -0.033458 | 121.9641 | 122.2212 | 122.1466 | -0.14125 | -0.012706 | -122.1433 | 0.042243 | 0.041943 | 0.054649 | -122.1355 | -122.0443 | -0.081746 | -0.25427 | 0.14297 | 0.026051 | 0.1078 | 0.002863 | -0.071772 | 0.13453 | 0.14229 | 0.23353 | 0.074651 | -122.2905 | 122.0236 | 122.2807 | 122.2061 | 0.54979 | -122.3596
2827.0625 | 122.3145 | -0.09613 | 122.2412 | -0.010149 | -0.047119 | 0.040293 | 0.021606 | -0.012719 | -0.0031579 | -0.013887 | -0.0024804 | -0.0022903 | 0.058687 | 0.043465 | 0.048756 | -0.021844 | 0.0243 | -0.012988 | 0.065863 | 0.073622 | 0.16944 | -0.081373 | 0.088043 | 0.49486 | -0.0243 | 121.9595 | 122.2212 | 122.1466 | -0.14125 | 0.014757 | -122.1753 | 0.074286 | 0.083142 | 0.068385 | -122.1676 | -122.0718 | -0.045125 | -0.28174 | 0.18417 | 0.07183 | 0.11695 | -0.020025 | -0.09466 | 0.16199 | 0.16975 | 0.26557 | 0.12043 | -122.3226 | 122.0556 | 122.3173 | 122.2427 | 0.59099 | -122.3825
2828.8281 | 122.4335 | -0.036621 | 122.2321 | -0.01778 | -0.047119 | 0.040293 | 0.021606 | -0.012719 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.043679 | 0.048542 | -0.017266 | 0.019721 | -0.017566 | 0.065863 | 0.078201 | 0.17402 | -0.081373 | 0.088043 | 0.49486 | -0.028879 | 121.9595 | 122.2258 | 122.1374 | -0.14125 | -0.044752 | -122.1662 | 0.019355 | 0.019055 | 0.063807 | -122.1539 | -122.058 | -0.10463 | -0.27259 | 0.12466 | 0.007742 | 0.11238 | -0.006291 | -0.094662 | 0.10248 | 0.11482 | 0.21064 | 0.056342 | -122.3134 | 121.9961 | 122.2624 | 122.174 | 0.53148 | -122.3733
2830.5156 | 122.3969 | -0.068665 | 122.2229 | -0.01778 | -0.047333 | 0.040293 | 0.021606 | -0.012719 | -0.0027305 | -0.029148 | -0.0024804 | -0.0022903 | 0.058473 | 0.043679 | 0.048542 | -0.012688 | 0.028878 | -0.017566 | 0.061284 | 0.078201 | 0.16944 | -0.076794 | 0.088043 | 0.49486 | -0.033458 | 121.9595 | 122.2166 | 122.142 | -0.14125 | -0.008129 | -122.1616 | 0.055977 | 0.051099 | 0.059228 | -122.1447 | -122.0535 | -0.07259 | -0.26343 | 0.15671 | 0.035207 | 0.1078 | -0.006292 | -0.080927 | 0.12995 | 0.14687 | 0.2381 | 0.097543 | -122.2997 | 122.0281 | 122.2853 | 122.2106 | 0.56353 | -122.3642
2832.2812 | 122.4289 | -0.059509 | 122.2092 | -0.01778 | -0.046692 | 0.040721 | 0.021606 | -0.012292 | -0.0033715 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058473 | 0.043465 | 0.048542 | -0.017266 | 0.015142 | -0.012988 | 0.070441 | 0.08278 | 0.16028 | -0.076794 | 0.088043 | 0.49028 | -0.033458 | 121.9641 | 122.2212 | 122.142 | -0.14125 | -0.017285 | -122.1387 | 0.042243 | 0.046521 | 0.063806 | -122.1264 | -122.0489 | -0.081746 | -0.24512 | 0.14755 | 0.026051 | 0.1078 | 0.012019 | -0.067194 | 0.12995 | 0.14229 | 0.21979 | 0.074651 | -122.286 | 122.0236 | 122.2807 | 122.2015 | 0.54979 | -122.3504
2834.0469 | 122.4335 | -0.064087 | 122.2275 | -0.01778 | -0.047547 | 0.040507 | 0.021606 | -0.012506 | -0.0027305 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058687 | 0.043252 | 0.048542 | -0.012688 | 0.0243 | -0.012988 | 0.065863 | 0.069043 | 0.17402 | -0.072215 | 0.088043 | 0.49486 | -0.038036 | 121.9686 | 122.2212 | 122.142 | -0.15499 | -0.008128 | -122.1616 | 0.051399 | 0.051099 | 0.059227 | -122.1584 | -122.0535 | -0.090904 | -0.25885 | 0.15213 | 0.026051 | 0.11695 | -0.006292 | -0.085505 | 0.12995 | 0.13313 | 0.2381 | 0.088387 | -122.2997 | 122.0327 | 122.2853 | 122.2061 | 0.55895 | -122.3825
2835.7969 | 122.438 | -0.045776 | 122.2137 | -0.010149 | -0.047333 | 0.040507 | 0.021606 | -0.012933 | -0.0029443 | -0.021518 | -0.0022666 | -0.0020767 | 0.058473 | 0.043893 | 0.048542 | -0.012688 | 0.010564 | -0.017566 | 0.070441 | 0.078201 | 0.17402 | -0.081373 | 0.083464 | 0.49944 | -0.033458 | 121.9641 | 122.2212 | 122.142 | -0.14125 | -0.035597 | -122.1433 | 0.033088 | 0.02821 | 0.063807 | -122.1355 | -122.0397 | -0.095479 | -0.2497 | 0.12924 | 0.012318 | 0.1078 | 0.007441 | -0.071772 | 0.11622 | 0.12398 | 0.21979 | 0.05634 | -122.2951 | 122.0098 | 122.267 | 122.1877 | 0.54521 | -122.355
2837.5469 | 122.3145 | -0.082397 | 122.2504 | -0.01778 | -0.047119 | 0.040721 | 0.021606 | -0.012933 | -0.0029443 | -0.029148 | -0.0022666 | -0.0018631 | 0.058473 | 0.043252 | 0.048756 | -0.017266 | 0.015142 | -0.017566 | 0.065863 | 0.073622 | 0.16486 | -0.081373 | 0.088043 | 0.49486 | -0.042615 | 121.9641 | 122.2303 | 122.1511 | -0.14125 | 0.001024 | -122.1845 | 0.065131 | 0.064831 | 0.063807 | -122.1767 | -122.0855 | -0.058858 | -0.28632 | 0.17044 | 0.039782 | 0.09864 | -0.020022 | -0.099236 | 0.14826 | 0.15602 | 0.24726 | 0.097539 | -122.3317 | 122.0464 | 122.3127 | 122.2335 | 0.57726 | -122.3916
2839.25 | 122.319 | -0.086975 | 122.2458 | -0.0025182 | -0.047119 | 0.040507 | 0.021392 | -0.012719 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.043465 | 0.048542 | -0.021844 | 0.015142 | -0.017566 | 0.065863 | 0.078201 | 0.1786 | -0.076794 | 0.088043 | 0.49028 | -0.038036 | 121.9686 | 122.2166 | 122.1466 | -0.14125 | 0.010181 | -122.1799 | 0.065131 | 0.069409 | 0.059228 | -122.1676 | -122.0672 | -0.05428 | -0.27716 | 0.17502 | 0.048939 | 0.10322 | -0.029181 | -0.099238 | 0.15284 | 0.16518 | 0.26557 | 0.10212 | -122.3226 | 122.0556 | 122.3036 | 122.2335 | 0.57726 | -122.387
2841 | 122.3145 | -0.10529 | 122.2504 | -0.010149 | -0.047119 | 0.040293 | 0.021606 | -0.012506 | -0.0027305 | -0.029148 | -0.002694 | -0.0022903 | 0.058473 | 0.043679 | 0.048542 | -0.017266 | 0.015142 | -0.017566 | 0.07502 | 0.073622 | 0.16944 | -0.081373 | 0.088043 | 0.49486 | -0.038036 | 121.9686 | 122.2303 | 122.1466 | -0.14583 | 0.023913 | -122.1753 | 0.08802 | 0.08772 | 0.063807 | -122.1767 | -122.0809 | -0.040547 | -0.28174 | 0.19333 | 0.06725 | 0.1078 | -0.020022 | -0.10381 | 0.18031 | 0.17891 | 0.27472 | 0.12043 | -122.3317 | 122.0739 | 122.3356 | 122.2518 | 0.60015 | -122.3962
2842.75 | 122.3328 | -0.09613 | 122.2549 | -0.0025182 | -0.047333 | 0.040293 | 0.021606 | -0.012292 | -0.0031579 | -0.0062567 | -0.0022666 | -0.0020767 | 0.058473 | 0.043465 | 0.048542 | -0.017266 | 0.015142 | -0.012988 | 0.061284 | 0.078201 | 0.16944 | -0.076794 | 0.092622 | 0.49486 | -0.0243 | 121.9641 | 122.2303 | 122.142 | -0.14125 | 0.019336 | -122.1937 | 0.078864 | 0.083142 | 0.063806 | -122.1767 | -122.0855 | -0.045125 | -0.29089 | 0.18875 | 0.07183 | 0.11695 | -0.0246 | -0.11297 | 0.15741 | 0.17433 | 0.26557 | 0.11127 | -122.3317 | 122.0602 | 122.3265 | 122.2381 | 0.59099 | -122.3962
2844.5 | 122.4564 | -0.054932 | 122.1863 | -0.0025182 | -0.047547 | 0.040507 | 0.021392 | -0.012719 | -0.0025169 | -0.036779 | -0.002053 | -0.0022903 | 0.058901 | 0.043465 | 0.048328 | -0.017266 | 0.0243 | -0.012988 | 0.070441 | 0.078201 | 0.1786 | -0.076794 | 0.088043 | 0.49486 | -0.033458 | 121.9686 | 122.2303 | 122.1466 | -0.14125 | -0.021862 | -122.1158 | 0.037666 | 0.041944 | 0.063806 | -122.1081 | -122.0077 | -0.086323 | -0.21765 | 0.14297 | 0.021474 | 0.1078 | 0.044065 | -0.039728 | 0.12537 | 0.13313 | 0.23353 | 0.079232 | -122.2631 | 122.0236 | 122.2853 | 122.2015 | 0.54979 | -122.3275
2846.1875 | 122.319 | -0.11902 | 122.2321 | -0.010149 | -0.046906 | 0.040507 | 0.021392 | -0.012506 | -0.0027305 | -0.029148 | -0.002053 | -0.0022903 | 0.058473 | 0.043679 | 0.048756 | -0.017266 | 0.015142 | -0.017566 | 0.070441 | 0.08278 | 0.17402 | -0.076794 | 0.078886 | 0.49486 | -0.033458 | 121.9686 | 122.2303 | 122.1466 | -0.14125 | 0.042225 | -122.1616 | 0.10175 | 0.10145 | 0.059228 | -122.1493 | -122.058 | -0.022236 | -0.26343 | 0.1979 | 0.085561 | 0.1078 | -0.001712 | -0.085505 | 0.18946 | 0.2018 | 0.29303 | 0.13416 | -122.3089 | 122.0876 | 122.3494 | 122.2656 | 0.61388 | -122.3733
2847.9375 | 122.3099 | -0.091553 | 122.2687 | -0.010149 | -0.047333 | 0.040293 | 0.021606 | -0.012292 | -0.0029443 | -0.021518 | -0.002053 | -0.0025041 | 0.058473 | 0.043465 | 0.048542 | -0.017266 | 0.0243 | -0.017566 | 0.070441 | 0.073622 | 0.17402 | -0.081373 | 0.083464 | 0.49028 | -0.0243 | 121.9595 | 122.2166 | 122.1511 | -0.14583 | 0.01018 | -122.1982 | 0.074287 | 0.073987 | 0.063807 | -122.1951 | -122.0947 | -0.05428 | -0.30921 | 0.17502 | 0.067253 | 0.12153 | -0.052069 | -0.11755 | 0.16199 | 0.16518 | 0.26557 | 0.11585 | -122.35 | 122.051 | 122.3082 | 122.2427 | 0.58183 | -122.4145
2849.6875 | 122.2916 | -0.10986 | 122.2275 | -0.010149 | -0.047119 | 0.040293 | 0.021606 | -0.012292 | -0.0033715 | -0.0062567 | -0.0022666 | -0.0022903 | 0.05826 | 0.043679 | 0.048756 | -0.008109 | 0.0243 | -0.012988 | 0.065863 | 0.073622 | 0.16944 | -0.081373 | 0.088043 | 0.4857 | -0.028879 | 121.9686 | 122.2303 | 122.1466 | -0.13668 | 0.02849 | -122.1616 | 0.10175 | 0.096875 | 0.068385 | -122.1539 | -122.058 | -0.026813 | -0.25885 | 0.19791 | 0.080984 | 0.1078 | 0.002866 | -0.080927 | 0.17573 | 0.18349 | 0.2793 | 0.13416 | -122.3089 | 122.0785 | 122.3402 | 122.2564 | 0.59557 | -122.3642
2851.3906 | 122.4472 | -0.068665 | 122.1909 | -0.010149 | -0.047547 | 0.040721 | 0.021606 | -0.012506 | -0.0027305 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058473 | 0.043465 | 0.048542 | -0.017266 | 0.019721 | -0.022144 | 0.065863 | 0.078201 | 0.17402 | -0.076794 | 0.083464 | 0.50402 | -0.028879 | 121.9686 | 122.2258 | 122.1374 | -0.14125 | -0.008129 | -122.125 | 0.051399 | 0.046521 | 0.05465 | -122.1127 | -122.0168 | -0.07259 | -0.22223 | 0.15213 | 0.039786 | 0.11238 | 0.034908 | -0.053463 | 0.13453 | 0.14687 | 0.24268 | 0.088386 | -122.2677 | 122.0373 | 122.2944 | 122.2061 | 0.57268 | -122.3321
2853.1562 | 122.3511 | -0.10986 | 122.2458 | -0.0025182 | -0.047547 | 0.040507 | 0.021178 | -0.012719 | -0.0029443 | -0.021518 | -0.0024804 | -0.0027177 | 0.058473 | 0.043679 | 0.048756 | -0.021844 | 0.015142 | -0.012988 | 0.065863 | 0.08278 | 0.16944 | -0.072215 | 0.092622 | 0.49028 | -0.033458 | 121.9641 | 122.2258 | 122.1466 | -0.14125 | 0.037648 | -122.1799 | 0.088019 | 0.096875 | 0.059227 | -122.163 | -122.0764 | -0.031392 | -0.28174 | 0.20248 | 0.076405 | 0.1078 | -0.020024 | -0.099238 | 0.17573 | 0.19264 | 0.2793 | 0.12501 | -122.318 | 122.0739 | 122.3356 | 122.2564 | 0.60014 | -122.387
2854.8594 | 122.3511 | -0.082397 | 122.2366 | -0.010149 | -0.047119 | 0.040507 | 0.021392 | -0.012506 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.043679 | 0.048969 | -0.012688 | 0.019721 | -0.017566 | 0.070441 | 0.08278 | 0.16944 | -0.076794 | 0.092622 | 0.49486 | -0.033458 | 121.9686 | 122.2258 | 122.1466 | -0.13668 | 0.005603 | -122.1662 | 0.069709 | 0.064831 | 0.059228 | -122.1539 | -122.0672 | -0.054279 | -0.26801 | 0.17502 | 0.048939 | 0.10322 | -0.010868 | -0.090082 | 0.15284 | 0.16518 | 0.25184 | 0.10212 | -122.3134 | 122.051 | 122.3082 | 122.2289 | 0.57726 | -122.3733
2856.625 | 122.3053 | -0.10529 | 122.2549 | -0.01778 | -0.047333 | 0.040507 | 0.021606 | -0.012506 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.058687 | 0.043893 | 0.048542 | -0.012688 | 0.019721 | -0.017566 | 0.065863 | 0.087359 | 0.17402 | -0.076794 | 0.088043 | 0.49486 | -0.033458 | 121.9732 | 122.2212 | 122.1511 | -0.14125 | 0.028492 | -122.1891 | 0.092598 | 0.08772 | 0.059228 | -122.1676 | -122.0809 | -0.035969 | -0.28174 | 0.19333 | 0.071828 | 0.1078 | -0.033758 | -0.10381 | 0.17115 | 0.19265 | 0.2793 | 0.12501 | -122.3317 | 122.0785 | 122.3265 | 122.2564 | 0.60015 | -122.3962
2858.375 | 122.3236 | -0.11444 | 122.2595 | -0.010149 | -0.047333 | 0.040293 | 0.021392 | -0.012506 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058473 | 0.043679 | 0.048542 | -0.012688 | 0.019721 | -0.017566 | 0.070441 | 0.078201 | 0.17402 | -0.072215 | 0.083464 | 0.49944 | -0.028879 | 121.9732 | 122.2258 | 122.1511 | -0.14125 | 0.042226 | -122.1891 | 0.10175 | 0.096875 | 0.054649 | -122.1813 | -122.0855 | -0.026814 | -0.28631 | 0.1979 | 0.085562 | 0.11238 | -0.033756 | -0.10839 | 0.18488 | 0.19264 | 0.28846 | 0.13416 | -122.3317 | 122.0876 | 122.3402 | 122.2656 | 0.61388 | -122.4008
2860.0625 | 122.3511 | -0.091553 | 122.2412 | -0.01778 | -0.047333 | 0.040507 | 0.021606 | -0.012292 | -0.0025169 | -0.029148 | -0.0024804 | -0.0022903 | 0.058687 | 0.043679 | 0.048542 | -0.021844 | 0.015142 | -0.008409 | 0.065863 | 0.078201 | 0.16944 | -0.076794 | 0.083464 | 0.49944 | -0.033458 | 121.9778 | 122.2303 | 122.1466 | -0.14125 | 0.014759 | -122.1753 | 0.069709 | 0.083144 | 0.068385 | -122.163 | -122.0718 | -0.049702 | -0.26343 | 0.17502 | 0.058095 | 0.1078 | -0.010867 | -0.09466 | 0.15742 | 0.16975 | 0.26099 | 0.10669 | -122.318 | 122.0693 | 122.3219 | 122.2381 | 0.59099 | -122.3825
2861.7656 | 122.4289 | -0.059509 | 122.2229 | -0.010149 | -0.047333 | 0.040507 | 0.021178 | -0.012292 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.044106 | 0.048328 | -0.026423 | 0.0243 | -0.012988 | 0.065863 | 0.073622 | 0.16486 | -0.076794 | 0.097201 | 0.50402 | -0.033458 | 121.9686 | 122.2258 | 122.1466 | -0.14125 | -0.017285 | -122.157 | 0.033086 | 0.046521 | 0.063806 | -122.1493 | -122.058 | -0.081746 | -0.25427 | 0.15671 | 0.026051 | 0.1078 | 0.002865 | -0.076349 | 0.12537 | 0.13313 | 0.22437 | 0.083809 | -122.2997 | 122.0281 | 122.2853 | 122.2061 | 0.56353 | -122.3642
2863.5312 | 122.4426 | -0.045776 | 122.2092 | 0.0051128 | -0.04776 | 0.040293 | 0.021606 | -0.012719 | -0.0029443 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.043893 | 0.048542 | -0.021844 | 0.019721 | -0.017566 | 0.070441 | 0.087359 | 0.16944 | -0.072215 | 0.092622 | 0.49486 | -0.033458 | 121.9732 | 122.2303 | 122.1511 | -0.13668 | -0.026439 | -122.1387 | 0.023932 | 0.02821 | 0.054649 | -122.1218 | -122.0397 | -0.0909 | -0.23596 | 0.1384 | 0.012318 | 0.10322 | 0.021177 | -0.058037 | 0.11622 | 0.13314 | 0.21521 | 0.065497 | -122.2814 | 122.019 | 122.2761 | 122.1969 | 0.54064 | -122.3458
2865.2969 | 122.438 | -0.054932 | 122.2 | -0.0025182 | -0.047547 | 0.040507 | 0.021606 | -0.012506 | -0.0029443 | -0.029148 | -0.002694 | -0.0020767 | 0.058473 | 0.043893 | 0.048328 | -0.021844 | 0.0243 | -0.017566 | 0.070441 | 0.078201 | 0.16944 | -0.072215 | 0.074307 | 0.49944 | -0.038036 | 121.9641 | 122.2303 | 122.1511 | -0.14583 | -0.017283 | -122.1296 | 0.033088 | 0.037366 | 0.054649 | -122.1218 | -122.0306 | -0.090901 | -0.23596 | 0.12924 | 0.016896 | 0.1078 | 0.030332 | -0.048882 | 0.12537 | 0.13313 | 0.22437 | 0.079232 | -122.2722 | 122.019 | 122.2853 | 122.2061 | 0.55437 | -122.3458
2867 | 122.3419 | -0.091553 | 122.2458 | 0.012744 | -0.047547 | 0.040507 | 0.021392 | -0.012719 | -0.0025169 | -0.029148 | -0.0024804 | -0.0025041 | 0.058687 | 0.043893 | 0.048542 | -0.017266 | 0.0243 | -0.017566 | 0.065863 | 0.078201 | 0.17402 | -0.072215 | 0.083464 | 0.49944 | -0.028879 | 121.9732 | 122.2303 | 122.1557 | -0.14583 | 0.019338 | -122.1799 | 0.074287 | 0.073987 | 0.054649 | -122.1676 | -122.0718 | -0.05428 | -0.27258 | 0.17502 | 0.062674 | 0.11695 | -0.015445 | -0.09008 | 0.15742 | 0.16975 | 0.26557 | 0.11585 | -122.318 | 122.0648 | 122.3219 | 122.2473 | 0.59099 | -122.3916
2868.75 | 122.4197 | -0.064087 | 122.2183 | -0.010149 | -0.047547 | 0.040293 | 0.021392 | -0.012292 | -0.0029443 | -0.029148 | -0.002053 | -0.0025041 | 0.058473 | 0.043679 | 0.048542 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.08278 | 0.17402 | -0.076794 | 0.078886 | 0.49486 | -0.033458 | 121.9686 | 122.2349 | 122.1374 | -0.14125 | -0.012707 | -122.1433 | 0.046821 | 0.051099 | 0.063806 | -122.1355 | -122.0443 | -0.077168 | -0.2497 | 0.14297 | 0.030629 | 0.1078 | 0.016599 | -0.080929 | 0.13911 | 0.14687 | 0.2381 | 0.083808 | -122.2951 | 122.0327 | 122.299 | 122.2015 | 0.55895 | -122.3596
2870.4531 | 122.3236 | -0.10529 | 122.2275 | 0.0051128 | -0.047547 | 0.040507 | 0.021392 | -0.012719 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.058473 | 0.044106 | 0.048328 | -0.012688 | 0.015142 | -0.017566 | 0.065863 | 0.08278 | 0.1786 | -0.076794 | 0.088043 | 0.49486 | -0.033458 | 121.9732 | 122.2212 | 122.1511 | -0.14125 | 0.028492 | -122.1616 | 0.092598 | 0.08772 | 0.059228 | -122.1447 | -122.0489 | -0.035969 | -0.25427 | 0.19333 | 0.071828 | 0.1078 | -0.006292 | -0.076348 | 0.17115 | 0.18807 | 0.28388 | 0.12043 | -122.3043 | 122.0785 | 122.3265 | 122.2564 | 0.60015 | -122.3687
2872.2188 | 122.3694 | -0.086975 | 122.2549 | -0.0025182 | -0.04776 | 0.040507 | 0.020965 | -0.012506 | -0.0031579 | -0.0062567 | -0.002694 | -0.0022903 | 0.058473 | 0.043465 | 0.048542 | -0.012688 | 0.0243 | -0.017566 | 0.061284 | 0.073622 | 0.16944 | -0.076794 | 0.078886 | 0.50402 | -0.038036 | 121.9686 | 122.2395 | 122.1511 | -0.14583 | 0.010181 | -122.1937 | 0.074287 | 0.069409 | 0.059228 | -122.1813 | -122.0855 | -0.058858 | -0.28632 | 0.16586 | 0.048939 | 0.1078 | -0.015443 | -0.10381 | 0.14826 | 0.1606 | 0.25641 | 0.11127 | -122.3317 | 122.0556 | 122.3265 | 122.2381 | 0.59099 | -122.4008
2873.9219 | 122.319 | -0.11444 | 122.2412 | -0.01778 | -0.047547 | 0.040721 | 0.021606 | -0.012506 | -0.0027305 | -0.013887 | -0.0024804 | -0.0022903 | 0.058473 | 0.043679 | 0.048542 | -0.017266 | 0.015142 | -0.008409 | 0.061284 | 0.073622 | 0.1786 | -0.072215 | 0.088043 | 0.49486 | -0.033458 | 121.9641 | 122.2303 | 122.1511 | -0.15041 | 0.042226 | -122.1799 | 0.097175 | 0.10603 | 0.063806 | -122.1676 | -122.0626 | -0.035971 | -0.27716 | 0.20248 | 0.080983 | 0.11695 | -0.010867 | -0.090081 | 0.17572 | 0.18806 | 0.29304 | 0.12958 | -122.3134 | 122.0785 | 122.3448 | 122.2656 | 0.6093 | -122.3916
2875.6719 | 122.3511 | -0.073242 | 122.2275 | -0.010149 | -0.04776 | 0.040507 | 0.021178 | -0.012719 | -0.0025169 | -0.013887 | -0.0024804 | -0.0020767 | 0.05826 | 0.043893 | 0.048328 | -0.021844 | 0.010564 | -0.017566 | 0.070441 | 0.078201 | 0.17402 | -0.076794 | 0.083464 | 0.50402 | -0.028879 | 121.9732 | 122.2303 | 122.1511 | -0.14125 | -0.003552 | -122.157 | 0.051398 | 0.055676 | 0.059228 | -122.1493 | -122.0535 | -0.068013 | -0.25427 | 0.15671 | 0.044363 | 0.11238 | 0.002866 | -0.076348 | 0.14368 | 0.15144 | 0.24726 | 0.083806 | -122.3043 | 122.0464 | 122.3036 | 122.2244 | 0.57726 | -122.3687
2877.3594 | 122.3557 | -0.091553 | 122.2092 | -0.010149 | -0.047547 | 0.040507 | 0.021178 | -0.012506 | -0.0029443 | -0.021518 | -0.0024804 | -0.0020767 | 0.05826 | 0.043679 | 0.048542 | -0.017266 | 0.019721 | -0.022144 | 0.070441 | 0.078201 | 0.17402 | -0.076794 | 0.088043 | 0.49944 | -0.038036 | 121.9732 | 122.2395 | 122.1466 | -0.14583 | 0.014759 | -122.1387 | 0.074287 | 0.069409 | 0.05465 | -122.131 | -122.0352 | -0.05428 | -0.23596 | 0.1796 | 0.053517 | 0.1078 | 0.030334 | -0.062616 | 0.16199 | 0.16975 | 0.26557 | 0.11127 | -122.286 | 122.0648 | 122.3311 | 122.2381 | 0.59099 | -122.355
2879.1094 | 122.3877 | -0.073242 | 122.1909 | -0.01778 | -0.04776 | 0.040293 | 0.021178 | -0.012506 | -0.0027305 | -0.029148 | -0.0024804 | -0.0020767 | 0.058473 | 0.043679 | 0.048542 | -0.012688 | 0.015142 | -0.008409 | 0.065863 | 0.087359 | 0.16944 | -0.072215 | 0.078886 | 0.50402 | -0.028879 | 121.9732 | 122.2349 | 122.1466 | -0.14125 | 0.001027 | -122.125 | 0.060554 | 0.064833 | 0.063806 | -122.1035 | -122.0214 | -0.068013 | -0.21765 | 0.15213 | 0.044363 | 0.11238 | 0.044065 | -0.044306 | 0.13911 | 0.1606 | 0.24268 | 0.088384 | -122.2631 | 122.0464 | 122.3082 | 122.2198 | 0.57726 | -122.3321
2880.875 | 122.3877 | -0.068665 | 122.2046 | -0.01778 | -0.04776 | 0.040293 | 0.021178 | -0.012506 | -0.0025169 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.043465 | 0.048542 | -0.012688 | 0.005985 | -0.017566 | 0.070441 | 0.08278 | 0.17402 | -0.072215 | 0.078886 | 0.50402 | -0.033458 | 121.9686 | 122.2349 | 122.1557 | -0.13668 | -0.00355 | -122.1341 | 0.055977 | 0.051099 | 0.054649 | -122.1218 | -122.0306 | -0.068011 | -0.23596 | 0.14755 | 0.035207 | 0.10322 | 0.030332 | -0.048881 | 0.13911 | 0.15144 | 0.24268 | 0.07465 | -122.2768 | 122.0373 | 122.3036 | 122.2244 | 0.57268 | -122.3413
2882.5781 | 122.3145 | -0.09613 | 122.2504 | -0.010149 | -0.04776 | 0.04008 | 0.021178 | -0.012292 | -0.0025169 | -0.036779 | -0.0022666 | -0.0025041 | 0.058473 | 0.04432 | 0.048756 | -0.017266 | 0.015142 | -0.012988 | 0.070441 | 0.08278 | 0.17402 | -0.072215 | 0.078886 | 0.49486 | -0.033458 | 121.9641 | 122.2303 | 122.1603 | -0.14125 | 0.023915 | -122.1799 | 0.078864 | 0.083142 | 0.059227 | -122.1676 | -122.0764 | -0.045125 | -0.28632 | 0.17502 | 0.062672 | 0.1078 | -0.020022 | -0.090079 | 0.16657 | 0.17891 | 0.27015 | 0.11127 | -122.3226 | 122.0602 | 122.3265 | 122.2564 | 0.59099 | -122.3916
2884.3281 | 122.3831 | -0.07782 | 122.2 | -0.01778 | -0.04776 | 0.040507 | 0.021392 | -0.012719 | -0.0029443 | -0.013887 | -0.0024804 | -0.0025041 | 0.058046 | 0.043893 | 0.048756 | -0.021844 | 0.015142 | -0.012988 | 0.065863 | 0.087359 | 0.1786 | -0.072215 | 0.083464 | 0.49486 | -0.033458 | 121.9686 | 122.2258 | 122.142 | -0.14583 | 0.005605 | -122.1341 | 0.055976 | 0.064832 | 0.059227 | -122.1127 | -122.0214 | -0.068013 | -0.23138 | 0.16128 | 0.044362 | 0.11237 | 0.025753 | -0.058039 | 0.14368 | 0.16518 | 0.25642 | 0.092962 | -122.2722 | 122.0464 | 122.3036 | 122.2198 | 0.57268 | -122.3458
2886.0781 | 122.4243 | -0.045776 | 122.2275 | -0.010149 | -0.04776 | 0.040293 | 0.021178 | -0.012506 | -0.0029443 | -0.013887 | -0.0022666 | -0.0020767 | 0.05826 | 0.043893 | 0.048542 | -0.017266 | 0.019721 | -0.017566 | 0.070441 | 0.078201 | 0.1786 | -0.076794 | 0.088043 | 0.49944 | -0.033458 | 121.9686 | 122.2303 | 122.1466 | -0.13668 | -0.031018 | -122.157 | 0.02851 | 0.02821 | 0.059228 | -122.1493 | -122.0489 | -0.0909 | -0.25885 | 0.13382 | 0.012318 | 0.10322 | 0.002866 | -0.080927 | 0.11622 | 0.12398 | 0.22437 | 0.065497 | -122.3043 | 122.0144 | 122.2761 | 122.1923 | 0.54521 | -122.3642
2887.8438 | 122.3373 | -0.082397 | 122.2595 | -0.0025182 | -0.04776 | 0.040721 | 0.021178 | -0.012292 | -0.0029443 | -0.013887 | -0.0024804 | -0.0025041 | 0.058473 | 0.043893 | 0.048542 | -0.021844 | 0.010564 | -0.012988 | 0.070441 | 0.08278 | 0.16944 | -0.076794 | 0.088043 | 0.49944 | -0.042615 | 121.9686 | 122.2303 | 122.1603 | -0.14125 | 0.005603 | -122.1891 | 0.060553 | 0.069409 | 0.063806 | -122.1767 | -122.0901 | -0.058858 | -0.29089 | 0.17044 | 0.039782 | 0.09864 | -0.029177 | -0.099234 | 0.15284 | 0.16518 | 0.25184 | 0.092961 | -122.3363 | 122.051 | 122.3127 | 122.2427 | 0.58183 | -122.4008
2889.5312 | 122.3282 | -0.10986 | 122.2412 | -0.010149 | -0.047547 | 0.040293 | 0.021178 | -0.012506 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.044106 | 0.048328 | -0.017266 | 0.010564 | -0.017566 | 0.07502 | 0.08278 | 0.17402 | -0.081373 | 0.083464 | 0.5086 | -0.033458 | 121.9732 | 122.2258 | 122.142 | -0.14125 | 0.02849 | -122.1662 | 0.092597 | 0.092297 | 0.063807 | -122.1584 | -122.0672 | -0.031392 | -0.268 | 0.19333 | 0.076405 | 0.1078 | -0.015446 | -0.099238 | 0.18488 | 0.19264 | 0.28388 | 0.12043 | -122.3226 | 122.0831 | 122.3356 | 122.2518 | 0.61846 | -122.3825
2891.2812 | 122.4518 | -0.059509 | 122.2092 | -0.010149 | -0.047547 | 0.040507 | 0.021178 | -0.012506 | -0.0029443 | -0.029148 | -0.0022666 | -0.0022903 | 0.05826 | 0.043679 | 0.048328 | -0.021844 | 0.019721 | -0.012988 | 0.065863 | 0.078201 | 0.1786 | -0.076794 | 0.083464 | 0.50402 | -0.033458 | 121.9732 | 122.2349 | 122.1511 | -0.14125 | -0.017285 | -122.1433 | 0.037665 | 0.046521 | 0.063806 | -122.131 | -122.0306 | -0.081746 | -0.23596 | 0.14297 | 0.026051 | 0.1078 | 0.025755 | -0.058037 | 0.12537 | 0.13771 | 0.2381 | 0.07923 | -122.286 | 122.0327 | 122.2944 | 122.2106 | 0.56353 | -122.3504
2893.0469 | 122.438 | -0.068665 | 122.2137 | -0.01778 | -0.04776 | 0.040293 | 0.021392 | -0.012292 | -0.0027305 | -0.021518 | -0.0024804 | -0.0022903 | 0.058473 | 0.043893 | 0.048328 | -0.012688 | 0.0243 | -0.017566 | 0.070441 | 0.078201 | 0.16944 | -0.072215 | 0.083464 | 0.49944 | -0.042615 | 121.9686 | 122.2349 | 122.1511 | -0.13668 | -0.00355 | -122.1433 | 0.055977 | 0.051099 | 0.054649 | -122.1355 | -122.0443 | -0.068011 | -0.24512 | 0.15213 | 0.02605 | 0.094061 | 0.021177 | -0.062615 | 0.13911 | 0.14687 | 0.2381 | 0.092965 | -122.286 | 122.0373 | 122.3036 | 122.2198 | 0.5681 | -122.3504
2894.7344 | 122.3557 | -0.082397 | 122.2275 | -0.0025182 | -0.047547 | 0.040507 | 0.021392 | -0.012506 | -0.0027305 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058473 | 0.043893 | 0.048328 | -0.012688 | 0.019721 | -0.008409 | 0.065863 | 0.078201 | 0.17402 | -0.072215 | 0.074307 | 0.50402 | -0.042615 | 121.9732 | 122.2349 | 122.1511 | -0.14583 | 0.010182 | -122.1616 | 0.069709 | 0.073988 | 0.063806 | -122.1493 | -122.0535 | -0.063436 | -0.25427 | 0.1567 | 0.039782 | 0.10322 | 0.007444 | -0.076348 | 0.14826 | 0.1606 | 0.25641 | 0.10212 | -122.2997 | 122.0556 | 122.3173 | 122.2335 | 0.58641 | -122.3733
2896.4844 | 122.3282 | -0.10071 | 122.2549 | -0.01778 | -0.047547 | 0.040721 | 0.021178 | -0.012506 | -0.0027305 | -0.021518 | -0.002694 | -0.0025041 | 0.058687 | 0.043893 | 0.048542 | -0.017266 | 0.015142 | -0.012988 | 0.070441 | 0.08278 | 0.17402 | -0.076794 | 0.083464 | 0.50402 | -0.0243 | 121.9686 | 122.2303 | 122.1603 | -0.14125 | 0.023914 | -122.1845 | 0.083442 | 0.08772 | 0.063806 | -122.1722 | -122.0809 | -0.040547 | -0.28632 | 0.18417 | 0.076408 | 0.11695 | -0.0246 | -0.094657 | 0.17115 | 0.18349 | 0.27472 | 0.11585 | -122.3317 | 122.0693 | 122.3311 | 122.261 | 0.60473 | -122.3962
2898.2344 | 122.4289 | -0.032043 | 122.1725 | -0.0025182 | -0.04776 | 0.040507 | 0.021178 | -0.012292 | -0.0029443 | -0.021518 | -0.0022666 | -0.0025041 | 0.05826 | 0.043893 | 0.048328 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.08278 | 0.1786 | -0.076794 | 0.083464 | 0.5086 | -0.028879 | 121.9686 | 122.2303 | 122.1466 | -0.14125 | -0.044751 | -122.0975 | 0.014777 | 0.019055 | 0.063806 | -122.0898 | -121.994 | -0.10921 | -0.20392 | 0.11551 | 0.003164 | 0.11238 | 0.057798 | -0.025995 | 0.10706 | 0.11482 | 0.21064 | 0.047185 | -122.2493 | 122.0007 | 122.2624 | 122.1786 | 0.54064 | -122.3138
2899.9219 | 122.3557 | -0.086975 | 122.2504 | -0.0025182 | -0.047974 | 0.040507 | 0.021178 | -0.012292 | -0.0029443 | -0.013887 | -0.0024804 | -0.0020767 | 0.058046 | 0.04432 | 0.048115 | -0.021844 | 0.028878 | -0.017566 | 0.07502 | 0.078201 | 0.18317 | -0.076794 | 0.088043 | 0.49486 | -0.028879 | 121.9732 | 122.2395 | 122.1511 | -0.13668 | 0.010181 | -122.1753 | 0.065131 | 0.069409 | 0.059228 | -122.1722 | -122.0672 | -0.049701 | -0.27716 | 0.17502 | 0.058096 | 0.1078 | -0.010865 | -0.099236 | 0.162 | 0.16518 | 0.27015 | 0.11585 | -122.3272 | 122.0602 | 122.3265 | 122.2381 | 0.58183 | -122.387
2901.6719 | 122.3648 | -0.082397 | 122.2458 | -0.010149 | -0.04776 | 0.040507 | 0.021178 | -0.012506 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.043893 | 0.048542 | -0.017266 | 0.0243 | -0.012988 | 0.070441 | 0.078201 | 0.16944 | -0.081373 | 0.078886 | 0.50402 | -0.028879 | 121.9732 | 122.2349 | 122.1557 | -0.14125 | 0.001024 | -122.1753 | 0.065131 | 0.069409 | 0.068385 | -122.1676 | -122.0764 | -0.058858 | -0.27258 | 0.16128 | 0.053518 | 0.11238 | -0.010867 | -0.09008 | 0.15284 | 0.1606 | 0.25184 | 0.1067 | -122.3272 | 122.0556 | 122.3173 | 122.2381 | 0.58641 | -122.387
2903.375 | 122.3877 | -0.059509 | 122.2458 | -0.010149 | -0.047547 | 0.040934 | 0.021606 | -0.012933 | -0.0027305 | -0.021518 | -0.0024804 | -0.0025041 | 0.05826 | 0.043893 | 0.048542 | -0.017266 | 0.015142 | -0.008409 | 0.070441 | 0.078201 | 0.1786 | -0.081373 | 0.083464 | 0.51317 | -0.028879 | 121.9732 | 122.2349 | 122.1557 | -0.13668 | -0.021864 | -122.1753 | 0.042243 | 0.0511 | 0.072964 | -122.1676 | -122.0672 | -0.077167 | -0.27258 | 0.14297 | 0.03063 | 0.1078 | -0.010867 | -0.09008 | 0.12995 | 0.13771 | 0.2381 | 0.074651 | -122.3272 | 122.0327 | 122.2944 | 122.2152 | 0.57268 | -122.3825
2905.1406 | 122.319 | -0.091553 | 122.2321 | -0.010149 | -0.047547 | 0.040293 | 0.021178 | -0.012719 | -0.0029443 | -0.029148 | -0.002694 | -0.0025041 | 0.05826 | 0.043893 | 0.048328 | -0.017266 | 0.015142 | -0.017566 | 0.07502 | 0.08278 | 0.17402 | -0.076794 | 0.078886 | 0.5086 | -0.028879 | 121.9732 | 122.2395 | 122.1511 | -0.14125 | 0.014759 | -122.157 | 0.074287 | 0.073987 | 0.059228 | -122.1493 | -122.058 | -0.049702 | -0.25885 | 0.17044 | 0.062674 | 0.11238 | 0.007445 | -0.080926 | 0.16657 | 0.17433 | 0.26557 | 0.10669 | -122.3089 | 122.0648 | 122.3311 | 122.2427 | 0.60015 | -122.3733
2906.9062 | 122.3145 | -0.10986 | 122.2641 | -0.0025182 | -0.04776 | 0.040293 | 0.020965 | -0.012506 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.044106 | 0.048328 | -0.012688 | 0.015142 | -0.017566 | 0.070441 | 0.078201 | 0.17402 | -0.076794 | 0.083464 | 0.5086 | -0.033458 | 121.9686 | 122.2349 | 122.1466 | -0.13668 | 0.033069 | -122.1937 | 0.097175 | 0.092297 | 0.059228 | -122.1859 | -122.0901 | -0.026813 | -0.29547 | 0.19333 | 0.076405 | 0.10322 | -0.029177 | -0.11755 | 0.1803 | 0.18806 | 0.28388 | 0.12501 | -122.3409 | 122.0785 | 122.3448 | 122.2564 | 0.61846 | -122.4008
2908.6094 | 122.2961 | -0.10529 | 122.2641 | 0.0051128 | -0.047547 | 0.040721 | 0.020965 | -0.012506 | -0.0031579 | -0.013887 | -0.002053 | -0.0018631 | 0.058473 | 0.043893 | 0.048542 | -0.012688 | 0.019721 | -0.012988 | 0.061284 | 0.087359 | 0.17402 | -0.076794 | 0.083464 | 0.49944 | -0.0243 | 121.9641 | 122.2395 | 122.1557 | -0.14125 | 0.028492 | -122.2028 | 0.092598 | 0.092298 | 0.063806 | -122.1767 | -122.0901 | -0.035969 | -0.30005 | 0.18875 | 0.080986 | 0.11695 | -0.024598 | -0.10839 | 0.16657 | 0.19265 | 0.2793 | 0.12501 | -122.3409 | 122.0693 | 122.3448 | 122.261 | 0.60472 | -122.4054
2910.3594 | 122.3007 | -0.11444 | 122.2504 | -0.010149 | -0.047547 | 0.040721 | 0.021178 | -0.012506 | -0.0027305 | -0.029148 | -0.0024804 | -0.0025041 | 0.058687 | 0.044106 | 0.048328 | -0.012688 | 0.019721 | -0.017566 | 0.07502 | 0.073622 | 0.17402 | -0.076794 | 0.083464 | 0.5086 | -0.028879 | 121.9778 | 122.2395 | 122.1511 | -0.13668 | 0.037647 | -122.1753 | 0.10175 | 0.096875 | 0.059228 | -122.1767 | -122.0764 | -0.022235 | -0.27258 | 0.1979 | 0.085562 | 0.1078 | -0.010865 | -0.099236 | 0.18946 | 0.18806 | 0.28846 | 0.13416 | -122.3272 | 122.0922 | 122.3539 | 122.2656 | 0.62304 | -122.387
2912.125 | 122.3419 | -0.09613 | 122.2733 | -0.01778 | -0.047974 | 0.04008 | 0.020965 | -0.012506 | -0.0027305 | -0.021518 | -0.0022666 | -0.0020767 | 0.058473 | 0.043893 | 0.048756 | -0.008109 | 0.015142 | -0.012988 | 0.070441 | 0.08278 | 0.16944 | -0.076794 | 0.088043 | 0.5086 | -0.0243 | 121.9732 | 122.2395 | 122.1511 | -0.15041 | 0.019336 | -122.2028 | 0.088021 | 0.083142 | 0.063806 | -122.1905 | -122.1038 | -0.054282 | -0.30005 | 0.18417 | 0.07183 | 0.12611 | -0.033753 | -0.12212 | 0.16657 | 0.17891 | 0.26557 | 0.11127 | -122.35 | 122.0693 | 122.3356 | 122.2473 | 0.60473 | -122.4237
2913.8281 | 122.3511 | -0.10071 | 122.2641 | -0.0025182 | -0.047547 | 0.040293 | 0.020965 | -0.012719 | -0.0027305 | -0.029148 | -0.0022666 | -0.0022903 | 0.058473 | 0.044106 | 0.048542 | -0.017266 | 0.019721 | -0.003831 | 0.065863 | 0.08278 | 0.17402 | -0.081373 | 0.083464 | 0.50402 | -0.042615 | 121.9824 | 122.2395 | 122.1511 | -0.14125 | 0.019335 | -122.1982 | 0.083442 | 0.096877 | 0.077542 | -122.1813 | -122.0901 | -0.040547 | -0.28173 | 0.18417 | 0.058093 | 0.09864 | -0.024598 | -0.11297 | 0.16657 | 0.18349 | 0.27472 | 0.12043 | -122.3455 | 122.0831 | 122.3402 | 122.2518 | 0.60473 | -122.4054
2915.5781 | 122.4701 | -0.068665 | 122.2229 | -0.0025182 | -0.04776 | 0.040507 | 0.021178 | -0.012719 | -0.0027305 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.044106 | 0.048542 | -0.021844 | 0.015142 | -0.017566 | 0.070441 | 0.087359 | 0.1786 | -0.072215 | 0.088043 | 0.49486 | -0.038036 | 121.9732 | 122.2395 | 122.1557 | -0.14125 | -0.00355 | -122.1525 | 0.046821 | 0.051099 | 0.054649 | -122.1355 | -122.0443 | -0.07259 | -0.24969 | 0.15671 | 0.030629 | 0.10322 | 0.016601 | -0.067191 | 0.13911 | 0.15602 | 0.24726 | 0.083807 | -122.2951 | 122.0419 | 122.3082 | 122.2244 | 0.56353 | -122.3642
2917.3281 | 122.3923 | -0.064087 | 122.2366 | -0.010149 | -0.04776 | 0.040721 | 0.020965 | -0.012506 | -0.0025169 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.044106 | 0.048542 | -0.017266 | 0.019721 | -0.022144 | 0.070441 | 0.078201 | 0.17402 | -0.072215 | 0.083464 | 0.51317 | -0.033458 | 121.9778 | 122.2441 | 122.1466 | -0.14583 | -0.008128 | -122.1662 | 0.046821 | 0.041943 | 0.050071 | -122.1584 | -122.0626 | -0.081746 | -0.25885 | 0.14755 | 0.030629 | 0.11237 | 0.007446 | -0.090082 | 0.13453 | 0.14229 | 0.2381 | 0.083808 | -122.3088 | 122.0419 | 122.3082 | 122.2106 | 0.57726 | -122.3825
2919.0938 | 122.4014 | -0.07782 | 122.2321 | -0.010149 | -0.047974 | 0.040934 | 0.021178 | -0.012719 | -0.0029443 | -0.021518 | -0.002053 | -0.0022903 | 0.058473 | 0.043679 | 0.048542 | -0.012688 | 0.019721 | -0.017566 | 0.070441 | 0.08278 | 0.17402 | -0.076794 | 0.092622 | 0.50402 | -0.033458 | 121.9778 | 122.2441 | 122.1511 | -0.14125 | 0.001026 | -122.1616 | 0.065132 | 0.060254 | 0.059228 | -122.1493 | -122.058 | -0.063435 | -0.25427 | 0.17044 | 0.044362 | 0.1078 | 0.012023 | -0.080926 | 0.14826 | 0.1606 | 0.25184 | 0.097541 | -122.3089 | 122.0556 | 122.3219 | 122.2289 | 0.58184 | -122.3733
2920.7969 | 122.3648 | -0.09613 | 122.2137 | -0.0025182 | -0.04776 | 0.040293 | 0.020965 | -0.012719 | -0.0027305 | -0.013887 | -0.0024804 | -0.0027177 | 0.058687 | 0.04432 | 0.048542 | -0.021844 | 0.010564 | -0.012988 | 0.079598 | 0.078201 | 0.1786 | -0.072215 | 0.078886 | 0.5086 | -0.033458 | 121.9732 | 122.2395 | 122.1557 | -0.13668 | 0.023915 | -122.1341 | 0.074286 | 0.083142 | 0.059227 | -122.1355 | -122.0352 | -0.040546 | -0.24054 | 0.17502 | 0.062672 | 0.10322 | 0.025756 | -0.058036 | 0.17573 | 0.17433 | 0.27472 | 0.10669 | -122.286 | 122.0693 | 122.3356 | 122.2518 | 0.60473 | -122.3504
2922.5625 | 122.319 | -0.073242 | 122.2824 | -0.010149 | -0.04776 | 0.040507 | 0.021178 | -0.012506 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058473 | 0.043679 | 0.048328 | -0.021844 | 0.0243 | -0.012988 | 0.070441 | 0.08278 | 0.1786 | -0.081373 | 0.088043 | 0.51317 | -0.028879 | 121.9686 | 122.2349 | 122.1557 | -0.14125 | -0.008131 | -122.212 | 0.051398 | 0.060254 | 0.068385 | -122.1996 | -122.1038 | -0.068013 | -0.31378 | 0.16129 | 0.044363 | 0.11238 | -0.047488 | -0.1267 | 0.14368 | 0.15602 | 0.25184 | 0.097542 | -122.3638 | 122.0419 | 122.3082 | 122.229 | 0.58642 | -122.4237
2924.2812 | 122.3557 | -0.082397 | 122.2275 | -0.010149 | -0.047974 | 0.040721 | 0.020965 | -0.012719 | -0.0031579 | -0.013887 | -0.0024804 | -0.0022903 | 0.058473 | 0.044534 | 0.048328 | -0.012688 | 0.0243 | -0.012988 | 0.065863 | 0.087359 | 0.1786 | -0.072215 | 0.092622 | 0.5086 | -0.033458 | 121.9778 | 122.2441 | 122.1511 | -0.14583 | 0.010182 | -122.1616 | 0.069709 | 0.069409 | 0.059227 | -122.1401 | -122.0489 | -0.063436 | -0.24969 | 0.17502 | 0.048939 | 0.11237 | 0.016601 | -0.076348 | 0.14826 | 0.16976 | 0.26099 | 0.1067 | -122.2997 | 122.0602 | 122.3265 | 122.2335 | 0.59099 | -122.3733
2926.0312 | 122.4289 | -0.045776 | 122.2092 | -0.010149 | -0.04776 | 0.040721 | 0.021178 | -0.012719 | -0.0027305 | -0.013887 | -0.002694 | -0.0018631 | 0.05826 | 0.043679 | 0.048328 | -0.021844 | 0.019721 | -0.017566 | 0.07502 | 0.073622 | 0.17402 | -0.081373 | 0.088043 | 0.50402 | -0.033458 | 121.9778 | 122.2395 | 122.1511 | -0.14125 | -0.035597 | -122.1341 | 0.023932 | 0.02821 | 0.063807 | -122.1355 | -122.0352 | -0.095479 | -0.23138 | 0.13382 | 0.012318 | 0.1078 | 0.030334 | -0.058037 | 0.1208 | 0.1194 | 0.21979 | 0.065497 | -122.2905 | 122.0236 | 122.2853 | 122.1969 | 0.54979 | -122.3504
2927.7812 | 122.3007 | -0.10071 | 122.2641 | -0.010149 | -0.04776 | 0.040293 | 0.020751 | -0.012292 | -0.0027305 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.043893 | 0.048115 | -0.017266 | 0.019721 | -0.012988 | 0.070441 | 0.087359 | 0.16944 | -0.081373 | 0.092622 | 0.5086 | -0.033458 | 121.9778 | 122.2349 | 122.1557 | -0.14583 | 0.019335 | -122.1937 | 0.083442 | 0.08772 | 0.068385 | -122.1767 | -122.0947 | -0.045125 | -0.28631 | 0.19333 | 0.06725 | 0.11237 | -0.029177 | -0.10839 | 0.17115 | 0.18807 | 0.27015 | 0.12043 | -122.3455 | 122.0785 | 122.3356 | 122.2564 | 0.6093 | -122.4099
2929.5469 | 122.3328 | -0.11444 | 122.2458 | -0.01778 | -0.04776 | 0.040507 | 0.020965 | -0.012292 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.044106 | 0.048328 | -0.021844 | 0.019721 | -0.017566 | 0.070441 | 0.08278 | 0.1786 | -0.076794 | 0.088043 | 0.50402 | -0.038036 | 121.9686 | 122.2487 | 122.1557 | -0.14125 | 0.037647 | -122.1753 | 0.092597 | 0.096875 | 0.059228 | -122.163 | -122.0672 | -0.026814 | -0.27716 | 0.20248 | 0.076405 | 0.10322 | 0.002869 | -0.09008 | 0.18488 | 0.19722 | 0.29304 | 0.13416 | -122.3226 | 122.0831 | 122.3631 | 122.2702 | 0.61846 | -122.387
2931.2969 | 122.3145 | -0.068665 | 122.2595 | -0.010149 | -0.04776 | 0.040507 | 0.020965 | -0.012506 | -0.0031579 | -0.021518 | -0.002694 | -0.0020767 | 0.058473 | 0.04432 | 0.048328 | -0.017266 | 0.019721 | -0.012988 | 0.070441 | 0.08278 | 0.17402 | -0.085952 | 0.092622 | 0.50402 | -0.033458 | 121.9824 | 122.2441 | 122.1557 | -0.13668 | -0.017287 | -122.1891 | 0.051399 | 0.055677 | 0.072964 | -122.1767 | -122.0855 | -0.068011 | -0.27716 | 0.16129 | 0.035207 | 0.10322 | -0.015442 | -0.10381 | 0.13911 | 0.15144 | 0.24268 | 0.088386 | -122.3455 | 122.051 | 122.3127 | 122.2244 | 0.57268 | -122.3962
2933.0469 | 122.3419 | -0.086975 | 122.2412 | -0.025411 | -0.047974 | 0.040721 | 0.020965 | -0.012078 | -0.0031579 | -0.013887 | -0.002053 | -0.0027177 | 0.05826 | 0.043893 | 0.048542 | -0.012688 | 0.0243 | -0.012988 | 0.065863 | 0.087359 | 0.17402 | -0.072215 | 0.083464 | 0.51775 | -0.028879 | 121.9778 | 122.2349 | 122.1603 | -0.14125 | 0.01476 | -122.1753 | 0.074287 | 0.073987 | 0.059227 | -122.1539 | -122.0672 | -0.05428 | -0.26343 | 0.17044 | 0.058096 | 0.11238 | -0.006289 | -0.080924 | 0.15284 | 0.17433 | 0.26099 | 0.11127 | -122.3134 | 122.0648 | 122.3219 | 122.2473 | 0.60473 | -122.3825
2934.7344 | 122.4518 | -0.032043 | 122.2183 | -0.01778 | -0.047333 | 0.040293 | 0.020751 | -0.012292 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.044106 | 0.048542 | -0.017266 | 0.019721 | -0.017566 | 0.065863 | 0.08278 | 0.17402 | -0.081373 | 0.097201 | 0.5086 | -0.033458 | 121.9824 | 122.2395 | 122.1466 | -0.14583 | -0.04933 | -122.1525 | 0.014777 | 0.014477 | 0.063807 | -122.1355 | -122.0443 | -0.11379 | -0.23596 | 0.12924 | -0.001415 | 0.11237 | 0.021178 | -0.071772 | 0.097906 | 0.11482 | 0.20606 | 0.051764 | -122.2997 | 122.0144 | 122.2715 | 122.1786 | 0.54064 | -122.3642
2936.4844 | 122.4243 | -0.059509 | 122.2366 | -0.0025182 | -0.047974 | 0.040507 | 0.020965 | -0.012506 | -0.0031579 | -0.013887 | -0.002053 | -0.0022903 | 0.058687 | 0.04432 | 0.048542 | -0.012688 | 0.015142 | -0.012988 | 0.061284 | 0.073622 | 0.18317 | -0.076794 | 0.088043 | 0.5086 | -0.038036 | 121.9778 | 122.2395 | 122.1557 | -0.14583 | -0.017285 | -122.1753 | 0.046821 | 0.046521 | 0.063806 | -122.163 | -122.0535 | -0.086324 | -0.25885 | 0.14755 | 0.021473 | 0.1078 | 0.002868 | -0.080924 | 0.12079 | 0.13313 | 0.24268 | 0.074651 | -122.3134 | 122.0373 | 122.299 | 122.2152 | 0.56811 | -122.3825
2938.2344 | 122.4564 | -0.064087 | 122.2046 | -0.010149 | -0.04776 | 0.040293 | 0.020965 | -0.012506 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.04432 | 0.048542 | -0.017266 | 0.019721 | -0.012988 | 0.061284 | 0.078201 | 0.1786 | -0.081373 | 0.092622 | 0.5086 | -0.038036 | 121.9778 | 122.2395 | 122.1557 | -0.14583 | -0.017286 | -122.1433 | 0.046821 | 0.051099 | 0.068385 | -122.1264 | -122.026 | -0.081746 | -0.2268 | 0.15671 | 0.026051 | 0.1078 | 0.034911 | -0.048881 | 0.12537 | 0.14229 | 0.24268 | 0.083808 | -122.286 | 122.0419 | 122.3036 | 122.2198 | 0.57268 | -122.3504
2939.9375 | 122.3785 | -0.073242 | 122.2412 | -0.010149 | -0.04776 | 0.040721 | 0.021178 | -0.012506 | -0.0025169 | -0.021518 | -0.0024804 | -0.0020767 | 0.058046 | 0.044106 | 0.048542 | -0.021844 | 0.019721 | -0.003831 | 0.079598 | 0.08278 | 0.17402 | -0.081373 | 0.092622 | 0.49944 | -0.033458 | 121.9824 | 122.2395 | 122.1557 | -0.14125 | -0.008131 | -122.1616 | 0.051398 | 0.069411 | 0.077542 | -122.1584 | -122.0672 | -0.068013 | -0.25885 | 0.16586 | 0.039784 | 0.1078 | -0.00171 | -0.085502 | 0.15284 | 0.15602 | 0.24726 | 0.092963 | -122.3226 | 122.0556 | 122.3127 | 122.229 | 0.57268 | -122.3825
2941.7031 | 122.3099 | -0.082397 | 122.2504 | -0.01778 | -0.04776 | 0.040507 | 0.020965 | -0.012719 | -0.0031579 | -0.013887 | -0.0024804 | -0.0022903 | 0.058473 | 0.04432 | 0.048328 | -0.017266 | 0.019721 | -0.008409 | 0.070441 | 0.08278 | 0.1786 | -0.076794 | 0.083464 | 0.5086 | -0.033458 | 121.9824 | 122.2487 | 122.1511 | -0.14125 | 0.005603 | -122.1799 | 0.065131 | 0.073988 | 0.068385 | -122.1676 | -122.0718 | -0.058858 | -0.268 | 0.16586 | 0.048939 | 0.1078 | -0.001708 | -0.099236 | 0.15284 | 0.16518 | 0.26099 | 0.10212 | -122.3272 | 122.0648 | 122.3311 | 122.2335 | 0.59099 | -122.3916
2943.4062 | 122.4518 | -0.045776 | 122.2137 | -0.010149 | -0.04776 | 0.040293 | 0.020751 | -0.012719 | -0.0025169 | -0.021518 | -0.0024804 | -0.0022903 | 0.058473 | 0.044747 | 0.048542 | -0.012688 | 0.0243 | -0.008409 | 0.07502 | 0.078201 | 0.18317 | -0.072215 | 0.088043 | 0.5086 | -0.028879 | 121.9824 | 122.2395 | 122.1557 | -0.14125 | -0.026439 | -122.1387 | 0.033088 | 0.037367 | 0.063806 | -122.1355 | -122.0306 | -0.095479 | -0.23138 | 0.13382 | 0.016897 | 0.11238 | 0.025756 | -0.058036 | 0.1208 | 0.12398 | 0.22895 | 0.070076 | -122.286 | 122.0281 | 122.2853 | 122.2015 | 0.55437 | -122.355
2945.1562 | 122.438 | -0.050354 | 122.1954 | -0.010149 | -0.04776 | 0.040721 | 0.020965 | -0.012506 | -0.0029443 | -0.013887 | -0.0024804 | -0.0025041 | 0.058687 | 0.044106 | 0.048328 | -0.017266 | 0.019721 | -0.017566 | 0.065863 | 0.08278 | 0.1786 | -0.081373 | 0.078886 | 0.50402 | -0.038036 | 121.9778 | 122.2395 | 122.1603 | -0.14125 | -0.031019 | -122.1296 | 0.033088 | 0.032788 | 0.063807 | -122.1127 | -122.0168 | -0.090901 | -0.21765 | 0.12924 | 0.012318 | 0.10322 | 0.044066 | -0.035148 | 0.11622 | 0.13313 | 0.22895 | 0.070075 | -122.2768 | 122.0281 | 122.2899 | 122.2106 | 0.55437 | -122.3367
2946.9219 | 122.3602 | -0.10071 | 122.2183 | -0.0025182 | -0.04776 | 0.040507 | 0.021392 | -0.012719 | -0.0027305 | -0.021518 | -0.0024804 | -0.0022903 | 0.058687 | 0.044106 | 0.048542 | -0.017266 | 0.0243 | -0.017566 | 0.07502 | 0.08278 | 0.17402 | -0.081373 | 0.083464 | 0.5086 | -0.0243 | 121.9778 | 122.2395 | 122.1557 | -0.13668 | 0.019335 | -122.1433 | 0.083442 | 0.083142 | 0.063807 | -122.1355 | -122.0443 | -0.035968 | -0.24054 | 0.18417 | 0.076408 | 0.11238 | 0.021178 | -0.062614 | 0.17573 | 0.18349 | 0.27472 | 0.12501 | -122.2997 | 122.0785 | 122.3402 | 122.2564 | 0.6093 | -122.355
2948.6719 | 122.3053 | -0.091553 | 122.2595 | -0.010149 | -0.04776 | 0.040293 | 0.021178 | -0.012506 | -0.0031579 | -0.029148 | -0.002694 | -0.0025041 | 0.058473 | 0.04432 | 0.048328 | -0.017266 | 0.028878 | -0.012988 | 0.070441 | 0.08278 | 0.16944 | -0.072215 | 0.092622 | 0.51317 | -0.033458 | 121.9732 | 122.2487 | 122.1603 | -0.14125 | 0.019338 | -122.1891 | 0.074287 | 0.078565 | 0.059227 | -122.1767 | -122.0901 | -0.049702 | -0.28631 | 0.18417 | 0.058095 | 0.1078 | -0.010863 | -0.099234 | 0.16199 | 0.17433 | 0.26099 | 0.12043 | -122.3317 | 122.0648 | 122.3402 | 122.2518 | 0.60473 | -122.4008
2950.3594 | 122.4152 | -0.073242 | 122.2229 | -0.010149 | -0.047547 | 0.040293 | 0.020537 | -0.012078 | -0.0027305 | -0.029148 | -0.002694 | -0.0022903 | 0.058046 | 0.04432 | 0.048542 | -0.017266 | 0.019721 | -0.017566 | 0.070441 | 0.078201 | 0.17402 | -0.076794 | 0.083464 | 0.51317 | -0.033458 | 121.9778 | 122.2487 | 122.1557 | -0.14125 | -0.003552 | -122.1525 | 0.055976 | 0.055676 | 0.059228 | -122.1447 | -122.0489 | -0.068013 | -0.24511 | 0.15671 | 0.039784 | 0.1078 | 0.025758 | -0.067191 | 0.14368 | 0.15144 | 0.24726 | 0.092963 | -122.2997 | 122.051 | 122.3219 | 122.229 | 0.58642 | -122.3642
2952.125 | 122.319 | -0.10529 | 122.2595 | -0.010149 | -0.04776 | 0.040507 | 0.020751 | -0.012506 | -0.0029443 | -0.013887 | -0.0022666 | -0.0025041 | 0.058473 | 0.044534 | 0.048115 | -0.012688 | 0.019721 | -0.012988 | 0.07502 | 0.08278 | 0.16944 | -0.085952 | 0.078886 | 0.5086 | -0.028879 | 121.9732 | 122.2441 | 122.1603 | -0.14125 | 0.019334 | -122.1845 | 0.092598 | 0.092298 | 0.072964 | -122.1767 | -122.0901 | -0.035969 | -0.28631 | 0.18417 | 0.076407 | 0.11238 | -0.015442 | -0.099234 | 0.18031 | 0.18807 | 0.27472 | 0.12501 | -122.3455 | 122.0785 | 122.3494 | 122.2656 | 0.61388 | -122.4008
2953.9062 | 122.438 | -0.059509 | 122.2 | 0.0051128 | -0.04776 | 0.040293 | 0.020965 | -0.012506 | -0.0027305 | -0.013887 | -0.0022666 | -0.0020767 | 0.058687 | 0.044106 | 0.048115 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.08278 | 0.18317 | -0.072215 | 0.088043 | 0.50402 | -0.038036 | 121.9732 | 122.2532 | 122.1511 | -0.14125 | -0.012706 | -122.1341 | 0.046821 | 0.046521 | 0.059227 | -122.1172 | -122.0168 | -0.081746 | -0.2268 | 0.14755 | 0.021473 | 0.10322 | 0.053225 | -0.048882 | 0.12537 | 0.14229 | 0.24268 | 0.07923 | -122.2722 | 122.0327 | 122.3127 | 122.2106 | 0.56353 | -122.3413
2955.6562 | 122.3282 | -0.10529 | 122.287 | -0.0025182 | -0.04776 | 0.040507 | 0.020965 | -0.012506 | -0.0031579 | -0.029148 | -0.0024804 | -0.0020767 | 0.058473 | 0.044534 | 0.048542 | -0.017266 | 0.015142 | -0.008409 | 0.070441 | 0.087359 | 0.16944 | -0.085952 | 0.088043 | 0.51775 | -0.028879 | 121.9732 | 122.2349 | 122.1603 | -0.14583 | 0.019334 | -122.2165 | 0.08802 | 0.096877 | 0.077543 | -122.1996 | -122.1175 | -0.040547 | -0.31378 | 0.19333 | 0.076407 | 0.11695 | -0.052065 | -0.1267 | 0.17573 | 0.19265 | 0.27472 | 0.12043 | -122.3729 | 122.0785 | 122.3402 | 122.2656 | 0.62304 | -122.4328
2957.3438 | 122.4197 | -0.064087 | 122.2275 | -0.010149 | -0.04776 | 0.040293 | 0.020537 | -0.012719 | -0.0027305 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.04432 | 0.048328 | -0.017266 | 0.010564 | -0.012988 | 0.070441 | 0.078201 | 0.1786 | -0.076794 | 0.083464 | 0.5086 | -0.028879 | 121.9824 | 122.2395 | 122.1603 | -0.14125 | -0.012707 | -122.157 | 0.046821 | 0.051099 | 0.063806 | -122.1493 | -122.0489 | -0.077168 | -0.24511 | 0.14755 | 0.035208 | 0.11238 | 0.012023 | -0.067191 | 0.13453 | 0.14229 | 0.24268 | 0.074651 | -122.3043 | 122.0465 | 122.3036 | 122.2244 | 0.57268 | -122.3687
2959.1094 | 122.4335 | -0.054932 | 122.2321 | -0.0025182 | -0.048401 | 0.040293 | 0.020965 | -0.012719 | -0.0029443 | -0.029148 | -0.0022666 | -0.0020767 | 0.05826 | 0.044106 | 0.048756 | -0.017266 | 0.015142 | -0.017566 | 0.065863 | 0.078201 | 0.1786 | -0.072215 | 0.083464 | 0.5086 | -0.038036 | 121.9869 | 122.2441 | 122.1603 | -0.14125 | -0.017283 | -122.1662 | 0.037666 | 0.037366 | 0.054649 | -122.1539 | -122.0535 | -0.086323 | -0.24511 | 0.1384 | 0.016896 | 0.10322 | 0.012023 | -0.071769 | 0.1208 | 0.13313 | 0.23353 | 0.070074 | -122.3043 | 122.0419 | 122.299 | 122.2152 | 0.56353 | -122.3733
2960.7969 | 122.374 | -0.10071 | 122.2504 | -0.01778 | -0.047974 | 0.040507 | 0.020965 | -0.012506 | -0.0031579 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.044106 | 0.048328 | -0.008109 | 0.019721 | -0.003831 | 0.070441 | 0.08278 | 0.1786 | -0.076794 | 0.083464 | 0.50402 | -0.033458 | 121.9732 | 122.2487 | 122.1603 | -0.14583 | 0.023914 | -122.1799 | 0.092599 | 0.096877 | 0.072963 | -122.1676 | -122.0718 | -0.045125 | -0.27716 | 0.18417 | 0.06725 | 0.11237 | -0.001708 | -0.090079 | 0.17115 | 0.18349 | 0.2793 | 0.12043 | -122.3272 | 122.0739 | 122.3494 | 122.261 | 0.60473 | -122.3962
2962.5469 | 122.3831 | -0.07782 | 122.2229 | -0.01778 | -0.048188 | 0.04008 | 0.020751 | -0.012719 | -0.0027305 | -0.021518 | -0.0022666 | -0.0020767 | 0.05826 | 0.044534 | 0.048542 | -0.017266 | 0.019721 | -0.012988 | 0.070441 | 0.08278 | 0.1786 | -0.081373 | 0.083464 | 0.51317 | -0.028879 | 121.9778 | 122.2487 | 122.1557 | -0.14125 | -0.003553 | -122.1525 | 0.060554 | 0.064832 | 0.068385 | -122.1401 | -122.0443 | -0.063435 | -0.24511 | 0.16128 | 0.048941 | 0.11238 | 0.025758 | -0.067191 | 0.14826 | 0.1606 | 0.25642 | 0.097541 | -122.3043 | 122.0556 | 122.3265 | 122.2335 | 0.59099 | -122.3642
2964.3125 | 122.3282 | -0.10071 | 122.2549 | -0.010149 | -0.047974 | 0.040507 | 0.020965 | -0.012719 | -0.0027305 | -0.021518 | -0.0024804 | -0.0025041 | 0.05826 | 0.04432 | 0.048328 | -0.021844 | 0.019721 | -0.022144 | 0.07502 | 0.08278 | 0.18317 | -0.072215 | 0.083464 | 0.50402 | -0.038036 | 121.9778 | 122.2441 | 122.1557 | -0.14583 | 0.028493 | -122.1799 | 0.078864 | 0.078564 | 0.050071 | -122.1722 | -122.0718 | -0.045125 | -0.27716 | 0.18417 | 0.062672 | 0.1078 | -0.010865 | -0.099235 | 0.17573 | 0.18349 | 0.28388 | 0.12043 | -122.3272 | 122.0785 | 122.3448 | 122.2564 | 0.60473 | -122.4008
2966 | 122.3648 | -0.086975 | 122.2549 | -0.0025182 | -0.048188 | 0.040721 | 0.020965 | -0.012292 | -0.0029443 | -0.021518 | -0.0024804 | -0.0025041 | 0.058473 | 0.044747 | 0.048328 | -0.026423 | 0.0243 | -0.012988 | 0.079598 | 0.08278 | 0.18317 | -0.072215 | 0.088043 | 0.51317 | -0.033458 | 121.9778 | 122.2349 | 122.1603 | -0.15041 | 0.01476 | -122.1753 | 0.060552 | 0.073987 | 0.059227 | -122.1722 | -122.0718 | -0.063437 | -0.27716 | 0.17502 | 0.053517 | 0.11695 | -0.020022 | -0.094657 | 0.16657 | 0.16975 | 0.27015 | 0.11127 | -122.3272 | 122.0648 | 122.3219 | 122.2473 | 0.60015 | -122.4054
2967.75 | 122.4243 | -0.064087 | 122.2687 | -0.010149 | -0.04776 | 0.040721 | 0.020537 | -0.012506 | -0.0029443 | -0.013887 | -0.0018394 | -0.0025041 | 0.058473 | 0.04432 | 0.048542 | -0.012688 | 0.019721 | -0.017566 | 0.079598 | 0.08278 | 0.16944 | -0.076794 | 0.092622 | 0.50402 | -0.033458 | 121.9778 | 122.2441 | 122.1557 | -0.14125 | -0.012707 | -122.1891 | 0.051399 | 0.046521 | 0.059228 | -122.1859 | -122.0992 | -0.077168 | -0.29089 | 0.15671 | 0.030629 | 0.1078 | -0.024598 | -0.11297 | 0.14369 | 0.14687 | 0.23353 | 0.083808 | -122.3455 | 122.0419 | 122.3082 | 122.2198 | 0.5681 | -122.4099
2969.4531 | 122.406 | -0.073242 | 122.1954 | -0.0025182 | -0.047974 | 0.040507 | 0.020965 | -0.012719 | -0.0029443 | -0.021518 | -0.002053 | -0.0022903 | 0.058046 | 0.04432 | 0.048115 | -0.017266 | 0.0243 | -0.012988 | 0.070441 | 0.08278 | 0.18775 | -0.076794 | 0.078886 | 0.51317 | -0.033458 | 121.9824 | 122.2441 | 122.1603 | -0.14583 | -0.003552 | -122.125 | 0.055976 | 0.060254 | 0.063806 | -122.1127 | -122.0077 | -0.072591 | -0.21307 | 0.15213 | 0.039784 | 0.11237 | 0.048644 | -0.035148 | 0.14368 | 0.15602 | 0.26099 | 0.097542 | -122.2722 | 122.0556 | 122.3173 | 122.2335 | 0.58642 | -122.3413
2971.2031 | 122.3694 | -0.10071 | 122.2321 | 0.0051128 | -0.047974 | 0.040293 | 0.020751 | -0.012506 | -0.0031579 | -0.013887 | -0.0024804 | -0.0020767 | 0.058473 | 0.044106 | 0.048115 | -0.017266 | 0.015142 | -0.012988 | 0.070441 | 0.08278 | 0.18317 | -0.072215 | 0.083464 | 0.51317 | -0.028879 | 121.9732 | 122.2487 | 122.1603 | -0.13668 | 0.028493 | -122.1616 | 0.083442 | 0.08772 | 0.059227 | -122.1493 | -122.0489 | -0.035968 | -0.25885 | 0.18417 | 0.071829 | 0.1078 | 0.016602 | -0.071769 | 0.17115 | 0.18349 | 0.28388 | 0.11585 | -122.3043 | 122.0739 | 122.3494 | 122.261 | 0.61388 | -122.3687
2972.9688 | 122.4243 | -0.064087 | 122.2092 | -0.010149 | -0.047974 | 0.040293 | 0.020751 | -0.012719 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.044534 | 0.048328 | -0.012688 | 0.019721 | -0.017566 | 0.070441 | 0.08278 | 0.1786 | -0.072215 | 0.083464 | 0.49944 | -0.028879 | 121.9778 | 122.2441 | 122.1511 | -0.14125 | -0.008128 | -122.1387 | 0.051399 | 0.046521 | 0.054649 | -122.1264 | -122.0306 | -0.077168 | -0.23138 | 0.14755 | 0.035208 | 0.11238 | 0.034912 | -0.058037 | 0.13453 | 0.14687 | 0.24268 | 0.083808 | -122.2814 | 122.0419 | 122.3082 | 122.2152 | 0.56353 | -122.3504
2974.6562 | 122.3785 | -0.073242 | 122.2549 | -0.01778 | -0.047974 | 0.040507 | 0.020537 | -0.012719 | -0.0033715 | -0.029148 | -0.0022666 | -0.0020767 | 0.058473 | 0.044534 | 0.048328 | -0.017266 | 0.019721 | -0.008409 | 0.070441 | 0.087359 | 0.1786 | -0.076794 | 0.083464 | 0.5086 | -0.033458 | 121.9824 | 122.2487 | 122.1603 | -0.14583 | -0.003552 | -122.1845 | 0.055976 | 0.064833 | 0.068385 | -122.1676 | -122.0763 | -0.072591 | -0.27258 | 0.15671 | 0.039784 | 0.11237 | -0.006286 | -0.094657 | 0.14368 | 0.1606 | 0.25184 | 0.092963 | -122.3317 | 122.0556 | 122.3219 | 122.2335 | 0.58184 | -122.4008
2976.4062 | 122.374 | -0.10071 | 122.2412 | -0.0025182 | -0.047974 | 0.040507 | 0.020751 | -0.012719 | -0.0031579 | -0.021518 | -0.002053 | -0.0022903 | 0.058687 | 0.04432 | 0.047901 | -0.017266 | 0.010564 | -0.003831 | 0.070441 | 0.08278 | 0.18317 | -0.076794 | 0.088043 | 0.5086 | -0.028879 | 121.9778 | 122.2441 | 122.1649 | -0.14583 | 0.023914 | -122.1708 | 0.083442 | 0.096877 | 0.072963 | -122.1584 | -122.058 | -0.045125 | -0.26343 | 0.18875 | 0.071829 | 0.11695 | 0.002868 | -0.076345 | 0.17115 | 0.18349 | 0.28388 | 0.11127 | -122.318 | 122.0785 | 122.3448 | 122.2656 | 0.6093 | -122.387
2978.0938 | 122.374 | -0.086975 | 122.2275 | -0.010149 | -0.047974 | 0.04008 | 0.020751 | -0.012933 | -0.0031579 | -0.021518 | -0.002053 | -0.0025041 | 0.05826 | 0.044106 | 0.048328 | -0.021844 | 0.019721 | -0.017566 | 0.07502 | 0.078201 | 0.1786 | -0.081373 | 0.083464 | 0.51775 | -0.028879 | 121.9732 | 122.2487 | 122.1603 | -0.14583 | 0.005602 | -122.1525 | 0.065131 | 0.069409 | 0.063807 | -122.1493 | -122.0489 | -0.058858 | -0.25427 | 0.17044 | 0.058096 | 0.11695 | 0.02118 | -0.067191 | 0.162 | 0.16518 | 0.26557 | 0.1067 | -122.3089 | 122.0602 | 122.3356 | 122.2473 | 0.60473 | -122.3733
2979.8438 | 122.3511 | -0.10529 | 122.2275 | -0.01778 | -0.048188 | 0.040507 | 0.020965 | -0.012506 | -0.0031579 | -0.029148 | -0.002053 | -0.0025041 | 0.05826 | 0.044534 | 0.048542 | -0.017266 | 0.015142 | -0.017566 | 0.07502 | 0.08278 | 0.1786 | -0.076794 | 0.078886 | 0.51317 | -0.038036 | 121.9824 | 122.2441 | 122.1557 | -0.15041 | 0.028492 | -122.1525 | 0.08802 | 0.08772 | 0.059228 | -122.1447 | -122.0489 | -0.045126 | -0.24511 | 0.18417 | 0.06725 | 0.11238 | 0.016601 | -0.071769 | 0.18031 | 0.18807 | 0.28388 | 0.12043 | -122.3043 | 122.0877 | 122.3494 | 122.261 | 0.61846 | -122.3779
2981.6094 | 122.438 | -0.050354 | 122.2046 | -0.0025182 | -0.047974 | 0.040507 | 0.020751 | -0.012506 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.05826 | 0.044534 | 0.048542 | -0.021844 | 0.0243 | -0.008409 | 0.065863 | 0.08278 | 0.1786 | -0.081373 | 0.083464 | 0.50402 | -0.0243 | 121.9824 | 122.2441 | 122.1603 | -0.14583 | -0.031019 | -122.1387 | 0.02851 | 0.041945 | 0.072964 | -122.1218 | -122.026 | -0.095479 | -0.22223 | 0.13382 | 0.026054 | 0.12153 | 0.039489 | -0.044303 | 0.11622 | 0.13313 | 0.22895 | 0.074654 | -122.286 | 122.0327 | 122.2944 | 122.2106 | 0.55437 | -122.3504
2983.3125 | 122.3373 | -0.091553 | 122.2504 | -0.0025182 | -0.048188 | 0.040293 | 0.020965 | -0.012506 | -0.0029443 | -0.013887 | -0.0024804 | -0.0020767 | 0.058687 | 0.044534 | 0.048115 | -0.026423 | 0.019721 | -0.012988 | 0.07502 | 0.078201 | 0.1786 | -0.076794 | 0.088043 | 0.49944 | -0.028879 | 121.9824 | 122.2532 | 122.1603 | -0.14583 | 0.014759 | -122.1753 | 0.06513 | 0.078565 | 0.063806 | -122.1722 | -122.0718 | -0.05428 | -0.268 | 0.1796 | 0.062674 | 0.11695 | 0.002871 | -0.090079 | 0.16657 | 0.16975 | 0.27015 | 0.11127 | -122.3272 | 122.0739 | 122.3448 | 122.2518 | 0.59099 | -122.3962
2985.0781 | 122.3236 | -0.10529 | 122.2641 | -0.0025182 | -0.048188 | 0.040507 | 0.020965 | -0.012933 | -0.0029443 | -0.021518 | -0.0024804 | -0.0025041 | 0.058687 | 0.04432 | 0.048115 | -0.012688 | 0.019721 | -0.012988 | 0.070441 | 0.08278 | 0.1786 | -0.076794 | 0.088043 | 0.5086 | -0.0243 | 121.9824 | 122.2487 | 122.1649 | -0.14125 | 0.028492 | -122.1937 | 0.092598 | 0.092298 | 0.063806 | -122.1813 | -122.0855 | -0.035969 | -0.28173 | 0.19333 | 0.080986 | 0.11695 | -0.015441 | -0.099233 | 0.17573 | 0.18807 | 0.28388 | 0.12501 | -122.3409 | 122.0877 | 122.3539 | 122.2702 | 0.61388 | -122.4054
2986.7656 | 122.3328 | -0.10529 | 122.2687 | -0.0025182 | -0.047974 | 0.040293 | 0.020751 | -0.012719 | -0.0027305 | -0.013887 | -0.0024804 | -0.0025041 | 0.058473 | 0.044534 | 0.047901 | -0.021844 | 0.019721 | -0.012988 | 0.070441 | 0.078201 | 0.18317 | -0.072215 | 0.083464 | 0.50402 | -0.033458 | 121.9824 | 122.2487 | 122.1603 | -0.14125 | 0.033071 | -122.1982 | 0.083442 | 0.092298 | 0.059227 | -122.1905 | -122.0855 | -0.035969 | -0.28631 | 0.18875 | 0.071828 | 0.1078 | -0.020019 | -0.10839 | 0.17573 | 0.18349 | 0.28846 | 0.12501 | -122.3409 | 122.0877 | 122.3539 | 122.2656 | 0.6093 | -122.4099
2988.5156 | 122.4106 | -0.073242 | 122.2412 | -0.0025182 | -0.048188 | 0.040293 | 0.020965 | -0.012506 | -0.0031579 | -0.013887 | -0.0024804 | -0.0025041 | 0.05826 | 0.044534 | 0.048328 | -0.021844 | 0.0243 | -0.012988 | 0.070441 | 0.08278 | 0.1786 | -0.081373 | 0.078886 | 0.5086 | -0.028879 | 121.9778 | 122.2441 | 122.1603 | -0.14125 | -0.008131 | -122.1708 | 0.051398 | 0.060254 | 0.068385 | -122.1584 | -122.0626 | -0.068013 | -0.26343 | 0.15213 | 0.044363 | 0.11238 | 0.002868 | -0.080924 | 0.14368 | 0.15602 | 0.25184 | 0.097542 | -122.3226 | 122.051 | 122.3173 | 122.2335 | 0.58184 | -122.3825
2990.2031 | 122.3602 | -0.068665 | 122.2504 | -0.010149 | -0.048188 | 0.040293 | 0.020965 | -0.012719 | -0.0031579 | -0.029148 | -0.002053 | -0.0022903 | 0.058473 | 0.044747 | 0.048115 | -0.026423 | 0.019721 | -0.012988 | 0.070441 | 0.08278 | 0.17402 | -0.076794 | 0.083464 | 0.50402 | -0.033458 | 121.9869 | 122.2441 | 122.1649 | -0.14125 | -0.008129 | -122.1799 | 0.042242 | 0.055677 | 0.063806 | -122.1676 | -122.0764 | -0.07259 | -0.26342 | 0.15213 | 0.035207 | 0.1078 | -0.006287 | -0.0855 | 0.13911 | 0.15144 | 0.24268 | 0.088386 | -122.3272 | 122.0556 | 122.3127 | 122.2335 | 0.57268 | -122.3916
2991.9688 | 122.406 | -0.050354 | 122.2275 | -0.010149 | -0.04776 | 0.040293 | 0.020751 | -0.012933 | -0.0029443 | -0.021518 | -0.0024804 | -0.0022903 | 0.058473 | 0.044747 | 0.048115 | -0.021844 | 0.0243 | -0.008409 | 0.065863 | 0.08278 | 0.18317 | -0.072215 | 0.083464 | 0.50402 | -0.033458 | 121.9824 | 122.2487 | 122.1557 | -0.13668 | -0.021861 | -122.1616 | 0.02851 | 0.041945 | 0.063806 | -122.1447 | -122.0443 | -0.086322 | -0.24511 | 0.13382 | 0.016896 | 0.10322 | 0.02118 | -0.071769 | 0.11622 | 0.13313 | 0.23353 | 0.074654 | -122.2997 | 122.0327 | 122.299 | 122.2061 | 0.55437 | -122.3642
2993.7344 | 122.4335 | -0.059509 | 122.2366 | -0.025411 | -0.048401 | 0.039652 | 0.020751 | -0.012719 | -0.0033715 | -0.021518 | -0.0022666 | -0.0020767 | 0.05826 | 0.04432 | 0.048115 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.08278 | 0.1786 | -0.076794 | 0.083464 | 0.5086 | -0.038036 | 121.9778 | 122.2487 | 122.1649 | -0.14583 | -0.017285 | -122.157 | 0.037665 | 0.046521 | 0.063806 | -122.1539 | -122.058 | -0.086324 | -0.25885 | 0.14297 | 0.021473 | 0.1078 | 0.012025 | -0.071767 | 0.13911 | 0.14229 | 0.2381 | 0.083809 | -122.3134 | 122.0373 | 122.3082 | 122.2244 | 0.56811 | -122.3825
2995.4844 | 122.3145 | -0.10071 | 122.2778 | -0.010149 | -0.047974 | 0.039652 | 0.020965 | -0.012506 | -0.0031579 | -0.021518 | -0.0024804 | -0.0025041 | 0.058046 | 0.04432 | 0.048115 | -0.017266 | 0.0243 | -0.012988 | 0.070441 | 0.08278 | 0.17402 | -0.076794 | 0.083464 | 0.5086 | -0.033458 | 121.9686 | 122.2487 | 122.1603 | -0.14583 | 0.023914 | -122.2074 | 0.083442 | 0.08772 | 0.063806 | -122.1951 | -122.1038 | -0.045125 | -0.3092 | 0.18417 | 0.06725 | 0.11237 | -0.029174 | -0.11755 | 0.17115 | 0.18349 | 0.27472 | 0.12501 | -122.3546 | 122.0693 | 122.3494 | 122.261 | 0.6093 | -122.4237
2997.1875 | 122.3602 | -0.086975 | 122.2549 | -0.010149 | -0.04776 | 0.040293 | 0.020965 | -0.012719 | -0.0029443 | -0.029148 | -0.002053 | -0.0022903 | 0.05826 | 0.04432 | 0.048115 | -0.017266 | 0.019721 | -0.008409 | 0.07502 | 0.08278 | 0.18317 | -0.081373 | 0.083464 | 0.51317 | -0.033458 | 121.9824 | 122.2441 | 122.1649 | -0.14583 | 0.005602 | -122.1799 | 0.069709 | 0.078566 | 0.072964 | -122.1722 | -122.0718 | -0.058858 | -0.27258 | 0.17044 | 0.053517 | 0.11237 | -0.010865 | -0.090078 | 0.162 | 0.16975 | 0.27015 | 0.1067 | -122.3363 | 122.0693 | 122.3311 | 122.2518 | 0.60015 | -122.4008
2998.9531 | 122.4197 | -0.064087 | 122.2549 | -0.010149 | -0.048188 | 0.040293 | 0.020751 | -0.012719 | -0.0029443 | -0.029148 | -0.0022666 | -0.0022903 | 0.05826 | 0.04432 | 0.048542 | -0.021844 | 0.0243 | -0.012988 | 0.065863 | 0.08278 | 0.1786 | -0.081373 | 0.078886 | 0.51317 | -0.038036 | 121.9824 | 122.2532 | 122.1603 | -0.14583 | -0.017286 | -122.1891 | 0.042243 | 0.051099 | 0.068385 | -122.1722 | -122.0763 | -0.081746 | -0.27258 | 0.14297 | 0.026051 | 0.1078 | -0.001707 | -0.094657 | 0.12995 | 0.14687 | 0.24268 | 0.088387 | -122.3363 | 122.0465 | 122.3173 | 122.2244 | 0.57726 | -122.4008
3000.7188 | 122.4197 | -0.041199 | 122.2275 | -0.010149 | -0.047974 | 0.039652 | 0.020323 | -0.012506 | -0.0029443 | -0.029148 | -0.0022666 | -0.0022903 | 0.058473 | 0.044961 | 0.048115 | -0.012688 | 0.019721 | -0.012988 | 0.07502 | 0.08278 | 0.17402 | -0.081373 | 0.083464 | 0.51775 | -0.033458 | 121.9869 | 122.2532 | 122.1649 | -0.13668 | -0.040174 | -122.1525 | 0.028511 | 0.028211 | 0.068385 | -122.1447 | -122.0535 | -0.095477 | -0.24054 | 0.12466 | 0.007741 | 0.10322 | 0.025759 | -0.062612 | 0.11622 | 0.12398 | 0.21521 | 0.06092 | -122.3089 | 122.0281 | 122.2944 | 122.2061 | 0.55895 | -122.3642
3002.4844 | 122.4609 | -0.054932 | 122.2 | -0.010149 | -0.048188 | 0.04008 | 0.020537 | -0.012933 | -0.0029443 | -0.013887 | -0.002053 | -0.0022903 | 0.05826 | 0.044747 | 0.048328 | -0.017266 | 0.028878 | -0.008409 | 0.065863 | 0.087359 | 0.1786 | -0.072215 | 0.083464 | 0.51317 | -0.033458 | 121.9824 | 122.2441 | 122.1557 | -0.13668 | -0.017283 | -122.1341 | 0.037666 | 0.046523 | 0.063806 | -122.1127 | -122.0214 | -0.081744 | -0.21765 | 0.1384 | 0.021474 | 0.10322 | 0.044067 | -0.044303 | 0.1208 | 0.14229 | 0.23353 | 0.08381 | -122.2722 | 122.0373 | 122.299 | 122.2106 | 0.56811 | -122.3367
3004.1875 | 122.4518 | -0.036621 | 122.2366 | -0.0025182 | -0.048188 | 0.04008 | 0.020537 | -0.012719 | -0.0031579 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.04432 | 0.048328 | -0.021844 | 0.0243 | -0.008409 | 0.070441 | 0.087359 | 0.1786 | -0.081373 | 0.088043 | 0.51775 | -0.033458 | 121.9869 | 122.2441 | 122.1603 | -0.15041 | -0.044752 | -122.1662 | 0.014777 | 0.028212 | 0.072964 | -122.1493 | -122.058 | -0.11379 | -0.24969 | 0.12466 | 0.003163 | 0.11695 | 0.007446 | -0.076346 | 0.10706 | 0.12398 | 0.21522 | 0.060921 | -122.318 | 122.0236 | 122.2807 | 122.1969 | 0.55437 | -122.387
3005.9375 | 122.4472 | -0.054932 | 122.2412 | -0.010149 | -0.047974 | 0.04008 | 0.020751 | -0.012506 | -0.0027305 | -0.021518 | -0.002053 | -0.0025041 | 0.058046 | 0.044534 | 0.048328 | -0.012688 | 0.019721 | -0.012988 | 0.07502 | 0.078201 | 0.1786 | -0.076794 | 0.088043 | 0.51317 | -0.033458 | 121.9824 | 122.2487 | 122.1557 | -0.13668 | -0.021862 | -122.1662 | 0.042244 | 0.041944 | 0.063806 | -122.163 | -122.0626 | -0.081744 | -0.25885 | 0.14297 | 0.021474 | 0.10322 | 0.007447 | -0.085502 | 0.12995 | 0.13313 | 0.23353 | 0.074653 | -122.318 | 122.0373 | 122.3036 | 122.2106 | 0.56811 | -122.3779
3007.6875 | 122.3785 | -0.054932 | 122.2366 | -0.0025182 | -0.047974 | 0.04008 | 0.020751 | -0.012506 | -0.0029443 | -0.029148 | -0.002053 | -0.0025041 | 0.058473 | 0.044534 | 0.048542 | -0.017266 | 0.019721 | -0.003831 | 0.065863 | 0.087359 | 0.18317 | -0.081373 | 0.074307 | 0.50402 | -0.033458 | 121.9869 | 122.2395 | 122.1649 | -0.14583 | -0.026441 | -122.1708 | 0.037666 | 0.051101 | 0.077542 | -122.1493 | -122.0535 | -0.090901 | -0.24969 | 0.12924 | 0.021474 | 0.11237 | 0.002868 | -0.071767 | 0.1208 | 0.14229 | 0.23811 | 0.074653 | -122.318 | 122.0419 | 122.2944 | 122.2198 | 0.55895 | -122.3825
3009.4531 | 122.3145 | -0.10529 | 122.2687 | -0.01778 | -0.048188 | 0.04008 | 0.020537 | -0.012292 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.05826 | 0.044534 | 0.048328 | -0.012688 | 0.019721 | -0.012988 | 0.07502 | 0.08278 | 0.18317 | -0.076794 | 0.088043 | 0.51317 | -0.038036 | 121.9732 | 122.2532 | 122.1649 | -0.14583 | 0.028492 | -122.1937 | 0.092598 | 0.092298 | 0.063806 | -122.1859 | -122.0855 | -0.040547 | -0.29547 | 0.19333 | 0.06725 | 0.1078 | -0.01544 | -0.10381 | 0.18031 | 0.18807 | 0.28846 | 0.12501 | -122.3455 | 122.0785 | 122.3585 | 122.2702 | 0.61846 | -122.4145
3011.1562 | 122.3328 | -0.10071 | 122.2595 | -0.0025182 | -0.048188 | 0.039866 | 0.020537 | -0.012292 | -0.0031579 | -0.021518 | -0.002053 | -0.0020767 | 0.05826 | 0.044961 | 0.048115 | -0.026423 | 0.019721 | -0.012988 | 0.065863 | 0.096516 | 0.18317 | -0.076794 | 0.092622 | 0.51775 | -0.019721 | 121.9824 | 122.2532 | 122.1603 | -0.14125 | 0.023914 | -122.1937 | 0.074285 | 0.08772 | 0.063806 | -122.163 | -122.0763 | -0.040547 | -0.27716 | 0.19333 | 0.080987 | 0.12153 | -0.006284 | -0.099234 | 0.16657 | 0.19722 | 0.28388 | 0.12043 | -122.3363 | 122.0831 | 122.3539 | 122.261 | 0.61846 | -122.4008
3012.9062 | 122.3694 | -0.07782 | 122.2321 | -0.0025182 | -0.048188 | 0.04008 | 0.020537 | -0.012506 | -0.0031579 | -0.013887 | -0.002694 | -0.0025041 | 0.058473 | 0.044534 | 0.047901 | -0.017266 | 0.019721 | -0.008409 | 0.07502 | 0.08278 | 0.1786 | -0.072215 | 0.092622 | 0.51317 | -0.0243 | 121.9824 | 122.2441 | 122.1649 | -0.14583 | 0.005605 | -122.157 | 0.060554 | 0.069411 | 0.063806 | -122.1493 | -122.0535 | -0.068013 | -0.24969 | 0.17044 | 0.05352 | 0.12153 | 0.012023 | -0.06719 | 0.15284 | 0.1606 | 0.25642 | 0.097541 | -122.3043 | 122.0602 | 122.3219 | 122.2427 | 0.59099 | -122.3779
3014.6719 | 122.4792 | -0.050354 | 122.2321 | -0.010149 | -0.04776 | 0.040293 | 0.020965 | -0.012719 | -0.0031579 | -0.013887 | -0.002694 | -0.0022903 | 0.058046 | 0.044747 | 0.048115 | -0.021844 | 0.028878 | -0.017566 | 0.070441 | 0.091937 | 0.18317 | -0.085952 | 0.083464 | 0.5086 | -0.033458 | 121.9824 | 122.2532 | 122.1649 | -0.14583 | -0.035598 | -122.1616 | 0.02851 | 0.032788 | 0.068386 | -122.1401 | -122.0489 | -0.095479 | -0.24969 | 0.13382 | 0.016896 | 0.11237 | 0.021181 | -0.06719 | 0.1208 | 0.14229 | 0.23353 | 0.079232 | -122.318 | 122.0327 | 122.3036 | 122.2152 | 0.55895 | -122.3779
3016.4219 | 122.406 | -0.064087 | 122.2549 | -0.01778 | -0.048401 | 0.039866 | 0.020751 | -0.012719 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.058473 | 0.044534 | 0.048115 | -0.017266 | 0.028878 | -0.012988 | 0.070441 | 0.087359 | 0.1786 | -0.081373 | 0.088043 | 0.52233 | -0.033458 | 121.9778 | 122.2441 | 122.1649 | -0.14125 | -0.017286 | -122.1845 | 0.046821 | 0.051099 | 0.068385 | -122.1676 | -122.0763 | -0.077168 | -0.27716 | 0.15213 | 0.030629 | 0.1078 | -0.010865 | -0.090078 | 0.13453 | 0.15145 | 0.24268 | 0.092965 | -122.3363 | 122.0419 | 122.3082 | 122.229 | 0.58642 | -122.3962
3018.125 | 122.4747 | -0.045776 | 122.2458 | -0.01778 | -0.047974 | 0.04008 | 0.020751 | -0.012719 | -0.0033715 | -0.013887 | -0.002694 | -0.0025041 | 0.058473 | 0.044961 | 0.048115 | -0.008109 | 0.028878 | -0.012988 | 0.065863 | 0.087359 | 0.17402 | -0.081373 | 0.088043 | 0.51775 | -0.028879 | 121.9778 | 122.2532 | 122.1603 | -0.14125 | -0.035597 | -122.1799 | 0.037667 | 0.032788 | 0.068385 | -122.1584 | -122.0718 | -0.095479 | -0.268 | 0.13382 | 0.016897 | 0.11238 | 0.007448 | -0.085502 | 0.11164 | 0.13314 | 0.21979 | 0.074654 | -122.3272 | 122.0236 | 122.299 | 122.2061 | 0.56353 | -122.387
3019.8906 | 122.3694 | -0.086975 | 122.2504 | -0.010149 | -0.047974 | 0.040293 | 0.020751 | -0.013147 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.058046 | 0.044534 | 0.048542 | -0.017266 | 0.019721 | -0.008409 | 0.070441 | 0.08278 | 0.18317 | -0.076794 | 0.092622 | 0.51317 | -0.038036 | 121.9824 | 122.2487 | 122.1603 | -0.15041 | 0.010181 | -122.1799 | 0.069709 | 0.078566 | 0.068385 | -122.1676 | -122.0672 | -0.063437 | -0.268 | 0.1796 | 0.048939 | 0.11238 | -0.001708 | -0.090079 | 0.15742 | 0.16975 | 0.27015 | 0.1067 | -122.3272 | 122.0693 | 122.3356 | 122.2473 | 0.60015 | -122.4008
3021.6406 | 122.3648 | -0.086975 | 122.2458 | 0.0051128 | -0.048188 | 0.040293 | 0.020537 | -0.012506 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.058046 | 0.044747 | 0.048115 | -0.008109 | 0.0243 | -0.008409 | 0.065863 | 0.087359 | 0.1786 | -0.076794 | 0.092622 | 0.51317 | -0.033458 | 121.9869 | 122.2532 | 122.1603 | -0.14583 | 0.010181 | -122.1799 | 0.078866 | 0.078566 | 0.068385 | -122.1584 | -122.0672 | -0.058858 | -0.25885 | 0.1796 | 0.053517 | 0.11237 | 0.007448 | -0.085502 | 0.15284 | 0.17433 | 0.26557 | 0.11127 | -122.3226 | 122.0739 | 122.3402 | 122.2473 | 0.60015 | -122.3916
3023.3281 | 122.319 | -0.11444 | 122.2549 | -0.010149 | -0.048188 | 0.039866 | 0.020751 | -0.012719 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.044747 | 0.048115 | -0.012688 | 0.0243 | -0.017566 | 0.070441 | 0.08278 | 0.18317 | -0.081373 | 0.078886 | 0.51317 | -0.033458 | 121.9824 | 122.2532 | 122.1649 | -0.14583 | 0.033068 | -122.1845 | 0.10175 | 0.096875 | 0.063807 | -122.1722 | -122.0718 | -0.031392 | -0.27258 | 0.19333 | 0.080983 | 0.11237 | -0.001707 | -0.090078 | 0.18488 | 0.19722 | 0.29761 | 0.13874 | -122.3363 | 122.0968 | 122.3677 | 122.2793 | 0.62762 | -122.4008
3025.1094 | 122.3465 | -0.091553 | 122.2412 | -0.010149 | -0.048188 | 0.04008 | 0.020537 | -0.012506 | -0.0031579 | -0.021518 | -0.0022666 | -0.0025041 | 0.05826 | 0.044747 | 0.047901 | -0.021844 | 0.0243 | -0.012988 | 0.065863 | 0.078201 | 0.18317 | -0.076794 | 0.092622 | 0.51317 | -0.033458 | 121.9824 | 122.2487 | 122.1649 | -0.13668 | 0.014759 | -122.1753 | 0.069709 | 0.078565 | 0.063806 | -122.163 | -122.058 | -0.045123 | -0.25885 | 0.18417 | 0.058095 | 0.10322 | 0.007447 | -0.076345 | 0.15742 | 0.16975 | 0.27473 | 0.11585 | -122.318 | 122.0739 | 122.3402 | 122.2564 | 0.60473 | -122.3779
3026.875 | 122.3373 | -0.1236 | 122.2366 | -0.0025182 | -0.048188 | 0.039866 | 0.020751 | -0.012933 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.058046 | 0.044534 | 0.048542 | -0.012688 | 0.019721 | -0.017566 | 0.07502 | 0.078201 | 0.18775 | -0.081373 | 0.083464 | 0.51317 | -0.033458 | 121.9824 | 122.2487 | 122.1603 | -0.14583 | 0.042223 | -122.1616 | 0.11091 | 0.10603 | 0.063807 | -122.1584 | -122.0489 | -0.022237 | -0.25427 | 0.20706 | 0.090138 | 0.11237 | 0.012025 | -0.076346 | 0.19862 | 0.2018 | 0.31135 | 0.14332 | -122.318 | 122.106 | 122.3723 | 122.2839 | 0.63677 | -122.3825
3028.6406 | 122.4289 | -0.064087 | 122.2092 | -0.025411 | -0.048401 | 0.039866 | 0.020751 | -0.012506 | -0.0031579 | -0.029148 | -0.0022666 | -0.0025041 | 0.058046 | 0.044747 | 0.048542 | -0.012688 | 0.015142 | -0.017566 | 0.07502 | 0.078201 | 0.18775 | -0.076794 | 0.088043 | 0.5086 | -0.028879 | 121.9869 | 122.2532 | 122.1603 | -0.14583 | -0.012707 | -122.1341 | 0.051399 | 0.046521 | 0.059228 | -122.131 | -122.0214 | -0.081746 | -0.22222 | 0.15213 | 0.035208 | 0.11695 | 0.04407 | -0.04888 | 0.13911 | 0.14229 | 0.25184 | 0.079229 | -122.286 | 122.051 | 122.3173 | 122.2244 | 0.57268 | -122.355
3030.3281 | 122.4197 | -0.082397 | 122.2275 | -0.01778 | -0.048615 | 0.039866 | 0.020965 | -0.012506 | -0.0031579 | -0.029148 | -0.0024804 | -0.0025041 | 0.058046 | 0.044747 | 0.047901 | -0.017266 | 0.0243 | -0.003831 | 0.070441 | 0.078201 | 0.1786 | -0.076794 | 0.083464 | 0.5086 | -0.038036 | 121.9824 | 122.2532 | 122.1649 | -0.15041 | 0.005603 | -122.157 | 0.065131 | 0.078566 | 0.072963 | -122.1493 | -122.0489 | -0.068015 | -0.24511 | 0.16586 | 0.044361 | 0.11238 | 0.025759 | -0.062612 | 0.15284 | 0.1606 | 0.26099 | 0.1067 | -122.3043 | 122.0648 | 122.3356 | 122.2473 | 0.59099 | -122.3779
3032.0938 | 122.3373 | -0.10529 | 122.2504 | -0.010149 | -0.048188 | 0.04008 | 0.020537 | -0.012292 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.058687 | 0.044747 | 0.048328 | -0.012688 | 0.0243 | -0.008409 | 0.07502 | 0.08278 | 0.1786 | -0.076794 | 0.092622 | 0.51775 | -0.028879 | 121.9915 | 122.2441 | 122.1649 | -0.15041 | 0.028492 | -122.1753 | 0.092598 | 0.096877 | 0.068385 | -122.1676 | -122.0718 | -0.045126 | -0.25884 | 0.19791 | 0.076407 | 0.12153 | -0.006287 | -0.0855 | 0.18031 | 0.18807 | 0.28388 | 0.12959 | -122.3272 | 122.0968 | 122.3494 | 122.2702 | 0.62304 | -122.4008
3033.7812 | 122.3099 | -0.082397 | 122.2321 | -0.010149 | -0.048188 | 0.04008 | 0.020323 | -0.012078 | -0.0033715 | -0.021518 | -0.002053 | -0.0025041 | 0.058473 | 0.044534 | 0.048115 | -0.017266 | 0.019721 | -0.008409 | 0.07502 | 0.087359 | 0.18775 | -0.081373 | 0.092622 | 0.50402 | -0.028879 | 121.9824 | 122.2532 | 122.1694 | -0.15041 | 0.001024 | -122.157 | 0.065131 | 0.073988 | 0.072964 | -122.1447 | -122.0443 | -0.068015 | -0.24969 | 0.17502 | 0.053518 | 0.12153 | 0.021181 | -0.062612 | 0.15742 | 0.16976 | 0.27015 | 0.10212 | -122.3134 | 122.0648 | 122.3356 | 122.2518 | 0.58641 | -122.3825
3035.5469 | 122.3373 | -0.10529 | 122.2595 | -0.0025182 | -0.048188 | 0.039866 | 0.020751 | -0.012506 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.044747 | 0.048328 | -0.012688 | 0.015142 | -0.008409 | 0.07502 | 0.08278 | 0.18317 | -0.076794 | 0.092622 | 0.51775 | -0.038036 | 121.9824 | 122.2532 | 122.1694 | -0.14583 | 0.028492 | -122.1845 | 0.092598 | 0.096877 | 0.068385 | -122.1767 | -122.0763 | -0.040547 | -0.27716 | 0.19791 | 0.06725 | 0.1078 | -0.006284 | -0.090077 | 0.18031 | 0.18807 | 0.28846 | 0.12043 | -122.3363 | 122.0877 | 122.3585 | 122.2747 | 0.62304 | -122.4054
3037.2969 | 122.4106 | -0.050354 | 122.2275 | -0.01778 | -0.048188 | 0.04008 | 0.020537 | -0.012933 | -0.0033715 | -0.021518 | -0.0024804 | -0.0018631 | 0.05826 | 0.044747 | 0.047901 | -0.021844 | 0.0243 | -0.017566 | 0.070441 | 0.08278 | 0.18317 | -0.081373 | 0.078886 | 0.5086 | -0.038036 | 121.9869 | 122.2532 | 122.1694 | -0.14583 | -0.031019 | -122.157 | 0.02851 | 0.032788 | 0.063807 | -122.1447 | -122.0443 | -0.095479 | -0.24054 | 0.12924 | 0.012318 | 0.1078 | 0.025759 | -0.058034 | 0.1208 | 0.13313 | 0.23353 | 0.074654 | -122.3089 | 122.0373 | 122.3036 | 122.2198 | 0.55895 | -122.3733
3039.0625 | 122.406 | -0.054932 | 122.2183 | -0.01778 | -0.048188 | 0.04008 | 0.020323 | -0.012719 | -0.0031579 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.044747 | 0.048328 | -0.017266 | 0.0243 | -0.012988 | 0.07502 | 0.078201 | 0.18317 | -0.081373 | 0.092622 | 0.51317 | -0.038036 | 121.9824 | 122.2441 | 122.1649 | -0.15041 | -0.026441 | -122.1433 | 0.037666 | 0.041944 | 0.068385 | -122.1401 | -122.0352 | -0.09548 | -0.23596 | 0.14755 | 0.016896 | 0.11238 | 0.025756 | -0.053457 | 0.12995 | 0.13313 | 0.23811 | 0.079232 | -122.2997 | 122.0373 | 122.299 | 122.2198 | 0.56811 | -122.3687
3040.7656 | 122.3099 | -0.10986 | 122.2504 | -0.010149 | -0.048188 | 0.039866 | 0.020537 | -0.012506 | -0.0029443 | -0.021518 | -0.0024804 | -0.0025041 | 0.058473 | 0.044534 | 0.048115 | -0.017266 | 0.019721 | -0.012988 | 0.070441 | 0.08278 | 0.1786 | -0.081373 | 0.088043 | 0.51775 | -0.033458 | 121.9915 | 122.2487 | 122.1649 | -0.14125 | 0.02849 | -122.1799 | 0.092597 | 0.096875 | 0.068385 | -122.1676 | -122.0718 | -0.031392 | -0.25884 | 0.19791 | 0.076405 | 0.1078 | -0.001708 | -0.0855 | 0.1803 | 0.19264 | 0.28846 | 0.12958 | -122.3317 | 122.1014 | 122.3585 | 122.2747 | 0.62762 | -122.3916
3042.5156 | 122.4289 | -0.064087 | 122.2183 | -0.01778 | -0.048401 | 0.039652 | 0.020751 | -0.012719 | -0.0029443 | -0.021518 | -0.0022666 | -0.0025041 | 0.05826 | 0.044534 | 0.048328 | -0.017266 | 0.015142 | -0.008409 | 0.070441 | 0.08278 | 0.18317 | -0.076794 | 0.083464 | 0.51317 | -0.033458 | 121.9824 | 122.2578 | 122.1694 | -0.14583 | -0.012707 | -122.1479 | 0.046821 | 0.055678 | 0.068385 | -122.1355 | -122.0352 | -0.081746 | -0.23596 | 0.14755 | 0.030629 | 0.11237 | 0.039492 | -0.048879 | 0.13453 | 0.14687 | 0.24726 | 0.079229 | -122.2951 | 122.0465 | 122.3219 | 122.2335 | 0.57726 | -122.3642
3044.2031 | 122.3145 | -0.091553 | 122.2733 | -0.01778 | -0.048401 | 0.039866 | 0.020751 | -0.012506 | -0.0031579 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058473 | 0.044747 | 0.047901 | -0.012688 | 0.0243 | -0.012988 | 0.065863 | 0.087359 | 0.17402 | -0.081373 | 0.083464 | 0.52233 | -0.033458 | 121.9824 | 122.2487 | 122.1649 | -0.14125 | 0.01018 | -122.2074 | 0.078865 | 0.078565 | 0.068385 | -122.1859 | -122.0992 | -0.049702 | -0.29089 | 0.17502 | 0.058095 | 0.1078 | -0.024596 | -0.10839 | 0.15742 | 0.17891 | 0.26557 | 0.11585 | -122.3546 | 122.0739 | 122.3402 | 122.2564 | 0.61389 | -122.4145
3045.9688 | 122.3328 | -0.091553 | 122.2824 | 0.0051128 | -0.04776 | 0.04008 | 0.020537 | -0.012292 | -0.0031579 | -0.029148 | -0.0022666 | -0.0025041 | 0.05826 | 0.045388 | 0.048115 | -0.017266 | 0.015142 | -0.017566 | 0.065863 | 0.078201 | 0.18317 | -0.085952 | 0.078886 | 0.51317 | -0.028879 | 121.9915 | 122.2532 | 122.1649 | -0.14583 | 0.005601 | -122.2165 | 0.074287 | 0.073987 | 0.068386 | -122.2042 | -122.0992 | -0.05428 | -0.29089 | 0.17044 | 0.062674 | 0.11695 | -0.029173 | -0.11754 | 0.15742 | 0.16975 | 0.27473 | 0.10669 | -122.3684 | 122.0831 | 122.3448 | 122.2564 | 0.60473 | -122.4282
3047.6562 | 122.3373 | -0.10529 | 122.2733 | -0.01778 | -0.048401 | 0.039866 | 0.020323 | -0.012719 | -0.0031579 | -0.013887 | -0.0022666 | -0.0020767 | 0.058046 | 0.044961 | 0.048115 | -0.017266 | 0.019721 | -0.003831 | 0.065863 | 0.078201 | 0.18775 | -0.076794 | 0.083464 | 0.52233 | -0.028879 | 121.9824 | 122.2487 | 122.1649 | -0.15041 | 0.028492 | -122.2074 | 0.08802 | 0.10146 | 0.072963 | -122.1951 | -122.0855 | -0.045126 | -0.29089 | 0.18875 | 0.076407 | 0.12153 | -0.024596 | -0.10839 | 0.17115 | 0.18349 | 0.29304 | 0.12501 | -122.35 | 122.0877 | 122.3539 | 122.2702 | 0.62762 | -122.4237
3049.4062 | 122.3145 | -0.10986 | 122.2412 | -0.01778 | -0.048401 | 0.04008 | 0.020537 | -0.012506 | -0.0033715 | -0.013887 | -0.002053 | -0.0022903 | 0.058473 | 0.044961 | 0.048115 | -0.017266 | 0.019721 | -0.017566 | 0.079598 | 0.078201 | 0.18317 | -0.081373 | 0.088043 | 0.51317 | -0.0243 | 121.9824 | 122.2578 | 122.1786 | -0.14583 | 0.02849 | -122.1616 | 0.092597 | 0.092297 | 0.063807 | -122.163 | -122.058 | -0.03597 | -0.25885 | 0.19791 | 0.085563 | 0.12153 | 0.016604 | -0.062609 | 0.18946 | 0.18806 | 0.29304 | 0.12958 | -122.3226 | 122.0922 | 122.3677 | 122.2885 | 0.62304 | -122.387
3051.1719 | 122.3099 | -0.086975 | 122.2778 | -0.01778 | -0.048188 | 0.039652 | 0.020751 | -0.012506 | -0.0031579 | -0.029148 | -0.0024804 | -0.0022903 | 0.058046 | 0.044747 | 0.048115 | -0.017266 | 0.0243 | -0.008409 | 0.070441 | 0.087359 | 0.18775 | -0.072215 | 0.083464 | 0.51775 | -0.033458 | 121.9869 | 122.2487 | 122.1649 | -0.15041 | 0.01476 | -122.2074 | 0.069709 | 0.078566 | 0.063806 | -122.1905 | -122.0901 | -0.063437 | -0.29089 | 0.17044 | 0.053517 | 0.11695 | -0.029174 | -0.11297 | 0.15742 | 0.17433 | 0.27473 | 0.11127 | -122.35 | 122.0739 | 122.3356 | 122.2518 | 0.60473 | -122.4282
3052.9219 | 122.3145 | -0.091553 | 122.2641 | -0.010149 | -0.048401 | 0.039866 | 0.020537 | -0.012719 | -0.0031579 | -0.021518 | -0.0024804 | -0.0025041 | 0.05826 | 0.044747 | 0.048115 | -0.012688 | 0.019721 | -0.012988 | 0.070441 | 0.08278 | 0.18317 | -0.072215 | 0.092622 | 0.51775 | -0.038036 | 121.9869 | 122.2487 | 122.1603 | -0.14583 | 0.019338 | -122.1937 | 0.078865 | 0.078565 | 0.059227 | -122.1813 | -122.0809 | -0.05428 | -0.27716 | 0.18417 | 0.053517 | 0.1078 | -0.015441 | -0.10381 | 0.16199 | 0.17433 | 0.27473 | 0.11127 | -122.3363 | 122.0785 | 122.3402 | 122.2518 | 0.60931 | -122.4099
3054.6875 | 122.3694 | -0.091553 | 122.2733 | -0.0025182 | -0.048401 | 0.04008 | 0.020751 | -0.012933 | -0.0027305 | -0.013887 | -0.0022666 | -0.0020767 | 0.05826 | 0.044747 | 0.048115 | -0.017266 | 0.019721 | -0.017566 | 0.070441 | 0.08278 | 0.18317 | -0.081373 | 0.083464 | 0.51775 | -0.028879 | 121.9869 | 122.2578 | 122.1603 | -0.14583 | 0.01018 | -122.2028 | 0.074287 | 0.073987 | 0.063807 | -122.1905 | -122.0901 | -0.05428 | -0.28631 | 0.17502 | 0.062674 | 0.11695 | -0.015439 | -0.11297 | 0.16199 | 0.17433 | 0.27473 | 0.11127 | -122.3546 | 122.0785 | 122.3494 | 122.2518 | 0.60931 | -122.4191
3056.375 | 122.3694 | -0.086975 | 122.2504 | -0.01778 | -0.048615 | 0.040507 | 0.020323 | -0.012506 | -0.0029443 | -0.021518 | -0.0024804 | -0.0027177 | 0.058046 | 0.044747 | 0.048115 | -0.017266 | 0.028878 | -0.008409 | 0.070441 | 0.087359 | 0.18317 | -0.076794 | 0.083464 | 0.51775 | -0.033458 | 121.9824 | 122.2578 | 122.1694 | -0.14125 | 0.010181 | -122.1799 | 0.069709 | 0.078566 | 0.068385 | -122.163 | -122.0672 | -0.05428 | -0.268 | 0.17044 | 0.053517 | 0.1078 | 0.007449 | -0.080922 | 0.15742 | 0.17433 | 0.27015 | 0.11585 | -122.3272 | 122.0693 | 122.3448 | 122.2564 | 0.60473 | -122.3916
3058.125 | 122.3373 | -0.12817 | 122.2778 | -0.010149 | -0.048829 | 0.040293 | 0.020323 | -0.012506 | -0.0027305 | -0.021518 | -0.002053 | -0.0022903 | 0.058473 | 0.044747 | 0.048542 | -0.012688 | 0.019721 | -0.003831 | 0.070441 | 0.087359 | 0.1786 | -0.085952 | 0.088043 | 0.52233 | -0.033458 | 121.9824 | 122.2441 | 122.1603 | -0.14583 | 0.042222 | -122.2074 | 0.11549 | 0.12434 | 0.082121 | -122.1905 | -122.0992 | -0.017659 | -0.29547 | 0.21622 | 0.094716 | 0.11237 | -0.033753 | -0.11755 | 0.19862 | 0.21553 | 0.30677 | 0.14789 | -122.3638 | 122.1105 | 122.3723 | 122.2885 | 0.65051 | -122.4237
3059.8281 | 122.4655 | -0.027466 | 122.2321 | -0.01778 | -0.048615 | 0.040293 | 0.020537 | -0.012506 | -0.0029443 | -0.021518 | -0.002053 | -0.0022903 | 0.058046 | 0.044747 | 0.048115 | -0.012688 | 0.0243 | -0.012988 | 0.07502 | 0.08278 | 0.1786 | -0.076794 | 0.083464 | 0.52233 | -0.028879 | 121.9869 | 122.2578 | 122.1694 | -0.14583 | -0.049328 | -122.157 | 0.014778 | 0.014478 | 0.063806 | -122.1493 | -122.0535 | -0.11837 | -0.24511 | 0.11093 | -0.001413 | 0.11695 | 0.025759 | -0.062612 | 0.10249 | 0.11025 | 0.20606 | 0.051766 | -122.3089 | 122.0144 | 122.2853 | 122.1969 | 0.5498 | -122.3779
3061.5781 | 122.4426 | -0.050354 | 122.2137 | -0.010149 | -0.048829 | 0.040507 | 0.020323 | -0.012719 | -0.0027305 | -0.029148 | -0.0022666 | -0.0022903 | 0.058046 | 0.044747 | 0.048328 | -0.021844 | 0.0243 | -0.008409 | 0.065863 | 0.078201 | 0.17402 | -0.076794 | 0.083464 | 0.51775 | -0.033458 | 121.9915 | 122.2487 | 122.1649 | -0.15041 | -0.02644 | -122.1479 | 0.02851 | 0.041945 | 0.068385 | -122.1355 | -122.0397 | -0.10006 | -0.22222 | 0.13382 | 0.016896 | 0.11695 | 0.034913 | -0.048879 | 0.11622 | 0.12856 | 0.22437 | 0.074654 | -122.2905 | 122.0419 | 122.299 | 122.2152 | 0.56811 | -122.3642
3063.3438 | 122.3053 | -0.09613 | 122.2641 | -0.010149 | -0.048829 | 0.040507 | 0.020323 | -0.012506 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.05826 | 0.045175 | 0.048115 | -0.017266 | 0.028878 | -0.008409 | 0.065863 | 0.087359 | 0.18317 | -0.081373 | 0.083464 | 0.52233 | -0.028879 | 121.9869 | 122.2624 | 122.1649 | -0.14583 | 0.014757 | -122.1982 | 0.078864 | 0.087721 | 0.072964 | -122.1767 | -122.0809 | -0.049703 | -0.27716 | 0.17959 | 0.067251 | 0.11695 | -0.001705 | -0.099233 | 0.16199 | 0.18349 | 0.2793 | 0.12501 | -122.3455 | 122.0831 | 122.3585 | 122.261 | 0.61846 | -122.4099
3065.0469 | 122.4426 | -0.059509 | 122.2412 | -0.01778 | -0.048401 | 0.040293 | 0.020323 | -0.012506 | -0.0029443 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.045175 | 0.047901 | -0.017266 | 0.028878 | -0.012988 | 0.07502 | 0.08278 | 0.1786 | -0.076794 | 0.088043 | 0.51775 | -0.033458 | 121.9824 | 122.2578 | 122.1694 | -0.15041 | -0.017285 | -122.1662 | 0.042243 | 0.046521 | 0.063806 | -122.1584 | -122.0626 | -0.090903 | -0.25885 | 0.14755 | 0.026051 | 0.11695 | 0.016604 | -0.071767 | 0.13453 | 0.14229 | 0.2381 | 0.088387 | -122.318 | 122.0419 | 122.3173 | 122.229 | 0.57726 | -122.3916
3066.7969 | 122.374 | -0.07782 | 122.2321 | -0.010149 | -0.048615 | 0.040293 | 0.020537 | -0.012719 | -0.0033715 | -0.021518 | -0.002694 | -0.0020767 | 0.05826 | 0.044747 | 0.048328 | -0.017266 | 0.019721 | -0.017566 | 0.07502 | 0.087359 | 0.1786 | -0.076794 | 0.088043 | 0.51317 | -0.033458 | 121.9869 | 122.2578 | 122.1557 | -0.14583 | 0.001026 | -122.157 | 0.060554 | 0.060254 | 0.059228 | -122.1447 | -122.0535 | -0.068013 | -0.24511 | 0.16586 | 0.044362 | 0.11237 | 0.025759 | -0.076347 | 0.15284 | 0.16518 | 0.25642 | 0.097541 | -122.3089 | 122.0648 | 122.3356 | 122.2335 | 0.59099 | -122.3779
3068.5625 | 122.3099 | -0.09613 | 122.3007 | -0.010149 | -0.049042 | 0.040507 | 0.02011 | -0.012719 | -0.0029443 | -0.021518 | -0.0024804 | -0.0022903 | 0.05826 | 0.044961 | 0.048328 | -0.021844 | 0.0243 | -0.012988 | 0.070441 | 0.087359 | 0.18317 | -0.081373 | 0.078886 | 0.51317 | -0.033458 | 121.9824 | 122.2532 | 122.1694 | -0.15041 | 0.014757 | -122.2303 | 0.074286 | 0.083142 | 0.068385 | -122.2134 | -122.1175 | -0.054282 | -0.31836 | 0.17502 | 0.062672 | 0.11695 | -0.047483 | -0.13128 | 0.16657 | 0.18349 | 0.2793 | 0.12043 | -122.3821 | 122.0785 | 122.3494 | 122.2656 | 0.6093 | -122.4511
3070.3281 | 122.3511 | -0.10986 | 122.2641 | -0.010149 | -0.048829 | 0.040507 | 0.020751 | -0.012719 | -0.0033715 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.044961 | 0.048115 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.087359 | 0.1786 | -0.081373 | 0.083464 | 0.51317 | -0.033458 | 121.9824 | 122.2624 | 122.1694 | -0.14583 | 0.02849 | -122.1891 | 0.092597 | 0.096875 | 0.068385 | -122.1767 | -122.0855 | -0.03597 | -0.28173 | 0.19333 | 0.076405 | 0.11237 | -0.001705 | -0.094655 | 0.18488 | 0.19722 | 0.28846 | 0.12958 | -122.3455 | 122.0922 | 122.3723 | 122.2793 | 0.62304 | -122.4099
3072.0156 | 122.4289 | -0.050354 | 122.2092 | -0.010149 | -0.048615 | 0.040507 | 0.02011 | -0.012719 | -0.0031579 | -0.021518 | -0.0022666 | -0.0027177 | 0.05826 | 0.044747 | 0.048115 | -0.012688 | 0.0243 | -0.017566 | 0.07502 | 0.087359 | 0.1786 | -0.081373 | 0.083464 | 0.52233 | -0.033458 | 121.9869 | 122.2578 | 122.1649 | -0.14583 | -0.031019 | -122.1341 | 0.037666 | 0.032788 | 0.063807 | -122.1218 | -122.0306 | -0.095479 | -0.22222 | 0.13382 | 0.016896 | 0.11237 | 0.048648 | -0.044301 | 0.12537 | 0.13771 | 0.22895 | 0.074654 | -122.2905 | 122.0373 | 122.3082 | 122.2152 | 0.57269 | -122.355
3073.7656 | 122.3923 | -0.050354 | 122.2366 | -0.010149 | -0.048401 | 0.040293 | 0.020323 | -0.012719 | -0.0027305 | -0.013887 | -0.0024804 | -0.0025041 | 0.05826 | 0.045388 | 0.048328 | -0.021844 | 0.0243 | -0.012988 | 0.065863 | 0.091937 | 0.18775 | -0.085952 | 0.088043 | 0.52233 | -0.038036 | 121.9869 | 122.2487 | 122.1694 | -0.14583 | -0.035598 | -122.1708 | 0.02851 | 0.037366 | 0.072964 | -122.1447 | -122.0489 | -0.095479 | -0.24969 | 0.1384 | 0.012318 | 0.1078 | 0.012025 | -0.067189 | 0.11622 | 0.14229 | 0.23811 | 0.074654 | -122.3226 | 122.0373 | 122.299 | 122.2198 | 0.57269 | -122.3825
3075.5312 | 122.3648 | -0.082397 | 122.2916 | -0.0025182 | -0.048829 | 0.040507 | 0.020323 | -0.012719 | -0.0029443 | -0.013887 | -0.0022666 | -0.0020767 | 0.05826 | 0.044961 | 0.048328 | -0.026423 | 0.028878 | -0.008409 | 0.07502 | 0.087359 | 0.1786 | -0.081373 | 0.088043 | 0.52233 | -0.033458 | 121.9915 | 122.2624 | 122.1694 | -0.14583 | 0.001024 | -122.2165 | 0.055974 | 0.073988 | 0.072964 | -122.2042 | -122.113 | -0.063436 | -0.30004 | 0.17044 | 0.048939 | 0.11237 | -0.029171 | -0.12212 | 0.15742 | 0.16976 | 0.26099 | 0.11127 | -122.3729 | 122.0739 | 122.3448 | 122.2518 | 0.60473 | -122.4374
3077.2188 | 122.2916 | -0.10529 | 122.2641 | -0.010149 | -0.048401 | 0.040721 | 0.020323 | -0.012506 | -0.0031579 | -0.0062567 | -0.0024804 | -0.0020767 | 0.058473 | 0.045175 | 0.048328 | -0.021844 | 0.019721 | -0.008409 | 0.079598 | 0.078201 | 0.18775 | -0.081373 | 0.088043 | 0.51775 | -0.038036 | 121.9869 | 122.2532 | 122.1694 | -0.14583 | 0.023913 | -122.1845 | 0.083442 | 0.096877 | 0.072964 | -122.1859 | -122.0763 | -0.040547 | -0.27716 | 0.19333 | 0.06725 | 0.1078 | -0.010862 | -0.094655 | 0.18488 | 0.18349 | 0.29304 | 0.12501 | -122.3455 | 122.0922 | 122.3585 | 122.2747 | 0.62304 | -122.4099
3078.9844 | 122.3282 | -0.086975 | 122.2961 | -0.025411 | -0.049256 | 0.040507 | 0.020323 | -0.012292 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.044747 | 0.048115 | -0.012688 | 0.0243 | -0.008409 | 0.070441 | 0.08278 | 0.18317 | -0.081373 | 0.088043 | 0.52233 | -0.038036 | 121.9869 | 122.2624 | 122.174 | -0.14583 | 0.005602 | -122.2257 | 0.074287 | 0.078566 | 0.072964 | -122.2134 | -122.113 | -0.058858 | -0.3092 | 0.17502 | 0.048939 | 0.1078 | -0.033749 | -0.12212 | 0.15742 | 0.16975 | 0.27015 | 0.11127 | -122.3775 | 122.0739 | 122.3494 | 122.261 | 0.60931 | -122.442
3080.75 | 122.4289 | -0.059509 | 122.2275 | -0.010149 | -0.049042 | 0.040721 | 0.020537 | -0.012719 | -0.0031579 | -0.0062567 | -0.0022666 | -0.0020767 | 0.05826 | 0.044747 | 0.047901 | -0.017266 | 0.019721 | -0.012988 | 0.065863 | 0.091937 | 0.18317 | -0.081373 | 0.083464 | 0.51775 | -0.033458 | 121.9869 | 122.2532 | 122.1649 | -0.15499 | -0.021864 | -122.1616 | 0.042243 | 0.046521 | 0.068385 | -122.1355 | -122.0443 | -0.095482 | -0.24054 | 0.14297 | 0.026051 | 0.12153 | 0.025759 | -0.062612 | 0.12537 | 0.15145 | 0.24268 | 0.07923 | -122.3089 | 122.0465 | 122.3127 | 122.2244 | 0.57726 | -122.3825
3082.4375 | 122.3328 | -0.10529 | 122.2504 | -0.010149 | -0.048829 | 0.040721 | 0.020323 | -0.012719 | -0.0027305 | -0.021518 | -0.0022666 | -0.0025041 | 0.058473 | 0.044961 | 0.048115 | -0.021844 | 0.0243 | -0.012988 | 0.07502 | 0.078201 | 0.18775 | -0.076794 | 0.083464 | 0.52233 | -0.028879 | 121.9869 | 122.2578 | 122.1649 | -0.14583 | 0.028492 | -122.1753 | 0.083442 | 0.092298 | 0.063806 | -122.1722 | -122.0626 | -0.040547 | -0.26342 | 0.18875 | 0.076407 | 0.11695 | 0.007449 | -0.0855 | 0.18031 | 0.18349 | 0.29304 | 0.12959 | -122.3272 | 122.0922 | 122.3631 | 122.2702 | 0.62762 | -122.3962
3084.1875 | 122.4335 | -0.07782 | 122.2412 | -0.010149 | -0.048401 | 0.040507 | 0.020323 | -0.012933 | -0.0031579 | -0.013887 | -0.0022666 | -0.0020767 | 0.058473 | 0.044961 | 0.048115 | -0.021844 | 0.015142 | -0.012988 | 0.070441 | 0.087359 | 0.1786 | -0.081373 | 0.092622 | 0.52233 | -0.033458 | 121.9824 | 122.2532 | 122.1649 | -0.15041 | -0.003553 | -122.1708 | 0.055976 | 0.064832 | 0.068385 | -122.1539 | -122.0626 | -0.072592 | -0.25885 | 0.17044 | 0.044362 | 0.11695 | 0.012026 | -0.076345 | 0.14826 | 0.16518 | 0.25642 | 0.092962 | -122.3226 | 122.0602 | 122.3311 | 122.2427 | 0.60015 | -122.3916
3085.8906 | 122.4472 | -0.036621 | 122.2137 | -0.01778 | -0.048829 | 0.040293 | 0.020323 | -0.012506 | -0.0033715 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.044961 | 0.047901 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.08278 | 0.18317 | -0.076794 | 0.078886 | 0.52233 | -0.038036 | 121.9869 | 122.2624 | 122.1649 | -0.14583 | -0.040173 | -122.1387 | 0.019355 | 0.023633 | 0.063806 | -122.131 | -122.0306 | -0.10921 | -0.2268 | 0.11551 | -0.001415 | 0.1078 | 0.048649 | -0.048879 | 0.11164 | 0.1194 | 0.21979 | 0.051763 | -122.2905 | 122.0236 | 122.299 | 122.2015 | 0.55895 | -122.3596
3087.6562 | 122.4289 | -0.064087 | 122.2504 | -0.010149 | -0.048829 | 0.040507 | 0.020323 | -0.012719 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.044961 | 0.048115 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.087359 | 0.18317 | -0.081373 | 0.083464 | 0.51775 | -0.033458 | 121.9869 | 122.2532 | 122.1694 | -0.14583 | -0.017286 | -122.1753 | 0.046821 | 0.051099 | 0.068385 | -122.163 | -122.0672 | -0.081746 | -0.26342 | 0.14755 | 0.030629 | 0.11237 | 0.002871 | -0.080922 | 0.13911 | 0.15145 | 0.24726 | 0.083808 | -122.3317 | 122.051 | 122.3173 | 122.2335 | 0.58184 | -122.3962
3089.3594 | 122.4335 | -0.041199 | 122.2321 | -0.010149 | -0.049042 | 0.04008 | 0.020751 | -0.012719 | -0.0029443 | -0.021518 | -0.0018394 | -0.0025041 | 0.05826 | 0.045175 | 0.048115 | -0.021844 | 0.0243 | -0.012988 | 0.07502 | 0.087359 | 0.18775 | -0.081373 | 0.078886 | 0.51317 | -0.038036 | 121.9915 | 122.2532 | 122.1694 | -0.14583 | -0.040174 | -122.157 | 0.019355 | 0.028211 | 0.068385 | -122.1447 | -122.0443 | -0.10463 | -0.24053 | 0.12008 | 0.003163 | 0.1078 | 0.021181 | -0.062612 | 0.11622 | 0.12856 | 0.22895 | 0.065499 | -122.3134 | 122.0327 | 122.2944 | 122.2106 | 0.55437 | -122.3779
3091.125 | 122.4838 | -0.050354 | 122.2229 | -0.01778 | -0.049042 | 0.040507 | 0.020323 | -0.012933 | -0.0025169 | -0.013887 | -0.002053 | -0.0027177 | 0.058046 | 0.044961 | 0.048115 | -0.021844 | 0.0243 | -0.012988 | 0.07502 | 0.091937 | 0.1786 | -0.076794 | 0.083464 | 0.51775 | -0.038036 | 121.9869 | 122.2578 | 122.1694 | -0.15041 | -0.02644 | -122.1479 | 0.02851 | 0.037366 | 0.063806 | -122.131 | -122.0443 | -0.10006 | -0.23596 | 0.13382 | 0.012318 | 0.11238 | 0.034915 | -0.053456 | 0.12537 | 0.14229 | 0.22895 | 0.074654 | -122.2997 | 122.0373 | 122.3082 | 122.2198 | 0.56811 | -122.3733
3092.8906 | 122.4335 | -0.064087 | 122.2412 | -0.010149 | -0.048829 | 0.040507 | 0.02011 | -0.012506 | -0.0027305 | -0.021518 | -0.0022666 | -0.0025041 | 0.058687 | 0.044747 | 0.047901 | -0.017266 | 0.028878 | -0.012988 | 0.07502 | 0.087359 | 0.19233 | -0.085952 | 0.088043 | 0.52691 | -0.028879 | 121.9869 | 122.2578 | 122.1603 | -0.14583 | -0.021865 | -122.1662 | 0.046821 | 0.051099 | 0.072964 | -122.1539 | -122.0489 | -0.081746 | -0.25427 | 0.15213 | 0.035208 | 0.11695 | 0.016604 | -0.080924 | 0.13911 | 0.15145 | 0.25642 | 0.092965 | -122.3272 | 122.051 | 122.3219 | 122.2244 | 0.591 | -122.387
3094.6875 | 122.4106 | -0.059509 | 122.2366 | -0.010149 | -0.048829 | 0.040507 | 0.019896 | -0.012506 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.045175 | 0.048115 | 0.14756 | 0.038035 | -0.003831 | 0.084176 | 0.087359 | 0.18317 | -0.076794 | 0.092622 | 0.53149 | -0.033458 | 122.0007 | 122.2532 | 122.1603 | -0.15041 | -0.017285 | -122.1525 | 0.20706 | 0.055678 | 0.072963 | -122.1493 | -122.0535 | -0.090903 | -0.23596 | 0.15213 | 0.026051 | 0.11695 | 0.016604 | -0.076346 | 0.14369 | 0.14687 | 0.24268 | 0.097544 | -122.3134 | 122.0602 | 122.3127 | 122.2198 | 0.591 | -122.387
3096.3906 | 122.3419 | -0.09613 | 122.2366 | -0.010149 | -0.049256 | 0.040293 | 0.020537 | -0.012933 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.044961 | 0.047901 | -0.012688 | 0.028878 | -0.012988 | 0.07502 | 0.08278 | 0.19233 | -0.072215 | 0.092622 | 0.52691 | -0.028879 | 121.9869 | 122.2624 | 122.1786 | -0.15041 | 0.023915 | -122.1616 | 0.083442 | 0.083142 | 0.059227 | -122.1539 | -122.0443 | -0.054282 | -0.24969 | 0.18875 | 0.067251 | 0.12153 | 0.025761 | -0.058031 | 0.17115 | 0.17891 | 0.28846 | 0.12501 | -122.3088 | 122.0831 | 122.3585 | 122.2747 | 0.62304 | -122.387
3098.1562 | 122.4655 | -0.064087 | 122.2229 | -0.010149 | -0.048829 | 0.040507 | 0.020323 | -0.012506 | -0.0029443 | -0.021518 | -0.0022666 | -0.0020767 | 0.05826 | 0.045175 | 0.047687 | -0.012688 | 0.019721 | -0.012988 | 0.07502 | 0.08278 | 0.18775 | -0.076794 | 0.074307 | 0.51775 | -0.028879 | 121.9869 | 122.2578 | 122.1649 | -0.14125 | -0.012707 | -122.1479 | 0.051399 | 0.051099 | 0.063806 | -122.1401 | -122.0351 | -0.077168 | -0.23596 | 0.13839 | 0.035208 | 0.11238 | 0.034915 | -0.058034 | 0.13911 | 0.14687 | 0.25184 | 0.083808 | -122.2997 | 122.051 | 122.3219 | 122.229 | 0.58184 | -122.3642
3099.8438 | 122.374 | -0.10071 | 122.2549 | -0.0025182 | -0.049042 | 0.040293 | 0.020537 | -0.012506 | -0.0029443 | -0.013887 | -0.0024804 | -0.0025041 | 0.05826 | 0.045388 | 0.048328 | -0.017266 | 0.015142 | -0.008409 | 0.070441 | 0.08278 | 0.18317 | -0.081373 | 0.088043 | 0.51775 | -0.028879 | 121.9961 | 122.2532 | 122.1694 | -0.15957 | 0.019335 | -122.1845 | 0.083442 | 0.092299 | 0.072964 | -122.1722 | -122.0718 | -0.058862 | -0.25884 | 0.18875 | 0.071829 | 0.13069 | -0.001707 | -0.0855 | 0.17115 | 0.18349 | 0.28388 | 0.11585 | -122.3363 | 122.0968 | 122.3539 | 122.2702 | 0.61846 | -122.4145
3101.625 | 122.4289 | -0.059509 | 122.2137 | -0.01778 | -0.049042 | 0.04008 | 0.020323 | -0.012506 | -0.0031579 | -0.021518 | -0.0022666 | -0.0018631 | 0.05826 | 0.045175 | 0.048328 | -0.017266 | 0.015142 | -0.012988 | 0.065863 | 0.08278 | 0.18775 | -0.076794 | 0.088043 | 0.52691 | -0.028879 | 121.9869 | 122.2578 | 122.1694 | -0.14583 | -0.017285 | -122.1479 | 0.042243 | 0.046521 | 0.063806 | -122.131 | -122.026 | -0.086324 | -0.2268 | 0.14755 | 0.03063 | 0.11695 | 0.04407 | -0.044301 | 0.12537 | 0.14229 | 0.24726 | 0.074651 | -122.2905 | 122.0465 | 122.3173 | 122.229 | 0.58642 | -122.3596
3103.3125 | 122.4472 | -0.054932 | 122.2366 | -0.0025182 | -0.048829 | 0.040293 | 0.02011 | -0.012719 | -0.0027305 | -0.013887 | -0.002053 | -0.0025041 | 0.05826 | 0.045175 | 0.048328 | -0.012688 | 0.028878 | -0.012988 | 0.07502 | 0.08278 | 0.18317 | -0.081373 | 0.088043 | 0.52233 | -0.038036 | 121.9869 | 122.2578 | 122.1694 | -0.15499 | -0.026441 | -122.1616 | 0.042244 | 0.041944 | 0.068385 | -122.1539 | -122.0535 | -0.10006 | -0.24969 | 0.14297 | 0.016896 | 0.11695 | 0.021182 | -0.067189 | 0.12995 | 0.13771 | 0.23811 | 0.08381 | -122.318 | 122.0419 | 122.3127 | 122.2244 | 0.57726 | -122.3916
3105.0625 | 122.3557 | -0.091553 | 122.2504 | -0.010149 | -0.049042 | 0.040293 | 0.019896 | -0.012719 | -0.0031579 | 0.0013733 | -0.0022666 | -0.0025041 | 0.058473 | 0.045175 | 0.048328 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.091937 | 0.18317 | -0.081373 | 0.088043 | 0.51317 | -0.033458 | 121.9961 | 122.2578 | 122.174 | -0.14583 | 0.01018 | -122.1662 | 0.069709 | 0.083144 | 0.072964 | -122.1584 | -122.0672 | -0.05428 | -0.25427 | 0.1796 | 0.058095 | 0.11237 | 0.007449 | -0.076343 | 0.17573 | 0.18349 | 0.27473 | 0.11585 | -122.3317 | 122.0877 | 122.3494 | 122.2656 | 0.60473 | -122.3962
3106.7656 | 122.3648 | -0.091553 | 122.2412 | -0.010149 | -0.04947 | 0.04008 | 0.020537 | -0.012719 | -0.0027305 | -0.013887 | -0.0022666 | -0.0022903 | 0.058046 | 0.044961 | 0.048115 | -0.012688 | 0.019721 | -0.008409 | 0.070441 | 0.078201 | 0.18317 | -0.076794 | 0.083464 | 0.51775 | -0.028879 | 121.9915 | 122.2578 | 122.1649 | -0.15041 | 0.014759 | -122.1708 | 0.078865 | 0.083144 | 0.068385 | -122.163 | -122.058 | -0.058859 | -0.24969 | 0.17502 | 0.062674 | 0.12153 | 0.016604 | -0.076345 | 0.16199 | 0.16975 | 0.27473 | 0.11127 | -122.318 | 122.0831 | 122.3494 | 122.2564 | 0.60931 | -122.3916
3108.5156 | 122.3282 | -0.10071 | 122.2595 | -0.0025182 | -0.048829 | 0.040293 | 0.020323 | -0.012719 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.057832 | 0.045175 | 0.048542 | -0.008109 | 0.015142 | -0.008409 | 0.065863 | 0.087359 | 0.18317 | -0.085952 | 0.092622 | 0.52233 | -0.033458 | 121.9869 | 122.2578 | 122.1694 | -0.15041 | 0.014756 | -122.1937 | 0.092599 | 0.092299 | 0.077543 | -122.1722 | -122.0763 | -0.049704 | -0.27258 | 0.19333 | 0.06725 | 0.11695 | -0.001706 | -0.090077 | 0.16657 | 0.18807 | 0.28388 | 0.11585 | -122.3455 | 122.0876 | 122.3585 | 122.2702 | 0.62304 | -122.4099
3110.2812 | 122.3465 | -0.10529 | 122.2412 | -0.025411 | -0.049256 | 0.040293 | 0.019896 | -0.012933 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.05826 | 0.044961 | 0.048328 | -0.017266 | 0.028878 | -0.003831 | 0.07502 | 0.08278 | 0.18317 | -0.076794 | 0.088043 | 0.52691 | -0.038036 | 121.9869 | 122.2532 | 122.1694 | -0.14583 | 0.028492 | -122.1662 | 0.08802 | 0.10146 | 0.072963 | -122.1584 | -122.058 | -0.040547 | -0.25427 | 0.19333 | 0.06725 | 0.1078 | 0.012026 | -0.071767 | 0.18031 | 0.18807 | 0.28846 | 0.13416 | -122.318 | 122.0922 | 122.3585 | 122.2747 | 0.6322 | -122.387
3112.0469 | 122.3923 | -0.086975 | 122.2687 | -0.01778 | -0.048829 | 0.040507 | 0.020323 | -0.012506 | -0.0031579 | -0.013887 | -0.002053 | -0.0018631 | 0.058046 | 0.045388 | 0.047901 | -0.017266 | 0.0243 | -0.017566 | 0.079598 | 0.087359 | 0.18775 | -0.076794 | 0.092622 | 0.52233 | -0.042615 | 121.9915 | 122.2624 | 122.1786 | -0.15499 | 0.010181 | -122.1891 | 0.069709 | 0.069409 | 0.059228 | -122.1813 | -122.0809 | -0.068016 | -0.27716 | 0.1796 | 0.04436 | 0.11238 | -0.006283 | -0.090075 | 0.16657 | 0.17433 | 0.27473 | 0.11127 | -122.3455 | 122.0785 | 122.3494 | 122.2656 | 0.60931 | -122.4237
3113.75 | 122.4243 | -0.054932 | 122.2412 | -0.0025182 | -0.049256 | 0.040721 | 0.019896 | -0.012506 | -0.0031579 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.045388 | 0.048115 | -0.021844 | 0.0243 | -0.008409 | 0.070441 | 0.091937 | 0.18775 | -0.081373 | 0.088043 | 0.51775 | -0.033458 | 121.9915 | 122.2624 | 122.1694 | -0.14583 | -0.026441 | -122.1708 | 0.033088 | 0.046523 | 0.072964 | -122.1493 | -122.0535 | -0.090901 | -0.24969 | 0.14297 | 0.021474 | 0.11237 | 0.021183 | -0.071767 | 0.12537 | 0.14687 | 0.24268 | 0.079232 | -122.3226 | 122.0465 | 122.3173 | 122.2244 | 0.57268 | -122.387
3115.5156 | 122.3785 | -0.10529 | 122.2595 | -0.025411 | -0.049256 | 0.040507 | 0.020323 | -0.012933 | -0.0023033 | -0.013887 | -0.0024804 | -0.0020767 | 0.058046 | 0.045175 | 0.048328 | -0.012688 | 0.0243 | -0.017566 | 0.065863 | 0.091937 | 0.18775 | -0.081373 | 0.092622 | 0.53149 | -0.033458 | 121.9961 | 122.2578 | 122.1694 | -0.15041 | 0.023913 | -122.1937 | 0.092598 | 0.08772 | 0.063807 | -122.1676 | -122.0718 | -0.045126 | -0.26342 | 0.19791 | 0.071828 | 0.11695 | -0.001706 | -0.090077 | 0.17115 | 0.19722 | 0.29304 | 0.12959 | -122.3409 | 122.1014 | 122.3631 | 122.2747 | 0.63677 | -122.4099
3117.2656 | 122.4609 | -0.068665 | 122.2092 | -0.01778 | -0.049256 | 0.040507 | 0.02011 | -0.012719 | -0.0027305 | -0.021518 | -0.0022666 | -0.0025041 | 0.05826 | 0.045175 | 0.048115 | -0.017266 | 0.019721 | -0.008409 | 0.079598 | 0.087359 | 0.1786 | -0.076794 | 0.078886 | 0.52233 | -0.042615 | 121.9961 | 122.2578 | 122.1649 | -0.15041 | -0.008129 | -122.1296 | 0.051399 | 0.060256 | 0.068385 | -122.1218 | -122.0306 | -0.081747 | -0.21307 | 0.14755 | 0.02605 | 0.1078 | 0.048648 | -0.044301 | 0.14826 | 0.15602 | 0.24726 | 0.088386 | -122.286 | 122.0648 | 122.3265 | 122.2335 | 0.591 | -122.3596
3119.0156 | 122.4243 | -0.045776 | 122.2321 | -0.010149 | -0.049256 | 0.040507 | 0.02011 | -0.012719 | -0.0029443 | -0.021518 | -0.0024804 | -0.0020767 | 0.05826 | 0.045388 | 0.048328 | -0.021844 | 0.019721 | -0.008409 | 0.070441 | 0.08278 | 0.18317 | -0.076794 | 0.088043 | 0.52691 | -0.033458 | 121.9915 | 122.2578 | 122.1694 | -0.15041 | -0.031018 | -122.1616 | 0.023932 | 0.037367 | 0.068385 | -122.1493 | -122.0489 | -0.10464 | -0.24053 | 0.13382 | 0.012318 | 0.11695 | 0.025759 | -0.062612 | 0.11622 | 0.12856 | 0.22895 | 0.065497 | -122.3089 | 122.0373 | 122.3036 | 122.2152 | 0.57269 | -122.3825
3120.7812 | 122.4106 | -0.059509 | 122.2321 | -0.01778 | -0.049256 | 0.040721 | 0.02011 | -0.012292 | -0.0029443 | -0.029148 | -0.0024804 | -0.0025041 | 0.058046 | 0.045175 | 0.047901 | -0.017266 | 0.028878 | -0.017566 | 0.07502 | 0.087359 | 0.18317 | -0.081373 | 0.078886 | 0.51775 | -0.033458 | 121.9869 | 122.2487 | 122.1649 | -0.14583 | -0.021864 | -122.157 | 0.042243 | 0.041943 | 0.063807 | -122.1447 | -122.0489 | -0.086324 | -0.24511 | 0.13839 | 0.026051 | 0.11237 | 0.016602 | -0.06719 | 0.13453 | 0.14687 | 0.24268 | 0.088387 | -122.3134 | 122.0465 | 122.3082 | 122.2244 | 0.57726 | -122.3779
3122.4688 | 122.3831 | -0.09613 | 122.2595 | -0.01778 | -0.049042 | 0.040507 | 0.02011 | -0.012933 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.045388 | 0.048542 | -0.017266 | 0.0243 | -0.017566 | 0.07502 | 0.087359 | 0.18317 | -0.081373 | 0.088043 | 0.52691 | -0.033458 | 121.9915 | 122.2624 | 122.174 | -0.14583 | 0.014757 | -122.1845 | 0.078864 | 0.078564 | 0.063807 | -122.1722 | -122.0763 | -0.049703 | -0.268 | 0.18417 | 0.062672 | 0.11237 | 0.002873 | -0.085498 | 0.17115 | 0.18349 | 0.2793 | 0.12043 | -122.3409 | 122.0877 | 122.3585 | 122.2702 | 0.62304 | -122.4054
3124.2344 | 122.2916 | -0.10071 | 122.2733 | -0.010149 | -0.04947 | 0.040293 | 0.019896 | -0.012719 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.045175 | 0.047901 | -0.012688 | 0.019721 | -0.012988 | 0.070441 | 0.078201 | 0.1786 | -0.076794 | 0.083464 | 0.53149 | -0.028879 | 121.9915 | 122.2578 | 122.1694 | -0.14583 | 0.023914 | -122.2028 | 0.08802 | 0.08772 | 0.063806 | -122.1951 | -122.0947 | -0.045125 | -0.28173 | 0.18417 | 0.071829 | 0.11695 | -0.015439 | -0.10381 | 0.17115 | 0.17891 | 0.2793 | 0.12043 | -122.35 | 122.0922 | 122.3585 | 122.2702 | 0.6322 | -122.4191
3126 | 122.4701 | -0.032043 | 122.2137 | -0.010149 | -0.049256 | 0.040293 | 0.019896 | -0.012933 | -0.0027305 | -0.021518 | -0.0022666 | -0.0027177 | 0.058046 | 0.045602 | 0.048115 | -0.012688 | 0.0243 | -0.012988 | 0.070441 | 0.087359 | 0.18775 | -0.076794 | 0.092622 | 0.52691 | -0.0243 | 121.9915 | 122.2578 | 122.1694 | -0.15041 | -0.044751 | -122.1433 | 0.019355 | 0.019055 | 0.063806 | -122.1264 | -122.026 | -0.11837 | -0.22222 | 0.12466 | 0.007743 | 0.12611 | 0.04407 | -0.044301 | 0.10248 | 0.1194 | 0.2198 | 0.056343 | -122.2905 | 122.0236 | 122.2899 | 122.2015 | 0.55895 | -122.3642
3127.7031 | 122.4243 | -0.059509 | 122.2549 | -0.01778 | -0.04947 | 0.040507 | 0.020323 | -0.012719 | -0.0027305 | -0.013887 | -0.0022666 | -0.0020767 | 0.05826 | 0.045175 | 0.048328 | -0.012688 | 0.0243 | -0.012988 | 0.07502 | 0.091937 | 0.18317 | -0.085952 | 0.083464 | 0.52691 | -0.038036 | 121.9869 | 122.267 | 122.1786 | -0.15041 | -0.026443 | -122.1799 | 0.046821 | 0.046521 | 0.072964 | -122.163 | -122.0718 | -0.090903 | -0.268 | 0.14297 | 0.021473 | 0.11238 | 0.012028 | -0.076342 | 0.13453 | 0.15145 | 0.24268 | 0.083809 | -122.3409 | 122.0465 | 122.3265 | 122.2381 | 0.58642 | -122.4054
3129.4531 | 122.4106 | -0.064087 | 122.2321 | -0.010149 | -0.049256 | 0.040507 | 0.020323 | -0.012292 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.058046 | 0.044961 | 0.048115 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.087359 | 0.18775 | -0.085952 | 0.088043 | 0.52233 | -0.038036 | 121.9961 | 122.2624 | 122.174 | -0.14583 | -0.021865 | -122.1662 | 0.051399 | 0.051099 | 0.072964 | -122.1447 | -122.0443 | -0.081746 | -0.23596 | 0.15213 | 0.026051 | 0.1078 | 0.030338 | -0.058033 | 0.12995 | 0.15145 | 0.25184 | 0.083808 | -122.318 | 122.0602 | 122.3265 | 122.2381 | 0.58642 | -122.3779
3131.2188 | 122.3282 | -0.10986 | 122.2549 | -0.010149 | -0.04947 | 0.040721 | 0.02011 | -0.012719 | -0.0027305 | -0.013887 | -0.0022666 | -0.0025041 | 0.058473 | 0.045175 | 0.048115 | -0.021844 | 0.019721 | -0.012988 | 0.070441 | 0.087359 | 0.18775 | -0.085952 | 0.088043 | 0.52233 | -0.028879 | 121.9915 | 122.2624 | 122.1694 | -0.14125 | 0.023911 | -122.1845 | 0.088019 | 0.096875 | 0.072964 | -122.1676 | -122.0672 | -0.031392 | -0.26342 | 0.19791 | 0.080984 | 0.11238 | 0.00745 | -0.0855 | 0.1803 | 0.19722 | 0.29762 | 0.12958 | -122.3409 | 122.1014 | 122.3723 | 122.2793 | 0.6322 | -122.3962
3132.9844 | 122.319 | -0.09613 | 122.2595 | -0.01778 | -0.04947 | 0.040507 | 0.019896 | -0.012933 | -0.0027305 | -0.0062567 | -0.0022666 | -0.0022903 | 0.057832 | 0.045388 | 0.048328 | -0.003531 | 0.028878 | -0.012988 | 0.07502 | 0.091937 | 0.18317 | -0.076794 | 0.083464 | 0.52691 | -0.028879 | 121.9961 | 122.2624 | 122.174 | -0.15041 | 0.019336 | -122.1845 | 0.092599 | 0.083142 | 0.063806 | -122.1676 | -122.0763 | -0.054282 | -0.26342 | 0.17959 | 0.067251 | 0.12153 | 0.002873 | -0.085498 | 0.17115 | 0.18807 | 0.2793 | 0.12501 | -122.3363 | 122.0922 | 122.3585 | 122.2702 | 0.62304 | -122.4099
3134.75 | 122.4335 | -0.07782 | 122.2321 | -0.01778 | -0.04947 | 0.040721 | 0.020323 | -0.012719 | -0.0027305 | -0.021518 | -0.0022666 | -0.0020767 | 0.058473 | 0.044961 | 0.048115 | -0.017266 | 0.0243 | -0.017566 | 0.07502 | 0.08278 | 0.18775 | -0.085952 | 0.088043 | 0.53149 | -0.033458 | 121.9915 | 122.2578 | 122.1694 | -0.15499 | -0.008132 | -122.157 | 0.060554 | 0.060254 | 0.068386 | -122.1493 | -122.0443 | -0.077171 | -0.24053 | 0.16586 | 0.044362 | 0.12153 | 0.025759 | -0.062612 | 0.15284 | 0.1606 | 0.26557 | 0.10212 | -122.318 | 122.0693 | 122.3356 | 122.2473 | 0.60931 | -122.387
3136.5156 | 122.3236 | -0.10071 | 122.2733 | -0.010149 | -0.049256 | 0.040507 | 0.02011 | -0.012933 | -0.0027305 | -0.029148 | -0.0024804 | -0.0025041 | 0.05826 | 0.045388 | 0.048328 | -0.021844 | 0.033457 | -0.008409 | 0.079598 | 0.08278 | 0.1786 | -0.085952 | 0.088043 | 0.52691 | -0.033458 | 121.9869 | 122.267 | 122.1694 | -0.15041 | 0.014756 | -122.1937 | 0.078864 | 0.092299 | 0.077543 | -122.1905 | -122.0947 | -0.049704 | -0.28631 | 0.18875 | 0.06725 | 0.11695 | -0.006282 | -0.10381 | 0.18031 | 0.18349 | 0.2793 | 0.13417 | -122.3592 | 122.0876 | 122.3677 | 122.2702 | 0.62762 | -122.4237
3138.2031 | 122.4564 | -0.036621 | 122.2092 | -0.010149 | -0.049042 | 0.04008 | 0.019896 | -0.012719 | -0.0029443 | -0.029148 | -0.0022666 | -0.0025041 | 0.058473 | 0.045175 | 0.048542 | -0.017266 | 0.033457 | -0.012988 | 0.065863 | 0.091937 | 0.18775 | -0.081373 | 0.083464 | 0.53149 | -0.028879 | 121.9915 | 122.267 | 122.1649 | -0.15499 | -0.044752 | -122.1433 | 0.019355 | 0.023633 | 0.068385 | -122.1172 | -122.0214 | -0.11837 | -0.21765 | 0.12008 | 0.007742 | 0.12611 | 0.057805 | -0.044301 | 0.10248 | 0.12856 | 0.22437 | 0.070078 | -122.2905 | 122.0281 | 122.3036 | 122.2015 | 0.56811 | -122.3642
3139.9531 | 122.3557 | -0.073242 | 122.2504 | -0.010149 | -0.049683 | 0.040507 | 0.020323 | -0.012719 | -0.0029443 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.045388 | 0.048542 | -0.021844 | 0.028878 | -0.017566 | 0.07502 | 0.091937 | 0.18317 | -0.076794 | 0.088043 | 0.52233 | -0.038036 | 121.9915 | 122.2624 | 122.1649 | -0.15041 | -0.003552 | -122.1753 | 0.051398 | 0.055676 | 0.059228 | -122.1584 | -122.0672 | -0.07717 | -0.25884 | 0.16129 | 0.035206 | 0.11238 | 0.012028 | -0.0855 | 0.14826 | 0.16518 | 0.25642 | 0.10212 | -122.3272 | 122.0648 | 122.3356 | 122.2381 | 0.59557 | -122.4008
3141.7188 | 122.493 | -0.045776 | 122.2137 | -0.010149 | -0.049683 | 0.040507 | 0.02011 | -0.012719 | -0.0029443 | -0.021518 | -0.0022666 | -0.0025041 | 0.058473 | 0.045388 | 0.047901 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.08278 | 0.18317 | -0.085952 | 0.088043 | 0.52691 | -0.033458 | 121.9915 | 122.2624 | 122.1694 | -0.14583 | -0.040176 | -122.1341 | 0.023932 | 0.032788 | 0.072964 | -122.131 | -122.0306 | -0.10006 | -0.22222 | 0.13382 | 0.012318 | 0.11237 | 0.048649 | -0.044301 | 0.12537 | 0.12856 | 0.22895 | 0.070076 | -122.2997 | 122.0373 | 122.3082 | 122.2152 | 0.57269 | -122.3596
3143.4062 | 122.3694 | -0.09613 | 122.2458 | 0.0051128 | -0.049256 | 0.040721 | 0.02011 | -0.012719 | -0.0025169 | -0.013887 | -0.0022666 | -0.0020767 | 0.05826 | 0.045175 | 0.047687 | -0.012688 | 0.019721 | -0.017566 | 0.079598 | 0.091937 | 0.18775 | -0.081373 | 0.083464 | 0.53607 | -0.038036 | 121.9869 | 122.2624 | 122.1649 | -0.14583 | 0.014757 | -122.1662 | 0.083442 | 0.078564 | 0.063807 | -122.1539 | -122.058 | -0.049703 | -0.25885 | 0.17959 | 0.058094 | 0.1078 | 0.016605 | -0.080923 | 0.17573 | 0.18807 | 0.28388 | 0.11585 | -122.3272 | 122.0831 | 122.3585 | 122.261 | 0.6322 | -122.3916
3145.1562 | 122.3282 | -0.10986 | 122.2595 | -0.0025182 | -0.04947 | 0.040507 | 0.020537 | -0.012933 | -0.0023033 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.045602 | 0.048115 | -0.012688 | 0.019721 | -0.017566 | 0.07502 | 0.087359 | 0.18317 | -0.081373 | 0.083464 | 0.52233 | -0.042615 | 121.9915 | 122.267 | 122.174 | -0.15041 | 0.02849 | -122.1845 | 0.097175 | 0.092297 | 0.063807 | -122.1722 | -122.0763 | -0.040549 | -0.268 | 0.19333 | 0.067248 | 0.1078 | 0.007451 | -0.085498 | 0.18488 | 0.19722 | 0.29304 | 0.12958 | -122.3409 | 122.1014 | 122.3768 | 122.2839 | 0.6322 | -122.4099
3146.9062 | 122.3877 | -0.064087 | 122.2458 | -0.0025182 | -0.04947 | 0.040293 | 0.02011 | -0.012506 | -0.0027305 | -0.0062567 | -0.0024804 | -0.0020767 | 0.05826 | 0.045388 | 0.048328 | -0.012688 | 0.028878 | -0.012988 | 0.065863 | 0.087359 | 0.18775 | -0.085952 | 0.083464 | 0.52691 | -0.033458 | 121.9961 | 122.2624 | 122.1786 | -0.15041 | -0.021865 | -122.1799 | 0.051399 | 0.051099 | 0.072964 | -122.1584 | -122.058 | -0.086325 | -0.24969 | 0.14755 | 0.030629 | 0.11695 | 0.016605 | -0.067187 | 0.12995 | 0.15145 | 0.25184 | 0.092965 | -122.3317 | 122.0602 | 122.3265 | 122.2427 | 0.591 | -122.3962
3148.6094 | 122.4014 | -0.073242 | 122.2275 | -0.01778 | -0.04947 | 0.040293 | 0.02011 | -0.012719 | -0.0025169 | -0.029148 | -0.0024804 | -0.0020767 | 0.058046 | 0.045388 | 0.047901 | -0.012688 | 0.0243 | -0.017566 | 0.07502 | 0.091937 | 0.18775 | -0.081373 | 0.088043 | 0.52691 | -0.028879 | 122.0007 | 122.2624 | 122.174 | -0.15041 | -0.008131 | -122.1525 | 0.060554 | 0.055676 | 0.063807 | -122.1355 | -122.0397 | -0.07717 | -0.2268 | 0.16129 | 0.044363 | 0.12153 | 0.034916 | -0.053455 | 0.14826 | 0.16518 | 0.26099 | 0.097542 | -122.3089 | 122.0739 | 122.3356 | 122.2473 | 0.60015 | -122.3779
3150.375 | 122.4152 | -0.064087 | 122.2366 | -0.0025182 | -0.04947 | 0.039866 | 0.020323 | -0.012719 | -0.0029443 | -0.021518 | -0.002053 | -0.0022903 | 0.05826 | 0.045388 | 0.048115 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.087359 | 0.18775 | -0.081373 | 0.083464 | 0.53149 | -0.033458 | 121.9869 | 122.267 | 122.1694 | -0.15041 | -0.017286 | -122.1616 | 0.046821 | 0.051099 | 0.068385 | -122.1493 | -122.0489 | -0.086325 | -0.24969 | 0.14755 | 0.030629 | 0.11695 | 0.030339 | -0.067189 | 0.13911 | 0.15145 | 0.25184 | 0.079229 | -122.318 | 122.051 | 122.3311 | 122.2335 | 0.59558 | -122.387
3152.1562 | 122.4152 | -0.054932 | 122.2321 | -0.025411 | -0.04947 | 0.040293 | 0.019896 | -0.012719 | -0.0025169 | -0.021518 | -0.0024804 | -0.0022903 | 0.058473 | 0.045175 | 0.048115 | -0.017266 | 0.019721 | -0.008409 | 0.070441 | 0.096516 | 0.1786 | -0.081373 | 0.083464 | 0.52233 | -0.033458 | 121.9869 | 122.2578 | 122.1694 | -0.15041 | -0.026441 | -122.1616 | 0.037666 | 0.046523 | 0.072964 | -122.1355 | -122.0535 | -0.09548 | -0.24511 | 0.1384 | 0.021474 | 0.11695 | 0.025759 | -0.062612 | 0.12537 | 0.15145 | 0.23353 | 0.074653 | -122.3134 | 122.0419 | 122.3127 | 122.2244 | 0.57726 | -122.3825
3153.8438 | 122.4518 | -0.050354 | 122.2321 | -0.010149 | -0.04947 | 0.040507 | 0.019682 | -0.012292 | -0.0031579 | -0.013887 | -0.0022666 | -0.0022903 | 0.058046 | 0.045175 | 0.047901 | -0.017266 | 0.028878 | -0.017566 | 0.07502 | 0.087359 | 0.18775 | -0.081373 | 0.088043 | 0.53607 | -0.033458 | 121.9961 | 122.267 | 122.174 | -0.15499 | -0.031019 | -122.157 | 0.033088 | 0.032788 | 0.063807 | -122.1447 | -122.0443 | -0.10464 | -0.23596 | 0.1384 | 0.016896 | 0.12153 | 0.034916 | -0.058033 | 0.12537 | 0.13771 | 0.23811 | 0.079232 | -122.3134 | 122.0465 | 122.3173 | 122.2244 | 0.58642 | -122.387
3155.5938 | 122.3373 | -0.082397 | 122.2549 | -0.0025182 | -0.049683 | 0.040293 | 0.019896 | -0.012933 | -0.0027305 | -0.021518 | -0.0022666 | -0.0025041 | 0.058046 | 0.045602 | 0.048115 | -0.021844 | 0.015142 | -0.017566 | 0.079598 | 0.087359 | 0.18317 | -0.081373 | 0.083464 | 0.53149 | -0.028879 | 121.9961 | 122.267 | 122.1694 | -0.15041 | 0.001024 | -122.1753 | 0.060553 | 0.064831 | 0.063807 | -122.1676 | -122.0718 | -0.068015 | -0.25884 | 0.16586 | 0.053518 | 0.12153 | 0.012028 | -0.0855 | 0.162 | 0.16976 | 0.26557 | 0.097539 | -122.3363 | 122.0785 | 122.3494 | 122.2518 | 0.61389 | -122.4054
3157.3594 | 122.3099 | -0.10529 | 122.2641 | -0.01778 | -0.049683 | 0.040293 | 0.019896 | -0.012933 | -0.0027305 | -0.029148 | -0.0022666 | -0.0022903 | 0.05826 | 0.045388 | 0.048328 | -0.017266 | 0.0243 | -0.012988 | 0.07502 | 0.091937 | 0.18775 | -0.076794 | 0.083464 | 0.52691 | -0.033458 | 121.9961 | 122.2624 | 122.174 | -0.14583 | 0.028492 | -122.1891 | 0.08802 | 0.092298 | 0.063806 | -122.1722 | -122.0763 | -0.040547 | -0.268 | 0.18875 | 0.071828 | 0.11237 | -0.001705 | -0.090076 | 0.18031 | 0.19722 | 0.29304 | 0.12959 | -122.3409 | 122.1014 | 122.3677 | 122.2793 | 0.6322 | -122.4099
3159.0625 | 122.4289 | -0.054932 | 122.2458 | -0.01778 | -0.049683 | 0.040293 | 0.020537 | -0.012506 | -0.0027305 | -0.0062567 | -0.0022666 | -0.0020767 | 0.058046 | 0.045388 | 0.048328 | -0.012688 | 0.028878 | -0.012988 | 0.07502 | 0.091937 | 0.19233 | -0.081373 | 0.083464 | 0.52691 | -0.038036 | 121.9915 | 122.2532 | 122.1649 | -0.15041 | -0.026441 | -122.1708 | 0.042244 | 0.041944 | 0.068385 | -122.1539 | -122.0535 | -0.09548 | -0.25427 | 0.1384 | 0.016896 | 0.11238 | 0.007448 | -0.080923 | 0.12995 | 0.14687 | 0.24726 | 0.08381 | -122.3272 | 122.0465 | 122.3082 | 122.2198 | 0.58184 | -122.3962
3160.8281 | 122.3145 | -0.09613 | 122.2778 | -0.010149 | -0.04947 | 0.040293 | 0.02011 | -0.012506 | -0.0025169 | -0.0062567 | -0.0022666 | -0.0022903 | 0.05826 | 0.045388 | 0.047901 | -0.012688 | 0.0243 | -0.017566 | 0.070441 | 0.091937 | 0.18317 | -0.081373 | 0.083464 | 0.53149 | -0.033458 | 121.9915 | 122.2578 | 122.174 | -0.15499 | 0.014757 | -122.2074 | 0.083442 | 0.078564 | 0.063807 | -122.1859 | -122.0947 | -0.058861 | -0.28631 | 0.17959 | 0.062672 | 0.12153 | -0.020017 | -0.10381 | 0.16657 | 0.18807 | 0.2793 | 0.12043 | -122.3592 | 122.0877 | 122.3539 | 122.2702 | 0.62762 | -122.4328
3162.5938 | 122.3328 | -0.10529 | 122.2778 | -0.0025182 | -0.049683 | 0.040507 | 0.020323 | -0.012933 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.045388 | 0.047901 | -0.021844 | 0.019721 | -0.008409 | 0.07502 | 0.087359 | 0.18317 | -0.076794 | 0.083464 | 0.52691 | -0.033458 | 121.9961 | 122.267 | 122.174 | -0.15041 | 0.028492 | -122.2028 | 0.083442 | 0.096877 | 0.068385 | -122.1905 | -122.0947 | -0.045126 | -0.28173 | 0.18875 | 0.071828 | 0.11695 | -0.01086 | -0.10381 | 0.18031 | 0.19265 | 0.28846 | 0.12501 | -122.3546 | 122.1014 | 122.3723 | 122.2793 | 0.6322 | -122.4282
3164.3594 | 122.3236 | -0.10529 | 122.2412 | -0.0025182 | -0.049683 | 0.040507 | 0.020323 | -0.012506 | -0.0029443 | -0.029148 | -0.0024804 | -0.0020767 | 0.05826 | 0.045388 | 0.047901 | -0.008109 | 0.0243 | -0.008409 | 0.079598 | 0.087359 | 0.18775 | -0.081373 | 0.092622 | 0.53149 | -0.033458 | 121.9961 | 122.267 | 122.174 | -0.15041 | 0.023913 | -122.1616 | 0.097177 | 0.096877 | 0.072964 | -122.1539 | -122.0535 | -0.045126 | -0.24511 | 0.19791 | 0.071828 | 0.11695 | 0.025761 | -0.067188 | 0.18488 | 0.19265 | 0.29304 | 0.12959 | -122.3226 | 122.1014 | 122.3723 | 122.2793 | 0.63677 | -122.3916
3166.1094 | 122.3373 | -0.10986 | 122.2549 | -0.010149 | -0.04947 | 0.040293 | 0.02011 | -0.012719 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058046 | 0.045388 | 0.048328 | -0.021844 | 0.019721 | -0.017566 | 0.07502 | 0.087359 | 0.18775 | -0.072215 | 0.092622 | 0.53149 | -0.028879 | 121.9915 | 122.2624 | 122.1694 | -0.15957 | 0.037648 | -122.1799 | 0.088019 | 0.092297 | 0.054649 | -122.1676 | -122.0672 | -0.049707 | -0.26342 | 0.20248 | 0.080984 | 0.13069 | 0.00745 | -0.0855 | 0.18488 | 0.19722 | 0.29762 | 0.12958 | -122.3272 | 122.1014 | 122.3723 | 122.2793 | 0.64135 | -122.4145
3167.8125 | 122.4152 | -0.054932 | 122.2321 | -0.010149 | -0.049897 | 0.040293 | 0.02011 | -0.012933 | -0.0029443 | -0.029148 | -0.0022666 | -0.0022903 | 0.05826 | 0.045388 | 0.048115 | -0.026423 | 0.028878 | -0.017566 | 0.070441 | 0.091937 | 0.19233 | -0.085952 | 0.088043 | 0.53607 | -0.0243 | 121.9915 | 122.2624 | 122.174 | -0.15041 | -0.03102 | -122.1616 | 0.028509 | 0.037366 | 0.068386 | -122.1401 | -122.0397 | -0.09548 | -0.24053 | 0.14297 | 0.030632 | 0.12611 | 0.030338 | -0.058033 | 0.12537 | 0.14687 | 0.24726 | 0.08381 | -122.318 | 122.0465 | 122.3173 | 122.229 | 0.591 | -122.3825
3169.5781 | 122.4152 | -0.082397 | 122.2366 | -0.01778 | -0.049683 | 0.040507 | 0.019896 | -0.012933 | -0.0027305 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058046 | 0.045602 | 0.047901 | -0.026423 | 0.015142 | -0.008409 | 0.070441 | 0.087359 | 0.19233 | -0.085952 | 0.092622 | 0.53149 | -0.028879 | 122.0007 | 122.2624 | 122.1694 | -0.15041 | -0.003555 | -122.1662 | 0.055974 | 0.073988 | 0.077543 | -122.1493 | -122.0443 | -0.068015 | -0.23596 | 0.17502 | 0.053518 | 0.12153 | 0.025761 | -0.067189 | 0.15284 | 0.16976 | 0.27473 | 0.097539 | -122.3226 | 122.0831 | 122.3448 | 122.2518 | 0.61389 | -122.387
3171.3438 | 122.374 | -0.068665 | 122.2458 | -0.01778 | -0.049683 | 0.040507 | 0.02011 | -0.012506 | -0.0029443 | -0.029148 | -0.0024804 | -0.0025041 | 0.05826 | 0.045388 | 0.048115 | -0.021844 | 0.015142 | -0.012988 | 0.070441 | 0.087359 | 0.18317 | -0.076794 | 0.092622 | 0.53149 | -0.028879 | 121.9915 | 122.267 | 122.1694 | -0.14125 | -0.008129 | -122.1753 | 0.046821 | 0.055677 | 0.063806 | -122.1584 | -122.0626 | -0.07259 | -0.25427 | 0.16129 | 0.039786 | 0.11238 | 0.021183 | -0.076345 | 0.13911 | 0.15602 | 0.25184 | 0.083807 | -122.3226 | 122.0602 | 122.3356 | 122.2381 | 0.60015 | -122.387
3173.1094 | 122.4197 | -0.050354 | 122.2183 | -0.01778 | -0.04947 | 0.040934 | 0.020323 | -0.012933 | -0.0027305 | -0.029148 | -0.0024804 | -0.0022903 | 0.05826 | 0.045602 | 0.047901 | -0.012688 | 0.019721 | -0.017566 | 0.07502 | 0.096516 | 0.19233 | -0.076794 | 0.083464 | 0.53149 | -0.028879 | 121.9961 | 122.267 | 122.174 | -0.15041 | -0.02644 | -122.1433 | 0.037666 | 0.032788 | 0.059228 | -122.1218 | -122.026 | -0.10006 | -0.22222 | 0.13382 | 0.021475 | 0.12153 | 0.048649 | -0.0443 | 0.12537 | 0.14687 | 0.24269 | 0.070075 | -122.2951 | 122.0465 | 122.3173 | 122.2244 | 0.58184 | -122.3687
3174.7969 | 122.4609 | -0.054932 | 122.2412 | 0.0051128 | -0.049683 | 0.040507 | 0.019896 | -0.012933 | -0.0031579 | -0.013887 | -0.0022666 | -0.0022903 | 0.058473 | 0.045388 | 0.047901 | -0.017266 | 0.015142 | -0.022144 | 0.07502 | 0.091937 | 0.18317 | -0.081373 | 0.088043 | 0.53607 | -0.042615 | 121.9961 | 122.267 | 122.1649 | -0.15041 | -0.026441 | -122.1662 | 0.037666 | 0.032788 | 0.059229 | -122.1493 | -122.058 | -0.09548 | -0.24511 | 0.14297 | 0.012317 | 0.1078 | 0.025761 | -0.076345 | 0.12995 | 0.14687 | 0.23811 | 0.070074 | -122.3226 | 122.051 | 122.3219 | 122.2198 | 0.591 | -122.3916
3176.5625 | 122.3602 | -0.09613 | 122.2595 | -0.010149 | -0.04947 | 0.040293 | 0.019896 | -0.012933 | -0.0027305 | -0.013887 | -0.0022666 | -0.0025041 | 0.058473 | 0.045816 | 0.048115 | -0.026423 | 0.019721 | -0.012988 | 0.070441 | 0.091937 | 0.18775 | -0.076794 | 0.083464 | 0.53607 | -0.033458 | 121.9961 | 122.267 | 122.1649 | -0.15041 | 0.019336 | -122.1891 | 0.069707 | 0.083142 | 0.063806 | -122.1676 | -122.0718 | -0.054282 | -0.26342 | 0.17959 | 0.062672 | 0.11695 | 0.007451 | -0.094655 | 0.16657 | 0.18807 | 0.28388 | 0.11585 | -122.3363 | 122.0922 | 122.3631 | 122.261 | 0.6322 | -122.4099
3178.2656 | 122.3419 | -0.10529 | 122.2687 | -0.01778 | -0.050111 | 0.04008 | 0.020323 | -0.012506 | -0.0029443 | -0.021518 | -0.0022666 | -0.0020767 | 0.05826 | 0.044961 | 0.048115 | -0.021844 | 0.019721 | -0.012988 | 0.07502 | 0.091937 | 0.18775 | -0.081373 | 0.083464 | 0.53607 | -0.028879 | 122.0007 | 122.2624 | 122.1694 | -0.15041 | 0.023913 | -122.1937 | 0.083442 | 0.092298 | 0.068385 | -122.1767 | -122.0809 | -0.045126 | -0.268 | 0.18875 | 0.076407 | 0.12153 | -0.006283 | -0.099233 | 0.18031 | 0.19722 | 0.29304 | 0.12501 | -122.35 | 122.106 | 122.3677 | 122.2747 | 0.64135 | -122.4191
3180.0312 | 122.4976 | -0.091553 | 122.2321 | 0.0051128 | -0.049683 | 0.040293 | 0.019896 | -0.012506 | -0.0027305 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.045816 | 0.048328 | 0.074302 | 0.019721 | -0.012988 | 0.07502 | 0.087359 | 0.18317 | -0.081373 | 0.074307 | 0.5498 | -0.028879 | 121.9915 | 122.267 | 122.1694 | -0.15041 | 0.01018 | -122.157 | 0.16586 | 0.078565 | 0.068385 | -122.1447 | -122.0489 | -0.058859 | -0.24053 | 0.16586 | 0.062674 | 0.12153 | 0.034916 | -0.062612 | 0.16657 | 0.17891 | 0.27473 | 0.11127 | -122.3134 | 122.0831 | 122.3585 | 122.261 | 0.64136 | -122.3825
3181.7969 | 122.4518 | -0.10986 | 122.2687 | -0.0025182 | -0.049683 | 0.040293 | 0.02011 | -0.013147 | -0.0031579 | -0.013887 | -0.0024804 | -0.0020767 | 0.05826 | 0.045816 | 0.047901 | 0.088037 | 0.0243 | 0.000747 | 0.07502 | 0.091937 | 0.18775 | -0.081373 | 0.083464 | 0.54065 | -0.033458 | 121.9915 | 122.2624 | 122.1786 | -0.15041 | 0.02849 | -122.1937 | 0.1979 | 0.11061 | 0.08212 | -122.1767 | -122.0809 | -0.040549 | -0.27716 | 0.19333 | 0.076405 | 0.11695 | -0.006283 | -0.090075 | 0.18488 | 0.2018 | 0.29762 | 0.13416 | -122.35 | 122.1014 | 122.3723 | 122.2885 | 0.65051 | -122.4191
3183.5 | 122.374 | -0.09613 | 122.2641 | -0.0025182 | -0.049683 | 0.040293 | 0.019896 | -0.012933 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.05826 | 0.045816 | 0.048328 | -0.017266 | 0.028878 | -0.012988 | 0.07502 | 0.087359 | 0.18317 | -0.085952 | 0.083464 | 0.52691 | -0.038036 | 121.9915 | 122.2624 | 122.1694 | -0.14583 | 0.010178 | -122.1891 | 0.078864 | 0.083142 | 0.072964 | -122.1767 | -122.0809 | -0.049703 | -0.27258 | 0.17959 | 0.058094 | 0.1078 | -0.001705 | -0.094655 | 0.17115 | 0.18349 | 0.2793 | 0.12501 | -122.3501 | 122.0877 | 122.3585 | 122.2656 | 0.62304 | -122.4099
3185.2656 | 122.3419 | -0.091553 | 122.2687 | -0.0025182 | -0.049256 | 0.040293 | 0.020323 | -0.012719 | -0.0027305 | -0.013887 | -0.0024804 | -0.0025041 | 0.05826 | 0.045602 | 0.047687 | -0.017266 | 0.0243 | -0.012988 | 0.070441 | 0.087359 | 0.1786 | -0.076794 | 0.088043 | 0.53607 | -0.033458 | 122.0053 | 122.2624 | 122.174 | -0.15499 | 0.014759 | -122.1982 | 0.074287 | 0.078565 | 0.063806 | -122.1813 | -122.0901 | -0.063438 | -0.26342 | 0.1796 | 0.058095 | 0.12153 | -0.006283 | -0.094654 | 0.16199 | 0.17891 | 0.27015 | 0.11585 | -122.3455 | 122.0968 | 122.3539 | 122.2656 | 0.62762 | -122.4237
3186.9688 | 122.3785 | -0.10071 | 122.2824 | -0.0025182 | -0.049683 | 0.040293 | 0.02011 | -0.012506 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058473 | 0.045388 | 0.048328 | -0.021844 | 0.019721 | -0.003831 | 0.07502 | 0.08278 | 0.18317 | -0.076794 | 0.078886 | 0.54065 | -0.028879 | 122.0007 | 122.2716 | 122.174 | -0.15041 | 0.023914 | -122.2074 | 0.078864 | 0.096877 | 0.072963 | -122.1996 | -122.0992 | -0.049704 | -0.28173 | 0.17959 | 0.071829 | 0.12153 | -0.010859 | -0.10839 | 0.17573 | 0.18349 | 0.28388 | 0.12043 | -122.3592 | 122.1014 | 122.3723 | 122.2747 | 0.64136 | -122.4328
3188.7188 | 122.3236 | -0.09613 | 122.2824 | -0.010149 | -0.049683 | 0.040293 | 0.019682 | -0.012933 | -0.0031579 | -0.029148 | -0.0022666 | -0.0025041 | 0.058046 | 0.045602 | 0.047901 | -0.017266 | 0.0243 | -0.012988 | 0.070441 | 0.087359 | 0.19233 | -0.072215 | 0.088043 | 0.53149 | -0.033458 | 121.9915 | 122.267 | 122.1694 | -0.14125 | 0.023915 | -122.212 | 0.078864 | 0.083142 | 0.059227 | -122.1951 | -122.0901 | -0.045125 | -0.29089 | 0.18417 | 0.062672 | 0.1078 | -0.015438 | -0.11297 | 0.16657 | 0.18349 | 0.28846 | 0.12043 | -122.3546 | 122.0877 | 122.3631 | 122.2656 | 0.62762 | -122.4237
3190.4688 | 122.4243 | -0.045776 | 122.2366 | -0.010149 | -0.049897 | 0.040293 | 0.019896 | -0.012719 | -0.0029443 | -0.021518 | -0.002053 | -0.0022903 | 0.058046 | 0.045388 | 0.048328 | -0.017266 | 0.015142 | -0.012988 | 0.070441 | 0.091937 | 0.18775 | -0.076794 | 0.083464 | 0.54065 | -0.028879 | 122.0007 | 122.267 | 122.1694 | -0.15041 | -0.031018 | -122.1662 | 0.02851 | 0.032788 | 0.063806 | -122.1447 | -122.0489 | -0.10464 | -0.23596 | 0.12924 | 0.016897 | 0.12153 | 0.030339 | -0.067189 | 0.11622 | 0.13771 | 0.23353 | 0.060918 | -122.3134 | 122.0465 | 122.3127 | 122.2152 | 0.58642 | -122.387
3192.1875 | 122.3511 | -0.11902 | 122.2778 | -0.01778 | -0.049683 | 0.039652 | 0.019682 | -0.012719 | -0.0027305 | -0.021518 | -0.0022666 | -0.0025041 | 0.057832 | 0.045602 | 0.048115 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.091937 | 0.19233 | -0.081373 | 0.083464 | 0.53149 | -0.028879 | 121.9961 | 122.267 | 122.1786 | -0.15041 | 0.037646 | -122.2028 | 0.10175 | 0.10603 | 0.068385 | -122.1859 | -122.0855 | -0.031393 | -0.28173 | 0.20248 | 0.09014 | 0.12153 | -0.01086 | -0.09923 | 0.19404 | 0.21096 | 0.31135 | 0.13874 | -122.3592 | 122.1151 | 122.386 | 122.2976 | 0.65051 | -122.4282
3193.9531 | 122.4792 | -0.059509 | 122.2412 | -0.01778 | -0.049683 | 0.04008 | 0.019896 | -0.012933 | -0.0027305 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.045602 | 0.048115 | -0.012688 | 0.0243 | -0.017566 | 0.079598 | 0.087359 | 0.18775 | -0.085952 | 0.083464 | 0.53607 | -0.033458 | 121.9961 | 122.2716 | 122.174 | -0.15041 | -0.026443 | -122.1616 | 0.046821 | 0.041943 | 0.068386 | -122.1539 | -122.0535 | -0.090903 | -0.24511 | 0.14297 | 0.026051 | 0.11695 | 0.03034 | -0.067188 | 0.13911 | 0.14687 | 0.24726 | 0.083809 | -122.3272 | 122.0556 | 122.3311 | 122.2335 | 0.59558 | -122.3916
3195.7031 | 122.493 | -0.045776 | 122.2366 | -0.01778 | -0.049683 | 0.04008 | 0.019682 | -0.012933 | -0.0029443 | -0.036779 | -0.002694 | -0.0025041 | 0.058046 | 0.045816 | 0.047687 | -0.017266 | 0.015142 | -0.012988 | 0.079598 | 0.091937 | 0.18775 | -0.081373 | 0.088043 | 0.53607 | -0.033458 | 122.0007 | 122.2624 | 122.1694 | -0.15499 | -0.035597 | -122.157 | 0.02851 | 0.032788 | 0.068385 | -122.1447 | -122.0489 | -0.10921 | -0.23596 | 0.13382 | 0.012318 | 0.12153 | 0.025761 | -0.067189 | 0.12537 | 0.13771 | 0.23353 | 0.060918 | -122.318 | 122.0465 | 122.3082 | 122.2152 | 0.58184 | -122.3916
3197.4688 | 122.3419 | -0.10986 | 122.2778 | 0.0051128 | -0.049897 | 0.040721 | 0.019896 | -0.012719 | -0.0025169 | -0.0062567 | -0.0024804 | -0.0020767 | 0.05826 | 0.045602 | 0.048115 | -0.017266 | 0.015142 | -0.008409 | 0.07502 | 0.091937 | 0.18317 | -0.081373 | 0.088043 | 0.53607 | -0.028879 | 121.9915 | 122.2578 | 122.1832 | -0.14583 | 0.02849 | -122.2028 | 0.092597 | 0.10145 | 0.072964 | -122.1859 | -122.0947 | -0.03597 | -0.28631 | 0.19791 | 0.080984 | 0.11695 | -0.020017 | -0.094652 | 0.18488 | 0.2018 | 0.29304 | 0.12501 | -122.3592 | 122.1014 | 122.3677 | 122.293 | 0.64593 | -122.4237
3199.2344 | 122.3694 | -0.086975 | 122.2549 | -0.010149 | -0.049897 | 0.04008 | 0.02011 | -0.012506 | -0.0029443 | -0.021518 | -0.0024804 | -0.0022903 | 0.05826 | 0.045388 | 0.047901 | -0.012688 | 0.015142 | -0.008409 | 0.084176 | 0.1011 | 0.18317 | -0.085952 | 0.088043 | 0.54065 | -0.028879 | 121.9961 | 122.267 | 122.1786 | -0.15041 | 0.001023 | -122.1708 | 0.074287 | 0.078566 | 0.077543 | -122.1538 | -122.0718 | -0.063437 | -0.25884 | 0.17502 | 0.058096 | 0.12153 | 0.012028 | -0.076342 | 0.17115 | 0.18807 | 0.27015 | 0.10212 | -122.3409 | 122.0831 | 122.3539 | 122.2656 | 0.62762 | -122.4054
3200.9375 | 122.3145 | -0.09613 | 122.2916 | -0.01778 | -0.049897 | 0.040293 | 0.02011 | -0.012719 | -0.0027305 | -0.021518 | -0.0022666 | -0.0020767 | 0.057832 | 0.045602 | 0.048115 | -0.012688 | 0.015142 | -0.012988 | 0.079598 | 0.087359 | 0.18317 | -0.085952 | 0.083464 | 0.53607 | -0.033458 | 121.9961 | 122.267 | 122.1786 | -0.15499 | 0.010178 | -122.212 | 0.083442 | 0.083142 | 0.072964 | -122.2042 | -122.1084 | -0.058861 | -0.29547 | 0.17959 | 0.062672 | 0.12153 | -0.024593 | -0.11296 | 0.17573 | 0.18349 | 0.2793 | 0.11127 | -122.3775 | 122.0922 | 122.3631 | 122.2747 | 0.6322 | -122.4466
3202.6406 | 122.3831 | -0.091553 | 122.2595 | -0.0025182 | -0.04947 | 0.04008 | 0.019682 | -0.012933 | -0.0025169 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.045175 | 0.047901 | -0.012688 | 0.019721 | -0.003831 | 0.070441 | 0.096516 | 0.18317 | -0.076794 | 0.083464 | 0.54065 | -0.028879 | 121.9915 | 122.267 | 122.174 | -0.15041 | 0.014759 | -122.1891 | 0.078865 | 0.087722 | 0.072963 | -122.163 | -122.0763 | -0.058859 | -0.268 | 0.17502 | 0.062674 | 0.12153 | 0.007451 | -0.085498 | 0.16199 | 0.18807 | 0.27473 | 0.11127 | -122.3363 | 122.0831 | 122.3585 | 122.2656 | 0.6322 | -122.4099
3204.3906 | 122.3465 | -0.10529 | 122.2412 | -0.0025182 | -0.049683 | 0.040293 | 0.019896 | -0.012933 | -0.0029443 | -0.0062567 | -0.002053 | -0.0025041 | 0.057832 | 0.045388 | 0.047901 | -0.017266 | 0.015142 | -0.017566 | 0.070441 | 0.091937 | 0.18775 | -0.085952 | 0.088043 | 0.54065 | -0.028879 | 121.9915 | 122.2624 | 122.1694 | -0.15041 | 0.019334 | -122.1708 | 0.08802 | 0.08772 | 0.068386 | -122.1493 | -122.0535 | -0.045126 | -0.24969 | 0.19333 | 0.076407 | 0.12153 | 0.021183 | -0.071767 | 0.17573 | 0.19722 | 0.29304 | 0.12043 | -122.3272 | 122.0968 | 122.3677 | 122.2747 | 0.64593 | -122.3916
3206.1562 | 122.3465 | -0.10529 | 122.2687 | -0.01778 | -0.049897 | 0.040507 | 0.019896 | -0.012719 | -0.0031579 | -0.021518 | -0.0024804 | -0.0025041 | 0.058046 | 0.045388 | 0.047901 | -0.021844 | 0.015142 | -0.012988 | 0.070441 | 0.087359 | 0.18775 | -0.085952 | 0.092622 | 0.54065 | -0.033458 | 121.9961 | 122.2624 | 122.174 | -0.15499 | 0.019334 | -122.1982 | 0.083442 | 0.092298 | 0.072964 | -122.1813 | -122.0809 | -0.049705 | -0.27258 | 0.19791 | 0.071828 | 0.12153 | -0.006283 | -0.094654 | 0.17573 | 0.19265 | 0.29304 | 0.12043 | -122.3546 | 122.1014 | 122.3677 | 122.2793 | 0.64593 | -122.4237
3207.8594 | 122.4701 | -0.068665 | 122.2366 | -0.010149 | -0.049897 | 0.040507 | 0.019896 | -0.012292 | -0.0029443 | -0.0062567 | -0.0024804 | -0.0025041 | 0.05826 | 0.045602 | 0.047901 | -0.021844 | 0.015142 | -0.012988 | 0.070441 | 0.091937 | 0.18317 | -0.072215 | 0.088043 | 0.52691 | -0.038036 | 121.9915 | 122.267 | 122.174 | -0.15041 | -0.00355 | -122.1662 | 0.046821 | 0.055677 | 0.059227 | -122.1447 | -122.0535 | -0.081747 | -0.24511 | 0.15671 | 0.030629 | 0.11238 | 0.030339 | -0.06261 | 0.13911 | 0.1606 | 0.25184 | 0.083807 | -122.3088 | 122.0602 | 122.3356 | 122.2427 | 0.59558 | -122.387
3209.625 | 122.4747 | -0.068665 | 122.2137 | -0.010149 | -0.049683 | 0.040721 | 0.019896 | -0.012933 | -0.0027305 | -0.013887 | -0.002053 | -0.0022903 | 0.05826 | 0.045816 | 0.047687 | -0.012688 | 0.0243 | -0.008409 | 0.079598 | 0.087359 | 0.18775 | -0.076794 | 0.088043 | 0.53149 | -0.033458 | 121.9961 | 122.2624 | 122.174 | -0.15499 | -0.008129 | -122.1341 | 0.055977 | 0.060256 | 0.068385 | -122.1264 | -122.026 | -0.086326 | -0.21765 | 0.15671 | 0.035207 | 0.12153 | 0.048649 | -0.039722 | 0.14826 | 0.15602 | 0.25642 | 0.092965 | -122.2905 | 122.0648 | 122.3311 | 122.2427 | 0.60015 | -122.3687
3211.3906 | 122.4518 | -0.054932 | 122.2229 | -0.010149 | -0.049897 | 0.040293 | 0.020323 | -0.012933 | -0.0029443 | -0.036779 | -0.0024804 | -0.0022903 | 0.058046 | 0.045602 | 0.048328 | -0.021844 | 0.015142 | -0.008409 | 0.07502 | 0.087359 | 0.18775 | -0.085952 | 0.092622 | 0.54522 | -0.028879 | 121.9961 | 122.2761 | 122.1786 | -0.15041 | -0.03102 | -122.1479 | 0.033088 | 0.046523 | 0.077543 | -122.1355 | -122.0351 | -0.09548 | -0.2268 | 0.14755 | 0.026053 | 0.12153 | 0.05323 | -0.044298 | 0.12995 | 0.14229 | 0.24268 | 0.070074 | -122.3089 | 122.051 | 122.3311 | 122.2335 | 0.60016 | -122.3733
3213.0938 | 122.3236 | -0.09613 | 122.2321 | -0.010149 | -0.049683 | 0.04008 | 0.019896 | -0.012506 | -0.0033715 | -0.013887 | -0.0022666 | -0.0025041 | 0.058687 | 0.045388 | 0.047901 | -0.021844 | 0.0243 | -0.017566 | 0.084176 | 0.08278 | 0.19233 | -0.076794 | 0.088043 | 0.53607 | -0.028879 | 121.9915 | 122.2624 | 122.1786 | -0.15041 | 0.019336 | -122.1479 | 0.074286 | 0.078564 | 0.059228 | -122.1493 | -122.0397 | -0.054282 | -0.24053 | 0.18417 | 0.067251 | 0.12153 | 0.030338 | -0.053454 | 0.18031 | 0.17891 | 0.28846 | 0.12043 | -122.3089 | 122.0877 | 122.3585 | 122.2747 | 0.6322 | -122.3825
3214.8594 | 122.3511 | -0.10529 | 122.2733 | -0.010149 | -0.049897 | 0.040293 | 0.02011 | -0.012933 | -0.0031579 | -0.013887 | -0.002053 | -0.0022903 | 0.057832 | 0.045816 | 0.048115 | -0.012688 | 0.015142 | -0.012988 | 0.07502 | 0.091937 | 0.19233 | -0.081373 | 0.083464 | 0.53607 | -0.038036 | 121.9915 | 122.267 | 122.174 | -0.15957 | 0.023913 | -122.1982 | 0.092598 | 0.092298 | 0.068385 | -122.1813 | -122.0809 | -0.054284 | -0.28173 | 0.18875 | 0.06725 | 0.12153 | -0.006282 | -0.099231 | 0.18031 | 0.19722 | 0.29762 | 0.12043 | -122.3546 | 122.0968 | 122.3723 | 122.2793 | 0.64135 | -122.4328
3216.6406 | 122.3282 | -0.10986 | 122.2641 | -0.01778 | -0.049683 | 0.040293 | 0.019682 | -0.012719 | -0.0029443 | -0.0062567 | -0.0024804 | -0.0025041 | 0.058046 | 0.045175 | 0.048328 | -0.012688 | 0.019721 | -0.008409 | 0.084176 | 0.087359 | 0.19233 | -0.076794 | 0.088043 | 0.53607 | -0.042615 | 122.0007 | 122.2624 | 122.1786 | -0.15041 | 0.033069 | -122.1799 | 0.097175 | 0.10145 | 0.068385 | -122.1767 | -122.0718 | -0.040549 | -0.26342 | 0.19791 | 0.067248 | 0.1078 | -0.001705 | -0.085497 | 0.19404 | 0.19722 | 0.30219 | 0.12958 | -122.3409 | 122.1105 | 122.3723 | 122.2885 | 0.64593 | -122.4145
3218.4062 | 122.3282 | -0.10986 | 122.2778 | -0.010149 | -0.049897 | 0.040293 | 0.02011 | -0.012719 | -0.0029443 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.045388 | 0.047901 | -0.012688 | 0.015142 | -0.003831 | 0.07502 | 0.087359 | 0.18317 | -0.081373 | 0.083464 | 0.54065 | -0.033458 | 121.9961 | 122.2624 | 122.174 | -0.15041 | 0.02849 | -122.2028 | 0.097175 | 0.10603 | 0.077542 | -122.1905 | -122.0947 | -0.040549 | -0.28173 | 0.19333 | 0.076405 | 0.11695 | -0.015438 | -0.10381 | 0.18488 | 0.19722 | 0.29304 | 0.12501 | -122.3592 | 122.106 | 122.3723 | 122.2839 | 0.65051 | -122.4282
3220.1562 | 122.3328 | -0.082397 | 122.2733 | -0.033042 | -0.049897 | 0.04008 | 0.019682 | -0.012719 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.058046 | 0.045602 | 0.047901 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.091937 | 0.19233 | -0.085952 | 0.083464 | 0.53607 | -0.028879 | 121.9961 | 122.2716 | 122.174 | -0.15041 | -0.003555 | -122.1891 | 0.065131 | 0.064831 | 0.068386 | -122.1813 | -122.0809 | -0.068015 | -0.27715 | 0.16586 | 0.053518 | 0.12153 | -0.001703 | -0.099231 | 0.16657 | 0.17433 | 0.27473 | 0.1067 | -122.3592 | 122.0785 | 122.3539 | 122.2564 | 0.61847 | -122.4237
3221.8594 | 122.3602 | -0.091553 | 122.2595 | -0.010149 | -0.049897 | 0.04008 | 0.019682 | -0.012933 | -0.0029443 | -0.0062567 | -0.0022666 | -0.0020767 | 0.057832 | 0.045602 | 0.047687 | -0.012688 | 0.0243 | -0.012988 | 0.07502 | 0.1011 | 0.18775 | -0.085952 | 0.088043 | 0.53149 | -0.028879 | 121.9915 | 122.2624 | 122.174 | -0.15041 | 0.005601 | -122.1845 | 0.078865 | 0.078565 | 0.072964 | -122.1584 | -122.0718 | -0.058859 | -0.268 | 0.1796 | 0.062674 | 0.12153 | 0.002873 | -0.085498 | 0.16657 | 0.19265 | 0.27931 | 0.11585 | -122.3455 | 122.0831 | 122.3539 | 122.2656 | 0.62304 | -122.4099
3223.625 | 122.3419 | -0.10529 | 122.2961 | -0.0025182 | -0.049683 | 0.04008 | 0.019682 | -0.012719 | -0.0027305 | -0.021518 | -0.002053 | -0.0020767 | 0.05826 | 0.045388 | 0.047687 | -0.012688 | 0.0243 | -0.008409 | 0.070441 | 0.091937 | 0.18775 | -0.081373 | 0.074307 | 0.53149 | -0.033458 | 121.9961 | 122.2624 | 122.1694 | -0.14583 | 0.023913 | -122.2257 | 0.092598 | 0.096877 | 0.072964 | -122.2042 | -122.1084 | -0.040547 | -0.30004 | 0.17959 | 0.071828 | 0.11237 | -0.033749 | -0.1267 | 0.17573 | 0.19722 | 0.29304 | 0.12959 | -122.3775 | 122.1014 | 122.3677 | 122.2747 | 0.63677 | -122.442
3225.3281 | 122.4197 | -0.064087 | 122.2504 | -0.01778 | -0.050111 | 0.040507 | 0.019682 | -0.013147 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.045388 | 0.047687 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.091937 | 0.18775 | -0.085952 | 0.083464 | 0.54065 | -0.033458 | 122.0007 | 122.267 | 122.1786 | -0.14583 | -0.021865 | -122.1753 | 0.046821 | 0.051099 | 0.072964 | -122.1584 | -122.0626 | -0.081746 | -0.24969 | 0.14755 | 0.030629 | 0.11237 | 0.016606 | -0.071764 | 0.13911 | 0.15602 | 0.25184 | 0.079229 | -122.3363 | 122.0648 | 122.3311 | 122.2427 | 0.60473 | -122.3962
3227.0938 | 122.4609 | -0.050354 | 122.2412 | -0.01778 | -0.049897 | 0.040507 | 0.019682 | -0.012719 | -0.0033715 | -0.013887 | -0.0022666 | -0.0022903 | 0.05826 | 0.046029 | 0.047901 | -0.021844 | 0.015142 | -0.012988 | 0.079598 | 0.091937 | 0.19233 | -0.081373 | 0.092622 | 0.53607 | -0.0243 | 122.0007 | 122.267 | 122.1694 | -0.15041 | -0.031019 | -122.1616 | 0.02851 | 0.037366 | 0.068385 | -122.1493 | -122.0489 | -0.10006 | -0.24053 | 0.14298 | 0.026054 | 0.12611 | 0.025761 | -0.071767 | 0.12995 | 0.14229 | 0.24269 | 0.065496 | -122.3226 | 122.051 | 122.3173 | 122.2198 | 0.58642 | -122.3916
3228.7812 | 122.3145 | -0.10529 | 122.2778 | -0.01778 | -0.050538 | 0.040293 | 0.02011 | -0.012933 | -0.0029443 | -0.029148 | -0.0024804 | -0.0027177 | 0.057832 | 0.045816 | 0.048328 | -0.017266 | 0.0243 | -0.008409 | 0.084176 | 0.087359 | 0.19233 | -0.085952 | 0.078886 | 0.54065 | -0.033458 | 121.9961 | 122.2716 | 122.1786 | -0.14583 | 0.019334 | -122.1937 | 0.08802 | 0.096877 | 0.077543 | -122.1905 | -122.0855 | -0.040547 | -0.28173 | 0.18417 | 0.071828 | 0.11237 | -0.006281 | -0.09923 | 0.18946 | 0.19265 | 0.29762 | 0.12959 | -122.3638 | 122.1014 | 122.3768 | 122.2839 | 0.64593 | -122.4237
3230.5312 | 122.3282 | -0.10071 | 122.2778 | -0.010149 | -0.04947 | 0.040293 | 0.019896 | -0.012933 | -0.0027305 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.045602 | 0.047687 | -0.017266 | 0.019721 | -0.008409 | 0.079598 | 0.096516 | 0.18775 | -0.076794 | 0.092622 | 0.54065 | -0.028879 | 121.9961 | 122.2761 | 122.174 | -0.14583 | 0.023914 | -122.1982 | 0.083442 | 0.092299 | 0.068385 | -122.1813 | -122.0901 | -0.045125 | -0.28173 | 0.19333 | 0.071829 | 0.11695 | -0.001702 | -0.10381 | 0.18031 | 0.19722 | 0.28846 | 0.12043 | -122.3546 | 122.0968 | 122.3768 | 122.2747 | 0.64136 | -122.4237
3232.2812 | 122.3557 | -0.091553 | 122.2412 | -0.010149 | -0.050111 | 0.04008 | 0.019896 | -0.013147 | -0.0031579 | -0.021518 | -0.0024804 | -0.0020767 | 0.057832 | 0.046029 | 0.048328 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.08278 | 0.18775 | -0.081373 | 0.092622 | 0.54522 | -0.033458 | 122.0007 | 122.2716 | 122.174 | -0.15957 | 0.01018 | -122.1662 | 0.074287 | 0.078565 | 0.068385 | -122.1584 | -122.0535 | -0.068017 | -0.24053 | 0.18417 | 0.058095 | 0.12611 | 0.03034 | -0.067188 | 0.16657 | 0.17433 | 0.27931 | 0.11127 | -122.3226 | 122.0922 | 122.3631 | 122.2656 | 0.63678 | -122.4008
3234.0469 | 122.3282 | -0.11444 | 122.2641 | -0.010149 | -0.049897 | 0.040293 | 0.019682 | -0.012719 | -0.0031579 | -0.0062567 | -0.0022666 | -0.0020767 | 0.057619 | 0.045816 | 0.047901 | -0.012688 | 0.019721 | -0.017566 | 0.07502 | 0.08278 | 0.19233 | -0.081373 | 0.083464 | 0.54065 | -0.033458 | 122.0007 | 122.267 | 122.1786 | -0.15041 | 0.033068 | -122.1891 | 0.10175 | 0.096875 | 0.063807 | -122.1813 | -122.0718 | -0.035971 | -0.26342 | 0.1979 | 0.080983 | 0.11695 | 0.002873 | -0.085497 | 0.18946 | 0.19722 | 0.30677 | 0.13416 | -122.3455 | 122.1151 | 122.3814 | 122.293 | 0.65509 | -122.4145
3235.7344 | 122.4518 | -0.07782 | 122.2275 | -0.01778 | -0.050111 | 0.04008 | 0.019682 | -0.012719 | -0.0029443 | -0.013887 | -0.002053 | -0.0025041 | 0.05826 | 0.045175 | 0.047687 | -0.017266 | 0.015142 | -0.008409 | 0.079598 | 0.091937 | 0.19233 | -0.076794 | 0.083464 | 0.53607 | -0.038036 | 121.9961 | 122.267 | 122.174 | -0.15041 | 0.001026 | -122.1479 | 0.060554 | 0.069411 | 0.068385 | -122.1355 | -122.0351 | -0.072592 | -0.23138 | 0.16128 | 0.039784 | 0.11238 | 0.039494 | -0.053455 | 0.15742 | 0.16976 | 0.27015 | 0.092962 | -122.3043 | 122.0739 | 122.3448 | 122.2518 | 0.61389 | -122.3779
3237.5 | 122.3282 | -0.10529 | 122.2733 | -0.01778 | -0.049897 | 0.040293 | 0.019896 | -0.012933 | -0.0029443 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058046 | 0.045816 | 0.048115 | -0.017266 | 0.028878 | -0.012988 | 0.07502 | 0.087359 | 0.19691 | -0.081373 | 0.078886 | 0.54065 | -0.028879 | 122.0053 | 122.2624 | 122.1786 | -0.15041 | 0.023913 | -122.1982 | 0.08802 | 0.092298 | 0.068385 | -122.1859 | -122.0763 | -0.045126 | -0.268 | 0.18417 | 0.076407 | 0.12153 | -0.01086 | -0.094652 | 0.18031 | 0.19265 | 0.30219 | 0.13416 | -122.3546 | 122.1105 | 122.3677 | 122.2839 | 0.64593 | -122.4237
3239.2656 | 122.3923 | -0.082397 | 122.2595 | -0.010149 | -0.049897 | 0.040293 | 0.02011 | -0.012719 | -0.0029443 | -0.021518 | -0.0022666 | -0.0018631 | 0.058046 | 0.045602 | 0.047687 | -0.021844 | 0.015142 | -0.012988 | 0.070441 | 0.091937 | 0.18775 | -0.085952 | 0.083464 | 0.54065 | -0.033458 | 122.0053 | 122.2716 | 122.174 | -0.15041 | -0.003555 | -122.1891 | 0.060553 | 0.069409 | 0.072964 | -122.1676 | -122.0718 | -0.068015 | -0.25427 | 0.16586 | 0.048939 | 0.11695 | 0.01203 | -0.085498 | 0.15284 | 0.17433 | 0.27015 | 0.097539 | -122.3455 | 122.0877 | 122.3539 | 122.2564 | 0.62304 | -122.4099
3241.0312 | 122.4838 | -0.050354 | 122.2275 | -0.010149 | -0.050111 | 0.040293 | 0.019682 | -0.012933 | -0.0031579 | -0.021518 | -0.0024804 | -0.0016495 | 0.058046 | 0.045816 | 0.047901 | -0.012688 | 0.019721 | -0.003831 | 0.079598 | 0.08278 | 0.18775 | -0.081373 | 0.088043 | 0.54065 | -0.038036 | 122.0007 | 122.2761 | 122.1786 | -0.15041 | -0.031019 | -122.1479 | 0.037666 | 0.046523 | 0.077542 | -122.1447 | -122.0397 | -0.10006 | -0.2268 | 0.1384 | 0.012318 | 0.11238 | 0.048652 | -0.048876 | 0.12995 | 0.13313 | 0.23811 | 0.070075 | -122.3089 | 122.051 | 122.3265 | 122.229 | 0.591 | -122.3779
3242.7969 | 122.4701 | -0.032043 | 122.2458 | -0.010149 | -0.050111 | 0.040507 | 0.019682 | -0.012933 | -0.0029443 | -0.021518 | -0.0022666 | -0.0022903 | 0.058046 | 0.045816 | 0.047687 | -0.017266 | 0.0243 | -0.012988 | 0.07502 | 0.091937 | 0.18775 | -0.085952 | 0.078886 | 0.54522 | -0.028879 | 121.9961 | 122.2624 | 122.1786 | -0.15041 | -0.053909 | -122.1708 | 0.014777 | 0.019055 | 0.072964 | -122.1539 | -122.058 | -0.11837 | -0.24969 | 0.11093 | 0.003164 | 0.12153 | 0.016605 | -0.067187 | 0.10706 | 0.12398 | 0.2198 | 0.056343 | -122.3317 | 122.0281 | 122.2944 | 122.2106 | 0.57727 | -122.3962
3244.5 | 122.3923 | -0.073242 | 122.2549 | -0.010149 | -0.049897 | 0.04008 | 0.019469 | -0.013147 | -0.0035853 | -0.029148 | -0.0024804 | -0.0022903 | 0.05826 | 0.046029 | 0.047687 | -0.021844 | 0.019721 | -0.012988 | 0.07502 | 0.091937 | 0.18775 | -0.076794 | 0.088043 | 0.54522 | -0.028879 | 122.0007 | 122.2716 | 122.1832 | -0.15041 | -0.003552 | -122.1799 | 0.051398 | 0.060254 | 0.063806 | -122.163 | -122.0672 | -0.07717 | -0.25427 | 0.16129 | 0.044363 | 0.12153 | 0.016607 | -0.071764 | 0.14826 | 0.16518 | 0.26099 | 0.092963 | -122.3317 | 122.0739 | 122.3448 | 122.2564 | 0.61847 | -122.4054
3246.2656 | 122.3419 | -0.09613 | 122.2824 | -0.0025182 | -0.050111 | 0.04008 | 0.019682 | -0.012719 | -0.0035853 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.046243 | 0.048115 | -0.017266 | 0.015142 | -0.017566 | 0.07502 | 0.091937 | 0.18775 | -0.076794 | 0.083464 | 0.54522 | -0.033458 | 122.0053 | 122.267 | 122.1786 | -0.14583 | 0.019336 | -122.2074 | 0.078864 | 0.078564 | 0.059228 | -122.1905 | -122.0947 | -0.049703 | -0.27715 | 0.17959 | 0.062672 | 0.11237 | -0.015438 | -0.10381 | 0.17115 | 0.18807 | 0.28388 | 0.11127 | -122.3592 | 122.1014 | 122.3631 | 122.2747 | 0.64135 | -122.4282
3248.0312 | 122.3282 | -0.07782 | 122.2778 | -0.0025182 | -0.050538 | 0.04008 | 0.019682 | -0.012933 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.058046 | 0.046029 | 0.048115 | -0.012688 | 0.028878 | -0.008409 | 0.079598 | 0.096516 | 0.18317 | -0.081373 | 0.088043 | 0.54065 | -0.038036 | 121.9961 | 122.2716 | 122.1786 | -0.14583 | -0.003553 | -122.1982 | 0.065132 | 0.069411 | 0.072964 | -122.1813 | -122.0947 | -0.068013 | -0.28173 | 0.16586 | 0.039784 | 0.1078 | -0.006281 | -0.09923 | 0.15742 | 0.17434 | 0.26099 | 0.1067 | -122.3592 | 122.0739 | 122.3494 | 122.2564 | 0.61847 | -122.4237
3249.7344 | 122.3785 | -0.086975 | 122.2504 | -0.0025182 | -0.050111 | 0.040507 | 0.019682 | -0.012719 | -0.0029443 | -0.013887 | -0.002053 | -0.0020767 | 0.058046 | 0.045816 | 0.048115 | -0.012688 | 0.0243 | -0.012988 | 0.079598 | 0.096516 | 0.18317 | -0.081373 | 0.092622 | 0.5498 | -0.028879 | 121.9961 | 122.267 | 122.174 | -0.14583 | 0.005602 | -122.1708 | 0.074287 | 0.073987 | 0.068385 | -122.1539 | -122.0672 | -0.058858 | -0.25427 | 0.1796 | 0.058096 | 0.11695 | 0.016606 | -0.076343 | 0.16657 | 0.18349 | 0.27015 | 0.11127 | -122.3317 | 122.0831 | 122.3539 | 122.261 | 0.63678 | -122.3962
3251.4844 | 122.4152 | -0.086975 | 122.2549 | -0.010149 | -0.050111 | 0.040293 | 0.02011 | -0.012933 | -0.0031579 | -0.021518 | -0.0024804 | -0.0020767 | 0.058046 | 0.045816 | 0.047687 | -0.012688 | 0.0243 | -0.003831 | 0.070441 | 0.087359 | 0.19233 | -0.085952 | 0.083464 | 0.54522 | -0.042615 | 122.0053 | 122.2624 | 122.1786 | -0.15499 | 0.001023 | -122.1845 | 0.074287 | 0.083144 | 0.082121 | -122.1676 | -122.0626 | -0.068016 | -0.24969 | 0.17044 | 0.04436 | 0.11238 | 0.00745 | -0.076342 | 0.15742 | 0.17433 | 0.27931 | 0.11127 | -122.3409 | 122.0922 | 122.3494 | 122.2656 | 0.6322 | -122.4099
3253.2344 | 122.3602 | -0.091553 | 122.2412 | 0.0051128 | -0.050111 | 0.040293 | 0.019896 | -0.013147 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.058046 | 0.045816 | 0.048115 | -0.017266 | 0.0243 | -0.012988 | 0.070441 | 0.091937 | 0.19691 | -0.081373 | 0.088043 | 0.54522 | -0.028879 | 122.0007 | 122.267 | 122.174 | -0.15499 | 0.01018 | -122.1708 | 0.074287 | 0.078565 | 0.068385 | -122.1493 | -122.0443 | -0.063438 | -0.24053 | 0.1796 | 0.062674 | 0.12611 | 0.025761 | -0.067188 | 0.16199 | 0.18349 | 0.28846 | 0.11585 | -122.3226 | 122.0922 | 122.3585 | 122.2656 | 0.63678 | -122.3962
3255 | 122.3465 | -0.10986 | 122.2824 | -0.01778 | -0.050111 | 0.039866 | 0.019682 | -0.012933 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.045816 | 0.048115 | -0.012688 | 0.015142 | -0.017566 | 0.079598 | 0.091937 | 0.19233 | -0.085952 | 0.088043 | 0.5498 | -0.033458 | 122.0098 | 122.267 | 122.174 | -0.15499 | 0.023911 | -122.2028 | 0.097175 | 0.092297 | 0.068386 | -122.1905 | -122.0901 | -0.045128 | -0.27258 | 0.19791 | 0.076405 | 0.12153 | -0.015438 | -0.10839 | 0.18946 | 0.2018 | 0.30219 | 0.12501 | -122.3684 | 122.1197 | 122.3768 | 122.2839 | 0.65967 | -122.4374
3256.7031 | 122.3419 | -0.10071 | 122.2733 | -0.01778 | -0.050111 | 0.040293 | 0.019896 | -0.012719 | -0.0027305 | -0.013887 | -0.0024804 | -0.0025041 | 0.05826 | 0.046029 | 0.047901 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.091937 | 0.18775 | -0.081373 | 0.088043 | 0.5498 | -0.028879 | 122.0144 | 122.2716 | 122.1786 | -0.15499 | 0.019335 | -122.1982 | 0.083442 | 0.08772 | 0.068385 | -122.1813 | -122.0855 | -0.054283 | -0.25884 | 0.18875 | 0.071829 | 0.12611 | -0.001703 | -0.094652 | 0.17573 | 0.19265 | 0.28846 | 0.11585 | -122.3546 | 122.1151 | 122.3723 | 122.2793 | 0.65051 | -122.4282
3258.4688 | 122.4152 | -0.068665 | 122.2549 | -0.010149 | -0.050111 | 0.040507 | 0.019896 | -0.013147 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.05826 | 0.045816 | 0.047687 | -0.008109 | 0.019721 | -0.012988 | 0.070441 | 0.091937 | 0.18775 | -0.076794 | 0.088043 | 0.54522 | -0.033458 | 122.0144 | 122.2624 | 122.174 | -0.15041 | -0.008129 | -122.1845 | 0.060556 | 0.055677 | 0.063806 | -122.163 | -122.0672 | -0.081747 | -0.24053 | 0.15671 | 0.035207 | 0.11695 | 0.00745 | -0.080921 | 0.13911 | 0.1606 | 0.25642 | 0.088386 | -122.3317 | 122.0831 | 122.3311 | 122.2427 | 0.61389 | -122.4054
3260.1719 | 122.3511 | -0.09613 | 122.2687 | -0.010149 | -0.050324 | 0.04008 | 0.019896 | -0.012933 | -0.0033715 | -0.021518 | -0.0022666 | -0.0016495 | 0.058046 | 0.046029 | 0.047901 | -0.012688 | 0.019721 | -0.012988 | 0.065863 | 0.1011 | 0.19233 | -0.081373 | 0.083464 | 0.54522 | -0.033458 | 122.0053 | 122.267 | 122.1786 | -0.15957 | 0.014757 | -122.2028 | 0.083442 | 0.083142 | 0.068385 | -122.1676 | -122.0763 | -0.06344 | -0.26342 | 0.17959 | 0.062672 | 0.12611 | -0.001705 | -0.090075 | 0.16199 | 0.19722 | 0.28846 | 0.11585 | -122.35 | 122.1014 | 122.3631 | 122.2747 | 0.64135 | -122.4282
3261.9375 | 122.4472 | -0.045776 | 122.2229 | -0.010149 | -0.050538 | 0.040293 | 0.019896 | -0.012933 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.045816 | 0.047901 | -0.021844 | 0.015142 | -0.012988 | 0.07502 | 0.087359 | 0.19691 | -0.081373 | 0.088043 | 0.5498 | -0.028879 | 122.0144 | 122.2761 | 122.1786 | -0.15041 | -0.035597 | -122.1479 | 0.023932 | 0.032788 | 0.068385 | -122.1355 | -122.026 | -0.10464 | -0.20849 | 0.13382 | 0.016897 | 0.12153 | 0.05323 | -0.044298 | 0.1208 | 0.13314 | 0.24268 | 0.060918 | -122.3043 | 122.0602 | 122.3219 | 122.2244 | 0.59558 | -122.3733
3263.7031 | 122.3373 | -0.086975 | 122.2504 | -0.01778 | -0.049897 | 0.039866 | 0.019682 | -0.013147 | -0.0033715 | -0.021518 | -0.0024804 | -0.0025041 | 0.05826 | 0.045816 | 0.047687 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.087359 | 0.19233 | -0.081373 | 0.083464 | 0.5498 | -0.038036 | 122.0144 | 122.2761 | 122.1786 | -0.15499 | 0.005602 | -122.1753 | 0.069709 | 0.073987 | 0.068385 | -122.163 | -122.058 | -0.068016 | -0.23595 | 0.17044 | 0.048939 | 0.11695 | 0.025764 | -0.071764 | 0.162 | 0.17433 | 0.27931 | 0.1067 | -122.3317 | 122.1014 | 122.3631 | 122.2656 | 0.63678 | -122.4054
3265.3906 | 122.4701 | -0.064087 | 122.2412 | -0.010149 | -0.050324 | 0.040293 | 0.02011 | -0.013147 | -0.0031579 | -0.021518 | -0.0024804 | -0.0025041 | 0.058046 | 0.046029 | 0.047901 | -0.021844 | 0.019721 | -0.003831 | 0.07502 | 0.08278 | 0.19691 | -0.081373 | 0.083464 | 0.5498 | -0.033458 | 122.0144 | 122.2761 | 122.1832 | -0.15499 | -0.017286 | -122.1662 | 0.042243 | 0.060256 | 0.077542 | -122.1584 | -122.0443 | -0.090904 | -0.2268 | 0.14755 | 0.030629 | 0.12153 | 0.034919 | -0.058031 | 0.13911 | 0.14687 | 0.261 | 0.083808 | -122.3226 | 122.0785 | 122.3402 | 122.2473 | 0.61389 | -122.3962
3267.1562 | 122.3465 | -0.10529 | 122.287 | -0.0025182 | -0.050111 | 0.040293 | 0.019682 | -0.012933 | -0.0029443 | -0.013887 | -0.002694 | -0.0025041 | 0.058046 | 0.046029 | 0.047901 | -0.017266 | 0.019721 | -0.017566 | 0.070441 | 0.091937 | 0.18317 | -0.081373 | 0.092622 | 0.5498 | -0.033458 | 122.0098 | 122.267 | 122.1786 | -0.15499 | 0.023913 | -122.2165 | 0.08802 | 0.08772 | 0.063807 | -122.195 | -122.1038 | -0.049705 | -0.27715 | 0.19791 | 0.071828 | 0.12153 | -0.020015 | -0.10838 | 0.17573 | 0.19722 | 0.28846 | 0.12501 | -122.3684 | 122.1151 | 122.3723 | 122.2839 | 0.65509 | -122.442
3268.9219 | 122.4609 | -0.059509 | 122.2275 | -0.0025182 | -0.050111 | 0.04008 | 0.019682 | -0.012719 | -0.0031579 | -0.021518 | -0.0022666 | -0.0025041 | 0.05826 | 0.045602 | 0.047687 | -0.017266 | 0.0243 | -0.008409 | 0.07502 | 0.091937 | 0.19233 | -0.085952 | 0.088043 | 0.55438 | -0.033458 | 122.0098 | 122.2716 | 122.174 | -0.14583 | -0.026443 | -122.1525 | 0.042243 | 0.0511 | 0.077543 | -122.1355 | -122.0351 | -0.086324 | -0.21764 | 0.14755 | 0.026051 | 0.11237 | 0.044073 | -0.053455 | 0.13453 | 0.15145 | 0.25184 | 0.083809 | -122.3134 | 122.0693 | 122.3311 | 122.2335 | 0.61389 | -122.3733
3270.6719 | 122.4335 | -0.054932 | 122.2229 | -0.01778 | -0.050324 | 0.040293 | 0.019682 | -0.012933 | -0.0033715 | -0.029148 | -0.002053 | -0.0025041 | 0.058046 | 0.046029 | 0.048115 | -0.017266 | 0.015142 | -0.012988 | 0.084176 | 0.087359 | 0.18775 | -0.076794 | 0.092622 | 0.54522 | -0.047194 | 122.0053 | 122.2716 | 122.1786 | -0.15041 | -0.021862 | -122.1387 | 0.037666 | 0.041944 | 0.063806 | -122.1355 | -122.0351 | -0.09548 | -0.21764 | 0.14755 | 0.007738 | 0.10322 | 0.048651 | -0.044298 | 0.13911 | 0.14229 | 0.24268 | 0.070074 | -122.2997 | 122.0602 | 122.3265 | 122.2335 | 0.60016 | -122.3733
3272.375 | 122.3557 | -0.091553 | 122.2778 | -0.010149 | -0.050111 | 0.040293 | 0.019682 | -0.01336 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.05826 | 0.045816 | 0.047901 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.096516 | 0.19691 | -0.081373 | 0.088043 | 0.54065 | -0.038036 | 122.0144 | 122.2761 | 122.1832 | -0.14583 | 0.01018 | -122.2028 | 0.074287 | 0.078565 | 0.068385 | -122.1813 | -122.0809 | -0.05428 | -0.26342 | 0.1796 | 0.053517 | 0.1078 | -0.001702 | -0.094652 | 0.16657 | 0.18807 | 0.28846 | 0.11127 | -122.3592 | 122.106 | 122.3677 | 122.2747 | 0.6322 | -122.4237
3274.1406 | 122.4472 | -0.045776 | 122.2366 | -0.01778 | -0.050324 | 0.040293 | 0.019896 | -0.012933 | -0.0027305 | -0.013887 | -0.0024804 | -0.0027177 | 0.057832 | 0.045816 | 0.048115 | -0.012688 | 0.019721 | -0.012988 | 0.079598 | 0.096516 | 0.20149 | -0.076794 | 0.078886 | 0.55896 | -0.033458 | 122.0144 | 122.267 | 122.1786 | -0.15041 | -0.031018 | -122.157 | 0.033088 | 0.032788 | 0.063806 | -122.1401 | -122.0351 | -0.10464 | -0.22222 | 0.12466 | 0.012318 | 0.11695 | 0.030339 | -0.058031 | 0.12537 | 0.14229 | 0.24726 | 0.065497 | -122.3134 | 122.0602 | 122.3127 | 122.2244 | 0.60474 | -122.387
3275.875 | 122.3373 | -0.10986 | 122.2641 | -0.01778 | -0.050111 | 0.039866 | 0.019682 | -0.012933 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.045816 | 0.048115 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.091937 | 0.18775 | -0.081373 | 0.083464 | 0.55438 | -0.028879 | 122.0098 | 122.2761 | 122.1832 | -0.15499 | 0.02849 | -122.1891 | 0.092597 | 0.096875 | 0.068385 | -122.1722 | -122.0763 | -0.045128 | -0.25426 | 0.19333 | 0.080984 | 0.12611 | 0.012031 | -0.080919 | 0.18488 | 0.2018 | 0.29762 | 0.12501 | -122.3455 | 122.1197 | 122.386 | 122.293 | 0.66425 | -122.4191
3277.6406 | 122.319 | -0.086975 | 122.2504 | -0.010149 | -0.050324 | 0.04008 | 0.02011 | -0.012933 | -0.0031579 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058046 | 0.046029 | 0.047901 | -0.017266 | 0.019721 | -0.008409 | 0.079598 | 0.096516 | 0.19691 | -0.076794 | 0.088043 | 0.54522 | -0.028879 | 122.0053 | 122.2761 | 122.1832 | -0.15041 | 0.010181 | -122.1708 | 0.069709 | 0.078566 | 0.068385 | -122.1539 | -122.0535 | -0.063437 | -0.24511 | 0.17502 | 0.058096 | 0.12153 | 0.025764 | -0.067186 | 0.16657 | 0.18349 | 0.28388 | 0.1067 | -122.3272 | 122.0922 | 122.3631 | 122.2702 | 0.6322 | -122.4008
3279.4219 | 122.4884 | -0.050354 | 122.2 | -0.0025182 | -0.050324 | 0.040293 | 0.019469 | -0.012719 | -0.0029443 | -0.029148 | -0.002053 | -0.0022903 | 0.05826 | 0.045816 | 0.047687 | -0.026423 | 0.019721 | -0.008409 | 0.079598 | 0.087359 | 0.18775 | -0.081373 | 0.092622 | 0.55438 | -0.033458 | 122.0098 | 122.2624 | 122.174 | -0.14125 | -0.031019 | -122.1204 | 0.023931 | 0.041945 | 0.072964 | -122.1127 | -122.0123 | -0.090901 | -0.19018 | 0.14298 | 0.016896 | 0.1078 | 0.062382 | -0.025989 | 0.12995 | 0.13771 | 0.23811 | 0.070075 | -122.2814 | 122.0602 | 122.3127 | 122.2244 | 0.60474 | -122.3413
3281.125 | 122.3648 | -0.09613 | 122.2321 | -0.010149 | -0.050324 | 0.04008 | 0.019682 | -0.013147 | -0.0033715 | -0.013887 | -0.0024804 | -0.0022903 | 0.057619 | 0.045816 | 0.048115 | -0.017266 | 0.015142 | -0.008409 | 0.079598 | 0.091937 | 0.19691 | -0.081373 | 0.088043 | 0.55438 | -0.033458 | 122.0098 | 122.267 | 122.1786 | -0.15041 | 0.014757 | -122.1525 | 0.078864 | 0.087721 | 0.072964 | -122.1401 | -122.0351 | -0.054282 | -0.22222 | 0.18417 | 0.062672 | 0.11695 | 0.034916 | -0.053454 | 0.17573 | 0.18807 | 0.29304 | 0.11127 | -122.3134 | 122.106 | 122.3631 | 122.2747 | 0.65051 | -122.3825
3282.875 | 122.3511 | -0.09613 | 122.2595 | -0.010149 | -0.050324 | 0.040507 | 0.019682 | -0.012933 | -0.0029443 | -0.0062567 | -0.002053 | -0.0022903 | 0.05826 | 0.046029 | 0.048328 | -0.008109 | 0.019721 | -0.012988 | 0.079598 | 0.096516 | 0.19233 | -0.081373 | 0.088043 | 0.55438 | -0.028879 | 122.019 | 122.2716 | 122.1786 | -0.15499 | 0.014757 | -122.1799 | 0.088021 | 0.083142 | 0.068385 | -122.163 | -122.0672 | -0.058861 | -0.24053 | 0.18417 | 0.067251 | 0.12611 | 0.01203 | -0.080919 | 0.17573 | 0.19265 | 0.28846 | 0.11585 | -122.3409 | 122.1151 | 122.3677 | 122.2747 | 0.65051 | -122.4145
3284.6406 | 122.4838 | -0.032043 | 122.2183 | -0.010149 | -0.050538 | 0.04008 | 0.019896 | -0.013147 | -0.0027305 | -0.013887 | -0.0022666 | -0.0020767 | 0.05826 | 0.046243 | 0.048115 | -0.021844 | 0.019721 | -0.008409 | 0.079598 | 0.096516 | 0.18775 | -0.085952 | 0.083464 | 0.54065 | -0.033458 | 122.0098 | 122.2624 | 122.174 | -0.14583 | -0.053909 | -122.1387 | 0.010199 | 0.023634 | 0.077543 | -122.1218 | -122.0306 | -0.11379 | -0.20849 | 0.11551 | -0.001415 | 0.11237 | 0.044071 | -0.0443 | 0.11164 | 0.12856 | 0.2198 | 0.051764 | -122.3043 | 122.0419 | 122.2944 | 122.2061 | 0.57269 | -122.3642
3286.3906 | 122.438 | -0.036621 | 122.2137 | -0.01778 | -0.050538 | 0.04008 | 0.019255 | -0.012933 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.057832 | 0.045816 | 0.047687 | -0.021844 | 0.019721 | -0.012988 | 0.07502 | 0.091937 | 0.19233 | -0.067636 | 0.078886 | 0.54522 | -0.028879 | 122.0144 | 122.2807 | 122.1786 | -0.15499 | -0.031015 | -122.1387 | 0.014777 | 0.023633 | 0.054648 | -122.1218 | -122.0214 | -0.11837 | -0.19933 | 0.11551 | 0.007742 | 0.12611 | 0.066963 | -0.035143 | 0.11164 | 0.12856 | 0.22895 | 0.056342 | -122.2814 | 122.051 | 122.3173 | 122.2152 | 0.58185 | -122.3687
3288.0781 | 122.3648 | -0.09613 | 122.2778 | -0.010149 | -0.050111 | 0.040721 | 0.019896 | -0.012719 | -0.0033715 | -0.021518 | -0.002694 | -0.0025041 | 0.057832 | 0.045602 | 0.048115 | -0.017266 | 0.015142 | -0.008409 | 0.07502 | 0.091937 | 0.19233 | -0.090531 | 0.088043 | 0.5498 | -0.028879 | 122.0144 | 122.2761 | 122.1878 | -0.15041 | 0.005599 | -122.2028 | 0.078864 | 0.087721 | 0.082122 | -122.1859 | -122.0855 | -0.054282 | -0.26342 | 0.18417 | 0.067251 | 0.12153 | -0.001702 | -0.090073 | 0.17115 | 0.18807 | 0.28846 | 0.11127 | -122.3684 | 122.1105 | 122.3723 | 122.2839 | 0.64593 | -122.4282
3289.8438 | 122.4426 | -0.054932 | 122.2321 | -0.01778 | -0.050538 | 0.04008 | 0.019682 | -0.012933 | -0.0031579 | -0.0062567 | -0.002053 | -0.0027177 | 0.05826 | 0.046029 | 0.047687 | -0.021844 | 0.019721 | -0.017566 | 0.079598 | 0.096516 | 0.19233 | -0.085952 | 0.078886 | 0.5498 | -0.028879 | 122.0144 | 122.2624 | 122.1832 | -0.15957 | -0.03102 | -122.1525 | 0.033088 | 0.037366 | 0.068386 | -122.1355 | -122.0397 | -0.10464 | -0.21764 | 0.13382 | 0.026053 | 0.13069 | 0.030338 | -0.048876 | 0.13453 | 0.15145 | 0.24726 | 0.074653 | -122.318 | 122.0693 | 122.3173 | 122.2381 | 0.60474 | -122.3916
3291.6094 | 122.3602 | -0.07782 | 122.2824 | -0.0025182 | -0.050752 | 0.040293 | 0.019255 | -0.012933 | -0.0031579 | -0.013887 | -0.0024804 | -0.0020767 | 0.058046 | 0.046243 | 0.047687 | -0.017266 | 0.019721 | -0.017566 | 0.079598 | 0.087359 | 0.19691 | -0.090531 | 0.083464 | 0.5498 | -0.033458 | 122.019 | 122.2807 | 122.1832 | -0.15041 | -0.012711 | -122.2028 | 0.060554 | 0.060254 | 0.072965 | -122.1951 | -122.0855 | -0.072592 | -0.26342 | 0.16128 | 0.044362 | 0.11695 | -0.001702 | -0.09923 | 0.15742 | 0.16518 | 0.27473 | 0.097541 | -122.3729 | 122.0968 | 122.3585 | 122.261 | 0.62762 | -122.4328
3293.375 | 122.3511 | -0.068665 | 122.2549 | -0.010149 | -0.050538 | 0.040293 | 0.02011 | -0.012719 | -0.0031579 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058046 | 0.046029 | 0.047474 | -0.021844 | 0.015142 | -0.017566 | 0.088755 | 0.091937 | 0.19233 | -0.076794 | 0.078886 | 0.55438 | -0.0243 | 122.0053 | 122.267 | 122.1786 | -0.15499 | -0.008129 | -122.1662 | 0.046821 | 0.051099 | 0.059228 | -122.163 | -122.0626 | -0.086326 | -0.24969 | 0.14755 | 0.044365 | 0.13069 | 0.012028 | -0.076342 | 0.15742 | 0.1606 | 0.261 | 0.083807 | -122.3317 | 122.0739 | 122.3356 | 122.2473 | 0.62305 | -122.4099
3295.0781 | 122.4426 | -0.032043 | 122.2412 | -0.010149 | -0.050538 | 0.040293 | 0.019469 | -0.012719 | -0.0033715 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.045816 | 0.047901 | -0.012688 | 0.015142 | -0.012988 | 0.079598 | 0.096516 | 0.19691 | -0.076794 | 0.088043 | 0.55896 | -0.042615 | 122.0144 | 122.267 | 122.174 | -0.15041 | -0.044751 | -122.1616 | 0.019355 | 0.019055 | 0.063806 | -122.1447 | -122.0443 | -0.11837 | -0.2268 | 0.12009 | -0.010572 | 0.1078 | 0.025761 | -0.067188 | 0.11164 | 0.12856 | 0.22895 | 0.047185 | -122.318 | 122.0465 | 122.299 | 122.2061 | 0.59101 | -122.3916
3296.8594 | 122.3236 | -0.10529 | 122.2504 | -0.010149 | -0.050324 | 0.040293 | 0.019682 | -0.01336 | -0.0033715 | -0.013887 | -0.002053 | -0.0025041 | 0.05826 | 0.046029 | 0.047901 | -0.017266 | 0.0243 | -0.008409 | 0.079598 | 0.096516 | 0.19233 | -0.081373 | 0.088043 | 0.55438 | -0.033458 | 122.0144 | 122.2807 | 122.1832 | -0.15499 | 0.023913 | -122.1708 | 0.08802 | 0.096877 | 0.072964 | -122.1539 | -122.058 | -0.049705 | -0.23595 | 0.19333 | 0.071828 | 0.12153 | 0.030342 | -0.067186 | 0.18488 | 0.2018 | 0.29762 | 0.12959 | -122.3317 | 122.1197 | 122.386 | 122.2885 | 0.65967 | -122.4054
3298.5625 | 122.4518 | -0.050354 | 122.2183 | -0.010149 | -0.050324 | 0.04008 | 0.019682 | -0.012933 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.05826 | 0.046243 | 0.047474 | -0.021844 | 0.010564 | -0.017566 | 0.079598 | 0.091937 | 0.20149 | -0.081373 | 0.083464 | 0.55438 | -0.033458 | 122.0144 | 122.2761 | 122.174 | -0.15499 | -0.031019 | -122.1387 | 0.02851 | 0.032788 | 0.063807 | -122.1264 | -122.0168 | -0.10464 | -0.20391 | 0.13382 | 0.016896 | 0.12153 | 0.057807 | -0.0443 | 0.12995 | 0.14229 | 0.25184 | 0.060918 | -122.2997 | 122.0648 | 122.3265 | 122.2244 | 0.60474 | -122.3733
3300.3281 | 122.4197 | -0.064087 | 122.2366 | -0.0025182 | -0.050752 | 0.040293 | 0.019682 | -0.012933 | -0.0033715 | -0.036779 | -0.0024804 | -0.0025041 | 0.058046 | 0.045816 | 0.047687 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.087359 | 0.18775 | -0.090531 | 0.088043 | 0.55438 | -0.038036 | 122.0098 | 122.2853 | 122.1832 | -0.15041 | -0.026444 | -122.1616 | 0.046821 | 0.051099 | 0.077543 | -122.1493 | -122.0489 | -0.086325 | -0.2268 | 0.15213 | 0.026051 | 0.11238 | 0.048654 | -0.053453 | 0.13911 | 0.15145 | 0.25184 | 0.083808 | -122.3272 | 122.0739 | 122.3494 | 122.2473 | 0.61847 | -122.387
3302.1094 | 122.4014 | -0.07782 | 122.2504 | -0.033042 | -0.050538 | 0.04008 | 0.019896 | -0.013147 | -0.0035853 | -0.013887 | -0.0024804 | -0.0025041 | 0.058046 | 0.046243 | 0.047687 | -0.012688 | 0.019721 | -0.017566 | 0.084176 | 0.087359 | 0.19233 | -0.081373 | 0.088043 | 0.5498 | -0.038036 | 122.0144 | 122.2761 | 122.1786 | -0.15499 | -0.003553 | -122.1662 | 0.065132 | 0.060254 | 0.063807 | -122.163 | -122.058 | -0.077171 | -0.23595 | 0.16586 | 0.039784 | 0.11695 | 0.025764 | -0.071764 | 0.162 | 0.16518 | 0.27015 | 0.097541 | -122.3317 | 122.0922 | 122.3539 | 122.2564 | 0.62762 | -122.4054
3303.8125 | 122.3785 | -0.091553 | 122.287 | -0.010149 | -0.050538 | 0.039866 | 0.019896 | -0.012933 | -0.0031579 | -0.013887 | -0.0022666 | -0.0020767 | 0.057832 | 0.046029 | 0.048115 | -0.012688 | 0.015142 | -0.017566 | 0.07502 | 0.091937 | 0.19233 | -0.081373 | 0.083464 | 0.5498 | -0.028879 | 122.0098 | 122.2807 | 122.1786 | -0.15957 | 0.01018 | -122.212 | 0.078865 | 0.073987 | 0.063807 | -122.195 | -122.0947 | -0.068017 | -0.27715 | 0.17502 | 0.062674 | 0.13069 | -0.006279 | -0.10838 | 0.16657 | 0.18349 | 0.28388 | 0.10669 | -122.3684 | 122.1014 | 122.3723 | 122.2702 | 0.64136 | -122.4466
3305.5625 | 122.4655 | -0.050354 | 122.2321 | -0.0025182 | -0.050538 | 0.040293 | 0.019469 | -0.012933 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.058046 | 0.046029 | 0.047474 | -0.026423 | 0.019721 | -0.012988 | 0.079598 | 0.091937 | 0.19233 | -0.076794 | 0.083464 | 0.55438 | -0.028879 | 122.0144 | 122.2807 | 122.174 | -0.15499 | -0.02644 | -122.1525 | 0.023931 | 0.037366 | 0.063806 | -122.1401 | -122.0397 | -0.10464 | -0.21764 | 0.13382 | 0.021475 | 0.12611 | 0.048652 | -0.058033 | 0.12995 | 0.14229 | 0.24269 | 0.070075 | -122.3089 | 122.0648 | 122.3311 | 122.2244 | 0.60474 | -122.387
3307.3125 | 122.3877 | -0.073242 | 122.2504 | -0.0025182 | -0.050752 | 0.04008 | 0.019469 | -0.012933 | -0.0033715 | -0.021518 | -0.002053 | -0.0022903 | 0.057832 | 0.046457 | 0.047901 | -0.017266 | 0.019721 | -0.012988 | 0.065863 | 0.096516 | 0.19233 | -0.081373 | 0.088043 | 0.55438 | -0.028879 | 122.019 | 122.2807 | 122.1786 | -0.15041 | -0.008131 | -122.1845 | 0.055976 | 0.060254 | 0.068385 | -122.1539 | -122.058 | -0.07717 | -0.23137 | 0.16129 | 0.044363 | 0.12153 | 0.030342 | -0.071764 | 0.13911 | 0.16976 | 0.26557 | 0.092963 | -122.3317 | 122.0922 | 122.3539 | 122.2518 | 0.62762 | -122.4008
3309.0781 | 122.3419 | -0.09613 | 122.2687 | -0.01778 | -0.050752 | 0.040934 | 0.019896 | -0.012933 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.046243 | 0.047687 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.091937 | 0.20149 | -0.081373 | 0.088043 | 0.5498 | -0.042615 | 122.0098 | 122.2761 | 122.1832 | -0.15957 | 0.014757 | -122.1937 | 0.078864 | 0.083142 | 0.068385 | -122.1767 | -122.0672 | -0.06344 | -0.25884 | 0.18417 | 0.053515 | 0.11695 | 0.007453 | -0.085497 | 0.17115 | 0.18807 | 0.29762 | 0.11585 | -122.35 | 122.106 | 122.3723 | 122.2793 | 0.64593 | -122.4282
3310.7812 | 122.406 | -0.059509 | 122.2458 | -0.01778 | -0.050752 | 0.040293 | 0.019682 | -0.012719 | -0.0031579 | -0.013887 | -0.0022666 | -0.0022903 | 0.058046 | 0.046029 | 0.047901 | -0.021844 | 0.010564 | -0.008409 | 0.070441 | 0.091937 | 0.19691 | -0.085952 | 0.083464 | 0.55438 | -0.028879 | 122.019 | 122.2716 | 122.1878 | -0.15957 | -0.026443 | -122.1753 | 0.037665 | 0.0511 | 0.077543 | -122.1539 | -122.0489 | -0.10006 | -0.2268 | 0.14297 | 0.03063 | 0.13069 | 0.025762 | -0.05803 | 0.12995 | 0.15145 | 0.25642 | 0.070073 | -122.3317 | 122.0785 | 122.3311 | 122.2473 | 0.61389 | -122.4054
3312.5312 | 122.4243 | -0.059509 | 122.2458 | -0.01778 | -0.050538 | 0.040293 | 0.019682 | -0.012933 | -0.0031579 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.046457 | 0.047687 | -0.026423 | 0.015142 | -0.017566 | 0.084176 | 0.1011 | 0.19233 | -0.085952 | 0.083464 | 0.5498 | -0.028879 | 122.019 | 122.2807 | 122.1832 | -0.15041 | -0.026443 | -122.1616 | 0.033086 | 0.041943 | 0.068386 | -122.1447 | -122.0535 | -0.090903 | -0.2268 | 0.14297 | 0.03063 | 0.12153 | 0.034919 | -0.062609 | 0.14369 | 0.1606 | 0.25184 | 0.074651 | -122.3317 | 122.0785 | 122.3402 | 122.2427 | 0.60931 | -122.3962
3314.2812 | 122.406 | -0.064087 | 122.2412 | -0.010149 | -0.050324 | 0.040293 | 0.019255 | -0.013147 | -0.0033715 | -0.0062567 | -0.0022666 | -0.0020767 | 0.057832 | 0.046457 | 0.047901 | -0.017266 | 0.0243 | -0.012988 | 0.065863 | 0.091937 | 0.18775 | -0.085952 | 0.088043 | 0.55438 | -0.033458 | 122.0144 | 122.2807 | 122.1832 | -0.15041 | -0.021865 | -122.1753 | 0.046821 | 0.051099 | 0.072964 | -122.1493 | -122.0535 | -0.086325 | -0.2268 | 0.15213 | 0.030629 | 0.11695 | 0.039497 | -0.058031 | 0.12995 | 0.15602 | 0.25184 | 0.088387 | -122.3272 | 122.0785 | 122.3448 | 122.2473 | 0.61847 | -122.3916
3316.0312 | 122.4518 | -0.041199 | 122.2595 | -0.010149 | -0.050324 | 0.040293 | 0.019682 | -0.012933 | -0.0035853 | -0.029148 | -0.0024804 | -0.0022903 | 0.058046 | 0.046243 | 0.047474 | -0.021844 | 0.019721 | -0.012988 | 0.084176 | 0.1011 | 0.19233 | -0.085952 | 0.083464 | 0.55896 | -0.033458 | 122.0144 | 122.2761 | 122.174 | -0.15957 | -0.044753 | -122.1753 | 0.019355 | 0.028211 | 0.072964 | -122.1584 | -122.0672 | -0.11837 | -0.24511 | 0.12466 | 0.007741 | 0.12611 | 0.016609 | -0.085498 | 0.12538 | 0.14229 | 0.23353 | 0.06092 | -122.3455 | 122.0556 | 122.3173 | 122.2152 | 0.60016 | -122.4191
3317.7812 | 122.4243 | -0.082397 | 122.2229 | -0.010149 | -0.050538 | 0.04008 | 0.019682 | -0.012719 | -0.0033715 | -0.029148 | -0.0022666 | -0.0020767 | 0.05826 | 0.046243 | 0.047901 | -0.017266 | 0.010564 | -0.012988 | 0.07502 | 0.091937 | 0.19691 | -0.085952 | 0.088043 | 0.55438 | -0.038036 | 122.0098 | 122.2761 | 122.174 | -0.16415 | -0.003555 | -122.1479 | 0.065131 | 0.069409 | 0.072964 | -122.131 | -122.026 | -0.081752 | -0.21307 | 0.17044 | 0.044361 | 0.12611 | 0.05323 | -0.048877 | 0.15742 | 0.17433 | 0.27931 | 0.092961 | -122.3089 | 122.0922 | 122.3585 | 122.2564 | 0.63678 | -122.387
3319.4844 | 122.4152 | -0.082397 | 122.2137 | -0.01778 | -0.050752 | 0.040293 | 0.019469 | -0.013147 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.046029 | 0.047474 | -0.017266 | 0.015142 | -0.012988 | 0.088755 | 0.096516 | 0.19691 | -0.085952 | 0.088043 | 0.55438 | -0.033458 | 122.0053 | 122.2807 | 122.174 | -0.15041 | -0.003555 | -122.125 | 0.065131 | 0.069409 | 0.072964 | -122.1172 | -122.0168 | -0.068015 | -0.20849 | 0.17044 | 0.048939 | 0.11695 | 0.066963 | -0.039722 | 0.17115 | 0.17891 | 0.27931 | 0.097539 | -122.2997 | 122.0877 | 122.3631 | 122.2564 | 0.63678 | -122.3642
3321.2344 | 122.406 | -0.064087 | 122.2092 | -0.010149 | -0.051179 | 0.040293 | 0.019469 | -0.013147 | -0.0035853 | -0.021518 | -0.002053 | -0.0027177 | 0.05826 | 0.045816 | 0.047687 | -0.017266 | 0.015142 | -0.008409 | 0.07502 | 0.091937 | 0.19233 | -0.085952 | 0.088043 | 0.56354 | -0.038036 | 122.019 | 122.2807 | 122.1832 | -0.15499 | -0.021865 | -122.1341 | 0.046821 | 0.055678 | 0.077543 | -122.1172 | -122.0168 | -0.090904 | -0.19017 | 0.15213 | 0.026051 | 0.11695 | 0.071541 | -0.025987 | 0.13911 | 0.15602 | 0.25642 | 0.079229 | -122.2951 | 122.0831 | 122.3448 | 122.2473 | 0.62763 | -122.3642
3322.9219 | 122.3923 | -0.082397 | 122.2366 | -0.010149 | -0.050538 | 0.040507 | 0.019682 | -0.012719 | -0.0031579 | -0.013887 | -0.0024804 | -0.0027177 | 0.057832 | 0.046243 | 0.047901 | -0.008109 | 0.019721 | -0.008409 | 0.084176 | 0.091937 | 0.19233 | -0.090531 | 0.083464 | 0.55438 | -0.028879 | 122.0144 | 122.2761 | 122.1786 | -0.15041 | -0.008134 | -122.1525 | 0.074288 | 0.073988 | 0.082122 | -122.1447 | -122.0443 | -0.068015 | -0.22222 | 0.16586 | 0.053518 | 0.12153 | 0.039497 | -0.058031 | 0.16657 | 0.17433 | 0.27473 | 0.10212 | -122.3272 | 122.0968 | 122.3585 | 122.261 | 0.63678 | -122.387
3324.6875 | 122.3419 | -0.091553 | 122.2778 | -0.01778 | -0.050752 | 0.040293 | 0.019896 | -0.012933 | -0.0033715 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.045816 | 0.047687 | -0.012688 | 0.0243 | -0.012988 | 0.07502 | 0.087359 | 0.19233 | -0.085952 | 0.083464 | 0.5498 | -0.038036 | 122.019 | 122.2853 | 122.1786 | -0.15499 | 0.005601 | -122.2028 | 0.078865 | 0.078565 | 0.072964 | -122.1905 | -122.0855 | -0.063438 | -0.25884 | 0.17502 | 0.053517 | 0.11695 | 0.007455 | -0.09923 | 0.16657 | 0.17891 | 0.28388 | 0.11585 | -122.3638 | 122.1105 | 122.3768 | 122.2702 | 0.64136 | -122.4328
3326.4375 | 122.3282 | -0.10529 | 122.2778 | -0.01778 | -0.050965 | 0.040293 | 0.019682 | -0.013147 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.04667 | 0.047901 | -0.021844 | 0.028878 | -0.008409 | 0.084176 | 0.087359 | 0.20149 | -0.081373 | 0.092622 | 0.5498 | -0.028879 | 122.0053 | 122.2716 | 122.1786 | -0.15041 | 0.023913 | -122.1937 | 0.083442 | 0.096877 | 0.072964 | -122.1905 | -122.0763 | -0.045126 | -0.27258 | 0.19791 | 0.076407 | 0.12153 | -0.006281 | -0.09923 | 0.18946 | 0.19265 | 0.30677 | 0.13416 | -122.3592 | 122.1105 | 122.3768 | 122.2839 | 0.65509 | -122.4282
3328.125 | 122.3602 | -0.10529 | 122.2595 | -0.01778 | -0.050965 | 0.040293 | 0.019682 | -0.012719 | -0.0037989 | -0.021518 | -0.002053 | -0.0020767 | 0.058046 | 0.046457 | 0.047901 | -0.017266 | 0.015142 | -0.012988 | 0.084176 | 0.091937 | 0.19691 | -0.085952 | 0.083464 | 0.55896 | -0.033458 | 122.0236 | 122.2807 | 122.1832 | -0.15499 | 0.019334 | -122.1753 | 0.08802 | 0.092298 | 0.072964 | -122.1676 | -122.0626 | -0.049705 | -0.23595 | 0.18875 | 0.071828 | 0.12153 | 0.021187 | -0.076341 | 0.18946 | 0.19722 | 0.30219 | 0.12043 | -122.3455 | 122.1289 | 122.386 | 122.2885 | 0.66425 | -122.4145
3329.9062 | 122.4472 | -0.054932 | 122.2321 | -0.010149 | -0.050752 | 0.04008 | 0.019469 | -0.012933 | -0.0033715 | -0.021518 | -0.002694 | -0.0018631 | 0.058473 | 0.046029 | 0.047687 | -0.017266 | 0.015142 | -0.017566 | 0.07502 | 0.091937 | 0.19233 | -0.081373 | 0.088043 | 0.55896 | -0.042615 | 122.0098 | 122.2761 | 122.1786 | -0.14583 | -0.026441 | -122.157 | 0.037666 | 0.037366 | 0.063807 | -122.1401 | -122.0397 | -0.090901 | -0.22222 | 0.14297 | 0.012317 | 0.10322 | 0.044074 | -0.053454 | 0.12995 | 0.14687 | 0.24726 | 0.070074 | -122.3134 | 122.0648 | 122.3311 | 122.2335 | 0.61389 | -122.3779
3331.6562 | 122.3465 | -0.10529 | 122.2961 | -0.0025182 | -0.050538 | 0.039866 | 0.019469 | -0.012719 | -0.0035853 | -0.013887 | -0.0022666 | -0.0025041 | 0.058046 | 0.046457 | 0.047687 | -0.017266 | 0.010564 | -0.008409 | 0.079598 | 0.096516 | 0.19233 | -0.081373 | 0.078886 | 0.55896 | -0.028879 | 122.0098 | 122.2761 | 122.174 | -0.14583 | 0.023913 | -122.2165 | 0.08802 | 0.096877 | 0.072964 | -122.1996 | -122.1038 | -0.040547 | -0.28631 | 0.18417 | 0.076407 | 0.11695 | -0.020013 | -0.12212 | 0.18488 | 0.2018 | 0.29762 | 0.11585 | -122.3775 | 122.1151 | 122.3814 | 122.2793 | 0.66425 | -122.442
3333.4062 | 122.4564 | -0.054932 | 122.2183 | -0.010149 | -0.050965 | 0.040293 | 0.019682 | -0.012933 | -0.0033715 | -0.021518 | -0.0022666 | -0.0020767 | 0.058046 | 0.046243 | 0.047687 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.096516 | 0.19233 | -0.085952 | 0.083464 | 0.55896 | -0.033458 | 122.019 | 122.2807 | 122.174 | -0.15499 | -0.03102 | -122.1433 | 0.037666 | 0.041944 | 0.072964 | -122.1218 | -122.026 | -0.10006 | -0.19933 | 0.1384 | 0.021474 | 0.12153 | 0.062385 | -0.0443 | 0.12995 | 0.15145 | 0.24726 | 0.070074 | -122.3043 | 122.0739 | 122.3356 | 122.229 | 0.61389 | -122.3733
3335.1719 | 122.4609 | -0.054932 | 122.2275 | -0.0025182 | -0.050752 | 0.039866 | 0.019682 | -0.012933 | -0.0035853 | -0.013887 | -0.002053 | -0.0020767 | 0.05826 | 0.045816 | 0.047901 | -0.012688 | 0.015142 | -0.022144 | 0.07502 | 0.091937 | 0.19233 | -0.081373 | 0.083464 | 0.55896 | -0.033458 | 122.019 | 122.2807 | 122.1694 | -0.15499 | -0.026441 | -122.1525 | 0.042244 | 0.032788 | 0.059229 | -122.1355 | -122.0351 | -0.10006 | -0.20849 | 0.1384 | 0.021474 | 0.12153 | 0.05323 | -0.058034 | 0.12995 | 0.14687 | 0.24726 | 0.070074 | -122.3089 | 122.0739 | 122.3356 | 122.2244 | 0.61389 | -122.3825
3336.875 | 122.4426 | -0.045776 | 122.2183 | -0.010149 | -0.050965 | 0.04008 | 0.019896 | -0.012933 | -0.0033715 | -0.021518 | -0.0022666 | -0.0025041 | 0.05826 | 0.046457 | 0.047474 | -0.017266 | 0.0243 | -0.012988 | 0.07502 | 0.087359 | 0.19233 | -0.081373 | 0.078886 | 0.55896 | -0.033458 | 122.019 | 122.2807 | 122.1832 | -0.15957 | -0.035597 | -122.1433 | 0.02851 | 0.032788 | 0.068385 | -122.131 | -122.026 | -0.11379 | -0.19933 | 0.12466 | 0.012318 | 0.12611 | 0.062385 | -0.035143 | 0.1208 | 0.13314 | 0.23811 | 0.070076 | -122.2997 | 122.0648 | 122.3265 | 122.229 | 0.60474 | -122.3779
3338.6406 | 122.4243 | -0.059509 | 122.2595 | -0.0025182 | -0.051179 | 0.040293 | 0.019896 | -0.012933 | -0.0037989 | -0.013887 | -0.0022666 | -0.0025041 | 0.058046 | 0.046457 | 0.047901 | -0.017266 | 0.019721 | -0.003831 | 0.079598 | 0.096516 | 0.19233 | -0.085952 | 0.088043 | 0.56354 | -0.033458 | 122.0144 | 122.2716 | 122.1832 | -0.15041 | -0.026443 | -122.1799 | 0.042243 | 0.055678 | 0.082121 | -122.163 | -122.0672 | -0.090903 | -0.24511 | 0.14755 | 0.026051 | 0.11695 | 0.01203 | -0.076341 | 0.13911 | 0.15602 | 0.25184 | 0.07923 | -122.3455 | 122.0739 | 122.3311 | 122.2427 | 0.62305 | -122.4099
3340.4062 | 122.438 | -0.059509 | 122.2321 | -0.010149 | -0.050538 | 0.040293 | 0.019682 | -0.012719 | -0.0035853 | -0.029148 | -0.002053 | -0.0022903 | 0.058046 | 0.046243 | 0.04726 | -0.017266 | 0.0243 | -0.012988 | 0.07502 | 0.091937 | 0.20607 | -0.081373 | 0.083464 | 0.55896 | -0.028879 | 122.0144 | 122.2761 | 122.1832 | -0.14583 | -0.021864 | -122.157 | 0.042243 | 0.046521 | 0.068385 | -122.1401 | -122.026 | -0.086324 | -0.21764 | 0.14297 | 0.03063 | 0.11695 | 0.044074 | -0.048876 | 0.13453 | 0.15145 | 0.26558 | 0.083809 | -122.3134 | 122.0739 | 122.3356 | 122.2427 | 0.61847 | -122.3779
3342.1875 | 122.4426 | -0.041199 | 122.2183 | -0.0025182 | -0.050752 | 0.040507 | 0.019682 | -0.013147 | -0.0035853 | -0.0062567 | -0.0022666 | -0.0025041 | 0.058046 | 0.046243 | 0.047687 | -0.017266 | 0.019721 | -0.008409 | 0.084176 | 0.096516 | 0.19233 | -0.085952 | 0.088043 | 0.5727 | -0.033458 | 122.019 | 122.267 | 122.1878 | -0.15499 | -0.044753 | -122.1341 | 0.023933 | 0.03279 | 0.077543 | -122.1218 | -122.026 | -0.11379 | -0.19933 | 0.12924 | 0.007741 | 0.12153 | 0.048649 | -0.030564 | 0.12538 | 0.13772 | 0.23353 | 0.06092 | -122.3043 | 122.0602 | 122.3082 | 122.229 | 0.6139 | -122.3733
3343.9531 | 122.4792 | -0.050354 | 122.2183 | -0.01778 | -0.050538 | 0.04008 | 0.019682 | -0.012719 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.058046 | 0.046243 | 0.047687 | -0.021844 | 0.0243 | -0.012988 | 0.07502 | 0.091937 | 0.19691 | -0.085952 | 0.088043 | 0.55438 | -0.038036 | 122.019 | 122.2853 | 122.1832 | -0.15041 | -0.035598 | -122.1433 | 0.02851 | 0.037366 | 0.072964 | -122.1264 | -122.0214 | -0.10006 | -0.19933 | 0.1384 | 0.012318 | 0.11238 | 0.066964 | -0.035143 | 0.12537 | 0.14229 | 0.24726 | 0.074654 | -122.3043 | 122.0693 | 122.3356 | 122.2335 | 0.60474 | -122.3687
3345.6406 | 122.4472 | -0.054932 | 122.2366 | -0.01778 | -0.050965 | 0.04008 | 0.019469 | -0.012933 | -0.0035853 | -0.0062567 | -0.0024804 | -0.0020767 | 0.058473 | 0.046457 | 0.04726 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.091937 | 0.19691 | -0.081373 | 0.083464 | 0.55438 | -0.033458 | 122.019 | 122.2807 | 122.1786 | -0.15499 | -0.026441 | -122.157 | 0.033088 | 0.041944 | 0.068385 | -122.1447 | -122.0397 | -0.10006 | -0.21764 | 0.1384 | 0.021474 | 0.12153 | 0.044075 | -0.058031 | 0.13453 | 0.14687 | 0.25184 | 0.079232 | -122.318 | 122.0739 | 122.3356 | 122.2335 | 0.60931 | -122.3916
3347.3281 | 122.4701 | -0.054932 | 122.2183 | -0.010149 | -0.050752 | 0.04008 | 0.019682 | -0.012933 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.05826 | 0.046457 | 0.047901 | -0.026423 | 0.0243 | -0.012988 | 0.084176 | 0.091937 | 0.19233 | -0.081373 | 0.078886 | 0.56812 | -0.033458 | 122.0281 | 122.2716 | 122.1878 | -0.15957 | -0.026441 | -122.1341 | 0.028509 | 0.041944 | 0.068385 | -122.1264 | -122.026 | -0.10464 | -0.19017 | 0.13382 | 0.021474 | 0.12611 | 0.053228 | -0.030564 | 0.13911 | 0.14687 | 0.24726 | 0.079232 | -122.2997 | 122.0831 | 122.3265 | 122.2427 | 0.62305 | -122.3779
3349.0938 | 122.3602 | -0.086975 | 122.2504 | -0.01778 | -0.050965 | 0.039866 | 0.019255 | -0.013147 | -0.0040125 | -0.021518 | -0.0024804 | -0.0020767 | 0.05826 | 0.046029 | 0.047687 | -0.021844 | 0.0243 | -0.008409 | 0.07502 | 0.091937 | 0.19233 | -0.081373 | 0.083464 | 0.55896 | -0.028879 | 122.019 | 122.2807 | 122.1832 | -0.15041 | 0.005602 | -122.1753 | 0.065131 | 0.078566 | 0.072964 | -122.1584 | -122.058 | -0.063437 | -0.23137 | 0.17044 | 0.058096 | 0.12153 | 0.030342 | -0.067186 | 0.162 | 0.17891 | 0.27931 | 0.11127 | -122.3317 | 122.106 | 122.3677 | 122.2702 | 0.64594 | -122.4008
3350.7812 | 122.4152 | -0.068665 | 122.2321 | -0.0025182 | -0.051179 | 0.040721 | 0.019255 | -0.013147 | -0.0037989 | -0.013887 | -0.0024804 | -0.0022903 | 0.058046 | 0.046457 | 0.047687 | -0.021844 | 0.019721 | -0.012988 | 0.079598 | 0.096516 | 0.19691 | -0.081373 | 0.088043 | 0.56354 | -0.033458 | 122.0144 | 122.2807 | 122.1786 | -0.15957 | -0.012708 | -122.1525 | 0.046821 | 0.055677 | 0.068385 | -122.1355 | -122.0351 | -0.090905 | -0.21764 | 0.15671 | 0.035207 | 0.12611 | 0.048652 | -0.053454 | 0.14826 | 0.16518 | 0.26557 | 0.088386 | -122.3134 | 122.0831 | 122.3494 | 122.2473 | 0.63221 | -122.3916
3352.5469 | 122.3877 | -0.082397 | 122.2549 | -0.010149 | -0.050965 | 0.04008 | 0.019469 | -0.012933 | -0.0040125 | -0.0062567 | -0.002694 | -0.0022903 | 0.057832 | 0.046457 | 0.047901 | -0.017266 | 0.019721 | -0.012988 | 0.079598 | 0.091937 | 0.19691 | -0.090531 | 0.083464 | 0.56812 | -0.038036 | 122.0236 | 122.2853 | 122.1969 | -0.15499 | -0.008134 | -122.1753 | 0.065131 | 0.069409 | 0.077543 | -122.163 | -122.058 | -0.072594 | -0.23137 | 0.16586 | 0.044361 | 0.11695 | 0.030343 | -0.058028 | 0.162 | 0.17433 | 0.27931 | 0.10212 | -122.3455 | 122.106 | 122.3677 | 122.2793 | 0.65052 | -122.4099
3354.3125 | 122.438 | -0.064087 | 122.2275 | -0.010149 | -0.050965 | 0.039866 | 0.019469 | -0.013147 | -0.0037989 | -0.0062567 | -0.0024804 | -0.0025041 | 0.05826 | 0.046243 | 0.047687 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.096516 | 0.19233 | -0.090531 | 0.088043 | 0.55896 | -0.033458 | 122.0144 | 122.2716 | 122.1786 | -0.15041 | -0.026444 | -122.1525 | 0.046821 | 0.051099 | 0.077543 | -122.131 | -122.0351 | -0.086325 | -0.21307 | 0.15213 | 0.030629 | 0.11695 | 0.044073 | -0.048876 | 0.13911 | 0.1606 | 0.25642 | 0.079229 | -122.318 | 122.0785 | 122.3356 | 122.2427 | 0.62305 | -122.3779
3356.0781 | 122.3831 | -0.082397 | 122.2549 | -0.0025182 | -0.050752 | 0.039866 | 0.019469 | -0.01336 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.046457 | 0.047687 | -0.021844 | 0.019721 | -0.008409 | 0.084176 | 0.091937 | 0.19691 | -0.081373 | 0.083464 | 0.55438 | -0.028879 | 122.019 | 122.2761 | 122.1832 | -0.15499 | 0.001024 | -122.1708 | 0.060553 | 0.073988 | 0.072964 | -122.163 | -122.058 | -0.072594 | -0.23595 | 0.16586 | 0.053518 | 0.12611 | 0.021186 | -0.071764 | 0.16657 | 0.17433 | 0.27931 | 0.10212 | -122.3363 | 122.1014 | 122.3585 | 122.2656 | 0.63678 | -122.4099
3357.7656 | 122.4243 | -0.050354 | 122.2504 | -0.010149 | -0.050965 | 0.04008 | 0.019682 | -0.013147 | -0.0037989 | -0.013887 | -0.0024804 | -0.0020767 | 0.057832 | 0.046457 | 0.047901 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.091937 | 0.19691 | -0.076794 | 0.083464 | 0.56354 | -0.033458 | 122.019 | 122.2807 | 122.1786 | -0.15499 | -0.02644 | -122.1753 | 0.033088 | 0.037366 | 0.063806 | -122.1584 | -122.0535 | -0.10464 | -0.23137 | 0.13382 | 0.016896 | 0.12153 | 0.030342 | -0.071764 | 0.12537 | 0.14229 | 0.24726 | 0.070075 | -122.3272 | 122.0693 | 122.3311 | 122.229 | 0.61389 | -122.4054
3359.5312 | 122.406 | -0.059509 | 122.2046 | -0.01778 | -0.050538 | 0.040507 | 0.019682 | -0.012506 | -0.0037989 | -0.029148 | -0.0024804 | -0.0020767 | 0.058046 | 0.046457 | 0.047687 | -0.012688 | 0.015142 | -0.022144 | 0.079598 | 0.091937 | 0.19233 | -0.076794 | 0.083464 | 0.55896 | -0.038036 | 122.019 | 122.2716 | 122.1832 | -0.15957 | -0.017285 | -122.125 | 0.046821 | 0.037365 | 0.05465 | -122.1127 | -122.0123 | -0.10006 | -0.1856 | 0.14297 | 0.021473 | 0.12153 | 0.066961 | -0.02141 | 0.13911 | 0.15145 | 0.25184 | 0.074651 | -122.2814 | 122.0785 | 122.3311 | 122.2427 | 0.61847 | -122.3642
3361.2969 | 122.4701 | -0.045776 | 122.2366 | -0.025411 | -0.051179 | 0.040293 | 0.019682 | -0.013147 | -0.0035853 | -0.021518 | -0.0024804 | -0.0018631 | 0.057832 | 0.04667 | 0.047687 | -0.021844 | 0.019721 | -0.008409 | 0.079598 | 0.1011 | 0.19233 | -0.076794 | 0.088043 | 0.56354 | -0.038036 | 122.019 | 122.2807 | 122.1832 | -0.15499 | -0.031018 | -122.157 | 0.023932 | 0.037367 | 0.068385 | -122.1355 | -122.0443 | -0.10921 | -0.21764 | 0.13382 | 0.00774 | 0.11695 | 0.044075 | -0.053453 | 0.12537 | 0.14687 | 0.23811 | 0.065497 | -122.3134 | 122.0648 | 122.3265 | 122.229 | 0.60932 | -122.3916
3362.9844 | 122.4106 | -0.082397 | 122.2504 | -0.025411 | -0.050752 | 0.04008 | 0.019255 | -0.01336 | -0.0035853 | -0.036779 | -0.0022666 | -0.0022903 | 0.057832 | 0.046457 | 0.047901 | -0.012688 | 0.0243 | -0.008409 | 0.084176 | 0.087359 | 0.20149 | -0.09511 | 0.088043 | 0.56354 | -0.038036 | 122.0144 | 122.2716 | 122.1786 | -0.15499 | -0.012713 | -122.1662 | 0.069709 | 0.073988 | 0.086701 | -122.163 | -122.0489 | -0.072594 | -0.23595 | 0.17044 | 0.044361 | 0.11695 | 0.021185 | -0.071764 | 0.16657 | 0.16976 | 0.28388 | 0.1067 | -122.3455 | 122.0968 | 122.3539 | 122.261 | 0.64594 | -122.4054
3364.75 | 122.319 | -0.10529 | 122.2504 | -0.0025182 | -0.050752 | 0.039866 | 0.019469 | -0.012719 | -0.0037989 | -0.013887 | -0.002053 | -0.0020767 | 0.057832 | 0.046457 | 0.047474 | -0.017266 | 0.019721 | -0.003831 | 0.07502 | 0.1011 | 0.19691 | -0.081373 | 0.088043 | 0.56354 | -0.038036 | 122.019 | 122.2761 | 122.1923 | -0.15041 | 0.023913 | -122.1753 | 0.08802 | 0.10146 | 0.077542 | -122.1493 | -122.0535 | -0.045126 | -0.23137 | 0.19333 | 0.06725 | 0.11238 | 0.025764 | -0.058029 | 0.18031 | 0.20638 | 0.30219 | 0.12501 | -122.3317 | 122.1243 | 122.3814 | 122.2976 | 0.66883 | -122.4008
3366.5 | 122.3465 | -0.10071 | 122.2778 | -0.025411 | -0.050965 | 0.040293 | 0.019682 | -0.013147 | -0.0042263 | -0.0062567 | -0.0024804 | -0.0022903 | 0.058046 | 0.046243 | 0.047474 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.1011 | 0.19691 | -0.081373 | 0.088043 | 0.56812 | -0.033458 | 122.0098 | 122.2853 | 122.1832 | -0.15499 | 0.019335 | -122.2028 | 0.083442 | 0.08772 | 0.068385 | -122.1767 | -122.0809 | -0.054283 | -0.268 | 0.18875 | 0.06725 | 0.12153 | 0.007455 | -0.094652 | 0.17573 | 0.2018 | 0.29762 | 0.12043 | -122.3592 | 122.1105 | 122.386 | 122.2839 | 0.66883 | -122.4328
3368.2656 | 122.4014 | -0.073242 | 122.2366 | -0.025411 | -0.050965 | 0.04008 | 0.019682 | -0.012933 | -0.0037989 | -0.021518 | -0.0022666 | -0.0025041 | 0.057832 | 0.046457 | 0.047474 | -0.017266 | 0.0243 | -0.012988 | 0.079598 | 0.096516 | 0.20149 | -0.081373 | 0.092622 | 0.55896 | -0.033458 | 122.019 | 122.2807 | 122.1786 | -0.16415 | -0.008131 | -122.157 | 0.055976 | 0.060254 | 0.068385 | -122.1401 | -122.0351 | -0.090907 | -0.21764 | 0.16586 | 0.039784 | 0.13069 | 0.044075 | -0.058031 | 0.15284 | 0.16976 | 0.27473 | 0.097542 | -122.318 | 122.0922 | 122.3539 | 122.2518 | 0.6322 | -122.4008
3369.9688 | 122.4747 | -0.059509 | 122.2549 | -0.0025182 | -0.051179 | 0.04008 | 0.019255 | -0.013147 | -0.0040125 | -0.021518 | -0.0024804 | -0.0020767 | 0.058046 | 0.046457 | 0.047474 | -0.021844 | 0.015142 | -0.017566 | 0.079598 | 0.091937 | 0.19691 | -0.085952 | 0.083464 | 0.55438 | -0.038036 | 122.019 | 122.2716 | 122.1878 | -0.15499 | -0.026443 | -122.1753 | 0.037665 | 0.041943 | 0.068386 | -122.163 | -122.058 | -0.095482 | -0.23595 | 0.14297 | 0.021473 | 0.11695 | 0.016607 | -0.067185 | 0.13911 | 0.15145 | 0.25642 | 0.074651 | -122.3409 | 122.0785 | 122.3311 | 122.2473 | 0.61389 | -122.4099
3371.7344 | 122.3877 | -0.082397 | 122.2687 | -0.01778 | -0.051179 | 0.040293 | 0.019255 | -0.013147 | -0.0037989 | -0.021518 | -0.0024804 | -0.0027177 | 0.058046 | 0.04667 | 0.047474 | -0.021844 | 0.015142 | -0.017566 | 0.079598 | 0.096516 | 0.19691 | -0.081373 | 0.088043 | 0.56354 | -0.033458 | 122.019 | 122.2807 | 122.1786 | -0.15041 | 0.001024 | -122.1891 | 0.060553 | 0.064831 | 0.063807 | -122.1722 | -122.0718 | -0.068015 | -0.24968 | 0.17044 | 0.048939 | 0.11695 | 0.012031 | -0.090075 | 0.162 | 0.17891 | 0.27931 | 0.097539 | -122.35 | 122.1014 | 122.3631 | 122.261 | 0.64594 | -122.4191
3373.4844 | 122.4564 | -0.059509 | 122.2321 | -0.0025182 | -0.050965 | 0.04008 | 0.019255 | -0.013574 | -0.0037989 | -0.013887 | -0.002694 | -0.0027177 | 0.05826 | 0.046884 | 0.047901 | -0.021844 | 0.0243 | -0.003831 | 0.07502 | 0.091937 | 0.20149 | -0.081373 | 0.083464 | 0.56812 | -0.028879 | 122.0236 | 122.2807 | 122.1832 | -0.16415 | -0.021864 | -122.157 | 0.037665 | 0.055678 | 0.077542 | -122.1401 | -122.0306 | -0.10464 | -0.20849 | 0.14297 | 0.03063 | 0.13527 | 0.048652 | -0.048876 | 0.13453 | 0.15145 | 0.261 | 0.083809 | -122.3134 | 122.0831 | 122.3402 | 122.2427 | 0.62763 | -122.3962
3375.2656 | 122.406 | -0.054932 | 122.2412 | -0.010149 | -0.050752 | 0.04008 | 0.019255 | -0.012933 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.058046 | 0.04667 | 0.048115 | -0.021844 | 0.015142 | -0.012988 | 0.079598 | 0.096516 | 0.20149 | -0.090531 | 0.078886 | 0.56812 | -0.038036 | 122.0236 | 122.2761 | 122.1786 | -0.15041 | -0.035599 | -122.1616 | 0.033088 | 0.041944 | 0.077543 | -122.1447 | -122.0397 | -0.09548 | -0.21764 | 0.13382 | 0.016896 | 0.11238 | 0.034919 | -0.062609 | 0.13453 | 0.15145 | 0.25642 | 0.070074 | -122.3317 | 122.0785 | 122.3311 | 122.2335 | 0.62305 | -122.3916
3376.9688 | 122.374 | -0.07782 | 122.2229 | -0.010149 | -0.051179 | 0.039866 | 0.019682 | -0.01336 | -0.0037989 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.04667 | 0.047687 | -0.017266 | 0.019721 | -0.012988 | 0.079598 | 0.087359 | 0.18317 | -0.090531 | 0.088043 | 0.56354 | -0.033458 | 122.0144 | 122.2761 | 122.1786 | -0.15041 | -0.012711 | -122.1433 | 0.060554 | 0.064832 | 0.077543 | -122.1355 | -122.0397 | -0.072592 | -0.20849 | 0.16586 | 0.044362 | 0.11695 | 0.05323 | -0.044298 | 0.15742 | 0.16518 | 0.26099 | 0.097541 | -122.3134 | 122.0922 | 122.3539 | 122.2564 | 0.64136 | -122.3733
3378.7188 | 122.406 | -0.082397 | 122.2412 | -0.010149 | -0.051179 | 0.04008 | 0.019255 | -0.01336 | -0.0040125 | -0.013887 | -0.002694 | -0.0018631 | 0.05826 | 0.046884 | 0.047901 | -0.012688 | 0.015142 | -0.003831 | 0.084176 | 0.1011 | 0.20149 | -0.081373 | 0.083464 | 0.56354 | -0.028879 | 122.0236 | 122.2807 | 122.1832 | -0.15499 | 0.001024 | -122.157 | 0.069709 | 0.078566 | 0.077542 | -122.1401 | -122.0397 | -0.072594 | -0.21764 | 0.16586 | 0.053518 | 0.12611 | 0.039497 | -0.058031 | 0.16657 | 0.18349 | 0.28388 | 0.097539 | -122.3226 | 122.106 | 122.3631 | 122.2656 | 0.64594 | -122.3962
3380.4844 | 122.374 | -0.082397 | 122.2687 | -0.0025182 | -0.050965 | 0.04008 | 0.019469 | -0.013147 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.058046 | 0.04667 | 0.047901 | -0.017266 | 0.019721 | -0.017566 | 0.084176 | 0.091937 | 0.20149 | -0.081373 | 0.088043 | 0.5727 | -0.028879 | 122.019 | 122.2807 | 122.1832 | -0.15499 | 0.001024 | -122.1845 | 0.065131 | 0.064831 | 0.063807 | -122.1767 | -122.0672 | -0.072594 | -0.24968 | 0.17044 | 0.053518 | 0.12611 | 0.012031 | -0.085497 | 0.16657 | 0.17433 | 0.28388 | 0.10212 | -122.35 | 122.1014 | 122.3631 | 122.2656 | 0.65509 | -122.4237
3382.25 | 122.4106 | -0.082397 | 122.2275 | -0.01778 | -0.050965 | 0.040293 | 0.019469 | -0.012933 | -0.0037989 | -0.021518 | -0.002053 | -0.0022903 | 0.05826 | 0.046457 | 0.047687 | -0.021844 | 0.028878 | -0.003831 | 0.084176 | 0.10567 | 0.19691 | -0.090531 | 0.088043 | 0.56812 | -0.028879 | 122.0236 | 122.2807 | 122.1832 | -0.15957 | -0.008134 | -122.1433 | 0.060553 | 0.078566 | 0.0867 | -122.1218 | -122.0306 | -0.077173 | -0.20391 | 0.17044 | 0.053518 | 0.13069 | 0.05323 | -0.044298 | 0.16657 | 0.18807 | 0.27931 | 0.11127 | -122.318 | 122.106 | 122.3631 | 122.2656 | 0.65052 | -122.387
3384.0156 | 122.3328 | -0.11444 | 122.2733 | -0.025411 | -0.050752 | 0.039652 | 0.019896 | -0.012933 | -0.0042263 | -0.021518 | -0.0022666 | -0.0020767 | 0.058046 | 0.046884 | 0.047687 | -0.017266 | 0.019721 | -0.008409 | 0.07502 | 0.091937 | 0.19691 | -0.085952 | 0.083464 | 0.56812 | -0.033458 | 122.0236 | 122.2761 | 122.1923 | -0.15957 | 0.028489 | -122.1982 | 0.097175 | 0.10603 | 0.077543 | -122.1813 | -122.0763 | -0.045129 | -0.24968 | 0.1979 | 0.080983 | 0.12611 | 0.002876 | -0.080917 | 0.18946 | 0.20638 | 0.31135 | 0.13416 | -122.3592 | 122.138 | 122.3906 | 122.3068 | 0.68256 | -122.4328
3385.7188 | 122.3602 | -0.09613 | 122.2549 | -0.010149 | -0.050752 | 0.039439 | 0.019896 | -0.012506 | -0.0035853 | -0.021518 | -0.0024804 | -0.0018631 | 0.058046 | 0.046243 | 0.04726 | -0.021844 | 0.019721 | -0.017566 | 0.079598 | 0.091937 | 0.19691 | -0.081373 | 0.088043 | 0.56812 | -0.028879 | 122.019 | 122.2716 | 122.1832 | -0.15499 | 0.014757 | -122.1753 | 0.074286 | 0.078564 | 0.063807 | -122.163 | -122.058 | -0.058861 | -0.23595 | 0.18417 | 0.067251 | 0.12611 | 0.016607 | -0.071764 | 0.17573 | 0.18807 | 0.29304 | 0.11585 | -122.3363 | 122.1151 | 122.3677 | 122.2793 | 0.66425 | -122.4099
3387.4688 | 122.4106 | -0.064087 | 122.2321 | -0.010149 | -0.050752 | 0.039439 | 0.019682 | -0.012933 | -0.0037989 | -0.013887 | -0.0024804 | -0.0025041 | 0.058046 | 0.046884 | 0.047474 | -0.012688 | 0.019721 | -0.017566 | 0.079598 | 0.1011 | 0.19233 | -0.081373 | 0.088043 | 0.56354 | -0.028879 | 122.0144 | 122.2807 | 122.1878 | -0.15499 | -0.017286 | -122.1525 | 0.051399 | 0.046521 | 0.063807 | -122.131 | -122.0397 | -0.090904 | -0.21764 | 0.15213 | 0.035208 | 0.12611 | 0.048652 | -0.044297 | 0.14369 | 0.16518 | 0.25642 | 0.083808 | -122.3134 | 122.0785 | 122.3448 | 122.2518 | 0.62763 | -122.387
3389.2344 | 122.4243 | -0.059509 | 122.2458 | -0.010149 | -0.050752 | 0.039439 | 0.019469 | -0.013147 | -0.0040125 | -0.021518 | -0.002694 | -0.0025041 | 0.057832 | 0.046457 | 0.047901 | -0.017266 | 0.019721 | -0.012988 | 0.079598 | 0.096516 | 0.19691 | -0.085952 | 0.083464 | 0.56812 | -0.0243 | 122.0144 | 122.2807 | 122.1832 | -0.15499 | -0.026443 | -122.1662 | 0.042243 | 0.046521 | 0.072964 | -122.1493 | -122.0489 | -0.095482 | -0.23138 | 0.14297 | 0.035209 | 0.13069 | 0.034919 | -0.062609 | 0.13911 | 0.15602 | 0.25642 | 0.07923 | -122.3317 | 122.0739 | 122.3402 | 122.2427 | 0.62763 | -122.4008
3391 | 122.4243 | -0.054932 | 122.2229 | -0.025411 | -0.050752 | 0.039652 | 0.019469 | -0.012933 | -0.0037989 | -0.013887 | -0.0024804 | -0.0020767 | 0.057832 | 0.046457 | 0.047687 | -0.017266 | 0.015142 | -0.012988 | 0.07502 | 0.1011 | 0.19691 | -0.081373 | 0.088043 | 0.56812 | -0.028879 | 122.019 | 122.2761 | 122.1832 | -0.15499 | -0.026441 | -122.1479 | 0.037666 | 0.041944 | 0.068385 | -122.1218 | -122.026 | -0.10006 | -0.20391 | 0.14297 | 0.026053 | 0.12611 | 0.05323 | -0.03972 | 0.12995 | 0.15603 | 0.25184 | 0.070074 | -122.3043 | 122.0739 | 122.3311 | 122.2381 | 0.62305 | -122.3779
3392.7031 | 122.4838 | -0.059509 | 122.2229 | -0.0025182 | -0.050752 | 0.039225 | 0.019255 | -0.013147 | -0.0040125 | -0.021518 | -0.0022666 | -0.0020767 | 0.058046 | 0.04667 | 0.04726 | -0.026423 | 0.0243 | -0.003831 | 0.079598 | 0.091937 | 0.19233 | -0.081373 | 0.092622 | 0.56354 | -0.028879 | 122.019 | 122.2853 | 122.1786 | -0.15041 | -0.021864 | -122.1433 | 0.033086 | 0.055678 | 0.077542 | -122.131 | -122.0306 | -0.090903 | -0.20391 | 0.15213 | 0.03063 | 0.12153 | 0.062387 | -0.044298 | 0.13911 | 0.15145 | 0.25184 | 0.083809 | -122.3043 | 122.0785 | 122.3448 | 122.2381 | 0.62305 | -122.3733
3394.4688 | 122.3694 | -0.11444 | 122.2595 | -0.010149 | -0.050752 | 0.039439 | 0.019469 | -0.012933 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.05826 | 0.04667 | 0.047474 | -0.008109 | 0.015142 | -0.003831 | 0.079598 | 0.096516 | 0.19691 | -0.090531 | 0.092622 | 0.55896 | -0.0243 | 122.0144 | 122.2807 | 122.1786 | -0.15499 | 0.02391 | -122.1799 | 0.10633 | 0.11061 | 0.0867 | -122.163 | -122.0626 | -0.04055 | -0.24511 | 0.20706 | 0.090141 | 0.13069 | 0.021187 | -0.080919 | 0.19404 | 0.21096 | 0.31135 | 0.12958 | -122.3501 | 122.1289 | 122.3951 | 122.293 | 0.6734 | -122.4145
3396.1562 | 122.4106 | -0.082397 | 122.2504 | -0.010149 | -0.050752 | 0.039652 | 0.019469 | -0.013147 | -0.0042263 | -0.029148 | -0.002694 | -0.0022903 | 0.058046 | 0.04667 | 0.047687 | -0.017266 | 0.019721 | -0.012988 | 0.079598 | 0.091937 | 0.20607 | -0.090531 | 0.092622 | 0.56812 | -0.033458 | 122.0236 | 122.2853 | 122.1832 | -0.15041 | -0.008134 | -122.1708 | 0.065131 | 0.069409 | 0.077543 | -122.1584 | -122.0443 | -0.068015 | -0.2268 | 0.17502 | 0.048939 | 0.11695 | 0.034921 | -0.067186 | 0.162 | 0.17433 | 0.28846 | 0.10212 | -122.3409 | 122.106 | 122.3677 | 122.2656 | 0.65052 | -122.4008
3397.9062 | 122.4197 | -0.064087 | 122.2458 | -0.010149 | -0.050752 | 0.039439 | 0.019469 | -0.012933 | -0.0040125 | -0.013887 | -0.0024804 | -0.0022903 | 0.058046 | 0.046884 | 0.047474 | -0.021844 | 0.019721 | -0.012988 | 0.084176 | 0.10567 | 0.20607 | -0.081373 | 0.088043 | 0.56354 | -0.033458 | 122.0144 | 122.2899 | 122.1878 | -0.15041 | -0.017286 | -122.1616 | 0.042243 | 0.051099 | 0.068385 | -122.1401 | -122.0397 | -0.086325 | -0.23138 | 0.15213 | 0.030629 | 0.11695 | 0.044076 | -0.05803 | 0.14826 | 0.16976 | 0.27015 | 0.083808 | -122.3272 | 122.0785 | 122.354 | 122.2518 | 0.62763 | -122.3962
3399.6094 | 122.4426 | -0.036621 | 122.2458 | -0.010149 | -0.051179 | 0.039225 | 0.019682 | -0.012719 | -0.0037989 | -0.021518 | -0.0029076 | -0.0022903 | 0.05826 | 0.04667 | 0.04726 | -0.017266 | 0.0243 | -0.003831 | 0.079598 | 0.096516 | 0.20149 | -0.076794 | 0.088043 | 0.5727 | -0.028879 | 122.019 | 122.2807 | 122.1832 | -0.15499 | -0.040173 | -122.1662 | 0.019355 | 0.03279 | 0.072963 | -122.1493 | -122.0443 | -0.11837 | -0.2268 | 0.12466 | 0.007742 | 0.12611 | 0.034919 | -0.062609 | 0.11622 | 0.13314 | 0.23811 | 0.060921 | -122.3226 | 122.0556 | 122.3173 | 122.2198 | 0.60932 | -122.4008
3401.3594 | 122.4518 | -0.064087 | 122.2183 | -0.010149 | -0.050752 | 0.039652 | 0.019469 | -0.013147 | -0.0042263 | -0.036779 | -0.0024804 | -0.0020767 | 0.057619 | 0.04667 | 0.047474 | -0.017266 | 0.019721 | -0.008409 | 0.079598 | 0.091937 | 0.20149 | -0.085952 | 0.092622 | 0.5727 | -0.033458 | 122.0236 | 122.2853 | 122.1969 | -0.15499 | -0.021865 | -122.1387 | 0.046821 | 0.055678 | 0.077543 | -122.1264 | -122.0168 | -0.090904 | -0.19475 | 0.15671 | 0.030629 | 0.12153 | 0.066964 | -0.021407 | 0.14369 | 0.15602 | 0.26558 | 0.083808 | -122.3043 | 122.0877 | 122.3494 | 122.261 | 0.63679 | -122.3733
3403.1094 | 122.4655 | -0.050354 | 122.2321 | -0.01778 | -0.051179 | 0.039652 | 0.019682 | -0.013147 | -0.0035853 | -0.021518 | -0.0022666 | -0.0020767 | 0.058046 | 0.04667 | 0.047687 | -0.017266 | 0.019721 | -0.003831 | 0.084176 | 0.096516 | 0.20149 | -0.085952 | 0.088043 | 0.56812 | -0.028879 | 122.0236 | 122.2853 | 122.1878 | -0.15957 | -0.035598 | -122.1479 | 0.033088 | 0.046523 | 0.082121 | -122.1355 | -122.0306 | -0.10922 | -0.20849 | 0.1384 | 0.021475 | 0.13069 | 0.053231 | -0.044297 | 0.13453 | 0.14687 | 0.25184 | 0.070075 | -122.318 | 122.0739 | 122.3356 | 122.2381 | 0.61847 | -122.3916
3404.875 | 122.3877 | -0.091553 | 122.2641 | -0.010149 | -0.050752 | 0.039439 | 0.019682 | -0.01336 | -0.0037989 | -0.0062567 | -0.002694 | -0.0025041 | 0.058046 | 0.046243 | 0.047474 | -0.026423 | 0.019721 | -0.008409 | 0.07502 | 0.091937 | 0.19691 | -0.090531 | 0.097201 | 0.56812 | -0.028879 | 122.0144 | 122.2899 | 122.1832 | -0.15957 | 0.001022 | -122.1891 | 0.06513 | 0.083144 | 0.082122 | -122.1722 | -122.0672 | -0.068017 | -0.24969 | 0.18875 | 0.062674 | 0.13069 | 0.025766 | -0.080919 | 0.16657 | 0.18349 | 0.28846 | 0.11127 | -122.3546 | 122.106 | 122.3814 | 122.2747 | 0.65967 | -122.4237
3406.6562 | 122.4335 | -0.064087 | 122.2641 | -0.01778 | -0.050752 | 0.039439 | 0.019255 | -0.013147 | -0.0037989 | -0.021518 | -0.0024804 | -0.0020767 | 0.057832 | 0.04667 | 0.047474 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.1011 | 0.19691 | -0.081373 | 0.083464 | 0.5727 | -0.028879 | 122.019 | 122.2853 | 122.1832 | -0.15957 | -0.017286 | -122.1799 | 0.042243 | 0.055678 | 0.072964 | -122.163 | -122.0672 | -0.095483 | -0.24511 | 0.14755 | 0.035208 | 0.13069 | 0.021188 | -0.080919 | 0.14826 | 0.16518 | 0.261 | 0.088387 | -122.3455 | 122.0831 | 122.3494 | 122.2473 | 0.63679 | -122.4237
3408.3438 | 122.3969 | -0.059509 | 122.2549 | -0.01778 | -0.050752 | 0.039652 | 0.019469 | -0.013574 | -0.0035853 | -0.021518 | -0.0022666 | -0.0022903 | 0.058046 | 0.04667 | 0.047687 | -0.031001 | 0.019721 | -0.008409 | 0.07502 | 0.096516 | 0.19691 | -0.085952 | 0.078886 | 0.56812 | -0.028879 | 122.0236 | 122.2853 | 122.1878 | -0.15499 | -0.026443 | -122.1799 | 0.028508 | 0.0511 | 0.077543 | -122.1584 | -122.058 | -0.095482 | -0.23137 | 0.13839 | 0.03063 | 0.12611 | 0.030343 | -0.067185 | 0.13453 | 0.15602 | 0.25642 | 0.07923 | -122.3409 | 122.0831 | 122.3448 | 122.2473 | 0.62763 | -122.4099
3410.1094 | 122.3511 | -0.10071 | 122.2961 | -0.0025182 | -0.050752 | 0.039652 | 0.019896 | -0.01336 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.04667 | 0.047687 | -0.021844 | 0.019721 | -0.003831 | 0.07502 | 0.1011 | 0.20149 | -0.081373 | 0.083464 | 0.56354 | -0.028879 | 122.019 | 122.2944 | 122.1923 | -0.15957 | 0.019335 | -122.2211 | 0.078864 | 0.096877 | 0.077542 | -122.195 | -122.0947 | -0.058862 | -0.27715 | 0.18417 | 0.071829 | 0.13069 | -0.001699 | -0.10381 | 0.17573 | 0.2018 | 0.3022 | 0.12043 | -122.3775 | 122.1197 | 122.3952 | 122.293 | 0.66425 | -122.4557
3411.8125 | 122.3145 | -0.10071 | 122.2641 | -0.010149 | -0.050752 | 0.039439 | 0.019682 | -0.013147 | -0.0035853 | -0.021518 | -0.0022666 | -0.0020767 | 0.057832 | 0.046457 | 0.047687 | -0.021844 | 0.015142 | -0.012988 | 0.084176 | 0.096516 | 0.19691 | -0.076794 | 0.088043 | 0.56354 | -0.028879 | 122.0236 | 122.2899 | 122.1878 | -0.16415 | 0.023914 | -122.1799 | 0.078864 | 0.08772 | 0.063806 | -122.1676 | -122.0672 | -0.063441 | -0.24053 | 0.18875 | 0.071829 | 0.13527 | 0.025766 | -0.07634 | 0.18488 | 0.19722 | 0.29762 | 0.11585 | -122.3409 | 122.1243 | 122.3906 | 122.2885 | 0.66425 | -122.4282
3413.5781 | 122.3373 | -0.10986 | 122.2412 | -0.01778 | -0.050965 | 0.039439 | 0.019682 | -0.012933 | -0.0037989 | -0.013887 | -0.0022666 | -0.0022903 | 0.057832 | 0.04667 | 0.047474 | -0.021844 | 0.015142 | -0.008409 | 0.079598 | 0.096516 | 0.20149 | -0.076794 | 0.092622 | 0.56354 | -0.033458 | 122.0281 | 122.2853 | 122.1923 | -0.15041 | 0.033069 | -122.1616 | 0.088019 | 0.10145 | 0.068385 | -122.1447 | -122.0397 | -0.040549 | -0.21306 | 0.20248 | 0.076405 | 0.11695 | 0.044076 | -0.048874 | 0.18946 | 0.20638 | 0.31135 | 0.12501 | -122.318 | 122.138 | 122.3952 | 122.3022 | 0.6734 | -122.3916
3415.3438 | 122.3373 | -0.10071 | 122.2778 | -0.010149 | -0.050965 | 0.039439 | 0.019682 | -0.013147 | -0.0037989 | -0.013887 | -0.0022666 | -0.0018631 | 0.057832 | 0.046243 | 0.04726 | -0.017266 | 0.019721 | -0.003831 | 0.084176 | 0.096516 | 0.19691 | -0.085952 | 0.088043 | 0.55896 | -0.028879 | 122.0144 | 122.2899 | 122.1832 | -0.14583 | 0.014756 | -122.1937 | 0.083442 | 0.096877 | 0.082121 | -122.1813 | -122.0809 | -0.045125 | -0.26342 | 0.18875 | 0.071829 | 0.11695 | 0.012033 | -0.094652 | 0.18488 | 0.19722 | 0.29762 | 0.12043 | -122.3638 | 122.1151 | 122.3906 | 122.2839 | 0.65967 | -122.4237
3417.1094 | 122.374 | -0.091553 | 122.2778 | -0.01778 | -0.050538 | 0.039439 | 0.019682 | -0.012933 | -0.0035853 | -0.013887 | -0.0024804 | -0.0022903 | 0.058046 | 0.046884 | 0.047687 | -0.012688 | 0.019721 | -0.003831 | 0.079598 | 0.096516 | 0.19691 | -0.085952 | 0.092622 | 0.56812 | -0.028879 | 122.0144 | 122.2853 | 122.1832 | -0.15499 | 0.005601 | -122.1982 | 0.078865 | 0.087722 | 0.082121 | -122.1813 | -122.0809 | -0.063438 | -0.26342 | 0.18417 | 0.062674 | 0.12611 | 0.007455 | -0.094652 | 0.17115 | 0.18807 | 0.28846 | 0.11127 | -122.3638 | 122.106 | 122.3768 | 122.2747 | 0.65967 | -122.4328
3418.8125 | 122.4564 | -0.050354 | 122.2366 | -0.025411 | -0.051179 | 0.039652 | 0.019469 | -0.01336 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.058046 | 0.047098 | 0.047474 | -0.017266 | 0.019721 | -0.008409 | 0.07502 | 0.096516 | 0.19691 | -0.090531 | 0.088043 | 0.56812 | -0.0243 | 122.0236 | 122.2899 | 122.1832 | -0.15499 | -0.040177 | -122.1616 | 0.033088 | 0.041945 | 0.082122 | -122.1401 | -122.0397 | -0.10464 | -0.21306 | 0.1384 | 0.026054 | 0.13069 | 0.053232 | -0.053453 | 0.12537 | 0.14687 | 0.24726 | 0.070075 | -122.3272 | 122.0739 | 122.3402 | 122.2335 | 0.61847 | -122.3916
3420.5781 | 122.3694 | -0.10529 | 122.287 | -0.010149 | -0.051179 | 0.039225 | 0.019255 | -0.013574 | -0.0035853 | -0.013887 | -0.0024804 | -0.0020767 | 0.058046 | 0.046457 | 0.04726 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.096516 | 0.20149 | -0.085952 | 0.083464 | 0.56812 | -0.033458 | 122.0281 | 122.2853 | 122.1832 | -0.15499 | 0.019334 | -122.2028 | 0.083442 | 0.096877 | 0.077543 | -122.1905 | -122.0855 | -0.049705 | -0.25884 | 0.18875 | 0.071828 | 0.12153 | -0.0017 | -0.10381 | 0.18946 | 0.2018 | 0.30677 | 0.12959 | -122.3729 | 122.1334 | 122.3906 | 122.2885 | 0.67341 | -122.442
3422.3281 | 122.319 | -0.091553 | 122.2824 | -0.025411 | -0.050965 | 0.039439 | 0.019255 | -0.013147 | -0.0040125 | -0.013887 | -0.002694 | -0.0022903 | 0.058046 | 0.046884 | 0.047901 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.096516 | 0.20149 | -0.085952 | 0.083464 | 0.56812 | -0.033458 | 122.0236 | 122.2899 | 122.1969 | -0.15041 | 0.005601 | -122.2074 | 0.074287 | 0.078565 | 0.072964 | -122.1859 | -122.0809 | -0.058859 | -0.25884 | 0.17502 | 0.058095 | 0.11695 | 0.007455 | -0.085494 | 0.16657 | 0.18807 | 0.29304 | 0.11127 | -122.3684 | 122.1151 | 122.3814 | 122.2885 | 0.65967 | -122.4328
3424.0938 | 122.3373 | -0.10529 | 122.2595 | -0.010149 | -0.050752 | 0.039439 | 0.019469 | -0.013147 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.04667 | 0.047474 | -0.021844 | 0.0243 | -0.008409 | 0.079598 | 0.091937 | 0.19691 | -0.081373 | 0.088043 | 0.5727 | -0.033458 | 122.0236 | 122.2899 | 122.1923 | -0.15499 | 0.023913 | -122.1799 | 0.083442 | 0.096877 | 0.072964 | -122.1676 | -122.0626 | -0.049705 | -0.23595 | 0.19333 | 0.071828 | 0.12153 | 0.030344 | -0.067184 | 0.18488 | 0.19722 | 0.30219 | 0.12959 | -122.3409 | 122.1289 | 122.3952 | 122.2976 | 0.67798 | -122.4145
3425.8594 | 122.4426 | -0.059509 | 122.2275 | -0.010149 | -0.050965 | 0.039439 | 0.019255 | -0.013147 | -0.0037989 | -0.029148 | -0.002694 | -0.0022903 | 0.05826 | 0.046457 | 0.047901 | -0.012688 | 0.0243 | -0.008409 | 0.079598 | 0.1011 | 0.20149 | -0.085952 | 0.083464 | 0.5727 | -0.0243 | 122.0281 | 122.2807 | 122.1832 | -0.15499 | -0.026443 | -122.1479 | 0.046821 | 0.0511 | 0.077543 | -122.1264 | -122.026 | -0.095482 | -0.19933 | 0.14297 | 0.035209 | 0.13069 | 0.05323 | -0.044298 | 0.13911 | 0.1606 | 0.261 | 0.083809 | -122.3134 | 122.0877 | 122.3402 | 122.2427 | 0.63221 | -122.3825
3427.625 | 122.3419 | -0.10986 | 122.2824 | -0.01778 | -0.050965 | 0.039225 | 0.019255 | -0.012933 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.04667 | 0.04726 | -0.012688 | 0.0243 | -0.008409 | 0.079598 | 0.091937 | 0.20607 | -0.081373 | 0.092622 | 0.5727 | -0.033458 | 122.019 | 122.2899 | 122.1786 | -0.15041 | 0.02849 | -122.2028 | 0.097175 | 0.10145 | 0.072964 | -122.1905 | -122.0763 | -0.040549 | -0.26342 | 0.20248 | 0.076405 | 0.11695 | 0.007455 | -0.10381 | 0.18946 | 0.2018 | 0.31593 | 0.13416 | -122.3638 | 122.1289 | 122.3997 | 122.2885 | 0.68256 | -122.4328
3429.3281 | 122.3602 | -0.073242 | 122.2824 | -0.010149 | -0.050965 | 0.039011 | 0.019255 | -0.013147 | -0.0040125 | -0.013887 | -0.0022666 | -0.0025041 | 0.058046 | 0.04667 | 0.047474 | -0.017266 | 0.019721 | -0.017566 | 0.079598 | 0.096516 | 0.19233 | -0.081373 | 0.088043 | 0.5727 | -0.033458 | 122.019 | 122.2899 | 122.1923 | -0.14583 | -0.008131 | -122.2028 | 0.055976 | 0.055676 | 0.063807 | -122.1859 | -122.0901 | -0.072591 | -0.26342 | 0.16129 | 0.039784 | 0.11237 | 0.007455 | -0.090073 | 0.15284 | 0.16976 | 0.26557 | 0.092963 | -122.3638 | 122.0922 | 122.3631 | 122.2656 | 0.64594 | -122.4282
3431.1094 | 122.4609 | -0.068665 | 122.2229 | -0.0025182 | -0.050538 | 0.039652 | 0.019469 | -0.013147 | -0.0035853 | -0.013887 | -0.0024804 | -0.0025041 | 0.058046 | 0.046243 | 0.04726 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.1011 | 0.20149 | -0.085952 | 0.083464 | 0.58186 | -0.028879 | 122.0236 | 122.2899 | 122.1878 | -0.15041 | -0.017287 | -122.1387 | 0.046821 | 0.060256 | 0.077543 | -122.1218 | -122.0214 | -0.081747 | -0.19933 | 0.15213 | 0.039786 | 0.12153 | 0.066965 | -0.035141 | 0.15284 | 0.16976 | 0.27015 | 0.092965 | -122.3089 | 122.0922 | 122.3585 | 122.2564 | 0.65052 | -122.3733
3432.8125 | 122.3877 | -0.073242 | 122.2778 | -0.0025182 | -0.050965 | 0.039225 | 0.019469 | -0.013147 | -0.0035853 | -0.021518 | -0.0022666 | -0.0025041 | 0.05826 | 0.046884 | 0.047474 | -0.021844 | 0.0243 | -0.003831 | 0.084176 | 0.091937 | 0.19691 | -0.085952 | 0.092622 | 0.5727 | -0.033458 | 122.0236 | 122.2853 | 122.1878 | -0.15041 | -0.01271 | -122.1937 | 0.051398 | 0.069411 | 0.082121 | -122.1859 | -122.0809 | -0.07717 | -0.25426 | 0.16586 | 0.039784 | 0.11695 | 0.007455 | -0.090073 | 0.15742 | 0.16518 | 0.27015 | 0.097542 | -122.3638 | 122.0968 | 122.3585 | 122.261 | 0.64594 | -122.4282
3434.5781 | 122.3419 | -0.10071 | 122.2641 | -0.025411 | -0.050965 | 0.039225 | 0.018828 | -0.012933 | -0.0037989 | -0.021518 | -0.002694 | -0.0025041 | 0.05826 | 0.046884 | 0.047687 | -0.008109 | 0.028878 | -0.008409 | 0.084176 | 0.1011 | 0.18775 | -0.085952 | 0.092622 | 0.5727 | -0.038036 | 122.0236 | 122.2899 | 122.1878 | -0.15499 | 0.014756 | -122.1799 | 0.092599 | 0.092299 | 0.077543 | -122.163 | -122.0763 | -0.054283 | -0.24053 | 0.19333 | 0.062672 | 0.11695 | 0.025766 | -0.07634 | 0.18488 | 0.2018 | 0.28846 | 0.12959 | -122.3501 | 122.1243 | 122.3906 | 122.2885 | 0.67341 | -122.4191
3436.3281 | 122.4472 | -0.073242 | 122.2366 | 0.0051128 | -0.051179 | 0.039439 | 0.019469 | -0.01336 | -0.0035853 | -0.036779 | -0.0022666 | -0.0027177 | 0.057832 | 0.04667 | 0.047687 | -0.017266 | 0.019721 | -0.012988 | 0.079598 | 0.1011 | 0.20149 | -0.081373 | 0.083464 | 0.57728 | -0.033458 | 122.0281 | 122.2853 | 122.1878 | -0.15499 | -0.008131 | -122.157 | 0.055976 | 0.060254 | 0.068385 | -122.1355 | -122.0351 | -0.081749 | -0.20848 | 0.15671 | 0.039784 | 0.12153 | 0.048654 | -0.048874 | 0.15284 | 0.17434 | 0.27473 | 0.092963 | -122.318 | 122.1014 | 122.3585 | 122.261 | 0.65052 | -122.3916
3438.0781 | 122.4472 | -0.054932 | 122.2412 | -0.01778 | -0.051179 | 0.039225 | 0.019255 | -0.013574 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.058046 | 0.046884 | 0.047687 | -0.021844 | 0.0243 | -0.003831 | 0.088755 | 0.096516 | 0.19691 | -0.081373 | 0.083464 | 0.5727 | -0.033458 | 122.0281 | 122.2853 | 122.1832 | -0.15499 | -0.026441 | -122.1525 | 0.033088 | 0.051101 | 0.077542 | -122.1447 | -122.0443 | -0.10006 | -0.21306 | 0.1384 | 0.021474 | 0.12153 | 0.044076 | -0.058031 | 0.14369 | 0.15145 | 0.25184 | 0.079232 | -122.3226 | 122.0831 | 122.3402 | 122.2381 | 0.62763 | -122.3962
3439.8438 | 122.4152 | -0.064087 | 122.2549 | -0.010149 | -0.051393 | 0.039439 | 0.019469 | -0.012933 | -0.0037989 | -0.021518 | -0.0024804 | -0.0018631 | 0.058046 | 0.04667 | 0.047474 | -0.017266 | 0.015142 | -0.008409 | 0.079598 | 0.096516 | 0.19691 | -0.085952 | 0.083464 | 0.5727 | -0.033458 | 122.0236 | 122.2899 | 122.1878 | -0.15041 | -0.021865 | -122.1753 | 0.046821 | 0.055678 | 0.077543 | -122.1584 | -122.058 | -0.086325 | -0.23137 | 0.14755 | 0.030629 | 0.11695 | 0.034921 | -0.067185 | 0.14369 | 0.1606 | 0.261 | 0.079229 | -122.3409 | 122.0877 | 122.354 | 122.2518 | 0.63679 | -122.4054
3441.6094 | 122.4564 | -0.041199 | 122.2275 | -0.01778 | -0.050965 | 0.039225 | 0.019682 | -0.013147 | -0.0033715 | -0.029148 | -0.002694 | -0.0018631 | 0.057832 | 0.047098 | 0.047687 | -0.017266 | 0.019721 | -0.003831 | 0.079598 | 0.1011 | 0.19691 | -0.081373 | 0.083464 | 0.57728 | -0.038036 | 122.0236 | 122.2899 | 122.1832 | -0.15957 | -0.040174 | -122.1479 | 0.023933 | 0.037368 | 0.077542 | -122.1264 | -122.0306 | -0.11837 | -0.20391 | 0.12466 | 0.003163 | 0.12153 | 0.062387 | -0.044298 | 0.1208 | 0.14229 | 0.23811 | 0.06092 | -122.3089 | 122.0648 | 122.3311 | 122.2244 | 0.61847 | -122.387
3443.3594 | 122.4701 | -0.064087 | 122.2458 | -0.025411 | -0.051393 | 0.039225 | 0.019469 | -0.012719 | -0.0037989 | -0.036779 | -0.0024804 | -0.0022903 | 0.058046 | 0.047098 | 0.047474 | -0.021844 | 0.019721 | -0.012988 | 0.084176 | 0.096516 | 0.20607 | -0.081373 | 0.088043 | 0.58186 | -0.033458 | 122.0281 | 122.2853 | 122.1878 | -0.15499 | -0.017286 | -122.1616 | 0.042243 | 0.051099 | 0.068385 | -122.1493 | -122.0397 | -0.090904 | -0.21764 | 0.15213 | 0.030629 | 0.12153 | 0.039498 | -0.05803 | 0.14826 | 0.1606 | 0.27015 | 0.083808 | -122.3272 | 122.0922 | 122.3494 | 122.2518 | 0.64594 | -122.4008
3445.1094 | 122.4152 | -0.07782 | 122.2412 | -0.010149 | -0.051179 | 0.039011 | 0.019255 | -0.012933 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.04667 | 0.04726 | -0.017266 | 0.0243 | -0.008409 | 0.079598 | 0.091937 | 0.19691 | -0.076794 | 0.088043 | 0.58186 | -0.042615 | 122.0236 | 122.2944 | 122.1786 | -0.15957 | 0.001026 | -122.1616 | 0.060554 | 0.069411 | 0.068385 | -122.1493 | -122.0443 | -0.08175 | -0.21764 | 0.16586 | 0.035205 | 0.11695 | 0.053233 | -0.062609 | 0.15742 | 0.16976 | 0.27473 | 0.10212 | -122.318 | 122.1014 | 122.3723 | 122.2564 | 0.65968 | -122.4008
3446.8125 | 122.4655 | -0.064087 | 122.2595 | -0.01778 | -0.051393 | 0.039652 | 0.019255 | -0.012933 | -0.0035853 | -0.013887 | -0.0022666 | -0.0025041 | 0.057832 | 0.046884 | 0.047687 | -0.021844 | 0.0243 | -0.008409 | 0.07502 | 0.1011 | 0.20149 | -0.081373 | 0.092622 | 0.58643 | -0.033458 | 122.019 | 122.2944 | 122.1832 | -0.15499 | -0.017286 | -122.1845 | 0.042243 | 0.055678 | 0.072964 | -122.1584 | -122.058 | -0.090904 | -0.24053 | 0.15671 | 0.030629 | 0.12153 | 0.034923 | -0.076341 | 0.13911 | 0.16518 | 0.26558 | 0.088387 | -122.3409 | 122.0831 | 122.3585 | 122.2473 | 0.65052 | -122.4145
3448.5625 | 122.4609 | -0.054932 | 122.2366 | -0.0025182 | -0.051393 | 0.039652 | 0.019255 | -0.013574 | -0.0037989 | -0.029148 | -0.002694 | -0.0018631 | 0.058046 | 0.046884 | 0.047474 | -0.008109 | 0.010564 | -0.008409 | 0.07502 | 0.10567 | 0.20607 | -0.081373 | 0.088043 | 0.58186 | -0.028879 | 122.019 | 122.2853 | 122.1878 | -0.15957 | -0.026441 | -122.1616 | 0.046823 | 0.046523 | 0.072964 | -122.131 | -122.0306 | -0.10464 | -0.21764 | 0.14297 | 0.026053 | 0.13069 | 0.048654 | -0.048874 | 0.12995 | 0.16061 | 0.261 | 0.065496 | -122.318 | 122.0739 | 122.3402 | 122.2427 | 0.63679 | -122.3962
3450.3281 | 122.4106 | -0.07782 | 122.2366 | -0.01778 | -0.051179 | 0.039652 | 0.019469 | -0.012933 | -0.0040125 | -0.029148 | -0.002694 | -0.0022903 | 0.057619 | 0.04667 | 0.047474 | -0.021844 | 0.015142 | -0.003831 | 0.088755 | 0.10567 | 0.20149 | -0.076794 | 0.088043 | 0.58186 | -0.033458 | 122.0281 | 122.2944 | 122.1832 | -0.14583 | 0.001026 | -122.1479 | 0.055976 | 0.073989 | 0.072963 | -122.131 | -122.0351 | -0.068013 | -0.20848 | 0.16586 | 0.044362 | 0.11237 | 0.057811 | -0.053453 | 0.16658 | 0.18349 | 0.27931 | 0.092962 | -122.3134 | 122.106 | 122.3723 | 122.261 | 0.65968 | -122.3825
3452.0312 | 122.4197 | -0.07782 | 122.2366 | -0.010149 | -0.051179 | 0.039439 | 0.019041 | -0.01336 | -0.0042263 | -0.021518 | -0.0024804 | -0.0025041 | 0.058046 | 0.046884 | 0.047687 | -0.017266 | 0.015142 | -0.012988 | 0.079598 | 0.1011 | 0.20149 | -0.085952 | 0.088043 | 0.57728 | -0.028879 | 122.019 | 122.2853 | 122.1832 | -0.15499 | -0.008132 | -122.157 | 0.060554 | 0.064832 | 0.072964 | -122.1355 | -122.0351 | -0.077171 | -0.21764 | 0.16586 | 0.048941 | 0.12611 | 0.048654 | -0.053453 | 0.15742 | 0.17891 | 0.27931 | 0.092962 | -122.3226 | 122.0968 | 122.3631 | 122.261 | 0.6551 | -122.3916
3453.7812 | 122.4655 | -0.054932 | 122.2504 | -0.0025182 | -0.051393 | 0.039652 | 0.019255 | -0.01336 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.058046 | 0.046884 | 0.047474 | -0.017266 | 0.028878 | -0.008409 | 0.084176 | 0.096516 | 0.20607 | -0.076794 | 0.088043 | 0.5727 | -0.033458 | 122.0236 | 122.299 | 122.1923 | -0.15957 | -0.021862 | -122.1662 | 0.037666 | 0.046523 | 0.068385 | -122.1539 | -122.0443 | -0.10464 | -0.2268 | 0.14297 | 0.021474 | 0.12611 | 0.048657 | -0.058029 | 0.13911 | 0.15145 | 0.261 | 0.08381 | -122.3272 | 122.0785 | 122.354 | 122.2473 | 0.62763 | -122.4099
3455.5469 | 122.4747 | -0.050354 | 122.2092 | -0.010149 | -0.051393 | 0.039439 | 0.019255 | -0.013147 | -0.0040125 | -0.029148 | -0.002694 | -0.0022903 | 0.058046 | 0.047098 | 0.047474 | -0.021844 | 0.015142 | -0.003831 | 0.079598 | 0.096516 | 0.19233 | -0.085952 | 0.083464 | 0.58186 | -0.033458 | 122.0236 | 122.2944 | 122.1878 | -0.15041 | -0.035598 | -122.1296 | 0.02851 | 0.046523 | 0.082121 | -122.1127 | -122.0168 | -0.10006 | -0.1856 | 0.13382 | 0.016896 | 0.11695 | 0.085277 | -0.021408 | 0.12995 | 0.14687 | 0.24269 | 0.065496 | -122.2951 | 122.0739 | 122.3448 | 122.2381 | 0.63221 | -122.3596
3457.3125 | 122.4747 | -0.036621 | 122.2504 | -0.01778 | -0.051393 | 0.039866 | 0.019041 | -0.01336 | -0.0040125 | -0.021518 | -0.002694 | -0.0022903 | 0.057832 | 0.046884 | 0.047046 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.1011 | 0.20149 | -0.090531 | 0.092622 | 0.58186 | -0.033458 | 122.019 | 122.299 | 122.1786 | -0.15957 | -0.05391 | -122.1753 | 0.019355 | 0.023633 | 0.077543 | -122.1493 | -122.0489 | -0.12295 | -0.23137 | 0.12924 | 0.003163 | 0.12611 | 0.048657 | -0.071764 | 0.11164 | 0.13772 | 0.23811 | 0.056342 | -122.3409 | 122.0556 | 122.3356 | 122.2152 | 0.61848 | -122.4099
3459.0156 | 122.3877 | -0.10071 | 122.2412 | -0.010149 | -0.051606 | 0.04008 | 0.019255 | -0.013147 | -0.0040125 | -0.021518 | -0.002694 | -0.0022903 | 0.057832 | 0.047098 | 0.047474 | -0.012688 | 0.0243 | -0.012988 | 0.084176 | 0.096516 | 0.19233 | -0.081373 | 0.088043 | 0.58186 | -0.028879 | 122.0236 | 122.299 | 122.1878 | -0.15041 | 0.019335 | -122.157 | 0.08802 | 0.08772 | 0.068385 | -122.1447 | -122.0489 | -0.049704 | -0.21764 | 0.18875 | 0.071829 | 0.12153 | 0.057812 | -0.053452 | 0.18488 | 0.19722 | 0.29304 | 0.12501 | -122.3226 | 122.1243 | 122.3997 | 122.2885 | 0.68256 | -122.3916
3460.7969 | 122.4564 | -0.045776 | 122.2504 | -0.0025182 | -0.051393 | 0.04008 | 0.019255 | -0.013147 | -0.0037989 | -0.013887 | -0.0022666 | -0.0025041 | 0.05826 | 0.046884 | 0.047474 | -0.021844 | 0.0243 | -0.017566 | 0.084176 | 0.096516 | 0.20149 | -0.090531 | 0.088043 | 0.58186 | -0.033458 | 122.019 | 122.299 | 122.1878 | -0.15041 | -0.044755 | -122.1662 | 0.023932 | 0.02821 | 0.072965 | -122.1539 | -122.0489 | -0.10464 | -0.23137 | 0.13382 | 0.012318 | 0.11695 | 0.048657 | -0.062607 | 0.12995 | 0.14229 | 0.24726 | 0.070076 | -122.3409 | 122.0648 | 122.3448 | 122.2335 | 0.62763 | -122.4008
3462.5625 | 122.374 | -0.086975 | 122.2549 | -0.01778 | -0.051606 | 0.039866 | 0.019041 | -0.01336 | -0.0040125 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.047098 | 0.047474 | -0.021844 | 0.0243 | -0.012988 | 0.07502 | 0.091937 | 0.20149 | -0.081373 | 0.088043 | 0.57728 | -0.033458 | 122.0373 | 122.299 | 122.1832 | -0.15499 | 0.005602 | -122.1799 | 0.065131 | 0.073987 | 0.068385 | -122.163 | -122.0535 | -0.068016 | -0.21764 | 0.17502 | 0.053517 | 0.12153 | 0.044079 | -0.071764 | 0.162 | 0.17891 | 0.28846 | 0.11127 | -122.3363 | 122.1243 | 122.386 | 122.2702 | 0.66425 | -122.4099
3464.3125 | 122.3419 | -0.086975 | 122.2778 | -0.01778 | -0.051606 | 0.04008 | 0.019255 | -0.013147 | -0.0042263 | -0.029148 | -0.0024804 | -0.0022903 | 0.058046 | 0.04667 | 0.047474 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.091937 | 0.19691 | -0.085952 | 0.092622 | 0.58643 | -0.028879 | 122.0236 | 122.2944 | 122.1878 | -0.15957 | 0.001023 | -122.2028 | 0.069709 | 0.073987 | 0.072964 | -122.1859 | -122.0809 | -0.072595 | -0.25426 | 0.1796 | 0.058096 | 0.13069 | 0.016612 | -0.090073 | 0.162 | 0.17891 | 0.28388 | 0.1067 | -122.3638 | 122.1105 | 122.3814 | 122.2747 | 0.67341 | -122.4374
3466 | 122.493 | -0.059509 | 122.2321 | -0.0025182 | -0.051606 | 0.039652 | 0.019469 | -0.01336 | -0.0040125 | -0.021518 | -0.0024804 | -0.0029313 | 0.05826 | 0.04667 | 0.047474 | -0.026423 | 0.015142 | -0.012988 | 0.084176 | 0.1011 | 0.20607 | -0.085952 | 0.083464 | 0.57728 | -0.038036 | 122.0281 | 122.2899 | 122.1878 | -0.15499 | -0.026443 | -122.1479 | 0.033086 | 0.046521 | 0.072964 | -122.131 | -122.026 | -0.095482 | -0.20391 | 0.14297 | 0.021473 | 0.11695 | 0.057809 | -0.044297 | 0.14369 | 0.1606 | 0.26558 | 0.074651 | -122.318 | 122.0877 | 122.3494 | 122.2473 | 0.63679 | -122.387
3467.75 | 122.4106 | -0.064087 | 122.2504 | -0.010149 | -0.05182 | 0.039652 | 0.019255 | -0.013147 | -0.0040125 | -0.0062567 | -0.0022666 | -0.0022903 | 0.058046 | 0.047098 | 0.047901 | -0.026423 | 0.019721 | -0.017566 | 0.084176 | 0.10567 | 0.20607 | -0.085952 | 0.097201 | 0.58186 | -0.028879 | 122.0281 | 122.2853 | 122.1923 | -0.15499 | -0.021865 | -122.1662 | 0.037664 | 0.046521 | 0.068386 | -122.1447 | -122.0443 | -0.090904 | -0.22222 | 0.16129 | 0.035208 | 0.12611 | 0.034921 | -0.058029 | 0.14826 | 0.16976 | 0.27015 | 0.083808 | -122.3363 | 122.0922 | 122.3494 | 122.2564 | 0.64594 | -122.4054
3469.5156 | 122.3785 | -0.082397 | 122.2366 | 0.0051128 | -0.051606 | 0.039866 | 0.019469 | -0.01336 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.057832 | 0.047098 | 0.047901 | -0.021844 | 0.015142 | -0.012988 | 0.084176 | 0.096516 | 0.20607 | -0.081373 | 0.088043 | 0.58186 | -0.033458 | 122.0236 | 122.2853 | 122.1923 | -0.15499 | 0.001024 | -122.1525 | 0.060553 | 0.069409 | 0.068385 | -122.1401 | -122.0306 | -0.072594 | -0.21306 | 0.17044 | 0.048939 | 0.12153 | 0.048654 | -0.044296 | 0.16657 | 0.17891 | 0.28846 | 0.097539 | -122.318 | 122.106 | 122.3677 | 122.2747 | 0.66425 | -122.3916
3471.2344 | 122.4609 | -0.054932 | 122.2366 | -0.01778 | -0.051393 | 0.039652 | 0.019255 | -0.01336 | -0.0040125 | -0.013887 | -0.0022666 | -0.0020767 | 0.05826 | 0.047098 | 0.047474 | -0.012688 | 0.0243 | -0.008409 | 0.079598 | 0.096516 | 0.20607 | -0.081373 | 0.088043 | 0.58186 | -0.033458 | 122.0281 | 122.2899 | 122.1878 | -0.15957 | -0.026441 | -122.157 | 0.042244 | 0.046523 | 0.072964 | -122.1401 | -122.0306 | -0.10464 | -0.20848 | 0.14297 | 0.021474 | 0.12611 | 0.053232 | -0.048874 | 0.13453 | 0.15145 | 0.261 | 0.079232 | -122.318 | 122.0831 | 122.3448 | 122.2427 | 0.63679 | -122.3962
3472.9844 | 122.4426 | -0.073242 | 122.2412 | -0.01778 | -0.05182 | 0.039866 | 0.019469 | -0.013147 | -0.0037989 | -0.029148 | -0.0024804 | -0.0020767 | 0.057832 | 0.046884 | 0.047474 | -0.017266 | 0.0243 | -0.008409 | 0.084176 | 0.096516 | 0.20149 | -0.090531 | 0.088043 | 0.59101 | -0.038036 | 122.0281 | 122.2944 | 122.1832 | -0.15499 | -0.017289 | -122.157 | 0.055976 | 0.064833 | 0.082122 | -122.1447 | -122.0397 | -0.081749 | -0.21306 | 0.16129 | 0.035206 | 0.11695 | 0.053233 | -0.058031 | 0.15742 | 0.16976 | 0.27473 | 0.097542 | -122.3317 | 122.1014 | 122.3677 | 122.2564 | 0.66426 | -122.3962
3474.7344 | 122.4152 | -0.068665 | 122.2549 | -0.010149 | -0.052034 | 0.039439 | 0.019469 | -0.012933 | -0.0040125 | -0.021518 | -0.0022666 | -0.0022903 | 0.057405 | 0.047098 | 0.047687 | -0.017266 | 0.028878 | -0.012988 | 0.084176 | 0.096516 | 0.20149 | -0.090531 | 0.088043 | 0.58643 | -0.033458 | 122.0236 | 122.2899 | 122.1832 | -0.15957 | -0.021866 | -122.1708 | 0.051399 | 0.055677 | 0.077543 | -122.1584 | -122.0535 | -0.090905 | -0.23137 | 0.15671 | 0.035207 | 0.12611 | 0.034921 | -0.071764 | 0.15284 | 0.16518 | 0.27015 | 0.097543 | -122.3455 | 122.0922 | 122.3585 | 122.2518 | 0.6551 | -122.4145
3476.5 | 122.3602 | -0.10986 | 122.2824 | -0.010149 | -0.05182 | 0.039652 | 0.019041 | -0.013147 | -0.0042263 | -0.021518 | -0.0022666 | -0.0025041 | 0.057619 | 0.047098 | 0.047687 | -0.017266 | 0.015142 | -0.003831 | 0.079598 | 0.10567 | 0.19691 | -0.090531 | 0.092622 | 0.57728 | -0.028879 | 122.019 | 122.2899 | 122.1878 | -0.15041 | 0.019332 | -122.2028 | 0.092597 | 0.10603 | 0.0867 | -122.1767 | -122.0855 | -0.040549 | -0.26342 | 0.20248 | 0.080984 | 0.12153 | 0.007455 | -0.094651 | 0.18946 | 0.21554 | 0.30677 | 0.12501 | -122.3729 | 122.1289 | 122.3997 | 122.2976 | 0.68714 | -122.4328
3478.2031 | 122.3282 | -0.091553 | 122.2687 | -0.0025182 | -0.051393 | 0.039439 | 0.019255 | -0.01336 | -0.0037989 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.047311 | 0.047687 | -0.021844 | 0.019721 | 0.000747 | 0.084176 | 0.11025 | 0.20149 | -0.085952 | 0.097201 | 0.58186 | -0.0243 | 122.0281 | 122.2899 | 122.1969 | -0.15957 | 0.005601 | -122.1845 | 0.069709 | 0.0923 | 0.086699 | -122.1584 | -122.0672 | -0.068017 | -0.24053 | 0.18875 | 0.067253 | 0.13527 | 0.021188 | -0.071761 | 0.17573 | 0.20181 | 0.29304 | 0.11127 | -122.3546 | 122.1197 | 122.3814 | 122.2885 | 0.67341 | -122.4282
3479.9844 | 122.4106 | -0.086975 | 122.2733 | -0.010149 | -0.052034 | 0.039652 | 0.019255 | -0.013147 | -0.0037989 | -0.013887 | -0.0024804 | -0.0020767 | 0.058046 | 0.047311 | 0.047474 | -0.012688 | 0.019721 | -0.008409 | 0.079598 | 0.1011 | 0.20607 | -0.081373 | 0.088043 | 0.59101 | -0.028879 | 122.0236 | 122.299 | 122.1923 | -0.15499 | 0.005602 | -122.1937 | 0.074287 | 0.078566 | 0.072964 | -122.1722 | -122.0672 | -0.068016 | -0.24968 | 0.17502 | 0.058096 | 0.12611 | 0.025769 | -0.080917 | 0.16657 | 0.18807 | 0.29304 | 0.1067 | -122.3546 | 122.1105 | 122.386 | 122.2793 | 0.67799 | -122.4282
3481.6875 | 122.4335 | -0.068665 | 122.2366 | -0.010149 | -0.05182 | 0.039652 | 0.019469 | -0.013147 | -0.0037989 | -0.021518 | -0.0024804 | -0.0027177 | 0.057832 | 0.046884 | 0.047474 | -0.021844 | 0.019721 | -0.008409 | 0.084176 | 0.096516 | 0.20607 | -0.090531 | 0.088043 | 0.58186 | -0.033458 | 122.0144 | 122.2853 | 122.1923 | -0.15499 | -0.021866 | -122.1525 | 0.046821 | 0.060256 | 0.082122 | -122.1401 | -122.0306 | -0.086326 | -0.22222 | 0.15671 | 0.035207 | 0.12153 | 0.048654 | -0.044296 | 0.15284 | 0.16518 | 0.27473 | 0.088386 | -122.3272 | 122.0831 | 122.354 | 122.261 | 0.65052 | -122.3916
3483.4375 | 122.319 | -0.09613 | 122.2961 | -0.010149 | -0.052247 | 0.039866 | 0.019469 | -0.013147 | -0.0042263 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.046884 | 0.047474 | -0.003531 | 0.0243 | -0.008409 | 0.084176 | 0.1011 | 0.20607 | -0.085952 | 0.088043 | 0.58643 | -0.028879 | 122.0281 | 122.2944 | 122.1969 | -0.15041 | 0.010178 | -122.212 | 0.092599 | 0.087721 | 0.077543 | -122.195 | -122.0901 | -0.054282 | -0.26799 | 0.18417 | 0.067251 | 0.12153 | -0.001699 | -0.099227 | 0.18031 | 0.19722 | 0.3022 | 0.12043 | -122.3821 | 122.1243 | 122.3906 | 122.293 | 0.68256 | -122.4466
3485.2031 | 122.4609 | -0.032043 | 122.2321 | -0.01778 | -0.05182 | 0.039866 | 0.019255 | -0.013147 | -0.0035853 | -0.029148 | -0.0024804 | -0.0022903 | 0.057405 | 0.047098 | 0.047687 | -0.017266 | 0.0243 | -0.012988 | 0.084176 | 0.091937 | 0.19691 | -0.09511 | 0.088043 | 0.59101 | -0.028879 | 122.019 | 122.2899 | 122.1878 | -0.15499 | -0.063067 | -122.1479 | 0.014777 | 0.019055 | 0.082122 | -122.1401 | -122.0351 | -0.12295 | -0.21306 | 0.12009 | 0.003164 | 0.12611 | 0.057809 | -0.044297 | 0.11622 | 0.12398 | 0.22895 | 0.056343 | -122.3272 | 122.051 | 122.3219 | 122.2198 | 0.62306 | -122.387
3486.9688 | 122.3877 | -0.086975 | 122.2504 | -0.01778 | -0.05182 | 0.039866 | 0.019255 | -0.01336 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.058046 | 0.046884 | 0.047474 | -0.008109 | 0.015142 | -0.017566 | 0.084176 | 0.096516 | 0.20607 | -0.090531 | 0.092622 | 0.59101 | -0.0243 | 122.0281 | 122.2899 | 122.1878 | -0.15041 | -0.003556 | -122.1662 | 0.078866 | 0.069409 | 0.072965 | -122.1539 | -122.0443 | -0.063437 | -0.22222 | 0.1796 | 0.062675 | 0.12611 | 0.039499 | -0.062607 | 0.17115 | 0.18349 | 0.29304 | 0.10212 | -122.3409 | 122.1151 | 122.3768 | 122.2747 | 0.67799 | -122.4008
3488.6719 | 122.4747 | -0.059509 | 122.2229 | -0.01778 | -0.052034 | 0.039652 | 0.019255 | -0.013147 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.047098 | 0.047687 | -0.017266 | 0.015142 | -0.008409 | 0.084176 | 0.10567 | 0.20149 | -0.081373 | 0.083464 | 0.59559 | -0.033458 | 122.0236 | 122.299 | 122.1878 | -0.15499 | -0.021864 | -122.1387 | 0.042243 | 0.0511 | 0.072964 | -122.1172 | -122.0214 | -0.095482 | -0.19933 | 0.14297 | 0.026051 | 0.12153 | 0.076123 | -0.035141 | 0.14369 | 0.16518 | 0.261 | 0.074651 | -122.3043 | 122.0831 | 122.3585 | 122.2473 | 0.6551 | -122.3779
3490.4219 | 122.4976 | -0.045776 | 122.2549 | -0.010149 | -0.05182 | 0.039866 | 0.019255 | -0.01336 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.057832 | 0.046884 | 0.047687 | -0.017266 | 0.019721 | -0.008409 | 0.084176 | 0.10567 | 0.20149 | -0.081373 | 0.083464 | 0.59559 | -0.033458 | 122.0281 | 122.2899 | 122.1878 | -0.15041 | -0.035597 | -122.1708 | 0.02851 | 0.037367 | 0.072964 | -122.1493 | -122.0535 | -0.10464 | -0.22679 | 0.12924 | 0.012318 | 0.11695 | 0.034921 | -0.067185 | 0.12995 | 0.15145 | 0.24726 | 0.065497 | -122.3363 | 122.0739 | 122.3356 | 122.2335 | 0.64137 | -122.4054
3492.1875 | 122.4106 | -0.064087 | 122.2504 | -0.0025182 | -0.05182 | 0.039439 | 0.018828 | -0.012933 | -0.0037989 | -0.013887 | -0.0022666 | -0.0020767 | 0.057619 | 0.047098 | 0.047687 | -0.012688 | 0.0243 | -0.003831 | 0.084176 | 0.1011 | 0.20149 | -0.081373 | 0.092622 | 0.58643 | -0.033458 | 122.0236 | 122.2944 | 122.1923 | -0.15041 | -0.017286 | -122.1662 | 0.051399 | 0.060256 | 0.077542 | -122.1493 | -122.0489 | -0.086325 | -0.2268 | 0.15671 | 0.030629 | 0.11695 | 0.044078 | -0.058029 | 0.14826 | 0.16518 | 0.26558 | 0.088387 | -122.3317 | 122.0877 | 122.3585 | 122.2564 | 0.65052 | -122.4008
3493.9375 | 122.4472 | -0.064087 | 122.2321 | -0.01778 | -0.052034 | 0.039866 | 0.019469 | -0.01336 | -0.0040125 | -0.0062567 | -0.0024804 | -0.0025041 | 0.05826 | 0.047098 | 0.047474 | -0.012688 | 0.019721 | -0.008409 | 0.088755 | 0.10567 | 0.20607 | -0.090531 | 0.092622 | 0.58643 | -0.033458 | 122.0281 | 122.2899 | 122.1878 | -0.15957 | -0.026444 | -122.1433 | 0.051399 | 0.055678 | 0.082122 | -122.1264 | -122.026 | -0.095483 | -0.20391 | 0.15671 | 0.030629 | 0.12611 | 0.057809 | -0.044297 | 0.15284 | 0.16976 | 0.27015 | 0.083808 | -122.3226 | 122.0922 | 122.354 | 122.2518 | 0.65052 | -122.3916
3495.6875 | 122.4152 | -0.045776 | 122.2458 | -0.010149 | -0.05182 | 0.039652 | 0.019469 | -0.012933 | -0.0040125 | -0.013887 | -0.0024804 | -0.0022903 | 0.05826 | 0.047098 | 0.047474 | -0.017266 | 0.0243 | -0.008409 | 0.088755 | 0.1011 | 0.19691 | -0.090531 | 0.097201 | 0.59101 | -0.033458 | 122.0281 | 122.2899 | 122.1832 | -0.15499 | -0.044755 | -122.157 | 0.02851 | 0.037367 | 0.082122 | -122.1447 | -122.0489 | -0.10921 | -0.21764 | 0.14298 | 0.012318 | 0.12153 | 0.044076 | -0.062609 | 0.13453 | 0.14687 | 0.24268 | 0.070076 | -122.3363 | 122.0739 | 122.3356 | 122.229 | 0.63679 | -122.4008
3497.4531 | 122.4609 | -0.050354 | 122.2366 | -0.0025182 | -0.052034 | 0.039652 | 0.019469 | -0.013574 | -0.0035853 | -0.013887 | -0.0022666 | -0.0022903 | 0.057832 | 0.046884 | 0.047687 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.10567 | 0.19691 | -0.081373 | 0.092622 | 0.59559 | -0.028879 | 122.0281 | 122.2944 | 122.1923 | -0.15957 | -0.031019 | -122.1525 | 0.02851 | 0.041945 | 0.072964 | -122.131 | -122.0397 | -0.10922 | -0.20848 | 0.14298 | 0.021475 | 0.13069 | 0.057811 | -0.044296 | 0.13453 | 0.15603 | 0.24726 | 0.074654 | -122.318 | 122.0785 | 122.3448 | 122.2427 | 0.64594 | -122.3962
3499.1562 | 122.3969 | -0.091553 | 122.2595 | -0.0025182 | -0.052034 | 0.039866 | 0.019041 | -0.013147 | -0.0040125 | -0.013887 | -0.0024804 | -0.0027177 | 0.05826 | 0.046884 | 0.047687 | -0.017266 | 0.028878 | -0.012988 | 0.088755 | 0.1011 | 0.21064 | -0.085952 | 0.083464 | 0.59101 | -0.033458 | 122.0236 | 122.2944 | 122.1878 | -0.15957 | 0.005601 | -122.1708 | 0.074287 | 0.078565 | 0.072964 | -122.1584 | -122.0489 | -0.068017 | -0.23595 | 0.17502 | 0.058095 | 0.12611 | 0.034923 | -0.071762 | 0.18031 | 0.19265 | 0.3022 | 0.12043 | -122.3455 | 122.1151 | 122.386 | 122.2793 | 0.68257 | -122.4191
3500.9219 | 122.3877 | -0.086975 | 122.2595 | -0.010149 | -0.052034 | 0.039652 | 0.019255 | -0.013574 | -0.0037989 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.046884 | 0.04726 | -0.017266 | 0.019721 | -0.008409 | 0.088755 | 0.1011 | 0.20149 | -0.085952 | 0.097201 | 0.60017 | -0.028879 | 122.0281 | 122.299 | 122.1923 | -0.15499 | 0.001023 | -122.1708 | 0.069709 | 0.078566 | 0.077543 | -122.1584 | -122.058 | -0.068016 | -0.23137 | 0.18418 | 0.058096 | 0.12611 | 0.039502 | -0.067184 | 0.17573 | 0.18807 | 0.28846 | 0.1067 | -122.3455 | 122.1151 | 122.386 | 122.2793 | 0.68715 | -122.4145
3502.6875 | 122.4701 | -0.050354 | 122.2458 | -0.0025182 | -0.05182 | 0.039866 | 0.019469 | -0.012933 | -0.0037989 | -0.021518 | -0.002053 | -0.0018631 | 0.057832 | 0.04667 | 0.047901 | -0.021844 | 0.0243 | -0.008409 | 0.07502 | 0.1011 | 0.20149 | -0.090531 | 0.088043 | 0.59559 | -0.028879 | 122.0144 | 122.2899 | 122.1786 | -0.15041 | -0.040177 | -122.1708 | 0.02851 | 0.041945 | 0.082122 | -122.1447 | -122.0443 | -0.10006 | -0.23138 | 0.1384 | 0.021475 | 0.12153 | 0.044076 | -0.067187 | 0.12537 | 0.15145 | 0.25184 | 0.074654 | -122.3363 | 122.0648 | 122.3402 | 122.229 | 0.64594 | -122.3962
3504.3906 | 122.3328 | -0.086975 | 122.2733 | -0.010149 | -0.052247 | 0.039439 | 0.019469 | -0.013147 | -0.0035853 | -0.013887 | -0.0022666 | -0.0022903 | 0.058046 | 0.047098 | 0.04726 | -0.012688 | 0.0243 | -0.008409 | 0.079598 | 0.096516 | 0.20607 | -0.076794 | 0.088043 | 0.60017 | -0.028879 | 122.0144 | 122.2944 | 122.1923 | -0.15499 | 0.010181 | -122.1937 | 0.074287 | 0.078566 | 0.068385 | -122.1767 | -122.0672 | -0.068016 | -0.25884 | 0.17502 | 0.058096 | 0.12611 | 0.02119 | -0.080917 | 0.16657 | 0.18349 | 0.29304 | 0.11127 | -122.35 | 122.1014 | 122.3814 | 122.2793 | 0.68715 | -122.4282
3506.1406 | 122.3602 | -0.09613 | 122.2961 | -0.010149 | -0.052034 | 0.04008 | 0.019469 | -0.01336 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.05826 | 0.046884 | 0.047474 | -0.012688 | 0.015142 | -0.012988 | 0.084176 | 0.10567 | 0.20607 | -0.085952 | 0.088043 | 0.59101 | -0.0243 | 122.019 | 122.2944 | 122.1923 | -0.15957 | 0.010178 | -122.212 | 0.083442 | 0.083142 | 0.072964 | -122.1905 | -122.0901 | -0.06344 | -0.27715 | 0.18417 | 0.07183 | 0.13527 | -0.001699 | -0.10381 | 0.18031 | 0.2018 | 0.3022 | 0.11127 | -122.3821 | 122.1151 | 122.3906 | 122.2885 | 0.68714 | -122.4557
3507.9062 | 122.374 | -0.07782 | 122.2687 | -0.01778 | -0.052034 | 0.039866 | 0.019469 | -0.013147 | -0.0042263 | -0.021518 | -0.002694 | -0.0022903 | 0.057832 | 0.047311 | 0.047474 | -0.012688 | 0.0243 | 0.000747 | 0.079598 | 0.10567 | 0.20607 | -0.099689 | 0.083464 | 0.58643 | -0.033458 | 122.0098 | 122.2944 | 122.1969 | -0.15957 | -0.021869 | -122.1891 | 0.065132 | 0.078567 | 0.10044 | -122.163 | -122.0626 | -0.08175 | -0.25884 | 0.16128 | 0.044362 | 0.12611 | 0.025767 | -0.071761 | 0.15742 | 0.18349 | 0.28389 | 0.10212 | -122.3684 | 122.0877 | 122.3723 | 122.2747 | 0.66425 | -122.4282
3509.6562 | 122.4518 | -0.073242 | 122.2504 | -0.010149 | -0.052247 | 0.039652 | 0.019682 | -0.013147 | -0.0035853 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.047098 | 0.04726 | -0.017266 | 0.015142 | -0.008409 | 0.079598 | 0.096516 | 0.19691 | -0.081373 | 0.083464 | 0.59101 | -0.028879 | 122.0144 | 122.2944 | 122.1832 | -0.15041 | -0.008131 | -122.1708 | 0.055976 | 0.064833 | 0.072964 | -122.1539 | -122.0535 | -0.07717 | -0.23595 | 0.15671 | 0.044363 | 0.12153 | 0.044078 | -0.067186 | 0.15284 | 0.16976 | 0.27015 | 0.088384 | -122.3317 | 122.0877 | 122.3677 | 122.2564 | 0.66426 | -122.4008
3511.3438 | 122.4564 | -0.041199 | 122.2458 | -0.01778 | -0.052247 | 0.039439 | 0.019469 | -0.013147 | -0.0037989 | -0.013887 | -0.0022666 | -0.0022903 | 0.057832 | 0.047098 | 0.04726 | -0.017266 | 0.015142 | -0.008409 | 0.084176 | 0.10567 | 0.20149 | -0.09511 | 0.083464 | 0.59559 | -0.033458 | 122.0144 | 122.2944 | 122.1969 | -0.15499 | -0.053911 | -122.1616 | 0.023933 | 0.03279 | 0.086701 | -122.1401 | -122.0443 | -0.11379 | -0.23138 | 0.12466 | 0.007741 | 0.12153 | 0.048655 | -0.048873 | 0.12538 | 0.14687 | 0.24269 | 0.056341 | -122.3409 | 122.0556 | 122.3356 | 122.2381 | 0.63679 | -122.4008
3513.1094 | 122.3648 | -0.091553 | 122.2733 | -0.01778 | -0.052247 | 0.039439 | 0.019682 | -0.01336 | -0.0037989 | -0.021518 | -0.0024804 | -0.0020767 | 0.057405 | 0.047098 | 0.04726 | -0.017266 | 0.0243 | -0.008409 | 0.07502 | 0.091937 | 0.19233 | -0.081373 | 0.092622 | 0.59559 | -0.033458 | 122.0144 | 122.2853 | 122.1969 | -0.15957 | 0.01018 | -122.1982 | 0.074287 | 0.083144 | 0.072964 | -122.1813 | -122.0809 | -0.068017 | -0.25884 | 0.18417 | 0.058095 | 0.12611 | 0.012033 | -0.076338 | 0.16657 | 0.18349 | 0.28388 | 0.11585 | -122.3546 | 122.106 | 122.3768 | 122.2885 | 0.68714 | -122.4328
3514.8125 | 122.3831 | -0.10071 | 122.2778 | -0.01778 | -0.052034 | 0.039439 | 0.019469 | -0.013147 | -0.0035853 | -0.013887 | -0.002694 | -0.0020767 | 0.057832 | 0.047311 | 0.047474 | -0.021844 | 0.019721 | -0.012988 | 0.079598 | 0.091937 | 0.19691 | -0.081373 | 0.097201 | 0.60017 | -0.033458 | 122.019 | 122.2899 | 122.1878 | -0.15499 | 0.019335 | -122.1982 | 0.078864 | 0.08772 | 0.068385 | -122.1859 | -122.0809 | -0.054283 | -0.25884 | 0.19791 | 0.06725 | 0.12153 | 0.012033 | -0.090073 | 0.18031 | 0.19265 | 0.29762 | 0.12043 | -122.3592 | 122.1197 | 122.3906 | 122.2885 | 0.70088 | -122.4328
3516.5781 | 122.4106 | -0.073242 | 122.2321 | -0.0025182 | -0.052247 | 0.039225 | 0.019469 | -0.013147 | -0.0035853 | -0.0062567 | -0.0024804 | -0.0020767 | 0.057832 | 0.047525 | 0.047474 | -0.017266 | 0.019721 | -0.012988 | 0.084176 | 0.096516 | 0.20149 | -0.085952 | 0.083464 | 0.59101 | -0.028879 | 122.0144 | 122.2944 | 122.1878 | -0.15957 | -0.01271 | -122.1479 | 0.055976 | 0.060254 | 0.072964 | -122.1355 | -122.0306 | -0.086328 | -0.21764 | 0.15671 | 0.044363 | 0.13069 | 0.062388 | -0.044297 | 0.15742 | 0.16976 | 0.27473 | 0.092963 | -122.318 | 122.0877 | 122.3677 | 122.261 | 0.66426 | -122.3916
3518.3438 | 122.4884 | -0.064087 | 122.2366 | -0.0025182 | -0.052247 | 0.039652 | 0.019255 | -0.012719 | -0.0037989 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.047311 | 0.047474 | -0.021844 | 0.015142 | -0.017566 | 0.079598 | 0.096516 | 0.20149 | -0.085952 | 0.088043 | 0.59559 | -0.038036 | 122.0281 | 122.2944 | 122.1878 | -0.15499 | -0.021865 | -122.157 | 0.042243 | 0.046521 | 0.068386 | -122.1401 | -122.0351 | -0.090904 | -0.20848 | 0.15213 | 0.026051 | 0.11695 | 0.057811 | -0.048874 | 0.14369 | 0.1606 | 0.26558 | 0.079229 | -122.3226 | 122.0922 | 122.3585 | 122.2518 | 0.65968 | -122.3916
3520.0625 | 122.3877 | -0.082397 | 122.2778 | -0.010149 | -0.052034 | 0.039439 | 0.019469 | -0.013147 | -0.0037989 | -0.013887 | -0.0022666 | -0.0022903 | 0.05826 | 0.047311 | 0.047687 | -0.017266 | 0.0243 | -0.012988 | 0.079598 | 0.096516 | 0.20149 | -0.081373 | 0.078886 | 0.60017 | -0.0243 | 122.0144 | 122.2853 | 122.1923 | -0.15041 | 0.001024 | -122.1982 | 0.065131 | 0.069409 | 0.068385 | -122.1813 | -122.0763 | -0.068015 | -0.26342 | 0.16128 | 0.058097 | 0.12611 | 0.007455 | -0.085495 | 0.162 | 0.17891 | 0.28388 | 0.1067 | -122.3592 | 122.0968 | 122.3677 | 122.2747 | 0.68257 | -122.4282
3521.8438 | 122.4609 | -0.050354 | 122.2366 | -0.010149 | -0.052247 | 0.039439 | 0.019469 | -0.01336 | -0.0033715 | -0.029148 | -0.0022666 | -0.0022903 | 0.058046 | 0.047311 | 0.04726 | -0.026423 | 0.019721 | -0.008409 | 0.084176 | 0.096516 | 0.21064 | -0.081373 | 0.092622 | 0.60475 | -0.028879 | 122.0144 | 122.2944 | 122.1969 | -0.15957 | -0.031019 | -122.1525 | 0.023931 | 0.041945 | 0.072964 | -122.1401 | -122.026 | -0.10922 | -0.22222 | 0.14298 | 0.021475 | 0.13069 | 0.057811 | -0.039717 | 0.13453 | 0.14687 | 0.261 | 0.070075 | -122.318 | 122.0648 | 122.3448 | 122.2473 | 0.6551 | -122.3962
3523.6094 | 122.438 | -0.050354 | 122.2412 | -0.01778 | -0.052247 | 0.039225 | 0.019469 | -0.01336 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.05826 | 0.047311 | 0.04726 | -0.012688 | 0.019721 | -0.003831 | 0.079598 | 0.1011 | 0.19691 | -0.085952 | 0.083464 | 0.59559 | -0.028879 | 122.0236 | 122.2899 | 122.1878 | -0.15499 | -0.035598 | -122.1616 | 0.037666 | 0.046523 | 0.082121 | -122.1401 | -122.0443 | -0.10464 | -0.21764 | 0.13382 | 0.021475 | 0.12611 | 0.048654 | -0.053452 | 0.12995 | 0.15145 | 0.24726 | 0.070075 | -122.3272 | 122.0739 | 122.3402 | 122.2381 | 0.64594 | -122.3962
3525.375 | 122.3328 | -0.10071 | 122.2778 | -0.010149 | -0.052247 | 0.039866 | 0.019255 | -0.013147 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.047098 | 0.04726 | -0.021844 | 0.019721 | -0.008409 | 0.084176 | 0.1011 | 0.19691 | -0.081373 | 0.088043 | 0.60017 | -0.028879 | 122.019 | 122.3036 | 122.1878 | -0.15041 | 0.019335 | -122.1937 | 0.078864 | 0.092299 | 0.072964 | -122.1767 | -122.0809 | -0.049704 | -0.25884 | 0.18875 | 0.071829 | 0.12153 | 0.025769 | -0.090073 | 0.18488 | 0.2018 | 0.29762 | 0.12043 | -122.3592 | 122.1197 | 122.4043 | 122.2885 | 0.70088 | -122.4282
3527.0938 | 122.525 | -0.054932 | 122.2549 | -0.0025182 | -0.052461 | 0.039439 | 0.019469 | -0.01336 | -0.0035853 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.047311 | 0.04726 | -0.021844 | 0.019721 | -0.003831 | 0.079598 | 0.1011 | 0.20607 | -0.081373 | 0.088043 | 0.60475 | -0.033458 | 122.0098 | 122.299 | 122.1878 | -0.15499 | -0.026441 | -122.1753 | 0.033088 | 0.051101 | 0.077542 | -122.1538 | -122.0489 | -0.10006 | -0.24511 | 0.14297 | 0.021474 | 0.12153 | 0.044079 | -0.067185 | 0.13453 | 0.15603 | 0.261 | 0.074653 | -122.3363 | 122.0648 | 122.354 | 122.2427 | 0.65968 | -122.4099
3528.8594 | 122.4472 | -0.050354 | 122.2183 | -0.01778 | -0.052247 | 0.039439 | 0.019469 | -0.01336 | -0.0037989 | -0.021518 | -0.002694 | -0.0020767 | 0.057619 | 0.047525 | 0.047474 | -0.021844 | 0.019721 | -0.003831 | 0.084176 | 0.10567 | 0.20607 | -0.085952 | 0.092622 | 0.59559 | -0.028879 | 122.019 | 122.299 | 122.1878 | -0.15957 | -0.035598 | -122.1341 | 0.02851 | 0.046523 | 0.082121 | -122.1126 | -122.0123 | -0.10922 | -0.19933 | 0.14298 | 0.021475 | 0.13069 | 0.0807 | -0.030564 | 0.13453 | 0.15603 | 0.25642 | 0.070075 | -122.3043 | 122.0693 | 122.3494 | 122.2381 | 0.64594 | -122.3779
3530.625 | 122.4701 | -0.036621 | 122.2366 | -0.01778 | -0.052247 | 0.039439 | 0.019255 | -0.013574 | -0.0037989 | -0.013887 | -0.0024804 | -0.0022903 | 0.058046 | 0.047311 | 0.047687 | -0.012688 | 0.019721 | -0.008409 | 0.084176 | 0.10567 | 0.20149 | -0.085952 | 0.078886 | 0.60017 | -0.033458 | 122.0236 | 122.3036 | 122.1923 | -0.15041 | -0.049331 | -122.1525 | 0.023933 | 0.028212 | 0.077543 | -122.131 | -122.0351 | -0.11379 | -0.21306 | 0.11551 | 0.003163 | 0.11695 | 0.066968 | -0.044296 | 0.1208 | 0.1423 | 0.23811 | 0.056342 | -122.3226 | 122.0602 | 122.3402 | 122.229 | 0.63679 | -122.387
3532.3281 | 122.3465 | -0.10529 | 122.2687 | -0.010149 | -0.052461 | 0.039652 | 0.019682 | -0.01336 | -0.0035853 | -0.021518 | -0.002694 | -0.0022903 | 0.057619 | 0.047311 | 0.047046 | -0.017266 | 0.019721 | -0.008409 | 0.084176 | 0.096516 | 0.20607 | -0.085952 | 0.088043 | 0.60017 | -0.033458 | 122.019 | 122.299 | 122.1923 | -0.15499 | 0.019334 | -122.1845 | 0.08802 | 0.096877 | 0.077543 | -122.1722 | -122.0626 | -0.049705 | -0.24968 | 0.19333 | 0.071828 | 0.12153 | 0.030346 | -0.07634 | 0.18946 | 0.2018 | 0.31135 | 0.12501 | -122.3546 | 122.1243 | 122.4043 | 122.2976 | 0.70546 | -122.4237
3534.1406 | 122.4655 | -0.068665 | 122.2549 | -0.01778 | -0.052247 | 0.039652 | 0.019682 | -0.013574 | -0.0037989 | -0.013887 | -0.002694 | -0.0020767 | 0.057832 | 0.047311 | 0.047474 | -0.017266 | 0.019721 | -0.008409 | 0.084176 | 0.1011 | 0.20149 | -0.085952 | 0.083464 | 0.60475 | -0.0243 | 122.0098 | 122.3036 | 122.1878 | -0.15957 | -0.017287 | -122.1708 | 0.051399 | 0.060256 | 0.077543 | -122.1538 | -122.0535 | -0.090905 | -0.24511 | 0.15213 | 0.044365 | 0.13527 | 0.048657 | -0.067185 | 0.15284 | 0.16976 | 0.27015 | 0.088386 | -122.3409 | 122.0785 | 122.3723 | 122.2564 | 0.67341 | -122.4145
3535.8438 | 122.3373 | -0.09613 | 122.2549 | -0.010149 | -0.052034 | 0.039225 | 0.019469 | -0.013147 | -0.0037989 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.047098 | 0.047687 | -0.017266 | 0.019721 | -0.008409 | 0.079598 | 0.10567 | 0.20149 | -0.090531 | 0.088043 | 0.60933 | -0.0243 | 122.0144 | 122.299 | 122.2015 | -0.15499 | 0.005599 | -122.1753 | 0.078864 | 0.087721 | 0.082122 | -122.1493 | -122.0535 | -0.058861 | -0.24053 | 0.18417 | 0.07183 | 0.13069 | 0.044079 | -0.053449 | 0.17573 | 0.2018 | 0.29762 | 0.11585 | -122.3455 | 122.1105 | 122.3952 | 122.2976 | 0.70546 | -122.4099
3537.5781 | 122.4335 | -0.064087 | 122.2275 | -0.01778 | -0.052034 | 0.039652 | 0.019682 | -0.013147 | -0.0033715 | -0.021518 | -0.0029076 | -0.0020767 | 0.058046 | 0.047098 | 0.047474 | -0.021844 | 0.019721 | -0.008409 | 0.07502 | 0.1011 | 0.20149 | -0.085952 | 0.092622 | 0.60475 | -0.028879 | 122.0144 | 122.299 | 122.1832 | -0.15041 | -0.021865 | -122.1525 | 0.042243 | 0.055678 | 0.077543 | -122.1264 | -122.026 | -0.086325 | -0.21307 | 0.15671 | 0.035208 | 0.12153 | 0.071545 | -0.044298 | 0.13911 | 0.16518 | 0.26558 | 0.083808 | -122.3134 | 122.0785 | 122.3631 | 122.2473 | 0.66884 | -122.3779
3539.3594 | 122.4747 | -0.041199 | 122.2549 | -0.010149 | -0.052034 | 0.039866 | 0.019255 | -0.01336 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.047098 | 0.04726 | -0.012688 | 0.015142 | -0.003831 | 0.084176 | 0.10567 | 0.20607 | -0.081373 | 0.092622 | 0.60475 | -0.033458 | 122.0144 | 122.299 | 122.1923 | -0.15499 | -0.040174 | -122.1708 | 0.028511 | 0.037368 | 0.077542 | -122.1493 | -122.0489 | -0.11379 | -0.24053 | 0.13382 | 0.007741 | 0.12153 | 0.044079 | -0.062607 | 0.12538 | 0.14687 | 0.24727 | 0.056341 | -122.3363 | 122.0556 | 122.3402 | 122.2335 | 0.64595 | -122.4099
3541.0781 | 122.3511 | -0.11444 | 122.2641 | -0.010149 | -0.052034 | 0.039866 | 0.019469 | -0.01336 | -0.0037989 | -0.0062567 | -0.002694 | -0.0022903 | 0.057832 | 0.047311 | 0.047474 | -0.021844 | 0.019721 | -0.008409 | 0.084176 | 0.1011 | 0.20607 | -0.085952 | 0.092622 | 0.61391 | -0.0243 | 122.019 | 122.299 | 122.2015 | -0.15499 | 0.028489 | -122.1799 | 0.092597 | 0.10603 | 0.077543 | -122.163 | -122.058 | -0.04055 | -0.24511 | 0.20706 | 0.090141 | 0.13069 | 0.034924 | -0.062604 | 0.19862 | 0.21554 | 0.32051 | 0.13416 | -122.3501 | 122.1334 | 122.4135 | 122.3159 | 0.72835 | -122.4191
3542.8594 | 122.3969 | -0.064087 | 122.2229 | -0.01778 | -0.052461 | 0.039439 | 0.019041 | -0.01336 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.047098 | 0.047687 | -0.008109 | 0.015142 | -0.012988 | 0.079598 | 0.11025 | 0.20607 | -0.090531 | 0.092622 | 0.60475 | -0.0243 | 122.019 | 122.299 | 122.1832 | -0.15499 | -0.026444 | -122.1433 | 0.055978 | 0.051099 | 0.077543 | -122.1126 | -122.0168 | -0.090904 | -0.20391 | 0.15671 | 0.039787 | 0.13069 | 0.076123 | -0.03972 | 0.14369 | 0.17434 | 0.27015 | 0.079229 | -122.3134 | 122.0831 | 122.3631 | 122.2473 | 0.66884 | -122.3779
3544.6406 | 122.4838 | -0.064087 | 122.2458 | -0.01778 | -0.052247 | 0.039652 | 0.019682 | -0.013147 | -0.0035853 | -0.013887 | -0.0024804 | -0.0020767 | 0.057405 | 0.047098 | 0.047687 | -0.021844 | 0.0243 | -0.012988 | 0.088755 | 0.096516 | 0.20149 | -0.085952 | 0.092622 | 0.60475 | -0.028879 | 122.0236 | 122.2944 | 122.1923 | -0.15957 | -0.021865 | -122.157 | 0.042243 | 0.051099 | 0.072964 | -122.1493 | -122.0443 | -0.095483 | -0.22222 | 0.15671 | 0.035208 | 0.13069 | 0.048655 | -0.053452 | 0.15284 | 0.1606 | 0.26558 | 0.088387 | -122.3317 | 122.0877 | 122.3585 | 122.2564 | 0.66884 | -122.4054
3546.3281 | 122.493 | -0.054932 | 122.2366 | -0.01778 | -0.052034 | 0.039439 | 0.019255 | -0.012933 | -0.0035853 | -0.036779 | -0.0024804 | -0.0020767 | 0.057832 | 0.047098 | 0.047474 | -0.017266 | 0.019721 | -0.012988 | 0.084176 | 0.1011 | 0.20149 | -0.081373 | 0.083464 | 0.60933 | -0.028879 | 122.019 | 122.2944 | 122.1923 | -0.15499 | -0.026441 | -122.1525 | 0.037666 | 0.041944 | 0.068385 | -122.1355 | -122.0351 | -0.10006 | -0.21764 | 0.1384 | 0.026053 | 0.12611 | 0.057811 | -0.044296 | 0.13911 | 0.15603 | 0.25642 | 0.074653 | -122.318 | 122.0739 | 122.3494 | 122.2473 | 0.66426 | -122.3916
3548.0938 | 122.3373 | -0.091553 | 122.2824 | -0.010149 | -0.052461 | 0.039439 | 0.019469 | -0.01336 | -0.0035853 | -0.013887 | -0.0022666 | -0.0022903 | 0.057832 | 0.047311 | 0.047901 | -0.021844 | 0.028878 | -0.003831 | 0.084176 | 0.10567 | 0.20607 | -0.085952 | 0.088043 | 0.60475 | -0.0243 | 122.019 | 122.2944 | 122.1923 | -0.15499 | 0.005601 | -122.1982 | 0.069709 | 0.087722 | 0.082121 | -122.1767 | -122.0763 | -0.063438 | -0.26342 | 0.1796 | 0.067253 | 0.13069 | 0.012034 | -0.090073 | 0.17573 | 0.19723 | 0.29762 | 0.12043 | -122.3684 | 122.1105 | 122.386 | 122.2839 | 0.6963 | -122.4374
3549.8438 | 122.3923 | -0.11444 | 122.2824 | -0.0025182 | -0.052247 | 0.039439 | 0.019255 | -0.013147 | -0.0037989 | -0.0062567 | -0.002694 | -0.0022903 | 0.057619 | 0.047098 | 0.047474 | -0.021844 | 0.019721 | -0.008409 | 0.088755 | 0.1011 | 0.19691 | -0.085952 | 0.097201 | 0.60933 | -0.0243 | 122.0144 | 122.2944 | 122.1923 | -0.16415 | 0.028489 | -122.1937 | 0.092597 | 0.10603 | 0.077543 | -122.1813 | -122.0855 | -0.049708 | -0.268 | 0.21164 | 0.090141 | 0.13985 | 0.012034 | -0.090073 | 0.2032 | 0.21554 | 0.31135 | 0.13416 | -122.3684 | 122.1289 | 122.4089 | 122.3068 | 0.72377 | -122.4466
3551.5938 | 122.3648 | -0.10986 | 122.2641 | -0.010149 | -0.052034 | 0.039652 | 0.019682 | -0.013147 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.058046 | 0.047098 | 0.047474 | -0.021844 | 0.019721 | -0.003831 | 0.079598 | 0.10567 | 0.21064 | -0.090531 | 0.088043 | 0.60475 | -0.028879 | 122.0144 | 122.299 | 122.1923 | -0.15957 | 0.019332 | -122.1845 | 0.088019 | 0.10603 | 0.0867 | -122.1584 | -122.0535 | -0.049707 | -0.24969 | 0.19791 | 0.080984 | 0.13069 | 0.034924 | -0.071762 | 0.18946 | 0.21554 | 0.32051 | 0.12958 | -122.3546 | 122.1243 | 122.4089 | 122.3022 | 0.71461 | -122.4237
3553.2812 | 122.4701 | -0.050354 | 122.2458 | -0.01778 | -0.052247 | 0.039439 | 0.019469 | -0.013147 | -0.0040125 | -0.021518 | -0.002694 | -0.0022903 | 0.057832 | 0.047311 | 0.04726 | -0.017266 | 0.019721 | -0.008409 | 0.084176 | 0.1011 | 0.20149 | -0.081373 | 0.088043 | 0.61391 | -0.028879 | 122.0236 | 122.299 | 122.1969 | -0.15499 | -0.031019 | -122.1616 | 0.033088 | 0.041945 | 0.072964 | -122.1447 | -122.0443 | -0.10464 | -0.22222 | 0.1384 | 0.021475 | 0.12611 | 0.053234 | -0.048873 | 0.13453 | 0.15145 | 0.25184 | 0.070075 | -122.3272 | 122.0739 | 122.3494 | 122.2473 | 0.66426 | -122.4008
3555.0469 | 122.4335 | -0.059509 | 122.2412 | -0.01778 | -0.052247 | 0.039225 | 0.019682 | -0.01336 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057832 | 0.047311 | 0.047474 | -0.017266 | 0.019721 | -0.003831 | 0.088755 | 0.10567 | 0.20149 | -0.085952 | 0.078886 | 0.61391 | -0.033458 | 122.0144 | 122.2944 | 122.1878 | -0.15957 | -0.026443 | -122.1525 | 0.042243 | 0.055678 | 0.082121 | -122.1355 | -122.0397 | -0.10006 | -0.2268 | 0.13839 | 0.026051 | 0.12611 | 0.053233 | -0.053452 | 0.14826 | 0.16518 | 0.261 | 0.07923 | -122.3272 | 122.0739 | 122.354 | 122.2473 | 0.67341 | -122.4008
3556.75 | 122.3923 | -0.09613 | 122.2504 | -0.0025182 | -0.052675 | 0.039225 | 0.019041 | -0.012933 | -0.0037989 | -0.0062567 | -0.002694 | -0.0020767 | 0.057832 | 0.047098 | 0.04726 | -0.012688 | 0.0243 | -0.008409 | 0.084176 | 0.096516 | 0.20607 | -0.085952 | 0.092622 | 0.61391 | -0.0243 | 122.0144 | 122.2899 | 122.1969 | -0.15499 | 0.010178 | -122.1662 | 0.083442 | 0.087721 | 0.077543 | -122.1539 | -122.0443 | -0.058861 | -0.23595 | 0.18875 | 0.07183 | 0.13069 | 0.039499 | -0.05345 | 0.18031 | 0.19265 | 0.3022 | 0.12043 | -122.3363 | 122.1105 | 122.386 | 122.293 | 0.71004 | -122.4054
3558.5156 | 122.4701 | -0.050354 | 122.2321 | -0.025411 | -0.052461 | 0.039225 | 0.019682 | -0.013788 | -0.0037989 | -0.013887 | -0.002053 | -0.0022903 | 0.057832 | 0.047098 | 0.047474 | -0.012688 | 0.028878 | -0.003831 | 0.088755 | 0.1011 | 0.20149 | -0.081373 | 0.088043 | 0.61391 | -0.0243 | 122.019 | 122.299 | 122.2015 | -0.16415 | -0.031019 | -122.1433 | 0.037666 | 0.046523 | 0.077542 | -122.131 | -122.0306 | -0.11379 | -0.21306 | 0.1384 | 0.026054 | 0.13985 | 0.066967 | -0.030561 | 0.13911 | 0.15145 | 0.25184 | 0.079232 | -122.3134 | 122.0693 | 122.3494 | 122.2518 | 0.66426 | -122.3962
3560.2656 | 122.4289 | -0.07782 | 122.2321 | -0.010149 | -0.052247 | 0.039652 | 0.019255 | -0.013147 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.058046 | 0.047098 | 0.04726 | -0.012688 | 0.028878 | -0.008409 | 0.079598 | 0.1011 | 0.20149 | -0.085952 | 0.088043 | 0.61848 | -0.0243 | 122.0236 | 122.3036 | 122.1878 | -0.15957 | -0.008132 | -122.1525 | 0.065132 | 0.069411 | 0.077543 | -122.131 | -122.0306 | -0.08175 | -0.20849 | 0.16586 | 0.05352 | 0.13527 | 0.071545 | -0.044297 | 0.15742 | 0.17891 | 0.27931 | 0.1067 | -122.318 | 122.1014 | 122.3814 | 122.2656 | 0.6963 | -122.3916
3562.0156 | 122.4152 | -0.07782 | 122.2412 | -0.01778 | -0.052461 | 0.039439 | 0.019469 | -0.013147 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057832 | 0.047098 | 0.04726 | -0.017266 | 0.019721 | 0.000747 | 0.088755 | 0.10567 | 0.20607 | -0.076794 | 0.088043 | 0.60475 | -0.0243 | 122.019 | 122.299 | 122.1969 | -0.15041 | 0.001026 | -122.1525 | 0.060554 | 0.078567 | 0.077541 | -122.1355 | -122.0351 | -0.072592 | -0.22222 | 0.16586 | 0.05352 | 0.12611 | 0.057812 | -0.044295 | 0.16658 | 0.18349 | 0.28389 | 0.097541 | -122.318 | 122.0968 | 122.3768 | 122.2747 | 0.68257 | -122.3916
3563.7812 | 122.3373 | -0.11902 | 122.2778 | -0.01778 | -0.052034 | 0.039439 | 0.019469 | -0.013147 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.057405 | 0.047311 | 0.047901 | -0.012688 | 0.019721 | -0.008409 | 0.084176 | 0.1011 | 0.20607 | -0.072215 | 0.083464 | 0.61391 | -0.033458 | 122.019 | 122.299 | 122.1878 | -0.15957 | 0.046804 | -122.1937 | 0.10633 | 0.11061 | 0.063806 | -122.1767 | -122.0718 | -0.040551 | -0.25884 | 0.20248 | 0.085561 | 0.12611 | 0.021191 | -0.090073 | 0.2032 | 0.22011 | 0.32509 | 0.13874 | -122.35 | 122.138 | 122.418 | 122.3068 | 0.73292 | -122.4374
3565.4844 | 122.3877 | -0.086975 | 122.2549 | 0.0051128 | -0.052247 | 0.039439 | 0.019255 | -0.013147 | -0.0037989 | -0.029148 | -0.0024804 | -0.0025041 | 0.057619 | 0.047311 | 0.04726 | -0.008109 | 0.0243 | -0.008409 | 0.084176 | 0.1011 | 0.21064 | -0.085952 | 0.088043 | 0.61391 | -0.033458 | 122.019 | 122.3036 | 122.1878 | -0.16415 | 0.001023 | -122.1708 | 0.078866 | 0.078566 | 0.077543 | -122.1538 | -122.0443 | -0.077174 | -0.23595 | 0.17502 | 0.053517 | 0.13069 | 0.048657 | -0.067185 | 0.17115 | 0.18807 | 0.29762 | 0.11127 | -122.3409 | 122.106 | 122.3906 | 122.2747 | 0.70088 | -122.4191
3567.25 | 122.4335 | -0.054932 | 122.2183 | -0.01778 | -0.052247 | 0.039439 | 0.019255 | -0.013147 | -0.0040125 | -0.029148 | -0.0024804 | -0.0022903 | 0.057832 | 0.046884 | 0.04726 | -0.017266 | 0.0243 | -0.008409 | 0.084176 | 0.096516 | 0.21064 | -0.085952 | 0.088043 | 0.61391 | -0.038036 | 122.0144 | 122.299 | 122.1923 | -0.15957 | -0.03102 | -122.1341 | 0.037666 | 0.046523 | 0.077543 | -122.1218 | -122.0077 | -0.10464 | -0.20391 | 0.14297 | 0.016896 | 0.12153 | 0.0807 | -0.025986 | 0.13911 | 0.15145 | 0.26558 | 0.079232 | -122.3043 | 122.0693 | 122.354 | 122.2473 | 0.66884 | -122.3779
3569 | 122.4426 | -0.050354 | 122.2595 | -0.010149 | -0.052461 | 0.039652 | 0.019255 | -0.013574 | -0.0037989 | -0.021518 | -0.0024804 | -0.0025041 | 0.057619 | 0.047311 | 0.047474 | -0.021844 | 0.0243 | -0.003831 | 0.079598 | 0.096516 | 0.21064 | -0.081373 | 0.088043 | 0.61391 | -0.033458 | 122.0144 | 122.299 | 122.1923 | -0.15041 | -0.031019 | -122.1799 | 0.02851 | 0.046523 | 0.077542 | -122.163 | -122.0489 | -0.10006 | -0.24511 | 0.1384 | 0.016896 | 0.11695 | 0.039502 | -0.067184 | 0.12995 | 0.14687 | 0.261 | 0.074654 | -122.3409 | 122.0648 | 122.3494 | 122.2427 | 0.66426 | -122.4099
3570.7031 | 122.3328 | -0.091553 | 122.2595 | -0.0025182 | -0.052461 | 0.039439 | 0.019255 | -0.01336 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.047311 | 0.047687 | -0.021844 | 0.028878 | 0.000747 | 0.084176 | 0.096516 | 0.20149 | -0.090531 | 0.088043 | 0.61848 | -0.019721 | 122.0144 | 122.3082 | 122.1969 | -0.15499 | 0.001022 | -122.1753 | 0.069709 | 0.0923 | 0.091278 | -122.163 | -122.058 | -0.063438 | -0.24511 | 0.1796 | 0.071832 | 0.13527 | 0.048659 | -0.062605 | 0.17573 | 0.18807 | 0.29304 | 0.12043 | -122.3501 | 122.106 | 122.3997 | 122.2885 | 0.71004 | -122.4145
3572.4688 | 122.4609 | -0.059509 | 122.2458 | -0.010149 | -0.052461 | 0.039225 | 0.019255 | -0.013147 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.047311 | 0.04726 | -0.012688 | 0.0243 | -0.008409 | 0.084176 | 0.10567 | 0.19691 | -0.085952 | 0.097201 | 0.61848 | -0.0243 | 122.019 | 122.2944 | 122.1923 | -0.15957 | -0.026443 | -122.1616 | 0.046821 | 0.0511 | 0.077543 | -122.1401 | -122.0489 | -0.10006 | -0.2268 | 0.15671 | 0.035209 | 0.13527 | 0.048655 | -0.053452 | 0.14369 | 0.16518 | 0.25642 | 0.083809 | -122.3317 | 122.0785 | 122.354 | 122.2518 | 0.67799 | -122.4054
3574.1719 | 122.4701 | -0.041199 | 122.2458 | -0.01778 | -0.052461 | 0.039652 | 0.019469 | -0.01336 | -0.0040125 | -0.013887 | -0.002694 | -0.0022903 | 0.058046 | 0.047311 | 0.04726 | -0.008109 | 0.0243 | -0.008409 | 0.088755 | 0.10567 | 0.20607 | -0.085952 | 0.088043 | 0.61848 | -0.028879 | 122.0236 | 122.3036 | 122.1923 | -0.15041 | -0.044753 | -122.157 | 0.03309 | 0.03279 | 0.077543 | -122.1401 | -122.0397 | -0.10921 | -0.22222 | 0.12924 | 0.01232 | 0.12153 | 0.057812 | -0.053452 | 0.12995 | 0.14687 | 0.24727 | 0.065499 | -122.3317 | 122.0648 | 122.3448 | 122.2335 | 0.65968 | -122.3962
3575.9375 | 122.4701 | -0.036621 | 122.2778 | -0.010149 | -0.052247 | 0.039011 | 0.019469 | -0.013574 | -0.0037989 | -0.021518 | -0.002694 | -0.0020767 | 0.057832 | 0.047311 | 0.047474 | -0.012688 | 0.019721 | -0.003831 | 0.079598 | 0.10567 | 0.21064 | -0.090531 | 0.088043 | 0.61848 | -0.038036 | 122.0281 | 122.299 | 122.1923 | -0.15499 | -0.05391 | -122.1982 | 0.023933 | 0.03279 | 0.0867 | -122.1722 | -122.0672 | -0.11837 | -0.24968 | 0.12466 | -0.001415 | 0.11695 | 0.021191 | -0.085495 | 0.11622 | 0.1423 | 0.24727 | 0.056342 | -122.3684 | 122.0648 | 122.3356 | 122.229 | 0.65511 | -122.4328
3577.625 | 122.3328 | -0.091553 | 122.287 | -0.010149 | -0.052461 | 0.039439 | 0.019255 | -0.013147 | -0.0042263 | -0.021518 | -0.002694 | -0.0020767 | 0.058046 | 0.047098 | 0.047687 | -0.012688 | 0.028878 | -0.003831 | 0.088755 | 0.1011 | 0.20149 | -0.090531 | 0.088043 | 0.61848 | -0.033458 | 122.019 | 122.3082 | 122.1923 | -0.15499 | 0.001022 | -122.1982 | 0.078865 | 0.087722 | 0.0867 | -122.1859 | -122.0855 | -0.063438 | -0.26799 | 0.1796 | 0.058095 | 0.12153 | 0.021193 | -0.09465 | 0.18031 | 0.19265 | 0.29304 | 0.12043 | -122.3775 | 122.1105 | 122.3997 | 122.2839 | 0.71004 | -122.442
3579.375 | 122.3602 | -0.086975 | 122.2458 | -0.0025182 | -0.052461 | 0.039225 | 0.019255 | -0.01336 | -0.0037989 | -0.013887 | -0.0024804 | -0.0018631 | 0.057619 | 0.047525 | 0.047687 | -0.017266 | 0.0243 | -0.003831 | 0.079598 | 0.10567 | 0.21064 | -0.085952 | 0.088043 | 0.62306 | -0.033458 | 122.0236 | 122.299 | 122.1786 | -0.15499 | 0.001023 | -122.1662 | 0.069709 | 0.083144 | 0.082121 | -122.1401 | -122.0351 | -0.068016 | -0.22222 | 0.17502 | 0.053517 | 0.12153 | 0.053234 | -0.067187 | 0.16657 | 0.19265 | 0.29762 | 0.11127 | -122.3317 | 122.1105 | 122.386 | 122.2656 | 0.71004 | -122.4008
3581.1406 | 122.4289 | -0.068665 | 122.2549 | -0.010149 | -0.052675 | 0.039652 | 0.019041 | -0.013574 | -0.0042263 | -0.021518 | -0.002694 | -0.0020767 | 0.057619 | 0.047311 | 0.047687 | -0.012688 | 0.0243 | -0.008409 | 0.079598 | 0.1011 | 0.20149 | -0.081373 | 0.083464 | 0.61848 | -0.033458 | 122.019 | 122.2944 | 122.1923 | -0.15499 | -0.012708 | -122.1753 | 0.055977 | 0.060256 | 0.072964 | -122.1538 | -122.0535 | -0.086326 | -0.23595 | 0.15213 | 0.035207 | 0.12153 | 0.0395 | -0.062607 | 0.14826 | 0.16976 | 0.27015 | 0.092965 | -122.3363 | 122.0877 | 122.3631 | 122.261 | 0.68715 | -122.4099
3582.8594 | 122.3557 | -0.10071 | 122.2824 | -0.0025182 | -0.052461 | 0.039652 | 0.019682 | -0.013574 | -0.0040125 | -0.021518 | -0.002694 | -0.0022903 | 0.058046 | 0.047525 | 0.04726 | -0.012688 | 0.0243 | -0.008409 | 0.079598 | 0.10567 | 0.20607 | -0.085952 | 0.088043 | 0.62764 | -0.038036 | 122.019 | 122.299 | 122.1969 | -0.15499 | 0.014756 | -122.2028 | 0.08802 | 0.092299 | 0.077543 | -122.1767 | -122.0763 | -0.054283 | -0.26342 | 0.18875 | 0.062672 | 0.11695 | 0.016613 | -0.085494 | 0.18031 | 0.20638 | 0.30677 | 0.12501 | -122.3684 | 122.1197 | 122.3997 | 122.2976 | 0.72835 | -122.4374
3584.6406 | 122.4472 | -0.050354 | 122.2275 | -0.025411 | -0.052247 | 0.039225 | 0.019255 | -0.01336 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.057619 | 0.047098 | 0.04726 | -0.017266 | 0.019721 | -0.003831 | 0.084176 | 0.1011 | 0.21064 | -0.090531 | 0.088043 | 0.61391 | -0.033458 | 122.0144 | 122.2944 | 122.1832 | -0.15957 | -0.040177 | -122.1433 | 0.033088 | 0.046523 | 0.0867 | -122.1264 | -122.0168 | -0.10922 | -0.21307 | 0.1384 | 0.016896 | 0.12611 | 0.066966 | -0.044298 | 0.13453 | 0.15145 | 0.261 | 0.070075 | -122.318 | 122.0648 | 122.3448 | 122.2335 | 0.66426 | -122.387
3586.3906 | 122.3465 | -0.09613 | 122.2778 | -0.010149 | -0.052461 | 0.039225 | 0.019255 | -0.013574 | -0.0037989 | -0.029148 | -0.0024804 | -0.0025041 | 0.057619 | 0.047311 | 0.047474 | -0.021844 | 0.0243 | -0.003831 | 0.084176 | 0.1011 | 0.20149 | -0.085952 | 0.083464 | 0.62306 | -0.028879 | 122.019 | 122.2899 | 122.1923 | -0.14583 | 0.010178 | -122.1937 | 0.074286 | 0.092299 | 0.082121 | -122.1767 | -122.0763 | -0.049703 | -0.25884 | 0.17959 | 0.067251 | 0.11695 | 0.012033 | -0.085495 | 0.18031 | 0.19722 | 0.29762 | 0.12043 | -122.3638 | 122.1151 | 122.386 | 122.2885 | 0.71919 | -122.4237
3588.1562 | 122.4884 | -0.064087 | 122.2321 | -0.0025182 | -0.052461 | 0.039439 | 0.019255 | -0.013574 | -0.0040125 | -0.021518 | -0.002694 | -0.0022903 | 0.057832 | 0.047525 | 0.047687 | -0.017266 | 0.019721 | -0.012988 | 0.088755 | 0.10567 | 0.21064 | -0.081373 | 0.092622 | 0.61848 | -0.033458 | 122.0236 | 122.299 | 122.1969 | -0.15499 | -0.017286 | -122.1433 | 0.046821 | 0.051099 | 0.068385 | -122.1264 | -122.0214 | -0.090904 | -0.20849 | 0.15671 | 0.030629 | 0.12153 | 0.066967 | -0.03514 | 0.15284 | 0.16976 | 0.27473 | 0.083808 | -122.3134 | 122.0877 | 122.3631 | 122.261 | 0.68257 | -122.387
3589.8594 | 122.3328 | -0.10071 | 122.2733 | -0.010149 | -0.052461 | 0.039011 | 0.019255 | -0.01336 | -0.0035853 | -0.021518 | -0.0022666 | -0.0020767 | 0.057832 | 0.047311 | 0.04726 | -0.017266 | 0.019721 | 0.000747 | 0.079598 | 0.11025 | 0.20149 | -0.085952 | 0.092622 | 0.62764 | -0.028879 | 122.0281 | 122.2944 | 122.1878 | -0.15499 | 0.014756 | -122.1937 | 0.083442 | 0.10146 | 0.086699 | -122.163 | -122.0718 | -0.054283 | -0.2451 | 0.19333 | 0.071829 | 0.12611 | 0.02119 | -0.085495 | 0.18031 | 0.21096 | 0.3022 | 0.12043 | -122.3592 | 122.1289 | 122.3952 | 122.2885 | 0.72835 | -122.4282
3591.6094 | 122.3877 | -0.068665 | 122.2641 | -0.010149 | -0.052675 | 0.039652 | 0.019255 | -0.013147 | -0.0037989 | -0.013887 | -0.0022666 | -0.0025041 | 0.057832 | 0.047525 | 0.04726 | -0.008109 | 0.028878 | -0.003831 | 0.084176 | 0.10567 | 0.20607 | -0.090531 | 0.092622 | 0.62306 | -0.028879 | 122.019 | 122.3036 | 122.1878 | -0.15499 | -0.021866 | -122.1799 | 0.060556 | 0.064834 | 0.0867 | -122.1584 | -122.058 | -0.086326 | -0.24511 | 0.16129 | 0.039786 | 0.12611 | 0.039502 | -0.07634 | 0.15284 | 0.17434 | 0.27473 | 0.097543 | -122.3546 | 122.0877 | 122.3723 | 122.2564 | 0.69173 | -122.4191
3593.375 | 122.3831 | -0.082397 | 122.2595 | -0.0025182 | -0.052675 | 0.039225 | 0.019041 | -0.01336 | -0.0037989 | -0.013887 | -0.002694 | -0.0020767 | 0.057619 | 0.047525 | 0.047474 | -0.021844 | 0.0243 | -0.003831 | 0.093333 | 0.10567 | 0.21064 | -0.09511 | 0.088043 | 0.62764 | -0.033458 | 122.019 | 122.3036 | 122.2061 | -0.15041 | -0.012713 | -122.1662 | 0.060553 | 0.078566 | 0.091279 | -122.1538 | -122.0489 | -0.068015 | -0.24053 | 0.17044 | 0.048939 | 0.11695 | 0.04408 | -0.053448 | 0.17573 | 0.18807 | 0.29304 | 0.1067 | -122.3546 | 122.1014 | 122.386 | 122.2885 | 0.71004 | -122.4099
3595.1406 | 122.4243 | -0.054932 | 122.2321 | -0.010149 | -0.052461 | 0.039439 | 0.019469 | -0.01336 | -0.0035853 | -0.013887 | -0.002053 | -0.0025041 | 0.057405 | 0.047739 | 0.04726 | -0.021844 | 0.019721 | 0.000747 | 0.088755 | 0.11025 | 0.20607 | -0.081373 | 0.083464 | 0.62306 | -0.033458 | 122.0281 | 122.2944 | 122.1923 | -0.15957 | -0.026441 | -122.1433 | 0.033088 | 0.055679 | 0.08212 | -122.1218 | -122.026 | -0.10464 | -0.20391 | 0.1384 | 0.021474 | 0.12611 | 0.062388 | -0.039719 | 0.14369 | 0.16518 | 0.261 | 0.074653 | -122.3134 | 122.0831 | 122.3494 | 122.2473 | 0.678 | -122.3916
3596.9062 | 122.3373 | -0.10529 | 122.2733 | -0.0025182 | -0.052675 | 0.039652 | 0.018828 | -0.01336 | -0.0035853 | -0.013887 | -0.0022666 | -0.0022903 | 0.057619 | 0.047311 | 0.04726 | -0.012688 | 0.028878 | -0.003831 | 0.084176 | 0.1011 | 0.20607 | -0.085952 | 0.088043 | 0.62306 | -0.033458 | 122.0236 | 122.3082 | 122.1923 | -0.15499 | 0.019334 | -122.1891 | 0.092598 | 0.10146 | 0.082121 | -122.1722 | -122.0672 | -0.049705 | -0.24968 | 0.19333 | 0.071828 | 0.12153 | 0.034926 | -0.080917 | 0.18946 | 0.20638 | 0.31135 | 0.13416 | -122.3592 | 122.1289 | 122.4135 | 122.2976 | 0.72835 | -122.4282
3598.6094 | 122.4976 | -0.054932 | 122.2458 | -0.010149 | -0.052675 | 0.039866 | 0.019469 | -0.013147 | -0.0037989 | -0.013887 | -0.0024804 | -0.0018631 | 0.057832 | 0.047311 | 0.04726 | -0.008109 | 0.0243 | 0.005325 | 0.088755 | 0.1011 | 0.20607 | -0.085952 | 0.083464 | 0.62764 | -0.038036 | 122.019 | 122.3036 | 122.2015 | -0.15957 | -0.03102 | -122.157 | 0.046823 | 0.060257 | 0.091277 | -122.1447 | -122.0397 | -0.10464 | -0.2268 | 0.1384 | 0.016896 | 0.12153 | 0.057812 | -0.044294 | 0.14369 | 0.15603 | 0.261 | 0.079232 | -122.3317 | 122.0739 | 122.3585 | 122.2564 | 0.68257 | -122.4054
3600.3594 | 122.3511 | -0.07782 | 122.2778 | -0.010149 | -0.052461 | 0.039439 | 0.019255 | -0.013574 | -0.0037989 | -0.013887 | -0.002053 | -0.0020767 | 0.057619 | 0.047525 | 0.047687 | -0.012688 | 0.0243 | -0.012988 | 0.084176 | 0.10567 | 0.20607 | -0.085952 | 0.092622 | 0.62306 | -0.038036 | 122.019 | 122.2944 | 122.1878 | -0.15041 | -0.008132 | -122.1937 | 0.065132 | 0.064832 | 0.072964 | -122.1722 | -122.0718 | -0.072592 | -0.25884 | 0.17044 | 0.039784 | 0.11238 | 0.016612 | -0.090073 | 0.162 | 0.18349 | 0.28389 | 0.10212 | -122.3638 | 122.0968 | 122.3723 | 122.2656 | 0.70088 | -122.4282
3602.125 | 122.3877 | -0.09613 | 122.287 | -0.010149 | -0.052675 | 0.039439 | 0.019682 | -0.013574 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.057832 | 0.047311 | 0.04726 | -0.017266 | 0.0243 | 0.000747 | 0.088755 | 0.10567 | 0.21064 | -0.076794 | 0.092622 | 0.6368 | -0.028879 | 122.019 | 122.299 | 122.1832 | -0.15957 | 0.019336 | -122.1982 | 0.078864 | 0.096877 | 0.077541 | -122.1813 | -122.0763 | -0.06344 | -0.26799 | 0.18875 | 0.067251 | 0.13069 | 0.012036 | -0.10381 | 0.18488 | 0.2018 | 0.30678 | 0.12043 | -122.3638 | 122.1151 | 122.3952 | 122.2793 | 0.73293 | -122.4466
3603.8906 | 122.4976 | -0.064087 | 122.2366 | -0.010149 | -0.052675 | 0.039439 | 0.019041 | -0.01336 | -0.0035853 | -0.013887 | -0.002694 | -0.0022903 | 0.058046 | 0.047525 | 0.047474 | -0.021844 | 0.015142 | -0.008409 | 0.088755 | 0.1011 | 0.20607 | -0.081373 | 0.083464 | 0.62306 | -0.028879 | 122.0144 | 122.2899 | 122.1923 | -0.16415 | -0.017286 | -122.1479 | 0.042243 | 0.055678 | 0.072964 | -122.1355 | -122.0306 | -0.10006 | -0.22222 | 0.14755 | 0.035208 | 0.13527 | 0.053232 | -0.044296 | 0.15284 | 0.16518 | 0.27015 | 0.079229 | -122.318 | 122.0785 | 122.354 | 122.2564 | 0.68715 | -122.4008
3605.6406 | 122.4792 | -0.059509 | 122.2595 | -0.0025182 | -0.052461 | 0.039652 | 0.019255 | -0.013147 | -0.0037989 | -0.0062567 | -0.0024804 | -0.0020767 | 0.057405 | 0.047525 | 0.047046 | -0.012688 | 0.028878 | 0.000747 | 0.084176 | 0.10567 | 0.20149 | -0.085952 | 0.083464 | 0.62306 | -0.028879 | 122.019 | 122.299 | 122.1923 | -0.15041 | -0.026443 | -122.1753 | 0.046821 | 0.060256 | 0.086699 | -122.1538 | -122.058 | -0.090903 | -0.24053 | 0.14297 | 0.03063 | 0.12153 | 0.039502 | -0.067184 | 0.14369 | 0.16518 | 0.261 | 0.088387 | -122.3455 | 122.0785 | 122.3585 | 122.2518 | 0.68257 | -122.4099
3607.4062 | 122.3465 | -0.10986 | 122.287 | -0.01778 | -0.052675 | 0.039439 | 0.019469 | -0.01336 | -0.0042263 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.047311 | 0.04726 | -0.008109 | 0.028878 | -0.008409 | 0.088755 | 0.11025 | 0.20607 | -0.090531 | 0.088043 | 0.63222 | -0.033458 | 122.019 | 122.3036 | 122.1878 | -0.16415 | 0.019332 | -122.1982 | 0.10175 | 0.10145 | 0.082122 | -122.1767 | -122.0809 | -0.054286 | -0.26799 | 0.19791 | 0.076405 | 0.13069 | 0.016614 | -0.099228 | 0.19862 | 0.22012 | 0.31593 | 0.13874 | -122.3775 | 122.1289 | 122.4135 | 122.2976 | 0.74208 | -122.4511
3609.1094 | 122.4335 | -0.050354 | 122.2412 | -0.01778 | -0.052461 | 0.039439 | 0.019255 | -0.013147 | -0.0042263 | -0.013887 | -0.0024804 | -0.0025041 | 0.057832 | 0.047739 | 0.04726 | -0.017266 | 0.0243 | -0.008409 | 0.084176 | 0.1011 | 0.20607 | -0.081373 | 0.092622 | 0.62764 | -0.028879 | 122.019 | 122.3036 | 122.1969 | -0.15041 | -0.031019 | -122.157 | 0.033088 | 0.041945 | 0.072964 | -122.1401 | -122.0351 | -0.10006 | -0.22222 | 0.14298 | 0.021475 | 0.12153 | 0.06239 | -0.044295 | 0.13453 | 0.15145 | 0.25642 | 0.074654 | -122.3226 | 122.0693 | 122.354 | 122.2473 | 0.678 | -122.3916
3610.8594 | 122.4792 | -0.050354 | 122.2549 | -0.01778 | -0.052675 | 0.039439 | 0.018828 | -0.013574 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.047525 | 0.047474 | -0.017266 | 0.0243 | -0.008409 | 0.084176 | 0.1011 | 0.20607 | -0.090531 | 0.083464 | 0.6368 | -0.042615 | 122.019 | 122.3036 | 122.1969 | -0.15499 | -0.040177 | -122.1708 | 0.033088 | 0.041945 | 0.082122 | -122.1538 | -122.0489 | -0.10464 | -0.23595 | 0.13382 | 0.007739 | 0.11238 | 0.048657 | -0.058028 | 0.13453 | 0.15145 | 0.25642 | 0.074654 | -122.3455 | 122.0693 | 122.354 | 122.2473 | 0.68715 | -122.4099
3612.6094 | 122.3923 | -0.11444 | 122.2504 | -0.01778 | -0.052675 | 0.039652 | 0.019255 | -0.013147 | -0.0037989 | -0.013887 | -0.0022666 | -0.0018631 | 0.057619 | 0.047952 | 0.047474 | -0.012688 | 0.028878 | 0.000747 | 0.088755 | 0.10567 | 0.20607 | -0.085952 | 0.088043 | 0.62764 | -0.033458 | 122.0144 | 122.299 | 122.1923 | -0.15957 | 0.028489 | -122.1616 | 0.10175 | 0.11519 | 0.086699 | -122.1447 | -122.0443 | -0.045129 | -0.23595 | 0.20248 | 0.080983 | 0.12611 | 0.048657 | -0.058029 | 0.2032 | 0.22012 | 0.32051 | 0.14332 | -122.3363 | 122.1289 | 122.4135 | 122.3068 | 0.74208 | -122.4099
3614.3125 | 122.4701 | -0.045776 | 122.2412 | -0.010149 | -0.052461 | 0.039652 | 0.019255 | -0.013574 | -0.0035853 | -0.029148 | -0.0022666 | -0.0027177 | 0.057619 | 0.047739 | 0.047046 | -0.021844 | 0.028878 | -0.003831 | 0.093333 | 0.1011 | 0.19691 | -0.081373 | 0.092622 | 0.63222 | -0.028879 | 122.0144 | 122.2944 | 122.2015 | -0.15499 | -0.035597 | -122.1479 | 0.023932 | 0.041945 | 0.077542 | -122.1401 | -122.0443 | -0.10921 | -0.2268 | 0.1384 | 0.016897 | 0.12611 | 0.053233 | -0.039716 | 0.13911 | 0.14687 | 0.24268 | 0.074654 | -122.3226 | 122.0602 | 122.3402 | 122.2473 | 0.678 | -122.3962
3616.0781 | 122.3877 | -0.086975 | 122.2687 | -0.010149 | -0.052461 | 0.039652 | 0.018828 | -0.013574 | -0.0040125 | -0.013887 | -0.0024804 | -0.0025041 | 0.058046 | 0.047311 | 0.047046 | -0.012688 | 0.019721 | -0.008409 | 0.097912 | 0.1011 | 0.21064 | -0.09511 | 0.088043 | 0.62764 | -0.028879 | 122.0236 | 122.2944 | 122.2015 | -0.16873 | -0.008135 | -122.1708 | 0.074287 | 0.078566 | 0.086701 | -122.1676 | -122.058 | -0.081753 | -0.24511 | 0.17502 | 0.058096 | 0.13985 | 0.025767 | -0.067182 | 0.18489 | 0.18807 | 0.29762 | 0.1067 | -122.3638 | 122.1105 | 122.3814 | 122.2885 | 0.71462 | -122.4374
3617.8281 | 122.3969 | -0.068665 | 122.2458 | 0.0051128 | -0.052247 | 0.039225 | 0.019255 | -0.013147 | -0.0037989 | -0.029148 | -0.002694 | -0.0022903 | 0.057832 | 0.047739 | 0.047474 | -0.021844 | 0.028878 | 0.000747 | 0.088755 | 0.10567 | 0.21064 | -0.085952 | 0.092622 | 0.62764 | -0.028879 | 122.0236 | 122.2944 | 122.1969 | -0.15957 | -0.017287 | -122.157 | 0.046821 | 0.069412 | 0.086699 | -122.1401 | -122.0351 | -0.090905 | -0.22222 | 0.16129 | 0.039786 | 0.13069 | 0.048655 | -0.048873 | 0.15742 | 0.17434 | 0.27931 | 0.097543 | -122.3317 | 122.0922 | 122.3631 | 122.2656 | 0.69631 | -122.4054
3619.5938 | 122.4609 | -0.041199 | 122.2412 | -0.010149 | -0.052461 | 0.039011 | 0.019041 | -0.01336 | -0.0037989 | -0.029148 | -0.0022666 | -0.0020767 | 0.057832 | 0.047525 | 0.047046 | -0.012688 | 0.0243 | -0.003831 | 0.084176 | 0.1011 | 0.20607 | -0.090531 | 0.083464 | 0.6368 | -0.0243 | 122.019 | 122.2944 | 122.1969 | -0.15499 | -0.049332 | -122.157 | 0.028511 | 0.037368 | 0.0867 | -122.1401 | -122.0351 | -0.11379 | -0.22222 | 0.12466 | 0.016899 | 0.13069 | 0.053233 | -0.044295 | 0.12538 | 0.14229 | 0.24727 | 0.065499 | -122.3317 | 122.0602 | 122.3356 | 122.2381 | 0.678 | -122.3962
3621.3594 | 122.4335 | -0.059509 | 122.2412 | -0.01778 | -0.052461 | 0.039225 | 0.019041 | -0.01336 | -0.0037989 | -0.013887 | -0.0022666 | -0.0020767 | 0.058046 | 0.047525 | 0.04726 | -0.017266 | 0.019721 | 0.000747 | 0.07502 | 0.10567 | 0.20149 | -0.081373 | 0.088043 | 0.64138 | -0.028879 | 122.019 | 122.299 | 122.1878 | -0.15957 | -0.021864 | -122.1662 | 0.042243 | 0.060256 | 0.08212 | -122.1355 | -122.0397 | -0.10006 | -0.22222 | 0.14755 | 0.03063 | 0.13069 | 0.057812 | -0.053452 | 0.13453 | 0.16518 | 0.261 | 0.07923 | -122.3226 | 122.0785 | 122.3585 | 122.2473 | 0.70089 | -122.4008
3623.125 | 122.3511 | -0.086975 | 122.2916 | -0.010149 | -0.052675 | 0.039225 | 0.018828 | -0.013147 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.057832 | 0.047525 | 0.04726 | -0.021844 | 0.0243 | 0.000747 | 0.084176 | 0.096516 | 0.20607 | -0.081373 | 0.088043 | 0.6368 | -0.028879 | 122.019 | 122.299 | 122.1923 | -0.15499 | 0.005602 | -122.2074 | 0.065131 | 0.087722 | 0.08212 | -122.195 | -122.0855 | -0.068016 | -0.27257 | 0.17502 | 0.058096 | 0.12611 | 0.007458 | -0.099228 | 0.17115 | 0.18349 | 0.29304 | 0.11127 | -122.3729 | 122.106 | 122.386 | 122.2793 | 0.72378 | -122.4466
3624.8281 | 122.4197 | -0.050354 | 122.2641 | 0.0051128 | -0.052247 | 0.039439 | 0.019255 | -0.013147 | -0.0037989 | -0.021518 | -0.0022666 | -0.0022903 | 0.057832 | 0.047952 | 0.047046 | -0.021844 | 0.0243 | -0.008409 | 0.088755 | 0.1011 | 0.21064 | -0.085952 | 0.088043 | 0.64138 | -0.028879 | 122.0281 | 122.299 | 122.1923 | -0.15499 | -0.035598 | -122.1753 | 0.02851 | 0.041945 | 0.077543 | -122.163 | -122.0535 | -0.10464 | -0.23595 | 0.1384 | 0.021475 | 0.12611 | 0.034924 | -0.071762 | 0.13911 | 0.15145 | 0.261 | 0.074654 | -122.3501 | 122.0785 | 122.3494 | 122.2427 | 0.69173 | -122.4191
3626.5781 | 122.4701 | -0.041199 | 122.2458 | -0.01778 | -0.052461 | 0.039439 | 0.019469 | -0.01336 | -0.0037989 | -0.021518 | -0.0022666 | -0.0022903 | 0.057619 | 0.047952 | 0.047687 | -0.017266 | 0.019721 | -0.003831 | 0.084176 | 0.10567 | 0.21064 | -0.090531 | 0.088043 | 0.64138 | -0.033458 | 122.0236 | 122.3036 | 122.1969 | -0.15499 | -0.049332 | -122.1616 | 0.023933 | 0.037368 | 0.0867 | -122.1401 | -122.0351 | -0.11379 | -0.22222 | 0.12924 | 0.007741 | 0.12153 | 0.057812 | -0.048873 | 0.12538 | 0.14687 | 0.25184 | 0.06092 | -122.3363 | 122.0648 | 122.3448 | 122.2381 | 0.68258 | -122.4008
3628.3281 | 122.4655 | -0.064087 | 122.2458 | -0.01778 | -0.052461 | 0.039652 | 0.019041 | -0.013574 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057405 | 0.047525 | 0.04726 | -0.008109 | 0.0243 | -0.003831 | 0.088755 | 0.10567 | 0.20149 | -0.090531 | 0.092622 | 0.63222 | -0.033458 | 122.0281 | 122.299 | 122.1878 | -0.15957 | -0.026444 | -122.157 | 0.055978 | 0.060256 | 0.0867 | -122.1401 | -122.0443 | -0.095483 | -0.21764 | 0.15671 | 0.030629 | 0.12611 | 0.053234 | -0.05803 | 0.15284 | 0.16976 | 0.26558 | 0.088387 | -122.3363 | 122.0922 | 122.3631 | 122.2518 | 0.69631 | -122.4054
3630.0938 | 122.3465 | -0.091553 | 122.2641 | -0.0025182 | -0.052888 | 0.039652 | 0.019041 | -0.01336 | -0.0037989 | -0.021518 | -0.0024804 | -0.0020767 | 0.057619 | 0.047739 | 0.04726 | -0.008109 | 0.028878 | -0.003831 | 0.084176 | 0.10567 | 0.20607 | -0.081373 | 0.097201 | 0.64596 | -0.028879 | 122.0281 | 122.299 | 122.1878 | -0.15041 | 0.01018 | -122.1799 | 0.083444 | 0.087722 | 0.077542 | -122.1584 | -122.058 | -0.058859 | -0.23595 | 0.18875 | 0.062674 | 0.12153 | 0.034924 | -0.07634 | 0.17573 | 0.19723 | 0.29762 | 0.12043 | -122.3455 | 122.1197 | 122.3906 | 122.2793 | 0.73751 | -122.4145
3631.7969 | 122.3969 | -0.10529 | 122.2687 | -0.0025182 | -0.052888 | 0.039225 | 0.019255 | -0.012933 | -0.0037989 | -0.021518 | -0.002694 | -0.0025041 | 0.05826 | 0.047739 | 0.047474 | -0.017266 | 0.028878 | 0.000747 | 0.084176 | 0.10567 | 0.20607 | -0.085952 | 0.088043 | 0.6368 | -0.033458 | 122.0281 | 122.3036 | 122.1923 | -0.15957 | 0.019334 | -122.1845 | 0.08802 | 0.10603 | 0.086699 | -122.163 | -122.0626 | -0.054284 | -0.24053 | 0.19333 | 0.071828 | 0.12611 | 0.034924 | -0.07634 | 0.18946 | 0.21096 | 0.31135 | 0.13416 | -122.3546 | 122.1334 | 122.4089 | 122.2976 | 0.74209 | -122.4282
3633.5625 | 122.3831 | -0.073242 | 122.2824 | -0.0025182 | -0.052888 | 0.039652 | 0.019255 | -0.013147 | -0.0042263 | -0.0062567 | -0.0022666 | -0.0022903 | 0.057832 | 0.047525 | 0.04726 | -0.021844 | 0.028878 | 0.000747 | 0.088755 | 0.1011 | 0.21064 | -0.081373 | 0.088043 | 0.6368 | -0.0243 | 122.019 | 122.299 | 122.1923 | -0.15499 | -0.008131 | -122.1937 | 0.051398 | 0.073989 | 0.08212 | -122.1813 | -122.0718 | -0.081749 | -0.26342 | 0.16129 | 0.048942 | 0.13069 | 0.016613 | -0.090073 | 0.162 | 0.17434 | 0.28389 | 0.10212 | -122.3638 | 122.0922 | 122.3723 | 122.2656 | 0.71004 | -122.4374
3635.3281 | 122.3694 | -0.10071 | 122.3007 | 0.0051128 | -0.052675 | 0.039652 | 0.019041 | -0.013147 | -0.0037989 | -0.013887 | -0.0024804 | -0.0020767 | 0.057405 | 0.047525 | 0.047046 | -0.017266 | 0.0243 | -0.003831 | 0.088755 | 0.1011 | 0.20607 | -0.085952 | 0.092622 | 0.6368 | -0.038036 | 122.0144 | 122.299 | 122.1969 | -0.15957 | 0.014756 | -122.212 | 0.083442 | 0.096877 | 0.082121 | -122.1996 | -122.0947 | -0.058862 | -0.28631 | 0.19333 | 0.062672 | 0.12153 | -0.001697 | -0.1038 | 0.18946 | 0.2018 | 0.30677 | 0.12501 | -122.3867 | 122.1151 | 122.3997 | 122.2976 | 0.73751 | -122.4603
3637.0781 | 122.4655 | -0.068665 | 122.2137 | -0.010149 | -0.053102 | 0.039439 | 0.019255 | -0.01336 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.047739 | 0.04726 | -0.003531 | 0.015142 | 0.000747 | 0.084176 | 0.11025 | 0.20149 | -0.090531 | 0.092622 | 0.64596 | -0.028879 | 122.0236 | 122.299 | 122.1969 | -0.16415 | -0.021866 | -122.1296 | 0.065134 | 0.069412 | 0.091278 | -122.1035 | -122.0123 | -0.095484 | -0.19017 | 0.16129 | 0.039786 | 0.13527 | 0.085278 | -0.016829 | 0.15284 | 0.17892 | 0.27015 | 0.083807 | -122.3043 | 122.0922 | 122.3677 | 122.2656 | 0.71462 | -122.3779
3638.8281 | 122.4518 | -0.050354 | 122.2687 | -0.010149 | -0.052675 | 0.039225 | 0.019469 | -0.013147 | -0.0040125 | -0.029148 | -0.0024804 | -0.0022903 | 0.057832 | 0.047311 | 0.04726 | -0.021844 | 0.028878 | -0.003831 | 0.093333 | 0.10567 | 0.20607 | -0.085952 | 0.088043 | 0.64138 | -0.033458 | 122.0281 | 122.2944 | 122.1969 | -0.15499 | -0.035598 | -122.1753 | 0.02851 | 0.046523 | 0.082121 | -122.163 | -122.0626 | -0.10464 | -0.24053 | 0.1384 | 0.016896 | 0.12153 | 0.025767 | -0.071761 | 0.14369 | 0.15603 | 0.25642 | 0.079232 | -122.3546 | 122.0785 | 122.3448 | 122.2473 | 0.69173 | -122.4237
3640.5938 | 122.4335 | -0.054932 | 122.2412 | -0.01778 | -0.053102 | 0.039225 | 0.019041 | -0.013574 | -0.0042263 | -0.021518 | -0.002694 | -0.0025041 | 0.057832 | 0.047311 | 0.04726 | -0.012688 | 0.0243 | 0.000747 | 0.088755 | 0.11483 | 0.20607 | -0.085952 | 0.092622 | 0.6368 | -0.028879 | 122.0281 | 122.2944 | 122.1923 | -0.15957 | -0.03102 | -122.1525 | 0.042244 | 0.055679 | 0.086699 | -122.1264 | -122.0351 | -0.10464 | -0.21306 | 0.14755 | 0.026053 | 0.13069 | 0.053233 | -0.048874 | 0.14369 | 0.16976 | 0.261 | 0.079232 | -122.3272 | 122.0831 | 122.3494 | 122.2473 | 0.69173 | -122.4008
3642.2812 | 122.3557 | -0.082397 | 122.2916 | -0.0025182 | -0.052888 | 0.039439 | 0.019469 | -0.013574 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.057405 | 0.047525 | 0.047046 | -0.012688 | 0.015142 | -0.003831 | 0.079598 | 0.11025 | 0.20607 | -0.085952 | 0.088043 | 0.64138 | -0.028879 | 122.0236 | 122.2944 | 122.1923 | -0.15499 | -0.003555 | -122.212 | 0.069709 | 0.078566 | 0.082121 | -122.1813 | -122.0855 | -0.072594 | -0.26799 | 0.17044 | 0.053518 | 0.12611 | 0.002879 | -0.099228 | 0.162 | 0.19265 | 0.28846 | 0.097539 | -122.3775 | 122.106 | 122.3768 | 122.2747 | 0.72378 | -122.4466
3644.0469 | 122.3831 | -0.07782 | 122.2824 | -0.01778 | -0.052675 | 0.039439 | 0.019041 | -0.013147 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.047739 | 0.047046 | -0.017266 | 0.028878 | -0.003831 | 0.079598 | 0.11025 | 0.20607 | -0.090531 | 0.083464 | 0.65511 | -0.028879 | 122.0281 | 122.299 | 122.1969 | -0.15499 | -0.012711 | -122.2028 | 0.060554 | 0.073989 | 0.0867 | -122.1722 | -122.0763 | -0.077171 | -0.25426 | 0.16128 | 0.048941 | 0.12611 | 0.016613 | -0.085494 | 0.15742 | 0.18807 | 0.28389 | 0.1067 | -122.3729 | 122.106 | 122.3768 | 122.2747 | 0.73293 | -122.4374
3645.8125 | 122.4747 | -0.022888 | 122.2595 | -0.01778 | -0.053102 | 0.039439 | 0.018828 | -0.013574 | -0.0037989 | -0.021518 | -0.002694 | -0.0022903 | 0.057832 | 0.047525 | 0.047474 | -0.012688 | 0.0243 | -0.008409 | 0.088755 | 0.10567 | 0.21064 | -0.09511 | 0.092622 | 0.64138 | -0.028879 | 122.019 | 122.299 | 122.1878 | -0.15499 | -0.072222 | -122.1708 | 0.0102 | 0.014479 | 0.086701 | -122.1538 | -122.0489 | -0.1321 | -0.24053 | 0.11551 | -0.005991 | 0.12611 | 0.039502 | -0.071762 | 0.11164 | 0.12856 | 0.23353 | 0.047188 | -122.3546 | 122.0419 | 122.3219 | 122.2106 | 0.66427 | -122.4145
3647.5156 | 122.4289 | -0.045776 | 122.2641 | -0.01778 | -0.053102 | 0.039652 | 0.019255 | -0.01336 | -0.0042263 | -0.021518 | -0.002053 | -0.0022903 | 0.057619 | 0.047311 | 0.04726 | -0.026423 | 0.019721 | 0.000747 | 0.084176 | 0.11025 | 0.21522 | -0.090531 | 0.088043 | 0.64138 | -0.028879 | 122.0236 | 122.299 | 122.1878 | -0.15499 | -0.044755 | -122.1799 | 0.019353 | 0.046523 | 0.091278 | -122.1538 | -122.0489 | -0.10921 | -0.24053 | 0.13382 | 0.016897 | 0.12611 | 0.034924 | -0.07634 | 0.12995 | 0.15603 | 0.261 | 0.065497 | -122.3546 | 122.0693 | 122.3448 | 122.2335 | 0.68715 | -122.4191
3649.2812 | 122.4518 | -0.050354 | 122.2321 | -0.01778 | -0.052888 | 0.039652 | 0.019469 | -0.01336 | -0.0044399 | -0.021518 | -0.0022666 | -0.0020767 | 0.057832 | 0.047525 | 0.047474 | -0.008109 | 0.028878 | 0.000747 | 0.084176 | 0.1011 | 0.20607 | -0.085952 | 0.083464 | 0.65054 | -0.028879 | 122.0144 | 122.3036 | 122.1969 | -0.15957 | -0.035598 | -122.1479 | 0.042245 | 0.051101 | 0.086699 | -122.131 | -122.026 | -0.10922 | -0.21764 | 0.13382 | 0.021475 | 0.13069 | 0.071545 | -0.03514 | 0.13453 | 0.15145 | 0.25642 | 0.079232 | -122.318 | 122.0648 | 122.354 | 122.2473 | 0.70089 | -122.3916
3651.0469 | 122.4518 | -0.059509 | 122.2504 | -0.010149 | -0.053102 | 0.039225 | 0.019041 | -0.01336 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.047952 | 0.04726 | -0.021844 | 0.019721 | 0.000747 | 0.084176 | 0.1011 | 0.20607 | -0.085952 | 0.088043 | 0.64596 | -0.028879 | 122.019 | 122.299 | 122.2015 | -0.15957 | -0.026443 | -122.1662 | 0.037665 | 0.060256 | 0.086699 | -122.1493 | -122.0443 | -0.10006 | -0.23137 | 0.14755 | 0.03063 | 0.13069 | 0.048657 | -0.048871 | 0.14369 | 0.1606 | 0.26558 | 0.07923 | -122.3363 | 122.0785 | 122.3585 | 122.261 | 0.70547 | -122.4099
3652.8125 | 122.4884 | -0.045776 | 122.2458 | -0.010149 | -0.052675 | 0.039439 | 0.019041 | -0.013147 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057619 | 0.047739 | 0.047474 | -0.021844 | 0.019721 | 0.000747 | 0.088755 | 0.11025 | 0.20607 | -0.085952 | 0.083464 | 0.65054 | -0.0243 | 122.0236 | 122.299 | 122.1923 | -0.15957 | -0.040176 | -122.157 | 0.023932 | 0.046523 | 0.086699 | -122.1355 | -122.0397 | -0.11379 | -0.22222 | 0.12924 | 0.021476 | 0.13527 | 0.053234 | -0.053452 | 0.13453 | 0.15603 | 0.25184 | 0.065497 | -122.3317 | 122.0693 | 122.3448 | 122.2381 | 0.69631 | -122.4054
3654.5781 | 122.3511 | -0.09613 | 122.2824 | -0.010149 | -0.053102 | 0.039439 | 0.019255 | -0.013574 | -0.0044399 | -0.036779 | -0.0022666 | -0.0020767 | 0.058046 | 0.047739 | 0.04726 | -0.012688 | 0.019721 | -0.003831 | 0.093333 | 0.10567 | 0.21064 | -0.090531 | 0.088043 | 0.64596 | -0.033458 | 122.0236 | 122.2944 | 122.1969 | -0.16415 | 0.005599 | -122.1891 | 0.083442 | 0.092299 | 0.0867 | -122.1767 | -122.0718 | -0.068019 | -0.25884 | 0.18417 | 0.062672 | 0.13069 | 0.012034 | -0.085494 | 0.18946 | 0.2018 | 0.30678 | 0.11585 | -122.3729 | 122.1197 | 122.3906 | 122.293 | 0.74209 | -122.4466
3656.2812 | 122.4289 | -0.059509 | 122.2687 | -0.01778 | -0.052888 | 0.038798 | 0.019041 | -0.01336 | -0.0040125 | -0.013887 | -0.0024804 | -0.0027177 | 0.058046 | 0.047739 | 0.047046 | -0.012688 | 0.019721 | -0.008409 | 0.088755 | 0.10567 | 0.20607 | -0.090531 | 0.088043 | 0.65054 | -0.033458 | 122.019 | 122.3036 | 122.1923 | -0.15499 | -0.031022 | -122.1799 | 0.046821 | 0.0511 | 0.082122 | -122.163 | -122.0626 | -0.095482 | -0.24968 | 0.14755 | 0.026051 | 0.12153 | 0.034924 | -0.07634 | 0.14826 | 0.16518 | 0.26558 | 0.07923 | -122.3592 | 122.0785 | 122.3631 | 122.2518 | 0.71005 | -122.4237
3658.0469 | 122.5067 | -0.059509 | 122.2412 | -0.0025182 | -0.052461 | 0.039439 | 0.019255 | -0.013574 | -0.0042263 | -0.021518 | -0.0022666 | -0.0020767 | 0.057405 | 0.047525 | 0.047046 | -0.017266 | 0.019721 | -0.003831 | 0.093333 | 0.10567 | 0.20149 | -0.085952 | 0.088043 | 0.65054 | -0.038036 | 122.0236 | 122.299 | 122.1878 | -0.15041 | -0.026443 | -122.1479 | 0.042243 | 0.055678 | 0.082121 | -122.1355 | -122.0397 | -0.090903 | -0.21764 | 0.14755 | 0.021473 | 0.11238 | 0.057812 | -0.053452 | 0.15284 | 0.16518 | 0.261 | 0.07923 | -122.3272 | 122.0831 | 122.3585 | 122.2473 | 0.71005 | -122.3916
3659.75 | 122.4472 | -0.045776 | 122.2412 | -0.010149 | -0.053102 | 0.039652 | 0.019041 | -0.013788 | -0.0042263 | -0.021518 | -0.0024804 | -0.0020767 | 0.057405 | 0.048166 | 0.047474 | -0.012688 | 0.019721 | -0.003831 | 0.088755 | 0.10567 | 0.21064 | -0.085952 | 0.083464 | 0.65054 | -0.033458 | 122.0236 | 122.3036 | 122.1832 | -0.15957 | -0.040176 | -122.1525 | 0.033088 | 0.041945 | 0.082121 | -122.1355 | -122.0306 | -0.11379 | -0.21764 | 0.12924 | 0.012318 | 0.12611 | 0.06239 | -0.058031 | 0.13453 | 0.15145 | 0.25642 | 0.065497 | -122.3272 | 122.0693 | 122.3494 | 122.229 | 0.69631 | -122.4008
3661.5156 | 122.4609 | -0.041199 | 122.2275 | -0.010149 | -0.052888 | 0.039225 | 0.019041 | -0.013788 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.057405 | 0.047311 | 0.047474 | -0.012688 | 0.0243 | 0.000747 | 0.084176 | 0.096516 | 0.21064 | -0.085952 | 0.092622 | 0.65054 | -0.0243 | 122.019 | 122.3036 | 122.1878 | -0.15499 | -0.044753 | -122.1433 | 0.028511 | 0.041946 | 0.086699 | -122.131 | -122.0168 | -0.11379 | -0.20849 | 0.13382 | 0.016899 | 0.13069 | 0.076123 | -0.039719 | 0.12538 | 0.13772 | 0.25184 | 0.065499 | -122.3134 | 122.0602 | 122.3448 | 122.229 | 0.69173 | -122.3825
3663.2812 | 122.3557 | -0.10529 | 122.2916 | -0.01778 | -0.053316 | 0.039225 | 0.019469 | -0.013147 | -0.0044399 | -0.013887 | -0.0022666 | -0.0025041 | 0.057832 | 0.047739 | 0.04726 | -0.017266 | 0.0243 | -0.003831 | 0.084176 | 0.10567 | 0.21064 | -0.081373 | 0.088043 | 0.64596 | -0.033458 | 122.019 | 122.3036 | 122.1923 | -0.15957 | 0.023913 | -122.2074 | 0.08802 | 0.10146 | 0.077542 | -122.1859 | -122.0809 | -0.054284 | -0.27257 | 0.19333 | 0.071828 | 0.12611 | 0.012036 | -0.099228 | 0.18946 | 0.21096 | 0.31593 | 0.12959 | -122.3729 | 122.1243 | 122.4089 | 122.2976 | 0.75124 | -122.4511
3665.0469 | 122.3831 | -0.07782 | 122.2549 | -0.01778 | -0.052675 | 0.039225 | 0.019041 | -0.01336 | -0.0040125 | -0.029148 | -0.002694 | -0.0025041 | 0.057619 | 0.047739 | 0.04726 | -0.012688 | 0.0243 | 0.000747 | 0.093333 | 0.10567 | 0.21522 | -0.09511 | 0.097201 | 0.64596 | -0.0243 | 122.0281 | 122.3036 | 122.2015 | -0.15041 | -0.01729 | -122.1616 | 0.065132 | 0.078567 | 0.095857 | -122.1493 | -122.0397 | -0.072592 | -0.22679 | 0.17502 | 0.05352 | 0.12611 | 0.048657 | -0.053449 | 0.17115 | 0.18349 | 0.29304 | 0.10212 | -122.3501 | 122.106 | 122.3814 | 122.2793 | 0.72378 | -122.4054
3666.8125 | 122.3648 | -0.11444 | 122.2916 | -0.0025182 | -0.052888 | 0.039652 | 0.019041 | -0.013147 | -0.0044399 | -0.013887 | -0.0022666 | -0.0020767 | 0.057619 | 0.047739 | 0.047046 | -0.008109 | 0.019721 | -0.008409 | 0.088755 | 0.1011 | 0.21064 | -0.085952 | 0.092622 | 0.64596 | -0.033458 | 122.0281 | 122.3082 | 122.1923 | -0.15041 | 0.028489 | -122.2028 | 0.10633 | 0.10603 | 0.077543 | -122.1905 | -122.0809 | -0.035971 | -0.26342 | 0.20706 | 0.080983 | 0.11695 | 0.016615 | -0.099228 | 0.2032 | 0.21554 | 0.32509 | 0.13416 | -122.3775 | 122.1426 | 122.4226 | 122.3068 | 0.7604 | -122.442
3668.5156 | 122.4747 | -0.054932 | 122.2321 | -0.033042 | -0.052888 | 0.039652 | 0.019255 | -0.013147 | -0.0042263 | -0.0062567 | -0.0024804 | -0.0020767 | 0.057832 | 0.047952 | 0.047046 | -0.012688 | 0.0243 | 0.000747 | 0.088755 | 0.1011 | 0.20607 | -0.081373 | 0.088043 | 0.65969 | -0.028879 | 122.0236 | 122.299 | 122.1878 | -0.15957 | -0.026441 | -122.1433 | 0.042244 | 0.055679 | 0.08212 | -122.131 | -122.026 | -0.10464 | -0.20849 | 0.14297 | 0.026053 | 0.13069 | 0.066967 | -0.044297 | 0.14369 | 0.15603 | 0.261 | 0.079232 | -122.3134 | 122.0785 | 122.354 | 122.2427 | 0.71462 | -122.3916
3670.2812 | 122.3969 | -0.10071 | 122.2733 | -0.010149 | -0.052888 | 0.039652 | 0.019255 | -0.01336 | -0.0042263 | -0.013887 | -0.0024804 | -0.0025041 | 0.057405 | 0.047739 | 0.04726 | -0.012688 | 0.0243 | 0.000747 | 0.084176 | 0.10567 | 0.21522 | -0.081373 | 0.092622 | 0.65969 | -0.033458 | 122.019 | 122.299 | 122.2015 | -0.15957 | 0.019335 | -122.1891 | 0.08802 | 0.10146 | 0.08212 | -122.1676 | -122.058 | -0.058862 | -0.25426 | 0.19333 | 0.06725 | 0.12611 | 0.025769 | -0.071759 | 0.18488 | 0.20638 | 0.31593 | 0.12501 | -122.3546 | 122.1197 | 122.3997 | 122.3022 | 0.7604 | -122.4328
3672.0312 | 122.4014 | -0.086975 | 122.2687 | -0.010149 | -0.053316 | 0.039439 | 0.019041 | -0.01336 | -0.0040125 | -0.013887 | -0.002053 | -0.0022903 | 0.058046 | 0.047739 | 0.04726 | -0.021844 | 0.0243 | 0.005325 | 0.084176 | 0.11025 | 0.20607 | -0.085952 | 0.088043 | 0.65969 | -0.028879 | 122.019 | 122.3036 | 122.1923 | -0.15041 | 0.001023 | -122.1845 | 0.065131 | 0.0923 | 0.091277 | -122.1584 | -122.0626 | -0.063437 | -0.24968 | 0.17502 | 0.058096 | 0.12153 | 0.034924 | -0.07634 | 0.17115 | 0.19723 | 0.29304 | 0.11127 | -122.3546 | 122.106 | 122.3906 | 122.2793 | 0.74667 | -122.4191
3673.7969 | 122.3923 | -0.068665 | 122.2687 | -0.025411 | -0.052888 | 0.039652 | 0.019041 | -0.01336 | -0.0044399 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.047952 | 0.046833 | -0.012688 | 0.0243 | -0.003831 | 0.088755 | 0.11025 | 0.21064 | -0.09511 | 0.092622 | 0.65969 | -0.028879 | 122.019 | 122.299 | 122.1923 | -0.16415 | -0.026445 | -122.1799 | 0.055977 | 0.064834 | 0.091279 | -122.1584 | -122.058 | -0.095484 | -0.24968 | 0.16129 | 0.039786 | 0.13527 | 0.030346 | -0.07634 | 0.15742 | 0.17892 | 0.27931 | 0.092965 | -122.3638 | 122.0877 | 122.3677 | 122.261 | 0.72836 | -122.4328
3675.5625 | 122.4289 | -0.050354 | 122.2412 | -0.010149 | -0.053102 | 0.039225 | 0.018614 | -0.01336 | -0.0040125 | -0.021518 | -0.0022666 | -0.0022903 | 0.057832 | 0.048166 | 0.04726 | -0.008109 | 0.015142 | 0.000747 | 0.084176 | 0.10567 | 0.20607 | -0.090531 | 0.088043 | 0.65969 | -0.028879 | 122.0327 | 122.3082 | 122.1969 | -0.16415 | -0.040177 | -122.157 | 0.042245 | 0.051101 | 0.091278 | -122.1355 | -122.0351 | -0.11379 | -0.20848 | 0.1384 | 0.021475 | 0.13527 | 0.066969 | -0.044295 | 0.13453 | 0.15603 | 0.25642 | 0.065496 | -122.3317 | 122.0831 | 122.3585 | 122.2473 | 0.71005 | -122.4054
3677.3281 | 122.4838 | -0.054932 | 122.2321 | -0.01778 | -0.052888 | 0.039439 | 0.019041 | -0.01336 | -0.0042263 | -0.029148 | -0.0024804 | -0.0025041 | 0.057832 | 0.047525 | 0.047474 | -0.017266 | 0.019721 | -0.003831 | 0.088755 | 0.1011 | 0.21064 | -0.085952 | 0.092622 | 0.65969 | -0.033458 | 122.0281 | 122.3036 | 122.1923 | -0.15499 | -0.03102 | -122.1433 | 0.037666 | 0.051101 | 0.082121 | -122.131 | -122.0214 | -0.10006 | -0.20391 | 0.14755 | 0.021474 | 0.12153 | 0.071545 | -0.039719 | 0.14369 | 0.15603 | 0.26558 | 0.074653 | -122.318 | 122.0831 | 122.3585 | 122.2473 | 0.71462 | -122.387
3679.0312 | 122.4747 | -0.050354 | 122.2458 | -0.01778 | -0.053102 | 0.039439 | 0.018828 | -0.01336 | -0.0046535 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.047952 | 0.04726 | -0.012688 | 0.0243 | 0.000747 | 0.093333 | 0.11025 | 0.20607 | -0.081373 | 0.088043 | 0.65969 | -0.028879 | 122.0327 | 122.299 | 122.1878 | -0.15499 | -0.031019 | -122.1525 | 0.037666 | 0.051101 | 0.08212 | -122.1355 | -122.0397 | -0.10464 | -0.21306 | 0.1384 | 0.021475 | 0.12611 | 0.053234 | -0.05803 | 0.14369 | 0.16061 | 0.25642 | 0.074654 | -122.3272 | 122.0831 | 122.3494 | 122.2381 | 0.71005 | -122.4008
3680.7969 | 122.4014 | -0.082397 | 122.2916 | -0.01778 | -0.053316 | 0.039652 | 0.019041 | -0.01336 | -0.0042263 | -0.021518 | -0.002694 | -0.0025041 | 0.058046 | 0.047739 | 0.04726 | -0.012688 | 0.019721 | 0.000747 | 0.084176 | 0.10567 | 0.20607 | -0.090531 | 0.088043 | 0.66427 | -0.0243 | 122.0236 | 122.3036 | 122.1969 | -0.15041 | -0.008134 | -122.2074 | 0.069709 | 0.083144 | 0.091278 | -122.1859 | -122.0855 | -0.068015 | -0.26799 | 0.17044 | 0.058097 | 0.12611 | 0.012036 | -0.094649 | 0.16657 | 0.18807 | 0.28846 | 0.10212 | -122.3821 | 122.106 | 122.386 | 122.2793 | 0.74667 | -122.442
3682.5 | 122.4792 | -0.045776 | 122.2229 | -0.0025182 | -0.053316 | 0.039439 | 0.019041 | -0.013147 | -0.0044399 | -0.021518 | -0.0024804 | -0.0020767 | 0.057405 | 0.047952 | 0.047474 | -0.017266 | 0.0243 | -0.008409 | 0.093333 | 0.11025 | 0.21064 | -0.085952 | 0.092622 | 0.65511 | -0.0243 | 122.0327 | 122.3036 | 122.1923 | -0.15957 | -0.040176 | -122.1296 | 0.02851 | 0.037367 | 0.077543 | -122.1126 | -122.0123 | -0.11379 | -0.19017 | 0.1384 | 0.021476 | 0.13527 | 0.080701 | -0.030563 | 0.13911 | 0.15603 | 0.25642 | 0.070076 | -122.3089 | 122.0785 | 122.3494 | 122.2381 | 0.70089 | -122.3825
3684.2656 | 122.3648 | -0.091553 | 122.2824 | -0.010149 | -0.052675 | 0.039225 | 0.019041 | -0.01336 | -0.0040125 | -0.013887 | -0.0029076 | -0.0025041 | 0.057832 | 0.047952 | 0.047046 | -0.008109 | 0.019721 | 0.000747 | 0.088755 | 0.1011 | 0.20149 | -0.081373 | 0.092622 | 0.65969 | -0.0243 | 122.019 | 122.3036 | 122.2015 | -0.15957 | 0.01018 | -122.1937 | 0.083444 | 0.0923 | 0.08212 | -122.1813 | -122.0809 | -0.068017 | -0.26342 | 0.18417 | 0.067253 | 0.13527 | 0.021191 | -0.080915 | 0.18031 | 0.19265 | 0.29304 | 0.11127 | -122.3638 | 122.1105 | 122.3952 | 122.293 | 0.75125 | -122.442
3686.0156 | 122.374 | -0.09613 | 122.2824 | -0.010149 | -0.053316 | 0.039439 | 0.018614 | -0.013574 | -0.0044399 | -0.013887 | -0.002694 | -0.0022903 | 0.058046 | 0.047739 | 0.04726 | -0.021844 | 0.028878 | -0.012988 | 0.088755 | 0.11025 | 0.20149 | -0.090531 | 0.097201 | 0.66427 | -0.0243 | 122.0236 | 122.299 | 122.1969 | -0.15957 | 0.005599 | -122.1937 | 0.074286 | 0.083142 | 0.077543 | -122.1722 | -122.0809 | -0.06344 | -0.25884 | 0.19333 | 0.07183 | 0.13527 | 0.016613 | -0.085494 | 0.18488 | 0.20638 | 0.29762 | 0.12501 | -122.3729 | 122.1197 | 122.3952 | 122.293 | 0.7604 | -122.442
3687.7656 | 122.3282 | -0.091553 | 122.2733 | -0.01778 | -0.052675 | 0.039439 | 0.019041 | -0.013147 | -0.0044399 | -0.021518 | -0.002694 | -0.0025041 | 0.057619 | 0.047952 | 0.04726 | -0.008109 | 0.015142 | -0.003831 | 0.088755 | 0.1011 | 0.21064 | -0.090531 | 0.097201 | 0.66885 | -0.0243 | 122.0281 | 122.3082 | 122.1969 | -0.15499 | 0.001022 | -122.1845 | 0.083444 | 0.087722 | 0.0867 | -122.1722 | -122.0626 | -0.063438 | -0.2451 | 0.18875 | 0.067253 | 0.13069 | 0.034926 | -0.076338 | 0.18031 | 0.19265 | 0.3022 | 0.10669 | -122.3638 | 122.1197 | 122.3997 | 122.2885 | 0.7604 | -122.4282
3689.4688 | 122.4884 | -0.050354 | 122.2229 | -0.01778 | -0.053316 | 0.039652 | 0.018828 | -0.013574 | -0.0042263 | -0.021518 | -0.0022666 | -0.0022903 | 0.057619 | 0.047952 | 0.04726 | -0.021844 | 0.0243 | -0.003831 | 0.093333 | 0.11025 | 0.20607 | -0.085952 | 0.088043 | 0.66427 | -0.033458 | 122.019 | 122.299 | 122.2015 | -0.15041 | -0.035598 | -122.1296 | 0.02851 | 0.046523 | 0.082121 | -122.1126 | -122.0168 | -0.10006 | -0.20391 | 0.1384 | 0.016896 | 0.11695 | 0.076123 | -0.021405 | 0.14369 | 0.16061 | 0.25642 | 0.074654 | -122.3089 | 122.0693 | 122.3494 | 122.2518 | 0.71463 | -122.3733
3691.2344 | 122.4701 | -0.032043 | 122.2412 | -0.0025182 | -0.053529 | 0.039439 | 0.019041 | -0.01336 | -0.0042263 | -0.013887 | -0.002694 | -0.0020767 | 0.057619 | 0.048166 | 0.047474 | -0.012688 | 0.028878 | -0.008409 | 0.093333 | 0.11025 | 0.21064 | -0.081373 | 0.088043 | 0.66427 | -0.028879 | 122.0327 | 122.3036 | 122.1923 | -0.15499 | -0.04933 | -122.1479 | 0.019355 | 0.023634 | 0.072964 | -122.131 | -122.0306 | -0.12295 | -0.20848 | 0.12009 | 0.003164 | 0.12611 | 0.06239 | -0.048874 | 0.12538 | 0.1423 | 0.24269 | 0.060921 | -122.3226 | 122.0648 | 122.3356 | 122.2244 | 0.69632 | -122.3962
3693 | 122.4197 | -0.068665 | 122.2687 | -0.01778 | -0.052675 | 0.039439 | 0.019041 | -0.013574 | -0.0042263 | -0.021518 | -0.0024804 | -0.0016495 | 0.057619 | 0.047739 | 0.047474 | -0.021844 | 0.019721 | -0.008409 | 0.088755 | 0.11025 | 0.21064 | -0.090531 | 0.097201 | 0.66427 | -0.033458 | 122.0281 | 122.3082 | 122.1878 | -0.15957 | -0.021866 | -122.1799 | 0.046821 | 0.060256 | 0.082122 | -122.1584 | -122.058 | -0.090905 | -0.24053 | 0.16587 | 0.035207 | 0.12611 | 0.039503 | -0.080918 | 0.15742 | 0.17892 | 0.27931 | 0.088386 | -122.3592 | 122.0968 | 122.3768 | 122.2564 | 0.73294 | -122.4282
3694.7812 | 122.3831 | -0.082397 | 122.2733 | -0.01778 | -0.052888 | 0.039225 | 0.019041 | -0.01336 | -0.0042263 | -0.021518 | -0.002053 | -0.0025041 | 0.057619 | 0.047739 | 0.047046 | -0.012688 | 0.0243 | 0.005325 | 0.079598 | 0.1011 | 0.21522 | -0.085952 | 0.088043 | 0.67343 | -0.033458 | 122.0281 | 122.299 | 122.1969 | -0.15041 | -0.003555 | -122.1937 | 0.069709 | 0.087722 | 0.091277 | -122.1722 | -122.058 | -0.068015 | -0.2451 | 0.17044 | 0.048939 | 0.11695 | 0.025769 | -0.076338 | 0.162 | 0.18349 | 0.29762 | 0.1067 | -122.3592 | 122.1105 | 122.3814 | 122.2793 | 0.75583 | -122.4237
3696.5625 | 122.4701 | -0.041199 | 122.2458 | -0.010149 | -0.053102 | 0.039439 | 0.018614 | -0.013147 | -0.0042263 | -0.029148 | -0.0024804 | -0.0022903 | 0.057619 | 0.047952 | 0.047474 | -0.017266 | 0.0243 | -0.003831 | 0.088755 | 0.10567 | 0.21064 | -0.085952 | 0.088043 | 0.65969 | -0.033458 | 122.0236 | 122.3036 | 122.1878 | -0.15499 | -0.044753 | -122.157 | 0.023933 | 0.037368 | 0.082121 | -122.1401 | -122.0351 | -0.11379 | -0.22222 | 0.12924 | 0.007741 | 0.12153 | 0.057812 | -0.05803 | 0.12995 | 0.14687 | 0.25184 | 0.065499 | -122.3317 | 122.0648 | 122.3448 | 122.229 | 0.70089 | -122.4008
3698.25 | 122.3373 | -0.10529 | 122.2687 | -0.01778 | -0.053316 | 0.039652 | 0.018828 | -0.013574 | -0.0044399 | -0.013887 | -0.0022666 | -0.0022903 | 0.057405 | 0.047525 | 0.047046 | -0.012688 | 0.015142 | 0.005325 | 0.084176 | 0.10567 | 0.21064 | -0.090531 | 0.097201 | 0.66885 | -0.028879 | 122.0281 | 122.299 | 122.1923 | -0.15957 | 0.014755 | -122.1845 | 0.092598 | 0.11061 | 0.095856 | -122.163 | -122.058 | -0.054284 | -0.24053 | 0.20249 | 0.076407 | 0.13069 | 0.030346 | -0.07634 | 0.18946 | 0.21096 | 0.31593 | 0.12043 | -122.3592 | 122.1334 | 122.4043 | 122.2976 | 0.77414 | -122.4282
3699.9375 | 122.4838 | -0.018311 | 122.2321 | -0.010149 | -0.053102 | 0.039225 | 0.018614 | -0.013147 | -0.0040125 | -0.0062567 | -0.0022666 | -0.0022903 | 0.057619 | 0.047739 | 0.04726 | -0.017266 | 0.028878 | -0.003831 | 0.084176 | 0.11025 | 0.21064 | -0.090531 | 0.088043 | 0.65511 | -0.028879 | 122.0281 | 122.299 | 122.1923 | -0.15499 | -0.07222 | -122.1479 | 0.001045 | 0.01448 | 0.0867 | -122.1218 | -122.0214 | -0.13668 | -0.20391 | 0.10635 | -0.010568 | 0.12611 | 0.066967 | -0.039719 | 0.10249 | 0.12856 | 0.22896 | 0.047189 | -122.3226 | 122.0465 | 122.3173 | 122.2106 | 0.67342 | -122.387
3701.7188 | 122.4609 | -0.059509 | 122.2504 | -0.010149 | -0.053529 | 0.039439 | 0.018828 | -0.013574 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057832 | 0.047952 | 0.04726 | -0.021844 | 0.0243 | 0.000747 | 0.088755 | 0.11025 | 0.21064 | -0.085952 | 0.092622 | 0.67801 | -0.033458 | 122.019 | 122.299 | 122.1969 | -0.15041 | -0.026443 | -122.1616 | 0.037665 | 0.060256 | 0.086699 | -122.1401 | -122.0397 | -0.090903 | -0.23137 | 0.15213 | 0.026051 | 0.11695 | 0.048657 | -0.05345 | 0.14826 | 0.16976 | 0.27015 | 0.083809 | -122.3363 | 122.0785 | 122.3585 | 122.2564 | 0.73752 | -122.4008
3703.4844 | 122.4792 | -0.059509 | 122.2504 | -0.01778 | -0.053102 | 0.039439 | 0.019041 | -0.013147 | -0.0040125 | -0.021518 | -0.002694 | -0.0020767 | 0.057191 | 0.047311 | 0.046833 | -0.017266 | 0.0243 | 0.000747 | 0.093333 | 0.11025 | 0.21522 | -0.090531 | 0.088043 | 0.67801 | -0.028879 | 122.0281 | 122.299 | 122.1969 | -0.15957 | -0.031022 | -122.157 | 0.042243 | 0.060256 | 0.091278 | -122.1401 | -122.0351 | -0.10006 | -0.22222 | 0.14755 | 0.03063 | 0.13069 | 0.048657 | -0.05345 | 0.15284 | 0.16976 | 0.27473 | 0.083809 | -122.3409 | 122.0877 | 122.3585 | 122.2564 | 0.73752 | -122.4099
3705.25 | 122.4792 | -0.032043 | 122.2504 | -0.010149 | -0.053102 | 0.039652 | 0.019041 | -0.01336 | -0.0042263 | -0.021518 | -0.002694 | -0.0020767 | 0.057619 | 0.04838 | 0.04726 | -0.021844 | 0.028878 | -0.003831 | 0.088755 | 0.1011 | 0.21064 | -0.085952 | 0.092622 | 0.67343 | -0.033458 | 122.0236 | 122.3036 | 122.1969 | -0.15041 | -0.053909 | -122.1616 | 0.010199 | 0.028212 | 0.082121 | -122.1493 | -122.0397 | -0.11837 | -0.2268 | 0.12466 | -0.001415 | 0.11695 | 0.053235 | -0.05345 | 0.1208 | 0.13314 | 0.24269 | 0.060921 | -122.3363 | 122.0556 | 122.3356 | 122.229 | 0.70547 | -122.4008
3706.9531 | 122.4747 | -0.045776 | 122.2412 | -0.010149 | -0.053316 | 0.039225 | 0.019255 | -0.013574 | -0.0040125 | -0.021518 | -0.0022666 | -0.0020767 | 0.057619 | 0.047952 | 0.047046 | -0.026423 | 0.019721 | -0.003831 | 0.093333 | 0.1011 | 0.21064 | -0.085952 | 0.088043 | 0.67343 | -0.028879 | 122.0281 | 122.3082 | 122.2015 | -0.15499 | -0.040176 | -122.1479 | 0.019353 | 0.041945 | 0.082121 | -122.1401 | -122.0306 | -0.10921 | -0.21306 | 0.13382 | 0.016897 | 0.12611 | 0.066969 | -0.039716 | 0.13911 | 0.14687 | 0.25642 | 0.065497 | -122.3272 | 122.0739 | 122.354 | 122.2473 | 0.71921 | -122.3962
3708.7188 | 122.3511 | -0.10071 | 122.2824 | -0.0025182 | -0.053316 | 0.039225 | 0.018828 | -0.013788 | -0.0042263 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.048166 | 0.047046 | -0.021844 | 0.0243 | -0.003831 | 0.088755 | 0.10567 | 0.21064 | -0.090531 | 0.088043 | 0.66885 | -0.028879 | 122.0236 | 122.299 | 122.1923 | -0.15957 | 0.010177 | -122.1937 | 0.078864 | 0.096877 | 0.0867 | -122.1767 | -122.0718 | -0.058862 | -0.25884 | 0.18875 | 0.071829 | 0.13069 | 0.016613 | -0.090073 | 0.18946 | 0.20638 | 0.31135 | 0.12501 | -122.3729 | 122.1243 | 122.3997 | 122.293 | 0.76956 | -122.442
3710.4844 | 122.3328 | -0.10071 | 122.287 | -0.0025182 | -0.053316 | 0.039439 | 0.018828 | -0.013574 | -0.0040125 | -0.013887 | -0.002053 | -0.0022903 | 0.057619 | 0.047739 | 0.047474 | -0.031001 | 0.019721 | 0.000747 | 0.088755 | 0.11025 | 0.21064 | -0.090531 | 0.088043 | 0.66885 | -0.028879 | 122.0236 | 122.299 | 122.1969 | -0.15499 | 0.010177 | -122.1982 | 0.069707 | 0.10146 | 0.091278 | -122.1767 | -122.0763 | -0.054283 | -0.26342 | 0.18875 | 0.071829 | 0.12611 | 0.012036 | -0.090071 | 0.18946 | 0.21096 | 0.31135 | 0.12043 | -122.3775 | 122.1243 | 122.3997 | 122.2976 | 0.76956 | -122.442
3712.25 | 122.3923 | -0.07782 | 122.2687 | 0.0051128 | -0.053529 | 0.039439 | 0.019041 | -0.01336 | -0.0042263 | -0.013887 | -0.002694 | -0.0025041 | 0.057619 | 0.047525 | 0.047046 | -0.017266 | 0.0243 | -0.008409 | 0.088755 | 0.10567 | 0.21522 | -0.085952 | 0.088043 | 0.67343 | -0.028879 | 122.0236 | 122.299 | 122.1923 | -0.15041 | -0.008132 | -122.1799 | 0.060554 | 0.069411 | 0.077543 | -122.163 | -122.0535 | -0.072592 | -0.24511 | 0.16586 | 0.048941 | 0.12153 | 0.030346 | -0.07634 | 0.16658 | 0.18349 | 0.29304 | 0.10212 | -122.3546 | 122.1014 | 122.3768 | 122.2702 | 0.75125 | -122.4191
3713.9531 | 122.4655 | -0.064087 | 122.2321 | -0.010149 | -0.053529 | 0.039225 | 0.019041 | -0.013574 | -0.0040125 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.047952 | 0.04726 | -0.017266 | 0.028878 | -0.008409 | 0.079598 | 0.11025 | 0.20607 | -0.085952 | 0.092622 | 0.67801 | -0.033458 | 122.0281 | 122.2944 | 122.1923 | -0.15041 | -0.021865 | -122.1525 | 0.046821 | 0.055678 | 0.077543 | -122.1218 | -122.026 | -0.086325 | -0.20391 | 0.15671 | 0.030629 | 0.11695 | 0.062388 | -0.039719 | 0.14369 | 0.17434 | 0.27015 | 0.092965 | -122.318 | 122.0922 | 122.3585 | 122.2564 | 0.7421 | -122.3825
3715.7188 | 122.4655 | -0.045776 | 122.2321 | -0.010149 | -0.053316 | 0.039011 | 0.019041 | -0.013574 | -0.0037989 | -0.013887 | -0.0029076 | -0.0022903 | 0.057619 | 0.047952 | 0.047046 | -0.012688 | 0.0243 | -0.012988 | 0.093333 | 0.11025 | 0.21064 | -0.090531 | 0.092622 | 0.67801 | -0.028879 | 122.0281 | 122.3082 | 122.1878 | -0.15957 | -0.044755 | -122.1387 | 0.033088 | 0.032788 | 0.077543 | -122.1218 | -122.0214 | -0.11379 | -0.20391 | 0.1384 | 0.016897 | 0.13069 | 0.076124 | -0.044297 | 0.13911 | 0.15603 | 0.25642 | 0.070076 | -122.3226 | 122.0739 | 122.354 | 122.2335 | 0.72378 | -122.3916
3717.4219 | 122.3419 | -0.11902 | 122.287 | -0.0025182 | -0.053957 | 0.039011 | 0.019041 | -0.013574 | -0.0037989 | -0.021518 | -0.0024804 | -0.0025041 | 0.057619 | 0.047739 | 0.046833 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.11025 | 0.21064 | -0.090531 | 0.088043 | 0.67343 | -0.028879 | 122.0236 | 122.3173 | 122.1832 | -0.15499 | 0.028488 | -122.2028 | 0.097175 | 0.11061 | 0.082122 | -122.1767 | -122.0763 | -0.035972 | -0.26342 | 0.20706 | 0.09014 | 0.12611 | 0.03035 | -0.10381 | 0.2032 | 0.22927 | 0.32966 | 0.14332 | -122.3775 | 122.1426 | 122.4364 | 122.3022 | 0.79245 | -122.442
3719.1875 | 122.4976 | -0.036621 | 122.2275 | -0.01778 | -0.053316 | 0.039439 | 0.018614 | -0.013147 | -0.0040125 | -0.0062567 | -0.0022666 | -0.0022903 | 0.057405 | 0.047952 | 0.047046 | -0.017266 | 0.019721 | -0.003831 | 0.088755 | 0.11025 | 0.21522 | -0.085952 | 0.092622 | 0.67801 | -0.038036 | 122.0281 | 122.3082 | 122.1969 | -0.15041 | -0.049331 | -122.1387 | 0.019355 | 0.03279 | 0.082121 | -122.1172 | -122.0123 | -0.11379 | -0.19933 | 0.12924 | -0.001415 | 0.11238 | 0.080702 | -0.030562 | 0.12538 | 0.14687 | 0.25184 | 0.056342 | -122.3134 | 122.0648 | 122.3448 | 122.2335 | 0.71463 | -122.3779
3720.9531 | 122.4243 | -0.064087 | 122.2366 | -0.010149 | -0.053316 | 0.039225 | 0.018828 | -0.013574 | -0.0040125 | -0.021518 | -0.002694 | -0.0020767 | 0.057619 | 0.047952 | 0.04726 | -0.017266 | 0.0243 | -0.003831 | 0.088755 | 0.1011 | 0.21064 | -0.085952 | 0.088043 | 0.67801 | -0.028879 | 122.0236 | 122.3036 | 122.1969 | -0.15499 | -0.021865 | -122.1479 | 0.046821 | 0.060256 | 0.082121 | -122.1355 | -122.026 | -0.090904 | -0.21306 | 0.15213 | 0.035208 | 0.12611 | 0.066968 | -0.039717 | 0.15284 | 0.16518 | 0.27473 | 0.088387 | -122.3226 | 122.0877 | 122.3677 | 122.261 | 0.7421 | -122.3916
3722.6562 | 122.3877 | -0.068665 | 122.2687 | -0.01778 | -0.053529 | 0.039225 | 0.018828 | -0.013147 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.04838 | 0.04726 | -0.021844 | 0.019721 | -0.008409 | 0.088755 | 0.10567 | 0.21064 | -0.085952 | 0.092622 | 0.68259 | -0.033458 | 122.0236 | 122.3128 | 122.1878 | -0.15041 | -0.017287 | -122.1799 | 0.046821 | 0.060256 | 0.077543 | -122.163 | -122.058 | -0.081747 | -0.24511 | 0.16129 | 0.035207 | 0.11695 | 0.044081 | -0.080918 | 0.15742 | 0.17434 | 0.27931 | 0.088386 | -122.3546 | 122.0922 | 122.3814 | 122.2564 | 0.75125 | -122.4191
3724.4219 | 122.3877 | -0.082397 | 122.2504 | -0.010149 | -0.053316 | 0.039011 | 0.018828 | -0.013574 | -0.0042263 | -0.021518 | -0.0024804 | -0.0025041 | 0.057832 | 0.047739 | 0.04726 | -0.017266 | 0.028878 | -0.003831 | 0.088755 | 0.11025 | 0.21064 | -0.085952 | 0.088043 | 0.68259 | -0.028879 | 122.0281 | 122.3128 | 122.2015 | -0.15957 | -0.003555 | -122.1616 | 0.065131 | 0.078566 | 0.082121 | -122.1401 | -122.0397 | -0.077173 | -0.22222 | 0.17044 | 0.053518 | 0.13069 | 0.062392 | -0.048871 | 0.17115 | 0.19265 | 0.29304 | 0.11127 | -122.3363 | 122.1105 | 122.3952 | 122.2839 | 0.76498 | -122.4099
3726.125 | 122.3465 | -0.10529 | 122.2778 | 0.012744 | -0.053529 | 0.039011 | 0.018614 | -0.013788 | -0.0040125 | -0.013887 | -0.002694 | -0.0025041 | 0.057832 | 0.047525 | 0.04726 | -0.017266 | 0.0243 | -0.003831 | 0.079598 | 0.10567 | 0.21522 | -0.081373 | 0.088043 | 0.68259 | -0.028879 | 122.019 | 122.3036 | 122.1923 | -0.15499 | 0.023913 | -122.1982 | 0.08802 | 0.10146 | 0.077542 | -122.1722 | -122.0626 | -0.049705 | -0.25884 | 0.19333 | 0.076407 | 0.12611 | 0.025769 | -0.085495 | 0.18488 | 0.21096 | 0.32051 | 0.12959 | -122.3592 | 122.1243 | 122.4089 | 122.2976 | 0.78787 | -122.4328
3727.8906 | 122.406 | -0.091553 | 122.2778 | -0.010149 | -0.053743 | 0.039225 | 0.018828 | -0.013147 | -0.0040125 | -0.013887 | -0.0024804 | -0.0022903 | 0.057832 | 0.047952 | 0.047046 | -0.017266 | 0.010564 | -0.003831 | 0.084176 | 0.10567 | 0.21064 | -0.085952 | 0.092622 | 0.68717 | -0.033458 | 122.0236 | 122.3036 | 122.2015 | -0.15957 | 0.005601 | -122.1937 | 0.074287 | 0.087722 | 0.082121 | -122.1722 | -122.0672 | -0.068017 | -0.25426 | 0.18417 | 0.058095 | 0.12611 | 0.025769 | -0.076337 | 0.17573 | 0.19723 | 0.3022 | 0.10212 | -122.3638 | 122.1151 | 122.3952 | 122.293 | 0.77872 | -122.4374
3729.6406 | 122.3419 | -0.10529 | 122.287 | -0.010149 | -0.053529 | 0.039011 | 0.019041 | -0.01336 | -0.0035853 | -0.021518 | -0.002694 | -0.0020767 | 0.057619 | 0.047952 | 0.046833 | -0.017266 | 0.028878 | -0.008409 | 0.088755 | 0.11025 | 0.20607 | -0.081373 | 0.092622 | 0.68717 | -0.0243 | 122.0236 | 122.299 | 122.1969 | -0.15499 | 0.023913 | -122.1982 | 0.08802 | 0.096877 | 0.072964 | -122.1767 | -122.0809 | -0.049705 | -0.26342 | 0.19791 | 0.080986 | 0.13069 | 0.012036 | -0.090071 | 0.19404 | 0.21554 | 0.31135 | 0.13416 | -122.3684 | 122.1289 | 122.4043 | 122.3022 | 0.79245 | -122.442
3731.4062 | 122.3282 | -0.10529 | 122.287 | -0.025411 | -0.053529 | 0.039225 | 0.019041 | -0.013574 | -0.0040125 | -0.021518 | -0.0022666 | -0.0020767 | 0.057619 | 0.048166 | 0.04726 | -0.012688 | 0.019721 | -0.008409 | 0.079598 | 0.1011 | 0.20607 | -0.090531 | 0.097201 | 0.68259 | -0.028879 | 122.0327 | 122.3036 | 122.1969 | -0.15041 | 0.014755 | -122.2074 | 0.092598 | 0.096877 | 0.082122 | -122.1859 | -122.0809 | -0.045126 | -0.25426 | 0.20249 | 0.076407 | 0.12153 | 0.016614 | -0.090071 | 0.18488 | 0.20638 | 0.31135 | 0.12501 | -122.3775 | 122.138 | 122.4089 | 122.3022 | 0.78787 | -122.4374
3733.1094 | 122.4838 | -0.059509 | 122.2412 | -0.010149 | -0.053743 | 0.039225 | 0.019041 | -0.013574 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057832 | 0.047739 | 0.047474 | -0.017266 | 0.019721 | -0.008409 | 0.084176 | 0.10567 | 0.2198 | -0.090531 | 0.097201 | 0.68717 | -0.028879 | 122.0236 | 122.3082 | 122.1969 | -0.15499 | -0.031022 | -122.157 | 0.042243 | 0.0511 | 0.082122 | -122.1355 | -122.0214 | -0.095482 | -0.21764 | 0.15671 | 0.03063 | 0.12611 | 0.066969 | -0.044295 | 0.14369 | 0.16518 | 0.27931 | 0.07923 | -122.3317 | 122.0831 | 122.3677 | 122.2564 | 0.74667 | -122.3962
3734.8906 | 122.3785 | -0.086975 | 122.2504 | -0.010149 | -0.053529 | 0.039225 | 0.019041 | -0.013574 | -0.0035853 | -0.029148 | -0.0022666 | -0.0022903 | 0.057832 | 0.047739 | 0.04726 | -0.017266 | 0.0243 | -0.003831 | 0.093333 | 0.11025 | 0.21064 | -0.090531 | 0.088043 | 0.67801 | -0.0243 | 122.0236 | 122.3082 | 122.1969 | -0.15041 | -0.003556 | -122.157 | 0.069709 | 0.083144 | 0.0867 | -122.1401 | -122.0397 | -0.063437 | -0.2268 | 0.17502 | 0.062675 | 0.12611 | 0.057814 | -0.05345 | 0.18031 | 0.19723 | 0.29762 | 0.11127 | -122.3409 | 122.1105 | 122.3952 | 122.2839 | 0.76498 | -122.4008
3736.6562 | 122.493 | -0.050354 | 122.2458 | -0.0025182 | -0.053102 | 0.039225 | 0.019041 | -0.01336 | -0.0037989 | -0.021518 | -0.0024804 | -0.0020767 | 0.057405 | 0.048166 | 0.04726 | -0.021844 | 0.019721 | -0.003831 | 0.084176 | 0.11483 | 0.21522 | -0.085952 | 0.097201 | 0.69174 | -0.028879 | 122.0281 | 122.3036 | 122.1923 | -0.15499 | -0.035598 | -122.1616 | 0.02851 | 0.046523 | 0.082121 | -122.131 | -122.0306 | -0.10464 | -0.21764 | 0.14755 | 0.021475 | 0.12611 | 0.057812 | -0.053452 | 0.13453 | 0.16519 | 0.26558 | 0.070075 | -122.3317 | 122.0785 | 122.354 | 122.2427 | 0.7421 | -122.4008
3738.4062 | 122.4472 | -0.050354 | 122.2412 | -0.010149 | -0.053529 | 0.039439 | 0.018828 | -0.013788 | -0.0037989 | -0.021518 | -0.0024804 | -0.0020767 | 0.057619 | 0.047525 | 0.046833 | -0.017266 | 0.0243 | -0.003831 | 0.084176 | 0.10567 | 0.21522 | -0.090531 | 0.078886 | 0.68259 | -0.033458 | 122.0236 | 122.3036 | 122.1923 | -0.15499 | -0.040177 | -122.157 | 0.033088 | 0.046523 | 0.0867 | -122.1355 | -122.026 | -0.10464 | -0.21764 | 0.12924 | 0.016896 | 0.12153 | 0.06239 | -0.048874 | 0.13453 | 0.15603 | 0.26558 | 0.074654 | -122.3317 | 122.0739 | 122.354 | 122.2427 | 0.73294 | -122.3962
3740.1719 | 122.4335 | -0.059509 | 122.2321 | -0.010149 | -0.053529 | 0.039225 | 0.019041 | -0.013574 | -0.0040125 | -0.021518 | -0.002053 | -0.0022903 | 0.057619 | 0.047952 | 0.04726 | -0.008109 | 0.0243 | -0.008409 | 0.079598 | 0.11025 | 0.21064 | -0.085952 | 0.092622 | 0.69632 | -0.0243 | 122.0236 | 122.3082 | 122.1923 | -0.15499 | -0.026443 | -122.1525 | 0.0514 | 0.0511 | 0.077543 | -122.1218 | -122.0214 | -0.095482 | -0.20849 | 0.15213 | 0.035209 | 0.13069 | 0.076124 | -0.039719 | 0.13911 | 0.16976 | 0.27015 | 0.083809 | -122.318 | 122.0831 | 122.3677 | 122.2518 | 0.75583 | -122.387
3741.875 | 122.319 | -0.10071 | 122.287 | -0.01778 | -0.053529 | 0.039225 | 0.018828 | -0.013788 | -0.0040125 | 0.0013733 | -0.0024804 | -0.0016495 | 0.057832 | 0.048166 | 0.047046 | -0.021844 | 0.0243 | -0.003831 | 0.088755 | 0.11025 | 0.21064 | -0.085952 | 0.088043 | 0.69632 | -0.0243 | 122.0281 | 122.3036 | 122.1923 | -0.15957 | 0.014756 | -122.1982 | 0.078864 | 0.096877 | 0.082121 | -122.1767 | -122.0763 | -0.058862 | -0.25884 | 0.18875 | 0.076408 | 0.13527 | 0.016614 | -0.09465 | 0.18946 | 0.21096 | 0.31135 | 0.12501 | -122.3729 | 122.1289 | 122.4043 | 122.293 | 0.79703 | -122.4466
3743.6406 | 122.374 | -0.10529 | 122.2778 | -0.01778 | -0.053529 | 0.039225 | 0.019041 | -0.014001 | -0.0037989 | -0.021518 | -0.0022666 | -0.0025041 | 0.057832 | 0.048166 | 0.047046 | -0.017266 | 0.0243 | -0.008409 | 0.093333 | 0.10567 | 0.21064 | -0.081373 | 0.097201 | 0.69174 | -0.0243 | 122.0327 | 122.3036 | 122.1923 | -0.15957 | 0.023913 | -122.1845 | 0.08802 | 0.096877 | 0.072964 | -122.1722 | -122.0672 | -0.054284 | -0.24511 | 0.20249 | 0.080986 | 0.13527 | 0.025769 | -0.085495 | 0.19862 | 0.21096 | 0.31593 | 0.12959 | -122.3592 | 122.138 | 122.4089 | 122.2976 | 0.79703 | -122.4374
3745.3438 | 122.4289 | -0.054932 | 122.2458 | -0.010149 | -0.053529 | 0.039225 | 0.018614 | -0.013788 | -0.0040125 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.048166 | 0.04726 | -0.017266 | 0.019721 | -0.003831 | 0.088755 | 0.11025 | 0.21064 | -0.090531 | 0.097201 | 0.68717 | -0.033458 | 122.0236 | 122.3036 | 122.1969 | -0.15499 | -0.035599 | -122.157 | 0.037666 | 0.051101 | 0.0867 | -122.1355 | -122.0351 | -0.10006 | -0.22222 | 0.15213 | 0.021474 | 0.12153 | 0.057812 | -0.048873 | 0.14369 | 0.16518 | 0.26558 | 0.074653 | -122.3363 | 122.0785 | 122.3585 | 122.2518 | 0.7421 | -122.4008
3747.1094 | 122.438 | -0.068665 | 122.2549 | -0.010149 | -0.053529 | 0.039439 | 0.018828 | -0.013574 | -0.0035853 | -0.036779 | -0.0024804 | -0.0020767 | 0.057405 | 0.047952 | 0.047046 | -0.017266 | 0.0243 | -0.003831 | 0.084176 | 0.11483 | 0.21064 | -0.081373 | 0.088043 | 0.69174 | -0.033458 | 122.0327 | 122.3036 | 122.1878 | -0.15499 | -0.012708 | -122.1708 | 0.051399 | 0.064834 | 0.077542 | -122.1401 | -122.0443 | -0.086326 | -0.22222 | 0.15671 | 0.035207 | 0.12153 | 0.048657 | -0.067185 | 0.15284 | 0.1835 | 0.27931 | 0.092965 | -122.3363 | 122.1014 | 122.3723 | 122.2564 | 0.76041 | -122.4099
3748.875 | 122.3877 | -0.064087 | 122.2687 | 0.0051128 | -0.053743 | 0.039225 | 0.018614 | -0.013574 | -0.0035853 | -0.029148 | -0.002694 | -0.0022903 | 0.057832 | 0.048166 | 0.046833 | -0.017266 | 0.0243 | -0.003831 | 0.079598 | 0.10567 | 0.20607 | -0.081373 | 0.092622 | 0.69174 | -0.019721 | 122.0281 | 122.299 | 122.1923 | -0.15499 | -0.017286 | -122.1891 | 0.046821 | 0.060256 | 0.077542 | -122.163 | -122.0626 | -0.090904 | -0.24053 | 0.15671 | 0.044366 | 0.13527 | 0.030346 | -0.07634 | 0.14369 | 0.16976 | 0.27015 | 0.088387 | -122.35 | 122.0922 | 122.3631 | 122.2564 | 0.75583 | -122.4237
3750.6406 | 122.3602 | -0.09613 | 122.2916 | -0.0025182 | -0.053743 | 0.039225 | 0.018614 | -0.013788 | -0.0040125 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.048166 | 0.046833 | -0.021844 | 0.028878 | -0.012988 | 0.093333 | 0.1011 | 0.21522 | -0.085952 | 0.092622 | 0.69632 | -0.0243 | 122.0281 | 122.3036 | 122.1969 | -0.15499 | 0.010178 | -122.1982 | 0.074286 | 0.083142 | 0.072964 | -122.1905 | -122.0763 | -0.058861 | -0.26342 | 0.18875 | 0.07183 | 0.13069 | 0.012036 | -0.094649 | 0.18946 | 0.19722 | 0.31135 | 0.12501 | -122.3775 | 122.1243 | 122.3997 | 122.293 | 0.79245 | -122.4466
3752.3281 | 122.3419 | -0.11444 | 122.3053 | -0.01778 | -0.053957 | 0.039011 | 0.019041 | -0.013574 | -0.0035853 | -0.021518 | -0.002694 | -0.0022903 | 0.057832 | 0.048166 | 0.047046 | -0.012688 | 0.0243 | -0.003831 | 0.084176 | 0.11025 | 0.21522 | -0.090531 | 0.097201 | 0.7009 | -0.0243 | 122.0281 | 122.3036 | 122.2061 | -0.15499 | 0.02391 | -122.2211 | 0.10175 | 0.11061 | 0.0867 | -122.195 | -122.0901 | -0.04055 | -0.27715 | 0.21164 | 0.090141 | 0.13069 | -0.001697 | -0.099225 | 0.19862 | 0.22469 | 0.32966 | 0.13874 | -122.3958 | 122.1426 | 122.418 | 122.3205 | 0.81534 | -122.4603
3754.0938 | 122.4747 | -0.045776 | 122.2137 | -0.010149 | -0.053743 | 0.039225 | 0.018614 | -0.013574 | -0.0037989 | -0.021518 | -0.0022666 | -0.0022903 | 0.057619 | 0.04838 | 0.047046 | -0.017266 | 0.015142 | -0.003831 | 0.088755 | 0.10567 | 0.21064 | -0.081373 | 0.092622 | 0.69632 | -0.028879 | 122.0373 | 122.299 | 122.1969 | -0.15041 | -0.035597 | -122.125 | 0.02851 | 0.041945 | 0.077542 | -122.1081 | -122.0031 | -0.10464 | -0.17644 | 0.1384 | 0.016897 | 0.12153 | 0.085278 | -0.016829 | 0.13453 | 0.15145 | 0.25642 | 0.060918 | -122.2951 | 122.0831 | 122.3448 | 122.2427 | 0.7421 | -122.3642
3755.7969 | 122.4197 | -0.059509 | 122.2687 | -0.025411 | -0.053743 | 0.039225 | 0.019041 | -0.013147 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.057405 | 0.047952 | 0.04726 | -0.012688 | 0.0243 | -0.003831 | 0.084176 | 0.11483 | 0.21522 | -0.085952 | 0.092622 | 0.69632 | -0.0243 | 122.019 | 122.3036 | 122.1923 | -0.14583 | -0.026443 | -122.1845 | 0.046821 | 0.055678 | 0.082121 | -122.1538 | -122.0535 | -0.086324 | -0.24968 | 0.15213 | 0.035209 | 0.12153 | 0.034924 | -0.07634 | 0.14369 | 0.17434 | 0.27473 | 0.083809 | -122.3546 | 122.0785 | 122.3631 | 122.2518 | 0.75583 | -122.4145
3757.5469 | 122.4106 | -0.064087 | 122.2321 | -0.01778 | -0.053743 | 0.039011 | 0.018828 | -0.01336 | -0.0037989 | -0.029148 | -0.0024804 | -0.0020767 | 0.057405 | 0.047952 | 0.046833 | -0.017266 | 0.0243 | -0.003831 | 0.084176 | 0.11025 | 0.2198 | -0.090531 | 0.097201 | 0.7009 | -0.033458 | 122.0327 | 122.3036 | 122.1969 | -0.15957 | -0.026444 | -122.1479 | 0.046821 | 0.060256 | 0.0867 | -122.1218 | -122.0123 | -0.095483 | -0.19933 | 0.16129 | 0.030629 | 0.12611 | 0.071545 | -0.03514 | 0.14826 | 0.17434 | 0.28389 | 0.088387 | -122.3226 | 122.0968 | 122.3677 | 122.261 | 0.76499 | -122.3916
3759.3125 | 122.3602 | -0.091553 | 122.287 | -0.010149 | -0.053957 | 0.039225 | 0.019041 | -0.01336 | -0.0037989 | -0.013887 | -0.0022666 | -0.0020767 | 0.057619 | 0.048166 | 0.046833 | -0.021844 | 0.019721 | -0.008409 | 0.093333 | 0.11025 | 0.21522 | -0.085952 | 0.097201 | 0.7009 | -0.0243 | 122.0327 | 122.299 | 122.1969 | -0.15499 | 0.005601 | -122.1937 | 0.069709 | 0.083144 | 0.077543 | -122.1767 | -122.0718 | -0.063438 | -0.25426 | 0.18875 | 0.067253 | 0.13069 | 0.012036 | -0.090071 | 0.18489 | 0.20181 | 0.30678 | 0.11127 | -122.3729 | 122.1243 | 122.3906 | 122.2885 | 0.79246 | -122.442
3761.0781 | 122.4335 | -0.045776 | 122.2595 | -0.010149 | -0.053529 | 0.039225 | 0.018614 | -0.01336 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.04838 | 0.047046 | -0.021844 | 0.0243 | 0.000747 | 0.093333 | 0.11025 | 0.21064 | -0.081373 | 0.092622 | 0.69632 | -0.0243 | 122.0327 | 122.3036 | 122.1969 | -0.15499 | -0.035597 | -122.1662 | 0.023932 | 0.046523 | 0.08212 | -122.1493 | -122.0489 | -0.10921 | -0.22679 | 0.1384 | 0.021476 | 0.13069 | 0.04408 | -0.062605 | 0.13911 | 0.15603 | 0.25642 | 0.070076 | -122.3409 | 122.0785 | 122.3494 | 122.2427 | 0.7421 | -122.4145
3762.7969 | 122.4289 | -0.041199 | 122.2412 | -0.025411 | -0.053743 | 0.039225 | 0.0184 | -0.013574 | -0.0035853 | -0.021518 | -0.002053 | -0.0022903 | 0.057405 | 0.048166 | 0.046833 | -0.017266 | 0.019721 | -0.012988 | 0.088755 | 0.11483 | 0.21522 | -0.090531 | 0.088043 | 0.70548 | -0.033458 | 122.0281 | 122.299 | 122.1969 | -0.15957 | -0.049332 | -122.1525 | 0.023933 | 0.028211 | 0.077543 | -122.1264 | -122.026 | -0.11837 | -0.21306 | 0.12924 | 0.007741 | 0.12611 | 0.057812 | -0.044295 | 0.12995 | 0.15603 | 0.25642 | 0.06092 | -122.3317 | 122.0693 | 122.3402 | 122.2381 | 0.74668 | -122.4008
3764.5625 | 122.4243 | -0.059509 | 122.2733 | -0.025411 | -0.053957 | 0.039225 | 0.018614 | -0.013574 | -0.0037989 | -0.013887 | -0.0022666 | -0.0025041 | 0.057619 | 0.047952 | 0.047046 | -0.017266 | 0.019721 | 0.000747 | 0.088755 | 0.11025 | 0.21064 | -0.085952 | 0.088043 | 0.70548 | -0.033458 | 122.0281 | 122.3036 | 122.1923 | -0.15957 | -0.026443 | -122.1845 | 0.042243 | 0.060256 | 0.086699 | -122.163 | -122.0626 | -0.10006 | -0.2451 | 0.14755 | 0.026051 | 0.12611 | 0.030347 | -0.080917 | 0.14826 | 0.16976 | 0.27015 | 0.07923 | -122.3592 | 122.0877 | 122.3631 | 122.2518 | 0.76499 | -122.4328
3766.3125 | 122.4701 | -0.032043 | 122.2595 | -0.010149 | -0.053529 | 0.039225 | 0.018828 | -0.013574 | -0.0042263 | -0.029148 | -0.0029076 | -0.0022903 | 0.057405 | 0.047952 | 0.047046 | -0.017266 | 0.028878 | -0.003831 | 0.084176 | 0.11025 | 0.21064 | -0.090531 | 0.088043 | 0.70548 | -0.038036 | 122.0327 | 122.3128 | 122.1969 | -0.16415 | -0.058488 | -122.1753 | 0.014777 | 0.028212 | 0.0867 | -122.1493 | -122.0489 | -0.13211 | -0.22679 | 0.12009 | -0.005993 | 0.12611 | 0.053237 | -0.062605 | 0.11622 | 0.1423 | 0.24269 | 0.060921 | -122.3501 | 122.0648 | 122.3448 | 122.229 | 0.73752 | -122.4237
3768.0781 | 122.438 | -0.050354 | 122.2504 | -0.01778 | -0.053743 | 0.039011 | 0.018828 | -0.013574 | -0.0035853 | -0.021518 | -0.002694 | -0.0020767 | 0.057405 | 0.04838 | 0.046833 | -0.017266 | 0.0243 | -0.003831 | 0.07502 | 0.11025 | 0.21522 | -0.090531 | 0.083464 | 0.71006 | -0.033458 | 122.0327 | 122.3082 | 122.1969 | -0.15041 | -0.040177 | -122.1753 | 0.033088 | 0.046523 | 0.0867 | -122.1401 | -122.0351 | -0.10006 | -0.21764 | 0.13382 | 0.016896 | 0.11695 | 0.057814 | -0.05345 | 0.12537 | 0.16061 | 0.26558 | 0.074654 | -122.3409 | 122.0831 | 122.3585 | 122.2473 | 0.76041 | -122.4008
3769.8438 | 122.4152 | -0.073242 | 122.2458 | -0.010149 | -0.053743 | 0.039225 | 0.018828 | -0.013574 | -0.0037989 | -0.029148 | -0.0024804 | -0.0027177 | 0.057619 | 0.048166 | 0.047046 | -0.021844 | 0.028878 | -0.003831 | 0.070441 | 0.11483 | 0.21522 | -0.085952 | 0.092622 | 0.70548 | -0.0243 | 122.0236 | 122.3082 | 122.1969 | -0.15957 | -0.01271 | -122.1753 | 0.051398 | 0.069411 | 0.082121 | -122.131 | -122.0306 | -0.086328 | -0.22222 | 0.16586 | 0.048942 | 0.13527 | 0.062391 | -0.048873 | 0.14368 | 0.18807 | 0.28847 | 0.10212 | -122.3317 | 122.0968 | 122.3814 | 122.2702 | 0.77872 | -122.4054
3771.5469 | 122.3923 | -0.086975 | 122.2595 | -0.01778 | -0.053743 | 0.039011 | 0.019041 | -0.013574 | -0.0037989 | -0.029148 | -0.0022666 | -0.0020767 | 0.057405 | 0.04838 | 0.046833 | -0.017266 | 0.0243 | -0.003831 | 0.070441 | 0.10567 | 0.21522 | -0.085952 | 0.092622 | 0.7009 | -0.028879 | 122.019 | 122.3082 | 122.2015 | -0.15957 | 0.001023 | -122.1891 | 0.069709 | 0.083144 | 0.082121 | -122.1538 | -122.0443 | -0.072595 | -0.24053 | 0.1796 | 0.058096 | 0.13069 | 0.048659 | -0.058026 | 0.15742 | 0.19265 | 0.3022 | 0.11127 | -122.3455 | 122.106 | 122.3952 | 122.2885 | 0.78788 | -122.4191
3773.2969 | 122.3419 | -0.10529 | 122.2916 | -0.01778 | -0.053743 | 0.039225 | 0.018828 | -0.013574 | -0.0040125 | -0.021518 | -0.0022666 | -0.0022903 | 0.057191 | 0.048166 | 0.047046 | -0.021844 | 0.028878 | -0.008409 | 0.07502 | 0.11483 | 0.21064 | -0.090531 | 0.092622 | 0.70548 | -0.033458 | 122.019 | 122.3082 | 122.2015 | -0.15957 | 0.014755 | -122.2165 | 0.083442 | 0.096877 | 0.082122 | -122.1767 | -122.0809 | -0.054284 | -0.27257 | 0.19791 | 0.071828 | 0.12611 | 0.016615 | -0.09007 | 0.18031 | 0.22012 | 0.31593 | 0.13416 | -122.3821 | 122.1243 | 122.4135 | 122.3068 | 0.81077 | -122.4511
3775.0469 | 122.4289 | -0.068665 | 122.2321 | -0.0025182 | -0.053529 | 0.038798 | 0.019041 | -0.013574 | -0.0040125 | -0.029148 | -0.002053 | -0.0022903 | 0.057405 | 0.048593 | 0.047046 | -0.012688 | 0.028878 | -0.008409 | 0.065863 | 0.11025 | 0.20607 | -0.09511 | 0.092622 | 0.71006 | -0.0243 | 122.0281 | 122.3036 | 122.1923 | -0.15957 | -0.026445 | -122.1662 | 0.055977 | 0.060256 | 0.086701 | -122.1218 | -122.026 | -0.090905 | -0.20391 | 0.16129 | 0.044365 | 0.13527 | 0.071545 | -0.039719 | 0.13453 | 0.17892 | 0.27473 | 0.097543 | -122.3272 | 122.0968 | 122.3723 | 122.261 | 0.77872 | -122.3916
3776.75 | 122.4518 | -0.050354 | 122.2641 | -0.01778 | -0.053743 | 0.039225 | 0.018614 | -0.013574 | -0.0040125 | -0.021518 | -0.002694 | -0.0018631 | 0.057405 | 0.047739 | 0.047046 | -0.012688 | 0.028878 | -0.008409 | 0.070441 | 0.11483 | 0.21064 | -0.085952 | 0.097201 | 0.71464 | -0.0243 | 122.0327 | 122.299 | 122.1923 | -0.15957 | -0.035598 | -122.1937 | 0.037666 | 0.041945 | 0.077543 | -122.1493 | -122.0535 | -0.10922 | -0.23137 | 0.14755 | 0.026054 | 0.13527 | 0.034924 | -0.071762 | 0.1208 | 0.16519 | 0.261 | 0.079232 | -122.3501 | 122.0831 | 122.3494 | 122.2427 | 0.76499 | -122.4237
3778.5 | 122.3923 | -0.09613 | 122.2778 | -0.0025182 | -0.053957 | 0.039225 | 0.019041 | -0.013574 | -0.0037989 | -0.021518 | -0.002694 | -0.0025041 | 0.057405 | 0.047952 | 0.047046 | -0.017266 | 0.033457 | -0.008409 | 0.07502 | 0.10567 | 0.21522 | -0.085952 | 0.088043 | 0.71464 | -0.033458 | 122.0236 | 122.3082 | 122.1923 | -0.15957 | 0.010178 | -122.2028 | 0.078864 | 0.087721 | 0.077543 | -122.1722 | -122.0626 | -0.06344 | -0.25426 | 0.18417 | 0.062672 | 0.12611 | 0.030348 | -0.085495 | 0.17115 | 0.2018 | 0.31135 | 0.12959 | -122.3638 | 122.1197 | 122.4043 | 122.2885 | 0.81077 | -122.4374
3780.2656 | 122.4106 | -0.082397 | 122.3007 | -0.010149 | -0.053743 | 0.039439 | 0.019041 | -0.013574 | -0.0040125 | -0.013887 | -0.0022666 | -0.0020767 | 0.057405 | 0.048166 | 0.047046 | -0.017266 | 0.028878 | -0.003831 | 0.070441 | 0.11025 | 0.21522 | -0.085952 | 0.092622 | 0.70548 | -0.028879 | 122.0281 | 122.3082 | 122.2061 | -0.15957 | -0.003555 | -122.2303 | 0.065131 | 0.078566 | 0.082121 | -122.1905 | -122.0855 | -0.077173 | -0.27257 | 0.17502 | 0.053518 | 0.13069 | 0.00746 | -0.094647 | 0.15284 | 0.19265 | 0.29762 | 0.11127 | -122.3867 | 122.1105 | 122.3906 | 122.2885 | 0.78788 | -122.4603
3781.9844 | 122.3785 | -0.10529 | 122.287 | -0.010149 | -0.053529 | 0.039225 | 0.018828 | -0.013574 | -0.0037989 | -0.021518 | -0.002694 | -0.0025041 | 0.057619 | 0.047952 | 0.046619 | -0.017266 | 0.033457 | -0.003831 | 0.07502 | 0.11025 | 0.21064 | -0.090531 | 0.092622 | 0.70548 | -0.028879 | 122.0327 | 122.3036 | 122.1969 | -0.16415 | 0.014755 | -122.212 | 0.08802 | 0.10146 | 0.0867 | -122.1767 | -122.0763 | -0.058863 | -0.25426 | 0.19791 | 0.076407 | 0.13527 | 0.016614 | -0.090071 | 0.18031 | 0.21554 | 0.31593 | 0.13874 | -122.3775 | 122.138 | 122.4089 | 122.3022 | 0.81077 | -122.4511
3783.75 | 122.3282 | -0.091553 | 122.3053 | -0.01778 | -0.053743 | 0.039225 | 0.018828 | -0.013574 | -0.0035853 | -0.021518 | -0.002694 | -0.0020767 | 0.057619 | 0.047952 | 0.046833 | -0.017266 | 0.028878 | 0.000747 | 0.07502 | 0.11025 | 0.21522 | -0.090531 | 0.088043 | 0.71464 | -0.028879 | 122.0236 | 122.3082 | 122.1969 | -0.15499 | 0.001022 | -122.2303 | 0.074287 | 0.0923 | 0.091278 | -122.195 | -122.0901 | -0.063438 | -0.28173 | 0.1796 | 0.062674 | 0.12611 | 0.002882 | -0.10838 | 0.16657 | 0.20181 | 0.30678 | 0.12043 | -122.3958 | 122.1151 | 122.3997 | 122.2885 | 0.80619 | -122.4603
3785.5312 | 122.4655 | -0.054932 | 122.2641 | -0.010149 | -0.053957 | 0.039652 | 0.018828 | -0.013574 | -0.0040125 | -0.0062567 | -0.0022666 | -0.0022903 | 0.057619 | 0.048593 | 0.046833 | -0.017266 | 0.019721 | -0.012988 | 0.070441 | 0.11025 | 0.21064 | -0.090531 | 0.088043 | 0.71464 | -0.028879 | 122.0281 | 122.3036 | 122.1923 | -0.16415 | -0.035599 | -122.1937 | 0.037666 | 0.041944 | 0.077543 | -122.1538 | -122.0535 | -0.10922 | -0.23595 | 0.14297 | 0.026053 | 0.13527 | 0.039502 | -0.071762 | 0.12537 | 0.16518 | 0.26558 | 0.074653 | -122.3546 | 122.0831 | 122.3585 | 122.2473 | 0.76957 | -122.4282
3787.2812 | 122.4701 | -0.045776 | 122.2733 | -0.010149 | -0.054171 | 0.039439 | 0.018828 | -0.01336 | -0.0035853 | -0.029148 | -0.002694 | -0.0020767 | 0.057619 | 0.048593 | 0.047046 | -0.012688 | 0.033457 | -0.008409 | 0.065863 | 0.11025 | 0.21522 | -0.090531 | 0.092622 | 0.72379 | -0.028879 | 122.0327 | 122.299 | 122.2015 | -0.16415 | -0.044755 | -122.2074 | 0.033088 | 0.037367 | 0.082122 | -122.163 | -122.058 | -0.11837 | -0.24053 | 0.1384 | 0.016897 | 0.13527 | 0.025769 | -0.071759 | 0.11164 | 0.15603 | 0.261 | 0.079233 | -122.3638 | 122.0785 | 122.3448 | 122.2473 | 0.76957 | -122.4374
3788.9844 | 122.4014 | -0.068665 | 122.2549 | -0.01778 | -0.053743 | 0.039439 | 0.018614 | -0.01336 | -0.0035853 | -0.029148 | -0.0022666 | -0.0022903 | 0.057619 | 0.048166 | 0.04726 | -0.017266 | 0.0243 | -0.008409 | 0.070441 | 0.11941 | 0.20607 | -0.090531 | 0.097201 | 0.71922 | -0.0243 | 122.0327 | 122.3036 | 122.1969 | -0.15499 | -0.021866 | -122.1845 | 0.051399 | 0.060256 | 0.082122 | -122.1355 | -122.0489 | -0.086326 | -0.22222 | 0.16587 | 0.044365 | 0.13069 | 0.048657 | -0.058028 | 0.13911 | 0.18808 | 0.27473 | 0.092965 | -122.3455 | 122.1014 | 122.3723 | 122.2656 | 0.78788 | -122.4099
3790.75 | 122.3511 | -0.10071 | 122.2916 | -0.01778 | -0.054171 | 0.039225 | 0.018828 | -0.013788 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.057832 | 0.048166 | 0.046833 | -0.021844 | 0.028878 | -0.008409 | 0.070441 | 0.11025 | 0.21064 | -0.085952 | 0.092622 | 0.71464 | -0.033458 | 122.0281 | 122.3082 | 122.1969 | -0.16415 | 0.014756 | -122.2211 | 0.078864 | 0.092299 | 0.077543 | -122.1813 | -122.0809 | -0.063441 | -0.26342 | 0.19333 | 0.06725 | 0.13069 | 0.016615 | -0.094649 | 0.17115 | 0.21096 | 0.31135 | 0.12959 | -122.3775 | 122.1289 | 122.4089 | 122.2976 | 0.81535 | -122.4557
3792.4531 | 122.3511 | -0.086975 | 122.2961 | -0.010149 | -0.053957 | 0.039439 | 0.018828 | -0.01336 | -0.0040125 | -0.013887 | -0.0022666 | -0.0020767 | 0.057405 | 0.04838 | 0.047046 | -0.026423 | 0.0243 | -0.012988 | 0.065863 | 0.10567 | 0.21064 | -0.090531 | 0.092622 | 0.71464 | -0.028879 | 122.0327 | 122.3036 | 122.2015 | -0.16415 | -0.003556 | -122.2303 | 0.060552 | 0.073987 | 0.077543 | -122.1905 | -122.0855 | -0.077174 | -0.26342 | 0.1796 | 0.058096 | 0.13527 | 0.007458 | -0.094648 | 0.15284 | 0.19265 | 0.29762 | 0.11127 | -122.3867 | 122.1197 | 122.3906 | 122.2885 | 0.80161 | -122.4603
3794.2031 | 122.3419 | -0.10529 | 122.2778 | -0.010149 | -0.053743 | 0.039011 | 0.018614 | -0.01336 | -0.0040125 | -0.021518 | -0.0022666 | -0.0022903 | 0.057405 | 0.04838 | 0.047046 | -0.021844 | 0.033457 | -0.008409 | 0.070441 | 0.10567 | 0.2198 | -0.090531 | 0.088043 | 0.71922 | -0.028879 | 122.0327 | 122.3082 | 122.2015 | -0.15499 | 0.014755 | -122.2074 | 0.083442 | 0.096877 | 0.082122 | -122.1722 | -122.058 | -0.049705 | -0.24511 | 0.19333 | 0.076407 | 0.12611 | 0.030348 | -0.076337 | 0.17573 | 0.21096 | 0.32509 | 0.13874 | -122.3684 | 122.138 | 122.4135 | 122.3068 | 0.8245 | -122.4328
3795.9531 | 122.3373 | -0.091553 | 122.3007 | -0.010149 | -0.054171 | 0.039225 | 0.018614 | -0.013574 | -0.0033715 | -0.0062567 | -0.002053 | -0.0022903 | 0.057405 | 0.048166 | 0.04726 | -0.012688 | 0.0243 | -0.003831 | 0.07502 | 0.11483 | 0.20607 | -0.090531 | 0.092622 | 0.72379 | -0.028879 | 122.0236 | 122.3082 | 122.1969 | -0.15957 | 0.001022 | -122.2257 | 0.078865 | 0.087722 | 0.0867 | -122.1859 | -122.0947 | -0.068017 | -0.27715 | 0.18417 | 0.062674 | 0.13069 | 0.00746 | -0.1038 | 0.16657 | 0.20638 | 0.29762 | 0.11585 | -122.3913 | 122.1151 | 122.3997 | 122.2885 | 0.81535 | -122.4603
3797.7031 | 122.3511 | -0.10986 | 122.2778 | -0.0025182 | -0.053957 | 0.039225 | 0.018828 | -0.01336 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057619 | 0.04838 | 0.047046 | -0.021844 | 0.038035 | 0.000747 | 0.070441 | 0.11025 | 0.21064 | -0.085952 | 0.092622 | 0.71922 | -0.0243 | 122.0281 | 122.3036 | 122.2015 | -0.15499 | 0.023911 | -122.2074 | 0.088019 | 0.11061 | 0.086699 | -122.1676 | -122.0672 | -0.045128 | -0.24968 | 0.20248 | 0.085563 | 0.13069 | 0.025769 | -0.076337 | 0.1803 | 0.22012 | 0.32051 | 0.1479 | -122.3638 | 122.138 | 122.4135 | 122.3114 | 0.82908 | -122.4328
3799.3906 | 122.4152 | -0.059509 | 122.2458 | -0.0025182 | -0.053957 | 0.039225 | 0.018614 | -0.013574 | -0.0040125 | -0.021518 | -0.002053 | -0.0022903 | 0.057619 | 0.047952 | 0.046619 | -0.017266 | 0.028878 | -0.012988 | 0.07502 | 0.10567 | 0.21064 | -0.085952 | 0.083464 | 0.71922 | -0.028879 | 122.0281 | 122.299 | 122.1969 | -0.15957 | -0.026443 | -122.1708 | 0.042243 | 0.046521 | 0.072964 | -122.1401 | -122.0351 | -0.10006 | -0.21764 | 0.14297 | 0.03063 | 0.13069 | 0.053234 | -0.048873 | 0.13453 | 0.16518 | 0.27015 | 0.088387 | -122.3317 | 122.0877 | 122.3585 | 122.2564 | 0.77873 | -122.4054
3801.1562 | 122.3557 | -0.11902 | 122.287 | -0.01778 | -0.053957 | 0.038798 | 0.018828 | -0.013574 | -0.0040125 | -0.021518 | -0.002053 | -0.0027177 | 0.057619 | 0.048166 | 0.04726 | -0.021844 | 0.0243 | -0.003831 | 0.07502 | 0.11483 | 0.21064 | -0.090531 | 0.097201 | 0.71922 | -0.028879 | 122.0327 | 122.3036 | 122.1969 | -0.15041 | 0.028488 | -122.212 | 0.097175 | 0.11519 | 0.0867 | -122.1722 | -122.0763 | -0.031393 | -0.25426 | 0.21622 | 0.09014 | 0.12153 | 0.016614 | -0.090071 | 0.19404 | 0.23385 | 0.32966 | 0.14332 | -122.3775 | 122.1517 | 122.4226 | 122.3159 | 0.83823 | -122.4374
3802.9219 | 122.3694 | -0.082397 | 122.287 | -0.0025182 | -0.053743 | 0.039439 | 0.018614 | -0.013574 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057405 | 0.04838 | 0.04726 | -0.017266 | 0.019721 | -0.008409 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.092622 | 0.72837 | -0.028879 | 122.0327 | 122.3036 | 122.1969 | -0.15041 | -0.008134 | -122.212 | 0.065131 | 0.073988 | 0.082122 | -122.1722 | -122.0672 | -0.068015 | -0.25426 | 0.17502 | 0.053518 | 0.12153 | 0.016614 | -0.090071 | 0.15742 | 0.19723 | 0.3022 | 0.10212 | -122.3775 | 122.1151 | 122.386 | 122.2793 | 0.81077 | -122.4374
3804.6875 | 122.4197 | -0.068665 | 122.2321 | -0.010149 | -0.053957 | 0.039439 | 0.018614 | -0.013574 | -0.0040125 | -0.021518 | -0.002053 | -0.0020767 | 0.057405 | 0.048166 | 0.046833 | -0.012688 | 0.028878 | -0.008409 | 0.070441 | 0.11483 | 0.21064 | -0.085952 | 0.088043 | 0.72379 | -0.0243 | 122.0327 | 122.3036 | 122.2015 | -0.15957 | -0.017287 | -122.1616 | 0.055977 | 0.060256 | 0.077543 | -122.1172 | -122.0214 | -0.090905 | -0.19933 | 0.15671 | 0.044365 | 0.13527 | 0.071545 | -0.030561 | 0.13911 | 0.1835 | 0.27931 | 0.097543 | -122.318 | 122.1014 | 122.3723 | 122.2702 | 0.79246 | -122.3916
3806.4531 | 122.4701 | -0.045776 | 122.2275 | -0.01778 | -0.053957 | 0.039225 | 0.0184 | -0.013788 | -0.0037989 | -0.021518 | -0.002694 | -0.0020767 | 0.057832 | 0.048166 | 0.047046 | -0.017266 | 0.0243 | -0.003831 | 0.07502 | 0.11025 | 0.21064 | -0.081373 | 0.088043 | 0.71922 | -0.0243 | 122.0281 | 122.3036 | 122.2015 | -0.15957 | -0.035597 | -122.1525 | 0.02851 | 0.041945 | 0.077542 | -122.1172 | -122.0168 | -0.11379 | -0.19933 | 0.13382 | 0.021476 | 0.13527 | 0.076123 | -0.025983 | 0.1208 | 0.15603 | 0.25642 | 0.070076 | -122.3089 | 122.0739 | 122.3494 | 122.2473 | 0.76499 | -122.387
3808.2188 | 122.438 | -0.068665 | 122.2549 | -0.01778 | -0.054171 | 0.039439 | 0.018614 | -0.013788 | -0.0037989 | -0.013887 | -0.002053 | -0.0031451 | 0.057191 | 0.048166 | 0.046833 | -0.021844 | 0.028878 | -0.008409 | 0.070441 | 0.10567 | 0.21064 | -0.085952 | 0.097201 | 0.73753 | -0.0243 | 122.0236 | 122.3082 | 122.1969 | -0.15499 | -0.017287 | -122.1845 | 0.046821 | 0.060256 | 0.077543 | -122.1493 | -122.0443 | -0.086326 | -0.23137 | 0.16587 | 0.044365 | 0.13069 | 0.053236 | -0.058028 | 0.13911 | 0.17434 | 0.27931 | 0.097543 | -122.3409 | 122.0922 | 122.3768 | 122.2656 | 0.8062 | -122.4099
3809.9219 | 122.3602 | -0.086975 | 122.3053 | -0.0025182 | -0.053957 | 0.039225 | 0.018828 | -0.013574 | -0.0037989 | -0.0062567 | -0.0024804 | -0.0022903 | 0.057832 | 0.048807 | 0.046833 | -0.021844 | 0.019721 | -0.003831 | 0.070441 | 0.11025 | 0.21522 | -0.085952 | 0.088043 | 0.72379 | -0.028879 | 122.0281 | 122.3036 | 122.1969 | -0.15957 | 0.001023 | -122.2349 | 0.065131 | 0.083144 | 0.082121 | -122.195 | -122.0901 | -0.072595 | -0.27715 | 0.17502 | 0.058096 | 0.13069 | -0.001697 | -0.10838 | 0.15742 | 0.19723 | 0.3022 | 0.1067 | -122.3912 | 122.1151 | 122.3906 | 122.2839 | 0.81077 | -122.4649
3811.6875 | 122.4289 | -0.059509 | 122.2229 | -0.010149 | -0.053529 | 0.039225 | 0.018828 | -0.01336 | -0.0037989 | -0.029148 | -0.0022666 | -0.0025041 | 0.057405 | 0.048166 | 0.046833 | -0.021844 | 0.0243 | -0.003831 | 0.065863 | 0.11025 | 0.21522 | -0.090531 | 0.088043 | 0.73295 | -0.033458 | 122.0327 | 122.3036 | 122.1969 | -0.15041 | -0.031022 | -122.157 | 0.037665 | 0.055678 | 0.0867 | -122.1126 | -122.0077 | -0.090903 | -0.19017 | 0.14755 | 0.026051 | 0.11695 | 0.080701 | -0.025984 | 0.12537 | 0.16976 | 0.27473 | 0.083809 | -122.3134 | 122.0922 | 122.3631 | 122.2564 | 0.79246 | -122.3733
3813.4531 | 122.4701 | -0.059509 | 122.2321 | -0.0025182 | -0.053957 | 0.039011 | 0.0184 | -0.013574 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.057619 | 0.04838 | 0.046619 | -0.021844 | 0.0243 | -0.003831 | 0.065863 | 0.11025 | 0.21064 | -0.081373 | 0.092622 | 0.72837 | -0.0243 | 122.0281 | 122.3128 | 122.1969 | -0.15957 | -0.021864 | -122.1662 | 0.037665 | 0.055678 | 0.077542 | -122.1218 | -122.0214 | -0.10006 | -0.20391 | 0.15213 | 0.035209 | 0.13527 | 0.080702 | -0.03514 | 0.12537 | 0.16976 | 0.27015 | 0.083809 | -122.3134 | 122.0877 | 122.3723 | 122.2564 | 0.78788 | -122.3916
3815.1562 | 122.3648 | -0.073242 | 122.2961 | -0.01778 | -0.054171 | 0.039011 | 0.018614 | -0.013574 | -0.0042263 | -0.0062567 | -0.0024804 | -0.0025041 | 0.057619 | 0.048593 | 0.046833 | -0.021844 | 0.0243 | -0.003831 | 0.079598 | 0.11483 | 0.21522 | -0.081373 | 0.092622 | 0.72837 | -0.028879 | 122.0281 | 122.3128 | 122.2061 | -0.15499 | -0.008131 | -122.2165 | 0.051398 | 0.069411 | 0.077542 | -122.1813 | -122.0809 | -0.081749 | -0.26799 | 0.16586 | 0.044363 | 0.12611 | 0.016615 | -0.09007 | 0.15284 | 0.18807 | 0.28847 | 0.097542 | -122.3775 | 122.1014 | 122.386 | 122.2793 | 0.80162 | -122.4511
3816.9219 | 122.4838 | -0.064087 | 122.2321 | -0.010149 | -0.054384 | 0.039011 | 0.018828 | -0.01336 | -0.0033715 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.048593 | 0.046833 | -0.017266 | 0.028878 | -0.003831 | 0.07502 | 0.10567 | 0.22438 | -0.090531 | 0.088043 | 0.72837 | -0.028879 | 122.0281 | 122.3082 | 122.1969 | -0.15957 | -0.026444 | -122.157 | 0.046821 | 0.060256 | 0.0867 | -122.1264 | -122.0077 | -0.095483 | -0.20391 | 0.15213 | 0.035208 | 0.13069 | 0.076124 | -0.03514 | 0.13911 | 0.16976 | 0.28847 | 0.092965 | -122.3226 | 122.0922 | 122.3723 | 122.261 | 0.79246 | -122.3916
3818.6875 | 122.3648 | -0.091553 | 122.287 | -0.010149 | -0.054384 | 0.039225 | 0.018828 | -0.013574 | -0.0037989 | -0.013887 | -0.0024804 | -0.0020767 | 0.057832 | 0.04838 | 0.047046 | -0.017266 | 0.028878 | 0.000747 | 0.07502 | 0.10567 | 0.21522 | -0.090531 | 0.088043 | 0.72837 | -0.028879 | 122.0327 | 122.3128 | 122.2015 | -0.16873 | 0.001022 | -122.212 | 0.074287 | 0.0923 | 0.091278 | -122.1813 | -122.0718 | -0.077175 | -0.25426 | 0.1796 | 0.062674 | 0.13985 | 0.025771 | -0.085492 | 0.16657 | 0.19723 | 0.30678 | 0.12043 | -122.3775 | 122.1243 | 122.4043 | 122.293 | 0.81993 | -122.4557
3820.3906 | 122.3511 | -0.10071 | 122.2916 | -0.0025182 | -0.054171 | 0.039225 | 0.018614 | -0.01336 | -0.0037989 | -0.021518 | -0.0024804 | -0.0025041 | 0.057619 | 0.048807 | 0.046833 | -0.012688 | 0.0243 | -0.003831 | 0.070441 | 0.11025 | 0.21522 | -0.090531 | 0.092622 | 0.73753 | -0.0243 | 122.0327 | 122.3082 | 122.1969 | -0.16415 | 0.010177 | -122.2211 | 0.08802 | 0.096877 | 0.0867 | -122.1813 | -122.0763 | -0.063441 | -0.25884 | 0.19333 | 0.076408 | 0.13985 | 0.016615 | -0.094649 | 0.17115 | 0.21096 | 0.31593 | 0.12501 | -122.3821 | 122.1334 | 122.4089 | 122.2976 | 0.83824 | -122.4557
3822.1719 | 122.3328 | -0.082397 | 122.2733 | -0.010149 | -0.054384 | 0.039225 | 0.0184 | -0.013574 | -0.0037989 | -0.013887 | -0.0022666 | -0.0027177 | 0.057191 | 0.048593 | 0.046619 | -0.012688 | 0.019721 | -0.003831 | 0.079598 | 0.11941 | 0.20607 | -0.085952 | 0.097201 | 0.73295 | -0.019721 | 122.0281 | 122.3082 | 122.1969 | -0.16415 | -0.003555 | -122.1937 | 0.069709 | 0.078566 | 0.082121 | -122.1538 | -122.0672 | -0.081752 | -0.2451 | 0.1796 | 0.062676 | 0.14443 | 0.034926 | -0.076338 | 0.162 | 0.20181 | 0.28846 | 0.10212 | -122.3592 | 122.1105 | 122.3906 | 122.2793 | 0.81535 | -122.4374
3823.9375 | 122.3923 | -0.091553 | 122.2641 | -0.010149 | -0.054171 | 0.039225 | 0.018828 | -0.013788 | -0.0040125 | -0.029148 | -0.0022666 | -0.0018631 | 0.057619 | 0.048593 | 0.046833 | -0.012688 | 0.0243 | -0.003831 | 0.07502 | 0.11025 | 0.21522 | -0.085952 | 0.097201 | 0.73753 | -0.0243 | 122.0281 | 122.3082 | 122.2015 | -0.16415 | 0.005601 | -122.1891 | 0.078865 | 0.087722 | 0.082121 | -122.1538 | -122.0489 | -0.072596 | -0.23595 | 0.18875 | 0.067253 | 0.13985 | 0.044081 | -0.062604 | 0.16657 | 0.20181 | 0.30678 | 0.11585 | -122.3501 | 122.1197 | 122.3997 | 122.293 | 0.82908 | -122.4282
3825.7031 | 122.3557 | -0.10529 | 122.2687 | -0.010149 | -0.054171 | 0.039011 | 0.0184 | -0.013574 | -0.0040125 | -0.021518 | -0.0024804 | -0.0027177 | 0.057619 | 0.048166 | 0.047046 | -0.012688 | 0.0243 | 0.000747 | 0.070441 | 0.11941 | 0.21064 | -0.090531 | 0.092622 | 0.74211 | -0.038036 | 122.0327 | 122.3036 | 122.2015 | -0.15957 | 0.014755 | -122.1982 | 0.092598 | 0.10603 | 0.091278 | -122.1493 | -122.058 | -0.054284 | -0.23595 | 0.19791 | 0.06725 | 0.12153 | 0.034924 | -0.067182 | 0.17573 | 0.2247 | 0.31593 | 0.12959 | -122.3592 | 122.138 | 122.4089 | 122.3068 | 0.8474 | -122.4282
3827.4219 | 122.4106 | -0.07782 | 122.2916 | -0.010149 | -0.053957 | 0.039225 | 0.018614 | -0.013574 | -0.0037989 | -0.021518 | -0.002053 | -0.0022903 | 0.057405 | 0.048593 | 0.046833 | -0.017266 | 0.0243 | -0.003831 | 0.07502 | 0.11025 | 0.21522 | -0.090531 | 0.083464 | 0.73295 | -0.019721 | 122.0281 | 122.3082 | 122.2061 | -0.15499 | -0.012711 | -122.2165 | 0.060554 | 0.073989 | 0.0867 | -122.1813 | -122.0763 | -0.077171 | -0.26342 | 0.16128 | 0.058099 | 0.13527 | 0.016615 | -0.085492 | 0.15284 | 0.18807 | 0.29304 | 0.10212 | -122.3821 | 122.106 | 122.386 | 122.2839 | 0.81077 | -122.4466
3829.1875 | 122.3831 | -0.086975 | 122.2778 | -0.010149 | -0.054384 | 0.039225 | 0.018828 | -0.013574 | -0.0042263 | -0.013887 | -0.0024804 | -0.0020767 | 0.057191 | 0.047952 | 0.047046 | -0.017266 | 0.0243 | -0.003831 | 0.07502 | 0.11483 | 0.21064 | -0.081373 | 0.088043 | 0.73295 | -0.028879 | 122.0281 | 122.3082 | 122.2015 | -0.16415 | 0.005602 | -122.2028 | 0.069709 | 0.083144 | 0.077542 | -122.163 | -122.0672 | -0.077174 | -0.24968 | 0.17502 | 0.058096 | 0.13527 | 0.030348 | -0.076337 | 0.162 | 0.20181 | 0.29762 | 0.11127 | -122.3592 | 122.1151 | 122.3952 | 122.2885 | 0.81993 | -122.442
3830.9531 | 122.3969 | -0.082397 | 122.2733 | 0.0051128 | -0.054171 | 0.039225 | 0.018828 | -0.01336 | -0.0033715 | -0.013887 | -0.0022666 | -0.0022903 | 0.057619 | 0.047952 | 0.04726 | -0.021844 | 0.028878 | -0.003831 | 0.079598 | 0.11483 | 0.2198 | -0.085952 | 0.088043 | 0.73753 | -0.0243 | 122.0281 | 122.3128 | 122.1969 | -0.15957 | -0.003555 | -122.1937 | 0.060553 | 0.078566 | 0.082121 | -122.1584 | -122.0535 | -0.077173 | -0.2451 | 0.17044 | 0.058097 | 0.13527 | 0.039504 | -0.076338 | 0.162 | 0.19723 | 0.3022 | 0.11127 | -122.3592 | 122.1105 | 122.3952 | 122.2793 | 0.81993 | -122.4328
3832.7344 | 122.4197 | -0.059509 | 122.2549 | -0.01778 | -0.054598 | 0.039225 | 0.0184 | -0.013788 | -0.0042263 | -0.029148 | -0.0024804 | -0.0022903 | 0.057405 | 0.048807 | 0.046406 | -0.021844 | 0.028878 | 0.000747 | 0.070441 | 0.11025 | 0.21522 | -0.085952 | 0.088043 | 0.73753 | -0.0243 | 122.0281 | 122.3082 | 122.1969 | -0.16415 | -0.026443 | -122.1845 | 0.037665 | 0.060256 | 0.086699 | -122.1447 | -122.0397 | -0.10464 | -0.22679 | 0.14755 | 0.035209 | 0.13985 | 0.053236 | -0.058028 | 0.12995 | 0.16976 | 0.27473 | 0.088387 | -122.3409 | 122.0877 | 122.3677 | 122.2564 | 0.79704 | -122.4191
3834.5 | 122.3511 | -0.10071 | 122.2733 | -0.0025182 | -0.054384 | 0.039225 | 0.018614 | -0.013574 | -0.0042263 | -0.0062567 | -0.002053 | -0.0020767 | 0.057405 | 0.04838 | 0.046833 | -0.017266 | 0.0243 | -0.003831 | 0.07502 | 0.11025 | 0.21064 | -0.090531 | 0.088043 | 0.73753 | -0.028879 | 122.0281 | 122.3082 | 122.1923 | -0.16873 | 0.010177 | -122.1982 | 0.083442 | 0.096877 | 0.0867 | -122.163 | -122.0626 | -0.06802 | -0.2451 | 0.18875 | 0.071829 | 0.13985 | 0.034926 | -0.080917 | 0.17573 | 0.21096 | 0.31135 | 0.12501 | -122.3638 | 122.1289 | 122.4089 | 122.293 | 0.83824 | -122.442
3836.2656 | 122.3328 | -0.082397 | 122.2641 | -0.010149 | -0.054384 | 0.039225 | 0.018614 | -0.013788 | -0.0040125 | -0.021518 | -0.002694 | -0.0022903 | 0.057405 | 0.04838 | 0.046833 | -0.021844 | 0.0243 | 0.000747 | 0.079598 | 0.11483 | 0.21522 | -0.085952 | 0.088043 | 0.75127 | -0.028879 | 122.0236 | 122.3128 | 122.2015 | -0.15957 | -0.003555 | -122.1845 | 0.060553 | 0.083144 | 0.086699 | -122.1493 | -122.0489 | -0.077173 | -0.24053 | 0.17044 | 0.053518 | 0.13069 | 0.048659 | -0.062604 | 0.162 | 0.19723 | 0.29762 | 0.1067 | -122.3501 | 122.106 | 122.3952 | 122.2839 | 0.83366 | -122.4237
3838.0312 | 122.5021 | -0.054932 | 122.2595 | -0.010149 | -0.053957 | 0.039225 | 0.018614 | -0.013147 | -0.0040125 | -0.029148 | -0.0022666 | -0.0022903 | 0.057619 | 0.048593 | 0.047046 | -0.017266 | 0.019721 | -0.003831 | 0.065863 | 0.10567 | 0.21064 | -0.09511 | 0.092622 | 0.74669 | -0.0243 | 122.0236 | 122.3036 | 122.1969 | -0.15957 | -0.040178 | -122.1937 | 0.037666 | 0.051101 | 0.091279 | -122.1538 | -122.0489 | -0.10464 | -0.23595 | 0.14755 | 0.030632 | 0.13527 | 0.04408 | -0.062605 | 0.1208 | 0.16061 | 0.26558 | 0.074653 | -122.3546 | 122.0785 | 122.3585 | 122.2518 | 0.80162 | -122.4191
3839.7344 | 122.4747 | -0.045776 | 122.2412 | -0.01778 | -0.054384 | 0.039439 | 0.018187 | -0.013788 | -0.0035853 | -0.021518 | -0.002694 | -0.0022903 | 0.057619 | 0.048593 | 0.046833 | -0.012688 | 0.019721 | -0.003831 | 0.07502 | 0.11483 | 0.2198 | -0.081373 | 0.088043 | 0.75127 | -0.028879 | 122.0281 | 122.3036 | 122.2015 | -0.15957 | -0.035597 | -122.1662 | 0.033088 | 0.041945 | 0.077542 | -122.1264 | -122.0214 | -0.11379 | -0.21306 | 0.13382 | 0.016897 | 0.13069 | 0.06239 | -0.039716 | 0.1208 | 0.16061 | 0.26558 | 0.065497 | -122.3226 | 122.0739 | 122.3494 | 122.2473 | 0.79704 | -122.4008
3841.4844 | 122.4243 | -0.068665 | 122.2458 | -0.010149 | -0.054171 | 0.039225 | 0.018828 | -0.013574 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.049021 | 0.046833 | -0.017266 | 0.0243 | 0.000747 | 0.079598 | 0.11483 | 0.2198 | -0.081373 | 0.092622 | 0.74211 | -0.028879 | 122.0373 | 122.3173 | 122.1969 | -0.16415 | -0.012708 | -122.1662 | 0.051399 | 0.069412 | 0.08212 | -122.131 | -122.026 | -0.095484 | -0.20848 | 0.16129 | 0.039786 | 0.13527 | 0.071548 | -0.048873 | 0.14826 | 0.1835 | 0.28847 | 0.092965 | -122.3272 | 122.106 | 122.386 | 122.2656 | 0.81078 | -122.4099
3843.25 | 122.4335 | -0.064087 | 122.2275 | -0.010149 | -0.054598 | 0.039439 | 0.0184 | -0.013574 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.048166 | 0.046619 | -0.026423 | 0.033457 | -0.003831 | 0.07502 | 0.11025 | 0.21522 | -0.09511 | 0.083464 | 0.75127 | -0.033458 | 122.0236 | 122.3128 | 122.2061 | -0.16873 | -0.031023 | -122.1525 | 0.037664 | 0.060256 | 0.091279 | -122.1172 | -122.0123 | -0.10464 | -0.20391 | 0.14755 | 0.030629 | 0.13527 | 0.08528 | -0.021405 | 0.13911 | 0.17434 | 0.27931 | 0.097544 | -122.3226 | 122.0877 | 122.3768 | 122.2702 | 0.81535 | -122.3962
3845.0156 | 122.3923 | -0.07782 | 122.2687 | 0.0051128 | -0.054171 | 0.039011 | 0.018614 | -0.013788 | -0.0033715 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.048593 | 0.046619 | -0.017266 | 0.028878 | -0.003831 | 0.07502 | 0.11025 | 0.2198 | -0.090531 | 0.092622 | 0.75127 | -0.0243 | 122.0373 | 122.3082 | 122.1969 | -0.16415 | -0.012711 | -122.1937 | 0.060554 | 0.073989 | 0.0867 | -122.1584 | -122.0489 | -0.086329 | -0.23137 | 0.17044 | 0.05352 | 0.13985 | 0.039503 | -0.071761 | 0.15284 | 0.18807 | 0.29762 | 0.1067 | -122.3592 | 122.1151 | 122.386 | 122.2747 | 0.82909 | -122.4328
3846.7188 | 122.3877 | -0.091553 | 122.2824 | -0.01778 | -0.054598 | 0.039439 | 0.018828 | -0.013788 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.048593 | 0.046833 | -0.017266 | 0.019721 | -0.003831 | 0.065863 | 0.11025 | 0.21522 | -0.085952 | 0.092622 | 0.74669 | -0.033458 | 122.0327 | 122.3128 | 122.2015 | -0.16415 | 0.005601 | -122.2165 | 0.074287 | 0.087722 | 0.082121 | -122.1722 | -122.0672 | -0.072596 | -0.24968 | 0.18417 | 0.058095 | 0.13069 | 0.030348 | -0.080915 | 0.15742 | 0.20181 | 0.30678 | 0.11127 | -122.3684 | 122.1243 | 122.4043 | 122.293 | 0.83824 | -122.4466
3848.4844 | 122.4472 | -0.059509 | 122.2778 | -0.010149 | -0.054384 | 0.039225 | 0.018614 | -0.013574 | -0.0035853 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.047952 | 0.046833 | -0.017266 | 0.033457 | -0.003831 | 0.07502 | 0.11483 | 0.2198 | -0.085952 | 0.083464 | 0.75585 | -0.033458 | 122.0327 | 122.3128 | 122.1969 | -0.16415 | -0.026443 | -122.2028 | 0.042243 | 0.055678 | 0.082121 | -122.163 | -122.058 | -0.10464 | -0.24511 | 0.14297 | 0.026051 | 0.13069 | 0.034926 | -0.080916 | 0.13453 | 0.17434 | 0.27931 | 0.092966 | -122.3638 | 122.0922 | 122.3723 | 122.2564 | 0.81536 | -122.442
3850.1719 | 122.3602 | -0.10071 | 122.2916 | -0.010149 | -0.054171 | 0.039011 | 0.0184 | -0.013574 | -0.0040125 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.048593 | 0.047046 | -0.017266 | 0.0243 | -0.003831 | 0.079598 | 0.11483 | 0.2198 | -0.090531 | 0.097201 | 0.75585 | -0.028879 | 122.0373 | 122.3082 | 122.1969 | -0.16415 | 0.010177 | -122.212 | 0.083442 | 0.096877 | 0.0867 | -122.1767 | -122.0718 | -0.063441 | -0.25426 | 0.19791 | 0.071829 | 0.13527 | 0.016615 | -0.094649 | 0.18031 | 0.21554 | 0.32051 | 0.12501 | -122.3821 | 122.138 | 122.4089 | 122.2976 | 0.85655 | -122.4557
3851.9375 | 122.3923 | -0.091553 | 122.2916 | -0.010149 | -0.054171 | 0.039011 | 0.018614 | -0.013574 | -0.0035853 | -0.013887 | -0.0022666 | -0.0022903 | 0.057619 | 0.048593 | 0.046619 | -0.012688 | 0.0243 | -0.003831 | 0.07502 | 0.11025 | 0.21522 | -0.090531 | 0.088043 | 0.75127 | -0.028879 | 122.0281 | 122.3173 | 122.2015 | -0.15957 | 0.001022 | -122.2165 | 0.078865 | 0.087722 | 0.0867 | -122.1813 | -122.0763 | -0.068017 | -0.26342 | 0.1796 | 0.062674 | 0.13069 | 0.025772 | -0.09007 | 0.16657 | 0.20181 | 0.30678 | 0.11585 | -122.3821 | 122.1197 | 122.4089 | 122.293 | 0.84282 | -122.4511
3853.7031 | 122.438 | -0.068665 | 122.2824 | -0.010149 | -0.054384 | 0.039439 | 0.018614 | -0.013788 | -0.0042263 | -0.021518 | -0.002694 | -0.0022903 | 0.057619 | 0.048593 | 0.047046 | -0.012688 | 0.033457 | -0.003831 | 0.065863 | 0.11025 | 0.2198 | -0.081373 | 0.092622 | 0.75585 | -0.033458 | 122.0327 | 122.3082 | 122.1969 | -0.16415 | -0.012708 | -122.2165 | 0.055977 | 0.064834 | 0.077542 | -122.1722 | -122.0626 | -0.095484 | -0.24968 | 0.16129 | 0.035207 | 0.13069 | 0.02577 | -0.085494 | 0.13453 | 0.17892 | 0.28847 | 0.10212 | -122.3638 | 122.1014 | 122.3768 | 122.2656 | 0.82451 | -122.4466
3855.4531 | 122.3923 | -0.09613 | 122.2687 | -0.0025182 | -0.054171 | 0.039011 | 0.0184 | -0.013788 | -0.0037989 | -0.013887 | -0.0024804 | -0.0025041 | 0.057405 | 0.048593 | 0.046833 | -0.021844 | 0.019721 | 0.005325 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.092622 | 0.75585 | -0.019721 | 122.0281 | 122.3128 | 122.1969 | -0.15957 | 0.005599 | -122.1937 | 0.074286 | 0.10145 | 0.095856 | -122.1538 | -122.0489 | -0.06344 | -0.24053 | 0.18875 | 0.076409 | 0.13985 | 0.044081 | -0.071761 | 0.17115 | 0.21096 | 0.31593 | 0.11585 | -122.3592 | 122.1243 | 122.4089 | 122.293 | 0.85198 | -122.4282
3857.1719 | 122.3831 | -0.086975 | 122.2824 | -0.0025182 | -0.054384 | 0.039225 | 0.0184 | -0.014001 | -0.0037989 | -0.0062567 | -0.0022666 | -0.0020767 | 0.057619 | 0.04838 | 0.046619 | -0.017266 | 0.0243 | 0.000747 | 0.070441 | 0.11483 | 0.22438 | -0.090531 | 0.092622 | 0.76043 | -0.019721 | 122.0236 | 122.3082 | 122.2015 | -0.16415 | -0.003556 | -122.212 | 0.069709 | 0.087722 | 0.091278 | -122.1676 | -122.058 | -0.077174 | -0.25884 | 0.1796 | 0.067254 | 0.14443 | 0.02577 | -0.080915 | 0.15742 | 0.20181 | 0.31136 | 0.11127 | -122.3729 | 122.1105 | 122.3952 | 122.2885 | 0.8474 | -122.4466
3858.9375 | 122.4289 | -0.064087 | 122.2366 | -0.01778 | -0.054812 | 0.039439 | 0.018614 | -0.013788 | -0.0040125 | -0.021518 | -0.0024804 | -0.0020767 | 0.057619 | 0.048807 | 0.046833 | -0.017266 | 0.028878 | 0.000747 | 0.07502 | 0.11483 | 0.21522 | -0.090531 | 0.097201 | 0.76043 | -0.033458 | 122.0281 | 122.3128 | 122.2015 | -0.15499 | -0.026444 | -122.1616 | 0.046821 | 0.064834 | 0.091278 | -122.1218 | -122.0214 | -0.090904 | -0.20848 | 0.16129 | 0.030629 | 0.12153 | 0.076125 | -0.035138 | 0.13911 | 0.17892 | 0.27931 | 0.092965 | -122.3272 | 122.0922 | 122.3768 | 122.2656 | 0.82451 | -122.3916
3860.6875 | 122.4518 | -0.054932 | 122.2549 | -0.0025182 | -0.054598 | 0.039439 | 0.0184 | -0.013574 | -0.0040125 | -0.021518 | -0.0029076 | -0.0022903 | 0.057405 | 0.04838 | 0.046833 | -0.017266 | 0.019721 | -0.003831 | 0.070441 | 0.11483 | 0.21522 | -0.085952 | 0.088043 | 0.76958 | -0.0243 | 122.0281 | 122.3128 | 122.1923 | -0.16415 | -0.03102 | -122.1845 | 0.037666 | 0.051101 | 0.082121 | -122.1401 | -122.0397 | -0.10922 | -0.22679 | 0.14297 | 0.030632 | 0.13985 | 0.057814 | -0.062607 | 0.12537 | 0.16976 | 0.27016 | 0.074653 | -122.3409 | 122.0831 | 122.3677 | 122.2473 | 0.82451 | -122.4191
3862.3906 | 122.3511 | -0.11444 | 122.2778 | -0.01778 | -0.054598 | 0.039011 | 0.018828 | -0.013574 | -0.0037989 | -0.021518 | -0.0022666 | -0.0022903 | 0.057619 | 0.048166 | 0.047046 | -0.017266 | 0.028878 | -0.008409 | 0.07502 | 0.1011 | 0.21522 | -0.085952 | 0.092622 | 0.75585 | -0.0243 | 122.0373 | 122.3082 | 122.1969 | -0.15957 | 0.028489 | -122.2028 | 0.097175 | 0.10603 | 0.077543 | -122.1767 | -122.0626 | -0.045129 | -0.24053 | 0.20706 | 0.090141 | 0.13527 | 0.030348 | -0.080916 | 0.18946 | 0.21554 | 0.32966 | 0.14332 | -122.3638 | 122.1517 | 122.4226 | 122.3114 | 0.87029 | -122.4374
3864.1562 | 122.319 | -0.11902 | 122.2641 | -0.01778 | -0.054384 | 0.039439 | 0.0184 | -0.014001 | -0.0037989 | -0.021518 | -0.002053 | -0.0025041 | 0.057191 | 0.04838 | 0.046619 | -0.017266 | 0.028878 | -0.008409 | 0.07502 | 0.11483 | 0.21522 | -0.090531 | 0.092622 | 0.76958 | -0.028879 | 122.0281 | 122.3128 | 122.2015 | -0.15957 | 0.028488 | -122.1891 | 0.10175 | 0.11061 | 0.082122 | -122.1493 | -122.0489 | -0.040551 | -0.23595 | 0.21164 | 0.09014 | 0.13069 | 0.048659 | -0.062604 | 0.19404 | 0.23385 | 0.33424 | 0.1479 | -122.3546 | 122.1472 | 122.4318 | 122.3205 | 0.8886 | -122.4237
3865.8594 | 122.4197 | -0.068665 | 122.2549 | -0.01778 | -0.054598 | 0.039225 | 0.0184 | -0.013788 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057619 | 0.048807 | 0.046833 | -0.017266 | 0.028878 | -0.003831 | 0.07502 | 0.12399 | 0.2198 | -0.090531 | 0.083464 | 0.76043 | -0.0243 | 122.0327 | 122.3128 | 122.1878 | -0.16415 | -0.021866 | -122.1799 | 0.051399 | 0.064834 | 0.0867 | -122.131 | -122.0351 | -0.095484 | -0.22222 | 0.15213 | 0.044365 | 0.13985 | 0.057814 | -0.067185 | 0.14369 | 0.19266 | 0.28847 | 0.097543 | -122.3455 | 122.1014 | 122.3814 | 122.2564 | 0.82909 | -122.4191
3867.6406 | 122.4518 | -0.064087 | 122.2412 | -0.010149 | -0.054598 | 0.039439 | 0.018828 | -0.013574 | -0.0037989 | -0.013887 | -0.0022666 | -0.0025041 | 0.057405 | 0.049234 | 0.047046 | -0.017266 | 0.028878 | -0.003831 | 0.07502 | 0.11483 | 0.21064 | -0.090531 | 0.092622 | 0.765 | -0.028879 | 122.0281 | 122.3173 | 122.2015 | -0.16873 | -0.026444 | -122.1662 | 0.046821 | 0.060256 | 0.0867 | -122.1264 | -122.0306 | -0.10464 | -0.21306 | 0.15671 | 0.035208 | 0.13985 | 0.076126 | -0.039716 | 0.13911 | 0.17892 | 0.27473 | 0.092965 | -122.3317 | 122.0922 | 122.3814 | 122.2656 | 0.82909 | -122.4099
3869.4219 | 122.3465 | -0.10529 | 122.2687 | -0.01778 | -0.054171 | 0.039225 | 0.018187 | -0.013788 | -0.0037989 | -0.021518 | -0.0024804 | -0.0020767 | 0.057191 | 0.048807 | 0.047046 | -0.012688 | 0.019721 | -0.003831 | 0.07502 | 0.11941 | 0.2198 | -0.090531 | 0.097201 | 0.765 | -0.033458 | 122.0281 | 122.3082 | 122.2015 | -0.16415 | 0.014755 | -122.1937 | 0.092598 | 0.10146 | 0.0867 | -122.1493 | -122.0489 | -0.058863 | -0.24053 | 0.20249 | 0.071828 | 0.13069 | 0.039503 | -0.067182 | 0.18031 | 0.2247 | 0.32509 | 0.12501 | -122.3592 | 122.1334 | 122.4135 | 122.3068 | 0.87029 | -122.4328
3871.1875 | 122.4289 | -0.082397 | 122.2687 | -0.010149 | -0.054171 | 0.039011 | 0.0184 | -0.013788 | -0.0040125 | -0.013887 | -0.0024804 | -0.0020767 | 0.057619 | 0.048593 | 0.046833 | -0.021844 | 0.0243 | -0.003831 | 0.07502 | 0.10567 | 0.21522 | -0.081373 | 0.092622 | 0.76958 | -0.028879 | 122.0281 | 122.3128 | 122.1969 | -0.15957 | 0.001024 | -122.1937 | 0.060553 | 0.078566 | 0.077542 | -122.163 | -122.0535 | -0.077173 | -0.24053 | 0.17502 | 0.053518 | 0.13069 | 0.044081 | -0.071761 | 0.15742 | 0.18807 | 0.29762 | 0.1067 | -122.35 | 122.1105 | 122.3952 | 122.2793 | 0.85198 | -122.4282
3872.8906 | 122.3419 | -0.09613 | 122.2778 | -0.010149 | -0.054598 | 0.039225 | 0.0184 | -0.01336 | -0.0037989 | -0.0062567 | -0.0024804 | -0.0022903 | 0.057191 | 0.048593 | 0.047046 | -0.017266 | 0.028878 | 0.000747 | 0.07502 | 0.11025 | 0.21522 | -0.09511 | 0.097201 | 0.765 | -0.0243 | 122.0327 | 122.3219 | 122.2015 | -0.16415 | 0.00102 | -122.2028 | 0.078864 | 0.096877 | 0.095857 | -122.1676 | -122.0626 | -0.068019 | -0.24511 | 0.19333 | 0.07183 | 0.13985 | 0.044084 | -0.076337 | 0.17115 | 0.20638 | 0.31135 | 0.12501 | -122.3729 | 122.1289 | 122.418 | 122.2976 | 0.86113 | -122.442
3874.6406 | 122.3511 | -0.086975 | 122.2824 | -0.010149 | -0.054598 | 0.039439 | 0.0184 | -0.013788 | -0.0040125 | -0.036779 | -0.002053 | -0.0022903 | 0.057405 | 0.048593 | 0.047046 | -0.017266 | 0.028878 | -0.003831 | 0.070441 | 0.10567 | 0.21522 | -0.090531 | 0.088043 | 0.76958 | -0.0243 | 122.0327 | 122.3173 | 122.1969 | -0.16415 | -0.003556 | -122.212 | 0.069709 | 0.083144 | 0.0867 | -122.1767 | -122.0672 | -0.077174 | -0.24968 | 0.17502 | 0.062675 | 0.13985 | 0.034927 | -0.085494 | 0.15742 | 0.19265 | 0.3022 | 0.11585 | -122.3729 | 122.1197 | 122.4043 | 122.2839 | 0.85656 | -122.4466
3876.3281 | 122.4152 | -0.059509 | 122.2321 | -0.010149 | -0.054384 | 0.039225 | 0.0184 | -0.013788 | -0.0040125 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.048593 | 0.047046 | -0.026423 | 0.0243 | -0.008409 | 0.070441 | 0.11483 | 0.2198 | -0.085952 | 0.097201 | 0.77416 | -0.038036 | 122.0373 | 122.3173 | 122.1923 | -0.16415 | -0.026443 | -122.1616 | 0.033086 | 0.0511 | 0.077543 | -122.1172 | -122.0123 | -0.10464 | -0.19475 | 0.15671 | 0.021473 | 0.12611 | 0.085281 | -0.039719 | 0.12995 | 0.17434 | 0.27931 | 0.083809 | -122.318 | 122.0968 | 122.3768 | 122.2518 | 0.83367 | -122.3962
3878.0938 | 122.4564 | -0.07782 | 122.2458 | -0.010149 | -0.054384 | 0.039225 | 0.018614 | -0.014001 | -0.0042263 | -0.021518 | -0.002694 | -0.0022903 | 0.057405 | 0.04838 | 0.047046 | -0.026423 | 0.033457 | -0.003831 | 0.07502 | 0.11483 | 0.22438 | -0.09511 | 0.088043 | 0.76958 | -0.028879 | 122.0373 | 122.3082 | 122.2015 | -0.16415 | -0.01729 | -122.1708 | 0.051397 | 0.073989 | 0.091279 | -122.131 | -122.0214 | -0.086329 | -0.20848 | 0.16586 | 0.048941 | 0.13527 | 0.062391 | -0.044294 | 0.15284 | 0.19265 | 0.3022 | 0.11128 | -122.3409 | 122.1151 | 122.386 | 122.2793 | 0.8474 | -122.4099
3879.8438 | 122.4701 | -0.045776 | 122.2366 | -0.01778 | -0.054384 | 0.039225 | 0.0184 | -0.013788 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.057832 | 0.048593 | 0.046833 | -0.021844 | 0.033457 | -0.003831 | 0.07502 | 0.11483 | 0.2198 | -0.085952 | 0.088043 | 0.77416 | -0.028879 | 122.0327 | 122.3036 | 122.2015 | -0.16415 | -0.040176 | -122.1616 | 0.023932 | 0.041945 | 0.082121 | -122.1218 | -122.0168 | -0.11837 | -0.20391 | 0.13382 | 0.016897 | 0.13527 | 0.066968 | -0.035138 | 0.1208 | 0.16061 | 0.26558 | 0.079233 | -122.3226 | 122.0785 | 122.3494 | 122.2473 | 0.81994 | -122.4008
3881.5938 | 122.4655 | -0.059509 | 122.2366 | -0.01778 | -0.054171 | 0.039439 | 0.018614 | -0.014001 | -0.0040125 | -0.021518 | -0.002694 | -0.0022903 | 0.057619 | 0.048593 | 0.046833 | -0.012688 | 0.028878 | -0.003831 | 0.070441 | 0.11483 | 0.22438 | -0.085952 | 0.092622 | 0.77874 | -0.028879 | 122.0327 | 122.3173 | 122.1969 | -0.16415 | -0.026443 | -122.1662 | 0.046821 | 0.055678 | 0.082121 | -122.1218 | -122.0123 | -0.10464 | -0.20391 | 0.15213 | 0.03063 | 0.13527 | 0.080704 | -0.039717 | 0.12995 | 0.17434 | 0.28389 | 0.088387 | -122.3226 | 122.0922 | 122.3768 | 122.2564 | 0.83825 | -122.4008
3883.2969 | 122.4197 | -0.041199 | 122.2229 | -0.010149 | -0.054812 | 0.039225 | 0.0184 | -0.013574 | -0.0035853 | -0.021518 | -0.0024804 | -0.0020767 | 0.057405 | 0.048593 | 0.046833 | -0.021844 | 0.019721 | -0.003831 | 0.065863 | 0.10567 | 0.21522 | -0.09511 | 0.092622 | 0.77416 | -0.028879 | 122.0281 | 122.3128 | 122.2061 | -0.16415 | -0.053911 | -122.157 | 0.019355 | 0.037368 | 0.091279 | -122.1172 | -122.0077 | -0.12295 | -0.19475 | 0.13382 | 0.01232 | 0.13527 | 0.089858 | -0.016827 | 0.10706 | 0.14687 | 0.25642 | 0.06092 | -122.318 | 122.0693 | 122.354 | 122.2473 | 0.81536 | -122.387
3885.0469 | 122.3648 | -0.091553 | 122.2733 | -0.010149 | -0.054598 | 0.039225 | 0.018614 | -0.013574 | -0.0040125 | -0.021518 | -0.0022666 | -0.0020767 | 0.057191 | 0.048807 | 0.046619 | -0.021844 | 0.028878 | -0.008409 | 0.07502 | 0.11483 | 0.21522 | -0.085952 | 0.083464 | 0.76958 | -0.033458 | 122.0419 | 122.3173 | 122.2015 | -0.16873 | 0.005601 | -122.1982 | 0.069709 | 0.083144 | 0.077543 | -122.1584 | -122.058 | -0.077175 | -0.23137 | 0.17502 | 0.058095 | 0.13527 | 0.044083 | -0.071759 | 0.16657 | 0.20638 | 0.30678 | 0.12043 | -122.3592 | 122.1334 | 122.4089 | 122.293 | 0.86113 | -122.442
3886.8125 | 122.3282 | -0.10071 | 122.2778 | -0.0025182 | -0.054384 | 0.039225 | 0.018828 | -0.013574 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.04838 | 0.046619 | -0.021844 | 0.0243 | -0.012988 | 0.070441 | 0.11483 | 0.22438 | -0.090531 | 0.092622 | 0.77416 | -0.028879 | 122.0281 | 122.3128 | 122.2015 | -0.16415 | 0.010177 | -122.2074 | 0.078864 | 0.08772 | 0.077543 | -122.163 | -122.0535 | -0.063441 | -0.24968 | 0.19333 | 0.071829 | 0.13527 | 0.034926 | -0.076337 | 0.17115 | 0.21554 | 0.32509 | 0.12501 | -122.3684 | 122.1289 | 122.4135 | 122.3022 | 0.87487 | -122.442
3888.5781 | 122.3465 | -0.11444 | 122.2504 | 0.012744 | -0.054598 | 0.039225 | 0.0184 | -0.013788 | -0.0042263 | -0.021518 | -0.0024804 | -0.0020767 | 0.057191 | 0.048593 | 0.046833 | -0.012688 | 0.019721 | -0.003831 | 0.065863 | 0.11025 | 0.2198 | -0.085952 | 0.092622 | 0.77874 | -0.0243 | 122.0281 | 122.3082 | 122.1969 | -0.15957 | 0.028489 | -122.1845 | 0.10175 | 0.11061 | 0.082121 | -122.1401 | -122.0306 | -0.045129 | -0.22222 | 0.20706 | 0.090141 | 0.13527 | 0.057814 | -0.05345 | 0.1803 | 0.22469 | 0.33424 | 0.13416 | -122.3363 | 122.1426 | 122.4226 | 122.3114 | 0.89318 | -122.4099
3890.3438 | 122.4747 | -0.032043 | 122.2137 | -0.010149 | -0.054384 | 0.039225 | 0.018614 | -0.013574 | -0.0042263 | -0.036779 | -0.002694 | -0.0025041 | 0.057405 | 0.048593 | 0.047046 | -0.008109 | 0.028878 | -0.008409 | 0.070441 | 0.11025 | 0.2198 | -0.090531 | 0.092622 | 0.7879 | -0.033458 | 122.0327 | 122.3082 | 122.1969 | -0.16873 | -0.058488 | -122.1433 | 0.023934 | 0.023634 | 0.082122 | -122.1035 | -121.9939 | -0.13669 | -0.18102 | 0.12466 | -0.001415 | 0.13527 | 0.094435 | -0.016829 | 0.10248 | 0.1423 | 0.25184 | 0.060921 | -122.3043 | 122.0648 | 122.3402 | 122.229 | 0.81994 | -122.3825
3892.0469 | 122.4518 | -0.068665 | 122.2229 | -0.010149 | -0.054598 | 0.039439 | 0.018187 | -0.013788 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057191 | 0.048593 | 0.047046 | -0.017266 | 0.033457 | 0.000747 | 0.079598 | 0.11025 | 0.21522 | -0.090531 | 0.088043 | 0.79248 | -0.0243 | 122.0327 | 122.3128 | 122.1923 | -0.15957 | -0.021866 | -122.1433 | 0.051399 | 0.069412 | 0.091278 | -122.1126 | -122.0077 | -0.090905 | -0.19017 | 0.15671 | 0.044365 | 0.13527 | 0.089858 | -0.030563 | 0.14826 | 0.17892 | 0.28389 | 0.10212 | -122.3134 | 122.1014 | 122.3814 | 122.261 | 0.86114 | -122.3825
3893.75 | 122.438 | -0.068665 | 122.2366 | -0.01778 | -0.054598 | 0.039225 | 0.0184 | -0.013788 | -0.0037989 | -0.021518 | -0.0029076 | -0.0022903 | 0.056978 | 0.04838 | 0.046833 | -0.017266 | 0.019721 | -0.008409 | 0.070441 | 0.1011 | 0.21522 | -0.090531 | 0.092622 | 0.77874 | -0.0243 | 122.0419 | 122.3173 | 122.1923 | -0.15957 | -0.021866 | -122.1662 | 0.051399 | 0.060256 | 0.082122 | -122.1355 | -122.0214 | -0.090905 | -0.19475 | 0.16129 | 0.044365 | 0.13527 | 0.080704 | -0.044296 | 0.13911 | 0.16976 | 0.28389 | 0.088386 | -122.3272 | 122.1105 | 122.386 | 122.261 | 0.8474 | -122.3962
3895.5 | 122.3511 | -0.086975 | 122.2549 | -0.010149 | -0.054598 | 0.039439 | 0.0184 | -0.01336 | -0.0037989 | -0.029148 | -0.0024804 | -0.0022903 | 0.057405 | 0.048807 | 0.046833 | -0.008109 | 0.028878 | -0.017566 | 0.070441 | 0.11941 | 0.22438 | -0.090531 | 0.097201 | 0.7879 | -0.028879 | 122.0327 | 122.3082 | 122.1969 | -0.16415 | -0.003556 | -122.1845 | 0.078866 | 0.069409 | 0.072965 | -122.1355 | -122.0306 | -0.077174 | -0.22222 | 0.18418 | 0.058096 | 0.13527 | 0.053236 | -0.058028 | 0.15742 | 0.20639 | 0.31136 | 0.11585 | -122.3455 | 122.1197 | 122.3952 | 122.2839 | 0.87487 | -122.4191
3897.25 | 122.3694 | -0.086975 | 122.2504 | -0.010149 | -0.054812 | 0.039011 | 0.018614 | -0.013788 | -0.0042263 | -0.013887 | -0.002694 | -0.0025041 | 0.057619 | 0.04838 | 0.046619 | -0.012688 | 0.0243 | -0.008409 | 0.084176 | 0.11483 | 0.2198 | -0.085952 | 0.088043 | 0.79248 | -0.033458 | 122.0281 | 122.3128 | 122.2015 | -0.17331 | 0.001023 | -122.1662 | 0.074287 | 0.078566 | 0.077543 | -122.1355 | -122.0306 | -0.086331 | -0.22222 | 0.17502 | 0.053517 | 0.13985 | 0.062392 | -0.048871 | 0.17115 | 0.20181 | 0.30678 | 0.11127 | -122.3363 | 122.1151 | 122.3997 | 122.2885 | 0.87945 | -122.4237
3899.0156 | 122.3969 | -0.082397 | 122.2641 | -0.0025182 | -0.054598 | 0.039225 | 0.0184 | -0.013788 | -0.0040125 | -0.013887 | -0.0022666 | -0.0020767 | 0.057832 | 0.04838 | 0.046619 | -0.012688 | 0.019721 | -0.008409 | 0.07502 | 0.11025 | 0.21064 | -0.09511 | 0.092622 | 0.7879 | -0.0243 | 122.0281 | 122.3128 | 122.1969 | -0.16415 | -0.012713 | -122.1891 | 0.069709 | 0.073988 | 0.086701 | -122.1538 | -122.0535 | -0.081752 | -0.23595 | 0.17502 | 0.058097 | 0.13985 | 0.048659 | -0.067183 | 0.15742 | 0.19265 | 0.29304 | 0.10212 | -122.3592 | 122.1105 | 122.3952 | 122.2793 | 0.87029 | -122.4282
3900.7656 | 122.3831 | -0.086975 | 122.2549 | -0.010149 | -0.054598 | 0.039225 | 0.018828 | -0.013788 | -0.0040125 | -0.029148 | -0.002694 | -0.0025041 | 0.057619 | 0.048807 | 0.047046 | -0.017266 | 0.019721 | -0.003831 | 0.07502 | 0.11025 | 0.2198 | -0.085952 | 0.097201 | 0.79705 | -0.028879 | 122.0281 | 122.3082 | 122.1969 | -0.16415 | 0.001023 | -122.1799 | 0.069709 | 0.083144 | 0.082121 | -122.1447 | -122.0351 | -0.077174 | -0.22679 | 0.18418 | 0.058096 | 0.13527 | 0.053236 | -0.058028 | 0.162 | 0.19723 | 0.30678 | 0.1067 | -122.3409 | 122.1151 | 122.3952 | 122.2839 | 0.88403 | -122.4191
3902.5312 | 122.4197 | -0.050354 | 122.2733 | -0.010149 | -0.054812 | 0.039225 | 0.018614 | -0.014001 | -0.0040125 | -0.021518 | -0.0024804 | -0.0020767 | 0.057619 | 0.04838 | 0.046619 | -0.012688 | 0.0243 | -0.003831 | 0.07502 | 0.11025 | 0.2198 | -0.090531 | 0.097201 | 0.7879 | -0.0243 | 122.0327 | 122.3128 | 122.1969 | -0.16873 | -0.040177 | -122.1982 | 0.037666 | 0.046523 | 0.0867 | -122.163 | -122.0535 | -0.11837 | -0.24053 | 0.14755 | 0.026054 | 0.14443 | 0.039504 | -0.076338 | 0.12537 | 0.16061 | 0.27016 | 0.074654 | -122.3638 | 122.0831 | 122.3631 | 122.2473 | 0.83825 | -122.442
3904.2344 | 122.4655 | -0.041199 | 122.2549 | -0.010149 | -0.054384 | 0.039225 | 0.0184 | -0.013574 | -0.0040125 | -0.029148 | -0.002694 | -0.0020767 | 0.057191 | 0.048807 | 0.046619 | -0.021844 | 0.015142 | -0.003831 | 0.065863 | 0.11483 | 0.21064 | -0.090531 | 0.088043 | 0.79705 | -0.033458 | 122.0327 | 122.3173 | 122.2015 | -0.16415 | -0.049332 | -122.1891 | 0.019355 | 0.037368 | 0.0867 | -122.1401 | -122.0443 | -0.12295 | -0.22222 | 0.12924 | 0.007741 | 0.13069 | 0.062393 | -0.053449 | 0.10706 | 0.15603 | 0.25184 | 0.056341 | -122.3455 | 122.0739 | 122.3585 | 122.2427 | 0.83825 | -122.4191
3906 | 122.438 | -0.064087 | 122.2504 | -0.010149 | -0.054812 | 0.039225 | 0.018614 | -0.014001 | -0.0035853 | -0.021518 | -0.0024804 | -0.0025041 | 0.057191 | 0.048593 | 0.046406 | -0.021844 | 0.028878 | -0.012988 | 0.079598 | 0.11941 | 0.2198 | -0.090531 | 0.10178 | 0.79705 | -0.0243 | 122.0327 | 122.3173 | 122.1969 | -0.16415 | -0.026444 | -122.1708 | 0.042243 | 0.051099 | 0.077543 | -122.131 | -122.0306 | -0.10006 | -0.21764 | 0.16587 | 0.039787 | 0.13985 | 0.066971 | -0.05345 | 0.14369 | 0.1835 | 0.28389 | 0.092965 | -122.3409 | 122.0968 | 122.3814 | 122.261 | 0.86114 | -122.4145
3907.7656 | 122.3511 | -0.10986 | 122.3007 | -0.010149 | -0.054598 | 0.039011 | 0.018614 | -0.013788 | -0.0037989 | -0.036779 | -0.002694 | -0.0025041 | 0.057619 | 0.048807 | 0.046833 | -0.017266 | 0.028878 | -0.003831 | 0.065863 | 0.11025 | 0.2198 | -0.09511 | 0.097201 | 0.79248 | -0.028879 | 122.0327 | 122.299 | 122.2015 | -0.16415 | 0.014753 | -122.2349 | 0.092597 | 0.10603 | 0.091279 | -122.1905 | -122.0809 | -0.054286 | -0.26799 | 0.20706 | 0.080984 | 0.13527 | -0.001697 | -0.099225 | 0.17573 | 0.22012 | 0.32966 | 0.13874 | -122.3958 | 122.1426 | 122.4089 | 122.3114 | 0.90234 | -122.4649
3909.4688 | 122.4289 | -0.050354 | 122.2641 | -0.010149 | -0.054812 | 0.038798 | 0.018614 | -0.013788 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.048593 | 0.046619 | -0.017266 | 0.028878 | -0.008409 | 0.07502 | 0.12399 | 0.22438 | -0.085952 | 0.092622 | 0.79248 | -0.028879 | 122.0281 | 122.3128 | 122.1969 | -0.17331 | -0.035598 | -122.1891 | 0.033088 | 0.041945 | 0.077543 | -122.1401 | -122.0397 | -0.12295 | -0.23595 | 0.14298 | 0.021475 | 0.14443 | 0.048659 | -0.067183 | 0.12537 | 0.17434 | 0.27474 | 0.079232 | -122.3501 | 122.0785 | 122.3631 | 122.2473 | 0.84283 | -122.4374
3911.2188 | 122.4197 | -0.068665 | 122.2504 | -0.01778 | -0.055025 | 0.039225 | 0.0184 | -0.014001 | -0.0040125 | -0.021518 | -0.0024804 | -0.0022903 | 0.057405 | 0.048593 | 0.046619 | -0.021844 | 0.028878 | -0.012988 | 0.07502 | 0.11483 | 0.21522 | -0.09511 | 0.092622 | 0.80163 | -0.028879 | 122.0419 | 122.3128 | 122.2015 | -0.16415 | -0.026445 | -122.1753 | 0.046821 | 0.055677 | 0.082122 | -122.1355 | -122.0351 | -0.095484 | -0.20848 | 0.16129 | 0.039786 | 0.13527 | 0.062392 | -0.048871 | 0.14369 | 0.1835 | 0.28389 | 0.097543 | -122.3455 | 122.1105 | 122.3814 | 122.2702 | 0.8703 | -122.4145
3912.9219 | 122.4701 | -0.041199 | 122.2412 | 0.0051128 | -0.054598 | 0.039225 | 0.018614 | -0.013574 | -0.0042263 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.048807 | 0.047046 | -0.017266 | 0.0243 | -0.008409 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.088043 | 0.79705 | -0.0243 | 122.0373 | 122.3128 | 122.1969 | -0.16415 | -0.049332 | -122.1662 | 0.023933 | 0.03279 | 0.082122 | -122.1264 | -122.0214 | -0.12295 | -0.20391 | 0.12924 | 0.016899 | 0.13985 | 0.071547 | -0.044295 | 0.11622 | 0.15603 | 0.261 | 0.065499 | -122.3317 | 122.0785 | 122.354 | 122.2381 | 0.83825 | -122.4054
3914.6875 | 122.3511 | -0.10529 | 122.2961 | -0.010149 | -0.054812 | 0.039011 | 0.018187 | -0.013574 | -0.0040125 | -0.021518 | -0.0024804 | -0.0022903 | 0.057619 | 0.048807 | 0.046833 | -0.021844 | 0.028878 | -0.008409 | 0.07502 | 0.11483 | 0.22438 | -0.09511 | 0.092622 | 0.80163 | -0.028879 | 122.0373 | 122.3082 | 122.1969 | -0.16873 | 0.010176 | -122.2211 | 0.083442 | 0.096877 | 0.086701 | -122.1813 | -122.0718 | -0.063442 | -0.25884 | 0.19791 | 0.076407 | 0.13985 | 0.012037 | -0.099227 | 0.18031 | 0.22012 | 0.32967 | 0.13416 | -122.3913 | 122.1426 | 122.4135 | 122.3022 | 0.90692 | -122.4649
3916.3906 | 122.4426 | -0.073242 | 122.2458 | -0.0025182 | -0.054812 | 0.039011 | 0.0184 | -0.014001 | -0.0037989 | -0.013887 | -0.0024804 | -0.0027177 | 0.057191 | 0.048807 | 0.046406 | -0.021844 | 0.028878 | -0.012988 | 0.07502 | 0.11483 | 0.2198 | -0.081373 | 0.092622 | 0.79705 | -0.0243 | 122.0327 | 122.3128 | 122.1969 | -0.16415 | -0.008131 | -122.1708 | 0.051398 | 0.060254 | 0.068385 | -122.131 | -122.026 | -0.090907 | -0.21306 | 0.16586 | 0.048942 | 0.13985 | 0.066969 | -0.048873 | 0.14826 | 0.18807 | 0.29304 | 0.10212 | -122.3272 | 122.106 | 122.386 | 122.2702 | 0.8703 | -122.4099
3918.1562 | 122.3694 | -0.09613 | 122.2595 | -0.010149 | -0.054598 | 0.039011 | 0.0184 | -0.013788 | -0.0040125 | -0.029148 | -0.0022666 | -0.0022903 | 0.057191 | 0.048807 | 0.046619 | -0.017266 | 0.0243 | -0.008409 | 0.07502 | 0.11025 | 0.21522 | -0.090531 | 0.092622 | 0.79705 | -0.028879 | 122.0373 | 122.3128 | 122.2015 | -0.16415 | 0.005599 | -122.1845 | 0.078864 | 0.087721 | 0.082122 | -122.1493 | -122.0443 | -0.068019 | -0.22222 | 0.18875 | 0.067251 | 0.13527 | 0.053237 | -0.058026 | 0.17115 | 0.20638 | 0.31135 | 0.12043 | -122.3501 | 122.1334 | 122.4089 | 122.2976 | 0.89318 | -122.4237
3919.9062 | 122.4197 | -0.073242 | 122.2458 | -0.010149 | -0.054598 | 0.039011 | 0.0184 | -0.013788 | -0.0040125 | -0.013887 | -0.0029076 | -0.0022903 | 0.057405 | 0.048807 | 0.046833 | -0.021844 | 0.0243 | -0.008409 | 0.07502 | 0.11025 | 0.22438 | -0.085952 | 0.092622 | 0.80163 | -0.028879 | 122.0373 | 122.3082 | 122.2015 | -0.16873 | -0.01271 | -122.1708 | 0.051398 | 0.064833 | 0.077543 | -122.1355 | -122.0214 | -0.095486 | -0.20848 | 0.16586 | 0.044363 | 0.13985 | 0.062391 | -0.044294 | 0.14826 | 0.1835 | 0.29762 | 0.097542 | -122.3317 | 122.1105 | 122.3814 | 122.2747 | 0.87488 | -122.4145
3921.6719 | 122.4472 | -0.054932 | 122.2366 | -0.01778 | -0.054598 | 0.038798 | 0.018614 | -0.013574 | -0.0037989 | -0.029148 | -0.002694 | -0.0020767 | 0.057191 | 0.048593 | 0.046833 | -0.017266 | 0.028878 | -0.008409 | 0.079598 | 0.11025 | 0.21522 | -0.090531 | 0.088043 | 0.81079 | -0.028879 | 122.0327 | 122.3128 | 122.2015 | -0.16415 | -0.035599 | -122.157 | 0.037666 | 0.046523 | 0.082122 | -122.1264 | -122.0214 | -0.10922 | -0.20391 | 0.14297 | 0.026053 | 0.13527 | 0.076125 | -0.035138 | 0.13453 | 0.16518 | 0.27016 | 0.08381 | -122.3272 | 122.0877 | 122.3677 | 122.2564 | 0.86572 | -122.4008
3923.375 | 122.3785 | -0.10071 | 122.2687 | -0.010149 | -0.054812 | 0.038798 | 0.018614 | -0.014001 | -0.0040125 | -0.013887 | -0.0024804 | -0.0025041 | 0.057832 | 0.048807 | 0.046833 | -0.012688 | 0.019721 | -0.012988 | 0.070441 | 0.11025 | 0.21522 | -0.09511 | 0.088043 | 0.80621 | -0.0243 | 122.0373 | 122.3173 | 122.1969 | -0.16873 | 0.005598 | -122.1982 | 0.08802 | 0.08772 | 0.082122 | -122.1584 | -122.0535 | -0.06802 | -0.23137 | 0.18875 | 0.076408 | 0.14443 | 0.04866 | -0.071761 | 0.17115 | 0.21096 | 0.31593 | 0.12043 | -122.3638 | 122.138 | 122.418 | 122.2976 | 0.90692 | -122.4374
3925.1406 | 122.3465 | -0.09613 | 122.2778 | -0.01778 | -0.054598 | 0.039011 | 0.018614 | -0.014001 | -0.0037989 | -0.013887 | -0.0024804 | -0.0027177 | 0.057405 | 0.049021 | 0.046406 | -0.021844 | 0.028878 | -0.012988 | 0.070441 | 0.11941 | 0.2198 | -0.085952 | 0.092622 | 0.81079 | -0.033458 | 122.0327 | 122.3082 | 122.2015 | -0.16415 | 0.010178 | -122.2074 | 0.074286 | 0.083142 | 0.072964 | -122.1584 | -122.058 | -0.068019 | -0.24511 | 0.18875 | 0.062672 | 0.13069 | 0.030348 | -0.076337 | 0.16657 | 0.21554 | 0.31593 | 0.12501 | -122.3638 | 122.1289 | 122.4043 | 122.2976 | 0.90692 | -122.442
3926.875 | 122.4792 | -0.050354 | 122.2412 | -0.01778 | -0.054384 | 0.039011 | 0.0184 | -0.01336 | -0.0040125 | -0.021518 | -0.0024804 | -0.0022903 | 0.057405 | 0.048593 | 0.046833 | -0.017266 | 0.033457 | -0.012988 | 0.065863 | 0.11941 | 0.21522 | -0.090531 | 0.088043 | 0.81079 | -0.033458 | 122.0373 | 122.3082 | 122.2015 | -0.17331 | -0.040177 | -122.1753 | 0.033088 | 0.037366 | 0.077543 | -122.1218 | -122.026 | -0.12295 | -0.20391 | 0.1384 | 0.016896 | 0.13985 | 0.066969 | -0.039716 | 0.11622 | 0.16976 | 0.26558 | 0.083811 | -122.3317 | 122.0877 | 122.3585 | 122.2518 | 0.86115 | -122.4145
3928.625 | 122.4747 | -0.041199 | 122.2549 | -0.010149 | -0.054812 | 0.039011 | 0.0184 | -0.013788 | -0.0040125 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.048807 | 0.046619 | -0.021844 | 0.028878 | -0.012988 | 0.07502 | 0.11025 | 0.21522 | -0.085952 | 0.088043 | 0.80163 | -0.0243 | 122.0327 | 122.3173 | 122.1969 | -0.16873 | -0.044753 | -122.1799 | 0.019355 | 0.028211 | 0.072964 | -122.1447 | -122.0397 | -0.12753 | -0.22222 | 0.12924 | 0.016899 | 0.14443 | 0.062393 | -0.058028 | 0.11622 | 0.15145 | 0.25642 | 0.070077 | -122.3409 | 122.0739 | 122.3585 | 122.2381 | 0.84283 | -122.4237
3930.3906 | 122.4655 | -0.041199 | 122.2549 | -0.010149 | -0.054384 | 0.039652 | 0.018828 | -0.01336 | -0.0040125 | -0.036779 | -0.0022666 | -0.0016495 | 0.057619 | 0.048593 | 0.046833 | -0.012688 | 0.0243 | -0.017566 | 0.065863 | 0.11483 | 0.22896 | -0.090531 | 0.088043 | 0.81079 | -0.038036 | 122.0373 | 122.3082 | 122.1969 | -0.16415 | -0.049332 | -122.1891 | 0.028511 | 0.023633 | 0.072965 | -122.1401 | -122.026 | -0.12295 | -0.21764 | 0.12924 | 0.003163 | 0.12611 | 0.053236 | -0.058028 | 0.10706 | 0.15603 | 0.27016 | 0.065499 | -122.3455 | 122.0785 | 122.3494 | 122.2381 | 0.85199 | -122.4191
3932.1562 | 122.4152 | -0.059509 | 122.2549 | -0.0025182 | -0.054812 | 0.039225 | 0.0184 | -0.013574 | -0.0040125 | -0.013887 | -0.0024804 | -0.0022903 | 0.057191 | 0.049021 | 0.046619 | -0.012688 | 0.019721 | -0.017566 | 0.070441 | 0.11483 | 0.22438 | -0.09511 | 0.097201 | 0.80621 | -0.033458 | 122.0373 | 122.3128 | 122.2061 | -0.16873 | -0.035601 | -122.1845 | 0.046821 | 0.041943 | 0.077544 | -122.1401 | -122.0306 | -0.10922 | -0.21764 | 0.15671 | 0.026051 | 0.13527 | 0.057814 | -0.048871 | 0.12995 | 0.17434 | 0.28389 | 0.07923 | -122.3501 | 122.0968 | 122.3723 | 122.2656 | 0.86572 | -122.4237
3933.8594 | 122.5067 | -0.041199 | 122.2641 | -0.0025182 | -0.054598 | 0.039439 | 0.018187 | -0.013788 | -0.0042263 | -0.021518 | -0.002053 | -0.0022903 | 0.057405 | 0.049021 | 0.046619 | -0.021844 | 0.0243 | -0.017566 | 0.070441 | 0.11025 | 0.22438 | -0.090531 | 0.088043 | 0.81079 | -0.033458 | 122.0327 | 122.3128 | 122.1969 | -0.16415 | -0.049332 | -122.1937 | 0.019355 | 0.023633 | 0.072965 | -122.1538 | -122.0397 | -0.12295 | -0.23137 | 0.12924 | 0.007741 | 0.13069 | 0.048659 | -0.067183 | 0.11164 | 0.15145 | 0.26558 | 0.065499 | -122.3546 | 122.0739 | 122.354 | 122.2381 | 0.85199 | -122.4282
3935.6094 | 122.3557 | -0.10529 | 122.2824 | -0.01778 | -0.054812 | 0.039011 | 0.0184 | -0.014215 | -0.0042263 | -0.029148 | -0.002694 | -0.0020767 | 0.057405 | 0.048807 | 0.046619 | -0.017266 | 0.0243 | -0.017566 | 0.07502 | 0.11941 | 0.22438 | -0.09511 | 0.088043 | 0.81537 | -0.0243 | 122.0327 | 122.3082 | 122.2061 | -0.15499 | 0.010176 | -122.2074 | 0.08802 | 0.08772 | 0.077544 | -122.163 | -122.058 | -0.049705 | -0.24968 | 0.19333 | 0.080986 | 0.13069 | 0.02577 | -0.076337 | 0.18031 | 0.2247 | 0.32967 | 0.12959 | -122.3775 | 122.138 | 122.4135 | 122.3114 | 0.92066 | -122.4374
3937.375 | 122.4701 | -0.036621 | 122.2321 | -0.025411 | -0.054812 | 0.038798 | 0.0184 | -0.01336 | -0.0042263 | -0.021518 | -0.002694 | -0.0025041 | 0.057405 | 0.048807 | 0.04726 | -0.017266 | 0.019721 | -0.017566 | 0.07502 | 0.11025 | 0.2198 | -0.085952 | 0.092622 | 0.81537 | -0.028879 | 122.0373 | 122.3173 | 122.2015 | -0.16873 | -0.049331 | -122.157 | 0.019355 | 0.019055 | 0.068386 | -122.1218 | -122.0123 | -0.13211 | -0.19475 | 0.12924 | 0.007742 | 0.13985 | 0.085281 | -0.030561 | 0.11164 | 0.14687 | 0.25642 | 0.056342 | -122.318 | 122.0739 | 122.354 | 122.2381 | 0.85199 | -122.4008
3939.1562 | 122.4792 | -0.050354 | 122.2366 | -0.010149 | -0.054812 | 0.039439 | 0.0184 | -0.013788 | -0.0040125 | -0.021518 | -0.0022666 | -0.0025041 | 0.057619 | 0.049021 | 0.046619 | -0.012688 | 0.028878 | -0.017566 | 0.07502 | 0.11025 | 0.22896 | -0.085952 | 0.092622 | 0.81995 | -0.0243 | 122.0327 | 122.3082 | 122.1969 | -0.16873 | -0.035598 | -122.1616 | 0.037666 | 0.032788 | 0.068386 | -122.1264 | -122.0077 | -0.11837 | -0.20391 | 0.14298 | 0.026054 | 0.14443 | 0.071547 | -0.039717 | 0.12537 | 0.16061 | 0.27931 | 0.079232 | -122.3226 | 122.0831 | 122.3585 | 122.2473 | 0.8703 | -122.4054
3940.8594 | 122.3969 | -0.082397 | 122.2824 | -0.01778 | -0.054598 | 0.038798 | 0.018614 | -0.013788 | -0.0044399 | -0.0062567 | -0.0022666 | -0.0020767 | 0.057619 | 0.048807 | 0.046619 | -0.017266 | 0.0243 | -0.008409 | 0.070441 | 0.11483 | 0.21522 | -0.085952 | 0.092622 | 0.82453 | -0.028879 | 122.0327 | 122.3082 | 122.2015 | -0.16873 | -0.003555 | -122.212 | 0.065131 | 0.073988 | 0.077543 | -122.1676 | -122.0672 | -0.086331 | -0.24968 | 0.17502 | 0.053518 | 0.13985 | 0.02577 | -0.080915 | 0.15284 | 0.19723 | 0.29762 | 0.1067 | -122.3684 | 122.1151 | 122.3906 | 122.2839 | 0.90692 | -122.4511
3942.625 | 122.4701 | -0.045776 | 122.2412 | -0.01778 | -0.054812 | 0.039439 | 0.018187 | -0.014001 | -0.0042263 | -0.021518 | -0.0022666 | -0.0020767 | 0.057191 | 0.048807 | 0.046619 | -0.012688 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.21522 | -0.09511 | 0.088043 | 0.8291 | -0.0243 | 122.0281 | 122.3173 | 122.1969 | -0.17331 | -0.049334 | -122.1616 | 0.033088 | 0.02821 | 0.077544 | -122.1218 | -122.026 | -0.12753 | -0.21306 | 0.13382 | 0.021476 | 0.14901 | 0.076126 | -0.044295 | 0.12537 | 0.16519 | 0.261 | 0.070076 | -122.3363 | 122.0739 | 122.3631 | 122.2427 | 0.87488 | -122.4145
3944.3438 | 122.438 | -0.068665 | 122.2504 | -0.01778 | -0.054598 | 0.039011 | 0.018187 | -0.013788 | -0.0042263 | -0.021518 | -0.002053 | -0.0022903 | 0.057619 | 0.048807 | 0.046833 | -0.012688 | 0.019721 | -0.017566 | 0.079598 | 0.11941 | 0.2198 | -0.085952 | 0.097201 | 0.8291 | -0.033458 | 122.0373 | 122.3128 | 122.1969 | -0.16415 | -0.017287 | -122.1708 | 0.055977 | 0.051099 | 0.068386 | -122.131 | -122.0306 | -0.095484 | -0.21306 | 0.16587 | 0.035207 | 0.13069 | 0.062392 | -0.05345 | 0.14826 | 0.18808 | 0.28847 | 0.088386 | -122.3363 | 122.106 | 122.3814 | 122.2656 | 0.89777 | -122.4145
3946.1094 | 122.4426 | -0.054932 | 122.2137 | -0.010149 | -0.054812 | 0.039011 | 0.0184 | -0.013574 | -0.0040125 | -0.021518 | -0.0024804 | -0.0025041 | 0.057405 | 0.049234 | 0.046833 | -0.021844 | 0.0243 | -0.022144 | 0.07502 | 0.11483 | 0.21522 | -0.099689 | 0.092622 | 0.82453 | -0.033458 | 122.0373 | 122.3219 | 122.1969 | -0.16873 | -0.044757 | -122.1387 | 0.033088 | 0.032788 | 0.077545 | -122.0989 | -121.9985 | -0.1138 | -0.17644 | 0.14755 | 0.021474 | 0.13527 | 0.10817 | -0.016829 | 0.12995 | 0.16976 | 0.27016 | 0.079232 | -122.3134 | 122.0922 | 122.3768 | 122.2518 | 0.87946 | -122.3825
3947.8594 | 122.4609 | -0.036621 | 122.2092 | -0.01778 | -0.054812 | 0.039439 | 0.0184 | -0.013788 | -0.0042263 | -0.029148 | -0.0022666 | -0.0020767 | 0.057405 | 0.048807 | 0.046619 | -0.008109 | 0.033457 | -0.008409 | 0.07502 | 0.12399 | 0.2198 | -0.081373 | 0.088043 | 0.82453 | -0.033458 | 122.0373 | 122.3082 | 122.1923 | -0.16873 | -0.044752 | -122.1341 | 0.028512 | 0.028212 | 0.072964 | -122.0852 | -121.9894 | -0.13211 | -0.17186 | 0.12466 | 0.003163 | 0.13527 | 0.099013 | -0.01683 | 0.11164 | 0.16061 | 0.25642 | 0.070078 | -122.2905 | 122.0739 | 122.3448 | 122.229 | 0.86115 | -122.3779
3949.6406 | 122.4701 | -0.045776 | 122.2321 | -0.010149 | -0.054812 | 0.039011 | 0.0184 | -0.013788 | -0.0042263 | -0.021518 | -0.0024804 | -0.0025041 | 0.057619 | 0.048807 | 0.046833 | -0.021844 | 0.028878 | -0.017566 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.092622 | 0.82453 | -0.0243 | 122.0327 | 122.3173 | 122.2061 | -0.16873 | -0.044755 | -122.157 | 0.023932 | 0.02821 | 0.072965 | -122.1172 | -122.0123 | -0.12295 | -0.19933 | 0.1384 | 0.021476 | 0.14443 | 0.085281 | -0.025983 | 0.1208 | 0.16061 | 0.26558 | 0.074654 | -122.3226 | 122.0785 | 122.3631 | 122.2518 | 0.8703 | -122.4008
3951.3438 | 122.3557 | -0.09613 | 122.2824 | -0.0025182 | -0.054812 | 0.039011 | 0.0184 | -0.013574 | -0.0044399 | -0.021518 | -0.0022666 | -0.0022903 | 0.057619 | 0.049234 | 0.046619 | -0.008109 | 0.033457 | -0.022144 | 0.07502 | 0.11483 | 0.22438 | -0.090531 | 0.10178 | 0.8291 | -0.028879 | 122.0236 | 122.3036 | 122.2061 | -0.15957 | 0.005599 | -122.2074 | 0.088021 | 0.073986 | 0.068387 | -122.1676 | -122.058 | -0.06344 | -0.25884 | 0.19791 | 0.067251 | 0.13069 | 0.021191 | -0.076337 | 0.17115 | 0.21096 | 0.32051 | 0.12959 | -122.3729 | 122.1197 | 122.3997 | 122.3022 | 0.92524 | -122.442
3953.1094 | 122.438 | -0.032043 | 122.2366 | -0.01778 | -0.055025 | 0.038798 | 0.018614 | -0.013788 | -0.0042263 | -0.013887 | -0.0022666 | -0.0022903 | 0.057405 | 0.048593 | 0.046619 | -0.012688 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.2198 | -0.09511 | 0.092622 | 0.8291 | -0.0243 | 122.0373 | 122.3128 | 122.2061 | -0.15957 | -0.063067 | -122.157 | 0.019355 | 0.014477 | 0.077544 | -122.1172 | -122.0168 | -0.12753 | -0.19933 | 0.12466 | 0.007743 | 0.13527 | 0.076125 | -0.03056 | 0.11164 | 0.15145 | 0.25184 | 0.056343 | -122.3317 | 122.0693 | 122.3448 | 122.2381 | 0.86115 | -122.3962
3954.8125 | 122.3831 | -0.091553 | 122.2458 | -0.010149 | -0.054598 | 0.039011 | 0.0184 | -0.014001 | -0.0044399 | -0.021518 | -0.0022666 | -0.0025041 | 0.057619 | 0.049021 | 0.046619 | -0.012688 | 0.028878 | -0.022144 | 0.07502 | 0.11483 | 0.21522 | -0.090531 | 0.088043 | 0.8291 | -0.0243 | 122.0327 | 122.3082 | 122.1969 | -0.16873 | 0.001022 | -122.1708 | 0.078865 | 0.069409 | 0.068387 | -122.131 | -122.0306 | -0.077175 | -0.21306 | 0.1796 | 0.067253 | 0.14443 | 0.062391 | -0.048873 | 0.16657 | 0.20638 | 0.30678 | 0.12043 | -122.3363 | 122.1243 | 122.3997 | 122.2885 | 0.92066 | -122.4145
3956.5156 | 122.3373 | -0.11444 | 122.2733 | -0.01778 | -0.055239 | 0.039225 | 0.018614 | -0.013574 | -0.0046535 | -0.021518 | -0.0024804 | -0.0025041 | 0.057405 | 0.049021 | 0.046619 | -0.017266 | 0.019721 | -0.017566 | 0.07502 | 0.11483 | 0.2198 | -0.09511 | 0.088043 | 0.84284 | -0.028879 | 122.0281 | 122.3128 | 122.1969 | -0.16415 | 0.019331 | -122.1982 | 0.097175 | 0.096875 | 0.077544 | -122.1584 | -122.0535 | -0.049708 | -0.2451 | 0.20248 | 0.085562 | 0.13527 | 0.039504 | -0.076338 | 0.18946 | 0.22927 | 0.33424 | 0.13416 | -122.3684 | 122.1426 | 122.4272 | 122.3114 | 0.95728 | -122.4374
3958.2812 | 122.4243 | -0.068665 | 122.2733 | -0.01778 | -0.055025 | 0.039011 | 0.0184 | -0.013574 | -0.0044399 | -0.036779 | -0.0024804 | -0.0020767 | 0.057191 | 0.048593 | 0.046406 | -0.017266 | 0.019721 | -0.022144 | 0.07502 | 0.11941 | 0.22438 | -0.085952 | 0.092622 | 0.83368 | -0.028879 | 122.0373 | 122.3128 | 122.1923 | -0.16415 | -0.017287 | -122.1982 | 0.051399 | 0.046521 | 0.063808 | -122.1538 | -122.0489 | -0.095484 | -0.23595 | 0.16129 | 0.039786 | 0.13527 | 0.039504 | -0.080917 | 0.14369 | 0.18808 | 0.29305 | 0.088386 | -122.3592 | 122.106 | 122.3814 | 122.261 | 0.90235 | -122.4374
3959.9844 | 122.3511 | -0.082397 | 122.2824 | -0.01778 | -0.054812 | 0.039011 | 0.018614 | -0.014001 | -0.0044399 | -0.036779 | -0.0024804 | -0.0025041 | 0.057405 | 0.048807 | 0.046406 | -0.008109 | 0.0243 | -0.017566 | 0.07502 | 0.11483 | 0.2198 | -0.09511 | 0.092622 | 0.84742 | -0.028879 | 122.0373 | 122.3082 | 122.2061 | -0.16873 | -0.012713 | -122.2074 | 0.074288 | 0.064831 | 0.077544 | -122.1676 | -122.0626 | -0.086331 | -0.2451 | 0.17502 | 0.053518 | 0.13985 | 0.02577 | -0.076337 | 0.15742 | 0.19723 | 0.3022 | 0.1067 | -122.3775 | 122.1197 | 122.3906 | 122.2885 | 0.92982 | -122.4511
3961.75 | 122.406 | -0.068665 | 122.287 | -0.010149 | -0.054812 | 0.039011 | 0.0184 | -0.014001 | -0.0042263 | -0.021518 | -0.0022666 | -0.0018631 | 0.057191 | 0.049021 | 0.046833 | -0.017266 | 0.028878 | -0.017566 | 0.079598 | 0.10567 | 0.21064 | -0.090531 | 0.092622 | 0.84284 | -0.033458 | 122.0327 | 122.3173 | 122.1969 | -0.15957 | -0.021866 | -122.2074 | 0.051399 | 0.051099 | 0.072965 | -122.1813 | -122.0763 | -0.090905 | -0.25426 | 0.16129 | 0.035207 | 0.12611 | 0.03035 | -0.090071 | 0.14826 | 0.17434 | 0.27931 | 0.097543 | -122.3775 | 122.1014 | 122.386 | 122.2656 | 0.91151 | -122.4466
3963.5156 | 122.3282 | -0.09613 | 122.2824 | -0.01778 | -0.054812 | 0.039439 | 0.0184 | -0.013788 | -0.0042263 | -0.029148 | -0.0022666 | -0.0022903 | 0.057405 | 0.048807 | 0.046406 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.11483 | 0.2198 | -0.085952 | 0.092622 | 0.83826 | -0.028879 | 122.0327 | 122.3128 | 122.1969 | -0.16415 | 0.010178 | -122.1982 | 0.078864 | 0.078564 | 0.068386 | -122.1676 | -122.0626 | -0.068019 | -0.24968 | 0.18875 | 0.067251 | 0.13527 | 0.030348 | -0.085494 | 0.18031 | 0.21096 | 0.31593 | 0.12043 | -122.3684 | 122.1289 | 122.4089 | 122.293 | 0.93439 | -122.4466
3965.2812 | 122.3557 | -0.082397 | 122.2595 | -0.01778 | -0.054598 | 0.039011 | 0.018187 | -0.014001 | -0.0048673 | -0.021518 | -0.0024804 | -0.0018631 | 0.057405 | 0.048807 | 0.046619 | -0.017266 | 0.033457 | -0.017566 | 0.070441 | 0.11025 | 0.2198 | -0.090531 | 0.097201 | 0.83368 | -0.028879 | 122.0327 | 122.3173 | 122.2061 | -0.16873 | -0.008134 | -122.1891 | 0.065131 | 0.064831 | 0.072965 | -122.1493 | -122.0397 | -0.086331 | -0.22679 | 0.1796 | 0.053518 | 0.13985 | 0.057816 | -0.053448 | 0.15284 | 0.19265 | 0.3022 | 0.11585 | -122.3501 | 122.1151 | 122.3997 | 122.2885 | 0.91608 | -122.4282
3966.9844 | 122.3511 | -0.10071 | 122.2733 | -0.010149 | -0.054812 | 0.039225 | 0.018187 | -0.014215 | -0.0044399 | -0.036779 | -0.0024804 | -0.0027177 | 0.057191 | 0.048807 | 0.046619 | -0.012688 | 0.028878 | -0.012988 | 0.07502 | 0.11025 | 0.22438 | -0.085952 | 0.097201 | 0.84742 | -0.028879 | 122.0327 | 122.3082 | 122.2015 | -0.16873 | 0.014756 | -122.1982 | 0.08802 | 0.08772 | 0.072964 | -122.163 | -122.0489 | -0.06802 | -0.24053 | 0.19791 | 0.071829 | 0.13985 | 0.034926 | -0.071759 | 0.17573 | 0.21096 | 0.32509 | 0.12959 | -122.3592 | 122.1334 | 122.4089 | 122.3022 | 0.94813 | -122.442
3968.75 | 122.3511 | -0.09613 | 122.2733 | -0.010149 | -0.055025 | 0.039011 | 0.0184 | -0.013788 | -0.0046535 | -0.021518 | -0.002694 | -0.0022903 | 0.057405 | 0.049021 | 0.046619 | -0.026423 | 0.028878 | -0.017566 | 0.079598 | 0.11483 | 0.22438 | -0.085952 | 0.097201 | 0.84742 | -0.042615 | 122.0281 | 122.3173 | 122.1969 | -0.16873 | 0.010178 | -122.1937 | 0.069707 | 0.078564 | 0.068386 | -122.1584 | -122.0489 | -0.072598 | -0.2451 | 0.19333 | 0.053515 | 0.12611 | 0.044083 | -0.076338 | 0.17573 | 0.21096 | 0.32051 | 0.12501 | -122.3592 | 122.1243 | 122.4135 | 122.293 | 0.94355 | -122.442
3970.5156 | 122.3785 | -0.07782 | 122.2687 | -0.01778 | -0.054812 | 0.039011 | 0.018187 | -0.013574 | -0.0040125 | -0.013887 | -0.0022666 | -0.0025041 | 0.057832 | 0.049021 | 0.046619 | -0.017266 | 0.0243 | -0.022144 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.092622 | 0.852 | -0.0243 | 122.0327 | 122.3219 | 122.2015 | -0.16873 | -0.012711 | -122.1937 | 0.060554 | 0.055676 | 0.068387 | -122.1538 | -122.0489 | -0.090908 | -0.23595 | 0.17044 | 0.05352 | 0.14443 | 0.053239 | -0.067182 | 0.15284 | 0.19265 | 0.29762 | 0.10212 | -122.3592 | 122.1105 | 122.3997 | 122.2793 | 0.92982 | -122.4374
3972.2812 | 122.3877 | -0.09613 | 122.319 | -0.01778 | -0.055239 | 0.039225 | 0.018187 | -0.013788 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.057405 | 0.049021 | 0.046833 | -0.012688 | 0.019721 | -0.017566 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.092622 | 0.852 | -0.038036 | 122.0373 | 122.3128 | 122.2015 | -0.16415 | 0.005599 | -122.244 | 0.083442 | 0.078564 | 0.072965 | -122.2042 | -122.0992 | -0.068019 | -0.28172 | 0.18875 | 0.058094 | 0.12611 | -0.006273 | -0.11754 | 0.17115 | 0.21096 | 0.31593 | 0.11585 | -122.4096 | 122.1334 | 122.4089 | 122.2976 | 0.94813 | -122.4832
3973.9844 | 122.3969 | -0.09613 | 122.2961 | -0.010149 | -0.055025 | 0.039011 | 0.018614 | -0.014001 | -0.0035853 | -0.013887 | -0.002053 | -0.0020767 | 0.057619 | 0.049021 | 0.046619 | -0.017266 | 0.019721 | -0.012988 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.088043 | 0.85658 | -0.038036 | 122.0327 | 122.3173 | 122.1969 | -0.15957 | 0.005599 | -122.2211 | 0.078864 | 0.083142 | 0.077543 | -122.1813 | -122.0763 | -0.06344 | -0.26342 | 0.18417 | 0.058094 | 0.12153 | 0.021194 | -0.099227 | 0.17115 | 0.21096 | 0.31593 | 0.11585 | -122.3867 | 122.1289 | 122.4135 | 122.293 | 0.95271 | -122.4557
3975.7344 | 122.4014 | -0.086975 | 122.2916 | -0.01778 | -0.055025 | 0.039439 | 0.0184 | -0.014001 | -0.0033715 | -0.021518 | -0.0024804 | -0.0020767 | 0.057405 | 0.048807 | 0.047046 | -0.012688 | 0.0243 | -0.012988 | 0.07502 | 0.10567 | 0.21522 | -0.090531 | 0.092622 | 0.85658 | -0.0243 | 122.0327 | 122.3128 | 122.2015 | -0.17331 | -0.003556 | -122.2165 | 0.074287 | 0.073987 | 0.077543 | -122.1859 | -122.0763 | -0.086331 | -0.25884 | 0.1796 | 0.062675 | 0.14901 | 0.021193 | -0.09007 | 0.162 | 0.19265 | 0.3022 | 0.11127 | -122.3821 | 122.1197 | 122.3997 | 122.2885 | 0.94355 | -122.4649
3977.4844 | 122.3282 | -0.09613 | 122.2595 | -0.01778 | -0.055025 | 0.039011 | 0.017973 | -0.014215 | -0.0040125 | -0.021518 | -0.0022666 | -0.0020767 | 0.057619 | 0.049021 | 0.046833 | -0.021844 | 0.0243 | -0.017566 | 0.079598 | 0.11025 | 0.2198 | -0.090531 | 0.092622 | 0.85658 | -0.028879 | 122.0373 | 122.3128 | 122.1969 | -0.15957 | 0.005599 | -122.1799 | 0.074286 | 0.078564 | 0.072965 | -122.1493 | -122.0397 | -0.06344 | -0.22222 | 0.18875 | 0.067251 | 0.13069 | 0.053237 | -0.062605 | 0.17573 | 0.20638 | 0.31593 | 0.12043 | -122.3501 | 122.1334 | 122.4089 | 122.293 | 0.95271 | -122.4191
3979.25 | 122.319 | -0.086975 | 122.2916 | -0.01778 | -0.054812 | 0.039011 | 0.018187 | -0.013788 | -0.0035853 | -0.0062567 | -0.0022666 | -0.0022903 | 0.056978 | 0.049021 | 0.046619 | -0.017266 | 0.028878 | -0.022144 | 0.079598 | 0.11025 | 0.2198 | -0.09511 | 0.092622 | 0.85658 | -0.0243 | 122.0327 | 122.3173 | 122.2015 | -0.16415 | -0.008135 | -122.212 | 0.069709 | 0.064831 | 0.072966 | -122.1813 | -122.0718 | -0.077174 | -0.25884 | 0.1796 | 0.062675 | 0.13985 | 0.025772 | -0.09007 | 0.16657 | 0.19723 | 0.30678 | 0.11585 | -122.3867 | 122.1197 | 122.4043 | 122.2885 | 0.94355 | -122.4557
3980.9531 | 122.4655 | -0.054932 | 122.2641 | 0.0051128 | -0.054812 | 0.039225 | 0.018187 | -0.013574 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.049021 | 0.046619 | -0.012688 | 0.0243 | -0.012988 | 0.079598 | 0.12399 | 0.22896 | -0.090531 | 0.097201 | 0.86116 | -0.028879 | 122.0327 | 122.3173 | 122.1923 | -0.16415 | -0.035599 | -122.1845 | 0.042244 | 0.041944 | 0.077543 | -122.1401 | -122.0351 | -0.10922 | -0.23137 | 0.15213 | 0.026053 | 0.13527 | 0.053238 | -0.071762 | 0.13453 | 0.17892 | 0.28389 | 0.079232 | -122.3546 | 122.0877 | 122.3723 | 122.2473 | 0.91609 | -122.4282
3982.7188 | 122.4289 | -0.045776 | 122.2733 | -0.0025182 | -0.054598 | 0.039011 | 0.018614 | -0.013788 | -0.0037989 | -0.021518 | -0.0024804 | -0.0025041 | 0.057191 | 0.049021 | 0.046406 | -0.017266 | 0.0243 | -0.012988 | 0.084176 | 0.11483 | 0.2198 | -0.09511 | 0.092622 | 0.86116 | -0.033458 | 122.0419 | 122.3173 | 122.1969 | -0.16415 | -0.049334 | -122.1891 | 0.02851 | 0.032788 | 0.082122 | -122.1584 | -122.0535 | -0.11837 | -0.23137 | 0.1384 | 0.012318 | 0.13069 | 0.044083 | -0.076338 | 0.12995 | 0.16061 | 0.26558 | 0.070076 | -122.3684 | 122.0877 | 122.3631 | 122.2427 | 0.90693 | -122.4374
3984.5 | 122.3419 | -0.091553 | 122.3007 | -0.025411 | -0.054812 | 0.039011 | 0.0184 | -0.013788 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.049234 | 0.046833 | -0.026423 | 0.033457 | -0.012988 | 0.07502 | 0.10567 | 0.22438 | -0.09511 | 0.097201 | 0.86116 | -0.028879 | 122.0327 | 122.3173 | 122.2015 | -0.16873 | -0.003557 | -122.2257 | 0.06513 | 0.078565 | 0.082122 | -122.195 | -122.0763 | -0.077175 | -0.26799 | 0.18875 | 0.062674 | 0.13985 | 0.016617 | -0.099225 | 0.16657 | 0.19723 | 0.31593 | 0.12501 | -122.3958 | 122.1243 | 122.4089 | 122.293 | 0.95271 | -122.4694
3986.2031 | 122.4976 | -0.050354 | 122.2641 | -0.01778 | -0.055025 | 0.039011 | 0.018187 | -0.013788 | -0.0035853 | -0.021518 | -0.0022666 | -0.0020767 | 0.057405 | 0.049021 | 0.046619 | -0.021844 | 0.019721 | -0.022144 | 0.084176 | 0.11025 | 0.22438 | -0.090531 | 0.088043 | 0.86574 | -0.028879 | 122.0419 | 122.3128 | 122.1969 | -0.16415 | -0.040177 | -122.1799 | 0.02851 | 0.02821 | 0.068387 | -122.1538 | -122.0397 | -0.11379 | -0.22222 | 0.1384 | 0.021475 | 0.13527 | 0.048659 | -0.067183 | 0.13453 | 0.16061 | 0.27474 | 0.070075 | -122.3546 | 122.0922 | 122.3631 | 122.2473 | 0.91609 | -122.4282
3987.9688 | 122.3602 | -0.082397 | 122.2824 | -0.010149 | -0.055025 | 0.039011 | 0.0184 | -0.014001 | -0.0033715 | -0.021518 | -0.002694 | -0.0022903 | 0.057191 | 0.049234 | 0.046619 | -0.017266 | 0.0243 | -0.017566 | 0.079598 | 0.11025 | 0.2198 | -0.090531 | 0.092622 | 0.87031 | -0.0243 | 122.0373 | 122.3128 | 122.2015 | -0.16415 | -0.008134 | -122.2028 | 0.065131 | 0.064831 | 0.072965 | -122.1722 | -122.0626 | -0.081752 | -0.2451 | 0.17502 | 0.058097 | 0.13985 | 0.030348 | -0.080915 | 0.162 | 0.19265 | 0.3022 | 0.1067 | -122.3729 | 122.1197 | 122.3952 | 122.2839 | 0.95271 | -122.4466
3989.6562 | 122.4655 | -0.059509 | 122.2778 | -0.010149 | -0.054812 | 0.039439 | 0.018187 | -0.013788 | -0.0031579 | -0.013887 | -0.0018394 | -0.0022903 | 0.057191 | 0.049234 | 0.047046 | -0.012688 | 0.019721 | -0.022144 | 0.07502 | 0.11941 | 0.2198 | -0.085952 | 0.092622 | 0.87031 | -0.033458 | 122.0373 | 122.3173 | 122.1969 | -0.16873 | -0.026443 | -122.2028 | 0.046821 | 0.037365 | 0.063808 | -122.1584 | -122.058 | -0.10922 | -0.24053 | 0.15213 | 0.026051 | 0.13527 | 0.039505 | -0.080916 | 0.13453 | 0.17892 | 0.27931 | 0.07923 | -122.3638 | 122.0968 | 122.3768 | 122.2564 | 0.92982 | -122.4466
3991.4062 | 122.4747 | -0.064087 | 122.2504 | -0.01778 | -0.055025 | 0.039439 | 0.0184 | -0.013788 | -0.0040125 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.049234 | 0.04726 | -0.017266 | 0.019721 | -0.017566 | 0.07502 | 0.11483 | 0.22896 | -0.099689 | 0.083464 | 0.87031 | -0.028879 | 122.0327 | 122.3173 | 122.2061 | -0.16873 | -0.035602 | -122.1753 | 0.046821 | 0.046521 | 0.082123 | -122.1355 | -122.0214 | -0.10464 | -0.21764 | 0.14755 | 0.035208 | 0.13985 | 0.066971 | -0.044293 | 0.13911 | 0.17892 | 0.29305 | 0.083808 | -122.3501 | 122.0968 | 122.3814 | 122.2702 | 0.9344 | -122.4191
3993.1094 | 122.4701 | -0.045776 | 122.2412 | -0.01778 | -0.054812 | 0.039225 | 0.0184 | -0.013788 | -0.0033715 | -0.021518 | -0.002053 | -0.0020767 | 0.057191 | 0.049234 | 0.046406 | -0.012688 | 0.028878 | -0.017566 | 0.084176 | 0.11483 | 0.22438 | -0.09511 | 0.088043 | 0.87489 | -0.028879 | 122.0281 | 122.3219 | 122.1969 | -0.16415 | -0.049334 | -122.157 | 0.033088 | 0.02821 | 0.077544 | -122.1264 | -122.0168 | -0.11837 | -0.21306 | 0.13382 | 0.016897 | 0.13527 | 0.080705 | -0.044295 | 0.12995 | 0.16061 | 0.27016 | 0.074654 | -122.3363 | 122.0739 | 122.3677 | 122.2427 | 0.92067 | -122.4054
3994.8281 | 122.3419 | -0.086975 | 122.2687 | -0.010149 | -0.055025 | 0.038584 | 0.018187 | -0.013788 | -0.0037989 | -0.021518 | -0.0024804 | -0.0025041 | 0.057405 | 0.049021 | 0.046833 | -0.012688 | 0.0243 | -0.022144 | 0.07502 | 0.11483 | 0.21522 | -0.090531 | 0.092622 | 0.87489 | -0.033458 | 122.0373 | 122.3173 | 122.2015 | -0.17331 | -0.003556 | -122.1937 | 0.074287 | 0.064831 | 0.068387 | -122.1538 | -122.0535 | -0.086331 | -0.23137 | 0.1796 | 0.053517 | 0.13985 | 0.04866 | -0.067182 | 0.162 | 0.20181 | 0.3022 | 0.11127 | -122.3592 | 122.1243 | 122.4043 | 122.2885 | 0.96187 | -122.442
3996.5938 | 122.3419 | -0.09613 | 122.2733 | -0.010149 | -0.055239 | 0.039011 | 0.018187 | -0.014001 | -0.0040125 | -0.029148 | -0.002053 | -0.0020767 | 0.057405 | 0.049021 | 0.046619 | -0.012688 | 0.0243 | -0.012988 | 0.07502 | 0.12399 | 0.22896 | -0.090531 | 0.083464 | 0.87489 | -0.033458 | 122.0327 | 122.3082 | 122.1969 | -0.16415 | 0.005599 | -122.1982 | 0.083442 | 0.083142 | 0.077543 | -122.1493 | -122.0443 | -0.068019 | -0.24053 | 0.17959 | 0.062672 | 0.13069 | 0.034926 | -0.076338 | 0.17115 | 0.22012 | 0.32509 | 0.12043 | -122.3638 | 122.1289 | 122.4043 | 122.293 | 0.97102 | -122.4374
3998.3438 | 122.374 | -0.086975 | 122.2733 | -0.01778 | -0.055239 | 0.039439 | 0.0184 | -0.013788 | -0.0033715 | -0.029148 | -0.0024804 | -0.0022903 | 0.057619 | 0.049234 | 0.046833 | -0.012688 | 0.028878 | -0.017566 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.088043 | 0.87947 | -0.028879 | 122.0281 | 122.3173 | 122.2061 | -0.16415 | -0.003556 | -122.1982 | 0.074287 | 0.069409 | 0.072965 | -122.1584 | -122.0535 | -0.077174 | -0.2451 | 0.17502 | 0.058096 | 0.13527 | 0.044083 | -0.067181 | 0.162 | 0.20181 | 0.30678 | 0.11585 | -122.3638 | 122.1151 | 122.4043 | 122.293 | 0.96645 | -122.4374
4000.0469 | 122.3373 | -0.10071 | 122.2961 | -0.01778 | -0.055453 | 0.038798 | 0.018187 | -0.013788 | -0.0033715 | -0.021518 | -0.0022666 | -0.0020767 | 0.056978 | 0.048807 | 0.046619 | -0.017266 | 0.028878 | -0.012988 | 0.07502 | 0.11025 | 0.2198 | -0.09511 | 0.092622 | 0.87947 | -0.0243 | 122.0373 | 122.3128 | 122.2015 | -0.16415 | 0.005598 | -122.2211 | 0.083442 | 0.08772 | 0.082122 | -122.1859 | -122.0763 | -0.063441 | -0.25884 | 0.19333 | 0.076408 | 0.13985 | 0.016615 | -0.094648 | 0.17573 | 0.21096 | 0.32051 | 0.12959 | -122.3913 | 122.138 | 122.4135 | 122.3022 | 0.98018 | -122.4603
4001.75 | 122.4335 | -0.059509 | 122.2458 | -0.01778 | -0.055239 | 0.039011 | 0.0184 | -0.013574 | -0.0035853 | -0.029148 | -0.002694 | -0.0022903 | 0.057405 | 0.049021 | 0.046619 | -0.021844 | 0.028878 | -0.026723 | 0.084176 | 0.11941 | 0.2198 | -0.090531 | 0.092622 | 0.88863 | -0.033458 | 122.0281 | 122.3082 | 122.1923 | -0.16873 | -0.031022 | -122.1616 | 0.037665 | 0.032786 | 0.063808 | -122.1264 | -122.026 | -0.10922 | -0.21764 | 0.15213 | 0.026051 | 0.13527 | 0.062391 | -0.053452 | 0.14369 | 0.17892 | 0.27931 | 0.088387 | -122.3363 | 122.0877 | 122.3677 | 122.2518 | 0.94814 | -122.4145
4003.4531 | 122.3831 | -0.09613 | 122.2595 | -0.01778 | -0.054812 | 0.039225 | 0.0184 | -0.014001 | -0.0033715 | -0.013887 | -0.0022666 | -0.0022903 | 0.057405 | 0.049021 | 0.046406 | -0.012688 | 0.028878 | -0.017566 | 0.07502 | 0.11025 | 0.2198 | -0.09511 | 0.088043 | 0.87947 | -0.033458 | 122.0327 | 122.3128 | 122.2015 | -0.16873 | 0.00102 | -122.1845 | 0.083442 | 0.078564 | 0.077544 | -122.1493 | -122.0397 | -0.072598 | -0.22679 | 0.18417 | 0.062672 | 0.13527 | 0.053237 | -0.058026 | 0.17115 | 0.20638 | 0.31593 | 0.12501 | -122.3546 | 122.1289 | 122.4089 | 122.2976 | 0.9756 | -122.4282
4005.2188 | 122.3785 | -0.086975 | 122.2641 | -0.010149 | -0.055025 | 0.039011 | 0.018614 | -0.014001 | -0.0033715 | -0.021518 | -0.0024804 | -0.0020767 | 0.057405 | 0.049234 | 0.046192 | -0.012688 | 0.0243 | -0.012988 | 0.07502 | 0.11483 | 0.22438 | -0.085952 | 0.092622 | 0.88863 | -0.028879 | 122.0327 | 122.3173 | 122.2015 | -0.17331 | 0.001023 | -122.1891 | 0.074287 | 0.073987 | 0.072964 | -122.1493 | -122.0397 | -0.086331 | -0.23137 | 0.1796 | 0.058096 | 0.14443 | 0.053238 | -0.062604 | 0.162 | 0.20181 | 0.31136 | 0.11127 | -122.3501 | 122.1197 | 122.4043 | 122.2885 | 0.9756 | -122.4374
4006.9844 | 122.4197 | -0.073242 | 122.2412 | -0.01778 | -0.055025 | 0.039225 | 0.018187 | -0.013788 | -0.0033715 | -0.0062567 | -0.0022666 | -0.0022903 | 0.057405 | 0.049021 | 0.046833 | -0.021844 | 0.0243 | -0.008409 | 0.079598 | 0.11025 | 0.22896 | -0.090531 | 0.092622 | 0.89321 | -0.028879 | 122.0419 | 122.3219 | 122.1969 | -0.16873 | -0.017289 | -122.1616 | 0.051398 | 0.064833 | 0.082122 | -122.131 | -122.0123 | -0.095486 | -0.19933 | 0.16586 | 0.044363 | 0.13985 | 0.080705 | -0.044295 | 0.15284 | 0.1835 | 0.3022 | 0.097542 | -122.3317 | 122.1151 | 122.3952 | 122.2702 | 0.96645 | -122.4099
4008.7344 | 122.4335 | -0.054932 | 122.2504 | -0.010149 | -0.054812 | 0.039011 | 0.018187 | -0.014001 | -0.0035853 | -0.013887 | -0.0022666 | -0.0018631 | 0.057405 | 0.049234 | 0.046406 | -0.008109 | 0.0243 | -0.022144 | 0.07502 | 0.11025 | 0.2198 | -0.090531 | 0.088043 | 0.89321 | -0.0243 | 122.0281 | 122.3173 | 122.1969 | -0.16873 | -0.035599 | -122.1753 | 0.046823 | 0.032788 | 0.068387 | -122.1401 | -122.0306 | -0.1138 | -0.22222 | 0.14297 | 0.030632 | 0.14443 | 0.066971 | -0.05345 | 0.12995 | 0.16518 | 0.27473 | 0.079232 | -122.3409 | 122.0831 | 122.3723 | 122.2518 | 0.94814 | -122.4191
4011.7656 | 122.438 | -0.064087 | 122.2549 | -0.0025182 | -0.055239 | 0.039011 | 0.0184 | -0.014001 | -0.0033715 | -0.029148 | -0.0024804 | -0.0022903 | 0.057619 | 0.049021 | 0.046406 | -0.017266 | 0.0243 | -0.022144 | 0.07502 | 0.11941 | 0.2198 | -0.099689 | 0.097201 | 0.89321 | -0.028879 | 122.0373 | 122.3173 | 122.2061 | -0.16873 | -0.035602 | -122.1799 | 0.046821 | 0.041943 | 0.077545 | -122.1355 | -122.0351 | -0.10464 | -0.21764 | 0.16129 | 0.035208 | 0.13985 | 0.062393 | -0.048871 | 0.13911 | 0.1835 | 0.28389 | 0.088387 | -122.3546 | 122.1014 | 122.3814 | 122.2702 | 0.95729 | -122.4237
4014.4531 | 122.3785 | -0.086975 | 122.2595 | -0.01778 | -0.055239 | 0.039011 | 0.018187 | -0.013574 | -0.0035853 | -0.029148 | -0.0029076 | -0.0022903 | 0.057405 | 0.049234 | 0.046619 | -0.017266 | 0.0243 | -0.012988 | 0.070441 | 0.11941 | 0.2198 | -0.085952 | 0.092622 | 0.89779 | -0.028879 | 122.0373 | 122.3173 | 122.2015 | -0.16873 | 0.001023 | -122.1891 | 0.069709 | 0.073987 | 0.072964 | -122.1401 | -122.0397 | -0.081753 | -0.22222 | 0.1796 | 0.058096 | 0.13985 | 0.057816 | -0.058026 | 0.15742 | 0.20639 | 0.30678 | 0.11127 | -122.3455 | 122.1243 | 122.4043 | 122.2885 | 0.98476 | -122.4282
4018.125 | 122.3602 | -0.086975 | 122.287 | -0.01778 | -0.055239 | 0.039011 | 0.018187 | -0.014001 | -0.0035853 | -0.021518 | -0.0022666 | -0.0025041 | 0.057405 | 0.049021 | 0.046406 | -0.021844 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.23354 | -0.09511 | 0.092622 | 0.91152 | -0.033458 | 122.0327 | 122.3173 | 122.1969 | -0.17331 | -0.008135 | -122.2074 | 0.065131 | 0.069409 | 0.077544 | -122.1676 | -122.0534 | -0.086331 | -0.25426 | 0.1796 | 0.053517 | 0.13985 | 0.03035 | -0.090071 | 0.16657 | 0.20639 | 0.32051 | 0.11127 | -122.3821 | 122.1197 | 122.4043 | 122.2839 | 0.9985 | -122.4603
4023.4375 | 122.3419 | -0.086975 | 122.2595 | -0.01778 | -0.055025 | 0.039011 | 0.017759 | -0.014001 | -0.0035853 | -0.013887 | -0.002053 | -0.0025041 | 0.057405 | 0.049021 | 0.046406 | -0.017266 | 0.0243 | -0.012988 | 0.079598 | 0.11483 | 0.22438 | -0.085952 | 0.083464 | 0.90694 | -0.028879 | 122.0281 | 122.3082 | 122.1969 | -0.16873 | 0.001023 | -122.1799 | 0.069709 | 0.073987 | 0.072964 | -122.1447 | -122.0351 | -0.081753 | -0.23137 | 0.17044 | 0.058096 | 0.13985 | 0.048659 | -0.062605 | 0.16657 | 0.20181 | 0.31136 | 0.11127 | -122.3455 | 122.1151 | 122.3952 | 122.2839 | 0.99392 | -122.4282
4025.2188 | 122.4472 | -0.068665 | 122.2366 | -0.025411 | -0.054812 | 0.039011 | 0.018187 | -0.013574 | -0.0035853 | -0.029148 | -0.0024804 | -0.0025041 | 0.056978 | 0.049234 | 0.046619 | -0.012688 | 0.028878 | -0.012988 | 0.079598 | 0.11483 | 0.2198 | -0.090531 | 0.088043 | 0.9161 | -0.028879 | 122.0419 | 122.3173 | 122.2061 | -0.16873 | -0.021866 | -122.157 | 0.055977 | 0.055677 | 0.077543 | -122.1218 | -122.0168 | -0.10006 | -0.19475 | 0.15671 | 0.039786 | 0.13985 | 0.080704 | -0.03056 | 0.14826 | 0.1835 | 0.28847 | 0.097543 | -122.3272 | 122.1105 | 122.386 | 122.2747 | 0.98477 | -122.4054
4026.9219 | 122.438 | -0.054932 | 122.2733 | -0.0025182 | -0.055025 | 0.039225 | 0.017973 | -0.013574 | -0.0035853 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.049662 | 0.046406 | -0.017266 | 0.0243 | -0.022144 | 0.079598 | 0.11025 | 0.2198 | -0.090531 | 0.088043 | 0.92068 | -0.028879 | 122.0419 | 122.3128 | 122.2015 | -0.16873 | -0.035599 | -122.1937 | 0.037666 | 0.032788 | 0.068387 | -122.163 | -122.0535 | -0.1138 | -0.23137 | 0.14297 | 0.026053 | 0.13985 | 0.039504 | -0.071759 | 0.13453 | 0.16518 | 0.27473 | 0.079232 | -122.3638 | 122.0968 | 122.3677 | 122.2564 | 0.97561 | -122.442
4028.6719 | 122.4106 | -0.07782 | 122.2778 | -0.0025182 | -0.055239 | 0.038798 | 0.0184 | -0.014001 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.048807 | 0.046619 | -0.017266 | 0.028878 | -0.017566 | 0.070441 | 0.11941 | 0.22896 | -0.090531 | 0.097201 | 0.92526 | -0.028879 | 122.0373 | 122.3173 | 122.2015 | -0.16415 | -0.012711 | -122.2074 | 0.060554 | 0.060254 | 0.072965 | -122.1584 | -122.0489 | -0.086329 | -0.24053 | 0.17502 | 0.048941 | 0.13527 | 0.039505 | -0.076337 | 0.14826 | 0.19723 | 0.30678 | 0.1067 | -122.3684 | 122.1151 | 122.3952 | 122.2793 | 1.0031 | -122.442
4030.4375 | 122.3785 | -0.068665 | 122.2778 | -0.01778 | -0.055666 | 0.039225 | 0.017973 | -0.013788 | -0.0035853 | -0.029148 | -0.002694 | -0.0022903 | 0.057405 | 0.049021 | 0.046406 | -0.008109 | 0.028878 | -0.017566 | 0.07502 | 0.11025 | 0.22896 | -0.090531 | 0.083464 | 0.92068 | -0.0243 | 122.0281 | 122.3265 | 122.2061 | -0.15957 | -0.021866 | -122.2028 | 0.060556 | 0.051099 | 0.072965 | -122.1676 | -122.0489 | -0.090905 | -0.24968 | 0.15213 | 0.044365 | 0.13527 | 0.048662 | -0.071759 | 0.14369 | 0.17892 | 0.29762 | 0.097543 | -122.3684 | 122.0968 | 122.3952 | 122.2747 | 0.98935 | -122.4374
4032.2188 | 122.3511 | -0.086975 | 122.2778 | -0.0025182 | -0.055239 | 0.038798 | 0.018187 | -0.014001 | -0.0031579 | -0.021518 | -0.0022666 | -0.0020767 | 0.057405 | 0.049234 | 0.046406 | -0.017266 | 0.0243 | -0.012988 | 0.07502 | 0.12399 | 0.22438 | -0.090531 | 0.097201 | 0.92526 | -0.0243 | 122.0373 | 122.3219 | 122.2015 | -0.17331 | -0.003556 | -122.2028 | 0.069709 | 0.073987 | 0.077543 | -122.1538 | -122.0535 | -0.086331 | -0.24053 | 0.18418 | 0.062675 | 0.14901 | 0.044084 | -0.076337 | 0.162 | 0.21097 | 0.31136 | 0.11127 | -122.3684 | 122.1243 | 122.4089 | 122.2885 | 1.0122 | -122.4511
4033.9219 | 122.4701 | -0.054932 | 122.2549 | -0.010149 | -0.055239 | 0.039011 | 0.018187 | -0.014001 | -0.0035853 | -0.029148 | -0.002053 | -0.0022903 | 0.057619 | 0.049234 | 0.046619 | -0.012688 | 0.019721 | -0.017566 | 0.07502 | 0.11941 | 0.22438 | -0.090531 | 0.097201 | 0.92068 | -0.028879 | 122.0327 | 122.3173 | 122.2061 | -0.17331 | -0.035599 | -122.1799 | 0.042244 | 0.037366 | 0.072965 | -122.1355 | -122.0306 | -0.11837 | -0.22222 | 0.15213 | 0.026053 | 0.14443 | 0.062393 | -0.048871 | 0.12995 | 0.17434 | 0.27931 | 0.074653 | -122.3455 | 122.0877 | 122.3723 | 122.261 | 0.97561 | -122.4282
4035.6094 | 122.3923 | -0.07782 | 122.2641 | -0.01778 | -0.055453 | 0.039011 | 0.017973 | -0.013574 | -0.0033715 | -0.021518 | -0.0022666 | -0.0020767 | 0.057191 | 0.049234 | 0.046406 | -0.012688 | 0.028878 | -0.017566 | 0.084176 | 0.11483 | 0.21522 | -0.090531 | 0.088043 | 0.92068 | -0.028879 | 122.0373 | 122.3173 | 122.2061 | -0.16873 | -0.012711 | -122.1799 | 0.065132 | 0.060254 | 0.072965 | -122.1493 | -122.0489 | -0.090908 | -0.22679 | 0.16586 | 0.048941 | 0.13985 | 0.053238 | -0.058026 | 0.162 | 0.19265 | 0.29304 | 0.1067 | -122.3546 | 122.1151 | 122.3952 | 122.2839 | 0.9985 | -122.4328
4037.375 | 122.3969 | -0.073242 | 122.2733 | -0.01778 | -0.055239 | 0.039011 | 0.018614 | -0.013788 | -0.0035853 | -0.013887 | -0.002694 | -0.0020767 | 0.057191 | 0.049234 | 0.046406 | -0.021844 | 0.028878 | -0.008409 | 0.079598 | 0.11941 | 0.2198 | -0.085952 | 0.097201 | 0.92526 | -0.033458 | 122.0373 | 122.3128 | 122.2015 | -0.16873 | -0.01271 | -122.1937 | 0.051398 | 0.064833 | 0.077543 | -122.1538 | -122.0535 | -0.095486 | -0.23595 | 0.17044 | 0.039784 | 0.13527 | 0.039504 | -0.071759 | 0.15284 | 0.19265 | 0.29304 | 0.10212 | -122.3592 | 122.1105 | 122.386 | 122.2747 | 0.9985 | -122.442
4039.1562 | 122.438 | -0.045776 | 122.2549 | -0.010149 | -0.055453 | 0.039011 | 0.0184 | -0.013574 | -0.0033715 | -0.013887 | -0.002694 | -0.0022903 | 0.057191 | 0.049662 | 0.046406 | -0.021844 | 0.0243 | -0.017566 | 0.07502 | 0.11025 | 0.21522 | -0.090531 | 0.092622 | 0.93442 | -0.033458 | 122.0327 | 122.3173 | 122.2015 | -0.16873 | -0.044755 | -122.1799 | 0.023932 | 0.02821 | 0.072965 | -122.1447 | -122.0397 | -0.12295 | -0.22222 | 0.1384 | 0.012318 | 0.13527 | 0.062393 | -0.053449 | 0.1208 | 0.15603 | 0.261 | 0.070076 | -122.3455 | 122.0785 | 122.3631 | 122.2473 | 0.98019 | -122.4237
4040.875 | 122.3694 | -0.10529 | 122.2824 | -0.010149 | -0.055239 | 0.039225 | 0.017973 | -0.014001 | -0.0037989 | -0.021518 | -0.0022666 | -0.0025041 | 0.057405 | 0.049448 | 0.046406 | -0.017266 | 0.019721 | -0.012988 | 0.070441 | 0.11025 | 0.22896 | -0.090531 | 0.097201 | 0.93442 | -0.028879 | 122.0373 | 122.3128 | 122.2061 | -0.16415 | 0.014755 | -122.212 | 0.08802 | 0.092298 | 0.077543 | -122.1722 | -122.0535 | -0.058863 | -0.2451 | 0.20249 | 0.076407 | 0.13527 | 0.030348 | -0.076337 | 0.17573 | 0.21554 | 0.33425 | 0.12501 | -122.3729 | 122.1426 | 122.418 | 122.3114 | 1.0397 | -122.4466
4042.6406 | 122.3465 | -0.10071 | 122.2824 | -0.010149 | -0.055453 | 0.039225 | 0.018614 | -0.013788 | -0.0037989 | -0.021518 | -0.0022666 | -0.0020767 | 0.057191 | 0.049448 | 0.046619 | -0.008109 | 0.028878 | -0.017566 | 0.079598 | 0.11941 | 0.22438 | -0.099689 | 0.097201 | 0.93899 | -0.019721 | 122.0327 | 122.3128 | 122.2061 | -0.15957 | 0.001019 | -122.2028 | 0.092599 | 0.083142 | 0.082123 | -122.163 | -122.058 | -0.058862 | -0.24968 | 0.19791 | 0.080987 | 0.13985 | 0.030348 | -0.076337 | 0.18031 | 0.22012 | 0.32509 | 0.12959 | -122.3821 | 122.1334 | 122.4135 | 122.3068 | 1.0397 | -122.442
4044.3438 | 122.4655 | -0.045776 | 122.2687 | -0.01778 | -0.055453 | 0.039225 | 0.018187 | -0.013788 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.057405 | 0.049448 | 0.046406 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.11941 | 0.2198 | -0.090531 | 0.088043 | 0.93442 | -0.028879 | 122.0327 | 122.3265 | 122.2015 | -0.17331 | -0.044755 | -122.1845 | 0.02851 | 0.02821 | 0.072965 | -122.1493 | -122.0489 | -0.12753 | -0.23595 | 0.13382 | 0.016897 | 0.14443 | 0.057817 | -0.067182 | 0.12995 | 0.16519 | 0.26558 | 0.070076 | -122.3592 | 122.0785 | 122.3723 | 122.2473 | 0.98019 | -122.442
4046.1094 | 122.4335 | -0.068665 | 122.2641 | 0.0051128 | -0.055025 | 0.039011 | 0.018187 | -0.014001 | -0.0040125 | -0.021518 | -0.002694 | -0.0020767 | 0.057191 | 0.049448 | 0.046406 | -0.021844 | 0.0243 | -0.017566 | 0.070441 | 0.11025 | 0.22896 | -0.090531 | 0.092622 | 0.93899 | -0.033458 | 122.0419 | 122.3173 | 122.1878 | -0.16873 | -0.021866 | -122.1937 | 0.046821 | 0.051099 | 0.072965 | -122.1538 | -122.0351 | -0.10006 | -0.22222 | 0.16129 | 0.035207 | 0.13527 | 0.053238 | -0.07634 | 0.13911 | 0.17892 | 0.29762 | 0.092965 | -122.3546 | 122.1105 | 122.386 | 122.2564 | 1.0077 | -122.4328
4047.7969 | 122.3969 | -0.07782 | 122.2549 | -0.0025182 | -0.055666 | 0.039439 | 0.017973 | -0.013574 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.057191 | 0.049448 | 0.046619 | -0.017266 | 0.0243 | -0.017566 | 0.079598 | 0.11483 | 0.22438 | -0.090531 | 0.097201 | 0.93899 | -0.033458 | 122.0327 | 122.3173 | 122.2015 | -0.16415 | -0.012711 | -122.1753 | 0.060554 | 0.060254 | 0.072965 | -122.1401 | -122.0306 | -0.086329 | -0.22222 | 0.17502 | 0.044362 | 0.13069 | 0.062393 | -0.053449 | 0.15742 | 0.19265 | 0.3022 | 0.10212 | -122.3455 | 122.1105 | 122.3952 | 122.2793 | 1.0168 | -122.4191
4049.5625 | 122.3282 | -0.091553 | 122.2961 | -0.0025182 | -0.055666 | 0.039011 | 0.0184 | -0.013788 | -0.0033715 | -0.013887 | -0.0024804 | -0.0025041 | 0.056978 | 0.049234 | 0.046406 | -0.012688 | 0.028878 | -0.017566 | 0.065863 | 0.11941 | 0.23354 | -0.09511 | 0.092622 | 0.94357 | -0.028879 | 122.0327 | 122.3173 | 122.1969 | -0.15957 | -0.003557 | -122.2303 | 0.078865 | 0.073987 | 0.077544 | -122.1767 | -122.0626 | -0.068017 | -0.26342 | 0.18417 | 0.062674 | 0.13069 | 0.021194 | -0.099227 | 0.15742 | 0.21096 | 0.32509 | 0.12043 | -122.3913 | 122.1243 | 122.4089 | 122.2885 | 1.0351 | -122.4557
4051.3281 | 122.3602 | -0.10071 | 122.2778 | -0.0025182 | -0.055666 | 0.039011 | 0.017973 | -0.014001 | -0.0035853 | -0.013887 | -0.002694 | -0.0020767 | 0.057405 | 0.049448 | 0.047046 | -0.012688 | 0.033457 | -0.017566 | 0.07502 | 0.11941 | 0.2198 | -0.090531 | 0.092622 | 0.94357 | -0.028879 | 122.0327 | 122.3173 | 122.2015 | -0.16873 | 0.010177 | -122.2028 | 0.08802 | 0.083142 | 0.072965 | -122.1584 | -122.058 | -0.06802 | -0.24511 | 0.19333 | 0.071829 | 0.13985 | 0.039505 | -0.076337 | 0.17573 | 0.22012 | 0.32051 | 0.13417 | -122.3684 | 122.1334 | 122.418 | 122.3022 | 1.0443 | -122.4466
4053.0938 | 122.4609 | -0.054932 | 122.2824 | -0.010149 | -0.055666 | 0.039011 | 0.018187 | -0.01336 | -0.0031579 | -0.029148 | -0.0022666 | -0.0022903 | 0.057191 | 0.049448 | 0.046406 | -0.021844 | 0.028878 | -0.017566 | 0.079598 | 0.11025 | 0.22438 | -0.090531 | 0.092622 | 0.94357 | -0.028879 | 122.0373 | 122.3128 | 122.1969 | -0.16415 | -0.035599 | -122.2028 | 0.033088 | 0.037366 | 0.072965 | -122.1722 | -122.058 | -0.10922 | -0.2451 | 0.14755 | 0.026053 | 0.13527 | 0.030348 | -0.085494 | 0.13453 | 0.16518 | 0.27931 | 0.08381 | -122.3729 | 122.0922 | 122.3677 | 122.2518 | 0.9985 | -122.4466
4054.7812 | 122.3511 | -0.082397 | 122.2778 | -0.01778 | -0.055239 | 0.039225 | 0.018187 | -0.014215 | -0.0040125 | -0.013887 | -0.0022666 | -0.0022903 | 0.057191 | 0.049234 | 0.046406 | -0.008109 | 0.0243 | -0.012988 | 0.079598 | 0.11025 | 0.22438 | -0.085952 | 0.092622 | 0.94357 | -0.0243 | 122.0419 | 122.3173 | 122.2015 | -0.16873 | -0.003555 | -122.1982 | 0.074288 | 0.069409 | 0.072964 | -122.1676 | -122.0535 | -0.086331 | -0.23595 | 0.17502 | 0.058097 | 0.14443 | 0.039505 | -0.076337 | 0.162 | 0.19265 | 0.30678 | 0.1067 | -122.3638 | 122.1243 | 122.3997 | 122.2839 | 1.026 | -122.4466
4056.5625 | 122.4197 | -0.064087 | 122.2595 | -0.010149 | -0.055453 | 0.039225 | 0.018187 | -0.014215 | -0.0033715 | -0.013887 | -0.0024804 | -0.0020767 | 0.057191 | 0.049875 | 0.046619 | -0.012688 | 0.019721 | -0.022144 | 0.07502 | 0.11941 | 0.22896 | -0.09511 | 0.088043 | 0.95273 | -0.0243 | 122.0281 | 122.3082 | 122.2015 | -0.16873 | -0.031023 | -122.1845 | 0.051399 | 0.041943 | 0.072966 | -122.1401 | -122.0306 | -0.10464 | -0.23137 | 0.15213 | 0.039787 | 0.14443 | 0.048659 | -0.058026 | 0.13911 | 0.1835 | 0.29305 | 0.083808 | -122.3546 | 122.0922 | 122.3723 | 122.2656 | 1.0168 | -122.4282
4058.3281 | 122.4792 | -0.045776 | 122.2321 | -0.01778 | -0.055239 | 0.039225 | 0.0184 | -0.013574 | -0.0035853 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.049234 | 0.046406 | -0.017266 | 0.0243 | -0.022144 | 0.084176 | 0.11025 | 0.22438 | -0.090531 | 0.092622 | 0.95273 | -0.033458 | 122.0419 | 122.3219 | 122.2015 | -0.17331 | -0.044755 | -122.1479 | 0.02851 | 0.023632 | 0.068387 | -122.1218 | -122.0077 | -0.12753 | -0.19017 | 0.1384 | 0.012318 | 0.13985 | 0.08986 | -0.030561 | 0.12995 | 0.15603 | 0.27016 | 0.070076 | -122.3226 | 122.0877 | 122.3677 | 122.2473 | 0.99851 | -122.4054
4060.0938 | 122.3557 | -0.086975 | 122.319 | -0.0025182 | -0.055666 | 0.038798 | 0.018187 | -0.013574 | -0.0035853 | -0.029148 | -0.0024804 | -0.0020767 | 0.056978 | 0.049662 | 0.046406 | -0.012688 | 0.0243 | -0.017566 | 0.079598 | 0.11483 | 0.2198 | -0.085952 | 0.088043 | 0.95273 | -0.0243 | 122.0373 | 122.3265 | 122.1969 | -0.17331 | 0.001023 | -122.2394 | 0.074287 | 0.069409 | 0.068386 | -122.2042 | -122.0992 | -0.086331 | -0.28172 | 0.17502 | 0.062675 | 0.14901 | 0.007463 | -0.12211 | 0.16657 | 0.20181 | 0.30678 | 0.11127 | -122.405 | 122.1243 | 122.4135 | 122.2839 | 1.0397 | -122.4923
4061.7969 | 122.4884 | -0.07782 | 122.2504 | -0.0025182 | -0.055025 | 0.039011 | 0.017973 | -0.014001 | -0.0033715 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.049448 | 0.046406 | -0.017266 | 0.015142 | -0.012988 | 0.070441 | 0.11483 | 0.22896 | -0.09511 | 0.092622 | 0.95273 | -0.028879 | 122.0465 | 122.3219 | 122.1969 | -0.16873 | -0.01729 | -122.1799 | 0.060554 | 0.064832 | 0.082122 | -122.1355 | -122.0214 | -0.090908 | -0.2039 | 0.17044 | 0.048941 | 0.13985 | 0.07155 | -0.05345 | 0.14826 | 0.19265 | 0.30678 | 0.092962 | -122.3455 | 122.1243 | 122.3997 | 122.2747 | 1.0306 | -122.4191
4063.5938 | 122.4106 | -0.068665 | 122.2504 | -0.025411 | -0.055453 | 0.039011 | 0.017973 | -0.014001 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.057405 | 0.049234 | 0.046406 | -0.026423 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.22896 | -0.099689 | 0.092622 | 0.95731 | -0.028879 | 122.0373 | 122.3173 | 122.2061 | -0.16873 | -0.031024 | -122.1708 | 0.042242 | 0.051099 | 0.082123 | -122.131 | -122.0214 | -0.10006 | -0.21306 | 0.16129 | 0.039786 | 0.13985 | 0.066971 | -0.044293 | 0.14826 | 0.18808 | 0.29762 | 0.092965 | -122.3501 | 122.106 | 122.386 | 122.2747 | 1.026 | -122.4191
4065.3906 | 122.4014 | -0.041199 | 122.2549 | -0.01778 | -0.055239 | 0.038798 | 0.018187 | -0.013788 | -0.0037989 | -0.021518 | -0.0022666 | -0.0022903 | 0.057405 | 0.049875 | 0.046406 | -0.017266 | 0.028878 | -0.022144 | 0.07502 | 0.11025 | 0.22438 | -0.085952 | 0.092622 | 0.96647 | -0.033458 | 122.0327 | 122.3173 | 122.2015 | -0.16873 | -0.044753 | -122.1799 | 0.023933 | 0.019055 | 0.063808 | -122.1447 | -122.0306 | -0.12753 | -0.22222 | 0.13382 | 0.007741 | 0.13527 | 0.062393 | -0.053449 | 0.11622 | 0.15145 | 0.26558 | 0.070077 | -122.3409 | 122.0739 | 122.3585 | 122.2427 | 1.0077 | -122.4237
4067.1406 | 122.3602 | -0.10529 | 122.2961 | -0.0025182 | -0.055453 | 0.039011 | 0.017973 | -0.014001 | -0.0035853 | -0.013887 | -0.002694 | -0.0020767 | 0.057191 | 0.049234 | 0.046406 | -0.021844 | 0.028878 | -0.012988 | 0.07502 | 0.11483 | 0.22438 | -0.090531 | 0.092622 | 0.96647 | -0.0243 | 122.0419 | 122.3219 | 122.2015 | -0.15957 | 0.014755 | -122.2211 | 0.083442 | 0.092298 | 0.077543 | -122.1813 | -122.0718 | -0.054284 | -0.25426 | 0.19791 | 0.080986 | 0.13527 | 0.025773 | -0.094648 | 0.18031 | 0.22012 | 0.32967 | 0.13416 | -122.3867 | 122.1472 | 122.4272 | 122.3068 | 1.0718 | -122.4557
4068.8438 | 122.4243 | -0.050354 | 122.2549 | -0.010149 | -0.055453 | 0.038798 | 0.0184 | -0.013788 | -0.0033715 | -0.013887 | -0.002053 | -0.0027177 | 0.057191 | 0.049448 | 0.046192 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.12399 | 0.22438 | -0.090531 | 0.088043 | 0.96647 | -0.0243 | 122.0373 | 122.3311 | 122.2015 | -0.17331 | -0.040177 | -122.1753 | 0.02851 | 0.037366 | 0.077543 | -122.131 | -122.0306 | -0.12295 | -0.21764 | 0.1384 | 0.026054 | 0.14901 | 0.076129 | -0.053449 | 0.12995 | 0.17434 | 0.27474 | 0.074654 | -122.3455 | 122.0877 | 122.3814 | 122.2518 | 1.0168 | -122.4282
4070.6094 | 122.4701 | -0.054932 | 122.2549 | 0.0051128 | -0.055453 | 0.039225 | 0.017759 | -0.014001 | -0.0033715 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.049448 | 0.046192 | -0.012688 | 0.028878 | -0.022144 | 0.07502 | 0.12399 | 0.22896 | -0.09511 | 0.092622 | 0.97105 | -0.028879 | 122.0419 | 122.3265 | 122.1969 | -0.16873 | -0.040178 | -122.1799 | 0.042244 | 0.032788 | 0.072966 | -122.131 | -122.026 | -0.1138 | -0.21306 | 0.14755 | 0.026053 | 0.13985 | 0.07155 | -0.058028 | 0.12995 | 0.17892 | 0.28389 | 0.08381 | -122.3501 | 122.0968 | 122.3814 | 122.2518 | 1.026 | -122.4237
4072.375 | 122.3969 | -0.073242 | 122.2687 | 0.0051128 | -0.055666 | 0.03837 | 0.017973 | -0.013574 | -0.0035853 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.049662 | 0.046619 | -0.017266 | 0.028878 | -0.012988 | 0.079598 | 0.11941 | 0.22438 | -0.085952 | 0.092622 | 0.96647 | -0.028879 | 122.0419 | 122.3173 | 122.1969 | -0.16873 | -0.01271 | -122.1891 | 0.055976 | 0.060254 | 0.072964 | -122.1493 | -122.0443 | -0.095486 | -0.22679 | 0.16586 | 0.044363 | 0.13985 | 0.04866 | -0.071761 | 0.15284 | 0.19265 | 0.29762 | 0.10212 | -122.3546 | 122.1151 | 122.3906 | 122.2702 | 1.0397 | -122.4374
4074.1562 | 122.3648 | -0.082397 | 122.2549 | -0.010149 | -0.055453 | 0.039225 | 0.017973 | -0.014215 | -0.0033715 | -0.013887 | -0.0022666 | -0.0025041 | 0.057405 | 0.049662 | 0.046406 | -0.012688 | 0.019721 | -0.012988 | 0.079598 | 0.11483 | 0.21522 | -0.090531 | 0.088043 | 0.97562 | -0.033458 | 122.0327 | 122.3265 | 122.2061 | -0.16415 | -0.008134 | -122.1753 | 0.069709 | 0.069409 | 0.077543 | -122.1401 | -122.0397 | -0.081752 | -0.22222 | 0.17044 | 0.048939 | 0.13069 | 0.07155 | -0.048871 | 0.162 | 0.19723 | 0.29762 | 0.10212 | -122.3455 | 122.1151 | 122.4089 | 122.2885 | 1.058 | -122.4191
4075.8594 | 122.493 | -0.064087 | 122.2412 | -0.01778 | -0.055239 | 0.039225 | 0.018187 | -0.013788 | -0.0035853 | -0.013887 | -0.0024804 | -0.0020767 | 0.057191 | 0.049875 | 0.046406 | -0.017266 | 0.019721 | -0.022144 | 0.07502 | 0.11025 | 0.23354 | -0.09511 | 0.083464 | 0.97105 | -0.028879 | 122.0419 | 122.3219 | 122.1969 | -0.15957 | -0.031023 | -122.1662 | 0.046821 | 0.041943 | 0.072966 | -122.131 | -122.0077 | -0.095483 | -0.19933 | 0.14755 | 0.035208 | 0.13069 | 0.080705 | -0.044295 | 0.13911 | 0.17434 | 0.29763 | 0.083808 | -122.3363 | 122.106 | 122.386 | 122.261 | 1.0351 | -122.4008
4077.625 | 122.3557 | -0.09613 | 122.2778 | -0.010149 | -0.055666 | 0.038798 | 0.018187 | -0.013788 | -0.0037989 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.049662 | 0.046406 | -0.012688 | 0.0243 | -0.017566 | 0.07502 | 0.11483 | 0.2198 | -0.09511 | 0.088043 | 0.97562 | -0.038036 | 122.0419 | 122.3173 | 122.1969 | -0.17331 | 0.00102 | -122.2028 | 0.083442 | 0.078564 | 0.077544 | -122.163 | -122.058 | -0.077176 | -0.23595 | 0.18417 | 0.058094 | 0.13527 | 0.039505 | -0.080916 | 0.17115 | 0.21096 | 0.31593 | 0.12043 | -122.3729 | 122.138 | 122.4135 | 122.293 | 1.0718 | -122.4511
4079.3906 | 122.3465 | -0.10529 | 122.2595 | -0.01778 | -0.055666 | 0.039439 | 0.017759 | -0.014215 | -0.0031579 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.049875 | 0.046406 | -0.008109 | 0.0243 | -0.017566 | 0.07502 | 0.11025 | 0.22896 | -0.090531 | 0.097201 | 0.98478 | -0.028879 | 122.0327 | 122.3173 | 122.2061 | -0.16415 | 0.014755 | -122.1845 | 0.097177 | 0.08772 | 0.072965 | -122.1493 | -122.0306 | -0.058863 | -0.22679 | 0.20249 | 0.076407 | 0.13527 | 0.057816 | -0.053448 | 0.18031 | 0.21554 | 0.33425 | 0.12959 | -122.3501 | 122.138 | 122.4226 | 122.3114 | 1.0901 | -122.4237
4081.2031 | 122.4747 | -0.045776 | 122.2275 | -0.010149 | -0.055666 | 0.039011 | 0.018187 | -0.013788 | -0.0031579 | -0.021518 | -0.002053 | -0.0020767 | 0.057405 | 0.049662 | 0.046406 | -0.017266 | 0.0243 | -0.012988 | 0.07502 | 0.11941 | 0.22438 | -0.085952 | 0.088043 | 0.94815 | -0.0243 | 122.0373 | 122.3128 | 122.1878 | -0.16415 | -0.040176 | -122.1525 | 0.02851 | 0.032788 | 0.072964 | -122.1081 | -122.0031 | -0.11837 | -0.19017 | 0.13382 | 0.021476 | 0.13985 | 0.08528 | -0.039719 | 0.1208 | 0.16519 | 0.27016 | 0.070076 | -122.3134 | 122.0831 | 122.3585 | 122.2335 | 0.99393 | -122.3916
4082.9844 | 122.3282 | -0.091553 | 122.2916 | -0.010149 | -0.055239 | 0.038798 | 0.017973 | -0.014215 | -0.0033715 | -0.021518 | -0.0024804 | -0.0025041 | 0.057619 | 0.049448 | 0.046406 | -0.021844 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.22438 | -0.09511 | 0.097201 | 0.95273 | -0.019721 | 122.0373 | 122.3128 | 122.1969 | -0.16873 | -0.003557 | -122.212 | 0.069709 | 0.073987 | 0.077544 | -122.1722 | -122.0672 | -0.077175 | -0.25426 | 0.18875 | 0.071832 | 0.14901 | 0.021193 | -0.094649 | 0.17115 | 0.21096 | 0.31593 | 0.11585 | -122.3867 | 122.1289 | 122.4043 | 122.2885 | 1.0443 | -122.4603
4084.7031 | 122.4289 | -0.054932 | 122.2733 | -0.010149 | -0.055453 | 0.039011 | 0.017759 | -0.014001 | -0.0033715 | -0.021518 | -0.002694 | -0.0020767 | 0.057405 | 0.049234 | 0.046619 | -0.012688 | 0.0243 | -0.022144 | 0.079598 | 0.11941 | 0.22896 | -0.09511 | 0.097201 | 0.95731 | -0.028879 | 122.0373 | 122.3173 | 122.1923 | -0.16873 | -0.040178 | -122.1937 | 0.042244 | 0.032788 | 0.072966 | -122.1538 | -122.0443 | -0.1138 | -0.23595 | 0.15213 | 0.026053 | 0.13985 | 0.044083 | -0.080917 | 0.13453 | 0.17434 | 0.28389 | 0.079232 | -122.3684 | 122.0922 | 122.3723 | 122.2473 | 1.0122 | -122.442
4086.4219 | 122.3923 | -0.11902 | 122.2733 | -0.010149 | -0.055666 | 0.038798 | 0.017973 | -0.013788 | -0.0031579 | -0.021518 | -0.0029076 | -0.0020767 | 0.057405 | 0.049875 | 0.046619 | -0.017266 | 0.0243 | -0.017566 | 0.070441 | 0.11483 | 0.2198 | -0.09511 | 0.088043 | 0.95273 | -0.033458 | 122.0327 | 122.3219 | 122.2015 | -0.16415 | 0.023909 | -122.2028 | 0.10175 | 0.10145 | 0.077544 | -122.1584 | -122.0535 | -0.04513 | -0.24053 | 0.20706 | 0.085561 | 0.13069 | 0.048662 | -0.071759 | 0.18946 | 0.23385 | 0.33882 | 0.14332 | -122.3684 | 122.1517 | 122.4409 | 122.3205 | 1.0717 | -122.4374
4088.1719 | 122.4747 | -0.054932 | 122.1954 | -0.01778 | -0.055666 | 0.039011 | 0.017759 | -0.014001 | -0.0031579 | -0.029148 | -0.0024804 | -0.0018631 | 0.057191 | 0.049662 | 0.046406 | -0.021844 | 0.033457 | -0.017566 | 0.070441 | 0.11941 | 0.22438 | -0.090531 | 0.092622 | 0.95731 | -0.028879 | 122.0373 | 122.3219 | 122.1969 | -0.16415 | -0.035599 | -122.125 | 0.033088 | 0.037366 | 0.072965 | -122.076 | -121.9711 | -0.10922 | -0.15813 | 0.14755 | 0.026053 | 0.13527 | 0.12648 | 0.001481 | 0.12537 | 0.17434 | 0.27931 | 0.088389 | -122.286 | 122.0922 | 122.3768 | 122.2518 | 1.0122 | -122.3596
4089.875 | 122.438 | -0.07782 | 122.2412 | -0.010149 | -0.055453 | 0.039225 | 0.017973 | -0.014429 | -0.0033715 | -0.0062567 | -0.0024804 | -0.0022903 | 0.057191 | 0.049662 | 0.046406 | -0.021844 | 0.0243 | -0.017566 | 0.07502 | 0.11941 | 0.22438 | -0.085952 | 0.097201 | 0.96647 | -0.028879 | 122.0327 | 122.3128 | 122.2015 | -0.17331 | -0.008132 | -122.1662 | 0.055976 | 0.060254 | 0.068386 | -122.1218 | -122.0168 | -0.095486 | -0.20848 | 0.17502 | 0.048941 | 0.14443 | 0.071547 | -0.039716 | 0.15284 | 0.19723 | 0.3022 | 0.10212 | -122.3272 | 122.1105 | 122.3906 | 122.2793 | 1.0443 | -122.4145
4091.625 | 122.3877 | -0.082397 | 122.2824 | -0.010149 | -0.055666 | 0.038798 | 0.018187 | -0.013788 | -0.0033715 | -0.013887 | -0.002053 | -0.0022903 | 0.057405 | 0.049662 | 0.046192 | -0.012688 | 0.015142 | -0.017566 | 0.079598 | 0.11483 | 0.22438 | -0.09511 | 0.097201 | 0.95731 | -0.033458 | 122.0373 | 122.3219 | 122.2015 | -0.16415 | -0.012713 | -122.2028 | 0.069709 | 0.064831 | 0.077544 | -122.1676 | -122.058 | -0.081752 | -0.2451 | 0.1796 | 0.048939 | 0.13069 | 0.039506 | -0.080915 | 0.162 | 0.19723 | 0.30678 | 0.097539 | -122.3775 | 122.1197 | 122.4043 | 122.2839 | 1.0397 | -122.4466
4093.3281 | 122.3877 | -0.10071 | 122.2687 | -0.01778 | -0.055666 | 0.038798 | 0.017759 | -0.014001 | -0.0033715 | -0.021518 | -0.002694 | -0.0027177 | 0.057191 | 0.049662 | 0.046192 | -0.008109 | 0.0243 | -0.017566 | 0.079598 | 0.11483 | 0.2198 | -0.099689 | 0.097201 | 0.96189 | -0.028879 | 122.0373 | 122.3128 | 122.1969 | -0.16873 | 0.001019 | -122.1891 | 0.092599 | 0.083142 | 0.082123 | -122.1538 | -122.0489 | -0.06802 | -0.23137 | 0.19791 | 0.071829 | 0.13985 | 0.044081 | -0.071761 | 0.18031 | 0.21554 | 0.32051 | 0.12501 | -122.3684 | 122.138 | 122.4135 | 122.2976 | 1.0626 | -122.4374
4095.0312 | 122.4426 | -0.059509 | 122.2916 | -0.010149 | -0.055666 | 0.038798 | 0.017546 | -0.014429 | -0.0035853 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.049448 | 0.046619 | -0.012688 | 0.0243 | -0.017566 | 0.07502 | 0.11025 | 0.22438 | -0.090531 | 0.092622 | 0.95731 | -0.033458 | 122.0419 | 122.3265 | 122.1969 | -0.17331 | -0.031022 | -122.2165 | 0.046821 | 0.041943 | 0.072965 | -122.1813 | -122.0672 | -0.1138 | -0.24968 | 0.15213 | 0.026051 | 0.13985 | 0.034929 | -0.094649 | 0.13453 | 0.16976 | 0.28389 | 0.083809 | -122.3821 | 122.1014 | 122.386 | 122.2564 | 1.0168 | -122.4649
4096.7188 | 122.3602 | -0.10529 | 122.2733 | -0.010149 | -0.055666 | 0.039011 | 0.017973 | -0.014001 | -0.0033715 | -0.013887 | -0.0022666 | -0.0018631 | 0.057191 | 0.049875 | 0.046406 | -0.017266 | 0.028878 | -0.012988 | 0.079598 | 0.11941 | 0.23354 | -0.09511 | 0.088043 | 0.97105 | -0.038036 | 122.0327 | 122.3219 | 122.1969 | -0.16873 | 0.010176 | -122.1937 | 0.08802 | 0.092298 | 0.082122 | -122.1538 | -122.0397 | -0.063442 | -0.24053 | 0.19333 | 0.06725 | 0.13069 | 0.048662 | -0.076338 | 0.18488 | 0.2247 | 0.33882 | 0.13416 | -122.3684 | 122.138 | 122.4272 | 122.3022 | 1.0763 | -122.442
4098.4219 | 122.4838 | -0.068665 | 122.2504 | -0.010149 | -0.055666 | 0.039439 | 0.0184 | -0.014215 | -0.0031579 | -0.013887 | -0.002694 | -0.0020767 | 0.056978 | 0.050089 | 0.046406 | -0.012688 | 0.0243 | -0.012988 | 0.07502 | 0.12399 | 0.22896 | -0.090531 | 0.092622 | 0.96647 | -0.033458 | 122.0327 | 122.3265 | 122.1969 | -0.16873 | -0.021866 | -122.1753 | 0.055977 | 0.055677 | 0.077543 | -122.1264 | -122.0214 | -0.10006 | -0.21764 | 0.16129 | 0.035207 | 0.13527 | 0.076128 | -0.05345 | 0.14369 | 0.19266 | 0.29762 | 0.092965 | -122.3409 | 122.1014 | 122.3952 | 122.2656 | 1.0351 | -122.4191
4100.125 | 122.374 | -0.086975 | 122.287 | -0.0025182 | -0.055666 | 0.039225 | 0.018187 | -0.013788 | -0.0035853 | -0.013887 | -0.0024804 | -0.0022903 | 0.057191 | 0.049662 | 0.046619 | -0.008109 | 0.0243 | -0.017566 | 0.07502 | 0.11483 | 0.23354 | -0.090531 | 0.097201 | 0.97105 | -0.0243 | 122.0327 | 122.3219 | 122.1969 | -0.16873 | -0.003556 | -122.212 | 0.078866 | 0.069409 | 0.072965 | -122.1722 | -122.0534 | -0.081753 | -0.25426 | 0.18418 | 0.062675 | 0.14443 | 0.034929 | -0.090071 | 0.162 | 0.20181 | 0.32051 | 0.11127 | -122.3775 | 122.1197 | 122.4089 | 122.2839 | 1.058 | -122.4557
4101.8281 | 122.4838 | -0.050354 | 122.2504 | -0.010149 | -0.055666 | 0.039011 | 0.017973 | -0.014001 | -0.0031579 | -0.013887 | -0.002694 | -0.0020767 | 0.057191 | 0.049662 | 0.046406 | -0.026423 | 0.028878 | -0.022144 | 0.07502 | 0.11941 | 0.23354 | -0.09511 | 0.092622 | 0.96647 | -0.028879 | 122.0373 | 122.3219 | 122.2015 | -0.15957 | -0.044756 | -122.1753 | 0.023931 | 0.02821 | 0.072966 | -122.131 | -122.0168 | -0.10922 | -0.21306 | 0.14298 | 0.021475 | 0.13069 | 0.07155 | -0.048871 | 0.12537 | 0.16976 | 0.28389 | 0.079232 | -122.3455 | 122.0877 | 122.3723 | 122.2518 | 1.0168 | -122.4099
4103.5781 | 122.4518 | -0.050354 | 122.2458 | -0.0025182 | -0.055666 | 0.038584 | 0.017759 | -0.013788 | -0.0033715 | -0.029148 | -0.0024804 | -0.0022903 | 0.057405 | 0.049662 | 0.046192 | -0.012688 | 0.0243 | -0.017566 | 0.079598 | 0.11483 | 0.22438 | -0.099689 | 0.10178 | 0.98478 | -0.028879 | 122.0419 | 122.3265 | 122.1969 | -0.16873 | -0.049335 | -122.1662 | 0.037666 | 0.032788 | 0.082123 | -122.131 | -122.0214 | -0.11837 | -0.20391 | 0.15213 | 0.021475 | 0.13985 | 0.080705 | -0.048873 | 0.12995 | 0.16519 | 0.27474 | 0.074654 | -122.3455 | 122.0922 | 122.3768 | 122.2473 | 1.0351 | -122.4145
4105.2812 | 122.3648 | -0.09613 | 122.2733 | -0.010149 | -0.05588 | 0.038584 | 0.017973 | -0.014001 | -0.0033715 | -0.013887 | -0.0022666 | -0.0022903 | 0.056978 | 0.049875 | 0.046406 | -0.021844 | 0.0243 | -0.022144 | 0.079598 | 0.11941 | 0.22896 | -0.085952 | 0.083464 | 0.9802 | -0.033458 | 122.0419 | 122.3219 | 122.2015 | -0.16873 | 0.010178 | -122.1937 | 0.074286 | 0.073986 | 0.063808 | -122.1538 | -122.0443 | -0.072598 | -0.23137 | 0.17959 | 0.062672 | 0.13527 | 0.048662 | -0.071759 | 0.17573 | 0.21554 | 0.32509 | 0.12043 | -122.3592 | 122.138 | 122.418 | 122.2976 | 1.0763 | -122.442
4106.9844 | 122.4609 | -0.045776 | 122.2549 | -0.010149 | -0.05588 | 0.038798 | 0.017973 | -0.014001 | -0.0033715 | -0.021518 | -0.002694 | -0.0022903 | 0.056978 | 0.049662 | 0.046192 | -0.012688 | 0.028878 | -0.012988 | 0.084176 | 0.11483 | 0.22896 | -0.099689 | 0.097201 | 0.9802 | -0.038036 | 122.0373 | 122.3173 | 122.1969 | -0.16873 | -0.053913 | -122.1708 | 0.033088 | 0.032788 | 0.086701 | -122.1401 | -122.026 | -0.12295 | -0.21764 | 0.14298 | 0.00774 | 0.13069 | 0.062393 | -0.058028 | 0.12995 | 0.16061 | 0.27474 | 0.074654 | -122.3546 | 122.0831 | 122.3631 | 122.2427 | 1.026 | -122.4237
4108.6875 | 122.3511 | -0.09613 | 122.2687 | -0.01778 | -0.055453 | 0.038584 | 0.017546 | -0.014215 | -0.0031579 | -0.013887 | -0.0024804 | -0.0020767 | 0.057405 | 0.049662 | 0.046192 | -0.012688 | 0.019721 | -0.017566 | 0.07502 | 0.11941 | 0.22896 | -0.090531 | 0.092622 | 0.98936 | -0.033458 | 122.0373 | 122.3219 | 122.2015 | -0.16873 | 0.005599 | -122.1937 | 0.083442 | 0.078564 | 0.072965 | -122.1493 | -122.0397 | -0.072598 | -0.23137 | 0.18875 | 0.062672 | 0.13527 | 0.053239 | -0.067182 | 0.17115 | 0.21554 | 0.32509 | 0.11585 | -122.3592 | 122.1334 | 122.418 | 122.2976 | 1.0855 | -122.4374
4110.375 | 122.4564 | -0.054932 | 122.2458 | -0.010149 | -0.055666 | 0.038798 | 0.017973 | -0.013788 | -0.0031579 | -0.021518 | -0.002694 | -0.0020767 | 0.057619 | 0.049448 | 0.046406 | -0.017266 | 0.0243 | -0.022144 | 0.079598 | 0.12399 | 0.22896 | -0.090531 | 0.092622 | 0.98936 | -0.033458 | 122.0373 | 122.3128 | 122.1969 | -0.16873 | -0.035599 | -122.1662 | 0.037666 | 0.032788 | 0.068387 | -122.1218 | -122.0168 | -0.1138 | -0.20848 | 0.14755 | 0.021474 | 0.13527 | 0.066969 | -0.048873 | 0.13453 | 0.17892 | 0.28389 | 0.079232 | -122.3363 | 122.0922 | 122.3677 | 122.2518 | 1.0443 | -122.4145
4112.0781 | 122.4014 | -0.10986 | 122.287 | -0.010149 | -0.055666 | 0.039011 | 0.017973 | -0.014001 | -0.0033715 | -0.021518 | -0.002694 | -0.0020767 | 0.057405 | 0.049875 | 0.046406 | -0.012688 | 0.0243 | -0.022144 | 0.084176 | 0.11483 | 0.22896 | -0.09511 | 0.10178 | 0.98936 | -0.028879 | 122.0373 | 122.3219 | 122.1969 | -0.17331 | 0.014753 | -122.2028 | 0.097175 | 0.087719 | 0.072966 | -122.1722 | -122.058 | -0.063443 | -0.24968 | 0.21164 | 0.080984 | 0.14443 | 0.034929 | -0.090071 | 0.19404 | 0.2247 | 0.33882 | 0.13416 | -122.3821 | 122.1472 | 122.4318 | 122.3068 | 1.0992 | -122.4603
4113.7812 | 122.4655 | -0.045776 | 122.2183 | -0.01778 | -0.056094 | 0.039225 | 0.018187 | -0.014001 | -0.0031579 | -0.0062567 | -0.002694 | -0.0022903 | 0.057191 | 0.050089 | 0.045978 | -0.021844 | 0.0243 | -0.022144 | 0.079598 | 0.11483 | 0.22896 | -0.099689 | 0.092622 | 0.98936 | -0.028879 | 122.0373 | 122.3219 | 122.2015 | -0.16415 | -0.053913 | -122.1387 | 0.023932 | 0.023632 | 0.077545 | -122.1035 | -121.9894 | -0.11837 | -0.18102 | 0.1384 | 0.016897 | 0.13527 | 0.10359 | -0.016828 | 0.12537 | 0.16061 | 0.27474 | 0.070076 | -122.318 | 122.0831 | 122.3677 | 122.2473 | 1.0351 | -122.3825
4115.5312 | 122.4152 | -0.068665 | 122.2412 | -0.010149 | -0.05588 | 0.039225 | 0.017759 | -0.014215 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.057191 | 0.049875 | 0.045978 | -0.017266 | 0.0243 | -0.017566 | 0.07502 | 0.12399 | 0.22896 | -0.085952 | 0.10178 | 0.99852 | -0.033458 | 122.0327 | 122.3173 | 122.2015 | -0.17331 | -0.017287 | -122.1662 | 0.051399 | 0.051099 | 0.068386 | -122.1172 | -122.0123 | -0.10464 | -0.20848 | 0.17044 | 0.035207 | 0.13985 | 0.076126 | -0.039716 | 0.14369 | 0.19266 | 0.29762 | 0.092965 | -122.3272 | 122.1014 | 122.386 | 122.2702 | 1.0672 | -122.4145
4117.2344 | 122.4747 | -0.054932 | 122.2641 | -0.0025182 | -0.055453 | 0.039225 | 0.017759 | -0.014001 | -0.0037989 | -0.013887 | -0.0022666 | -0.0025041 | 0.056978 | 0.049875 | 0.046406 | -0.017266 | 0.0243 | -0.017566 | 0.079598 | 0.11483 | 0.22896 | -0.090531 | 0.092622 | 0.99852 | -0.033458 | 122.0419 | 122.3173 | 122.1969 | -0.16415 | -0.035599 | -122.1845 | 0.037666 | 0.037366 | 0.072965 | -122.1493 | -122.0351 | -0.10922 | -0.22222 | 0.14755 | 0.021474 | 0.13069 | 0.053238 | -0.067183 | 0.13453 | 0.16976 | 0.28389 | 0.079232 | -122.3546 | 122.0968 | 122.3723 | 122.2518 | 1.0534 | -122.4282
4118.9375 | 122.3419 | -0.10529 | 122.2641 | -0.010149 | -0.05588 | 0.038798 | 0.017973 | -0.014001 | -0.0033715 | -0.013887 | -0.0024804 | -0.0025041 | 0.057191 | 0.049448 | 0.046406 | -0.021844 | 0.033457 | -0.022144 | 0.07502 | 0.11941 | 0.22896 | -0.09511 | 0.088043 | 1.0031 | -0.033458 | 122.0419 | 122.3219 | 122.1923 | -0.16873 | 0.010176 | -122.1891 | 0.083442 | 0.083142 | 0.072966 | -122.1447 | -122.0351 | -0.063442 | -0.22222 | 0.19333 | 0.071828 | 0.13527 | 0.057817 | -0.071762 | 0.18031 | 0.2247 | 0.33425 | 0.13874 | -122.3592 | 122.1472 | 122.4272 | 122.2976 | 1.1084 | -122.4328
4120.6406 | 122.4426 | -0.054932 | 122.2229 | -0.01778 | -0.055666 | 0.039011 | 0.017973 | -0.014001 | -0.0029443 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.050089 | 0.046192 | -0.017266 | 0.0243 | -0.022144 | 0.07502 | 0.11483 | 0.2198 | -0.090531 | 0.088043 | 1.0031 | -0.028879 | 122.0373 | 122.3357 | 122.2015 | -0.16873 | -0.035599 | -122.1479 | 0.037666 | 0.032788 | 0.068387 | -122.1081 | -122.0031 | -0.1138 | -0.18559 | 0.14297 | 0.026053 | 0.13985 | 0.11275 | -0.021405 | 0.12995 | 0.16976 | 0.27473 | 0.079232 | -122.3134 | 122.0922 | 122.3906 | 122.2564 | 1.058 | -122.3916
4122.3281 | 122.3923 | -0.086975 | 122.2824 | -0.010149 | -0.055666 | 0.039439 | 0.017973 | -0.014001 | -0.0033715 | -0.021518 | -0.002053 | -0.0022903 | 0.057191 | 0.050089 | 0.045978 | -0.021844 | 0.028878 | -0.022144 | 0.084176 | 0.11483 | 0.2198 | -0.09511 | 0.092622 | 1.0077 | -0.028879 | 122.0373 | 122.3265 | 122.2061 | -0.16415 | -0.008135 | -122.1982 | 0.065131 | 0.064831 | 0.072966 | -122.1676 | -122.0626 | -0.077174 | -0.2451 | 0.1796 | 0.058096 | 0.13527 | 0.044084 | -0.076337 | 0.17115 | 0.20181 | 0.30678 | 0.11585 | -122.3775 | 122.1243 | 122.4135 | 122.293 | 1.0947 | -122.4466
4124.0312 | 122.4609 | -0.050354 | 122.2412 | -0.0025182 | -0.05588 | 0.038584 | 0.017973 | -0.014215 | -0.0033715 | -0.013887 | -0.0024804 | -0.0022903 | 0.057405 | 0.050089 | 0.046192 | -0.012688 | 0.0243 | -0.017566 | 0.084176 | 0.11483 | 0.22896 | -0.09511 | 0.092622 | 1.0123 | -0.028879 | 122.0373 | 122.3265 | 122.1923 | -0.17788 | -0.044756 | -122.157 | 0.037666 | 0.032788 | 0.077544 | -122.1264 | -122.0123 | -0.12753 | -0.20391 | 0.14298 | 0.021475 | 0.14901 | 0.085283 | -0.048874 | 0.13453 | 0.16519 | 0.27931 | 0.074654 | -122.3363 | 122.0877 | 122.3768 | 122.2427 | 1.0626 | -122.4191
4125.75 | 122.4747 | -0.050354 | 122.2275 | -0.01778 | -0.055666 | 0.039011 | 0.017973 | -0.013788 | -0.0035853 | -0.029148 | -0.0024804 | -0.0022903 | 0.056978 | 0.049875 | 0.046406 | -0.017266 | 0.028878 | -0.022144 | 0.079598 | 0.11941 | 0.22438 | -0.090531 | 0.097201 | 1.0168 | -0.028879 | 122.0373 | 122.3219 | 122.1923 | -0.16873 | -0.040177 | -122.1479 | 0.033088 | 0.02821 | 0.068387 | -122.1081 | -122.0031 | -0.11837 | -0.19017 | 0.14755 | 0.021475 | 0.13985 | 0.094438 | -0.035141 | 0.12995 | 0.16976 | 0.27474 | 0.079232 | -122.318 | 122.0877 | 122.3723 | 122.2427 | 1.0672 | -122.3962
4127.4375 | 122.3969 | -0.064087 | 122.2549 | -0.0025182 | -0.05588 | 0.038798 | 0.017759 | -0.014001 | -0.0035853 | -0.021518 | -0.0022666 | -0.0020767 | 0.057191 | 0.050089 | 0.046406 | -0.017266 | 0.0243 | -0.017566 | 0.079598 | 0.11483 | 0.22438 | -0.090531 | 0.097201 | 1.0168 | -0.033458 | 122.0373 | 122.3219 | 122.2061 | -0.16873 | -0.026444 | -122.1753 | 0.046821 | 0.046521 | 0.072965 | -122.1401 | -122.0306 | -0.10464 | -0.21764 | 0.16129 | 0.030629 | 0.13527 | 0.066972 | -0.048871 | 0.14369 | 0.17892 | 0.28847 | 0.088387 | -122.3455 | 122.1014 | 122.386 | 122.2702 | 1.0809 | -122.4237
4129.1406 | 122.4197 | -0.068665 | 122.2412 | -0.010149 | -0.05588 | 0.039011 | 0.017759 | -0.014001 | -0.0033715 | -0.021518 | -0.0022666 | -0.0022903 | 0.056978 | 0.049875 | 0.046406 | -0.021844 | 0.028878 | -0.008409 | 0.084176 | 0.11483 | 0.22896 | -0.090531 | 0.10178 | 1.0168 | -0.028879 | 122.0373 | 122.3219 | 122.1969 | -0.17331 | -0.021866 | -122.157 | 0.046821 | 0.060256 | 0.082122 | -122.1264 | -122.0123 | -0.10464 | -0.20391 | 0.17044 | 0.039786 | 0.14443 | 0.080705 | -0.044295 | 0.15284 | 0.1835 | 0.29762 | 0.097543 | -122.3317 | 122.106 | 122.3906 | 122.2656 | 1.0855 | -122.4145
4130.8281 | 122.374 | -0.11444 | 122.2733 | -0.010149 | -0.056094 | 0.039225 | 0.017973 | -0.014001 | -0.0033715 | -0.021518 | -0.0022666 | -0.0018631 | 0.056764 | 0.049662 | 0.046406 | -0.012688 | 0.019721 | -0.022144 | 0.079598 | 0.11025 | 0.22896 | -0.090531 | 0.097201 | 1.0168 | -0.028879 | 122.0281 | 122.3311 | 122.1969 | -0.17331 | 0.02391 | -122.1937 | 0.10175 | 0.092297 | 0.068387 | -122.163 | -122.0443 | -0.058865 | -0.2451 | 0.21164 | 0.085562 | 0.14443 | 0.057819 | -0.076338 | 0.19404 | 0.22469 | 0.3434 | 0.13416 | -122.3638 | 122.1426 | 122.4455 | 122.3114 | 1.1313 | -122.4466
4132.5312 | 122.3923 | -0.07782 | 122.2504 | -0.010149 | -0.055666 | 0.039225 | 0.017759 | -0.013788 | -0.0031579 | -0.029148 | -0.0029076 | -0.0022903 | 0.057405 | 0.049662 | 0.046406 | -0.012688 | 0.028878 | -0.017566 | 0.07502 | 0.11483 | 0.22896 | -0.09511 | 0.097201 | 1.0214 | -0.0243 | 122.0327 | 122.3265 | 122.2015 | -0.16415 | -0.01729 | -122.1753 | 0.065132 | 0.060254 | 0.077544 | -122.1355 | -122.0214 | -0.086329 | -0.21764 | 0.17502 | 0.05352 | 0.13985 | 0.076128 | -0.048871 | 0.15284 | 0.19265 | 0.30678 | 0.1067 | -122.3455 | 122.1105 | 122.4043 | 122.2793 | 1.0992 | -122.4145
4134.25 | 122.3923 | -0.09613 | 122.2733 | -0.010149 | -0.056094 | 0.038798 | 0.017546 | -0.014429 | -0.0031579 | -0.021518 | -0.0022666 | -0.0020767 | 0.056978 | 0.049875 | 0.046406 | -0.026423 | 0.0243 | -0.017566 | 0.079598 | 0.12399 | 0.22438 | -0.09511 | 0.092622 | 1.0168 | -0.033458 | 122.0465 | 122.3219 | 122.1969 | -0.16873 | 0.00102 | -122.1937 | 0.069707 | 0.078564 | 0.077544 | -122.1493 | -122.0489 | -0.072598 | -0.22679 | 0.18875 | 0.062672 | 0.13527 | 0.048662 | -0.076338 | 0.17573 | 0.22012 | 0.32051 | 0.12043 | -122.3684 | 122.1426 | 122.418 | 122.293 | 1.113 | -122.442
4135.9375 | 122.4518 | -0.045776 | 122.2275 | -0.01778 | -0.05588 | 0.039011 | 0.017973 | -0.014429 | -0.0033715 | -0.013887 | -0.002694 | -0.0020767 | 0.056978 | 0.049875 | 0.046406 | -0.012688 | 0.028878 | -0.017566 | 0.079598 | 0.12399 | 0.22896 | -0.085952 | 0.088043 | 1.0306 | -0.0243 | 122.0373 | 122.3265 | 122.1969 | -0.16415 | -0.040176 | -122.1479 | 0.033088 | 0.02821 | 0.068386 | -122.1035 | -121.9985 | -0.11837 | -0.19017 | 0.13382 | 0.021476 | 0.13985 | 0.099016 | -0.030562 | 0.12537 | 0.16977 | 0.27474 | 0.074654 | -122.3134 | 122.0831 | 122.3723 | 122.2427 | 1.0763 | -122.3916
4137.6406 | 122.4609 | -0.07782 | 122.2504 | 0.0051128 | -0.055666 | 0.039011 | 0.017973 | -0.013788 | -0.0031579 | -0.021518 | -0.0024804 | -0.0025041 | 0.056764 | 0.050089 | 0.046406 | -0.021844 | 0.0243 | -0.022144 | 0.079598 | 0.12399 | 0.23354 | -0.09511 | 0.092622 | 1.026 | -0.028879 | 122.0465 | 122.3219 | 122.2015 | -0.16873 | -0.01729 | -122.1708 | 0.055976 | 0.055676 | 0.072966 | -122.1264 | -122.0168 | -0.090908 | -0.2039 | 0.17044 | 0.048941 | 0.13985 | 0.07155 | -0.048871 | 0.15742 | 0.20181 | 0.31136 | 0.10212 | -122.3455 | 122.1243 | 122.3997 | 122.2793 | 1.1038 | -122.4191
4139.3438 | 122.3328 | -0.10529 | 122.2824 | -0.01778 | -0.056094 | 0.038798 | 0.017759 | -0.014215 | -0.0031579 | -0.029148 | -0.0024804 | -0.0025041 | 0.056978 | 0.050089 | 0.046406 | -0.017266 | 0.0243 | -0.017566 | 0.079598 | 0.11483 | 0.22896 | -0.090531 | 0.10178 | 1.0351 | -0.033458 | 122.0327 | 122.3265 | 122.2061 | -0.17331 | 0.014755 | -122.2028 | 0.08802 | 0.08772 | 0.072965 | -122.1676 | -122.0535 | -0.06802 | -0.24968 | 0.20706 | 0.071828 | 0.13985 | 0.044084 | -0.076337 | 0.18488 | 0.22012 | 0.33425 | 0.12959 | -122.3729 | 122.138 | 122.4318 | 122.3114 | 1.1404 | -122.4557
4141.1094 | 122.4335 | -0.045776 | 122.2504 | -0.010149 | -0.05588 | 0.039011 | 0.017973 | -0.014215 | -0.0031579 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.049875 | 0.045978 | -0.017266 | 0.033457 | -0.012988 | 0.088755 | 0.11941 | 0.23354 | -0.085952 | 0.097201 | 1.0351 | -0.033458 | 122.0419 | 122.3265 | 122.1969 | -0.16873 | -0.040176 | -122.1616 | 0.02851 | 0.032788 | 0.072964 | -122.131 | -122.0168 | -0.12295 | -0.20848 | 0.14298 | 0.012318 | 0.13527 | 0.076128 | -0.05345 | 0.13453 | 0.16519 | 0.27931 | 0.079233 | -122.3363 | 122.0877 | 122.3723 | 122.2427 | 1.0809 | -122.4191
4142.7969 | 122.3648 | -0.091553 | 122.2961 | -0.010149 | -0.056307 | 0.038798 | 0.017759 | -0.014001 | -0.0033715 | -0.0062567 | -0.0024804 | -0.0020767 | 0.057405 | 0.050089 | 0.046406 | -0.021844 | 0.019721 | -0.017566 | 0.084176 | 0.11941 | 0.22438 | -0.09511 | 0.10178 | 1.0351 | -0.028879 | 122.0419 | 122.3219 | 122.2015 | -0.15957 | -0.003557 | -122.212 | 0.069709 | 0.073987 | 0.077544 | -122.1767 | -122.0718 | -0.068017 | -0.25426 | 0.19333 | 0.062674 | 0.13069 | 0.025773 | -0.094648 | 0.17573 | 0.21096 | 0.31593 | 0.11127 | -122.3913 | 122.1334 | 122.4135 | 122.293 | 1.1267 | -122.4557
4144.4844 | 122.4655 | -0.054932 | 122.2458 | -0.0025182 | -0.055666 | 0.038798 | 0.017973 | -0.014001 | -0.0029443 | -0.029148 | -0.0022666 | -0.0022903 | 0.057191 | 0.050089 | 0.046192 | -0.017266 | 0.028878 | -0.012988 | 0.07502 | 0.11483 | 0.22896 | -0.09511 | 0.097201 | 1.0397 | -0.028879 | 122.0419 | 122.3219 | 122.2015 | -0.16415 | -0.040178 | -122.1708 | 0.037666 | 0.041944 | 0.082122 | -122.131 | -122.0168 | -0.10922 | -0.20391 | 0.15213 | 0.026053 | 0.13527 | 0.076127 | -0.044294 | 0.12995 | 0.16976 | 0.28389 | 0.08381 | -122.3409 | 122.0968 | 122.3768 | 122.2564 | 1.0947 | -122.4099
4146.1875 | 122.4701 | -0.054932 | 122.2366 | -0.0025182 | -0.056094 | 0.038798 | 0.017759 | -0.014001 | -0.0027305 | -0.029148 | -0.0022666 | -0.0020767 | 0.057191 | 0.049662 | 0.046406 | -0.012688 | 0.0243 | -0.017566 | 0.079598 | 0.12399 | 0.22438 | -0.090531 | 0.088043 | 1.0443 | -0.033458 | 122.0327 | 122.3265 | 122.2015 | -0.16415 | -0.035599 | -122.157 | 0.042244 | 0.037366 | 0.072965 | -122.1126 | -122.0123 | -0.10922 | -0.20391 | 0.14297 | 0.021474 | 0.13069 | 0.089861 | -0.035138 | 0.13453 | 0.17892 | 0.27931 | 0.079232 | -122.3272 | 122.0877 | 122.3814 | 122.2564 | 1.0992 | -122.4008
4147.8906 | 122.3969 | -0.086975 | 122.2778 | -0.010149 | -0.05588 | 0.039225 | 0.017759 | -0.013788 | -0.0033715 | -0.021518 | -0.002694 | -0.0022903 | 0.056978 | 0.049875 | 0.046192 | -0.017266 | 0.028878 | -0.017566 | 0.079598 | 0.11941 | 0.22896 | -0.09511 | 0.092622 | 1.0397 | -0.0243 | 122.0419 | 122.3265 | 122.2015 | -0.16873 | -0.008135 | -122.1982 | 0.069709 | 0.069409 | 0.077544 | -122.1584 | -122.0489 | -0.081753 | -0.23595 | 0.1796 | 0.062675 | 0.14443 | 0.048662 | -0.076337 | 0.16657 | 0.20639 | 0.31593 | 0.11585 | -122.3729 | 122.1289 | 122.4135 | 122.2885 | 1.1267 | -122.4466
4149.6094 | 122.3557 | -0.086975 | 122.2733 | -0.0025182 | -0.056094 | 0.039011 | 0.017546 | -0.014215 | -0.0031579 | -0.029148 | -0.0022666 | -0.0020767 | 0.056978 | 0.049875 | 0.046192 | -0.017266 | 0.0243 | -0.012988 | 0.084176 | 0.11941 | 0.22896 | -0.09511 | 0.092622 | 1.0535 | -0.033458 | 122.0373 | 122.3219 | 122.2015 | -0.16873 | -0.008135 | -122.1891 | 0.069709 | 0.073987 | 0.082122 | -122.1538 | -122.0443 | -0.081753 | -0.23595 | 0.1796 | 0.053517 | 0.13527 | 0.048662 | -0.071759 | 0.17115 | 0.20639 | 0.31593 | 0.11127 | -122.3684 | 122.1243 | 122.4089 | 122.2885 | 1.1404 | -122.442
4151.3125 | 122.4609 | -0.041199 | 122.2412 | -0.010149 | -0.056094 | 0.039225 | 0.017759 | -0.013788 | -0.0031579 | -0.0062567 | -0.0024804 | -0.0022903 | 0.057405 | 0.049875 | 0.046192 | -0.021844 | 0.019721 | -0.017566 | 0.079598 | 0.11483 | 0.2198 | -0.090531 | 0.092622 | 1.0443 | -0.038036 | 122.0373 | 122.3219 | 122.1969 | -0.17331 | -0.049332 | -122.1616 | 0.019355 | 0.023633 | 0.072965 | -122.1264 | -122.0214 | -0.13211 | -0.20391 | 0.13382 | 0.003163 | 0.13527 | 0.080705 | -0.044295 | 0.1208 | 0.15603 | 0.261 | 0.06092 | -122.3317 | 122.0785 | 122.3631 | 122.2381 | 1.0855 | -122.4145
4153.0781 | 122.4976 | -0.036621 | 122.2412 | -0.0025182 | -0.056094 | 0.038798 | 0.017973 | -0.014001 | -0.0027305 | -0.029148 | -0.002694 | -0.0022903 | 0.056764 | 0.050303 | 0.045765 | -0.021844 | 0.0243 | -0.012988 | 0.07502 | 0.11941 | 0.22438 | -0.09511 | 0.097201 | 1.058 | -0.033458 | 122.0419 | 122.3219 | 122.2015 | -0.16873 | -0.058489 | -122.1662 | 0.014777 | 0.023633 | 0.082122 | -122.1218 | -122.0168 | -0.13211 | -0.19933 | 0.13382 | 0.003163 | 0.13527 | 0.080705 | -0.039716 | 0.11164 | 0.15603 | 0.261 | 0.060921 | -122.3363 | 122.0785 | 122.3585 | 122.2381 | 1.0947 | -122.4099
4154.7812 | 122.3785 | -0.09613 | 122.2733 | -0.010149 | -0.055666 | 0.039011 | 0.017973 | -0.014001 | -0.0031579 | -0.021518 | -0.002694 | -0.0018631 | 0.056978 | 0.049875 | 0.046406 | -0.017266 | 0.028878 | -0.012988 | 0.07502 | 0.11483 | 0.23354 | -0.099689 | 0.097201 | 1.058 | -0.028879 | 122.0373 | 122.3219 | 122.2015 | -0.16873 | -0.003559 | -122.1982 | 0.078864 | 0.083142 | 0.086701 | -122.1584 | -122.0397 | -0.072598 | -0.23595 | 0.19333 | 0.067251 | 0.13985 | 0.048662 | -0.071759 | 0.17115 | 0.21096 | 0.32967 | 0.12501 | -122.3729 | 122.1334 | 122.418 | 122.2976 | 1.1542 | -122.442
4156.5312 | 122.3877 | -0.086975 | 122.3007 | -0.025411 | -0.05588 | 0.038798 | 0.017973 | -0.014429 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.057191 | 0.049875 | 0.045978 | -0.021844 | 0.019721 | -0.012988 | 0.079598 | 0.11941 | 0.23812 | -0.099689 | 0.092622 | 1.058 | -0.0243 | 122.0373 | 122.3265 | 122.2015 | -0.16415 | -0.012714 | -122.2211 | 0.065131 | 0.073987 | 0.086701 | -122.1813 | -122.0626 | -0.077174 | -0.26341 | 0.1796 | 0.062675 | 0.13985 | 0.025774 | -0.099225 | 0.16657 | 0.20639 | 0.32509 | 0.1067 | -122.4004 | 122.1243 | 122.4135 | 122.2885 | 1.145 | -122.4649
4158.2344 | 122.4106 | -0.059509 | 122.2412 | -0.01778 | -0.056094 | 0.039011 | 0.017759 | -0.014001 | -0.0031579 | -0.021518 | -0.0022666 | -0.0022903 | 0.057191 | 0.049875 | 0.045765 | -0.017266 | 0.0243 | -0.012988 | 0.07502 | 0.12399 | 0.22896 | -0.09511 | 0.092622 | 1.0626 | -0.033458 | 122.0373 | 122.3173 | 122.2015 | -0.16873 | -0.035601 | -122.1662 | 0.042243 | 0.046521 | 0.082122 | -122.1172 | -122.0123 | -0.10922 | -0.20391 | 0.15213 | 0.026051 | 0.13527 | 0.076126 | -0.039716 | 0.13453 | 0.1835 | 0.28847 | 0.083809 | -122.3363 | 122.0968 | 122.3768 | 122.261 | 1.1221 | -122.4099
4159.9375 | 122.374 | -0.086975 | 122.2687 | -0.01778 | -0.05588 | 0.039225 | 0.017546 | -0.014215 | -0.0029443 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.050089 | 0.046619 | -0.017266 | 0.019721 | -0.017566 | 0.07502 | 0.11941 | 0.22896 | -0.090531 | 0.088043 | 1.058 | -0.033458 | 122.0327 | 122.3265 | 122.2061 | -0.17331 | -0.003556 | -122.1937 | 0.069709 | 0.069409 | 0.072965 | -122.1493 | -122.0397 | -0.086331 | -0.23595 | 0.17502 | 0.053517 | 0.13985 | 0.057817 | -0.062604 | 0.162 | 0.20639 | 0.31593 | 0.1067 | -122.3592 | 122.1197 | 122.4135 | 122.293 | 1.145 | -122.442
4161.625 | 122.4747 | -0.068665 | 122.2641 | -0.01778 | -0.056094 | 0.039225 | 0.017759 | -0.014001 | -0.0029443 | -0.021518 | -0.0024804 | -0.0020767 | 0.057191 | 0.050089 | 0.046406 | -0.012688 | 0.019721 | -0.012988 | 0.088755 | 0.11941 | 0.23354 | -0.09511 | 0.092622 | 1.0672 | -0.028879 | 122.0419 | 122.3265 | 122.1969 | -0.16873 | -0.026445 | -122.1753 | 0.055977 | 0.055677 | 0.082122 | -122.1447 | -122.0306 | -0.10006 | -0.22222 | 0.16129 | 0.039786 | 0.13985 | 0.062395 | -0.067183 | 0.15742 | 0.18808 | 0.3022 | 0.088386 | -122.3592 | 122.1105 | 122.3952 | 122.2656 | 1.1359 | -122.4328
4163.3438 | 122.3465 | -0.11444 | 122.3007 | -0.010149 | -0.055666 | 0.038798 | 0.017973 | -0.014215 | -0.0029443 | -0.013887 | -0.0022666 | -0.0020767 | 0.056978 | 0.049875 | 0.045978 | -0.026423 | 0.0243 | -0.012988 | 0.079598 | 0.11483 | 0.22896 | -0.085952 | 0.092622 | 1.0535 | -0.028879 | 122.0419 | 122.3265 | 122.1878 | -0.16873 | 0.028489 | -122.2211 | 0.088018 | 0.10145 | 0.072964 | -122.1859 | -122.0718 | -0.054287 | -0.25884 | 0.20706 | 0.085562 | 0.13985 | 0.025774 | -0.11296 | 0.19404 | 0.22927 | 0.3434 | 0.13874 | -122.3867 | 122.1563 | 122.4409 | 122.3022 | 1.1679 | -122.4694
4165.0469 | 122.3831 | -0.073242 | 122.2916 | -0.010149 | -0.055666 | 0.039011 | 0.017759 | -0.014001 | -0.0031579 | -0.021518 | -0.0024804 | -0.0022903 | 0.056764 | 0.049662 | 0.046192 | -0.012688 | 0.0243 | -0.017566 | 0.079598 | 0.11483 | 0.23354 | -0.09511 | 0.092622 | 1.0718 | -0.028879 | 122.0327 | 122.3265 | 122.2015 | -0.16873 | -0.021868 | -122.212 | 0.060554 | 0.055676 | 0.077544 | -122.1767 | -122.058 | -0.095486 | -0.25884 | 0.16586 | 0.044363 | 0.13985 | 0.034929 | -0.09007 | 0.15284 | 0.18807 | 0.30678 | 0.097542 | -122.3867 | 122.106 | 122.3997 | 122.2747 | 1.145 | -122.4603
4166.75 | 122.3511 | -0.10071 | 122.2916 | -0.0025182 | -0.05588 | 0.039011 | 0.017973 | -0.014001 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.057191 | 0.050089 | 0.046192 | -0.012688 | 0.0243 | 0.000747 | 0.079598 | 0.11941 | 0.22896 | -0.090531 | 0.092622 | 1.0672 | -0.033458 | 122.0373 | 122.3311 | 122.2061 | -0.17331 | 0.010177 | -122.212 | 0.08802 | 0.10146 | 0.091278 | -122.1722 | -122.0626 | -0.072598 | -0.25426 | 0.19333 | 0.06725 | 0.13985 | 0.039508 | -0.085492 | 0.18031 | 0.22012 | 0.32967 | 0.12501 | -122.3821 | 122.138 | 122.4318 | 122.3068 | 1.1679 | -122.4649
4168.4375 | 122.4609 | -0.032043 | 122.2504 | -0.010149 | -0.056307 | 0.039225 | 0.017973 | -0.014001 | -0.0029443 | -0.021518 | -0.002694 | -0.0025041 | 0.056978 | 0.050089 | 0.045978 | -0.021844 | 0.0243 | -0.008409 | 0.079598 | 0.11483 | 0.23354 | -0.090531 | 0.097201 | 1.0672 | -0.0243 | 122.0419 | 122.3265 | 122.2061 | -0.17331 | -0.058488 | -122.1708 | 0.010199 | 0.023634 | 0.082122 | -122.1355 | -122.0168 | -0.14126 | -0.20848 | 0.12924 | 0.007743 | 0.14901 | 0.076128 | -0.044293 | 0.11164 | 0.14688 | 0.26558 | 0.056343 | -122.3409 | 122.0739 | 122.3585 | 122.2381 | 1.0992 | -122.4237
4170.1406 | 122.4655 | -0.054932 | 122.2366 | -0.010149 | -0.05588 | 0.039225 | 0.017759 | -0.014215 | -0.0025169 | -0.021518 | -0.002694 | -0.0022903 | 0.056978 | 0.049875 | 0.045978 | -0.017266 | 0.0243 | -0.008409 | 0.070441 | 0.11483 | 0.23354 | -0.090531 | 0.10178 | 1.0672 | -0.033458 | 122.0419 | 122.3219 | 122.2061 | -0.17788 | -0.035599 | -122.1662 | 0.037666 | 0.046523 | 0.082122 | -122.1218 | -122.0031 | -0.12295 | -0.19475 | 0.15671 | 0.021474 | 0.14443 | 0.085283 | -0.03056 | 0.12537 | 0.16976 | 0.28847 | 0.079232 | -122.3272 | 122.0968 | 122.3768 | 122.261 | 1.1221 | -122.4145
4171.8438 | 122.3328 | -0.09613 | 122.2824 | -0.025411 | -0.056307 | 0.038798 | 0.018187 | -0.014215 | -0.0031579 | -0.021518 | -0.0024804 | -0.0025041 | 0.057405 | 0.050089 | 0.045978 | -0.012688 | 0.028878 | 0.000747 | 0.079598 | 0.11941 | 0.22438 | -0.090531 | 0.092622 | 1.0855 | -0.028879 | 122.0373 | 122.3219 | 122.2061 | -0.17331 | 0.005599 | -122.2028 | 0.083442 | 0.096877 | 0.091278 | -122.163 | -122.058 | -0.077176 | -0.2451 | 0.18875 | 0.067251 | 0.14443 | 0.039506 | -0.076337 | 0.17573 | 0.21554 | 0.32051 | 0.12501 | -122.3729 | 122.1334 | 122.418 | 122.3022 | 1.1816 | -122.4557
4173.5938 | 122.3602 | -0.10529 | 122.2778 | -0.010149 | -0.056094 | 0.039439 | 0.017973 | -0.014001 | -0.0029443 | -0.013887 | -0.0022666 | -0.0022903 | 0.057191 | 0.050089 | 0.046192 | -0.021844 | 0.028878 | -0.008409 | 0.079598 | 0.11941 | 0.22896 | -0.090531 | 0.097201 | 1.0855 | -0.033458 | 122.0373 | 122.3219 | 122.2061 | -0.16873 | 0.014755 | -122.1982 | 0.083442 | 0.096877 | 0.082122 | -122.1584 | -122.0489 | -0.063442 | -0.24053 | 0.20249 | 0.071828 | 0.13527 | 0.044084 | -0.071759 | 0.18488 | 0.2247 | 0.33425 | 0.13416 | -122.3684 | 122.1426 | 122.4272 | 122.3114 | 1.1908 | -122.4466
4175.2969 | 122.3557 | -0.082397 | 122.287 | -0.0025182 | -0.056307 | 0.039439 | 0.017546 | -0.014215 | -0.0027305 | -0.029148 | -0.002694 | -0.0022903 | 0.057191 | 0.050089 | 0.046406 | -0.017266 | 0.028878 | 0.000747 | 0.084176 | 0.11941 | 0.22896 | -0.09511 | 0.092622 | 1.0809 | -0.028879 | 122.0327 | 122.3311 | 122.1969 | -0.16873 | -0.012713 | -122.2028 | 0.065131 | 0.083144 | 0.095857 | -122.1676 | -122.058 | -0.086331 | -0.25426 | 0.17502 | 0.053518 | 0.13985 | 0.044086 | -0.090071 | 0.16657 | 0.20181 | 0.31136 | 0.11127 | -122.3821 | 122.1151 | 122.4135 | 122.2793 | 1.1633 | -122.4557
4177.0625 | 122.3831 | -0.10071 | 122.2641 | -0.010149 | -0.056094 | 0.038798 | 0.017546 | -0.013788 | -0.0029443 | -0.013887 | -0.002694 | -0.0022903 | 0.057405 | 0.050089 | 0.046192 | -0.017266 | 0.0243 | -0.003831 | 0.084176 | 0.11483 | 0.22896 | -0.09511 | 0.092622 | 1.0901 | -0.015143 | 122.0373 | 122.3219 | 122.2061 | -0.16873 | 0.005598 | -122.1799 | 0.083442 | 0.096877 | 0.091279 | -122.1493 | -122.0351 | -0.06802 | -0.22679 | 0.19333 | 0.085565 | 0.15358 | 0.057817 | -0.058026 | 0.18488 | 0.21554 | 0.32967 | 0.12501 | -122.3592 | 122.138 | 122.4226 | 122.3068 | 1.1908 | -122.4328
4178.7656 | 122.4197 | -0.068665 | 122.2595 | -0.01778 | -0.056094 | 0.039011 | 0.017973 | -0.014215 | -0.0029443 | -0.029148 | -0.002694 | -0.0022903 | 0.056764 | 0.050089 | 0.046192 | -0.017266 | 0.0243 | -0.003831 | 0.079598 | 0.11941 | 0.22438 | -0.090531 | 0.092622 | 1.0901 | -0.038036 | 122.0465 | 122.3219 | 122.2015 | -0.16873 | -0.021866 | -122.1799 | 0.051399 | 0.064834 | 0.0867 | -122.1401 | -122.0351 | -0.10006 | -0.21306 | 0.16129 | 0.030629 | 0.13069 | 0.062395 | -0.058026 | 0.14826 | 0.18808 | 0.29305 | 0.092965 | -122.3501 | 122.1151 | 122.3906 | 122.2702 | 1.1588 | -122.4282
4180.4688 | 122.438 | -0.064087 | 122.2687 | 0.0051128 | -0.05588 | 0.038798 | 0.017546 | -0.014215 | -0.0027305 | -0.013887 | -0.002694 | -0.0020767 | 0.057405 | 0.050089 | 0.046192 | -0.021844 | 0.0243 | -0.003831 | 0.084176 | 0.12399 | 0.22896 | -0.099689 | 0.092622 | 1.0855 | -0.028879 | 122.0419 | 122.3357 | 122.1969 | -0.16415 | -0.035602 | -122.1845 | 0.042243 | 0.060256 | 0.095858 | -122.1447 | -122.0397 | -0.10006 | -0.22679 | 0.15671 | 0.035208 | 0.13527 | 0.066974 | -0.071761 | 0.14826 | 0.18808 | 0.29305 | 0.088387 | -122.3684 | 122.106 | 122.3997 | 122.261 | 1.1496 | -122.4328
4182.1875 | 122.4518 | -0.036621 | 122.2504 | -0.010149 | -0.05588 | 0.039011 | 0.017973 | -0.014215 | -0.0029443 | -0.029148 | -0.002694 | -0.0022903 | 0.056978 | 0.050303 | 0.046406 | -0.017266 | 0.033457 | -0.008409 | 0.079598 | 0.11941 | 0.23354 | -0.085952 | 0.088043 | 1.0992 | -0.028879 | 122.0419 | 122.3265 | 122.2015 | -0.16873 | -0.049331 | -122.1708 | 0.019355 | 0.028212 | 0.077543 | -122.131 | -122.0168 | -0.13211 | -0.20848 | 0.12466 | 0.007742 | 0.13985 | 0.076128 | -0.048871 | 0.11622 | 0.15603 | 0.27016 | 0.070078 | -122.3363 | 122.0785 | 122.3631 | 122.2381 | 1.1359 | -122.4191
4183.8906 | 122.3419 | -0.10529 | 122.3007 | -0.010149 | -0.056094 | 0.038798 | 0.017546 | -0.013788 | -0.0025169 | -0.021518 | -0.0022666 | -0.0020767 | 0.057405 | 0.050303 | 0.045765 | -0.017266 | 0.019721 | -0.008409 | 0.07502 | 0.12399 | 0.22896 | -0.099689 | 0.097201 | 1.0947 | -0.033458 | 122.0419 | 122.3265 | 122.1969 | -0.16415 | 0.005597 | -122.2257 | 0.08802 | 0.096877 | 0.09128 | -122.1767 | -122.0718 | -0.058863 | -0.25884 | 0.20249 | 0.071828 | 0.13069 | 0.025774 | -0.1038 | 0.18031 | 0.22928 | 0.33425 | 0.12501 | -122.4004 | 122.1472 | 122.4318 | 122.3022 | 1.2 | -122.4649
4185.625 | 122.4335 | -0.059509 | 122.2504 | -0.010149 | -0.056094 | 0.039225 | 0.017546 | -0.014001 | -0.0025169 | -0.021518 | -0.002694 | -0.0025041 | 0.056978 | 0.049875 | 0.046192 | -0.012688 | 0.0243 | 0.000747 | 0.079598 | 0.12399 | 0.23812 | -0.099689 | 0.092622 | 1.1038 | -0.033458 | 122.0465 | 122.3311 | 122.2015 | -0.16415 | -0.04018 | -122.1708 | 0.046821 | 0.060256 | 0.10044 | -122.1264 | -122.0122 | -0.10464 | -0.2039 | 0.15213 | 0.026051 | 0.13069 | 0.080707 | -0.048871 | 0.13911 | 0.1835 | 0.29763 | 0.083809 | -122.3501 | 122.106 | 122.3906 | 122.261 | 1.1633 | -122.4145
4187.3281 | 122.3282 | -0.10071 | 122.2824 | -0.01778 | -0.05588 | 0.038798 | 0.017759 | -0.014001 | -0.0031579 | -0.021518 | -0.0024804 | -0.0020767 | 0.057405 | 0.050089 | 0.046192 | -0.021844 | 0.0243 | 0.000747 | 0.088755 | 0.11941 | 0.22438 | -0.09511 | 0.092622 | 1.1084 | -0.0243 | 122.0327 | 122.3173 | 122.1969 | -0.17331 | 0.005598 | -122.1937 | 0.078864 | 0.10146 | 0.095857 | -122.163 | -122.058 | -0.072598 | -0.24968 | 0.19333 | 0.076408 | 0.14901 | 0.034927 | -0.085494 | 0.18946 | 0.22012 | 0.32509 | 0.12501 | -122.3775 | 122.1334 | 122.418 | 122.2976 | 1.2091 | -122.4557
4189.0781 | 122.4564 | -0.050354 | 122.2046 | -0.010149 | -0.05588 | 0.039011 | 0.017973 | -0.013788 | -0.0035853 | -0.021518 | -0.0018394 | -0.0022903 | 0.056978 | 0.050303 | 0.046192 | -0.017266 | 0.0243 | 0.005325 | 0.079598 | 0.11941 | 0.23354 | -0.09511 | 0.097201 | 1.1038 | -0.028879 | 122.0419 | 122.3265 | 122.2015 | -0.17331 | -0.044756 | -122.125 | 0.033088 | 0.055679 | 0.10043 | -122.0852 | -121.9711 | -0.12295 | -0.16271 | 0.14755 | 0.021475 | 0.14443 | 0.1219 | -0.003095 | 0.12995 | 0.16976 | 0.28389 | 0.074654 | -122.2997 | 122.0922 | 122.3768 | 122.2518 | 1.1542 | -122.3779
4190.7969 | 122.4152 | -0.064087 | 122.2549 | -0.010149 | -0.056094 | 0.038798 | 0.017759 | -0.014215 | -0.0027305 | -0.021518 | -0.0022666 | -0.0020767 | 0.057191 | 0.050089 | 0.046406 | -0.021844 | 0.028878 | -0.003831 | 0.079598 | 0.11941 | 0.23354 | -0.090531 | 0.097201 | 1.1084 | -0.028879 | 122.0419 | 122.3265 | 122.2015 | -0.16873 | -0.026444 | -122.1753 | 0.042243 | 0.060256 | 0.0867 | -122.1355 | -122.0214 | -0.10464 | -0.21306 | 0.16129 | 0.035208 | 0.13985 | 0.07155 | -0.053449 | 0.14369 | 0.1835 | 0.29763 | 0.092965 | -122.3455 | 122.106 | 122.3906 | 122.2656 | 1.1725 | -122.4237
4192.5469 | 122.4609 | -0.045776 | 122.2229 | -0.01778 | -0.056307 | 0.038798 | 0.017332 | -0.014001 | -0.0031579 | -0.029148 | -0.002053 | -0.0022903 | 0.057191 | 0.050303 | 0.046192 | -0.017266 | 0.0243 | 0.000747 | 0.079598 | 0.12399 | 0.22438 | -0.09511 | 0.088043 | 1.113 | -0.028879 | 122.0419 | 122.3265 | 122.1923 | -0.16873 | -0.049334 | -122.1433 | 0.02851 | 0.046523 | 0.095857 | -122.0989 | -121.9985 | -0.12295 | -0.18102 | 0.13382 | 0.016897 | 0.13985 | 0.10359 | -0.030563 | 0.12537 | 0.16977 | 0.27016 | 0.070076 | -122.318 | 122.0877 | 122.3723 | 122.2381 | 1.1588 | -122.3916
4194.25 | 122.3511 | -0.11444 | 122.287 | -0.0025182 | -0.056094 | 0.039011 | 0.017759 | -0.014001 | -0.0031579 | -0.021518 | -0.0024804 | -0.0025041 | 0.057191 | 0.050089 | 0.046192 | -0.021844 | 0.0243 | -0.003831 | 0.079598 | 0.11941 | 0.22896 | -0.09511 | 0.097201 | 1.113 | -0.033458 | 122.0373 | 122.3311 | 122.2015 | -0.16873 | 0.019331 | -122.2074 | 0.092597 | 0.11061 | 0.091279 | -122.1676 | -122.058 | -0.054287 | -0.24968 | 0.21164 | 0.080983 | 0.13527 | 0.044086 | -0.085492 | 0.19404 | 0.23385 | 0.3434 | 0.13874 | -122.3821 | 122.1517 | 122.4455 | 122.3159 | 1.2274 | -122.4557
4195.9375 | 122.4335 | -0.050354 | 122.2549 | -0.010149 | -0.056094 | 0.039011 | 0.017546 | -0.014001 | -0.0027305 | -0.013887 | -0.0029076 | -0.0020767 | 0.056978 | 0.050089 | 0.045978 | -0.017266 | 0.0243 | 0.000747 | 0.079598 | 0.11483 | 0.22896 | -0.099689 | 0.092622 | 1.1084 | -0.028879 | 122.0419 | 122.3357 | 122.2015 | -0.16415 | -0.049335 | -122.1753 | 0.033088 | 0.051101 | 0.10044 | -122.1401 | -122.026 | -0.11379 | -0.21306 | 0.14298 | 0.021475 | 0.13527 | 0.080707 | -0.053449 | 0.12995 | 0.16519 | 0.27931 | 0.074654 | -122.3546 | 122.0922 | 122.386 | 122.2518 | 1.1588 | -122.4191
4197.6562 | 122.374 | -0.082397 | 122.2549 | -0.010149 | -0.056307 | 0.038798 | 0.017546 | -0.014001 | -0.0031579 | -0.029148 | -0.0029076 | -0.0022903 | 0.057191 | 0.050303 | 0.045978 | -0.012688 | 0.0243 | 0.000747 | 0.079598 | 0.11941 | 0.22896 | -0.09511 | 0.092622 | 1.1176 | -0.033458 | 122.0419 | 122.3311 | 122.1969 | -0.17331 | -0.012713 | -122.1753 | 0.069709 | 0.083144 | 0.095857 | -122.1355 | -122.026 | -0.090909 | -0.21306 | 0.17502 | 0.048939 | 0.13985 | 0.076129 | -0.058028 | 0.162 | 0.20181 | 0.31136 | 0.1067 | -122.3501 | 122.1243 | 122.4135 | 122.2793 | 1.2 | -122.4282
4199.3594 | 122.4747 | -0.054932 | 122.2275 | -0.010149 | -0.056307 | 0.038798 | 0.017759 | -0.014429 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.056978 | 0.050303 | 0.046406 | -0.012688 | 0.0243 | -0.003831 | 0.079598 | 0.12399 | 0.22896 | -0.099689 | 0.097201 | 1.113 | -0.028879 | 122.0419 | 122.3265 | 122.2015 | -0.18246 | -0.044757 | -122.1479 | 0.042244 | 0.051101 | 0.095858 | -122.1035 | -121.9985 | -0.12753 | -0.18559 | 0.15213 | 0.026053 | 0.15358 | 0.099016 | -0.025983 | 0.13453 | 0.17892 | 0.28389 | 0.079232 | -122.3272 | 122.0968 | 122.3814 | 122.2564 | 1.1679 | -122.4099
4201.0781 | 122.4243 | -0.050354 | 122.2412 | -0.025411 | -0.056307 | 0.038798 | 0.017973 | -0.014215 | -0.0031579 | -0.029148 | -0.002694 | -0.0025041 | 0.056978 | 0.050303 | 0.045978 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.11941 | 0.23354 | -0.09511 | 0.097201 | 1.1176 | -0.0243 | 122.0419 | 122.3311 | 122.1923 | -0.16873 | -0.044756 | -122.157 | 0.02851 | 0.041945 | 0.086701 | -122.1218 | -122.0077 | -0.11837 | -0.19933 | 0.14755 | 0.026054 | 0.14443 | 0.089862 | -0.048874 | 0.13453 | 0.16976 | 0.28389 | 0.074654 | -122.3363 | 122.0922 | 122.3814 | 122.2427 | 1.1679 | -122.4099
4202.7812 | 122.3969 | -0.091553 | 122.2549 | -0.010149 | -0.056307 | 0.039011 | 0.017973 | -0.013788 | -0.0029443 | -0.013887 | -0.0022666 | -0.0020767 | 0.056978 | 0.050303 | 0.046192 | -0.021844 | 0.0243 | -0.008409 | 0.079598 | 0.11941 | 0.22896 | -0.09511 | 0.092622 | 1.1267 | -0.028879 | 122.0373 | 122.3311 | 122.2015 | -0.16873 | -0.003557 | -122.1753 | 0.069709 | 0.083144 | 0.086701 | -122.1355 | -122.026 | -0.077175 | -0.21764 | 0.18417 | 0.062674 | 0.13985 | 0.076129 | -0.053449 | 0.17115 | 0.21096 | 0.32051 | 0.11585 | -122.3501 | 122.1289 | 122.4226 | 122.293 | 1.2183 | -122.4237
4204.4688 | 122.4243 | -0.059509 | 122.2641 | -0.025411 | -0.056094 | 0.039011 | 0.017546 | -0.014001 | -0.0031579 | -0.013887 | -0.0024804 | -0.0018631 | 0.056978 | 0.050089 | 0.046406 | -0.012688 | 0.019721 | -0.003831 | 0.07502 | 0.12399 | 0.23354 | -0.09511 | 0.097201 | 1.1267 | -0.028879 | 122.0419 | 122.3265 | 122.1969 | -0.17331 | -0.035601 | -122.1891 | 0.046821 | 0.055678 | 0.091279 | -122.1401 | -122.0306 | -0.1138 | -0.22222 | 0.15671 | 0.03063 | 0.14443 | 0.062395 | -0.067183 | 0.13453 | 0.1835 | 0.29305 | 0.07923 | -122.3592 | 122.1014 | 122.386 | 122.2564 | 1.1862 | -122.4374
4206.1875 | 122.3465 | -0.10986 | 122.2961 | -0.010149 | -0.056307 | 0.03837 | 0.017759 | -0.013788 | -0.0027305 | -0.021518 | -0.0022666 | -0.0022903 | 0.056978 | 0.050089 | 0.046192 | -0.017266 | 0.028878 | -0.008409 | 0.07502 | 0.11941 | 0.23354 | -0.090531 | 0.097201 | 1.1267 | -0.0243 | 122.0373 | 122.3311 | 122.1969 | -0.17331 | 0.019332 | -122.2211 | 0.092597 | 0.10145 | 0.082122 | -122.1767 | -122.0626 | -0.063443 | -0.25884 | 0.20706 | 0.085563 | 0.14901 | 0.03493 | -0.099227 | 0.18488 | 0.22927 | 0.3434 | 0.13874 | -122.3867 | 122.1472 | 122.4409 | 122.3068 | 1.2366 | -122.4694
4207.8906 | 122.4518 | -0.050354 | 122.2229 | -0.010149 | -0.056094 | 0.038798 | 0.017759 | -0.014215 | -0.0029443 | -0.021518 | -0.002694 | -0.0020767 | 0.056978 | 0.050517 | 0.046406 | -0.017266 | 0.0243 | -0.003831 | 0.079598 | 0.12399 | 0.22438 | -0.090531 | 0.092622 | 1.1267 | -0.033458 | 122.0373 | 122.3219 | 122.1969 | -0.16873 | -0.040177 | -122.1433 | 0.033088 | 0.046523 | 0.0867 | -122.0989 | -121.9985 | -0.11837 | -0.18559 | 0.14298 | 0.016896 | 0.13527 | 0.099016 | -0.025984 | 0.12995 | 0.17434 | 0.27474 | 0.074654 | -122.3134 | 122.0877 | 122.3723 | 122.2473 | 1.1771 | -122.3916
4209.6406 | 122.3465 | -0.10529 | 122.3053 | -0.010149 | -0.056307 | 0.039225 | 0.017546 | -0.014215 | -0.0029443 | -0.0062567 | -0.0022666 | -0.0022903 | 0.056978 | 0.050303 | 0.045978 | -0.021844 | 0.0243 | -0.003831 | 0.088755 | 0.11483 | 0.22438 | -0.099689 | 0.092622 | 1.1313 | -0.028879 | 122.0373 | 122.3219 | 122.1969 | -0.16873 | 0.005597 | -122.2165 | 0.083442 | 0.10146 | 0.095858 | -122.1905 | -122.0809 | -0.063442 | -0.26799 | 0.19791 | 0.076407 | 0.13985 | 0.016618 | -0.10838 | 0.19404 | 0.22012 | 0.32967 | 0.12959 | -122.405 | 122.1426 | 122.4272 | 122.3022 | 1.2366 | -122.474
4211.3438 | 122.3373 | -0.091553 | 122.2595 | -0.01778 | -0.056521 | 0.039011 | 0.017546 | -0.014429 | -0.0029443 | -0.029148 | -0.002694 | -0.0025041 | 0.057191 | 0.050303 | 0.046192 | -0.021844 | 0.028878 | -0.003831 | 0.084176 | 0.11025 | 0.22896 | -0.09511 | 0.097201 | 1.145 | -0.019721 | 122.0419 | 122.3265 | 122.2061 | -0.16415 | -0.003557 | -122.1753 | 0.069709 | 0.087722 | 0.091279 | -122.1493 | -122.0306 | -0.072596 | -0.21764 | 0.18875 | 0.071832 | 0.14443 | 0.066973 | -0.053448 | 0.17573 | 0.20181 | 0.32051 | 0.12043 | -122.3546 | 122.1334 | 122.418 | 122.2976 | 1.2366 | -122.4237
4213.0469 | 122.3419 | -0.086975 | 122.3053 | -0.010149 | -0.056094 | 0.038798 | 0.017759 | -0.013788 | -0.0027305 | -0.013887 | -0.0024804 | -0.0020767 | 0.056978 | 0.050517 | 0.046192 | -0.017266 | 0.0243 | 0.000747 | 0.079598 | 0.11483 | 0.22896 | -0.09511 | 0.092622 | 1.145 | -0.0243 | 122.0373 | 122.3311 | 122.1969 | -0.16873 | -0.008135 | -122.2257 | 0.069709 | 0.087722 | 0.095857 | -122.1905 | -122.0763 | -0.081753 | -0.26799 | 0.1796 | 0.062675 | 0.14443 | 0.025775 | -0.10838 | 0.16657 | 0.20181 | 0.31593 | 0.11127 | -122.4004 | 122.1243 | 122.418 | 122.2839 | 1.232 | -122.474
4214.7344 | 122.4335 | -0.054932 | 122.2412 | -0.0025182 | -0.056307 | 0.039011 | 0.017118 | -0.014001 | -0.0025169 | -0.013887 | -0.0024804 | -0.0022903 | 0.056764 | 0.050303 | 0.045978 | -0.012688 | 0.0243 | -0.008409 | 0.07502 | 0.11483 | 0.23354 | -0.090531 | 0.092622 | 1.145 | -0.0243 | 122.0373 | 122.3311 | 122.2015 | -0.16873 | -0.035599 | -122.1662 | 0.042244 | 0.046523 | 0.082122 | -122.1264 | -122.0077 | -0.1138 | -0.20391 | 0.14755 | 0.030632 | 0.14443 | 0.089862 | -0.039716 | 0.12995 | 0.16976 | 0.28847 | 0.079232 | -122.3317 | 122.0922 | 122.386 | 122.2564 | 1.2 | -122.4099
4216.4375 | 122.3465 | -0.09613 | 122.2778 | -0.025411 | -0.056521 | 0.039011 | 0.017759 | -0.013788 | -0.0029443 | -0.013887 | -0.0024804 | -0.0022903 | 0.056978 | 0.050303 | 0.045765 | -0.017266 | 0.0243 | -0.008409 | 0.079598 | 0.12399 | 0.23354 | -0.09511 | 0.092622 | 1.1542 | -0.033458 | 122.0419 | 122.3265 | 122.1923 | -0.16873 | 0.00102 | -122.1982 | 0.078864 | 0.087721 | 0.086701 | -122.1538 | -122.0443 | -0.072598 | -0.23595 | 0.18875 | 0.062672 | 0.13527 | 0.048662 | -0.085495 | 0.17573 | 0.22012 | 0.32967 | 0.12043 | -122.3729 | 122.138 | 122.4226 | 122.2885 | 1.2503 | -122.4466
4218.1406 | 122.4243 | -0.050354 | 122.2412 | -0.010149 | -0.056307 | 0.038584 | 0.017546 | -0.014215 | -0.0029443 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.050089 | 0.045978 | -0.021844 | 0.0243 | -0.008409 | 0.079598 | 0.12399 | 0.22896 | -0.090531 | 0.092622 | 1.1496 | -0.033458 | 122.0373 | 122.3311 | 122.2015 | -0.17331 | -0.040177 | -122.1616 | 0.02851 | 0.041945 | 0.082122 | -122.1172 | -122.0123 | -0.12295 | -0.20391 | 0.14298 | 0.016896 | 0.13985 | 0.089862 | -0.039716 | 0.12995 | 0.17434 | 0.27931 | 0.074654 | -122.3317 | 122.0877 | 122.3814 | 122.2518 | 1.2 | -122.4145
4219.8281 | 122.3602 | -0.10986 | 122.287 | -0.0025182 | -0.056521 | 0.038798 | 0.017546 | -0.014001 | -0.0027305 | -0.021518 | -0.002694 | -0.0022903 | 0.057191 | 0.049875 | 0.046192 | -0.017266 | 0.033457 | -0.012988 | 0.079598 | 0.12857 | 0.22896 | -0.09511 | 0.097201 | 1.1542 | -0.028879 | 122.0327 | 122.3311 | 122.1923 | -0.16873 | 0.014753 | -122.2074 | 0.092597 | 0.096875 | 0.082122 | -122.1584 | -122.058 | -0.058865 | -0.25426 | 0.20706 | 0.080984 | 0.13985 | 0.044086 | -0.09465 | 0.18946 | 0.23843 | 0.33882 | 0.14332 | -122.3821 | 122.1426 | 122.4409 | 122.3022 | 1.2641 | -122.4557
4221.5781 | 122.3465 | -0.10071 | 122.2641 | -0.010149 | -0.056094 | 0.039011 | 0.017973 | -0.013574 | -0.0027305 | -0.021518 | -0.0024804 | -0.0020767 | 0.057191 | 0.050303 | 0.046192 | -0.017266 | 0.0243 | -0.008409 | 0.079598 | 0.11941 | 0.23354 | -0.099689 | 0.097201 | 1.1588 | -0.0243 | 122.0419 | 122.3265 | 122.1969 | -0.16873 | 0.001019 | -122.1845 | 0.083442 | 0.092299 | 0.09128 | -122.1447 | -122.0306 | -0.06802 | -0.22222 | 0.19791 | 0.076408 | 0.14443 | 0.062395 | -0.067183 | 0.18031 | 0.22012 | 0.33425 | 0.12501 | -122.3638 | 122.1426 | 122.4272 | 122.2976 | 1.2595 | -122.4328
4223.2812 | 122.3602 | -0.082397 | 122.2595 | -0.025411 | -0.056521 | 0.039225 | 0.017118 | -0.014429 | -0.0031579 | -0.029148 | -0.0024804 | -0.0025041 | 0.057405 | 0.050089 | 0.046406 | -0.012688 | 0.019721 | -0.003831 | 0.079598 | 0.11941 | 0.22896 | -0.090531 | 0.092622 | 1.1588 | -0.033458 | 122.0419 | 122.3357 | 122.1969 | -0.16873 | -0.008134 | -122.1799 | 0.069709 | 0.078566 | 0.0867 | -122.1401 | -122.0306 | -0.086331 | -0.21764 | 0.17502 | 0.048939 | 0.13527 | 0.07613 | -0.062605 | 0.162 | 0.20181 | 0.31136 | 0.10212 | -122.3501 | 122.1243 | 122.418 | 122.2793 | 1.2412 | -122.4282
4224.9844 | 122.4518 | -0.059509 | 122.2687 | -0.010149 | -0.056521 | 0.038798 | 0.017759 | -0.014215 | -0.0027305 | -0.0062567 | -0.0022666 | -0.0022903 | 0.057191 | 0.050303 | 0.045765 | -0.021844 | 0.033457 | 0.000747 | 0.079598 | 0.11941 | 0.22896 | -0.09511 | 0.097201 | 1.1588 | -0.0243 | 122.0465 | 122.3265 | 122.1969 | -0.17331 | -0.035601 | -122.1891 | 0.037665 | 0.060256 | 0.095857 | -122.1493 | -122.0397 | -0.1138 | -0.22221 | 0.15671 | 0.035209 | 0.14901 | 0.057817 | -0.071761 | 0.13911 | 0.17892 | 0.28847 | 0.092966 | -122.3638 | 122.106 | 122.386 | 122.2564 | 1.2183 | -122.442
4226.6875 | 122.4152 | -0.050354 | 122.2733 | -0.010149 | -0.056521 | 0.039011 | 0.017973 | -0.013788 | -0.0027305 | -0.029148 | -0.0024804 | -0.0020767 | 0.056978 | 0.050303 | 0.045765 | -0.012688 | 0.028878 | -0.008409 | 0.084176 | 0.12399 | 0.23354 | -0.090531 | 0.092622 | 1.1679 | -0.0243 | 122.0465 | 122.3311 | 122.1923 | -0.17331 | -0.040177 | -122.1891 | 0.037666 | 0.041945 | 0.082122 | -122.1493 | -122.0397 | -0.12295 | -0.22679 | 0.14298 | 0.026054 | 0.14901 | 0.057819 | -0.080917 | 0.13453 | 0.17434 | 0.28389 | 0.079232 | -122.3638 | 122.0968 | 122.3814 | 122.2427 | 1.2183 | -122.4466
4228.3906 | 122.3831 | -0.082397 | 122.2412 | -0.01778 | -0.056521 | 0.039011 | 0.017546 | -0.013788 | -0.0029443 | -0.013887 | -0.0022666 | -0.0020767 | 0.056978 | 0.049875 | 0.045978 | -0.017266 | 0.028878 | -0.008409 | 0.084176 | 0.11941 | 0.23354 | -0.09511 | 0.092622 | 1.1634 | -0.028879 | 122.0419 | 122.3311 | 122.2015 | -0.16873 | -0.012713 | -122.157 | 0.065131 | 0.073988 | 0.086701 | -122.1218 | -122.0077 | -0.086331 | -0.19933 | 0.17502 | 0.053518 | 0.13985 | 0.089862 | -0.039716 | 0.16657 | 0.20181 | 0.31593 | 0.11127 | -122.3363 | 122.1243 | 122.4135 | 122.2839 | 1.2457 | -122.4099
4230.0938 | 122.4197 | -0.059509 | 122.2321 | -0.01778 | -0.056307 | 0.038584 | 0.017332 | -0.014001 | -0.0025169 | -0.013887 | -0.0022666 | -0.0020767 | 0.056764 | 0.05073 | 0.045978 | -0.021844 | 0.028878 | -0.012988 | 0.07502 | 0.11941 | 0.22896 | -0.090531 | 0.092622 | 1.1679 | -0.028879 | 122.0373 | 122.3402 | 122.2061 | -0.16873 | -0.031022 | -122.157 | 0.037665 | 0.046521 | 0.077543 | -122.1126 | -122.0031 | -0.10922 | -0.19475 | 0.15213 | 0.03063 | 0.13985 | 0.10817 | -0.025983 | 0.13453 | 0.17892 | 0.28847 | 0.088387 | -122.3226 | 122.0968 | 122.3997 | 122.2656 | 1.2274 | -122.4008
4231.7969 | 122.3282 | -0.09613 | 122.2916 | -0.010149 | -0.056521 | 0.038798 | 0.017118 | -0.014001 | -0.0029443 | -0.029148 | -0.002694 | -0.0022903 | 0.056764 | 0.050517 | 0.045978 | -0.017266 | 0.028878 | -0.008409 | 0.084176 | 0.11941 | 0.23354 | -0.090531 | 0.088043 | 1.1725 | -0.0243 | 122.0419 | 122.3357 | 122.2015 | -0.16415 | 0.005599 | -122.2074 | 0.078864 | 0.087721 | 0.082122 | -122.1722 | -122.058 | -0.068019 | -0.24968 | 0.18417 | 0.07183 | 0.13985 | 0.044086 | -0.09007 | 0.18031 | 0.21554 | 0.32967 | 0.12501 | -122.3821 | 122.138 | 122.4318 | 122.2976 | 1.2686 | -122.4557
4233.5 | 122.4564 | -0.041199 | 122.2275 | -0.010149 | -0.056094 | 0.038798 | 0.017332 | -0.014429 | -0.0027305 | -0.013887 | -0.0024804 | -0.0022903 | 0.056764 | 0.050303 | 0.045978 | -0.021844 | 0.028878 | -0.003831 | 0.079598 | 0.11941 | 0.22896 | -0.09511 | 0.097201 | 1.1771 | -0.028879 | 122.0419 | 122.3357 | 122.1969 | -0.16873 | -0.053911 | -122.1479 | 0.019355 | 0.037368 | 0.091279 | -122.1081 | -121.9985 | -0.12753 | -0.18559 | 0.1384 | 0.01232 | 0.13985 | 0.10817 | -0.030562 | 0.1208 | 0.16061 | 0.27016 | 0.070077 | -122.3226 | 122.0831 | 122.3769 | 122.2381 | 1.2183 | -122.3962
4235.2188 | 122.4289 | -0.036621 | 122.2137 | -0.01778 | -0.056521 | 0.039011 | 0.017332 | -0.014001 | -0.0027305 | -0.029148 | -0.0024804 | -0.0020767 | 0.056978 | 0.05073 | 0.045978 | -0.017266 | 0.0243 | -0.008409 | 0.07502 | 0.11941 | 0.22438 | -0.090531 | 0.088043 | 1.1725 | -0.033458 | 122.0419 | 122.3311 | 122.1969 | -0.17331 | -0.05391 | -122.1387 | 0.019355 | 0.028212 | 0.082122 | -122.0943 | -121.9894 | -0.13669 | -0.17186 | 0.12466 | 0.003163 | 0.13985 | 0.11733 | -0.016829 | 0.11164 | 0.15603 | 0.261 | 0.060921 | -122.3043 | 122.0785 | 122.3677 | 122.2335 | 1.2091 | -122.3871
4236.9219 | 122.3419 | -0.12817 | 122.2778 | -0.01778 | -0.056307 | 0.038584 | 0.017332 | -0.014001 | -0.0027305 | -0.021518 | -0.002694 | -0.0025041 | 0.056978 | 0.050303 | 0.046192 | -0.008109 | 0.028878 | -0.008409 | 0.088755 | 0.11941 | 0.23354 | -0.09511 | 0.097201 | 1.1771 | -0.028879 | 122.0419 | 122.3219 | 122.2015 | -0.17788 | 0.033064 | -122.1891 | 0.12007 | 0.11977 | 0.086701 | -122.1584 | -122.0443 | -0.049711 | -0.23595 | 0.22537 | 0.099295 | 0.14901 | 0.044084 | -0.076337 | 0.21693 | 0.24758 | 0.36171 | 0.15705 | -122.3729 | 122.1701 | 122.4501 | 122.3297 | 1.3053 | -122.4557
4238.625 | 122.4426 | -0.045776 | 122.2183 | -0.025411 | -0.056307 | 0.039011 | 0.017332 | -0.014429 | -0.0025169 | -0.029148 | -0.0024804 | -0.0022903 | 0.057191 | 0.050517 | 0.045765 | -0.012688 | 0.028878 | -0.008409 | 0.079598 | 0.12857 | 0.23354 | -0.090531 | 0.088043 | 1.1817 | -0.028879 | 122.0419 | 122.3265 | 122.2015 | -0.15957 | -0.044755 | -122.1387 | 0.033088 | 0.037367 | 0.082122 | -122.0898 | -121.9848 | -0.11379 | -0.17644 | 0.13382 | 0.016897 | 0.13069 | 0.10817 | -0.016828 | 0.12537 | 0.17434 | 0.27931 | 0.074654 | -122.3089 | 122.0877 | 122.3723 | 122.2473 | 1.2274 | -122.3779
4240.3438 | 122.3419 | -0.11444 | 122.2778 | -0.0025182 | -0.056521 | 0.038798 | 0.017546 | -0.014215 | -0.0029443 | -0.029148 | -0.0022666 | -0.0022903 | 0.056978 | 0.050303 | 0.045765 | -0.026423 | 0.0243 | -0.008409 | 0.07502 | 0.12399 | 0.23354 | -0.090531 | 0.092622 | 1.1771 | -0.033458 | 122.0373 | 122.3311 | 122.1969 | -0.17331 | 0.02391 | -122.2028 | 0.088018 | 0.10603 | 0.082122 | -122.1538 | -122.0443 | -0.058865 | -0.24053 | 0.20706 | 0.080983 | 0.13985 | 0.053241 | -0.080916 | 0.18946 | 0.23843 | 0.34798 | 0.13874 | -122.3684 | 122.1517 | 122.4455 | 122.3114 | 1.2915 | -122.4511
4242.0469 | 122.3831 | -0.10529 | 122.2778 | -0.0025182 | -0.056094 | 0.039011 | 0.017546 | -0.014215 | -0.0025169 | -0.036779 | -0.0022666 | -0.0022903 | 0.057191 | 0.050303 | 0.045978 | -0.017266 | 0.033457 | -0.012988 | 0.07502 | 0.13315 | 0.23354 | -0.09511 | 0.097201 | 1.1862 | -0.0243 | 122.0419 | 122.3265 | 122.2015 | -0.16873 | 0.010176 | -122.2028 | 0.08802 | 0.092298 | 0.082122 | -122.1447 | -122.0443 | -0.063442 | -0.23595 | 0.20249 | 0.080986 | 0.14443 | 0.048662 | -0.076337 | 0.18031 | 0.23843 | 0.33882 | 0.13874 | -122.3729 | 122.1472 | 122.4318 | 122.3068 | 1.2915 | -122.4466
4243.7656 | 122.3923 | -0.082397 | 122.2641 | -0.0025182 | -0.056521 | 0.038798 | 0.017546 | -0.014215 | -0.0025169 | -0.013887 | -0.002694 | -0.0020767 | 0.056978 | 0.050517 | 0.045765 | -0.017266 | 0.028878 | -0.012988 | 0.079598 | 0.11483 | 0.23354 | -0.090531 | 0.092622 | 1.1862 | -0.0243 | 122.0419 | 122.3265 | 122.1923 | -0.17331 | -0.008134 | -122.1845 | 0.065131 | 0.069409 | 0.077543 | -122.1493 | -122.0306 | -0.090909 | -0.22222 | 0.17502 | 0.058097 | 0.14901 | 0.062395 | -0.071762 | 0.162 | 0.19723 | 0.31593 | 0.11127 | -122.3546 | 122.1243 | 122.4089 | 122.2747 | 1.2686 | -122.4374
4245.4531 | 122.3557 | -0.10986 | 122.2916 | -0.01778 | -0.056521 | 0.038798 | 0.017759 | -0.014215 | -0.0027305 | -0.021518 | -0.0029076 | -0.0020767 | 0.057191 | 0.050517 | 0.046192 | -0.012688 | 0.033457 | -0.012988 | 0.079598 | 0.11941 | 0.23354 | -0.10427 | 0.097201 | 1.1817 | -0.0243 | 122.0419 | 122.3128 | 122.2061 | -0.16873 | 0.005595 | -122.212 | 0.097175 | 0.096875 | 0.09128 | -122.1722 | -122.058 | -0.058865 | -0.24968 | 0.20706 | 0.085563 | 0.14443 | 0.021193 | -0.085492 | 0.18946 | 0.22927 | 0.3434 | 0.14332 | -122.3958 | 122.1517 | 122.4226 | 122.3159 | 1.2915 | -122.4603
4247.1562 | 122.374 | -0.086975 | 122.2733 | -0.0025182 | -0.056307 | 0.038798 | 0.017332 | -0.013788 | -0.0025169 | -0.0062567 | -0.0022666 | -0.0022903 | 0.056978 | 0.050303 | 0.046192 | -0.012688 | 0.0243 | -0.017566 | 0.079598 | 0.12857 | 0.23354 | -0.090531 | 0.097201 | 1.1862 | -0.0243 | 122.0419 | 122.3265 | 122.1923 | -0.17788 | -0.003556 | -122.1937 | 0.074287 | 0.069409 | 0.072965 | -122.1447 | -122.0397 | -0.09091 | -0.23137 | 0.18418 | 0.062675 | 0.15358 | 0.05324 | -0.080917 | 0.16657 | 0.21554 | 0.32051 | 0.11127 | -122.3638 | 122.1289 | 122.4135 | 122.2793 | 1.2732 | -122.4511
4248.875 | 122.4243 | -0.068665 | 122.2504 | -0.01778 | -0.056307 | 0.038798 | 0.017546 | -0.014001 | -0.0025169 | -0.029148 | -0.0024804 | -0.0022903 | 0.056978 | 0.050303 | 0.045765 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.12857 | 0.22896 | -0.090531 | 0.088043 | 1.1954 | -0.019721 | 122.0465 | 122.3311 | 122.1969 | -0.17331 | -0.021866 | -122.1708 | 0.046821 | 0.055677 | 0.077543 | -122.1218 | -122.0214 | -0.10464 | -0.2039 | 0.15671 | 0.048944 | 0.15358 | 0.080707 | -0.05345 | 0.14826 | 0.19723 | 0.29762 | 0.092965 | -122.3409 | 122.1151 | 122.3997 | 122.2656 | 1.2641 | -122.4237
4250.625 | 122.4747 | -0.059509 | 122.1909 | -0.01778 | -0.056735 | 0.038798 | 0.017118 | -0.014001 | -0.0020895 | -0.021518 | -0.002694 | -0.0022903 | 0.056764 | 0.050517 | 0.045978 | -0.012688 | 0.033457 | -0.012988 | 0.084176 | 0.11941 | 0.22896 | -0.09511 | 0.097201 | 1.1908 | -0.028879 | 122.0419 | 122.3219 | 122.1969 | -0.16873 | -0.035601 | -122.1067 | 0.046821 | 0.046521 | 0.082122 | -122.0714 | -121.9619 | -0.10922 | -0.14897 | 0.15671 | 0.03063 | 0.13985 | 0.13106 | 0.006059 | 0.14369 | 0.17892 | 0.28847 | 0.092966 | -122.286 | 122.1014 | 122.3814 | 122.2564 | 1.2503 | -122.3596
4252.3281 | 122.3694 | -0.086975 | 122.2641 | -0.010149 | -0.056521 | 0.039225 | 0.017332 | -0.014429 | -0.0023033 | -0.029148 | -0.0024804 | -0.0022903 | 0.056978 | 0.050303 | 0.045978 | -0.017266 | 0.028878 | -0.003831 | 0.084176 | 0.11941 | 0.23354 | -0.099689 | 0.092622 | 1.2 | -0.028879 | 122.0419 | 122.3265 | 122.2015 | -0.16873 | -0.012714 | -122.1799 | 0.069709 | 0.083144 | 0.095858 | -122.1447 | -122.0306 | -0.081753 | -0.22222 | 0.1796 | 0.058096 | 0.13985 | 0.062395 | -0.062604 | 0.17115 | 0.20639 | 0.32051 | 0.11585 | -122.3638 | 122.1289 | 122.4135 | 122.2885 | 1.287 | -122.4328
4254.0312 | 122.4152 | -0.059509 | 122.2412 | -0.025411 | -0.056521 | 0.039011 | 0.017759 | -0.014429 | -0.0023033 | -0.029148 | -0.0024804 | -0.0025041 | 0.057191 | 0.049875 | 0.046192 | -0.021844 | 0.0243 | -0.017566 | 0.07502 | 0.11941 | 0.23354 | -0.099689 | 0.097201 | 1.1954 | -0.033458 | 122.0419 | 122.3265 | 122.1969 | -0.17331 | -0.04018 | -122.1662 | 0.037665 | 0.041943 | 0.082123 | -122.1218 | -122.0077 | -0.1138 | -0.19933 | 0.15671 | 0.026051 | 0.13985 | 0.085283 | -0.044295 | 0.13453 | 0.17892 | 0.29305 | 0.083809 | -122.3409 | 122.1014 | 122.386 | 122.2564 | 1.2549 | -122.4145
4255.7188 | 122.3282 | -0.11902 | 122.2961 | -0.010149 | -0.056307 | 0.039225 | 0.017759 | -0.014001 | -0.0020895 | -0.021518 | -0.0022666 | -0.0022903 | 0.056764 | 0.050517 | 0.045978 | -0.021844 | 0.033457 | -0.008409 | 0.084176 | 0.12857 | 0.22896 | -0.09511 | 0.097201 | 1.2091 | -0.028879 | 122.0419 | 122.3311 | 122.2015 | -0.17331 | 0.023909 | -122.212 | 0.097175 | 0.11061 | 0.086701 | -122.1676 | -122.0672 | -0.054287 | -0.25426 | 0.21622 | 0.09014 | 0.14443 | 0.03493 | -0.094648 | 0.2032 | 0.24759 | 0.34798 | 0.15248 | -122.3913 | 122.1609 | 122.4501 | 122.3205 | 1.3282 | -122.4694
4257.4531 | 122.3557 | -0.10529 | 122.2504 | -0.010149 | -0.056521 | 0.039011 | 0.017332 | -0.014001 | -0.0025169 | -0.013887 | -0.002694 | -0.0025041 | 0.056978 | 0.050517 | 0.045978 | -0.021844 | 0.0243 | -0.008409 | 0.079598 | 0.11941 | 0.23812 | -0.09511 | 0.088043 | 1.2046 | -0.0243 | 122.0419 | 122.3219 | 122.1969 | -0.16873 | 0.010176 | -122.1708 | 0.083442 | 0.096877 | 0.086701 | -122.131 | -122.0122 | -0.063442 | -0.20848 | 0.19333 | 0.080986 | 0.14443 | 0.07155 | -0.05345 | 0.18488 | 0.2247 | 0.3434 | 0.12959 | -122.3455 | 122.1472 | 122.4272 | 122.3022 | 1.3098 | -122.4191
4259.1406 | 122.4152 | -0.073242 | 122.2458 | -0.010149 | -0.056307 | 0.039011 | 0.017332 | -0.014215 | -0.0023033 | -0.036779 | -0.0022666 | -0.0020767 | 0.056978 | 0.050303 | 0.045978 | -0.017266 | 0.0243 | -0.012988 | 0.088755 | 0.12857 | 0.22896 | -0.09511 | 0.097201 | 1.2091 | -0.028879 | 122.0419 | 122.3265 | 122.1969 | -0.16873 | -0.021868 | -122.157 | 0.055976 | 0.060254 | 0.082122 | -122.1172 | -122.0168 | -0.095486 | -0.20391 | 0.17044 | 0.044363 | 0.13985 | 0.080705 | -0.048873 | 0.162 | 0.20181 | 0.3022 | 0.097542 | -122.3409 | 122.1151 | 122.3997 | 122.2702 | 1.2824 | -122.4145
4260.8594 | 122.4106 | -0.064087 | 122.2458 | -0.010149 | -0.056521 | 0.038584 | 0.017546 | -0.014429 | -0.0020895 | -0.029148 | -0.0024804 | -0.0018631 | 0.056764 | 0.05073 | 0.045765 | -0.012688 | 0.028878 | -0.012988 | 0.084176 | 0.11941 | 0.23354 | -0.099689 | 0.088043 | 1.2137 | -0.033458 | 122.0465 | 122.3265 | 122.1923 | -0.17788 | -0.035602 | -122.1616 | 0.051399 | 0.051099 | 0.086701 | -122.1264 | -122.0123 | -0.1138 | -0.19933 | 0.15213 | 0.030629 | 0.14443 | 0.080705 | -0.053452 | 0.14826 | 0.1835 | 0.29763 | 0.092965 | -122.3455 | 122.1106 | 122.3906 | 122.2564 | 1.2778 | -122.4237
4262.6094 | 122.4655 | -0.041199 | 122.2321 | -0.010149 | -0.056307 | 0.039011 | 0.017332 | -0.014429 | -0.0020895 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.050303 | 0.046192 | -0.021844 | 0.019721 | -0.022144 | 0.079598 | 0.12399 | 0.22438 | -0.09511 | 0.088043 | 1.2137 | -0.033458 | 122.0373 | 122.3173 | 122.1923 | -0.17788 | -0.053911 | -122.1525 | 0.019355 | 0.019055 | 0.072966 | -122.1081 | -122.0077 | -0.13669 | -0.19475 | 0.12924 | 0.007741 | 0.14443 | 0.085281 | -0.039719 | 0.1208 | 0.16519 | 0.26558 | 0.06092 | -122.3272 | 122.0785 | 122.3585 | 122.2335 | 1.2549 | -122.4099
4264.2969 | 122.374 | -0.10071 | 122.2687 | -0.010149 | -0.056521 | 0.039011 | 0.017332 | -0.014215 | -0.0020895 | -0.0062567 | -0.0024804 | -0.0022903 | 0.056764 | 0.050303 | 0.046192 | -0.017266 | 0.028878 | -0.008409 | 0.084176 | 0.11941 | 0.22896 | -0.090531 | 0.097201 | 1.2183 | -0.028879 | 122.0327 | 122.3265 | 122.2015 | -0.16873 | 0.010177 | -122.1845 | 0.083442 | 0.092299 | 0.082122 | -122.1493 | -122.0397 | -0.06802 | -0.23595 | 0.19791 | 0.071829 | 0.13985 | 0.057817 | -0.067182 | 0.18488 | 0.22012 | 0.32967 | 0.12959 | -122.3592 | 122.1334 | 122.4272 | 122.3022 | 1.319 | -122.4374
4266 | 122.4609 | -0.050354 | 122.2229 | -0.025411 | -0.056307 | 0.039439 | 0.017546 | -0.014001 | -0.0023033 | -0.021518 | -0.0024804 | -0.0022903 | 0.056764 | 0.050303 | 0.045978 | -0.017266 | 0.033457 | -0.022144 | 0.084176 | 0.12399 | 0.22438 | -0.09511 | 0.088043 | 1.2229 | -0.028879 | 122.0373 | 122.3265 | 122.1923 | -0.17331 | -0.044756 | -122.1387 | 0.033088 | 0.02821 | 0.072966 | -122.0989 | -121.9985 | -0.12295 | -0.18559 | 0.1384 | 0.021475 | 0.14443 | 0.10359 | -0.030563 | 0.13453 | 0.17434 | 0.27474 | 0.083811 | -122.318 | 122.0877 | 122.3768 | 122.2427 | 1.2732 | -122.3962
4267.7031 | 122.3877 | -0.10071 | 122.2687 | -0.0025182 | -0.056521 | 0.038798 | 0.017332 | -0.014215 | -0.0018759 | -0.021518 | -0.0022666 | -0.0022903 | 0.056978 | 0.050303 | 0.045978 | -0.017266 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.22896 | -0.099689 | 0.092622 | 1.2275 | -0.028879 | 122.0373 | 122.3265 | 122.1969 | -0.18246 | 0.001019 | -122.1891 | 0.083442 | 0.083142 | 0.082123 | -122.1493 | -122.0397 | -0.081756 | -0.23137 | 0.19333 | 0.071829 | 0.15358 | 0.057817 | -0.071761 | 0.18031 | 0.22012 | 0.32967 | 0.12501 | -122.3684 | 122.138 | 122.4272 | 122.2976 | 1.3282 | -122.4511
4269.3906 | 122.4472 | -0.059509 | 122.2504 | -0.01778 | -0.056307 | 0.038798 | 0.017759 | -0.014001 | -0.0020895 | -0.021518 | -0.002694 | -0.0022903 | 0.056978 | 0.050517 | 0.045765 | -0.017266 | 0.0243 | -0.012988 | 0.084176 | 0.12857 | 0.23354 | -0.09511 | 0.092622 | 1.2275 | -0.0243 | 122.0373 | 122.3357 | 122.1969 | -0.17331 | -0.035601 | -122.1662 | 0.042243 | 0.046521 | 0.082122 | -122.1218 | -122.0168 | -0.1138 | -0.21306 | 0.15213 | 0.035209 | 0.14901 | 0.085285 | -0.05345 | 0.14369 | 0.18808 | 0.29305 | 0.083809 | -122.3455 | 122.0968 | 122.3952 | 122.2564 | 1.287 | -122.4237
4271.0938 | 122.3831 | -0.082397 | 122.2504 | -0.0025182 | -0.056521 | 0.039011 | 0.017118 | -0.014429 | -0.0018759 | -0.0062567 | -0.0024804 | -0.0018631 | 0.056978 | 0.050303 | 0.045765 | -0.021844 | 0.0243 | -0.012988 | 0.084176 | 0.12399 | 0.22896 | -0.099689 | 0.092622 | 1.2275 | -0.0243 | 122.0373 | 122.3357 | 122.1969 | -0.17331 | -0.017292 | -122.1662 | 0.060553 | 0.069409 | 0.086701 | -122.1264 | -122.0214 | -0.090909 | -0.21306 | 0.17502 | 0.058097 | 0.14901 | 0.085285 | -0.05345 | 0.16657 | 0.20639 | 0.31136 | 0.1067 | -122.3501 | 122.1197 | 122.418 | 122.2793 | 1.3098 | -122.4237
4272.7969 | 122.4747 | -0.054932 | 122.2137 | -0.010149 | -0.056307 | 0.038798 | 0.017546 | -0.013788 | -0.0018759 | -0.029148 | -0.0022666 | -0.0022903 | 0.056978 | 0.050303 | 0.045978 | -0.021844 | 0.028878 | -0.022144 | 0.07502 | 0.11941 | 0.23354 | -0.090531 | 0.092622 | 1.2275 | -0.038036 | 122.0419 | 122.3265 | 122.1923 | -0.16873 | -0.035599 | -122.1387 | 0.033088 | 0.032788 | 0.068387 | -122.0943 | -121.9802 | -0.1138 | -0.17186 | 0.14755 | 0.016896 | 0.13069 | 0.11275 | -0.021408 | 0.12995 | 0.17434 | 0.28847 | 0.08381 | -122.3043 | 122.0968 | 122.3814 | 122.2473 | 1.2824 | -122.3825
4274.5312 | 122.3923 | -0.086975 | 122.2778 | -0.010149 | -0.056735 | 0.039225 | 0.017332 | -0.014001 | -0.0018759 | -0.021518 | -0.002694 | -0.0022903 | 0.057191 | 0.050303 | 0.045551 | -0.021844 | 0.028878 | -0.008409 | 0.084176 | 0.12399 | 0.23812 | -0.085952 | 0.10178 | 1.2366 | -0.033458 | 122.0419 | 122.3265 | 122.1969 | -0.16873 | 0.001023 | -122.1937 | 0.065131 | 0.078566 | 0.077543 | -122.1538 | -122.0397 | -0.081753 | -0.23595 | 0.18875 | 0.053517 | 0.13527 | 0.048662 | -0.080916 | 0.17115 | 0.21097 | 0.32509 | 0.11585 | -122.3638 | 122.1289 | 122.4135 | 122.2839 | 1.3236 | -122.4466
4276.2344 | 122.4106 | -0.07782 | 122.2229 | -0.01778 | -0.05588 | 0.038798 | 0.017332 | -0.013788 | -0.0018759 | -0.029148 | -0.0024804 | -0.0020767 | 0.057405 | 0.05073 | 0.045978 | -0.026423 | 0.019721 | -0.017566 | 0.079598 | 0.12857 | 0.23354 | -0.099689 | 0.097201 | 1.232 | -0.033458 | 122.0373 | 122.3357 | 122.1923 | -0.17331 | -0.021869 | -122.1433 | 0.051397 | 0.060254 | 0.082123 | -122.0943 | -121.9894 | -0.095486 | -0.18559 | 0.17502 | 0.044362 | 0.13985 | 0.11275 | -0.030563 | 0.15742 | 0.20639 | 0.31136 | 0.097541 | -122.3226 | 122.1151 | 122.4135 | 122.2702 | 1.3099 | -122.3962
4277.9531 | 122.4518 | -0.064087 | 122.2458 | -0.01778 | -0.056094 | 0.039011 | 0.017332 | -0.014215 | -0.0018759 | -0.013887 | -0.002694 | -0.0020767 | 0.056764 | 0.050517 | 0.045978 | -0.021844 | 0.033457 | -0.017566 | 0.07502 | 0.11941 | 0.23354 | -0.09511 | 0.097201 | 1.2412 | -0.028879 | 122.0373 | 122.3357 | 122.1969 | -0.17331 | -0.031023 | -122.1708 | 0.042243 | 0.046521 | 0.077544 | -122.1264 | -122.0123 | -0.10922 | -0.20848 | 0.16129 | 0.035208 | 0.14443 | 0.089862 | -0.048873 | 0.13911 | 0.1835 | 0.29763 | 0.097544 | -122.3409 | 122.1014 | 122.3997 | 122.261 | 1.3053 | -122.4191
4279.6719 | 122.4564 | -0.054932 | 122.2504 | -0.0025182 | -0.056094 | 0.038584 | 0.017332 | -0.014215 | -0.0016623 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.050517 | 0.046406 | -0.017266 | 0.028878 | -0.008409 | 0.079598 | 0.11941 | 0.23812 | -0.099689 | 0.088043 | 1.232 | -0.033458 | 122.0327 | 122.3311 | 122.2015 | -0.17788 | -0.044757 | -122.1708 | 0.037666 | 0.046523 | 0.09128 | -122.131 | -122.0122 | -0.12295 | -0.21764 | 0.14297 | 0.021474 | 0.14443 | 0.080707 | -0.048871 | 0.13453 | 0.17434 | 0.29305 | 0.08381 | -122.3501 | 122.0877 | 122.386 | 122.2564 | 1.287 | -122.4283
4281.3594 | 122.3694 | -0.091553 | 122.2778 | -0.010149 | -0.056094 | 0.039011 | 0.017546 | -0.014215 | -0.0016623 | -0.013887 | -0.0024804 | -0.0022903 | 0.057191 | 0.050517 | 0.045765 | -0.012688 | 0.028878 | -0.017566 | 0.079598 | 0.11025 | 0.23812 | -0.099689 | 0.10178 | 1.2366 | -0.028879 | 122.0419 | 122.3311 | 122.1969 | -0.16873 | -0.008136 | -122.1982 | 0.078865 | 0.073987 | 0.082123 | -122.1676 | -122.0397 | -0.077175 | -0.23595 | 0.19333 | 0.062674 | 0.13985 | 0.053241 | -0.080916 | 0.17115 | 0.20181 | 0.32967 | 0.12043 | -122.3775 | 122.1334 | 122.4226 | 122.2885 | 1.3282 | -122.4466
4283.0781 | 122.3785 | -0.064087 | 122.2641 | -0.010149 | -0.056521 | 0.039225 | 0.017546 | -0.014429 | -0.0016623 | -0.021518 | -0.0024804 | -0.0022903 | 0.056764 | 0.050517 | 0.045765 | -0.017266 | 0.0243 | -0.012988 | 0.084176 | 0.11941 | 0.23354 | -0.09511 | 0.097201 | 1.2503 | -0.019721 | 122.0419 | 122.3265 | 122.2015 | -0.17788 | -0.031023 | -122.1799 | 0.046821 | 0.051099 | 0.082122 | -122.1447 | -122.0306 | -0.1138 | -0.22222 | 0.16129 | 0.044366 | 0.15816 | 0.062395 | -0.062604 | 0.14826 | 0.1835 | 0.29763 | 0.088387 | -122.3592 | 122.106 | 122.3906 | 122.2656 | 1.3144 | -122.442
4284.7812 | 122.3557 | -0.10529 | 122.2641 | -0.0025182 | -0.056307 | 0.039225 | 0.017332 | -0.014642 | -0.0016623 | -0.021518 | -0.0029076 | -0.0022903 | 0.056764 | 0.050517 | 0.045765 | -0.021844 | 0.033457 | -0.012988 | 0.084176 | 0.11483 | 0.23354 | -0.085952 | 0.097201 | 1.2503 | -0.019721 | 122.0419 | 122.3219 | 122.1878 | -0.17788 | 0.019334 | -122.1799 | 0.083442 | 0.092298 | 0.072964 | -122.1493 | -122.0306 | -0.072599 | -0.22222 | 0.20249 | 0.085565 | 0.15816 | 0.057817 | -0.07634 | 0.18946 | 0.22012 | 0.33882 | 0.13874 | -122.3501 | 122.1472 | 122.4272 | 122.293 | 1.3556 | -122.442
4286.4688 | 122.4564 | -0.068665 | 122.2366 | -0.01778 | -0.056521 | 0.039011 | 0.017546 | -0.014215 | -0.0016623 | -0.021518 | -0.002694 | -0.0020767 | 0.057191 | 0.050517 | 0.045978 | -0.021844 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.23354 | -0.09511 | 0.092622 | 1.2458 | -0.028879 | 122.0419 | 122.3219 | 122.1969 | -0.16873 | -0.026445 | -122.157 | 0.046821 | 0.051099 | 0.077544 | -122.1172 | -122.0031 | -0.10006 | -0.19475 | 0.16129 | 0.039786 | 0.13985 | 0.085283 | -0.039717 | 0.14826 | 0.18808 | 0.3022 | 0.092965 | -122.3317 | 122.1105 | 122.3906 | 122.2656 | 1.3144 | -122.4054
4288.1719 | 122.3419 | -0.10529 | 122.287 | -0.0025182 | -0.056735 | 0.039011 | 0.017118 | -0.014001 | -0.0014487 | -0.013887 | -0.0024804 | -0.0022903 | 0.056764 | 0.050303 | 0.045978 | -0.017266 | 0.019721 | -0.017566 | 0.079598 | 0.12399 | 0.23354 | -0.090531 | 0.092622 | 1.2549 | -0.028879 | 122.0373 | 122.3173 | 122.2015 | -0.16873 | 0.014755 | -122.2074 | 0.08802 | 0.08772 | 0.072965 | -122.163 | -122.0534 | -0.063442 | -0.24968 | 0.19791 | 0.076407 | 0.13985 | 0.03035 | -0.085492 | 0.18488 | 0.22928 | 0.33882 | 0.12501 | -122.3775 | 122.1426 | 122.4226 | 122.3068 | 1.3602 | -122.4557
4289.8906 | 122.4976 | -0.054932 | 122.2412 | -0.010149 | -0.056307 | 0.038798 | 0.017332 | -0.014429 | -0.0018759 | -0.013887 | -0.0024804 | -0.0022903 | 0.057191 | 0.050303 | 0.045978 | -0.021844 | 0.033457 | -0.012988 | 0.079598 | 0.11941 | 0.23812 | -0.09511 | 0.092622 | 1.2503 | -0.0243 | 122.0419 | 122.3265 | 122.1969 | -0.17331 | -0.040178 | -122.1616 | 0.033088 | 0.041944 | 0.082122 | -122.1218 | -122.0031 | -0.11837 | -0.19933 | 0.14755 | 0.030632 | 0.14901 | 0.085283 | -0.044295 | 0.13453 | 0.17434 | 0.29305 | 0.088389 | -122.3363 | 122.0968 | 122.3814 | 122.2518 | 1.3053 | -122.4145
4291.6406 | 122.3923 | -0.09613 | 122.2595 | -0.010149 | -0.056735 | 0.039011 | 0.017759 | -0.014001 | -0.0014487 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.050303 | 0.046192 | -0.021844 | 0.028878 | -0.012988 | 0.079598 | 0.11941 | 0.23812 | -0.09511 | 0.092622 | 1.2549 | -0.0243 | 122.0327 | 122.3311 | 122.1923 | -0.16873 | 0.00102 | -122.1799 | 0.074286 | 0.083142 | 0.082122 | -122.1401 | -122.0214 | -0.072598 | -0.22679 | 0.18875 | 0.07183 | 0.14443 | 0.071552 | -0.067184 | 0.17573 | 0.21554 | 0.33425 | 0.12501 | -122.3546 | 122.1289 | 122.4272 | 122.2885 | 1.3511 | -122.4282
4293.3438 | 122.4609 | -0.045776 | 122.2412 | -0.01778 | -0.056521 | 0.039225 | 0.017332 | -0.014429 | -0.0012349 | -0.013887 | -0.002694 | -0.0025041 | 0.057191 | 0.050517 | 0.045765 | -0.026423 | 0.019721 | -0.017566 | 0.088755 | 0.13315 | 0.23354 | -0.099689 | 0.097201 | 1.2549 | -0.0243 | 122.0327 | 122.3311 | 122.1878 | -0.17788 | -0.053913 | -122.1525 | 0.019353 | 0.02821 | 0.082123 | -122.1081 | -122.0077 | -0.13211 | -0.20848 | 0.14298 | 0.021476 | 0.15358 | 0.089862 | -0.053452 | 0.13453 | 0.17892 | 0.27931 | 0.065497 | -122.3409 | 122.0785 | 122.3768 | 122.2335 | 1.3007 | -122.4191
4295.0469 | 122.3282 | -0.10529 | 122.2687 | -0.010149 | -0.056307 | 0.038798 | 0.017546 | -0.014429 | -0.0012349 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.050517 | 0.045765 | -0.017266 | 0.028878 | -0.017566 | 0.088755 | 0.12857 | 0.22896 | -0.09511 | 0.097201 | 1.2641 | -0.028879 | 122.0373 | 122.3173 | 122.1878 | -0.16415 | 0.010176 | -122.1799 | 0.08802 | 0.08772 | 0.077544 | -122.1401 | -122.0397 | -0.058863 | -0.23137 | 0.20249 | 0.076407 | 0.13527 | 0.04866 | -0.080918 | 0.19404 | 0.23385 | 0.33425 | 0.13416 | -122.3638 | 122.1426 | 122.4226 | 122.293 | 1.3694 | -122.4328
4296.7344 | 122.4197 | -0.07782 | 122.2366 | -0.01778 | -0.056521 | 0.039011 | 0.017546 | -0.014215 | -0.0012349 | -0.036779 | -0.0024804 | -0.0022903 | 0.056551 | 0.050517 | 0.045551 | -0.021844 | 0.028878 | -0.017566 | 0.088755 | 0.12857 | 0.23354 | -0.099689 | 0.10178 | 1.2641 | -0.0243 | 122.0373 | 122.3265 | 122.2015 | -0.17331 | -0.021869 | -122.1479 | 0.055976 | 0.060254 | 0.082123 | -122.1081 | -122.0031 | -0.095486 | -0.19933 | 0.1796 | 0.05352 | 0.14901 | 0.089861 | -0.035138 | 0.16658 | 0.20639 | 0.31136 | 0.1067 | -122.3363 | 122.1151 | 122.4043 | 122.2793 | 1.3419 | -122.4099
4298.4375 | 122.3877 | -0.086975 | 122.2595 | -0.010149 | -0.056307 | 0.038798 | 0.017759 | -0.014215 | -0.0012349 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.050517 | 0.045765 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.12399 | 0.23354 | -0.09511 | 0.097201 | 1.2687 | -0.028879 | 122.0373 | 122.3265 | 122.2015 | -0.16415 | -0.008135 | -122.1799 | 0.065131 | 0.073987 | 0.082122 | -122.1355 | -122.026 | -0.077174 | -0.22222 | 0.18418 | 0.058096 | 0.13527 | 0.066973 | -0.058026 | 0.16657 | 0.21097 | 0.32051 | 0.11127 | -122.3546 | 122.1243 | 122.4135 | 122.2885 | 1.3556 | -122.4237
4300.1875 | 122.3328 | -0.11444 | 122.2687 | -0.010149 | -0.056735 | 0.039011 | 0.017759 | -0.014215 | -0.0010213 | -0.013887 | -0.0022666 | -0.0020767 | 0.056764 | 0.050303 | 0.045978 | -0.012688 | 0.028878 | -0.012988 | 0.079598 | 0.12399 | 0.22896 | -0.09511 | 0.092622 | 1.2641 | -0.033458 | 122.0373 | 122.3219 | 122.1969 | -0.17331 | 0.019331 | -122.1891 | 0.10175 | 0.10145 | 0.082122 | -122.1447 | -122.0397 | -0.058865 | -0.23137 | 0.20706 | 0.080983 | 0.13985 | 0.053239 | -0.071761 | 0.19404 | 0.23843 | 0.3434 | 0.14332 | -122.3638 | 122.1517 | 122.4364 | 122.3114 | 1.3785 | -122.442
4301.8906 | 122.4747 | -0.059509 | 122.2229 | -0.01778 | -0.056521 | 0.039011 | 0.017332 | -0.014215 | -0.0010213 | -0.021518 | -0.002053 | -0.0022903 | 0.056978 | 0.050517 | 0.045978 | -0.021844 | 0.028878 | -0.017566 | 0.084176 | 0.12399 | 0.23812 | -0.099689 | 0.10178 | 1.2778 | -0.033458 | 122.0281 | 122.3219 | 122.1969 | -0.16873 | -0.04018 | -122.1387 | 0.037665 | 0.041943 | 0.082123 | -122.0989 | -121.9848 | -0.10922 | -0.19475 | 0.16129 | 0.026051 | 0.13527 | 0.099016 | -0.025984 | 0.14369 | 0.1835 | 0.29763 | 0.088387 | -122.3226 | 122.0877 | 122.3814 | 122.2564 | 1.3373 | -122.3916
4303.6406 | 122.3969 | -0.10071 | 122.2504 | -0.01778 | -0.056521 | 0.039011 | 0.017332 | -0.014215 | -0.00080773 | -0.013887 | -0.002694 | -0.0020767 | 0.056978 | 0.050944 | 0.045978 | -0.017266 | 0.0243 | -0.012988 | 0.084176 | 0.12857 | 0.22896 | -0.099689 | 0.097201 | 1.2687 | -0.028879 | 122.0373 | 122.3219 | 122.1969 | -0.17331 | 0.001019 | -122.1662 | 0.083442 | 0.08772 | 0.086701 | -122.1218 | -122.0214 | -0.072598 | -0.21306 | 0.19791 | 0.071829 | 0.14443 | 0.07155 | -0.05345 | 0.18488 | 0.22928 | 0.32967 | 0.12501 | -122.3501 | 122.138 | 122.4226 | 122.2976 | 1.3694 | -122.4237
4305.375 | 122.3511 | -0.10071 | 122.2778 | -0.01778 | -0.056094 | 0.038584 | 0.017332 | -0.014215 | -0.0010213 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.050303 | 0.045978 | -0.017266 | 0.019721 | -0.012988 | 0.079598 | 0.12399 | 0.23354 | -0.099689 | 0.092622 | 1.2732 | -0.033458 | 122.0373 | 122.3265 | 122.2015 | -0.17331 | 0.001019 | -122.1982 | 0.083442 | 0.08772 | 0.086701 | -122.1538 | -122.0443 | -0.072598 | -0.24053 | 0.19333 | 0.06725 | 0.13985 | 0.048662 | -0.076337 | 0.18031 | 0.2247 | 0.33425 | 0.12043 | -122.3775 | 122.138 | 122.4272 | 122.3022 | 1.3739 | -122.4511
4307.0781 | 122.4335 | -0.082397 | 122.2275 | -0.01778 | -0.056521 | 0.038798 | 0.017546 | -0.014429 | -0.0010213 | -0.029148 | -0.0024804 | -0.0020767 | 0.056978 | 0.050944 | 0.046192 | -0.017266 | 0.0243 | -0.026723 | 0.084176 | 0.11941 | 0.23354 | -0.099689 | 0.088043 | 1.2778 | -0.0243 | 122.0327 | 122.3219 | 122.1923 | -0.17331 | -0.017292 | -122.1433 | 0.065131 | 0.055674 | 0.072966 | -122.1081 | -121.9939 | -0.090909 | -0.19475 | 0.17044 | 0.058097 | 0.14901 | 0.094438 | -0.035141 | 0.16657 | 0.20181 | 0.31593 | 0.1067 | -122.3272 | 122.1151 | 122.4043 | 122.2747 | 1.3602 | -122.4008
4308.8125 | 122.3877 | -0.073242 | 122.2961 | -0.010149 | -0.056521 | 0.038798 | 0.017332 | -0.014001 | -0.00059393 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.05073 | 0.045551 | -0.012688 | 0.028878 | -0.017566 | 0.088755 | 0.12399 | 0.23812 | -0.085952 | 0.092622 | 1.2778 | -0.028879 | 122.0373 | 122.3311 | 122.2061 | -0.17331 | -0.01271 | -122.2074 | 0.060554 | 0.055676 | 0.068386 | -122.1722 | -122.058 | -0.10006 | -0.25884 | 0.16586 | 0.044363 | 0.14443 | 0.03493 | -0.09007 | 0.162 | 0.19723 | 0.31136 | 0.10212 | -122.3821 | 122.1105 | 122.4043 | 122.2793 | 1.3511 | -122.4694
4310.6094 | 122.3511 | -0.086975 | 122.2733 | -0.01778 | -0.056521 | 0.039011 | 0.017332 | -0.014215 | -0.00080773 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.050517 | 0.045978 | -0.017266 | 0.0243 | -0.022144 | 0.084176 | 0.12399 | 0.23812 | -0.099689 | 0.092622 | 1.2916 | -0.0243 | 122.0373 | 122.3311 | 122.1923 | -0.17331 | -0.012714 | -122.1891 | 0.069709 | 0.064831 | 0.077545 | -122.1493 | -122.0351 | -0.086331 | -0.23595 | 0.1796 | 0.062675 | 0.14901 | 0.057819 | -0.080917 | 0.17115 | 0.21097 | 0.32509 | 0.11127 | -122.3729 | 122.1243 | 122.418 | 122.2793 | 1.3785 | -122.4466
4312.3906 | 122.3282 | -0.082397 | 122.287 | -0.010149 | -0.056307 | 0.039011 | 0.017118 | -0.014215 | -0.0010213 | -0.013887 | -0.002694 | -0.0022903 | 0.056978 | 0.050517 | 0.046192 | -0.021844 | 0.033457 | -0.017566 | 0.084176 | 0.11483 | 0.23812 | -0.099689 | 0.092622 | 1.2916 | -0.033458 | 122.0327 | 122.3219 | 122.2061 | -0.18246 | -0.017292 | -122.2028 | 0.060553 | 0.064831 | 0.082123 | -122.1722 | -122.0489 | -0.10007 | -0.25426 | 0.17502 | 0.048939 | 0.14901 | 0.034929 | -0.080914 | 0.16657 | 0.19723 | 0.32051 | 0.11585 | -122.3867 | 122.1151 | 122.4043 | 122.2885 | 1.374 | -122.4695
4314.125 | 122.3557 | -0.10986 | 122.2824 | 0.0051128 | -0.056307 | 0.038798 | 0.017118 | -0.014215 | -0.00059393 | -0.021518 | -0.002694 | -0.0022903 | 0.056764 | 0.050303 | 0.045765 | -0.017266 | 0.019721 | -0.003831 | 0.079598 | 0.12857 | 0.22896 | -0.09511 | 0.088043 | 1.287 | -0.028879 | 122.0419 | 122.3265 | 122.1969 | -0.16873 | 0.014753 | -122.2028 | 0.092597 | 0.10603 | 0.091279 | -122.1538 | -122.0535 | -0.058865 | -0.24053 | 0.19791 | 0.080984 | 0.13985 | 0.044084 | -0.085494 | 0.18946 | 0.23843 | 0.33882 | 0.12958 | -122.3775 | 122.1517 | 122.4364 | 122.3068 | 1.3968 | -122.4511
4315.8906 | 122.438 | -0.059509 | 122.2366 | -0.0025182 | -0.056307 | 0.039011 | 0.017118 | -0.014429 | -0.00038033 | -0.013887 | -0.0024804 | -0.0022903 | 0.056764 | 0.050517 | 0.045765 | -0.021844 | 0.0243 | -0.012988 | 0.084176 | 0.11941 | 0.23354 | -0.09511 | 0.097201 | 1.287 | -0.028879 | 122.0419 | 122.3219 | 122.1878 | -0.17788 | -0.035601 | -122.1525 | 0.037665 | 0.046521 | 0.082122 | -122.1172 | -122.0031 | -0.11838 | -0.19475 | 0.15671 | 0.03063 | 0.14901 | 0.085283 | -0.048874 | 0.14369 | 0.17892 | 0.29305 | 0.083809 | -122.3317 | 122.1014 | 122.3814 | 122.2473 | 1.3465 | -122.4145
4317.6562 | 122.3602 | -0.10071 | 122.2824 | -0.010149 | -0.056521 | 0.039011 | 0.017332 | -0.014215 | -0.00080773 | -0.029148 | -0.002694 | -0.0022903 | 0.056764 | 0.050517 | 0.045978 | -0.021844 | 0.0243 | -0.022144 | 0.079598 | 0.12399 | 0.23812 | -0.09511 | 0.097201 | 1.2961 | -0.033458 | 122.0465 | 122.3311 | 122.1923 | -0.17331 | 0.005598 | -122.2028 | 0.078864 | 0.078564 | 0.072966 | -122.1584 | -122.0443 | -0.072598 | -0.23595 | 0.19791 | 0.06725 | 0.13985 | 0.048663 | -0.090073 | 0.18031 | 0.2247 | 0.33882 | 0.12501 | -122.3775 | 122.1472 | 122.4318 | 122.293 | 1.3968 | -122.4557
4319.3594 | 122.4884 | -0.045776 | 122.2366 | -0.025411 | -0.056521 | 0.038584 | 0.017118 | -0.014215 | -0.00059393 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.050303 | 0.045765 | -0.026423 | 0.0243 | -0.017566 | 0.07502 | 0.12399 | 0.23812 | -0.090531 | 0.092622 | 1.287 | -0.028879 | 122.0419 | 122.3173 | 122.1969 | -0.16873 | -0.044755 | -122.1616 | 0.019353 | 0.02821 | 0.072965 | -122.1126 | -121.9985 | -0.12295 | -0.19475 | 0.1384 | 0.016897 | 0.13985 | 0.080704 | -0.039717 | 0.1208 | 0.16977 | 0.28389 | 0.070076 | -122.3272 | 122.0877 | 122.3631 | 122.2427 | 1.3328 | -122.4054
4321.125 | 122.4289 | -0.073242 | 122.2549 | -0.010149 | -0.056521 | 0.039011 | 0.017332 | -0.014642 | -0.00059393 | -0.021518 | -0.0029076 | -0.0022903 | 0.056764 | 0.050517 | 0.045765 | -0.017266 | 0.028878 | -0.012988 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.097201 | 1.2916 | -0.028879 | 122.0373 | 122.3219 | 122.1923 | -0.17331 | -0.026447 | -122.1708 | 0.055976 | 0.060254 | 0.086701 | -122.1264 | -122.0168 | -0.10006 | -0.21764 | 0.17044 | 0.044363 | 0.14443 | 0.066972 | -0.062607 | 0.15742 | 0.20181 | 0.31136 | 0.10212 | -122.3546 | 122.1105 | 122.3952 | 122.2656 | 1.3648 | -122.4282
4322.8125 | 122.3648 | -0.10071 | 122.2687 | -0.010149 | -0.056521 | 0.038798 | 0.017546 | -0.014429 | -0.00080773 | -0.021518 | -0.0022666 | -0.0025041 | 0.056764 | 0.05073 | 0.045765 | -0.021844 | 0.028878 | -0.026723 | 0.084176 | 0.12399 | 0.22896 | -0.09511 | 0.097201 | 1.2961 | -0.028879 | 122.0373 | 122.3219 | 122.1969 | -0.18246 | 0.005598 | -122.1845 | 0.078864 | 0.073985 | 0.068387 | -122.1447 | -122.0397 | -0.081756 | -0.23137 | 0.19791 | 0.071829 | 0.15358 | 0.053239 | -0.071761 | 0.18488 | 0.2247 | 0.32967 | 0.12959 | -122.3638 | 122.138 | 122.4226 | 122.2976 | 1.3968 | -122.4511
4324.5781 | 122.3511 | -0.082397 | 122.2778 | -0.01778 | -0.056094 | 0.038584 | 0.017546 | -0.014001 | -0.00080773 | -0.013887 | -0.0022666 | -0.0022903 | 0.056551 | 0.050303 | 0.046192 | -0.026423 | 0.0243 | -0.012988 | 0.084176 | 0.11941 | 0.24269 | -0.099689 | 0.097201 | 1.3053 | -0.0243 | 122.0327 | 122.3173 | 122.2061 | -0.16415 | -0.017292 | -122.1937 | 0.055974 | 0.069409 | 0.086701 | -122.1584 | -122.0351 | -0.081752 | -0.24511 | 0.1796 | 0.058097 | 0.13985 | 0.039505 | -0.071759 | 0.16657 | 0.20181 | 0.32509 | 0.1067 | -122.3775 | 122.1151 | 122.3997 | 122.2885 | 1.3877 | -122.442
4326.3438 | 122.4106 | -0.091553 | 122.2641 | -0.01778 | -0.056094 | 0.038798 | 0.017332 | -0.014215 | -0.00080773 | -0.029148 | -0.0024804 | -0.0022903 | 0.056764 | 0.050517 | 0.045551 | -0.021844 | 0.028878 | -0.017566 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.092622 | 1.3053 | -0.038036 | 122.0281 | 122.3219 | 122.1969 | -0.16873 | -0.008136 | -122.1799 | 0.069709 | 0.073987 | 0.082123 | -122.1355 | -122.026 | -0.077175 | -0.23595 | 0.18417 | 0.053517 | 0.13069 | 0.057817 | -0.067183 | 0.17573 | 0.22012 | 0.32967 | 0.12043 | -122.3638 | 122.1197 | 122.4135 | 122.2885 | 1.3968 | -122.4328
4328.1094 | 122.3328 | -0.10071 | 122.2641 | 0.0051128 | -0.056521 | 0.039225 | 0.017118 | -0.014429 | -0.00059393 | -0.029148 | -0.0024804 | -0.0022903 | 0.056978 | 0.05073 | 0.045978 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.11941 | 0.23354 | -0.099689 | 0.097201 | 1.3099 | -0.028879 | 122.0419 | 122.3311 | 122.1923 | -0.17331 | 0.001019 | -122.1799 | 0.083442 | 0.083142 | 0.082123 | -122.1447 | -122.0306 | -0.072598 | -0.22222 | 0.19791 | 0.071829 | 0.14443 | 0.066974 | -0.071762 | 0.18488 | 0.22012 | 0.33425 | 0.12501 | -122.3638 | 122.1426 | 122.4318 | 122.293 | 1.4106 | -122.4374
4329.8125 | 122.3282 | -0.10986 | 122.2687 | 0.0051128 | -0.056521 | 0.038798 | 0.017546 | -0.014429 | -0.00059393 | -0.029148 | -0.002694 | -0.0027177 | 0.056764 | 0.05073 | 0.045765 | -0.021844 | 0.028878 | -0.017566 | 0.084176 | 0.12399 | 0.23354 | -0.09511 | 0.092622 | 1.3053 | -0.0243 | 122.0327 | 122.3219 | 122.1969 | -0.17331 | 0.014753 | -122.1845 | 0.088019 | 0.092297 | 0.077544 | -122.1447 | -122.0351 | -0.063443 | -0.23595 | 0.20248 | 0.085563 | 0.14901 | 0.053239 | -0.071761 | 0.19404 | 0.23385 | 0.3434 | 0.13874 | -122.3638 | 122.1426 | 122.4318 | 122.3068 | 1.4152 | -122.442
4331.5781 | 122.4197 | -0.054932 | 122.2687 | -0.01778 | -0.056735 | 0.039011 | 0.017118 | -0.014001 | -0.00059393 | -0.021518 | -0.0022666 | -0.0020767 | 0.056551 | 0.05073 | 0.045978 | -0.021844 | 0.028878 | -0.017566 | 0.084176 | 0.12399 | 0.23354 | -0.099689 | 0.097201 | 1.3144 | -0.028879 | 122.0327 | 122.3265 | 122.1969 | -0.17331 | -0.044757 | -122.1845 | 0.033088 | 0.037366 | 0.082123 | -122.1447 | -122.0351 | -0.11837 | -0.23595 | 0.15213 | 0.026053 | 0.14443 | 0.057817 | -0.071761 | 0.13911 | 0.17892 | 0.28847 | 0.08381 | -122.3684 | 122.0877 | 122.3814 | 122.2518 | 1.3694 | -122.442
4333.3281 | 122.4197 | -0.064087 | 122.2549 | -0.0025182 | -0.056735 | 0.038798 | 0.016905 | -0.014215 | -0.00038033 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.050944 | 0.045978 | -0.021844 | 0.0243 | -0.017566 | 0.084176 | 0.12399 | 0.24269 | -0.09511 | 0.097201 | 1.3099 | -0.033458 | 122.0373 | 122.3219 | 122.1923 | -0.17331 | -0.031023 | -122.1708 | 0.042243 | 0.046521 | 0.077544 | -122.131 | -122.0122 | -0.10922 | -0.21764 | 0.16129 | 0.030629 | 0.13985 | 0.066972 | -0.062607 | 0.14826 | 0.18808 | 0.30678 | 0.088387 | -122.3501 | 122.1014 | 122.386 | 122.2564 | 1.374 | -122.4282
4335.0938 | 122.3373 | -0.10071 | 122.2778 | -0.010149 | -0.056307 | 0.038798 | 0.017546 | -0.014001 | -0.00059393 | -0.036779 | -0.002694 | -0.0022903 | 0.056764 | 0.050517 | 0.045551 | -0.012688 | 0.033457 | -0.017566 | 0.084176 | 0.12857 | 0.23812 | -0.10427 | 0.097201 | 1.3236 | -0.028879 | 122.0281 | 122.3265 | 122.1969 | -0.17331 | -0.00356 | -122.1937 | 0.08802 | 0.083142 | 0.086702 | -122.1493 | -122.0397 | -0.072598 | -0.24968 | 0.19791 | 0.071829 | 0.14443 | 0.048662 | -0.080916 | 0.18488 | 0.22928 | 0.33882 | 0.13417 | -122.3821 | 122.1289 | 122.4272 | 122.2976 | 1.4243 | -122.4511
4336.8125 | 122.4426 | -0.064087 | 122.2412 | -0.025411 | -0.056948 | 0.038798 | 0.017118 | -0.014642 | -0.00059393 | -0.013887 | -0.0024804 | -0.0022903 | 0.056764 | 0.05073 | 0.045765 | -0.017266 | 0.028878 | -0.012988 | 0.079598 | 0.11941 | 0.23812 | -0.099689 | 0.097201 | 1.3144 | -0.028879 | 122.0373 | 122.3311 | 122.1923 | -0.17788 | -0.035602 | -122.1616 | 0.046821 | 0.051099 | 0.086701 | -122.1218 | -122.0031 | -0.1138 | -0.20391 | 0.16129 | 0.035208 | 0.14901 | 0.089862 | -0.048874 | 0.14369 | 0.1835 | 0.3022 | 0.092965 | -122.3409 | 122.1014 | 122.3952 | 122.2564 | 1.3785 | -122.4191
4338.5625 | 122.4564 | -0.059509 | 122.2412 | -0.010149 | -0.056735 | 0.038584 | 0.017118 | -0.014215 | -0.00016673 | -0.029148 | -0.0024804 | -0.0025041 | 0.056978 | 0.050944 | 0.045765 | -0.017266 | 0.028878 | -0.008409 | 0.079598 | 0.12399 | 0.24269 | -0.09511 | 0.092622 | 1.3144 | -0.0243 | 122.0373 | 122.3219 | 122.1969 | -0.18246 | -0.035601 | -122.1616 | 0.042243 | 0.0511 | 0.086701 | -122.1172 | -121.9985 | -0.12295 | -0.20391 | 0.15213 | 0.035209 | 0.15816 | 0.080705 | -0.044295 | 0.13911 | 0.1835 | 0.3022 | 0.088387 | -122.3363 | 122.0968 | 122.3814 | 122.2564 | 1.374 | -122.4237
4340.3281 | 122.3785 | -0.10071 | 122.2733 | -0.010149 | -0.056735 | 0.038584 | 0.017118 | -0.014215 | -0.00016673 | -0.021518 | -0.0024804 | -0.0027177 | 0.056978 | 0.050517 | 0.045765 | -0.021844 | 0.0243 | -0.017566 | 0.079598 | 0.12857 | 0.24269 | -0.09511 | 0.097201 | 1.319 | -0.0243 | 122.0373 | 122.3265 | 122.1969 | -0.16873 | 0.005598 | -122.1937 | 0.078864 | 0.083142 | 0.077544 | -122.1447 | -122.0306 | -0.06802 | -0.23595 | 0.19791 | 0.076408 | 0.14443 | 0.05324 | -0.076338 | 0.18031 | 0.22928 | 0.3434 | 0.12501 | -122.3684 | 122.138 | 122.4272 | 122.2976 | 1.4197 | -122.442
4342.0938 | 122.4564 | -0.045776 | 122.2321 | -0.010149 | -0.056521 | 0.03837 | 0.016905 | -0.014642 | -0.00038033 | -0.013887 | -0.0024804 | -0.0022903 | 0.056978 | 0.050303 | 0.045978 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.11941 | 0.23812 | -0.09511 | 0.092622 | 1.3282 | -0.028879 | 122.0327 | 122.3219 | 122.1923 | -0.17788 | -0.049334 | -122.1479 | 0.02851 | 0.02821 | 0.077544 | -122.1126 | -121.9939 | -0.13211 | -0.19933 | 0.1384 | 0.016897 | 0.14901 | 0.08986 | -0.039719 | 0.12995 | 0.16519 | 0.28389 | 0.070076 | -122.3272 | 122.0785 | 122.3677 | 122.2381 | 1.374 | -122.4099
4343.7969 | 122.4701 | -0.054932 | 122.2321 | -0.0025182 | -0.056735 | 0.038798 | 0.017118 | -0.014001 | -0.00038033 | -0.021518 | -0.0022666 | -0.0020767 | 0.056978 | 0.050303 | 0.045978 | -0.026423 | 0.0243 | -0.017566 | 0.079598 | 0.12399 | 0.23812 | -0.090531 | 0.097201 | 1.3282 | -0.028879 | 122.0327 | 122.3265 | 122.1923 | -0.17788 | -0.035599 | -122.1525 | 0.028509 | 0.037366 | 0.072965 | -122.1081 | -121.9939 | -0.12295 | -0.19933 | 0.15213 | 0.026053 | 0.14901 | 0.094438 | -0.039719 | 0.13453 | 0.17892 | 0.29305 | 0.079232 | -122.3226 | 122.0877 | 122.3814 | 122.2473 | 1.3831 | -122.4099
4345.5625 | 122.3236 | -0.10986 | 122.2916 | -0.010149 | -0.056948 | 0.038798 | 0.017118 | -0.014429 | -0.00038033 | -0.021518 | -0.002694 | -0.0022903 | 0.056764 | 0.05073 | 0.045765 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.12857 | 0.23354 | -0.099689 | 0.092622 | 1.3328 | -0.0243 | 122.0236 | 122.3219 | 122.1878 | -0.17331 | 0.010174 | -122.2074 | 0.092597 | 0.092297 | 0.082123 | -122.163 | -122.058 | -0.063443 | -0.26799 | 0.20248 | 0.085563 | 0.14901 | 0.030351 | -0.10381 | 0.19404 | 0.23843 | 0.3434 | 0.13416 | -122.3913 | 122.1334 | 122.4318 | 122.2976 | 1.4426 | -122.4649
4347.3281 | 122.3328 | -0.091553 | 122.2687 | -0.010149 | -0.056521 | 0.03837 | 0.017118 | -0.014215 | -0.00059393 | -0.029148 | -0.0024804 | -0.0025041 | 0.057191 | 0.05073 | 0.045551 | -0.017266 | 0.028878 | -0.012988 | 0.079598 | 0.12857 | 0.23354 | -0.09511 | 0.097201 | 1.3419 | -0.028879 | 122.0373 | 122.3219 | 122.1923 | -0.17331 | -0.003557 | -122.1891 | 0.074287 | 0.078565 | 0.082122 | -122.1401 | -122.0351 | -0.081753 | -0.23137 | 0.18875 | 0.062674 | 0.14443 | 0.053239 | -0.07634 | 0.17115 | 0.22012 | 0.32509 | 0.12043 | -122.3638 | 122.1289 | 122.4135 | 122.2839 | 1.4335 | -122.442
4349.0312 | 122.3877 | -0.10529 | 122.2824 | -0.0025182 | -0.056735 | 0.038798 | 0.017332 | -0.014429 | -0.00016673 | -0.021518 | -0.002694 | -0.0022903 | 0.056978 | 0.050517 | 0.045337 | -0.008109 | 0.028878 | -0.022144 | 0.07502 | 0.11941 | 0.23354 | -0.09511 | 0.10178 | 1.3419 | -0.033458 | 122.0465 | 122.3265 | 122.1969 | -0.16873 | 0.010176 | -122.2074 | 0.097177 | 0.083142 | 0.072966 | -122.163 | -122.0489 | -0.063442 | -0.23595 | 0.20706 | 0.071828 | 0.13527 | 0.044084 | -0.085494 | 0.18031 | 0.2247 | 0.33882 | 0.13416 | -122.3775 | 122.1517 | 122.4318 | 122.3022 | 1.4472 | -122.4511
4350.7969 | 122.3557 | -0.082397 | 122.2549 | -0.01778 | -0.056735 | 0.038584 | 0.016905 | -0.014215 | -0.00016673 | -0.0062567 | -0.002694 | -0.0020767 | 0.056978 | 0.050517 | 0.046192 | -0.017266 | 0.028878 | -0.017566 | 0.088755 | 0.11941 | 0.23812 | -0.09511 | 0.092622 | 1.3419 | -0.028879 | 122.0373 | 122.3265 | 122.1923 | -0.17331 | -0.012713 | -122.1662 | 0.065131 | 0.064831 | 0.077544 | -122.1355 | -122.0168 | -0.090909 | -0.21764 | 0.17502 | 0.053518 | 0.14443 | 0.07155 | -0.062607 | 0.17115 | 0.20181 | 0.32051 | 0.11127 | -122.3501 | 122.1197 | 122.4089 | 122.2747 | 1.4243 | -122.4282
4352.5781 | 122.3373 | -0.10529 | 122.2733 | 0.0051128 | -0.056948 | 0.039011 | 0.017332 | -0.014642 | -0.00038033 | -0.029148 | -0.0022666 | -0.0022903 | 0.056764 | 0.05073 | 0.045765 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.12857 | 0.23354 | -0.09511 | 0.10178 | 1.3465 | -0.0243 | 122.0373 | 122.3265 | 122.1969 | -0.17331 | 0.010176 | -122.1891 | 0.08802 | 0.08772 | 0.077544 | -122.1447 | -122.0397 | -0.06802 | -0.23595 | 0.20706 | 0.080986 | 0.14901 | 0.05324 | -0.076338 | 0.18946 | 0.23385 | 0.33882 | 0.12959 | -122.3684 | 122.1426 | 122.4318 | 122.3022 | 1.4518 | -122.4466
4354.2812 | 122.4518 | -0.045776 | 122.2 | -0.0025182 | -0.056735 | 0.038584 | 0.017118 | -0.014429 | -0.00016673 | -0.013887 | -0.002694 | -0.0020767 | 0.056551 | 0.050517 | 0.045551 | -0.017266 | 0.033457 | -0.012988 | 0.084176 | 0.12857 | 0.23354 | -0.09511 | 0.097201 | 1.3511 | -0.033458 | 122.0327 | 122.3219 | 122.1923 | -0.17788 | -0.049334 | -122.1158 | 0.02851 | 0.032788 | 0.082122 | -122.0714 | -121.9665 | -0.13211 | -0.16729 | 0.14298 | 0.012318 | 0.14443 | 0.1219 | -0.007675 | 0.12995 | 0.17434 | 0.27931 | 0.079233 | -122.2951 | 122.0785 | 122.3677 | 122.2381 | 1.3969 | -122.3779
4356.0469 | 122.3465 | -0.09613 | 122.2412 | 0.0051128 | -0.056307 | 0.039225 | 0.017332 | -0.014429 | -0.00038033 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.05073 | 0.045551 | -0.017266 | 0.028878 | -0.012988 | 0.084176 | 0.12857 | 0.23354 | -0.099689 | 0.097201 | 1.3465 | -0.028879 | 122.0373 | 122.3219 | 122.1923 | -0.17331 | -0.003559 | -122.157 | 0.078864 | 0.083142 | 0.086701 | -122.1126 | -122.0077 | -0.077176 | -0.20391 | 0.19333 | 0.067251 | 0.14443 | 0.080705 | -0.048874 | 0.18031 | 0.2247 | 0.32967 | 0.12501 | -122.3409 | 122.1334 | 122.418 | 122.2885 | 1.4426 | -122.4145
4357.8125 | 122.374 | -0.086975 | 122.2504 | -0.01778 | -0.056735 | 0.038798 | 0.017118 | -0.014215 | -0.00016673 | -0.013887 | -0.002694 | -0.0022903 | 0.056978 | 0.05073 | 0.045765 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.12399 | 0.23354 | -0.09511 | 0.083464 | 1.3511 | -0.028879 | 122.0373 | 122.3173 | 122.1969 | -0.17331 | -0.008135 | -122.1662 | 0.065131 | 0.078566 | 0.086701 | -122.1264 | -122.0168 | -0.086331 | -0.21306 | 0.17044 | 0.058096 | 0.14443 | 0.066971 | -0.05345 | 0.17115 | 0.21097 | 0.32051 | 0.11127 | -122.3455 | 122.1243 | 122.4043 | 122.2839 | 1.4381 | -122.4237
4359.5781 | 122.4152 | -0.064087 | 122.2549 | -0.010149 | -0.056948 | 0.038798 | 0.017332 | -0.014429 | -0.00016673 | -0.029148 | -0.0022666 | -0.0022903 | 0.056978 | 0.050517 | 0.045978 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.12399 | 0.24269 | -0.10427 | 0.092622 | 1.3557 | -0.033458 | 122.0281 | 122.3219 | 122.2015 | -0.17788 | -0.040181 | -122.1753 | 0.042243 | 0.051099 | 0.09128 | -122.131 | -122.0122 | -0.1138 | -0.22679 | 0.15671 | 0.030629 | 0.14443 | 0.066972 | -0.053449 | 0.14369 | 0.18808 | 0.30678 | 0.088387 | -122.3592 | 122.0922 | 122.386 | 122.2656 | 1.4197 | -122.4328
4361.3438 | 122.3831 | -0.10529 | 122.2504 | -0.01778 | -0.056948 | 0.038584 | 0.017118 | -0.014215 | 0.00026067 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.050944 | 0.045765 | -0.017266 | 0.019721 | -0.012988 | 0.079598 | 0.12399 | 0.22896 | -0.09511 | 0.097201 | 1.3648 | -0.028879 | 122.0419 | 122.3311 | 122.1878 | -0.16415 | 0.010176 | -122.1708 | 0.08802 | 0.092298 | 0.082122 | -122.1264 | -122.0214 | -0.058863 | -0.20848 | 0.20249 | 0.076407 | 0.13527 | 0.080707 | -0.062607 | 0.18488 | 0.22928 | 0.33425 | 0.12501 | -122.3455 | 122.1472 | 122.4364 | 122.293 | 1.4701 | -122.4145
4363.125 | 122.4426 | -0.041199 | 122.2549 | -0.010149 | -0.056735 | 0.03837 | 0.016905 | -0.014429 | 0.00068807 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.050517 | 0.045551 | -0.012688 | 0.028878 | -0.017566 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.092622 | 1.3648 | -0.038036 | 122.0373 | 122.3265 | 122.1969 | -0.17331 | -0.05849 | -122.1708 | 0.028511 | 0.023633 | 0.082123 | -122.1264 | -122.0168 | -0.13211 | -0.21764 | 0.13382 | 0.003163 | 0.13527 | 0.07155 | -0.058028 | 0.12538 | 0.16977 | 0.27932 | 0.070077 | -122.3546 | 122.0785 | 122.3677 | 122.2381 | 1.406 | -122.4282
4364.8281 | 122.4655 | -0.054932 | 122.2183 | -0.01778 | -0.056948 | 0.038798 | 0.017546 | -0.014642 | 0.00026067 | -0.021518 | -0.0024804 | -0.0022903 | 0.056551 | 0.05073 | 0.045765 | -0.017266 | 0.0243 | -0.012988 | 0.079598 | 0.12857 | 0.23354 | -0.09511 | 0.10178 | 1.3694 | -0.033458 | 122.0327 | 122.3311 | 122.1878 | -0.17331 | -0.040178 | -122.1387 | 0.037666 | 0.041944 | 0.082122 | -122.0898 | -121.9848 | -0.11837 | -0.1856 | 0.15671 | 0.021474 | 0.13985 | 0.11275 | -0.030564 | 0.13453 | 0.1835 | 0.28847 | 0.079232 | -122.3134 | 122.0877 | 122.386 | 122.2427 | 1.4243 | -122.3916
4366.5938 | 122.4564 | -0.054932 | 122.2321 | -0.010149 | -0.056735 | 0.039011 | 0.017118 | -0.014215 | 0.00047427 | -0.013887 | -0.0022666 | -0.0018631 | 0.056764 | 0.05073 | 0.046192 | -0.026423 | 0.0243 | -0.017566 | 0.084176 | 0.11483 | 0.22896 | -0.10427 | 0.097201 | 1.3786 | -0.033458 | 122.0281 | 122.3311 | 122.1878 | -0.17331 | -0.049336 | -122.1479 | 0.028509 | 0.037366 | 0.086702 | -122.1172 | -122.0031 | -0.11837 | -0.20391 | 0.15213 | 0.021474 | 0.13985 | 0.099017 | -0.044297 | 0.13911 | 0.16976 | 0.28389 | 0.079232 | -122.3363 | 122.0831 | 122.386 | 122.2427 | 1.4335 | -122.4054
4368.3438 | 122.3557 | -0.10529 | 122.2549 | -0.010149 | -0.056948 | 0.039011 | 0.017118 | -0.014215 | 4.7068e-05 | -0.021518 | -0.002694 | -0.0022903 | 0.056978 | 0.050944 | 0.045551 | -0.017266 | 0.028878 | -0.017566 | 0.084176 | 0.12399 | 0.23812 | -0.09511 | 0.092622 | 1.3831 | -0.028879 | 122.0327 | 122.3265 | 122.1832 | -0.17788 | 0.010176 | -122.1708 | 0.08802 | 0.08772 | 0.077544 | -122.131 | -122.0168 | -0.072599 | -0.22222 | 0.19791 | 0.076407 | 0.14901 | 0.07155 | -0.071764 | 0.18946 | 0.22928 | 0.3434 | 0.13416 | -122.3501 | 122.138 | 122.4318 | 122.2885 | 1.4884 | -122.4328
4370.0469 | 122.4655 | -0.059509 | 122.2092 | -0.010149 | -0.056735 | 0.038584 | 0.016905 | -0.014215 | 0.00026067 | -0.013887 | -0.0022666 | -0.0025041 | 0.056764 | 0.050944 | 0.045765 | -0.026423 | 0.033457 | -0.012988 | 0.079598 | 0.12399 | 0.23812 | -0.099689 | 0.097201 | 1.3969 | -0.0243 | 122.0373 | 122.3357 | 122.1878 | -0.17788 | -0.04018 | -122.1296 | 0.033086 | 0.046521 | 0.086701 | -122.0852 | -121.971 | -0.11838 | -0.17186 | 0.15671 | 0.035209 | 0.15358 | 0.12648 | -0.021408 | 0.13911 | 0.1835 | 0.29763 | 0.092966 | -122.3089 | 122.0968 | 122.3952 | 122.2473 | 1.4564 | -122.3871
4371.8281 | 122.3419 | -0.07782 | 122.2595 | -0.01778 | -0.056948 | 0.038584 | 0.017118 | -0.014215 | 0.00068807 | -0.036779 | -0.0024804 | -0.0022903 | 0.056978 | 0.05073 | 0.045551 | -0.017266 | 0.028878 | -0.017566 | 0.084176 | 0.11941 | 0.23354 | -0.090531 | 0.097201 | 1.4014 | -0.033458 | 122.0281 | 122.3311 | 122.1923 | -0.17788 | -0.012711 | -122.1753 | 0.060554 | 0.060254 | 0.072965 | -122.1401 | -122.026 | -0.10006 | -0.23137 | 0.17502 | 0.044362 | 0.14443 | 0.071552 | -0.067184 | 0.162 | 0.19723 | 0.31136 | 0.1067 | -122.3501 | 122.106 | 122.4089 | 122.2702 | 1.4793 | -122.4374
4373.5938 | 122.4838 | -0.050354 | 122.2595 | -0.01778 | -0.056948 | 0.038584 | 0.017118 | -0.014429 | 0.00026067 | -0.013887 | -0.0022666 | -0.0020767 | 0.056551 | 0.050944 | 0.045551 | -0.017266 | 0.028878 | -0.022144 | 0.07502 | 0.12857 | 0.23354 | -0.09511 | 0.092622 | 1.4014 | -0.028879 | 122.0419 | 122.3265 | 122.1878 | -0.16873 | -0.044756 | -122.1845 | 0.033088 | 0.02821 | 0.072966 | -122.131 | -122.026 | -0.11837 | -0.21764 | 0.14298 | 0.021475 | 0.13985 | 0.066973 | -0.071762 | 0.12537 | 0.17892 | 0.28389 | 0.079232 | -122.3546 | 122.0922 | 122.3768 | 122.2381 | 1.4518 | -122.4282
4375.3438 | 122.3465 | -0.10529 | 122.2687 | -0.01778 | -0.056948 | 0.038798 | 0.016905 | -0.014429 | 4.7068e-05 | -0.021518 | -0.0022666 | -0.0025041 | 0.056978 | 0.050944 | 0.045765 | -0.021844 | 0.033457 | -0.022144 | 0.079598 | 0.12399 | 0.24269 | -0.09511 | 0.097201 | 1.4152 | -0.028879 | 122.0373 | 122.3265 | 122.1878 | -0.17331 | 0.010176 | -122.1891 | 0.083442 | 0.083142 | 0.072966 | -122.1447 | -122.026 | -0.06802 | -0.23137 | 0.20249 | 0.076407 | 0.14443 | 0.057817 | -0.080918 | 0.18488 | 0.22928 | 0.34798 | 0.13874 | -122.3638 | 122.1426 | 122.4318 | 122.293 | 1.5205 | -122.442
4377.0469 | 122.4518 | -0.054932 | 122.2641 | -0.01778 | -0.057162 | 0.038798 | 0.016691 | -0.014429 | 0.00047427 | -0.021518 | -0.0024804 | -0.0027177 | 0.056551 | 0.051158 | 0.045551 | -0.026423 | 0.033457 | -0.026723 | 0.084176 | 0.11941 | 0.23354 | -0.09511 | 0.097201 | 1.4243 | -0.0243 | 122.0327 | 122.3219 | 122.1878 | -0.17331 | -0.040178 | -122.1799 | 0.028509 | 0.028209 | 0.068387 | -122.1447 | -122.0306 | -0.11837 | -0.23137 | 0.15213 | 0.030632 | 0.14901 | 0.057817 | -0.07634 | 0.13911 | 0.17434 | 0.28847 | 0.088389 | -122.3592 | 122.0877 | 122.3768 | 122.2427 | 1.4793 | -122.4374
4378.8125 | 122.3236 | -0.09613 | 122.2458 | -0.0025182 | -0.057162 | 0.03837 | 0.017118 | -0.014642 | 0.00026067 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.05073 | 0.045765 | -0.017266 | 0.019721 | -0.017566 | 0.084176 | 0.11941 | 0.23354 | -0.090531 | 0.10178 | 1.4335 | -0.019721 | 122.0327 | 122.3265 | 122.1923 | -0.17331 | 0.005599 | -122.1616 | 0.078864 | 0.078564 | 0.072965 | -122.1264 | -122.0123 | -0.077176 | -0.21306 | 0.19791 | 0.076409 | 0.15358 | 0.080705 | -0.053452 | 0.18031 | 0.21554 | 0.32967 | 0.11585 | -122.3363 | 122.1289 | 122.4226 | 122.2885 | 1.5296 | -122.4191
4380.5156 | 122.374 | -0.10071 | 122.2549 | -0.010149 | -0.056735 | 0.038584 | 0.017118 | -0.014429 | 0.00047427 | -0.013887 | -0.0024804 | -0.0022903 | 0.056764 | 0.05073 | 0.045978 | -0.021844 | 0.028878 | -0.017566 | 0.093333 | 0.12857 | 0.23812 | -0.09511 | 0.097201 | 1.4518 | -0.0243 | 122.0373 | 122.3173 | 122.1878 | -0.17331 | 0.005598 | -122.1616 | 0.078864 | 0.083142 | 0.077544 | -122.1264 | -122.0168 | -0.072598 | -0.21764 | 0.19791 | 0.076408 | 0.14901 | 0.062393 | -0.067185 | 0.19404 | 0.22928 | 0.33882 | 0.12959 | -122.3501 | 122.138 | 122.418 | 122.2885 | 1.5525 | -122.4282
4382.2812 | 122.4106 | -0.054932 | 122.2412 | -0.010149 | -0.056948 | 0.038584 | 0.017118 | -0.014856 | 0.00047427 | -0.029148 | -0.0022666 | -0.0022903 | 0.056551 | 0.050944 | 0.045978 | -0.012688 | 0.0243 | -0.017566 | 0.088755 | 0.11483 | 0.23812 | -0.099689 | 0.092622 | 1.4564 | -0.028879 | 122.0373 | 122.3219 | 122.1878 | -0.18246 | -0.044757 | -122.1525 | 0.042244 | 0.037366 | 0.082123 | -122.1264 | -122.0031 | -0.12753 | -0.20391 | 0.14755 | 0.026053 | 0.15358 | 0.080705 | -0.053452 | 0.14369 | 0.16976 | 0.29305 | 0.079232 | -122.3409 | 122.0922 | 122.3768 | 122.2427 | 1.5113 | -122.4237
4383.9844 | 122.3419 | -0.10529 | 122.2641 | -0.01778 | -0.056735 | 0.038798 | 0.016905 | -0.014429 | 0.00068807 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.050517 | 0.045551 | -0.017266 | 0.028878 | -0.012988 | 0.084176 | 0.12857 | 0.24269 | -0.10427 | 0.10178 | 1.4747 | -0.028879 | 122.0373 | 122.3173 | 122.1832 | -0.16873 | 0.001018 | -122.1799 | 0.08802 | 0.092298 | 0.09128 | -122.1355 | -122.0214 | -0.063442 | -0.22679 | 0.20706 | 0.076407 | 0.13985 | 0.053238 | -0.080919 | 0.18946 | 0.23385 | 0.34798 | 0.13416 | -122.3684 | 122.1426 | 122.4226 | 122.2885 | 1.58 | -122.4328
4385.75 | 122.406 | -0.068665 | 122.2275 | -0.010149 | -0.056948 | 0.038798 | 0.016905 | -0.014429 | 0.00068807 | -0.029148 | -0.002694 | -0.0020767 | 0.056551 | 0.05073 | 0.045551 | -0.021844 | 0.028878 | -0.012988 | 0.07502 | 0.12399 | 0.23354 | -0.099689 | 0.10636 | 1.4884 | -0.028879 | 122.051 | 122.3219 | 122.1878 | -0.17788 | -0.031024 | -122.1525 | 0.046821 | 0.055677 | 0.086701 | -122.1035 | -121.9939 | -0.10922 | -0.17644 | 0.17502 | 0.039786 | 0.14901 | 0.094438 | -0.039719 | 0.14369 | 0.19266 | 0.3022 | 0.097543 | -122.3272 | 122.1197 | 122.3906 | 122.2564 | 1.5571 | -122.4054
4387.5469 | 122.4655 | -0.050354 | 122.2458 | -0.025411 | -0.057162 | 0.038798 | 0.016905 | -0.014215 | 0.00068807 | -0.029148 | -0.002694 | -0.0020767 | 0.056978 | 0.05073 | 0.045765 | -0.026423 | 0.028878 | -0.017566 | 0.088755 | 0.12399 | 0.24269 | -0.099689 | 0.10178 | 1.5113 | -0.028879 | 122.0419 | 122.3219 | 122.1923 | -0.17788 | -0.049335 | -122.157 | 0.023931 | 0.032788 | 0.082123 | -122.1218 | -122.0031 | -0.12753 | -0.20391 | 0.15213 | 0.021475 | 0.14901 | 0.076127 | -0.053452 | 0.13911 | 0.17434 | 0.29305 | 0.079232 | -122.3455 | 122.0922 | 122.3723 | 122.2427 | 1.5617 | -122.4237
4389.25 | 122.3511 | -0.11902 | 122.2641 | -0.01778 | -0.057162 | 0.038584 | 0.017118 | -0.014215 | 0.00068807 | -0.021518 | -0.0024804 | -0.0020767 | 0.056764 | 0.050944 | 0.045765 | -0.021844 | 0.028878 | -0.012988 | 0.084176 | 0.12399 | 0.22438 | -0.09511 | 0.10178 | 1.5296 | -0.028879 | 122.0465 | 122.3219 | 122.1969 | -0.17331 | 0.023909 | -122.1799 | 0.097175 | 0.10603 | 0.082122 | -122.1401 | -122.0397 | -0.054287 | -0.21764 | 0.2208 | 0.09014 | 0.14443 | 0.057817 | -0.067183 | 0.2032 | 0.24301 | 0.3434 | 0.1479 | -122.3592 | 122.1655 | 122.4409 | 122.3159 | 1.6487 | -122.4374
4391 | 122.374 | -0.064087 | 122.2687 | -0.0025182 | -0.056948 | 0.039011 | 0.017118 | -0.014429 | 0.00090167 | -0.021518 | -0.0024804 | -0.0022903 | 0.056764 | 0.05073 | 0.045551 | -0.012688 | 0.028878 | -0.022144 | 0.088755 | 0.12857 | 0.23354 | -0.09511 | 0.097201 | 1.548 | -0.028879 | 122.0465 | 122.3265 | 122.1832 | -0.17788 | -0.031023 | -122.1799 | 0.051399 | 0.041943 | 0.072966 | -122.1401 | -122.0351 | -0.1138 | -0.22221 | 0.16129 | 0.035208 | 0.14901 | 0.057817 | -0.085497 | 0.15284 | 0.19266 | 0.29763 | 0.092965 | -122.3638 | 122.1106 | 122.3906 | 122.2473 | 1.612 | -122.4466
4392.7656 | 122.3785 | -0.091553 | 122.2641 | 0.0051128 | -0.056948 | 0.038798 | 0.017332 | -0.014429 | 0.0011153 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.05073 | 0.045551 | -0.021844 | 0.033457 | -0.008409 | 0.079598 | 0.12857 | 0.23354 | -0.099689 | 0.10636 | 1.5709 | -0.028879 | 122.051 | 122.3265 | 122.1923 | -0.17788 | -0.008136 | -122.1845 | 0.069709 | 0.083144 | 0.09128 | -122.1355 | -122.0306 | -0.086332 | -0.21306 | 0.19791 | 0.062674 | 0.14901 | 0.062395 | -0.071762 | 0.17115 | 0.22012 | 0.32509 | 0.12501 | -122.3638 | 122.1426 | 122.418 | 122.2839 | 1.6624 | -122.442
4394.4688 | 122.374 | -0.082397 | 122.2687 | -0.01778 | -0.056948 | 0.039011 | 0.017118 | -0.014642 | 0.0011153 | -0.021518 | -0.0024804 | -0.0025041 | 0.057191 | 0.05073 | 0.045551 | -0.017266 | 0.028878 | -0.012988 | 0.079598 | 0.12399 | 0.23812 | -0.09511 | 0.097201 | 1.5846 | -0.0243 | 122.0465 | 122.3128 | 122.1969 | -0.17331 | -0.012713 | -122.1891 | 0.065131 | 0.069409 | 0.082122 | -122.1447 | -122.0306 | -0.090909 | -0.22221 | 0.1796 | 0.058097 | 0.14901 | 0.044081 | -0.071761 | 0.162 | 0.20639 | 0.32051 | 0.11127 | -122.3638 | 122.1289 | 122.3952 | 122.2793 | 1.667 | -122.442
4396.2188 | 122.3785 | -0.068665 | 122.2687 | -0.010149 | -0.056948 | 0.03837 | 0.017332 | -0.014856 | 0.00090167 | -0.021518 | -0.0024804 | -0.0027177 | 0.056551 | 0.050944 | 0.045765 | -0.017266 | 0.028878 | -0.017566 | 0.084176 | 0.12857 | 0.23354 | -0.099689 | 0.088043 | 1.6075 | -0.028879 | 122.051 | 122.3173 | 122.1923 | -0.17788 | -0.031024 | -122.1845 | 0.051399 | 0.051099 | 0.082123 | -122.1401 | -122.0351 | -0.10922 | -0.21764 | 0.15671 | 0.039786 | 0.14901 | 0.04866 | -0.07634 | 0.15284 | 0.19723 | 0.3022 | 0.097543 | -122.3684 | 122.1197 | 122.386 | 122.261 | 1.6762 | -122.4466
4397.9844 | 122.4609 | -0.054932 | 122.2366 | -0.01778 | -0.057162 | 0.038798 | 0.016905 | -0.014642 | 0.0013291 | -0.021518 | -0.0024804 | -0.0022903 | 0.057191 | 0.050944 | 0.045765 | -0.017266 | 0.0243 | -0.012988 | 0.079598 | 0.11941 | 0.23354 | -0.09511 | 0.092622 | 1.6258 | -0.033458 | 122.0465 | 122.3265 | 122.1969 | -0.17331 | -0.040178 | -122.157 | 0.037666 | 0.041944 | 0.082122 | -122.1172 | -122.0031 | -0.11837 | -0.19017 | 0.14755 | 0.021474 | 0.13985 | 0.089861 | -0.039717 | 0.13453 | 0.17434 | 0.28847 | 0.079232 | -122.3317 | 122.1014 | 122.3814 | 122.2518 | 1.6807 | -122.4099
4399.75 | 122.4609 | -0.041199 | 122.2321 | -0.01778 | -0.056948 | 0.038798 | 0.017118 | -0.014429 | 0.0013291 | -0.0062567 | -0.0029076 | -0.0022903 | 0.056978 | 0.050517 | 0.045765 | -0.021844 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.24269 | -0.099689 | 0.10636 | 1.6441 | -0.028879 | 122.0465 | 122.3265 | 122.1878 | -0.17788 | -0.05849 | -122.1525 | 0.019355 | 0.023633 | 0.082123 | -122.1126 | -121.9894 | -0.13669 | -0.18559 | 0.14756 | 0.01232 | 0.14901 | 0.094438 | -0.044297 | 0.1208 | 0.16061 | 0.28389 | 0.065499 | -122.3317 | 122.0877 | 122.3677 | 122.229 | 1.6853 | -122.4099
4401.5156 | 122.4518 | -0.068665 | 122.2321 | -0.01778 | -0.057376 | 0.038584 | 0.016691 | -0.014215 | 0.00090167 | -0.021518 | -0.002694 | -0.0022903 | 0.056764 | 0.050944 | 0.045124 | -0.017266 | 0.0243 | -0.022144 | 0.07502 | 0.12399 | 0.23354 | -0.090531 | 0.10178 | 1.6807 | -0.028879 | 122.0419 | 122.3219 | 122.1878 | -0.17788 | -0.021866 | -122.157 | 0.051399 | 0.046521 | 0.068387 | -122.1081 | -121.9985 | -0.10922 | -0.19017 | 0.17044 | 0.039786 | 0.14901 | 0.08986 | -0.044297 | 0.14369 | 0.19266 | 0.3022 | 0.092965 | -122.3226 | 122.1105 | 122.3906 | 122.2564 | 1.7494 | -122.4099
4403.2031 | 122.3923 | -0.086975 | 122.2641 | -0.0025182 | -0.056735 | 0.038584 | 0.017118 | -0.014429 | 0.0013291 | -0.029148 | -0.002694 | -0.0020767 | 0.056551 | 0.050944 | 0.045551 | -0.026423 | 0.019721 | -0.022144 | 0.084176 | 0.11941 | 0.23812 | -0.10427 | 0.092622 | 1.7174 | -0.028879 | 122.0419 | 122.3173 | 122.1923 | -0.16873 | -0.017293 | -122.1799 | 0.060552 | 0.064831 | 0.082124 | -122.1447 | -122.026 | -0.081753 | -0.22222 | 0.1796 | 0.058096 | 0.13985 | 0.053238 | -0.071762 | 0.17115 | 0.20639 | 0.32509 | 0.1067 | -122.3684 | 122.1289 | 122.4043 | 122.2793 | 1.8044 | -122.4328
4404.9688 | 122.4609 | -0.059509 | 122.2183 | -0.01778 | -0.056948 | 0.038798 | 0.016905 | -0.014429 | 0.0013291 | -0.013887 | -0.002694 | -0.0022903 | 0.056551 | 0.050944 | 0.045551 | -0.017266 | 0.033457 | -0.012988 | 0.084176 | 0.12857 | 0.23812 | -0.09511 | 0.10178 | 1.7357 | -0.0243 | 122.0465 | 122.3219 | 122.1878 | -0.17331 | -0.035601 | -122.1341 | 0.042243 | 0.046521 | 0.082122 | -122.0898 | -121.9802 | -0.1138 | -0.17186 | 0.16129 | 0.035209 | 0.14901 | 0.10359 | -0.030564 | 0.14369 | 0.18808 | 0.29763 | 0.092966 | -122.3134 | 122.106 | 122.3814 | 122.2473 | 1.7952 | -122.3916
4406.6875 | 122.4792 | -0.050354 | 122.2183 | -0.01778 | -0.057162 | 0.038584 | 0.016905 | -0.014429 | 0.0013291 | -0.029148 | -0.0024804 | -0.0020767 | 0.056764 | 0.05073 | 0.045765 | -0.021844 | 0.033457 | -0.017566 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.097201 | 1.8135 | -0.0243 | 122.0373 | 122.3173 | 122.1923 | -0.17331 | -0.049335 | -122.1341 | 0.02851 | 0.032788 | 0.082123 | -122.0898 | -121.9802 | -0.12295 | -0.18102 | 0.14755 | 0.026054 | 0.14901 | 0.099014 | -0.025986 | 0.13453 | 0.17892 | 0.28847 | 0.083811 | -122.318 | 122.0877 | 122.3677 | 122.2427 | 1.8639 | -122.3916
4408.4375 | 122.3511 | -0.086975 | 122.2595 | -0.01778 | -0.057162 | 0.038798 | 0.016905 | -0.014215 | 0.0015427 | -0.029148 | -0.002694 | -0.0022903 | 0.056978 | 0.050944 | 0.045765 | -0.021844 | 0.019721 | -0.012988 | 0.079598 | 0.11941 | 0.23812 | -0.10427 | 0.10636 | 1.8502 | -0.028879 | 122.051 | 122.3173 | 122.1923 | -0.17788 | -0.017293 | -122.1799 | 0.065131 | 0.073987 | 0.09128 | -122.1401 | -122.0214 | -0.09091 | -0.20848 | 0.19333 | 0.058096 | 0.14901 | 0.057816 | -0.067184 | 0.16657 | 0.20639 | 0.32509 | 0.1067 | -122.3638 | 122.138 | 122.4043 | 122.2793 | 1.9371 | -122.4374
4410.1406 | 122.3465 | -0.10529 | 122.2412 | -0.01778 | -0.056948 | 0.03837 | 0.016691 | -0.014001 | 0.0017563 | -0.021518 | -0.0024804 | -0.0022903 | 0.056551 | 0.05073 | 0.045551 | -0.012688 | 0.028878 | -0.017566 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.092622 | 1.8822 | -0.019721 | 122.0373 | 122.3128 | 122.1923 | -0.17788 | 0.005597 | -122.157 | 0.092598 | 0.08772 | 0.082123 | -122.1126 | -122.0031 | -0.072599 | -0.20391 | 0.19791 | 0.085565 | 0.15816 | 0.071547 | -0.048874 | 0.18946 | 0.23385 | 0.3434 | 0.13416 | -122.3409 | 122.1426 | 122.418 | 122.2976 | 1.9875 | -122.4191
4411.9062 | 122.3602 | -0.064087 | 122.2733 | -0.010149 | -0.056735 | 0.038584 | 0.017332 | -0.014429 | 0.0013291 | -0.029148 | -0.0024804 | -0.0022903 | 0.056551 | 0.050944 | 0.045978 | -0.017266 | 0.019721 | -0.017566 | 0.079598 | 0.11941 | 0.24269 | -0.090531 | 0.10178 | 1.928 | -0.033458 | 122.0419 | 122.3173 | 122.1878 | -0.18246 | -0.026444 | -122.1937 | 0.046821 | 0.046521 | 0.072965 | -122.1538 | -122.0306 | -0.11838 | -0.23137 | 0.16587 | 0.030629 | 0.14901 | 0.044083 | -0.085495 | 0.14369 | 0.1835 | 0.30678 | 0.083808 | -122.3638 | 122.106 | 122.3814 | 122.2518 | 1.9921 | -122.4557
4413.6562 | 122.3557 | -0.073242 | 122.2733 | -0.0025182 | -0.057162 | 0.03837 | 0.016905 | -0.014429 | 0.0015427 | -0.021518 | -0.0024804 | -0.0020767 | 0.056764 | 0.05073 | 0.045765 | -0.017266 | 0.028878 | -0.022144 | 0.084176 | 0.11941 | 0.24269 | -0.10427 | 0.097201 | 1.9646 | -0.028879 | 122.0419 | 122.3219 | 122.1969 | -0.16873 | -0.031026 | -122.1891 | 0.055976 | 0.051098 | 0.082124 | -122.1538 | -122.0306 | -0.095486 | -0.23137 | 0.17044 | 0.044363 | 0.13985 | 0.048662 | -0.076338 | 0.15742 | 0.19265 | 0.31594 | 0.10212 | -122.3775 | 122.1151 | 122.3952 | 122.2702 | 2.0379 | -122.442
4415.3594 | 122.3282 | -0.073242 | 122.3236 | -0.01778 | -0.057162 | 0.038584 | 0.017118 | -0.014429 | 0.0017563 | -0.021518 | -0.0024804 | -0.0020767 | 0.056337 | 0.050944 | 0.045551 | -0.021844 | 0.0243 | -0.012988 | 0.084176 | 0.12399 | 0.23812 | -0.099689 | 0.10178 | 2.0104 | -0.0243 | 122.0419 | 122.3219 | 122.1832 | -0.17788 | -0.026447 | -122.2394 | 0.051398 | 0.060254 | 0.086701 | -122.1996 | -122.0855 | -0.10464 | -0.28172 | 0.17502 | 0.048942 | 0.15358 | -0.001692 | -0.14043 | 0.15742 | 0.19723 | 0.31136 | 0.097542 | -122.4233 | 122.1151 | 122.3952 | 122.2564 | 2.0837 | -122.5015
4417.125 | 122.4701 | -0.07782 | 122.2137 | -0.0025182 | -0.056948 | 0.038584 | 0.017118 | -0.014429 | 0.0019701 | -0.021518 | -0.002694 | -0.0022903 | 0.056764 | 0.050944 | 0.045551 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.12399 | 0.23812 | -0.10427 | 0.10178 | 2.0928 | -0.033458 | 122.0465 | 122.3219 | 122.1832 | -0.18246 | -0.026448 | -122.1296 | 0.060554 | 0.060254 | 0.086702 | -122.0898 | -121.9756 | -0.10464 | -0.16728 | 0.1796 | 0.044362 | 0.14901 | 0.10817 | -0.030565 | 0.162 | 0.20181 | 0.31594 | 0.10212 | -122.318 | 122.1243 | 122.3997 | 122.261 | 2.1706 | -122.3962
4418.8906 | 122.3145 | -0.11444 | 122.2778 | -0.01778 | -0.056948 | 0.038798 | 0.017332 | -0.014429 | 0.0017563 | -0.029148 | -0.0022666 | -0.0020767 | 0.056551 | 0.050944 | 0.045337 | -0.026423 | 0.033457 | -0.008409 | 0.084176 | 0.11941 | 0.22896 | -0.10427 | 0.10636 | 2.2668 | -0.028879 | 122.0419 | 122.3265 | 122.1878 | -0.17788 | 0.010173 | -122.1937 | 0.088018 | 0.10603 | 0.095859 | -122.1584 | -122.0489 | -0.063444 | -0.23595 | 0.2208 | 0.085562 | 0.14901 | 0.048662 | -0.090073 | 0.19862 | 0.23385 | 0.3434 | 0.1479 | -122.3821 | 122.1563 | 122.4409 | 122.3022 | 2.3813 | -122.4557
4420.5938 | 122.4655 | -0.027466 | 122.2778 | -0.01778 | -0.057162 | 0.038584 | 0.017118 | -0.014215 | 0.0021837 | -0.021518 | -0.0029076 | -0.0022903 | 0.056978 | 0.050944 | 0.045337 | -0.012688 | 0.028878 | -0.017566 | 0.084176 | 0.13315 | 0.24269 | -0.099689 | 0.097201 | 2.2989 | -0.033458 | 122.0373 | 122.3265 | 122.1923 | -0.17331 | -0.072223 | -122.1937 | 0.014778 | 0.0099 | 0.082123 | -122.1447 | -122.0351 | -0.14584 | -0.24053 | 0.12467 | -0.005992 | 0.13985 | 0.048662 | -0.085495 | 0.11164 | 0.16061 | 0.27016 | 0.056344 | -122.3775 | 122.0648 | 122.354 | 122.2198 | 2.3263 | -122.4511
4422.375 | 122.406 | -0.09613 | 122.2183 | -0.01778 | -0.057162 | 0.038798 | 0.016905 | -0.014429 | 0.0021837 | -0.0062567 | -0.002694 | -0.0020767 | 0.056551 | 0.05073 | 0.045551 | -0.021844 | 0.028878 | -0.022144 | 0.084176 | 0.12857 | 0.23812 | -0.10427 | 0.092622 | 2.3538 | -0.0243 | 122.0419 | 122.3173 | 122.1832 | -0.17331 | -0.008138 | -122.1341 | 0.074286 | 0.073986 | 0.082124 | -122.0898 | -121.9802 | -0.077176 | -0.17644 | 0.18875 | 0.07183 | 0.14901 | 0.099014 | -0.035143 | 0.18031 | 0.2247 | 0.33425 | 0.12501 | -122.3226 | 122.138 | 122.4135 | 122.2793 | 2.4499 | -122.3916
4424.1562 | 122.4243 | -0.059509 | 122.2778 | -0.025411 | -0.056948 | 0.038584 | 0.016905 | -0.014429 | 0.0023973 | -0.013887 | -0.0024804 | -0.0022903 | 0.056551 | 0.050944 | 0.045978 | -0.021844 | 0.0243 | -0.012988 | 0.084176 | 0.11941 | 0.24269 | -0.10427 | 0.097201 | 2.4591 | -0.028879 | 122.0465 | 122.3173 | 122.1878 | -0.17788 | -0.044759 | -122.1937 | 0.037665 | 0.046521 | 0.09128 | -122.1584 | -122.0351 | -0.11838 | -0.23137 | 0.15671 | 0.03063 | 0.14901 | 0.039505 | -0.090073 | 0.14369 | 0.17892 | 0.3022 | 0.083809 | -122.3821 | 122.106 | 122.3768 | 122.2473 | 2.5186 | -122.4557
4425.8438 | 122.4564 | -0.054932 | 122.2321 | -0.01778 | -0.057162 | 0.038584 | 0.017332 | -0.014642 | 0.0026109 | -0.021518 | -0.0029076 | -0.0022903 | 0.056978 | 0.051371 | 0.045551 | -0.017266 | 0.028878 | -0.017566 | 0.079598 | 0.12399 | 0.23812 | -0.099689 | 0.11094 | 2.5141 | -0.0243 | 122.0419 | 122.3219 | 122.1878 | -0.17788 | -0.044757 | -122.1525 | 0.037666 | 0.037366 | 0.082123 | -122.1081 | -121.9939 | -0.12295 | -0.19017 | 0.16587 | 0.030632 | 0.15358 | 0.08986 | -0.044297 | 0.13453 | 0.17892 | 0.29305 | 0.08381 | -122.3317 | 122.0968 | 122.3768 | 122.2427 | 2.569 | -122.4099
4427.6094 | 122.3282 | -0.10071 | 122.2412 | -0.010149 | -0.057162 | 0.03837 | 0.017118 | -0.014429 | 0.0021837 | -0.029148 | -0.0029076 | -0.0020767 | 0.056978 | 0.051158 | 0.045337 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.12399 | 0.23812 | -0.09511 | 0.10636 | 2.6194 | -0.019721 | 122.0419 | 122.3128 | 122.1878 | -0.17788 | 0.005598 | -122.157 | 0.083442 | 0.083142 | 0.077544 | -122.1172 | -122.0031 | -0.077177 | -0.19933 | 0.20707 | 0.080987 | 0.15816 | 0.071547 | -0.053452 | 0.18488 | 0.2247 | 0.33882 | 0.12501 | -122.3363 | 122.1426 | 122.4135 | 122.2885 | 2.7201 | -122.4191
4429.3125 | 122.4838 | -0.064087 | 122.2595 | -0.010149 | -0.057162 | 0.038584 | 0.017118 | -0.014429 | 0.0028247 | -0.021518 | -0.0024804 | -0.0018631 | 0.056764 | 0.05073 | 0.045124 | -0.021844 | 0.0243 | -0.012988 | 0.084176 | 0.12399 | 0.23354 | -0.10427 | 0.10636 | 2.7522 | -0.0243 | 122.0419 | 122.3173 | 122.1832 | -0.17788 | -0.040181 | -122.1753 | 0.042243 | 0.051099 | 0.09128 | -122.1355 | -122.026 | -0.1138 | -0.21764 | 0.17045 | 0.039787 | 0.15358 | 0.057816 | -0.076341 | 0.14826 | 0.18808 | 0.29763 | 0.088387 | -122.3638 | 122.106 | 122.3814 | 122.2473 | 2.8163 | -122.4374
4431.0781 | 122.3694 | -0.091553 | 122.2321 | -0.010149 | -0.057376 | 0.03837 | 0.016691 | -0.014642 | 0.0028247 | -0.029148 | -0.002053 | -0.0022903 | 0.056764 | 0.050944 | 0.045551 | -0.021844 | 0.0243 | -0.022144 | 0.084176 | 0.12399 | 0.23812 | -0.10427 | 0.10636 | 2.9399 | -0.015143 | 122.0373 | 122.3128 | 122.1786 | -0.17788 | -0.012715 | -122.1479 | 0.069709 | 0.069409 | 0.082124 | -122.1081 | -121.9939 | -0.086332 | -0.19475 | 0.19791 | 0.07641 | 0.16274 | 0.080702 | -0.053454 | 0.17573 | 0.21554 | 0.32967 | 0.11585 | -122.3363 | 122.1289 | 122.4043 | 122.2702 | 3.0314 | -122.4099
4432.7812 | 122.3236 | -0.10071 | 122.2549 | -0.01778 | -0.057162 | 0.03837 | 0.016905 | -0.014856 | 0.0026109 | -0.029148 | -0.0029076 | -0.0020767 | 0.057191 | 0.05073 | 0.045551 | -0.017266 | 0.028878 | -0.012988 | 0.079598 | 0.12857 | 0.23812 | -0.09511 | 0.10636 | 3.0131 | -0.019721 | 122.0419 | 122.3082 | 122.1923 | -0.18704 | 0.005598 | -122.1753 | 0.083442 | 0.08772 | 0.082122 | -122.1264 | -122.0168 | -0.086335 | -0.21306 | 0.20707 | 0.080987 | 0.16732 | 0.053236 | -0.062607 | 0.18031 | 0.22928 | 0.33882 | 0.12959 | -122.3501 | 122.1426 | 122.4089 | 122.293 | 3.1139 | -122.442
4434.5312 | 122.4335 | -0.050354 | 122.2321 | -0.010149 | -0.057162 | 0.038798 | 0.017118 | -0.014429 | 0.0030383 | -0.021518 | -0.0024804 | -0.0020767 | 0.056337 | 0.051158 | 0.045337 | -0.021844 | 0.033457 | -0.017566 | 0.079598 | 0.12857 | 0.23812 | -0.099689 | 0.10636 | 3.1917 | -0.0243 | 122.0373 | 122.3219 | 122.1878 | -0.17331 | -0.049335 | -122.1525 | 0.02851 | 0.032788 | 0.082123 | -122.1035 | -121.9939 | -0.12295 | -0.19475 | 0.15671 | 0.026054 | 0.14901 | 0.08986 | -0.044297 | 0.12995 | 0.17892 | 0.28847 | 0.083811 | -122.3317 | 122.0877 | 122.3723 | 122.2381 | 3.2421 | -122.4054
4436.2969 | 122.4335 | -0.073242 | 122.2137 | -0.01778 | -0.057376 | 0.038584 | 0.016905 | -0.014429 | 0.0028247 | -0.021518 | -0.0022666 | -0.0020767 | 0.056551 | 0.050944 | 0.045765 | -0.017266 | 0.028878 | -0.012988 | 0.084176 | 0.12857 | 0.24269 | -0.099689 | 0.12467 | 3.2329 | -0.0243 | 122.0419 | 122.3128 | 122.1878 | -0.18246 | -0.026447 | -122.1296 | 0.055976 | 0.060254 | 0.086701 | -122.0852 | -121.9711 | -0.10922 | -0.17186 | 0.19792 | 0.048942 | 0.15816 | 0.099013 | -0.025986 | 0.15742 | 0.20181 | 0.31594 | 0.10212 | -122.3134 | 122.1151 | 122.386 | 122.261 | 3.3062 | -122.3962
4438.0625 | 122.4243 | -0.091553 | 122.2321 | -0.01778 | -0.057376 | 0.039011 | 0.016691 | -0.014856 | 0.0030383 | -0.021518 | -0.0022666 | -0.0020767 | 0.056551 | 0.051158 | 0.045124 | -0.017266 | 0.015142 | -0.012988 | 0.079598 | 0.12857 | 0.23354 | -0.099689 | 0.10636 | 3.3978 | -0.019721 | 122.0465 | 122.3128 | 122.1878 | -0.17788 | -0.008136 | -122.1525 | 0.074287 | 0.078565 | 0.086701 | -122.1035 | -121.9985 | -0.086332 | -0.18559 | 0.19791 | 0.071832 | 0.15816 | 0.080702 | -0.044297 | 0.17115 | 0.22012 | 0.32509 | 0.10669 | -122.3317 | 122.138 | 122.4043 | 122.2793 | 3.4893 | -122.4099
4439.8125 | 122.4335 | -0.068665 | 122.2183 | -0.010149 | -0.057376 | 0.03837 | 0.016905 | -0.014215 | 0.0032519 | -0.021518 | -0.0024804 | -0.0020767 | 0.056551 | 0.051371 | 0.045337 | -0.017266 | 0.028878 | -0.012988 | 0.079598 | 0.11941 | 0.23354 | -0.099689 | 0.11094 | 3.4802 | -0.028879 | 122.0419 | 122.3128 | 122.1832 | -0.17331 | -0.031024 | -122.1387 | 0.051399 | 0.055677 | 0.086701 | -122.0989 | -121.9848 | -0.10464 | -0.17644 | 0.1796 | 0.039786 | 0.14443 | 0.094435 | -0.035143 | 0.14826 | 0.18808 | 0.3022 | 0.097543 | -122.318 | 122.1105 | 122.3814 | 122.2518 | 3.5488 | -122.3916
4441.5156 | 122.4289 | -0.07782 | 122.2458 | -0.01778 | -0.057376 | 0.038157 | 0.016691 | -0.014215 | 0.0034657 | -0.013887 | -0.002053 | -0.0020767 | 0.056551 | 0.05073 | 0.045124 | -0.017266 | 0.028878 | -0.022144 | 0.079598 | 0.13315 | 0.24269 | -0.099689 | 0.11552 | 3.613 | -0.019721 | 122.0373 | 122.3173 | 122.1786 | -0.17788 | -0.021869 | -122.1662 | 0.060554 | 0.055676 | 0.077545 | -122.1126 | -122.0031 | -0.10006 | -0.20848 | 0.19334 | 0.058099 | 0.15816 | 0.071548 | -0.067187 | 0.15742 | 0.21097 | 0.32051 | 0.1067 | -122.3455 | 122.1151 | 122.3952 | 122.2564 | 3.6908 | -122.4237
4443.2812 | 122.4197 | -0.054932 | 122.2733 | -0.0025182 | -0.057162 | 0.038798 | 0.017118 | -0.014429 | 0.0036793 | -0.021518 | -0.0022666 | -0.0018631 | 0.056551 | 0.051158 | 0.045765 | -0.021844 | 0.028878 | -0.012988 | 0.084176 | 0.12857 | 0.23812 | -0.10427 | 0.11094 | 3.7686 | -0.015143 | 122.0419 | 122.3128 | 122.1878 | -0.17788 | -0.049336 | -122.1891 | 0.033088 | 0.041944 | 0.09128 | -122.1447 | -122.0351 | -0.12295 | -0.23137 | 0.16587 | 0.039789 | 0.16274 | 0.039504 | -0.085495 | 0.13911 | 0.1835 | 0.29305 | 0.08381 | -122.3775 | 122.0968 | 122.3677 | 122.2427 | 3.8236 | -122.4511
4444.9844 | 122.4838 | -0.041199 | 122.2275 | -0.01778 | -0.057376 | 0.038798 | 0.017118 | -0.014429 | 0.0038929 | -0.021518 | -0.002694 | -0.0022903 | 0.056764 | 0.05073 | 0.045551 | -0.017266 | 0.019721 | -0.017566 | 0.079598 | 0.12857 | 0.24269 | -0.090531 | 0.12009 | 3.9655 | -0.015143 | 122.0373 | 122.3219 | 122.1786 | -0.17331 | -0.049332 | -122.1479 | 0.023933 | 0.023633 | 0.072965 | -122.0989 | -121.9848 | -0.13211 | -0.19017 | 0.16129 | 0.026056 | 0.15816 | 0.094438 | -0.048876 | 0.1208 | 0.16977 | 0.28389 | 0.06092 | -122.318 | 122.0785 | 122.3631 | 122.2198 | 4.0067 | -122.4008
4446.75 | 122.4609 | -0.054932 | 122.1954 | -0.01778 | -0.057376 | 0.038798 | 0.017118 | -0.014429 | 0.0041067 | -0.021518 | -0.002694 | -0.0022903 | 0.056764 | 0.05073 | 0.045551 | -0.021844 | 0.028878 | -0.022144 | 0.079598 | 0.13315 | 0.24269 | -0.099689 | 0.12009 | 4.025 | -0.033458 | 122.0373 | 122.3265 | 122.1786 | -0.17788 | -0.044757 | -122.1158 | 0.033088 | 0.032788 | 0.077545 | -122.0623 | -121.9527 | -0.12295 | -0.15813 | 0.17503 | 0.021474 | 0.14443 | 0.13106 | -0.016833 | 0.13453 | 0.18808 | 0.29763 | 0.08381 | -122.2951 | 122.0922 | 122.3814 | 122.2335 | 4.08 | -122.3733
4448.4531 | 122.4014 | -0.07782 | 122.2549 | -0.010149 | -0.057589 | 0.03837 | 0.016691 | -0.014215 | 0.0043203 | -0.013887 | -0.0029076 | -0.0022903 | 0.056978 | 0.05073 | 0.045765 | -0.021844 | 0.015142 | -0.012988 | 0.084176 | 0.13315 | 0.23812 | -0.099689 | 0.12009 | 4.0663 | -0.019721 | 122.0327 | 122.3173 | 122.1832 | -0.18246 | -0.021869 | -122.1708 | 0.055976 | 0.064832 | 0.086701 | -122.1218 | -122.0168 | -0.10464 | -0.22222 | 0.19791 | 0.058099 | 0.16274 | 0.062393 | -0.071764 | 0.162 | 0.21097 | 0.31594 | 0.092962 | -122.3546 | 122.1105 | 122.3952 | 122.261 | 4.1441 | -122.4374
4450.2031 | 122.3602 | -0.082397 | 122.2595 | -0.01778 | -0.057589 | 0.038584 | 0.017118 | -0.014215 | 0.0041067 | -0.021518 | -0.0024804 | -0.0020767 | 0.056764 | 0.051158 | 0.045337 | -0.017266 | 0.019721 | -0.017566 | 0.084176 | 0.12857 | 0.23354 | -0.099689 | 0.11552 | 4.2494 | -0.019721 | 122.0373 | 122.3219 | 122.1878 | -0.18704 | -0.017292 | -122.1753 | 0.065131 | 0.064831 | 0.082123 | -122.131 | -122.026 | -0.10465 | -0.22222 | 0.19791 | 0.062676 | 0.16732 | 0.062395 | -0.071762 | 0.16657 | 0.21097 | 0.31593 | 0.10212 | -122.3592 | 122.1197 | 122.4043 | 122.2702 | 4.3318 | -122.4466
4451.9844 | 122.3648 | -0.07782 | 122.2595 | -0.010149 | -0.057376 | 0.038798 | 0.016905 | -0.014429 | 0.0043203 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.050944 | 0.045551 | -0.017266 | 0.0243 | -0.017566 | 0.079598 | 0.12857 | 0.24269 | -0.099689 | 0.12009 | 4.3868 | -0.019721 | 122.0373 | 122.3173 | 122.1786 | -0.18246 | -0.021869 | -122.1799 | 0.060554 | 0.060254 | 0.082123 | -122.131 | -122.0168 | -0.10464 | -0.22222 | 0.19791 | 0.058099 | 0.16274 | 0.057816 | -0.080919 | 0.15742 | 0.20639 | 0.32051 | 0.10212 | -122.3592 | 122.1151 | 122.3952 | 122.2564 | 4.4646 | -122.442
4453.7031 | 122.3511 | -0.073242 | 122.2504 | 0.0051128 | -0.057376 | 0.038798 | 0.017118 | -0.014429 | 0.0038929 | -0.036779 | -0.0029076 | -0.0020767 | 0.056764 | 0.05073 | 0.045337 | -0.021844 | 0.0243 | -0.012988 | 0.088755 | 0.12399 | 0.23812 | -0.099689 | 0.12467 | 4.46 | -0.019721 | 122.0419 | 122.3082 | 122.1832 | -0.18704 | -0.026447 | -122.1616 | 0.051398 | 0.060254 | 0.086701 | -122.1264 | -122.0122 | -0.1138 | -0.20848 | 0.19792 | 0.053521 | 0.16732 | 0.057814 | -0.067186 | 0.162 | 0.19723 | 0.31136 | 0.097542 | -122.3501 | 122.1151 | 122.3814 | 122.2564 | 4.5333 | -122.4374
4455.4688 | 122.4106 | -0.064087 | 122.2275 | -0.01778 | -0.057162 | 0.038584 | 0.016905 | -0.014429 | 0.0043203 | -0.021518 | -0.0022666 | -0.0020767 | 0.056764 | 0.050944 | 0.045337 | -0.017266 | 0.0243 | -0.022144 | 0.088755 | 0.12399 | 0.24269 | -0.099689 | 0.12009 | 4.5745 | -0.019721 | 122.0419 | 122.3219 | 122.1832 | -0.16873 | -0.035602 | -122.1387 | 0.046821 | 0.041943 | 0.077545 | -122.1035 | -121.9848 | -0.10464 | -0.18559 | 0.18418 | 0.044366 | 0.14901 | 0.094438 | -0.044298 | 0.15284 | 0.18808 | 0.30678 | 0.088387 | -122.3272 | 122.106 | 122.386 | 122.2473 | 4.6386 | -122.3962
4457.1719 | 122.3648 | -0.07782 | 122.2412 | -0.01778 | -0.057376 | 0.038584 | 0.016905 | -0.014642 | 0.0045339 | -0.021518 | -0.0029076 | -0.0020767 | 0.056764 | 0.051158 | 0.045551 | -0.017266 | 0.019721 | -0.012988 | 0.084176 | 0.12399 | 0.23354 | -0.10427 | 0.12467 | 4.7164 | -0.019721 | 122.0419 | 122.3128 | 122.174 | -0.17788 | -0.026448 | -122.157 | 0.060554 | 0.064832 | 0.09128 | -122.1172 | -122.0077 | -0.10006 | -0.19933 | 0.20249 | 0.058099 | 0.15816 | 0.071547 | -0.067188 | 0.162 | 0.20181 | 0.31136 | 0.097541 | -122.3455 | 122.1197 | 122.3906 | 122.2518 | 4.7942 | -122.4191
4458.9375 | 122.3282 | -0.10986 | 122.2595 | -0.010149 | -0.057376 | 0.038584 | 0.016905 | -0.014856 | 0.0047477 | -0.013887 | -0.0024804 | -0.0025041 | 0.057191 | 0.051158 | 0.045765 | -0.017266 | 0.0243 | -0.017566 | 0.084176 | 0.12857 | 0.23812 | -0.10427 | 0.12467 | 4.8904 | -0.015143 | 122.0373 | 122.3128 | 122.1786 | -0.18246 | 0.005595 | -122.1753 | 0.092597 | 0.092297 | 0.086702 | -122.131 | -122.0214 | -0.072601 | -0.22222 | 0.23454 | 0.09472 | 0.16732 | 0.053237 | -0.080919 | 0.19404 | 0.23843 | 0.34798 | 0.13416 | -122.3638 | 122.1472 | 122.4226 | 122.2885 | 5.0003 | -122.442
4460.7031 | 122.3602 | -0.059509 | 122.2687 | -0.010149 | -0.057162 | 0.038798 | 0.016905 | -0.014215 | 0.0047477 | -0.036779 | -0.002694 | -0.0018631 | 0.056978 | 0.051371 | 0.045765 | -0.017266 | 0.0243 | -0.012988 | 0.079598 | 0.12399 | 0.23354 | -0.099689 | 0.13383 | 5.0598 | -0.019721 | 122.0327 | 122.3128 | 122.174 | -0.17331 | -0.04018 | -122.1891 | 0.042243 | 0.046521 | 0.086701 | -122.1447 | -122.0351 | -0.1138 | -0.23595 | 0.19334 | 0.039788 | 0.15358 | 0.044081 | -0.094654 | 0.13911 | 0.1835 | 0.29305 | 0.083809 | -122.3684 | 122.0922 | 122.3723 | 122.2335 | 5.1193 | -122.442
4462.4062 | 122.3511 | -0.091553 | 122.2549 | -0.0025182 | -0.057376 | 0.038584 | 0.017118 | -0.014215 | 0.0045339 | -0.0062567 | -0.002053 | -0.0022903 | 0.056978 | 0.051371 | 0.045337 | -0.021844 | 0.028878 | -0.012988 | 0.084176 | 0.13315 | 0.23354 | -0.099689 | 0.12925 | 5.243 | -0.015143 | 122.0327 | 122.3082 | 122.1832 | -0.17788 | -0.008136 | -122.1708 | 0.069709 | 0.078565 | 0.086701 | -122.1218 | -122.0214 | -0.086332 | -0.22222 | 0.2208 | 0.07641 | 0.16274 | 0.053236 | -0.071764 | 0.17573 | 0.2247 | 0.32509 | 0.12043 | -122.3546 | 122.1243 | 122.3997 | 122.2747 | 5.3345 | -122.4328
4464.1719 | 122.319 | -0.10529 | 122.2641 | -0.01778 | -0.057589 | 0.03837 | 0.016905 | -0.014429 | 0.0053887 | -0.029148 | -0.002053 | -0.0020767 | 0.056764 | 0.051158 | 0.045551 | -0.021844 | 0.0243 | -0.022144 | 0.07502 | 0.12399 | 0.24269 | -0.099689 | 0.12009 | 5.3758 | -0.019721 | 122.0327 | 122.3128 | 122.174 | -0.18246 | 0.005597 | -122.1891 | 0.083442 | 0.083142 | 0.077545 | -122.1401 | -122.0214 | -0.077178 | -0.23137 | 0.22538 | 0.085565 | 0.16274 | 0.048659 | -0.090076 | 0.18031 | 0.22928 | 0.34798 | 0.12959 | -122.3638 | 122.138 | 122.418 | 122.2793 | 5.4811 | -122.4466
4465.8906 | 122.438 | -0.09613 | 122.2137 | -0.01778 | -0.057803 | 0.038584 | 0.016905 | -0.014429 | 0.0049613 | -0.021518 | -0.0024804 | -0.0022903 | 0.056764 | 0.050944 | 0.045551 | -0.021844 | 0.0243 | -0.022144 | 0.084176 | 0.12857 | 0.22896 | -0.099689 | 0.13841 | 5.5498 | -0.015143 | 122.0327 | 122.3082 | 122.1786 | -0.18246 | -0.003559 | -122.1296 | 0.074286 | 0.073986 | 0.077545 | -122.0852 | -121.9848 | -0.086334 | -0.18102 | 0.23454 | 0.080987 | 0.16732 | 0.094435 | -0.035143 | 0.18031 | 0.2247 | 0.32509 | 0.12043 | -122.3134 | 122.1289 | 122.4043 | 122.2747 | 5.6459 | -122.3962
4467.6562 | 122.374 | -0.086975 | 122.2412 | -0.010149 | -0.057589 | 0.038584 | 0.016691 | -0.014429 | 0.0051749 | -0.029148 | -0.0024804 | -0.0025041 | 0.056551 | 0.051158 | 0.045765 | -0.017266 | 0.028878 | -0.017566 | 0.079598 | 0.12857 | 0.23812 | -0.099689 | 0.13841 | 5.7192 | -0.010564 | 122.0373 | 122.3036 | 122.1832 | -0.17331 | -0.012714 | -122.1616 | 0.069709 | 0.069409 | 0.082123 | -122.1126 | -122.0031 | -0.086331 | -0.20391 | 0.22538 | 0.076411 | 0.16274 | 0.06239 | -0.058031 | 0.16657 | 0.21554 | 0.32509 | 0.11585 | -122.3409 | 122.1243 | 122.3906 | 122.2702 | 5.8061 | -122.4145
4469.4219 | 122.3236 | -0.082397 | 122.2549 | -0.01778 | -0.057376 | 0.039011 | 0.016905 | -0.014215 | 0.0053887 | -0.021518 | -0.002694 | -0.0020767 | 0.056764 | 0.051158 | 0.045337 | -0.026423 | 0.033457 | -0.017566 | 0.079598 | 0.11941 | 0.23812 | -0.099689 | 0.13383 | 5.8886 | -0.010564 | 122.0327 | 122.3082 | 122.1832 | -0.18246 | -0.017292 | -122.1753 | 0.055974 | 0.064831 | 0.082123 | -122.1355 | -122.0168 | -0.10007 | -0.22222 | 0.21623 | 0.071833 | 0.1719 | 0.053236 | -0.071764 | 0.162 | 0.20181 | 0.32051 | 0.11585 | -122.3546 | 122.1151 | 122.3906 | 122.2656 | 5.971 | -122.4374
4471.1875 | 122.3557 | -0.091553 | 122.2687 | -0.010149 | -0.057376 | 0.038798 | 0.017118 | -0.014429 | 0.0058159 | -0.013887 | -0.002694 | -0.0020767 | 0.056764 | 0.051371 | 0.045551 | -0.017266 | 0.0243 | -0.026723 | 0.093333 | 0.12399 | 0.23354 | -0.099689 | 0.13841 | 6.0671 | -0.015143 | 122.0373 | 122.3036 | 122.1832 | -0.18246 | -0.008136 | -122.1753 | 0.074287 | 0.06483 | 0.072966 | -122.1447 | -122.0351 | -0.090911 | -0.23137 | 0.22996 | 0.07641 | 0.16732 | 0.034924 | -0.085497 | 0.18489 | 0.21554 | 0.32509 | 0.11585 | -122.3684 | 122.1289 | 122.3952 | 122.2747 | 6.1587 | -122.4511
4472.8906 | 122.3557 | -0.086975 | 122.2458 | -0.010149 | -0.057589 | 0.038584 | 0.016905 | -0.014642 | 0.0058159 | -0.021518 | -0.0024804 | -0.0022903 | 0.056978 | 0.051585 | 0.045551 | -0.021844 | 0.0243 | -0.026723 | 0.084176 | 0.11941 | 0.23812 | -0.10427 | 0.13841 | 6.1908 | -0.005985 | 122.0327 | 122.3082 | 122.1786 | -0.18246 | -0.017293 | -122.1616 | 0.065131 | 0.060252 | 0.077545 | -122.1264 | -122.0077 | -0.095489 | -0.21306 | 0.22538 | 0.08099 | 0.17648 | 0.062391 | -0.067187 | 0.17115 | 0.20639 | 0.32509 | 0.11127 | -122.3501 | 122.1197 | 122.3952 | 122.2656 | 6.2778 | -122.4283
4474.6562 | 122.3419 | -0.082397 | 122.2366 | -0.010149 | -0.057376 | 0.038584 | 0.016477 | -0.014429 | 0.0058159 | -0.029148 | -0.0029076 | -0.0020767 | 0.056978 | 0.051371 | 0.045765 | -0.021844 | 0.028878 | -0.017566 | 0.084176 | 0.12399 | 0.23812 | -0.10427 | 0.14299 | 6.3465 | -0.010564 | 122.0327 | 122.3082 | 122.1878 | -0.17331 | -0.021871 | -122.1525 | 0.060553 | 0.064831 | 0.086702 | -122.1126 | -121.9985 | -0.090909 | -0.20391 | 0.22539 | 0.071833 | 0.16274 | 0.071547 | -0.048874 | 0.16657 | 0.20639 | 0.32051 | 0.11127 | -122.3409 | 122.1151 | 122.3906 | 122.2702 | 6.4288 | -122.4099
4476.4219 | 122.4701 | -0.064087 | 122.2321 | -0.025411 | -0.057376 | 0.038798 | 0.016905 | -0.014429 | 0.0058159 | -0.021518 | -0.0024804 | -0.0022903 | 0.056337 | 0.051371 | 0.045551 | -0.03558 | 0.0243 | -0.012988 | 0.079598 | 0.12857 | 0.23354 | -0.099689 | 0.13383 | 6.3693 | -0.010564 | 122.0373 | 122.3173 | 122.1878 | -0.18246 | -0.035602 | -122.1525 | 0.028507 | 0.051099 | 0.086701 | -122.1035 | -121.9985 | -0.11838 | -0.19475 | 0.19792 | 0.053523 | 0.1719 | 0.085281 | -0.044297 | 0.14369 | 0.19266 | 0.29763 | 0.088387 | -122.3317 | 122.1014 | 122.3814 | 122.2518 | 6.4334 | -122.4145
4478.125 | 122.4197 | -0.073242 | 122.2412 | -0.01778 | -0.057589 | 0.038798 | 0.016905 | -0.014642 | 0.0060297 | -0.021518 | -0.0024804 | -0.0020767 | 0.056764 | 0.051158 | 0.045765 | -0.021844 | 0.0243 | -0.022144 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.13841 | 6.4975 | -0.005985 | 122.0327 | 122.3173 | 122.174 | -0.18246 | -0.026447 | -122.157 | 0.051398 | 0.051098 | 0.077545 | -122.1126 | -122.0031 | -0.10922 | -0.20848 | 0.21165 | 0.067257 | 0.17648 | 0.076126 | -0.067188 | 0.15742 | 0.20181 | 0.31136 | 0.097542 | -122.3409 | 122.106 | 122.3906 | 122.2473 | 6.5708 | -122.4237
4479.8906 | 122.4014 | -0.068665 | 122.2366 | -0.01778 | -0.057589 | 0.038584 | 0.016691 | -0.014215 | 0.0062433 | -0.029148 | -0.0024804 | -0.0018631 | 0.056978 | 0.051371 | 0.045765 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.12857 | 0.24269 | -0.10427 | 0.14299 | 6.612 | -0.005985 | 122.0327 | 122.3128 | 122.174 | -0.17331 | -0.035603 | -122.157 | 0.046821 | 0.055677 | 0.09128 | -122.1081 | -121.9939 | -0.10464 | -0.20391 | 0.21165 | 0.06268 | 0.16732 | 0.076125 | -0.06261 | 0.14826 | 0.19723 | 0.31136 | 0.092965 | -122.3409 | 122.1014 | 122.3814 | 122.2427 | 6.6807 | -122.4099
4481.5938 | 122.3969 | -0.050354 | 122.2321 | -0.01778 | -0.057376 | 0.039011 | 0.016477 | -0.014642 | 0.0062433 | -0.013887 | -0.002053 | -0.0020767 | 0.056978 | 0.050944 | 0.045551 | -0.021844 | 0.019721 | -0.017566 | 0.084176 | 0.12399 | 0.23812 | -0.09511 | 0.14299 | 6.699 | -0.001407 | 122.0373 | 122.3128 | 122.174 | -0.17788 | -0.044756 | -122.1479 | 0.02851 | 0.032788 | 0.077544 | -122.1081 | -121.9939 | -0.12753 | -0.19475 | 0.19334 | 0.048947 | 0.17648 | 0.080702 | -0.058033 | 0.13453 | 0.17434 | 0.28847 | 0.070075 | -122.3272 | 122.0877 | 122.3631 | 122.2244 | 6.7494 | -122.4099
4483.375 | 122.4014 | -0.059509 | 122.2229 | -0.010149 | -0.057589 | 0.038798 | 0.016905 | -0.014642 | 0.0066705 | -0.021518 | -0.0024804 | -0.0020767 | 0.056978 | 0.051158 | 0.045765 | -0.017266 | 0.028878 | -0.008409 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.13841 | 6.6212 | -0.005985 | 122.0236 | 122.3128 | 122.174 | -0.18246 | -0.04018 | -122.1387 | 0.042243 | 0.0511 | 0.09128 | -122.0943 | -121.9848 | -0.12295 | -0.19933 | 0.19792 | 0.053524 | 0.17648 | 0.089858 | -0.048877 | 0.14369 | 0.18808 | 0.29763 | 0.088387 | -122.3226 | 122.0831 | 122.3723 | 122.2335 | 6.6807 | -122.4054
4485.0625 | 122.406 | -0.064087 | 122.2046 | -0.025411 | -0.057376 | 0.03837 | 0.017332 | -0.014429 | 0.0068843 | -0.029148 | -0.0029076 | -0.0018631 | 0.057191 | 0.051158 | 0.045124 | -0.021844 | 0.0243 | -0.017566 | 0.079598 | 0.11941 | 0.23812 | -0.10427 | 0.13841 | 6.6624 | -0.001407 | 122.0281 | 122.3082 | 122.1694 | -0.18704 | -0.040181 | -122.125 | 0.042243 | 0.046521 | 0.086702 | -122.0852 | -121.9665 | -0.12296 | -0.17644 | 0.2025 | 0.06268 | 0.18564 | 0.10359 | -0.035146 | 0.14369 | 0.1835 | 0.3022 | 0.088387 | -122.3089 | 122.0922 | 122.3723 | 122.2335 | 6.7265 | -122.3916
4486.8281 | 122.3648 | -0.091553 | 122.2412 | -0.0025182 | -0.057376 | 0.038798 | 0.016905 | -0.014429 | 0.0070979 | -0.021518 | -0.002694 | -0.0020767 | 0.056978 | 0.051158 | 0.045978 | -0.021844 | 0.015142 | -0.017566 | 0.079598 | 0.12399 | 0.24269 | -0.099689 | 0.14757 | 6.786 | -0.010564 | 122.0236 | 122.3082 | 122.174 | -0.18246 | -0.008136 | -122.1616 | 0.069709 | 0.073987 | 0.082123 | -122.1172 | -121.9985 | -0.090911 | -0.21764 | 0.23912 | 0.080989 | 0.1719 | 0.066969 | -0.067188 | 0.17115 | 0.21554 | 0.33425 | 0.10669 | -122.3409 | 122.1151 | 122.3997 | 122.2656 | 6.8776 | -122.4237
4488.6094 | 122.3923 | -0.07782 | 122.2412 | -0.01778 | -0.057803 | 0.03837 | 0.016477 | -0.014642 | 0.0070979 | 0.0013733 | -0.002694 | -0.0020767 | 0.056551 | 0.050944 | 0.045551 | -0.021844 | 0.028878 | -0.008409 | 0.079598 | 0.12857 | 0.23812 | -0.099689 | 0.14299 | 6.9646 | -0.001407 | 122.0373 | 122.3036 | 122.1694 | -0.18704 | -0.021869 | -122.1616 | 0.055976 | 0.069411 | 0.09128 | -122.1126 | -122.0031 | -0.10922 | -0.20391 | 0.22081 | 0.076413 | 0.18564 | 0.06239 | -0.071767 | 0.15742 | 0.20639 | 0.31594 | 0.1067 | -122.3409 | 122.1151 | 122.3814 | 122.2473 | 7.0424 | -122.4283
4490.3125 | 122.4609 | -0.054932 | 122.2 | -0.010149 | -0.057803 | 0.039011 | 0.016905 | -0.014215 | 0.0068843 | -0.021518 | -0.002694 | -0.0018631 | 0.056764 | 0.051371 | 0.045765 | -0.021844 | 0.0243 | -0.012988 | 0.079598 | 0.12857 | 0.24727 | -0.099689 | 0.14757 | 7.0882 | 0.003172 | 122.0236 | 122.3082 | 122.1786 | -0.17331 | -0.044757 | -122.1204 | 0.033088 | 0.041944 | 0.086701 | -122.0714 | -121.9527 | -0.11837 | -0.17644 | 0.2025 | 0.058104 | 0.17648 | 0.10817 | -0.02141 | 0.13453 | 0.1835 | 0.30221 | 0.079232 | -122.2997 | 122.0785 | 122.3631 | 122.2335 | 7.1431 | -122.3733
4492.0938 | 122.4014 | -0.073242 | 122.2275 | -0.01778 | -0.057803 | 0.038798 | 0.016905 | -0.014429 | 0.0077389 | -0.021518 | -0.002694 | -0.0020767 | 0.056551 | 0.051158 | 0.045551 | -0.021844 | 0.0243 | -0.008409 | 0.079598 | 0.12399 | 0.23354 | -0.10885 | 0.15672 | 7.2118 | -0.001407 | 122.0327 | 122.3082 | 122.1649 | -0.17331 | -0.035605 | -122.1479 | 0.051398 | 0.064833 | 0.10044 | -122.1035 | -121.9939 | -0.10006 | -0.19475 | 0.22997 | 0.071835 | 0.1719 | 0.080702 | -0.062612 | 0.15284 | 0.19723 | 0.30678 | 0.097542 | -122.3363 | 122.106 | 122.3814 | 122.2381 | 7.2851 | -122.4008
4493.875 | 122.4335 | -0.036621 | 122.2137 | -0.010149 | -0.057376 | 0.038584 | 0.016691 | -0.014642 | 0.0081663 | -0.021518 | -0.0024804 | -0.0018631 | 0.056764 | 0.051371 | 0.045765 | -0.017266 | 0.019721 | -0.017566 | 0.088755 | 0.12857 | 0.23812 | -0.099689 | 0.15215 | 7.3721 | 0.003172 | 122.0327 | 122.3036 | 122.174 | -0.18704 | -0.063068 | -122.125 | 0.019355 | 0.019055 | 0.082123 | -122.0852 | -121.9756 | -0.15042 | -0.18102 | 0.18877 | 0.039793 | 0.19021 | 0.089856 | -0.039722 | 0.12538 | 0.16519 | 0.27474 | 0.056342 | -122.3134 | 122.0693 | 122.3402 | 122.2106 | 7.4087 | -122.4008
4495.5781 | 122.4472 | -0.059509 | 122.2046 | -0.0025182 | -0.057589 | 0.03837 | 0.017118 | -0.014429 | 0.0079525 | -0.021518 | -0.0029076 | -0.0018631 | 0.056551 | 0.051371 | 0.045978 | -0.021844 | 0.019721 | -0.012988 | 0.084176 | 0.11941 | 0.24269 | -0.099689 | 0.14757 | 7.4957 | 0.003172 | 122.0419 | 122.3082 | 122.174 | -0.18704 | -0.04018 | -122.1204 | 0.037665 | 0.046521 | 0.086701 | -122.0852 | -121.9619 | -0.12753 | -0.16271 | 0.20708 | 0.062681 | 0.19021 | 0.10359 | -0.030567 | 0.14369 | 0.17892 | 0.3022 | 0.07923 | -122.3043 | 122.1014 | 122.3677 | 122.2335 | 7.5552 | -122.3916
4497.3438 | 122.319 | -0.10529 | 122.2687 | -0.0025182 | -0.058017 | 0.038798 | 0.016691 | -0.014429 | 0.0079525 | -0.029148 | -0.0022666 | -0.0020767 | 0.056978 | 0.051371 | 0.045337 | -0.017266 | 0.0243 | -0.008409 | 0.088755 | 0.12399 | 0.24269 | -0.090531 | 0.15215 | 7.6605 | 0.003172 | 122.0281 | 122.3082 | 122.1649 | -0.17788 | 0.014755 | -122.1799 | 0.08802 | 0.096877 | 0.082122 | -122.1447 | -122.026 | -0.072599 | -0.24053 | 0.25743 | 0.10846 | 0.18106 | 0.039503 | -0.10381 | 0.19404 | 0.22928 | 0.34798 | 0.12959 | -122.3592 | 122.1334 | 122.4135 | 122.2702 | 7.7658 | -122.4466
4499.125 | 122.3419 | -0.09613 | 122.2504 | -0.010149 | -0.058017 | 0.038798 | 0.016905 | -0.014856 | 0.0088073 | -0.013887 | -0.0024804 | -0.0018631 | 0.056764 | 0.051371 | 0.045551 | -0.021844 | 0.033457 | 0.000747 | 0.07502 | 0.12857 | 0.24269 | -0.10427 | 0.15672 | 7.7155 | 0.007751 | 122.0327 | 122.3082 | 122.1786 | -0.18246 | -0.008138 | -122.1753 | 0.074286 | 0.096877 | 0.10501 | -122.1218 | -122.0077 | -0.086334 | -0.21764 | 0.25285 | 0.10388 | 0.19021 | 0.057814 | -0.071764 | 0.17115 | 0.2247 | 0.33882 | 0.12959 | -122.3546 | 122.1289 | 122.4043 | 122.2747 | 7.8116 | -122.4328
4500.8281 | 122.4518 | -0.054932 | 122.2229 | -0.0025182 | -0.057589 | 0.038584 | 0.017118 | -0.014642 | 0.0090209 | -0.021518 | -0.002694 | -0.0020767 | 0.056978 | 0.051158 | 0.045551 | -0.017266 | 0.015142 | -0.008409 | 0.084176 | 0.11941 | 0.23812 | -0.099689 | 0.15672 | 7.775 | 0.003172 | 122.0281 | 122.3128 | 122.1694 | -0.17788 | -0.044757 | -122.1387 | 0.037666 | 0.046523 | 0.09128 | -122.1035 | -121.9848 | -0.12295 | -0.19475 | 0.21166 | 0.058104 | 0.18106 | 0.089858 | -0.053456 | 0.13911 | 0.17434 | 0.29305 | 0.070074 | -122.3226 | 122.0831 | 122.3677 | 122.2244 | 7.8299 | -122.4008
4502.5938 | 122.3511 | -0.11444 | 122.2641 | -0.01778 | -0.057589 | 0.039011 | 0.017118 | -0.014429 | 0.0090209 | -0.013887 | -0.0024804 | -0.0020767 | 0.056764 | 0.051158 | 0.045765 | -0.026423 | 0.0243 | -0.008409 | 0.084176 | 0.12857 | 0.23812 | -0.10427 | 0.16588 | 7.9124 | 0.007751 | 122.0236 | 122.3082 | 122.1694 | -0.18246 | 0.010173 | -122.1799 | 0.088018 | 0.10603 | 0.095859 | -122.1355 | -122.026 | -0.068023 | -0.24053 | 0.28032 | 0.12219 | 0.19021 | 0.044081 | -0.094655 | 0.19862 | 0.24301 | 0.35256 | 0.13874 | -122.3684 | 122.138 | 122.4226 | 122.2839 | 8.0268 | -122.4466
4504.3438 | 122.319 | -0.10071 | 122.2321 | -0.010149 | -0.057803 | 0.038584 | 0.016691 | -0.014429 | 0.0096619 | -0.021518 | -0.0024804 | -0.0022903 | 0.056551 | 0.051371 | 0.045765 | -0.021844 | 0.0243 | -0.008409 | 0.079598 | 0.12857 | 0.23812 | -0.10427 | 0.17046 | 8.0223 | 0.007751 | 122.0281 | 122.299 | 122.174 | -0.17788 | -0.00356 | -122.1525 | 0.078864 | 0.092299 | 0.095859 | -122.1035 | -121.9939 | -0.077177 | -0.20391 | 0.27117 | 0.10846 | 0.18564 | 0.066967 | -0.058033 | 0.18031 | 0.22928 | 0.33882 | 0.12501 | -122.3363 | 122.1289 | 122.3997 | 122.2747 | 8.123 | -122.4099
4506.1094 | 122.3236 | -0.10071 | 122.2366 | 0.0051128 | -0.057376 | 0.038798 | 0.016691 | -0.014215 | 0.0096619 | -0.029148 | -0.002694 | -0.0020767 | 0.056551 | 0.051371 | 0.045337 | -0.021844 | 0.028878 | -0.008409 | 0.088755 | 0.11941 | 0.24269 | -0.099689 | 0.1613 | 8.2008 | 0.007751 | 122.0236 | 122.299 | 122.174 | -0.18704 | 0.001019 | -122.1479 | 0.078864 | 0.092299 | 0.09128 | -122.1172 | -121.9939 | -0.086335 | -0.21306 | 0.26201 | 0.10846 | 0.19479 | 0.06239 | -0.06261 | 0.18946 | 0.22012 | 0.3434 | 0.12959 | -122.3363 | 122.1243 | 122.3997 | 122.2747 | 8.3015 | -122.4237
4507.875 | 122.3328 | -0.10529 | 122.2321 | -0.0025182 | -0.057803 | 0.03837 | 0.016477 | -0.014215 | 0.010516 | -0.036779 | -0.0029076 | -0.0020767 | 0.056551 | 0.050944 | 0.045551 | -0.021844 | 0.0243 | -0.008409 | 0.097912 | 0.13315 | 0.23354 | -0.10427 | 0.1613 | 8.297 | 0.007751 | 122.0236 | 122.3036 | 122.1694 | -0.18246 | 0.001018 | -122.1341 | 0.083442 | 0.096877 | 0.095859 | -122.0989 | -121.9985 | -0.077178 | -0.20849 | 0.26659 | 0.11304 | 0.19021 | 0.071545 | -0.062612 | 0.2032 | 0.23843 | 0.33882 | 0.12959 | -122.3363 | 122.1289 | 122.4089 | 122.2747 | 8.4023 | -122.4145
4509.6406 | 122.3557 | -0.09613 | 122.2321 | -0.010149 | -0.057803 | 0.03837 | 0.017118 | -0.014856 | 0.01073 | -0.013887 | -0.0024804 | -0.0018631 | 0.056764 | 0.051371 | 0.045551 | -0.017266 | 0.015142 | -0.003831 | 0.084176 | 0.12399 | 0.23812 | -0.10427 | 0.15672 | 8.4023 | 0.007751 | 122.0236 | 122.3036 | 122.1694 | -0.19162 | -0.008138 | -122.1479 | 0.078864 | 0.092299 | 0.10044 | -122.1081 | -121.9939 | -0.095492 | -0.20849 | 0.25285 | 0.10388 | 0.19937 | 0.071545 | -0.062612 | 0.18031 | 0.22012 | 0.33425 | 0.11127 | -122.3363 | 122.1197 | 122.3997 | 122.2656 | 8.4984 | -122.4237
4511.4062 | 122.4426 | -0.064087 | 122.2183 | -0.010149 | -0.057803 | 0.038798 | 0.016905 | -0.014215 | 0.011798 | -0.021518 | -0.0029076 | -0.0020767 | 0.056978 | 0.051371 | 0.045337 | -0.017266 | 0.0243 | -0.003831 | 0.088755 | 0.11941 | 0.24269 | -0.099689 | 0.17046 | 8.4664 | -0.001407 | 122.0281 | 122.299 | 122.1649 | -0.18704 | -0.035602 | -122.1296 | 0.046821 | 0.060256 | 0.095858 | -122.0989 | -121.9756 | -0.12296 | -0.19017 | 0.23455 | 0.06268 | 0.18564 | 0.0807 | -0.053457 | 0.15284 | 0.1835 | 0.30678 | 0.088387 | -122.318 | 122.0922 | 122.3631 | 122.229 | 8.5305 | -122.4054
4513.1719 | 122.3007 | -0.10986 | 122.2275 | -0.01778 | -0.057803 | 0.03837 | 0.016691 | -0.014642 | 0.016499 | -0.013887 | -0.0022666 | -0.0020767 | 0.056978 | 0.051371 | 0.045551 | -0.017266 | 0.010564 | -0.008409 | 0.079598 | 0.12399 | 0.23812 | -0.10885 | 0.17046 | 8.5992 | 0.01233 | 122.0236 | 122.299 | 122.1603 | -0.18246 | 0.001016 | -122.1479 | 0.092597 | 0.10145 | 0.10044 | -122.1035 | -121.9894 | -0.072601 | -0.20391 | 0.28032 | 0.12219 | 0.19479 | 0.071545 | -0.067191 | 0.18946 | 0.23385 | 0.34798 | 0.12043 | -122.3363 | 122.1334 | 122.4089 | 122.2702 | 8.709 | -122.4099
4514.875 | 122.1222 | -0.39825 | 121.7514 | -0.01778 | -0.057162 | 0.037729 | 0.015836 | -0.014856 | 0.57224 | -0.013887 | -0.0024804 | -0.0022903 | 0.056337 | 0.051371 | 0.045337 | -0.095099 | -0.053537 | -0.081662 | 0.010922 | 0.055306 | 0.16486 | -0.292 | -0.081369 | 8.6953 | -0.2395 | 121.5978 | 121.8824 | 121.7391 | -0.43888 | 0.10625 | -121.7405 | 0.30316 | 0.31659 | 0.21034 | -121.6961 | -121.5865 | -0.040624 | -0.15363 | 0.31688 | 0.15876 | 0.19938 | 0.13097 | -0.012348 | 0.40918 | 0.45356 | 0.56311 | 0.34472 | -122.0434 | 121.996 | 122.2806 | 122.1373 | 9.0936 | -122.1903
4516.6406 | 122.1542 | -0.07782 | 122.0444 | 0.0051128 | -0.058658 | 0.038584 | 0.015195 | -0.014429 | -0.015123 | -0.021518 | -0.0022666 | -0.0022903 | 0.056764 | 0.051371 | 0.045551 | -0.021844 | 0.028878 | 0.000747 | 0.088755 | 0.12857 | 0.23812 | -0.10427 | 0.17504 | 8.8693 | 0.016908 | 121.813 | 122.093 | 121.9543 | -0.17788 | -0.026448 | -121.9556 | 0.055976 | 0.078567 | 0.10501 | -121.9158 | -121.8063 | -0.10006 | -0.23141 | 0.25286 | 0.094728 | 0.19479 | 0.048612 | -0.090123 | 0.16658 | 0.20639 | 0.31594 | 0.1067 | -122.1486 | 121.8908 | 122.1708 | 122.0321 | 8.9471 | -122.2223
4518.4062 | 122.2916 | -0.054932 | 122.0398 | -0.010149 | -0.058658 | 0.038584 | 0.015622 | -0.014856 | -0.016832 | -0.021518 | -0.0024804 | -0.0020767 | 0.056337 | 0.051371 | 0.045337 | -0.026423 | 0.0243 | -0.003831 | 0.084176 | 0.12399 | 0.23812 | -0.09511 | 0.1842 | 9.0342 | 0.021487 | 121.8816 | 122.1571 | 122.0229 | -0.17331 | -0.040178 | -121.9556 | 0.028509 | 0.051101 | 0.091279 | -121.9158 | -121.8017 | -0.11837 | -0.15816 | 0.23913 | 0.076419 | 0.19479 | 0.11729 | -0.016866 | 0.13911 | 0.17892 | 0.29305 | 0.079232 | -122.1349 | 121.9366 | 122.212 | 122.0779 | 9.0891 | -122.2131
4520.0938 | 122.2046 | -0.086975 | 122.1085 | -0.01778 | -0.058444 | 0.038798 | 0.015409 | -0.014429 | -0.016191 | -0.021518 | -0.0024804 | -0.0018631 | 0.056337 | 0.051585 | 0.045551 | -0.017266 | 0.0243 | 0.000747 | 0.088755 | 0.13315 | 0.23354 | -0.09511 | 0.17962 | 9.1853 | 0.021487 | 121.9045 | 122.1754 | 122.0412 | -0.18246 | -0.008135 | -122.0197 | 0.069709 | 0.087722 | 0.095857 | -121.9753 | -121.8749 | -0.095489 | -0.20393 | 0.26659 | 0.10846 | 0.20395 | 0.066941 | -0.067215 | 0.17573 | 0.22012 | 0.32051 | 0.11127 | -122.2036 | 121.9915 | 122.2624 | 122.1282 | 9.2722 | -122.2909
4521.8594 | 122.3282 | -0.050354 | 122.0901 | -0.0025182 | -0.058871 | 0.038584 | 0.015195 | -0.014429 | -0.016405 | -0.029148 | -0.0024804 | -0.0022903 | 0.056764 | 0.051158 | 0.045337 | -0.012688 | 0.019721 | -0.008409 | 0.079598 | 0.12399 | 0.24727 | -0.09511 | 0.18877 | 9.3501 | 0.026066 | 121.9183 | 122.1983 | 122.055 | -0.18704 | -0.044756 | -122.0106 | 0.037666 | 0.041945 | 0.086701 | -121.9662 | -121.8429 | -0.13669 | -0.17188 | 0.23913 | 0.07642 | 0.21311 | 0.10814 | -0.03517 | 0.12995 | 0.17434 | 0.29763 | 0.070075 | -122.1853 | 121.9686 | 122.2486 | 122.1053 | 9.4004 | -122.2772
4523.625 | 122.3602 | -0.036621 | 122.1039 | -0.01778 | -0.058871 | 0.038798 | 0.015195 | -0.014642 | -0.016191 | -0.021518 | -0.0024804 | -0.0018631 | 0.056764 | 0.050944 | 0.045337 | -0.021844 | 0.0243 | 0.000747 | 0.088755 | 0.12399 | 0.24269 | -0.09511 | 0.18877 | 9.5195 | 0.016908 | 121.932 | 122.2074 | 122.0596 | -0.17788 | -0.058489 | -122.0151 | 0.014777 | 0.037368 | 0.095857 | -121.9799 | -121.8612 | -0.14126 | -0.17188 | 0.2254 | 0.053529 | 0.19479 | 0.10357 | -0.044324 | 0.12538 | 0.16061 | 0.27932 | 0.060921 | -122.199 | 121.9686 | 122.2441 | 122.0962 | 9.5561 | -122.2818
4525.3125 | 122.2092 | -0.10529 | 122.1634 | -0.01778 | -0.058658 | 0.03837 | 0.015409 | -0.014429 | -0.016191 | -0.021518 | -0.0029076 | -0.0020767 | 0.056551 | 0.051585 | 0.045551 | -0.021844 | 0.028878 | -0.003831 | 0.088755 | 0.12399 | 0.24269 | -0.09511 | 0.19793 | 9.6752 | 0.030644 | 121.9366 | 122.212 | 122.087 | -0.17331 | 0.010176 | -122.0746 | 0.083442 | 0.10146 | 0.091279 | -122.0394 | -121.9207 | -0.06802 | -0.22681 | 0.30322 | 0.13593 | 0.20395 | 0.048638 | -0.076361 | 0.19404 | 0.22928 | 0.34798 | 0.13416 | -122.2585 | 122.0419 | 122.3173 | 122.1923 | 9.7805 | -122.3367
4527.0781 | 122.2504 | -0.082397 | 122.1497 | -0.010149 | -0.058658 | 0.038584 | 0.015836 | -0.014642 | -0.015123 | -0.013887 | -0.0024804 | -0.0022903 | 0.056551 | 0.051585 | 0.045337 | -0.017266 | 0.033457 | -0.003831 | 0.079598 | 0.12857 | 0.23812 | -0.099689 | 0.20251 | 9.8354 | 0.035223 | 121.9457 | 122.2303 | 122.087 | -0.17788 | -0.017292 | -122.0701 | 0.065131 | 0.078566 | 0.095858 | -122.0211 | -121.9115 | -0.095488 | -0.20392 | 0.28491 | 0.11762 | 0.21311 | 0.080686 | -0.062628 | 0.162 | 0.21097 | 0.32051 | 0.11585 | -122.2493 | 122.0281 | 122.3127 | 122.1694 | 9.9178 | -122.3275
4528.8438 | 122.2504 | -0.068665 | 122.1817 | -0.01778 | -0.058658 | 0.038584 | 0.014981 | -0.014642 | -0.014696 | -0.0062567 | -0.0024804 | -0.0020767 | 0.056978 | 0.051371 | 0.045337 | -0.026423 | 0.028878 | -0.003831 | 0.088755 | 0.12857 | 0.24269 | -0.099689 | 0.20251 | 10.0323 | 0.030644 | 121.9549 | 122.2303 | 122.0962 | -0.17788 | -0.031024 | -122.0929 | 0.042242 | 0.064834 | 0.095858 | -122.0531 | -121.939 | -0.10922 | -0.22681 | 0.27118 | 0.099309 | 0.20853 | 0.048642 | -0.085515 | 0.15742 | 0.19723 | 0.31136 | 0.097543 | -122.2814 | 122.0236 | 122.299 | 122.1649 | 10.101 | -122.3596
4530.5938 | 122.2687 | -0.082397 | 122.1771 | -0.025411 | -0.058444 | 0.03837 | 0.015195 | -0.014429 | -0.014696 | -0.021518 | -0.0024804 | -0.0018631 | 0.056764 | 0.051585 | 0.045337 | -0.012688 | 0.0243 | -0.003831 | 0.088755 | 0.13315 | 0.23354 | -0.099689 | 0.21167 | 10.1971 | 0.039802 | 121.9595 | 122.2395 | 122.1008 | -0.18246 | -0.017292 | -122.0884 | 0.069709 | 0.078566 | 0.095858 | -122.044 | -121.9436 | -0.10007 | -0.21765 | 0.29407 | 0.1222 | 0.22227 | 0.062377 | -0.076359 | 0.17115 | 0.21554 | 0.31593 | 0.1067 | -122.2768 | 122.0419 | 122.3219 | 122.1832 | 10.2795 | -122.3596
4532.2969 | 122.3557 | -0.07782 | 122.1497 | -0.01778 | -0.058871 | 0.03837 | 0.015195 | -0.014429 | -0.014696 | -0.029148 | -0.0024804 | -0.0020767 | 0.056551 | 0.051371 | 0.045337 | -0.017266 | 0.0243 | 0.005325 | 0.088755 | 0.13315 | 0.23354 | -0.099689 | 0.20251 | 10.4078 | 0.030644 | 121.9549 | 122.2395 | 122.0962 | -0.17788 | -0.021869 | -122.0609 | 0.060554 | 0.083145 | 0.10501 | -122.0165 | -121.9161 | -0.10006 | -0.19477 | 0.28033 | 0.10846 | 0.20853 | 0.089843 | -0.053471 | 0.16658 | 0.21097 | 0.31136 | 0.10212 | -122.2493 | 122.0327 | 122.3173 | 122.174 | 10.4856 | -122.3275
4534.0156 | 122.3511 | -0.054932 | 122.1725 | -0.0025182 | -0.058871 | 0.03837 | 0.015195 | -0.014215 | -0.014909 | -0.013887 | -0.0024804 | -0.0020767 | 0.056764 | 0.051158 | 0.045765 | -0.026423 | 0.028878 | 0.000747 | 0.084176 | 0.12399 | 0.24727 | -0.099689 | 0.21625 | 10.6321 | 0.039802 | 121.9595 | 122.2487 | 122.1053 | -0.18246 | -0.044757 | -122.0884 | 0.028509 | 0.055679 | 0.10044 | -122.0486 | -121.9253 | -0.12753 | -0.21308 | 0.27118 | 0.094734 | 0.22227 | 0.076112 | -0.067202 | 0.13911 | 0.17892 | 0.30221 | 0.08381 | -122.2722 | 122.0144 | 122.3036 | 122.1603 | 10.6871 | -122.355
4535.7969 | 122.3145 | -0.064087 | 122.1451 | -0.01778 | -0.059085 | 0.038157 | 0.015195 | -0.014642 | -0.014696 | -0.021518 | -0.0024804 | -0.0016495 | 0.056764 | 0.051585 | 0.045124 | -0.021844 | 0.028878 | 0.000747 | 0.088755 | 0.13315 | 0.25185 | -0.09511 | 0.2254 | 10.8107 | 0.044381 | 121.9686 | 122.2487 | 122.1053 | -0.17331 | -0.031023 | -122.0563 | 0.042243 | 0.064834 | 0.095857 | -122.0119 | -121.8932 | -0.10922 | -0.17645 | 0.28949 | 0.10847 | 0.21769 | 0.10358 | -0.039737 | 0.15284 | 0.19723 | 0.31594 | 0.092965 | -122.2402 | 122.0327 | 122.3127 | 122.1694 | 10.8748 | -122.3184
4537.5625 | 122.3373 | -0.064087 | 122.2 | -0.0025182 | -0.059299 | 0.03837 | 0.015409 | -0.014642 | -0.014696 | -0.021518 | -0.002694 | -0.0018631 | 0.056764 | 0.051799 | 0.045551 | -0.017266 | 0.019721 | -0.003831 | 0.084176 | 0.13315 | 0.24269 | -0.09511 | 0.22083 | 10.9893 | 0.048959 | 121.9732 | 122.2487 | 122.1145 | -0.17788 | -0.031023 | -122.1158 | 0.046821 | 0.060256 | 0.091279 | -122.0669 | -121.9573 | -0.1138 | -0.2268 | 0.28491 | 0.11305 | 0.22684 | 0.048646 | -0.085511 | 0.14826 | 0.19723 | 0.30678 | 0.083808 | -122.2951 | 122.0373 | 122.3127 | 122.1786 | 11.0534 | -122.3779
4539.2812 | 122.3602 | -0.059509 | 122.1634 | -0.010149 | -0.058871 | 0.038584 | 0.015409 | -0.014215 | -0.014268 | -0.029148 | -0.002694 | -0.0020767 | 0.056978 | 0.050944 | 0.045337 | -0.017266 | 0.019721 | -0.003831 | 0.088755 | 0.12857 | 0.24727 | -0.10427 | 0.2254 | 11.1175 | 0.053538 | 121.9778 | 122.2578 | 122.1099 | -0.18246 | -0.044759 | -122.0746 | 0.042243 | 0.055678 | 0.10044 | -122.0348 | -121.9161 | -0.12295 | -0.18561 | 0.28491 | 0.11305 | 0.236 | 0.094424 | -0.053468 | 0.14826 | 0.18808 | 0.30678 | 0.07923 | -122.2677 | 122.0373 | 122.3173 | 122.1694 | 11.177 | -122.3459
4541.0625 | 122.3877 | -0.050354 | 122.1451 | -0.010149 | -0.058871 | 0.03837 | 0.015409 | -0.014429 | -0.014482 | -0.021518 | -0.0022666 | -0.0018631 | 0.056764 | 0.051585 | 0.045337 | -0.021844 | 0.033457 | 0.000747 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.23456 | 11.3327 | 0.044381 | 121.9778 | 122.2624 | 122.1191 | -0.17788 | -0.049335 | -122.0609 | 0.02851 | 0.051101 | 0.10044 | -122.0165 | -121.907 | -0.12753 | -0.1673 | 0.28492 | 0.094735 | 0.22227 | 0.11731 | -0.026001 | 0.13453 | 0.17892 | 0.28847 | 0.083811 | -122.2448 | 122.0281 | 122.3127 | 122.1694 | 11.383 | -122.323
4542.7812 | 122.3511 | -0.064087 | 122.168 | -0.01778 | -0.059085 | 0.03837 | 0.015409 | -0.014429 | -0.014268 | -0.021518 | -0.0022666 | -0.0020767 | 0.056764 | 0.051585 | 0.045124 | -0.021844 | 0.028878 | -0.008409 | 0.088755 | 0.12399 | 0.23812 | -0.099689 | 0.23456 | 11.525 | 0.044381 | 121.9732 | 122.2578 | 122.1237 | -0.17331 | -0.035602 | -122.0792 | 0.042243 | 0.055678 | 0.09128 | -122.044 | -121.9299 | -0.10922 | -0.19476 | 0.29865 | 0.10847 | 0.21769 | 0.089846 | -0.044311 | 0.15284 | 0.18808 | 0.3022 | 0.092965 | -122.2677 | 122.0373 | 122.3219 | 122.1877 | 11.5891 | -122.3413
4544.5625 | 122.2824 | -0.082397 | 122.2137 | -0.01778 | -0.058658 | 0.038584 | 0.014981 | -0.014215 | -0.013841 | -0.013887 | -0.002694 | -0.0016495 | 0.056764 | 0.051585 | 0.045551 | -0.017266 | 0.028878 | -0.003831 | 0.084176 | 0.12857 | 0.24269 | -0.09511 | 0.23914 | 11.7493 | 0.053538 | 121.9824 | 122.267 | 122.1237 | -0.18246 | -0.012713 | -122.1296 | 0.065131 | 0.078566 | 0.091279 | -122.0852 | -121.9711 | -0.10007 | -0.23138 | 0.32154 | 0.13594 | 0.236 | 0.053227 | -0.090087 | 0.16657 | 0.21097 | 0.32509 | 0.11127 | -122.3089 | 122.0648 | 122.3494 | 122.2061 | 11.8317 | -122.3962
4546.3125 | 122.2916 | -0.10071 | 122.2183 | -0.0025182 | -0.058871 | 0.038798 | 0.015409 | -0.014429 | -0.014268 | -0.013887 | -0.0022666 | -0.0020767 | 0.056978 | 0.051371 | 0.045551 | -0.026423 | 0.033457 | 0.000747 | 0.088755 | 0.13315 | 0.24269 | -0.099689 | 0.24372 | 11.8638 | 0.048959 | 121.9869 | 122.267 | 122.1328 | -0.17788 | 0.001019 | -122.1296 | 0.074285 | 0.10146 | 0.10044 | -122.0852 | -121.9756 | -0.077177 | -0.23138 | 0.34443 | 0.14967 | 0.22684 | 0.048649 | -0.085507 | 0.18946 | 0.23386 | 0.3434 | 0.13417 | -122.318 | 122.0876 | 122.3677 | 122.2335 | 11.9645 | -122.3962
4548.0781 | 122.406 | -0.054932 | 122.1863 | -0.01778 | -0.058871 | 0.038798 | 0.015409 | -0.014856 | -0.014268 | -0.021518 | -0.0024804 | -0.0016495 | 0.056764 | 0.051371 | 0.045124 | -0.017266 | 0.028878 | 0.000747 | 0.079598 | 0.12857 | 0.24727 | -0.09511 | 0.25288 | 12.0882 | 0.062695 | 121.9869 | 122.267 | 122.1282 | -0.17788 | -0.040178 | -122.1067 | 0.037666 | 0.055679 | 0.095857 | -122.0577 | -121.939 | -0.12295 | -0.19934 | 0.30781 | 0.11763 | 0.24058 | 0.080693 | -0.058042 | 0.13453 | 0.1835 | 0.30221 | 0.08381 | -122.2814 | 122.0419 | 122.3219 | 122.1832 | 12.1431 | -122.3642
4549.8438 | 122.3969 | -0.045776 | 122.1542 | -0.010149 | -0.059085 | 0.038798 | 0.015622 | -0.014856 | -0.013841 | -0.036779 | -0.002694 | -0.0016495 | 0.056978 | 0.051371 | 0.045337 | -0.017266 | 0.0243 | -0.008409 | 0.088755 | 0.12857 | 0.24727 | -0.099689 | 0.25288 | 12.2988 | 0.053538 | 121.9915 | 122.2578 | 122.1237 | -0.18246 | -0.053913 | -122.0655 | 0.02851 | 0.037367 | 0.09128 | -122.0257 | -121.907 | -0.13669 | -0.16271 | 0.29865 | 0.099314 | 0.236 | 0.10358 | -0.030578 | 0.13453 | 0.17434 | 0.29305 | 0.070076 | -122.2539 | 122.0373 | 122.3036 | 122.1694 | 12.3445 | -122.3367
4551.5469 | 122.2824 | -0.10071 | 122.2 | -0.025411 | -0.058871 | 0.038584 | 0.015195 | -0.014429 | -0.013841 | -0.021518 | -0.0024804 | -0.0018631 | 0.056978 | 0.051371 | 0.045337 | -0.017266 | 0.0243 | -0.003831 | 0.07502 | 0.13315 | 0.24269 | -0.099689 | 0.25745 | 12.4773 | 0.062695 | 121.9869 | 122.2624 | 122.1328 | -0.17788 | 0.001019 | -122.125 | 0.083442 | 0.096877 | 0.095858 | -122.0669 | -121.9573 | -0.077177 | -0.21307 | 0.35816 | 0.1634 | 0.24058 | 0.062382 | -0.067196 | 0.17573 | 0.23386 | 0.3434 | 0.12501 | -122.2997 | 122.0876 | 122.3631 | 122.2335 | 12.5781 | -122.3779
4553.2969 | 122.3007 | -0.073242 | 122.2275 | -0.01778 | -0.059085 | 0.03837 | 0.015622 | -0.014642 | -0.013628 | -0.013887 | -0.0024804 | -0.0020767 | 0.056978 | 0.051371 | 0.045337 | -0.021844 | 0.028878 | 0.000747 | 0.079598 | 0.12399 | 0.25185 | -0.09511 | 0.25745 | 12.6284 | 0.067274 | 122.0007 | 122.2716 | 122.1282 | -0.17331 | -0.021868 | -122.1479 | 0.051398 | 0.073989 | 0.095857 | -122.1035 | -121.9756 | -0.10006 | -0.2268 | 0.3307 | 0.14052 | 0.24058 | 0.044073 | -0.099241 | 0.15284 | 0.19723 | 0.32509 | 0.10212 | -122.3226 | 122.0739 | 122.3448 | 122.2015 | 12.7017 | -122.4008
4555 | 122.3145 | -0.073242 | 122.2046 | -0.010149 | -0.058871 | 0.03837 | 0.015195 | -0.014429 | -0.014055 | -0.021518 | -0.0024804 | -0.0020767 | 0.056764 | 0.051371 | 0.045551 | -0.017266 | 0.033457 | 0.005325 | 0.084176 | 0.12857 | 0.24269 | -0.09511 | 0.26661 | 12.7566 | 0.067274 | 121.9869 | 122.2761 | 122.1328 | -0.17788 | -0.021868 | -122.1204 | 0.055976 | 0.078567 | 0.10043 | -122.076 | -121.9619 | -0.10464 | -0.21765 | 0.33986 | 0.14052 | 0.24516 | 0.07154 | -0.071774 | 0.15742 | 0.20181 | 0.31594 | 0.1067 | -122.2997 | 122.0602 | 122.3494 | 122.2061 | 12.8299 | -122.3825
4556.7656 | 122.3511 | -0.07782 | 122.2 | -0.010149 | -0.059085 | 0.03837 | 0.015622 | -0.014642 | -0.014055 | -0.021518 | -0.0024804 | -0.0020767 | 0.056551 | 0.050944 | 0.045551 | -0.021844 | 0.0243 | 0.000747 | 0.084176 | 0.13773 | 0.24269 | -0.099689 | 0.27119 | 12.9444 | 0.067274 | 121.9915 | 122.2716 | 122.1328 | -0.18246 | -0.021869 | -122.1158 | 0.055976 | 0.078567 | 0.10044 | -122.0623 | -121.9573 | -0.10464 | -0.20849 | 0.34901 | 0.14509 | 0.24974 | 0.071539 | -0.067196 | 0.162 | 0.21555 | 0.32051 | 0.10212 | -122.2997 | 122.0693 | 122.3494 | 122.2106 | 13.0222 | -122.3825
4558.5469 | 122.3969 | -0.050354 | 122.1817 | -0.010149 | -0.058871 | 0.03837 | 0.015195 | -0.014429 | -0.0132 | -0.021518 | -0.002694 | -0.0018631 | 0.056978 | 0.051371 | 0.045765 | -0.021844 | 0.0243 | 0.000747 | 0.084176 | 0.12857 | 0.24269 | -0.099689 | 0.27577 | 13.1458 | 0.08101 | 121.9915 | 122.267 | 122.142 | -0.17331 | -0.049335 | -122.0975 | 0.02851 | 0.051101 | 0.10044 | -122.0531 | -121.939 | -0.12295 | -0.19018 | 0.32612 | 0.13136 | 0.25432 | 0.08527 | -0.039729 | 0.13453 | 0.17892 | 0.29305 | 0.074654 | -122.2814 | 122.0419 | 122.3173 | 122.1923 | 13.1962 | -122.355
4560.3125 | 122.2733 | -0.10986 | 122.2137 | 0.0051128 | -0.059085 | 0.03837 | 0.015409 | -0.014642 | -0.013841 | -0.029148 | -0.0024804 | -0.0016495 | 0.056551 | 0.051585 | 0.045551 | -0.017266 | 0.0243 | 0.005325 | 0.093333 | 0.12857 | 0.23812 | -0.09511 | 0.28035 | 13.2374 | 0.076431 | 121.9915 | 122.267 | 122.1374 | -0.17788 | 0.014753 | -122.1204 | 0.092597 | 0.11519 | 0.10043 | -122.0852 | -121.9756 | -0.068022 | -0.22222 | 0.39021 | 0.18629 | 0.25432 | 0.053227 | -0.076351 | 0.2032 | 0.23843 | 0.34798 | 0.13416 | -122.3089 | 122.1014 | 122.3768 | 122.2473 | 13.3473 | -122.3916
4562.0156 | 122.2595 | -0.10071 | 122.2137 | -0.010149 | -0.059085 | 0.03837 | 0.015195 | -0.014429 | -0.013628 | -0.021518 | -0.0024804 | -0.0018631 | 0.057191 | 0.051585 | 0.045337 | -0.021844 | 0.0243 | -0.008409 | 0.084176 | 0.13315 | 0.23812 | -0.099689 | 0.28951 | 13.3885 | 0.071853 | 121.9915 | 122.2761 | 122.1328 | -0.17788 | 0.001019 | -122.1296 | 0.078864 | 0.092299 | 0.09128 | -122.0806 | -121.9756 | -0.077177 | -0.22222 | 0.39021 | 0.17256 | 0.24974 | 0.062385 | -0.080929 | 0.18488 | 0.23386 | 0.33882 | 0.12501 | -122.3134 | 122.0922 | 122.3768 | 122.2335 | 13.4892 | -122.3916
4563.7188 | 122.3282 | -0.07782 | 122.1771 | -0.01778 | -0.058871 | 0.038584 | 0.015409 | -0.014642 | -0.013414 | -0.021518 | -0.0024804 | -0.0018631 | 0.056551 | 0.051799 | 0.045551 | -0.021844 | 0.0243 | -0.008409 | 0.088755 | 0.13315 | 0.24269 | -0.09511 | 0.29408 | 13.5945 | 0.076431 | 121.9961 | 122.2716 | 122.1282 | -0.17331 | -0.01729 | -122.0884 | 0.055976 | 0.069411 | 0.086701 | -122.044 | -121.9344 | -0.095486 | -0.18103 | 0.3719 | 0.15425 | 0.24974 | 0.094427 | -0.048887 | 0.16658 | 0.21097 | 0.32051 | 0.10212 | -122.2722 | 122.0739 | 122.3494 | 122.2061 | 13.6724 | -122.3504
4565.4844 | 122.3328 | -0.10529 | 122.2183 | -0.01778 | -0.059085 | 0.038584 | 0.015622 | -0.014642 | -0.013628 | -0.021518 | -0.0024804 | -0.0016495 | 0.056978 | 0.051585 | 0.045551 | -0.017266 | 0.0243 | -0.003831 | 0.088755 | 0.12857 | 0.25185 | -0.099689 | 0.30782 | 13.7731 | 0.085589 | 121.9915 | 122.2761 | 122.1374 | -0.17788 | 0.005597 | -122.1296 | 0.08802 | 0.10146 | 0.095858 | -122.0898 | -121.9665 | -0.072599 | -0.2268 | 0.41311 | 0.19088 | 0.26347 | 0.057807 | -0.080929 | 0.19404 | 0.23385 | 0.35714 | 0.12959 | -122.318 | 122.0968 | 122.3814 | 122.2427 | 13.8784 | -122.3962
4567.1719 | 122.374 | -0.068665 | 122.2092 | -0.025411 | -0.059085 | 0.03837 | 0.014981 | -0.014642 | -0.013414 | -0.021518 | -0.002694 | -0.0018631 | 0.056978 | 0.051585 | 0.045765 | -0.026423 | 0.0243 | -0.008409 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.29866 | 13.8647 | 0.08101 | 121.9961 | 122.2761 | 122.1374 | -0.17331 | -0.031024 | -122.125 | 0.042242 | 0.060256 | 0.09128 | -122.0806 | -121.971 | -0.10464 | -0.21307 | 0.36733 | 0.14968 | 0.25432 | 0.066963 | -0.071773 | 0.15284 | 0.19723 | 0.30678 | 0.092965 | -122.3089 | 122.0648 | 122.3448 | 122.2061 | 13.9334 | -122.3825
4568.9375 | 122.4106 | -0.032043 | 122.1863 | -0.01778 | -0.059299 | 0.03837 | 0.015195 | -0.014215 | -0.012987 | -0.013887 | -0.0022666 | -0.0022903 | 0.056764 | 0.051799 | 0.045337 | -0.021844 | 0.028878 | -0.008409 | 0.084176 | 0.12857 | 0.24269 | -0.09511 | 0.30782 | 14.0753 | 0.094746 | 122.0007 | 122.2761 | 122.1466 | -0.17788 | -0.063067 | -122.1021 | 0.010199 | 0.023634 | 0.086701 | -122.0577 | -121.9436 | -0.14584 | -0.1856 | 0.33986 | 0.12679 | 0.27263 | 0.089851 | -0.039728 | 0.11622 | 0.16061 | 0.27474 | 0.060921 | -122.2814 | 122.0327 | 122.3082 | 122.1786 | 14.1074 | -122.3642
4570.7188 | 122.3648 | -0.059509 | 122.1725 | -0.01778 | -0.059085 | 0.038798 | 0.015409 | -0.014856 | -0.012987 | -0.021518 | -0.002694 | -0.0018631 | 0.056764 | 0.051799 | 0.045551 | -0.017266 | 0.028878 | -0.003831 | 0.079598 | 0.12399 | 0.24269 | -0.09511 | 0.31698 | 14.318 | 0.090168 | 122.0007 | 122.2807 | 122.142 | -0.17788 | -0.035601 | -122.0929 | 0.042243 | 0.055678 | 0.091279 | -122.0486 | -121.9299 | -0.11838 | -0.17187 | 0.37649 | 0.14968 | 0.26805 | 0.10816 | -0.030573 | 0.13911 | 0.1835 | 0.3022 | 0.088387 | -122.2677 | 122.0602 | 122.3402 | 122.2015 | 14.3775 | -122.3504
4572.4219 | 122.2824 | -0.11902 | 122.2183 | -0.010149 | -0.059085 | 0.03837 | 0.015195 | -0.014642 | -0.0132 | -0.021518 | -0.0029076 | -0.0018631 | 0.056764 | 0.051585 | 0.045551 | -0.021844 | 0.028878 | 0.000747 | 0.084176 | 0.12857 | 0.24269 | -0.10885 | 0.32614 | 14.4462 | 0.094746 | 122.0007 | 122.2716 | 122.1328 | -0.17788 | 0.010172 | -122.1341 | 0.097175 | 0.11977 | 0.10959 | -122.0898 | -121.9756 | -0.058866 | -0.21765 | 0.44515 | 0.21376 | 0.27263 | 0.053228 | -0.085507 | 0.2032 | 0.24759 | 0.36171 | 0.1479 | -122.3272 | 122.1197 | 122.3906 | 122.2518 | 14.5652 | -122.3962
4574.2031 | 122.3694 | -0.068665 | 122.1817 | -0.025411 | -0.059299 | 0.038157 | 0.015409 | -0.014856 | -0.0132 | -0.021518 | -0.0024804 | -0.0016495 | 0.056978 | 0.051585 | 0.045337 | -0.021844 | 0.015142 | -0.003831 | 0.079598 | 0.12857 | 0.24269 | -0.09511 | 0.32614 | 14.6064 | 0.099325 | 121.9961 | 122.2761 | 122.142 | -0.18246 | -0.026445 | -122.1021 | 0.046821 | 0.064834 | 0.091279 | -122.0531 | -121.939 | -0.1138 | -0.1856 | 0.3948 | 0.16799 | 0.28179 | 0.094428 | -0.039729 | 0.14826 | 0.19723 | 0.31136 | 0.083807 | -122.2768 | 122.0648 | 122.3448 | 122.2106 | 14.6751 | -122.3642
4575.9688 | 122.3648 | -0.073242 | 122.1954 | -0.010149 | -0.059299 | 0.038584 | 0.014981 | -0.014642 | -0.0132 | -0.021518 | -0.002694 | -0.0016495 | 0.056978 | 0.051371 | 0.045337 | -0.017266 | 0.028878 | -0.003831 | 0.079598 | 0.12399 | 0.24727 | -0.09511 | 0.34903 | 14.7118 | 0.099325 | 122.0007 | 122.2716 | 122.142 | -0.18246 | -0.021868 | -122.1158 | 0.055976 | 0.069411 | 0.091279 | -122.0714 | -121.9482 | -0.10922 | -0.19476 | 0.42227 | 0.17257 | 0.28179 | 0.076116 | -0.053462 | 0.15284 | 0.19723 | 0.32052 | 0.10212 | -122.2905 | 122.0739 | 122.3448 | 122.2152 | 14.785 | -122.3779
4577.7344 | 122.4426 | -0.07782 | 122.1634 | -0.025411 | -0.058871 | 0.038584 | 0.015836 | -0.014429 | -0.012987 | -0.013887 | -0.0024804 | -0.0014357 | 0.056978 | 0.051585 | 0.045765 | -0.021844 | 0.0243 | -0.012988 | 0.088755 | 0.12399 | 0.24727 | -0.099689 | 0.34903 | 14.9086 | 0.10848 | 122.0007 | 122.2807 | 122.142 | -0.18246 | -0.021869 | -122.0746 | 0.055976 | 0.064832 | 0.086701 | -122.0394 | -121.9161 | -0.10464 | -0.16271 | 0.42685 | 0.1863 | 0.29095 | 0.11732 | -0.021418 | 0.16658 | 0.20181 | 0.32509 | 0.10212 | -122.2631 | 122.0785 | 122.3585 | 122.2198 | 14.9865 | -122.3459
4579.4531 | 122.3923 | -0.045776 | 122.1817 | -0.010149 | -0.058871 | 0.03837 | 0.015195 | -0.014429 | -0.012559 | -0.021518 | -0.0024804 | -0.0016495 | 0.056978 | 0.051585 | 0.045337 | -0.021844 | 0.0243 | -0.003831 | 0.088755 | 0.12857 | 0.24269 | -0.099689 | 0.35361 | 15.0414 | 0.11306 | 122.0053 | 122.2853 | 122.1374 | -0.17788 | -0.053913 | -122.0929 | 0.023932 | 0.041945 | 0.095858 | -122.0531 | -121.939 | -0.13211 | -0.17645 | 0.39938 | 0.15884 | 0.29095 | 0.10358 | -0.044308 | 0.13453 | 0.17434 | 0.28847 | 0.070076 | -122.2814 | 122.051 | 122.3311 | 122.1832 | 15.0872 | -122.3596
4581.2188 | 122.319 | -0.07782 | 122.2137 | -0.0025182 | -0.059512 | 0.038584 | 0.015409 | -0.014856 | -0.012559 | -0.021518 | -0.0024804 | -0.0018631 | 0.057191 | 0.051585 | 0.045337 | -0.017266 | 0.028878 | 0.000747 | 0.084176 | 0.12857 | 0.23812 | -0.099689 | 0.36277 | 15.1925 | 0.11764 | 122.0053 | 122.2853 | 122.142 | -0.18246 | -0.021869 | -122.1296 | 0.060554 | 0.078567 | 0.10044 | -122.0852 | -121.9756 | -0.10464 | -0.20849 | 0.44059 | 0.19546 | 0.3001 | 0.071542 | -0.071772 | 0.162 | 0.20639 | 0.31594 | 0.1067 | -122.3134 | 122.0831 | 122.3631 | 122.2198 | 15.2703 | -122.3962
4582.9688 | 122.2961 | -0.10529 | 122.1771 | -0.010149 | -0.059299 | 0.038584 | 0.015195 | -0.014856 | -0.012559 | -0.013887 | -0.0024804 | -0.0014357 | 0.056978 | 0.051371 | 0.045551 | -0.026423 | 0.015142 | -0.012988 | 0.065863 | 0.11483 | 0.23354 | -0.12716 | 0.35361 | 15.3528 | 0.11306 | 121.9915 | 122.2716 | 122.1328 | -0.19162 | -0.021876 | -122.1113 | 0.078863 | 0.092298 | 0.11417 | -122.0623 | -121.9436 | -0.086336 | -0.1856 | 0.45889 | 0.21835 | 0.30468 | 0.094427 | -0.044308 | 0.17115 | 0.22012 | 0.33882 | 0.12043 | -122.3043 | 122.0968 | 122.3768 | 122.2381 | 15.4581 | -122.3687
4584.7344 | 122.4152 | 0.42572 | 122.7081 | -0.0025182 | -0.059299 | 0.038584 | 0.015195 | -0.014856 | -0.012346 | -0.021518 | -0.002694 | -0.0016495 | 0.056764 | 0.051158 | 0.045337 | 0.001048 | 0.047193 | 0.014482 | 0.07502 | 0.15146 | 0.26559 | -0.13174 | 0.3994 | 15.5039 | 0.14511 | 122.0236 | 122.3082 | 122.1694 | -0.15499 | -0.55746 | -122.6331 | -0.42467 | -0.41124 | 0.14622 | -122.5567 | -122.4425 | -0.58071 | -0.68456 | -0.026325 | -0.28061 | 0.3001 | -0.39995 | -0.53869 | -0.3507 | -0.27426 | -0.16013 | -0.37853 | -122.8399 | 121.5979 | 121.8825 | 121.7437 | 15.0782 | -122.8631
4586.4375 | 122.4243 | -0.054932 | 122.1588 | -0.010149 | -0.059299 | 0.038798 | 0.015195 | -0.014215 | -0.012346 | -0.013887 | -0.0024804 | -0.0014357 | 0.057191 | 0.052012 | 0.045551 | 0.001048 | 0.047193 | 0.014482 | 0.10249 | 0.14688 | 0.26559 | -0.09511 | 0.40855 | 15.6458 | 0.15885 | 122.0236 | 122.3128 | 122.1649 | -0.15499 | -0.040178 | -122.0563 | 0.05598 | 0.069414 | 0.10959 | -122.0119 | -121.8932 | -0.10006 | -0.13524 | 0.46348 | 0.21378 | 0.31384 | 0.15395 | 0.006053 | 0.15742 | 0.20182 | 0.32052 | 0.10212 | -122.2539 | 122.0785 | 122.3677 | 122.2198 | 15.7007 | -122.3138
4588.2031 | 122.4335 | 0.50812 | 122.8363 | -0.01778 | -0.059085 | 0.038584 | 0.015409 | -0.014429 | -0.012346 | -0.021518 | -0.0024804 | -0.0016495 | 0.056978 | 0.052012 | 0.045551 | 0.005626 | 0.051771 | 0.014482 | 0.093333 | 0.15146 | 0.26559 | -0.10885 | 0.41313 | 15.7649 | 0.14969 | 122.0236 | 122.299 | 122.1557 | -0.15957 | -0.61696 | -122.743 | -0.50249 | -0.49364 | 0.12333 | -122.6848 | -122.5707 | -0.66769 | -0.81273 | -0.094987 | -0.35843 | 0.30926 | -0.53728 | -0.68059 | -0.41478 | -0.35665 | -0.24253 | -0.45635 | -122.9452 | 121.5155 | 121.7909 | 121.6476 | 15.2567 | -122.9959
4589.9844 | 122.2549 | 0.4303 | 122.7814 | -0.01778 | -0.059299 | 0.03837 | 0.015622 | -0.014642 | -0.012132 | -0.0062567 | -0.0022666 | -0.0018631 | 0.056764 | 0.051799 | 0.045337 | -0.021844 | 0.015142 | -0.017566 | 0.065863 | 0.12399 | 0.23354 | -0.12258 | 0.38566 | 15.8427 | 0.12222 | 121.9915 | 122.2716 | 122.1237 | -0.1962 | -0.55288 | -122.7155 | -0.45214 | -0.44786 | 0.10502 | -122.6574 | -122.5478 | -0.6265 | -0.78985 | -0.044639 | -0.30808 | 0.31842 | -0.50982 | -0.65771 | -0.36444 | -0.30631 | -0.19676 | -0.41516 | -122.904 | 121.5612 | 121.8413 | 121.6934 | 15.4124 | -122.9776
4591.75 | 122.4014 | -0.45319 | 121.8063 | -0.010149 | -0.059085 | 0.03837 | 0.015409 | -0.014642 | -0.012132 | -0.029148 | -0.002053 | -0.0016495 | 0.056764 | 0.052012 | 0.045337 | -0.031001 | 0.0243 | -0.017566 | 0.065863 | 0.11941 | 0.24727 | -0.10885 | 0.3994 | 15.9572 | 0.13595 | 121.9961 | 122.2716 | 122.1328 | -0.18246 | 0.34434 | -121.7405 | 0.42218 | 0.43562 | 0.091281 | -121.6869 | -121.5591 | 0.27072 | 0.18976 | 0.85258 | 0.58914 | 0.31842 | 0.46522 | 0.32648 | 0.51905 | 0.5726 | 0.70046 | 0.47749 | -121.9152 | 122.4493 | 122.7247 | 122.586 | 16.4103 | -121.9888
4593.4531 | 122.287 | 0.46234 | 122.8088 | -0.010149 | -0.059299 | 0.038157 | 0.015195 | -0.014642 | -0.011705 | -0.021518 | -0.0029076 | -0.0014357 | 0.056764 | 0.051799 | 0.045765 | -0.012688 | 0.033457 | 0.005325 | 0.07502 | 0.13315 | 0.25185 | -0.12258 | 0.43145 | 16.0442 | 0.14969 | 122.0098 | 122.2899 | 122.1511 | -0.16873 | -0.58492 | -122.7338 | -0.47503 | -0.45702 | 0.12791 | -122.6757 | -122.557 | -0.63107 | -0.799 | -0.030895 | -0.31265 | 0.31842 | -0.51897 | -0.65771 | -0.38732 | -0.32919 | -0.21049 | -0.42888 | -122.9314 | 121.5475 | 121.8275 | 121.6888 | 15.5818 | -122.9776
4595.2188 | 122.2549 | 0.63629 | 122.9645 | -0.0025182 | -0.059512 | 0.03837 | 0.015409 | -0.014642 | -0.011491 | -0.021518 | -0.0024804 | -0.0012221 | 0.056764 | 0.051585 | 0.045551 | -0.095099 | -0.048958 | -0.090818 | -0.007391 | 0.050727 | 0.16944 | -0.21416 | 0.34445 | 16.0899 | 0.071853 | 121.9228 | 122.2029 | 122.0641 | -0.2603 | -0.85045 | -122.9719 | -0.73139 | -0.72711 | 0.12334 | -122.9138 | -122.795 | -0.8966 | -1.0416 | -0.29184 | -0.56444 | 0.33216 | -0.76161 | -0.90034 | -0.64368 | -0.58557 | -0.46685 | -0.68525 | -123.1786 | 121.2866 | 121.5666 | 121.4278 | 15.4537 | -123.2248
4596.9219 | 122.3648 | -0.59967 | 121.7148 | -0.010149 | -0.059085 | 0.038584 | 0.015195 | -0.014429 | -0.011491 | -0.021518 | -0.002694 | -0.0018631 | 0.056978 | 0.051799 | 0.045978 | -0.06305 | -0.021486 | -0.054192 | 0.006344 | 0.08278 | 0.20149 | -0.21416 | 0.38566 | 16.1907 | 0.1039 | 121.9641 | 122.2349 | 122.0916 | -0.22825 | 0.38551 | -121.7084 | 0.53662 | 0.54548 | 0.15997 | -121.632 | -121.5133 | 0.37142 | 0.24927 | 0.98533 | 0.70357 | 0.33216 | 0.52014 | 0.37682 | 0.60601 | 0.68245 | 0.80116 | 0.57818 | -121.9289 | 122.5637 | 122.8346 | 122.6913 | 16.7903 | -121.943
4598.6875 | 122.3007 | -0.10529 | 122.1909 | -0.025411 | -0.059299 | 0.038584 | 0.015195 | -0.014642 | -0.011277 | -0.013887 | -0.0024804 | -0.0016495 | 0.057619 | 0.052012 | 0.045337 | -0.031001 | 0.0243 | -0.008409 | 0.079598 | 0.12399 | 0.23812 | -0.10885 | 0.43145 | 16.2823 | 0.14969 | 121.9961 | 122.2761 | 122.1282 | -0.18704 | -0.003561 | -122.1113 | 0.074285 | 0.096877 | 0.10044 | -122.0669 | -121.9527 | -0.081757 | -0.19476 | 0.53673 | 0.25498 | 0.33673 | 0.085273 | -0.06262 | 0.18488 | 0.22928 | 0.3434 | 0.12959 | -122.2997 | 122.1014 | 122.3814 | 122.2335 | 16.3875 | -122.3779
4600.3906 | 122.4243 | -0.64545 | 121.5958 | -0.01778 | -0.059726 | 0.03837 | 0.015409 | -0.014215 | -0.01085 | -0.029148 | -0.0022666 | -0.0014357 | 0.056978 | 0.052012 | 0.045337 | -0.049315 | -0.007751 | -0.031301 | 0.047549 | 0.1011 | 0.21522 | -0.15464 | 0.42229 | 16.3555 | 0.13138 | 121.9778 | 122.2487 | 122.1145 | -0.20536 | 0.49081 | -121.5482 | 0.59613 | 0.61415 | 0.12334 | -121.4947 | -121.3805 | 0.44009 | 0.38202 | 1.0677 | 0.77682 | 0.33673 | 0.65289 | 0.51874 | 0.693 | 0.74654 | 0.86067 | 0.6377 | -121.7504 | 122.6232 | 122.8941 | 122.7599 | 17.001 | -121.8011
4602.1562 | 122.4335 | -0.35706 | 121.8475 | -0.010149 | -0.059512 | 0.038798 | 0.015195 | -0.014429 | -0.011277 | -0.021518 | -0.0022666 | -0.0014357 | 0.056978 | 0.051799 | 0.045551 | -0.026423 | 0.019721 | -0.017566 | 0.07502 | 0.12399 | 0.24269 | -0.1409 | 0.44976 | 16.4791 | 0.16801 | 122.0007 | 122.2807 | 122.1374 | -0.18704 | 0.21616 | -121.7725 | 0.33063 | 0.33949 | 0.12333 | -121.7235 | -121.6048 | 0.17001 | 0.15314 | 0.80682 | 0.52506 | 0.35505 | 0.43317 | 0.28986 | 0.43208 | 0.48105 | 0.59975 | 0.37678 | -121.9884 | 122.3577 | 122.6378 | 122.4945 | 16.8362 | -122.0346
4603.8594 | 122.3785 | -0.054932 | 122.1817 | -0.025411 | -0.059085 | 0.038157 | 0.015195 | -0.014642 | -0.01085 | -0.036779 | -0.002053 | -0.0014357 | 0.057191 | 0.051799 | 0.045551 | -0.021844 | 0.028878 | -0.003831 | 0.084176 | 0.13773 | 0.24727 | -0.099689 | 0.4635 | 16.5112 | 0.16343 | 121.9915 | 122.2807 | 122.1466 | -0.18246 | -0.044757 | -122.0975 | 0.033088 | 0.051101 | 0.095858 | -122.044 | -121.9344 | -0.12753 | -0.19018 | 0.51843 | 0.21836 | 0.34589 | 0.099006 | -0.035151 | 0.13911 | 0.19266 | 0.30221 | 0.08381 | -122.2814 | 122.0465 | 122.3356 | 122.2015 | 16.5661 | -122.3642
4605.625 | 122.3145 | -0.091553 | 122.2229 | -0.010149 | -0.059512 | 0.038584 | 0.015195 | -0.014429 | -0.01085 | -0.013887 | -0.0018394 | -0.0012221 | 0.056978 | 0.051799 | 0.045124 | -0.021844 | 0.028878 | -0.008409 | 0.084176 | 0.13315 | 0.24269 | -0.090531 | 0.47723 | 16.589 | 0.16801 | 122.0007 | 122.2761 | 122.1466 | -0.17331 | 0.001022 | -122.1387 | 0.069709 | 0.083144 | 0.082122 | -122.0898 | -121.9802 | -0.081753 | -0.22222 | 0.56879 | 0.25956 | 0.34131 | 0.05323 | -0.076349 | 0.17573 | 0.2247 | 0.33425 | 0.12043 | -122.3134 | 122.0922 | 122.3677 | 122.2381 | 16.6806 | -122.3962
4607.3281 | 122.319 | -0.10071 | 122.2458 | -0.01778 | -0.059726 | 0.03837 | 0.015195 | -0.014642 | -0.010636 | -0.021518 | -0.002694 | -0.0014357 | 0.056978 | 0.052012 | 0.045551 | -0.017266 | 0.019721 | -0.008409 | 0.084176 | 0.13773 | 0.24269 | -0.099689 | 0.48181 | 16.7127 | 0.17716 | 121.9915 | 122.2853 | 122.1466 | -0.18246 | 0.001019 | -122.1616 | 0.083442 | 0.092299 | 0.09128 | -122.1081 | -122.0031 | -0.081756 | -0.25427 | 0.58252 | 0.27787 | 0.35963 | 0.039498 | -0.099238 | 0.18488 | 0.23844 | 0.3434 | 0.12043 | -122.3455 | 122.0922 | 122.386 | 122.2473 | 16.8134 | -122.4283
4609.0938 | 122.3969 | -0.073242 | 122.2046 | -0.01778 | -0.059299 | 0.03837 | 0.015195 | -0.014429 | -0.011277 | -0.029148 | -0.0024804 | -0.0014357 | 0.056978 | 0.052012 | 0.045124 | -0.021844 | 0.0243 | -0.003831 | 0.084176 | 0.12857 | 0.23812 | -0.10427 | 0.49097 | 16.818 | 0.18632 | 121.9869 | 122.2807 | 122.142 | -0.17788 | -0.031026 | -122.1204 | 0.051398 | 0.069411 | 0.10044 | -122.076 | -121.9665 | -0.10464 | -0.21765 | 0.56421 | 0.25956 | 0.36421 | 0.076118 | -0.062617 | 0.15742 | 0.20181 | 0.31136 | 0.097542 | -122.3089 | 122.0602 | 122.3539 | 122.2152 | 16.8912 | -122.3825
4610.7969 | 122.3099 | -0.09613 | 122.2366 | -0.010149 | -0.059299 | 0.038584 | 0.015195 | -0.014429 | -0.010423 | -0.013887 | -0.0022666 | -0.0014357 | 0.057191 | 0.052012 | 0.045337 | -0.021844 | 0.028878 | -0.008409 | 0.088755 | 0.13315 | 0.23812 | -0.09511 | 0.50471 | 16.9645 | 0.1909 | 121.9915 | 122.2853 | 122.1328 | -0.17788 | 0.00102 | -122.1479 | 0.074286 | 0.087721 | 0.086701 | -122.1035 | -121.9985 | -0.081755 | -0.24511 | 0.60084 | 0.28703 | 0.36878 | 0.048654 | -0.10382 | 0.18488 | 0.22928 | 0.33425 | 0.12501 | -122.3317 | 122.0877 | 122.3814 | 122.2289 | 17.0606 | -122.4145
4612.5625 | 122.287 | -0.10071 | 122.2046 | -0.010149 | -0.059085 | 0.03837 | 0.014981 | -0.014429 | -0.010636 | -0.013887 | -0.0024804 | -0.0014357 | 0.056764 | 0.052012 | 0.045337 | -0.017266 | 0.033457 | -0.012988 | 0.084176 | 0.12399 | 0.24727 | -0.099689 | 0.51844 | 17.1385 | 0.19548 | 122.0007 | 122.2807 | 122.1466 | -0.18704 | 0.001019 | -122.1204 | 0.083442 | 0.08772 | 0.086701 | -122.0806 | -121.9573 | -0.086335 | -0.20391 | 0.61915 | 0.29619 | 0.38252 | 0.076118 | -0.058039 | 0.18488 | 0.2247 | 0.34798 | 0.13417 | -122.3043 | 122.1014 | 122.3814 | 122.2473 | 17.2392 | -122.3916
4614.3281 | 122.2824 | -0.10071 | 122.2046 | -0.010149 | -0.059726 | 0.038584 | 0.015195 | -0.014215 | -0.010209 | -0.021518 | -0.002053 | -0.0016495 | 0.056978 | 0.052012 | 0.045765 | -0.021844 | 0.028878 | -0.003831 | 0.088755 | 0.12857 | 0.24727 | -0.10427 | 0.52302 | 17.285 | 0.20006 | 121.9869 | 122.2853 | 122.142 | -0.18704 | -0.00356 | -122.1158 | 0.078864 | 0.096877 | 0.10044 | -122.076 | -121.9573 | -0.086335 | -0.21765 | 0.62373 | 0.30077 | 0.3871 | 0.080697 | -0.062617 | 0.18946 | 0.22928 | 0.34798 | 0.12959 | -122.3089 | 122.0876 | 122.386 | 122.2427 | 17.3857 | -122.3916
4616.0469 | 122.2687 | -0.10986 | 122.2137 | -0.010149 | -0.059726 | 0.038157 | 0.015409 | -0.014642 | -0.010209 | -0.021518 | -0.0022666 | -0.0012221 | 0.057191 | 0.051371 | 0.045551 | -0.021844 | 0.033457 | -0.003831 | 0.079598 | 0.12857 | 0.24269 | -0.10427 | 0.5276 | 17.4178 | 0.20921 | 121.9961 | 122.2716 | 122.1374 | -0.17788 | 0.005595 | -122.1341 | 0.088019 | 0.10603 | 0.10044 | -122.0852 | -121.9711 | -0.068022 | -0.21765 | 0.63746 | 0.31908 | 0.3871 | 0.057806 | -0.076351 | 0.18946 | 0.23843 | 0.35256 | 0.14332 | -122.318 | 122.106 | 122.3814 | 122.2473 | 17.5276 | -122.3916
4617.75 | 122.3419 | -0.082397 | 122.2183 | -0.010149 | -0.059299 | 0.03837 | 0.015195 | -0.014642 | -0.010209 | -0.013887 | -0.002694 | -0.0014357 | 0.056978 | 0.051799 | 0.045765 | -0.021844 | 0.028878 | -0.003831 | 0.079598 | 0.13315 | 0.24269 | -0.099689 | 0.54134 | 17.6101 | 0.20464 | 122.0007 | 122.2853 | 122.142 | -0.18246 | -0.017292 | -122.1387 | 0.060553 | 0.078566 | 0.095858 | -122.0852 | -121.9756 | -0.10007 | -0.21765 | 0.62373 | 0.28703 | 0.3871 | 0.066964 | -0.07635 | 0.162 | 0.21554 | 0.32509 | 0.11127 | -122.318 | 122.0831 | 122.3677 | 122.2244 | 17.6925 | -122.4008
4619.5 | 122.3099 | -0.086975 | 122.2137 | -0.010149 | -0.059299 | 0.038584 | 0.014768 | -0.014429 | -0.0099951 | -0.013887 | -0.0024804 | -0.0014357 | 0.056978 | 0.051799 | 0.045337 | -0.021844 | 0.028878 | -0.003831 | 0.093333 | 0.13315 | 0.24727 | -0.09511 | 0.55965 | 17.7566 | 0.21837 | 122.0007 | 122.2761 | 122.142 | -0.18704 | -0.008135 | -122.1204 | 0.065131 | 0.083144 | 0.091279 | -122.0806 | -121.9665 | -0.10007 | -0.21307 | 0.64663 | 0.30535 | 0.40541 | 0.062385 | -0.071772 | 0.18031 | 0.22012 | 0.33425 | 0.11585 | -122.3089 | 122.0877 | 122.3631 | 122.2289 | 17.8436 | -122.4008
4621.2656 | 122.3373 | -0.082397 | 122.2275 | -0.010149 | -0.059512 | 0.03837 | 0.015195 | -0.014856 | -0.0097815 | -0.021518 | -0.0022666 | -0.0014357 | 0.056764 | 0.051799 | 0.045765 | -0.021844 | 0.033457 | -0.003831 | 0.088755 | 0.12857 | 0.24269 | -0.099689 | 0.56881 | 17.9169 | 0.22295 | 121.9915 | 122.2761 | 122.142 | -0.17788 | -0.017292 | -122.1387 | 0.060553 | 0.078566 | 0.095858 | -122.0989 | -121.9848 | -0.095488 | -0.23596 | 0.65121 | 0.30535 | 0.40083 | 0.048652 | -0.085505 | 0.17115 | 0.21097 | 0.32509 | 0.11585 | -122.3272 | 122.0739 | 122.3585 | 122.2244 | 17.9992 | -122.4054
4622.9688 | 122.3557 | -0.068665 | 122.2412 | -0.010149 | -0.059512 | 0.038584 | 0.015409 | -0.014856 | -0.0093541 | -0.013887 | -0.0018394 | -0.0016495 | 0.057191 | 0.051799 | 0.045337 | -0.021844 | 0.0243 | -0.003831 | 0.088755 | 0.12857 | 0.24727 | -0.099689 | 0.57339 | 18.0954 | 0.23669 | 121.9915 | 122.2761 | 122.1466 | -0.18704 | -0.031024 | -122.1525 | 0.046821 | 0.064834 | 0.095858 | -122.1126 | -121.9939 | -0.11838 | -0.24969 | 0.64205 | 0.30535 | 0.42373 | 0.034919 | -0.09466 | 0.15742 | 0.19723 | 0.31594 | 0.092965 | -122.3409 | 122.0602 | 122.3448 | 122.2152 | 18.1641 | -122.4283
4624.7344 | 122.3007 | -0.1236 | 122.2183 | -0.010149 | -0.059512 | 0.038157 | 0.015409 | -0.014642 | -0.0093541 | -0.021518 | -0.0022666 | -0.0012221 | 0.057191 | 0.052012 | 0.045551 | -0.012688 | 0.0243 | -0.003831 | 0.093333 | 0.13315 | 0.23812 | -0.09511 | 0.5917 | 18.2282 | 0.23211 | 121.9869 | 122.2716 | 122.142 | -0.17788 | 0.028486 | -122.125 | 0.11091 | 0.11976 | 0.091279 | -122.0852 | -121.9802 | -0.054289 | -0.23138 | 0.7153 | 0.3557 | 0.40999 | 0.053228 | -0.07635 | 0.21693 | 0.25674 | 0.36171 | 0.1479 | -122.3134 | 122.1105 | 122.3951 | 122.2656 | 18.3518 | -122.3962
4626.4375 | 122.3923 | -0.059509 | 122.1588 | -0.01778 | -0.059512 | 0.038584 | 0.015195 | -0.014429 | -0.0089269 | -0.029148 | -0.002694 | -0.0014357 | 0.057405 | 0.051799 | 0.045551 | -0.017266 | 0.0243 | -0.012988 | 0.084176 | 0.13315 | 0.24269 | -0.099689 | 0.61002 | 18.3747 | 0.24584 | 121.9869 | 122.2807 | 122.1328 | -0.18246 | -0.04018 | -122.0746 | 0.042243 | 0.046521 | 0.086701 | -122.0257 | -121.9161 | -0.12295 | -0.17187 | 0.66953 | 0.30535 | 0.42831 | 0.1219 | -0.025997 | 0.14369 | 0.19266 | 0.3022 | 0.083809 | -122.2585 | 122.0465 | 122.3402 | 122.1923 | 18.4342 | -122.3413
4628.2031 | 122.3785 | -0.064087 | 122.1817 | -0.01778 | -0.059726 | 0.038157 | 0.015409 | -0.014642 | -0.0089269 | -0.021518 | -0.0024804 | -0.0014357 | 0.057405 | 0.051799 | 0.045765 | -0.012688 | 0.033457 | -0.003831 | 0.084176 | 0.13315 | 0.24727 | -0.09511 | 0.6146 | 18.5167 | 0.255 | 121.9869 | 122.2899 | 122.142 | -0.17788 | -0.031023 | -122.0975 | 0.051399 | 0.060256 | 0.091279 | -122.0486 | -121.9344 | -0.1138 | -0.19476 | 0.67868 | 0.31909 | 0.43289 | 0.10816 | -0.039729 | 0.14826 | 0.19723 | 0.31136 | 0.097544 | -122.2768 | 122.051 | 122.354 | 122.2061 | 18.5807 | -122.3596
4629.9219 | 122.3969 | -0.041199 | 122.1909 | -0.0025182 | -0.059512 | 0.03837 | 0.015409 | -0.014642 | -0.0084995 | -0.021518 | -0.0024804 | -0.0014357 | 0.056764 | 0.051799 | 0.045551 | -0.021844 | 0.015142 | -0.008409 | 0.088755 | 0.12857 | 0.25185 | -0.10427 | 0.63291 | 18.6494 | 0.25958 | 121.9961 | 122.2807 | 122.142 | -0.17788 | -0.063069 | -122.1021 | 0.019355 | 0.03279 | 0.095859 | -122.0623 | -121.939 | -0.13669 | -0.19476 | 0.67411 | 0.30078 | 0.43746 | 0.089851 | -0.048884 | 0.12995 | 0.16977 | 0.29305 | 0.056341 | -122.2951 | 122.0373 | 122.3219 | 122.1832 | 18.6906 | -122.3687
4631.6875 | 122.3419 | -0.082397 | 122.2046 | -0.01778 | -0.059512 | 0.038584 | 0.015195 | -0.014642 | -0.0084995 | -0.021518 | -0.0024804 | -0.0018631 | 0.056978 | 0.052012 | 0.045765 | -0.017266 | 0.0243 | -0.012988 | 0.084176 | 0.12399 | 0.24269 | -0.09511 | 0.63749 | 18.8097 | 0.25958 | 121.9961 | 122.2899 | 122.142 | -0.18704 | -0.012713 | -122.1204 | 0.065131 | 0.069409 | 0.082122 | -122.0806 | -121.9619 | -0.10465 | -0.20849 | 0.71989 | 0.34198 | 0.44662 | 0.085275 | -0.062617 | 0.16657 | 0.20639 | 0.32509 | 0.1067 | -122.2997 | 122.0785 | 122.3723 | 122.2244 | 18.8921 | -122.3916
4633.4375 | 122.3602 | -0.091553 | 122.2137 | -0.025411 | -0.059726 | 0.03837 | 0.015195 | -0.014429 | -0.0084995 | -0.013887 | -0.002053 | -0.0014357 | 0.056978 | 0.052012 | 0.045551 | -0.021844 | 0.0243 | -0.008409 | 0.088755 | 0.13773 | 0.23812 | -0.099689 | 0.65122 | 18.9562 | 0.27332 | 121.9915 | 122.2761 | 122.142 | -0.18246 | -0.008136 | -122.125 | 0.069709 | 0.083144 | 0.09128 | -122.076 | -121.9756 | -0.090911 | -0.22222 | 0.74278 | 0.36487 | 0.45578 | 0.062385 | -0.071772 | 0.18031 | 0.22928 | 0.32967 | 0.11585 | -122.3134 | 122.0831 | 122.3677 | 122.2335 | 19.0478 | -122.3962
4635.2031 | 122.319 | -0.15564 | 122.1405 | -0.01778 | -0.059299 | 0.038157 | 0.015195 | -0.014215 | -0.0080721 | -0.029148 | -0.0024804 | -0.0014357 | 0.057405 | 0.052226 | 0.045551 | -0.008109 | 0.028878 | 0.005325 | 0.084176 | 0.13315 | 0.25185 | -0.118 | 0.66954 | 19.1211 | 0.29163 | 121.9961 | 122.2853 | 122.142 | -0.17788 | 0.037636 | -122.0563 | 0.14753 | 0.16096 | 0.12333 | -122.0074 | -121.8887 | -0.022245 | -0.1444 | 0.82518 | 0.44727 | 0.46952 | 0.14478 | 0.00147 | 0.23982 | 0.28879 | 0.40749 | 0.18452 | -122.2585 | 122.1517 | 122.4409 | 122.2976 | 19.2767 | -122.3184
4636.9062 | 122.374 | -0.52643 | 121.7468 | -0.01778 | -0.059512 | 0.038157 | 0.015195 | -0.014429 | -0.0078585 | -0.029148 | -0.0024804 | -0.0014357 | 0.057191 | 0.052226 | 0.045978 | -0.031001 | 0.010564 | -0.017566 | 0.042971 | 0.11025 | 0.23354 | -0.17295 | 0.66496 | 19.2676 | 0.2779 | 121.9732 | 122.2624 | 122.1237 | -0.18704 | 0.35348 | -121.7039 | 0.49543 | 0.50886 | 0.15538 | -121.6366 | -121.5133 | 0.33939 | 0.22638 | 1.1914 | 0.80432 | 0.46494 | 0.51557 | 0.37683 | 0.5694 | 0.63668 | 0.75997 | 0.53699 | -121.9198 | 122.4996 | 122.7888 | 122.6501 | 19.794 | -121.9339
4638.6719 | 122.2412 | -0.29755 | 121.9894 | -0.010149 | -0.059512 | 0.03837 | 0.015409 | -0.014642 | -0.0078585 | -0.029148 | -0.0024804 | -0.0010085 | 0.057191 | 0.052012 | 0.045765 | -0.03558 | 0.015142 | -0.022144 | 0.047549 | 0.11483 | 0.22438 | -0.19127 | 0.67412 | 19.4324 | 0.28247 | 121.9732 | 122.2624 | 122.1282 | -0.1962 | 0.10628 | -121.9419 | 0.26197 | 0.2754 | 0.16912 | -121.8746 | -121.7651 | 0.10135 | -0.016234 | 0.97166 | 0.58002 | 0.47867 | 0.27295 | 0.1388 | 0.34509 | 0.41238 | 0.52193 | 0.31269 | -122.1807 | 122.2708 | 122.5599 | 122.4258 | 19.7299 | -122.1856
4640.375 | 122.3923 | -0.78735 | 121.4813 | -0.010149 | -0.059726 | 0.03837 | 0.015195 | -0.014429 | -0.0076449 | -0.021518 | -0.0022666 | -0.0010085 | 0.057405 | 0.051799 | 0.045978 | -0.031001 | 0.015142 | -0.022144 | 0.052128 | 0.12399 | 0.24269 | -0.17295 | 0.69243 | 19.5927 | 0.29621 | 121.9778 | 122.267 | 122.1282 | -0.18704 | 0.6144 | -121.4292 | 0.75635 | 0.76521 | 0.15081 | -121.3573 | -121.2386 | 0.60031 | 0.49646 | 1.4798 | 1.0836 | 0.48325 | 0.78565 | 0.64691 | 0.83948 | 0.91134 | 1.03 | 0.8025 | -121.6543 | 122.7651 | 123.0543 | 122.9156 | 20.38 | -121.6684
4642.1406 | 122.4152 | 0.16937 | 122.4564 | -0.01778 | -0.059726 | 0.038157 | 0.015195 | -0.014429 | -0.0070039 | -0.013887 | -0.002053 | -0.00079471 | 0.056978 | 0.052012 | 0.045551 | -0.026423 | 0.0243 | -0.012988 | 0.052128 | 0.12857 | 0.23812 | -0.20958 | 0.70159 | 19.7254 | 0.30079 | 121.9732 | 122.2716 | 122.1282 | -0.18704 | -0.37896 | -122.4042 | -0.1958 | -0.18236 | 0.19659 | -122.3278 | -122.2182 | -0.35642 | -0.48315 | 0.53222 | 0.13142 | 0.48783 | -0.18481 | -0.32812 | -0.11724 | -0.040804 | 0.068744 | -0.14507 | -122.6659 | 121.8038 | 122.1022 | 121.9589 | 19.5561 | -122.6434
4643.8438 | 122.3007 | -0.84686 | 121.4447 | -0.010149 | -0.059726 | 0.038157 | 0.014981 | -0.014642 | -0.0074311 | -0.013887 | -0.002053 | -0.0014357 | 0.056978 | 0.052012 | 0.045978 | -0.026423 | 0.019721 | -0.008409 | 0.042971 | 0.11941 | 0.24269 | -0.16379 | 0.72448 | 19.8124 | 0.31452 | 121.9824 | 122.2716 | 122.1374 | -0.1962 | 0.68307 | -121.4017 | 0.82044 | 0.83845 | 0.15538 | -121.3253 | -121.202 | 0.65066 | 0.53766 | 1.5713 | 1.1614 | 0.51072 | 0.82685 | 0.69269 | 0.88983 | 0.96627 | 1.0896 | 0.86658 | -121.6085 | 122.8292 | 123.1184 | 122.9843 | 20.6593 | -121.6409
4645.6094 | 122.2641 | -0.52643 | 121.7056 | -0.01778 | -0.059512 | 0.038584 | 0.014981 | -0.014642 | -0.0070039 | -0.021518 | -0.0024804 | -0.0014357 | 0.057405 | 0.052012 | 0.045765 | -0.021844 | 0.028878 | -0.008409 | 0.065863 | 0.11941 | 0.24269 | -0.15464 | 0.7428 | 19.991 | 0.33742 | 121.9915 | 122.2761 | 122.142 | -0.17788 | 0.37179 | -121.6398 | 0.50458 | 0.51802 | 0.14623 | -121.5862 | -121.4629 | 0.34854 | 0.28589 | 1.2692 | 0.86385 | 0.5153 | 0.5705 | 0.43635 | 0.59229 | 0.64584 | 0.76912 | 0.55531 | -121.8603 | 122.5179 | 122.8026 | 122.6684 | 20.5174 | -121.8835
4647.375 | 122.3694 | -0.6958 | 121.5454 | -0.025411 | -0.059726 | 0.03837 | 0.014981 | -0.014215 | -0.0061491 | -0.029148 | -0.0022666 | -0.0014357 | 0.056978 | 0.052226 | 0.045765 | -0.017266 | 0.033457 | 0.000747 | 0.065863 | 0.13315 | 0.25185 | -0.16837 | 0.76111 | 20.1055 | 0.33284 | 121.9915 | 122.2716 | 122.142 | -0.17788 | 0.52743 | -121.4795 | 0.67853 | 0.69655 | 0.16912 | -121.4123 | -121.2936 | 0.51792 | 0.44611 | 1.4569 | 1.0286 | 0.51072 | 0.72614 | 0.59656 | 0.76166 | 0.82895 | 0.94765 | 0.72926 | -121.7138 | 122.6873 | 122.9674 | 122.8378 | 20.8013 | -121.7233
4649.125 | 122.2641 | -0.082397 | 122.2366 | -0.010149 | -0.059512 | 0.03837 | 0.015195 | -0.014642 | -0.0057219 | -0.021518 | -0.0022666 | -0.0016495 | 0.057191 | 0.052226 | 0.045765 | -0.044736 | -0.016908 | -0.035879 | 0.042971 | 0.10567 | 0.2198 | -0.15464 | 0.73822 | 20.2291 | 0.31452 | 121.9549 | 122.2487 | 122.1008 | -0.20536 | -0.072239 | -122.1937 | 0.037661 | 0.046518 | 0.11876 | -122.131 | -122.0168 | -0.12296 | -0.28174 | 0.82062 | 0.39692 | 0.51988 | 0.012025 | -0.13587 | 0.12537 | 0.18807 | 0.3022 | 0.065489 | -122.3913 | 122.0373 | 122.3311 | 122.1832 | 20.3115 | -122.442
4650.8438 | 122.319 | 0.3479 | 122.6303 | 0.0051128 | -0.059512 | 0.038157 | 0.015409 | -0.014856 | -0.0055083 | -0.021518 | -0.002053 | -0.0012221 | 0.057405 | 0.05244 | 0.045978 | -0.095099 | -0.048958 | -0.081662 | 0.006344 | 0.055306 | 0.17402 | -0.20042 | 0.71075 | 20.3573 | 0.2779 | 121.9137 | 122.1983 | 122.0596 | -0.25115 | -0.54832 | -122.624 | -0.443 | -0.42956 | 0.11876 | -122.575 | -122.4563 | -0.59905 | -0.71662 | 0.36285 | -0.070005 | 0.52904 | -0.43202 | -0.57075 | -0.34156 | -0.29259 | -0.17388 | -0.39686 | -122.8307 | 121.5658 | 121.8504 | 121.7117 | 20.0094 | -122.8815
4652.6094 | 122.406 | -0.49896 | 121.6873 | -0.01778 | -0.05994 | 0.03837 | 0.014981 | -0.014429 | -0.0052945 | -0.021518 | -0.0018394 | -0.0014357 | 0.057405 | 0.052012 | 0.045978 | -0.026423 | 0.019721 | -0.008409 | 0.061284 | 0.13315 | 0.24727 | -0.13174 | 0.79316 | 20.5221 | 0.36031 | 121.9824 | 122.2761 | 122.1282 | -0.18246 | 0.36722 | -121.626 | 0.47254 | 0.49055 | 0.12333 | -121.5542 | -121.44 | 0.3165 | 0.29505 | 1.2921 | 0.85927 | 0.54278 | 0.58881 | 0.44092 | 0.56025 | 0.63211 | 0.74624 | 0.51868 | -121.8191 | 122.4813 | 122.7751 | 122.6272 | 21.0211 | -121.8698
4654.3594 | 122.4152 | -0.064087 | 122.1359 | -0.010149 | -0.059726 | 0.03837 | 0.015195 | -0.014215 | -0.0046535 | -0.029148 | -0.0024804 | -0.0012221 | 0.057191 | 0.052012 | 0.045978 | -0.044736 | -0.012329 | -0.040457 | 0.029236 | 0.096516 | 0.21064 | -0.16379 | 0.77943 | 20.6 | 0.33742 | 121.9549 | 122.2395 | 122.0916 | -0.20994 | -0.099707 | -122.1067 | 0.019351 | 0.02363 | 0.12334 | -122.0394 | -121.9253 | -0.14585 | -0.18103 | 0.84352 | 0.40151 | 0.54736 | 0.10358 | -0.044317 | 0.093323 | 0.1606 | 0.27473 | 0.051758 | -122.2997 | 122.019 | 122.3036 | 122.1557 | 20.6641 | -122.3459
4656.0625 | 122.3145 | 0.091553 | 122.3648 | -0.010149 | -0.059512 | 0.038584 | 0.014981 | -0.014642 | -0.0042263 | -0.021518 | -0.0024804 | -0.0014357 | 0.057405 | 0.052226 | 0.046192 | -0.03558 | 0.005985 | -0.026723 | 0.061284 | 0.11025 | 0.22896 | -0.15464 | 0.79774 | 20.7053 | 0.36947 | 121.9686 | 122.2578 | 122.1008 | -0.1962 | -0.24619 | -122.3035 | -0.12713 | -0.11828 | 0.12791 | -122.2546 | -122.1358 | -0.28775 | -0.39618 | 0.70619 | 0.27792 | 0.56567 | -0.10699 | -0.26404 | -0.030269 | 0.0187 | 0.13741 | -0.085568 | -122.5194 | 121.8771 | 122.1663 | 122.0092 | 20.6137 | -122.561
4657.8281 | 122.3465 | 0.33417 | 122.5983 | -0.010149 | -0.059726 | 0.038157 | 0.015195 | -0.014429 | -0.0040125 | -0.029148 | -0.002053 | -0.0012221 | 0.057191 | 0.052226 | 0.045765 | -0.044736 | 0.005985 | -0.022144 | 0.038393 | 0.11025 | 0.22438 | -0.15464 | 0.82522 | 20.8335 | 0.36947 | 121.9641 | 122.2487 | 122.1191 | -0.20536 | -0.4888 | -122.5599 | -0.3789 | -0.35631 | 0.13249 | -122.488 | -122.3739 | -0.53953 | -0.63422 | 0.49105 | 0.035302 | 0.57483 | -0.34961 | -0.47919 | -0.29577 | -0.22391 | -0.10979 | -0.32818 | -122.7529 | 121.6299 | 121.9145 | 121.7849 | 20.4993 | -122.8036
4659.5938 | 122.4152 | -0.25177 | 122.0398 | -0.010149 | -0.060153 | 0.03837 | 0.014768 | -0.014856 | -0.0031579 | -0.029148 | -0.0022666 | -0.0012221 | 0.057405 | 0.05244 | 0.045978 | -0.076785 | -0.021486 | -0.054192 | 0.029236 | 0.091937 | 0.19691 | -0.16379 | 0.81606 | 20.948 | 0.36031 | 121.9412 | 122.2258 | 122.087 | -0.2191 | 0.087976 | -122.0106 | 0.17499 | 0.19758 | 0.1096 | -121.9479 | -121.8429 | 0.032675 | -0.098638 | 1.0678 | 0.61208 | 0.57941 | 0.18597 | 0.047235 | 0.28101 | 0.34371 | 0.44868 | 0.23028 | -122.2036 | 122.1929 | 122.4775 | 122.3388 | 21.1997 | -122.2589
4661.2969 | 122.3511 | 0.018311 | 122.2733 | -0.01778 | -0.059512 | 0.03837 | 0.015409 | -0.014429 | -0.0029443 | -0.021518 | -0.0024804 | -0.0010085 | 0.057405 | 0.05244 | 0.045765 | -0.026423 | 0.019721 | -0.012988 | 0.065863 | 0.12857 | 0.24269 | -0.13632 | 0.86184 | 21.0578 | 0.39236 | 121.9686 | 122.2761 | 122.1191 | -0.18704 | -0.15463 | -122.2074 | -0.044734 | -0.031299 | 0.12333 | -122.1447 | -122.0306 | -0.20535 | -0.30463 | 0.84353 | 0.37405 | 0.5794 | 0.002876 | -0.15417 | 0.047552 | 0.11026 | 0.22438 | 0.00141 | -122.4096 | 121.9503 | 122.2578 | 122.1008 | 21.0395 | -122.4603
4663 | 122.4976 | 0.032043 | 122.2504 | -0.01778 | -0.059512 | 0.03837 | 0.015409 | -0.014215 | -0.0023033 | -0.029148 | -0.0024804 | -0.0010085 | 0.057405 | 0.052012 | 0.045765 | -0.026423 | 0.019721 | -0.008409 | 0.061284 | 0.12857 | 0.25185 | -0.13174 | 0.88474 | 21.2318 | 0.41526 | 121.9732 | 122.2716 | 122.1237 | -0.17788 | -0.16378 | -122.1891 | -0.058466 | -0.040452 | 0.12333 | -122.1218 | -121.9985 | -0.20993 | -0.27716 | 0.8527 | 0.38321 | 0.59314 | 0.021185 | -0.12671 | 0.029241 | 0.096526 | 0.21981 | -0.012322 | -122.3821 | 121.9412 | 122.2395 | 122.0916 | 21.1998 | -122.4283
4664.7656 | 122.3282 | 0.63629 | 122.937 | -0.0025182 | -0.059512 | 0.03837 | 0.015195 | -0.014642 | -0.0027305 | -0.036779 | -0.0022666 | -0.0014357 | 0.057191 | 0.052012 | 0.046192 | -0.021844 | 0.019721 | -0.017566 | 0.056706 | 0.12399 | 0.24269 | -0.18211 | 0.90305 | 21.3097 | 0.42441 | 121.9824 | 122.2624 | 122.1237 | -0.1962 | -0.8184 | -122.8803 | -0.65814 | -0.65386 | 0.16454 | -122.813 | -122.6943 | -0.83249 | -0.95465 | 0.26676 | -0.21188 | 0.62061 | -0.67462 | -0.81335 | -0.57959 | -0.5123 | -0.3936 | -0.61657 | -123.1191 | 121.3461 | 121.6261 | 121.4874 | 20.6734 | -123.1332
4666.5469 | 122.2549 | -0.51727 | 121.7422 | -0.0025182 | -0.059726 | 0.038584 | 0.014768 | -0.014429 | -0.0020895 | -0.021518 | -0.0022666 | -0.0012221 | 0.057191 | 0.05244 | 0.045978 | -0.026423 | 0.015142 | -0.017566 | 0.052128 | 0.11941 | 0.23812 | -0.18211 | 0.91221 | 21.3921 | 0.43815 | 121.9778 | 122.2624 | 122.1282 | -0.17788 | 0.33516 | -121.6901 | 0.49085 | 0.49971 | 0.16454 | -121.6228 | -121.5041 | 0.33939 | 0.23554 | 1.4295 | 0.95542 | 0.61603 | 0.52014 | 0.38599 | 0.5694 | 0.63668 | 0.75539 | 0.53241 | -121.9244 | 122.4951 | 122.7797 | 122.6455 | 21.9094 | -121.9201
4668.3125 | 122.3145 | 0.7782 | 123.1338 | -0.01778 | -0.059726 | 0.038157 | 0.015409 | -0.014642 | -0.0018759 | -0.029148 | -0.002053 | -0.0010085 | 0.057405 | 0.052226 | 0.045978 | -0.040158 | 0.015142 | -0.017566 | 0.042971 | 0.11941 | 0.22896 | -0.18211 | 0.92137 | 21.5157 | 0.43357 | 121.9595 | 122.2578 | 122.1053 | -0.1962 | -0.96031 | -123.0909 | -0.81836 | -0.79576 | 0.16454 | -123.0144 | -122.9049 | -0.9744 | -1.1744 | 0.14317 | -0.34463 | 0.62977 | -0.87604 | -1.0285 | -0.73523 | -0.65879 | -0.54924 | -0.76306 | -123.316 | 121.1813 | 121.4796 | 121.3271 | 20.7375 | -123.33
4670.0156 | 122.287 | -0.13733 | 122.1725 | -0.01778 | -0.059726 | 0.03837 | 0.015195 | -0.014642 | -0.0016623 | -0.029148 | -0.002053 | -0.0010085 | 0.057405 | 0.05244 | 0.046406 | -0.058472 | -0.012329 | -0.045036 | 0.052128 | 0.091937 | 0.21064 | -0.13174 | 0.91221 | 21.6302 | 0.42441 | 121.9457 | 122.2303 | 122.0916 | -0.2191 | 0.005588 | -122.1204 | 0.078857 | 0.092293 | 0.086705 | -122.0806 | -121.9619 | -0.081766 | -0.22681 | 1.0495 | 0.56174 | 0.64351 | 0.057798 | -0.080938 | 0.18946 | 0.22927 | 0.34797 | 0.125 | -122.3043 | 122.0831 | 122.3677 | 122.2289 | 21.7675 | -122.3916
4671.7812 | 122.3831 | -0.082397 | 122.1222 | -0.01778 | -0.059726 | 0.03837 | 0.015195 | -0.014429 | -0.0012349 | -0.029148 | -0.002053 | -0.0012221 | 0.057191 | 0.052226 | 0.045978 | -0.058472 | -0.003172 | -0.035879 | 0.056706 | 0.091937 | 0.21522 | -0.13632 | 0.93053 | 21.7355 | 0.43815 | 121.9412 | 122.2212 | 122.087 | -0.22367 | -0.053923 | -122.0655 | 0.023925 | 0.046518 | 0.10044 | -122.0303 | -121.907 | -0.14128 | -0.18103 | 1.0129 | 0.52055 | 0.66182 | 0.098994 | -0.035162 | 0.1391 | 0.17433 | 0.29762 | 0.079225 | -122.2585 | 122.0236 | 122.3036 | 122.1694 | 21.8179 | -122.3459
4673.5469 | 122.2595 | -0.13275 | 122.1909 | 0.0051128 | -0.059512 | 0.038157 | 0.015195 | -0.014642 | -0.00080773 | -0.021518 | -0.002053 | -0.0012221 | 0.057619 | 0.052226 | 0.045765 | -0.058472 | 0.001407 | -0.045036 | 0.056706 | 0.096516 | 0.21522 | -0.12716 | 0.95342 | 21.9049 | 0.43815 | 121.9412 | 122.2258 | 122.0916 | -0.21452 | 0.005589 | -122.1342 | 0.074279 | 0.087715 | 0.082126 | -122.0943 | -121.9756 | -0.081765 | -0.2497 | 1.0862 | 0.5709 | 0.65267 | 0.034908 | -0.099249 | 0.18946 | 0.22927 | 0.34798 | 0.13416 | -122.318 | 122.0739 | 122.3585 | 122.2244 | 22.0377 | -122.4054
4675.25 | 122.4243 | -0.086975 | 122.113 | -0.01778 | -0.059726 | 0.03837 | 0.014981 | -0.014642 | -0.00016673 | -0.036779 | -0.0018394 | -0.00058111 | 0.057405 | 0.05244 | 0.046192 | -0.058472 | -0.012329 | -0.045036 | 0.047549 | 0.091937 | 0.2198 | -0.13632 | 0.96258 | 21.9507 | 0.45189 | 121.9366 | 122.2303 | 122.0825 | -0.22367 | -0.049345 | -122.0655 | 0.028503 | 0.041939 | 0.091284 | -122.0211 | -121.8932 | -0.1367 | -0.17646 | 1.0496 | 0.53886 | 0.67556 | 0.11731 | -0.030586 | 0.13452 | 0.17891 | 0.30678 | 0.074646 | -122.2494 | 122.0236 | 122.3173 | 122.1694 | 22.0377 | -122.3367
4676.9688 | 122.3373 | -0.091553 | 122.1497 | -0.0025182 | -0.059512 | 0.038584 | 0.015195 | -0.014429 | -0.00016673 | -0.021518 | -0.002053 | -0.0010085 | 0.057405 | 0.052226 | 0.045978 | -0.058472 | -0.003172 | -0.045036 | 0.052128 | 0.096516 | 0.21064 | -0.13174 | 0.98089 | 22.056 | 0.46562 | 121.9274 | 122.2303 | 122.0916 | -0.22367 | -0.040188 | -122.0975 | 0.033081 | 0.046517 | 0.086705 | -122.0531 | -121.939 | -0.13212 | -0.22224 | 1.0724 | 0.55717 | 0.68929 | 0.080686 | -0.05805 | 0.14368 | 0.18807 | 0.3022 | 0.088381 | -122.2814 | 122.019 | 122.3219 | 122.1832 | 22.1476 | -122.3733
4678.7344 | 122.3419 | -0.091553 | 122.1405 | -0.01778 | -0.05994 | 0.038584 | 0.015195 | -0.014642 | 0.00026067 | -0.013887 | -0.002053 | -0.0010085 | 0.057191 | 0.052653 | 0.046192 | -0.053893 | -0.003172 | -0.045036 | 0.056706 | 0.096516 | 0.21522 | -0.13632 | 0.99921 | 22.1613 | 0.47478 | 121.9366 | 122.2303 | 122.087 | -0.2191 | -0.044767 | -122.0838 | 0.03766 | 0.046517 | 0.091284 | -122.044 | -121.9253 | -0.12754 | -0.20392 | 1.0908 | 0.56633 | 0.69387 | 0.089841 | -0.053473 | 0.14826 | 0.18807 | 0.30678 | 0.088381 | -122.2768 | 122.0281 | 122.3219 | 122.1786 | 22.2529 | -122.3596
4680.5 | 122.3145 | -0.10529 | 122.1634 | -0.010149 | -0.059512 | 0.038584 | 0.015195 | -0.014642 | 0.00068807 | -0.021518 | -0.002053 | -0.0010085 | 0.057191 | 0.052653 | 0.045765 | -0.044736 | -0.003172 | -0.040457 | 0.056706 | 0.1011 | 0.21064 | -0.13174 | 1.0175 | 22.2666 | 0.48851 | 121.9412 | 122.2258 | 122.087 | -0.21452 | -0.026455 | -122.1067 | 0.06055 | 0.064829 | 0.091284 | -122.0623 | -121.9527 | -0.10923 | -0.22223 | 1.1228 | 0.5938 | 0.70303 | 0.062374 | -0.076361 | 0.16199 | 0.20638 | 0.31593 | 0.10211 | -122.2951 | 122.0464 | 122.3311 | 122.1923 | 22.3719 | -122.3779
4682.2812 | 122.3969 | -0.073242 | 122.1313 | -0.025411 | -0.059726 | 0.03837 | 0.015409 | -0.014429 | 0.0013291 | -0.036779 | -0.0024804 | -0.0012221 | 0.057405 | 0.052653 | 0.045978 | -0.053893 | -0.007751 | -0.035879 | 0.056706 | 0.1011 | 0.21522 | -0.13632 | 1.0313 | 22.2666 | 0.49309 | 121.9412 | 122.2303 | 122.0825 | -0.21452 | -0.063078 | -122.0746 | 0.019349 | 0.037363 | 0.10044 | -122.0303 | -121.9161 | -0.14127 | -0.19019 | 1.1045 | 0.56634 | 0.70761 | 0.098996 | -0.048897 | 0.12995 | 0.17434 | 0.28847 | 0.065491 | -122.2677 | 122.0144 | 122.3036 | 122.1557 | 22.3399 | -122.3459
4684.0469 | 122.406 | -0.091553 | 122.1359 | -0.01778 | -0.05994 | 0.038584 | 0.015195 | -0.014642 | 0.0013291 | -0.021518 | -0.002053 | -0.0010085 | 0.057832 | 0.052226 | 0.046192 | -0.049315 | -0.007751 | -0.035879 | 0.056706 | 0.10567 | 0.21522 | -0.13632 | 1.0542 | 22.404 | 0.50225 | 121.9366 | 122.2212 | 122.0825 | -0.20994 | -0.044767 | -122.0792 | 0.042238 | 0.055674 | 0.10044 | -122.0303 | -121.9207 | -0.11838 | -0.19935 | 1.1457 | 0.59381 | 0.71219 | 0.085261 | -0.053474 | 0.14826 | 0.19723 | 0.30678 | 0.083802 | -122.2722 | 122.0281 | 122.3127 | 122.174 | 22.4955 | -122.3459
4685.7656 | 122.3465 | -0.09613 | 122.1405 | -0.010149 | -0.05994 | 0.03837 | 0.015195 | -0.014642 | 0.0015427 | -0.021518 | -0.0022666 | -0.00058111 | 0.057191 | 0.052226 | 0.045978 | -0.053893 | -0.007751 | -0.040457 | 0.056706 | 0.096516 | 0.2198 | -0.1409 | 1.0679 | 22.5185 | 0.51599 | 121.932 | 122.2258 | 122.087 | -0.2191 | -0.044769 | -122.0838 | 0.042237 | 0.055673 | 0.10044 | -122.044 | -121.9207 | -0.12297 | -0.2085 | 1.164 | 0.61212 | 0.73508 | 0.085262 | -0.053473 | 0.15284 | 0.19265 | 0.31593 | 0.088379 | -122.2814 | 122.0281 | 122.3219 | 122.1832 | 22.6146 | -122.3596
4687.5469 | 122.3465 | -0.11902 | 122.1359 | -0.01778 | -0.05994 | 0.038157 | 0.014981 | -0.014642 | 0.0019701 | -0.029148 | -0.0016258 | -0.0010085 | 0.057405 | 0.052867 | 0.045978 | -0.053893 | -0.007751 | -0.035879 | 0.061284 | 0.10567 | 0.21522 | -0.13174 | 1.0908 | 22.6283 | 0.52057 | 121.932 | 122.2258 | 122.0779 | -0.2191 | -0.012722 | -122.0746 | 0.065126 | 0.08314 | 0.095862 | -122.0303 | -121.9207 | -0.10008 | -0.20392 | 1.2098 | 0.63958 | 0.73966 | 0.08984 | -0.058053 | 0.1803 | 0.22469 | 0.33424 | 0.11127 | -122.2677 | 122.051 | 122.3448 | 122.1969 | 22.7474 | -122.355
4689.3125 | 122.2504 | -0.1236 | 122.1451 | -0.025411 | -0.05994 | 0.038584 | 0.014981 | -0.014429 | 0.0028247 | -0.021518 | -0.0018394 | -0.0012221 | 0.057405 | 0.052653 | 0.046192 | -0.058472 | -0.007751 | -0.040457 | 0.056706 | 0.1011 | 0.22438 | -0.13174 | 1.1137 | 22.7428 | 0.54346 | 121.932 | 122.2212 | 122.087 | -0.2191 | -0.008145 | -122.0884 | 0.065124 | 0.083139 | 0.091284 | -122.044 | -121.9207 | -0.095499 | -0.21308 | 1.2373 | 0.66706 | 0.76256 | 0.076105 | -0.058051 | 0.1803 | 0.22469 | 0.34798 | 0.11585 | -122.2768 | 122.0556 | 122.3448 | 122.2106 | 22.8664 | -122.3642
4691.0156 | 122.3099 | -0.12817 | 122.1588 | -0.0025182 | -0.059726 | 0.038798 | 0.015409 | -0.014856 | 0.0030383 | -0.021518 | -0.0022666 | -0.0012221 | 0.057619 | 0.05244 | 0.045765 | -0.049315 | -0.003172 | -0.031301 | 0.056706 | 0.1011 | 0.2198 | -0.13632 | 1.1274 | 22.6558 | 0.5343 | 121.9274 | 122.2212 | 122.0825 | -0.2191 | -0.008146 | -122.1021 | 0.078859 | 0.096873 | 0.10502 | -122.0577 | -121.939 | -0.090921 | -0.23139 | 1.2556 | 0.66248 | 0.7534 | 0.062373 | -0.076362 | 0.18488 | 0.22927 | 0.34798 | 0.125 | -122.2951 | 122.0556 | 122.3494 | 122.2106 | 22.784 | -122.3779
4692.7812 | 122.3648 | -0.10986 | 122.1313 | -0.01778 | -0.060153 | 0.03837 | 0.014981 | -0.014429 | 0.0036793 | -0.021518 | -0.0018394 | -0.00079471 | 0.057832 | 0.05244 | 0.046192 | -0.049315 | -0.007751 | -0.045036 | 0.052128 | 0.096516 | 0.21522 | -0.13174 | 1.1366 | 22.6375 | 0.5343 | 121.932 | 122.2166 | 122.0733 | -0.21452 | -0.021878 | -122.0792 | 0.060548 | 0.064827 | 0.086705 | -122.0348 | -121.9161 | -0.10465 | -0.19935 | 1.2464 | 0.64417 | 0.74882 | 0.08526 | -0.058054 | 0.16199 | 0.20638 | 0.32509 | 0.10211 | -122.2631 | 122.0419 | 122.3265 | 122.1832 | 22.7474 | -122.3459
4694.5469 | 122.2366 | -0.14191 | 122.1497 | -0.01778 | -0.059512 | 0.037943 | 0.014981 | -0.014429 | 0.0038929 | -0.013887 | -0.0018394 | -0.00079471 | 0.057619 | 0.05244 | 0.046192 | -0.049315 | -0.012329 | -0.035879 | 0.061284 | 0.1011 | 0.2198 | -0.13632 | 1.1411 | 22.6924 | 0.5572 | 121.932 | 122.2258 | 122.0779 | -0.2191 | 0.005587 | -122.0884 | 0.092592 | 0.10603 | 0.10044 | -122.0486 | -121.9299 | -0.077188 | -0.21766 | 1.2831 | 0.6991 | 0.77629 | 0.076107 | -0.071786 | 0.20319 | 0.243 | 0.36171 | 0.12958 | -122.286 | 122.0739 | 122.3677 | 122.2198 | 22.8344 | -122.3688
4696.3125 | 122.3007 | -0.1236 | 122.1451 | -0.010149 | -0.060367 | 0.03837 | 0.014768 | -0.014856 | 0.0043203 | -0.013887 | -0.002053 | -0.0010085 | 0.057619 | 0.052226 | 0.045978 | -0.053893 | -0.003172 | -0.045036 | 0.047549 | 0.096516 | 0.2198 | -0.1409 | 1.164 | 22.7382 | 0.5572 | 121.932 | 122.2212 | 122.0825 | -0.22367 | -0.017303 | -122.0975 | 0.069703 | 0.07856 | 0.095863 | -122.0486 | -121.9253 | -0.10008 | -0.21308 | 1.2876 | 0.68079 | 0.78087 | 0.076105 | -0.06263 | 0.17114 | 0.22011 | 0.3434 | 0.12042 | -122.286 | 122.0556 | 122.3448 | 122.206 | 22.8618 | -122.3688
4698.0781 | 122.2641 | -0.14191 | 122.1588 | -0.0025182 | -0.060153 | 0.037943 | 0.015195 | -0.014642 | 0.0051749 | -0.013887 | -0.0018394 | -0.0010085 | 0.057405 | 0.05244 | 0.046192 | -0.049315 | -0.012329 | -0.049614 | 0.065863 | 0.096516 | 0.21522 | -0.13632 | 1.1824 | 22.8344 | 0.56178 | 121.9274 | 122.212 | 122.0733 | -0.21452 | 0.005587 | -122.093 | 0.092592 | 0.092293 | 0.086706 | -122.0623 | -121.9436 | -0.072609 | -0.23139 | 1.3243 | 0.70368 | 0.77629 | 0.053216 | -0.085519 | 0.20777 | 0.23842 | 0.35713 | 0.12958 | -122.2951 | 122.0693 | 122.3539 | 122.2152 | 22.9763 | -122.3733
4699.7812 | 122.3465 | -0.10071 | 122.113 | -0.0025182 | -0.059726 | 0.03837 | 0.015195 | -0.014642 | 0.0051749 | -0.021518 | -0.0018394 | -0.0012221 | 0.057405 | 0.052653 | 0.046192 | -0.058472 | -0.007751 | -0.045036 | 0.056706 | 0.1011 | 0.21522 | -0.1409 | 1.2052 | 22.871 | 0.57551 | 121.9274 | 122.212 | 122.0733 | -0.20994 | -0.040191 | -122.0563 | 0.042236 | 0.055672 | 0.095863 | -122.0119 | -121.8978 | -0.10923 | -0.18561 | 1.306 | 0.67622 | 0.78545 | 0.098992 | -0.039743 | 0.15741 | 0.2018 | 0.31593 | 0.092957 | -122.2539 | 122.0281 | 122.3127 | 122.174 | 22.9717 | -122.323
4701.5469 | 122.374 | -0.091553 | 122.1085 | -0.01778 | -0.059726 | 0.038584 | 0.014768 | -0.014642 | 0.0058159 | -0.021518 | -0.0022666 | -0.0010085 | 0.057405 | 0.05244 | 0.046192 | -0.049315 | -0.016908 | -0.040457 | 0.052128 | 0.096516 | 0.21522 | -0.1409 | 1.2144 | 22.9443 | 0.58009 | 121.9228 | 122.2166 | 122.0687 | -0.21452 | -0.049346 | -122.0563 | 0.042238 | 0.051096 | 0.10044 | -122.0119 | -121.8932 | -0.12296 | -0.18562 | 1.306 | 0.67164 | 0.79461 | 0.10815 | -0.039744 | 0.14368 | 0.18807 | 0.30678 | 0.074645 | -122.2494 | 122.0144 | 122.3082 | 122.1603 | 23.0358 | -122.323
4703.3125 | 122.2458 | -0.14191 | 122.1817 | -0.010149 | -0.05994 | 0.038584 | 0.014981 | -0.014429 | 0.0056023 | -0.029148 | -0.0016258 | -0.0012221 | 0.057619 | 0.05244 | 0.045978 | -0.053893 | -0.003172 | -0.031301 | 0.052128 | 0.096516 | 0.21522 | -0.1409 | 1.2373 | 23.0084 | 0.60298 | 121.9228 | 122.212 | 122.0825 | -0.2191 | 0.001008 | -122.1296 | 0.088014 | 0.11061 | 0.1096 | -122.0852 | -121.9665 | -0.077188 | -0.25886 | 1.3792 | 0.74489 | 0.82208 | 0.030327 | -0.099251 | 0.19404 | 0.23842 | 0.35713 | 0.13873 | -122.3226 | 122.0648 | 122.3539 | 122.2244 | 23.1503 | -122.4008
4705.0781 | 122.3053 | -0.11444 | 122.1451 | -0.025411 | -0.05994 | 0.03837 | 0.015622 | -0.014856 | 0.0062433 | -0.021518 | -0.002053 | -0.00079471 | 0.057405 | 0.052226 | 0.045978 | -0.049315 | -0.003172 | -0.049614 | 0.052128 | 0.096516 | 0.21064 | -0.13632 | 1.2556 | 23.0725 | 0.61672 | 121.9183 | 122.2166 | 122.0733 | -0.2191 | -0.021879 | -122.093 | 0.065126 | 0.064827 | 0.086706 | -122.0486 | -121.9344 | -0.10465 | -0.22682 | 1.3701 | 0.73116 | 0.83581 | 0.071527 | -0.071787 | 0.16657 | 0.21096 | 0.32509 | 0.11127 | -122.2814 | 122.0327 | 122.331 | 122.1877 | 23.1869 | -122.3642
4706.7812 | 122.3511 | -0.086975 | 122.1268 | -0.010149 | -0.060153 | 0.038798 | 0.015409 | -0.014429 | 0.0066705 | -0.029148 | -0.0016258 | -0.00079471 | 0.057405 | 0.052653 | 0.046192 | -0.053893 | -0.003172 | -0.045036 | 0.056706 | 0.096516 | 0.21522 | -0.1409 | 1.2831 | 23.1915 | 0.61672 | 121.9091 | 122.212 | 122.0687 | -0.22367 | -0.053924 | -122.0701 | 0.033082 | 0.041939 | 0.095863 | -122.0303 | -121.9115 | -0.1367 | -0.21766 | 1.3701 | 0.70369 | 0.84039 | 0.085259 | -0.058055 | 0.14368 | 0.18349 | 0.3022 | 0.083803 | -122.2677 | 121.9961 | 122.299 | 122.1557 | 23.2785 | -122.3504
4708.5469 | 122.3145 | -0.11444 | 122.113 | -0.010149 | -0.05994 | 0.03837 | 0.015409 | -0.014642 | 0.0075253 | -0.021518 | -0.0018394 | -0.0010085 | 0.057619 | 0.052226 | 0.046192 | -0.049315 | -0.007751 | -0.035879 | 0.052128 | 0.087359 | 0.21064 | -0.1409 | 1.2922 | 23.1686 | 0.63045 | 121.9183 | 122.2074 | 122.0596 | -0.22367 | -0.026458 | -122.0609 | 0.065126 | 0.078562 | 0.10502 | -122.0257 | -121.9024 | -0.10923 | -0.19477 | 1.4067 | 0.7449 | 0.85413 | 0.094413 | -0.053479 | 0.16657 | 0.2018 | 0.32509 | 0.10669 | -122.2539 | 122.0327 | 122.3219 | 122.174 | 23.2831 | -122.3367
4710.25 | 122.287 | -0.13275 | 122.1497 | -0.010149 | -0.05994 | 0.038584 | 0.015195 | -0.014642 | 0.0090209 | -0.0062567 | -0.002053 | -0.00079471 | 0.057619 | 0.052653 | 0.046192 | -0.06305 | -0.007751 | -0.045036 | 0.061284 | 0.091937 | 0.21522 | -0.13632 | 1.3151 | 23.2098 | 0.63503 | 121.9183 | 122.2029 | 122.0687 | -0.2191 | -0.003569 | -122.0884 | 0.069701 | 0.087715 | 0.091284 | -122.0577 | -121.9344 | -0.086344 | -0.23139 | 1.4479 | 0.76778 | 0.85413 | 0.053214 | -0.080943 | 0.19404 | 0.22469 | 0.34798 | 0.125 | -122.286 | 122.051 | 122.3356 | 122.2015 | 23.3426 | -122.3688
4712.0312 | 122.3694 | -0.086975 | 122.1176 | -0.010149 | -0.060153 | 0.038157 | 0.014981 | -0.014856 | 0.0085935 | -0.036779 | -0.0018394 | -0.00079471 | 0.057405 | 0.052867 | 0.046192 | -0.058472 | -0.007751 | -0.035879 | 0.056706 | 0.1011 | 0.21522 | -0.13632 | 1.3289 | 23.2739 | 0.65335 | 121.9137 | 122.212 | 122.0596 | -0.2191 | -0.049345 | -122.0609 | 0.028503 | 0.051096 | 0.10044 | -122.0165 | -121.9024 | -0.13212 | -0.20393 | 1.4158 | 0.74032 | 0.87244 | 0.094414 | -0.058057 | 0.14368 | 0.18807 | 0.3022 | 0.079224 | -122.2539 | 122.0007 | 122.299 | 122.1465 | 23.3609 | -122.3367
4713.7812 | 122.3785 | -0.11444 | 122.1039 | -0.01778 | -0.059726 | 0.03837 | 0.014981 | -0.014642 | 0.0096619 | -0.021518 | -0.002053 | -0.0010085 | 0.057832 | 0.05244 | 0.045978 | -0.053893 | -0.012329 | -0.040457 | 0.052128 | 0.1011 | 0.21522 | -0.1409 | 1.3472 | 23.3701 | 0.65335 | 121.9137 | 122.2074 | 122.0641 | -0.2191 | -0.026458 | -122.0518 | 0.060548 | 0.073984 | 0.10044 | -122.0028 | -121.8887 | -0.10465 | -0.1902 | 1.4616 | 0.76779 | 0.87244 | 0.10357 | -0.039745 | 0.16657 | 0.21554 | 0.32966 | 0.10211 | -122.2448 | 122.0281 | 122.3219 | 122.1786 | 23.4845 | -122.323
4715.5469 | 122.2549 | -0.13275 | 122.1359 | -0.010149 | -0.060153 | 0.03837 | 0.015195 | -0.014642 | 0.010089 | -0.013887 | -0.002053 | -0.00079471 | 0.057619 | 0.05244 | 0.046192 | -0.044736 | -0.007751 | -0.045036 | 0.065863 | 0.096516 | 0.21064 | -0.1409 | 1.3747 | 23.5945 | 0.67166 | 121.9045 | 122.1983 | 122.0641 | -0.22367 | -0.008148 | -122.0701 | 0.088015 | 0.087715 | 0.095863 | -122.0394 | -121.9253 | -0.090922 | -0.2314 | 1.5074 | 0.80442 | 0.89534 | 0.062368 | -0.071788 | 0.19861 | 0.22927 | 0.3434 | 0.125 | -122.2768 | 122.0373 | 122.331 | 122.1969 | 23.7272 | -122.3596
4717.3438 | 122.3328 | -0.1236 | 122.1176 | -0.010149 | -0.05994 | 0.038798 | 0.014981 | -0.014642 | 0.010516 | -0.013887 | -0.0022666 | -0.00058111 | 0.057619 | 0.053081 | 0.046192 | -0.058472 | -0.012329 | -0.045036 | 0.052128 | 0.1011 | 0.21522 | -0.13632 | 1.3976 | 23.5807 | 0.67624 | 121.9137 | 122.2029 | 122.0596 | -0.22367 | -0.012724 | -122.0655 | 0.065124 | 0.07856 | 0.091284 | -122.0165 | -121.9024 | -0.10008 | -0.20393 | 1.5212 | 0.79984 | 0.89992 | 0.085257 | -0.058057 | 0.17572 | 0.22469 | 0.33882 | 0.11127 | -122.2539 | 122.0373 | 122.3265 | 122.1832 | 23.7043 | -122.3413
4719.1094 | 122.2961 | -0.12817 | 122.113 | -0.0025182 | -0.05994 | 0.038157 | 0.015195 | -0.014429 | 0.011798 | -0.021518 | -0.0018394 | -0.00058111 | 0.057619 | 0.05244 | 0.046192 | -0.049315 | 0.001407 | -0.040457 | 0.047549 | 0.096516 | 0.21522 | -0.1409 | 1.4204 | 23.6494 | 0.68998 | 121.9045 | 122.2029 | 122.0641 | -0.2191 | -0.012725 | -122.0655 | 0.078859 | 0.087717 | 0.10044 | -122.0165 | -121.8978 | -0.090921 | -0.20851 | 1.5486 | 0.81815 | 0.90907 | 0.089835 | -0.0489 | 0.17572 | 0.22469 | 0.3434 | 0.12958 | -122.2539 | 122.0327 | 122.331 | 122.1923 | 23.7776 | -122.3321
4720.8125 | 122.2366 | -0.14648 | 122.1451 | -0.01778 | -0.060153 | 0.038584 | 0.014981 | -0.014429 | 0.012653 | -0.029148 | -0.0014122 | -0.0010085 | 0.057832 | 0.052653 | 0.046406 | -0.058472 | -0.016908 | -0.040457 | 0.056706 | 0.096516 | 0.21064 | -0.13632 | 1.4296 | 23.7227 | 0.70371 | 121.9091 | 122.2074 | 122.0641 | -0.22367 | 0.010164 | -122.0884 | 0.088012 | 0.10603 | 0.095863 | -122.0486 | -121.9344 | -0.077189 | -0.23597 | 1.5761 | 0.8502 | 0.92739 | 0.062369 | -0.080944 | 0.20319 | 0.243 | 0.35713 | 0.12958 | -122.2814 | 122.0556 | 122.3539 | 122.2106 | 23.8691 | -122.3688
4722.6094 | 122.3648 | -0.10529 | 122.1176 | -0.01778 | -0.060153 | 0.038584 | 0.014981 | -0.014429 | 0.012226 | -0.021518 | -0.0018394 | -0.00079471 | 0.057405 | 0.052653 | 0.045978 | -0.053893 | -0.012329 | -0.045036 | 0.052128 | 0.10567 | 0.2198 | -0.13174 | 1.4388 | 23.4662 | 0.71745 | 121.9183 | 122.2029 | 122.0596 | -0.22367 | -0.026455 | -122.0655 | 0.051393 | 0.06025 | 0.086705 | -122.0119 | -121.8978 | -0.11839 | -0.19935 | 1.544 | 0.82274 | 0.94112 | 0.085257 | -0.058057 | 0.15741 | 0.21096 | 0.32509 | 0.092957 | -122.2494 | 122.0236 | 122.3082 | 122.1648 | 23.5715 | -122.3413
4724.3125 | 122.3785 | -0.10071 | 122.0901 | -0.01778 | -0.060153 | 0.03837 | 0.015195 | -0.014429 | 0.012653 | -0.021518 | -0.0016258 | -0.00036751 | 0.057832 | 0.053081 | 0.046406 | -0.053893 | -0.007751 | -0.045036 | 0.052128 | 0.096516 | 0.21064 | -0.13632 | 1.4708 | 23.5075 | 0.72661 | 121.9045 | 122.1983 | 122.0596 | -0.2191 | -0.035612 | -122.038 | 0.046815 | 0.055672 | 0.091284 | -121.9936 | -121.8795 | -0.11839 | -0.18562 | 1.5715 | 0.82732 | 0.9457 | 0.10814 | -0.030591 | 0.15284 | 0.19722 | 0.31135 | 0.092957 | -122.2265 | 122.0052 | 122.299 | 122.1603 | 23.6082 | -122.3092
4726.0781 | 122.2916 | -0.12817 | 122.113 | -0.010149 | -0.060153 | 0.037943 | 0.015195 | -0.014642 | 0.013508 | -0.021518 | -0.0018394 | -0.0010085 | 0.057405 | 0.052867 | 0.046406 | -0.044736 | -0.012329 | -0.045036 | 0.047549 | 0.091937 | 0.21522 | -0.13632 | 1.4846 | 23.5212 | 0.72661 | 121.9045 | 122.1983 | 122.0504 | -0.2191 | -0.008146 | -122.0655 | 0.083438 | 0.083138 | 0.091284 | -122.0211 | -121.8978 | -0.090921 | -0.20851 | 1.6127 | 0.85478 | 0.9457 | 0.085256 | -0.062636 | 0.17572 | 0.22011 | 0.3434 | 0.11585 | -122.2494 | 122.0327 | 122.3265 | 122.1786 | 23.6494 | -122.3321
4727.8594 | 122.2412 | -0.15106 | 122.1542 | -0.010149 | -0.059726 | 0.03837 | 0.014981 | -0.014642 | 0.014362 | -0.021518 | -0.0018394 | -0.00079471 | 0.058046 | 0.052867 | 0.046192 | -0.053893 | -0.012329 | -0.049614 | 0.052128 | 0.091937 | 0.21064 | -0.13632 | 1.4983 | 23.5945 | 0.73577 | 121.9 | 122.1983 | 122.055 | -0.22367 | 0.014742 | -122.1021 | 0.097169 | 0.10145 | 0.086706 | -122.0623 | -121.9436 | -0.072611 | -0.25428 | 1.6493 | 0.88683 | 0.95944 | 0.044057 | -0.099257 | 0.20319 | 0.243 | 0.36171 | 0.13873 | -122.2906 | 122.051 | 122.3494 | 122.206 | 23.7455 | -122.3779
4729.6406 | 122.3236 | -0.10071 | 122.049 | -0.010149 | -0.060367 | 0.03837 | 0.014981 | -0.014429 | 0.015003 | -0.021518 | -0.0016258 | -0.0010085 | 0.057832 | 0.052653 | 0.045978 | -0.06305 | -0.012329 | -0.045036 | 0.056706 | 0.1011 | 0.21522 | -0.14548 | 1.5258 | 23.7181 | 0.75866 | 121.9045 | 122.1937 | 122.0504 | -0.22825 | -0.04477 | -121.9922 | 0.037658 | 0.055672 | 0.10044 | -121.9479 | -121.8337 | -0.12754 | -0.14442 | 1.6265 | 0.85937 | 0.98691 | 0.14476 | 0.001451 | 0.15741 | 0.2018 | 0.31593 | 0.088379 | -122.1944 | 122.0052 | 122.2944 | 122.1511 | 23.8188 | -122.2772
4731.4062 | 122.3053 | -0.1236 | 122.0856 | -0.025411 | -0.05994 | 0.03837 | 0.015409 | -0.014429 | 0.015644 | -0.0062567 | -0.0018394 | -0.00058111 | 0.057619 | 0.053081 | 0.046192 | -0.06305 | -0.012329 | -0.049614 | 0.047549 | 0.087359 | 0.21522 | -0.1409 | 1.5532 | 23.7272 | 0.7724 | 121.9 | 122.1937 | 122.0412 | -0.2191 | -0.017303 | -122.038 | 0.060546 | 0.073982 | 0.091285 | -121.9982 | -121.8703 | -0.095499 | -0.18562 | 1.6768 | 0.89599 | 0.99149 | 0.10814 | -0.044327 | 0.17114 | 0.21096 | 0.33882 | 0.11127 | -122.2265 | 122.0235 | 122.3173 | 122.1648 | 23.8508 | -122.3047
4733.1094 | 122.3099 | -0.10071 | 122.113 | -0.025411 | -0.060153 | 0.038157 | 0.015195 | -0.014642 | 0.017567 | -0.036779 | -0.0016258 | -0.00058111 | 0.057619 | 0.052653 | 0.046406 | -0.06305 | -0.012329 | -0.040457 | 0.056706 | 0.087359 | 0.22438 | -0.14548 | 1.5715 | 23.7501 | 0.79071 | 121.8954 | 122.1891 | 122.0367 | -0.22825 | -0.04477 | -122.0563 | 0.037658 | 0.060251 | 0.10502 | -122.0257 | -121.8887 | -0.12754 | -0.21767 | 1.6723 | 0.89142 | 1.019 | 0.076099 | -0.076372 | 0.15741 | 0.18807 | 0.32509 | 0.088379 | -122.2585 | 121.9961 | 122.2898 | 122.1374 | 23.8508 | -122.3413
4734.8125 | 122.3007 | -0.11444 | 122.0764 | -0.025411 | -0.060153 | 0.037943 | 0.014981 | -0.014429 | 0.017354 | -0.013887 | -0.0016258 | -0.00058111 | 0.057832 | 0.052867 | 0.046192 | -0.058472 | -0.007751 | -0.045036 | 0.052128 | 0.1011 | 0.21522 | -0.13632 | 1.5944 | 23.7043 | 0.79071 | 121.8908 | 122.1891 | 122.0412 | -0.23283 | -0.021879 | -122.0243 | 0.055969 | 0.069405 | 0.091284 | -121.9753 | -121.8612 | -0.11839 | -0.18562 | 1.7089 | 0.90515 | 1.0235 | 0.11272 | -0.035172 | 0.16657 | 0.21554 | 0.32966 | 0.10669 | -122.2127 | 122.0052 | 122.3036 | 122.1557 | 23.8188 | -122.3092
4736.5625 | 122.2824 | -0.1236 | 122.113 | -0.010149 | -0.059726 | 0.038584 | 0.015195 | -0.014429 | 0.018208 | -0.021518 | -0.0016258 | -0.00079471 | 0.057832 | 0.053081 | 0.046406 | -0.06305 | -0.016908 | -0.035879 | 0.056706 | 0.091937 | 0.21522 | -0.15464 | 1.6265 | 23.654 | 0.81818 | 121.8908 | 122.18 | 122.0458 | -0.22367 | -0.03104 | -122.0563 | 0.060546 | 0.087717 | 0.11876 | -122.0211 | -121.8978 | -0.10008 | -0.22224 | 1.7501 | 0.94178 | 1.0419 | 0.066942 | -0.067215 | 0.1803 | 0.21553 | 0.33882 | 0.10669 | -122.2677 | 122.0144 | 122.3036 | 122.1694 | 23.7776 | -122.3367
4738.3281 | 122.3648 | -0.09613 | 122.0673 | -0.025411 | -0.060367 | 0.038157 | 0.014981 | -0.014429 | 0.018636 | -0.021518 | -0.0018394 | -0.00036751 | 0.057405 | 0.053081 | 0.045978 | -0.058472 | -0.003172 | -0.040457 | 0.052128 | 0.096516 | 0.21064 | -0.1409 | 1.654 | 23.6494 | 0.82734 | 121.8954 | 122.1891 | 122.0412 | -0.22367 | -0.044769 | -122.0151 | 0.037658 | 0.055673 | 0.10044 | -121.9707 | -121.8566 | -0.12754 | -0.17189 | 1.7501 | 0.92347 | 1.051 | 0.12188 | -0.026017 | 0.14826 | 0.19265 | 0.30678 | 0.092958 | -122.2082 | 121.9915 | 122.2853 | 122.1374 | 23.7455 | -122.2909
4740.0312 | 122.3648 | -0.10986 | 122.0856 | -0.01778 | -0.060581 | 0.03837 | 0.015409 | -0.014429 | 0.019277 | -0.021518 | -0.0016258 | -0.00058111 | 0.057619 | 0.052867 | 0.046406 | -0.053893 | -0.012329 | -0.040457 | 0.047549 | 0.096516 | 0.20607 | -0.1409 | 1.686 | 23.7089 | 0.8365 | 121.8862 | 122.1846 | 122.0367 | -0.23741 | -0.031036 | -122.038 | 0.05597 | 0.069406 | 0.10044 | -121.9891 | -121.8795 | -0.12755 | -0.19936 | 1.7959 | 0.94636 | 1.0739 | 0.098986 | -0.048906 | 0.15741 | 0.20638 | 0.31593 | 0.097534 | -122.2265 | 121.9961 | 122.2944 | 122.1465 | 23.8188 | -122.323
4741.7812 | 122.2641 | -0.14191 | 122.113 | -0.010149 | -0.060367 | 0.03837 | 0.015195 | -0.014856 | 0.020131 | -0.021518 | -0.0016258 | -0.00036751 | 0.057832 | 0.052653 | 0.046406 | -0.058472 | -0.007751 | -0.045036 | 0.052128 | 0.096516 | 0.21064 | -0.15006 | 1.7089 | 23.7639 | 0.85481 | 121.8816 | 122.1846 | 122.0367 | -0.22825 | -0.00815 | -122.0609 | 0.083435 | 0.096871 | 0.10502 | -122.0165 | -121.9024 | -0.086345 | -0.2314 | 1.8508 | 0.99672 | 1.0831 | 0.07152 | -0.076372 | 0.19404 | 0.23842 | 0.35255 | 0.13416 | -122.2631 | 122.0235 | 122.3265 | 122.1786 | 23.9058 | -122.3413
4743.4844 | 122.2549 | -0.13275 | 122.1313 | -0.010149 | -0.060367 | 0.03837 | 0.014981 | -0.014642 | 0.020772 | -0.021518 | -0.002053 | -0.00079471 | 0.057619 | 0.053081 | 0.046406 | -0.058472 | -0.012329 | -0.045036 | 0.052128 | 0.096516 | 0.21064 | -0.14548 | 1.7318 | 23.8005 | 0.86397 | 121.8908 | 122.18 | 122.0321 | -0.22367 | -0.012727 | -122.0792 | 0.074279 | 0.087715 | 0.10044 | -122.0348 | -121.9207 | -0.090922 | -0.24055 | 1.8646 | 0.99672 | 1.0876 | 0.048631 | -0.099262 | 0.18488 | 0.22927 | 0.3434 | 0.12042 | -122.2768 | 122.0235 | 122.3127 | 122.1648 | 23.9332 | -122.355
4745.25 | 122.2229 | -0.15106 | 122.081 | -0.01778 | -0.060153 | 0.038584 | 0.015195 | -0.014642 | 0.021413 | -0.021518 | -0.0016258 | -0.00036751 | 0.057619 | 0.053294 | 0.046406 | -0.058472 | -0.012329 | -0.054192 | 0.052128 | 0.1011 | 0.2198 | -0.1409 | 1.7639 | 23.8325 | 0.88686 | 121.8908 | 122.18 | 122.0229 | -0.22367 | 0.010163 | -122.0289 | 0.09259 | 0.09687 | 0.086707 | -121.9799 | -121.8612 | -0.072611 | -0.1902 | 1.9149 | 1.0379 | 1.1105 | 0.098985 | -0.058065 | 0.20319 | 0.25216 | 0.37086 | 0.13873 | -122.2219 | 122.0419 | 122.331 | 122.174 | 23.9836 | -122.3047
4747.0156 | 122.319 | -0.09613 | 122.0535 | -0.010149 | -0.060794 | 0.037943 | 0.014981 | -0.014642 | 0.021627 | -0.013887 | -0.0016258 | -0.00036751 | 0.057405 | 0.052867 | 0.046619 | -0.053893 | -0.007751 | -0.040457 | 0.047549 | 0.1011 | 0.21064 | -0.1409 | 1.7959 | 23.9241 | 0.90518 | 121.8816 | 122.1708 | 122.0321 | -0.22825 | -0.044769 | -122.006 | 0.042237 | 0.055673 | 0.10044 | -121.9524 | -121.8429 | -0.13212 | -0.17189 | 1.892 | 1.0013 | 1.1334 | 0.11729 | -0.021442 | 0.14368 | 0.19722 | 0.30678 | 0.088379 | -122.1944 | 121.9778 | 122.267 | 122.1282 | 24.0202 | -122.2818
4748.7969 | 122.2595 | -0.14191 | 122.0993 | 0.0051128 | -0.060153 | 0.038584 | 0.015195 | -0.014429 | 0.022268 | -0.013887 | -0.0016258 | -0.00079471 | 0.057832 | 0.052653 | 0.046833 | -0.06305 | -0.003172 | -0.045036 | 0.052128 | 0.096516 | 0.21064 | -0.14548 | 1.8371 | 23.947 | 0.92807 | 121.8862 | 122.1662 | 122.0321 | -0.22825 | -0.003571 | -122.0472 | 0.078857 | 0.096871 | 0.10044 | -122.0028 | -121.8887 | -0.086345 | -0.21309 | 1.979 | 1.07 | 1.1563 | 0.066939 | -0.067218 | 0.19404 | 0.23842 | 0.35255 | 0.13873 | -122.2448 | 122.0281 | 122.3081 | 122.174 | 24.0889 | -122.3276
4750.5 | 122.2275 | -0.15564 | 122.1359 | -0.010149 | -0.060153 | 0.03837 | 0.014981 | -0.01507 | 0.022482 | -0.013887 | -0.0014122 | -0.00058111 | 0.057619 | 0.053081 | 0.046406 | -0.053893 | -0.007751 | -0.045036 | 0.056706 | 0.096516 | 0.2198 | -0.1409 | 1.86 | 23.9928 | 0.95096 | 121.8771 | 122.1617 | 122.0321 | -0.22367 | 0.014741 | -122.0792 | 0.10175 | 0.1106 | 0.095863 | -122.0394 | -121.9161 | -0.068033 | -0.25887 | 2.0156 | 1.1066 | 1.1746 | 0.025739 | -0.10384 | 0.21235 | 0.25216 | 0.37544 | 0.14789 | -122.2768 | 122.0327 | 122.3173 | 122.1877 | 24.1484 | -122.3596
4752.2656 | 122.2961 | -0.1236 | 122.0856 | -0.01778 | -0.060367 | 0.03837 | 0.015409 | -0.014642 | 0.024191 | -0.013887 | -0.0014122 | -0.00058111 | 0.057832 | 0.052653 | 0.046833 | -0.058472 | -0.007751 | -0.045036 | 0.047549 | 0.096516 | 0.21522 | -0.15006 | 1.8921 | 24.0981 | 0.97386 | 121.8725 | 122.1617 | 122.0229 | -0.23283 | -0.026461 | -122.038 | 0.065124 | 0.07856 | 0.10502 | -121.9891 | -121.8703 | -0.10924 | -0.21309 | 2.0157 | 1.0975 | 1.2067 | 0.076093 | -0.062642 | 0.17114 | 0.22011 | 0.33882 | 0.11585 | -122.2356 | 121.9961 | 122.2853 | 122.1465 | 24.2217 | -122.3184
4754.0312 | 122.2961 | -0.11902 | 122.0947 | -0.0025182 | -0.060367 | 0.03837 | 0.015409 | -0.01507 | 0.025046 | -0.021518 | -0.0014122 | -0.00015391 | 0.057832 | 0.053294 | 0.046833 | -0.053893 | -0.016908 | -0.045036 | 0.056706 | 0.096516 | 0.21522 | -0.15006 | 1.9333 | 24.1668 | 0.99675 | 121.8816 | 122.1662 | 122.0138 | -0.22825 | -0.031038 | -122.038 | 0.065126 | 0.073983 | 0.10502 | -121.9982 | -121.8795 | -0.10923 | -0.21309 | 2.0523 | 1.1158 | 1.225 | 0.071516 | -0.080955 | 0.17572 | 0.21554 | 0.33424 | 0.10211 | -122.2448 | 122.0007 | 122.2853 | 122.1328 | 24.2858 | -122.323
4755.7344 | 122.2916 | -0.10986 | 122.0535 | -0.01778 | -0.060367 | 0.037729 | 0.014981 | -0.014429 | 0.025259 | -0.021518 | -0.0016258 | -0.00058111 | 0.057832 | 0.053294 | 0.046406 | -0.049315 | -0.012329 | -0.040457 | 0.052128 | 0.1011 | 0.21522 | -0.1409 | 1.9699 | 24.1988 | 1.0196 | 121.8725 | 122.1571 | 122.0184 | -0.23741 | -0.031036 | -122.0014 | 0.060548 | 0.069406 | 0.10044 | -121.9524 | -121.8383 | -0.12755 | -0.18105 | 2.0798 | 1.1295 | 1.2571 | 0.10356 | -0.035177 | 0.16199 | 0.21096 | 0.32509 | 0.097534 | -122.1944 | 121.9823 | 122.2669 | 122.1282 | 24.3087 | -122.2909
4757.5 | 122.2137 | -0.14191 | 122.0856 | -0.010149 | -0.060367 | 0.038584 | 0.015195 | -0.014642 | 0.026755 | -0.013887 | -0.0016258 | -0.00015391 | 0.057619 | 0.053081 | 0.046619 | -0.06305 | -0.012329 | -0.045036 | 0.056706 | 0.091937 | 0.2198 | -0.14548 | 1.9974 | 24.1988 | 1.038 | 121.8679 | 122.1525 | 122.0092 | -0.23741 | -0.003571 | -122.0289 | 0.078857 | 0.096871 | 0.10044 | -121.9936 | -121.8658 | -0.095503 | -0.21767 | 2.1393 | 1.1799 | 1.2754 | 0.066936 | -0.076378 | 0.19861 | 0.23384 | 0.36171 | 0.12958 | -122.231 | 122.0098 | 122.2944 | 122.1511 | 24.3407 | -122.323
4759.25 | 122.2229 | -0.14648 | 122.0764 | -0.010149 | -0.060153 | 0.038584 | 0.014981 | -0.014642 | 0.027396 | -0.013887 | -0.0016258 | -0.00058111 | 0.057832 | 0.053081 | 0.046619 | -0.058472 | -0.012329 | -0.049614 | 0.052128 | 0.10567 | 0.20607 | -0.14548 | 2.0294 | 24.2034 | 1.0563 | 121.8633 | 122.1571 | 122.0138 | -0.23741 | 0.001006 | -122.0243 | 0.088012 | 0.09687 | 0.095864 | -121.9707 | -121.8703 | -0.090926 | -0.21309 | 2.1759 | 1.2028 | 1.2937 | 0.08067 | -0.062644 | 0.19861 | 0.25216 | 0.35255 | 0.13415 | -122.2219 | 122.0098 | 122.3036 | 122.1603 | 24.3499 | -122.3138
4761.0156 | 122.3099 | -0.13275 | 122.0306 | -0.01778 | -0.05994 | 0.03837 | 0.015195 | -0.014429 | 0.029105 | -0.029148 | -0.0018394 | -0.00036751 | 0.057832 | 0.053081 | 0.046619 | -0.058472 | -0.007751 | -0.049614 | 0.056706 | 0.087359 | 0.21522 | -0.15006 | 2.0569 | 24.2584 | 1.0792 | 121.8587 | 122.1525 | 122.0092 | -0.24199 | -0.017306 | -121.9739 | 0.074279 | 0.083137 | 0.10044 | -121.9433 | -121.8154 | -0.10924 | -0.1719 | 2.1896 | 1.2119 | 1.3212 | 0.12187 | -0.021447 | 0.18946 | 0.22011 | 0.34798 | 0.125 | -122.1807 | 121.9915 | 122.2853 | 122.1419 | 24.3911 | -122.2726
4762.7969 | 122.1909 | -0.15106 | 122.0581 | -0.01778 | -0.060794 | 0.039011 | 0.014981 | -0.014642 | 0.030601 | -0.021518 | -0.0014122 | -0.00036751 | 0.057832 | 0.053294 | 0.046619 | -0.053893 | -0.012329 | -0.049614 | 0.047549 | 0.096516 | 0.21064 | -0.14548 | 2.0889 | 24.3042 | 1.0975 | 121.845 | 122.1433 | 121.9955 | -0.22825 | 0.005584 | -122.0106 | 0.097169 | 0.10145 | 0.095864 | -121.9616 | -121.8475 | -0.07719 | -0.2131 | 2.24 | 1.2485 | 1.3257 | 0.085245 | -0.062647 | 0.19861 | 0.24758 | 0.36171 | 0.13873 | -122.2036 | 121.9961 | 122.2944 | 122.1465 | 24.4552 | -122.2864
4764.5625 | 122.2916 | -0.1236 | 122.0352 | -0.010149 | -0.060367 | 0.03837 | 0.014981 | -0.014642 | 0.031669 | -0.021518 | -0.0014122 | -0.00036751 | 0.057832 | 0.053508 | 0.047046 | -0.06305 | -0.007751 | -0.045036 | 0.056706 | 0.096516 | 0.21064 | -0.1409 | 2.121 | 24.3087 | 1.1204 | 121.845 | 122.1433 | 122 | -0.23741 | -0.017303 | -121.9785 | 0.060546 | 0.07856 | 0.095863 | -121.9387 | -121.8246 | -0.11381 | -0.19021 | 2.2446 | 1.244 | 1.3578 | 0.10813 | -0.035181 | 0.1803 | 0.22011 | 0.33424 | 0.11585 | -122.1761 | 121.9686 | 122.2669 | 122.1236 | 24.4323 | -122.2726
4766.2656 | 117.9977 | -0.10986 | 117.8375 | -0.01778 | -0.060367 | 0.038584 | 0.014768 | -0.014642 | 0.033165 | -0.021518 | -0.0009848 | -0.00015391 | 0.058046 | 0.053081 | 0.046406 | -0.058472 | -0.007751 | -0.049614 | 0.052128 | 0.1011 | 0.20607 | -0.14548 | 2.1576 | 24.3728 | 1.1387 | 121.8359 | 122.1205 | 121.9863 | -0.22825 | -0.035615 | -117.7854 | 0.051391 | 0.060249 | 0.095864 | -117.7364 | -117.6315 | -0.11839 | 3.9983 | 2.2675 | 1.2486 | 1.3669 | 4.2829 | 4.1488 | 0.16199 | 0.21096 | 0.31593 | 0.10211 | -117.983 | 121.9457 | 122.2303 | 122.0962 | 24.4827 | -118.0658
4768.0312 | 122.1313 | -0.15564 | 122.049 | -0.01778 | -0.060367 | 0.038584 | 0.014768 | -0.014642 | 0.031669 | -0.021518 | -0.0014122 | -0.00015391 | 0.057832 | 0.052653 | 0.046833 | -0.058472 | -0.007751 | -0.040457 | 0.047549 | 0.096516 | 0.21064 | -0.14548 | 2.1851 | 24.4003 | 1.1707 | 121.8175 | 122.1205 | 121.9726 | -0.22825 | 0.010162 | -122.0014 | 0.097168 | 0.11518 | 0.10502 | -121.9524 | -121.8383 | -0.072612 | -0.23141 | 2.3407 | 1.3264 | 1.399 | 0.071507 | -0.076385 | 0.20319 | 0.25216 | 0.36628 | 0.14789 | -122.1944 | 121.9732 | 122.2761 | 122.1282 | 24.5559 | -122.2772
4769.8125 | 122.1725 | -0.16022 | 122.0673 | -0.01778 | -0.060794 | 0.038798 | 0.014981 | -0.014429 | 0.032951 | -0.021518 | -0.0011986 | -0.00015391 | 0.058046 | 0.053294 | 0.046833 | -0.058472 | -0.003172 | -0.040457 | 0.052128 | 0.1011 | 0.22438 | -0.14548 | 2.2309 | 24.4507 | 1.1982 | 121.8313 | 122.1159 | 121.9726 | -0.23283 | 0.014739 | -122.0151 | 0.10175 | 0.11976 | 0.10502 | -121.9662 | -121.8429 | -0.072614 | -0.23599 | 2.3911 | 1.3584 | 1.431 | 0.048617 | -0.094696 | 0.21235 | 0.26131 | 0.3846 | 0.15704 | -122.2127 | 121.9915 | 122.2761 | 122.1328 | 24.6109 | -122.3001
4771.5156 | 122.2137 | -0.13275 | 122.0718 | -0.01778 | -0.060153 | 0.03837 | 0.015195 | -0.014856 | 0.033806 | -0.0062567 | -0.0016258 | -0.00036751 | 0.057832 | 0.053081 | 0.047046 | -0.058472 | -0.003172 | -0.049614 | 0.061284 | 0.1011 | 0.21064 | -0.1409 | 2.2675 | 24.4827 | 1.2074 | 121.8267 | 122.1159 | 121.9726 | -0.23741 | -0.008148 | -122.0106 | 0.074279 | 0.083137 | 0.091285 | -121.9707 | -121.8612 | -0.10466 | -0.24514 | 2.4003 | 1.3401 | 1.4448 | 0.04404 | -0.099273 | 0.19404 | 0.23385 | 0.3434 | 0.12958 | -122.2127 | 121.9594 | 122.2486 | 122.1053 | 24.6155 | -122.3092
4773.2812 | 122.2504 | -0.11902 | 122.0306 | -0.033042 | -0.060581 | 0.03837 | 0.015195 | -0.014429 | 0.034019 | -0.021518 | -0.0014122 | -0.00015391 | 0.057832 | 0.053508 | 0.046619 | -0.053893 | -0.012329 | -0.045036 | 0.047549 | 0.096516 | 0.21064 | -0.14548 | 2.2996 | 24.5285 | 1.2303 | 121.8313 | 122.1205 | 121.9817 | -0.23283 | -0.026459 | -121.9831 | 0.065126 | 0.073983 | 0.10044 | -121.9341 | -121.82 | -0.11381 | -0.19937 | 2.4186 | 1.3493 | 1.4631 | 0.089817 | -0.048918 | 0.16657 | 0.21554 | 0.32966 | 0.10669 | -122.1761 | 121.9503 | 122.2395 | 122.1007 | 24.6475 | -122.2635
4775.0625 | 122.1405 | -0.14191 | 122.0306 | -0.01778 | -0.060367 | 0.038584 | 0.015409 | -0.014856 | 0.035942 | -0.021518 | -0.0016258 | -0.00036751 | 0.057832 | 0.053508 | 0.046833 | -0.053893 | -0.007751 | -0.045036 | 0.052128 | 0.1011 | 0.20607 | -0.15464 | 2.3408 | 24.5468 | 1.2623 | 121.813 | 122.1021 | 121.9726 | -0.23741 | -0.012729 | -121.9785 | 0.088014 | 0.096871 | 0.1096 | -121.9295 | -121.8246 | -0.095503 | -0.21768 | 2.4827 | 1.4042 | 1.4997 | 0.071503 | -0.058075 | 0.19404 | 0.243 | 0.34797 | 0.13416 | -122.1853 | 121.9549 | 122.2441 | 122.1145 | 24.6887 | -122.2681
4776.7656 | 122.1634 | -0.13733 | 122.0261 | -0.010149 | -0.060581 | 0.03837 | 0.015622 | -0.014429 | 0.036797 | -0.021518 | -0.0011986 | -0.00015391 | 0.057832 | 0.053294 | 0.047046 | -0.06305 | -0.007751 | -0.040457 | 0.052128 | 0.1011 | 0.21064 | -0.15006 | 2.3866 | 24.5926 | 1.2852 | 121.7855 | 122.0793 | 121.9359 | -0.24199 | -0.012728 | -121.9739 | 0.074279 | 0.096872 | 0.1096 | -121.925 | -121.8154 | -0.10466 | -0.24057 | 2.5239 | 1.4225 | 1.5272 | 0.053188 | -0.090126 | 0.18946 | 0.23842 | 0.34797 | 0.12958 | -122.1761 | 121.9228 | 122.2166 | 122.0733 | 24.7299 | -122.2681
4778.5312 | 122.1771 | -0.1236 | 121.9345 | -0.010149 | -0.060581 | 0.03837 | 0.014981 | -0.014856 | 0.038506 | -0.021518 | -0.0014122 | -0.00036751 | 0.05826 | 0.053294 | 0.047046 | -0.06305 | -0.007751 | -0.035879 | 0.056706 | 0.096516 | 0.21522 | -0.15464 | 2.4278 | 24.6247 | 1.3081 | 121.7351 | 122.0335 | 121.881 | -0.23283 | -0.03104 | -121.8778 | 0.060546 | 0.087717 | 0.11876 | -121.838 | -121.7193 | -0.10924 | -0.19938 | 2.5514 | 1.4317 | 1.5409 | 0.098955 | -0.053517 | 0.1803 | 0.22011 | 0.33882 | 0.11585 | -122.0891 | 121.8587 | 122.1571 | 122.0046 | 24.7483 | -122.1673
4780.2344 | 122.2458 | -0.10986 | 121.9528 | -0.010149 | -0.060153 | 0.038157 | 0.014981 | -0.014642 | 0.039788 | -0.029148 | -0.0011986 | -0.00036751 | 0.057832 | 0.053508 | 0.047046 | -0.058472 | -0.012329 | -0.049614 | 0.052128 | 0.091937 | 0.2198 | -0.15006 | 2.4598 | 24.6521 | 1.3493 | 121.7763 | 122.0609 | 121.9314 | -0.23741 | -0.040194 | -121.9007 | 0.051391 | 0.060249 | 0.10044 | -121.8609 | -121.733 | -0.12755 | -0.17649 | 2.5697 | 1.4592 | 1.5867 | 0.10811 | -0.021463 | 0.16199 | 0.2018 | 0.32966 | 0.097534 | -122.1029 | 121.8862 | 122.1708 | 122.0412 | 24.762 | -122.1902
4782 | 122.1222 | -0.15564 | 121.994 | -0.01778 | -0.060581 | 0.03837 | 0.015409 | -0.014856 | 0.040216 | -0.021518 | -0.0011986 | -0.00015391 | 0.057832 | 0.053508 | 0.046833 | -0.058472 | -0.012329 | -0.045036 | 0.052128 | 0.096516 | 0.21522 | -0.1409 | 2.501 | 24.6979 | 1.3768 | 121.7763 | 122.0655 | 121.9176 | -0.24199 | 0.014741 | -121.9419 | 0.097168 | 0.1106 | 0.095863 | -121.8975 | -121.7788 | -0.086349 | -0.21769 | 2.6567 | 1.5324 | 1.6188 | 0.071495 | -0.076398 | 0.20777 | 0.25216 | 0.37086 | 0.14331 | -122.1349 | 121.932 | 122.2212 | 122.0733 | 24.8536 | -122.236
4783.7656 | 122.113 | -0.14191 | 121.9391 | -0.0025182 | -0.060794 | 0.037943 | 0.014981 | -0.014429 | 0.04107 | -0.021518 | -0.0014122 | -0.00015391 | 0.057832 | 0.053294 | 0.046619 | -0.049315 | -0.007751 | -0.049614 | 0.052128 | 0.096516 | 0.21522 | -0.14548 | 2.5422 | 24.7208 | 1.4043 | 121.7214 | 122.0151 | 121.8581 | -0.23741 | -0.003571 | -121.887 | 0.092592 | 0.092293 | 0.095864 | -121.8426 | -121.7239 | -0.095503 | -0.2177 | 2.6841 | 1.5462 | 1.6417 | 0.076062 | -0.080988 | 0.19404 | 0.23842 | 0.35713 | 0.13416 | -122.0846 | 121.8633 | 122.1571 | 122 | 24.8627 | -122.1765
4785.4531 | 122.1222 | -0.11444 | 121.8704 | -0.01778 | -0.060367 | 0.038157 | 0.014981 | -0.014856 | 0.043207 | -0.013887 | -0.0011986 | 5.9888e-05 | 0.058046 | 0.053722 | 0.047046 | -0.053893 | -0.007751 | -0.040457 | 0.052128 | 0.091937 | 0.2198 | -0.1409 | 2.588 | 24.7208 | 1.4317 | 121.6939 | 121.9923 | 121.8306 | -0.23741 | -0.026458 | -121.8183 | 0.060548 | 0.073984 | 0.10044 | -121.7785 | -121.6506 | -0.12297 | -0.1765 | 2.7025 | 1.5462 | 1.6691 | 0.12183 | -0.039794 | 0.16657 | 0.20638 | 0.33424 | 0.10669 | -122.0113 | 121.8084 | 122.1067 | 121.9451 | 24.8353 | -122.1078
4787.2188 | 121.9391 | -0.1236 | 121.788 | -0.010149 | -0.060367 | 0.038584 | 0.015195 | -0.014856 | 0.044275 | -0.013887 | -0.0014122 | 5.9888e-05 | 0.057832 | 0.053294 | 0.046619 | -0.058472 | -0.012329 | -0.045036 | 0.056706 | 0.1011 | 0.21522 | -0.15464 | 2.6338 | 24.6979 | 1.4638 | 121.5886 | 121.8778 | 121.7299 | -0.24199 | -0.03104 | -121.7313 | 0.065124 | 0.07856 | 0.1096 | -121.6869 | -121.5728 | -0.11839 | -0.19941 | 2.7574 | 1.5874 | 1.7058 | 0.089766 | -0.058126 | 0.1803 | 0.22469 | 0.33882 | 0.11127 | -121.9427 | 121.7122 | 122.0014 | 121.8535 | 24.8215 | -122.03
4788.9219 | 121.9254 | -0.086975 | 121.7377 | -0.01778 | -0.060367 | 0.03837 | 0.015622 | -0.014856 | 0.043848 | -0.036779 | -0.0014122 | -0.00015391 | 0.058046 | 0.053508 | 0.047046 | -0.049315 | -0.012329 | -0.040457 | 0.052128 | 0.1011 | 0.21522 | -0.14548 | 2.675 | 24.6796 | 1.4867 | 121.5428 | 121.8503 | 121.6978 | -0.24657 | -0.058503 | -121.6855 | 0.03766 | 0.046518 | 0.10502 | -121.6366 | -121.5224 | -0.15959 | -0.19484 | 2.762 | 1.5736 | 1.7332 | 0.11265 | -0.039823 | 0.1391 | 0.18807 | 0.3022 | 0.074646 | -121.8831 | 121.6298 | 121.9373 | 121.7848 | 24.7666 | -121.9842
4790.6875 | 121.8384 | -0.091553 | 121.55 | -0.0025182 | -0.060581 | 0.03837 | 0.014768 | -0.014642 | 0.042352 | -0.029148 | -0.0009848 | -0.00015391 | 0.057832 | 0.053722 | 0.046833 | -0.06305 | -0.007751 | -0.040457 | 0.056706 | 0.096516 | 0.20607 | -0.15006 | 2.7254 | 24.6384 | 1.5233 | 121.3688 | 121.658 | 121.5101 | -0.23741 | -0.058504 | -121.4933 | 0.028503 | 0.051096 | 0.1096 | -121.4535 | -121.3439 | -0.14586 | -0.18114 | 2.8169 | 1.6149 | 1.7607 | 0.10803 | -0.039862 | 0.14826 | 0.18807 | 0.29762 | 0.083802 | -121.7 | 121.4604 | 121.7496 | 121.6017 | 24.73 | -121.7874
4792.4062 | 121.7102 | -0.13733 | 121.4676 | -0.010149 | -0.060581 | 0.03837 | 0.015195 | -0.014642 | 0.044275 | -0.036779 | -0.0007712 | -0.00015391 | 0.057832 | 0.053294 | 0.046833 | -0.053893 | -0.016908 | -0.049614 | 0.052128 | 0.091937 | 0.2198 | -0.15006 | 2.762 | 24.6247 | 1.5554 | 121.2819 | 121.5756 | 121.4277 | -0.23283 | -0.012728 | -121.4155 | 0.083436 | 0.087715 | 0.10044 | -121.3757 | -121.2478 | -0.095502 | -0.18574 | 2.8993 | 1.6927 | 1.7882 | 0.10801 | -0.039879 | 0.18946 | 0.22927 | 0.35713 | 0.12042 | -121.6176 | 121.4192 | 121.7129 | 121.565 | 24.762 | -121.7004
4794.1719 | 121.8613 | -0.14648 | 121.6736 | 0.0051128 | -0.060367 | 0.03837 | 0.015409 | -0.014642 | 0.044062 | -0.013887 | -0.0011986 | 5.9888e-05 | 0.05826 | 0.053508 | 0.046833 | -0.06305 | -0.016908 | -0.049614 | 0.047549 | 0.096516 | 0.22438 | -0.15006 | 2.8124 | 24.6979 | 1.592 | 121.4329 | 121.7175 | 121.588 | -0.23741 | -0.003573 | -121.626 | 0.083434 | 0.09687 | 0.10044 | -121.5771 | -121.4492 | -0.090926 | -0.24064 | 2.9589 | 1.7385 | 1.8294 | 0.043956 | -0.085622 | 0.19403 | 0.243 | 0.37087 | 0.12958 | -121.8236 | 121.5794 | 121.864 | 121.7344 | 24.8444 | -121.911
4795.9375 | 121.9162 | -0.082397 | 121.7102 | -0.0025182 | -0.060367 | 0.03837 | 0.015195 | -0.014429 | -0.015123 | -0.021518 | -0.0009848 | 0.00070089 | 0.057832 | 0.053722 | 0.047046 | -0.044736 | -0.007751 | -0.031301 | 0.061284 | 0.10567 | 0.22438 | -0.12258 | 2.8948 | 24.7117 | 1.6607 | 121.5108 | 121.8045 | 121.6566 | -0.20536 | -0.040186 | -121.6489 | 0.037661 | 0.051096 | 0.091282 | -121.6045 | -121.4858 | -0.12296 | -0.19943 | 2.9772 | 1.7431 | 1.866 | 0.094328 | -0.053564 | 0.14368 | 0.18807 | 0.30678 | 0.074646 | -121.8328 | 121.5932 | 121.8869 | 121.739 | 24.7941 | -121.9156
4797.6406 | 121.962 | -0.11902 | 121.8109 | -0.0025182 | -0.060581 | 0.038157 | 0.015195 | -0.014642 | -0.015337 | -0.013887 | -0.0009848 | -0.00015391 | 0.058687 | 0.053722 | 0.04726 | -0.044736 | -0.003172 | -0.035879 | 0.065863 | 0.10567 | 0.22896 | -0.118 | 2.9452 | 24.7345 | 1.6927 | 121.5978 | 121.8915 | 121.7436 | -0.20078 | 0.001015 | -121.7451 | 0.074283 | 0.08314 | 0.082125 | -121.7052 | -121.582 | -0.08176 | -0.21314 | 3.0642 | 1.8117 | 1.8935 | 0.080614 | -0.067279 | 0.18488 | 0.22469 | 0.34798 | 0.11585 | -121.9289 | 121.7168 | 122.0105 | 121.8627 | 24.8536 | -122.0117
4799.4219 | 122.081 | -0.073242 | 121.8246 | -0.01778 | -0.060367 | 0.03837 | 0.015195 | -0.014642 | -0.015337 | -0.029148 | -0.0011986 | -0.00015391 | 0.05826 | 0.053508 | 0.04726 | -0.044736 | 0.005985 | -0.031301 | 0.061284 | 0.1011 | 0.2198 | -0.12716 | 3.0001 | 24.7345 | 1.7293 | 121.6344 | 121.9282 | 121.7803 | -0.20536 | -0.05392 | -121.7634 | 0.028506 | 0.041941 | 0.095861 | -121.7236 | -121.6048 | -0.13212 | -0.19025 | 3.0733 | 1.8026 | 1.9347 | 0.10351 | -0.044383 | 0.13453 | 0.17434 | 0.29304 | 0.079227 | -121.9518 | 121.7076 | 122.0014 | 121.8535 | 24.8078 | -122.03
4801.1719 | 122.0581 | -0.07782 | 121.8338 | -0.01778 | -0.060581 | 0.037943 | 0.015409 | -0.014856 | -0.01555 | -0.029148 | -0.0009848 | 5.9888e-05 | 0.058473 | 0.053935 | 0.04726 | -0.044736 | -0.007751 | -0.035879 | 0.061284 | 0.1011 | 0.22896 | -0.12716 | 3.0596 | 24.762 | 1.7614 | 121.6664 | 121.951 | 121.8032 | -0.20078 | -0.049342 | -121.7725 | 0.033084 | 0.041941 | 0.091283 | -121.7327 | -121.6048 | -0.12296 | -0.16735 | 3.1374 | 1.8392 | 1.9622 | 0.11725 | -0.030645 | 0.1391 | 0.17891 | 0.30678 | 0.070069 | -121.961 | 121.7443 | 122.0289 | 121.881 | 24.8398 | -122.0346
4802.9375 | 122.113 | -0.082397 | 121.8704 | -0.010149 | -0.060367 | 0.03837 | 0.015195 | -0.014856 | -0.01555 | -0.013887 | -0.0007712 | 0.00048709 | 0.058473 | 0.053935 | 0.047474 | -0.044736 | -0.007751 | -0.031301 | 0.061284 | 0.10567 | 0.22438 | -0.118 | 3.1146 | 24.7895 | 1.8026 | 121.6939 | 121.9739 | 121.826 | -0.20078 | -0.035607 | -121.8091 | 0.037661 | 0.051096 | 0.086703 | -121.7647 | -121.646 | -0.11838 | -0.1765 | 3.197 | 1.885 | 2.0034 | 0.10352 | -0.044373 | 0.14368 | 0.18807 | 0.30678 | 0.074646 | -121.9884 | 121.7763 | 122.0563 | 121.9084 | 24.8719 | -122.0712
4804.7031 | 122.1176 | -0.07782 | 121.8933 | -0.01778 | -0.060581 | 0.03837 | 0.014981 | -0.014856 | -0.015337 | -0.021518 | -0.0009848 | 5.9888e-05 | 0.058687 | 0.053935 | 0.04726 | -0.044736 | -0.003172 | -0.031301 | 0.065863 | 0.11483 | 0.22896 | -0.12258 | 3.1695 | 24.8444 | 1.8438 | 121.6939 | 121.9923 | 121.8352 | -0.20078 | -0.044763 | -121.8274 | 0.033084 | 0.046519 | 0.091282 | -121.7785 | -121.6644 | -0.12296 | -0.19939 | 3.2473 | 1.9216 | 2.0446 | 0.098945 | -0.058105 | 0.14368 | 0.19265 | 0.30678 | 0.074648 | -122.0159 | 121.7717 | 122.0701 | 121.913 | 24.9223 | -122.0941
4806.4062 | 122.0261 | -0.10071 | 121.9208 | -0.010149 | -0.060581 | 0.038157 | 0.015195 | -0.014856 | -0.015337 | -0.021518 | -0.0009848 | 5.9888e-05 | 0.058473 | 0.053508 | 0.04726 | -0.040158 | -0.003172 | -0.031301 | 0.061284 | 0.11025 | 0.22896 | -0.12258 | 3.2382 | 24.8902 | 1.8804 | 121.7077 | 121.9923 | 121.8535 | -0.1962 | -0.021875 | -121.8595 | 0.06055 | 0.069407 | 0.091282 | -121.8105 | -121.6918 | -0.095492 | -0.21312 | 3.3389 | 1.9812 | 2.0766 | 0.07148 | -0.067255 | 0.16199 | 0.21096 | 0.32967 | 0.097536 | -122.0434 | 121.8084 | 122.093 | 121.9542 | 24.9909 | -122.117
4808.1875 | 122.0123 | -0.1236 | 121.9391 | -0.0025182 | -0.060367 | 0.038157 | 0.015409 | -0.014642 | -0.015337 | -0.021518 | -0.0014122 | 5.9888e-05 | 0.058473 | 0.053935 | 0.047687 | -0.040158 | 0.001407 | -0.031301 | 0.056706 | 0.11025 | 0.21522 | -0.12258 | 3.2931 | 24.936 | 1.9262 | 121.7168 | 121.9968 | 121.8535 | -0.20078 | 0.001013 | -121.8824 | 0.083438 | 0.092295 | 0.091282 | -121.8288 | -121.7239 | -0.077183 | -0.22228 | 3.4167 | 2.0498 | 2.127 | 0.057748 | -0.085566 | 0.1803 | 0.23385 | 0.33882 | 0.125 | -122.0617 | 121.8404 | 122.1204 | 121.9771 | 25.0596 | -122.1399
4809.9062 | 122.0764 | -0.10071 | 121.9299 | -0.01778 | -0.060794 | 0.038584 | 0.015409 | -0.014642 | -0.015337 | -0.013887 | -0.0009848 | 0.00027349 | 0.058473 | 0.054363 | 0.047474 | -0.044736 | -0.003172 | -0.040457 | 0.070441 | 0.11483 | 0.22438 | -0.13174 | 3.3481 | 24.9543 | 1.9674 | 121.7305 | 122.0106 | 121.8718 | -0.20078 | -0.031033 | -121.8595 | 0.055972 | 0.060251 | 0.091284 | -121.8151 | -121.7056 | -0.10007 | -0.19938 | 3.4488 | 2.0681 | 2.1682 | 0.080639 | -0.058097 | 0.17115 | 0.21554 | 0.32509 | 0.097536 | -122.0617 | 121.8313 | 122.1113 | 121.9725 | 25.055 | -122.1307
4811.6719 | 122.1222 | -0.082397 | 121.9299 | -0.01778 | -0.060367 | 0.038157 | 0.015195 | -0.014642 | -0.014909 | -0.029148 | -0.0007712 | 0.00027349 | 0.058473 | 0.054149 | 0.047687 | -0.044736 | 0.005985 | -0.035879 | 0.061284 | 0.11483 | 0.22438 | -0.12716 | 3.4168 | 24.9955 | 2.0132 | 121.7397 | 122.0197 | 121.8718 | -0.20078 | -0.044765 | -121.8686 | 0.037661 | 0.046518 | 0.091283 | -121.8151 | -121.7056 | -0.11838 | -0.19023 | 3.4992 | 2.0956 | 2.214 | 0.089796 | -0.058097 | 0.14368 | 0.19723 | 0.30678 | 0.088382 | -122.0571 | 121.8221 | 122.1021 | 121.9542 | 25.0779 | -122.1307
4813.375 | 122.0535 | -0.1236 | 121.9666 | 0.0051128 | -0.060367 | 0.038157 | 0.014981 | -0.014856 | -0.015337 | -0.029148 | -0.0009848 | 0.00070089 | 0.058473 | 0.054363 | 0.04726 | -0.040158 | -0.003172 | -0.035879 | 0.070441 | 0.11025 | 0.22896 | -0.12258 | 3.4809 | 25.0322 | 2.0636 | 121.7489 | 122.0243 | 121.881 | -0.20536 | 0.001013 | -121.8961 | 0.083438 | 0.087717 | 0.086704 | -121.8563 | -121.7376 | -0.081762 | -0.21769 | 3.6045 | 2.1872 | 2.2689 | 0.057753 | -0.085561 | 0.19404 | 0.23385 | 0.35256 | 0.12042 | -122.0891 | 121.8725 | 122.1479 | 122.0046 | 25.1558 | -122.1719
4815.1406 | 122.2 | -0.082397 | 121.9208 | -0.01778 | -0.060367 | 0.038157 | 0.014768 | -0.014856 | -0.015123 | -0.013887 | -0.0007712 | 0.00070089 | 0.058473 | 0.054149 | 0.047687 | -0.049315 | -0.003172 | -0.035879 | 0.065863 | 0.11025 | 0.23354 | -0.12258 | 3.5495 | 25.1008 | 2.114 | 121.7534 | 122.038 | 121.8902 | -0.20078 | -0.040186 | -121.8549 | 0.033082 | 0.046518 | 0.086704 | -121.8105 | -121.6872 | -0.11838 | -0.16734 | 3.6319 | 2.1964 | 2.3147 | 0.11727 | -0.030626 | 0.14826 | 0.19265 | 0.31593 | 0.079225 | -122.0434 | 121.8358 | 122.1204 | 121.9725 | 25.1832 | -122.1216
4816.9062 | 122.081 | -0.10986 | 122.0032 | -0.010149 | -0.060367 | 0.03837 | 0.015195 | -0.01507 | -0.015123 | -0.021518 | -0.000344 | 0.00027349 | 0.058901 | 0.053935 | 0.047474 | -0.040158 | 0.005985 | -0.035879 | 0.065863 | 0.11483 | 0.22438 | -0.12258 | 3.6182 | 25.1192 | 2.1643 | 121.758 | 122.0426 | 121.8947 | -0.20536 | -0.01272 | -121.9373 | 0.069705 | 0.073984 | 0.086704 | -121.8883 | -121.7788 | -0.095495 | -0.24516 | 3.7281 | 2.2742 | 2.3697 | 0.039447 | -0.10845 | 0.17573 | 0.2247 | 0.33424 | 0.11585 | -122.1258 | 121.8679 | 122.1525 | 122.0046 | 25.229 | -122.2085
4818.6875 | 122.0856 | -0.10986 | 121.9849 | -0.010149 | -0.060581 | 0.038798 | 0.015195 | -0.014642 | -0.015337 | -0.013887 | -0.0005576 | 0.00048709 | 0.058687 | 0.054363 | 0.047901 | -0.044736 | 0.001407 | -0.031301 | 0.061284 | 0.11025 | 0.2198 | -0.12716 | 3.6869 | 25.2107 | 2.2193 | 121.758 | 122.0518 | 121.9039 | -0.20536 | -0.017299 | -121.9236 | 0.065127 | 0.078562 | 0.095861 | -121.8746 | -121.7651 | -0.095495 | -0.22684 | 3.7968 | 2.3291 | 2.4246 | 0.066915 | -0.080978 | 0.17115 | 0.22012 | 0.32966 | 0.11127 | -122.112 | 121.8679 | 122.1616 | 122.0137 | 25.3206 | -122.1902
4820.4688 | 122.2183 | -0.07782 | 121.9482 | -0.0025182 | -0.060794 | 0.038798 | 0.015409 | -0.014642 | -0.01555 | -0.029148 | -0.0005576 | 0.00070089 | 0.058473 | 0.054576 | 0.047901 | -0.040158 | -0.012329 | -0.035879 | 0.061284 | 0.11483 | 0.23354 | -0.13174 | 3.7693 | 25.2977 | 2.2696 | 121.7626 | 122.0472 | 121.9039 | -0.20994 | -0.053921 | -121.887 | 0.037662 | 0.041941 | 0.095862 | -121.8334 | -121.7147 | -0.13212 | -0.18565 | 3.8471 | 2.3475 | 2.4796 | 0.098957 | -0.044357 | 0.1391 | 0.19265 | 0.31136 | 0.065491 | -122.08 | 121.8404 | 122.125 | 121.9817 | 25.3756 | -122.1582
4822.1875 | 122.1039 | -0.1236 | 121.9757 | -0.0025182 | -0.060581 | 0.038584 | 0.014981 | -0.014856 | -0.014909 | -0.021518 | -0.0005576 | 0.00048709 | 0.058687 | 0.054576 | 0.047687 | -0.044736 | 0.005985 | -0.026723 | 0.070441 | 0.11025 | 0.22438 | -0.12258 | 3.8334 | 25.3756 | 2.32 | 121.7672 | 122.0518 | 121.9085 | -0.21452 | 0.001013 | -121.9053 | 0.07886 | 0.096873 | 0.09586 | -121.8655 | -121.7513 | -0.09092 | -0.20853 | 3.957 | 2.4436 | 2.5345 | 0.07607 | -0.067244 | 0.19404 | 0.23385 | 0.34798 | 0.12958 | -122.0983 | 121.8908 | 122.1754 | 122.0321 | 25.4992 | -122.1902
4823.9688 | 122.2092 | -0.07782 | 121.9437 | -0.010149 | -0.060581 | 0.03837 | 0.014768 | -0.014856 | -0.015123 | -0.021518 | -0.0007712 | 0.00048709 | 0.058901 | 0.054576 | 0.047901 | -0.044736 | 0.001407 | -0.040457 | 0.061284 | 0.10567 | 0.23354 | -0.11342 | 3.9158 | 25.4122 | 2.3521 | 121.7809 | 122.0609 | 121.913 | -0.20078 | -0.035605 | -121.8824 | 0.033084 | 0.037363 | 0.072968 | -121.838 | -121.7101 | -0.12296 | -0.16275 | 3.9937 | 2.4299 | 2.5528 | 0.11727 | -0.030622 | 0.1391 | 0.18349 | 0.31136 | 0.079227 | -122.0571 | 121.8587 | 122.1388 | 121.9909 | 25.49 | -122.1444
4825.6719 | 122.1588 | -0.07782 | 121.962 | -0.025411 | -0.060794 | 0.03837 | 0.015195 | -0.01507 | -0.014909 | -0.036779 | -0.000344 | 0.00070089 | 0.058901 | 0.054576 | 0.048115 | -0.040158 | 0.015142 | -0.040457 | 0.065863 | 0.11025 | 0.22438 | -0.12716 | 3.9799 | 25.5404 | 2.4116 | 121.7763 | 122.0655 | 121.913 | -0.20536 | -0.049342 | -121.8961 | 0.037662 | 0.037363 | 0.086705 | -121.8517 | -121.7376 | -0.12754 | -0.18564 | 4.0578 | 2.4894 | 2.6169 | 0.10354 | -0.048932 | 0.14368 | 0.18807 | 0.3022 | 0.092962 | -122.0891 | 121.8542 | 122.1433 | 121.9909 | 25.6182 | -122.1673
4827.4375 | 122.1176 | -0.11444 | 121.9849 | -0.0025182 | -0.060367 | 0.03837 | 0.014981 | -0.014642 | -0.015123 | -0.021518 | -0.000344 | 0.00091449 | 0.058901 | 0.054576 | 0.048115 | -0.044736 | 0.001407 | -0.031301 | 0.065863 | 0.11025 | 0.22896 | -0.12258 | 4.0578 | 25.6869 | 2.4665 | 121.7763 | 122.0747 | 121.9176 | -0.20078 | -0.008142 | -121.919 | 0.069705 | 0.08314 | 0.091282 | -121.8746 | -121.7559 | -0.086338 | -0.20853 | 4.1722 | 2.581 | 2.6673 | 0.089808 | -0.067242 | 0.1803 | 0.22469 | 0.3434 | 0.11585 | -122.1074 | 121.8908 | 122.1891 | 122.0321 | 25.8014 | -122.1856
4829.2188 | 122.2412 | -0.07782 | 121.9757 | -0.01778 | -0.060581 | 0.038584 | 0.014981 | -0.01507 | -0.014696 | -0.013887 | -0.000344 | 0.00070089 | 0.058901 | 0.05479 | 0.048328 | -0.040158 | 0.005985 | -0.031301 | 0.065863 | 0.12399 | 0.23354 | -0.12258 | 4.1448 | 25.7785 | 2.526 | 121.7901 | 122.0655 | 121.9222 | -0.20536 | -0.044763 | -121.9098 | 0.037662 | 0.046519 | 0.091282 | -121.8517 | -121.7422 | -0.12754 | -0.18564 | 4.2226 | 2.6039 | 2.7314 | 0.089806 | -0.053508 | 0.14368 | 0.20181 | 0.31136 | 0.083805 | -122.0983 | 121.8679 | 122.1433 | 122 | 25.8563 | -122.1811
4830.9844 | 122.1359 | -0.10071 | 121.994 | -0.010149 | -0.060794 | 0.03837 | 0.014768 | -0.014642 | -0.015123 | -0.021518 | -0.000344 | 0.00070089 | 0.058687 | 0.054576 | 0.048328 | -0.03558 | 0.010564 | -0.026723 | 0.070441 | 0.11483 | 0.22438 | -0.12258 | 4.2318 | 25.9296 | 2.5947 | 121.7901 | 122.0747 | 121.9314 | -0.20536 | -0.021875 | -121.9236 | 0.065128 | 0.073985 | 0.09586 | -121.8792 | -121.7696 | -0.10465 | -0.20395 | 4.3325 | 2.6954 | 2.8001 | 0.080652 | -0.062662 | 0.17115 | 0.21554 | 0.32509 | 0.11127 | -122.1166 | 121.8908 | 122.1754 | 122.0321 | 26.0303 | -122.1994
4832.6875 | 122.1359 | -0.10071 | 122.0032 | -0.010149 | -0.060581 | 0.038584 | 0.015195 | -0.014856 | -0.015123 | -0.021518 | -0.0001304 | 0.00070089 | 0.058687 | 0.054576 | 0.048328 | -0.03558 | 0.010564 | -0.035879 | 0.065863 | 0.11025 | 0.22896 | -0.12258 | 4.3233 | 26.1173 | 2.6542 | 121.7946 | 122.0747 | 121.9268 | -0.20536 | -0.021875 | -121.9373 | 0.065128 | 0.064829 | 0.086704 | -121.8929 | -121.7742 | -0.10465 | -0.20853 | 4.4241 | 2.755 | 2.8596 | 0.071497 | -0.076395 | 0.16657 | 0.21096 | 0.32967 | 0.11127 | -122.1258 | 121.8954 | 122.1754 | 122.0275 | 26.218 | -122.2085
4834.4688 | 122.1542 | -0.09613 | 121.9894 | -0.01778 | -0.060794 | 0.03837 | 0.014981 | -0.014856 | -0.014696 | -0.029148 | 0.000297 | 0.00091449 | 0.058687 | 0.054576 | 0.048969 | -0.049315 | 0.005985 | -0.035879 | 0.07502 | 0.11483 | 0.22896 | -0.118 | 4.4149 | 26.2959 | 2.7183 | 121.7946 | 122.0793 | 121.9314 | -0.20536 | -0.021874 | -121.9144 | 0.046815 | 0.060251 | 0.082125 | -121.8746 | -121.7605 | -0.10923 | -0.19479 | 4.5111 | 2.8145 | 2.9237 | 0.089809 | -0.058084 | 0.17115 | 0.21096 | 0.32509 | 0.10211 | -122.1074 | 121.8908 | 122.1754 | 122.0275 | 26.392 | -122.1948
4836.1562 | 122.1085 | -0.13275 | 122.049 | -0.010149 | -0.060794 | 0.038157 | 0.015409 | -0.014642 | -0.014909 | -0.021518 | 8.3402e-05 | 0.00091449 | 0.059114 | 0.05479 | 0.048328 | -0.044736 | 0.005985 | -0.035879 | 0.065863 | 0.11483 | 0.23354 | -0.12258 | 4.5065 | 26.4378 | 2.7824 | 121.7901 | 122.0747 | 121.9405 | -0.20078 | 0.010168 | -121.9831 | 0.088015 | 0.096872 | 0.086704 | -121.9341 | -121.8154 | -0.068028 | -0.25888 | 4.6392 | 2.9152 | 2.9832 | 0.025721 | -0.10844 | 0.19861 | 0.24758 | 0.36629 | 0.13874 | -122.1715 | 121.9228 | 122.2074 | 122.0733 | 26.5706 | -122.2497
4837.9219 | 122.1085 | -0.11444 | 122.0215 | -0.025411 | -0.060581 | 0.03837 | 0.015195 | -0.014642 | -0.014696 | -0.013887 | 0.000297 | 0.00091449 | 0.059114 | 0.05479 | 0.048969 | -0.044736 | 0.001407 | -0.031301 | 0.065863 | 0.11483 | 0.22896 | -0.12716 | 4.6164 | 26.6393 | 2.8557 | 121.8038 | 122.0838 | 121.9451 | -0.20994 | -0.012721 | -121.9556 | 0.069705 | 0.08314 | 0.095861 | -121.9067 | -121.7925 | -0.095496 | -0.21768 | 4.7308 | 2.9701 | 3.0656 | 0.062344 | -0.076391 | 0.1803 | 0.22927 | 0.3434 | 0.11585 | -122.1486 | 121.9182 | 122.1983 | 122.0595 | 26.7537 | -122.2314
4839.6875 | 122.1085 | -0.12817 | 122.0398 | 0.0051128 | -0.060794 | 0.03837 | 0.015409 | -0.014856 | -0.014909 | -0.021518 | 8.3402e-05 | 0.00091449 | 0.059328 | 0.054576 | 0.048969 | -0.044736 | 0.005985 | -0.026723 | 0.065863 | 0.11941 | 0.22896 | -0.12258 | 4.7034 | 26.8911 | 2.929 | 121.8038 | 122.0838 | 121.9405 | -0.20078 | 0.005591 | -121.9739 | 0.083438 | 0.10145 | 0.09586 | -121.9204 | -121.8108 | -0.072605 | -0.23599 | 4.8316 | 3.0571 | 3.1297 | 0.044033 | -0.099281 | 0.19404 | 0.24758 | 0.35713 | 0.13416 | -122.1624 | 121.932 | 122.212 | 122.0687 | 27.0193 | -122.2406
4841.3906 | 122.1359 | -0.09613 | 122.0123 | -0.01778 | -0.060794 | 0.037943 | 0.014768 | -0.01507 | -0.014909 | -0.021518 | 0.000297 | 0.0011281 | 0.059328 | 0.055004 | 0.048756 | -0.040158 | 0.010564 | -0.031301 | 0.070441 | 0.11025 | 0.23354 | -0.12258 | 4.8041 | 27.0926 | 3.0022 | 121.813 | 122.093 | 121.9451 | -0.20078 | -0.026453 | -121.9419 | 0.055972 | 0.064829 | 0.091282 | -121.9021 | -121.7788 | -0.10465 | -0.19937 | 4.9002 | 3.0984 | 3.203 | 0.080656 | -0.067236 | 0.16657 | 0.20638 | 0.32967 | 0.10669 | -122.1349 | 121.9091 | 122.1891 | 122.0412 | 27.1887 | -122.2131
4843.1562 | 122.2 | -0.09613 | 121.9711 | -0.0025182 | -0.060581 | 0.03837 | 0.014981 | -0.014429 | -0.014696 | -0.021518 | 0.000297 | 0.0011281 | 0.059114 | 0.055004 | 0.048969 | -0.044736 | 0.005985 | -0.026723 | 0.070441 | 0.11483 | 0.22438 | -0.12258 | 4.9048 | 27.2849 | 3.0617 | 121.8084 | 122.0884 | 121.9405 | -0.20078 | -0.026453 | -121.9007 | 0.051394 | 0.069407 | 0.09586 | -121.8563 | -121.7467 | -0.10465 | -0.16275 | 5.001 | 3.1579 | 3.2625 | 0.11728 | -0.030616 | 0.16657 | 0.21096 | 0.32051 | 0.10211 | -122.0937 | 121.9045 | 122.1845 | 122.0366 | 27.381 | -122.1719
4844.8594 | 122.1725 | -0.086975 | 122.0078 | -0.0025182 | -0.060581 | 0.038157 | 0.014768 | -0.014642 | -0.014482 | -0.021518 | 0.0007242 | 0.0013417 | 0.059328 | 0.055217 | 0.049397 | -0.040158 | 0.005985 | -0.031301 | 0.07502 | 0.11025 | 0.23354 | -0.12258 | 5.0102 | 27.4955 | 3.1442 | 121.8175 | 122.0976 | 121.9543 | -0.20078 | -0.035608 | -121.9327 | 0.046817 | 0.055674 | 0.091282 | -121.8975 | -121.7742 | -0.1138 | -0.19021 | 5.0971 | 3.2311 | 3.3449 | 0.089813 | -0.053501 | 0.162 | 0.19723 | 0.32051 | 0.09296 | -122.1303 | 121.9045 | 122.1845 | 122.0412 | 27.5825 | -122.2085
4846.625 | 122.2412 | -0.064087 | 121.9803 | -0.01778 | -0.060794 | 0.037943 | 0.014768 | -0.014856 | -0.014696 | -0.021518 | 0.000297 | 0.0011281 | 0.059328 | 0.055217 | 0.049183 | -0.040158 | 0.010564 | -0.035879 | 0.079598 | 0.11483 | 0.23354 | -0.11342 | 5.1017 | 27.7199 | 3.2174 | 121.8221 | 122.093 | 121.9497 | -0.1962 | -0.049338 | -121.9007 | 0.023929 | 0.028208 | 0.077546 | -121.8655 | -121.7467 | -0.13211 | -0.15817 | 5.1658 | 3.2815 | 3.4136 | 0.1127 | -0.030614 | 0.14369 | 0.17892 | 0.29763 | 0.074651 | -122.0937 | 121.8862 | 122.1571 | 122.0138 | 27.784 | -122.1765
4848.3906 | 122.2458 | -0.07782 | 122.0078 | -0.01778 | -0.060581 | 0.03837 | 0.015409 | -0.014642 | -0.014482 | -0.021518 | 0.0007242 | 0.0011281 | 0.059114 | 0.055217 | 0.049183 | -0.040158 | 0.010564 | -0.035879 | 0.070441 | 0.11483 | 0.22438 | -0.118 | 5.2162 | 27.9625 | 3.2998 | 121.8221 | 122.1113 | 121.9497 | -0.20078 | -0.040184 | -121.9373 | 0.037662 | 0.041941 | 0.082125 | -121.8929 | -121.7834 | -0.12296 | -0.18563 | 5.294 | 3.3777 | 3.5006 | 0.10355 | -0.058079 | 0.14826 | 0.19265 | 0.3022 | 0.088384 | -122.1258 | 121.8999 | 122.1891 | 122.0275 | 28.0404 | -122.2085
4850.1562 | 122.1588 | -0.09613 | 122.0444 | -0.0025182 | -0.060794 | 0.03837 | 0.014981 | -0.014856 | -0.014696 | -0.013887 | 0.0009378 | 0.0011281 | 0.059328 | 0.055431 | 0.049183 | -0.040158 | 0.010564 | -0.031301 | 0.07502 | 0.11025 | 0.22896 | -0.12258 | 5.3352 | 28.2373 | 3.3914 | 121.8175 | 122.1113 | 121.9543 | -0.19162 | -0.026453 | -121.9694 | 0.055972 | 0.064829 | 0.091282 | -121.9341 | -121.8154 | -0.095492 | -0.22683 | 5.4314 | 3.4875 | 3.583 | 0.066927 | -0.090123 | 0.17115 | 0.20638 | 0.32509 | 0.10669 | -122.167 | 121.9137 | 122.2074 | 122.0504 | 28.3334 | -122.236
4851.8594 | 122.1634 | -0.1236 | 122.0398 | -0.0025182 | -0.061008 | 0.038157 | 0.014768 | -0.014642 | -0.014482 | -0.013887 | 0.0011516 | 0.0015555 | 0.059755 | 0.055217 | 0.049824 | -0.040158 | 0.001407 | -0.026723 | 0.056706 | 0.11483 | 0.23812 | -0.12258 | 5.4589 | 28.5532 | 3.4738 | 121.8221 | 122.1021 | 121.9497 | -0.20536 | 0.001013 | -121.9831 | 0.083438 | 0.096873 | 0.09586 | -121.925 | -121.8017 | -0.081762 | -0.21768 | 5.5825 | 3.5974 | 3.6792 | 0.062348 | -0.090123 | 0.1803 | 0.23843 | 0.36171 | 0.125 | -122.1624 | 121.9457 | 122.2257 | 122.0733 | 28.6768 | -122.2452
4853.625 | 122.1497 | -0.10071 | 122.0215 | -0.01778 | -0.061008 | 0.038157 | 0.015195 | -0.014642 | -0.014268 | -0.021518 | 0.0007242 | 0.0013417 | 0.059328 | 0.055217 | 0.049824 | -0.031001 | 0.010564 | -0.031301 | 0.061284 | 0.11941 | 0.22896 | -0.12258 | 5.5871 | 28.9103 | 3.5654 | 121.8267 | 122.1021 | 121.9588 | -0.20536 | -0.021875 | -121.9602 | 0.069707 | 0.069407 | 0.091282 | -121.9021 | -121.7925 | -0.10465 | -0.19479 | 5.6878 | 3.6661 | 3.7708 | 0.080659 | -0.062655 | 0.16199 | 0.22012 | 0.32967 | 0.11127 | -122.1441 | 121.9274 | 122.2029 | 122.0595 | 29.011 | -122.2268
4855.3438 | 122.2092 | -0.07782 | 122.0306 | -0.0025182 | -0.061008 | 0.038157 | 0.014768 | -0.014856 | -0.014696 | -0.029148 | 0.0011516 | 0.0013417 | 0.059542 | 0.055645 | 0.049824 | -0.040158 | 0.010564 | -0.035879 | 0.065863 | 0.11025 | 0.23354 | -0.118 | 5.7107 | 29.2858 | 3.6707 | 121.8267 | 122.1067 | 121.9588 | -0.20078 | -0.040184 | -121.9648 | 0.037662 | 0.041941 | 0.082125 | -121.9204 | -121.7971 | -0.12296 | -0.20395 | 5.7885 | 3.7485 | 3.8715 | 0.076081 | -0.071811 | 0.14368 | 0.18807 | 0.31136 | 0.088384 | -122.1486 | 121.9045 | 122.1845 | 122.0366 | 29.3636 | -122.2314
4857.125 | 122.1268 | -0.1236 | 122.0215 | -0.01778 | -0.061008 | 0.03837 | 0.014768 | -0.014642 | -0.014696 | -0.021518 | 0.0011516 | 0.0013417 | 0.059755 | 0.055431 | 0.050038 | -0.044736 | 0.005985 | -0.031301 | 0.070441 | 0.11025 | 0.23354 | -0.12258 | 5.8343 | 29.6109 | 3.7577 | 121.8313 | 122.1113 | 121.9726 | -0.20078 | 0.001013 | -121.951 | 0.07886 | 0.092295 | 0.091282 | -121.9112 | -121.7879 | -0.077183 | -0.19021 | 5.9579 | 3.8813 | 3.9585 | 0.089816 | -0.048919 | 0.19404 | 0.23385 | 0.35713 | 0.12958 | -122.1441 | 121.9549 | 122.2349 | 122.0962 | 29.7345 | -122.2223
4858.8281 | 122.1222 | -0.11902 | 122.0444 | -0.010149 | -0.060794 | 0.03837 | 0.014981 | -0.014856 | -0.014696 | -0.013887 | 0.0015788 | 0.0015555 | 0.059328 | 0.055858 | 0.049824 | -0.040158 | 0.001407 | -0.026723 | 0.070441 | 0.11025 | 0.22896 | -0.12258 | 5.9625 | 29.9634 | 3.8539 | 121.8267 | 122.1159 | 121.9634 | -0.20536 | -0.003564 | -121.9739 | 0.078861 | 0.092296 | 0.09586 | -121.9341 | -121.8154 | -0.086339 | -0.21768 | 6.0815 | 3.9729 | 4.0592 | 0.071505 | -0.080966 | 0.18946 | 0.22927 | 0.34798 | 0.12043 | -122.167 | 121.9457 | 122.2349 | 122.0824 | 30.0825 | -122.2497
4860.5938 | 122.1085 | -0.10986 | 122.0627 | -0.01778 | -0.060794 | 0.038157 | 0.014768 | -0.014856 | -0.014696 | -0.021518 | 0.0017924 | 0.0013417 | 0.059542 | 0.055645 | 0.050465 | -0.040158 | 0.010564 | -0.031301 | 0.070441 | 0.11483 | 0.22896 | -0.12258 | 6.1045 | 30.3297 | 3.9592 | 121.8313 | 122.1159 | 121.9726 | -0.20078 | -0.01272 | -121.9922 | 0.069705 | 0.078562 | 0.091282 | -121.9479 | -121.8337 | -0.090916 | -0.23141 | 6.2143 | 4.069 | 4.16 | 0.053195 | -0.090118 | 0.1803 | 0.2247 | 0.33882 | 0.12043 | -122.1853 | 121.9411 | 122.2257 | 122.0824 | 30.4396 | -122.2635
4862.3594 | 122.2458 | -0.073242 | 121.9894 | -0.01778 | -0.060581 | 0.03837 | 0.014981 | -0.014642 | -0.014696 | -0.021518 | 0.0015788 | 0.0013417 | 0.059755 | 0.055645 | 0.050251 | -0.044736 | 0.005985 | -0.035879 | 0.065863 | 0.11483 | 0.23354 | -0.12716 | 6.2601 | 30.6548 | 4.0599 | 121.8359 | 122.1205 | 121.968 | -0.20078 | -0.05392 | -121.9236 | 0.028506 | 0.037363 | 0.091283 | -121.8746 | -121.7559 | -0.12754 | -0.15359 | 6.3334 | 4.1332 | 4.2607 | 0.13102 | -0.021455 | 0.13911 | 0.18807 | 0.30678 | 0.079227 | -122.1166 | 121.9091 | 122.1937 | 122.0412 | 30.7281 | -122.1902
4864.0781 | 122.2366 | -0.091553 | 122.0261 | -0.01778 | -0.060794 | 0.03837 | 0.014981 | -0.014429 | -0.014055 | -0.029148 | 0.002006 | 0.0017691 | 0.059969 | 0.055858 | 0.050465 | -0.040158 | 0.010564 | -0.031301 | 0.070441 | 0.11025 | 0.23354 | -0.118 | 6.4158 | 30.9845 | 4.1561 | 121.8313 | 122.1067 | 121.968 | -0.20078 | -0.026451 | -121.9556 | 0.051395 | 0.060252 | 0.086703 | -121.9158 | -121.7925 | -0.10923 | -0.19479 | 6.5074 | 4.2476 | 4.3568 | 0.080659 | -0.058076 | 0.16199 | 0.20181 | 0.32509 | 0.10212 | -122.1441 | 121.9228 | 122.1983 | 122.0595 | 31.076 | -122.2268
4865.8438 | 122.1497 | -0.10071 | 122.0764 | -0.010149 | -0.060794 | 0.038584 | 0.014768 | -0.014856 | -0.014268 | -0.021518 | 0.0022198 | 0.0019827 | 0.060183 | 0.056072 | 0.050892 | -0.040158 | 0.005985 | -0.022144 | 0.070441 | 0.11483 | 0.23354 | -0.12258 | 6.5944 | 31.2913 | 4.2705 | 121.845 | 122.1113 | 121.9726 | -0.20994 | -0.021875 | -122.006 | 0.06055 | 0.078564 | 0.10044 | -121.9616 | -121.8429 | -0.10923 | -0.23141 | 6.6951 | 4.3712 | 4.4805 | 0.034884 | -0.10385 | 0.17115 | 0.21554 | 0.33425 | 0.10669 | -122.199 | 121.9457 | 122.212 | 122.0733 | 31.392 | -122.2864
4867.6094 | 122.2458 | -0.068665 | 122.0444 | -0.0025182 | -0.061008 | 0.03837 | 0.014981 | -0.014642 | -0.014482 | -0.013887 | 0.0022198 | 0.0017691 | 0.060183 | 0.056072 | 0.050465 | -0.040158 | 0.005985 | -0.035879 | 0.070441 | 0.11483 | 0.23812 | -0.118 | 6.7546 | 31.653 | 4.385 | 121.8313 | 122.1205 | 121.968 | -0.20078 | -0.049339 | -121.9739 | 0.028507 | 0.032786 | 0.082125 | -121.9295 | -121.8063 | -0.13211 | -0.2131 | 6.8233 | 4.4537 | 4.5858 | 0.076084 | -0.076387 | 0.13911 | 0.1835 | 0.30678 | 0.07465 | -122.1624 | 121.8999 | 122.1891 | 122.0367 | 31.7216 | -122.2452
4869.3281 | 122.2275 | -0.068665 | 122.0032 | -0.025411 | -0.061008 | 0.03837 | 0.014981 | -0.014642 | -0.014482 | -0.021518 | 0.002647 | 0.0015555 | 0.059969 | 0.056072 | 0.050892 | -0.044736 | 0.005985 | -0.035879 | 0.061284 | 0.11025 | 0.23354 | -0.12258 | 6.9241 | 31.9369 | 4.4903 | 121.8313 | 122.1205 | 121.9726 | -0.20536 | -0.053918 | -121.9419 | 0.023929 | 0.032786 | 0.086704 | -121.8929 | -121.7696 | -0.13669 | -0.1719 | 6.9927 | 4.559 | 4.6957 | 0.11728 | -0.030609 | 0.12995 | 0.17892 | 0.3022 | 0.07465 | -122.1258 | 121.8999 | 122.1891 | 122.0412 | 32.0055 | -122.2085
4871.0938 | 122.1817 | -0.10071 | 122.0764 | -0.010149 | -0.060794 | 0.037943 | 0.015195 | -0.014856 | -0.014268 | -0.021518 | 0.002647 | 0.0017691 | 0.060183 | 0.056499 | 0.050679 | -0.040158 | 0.005985 | -0.031301 | 0.065863 | 0.11483 | 0.22896 | -0.118 | 7.1072 | 32.2299 | 4.6094 | 121.8313 | 122.125 | 121.968 | -0.20536 | -0.017296 | -122.0106 | 0.06055 | 0.069407 | 0.086703 | -121.9616 | -121.8475 | -0.10465 | -0.24514 | 7.2079 | 4.7101 | 4.8147 | 0.04862 | -0.10843 | 0.16657 | 0.21554 | 0.32967 | 0.10669 | -122.1944 | 121.932 | 122.2257 | 122.0687 | 32.3306 | -122.2818
4872.7969 | 122.1725 | -0.11444 | 122.049 | -0.010149 | -0.061008 | 0.038157 | 0.014981 | -0.014642 | -0.014268 | -0.013887 | 0.002647 | 0.0017691 | 0.060183 | 0.056499 | 0.050892 | -0.044736 | 0.010564 | -0.031301 | 0.070441 | 0.11025 | 0.23812 | -0.12716 | 7.2629 | 32.5046 | 4.7284 | 121.8404 | 122.125 | 121.9726 | -0.20536 | -0.012721 | -121.9785 | 0.069705 | 0.08314 | 0.095861 | -121.9387 | -121.8108 | -0.090917 | -0.20852 | 7.3773 | 4.8428 | 4.9338 | 0.076086 | -0.076385 | 0.18488 | 0.22469 | 0.35256 | 0.12501 | -122.1761 | 121.9549 | 122.2395 | 122.087 | 32.6191 | -122.2543
4874.5781 | 122.2641 | -0.091553 | 122.0078 | -0.010149 | -0.060794 | 0.038157 | 0.014981 | -0.015283 | -0.014268 | -0.013887 | 0.0030742 | 0.0017691 | 0.060183 | 0.056499 | 0.05132 | -0.044736 | 0.010564 | -0.035879 | 0.065863 | 0.11025 | 0.22438 | -0.12716 | 7.4369 | 32.8114 | 4.8429 | 121.8404 | 122.1205 | 121.9726 | -0.20994 | -0.035609 | -121.9419 | 0.046817 | 0.055674 | 0.091283 | -121.8975 | -121.7834 | -0.11838 | -0.16732 | 7.5284 | 4.9344 | 5.0528 | 0.11271 | -0.035186 | 0.15742 | 0.20181 | 0.31593 | 0.10212 | -122.1349 | 121.932 | 122.212 | 122.0641 | 32.9029 | -122.2177
4876.3438 | 122.2275 | -0.082397 | 121.9986 | -0.010149 | -0.061222 | 0.038157 | 0.015195 | -0.014856 | -0.014055 | -0.021518 | 0.0032878 | 0.0019827 | 0.059969 | 0.056713 | 0.051533 | -0.03558 | -0.003172 | -0.031301 | 0.065863 | 0.11941 | 0.23354 | -0.11342 | 7.62 | 33.0907 | 4.9573 | 121.8359 | 122.125 | 121.9726 | -0.20994 | -0.031028 | -121.9327 | 0.046817 | 0.051096 | 0.082124 | -121.8792 | -121.7651 | -0.12754 | -0.16274 | 7.7024 | 5.0397 | 5.1673 | 0.12644 | -0.026031 | 0.14826 | 0.20181 | 0.31593 | 0.079225 | -122.112 | 121.9182 | 122.2074 | 122.055 | 33.1731 | -122.2085
4878.1094 | 122.2229 | -0.09613 | 122.049 | -0.025411 | -0.060794 | 0.038584 | 0.014768 | -0.014856 | -0.014055 | -0.021518 | 0.0030742 | 0.0017691 | 0.060396 | 0.056499 | 0.051747 | -0.044736 | 0.001407 | -0.026723 | 0.065863 | 0.11483 | 0.22896 | -0.12716 | 7.8032 | 33.3883 | 5.0855 | 121.8404 | 122.125 | 121.9771 | -0.20078 | -0.031032 | -121.9831 | 0.051394 | 0.069407 | 0.10044 | -121.9341 | -121.82 | -0.10465 | -0.20852 | 7.8993 | 5.1817 | 5.2863 | 0.076086 | -0.071807 | 0.16199 | 0.21096 | 0.32509 | 0.097537 | -122.1761 | 121.9366 | 122.2212 | 122.0733 | 33.4844 | -122.2497
4879.8125 | 122.2229 | -0.10986 | 122.0306 | -0.010149 | -0.061008 | 0.03837 | 0.014981 | -0.014642 | -0.014055 | -0.021518 | 0.0035016 | 0.0021965 | 0.060183 | 0.056499 | 0.05196 | -0.044736 | -0.003172 | -0.040457 | 0.065863 | 0.11941 | 0.23354 | -0.118 | 7.9772 | 33.6401 | 5.1954 | 121.845 | 122.125 | 121.9726 | -0.1962 | -0.008141 | -121.9648 | 0.065127 | 0.069406 | 0.077547 | -121.9112 | -121.7971 | -0.086337 | -0.18563 | 8.087 | 5.3053 | 5.3916 | 0.094396 | -0.058075 | 0.17573 | 0.22927 | 0.3434 | 0.10669 | -122.1486 | 121.9549 | 122.2349 | 122.0824 | 33.75 | -122.2268
4881.5781 | 122.1863 | -0.091553 | 122.0535 | -0.0025182 | -0.061222 | 0.038157 | 0.014981 | -0.01507 | -0.014268 | -0.021518 | 0.0035016 | 0.0019827 | 0.060396 | 0.057354 | 0.052388 | -0.040158 | 0.005985 | -0.026723 | 0.061284 | 0.11483 | 0.22896 | -0.118 | 8.1649 | 33.8737 | 5.3191 | 121.845 | 122.1159 | 121.9771 | -0.20078 | -0.026451 | -121.9922 | 0.051395 | 0.06483 | 0.091281 | -121.9387 | -121.8246 | -0.10923 | -0.20852 | 8.2564 | 5.4106 | 5.5198 | 0.06235 | -0.076385 | 0.15284 | 0.20638 | 0.32051 | 0.097538 | -122.1715 | 121.9366 | 122.2074 | 122.0687 | 33.9652 | -122.2543
4883.3281 | 122.2458 | -0.09613 | 122.0261 | -0.01778 | -0.061008 | 0.037943 | 0.014768 | -0.01507 | -0.013841 | -0.021518 | 0.0039288 | 0.0017691 | 0.060824 | 0.05714 | 0.05196 | -0.03558 | 0.001407 | -0.031301 | 0.065863 | 0.11025 | 0.23812 | -0.12258 | 8.3526 | 34.0385 | 5.4289 | 121.8359 | 122.1296 | 121.9726 | -0.20994 | -0.026453 | -121.9602 | 0.06055 | 0.064829 | 0.091282 | -121.9158 | -121.7879 | -0.11381 | -0.19021 | 8.4487 | 5.5251 | 5.6389 | 0.10355 | -0.053497 | 0.16199 | 0.20638 | 0.33425 | 0.097537 | -122.1486 | 121.932 | 122.2257 | 122.0687 | 34.1346 | -122.236
4885.0469 | 122.2275 | -0.068665 | 122.0352 | -0.010149 | -0.061222 | 0.03837 | 0.014981 | -0.014856 | -0.013841 | -0.021518 | 0.0039288 | 0.0024101 | 0.061037 | 0.056927 | 0.052174 | -0.040158 | 0.010564 | -0.031301 | 0.070441 | 0.11483 | 0.22896 | -0.118 | 8.5358 | 34.2125 | 5.5617 | 121.8404 | 122.1296 | 121.9726 | -0.20994 | -0.049339 | -121.9648 | 0.028507 | 0.037364 | 0.086703 | -121.9204 | -121.8063 | -0.14127 | -0.19479 | 8.6044 | 5.6304 | 5.7717 | 0.094397 | -0.062652 | 0.13911 | 0.1835 | 0.29762 | 0.079229 | -122.1532 | 121.9091 | 122.1983 | 122.0412 | 34.2811 | -122.2452
4886.8125 | 122.2 | -0.11902 | 122.0764 | -0.0025182 | -0.061222 | 0.03837 | 0.014768 | -0.014642 | -0.013841 | -0.013887 | 0.0041424 | 0.0026237 | 0.06061 | 0.05714 | 0.052815 | -0.03558 | 0.010564 | -0.031301 | 0.070441 | 0.11025 | 0.23354 | -0.118 | 8.7235 | 34.4185 | 5.6991 | 121.8359 | 122.1205 | 121.9817 | -0.20536 | 0.001015 | -122.006 | 0.083439 | 0.087718 | 0.086703 | -121.9662 | -121.8429 | -0.086339 | -0.24056 | 8.8425 | 5.8181 | 5.9044 | 0.044041 | -0.094694 | 0.18946 | 0.22927 | 0.35256 | 0.12958 | -122.1944 | 121.9549 | 122.2395 | 122.1007 | 34.5375 | -122.2818
4888.5781 | 122.1542 | -0.11444 | 122.0718 | -0.0025182 | -0.061435 | 0.037943 | 0.014981 | -0.014856 | -0.014055 | -0.021518 | 0.0041424 | 0.0026237 | 0.061251 | 0.057354 | 0.052815 | -0.040158 | 0.005985 | -0.031301 | 0.061284 | 0.10567 | 0.23354 | -0.13174 | 8.9158 | 34.5605 | 5.8273 | 121.8404 | 122.125 | 121.9863 | -0.20536 | -0.0173 | -122.0106 | 0.074283 | 0.08314 | 0.10044 | -121.9662 | -121.8383 | -0.090917 | -0.23141 | 9.0302 | 5.9417 | 6.0326 | 0.053198 | -0.085538 | 0.17572 | 0.22012 | 0.34798 | 0.12043 | -122.2036 | 121.9549 | 122.2395 | 122.1007 | 34.6749 | -122.2772
4890.2812 | 122.168 | -0.12817 | 122.0535 | -0.010149 | -0.061222 | 0.038157 | 0.015195 | -0.01507 | -0.013841 | -0.013887 | 0.0047834 | 0.0019827 | 0.061037 | 0.05714 | 0.053029 | -0.03558 | 0.010564 | -0.031301 | 0.079598 | 0.11025 | 0.22896 | -0.118 | 9.0944 | 34.7161 | 5.9601 | 121.8496 | 122.125 | 121.9817 | -0.20536 | 0.01017 | -121.9739 | 0.092594 | 0.096873 | 0.086703 | -121.9433 | -121.8246 | -0.077184 | -0.20394 | 9.2225 | 6.0882 | 6.1654 | 0.071508 | -0.071806 | 0.20777 | 0.23843 | 0.35713 | 0.13874 | -122.1715 | 121.9778 | 122.2532 | 122.1099 | 34.8443 | -122.2589
4892.0469 | 122.2641 | -0.064087 | 122.0169 | -0.01778 | -0.061008 | 0.03837 | 0.014981 | -0.014856 | -0.013841 | -0.021518 | 0.0047834 | 0.0028375 | 0.060824 | 0.057354 | 0.053456 | -0.03558 | 0.005985 | -0.035879 | 0.070441 | 0.11483 | 0.23812 | -0.12258 | 9.2775 | 34.8352 | 6.0883 | 121.8404 | 122.125 | 121.9863 | -0.20536 | -0.058496 | -121.9465 | 0.028507 | 0.028208 | 0.086704 | -121.9021 | -121.7788 | -0.14127 | -0.17648 | 9.3416 | 6.1524 | 6.2936 | 0.10813 | -0.030607 | 0.13453 | 0.17892 | 0.3022 | 0.070072 | -122.1395 | 121.9045 | 122.1891 | 122.0504 | 34.8993 | -122.2223
4893.75 | 122.1588 | -0.1236 | 122.0718 | -0.010149 | -0.061649 | 0.03837 | 0.014768 | -0.014642 | -0.013841 | -0.013887 | 0.0047834 | 0.0026237 | 0.060824 | 0.057568 | 0.053029 | -0.03558 | 0.005985 | -0.035879 | 0.07502 | 0.11941 | 0.23354 | -0.11342 | 9.4469 | 34.9313 | 6.2119 | 121.8542 | 122.1342 | 121.9817 | -0.20536 | 0.010171 | -121.9968 | 0.088016 | 0.087717 | 0.077546 | -121.9524 | -121.8383 | -0.081762 | -0.21767 | 9.5705 | 6.3355 | 6.4173 | 0.062355 | -0.090116 | 0.19862 | 0.24301 | 0.35713 | 0.12958 | -122.1853 | 121.9778 | 122.2578 | 122.1053 | 35.0549 | -122.2772
4895.5312 | 122.1497 | -0.13275 | 122.0673 | -0.010149 | -0.061435 | 0.038584 | 0.015195 | -0.01507 | -0.013628 | -0.013887 | 0.0052106 | 0.0026237 | 0.061037 | 0.057781 | 0.053456 | -0.03558 | 0.015142 | -0.035879 | 0.065863 | 0.11483 | 0.23812 | -0.12716 | 9.6163 | 34.9954 | 6.3447 | 121.8496 | 122.125 | 121.9863 | -0.20994 | 0.005589 | -122.0014 | 0.097171 | 0.096872 | 0.091283 | -121.9524 | -121.8291 | -0.077186 | -0.21767 | 9.7491 | 6.4774 | 6.5546 | 0.057775 | -0.080961 | 0.19861 | 0.24758 | 0.37087 | 0.14789 | -122.1944 | 121.9823 | 122.2578 | 122.1191 | 35.1282 | -122.2772
4897.2969 | 122.1542 | -0.11444 | 122.0581 | -0.0025182 | -0.061649 | 0.03837 | 0.014981 | -0.014642 | -0.013841 | -0.036779 | 0.0054242 | 0.0028375 | 0.061037 | 0.057781 | 0.053456 | -0.044736 | 0.005985 | -0.031301 | 0.070441 | 0.10567 | 0.23354 | -0.13174 | 9.7812 | 35.0824 | 6.482 | 121.8496 | 122.125 | 121.9863 | -0.20536 | -0.0173 | -121.9877 | 0.069705 | 0.08314 | 0.10044 | -121.9524 | -121.8246 | -0.090917 | -0.20852 | 9.8956 | 6.5965 | 6.6874 | 0.066931 | -0.071805 | 0.18488 | 0.22012 | 0.34798 | 0.12043 | -122.1898 | 121.964 | 122.2395 | 122.1007 | 35.1969 | -122.2635
4899.0625 | 122.1588 | -0.13733 | 122.0856 | -0.01778 | -0.061649 | 0.03837 | 0.014981 | -0.014429 | -0.013841 | -0.021518 | 0.0054242 | 0.0026237 | 0.061251 | 0.057995 | 0.053883 | -0.044736 | 0.010564 | -0.031301 | 0.070441 | 0.11483 | 0.23354 | -0.12258 | 9.9231 | 34.9771 | 6.6102 | 121.845 | 122.1296 | 121.9863 | -0.20536 | 0.014746 | -122.0151 | 0.092593 | 0.10603 | 0.091282 | -121.9707 | -121.852 | -0.068029 | -0.24056 | 10.0604 | 6.7476 | 6.8156 | 0.044043 | -0.099271 | 0.20777 | 0.25216 | 0.37087 | 0.14789 | -122.2082 | 121.9823 | 122.2669 | 122.1236 | 35.1145 | -122.2909
4900.8281 | 122.1771 | -0.11444 | 122.0535 | -0.010149 | -0.061008 | 0.03837 | 0.014981 | -0.014429 | -0.013414 | -0.029148 | 0.0054242 | 0.0032647 | 0.061037 | 0.058209 | 0.053456 | -0.03558 | 0.010564 | -0.035879 | 0.070441 | 0.11941 | 0.23354 | -0.12258 | 10.0788 | 35.0092 | 6.743 | 121.8496 | 122.1433 | 121.9955 | -0.1962 | -0.008142 | -121.9831 | 0.078861 | 0.078562 | 0.086704 | -121.9341 | -121.82 | -0.081759 | -0.20394 | 10.1932 | 6.8575 | 6.9392 | 0.089822 | -0.05807 | 0.18488 | 0.23385 | 0.34798 | 0.12501 | -122.1761 | 121.964 | 122.2578 | 122.1099 | 35.1236 | -122.2497
4902.5938 | 122.2412 | -0.073242 | 122.049 | -0.010149 | -0.061008 | 0.03837 | 0.015195 | -0.014642 | -0.013841 | -0.036779 | 0.0058516 | 0.0028375 | 0.061464 | 0.058422 | 0.053883 | -0.03558 | 0.010564 | -0.031301 | 0.07502 | 0.11483 | 0.23354 | -0.11342 | 10.2345 | 35.0183 | 6.8804 | 121.8496 | 122.1342 | 121.9909 | -0.20536 | -0.040183 | -121.9739 | 0.037662 | 0.041941 | 0.082124 | -121.9341 | -121.8154 | -0.13212 | -0.19936 | 10.3077 | 6.9536 | 7.0858 | 0.085243 | -0.058071 | 0.14826 | 0.18807 | 0.30678 | 0.083806 | -122.1624 | 121.9228 | 122.2074 | 122.0641 | 35.0916 | -122.2543
4904.3125 | 122.2412 | -0.064087 | 122.0215 | -0.010149 | -0.061649 | 0.038157 | 0.014981 | -0.014642 | -0.013628 | -0.029148 | 0.005638 | 0.0028375 | 0.061678 | 0.058209 | 0.054524 | -0.040158 | 0.015142 | -0.035879 | 0.070441 | 0.11941 | 0.23354 | -0.118 | 10.3993 | 35.0504 | 7.0132 | 121.8542 | 122.1342 | 121.9863 | -0.20536 | -0.053917 | -121.951 | 0.023929 | 0.028208 | 0.082125 | -121.9021 | -121.7879 | -0.14127 | -0.16732 | 10.4634 | 7.0773 | 7.2185 | 0.11271 | -0.035184 | 0.13453 | 0.1835 | 0.29763 | 0.079229 | -122.1395 | 121.9183 | 122.1983 | 122.0504 | 35.1145 | -122.2268
4906.0781 | 122.287 | -0.064087 | 122.0398 | -0.010149 | -0.061008 | 0.038157 | 0.014981 | -0.014642 | -0.013414 | -0.029148 | 0.005638 | 0.0028375 | 0.061678 | 0.058422 | 0.054097 | -0.040158 | 0.010564 | -0.031301 | 0.070441 | 0.11941 | 0.23354 | -0.12716 | 10.5504 | 35.0779 | 7.1551 | 121.8542 | 122.1296 | 121.9955 | -0.1962 | -0.063075 | -121.9694 | 0.023929 | 0.032786 | 0.095861 | -121.9204 | -121.8063 | -0.13211 | -0.18563 | 10.6145 | 7.2192 | 7.3513 | 0.089819 | -0.044337 | 0.13453 | 0.1835 | 0.29763 | 0.074651 | -122.167 | 121.9183 | 122.1937 | 122.0595 | 35.1419 | -122.236
4907.8438 | 122.1634 | -0.13275 | 122.081 | -0.0025182 | -0.061435 | 0.03837 | 0.015195 | -0.014856 | -0.013628 | -0.021518 | 0.0060652 | 0.0030511 | 0.061464 | 0.058209 | 0.054311 | -0.040158 | 0.010564 | -0.035879 | 0.061284 | 0.11941 | 0.23354 | -0.118 | 10.7198 | 35.1557 | 7.3016 | 121.8542 | 122.1342 | 121.9909 | -0.20994 | 0.014747 | -122.0197 | 0.092593 | 0.096872 | 0.082125 | -121.9616 | -121.8475 | -0.077186 | -0.22683 | 10.8526 | 7.4344 | 7.5116 | 0.053199 | -0.090115 | 0.19404 | 0.25216 | 0.36629 | 0.14331 | -122.199 | 121.9869 | 122.2669 | 122.1236 | 35.2884 | -122.2909
4909.625 | 122.2366 | -0.086975 | 122.0261 | -0.010149 | -0.061222 | 0.038157 | 0.015195 | -0.014642 | -0.013414 | -0.029148 | 0.0064924 | 0.0030511 | 0.061678 | 0.058422 | 0.054524 | -0.03558 | 0.010564 | -0.035879 | 0.070441 | 0.11483 | 0.24269 | -0.11342 | 10.8755 | 35.1923 | 7.4527 | 121.8587 | 122.1342 | 121.9863 | -0.20078 | -0.02645 | -121.9556 | 0.051395 | 0.051096 | 0.077546 | -121.9112 | -121.7834 | -0.1138 | -0.16732 | 10.9625 | 7.5397 | 7.6535 | 0.10813 | -0.039762 | 0.15742 | 0.20181 | 0.32967 | 0.097539 | -122.1395 | 121.9457 | 122.2212 | 122.0733 | 35.2793 | -122.2268
4911.3438 | 122.2549 | -0.068665 | 122.0123 | -0.010149 | -0.061435 | 0.038157 | 0.014768 | -0.014856 | -0.013414 | -0.029148 | 0.0064924 | 0.0030511 | 0.061678 | 0.058636 | 0.054738 | -0.03558 | 0.001407 | -0.035879 | 0.065863 | 0.11025 | 0.23812 | -0.12258 | 11.0357 | 35.2152 | 7.5947 | 121.8542 | 122.1342 | 121.9909 | -0.20536 | -0.053918 | -121.9465 | 0.033085 | 0.032786 | 0.086704 | -121.9021 | -121.7742 | -0.13669 | -0.15816 | 11.1044 | 7.6633 | 7.8 | 0.12186 | -0.02145 | 0.13453 | 0.17892 | 0.30678 | 0.070072 | -122.1349 | 121.9228 | 122.2029 | 122.0595 | 35.2839 | -122.2177
4913.1094 | 122.1634 | -0.11444 | 122.0673 | -0.01778 | -0.061435 | 0.037943 | 0.015409 | -0.014642 | -0.013414 | -0.021518 | 0.0067062 | 0.0032647 | 0.061892 | 0.058636 | 0.054952 | -0.03558 | 0.001407 | -0.031301 | 0.07502 | 0.11025 | 0.23812 | -0.118 | 11.2052 | 35.2152 | 7.7503 | 121.8542 | 122.1433 | 121.9909 | -0.20078 | -0.003563 | -121.9922 | 0.078861 | 0.08314 | 0.086703 | -121.957 | -121.8291 | -0.086338 | -0.21309 | 11.3196 | 7.8648 | 7.9511 | 0.076089 | -0.076382 | 0.18946 | 0.22469 | 0.35256 | 0.11585 | -122.1853 | 121.9686 | 122.2578 | 122.1053 | 35.3297 | -122.268
4914.875 | 122.1817 | -0.10071 | 122.049 | -0.01778 | -0.061222 | 0.038157 | 0.014981 | -0.014856 | -0.013414 | -0.013887 | 0.0069198 | 0.0036921 | 0.062105 | 0.05885 | 0.055379 | -0.040158 | 0.015142 | -0.035879 | 0.065863 | 0.11483 | 0.23354 | -0.118 | 11.37 | 35.2244 | 7.906 | 121.8587 | 122.1388 | 121.9955 | -0.20536 | -0.017296 | -121.9831 | 0.06055 | 0.064829 | 0.082125 | -121.9341 | -121.8154 | -0.10465 | -0.19021 | 11.4707 | 8.0067 | 8.1114 | 0.089821 | -0.053492 | 0.16657 | 0.21554 | 0.33425 | 0.11585 | -122.167 | 121.9595 | 122.2395 | 122.0962 | 35.3251 | -122.2543
4916.6562 | 122.2 | -0.11902 | 122.0856 | -0.010149 | -0.061435 | 0.038157 | 0.014768 | -0.01507 | -0.0132 | -0.021518 | 0.007347 | 0.0032647 | 0.062533 | 0.059277 | 0.055379 | -0.040158 | 0.005985 | -0.035879 | 0.061284 | 0.11483 | 0.22896 | -0.12716 | 11.5394 | 35.2656 | 8.0754 | 121.8542 | 122.1433 | 121.9955 | -0.20078 | -0.008143 | -122.0243 | 0.078861 | 0.08314 | 0.091283 | -121.9707 | -121.8566 | -0.08176 | -0.2314 | 11.6584 | 8.1945 | 8.2762 | 0.057779 | -0.090113 | 0.1803 | 0.23385 | 0.34798 | 0.125 | -122.2127 | 121.9732 | 122.2624 | 122.1145 | 35.3846 | -122.2863
4918.3594 | 122.2366 | -0.09613 | 122.0352 | -0.01778 | -0.061435 | 0.037943 | 0.014768 | -0.014642 | -0.012987 | -0.036779 | 0.0071334 | 0.0034783 | 0.062105 | 0.059277 | 0.055379 | -0.044736 | 0.010564 | -0.031301 | 0.070441 | 0.11483 | 0.23354 | -0.12716 | 11.7042 | 35.3205 | 8.2265 | 121.8587 | 122.1342 | 121.9955 | -0.20536 | -0.031032 | -121.9648 | 0.051394 | 0.064829 | 0.095861 | -121.9204 | -121.8017 | -0.10923 | -0.17647 | 11.8004 | 8.3227 | 8.4319 | 0.098976 | -0.039759 | 0.16657 | 0.21096 | 0.32967 | 0.10669 | -122.1624 | 121.9549 | 122.2303 | 122.0916 | 35.4167 | -122.2406
4920.125 | 122.1405 | -0.12817 | 122.0673 | -0.010149 | -0.061435 | 0.03837 | 0.014981 | -0.01507 | -0.0132 | -0.021518 | 0.0075606 | 0.0032647 | 0.062319 | 0.059277 | 0.055806 | -0.040158 | 0.005985 | -0.031301 | 0.065863 | 0.11483 | 0.23354 | -0.12258 | 11.8736 | 35.3159 | 8.4005 | 121.8587 | 122.1388 | 122.0046 | -0.20078 | 0.005591 | -122.0014 | 0.088016 | 0.096873 | 0.091282 | -121.9524 | -121.8337 | -0.072605 | -0.20852 | 12.0018 | 8.5287 | 8.6013 | 0.07151 | -0.062646 | 0.19404 | 0.24301 | 0.36171 | 0.13416 | -122.1898 | 121.9869 | 122.2669 | 122.1328 | 35.4441 | -122.268
4921.8281 | 122.2321 | -0.073242 | 122.0444 | -0.01778 | -0.061435 | 0.03837 | 0.014981 | -0.014856 | -0.0132 | -0.021518 | 0.0077742 | 0.0034783 | 0.062319 | 0.059277 | 0.05602 | -0.044736 | 0.005985 | -0.026723 | 0.07502 | 0.11941 | 0.23354 | -0.12716 | 12.0522 | 35.3572 | 8.5516 | 121.8633 | 122.1342 | 121.9955 | -0.20078 | -0.05392 | -121.9694 | 0.028506 | 0.046519 | 0.10044 | -121.925 | -121.8108 | -0.12754 | -0.18105 | 12.1255 | 8.6249 | 8.7524 | 0.08982 | -0.048915 | 0.14826 | 0.19265 | 0.30678 | 0.079227 | -122.1715 | 121.9366 | 122.2074 | 122.0687 | 35.4304 | -122.2452
4923.5938 | 122.168 | -0.10529 | 122.0764 | -0.01778 | -0.060794 | 0.038157 | 0.015195 | -0.014856 | -0.012987 | -0.021518 | 0.0077742 | 0.0034783 | 0.062105 | 0.059277 | 0.056234 | -0.040158 | 0.010564 | -0.035879 | 0.07502 | 0.11941 | 0.23812 | -0.12258 | 12.2079 | 35.348 | 8.7165 | 121.8633 | 122.1388 | 121.9955 | -0.20536 | -0.017297 | -122.0014 | 0.065128 | 0.069407 | 0.086704 | -121.957 | -121.8383 | -0.10007 | -0.21309 | 12.3132 | 8.8217 | 8.9218 | 0.062355 | -0.080958 | 0.18031 | 0.2247 | 0.3434 | 0.11585 | -122.199 | 121.9686 | 122.2441 | 122.1007 | 35.4533 | -122.2818
4925.3594 | 122.168 | -0.10529 | 122.0947 | -0.010149 | -0.061222 | 0.037943 | 0.014981 | -0.014856 | -0.012987 | -0.021518 | 0.0082016 | 0.0036921 | 0.062533 | 0.059918 | 0.056234 | -0.044736 | 0.005985 | -0.031301 | 0.07502 | 0.11941 | 0.23354 | -0.12716 | 12.3544 | 35.3755 | 8.8676 | 121.8542 | 122.1433 | 121.9909 | -0.20078 | -0.021876 | -122.0197 | 0.06055 | 0.073985 | 0.095861 | -121.9753 | -121.8612 | -0.095493 | -0.24056 | 12.4597 | 8.9728 | 9.0683 | 0.048623 | -0.10385 | 0.18031 | 0.2247 | 0.33882 | 0.11127 | -122.2219 | 121.9595 | 122.2486 | 122.0962 | 35.4808 | -122.2955
4927.0625 | 122.2641 | -0.07782 | 122.049 | -0.010149 | -0.061008 | 0.038157 | 0.015195 | -0.01507 | -0.0132 | -0.021518 | 0.0082016 | 0.0039057 | 0.062533 | 0.059918 | 0.056234 | -0.040158 | 0.005985 | -0.031301 | 0.065863 | 0.11025 | 0.22896 | -0.12258 | 12.5421 | 35.4396 | 9.0324 | 121.8587 | 122.1388 | 121.9909 | -0.20536 | -0.044763 | -121.9831 | 0.037662 | 0.046519 | 0.091282 | -121.9387 | -121.82 | -0.12754 | -0.19021 | 12.62 | 9.1102 | 9.2377 | 0.089821 | -0.058071 | 0.14368 | 0.18807 | 0.30678 | 0.083805 | -122.1715 | 121.9366 | 122.2166 | 122.0687 | 35.5174 | -122.2543
4928.8281 | 122.1542 | -0.12817 | 122.0947 | -0.01778 | -0.061222 | 0.03837 | 0.014981 | -0.014642 | -0.012987 | -0.029148 | 0.0086288 | 0.0039057 | 0.06296 | 0.060132 | 0.056234 | -0.040158 | 0.010564 | -0.031301 | 0.065863 | 0.11941 | 0.23354 | -0.12716 | 12.7344 | 35.4442 | 9.2018 | 121.8587 | 122.1388 | 121.9955 | -0.20536 | 0.001012 | -122.0289 | 0.088016 | 0.096873 | 0.095861 | -121.9753 | -121.8612 | -0.077184 | -0.23598 | 12.8626 | 9.33 | 9.4072 | 0.044044 | -0.099269 | 0.19404 | 0.24758 | 0.36171 | 0.13874 | -122.2219 | 121.9869 | 122.2669 | 122.1236 | 35.5723 | -122.3001
4930.6094 | 122.2 | -0.13275 | 122.0901 | -0.0025182 | -0.061008 | 0.038157 | 0.015195 | -0.014856 | -0.012987 | -0.021518 | 0.0082016 | 0.0039057 | 0.06296 | 0.059918 | 0.057088 | -0.049315 | 0.010564 | -0.031301 | 0.070441 | 0.11941 | 0.22438 | -0.12258 | 12.9451 | 35.5449 | 9.3895 | 121.8587 | 122.1433 | 121.9955 | -0.1962 | 0.010168 | -122.0197 | 0.083436 | 0.10145 | 0.091282 | -121.9707 | -121.8658 | -0.063449 | -0.2314 | 13.0778 | 9.5223 | 9.5857 | 0.053201 | -0.094691 | 0.20319 | 0.25216 | 0.35713 | 0.14331 | -122.2127 | 121.9915 | 122.2761 | 122.1282 | 35.6776 | -122.2863
4932.375 | 122.2275 | -0.082397 | 122.0398 | -0.010149 | -0.061649 | 0.03837 | 0.015195 | -0.014856 | -0.012773 | -0.021518 | 0.0088424 | 0.0043331 | 0.06296 | 0.060132 | 0.057302 | -0.040158 | 0.010564 | -0.031301 | 0.070441 | 0.11941 | 0.22896 | -0.12258 | 13.1465 | 35.6639 | 9.5544 | 121.8542 | 122.1479 | 122 | -0.20078 | -0.040186 | -121.9694 | 0.042239 | 0.051096 | 0.091282 | -121.9204 | -121.8108 | -0.11838 | -0.18563 | 13.2289 | 9.6368 | 9.7551 | 0.10813 | -0.039759 | 0.15284 | 0.20181 | 0.31136 | 0.092961 | -122.1624 | 121.9366 | 122.2303 | 122.0824 | 35.7463 | -122.2406
4934.0781 | 122.2412 | -0.07782 | 122.0581 | -0.01778 | -0.061222 | 0.038157 | 0.014768 | -0.014642 | -0.012987 | -0.029148 | 0.0094834 | 0.0043331 | 0.062746 | 0.060345 | 0.057302 | -0.049315 | 0.010564 | -0.040457 | 0.070441 | 0.11483 | 0.24269 | -0.12716 | 13.348 | 35.7189 | 9.7238 | 121.8633 | 122.1388 | 121.9955 | -0.20536 | -0.049342 | -121.9877 | 0.028505 | 0.037363 | 0.086705 | -121.9433 | -121.8154 | -0.12754 | -0.19478 | 13.4258 | 9.8016 | 9.9291 | 0.080666 | -0.062647 | 0.14826 | 0.19265 | 0.32051 | 0.088384 | -122.1853 | 121.9411 | 122.2166 | 122.0733 | 35.7967 | -122.2635
4935.8438 | 122.2549 | -0.086975 | 122.0535 | -0.01778 | -0.061435 | 0.038157 | 0.014981 | -0.014856 | -0.012773 | -0.021518 | 0.0090562 | 0.0041193 | 0.06296 | 0.060559 | 0.057515 | -0.044736 | 0.005985 | -0.045036 | 0.070441 | 0.11025 | 0.23812 | -0.12716 | 13.5632 | 35.8242 | 9.884 | 121.8725 | 122.1433 | 121.9955 | -0.1962 | -0.040187 | -121.9831 | 0.042239 | 0.041939 | 0.082126 | -121.9433 | -121.8154 | -0.10923 | -0.18105 | 13.6502 | 9.971 | 10.0802 | 0.089822 | -0.05807 | 0.15742 | 0.19723 | 0.32509 | 0.09296 | -122.1807 | 121.9595 | 122.2303 | 122.0824 | 35.9112 | -122.2497
4937.5469 | 122.2137 | -0.10071 | 122.0764 | -0.010149 | -0.061435 | 0.03837 | 0.014554 | -0.014642 | -0.012773 | -0.013887 | 0.0099106 | 0.0043331 | 0.06296 | 0.060559 | 0.057729 | -0.040158 | 0.005985 | -0.040457 | 0.056706 | 0.11025 | 0.23812 | -0.12716 | 13.783 | 35.9295 | 10.0718 | 121.8496 | 122.1433 | 121.9909 | -0.20536 | -0.026454 | -122.0197 | 0.06055 | 0.060251 | 0.086705 | -121.9662 | -121.8383 | -0.10465 | -0.22683 | 13.8837 | 10.1725 | 10.2771 | 0.066934 | -0.085537 | 0.15741 | 0.21096 | 0.33882 | 0.10669 | -122.2036 | 121.9503 | 122.2441 | 122.0916 | 36.0302 | -122.2818
4939.3281 | 122.2687 | -0.091553 | 122.0398 | -0.01778 | -0.061008 | 0.03837 | 0.014768 | -0.014856 | -0.012346 | -0.029148 | 0.009697 | 0.0045467 | 0.063601 | 0.060987 | 0.05837 | -0.049315 | 0.005985 | -0.035879 | 0.070441 | 0.11483 | 0.23812 | -0.12258 | 14.0256 | 36.0623 | 10.2824 | 121.8542 | 122.1388 | 121.9909 | -0.20994 | -0.03103 | -121.9694 | 0.042238 | 0.055674 | 0.086704 | -121.925 | -121.8017 | -0.11838 | -0.18563 | 14.1172 | 10.3739 | 10.4923 | 0.098976 | -0.048916 | 0.16199 | 0.20638 | 0.32967 | 0.097538 | -122.1624 | 121.9457 | 122.2303 | 122.0824 | 36.1538 | -122.2497
4941.0312 | 122.2824 | -0.082397 | 122.0352 | -0.010149 | -0.061222 | 0.037943 | 0.014768 | -0.014856 | -0.012559 | -0.013887 | 0.010338 | 0.0045467 | 0.063815 | 0.060987 | 0.058584 | -0.040158 | 0.010564 | -0.031301 | 0.070441 | 0.11941 | 0.23354 | -0.12258 | 14.25 | 36.1813 | 10.4838 | 121.8587 | 122.1388 | 121.9909 | -0.20536 | -0.040186 | -121.9648 | 0.042239 | 0.051096 | 0.091282 | -121.9158 | -121.8017 | -0.12296 | -0.17647 | 14.3324 | 10.5662 | 10.6892 | 0.10355 | -0.044338 | 0.15284 | 0.20181 | 0.31593 | 0.092961 | -122.1578 | 121.9411 | 122.2212 | 122.0733 | 36.2637 | -122.2406
4942.7344 | 122.2504 | -0.068665 | 122.0123 | -0.010149 | -0.061649 | 0.038157 | 0.014981 | -0.014856 | -0.012559 | -0.021518 | 0.010979 | 0.0049739 | 0.063601 | 0.060987 | 0.058797 | -0.040158 | 0.001407 | -0.031301 | 0.070441 | 0.11941 | 0.23354 | -0.11342 | 14.4881 | 36.2912 | 10.6761 | 121.8587 | 122.1433 | 121.9909 | -0.20536 | -0.04476 | -121.9419 | 0.028507 | 0.037364 | 0.082124 | -121.8929 | -121.7788 | -0.13669 | -0.15358 | 14.5568 | 10.7448 | 10.8815 | 0.13102 | -0.02145 | 0.13911 | 0.18808 | 0.3022 | 0.070072 | -122.1258 | 121.9274 | 122.212 | 122.0595 | 36.3599 | -122.2177
4944.5 | 122.1954 | -0.10986 | 122.0673 | -0.0025182 | -0.061649 | 0.038157 | 0.014981 | -0.014642 | -0.012559 | -0.013887 | 0.010552 | 0.0049739 | 0.063601 | 0.061414 | 0.059011 | -0.049315 | 0.005985 | -0.031301 | 0.065863 | 0.11025 | 0.23812 | -0.13632 | 14.7582 | 36.511 | 10.8868 | 121.8587 | 122.1388 | 122 | -0.20536 | -0.026457 | -122.0014 | 0.060548 | 0.078562 | 0.10502 | -121.957 | -121.8291 | -0.095495 | -0.20852 | 14.8681 | 10.9966 | 11.0921 | 0.07151 | -0.067225 | 0.17573 | 0.22012 | 0.34798 | 0.11585 | -122.2036 | 121.9686 | 122.2486 | 122.1099 | 36.6209 | -122.2726
4946.2188 | 122.2046 | -0.10986 | 122.049 | -0.0025182 | -0.061435 | 0.037943 | 0.014981 | -0.014856 | -0.012346 | -0.021518 | 0.011193 | 0.0047603 | 0.063815 | 0.061841 | 0.059438 | -0.044736 | 0.010564 | -0.031301 | 0.070441 | 0.11483 | 0.23354 | -0.12258 | 15.0009 | 36.6621 | 11.0928 | 121.8587 | 122.1388 | 121.9955 | -0.20536 | -0.01272 | -121.9785 | 0.065127 | 0.078562 | 0.091282 | -121.9341 | -121.8154 | -0.095495 | -0.19021 | 15.1108 | 11.2027 | 11.2982 | 0.089821 | -0.053492 | 0.1803 | 0.2247 | 0.3434 | 0.12043 | -122.1715 | 121.9686 | 122.2486 | 122.1053 | 36.772 | -122.2543
4947.9844 | 122.2687 | -0.091553 | 122.0169 | -0.01778 | -0.061222 | 0.03837 | 0.015195 | -0.01507 | -0.011918 | -0.021518 | 0.011193 | 0.0049739 | 0.063815 | 0.061628 | 0.059438 | -0.044736 | 0.005985 | -0.040457 | 0.065863 | 0.11941 | 0.23812 | -0.13174 | 15.2756 | 36.891 | 11.3172 | 121.8587 | 122.1388 | 121.9955 | -0.20078 | -0.040188 | -121.951 | 0.046817 | 0.051096 | 0.091284 | -121.8975 | -121.7788 | -0.10923 | -0.15816 | 15.3672 | 11.4087 | 11.5179 | 0.12186 | -0.021449 | 0.15742 | 0.21096 | 0.32967 | 0.097538 | -122.1486 | 121.9503 | 122.2303 | 122.087 | 36.9826 | -122.2177
4949.75 | 122.1725 | -0.11444 | 122.081 | -0.010149 | -0.061222 | 0.037943 | 0.014981 | -0.014856 | -0.012346 | -0.013887 | 0.011833 | 0.0047603 | 0.064242 | 0.061841 | 0.060079 | -0.044736 | 0.005985 | -0.031301 | 0.065863 | 0.11941 | 0.23812 | -0.118 | 15.5687 | 37.1612 | 11.5644 | 121.8587 | 122.1388 | 121.9909 | -0.20536 | -0.003563 | -122.0151 | 0.069705 | 0.08314 | 0.086703 | -121.9616 | -121.8429 | -0.090917 | -0.22225 | 15.6831 | 11.6789 | 11.7698 | 0.057777 | -0.090115 | 0.1803 | 0.23385 | 0.35256 | 0.12043 | -122.199 | 121.9732 | 122.2532 | 122.1053 | 37.2756 | -122.2864
4951.4531 | 122.1588 | -0.1236 | 122.0718 | -0.010149 | -0.061435 | 0.037943 | 0.014981 | -0.014856 | -0.011918 | -0.013887 | 0.012474 | 0.0051877 | 0.064456 | 0.062055 | 0.059866 | -0.040158 | 0.005985 | -0.031301 | 0.07502 | 0.12399 | 0.23812 | -0.12716 | 15.8159 | 37.4954 | 11.7888 | 121.8679 | 122.1479 | 121.9955 | -0.20536 | -0.003566 | -121.9968 | 0.083438 | 0.092295 | 0.095861 | -121.9478 | -121.8337 | -0.081762 | -0.20394 | 15.9395 | 11.9124 | 11.9941 | 0.076091 | -0.07638 | 0.19862 | 0.24759 | 0.36171 | 0.12958 | -122.199 | 121.9915 | 122.2715 | 122.1191 | 37.619 | -122.2772
4953.2031 | 122.2046 | -0.10071 | 122.0581 | -0.010149 | -0.061008 | 0.038157 | 0.015195 | -0.01507 | -0.012346 | -0.021518 | 0.012474 | 0.0051877 | 0.064242 | 0.062269 | 0.060293 | -0.03558 | 0.005985 | -0.026723 | 0.065863 | 0.11483 | 0.23812 | -0.12258 | 16.0494 | 37.6053 | 11.9994 | 121.8587 | 122.1433 | 121.9955 | -0.20994 | -0.021875 | -121.9922 | 0.065128 | 0.073985 | 0.09586 | -121.9433 | -121.82 | -0.10923 | -0.19936 | 16.1501 | 12.1001 | 12.2093 | 0.085245 | -0.062647 | 0.16657 | 0.21554 | 0.33882 | 0.10669 | -122.1807 | 121.9595 | 122.2441 | 122.0962 | 37.706 | -122.268
4954.9062 | 122.1588 | -0.1236 | 122.0856 | -0.01778 | -0.061435 | 0.038157 | 0.014981 | -0.015283 | -0.012132 | -0.029148 | 0.012902 | 0.0049739 | 0.064456 | 0.062696 | 0.060507 | -0.044736 | 0.010564 | -0.031301 | 0.070441 | 0.11025 | 0.24269 | -0.12716 | 16.2829 | 37.7335 | 12.2146 | 121.8542 | 122.1479 | 122 | -0.20536 | -0.003566 | -122.0151 | 0.07886 | 0.092295 | 0.095861 | -121.9753 | -121.8429 | -0.081762 | -0.2314 | 16.4065 | 12.3382 | 12.4199 | 0.062358 | -0.085535 | 0.19404 | 0.23385 | 0.36629 | 0.13416 | -122.2127 | 121.9778 | 122.2715 | 122.1236 | 37.8571 | -122.2909
4956.6719 | 122.1588 | -0.10986 | 122.0718 | -0.01778 | -0.061435 | 0.037943 | 0.014981 | -0.014856 | -0.011705 | -0.013887 | 0.013115 | 0.0056149 | 0.064883 | 0.062482 | 0.060934 | -0.03558 | 0.005985 | -0.031301 | 0.070441 | 0.11941 | 0.23812 | -0.118 | 16.5531 | 37.935 | 12.4573 | 121.8633 | 122.1479 | 121.9863 | -0.20078 | -0.008141 | -122.0014 | 0.074283 | 0.078562 | 0.086703 | -121.9524 | -121.8337 | -0.090916 | -0.20852 | 16.6629 | 12.5671 | 12.658 | 0.076091 | -0.085538 | 0.1803 | 0.22927 | 0.34798 | 0.11585 | -122.1898 | 121.9732 | 122.2578 | 122.0962 | 38.0448 | -122.2726
4958.4375 | 122.1954 | -0.1236 | 122.0581 | -0.010149 | -0.061222 | 0.03837 | 0.014768 | -0.014429 | -0.011918 | -0.021518 | 0.013329 | 0.0056149 | 0.064456 | 0.06291 | 0.061575 | -0.040158 | 0.010564 | -0.026723 | 0.084176 | 0.11483 | 0.23354 | -0.118 | 16.8278 | 38.1547 | 12.7366 | 121.8633 | 122.1433 | 121.9909 | -0.1962 | 0.005592 | -121.9739 | 0.083438 | 0.096873 | 0.091281 | -121.9433 | -121.8246 | -0.072604 | -0.19478 | 16.9514 | 12.8602 | 12.9328 | 0.085245 | -0.067226 | 0.20777 | 0.23843 | 0.35713 | 0.13416 | -122.1761 | 121.9869 | 122.2669 | 122.1145 | 38.2783 | -122.2543
4960.2031 | 122.2321 | -0.086975 | 122.0352 | -0.010149 | -0.061222 | 0.038157 | 0.014981 | -0.014642 | -0.011918 | -0.029148 | 0.01397 | 0.0054013 | 0.065096 | 0.06291 | 0.061361 | -0.044736 | 0.010564 | -0.031301 | 0.065863 | 0.11941 | 0.23354 | -0.12716 | 17.1071 | 38.3654 | 12.9884 | 121.8679 | 122.1525 | 121.9909 | -0.20536 | -0.040187 | -121.9694 | 0.042239 | 0.055674 | 0.095861 | -121.9158 | -121.8017 | -0.11838 | -0.16732 | 17.1941 | 13.0754 | 13.1938 | 0.11729 | -0.044338 | 0.15284 | 0.20639 | 0.32051 | 0.097539 | -122.1624 | 121.9549 | 122.2395 | 122.0779 | 38.4523 | -122.2406
4961.9062 | 122.2046 | -0.10986 | 122.049 | -0.010149 | -0.061222 | 0.037943 | 0.014768 | -0.014856 | -0.011918 | -0.021518 | 0.014397 | 0.0056149 | 0.064883 | 0.063123 | 0.062002 | -0.03558 | 0.005985 | -0.026723 | 0.07502 | 0.12399 | 0.23354 | -0.118 | 17.3956 | 38.5897 | 13.2311 | 121.8496 | 122.1342 | 122 | -0.20994 | -0.008141 | -121.9739 | 0.074283 | 0.08314 | 0.091281 | -121.925 | -121.8154 | -0.10007 | -0.19936 | 17.5054 | 13.3409 | 13.441 | 0.085243 | -0.048914 | 0.18488 | 0.23385 | 0.3434 | 0.11585 | -122.167 | 121.9595 | 122.2441 | 122.1099 | 38.6996 | -122.2589
4963.6719 | 122.2046 | -0.10529 | 122.0673 | -0.010149 | -0.061435 | 0.03837 | 0.014981 | -0.01507 | -0.011491 | -0.029148 | 0.015038 | 0.0058287 | 0.065096 | 0.063551 | 0.062216 | -0.044736 | 0.010564 | -0.026723 | 0.079598 | 0.11025 | 0.23354 | -0.12258 | 17.6749 | 38.8232 | 13.4966 | 121.8542 | 122.1433 | 121.9955 | -0.20536 | -0.017297 | -121.9877 | 0.06055 | 0.078563 | 0.09586 | -121.957 | -121.8337 | -0.10007 | -0.21309 | 17.7802 | 13.6019 | 13.702 | 0.076089 | -0.071803 | 0.18488 | 0.21554 | 0.33882 | 0.11585 | -122.1898 | 121.9595 | 122.2486 | 122.1007 | 38.9285 | -122.2726
4965.3594 | 122.2504 | -0.091553 | 122.0261 | -0.010149 | -0.061435 | 0.03837 | 0.014981 | -0.014856 | -0.011277 | -0.013887 | 0.015465 | 0.0058287 | 0.065096 | 0.063551 | 0.062857 | -0.049315 | 0.010564 | -0.035879 | 0.070441 | 0.11483 | 0.23812 | -0.12716 | 17.9816 | 39.0613 | 13.7576 | 121.8587 | 122.1433 | 121.9955 | -0.20536 | -0.035609 | -121.9556 | 0.042238 | 0.055674 | 0.091283 | -121.9112 | -121.7879 | -0.11381 | -0.16732 | 18.0732 | 13.8492 | 13.963 | 0.11729 | -0.030604 | 0.16199 | 0.20638 | 0.32967 | 0.10212 | -122.1532 | 121.9503 | 122.2349 | 122.087 | 39.1529 | -122.2314
4967.1406 | 122.2 | -0.11444 | 122.0352 | -0.01778 | -0.061649 | 0.03837 | 0.014981 | -0.01507 | -0.010209 | -0.013887 | 0.015465 | 0.0060423 | 0.065096 | 0.063764 | 0.063498 | -0.040158 | 0.010564 | -0.031301 | 0.070441 | 0.11483 | 0.23354 | -0.12258 | 18.3525 | 39.4688 | 14.0598 | 121.845 | 122.1342 | 121.9771 | -0.20536 | -0.008142 | -121.9648 | 0.074283 | 0.08314 | 0.091282 | -121.9204 | -121.8017 | -0.090917 | -0.19021 | 18.467 | 14.1743 | 14.2652 | 0.098976 | -0.058074 | 0.18488 | 0.22927 | 0.34798 | 0.12501 | -122.1578 | 121.9595 | 122.2486 | 122.0916 | 39.5833 | -122.2406
4968.9062 | 122.2687 | -0.068665 | 122.0123 | -0.0025182 | -0.061435 | 0.03837 | 0.014768 | -0.01507 | -0.0097815 | -0.021518 | 0.015893 | 0.0060423 | 0.06531 | 0.063978 | 0.064139 | -0.040158 | 0.015142 | -0.031301 | 0.07502 | 0.11483 | 0.23354 | -0.118 | 18.6639 | 39.6749 | 14.3254 | 121.845 | 122.125 | 121.9817 | -0.20078 | -0.049339 | -121.9373 | 0.028507 | 0.037364 | 0.086703 | -121.8975 | -121.7788 | -0.13211 | -0.16732 | 18.7325 | 14.394 | 14.5262 | 0.11271 | -0.030607 | 0.14369 | 0.1835 | 0.3022 | 0.083807 | -122.1303 | 121.9137 | 122.1937 | 122.0504 | 39.7435 | -122.2131
4970.6094 | 122.2778 | -0.068665 | 122.0215 | -0.010149 | -0.061435 | 0.038157 | 0.015195 | -0.014856 | -0.0099951 | -0.021518 | 0.01632 | 0.0062559 | 0.06531 | 0.064192 | 0.064139 | -0.040158 | 0.005985 | -0.031301 | 0.079598 | 0.11941 | 0.23812 | -0.12716 | 18.9477 | 39.8122 | 14.5726 | 121.845 | 122.1296 | 121.9817 | -0.20994 | -0.058497 | -121.9419 | 0.028507 | 0.037364 | 0.095861 | -121.9021 | -121.7834 | -0.14127 | -0.17647 | 19.0164 | 14.6413 | 14.7826 | 0.10813 | -0.039762 | 0.14826 | 0.18808 | 0.30678 | 0.07465 | -122.1486 | 121.9137 | 122.1983 | 122.0504 | 39.8809 | -122.2314
4972.375 | 122.2961 | -0.073242 | 122.0032 | -0.010149 | -0.061435 | 0.038157 | 0.014554 | -0.014856 | -0.0097815 | -0.013887 | 0.017174 | 0.0062559 | 0.065524 | 0.064405 | 0.06478 | -0.044736 | 0.005985 | -0.035879 | 0.065863 | 0.11025 | 0.23812 | -0.118 | 19.2499 | 40.0183 | 14.8519 | 121.8267 | 122.1205 | 121.9588 | -0.10462 | -0.044762 | -121.9373 | 0.028506 | 0.037363 | 0.082125 | -121.8929 | -121.7651 | -0.031382 | -0.17648 | 19.3232 | 14.9252 | 14.9566 | 0.11728 | -0.044345 | 0.13911 | 0.1835 | 0.31136 | 0.079227 | -122.1212 | 121.8999 | 122.1937 | 122.0321 | 40.0915 | -122.1078
4974.1406 | 122.1313 | -0.11444 | 122.0215 | -0.010149 | -0.061435 | 0.03837 | 0.014768 | -0.01507 | -0.013414 | -0.029148 | 0.017174 | 0.0066833 | 0.066165 | 0.064405 | 0.064993 | -0.040158 | 0.005985 | -0.031301 | 0.070441 | 0.11941 | 0.23812 | -0.118 | 19.4102 | 39.7436 | 15.0259 | 121.7992 | 122.0793 | 121.9268 | -0.20078 | -0.003563 | -121.951 | 0.074283 | 0.08314 | 0.086703 | -121.9021 | -121.7834 | -0.086338 | -0.22226 | 19.5246 | 15.1404 | 15.2267 | 0.057766 | -0.094705 | 0.18488 | 0.23385 | 0.35256 | 0.12043 | -122.1395 | 121.9137 | 122.1937 | 122.0412 | 39.858 | -122.2223
4975.9062 | 122.2549 | -0.064087 | 122.0032 | -0.01778 | -0.061649 | 0.038157 | 0.014981 | -0.015283 | -0.013414 | -0.021518 | 0.017815 | 0.0066833 | 0.066378 | 0.064619 | 0.065207 | -0.040158 | 0.015142 | -0.031301 | 0.070441 | 0.12399 | 0.23812 | -0.12258 | 19.7307 | 39.9679 | 15.3144 | 121.8267 | 122.1113 | 121.9543 | -0.20078 | -0.058496 | -121.9327 | 0.023929 | 0.032786 | 0.091282 | -121.8792 | -121.7651 | -0.13669 | -0.17648 | 19.7948 | 15.3785 | 15.5152 | 0.10813 | -0.048924 | 0.13453 | 0.18808 | 0.3022 | 0.079229 | -122.1258 | 121.8908 | 122.1754 | 122.0183 | 40.032 | -122.204
4977.6875 | 122.1771 | -0.091553 | 122.0444 | -0.0025182 | -0.061008 | 0.03837 | 0.014554 | -0.01507 | -0.013628 | -0.029148 | 0.017815 | 0.0068969 | 0.066378 | 0.065046 | 0.065848 | -0.040158 | 0.015142 | -0.031301 | 0.065863 | 0.11483 | 0.23812 | -0.12258 | 20.0604 | 40.1831 | 15.6074 | 121.8359 | 122.1205 | 121.9726 | -0.19162 | -0.03103 | -121.9785 | 0.051395 | 0.060252 | 0.091282 | -121.9295 | -121.8063 | -0.10007 | -0.20852 | 20.1519 | 15.699 | 15.799 | 0.076084 | -0.071808 | 0.15742 | 0.20638 | 0.32967 | 0.10669 | -122.167 | 121.9274 | 122.212 | 122.0641 | 40.2747 | -122.236
4979.4531 | 122.2504 | -0.068665 | 122.0078 | -0.025411 | -0.061435 | 0.038157 | 0.014768 | -0.01507 | -0.013414 | -0.021518 | 0.01867 | 0.0071105 | 0.066592 | 0.06526 | 0.066062 | -0.03558 | 0.001407 | -0.031301 | 0.070441 | 0.11483 | 0.24269 | -0.11342 | 20.3626 | 40.3571 | 15.9005 | 121.8496 | 122.1388 | 121.9771 | -0.20078 | -0.04476 | -121.9373 | 0.033085 | 0.037364 | 0.082124 | -121.8929 | -121.7651 | -0.13211 | -0.15816 | 20.4312 | 15.9691 | 16.1012 | 0.13102 | -0.030608 | 0.13911 | 0.1835 | 0.31136 | 0.070072 | -122.1212 | 121.9183 | 122.2074 | 122.0458 | 40.4258 | -122.2085
4981.1562 | 122.1451 | -0.11444 | 122.0856 | -0.010149 | -0.061435 | 0.038157 | 0.014981 | -0.014642 | -0.013414 | -0.036779 | 0.019097 | 0.0068969 | 0.066806 | 0.065687 | 0.066489 | -0.03558 | 0.010564 | -0.026723 | 0.07502 | 0.11941 | 0.24269 | -0.12716 | 20.6739 | 40.5494 | 16.1706 | 121.8496 | 122.1342 | 121.9863 | -0.20078 | -0.012721 | -122.0106 | 0.078861 | 0.087718 | 0.10044 | -121.9662 | -121.8429 | -0.086338 | -0.23598 | 20.7884 | 16.285 | 16.3714 | 0.048622 | -0.099271 | 0.18946 | 0.23385 | 0.35714 | 0.12501 | -122.2127 | 121.964 | 122.2486 | 122.1007 | 40.6639 | -122.2863
4982.8594 | 122.2229 | -0.086975 | 122.0581 | -0.01778 | -0.061649 | 0.038157 | 0.014768 | -0.014429 | -0.012987 | -0.021518 | 0.019311 | 0.0071105 | 0.066806 | 0.065474 | 0.066703 | -0.03558 | 0.015142 | -0.026723 | 0.079598 | 0.11941 | 0.23812 | -0.11342 | 20.9624 | 40.7417 | 16.4545 | 121.8587 | 122.1342 | 121.9955 | -0.1962 | -0.02645 | -121.9785 | 0.051395 | 0.060252 | 0.086702 | -121.9387 | -121.82 | -0.10923 | -0.19936 | 21.0494 | 16.5415 | 16.6507 | 0.076088 | -0.062647 | 0.16657 | 0.20639 | 0.32509 | 0.10212 | -122.1715 | 121.9457 | 122.2212 | 122.0824 | 40.8287 | -122.2543
4984.625 | 122.1771 | -0.1236 | 122.0535 | -0.01778 | -0.061435 | 0.037943 | 0.014554 | -0.01507 | -0.012773 | -0.021518 | 0.019952 | 0.0071105 | 0.066165 | 0.065687 | 0.067344 | -0.040158 | 0.019721 | -0.031301 | 0.07502 | 0.12399 | 0.23354 | -0.118 | 21.26 | 40.9661 | 16.7429 | 121.8542 | 122.1479 | 121.9955 | -0.20078 | 0.005592 | -121.9785 | 0.083438 | 0.092295 | 0.086703 | -121.9295 | -121.82 | -0.077183 | -0.19936 | 21.3836 | 16.8665 | 16.9437 | 0.094401 | -0.05807 | 0.19862 | 0.24759 | 0.35713 | 0.14332 | -122.1715 | 121.9778 | 122.2715 | 122.1191 | 41.0897 | -122.2543
4986.3125 | 122.287 | -0.068665 | 122.0444 | -0.010149 | -0.061649 | 0.038584 | 0.014554 | -0.01507 | -0.012773 | -0.021518 | 0.020165 | 0.0073243 | 0.067019 | 0.066115 | 0.067771 | -0.040158 | 0.015142 | -0.026723 | 0.07502 | 0.11941 | 0.23812 | -0.118 | 21.5713 | 41.1309 | 16.9902 | 121.8679 | 122.1525 | 122.0046 | -0.1962 | -0.049339 | -121.9694 | 0.028507 | 0.041942 | 0.091281 | -121.925 | -121.8063 | -0.12754 | -0.17647 | 21.64 | 17.0589 | 17.1864 | 0.10813 | -0.039758 | 0.14369 | 0.18808 | 0.30678 | 0.083807 | -122.1624 | 121.9366 | 122.2212 | 122.0733 | 41.1996 | -122.2406
4988.0938 | 122.1634 | -0.11444 | 122.1313 | -0.0025182 | -0.061435 | 0.037943 | 0.014981 | -0.015497 | -0.012987 | -0.021518 | 0.020806 | 0.0073243 | 0.067019 | 0.066115 | 0.067771 | -0.040158 | 0.015142 | -0.031301 | 0.070441 | 0.11941 | 0.24727 | -0.10885 | 21.8964 | 41.4102 | 17.3061 | 121.8679 | 122.1525 | 122.0092 | -0.19162 | 0.005594 | -122.0609 | 0.074283 | 0.08314 | 0.077546 | -122.0119 | -121.8841 | -0.077181 | -0.26345 | 22.0109 | 17.4206 | 17.4977 | 0.021159 | -0.12216 | 0.18488 | 0.23385 | 0.36172 | 0.12958 | -122.2402 | 121.9823 | 122.2669 | 122.1236 | 41.5247 | -122.323
4989.8594 | 122.1725 | -0.10986 | 122.0856 | -0.025411 | -0.061649 | 0.03837 | 0.014768 | -0.014429 | -0.012987 | -0.029148 | 0.02102 | 0.0077515 | 0.067019 | 0.066756 | 0.068839 | -0.03558 | 0.010564 | -0.031301 | 0.070441 | 0.12857 | 0.23812 | -0.12258 | 22.2078 | 41.6666 | 17.6083 | 121.8725 | 122.1525 | 122.0092 | -0.1962 | -0.01272 | -122.0151 | 0.074283 | 0.078562 | 0.091282 | -121.957 | -121.8475 | -0.086337 | -0.21309 | 22.3177 | 17.7182 | 17.8045 | 0.066936 | -0.076378 | 0.1803 | 0.23843 | 0.34798 | 0.12043 | -122.2082 | 121.9823 | 122.2624 | 122.1191 | 41.7765 | -122.2818
4991.5469 | 122.1954 | -0.10986 | 122.0901 | -0.010149 | -0.061649 | 0.037943 | 0.014768 | -0.014856 | -0.012773 | -0.029148 | 0.021447 | 0.0077515 | 0.067447 | 0.066756 | 0.069053 | -0.026423 | 0.015142 | -0.031301 | 0.070441 | 0.11941 | 0.23812 | -0.118 | 22.5283 | 41.8223 | 17.8876 | 121.8771 | 122.1617 | 122.0184 | -0.1962 | -0.008141 | -122.0197 | 0.08344 | 0.078562 | 0.086703 | -121.9707 | -121.852 | -0.086337 | -0.21309 | 22.6382 | 17.9975 | 18.0838 | 0.071515 | -0.071798 | 0.1803 | 0.22927 | 0.34798 | 0.12501 | -122.2082 | 121.9869 | 122.2715 | 122.1282 | 41.9322 | -122.2863
4993.3125 | 122.3236 | -0.086975 | 122.0535 | -0.0025182 | -0.061435 | 0.03837 | 0.01434 | -0.014642 | -0.012987 | -0.021518 | 0.021874 | 0.0079651 | 0.067447 | 0.066756 | 0.069266 | -0.031001 | 0.015142 | -0.031301 | 0.07502 | 0.11941 | 0.23354 | -0.118 | 22.8488 | 42.0512 | 18.2035 | 121.8771 | 122.1662 | 122.0138 | -0.1962 | -0.031029 | -121.9785 | 0.055974 | 0.055674 | 0.086703 | -121.9341 | -121.82 | -0.10923 | -0.17647 | 22.9358 | 18.2905 | 18.3997 | 0.11271 | -0.039756 | 0.162 | 0.20639 | 0.32051 | 0.10212 | -122.1715 | 121.964 | 122.2532 | 122.1007 | 42.1382 | -122.2497
4995.0781 | 122.2687 | -0.073242 | 122.0398 | -0.01778 | -0.061435 | 0.03837 | 0.014768 | -0.014856 | -0.012773 | -0.021518 | 0.022302 | 0.0079651 | 0.067874 | 0.067183 | 0.069907 | -0.03558 | 0.015142 | -0.031301 | 0.07502 | 0.12399 | 0.24269 | -0.12258 | 23.3113 | 42.2206 | 18.4737 | 121.8816 | 122.1617 | 122.0184 | -0.19162 | -0.049341 | -121.9648 | 0.037662 | 0.041941 | 0.091282 | -121.9158 | -121.7971 | -0.11838 | -0.15816 | 23.3845 | 18.5469 | 18.6653 | 0.12187 | -0.021444 | 0.14826 | 0.19723 | 0.31594 | 0.088384 | -122.1624 | 121.9549 | 122.2349 | 122.0916 | 42.2939 | -122.2314
4996.8438 | 122.319 | -0.059509 | 122.049 | -0.01778 | -0.062076 | 0.03837 | 0.014768 | -0.01507 | -0.012773 | -0.013887 | 0.022943 | 0.0083925 | 0.067447 | 0.06761 | 0.070548 | -0.040158 | 0.015142 | -0.031301 | 0.070441 | 0.12399 | 0.23812 | -0.12258 | 23.6684 | 42.4084 | 18.7484 | 121.8771 | 122.1662 | 122.0138 | -0.20536 | -0.063074 | -121.9785 | 0.019351 | 0.028208 | 0.091282 | -121.925 | -121.8108 | -0.14585 | -0.17189 | 23.7279 | 18.8079 | 18.9538 | 0.11729 | -0.035178 | 0.12995 | 0.1835 | 0.29763 | 0.074651 | -122.1715 | 121.9366 | 122.2258 | 122.0733 | 42.4679 | -122.2543
4998.6094 | 122.168 | -0.12817 | 122.1039 | -0.01778 | -0.061435 | 0.038157 | 0.014554 | -0.014856 | -0.012559 | -0.029148 | 0.024011 | 0.0086061 | 0.068088 | 0.06761 | 0.070762 | -0.040158 | 0.010564 | -0.026723 | 0.065863 | 0.12399 | 0.23812 | -0.13174 | 24.0301 | 42.6602 | 19.0735 | 121.8771 | 122.1617 | 122.0229 | -0.1962 | -0.003567 | -122.038 | 0.088016 | 0.10145 | 0.10502 | -121.9799 | -121.8658 | -0.068026 | -0.22682 | 24.1583 | 19.2017 | 19.2697 | 0.057782 | -0.080953 | 0.19404 | 0.25216 | 0.36629 | 0.13874 | -122.2356 | 122.0052 | 122.2898 | 122.1511 | 42.7884 | -122.3001
5000.3125 | 122.2916 | -0.086975 | 122.0856 | -0.010149 | -0.061435 | 0.038157 | 0.014554 | -0.01507 | -0.012559 | -0.029148 | 0.024438 | 0.0088199 | 0.068088 | 0.067824 | 0.071189 | -0.044736 | 0.010564 | -0.026723 | 0.07502 | 0.12399 | 0.24269 | -0.11342 | 24.3735 | 42.9029 | 19.3849 | 121.8816 | 122.1708 | 122.0275 | -0.1962 | -0.02645 | -122.0106 | 0.042239 | 0.060252 | 0.086702 | -121.9616 | -121.8429 | -0.10923 | -0.20393 | 24.4605 | 19.4718 | 19.5811 | 0.085251 | -0.058063 | 0.162 | 0.21097 | 0.32967 | 0.097539 | -122.199 | 121.9686 | 122.2578 | 122.1145 | 42.9898 | -122.2818
5002.0938 | 122.2549 | -0.091553 | 122.0764 | -0.0025182 | -0.061222 | 0.037943 | 0.014554 | -0.014856 | -0.012559 | -0.029148 | 0.024865 | 0.0088199 | 0.067874 | 0.068038 | 0.07183 | -0.044736 | 0.005985 | -0.026723 | 0.079598 | 0.11941 | 0.23354 | -0.118 | 24.7261 | 43.1593 | 19.6825 | 121.8862 | 122.1754 | 122.0229 | -0.20078 | -0.026451 | -121.9968 | 0.046817 | 0.06483 | 0.091281 | -121.957 | -121.8429 | -0.10923 | -0.1902 | 24.8176 | 19.774 | 19.8832 | 0.098984 | -0.053487 | 0.17115 | 0.21096 | 0.32509 | 0.097538 | -122.1944 | 121.9778 | 122.267 | 122.1145 | 43.2508 | -122.2772
5003.8594 | 122.2412 | -0.10986 | 122.1085 | -0.010149 | -0.061435 | 0.038157 | 0.014554 | -0.01507 | -0.012559 | -0.029148 | 0.025293 | 0.0092471 | 0.068515 | 0.068465 | 0.072471 | -0.031001 | 0.010564 | -0.022144 | 0.079598 | 0.12857 | 0.24269 | -0.12258 | 25.0832 | 43.347 | 19.9755 | 121.8908 | 122.18 | 122.0229 | -0.1962 | -0.01272 | -122.0289 | 0.078862 | 0.087719 | 0.10044 | -121.9799 | -121.8658 | -0.086337 | -0.21766 | 25.1931 | 20.0854 | 20.1717 | 0.07152 | -0.08553 | 0.18946 | 0.23843 | 0.35256 | 0.12043 | -122.231 | 122.0007 | 122.2898 | 122.1328 | 43.4569 | -122.3047
5005.5625 | 122.1771 | -0.1236 | 122.113 | -0.010149 | -0.061435 | 0.038157 | 0.014554 | -0.014642 | -0.012132 | -0.013887 | 0.025934 | 0.0088199 | 0.068728 | 0.068892 | 0.072899 | -0.03558 | 0.010564 | -0.031301 | 0.07502 | 0.12399 | 0.24269 | -0.118 | 25.3946 | 43.5302 | 20.2594 | 121.8908 | 122.1754 | 122.0184 | -0.1962 | 0.005592 | -122.038 | 0.088016 | 0.092295 | 0.086703 | -121.989 | -121.8703 | -0.072604 | -0.22224 | 25.5182 | 20.383 | 20.4556 | 0.062363 | -0.094686 | 0.19862 | 0.24759 | 0.36629 | 0.13416 | -122.231 | 122.0144 | 122.299 | 122.1419 | 43.6538 | -122.3092
5007.3438 | 122.3236 | -0.064087 | 122.0627 | -0.010149 | -0.061649 | 0.038157 | 0.014554 | -0.014429 | -0.012346 | -0.013887 | 0.026147 | 0.0090335 | 0.068515 | 0.068892 | 0.073112 | -0.044736 | 0.005985 | -0.031301 | 0.07502 | 0.12857 | 0.23812 | -0.12258 | 25.7929 | 43.6904 | 20.5707 | 121.8954 | 122.18 | 122.0275 | -0.1962 | -0.058496 | -121.9877 | 0.019351 | 0.032786 | 0.091282 | -121.9341 | -121.8246 | -0.13211 | -0.16731 | 25.857 | 20.6348 | 20.7669 | 0.1173 | -0.035175 | 0.13911 | 0.19266 | 0.3022 | 0.070072 | -122.1853 | 121.9595 | 122.2441 | 122.0916 | 43.7545 | -122.2589
5009.0469 | 122.3236 | -0.07782 | 122.0673 | -0.010149 | -0.061222 | 0.03837 | 0.014981 | -0.014856 | -0.012132 | -0.021518 | 0.026574 | 0.0092471 | 0.068728 | 0.069106 | 0.073753 | -0.03558 | 0.015142 | -0.040457 | 0.079598 | 0.11941 | 0.23354 | -0.12258 | 26.1134 | 43.8507 | 20.8043 | 121.8908 | 122.1754 | 122.0275 | -0.1962 | -0.044763 | -121.9877 | 0.04224 | 0.037363 | 0.082126 | -121.9479 | -121.8337 | -0.11838 | -0.17647 | 26.1913 | 20.8821 | 21.0005 | 0.10814 | -0.039753 | 0.15742 | 0.19723 | 0.31136 | 0.092962 | -122.1898 | 121.9686 | 122.2532 | 122.1053 | 43.9285 | -122.2635
5010.75 | 122.2137 | -0.10529 | 122.0718 | -0.0025182 | -0.062076 | 0.03837 | 0.014768 | -0.014856 | -0.012346 | -0.029148 | 0.027002 | 0.0094609 | 0.068942 | 0.06932 | 0.074608 | -0.031001 | 0.010564 | -0.026723 | 0.070441 | 0.12399 | 0.24269 | -0.118 | 26.4385 | 44.0521 | 21.1202 | 121.8862 | 122.1708 | 122.0275 | -0.20078 | -0.012718 | -122.0014 | 0.074285 | 0.078563 | 0.091281 | -121.9478 | -121.8291 | -0.095493 | -0.18562 | 26.5438 | 21.2255 | 21.321 | 0.098984 | -0.04433 | 0.17573 | 0.22928 | 0.34798 | 0.11585 | -122.1898 | 121.9915 | 122.2761 | 122.1328 | 44.1574 | -122.2726
5012.5312 | 122.1909 | -0.11444 | 122.0627 | -0.0025182 | -0.061435 | 0.038157 | 0.014768 | -0.014856 | -0.012132 | -0.029148 | 0.027643 | 0.0092471 | 0.068942 | 0.069533 | 0.074608 | -0.03558 | 0.015142 | -0.035879 | 0.065863 | 0.11483 | 0.23812 | -0.12258 | 26.8002 | 44.2307 | 21.4453 | 121.8862 | 122.1662 | 122.0275 | -0.20078 | -0.008142 | -121.9968 | 0.078861 | 0.078562 | 0.086704 | -121.9479 | -121.8246 | -0.086338 | -0.17647 | 26.9147 | 21.5597 | 21.646 | 0.10356 | -0.035175 | 0.1803 | 0.22927 | 0.35256 | 0.12958 | -122.1853 | 122.0007 | 122.2807 | 122.1419 | 44.3451 | -122.2635
5014.2969 | 122.2137 | -0.10071 | 122.0993 | -0.01778 | -0.061222 | 0.037943 | 0.014768 | -0.01507 | -0.012132 | -0.013887 | 0.028284 | 0.0098881 | 0.069156 | 0.069961 | 0.075462 | -0.040158 | 0.005985 | -0.035879 | 0.070441 | 0.12399 | 0.24269 | -0.12258 | 27.1711 | 44.4322 | 21.752 | 121.8908 | 122.1708 | 122.0229 | -0.19162 | -0.021875 | -122.0289 | 0.06055 | 0.064829 | 0.086704 | -121.9753 | -121.8566 | -0.090914 | -0.20851 | 27.2718 | 21.8528 | 21.9437 | 0.071518 | -0.076375 | 0.17115 | 0.2247 | 0.3434 | 0.10669 | -122.2219 | 121.9915 | 122.2715 | 122.1236 | 44.5329 | -122.2909
5016.0625 | 122.2687 | -0.073242 | 122.0581 | -0.01778 | -0.061222 | 0.038157 | 0.014554 | -0.014856 | -0.012132 | -0.013887 | 0.028924 | 0.010102 | 0.069156 | 0.069961 | 0.075676 | -0.03558 | 0.010564 | -0.035879 | 0.070441 | 0.12857 | 0.24269 | -0.12258 | 27.5054 | 44.6336 | 22.0268 | 121.8908 | 122.1754 | 122.0275 | -0.20078 | -0.049341 | -121.9877 | 0.037662 | 0.037363 | 0.086704 | -121.9295 | -121.8154 | -0.12754 | -0.16731 | 27.5786 | 22.1 | 22.2275 | 0.11729 | -0.030597 | 0.14368 | 0.20181 | 0.31594 | 0.083806 | -122.1807 | 121.964 | 122.2486 | 122.1007 | 44.7069 | -122.2589
5017.8281 | 122.3007 | -0.068665 | 122.0627 | -0.0025182 | -0.061435 | 0.037943 | 0.014554 | -0.015283 | -0.012132 | -0.029148 | 0.029565 | 0.010102 | 0.069583 | 0.070388 | 0.076317 | -0.044736 | 0.010564 | -0.040457 | 0.070441 | 0.12399 | 0.23812 | -0.118 | 27.9129 | 44.89 | 22.3564 | 121.8908 | 122.1754 | 122.0229 | -0.20078 | -0.049339 | -121.9922 | 0.023929 | 0.028208 | 0.077547 | -121.9387 | -121.8246 | -0.13211 | -0.17189 | 27.9815 | 22.4251 | 22.5572 | 0.11272 | -0.039754 | 0.13911 | 0.19266 | 0.30678 | 0.079229 | -122.1807 | 121.9595 | 122.2441 | 122.0916 | 44.9587 | -122.2635
5019.5938 | 122.2 | -0.1236 | 122.113 | -0.010149 | -0.061435 | 0.037943 | 0.014768 | -0.01507 | -0.011705 | -0.029148 | 0.029993 | 0.010315 | 0.069369 | 0.070815 | 0.076744 | -0.040158 | 0.005985 | -0.031301 | 0.07502 | 0.12399 | 0.24269 | -0.12716 | 28.27 | 45.0778 | 22.6815 | 121.8908 | 122.1617 | 122.0229 | -0.20078 | -0.003566 | -122.038 | 0.083438 | 0.092295 | 0.095861 | -121.989 | -121.8703 | -0.077183 | -0.22224 | 28.3936 | 22.8051 | 22.8823 | 0.048627 | -0.090108 | 0.19862 | 0.24759 | 0.36629 | 0.12958 | -122.2402 | 122.0144 | 122.2853 | 122.1465 | 45.2014 | -122.3138
5021.2969 | 122.3236 | -0.082397 | 122.0947 | -0.010149 | -0.061649 | 0.038157 | 0.01434 | -0.014856 | -0.011491 | -0.0062567 | 0.030634 | 0.010529 | 0.069369 | 0.070815 | 0.077385 | -0.044736 | 0.005985 | -0.026723 | 0.07502 | 0.11483 | 0.23812 | -0.118 | 28.6684 | 45.3067 | 22.9288 | 121.8954 | 122.1708 | 122.0275 | -0.1962 | -0.035607 | -122.0197 | 0.037661 | 0.055674 | 0.091281 | -121.9799 | -121.8566 | -0.1138 | -0.19936 | 28.7507 | 23.0112 | 23.125 | 0.076095 | -0.067219 | 0.15742 | 0.19723 | 0.32051 | 0.088382 | -122.2127 | 121.9778 | 122.2532 | 122.1099 | 45.3891 | -122.2909
5023.0625 | 122.3053 | -0.07782 | 122.0444 | -0.010149 | -0.061222 | 0.037943 | 0.014554 | -0.014856 | -0.012132 | -0.021518 | 0.031061 | 0.010529 | 0.069583 | 0.070602 | 0.078026 | -0.040158 | 0.015142 | -0.026723 | 0.07502 | 0.11941 | 0.23812 | -0.118 | 29.0575 | 45.4669 | 23.2264 | 121.8908 | 122.1708 | 122.0275 | -0.19162 | -0.040184 | -121.9694 | 0.037662 | 0.051097 | 0.091281 | -121.925 | -121.8063 | -0.1138 | -0.15358 | 29.1354 | 23.3042 | 23.418 | 0.12645 | -0.016865 | 0.15284 | 0.19723 | 0.31594 | 0.092962 | -122.1624 | 121.9686 | 122.2486 | 122.1053 | 45.5448 | -122.236
5024.8438 | 122.3053 | -0.068665 | 122.0764 | -0.01778 | -0.061222 | 0.038157 | 0.01434 | -0.01507 | -0.011705 | -0.021518 | 0.031702 | 0.010529 | 0.069583 | 0.071243 | 0.078667 | -0.044736 | 0.005985 | -0.031301 | 0.07502 | 0.11483 | 0.23812 | -0.118 | 29.3964 | 45.6638 | 23.5103 | 121.8954 | 122.1708 | 122.0275 | -0.20536 | -0.049339 | -122.0014 | 0.023929 | 0.037364 | 0.086703 | -121.9616 | -121.8383 | -0.13669 | -0.18104 | 29.465 | 23.5789 | 23.7156 | 0.094406 | -0.048908 | 0.14369 | 0.1835 | 0.30678 | 0.07465 | -122.1944 | 121.964 | 122.2395 | 122.0962 | 45.7325 | -122.2818
5026.5469 | 122.3282 | -0.082397 | 122.0764 | -0.010149 | -0.061435 | 0.03837 | 0.01434 | -0.01507 | -0.011705 | -0.021518 | 0.031702 | 0.010743 | 0.069797 | 0.071243 | 0.078881 | -0.03558 | 0.015142 | -0.026723 | 0.07502 | 0.11483 | 0.24269 | -0.12716 | 29.7306 | 45.847 | 23.785 | 121.8954 | 122.18 | 122.0229 | -0.20078 | -0.044765 | -122.0014 | 0.046817 | 0.055674 | 0.10044 | -121.9616 | -121.8337 | -0.11838 | -0.18104 | 29.813 | 23.8674 | 23.9858 | 0.10356 | -0.053487 | 0.15742 | 0.19723 | 0.32509 | 0.097539 | -122.2036 | 121.9778 | 122.2624 | 122.1053 | 45.9294 | -122.2772
5028.3125 | 122.3282 | -0.073242 | 122.0856 | -0.0025182 | -0.061435 | 0.03837 | 0.014554 | -0.015283 | -0.011491 | -0.029148 | 0.032556 | 0.010743 | 0.070224 | 0.071243 | 0.079735 | -0.040158 | 0.005985 | -0.031301 | 0.070441 | 0.11941 | 0.23812 | -0.12716 | 30.0832 | 46.0072 | 24.0322 | 121.8954 | 122.1846 | 122.0321 | -0.20078 | -0.05392 | -122.0151 | 0.033084 | 0.041941 | 0.095861 | -121.9662 | -121.8475 | -0.12754 | -0.1902 | 30.1564 | 24.1055 | 24.233 | 0.098986 | -0.053485 | 0.14368 | 0.19265 | 0.31136 | 0.079227 | -122.2127 | 121.9686 | 122.2578 | 122.1053 | 46.0805 | -122.2863
5030.0781 | 122.2778 | -0.082397 | 122.0352 | -0.010149 | -0.061649 | 0.038584 | 0.014127 | -0.014856 | -0.011491 | -0.029148 | 0.033197 | 0.01117 | 0.070438 | 0.07167 | 0.079735 | -0.044736 | 0.010564 | -0.040457 | 0.07502 | 0.12399 | 0.24269 | -0.118 | 30.4266 | 46.1583 | 24.3299 | 121.8908 | 122.1754 | 122.0229 | -0.20536 | -0.035607 | -121.9602 | 0.037661 | 0.04194 | 0.077547 | -121.9112 | -121.7925 | -0.12296 | -0.14442 | 30.509 | 24.4123 | 24.5352 | 0.14018 | -0.012288 | 0.15742 | 0.20639 | 0.32509 | 0.092961 | -122.1532 | 121.9732 | 122.2578 | 122.1053 | 46.2407 | -122.2406
5031.7812 | 122.3328 | -0.082397 | 122.0764 | -0.01778 | -0.061435 | 0.037943 | 0.014554 | -0.014856 | -0.011491 | -0.021518 | 0.033625 | 0.010956 | 0.070224 | 0.072098 | 0.080376 | -0.040158 | 0.010564 | -0.026723 | 0.07502 | 0.11483 | 0.23812 | -0.12716 | 30.7929 | 46.3094 | 24.5863 | 121.8954 | 122.18 | 122.0184 | -0.20078 | -0.044765 | -122.0014 | 0.042239 | 0.055674 | 0.10044 | -121.9616 | -121.8383 | -0.11838 | -0.18104 | 30.8753 | 24.6687 | 24.787 | 0.10356 | -0.058065 | 0.15742 | 0.19723 | 0.32051 | 0.092961 | -122.2036 | 121.9778 | 122.2624 | 122.1007 | 46.3918 | -122.2772
5033.5469 | 122.3145 | -0.07782 | 122.0764 | -0.010149 | -0.061649 | 0.037943 | 0.014768 | -0.01507 | -0.011277 | -0.021518 | 0.034052 | 0.010956 | 0.070438 | 0.072525 | 0.080804 | -0.040158 | 0.015142 | -0.031301 | 0.070441 | 0.11941 | 0.24269 | -0.118 | 31.1225 | 46.488 | 24.9068 | 121.9 | 122.1846 | 122.0367 | -0.20078 | -0.040184 | -122.006 | 0.037662 | 0.046519 | 0.086703 | -121.957 | -121.8337 | -0.12296 | -0.17646 | 31.2004 | 24.9846 | 25.1076 | 0.10814 | -0.039751 | 0.14826 | 0.19723 | 0.32051 | 0.092962 | -122.1944 | 121.9778 | 122.2624 | 122.1145 | 46.5658 | -122.2772
5035.2969 | 122.319 | -0.07782 | 122.0764 | -0.010149 | -0.061649 | 0.037943 | 0.014981 | -0.01507 | -0.011491 | -0.029148 | 0.034906 | 0.011384 | 0.070438 | 0.072525 | 0.081231 | -0.040158 | 0.010564 | -0.031301 | 0.07502 | 0.11941 | 0.23812 | -0.118 | 31.3698 | 46.6299 | 25.1357 | 121.8908 | 122.18 | 122.0275 | -0.20078 | -0.040184 | -122.0014 | 0.037662 | 0.046519 | 0.086703 | -121.957 | -121.8383 | -0.12296 | -0.18562 | 31.4476 | 25.2135 | 25.3365 | 0.10356 | -0.048908 | 0.15284 | 0.19723 | 0.31594 | 0.088384 | -122.1944 | 121.9686 | 122.2578 | 122.1053 | 46.7078 | -122.2772
5037.0781 | 122.3282 | -0.082397 | 122.0718 | -0.01778 | -0.061222 | 0.037943 | 0.014768 | -0.014856 | -0.011491 | -0.029148 | 0.035761 | 0.01117 | 0.070651 | 0.072525 | 0.081872 | -0.031001 | 0.005985 | -0.031301 | 0.07502 | 0.11483 | 0.24269 | -0.12716 | 31.6674 | 46.7261 | 25.4196 | 121.8954 | 122.1846 | 122.0229 | -0.1962 | -0.044765 | -121.9968 | 0.051396 | 0.051096 | 0.095861 | -121.957 | -121.8291 | -0.1138 | -0.17647 | 31.7498 | 25.502 | 25.6158 | 0.11272 | -0.048909 | 0.15742 | 0.19723 | 0.32509 | 0.088382 | -122.199 | 121.9778 | 122.267 | 122.1053 | 46.8085 | -122.268
5038.7969 | 122.1909 | -0.1236 | 122.0901 | -0.010149 | -0.061435 | 0.037729 | 0.014554 | -0.01507 | -0.011277 | -0.021518 | 0.035761 | 0.011384 | 0.070651 | 0.072525 | 0.082086 | -0.040158 | 0.015142 | -0.031301 | 0.084176 | 0.12399 | 0.23354 | -0.118 | 31.9421 | 46.8406 | 25.6439 | 121.8954 | 122.1754 | 122.0321 | -0.20078 | 0.005592 | -122.006 | 0.083438 | 0.092295 | 0.086703 | -121.9662 | -121.8566 | -0.077183 | -0.19478 | 32.0657 | 25.7675 | 25.8447 | 0.085251 | -0.058063 | 0.20777 | 0.24759 | 0.35713 | 0.13874 | -122.2082 | 122.019 | 122.299 | 122.1557 | 46.9642 | -122.2909
5040.5625 | 122.3236 | -0.064087 | 122.081 | -0.010149 | -0.061649 | 0.038157 | 0.01434 | -0.01507 | -0.011491 | -0.029148 | 0.036188 | 0.011597 | 0.070865 | 0.072739 | 0.082727 | -0.040158 | 0.010564 | -0.035879 | 0.070441 | 0.12399 | 0.24269 | -0.12258 | 32.2169 | 46.9321 | 25.8866 | 121.8954 | 122.1846 | 122.0367 | -0.20078 | -0.058496 | -122.0106 | 0.023929 | 0.028208 | 0.086704 | -121.957 | -121.8383 | -0.13669 | -0.18562 | 32.2809 | 25.9507 | 26.0874 | 0.10356 | -0.044329 | 0.13453 | 0.18808 | 0.30678 | 0.074651 | -122.2036 | 121.9595 | 122.2486 | 122.1008 | 46.9962 | -122.2818
5042.3281 | 122.2046 | -0.13275 | 122.1039 | -0.01778 | -0.061649 | 0.038157 | 0.01434 | -0.015283 | -0.011277 | -0.021518 | 0.036402 | 0.012238 | 0.070865 | 0.072952 | 0.083368 | -0.040158 | 0.010564 | -0.026723 | 0.07502 | 0.12399 | 0.24269 | -0.12258 | 32.519 | 47.01 | 26.1293 | 121.8954 | 122.18 | 122.0275 | -0.1962 | 0.010168 | -122.0289 | 0.092593 | 0.10603 | 0.09586 | -121.9799 | -121.8612 | -0.063449 | -0.20851 | 32.6518 | 26.262 | 26.3255 | 0.076097 | -0.076374 | 0.20777 | 0.25674 | 0.37545 | 0.14331 | -122.2265 | 122.0281 | 122.3127 | 122.1603 | 47.1427 | -122.3001
5044.1094 | 122.2778 | -0.054932 | 122.0901 | -0.010149 | -0.061649 | 0.037943 | 0.014768 | -0.015283 | -0.01085 | -0.029148 | 0.03747 | 0.012238 | 0.071079 | 0.073166 | 0.083581 | -0.03558 | 0.005985 | -0.035879 | 0.079598 | 0.11941 | 0.25185 | -0.12716 | 32.7617 | 47.1015 | 26.3765 | 121.8908 | 122.1846 | 122.0275 | -0.19162 | -0.07223 | -122.0106 | 0.019352 | 0.019053 | 0.091283 | -121.9707 | -121.8383 | -0.13669 | -0.19935 | 32.8166 | 26.4315 | 26.5682 | 0.094408 | -0.062641 | 0.13453 | 0.17434 | 0.30678 | 0.060917 | -122.2173 | 121.9457 | 122.2395 | 122.0824 | 47.1565 | -122.2818
5045.8125 | 122.3145 | -0.059509 | 122.0581 | -0.010149 | -0.061649 | 0.037943 | 0.014768 | -0.01507 | -0.011064 | -0.029148 | 0.037684 | 0.012452 | 0.071292 | 0.073593 | 0.084008 | -0.031001 | 0.010564 | -0.022144 | 0.065863 | 0.12399 | 0.24269 | -0.118 | 33.0731 | 47.129 | 26.578 | 121.8954 | 122.18 | 122.0321 | -0.20078 | -0.058495 | -121.9922 | 0.028508 | 0.037365 | 0.09586 | -121.9341 | -121.8154 | -0.14127 | -0.16273 | 33.1326 | 26.6375 | 26.7788 | 0.12187 | -0.026019 | 0.12537 | 0.1835 | 0.3022 | 0.070073 | -122.1761 | 121.9549 | 122.2395 | 122.0916 | 47.1885 | -122.2589
5047.5781 | 122.2778 | -0.082397 | 122.0856 | -0.010149 | -0.061649 | 0.038157 | 0.014768 | -0.014642 | -0.010636 | -0.029148 | 0.038111 | 0.012238 | 0.071506 | 0.073807 | 0.084436 | -0.03558 | 0.010564 | -0.026723 | 0.079598 | 0.12399 | 0.24269 | -0.118 | 33.2837 | 47.2389 | 26.8344 | 121.8908 | 122.18 | 122.0229 | -0.19162 | -0.035607 | -122.006 | 0.046817 | 0.055674 | 0.091281 | -121.9616 | -121.8429 | -0.10922 | -0.19478 | 33.3661 | 26.9168 | 27.026 | 0.094408 | -0.062642 | 0.162 | 0.20639 | 0.32509 | 0.092961 | -122.2036 | 121.9732 | 122.2624 | 122.1053 | 47.3213 | -122.2772
5049.2812 | 122.2733 | -0.086975 | 122.0764 | 0.0051128 | -0.061649 | 0.037943 | 0.014768 | -0.014856 | -0.01085 | -0.021518 | 0.038538 | 0.012238 | 0.071933 | 0.074021 | 0.084863 | -0.031001 | 0.005985 | -0.026723 | 0.084176 | 0.12399 | 0.24727 | -0.12258 | 33.5676 | 47.3534 | 27.0908 | 121.8908 | 122.1754 | 122.0229 | -0.19162 | -0.035608 | -121.9922 | 0.055974 | 0.060252 | 0.09586 | -121.9524 | -121.8291 | -0.10465 | -0.18562 | 33.6545 | 27.1778 | 27.2824 | 0.098984 | -0.053487 | 0.17115 | 0.21097 | 0.33425 | 0.09296 | -122.199 | 121.9778 | 122.2624 | 122.1099 | 47.4404 | -122.268
5051.0469 | 122.2229 | -0.1236 | 122.113 | -0.0025182 | -0.061863 | 0.038157 | 0.014554 | -0.014856 | -0.01085 | -0.013887 | 0.038752 | 0.012666 | 0.07172 | 0.074021 | 0.08529 | -0.03558 | 0.015142 | -0.022144 | 0.079598 | 0.11483 | 0.24269 | -0.12258 | 33.7095 | 47.4175 | 27.306 | 121.9 | 122.18 | 122.0321 | -0.20078 | 0.001013 | -122.0334 | 0.088016 | 0.10145 | 0.10044 | -121.9982 | -121.8703 | -0.077183 | -0.21309 | 33.8331 | 27.4296 | 27.5068 | 0.066942 | -0.080951 | 0.20319 | 0.23843 | 0.36629 | 0.13874 | -122.2356 | 122.0235 | 122.3036 | 122.1557 | 47.5411 | -122.3138
5052.8281 | 122.2412 | -0.11444 | 122.1085 | -0.010149 | -0.061649 | 0.038157 | 0.014768 | -0.01507 | -0.01085 | -0.029148 | 0.039179 | 0.012666 | 0.071933 | 0.074448 | 0.085718 | -0.044736 | 0.005985 | -0.031301 | 0.07502 | 0.12399 | 0.24727 | -0.12258 | 33.9888 | 47.4541 | 27.5487 | 121.8954 | 122.18 | 122.0275 | -0.20078 | -0.008142 | -122.0334 | 0.069705 | 0.08314 | 0.091282 | -121.9845 | -121.8612 | -0.086338 | -0.21309 | 34.1033 | 27.6631 | 27.7495 | 0.07152 | -0.080951 | 0.18946 | 0.23843 | 0.36172 | 0.12043 | -122.231 | 122.0098 | 122.2944 | 122.1419 | 47.5685 | -122.3092
5054.6094 | 122.2458 | -0.11902 | 122.1085 | -0.0025182 | -0.061649 | 0.037943 | 0.014768 | -0.01507 | -0.010636 | -0.021518 | 0.039606 | 0.012452 | 0.072574 | 0.074448 | 0.086145 | -0.044736 | 0.010564 | -0.026723 | 0.065863 | 0.11941 | 0.24269 | -0.13174 | 34.1949 | 47.5732 | 27.8097 | 121.8954 | 122.18 | 122.0367 | -0.1962 | -0.012722 | -122.0426 | 0.074283 | 0.092296 | 0.10502 | -121.989 | -121.8658 | -0.077181 | -0.21309 | 34.3139 | 27.9287 | 28.0059 | 0.07152 | -0.071794 | 0.18488 | 0.23843 | 0.36171 | 0.12958 | -122.2402 | 122.0144 | 122.299 | 122.1557 | 47.6922 | -122.3047
5056.3125 | 122.3007 | -0.054932 | 122.0581 | -0.01778 | -0.061863 | 0.037729 | 0.014554 | -0.01507 | -0.010423 | -0.013887 | 0.040461 | 0.013093 | 0.07172 | 0.074448 | 0.086145 | -0.03558 | 0.010564 | -0.026723 | 0.07502 | 0.11483 | 0.24269 | -0.12258 | 34.4238 | 47.6098 | 28.0066 | 121.9 | 122.18 | 122.0275 | -0.1962 | -0.067651 | -121.9831 | 0.019352 | 0.028209 | 0.09586 | -121.9433 | -121.8154 | -0.14127 | -0.15815 | 34.4787 | 28.0615 | 28.2028 | 0.12187 | -0.030597 | 0.12995 | 0.16976 | 0.29763 | 0.065496 | -122.1807 | 121.9549 | 122.2349 | 122.0824 | 47.6647 | -122.2543
5058.0781 | 122.2824 | -0.068665 | 122.0627 | -0.01778 | -0.061649 | 0.037943 | 0.01434 | -0.01507 | -0.01085 | -0.013887 | 0.040461 | 0.013093 | 0.071933 | 0.074662 | 0.086786 | -0.03558 | 0.010564 | -0.031301 | 0.070441 | 0.11483 | 0.25185 | -0.118 | 34.6985 | 47.6602 | 28.1897 | 121.8908 | 122.1754 | 122.0321 | -0.20078 | -0.049339 | -121.9922 | 0.033085 | 0.037364 | 0.086703 | -121.9479 | -121.8108 | -0.13211 | -0.17189 | 34.7672 | 28.2584 | 28.3905 | 0.11272 | -0.030597 | 0.13911 | 0.1835 | 0.32052 | 0.079229 | -122.1807 | 121.9595 | 122.2441 | 122.1008 | 47.7288 | -122.2635
5059.8438 | 122.1863 | -0.1236 | 122.0947 | -0.010149 | -0.061649 | 0.03837 | 0.014554 | -0.01507 | -0.010209 | -0.021518 | 0.040888 | 0.01352 | 0.072788 | 0.074448 | 0.087213 | -0.040158 | 0.005985 | -0.035879 | 0.079598 | 0.11941 | 0.24269 | -0.12258 | 34.8954 | 47.6968 | 28.3729 | 121.8908 | 122.1754 | 122.0321 | -0.19162 | 0.001013 | -122.0151 | 0.083438 | 0.087717 | 0.086704 | -121.9753 | -121.852 | -0.068026 | -0.20393 | 35.019 | 28.4965 | 28.5645 | 0.080673 | -0.062641 | 0.20319 | 0.24301 | 0.36629 | 0.12958 | -122.2173 | 122.0144 | 122.299 | 122.1557 | 47.8204 | -122.2863
5061.6094 | 122.3053 | -0.073242 | 122.0856 | -0.010149 | -0.061649 | 0.037729 | 0.014768 | -0.014856 | -0.01085 | -0.029148 | 0.041529 | 0.013307 | 0.072574 | 0.074875 | 0.087427 | -0.03558 | 0.010564 | -0.022144 | 0.070441 | 0.11941 | 0.24727 | -0.12258 | 35.0328 | 47.7288 | 28.5468 | 121.8908 | 122.1846 | 122.0275 | -0.1962 | -0.049341 | -122.0151 | 0.037662 | 0.051098 | 0.10044 | -121.9662 | -121.8383 | -0.12296 | -0.19478 | 35.106 | 28.6201 | 28.743 | 0.098986 | -0.058063 | 0.14368 | 0.19265 | 0.32052 | 0.083806 | -122.2082 | 121.964 | 122.2578 | 122.1007 | 47.8021 | -122.2818
5063.375 | 122.3328 | -0.073242 | 122.0856 | -0.010149 | -0.061649 | 0.038157 | 0.014554 | -0.014856 | -0.010209 | -0.029148 | 0.041956 | 0.013093 | 0.072574 | 0.075089 | 0.087854 | -0.044736 | 0.010564 | -0.035879 | 0.079598 | 0.11941 | 0.24269 | -0.12258 | 35.2754 | 47.7563 | 28.7895 | 121.8954 | 122.1754 | 122.0321 | -0.1962 | -0.049341 | -122.006 | 0.028506 | 0.037363 | 0.086704 | -121.9662 | -121.8429 | -0.12296 | -0.1902 | 35.3487 | 28.8628 | 28.9857 | 0.089829 | -0.053485 | 0.15284 | 0.19265 | 0.31594 | 0.083806 | -122.2082 | 121.9686 | 122.2486 | 122.1053 | 47.8295 | -122.2818
5065.0781 | 122.2229 | -0.1236 | 122.0947 | -0.01778 | -0.061863 | 0.038157 | 0.014554 | -0.014856 | -0.0099951 | -0.029148 | 0.042384 | 0.01352 | 0.072788 | 0.07573 | 0.088282 | -0.03558 | 0.015142 | -0.022144 | 0.079598 | 0.11941 | 0.24269 | -0.12716 | 35.4906 | 47.8616 | 29.0963 | 121.8908 | 122.1754 | 122.0275 | -0.20078 | -0.003566 | -122.0151 | 0.088016 | 0.10145 | 0.10502 | -121.9753 | -121.852 | -0.077183 | -0.20393 | 35.6142 | 29.2199 | 29.2971 | 0.080673 | -0.067219 | 0.20319 | 0.24301 | 0.36629 | 0.13874 | -122.2219 | 122.0144 | 122.299 | 122.1511 | 47.9852 | -122.2955
5066.8281 | 122.3099 | -0.054932 | 122.081 | -0.010149 | -0.061649 | 0.037943 | 0.01434 | -0.014856 | -0.010209 | -0.013887 | 0.042597 | 0.013734 | 0.072788 | 0.075516 | 0.088709 | -0.040158 | 0.010564 | -0.022144 | 0.079598 | 0.11941 | 0.24727 | -0.12258 | 35.7516 | 47.8662 | 29.3252 | 121.8908 | 122.1754 | 122.0184 | -0.1962 | -0.067651 | -122.0014 | 0.014774 | 0.032788 | 0.10044 | -121.9616 | -121.8337 | -0.14127 | -0.1902 | 35.8065 | 29.3802 | 29.5214 | 0.094406 | -0.062643 | 0.13453 | 0.17434 | 0.30221 | 0.065496 | -122.2036 | 121.9457 | 122.2303 | 122.0733 | 47.9211 | -122.2772
5068.6094 | 122.3145 | -0.068665 | 122.0993 | -0.010149 | -0.061222 | 0.038157 | 0.014554 | -0.014856 | -0.010209 | -0.013887 | 0.043025 | 0.013093 | 0.072788 | 0.076157 | 0.088922 | -0.03558 | 0.015142 | -0.035879 | 0.07502 | 0.12399 | 0.25185 | -0.118 | 35.9989 | 47.9761 | 29.6137 | 121.8954 | 122.18 | 122.0275 | -0.1962 | -0.049339 | -122.0243 | 0.033085 | 0.032786 | 0.082125 | -121.9753 | -121.8475 | -0.12754 | -0.20393 | 36.0675 | 29.6824 | 29.8099 | 0.080675 | -0.071796 | 0.14369 | 0.19266 | 0.32052 | 0.083807 | -122.2173 | 121.964 | 122.2486 | 122.0962 | 48.0447 | -122.2955
5070.3125 | 122.3007 | -0.068665 | 122.081 | -0.033042 | -0.06229 | 0.038157 | 0.013913 | -0.014856 | -0.010209 | -0.029148 | 0.043025 | 0.013948 | 0.073215 | 0.075944 | 0.08935 | -0.044736 | 0.010564 | -0.031301 | 0.07502 | 0.12857 | 0.23812 | -0.12258 | 36.2095 | 47.9349 | 29.7144 | 121.8908 | 122.1754 | 122.0229 | -0.1962 | -0.053918 | -122.006 | 0.023929 | 0.037364 | 0.091282 | -121.9524 | -121.8429 | -0.12754 | -0.1902 | 36.2782 | 29.7831 | 29.9106 | 0.094406 | -0.058065 | 0.14369 | 0.19723 | 0.30678 | 0.079229 | -122.2036 | 121.9595 | 122.2441 | 122.0916 | 48.0035 | -122.2772
5072.0938 | 122.2641 | -0.086975 | 122.113 | -0.010149 | -0.061863 | 0.037943 | 0.014554 | -0.015283 | -0.0099951 | -0.021518 | 0.043665 | 0.014161 | 0.073001 | 0.076157 | 0.08935 | -0.040158 | 0.015142 | -0.026723 | 0.079598 | 0.11483 | 0.23812 | -0.118 | 36.4384 | 47.9852 | 29.8838 | 121.8954 | 122.1846 | 122.0275 | -0.1962 | -0.031029 | -122.0334 | 0.046817 | 0.060252 | 0.091281 | -121.9982 | -121.8749 | -0.10923 | -0.21767 | 36.5254 | 29.9708 | 30.08 | 0.07152 | -0.085529 | 0.16657 | 0.20181 | 0.32509 | 0.10212 | -122.231 | 121.9823 | 122.2715 | 122.1145 | 48.0722 | -122.3092
5073.7969 | 122.2778 | -0.086975 | 122.0901 | -0.01778 | -0.061863 | 0.038157 | 0.014768 | -0.01507 | -0.0097815 | -0.029148 | 0.043879 | 0.014161 | 0.073215 | 0.076371 | 0.090204 | -0.040158 | 0.005985 | -0.026723 | 0.07502 | 0.12399 | 0.23812 | -0.12258 | 36.6033 | 47.999 | 30.0716 | 121.8954 | 122.1846 | 122.0184 | -0.1962 | -0.035608 | -122.0151 | 0.046817 | 0.060252 | 0.09586 | -121.9662 | -121.852 | -0.10923 | -0.19478 | 36.6902 | 30.1585 | 30.2678 | 0.094408 | -0.071798 | 0.162 | 0.21097 | 0.32509 | 0.09296 | -122.2127 | 121.9823 | 122.2715 | 122.1053 | 48.0859 | -122.2863
5075.5469 | 122.3099 | -0.082397 | 122.0581 | -0.01778 | -0.061649 | 0.037943 | 0.014127 | -0.014856 | -0.0099951 | -0.021518 | 0.044734 | 0.014161 | 0.073429 | 0.076585 | 0.090204 | -0.031001 | 0.005985 | -0.031301 | 0.07502 | 0.12399 | 0.24727 | -0.118 | 36.8551 | 48.0356 | 30.2822 | 121.8816 | 122.1708 | 122.0321 | -0.19162 | -0.035607 | -121.9831 | 0.051396 | 0.051096 | 0.086703 | -121.9341 | -121.8108 | -0.10922 | -0.17647 | 36.9375 | 30.3646 | 30.4738 | 0.11272 | -0.026019 | 0.15742 | 0.20639 | 0.32967 | 0.088382 | -122.1761 | 121.964 | 122.2532 | 122.1145 | 48.118 | -122.2497
5077.3125 | 122.2092 | -0.11902 | 122.1222 | -0.01778 | -0.062076 | 0.038157 | 0.014554 | -0.014642 | -0.0099951 | -0.013887 | 0.04452 | 0.014161 | 0.073856 | 0.076798 | 0.090418 | -0.044736 | 0.010564 | -0.031301 | 0.079598 | 0.11941 | 0.25185 | -0.12258 | 36.965 | 48.1226 | 30.4745 | 121.8908 | 122.18 | 122.0275 | -0.20078 | -0.003564 | -122.0426 | 0.074283 | 0.087718 | 0.091282 | -122.0028 | -121.8703 | -0.08176 | -0.2314 | 37.084 | 30.5935 | 30.6753 | 0.057787 | -0.094684 | 0.19862 | 0.23843 | 0.37087 | 0.12958 | -122.2448 | 122.0098 | 122.299 | 122.1465 | 48.2416 | -122.323
5079.0312 | 122.2046 | -0.10986 | 122.1313 | -0.010149 | -0.061863 | 0.038157 | 0.014768 | -0.014856 | -0.010209 | -0.013887 | 0.044947 | 0.014375 | 0.073642 | 0.076585 | 0.091273 | -0.040158 | 0.015142 | -0.035879 | 0.070441 | 0.12399 | 0.24269 | -0.118 | 37.1985 | 48.173 | 30.6439 | 121.8954 | 122.1846 | 122.0275 | -0.20536 | -0.008141 | -122.0609 | 0.069705 | 0.073984 | 0.082125 | -122.0074 | -121.8887 | -0.095495 | -0.23598 | 37.3083 | 30.7538 | 30.8493 | 0.053209 | -0.10384 | 0.1803 | 0.23385 | 0.35256 | 0.12501 | -122.2494 | 122.0052 | 122.2944 | 122.1374 | 48.2828 | -122.3367
5080.7969 | 122.3236 | -0.064087 | 122.0627 | -0.025411 | -0.062076 | 0.037943 | 0.014768 | -0.015283 | -0.010209 | -0.029148 | 0.045375 | 0.014802 | 0.073856 | 0.077012 | 0.091486 | -0.031001 | 0.010564 | -0.026723 | 0.088755 | 0.11941 | 0.24269 | -0.118 | 37.3587 | 48.1455 | 30.8362 | 121.8908 | 122.18 | 122.0321 | -0.1962 | -0.053917 | -121.9739 | 0.033086 | 0.037364 | 0.091281 | -121.9433 | -121.82 | -0.13211 | -0.17189 | 37.4228 | 30.9003 | 31.0324 | 0.1173 | -0.030597 | 0.15284 | 0.1835 | 0.30678 | 0.074651 | -122.1807 | 121.9549 | 122.2441 | 122.0962 | 48.2096 | -122.2589
5082.5625 | 122.2137 | -0.10986 | 122.0901 | -0.010149 | -0.061863 | 0.037943 | 0.01434 | -0.015283 | -0.0099951 | -0.021518 | 0.045588 | 0.014375 | 0.073642 | 0.077439 | 0.091914 | -0.03558 | 0.019721 | -0.017566 | 0.079598 | 0.12399 | 0.24269 | -0.12258 | 37.5556 | 48.1409 | 31.0239 | 121.8908 | 122.1754 | 122.0275 | -0.1962 | -0.01272 | -122.0106 | 0.074283 | 0.092297 | 0.10502 | -121.9662 | -121.8475 | -0.086337 | -0.19935 | 37.6655 | 31.1338 | 31.2201 | 0.085251 | -0.062641 | 0.18946 | 0.23385 | 0.35256 | 0.12958 | -122.2127 | 122.0007 | 122.2853 | 122.1374 | 48.2508 | -122.2863
5084.3281 | 122.3328 | -0.082397 | 122.0581 | -0.01778 | -0.062076 | 0.037729 | 0.014554 | -0.014856 | -0.0097815 | -0.029148 | 0.046016 | 0.015016 | 0.07407 | 0.077012 | 0.092555 | -0.03558 | 0.005985 | -0.026723 | 0.07502 | 0.12399 | 0.24269 | -0.12258 | 37.7983 | 48.1821 | 31.1979 | 121.8908 | 122.1754 | 122.0321 | -0.19162 | -0.040186 | -121.9831 | 0.046817 | 0.055674 | 0.09586 | -121.9341 | -121.8154 | -0.10922 | -0.16731 | 37.8807 | 31.2803 | 31.3895 | 0.11729 | -0.026019 | 0.15742 | 0.20639 | 0.32509 | 0.088382 | -122.1807 | 121.9732 | 122.2578 | 122.1145 | 48.2645 | -122.2497
5086.0312 | 122.1954 | -0.1236 | 122.0764 | -0.0025182 | -0.062076 | 0.037943 | 0.01434 | -0.01507 | -0.0099951 | -0.013887 | 0.046656 | 0.015016 | 0.07407 | 0.077226 | 0.092768 | -0.040158 | 0.010564 | -0.031301 | 0.07502 | 0.11941 | 0.24727 | -0.12716 | 37.899 | 48.1363 | 31.3856 | 121.8954 | 122.1708 | 122.0321 | -0.1962 | -0.003566 | -122.0014 | 0.083438 | 0.092295 | 0.095861 | -121.957 | -121.8291 | -0.072604 | -0.18104 | 38.0226 | 31.5092 | 31.5818 | 0.094406 | -0.04433 | 0.19862 | 0.24301 | 0.37087 | 0.13416 | -122.2036 | 122.019 | 122.2944 | 122.1557 | 48.2599 | -122.2726
5087.7969 | 122.3099 | -0.086975 | 122.0947 | -0.01778 | -0.062076 | 0.038157 | 0.014768 | -0.014856 | -0.0097815 | -0.021518 | 0.046443 | 0.015229 | 0.074497 | 0.077226 | 0.093196 | -0.03558 | 0.010564 | -0.026723 | 0.079598 | 0.12399 | 0.24269 | -0.12716 | 38.0455 | 48.205 | 31.6512 | 121.8908 | 122.18 | 122.0229 | -0.1962 | -0.040187 | -122.0151 | 0.051395 | 0.060252 | 0.10044 | -121.9707 | -121.852 | -0.10923 | -0.20393 | 38.1325 | 31.7382 | 31.8474 | 0.085252 | -0.071798 | 0.16657 | 0.21097 | 0.32967 | 0.097539 | -122.2219 | 121.9778 | 122.267 | 122.1099 | 48.292 | -122.2909
5089.5781 | 122.3236 | -0.068665 | 122.0718 | -0.0025182 | -0.062076 | 0.037943 | 0.014554 | -0.015283 | -0.0095679 | -0.036779 | 0.047084 | 0.015016 | 0.074924 | 0.077653 | 0.093196 | -0.044736 | 0.015142 | -0.026723 | 0.070441 | 0.12857 | 0.23812 | -0.12716 | 38.247 | 48.2508 | 31.8573 | 121.9 | 122.18 | 122.0229 | -0.18246 | -0.058497 | -122.0014 | 0.023929 | 0.041942 | 0.10044 | -121.9433 | -121.8337 | -0.1138 | -0.17189 | 38.3157 | 31.9259 | 32.0397 | 0.10814 | -0.048909 | 0.13911 | 0.19723 | 0.30678 | 0.083807 | -122.199 | 121.9686 | 122.2486 | 122.0916 | 48.3195 | -122.2543
5091.3438 | 122.2595 | -0.10071 | 122.1176 | -0.0025182 | -0.061863 | 0.038157 | 0.014554 | -0.014856 | -0.0097815 | -0.029148 | 0.047084 | 0.015443 | 0.074711 | 0.077867 | 0.093409 | -0.03558 | 0.010564 | -0.026723 | 0.079598 | 0.12857 | 0.24727 | -0.12716 | 38.302 | 48.2783 | 32.0587 | 121.8862 | 122.1846 | 122.0138 | -0.1962 | -0.026454 | -122.038 | 0.065128 | 0.073985 | 0.10044 | -121.989 | -121.8703 | -0.095492 | -0.2314 | 38.4027 | 32.1594 | 32.2549 | 0.066942 | -0.10384 | 0.18031 | 0.22928 | 0.34798 | 0.11127 | -122.2448 | 121.9869 | 122.2853 | 122.1145 | 48.379 | -122.3138
5093.0469 | 122.2 | -0.10986 | 122.1268 | -0.010149 | -0.062076 | 0.037943 | 0.014554 | -0.014856 | -0.0097815 | -0.021518 | 0.047511 | 0.015443 | 0.075138 | 0.077867 | 0.093837 | -0.040158 | 0.015142 | -0.031301 | 0.07502 | 0.11941 | 0.24727 | -0.118 | 38.4622 | 48.292 | 32.164 | 121.8908 | 122.1846 | 122.0229 | -0.20078 | -0.008141 | -122.0517 | 0.069705 | 0.078562 | 0.086703 | -122.0074 | -121.8795 | -0.090916 | -0.23598 | 38.5721 | 32.2739 | 32.3648 | 0.057787 | -0.10384 | 0.18488 | 0.22927 | 0.35714 | 0.12501 | -122.2448 | 122.0007 | 122.2944 | 122.1328 | 48.4019 | -122.3275
5094.8281 | 122.2275 | -0.10529 | 122.113 | -0.010149 | -0.06229 | 0.037943 | 0.014554 | -0.01507 | -0.0095679 | -0.013887 | 0.048152 | 0.015443 | 0.074711 | 0.077867 | 0.093837 | -0.040158 | 0.010564 | -0.022144 | 0.079598 | 0.11941 | 0.24727 | -0.12258 | 38.6408 | 48.2554 | 32.3105 | 121.8908 | 122.1754 | 122.0321 | -0.19162 | -0.017297 | -122.0334 | 0.065128 | 0.083142 | 0.10044 | -121.9936 | -121.8658 | -0.086336 | -0.22224 | 38.7461 | 32.4158 | 32.5022 | 0.062363 | -0.080951 | 0.18488 | 0.2247 | 0.35256 | 0.11585 | -122.2356 | 121.9961 | 122.2807 | 122.1374 | 48.3607 | -122.3047
5096.6094 | 122.2092 | -0.13275 | 122.1085 | -0.01778 | -0.062076 | 0.038157 | 0.014768 | -0.014856 | -0.0089269 | -0.029148 | 0.048366 | 0.015443 | 0.075138 | 0.078508 | 0.094477 | -0.040158 | 0.015142 | -0.035879 | 0.07502 | 0.12857 | 0.24727 | -0.12716 | 38.7598 | 48.347 | 32.5624 | 121.8954 | 122.1754 | 122.0229 | -0.19162 | 0.005589 | -122.0334 | 0.092593 | 0.096872 | 0.091283 | -121.9799 | -121.8612 | -0.058871 | -0.21309 | 38.8926 | 32.6951 | 32.754 | 0.066941 | -0.08553 | 0.20777 | 0.26132 | 0.38003 | 0.14789 | -122.2356 | 122.0281 | 122.3082 | 122.1557 | 48.4797 | -122.3001
5098.375 | 122.3053 | -0.068665 | 122.0718 | -0.01778 | -0.061863 | 0.038157 | 0.01434 | -0.014856 | -0.0095679 | -0.013887 | 0.048793 | 0.015657 | 0.075565 | 0.078721 | 0.094691 | -0.031001 | 0.005985 | -0.031301 | 0.07502 | 0.11941 | 0.23812 | -0.12258 | 38.975 | 48.3836 | 32.9424 | 121.8908 | 122.1754 | 122.0184 | -0.20078 | -0.053918 | -121.9968 | 0.037664 | 0.037364 | 0.091282 | -121.9524 | -121.8337 | -0.13211 | -0.18104 | 39.0437 | 33.0111 | 33.1432 | 0.10356 | -0.053487 | 0.14369 | 0.18808 | 0.30678 | 0.07465 | -122.1944 | 121.9595 | 122.2441 | 122.087 | 48.4523 | -122.2726
5100.0781 | 122.2778 | -0.091553 | 122.0856 | -0.025411 | -0.062717 | 0.03837 | 0.014554 | -0.01507 | -0.0093541 | -0.021518 | 0.04922 | 0.015443 | 0.075565 | 0.078721 | 0.095332 | -0.040158 | 0.010564 | -0.031301 | 0.07502 | 0.13315 | 0.24269 | -0.12258 | 39.1444 | 48.4019 | 33.1713 | 121.8908 | 122.18 | 122.0184 | -0.19162 | -0.03103 | -122.0106 | 0.051395 | 0.060252 | 0.091282 | -121.9524 | -121.8429 | -0.10007 | -0.19478 | 39.236 | 33.2629 | 33.363 | 0.094408 | -0.06722 | 0.16657 | 0.2247 | 0.33425 | 0.10212 | -122.2082 | 121.9823 | 122.2715 | 122.1099 | 48.4935 | -122.2772
5101.8438 | 122.2183 | -0.10529 | 122.1176 | -0.010149 | -0.06229 | 0.038157 | 0.014127 | -0.014642 | -0.0093541 | -0.021518 | 0.049647 | 0.015657 | 0.075779 | 0.078935 | 0.095973 | -0.040158 | 0.019721 | -0.026723 | 0.079598 | 0.12399 | 0.24269 | -0.11342 | 39.3413 | 48.4797 | 33.3499 | 121.8908 | 122.1754 | 122.0229 | -0.19162 | -0.008139 | -122.038 | 0.065128 | 0.078563 | 0.086702 | -121.9936 | -121.8749 | -0.086336 | -0.22682 | 39.4466 | 33.4552 | 33.5415 | 0.057785 | -0.094686 | 0.18488 | 0.22928 | 0.34798 | 0.12501 | -122.231 | 121.9961 | 122.2807 | 122.1282 | 48.585 | -122.3092
5103.625 | 122.2733 | -0.09613 | 122.0627 | -0.010149 | -0.06229 | 0.03837 | 0.014768 | -0.014856 | -0.0091405 | -0.021518 | 0.049861 | 0.016084 | 0.07642 | 0.078721 | 0.0964 | -0.040158 | 0.005985 | -0.026723 | 0.079598 | 0.12399 | 0.24269 | -0.12258 | 39.703 | 48.4935 | 33.5239 | 121.8862 | 122.18 | 122.0229 | -0.20078 | -0.026453 | -121.9831 | 0.055972 | 0.069407 | 0.09586 | -121.9387 | -121.82 | -0.10465 | -0.17647 | 39.7992 | 33.62 | 33.7247 | 0.1173 | -0.039754 | 0.17573 | 0.22012 | 0.33882 | 0.10211 | -122.1853 | 121.9823 | 122.2761 | 122.1191 | 48.5896 | -122.2635
5105.3281 | 122.2366 | -0.10071 | 122.0856 | -0.01778 | -0.061863 | 0.038157 | 0.014554 | -0.015283 | -0.0091405 | -0.021518 | 0.050288 | 0.016084 | 0.076206 | 0.078721 | 0.096614 | -0.040158 | 0.019721 | -0.017566 | 0.07502 | 0.12399 | 0.24727 | -0.12258 | 39.7305 | 48.3241 | 33.6063 | 121.8816 | 122.1754 | 122.0229 | -0.1962 | -0.021875 | -122.0106 | 0.06055 | 0.083142 | 0.10502 | -121.9616 | -121.8383 | -0.095492 | -0.20393 | 39.8312 | 33.707 | 33.8025 | 0.089829 | -0.062642 | 0.17573 | 0.2247 | 0.34798 | 0.12043 | -122.2082 | 121.9823 | 122.2761 | 122.1236 | 48.4248 | -122.2818
5107.0938 | 122.1634 | -0.1236 | 122.113 | -0.010149 | -0.062076 | 0.038157 | 0.014554 | -0.01507 | -0.0091405 | -0.021518 | 0.050716 | 0.016298 | 0.076206 | 0.079362 | 0.097041 | -0.040158 | 0.019721 | -0.026723 | 0.084176 | 0.12399 | 0.24269 | -0.12258 | 40.0236 | 48.2691 | 33.8673 | 121.8954 | 122.1754 | 122.0275 | -0.19162 | 0.001013 | -122.0289 | 0.083438 | 0.096873 | 0.09586 | -121.989 | -121.8703 | -0.068026 | -0.21767 | 40.1471 | 33.9909 | 34.0589 | 0.062363 | -0.085529 | 0.20777 | 0.24759 | 0.36629 | 0.14332 | -122.2356 | 122.019 | 122.299 | 122.1511 | 48.3927 | -122.3047
5108.8594 | 122.2961 | -0.064087 | 122.0535 | -0.010149 | -0.062504 | 0.038157 | 0.014554 | -0.014642 | -0.0087131 | -0.036779 | 0.051356 | 0.016298 | 0.076633 | 0.079576 | 0.097255 | -0.040158 | 0.015142 | -0.022144 | 0.070441 | 0.13315 | 0.24269 | -0.12258 | 40.0602 | 48.2966 | 34.1741 | 121.8771 | 122.1662 | 122.0229 | -0.20078 | -0.058496 | -121.9831 | 0.023929 | 0.041943 | 0.10044 | -121.9204 | -121.8108 | -0.13669 | -0.17647 | 40.1243 | 34.2382 | 34.3749 | 0.11271 | -0.030599 | 0.13453 | 0.19723 | 0.30678 | 0.079229 | -122.1761 | 121.9411 | 122.2303 | 122.087 | 48.3607 | -122.2543
5110.6406 | 122.2687 | -0.086975 | 122.0581 | -0.010149 | -0.06229 | 0.038157 | 0.014127 | -0.014856 | -0.0089269 | -0.029148 | 0.05157 | 0.016511 | 0.076847 | 0.079576 | 0.097682 | -0.044736 | 0.019721 | -0.026723 | 0.079598 | 0.12857 | 0.24727 | -0.12258 | 40.3486 | 48.466 | 34.4671 | 121.8908 | 122.18 | 122.0138 | -0.20078 | -0.035608 | -121.9785 | 0.042239 | 0.060252 | 0.09586 | -121.9295 | -121.8108 | -0.1138 | -0.16731 | 40.4356 | 34.5541 | 34.6679 | 0.12187 | -0.044333 | 0.16657 | 0.21554 | 0.33425 | 0.1067 | -122.1807 | 121.9778 | 122.267 | 122.1007 | 48.553 | -122.2589
5112.4062 | 122.2412 | -0.10071 | 122.081 | -0.010149 | -0.06229 | 0.03837 | 0.014768 | -0.015283 | -0.0087131 | -0.021518 | 0.05157 | 0.016298 | 0.077061 | 0.07979 | 0.097682 | -0.03558 | 0.010564 | -0.022144 | 0.07502 | 0.12399 | 0.25185 | -0.12258 | 40.1334 | 48.4752 | 34.632 | 121.8816 | 122.1708 | 122.0184 | -0.1962 | -0.021875 | -122.006 | 0.065128 | 0.078564 | 0.10044 | -121.957 | -121.8291 | -0.095492 | -0.19936 | 40.2341 | 34.7327 | 34.8282 | 0.089828 | -0.062643 | 0.17573 | 0.2247 | 0.35256 | 0.11127 | -122.2036 | 121.9823 | 122.2715 | 122.1191 | 48.5759 | -122.2772
5114.1094 | 122.2687 | -0.086975 | 122.0673 | -0.010149 | -0.062076 | 0.037729 | 0.014768 | -0.01507 | -0.0084995 | -0.029148 | 0.051784 | 0.016725 | 0.076847 | 0.079576 | 0.09811 | -0.03558 | 0.015142 | -0.026723 | 0.079598 | 0.11941 | 0.24269 | -0.12258 | 40.2342 | 48.3286 | 34.7464 | 121.8862 | 122.1754 | 122.0138 | -0.18704 | -0.035608 | -121.9877 | 0.051395 | 0.060252 | 0.09586 | -121.9479 | -121.8246 | -0.10007 | -0.18105 | 40.3211 | 34.8334 | 34.9335 | 0.10814 | -0.053489 | 0.16657 | 0.20639 | 0.32967 | 0.10212 | -122.1898 | 121.9732 | 122.2624 | 122.1007 | 48.4156 | -122.2543
5115.875 | 122.2046 | -0.11444 | 122.0947 | 0.012744 | -0.06229 | 0.037943 | 0.014554 | -0.01507 | -0.0087131 | -0.013887 | 0.052211 | 0.016298 | 0.077274 | 0.080217 | 0.098537 | -0.03558 | 0.010564 | -0.035879 | 0.079598 | 0.11941 | 0.24727 | -0.12258 | 40.3532 | 48.4248 | 35.044 | 121.8816 | 122.1708 | 122.0229 | -0.19162 | -0.008142 | -122.0151 | 0.078861 | 0.078562 | 0.086704 | -121.9753 | -121.8475 | -0.077181 | -0.21309 | 40.4677 | 35.1585 | 35.2357 | 0.076095 | -0.071798 | 0.19404 | 0.23385 | 0.36172 | 0.12501 | -122.2173 | 121.9961 | 122.2853 | 122.1374 | 48.5392 | -122.2863
5117.6406 | 122.2046 | -0.11902 | 122.1039 | -0.010149 | -0.062504 | 0.038157 | 0.014554 | -0.01507 | -0.0087131 | -0.013887 | 0.053066 | 0.016725 | 0.077061 | 0.080217 | 0.099391 | -0.03558 | 0.010564 | -0.026723 | 0.084176 | 0.12399 | 0.24727 | -0.13174 | 40.5409 | 48.434 | 34.9754 | 121.8862 | 122.1708 | 122.0229 | -0.18704 | -0.012722 | -122.0197 | 0.083439 | 0.092296 | 0.10502 | -121.9799 | -121.8566 | -0.068024 | -0.21767 | 40.66 | 35.0944 | 35.1624 | 0.06694 | -0.080953 | 0.2032 | 0.24301 | 0.36629 | 0.12958 | -122.2356 | 122.0052 | 122.2898 | 122.1419 | 48.553 | -122.2909
5119.3594 | 122.3053 | -0.073242 | 122.0627 | -0.01778 | -0.06229 | 0.038157 | 0.014554 | -0.01507 | -0.0087131 | -0.021518 | 0.052852 | 0.016939 | 0.077274 | 0.080217 | 0.099178 | -0.040158 | 0.010564 | -0.035879 | 0.084176 | 0.11941 | 0.24727 | -0.118 | 40.6188 | 48.434 | 35.2318 | 121.8908 | 122.1754 | 122.0184 | -0.19162 | -0.044762 | -121.9785 | 0.033084 | 0.037363 | 0.082125 | -121.9433 | -121.8154 | -0.11838 | -0.17189 | 40.692 | 35.305 | 35.4234 | 0.11272 | -0.044332 | 0.15742 | 0.19265 | 0.32052 | 0.083806 | -122.1807 | 121.964 | 122.2486 | 122.0916 | 48.5072 | -122.2543
5121.125 | 122.2733 | -0.091553 | 122.0581 | -0.01778 | -0.062504 | 0.037943 | 0.014554 | -0.014856 | -0.0082859 | -0.021518 | 0.053706 | 0.016939 | 0.077915 | 0.080431 | 0.099819 | -0.031001 | 0.010564 | -0.026723 | 0.07502 | 0.12399 | 0.25185 | -0.118 | 40.6463 | 48.3973 | 35.4103 | 121.8816 | 122.1846 | 122.0092 | -0.19162 | -0.026451 | -121.9831 | 0.060552 | 0.06483 | 0.091281 | -121.9341 | -121.8063 | -0.10007 | -0.17647 | 40.7378 | 35.5019 | 35.602 | 0.12645 | -0.048912 | 0.16657 | 0.21554 | 0.34341 | 0.10212 | -122.1761 | 121.9732 | 122.2761 | 122.1007 | 48.4889 | -122.2497
5122.8281 | 122.3145 | -0.082397 | 122.0444 | -0.010149 | -0.062076 | 0.038157 | 0.01434 | -0.01507 | -0.0082859 | -0.029148 | 0.05392 | 0.01758 | 0.078556 | 0.080858 | 0.10025 | -0.040158 | 0.019721 | -0.022144 | 0.070441 | 0.12857 | 0.25185 | -0.12716 | 40.2159 | 48.5118 | 35.8865 | 121.8771 | 122.1708 | 122.0138 | -0.19162 | -0.044765 | -121.9739 | 0.042239 | 0.060253 | 0.10502 | -121.9158 | -121.7925 | -0.10922 | -0.16731 | 40.2983 | 35.9689 | 36.0781 | 0.12645 | -0.030601 | 0.15284 | 0.21097 | 0.33425 | 0.10212 | -122.1715 | 121.9595 | 122.2532 | 122.0962 | 48.5942 | -122.236
5124.5938 | 122.2092 | -0.11902 | 122.0856 | -0.010149 | -0.06229 | 0.037943 | 0.01434 | -0.015283 | -0.0082859 | -0.029148 | 0.054134 | 0.01758 | 0.078343 | 0.080858 | 0.1011 | -0.040158 | 0.015142 | -0.031301 | 0.084176 | 0.11483 | 0.25185 | -0.118 | 39.7946 | 48.3927 | 35.9689 | 121.8908 | 122.1662 | 122.0184 | -0.1962 | 0.001015 | -122.0014 | 0.078861 | 0.087718 | 0.086703 | -121.9707 | -121.8337 | -0.077181 | -0.19478 | 39.9136 | 36.088 | 36.1651 | 0.080672 | -0.06722 | 0.2032 | 0.23385 | 0.37087 | 0.13416 | -122.2036 | 122.0098 | 122.2853 | 122.1374 | 48.5118 | -122.2818
5126.3594 | 122.1725 | -0.12817 | 122.1176 | -0.0025182 | -0.06229 | 0.03837 | 0.014554 | -0.014642 | -0.0082859 | -0.021518 | 0.054347 | 0.018007 | 0.078984 | 0.081285 | 0.10153 | -0.03558 | 0.019721 | -0.022144 | 0.065863 | 0.13315 | 0.24269 | -0.118 | 40.4814 | 48.4614 | 36.7198 | 121.8816 | 122.1662 | 122.0184 | -0.19162 | 0.01017 | -122.0518 | 0.092594 | 0.10603 | 0.09586 | -121.9845 | -121.8749 | -0.063448 | -0.23598 | 40.6096 | 36.848 | 36.9115 | 0.048628 | -0.099264 | 0.19404 | 0.26132 | 0.37087 | 0.14789 | -122.2356 | 122.0098 | 122.2944 | 122.1465 | 48.5896 | -122.3092
5128.0625 | 122.2916 | -0.068665 | 122.0673 | -0.025411 | -0.062504 | 0.038157 | 0.014127 | -0.014642 | -0.0080721 | -0.029148 | 0.054775 | 0.018434 | 0.080052 | 0.081713 | 0.10196 | -0.044736 | 0.015142 | -0.031301 | 0.079598 | 0.11941 | 0.24269 | -0.118 | 40.2754 | 48.6995 | 37.4341 | 121.8771 | 122.1662 | 122.0184 | -0.18246 | -0.049339 | -121.9877 | 0.023929 | 0.037364 | 0.086703 | -121.9479 | -121.8246 | -0.1138 | -0.1902 | 40.344 | 37.5028 | 37.6166 | 0.098982 | -0.04891 | 0.14826 | 0.18808 | 0.31136 | 0.083807 | -122.1853 | 121.9457 | 122.2349 | 122.087 | 48.7682 | -122.2497
5129.7812 | 122.168 | -0.11444 | 122.0856 | -0.010149 | -0.062504 | 0.037943 | 0.014554 | -0.01507 | -0.0082859 | -0.029148 | 0.054561 | 0.019716 | 0.080052 | 0.081713 | 0.10302 | -0.03558 | 0.015142 | -0.022144 | 0.07502 | 0.11941 | 0.24269 | -0.118 | 41.2369 | 48.5209 | 37.3792 | 121.8771 | 122.1662 | 122.0184 | -0.1962 | -0.003563 | -122.0106 | 0.078861 | 0.092297 | 0.09586 | -121.9662 | -121.8429 | -0.081759 | -0.20851 | 41.3513 | 37.4936 | 37.5754 | 0.080672 | -0.06722 | 0.18946 | 0.23385 | 0.35714 | 0.12958 | -122.2036 | 121.9915 | 122.2807 | 122.1328 | 48.6354 | -122.2818
5131.5469 | 122.1817 | -0.10986 | 122.0901 | -0.01778 | -0.06229 | 0.037516 | 0.014554 | -0.01507 | -0.0076449 | -0.036779 | 0.055416 | 0.01993 | 0.080265 | 0.081926 | 0.10388 | -0.03558 | 0.010564 | -0.022144 | 0.079598 | 0.12399 | 0.25185 | -0.118 | 40.0831 | 48.2691 | 37.544 | 121.8816 | 122.1662 | 122.0092 | -0.1962 | -0.008141 | -122.0106 | 0.074283 | 0.087719 | 0.09586 | -121.9662 | -121.8383 | -0.086337 | -0.20851 | 40.1929 | 37.6539 | 37.7402 | 0.076094 | -0.080956 | 0.18946 | 0.23385 | 0.36172 | 0.12043 | -122.2082 | 121.9915 | 122.2761 | 122.1191 | 48.379 | -122.2863
5133.3281 | 122.1863 | -0.1236 | 122.113 | -0.0025182 | -0.062504 | 0.037943 | 0.014554 | -0.014856 | -0.0082859 | -0.021518 | 0.055843 | 0.019289 | 0.080265 | 0.082354 | 0.10452 | -0.031001 | 0.0243 | -0.017566 | 0.079598 | 0.12399 | 0.25185 | -0.12716 | 37.3908 | 48.4294 | 37.5669 | 121.8771 | 122.1662 | 122.0184 | -0.1962 | -0.003566 | -122.0334 | 0.092595 | 0.10603 | 0.1096 | -121.989 | -121.8612 | -0.072604 | -0.23598 | 37.5144 | 37.6905 | 37.7631 | 0.053206 | -0.094686 | 0.20319 | 0.24759 | 0.37545 | 0.1479 | -122.2402 | 122.0007 | 122.2898 | 122.1419 | 48.553 | -122.3092
5135.1094 | 122.3053 | -0.082397 | 122.081 | -0.010149 | -0.062076 | 0.037729 | 0.01434 | -0.014856 | -0.0076449 | -0.013887 | 0.055843 | 0.019503 | 0.08112 | 0.082354 | 0.10388 | -0.040158 | 0.015142 | -0.026723 | 0.07502 | 0.12399 | 0.24727 | -0.118 | 38.6362 | 48.118 | 38.2308 | 121.8771 | 122.1617 | 122.0138 | -0.1962 | -0.035607 | -122.006 | 0.042239 | 0.055674 | 0.091281 | -121.957 | -121.8337 | -0.1138 | -0.20394 | 38.7186 | 38.3132 | 38.427 | 0.08067 | -0.067222 | 0.15742 | 0.20639 | 0.32967 | 0.097539 | -122.199 | 121.9595 | 122.2441 | 122.0962 | 48.2004 | -122.2772
5136.8281 | 122.287 | -0.064087 | 122.0627 | -0.01778 | -0.061863 | 0.037943 | 0.014127 | -0.01507 | -0.0078585 | -0.021518 | 0.05627 | 0.01993 | 0.081334 | 0.082781 | 0.10495 | -0.031001 | 0.015142 | -0.026723 | 0.079598 | 0.13315 | 0.23812 | -0.118 | 38.2745 | 48.3515 | 38.4552 | 121.8816 | 122.1525 | 122.0138 | -0.19162 | -0.053917 | -121.9831 | 0.033086 | 0.037364 | 0.091281 | -121.9295 | -121.8246 | -0.12753 | -0.18105 | 38.3386 | 38.5193 | 38.6468 | 0.089824 | -0.048911 | 0.14369 | 0.19723 | 0.3022 | 0.079229 | -122.1807 | 121.9457 | 122.2166 | 122.0779 | 48.4156 | -122.2543
5138.5938 | 122.3007 | -0.050354 | 122.0627 | -0.025411 | -0.06229 | 0.038157 | 0.014554 | -0.015283 | -0.0074311 | -0.029148 | 0.05627 | 0.020357 | 0.083043 | 0.084277 | 0.10537 | -0.040158 | 0.015142 | -0.022144 | 0.070441 | 0.12857 | 0.24727 | -0.118 | 38.8972 | 48.8735 | 40.0486 | 121.8679 | 122.1617 | 122.0092 | -0.1962 | -0.06765 | -121.9922 | 0.010196 | 0.02821 | 0.09586 | -121.9341 | -121.8154 | -0.14585 | -0.19478 | 38.9475 | 40.0989 | 40.2448 | 0.098981 | -0.05349 | 0.1208 | 0.17892 | 0.29763 | 0.065496 | -122.1807 | 121.9183 | 122.212 | 122.0595 | 48.9239 | -122.2589
5140.3594 | 122.2824 | -0.086975 | 122.0581 | -0.010149 | -0.06229 | 0.037729 | 0.014554 | -0.01507 | -0.0070039 | -0.021518 | 0.057125 | 0.021426 | 0.082829 | 0.084063 | 0.10687 | -0.03558 | 0.0243 | -0.022144 | 0.079598 | 0.12857 | 0.25185 | -0.118 | 38.5721 | 48.6904 | 39.9204 | 121.8725 | 122.1571 | 122.0092 | -0.1962 | -0.031029 | -121.9785 | 0.051395 | 0.064831 | 0.09586 | -121.9295 | -121.8063 | -0.10923 | -0.18563 | 38.6591 | 40.0073 | 40.1166 | 0.098981 | -0.048912 | 0.16657 | 0.21554 | 0.33883 | 0.11127 | -122.1761 | 121.9595 | 122.2441 | 122.0962 | 48.7773 | -122.2543
5142.0625 | 122.2824 | -0.073242 | 122.0673 | -0.01778 | -0.062076 | 0.03837 | 0.014768 | -0.014856 | -0.0072175 | -0.021518 | 0.057552 | 0.020998 | 0.082829 | 0.084063 | 0.10708 | -0.031001 | 0.019721 | -0.026723 | 0.07502 | 0.12857 | 0.24269 | -0.11342 | 37.4274 | 48.7316 | 40.1218 | 121.8771 | 122.1571 | 122.0138 | -0.20078 | -0.040183 | -121.9922 | 0.042241 | 0.046519 | 0.086702 | -121.9387 | -121.8246 | -0.12754 | -0.1902 | 37.5007 | 40.1951 | 40.3226 | 0.089825 | -0.053489 | 0.14826 | 0.20181 | 0.31594 | 0.092963 | -122.1807 | 121.9503 | 122.2303 | 122.087 | 48.8048 | -122.268
5143.8281 | 122.168 | -0.11444 | 122.1039 | -0.010149 | -0.06229 | 0.038157 | 0.01434 | -0.015497 | -0.0074311 | -0.021518 | 0.058193 | 0.020785 | 0.083257 | 0.084277 | 0.1073 | -0.03558 | 0.015142 | -0.031301 | 0.084176 | 0.12857 | 0.24269 | -0.11342 | 37.6472 | 48.4385 | 40.5202 | 121.8771 | 122.1571 | 122.0046 | -0.18704 | 0.001016 | -122.0197 | 0.078861 | 0.08314 | 0.082124 | -121.9753 | -121.8612 | -0.072602 | -0.22682 | 37.7616 | 40.6346 | 40.7072 | 0.053204 | -0.099267 | 0.19862 | 0.24301 | 0.35714 | 0.12958 | -122.2173 | 121.9915 | 122.2715 | 122.1191 | 48.553 | -122.2909
5145.6094 | 122.2092 | -0.12817 | 122.1268 | -0.010149 | -0.062504 | 0.03837 | 0.01434 | -0.01507 | -0.0072175 | -0.021518 | 0.058193 | 0.021212 | 0.083043 | 0.084491 | 0.10751 | -0.03558 | 0.015142 | -0.026723 | 0.084176 | 0.12857 | 0.24269 | -0.12258 | 38.2699 | 48.4202 | 40.4973 | 121.8771 | 122.1617 | 122.0138 | -0.19162 | 0.005591 | -122.0426 | 0.092594 | 0.10145 | 0.09586 | -121.9982 | -121.8841 | -0.063448 | -0.24971 | 38.3981 | 40.6255 | 40.6889 | 0.034894 | -0.113 | 0.21235 | 0.25674 | 0.37087 | 0.14332 | -122.2494 | 122.0052 | 122.2898 | 122.1419 | 48.5484 | -122.3184
5147.3281 | 122.2733 | -0.091553 | 122.0718 | -0.0025182 | -0.062076 | 0.038157 | 0.014127 | -0.015283 | -0.0074311 | -0.021518 | 0.05862 | 0.022708 | 0.083043 | 0.084704 | 0.10943 | -0.03558 | 0.005985 | -0.026723 | 0.079598 | 0.12399 | 0.25185 | -0.118 | 40.0007 | 48.4111 | 40.6621 | 121.8725 | 122.1662 | 122.0046 | -0.19162 | -0.026451 | -121.9922 | 0.055973 | 0.06483 | 0.091281 | -121.9478 | -121.82 | -0.10007 | -0.19936 | 40.0922 | 40.7537 | 40.8537 | 0.094405 | -0.067223 | 0.17115 | 0.21554 | 0.34341 | 0.097538 | -122.1898 | 121.964 | 122.2578 | 122.0962 | 48.5026 | -122.2635
5149.0938 | 122.2458 | -0.082397 | 122.0764 | -0.01778 | -0.062504 | 0.038157 | 0.014127 | -0.015283 | -0.0070039 | -0.036779 | 0.059902 | 0.022067 | 0.083257 | 0.084704 | 0.10901 | -0.031001 | 0.0243 | -0.026723 | 0.079598 | 0.12857 | 0.25185 | -0.12258 | 37.8212 | 48.2966 | 40.8636 | 121.8679 | 122.1571 | 122.0092 | -0.1962 | -0.040186 | -121.9968 | 0.051396 | 0.055674 | 0.09586 | -121.9478 | -121.8246 | -0.1138 | -0.20851 | 37.9036 | 40.946 | 41.0598 | 0.08067 | -0.067223 | 0.162 | 0.21097 | 0.33425 | 0.1067 | -122.199 | 121.9503 | 122.2395 | 122.0916 | 48.379 | -122.2726
5150.8594 | 122.2183 | -0.10529 | 122.1039 | -0.01778 | -0.062076 | 0.037943 | 0.01434 | -0.01507 | -0.0072175 | -0.013887 | 0.060116 | 0.021639 | 0.084111 | 0.084918 | 0.10943 | -0.03558 | 0.019721 | -0.017566 | 0.070441 | 0.12857 | 0.25643 | -0.118 | 38.2699 | 48.0768 | 41.3718 | 121.8725 | 122.1617 | 122.0046 | -0.19162 | -0.012718 | -122.0334 | 0.069706 | 0.08772 | 0.10044 | -121.9753 | -121.8475 | -0.086336 | -0.2314 | 38.3752 | 41.4771 | 41.5634 | 0.057782 | -0.099267 | 0.17573 | 0.23385 | 0.36172 | 0.12501 | -122.2219 | 121.9778 | 122.267 | 122.1099 | 48.1821 | -122.2955
5152.6406 | 122.2504 | -0.086975 | 122.0627 | -0.01778 | -0.06229 | 0.037943 | 0.014554 | -0.014856 | -0.0070039 | -0.029148 | 0.059902 | 0.02463 | 0.084325 | 0.085345 | 0.112 | -0.031001 | 0.019721 | -0.022144 | 0.084176 | 0.12857 | 0.25185 | -0.12258 | 39.8038 | 48.1821 | 42.0495 | 121.8679 | 122.1571 | 122 | -0.19162 | -0.035608 | -121.9785 | 0.055974 | 0.064831 | 0.10044 | -121.9341 | -121.8108 | -0.10465 | -0.19478 | 39.8907 | 42.1364 | 42.2411 | 0.094403 | -0.062647 | 0.17115 | 0.21554 | 0.33883 | 0.1067 | -122.1853 | 121.9549 | 122.2441 | 122.087 | 48.2691 | -122.2543
5154.4219 | 122.3053 | -0.07782 | 122.0581 | -0.010149 | -0.06229 | 0.037729 | 0.014554 | -0.014856 | -0.0065765 | -0.013887 | 0.061184 | 0.024844 | 0.084752 | 0.0862 | 0.11307 | -0.026423 | 0.005985 | -0.026723 | 0.088755 | 0.12399 | 0.25185 | -0.12258 | 38.073 | 48.0722 | 42.544 | 121.8633 | 122.1571 | 122 | -0.20078 | -0.044763 | -121.9693 | 0.051397 | 0.051097 | 0.09586 | -121.9341 | -121.8063 | -0.12296 | -0.19478 | 38.1508 | 42.6218 | 42.7447 | 0.098981 | -0.058069 | 0.16658 | 0.20181 | 0.32967 | 0.083805 | -122.1807 | 121.9411 | 122.2349 | 122.0779 | 48.1501 | -122.2589
5156.125 | 122.2641 | -0.073242 | 122.0673 | -0.01778 | -0.062076 | 0.037943 | 0.01434 | -0.015283 | -0.0067901 | -0.021518 | 0.060757 | 0.025271 | 0.085179 | 0.085773 | 0.11307 | -0.044736 | 0.010564 | -0.022144 | 0.07502 | 0.12857 | 0.25185 | -0.118 | 39.671 | 47.7884 | 42.6172 | 121.8633 | 122.1525 | 122 | -0.18704 | -0.044762 | -121.9922 | 0.028506 | 0.051098 | 0.09586 | -121.9387 | -121.8154 | -0.1138 | -0.20394 | 39.7442 | 42.6905 | 42.8043 | 0.085246 | -0.067225 | 0.14826 | 0.20181 | 0.32509 | 0.083806 | -122.1853 | 121.9366 | 122.2257 | 122.0733 | 47.8616 | -122.2543
5157.8906 | 122.1588 | -0.12817 | 122.1085 | -0.010149 | -0.062504 | 0.037729 | 0.01434 | -0.015283 | -0.0061491 | -0.013887 | 0.060757 | 0.025485 | 0.084752 | 0.085986 | 0.11307 | -0.03558 | 0.005985 | -0.022144 | 0.079598 | 0.12857 | 0.24269 | -0.12716 | 41.8688 | 47.9715 | 42.4112 | 121.8633 | 122.1525 | 122 | -0.18704 | 0.001012 | -122.0289 | 0.092594 | 0.10603 | 0.10502 | -121.9799 | -121.8658 | -0.058869 | -0.24514 | 41.9969 | 42.5394 | 42.5982 | 0.044048 | -0.10842 | 0.20777 | 0.25674 | 0.37087 | 0.13416 | -122.2356 | 121.9915 | 122.2807 | 122.1282 | 48.0997 | -122.2955
5159.6562 | 122.2824 | -0.064087 | 122.0398 | -0.010149 | -0.062504 | 0.038157 | 0.01434 | -0.015283 | -0.0067901 | -0.021518 | 0.061184 | 0.025912 | 0.084325 | 0.085773 | 0.11371 | -0.03558 | 0.019721 | -0.022144 | 0.084176 | 0.12857 | 0.24727 | -0.118 | 42.4823 | 47.9761 | 42.3974 | 121.8633 | 122.1571 | 121.9955 | -0.1962 | -0.053917 | -121.9556 | 0.028507 | 0.041943 | 0.09586 | -121.9112 | -121.7925 | -0.13211 | -0.17647 | 42.5464 | 42.4615 | 42.5936 | 0.11729 | -0.044337 | 0.14826 | 0.19266 | 0.31136 | 0.083808 | -122.1578 | 121.9274 | 122.2212 | 122.0595 | 48.0402 | -122.236
5161.4219 | 122.3053 | -0.054932 | 122.0398 | -0.010149 | -0.062076 | 0.037943 | 0.014554 | -0.014856 | -0.0063629 | -0.013887 | 0.061397 | 0.026126 | 0.085393 | 0.086627 | 0.11349 | -0.040158 | 0.015142 | -0.026723 | 0.079598 | 0.12857 | 0.24727 | -0.118 | 43.8285 | 47.738 | 43.6016 | 121.8633 | 122.1525 | 121.9955 | -0.18246 | -0.063072 | -121.9602 | 0.014774 | 0.028209 | 0.091281 | -121.9112 | -121.7925 | -0.12753 | -0.17647 | 43.8834 | 43.6566 | 43.7841 | 0.11271 | -0.044337 | 0.13453 | 0.1835 | 0.30221 | 0.070074 | -122.1578 | 121.9183 | 122.2074 | 122.0504 | 47.7929 | -122.2223
5163.125 | 122.2366 | -0.086975 | 122.0627 | -0.01778 | -0.062076 | 0.037943 | 0.01434 | -0.014856 | -0.0061491 | -0.021518 | 0.061611 | 0.026767 | 0.08582 | 0.087268 | 0.11413 | -0.03558 | 0.010564 | -0.026723 | 0.084176 | 0.11941 | 0.24727 | -0.11342 | 45.138 | 47.2939 | 44.2381 | 121.8587 | 122.1571 | 121.9909 | -0.19162 | -0.02645 | -121.9785 | 0.051395 | 0.060252 | 0.086702 | -121.9433 | -121.8154 | -0.10465 | -0.20394 | 45.2249 | 44.3251 | 44.4297 | 0.094403 | -0.071804 | 0.17115 | 0.20639 | 0.33425 | 0.097539 | -122.1761 | 121.9457 | 122.2441 | 122.0779 | 47.3808 | -122.2543
5164.8906 | 122.2595 | -0.064087 | 122.0535 | -0.01778 | -0.062076 | 0.037943 | 0.014127 | -0.01507 | -0.0059355 | -0.0062567 | 0.060757 | 0.027622 | 0.089025 | 0.088978 | 0.11499 | -0.040158 | 0.010564 | -0.022144 | 0.084176 | 0.12399 | 0.24727 | -0.118 | 46.2094 | 48.3973 | 46.6602 | 121.8587 | 122.1479 | 121.9955 | -0.18704 | -0.053917 | -121.9694 | 0.023929 | 0.041943 | 0.09586 | -121.9295 | -121.8063 | -0.12296 | -0.19478 | 46.2735 | 46.7243 | 46.8473 | 0.094401 | -0.05807 | 0.14826 | 0.18808 | 0.31136 | 0.074651 | -122.1715 | 121.9228 | 122.212 | 122.0595 | 48.4614 | -122.2406
5166.6562 | 122.3007 | -0.073242 | 122.0535 | -0.01778 | -0.06229 | 0.037729 | 0.01434 | -0.01507 | -0.0059355 | -0.029148 | 0.061825 | 0.028263 | 0.088384 | 0.088764 | 0.11606 | -0.031001 | 0.015142 | -0.031301 | 0.079598 | 0.12399 | 0.24727 | -0.118 | 45.4676 | 48.0722 | 45.9734 | 121.8633 | 122.1525 | 121.9955 | -0.19162 | -0.044762 | -121.9739 | 0.042241 | 0.041941 | 0.086703 | -121.9295 | -121.8063 | -0.11838 | -0.19021 | 45.5409 | 46.0467 | 46.165 | 0.098979 | -0.05807 | 0.15284 | 0.19723 | 0.32052 | 0.088384 | -122.1715 | 121.9366 | 122.2257 | 122.0687 | 48.1455 | -122.2451
5168.4219 | 122.2961 | -0.07782 | 122.0444 | -0.025411 | -0.062717 | 0.037943 | 0.01434 | -0.01507 | -0.0057219 | -0.021518 | 0.062038 | 0.027835 | 0.087743 | 0.087696 | 0.11606 | -0.03558 | 0.010564 | -0.026723 | 0.084176 | 0.12857 | 0.25185 | -0.12716 | 45.692 | 48.4294 | 45.0806 | 121.8496 | 122.1433 | 121.9863 | -0.1962 | -0.049342 | -121.9602 | 0.04224 | 0.051097 | 0.10044 | -121.9158 | -121.7925 | -0.11838 | -0.19478 | 45.7698 | 45.1584 | 45.2768 | 0.098977 | -0.058073 | 0.162 | 0.20639 | 0.32967 | 0.088384 | -122.1715 | 121.9274 | 122.2212 | 122.0641 | 48.5072 | -122.2406
5170.1406 | 122.1863 | -0.10986 | 122.0718 | -0.010149 | -0.06229 | 0.03837 | 0.014554 | -0.01507 | -0.0059355 | -0.021518 | 0.062466 | 0.030827 | 0.08817 | 0.087909 | 0.11883 | -0.026423 | 0.010564 | -0.017566 | 0.07502 | 0.12399 | 0.24727 | -0.12258 | 46.8229 | 48.4431 | 45.4194 | 121.8542 | 122.1433 | 121.9863 | -0.1962 | -0.01272 | -121.9968 | 0.08344 | 0.092297 | 0.10502 | -121.9478 | -121.8246 | -0.086337 | -0.21767 | 46.9328 | 45.5293 | 45.6156 | 0.071512 | -0.085538 | 0.18488 | 0.23385 | 0.35714 | 0.12043 | -122.1944 | 121.964 | 122.2532 | 122.0962 | 48.553 | -122.268
5171.9219 | 122.2687 | -0.064087 | 122.0627 | -0.01778 | -0.06229 | 0.03837 | 0.014554 | -0.01507 | -0.0055083 | -0.013887 | 0.062252 | 0.031681 | 0.088598 | 0.088337 | 0.11947 | -0.021844 | 0.019721 | -0.022144 | 0.084176 | 0.13315 | 0.25185 | -0.11342 | 47.6517 | 48.5209 | 45.9322 | 121.8587 | 122.1433 | 121.9909 | -0.18704 | -0.049338 | -121.9785 | 0.042243 | 0.041943 | 0.091281 | -121.9295 | -121.8108 | -0.12296 | -0.20394 | 47.7158 | 45.9963 | 46.1193 | 0.080667 | -0.071804 | 0.14826 | 0.19723 | 0.31594 | 0.083808 | -122.1761 | 121.9228 | 122.2074 | 122.055 | 48.585 | -122.2497
5173.6875 | 122.2504 | -0.059509 | 122.0535 | -0.025411 | -0.062504 | 0.03837 | 0.014554 | -0.015283 | -0.0057219 | -0.021518 | 0.061611 | 0.032536 | 0.092443 | 0.090901 | 0.12097 | -0.031001 | 0.015142 | -0.017566 | 0.084176 | 0.13315 | 0.25643 | -0.118 | 49.0345 | 49.6656 | 48.9175 | 121.8633 | 122.1433 | 121.9909 | -0.18704 | -0.058495 | -121.9694 | 0.028508 | 0.041943 | 0.10044 | -121.9204 | -121.7971 | -0.12753 | -0.19021 | 49.094 | 48.977 | 49.1046 | 0.089822 | -0.062649 | 0.14369 | 0.19266 | 0.31594 | 0.074651 | -122.1715 | 121.9228 | 122.2029 | 122.0504 | 49.7251 | -122.2406
5175.4531 | 122.1451 | -0.10529 | 122.081 | -0.01778 | -0.06229 | 0.038157 | 0.01434 | -0.015283 | -0.0050809 | -0.013887 | 0.062252 | 0.03104 | 0.092443 | 0.090687 | 0.1199 | -0.031001 | 0.019721 | -0.008409 | 0.093333 | 0.14231 | 0.24727 | -0.11342 | 48.9337 | 49.7984 | 49.0961 | 121.8633 | 122.1388 | 121.9909 | -0.18704 | -0.008139 | -121.9877 | 0.074285 | 0.096877 | 0.10502 | -121.9387 | -121.8337 | -0.081757 | -0.21767 | 49.039 | 49.2014 | 49.2831 | 0.057777 | -0.090115 | 0.19862 | 0.24759 | 0.35256 | 0.12501 | -122.1944 | 121.9686 | 122.2441 | 122.0962 | 49.9037 | -122.268
5177.1562 | 122.2275 | -0.07782 | 122.0627 | -0.01778 | -0.062504 | 0.037943 | 0.014554 | -0.015283 | -0.0052945 | -0.021518 | 0.067166 | 0.032322 | 0.085179 | 0.089191 | 0.12076 | -0.031001 | 0.019721 | -0.017566 | 0.084176 | 0.13773 | 0.24269 | -0.118 | 49.3046 | 48.2462 | 46.5641 | 121.8542 | 122.1433 | 121.9955 | -0.18246 | -0.040184 | -121.9785 | 0.046819 | 0.060254 | 0.10044 | -121.925 | -121.82 | -0.10464 | -0.20852 | 49.3824 | 46.6419 | 46.7465 | 0.080667 | -0.067225 | 0.162 | 0.21555 | 0.32051 | 0.097541 | -122.1807 | 121.932 | 122.2212 | 122.0733 | 48.324 | -122.2451
5178.9219 | 122.1817 | -0.09613 | 122.0535 | -0.0025182 | -0.062076 | 0.037943 | 0.014554 | -0.015283 | -0.0067901 | -0.0062567 | 0.069943 | 0.032963 | 0.083684 | 0.089405 | 0.12161 | -0.026423 | 0.0243 | -0.012988 | 0.088755 | 0.13315 | 0.26101 | -0.10885 | 48.8147 | 48.2554 | 46.9121 | 121.8542 | 122.1433 | 121.9863 | -0.18704 | -0.012717 | -121.9648 | 0.069707 | 0.083142 | 0.095859 | -121.9204 | -121.7925 | -0.090913 | -0.19936 | 48.9108 | 47.0082 | 47.0991 | 0.089822 | -0.067228 | 0.18488 | 0.22928 | 0.35714 | 0.12043 | -122.1624 | 121.9503 | 122.2395 | 122.0824 | 48.3515 | -122.2406
5180.7031 | 122.2458 | -0.064087 | 122.0581 | -0.0025182 | -0.062717 | 0.038157 | 0.014127 | -0.015283 | -0.0065765 | -0.013887 | 0.071225 | 0.034031 | 0.082402 | 0.089191 | 0.12247 | -0.026423 | 0.019721 | -0.012988 | 0.088755 | 0.13773 | 0.25643 | -0.11342 | 50.8888 | 48.3653 | 47.1593 | 121.8496 | 122.1388 | 121.9863 | -0.18246 | -0.049338 | -121.9693 | 0.037664 | 0.051099 | 0.10044 | -121.9204 | -121.8017 | -0.11838 | -0.20852 | 50.9529 | 47.2234 | 47.3418 | 0.080666 | -0.071805 | 0.15284 | 0.20181 | 0.32052 | 0.083808 | -122.1715 | 121.9137 | 122.2029 | 122.0504 | 48.4294 | -122.2406
5182.4219 | 122.2961 | -0.064087 | 122.0261 | -0.01778 | -0.062504 | 0.037729 | 0.014554 | -0.015283 | -0.0067901 | -0.013887 | 0.072934 | 0.035741 | 0.081334 | 0.089619 | 0.12418 | -0.021844 | 0.019721 | -0.017566 | 0.088755 | 0.14231 | 0.25643 | -0.11342 | 53.1507 | 48.5713 | 47.576 | 121.8496 | 122.125 | 121.9817 | -0.17788 | -0.049338 | -121.9373 | 0.042243 | 0.046521 | 0.095859 | -121.8838 | -121.7696 | -0.1138 | -0.17647 | 53.2148 | 47.6401 | 47.7539 | 0.098974 | -0.04434 | 0.15284 | 0.20639 | 0.32052 | 0.083808 | -122.1395 | 121.9137 | 122.1891 | 122.0458 | 48.6354 | -122.2039
5184.1875 | 122.1725 | -0.09613 | 122.0627 | -0.01778 | -0.06229 | 0.037943 | 0.01434 | -0.015497 | -0.0065765 | -0.013887 | 0.074216 | 0.034672 | 0.079838 | 0.088978 | 0.12311 | -0.026423 | 0.0243 | -0.012988 | 0.088755 | 0.13773 | 0.25643 | -0.12258 | 52.7386 | 47.7288 | 46.9395 | 121.8404 | 122.1342 | 121.9771 | -0.18246 | -0.026453 | -121.9739 | 0.069707 | 0.083142 | 0.10959 | -121.925 | -121.8063 | -0.086334 | -0.22225 | 52.8348 | 47.0357 | 47.122 | 0.07151 | -0.08554 | 0.18488 | 0.23386 | 0.35256 | 0.12043 | -122.1853 | 121.9366 | 122.2303 | 122.0733 | 47.825 | -122.2451
5185.9531 | 122.1451 | -0.13733 | 122.0444 | -0.010149 | -0.062717 | 0.038157 | 0.014127 | -0.015497 | -0.0063629 | -0.021518 | 0.075284 | 0.035313 | 0.079411 | 0.089191 | 0.12375 | -0.021844 | 0.0243 | -0.017566 | 0.088755 | 0.13773 | 0.25643 | -0.118 | 53.343 | 48.0081 | 46.9121 | 121.845 | 122.125 | 121.9726 | -0.18246 | 0.019325 | -121.9556 | 0.11549 | 0.11976 | 0.10044 | -121.9066 | -121.7879 | -0.045135 | -0.19936 | 53.4803 | 47.0494 | 47.0945 | 0.080663 | -0.071808 | 0.22608 | 0.27506 | 0.39376 | 0.16163 | -122.1624 | 121.9823 | 122.2624 | 122.1099 | 48.1455 | -122.2268
5187.7188 | 122.1542 | -0.09613 | 122.0306 | -0.01778 | -0.062931 | 0.038157 | 0.01434 | -0.014856 | -0.0061491 | -0.029148 | 0.075498 | 0.036595 | 0.078984 | 0.089619 | 0.12524 | -0.021844 | 0.019721 | -0.012988 | 0.088755 | 0.14231 | 0.26101 | -0.118 | 54.8219 | 48.1134 | 46.9945 | 121.8404 | 122.1296 | 121.9726 | -0.18704 | -0.021874 | -121.9419 | 0.074286 | 0.083142 | 0.10502 | -121.8883 | -121.7696 | -0.090913 | -0.19021 | 54.9181 | 47.0906 | 47.1815 | 0.098974 | -0.058075 | 0.18488 | 0.23844 | 0.35714 | 0.11585 | -122.1486 | 121.9366 | 122.2257 | 122.0687 | 48.2096 | -122.2177
5189.4219 | 122.1222 | -0.13275 | 122.0535 | -0.010149 | -0.062504 | 0.037943 | 0.014127 | -0.015283 | -0.0063629 | -0.021518 | 0.076566 | 0.037023 | 0.07877 | 0.089832 | 0.12503 | -0.026423 | 0.0243 | -0.012988 | 0.088755 | 0.13773 | 0.24727 | -0.118 | 54.8769 | 48.3973 | 47.3562 | 121.8404 | 122.1205 | 121.9634 | -0.18246 | 0.014747 | -121.9648 | 0.10633 | 0.11976 | 0.10502 | -121.9158 | -121.8063 | -0.049713 | -0.2131 | 55.0096 | 47.4889 | 47.5387 | 0.066929 | -0.090121 | 0.22151 | 0.27048 | 0.38003 | 0.15705 | -122.1715 | 121.9732 | 122.2532 | 122.0962 | 48.5301 | -122.236
5191.2031 | 122.2366 | -0.054932 | 122.0169 | -0.010149 | -0.062717 | 0.037729 | 0.014554 | -0.015283 | -0.0061491 | -0.036779 | 0.076779 | 0.037877 | 0.07877 | 0.089832 | 0.12588 | -0.021844 | 0.019721 | -0.022144 | 0.088755 | 0.13773 | 0.26559 | -0.11342 | 55.8567 | 48.6171 | 47.8736 | 121.8359 | 122.1159 | 121.9634 | -0.18246 | -0.058493 | -121.9282 | 0.033088 | 0.032788 | 0.091281 | -121.8792 | -121.7513 | -0.12753 | -0.18106 | 55.9117 | 47.9285 | 48.056 | 0.098971 | -0.0535 | 0.14369 | 0.19266 | 0.32052 | 0.074653 | -122.1303 | 121.8908 | 122.1708 | 122.0183 | 48.672 | -122.1994
5192.9688 | 122.1313 | -0.1236 | 122.0444 | -0.010149 | -0.062504 | 0.037943 | 0.01434 | -0.01507 | -0.0061491 | -0.021518 | 0.077848 | 0.037023 | 0.079197 | 0.090687 | 0.12567 | -0.031001 | 0.019721 | -0.017566 | 0.084176 | 0.13773 | 0.25643 | -0.10885 | 56.452 | 49.0887 | 48.6703 | 121.8267 | 122.125 | 121.9634 | -0.17788 | 0.014749 | -121.9602 | 0.092595 | 0.10603 | 0.091281 | -121.9066 | -121.7879 | -0.054289 | -0.21768 | 56.5756 | 48.7939 | 48.8482 | 0.080663 | -0.080966 | 0.20777 | 0.26132 | 0.38003 | 0.14332 | -122.1532 | 121.9503 | 122.2486 | 122.087 | 49.2123 | -122.2223
5194.7344 | 122.2641 | -0.068665 | 122.0078 | -0.01778 | -0.062504 | 0.037943 | 0.014554 | -0.01507 | -0.0061491 | -0.021518 | 0.078916 | 0.035741 | 0.080052 | 0.091114 | 0.12524 | -0.031001 | 0.0243 | -0.022144 | 0.097912 | 0.13315 | 0.25185 | -0.10885 | 55.6873 | 49.4779 | 49.3296 | 121.8359 | 122.1205 | 121.9588 | -0.18704 | -0.040182 | -121.9098 | 0.037664 | 0.046521 | 0.086703 | -121.8746 | -121.7559 | -0.11838 | -0.1719 | 55.756 | 49.3983 | 49.5167 | 0.11271 | -0.048922 | 0.16658 | 0.20181 | 0.32052 | 0.092965 | -122.1166 | 121.9045 | 122.1891 | 122.0275 | 49.5466 | -122.1948
5196.4531 | 122.1405 | -0.10986 | 122.0535 | -0.01778 | -0.062931 | 0.037943 | 0.014768 | -0.01507 | -0.0055083 | -0.029148 | 0.07977 | 0.037236 | 0.079625 | 0.091542 | 0.12653 | -0.026423 | 0.019721 | -0.012988 | 0.093333 | 0.13315 | 0.25643 | -0.11342 | 56.452 | 49.7389 | 49.7875 | 121.8267 | 122.1205 | 121.9543 | -0.18246 | -0.003562 | -121.9602 | 0.08344 | 0.096875 | 0.10044 | -121.9204 | -121.7971 | -0.072601 | -0.22683 | 56.5618 | 49.8973 | 49.9699 | 0.066929 | -0.099278 | 0.2032 | 0.24301 | 0.36629 | 0.12958 | -122.167 | 121.9366 | 122.2303 | 122.0641 | 49.8487 | -122.236
5198.2188 | 122.1909 | -0.082397 | 122.0215 | -0.0025182 | -0.062504 | 0.037943 | 0.01434 | -0.015283 | -0.0057219 | -0.029148 | 0.080625 | 0.036168 | 0.080052 | 0.091542 | 0.12653 | -0.021844 | 0.015142 | -0.017566 | 0.088755 | 0.13773 | 0.26101 | -0.11342 | 55.1562 | 49.9541 | 50.1721 | 121.8313 | 122.1113 | 121.9543 | -0.17788 | -0.031028 | -121.9327 | 0.060553 | 0.064831 | 0.095859 | -121.8838 | -121.7605 | -0.095488 | -0.19021 | 55.2386 | 50.2545 | 50.35 | 0.089816 | -0.067234 | 0.17115 | 0.22012 | 0.34341 | 0.097539 | -122.1349 | 121.9137 | 122.1937 | 122.0366 | 50.0365 | -122.1994
5199.9844 | 122.2504 | -0.045776 | 122.0306 | -0.01778 | -0.062717 | 0.037943 | 0.014554 | -0.015283 | -0.0057219 | -0.021518 | 0.080839 | 0.034886 | 0.080052 | 0.091969 | 0.12567 | -0.021844 | 0.0243 | -0.017566 | 0.093333 | 0.13773 | 0.25643 | -0.10427 | 54.1122 | 50.6684 | 50.5842 | 121.8267 | 122.1113 | 121.9497 | -0.18246 | -0.058492 | -121.9373 | 0.023932 | 0.02821 | 0.086702 | -121.8929 | -121.7742 | -0.13669 | -0.20395 | 54.158 | 50.63 | 50.7666 | 0.08066 | -0.080968 | 0.13911 | 0.1835 | 0.30221 | 0.070076 | -122.1349 | 121.8725 | 122.1571 | 121.9954 | 50.7141 | -122.2131
5201.7031 | 122.2504 | -0.064087 | 121.9986 | -0.0025182 | -0.062717 | 0.037943 | 0.01434 | -0.015283 | -0.0059355 | -0.029148 | 0.08212 | 0.034459 | 0.080906 | 0.092824 | 0.12588 | -0.021844 | 0.019721 | -0.017566 | 0.088755 | 0.13773 | 0.26101 | -0.11342 | 53.7231 | 50.238 | 51.0741 | 121.8175 | 122.1067 | 121.9543 | -0.18246 | -0.049338 | -121.9098 | 0.042243 | 0.046521 | 0.095859 | -121.8609 | -121.7376 | -0.11838 | -0.18106 | 53.7871 | 51.1382 | 51.2566 | 0.10812 | -0.044346 | 0.15284 | 0.20181 | 0.3251 | 0.083808 | -122.112 | 121.8816 | 122.1708 | 122.0183 | 50.3021 | -122.1811
5203.4688 | 122.1451 | -0.10529 | 122.0627 | -0.025411 | -0.062504 | 0.037943 | 0.014554 | -0.015497 | -0.0055083 | -0.021518 | 0.080625 | 0.034886 | 0.079625 | 0.090473 | 0.12653 | -0.026423 | 0.0243 | -0.022144 | 0.088755 | 0.13773 | 0.26101 | -0.11342 | 54.3549 | 48.4752 | 47.9926 | 121.8267 | 122.1021 | 121.9497 | -0.17788 | -0.008139 | -121.9739 | 0.078863 | 0.083142 | 0.091281 | -121.925 | -121.8017 | -0.072599 | -0.23599 | 54.4602 | 48.0979 | 48.1705 | 0.03946 | -0.11301 | 0.19404 | 0.24301 | 0.3663 | 0.12959 | -122.1761 | 121.932 | 122.2074 | 122.055 | 48.5804 | -122.2406
5205.1719 | 122.2183 | -0.068665 | 122.0215 | -0.01778 | -0.062717 | 0.037729 | 0.014127 | -0.014856 | -0.0055083 | -0.029148 | 0.081693 | 0.0351 | 0.079838 | 0.090687 | 0.12653 | -0.026423 | 0.019721 | -0.012988 | 0.088755 | 0.13315 | 0.26101 | -0.11342 | 54.2633 | 48.4935 | 48.3315 | 121.8221 | 122.1159 | 121.9543 | -0.18704 | -0.04476 | -121.9327 | 0.042242 | 0.055677 | 0.10044 | -121.8883 | -121.7605 | -0.11838 | -0.19937 | 54.332 | 48.4001 | 48.5185 | 0.094394 | -0.067234 | 0.15742 | 0.20181 | 0.32968 | 0.088386 | -122.1349 | 121.8908 | 122.1845 | 122.0229 | 48.5621 | -122.2085
5206.9375 | 122.2504 | -0.045776 | 121.9986 | -0.01778 | -0.062504 | 0.038157 | 0.01434 | -0.015497 | -0.0050809 | -0.029148 | 0.080839 | 0.039159 | 0.079625 | 0.089832 | 0.12866 | -0.021844 | 0.0243 | -0.017566 | 0.088755 | 0.13773 | 0.25185 | -0.11342 | 56.5161 | 48.3882 | 48.4551 | 121.813 | 122.1021 | 121.9497 | -0.18246 | -0.067649 | -121.9098 | 0.023932 | 0.02821 | 0.095859 | -121.8609 | -121.7467 | -0.13669 | -0.18564 | 56.5618 | 48.5009 | 48.6375 | 0.10355 | -0.048924 | 0.13453 | 0.1835 | 0.29763 | 0.070076 | -122.112 | 121.8587 | 122.1479 | 121.9954 | 48.4339 | -122.1811
5208.7031 | 122.2412 | -0.064087 | 122.0261 | -0.01778 | -0.06229 | 0.037943 | 0.014554 | -0.014856 | -0.0050809 | -0.013887 | 0.078488 | 0.043432 | 0.077061 | 0.091114 | 0.12781 | -0.026423 | 0.019721 | -0.017566 | 0.093333 | 0.14231 | 0.26559 | -0.10885 | 55.5362 | 48.7087 | 48.8397 | 121.8084 | 122.1021 | 121.9497 | -0.18704 | -0.04476 | -121.9327 | 0.037664 | 0.046521 | 0.091281 | -121.8838 | -121.7605 | -0.12296 | -0.21768 | 55.6003 | 48.9038 | 49.0267 | 0.076081 | -0.07639 | 0.15742 | 0.20639 | 0.32967 | 0.083808 | -122.1349 | 121.8725 | 122.1662 | 122.0138 | 48.7728 | -122.2131
5210.5781 | 122.2 | -0.073242 | 121.9711 | -0.010149 | -0.062717 | 0.037943 | 0.014127 | -0.01507 | -0.0048673 | -0.021518 | 0.076138 | 0.047706 | 0.074497 | 0.090901 | 0.12674 | -0.026423 | 0.015142 | -0.008409 | 0.093333 | 0.13773 | 0.26559 | -0.12258 | 55.6003 | 48.553 | 48.8305 | 121.8175 | 122.1021 | 121.9405 | -0.18246 | -0.049341 | -121.8778 | 0.046819 | 0.064833 | 0.11417 | -121.8334 | -121.7055 | -0.10922 | -0.15359 | 55.6736 | 48.9038 | 49.013 | 0.13101 | -0.030616 | 0.16658 | 0.21097 | 0.33883 | 0.088384 | -122.0937 | 121.8908 | 122.1754 | 122.0138 | 48.6262 | -122.1536
5212.375 | 122.0993 | -0.11902 | 122.0169 | -0.0025182 | -0.062931 | 0.037729 | 0.014127 | -0.015283 | -0.0046535 | -0.021518 | 0.074002 | 0.048774 | 0.073001 | 0.090473 | 0.1246 | -0.021844 | 0.0243 | -0.022144 | 0.088755 | 0.13315 | 0.26101 | -0.10885 | 52.615 | 48.3973 | 48.7985 | 121.8175 | 122.1021 | 121.9451 | -0.18704 | 0.010172 | -121.9282 | 0.097175 | 0.096875 | 0.086703 | -121.8838 | -121.7559 | -0.068024 | -0.19937 | 52.734 | 48.9175 | 48.9855 | 0.085236 | -0.071814 | 0.20777 | 0.25217 | 0.38003 | 0.14332 | -122.1258 | 121.9366 | 122.2212 | 122.0641 | 48.5163 | -122.204
5214.0938 | 122.0947 | -0.11444 | 122.0306 | -0.01778 | -0.062504 | 0.037729 | 0.014127 | -0.015283 | -0.0044399 | -0.036779 | 0.072934 | 0.05732 | 0.071506 | 0.094106 | 0.1261 | -0.026423 | 0.0243 | -0.017566 | 0.093333 | 0.13773 | 0.26559 | -0.10885 | 53.0317 | 50.0136 | 53.4642 | 121.8084 | 122.093 | 121.9359 | -0.18246 | 0.005594 | -121.9373 | 0.088018 | 0.096875 | 0.091281 | -121.8929 | -121.7651 | -0.068023 | -0.22226 | 53.1461 | 53.5786 | 53.6467 | 0.062345 | -0.094704 | 0.20777 | 0.25217 | 0.38003 | 0.13874 | -122.1395 | 121.9228 | 122.2074 | 122.0504 | 50.128 | -122.2131
5215.7969 | 122.1405 | -0.07782 | 122.0169 | -0.01778 | -0.062717 | 0.038157 | 0.014554 | -0.01507 | -0.0014487 | -0.021518 | 0.096007 | 0.079327 | 0.093725 | 0.14539 | 0.13358 | -0.026423 | 0.0243 | -0.017566 | 0.093333 | 0.13773 | 0.26101 | -0.11342 | 54.0207 | 71.4969 | 119.5487 | 121.7901 | 122.0793 | 121.9359 | -0.17788 | -0.035605 | -121.9236 | 0.051397 | 0.060254 | 0.095859 | -121.8792 | -121.7559 | -0.10006 | -0.22684 | 54.0985 | 119.6265 | 119.7266 | 0.062343 | -0.080971 | 0.17115 | 0.21555 | 0.33883 | 0.10212 | -122.1303 | 121.8679 | 122.1571 | 122.0138 | 71.5747 | -122.1948
5217.5312 | 122.1863 | -0.059509 | 121.9711 | -0.010149 | -0.062717 | 0.038157 | 0.013913 | -0.01507 | -0.00059393 | -0.021518 | 0.095152 | 0.082318 | 0.092871 | 0.14496 | 0.13507 | -0.026423 | 0.0243 | -0.022144 | 0.088755 | 0.14231 | 0.26101 | -0.11342 | 55.4675 | 72.1791 | 119.6586 | 121.7809 | 122.0747 | 121.9176 | -0.17788 | -0.053916 | -121.8824 | 0.033086 | 0.037365 | 0.091281 | -121.8288 | -121.7101 | -0.11838 | -0.19022 | 55.527 | 119.7181 | 119.8365 | 0.10354 | -0.053509 | 0.14826 | 0.20181 | 0.32052 | 0.083809 | -122.0846 | 121.8404 | 122.1342 | 121.9771 | 72.2387 | -122.149
5219.3594 | 122.2275 | -0.073242 | 121.9574 | -0.010149 | -0.062717 | 0.038157 | 0.01434 | -0.015497 | -0.0012349 | -0.021518 | 0.095152 | 0.084455 | 0.092443 | 0.14517 | 0.13593 | -0.021844 | 0.0243 | -0.022144 | 0.088755 | 0.13315 | 0.26101 | -0.11342 | 55.9163 | 73.7359 | 119.7227 | 121.7809 | 122.0701 | 121.9176 | -0.17331 | -0.040183 | -121.8686 | 0.051398 | 0.051098 | 0.091281 | -121.8242 | -121.6964 | -0.10006 | -0.17649 | 55.9895 | 119.7959 | 119.896 | 0.1127 | -0.039776 | 0.162 | 0.20639 | 0.33425 | 0.097542 | -122.0708 | 121.8542 | 122.1433 | 121.9909 | 73.8091 | -122.1307
5221.1094 | 122.1451 | -0.064087 | 121.994 | -0.01778 | -0.062717 | 0.038157 | 0.01434 | -0.015283 | -0.0010213 | -0.013887 | 0.095152 | 0.08595 | 0.09223 | 0.14539 | 0.13742 | -0.031001 | 0.019721 | -0.012988 | 0.084176 | 0.14231 | 0.26559 | -0.10885 | 56.6855 | 74.615 | 119.7227 | 121.7763 | 122.0701 | 121.913 | -0.17788 | -0.04476 | -121.9098 | 0.033086 | 0.051099 | 0.095859 | -121.8517 | -121.7284 | -0.1138 | -0.21769 | 56.7496 | 119.7868 | 119.9006 | 0.076073 | -0.080976 | 0.14826 | 0.20639 | 0.32967 | 0.083808 | -122.1029 | 121.8404 | 122.1342 | 121.9771 | 74.6791 | -122.1719
5222.875 | 122.0947 | -0.10529 | 122.0123 | -0.0025182 | -0.062717 | 0.037943 | 0.014554 | -0.01507 | -0.00059393 | -0.021518 | 0.096007 | 0.08766 | 0.093298 | 0.14517 | 0.13934 | -0.021844 | 0.0243 | -0.017566 | 0.088755 | 0.13315 | 0.25643 | -0.12716 | 57.2303 | 76.4144 | 119.7227 | 121.7763 | 122.0655 | 121.913 | -0.17788 | -0.021876 | -121.9236 | 0.083442 | 0.08772 | 0.1096 | -121.8792 | -121.7559 | -0.072599 | -0.236 | 57.3356 | 119.828 | 119.9006 | 0.053185 | -0.099286 | 0.19404 | 0.23843 | 0.36172 | 0.12959 | -122.1395 | 121.8816 | 122.1708 | 122.0183 | 76.5197 | -122.1902
5224.7031 | 122.1634 | -0.091553 | 121.9574 | -0.01778 | -0.062504 | 0.038157 | 0.01434 | -0.015283 | -0.00038033 | -0.029148 | 0.095366 | 0.088301 | 0.092443 | 0.14475 | 0.13849 | -0.03558 | 0.019721 | -0.017566 | 0.097912 | 0.13773 | 0.26101 | -0.11342 | 57.4226 | 73.6352 | 119.7044 | 121.7718 | 122.0609 | 121.8993 | -0.18246 | -0.021872 | -121.8595 | 0.055973 | 0.073987 | 0.095859 | -121.8197 | -121.6964 | -0.090911 | -0.18564 | 57.5142 | 119.7959 | 119.8868 | 0.10354 | -0.05809 | 0.18946 | 0.22928 | 0.35256 | 0.11127 | -122.0708 | 121.8633 | 122.1525 | 121.9909 | 73.7267 | -122.1399
5226.5 | 122.0764 | -0.11444 | 121.9711 | -0.0025182 | -0.062717 | 0.038157 | 0.014554 | -0.01507 | -0.00016673 | -0.021518 | 0.095793 | 0.089582 | 0.093084 | 0.14496 | 0.14041 | -0.026423 | 0.015142 | -0.022144 | 0.088755 | 0.13773 | 0.27017 | -0.11342 | 59.1122 | 72.9575 | 119.7181 | 121.7718 | 122.0609 | 121.9039 | -0.17788 | 0.001016 | -121.8824 | 0.088018 | 0.092297 | 0.091281 | -121.8334 | -121.701 | -0.063444 | -0.19938 | 59.2266 | 119.8326 | 119.896 | 0.089805 | -0.067245 | 0.2032 | 0.25217 | 0.38461 | 0.12958 | -122.0846 | 121.8862 | 122.1754 | 122.0183 | 73.072 | -122.149
5228.2969 | 121.0098 | -0.064087 | 120.7901 | -0.010149 | -0.063145 | 0.037943 | 0.013699 | -0.01507 | -0.011277 | -0.021518 | 0.093443 | 0.088087 | 0.090734 | 0.14176 | 0.13806 | -0.021844 | 0.019721 | -0.017566 | 0.088755 | 0.13773 | 0.25643 | -0.11342 | 56.951 | 70.4575 | 116.0323 | 118.4661 | 118.7414 | 118.621 | -0.16873 | -0.049338 | -120.7013 | 0.042243 | 0.046521 | 0.095859 | -120.6524 | -120.5337 | -0.10464 | -2.324 | 57.0151 | 116.0963 | 116.201 | -2.0487 | -2.1691 | 0.15284 | 0.20181 | 0.32052 | 0.083808 | -120.9035 | 118.5302 | 118.8055 | 118.6851 | 70.5216 | -120.9588
5230.0156 | 121.8475 | -0.073242 | 121.6461 | -0.010149 | -0.062504 | 0.037943 | 0.01434 | -0.015497 | -0.00038033 | -0.021518 | 0.096007 | 0.090864 | 0.093725 | 0.14432 | 0.14148 | -0.017266 | 0.028878 | -0.017566 | 0.084176 | 0.13773 | 0.26101 | -0.10885 | 59.2908 | 71.8083 | 119.3564 | 121.4513 | 121.7359 | 121.5834 | -0.18704 | -0.035605 | -121.5619 | 0.055976 | 0.055676 | 0.091281 | -121.5084 | -121.3851 | -0.1138 | -0.19486 | 59.364 | 119.4296 | 119.5434 | 0.089736 | -0.062735 | 0.15742 | 0.21097 | 0.33425 | 0.10212 | -121.755 | 121.5245 | 121.8091 | 121.6566 | 71.8815 | -121.8332
5231.8125 | 121.9482 | -0.07782 | 121.7194 | -0.01778 | -0.062717 | 0.037943 | 0.01434 | -0.015497 | 0.013508 | -0.029148 | 0.096007 | 0.091505 | 0.093084 | 0.14453 | 0.14234 | -0.031001 | 0.019721 | -0.022144 | 0.088755 | 0.13315 | 0.25185 | -0.118 | 57.4868 | 71.529 | 119.5212 | 121.5199 | 121.8091 | 121.6475 | -0.17788 | -0.040184 | -121.6306 | 0.046819 | 0.055676 | 0.09586 | -121.5862 | -121.4675 | -0.10006 | -0.19942 | 57.5646 | 119.5991 | 119.6991 | 0.089752 | -0.071876 | 0.16658 | 0.21097 | 0.32967 | 0.097541 | -121.8374 | 121.5978 | 121.8869 | 121.7253 | 71.6068 | -121.8972
5233.6094 | 121.9254 | -0.11444 | 121.6095 | -0.010149 | -0.062717 | 0.037943 | 0.01434 | -0.015283 | 0.07547 | -0.013887 | 0.097716 | 0.093001 | 0.09458 | 0.14453 | 0.1464 | -0.044736 | 0.015142 | -0.026723 | 0.079598 | 0.12857 | 0.24269 | -0.17295 | 57.5188 | 68.4521 | 119.4526 | 121.4238 | 121.713 | 121.5559 | -0.20994 | -0.05851 | -121.5299 | 0.069705 | 0.087718 | 0.14623 | -121.4809 | -121.3668 | -0.095496 | -0.18571 | 57.6332 | 119.567 | 119.6625 | 0.10346 | -0.053585 | 0.19404 | 0.24301 | 0.35714 | 0.12958 | -121.7824 | 121.5382 | 121.8274 | 121.6704 | 68.5665 | -121.8194
5235.375 | 121.8475 | -0.13275 | 121.6599 | -0.0025182 | -0.062504 | 0.038157 | 0.014127 | -0.015283 | 0.13444 | -0.021518 | 0.097075 | 0.093001 | 0.09458 | 0.14432 | 0.14404 | -0.03558 | -0.003172 | -0.031301 | 0.07502 | 0.12399 | 0.23812 | -0.18669 | 59.6662 | 74.0793 | 119.4159 | 121.4284 | 121.713 | 121.5696 | -0.24199 | -0.053937 | -121.5848 | 0.097171 | 0.10145 | 0.15539 | -121.5359 | -121.4217 | -0.10924 | -0.23149 | 59.799 | 119.5487 | 119.6579 | 0.05311 | -0.090203 | 0.20777 | 0.25674 | 0.37087 | 0.12958 | -121.8465 | 121.5611 | 121.8457 | 121.7024 | 74.2121 | -121.9018
5237.125 | 121.8246 | -0.10986 | 121.7194 | -0.0025182 | -0.062717 | 0.037729 | 0.014127 | -0.015497 | 0.037865 | -0.021518 | 0.097716 | 0.092787 | 0.09458 | 0.14389 | 0.14533 | -0.031001 | 0.019721 | -0.017566 | 0.088755 | 0.12857 | 0.26559 | -0.12716 | 59.4464 | 76.941 | 119.5441 | 121.5062 | 121.7908 | 121.6292 | -0.18704 | -0.017299 | -121.6306 | 0.078862 | 0.092297 | 0.1096 | -121.5908 | -121.4538 | -0.07718 | -0.21316 | 59.5563 | 119.654 | 119.7312 | 0.071438 | -0.090191 | 0.19862 | 0.23843 | 0.37545 | 0.12958 | -121.8465 | 121.6161 | 121.9007 | 121.739 | 77.0509 | -121.9064
5238.9688 | 121.962 | -0.086975 | 121.6965 | -0.01778 | -0.062717 | 0.03837 | 0.013913 | -0.01507 | 0.029105 | -0.029148 | 0.09857 | 0.094283 | 0.096289 | 0.14432 | 0.14853 | -0.031001 | 0.019721 | -0.012988 | 0.088755 | 0.13315 | 0.25643 | -0.12258 | 59.8173 | 74.2167 | 119.6082 | 121.5383 | 121.8183 | 121.6566 | -0.18246 | -0.035608 | -121.6077 | 0.055974 | 0.073987 | 0.10959 | -121.5633 | -121.44 | -0.095489 | -0.15822 | 59.9043 | 119.6952 | 119.7907 | 0.1218 | -0.039831 | 0.17573 | 0.22012 | 0.34341 | 0.1067 | -121.8191 | 121.6252 | 121.9052 | 121.7436 | 74.3036 | -121.8789
5240.7031 | 121.8201 | -0.31586 | 121.5317 | -0.01778 | -0.062076 | 0.037943 | 0.013913 | -0.01507 | 0.51027 | -0.021518 | 0.098784 | 0.094283 | 0.096503 | 0.14389 | 0.14746 | -0.095099 | -0.048958 | -0.077084 | 0.029236 | 0.069043 | 0.19233 | -0.29658 | 57.6287 | 74.6883 | 119.2786 | 121.2498 | 121.5252 | 121.3819 | -0.41598 | 0.019275 | -121.5024 | 0.22076 | 0.23877 | 0.2195 | -121.4626 | -121.3393 | -0.10013 | -0.28187 | 57.9445 | 119.5944 | 119.6945 | -0.006438 | -0.14975 | 0.34509 | 0.3849 | 0.50819 | 0.2669 | -121.8283 | 121.5657 | 121.8411 | 121.6978 | 75.0041 | -121.9477
5242.4219 | 117.0181 | -0.1236 | 116.7114 | -0.01778 | -0.062931 | 0.037943 | 0.013272 | -0.014856 | 0.05795 | -0.021518 | 0.095152 | 0.090223 | 0.092443 | 0.14069 | 0.14148 | -0.031001 | 0.019721 | -0.026723 | 0.084176 | 0.12399 | 0.24727 | -0.14548 | 56.2001 | 72.9438 | 115.2127 | 117.0834 | 117.377 | 117.1925 | -0.19162 | -0.021882 | -116.6273 | 0.092595 | 0.096873 | 0.11875 | -116.5874 | -116.4642 | -0.068026 | 0.37195 | 56.3237 | 115.3363 | 115.4043 | 0.6656 | 0.48108 | 0.20777 | 0.24759 | 0.37087 | 0.14332 | -116.8569 | 117.207 | 117.5006 | 117.3161 | 73.0674 | -116.903
5244.1719 | 121.5591 | -0.07782 | 121.3577 | -0.010149 | -0.062504 | 0.037729 | 0.014554 | -0.015283 | 0.025473 | -0.021518 | 0.10028 | 0.094497 | 0.097144 | 0.14389 | 0.15003 | -0.026423 | 0.019721 | -0.008409 | 0.088755 | 0.13773 | 0.26101 | -0.11342 | 58.8924 | 77.495 | 119.2145 | 121.1582 | 121.4428 | 121.2904 | -0.17788 | -0.035605 | -121.269 | 0.051397 | 0.069411 | 0.10502 | -121.22 | -121.0967 | -0.10006 | -0.19949 | 58.9702 | 119.2923 | 119.3923 | 0.085097 | -0.067374 | 0.16658 | 0.21555 | 0.33883 | 0.097541 | -121.4712 | 121.2361 | 121.5206 | 121.3682 | 77.5728 | -121.5356
5245.9062 | 121.6873 | -0.068665 | 121.463 | -0.010149 | -0.062931 | 0.03837 | 0.014127 | -0.015283 | 0.020131 | -0.0062567 | 0.10049 | 0.094497 | 0.097785 | 0.14346 | 0.15045 | -0.021844 | 0.019721 | -0.017566 | 0.084176 | 0.13773 | 0.26101 | -0.118 | 58.5856 | 77.7011 | 119.3015 | 121.2361 | 121.5298 | 121.3728 | -0.17331 | -0.049339 | -121.3788 | 0.046821 | 0.051099 | 0.10044 | -121.3253 | -121.202 | -0.10464 | -0.22694 | 58.6543 | 119.3701 | 119.4748 | 0.066804 | -0.090245 | 0.15284 | 0.20639 | 0.32968 | 0.088386 | -121.581 | 121.3047 | 121.5985 | 121.4414 | 77.7697 | -121.6363
5247.625 | 121.6141 | -0.10986 | 121.5637 | -0.0025182 | -0.062931 | 0.037943 | 0.01434 | -0.015283 | 0.014362 | -0.013887 | 0.10113 | 0.09642 | 0.098212 | 0.14368 | 0.15387 | -0.031001 | 0.019721 | -0.003831 | 0.084176 | 0.12857 | 0.25185 | -0.12258 | 58.7001 | 74.7844 | 119.3518 | 121.2956 | 121.5802 | 121.4277 | -0.16873 | -0.01272 | -121.4795 | 0.078862 | 0.10603 | 0.11875 | -121.4352 | -121.3119 | -0.058865 | -0.26813 | 58.81 | 119.4617 | 119.5206 | 0.016461 | -0.13601 | 0.19404 | 0.23843 | 0.36172 | 0.12958 | -121.6863 | 121.4055 | 121.69 | 121.5376 | 74.8943 | -121.7324
5249.3594 | 121.7239 | -0.064087 | 121.5271 | -0.025411 | -0.063145 | 0.037943 | 0.014127 | -0.015283 | 0.015858 | -0.029148 | 0.10818 | 0.10262 | 0.10483 | 0.14325 | 0.17396 | -0.03558 | 0.0243 | -0.008409 | 0.088755 | 0.13773 | 0.26101 | -0.12258 | 58.7917 | 74.9493 | 119.4022 | 121.3185 | 121.6031 | 121.4506 | -0.14583 | -0.058496 | -121.4383 | 0.028507 | 0.055678 | 0.11417 | -121.3894 | -121.2661 | -0.081746 | -0.20862 | 58.8558 | 119.4663 | 119.548 | 0.075975 | -0.076496 | 0.15284 | 0.20181 | 0.3251 | 0.088387 | -121.6497 | 121.3826 | 121.6672 | 121.5147 | 75.0133 | -121.6729
5251.1562 | 121.7239 | -0.059509 | 121.6141 | -0.01778 | -0.063145 | 0.037729 | 0.01434 | -0.015283 | -0.0029443 | -0.021518 | -0.023203 | -0.0095547 | 0.022794 | 0.055217 | -0.00017086 | -0.026423 | 0.028878 | -0.017566 | 0.088755 | 0.14231 | 0.25643 | -0.10885 | 0.38108 | 0.43534 | 0.38778 | 0.53778 | 0.69592 | 0.67165 | 0.083107 | -0.049338 | -121.5253 | 0.033086 | 0.041943 | 0.091281 | -121.4718 | -121.3576 | 0.14262 | -121.0763 | 0.44059 | 0.44729 | 0.30468 | -120.9182 | -120.9424 | 0.14826 | 0.20181 | 0.31594 | 0.088387 | -121.7229 | 0.59729 | 0.75543 | 0.73116 | 0.49484 | -121.531
5252.8594 | 121.7651 | -0.054932 | 121.637 | -0.025411 | -0.062717 | 0.038157 | 0.014127 | -0.015283 | -0.0027305 | -0.029148 | -0.023203 | -0.0091275 | 0.022794 | 0.055217 | -0.00017086 | -0.012688 | 0.019721 | -0.003831 | 0.088755 | 0.15146 | 0.27017 | -0.10885 | 0.28035 | 0.31629 | 0.23211 | 0.37295 | 0.53567 | 0.52055 | 0.005267 | -0.053915 | -121.5482 | 0.042244 | 0.051101 | 0.10502 | -121.4855 | -121.3668 | 0.060199 | -121.264 | 0.33528 | 0.28704 | 0.22684 | -121.1013 | -121.1164 | 0.14369 | 0.20639 | 0.3251 | 0.074653 | -121.7458 | 0.42788 | 0.5906 | 0.57549 | 0.37122 | -121.6317
5254.5625 | 121.7743 | -0.064087 | 121.6187 | -0.01778 | -0.063145 | 0.038157 | 0.01434 | -0.015283 | 4.7068e-05 | -0.013887 | -0.022776 | -0.0091275 | 0.022581 | 0.055431 | -0.00038466 | -0.021844 | 0.0243 | -0.012988 | 0.084176 | 0.14688 | 0.26101 | -0.118 | 0.23914 | 0.2705 | 0.17716 | 0.31801 | 0.48072 | 0.46103 | -0.035942 | -0.053917 | -121.5345 | 0.042243 | 0.051099 | 0.10502 | -121.4718 | -121.3576 | 0.028145 | -121.3006 | 0.30323 | 0.24125 | 0.2131 | -121.1379 | -121.1576 | 0.14826 | 0.21097 | 0.3251 | 0.088387 | -121.7367 | 0.3821 | 0.54481 | 0.52512 | 0.33459 | -121.6546
5256.3281 | 121.7606 | -0.068665 | 121.5729 | -0.01778 | -0.062931 | 0.037943 | 0.01434 | -0.015711 | -0.0040125 | -0.029148 | -0.022776 | -0.0095547 | 0.022367 | 0.055004 | -0.00017086 | -0.021844 | 0.019721 | -0.012988 | 0.084176 | 0.14231 | 0.26559 | -0.10885 | 0.22083 | 0.24303 | 0.14053 | 0.29054 | 0.4441 | 0.43814 | -0.054257 | -0.040182 | -121.4887 | 0.046821 | 0.055677 | 0.095859 | -121.4306 | -121.3073 | 0.014408 | -121.2823 | 0.28949 | 0.2092 | 0.19479 | -121.1288 | -121.1347 | 0.15284 | 0.21097 | 0.33425 | 0.088386 | -121.6817 | 0.3592 | 0.51276 | 0.5068 | 0.3117 | -121.6271
5258.1094 | 121.7789 | -0.10986 | 121.6461 | -0.0025182 | -0.062504 | 0.038157 | 0.01434 | -0.01507 | 0.10154 | -0.013887 | -0.022776 | -0.0091275 | 0.022581 | 0.055217 | -0.00038466 | -0.031001 | 0.001407 | -0.026723 | 0.079598 | 0.12857 | 0.25185 | -0.15464 | 0.20251 | 0.23387 | 0.1039 | 0.24933 | 0.40747 | 0.40151 | -0.049678 | -0.044773 | -121.5665 | 0.078862 | 0.08314 | 0.12791 | -121.5175 | -121.3943 | 0.060185 | -121.3968 | 0.31237 | 0.21377 | 0.15358 | -121.2387 | -121.2446 | 0.18946 | 0.23843 | 0.36172 | 0.11127 | -121.8008 | 0.3592 | 0.51733 | 0.51137 | 0.34374 | -121.6958
5259.875 | 121.8018 | -0.09613 | 121.6461 | -0.010149 | -0.062717 | 0.037943 | 0.014127 | -0.015711 | 0.038934 | -0.021518 | -0.022562 | -0.0095547 | 0.022581 | 0.055217 | -0.00038466 | -0.026423 | 0.019721 | -0.008409 | 0.093333 | 0.13315 | 0.26101 | -0.15464 | 0.19793 | 0.21098 | 0.090168 | 0.22644 | 0.39831 | 0.38777 | -0.058836 | -0.058506 | -121.5528 | 0.069707 | 0.087721 | 0.14623 | -121.513 | -121.3851 | 0.037294 | -121.4197 | 0.29406 | 0.1863 | 0.149 | -121.2478 | -121.2583 | 0.18946 | 0.22928 | 0.35714 | 0.11585 | -121.8008 | 0.32257 | 0.49444 | 0.4839 | 0.30711 | -121.705
5261.6562 | 121.756 | -0.11902 | 121.6278 | -0.01778 | -0.062717 | 0.038157 | 0.014127 | -0.015497 | 0.032951 | -0.013887 | -0.022562 | -0.0091275 | 0.022581 | 0.055217 | 4.2736e-05 | -0.031001 | 0.015142 | -0.012988 | 0.084176 | 0.13315 | 0.25643 | -0.12716 | 0.1842 | 0.2064 | 0.094746 | 0.21728 | 0.38915 | 0.37404 | -0.063415 | -0.008143 | -121.5436 | 0.088018 | 0.10603 | 0.11417 | -121.4947 | -121.3714 | 0.055604 | -121.4105 | 0.30322 | 0.21376 | 0.15816 | -121.2387 | -121.2538 | 0.2032 | 0.25217 | 0.37545 | 0.13416 | -121.755 | 0.3363 | 0.50817 | 0.49306 | 0.32542 | -121.6912
5263.4062 | 121.7056 | -0.12817 | 121.6324 | -0.0025182 | -0.062504 | 0.037943 | 0.014127 | -0.015711 | 0.12589 | -0.029148 | -0.022776 | -0.0091275 | 0.022581 | 0.055217 | -0.00017086 | -0.03558 | 0.015142 | -0.017566 | 0.084176 | 0.12857 | 0.24727 | -0.15464 | 0.17962 | 0.19724 | 0.08101 | 0.20813 | 0.38 | 0.3603 | -0.077151 | -0.026462 | -121.5482 | 0.092594 | 0.11061 | 0.13707 | -121.5038 | -121.3851 | 0.051023 | -121.4243 | 0.30779 | 0.20918 | 0.15816 | -121.2524 | -121.2721 | 0.21235 | 0.25674 | 0.37545 | 0.14332 | -121.787 | 0.3363 | 0.50817 | 0.48848 | 0.32542 | -121.7095
5265.1719 | 121.7285 | -0.56763 | 121.0464 | -0.010149 | -0.062076 | 0.037729 | 0.013699 | -0.015711 | 0.46989 | -0.013887 | -0.022776 | -0.0091275 | 0.022581 | 0.055217 | -0.00017086 | -0.085942 | -0.035222 | -0.072505 | 0.042971 | 0.073622 | 0.20607 | -0.27369 | 0.17046 | 0.19267 | 0.067274 | 0.20355 | 0.36626 | 0.35115 | -0.086309 | 0.29394 | -121.0035 | 0.48168 | 0.49512 | 0.20118 | -120.9728 | -120.8404 | 0.48132 | -120.8429 | 0.73809 | 0.6349 | 0.15358 | -120.6802 | -120.6953 | 0.6106 | 0.64125 | 0.77369 | 0.53241 | -121.3201 | 0.77118 | 0.93389 | 0.91877 | 0.76029 | -121.1328
5266.9219 | 121.7331 | -0.18768 | 121.5042 | -0.01778 | -0.062504 | 0.037729 | 0.013913 | -0.015283 | 0.27567 | -0.013887 | -0.022562 | -0.0089137 | 0.022794 | 0.055431 | -0.00038466 | -0.058472 | -0.012329 | -0.040457 | 0.061284 | 0.11025 | 0.23354 | -0.20958 | 0.16588 | 0.18351 | 0.062695 | 0.19439 | 0.36168 | 0.34657 | -0.090888 | -0.0219 | -121.4429 | 0.12921 | 0.14723 | 0.16913 | -121.394 | -121.2707 | 0.096795 | -121.3098 | 0.35356 | 0.25038 | 0.15358 | -121.1425 | -121.1576 | 0.24897 | 0.29794 | 0.42122 | 0.17535 | -121.7138 | 0.38207 | 0.54936 | 0.53425 | 0.37119 | -121.5951
5268.625 | 121.3028 | -0.10529 | 121.2067 | -0.010149 | -0.062717 | 0.037516 | 0.01434 | -0.015711 | 0.05624 | -0.013887 | -0.022562 | -0.0089137 | 0.022794 | 0.055431 | -0.00038466 | -0.031001 | 0.010564 | -0.022144 | 0.093333 | 0.13315 | 0.26101 | -0.14548 | 0.16588 | 0.17893 | 0.058117 | 0.18524 | 0.35252 | 0.33741 | -0.095467 | -0.040192 | -121.1133 | 0.074285 | 0.083142 | 0.12333 | -121.0735 | -120.9457 | 0.009819 | -121.0214 | 0.27117 | 0.1634 | 0.15358 | -120.8541 | -120.8693 | 0.19862 | 0.23843 | 0.3663 | 0.11585 | -121.3521 | 0.29052 | 0.45781 | 0.4427 | 0.28421 | -121.3021
5270.375 | 121.4859 | -0.068665 | 121.2936 | -0.01778 | -0.062717 | 0.037943 | 0.01434 | -0.015497 | 0.019277 | -0.029148 | -0.021708 | -0.0093411 | 0.022581 | 0.055431 | -0.00017086 | -0.017266 | 0.033457 | -0.008409 | 0.093333 | 0.14688 | 0.26559 | -0.118 | 0.15672 | 0.17893 | 0.053538 | 0.18524 | 0.34337 | 0.32825 | -0.10462 | -0.049339 | -121.2003 | 0.051399 | 0.060256 | 0.10959 | -121.1468 | -121.0281 | -0.035959 | -121.1084 | 0.22539 | 0.1222 | 0.15816 | -120.9503 | -120.9654 | 0.162 | 0.21555 | 0.33425 | 0.10212 | -121.4116 | 0.2539 | 0.41203 | 0.39692 | 0.24759 | -121.3983
5272.1562 | 121.582 | -0.054932 | 121.3669 | -0.01778 | -0.062931 | 0.037729 | 0.01434 | -0.015283 | 0.020131 | -0.029148 | -0.021921 | -0.0093411 | 0.022794 | 0.055217 | -0.00017086 | -0.021844 | 0.019721 | -0.008409 | 0.088755 | 0.13773 | 0.25643 | -0.11342 | 0.15672 | 0.17435 | 0.053538 | 0.18066 | 0.33879 | 0.33283 | -0.11378 | -0.058493 | -121.2781 | 0.033088 | 0.046523 | 0.10502 | -121.2292 | -121.1105 | -0.05885 | -121.1862 | 0.21166 | 0.10847 | 0.16732 | -121.0281 | -121.0341 | 0.14369 | 0.19266 | 0.31136 | 0.074653 | -121.4803 | 0.23559 | 0.39372 | 0.38776 | 0.22928 | -121.4807
5273.8594 | 121.5317 | -0.082397 | 121.4584 | -0.010149 | -0.062931 | 0.037729 | 0.013913 | -0.015497 | 0.018422 | -0.029148 | -0.021494 | -0.0091275 | 0.022367 | 0.055217 | -0.00017086 | -0.021844 | 0.028878 | -0.008409 | 0.093333 | 0.13773 | 0.25643 | -0.11342 | 0.15215 | 0.16977 | 0.044381 | 0.18524 | 0.33421 | 0.33283 | -0.10462 | -0.031028 | -121.3651 | 0.060553 | 0.073988 | 0.10502 | -121.3207 | -121.202 | -0.022227 | -121.2732 | 0.23454 | 0.12678 | 0.149 | -121.1242 | -121.1256 | 0.17573 | 0.22012 | 0.33883 | 0.11127 | -121.5719 | 0.26763 | 0.41661 | 0.41523 | 0.25217 | -121.5631
5275.625 | 120.9915 | -0.068665 | 120.7993 | -0.010149 | -0.062931 | 0.037729 | 0.014127 | -0.015497 | 0.050899 | -0.013887 | -0.021708 | -0.0093411 | 0.023008 | 0.055217 | -0.00038466 | -0.03558 | 0.010564 | -0.012988 | 0.079598 | 0.13773 | 0.25643 | -0.12258 | 0.14757 | 0.16977 | 0.053538 | 0.1715 | 0.32505 | 0.32367 | -0.11836 | -0.053918 | -120.7197 | 0.033085 | 0.055677 | 0.10959 | -120.6615 | -120.5428 | -0.049696 | -120.6278 | 0.21623 | 0.1222 | 0.1719 | -120.4742 | -120.4756 | 0.14826 | 0.20639 | 0.3251 | 0.079229 | -120.9218 | 0.24016 | 0.39372 | 0.39234 | 0.23844 | -120.9176
5277.3906 | 121.1334 | -0.15564 | 120.9229 | -0.01778 | -0.062717 | 0.037943 | 0.013913 | -0.015497 | 0.13893 | -0.021518 | -0.021708 | -0.0091275 | 0.023435 | 0.055004 | -0.00017086 | -0.040158 | 0.019721 | -0.017566 | 0.079598 | 0.11941 | 0.24727 | -0.18211 | 0.14757 | 0.16519 | 0.035223 | 0.16692 | 0.32963 | 0.3191 | -0.11378 | -0.026469 | -120.8433 | 0.11548 | 0.13807 | 0.16454 | -120.8034 | -120.6756 | 0.041858 | -120.7559 | 0.30321 | 0.19086 | 0.149 | -120.5932 | -120.6038 | 0.23524 | 0.27505 | 0.40291 | 0.17536 | -121.105 | 0.32256 | 0.48527 | 0.47474 | 0.32083 | -121.0366
5279.0938 | 121.1975 | -0.2655 | 120.8359 | -0.010149 | -0.063145 | 0.037943 | 0.013913 | -0.01507 | 0.36926 | -0.021518 | -0.021494 | -0.0093411 | 0.023221 | 0.055217 | -0.00017086 | -0.06305 | -0.016908 | -0.05877 | 0.052128 | 0.091937 | 0.21064 | -0.24163 | 0.14757 | 0.16061 | 0.039802 | 0.16234 | 0.32047 | 0.30994 | -0.11836 | 0.023868 | -120.7837 | 0.20245 | 0.20673 | 0.18286 | -120.7439 | -120.6252 | 0.14714 | -120.6735 | 0.41307 | 0.3053 | 0.15816 | -120.5154 | -120.5259 | 0.31763 | 0.35744 | 0.47615 | 0.24859 | -121.0775 | 0.42784 | 0.58598 | 0.57544 | 0.42612 | -120.9542
5280.7812 | 121.2387 | -0.36163 | 120.7535 | -0.010149 | -0.06229 | 0.037943 | 0.013913 | -0.015497 | 0.52288 | -0.013887 | -0.022135 | -0.0093411 | 0.022794 | 0.055217 | -0.00038466 | -0.09052 | -0.048958 | -0.081662 | 0.033814 | 0.08278 | 0.19691 | -0.28742 | 0.13841 | 0.17893 | 0.030644 | 0.16234 | 0.32047 | 0.30536 | -0.12294 | 0.074208 | -120.7197 | 0.27111 | 0.27997 | 0.20576 | -120.6707 | -120.5566 | 0.23869 | -120.5911 | 0.50004 | 0.39228 | 0.15358 | -120.433 | -120.4481 | 0.39545 | 0.44441 | 0.55854 | 0.31267 | -121.0409 | 0.52397 | 0.68211 | 0.66699 | 0.54056 | -120.8764
5282.5469 | 121.1792 | -0.37537 | 120.7901 | -0.01778 | -0.062504 | 0.037943 | 0.013913 | -0.015497 | 0.55771 | -0.036779 | -0.021708 | -0.0089137 | 0.023008 | 0.055431 | -0.00017086 | -0.095099 | -0.048958 | -0.077084 | 0.024657 | 0.064464 | 0.19691 | -0.30116 | 0.13841 | 0.16977 | 0.035223 | 0.15776 | 0.31132 | 0.30994 | -0.11836 | 0.074205 | -120.7654 | 0.28027 | 0.29828 | 0.22408 | -120.7256 | -120.5932 | 0.257 | -120.6323 | 0.51377 | 0.41059 | 0.15358 | -120.4788 | -120.4802 | 0.40002 | 0.43983 | 0.57227 | 0.32641 | -121.0913 | 0.53313 | 0.68668 | 0.6853 | 0.54514 | -120.9085
5284.3125 | 117.7002 | -0.17853 | 117.4805 | -0.025411 | -0.063145 | 0.037729 | 0.013699 | -0.01507 | 0.30003 | -0.021518 | -0.021921 | -0.0089137 | 0.023221 | 0.055004 | 4.2736e-05 | -0.067628 | -0.012329 | -0.040457 | 0.052128 | 0.10567 | 0.2198 | -0.23248 | 0.13841 | 0.16061 | 0.035223 | 0.15776 | 0.30674 | 0.30994 | -0.12294 | -0.053949 | -117.4283 | 0.1109 | 0.13807 | 0.19202 | -117.3748 | -117.2607 | 0.055589 | -117.3227 | 0.31694 | 0.21375 | 0.15816 | -117.1737 | -117.1705 | 0.23066 | 0.2842 | 0.39833 | 0.1662 | -117.7129 | 0.33629 | 0.48526 | 0.48847 | 0.33914 | -117.6034
5286.0781 | 120.9686 | -0.10529 | 120.7718 | -0.01778 | -0.063145 | 0.037729 | 0.013913 | -0.015497 | 0.13957 | -0.021518 | -0.021494 | -0.0091275 | 0.023221 | 0.055217 | -0.00059826 | -0.044736 | 0.005985 | -0.031301 | 0.079598 | 0.12399 | 0.25185 | -0.15921 | 0.13841 | 0.15604 | 0.035223 | 0.15318 | 0.31132 | 0.30536 | -0.12294 | -0.053929 | -120.6922 | 0.06055 | 0.073985 | 0.12791 | -120.6478 | -120.5199 | -0.017653 | -120.6186 | 0.24369 | 0.14051 | 0.15816 | -120.4605 | -120.4664 | 0.18488 | 0.22928 | 0.35714 | 0.11127 | -120.931 | 0.25847 | 0.4166 | 0.41065 | 0.26132 | -120.8947
5287.7812 | 121.2158 | -0.31128 | 120.5795 | -0.01778 | -0.06229 | 0.037302 | 0.013699 | -0.015283 | 0.70813 | -0.036779 | -0.021921 | -0.0091275 | 0.023008 | 0.055645 | -0.00017086 | -0.11341 | -0.067272 | -0.10913 | 0.010922 | 0.050727 | 0.17402 | -0.36527 | 0.14299 | 0.15604 | 0.026066 | 0.14861 | 0.30674 | 0.2962 | -0.12752 | -0.053987 | -120.5686 | 0.19787 | 0.20215 | 0.25613 | -120.5288 | -120.4055 | 0.18376 | -120.4309 | 0.45427 | 0.33734 | 0.15358 | -120.2728 | -120.2833 | 0.3222 | 0.36201 | 0.48529 | 0.24401 | -120.9448 | 0.45989 | 0.61802 | 0.60748 | 0.46731 | -120.707
5289.5312 | 121.1746 | -0.20599 | 120.7489 | -0.010149 | -0.062717 | 0.037943 | 0.014127 | -0.015283 | 0.38528 | -0.021518 | -0.021921 | -0.0093411 | 0.023435 | 0.055431 | 4.2736e-05 | -0.072207 | -0.016908 | -0.054192 | 0.056706 | 0.096516 | 0.21522 | -0.24163 | 0.13841 | 0.14688 | 0.026066 | 0.14403 | 0.30674 | 0.2962 | -0.1321 | -0.035641 | -120.6922 | 0.13379 | 0.1518 | 0.18744 | -120.6524 | -120.5337 | 0.073897 | -120.6049 | 0.3444 | 0.23206 | 0.15816 | -120.4422 | -120.4527 | 0.2627 | 0.30251 | 0.42122 | 0.18909 | -120.9905 | 0.35002 | 0.51273 | 0.5022 | 0.35287 | -120.881
5291.2812 | 121.1014 | -0.21057 | 120.8359 | -0.010149 | -0.062717 | 0.037516 | 0.014127 | -0.015283 | 0.36434 | -0.013887 | -0.021708 | -0.0093411 | 0.023008 | 0.055431 | -0.00017086 | -0.072207 | -0.021486 | -0.054192 | 0.056706 | 0.1011 | 0.2198 | -0.23248 | 0.12925 | 0.14688 | 0.021487 | 0.14403 | 0.31132 | 0.29162 | -0.12294 | -0.021906 | -120.7792 | 0.13836 | 0.15638 | 0.17828 | -120.7348 | -120.6161 | 0.087632 | -120.6918 | 0.33982 | 0.23206 | 0.14443 | -120.5246 | -120.5443 | 0.26728 | 0.31167 | 0.43037 | 0.18909 | -121.0684 | 0.3546 | 0.52189 | 0.50219 | 0.35745 | -120.9588
5292.9844 | 121.1517 | -0.20142 | 120.9 | -0.01778 | -0.062504 | 0.038157 | 0.013699 | -0.015497 | 0.34169 | -0.021518 | -0.021708 | -0.0089137 | 0.023221 | 0.055217 | -0.00038466 | -0.072207 | -0.021486 | -0.05877 | 0.047549 | 0.1011 | 0.2198 | -0.2279 | 0.13383 | 0.15146 | 0.016908 | 0.14861 | 0.30674 | 0.29162 | -0.12752 | -0.026483 | -120.8524 | 0.12921 | 0.14265 | 0.16913 | -120.7989 | -120.6802 | 0.073898 | -120.7514 | 0.33525 | 0.21832 | 0.14443 | -120.5932 | -120.6083 | 0.24897 | 0.30251 | 0.42122 | 0.17993 | -121.1279 | 0.35002 | 0.50815 | 0.49304 | 0.35287 | -121.0275
5294.7344 | 121.2387 | -0.1831 | 120.8771 | -0.010149 | -0.062717 | 0.037943 | 0.014127 | -0.015283 | 0.2746 | -0.013887 | -0.021921 | -0.0095547 | 0.022794 | 0.055431 | -0.00017086 | -0.067628 | -0.012329 | -0.049614 | 0.061284 | 0.11025 | 0.23354 | -0.20042 | 0.13841 | 0.15146 | 0.021487 | 0.14403 | 0.29758 | 0.28247 | -0.12294 | -0.01732 | -120.8158 | 0.11548 | 0.13349 | 0.15081 | -120.7668 | -120.6435 | 0.060166 | -120.733 | 0.32151 | 0.20459 | 0.14443 | -120.5795 | -120.5946 | 0.24439 | 0.29336 | 0.41664 | 0.17078 | -121.0775 | 0.32713 | 0.48069 | 0.46557 | 0.33456 | -121
5296.5 | 121.1472 | -0.21057 | 120.9412 | -0.01778 | -0.062717 | 0.037943 | 0.014127 | -0.015497 | 0.31627 | -0.021518 | -0.021708 | -0.0089137 | 0.023221 | 0.055217 | -0.00017086 | -0.06305 | -0.016908 | -0.049614 | 0.056706 | 0.091937 | 0.22896 | -0.21416 | 0.12925 | 0.1423 | 0.026066 | 0.13945 | 0.29758 | 0.29162 | -0.13668 | -0.003591 | -120.8845 | 0.14752 | 0.16096 | 0.16455 | -120.8492 | -120.7122 | 0.073895 | -120.8017 | 0.33982 | 0.23664 | 0.16274 | -120.6436 | -120.6495 | 0.26728 | 0.30251 | 0.43953 | 0.19366 | -121.1553 | 0.35002 | 0.50815 | 0.50219 | 0.35287 | -121.0778
5298.2188 | 121.1426 | -0.42114 | 120.7077 | -0.033042 | -0.062504 | 0.037729 | 0.013913 | -0.015283 | 0.59211 | -0.021518 | -0.021708 | -0.0084865 | 0.023008 | 0.055645 | -0.00038466 | -0.10883 | -0.053537 | -0.08624 | 0.015501 | 0.055306 | 0.18317 | -0.3149 | 0.13383 | 0.1423 | 0.026066 | 0.13945 | 0.29758 | 0.27789 | -0.1321 | 0.10624 | -120.6922 | 0.31231 | 0.3349 | 0.22866 | -120.6524 | -120.5245 | 0.28905 | -120.5683 | 0.55497 | 0.44721 | 0.15816 | -120.4101 | -120.4298 | 0.43664 | 0.47645 | 0.60432 | 0.36761 | -121.0226 | 0.56059 | 0.71872 | 0.69903 | 0.56344 | -120.8398
5299.9844 | 121.1975 | -0.48981 | 120.5246 | -0.033042 | -0.062504 | 0.037943 | 0.013272 | -0.015283 | 0.83248 | -0.029148 | -0.021708 | -0.0087001 | 0.023221 | 0.055431 | 4.2736e-05 | -0.1363 | -0.090166 | -0.12287 | -0.002813 | 0.032411 | 0.16028 | -0.39274 | 0.14299 | 0.13314 | 0.016908 | 0.13487 | 0.28842 | 0.28247 | -0.1321 | 0.097067 | -120.5274 | 0.3535 | 0.36694 | 0.26987 | -120.4922 | -120.3643 | 0.35771 | -120.3897 | 0.63279 | 0.50672 | 0.149 | -120.2362 | -120.2421 | 0.48699 | 0.52222 | 0.65009 | 0.39964 | -120.9173 | 0.62468 | 0.77823 | 0.77227 | 0.62295 | -120.6567
5301.75 | 121.0968 | -0.46234 | 120.6299 | -0.01778 | -0.06229 | 0.037516 | 0.013699 | -0.01507 | 0.72137 | -0.021518 | -0.021921 | -0.0087001 | 0.023221 | 0.055431 | 4.2736e-05 | -0.12257 | -0.067272 | -0.10455 | 0.006344 | 0.041569 | 0.16944 | -0.36527 | 0.13383 | 0.1423 | 0.016908 | 0.13945 | 0.29758 | 0.27789 | -0.13668 | 0.097075 | -120.6235 | 0.33977 | 0.35779 | 0.26071 | -120.5883 | -120.4604 | 0.32566 | -120.4904 | 0.59617 | 0.47925 | 0.15358 | -120.3323 | -120.352 | 0.46869 | 0.50391 | 0.63178 | 0.39507 | -120.9951 | 0.60179 | 0.75992 | 0.74023 | 0.60464 | -120.7666
5303.4531 | 121.1472 | -0.59967 | 120.3598 | -0.01778 | -0.062076 | 0.037729 | 0.013058 | -0.01507 | 1.2914 | -0.021518 | -0.022135 | -0.0084865 | 0.023435 | 0.055431 | -0.00017086 | -0.18667 | -0.14511 | -0.17323 | -0.062332 | -0.027115 | 0.091601 | -0.56216 | 0.13383 | 0.13772 | 0.016908 | 0.13487 | 0.28842 | 0.27789 | -0.13668 | 0.03751 | -120.4221 | 0.413 | 0.42644 | 0.38893 | -120.3869 | -120.2682 | 0.46299 | -120.2249 | 0.7335 | 0.61658 | 0.15358 | -120.0714 | -120.0819 | 0.53734 | 0.57256 | 0.69127 | 0.45456 | -120.922 | 0.73454 | 0.88809 | 0.87756 | 0.73739 | -120.4965
5305.2188 | 120.9457 | -1.1581 | 119.6732 | -0.025411 | -0.061008 | 0.037302 | 0.012417 | -0.015283 | 1.8976 | -0.029148 | -0.021494 | -0.0087001 | 0.022794 | 0.055217 | -0.00038466 | -0.27823 | -0.22752 | -0.26021 | -0.12185 | -0.10953 | 0.009187 | -0.80484 | 0.12009 | 0.13314 | 0.016908 | 0.12571 | 0.27926 | 0.27789 | -0.14125 | 0.3533 | -119.795 | 0.87991 | 0.89793 | 0.54463 | -119.7827 | -119.664 | 1.0169 | -119.5474 | 1.2782 | 1.175 | 0.15816 | -119.3939 | -119.3953 | 1.0363 | 1.0486 | 1.1673 | 0.93062 | -120.478 | 1.2839 | 1.4374 | 1.436 | 1.2913 | -119.8144
5306.9375 | 120.7901 | -120.0302 | 0.36163 | -0.01778 | -0.068487 | 0.03837 | 0.015409 | -0.015497 | 0.0092345 | -0.013887 | -0.021921 | -0.0082729 | 0.023008 | 0.055431 | 4.2736e-05 | -0.017266 | 0.0243 | 0.005325 | 0.10249 | 0.073622 | 0.27017 | -0.11342 | 0.13841 | 0.14688 | 0.026066 | 0.13945 | 0.30216 | 0.28704 | -0.12752 | 119.9168 | -0.25914 | 120.0129 | 120.0355 | 0.11875 | -0.28801 | -0.091466 | 119.9027 | -0.22218 | 120.1686 | 120.0563 | 0.15358 | -0.059475 | -0.074588 | 120.1327 | 120.1038 | 120.3004 | 120.0545 | -0.47506 | 120.1697 | 120.3324 | 120.3173 | 120.1771 | -0.48915
5308.7031 | 120.8908 | -120.3094 | 0.40741 | -0.01778 | -0.068487 | 0.038157 | 0.015195 | -0.015497 | 0.0083799 | -0.013887 | -0.021921 | -0.0087001 | 0.023008 | 0.055217 | 0.00025634 | -0.017266 | 0.033457 | 0.005325 | 0.097912 | 0.078201 | 0.27475 | -0.099689 | 0.13841 | 0.1423 | 0.021487 | 0.14403 | 0.29758 | 0.28247 | -0.12752 | 120.2098 | -0.3095 | 120.2922 | 120.3148 | 0.10501 | -0.32921 | -0.13266 | 120.1819 | -0.26338 | 120.4479 | 120.3309 | 0.149 | -0.10983 | -0.12494 | 120.4074 | 120.3876 | 120.5842 | 120.3429 | -0.5071 | 120.4535 | 120.607 | 120.5919 | 120.4517 | -0.53493
5310.4688 | 120.8038 | -120.1492 | 0.4303 | -0.0025182 | -0.068273 | 0.03837 | 0.015622 | -0.015283 | 0.0085935 | -0.021518 | -0.021708 | -0.0087001 | 0.023008 | 0.055431 | -0.00038466 | -0.012688 | 0.033457 | 0.000747 | 0.11165 | 0.078201 | 0.27475 | -0.09511 | 0.13383 | 0.1423 | 0.026066 | 0.13945 | 0.29758 | 0.28704 | -0.12752 | 120.0541 | -0.31865 | 120.1365 | 120.15 | 0.095857 | -0.3521 | -0.15555 | 120.0217 | -0.29085 | 120.2831 | 120.1753 | 0.15358 | -0.13272 | -0.14325 | 120.2609 | 120.2274 | 120.424 | 120.1827 | -0.52541 | 120.2887 | 120.4468 | 120.4363 | 120.2915 | -0.55782
5312.2344 | 120.9503 | -120.2499 | 0.4715 | -0.010149 | -0.068487 | 0.03837 | 0.014981 | -0.015497 | 0.0085935 | -0.021518 | -0.021494 | -0.0089137 | 0.023008 | 0.055217 | 4.2736e-05 | -0.012688 | 0.038035 | 0.000747 | 0.11165 | 0.073622 | 0.27475 | -0.10427 | 0.13841 | 0.13772 | 0.030644 | 0.13487 | 0.29758 | 0.29162 | -0.1321 | 120.1457 | -0.35985 | 120.2373 | 120.2507 | 0.10501 | -0.39787 | -0.19675 | 120.1178 | -0.33663 | 120.3883 | 120.2806 | 0.16274 | -0.17392 | -0.17987 | 120.3616 | 120.3236 | 120.5247 | 120.288 | -0.57576 | 120.3848 | 120.5475 | 120.5416 | 120.3877 | -0.60359
5313.9375 | 121.0007 | -120.2591 | 0.50354 | -0.010149 | -0.068273 | 0.038157 | 0.015195 | -0.015283 | 0.0079525 | -0.013887 | -0.021708 | -0.0082729 | 0.023008 | 0.055431 | 4.2736e-05 | -0.017266 | 0.033457 | 0.005325 | 0.10707 | 0.078201 | 0.27475 | -0.099689 | 0.13841 | 0.1423 | 0.01233 | 0.13945 | 0.29758 | 0.29162 | -0.13668 | 120.1594 | -0.39647 | 120.2418 | 120.2644 | 0.10501 | -0.42534 | -0.22879 | 120.1224 | -0.36409 | 120.3975 | 120.2714 | 0.14901 | -0.20596 | -0.21192 | 120.3662 | 120.3373 | 120.5338 | 120.2926 | -0.60323 | 120.3985 | 120.5567 | 120.5507 | 120.4014 | -0.64022
5315.6875 | 121.1105 | -120.3094 | 0.50812 | -0.010149 | -0.0687 | 0.038157 | 0.015409 | -0.015497 | 0.0079525 | -0.029148 | -0.022135 | -0.0089137 | 0.022794 | 0.055858 | -0.00017086 | -0.017266 | 0.038035 | 0.000747 | 0.10707 | 0.073622 | 0.27017 | -0.10427 | 0.13383 | 0.1423 | 0.030644 | 0.13029 | 0.28842 | 0.28704 | -0.1321 | 120.2052 | -0.40105 | 120.2922 | 120.3102 | 0.10501 | -0.4345 | -0.23795 | 120.1774 | -0.37782 | 120.4433 | 120.3401 | 0.16274 | -0.21969 | -0.22107 | 120.4165 | 120.3831 | 120.5796 | 120.3475 | -0.61239 | 120.4397 | 120.5979 | 120.5965 | 120.4517 | -0.64021
5317.4375 | 121.1105 | -120.3461 | 0.49439 | -0.01778 | -0.068273 | 0.037943 | 0.015409 | -0.015283 | 0.0096619 | -0.029148 | -0.021708 | -0.0084865 | 0.023008 | 0.055858 | -0.00017086 | -0.017266 | 0.028878 | 0.000747 | 0.10249 | 0.069043 | 0.27932 | -0.099689 | 0.13841 | 0.13772 | 0.021487 | 0.13487 | 0.29758 | 0.27789 | -0.1321 | 120.2464 | -0.39189 | 120.3288 | 120.3468 | 0.10044 | -0.42534 | -0.21506 | 120.214 | -0.35951 | 120.4845 | 120.3676 | 0.15358 | -0.19681 | -0.2165 | 120.4486 | 120.4151 | 120.6254 | 120.3749 | -0.59407 | 120.4809 | 120.6436 | 120.624 | 120.4838 | -0.62648
5319.1562 | 121.0876 | -120.3827 | 0.52643 | -0.010149 | -0.068273 | 0.038157 | 0.014981 | -0.015497 | 0.0094483 | -0.021518 | -0.021494 | -0.0082729 | 0.023221 | 0.055645 | 4.2736e-05 | -0.008109 | 0.028878 | -0.003831 | 0.10249 | 0.073622 | 0.27475 | -0.099689 | 0.12925 | 0.15146 | 0.021487 | 0.13487 | 0.293 | 0.27789 | -0.14125 | 120.283 | -0.42394 | 120.3746 | 120.3789 | 0.095858 | -0.45281 | -0.25168 | 120.2414 | -0.39156 | 120.5119 | 120.4042 | 0.16274 | -0.23343 | -0.24854 | 120.4852 | 120.4563 | 120.6574 | 120.4116 | -0.62612 | 120.5176 | 120.6757 | 120.6606 | 120.5341 | -0.66768
5320.8594 | 120.6253 | -3.2364 | 117.3248 | -0.010149 | -0.068273 | 0.037729 | 0.014981 | -0.015497 | 0.0094483 | -0.021518 | -0.021708 | -0.0080591 | 0.023221 | 0.055431 | 4.2736e-05 | -0.021844 | 0.0243 | -0.003831 | 0.088755 | 0.069043 | 0.27017 | -0.10885 | 0.12925 | 0.13772 | 0.026066 | 0.13487 | 0.28384 | 0.27789 | -0.14125 | 3.1275 | -117.2361 | 3.2145 | 3.2326 | 0.10502 | -117.2558 | -117.0547 | 3.0951 | -117.19 | 3.3656 | 3.2625 | 0.16732 | -117.041 | -117.0469 | 3.3251 | 3.3054 | 3.5066 | 3.2607 | -117.4337 | 3.3713 | 3.5202 | 3.5143 | 3.3741 | -117.4661
5322.625 | 120.7352 | -104.9927 | 15.2435 | -0.01778 | -0.068487 | 0.038157 | 0.014768 | -0.015497 | 0.0096619 | -0.0062567 | -0.021708 | -0.0089137 | 0.022794 | 0.055217 | 4.2736e-05 | -0.017266 | 0.033457 | 0.000747 | 0.10249 | 0.078201 | 0.27475 | -0.09511 | 0.13383 | 0.13772 | 0.016908 | 0.12571 | 0.28384 | 0.27331 | -0.13668 | 104.8976 | -15.141 | 104.9754 | 104.9934 | 0.095857 | -15.1653 | -14.9688 | 104.856 | -15.1178 | 105.1265 | 105.0096 | 0.15358 | -14.9597 | -14.9702 | 105.0952 | 105.0709 | 105.2674 | 105.0261 | -15.3386 | 105.1184 | 105.2765 | 105.266 | 105.1304 | -15.3802
5324.3906 | 120.9045 | -105.2948 | 15.1932 | -0.025411 | -0.0687 | 0.038584 | 0.015195 | -0.015283 | 0.0094483 | -0.021518 | -0.021708 | -0.0084865 | 0.023008 | 0.055217 | -0.00017086 | -0.012688 | 0.028878 | -0.008409 | 0.10249 | 0.073622 | 0.27932 | -0.099689 | 0.12925 | 0.13772 | 0.016908 | 0.12571 | 0.27926 | 0.27789 | -0.13668 | 105.1951 | -15.0907 | 105.2821 | 105.2864 | 0.09128 | -15.1196 | -14.9139 | 105.1581 | -15.0675 | 105.4241 | 105.3117 | 0.15358 | -14.9139 | -14.9153 | 105.3973 | 105.3684 | 105.5741 | 105.3237 | -15.2929 | 105.4205 | 105.5741 | 105.5727 | 105.4325 | -15.3299
5326.1562 | 116.4551 | -80.4382 | 35.1379 | -0.010149 | -0.068487 | 0.038157 | 0.015409 | -0.01507 | 0.0094483 | -0.021518 | -0.021708 | -0.0084865 | 0.022794 | 0.055645 | -0.00059826 | -0.021844 | 0.033457 | 0.005325 | 0.10249 | 0.078201 | 0.27017 | -0.099689 | 0.13383 | 0.13772 | 0.016908 | 0.13029 | 0.27926 | 0.27789 | -0.14583 | 80.3385 | -35.0354 | 80.4164 | 80.4436 | 0.10501 | -35.0597 | -34.8678 | 80.2924 | -35.0076 | 80.5721 | 80.4551 | 0.16274 | -34.8587 | -34.8601 | 80.5407 | 80.5164 | 80.7084 | 80.4717 | -35.2376 | 80.5685 | 80.7175 | 80.7161 | 80.576 | -35.2838
5327.8594 | 120.726 | -105.2124 | 15.0101 | -0.0025182 | -0.0687 | 0.038157 | 0.014981 | -0.015497 | 0.0092345 | -0.013887 | -0.021921 | -0.0082729 | 0.022794 | 0.055431 | -0.00059826 | -0.012688 | 0.028878 | 0.009904 | 0.097912 | 0.073622 | 0.27475 | -0.10427 | 0.12467 | 0.13314 | 0.016908 | 0.12571 | 0.27926 | 0.28247 | -0.14583 | 105.1081 | -14.9122 | 105.1997 | 105.2223 | 0.11417 | -14.9364 | -14.7353 | 105.0666 | -14.8844 | 105.3371 | 105.2293 | 0.16274 | -14.7308 | -14.7276 | 105.3103 | 105.286 | 105.4871 | 105.2413 | -15.1143 | 105.3381 | 105.4917 | 105.4949 | 105.3455 | -15.1559
5329.6094 | 120.7489 | -105.3772 | 15.1245 | -0.0025182 | -0.068487 | 0.038157 | 0.014981 | -0.015497 | 0.0092345 | -0.021518 | -0.021708 | -0.0087001 | 0.023008 | 0.055431 | -0.00038466 | -0.008109 | 0.038035 | 0.000747 | 0.097912 | 0.073622 | 0.27932 | -0.10427 | 0.12925 | 0.13772 | 0.003172 | 0.13945 | 0.27926 | 0.27331 | -0.14583 | 105.2729 | -15.0266 | 105.3691 | 105.3779 | 0.10501 | -15.0509 | -14.8452 | 105.2314 | -14.9851 | 105.5064 | 105.3804 | 0.149 | -14.8452 | -14.8512 | 105.4751 | 105.4508 | 105.6565 | 105.4152 | -15.2288 | 105.5166 | 105.6565 | 105.6505 | 105.5149 | -15.2703
5331.3125 | 120.8359 | -105.9631 | 14.6622 | -0.0025182 | -0.068487 | 0.037943 | 0.014981 | -0.015283 | 0.0096619 | -0.013887 | -0.022135 | -0.0084865 | 0.023221 | 0.055431 | -0.00017086 | -0.017266 | 0.028878 | 0.000747 | 0.10249 | 0.069043 | 0.27932 | -0.09511 | 0.13383 | 0.13314 | 0.01233 | 0.12571 | 0.27469 | 0.27789 | -0.13668 | 105.868 | -14.5597 | 105.9459 | 105.9639 | 0.095857 | -14.5931 | -14.3828 | 105.8265 | -14.5365 | 106.097 | 105.9755 | 0.14901 | -14.3875 | -14.3843 | 106.0656 | 106.0322 | 106.2425 | 105.992 | -14.7573 | 106.0888 | 106.2378 | 106.241 | 106.0963 | -14.7988
5333.0938 | 120.9091 | -105.661 | 15.0146 | -0.025411 | -0.068487 | 0.03837 | 0.015195 | -0.015711 | 0.0092345 | -0.029148 | -0.022135 | -0.0084865 | 0.022794 | 0.055645 | -0.00017086 | -0.017266 | 0.0243 | 0.000747 | 0.10249 | 0.073622 | 0.27017 | -0.10427 | 0.13383 | 0.13772 | 0.016908 | 0.11656 | 0.27469 | 0.27331 | -0.14125 | 105.5567 | -14.9122 | 105.6437 | 105.6618 | 0.10501 | -14.941 | -14.7445 | 105.5198 | -14.8981 | 105.7948 | 105.6779 | 0.15816 | -14.74 | -14.7413 | 105.7635 | 105.7346 | 105.9312 | 105.6853 | -15.1189 | 105.7776 | 105.9357 | 105.9343 | 105.7987 | -15.1559
5334.7969 | 120.9961 | -105.1209 | 15.6006 | -0.010149 | -0.0687 | 0.038157 | 0.014981 | -0.015924 | 0.0092345 | -0.013887 | -0.021921 | -0.0084865 | 0.022794 | 0.055645 | -0.00059826 | -0.017266 | 0.038035 | 0.005325 | 0.097912 | 0.073622 | 0.27475 | -0.099689 | 0.12925 | 0.13314 | 0.01233 | 0.13029 | 0.27926 | 0.26873 | -0.14125 | 105.0212 | -15.5027 | 105.1036 | 105.1262 | 0.10501 | -15.527 | -15.3258 | 104.9796 | -15.4703 | 105.2501 | 105.1332 | 0.15358 | -15.3213 | -15.3319 | 105.2188 | 105.1945 | 105.3956 | 105.1589 | -15.7003 | 105.2511 | 105.4001 | 105.3896 | 105.254 | -15.7418
5336.5469 | 120.5658 | -105.5054 | 14.6805 | -0.025411 | -0.0687 | 0.038157 | 0.015195 | -0.015283 | 0.0092345 | -0.013887 | -0.021494 | -0.0084865 | 0.022794 | 0.055431 | -0.00017086 | -0.012688 | 0.028878 | -0.003831 | 0.093333 | 0.078201 | 0.27017 | -0.10427 | 0.12925 | 0.13314 | 0.01233 | 0.12114 | 0.27926 | 0.27331 | -0.14125 | 105.4011 | -14.5871 | 105.4927 | 105.5015 | 0.10044 | -14.6023 | -14.4103 | 105.3641 | -14.5593 | 105.6346 | 105.5177 | 0.15358 | -14.4012 | -14.4072 | 105.5987 | 105.5836 | 105.7755 | 105.5342 | -14.7847 | 105.6265 | 105.7846 | 105.7787 | 105.6385 | -14.8217
5338.3125 | 120.9229 | -106.0272 | 14.534 | -0.010149 | -0.068487 | 0.038157 | 0.015195 | -0.015497 | 0.0092345 | -0.0062567 | -0.021921 | -0.0087001 | 0.022794 | 0.055645 | -0.00017086 | -0.017266 | 0.0243 | 0.000747 | 0.097912 | 0.064464 | 0.26559 | -0.099689 | 0.12925 | 0.12856 | 0.021487 | 0.12571 | 0.27011 | 0.27331 | -0.13668 | 105.9275 | -14.4361 | 106.01 | 106.028 | 0.10044 | -14.4695 | -14.2684 | 105.8905 | -14.4083 | 106.1565 | 106.0487 | 0.15816 | -14.2639 | -14.2607 | 106.1251 | 106.0917 | 106.2928 | 106.0515 | -14.6337 | 106.1529 | 106.2973 | 106.3005 | 106.1558 | -14.6707
5340.0312 | 120.9457 | -106.2653 | 14.4424 | -0.01778 | -0.0687 | 0.038157 | 0.014768 | -0.015497 | 0.0092345 | -0.044409 | -0.022135 | -0.0087001 | 0.023008 | 0.055645 | -0.00017086 | -0.017266 | 0.033457 | -0.003831 | 0.10249 | 0.073622 | 0.27932 | -0.10885 | 0.12467 | 0.13314 | 0.007751 | 0.11656 | 0.27469 | 0.26873 | -0.14125 | 106.1564 | -14.34 | 106.248 | 106.2614 | 0.10502 | -14.3688 | -14.1631 | 106.124 | -14.3259 | 106.3899 | 106.273 | 0.14901 | -14.1678 | -14.1737 | 106.3677 | 106.3389 | 106.5446 | 106.2987 | -14.5513 | 106.3818 | 106.5399 | 106.534 | 106.3984 | -14.5837
5341.7969 | 120.9641 | -106.1874 | 14.6027 | -0.010149 | -0.068487 | 0.037729 | 0.015195 | -0.015711 | 0.0090209 | -0.021518 | -0.021708 | -0.0082729 | 0.023221 | 0.055858 | 4.2736e-05 | -0.008109 | 0.028878 | 0.005325 | 0.093333 | 0.078201 | 0.27475 | -0.09511 | 0.12009 | 0.13314 | 0.01233 | 0.12114 | 0.27926 | 0.26873 | -0.15041 | 106.0923 | -14.5093 | 106.1793 | 106.1928 | 0.10043 | -14.5245 | -14.3279 | 106.037 | -14.4815 | 106.3075 | 106.1998 | 0.16274 | -14.3234 | -14.3339 | 106.2808 | 106.2656 | 106.4622 | 106.2163 | -14.6978 | 106.3086 | 106.4667 | 106.4562 | 106.3206 | -14.7531
5343.5625 | 120.9961 | -106.2241 | 14.6484 | -0.0025182 | -0.068487 | 0.037943 | 0.015195 | -0.015711 | 0.0090209 | -0.029148 | -0.021921 | -0.0084865 | 0.022581 | 0.055217 | 4.2736e-05 | -0.017266 | 0.028878 | 0.000747 | 0.097912 | 0.08278 | 0.27017 | -0.090531 | 0.12009 | 0.13314 | 0.01233 | 0.12114 | 0.27011 | 0.26873 | -0.14125 | 106.1335 | -14.5505 | 106.2068 | 106.2248 | 0.091278 | -14.5657 | -14.3783 | 106.0828 | -14.5273 | 106.3442 | 106.2364 | 0.15358 | -14.3783 | -14.3797 | 106.322 | 106.3068 | 106.4942 | 106.2529 | -14.739 | 106.3452 | 106.4942 | 106.4928 | 106.3572 | -14.7897
5345.3281 | 120.3827 | -5.1956 | 115.7547 | -0.010149 | -0.068487 | 0.03837 | 0.014981 | -0.015924 | 0.0092345 | -0.021518 | -0.021921 | -0.0089137 | 0.023008 | 0.055217 | -0.00017086 | -0.017266 | 0.028878 | 0.000747 | 0.097912 | 0.073622 | 0.26559 | -0.10885 | 0.11552 | 0.1194 | 0.007751 | 0.11198 | 0.27011 | 0.26415 | -0.14125 | 5.0868 | -115.6568 | 5.1784 | 5.1964 | 0.10959 | -115.6811 | -115.4891 | 5.0544 | -115.6427 | 5.3111 | 5.2034 | 0.14901 | -115.4846 | -115.4905 | 5.2935 | 5.2692 | 5.4612 | 5.2245 | -115.8635 | 5.3076 | 5.4657 | 5.4598 | 5.315 | -115.896
5347.0312 | 120.4788 | -4.8203 | 116.1438 | -0.010149 | -0.068273 | 0.038157 | 0.015409 | -0.015283 | 0.0092345 | -0.029148 | -0.021921 | -0.0084865 | 0.023008 | 0.055645 | -0.00081186 | -0.021844 | 0.028878 | -0.003831 | 0.097912 | 0.073622 | 0.26559 | -0.10885 | 0.12009 | 0.1194 | 0.003172 | 0.11656 | 0.27011 | 0.25957 | -0.15041 | 4.7114 | -116.0459 | 4.7984 | 4.8164 | 0.10502 | -116.0702 | -115.8782 | 4.6698 | -116.0272 | 4.9403 | 4.8234 | 0.15358 | -115.8737 | -115.8842 | 4.9182 | 4.8939 | 5.0858 | 4.8491 | -116.2526 | 4.9368 | 5.0904 | 5.0798 | 4.9397 | -116.2942
5348.7969 | 120.9641 | -4.5547 | 116.4825 | -0.0025182 | -0.068487 | 0.037943 | 0.015195 | -0.015283 | 0.0092345 | -0.021518 | -0.021921 | -0.0084865 | 0.023008 | 0.055858 | -0.00017086 | -0.026423 | 0.0243 | 0.000747 | 0.10249 | 0.078201 | 0.27017 | -0.10885 | 0.11552 | 0.1194 | 0.007751 | 0.11656 | 0.26095 | 0.26415 | -0.14583 | 4.4459 | -116.3801 | 4.5283 | 4.5555 | 0.10959 | -116.4043 | -116.2124 | 4.4089 | -116.366 | 4.6703 | 4.5625 | 0.15358 | -116.2216 | -116.2184 | 4.6572 | 4.633 | 4.8249 | 4.579 | -116.5914 | 4.6713 | 4.8157 | 4.8189 | 4.6742 | -116.6284
5350.4844 | 120.3003 | -2.7786 | 118.2083 | -0.01778 | -0.068487 | 0.037943 | 0.015409 | -0.015497 | 0.0090209 | -0.013887 | -0.021921 | -0.0087001 | 0.023221 | 0.055645 | 4.2736e-05 | -0.026423 | 0.0243 | 0.000747 | 0.093333 | 0.073622 | 0.27017 | -0.10427 | 0.12467 | 0.12856 | 0.01233 | 0.11198 | 0.26095 | 0.25957 | -0.15041 | 2.6744 | -118.115 | 2.7522 | 2.7794 | 0.10501 | -118.1347 | -117.9381 | 2.6282 | -118.0963 | 2.9033 | 2.791 | 0.16274 | -117.9474 | -117.9487 | 2.872 | 2.8522 | 3.0488 | 2.8029 | -118.3126 | 2.8906 | 3.0396 | 3.0382 | 2.9072 | -118.3587
5352.2344 | 121.0098 | -2.7008 | 118.3182 | -0.01778 | -0.0687 | 0.037729 | 0.014768 | -0.015283 | 0.0094483 | -0.0062567 | -0.021708 | -0.0087001 | 0.023435 | 0.055431 | -0.00059826 | -0.021844 | 0.019721 | -0.003831 | 0.093333 | 0.069043 | 0.27017 | -0.10427 | 0.11552 | 0.12856 | 0.007751 | 0.12114 | 0.26553 | 0.25957 | -0.15041 | 2.5965 | -118.2248 | 2.679 | 2.697 | 0.10044 | -118.2491 | -118.048 | 2.5504 | -118.197 | 2.8163 | 2.7086 | 0.15816 | -118.0526 | -118.0586 | 2.7941 | 2.7698 | 2.971 | 2.7205 | -118.4224 | 2.8219 | 2.9663 | 2.9604 | 2.8294 | -118.4686
5354 | 120.607 | -71.5073 | 47.7448 | -0.025411 | -0.068487 | 0.037943 | 0.015195 | -0.015711 | 0.0092345 | -0.029148 | -0.021921 | -0.0082729 | 0.023221 | 0.055858 | -0.00017086 | -0.012688 | 0.038035 | 0.000747 | 0.10249 | 0.069043 | 0.27017 | -0.099689 | 0.11094 | 0.13314 | 0.003172 | 0.11198 | 0.26553 | 0.26415 | -0.15041 | 71.4076 | -47.6423 | 71.4946 | 71.508 | 0.10044 | -47.6757 | -47.4746 | 71.3569 | -47.6328 | 71.6182 | 71.5104 | 0.15358 | -47.4792 | -47.4806 | 71.6098 | 71.5763 | 71.7774 | 71.5453 | -47.8444 | 71.6192 | 71.7728 | 71.7714 | 71.6404 | -47.8952
5355.7031 | 120.8588 | -7.1228 | 113.5712 | -0.0025182 | -0.0687 | 0.038157 | 0.014768 | -0.015497 | 0.0092345 | -0.029148 | -0.021708 | -0.0087001 | 0.023008 | 0.055431 | -0.00017086 | -0.021844 | 0.033457 | -0.012988 | 0.093333 | 0.069043 | 0.27932 | -0.099689 | 0.11552 | 0.12856 | 0.003172 | 0.11656 | 0.26095 | 0.25957 | -0.15041 | 7.0231 | -113.4778 | 7.101 | 7.1098 | 0.086701 | -113.5021 | -113.2918 | 6.9724 | -113.4546 | 7.2383 | 7.126 | 0.15358 | -113.3102 | -113.3116 | 7.2161 | 7.1918 | 7.4021 | 7.1563 | -113.6709 | 7.2394 | 7.3838 | 7.3824 | 7.2514 | -113.7216
5357.4688 | 120.8862 | -6.546 | 114.2395 | -0.01778 | -0.068487 | 0.03837 | 0.014981 | -0.015283 | 0.0092345 | -0.029148 | -0.02128 | -0.0087001 | 0.023221 | 0.055217 | -0.00038466 | -0.017266 | 0.0243 | -0.008409 | 0.10249 | 0.073622 | 0.27017 | -0.10885 | 0.12009 | 0.12398 | 0.007751 | 0.11656 | 0.26095 | 0.25957 | -0.14583 | 6.4372 | -114.137 | 6.5288 | 6.5376 | 0.10044 | -114.1659 | -113.9693 | 6.4002 | -114.1229 | 6.6661 | 6.5538 | 0.15358 | -113.9786 | -113.9799 | 6.6485 | 6.6196 | 6.8162 | 6.5703 | -114.3483 | 6.6626 | 6.807 | 6.8056 | 6.67 | -114.3853
5359.2344 | 120.8862 | -5.7175 | 115.21 | -0.0025182 | -0.068487 | 0.038584 | 0.015195 | -0.015283 | 0.0092345 | -0.013887 | -0.021921 | -0.0087001 | 0.023221 | 0.055431 | -0.00017086 | -0.017266 | 0.028878 | 0.000747 | 0.093333 | 0.078201 | 0.27017 | -0.099689 | 0.11094 | 0.11483 | 0.003172 | 0.1074 | 0.25637 | 0.255 | -0.15499 | 5.6178 | -115.1166 | 5.7002 | 5.7182 | 0.10044 | -115.1318 | -114.9398 | 5.5625 | -115.1026 | 5.8284 | 5.7206 | 0.15816 | -114.9536 | -114.955 | 5.8108 | 5.7957 | 5.9876 | 5.7463 | -115.3097 | 5.8249 | 5.9738 | 5.9725 | 5.8323 | -115.365
5360.9375 | 121.0236 | -4.7653 | 116.1163 | -0.010149 | -0.068914 | 0.038157 | 0.014981 | -0.015711 | 0.0090209 | -0.021518 | -0.021921 | -0.0084865 | 0.023221 | 0.055431 | -0.00038466 | -0.021844 | 0.0243 | -0.003831 | 0.084176 | 0.073622 | 0.27017 | -0.10427 | 0.11552 | 0.12398 | -0.005985 | 0.10282 | 0.26095 | 0.255 | -0.15499 | 4.6611 | -116.0322 | 4.7435 | 4.7615 | 0.10044 | -116.0427 | -115.8462 | 4.6103 | -116.0135 | 4.8808 | 4.7593 | 0.14901 | -115.8554 | -115.8613 | 4.8495 | 4.8389 | 5.0355 | 4.7896 | -116.2206 | 4.8681 | 5.0263 | 5.0203 | 4.8893 | -116.2713
5362.7031 | 121.0098 | -4.7333 | 116.2628 | -0.01778 | -0.0687 | 0.038157 | 0.015409 | -0.016138 | 0.0090209 | -0.021518 | -0.021708 | -0.0084865 | 0.023221 | 0.055645 | 4.2736e-05 | -0.026423 | 0.033457 | -0.008409 | 0.10249 | 0.078201 | 0.27475 | -0.10427 | 0.12009 | 0.12398 | -0.001407 | 0.10282 | 0.26095 | 0.255 | -0.14125 | 4.629 | -116.1603 | 4.7069 | 4.7249 | 0.095859 | -116.1846 | -115.9881 | 4.592 | -116.16 | 4.8534 | 4.7319 | 0.13985 | -116.0019 | -116.0078 | 4.8358 | 4.8115 | 5.008 | 4.7667 | -116.3671 | 4.8361 | 4.9942 | 4.9883 | 4.8573 | -116.4041
5364.4688 | 121.0602 | -4.6829 | 116.2949 | -0.01778 | -0.068914 | 0.038157 | 0.014768 | -0.015497 | 0.0094483 | -0.029148 | -0.021921 | -0.0087001 | 0.023435 | 0.055858 | -0.00017086 | -0.021844 | 0.028878 | 0.009904 | 0.097912 | 0.073622 | 0.26559 | -0.10885 | 0.11094 | 0.12398 | 0.007751 | 0.1074 | 0.26095 | 0.255 | -0.15041 | 4.5741 | -116.1969 | 4.6611 | 4.6928 | 0.11875 | -116.2212 | -116.0293 | 4.5325 | -116.1875 | 4.7939 | 4.6907 | 0.15816 | -116.0339 | -116.0399 | 4.7808 | 4.7565 | 4.9485 | 4.7118 | -116.4037 | 4.7903 | 4.9439 | 4.9379 | 4.8069 | -116.4453
5366.2344 | 121.0739 | -4.715 | 116.3177 | -0.010149 | -0.068914 | 0.037943 | 0.015409 | -0.015497 | 0.0092345 | -0.021518 | -0.021921 | -0.0084865 | 0.023008 | 0.055431 | 4.2736e-05 | -0.017266 | 0.0243 | 0.000747 | 0.088755 | 0.078201 | 0.26559 | -0.10427 | 0.11552 | 0.12398 | -0.001407 | 0.10282 | 0.26553 | 0.24584 | -0.15041 | 4.6107 | -116.229 | 4.6977 | 4.7157 | 0.10501 | -116.2395 | -116.0522 | 4.5646 | -116.2149 | 4.8305 | 4.7136 | 0.149 | -116.0522 | -116.0719 | 4.8037 | 4.7932 | 4.9806 | 4.7393 | -116.422 | 4.8178 | 4.9805 | 4.9608 | 4.839 | -116.4682
5367.9375 | 121.0693 | -4.4632 | 116.6428 | -0.01778 | -0.069128 | 0.038157 | 0.015409 | -0.015497 | 0.0092345 | -0.013887 | -0.022135 | -0.0082729 | 0.022794 | 0.055645 | 4.2736e-05 | -0.021844 | 0.028878 | -0.003831 | 0.093333 | 0.069043 | 0.26559 | -0.10427 | 0.11552 | 0.1194 | -0.001407 | 0.1074 | 0.26095 | 0.255 | -0.15499 | 4.3589 | -116.5494 | 4.4414 | 4.4594 | 0.10044 | -116.5737 | -116.3772 | 4.3082 | -116.5354 | 4.5787 | 4.4618 | 0.15358 | -116.3818 | -116.3878 | 4.5565 | 4.5322 | 4.7288 | 4.4921 | -116.747 | 4.5706 | 4.7241 | 4.7182 | 4.5826 | -116.7978
5369.7031 | 121.1884 | -4.3488 | 116.6611 | -0.01778 | -0.068487 | 0.038157 | 0.014981 | -0.015497 | 0.0090209 | -0.036779 | -0.022135 | -0.0084865 | 0.023008 | 0.055858 | -0.00059826 | -0.021844 | 0.0243 | 0.000747 | 0.097912 | 0.069043 | 0.26101 | -0.099689 | 0.12467 | 0.12856 | 0.003172 | 0.10282 | 0.25179 | 0.25042 | -0.15041 | 4.2491 | -116.5632 | 4.3269 | 4.3495 | 0.10044 | -116.592 | -116.4001 | 4.1983 | -116.5583 | 4.4734 | 4.3519 | 0.15358 | -116.4093 | -116.4107 | 4.4467 | 4.4178 | 4.6098 | 4.3731 | -116.7608 | 4.4516 | 4.6005 | 4.5992 | 4.4773 | -116.8115
5371.4062 | 121.2204 | -4.4861 | 116.5924 | -0.0025182 | -0.068487 | 0.037943 | 0.014768 | -0.01507 | 0.0092345 | -0.021518 | -0.021921 | -0.0084865 | 0.022794 | 0.055858 | -0.00038466 | -0.021844 | 0.033457 | 0.000747 | 0.097912 | 0.069043 | 0.27017 | -0.10885 | 0.12467 | 0.11483 | 0.003172 | 0.10282 | 0.26095 | 0.25042 | -0.15499 | 4.3772 | -116.4945 | 4.4642 | 4.4868 | 0.10959 | -116.5234 | -116.3222 | 4.3311 | -116.4896 | 4.6108 | 4.4893 | 0.15816 | -116.3315 | -116.342 | 4.584 | 4.5551 | 4.7563 | 4.5195 | -116.7013 | 4.5889 | 4.747 | 4.7365 | 4.6009 | -116.7474
5373.1719 | 121.1746 | -4.5502 | 116.6382 | -0.01778 | -0.0687 | 0.037943 | 0.015622 | -0.015283 | 0.0092345 | -0.013887 | -0.021708 | -0.0084865 | 0.022794 | 0.055645 | -0.00038466 | -0.026423 | 0.028878 | 0.005325 | 0.11165 | 0.064464 | 0.27017 | -0.10427 | 0.11552 | 0.1194 | -0.001407 | 0.10282 | 0.25179 | 0.25042 | -0.14583 | 4.4459 | -116.5265 | 4.5237 | 4.5555 | 0.10959 | -116.5737 | -116.368 | 4.4043 | -116.5354 | 4.6657 | 4.5488 | 0.14443 | -116.3864 | -116.3878 | 4.6618 | 4.6146 | 4.8203 | 4.579 | -116.7425 | 4.653 | 4.802 | 4.8006 | 4.6696 | -116.784
5374.875 | 121.1334 | -4.4449 | 116.6885 | -0.010149 | -0.0687 | 0.037943 | 0.015195 | -0.015497 | 0.0092345 | -0.013887 | -0.022349 | -0.0084865 | 0.023008 | 0.055645 | -0.00059826 | -0.021844 | 0.028878 | -0.003831 | 0.097912 | 0.078201 | 0.26559 | -0.10427 | 0.11094 | 0.11483 | -0.001407 | 0.10282 | 0.25637 | 0.25042 | -0.15499 | 4.3406 | -116.5906 | 4.423 | 4.4411 | 0.10044 | -116.6103 | -116.423 | 4.2899 | -116.5857 | 4.5558 | 4.4435 | 0.15358 | -116.4322 | -116.4381 | 4.5428 | 4.5231 | 4.7105 | 4.4738 | -116.7928 | 4.5477 | 4.7013 | 4.6953 | 4.5597 | -116.8435
5376.6406 | 121.1792 | -3.8635 | 117.3157 | -0.010149 | -0.068914 | 0.037729 | 0.014981 | -0.01507 | 0.0090209 | -0.021518 | -0.021708 | -0.0087001 | 0.022581 | 0.055431 | -0.00017086 | -0.026423 | 0.019721 | 0.005325 | 0.097912 | 0.073622 | 0.27017 | -0.10885 | 0.10636 | 0.12398 | 0.003172 | 0.10282 | 0.25637 | 0.25042 | -0.15957 | 3.7547 | -117.2178 | 3.8371 | 3.8689 | 0.11417 | -117.2421 | -117.0455 | 3.704 | -117.2129 | 3.9699 | 3.8667 | 0.16274 | -117.0593 | -117.0653 | 3.9614 | 3.9371 | 4.1337 | 3.8832 | -117.4245 | 3.9663 | 4.1199 | 4.1139 | 3.9875 | -117.4752
5378.3906 | 120.4285 | -82.1915 | 38.1546 | -0.010149 | -0.068487 | 0.038157 | 0.015195 | -0.01507 | 0.0092345 | -0.0062567 | -0.021708 | -0.0084865 | 0.022581 | 0.055645 | 4.2736e-05 | -0.012688 | 0.033457 | -0.003831 | 0.10249 | 0.069043 | 0.26559 | -0.099689 | 0.11094 | 0.1194 | 0.003172 | 0.1074 | 0.26553 | 0.255 | -0.15499 | 82.0918 | -38.0521 | 82.1788 | 82.1876 | 0.095858 | -38.0856 | -37.889 | 82.0365 | -38.0472 | 82.3024 | 82.1946 | 0.15816 | -37.8891 | -37.8996 | 82.294 | 82.2605 | 82.4571 | 82.2249 | -38.2543 | 82.2989 | 82.457 | 82.4465 | 82.3109 | -38.3096
5380.1719 | 120.2316 | -10.7208 | 109.7992 | -0.010149 | -0.068914 | 0.03837 | 0.014981 | -0.015283 | 0.0090209 | -0.029148 | -0.021921 | -0.0084865 | 0.023008 | 0.056072 | -0.00017086 | -0.021844 | 0.0243 | -0.008409 | 0.093333 | 0.073622 | 0.27017 | -0.10885 | 0.12009 | 0.12856 | 0.003172 | 0.1074 | 0.25637 | 0.25042 | -0.15499 | 10.612 | -109.7059 | 10.699 | 10.7124 | 0.10044 | -109.7256 | -109.529 | 10.5658 | -109.6918 | 10.8409 | 10.724 | 0.15816 | -109.5428 | -109.5488 | 10.8142 | 10.7944 | 10.991 | 10.7451 | -109.908 | 10.8282 | 10.9772 | 10.9712 | 10.8494 | -109.9542
5381.8594 | 120.9732 | -111.0214 | 9.4254 | -0.0025182 | -0.0687 | 0.03837 | 0.015195 | -0.015283 | 0.0092345 | -0.013887 | -0.021921 | -0.0080591 | 0.023221 | 0.055645 | -0.00017086 | -0.012688 | 0.028878 | 0.000747 | 0.10249 | 0.073622 | 0.27475 | -0.09511 | 0.12009 | 0.13314 | 0.007751 | 0.11198 | 0.26553 | 0.25957 | -0.14125 | 110.9263 | -9.3229 | 111.0087 | 111.0222 | 0.095857 | -9.3517 | -9.1506 | 110.8802 | -9.3134 | 111.1415 | 111.0292 | 0.14901 | -9.1598 | -9.1658 | 111.1239 | 111.095 | 111.2962 | 111.0503 | -9.5205 | 111.1334 | 111.287 | 111.281 | 111.1546 | -9.5666
5383.6094 | 121.0144 | -119.1605 | 1.4923 | -0.01778 | -0.068914 | 0.03837 | 0.015195 | -0.015283 | 0.0085935 | -0.013887 | -0.021921 | -0.0084865 | 0.023435 | 0.056072 | -0.00059826 | -0.017266 | 0.0243 | 0.000747 | 0.097912 | 0.073622 | 0.27475 | -0.090531 | 0.12009 | 0.13314 | -0.001407 | 0.12114 | 0.26095 | 0.26415 | -0.14583 | 119.0699 | -1.3944 | 119.1432 | 119.1612 | 0.091278 | -1.4187 | -1.2176 | 119.0146 | -1.3712 | 119.2806 | 119.1591 | 0.14443 | -1.2314 | -1.2282 | 119.2584 | 119.2341 | 119.4352 | 119.1848 | -1.5828 | 119.2816 | 119.4214 | 119.4246 | 119.2936 | -1.6381
5385.375 | 121.1014 | -119.696 | 0.99792 | -0.0025182 | -0.068914 | 0.038157 | 0.014981 | -0.015283 | 0.0092345 | -0.029148 | -0.021921 | -0.0082729 | 0.023221 | 0.055645 | -0.00017086 | -0.017266 | 0.038035 | 0.000747 | 0.10249 | 0.069043 | 0.27475 | -0.099689 | 0.12467 | 0.13314 | 0.016908 | 0.1074 | 0.25637 | 0.25042 | -0.15499 | 119.5964 | -0.89543 | 119.6788 | 119.6968 | 0.10044 | -0.92888 | -0.72318 | 119.5411 | -0.89052 | 119.8207 | 119.713 | 0.1719 | -0.74155 | -0.74751 | 119.7985 | 119.7651 | 119.9708 | 119.7341 | -1.0976 | 119.8034 | 119.9524 | 119.9465 | 119.8292 | -1.1529
5387.125 | 120.9961 | -0.40741 | 120.5566 | -0.01778 | -0.0687 | 0.037943 | 0.015195 | -0.015497 | 0.0092345 | -0.029148 | -0.021708 | -0.0084865 | 0.023008 | 0.056072 | -0.00038466 | -0.031001 | 0.033457 | 0.005325 | 0.097912 | 0.078201 | 0.27017 | -0.099689 | 0.11552 | 0.12398 | 0.003172 | 0.1074 | 0.26553 | 0.255 | -0.15499 | 0.30772 | -120.4587 | 0.37641 | 0.41274 | 0.10501 | -120.4784 | -120.2865 | 0.25242 | -120.4492 | 0.52292 | 0.41058 | 0.15816 | -120.2911 | -120.3016 | 0.50532 | 0.48561 | 0.67758 | 0.44087 | -120.6563 | 0.51481 | 0.67294 | 0.66241 | 0.53139 | -120.7116
5388.8281 | 121.0556 | -0.3891 | 120.575 | -0.025411 | -0.068914 | 0.038157 | 0.015409 | -0.015711 | 0.0092345 | -0.029148 | -0.021708 | -0.0087001 | 0.022794 | 0.055858 | -0.00017086 | -0.021844 | 0.028878 | 0.000747 | 0.093333 | 0.073622 | 0.26559 | -0.11342 | 0.12009 | 0.1194 | 0.003172 | 0.10282 | 0.26095 | 0.25042 | -0.15499 | 0.27567 | -120.4816 | 0.36725 | 0.38985 | 0.11417 | -120.5013 | -120.3094 | 0.23411 | -120.4721 | 0.50919 | 0.39227 | 0.15816 | -120.314 | -120.3245 | 0.48243 | 0.46272 | 0.65469 | 0.41798 | -120.6884 | 0.49192 | 0.65005 | 0.63952 | 0.5085 | -120.7299
5390.5781 | 121.1151 | -0.38452 | 120.6436 | -0.010149 | -0.0687 | 0.038157 | 0.015409 | -0.015283 | 0.0092345 | -0.021518 | -0.021708 | -0.0084865 | 0.023008 | 0.055858 | -0.00038466 | -0.026423 | 0.033457 | 0.000747 | 0.097912 | 0.078201 | 0.27932 | -0.10885 | 0.11552 | 0.12398 | 0.007751 | 0.1074 | 0.25637 | 0.23668 | -0.14583 | 0.27567 | -120.5457 | 0.3581 | 0.38527 | 0.10959 | -120.5654 | -120.3643 | 0.23869 | -120.5362 | 0.50004 | 0.39227 | 0.15358 | -120.3872 | -120.4069 | 0.48243 | 0.46272 | 0.66385 | 0.41798 | -120.7525 | 0.49192 | 0.64089 | 0.6212 | 0.5085 | -120.7894
5392.3281 | 121.1426 | -0.38452 | 120.6619 | -0.01778 | -0.068914 | 0.037943 | 0.015195 | -0.015711 | 0.0092345 | -0.021518 | -0.021708 | -0.0089137 | 0.023008 | 0.055645 | -0.00038466 | -0.017266 | 0.0243 | -0.003831 | 0.097912 | 0.069043 | 0.26559 | -0.10427 | 0.11552 | 0.11483 | 0.003172 | 0.1074 | 0.25637 | 0.255 | -0.15041 | 0.28025 | -120.564 | 0.36725 | 0.38069 | 0.10044 | -120.5929 | -120.3963 | 0.23411 | -120.5545 | 0.50004 | 0.38769 | 0.15358 | -120.4056 | -120.4069 | 0.48243 | 0.45356 | 0.65011 | 0.40882 | -120.7662 | 0.49192 | 0.64089 | 0.63952 | 0.49935 | -120.8123
5394.0312 | 121.0922 | -0.4303 | 120.7169 | -0.010149 | -0.069128 | 0.03837 | 0.014981 | -0.01507 | 0.0092345 | -0.013887 | -0.021708 | -0.0084865 | 0.023221 | 0.055431 | -0.00017086 | -0.026423 | 0.033457 | -0.003831 | 0.10249 | 0.078201 | 0.27017 | -0.10427 | 0.12009 | 0.1194 | -0.001407 | 0.11198 | 0.25637 | 0.25042 | -0.15499 | 0.32603 | -120.6144 | 0.40388 | 0.42647 | 0.10044 | -120.6387 | -120.4467 | 0.27531 | -120.6049 | 0.55039 | 0.42889 | 0.15358 | -120.4605 | -120.4664 | 0.53279 | 0.5085 | 0.70047 | 0.46376 | -120.8211 | 0.54228 | 0.68667 | 0.68071 | 0.5497 | -120.8718
5395.7812 | 121.2067 | -0.36621 | 120.7031 | -0.01778 | -0.068487 | 0.037943 | 0.014981 | -0.015283 | 0.0092345 | -0.021518 | -0.022135 | -0.0084865 | 0.022794 | 0.055431 | -0.00059826 | -0.026423 | 0.0243 | -0.003831 | 0.093333 | 0.078201 | 0.27017 | -0.099689 | 0.12009 | 0.1194 | 0.003172 | 0.10282 | 0.25637 | 0.24126 | -0.15041 | 0.26652 | -120.6098 | 0.33979 | 0.36238 | 0.095858 | -120.6249 | -120.433 | 0.2158 | -120.6003 | 0.4863 | 0.36938 | 0.15358 | -120.4468 | -120.4619 | 0.45954 | 0.44441 | 0.63638 | 0.39051 | -120.8028 | 0.46903 | 0.62258 | 0.60747 | 0.48562 | -120.8535
5397.5312 | 121.1563 | -0.41657 | 120.7535 | -0.025411 | -0.068487 | 0.03837 | 0.015409 | -0.015497 | 0.0094483 | -0.021518 | -0.02128 | -0.0078455 | 0.022581 | 0.055858 | -0.00081186 | -0.026423 | 0.0243 | 0.005325 | 0.097912 | 0.069043 | 0.27475 | -0.10427 | 0.12009 | 0.12398 | -0.001407 | 0.1074 | 0.25179 | 0.24126 | -0.14583 | 0.3123 | -120.6556 | 0.39014 | 0.42189 | 0.10959 | -120.6844 | -120.4787 | 0.27073 | -120.6461 | 0.53666 | 0.41516 | 0.14443 | -120.5017 | -120.5122 | 0.51448 | 0.48561 | 0.69131 | 0.44087 | -120.8577 | 0.52397 | 0.66836 | 0.65782 | 0.54055 | -120.8993
5399.2969 | 120.3506 | -0.37079 | 119.8334 | -0.010149 | -0.068914 | 0.038157 | 0.015409 | -0.015711 | 0.0088073 | -0.021518 | -0.021708 | -0.0084865 | 0.023008 | 0.055217 | -0.00038466 | -0.031001 | 0.028878 | -0.003831 | 0.10249 | 0.073622 | 0.26559 | -0.09511 | 0.11552 | 0.12398 | 0.003172 | 0.10282 | 0.25637 | 0.25042 | -0.15041 | 0.27568 | -119.7309 | 0.33979 | 0.36696 | 0.091279 | -119.7598 | -119.5678 | 0.22038 | -119.7306 | 0.4863 | 0.37396 | 0.15358 | -119.577 | -119.583 | 0.47328 | 0.44441 | 0.63638 | 0.39967 | -119.9285 | 0.47361 | 0.62716 | 0.62121 | 0.49477 | -119.9838
5401 | 120.6802 | -0.38452 | 120.2637 | -0.0025182 | -0.0687 | 0.038157 | 0.014981 | -0.015497 | 0.0094483 | -0.021518 | -0.021494 | -0.0084865 | 0.023008 | 0.055645 | 0.00025634 | -0.026423 | 0.033457 | -0.003831 | 0.093333 | 0.078201 | 0.27017 | -0.10427 | 0.11552 | 0.12398 | 0.003172 | 0.10282 | 0.25179 | 0.24584 | -0.15041 | 0.28025 | -120.1703 | 0.3581 | 0.38069 | 0.10044 | -120.1855 | -119.9935 | 0.23411 | -120.1608 | 0.50004 | 0.38769 | 0.15358 | -120.0119 | -120.0178 | 0.47785 | 0.46272 | 0.65469 | 0.41798 | -120.3679 | 0.48734 | 0.63631 | 0.63036 | 0.5085 | -120.4141
5402.7656 | 120.7993 | -0.40283 | 120.3781 | -0.010149 | -0.0687 | 0.037729 | 0.015409 | -0.015497 | 0.0094483 | -0.021518 | -0.021921 | -0.0084865 | 0.022794 | 0.055858 | -0.00059826 | -0.031001 | 0.028878 | -0.008409 | 0.10249 | 0.078201 | 0.27017 | -0.10427 | 0.11094 | 0.12398 | 0.007751 | 0.098244 | 0.25637 | 0.24584 | -0.15957 | 0.29856 | -120.2756 | 0.37183 | 0.39442 | 0.095859 | -120.2999 | -120.1079 | 0.24326 | -120.2799 | 0.51377 | 0.41058 | 0.16732 | -120.1217 | -120.1323 | 0.50532 | 0.48103 | 0.673 | 0.43171 | -120.4824 | 0.50108 | 0.6592 | 0.64867 | 0.52682 | -120.5377
5404.5312 | 120.8725 | -0.39825 | 120.4559 | -0.0025182 | -0.068914 | 0.037729 | 0.014981 | -0.015283 | 0.0094483 | -0.021518 | -0.021921 | -0.0084865 | 0.022794 | 0.055858 | -0.00038466 | -0.026423 | 0.019721 | -0.003831 | 0.10249 | 0.078201 | 0.26559 | -0.099689 | 0.11552 | 0.1194 | 0.003172 | 0.1074 | 0.25179 | 0.24126 | -0.15499 | 0.29856 | -120.3534 | 0.37183 | 0.39442 | 0.095858 | -120.3777 | -120.1903 | 0.24326 | -120.3485 | 0.51377 | 0.40143 | 0.15816 | -120.2041 | -120.2147 | 0.50074 | 0.47646 | 0.66384 | 0.41797 | -120.5556 | 0.50565 | 0.65005 | 0.63951 | 0.51766 | -120.6109
5406.2969 | 120.8633 | -0.41657 | 120.5246 | -0.010149 | -0.069128 | 0.03837 | 0.014981 | -0.015497 | 0.0094483 | -0.021518 | -0.021708 | -0.0082729 | 0.023008 | 0.055645 | -0.00017086 | -0.026423 | 0.028878 | 0.000747 | 0.097912 | 0.08278 | 0.27017 | -0.10427 | 0.11094 | 0.1194 | 0.003172 | 0.098244 | 0.25179 | 0.24126 | -0.15499 | 0.3123 | -120.4267 | 0.39014 | 0.41731 | 0.10501 | -120.4418 | -120.2544 | 0.26157 | -120.4264 | 0.5275 | 0.41974 | 0.15816 | -120.2728 | -120.2833 | 0.51448 | 0.49935 | 0.68673 | 0.44544 | -120.6289 | 0.51481 | 0.66836 | 0.65782 | 0.53597 | -120.6796
5408.0469 | 120.9778 | -0.37994 | 120.5658 | -0.010149 | -0.068914 | 0.037943 | 0.014981 | -0.015283 | 0.0092345 | -0.029148 | -0.022135 | -0.0082729 | 0.023008 | 0.055645 | 4.2736e-05 | -0.017266 | 0.028878 | 0.000747 | 0.093333 | 0.073622 | 0.27475 | -0.10427 | 0.11094 | 0.12398 | -0.001407 | 0.10282 | 0.25179 | 0.255 | -0.15041 | 0.27568 | -120.4725 | 0.36268 | 0.38069 | 0.10501 | -120.4922 | -120.2911 | 0.22953 | -120.463 | 0.49088 | 0.37854 | 0.149 | -120.314 | -120.3108 | 0.47328 | 0.45357 | 0.65469 | 0.40882 | -120.6701 | 0.48277 | 0.63174 | 0.63494 | 0.50393 | -120.7162
5409.75 | 121.0876 | -0.36163 | 120.6116 | -0.0025182 | -0.068914 | 0.038157 | 0.014768 | -0.015283 | 0.0090209 | -0.013887 | -0.021494 | -0.0080591 | 0.023008 | 0.056072 | -0.00038466 | -0.021844 | 0.028878 | -0.003831 | 0.10249 | 0.069043 | 0.27475 | -0.10427 | 0.11094 | 0.1194 | -0.010564 | 0.093665 | 0.25179 | 0.24126 | -0.15957 | 0.25736 | -120.5091 | 0.33979 | 0.3578 | 0.10044 | -120.5425 | -120.3368 | 0.20206 | -120.5179 | 0.47257 | 0.35107 | 0.14901 | -120.3598 | -120.3703 | 0.46412 | 0.43068 | 0.63638 | 0.39051 | -120.7158 | 0.4553 | 0.61343 | 0.60289 | 0.48104 | -120.7711
5411.5156 | 121.1288 | -0.3891 | 120.6436 | -0.010149 | -0.0687 | 0.038157 | 0.014981 | -0.015497 | 0.0088073 | -0.029148 | -0.021494 | -0.0084865 | 0.023221 | 0.056072 | -0.00017086 | -0.021844 | 0.0243 | 0.000747 | 0.10249 | 0.073622 | 0.27475 | -0.10427 | 0.11552 | 0.1194 | -0.005985 | 0.098244 | 0.25179 | 0.24126 | -0.15499 | 0.28483 | -120.5411 | 0.36725 | 0.38985 | 0.10501 | -120.57 | -120.3689 | 0.23411 | -120.5454 | 0.50461 | 0.38311 | 0.14901 | -120.3918 | -120.4024 | 0.49159 | 0.46272 | 0.66384 | 0.4134 | -120.7479 | 0.48734 | 0.64089 | 0.63036 | 0.5085 | -120.7986
5413.2812 | 121.2204 | -0.35706 | 120.6573 | -0.01778 | -0.069128 | 0.037943 | 0.014768 | -0.015497 | 0.0090209 | -0.0062567 | -0.021708 | -0.0087001 | 0.022794 | 0.055858 | -0.00017086 | -0.026423 | 0.028878 | -0.003831 | 0.093333 | 0.073622 | 0.27017 | -0.11342 | 0.11094 | 0.1194 | -0.005985 | 0.10282 | 0.25179 | 0.24584 | -0.15499 | 0.24363 | -120.564 | 0.33063 | 0.35323 | 0.10959 | -120.5837 | -120.3872 | 0.20206 | -120.5545 | 0.46799 | 0.35107 | 0.14901 | -120.4056 | -120.4115 | 0.45039 | 0.43068 | 0.62722 | 0.38593 | -120.7708 | 0.45988 | 0.60885 | 0.60289 | 0.47646 | -120.8123
5415 | 121.1334 | -0.40741 | 120.7443 | -0.01778 | -0.068914 | 0.038157 | 0.015195 | -0.015711 | 0.0090209 | -0.013887 | -0.021921 | -0.0084865 | 0.022794 | 0.055645 | -0.00038466 | -0.021844 | 0.0243 | 0.000747 | 0.097912 | 0.073622 | 0.27017 | -0.099689 | 0.11094 | 0.12398 | -0.001407 | 0.093665 | 0.25637 | 0.24584 | -0.15957 | 0.30772 | -120.6464 | 0.38557 | 0.40816 | 0.10044 | -120.6707 | -120.4742 | 0.24784 | -120.6507 | 0.51835 | 0.406 | 0.15816 | -120.488 | -120.4985 | 0.50532 | 0.48103 | 0.67758 | 0.43171 | -120.844 | 0.50107 | 0.66378 | 0.65325 | 0.53139 | -120.9039
5416.75 | 121.1746 | -0.39825 | 120.7123 | -0.010149 | -0.0687 | 0.037943 | 0.015409 | -0.015497 | 0.0092345 | -0.021518 | -0.021708 | -0.0087001 | 0.022794 | 0.055858 | -0.00038466 | -0.021844 | 0.019721 | 0.000747 | 0.088755 | 0.064464 | 0.26559 | -0.10427 | 0.11094 | 0.11483 | 0.003172 | 0.093665 | 0.25179 | 0.24584 | -0.15041 | 0.29399 | -120.6235 | 0.37641 | 0.399 | 0.10501 | -120.6478 | -120.4467 | 0.24784 | -120.6186 | 0.50919 | 0.40143 | 0.15358 | -120.4605 | -120.4664 | 0.48701 | 0.46272 | 0.66384 | 0.41797 | -120.8165 | 0.49192 | 0.65005 | 0.64409 | 0.51308 | -120.8627
5418.5 | 121.2341 | -0.39825 | 120.7535 | -0.010149 | -0.068914 | 0.037943 | 0.015195 | -0.015283 | 0.0092345 | -0.021518 | -0.021708 | -0.0080591 | 0.023008 | 0.056072 | -0.00038466 | -0.021844 | 0.038035 | 0.000747 | 0.10249 | 0.073622 | 0.27017 | -0.10885 | 0.11552 | 0.1194 | -0.001407 | 0.098244 | 0.24721 | 0.24126 | -0.15957 | 0.28941 | -120.651 | 0.37641 | 0.399 | 0.10959 | -120.6799 | -120.4833 | 0.23868 | -120.6552 | 0.51377 | 0.39685 | 0.15816 | -120.5063 | -120.5122 | 0.50074 | 0.47188 | 0.66842 | 0.43629 | -120.8623 | 0.4965 | 0.64547 | 0.63951 | 0.51766 | -120.913
5420.2812 | 121.2708 | -0.37079 | 120.7352 | -0.01778 | -0.0687 | 0.038157 | 0.015622 | -0.015497 | 0.0090209 | -0.029148 | -0.021708 | -0.0080591 | 0.022794 | 0.056072 | -0.00038466 | -0.026423 | 0.033457 | -0.008409 | 0.093333 | 0.073622 | 0.27017 | -0.10885 | 0.10636 | 0.10109 | -0.001407 | 0.093665 | 0.23806 | 0.2321 | -0.16873 | 0.26194 | -120.6418 | 0.34437 | 0.36238 | 0.10044 | -120.6615 | -120.465 | 0.20206 | -120.6415 | 0.47715 | 0.36938 | 0.16732 | -120.4971 | -120.5031 | 0.46412 | 0.44441 | 0.64096 | 0.40425 | -120.844 | 0.46445 | 0.60885 | 0.60289 | 0.47188 | -120.9039
5422.0469 | 121.225 | -0.40283 | 120.7947 | -0.010149 | -0.068914 | 0.03837 | 0.014981 | -0.015497 | 0.0094483 | -0.029148 | -0.021708 | -0.0084865 | 0.023008 | 0.055645 | -0.00038466 | -0.031001 | 0.028878 | -0.003831 | 0.097912 | 0.069043 | 0.27017 | -0.099689 | 0.10636 | 0.11025 | -0.010564 | 0.098244 | 0.24264 | 0.23668 | -0.16415 | 0.30314 | -120.6968 | 0.37183 | 0.399 | 0.095858 | -120.7256 | -120.5245 | 0.23868 | -120.6964 | 0.50919 | 0.39227 | 0.15358 | -120.552 | -120.558 | 0.50074 | 0.47187 | 0.673 | 0.43171 | -120.8944 | 0.50108 | 0.64547 | 0.63951 | 0.51308 | -120.9588
5423.75 | 121.312 | -0.3891 | 120.7764 | -0.01778 | -0.068914 | 0.03837 | 0.014981 | -0.015711 | 0.0092345 | -0.029148 | -0.021921 | -0.0084865 | 0.022794 | 0.055858 | -0.00017086 | -0.017266 | 0.028878 | 0.005325 | 0.10249 | 0.073622 | 0.26559 | -0.10885 | 0.10178 | 0.11025 | -0.005985 | 0.084508 | 0.24264 | 0.24126 | -0.16415 | 0.28025 | -120.6739 | 0.37183 | 0.39442 | 0.11417 | -120.7027 | -120.5108 | 0.22495 | -120.6919 | 0.49088 | 0.38311 | 0.15816 | -120.5337 | -120.5351 | 0.49159 | 0.46272 | 0.65469 | 0.41798 | -120.8852 | 0.47361 | 0.63174 | 0.63036 | 0.49935 | -120.9405
5425.5156 | 121.3531 | -0.37079 | 120.7855 | -0.01778 | -0.069128 | 0.037943 | 0.015195 | -0.015711 | 0.0090209 | -0.021518 | -0.022135 | -0.0087001 | 0.023008 | 0.055858 | -0.00038466 | -0.017266 | 0.033457 | 0.005325 | 0.093333 | 0.069043 | 0.27475 | -0.099689 | 0.11094 | 0.10567 | -0.019721 | 0.093665 | 0.24264 | 0.23668 | -0.16415 | 0.2711 | -120.6922 | 0.35352 | 0.37611 | 0.10501 | -120.7165 | -120.5108 | 0.20664 | -120.6919 | 0.48173 | 0.35107 | 0.14443 | -120.5429 | -120.5488 | 0.46412 | 0.43983 | 0.64553 | 0.40425 | -120.8852 | 0.46445 | 0.61343 | 0.60747 | 0.47646 | -120.9497
5427.2812 | 121.2479 | -0.4303 | 120.8405 | -0.01778 | -0.069341 | 0.038157 | 0.014768 | -0.015924 | 0.0092345 | -0.021518 | -0.021921 | -0.0082729 | 0.022794 | 0.056072 | -0.00017086 | -0.021844 | 0.019721 | 0.005325 | 0.10249 | 0.073622 | 0.27475 | -0.10427 | 0.10178 | 0.10567 | -0.005985 | 0.084508 | 0.23806 | 0.23668 | -0.16415 | 0.32603 | -120.738 | 0.40845 | 0.43562 | 0.10959 | -120.7668 | -120.5657 | 0.26615 | -120.7559 | 0.53208 | 0.42431 | 0.15816 | -120.6024 | -120.6038 | 0.53279 | 0.50392 | 0.70504 | 0.45002 | -120.9447 | 0.51481 | 0.66836 | 0.66698 | 0.53597 | -121.0046
5429.0312 | 121.3028 | -0.42114 | 120.8633 | -0.01778 | -0.069128 | 0.038157 | 0.014981 | -0.015497 | 0.0094483 | -0.013887 | -0.021708 | -0.0080591 | 0.022794 | 0.055858 | -0.00038466 | -0.017266 | 0.0243 | 0.000747 | 0.10707 | 0.073622 | 0.27017 | -0.10885 | 0.10178 | 0.11025 | -0.015143 | 0.084508 | 0.23806 | 0.23668 | -0.15957 | 0.3123 | -120.7563 | 0.40388 | 0.42189 | 0.10959 | -120.7897 | -120.5932 | 0.26157 | -120.7788 | 0.52292 | 0.406 | 0.14443 | -120.6253 | -120.6267 | 0.52821 | 0.49477 | 0.69131 | 0.44544 | -120.9722 | 0.50565 | 0.6592 | 0.65782 | 0.53139 | -121.0229
5430.7344 | 121.3348 | -0.4303 | 120.8817 | -0.010149 | -0.068914 | 0.038157 | 0.014981 | -0.015497 | 0.0085935 | -0.021518 | -0.021921 | -0.0087001 | 0.022581 | 0.055858 | -0.00038466 | -0.026423 | 0.033457 | 0.000747 | 0.097912 | 0.078201 | 0.27017 | -0.10427 | 0.10636 | 0.10109 | -0.010564 | 0.089087 | 0.23348 | 0.22752 | -0.16415 | 0.32603 | -120.7837 | 0.40388 | 0.43105 | 0.10501 | -120.8035 | -120.6115 | 0.26615 | -120.7926 | 0.53666 | 0.41973 | 0.15358 | -120.6482 | -120.6541 | 0.52821 | 0.5085 | 0.70047 | 0.46376 | -120.9859 | 0.51938 | 0.66378 | 0.65782 | 0.53139 | -121.0458
5432.4844 | 121.344 | -0.42572 | 120.8908 | -0.010149 | -0.0687 | 0.037943 | 0.014768 | -0.015711 | 0.0090209 | -0.021518 | -0.021708 | -0.0087001 | 0.023008 | 0.055858 | -0.00081186 | -0.017266 | 0.0243 | 0.000747 | 0.10249 | 0.078201 | 0.27475 | -0.10885 | 0.10178 | 0.11025 | -0.015143 | 0.093665 | 0.23348 | 0.23668 | -0.16873 | 0.31687 | -120.7883 | 0.40845 | 0.42647 | 0.10959 | -120.8126 | -120.6161 | 0.25699 | -120.7971 | 0.5275 | 0.41058 | 0.15358 | -120.6573 | -120.6541 | 0.52821 | 0.50392 | 0.70047 | 0.45002 | -120.9997 | 0.51938 | 0.6592 | 0.6624 | 0.53597 | -121.0595
5434.1875 | 121.4035 | -0.39825 | 120.8862 | -0.01778 | -0.069128 | 0.03837 | 0.014768 | -0.015711 | 0.0090209 | -0.029148 | -0.021708 | -0.0087001 | 0.022581 | 0.056072 | -0.00059826 | -0.021844 | 0.033457 | 0.000747 | 0.097912 | 0.078201 | 0.27475 | -0.10885 | 0.097201 | 0.10567 | -0.010564 | 0.084508 | 0.23348 | 0.22752 | -0.16415 | 0.28941 | -120.7883 | 0.37641 | 0.399 | 0.10959 | -120.808 | -120.6115 | 0.23411 | -120.8017 | 0.49545 | 0.38769 | 0.15358 | -120.6528 | -120.6587 | 0.49617 | 0.47646 | 0.673 | 0.43171 | -120.9951 | 0.48276 | 0.63173 | 0.62578 | 0.50392 | -121.0504
5435.9531 | 121.4035 | -0.44403 | 120.8633 | -0.01778 | -0.069128 | 0.037943 | 0.015195 | -0.015497 | 0.0092345 | -0.021518 | -0.021494 | -0.0084865 | 0.023008 | 0.056072 | -0.00017086 | -0.012688 | 0.0243 | 0.005325 | 0.097912 | 0.073622 | 0.27017 | -0.10885 | 0.10636 | 0.11483 | -0.015143 | 0.084508 | 0.23806 | 0.22295 | -0.16415 | 0.33518 | -120.7654 | 0.43134 | 0.44936 | 0.11417 | -120.7897 | -120.5932 | 0.27988 | -120.7788 | 0.55039 | 0.42889 | 0.14901 | -120.6253 | -120.6404 | 0.54194 | 0.51765 | 0.7142 | 0.46833 | -120.9722 | 0.52854 | 0.68209 | 0.66698 | 0.55886 | -121.0275
5437.7188 | 121.3852 | -0.44403 | 120.9366 | -0.01778 | -0.069341 | 0.03837 | 0.014768 | -0.015497 | 0.0090209 | -0.029148 | -0.021921 | -0.0087001 | 0.022794 | 0.056499 | -0.00038466 | -0.026423 | 0.019721 | 0.000747 | 0.10249 | 0.073622 | 0.27017 | -0.10885 | 0.10178 | 0.10567 | -0.015143 | 0.07993 | 0.23806 | 0.23668 | -0.16873 | 0.33518 | -120.8341 | 0.41761 | 0.44478 | 0.10959 | -120.863 | -120.6664 | 0.2753 | -120.8567 | 0.54581 | 0.42889 | 0.15358 | -120.6985 | -120.6999 | 0.54652 | 0.51765 | 0.7142 | 0.46375 | -121.0454 | 0.52396 | 0.68209 | 0.68071 | 0.5497 | -121.1053
5439.4062 | 121.4172 | -0.43945 | 120.9412 | -0.0025182 | -0.068914 | 0.037516 | 0.015195 | -0.015711 | 0.0088073 | -0.021518 | -0.021921 | -0.0082729 | 0.022794 | 0.056072 | -0.00017086 | -0.017266 | 0.028878 | 0.005325 | 0.093333 | 0.073622 | 0.27017 | -0.10427 | 0.10636 | 0.10109 | -0.010564 | 0.093665 | 0.23348 | 0.2321 | -0.17331 | 0.33518 | -120.8478 | 0.42219 | 0.44478 | 0.10959 | -120.8675 | -120.671 | 0.26615 | -120.8475 | 0.54581 | 0.42889 | 0.16274 | -120.7077 | -120.7091 | 0.53279 | 0.51307 | 0.70962 | 0.46833 | -121.0454 | 0.53312 | 0.67293 | 0.67156 | 0.54054 | -121.1145
5441.1719 | 121.4539 | -0.41199 | 120.9457 | -0.010149 | -0.069555 | 0.037943 | 0.014981 | -0.015711 | 0.0088073 | -0.0062567 | -0.021708 | -0.0082729 | 0.023008 | 0.056072 | -0.00059826 | -0.021844 | 0.028878 | -0.003831 | 0.093333 | 0.078201 | 0.27017 | -0.11342 | 0.10178 | 0.11025 | -0.005985 | 0.07993 | 0.23348 | 0.23668 | -0.16873 | 0.29856 | -120.8524 | 0.39014 | 0.40816 | 0.10959 | -120.8675 | -120.6756 | 0.24326 | -120.8658 | 0.51377 | 0.406 | 0.16274 | -120.7123 | -120.7091 | 0.50532 | 0.49019 | 0.68215 | 0.44087 | -121.0592 | 0.49192 | 0.64547 | 0.64867 | 0.52224 | -121.1145
5442.9375 | 121.3989 | -0.44861 | 120.9686 | -0.010149 | -0.069341 | 0.037943 | 0.014981 | -0.015497 | 0.0088073 | -0.021518 | -0.021921 | -0.0084865 | 0.022581 | 0.056286 | -0.00059826 | -0.026423 | 0.028878 | 0.000747 | 0.10249 | 0.078201 | 0.27475 | -0.10885 | 0.10636 | 0.11483 | -0.015143 | 0.089087 | 0.23348 | 0.2321 | -0.16873 | 0.33976 | -120.8661 | 0.42219 | 0.44936 | 0.10959 | -120.8904 | -120.6939 | 0.27988 | -120.8795 | 0.55497 | 0.43346 | 0.15358 | -120.7351 | -120.7365 | 0.5511 | 0.52681 | 0.72335 | 0.47749 | -121.0775 | 0.5377 | 0.68209 | 0.68071 | 0.56344 | -121.1374
5444.7188 | 121.4264 | -0.45776 | 120.9732 | -0.010149 | -0.069128 | 0.03837 | 0.014768 | -0.015283 | 0.0092345 | -0.021518 | -0.022135 | -0.0084865 | 0.023008 | 0.056072 | -0.00059826 | -0.021844 | 0.033457 | 0.005325 | 0.093333 | 0.078201 | 0.27475 | -0.10885 | 0.10178 | 0.11025 | -0.010564 | 0.07993 | 0.2289 | 0.23668 | -0.16873 | 0.34892 | -120.8799 | 0.43592 | 0.46309 | 0.11417 | -120.895 | -120.6985 | 0.28904 | -120.8933 | 0.55954 | 0.4472 | 0.15816 | -120.7443 | -120.7365 | 0.5511 | 0.53597 | 0.73251 | 0.49122 | -121.0821 | 0.53769 | 0.68666 | 0.69444 | 0.56801 | -121.1419
5446.4844 | 121.5546 | -0.40283 | 120.9549 | -0.010149 | -0.068914 | 0.037729 | 0.014768 | -0.015497 | 0.0092345 | -0.021518 | -0.021708 | -0.0084865 | 0.022794 | 0.055858 | -0.00059826 | -0.017266 | 0.038035 | -0.003831 | 0.10249 | 0.078201 | 0.27017 | -0.09511 | 0.10178 | 0.11025 | -0.010564 | 0.07993 | 0.22432 | 0.22295 | -0.16873 | 0.30772 | -120.8524 | 0.38557 | 0.399 | 0.091279 | -120.8767 | -120.6847 | 0.2341 | -120.875 | 0.50461 | 0.39227 | 0.15816 | -120.7306 | -120.7319 | 0.50532 | 0.48103 | 0.673 | 0.44087 | -121.05 | 0.48276 | 0.62715 | 0.62578 | 0.51308 | -121.1236
5448.1875 | 120.5429 | -119.2291 | 0.86517 | -0.01778 | -0.069341 | 0.038157 | 0.014554 | -0.015497 | 0.0088073 | -0.0062567 | -0.021921 | -0.0082729 | 0.022581 | 0.056072 | -0.00017086 | -0.012688 | 0.028878 | 0.000747 | 0.093333 | 0.073622 | 0.27475 | -0.099689 | 0.10636 | 0.11025 | -0.005985 | 0.084508 | 0.23806 | 0.22752 | -0.15957 | 119.1294 | -0.77184 | 119.2164 | 119.2299 | 0.10044 | -0.79155 | -0.59043 | 119.0696 | -0.78066 | 119.3355 | 119.2231 | 0.15358 | -0.62711 | -0.63765 | 119.3225 | 119.3027 | 119.5039 | 119.258 | -0.96486 | 119.3136 | 119.4672 | 119.4566 | 119.3394 | -1.0247
5449.8906 | 121.0876 | -120.1447 | 0.72784 | -0.010149 | -0.069341 | 0.037943 | 0.014768 | -0.015497 | 0.0092345 | -0.0062567 | -0.021494 | -0.0082729 | 0.022581 | 0.055858 | -0.00038466 | -0.012688 | 0.038035 | 0.009904 | 0.10249 | 0.073622 | 0.27932 | -0.099689 | 0.10178 | 0.11483 | -0.010564 | 0.089087 | 0.23806 | 0.2321 | -0.16873 | 120.045 | -0.62535 | 120.132 | 120.1546 | 0.10959 | -0.65422 | -0.44852 | 119.9759 | -0.63876 | 120.2464 | 120.1341 | 0.15816 | -0.48979 | -0.49574 | 120.2471 | 120.2183 | 120.424 | 120.1827 | -0.82753 | 120.2337 | 120.3827 | 120.3768 | 120.2595 | -0.89657
5451.6406 | 121.1792 | -120.369 | 0.6546 | -0.010149 | -0.069128 | 0.037943 | 0.015195 | -0.01507 | 0.0088073 | -0.0062567 | -0.021921 | -0.0087001 | 0.022581 | 0.055645 | -0.00038466 | -0.017266 | 0.028878 | 0.005325 | 0.10249 | 0.073622 | 0.27475 | -0.10885 | 0.10636 | 0.11025 | -0.010564 | 0.084508 | 0.24264 | 0.22752 | -0.15957 | 120.2601 | -0.55211 | 120.3517 | 120.3743 | 0.11417 | -0.58098 | -0.37986 | 120.2094 | -0.57009 | 120.4753 | 120.3584 | 0.14901 | -0.41197 | -0.42708 | 120.4714 | 120.4426 | 120.6437 | 120.3978 | -0.76345 | 120.4535 | 120.6116 | 120.5965 | 120.4792 | -0.81417
5453.4062 | 121.3577 | -120.4102 | 0.6134 | -0.010149 | -0.069128 | 0.037943 | 0.014768 | -0.015497 | 0.0092345 | -0.029148 | -0.021708 | -0.0084865 | 0.022794 | 0.056286 | -0.00038466 | -0.017266 | 0.033457 | 0.000747 | 0.10707 | 0.08278 | 0.27932 | -0.10885 | 0.10636 | 0.10567 | -0.019721 | 0.084508 | 0.2289 | 0.22752 | -0.16873 | 120.3013 | -0.50633 | 120.3929 | 120.4109 | 0.10959 | -0.53062 | -0.33408 | 120.2414 | -0.5289 | 120.5165 | 120.3904 | 0.14901 | -0.3845 | -0.38588 | 120.5172 | 120.4929 | 120.6895 | 120.4436 | -0.72225 | 120.4947 | 120.6391 | 120.6377 | 120.5158 | -0.78213
5455.1875 | 121.3806 | -120.1218 | 0.9613 | -0.010149 | -0.068914 | 0.037729 | 0.014981 | -0.015497 | 0.0092345 | -0.013887 | -0.021921 | -0.0082729 | 0.023008 | 0.055858 | -0.00038466 | -0.021844 | 0.033457 | 0.000747 | 0.10249 | 0.073622 | 0.2839 | -0.09511 | 0.10636 | 0.11483 | -0.010564 | 0.093665 | 0.23348 | 0.22752 | -0.16415 | 120.0267 | -0.85881 | 120.0999 | 120.1225 | 0.095857 | -0.88768 | -0.6774 | 119.9576 | -0.86764 | 120.2281 | 120.1112 | 0.15358 | -0.72783 | -0.73378 | 120.2243 | 120.1954 | 120.4057 | 120.1552 | -1.0564 | 120.2154 | 120.3552 | 120.3493 | 120.2366 | -1.1255
5456.8906 | 121.2982 | -120.1035 | 1.0574 | -0.01778 | -0.069555 | 0.037943 | 0.014981 | -0.015924 | 0.0090209 | -0.029148 | -0.021708 | -0.0082729 | 0.022794 | 0.055858 | -0.00038466 | -0.017266 | 0.038035 | 0.005325 | 0.10249 | 0.08278 | 0.27932 | -0.099689 | 0.10178 | 0.1194 | -0.010564 | 0.089087 | 0.23348 | 0.22295 | -0.16873 | 120.0038 | -0.95494 | 120.0862 | 120.1088 | 0.10501 | -0.97465 | -0.77811 | 119.9347 | -0.96835 | 120.2052 | 120.0929 | 0.15816 | -0.82395 | -0.83449 | 120.2059 | 120.1862 | 120.3828 | 120.1415 | -1.1571 | 120.1925 | 120.3369 | 120.3264 | 120.2229 | -1.2262
5458.6406 | 121.4447 | -120.4834 | 0.66834 | -0.010149 | -0.069341 | 0.037943 | 0.014981 | -0.015497 | 0.0088073 | -0.013887 | -0.021494 | -0.0084865 | 0.023008 | 0.056072 | -0.00038466 | -0.012688 | 0.033457 | 0.005325 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.10178 | 0.10567 | -0.005985 | 0.084508 | 0.23806 | 0.2321 | -0.16415 | 120.3791 | -0.56585 | 120.4707 | 120.4887 | 0.10959 | -0.59471 | -0.38901 | 120.3192 | -0.58383 | 120.5852 | 120.4774 | 0.15816 | -0.43028 | -0.43623 | 120.5859 | 120.557 | 120.7627 | 120.5169 | -0.7726 | 120.5679 | 120.7215 | 120.7155 | 120.5891 | -0.83248
5460.3438 | 121.3852 | -120.5658 | 0.69122 | -0.010149 | -0.069128 | 0.03837 | 0.014981 | -0.015497 | 0.0090209 | -0.021518 | -0.022135 | -0.0084865 | 0.022581 | 0.056072 | -0.00038466 | -0.021844 | 0.033457 | 0.005325 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.10178 | 0.10567 | -0.005985 | 0.084508 | 0.22432 | 0.2321 | -0.16415 | 120.4615 | -0.58873 | 120.544 | 120.5711 | 0.10959 | -0.6176 | -0.4119 | 120.4016 | -0.60672 | 120.6676 | 120.5598 | 0.15816 | -0.4669 | -0.45912 | 120.6683 | 120.6394 | 120.8451 | 120.5993 | -0.79549 | 120.6503 | 120.7901 | 120.7979 | 120.6715 | -0.85537
5462.125 | 121.4676 | -120.5429 | 0.66376 | -0.0025182 | -0.069341 | 0.037729 | 0.014981 | -0.015711 | 0.0090209 | -0.029148 | -0.022135 | -0.0087001 | 0.023008 | 0.056286 | 4.2736e-05 | -0.021844 | 0.038035 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | -0.099689 | 0.10636 | 0.11025 | -0.010564 | 0.089087 | 0.23348 | 0.22752 | -0.16873 | 120.4432 | -0.55669 | 120.5211 | 120.5437 | 0.10044 | -0.59014 | -0.38443 | 120.3742 | -0.57467 | 120.6493 | 120.5323 | 0.15816 | -0.43028 | -0.43623 | 120.65 | 120.6165 | 120.8222 | 120.5809 | -0.76345 | 120.632 | 120.7764 | 120.7704 | 120.6532 | -0.83249
5463.8281 | 121.4081 | -120.5338 | 0.737 | -0.010149 | -0.068914 | 0.037729 | 0.014981 | -0.015497 | 0.0088073 | -0.021518 | -0.021921 | -0.0087001 | 0.022794 | 0.056286 | -0.00059826 | -0.012688 | 0.038035 | 0.005325 | 0.10249 | 0.078201 | 0.27475 | -0.10885 | 0.10636 | 0.10567 | -0.005985 | 0.089087 | 0.23806 | 0.2321 | -0.16873 | 120.4249 | -0.63451 | 120.5211 | 120.5391 | 0.11417 | -0.6588 | -0.46225 | 120.365 | -0.64791 | 120.6401 | 120.5278 | 0.16274 | -0.49894 | -0.5049 | 120.6362 | 120.612 | 120.8085 | 120.5718 | -0.84585 | 120.6228 | 120.7718 | 120.7659 | 120.6394 | -0.90573
5465.5938 | 121.5271 | -120.6116 | 0.61798 | -0.01778 | -0.069128 | 0.037943 | 0.014768 | -0.015711 | 0.0090209 | -0.029148 | -0.021921 | -0.0084865 | 0.023008 | 0.056072 | -0.00059826 | -0.012688 | 0.033457 | 0.009904 | 0.097912 | 0.073622 | 0.27932 | -0.10427 | 0.10636 | 0.11025 | -0.015143 | 0.084508 | 0.23348 | 0.22295 | -0.15957 | 120.5073 | -0.52007 | 120.5989 | 120.6215 | 0.11417 | -0.54436 | -0.33866 | 120.452 | -0.53347 | 120.7179 | 120.5964 | 0.14443 | -0.3845 | -0.39504 | 120.7095 | 120.6852 | 120.8909 | 120.645 | -0.72225 | 120.6961 | 120.8451 | 120.8345 | 120.7218 | -0.77755
5467.2969 | 121.4722 | -120.6345 | 0.65002 | -0.010149 | -0.069128 | 0.037943 | 0.015195 | -0.015711 | 0.0090209 | -0.013887 | -0.021921 | -0.0087001 | 0.022794 | 0.055645 | -0.00038466 | -0.017266 | 0.038035 | 0.005325 | 0.10707 | 0.078201 | 0.2839 | -0.099689 | 0.10636 | 0.11483 | -0.015143 | 0.084508 | 0.22432 | 0.22752 | -0.16415 | 120.5348 | -0.54296 | 120.6172 | 120.6398 | 0.10501 | -0.57182 | -0.36612 | 120.4703 | -0.56552 | 120.7408 | 120.6193 | 0.14901 | -0.4257 | -0.4225 | 120.7415 | 120.7127 | 120.9184 | 120.6725 | -0.74971 | 120.719 | 120.8588 | 120.862 | 120.7493 | -0.81417
5469.0625 | 120.9915 | -102.8915 | 17.5964 | -0.01778 | -0.069555 | 0.037729 | 0.014554 | -0.015711 | 0.0088073 | -0.029148 | -0.021921 | -0.0082729 | 0.022581 | 0.056072 | -0.00038466 | -0.021844 | 0.028878 | 0.014482 | 0.10249 | 0.073622 | 0.27932 | -0.099689 | 0.10178 | 0.11025 | -0.015143 | 0.07993 | 0.2289 | 0.2321 | -0.16415 | 102.7919 | -17.4939 | 102.8697 | 102.906 | 0.11417 | -17.5228 | -17.3171 | 102.7274 | -17.5165 | 102.9933 | 102.8764 | 0.14901 | -17.3675 | -17.3643 | 102.994 | 102.9652 | 103.1709 | 102.9204 | -17.6961 | 102.9715 | 103.1204 | 103.1236 | 103.0018 | -17.7606
5470.8281 | 121.2891 | -105.1987 | 15.7516 | -0.01778 | -0.069341 | 0.037943 | 0.01434 | -0.015711 | 0.0092345 | -0.029148 | -0.021494 | -0.0082729 | 0.023008 | 0.055858 | -0.00038466 | -0.012688 | 0.028878 | 0.000747 | 0.11165 | 0.087359 | 0.27475 | -0.10427 | 0.10636 | 0.11483 | -0.005985 | 0.089087 | 0.23348 | 0.2321 | -0.15957 | 105.0944 | -15.64 | 105.186 | 105.1994 | 0.10501 | -15.6643 | -15.4769 | 105.0391 | -15.6626 | 105.305 | 105.1927 | 0.15358 | -15.5182 | -15.5195 | 105.3103 | 105.286 | 105.4734 | 105.2275 | -15.8559 | 105.2878 | 105.4321 | 105.4308 | 105.3135 | -15.9112
5472.5938 | 121.3943 | -104.6906 | 16.3239 | -0.0025182 | -0.069341 | 0.037729 | 0.014981 | -0.015497 | 0.0092345 | -0.013887 | -0.021708 | -0.0084865 | 0.022794 | 0.056286 | -0.00038466 | -0.012688 | 0.038035 | 0.005325 | 0.097912 | 0.078201 | 0.27932 | -0.10427 | 0.11094 | 0.11483 | -0.010564 | 0.084508 | 0.24264 | 0.22752 | -0.16415 | 104.5863 | -16.2259 | 104.6779 | 104.6959 | 0.10959 | -16.2457 | -16.0445 | 104.5264 | -16.2393 | 104.8015 | 104.68 | 0.15358 | -16.0812 | -16.0963 | 104.7885 | 104.7688 | 104.9699 | 104.7286 | -16.4281 | 104.7751 | 104.9332 | 104.9181 | 104.8054 | -16.488
5474.3594 | 121.4813 | -104.1275 | 16.9373 | -0.010149 | -0.069555 | 0.038157 | 0.014768 | -0.015497 | 0.0092345 | -0.021518 | -0.021708 | -0.0084865 | 0.023008 | 0.056072 | -0.00059826 | -0.017266 | 0.033457 | 0.005325 | 0.10249 | 0.08278 | 0.27475 | -0.10427 | 0.10178 | 0.11025 | -0.015143 | 0.075351 | 0.2289 | 0.22752 | -0.16415 | 104.0232 | -16.8348 | 104.1102 | 104.1328 | 0.10959 | -16.8545 | -16.6625 | 103.9634 | -16.8619 | 104.2293 | 104.1124 | 0.14901 | -16.7084 | -16.7097 | 104.23 | 104.2103 | 104.4022 | 104.161 | -17.0415 | 104.2029 | 104.3564 | 104.355 | 104.2378 | -17.1014
5476.125 | 121.4035 | -104.6173 | 16.571 | -0.010149 | -0.069341 | 0.037943 | 0.014768 | -0.015711 | 0.0088073 | -0.013887 | -0.021708 | -0.0087001 | 0.023221 | 0.056286 | -0.00017086 | -0.012688 | 0.028878 | 0.009904 | 0.097912 | 0.078201 | 0.27932 | -0.099689 | 0.10636 | 0.11025 | -0.010564 | 0.089087 | 0.2289 | 0.22752 | -0.16415 | 104.5176 | -16.4731 | 104.6046 | 104.6272 | 0.10959 | -16.4928 | -16.2917 | 104.4532 | -16.482 | 104.7237 | 104.6067 | 0.15358 | -16.3421 | -16.3435 | 104.7152 | 104.6955 | 104.8966 | 104.6462 | -16.6707 | 104.7064 | 104.8462 | 104.8448 | 104.7276 | -16.7352
5477.8438 | 121.5225 | -105.0659 | 16.0629 | -0.01778 | -0.069341 | 0.037943 | 0.014554 | -0.015283 | 0.0092345 | -0.021518 | -0.02128 | -0.0084865 | 0.023008 | 0.055858 | -0.00059826 | -0.021844 | 0.033457 | 0.005325 | 0.10707 | 0.073622 | 0.27475 | -0.10427 | 0.11094 | 0.11025 | -0.005985 | 0.089087 | 0.23806 | 0.22752 | -0.16415 | 104.9616 | -15.9559 | 105.0441 | 105.0712 | 0.10959 | -15.9893 | -15.7882 | 104.9018 | -15.9738 | 105.1769 | 105.0599 | 0.15816 | -15.8249 | -15.8354 | 105.173 | 105.1395 | 105.3407 | 105.0994 | -16.1672 | 105.155 | 105.304 | 105.2934 | 105.1762 | -16.2271
5479.6094 | 121.5637 | -105.5923 | 15.6006 | -0.01778 | -0.069555 | 0.037943 | 0.014981 | -0.015711 | 0.0090209 | -0.013887 | -0.02128 | -0.0082729 | 0.022794 | 0.056499 | -0.00038466 | -0.021844 | 0.038035 | 0.005325 | 0.10707 | 0.08278 | 0.27475 | -0.10885 | 0.11552 | 0.11025 | -0.010564 | 0.084508 | 0.23348 | 0.2321 | -0.15957 | 105.4835 | -15.4935 | 105.5705 | 105.5977 | 0.11417 | -15.5178 | -15.3258 | 105.4328 | -15.5161 | 105.7079 | 105.5818 | 0.14901 | -15.3671 | -15.3685 | 105.6994 | 105.6751 | 105.8671 | 105.6304 | -15.7094 | 105.6769 | 105.8258 | 105.8244 | 105.7026 | -15.7602
5481.375 | 121.463 | -104.9561 | 16.3055 | -0.010149 | -0.069555 | 0.038157 | 0.014768 | -0.015497 | 0.0090209 | -0.029148 | -0.021494 | -0.0084865 | 0.022794 | 0.055858 | -0.00017086 | -0.026423 | 0.028878 | 0.005325 | 0.10707 | 0.078201 | 0.27017 | -0.099689 | 0.11094 | 0.11025 | -0.010564 | 0.089087 | 0.22432 | 0.22752 | -0.16415 | 104.8564 | -16.1985 | 104.9296 | 104.9614 | 0.10501 | -16.2273 | -16.0354 | 104.7919 | -16.2165 | 105.067 | 104.9455 | 0.15358 | -16.0812 | -16.078 | 105.0631 | 105.0343 | 105.2262 | 104.9849 | -16.4052 | 105.0451 | 105.1804 | 105.1836 | 105.0663 | -16.4697
5483.1562 | 121.582 | -104.1 | 17.1249 | -0.010149 | -0.069341 | 0.038157 | 0.015195 | -0.015711 | 0.0090209 | -0.036779 | -0.021708 | -0.0082729 | 0.023221 | 0.056286 | -0.00017086 | -0.012688 | 0.028878 | 0.000747 | 0.10249 | 0.078201 | 0.27932 | -0.099689 | 0.10178 | 0.11025 | -0.010564 | 0.084508 | 0.23348 | 0.22295 | -0.15957 | 104.0003 | -17.0224 | 104.0873 | 104.1008 | 0.10044 | -17.0467 | -16.8456 | 103.9405 | -17.0404 | 104.2018 | 104.0895 | 0.14901 | -16.8915 | -16.902 | 104.2025 | 104.1782 | 104.3794 | 104.1289 | -17.2246 | 104.1845 | 104.3335 | 104.323 | 104.2103 | -17.2845
5484.8594 | 121.55 | -102.626 | 18.5852 | -0.010149 | -0.069341 | 0.038157 | 0.014554 | -0.015497 | 0.0090209 | -0.021518 | -0.021708 | -0.0089137 | 0.022794 | 0.056072 | -0.00038466 | -0.017266 | 0.0243 | 0.000747 | 0.10249 | 0.069043 | 0.27932 | -0.10427 | 0.10636 | 0.11025 | -0.005985 | 0.07993 | 0.23348 | 0.2321 | -0.15957 | 102.5218 | -18.4827 | 102.6088 | 102.6268 | 0.10501 | -18.5162 | -18.3059 | 102.4665 | -18.5053 | 102.7324 | 102.6201 | 0.15358 | -18.3517 | -18.3531 | 102.7285 | 102.6951 | 102.9054 | 102.6503 | -18.6895 | 102.706 | 102.8595 | 102.8581 | 102.7363 | -18.7448
5486.625 | 121.2021 | -16.9327 | 104.5166 | -0.01778 | -0.069128 | 0.03837 | 0.015195 | -0.015711 | 0.0092345 | -0.013887 | -0.021921 | -0.0084865 | 0.022794 | 0.056072 | -0.00038466 | -0.012688 | 0.033457 | 0.014482 | 0.097912 | 0.08278 | 0.27475 | -0.099689 | 0.10636 | 0.10109 | -0.015143 | 0.075351 | 0.2289 | 0.2321 | -0.16415 | 16.833 | -104.4187 | 16.92 | 16.9472 | 0.11417 | -104.4338 | -104.2419 | 16.7685 | -104.4413 | 17.039 | 16.9175 | 0.14901 | -104.2877 | -104.2845 | 17.0306 | 17.0155 | 17.2074 | 16.9661 | -104.6163 | 17.008 | 17.1616 | 17.1648 | 17.0338 | -104.6808
5488.3906 | 120.9183 | -10.6064 | 110.8383 | -0.0025182 | -0.069128 | 0.038157 | 0.014554 | -0.015497 | 0.0094483 | -0.021518 | -0.021708 | -0.0084865 | 0.022581 | 0.056286 | -0.00038466 | -0.017266 | 0.0243 | 0.005325 | 0.10249 | 0.078201 | 0.27475 | -0.10427 | 0.11094 | 0.10567 | -0.010564 | 0.084508 | 0.23348 | 0.23668 | -0.16415 | 10.5021 | -110.7358 | 10.5891 | 10.6117 | 0.10959 | -110.7601 | -110.5636 | 10.4422 | -110.7538 | 10.7173 | 10.5958 | 0.15358 | -110.6048 | -110.6016 | 10.7089 | 10.6846 | 10.8811 | 10.6307 | -110.9426 | 10.6909 | 10.8399 | 10.8431 | 10.7121 | -111.0025
5490.1562 | 121.3394 | -9.4849 | 111.9278 | -0.010149 | -0.069555 | 0.037943 | 0.014981 | -0.015711 | 0.0090209 | -0.021518 | -0.022135 | -0.0082729 | 0.022794 | 0.056286 | -0.00038466 | -0.021844 | 0.019721 | 0.005325 | 0.10249 | 0.078201 | 0.2839 | -0.10885 | 0.10636 | 0.10567 | -0.005985 | 0.089087 | 0.2289 | 0.22752 | -0.16415 | 9.376 | -111.8253 | 9.463 | 9.4902 | 0.11417 | -111.8496 | -111.6439 | 9.3207 | -111.8387 | 9.5912 | 9.4789 | 0.15816 | -111.6989 | -111.7003 | 9.5874 | 9.5631 | 9.7688 | 9.5046 | -112.0366 | 9.5739 | 9.7138 | 9.7124 | 9.5905 | -112.0919
5491.8594 | 121.4996 | -9.0775 | 112.3718 | -0.010149 | -0.069341 | 0.038157 | 0.014981 | -0.015497 | 0.0088073 | -0.021518 | -0.021921 | -0.0084865 | 0.022581 | 0.056072 | -0.00017086 | -0.021844 | 0.028878 | 0.005325 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.10178 | 0.10567 | -0.015143 | 0.07993 | 0.2289 | 0.21837 | -0.16873 | 8.9732 | -112.2693 | 9.0556 | 9.0828 | 0.10959 | -112.2982 | -112.0925 | 8.9087 | -112.2919 | 9.1792 | 9.0623 | 0.15358 | -112.1429 | -112.1535 | 9.1799 | 9.1511 | 9.3568 | 9.1063 | -112.4761 | 9.1574 | 9.3064 | 9.2958 | 9.1831 | -112.5406
5493.6094 | 121.4722 | -8.7891 | 112.6785 | -0.01778 | -0.069341 | 0.038157 | 0.014981 | -0.015711 | 0.0092345 | -0.021518 | -0.021494 | -0.0084865 | 0.023221 | 0.056286 | -0.00059826 | -0.017266 | 0.028878 | 0.000747 | 0.10249 | 0.073622 | 0.27475 | -0.10427 | 0.10636 | 0.10109 | -0.001407 | 0.089087 | 0.23348 | 0.22752 | -0.16873 | 8.6848 | -112.576 | 8.7718 | 8.7898 | 0.10501 | -112.6049 | -112.4038 | 8.6203 | -112.5894 | 8.8954 | 8.7877 | 0.16732 | -112.445 | -112.451 | 8.8916 | 8.8627 | 9.0638 | 8.8179 | -112.7828 | 8.8781 | 9.0225 | 9.0166 | 8.8902 | -112.8473
5495.3906 | 121.5958 | -9.4711 | 111.9598 | -0.01778 | -0.069341 | 0.037943 | 0.014768 | -0.015497 | 0.0090209 | -0.021518 | -0.022135 | -0.0084865 | 0.022794 | 0.056072 | -0.00059826 | -0.021844 | 0.038035 | 0.009904 | 0.10249 | 0.078201 | 0.27475 | -0.10427 | 0.10636 | 0.11025 | -0.015143 | 0.07993 | 0.22432 | 0.22752 | -0.16873 | 9.3669 | -111.8573 | 9.4493 | 9.481 | 0.11417 | -111.8816 | -111.6851 | 9.3024 | -111.8799 | 9.5775 | 9.456 | 0.15358 | -111.7355 | -111.7323 | 9.5736 | 9.5493 | 9.7459 | 9.5092 | -112.0641 | 9.5511 | 9.6955 | 9.6987 | 9.5814 | -112.1286
5497.0938 | 121.5912 | -8.8028 | 112.619 | -0.01778 | -0.069341 | 0.037943 | 0.014554 | -0.015497 | 0.0090209 | -0.021518 | -0.021708 | -0.0084865 | 0.022581 | 0.056286 | -0.00059826 | -0.012688 | 0.033457 | 0.005325 | 0.097912 | 0.078201 | 0.27932 | -0.10885 | 0.11094 | 0.10567 | -0.005985 | 0.07993 | 0.2289 | 0.22295 | -0.16415 | 8.6939 | -112.5211 | 8.7901 | 8.8081 | 0.11417 | -112.5408 | -112.3397 | 8.6386 | -112.5391 | 8.9137 | 8.7968 | 0.15816 | -112.3901 | -112.3961 | 8.9007 | 8.881 | 9.0821 | 8.8363 | -112.7279 | 8.8827 | 9.0317 | 9.0257 | 8.9085 | -112.7832
5498.8594 | 121.582 | -8.67 | 112.793 | -0.025411 | -0.069341 | 0.037943 | 0.014554 | -0.015283 | 0.0090209 | -0.029148 | -0.021708 | -0.0087001 | 0.023008 | 0.056072 | -0.00038466 | -0.017266 | 0.033457 | -0.008409 | 0.097912 | 0.078201 | 0.27017 | -0.10427 | 0.10178 | 0.11483 | -0.005985 | 0.084508 | 0.23348 | 0.22752 | -0.16415 | 8.5658 | -112.6951 | 8.6528 | 8.6616 | 0.095859 | -112.7148 | -112.5228 | 8.5059 | -112.7085 | 8.7718 | 8.6641 | 0.15816 | -112.5595 | -112.5654 | 8.768 | 8.7482 | 8.9402 | 8.7035 | -112.8972 | 8.7546 | 8.9035 | 8.8976 | 8.7849 | -112.9571
5500.625 | 121.6507 | -8.4274 | 113.0127 | -0.010149 | -0.069555 | 0.038157 | 0.014981 | -0.015283 | 0.0092345 | -0.021518 | -0.021708 | -0.0084865 | 0.023008 | 0.056072 | -0.00017086 | -0.017266 | 0.028878 | -0.003831 | 0.097912 | 0.073622 | 0.27475 | -0.099689 | 0.10636 | 0.11025 | -0.005985 | 0.089087 | 0.22432 | 0.21837 | -0.16415 | 8.3277 | -112.9148 | 8.4102 | 8.4236 | 0.095858 | -112.9391 | -112.7379 | 8.2633 | -112.9236 | 8.5338 | 8.4214 | 0.15816 | -112.7884 | -112.7943 | 8.5253 | 8.5011 | 8.7022 | 8.4563 | -113.1124 | 8.5165 | 8.6518 | 8.6458 | 8.5377 | -113.1768
5502.3906 | 121.6324 | -8.4503 | 112.999 | -0.01778 | -0.069341 | 0.037943 | 0.014768 | -0.015711 | 0.0092345 | -0.013887 | -0.021708 | -0.0080591 | 0.023221 | 0.055431 | -0.00081186 | -0.017266 | 0.028878 | -0.003831 | 0.10707 | 0.078201 | 0.2839 | -0.11342 | 0.10178 | 0.11025 | -0.005985 | 0.07993 | 0.22432 | 0.21837 | -0.15957 | 8.3369 | -112.8919 | 8.4331 | 8.4465 | 0.10959 | -112.9208 | -112.7151 | 8.2907 | -112.919 | 8.5521 | 8.4443 | 0.15358 | -112.7746 | -112.7806 | 8.5574 | 8.5285 | 8.7342 | 8.4792 | -113.1124 | 8.5302 | 8.6746 | 8.6687 | 8.5606 | -113.1585
5504.1562 | 121.582 | -8.1894 | 113.3469 | -0.01778 | -0.069341 | 0.037729 | 0.014768 | -0.015924 | 0.0090209 | -0.021518 | -0.021921 | -0.0084865 | 0.022794 | 0.056286 | -0.00059826 | -0.026423 | 0.0243 | 0.005325 | 0.097912 | 0.078201 | 0.27017 | -0.099689 | 0.10636 | 0.10567 | -0.010564 | 0.07993 | 0.24721 | 0.22752 | -0.16873 | 8.0897 | -113.249 | 8.163 | 8.1947 | 0.10501 | -113.2687 | -113.0767 | 8.0207 | -113.2669 | 8.2957 | 8.1788 | 0.15816 | -113.0996 | -113.1193 | 8.2873 | 8.2676 | 8.4596 | 8.2137 | -113.4466 | 8.2693 | 8.4366 | 8.4169 | 8.2951 | -113.5156
5505.8594 | 121.7056 | -8.1345 | 113.3194 | -0.010149 | -0.069555 | 0.037943 | 0.014554 | -0.015283 | 0.0092345 | -0.021518 | -0.021708 | -0.0087001 | 0.022794 | 0.056072 | -0.00059826 | -0.021844 | 0.033457 | 0.000747 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.10636 | 0.11025 | -0.015143 | 0.089087 | 0.22432 | 0.22295 | -0.16415 | 8.0302 | -113.2169 | 8.1126 | 8.1352 | 0.10501 | -113.2458 | -113.0401 | 7.9703 | -113.2303 | 8.2408 | 8.1193 | 0.14901 | -113.0951 | -113.0965 | 8.237 | 8.2081 | 8.4138 | 8.1679 | -113.4237 | 8.2235 | 8.3588 | 8.3574 | 8.2447 | -113.4835
5507.625 | 121.5958 | -7.9376 | 113.5849 | -0.010149 | -0.069341 | 0.037516 | 0.014768 | -0.015283 | 0.0090209 | -0.029148 | -0.021921 | -0.0087001 | 0.022794 | 0.056072 | -0.00038466 | -0.021844 | 0.028878 | 0.000747 | 0.097912 | 0.078201 | 0.2839 | -0.10885 | 0.10636 | 0.10567 | -0.010564 | 0.07993 | 0.21974 | 0.22295 | -0.16415 | 7.8288 | -113.487 | 7.9158 | 7.9384 | 0.10959 | -113.5067 | -113.301 | 7.7735 | -113.505 | 8.044 | 7.9271 | 0.15358 | -113.3652 | -113.362 | 8.0355 | 8.0158 | 8.2215 | 7.9665 | -113.6937 | 8.0176 | 8.1574 | 8.1606 | 8.0433 | -113.749
5509.3281 | 121.6095 | -7.8049 | 113.7497 | -0.0025182 | -0.069128 | 0.037943 | 0.014981 | -0.015711 | 0.0092345 | -0.013887 | -0.021708 | -0.0084865 | 0.022794 | 0.056072 | -0.00059826 | -0.021844 | 0.033457 | -0.003831 | 0.11165 | 0.078201 | 0.27932 | -0.10885 | 0.097201 | 0.11025 | -0.010564 | 0.07993 | 0.22432 | 0.21379 | -0.16415 | 7.696 | -113.638 | 7.783 | 7.801 | 0.10502 | -113.6715 | -113.4704 | 7.6407 | -113.6698 | 7.9021 | 7.7943 | 0.15358 | -113.5254 | -113.5359 | 7.9165 | 7.8831 | 8.0842 | 7.8383 | -113.8585 | 7.8848 | 8.0292 | 8.0187 | 7.9151 | -113.9138
5511.1094 | 121.6003 | -7.7408 | 113.8687 | -0.025411 | -0.069128 | 0.037729 | 0.014768 | -0.015711 | 0.0090209 | -0.021518 | -0.021921 | -0.0082729 | 0.022794 | 0.056286 | -0.00059826 | -0.017266 | 0.028878 | 0.000747 | 0.10249 | 0.08278 | 0.27475 | -0.10885 | 0.10636 | 0.11025 | -0.010564 | 0.089087 | 0.22432 | 0.2321 | -0.15957 | 7.6319 | -113.7662 | 7.7235 | 7.7415 | 0.10959 | -113.7859 | -113.594 | 7.5812 | -113.7796 | 7.8471 | 7.7302 | 0.14901 | -113.6444 | -113.6366 | 7.8433 | 7.8236 | 8.0155 | 7.7697 | -113.9776 | 7.8299 | 7.9651 | 7.9729 | 7.851 | -114.0283
5512.8125 | 121.7514 | -7.6859 | 113.7955 | -0.01778 | -0.069128 | 0.037943 | 0.014768 | -0.015283 | 0.0092345 | -0.029148 | -0.021708 | -0.0080591 | 0.022581 | 0.056072 | -0.00017086 | -0.021844 | 0.033457 | -0.003831 | 0.10707 | 0.073622 | 0.27475 | -0.10885 | 0.11094 | 0.10567 | -0.015143 | 0.07993 | 0.22432 | 0.22295 | -0.16873 | 7.577 | -113.6884 | 7.664 | 7.682 | 0.10502 | -113.7218 | -113.5207 | 7.5171 | -113.7155 | 7.7968 | 7.6707 | 0.15358 | -113.5711 | -113.5725 | 7.7929 | 7.7595 | 7.9606 | 7.7193 | -113.9043 | 7.7658 | 7.9102 | 7.9088 | 7.7915 | -113.9642
5514.5781 | 121.6324 | -7.5943 | 114.0335 | -0.010149 | -0.069769 | 0.038157 | 0.014981 | -0.015711 | 0.0092345 | -0.013887 | -0.021708 | -0.0082729 | 0.022794 | 0.056072 | -0.00059826 | -0.017266 | 0.028878 | -0.003831 | 0.10249 | 0.08278 | 0.27932 | -0.11342 | 0.10636 | 0.11025 | -0.015143 | 0.07993 | 0.2289 | 0.22752 | -0.17788 | 7.4809 | -113.931 | 7.577 | 7.5905 | 0.10959 | -113.9507 | -113.7542 | 7.4164 | -113.9536 | 7.7007 | 7.5792 | 0.16274 | -113.8046 | -113.806 | 7.6968 | 7.6771 | 7.8736 | 7.6232 | -114.1469 | 7.6742 | 7.8232 | 7.8218 | 7.7045 | -114.2114
5516.3438 | 121.637 | -7.4799 | 114.1113 | -0.01778 | -0.069341 | 0.037943 | 0.014768 | -0.015497 | 0.0088073 | -0.013887 | -0.021494 | -0.0084865 | 0.022581 | 0.056286 | -0.00081186 | -0.017266 | 0.033457 | 0.000747 | 0.10249 | 0.073622 | 0.27017 | -0.10885 | 0.10636 | 0.11025 | -0.005985 | 0.07993 | 0.21974 | 0.22295 | -0.17331 | 7.371 | -114.0088 | 7.4626 | 7.4806 | 0.10959 | -114.0377 | -113.8412 | 7.3066 | -114.0314 | 7.5862 | 7.4739 | 0.16732 | -113.8916 | -113.8884 | 7.5823 | 7.5535 | 7.75 | 7.5133 | -114.2202 | 7.5598 | 7.6996 | 7.7028 | 7.5901 | -114.2846
5518.1094 | 121.6965 | -7.4158 | 114.1251 | -0.0025182 | -0.069128 | 0.037943 | 0.014768 | -0.015283 | 0.0088073 | -0.013887 | -0.021921 | -0.0084865 | 0.022794 | 0.056072 | -0.00059826 | -0.021844 | 0.033457 | -0.003831 | 0.097912 | 0.08278 | 0.27932 | -0.10427 | 0.10178 | 0.11025 | -0.005985 | 0.07993 | 0.21974 | 0.22295 | -0.16873 | 7.3115 | -114.0271 | 7.3939 | 7.4119 | 0.10044 | -114.0423 | -113.8457 | 7.247 | -114.0451 | 7.5175 | 7.4098 | 0.16274 | -113.9053 | -113.9021 | 7.5137 | 7.4986 | 7.6951 | 7.4492 | -114.2293 | 7.4957 | 7.6355 | 7.6387 | 7.526 | -114.2938
5519.875 | 121.6919 | -7.3975 | 114.2075 | -0.010149 | -0.069341 | 0.037943 | 0.014768 | -0.015497 | 0.0090209 | -0.029148 | -0.022135 | -0.0084865 | 0.022581 | 0.056286 | -0.00059826 | -0.031001 | 0.028878 | 0.000747 | 0.097912 | 0.073622 | 0.27475 | -0.10885 | 0.10178 | 0.11025 | -0.0243 | 0.07993 | 0.22432 | 0.21379 | -0.16415 | 7.2886 | -114.1095 | 7.3665 | 7.3982 | 0.10959 | -114.1338 | -113.9327 | 7.2333 | -114.1275 | 7.4992 | 7.3732 | 0.13985 | -113.9831 | -113.9937 | 7.4954 | 7.4711 | 7.6722 | 7.4263 | -114.3163 | 7.4774 | 7.6218 | 7.6112 | 7.5077 | -114.3716
5521.6562 | 121.0968 | -5.0446 | 115.9241 | -0.025411 | -0.069128 | 0.037943 | 0.014554 | -0.015924 | 0.0090209 | -0.013887 | -0.021921 | -0.0082729 | 0.022794 | 0.056286 | -0.00059826 | -0.026423 | 0.033457 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | -0.10885 | 0.097201 | 0.096512 | -0.015143 | 0.070773 | 0.21974 | 0.21379 | -0.16873 | 4.9357 | -115.817 | 5.0181 | 5.0499 | 0.11417 | -115.8504 | -115.6447 | 4.8758 | -115.8533 | 5.1418 | 5.0294 | 0.15358 | -115.7043 | -115.7103 | 5.1516 | 5.1182 | 5.3239 | 5.078 | -116.0329 | 5.1153 | 5.2643 | 5.2583 | 5.1411 | -116.0928
5523.4219 | 121.3486 | -3.772 | 117.4118 | -0.01778 | -0.069555 | 0.038157 | 0.014981 | -0.015283 | 0.0090209 | -0.029148 | -0.021708 | -0.0082729 | 0.022581 | 0.056286 | -0.00038466 | -0.021844 | 0.028878 | 0.000747 | 0.097912 | 0.073622 | 0.27932 | -0.10427 | 0.097201 | 0.11025 | -0.019721 | 0.075351 | 0.21974 | 0.21379 | -0.17331 | 3.6677 | -117.3139 | 3.7501 | 3.7727 | 0.10501 | -117.3382 | -117.1325 | 3.5987 | -117.3365 | 3.8692 | 3.7523 | 0.15358 | -117.1921 | -117.198 | 3.8699 | 3.8456 | 4.0513 | 3.8009 | -117.5161 | 3.8473 | 3.9917 | 3.9858 | 3.8822 | -117.5851
5525.1875 | 121.3577 | -3.7537 | 117.5858 | -0.010149 | -0.069769 | 0.037729 | 0.014554 | -0.015924 | 0.0090209 | -0.021518 | -0.021708 | -0.0087001 | 0.023008 | 0.056286 | -0.00017086 | -0.017266 | 0.0243 | 0.000747 | 0.10249 | 0.08278 | 0.27475 | -0.11342 | 0.097201 | 0.10109 | -0.015143 | 0.066194 | 0.21974 | 0.21379 | -0.17788 | 3.6402 | -117.4833 | 3.7364 | 3.7544 | 0.11417 | -117.503 | -117.311 | 3.5758 | -117.5196 | 3.8509 | 3.7385 | 0.16274 | -117.366 | -117.372 | 3.8562 | 3.8364 | 4.0284 | 3.778 | -117.6992 | 3.8199 | 3.9734 | 3.9674 | 3.8548 | -117.7636
5526.9531 | 121.4584 | -4.2709 | 117.0731 | -0.010149 | -0.069341 | 0.037729 | 0.014768 | -0.015497 | 0.0092345 | -0.013887 | -0.02128 | -0.0080591 | 0.022794 | 0.056072 | -0.00038466 | -0.017266 | 0.028878 | -0.003831 | 0.10707 | 0.078201 | 0.27932 | -0.10427 | 0.088043 | 0.10109 | -0.010564 | 0.075351 | 0.21974 | 0.21837 | -0.17331 | 4.1667 | -116.966 | 4.2537 | 4.2671 | 0.10044 | -116.9949 | -116.7937 | 4.0976 | -116.9977 | 4.359 | 4.2604 | 0.16274 | -116.8533 | -116.8547 | 4.378 | 4.3491 | 4.5503 | 4.2998 | -117.1773 | 4.3463 | 4.4907 | 4.4893 | 4.372 | -117.2464
5528.6562 | 121.4035 | -4.0237 | 117.4393 | -0.01778 | -0.069555 | 0.037729 | 0.014554 | -0.015497 | 0.0088073 | -0.021518 | -0.021921 | -0.0082729 | 0.022367 | 0.056286 | -0.00038466 | -0.021844 | 0.028878 | -0.003831 | 0.10707 | 0.078201 | 0.27932 | -0.10427 | 0.10178 | 0.10567 | -0.019721 | 0.070773 | 0.22432 | 0.21379 | -0.17331 | 3.9195 | -117.3322 | 4.0019 | 4.0199 | 0.10044 | -117.3611 | -117.1599 | 3.8504 | -117.3685 | 4.1255 | 4.004 | 0.15358 | -117.2149 | -117.2255 | 4.1308 | 4.1019 | 4.3031 | 4.0526 | -117.5435 | 4.0945 | 4.2481 | 4.2375 | 4.1294 | -117.6126
5530.4062 | 121.5454 | -3.7949 | 117.5949 | -0.010149 | -0.069555 | 0.037943 | 0.014768 | -0.015711 | 0.0085935 | -0.029148 | -0.021708 | -0.0084865 | 0.022581 | 0.056286 | -0.00038466 | -0.017266 | 0.028878 | 0.000747 | 0.10249 | 0.073622 | 0.27017 | -0.10885 | 0.092622 | 0.10567 | -0.019721 | 0.075351 | 0.22432 | 0.21379 | -0.16873 | 3.686 | -117.4924 | 3.7776 | 3.7956 | 0.10959 | -117.5213 | -117.3247 | 3.6261 | -117.5196 | 3.8875 | 3.7751 | 0.14901 | -117.3706 | -117.3811 | 3.8974 | 3.8685 | 4.065 | 3.8237 | -117.7038 | 3.8702 | 4.0192 | 4.0086 | 3.9005 | -117.7636
5532.1719 | 121.6278 | -3.392 | 118.0161 | -0.010149 | -0.069555 | 0.037943 | 0.014981 | -0.015711 | 0.0092345 | -0.029148 | -0.021708 | -0.0087001 | 0.022581 | 0.056499 | -0.00038466 | -0.031001 | 0.028878 | -0.008409 | 0.10249 | 0.073622 | 0.2839 | -0.10885 | 0.097201 | 0.10109 | -0.019721 | 0.070773 | 0.21974 | 0.21379 | -0.17788 | 3.2832 | -117.9136 | 3.361 | 3.3836 | 0.10044 | -117.9424 | -117.7321 | 3.2141 | -117.9453 | 3.4892 | 3.3723 | 0.15816 | -117.7963 | -117.8023 | 3.4945 | 3.4657 | 3.6759 | 3.4209 | -118.1249 | 3.4628 | 3.6118 | 3.6058 | 3.4931 | -118.1939
5533.9375 | 121.5454 | -3.3829 | 118.1213 | -0.01778 | -0.069341 | 0.037943 | 0.014768 | -0.015497 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.023008 | 0.056072 | -0.00081186 | -0.021844 | 0.033457 | 0.005325 | 0.093333 | 0.08278 | 0.27932 | -0.10427 | 0.097201 | 0.11025 | -0.019721 | 0.066194 | 0.21059 | 0.20921 | -0.17331 | 3.2786 | -118.028 | 3.361 | 3.3882 | 0.10959 | -118.0386 | -117.842 | 3.2096 | -118.0551 | 3.4801 | 3.3632 | 0.15358 | -117.9108 | -117.9121 | 3.4762 | 3.4657 | 3.6622 | 3.4163 | -118.2256 | 3.4491 | 3.5935 | 3.5921 | 3.4931 | -118.2946
5535.6875 | 121.5088 | -3.2913 | 118.2678 | -0.010149 | -0.069341 | 0.037729 | 0.014768 | -0.016138 | 0.0090209 | -0.021518 | -0.021708 | -0.0084865 | 0.022581 | 0.056286 | -0.00059826 | -0.021844 | 0.028878 | 0.000747 | 0.097912 | 0.078201 | 0.27475 | -0.10427 | 0.088043 | 0.10109 | -0.019721 | 0.066194 | 0.21974 | 0.21379 | -0.17331 | 3.1871 | -118.1699 | 3.2695 | 3.2921 | 0.10501 | -118.1896 | -117.9931 | 3.118 | -118.2016 | 3.3794 | 3.2716 | 0.15358 | -118.0481 | -118.054 | 3.3892 | 3.3695 | 3.5661 | 3.3202 | -118.3721 | 3.3575 | 3.5111 | 3.5051 | 3.3924 | -118.4411
5537.3906 | 121.637 | -3.2364 | 118.277 | -0.0025182 | -0.069555 | 0.038157 | 0.014768 | -0.015497 | 0.0090209 | -0.029148 | -0.021708 | -0.0082729 | 0.022794 | 0.056499 | -0.00038466 | -0.021844 | 0.0243 | 0.000747 | 0.10249 | 0.08278 | 0.27932 | -0.10427 | 0.097201 | 0.10567 | -0.019721 | 0.075351 | 0.21974 | 0.22295 | -0.17788 | 3.1321 | -118.1745 | 3.2145 | 3.2371 | 0.10501 | -118.1942 | -117.9977 | 3.0585 | -118.2016 | 3.3336 | 3.2167 | 0.15816 | -118.0572 | -118.054 | 3.3389 | 3.3192 | 3.5157 | 3.2607 | -118.3812 | 3.3117 | 3.4561 | 3.4593 | 3.3421 | -118.4549
5539.1562 | 121.5637 | -3.1952 | 118.3502 | -0.01778 | -0.069555 | 0.038157 | 0.014768 | -0.015924 | 0.0088073 | -0.036779 | -0.021921 | -0.0084865 | 0.022581 | 0.056286 | -0.00059826 | -0.021844 | 0.028878 | -0.008409 | 0.10707 | 0.078201 | 0.27932 | -0.10427 | 0.088043 | 0.10567 | -0.019721 | 0.070773 | 0.21059 | 0.21379 | -0.17788 | 3.0909 | -118.2432 | 3.1733 | 3.1868 | 0.095859 | -118.272 | -118.0709 | 3.0173 | -118.2794 | 3.2832 | 3.1755 | 0.15816 | -118.1396 | -118.1364 | 3.3023 | 3.2734 | 3.4745 | 3.2241 | -118.4545 | 3.266 | 3.4058 | 3.409 | 3.3009 | -118.5281
5540.8594 | 121.7239 | -3.1448 | 118.3456 | -0.01778 | -0.069341 | 0.038157 | 0.01434 | -0.015711 | 0.0094483 | -0.029148 | -0.021921 | -0.0080591 | 0.022794 | 0.056286 | -0.00017086 | -0.021844 | 0.028878 | 0.000747 | 0.093333 | 0.073622 | 0.27475 | -0.10885 | 0.10178 | 0.10109 | -0.019721 | 0.066194 | 0.20601 | 0.21379 | -0.17331 | 3.036 | -118.2523 | 3.123 | 3.1456 | 0.10959 | -118.272 | -118.0709 | 2.9715 | -118.2794 | 3.2466 | 3.1251 | 0.15358 | -118.1396 | -118.1319 | 3.2382 | 3.2185 | 3.4196 | 3.1737 | -118.4545 | 3.211 | 3.3508 | 3.3586 | 3.2459 | -118.5189
5542.6562 | 121.6599 | -3.3646 | 118.19 | -0.01778 | -0.069341 | 0.038157 | 0.014554 | -0.015711 | 0.0088073 | -0.029148 | -0.021921 | -0.0084865 | 0.022367 | 0.056499 | -0.00059826 | -0.021844 | 0.038035 | 0.000747 | 0.093333 | 0.078201 | 0.2839 | -0.11342 | 0.092622 | 0.10109 | -0.019721 | 0.070773 | 0.20601 | 0.21379 | -0.17788 | 3.2511 | -118.0967 | 3.3427 | 3.3653 | 0.11417 | -118.1118 | -117.9061 | 3.1867 | -118.1192 | 3.4572 | 3.3448 | 0.15816 | -117.984 | -117.9762 | 3.4579 | 3.4428 | 3.6485 | 3.4026 | -118.3034 | 3.4353 | 3.5706 | 3.5784 | 3.4657 | -118.3679
5544.3594 | 121.6232 | -3.4012 | 118.2083 | -0.0025182 | -0.069128 | 0.037943 | 0.014768 | -0.015283 | 0.0090209 | -0.029148 | -0.021921 | -0.0087001 | 0.022581 | 0.056286 | -0.00059826 | -0.017266 | 0.033457 | -0.003831 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.083464 | 0.10567 | -0.0243 | 0.066194 | 0.21974 | 0.21379 | -0.17331 | 3.2923 | -118.1058 | 3.3839 | 3.3974 | 0.10502 | -118.1301 | -117.929 | 3.2279 | -118.1421 | 3.4846 | 3.3769 | 0.14901 | -117.9886 | -117.9945 | 3.5037 | 3.4794 | 3.6805 | 3.4346 | -118.3172 | 3.4674 | 3.6209 | 3.615 | 3.5069 | -118.3816
5546.125 | 121.6415 | -3.392 | 118.2404 | -0.010149 | -0.069341 | 0.03837 | 0.014981 | -0.015497 | 0.0088073 | -0.013887 | -0.021708 | -0.0080591 | 0.022794 | 0.056499 | -0.00038466 | -0.012688 | 0.033457 | 0.000747 | 0.10249 | 0.078201 | 0.27017 | -0.10427 | 0.097201 | 0.096512 | -0.015143 | 0.061616 | 0.21516 | 0.20921 | -0.16873 | 3.2878 | -118.1379 | 3.3793 | 3.3928 | 0.10501 | -118.1622 | -117.9702 | 3.2233 | -118.1787 | 3.4892 | 3.3769 | 0.15358 | -118.0252 | -118.0311 | 3.4945 | 3.4702 | 3.6622 | 3.4255 | -118.3446 | 3.4536 | 3.6072 | 3.6012 | 3.4885 | -118.4091
5547.8906 | 121.6919 | -3.392 | 118.2312 | -0.010149 | -0.069555 | 0.038157 | 0.014981 | -0.015711 | 0.0088073 | -0.021518 | -0.021708 | -0.0084865 | 0.022794 | 0.056072 | -0.00059826 | -0.017266 | 0.028878 | 0.000747 | 0.10707 | 0.078201 | 0.27932 | -0.10885 | 0.092622 | 0.091933 | -0.015143 | 0.061616 | 0.20601 | 0.20463 | -0.17788 | 3.2832 | -118.1241 | 3.3748 | 3.3928 | 0.10959 | -118.153 | -117.9519 | 3.2141 | -118.1696 | 3.4847 | 3.3769 | 0.16274 | -118.0252 | -118.0266 | 3.4991 | 3.4702 | 3.6714 | 3.4209 | -118.34 | 3.4536 | 3.598 | 3.5967 | 3.484 | -118.4091
5549.6406 | 121.6507 | -3.3966 | 118.2541 | -0.025411 | -0.069341 | 0.037943 | 0.014554 | -0.015711 | 0.0088073 | -0.029148 | -0.021708 | -0.0082729 | 0.022794 | 0.056072 | -0.00038466 | -0.021844 | 0.028878 | 0.005325 | 0.088755 | 0.073622 | 0.27932 | -0.11342 | 0.097201 | 0.096512 | -0.019721 | 0.070773 | 0.21516 | 0.20921 | -0.16873 | 3.2832 | -118.1653 | 3.3748 | 3.4019 | 0.11875 | -118.1805 | -117.9748 | 3.2279 | -118.1833 | 3.4938 | 3.3769 | 0.14901 | -118.0389 | -118.0449 | 3.4854 | 3.4702 | 3.6759 | 3.4255 | -118.3675 | 3.4674 | 3.6118 | 3.6058 | 3.4931 | -118.4228
5551.4062 | 121.7926 | -3.3325 | 118.2587 | -0.010149 | -0.069128 | 0.037943 | 0.014554 | -0.015711 | 0.0090209 | -0.029148 | -0.021494 | -0.0084865 | 0.022581 | 0.056286 | -0.00038466 | -0.021844 | 0.028878 | 0.000747 | 0.10249 | 0.073622 | 0.27932 | -0.10885 | 0.088043 | 0.096512 | -0.028879 | 0.061616 | 0.20601 | 0.20463 | -0.18246 | 3.2237 | -118.1562 | 3.3107 | 3.3333 | 0.10959 | -118.185 | -117.9793 | 3.1501 | -118.1971 | 3.4206 | 3.3036 | 0.15358 | -118.0527 | -118.054 | 3.435 | 3.4061 | 3.6118 | 3.3614 | -118.3675 | 3.3941 | 3.5385 | 3.5372 | 3.429 | -118.4411
5553.1875 | 121.6827 | -3.3737 | 118.2953 | -0.010149 | -0.068914 | 0.038157 | 0.014981 | -0.015497 | 0.0090209 | -0.021518 | -0.021494 | -0.0084865 | 0.022794 | 0.056072 | -0.00038466 | -0.021844 | 0.028878 | 0.000747 | 0.097912 | 0.078201 | 0.2839 | -0.10427 | 0.092622 | 0.096512 | -0.019721 | 0.070773 | 0.20601 | 0.20921 | -0.17788 | 3.2695 | -118.1974 | 3.3519 | 3.3745 | 0.10501 | -118.2171 | -118.0114 | 3.1958 | -118.2245 | 3.4663 | 3.354 | 0.15816 | -118.0893 | -118.0861 | 3.4716 | 3.4519 | 3.6576 | 3.4026 | -118.3996 | 3.4445 | 3.5797 | 3.5829 | 3.4702 | -118.4732
5554.9531 | 121.7834 | -3.2135 | 118.364 | -0.025411 | -0.069341 | 0.037516 | 0.014554 | -0.015711 | 0.0090209 | -0.013887 | -0.021708 | -0.0082729 | 0.022794 | 0.056286 | -0.00038466 | -0.026423 | 0.028878 | -0.008409 | 0.10249 | 0.078201 | 0.27932 | -0.118 | 0.092622 | 0.091933 | -0.019721 | 0.066194 | 0.21516 | 0.20921 | -0.17788 | 3.0955 | -118.2615 | 3.1871 | 3.2051 | 0.10959 | -118.2858 | -118.0846 | 3.0356 | -118.2978 | 3.3061 | 3.1938 | 0.15816 | -118.1488 | -118.1547 | 3.316 | 3.2917 | 3.4928 | 3.2424 | -118.482 | 3.2797 | 3.4287 | 3.4227 | 3.3054 | -118.5418
5556.6562 | 121.6827 | -3.2547 | 118.4189 | -0.010149 | -0.069555 | 0.038157 | 0.014554 | -0.015711 | 0.0090209 | -0.021518 | -0.021921 | -0.0084865 | 0.023008 | 0.056072 | -0.0010255 | -0.017266 | 0.0243 | 0.000747 | 0.11165 | 0.073622 | 0.2839 | -0.10885 | 0.097201 | 0.10109 | -0.019721 | 0.061616 | 0.21059 | 0.20005 | -0.17331 | 3.1459 | -118.3072 | 3.2374 | 3.2554 | 0.10959 | -118.3453 | -118.135 | 3.0814 | -118.3573 | 3.3519 | 3.235 | 0.15358 | -118.2083 | -118.2188 | 3.3663 | 3.3283 | 3.5386 | 3.279 | -118.5277 | 3.3163 | 3.4653 | 3.4548 | 3.3558 | -118.5922
5558.4062 | 121.6599 | -3.1998 | 118.5059 | -0.010149 | -0.069555 | 0.037943 | 0.014768 | -0.015711 | 0.0088073 | -0.021518 | -0.021921 | -0.0084865 | 0.022794 | 0.056499 | -0.00038466 | -0.021844 | 0.038035 | 0.000747 | 0.10249 | 0.078201 | 0.27932 | -0.11342 | 0.092622 | 0.096512 | -0.015143 | 0.057037 | 0.21516 | 0.20463 | -0.18246 | 3.0863 | -118.4034 | 3.1779 | 3.2005 | 0.11417 | -118.4277 | -118.2265 | 3.0173 | -118.4488 | 3.2924 | 3.1846 | 0.16732 | -118.2907 | -118.3012 | 3.3023 | 3.278 | 3.4791 | 3.2378 | -118.6193 | 3.2568 | 3.4149 | 3.4044 | 3.2963 | -118.6883
5560.1719 | 121.7422 | -3.1631 | 118.515 | -0.0025182 | -0.069341 | 0.037729 | 0.014768 | -0.015711 | 0.0090209 | -0.021518 | -0.021921 | -0.0084865 | 0.022581 | 0.056499 | -0.00017086 | -0.012688 | 0.033457 | 0.000747 | 0.10249 | 0.078201 | 0.27932 | -0.10427 | 0.088043 | 0.096512 | -0.019721 | 0.057037 | 0.20601 | 0.20005 | -0.18246 | 3.0589 | -118.4125 | 3.1505 | 3.1639 | 0.10501 | -118.4368 | -118.2357 | 2.9807 | -118.458 | 3.2512 | 3.1434 | 0.16274 | -118.309 | -118.315 | 3.2656 | 3.2413 | 3.4425 | 3.1966 | -118.6193 | 3.2202 | 3.3692 | 3.3632 | 3.2597 | -118.6975
5561.875 | 121.7194 | -3.1998 | 118.5287 | -0.010149 | -0.069128 | 0.037729 | 0.014768 | -0.015497 | 0.0092345 | -0.021518 | -0.021708 | -0.0082729 | 0.022794 | 0.056072 | -0.00059826 | -0.021844 | 0.028878 | -0.003831 | 0.10249 | 0.073622 | 0.27932 | -0.10885 | 0.088043 | 0.091933 | -0.0243 | 0.066194 | 0.20601 | 0.20921 | -0.17788 | 3.0909 | -118.4263 | 3.1779 | 3.1959 | 0.10502 | -118.4551 | -118.2494 | 3.0219 | -118.4626 | 3.2878 | 3.1755 | 0.15358 | -118.3227 | -118.3195 | 3.3023 | 3.2734 | 3.4791 | 3.2286 | -118.6376 | 3.266 | 3.4058 | 3.409 | 3.2917 | -118.7066
5563.625 | 121.7056 | -3.1311 | 118.5791 | -0.010149 | -0.069982 | 0.038157 | 0.014768 | -0.015924 | 0.0090209 | -0.021518 | -0.021921 | -0.0084865 | 0.023008 | 0.056286 | -0.00038466 | -0.021844 | 0.033457 | -0.003831 | 0.093333 | 0.073622 | 0.27932 | -0.11342 | 0.088043 | 0.10109 | -0.019721 | 0.057037 | 0.21059 | 0.20005 | -0.17788 | 3.0177 | -118.4858 | 3.1093 | 3.1273 | 0.10959 | -118.5055 | -118.2998 | 2.9532 | -118.5221 | 3.2191 | 3.1114 | 0.15816 | -118.3685 | -118.3791 | 3.2244 | 3.2047 | 3.4104 | 3.1646 | -118.6925 | 3.1881 | 3.3417 | 3.3312 | 3.2322 | -118.757
5565.3438 | 121.8155 | -3.0991 | 118.5699 | -0.0025182 | -0.069769 | 0.037729 | 0.014554 | -0.015924 | 0.0090209 | -0.021518 | -0.021708 | -0.0082729 | 0.022153 | 0.056072 | -0.00059826 | -0.026423 | 0.038035 | -0.008409 | 0.10249 | 0.073622 | 0.2839 | -0.10885 | 0.092622 | 0.091933 | -0.028879 | 0.057037 | 0.20601 | 0.20463 | -0.17331 | 2.9902 | -118.4675 | 3.0726 | 3.0907 | 0.10044 | -118.4963 | -118.286 | 2.9258 | -118.5129 | 3.1917 | 3.0702 | 0.14443 | -118.3639 | -118.3653 | 3.2016 | 3.1727 | 3.383 | 3.1371 | -118.6788 | 3.1561 | 3.3051 | 3.3037 | 3.191 | -118.7433
5567.1094 | 121.756 | -3.1128 | 118.6066 | -0.010149 | -0.069341 | 0.037943 | 0.014768 | -0.015711 | 0.0090209 | -0.013887 | -0.021708 | -0.0087001 | 0.022367 | 0.056499 | -0.00038466 | -0.026423 | 0.033457 | 0.005325 | 0.097912 | 0.078201 | 0.27475 | -0.10427 | 0.083464 | 0.10109 | -0.019721 | 0.057037 | 0.19685 | 0.20463 | -0.17788 | 3.0085 | -118.5087 | 3.0864 | 3.1181 | 0.10959 | -118.5284 | -118.3318 | 2.9349 | -118.5495 | 3.1963 | 3.0931 | 0.15816 | -118.4097 | -118.4019 | 3.2107 | 3.191 | 3.3875 | 3.1463 | -118.7108 | 3.1698 | 3.3096 | 3.3174 | 3.2139 | -118.7845
5568.8594 | 121.7743 | -3.0991 | 118.6203 | -0.0025182 | -0.069555 | 0.038157 | 0.014554 | -0.015497 | 0.0090209 | -0.021518 | -0.021708 | -0.0082729 | 0.022794 | 0.056072 | -0.00059826 | -0.012688 | 0.028878 | 0.000747 | 0.097912 | 0.078201 | 0.2839 | -0.10885 | 0.092622 | 0.096512 | -0.019721 | 0.061616 | 0.21059 | 0.20463 | -0.17788 | 2.9902 | -118.5224 | 3.0864 | 3.0998 | 0.10959 | -118.5421 | -118.3364 | 2.9212 | -118.5587 | 3.1917 | 3.0793 | 0.15816 | -118.4097 | -118.4157 | 3.197 | 3.1773 | 3.383 | 3.1279 | -118.7291 | 3.1607 | 3.3096 | 3.3037 | 3.1956 | -118.7982
5570.625 | 121.788 | -3.1219 | 118.5928 | -0.025411 | -0.069341 | 0.037729 | 0.01434 | -0.015711 | 0.0090209 | -0.029148 | -0.021708 | -0.0084865 | 0.022581 | 0.056286 | -0.00059826 | -0.017266 | 0.033457 | 0.009904 | 0.093333 | 0.078201 | 0.27475 | -0.10885 | 0.092622 | 0.096512 | -0.028879 | 0.057037 | 0.21516 | 0.19547 | -0.17788 | 3.0131 | -118.4995 | 3.1047 | 3.1319 | 0.11875 | -118.5146 | -118.3181 | 2.9441 | -118.5358 | 3.2146 | 3.0931 | 0.14901 | -118.3777 | -118.3974 | 3.2153 | 3.2001 | 3.3967 | 3.1554 | -118.7017 | 3.179 | 3.3371 | 3.3174 | 3.2185 | -118.7707
5572.3281 | 121.8842 | -3.1952 | 118.4738 | -0.01778 | -0.069128 | 0.037729 | 0.014554 | -0.015497 | 0.0092345 | -0.013887 | -0.021708 | -0.0082729 | 0.023221 | 0.056072 | -0.00059826 | -0.021844 | 0.028878 | -0.003831 | 0.10249 | 0.078201 | 0.27475 | -0.10885 | 0.088043 | 0.096512 | -0.019721 | 0.066194 | 0.21516 | 0.20005 | -0.18246 | 3.0863 | -118.3713 | 3.1733 | 3.1914 | 0.10502 | -118.3956 | -118.1991 | 3.0127 | -118.4076 | 3.2832 | 3.1755 | 0.16274 | -118.2587 | -118.2738 | 3.2977 | 3.2734 | 3.4699 | 3.2241 | -118.5827 | 3.2614 | 3.4104 | 3.3952 | 3.2917 | -118.6563
5574.1094 | 121.8246 | -3.2272 | 118.4921 | -0.025411 | -0.069341 | 0.037943 | 0.014768 | -0.015711 | 0.0090209 | -0.021518 | -0.021708 | -0.0087001 | 0.022581 | 0.056499 | -0.00038466 | -0.017266 | 0.033457 | 0.005325 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.083464 | 0.091933 | -0.0243 | 0.052459 | 0.20143 | 0.20005 | -0.18246 | 3.123 | -118.3896 | 3.21 | 3.2326 | 0.10959 | -118.4185 | -118.2128 | 3.0448 | -118.4397 | 3.3107 | 3.2029 | 0.15816 | -118.2907 | -118.2921 | 3.3297 | 3.3009 | 3.5066 | 3.2607 | -118.5964 | 3.2797 | 3.4287 | 3.4273 | 3.3192 | -118.6746
5575.8125 | 121.7697 | -3.2318 | 118.5471 | -0.010149 | -0.069128 | 0.037943 | 0.01434 | -0.015497 | 0.0090209 | -0.029148 | -0.021708 | -0.0087001 | 0.022581 | 0.056499 | -0.00038466 | -0.021844 | 0.033457 | 0.000747 | 0.097912 | 0.078201 | 0.27932 | -0.10885 | 0.088043 | 0.096512 | -0.0243 | 0.052459 | 0.21516 | 0.19547 | -0.18246 | 3.123 | -118.4491 | 3.21 | 3.2326 | 0.10959 | -118.4689 | -118.2677 | 3.0493 | -118.4946 | 3.3199 | 3.2075 | 0.15816 | -118.3319 | -118.3516 | 3.3297 | 3.31 | 3.5111 | 3.2653 | -118.6559 | 3.2843 | 3.447 | 3.4273 | 3.3283 | -118.7295
5577.5781 | 121.8567 | -3.1815 | 118.4921 | -0.025411 | -0.069341 | 0.038157 | 0.014554 | -0.015497 | 0.0090209 | -0.029148 | -0.022135 | -0.0082729 | 0.022581 | 0.056286 | -0.00081186 | -0.026423 | 0.028878 | -0.003831 | 0.10249 | 0.08278 | 0.27932 | -0.10885 | 0.083464 | 0.096512 | -0.028879 | 0.052459 | 0.21059 | 0.20005 | -0.18246 | 3.0726 | -118.3896 | 3.155 | 3.1776 | 0.10502 | -118.4093 | -118.2128 | 2.999 | -118.4397 | 3.2649 | 3.1526 | 0.15358 | -118.2815 | -118.2921 | 3.2839 | 3.2642 | 3.4608 | 3.2103 | -118.601 | 3.2339 | 3.392 | 3.3815 | 3.278 | -118.6746
5579.2812 | 121.8246 | -3.2043 | 118.5242 | -0.010149 | -0.069341 | 0.037729 | 0.014554 | -0.015711 | 0.0090209 | -0.021518 | -0.021921 | -0.0082729 | 0.022794 | 0.056286 | -0.00038466 | -0.021844 | 0.033457 | 0.005325 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.092622 | 0.10109 | -0.0243 | 0.057037 | 0.21059 | 0.20463 | -0.17788 | 3.1001 | -118.4217 | 3.1825 | 3.2097 | 0.10959 | -118.4505 | -118.2448 | 3.0265 | -118.4671 | 3.297 | 3.18 | 0.15358 | -118.3136 | -118.3195 | 3.3068 | 3.278 | 3.4837 | 3.2378 | -118.6284 | 3.2614 | 3.4149 | 3.409 | 3.3054 | -118.7021
5581.0312 | 121.8979 | -3.1815 | 118.5379 | -0.010149 | -0.069555 | 0.037943 | 0.014768 | -0.015711 | 0.0088073 | -0.013887 | -0.021708 | -0.0084865 | 0.022794 | 0.056499 | -0.00038466 | -0.021844 | 0.028878 | -0.003831 | 0.10249 | 0.078201 | 0.27475 | -0.10427 | 0.083464 | 0.091933 | -0.028879 | 0.061616 | 0.20601 | 0.19547 | -0.17788 | 3.0772 | -118.4354 | 3.1596 | 3.1776 | 0.10044 | -118.4597 | -118.2632 | 3.0036 | -118.4763 | 3.2649 | 3.1526 | 0.14901 | -118.3319 | -118.3424 | 3.2839 | 3.2597 | 3.4562 | 3.2103 | -118.6422 | 3.2431 | 3.3875 | 3.3769 | 3.2734 | -118.7158
5582.7969 | 121.843 | -3.2135 | 118.5471 | -0.0025182 | -0.069341 | 0.03837 | 0.014554 | -0.016138 | 0.0092345 | -0.0062567 | -0.021921 | -0.0087001 | 0.022367 | 0.056286 | -0.00059826 | -0.021844 | 0.042614 | -0.008409 | 0.10249 | 0.073622 | 0.27475 | -0.10885 | 0.088043 | 0.087354 | -0.0243 | 0.061616 | 0.20143 | 0.20463 | -0.17788 | 3.1047 | -118.4446 | 3.1917 | 3.2051 | 0.10044 | -118.4734 | -118.2723 | 3.0356 | -118.4854 | 3.3015 | 3.1892 | 0.15358 | -118.3456 | -118.3424 | 3.316 | 3.2871 | 3.4882 | 3.2561 | -118.6559 | 3.2751 | 3.4149 | 3.4181 | 3.3009 | -118.7249
5584.5625 | 121.8933 | -3.1952 | 118.5699 | -0.010149 | -0.069555 | 0.037729 | 0.014768 | -0.015924 | 0.0092345 | -0.021518 | -0.021708 | -0.0082729 | 0.022581 | 0.056286 | -0.00059826 | -0.026423 | 0.0243 | 0.000747 | 0.10707 | 0.073622 | 0.27475 | -0.10427 | 0.083464 | 0.096512 | -0.028879 | 0.057037 | 0.20601 | 0.20005 | -0.17788 | 3.0909 | -118.4629 | 3.1688 | 3.1959 | 0.10501 | -118.4963 | -118.2952 | 3.0173 | -118.5129 | 3.2787 | 3.1663 | 0.14901 | -118.3639 | -118.3699 | 3.3023 | 3.2688 | 3.4699 | 3.2195 | -118.6742 | 3.2522 | 3.4012 | 3.3952 | 3.2917 | -118.7478
5586.2656 | 121.8018 | -3.1952 | 118.5928 | -0.01778 | -0.069555 | 0.037516 | 0.014554 | -0.015924 | 0.0088073 | -0.029148 | -0.021494 | -0.0080591 | 0.022367 | 0.056286 | -0.00059826 | -0.026423 | 0.033457 | -0.008409 | 0.10707 | 0.078201 | 0.27932 | -0.11342 | 0.088043 | 0.091933 | -0.0243 | 0.057037 | 0.19685 | 0.20005 | -0.19162 | 3.0818 | -118.4858 | 3.1688 | 3.1868 | 0.10502 | -118.5146 | -118.3135 | 3.0036 | -118.5358 | 3.2832 | 3.1709 | 0.16732 | -118.396 | -118.3928 | 3.3023 | 3.2734 | 3.4745 | 3.2286 | -118.7063 | 3.2522 | 3.392 | 3.3952 | 3.2871 | -118.7845
5588.0312 | 121.8521 | -3.2135 | 118.5837 | -0.01778 | -0.069341 | 0.037729 | 0.014554 | -0.015924 | 0.0085935 | -0.029148 | -0.021708 | -0.0082729 | 0.022581 | 0.056713 | -0.00038466 | -0.017266 | 0.028878 | -0.003831 | 0.10249 | 0.069043 | 0.27932 | -0.10885 | 0.092622 | 0.091933 | -0.0243 | 0.061616 | 0.20143 | 0.20005 | -0.17788 | 3.1047 | -118.4812 | 3.1962 | 3.2097 | 0.10502 | -118.5146 | -118.3044 | 3.0356 | -118.5221 | 3.3061 | 3.1892 | 0.15358 | -118.3822 | -118.3836 | 3.316 | 3.2825 | 3.4928 | 3.2424 | -118.6925 | 3.2751 | 3.4149 | 3.4136 | 3.3054 | -118.7616
5589.7969 | 121.9437 | -3.1906 | 118.5379 | -0.010149 | -0.069555 | 0.037943 | 0.014981 | -0.015924 | 0.0090209 | -0.013887 | -0.021708 | -0.0084865 | 0.022581 | 0.056286 | -0.00038466 | -0.017266 | 0.038035 | -0.008409 | 0.093333 | 0.073622 | 0.27932 | -0.10885 | 0.092622 | 0.091933 | -0.015143 | 0.061616 | 0.19227 | 0.20005 | -0.18246 | 3.0818 | -118.4446 | 3.1733 | 3.1822 | 0.10044 | -118.4643 | -118.2586 | 3.0081 | -118.4763 | 3.2832 | 3.1755 | 0.16732 | -118.3456 | -118.3379 | 3.2839 | 3.2642 | 3.4699 | 3.2286 | -118.6467 | 3.2522 | 3.3829 | 3.3907 | 3.2825 | -118.7204
5591.5 | 121.9208 | -3.2227 | 118.5425 | -0.01778 | -0.069555 | 0.037943 | 0.014554 | -0.015924 | 0.0088073 | -0.021518 | -0.022135 | -0.0082729 | 0.022794 | 0.056286 | -0.00017086 | -0.021844 | 0.0243 | -0.008409 | 0.10249 | 0.073622 | 0.2839 | -0.10427 | 0.078886 | 0.091933 | -0.028879 | 0.061616 | 0.20143 | 0.20463 | -0.18704 | 3.1184 | -118.44 | 3.2008 | 3.2142 | 0.095859 | -118.4689 | -118.2586 | 3.0356 | -118.4809 | 3.3015 | 3.1938 | 0.15816 | -118.3411 | -118.3378 | 3.3251 | 3.2963 | 3.5066 | 3.247 | -118.6467 | 3.2843 | 3.4241 | 3.4273 | 3.3146 | -118.7295
5593.2656 | 121.8567 | -3.273 | 118.5333 | -0.0025182 | -0.069555 | 0.037729 | 0.014554 | -0.015711 | 0.0085935 | -0.029148 | -0.021708 | -0.0082729 | 0.022153 | 0.056499 | -0.00059826 | -0.021844 | 0.038035 | 0.000747 | 0.097912 | 0.078201 | 0.27932 | -0.11342 | 0.092622 | 0.087354 | -0.0243 | 0.057037 | 0.20143 | 0.20005 | -0.18246 | 3.1596 | -118.4354 | 3.2512 | 3.2738 | 0.11417 | -118.4551 | -118.254 | 3.0905 | -118.4763 | 3.3656 | 3.2487 | 0.15816 | -118.3319 | -118.3333 | 3.3709 | 3.3512 | 3.5523 | 3.311 | -118.6468 | 3.33 | 3.4744 | 3.4731 | 3.3604 | -118.7158
5595.0312 | 121.9666 | -3.2684 | 118.4875 | -0.01778 | -0.069341 | 0.037729 | 0.014768 | -0.015711 | 0.0088073 | -0.013887 | -0.021708 | -0.0082729 | 0.022794 | 0.056286 | -0.00017086 | -0.021844 | 0.033457 | -0.003831 | 0.097912 | 0.087359 | 0.27932 | -0.10885 | 0.088043 | 0.096512 | -0.0243 | 0.052459 | 0.20143 | 0.20005 | -0.18246 | 3.1596 | -118.3896 | 3.2466 | 3.2646 | 0.10502 | -118.4002 | -118.2082 | 3.086 | -118.4351 | 3.3565 | 3.2441 | 0.15816 | -118.2861 | -118.2875 | 3.3663 | 3.3558 | 3.5478 | 3.3019 | -118.5964 | 3.3209 | 3.4699 | 3.4685 | 3.3649 | -118.67
5596.7812 | 121.8887 | -3.3875 | 118.4555 | -0.01778 | -0.069769 | 0.037943 | 0.014768 | -0.015497 | 0.0090209 | -0.021518 | -0.02128 | -0.0084865 | 0.022794 | 0.056286 | -0.00017086 | -0.026423 | 0.033457 | -0.008409 | 0.097912 | 0.08278 | 0.27475 | -0.118 | 0.083464 | 0.087354 | -0.0243 | 0.057037 | 0.20601 | 0.20005 | -0.18704 | 3.2694 | -118.3576 | 3.361 | 3.379 | 0.10959 | -118.3727 | -118.1808 | 3.2004 | -118.3985 | 3.4709 | 3.3632 | 0.16274 | -118.2495 | -118.2555 | 3.4854 | 3.4702 | 3.6622 | 3.4209 | -118.5735 | 3.4445 | 3.5935 | 3.5875 | 3.4748 | -118.6425
5598.5469 | 121.8796 | -3.392 | 118.4555 | -0.01778 | -0.069555 | 0.037943 | 0.014768 | -0.015924 | 0.0092345 | -0.029148 | -0.021708 | -0.0080591 | 0.022581 | 0.056286 | -0.00081186 | -0.021844 | 0.028878 | 0.000747 | 0.097912 | 0.073622 | 0.2839 | -0.11342 | 0.092622 | 0.096512 | -0.028879 | 0.061616 | 0.20601 | 0.20005 | -0.18246 | 3.2786 | -118.3576 | 3.3702 | 3.3928 | 0.11417 | -118.3819 | -118.1716 | 3.2096 | -118.3939 | 3.4847 | 3.3632 | 0.15358 | -118.2495 | -118.2555 | 3.4899 | 3.4657 | 3.6759 | 3.4209 | -118.5689 | 3.4536 | 3.598 | 3.5921 | 3.4885 | -118.638
5600.3125 | 121.843 | -3.4058 | 118.4555 | -0.010149 | -0.069769 | 0.038157 | 0.014981 | -0.015711 | 0.0085935 | -0.021518 | -0.021494 | -0.0082729 | 0.022794 | 0.056286 | -0.00038466 | -0.026423 | 0.028878 | 0.000747 | 0.10249 | 0.087359 | 0.2839 | -0.11342 | 0.092622 | 0.096512 | -0.028879 | 0.052459 | 0.20601 | 0.20005 | -0.18246 | 3.2923 | -118.353 | 3.3793 | 3.4065 | 0.11417 | -118.3681 | -118.1716 | 3.2233 | -118.403 | 3.4984 | 3.3769 | 0.15358 | -118.2495 | -118.2555 | 3.5083 | 3.4931 | 3.6897 | 3.4346 | -118.5689 | 3.4582 | 3.6118 | 3.6058 | 3.5023 | -118.638
5602.0156 | 121.8567 | -3.3829 | 118.483 | -0.01778 | -0.069555 | 0.038157 | 0.014554 | -0.015924 | 0.0092345 | -0.021518 | -0.021708 | -0.0082729 | 0.022367 | 0.056286 | -0.00059826 | -0.021844 | 0.028878 | 0.000747 | 0.10249 | 0.078201 | 0.27932 | -0.10427 | 0.097201 | 0.091933 | -0.0243 | 0.057037 | 0.20601 | 0.20005 | -0.18246 | 3.2786 | -118.3805 | 3.361 | 3.3836 | 0.10501 | -118.4048 | -118.2036 | 3.2004 | -118.4259 | 3.4801 | 3.3586 | 0.15816 | -118.277 | -118.2829 | 3.4854 | 3.4611 | 3.6622 | 3.4118 | -118.5872 | 3.4399 | 3.5889 | 3.5829 | 3.4748 | -118.6654
5603.7812 | 121.9437 | -3.3188 | 118.4509 | -0.01778 | -0.069555 | 0.037943 | 0.01434 | -0.015711 | 0.0085935 | -0.013887 | -0.021494 | -0.0084865 | 0.022794 | 0.056713 | -0.00059826 | -0.017266 | 0.038035 | -0.003831 | 0.10707 | 0.08278 | 0.27932 | -0.11342 | 0.092622 | 0.096512 | -0.019721 | 0.052459 | 0.20601 | 0.20921 | -0.17331 | 3.2054 | -118.3439 | 3.3015 | 3.315 | 0.10959 | -118.3681 | -118.1716 | 3.1455 | -118.3985 | 3.4114 | 3.2991 | 0.15358 | -118.2449 | -118.2417 | 3.4259 | 3.4016 | 3.5981 | 3.3568 | -118.5644 | 3.3712 | 3.5248 | 3.528 | 3.4153 | -118.6242
5605.4844 | 121.9986 | -3.3096 | 118.5013 | -0.010149 | -0.069555 | 0.038157 | 0.014768 | -0.015924 | 0.0088073 | -0.029148 | -0.021708 | -0.0084865 | 0.022367 | 0.056286 | -0.00038466 | -0.021844 | 0.028878 | -0.008409 | 0.10249 | 0.073622 | 0.27932 | -0.10885 | 0.097201 | 0.091933 | -0.0243 | 0.057037 | 0.20601 | 0.19547 | -0.17788 | 3.2008 | -118.3988 | 3.2878 | 3.3012 | 0.10044 | -118.4277 | -118.222 | 3.1317 | -118.4442 | 3.4068 | 3.2853 | 0.15358 | -118.2953 | -118.3058 | 3.4121 | 3.3833 | 3.589 | 3.3385 | -118.6101 | 3.3667 | 3.5156 | 3.5051 | 3.4016 | -118.6792
5607.25 | 121.9208 | -3.3234 | 118.5196 | -0.010149 | -0.069341 | 0.037729 | 0.014981 | -0.015497 | 0.0088073 | -0.021518 | -0.021708 | -0.0082729 | 0.022794 | 0.056499 | -0.00038466 | -0.021844 | 0.038035 | -0.003831 | 0.10249 | 0.078201 | 0.2839 | -0.10885 | 0.088043 | 0.10109 | -0.0243 | 0.052459 | 0.20601 | 0.20463 | -0.17788 | 3.2145 | -118.4171 | 3.3015 | 3.3195 | 0.10502 | -118.4414 | -118.2357 | 3.1455 | -118.4671 | 3.4114 | 3.2991 | 0.15358 | -118.3136 | -118.315 | 3.4259 | 3.4016 | 3.6073 | 3.3614 | -118.6284 | 3.3758 | 3.5294 | 3.528 | 3.4245 | -118.6975
5609.0156 | 122.0032 | -3.3051 | 118.5104 | -0.0025182 | -0.069555 | 0.038157 | 0.01434 | -0.015283 | 0.0090209 | -0.013887 | -0.02128 | -0.0084865 | 0.023008 | 0.056499 | -0.00059826 | -0.026423 | 0.033457 | -0.008409 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.088043 | 0.10109 | -0.028879 | 0.061616 | 0.20143 | 0.19547 | -0.18246 | 3.1962 | -118.4079 | 3.2786 | 3.2966 | 0.10044 | -118.4322 | -118.2311 | 3.1226 | -118.4488 | 3.3931 | 3.2762 | 0.15358 | -118.309 | -118.315 | 3.4075 | 3.3833 | 3.5844 | 3.3385 | -118.6193 | 3.3667 | 3.5065 | 3.5005 | 3.4061 | -118.6929
5610.7188 | 122.0215 | -3.3005 | 118.5196 | -0.025411 | -0.069769 | 0.037943 | 0.014554 | -0.015711 | 0.0090209 | -0.021518 | -0.021494 | -0.0087001 | 0.022794 | 0.056286 | -0.00038466 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.073622 | 0.27475 | -0.10885 | 0.088043 | 0.10109 | -0.028879 | 0.061616 | 0.20601 | 0.20005 | -0.17788 | 3.1916 | -118.4125 | 3.2832 | 3.2921 | 0.10044 | -118.446 | -118.2448 | 3.1226 | -118.458 | 3.3885 | 3.2716 | 0.14901 | -118.3136 | -118.3195 | 3.4075 | 3.3741 | 3.5752 | 3.3339 | -118.6284 | 3.3621 | 3.5065 | 3.5005 | 3.4016 | -118.6975
5612.4844 | 121.9757 | -3.3508 | 118.4647 | -0.01778 | -0.069555 | 0.038157 | 0.01434 | -0.015497 | 0.0088073 | -0.029148 | -0.021494 | -0.0082729 | 0.022581 | 0.056713 | -0.00059826 | -0.017266 | 0.033457 | -0.003831 | 0.097912 | 0.078201 | 0.27017 | -0.10885 | 0.088043 | 0.091933 | -0.019721 | 0.061616 | 0.20143 | 0.20005 | -0.18246 | 3.242 | -118.3667 | 3.3336 | 3.347 | 0.10502 | -118.3865 | -118.1945 | 3.1684 | -118.403 | 3.4389 | 3.3311 | 0.16274 | -118.2632 | -118.2646 | 3.4487 | 3.429 | 3.621 | 3.3843 | -118.5735 | 3.4124 | 3.5523 | 3.5509 | 3.4428 | -118.6471
5614.1875 | 121.962 | -3.4378 | 118.3823 | -0.01778 | -0.069769 | 0.037943 | 0.014127 | -0.015711 | 0.0090209 | -0.021518 | -0.021708 | -0.0082729 | 0.022581 | 0.056499 | -0.00059826 | -0.017266 | 0.0243 | -0.003831 | 0.10707 | 0.078201 | 0.2839 | -0.10427 | 0.092622 | 0.096512 | -0.0243 | 0.057037 | 0.20143 | 0.20005 | -0.17788 | 3.3335 | -118.2752 | 3.4205 | 3.434 | 0.10044 | -118.3041 | -118.0984 | 3.2599 | -118.3252 | 3.5304 | 3.4135 | 0.15358 | -118.1808 | -118.1822 | 3.5449 | 3.516 | 3.7217 | 3.4621 | -118.4865 | 3.4948 | 3.6392 | 3.6379 | 3.5343 | -118.5601
5615.9531 | 121.9849 | -3.4195 | 118.4189 | -0.010149 | -0.069769 | 0.038157 | 0.014554 | -0.016138 | 0.0085935 | -0.021518 | -0.021494 | -0.0082729 | 0.022794 | 0.056499 | -0.00038466 | -0.021844 | 0.0243 | -0.003831 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.088043 | 0.096512 | -0.028879 | 0.052459 | 0.19685 | 0.20921 | -0.17788 | 3.3106 | -118.3164 | 3.3977 | 3.4157 | 0.10502 | -118.3407 | -118.1396 | 3.2416 | -118.3664 | 3.5075 | 3.3906 | 0.14901 | -118.222 | -118.2097 | 3.522 | 3.4977 | 3.6988 | 3.4438 | -118.5277 | 3.472 | 3.6163 | 3.6287 | 3.516 | -118.5968
5617.6719 | 122.0581 | -3.479 | 118.3319 | -0.010149 | -0.069769 | 0.038157 | 0.014768 | -0.015711 | 0.0088073 | -0.021518 | -0.021708 | -0.0087001 | 0.022581 | 0.056499 | -0.00038466 | -0.021844 | 0.033457 | -0.003831 | 0.10249 | 0.08278 | 0.27932 | -0.10885 | 0.088043 | 0.096512 | -0.019721 | 0.057037 | 0.19227 | 0.20005 | -0.18246 | 3.3702 | -118.2294 | 3.4572 | 3.4752 | 0.10502 | -118.2491 | -118.0526 | 3.2965 | -118.2749 | 3.567 | 3.4593 | 0.16274 | -118.1396 | -118.1319 | 3.5815 | 3.5618 | 3.7583 | 3.5125 | -118.4408 | 3.536 | 3.6713 | 3.6791 | 3.5755 | -118.5144
5619.4375 | 122.0535 | -3.479 | 118.3685 | -0.01778 | -0.069555 | 0.037729 | 0.014554 | -0.015711 | 0.0088073 | -0.013887 | -0.021494 | -0.0080591 | 0.022794 | 0.056499 | -0.00081186 | -0.017266 | 0.028878 | -0.003831 | 0.10249 | 0.08278 | 0.2839 | -0.10885 | 0.083464 | 0.091933 | -0.033458 | 0.061616 | 0.19685 | 0.20005 | -0.17788 | 3.3702 | -118.266 | 3.4617 | 3.4752 | 0.10502 | -118.2858 | -118.0846 | 3.3011 | -118.3069 | 3.5625 | 3.4455 | 0.14443 | -118.1717 | -118.1685 | 3.5815 | 3.5618 | 3.7629 | 3.5079 | -118.4774 | 3.5406 | 3.6759 | 3.6791 | 3.5709 | -118.5464
5621.1406 | 121.9437 | -3.4973 | 118.3914 | -0.025411 | -0.069769 | 0.037943 | 0.014981 | -0.015711 | 0.0094483 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.056713 | -0.00059826 | -0.021844 | 0.028878 | -0.003831 | 0.10249 | 0.073622 | 0.27932 | -0.11342 | 0.088043 | 0.096512 | -0.015143 | 0.057037 | 0.20143 | 0.20005 | -0.18246 | 3.3839 | -118.2889 | 3.4755 | 3.4935 | 0.10959 | -118.3178 | -118.1121 | 3.3148 | -118.3344 | 3.5854 | 3.4822 | 0.16732 | -118.19 | -118.1914 | 3.5998 | 3.5709 | 3.7766 | 3.5262 | -118.5048 | 3.5544 | 3.6987 | 3.6974 | 3.5938 | -118.5739
5622.9062 | 121.9116 | -3.511 | 118.4235 | -0.01778 | -0.069982 | 0.037729 | 0.014981 | -0.015711 | 0.0088073 | -0.013887 | -0.021494 | -0.0084865 | 0.022367 | 0.056499 | -0.00059826 | -0.021844 | 0.033457 | -0.003831 | 0.10249 | 0.073622 | 0.2839 | -0.10885 | 0.083464 | 0.096512 | -0.019721 | 0.061616 | 0.19685 | 0.20463 | -0.18704 | 3.4022 | -118.321 | 3.4892 | 3.5072 | 0.10502 | -118.3498 | -118.1396 | 3.324 | -118.3618 | 3.5945 | 3.4913 | 0.16732 | -118.2266 | -118.2188 | 3.6135 | 3.5847 | 3.795 | 3.5445 | -118.5323 | 3.5727 | 3.7079 | 3.7157 | 3.6076 | -118.6105
5624.6719 | 121.9025 | -3.4744 | 118.428 | -0.010149 | -0.069982 | 0.038157 | 0.014554 | -0.015924 | 0.0088073 | -0.021518 | -0.021921 | -0.0084865 | 0.022581 | 0.056286 | -0.00038466 | -0.021844 | 0.033457 | -0.003831 | 0.10249 | 0.08278 | 0.27475 | -0.10427 | 0.088043 | 0.091933 | -0.028879 | 0.052459 | 0.19685 | 0.20005 | -0.18704 | 3.3702 | -118.3255 | 3.4526 | 3.4706 | 0.10044 | -118.3453 | -118.1533 | 3.2874 | -118.3756 | 3.5625 | 3.4455 | 0.15816 | -118.2312 | -118.228 | 3.5769 | 3.5572 | 3.7492 | 3.5079 | -118.5323 | 3.5269 | 3.6713 | 3.6745 | 3.5664 | -118.6151
5626.4375 | 122.0764 | -3.4195 | 118.4235 | -0.01778 | -0.069555 | 0.037943 | 0.014981 | -0.015711 | 0.0090209 | -0.021518 | -0.021708 | -0.0080591 | 0.022581 | 0.056713 | -0.00038466 | -0.021844 | 0.028878 | 0.000747 | 0.097912 | 0.08278 | 0.2839 | -0.10427 | 0.083464 | 0.091933 | -0.028879 | 0.052459 | 0.19685 | 0.19547 | -0.17331 | 3.3152 | -118.3256 | 3.3977 | 3.4202 | 0.10501 | -118.3407 | -118.1396 | 3.2462 | -118.371 | 3.503 | 3.3906 | 0.14443 | -118.2266 | -118.228 | 3.5174 | 3.5023 | 3.7034 | 3.4484 | -118.5277 | 3.472 | 3.6163 | 3.615 | 3.5114 | -118.5968
5628.1562 | 121.907 | -3.4744 | 118.4601 | -0.010149 | -0.069982 | 0.037943 | 0.014768 | -0.015924 | 0.0090209 | -0.029148 | -0.021708 | -0.0084865 | 0.022153 | 0.056713 | -0.00038466 | -0.012688 | 0.028878 | 0.000747 | 0.10249 | 0.08278 | 0.27932 | -0.10885 | 0.088043 | 0.087354 | -0.019721 | 0.061616 | 0.19685 | 0.19547 | -0.18246 | 3.3656 | -118.3576 | 3.4617 | 3.4752 | 0.10959 | -118.3773 | -118.1808 | 3.292 | -118.3985 | 3.5625 | 3.4547 | 0.16274 | -118.2632 | -118.2646 | 3.5769 | 3.5572 | 3.7538 | 3.5033 | -118.5689 | 3.536 | 3.6713 | 3.6699 | 3.5618 | -118.6425
5629.9219 | 122.0627 | -3.4195 | 118.4372 | -0.0025182 | -0.069982 | 0.037943 | 0.01434 | -0.015924 | 0.0090209 | -0.021518 | -0.02128 | -0.0084865 | 0.022794 | 0.056713 | -0.00059826 | -0.021844 | 0.028878 | 0.000747 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.083464 | 0.091933 | -0.028879 | 0.057037 | 0.19685 | 0.19547 | -0.18246 | 3.3106 | -118.3347 | 3.3977 | 3.4202 | 0.10959 | -118.359 | -118.1579 | 3.237 | -118.3802 | 3.503 | 3.3906 | 0.15358 | -118.2403 | -118.2417 | 3.522 | 3.4977 | 3.6988 | 3.4484 | -118.546 | 3.4765 | 3.6163 | 3.615 | 3.5114 | -118.6197
5631.625 | 121.9894 | -3.4378 | 118.4647 | -0.0025182 | -0.069769 | 0.038157 | 0.014554 | -0.015497 | 0.0088073 | -0.013887 | -0.021708 | -0.0082729 | 0.022794 | 0.056072 | -0.00059826 | -0.021844 | 0.038035 | -0.012988 | 0.10249 | 0.08278 | 0.27932 | -0.10885 | 0.088043 | 0.082776 | -0.028879 | 0.057037 | 0.20143 | 0.20005 | -0.18246 | 3.329 | -118.3622 | 3.416 | 3.4248 | 0.095859 | -118.3819 | -118.1853 | 3.2553 | -118.4076 | 3.5258 | 3.4089 | 0.15358 | -118.2632 | -118.2646 | 3.5403 | 3.5206 | 3.7171 | 3.4758 | -118.5735 | 3.4948 | 3.6392 | 3.6379 | 3.5206 | -118.6471
5633.3906 | 122.0261 | -3.4149 | 118.4235 | -0.010149 | -0.069555 | 0.038157 | 0.014554 | -0.015283 | 0.0088073 | -0.029148 | -0.021708 | -0.0084865 | 0.022581 | 0.056072 | -0.00059826 | -0.021844 | 0.0243 | -0.003831 | 0.10249 | 0.078201 | 0.27932 | -0.10427 | 0.092622 | 0.091933 | -0.028879 | 0.061616 | 0.19227 | 0.20463 | -0.18246 | 3.3106 | -118.321 | 3.3931 | 3.4111 | 0.10044 | -118.3453 | -118.1441 | 3.2325 | -118.3618 | 3.5075 | 3.386 | 0.15358 | -118.2312 | -118.2188 | 3.5174 | 3.4931 | 3.6942 | 3.4392 | -118.5277 | 3.4765 | 3.6072 | 3.6195 | 3.5069 | -118.6059
5635.1562 | 122.0764 | -3.392 | 118.4326 | -0.0025182 | -0.069769 | 0.037943 | 0.014554 | -0.015924 | 0.0083799 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.056286 | -0.00038466 | -0.017266 | 0.033457 | 0.000747 | 0.10707 | 0.08278 | 0.27017 | -0.10885 | 0.092622 | 0.091933 | -0.028879 | 0.057037 | 0.20143 | 0.20463 | -0.18246 | 3.2832 | -118.3255 | 3.3748 | 3.3928 | 0.10959 | -118.3498 | -118.1624 | 3.2096 | -118.3756 | 3.4847 | 3.3632 | 0.15358 | -118.2312 | -118.228 | 3.4991 | 3.4748 | 3.6622 | 3.4255 | -118.5415 | 3.4491 | 3.5935 | 3.5967 | 3.484 | -118.6151
5636.8594 | 121.9986 | -3.4653 | 118.4601 | -0.01778 | -0.069555 | 0.037729 | 0.014768 | -0.015711 | 0.0090209 | -0.029148 | -0.021708 | -0.0082729 | 0.022581 | 0.056499 | -0.00038466 | -0.017266 | 0.033457 | -0.003831 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.088043 | 0.10109 | -0.028879 | 0.057037 | 0.20601 | 0.20005 | -0.17788 | 3.361 | -118.3576 | 3.448 | 3.4614 | 0.10044 | -118.3865 | -118.1808 | 3.2874 | -118.403 | 3.5533 | 3.4364 | 0.14901 | -118.2541 | -118.26 | 3.5678 | 3.5389 | 3.7446 | 3.4987 | -118.5644 | 3.5223 | 3.6713 | 3.6653 | 3.5664 | -118.638
5638.6406 | 121.9986 | -3.4515 | 118.4509 | -0.01778 | -0.069769 | 0.037943 | 0.01434 | -0.015711 | 0.0090209 | -0.021518 | -0.021494 | -0.0084865 | 0.022581 | 0.056499 | -0.00059826 | -0.021844 | 0.028878 | 0.000747 | 0.093333 | 0.08278 | 0.27932 | -0.10885 | 0.088043 | 0.091933 | -0.0243 | 0.057037 | 0.19685 | 0.20005 | -0.18246 | 3.3427 | -118.3576 | 3.4297 | 3.4523 | 0.10959 | -118.3681 | -118.1716 | 3.2691 | -118.3939 | 3.5396 | 3.4272 | 0.15816 | -118.2541 | -118.2509 | 3.5449 | 3.5343 | 3.7309 | 3.4804 | -118.5598 | 3.5086 | 3.6484 | 3.6516 | 3.5435 | -118.6334
5640.4219 | 122.0535 | -3.4607 | 118.428 | -0.01778 | -0.069769 | 0.037943 | 0.014554 | -0.015497 | 0.0085935 | -0.013887 | -0.021494 | -0.0084865 | 0.022581 | 0.056286 | -0.00038466 | -0.008109 | 0.028878 | 0.000747 | 0.10707 | 0.078201 | 0.2839 | -0.11342 | 0.088043 | 0.091933 | -0.0243 | 0.061616 | 0.19227 | 0.20005 | -0.18246 | 3.3473 | -118.321 | 3.4526 | 3.4614 | 0.11417 | -118.3498 | -118.1441 | 3.2782 | -118.3664 | 3.5487 | 3.4364 | 0.15816 | -118.2358 | -118.228 | 3.5678 | 3.5389 | 3.7446 | 3.4896 | -118.5415 | 3.5223 | 3.653 | 3.6607 | 3.5526 | -118.6105
5642.1875 | 122.0901 | -3.4378 | 118.4555 | -0.01778 | -0.069555 | 0.037943 | 0.014554 | -0.015924 | 0.0088073 | -0.013887 | -0.02128 | -0.0084865 | 0.022153 | 0.056286 | -0.00059826 | -0.021844 | 0.0243 | -0.003831 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.088043 | 0.091933 | -0.0243 | 0.052459 | 0.19227 | 0.20005 | -0.18246 | 3.3335 | -118.353 | 3.416 | 3.434 | 0.10044 | -118.3819 | -118.1762 | 3.2553 | -118.403 | 3.5258 | 3.4135 | 0.15816 | -118.2632 | -118.2555 | 3.5403 | 3.5114 | 3.7171 | 3.4621 | -118.5598 | 3.4903 | 3.6301 | 3.6379 | 3.5297 | -118.638
5643.9062 | 122.0444 | -3.4424 | 118.4692 | -0.01778 | -0.070196 | 0.037943 | 0.01434 | -0.015497 | 0.0092345 | -0.029148 | -0.021708 | -0.0087001 | 0.022367 | 0.056499 | -0.00059826 | -0.021844 | 0.038035 | 0.000747 | 0.10249 | 0.073622 | 0.2839 | -0.10427 | 0.088043 | 0.087354 | -0.028879 | 0.052459 | 0.19685 | 0.19547 | -0.18246 | 3.3381 | -118.3667 | 3.4205 | 3.4431 | 0.10501 | -118.3956 | -118.1853 | 3.2599 | -118.4168 | 3.5304 | 3.4135 | 0.15358 | -118.2724 | -118.2738 | 3.5449 | 3.516 | 3.7263 | 3.4804 | -118.5735 | 3.4948 | 3.6392 | 3.6379 | 3.5297 | -118.6517
5645.6719 | 121.9757 | -3.4653 | 118.5059 | -0.010149 | -0.069555 | 0.037943 | 0.014554 | -0.015711 | 0.0088073 | -0.021518 | -0.021708 | -0.0082729 | 0.022581 | 0.056286 | -0.00059826 | -0.021844 | 0.033457 | -0.012988 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.088043 | 0.10109 | -0.0243 | 0.052459 | 0.18769 | 0.19547 | -0.17788 | 3.3564 | -118.4034 | 3.4434 | 3.4523 | 0.095859 | -118.4277 | -118.2265 | 3.2874 | -118.4534 | 3.5533 | 3.441 | 0.15358 | -118.3182 | -118.3104 | 3.5678 | 3.5435 | 3.7446 | 3.4987 | -118.6147 | 3.5177 | 3.653 | 3.6607 | 3.5664 | -118.6837
5647.4375 | 121.994 | -3.4561 | 118.483 | -0.010149 | -0.069769 | 0.037729 | 0.01434 | -0.015497 | 0.0090209 | -0.013887 | -0.02128 | -0.0084865 | 0.022581 | 0.056713 | -0.00059826 | -0.021844 | 0.033457 | -0.003831 | 0.10707 | 0.08278 | 0.27932 | -0.11342 | 0.088043 | 0.091933 | -0.033458 | 0.052459 | 0.19227 | 0.1909 | -0.18704 | 3.3427 | -118.3759 | 3.4343 | 3.4523 | 0.10959 | -118.4002 | -118.2036 | 3.2691 | -118.4305 | 3.5442 | 3.4227 | 0.15358 | -118.2907 | -118.2921 | 3.5632 | 3.5389 | 3.7354 | 3.4896 | -118.5964 | 3.5086 | 3.6484 | 3.647 | 3.548 | -118.67
5649.1406 | 122.1039 | -3.4241 | 118.4555 | -0.01778 | -0.069769 | 0.037943 | 0.014768 | -0.015711 | 0.0090209 | -0.029148 | -0.021921 | -0.0080591 | 0.022581 | 0.056499 | -0.00081186 | -0.012688 | 0.028878 | -0.008409 | 0.10249 | 0.073622 | 0.27932 | -0.11342 | 0.083464 | 0.087354 | -0.028879 | 0.043302 | 0.20143 | 0.20005 | -0.18704 | 3.3106 | -118.353 | 3.4114 | 3.4157 | 0.10502 | -118.3819 | -118.1762 | 3.237 | -118.4122 | 3.5075 | 3.3952 | 0.15816 | -118.2541 | -118.2555 | 3.5266 | 3.4977 | 3.7034 | 3.4529 | -118.5689 | 3.4674 | 3.6255 | 3.6241 | 3.5114 | -118.6425
5650.9062 | 122.0627 | -3.4149 | 118.4692 | -0.033042 | -0.069769 | 0.037729 | 0.014554 | -0.015497 | 0.0090209 | -0.029148 | -0.021708 | -0.0082729 | 0.022367 | 0.056072 | -0.00059826 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.078201 | 0.27475 | -0.11342 | 0.092622 | 0.091933 | -0.033458 | 0.043302 | 0.19227 | 0.20463 | -0.18246 | 3.3015 | -118.3622 | 3.3977 | 3.4111 | 0.10959 | -118.391 | -118.1945 | 3.2325 | -118.4259 | 3.5075 | 3.3815 | 0.14901 | -118.277 | -118.2646 | 3.522 | 3.4931 | 3.6897 | 3.4484 | -118.5827 | 3.4582 | 3.6072 | 3.6195 | 3.5069 | -118.6517
5652.6094 | 121.9849 | -3.5065 | 118.5013 | -0.01778 | -0.069982 | 0.037943 | 0.014554 | -0.015924 | 0.0090209 | -0.029148 | -0.021708 | -0.0089137 | 0.022581 | 0.056499 | -0.00059826 | -0.021844 | 0.038035 | -0.008409 | 0.10707 | 0.08278 | 0.2839 | -0.10885 | 0.088043 | 0.091933 | -0.028879 | 0.043302 | 0.19685 | 0.20005 | -0.17788 | 3.3976 | -118.3942 | 3.4846 | 3.4981 | 0.10044 | -118.4185 | -118.2174 | 3.3286 | -118.458 | 3.5945 | 3.4776 | 0.14901 | -118.3044 | -118.3012 | 3.6135 | 3.5893 | 3.7904 | 3.5445 | -118.6101 | 3.5498 | 3.7033 | 3.7065 | 3.5984 | -118.6792
5654.375 | 122.0901 | -3.4241 | 118.5287 | -0.01778 | -0.069769 | 0.037516 | 0.01434 | -0.015711 | 0.0088073 | -0.029148 | -0.021708 | -0.0084865 | 0.022581 | 0.056499 | -0.00059826 | -0.021844 | 0.038035 | -0.008409 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.092622 | 0.10109 | -0.033458 | 0.043302 | 0.20601 | 0.19547 | -0.18246 | 3.3152 | -118.4263 | 3.4022 | 3.4157 | 0.10044 | -118.4505 | -118.2494 | 3.2416 | -118.4854 | 3.5167 | 3.3906 | 0.14901 | -118.3227 | -118.3333 | 3.5266 | 3.5023 | 3.7034 | 3.4621 | -118.6376 | 3.4674 | 3.6301 | 3.6195 | 3.5252 | -118.7112
5656.125 | 122.0718 | -3.4149 | 118.5013 | -0.01778 | -0.069555 | 0.037729 | 0.014554 | -0.015283 | 0.0088073 | -0.013887 | -0.021494 | -0.0087001 | 0.022581 | 0.056499 | -0.00059826 | -0.026423 | 0.028878 | -0.003831 | 0.10707 | 0.073622 | 0.27932 | -0.10427 | 0.083464 | 0.091933 | -0.028879 | 0.043302 | 0.19685 | 0.19547 | -0.18704 | 3.3106 | -118.3942 | 3.3885 | 3.4111 | 0.10044 | -118.4277 | -118.222 | 3.2279 | -118.458 | 3.4984 | 3.386 | 0.15816 | -118.3044 | -118.3058 | 3.522 | 3.4885 | 3.6942 | 3.4438 | -118.6056 | 3.4582 | 3.6118 | 3.6104 | 3.5069 | -118.6883
5657.8906 | 122.113 | -3.3875 | 118.5287 | -0.010149 | -0.069982 | 0.037943 | 0.014768 | -0.016138 | 0.0088073 | -0.013887 | -0.021494 | -0.0084865 | 0.022367 | 0.056499 | -0.00059826 | -0.026423 | 0.0243 | -0.003831 | 0.10249 | 0.078201 | 0.2839 | -0.10885 | 0.083464 | 0.096512 | -0.0243 | 0.038723 | 0.20143 | 0.20005 | -0.18704 | 3.2786 | -118.4263 | 3.361 | 3.3836 | 0.10502 | -118.4505 | -118.2448 | 3.2004 | -118.49 | 3.4709 | 3.3632 | 0.16274 | -118.3273 | -118.3287 | 3.4899 | 3.4657 | 3.6714 | 3.4118 | -118.6376 | 3.4262 | 3.5889 | 3.5875 | 3.484 | -118.7158
5659.6562 | 121.9986 | -3.392 | 118.5883 | -0.01778 | -0.069982 | 0.037943 | 0.014127 | -0.015711 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.022581 | 0.056286 | -0.00038466 | -0.021844 | 0.038035 | 0.000747 | 0.10707 | 0.078201 | 0.27932 | -0.10885 | 0.092622 | 0.091933 | -0.028879 | 0.043302 | 0.21059 | 0.1909 | -0.18246 | 3.2832 | -118.4812 | 3.3702 | 3.3928 | 0.10959 | -118.5101 | -118.3089 | 3.2096 | -118.545 | 3.4847 | 3.3632 | 0.15358 | -118.3777 | -118.3974 | 3.4991 | 3.4702 | 3.6714 | 3.4301 | -118.6971 | 3.4353 | 3.6026 | 3.5829 | 3.484 | -118.7707
5661.3594 | 122.049 | -3.3875 | 118.5791 | -0.01778 | -0.069769 | 0.038157 | 0.01434 | -0.016352 | 0.0083799 | -0.029148 | -0.021708 | -0.0084865 | 0.022794 | 0.056927 | -0.00038466 | -0.026423 | 0.028878 | -0.003831 | 0.10249 | 0.08278 | 0.2839 | -0.11342 | 0.088043 | 0.087354 | -0.0243 | 0.034145 | 0.19685 | 0.1909 | -0.18704 | 3.274 | -118.4766 | 3.361 | 3.3836 | 0.10959 | -118.4963 | -118.2952 | 3.2004 | -118.545 | 3.4755 | 3.3632 | 0.16274 | -118.3823 | -118.3882 | 3.4899 | 3.4702 | 3.6714 | 3.4163 | -118.6925 | 3.4216 | 3.5843 | 3.5783 | 3.4748 | -118.7661
5663.1406 | 122.1268 | -3.3325 | 118.5699 | -0.01778 | -0.069555 | 0.038157 | 0.014127 | -0.015711 | 0.0085935 | -0.029148 | -0.021494 | -0.0084865 | 0.022581 | 0.056286 | -0.00059826 | -0.017266 | 0.0243 | -0.008409 | 0.10249 | 0.08278 | 0.27475 | -0.10885 | 0.088043 | 0.091933 | -0.028879 | 0.04788 | 0.19227 | 0.19547 | -0.18246 | 3.2237 | -118.4675 | 3.3153 | 3.3241 | 0.10044 | -118.4872 | -118.2952 | 3.1501 | -118.5221 | 3.4206 | 3.3036 | 0.15358 | -118.3777 | -118.3745 | 3.435 | 3.4153 | 3.6073 | 3.3568 | -118.6788 | 3.3804 | 3.5248 | 3.528 | 3.4245 | -118.7524
5664.9219 | 122.1634 | -3.3096 | 118.6111 | -0.010149 | -0.069982 | 0.037943 | 0.014554 | -0.015711 | 0.0090209 | -0.029148 | -0.021708 | -0.0080591 | 0.022794 | 0.056713 | -0.00038466 | -0.021844 | 0.028878 | -0.003831 | 0.097912 | 0.08278 | 0.27932 | -0.10427 | 0.083464 | 0.091933 | -0.028879 | 0.043302 | 0.19685 | 0.19547 | -0.18246 | 3.2054 | -118.5132 | 3.2878 | 3.3058 | 0.10044 | -118.5284 | -118.3318 | 3.1272 | -118.5678 | 3.3931 | 3.2808 | 0.15358 | -118.4143 | -118.4157 | 3.4075 | 3.3924 | 3.589 | 3.3385 | -118.7154 | 3.3529 | 3.5065 | 3.5051 | 3.4016 | -118.7936
5666.6406 | 122.1588 | -3.3051 | 118.6386 | -0.010149 | -0.069982 | 0.037729 | 0.014127 | -0.015924 | 0.0090209 | -0.036779 | -0.02128 | -0.0084865 | 0.022794 | 0.05714 | -0.00059826 | -0.021844 | 0.028878 | -0.008409 | 0.097912 | 0.078201 | 0.2839 | -0.11342 | 0.083464 | 0.087354 | -0.028879 | 0.043302 | 0.19227 | 0.19547 | -0.18704 | 3.1916 | -118.5407 | 3.2832 | 3.2966 | 0.10502 | -118.5604 | -118.3547 | 3.118 | -118.5953 | 3.3885 | 3.2762 | 0.15816 | -118.4463 | -118.4431 | 3.403 | 3.3833 | 3.589 | 3.3339 | -118.752 | 3.3484 | 3.4973 | 3.5005 | 3.3924 | -118.8257
5668.4062 | 122.1359 | -3.2913 | 118.6478 | -0.01778 | -0.069769 | 0.038157 | 0.014768 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.056499 | -0.00059826 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.078201 | 0.28848 | -0.11342 | 0.078886 | 0.091933 | -0.0243 | 0.038723 | 0.19227 | 0.19547 | -0.19162 | 3.1779 | -118.5407 | 3.2741 | 3.2829 | 0.10502 | -118.5696 | -118.3593 | 3.0997 | -118.609 | 3.3702 | 3.267 | 0.16732 | -118.4555 | -118.4523 | 3.3984 | 3.3695 | 3.5798 | 3.3248 | -118.7612 | 3.33 | 3.4836 | 3.4868 | 3.3833 | -118.8394
5670.1719 | 122.0261 | -3.4103 | 118.6249 | -0.010149 | -0.069769 | 0.037729 | 0.014554 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0087001 | 0.022367 | 0.056713 | -0.00059826 | -0.017266 | 0.033457 | -0.012988 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.088043 | 0.087354 | -0.028879 | 0.043302 | 0.19685 | 0.19547 | -0.17788 | 3.3015 | -118.5224 | 3.3931 | 3.3974 | 0.095859 | -118.5467 | -118.3456 | 3.2325 | -118.5816 | 3.4984 | 3.3815 | 0.14901 | -118.428 | -118.4294 | 3.5128 | 3.4885 | 3.6897 | 3.4438 | -118.7337 | 3.4536 | 3.6072 | 3.6058 | 3.4977 | -118.8028
5671.9219 | 122.0444 | -3.3463 | 118.6935 | -0.010149 | -0.069769 | 0.038157 | 0.014768 | -0.015711 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022367 | 0.056713 | -0.00017086 | -0.021844 | 0.028878 | -0.008409 | 0.10249 | 0.073622 | 0.27932 | -0.10427 | 0.083464 | 0.091933 | -0.0243 | 0.038723 | 0.18769 | 0.20005 | -0.18704 | 3.242 | -118.5911 | 3.3244 | 3.3378 | 0.095859 | -118.6199 | -118.4142 | 3.1592 | -118.6548 | 3.4297 | 3.322 | 0.16274 | -118.5058 | -118.4935 | 3.4487 | 3.4199 | 3.6256 | 3.3751 | -118.7978 | 3.385 | 3.5339 | 3.5463 | 3.4382 | -118.8806
5673.625 | 122.081 | -3.3279 | 118.6386 | -0.010149 | -0.070196 | 0.037729 | 0.014554 | -0.016138 | 0.0083799 | -0.021518 | -0.021708 | -0.0084865 | 0.022794 | 0.056499 | -0.00038466 | -0.017266 | 0.028878 | -0.008409 | 0.10707 | 0.078201 | 0.27932 | -0.10885 | 0.083464 | 0.082776 | -0.0243 | 0.038723 | 0.19685 | 0.1909 | -0.19162 | 3.2191 | -118.5315 | 3.3107 | 3.3195 | 0.10044 | -118.5604 | -118.3593 | 3.1363 | -118.5999 | 3.4114 | 3.3036 | 0.16732 | -118.4418 | -118.4477 | 3.435 | 3.4061 | 3.6073 | 3.3568 | -118.7475 | 3.3667 | 3.5248 | 3.5188 | 3.4107 | -118.8302
5675.3906 | 122.1588 | -3.3188 | 118.6478 | -0.0025182 | -0.069555 | 0.037943 | 0.014554 | -0.015711 | 0.0088073 | -0.029148 | -0.02128 | -0.0084865 | 0.022367 | 0.056499 | -0.00081186 | -0.026423 | 0.033457 | -0.008409 | 0.10707 | 0.08278 | 0.2839 | -0.099689 | 0.078886 | 0.087354 | -0.028879 | 0.038723 | 0.19227 | 0.19547 | -0.18704 | 3.2191 | -118.5407 | 3.2924 | 3.3104 | 0.09128 | -118.565 | -118.3639 | 3.1317 | -118.609 | 3.3977 | 3.2899 | 0.15816 | -118.4555 | -118.4523 | 3.4259 | 3.4016 | 3.6027 | 3.3522 | -118.7475 | 3.3575 | 3.5111 | 3.5143 | 3.4061 | -118.8348
5677.1406 | 122.0444 | -3.2135 | 118.8217 | -0.010149 | -0.069982 | 0.037943 | 0.014768 | -0.015283 | 0.0092345 | -0.021518 | -0.021494 | -0.0087001 | 0.022367 | 0.056499 | -0.00081186 | -0.021844 | 0.0243 | -0.008409 | 0.097912 | 0.078201 | 0.2839 | -0.10885 | 0.083464 | 0.091933 | -0.033458 | 0.034145 | 0.18769 | 0.19547 | -0.19162 | 3.1047 | -118.7238 | 3.1917 | 3.2051 | 0.10044 | -118.7435 | -118.5378 | 3.0219 | -118.7876 | 3.297 | 3.18 | 0.15816 | -118.634 | -118.6262 | 3.3114 | 3.2917 | 3.4974 | 3.2378 | -118.9306 | 3.2476 | 3.4012 | 3.409 | 3.3054 | -119.0133
5678.9062 | 122.1634 | -3.1677 | 118.7805 | -0.010149 | -0.069555 | 0.037729 | 0.014127 | -0.015711 | 0.0090209 | -0.036779 | -0.021708 | -0.0080591 | 0.022581 | 0.056499 | -0.00059826 | -0.017266 | 0.038035 | -0.003831 | 0.10707 | 0.078201 | 0.27475 | -0.11342 | 0.092622 | 0.087354 | -0.028879 | 0.043302 | 0.19685 | 0.20005 | -0.18704 | 3.0543 | -118.6735 | 3.1505 | 3.1639 | 0.10959 | -118.7023 | -118.5058 | 2.9807 | -118.7372 | 3.2603 | 3.1388 | 0.15816 | -118.5837 | -118.5805 | 3.2748 | 3.2459 | 3.4425 | 3.2058 | -118.8939 | 3.211 | 3.3646 | 3.3678 | 3.2551 | -118.9676
5680.6719 | 122.081 | -3.2227 | 118.8034 | -0.010149 | -0.069982 | 0.037943 | 0.014981 | -0.015924 | 0.0088073 | -0.021518 | -0.021708 | -0.0080591 | 0.022367 | 0.056713 | -0.00059826 | -0.031001 | 0.038035 | -0.008409 | 0.10249 | 0.08278 | 0.2839 | -0.10427 | 0.088043 | 0.091933 | -0.019721 | 0.043302 | 0.19685 | 0.19547 | -0.18704 | 3.1184 | -118.7009 | 3.1917 | 3.2142 | 0.095859 | -118.7206 | -118.5195 | 3.0356 | -118.7601 | 3.3107 | 3.2029 | 0.16732 | -118.6066 | -118.6079 | 3.3251 | 3.3054 | 3.5066 | 3.2607 | -118.9077 | 3.266 | 3.4195 | 3.4181 | 3.3146 | -118.9904
5682.4375 | 122.1176 | -3.2043 | 118.7988 | -0.010149 | -0.069982 | 0.037516 | 0.014768 | -0.015924 | 0.0088073 | -0.0062567 | -0.021708 | -0.0084865 | 0.022367 | 0.056713 | -0.00038466 | -0.026423 | 0.033457 | -0.012988 | 0.10707 | 0.073622 | 0.28848 | -0.118 | 0.083464 | 0.087354 | -0.028879 | 0.043302 | 0.19227 | 0.1909 | -0.19162 | 3.0863 | -118.6918 | 3.1779 | 3.1914 | 0.10502 | -118.7252 | -118.5103 | 3.0127 | -118.7555 | 3.2878 | 3.1755 | 0.16274 | -118.6066 | -118.6079 | 3.3114 | 3.278 | 3.4928 | 3.2378 | -118.9168 | 3.2476 | 3.3966 | 3.3952 | 3.2917 | -118.9904
5684.1562 | 122.0947 | -3.2318 | 118.8171 | -0.010149 | -0.070196 | 0.037943 | 0.014554 | -0.015924 | 0.0090209 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.056713 | -0.00038466 | -0.017266 | 0.028878 | -0.003831 | 0.10249 | 0.078201 | 0.2839 | -0.10885 | 0.083464 | 0.087354 | -0.0243 | 0.038723 | 0.19227 | 0.18632 | -0.18246 | 3.123 | -118.7146 | 3.2145 | 3.228 | 0.10502 | -118.7389 | -118.5332 | 3.0493 | -118.7784 | 3.3153 | 3.2075 | 0.15816 | -118.6249 | -118.6308 | 3.3343 | 3.31 | 3.5157 | 3.2607 | -118.926 | 3.2705 | 3.4241 | 3.4181 | 3.3192 | -118.9996
5685.9062 | 122.0993 | -3.2181 | 118.8263 | -0.010149 | -0.07041 | 0.037729 | 0.01434 | -0.015924 | 0.0090209 | -0.021518 | -0.021708 | -0.0084865 | 0.022581 | 0.056713 | -0.00038466 | -0.026423 | 0.033457 | -0.003831 | 0.10249 | 0.069043 | 0.27017 | -0.10885 | 0.083464 | 0.087354 | -0.028879 | 0.038723 | 0.18311 | 0.19547 | -0.18704 | 3.1092 | -118.7238 | 3.1917 | 3.2142 | 0.10502 | -118.7573 | -118.5561 | 3.031 | -118.7876 | 3.3015 | 3.1892 | 0.15816 | -118.6432 | -118.6308 | 3.3206 | 3.2871 | 3.4882 | 3.2515 | -118.9351 | 3.2568 | 3.4012 | 3.4136 | 3.3054 | -119.0133
5687.6719 | 122.1451 | -3.1906 | 118.8217 | -0.01778 | -0.069769 | 0.037729 | 0.014554 | -0.016352 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.056286 | -0.00059826 | -0.021844 | 0.033457 | -0.003831 | 0.10249 | 0.073622 | 0.2839 | -0.11342 | 0.083464 | 0.087354 | -0.033458 | 0.043302 | 0.19227 | 0.1909 | -0.18246 | 3.0772 | -118.7192 | 3.1688 | 3.1868 | 0.10959 | -118.7481 | -118.5378 | 3.0081 | -118.7784 | 3.2741 | 3.1572 | 0.14901 | -118.6294 | -118.6308 | 3.2931 | 3.2642 | 3.4745 | 3.2241 | -118.9351 | 3.2339 | 3.3829 | 3.3815 | 3.278 | -119.0042
5689.375 | 122.1222 | -3.1815 | 118.8309 | -0.01778 | -0.069769 | 0.038157 | 0.01434 | -0.015924 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.056713 | -0.00038466 | -0.017266 | 0.033457 | -0.003831 | 0.097912 | 0.073622 | 0.27932 | -0.10885 | 0.088043 | 0.087354 | -0.028879 | 0.043302 | 0.19685 | 0.19547 | -0.18704 | 3.0726 | -118.733 | 3.1642 | 3.1776 | 0.10502 | -118.7572 | -118.5515 | 2.9944 | -118.7876 | 3.2695 | 3.1526 | 0.15816 | -118.634 | -118.6354 | 3.2794 | 3.2551 | 3.4608 | 3.2149 | -118.9397 | 3.2248 | 3.3783 | 3.3769 | 3.2688 | -119.0179
5691.1406 | 122.1222 | -3.3005 | 118.7759 | -0.010149 | -0.069982 | 0.037943 | 0.014554 | -0.015711 | 0.0088073 | -0.013887 | -0.021494 | -0.0084865 | 0.022581 | 0.056072 | -0.00038466 | -0.017266 | 0.033457 | -0.008409 | 0.10249 | 0.078201 | 0.27932 | -0.11342 | 0.083464 | 0.087354 | -0.0243 | 0.038723 | 0.18769 | 0.1909 | -0.19162 | 3.1871 | -118.6735 | 3.2832 | 3.2921 | 0.10502 | -118.6977 | -118.4966 | 3.1089 | -118.7372 | 3.3839 | 3.2762 | 0.16732 | -118.5882 | -118.585 | 3.403 | 3.3787 | 3.5798 | 3.3339 | -118.8894 | 3.3392 | 3.4882 | 3.4914 | 3.3878 | -118.9676
5692.8438 | 122.081 | -3.2867 | 118.7897 | -0.01778 | -0.069555 | 0.037729 | 0.01434 | -0.015711 | 0.0088073 | -0.013887 | -0.021708 | -0.0084865 | 0.022367 | 0.056927 | -0.00059826 | -0.021844 | 0.038035 | 0.005325 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.088043 | 0.082776 | -0.0243 | 0.043302 | 0.19685 | 0.1909 | -0.19162 | 3.1779 | -118.6872 | 3.2649 | 3.2921 | 0.11417 | -118.7115 | -118.5103 | 3.0951 | -118.7464 | 3.3748 | 3.2624 | 0.16732 | -118.5928 | -118.5988 | 3.3892 | 3.3649 | 3.5661 | 3.3248 | -118.8985 | 3.33 | 3.4836 | 3.4776 | 3.3695 | -118.9813
5694.6094 | 122.1542 | -3.2272 | 118.7988 | -0.01778 | -0.070196 | 0.037943 | 0.014554 | -0.015924 | 0.0088073 | -0.0062567 | -0.021067 | -0.0084865 | 0.022581 | 0.056713 | -0.00059826 | -0.021844 | 0.033457 | -0.008409 | 0.097912 | 0.078201 | 0.27932 | -0.10427 | 0.083464 | 0.087354 | -0.0243 | 0.029566 | 0.19227 | 0.19547 | -0.18246 | 3.123 | -118.7009 | 3.2054 | 3.2188 | 0.095859 | -118.7206 | -118.5195 | 3.0448 | -118.7693 | 3.3107 | 3.2029 | 0.15816 | -118.6066 | -118.6034 | 3.3251 | 3.3054 | 3.5066 | 3.2607 | -118.9031 | 3.2568 | 3.4195 | 3.4227 | 3.3146 | -118.9813
5696.375 | 122.1588 | -3.2181 | 118.8263 | -0.01778 | -0.069982 | 0.038157 | 0.014768 | -0.016138 | 0.0088073 | -0.021518 | -0.021708 | -0.0084865 | 0.022153 | 0.056927 | -0.00059826 | -0.021844 | 0.028878 | 0.000747 | 0.10249 | 0.08278 | 0.27932 | -0.10427 | 0.083464 | 0.087354 | -0.028879 | 0.034145 | 0.18769 | 0.20005 | -0.19162 | 3.1138 | -118.7238 | 3.1962 | 3.2188 | 0.10501 | -118.7435 | -118.547 | 3.0265 | -118.7921 | 3.3015 | 3.1892 | 0.16274 | -118.6386 | -118.6262 | 3.3206 | 3.3009 | 3.4974 | 3.247 | -118.9306 | 3.2522 | 3.4058 | 3.4181 | 3.3054 | -119.0179
5698.1562 | 122.2229 | -3.1906 | 118.8126 | -0.01778 | -0.069982 | 0.037302 | 0.014554 | -0.015924 | 0.0088073 | -0.036779 | -0.021708 | -0.0082729 | 0.022367 | 0.056927 | -0.00059826 | -0.017266 | 0.033457 | -0.003831 | 0.10249 | 0.078201 | 0.27932 | -0.11342 | 0.083464 | 0.087354 | -0.0243 | 0.034145 | 0.19685 | 0.1909 | -0.18246 | 3.0772 | -118.7101 | 3.1733 | 3.1868 | 0.10959 | -118.7344 | -118.5332 | 3.0081 | -118.7784 | 3.2741 | 3.1663 | 0.15816 | -118.6157 | -118.6217 | 3.2931 | 3.2688 | 3.4699 | 3.2241 | -118.926 | 3.2248 | 3.3875 | 3.3815 | 3.278 | -118.995
5699.875 | 122.1085 | -3.2364 | 118.8538 | -0.025411 | -0.070196 | 0.037943 | 0.01434 | -0.015711 | 0.0088073 | -0.036779 | -0.02128 | -0.0082729 | 0.022581 | 0.056713 | -0.00081186 | -0.026423 | 0.033457 | -0.003831 | 0.10707 | 0.078201 | 0.27475 | -0.10885 | 0.088043 | 0.091933 | -0.019721 | 0.029566 | 0.19685 | 0.20005 | -0.18704 | 3.1275 | -118.7467 | 3.21 | 3.2326 | 0.10502 | -118.7756 | -118.579 | 3.0493 | -118.8242 | 3.3244 | 3.2167 | 0.16732 | -118.6569 | -118.6537 | 3.3435 | 3.3146 | 3.5111 | 3.2698 | -118.9626 | 3.266 | 3.4332 | 3.4364 | 3.3283 | -119.0408
5701.6406 | 122.2275 | -3.1128 | 118.9041 | -0.01778 | -0.070196 | 0.037302 | 0.014554 | -0.016138 | 0.0088073 | -0.036779 | -0.021494 | -0.0080591 | 0.022153 | 0.056713 | -0.00059826 | -0.026423 | 0.028878 | -0.012988 | 0.10707 | 0.078201 | 0.2839 | -0.10885 | 0.097201 | 0.091933 | -0.033458 | 0.038723 | 0.18769 | 0.1909 | -0.18704 | 3.0039 | -118.797 | 3.0864 | 3.0998 | 0.095859 | -118.8259 | -118.6202 | 2.9257 | -118.8654 | 3.21 | 3.0793 | 0.15358 | -118.7164 | -118.7132 | 3.2199 | 3.191 | 3.3967 | 3.1417 | -119.013 | 3.1515 | 3.3005 | 3.3037 | 3.2047 | -119.0912
5703.4062 | 122.1405 | -3.1815 | 118.8721 | -0.025411 | -0.069982 | 0.037516 | 0.014127 | -0.016138 | 0.0085935 | -0.021518 | -0.021708 | -0.0084865 | 0.022367 | 0.056927 | -0.00081186 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.078201 | 0.27932 | -0.11342 | 0.088043 | 0.096512 | -0.028879 | 0.029566 | 0.19685 | 0.20005 | -0.18246 | 3.068 | -118.765 | 3.1642 | 3.173 | 0.10502 | -118.7939 | -118.5927 | 2.999 | -118.8425 | 3.2695 | 3.1526 | 0.15358 | -118.6752 | -118.672 | 3.2885 | 3.2597 | 3.4608 | 3.2149 | -118.9855 | 3.211 | 3.3783 | 3.3815 | 3.278 | -119.0545
5705.1094 | 122.081 | -3.1586 | 118.9453 | -0.010149 | -0.07041 | 0.038157 | 0.014554 | -0.015924 | 0.0088073 | -0.021518 | -0.021708 | -0.0082729 | 0.022581 | 0.056286 | -0.00059826 | -0.021844 | 0.033457 | -0.003831 | 0.10249 | 0.078201 | 0.28848 | -0.11342 | 0.083464 | 0.087354 | -0.028879 | 0.034145 | 0.19227 | 0.1909 | -0.18704 | 3.0451 | -118.8428 | 3.1367 | 3.1547 | 0.10959 | -118.8671 | -118.6568 | 2.9715 | -118.9112 | 3.242 | 3.1297 | 0.15816 | -118.753 | -118.7544 | 3.2611 | 3.2368 | 3.447 | 3.192 | -119.0587 | 3.1927 | 3.3508 | 3.3495 | 3.2459 | -119.1324
5706.875 | 122.1497 | -3.1586 | 118.9133 | -0.01778 | -0.069982 | 0.037516 | 0.01434 | -0.015924 | 0.0088073 | -0.021518 | -0.021494 | -0.0084865 | 0.022581 | 0.056713 | -0.00038466 | -0.008109 | 0.0243 | -0.003831 | 0.10707 | 0.08278 | 0.2839 | -0.10885 | 0.083464 | 0.091933 | -0.0243 | 0.038723 | 0.19227 | 0.19547 | -0.1962 | 3.0497 | -118.8062 | 3.1505 | 3.1547 | 0.10502 | -118.8305 | -118.6294 | 2.9624 | -118.8745 | 3.242 | 3.1343 | 0.1719 | -118.721 | -118.7178 | 3.2656 | 3.2413 | 3.4425 | 3.1829 | -119.0221 | 3.1973 | 3.3508 | 3.354 | 3.2505 | -119.1095
5708.5781 | 122.0993 | -3.1677 | 118.927 | -0.010149 | -0.069982 | 0.037943 | 0.01434 | -0.015711 | 0.0092345 | -0.021518 | -0.021494 | -0.0084865 | 0.022794 | 0.056713 | -0.00081186 | -0.021844 | 0.028878 | -0.003831 | 0.10707 | 0.08278 | 0.2839 | -0.10427 | 0.083464 | 0.087354 | -0.0243 | 0.038723 | 0.19227 | 0.18632 | -0.18704 | 3.0635 | -118.8199 | 3.1459 | 3.1639 | 0.10044 | -118.8442 | -118.6431 | 2.9807 | -118.8883 | 3.2512 | 3.1434 | 0.16274 | -118.7347 | -118.7407 | 3.2748 | 3.2505 | 3.4516 | 3.1966 | -119.0313 | 3.2064 | 3.36 | 3.354 | 3.2551 | -119.114
5710.3438 | 122.1039 | -3.1586 | 118.9362 | -0.010149 | -0.070196 | 0.037943 | 0.014127 | -0.016138 | 0.0090209 | -0.021518 | -0.021708 | -0.0084865 | 0.022153 | 0.056499 | -0.00081186 | -0.017266 | 0.028878 | -0.003831 | 0.10249 | 0.08278 | 0.27932 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.034145 | 0.18769 | 0.1909 | -0.18704 | 3.0497 | -118.8337 | 3.1413 | 3.1547 | 0.10502 | -118.8534 | -118.6568 | 2.9715 | -118.902 | 3.2375 | 3.1251 | 0.15358 | -118.7485 | -118.7453 | 3.2611 | 3.2413 | 3.4379 | 3.1874 | -119.045 | 3.1927 | 3.3463 | 3.3495 | 3.2459 | -119.1232
5712.0469 | 122.1542 | -3.1769 | 118.9041 | -0.010149 | -0.07041 | 0.037516 | 0.01434 | -0.015924 | 0.0090209 | -0.029148 | -0.021708 | -0.0082729 | 0.022794 | 0.056713 | -0.00081186 | -0.017266 | 0.0243 | -0.008409 | 0.097912 | 0.08278 | 0.2839 | -0.118 | 0.078886 | 0.091933 | -0.0243 | 0.034145 | 0.18769 | 0.18632 | -0.18704 | 3.0589 | -118.8062 | 3.1596 | 3.1685 | 0.10959 | -118.8213 | -118.6202 | 2.9898 | -118.87 | 3.2558 | 3.1526 | 0.16274 | -118.7164 | -118.7178 | 3.2748 | 3.2597 | 3.4608 | 3.2012 | -119.0221 | 3.211 | 3.3646 | 3.3632 | 3.2688 | -119.0912
5713.7969 | 122.1085 | -3.2043 | 118.8995 | -0.010149 | -0.070196 | 0.037729 | 0.014127 | -0.015497 | 0.0090209 | -0.036779 | -0.021708 | -0.0084865 | 0.022367 | 0.056713 | -0.00038466 | -0.017266 | 0.028878 | -0.008409 | 0.10707 | 0.078201 | 0.2839 | -0.10427 | 0.078886 | 0.091933 | -0.028879 | 0.034145 | 0.18769 | 0.1909 | -0.18704 | 3.1001 | -118.7925 | 3.1871 | 3.1959 | 0.095859 | -118.8213 | -118.6156 | 3.0173 | -118.8654 | 3.2832 | 3.1755 | 0.15816 | -118.7118 | -118.7086 | 3.3114 | 3.2825 | 3.4882 | 3.2332 | -119.0038 | 3.2385 | 3.392 | 3.3952 | 3.2963 | -119.0866
5715.5781 | 122.1588 | -3.2364 | 118.84 | -0.025411 | -0.07041 | 0.038157 | 0.014554 | -0.015924 | 0.0090209 | -0.0062567 | -0.021708 | -0.0089137 | 0.022581 | 0.056713 | -0.00081186 | -0.017266 | 0.028878 | 0.000747 | 0.10249 | 0.087359 | 0.27932 | -0.11342 | 0.078886 | 0.091933 | -0.0243 | 0.034145 | 0.18769 | 0.1909 | -0.1962 | 3.123 | -118.7375 | 3.2191 | 3.2371 | 0.11417 | -118.7527 | -118.5607 | 3.0402 | -118.8059 | 3.3153 | 3.2121 | 0.1719 | -118.6523 | -118.6491 | 3.3389 | 3.3237 | 3.5157 | 3.2653 | -118.9535 | 3.2705 | 3.4241 | 3.4273 | 3.3283 | -119.0362
5717.2812 | 122.2229 | -3.2089 | 118.8217 | -0.01778 | -0.070196 | 0.037729 | 0.013913 | -0.016138 | 0.0088073 | -0.021518 | -0.02128 | -0.0084865 | 0.022367 | 0.056927 | -0.00038466 | -0.017266 | 0.033457 | -0.003831 | 0.10249 | 0.087359 | 0.2839 | -0.118 | 0.088043 | 0.087354 | -0.033458 | 0.038723 | 0.18769 | 0.19547 | -0.19162 | 3.0909 | -118.7192 | 3.1917 | 3.2051 | 0.11417 | -118.7344 | -118.5378 | 3.0173 | -118.783 | 3.297 | 3.1755 | 0.15816 | -118.634 | -118.6262 | 3.3114 | 3.2963 | 3.4928 | 3.2424 | -118.9397 | 3.2476 | 3.3966 | 3.4044 | 3.2963 | -119.0133
5719.0469 | 122.2458 | -3.2181 | 118.8263 | -0.010149 | -0.070196 | 0.037516 | 0.01434 | -0.016138 | 0.0085935 | -0.021518 | -0.021708 | -0.0082729 | 0.022367 | 0.056499 | -0.00081186 | -0.026423 | 0.038035 | -0.003831 | 0.10249 | 0.078201 | 0.27932 | -0.10885 | 0.083464 | 0.087354 | -0.033458 | 0.034145 | 0.18311 | 0.19547 | -0.19162 | 3.1092 | -118.7238 | 3.1917 | 3.2142 | 0.10502 | -118.7481 | -118.547 | 3.0265 | -118.7921 | 3.3015 | 3.1846 | 0.15816 | -118.6432 | -118.6308 | 3.3206 | 3.2963 | 3.4974 | 3.2561 | -118.9351 | 3.2522 | 3.4012 | 3.4136 | 3.3054 | -119.0179
5720.75 | 122.2321 | -3.2135 | 118.84 | -0.010149 | -0.070196 | 0.037516 | 0.014127 | -0.016138 | 0.0083799 | -0.021518 | -0.021494 | -0.0084865 | 0.022367 | 0.056713 | -0.0010255 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.078201 | 0.27932 | -0.10885 | 0.083464 | 0.078197 | -0.033458 | 0.034145 | 0.18769 | 0.18174 | -0.19162 | 3.1047 | -118.733 | 3.1962 | 3.2051 | 0.10044 | -118.7618 | -118.5607 | 3.0219 | -118.8059 | 3.297 | 3.18 | 0.15816 | -118.6523 | -118.6583 | 3.3206 | 3.2917 | 3.4928 | 3.247 | -118.9489 | 3.2476 | 3.4012 | 3.3952 | 3.2917 | -119.0316
5722.5156 | 121.3577 | -39.6149 | 80.8685 | -0.025411 | -0.069982 | 0.037943 | 0.01434 | -0.016138 | 0.0085935 | -0.021518 | -0.021708 | -0.0080591 | 0.022367 | 0.056499 | -0.00059826 | -0.017266 | 0.033457 | 0.000747 | 0.10707 | 0.073622 | 0.2839 | -0.10427 | 0.088043 | 0.091933 | -0.028879 | 0.034145 | 0.19227 | 0.1909 | -0.18246 | 39.5106 | -80.7615 | 39.5976 | 39.6156 | 0.10501 | -80.7949 | -80.5846 | 39.4324 | -80.8344 | 39.7029 | 39.586 | 0.15358 | -80.6763 | -80.6776 | 39.7219 | 39.6885 | 39.8988 | 39.6483 | -80.9728 | 39.649 | 39.8071 | 39.8058 | 39.7068 | -81.051
5724.2188 | 120.7123 | -11.6592 | 109.7397 | -0.010149 | -0.069982 | 0.037516 | 0.01434 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0087001 | 0.022581 | 0.056927 | -0.00081186 | -0.021844 | 0.028878 | 0.000747 | 0.10249 | 0.08278 | 0.2839 | -0.118 | 0.088043 | 0.091933 | -0.033458 | 0.034145 | 0.19685 | 0.18632 | -0.18246 | 11.5412 | -109.6372 | 11.6374 | 11.66 | 0.11875 | -109.6569 | -109.4558 | 11.4768 | -109.7055 | 11.7473 | 11.6258 | 0.14901 | -109.5428 | -109.5534 | 11.7617 | 11.742 | 11.9431 | 11.6881 | -109.8577 | 11.6934 | 11.8561 | 11.8456 | 11.7512 | -109.9221
5725.9844 | 121.6049 | -10.3317 | 111.1633 | -0.010149 | -0.070196 | 0.037943 | 0.01434 | -0.015924 | 0.0088073 | -0.021518 | -0.02128 | -0.0087001 | 0.022153 | 0.056927 | -0.00081186 | -0.026423 | 0.033457 | -0.003831 | 0.10707 | 0.08278 | 0.28848 | -0.10427 | 0.088043 | 0.087354 | -0.038036 | 0.034145 | 0.18311 | 0.1909 | -0.18704 | 10.2275 | -111.0563 | 10.3053 | 10.3279 | 0.10044 | -111.0806 | -110.8748 | 10.1447 | -111.1292 | 10.4198 | 10.2937 | 0.14901 | -110.9802 | -110.9724 | 10.4388 | 10.4145 | 10.6202 | 10.3652 | -111.2676 | 10.3659 | 10.5148 | 10.5226 | 10.4191 | -111.3504
5727.6875 | 121.6049 | -9.819 | 111.6074 | -0.01778 | -0.069982 | 0.037943 | 0.014554 | -0.016138 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.022581 | 0.056713 | -0.00038466 | -0.021844 | 0.0243 | -0.003831 | 0.10249 | 0.073622 | 0.2839 | -0.11342 | 0.074307 | 0.091933 | -0.033458 | 0.034145 | 0.19685 | 0.1909 | -0.18704 | 9.7056 | -111.5049 | 9.7972 | 9.8152 | 0.10959 | -111.5337 | -111.3235 | 9.632 | -111.5732 | 9.8933 | 9.7856 | 0.15358 | -111.4105 | -111.4165 | 9.9215 | 9.8927 | 10.1029 | 9.8433 | -111.7208 | 9.8532 | 10.0159 | 10.0099 | 9.911 | -111.7944
5729.4531 | 121.7377 | -11.0046 | 110.5453 | -0.0025182 | -0.070196 | 0.037943 | 0.014554 | -0.016138 | 0.0092345 | -0.021518 | -0.021708 | -0.0084865 | 0.022367 | 0.056713 | -0.0010255 | -0.021844 | 0.028878 | -0.008409 | 0.11165 | 0.078201 | 0.27932 | -0.11342 | 0.083464 | 0.087354 | -0.028879 | 0.038723 | 0.18311 | 0.19547 | -0.18246 | 10.8912 | -110.4337 | 10.9828 | 10.9962 | 0.10502 | -110.4671 | -110.266 | 10.8222 | -110.5066 | 11.0881 | 10.9758 | 0.15358 | -110.3622 | -110.3499 | 11.1163 | 11.0828 | 11.284 | 11.0335 | -110.6588 | 11.0434 | 11.1878 | 11.2001 | 11.092 | -110.7278
5731.1562 | 121.0922 | -19.6152 | 102.475 | -0.0025182 | -0.070196 | 0.037943 | 0.014554 | -0.015924 | 0.0088073 | -0.013887 | -0.02128 | -0.0084865 | 0.022367 | 0.056713 | -0.00059826 | -0.021844 | 0.038035 | -0.003831 | 0.10249 | 0.087359 | 0.27932 | -0.118 | 0.088043 | 0.087354 | -0.028879 | 0.038723 | 0.18311 | 0.18632 | -0.19162 | 19.4972 | -102.3725 | 19.5933 | 19.6113 | 0.11417 | -102.3876 | -102.1957 | 19.4236 | -102.4363 | 19.7032 | 19.5863 | 0.16274 | -102.2919 | -102.2887 | 19.7177 | 19.7025 | 19.8945 | 19.6532 | -102.593 | 19.6539 | 19.7983 | 19.8015 | 19.7025 | -102.6666
5732.9219 | 121.3989 | -14.2914 | 107.4371 | -0.01778 | -0.070196 | 0.037729 | 0.01434 | -0.016138 | 0.0090209 | -0.021518 | -0.021494 | -0.0082729 | 0.022153 | 0.056927 | -0.00081186 | -0.017266 | 0.038035 | -0.003831 | 0.10707 | 0.087359 | 0.27932 | -0.11342 | 0.083464 | 0.087354 | -0.0243 | 0.034145 | 0.18769 | 0.1909 | -0.18704 | 14.178 | -107.3301 | 14.2741 | 14.2876 | 0.10959 | -107.3498 | -107.1578 | 14.1043 | -107.403 | 14.3748 | 14.2671 | 0.16274 | -107.2494 | -107.2462 | 14.3985 | 14.3787 | 14.5707 | 14.3294 | -107.5506 | 14.3255 | 14.4791 | 14.4823 | 14.3787 | -107.6242
5734.6406 | 121.8246 | -10.3226 | 111.3007 | -0.01778 | -0.07041 | 0.037729 | 0.01434 | -0.015711 | 0.0088073 | -0.029148 | -0.02128 | -0.0084865 | 0.022367 | 0.056713 | -0.00059826 | -0.026423 | 0.028878 | -0.003831 | 0.10707 | 0.078201 | 0.27932 | -0.099689 | 0.083464 | 0.087354 | -0.038036 | 0.034145 | 0.19227 | 0.1909 | -0.18704 | 10.2229 | -111.1936 | 10.2961 | 10.3187 | 0.095858 | -111.2225 | -111.0213 | 10.1355 | -111.2665 | 10.406 | 10.2845 | 0.14901 | -111.1084 | -111.1098 | 10.4296 | 10.4008 | 10.6019 | 10.3514 | -111.4003 | 10.3567 | 10.5148 | 10.5135 | 10.4099 | -111.4877
5736.4062 | 121.669 | -10.5698 | 111.1084 | -0.010149 | -0.069982 | 0.037729 | 0.01434 | -0.015924 | 0.0088073 | -0.029148 | -0.021708 | -0.0082729 | 0.022153 | 0.05714 | -0.00059826 | -0.012688 | 0.033457 | -0.008409 | 0.097912 | 0.078201 | 0.2839 | -0.10885 | 0.083464 | 0.091933 | -0.028879 | 0.029566 | 0.18769 | 0.19547 | -0.1962 | 10.4609 | -111.0105 | 10.5571 | 10.5614 | 0.10044 | -111.0302 | -110.8245 | 10.3736 | -111.0788 | 10.6532 | 10.5409 | 0.16732 | -110.9207 | -110.9129 | 10.6677 | 10.648 | 10.8537 | 10.6032 | -111.2172 | 10.5993 | 10.7575 | 10.7652 | 10.6617 | -111.3046
5738.1719 | 121.843 | -25.6531 | 95.9244 | -0.025411 | -0.07041 | 0.037729 | 0.014127 | -0.015711 | 0.0090209 | -0.029148 | -0.021708 | -0.0082729 | 0.022153 | 0.056927 | -0.00059826 | -0.021844 | 0.028878 | -0.003831 | 0.10249 | 0.08278 | 0.2839 | -0.10885 | 0.083464 | 0.087354 | -0.038036 | 0.034145 | 0.18769 | 0.1909 | -0.18704 | 25.5442 | -95.8219 | 25.6312 | 25.6492 | 0.10502 | -95.8416 | -95.6405 | 25.466 | -95.8902 | 25.7365 | 25.615 | 0.14901 | -95.7367 | -95.7335 | 25.7556 | 25.7359 | 25.937 | 25.682 | -96.0332 | 25.6872 | 25.8408 | 25.844 | 25.7404 | -96.1114
5739.9375 | 121.7972 | -26.0422 | 95.549 | -0.01778 | -0.07041 | 0.037729 | 0.014127 | -0.015924 | 0.0090209 | -0.021518 | -0.021494 | -0.0084865 | 0.022153 | 0.05714 | -0.00059826 | -0.017266 | 0.028878 | 0.000747 | 0.10707 | 0.078201 | 0.2839 | -0.11342 | 0.074307 | 0.091933 | -0.0243 | 0.038723 | 0.18769 | 0.18632 | -0.19162 | 25.9288 | -95.4419 | 26.0249 | 26.0429 | 0.11417 | -95.4708 | -95.2651 | 25.8506 | -95.5103 | 26.1165 | 26.0179 | 0.16732 | -95.3613 | -95.3627 | 26.1492 | 26.1204 | 26.3261 | 26.0711 | -95.6624 | 26.0809 | 26.2299 | 26.2285 | 26.1341 | -95.7406
5741.7031 | 121.8613 | -17.7017 | 103.9856 | -0.010149 | -0.069982 | 0.037943 | 0.01434 | -0.015711 | 0.0088073 | -0.013887 | -0.02128 | -0.0082729 | 0.022794 | 0.056927 | -0.00081186 | -0.021844 | 0.028878 | 0.000747 | 0.10249 | 0.078201 | 0.2839 | -0.099689 | 0.083464 | 0.087354 | -0.033458 | 0.038723 | 0.19227 | 0.18632 | -0.18246 | 17.602 | -103.8831 | 17.6799 | 17.7025 | 0.10044 | -103.9074 | -103.7017 | 17.5193 | -103.9469 | 17.7852 | 17.6683 | 0.14901 | -103.7933 | -103.7993 | 17.8042 | 17.7799 | 17.9856 | 17.7306 | -104.0853 | 17.7404 | 17.894 | 17.888 | 17.7891 | -104.1681
5743.4062 | 121.17 | -13.9389 | 107.7942 | -0.010149 | -0.070623 | 0.037943 | 0.014127 | -0.015924 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.056713 | -0.00081186 | -0.012688 | 0.038035 | -0.003831 | 0.10249 | 0.069043 | 0.2839 | -0.118 | 0.083464 | 0.082776 | -0.028879 | 0.043302 | 0.18769 | 0.18632 | -0.18704 | 13.8209 | -107.6917 | 13.9262 | 13.9351 | 0.11417 | -107.7251 | -107.5103 | 13.7519 | -107.7509 | 14.0224 | 13.91 | 0.15816 | -107.6065 | -107.6079 | 14.0414 | 14.0079 | 14.2228 | 13.9769 | -107.9122 | 13.9822 | 14.1266 | 14.1252 | 14.0217 | -107.9812
5745.2188 | 121.7148 | -14.2181 | 107.5424 | -0.010149 | -0.07041 | 0.037943 | 0.01434 | -0.015711 | 0.0088073 | -0.013887 | -0.021494 | -0.0082729 | 0.022153 | 0.056927 | -0.00081186 | -0.017266 | 0.038035 | -0.008409 | 0.11165 | 0.08278 | 0.2839 | -0.11342 | 0.088043 | 0.087354 | -0.028879 | 0.038723 | 0.18769 | 0.18174 | -0.19162 | 14.1047 | -107.4308 | 14.2009 | 14.2097 | 0.10502 | -107.4596 | -107.2585 | 14.0265 | -107.5037 | 14.3062 | 14.1893 | 0.16274 | -107.3547 | -107.3607 | 14.3298 | 14.3009 | 14.502 | 14.2562 | -107.6558 | 14.2569 | 14.4058 | 14.3999 | 14.3055 | -107.734
5746.9375 | 121.9391 | -17.6514 | 103.8437 | -0.01778 | -0.07041 | 0.037729 | 0.014127 | -0.016138 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022367 | 0.056713 | -0.00081186 | -0.026423 | 0.028878 | -0.003831 | 0.10249 | 0.078201 | 0.28848 | -0.10885 | 0.074307 | 0.091933 | -0.028879 | 0.024988 | 0.18769 | 0.17716 | -0.18704 | 17.5425 | -103.7412 | 17.6249 | 17.6475 | 0.10502 | -103.7655 | -103.5552 | 17.4643 | -103.8187 | 17.7257 | 17.6225 | 0.15816 | -103.656 | -103.6665 | 17.7539 | 17.7296 | 17.9398 | 17.6802 | -103.9525 | 17.6764 | 17.8391 | 17.8285 | 17.7433 | -104.0307
5748.7031 | 121.9482 | -23.5886 | 98.0621 | -0.010149 | -0.07041 | 0.037943 | 0.01434 | -0.015711 | 0.0090209 | -0.021518 | -0.02128 | -0.0084865 | 0.022153 | 0.056713 | -0.00059826 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.078201 | 0.29306 | -0.10427 | 0.088043 | 0.087354 | -0.033458 | 0.034145 | 0.19227 | 0.18632 | -0.19162 | 23.4843 | -97.9551 | 23.5713 | 23.5802 | 0.095859 | -97.9839 | -97.7691 | 23.3969 | -98.028 | 23.6766 | 23.5551 | 0.15816 | -97.8699 | -97.8758 | 23.6956 | 23.6668 | 23.8816 | 23.622 | -98.1664 | 23.6227 | 23.7808 | 23.7749 | 23.6759 | -98.2538
5750.4375 | 121.9025 | -31.1234 | 90.5319 | -0.010149 | -0.069982 | 0.037943 | 0.014554 | -0.015497 | 0.0088073 | -0.029148 | -0.021708 | -0.0084865 | 0.022153 | 0.056927 | -0.00059826 | -0.021844 | 0.033457 | 0.000747 | 0.10249 | 0.078201 | 0.28848 | -0.10885 | 0.074307 | 0.087354 | -0.028879 | 0.029566 | 0.18769 | 0.1909 | -0.18704 | 31.0145 | -90.4294 | 31.1015 | 31.1241 | 0.10959 | -90.4537 | -90.2434 | 30.9363 | -90.5024 | 31.1977 | 31.0945 | 0.15816 | -90.3442 | -90.341 | 31.2258 | 31.2016 | 31.4118 | 31.1568 | -90.6408 | 31.1529 | 31.311 | 31.3142 | 31.2107 | -90.719
5752.2031 | 121.9025 | -28.0289 | 93.6356 | -0.010149 | -0.069982 | 0.037729 | 0.014554 | -0.015924 | 0.0090209 | -0.036779 | -0.021067 | -0.0084865 | 0.02194 | 0.056499 | -0.0010255 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.08278 | 0.2839 | -0.10885 | 0.074307 | 0.091933 | -0.033458 | 0.034145 | 0.18769 | 0.18632 | -0.19162 | 27.92 | -93.5285 | 28.0116 | 28.0205 | 0.10044 | -93.5528 | -93.3517 | 27.8372 | -93.6014 | 28.1032 | 27.9954 | 0.15816 | -93.4479 | -93.4492 | 28.1359 | 28.1117 | 28.3128 | 28.0623 | -93.7444 | 28.063 | 28.2166 | 28.2152 | 28.1208 | -93.8272
5753.9688 | 121.9391 | -28.2669 | 93.4708 | -0.01778 | -0.069769 | 0.037729 | 0.01434 | -0.015924 | 0.0088073 | -0.029148 | -0.021494 | -0.0082729 | 0.022153 | 0.056927 | -0.00059826 | -0.026423 | 0.038035 | -0.003831 | 0.10249 | 0.087359 | 0.28848 | -0.11342 | 0.083464 | 0.091933 | -0.0243 | 0.029566 | 0.18769 | 0.18174 | -0.1962 | 28.1535 | -93.3683 | 28.2405 | 28.2631 | 0.10959 | -93.3834 | -93.1823 | 28.0707 | -93.4412 | 28.3504 | 28.2426 | 0.1719 | -93.2831 | -93.289 | 28.3694 | 28.3543 | 28.5554 | 28.3049 | -93.5842 | 28.2965 | 28.4546 | 28.4486 | 28.3588 | -93.667
5755.75 | 121.312 | -43.7119 | 84.6542 | -0.010149 | -0.070196 | 0.037729 | 0.01434 | -0.015924 | 0.0085935 | -0.013887 | -0.021708 | -0.0080591 | 0.022581 | 0.057354 | -0.00081186 | -0.012688 | 0.028878 | -0.003831 | 0.097912 | 0.078201 | 0.2839 | -0.118 | 0.083464 | 0.091933 | -0.019721 | 0.038723 | 0.18769 | 0.1909 | -0.18704 | 43.5938 | -84.5563 | 43.6992 | 43.708 | 0.11417 | -84.576 | -84.3703 | 43.5248 | -84.6155 | 43.7953 | 43.6921 | 0.16732 | -84.4665 | -84.4633 | 43.8098 | 43.7901 | 43.9958 | 43.7407 | -84.7722 | 43.7506 | 43.8995 | 43.9027 | 43.8038 | -84.8413
5757.5156 | 122.0856 | -118.364 | 3.2272 | -0.01778 | -0.070196 | 0.037729 | 0.014554 | -0.015924 | 0.0090209 | -0.021518 | -0.021921 | -0.0082729 | 0.022153 | 0.056927 | -0.00059826 | -0.021844 | 0.033457 | -0.003831 | 0.097912 | 0.078201 | 0.28848 | -0.10427 | 0.088043 | 0.091933 | -0.028879 | 0.038723 | 0.19227 | 0.1909 | -0.18246 | 118.2597 | -3.1293 | 118.3421 | 118.3601 | 0.10044 | -3.149 | -2.9388 | 118.1815 | -3.1885 | 118.452 | 118.3351 | 0.15358 | -3.035 | -3.0363 | 118.4619 | 118.4422 | 118.6524 | 118.3974 | -3.3315 | 118.4027 | 118.5562 | 118.5548 | 118.4559 | -3.4097
5759.2812 | 122.1497 | -119.6915 | 1.9913 | -0.01778 | -0.069982 | 0.037943 | 0.014127 | -0.016138 | 0.0090209 | -0.029148 | -0.021494 | -0.0082729 | 0.022367 | 0.056713 | -0.00059826 | -0.012688 | 0.038035 | 0.000747 | 0.10249 | 0.078201 | 0.27932 | -0.10427 | 0.078886 | 0.082776 | -0.033458 | 0.038723 | 0.19227 | 0.1909 | -0.18246 | 119.5872 | -1.8888 | 119.6788 | 119.6922 | 0.10501 | -1.9131 | -1.7119 | 119.509 | -1.9525 | 119.7704 | 119.658 | 0.14901 | -1.799 | -1.8004 | 119.794 | 119.7697 | 119.9708 | 119.7295 | -2.0955 | 119.7302 | 119.8837 | 119.8824 | 119.7742 | -2.1737
5760.9844 | 122.0627 | -118.0298 | 3.6758 | -0.0025182 | -0.070196 | 0.037943 | 0.01434 | -0.015924 | 0.0085935 | -0.021518 | -0.02128 | -0.0087001 | 0.022367 | 0.056927 | -0.00038466 | -0.012688 | 0.033457 | 0.000747 | 0.10707 | 0.087359 | 0.29306 | -0.10885 | 0.083464 | 0.091933 | -0.033458 | 0.034145 | 0.18311 | 0.1909 | -0.18704 | 117.9209 | -3.5688 | 118.0171 | 118.0305 | 0.10959 | -3.5885 | -3.3828 | 117.8427 | -3.6417 | 118.1132 | 117.9963 | 0.15358 | -3.4927 | -3.4849 | 118.1369 | 118.1171 | 118.3228 | 118.0632 | -3.7847 | 118.0639 | 118.2129 | 118.2207 | 118.1217 | -3.8629
5762.75 | 122.1451 | -118.428 | 3.2547 | -0.010149 | -0.07041 | 0.037943 | 0.01434 | -0.016138 | 0.0088073 | -0.021518 | -0.021708 | -0.0082729 | 0.022153 | 0.057354 | -0.00059826 | -0.026423 | 0.038035 | 0.000747 | 0.11165 | 0.08278 | 0.28848 | -0.10885 | 0.078886 | 0.091933 | -0.028879 | 0.043302 | 0.18769 | 0.18174 | -0.18704 | 118.3192 | -3.1431 | 118.4016 | 118.4288 | 0.10959 | -3.1719 | -2.9662 | 118.241 | -3.2114 | 118.5069 | 118.3992 | 0.15816 | -3.067 | -3.073 | 118.5397 | 118.5108 | 118.7165 | 118.4661 | -3.3635 | 118.4713 | 118.6157 | 118.6098 | 118.52 | -3.4417
5764.5156 | 122.0123 | -118.7027 | 3.1357 | -0.0025182 | -0.07041 | 0.037516 | 0.014127 | -0.015924 | 0.0088073 | -0.029148 | -0.02128 | -0.0080591 | 0.022367 | 0.056713 | -0.00059826 | -0.017266 | 0.042614 | -0.003831 | 0.11165 | 0.087359 | 0.28848 | -0.10427 | 0.078886 | 0.087354 | -0.033458 | 0.034145 | 0.18769 | 0.18632 | -0.19162 | 118.5984 | -3.024 | 118.6854 | 118.6989 | 0.10044 | -3.0483 | -2.8472 | 118.5111 | -3.1015 | 118.7816 | 118.6692 | 0.15816 | -2.948 | -2.9494 | 118.8143 | 118.7901 | 118.9912 | 118.7453 | -3.2399 | 118.7368 | 118.8904 | 118.889 | 118.7901 | -3.3273
5766.2812 | 122.168 | -120.6299 | 1.0986 | -0.010149 | -0.07041 | 0.037943 | 0.014127 | -0.015711 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022153 | 0.05714 | -0.0010255 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.087359 | 0.2839 | -0.099689 | 0.078886 | 0.087354 | -0.0243 | 0.043302 | 0.18769 | 0.1909 | -0.19162 | 120.5302 | -0.99157 | 120.6126 | 120.6215 | 0.09128 | -1.0113 | -0.81473 | 120.4383 | -1.0553 | 120.7088 | 120.6056 | 0.16732 | -0.91094 | -0.90774 | 120.737 | 120.7172 | 120.9138 | 120.6633 | -1.1983 | 120.6732 | 120.8176 | 120.8208 | 120.7172 | -1.2903
5767.9844 | 122.0627 | -120.6985 | 1.1444 | -0.01778 | -0.070623 | 0.037729 | 0.01434 | -0.015924 | 0.0088073 | -0.021518 | -0.02128 | -0.0082729 | 0.022367 | 0.05714 | -0.00059826 | -0.017266 | 0.042614 | 0.000747 | 0.10249 | 0.08278 | 0.28848 | -0.10885 | 0.083464 | 0.087354 | -0.028879 | 0.029566 | 0.18769 | 0.1909 | -0.19162 | 120.5897 | -1.0419 | 120.6813 | 120.6993 | 0.10959 | -1.0616 | -0.85593 | 120.5069 | -1.1148 | 120.782 | 120.6697 | 0.16274 | -0.95672 | -0.95351 | 120.801 | 120.7813 | 120.987 | 120.7412 | -1.2533 | 120.7281 | 120.8862 | 120.8894 | 120.7859 | -1.336
5769.75 | 122.0261 | -120.7077 | 1.181 | -0.010149 | -0.070623 | 0.037516 | 0.014554 | -0.015924 | 0.0092345 | -0.0062567 | -0.021494 | -0.0082729 | 0.022153 | 0.056713 | -0.00081186 | -0.012688 | 0.038035 | 0.000747 | 0.11622 | 0.08278 | 0.28848 | -0.10427 | 0.074307 | 0.087354 | -0.028879 | 0.038723 | 0.18311 | 0.18632 | -0.19162 | 120.6034 | -1.0648 | 120.695 | 120.7084 | 0.10501 | -1.0982 | -0.89255 | 120.5161 | -1.1423 | 120.782 | 120.6788 | 0.16274 | -0.99791 | -0.99471 | 120.8239 | 120.7905 | 120.9962 | 120.7457 | -1.2853 | 120.7464 | 120.8908 | 120.894 | 120.7951 | -1.3727
5771.5156 | 122.1085 | -120.7077 | 1.149 | -0.010149 | -0.07041 | 0.037729 | 0.013913 | -0.015711 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.056927 | -0.0010255 | -0.017266 | 0.033457 | 0.000747 | 0.10707 | 0.087359 | 0.29764 | -0.11342 | 0.074307 | 0.087354 | -0.033458 | 0.029566 | 0.18311 | 0.18632 | -0.18704 | 120.5943 | -1.0419 | 120.6904 | 120.7084 | 0.11417 | -1.0616 | -0.85135 | 120.5207 | -1.1194 | 120.782 | 120.6742 | 0.15358 | -0.96587 | -0.96267 | 120.8148 | 120.7951 | 121.0053 | 120.7412 | -1.2624 | 120.7373 | 120.8908 | 120.894 | 120.7951 | -1.336
5773.2188 | 122.0993 | -120.5795 | 1.1673 | -0.010149 | -0.07041 | 0.037729 | 0.01434 | -0.016138 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022367 | 0.056927 | -0.00081186 | -0.017266 | 0.038035 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | -0.11342 | 0.083464 | 0.091933 | -0.028879 | 0.038723 | 0.18769 | 0.1909 | -0.18246 | 120.4661 | -1.0556 | 120.5623 | 120.5849 | 0.11875 | -1.0845 | -0.87882 | 120.3971 | -1.1286 | 120.663 | 120.5506 | 0.15358 | -0.9796 | -0.9764 | 120.6912 | 120.6623 | 120.868 | 120.6176 | -1.2807 | 120.6183 | 120.7672 | 120.7704 | 120.6715 | -1.3498
5774.9844 | 122.0352 | -120.3964 | 1.4923 | -0.025411 | -0.07041 | 0.037516 | 0.01434 | -0.015924 | 0.0090209 | -0.021518 | -0.02128 | -0.0084865 | 0.022367 | 0.056927 | -0.00081186 | -0.017266 | 0.028878 | -0.003831 | 0.11165 | 0.087359 | 0.27932 | -0.11342 | 0.083464 | 0.091933 | -0.028879 | 0.029566 | 0.18311 | 0.18174 | -0.19162 | 120.283 | -1.3807 | 120.3792 | 120.3926 | 0.10959 | -1.405 | -1.213 | 120.2048 | -1.4627 | 120.4799 | 120.3675 | 0.16274 | -1.3092 | -1.3106 | 120.5081 | 120.4838 | 120.6757 | 120.4253 | -1.6057 | 120.426 | 120.5795 | 120.5782 | 120.4884 | -1.6839
5776.75 | 122.1359 | -120.2637 | 1.5884 | -0.010149 | -0.070623 | 0.037729 | 0.014554 | -0.015711 | 0.0088073 | -0.029148 | -0.021494 | -0.0082729 | 0.022367 | 0.05714 | -0.00059826 | -0.021844 | 0.038035 | -0.008409 | 0.10707 | 0.08278 | 0.2839 | -0.10885 | 0.083464 | 0.087354 | -0.0243 | 0.034145 | 0.18311 | 0.18174 | -0.1962 | 120.1548 | -1.4814 | 120.2418 | 120.2553 | 0.10044 | -1.5057 | -1.3045 | 120.0675 | -1.5543 | 120.3471 | 120.2394 | 0.1719 | -1.4053 | -1.4067 | 120.3707 | 120.3465 | 120.5476 | 120.3017 | -1.6973 | 120.2978 | 120.4468 | 120.4454 | 120.351 | -1.7846
5778.5156 | 121.9986 | -120.1721 | 1.7441 | -0.01778 | -0.070837 | 0.037516 | 0.01434 | -0.016138 | 0.0085935 | -0.013887 | -0.021708 | -0.0080591 | 0.022153 | 0.056713 | -0.00081186 | -0.012688 | 0.038035 | -0.003831 | 0.11165 | 0.08278 | 0.2839 | -0.099689 | 0.083464 | 0.078197 | -0.028879 | 0.029566 | 0.19227 | 0.1909 | -0.18246 | 120.0724 | -1.6324 | 120.1594 | 120.1683 | 0.095858 | -1.6613 | -1.4602 | 119.9897 | -1.7145 | 120.2556 | 120.1432 | 0.15358 | -1.5518 | -1.5532 | 120.2838 | 120.2549 | 120.456 | 120.2102 | -1.8438 | 120.2017 | 120.3644 | 120.363 | 120.2503 | -1.9265
5780.2812 | 122.049 | -120.1263 | 1.7853 | 0.0051128 | -0.070196 | 0.037943 | 0.013913 | -0.015924 | 0.0085935 | -0.013887 | -0.021494 | -0.0082729 | 0.022153 | 0.056927 | -0.00059826 | -0.021844 | 0.033457 | 0.000747 | 0.10707 | 0.08278 | 0.2839 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.034145 | 0.18769 | 0.1909 | -0.19162 | 120.0129 | -1.6782 | 120.1045 | 120.1271 | 0.11417 | -1.7025 | -1.5014 | 119.9347 | -1.7511 | 120.2052 | 120.0929 | 0.15816 | -1.5976 | -1.5944 | 120.2334 | 120.2091 | 120.4102 | 120.1598 | -1.8987 | 120.1605 | 120.314 | 120.3172 | 120.2137 | -1.9769
5781.9844 | 122.2412 | -117.0593 | 4.6097 | -0.01778 | -0.07041 | 0.037943 | 0.01434 | -0.015924 | 0.0088073 | -0.021518 | -0.021708 | -0.0087001 | 0.022153 | 0.056499 | -0.00081186 | -0.017266 | 0.033457 | -0.003831 | 0.10249 | 0.087359 | 0.28848 | -0.10885 | 0.088043 | 0.091933 | -0.028879 | 0.038723 | 0.18311 | 0.18632 | -0.18704 | 116.9505 | -4.5072 | 117.0421 | 117.0555 | 0.10502 | -4.5223 | -4.3212 | 116.8723 | -4.571 | 117.1474 | 117.0304 | 0.15816 | -4.4266 | -4.4234 | 117.1618 | 117.1467 | 117.3478 | 117.0928 | -4.7185 | 117.098 | 117.2424 | 117.2456 | 117.1513 | -4.7967
5783.75 | 122.1725 | -116.6382 | 5.1407 | -0.010149 | -0.07041 | 0.037943 | 0.014127 | -0.015924 | 0.0088073 | -0.021518 | -0.02128 | -0.0082729 | 0.022367 | 0.056713 | -0.00081186 | -0.021844 | 0.028878 | -0.003831 | 0.10707 | 0.08278 | 0.2839 | -0.099689 | 0.074307 | 0.082776 | -0.033458 | 0.034145 | 0.18311 | 0.18632 | -0.18704 | 116.5385 | -5.0336 | 116.6163 | 116.6344 | 0.095858 | -5.0579 | -4.8568 | 116.4511 | -5.1065 | 116.7125 | 116.6047 | 0.15358 | -4.9576 | -4.9544 | 116.7453 | 116.721 | 116.9221 | 116.6671 | -5.2404 | 116.6723 | 116.8213 | 116.8245 | 116.721 | -5.3277
5785.5156 | 122.1542 | -119.0323 | 2.8152 | -0.01778 | -0.070623 | 0.037729 | 0.014127 | -0.016138 | 0.0090209 | -0.021518 | -0.021067 | -0.0082729 | 0.02194 | 0.056927 | -0.00059826 | -0.017266 | 0.033457 | -0.008409 | 0.10249 | 0.08278 | 0.28848 | -0.10427 | 0.078886 | 0.082776 | -0.033458 | 0.034145 | 0.17854 | 0.18632 | -0.18704 | 118.928 | -2.7128 | 119.015 | 119.0239 | 0.095859 | -2.7325 | -2.5268 | 118.8452 | -2.7811 | 119.1112 | 118.9988 | 0.15358 | -2.6367 | -2.6289 | 119.1348 | 119.1151 | 119.3208 | 119.0657 | -2.9195 | 119.0664 | 119.2108 | 119.2186 | 119.1151 | -3.0023
5787.2812 | 122.1497 | -119.7464 | 2.1286 | -0.025411 | -0.070837 | 0.037729 | 0.014554 | -0.015711 | 0.0088073 | -0.029148 | -0.021708 | -0.0084865 | 0.022153 | 0.056927 | -0.00059826 | -0.021844 | 0.0243 | -0.008409 | 0.11165 | 0.08278 | 0.28848 | -0.099689 | 0.083464 | 0.087354 | -0.042615 | 0.034145 | 0.18311 | 0.18174 | -0.1962 | 119.6467 | -2.017 | 119.7246 | 119.738 | 0.09128 | -2.0458 | -1.8401 | 119.5502 | -2.0945 | 119.8299 | 119.7038 | 0.15359 | -1.9455 | -1.9469 | 119.858 | 119.8292 | 120.0349 | 119.7707 | -2.2283 | 119.7805 | 119.9295 | 119.9281 | 119.8338 | -2.3248
5789 | 122.1222 | -119.7876 | 2.1286 | -0.0025182 | -0.07041 | 0.037943 | 0.014554 | -0.015711 | 0.0083799 | -0.021518 | -0.021494 | -0.0084865 | 0.022367 | 0.057354 | -0.00059826 | -0.017266 | 0.042614 | 0.000747 | 0.10707 | 0.087359 | 0.27932 | -0.099689 | 0.078886 | 0.091933 | -0.019721 | 0.034145 | 0.17396 | 0.18632 | -0.19162 | 119.6879 | -2.0215 | 119.7703 | 119.7883 | 0.10044 | -2.0412 | -1.8493 | 119.596 | -2.0945 | 119.8665 | 119.7679 | 0.1719 | -1.9546 | -1.9423 | 119.8947 | 119.875 | 120.0669 | 119.8302 | -2.2283 | 119.8217 | 119.9616 | 119.9739 | 119.8795 | -2.3202
5790.7656 | 122.2687 | -119.2108 | 2.6093 | -0.01778 | -0.070196 | 0.037729 | 0.01434 | -0.015711 | 0.0085935 | -0.013887 | -0.021494 | -0.0084865 | 0.022153 | 0.056927 | -0.00081186 | -0.017266 | 0.028878 | 0.009904 | 0.10707 | 0.078201 | 0.2839 | -0.10427 | 0.088043 | 0.087354 | -0.028879 | 0.029566 | 0.18769 | 0.18632 | -0.1962 | 119.1065 | -2.5022 | 119.1935 | 119.2207 | 0.11417 | -2.5311 | -2.3253 | 119.0146 | -2.5797 | 119.2989 | 119.1819 | 0.16732 | -2.4216 | -2.4229 | 119.3179 | 119.289 | 119.4947 | 119.2397 | -2.7135 | 119.2404 | 119.3985 | 119.3971 | 119.2982 | -2.8055
5792.5312 | 122.2458 | -119.3893 | 2.4307 | -0.0025182 | -0.07041 | 0.038157 | 0.01434 | -0.015924 | 0.0088073 | -0.029148 | -0.021494 | -0.0084865 | 0.022367 | 0.056927 | -0.00059826 | -0.012688 | 0.038035 | -0.003831 | 0.10249 | 0.078201 | 0.29306 | -0.10427 | 0.078886 | 0.082776 | -0.0243 | 0.034145 | 0.17854 | 0.1909 | -0.19162 | 119.2851 | -2.3282 | 119.3767 | 119.3855 | 0.10044 | -2.3525 | -2.1377 | 119.1977 | -2.3966 | 119.4682 | 119.365 | 0.16732 | -2.2522 | -2.2398 | 119.4918 | 119.4675 | 119.6824 | 119.4274 | -2.535 | 119.4235 | 119.5679 | 119.5802 | 119.4721 | -2.6223
5794.2344 | 122.1588 | -119.5129 | 2.3849 | -0.01778 | -0.07041 | 0.037943 | 0.014127 | -0.015924 | 0.0090209 | -0.013887 | -0.021067 | -0.0082729 | 0.022367 | 0.056713 | -0.0010255 | -0.017266 | 0.033457 | 0.000747 | 0.10707 | 0.08278 | 0.29306 | -0.10885 | 0.078886 | 0.087354 | -0.0243 | 0.024988 | 0.18311 | 0.18632 | -0.18246 | 119.4041 | -2.2779 | 119.4957 | 119.5137 | 0.10959 | -2.3022 | -2.0919 | 119.3305 | -2.36 | 119.5918 | 119.4886 | 0.15816 | -2.2018 | -2.1986 | 119.62 | 119.5957 | 119.806 | 119.5464 | -2.4938 | 119.5379 | 119.6961 | 119.6993 | 119.6003 | -2.5674
5796 | 122.0947 | -119.9387 | 2.0142 | -0.0025182 | -0.070623 | 0.037729 | 0.014127 | -0.015924 | 0.0090209 | -0.013887 | -0.021708 | -0.0082729 | 0.022367 | 0.056927 | -0.00081186 | -0.012688 | 0.033457 | -0.003831 | 0.11165 | 0.08278 | 0.28848 | -0.10427 | 0.069728 | 0.091933 | -0.033458 | 0.029566 | 0.17854 | 0.18632 | -0.18704 | 119.8344 | -1.9025 | 119.926 | 119.9348 | 0.10044 | -1.9314 | -1.7257 | 119.7516 | -1.9846 | 120.0084 | 119.9052 | 0.15358 | -1.8356 | -1.8278 | 120.0503 | 120.0214 | 120.2271 | 119.9721 | -2.1184 | 119.9682 | 120.1172 | 120.125 | 120.0306 | -2.2012
5797.7031 | 122.0947 | -120.5154 | 1.4648 | -0.010149 | -0.070623 | 0.037516 | 0.014127 | -0.015711 | 0.0090209 | -0.029148 | -0.021494 | -0.0078455 | 0.022153 | 0.05714 | -0.0010255 | -0.021844 | 0.033457 | -0.003831 | 0.10249 | 0.091937 | 0.28848 | -0.10885 | 0.074307 | 0.082776 | -0.028879 | 0.029566 | 0.17396 | 0.18174 | -0.19162 | 120.4066 | -1.3624 | 120.4936 | 120.5116 | 0.10502 | -1.3729 | -1.1764 | 120.3238 | -1.4353 | 120.5897 | 120.4866 | 0.16274 | -1.2909 | -1.2831 | 120.6179 | 120.6074 | 120.8039 | 120.5489 | -1.5737 | 120.545 | 120.6894 | 120.6972 | 120.5982 | -1.6565
5799.4531 | 122.1817 | -117.3981 | 4.5181 | -0.010149 | -0.070623 | 0.037729 | 0.014127 | -0.015924 | 0.0088073 | -0.021518 | -0.021494 | -0.0084865 | 0.022367 | 0.05714 | -0.00038466 | -0.012688 | 0.028878 | -0.008409 | 0.10249 | 0.087359 | 0.2839 | -0.11342 | 0.074307 | 0.087354 | -0.033458 | 0.024988 | 0.18311 | 0.18174 | -0.18704 | 117.2846 | -4.4156 | 117.3854 | 117.3897 | 0.10502 | -4.4308 | -4.2342 | 117.211 | -4.4931 | 117.4724 | 117.3646 | 0.15358 | -4.335 | -4.3364 | 117.5006 | 117.4854 | 117.682 | 117.4269 | -4.6316 | 117.4231 | 117.5812 | 117.5798 | 117.4854 | -4.7052
5801.1562 | 122.1954 | -120.5887 | 1.2909 | -0.010149 | -0.070623 | 0.037729 | 0.014127 | -0.015711 | 0.0083799 | -0.013887 | -0.02128 | -0.0084865 | 0.022581 | 0.05714 | -0.0010255 | -0.012688 | 0.033457 | -0.003831 | 0.10707 | 0.087359 | 0.28848 | -0.10885 | 0.078886 | 0.087354 | -0.038036 | 0.034145 | 0.17854 | 0.17258 | -0.19162 | 120.4798 | -1.1838 | 120.576 | 120.5849 | 0.10502 | -1.2035 | -1.0024 | 120.3971 | -1.2567 | 120.6676 | 120.5506 | 0.15359 | -1.1124 | -1.1183 | 120.6958 | 120.676 | 120.8772 | 120.6221 | -1.3997 | 120.6228 | 120.7672 | 120.7613 | 120.676 | -1.4825
5802.9219 | 122.1451 | -120.8221 | 1.1261 | -0.010149 | -0.070623 | 0.037516 | 0.01434 | -0.015711 | 0.0088073 | -0.013887 | -0.02128 | -0.0084865 | 0.022367 | 0.057354 | -0.00081186 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.08278 | 0.29306 | -0.10885 | 0.078886 | 0.087354 | -0.028879 | 0.029566 | 0.17396 | 0.17716 | -0.18704 | 120.7133 | -1.019 | 120.8049 | 120.8183 | 0.10502 | -1.0433 | -0.83304 | 120.6351 | -1.0965 | 120.901 | 120.7933 | 0.15816 | -0.95214 | -0.94894 | 120.9292 | 120.9049 | 121.1152 | 120.8556 | -1.2349 | 120.8517 | 120.9961 | 120.9993 | 120.9095 | -1.3131
5804.6875 | 122.1725 | -120.9091 | 1.0712 | -0.0025182 | -0.070623 | 0.037729 | 0.01434 | -0.015711 | 0.0085935 | -0.029148 | -0.021494 | -0.0084865 | 0.022367 | 0.057354 | -0.00059826 | -0.012688 | 0.038035 | 0.000747 | 0.11165 | 0.08278 | 0.28848 | -0.10885 | 0.074307 | 0.087354 | -0.028879 | 0.034145 | 0.17396 | 0.18632 | -0.1962 | 120.8003 | -0.95952 | 120.8964 | 120.9099 | 0.10959 | -0.98839 | -0.78269 | 120.7129 | -1.037 | 120.9834 | 120.8802 | 0.16732 | -0.89721 | -0.88485 | 121.0208 | 120.9919 | 121.1976 | 120.9472 | -1.18 | 120.9433 | 121.0831 | 121.0954 | 120.9965 | -1.2674
5806.3906 | 122.0901 | -120.0531 | 1.9455 | -0.010149 | -0.070623 | 0.037943 | 0.014127 | -0.016138 | 0.0085935 | -0.013887 | -0.02128 | -0.0084865 | 0.022153 | 0.057354 | -0.00059826 | -0.008109 | 0.038035 | -0.003831 | 0.11165 | 0.08278 | 0.28848 | -0.10427 | 0.083464 | 0.091933 | -0.038036 | 0.024988 | 0.18311 | 0.18174 | -0.1962 | 119.9488 | -1.8338 | 120.045 | 120.0493 | 0.10044 | -1.8627 | -1.657 | 119.8569 | -1.9205 | 120.1366 | 120.0151 | 0.15816 | -1.7624 | -1.7638 | 120.1647 | 120.1359 | 120.3416 | 120.0911 | -2.0498 | 120.0781 | 120.2362 | 120.2348 | 120.145 | -2.1417
5808.1719 | 122.1863 | -118.895 | 3.1952 | -0.010149 | -0.07041 | 0.037943 | 0.01434 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0082729 | 0.022153 | 0.057568 | -0.0010255 | -0.017266 | 0.033457 | 0.005325 | 0.10707 | 0.087359 | 0.29306 | -0.10885 | 0.083464 | 0.078197 | -0.038036 | 0.024988 | 0.18311 | 0.18632 | -0.19162 | 118.7861 | -3.0881 | 118.8777 | 118.9003 | 0.11417 | -3.1078 | -2.9021 | 118.7033 | -3.1702 | 118.9784 | 118.8569 | 0.15359 | -3.0121 | -3.0089 | 119.002 | 118.9823 | 119.188 | 118.9284 | -3.304 | 118.9199 | 119.0781 | 119.0813 | 118.9732 | -3.3868
5809.875 | 122.2549 | -120.8817 | 1.03 | -0.0025182 | -0.07041 | 0.037516 | 0.013913 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0084865 | 0.022367 | 0.057354 | -0.00059826 | -0.017266 | 0.038035 | 0.000747 | 0.11622 | 0.08278 | 0.29306 | -0.10885 | 0.083464 | 0.082776 | -0.033458 | 0.029566 | 0.19227 | 0.17716 | -0.1962 | 120.7728 | -0.91374 | 120.8644 | 120.8824 | 0.10959 | -0.94719 | -0.73691 | 120.6855 | -1.0004 | 120.9651 | 120.8482 | 0.16274 | -0.8377 | -0.85281 | 120.9979 | 120.9644 | 121.1747 | 120.9197 | -1.1388 | 120.9112 | 121.0739 | 121.0588 | 120.9644 | -1.2262
5811.6406 | 122.1039 | -120.9045 | 1.0849 | -0.0025182 | -0.070196 | 0.037729 | 0.01434 | -0.016138 | 0.0090209 | -0.013887 | -0.021494 | -0.0080591 | 0.022367 | 0.056927 | -0.00081186 | -0.017266 | 0.033457 | 0.000747 | 0.10707 | 0.078201 | 0.28848 | -0.10427 | 0.083464 | 0.087354 | -0.028879 | 0.024988 | 0.18311 | 0.18632 | -0.19162 | 120.8003 | -0.97783 | 120.8873 | 120.9053 | 0.10501 | -1.0067 | -0.79642 | 120.7129 | -1.0599 | 120.988 | 120.8757 | 0.16274 | -0.90178 | -0.89858 | 121.0116 | 120.9827 | 121.193 | 120.938 | -1.1892 | 120.9295 | 121.0877 | 121.0909 | 120.9919 | -1.2765
5813.3281 | 122.1542 | -120.8221 | 1.1627 | -0.025411 | -0.07041 | 0.037516 | 0.014127 | -0.016138 | 0.0088073 | -0.021518 | -0.021708 | -0.0082729 | 0.022367 | 0.05714 | -0.00059826 | -0.021844 | 0.033457 | -0.003831 | 0.10707 | 0.073622 | 0.2839 | -0.10885 | 0.088043 | 0.082776 | -0.033458 | 0.024988 | 0.18311 | 0.18632 | -0.19162 | 120.7133 | -1.0557 | 120.8003 | 120.8183 | 0.10502 | -1.0891 | -0.87882 | 120.6305 | -1.1377 | 120.9102 | 120.7887 | 0.15816 | -0.9796 | -0.9764 | 120.9292 | 120.8958 | 121.106 | 120.8556 | -1.2716 | 120.8471 | 121.0053 | 121.0085 | 120.9049 | -1.3543
5815.1094 | 122.1542 | -120.8267 | 1.1581 | -0.01778 | -0.070837 | 0.037729 | 0.01434 | -0.015711 | 0.0085935 | -0.021518 | -0.02128 | -0.0084865 | 0.022153 | 0.05714 | -0.00038466 | -0.021844 | 0.033457 | -0.003831 | 0.11622 | 0.087359 | 0.28848 | -0.099689 | 0.083464 | 0.087354 | -0.038036 | 0.029566 | 0.17854 | 0.17716 | -0.19162 | 120.727 | -1.0419 | 120.8049 | 120.8229 | 0.095858 | -1.0708 | -0.86966 | 120.6351 | -1.1286 | 120.9102 | 120.7887 | 0.15359 | -0.97961 | -0.98098 | 120.9429 | 120.9141 | 121.1152 | 120.8602 | -1.2578 | 120.8563 | 121.0053 | 121.0039 | 120.9141 | -1.3498
5816.8281 | 122.1268 | -120.8588 | 1.1307 | -0.01778 | -0.07041 | 0.037516 | 0.014127 | -0.015924 | 0.0090209 | -0.021518 | -0.021494 | -0.0087001 | 0.022367 | 0.05714 | -0.00081186 | -0.008109 | 0.042614 | 0.000747 | 0.10707 | 0.08278 | 0.2839 | -0.10427 | 0.083464 | 0.078197 | -0.0243 | 0.029566 | 0.16938 | 0.18174 | -0.1962 | 120.7545 | -1.0236 | 120.8507 | 120.8595 | 0.10501 | -1.0479 | -0.84677 | 120.6626 | -1.1011 | 120.9422 | 120.8345 | 0.1719 | -0.9613 | -0.94894 | 120.9658 | 120.9415 | 121.1427 | 120.9014 | -1.2349 | 120.8883 | 121.0281 | 121.0405 | 120.937 | -1.3269
5818.5938 | 122.1451 | -120.9366 | 1.0529 | -0.010149 | -0.070837 | 0.037943 | 0.01434 | -0.015924 | 0.0088073 | -0.021518 | -0.021921 | -0.0087001 | 0.022153 | 0.05714 | -0.0010255 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.091937 | 0.28848 | -0.10427 | 0.088043 | 0.091933 | -0.028879 | 0.020409 | 0.18311 | 0.18632 | -0.1962 | 120.8323 | -0.94579 | 120.9193 | 120.9328 | 0.10044 | -0.96092 | -0.76438 | 120.7404 | -1.0324 | 121.0246 | 120.9077 | 0.16732 | -0.86974 | -0.86654 | 121.0437 | 121.0285 | 121.2251 | 120.97 | -1.1571 | 120.957 | 121.1197 | 121.1229 | 121.0285 | -1.2491
5820.2969 | 122.1725 | -120.9366 | 1.0666 | -0.010149 | -0.07041 | 0.037516 | 0.01434 | -0.015711 | 0.0088073 | -0.013887 | -0.02128 | -0.0082729 | 0.022367 | 0.05714 | -0.00059826 | -0.021844 | 0.033457 | 0.000747 | 0.11622 | 0.091937 | 0.29306 | -0.11342 | 0.088043 | 0.087354 | -0.019721 | 0.029566 | 0.17854 | 0.17716 | -0.18704 | 120.8232 | -0.95036 | 120.9147 | 120.9373 | 0.11417 | -0.97465 | -0.77353 | 120.7495 | -1.037 | 121.0246 | 120.9169 | 0.16732 | -0.88805 | -0.88943 | 121.0528 | 121.0285 | 121.2296 | 120.97 | -1.18 | 120.9661 | 121.1151 | 121.1137 | 121.0239 | -1.2536
5822.0625 | 122.2549 | -120.9274 | 1.0208 | -0.01778 | -0.069982 | 0.037729 | 0.014127 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.02194 | 0.056927 | -0.00038466 | -0.017266 | 0.038035 | 0.000747 | 0.11622 | 0.08278 | 0.29306 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.17854 | 0.1909 | -0.1962 | 120.8186 | -0.90459 | 120.9102 | 120.9282 | 0.10959 | -0.93803 | -0.72775 | 120.7312 | -1.0004 | 121.0063 | 120.894 | 0.16274 | -0.84228 | -0.82992 | 121.0437 | 121.0102 | 121.2205 | 120.9655 | -1.1297 | 120.9478 | 121.106 | 121.1183 | 121.0148 | -1.217
5823.75 | 122.2504 | -120.8496 | 1.0712 | -0.010149 | -0.07041 | 0.037943 | 0.013486 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.05714 | -0.00059826 | -0.012688 | 0.033457 | 0.000747 | 0.10707 | 0.08278 | 0.28848 | -0.11342 | 0.074307 | 0.091933 | -0.033458 | 0.015831 | 0.17396 | 0.17716 | -0.19162 | 120.7362 | -0.9641 | 120.8369 | 120.8504 | 0.11417 | -0.98839 | -0.78269 | 120.658 | -1.0553 | 120.9239 | 120.8162 | 0.15816 | -0.89721 | -0.89401 | 120.9567 | 120.9324 | 121.1381 | 120.8831 | -1.1846 | 120.8654 | 121.0236 | 121.0268 | 120.9415 | -1.2628
5825.5156 | 122.168 | -120.9 | 1.1124 | -0.0025182 | -0.070837 | 0.037516 | 0.01434 | -0.015924 | 0.0088073 | -0.021518 | -0.02128 | -0.0080591 | 0.022153 | 0.05714 | -0.00059826 | -0.012688 | 0.028878 | -0.003831 | 0.097912 | 0.087359 | 0.28848 | -0.10427 | 0.078886 | 0.082776 | -0.033458 | 0.024988 | 0.18311 | 0.18174 | -0.1962 | 120.7957 | -1.0145 | 120.8873 | 120.8961 | 0.10044 | -1.025 | -0.82388 | 120.7038 | -1.0874 | 120.9788 | 120.8665 | 0.16274 | -0.92925 | -0.93063 | 120.9979 | 120.9873 | 121.1884 | 120.9288 | -1.2166 | 120.925 | 121.0831 | 121.0817 | 120.9827 | -1.3086
5827.2812 | 122.1817 | -120.8862 | 1.1078 | -0.010149 | -0.07041 | 0.037943 | 0.014127 | -0.015924 | 0.0085935 | -0.021518 | -0.021067 | -0.0084865 | 0.022367 | 0.05714 | -0.0010255 | -0.017266 | 0.038035 | -0.003831 | 0.11165 | 0.08278 | 0.2839 | -0.11342 | 0.088043 | 0.082776 | -0.028879 | 0.020409 | 0.17396 | 0.18632 | -0.1962 | 120.7728 | -0.99614 | 120.869 | 120.8824 | 0.10959 | -1.025 | -0.82388 | 120.69 | -1.0874 | 120.9743 | 120.8574 | 0.16732 | -0.93383 | -0.92147 | 120.9979 | 120.969 | 121.1701 | 120.9243 | -1.2212 | 120.9066 | 121.0602 | 121.0725 | 120.969 | -1.304
5829.0469 | 122.1909 | -120.9137 | 1.1078 | -0.025411 | -0.070837 | 0.037516 | 0.01434 | -0.015711 | 0.0088073 | -0.021518 | -0.021494 | -0.0084865 | 0.02194 | 0.057354 | -0.0010255 | -0.008109 | 0.042614 | -0.008409 | 0.10249 | 0.091937 | 0.28848 | -0.10885 | 0.074307 | 0.087354 | -0.028879 | 0.020409 | 0.17854 | 0.18174 | -0.19162 | 120.8048 | -1.0053 | 120.9056 | 120.9053 | 0.10044 | -1.0159 | -0.81931 | 120.7221 | -1.0874 | 120.988 | 120.8848 | 0.16274 | -0.92925 | -0.92605 | 121.0162 | 121.0056 | 121.2022 | 120.9563 | -1.2166 | 120.9341 | 121.0922 | 121.0954 | 121.0011 | -1.2994
5830.75 | 122.1451 | -120.9229 | 1.1398 | -0.010149 | -0.07041 | 0.037729 | 0.014127 | -0.015497 | 0.0085935 | -0.029148 | -0.021494 | -0.0082729 | 0.022153 | 0.057354 | -0.00081186 | -0.012688 | 0.033457 | -0.003831 | 0.11165 | 0.078201 | 0.2839 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.024988 | 0.18311 | 0.17258 | -0.18704 | 120.814 | -1.0282 | 120.9102 | 120.919 | 0.10502 | -1.0616 | -0.85593 | 120.7358 | -1.1148 | 121.0017 | 120.8894 | 0.15358 | -0.95672 | -0.96725 | 121.0345 | 121.0011 | 121.2068 | 120.9563 | -1.2487 | 120.9478 | 121.106 | 121.0954 | 121.0102 | -1.3269
5832.5312 | 122.2733 | -120.8954 | 1.062 | -0.010149 | -0.07041 | 0.037729 | 0.014127 | -0.015924 | 0.0090209 | -0.021518 | -0.02128 | -0.0082729 | 0.02194 | 0.057354 | -0.00081186 | -0.021844 | 0.028878 | -0.003831 | 0.10707 | 0.087359 | 0.28848 | -0.10427 | 0.078886 | 0.078197 | -0.033458 | 0.029566 | 0.19685 | 0.18174 | -0.19162 | 120.7911 | -0.95494 | 120.8735 | 120.8916 | 0.10044 | -0.97465 | -0.77353 | 120.7038 | -1.0324 | 120.9743 | 120.8619 | 0.15816 | -0.86516 | -0.88027 | 121.0025 | 120.9827 | 121.1839 | 120.9243 | -1.1663 | 120.925 | 121.0922 | 121.0771 | 120.9736 | -1.2536
5834.2969 | 122.1863 | -120.9457 | 1.1032 | -0.0025182 | -0.071051 | 0.037729 | 0.01434 | -0.015924 | 0.0085935 | -0.021518 | -0.021708 | -0.0080591 | 0.02194 | 0.056927 | -0.00059826 | -0.012688 | 0.033457 | 0.000747 | 0.11165 | 0.087359 | 0.2839 | -0.099689 | 0.078886 | 0.087354 | -0.033458 | 0.029566 | 0.18311 | 0.1909 | -0.1962 | 120.8461 | -0.99156 | 120.9331 | 120.9465 | 0.10044 | -1.0159 | -0.81931 | 120.7495 | -1.0736 | 121.0246 | 120.9123 | 0.16274 | -0.92009 | -0.91231 | 121.0574 | 121.0331 | 121.2296 | 120.9792 | -1.2029 | 120.9753 | 121.1289 | 121.1366 | 121.0331 | -1.2994
5836.0625 | 122.2321 | -120.9183 | 1.0391 | -0.0025182 | -0.070623 | 0.038157 | 0.014127 | -0.015711 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.022581 | 0.05714 | -0.00081186 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.087359 | 0.28848 | -0.10427 | 0.078886 | 0.082776 | -0.038036 | 0.029566 | 0.18311 | 0.17716 | -0.19162 | 120.814 | -0.93206 | 120.901 | 120.9099 | 0.095859 | -0.95176 | -0.75064 | 120.7267 | -1.0096 | 120.9972 | 120.8802 | 0.15359 | -0.85601 | -0.86196 | 121.0253 | 121.0056 | 121.2068 | 120.9517 | -1.1434 | 120.9478 | 121.1014 | 121.0954 | 121.001 | -1.2307
5837.8438 | 122.2778 | -120.9412 | 1.0483 | -0.025411 | -0.070837 | 0.037729 | 0.013913 | -0.016138 | 0.0090209 | -0.029148 | -0.021494 | -0.0087001 | 0.021726 | 0.057354 | -0.00081186 | -0.026423 | 0.038035 | -0.003831 | 0.10249 | 0.087359 | 0.29764 | -0.10427 | 0.078886 | 0.091933 | -0.033458 | 0.024988 | 0.18769 | 0.18632 | -0.19162 | 120.8369 | -0.94579 | 120.9147 | 120.9373 | 0.10044 | -0.96092 | -0.75064 | 120.7495 | -1.0233 | 121.02 | 120.9077 | 0.15816 | -0.86059 | -0.86196 | 121.0437 | 121.0285 | 121.2388 | 120.9792 | -1.1525 | 120.9661 | 121.1289 | 121.1275 | 121.0331 | -1.2399
5839.6094 | 122.1909 | -120.9641 | 1.0574 | -0.010149 | -0.070623 | 0.037088 | 0.013699 | -0.015711 | 0.0085935 | -0.021518 | -0.021708 | -0.0087001 | 0.022367 | 0.05714 | -0.00081186 | -0.017266 | 0.042614 | 0.000747 | 0.11165 | 0.08278 | 0.28848 | -0.10427 | 0.078886 | 0.078197 | -0.028879 | 0.024988 | 0.17854 | 0.18174 | -0.1962 | 120.8598 | -0.94579 | 120.9468 | 120.9648 | 0.10501 | -0.97465 | -0.76895 | 120.7678 | -1.0324 | 121.0429 | 120.9352 | 0.16732 | -0.8789 | -0.8757 | 121.0757 | 121.0468 | 121.2525 | 121.0067 | -1.1617 | 120.989 | 121.1426 | 121.1458 | 121.0422 | -1.2536
5841.3125 | 122.1863 | -120.9824 | 1.0666 | -0.01778 | -0.070837 | 0.037729 | 0.01434 | -0.016138 | 0.0088073 | -0.013887 | -0.021494 | -0.0082729 | 0.022153 | 0.056927 | -0.00081186 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.091937 | 0.27932 | -0.10885 | 0.078886 | 0.082776 | -0.028879 | 0.029566 | 0.18311 | 0.18174 | -0.1962 | 120.8735 | -0.95952 | 120.9651 | 120.9785 | 0.10502 | -0.97465 | -0.78726 | 120.7862 | -1.037 | 121.0612 | 120.9535 | 0.16732 | -0.88347 | -0.88485 | 121.0894 | 121.0743 | 121.2617 | 121.0158 | -1.1754 | 121.0119 | 121.1655 | 121.1641 | 121.0651 | -1.2628
5843.1094 | 122.2733 | -120.9412 | 1.0483 | -0.010149 | -0.070837 | 0.037729 | 0.014127 | -0.015711 | 0.0088073 | -0.013887 | -0.021494 | -0.0082729 | 0.022367 | 0.056927 | -0.0010255 | -0.021844 | 0.033457 | -0.003831 | 0.11165 | 0.08278 | 0.29764 | -0.11342 | 0.083464 | 0.078197 | -0.033458 | 0.029566 | 0.19227 | 0.168 | -0.19162 | 120.8277 | -0.93663 | 120.9193 | 120.9373 | 0.10959 | -0.9655 | -0.75064 | 120.7495 | -1.0187 | 121.0246 | 120.9077 | 0.15816 | -0.85601 | -0.88028 | 121.0528 | 121.0239 | 121.2388 | 120.9746 | -1.1617 | 120.9707 | 121.1334 | 121.1092 | 121.0194 | -1.2399
5844.875 | 122.2916 | -120.9641 | 1.0345 | -0.010149 | -0.070837 | 0.037729 | 0.01434 | -0.015924 | 0.0092345 | -0.029148 | -0.021708 | -0.0082729 | 0.022153 | 0.05714 | -0.0010255 | -0.012688 | 0.038035 | 0.000747 | 0.11165 | 0.08278 | 0.29306 | -0.11342 | 0.069728 | 0.082776 | -0.042615 | 0.024988 | 0.18311 | 0.17716 | -0.18704 | 120.8506 | -0.9229 | 120.9514 | 120.9648 | 0.11417 | -0.95177 | -0.74149 | 120.777 | -1.0096 | 121.0338 | 120.9214 | 0.14443 | -0.85143 | -0.85739 | 121.0757 | 121.0468 | 121.2571 | 121.0021 | -1.148 | 120.989 | 121.1472 | 121.1412 | 121.0468 | -1.2216
5846.6562 | 122.168 | -120.9915 | 1.0849 | -0.01778 | -0.071051 | 0.037516 | 0.014127 | -0.015711 | 0.0085935 | -0.021518 | -0.021708 | -0.0087001 | 0.022153 | 0.057354 | -0.00081186 | -0.021844 | 0.038035 | -0.003831 | 0.10249 | 0.087359 | 0.28848 | -0.10427 | 0.078886 | 0.082776 | -0.033458 | 0.024988 | 0.17854 | 0.17716 | -0.18704 | 120.8872 | -0.98241 | 120.9697 | 120.9877 | 0.10044 | -0.99754 | -0.79642 | 120.8045 | -1.0599 | 121.0704 | 120.9581 | 0.15358 | -0.90636 | -0.90774 | 121.094 | 121.0789 | 121.28 | 121.0296 | -1.1892 | 121.0165 | 121.1701 | 121.1687 | 121.0743 | -1.2719
5848.3594 | 122.2275 | -120.9824 | 1.0803 | -0.010149 | -0.070837 | 0.037729 | 0.01434 | -0.015924 | 0.0085935 | -0.021518 | -0.021708 | -0.0082729 | 0.02194 | 0.057354 | -0.00081186 | -0.012688 | 0.038035 | 0.000747 | 0.10707 | 0.08278 | 0.29306 | -0.10427 | 0.069728 | 0.078197 | -0.028879 | 0.024988 | 0.17854 | 0.17716 | -0.20078 | 120.8781 | -0.97325 | 120.9697 | 120.9831 | 0.10501 | -0.99754 | -0.78726 | 120.7816 | -1.0553 | 121.0521 | 120.9535 | 0.1719 | -0.90179 | -0.90316 | 121.0894 | 121.0651 | 121.2754 | 121.0204 | -1.1846 | 121.0073 | 121.1609 | 121.1595 | 121.0606 | -1.2811
5850.0625 | 122.1817 | -121.0098 | 1.0895 | -0.010149 | -0.070837 | 0.037516 | 0.01434 | -0.015711 | 0.0088073 | -0.013887 | -0.02128 | -0.0082729 | 0.02194 | 0.057354 | -0.00059826 | -0.017266 | 0.042614 | 0.005325 | 0.097912 | 0.078201 | 0.29306 | -0.11342 | 0.092622 | 0.087354 | -0.038036 | 0.020409 | 0.18769 | 0.17716 | -0.1962 | 120.8964 | -0.99157 | 120.9926 | 121.0152 | 0.11875 | -1.0113 | -0.79642 | 120.8136 | -1.0691 | 121.1024 | 120.9718 | 0.15816 | -0.90178 | -0.91232 | 121.1077 | 121.088 | 121.3029 | 121.0524 | -1.2029 | 121.0302 | 121.1975 | 121.187 | 121.0972 | -1.2857
5851.7812 | 122.2321 | -120.9641 | 1.0986 | -0.010149 | -0.070623 | 0.037302 | 0.01434 | -0.015497 | 0.0092345 | -0.021518 | -0.02128 | -0.0082729 | 0.022153 | 0.057354 | -0.00081186 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.08278 | 0.2839 | -0.10427 | 0.078886 | 0.091933 | -0.028879 | 0.024988 | 0.17854 | 0.17258 | -0.19162 | 120.8598 | -0.98699 | 120.9468 | 120.9602 | 0.10044 | -1.0159 | -0.81473 | 120.7724 | -1.0736 | 121.0429 | 120.9352 | 0.16274 | -0.9201 | -0.92605 | 121.0757 | 121.0468 | 121.248 | 120.9975 | -1.2029 | 120.989 | 121.1426 | 121.1366 | 121.056 | -1.2903
5853.5312 | 122.3145 | -120.9137 | 1.0941 | -0.033042 | -0.071264 | 0.037302 | 0.014127 | -0.015711 | 0.0090209 | -0.013887 | -0.02128 | -0.0082729 | 0.022794 | 0.057354 | -0.00081186 | -0.017266 | 0.028878 | -0.008409 | 0.11165 | 0.08278 | 0.29306 | -0.10427 | 0.078886 | 0.087354 | -0.028879 | 0.029566 | 0.17854 | 0.17716 | -0.19162 | 120.8094 | -0.98241 | 120.8964 | 120.9053 | 0.095859 | -1.0113 | -0.801 | 120.7221 | -1.0645 | 120.9926 | 120.8848 | 0.16274 | -0.91552 | -0.9169 | 121.0253 | 120.9965 | 121.2068 | 120.9426 | -1.1983 | 120.9433 | 121.0922 | 121.0909 | 121.0011 | -1.2857
5855.2344 | 122.1725 | -120.9778 | 1.1398 | -0.010149 | -0.070837 | 0.037729 | 0.013913 | -0.015497 | 0.0088073 | -0.021518 | -0.02128 | -0.0080591 | 0.02194 | 0.057354 | -0.0010255 | -0.012688 | 0.033457 | 0.000747 | 0.11622 | 0.087359 | 0.29306 | -0.10885 | 0.083464 | 0.082776 | -0.033458 | 0.029566 | 0.18311 | 0.17716 | -0.19162 | 120.8689 | -1.0236 | 120.9651 | 120.9785 | 0.10959 | -1.0525 | -0.84677 | 120.7862 | -1.1103 | 121.0612 | 120.9443 | 0.15816 | -0.95672 | -0.96267 | 121.094 | 121.0651 | 121.2708 | 121.0112 | -1.2487 | 121.0073 | 121.1609 | 121.1549 | 121.0606 | -1.3315
5856.9375 | 122.2504 | -120.932 | 1.1215 | -0.025411 | -0.071051 | 0.037516 | 0.013913 | -0.015711 | 0.0085935 | -0.013887 | -0.021494 | -0.0082729 | 0.022367 | 0.057354 | -0.00081186 | -0.017266 | 0.0243 | -0.008409 | 0.10707 | 0.078201 | 0.29764 | -0.10885 | 0.083464 | 0.082776 | -0.038036 | 0.024988 | 0.18311 | 0.18174 | -0.1962 | 120.8232 | -1.0145 | 120.9147 | 120.9236 | 0.10044 | -1.0433 | -0.82388 | 120.7358 | -1.0965 | 121.0155 | 120.894 | 0.15816 | -0.93841 | -0.93978 | 121.0391 | 121.0102 | 121.2296 | 120.9563 | -1.2304 | 120.957 | 121.1151 | 121.1137 | 121.0148 | -1.3177
5858.6719 | 122.3145 | -120.8908 | 1.1078 | -0.01778 | -0.070837 | 0.037729 | 0.014127 | -0.015711 | 0.0088073 | -0.021518 | -0.021708 | -0.0084865 | 0.022153 | 0.057354 | -0.00081186 | -0.017266 | 0.038035 | -0.003831 | 0.10707 | 0.08278 | 0.28848 | -0.10427 | 0.074307 | 0.087354 | -0.047194 | 0.024988 | 0.18769 | 0.17716 | -0.19162 | 120.7865 | -1.0007 | 120.8735 | 120.887 | 0.10044 | -1.025 | -0.81931 | 120.6992 | -1.0828 | 120.9651 | 120.8436 | 0.14443 | -0.92009 | -0.93063 | 120.9979 | 120.9736 | 121.1793 | 120.9288 | -1.2121 | 120.9158 | 121.0785 | 121.068 | 120.9782 | -1.2994
5860.3594 | 122.2504 | -120.9137 | 1.1536 | -0.01778 | -0.070837 | 0.037516 | 0.013913 | -0.015924 | 0.0088073 | -0.0062567 | -0.02128 | -0.0084865 | 0.022153 | 0.057354 | -0.00081186 | -0.017266 | 0.042614 | 0.000747 | 0.10249 | 0.087359 | 0.2839 | -0.10885 | 0.074307 | 0.082776 | -0.038036 | 0.024988 | 0.18311 | 0.18174 | -0.1962 | 120.8048 | -1.0511 | 120.8964 | 120.9144 | 0.10959 | -1.0662 | -0.86966 | 120.7175 | -1.1286 | 120.988 | 120.8757 | 0.15816 | -0.97045 | -0.97183 | 121.0162 | 121.0011 | 121.1976 | 120.9563 | -1.2624 | 120.9387 | 121.0968 | 121.0954 | 120.9965 | -1.3498
5862.0781 | 122.2275 | -120.9091 | 1.1993 | -0.010149 | -0.07041 | 0.037943 | 0.014127 | -0.016138 | 0.0088073 | -0.0062567 | -0.02128 | -0.0080591 | 0.022153 | 0.057354 | -0.00059826 | -0.017266 | 0.038035 | 0.005325 | 0.10707 | 0.091937 | 0.29306 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.029566 | 0.17854 | 0.17716 | -0.1962 | 120.8003 | -1.0923 | 120.8919 | 120.9144 | 0.11417 | -1.1074 | -0.90628 | 120.7129 | -1.1698 | 120.988 | 120.8757 | 0.16274 | -1.0208 | -1.0222 | 121.0162 | 121.0011 | 121.2022 | 120.9472 | -1.3082 | 120.9387 | 121.0877 | 121.0863 | 120.9965 | -1.3955
5863.7812 | 122.2733 | -120.7855 | 1.2314 | -0.01778 | -0.071051 | 0.037729 | 0.014127 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.022367 | 0.05714 | -0.0010255 | -0.017266 | 0.042614 | 0.000747 | 0.10707 | 0.08278 | 0.28848 | -0.10427 | 0.074307 | 0.087354 | -0.038036 | 0.029566 | 0.16938 | 0.18174 | -0.1962 | 120.6813 | -1.1243 | 120.7683 | 120.7863 | 0.10501 | -1.1486 | -0.9429 | 120.5893 | -1.2018 | 120.8598 | 120.7475 | 0.15816 | -1.062 | -1.0496 | 120.8926 | 120.8683 | 121.074 | 120.8281 | -1.3357 | 120.8151 | 120.9549 | 120.9673 | 120.8729 | -1.4276
5865.5938 | 122.3099 | -120.7489 | 1.2543 | -0.0025182 | -0.071051 | 0.037943 | 0.014127 | -0.015711 | 0.0088073 | -0.021518 | -0.021494 | -0.0084865 | 0.022367 | 0.057568 | -0.0010255 | -0.017266 | 0.033457 | -0.008409 | 0.10249 | 0.08278 | 0.28848 | -0.10885 | 0.074307 | 0.078197 | -0.042615 | 0.024988 | 0.18311 | 0.17716 | -0.19162 | 120.6401 | -1.1518 | 120.7316 | 120.7405 | 0.10044 | -1.1715 | -0.96579 | 120.5573 | -1.2293 | 120.8232 | 120.7063 | 0.14901 | -1.0712 | -1.0771 | 120.8514 | 120.8317 | 121.0374 | 120.7824 | -1.3631 | 120.7739 | 120.932 | 120.9261 | 120.8271 | -1.4459
5867.2969 | 122.2321 | -120.7764 | 1.3458 | -0.033042 | -0.071051 | 0.037943 | 0.014127 | -0.016138 | 0.0085935 | -0.029148 | -0.021708 | -0.0082729 | 0.022153 | 0.057354 | -0.00059826 | -0.017266 | 0.028878 | -0.003831 | 0.10707 | 0.08278 | 0.28848 | -0.10885 | 0.083464 | 0.082776 | -0.038036 | 0.024988 | 0.17854 | 0.18174 | -0.1962 | 120.6675 | -1.2388 | 120.7591 | 120.7725 | 0.10502 | -1.263 | -1.0573 | 120.5802 | -1.3208 | 120.8598 | 120.7383 | 0.15816 | -1.1673 | -1.1641 | 120.8834 | 120.8591 | 121.0648 | 120.8052 | -1.4547 | 120.8014 | 120.9549 | 120.9581 | 120.8591 | -1.542
5869 | 122.3419 | -120.7031 | 1.3321 | -0.010149 | -0.070623 | 0.037729 | 0.014127 | -0.015924 | 0.0085935 | -0.013887 | -0.021067 | -0.0084865 | 0.022367 | 0.057354 | -0.0010255 | -0.012688 | 0.042614 | 0.005325 | 0.11165 | 0.087359 | 0.2839 | -0.11342 | 0.078886 | 0.087354 | -0.028879 | 0.029566 | 0.17854 | 0.17716 | -0.18704 | 120.5897 | -1.2204 | 120.6904 | 120.7084 | 0.11875 | -1.2447 | -1.0482 | 120.5161 | -1.3025 | 120.782 | 120.6742 | 0.15816 | -1.1536 | -1.1549 | 120.8148 | 120.7905 | 120.987 | 120.7457 | -1.4455 | 120.7327 | 120.8817 | 120.8803 | 120.7905 | -1.5191
5870.7031 | 122.3328 | -120.6619 | 1.355 | -0.010149 | -0.071051 | 0.037729 | 0.014127 | -0.016138 | 0.0085935 | -0.021518 | -0.021708 | -0.0084865 | 0.022367 | 0.056927 | -0.00081186 | -0.017266 | 0.042614 | 0.000747 | 0.10707 | 0.087359 | 0.28848 | -0.10885 | 0.083464 | 0.087354 | -0.033458 | 0.024988 | 0.17854 | 0.18174 | -0.19162 | 120.5531 | -1.2479 | 120.6447 | 120.6627 | 0.10959 | -1.2676 | -1.0665 | 120.4703 | -1.33 | 120.7454 | 120.6285 | 0.15816 | -1.1764 | -1.1732 | 120.769 | 120.7493 | 120.9504 | 120.7045 | -1.4638 | 120.6869 | 120.8405 | 120.8437 | 120.7493 | -1.5466
5872.3906 | 122.2687 | -120.6802 | 1.4191 | -0.01778 | -0.071264 | 0.037729 | 0.01434 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0080591 | 0.022153 | 0.057354 | -0.0010255 | -0.017266 | 0.042614 | -0.003831 | 0.10249 | 0.091937 | 0.29306 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.020409 | 0.17396 | 0.17258 | -0.18704 | 120.5714 | -1.3166 | 120.663 | 120.6764 | 0.10502 | -1.3271 | -1.126 | 120.4932 | -1.3987 | 120.7591 | 120.6422 | 0.14901 | -1.2451 | -1.2465 | 120.7827 | 120.7722 | 120.9733 | 120.7229 | -1.5279 | 120.7006 | 120.8542 | 120.8528 | 120.763 | -1.6061
5874.1406 | 122.2229 | -120.7581 | 1.355 | -0.01778 | -0.071264 | 0.037729 | 0.013913 | -0.016138 | 0.0085935 | -0.021518 | -0.02128 | -0.0084865 | 0.022153 | 0.05714 | -0.00081186 | -0.017266 | 0.038035 | -0.008409 | 0.10707 | 0.08278 | 0.28848 | -0.10885 | 0.074307 | 0.087354 | -0.038036 | 0.020409 | 0.18311 | 0.18632 | -0.19162 | 120.6492 | -1.2479 | 120.7408 | 120.7496 | 0.10044 | -1.2722 | -1.0665 | 120.5664 | -1.3346 | 120.8324 | 120.72 | 0.15359 | -1.1719 | -1.1687 | 120.8651 | 120.8408 | 121.0465 | 120.7961 | -1.4638 | 120.7785 | 120.9412 | 120.9444 | 120.8454 | -1.5466
5875.8594 | 122.3328 | -120.7718 | 1.2863 | -0.025411 | -0.070837 | 0.037516 | 0.014127 | -0.015924 | 0.0088073 | -0.036779 | -0.021067 | -0.0087001 | 0.02194 | 0.057568 | -0.00059826 | -0.026423 | 0.028878 | -0.003831 | 0.10707 | 0.08278 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.038036 | 0.024988 | 0.17854 | 0.17716 | -0.19162 | 120.6629 | -1.1792 | 120.7454 | 120.768 | 0.10502 | -1.2035 | -0.98868 | 120.5802 | -1.2613 | 120.8507 | 120.7338 | 0.15359 | -1.1078 | -1.1092 | 120.8789 | 120.8546 | 121.0694 | 120.8007 | -1.3952 | 120.7968 | 120.9503 | 120.9489 | 120.8591 | -1.4779
5877.625 | 122.3099 | -120.7672 | 1.3 | -0.010149 | -0.070837 | 0.037729 | 0.014554 | -0.015924 | 0.0088073 | -0.0062567 | -0.021494 | -0.0078455 | 0.022153 | 0.057354 | -0.0010255 | -0.017266 | 0.038035 | -0.003831 | 0.10249 | 0.08278 | 0.28848 | -0.10885 | 0.074307 | 0.087354 | -0.033458 | 0.024988 | 0.17396 | 0.17258 | -0.19162 | 120.6584 | -1.1976 | 120.7499 | 120.7634 | 0.10502 | -1.2173 | -1.0116 | 120.5756 | -1.2751 | 120.8415 | 120.7338 | 0.15816 | -1.1261 | -1.1275 | 120.8697 | 120.85 | 121.0557 | 120.8052 | -1.4089 | 120.7922 | 120.9412 | 120.9398 | 120.8546 | -1.4917
5879.3438 | 122.2641 | -120.8221 | 1.2772 | -0.010149 | -0.070837 | 0.037516 | 0.014127 | -0.016138 | 0.0085935 | -0.021518 | -0.021494 | -0.0087001 | 0.022581 | 0.057354 | -0.0014529 | -0.017266 | 0.038035 | -0.003831 | 0.10707 | 0.091937 | 0.28848 | -0.11342 | 0.083464 | 0.082776 | -0.0243 | 0.020409 | 0.18311 | 0.17716 | -0.1962 | 120.7087 | -1.1701 | 120.8049 | 120.8183 | 0.10959 | -1.1852 | -0.98868 | 120.6259 | -1.2568 | 120.9056 | 120.7978 | 0.1719 | -1.094 | -1.1 | 120.9292 | 120.9141 | 121.1106 | 120.8602 | -1.3906 | 120.8426 | 121.0053 | 120.9993 | 120.9049 | -1.4734
5881.0781 | 122.319 | -120.7947 | 1.268 | -0.01778 | -0.071051 | 0.037516 | 0.013913 | -0.015924 | 0.0088073 | -0.036779 | -0.021708 | -0.0087001 | 0.02194 | 0.057354 | -0.0012393 | -0.021844 | 0.038035 | -0.012988 | 0.11622 | 0.08278 | 0.29764 | -0.11342 | 0.083464 | 0.082776 | -0.038036 | 0.024988 | 0.17854 | 0.17716 | -0.20078 | 120.6813 | -1.1518 | 120.7728 | 120.7817 | 0.10044 | -1.1852 | -0.97037 | 120.5939 | -1.243 | 120.8781 | 120.7566 | 0.16274 | -1.0895 | -1.0908 | 120.9109 | 120.8775 | 121.0923 | 120.8327 | -1.3814 | 120.8197 | 120.9732 | 120.9718 | 120.8775 | -1.4688
5882.7969 | 122.2321 | -120.8588 | 1.2955 | -0.01778 | -0.071051 | 0.037516 | 0.014127 | -0.015924 | 0.0085935 | -0.021518 | -0.02128 | -0.0084865 | 0.02194 | 0.057354 | -0.0010255 | -0.021844 | 0.033457 | -0.003831 | 0.10707 | 0.08278 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.028879 | 0.020409 | 0.17854 | 0.168 | -0.20078 | 120.7499 | -1.1884 | 120.8369 | 120.8549 | 0.10502 | -1.2127 | -0.99783 | 120.658 | -1.2751 | 120.9377 | 120.8299 | 0.1719 | -1.1169 | -1.1275 | 120.9658 | 120.9415 | 121.1564 | 120.8922 | -1.4043 | 120.8792 | 121.0373 | 121.0268 | 120.9461 | -1.4963
5884.5 | 122.3557 | -120.7993 | 1.2497 | -0.01778 | -0.071051 | 0.037516 | 0.01434 | -0.015924 | 0.0090209 | -0.029148 | -0.02128 | -0.0082729 | 0.022153 | 0.057354 | -0.0012393 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.08278 | 0.28848 | -0.099689 | 0.078886 | 0.082776 | -0.028879 | 0.024988 | 0.17854 | 0.17716 | -0.20078 | 120.6996 | -1.138 | 120.782 | 120.7954 | 0.095858 | -1.1669 | -0.96121 | 120.5985 | -1.2247 | 120.8781 | 120.7704 | 0.1719 | -1.0712 | -1.0725 | 120.9109 | 120.882 | 121.0877 | 120.8327 | -1.3494 | 120.8242 | 120.9778 | 120.9764 | 120.882 | -1.4505
5886.25 | 122.2824 | -120.8496 | 1.2863 | -0.01778 | -0.071051 | 0.037516 | 0.013913 | -0.015711 | 0.0083799 | -0.021518 | -0.02128 | -0.0084865 | 0.02194 | 0.057781 | -0.0010255 | -0.012688 | 0.038035 | 0.000747 | 0.11165 | 0.087359 | 0.29764 | -0.11342 | 0.074307 | 0.078197 | -0.028879 | 0.015831 | 0.17396 | 0.17258 | -0.18704 | 120.7362 | -1.1747 | 120.8369 | 120.8504 | 0.11417 | -1.199 | -0.98868 | 120.6626 | -1.2705 | 120.9239 | 120.8207 | 0.15816 | -1.1124 | -1.1137 | 120.9613 | 120.937 | 121.1472 | 120.8876 | -1.3997 | 120.8654 | 121.0236 | 121.0222 | 120.9278 | -1.4734
5887.9844 | 122.2549 | -120.8405 | 1.2817 | -0.01778 | -0.071051 | 0.037516 | 0.014127 | -0.016138 | 0.0085935 | -0.036779 | -0.021494 | -0.0082729 | 0.022153 | 0.057354 | -0.0010255 | -0.017266 | 0.0243 | -0.008409 | 0.10707 | 0.096516 | 0.29306 | -0.11342 | 0.069728 | 0.091933 | -0.033458 | 0.029566 | 0.16938 | 0.168 | -0.20536 | 120.727 | -1.1747 | 120.8232 | 120.832 | 0.10502 | -1.1852 | -0.98868 | 120.6351 | -1.2522 | 120.9102 | 120.807 | 0.1719 | -1.1124 | -1.1137 | 120.9475 | 120.937 | 121.1335 | 120.8648 | -1.3952 | 120.87 | 121.0098 | 121.0085 | 120.9324 | -1.4871
5889.7344 | 122.319 | -120.8633 | 1.2405 | -0.010149 | -0.071264 | 0.037302 | 0.014127 | -0.015924 | 0.0088073 | -0.029148 | -0.021494 | -0.0080591 | 0.022153 | 0.057568 | -0.0010255 | -0.017266 | 0.038035 | -0.008409 | 0.10707 | 0.08278 | 0.29764 | -0.099689 | 0.078886 | 0.091933 | -0.033458 | 0.020409 | 0.17854 | 0.18174 | -0.19162 | 120.7637 | -1.1335 | 120.8461 | 120.8549 | 0.09128 | -1.1578 | -0.9429 | 120.6717 | -1.2201 | 120.9422 | 120.8299 | 0.15816 | -1.062 | -1.0588 | 120.9704 | 120.9461 | 121.161 | 120.9014 | -1.3402 | 120.8838 | 121.0419 | 121.0451 | 120.9553 | -1.4322
5891.4219 | 122.2458 | -120.8725 | 1.2589 | -0.01778 | -0.070837 | 0.037516 | 0.013699 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0084865 | 0.02194 | 0.057568 | -0.0010255 | -0.012688 | 0.038035 | -0.003831 | 0.11165 | 0.08278 | 0.29306 | -0.11342 | 0.083464 | 0.078197 | -0.028879 | 0.024988 | 0.17396 | 0.17716 | -0.18246 | 120.7591 | -1.1472 | 120.8598 | 120.8687 | 0.10959 | -1.1761 | -0.96579 | 120.69 | -1.2339 | 120.956 | 120.8436 | 0.15358 | -1.0849 | -1.0817 | 120.9841 | 120.9553 | 121.1656 | 120.9105 | -1.3723 | 120.8975 | 121.0465 | 121.0497 | 120.9507 | -1.4413
5893.125 | 122.3419 | -120.9045 | 1.2039 | -0.025411 | -0.071051 | 0.037516 | 0.013913 | -0.015711 | 0.0090209 | -0.021518 | -0.02128 | -0.0082729 | 0.021726 | 0.057568 | -0.0012393 | -0.017266 | 0.028878 | -0.003831 | 0.11622 | 0.08278 | 0.29306 | -0.10427 | 0.083464 | 0.082776 | -0.038036 | 0.020409 | 0.16938 | 0.17716 | -0.1962 | 120.8003 | -1.0877 | 120.8873 | 120.9007 | 0.10044 | -1.1211 | -0.91086 | 120.7083 | -1.1835 | 120.988 | 120.8665 | 0.15816 | -1.0345 | -1.0268 | 121.0208 | 120.9873 | 121.1976 | 120.9334 | -1.3082 | 120.9249 | 121.0739 | 121.0817 | 120.9873 | -1.4001
5894.8281 | 122.2412 | -120.7672 | 1.3824 | -0.01778 | -0.071051 | 0.037302 | 0.013699 | -0.016352 | 0.0085935 | -0.029148 | -0.021708 | -0.0082729 | 0.02194 | 0.057354 | -0.0010255 | -0.008109 | 0.038035 | -0.003831 | 0.10249 | 0.08278 | 0.29306 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.17396 | 0.18174 | -0.19162 | 120.6538 | -1.28 | 120.7591 | 120.7634 | 0.10959 | -1.2997 | -1.0894 | 120.5756 | -1.362 | 120.8461 | 120.7338 | 0.15816 | -1.2085 | -1.2007 | 120.8697 | 120.85 | 121.0603 | 120.8052 | -1.4959 | 120.7876 | 120.9412 | 120.9489 | 120.8546 | -1.5741
5896.5938 | 122.3969 | -120.6802 | 1.3733 | -0.01778 | -0.070623 | 0.037302 | 0.014127 | -0.016138 | 0.0088073 | -0.029148 | -0.021494 | -0.0082729 | 0.02194 | 0.057568 | -0.0012393 | -0.017266 | 0.047193 | -0.008409 | 0.11622 | 0.08278 | 0.29306 | -0.10427 | 0.088043 | 0.091933 | -0.033458 | 0.015831 | 0.17854 | 0.17258 | -0.19162 | 120.576 | -1.2571 | 120.663 | 120.6718 | 0.095859 | -1.2905 | -1.0802 | 120.4886 | -1.3575 | 120.7683 | 120.6468 | 0.15816 | -1.1948 | -1.2007 | 120.7965 | 120.763 | 120.9733 | 120.7274 | -1.4776 | 120.6961 | 120.8588 | 120.8528 | 120.7722 | -1.5649
5898.3125 | 122.3007 | -119.5999 | 2.536 | -0.010149 | -0.071051 | 0.037516 | 0.014127 | -0.015924 | 0.0085935 | -0.029148 | -0.021494 | -0.0084865 | 0.02194 | 0.057354 | -0.00081186 | -0.017266 | 0.038035 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.020409 | 0.16938 | 0.18174 | -0.1962 | 119.4911 | -2.4244 | 119.5826 | 119.5961 | 0.10502 | -2.4487 | -2.2384 | 119.4037 | -2.5156 | 119.6788 | 119.5665 | 0.16274 | -2.3666 | -2.3543 | 119.7116 | 119.6873 | 119.8976 | 119.6379 | -2.6449 | 119.6203 | 119.7693 | 119.7817 | 119.6827 | -2.7322
5900.0469 | 122.3877 | -120.7947 | 1.2772 | -0.010149 | -0.071264 | 0.037516 | 0.013913 | -0.015711 | 0.0088073 | -0.021518 | -0.021708 | -0.0082729 | 0.022153 | 0.057781 | -0.00081186 | -0.017266 | 0.038035 | -0.008409 | 0.11165 | 0.087359 | 0.29306 | -0.10885 | 0.078886 | 0.082776 | -0.028879 | 0.029566 | 0.17396 | 0.17716 | -0.19162 | 120.6858 | -1.1655 | 120.7774 | 120.7863 | 0.10044 | -1.1898 | -0.9841 | 120.6031 | -1.2476 | 120.8736 | 120.7658 | 0.16274 | -1.1032 | -1.1 | 120.9063 | 120.882 | 121.0877 | 120.8327 | -1.386 | 120.8242 | 120.9686 | 120.9718 | 120.8775 | -1.4688
5901.7812 | 122.4014 | -120.7855 | 1.3229 | -0.025411 | -0.070837 | 0.037302 | 0.014127 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0087001 | 0.02194 | 0.057354 | -0.0010255 | -0.021844 | 0.028878 | -0.008409 | 0.10707 | 0.087359 | 0.29306 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.029566 | 0.17396 | 0.17716 | -0.20078 | 120.6721 | -1.2159 | 120.7637 | 120.7771 | 0.10502 | -1.2356 | -1.0299 | 120.5847 | -1.2934 | 120.8644 | 120.7521 | 0.16732 | -1.149 | -1.1458 | 120.8926 | 120.8729 | 121.0786 | 120.8144 | -1.4364 | 120.8151 | 120.9595 | 120.9627 | 120.8729 | -1.5237
5903.5156 | 122.2687 | -120.8038 | 1.355 | -0.0025182 | -0.071051 | 0.037516 | 0.013913 | -0.015924 | 0.0088073 | -0.029148 | -0.02128 | -0.0084865 | 0.022153 | 0.057568 | -0.0010255 | -0.008109 | 0.042614 | -0.008409 | 0.10707 | 0.087359 | 0.29306 | -0.10885 | 0.074307 | 0.082776 | -0.028879 | 0.020409 | 0.17396 | 0.17258 | -0.19162 | 120.695 | -1.2479 | 120.7957 | 120.7954 | 0.10044 | -1.2676 | -1.0619 | 120.6122 | -1.3346 | 120.8781 | 120.775 | 0.16274 | -1.181 | -1.1824 | 120.9109 | 120.8912 | 121.0969 | 120.8464 | -1.4638 | 120.8242 | 120.9778 | 120.9764 | 120.8866 | -1.5466
5905.25 | 122.2733 | -120.8221 | 1.3687 | -0.010149 | -0.071264 | 0.037729 | 0.014127 | -0.015924 | 0.0085935 | -0.029148 | -0.021494 | -0.0082729 | 0.02194 | 0.057568 | -0.0012393 | -0.012688 | 0.038035 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.11342 | 0.083464 | 0.082776 | -0.042615 | 0.024988 | 0.16938 | 0.17716 | -0.1962 | 120.7087 | -1.2571 | 120.8095 | 120.8183 | 0.10959 | -1.2814 | -1.0711 | 120.6259 | -1.3437 | 120.9056 | 120.7795 | 0.15359 | -1.1993 | -1.1916 | 120.9338 | 120.9095 | 121.1198 | 120.8602 | -1.4821 | 120.8471 | 120.9915 | 120.9993 | 120.9049 | -1.5649
5906.9844 | 122.374 | -120.7489 | 1.3641 | -0.010149 | -0.070837 | 0.037516 | 0.013486 | -0.015711 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.022153 | 0.057354 | -0.0010255 | -0.026423 | 0.038035 | -0.003831 | 0.10707 | 0.087359 | 0.29306 | -0.10885 | 0.083464 | 0.087354 | -0.038036 | 0.024988 | 0.16938 | 0.17716 | -0.1962 | 120.6401 | -1.2571 | 120.7225 | 120.7451 | 0.10502 | -1.2768 | -1.0711 | 120.5527 | -1.3391 | 120.8324 | 120.7109 | 0.15816 | -1.1948 | -1.187 | 120.856 | 120.8363 | 121.042 | 120.7869 | -1.473 | 120.7739 | 120.9183 | 120.9261 | 120.8363 | -1.5603
5908.7188 | 122.3419 | -120.7489 | 1.3824 | -0.0025182 | -0.071264 | 0.038157 | 0.013699 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0082729 | 0.02194 | 0.05714 | -0.0010255 | -0.021844 | 0.038035 | -0.003831 | 0.10707 | 0.091937 | 0.2839 | -0.10885 | 0.088043 | 0.078197 | -0.028879 | 0.015831 | 0.17396 | 0.18174 | -0.1962 | 120.6401 | -1.2754 | 120.7271 | 120.7451 | 0.10502 | -1.2905 | -1.0985 | 120.5527 | -1.3666 | 120.8369 | 120.72 | 0.16732 | -1.2085 | -1.2007 | 120.856 | 120.8408 | 121.0328 | 120.7869 | -1.4913 | 120.7647 | 120.9229 | 120.9306 | 120.8271 | -1.5786
5910.4688 | 122.287 | -120.7489 | 1.4191 | -0.010149 | -0.071051 | 0.037302 | 0.014127 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0080591 | 0.022153 | 0.057568 | -0.0012393 | -0.017266 | 0.028878 | -0.008409 | 0.10707 | 0.08278 | 0.29306 | -0.10427 | 0.078886 | 0.087354 | -0.028879 | 0.020409 | 0.17396 | 0.168 | -0.19162 | 120.6446 | -1.312 | 120.7316 | 120.7405 | 0.095859 | -1.3363 | -1.126 | 120.5573 | -1.3987 | 120.8278 | 120.72 | 0.16274 | -1.2451 | -1.2511 | 120.856 | 120.8317 | 121.042 | 120.7778 | -1.5233 | 120.7693 | 120.9229 | 120.9169 | 120.8363 | -1.6107
5912.1875 | 122.3969 | -120.6848 | 1.4328 | -0.01778 | -0.071051 | 0.037729 | 0.013913 | -0.016138 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.022153 | 0.057354 | -0.0010255 | -0.021844 | 0.038035 | -0.012988 | 0.11165 | 0.087359 | 0.28848 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.024988 | 0.17396 | 0.17716 | -0.19162 | 120.576 | -1.3212 | 120.663 | 120.6718 | 0.095859 | -1.3454 | -1.1443 | 120.4932 | -1.4078 | 120.7637 | 120.6514 | 0.15816 | -1.2588 | -1.2556 | 120.7965 | 120.7722 | 120.9733 | 120.7228 | -1.5416 | 120.7098 | 120.8588 | 120.862 | 120.763 | -1.6244
5913.9062 | 122.2824 | -120.7123 | 1.4694 | -0.010149 | -0.071478 | 0.037516 | 0.013913 | -0.016138 | 0.0083799 | -0.029148 | -0.021494 | -0.0082729 | 0.02194 | 0.057354 | -0.00081186 | -0.017266 | 0.038035 | -0.003831 | 0.10707 | 0.08278 | 0.28848 | -0.10427 | 0.074307 | 0.078197 | -0.033458 | 0.024988 | 0.17854 | 0.17716 | -0.1962 | 120.608 | -1.3624 | 120.695 | 120.7084 | 0.10044 | -1.3866 | -1.1809 | 120.5161 | -1.4444 | 120.7866 | 120.6788 | 0.16274 | -1.2909 | -1.2923 | 120.8193 | 120.7951 | 121.0008 | 120.7503 | -1.5737 | 120.7373 | 120.8908 | 120.8894 | 120.7905 | -1.6656
5915.6406 | 122.3007 | -120.6802 | 1.4877 | -0.0025182 | -0.071051 | 0.037516 | 0.013913 | -0.016138 | 0.0088073 | -0.029148 | -0.021494 | -0.0082729 | 0.022153 | 0.057354 | -0.00081186 | -0.017266 | 0.047193 | -0.012988 | 0.10249 | 0.091937 | 0.28848 | -0.10885 | 0.074307 | 0.082776 | -0.028879 | 0.015831 | 0.17396 | 0.17716 | -0.20078 | 120.5714 | -1.3852 | 120.663 | 120.6672 | 0.095859 | -1.3958 | -1.1993 | 120.4795 | -1.4719 | 120.7545 | 120.6514 | 0.1719 | -1.3138 | -1.3106 | 120.7827 | 120.7722 | 120.9687 | 120.7274 | -1.5966 | 120.6961 | 120.8542 | 120.8574 | 120.763 | -1.6885
5917.375 | 122.3969 | -120.6116 | 1.474 | -0.010149 | -0.070837 | 0.037302 | 0.014127 | -0.015711 | 0.0085935 | -0.021518 | -0.021494 | -0.0080591 | 0.021726 | 0.05714 | -0.0010255 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.078201 | 0.29764 | -0.10885 | 0.083464 | 0.082776 | -0.0243 | 0.015831 | 0.17854 | 0.18174 | -0.19162 | 120.5027 | -1.3669 | 120.5943 | 120.6032 | 0.10044 | -1.3958 | -1.1764 | 120.42 | -1.4582 | 120.695 | 120.5873 | 0.16732 | -1.2955 | -1.2923 | 120.7186 | 120.6898 | 120.9092 | 120.645 | -1.5828 | 120.6274 | 120.7901 | 120.7933 | 120.6943 | -1.6656
5919.1094 | 122.4472 | -120.607 | 1.4969 | -0.010149 | -0.070837 | 0.037516 | 0.01434 | -0.015924 | 0.0085935 | -0.021518 | -0.02128 | -0.0084865 | 0.02194 | 0.057354 | -0.00081186 | -0.017266 | 0.038035 | -0.012988 | 0.11165 | 0.08278 | 0.28848 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.015831 | 0.17854 | 0.17716 | -0.1962 | 120.4981 | -1.3852 | 120.5897 | 120.594 | 0.095859 | -1.4141 | -1.2084 | 120.4108 | -1.4811 | 120.6859 | 120.5735 | 0.16274 | -1.3184 | -1.3197 | 120.7186 | 120.6898 | 120.8955 | 120.645 | -1.6057 | 120.6228 | 120.7855 | 120.7842 | 120.6852 | -1.6931
5920.8438 | 122.4289 | -120.5795 | 1.5106 | -0.025411 | -0.071692 | 0.037302 | 0.014127 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0082729 | 0.021726 | 0.057354 | -0.0010255 | -0.012688 | 0.033457 | -0.003831 | 0.11622 | 0.08278 | 0.28848 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.16938 | 0.17716 | -0.19162 | 120.4661 | -1.3944 | 120.5668 | 120.5757 | 0.10959 | -1.4278 | -1.2221 | 120.3879 | -1.4902 | 120.6584 | 120.5461 | 0.15816 | -1.3412 | -1.3335 | 120.6958 | 120.6623 | 120.868 | 120.613 | -1.624 | 120.5999 | 120.7489 | 120.7567 | 120.6669 | -1.7022
5922.625 | 122.4106 | -120.5612 | 1.561 | -0.010149 | -0.071051 | 0.037729 | 0.014127 | -0.016138 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.02194 | 0.057995 | -0.0010255 | -0.012688 | 0.038035 | -0.008409 | 0.10707 | 0.08278 | 0.29306 | -0.10427 | 0.078886 | 0.087354 | -0.028879 | 0.020409 | 0.16938 | 0.18174 | -0.19162 | 120.4569 | -1.4539 | 120.5485 | 120.5528 | 0.095859 | -1.4782 | -1.2679 | 120.3696 | -1.5406 | 120.6401 | 120.5323 | 0.16274 | -1.3916 | -1.3792 | 120.6683 | 120.644 | 120.8543 | 120.5993 | -1.6652 | 120.5816 | 120.7306 | 120.743 | 120.6486 | -1.7526
5924.3438 | 122.4152 | -120.575 | 1.5289 | -0.01778 | -0.071051 | 0.037729 | 0.014127 | -0.016138 | 0.0088073 | -0.029148 | -0.02128 | -0.0080591 | 0.022153 | 0.057354 | -0.0010255 | -0.012688 | 0.033457 | -0.008409 | 0.10707 | 0.078201 | 0.29306 | -0.10885 | 0.074307 | 0.091933 | -0.028879 | 0.024988 | 0.17854 | 0.17716 | -0.19162 | 120.4661 | -1.4219 | 120.5623 | 120.5665 | 0.10044 | -1.4507 | -1.2359 | 120.3833 | -1.5039 | 120.6493 | 120.5461 | 0.16274 | -1.3504 | -1.3518 | 120.682 | 120.6532 | 120.868 | 120.6084 | -1.6378 | 120.5999 | 120.7535 | 120.7521 | 120.6669 | -1.7206
5926.0781 | 122.2961 | -120.5246 | 1.6663 | -0.01778 | -0.071264 | 0.037729 | 0.014127 | -0.015924 | 0.0090209 | -0.029148 | -0.021067 | -0.0080591 | 0.022153 | 0.057354 | -0.0012393 | -0.017266 | 0.028878 | -0.003831 | 0.11165 | 0.08278 | 0.28848 | -0.10427 | 0.078886 | 0.091933 | -0.033458 | 0.024988 | 0.1648 | 0.17258 | -0.18704 | 120.4203 | -1.5546 | 120.5073 | 120.5208 | 0.10044 | -1.5835 | -1.3778 | 120.3376 | -1.6413 | 120.6035 | 120.4911 | 0.15358 | -1.5015 | -1.4937 | 120.6362 | 120.6074 | 120.8131 | 120.5535 | -1.7705 | 120.5496 | 120.6894 | 120.6972 | 120.6165 | -1.8533
5927.7812 | 122.3969 | -120.0714 | 2.0691 | -0.01778 | -0.070623 | 0.037516 | 0.014127 | -0.015924 | 0.0085935 | -0.029148 | -0.021494 | -0.0082729 | 0.022153 | 0.057781 | -0.00081186 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.024988 | 0.17854 | 0.17258 | -0.1962 | 119.9626 | -1.962 | 120.0541 | 120.063 | 0.10044 | -1.9817 | -1.7715 | 119.8752 | -2.0441 | 120.1503 | 120.038 | 0.16274 | -1.8906 | -1.8965 | 120.1785 | 120.1588 | 120.369 | 120.1049 | -2.1779 | 120.0964 | 120.2499 | 120.244 | 120.1496 | -2.2653
5929.5 | 122.438 | -120.1813 | 1.9089 | -0.01778 | -0.071478 | 0.037302 | 0.014127 | -0.015924 | 0.0083799 | -0.021518 | -0.021494 | -0.0082729 | 0.02194 | 0.057568 | -0.0010255 | -0.021844 | 0.042614 | -0.003831 | 0.10707 | 0.087359 | 0.29764 | -0.11342 | 0.074307 | 0.082776 | -0.028879 | 0.020409 | 0.16938 | 0.17716 | -0.20078 | 120.0678 | -1.8018 | 120.1594 | 120.1774 | 0.10959 | -1.8215 | -1.6112 | 119.9805 | -1.8885 | 120.2556 | 120.1524 | 0.1719 | -1.7395 | -1.7317 | 120.2883 | 120.2686 | 120.4789 | 120.2239 | -2.0223 | 120.2017 | 120.3507 | 120.3584 | 120.264 | -2.1097
5931.2031 | 122.3373 | -120.0439 | 2.1332 | -0.01778 | -0.071051 | 0.037516 | 0.013913 | -0.015711 | 0.0081663 | -0.013887 | -0.021494 | -0.0084865 | 0.022153 | 0.057354 | -0.0010255 | -0.012688 | 0.042614 | -0.003831 | 0.10707 | 0.091937 | 0.29306 | -0.10427 | 0.074307 | 0.087354 | -0.028879 | 0.015831 | 0.16938 | 0.17258 | -0.1962 | 119.9397 | -2.0261 | 120.0313 | 120.0401 | 0.10044 | -2.0412 | -1.8401 | 119.8477 | -2.1173 | 120.1183 | 120.0151 | 0.16732 | -1.9638 | -1.9606 | 120.151 | 120.1359 | 120.337 | 120.0866 | -2.2374 | 120.0598 | 120.2133 | 120.2165 | 120.1313 | -2.3294
5932.9375 | 122.4426 | -120.2591 | 1.886 | -0.010149 | -0.070837 | 0.037729 | 0.013913 | -0.015924 | 0.0085935 | -0.029148 | -0.02128 | -0.0082729 | 0.02194 | 0.057568 | -0.0010255 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.08278 | 0.28848 | -0.10885 | 0.074307 | 0.078197 | -0.033458 | 0.011252 | 0.17396 | 0.17258 | -0.20078 | 120.1502 | -1.7698 | 120.2418 | 120.2461 | 0.095859 | -1.8032 | -1.5975 | 120.0583 | -1.8747 | 120.3334 | 120.2256 | 0.16732 | -1.712 | -1.7134 | 120.3753 | 120.3419 | 120.5476 | 120.2971 | -1.9948 | 120.2703 | 120.4331 | 120.4317 | 120.3373 | -2.0868
5934.6875 | 122.3602 | -120.3598 | 1.8356 | -0.010149 | -0.071264 | 0.037516 | 0.013913 | -0.016352 | 0.0090209 | -0.013887 | -0.02128 | -0.0084865 | 0.022153 | 0.057354 | -0.0010255 | -0.012688 | 0.033457 | -0.003831 | 0.11622 | 0.091937 | 0.28848 | -0.10885 | 0.083464 | 0.082776 | -0.033458 | 0.020409 | 0.17396 | 0.17716 | -0.18704 | 120.251 | -1.7194 | 120.3471 | 120.356 | 0.10502 | -1.7437 | -1.5472 | 120.1728 | -1.8152 | 120.4433 | 120.3263 | 0.15358 | -1.6617 | -1.6585 | 120.476 | 120.4517 | 120.6483 | 120.3933 | -1.9445 | 120.3802 | 120.5338 | 120.537 | 120.4426 | -2.0227
5936.4219 | 122.3282 | -120.108 | 2.0828 | -0.010149 | -0.071051 | 0.037516 | 0.014127 | -0.015711 | 0.0088073 | -0.021518 | -0.02128 | -0.0087001 | 0.021512 | 0.05714 | -0.0010255 | -0.017266 | 0.033457 | -0.003831 | 0.11622 | 0.091937 | 0.29764 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.024988 | 0.16938 | 0.17258 | -0.1962 | 119.9946 | -1.9666 | 120.0908 | 120.1042 | 0.10959 | -1.9909 | -1.7852 | 119.9118 | -2.0578 | 120.1869 | 120.0746 | 0.16274 | -1.9134 | -1.9102 | 120.2243 | 120.2 | 120.4057 | 120.1415 | -2.1963 | 120.133 | 120.2774 | 120.2806 | 120.1954 | -2.279
5938.1406 | 122.3419 | -120.0989 | 2.092 | -0.025411 | -0.071051 | 0.037516 | 0.013913 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0082729 | 0.021726 | 0.05714 | -0.0012393 | -0.017266 | 0.038035 | -0.008409 | 0.11165 | 0.087359 | 0.28848 | -0.10427 | 0.074307 | 0.078197 | -0.033458 | 0.020409 | 0.17396 | 0.17716 | -0.19162 | 119.9946 | -1.9803 | 120.0816 | 120.0905 | 0.095859 | -2.0046 | -1.8035 | 119.9073 | -2.0716 | 120.1732 | 120.0654 | 0.15816 | -1.918 | -1.9148 | 120.2105 | 120.1862 | 120.3874 | 120.1369 | -2.1962 | 120.1193 | 120.2728 | 120.276 | 120.1771 | -2.2836
5939.8906 | 122.2733 | -119.4855 | 2.6917 | -0.010149 | -0.071051 | 0.037729 | 0.013699 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.021726 | 0.057354 | -0.0010255 | -0.008109 | 0.038035 | -0.003831 | 0.11165 | 0.087359 | 0.29306 | -0.11342 | 0.078886 | 0.087354 | -0.038036 | 0.029566 | 0.16938 | 0.17258 | -0.1962 | 119.372 | -2.58 | 119.4774 | 119.4816 | 0.10959 | -2.6043 | -2.3986 | 119.2893 | -2.6621 | 119.5644 | 119.4474 | 0.15816 | -2.5223 | -2.5191 | 119.5971 | 119.5728 | 119.7785 | 119.5235 | -2.8051 | 119.515 | 119.6549 | 119.6581 | 119.5728 | -2.8879
5941.6406 | 122.3969 | -118.2266 | 3.8864 | -0.033042 | -0.071478 | 0.037302 | 0.014127 | -0.016138 | 0.0085935 | -0.013887 | -0.021067 | -0.0082729 | 0.021726 | 0.057354 | -0.0010255 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.08278 | 0.30222 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.024988 | 0.17396 | 0.17258 | -0.18704 | 118.1178 | -3.7748 | 118.2094 | 118.2228 | 0.10502 | -3.8036 | -3.5842 | 118.0396 | -3.8614 | 118.3055 | 118.1932 | 0.15358 | -3.7125 | -3.7138 | 118.3383 | 118.3094 | 118.5288 | 118.2601 | -3.9953 | 118.2516 | 118.4006 | 118.3992 | 118.3094 | -4.0735
5943.3594 | 122.3511 | -119.5633 | 2.6184 | -0.01778 | -0.071264 | 0.037516 | 0.013699 | -0.016138 | 0.0085935 | -0.029148 | -0.02128 | -0.0082729 | 0.02194 | 0.057781 | -0.0012393 | -0.017266 | 0.038035 | -0.003831 | 0.10707 | 0.087359 | 0.29306 | -0.10427 | 0.074307 | 0.087354 | -0.033458 | 0.020409 | 0.16938 | 0.17716 | -0.1962 | 119.459 | -2.5113 | 119.546 | 119.5595 | 0.10044 | -2.531 | -2.3253 | 119.3671 | -2.598 | 119.6376 | 119.5298 | 0.16274 | -2.449 | -2.4412 | 119.6704 | 119.6507 | 119.8564 | 119.6013 | -2.7227 | 119.5837 | 119.7327 | 119.7405 | 119.6506 | -2.8146
5945.0625 | 122.4106 | -120.5154 | 1.6571 | -0.0025182 | -0.071264 | 0.037088 | 0.013486 | -0.015924 | 0.0088073 | -0.013887 | -0.021494 | -0.0084865 | 0.02194 | 0.057568 | -0.0012393 | -0.012688 | 0.028878 | -0.012988 | 0.11165 | 0.08278 | 0.28848 | -0.10427 | 0.083464 | 0.082776 | -0.038036 | 0.029566 | 0.17396 | 0.17258 | -0.20078 | 120.4112 | -1.5455 | 120.5028 | 120.5025 | 0.09128 | -1.5743 | -1.3686 | 120.3147 | -1.6275 | 120.5989 | 120.4774 | 0.16274 | -1.4831 | -1.4845 | 120.6271 | 120.5982 | 120.8039 | 120.5443 | -1.7614 | 120.545 | 120.6894 | 120.688 | 120.5982 | -1.8579
5946.7812 | 122.3465 | -120.3278 | 1.8356 | 0.0051128 | -0.071264 | 0.037302 | 0.013913 | -0.015711 | 0.0088073 | -0.029148 | -0.02128 | -0.0080591 | 0.021726 | 0.057781 | -0.0010255 | -0.017266 | 0.028878 | -0.008409 | 0.11165 | 0.087359 | 0.29306 | -0.10885 | 0.083464 | 0.078197 | -0.033458 | 0.024988 | 0.17396 | 0.18174 | -0.1962 | 120.2189 | -1.724 | 120.3105 | 120.3194 | 0.10044 | -1.7483 | -1.5426 | 120.1316 | -1.8106 | 120.4112 | 120.2943 | 0.16274 | -1.6617 | -1.6539 | 120.4394 | 120.4151 | 120.6208 | 120.3566 | -1.9445 | 120.3527 | 120.5017 | 120.5095 | 120.406 | -2.0318
5948.5781 | 122.4197 | -120.6253 | 1.5381 | -0.010149 | -0.071051 | 0.037302 | 0.013699 | -0.015924 | 0.0088073 | -0.029148 | -0.02128 | -0.0082729 | 0.021512 | 0.057568 | -0.0012393 | -0.017266 | 0.042614 | -0.012988 | 0.10249 | 0.087359 | 0.29306 | -0.11342 | 0.078886 | 0.091933 | -0.033458 | 0.020409 | 0.16938 | 0.17258 | -0.20078 | 120.5119 | -1.4356 | 120.608 | 120.6123 | 0.10044 | -1.4507 | -1.245 | 120.4245 | -1.5177 | 120.7042 | 120.5918 | 0.16732 | -1.3687 | -1.3655 | 120.7278 | 120.7127 | 120.9184 | 120.6679 | -1.6515 | 120.6457 | 120.7947 | 120.7979 | 120.7172 | -1.7389
5950.2969 | 122.4426 | -120.5887 | 1.5518 | -0.01778 | -0.071264 | 0.037516 | 0.013699 | -0.015924 | 0.0085935 | -0.029148 | -0.02128 | -0.0082729 | 0.022153 | 0.057354 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.087359 | 0.29306 | -0.10427 | 0.078886 | 0.087354 | -0.028879 | 0.024988 | 0.17396 | 0.17716 | -0.20078 | 120.4844 | -1.4448 | 120.5714 | 120.5803 | 0.095859 | -1.4645 | -1.2588 | 120.3879 | -1.5268 | 120.6676 | 120.5598 | 0.1719 | -1.3779 | -1.3747 | 120.6958 | 120.676 | 120.8817 | 120.6221 | -1.6561 | 120.6137 | 120.7626 | 120.7658 | 120.676 | -1.7526
5952.0781 | 122.4701 | -120.4605 | 1.6479 | -0.01778 | -0.071264 | 0.037516 | 0.013699 | -0.015924 | 0.0088073 | -0.029148 | -0.021494 | -0.0084865 | 0.021726 | 0.057781 | -0.0010255 | -0.017266 | 0.0243 | -0.008409 | 0.10707 | 0.087359 | 0.29306 | -0.10427 | 0.074307 | 0.087354 | -0.033458 | 0.024988 | 0.17396 | 0.17716 | -0.1962 | 120.3562 | -1.5409 | 120.4432 | 120.4521 | 0.095859 | -1.5606 | -1.3549 | 120.2643 | -1.623 | 120.5348 | 120.4271 | 0.16274 | -1.474 | -1.4708 | 120.5676 | 120.5479 | 120.7536 | 120.4848 | -1.7522 | 120.4855 | 120.6345 | 120.6377 | 120.5479 | -1.8441
5953.7812 | 122.3419 | -120.5154 | 1.7075 | -0.010149 | -0.071051 | 0.037516 | 0.013913 | -0.015924 | 0.0090209 | -0.036779 | -0.021708 | -0.0087001 | 0.02194 | 0.057568 | -0.00081186 | -0.017266 | 0.028878 | -0.008409 | 0.11165 | 0.091937 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.16938 | 0.168 | -0.20078 | 120.4066 | -1.5958 | 120.4982 | 120.507 | 0.10044 | -1.6155 | -1.4098 | 120.3147 | -1.687 | 120.5943 | 120.482 | 0.16732 | -1.5381 | -1.5395 | 120.6271 | 120.6074 | 120.8131 | 120.5443 | -1.8163 | 120.5359 | 120.6848 | 120.6834 | 120.6028 | -1.9082
5955.5156 | 122.3602 | -120.4559 | 1.7578 | -0.010149 | -0.071264 | 0.037516 | 0.013913 | -0.015711 | 0.0085935 | -0.029148 | -0.021494 | -0.0080591 | 0.02194 | 0.057781 | -0.0010255 | -0.017266 | 0.033457 | -0.003831 | 0.10249 | 0.087359 | 0.29306 | -0.10885 | 0.078886 | 0.078197 | -0.0243 | 0.024988 | 0.16938 | 0.17258 | -0.20078 | 120.3471 | -1.6553 | 120.4387 | 120.4521 | 0.10502 | -1.6705 | -1.4648 | 120.2552 | -1.7328 | 120.5348 | 120.4316 | 0.17648 | -1.5884 | -1.5852 | 120.5584 | 120.5433 | 120.749 | 120.4894 | -1.8667 | 120.4809 | 120.6253 | 120.6285 | 120.5341 | -1.9586
5957.2188 | 122.374 | -120.4239 | 1.799 | -0.025411 | -0.071264 | 0.037516 | 0.01434 | -0.015924 | 0.0088073 | -0.013887 | -0.021067 | -0.0080591 | 0.02194 | 0.057568 | -0.0012393 | -0.017266 | 0.028878 | -0.017566 | 0.11165 | 0.078201 | 0.29764 | -0.09511 | 0.078886 | 0.078197 | -0.038036 | 0.020409 | 0.16938 | 0.17258 | -0.20078 | 120.3288 | -1.6874 | 120.4066 | 120.4063 | 0.077544 | -1.7208 | -1.5014 | 120.2231 | -1.7786 | 120.5028 | 120.3859 | 0.16274 | -1.6296 | -1.6264 | 120.5355 | 120.5021 | 120.7215 | 120.4528 | -1.8941 | 120.4443 | 120.5933 | 120.5965 | 120.5021 | -1.9998
5958.9219 | 122.4655 | -120.314 | 1.886 | -0.025411 | -0.071264 | 0.037516 | 0.014127 | -0.015711 | 0.0085935 | -0.021518 | -0.02128 | -0.0082729 | 0.022153 | 0.057781 | -0.0010255 | -0.008109 | 0.0243 | 0.000747 | 0.10707 | 0.08278 | 0.29306 | -0.11342 | 0.078886 | 0.087354 | -0.028879 | 0.015831 | 0.16938 | 0.17716 | -0.1962 | 120.2006 | -1.7789 | 120.3059 | 120.3148 | 0.11417 | -1.8032 | -1.5929 | 120.1178 | -1.8702 | 120.3929 | 120.2851 | 0.16732 | -1.7166 | -1.7088 | 120.4211 | 120.3968 | 120.6071 | 120.3383 | -1.9994 | 120.3299 | 120.4834 | 120.4912 | 120.4014 | -2.0822
5960.6406 | 122.3511 | -119.8654 | 2.3987 | -0.0025182 | -0.071051 | 0.037516 | 0.014127 | -0.016138 | 0.0090209 | -0.021518 | -0.02128 | -0.0082729 | 0.022153 | 0.057781 | -0.0010255 | -0.021844 | 0.0243 | 0.000747 | 0.10707 | 0.08278 | 0.28848 | -0.11342 | 0.074307 | 0.082776 | -0.038036 | 0.020409 | 0.17396 | 0.17258 | -0.20078 | 119.752 | -2.2916 | 119.8436 | 119.8662 | 0.11417 | -2.3159 | -2.1102 | 119.6646 | -2.3783 | 119.9397 | 119.8274 | 0.16274 | -2.2247 | -2.2261 | 119.9725 | 119.9482 | 120.1539 | 119.8897 | -2.5121 | 119.8858 | 120.0394 | 120.038 | 119.9482 | -2.5995
5962.3438 | 122.4564 | -120.0943 | 2.0645 | -0.010149 | -0.071478 | 0.037516 | 0.013913 | -0.015924 | 0.0083799 | -0.013887 | -0.02128 | -0.0084865 | 0.021512 | 0.057354 | -0.0012393 | -0.012688 | 0.033457 | -0.003831 | 0.10707 | 0.087359 | 0.28848 | -0.099689 | 0.078886 | 0.078197 | -0.028879 | 0.024988 | 0.17396 | 0.17716 | -0.20078 | 119.9946 | -1.9574 | 120.0816 | 120.0905 | 0.095858 | -1.9772 | -1.776 | 119.8935 | -2.0395 | 120.1732 | 120.0654 | 0.1719 | -1.8906 | -1.8874 | 120.2014 | 120.1817 | 120.3828 | 120.1278 | -2.1642 | 120.1193 | 120.2683 | 120.2715 | 120.1725 | -2.2653
5964.0469 | 122.3969 | -119.5267 | 2.6962 | -0.01778 | -0.071264 | 0.037516 | 0.013913 | -0.016138 | 0.0088073 | -0.013887 | -0.02128 | -0.0082729 | 0.022153 | 0.057781 | -0.0012393 | -0.017266 | 0.028878 | 0.000747 | 0.11165 | 0.091937 | 0.27932 | -0.099689 | 0.078886 | 0.082776 | -0.033458 | 0.020409 | 0.1648 | 0.168 | -0.19162 | 119.427 | -2.5846 | 119.5094 | 119.5274 | 0.10044 | -2.6043 | -2.4169 | 119.3351 | -2.6758 | 119.6056 | 119.4932 | 0.15816 | -2.5314 | -2.5282 | 119.6383 | 119.6186 | 119.806 | 119.5556 | -2.7959 | 119.5471 | 119.6915 | 119.6947 | 119.6094 | -2.8879
5965.75 | 122.4838 | -119.0643 | 3.0716 | -0.010149 | -0.071478 | 0.037302 | 0.013913 | -0.016138 | 0.0085935 | -0.021518 | -0.021708 | -0.0084865 | 0.02194 | 0.057781 | -0.0014529 | -0.021844 | 0.028878 | -0.008409 | 0.1208 | 0.078201 | 0.29764 | -0.099689 | 0.078886 | 0.078197 | -0.0243 | 0.024988 | 0.16938 | 0.17716 | -0.20078 | 118.9646 | -2.9508 | 119.0425 | 119.0559 | 0.09128 | -2.9934 | -2.774 | 118.8636 | -3.0466 | 119.1432 | 119.04 | 0.17648 | -2.9022 | -2.8944 | 119.1851 | 119.1425 | 119.362 | 119.0932 | -3.1713 | 119.0893 | 119.2337 | 119.2415 | 119.1425 | -3.2724
5967.5469 | 122.4335 | -119.0598 | 3.1265 | -0.01778 | -0.071051 | 0.037302 | 0.013699 | -0.016138 | 0.0090209 | -0.036779 | -0.021708 | -0.0082729 | 0.022367 | 0.057781 | -0.00081186 | -0.017266 | 0.028878 | -0.012988 | 0.10249 | 0.091937 | 0.28848 | -0.10885 | 0.083464 | 0.087354 | -0.028879 | 0.020409 | 0.17396 | 0.168 | -0.1962 | 118.9509 | -3.024 | 119.0425 | 119.0468 | 0.095859 | -3.0346 | -2.838 | 118.8636 | -3.1061 | 119.1432 | 119.0309 | 0.16732 | -2.9526 | -2.9585 | 119.1622 | 119.1517 | 119.3482 | 119.0886 | -3.2354 | 119.0802 | 119.2337 | 119.2278 | 119.1471 | -3.3227
5969.2812 | 122.4472 | -118.1213 | 4.01 | -0.01778 | -0.071264 | 0.037302 | 0.013913 | -0.015924 | 0.0085935 | -0.021518 | -0.02128 | -0.0080591 | 0.02194 | 0.057354 | -0.0010255 | -0.008109 | 0.033457 | -0.012988 | 0.11165 | 0.08278 | 0.28848 | -0.10427 | 0.069728 | 0.082776 | -0.033458 | 0.020409 | 0.16938 | 0.17716 | -0.1962 | 118.0171 | -3.8984 | 118.1132 | 118.1084 | 0.09128 | -3.9272 | -3.7215 | 117.9251 | -3.9896 | 118.1911 | 118.0879 | 0.16274 | -3.8406 | -3.8329 | 118.233 | 118.2041 | 118.4098 | 118.1548 | -4.1143 | 118.1417 | 118.2907 | 118.2985 | 118.2041 | -4.2062
5970.9844 | 122.3694 | -120.2179 | 2.0096 | -0.010149 | -0.071264 | 0.037302 | 0.014127 | -0.015924 | 0.0083799 | -0.021518 | -0.021708 | -0.0082729 | 0.022153 | 0.057568 | -0.0012393 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.08278 | 0.28848 | -0.10427 | 0.083464 | 0.087354 | -0.033458 | 0.024988 | 0.16938 | 0.17716 | -0.18246 | 120.1136 | -1.9025 | 120.2006 | 120.2141 | 0.10044 | -1.9268 | -1.7211 | 120.0354 | -1.9846 | 120.3014 | 120.1844 | 0.14901 | -1.8402 | -1.8324 | 120.325 | 120.3007 | 120.5064 | 120.2514 | -2.1139 | 120.2429 | 120.3873 | 120.3951 | 120.3053 | -2.192
5972.7188 | 122.4838 | -120.1355 | 2.0142 | -0.010149 | -0.071478 | 0.037302 | 0.013699 | -0.015924 | 0.0083799 | -0.021518 | -0.021067 | -0.0082729 | 0.021726 | 0.057354 | -0.0010255 | -0.012688 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.29306 | -0.10885 | 0.083464 | 0.082776 | -0.028879 | 0.024988 | 0.1648 | 0.17716 | -0.1962 | 120.0267 | -1.9025 | 120.1228 | 120.1271 | 0.10044 | -1.9268 | -1.7211 | 119.9393 | -1.9892 | 120.219 | 120.1066 | 0.16732 | -1.8494 | -1.837 | 120.2471 | 120.2229 | 120.4286 | 120.169 | -2.123 | 120.1605 | 120.3003 | 120.3127 | 120.2183 | -2.2104
5974.4219 | 122.3923 | -119.6732 | 2.5131 | -0.01778 | -0.071051 | 0.037088 | 0.014127 | -0.015924 | 0.0088073 | -0.013887 | -0.02128 | -0.0084865 | 0.021726 | 0.057781 | -0.0014529 | -0.012688 | 0.033457 | -0.012988 | 0.11165 | 0.091937 | 0.29306 | -0.10885 | 0.083464 | 0.082776 | -0.038036 | 0.015831 | 0.17396 | 0.17258 | -0.19162 | 119.5643 | -2.4015 | 119.6605 | 119.6602 | 0.095859 | -2.4212 | -2.2201 | 119.4815 | -2.4973 | 119.7566 | 119.6351 | 0.15359 | -2.3392 | -2.3405 | 119.7848 | 119.7651 | 119.9662 | 119.7066 | -2.622 | 119.689 | 119.8471 | 119.8457 | 119.7559 | -2.7047
5976.125 | 122.3694 | -119.1238 | 3.1174 | -0.01778 | -0.071264 | 0.037516 | 0.014127 | -0.015924 | 0.0085935 | -0.013887 | -0.02128 | -0.0082729 | 0.021726 | 0.057781 | -0.0014529 | -0.021844 | 0.028878 | -0.012988 | 0.11165 | 0.087359 | 0.29306 | -0.118 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.17258 | -0.19162 | 119.0058 | -3.0057 | 119.102 | 119.1109 | 0.10502 | -3.03 | -2.8243 | 118.9322 | -3.1015 | 119.2027 | 119.0904 | 0.15816 | -2.948 | -2.9448 | 119.2355 | 119.2112 | 119.4169 | 119.1527 | -3.2354 | 119.1397 | 119.2932 | 119.2964 | 119.2066 | -3.309
5977.8594 | 122.3648 | -119.9295 | 2.2888 | -0.010149 | -0.071264 | 0.037516 | 0.014127 | -0.015924 | 0.0090209 | -0.021518 | -0.02128 | -0.0082729 | 0.022153 | 0.057568 | -0.0012393 | -0.021844 | 0.033457 | -0.003831 | 0.10707 | 0.091937 | 0.28848 | -0.10885 | 0.078886 | 0.082776 | -0.0243 | 0.015831 | 0.1648 | 0.17716 | -0.18704 | 119.8207 | -2.1818 | 119.9077 | 119.9257 | 0.10502 | -2.1969 | -2.0003 | 119.7425 | -2.273 | 120.0084 | 119.9052 | 0.16274 | -2.124 | -2.1117 | 120.0366 | 120.0214 | 120.218 | 119.963 | -2.3977 | 119.9453 | 120.0943 | 120.1067 | 120.0123 | -2.4759
5979.5625 | 122.3648 | -119.4763 | 2.7603 | -0.010149 | -0.071692 | 0.037088 | 0.014127 | -0.016138 | 0.0083799 | -0.029148 | -0.021494 | -0.0084865 | 0.022153 | 0.057568 | -0.0010255 | -0.021844 | 0.038035 | -0.008409 | 0.12538 | 0.087359 | 0.30222 | -0.10885 | 0.06515 | 0.087354 | -0.033458 | 0.015831 | 0.16938 | 0.17258 | -0.1962 | 119.3675 | -2.6349 | 119.4545 | 119.4679 | 0.10044 | -2.673 | -2.4581 | 119.2801 | -2.7445 | 119.5415 | 119.4429 | 0.16274 | -2.5909 | -2.5877 | 119.6017 | 119.5637 | 119.7785 | 119.5144 | -2.8692 | 119.4921 | 119.6457 | 119.6489 | 119.5637 | -2.9565
5981.2812 | 122.3602 | -119.1284 | 3.1265 | -0.010149 | -0.071478 | 0.037088 | 0.013913 | -0.015924 | 0.0085935 | -0.021518 | -0.021067 | -0.0084865 | 0.021512 | 0.057568 | -0.0010255 | -0.017266 | 0.0243 | -0.003831 | 0.11165 | 0.08278 | 0.29306 | -0.118 | 0.083464 | 0.082776 | -0.028879 | 0.024988 | 0.17396 | 0.168 | -0.18704 | 119.0104 | -3.0149 | 119.1112 | 119.1246 | 0.11417 | -3.0437 | -2.8335 | 118.9414 | -3.1015 | 119.2119 | 119.0995 | 0.15816 | -2.9526 | -2.9585 | 119.2401 | 119.2112 | 119.4215 | 119.1527 | -3.2445 | 119.1534 | 119.3024 | 119.2964 | 119.2112 | -3.3136
5982.9844 | 122.4701 | -119.3069 | 2.8336 | -0.010149 | -0.071478 | 0.037088 | 0.013913 | -0.015924 | 0.0085935 | -0.029148 | -0.02128 | -0.0082729 | 0.022153 | 0.057781 | -0.0012393 | -0.012688 | 0.033457 | -0.012988 | 0.11165 | 0.087359 | 0.29306 | -0.10427 | 0.074307 | 0.087354 | -0.028879 | 0.024988 | 0.17396 | 0.17258 | -0.1962 | 119.2027 | -2.7219 | 119.2943 | 119.294 | 0.09128 | -2.7462 | -2.5405 | 119.1107 | -2.8086 | 119.3813 | 119.2781 | 0.16732 | -2.6596 | -2.661 | 119.4186 | 119.3943 | 119.6 | 119.3404 | -2.9378 | 119.3319 | 119.4809 | 119.4795 | 119.3943 | -3.0298
5984.7188 | 122.4838 | -119.2703 | 2.9022 | -0.01778 | -0.071264 | 0.037088 | 0.013913 | -0.015711 | 0.0083799 | -0.013887 | -0.021494 | -0.0084865 | 0.021726 | 0.057781 | -0.0010255 | -0.017266 | 0.028878 | 0.000747 | 0.11165 | 0.08278 | 0.29306 | -0.10885 | 0.078886 | 0.082776 | -0.042615 | 0.015831 | 0.17854 | 0.17258 | -0.1962 | 119.1615 | -2.7906 | 119.2531 | 119.2711 | 0.10959 | -2.8194 | -2.6092 | 119.0741 | -2.8864 | 119.3492 | 119.2277 | 0.15359 | -2.7237 | -2.7296 | 119.382 | 119.3531 | 119.5634 | 119.2992 | -3.0111 | 119.2862 | 119.4489 | 119.4429 | 119.3531 | -3.0984
5986.4219 | 122.4014 | -119.5175 | 2.7191 | -0.010149 | -0.071478 | 0.037302 | 0.013913 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0080591 | 0.02194 | 0.057781 | -0.0012393 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.020409 | 0.17396 | 0.17258 | -0.18704 | 119.4087 | -2.612 | 119.5003 | 119.5137 | 0.10502 | -2.6318 | -2.4215 | 119.3305 | -2.6987 | 119.5964 | 119.4795 | 0.14901 | -2.5452 | -2.5465 | 119.6246 | 119.6049 | 119.8152 | 119.551 | -2.828 | 119.5379 | 119.6915 | 119.6901 | 119.6003 | -2.9062
5988.1562 | 122.5113 | -119.6091 | 2.5772 | -0.010149 | -0.071478 | 0.037516 | 0.013913 | -0.015924 | 0.0088073 | -0.021518 | -0.02128 | -0.0082729 | 0.021726 | 0.057568 | -0.0012393 | -0.021844 | 0.038035 | -0.003831 | 0.11165 | 0.08278 | 0.29764 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.020409 | 0.17854 | 0.17258 | -0.19162 | 119.4956 | -2.4656 | 119.5872 | 119.6052 | 0.10959 | -2.4944 | -2.2796 | 119.4174 | -2.5568 | 119.688 | 119.5756 | 0.15816 | -2.3987 | -2.4046 | 119.7207 | 119.6919 | 119.9067 | 119.6471 | -2.6906 | 119.6295 | 119.7876 | 119.7816 | 119.6918 | -2.7688
5989.8594 | 122.374 | -117.4393 | 4.7333 | -0.010149 | -0.071264 | 0.037516 | 0.013913 | -0.015924 | 0.0085935 | -0.013887 | -0.02128 | -0.0084865 | 0.021512 | 0.057568 | -0.0012393 | -0.012688 | 0.038035 | -0.003831 | 0.10707 | 0.087359 | 0.29764 | -0.099689 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.17854 | 0.17716 | -0.19162 | 117.3396 | -4.6262 | 117.4266 | 117.4354 | 0.095858 | -4.6459 | -4.4356 | 117.2476 | -4.7129 | 117.5182 | 117.4058 | 0.15816 | -4.5547 | -4.5561 | 117.5463 | 117.5266 | 117.7369 | 117.4773 | -4.833 | 117.4597 | 117.6178 | 117.6164 | 117.5266 | -4.9249
5991.6094 | 122.438 | -119.3802 | 2.7695 | -0.01778 | -0.071478 | 0.037302 | 0.013913 | -0.016138 | 0.0085935 | -0.021518 | -0.021067 | -0.0087001 | 0.022367 | 0.057781 | -0.0010255 | -0.021844 | 0.038035 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.17854 | 0.17716 | -0.1962 | 119.2668 | -2.6578 | 119.3583 | 119.3764 | 0.10959 | -2.6821 | -2.4718 | 119.184 | -2.7491 | 119.4591 | 119.3467 | 0.16274 | -2.5909 | -2.5923 | 119.4918 | 119.4675 | 119.6778 | 119.4182 | -2.8829 | 119.4006 | 119.5587 | 119.5573 | 119.4675 | -2.9657
5993.2969 | 122.4152 | -119.5541 | 2.6871 | -0.0025182 | -0.071478 | 0.037088 | 0.013913 | -0.015924 | 0.0083799 | -0.021518 | -0.021494 | -0.0082729 | 0.02194 | 0.057568 | -0.0014529 | -0.017266 | 0.028878 | -0.003831 | 0.11165 | 0.087359 | 0.29306 | -0.10885 | 0.074307 | 0.091933 | -0.028879 | 0.015831 | 0.16938 | 0.168 | -0.19162 | 119.4453 | -2.5754 | 119.5369 | 119.5503 | 0.10502 | -2.5997 | -2.394 | 119.3625 | -2.6712 | 119.6284 | 119.5253 | 0.16274 | -2.5177 | -2.5191 | 119.6658 | 119.6415 | 119.8472 | 119.583 | -2.7959 | 119.57 | 119.7235 | 119.7221 | 119.6461 | -2.8787
5995.0312 | 122.3557 | -119.5908 | 2.6779 | -0.010149 | -0.071264 | 0.037302 | 0.013913 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0080591 | 0.02194 | 0.057568 | -0.0012393 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.29764 | -0.10427 | 0.083464 | 0.091933 | -0.038036 | 0.024988 | 0.16938 | 0.17258 | -0.1962 | 119.4865 | -2.5617 | 119.5781 | 119.5824 | 0.095859 | -2.586 | -2.3803 | 119.3946 | -2.6529 | 119.6742 | 119.5527 | 0.15816 | -2.5085 | -2.5053 | 119.707 | 119.6827 | 119.8884 | 119.6242 | -2.7822 | 119.6157 | 119.7601 | 119.7633 | 119.6827 | -2.8741
5996.7812 | 122.3831 | -119.2841 | 2.98 | -0.010149 | -0.071264 | 0.037302 | 0.013699 | -0.015711 | 0.0085935 | -0.021518 | -0.021067 | -0.0082729 | 0.02194 | 0.057781 | -0.0010255 | -0.017266 | 0.028878 | -0.003831 | 0.11165 | 0.087359 | 0.28848 | -0.10885 | 0.083464 | 0.087354 | -0.038036 | 0.015831 | 0.16938 | 0.17258 | -0.1962 | 119.1752 | -2.8684 | 119.2668 | 119.2802 | 0.10502 | -2.8927 | -2.6916 | 119.0879 | -2.9642 | 119.3675 | 119.246 | 0.15816 | -2.8107 | -2.8075 | 119.3957 | 119.3714 | 119.5725 | 119.3129 | -3.0889 | 119.2999 | 119.4534 | 119.4566 | 119.3714 | -3.1762
5998.4844 | 122.406 | -119.5633 | 2.6642 | -0.01778 | -0.071478 | 0.037516 | 0.014127 | -0.016138 | 0.0083799 | -0.013887 | -0.021708 | -0.0082729 | 0.021726 | 0.057781 | -0.0012393 | -0.021844 | 0.038035 | -0.008409 | 0.11622 | 0.08278 | 0.29306 | -0.10427 | 0.078886 | 0.091933 | -0.033458 | 0.024988 | 0.17396 | 0.17258 | -0.20078 | 119.459 | -2.548 | 119.5414 | 119.5549 | 0.095859 | -2.5814 | -2.3711 | 119.3625 | -2.6392 | 119.6422 | 119.5298 | 0.16732 | -2.4902 | -2.4916 | 119.6795 | 119.6461 | 119.8564 | 119.6013 | -2.7685 | 119.5883 | 119.7373 | 119.7359 | 119.6552 | -2.865
6000.1875 | 122.4792 | -119.8196 | 2.3483 | -0.01778 | -0.071478 | 0.037516 | 0.013699 | -0.015924 | 0.0090209 | -0.021518 | -0.02128 | -0.0080591 | 0.021726 | 0.057354 | -0.0010255 | -0.008109 | 0.0243 | -0.008409 | 0.11622 | 0.08278 | 0.29764 | -0.11342 | 0.088043 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.17258 | -0.20078 | 119.7062 | -2.2321 | 119.8115 | 119.8112 | 0.10502 | -2.2655 | -2.0507 | 119.6189 | -2.3325 | 119.9077 | 119.7862 | 0.16732 | -2.1789 | -2.1757 | 119.9359 | 119.9024 | 120.1173 | 119.8439 | -2.4618 | 119.8355 | 119.989 | 119.9922 | 119.9024 | -2.5491
6001.8906 | 122.4152 | -120.0119 | 2.2705 | -0.01778 | -0.071478 | 0.037516 | 0.014127 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.022153 | 0.057781 | -0.0012393 | -0.021844 | 0.028878 | -0.008409 | 0.11165 | 0.08278 | 0.29306 | -0.10427 | 0.088043 | 0.082776 | -0.028879 | 0.015831 | 0.16938 | 0.17716 | -0.19162 | 119.9076 | -2.1589 | 119.9901 | 120.0035 | 0.095859 | -2.1877 | -1.9774 | 119.8203 | -2.2547 | 120.0999 | 119.983 | 0.16274 | -2.1011 | -2.0933 | 120.1235 | 120.0947 | 120.305 | 120.0408 | -2.3748 | 120.0277 | 120.1813 | 120.1891 | 120.0947 | -2.4621
6003.6406 | 122.3877 | -119.8563 | 2.4307 | -0.0025182 | -0.071264 | 0.037516 | 0.013699 | -0.016352 | 0.0085935 | -0.013887 | -0.02128 | -0.0082729 | 0.021726 | 0.057781 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.28848 | -0.11342 | 0.083464 | 0.082776 | -0.033458 | 0.015831 | 0.18311 | 0.17258 | -0.19162 | 119.7428 | -2.3191 | 119.839 | 119.8479 | 0.10502 | -2.3434 | -2.1422 | 119.6646 | -2.4149 | 119.9397 | 119.8228 | 0.15816 | -2.2476 | -2.2581 | 119.9679 | 119.9436 | 120.1447 | 119.8897 | -2.5441 | 119.8721 | 120.0394 | 120.0288 | 119.939 | -2.6223
6005.3438 | 122.4655 | -119.4122 | 2.7969 | -0.010149 | -0.071478 | 0.037516 | 0.013699 | -0.015711 | 0.0088073 | -0.029148 | -0.021494 | -0.0084865 | 0.021726 | 0.057781 | -0.0010255 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.099689 | 0.083464 | 0.082776 | -0.028879 | 0.020409 | 0.16938 | 0.168 | -0.1962 | 119.3125 | -2.6853 | 119.395 | 119.4084 | 0.095858 | -2.7096 | -2.4993 | 119.216 | -2.7765 | 119.4957 | 119.3834 | 0.16732 | -2.6276 | -2.6289 | 119.5239 | 119.4996 | 119.7099 | 119.4457 | -2.8966 | 119.4326 | 119.5816 | 119.5802 | 119.495 | -2.9931
6007.0469 | 122.4335 | -119.5496 | 2.7237 | -0.010149 | -0.071905 | 0.037516 | 0.013699 | -0.015924 | 0.0085935 | -0.021518 | -0.02128 | -0.0082729 | 0.02194 | 0.057568 | -0.00081186 | -0.021844 | 0.028878 | -0.008409 | 0.11622 | 0.08278 | 0.29306 | -0.10427 | 0.074307 | 0.087354 | -0.0243 | 0.020409 | 0.16938 | 0.17716 | -0.20078 | 119.4453 | -2.6075 | 119.5277 | 119.5412 | 0.095859 | -2.6409 | -2.4306 | 119.3488 | -2.7033 | 119.6239 | 119.5253 | 0.17648 | -2.5543 | -2.5465 | 119.6658 | 119.6323 | 119.8426 | 119.5784 | -2.828 | 119.57 | 119.7189 | 119.7267 | 119.6369 | -2.9245
6008.75 | 122.438 | -119.7418 | 2.449 | -0.010149 | -0.071692 | 0.037302 | 0.013699 | -0.016138 | 0.0085935 | -0.021518 | -0.021494 | -0.0080591 | 0.02194 | 0.057995 | -0.00081186 | -0.021844 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.30222 | -0.10885 | 0.092622 | 0.091933 | -0.038036 | 0.020409 | 0.17396 | 0.17716 | -0.1962 | 119.633 | -2.3374 | 119.72 | 119.7334 | 0.10044 | -2.3617 | -2.1468 | 119.5456 | -2.4286 | 119.8344 | 119.7038 | 0.15816 | -2.2751 | -2.2719 | 119.8535 | 119.8292 | 120.044 | 119.7753 | -2.5579 | 119.7622 | 119.9158 | 119.919 | 119.8338 | -2.6452
6010.4844 | 122.4243 | -119.8334 | 2.3941 | -0.0025182 | -0.071478 | 0.037302 | 0.013913 | -0.015924 | 0.0083799 | -0.013887 | -0.021494 | -0.0084865 | 0.02194 | 0.057781 | -0.0010255 | -0.021844 | 0.033457 | -0.012988 | 0.11165 | 0.091937 | 0.29306 | -0.10885 | 0.083464 | 0.082776 | -0.028879 | 0.015831 | 0.17396 | 0.168 | -0.20078 | 119.7245 | -2.2825 | 119.8115 | 119.8204 | 0.095859 | -2.3022 | -2.101 | 119.6326 | -2.3783 | 119.9168 | 119.8045 | 0.1719 | -2.2201 | -2.2261 | 119.945 | 119.9253 | 120.1264 | 119.8668 | -2.503 | 119.8492 | 120.0073 | 120.0014 | 119.9162 | -2.5949
6012.1875 | 122.5204 | -120.0302 | 2.1835 | -0.010149 | -0.071692 | 0.037729 | 0.013699 | -0.016138 | 0.0085935 | -0.029148 | -0.021494 | -0.0089137 | 0.021726 | 0.057781 | -0.0010255 | -0.021844 | 0.038035 | 0.000747 | 0.11165 | 0.08278 | 0.29764 | -0.10427 | 0.074307 | 0.082776 | -0.033458 | 0.020409 | 0.17396 | 0.17716 | -0.1962 | 119.9259 | -2.0719 | 120.0084 | 120.031 | 0.10501 | -2.1008 | -1.8859 | 119.834 | -2.1631 | 120.1045 | 119.9968 | 0.16274 | -2.0096 | -2.0064 | 120.1419 | 120.113 | 120.3279 | 120.0682 | -2.2878 | 120.0506 | 120.2042 | 120.2074 | 120.113 | -2.3797
6013.8906 | 122.4152 | -119.9799 | 2.3071 | -0.010149 | -0.071478 | 0.037302 | 0.013913 | -0.015924 | 0.0079525 | -0.021518 | -0.021494 | -0.0082729 | 0.02194 | 0.057781 | -0.00081186 | -0.021844 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.29306 | -0.11342 | 0.074307 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.168 | -0.1962 | 119.8664 | -2.1955 | 119.958 | 119.9714 | 0.10502 | -2.2198 | -2.0141 | 119.7837 | -2.2913 | 120.0542 | 119.9464 | 0.16274 | -2.1378 | -2.1391 | 120.0915 | 120.0672 | 120.2729 | 120.0133 | -2.4206 | 119.9957 | 120.1492 | 120.1479 | 120.0626 | -2.5033
6015.6406 | 122.438 | -119.8059 | 2.3895 | -0.025411 | -0.071692 | 0.037516 | 0.013699 | -0.016138 | 0.0085935 | -0.029148 | -0.021708 | -0.0082729 | 0.02194 | 0.057568 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.073622 | 0.29764 | -0.10885 | 0.074307 | 0.082776 | -0.033458 | 0.020409 | 0.1648 | 0.17258 | -0.20078 | 119.6971 | -2.2779 | 119.7886 | 119.7975 | 0.10044 | -2.3159 | -2.0919 | 119.6051 | -2.3691 | 119.8802 | 119.7725 | 0.16732 | -2.2247 | -2.2169 | 119.9176 | 119.8795 | 120.1035 | 119.8394 | -2.4984 | 119.8263 | 119.9707 | 119.9785 | 119.8887 | -2.5903
6017.3438 | 122.438 | -119.9432 | 2.3346 | -0.01778 | -0.071692 | 0.037516 | 0.013486 | -0.016352 | 0.0085935 | -0.013887 | -0.02128 | -0.0087001 | 0.021726 | 0.057995 | -0.0014529 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.091937 | 0.29764 | -0.10427 | 0.078886 | 0.082776 | -0.028879 | 0.015831 | 0.16022 | 0.17716 | -0.19162 | 119.839 | -2.2275 | 119.926 | 119.9348 | 0.095859 | -2.2427 | -2.037 | 119.7516 | -2.3188 | 120.0221 | 119.9144 | 0.16274 | -2.1744 | -2.1574 | 120.0503 | 120.0352 | 120.2409 | 119.9767 | -2.4389 | 119.9591 | 120.1035 | 120.1204 | 120.026 | -2.5262
6019.0781 | 122.5571 | -119.9112 | 2.3026 | -0.01778 | -0.071692 | 0.037302 | 0.013486 | -0.016352 | 0.0083799 | -0.021518 | -0.02128 | -0.0084865 | 0.021726 | 0.057781 | -0.0012393 | -0.021844 | 0.038035 | -0.012988 | 0.11165 | 0.078201 | 0.29764 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.020409 | 0.17396 | 0.18174 | -0.1962 | 119.8023 | -2.1909 | 119.8893 | 119.8982 | 0.095859 | -2.2243 | -2.0049 | 119.715 | -2.2821 | 119.9901 | 119.8777 | 0.16274 | -2.1286 | -2.1208 | 120.0228 | 119.9894 | 120.2088 | 119.9492 | -2.4114 | 119.9316 | 120.0852 | 120.0929 | 119.9894 | -2.4988
6020.7812 | 122.525 | -119.8791 | 2.3712 | -0.01778 | -0.071692 | 0.037088 | 0.013699 | -0.015924 | 0.0083799 | -0.021518 | -0.02128 | -0.0080591 | 0.02194 | 0.057781 | -0.0014529 | -0.021844 | 0.033457 | -0.003831 | 0.11165 | 0.08278 | 0.28848 | -0.11342 | 0.074307 | 0.087354 | -0.033458 | 0.020409 | 0.16938 | 0.17258 | -0.19162 | 119.7657 | -2.2596 | 119.8573 | 119.8753 | 0.10959 | -2.2884 | -2.0827 | 119.6875 | -2.3508 | 119.9535 | 119.8457 | 0.15816 | -2.2018 | -2.1986 | 119.9908 | 119.9619 | 120.1676 | 119.9126 | -2.4846 | 119.8996 | 120.0485 | 120.0517 | 119.9665 | -2.5628
6022.4844 | 122.406 | -119.8151 | 2.4857 | -0.010149 | -0.071478 | 0.037302 | 0.013699 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0082729 | 0.02194 | 0.057568 | -0.0012393 | -0.008109 | 0.028878 | -0.008409 | 0.11622 | 0.096516 | 0.29764 | -0.118 | 0.074307 | 0.082776 | -0.028879 | 0.024988 | 0.1648 | 0.168 | -0.1962 | 119.6971 | -2.3694 | 119.807 | 119.8067 | 0.10959 | -2.3891 | -2.188 | 119.6189 | -2.4607 | 119.8894 | 119.7862 | 0.16732 | -2.3209 | -2.3177 | 119.9313 | 119.9116 | 120.1127 | 119.8439 | -2.6037 | 119.8401 | 119.9799 | 119.9831 | 119.8978 | -2.6819
6024.2188 | 122.4472 | -120.1401 | 2.1103 | -0.025411 | -0.071478 | 0.037088 | 0.013699 | -0.015924 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.02194 | 0.057781 | -0.0014529 | -0.021844 | 0.038035 | -0.012988 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.015831 | 0.16938 | 0.16342 | -0.1962 | 120.0312 | -1.9986 | 120.1182 | 120.1271 | 0.095859 | -2.0229 | -1.8127 | 119.9439 | -2.0945 | 120.219 | 120.1066 | 0.16274 | -1.9409 | -1.9469 | 120.2517 | 120.2274 | 120.4377 | 120.1781 | -2.2191 | 120.1559 | 120.3095 | 120.3035 | 120.2274 | -2.3065
6025.9219 | 122.5067 | -119.9295 | 2.2751 | -0.010149 | -0.071692 | 0.037302 | 0.013699 | -0.016352 | 0.0085935 | -0.029148 | -0.02128 | -0.0082729 | 0.021726 | 0.057568 | -0.0012393 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.011252 | 0.16938 | 0.17258 | -0.20078 | 119.8207 | -2.168 | 119.9122 | 119.9257 | 0.10502 | -2.1877 | -1.9774 | 119.7287 | -2.2638 | 120.0084 | 119.896 | 0.16732 | -2.1057 | -2.1025 | 120.0366 | 120.0169 | 120.2271 | 119.963 | -2.3839 | 119.9408 | 120.0989 | 120.1021 | 120.0123 | -2.4759
6027.625 | 122.5159 | -119.7784 | 2.449 | -0.010149 | -0.071905 | 0.037302 | 0.013913 | -0.015711 | 0.0085935 | -0.021518 | -0.02128 | -0.0084865 | 0.021726 | 0.057995 | -0.0012393 | -0.012688 | 0.038035 | 0.000747 | 0.11622 | 0.096516 | 0.29306 | -0.10427 | 0.074307 | 0.082776 | -0.038036 | 0.015831 | 0.16938 | 0.168 | -0.1962 | 119.6742 | -2.3328 | 119.7658 | 119.7792 | 0.10501 | -2.3525 | -2.156 | 119.5822 | -2.4332 | 119.8527 | 119.7404 | 0.15816 | -2.2797 | -2.281 | 119.8947 | 119.875 | 120.0715 | 119.8165 | -2.5533 | 119.7943 | 119.9478 | 119.9464 | 119.8612 | -2.6452
6029.3438 | 122.3969 | -119.6548 | 2.6505 | -0.010149 | -0.072119 | 0.037088 | 0.013699 | -0.015924 | 0.0081663 | -0.021518 | -0.021494 | -0.0082729 | 0.02194 | 0.057781 | -0.0016665 | -0.026423 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.29764 | -0.10427 | 0.078886 | 0.082776 | -0.033458 | 0.020409 | 0.16938 | 0.168 | -0.20078 | 119.5506 | -2.5342 | 119.6284 | 119.6464 | 0.095859 | -2.5585 | -2.3528 | 119.4541 | -2.63 | 119.7337 | 119.6214 | 0.16732 | -2.4811 | -2.4825 | 119.7711 | 119.7468 | 119.9525 | 119.6883 | -2.7547 | 119.6753 | 119.8242 | 119.8228 | 119.7376 | -2.8512
6031.0781 | 122.4335 | -119.5633 | 2.7191 | -0.010149 | -0.071478 | 0.037088 | 0.013699 | -0.015924 | 0.0081663 | -0.013887 | -0.02128 | -0.0078455 | 0.02194 | 0.057568 | -0.0012393 | -0.012688 | 0.038035 | -0.008409 | 0.10707 | 0.096516 | 0.29306 | -0.10427 | 0.083464 | 0.082776 | -0.038036 | 0.020409 | 0.16938 | 0.17716 | -0.1962 | 119.459 | -2.612 | 119.5506 | 119.5549 | 0.095859 | -2.6226 | -2.4261 | 119.3671 | -2.6987 | 119.6468 | 119.5253 | 0.15816 | -2.5497 | -2.542 | 119.6704 | 119.6598 | 119.8564 | 119.6013 | -2.8234 | 119.5837 | 119.7327 | 119.7405 | 119.6461 | -2.9153
6032.7969 | 122.3831 | -119.4168 | 2.8931 | -0.010149 | -0.071905 | 0.037302 | 0.013486 | -0.015924 | 0.0083799 | -0.021518 | -0.021067 | -0.0082729 | 0.021726 | 0.057995 | -0.0012393 | -0.012688 | 0.033457 | -0.003831 | 0.11165 | 0.087359 | 0.29306 | -0.118 | 0.074307 | 0.087354 | -0.033458 | 0.011252 | 0.16938 | 0.17258 | -0.19162 | 119.2988 | -2.7814 | 119.4041 | 119.413 | 0.11417 | -2.8057 | -2.6 | 119.2252 | -2.8818 | 119.4911 | 119.3834 | 0.15816 | -2.7237 | -2.7205 | 119.5285 | 119.5042 | 119.7099 | 119.4503 | -3.0111 | 119.4281 | 119.5862 | 119.5894 | 119.5042 | -3.0847
6034.5625 | 122.4197 | -120.3781 | 1.9135 | -0.01778 | -0.071264 | 0.036874 | 0.013913 | -0.016138 | 0.0088073 | -0.029148 | -0.02128 | -0.0082729 | 0.022153 | 0.057568 | -0.0012393 | -0.012688 | 0.038035 | -0.003831 | 0.11165 | 0.091937 | 0.29764 | -0.10885 | 0.083464 | 0.078197 | -0.033458 | 0.020409 | 0.17854 | 0.168 | -0.19162 | 120.2693 | -1.8018 | 120.3654 | 120.3743 | 0.10502 | -1.8215 | -1.6158 | 120.1865 | -1.893 | 120.4616 | 120.3447 | 0.15816 | -1.7349 | -1.7454 | 120.4898 | 120.4701 | 120.6758 | 120.4161 | -2.0223 | 120.3985 | 120.5566 | 120.5461 | 120.4563 | -2.1051
6036.2656 | 122.493 | -120.2408 | 2.0142 | -0.033042 | -0.071692 | 0.037302 | 0.013699 | -0.016138 | 0.0085935 | -0.036779 | -0.021494 | -0.0082729 | 0.02194 | 0.057781 | -0.0014529 | -0.021844 | 0.038035 | 0.000747 | 0.10707 | 0.091937 | 0.29764 | -0.10885 | 0.069728 | 0.082776 | -0.033458 | 0.029566 | 0.1648 | 0.168 | -0.1962 | 120.1319 | -1.9071 | 120.2189 | 120.2415 | 0.10959 | -1.9222 | -1.7165 | 120.0446 | -1.9846 | 120.3105 | 120.2073 | 0.16274 | -1.8494 | -1.8462 | 120.3479 | 120.3327 | 120.5384 | 120.2788 | -2.123 | 120.2704 | 120.4056 | 120.4088 | 120.3236 | -2.2104
6037.9688 | 122.4518 | -120.2591 | 2.0325 | -0.01778 | -0.071905 | 0.037088 | 0.013486 | -0.016352 | 0.0085935 | -0.021518 | -0.021708 | -0.0080591 | 0.02194 | 0.057568 | -0.0014529 | -0.012688 | 0.028878 | -0.008409 | 0.11165 | 0.091937 | 0.29764 | -0.118 | 0.083464 | 0.082776 | -0.038036 | 0.020409 | 0.1648 | 0.17258 | -0.19162 | 120.1411 | -1.9208 | 120.2464 | 120.2507 | 0.10959 | -1.9405 | -1.7348 | 120.0675 | -2.0121 | 120.3426 | 120.2211 | 0.15359 | -1.8677 | -1.8599 | 120.3707 | 120.351 | 120.5567 | 120.288 | -2.1505 | 120.2795 | 120.4239 | 120.4317 | 120.3419 | -2.2241
6039.7031 | 122.4335 | -120.2728 | 2.0325 | -0.01778 | -0.071692 | 0.037302 | 0.014127 | -0.015924 | 0.0083799 | -0.0062567 | -0.02128 | -0.0084865 | 0.021726 | 0.057781 | -0.0014529 | -0.012688 | 0.038035 | -0.003831 | 0.11165 | 0.091937 | 0.29764 | -0.11342 | 0.083464 | 0.078197 | -0.033458 | 0.024988 | 0.1648 | 0.168 | -0.19162 | 120.1594 | -1.9208 | 120.2601 | 120.269 | 0.10959 | -1.9405 | -1.7348 | 120.0812 | -2.0075 | 120.3563 | 120.2394 | 0.15816 | -1.8677 | -1.8645 | 120.3845 | 120.3648 | 120.5705 | 120.3109 | -2.1459 | 120.2978 | 120.4376 | 120.4408 | 120.351 | -2.2241
6041.4062 | 122.4976 | -120.108 | 2.1378 | -0.01778 | -0.071905 | 0.036874 | 0.013913 | -0.015711 | 0.0085935 | -0.029148 | -0.021067 | -0.0084865 | 0.021726 | 0.057995 | -0.0012393 | -0.012688 | 0.038035 | -0.003831 | 0.1208 | 0.087359 | 0.29306 | -0.10885 | 0.083464 | 0.082776 | -0.028879 | 0.015831 | 0.16938 | 0.16342 | -0.19162 | 119.9992 | -2.017 | 120.0953 | 120.1042 | 0.10502 | -2.0504 | -1.8447 | 119.9164 | -2.1219 | 120.1915 | 120.0792 | 0.16274 | -1.9684 | -1.9743 | 120.2288 | 120.1954 | 120.4011 | 120.1461 | -2.2466 | 120.1239 | 120.2774 | 120.2715 | 120.1908 | -2.3294
6043.1406 | 122.438 | -120.108 | 2.179 | -0.010149 | -0.071905 | 0.037516 | 0.013486 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0082729 | 0.021512 | 0.057781 | -0.00081186 | -0.012688 | 0.028878 | -0.003831 | 0.11165 | 0.087359 | 0.29306 | -0.10885 | 0.078886 | 0.078197 | -0.028879 | 0.020409 | 0.16938 | 0.17258 | -0.20078 | 119.9992 | -2.0673 | 120.0953 | 120.1042 | 0.10502 | -2.0916 | -1.8859 | 119.9073 | -2.1585 | 120.1869 | 120.0792 | 0.1719 | -2.0096 | -2.0064 | 120.2197 | 120.1954 | 120.4011 | 120.1369 | -2.2878 | 120.1284 | 120.2774 | 120.2806 | 120.1862 | -2.3797
6044.8438 | 122.4609 | -119.9707 | 2.3254 | -0.0025182 | -0.071692 | 0.037516 | 0.013486 | -0.016138 | 0.0085935 | -0.021518 | -0.02128 | -0.0080591 | 0.021512 | 0.057781 | -0.0014529 | -0.008109 | 0.0243 | -0.012988 | 0.10707 | 0.087359 | 0.29306 | -0.10885 | 0.092622 | 0.082776 | -0.033458 | 0.020409 | 0.16938 | 0.17258 | -0.19162 | 119.8619 | -2.2184 | 119.9626 | 119.9577 | 0.095859 | -2.2381 | -2.0324 | 119.7791 | -2.305 | 120.0633 | 119.9372 | 0.15816 | -2.1561 | -2.1529 | 120.0778 | 120.0581 | 120.2638 | 119.995 | -2.4343 | 119.9911 | 120.1401 | 120.1433 | 120.0535 | -2.5171
6046.5469 | 122.5571 | -119.9158 | 2.33 | -0.010149 | -0.071905 | 0.037729 | 0.013486 | -0.015711 | 0.0085935 | -0.021518 | -0.02128 | -0.0082729 | 0.021726 | 0.057995 | -0.0012393 | -0.012688 | 0.033457 | -0.008409 | 0.10249 | 0.087359 | 0.29764 | -0.10885 | 0.083464 | 0.087354 | -0.033458 | 0.024988 | 0.1648 | 0.168 | -0.1962 | 119.8069 | -2.2275 | 119.9031 | 119.9074 | 0.10044 | -2.2427 | -2.0324 | 119.7196 | -2.305 | 119.9992 | 119.8823 | 0.16274 | -2.1652 | -2.162 | 120.0183 | 120.0031 | 120.2134 | 119.9492 | -2.4389 | 119.9408 | 120.0806 | 120.0838 | 120.0031 | -2.5262
6048.2656 | 122.5662 | -119.7601 | 2.4902 | -0.010149 | -0.071692 | 0.037516 | 0.013699 | -0.015924 | 0.0083799 | -0.029148 | -0.021494 | -0.0082729 | 0.021726 | 0.057781 | -0.0014529 | -0.017266 | 0.028878 | -0.008409 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.028879 | 0.015831 | 0.17396 | 0.17716 | -0.1962 | 119.6513 | -2.3786 | 119.7429 | 119.7517 | 0.10044 | -2.4029 | -2.1926 | 119.5639 | -2.4744 | 119.839 | 119.7313 | 0.16732 | -2.3163 | -2.3131 | 119.8718 | 119.8475 | 120.0578 | 119.789 | -2.5991 | 119.776 | 119.9341 | 119.9373 | 119.8475 | -2.6864
6049.9688 | 122.4243 | -120.2225 | 2.0828 | -0.010149 | -0.071905 | 0.037302 | 0.013913 | -0.016352 | 0.0081663 | -0.021518 | -0.021494 | -0.0082729 | 0.021299 | 0.057995 | -0.0014529 | -0.017266 | 0.033457 | 0.000747 | 0.11165 | 0.08278 | 0.29306 | -0.11342 | 0.074307 | 0.082776 | -0.033458 | 0.015831 | 0.17396 | 0.17258 | -0.1962 | 120.109 | -1.9712 | 120.2052 | 120.2232 | 0.11417 | -2 | -1.7898 | 120.0263 | -2.067 | 120.2968 | 120.189 | 0.16274 | -1.9089 | -1.9102 | 120.3341 | 120.3053 | 120.5155 | 120.2559 | -2.1963 | 120.2383 | 120.3964 | 120.3951 | 120.3052 | -2.279
6051.6719 | 122.4518 | -120.076 | 2.2339 | -0.010149 | -0.071692 | 0.037302 | 0.013913 | -0.016138 | 0.0083799 | -0.029148 | -0.02128 | -0.0082729 | 0.02194 | 0.057781 | -0.0010255 | -0.026423 | 0.028878 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.083464 | 0.082776 | -0.042615 | 0.024988 | 0.16938 | 0.17716 | -0.19162 | 119.9671 | -2.1222 | 120.0496 | 120.0722 | 0.10502 | -2.1465 | -1.9362 | 119.8844 | -2.2089 | 120.1595 | 120.0334 | 0.14901 | -2.0645 | -2.0567 | 120.1876 | 120.1633 | 120.3736 | 120.1049 | -2.3427 | 120.101 | 120.2454 | 120.2531 | 120.1588 | -2.4255
6053.3906 | 122.4472 | -119.8837 | 2.3849 | -0.01778 | -0.071692 | 0.037516 | 0.013699 | -0.015711 | 0.0081663 | -0.021518 | -0.02128 | -0.0080591 | 0.02194 | 0.057781 | -0.0012393 | -0.017266 | 0.028878 | -0.008409 | 0.11622 | 0.091937 | 0.29764 | -0.10427 | 0.083464 | 0.082776 | -0.038036 | 0.024988 | 0.17396 | 0.17258 | -0.20536 | 119.7795 | -2.2687 | 119.8665 | 119.8753 | 0.095859 | -2.293 | -2.0873 | 119.6784 | -2.36 | 119.9672 | 119.8457 | 0.16732 | -2.211 | -2.2124 | 120 | 119.9757 | 120.1814 | 119.9126 | -2.4892 | 119.9087 | 120.0577 | 120.0563 | 119.9665 | -2.5903
6055.0938 | 122.4289 | -119.9387 | 2.3804 | -0.0025182 | -0.071905 | 0.037088 | 0.013913 | -0.016138 | 0.0088073 | -0.013887 | -0.02128 | -0.0084865 | 0.02194 | 0.058209 | -0.0012393 | -0.012688 | 0.033457 | -0.003831 | 0.11622 | 0.08278 | 0.29306 | -0.10885 | 0.074307 | 0.087354 | -0.033458 | 0.015831 | 0.1648 | 0.168 | -0.20078 | 119.8298 | -2.2641 | 119.926 | 119.9348 | 0.10502 | -2.2976 | -2.0873 | 119.7379 | -2.3645 | 120.013 | 119.9052 | 0.16732 | -2.2156 | -2.2124 | 120.0549 | 120.0214 | 120.2317 | 119.9721 | -2.4892 | 119.9545 | 120.1035 | 120.1067 | 120.026 | -2.5811
6056.8125 | 122.5754 | -119.6045 | 2.6276 | -0.010149 | -0.071905 | 0.037088 | 0.013913 | -0.015924 | 0.0083799 | -0.029148 | -0.02128 | -0.0082729 | 0.021726 | 0.057781 | -0.0014529 | -0.026423 | 0.033457 | 0.000747 | 0.11165 | 0.087359 | 0.3068 | -0.11342 | 0.069728 | 0.082776 | -0.038036 | 0.020409 | 0.16938 | 0.168 | -0.1962 | 119.4911 | -2.5159 | 119.5781 | 119.6052 | 0.11417 | -2.5402 | -2.3208 | 119.4083 | -2.6072 | 119.6742 | 119.5665 | 0.15816 | -2.4582 | -2.4596 | 119.7161 | 119.6919 | 119.9113 | 119.6379 | -2.741 | 119.6249 | 119.7739 | 119.7725 | 119.6873 | -2.8238
6058.5781 | 122.4197 | -119.5862 | 2.7649 | -0.01778 | -0.071692 | 0.037516 | 0.013699 | -0.015711 | 0.0088073 | -0.021518 | -0.021494 | -0.0080591 | 0.02194 | 0.057781 | -0.0012393 | -0.021844 | 0.028878 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.020409 | 0.17396 | 0.168 | -0.19162 | 119.4773 | -2.6532 | 119.5643 | 119.5824 | 0.10502 | -2.6775 | -2.4627 | 119.3946 | -2.7445 | 119.6651 | 119.5527 | 0.15816 | -2.5909 | -2.5969 | 119.6978 | 119.6735 | 119.8884 | 119.6151 | -2.8737 | 119.6066 | 119.7601 | 119.7542 | 119.6644 | -2.9565
6060.2812 | 122.493 | -119.3069 | 2.9388 | -0.01778 | -0.071478 | 0.037516 | 0.013913 | -0.015711 | 0.0085935 | 0.0013733 | -0.02128 | -0.0080591 | 0.02194 | 0.057568 | -0.0010255 | -0.012688 | 0.028878 | -0.008409 | 0.11622 | 0.078201 | 0.30222 | -0.099689 | 0.083464 | 0.082776 | -0.028879 | 0.020409 | 0.16022 | 0.17716 | -0.1962 | 119.2073 | -2.8226 | 119.2943 | 119.2985 | 0.09128 | -2.8606 | -2.6366 | 119.1107 | -2.9184 | 119.3904 | 119.2781 | 0.16732 | -2.7786 | -2.7617 | 119.4232 | 119.3851 | 119.6092 | 119.3358 | -3.0385 | 119.3274 | 119.4672 | 119.4841 | 119.3897 | -3.135
6062 | 122.5067 | -119.8105 | 2.449 | -0.01778 | -0.071905 | 0.037302 | 0.013913 | -0.015924 | 0.0085935 | -0.036779 | -0.02128 | -0.0082729 | 0.02194 | 0.057995 | -0.0010255 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | -0.10427 | 0.074307 | 0.082776 | -0.033458 | 0.015831 | 0.1648 | 0.168 | -0.1962 | 119.7062 | -2.3374 | 119.7932 | 119.8067 | 0.10044 | -2.3617 | -2.1468 | 119.6143 | -2.4332 | 119.8848 | 119.777 | 0.16274 | -2.2842 | -2.281 | 119.9221 | 119.8978 | 120.1127 | 119.8439 | -2.5533 | 119.8263 | 119.9753 | 119.9785 | 119.8933 | -2.6452
6063.6875 | 122.4243 | -119.6915 | 2.623 | -0.010149 | -0.071692 | 0.036661 | 0.013486 | -0.016352 | 0.0085935 | -0.036779 | -0.02128 | -0.0084865 | 0.02194 | 0.057995 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.29764 | -0.118 | 0.083464 | 0.082776 | -0.033458 | 0.015831 | 0.16022 | 0.17258 | -0.1962 | 119.5735 | -2.5113 | 119.6742 | 119.6831 | 0.10959 | -2.5356 | -2.3253 | 119.4953 | -2.6072 | 119.7749 | 119.658 | 0.16274 | -2.4628 | -2.4504 | 119.8031 | 119.7788 | 119.9891 | 119.7249 | -2.741 | 119.7073 | 119.8517 | 119.864 | 119.7742 | -2.8192
6065.3906 | 122.5204 | -119.8196 | 2.4719 | -0.025411 | -0.071692 | 0.037302 | 0.013486 | -0.015924 | 0.0083799 | -0.021518 | -0.021494 | -0.0084865 | 0.021726 | 0.057995 | -0.0014529 | -0.017266 | 0.028878 | -0.003831 | 0.10707 | 0.08278 | 0.28848 | -0.10427 | 0.078886 | 0.091933 | -0.028879 | 0.020409 | 0.17396 | 0.17258 | -0.1962 | 119.7154 | -2.3649 | 119.8024 | 119.8158 | 0.10044 | -2.3891 | -2.1834 | 119.6234 | -2.4515 | 119.8985 | 119.7908 | 0.16732 | -2.298 | -2.2993 | 119.9267 | 119.9024 | 120.1081 | 119.8485 | -2.5762 | 119.8401 | 119.9936 | 119.9922 | 119.9116 | -2.6681
6067.0938 | 122.4472 | -119.5038 | 2.7969 | -0.01778 | -0.071692 | 0.037516 | 0.013486 | -0.015924 | 0.0083799 | -0.013887 | -0.02128 | -0.0080591 | 0.02194 | 0.057995 | -0.0014529 | -0.021844 | 0.033457 | -0.012988 | 0.11622 | 0.091937 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.16022 | 0.168 | -0.20078 | 119.3949 | -2.6807 | 119.4819 | 119.4908 | 0.095859 | -2.705 | -2.4993 | 119.303 | -2.7765 | 119.5827 | 119.4703 | 0.16732 | -2.6367 | -2.6289 | 119.62 | 119.5957 | 119.8014 | 119.5372 | -2.9058 | 119.5242 | 119.664 | 119.6718 | 119.5911 | -2.9977
6068.7969 | 122.4518 | -119.8563 | 2.4399 | -0.01778 | -0.071692 | 0.037302 | 0.013699 | -0.015924 | 0.0088073 | -0.021518 | -0.021494 | -0.0082729 | 0.021726 | 0.057781 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.29306 | -0.10885 | 0.078886 | 0.091933 | -0.033458 | 0.020409 | 0.16938 | 0.17258 | -0.18704 | 119.7474 | -2.3282 | 119.839 | 119.8479 | 0.10044 | -2.3525 | -2.1468 | 119.6692 | -2.4195 | 119.9351 | 119.8228 | 0.15358 | -2.2705 | -2.2673 | 119.9679 | 119.9436 | 120.1493 | 119.8897 | -2.5487 | 119.8767 | 120.0256 | 120.0288 | 119.9482 | -2.6269
6070.5625 | 122.5113 | -119.4672 | 2.8152 | -0.010149 | -0.072119 | 0.037516 | 0.013699 | -0.016138 | 0.0085935 | -0.021518 | -0.021494 | -0.0082729 | 0.02194 | 0.057995 | -0.0014529 | -0.012688 | 0.028878 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.020409 | 0.1648 | 0.17716 | -0.1962 | 119.3583 | -2.7036 | 119.4545 | 119.4633 | 0.10502 | -2.7279 | -2.5176 | 119.271 | -2.7948 | 119.546 | 119.4337 | 0.16274 | -2.6504 | -2.6381 | 119.5788 | 119.5545 | 119.7648 | 119.496 | -2.9241 | 119.4876 | 119.632 | 119.6443 | 119.5454 | -3.0114
6072.2656 | 122.5159 | -119.9936 | 2.2659 | -0.01778 | -0.071692 | 0.037302 | 0.013699 | -0.015924 | 0.0085935 | -0.029148 | -0.021067 | -0.0078455 | 0.021726 | 0.057568 | -0.0012393 | -0.021844 | 0.033457 | -0.003831 | 0.11622 | 0.08278 | 0.29306 | -0.10427 | 0.078886 | 0.082776 | -0.038036 | 0.020409 | 0.16938 | 0.17716 | -0.20078 | 119.8893 | -2.1497 | 119.9717 | 119.9898 | 0.10044 | -2.1831 | -1.9729 | 119.7928 | -2.2455 | 120.0725 | 119.9556 | 0.16274 | -2.0966 | -2.0888 | 120.1098 | 120.0764 | 120.2867 | 120.027 | -2.3702 | 120.014 | 120.163 | 120.1707 | 120.0764 | -2.4667
6073.9688 | 122.5204 | -119.7739 | 2.5131 | -0.010149 | -0.071905 | 0.037516 | 0.013486 | -0.016138 | 0.0083799 | -0.029148 | -0.021494 | -0.0082729 | 0.021726 | 0.057568 | -0.0012393 | -0.017266 | 0.028878 | -0.008409 | 0.10707 | 0.08278 | 0.29306 | -0.11342 | 0.069728 | 0.091933 | -0.028879 | 0.015831 | 0.1648 | 0.17258 | -0.18704 | 119.6604 | -2.4061 | 119.7566 | 119.7655 | 0.10502 | -2.4303 | -2.2201 | 119.5868 | -2.4973 | 119.8436 | 119.745 | 0.15816 | -2.3483 | -2.3405 | 119.8809 | 119.8566 | 120.0669 | 119.8027 | -2.6265 | 119.7897 | 119.9387 | 119.9464 | 119.8658 | -2.7002
6075.6719 | 122.493 | -119.6045 | 2.7191 | -0.0025182 | -0.071692 | 0.037302 | 0.013699 | -0.016138 | 0.0083799 | -0.029148 | -0.021494 | -0.0084865 | 0.021512 | 0.057781 | -0.0014529 | -0.017266 | 0.0243 | -0.008409 | 0.11165 | 0.08278 | 0.30222 | -0.118 | 0.083464 | 0.087354 | -0.033458 | 0.020409 | 0.1648 | 0.17716 | -0.18704 | 119.4865 | -2.6075 | 119.5872 | 119.5961 | 0.10959 | -2.6363 | -2.4169 | 119.4174 | -2.6987 | 119.688 | 119.571 | 0.15358 | -2.5543 | -2.542 | 119.7161 | 119.6873 | 119.9067 | 119.6288 | -2.8371 | 119.6249 | 119.7693 | 119.7817 | 119.6918 | -2.9062
6077.3906 | 122.493 | -119.4855 | 2.8152 | 0.0051128 | -0.072333 | 0.037302 | 0.013913 | -0.016138 | 0.0088073 | -0.029148 | -0.021708 | -0.0082729 | 0.02194 | 0.058209 | -0.0012393 | -0.012688 | 0.038035 | -0.003831 | 0.11622 | 0.087359 | 0.29306 | -0.10427 | 0.078886 | 0.082776 | -0.028879 | 0.020409 | 0.16938 | 0.17258 | -0.19162 | 119.3812 | -2.699 | 119.4728 | 119.4816 | 0.10044 | -2.7279 | -2.5222 | 119.2939 | -2.7948 | 119.5644 | 119.4566 | 0.16274 | -2.6459 | -2.6427 | 119.6017 | 119.5728 | 119.7785 | 119.5235 | -2.9195 | 119.5059 | 119.6549 | 119.6581 | 119.5682 | -3.0069
6079.1094 | 122.4243 | -119.8425 | 2.4948 | -0.010149 | -0.071905 | 0.037302 | 0.013699 | -0.015924 | 0.0083799 | -0.021518 | -0.021494 | -0.0082729 | 0.021726 | 0.057995 | -0.0012393 | -0.017266 | 0.028878 | -0.003831 | 0.1208 | 0.087359 | 0.29306 | -0.10427 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.16938 | 0.168 | -0.20078 | 119.7383 | -2.374 | 119.8253 | 119.8387 | 0.10044 | -2.4075 | -2.2018 | 119.6418 | -2.4744 | 119.9214 | 119.8091 | 0.16732 | -2.3254 | -2.3268 | 119.9633 | 119.9299 | 120.1356 | 119.8714 | -2.5991 | 119.8629 | 120.0119 | 120.0105 | 119.9299 | -2.6956
6080.8125 | 122.438 | -120.369 | 1.9958 | -0.0025182 | -0.071905 | 0.037088 | 0.013486 | -0.016138 | 0.0083799 | -0.013887 | -0.021494 | -0.0080591 | 0.02194 | 0.057995 | -0.0014529 | -0.017266 | 0.033457 | -0.008409 | 0.10707 | 0.08278 | 0.30222 | -0.099689 | 0.074307 | 0.082776 | -0.033458 | 0.020409 | 0.16938 | 0.17258 | -0.1962 | 120.2693 | -1.8888 | 120.3517 | 120.3605 | 0.09128 | -1.9131 | -1.6936 | 120.1728 | -1.9754 | 120.4433 | 120.3355 | 0.16274 | -1.8265 | -1.8233 | 120.476 | 120.4517 | 120.6712 | 120.4024 | -2.0955 | 120.3894 | 120.5383 | 120.5415 | 120.4517 | -2.1921
6082.5156 | 122.5525 | -119.751 | 2.5223 | -0.01778 | -0.071692 | 0.037302 | 0.013699 | -0.015924 | 0.0085935 | -0.021518 | -0.021494 | -0.0080591 | 0.02194 | 0.057995 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.091937 | 0.30222 | -0.10885 | 0.083464 | 0.078197 | -0.033458 | 0.020409 | 0.1648 | 0.17258 | -0.18704 | 119.6421 | -2.4106 | 119.7337 | 119.7426 | 0.10044 | -2.4303 | -2.2201 | 119.5639 | -2.5019 | 119.8344 | 119.7175 | 0.15358 | -2.3575 | -2.3497 | 119.8626 | 119.8429 | 120.0532 | 119.7844 | -2.6311 | 119.7714 | 119.9158 | 119.9236 | 119.8292 | -2.7093
6084.2188 | 122.4472 | -119.8563 | 2.4948 | -0.010149 | -0.071692 | 0.037088 | 0.013699 | -0.015924 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.02194 | 0.057995 | -0.0010255 | -0.012688 | 0.033457 | -0.012988 | 0.11165 | 0.091937 | 0.29306 | -0.10885 | 0.083464 | 0.087354 | -0.038036 | 0.020409 | 0.1648 | 0.17258 | -0.1962 | 119.7474 | -2.3832 | 119.8436 | 119.8433 | 0.095859 | -2.4029 | -2.2018 | 119.6601 | -2.4744 | 119.9397 | 119.8182 | 0.15816 | -2.33 | -2.3222 | 119.9679 | 119.9482 | 120.1493 | 119.8897 | -2.6037 | 119.8767 | 120.0211 | 120.0288 | 119.9436 | -2.691
6085.9375 | 122.4655 | -119.8471 | 2.4994 | -0.0025182 | -0.071692 | 0.037302 | 0.013699 | -0.016138 | 0.0085935 | -0.013887 | -0.02128 | -0.0080591 | 0.021726 | 0.057995 | -0.0014529 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.29306 | -0.11342 | 0.078886 | 0.082776 | -0.028879 | 0.015831 | 0.1648 | 0.16342 | -0.19162 | 119.7337 | -2.3877 | 119.8298 | 119.8387 | 0.10502 | -2.412 | -2.2063 | 119.6555 | -2.4836 | 119.926 | 119.8182 | 0.16274 | -2.3346 | -2.336 | 119.9588 | 119.9345 | 120.1402 | 119.8806 | -2.6128 | 119.8629 | 120.0119 | 120.0105 | 119.9299 | -2.691
6087.6562 | 122.5662 | -119.6869 | 2.536 | -0.010149 | -0.071905 | 0.037088 | 0.013699 | -0.015924 | 0.0083799 | -0.029148 | -0.021708 | -0.0082729 | 0.02194 | 0.057781 | -0.0012393 | -0.017266 | 0.028878 | 0.005325 | 0.10707 | 0.08278 | 0.29306 | -0.11342 | 0.083464 | 0.087354 | -0.033458 | 0.020409 | 0.16938 | 0.17716 | -0.20078 | 119.5735 | -2.4289 | 119.6696 | 119.6922 | 0.11875 | -2.4532 | -2.243 | 119.4861 | -2.5156 | 119.7704 | 119.6534 | 0.16732 | -2.3666 | -2.3589 | 119.794 | 119.7697 | 119.98 | 119.7158 | -2.6494 | 119.7073 | 119.8563 | 119.864 | 119.7742 | -2.7368
6089.3594 | 122.5708 | -119.6732 | 2.5955 | -0.01778 | -0.071692 | 0.037302 | 0.013699 | -0.016138 | 0.0088073 | -0.013887 | -0.02128 | -0.0087001 | 0.021726 | 0.057781 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.08278 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.047194 | 0.015831 | 0.16022 | 0.17258 | -0.19162 | 119.5643 | -2.4839 | 119.6559 | 119.6647 | 0.10044 | -2.5127 | -2.2979 | 119.4815 | -2.5797 | 119.752 | 119.626 | 0.14443 | -2.4353 | -2.4229 | 119.7848 | 119.7559 | 119.9708 | 119.7066 | -2.7044 | 119.689 | 119.8334 | 119.8457 | 119.7605 | -2.7871
6091.0625 | 122.5616 | -119.3985 | 2.8427 | -0.0025182 | -0.071905 | 0.037516 | 0.013699 | -0.015711 | 0.0083799 | -0.029148 | -0.021494 | -0.0082729 | 0.02194 | 0.058209 | -0.0014529 | -0.026423 | 0.033457 | -0.003831 | 0.11165 | 0.08278 | 0.30222 | -0.10885 | 0.074307 | 0.087354 | -0.033458 | 0.011252 | 0.1648 | 0.17258 | -0.20078 | 119.2897 | -2.7311 | 119.3721 | 119.3947 | 0.10502 | -2.7599 | -2.5405 | 119.1977 | -2.8315 | 119.4728 | 119.365 | 0.16732 | -2.6779 | -2.6701 | 119.5101 | 119.4813 | 119.7007 | 119.432 | -2.9516 | 119.4098 | 119.5633 | 119.5711 | 119.4859 | -3.0435
6092.7656 | 122.5067 | -119.8013 | 2.4948 | -0.010149 | -0.071905 | 0.037516 | 0.013486 | -0.016138 | 0.0085935 | -0.029148 | -0.021708 | -0.0082729 | 0.021512 | 0.057781 | -0.0016665 | -0.017266 | 0.033457 | -0.017566 | 0.11165 | 0.091937 | 0.29306 | -0.10885 | 0.083464 | 0.082776 | -0.038036 | 0.020409 | 0.1648 | 0.17716 | -0.20078 | 119.6925 | -2.3832 | 119.7841 | 119.7838 | 0.091281 | -2.4029 | -2.2018 | 119.6006 | -2.4744 | 119.8848 | 119.7633 | 0.16274 | -2.33 | -2.3177 | 119.913 | 119.8933 | 120.0944 | 119.8348 | -2.6037 | 119.8217 | 119.9661 | 119.9785 | 119.8841 | -2.6956
6094.4844 | 122.4564 | -119.7922 | 2.5589 | -0.01778 | -0.071692 | 0.036874 | 0.013699 | -0.016138 | 0.0083799 | -0.029148 | -0.02128 | -0.0080591 | 0.02194 | 0.058209 | -0.0016665 | -0.017266 | 0.038035 | -0.003831 | 0.11165 | 0.096516 | 0.29306 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.020409 | 0.1648 | 0.168 | -0.20078 | 119.6787 | -2.4473 | 119.7749 | 119.7883 | 0.10959 | -2.4624 | -2.2658 | 119.5914 | -2.5385 | 119.8711 | 119.7587 | 0.16732 | -2.3941 | -2.3909 | 119.9038 | 119.8887 | 120.0852 | 119.8302 | -2.6723 | 119.8126 | 119.957 | 119.9602 | 119.875 | -2.7597
6096.1875 | 121.8338 | -118.9362 | 2.1286 | -0.010149 | -0.071905 | 0.037088 | 0.013272 | -0.016138 | 0.0085935 | -0.0062567 | -0.021708 | -0.0080591 | 0.021726 | 0.057995 | -0.0016665 | -0.021844 | 0.028878 | -0.008409 | 0.11622 | 0.087359 | 0.3068 | -0.10427 | 0.074307 | 0.087354 | -0.033458 | 0.011252 | 0.1648 | 0.168 | -0.1962 | 118.8319 | -2.0124 | 118.9143 | 118.9277 | 0.095859 | -2.0412 | -1.8218 | 118.74 | -2.1173 | 119.0105 | 118.9027 | 0.16274 | -1.9638 | -1.9606 | 119.0524 | 119.0235 | 119.243 | 118.965 | -2.2329 | 118.9474 | 119.101 | 119.1042 | 119.0235 | -2.3248
6097.8906 | 122.0901 | -108.9157 | 12.8677 | -0.0025182 | -0.071478 | 0.037302 | 0.013913 | -0.015711 | 0.0083799 | -0.013887 | -0.02128 | -0.0080591 | 0.021512 | 0.057995 | -0.0012393 | -0.021844 | 0.028878 | -0.008409 | 0.11622 | 0.087359 | 0.29306 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.17396 | 0.168 | -0.19162 | 108.8023 | -12.7515 | 108.8939 | 108.9073 | 0.10502 | -12.7804 | -12.5747 | 108.7241 | -12.8473 | 108.9946 | 108.8823 | 0.15816 | -12.6938 | -12.6997 | 109.0319 | 109.0031 | 109.2088 | 108.9446 | -12.9812 | 108.9361 | 109.0897 | 109.0837 | 109.0031 | -13.0594
6099.6406 | 122.3145 | -120.4788 | 1.3779 | -0.01778 | -0.071905 | 0.037302 | 0.013486 | -0.015711 | 0.0085935 | -0.029148 | -0.021494 | -0.0082729 | 0.02194 | 0.057995 | -0.0010255 | -0.021844 | 0.033457 | -0.003831 | 0.11165 | 0.08278 | 0.29764 | -0.11342 | 0.078886 | 0.078197 | -0.033458 | 0.015831 | 0.16938 | 0.17258 | -0.20078 | 120.3654 | -1.2662 | 120.457 | 120.475 | 0.10959 | -1.2951 | -1.0802 | 120.278 | -1.362 | 120.5577 | 120.4454 | 0.16732 | -1.2085 | -1.2053 | 120.5905 | 120.5616 | 120.7765 | 120.5123 | -1.4913 | 120.4947 | 120.6482 | 120.6514 | 120.557 | -1.5786
6101.3438 | 122.2183 | -120.5612 | 1.4374 | -0.010149 | -0.071905 | 0.037302 | 0.013486 | -0.016138 | 0.0085935 | -0.021518 | -0.021708 | -0.0080591 | 0.021726 | 0.057781 | -0.0012393 | -0.012688 | 0.033457 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.083464 | 0.082776 | -0.033458 | 0.015831 | 0.1648 | 0.17258 | -0.1962 | 120.4524 | -1.3257 | 120.5485 | 120.5574 | 0.10502 | -1.35 | -1.1397 | 120.365 | -1.4215 | 120.6447 | 120.5278 | 0.16274 | -1.2726 | -1.2648 | 120.6729 | 120.6486 | 120.8589 | 120.5947 | -1.5462 | 120.577 | 120.726 | 120.7338 | 120.644 | -1.6336
6103.0625 | 122.2458 | -120.6345 | 1.442 | -0.010149 | -0.071905 | 0.037302 | 0.013486 | -0.016352 | 0.0085935 | -0.013887 | -0.021494 | -0.0082729 | 0.021512 | 0.057568 | -0.0014529 | -0.017266 | 0.028878 | -0.003831 | 0.12538 | 0.087359 | 0.29764 | -0.11342 | 0.069728 | 0.078197 | -0.038036 | 0.015831 | 0.1648 | 0.17258 | -0.19162 | 120.521 | -1.3166 | 120.6172 | 120.6306 | 0.10959 | -1.3546 | -1.1443 | 120.4428 | -1.4261 | 120.7042 | 120.5964 | 0.15359 | -1.2772 | -1.2694 | 120.7598 | 120.7218 | 120.9321 | 120.6633 | -1.5554 | 120.6503 | 120.7993 | 120.807 | 120.7127 | -1.6336
6104.7656 | 122.3694 | -120.6024 | 1.442 | -0.010149 | -0.071905 | 0.037088 | 0.013699 | -0.015924 | 0.0083799 | -0.036779 | -0.021494 | -0.0082729 | 0.021726 | 0.057995 | -0.0010255 | -0.026423 | 0.033457 | -0.008409 | 0.11165 | 0.091937 | 0.29306 | -0.11342 | 0.069728 | 0.082776 | -0.042615 | 0.015831 | 0.1648 | 0.17258 | -0.1962 | 120.489 | -1.3303 | 120.576 | 120.594 | 0.10502 | -1.35 | -1.1489 | 120.4062 | -1.4261 | 120.6721 | 120.5598 | 0.15359 | -1.2772 | -1.2694 | 120.7141 | 120.6944 | 120.8955 | 120.6359 | -1.5554 | 120.6182 | 120.7672 | 120.775 | 120.6852 | -1.6382
6106.5 | 122.2916 | -118.5791 | 3.5202 | -0.010149 | -0.071905 | 0.037302 | 0.013699 | -0.016138 | 0.0085935 | -0.036779 | -0.021494 | -0.0080591 | 0.021512 | 0.057781 | -0.0014529 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.091937 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.015831 | 0.16938 | 0.168 | -0.20078 | 118.4703 | -3.4131 | 118.5618 | 118.5753 | 0.10502 | -3.4283 | -3.2226 | 118.3783 | -3.5044 | 118.658 | 118.5411 | 0.16274 | -3.3508 | -3.3522 | 118.6862 | 118.671 | 118.8767 | 118.6126 | -3.629 | 118.5949 | 118.7485 | 118.7471 | 118.6619 | -3.721
6108.2031 | 122.3602 | -94.3588 | 27.5116 | -0.01778 | -0.071692 | 0.037516 | 0.013486 | -0.015924 | 0.0083799 | -0.013887 | -0.02128 | -0.0082729 | 0.02194 | 0.057995 | -0.0014529 | -0.012688 | 0.028878 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | -0.10885 | 0.074307 | 0.082776 | -0.038036 | 0.011252 | 0.16938 | 0.17258 | -0.20078 | 94.25 | -27.3999 | 94.3461 | 94.355 | 0.10502 | -27.4242 | -27.2094 | 94.158 | -27.5003 | 94.4331 | 94.3208 | 0.16274 | -27.3422 | -27.339 | 94.4705 | 94.4462 | 94.661 | 94.3877 | -27.6204 | 94.3701 | 94.5282 | 94.5314 | 94.4416 | -27.7124
6109.9219 | 122.3419 | -120.6253 | 1.4923 | -0.0025182 | -0.072119 | 0.037302 | 0.013486 | -0.016138 | 0.0083799 | -0.021518 | -0.021708 | -0.0084865 | 0.021726 | 0.058209 | -0.0010255 | -0.017266 | 0.028878 | -0.008409 | 0.1208 | 0.087359 | 0.30222 | -0.11342 | 0.078886 | 0.082776 | -0.028879 | 0.011252 | 0.15564 | 0.17258 | -0.20078 | 120.5119 | -1.3715 | 120.608 | 120.6169 | 0.10502 | -1.405 | -1.1901 | 120.4245 | -1.4811 | 120.7042 | 120.5964 | 0.1719 | -1.3367 | -1.3197 | 120.7461 | 120.7127 | 120.9275 | 120.6542 | -1.6057 | 120.6366 | 120.7809 | 120.7979 | 120.7081 | -1.6931
6111.6406 | 122.3511 | -113.7634 | 8.2535 | -0.01778 | -0.071692 | 0.037516 | 0.013486 | -0.016138 | 0.0083799 | -0.029148 | -0.02128 | -0.0082729 | 0.021512 | 0.058209 | -0.0014529 | -0.012688 | 0.028878 | -0.008409 | 0.11622 | 0.08278 | 0.29764 | -0.10885 | 0.074307 | 0.082776 | -0.028879 | 0.011252 | 0.1648 | 0.168 | -0.1962 | 113.6546 | -8.1373 | 113.7507 | 113.755 | 0.10044 | -8.1707 | -7.9558 | 113.5672 | -8.2422 | 113.8377 | 113.7345 | 0.16732 | -8.0887 | -8.0855 | 113.8797 | 113.8462 | 114.0611 | 113.7923 | -8.3623 | 113.7747 | 113.9282 | 113.9314 | 113.8462 | -8.4497
6113.3438 | 122.3465 | -120.6207 | 1.5198 | -0.010149 | -0.071905 | 0.037516 | 0.013913 | -0.015924 | 0.0088073 | -0.021518 | -0.02128 | -0.0082729 | 0.021726 | 0.057781 | -0.0012393 | -0.017266 | 0.033457 | 0.000747 | 0.11622 | 0.087359 | 0.30222 | -0.11342 | 0.078886 | 0.082776 | -0.028879 | 0.020409 | 0.17396 | 0.168 | -0.19162 | 120.5073 | -1.4036 | 120.6035 | 120.6215 | 0.11417 | -1.4324 | -1.2176 | 120.4291 | -1.4994 | 120.6996 | 120.5918 | 0.16274 | -1.3458 | -1.3518 | 120.737 | 120.7081 | 120.9229 | 120.6542 | -1.6332 | 120.6411 | 120.7947 | 120.7887 | 120.7035 | -1.7114
6115.0469 | 122.438 | -120.5933 | 1.5198 | -0.01778 | -0.071905 | 0.037516 | 0.013699 | -0.016138 | 0.0085935 | -0.029148 | -0.021494 | -0.0078455 | 0.021726 | 0.058209 | -0.0010255 | -0.017266 | 0.038035 | -0.008409 | 0.11165 | 0.091937 | 0.29764 | -0.10427 | 0.078886 | 0.078197 | -0.033458 | 0.020409 | 0.1648 | 0.17258 | -0.19162 | 120.489 | -1.4081 | 120.576 | 120.5849 | 0.095859 | -1.4278 | -1.2221 | 120.4016 | -1.4994 | 120.6721 | 120.5598 | 0.15816 | -1.355 | -1.3472 | 120.7049 | 120.6852 | 120.8909 | 120.6313 | -1.624 | 120.6137 | 120.7581 | 120.7658 | 120.6715 | -1.7114
6116.75 | 122.3877 | -120.5704 | 1.5564 | -0.010149 | -0.071692 | 0.037088 | 0.013486 | -0.015924 | 0.0085935 | -0.021518 | -0.02128 | -0.0078455 | 0.021726 | 0.057995 | -0.0016665 | -0.017266 | 0.0243 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | -0.10885 | 0.083464 | 0.087354 | -0.038036 | 0.020409 | 0.1648 | 0.17258 | -0.20078 | 120.4615 | -1.4447 | 120.5531 | 120.5665 | 0.10502 | -1.469 | -1.2542 | 120.3696 | -1.536 | 120.6538 | 120.5323 | 0.16274 | -1.3916 | -1.3838 | 120.682 | 120.6577 | 120.8726 | 120.5947 | -1.6652 | 120.5908 | 120.7352 | 120.743 | 120.6577 | -1.7572
6118.4688 | 122.406 | -120.5475 | 1.5381 | -0.010149 | -0.071478 | 0.037302 | 0.013486 | -0.016138 | 0.0081663 | -0.013887 | -0.02128 | -0.0084865 | 0.021512 | 0.057995 | -0.0016665 | -0.021844 | 0.033457 | -0.012988 | 0.11165 | 0.08278 | 0.29764 | -0.11342 | 0.074307 | 0.078197 | -0.033458 | 0.020409 | 0.16938 | 0.168 | -0.1962 | 120.4341 | -1.4264 | 120.5256 | 120.5345 | 0.10044 | -1.4553 | -1.2404 | 120.3513 | -1.5177 | 120.6218 | 120.514 | 0.16274 | -1.3687 | -1.3701 | 120.6591 | 120.6303 | 120.8451 | 120.5809 | -1.6515 | 120.5679 | 120.7169 | 120.7155 | 120.6257 | -1.7343
6120.1719 | 122.3236 | -120.5933 | 1.5793 | -0.0025182 | -0.071905 | 0.037302 | 0.013486 | -0.016138 | 0.0083799 | -0.021518 | -0.02128 | -0.0080591 | 0.021512 | 0.057568 | -0.0016665 | -0.008109 | 0.0243 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.10427 | 0.083464 | 0.082776 | -0.033458 | 0.020409 | 0.1648 | 0.16342 | -0.1962 | 120.489 | -1.4676 | 120.5852 | 120.5894 | 0.10044 | -1.4919 | -1.2816 | 120.3971 | -1.5589 | 120.6767 | 120.5598 | 0.16274 | -1.4145 | -1.4159 | 120.7049 | 120.6806 | 120.8909 | 120.6176 | -1.6836 | 120.6137 | 120.7581 | 120.7567 | 120.676 | -1.7755
6121.8906 | 122.438 | -120.5475 | 1.5656 | -0.010149 | -0.071478 | 0.037088 | 0.013486 | -0.016138 | 0.0085935 | -0.021518 | -0.021494 | -0.0084865 | 0.02194 | 0.057995 | -0.0014529 | -0.017266 | 0.0243 | -0.008409 | 0.11165 | 0.08278 | 0.29764 | -0.10885 | 0.074307 | 0.073618 | -0.033458 | 0.020409 | 0.17396 | 0.16342 | -0.1962 | 120.4386 | -1.4539 | 120.5302 | 120.5391 | 0.10044 | -1.4828 | -1.2679 | 120.3513 | -1.5451 | 120.6218 | 120.514 | 0.16274 | -1.3916 | -1.4021 | 120.6591 | 120.6303 | 120.8451 | 120.5718 | -1.6744 | 120.5679 | 120.7214 | 120.7109 | 120.6211 | -1.7618
6123.6406 | 122.3877 | -120.2682 | 1.8951 | -0.010149 | -0.071692 | 0.037302 | 0.013272 | -0.016138 | 0.0085935 | -0.0062567 | -0.02128 | -0.0082729 | 0.02194 | 0.057995 | -0.0012393 | -0.012688 | 0.0243 | -0.012988 | 0.11165 | 0.078201 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.17258 | -0.1962 | 120.1594 | -1.7835 | 120.2556 | 120.2553 | 0.095859 | -1.8169 | -1.5975 | 120.072 | -1.8793 | 120.3471 | 120.2348 | 0.16274 | -1.7258 | -1.7226 | 120.3799 | 120.3465 | 120.5659 | 120.2925 | -2.004 | 120.2841 | 120.4376 | 120.4408 | 120.351 | -2.0913
6125.3281 | 122.3053 | -120.2911 | 1.9226 | -0.010149 | -0.071692 | 0.037302 | 0.013699 | -0.016138 | 0.0081663 | -0.021518 | -0.021067 | -0.0087001 | 0.021512 | 0.057781 | -0.0012393 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.087359 | 0.29306 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.1648 | 0.168 | -0.1962 | 120.1823 | -1.8155 | 120.2739 | 120.2873 | 0.10502 | -1.8352 | -1.6295 | 120.0949 | -1.9022 | 120.37 | 120.2577 | 0.16274 | -1.7578 | -1.7546 | 120.3982 | 120.3785 | 120.5842 | 120.3246 | -2.0315 | 120.3115 | 120.4559 | 120.4591 | 120.3785 | -2.1188
6127.0312 | 122.4197 | -120.2728 | 1.8768 | -0.010149 | -0.072119 | 0.037302 | 0.013699 | -0.016138 | 0.0083799 | -0.029148 | -0.021494 | -0.0080591 | 0.021726 | 0.057781 | -0.0014529 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.087359 | 0.29764 | -0.10885 | 0.074307 | 0.096512 | -0.033458 | 0.015831 | 0.1648 | 0.17258 | -0.1962 | 120.164 | -1.7698 | 120.2556 | 120.269 | 0.10502 | -1.7895 | -1.5792 | 120.0766 | -1.861 | 120.3471 | 120.2394 | 0.16274 | -1.712 | -1.7043 | 120.3799 | 120.3602 | 120.5705 | 120.3063 | -1.9857 | 120.2887 | 120.4376 | 120.4454 | 120.3693 | -2.073
6128.75 | 122.3053 | -120.3003 | 1.9089 | -0.01778 | -0.071905 | 0.037088 | 0.013699 | -0.016352 | 0.0083799 | -0.021518 | -0.020853 | -0.0082729 | 0.021726 | 0.057995 | -0.0016665 | -0.012688 | 0.028878 | -0.008409 | 0.1208 | 0.08278 | 0.29764 | -0.11342 | 0.083464 | 0.082776 | -0.038036 | 0.011252 | 0.16022 | 0.17258 | -0.20536 | 120.1869 | -1.7881 | 120.2876 | 120.2919 | 0.10502 | -1.8261 | -1.6112 | 120.0949 | -1.8976 | 120.3838 | 120.2623 | 0.16732 | -1.7487 | -1.7363 | 120.4211 | 120.3831 | 120.5979 | 120.3292 | -2.0223 | 120.3115 | 120.4605 | 120.4729 | 120.3831 | -2.1142
6130.4531 | 122.4609 | -120.4559 | 1.6891 | -0.01778 | -0.071692 | 0.037516 | 0.013699 | -0.015924 | 0.0085935 | -0.029148 | -0.021067 | -0.0082729 | 0.021512 | 0.057995 | -0.0012393 | -0.021844 | 0.028878 | 0.000747 | 0.10707 | 0.087359 | 0.29764 | -0.10427 | 0.083464 | 0.082776 | -0.038036 | 0.015831 | 0.1648 | 0.16342 | -0.20078 | 120.3517 | -1.5821 | 120.4341 | 120.4567 | 0.10501 | -1.6018 | -1.3915 | 120.2552 | -1.6733 | 120.5394 | 120.4179 | 0.16274 | -1.5243 | -1.5257 | 120.563 | 120.5433 | 120.7536 | 120.4848 | -1.7934 | 120.4718 | 120.6207 | 120.6194 | 120.5387 | -1.8899
6132.1562 | 122.2824 | -120.4147 | 1.7807 | -0.01778 | -0.071905 | 0.037088 | 0.013486 | -0.015924 | 0.0085935 | -0.036779 | -0.021494 | -0.0084865 | 0.021726 | 0.058422 | -0.0014529 | -0.021844 | 0.028878 | -0.003831 | 0.11622 | 0.08278 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.042615 | 0.011252 | 0.16022 | 0.17258 | -0.1962 | 120.3059 | -1.6645 | 120.3929 | 120.4109 | 0.10502 | -1.6979 | -1.4831 | 120.2185 | -1.7694 | 120.4936 | 120.3721 | 0.15359 | -1.6205 | -1.6081 | 120.531 | 120.4975 | 120.7124 | 120.4436 | -1.8895 | 120.426 | 120.575 | 120.5873 | 120.5021 | -1.9769
6133.8906 | 122.3236 | -120.282 | 1.9363 | -0.01778 | -0.072119 | 0.037516 | 0.013699 | -0.015924 | 0.0079525 | -0.013887 | -0.021067 | -0.0084865 | 0.021726 | 0.058209 | -0.0012393 | -0.008109 | 0.0243 | -0.008409 | 0.11622 | 0.087359 | 0.29764 | -0.10427 | 0.078886 | 0.087354 | -0.042615 | 0.020409 | 0.16938 | 0.17258 | -0.1962 | 120.1777 | -1.8201 | 120.2739 | 120.2736 | 0.095859 | -1.849 | -1.6387 | 120.0858 | -1.9159 | 120.3609 | 120.2394 | 0.15359 | -1.767 | -1.7638 | 120.3982 | 120.3693 | 120.5796 | 120.3063 | -2.0406 | 120.3024 | 120.4514 | 120.4546 | 120.3693 | -2.1325
6135.6406 | 122.3785 | -120.4971 | 1.6937 | -0.01778 | -0.071692 | 0.037516 | 0.013699 | -0.015924 | 0.0081663 | -0.029148 | -0.021708 | -0.0080591 | 0.021512 | 0.058422 | -0.0014529 | -0.021844 | 0.033457 | -0.003831 | 0.10707 | 0.08278 | 0.30222 | -0.11342 | 0.083464 | 0.078197 | -0.033458 | 0.015831 | 0.17396 | 0.17258 | -0.1962 | 120.3837 | -1.5867 | 120.4753 | 120.4933 | 0.10959 | -1.6109 | -1.3915 | 120.3009 | -1.6779 | 120.5806 | 120.4637 | 0.16274 | -1.5198 | -1.5211 | 120.6042 | 120.5799 | 120.7993 | 120.5306 | -1.8072 | 120.513 | 120.6711 | 120.6697 | 120.5753 | -1.8899
6137.3906 | 122.3785 | -120.5017 | 1.7029 | -0.0025182 | -0.071905 | 0.037088 | 0.013913 | -0.015711 | 0.0088073 | -0.021518 | -0.021067 | -0.0082729 | 0.02194 | 0.058209 | -0.0016665 | -0.017266 | 0.038035 | -0.003831 | 0.11165 | 0.096516 | 0.29306 | -0.10427 | 0.074307 | 0.087354 | -0.033458 | 0.006674 | 0.16938 | 0.168 | -0.1962 | 120.3974 | -1.5912 | 120.4844 | 120.4979 | 0.10044 | -1.6064 | -1.4098 | 120.3055 | -1.6962 | 120.576 | 120.4683 | 0.16274 | -1.5335 | -1.5349 | 120.6134 | 120.5982 | 120.7948 | 120.5397 | -1.8071 | 120.5084 | 120.6711 | 120.6697 | 120.5891 | -1.8991
6139.0938 | 122.3877 | -98.2086 | 23.9227 | -0.01778 | -0.071905 | 0.037516 | 0.013699 | -0.015924 | 0.0085935 | -0.029148 | -0.021494 | -0.0082729 | 0.02194 | 0.058209 | -0.0012393 | -0.012688 | 0.028878 | -0.003831 | 0.10249 | 0.087359 | 0.29764 | -0.10427 | 0.083464 | 0.082776 | -0.033458 | 0.011252 | 0.16938 | 0.168 | -0.1962 | 98.1043 | -23.8202 | 98.1959 | 98.2048 | 0.10044 | -23.8354 | -23.6251 | 98.0124 | -23.9115 | 98.2921 | 98.1752 | 0.16274 | -23.7534 | -23.7547 | 98.3111 | 98.296 | 98.5063 | 98.2375 | -24.027 | 98.2199 | 98.378 | 98.3766 | 98.2914 | -24.1189
6140.7969 | 122.3877 | -120.5704 | 1.6022 | -0.010149 | -0.071905 | 0.037302 | 0.013486 | -0.015711 | 0.0085935 | -0.021518 | -0.02128 | -0.0082729 | 0.021512 | 0.057781 | -0.0014529 | -0.012688 | 0.038035 | 0.005325 | 0.11622 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.015831 | 0.1648 | 0.16342 | -0.20078 | 120.4615 | -1.4859 | 120.5577 | 120.5757 | 0.11417 | -1.5148 | -1.3045 | 120.3696 | -1.5863 | 120.6493 | 120.5369 | 0.16732 | -1.4374 | -1.4387 | 120.6866 | 120.6577 | 120.868 | 120.6084 | -1.711 | 120.5862 | 120.7352 | 120.7338 | 120.6577 | -1.803
6142.5625 | 122.5113 | -120.5658 | 1.5701 | -0.01778 | -0.071905 | 0.037088 | 0.014127 | -0.015924 | 0.0085935 | -0.013887 | -0.02128 | -0.0080591 | 0.021726 | 0.057995 | -0.0014529 | -0.017266 | 0.0243 | -0.008409 | 0.10707 | 0.08278 | 0.29764 | -0.10885 | 0.088043 | 0.082776 | -0.033458 | 0.020409 | 0.1648 | 0.168 | -0.20078 | 120.4569 | -1.4631 | 120.5485 | 120.5574 | 0.10044 | -1.4873 | -1.2725 | 120.365 | -1.5497 | 120.6538 | 120.5323 | 0.16732 | -1.4053 | -1.4021 | 120.6729 | 120.6486 | 120.8634 | 120.5901 | -1.679 | 120.5862 | 120.7306 | 120.7338 | 120.6486 | -1.7709
6144.2656 | 122.4335 | -120.6162 | 1.5884 | -0.0025182 | -0.072119 | 0.036874 | 0.013699 | -0.016352 | 0.0085935 | -0.029148 | -0.021067 | -0.0082729 | 0.021512 | 0.057995 | -0.0014529 | -0.017266 | 0.038035 | -0.003831 | 0.11622 | 0.091937 | 0.3068 | -0.10427 | 0.078886 | 0.082776 | -0.028879 | 0.011252 | 0.16938 | 0.16342 | -0.19162 | 120.5119 | -1.4722 | 120.5989 | 120.6123 | 0.10044 | -1.4965 | -1.2816 | 120.4245 | -1.5772 | 120.695 | 120.5873 | 0.16274 | -1.4191 | -1.425 | 120.7324 | 120.7081 | 120.9229 | 120.6542 | -1.6927 | 120.6274 | 120.7855 | 120.7796 | 120.6989 | -1.7801
6145.9844 | 122.4747 | -120.6024 | 1.5656 | -0.01778 | -0.072119 | 0.037088 | 0.013699 | -0.016138 | 0.0083799 | -0.013887 | -0.021067 | -0.0080591 | 0.021726 | 0.057781 | -0.0016665 | -0.017266 | 0.0243 | -0.008409 | 0.10707 | 0.091937 | 0.29764 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.015831 | 0.15564 | 0.168 | -0.20536 | 120.4936 | -1.4585 | 120.5852 | 120.594 | 0.10044 | -1.4736 | -1.2679 | 120.3971 | -1.5497 | 120.6813 | 120.569 | 0.1719 | -1.4099 | -1.3976 | 120.7095 | 120.6944 | 120.9001 | 120.6267 | -1.6744 | 120.6182 | 120.7581 | 120.7704 | 120.6806 | -1.7709
6147.6875 | 121.7834 | -107.7026 | 13.9664 | -0.01778 | -0.071905 | 0.037088 | 0.013486 | -0.015924 | 0.0085935 | -0.013887 | -0.02128 | -0.0080591 | 0.021299 | 0.058209 | -0.0016665 | -0.017266 | 0.028878 | -0.008409 | 0.10707 | 0.091937 | 0.30222 | -0.11342 | 0.074307 | 0.078197 | -0.038036 | 0.011252 | 0.1648 | 0.16342 | -0.20078 | 107.5892 | -13.8593 | 107.6854 | 107.6942 | 0.10502 | -13.8744 | -13.6642 | 107.5019 | -13.9551 | 107.7769 | 107.6646 | 0.16274 | -13.8016 | -13.8029 | 107.8097 | 107.7946 | 108.0049 | 107.7315 | -14.0798 | 107.7139 | 107.8674 | 107.8661 | 107.7808 | -14.1671
6149.375 | 122.0261 | -65.5151 | 56.1584 | -0.0025182 | -0.071905 | 0.037302 | 0.013699 | -0.016138 | 0.0085935 | -0.021518 | -0.021708 | -0.0082729 | 0.021512 | 0.058209 | -0.0014529 | -0.017266 | 0.028878 | -0.012988 | 0.11165 | 0.087359 | 0.29306 | -0.11342 | 0.069728 | 0.078197 | -0.038036 | 0.015831 | 0.1648 | 0.16342 | -0.20994 | 65.4017 | -56.0468 | 65.4979 | 65.5021 | 0.10044 | -56.0711 | -55.8654 | 65.3052 | -56.1426 | 65.5849 | 65.4771 | 0.1719 | -55.9936 | -55.995 | 65.6268 | 65.6025 | 65.8082 | 65.544 | -56.2719 | 65.531 | 65.6799 | 65.6786 | 65.5933 | -56.3684
6151.0938 | 121.7606 | -12.0712 | 109.8953 | -0.01778 | -0.071692 | 0.037088 | 0.013486 | -0.016138 | 0.0085935 | -0.021518 | -0.02128 | -0.0082729 | 0.021726 | 0.057995 | -0.0012393 | -0.017266 | 0.0243 | -0.008409 | 0.11622 | 0.078201 | 0.29764 | -0.118 | 0.074307 | 0.078197 | -0.038036 | 0.011252 | 0.1648 | 0.16342 | -0.1962 | 11.9532 | -109.7791 | 12.054 | 12.0628 | 0.10959 | -109.8171 | -109.5977 | 11.875 | -109.8841 | 12.1455 | 12.0332 | 0.15816 | -109.7305 | -109.7319 | 12.1875 | 12.1494 | 12.3689 | 12.0955 | -110.0133 | 12.0825 | 12.236 | 12.2347 | 12.1494 | -110.0915
6152.8125 | 122.1039 | -10.112 | 111.113 | -0.01778 | -0.071692 | 0.037302 | 0.013699 | -0.016138 | 0.0085935 | -0.021518 | -0.021708 | -0.0082729 | 0.02194 | 0.058209 | -0.0014529 | -0.021844 | 0.028878 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | -0.10885 | 0.074307 | 0.06904 | -0.038036 | 0.011252 | 0.16022 | 0.168 | -0.20536 | 10.0032 | -110.9968 | 10.0902 | 10.1036 | 0.10044 | -111.0256 | -110.8108 | 9.9066 | -111.1017 | 10.1863 | 10.074 | 0.16732 | -110.9528 | -110.945 | 10.2282 | 10.1994 | 10.4142 | 10.1409 | -111.2218 | 10.1233 | 10.2722 | 10.28 | 10.181 | -111.3183
6154.5 | 108.0002 | -12.1902 | 95.6268 | -0.01778 | -0.071905 | 0.036874 | 0.013272 | -0.015924 | 0.0083799 | -0.036779 | -0.020853 | -0.0084865 | 0.021512 | 0.057995 | -0.0014529 | -0.021844 | 0.0243 | -0.017566 | 0.11165 | 0.087359 | 0.29306 | -0.13174 | 0.074307 | 0.082776 | -0.038036 | 0.015831 | 0.15564 | 0.168 | -0.20536 | 12.0585 | -95.5152 | 12.1684 | 12.1727 | 0.11417 | -95.5395 | -95.3338 | 11.9849 | -95.611 | 12.2646 | 12.1522 | 0.16732 | -95.4712 | -95.4588 | 12.3019 | 12.2776 | 12.4833 | 12.2145 | -95.7586 | 12.2061 | 12.3459 | 12.3582 | 12.273 | -95.8322
6156.2031 | 91.2827 | -13.2202 | 80.8228 | -0.01778 | -0.072119 | 0.037088 | 0.013486 | -0.016138 | 0.0079525 | -0.013887 | -0.02128 | -0.0084865 | 0.021726 | 0.057995 | -0.0010255 | -0.021844 | 0.019721 | -0.003831 | 0.10707 | 0.087359 | 0.29306 | -0.11342 | 0.069728 | 0.073618 | -0.033458 | 0.011252 | 0.17396 | 0.16342 | -0.20536 | 13.1068 | -80.7157 | 13.1984 | 13.2164 | 0.10959 | -80.7354 | -80.5297 | 13.0149 | -80.8115 | 13.2899 | 13.1868 | 0.1719 | -80.6488 | -80.6593 | 13.3273 | 13.3076 | 13.5133 | 13.2399 | -80.9362 | 13.2315 | 13.3942 | 13.3836 | 13.2938 | -81.0281
6157.9062 | 121.7468 | -12.1857 | 109.584 | -0.010149 | -0.071905 | 0.037302 | 0.013699 | -0.015924 | 0.0081663 | -0.021518 | -0.021067 | -0.0082729 | 0.021726 | 0.057995 | -0.0016665 | -0.026423 | 0.028878 | -0.012988 | 0.11165 | 0.078201 | 0.29306 | -0.11342 | 0.083464 | 0.087354 | -0.038036 | 0.015831 | 0.1648 | 0.16342 | -0.1962 | 12.0722 | -109.4724 | 12.1592 | 12.1727 | 0.10044 | -109.5058 | -109.291 | 11.9895 | -109.5682 | 12.2691 | 12.1476 | 0.15816 | -109.4192 | -109.4206 | 12.2973 | 12.2639 | 12.4787 | 12.2145 | -109.6975 | 12.2015 | 12.3505 | 12.3491 | 12.273 | -109.7802
6159.6094 | 122.3373 | -107.1671 | 14.653 | -0.010149 | -0.071905 | 0.036874 | 0.013272 | -0.016138 | 0.0083799 | -0.013887 | -0.02128 | -0.0082729 | 0.021512 | 0.058209 | -0.0014529 | -0.021844 | 0.038035 | -0.012988 | 0.10249 | 0.091937 | 0.29764 | -0.10427 | 0.083464 | 0.082776 | -0.038036 | 0.015831 | 0.16022 | 0.17258 | -0.19162 | 107.0628 | -14.5505 | 107.1452 | 107.1541 | 0.09128 | -14.5611 | -14.3554 | 106.9754 | -14.6372 | 107.2505 | 107.129 | 0.15359 | -14.4928 | -14.4804 | 107.2695 | 107.259 | 107.4647 | 107.2051 | -14.7573 | 107.1829 | 107.3273 | 107.3396 | 107.2498 | -14.8446
6161.3281 | 122.3373 | -113.0447 | 8.8852 | -0.010149 | -0.071905 | 0.037302 | 0.013486 | -0.016138 | 0.0085935 | -0.0062567 | -0.02128 | -0.0080591 | 0.02194 | 0.057995 | -0.0012393 | -0.021844 | 0.033457 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.020409 | 0.1648 | 0.168 | -0.1962 | 112.9359 | -8.7735 | 113.0229 | 113.0409 | 0.10502 | -8.7978 | -8.5876 | 112.8485 | -8.8648 | 113.1236 | 113.0067 | 0.15816 | -8.7204 | -8.7172 | 113.1564 | 113.1321 | 113.3424 | 113.0782 | -8.994 | 113.0651 | 113.2095 | 113.2127 | 113.1275 | -9.0814
6163.0312 | 122.3557 | -105.954 | 15.889 | -0.010149 | -0.071478 | 0.037516 | 0.013486 | -0.016138 | 0.0083799 | -0.013887 | -0.021067 | -0.0082729 | 0.021726 | 0.058209 | -0.0016665 | -0.017266 | 0.019721 | -0.003831 | 0.1208 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.020409 | 0.1648 | 0.168 | -0.19162 | 105.8451 | -15.7682 | 105.9367 | 105.9501 | 0.10502 | -15.8016 | -15.5913 | 105.7624 | -15.8686 | 106.0329 | 105.9159 | 0.15359 | -15.7242 | -15.721 | 106.0748 | 106.0413 | 106.2516 | 105.9737 | -15.9978 | 105.9744 | 106.1188 | 106.122 | 106.0368 | -16.0806
6164.7656 | 122.2824 | -121.0556 | 0.94757 | -0.010149 | -0.072119 | 0.037088 | 0.013272 | -0.016138 | 0.0079525 | -0.021518 | -0.02128 | -0.0082729 | 0.021299 | 0.058209 | -0.0014529 | -0.012688 | 0.033457 | -0.003831 | 0.11165 | 0.091937 | 0.29764 | -0.118 | 0.083464 | 0.078197 | -0.033458 | 0.011252 | 0.16022 | 0.17258 | -0.1962 | 120.9376 | -0.83592 | 121.0429 | 121.0518 | 0.11417 | -0.85563 | -0.64993 | 120.8594 | -0.93632 | 121.1391 | 121.0221 | 0.16274 | -0.78735 | -0.77499 | 121.1673 | 121.1475 | 121.3532 | 121.0891 | -1.0656 | 121.0669 | 121.2158 | 121.2282 | 121.1338 | -1.1438
6166.5312 | 122.2504 | -115.8966 | 6.0974 | -0.025411 | -0.071692 | 0.037302 | 0.013486 | -0.016138 | 0.0085935 | -0.029148 | -0.02128 | -0.0084865 | 0.021512 | 0.058422 | -0.0016665 | -0.017266 | 0.0243 | -0.008409 | 0.11622 | 0.08278 | 0.29764 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.15564 | 0.16342 | -0.1962 | 115.7832 | -5.9812 | 115.8793 | 115.8882 | 0.10502 | -6.0146 | -5.7998 | 115.7004 | -6.0816 | 115.9755 | 115.8631 | 0.16274 | -5.9418 | -5.934 | 116.0128 | 115.9794 | 116.1942 | 115.9209 | -6.2108 | 115.9124 | 116.0522 | 116.06 | 115.9794 | -6.2936
6168.2344 | 122.1954 | -112.4634 | 9.4894 | -0.010149 | -0.071692 | 0.036874 | 0.013913 | -0.015924 | 0.0083799 | -0.021518 | -0.021494 | -0.0084865 | 0.021085 | 0.058422 | -0.0012393 | -0.012688 | 0.038035 | -0.012988 | 0.11622 | 0.091937 | 0.29306 | -0.118 | 0.074307 | 0.091933 | -0.028879 | 0.020409 | 0.1648 | 0.168 | -0.1962 | 112.3454 | -9.3732 | 112.4507 | 112.4504 | 0.10502 | -9.3975 | -9.1964 | 112.2672 | -9.469 | 112.5377 | 112.4345 | 0.16732 | -9.3246 | -9.3214 | 112.5796 | 112.5553 | 112.7564 | 112.5014 | -9.6074 | 112.4838 | 112.6282 | 112.6314 | 112.5553 | -9.6856
6169.9375 | 122.3419 | -121.1243 | 0.88348 | -0.010149 | -0.071692 | 0.036874 | 0.013699 | -0.015924 | 0.0085935 | -0.021518 | -0.021067 | -0.0082729 | 0.02194 | 0.057995 | -0.0014529 | -0.017266 | 0.019721 | -0.012988 | 0.11165 | 0.08278 | 0.30222 | -0.11342 | 0.083464 | 0.082776 | -0.033458 | 0.015831 | 0.17396 | 0.17258 | -0.1962 | 121.0108 | -0.77184 | 121.107 | 121.1113 | 0.10044 | -0.8007 | -0.58127 | 120.9281 | -0.86765 | 121.2077 | 121.0908 | 0.16274 | -0.70953 | -0.7109 | 121.2359 | 121.207 | 121.4265 | 121.144 | -0.99691 | 121.1401 | 121.2982 | 121.2968 | 121.207 | -1.0797
6171.6562 | 122.2183 | -121.1838 | 0.90637 | -0.010149 | -0.071692 | 0.037088 | 0.013699 | -0.016138 | 0.0083799 | -0.021518 | -0.02128 | -0.0080591 | 0.021512 | 0.057995 | -0.0014529 | -0.012688 | 0.033457 | -0.008409 | 0.10707 | 0.087359 | 0.29764 | -0.10885 | 0.074307 | 0.087354 | -0.033458 | 0.020409 | 0.1648 | 0.168 | -0.1962 | 121.0749 | -0.7993 | 121.1711 | 121.1754 | 0.10044 | -0.81901 | -0.60873 | 120.9876 | -0.88596 | 121.2581 | 121.1503 | 0.16274 | -0.74157 | -0.73837 | 121.2908 | 121.2711 | 121.4814 | 121.2172 | -1.0152 | 121.2042 | 121.3486 | 121.3518 | 121.2711 | -1.1026
6173.3438 | 122.3236 | -121.1792 | 0.85602 | -0.01778 | -0.071905 | 0.037302 | 0.013486 | -0.016138 | 0.0085935 | -0.029148 | -0.02064 | -0.0082729 | 0.021299 | 0.058209 | -0.0016665 | -0.017266 | 0.033457 | -0.012988 | 0.11165 | 0.08278 | 0.30222 | -0.10885 | 0.074307 | 0.082776 | -0.038036 | 0.020409 | 0.16938 | 0.168 | -0.19162 | 121.0704 | -0.74437 | 121.1619 | 121.1662 | 0.095859 | -0.77324 | -0.5538 | 120.9876 | -0.83561 | 121.2535 | 121.1412 | 0.15359 | -0.68664 | -0.68802 | 121.2908 | 121.262 | 121.4814 | 121.2127 | -0.96486 | 121.1996 | 121.3486 | 121.3472 | 121.262 | -1.0476
6175.0625 | 122.3236 | -121.1929 | 0.8606 | -0.010149 | -0.071692 | 0.037088 | 0.013272 | -0.016138 | 0.0081663 | -0.029148 | -0.02128 | -0.0078455 | 0.021726 | 0.058422 | -0.0014529 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.30222 | -0.10885 | 0.069728 | 0.082776 | -0.033458 | 0.020409 | 0.16938 | 0.168 | -0.1962 | 121.0841 | -0.74895 | 121.1757 | 121.1845 | 0.10044 | -0.77324 | -0.55838 | 120.9967 | -0.84019 | 121.2627 | 121.1595 | 0.16274 | -0.69122 | -0.69259 | 121.3046 | 121.2803 | 121.4951 | 121.2264 | -0.96944 | 121.2133 | 121.3623 | 121.3609 | 121.2757 | -1.0568
6176.7656 | 122.3053 | -121.1884 | 0.86975 | -0.025411 | -0.071905 | 0.037302 | 0.013272 | -0.016352 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.021726 | 0.058422 | -0.0014529 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.029566 | 0.16022 | 0.16342 | -0.20078 | 121.0795 | -0.75353 | 121.1711 | 121.1754 | 0.095859 | -0.78239 | -0.57211 | 120.9876 | -0.84019 | 121.2672 | 121.1503 | 0.16274 | -0.70953 | -0.70633 | 121.3046 | 121.2757 | 121.486 | 121.2264 | -0.9786 | 121.2179 | 121.3486 | 121.3518 | 121.2711 | -1.0705
6178.4688 | 122.2549 | -121.1975 | 0.91095 | -0.01778 | -0.071905 | 0.037302 | 0.013486 | -0.016138 | 0.0083799 | -0.021518 | -0.021708 | -0.0087001 | 0.021512 | 0.058209 | -0.0014529 | -0.021844 | 0.038035 | -0.012988 | 0.11165 | 0.087359 | 0.3068 | -0.11342 | 0.074307 | 0.082776 | -0.028879 | 0.011252 | 0.16938 | 0.168 | -0.1962 | 121.0841 | -0.7993 | 121.1757 | 121.1845 | 0.10044 | -0.82359 | -0.60415 | 121.0013 | -0.8997 | 121.2718 | 121.1686 | 0.16732 | -0.74157 | -0.74295 | 121.3092 | 121.2849 | 121.5043 | 121.2355 | -1.0244 | 121.2088 | 121.3669 | 121.3655 | 121.2803 | -1.1072
6180.1719 | 122.3602 | -121.1975 | 0.89264 | -0.01778 | -0.071692 | 0.037302 | 0.013486 | -0.015924 | 0.0083799 | -0.036779 | -0.021067 | -0.0080591 | 0.021726 | 0.058209 | -0.0014529 | -0.021844 | 0.033457 | -0.012988 | 0.11622 | 0.087359 | 0.29306 | -0.10427 | 0.078886 | 0.078197 | -0.042615 | 0.015831 | 0.16022 | 0.16342 | -0.1962 | 121.0932 | -0.77641 | 121.1757 | 121.1845 | 0.09128 | -0.80528 | -0.59958 | 121.0013 | -0.87681 | 121.2764 | 121.1549 | 0.15359 | -0.73242 | -0.72922 | 121.3137 | 121.2849 | 121.4906 | 121.231 | -0.99691 | 121.2133 | 121.3577 | 121.3609 | 121.2757 | -1.0888
6181.8906 | 122.3785 | -121.1746 | 0.86975 | -0.01778 | -0.071905 | 0.037088 | 0.013272 | -0.015924 | 0.0083799 | -0.021518 | -0.021067 | -0.0080591 | 0.021512 | 0.058209 | -0.0014529 | -0.008109 | 0.038035 | -0.008409 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.028879 | 0.015831 | 0.1648 | 0.15884 | -0.1962 | 121.0658 | -0.7581 | 121.1665 | 121.1662 | 0.10044 | -0.78239 | -0.57211 | 120.9784 | -0.85392 | 121.2535 | 121.1457 | 0.16732 | -0.70495 | -0.71091 | 121.2863 | 121.262 | 121.4723 | 121.2127 | -0.9786 | 121.1905 | 121.3394 | 121.3335 | 121.2574 | -1.066
6183.6406 | 122.3328 | -121.2067 | 0.86975 | -0.025411 | -0.071905 | 0.037302 | 0.013699 | -0.016138 | 0.0088073 | -0.036779 | -0.021494 | -0.0084865 | 0.021512 | 0.058422 | -0.0012393 | -0.012688 | 0.038035 | -0.012988 | 0.11622 | 0.087359 | 0.29764 | -0.099689 | 0.083464 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.168 | -0.20078 | 121.107 | -0.75353 | 121.194 | 121.1937 | 0.086701 | -0.78239 | -0.57211 | 121.0059 | -0.85392 | 121.2901 | 121.1732 | 0.16732 | -0.70037 | -0.70175 | 121.3229 | 121.294 | 121.5043 | 121.2447 | -0.96944 | 121.2225 | 121.376 | 121.3747 | 121.2894 | -1.0705
6185.3906 | 122.2961 | -121.2479 | 0.87891 | -0.010149 | -0.071692 | 0.036874 | 0.013272 | -0.016352 | 0.0083799 | -0.021518 | -0.021494 | -0.0082729 | 0.022153 | 0.058209 | -0.0014529 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | -0.10427 | 0.069728 | 0.082776 | -0.033458 | 0.015831 | 0.16022 | 0.16342 | -0.1962 | 121.1436 | -0.76268 | 121.2306 | 121.2395 | 0.095859 | -0.79155 | -0.57669 | 121.0517 | -0.86307 | 121.3176 | 121.2144 | 0.16274 | -0.71868 | -0.71548 | 121.3641 | 121.3352 | 121.5501 | 121.2813 | -0.98317 | 121.2637 | 121.4081 | 121.4113 | 121.3306 | -1.0751
6187.0938 | 122.3785 | -121.225 | 0.86975 | -0.0025182 | -0.071905 | 0.037088 | 0.013486 | -0.016138 | 0.0081663 | -0.021518 | -0.02128 | -0.0082729 | 0.02194 | 0.058422 | -0.0012393 | -0.021844 | 0.0243 | -0.008409 | 0.11622 | 0.08278 | 0.30222 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.015831 | 0.16022 | 0.168 | -0.19162 | 121.1161 | -0.75353 | 121.2031 | 121.2166 | 0.10044 | -0.78697 | -0.56753 | 121.0334 | -0.85392 | 121.3039 | 121.1915 | 0.15816 | -0.70953 | -0.70175 | 121.3412 | 121.3078 | 121.5272 | 121.2493 | -0.9786 | 121.2408 | 121.3852 | 121.393 | 121.3123 | -1.0614
6188.7969 | 122.3785 | -121.225 | 0.86517 | -0.025411 | -0.071692 | 0.037302 | 0.013486 | -0.016352 | 0.0081663 | -0.029148 | -0.02128 | -0.0080591 | 0.021726 | 0.058209 | -0.0018801 | -0.017266 | 0.028878 | -0.003831 | 0.11622 | 0.087359 | 0.29764 | -0.10885 | 0.083464 | 0.082776 | -0.042615 | 0.015831 | 0.17396 | 0.17716 | -0.1962 | 121.1161 | -0.74895 | 121.2077 | 121.2211 | 0.10502 | -0.77781 | -0.56753 | 121.0288 | -0.84934 | 121.3084 | 121.1824 | 0.15359 | -0.69121 | -0.68801 | 121.3412 | 121.3123 | 121.5226 | 121.2539 | -0.97402 | 121.2408 | 121.3989 | 121.4021 | 121.3078 | -1.0614
6190.5625 | 122.3419 | -121.2341 | 0.87891 | -0.0025182 | -0.071692 | 0.037516 | 0.013699 | -0.016138 | 0.0085935 | -0.029148 | -0.02128 | -0.0082729 | 0.021512 | 0.058209 | -0.0016665 | -0.021844 | 0.028878 | -0.008409 | 0.1208 | 0.08278 | 0.3068 | -0.11342 | 0.074307 | 0.078197 | -0.033458 | 0.015831 | 0.16938 | 0.168 | -0.20536 | 121.1207 | -0.7581 | 121.2123 | 121.2257 | 0.10502 | -0.79613 | -0.57211 | 121.0288 | -0.86307 | 121.3084 | 121.2007 | 0.1719 | -0.70953 | -0.7109 | 121.3549 | 121.3169 | 121.5409 | 121.263 | -0.99233 | 121.25 | 121.4035 | 121.4021 | 121.3123 | -1.0843
6192.2656 | 122.2504 | -121.2479 | 0.89722 | -0.010149 | -0.071692 | 0.037302 | 0.013486 | -0.015924 | 0.0083799 | -0.029148 | -0.021494 | -0.0082729 | 0.021512 | 0.058422 | -0.0014529 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.10885 | 0.074307 | 0.087354 | -0.033458 | 0.011252 | 0.1648 | 0.16342 | -0.20536 | 121.139 | -0.78099 | 121.226 | 121.2395 | 0.10044 | -0.80528 | -0.59042 | 121.0425 | -0.88597 | 121.3222 | 121.2144 | 0.1719 | -0.73242 | -0.73379 | 121.3641 | 121.3398 | 121.5547 | 121.2813 | -1.0061 | 121.2591 | 121.4127 | 121.4113 | 121.3352 | -1.1026
6193.9844 | 122.3785 | -121.2204 | 0.85602 | -0.01778 | -0.071905 | 0.037302 | 0.013699 | -0.016138 | 0.0081663 | -0.021518 | -0.021067 | -0.0080591 | 0.021512 | 0.058209 | -0.0016665 | -0.012688 | 0.038035 | -0.008409 | 0.11165 | 0.087359 | 0.30222 | -0.118 | 0.083464 | 0.082776 | -0.028879 | 0.015831 | 0.17396 | 0.16342 | -0.20078 | 121.1024 | -0.74437 | 121.2077 | 121.212 | 0.10959 | -0.76866 | -0.5538 | 121.0196 | -0.84019 | 121.3039 | 121.1915 | 0.1719 | -0.68206 | -0.69259 | 121.332 | 121.3078 | 121.5226 | 121.2584 | -0.97402 | 121.2362 | 121.3944 | 121.3838 | 121.3032 | -1.0568
6195.6875 | 122.319 | -121.2662 | 0.88806 | -0.010149 | -0.071692 | 0.037302 | 0.013486 | -0.016565 | 0.0085935 | -0.021518 | -0.021067 | -0.0080591 | 0.021726 | 0.058209 | -0.0014529 | -0.012688 | 0.0243 | -0.003831 | 0.11622 | 0.087359 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.028879 | 0.015831 | 0.16938 | 0.16342 | -0.20078 | 121.1573 | -0.77184 | 121.2535 | 121.2623 | 0.10502 | -0.8007 | -0.59042 | 121.0654 | -0.87223 | 121.3451 | 121.2373 | 0.1719 | -0.71868 | -0.72464 | 121.3824 | 121.3535 | 121.5638 | 121.2905 | -0.99691 | 121.282 | 121.4356 | 121.4296 | 121.349 | -1.0888
6197.4219 | 122.3969 | -121.2662 | 0.8606 | -0.0025182 | -0.072119 | 0.037302 | 0.013272 | -0.015924 | 0.0081663 | -0.013887 | -0.021494 | -0.0082729 | 0.021299 | 0.058422 | -0.0016665 | -0.012688 | 0.028878 | -0.012988 | 0.11622 | 0.091937 | 0.29764 | -0.118 | 0.083464 | 0.082776 | -0.038036 | 0.011252 | 0.16938 | 0.168 | -0.19162 | 121.1482 | -0.74437 | 121.2535 | 121.2532 | 0.10502 | -0.76866 | -0.56296 | 121.0746 | -0.84934 | 121.3496 | 121.2281 | 0.15359 | -0.69122 | -0.69259 | 121.3824 | 121.3581 | 121.5638 | 121.2951 | -0.9786 | 121.2774 | 121.4356 | 121.4342 | 121.349 | -1.0522
6199.1406 | 122.2824 | -121.2067 | 0.94757 | -0.01778 | -0.071905 | 0.037088 | 0.013699 | -0.016352 | 0.0083799 | -0.021518 | -0.021067 | -0.0084865 | 0.021512 | 0.058209 | -0.0014529 | -0.008109 | 0.0243 | -0.012988 | 0.11165 | 0.096516 | 0.31137 | -0.10885 | 0.078886 | 0.073618 | -0.033458 | 0.015831 | 0.17396 | 0.168 | -0.1962 | 121.0978 | -0.83592 | 121.1986 | 121.1937 | 0.095859 | -0.85106 | -0.6362 | 121.0105 | -0.93174 | 121.2856 | 121.1732 | 0.16274 | -0.77361 | -0.77957 | 121.3183 | 121.3032 | 121.518 | 121.231 | -1.0564 | 121.2225 | 121.3806 | 121.3747 | 121.2803 | -1.1438
6200.8438 | 122.2778 | -121.2708 | 0.92926 | -0.010149 | -0.071905 | 0.037302 | 0.013486 | -0.016352 | 0.0083799 | -0.0062567 | -0.021494 | -0.0080591 | 0.021512 | 0.058209 | -0.0014529 | -0.017266 | 0.038035 | -0.003831 | 0.10249 | 0.087359 | 0.3068 | -0.10885 | 0.069728 | 0.078197 | -0.033458 | 0.015831 | 0.1648 | 0.17258 | -0.20536 | 121.1619 | -0.82677 | 121.2535 | 121.2669 | 0.10502 | -0.8419 | -0.62246 | 121.0654 | -0.91343 | 121.3405 | 121.2373 | 0.1719 | -0.76446 | -0.75668 | 121.3732 | 121.3581 | 121.5775 | 121.3088 | -1.0381 | 121.2866 | 121.4356 | 121.4433 | 121.3489 | -1.1346
6202.5469 | 122.2916 | -121.2708 | 0.9201 | 0.0051128 | -0.071692 | 0.037302 | 0.013486 | -0.016352 | 0.0085935 | -0.021518 | -0.020853 | -0.0084865 | 0.021512 | 0.058209 | -0.0016665 | -0.021844 | 0.028878 | 0.000747 | 0.1208 | 0.096516 | 0.29764 | -0.10885 | 0.083464 | 0.082776 | -0.028879 | 0.020409 | 0.17396 | 0.17258 | -0.20078 | 121.1619 | -0.7993 | 121.2489 | 121.2715 | 0.10959 | -0.82359 | -0.62247 | 121.07 | -0.8997 | 121.3542 | 121.2419 | 0.1719 | -0.74615 | -0.74752 | 121.3916 | 121.3673 | 121.5684 | 121.2996 | -1.029 | 121.2912 | 121.4447 | 121.4433 | 121.3535 | -1.1209
6204.2812 | 122.2504 | -121.2662 | 0.9201 | -0.01778 | -0.071905 | 0.036874 | 0.013058 | -0.016138 | 0.0081663 | -0.021518 | -0.021067 | -0.0084865 | 0.021512 | 0.057995 | -0.0014529 | -0.012688 | 0.028878 | -0.003831 | 0.11165 | 0.08278 | 0.29764 | -0.10427 | 0.078886 | 0.087354 | -0.033458 | 0.006674 | 0.1648 | 0.168 | -0.20078 | 121.1619 | -0.80846 | 121.2535 | 121.2623 | 0.10044 | -0.83732 | -0.62247 | 121.0654 | -0.91343 | 121.3451 | 121.2327 | 0.16732 | -0.7553 | -0.7521 | 121.3778 | 121.349 | 121.5638 | 121.2951 | -1.0244 | 121.2728 | 121.431 | 121.4342 | 121.3535 | -1.1209
6206.0156 | 122.2961 | -121.2524 | 0.92926 | -0.01778 | -0.071905 | 0.037088 | 0.013272 | -0.016138 | 0.0085935 | -0.021518 | -0.02128 | -0.0080591 | 0.021299 | 0.058422 | -0.0016665 | -0.017266 | 0.028878 | -0.008409 | 0.11165 | 0.091937 | 0.29306 | -0.10885 | 0.074307 | 0.082776 | -0.038036 | 0.011252 | 0.16938 | 0.17258 | -0.20078 | 121.1436 | -0.81761 | 121.2352 | 121.244 | 0.10044 | -0.83732 | -0.6362 | 121.0517 | -0.91801 | 121.3267 | 121.2144 | 0.16274 | -0.75988 | -0.75668 | 121.3641 | 121.3444 | 121.5455 | 121.2813 | -1.0381 | 121.2637 | 121.4218 | 121.425 | 121.3352 | -1.13
6207.7188 | 122.4014 | -121.225 | 0.89264 | -0.01778 | -0.072119 | 0.036874 | 0.013486 | -0.016352 | 0.0083799 | -0.013887 | -0.02128 | -0.0082729 | 0.02194 | 0.058422 | -0.0016665 | -0.017266 | 0.033457 | -0.012988 | 0.11622 | 0.091937 | 0.30222 | -0.10885 | 0.074307 | 0.082776 | -0.028879 | 0.015831 | 0.16022 | 0.16342 | -0.20078 | 121.1161 | -0.77641 | 121.2077 | 121.212 | 0.095859 | -0.8007 | -0.59042 | 121.0242 | -0.87681 | 121.2993 | 121.1961 | 0.1719 | -0.73242 | -0.72922 | 121.3412 | 121.3169 | 121.5272 | 121.2584 | -1.0015 | 121.2408 | 121.3852 | 121.3884 | 121.3078 | -1.0934
6209.4219 | 122.2824 | -121.2708 | 0.93842 | -0.010149 | -0.072119 | 0.037088 | 0.013272 | -0.015924 | 0.0081663 | -0.029148 | -0.02128 | -0.0082729 | 0.021726 | 0.058209 | -0.0014529 | -0.017266 | 0.028878 | -0.012988 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.074307 | 0.082776 | -0.028879 | 0.020409 | 0.1648 | 0.168 | -0.1962 | 121.1573 | -0.82219 | 121.2535 | 121.2578 | 0.10044 | -0.84648 | -0.63162 | 121.0746 | -0.91801 | 121.3451 | 121.2419 | 0.16732 | -0.77362 | -0.77041 | 121.387 | 121.3627 | 121.5775 | 121.2996 | -1.0518 | 121.2912 | 121.4356 | 121.4388 | 121.3535 | -1.1346
6211.1562 | 122.3923 | -121.2662 | 0.87891 | -0.01778 | -0.072119 | 0.037302 | 0.013486 | -0.016352 | 0.0081663 | -0.029148 | -0.021067 | -0.0080591 | 0.021299 | 0.058636 | -0.0016665 | -0.012688 | 0.028878 | -0.008409 | 0.10707 | 0.087359 | 0.3068 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.015831 | 0.16022 | 0.17258 | -0.1962 | 121.1527 | -0.77184 | 121.2535 | 121.2578 | 0.10502 | -0.79155 | -0.57211 | 121.07 | -0.86307 | 121.3451 | 121.2327 | 0.16274 | -0.71868 | -0.70633 | 121.3732 | 121.3535 | 121.573 | 121.2951 | -0.99233 | 121.282 | 121.4264 | 121.4388 | 121.3535 | -1.0751
6212.8594 | 122.3465 | -121.2753 | 0.90179 | -0.0025182 | -0.071692 | 0.037088 | 0.013486 | -0.016138 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.021512 | 0.058422 | -0.0016665 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | -0.118 | 0.083464 | 0.082776 | -0.038036 | 0.006674 | 0.1648 | 0.14053 | -0.19162 | 121.1573 | -0.78557 | 121.2581 | 121.2669 | 0.10959 | -0.81444 | -0.59958 | 121.0837 | -0.89512 | 121.3588 | 121.2373 | 0.15359 | -0.73699 | -0.76126 | 121.3916 | 121.3627 | 121.5775 | 121.3088 | -1.0198 | 121.282 | 121.4401 | 121.4159 | 121.3581 | -1.0934
6214.6094 | 122.3099 | -121.2753 | 0.89722 | -0.01778 | -0.072119 | 0.036661 | 0.013272 | -0.016138 | 0.0081663 | -0.013887 | -0.02128 | -0.0082729 | 0.021512 | 0.057995 | -0.0018801 | -0.012688 | 0.033457 | -0.003831 | 0.11165 | 0.096516 | 0.28848 | -0.11342 | 0.078886 | 0.082776 | -0.038036 | 0.015831 | 0.1648 | 0.14053 | -0.20536 | 121.1619 | -0.78557 | 121.2626 | 121.2715 | 0.10959 | -0.8007 | -0.60874 | 121.07 | -0.88139 | 121.3542 | 121.2373 | 0.16732 | -0.73242 | -0.75669 | 121.387 | 121.3718 | 121.5638 | 121.3088 | -1.0106 | 121.2912 | 121.4401 | 121.4159 | 121.3581 | -1.1026
6216.3125 | 122.3969 | -121.225 | 0.90179 | -0.010149 | -0.072119 | 0.037302 | 0.013486 | -0.016138 | 0.0085935 | -0.021518 | -0.02128 | -0.0082729 | 0.021512 | 0.058422 | -0.0014529 | -0.017266 | 0.019721 | -0.008409 | 0.1208 | 0.087359 | 0.29764 | -0.11342 | 0.078886 | 0.087354 | -0.028879 | 0.015831 | 0.16938 | 0.13137 | -0.20078 | 121.1116 | -0.78099 | 121.2077 | 121.2166 | 0.10502 | -0.81444 | -0.60416 | 121.0242 | -0.88596 | 121.3039 | 121.1961 | 0.1719 | -0.73242 | -0.77042 | 121.3458 | 121.3123 | 121.5226 | 121.2447 | -1.0152 | 121.2408 | 121.3944 | 121.3563 | 121.3123 | -1.1026
6218.0469 | 122.3236 | -121.2753 | 0.91095 | -0.01778 | -0.072119 | 0.036874 | 0.013699 | -0.016565 | 0.0081663 | -0.029148 | -0.021067 | -0.0080591 | 0.021726 | 0.058422 | -0.0012393 | -0.017266 | 0.028878 | -0.008409 | 0.11622 | 0.08278 | 0.29764 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.011252 | 0.17396 | 0.14053 | -0.20078 | 121.1665 | -0.79473 | 121.2581 | 121.2669 | 0.10044 | -0.82817 | -0.61331 | 121.0746 | -0.8997 | 121.3542 | 121.2419 | 0.16732 | -0.73699 | -0.77042 | 121.3916 | 121.3581 | 121.573 | 121.3042 | -1.0198 | 121.2866 | 121.4493 | 121.4159 | 121.3535 | -1.1117
6219.7656 | 122.2961 | -121.2891 | 0.9201 | -0.01778 | -0.072333 | 0.037516 | 0.013272 | -0.016138 | 0.0083799 | -0.029148 | -0.021067 | -0.0082729 | 0.021726 | 0.058422 | -0.0018801 | -0.017266 | 0.0243 | 0.000747 | 0.11165 | 0.08278 | 0.30222 | -0.118 | 0.083464 | 0.078197 | -0.028879 | 0.011252 | 0.1648 | 0.13137 | -0.1962 | 121.1711 | -0.80846 | 121.2718 | 121.2898 | 0.11875 | -0.83732 | -0.61789 | 121.0929 | -0.90885 | 121.3725 | 121.2602 | 0.16732 | -0.7553 | -0.78873 | 121.4007 | 121.3718 | 121.5913 | 121.3134 | -1.0381 | 121.3003 | 121.4539 | 121.4204 | 121.3673 | -1.1163
6221.4688 | 122.3923 | -121.257 | 0.90179 | -0.033042 | -0.071905 | 0.037088 | 0.013272 | -0.016565 | 0.0081663 | -0.021518 | -0.02128 | -0.0084865 | 0.021512 | 0.058209 | -0.0012393 | -0.017266 | 0.038035 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | -0.118 | 0.074307 | 0.078197 | -0.028879 | 0.015831 | 0.1648 | 0.13595 | -0.20078 | 121.139 | -0.78557 | 121.2398 | 121.2532 | 0.11417 | -0.81444 | -0.59958 | 121.0562 | -0.88596 | 121.3313 | 121.2281 | 0.1719 | -0.73699 | -0.76584 | 121.3732 | 121.3444 | 121.5592 | 121.2951 | -1.0198 | 121.2729 | 121.4218 | 121.393 | 121.3352 | -1.1026
6223.1719 | 122.319 | -121.2936 | 0.94757 | -0.010149 | -0.071905 | 0.037302 | 0.013486 | -0.016352 | 0.0083799 | -0.013887 | -0.02128 | -0.0084865 | 0.021726 | 0.058209 | -0.0012393 | -0.012688 | 0.033457 | -0.008409 | 0.1208 | 0.08278 | 0.29764 | -0.11342 | 0.078886 | 0.073618 | -0.033458 | 0.015831 | 0.16938 | 0.13595 | -0.20078 | 121.1802 | -0.82677 | 121.281 | 121.2852 | 0.10502 | -0.86479 | -0.64993 | 121.0929 | -0.93174 | 121.3725 | 121.2602 | 0.16732 | -0.77819 | -0.81162 | 121.4144 | 121.3764 | 121.5913 | 121.3271 | -1.061 | 121.3095 | 121.463 | 121.4296 | 121.3673 | -1.1483
6224.9062 | 122.4243 | -121.2662 | 0.89264 | -0.01778 | -0.071905 | 0.036874 | 0.013486 | -0.015924 | 0.0079525 | -0.013887 | -0.021067 | -0.0082729 | 0.021512 | 0.057995 | -0.0014529 | -0.012688 | 0.028878 | -0.003831 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.087354 | -0.028879 | 0.015831 | 0.16022 | 0.13595 | -0.20536 | 121.1527 | -0.77641 | 121.2535 | 121.2623 | 0.10959 | -0.8007 | -0.58584 | 121.0608 | -0.87681 | 121.3451 | 121.2373 | 0.17648 | -0.73242 | -0.75669 | 121.3824 | 121.3581 | 121.573 | 121.2951 | -1.0061 | 121.282 | 121.4264 | 121.4021 | 121.3535 | -1.098
6226.6094 | 122.3465 | -121.3211 | 0.89722 | -0.010149 | -0.072119 | 0.036874 | 0.013486 | -0.016138 | 0.0083799 | -0.029148 | -0.02128 | -0.0082729 | 0.021299 | 0.058422 | -0.0016665 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.091937 | 0.3068 | -0.11342 | 0.074307 | 0.082776 | -0.033458 | 0.015831 | 0.1648 | 0.13595 | -0.20536 | 121.2077 | -0.78557 | 121.3038 | 121.3173 | 0.10959 | -0.80528 | -0.59042 | 121.1157 | -0.88139 | 121.3954 | 121.2876 | 0.1719 | -0.73242 | -0.76127 | 121.4328 | 121.413 | 121.6279 | 121.3546 | -1.0106 | 121.3369 | 121.4859 | 121.4571 | 121.4039 | -1.1026
6228.2969 | 122.3648 | -121.2799 | 0.90179 | -0.010149 | -0.072119 | 0.037088 | 0.013913 | -0.016138 | 0.0081663 | -0.021518 | -0.021067 | -0.0082729 | 0.021512 | 0.058636 | -0.0014529 | -0.008109 | 0.028878 | -0.008409 | 0.11622 | 0.087359 | 0.29306 | -0.118 | 0.078886 | 0.082776 | -0.038036 | 0.015831 | 0.16022 | 0.14053 | -0.20078 | 121.1619 | -0.78557 | 121.2718 | 121.2715 | 0.10959 | -0.81444 | -0.60873 | 121.0791 | -0.88596 | 121.3588 | 121.2419 | 0.16274 | -0.74157 | -0.76126 | 121.3961 | 121.3673 | 121.573 | 121.3088 | -1.0198 | 121.2957 | 121.4401 | 121.4204 | 121.3627 | -1.1026
6230.0156 | 122.319 | -121.3074 | 0.90179 | -0.01778 | -0.071905 | 0.037088 | 0.013699 | -0.016138 | 0.0081663 | -0.021518 | -0.02128 | -0.0082729 | 0.021512 | 0.058209 | -0.0016665 | -0.012688 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.29764 | -0.10427 | 0.083464 | 0.087354 | -0.038036 | 0.015831 | 0.16022 | 0.13595 | -0.19162 | 121.2031 | -0.79015 | 121.2947 | 121.299 | 0.095859 | -0.81444 | -0.60416 | 121.1158 | -0.88596 | 121.3908 | 121.2693 | 0.15359 | -0.74157 | -0.76584 | 121.419 | 121.3947 | 121.605 | 121.3408 | -1.0061 | 121.3232 | 121.4676 | 121.4433 | 121.3947 | -1.0934
6231.7188 | 122.3648 | -121.3028 | 0.90179 | -0.01778 | -0.071905 | 0.036661 | 0.013272 | -0.015711 | 0.0081663 | -0.013887 | -0.021067 | -0.0082729 | 0.021512 | 0.058422 | -0.0012393 | -0.012688 | 0.028878 | -0.012988 | 0.11622 | 0.091937 | 0.31137 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.006674 | 0.16022 | 0.13137 | -0.1962 | 121.1939 | -0.78557 | 121.2901 | 121.2898 | 0.095859 | -0.80986 | -0.59042 | 121.1066 | -0.89512 | 121.3817 | 121.2648 | 0.15816 | -0.74157 | -0.77042 | 121.419 | 121.3947 | 121.6142 | 121.3317 | -1.0106 | 121.3095 | 121.463 | 121.4342 | 121.3856 | -1.098
6233.4062 | 122.4426 | -121.2616 | 0.87433 | -0.01778 | -0.071905 | 0.037088 | 0.013699 | -0.016352 | 0.0083799 | -0.029148 | -0.02128 | -0.0080591 | 0.021512 | 0.05885 | -0.0016665 | -0.012688 | 0.028878 | -0.008409 | 0.11165 | 0.08278 | 0.29764 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.011252 | 0.16938 | 0.14511 | -0.1962 | 121.1527 | -0.76268 | 121.2489 | 121.2532 | 0.10044 | -0.79155 | -0.57669 | 121.0654 | -0.86308 | 121.3405 | 121.2236 | 0.15816 | -0.70495 | -0.72922 | 121.3732 | 121.3444 | 121.5592 | 121.2905 | -0.98318 | 121.2728 | 121.431 | 121.4067 | 121.3444 | -1.0705
6235.1406 | 122.3785 | -121.312 | 0.90179 | -0.01778 | -0.071692 | 0.037088 | 0.013486 | -0.016565 | 0.0085935 | -0.029148 | -0.02128 | -0.0082729 | 0.021299 | 0.058636 | -0.0016665 | -0.021844 | 0.038035 | -0.008409 | 0.10707 | 0.096516 | 0.29764 | -0.10885 | 0.069728 | 0.087354 | -0.038036 | 0.011252 | 0.16938 | 0.13595 | -0.1962 | 121.2031 | -0.79473 | 121.2901 | 121.3035 | 0.10044 | -0.80528 | -0.60416 | 121.1158 | -0.89054 | 121.3817 | 121.2739 | 0.15816 | -0.73242 | -0.76584 | 121.419 | 121.4085 | 121.6096 | 121.35 | -1.0106 | 121.3232 | 121.4813 | 121.4479 | 121.3993 | -1.098
6236.8438 | 122.438 | -121.2616 | 0.88348 | -0.01778 | -0.071905 | 0.036874 | 0.013272 | -0.016138 | 0.0085935 | -0.029148 | -0.021708 | -0.0082729 | 0.021512 | 0.058636 | -0.0018801 | -0.012688 | 0.0243 | -0.003831 | 0.11622 | 0.08278 | 0.3068 | -0.118 | 0.083464 | 0.082776 | -0.033458 | 0.006674 | 0.16022 | 0.13137 | -0.20078 | 121.1436 | -0.76726 | 121.2489 | 121.2578 | 0.11417 | -0.8007 | -0.57669 | 121.0608 | -0.87681 | 121.3451 | 121.2281 | 0.16732 | -0.72326 | -0.75211 | 121.3778 | 121.3444 | 121.5684 | 121.2859 | -1.0015 | 121.2683 | 121.4218 | 121.393 | 121.3444 | -1.0843
6238.6094 | 122.4426 | -121.2708 | 0.88806 | -0.0025182 | -0.072333 | 0.037088 | 0.013272 | -0.016352 | 0.0083799 | -0.029148 | -0.021494 | -0.0080591 | 0.021299 | 0.058636 | -0.0016665 | -0.021844 | 0.033457 | -0.017566 | 0.11622 | 0.087359 | 0.3068 | -0.10427 | 0.083464 | 0.078197 | -0.033458 | 0.020409 | 0.16022 | 0.13137 | -0.20536 | 121.1665 | -0.77184 | 121.2489 | 121.2532 | 0.086702 | -0.8007 | -0.58127 | 121.0654 | -0.86765 | 121.3542 | 121.2373 | 0.1719 | -0.72784 | -0.75669 | 121.387 | 121.3581 | 121.5775 | 121.3042 | -0.99233 | 121.2912 | 121.431 | 121.4021 | 121.3489 | -1.0934
6240.2969 | 122.4152 | -121.312 | 0.90179 | -0.0025182 | -0.072119 | 0.036874 | 0.013272 | -0.016352 | 0.0085935 | -0.021518 | -0.02128 | -0.0080591 | 0.021512 | 0.058422 | -0.0014529 | -0.012688 | 0.028878 | -0.003831 | 0.11622 | 0.091937 | 0.30222 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.006674 | 0.1648 | 0.13595 | -0.20078 | 121.1985 | -0.78557 | 121.2993 | 121.3081 | 0.10959 | -0.80986 | -0.59958 | 121.1112 | -0.89512 | 121.3908 | 121.2785 | 0.16732 | -0.73699 | -0.76584 | 121.4282 | 121.4039 | 121.6142 | 121.3408 | -1.0152 | 121.3186 | 121.4768 | 121.4479 | 121.3947 | -1.1026
6242.0625 | 122.406 | -121.3257 | 0.87433 | -0.025411 | -0.071905 | 0.036874 | 0.013486 | -0.016565 | 0.0081663 | -0.029148 | -0.021494 | -0.0076319 | 0.021299 | 0.057781 | -0.0016665 | -0.017266 | 0.033457 | -0.012988 | 0.11622 | 0.087359 | 0.30222 | -0.118 | 0.078886 | 0.078197 | -0.033458 | 0.011252 | 0.16938 | 0.13595 | -0.1962 | 121.2077 | -0.7581 | 121.3084 | 121.3127 | 0.10502 | -0.78697 | -0.57211 | 121.1295 | -0.86308 | 121.4046 | 121.2922 | 0.16274 | -0.70495 | -0.73838 | 121.4419 | 121.413 | 121.6279 | 121.3591 | -0.99233 | 121.3369 | 121.4951 | 121.4616 | 121.4039 | -1.0705
6243.7656 | 122.3648 | -121.3623 | 0.89722 | -0.0025182 | -0.072119 | 0.037302 | 0.013272 | -0.016565 | 0.0085935 | -0.013887 | -0.021708 | -0.0084865 | 0.021512 | 0.058636 | -0.0014529 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.096516 | 0.29306 | -0.10885 | 0.083464 | 0.091933 | -0.028879 | 0.011252 | 0.16938 | 0.13137 | -0.20078 | 121.2535 | -0.78099 | 121.345 | 121.3493 | 0.095859 | -0.8007 | -0.60416 | 121.1615 | -0.88597 | 121.4458 | 121.3334 | 0.1719 | -0.72784 | -0.76584 | 121.4785 | 121.4588 | 121.6554 | 121.4003 | -1.0061 | 121.3736 | 121.5317 | 121.4937 | 121.4542 | -1.098
6245.5 | 122.3328 | -121.3394 | 0.90179 | -0.010149 | -0.071905 | 0.037088 | 0.013058 | -0.015924 | 0.0083799 | -0.0062567 | -0.02128 | -0.0082729 | 0.021726 | 0.058422 | -0.0018801 | -0.021844 | 0.033457 | -0.003831 | 0.10707 | 0.096516 | 0.29306 | -0.11342 | 0.074307 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.14511 | -0.20078 | 121.226 | -0.79473 | 121.3176 | 121.3356 | 0.10959 | -0.80528 | -0.60873 | 121.1386 | -0.88596 | 121.4137 | 121.306 | 0.16732 | -0.73242 | -0.75669 | 121.4465 | 121.4359 | 121.6325 | 121.3729 | -1.0152 | 121.3552 | 121.5088 | 121.4845 | 121.4222 | -1.1026
6247.2188 | 122.4792 | -121.3348 | 0.85602 | -0.025411 | -0.072119 | 0.037302 | 0.013272 | -0.016138 | 0.0083799 | -0.021518 | -0.02128 | -0.0080591 | 0.021512 | 0.058209 | -0.0014529 | -0.017266 | 0.0243 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.1648 | 0.13595 | -0.20078 | 121.226 | -0.73979 | 121.3176 | 121.3264 | 0.10044 | -0.76408 | -0.54922 | 121.1341 | -0.84019 | 121.4137 | 121.3014 | 0.16732 | -0.69122 | -0.72007 | 121.4511 | 121.4268 | 121.6416 | 121.3591 | -0.96486 | 121.3507 | 121.4996 | 121.4708 | 121.4176 | -1.0568
6248.9219 | 122.3923 | -121.3165 | 0.87891 | -0.01778 | -0.072119 | 0.037088 | 0.013699 | -0.016352 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.021726 | 0.058209 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.30222 | -0.11342 | 0.083464 | 0.082776 | -0.042615 | 0.006674 | 0.1648 | 0.13137 | -0.1962 | 121.2031 | -0.76726 | 121.2993 | 121.3081 | 0.10502 | -0.79155 | -0.57669 | 121.1203 | -0.87223 | 121.4 | 121.2739 | 0.15359 | -0.71411 | -0.74753 | 121.4282 | 121.4039 | 121.6187 | 121.35 | -0.99233 | 121.3232 | 121.4813 | 121.4479 | 121.3993 | -1.0751
6250.6562 | 122.406 | -121.3531 | 0.89722 | -0.0025182 | -0.072333 | 0.037088 | 0.013058 | -0.016352 | 0.0081663 | -0.013887 | -0.021067 | -0.0078455 | 0.021726 | 0.058422 | -0.0014529 | -0.021844 | 0.033457 | -0.003831 | 0.11622 | 0.091937 | 0.30222 | -0.10885 | 0.078886 | 0.078197 | -0.028879 | 0.011252 | 0.16022 | 0.14053 | -0.20078 | 121.2443 | -0.78099 | 121.3313 | 121.3493 | 0.10502 | -0.80528 | -0.595 | 121.1524 | -0.88597 | 121.432 | 121.3243 | 0.1719 | -0.737 | -0.75669 | 121.4694 | 121.4451 | 121.6554 | 121.3866 | -1.0061 | 121.3644 | 121.5134 | 121.4937 | 121.4313 | -1.098
6252.3438 | 122.4472 | -121.312 | 0.86975 | -0.010149 | -0.071905 | 0.036874 | 0.013272 | -0.015924 | 0.0088073 | -0.021518 | -0.021067 | -0.0082729 | 0.021512 | 0.058636 | -0.0012393 | -0.021844 | 0.0243 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.10885 | 0.074307 | 0.087354 | -0.028879 | 0.015831 | 0.16022 | 0.13137 | -0.19162 | 121.2031 | -0.75353 | 121.2901 | 121.3035 | 0.10044 | -0.77781 | -0.56296 | 121.1203 | -0.85392 | 121.3863 | 121.2831 | 0.16274 | -0.70953 | -0.73838 | 121.4282 | 121.4039 | 121.6187 | 121.3363 | -0.9786 | 121.3278 | 121.4722 | 121.4433 | 121.3993 | -1.0614
6254.0469 | 122.3648 | -121.3531 | 0.89722 | -0.01778 | -0.072119 | 0.037088 | 0.013486 | -0.016565 | 0.0083799 | -0.013887 | -0.02128 | -0.0082729 | 0.021512 | 0.058209 | -0.0018801 | -0.008109 | 0.0243 | -0.003831 | 0.11165 | 0.096516 | 0.3068 | -0.10885 | 0.083464 | 0.087354 | -0.033458 | 0.015831 | 0.16022 | 0.13595 | -0.20078 | 121.2443 | -0.78557 | 121.345 | 121.3493 | 0.10502 | -0.8007 | -0.59042 | 121.1524 | -0.88139 | 121.4366 | 121.3197 | 0.16732 | -0.737 | -0.76127 | 121.4648 | 121.4497 | 121.6599 | 121.3774 | -1.0061 | 121.369 | 121.5134 | 121.4891 | 121.4405 | -1.098
6255.7656 | 122.4792 | -121.3165 | 0.86975 | -0.01778 | -0.072333 | 0.037088 | 0.013486 | -0.015924 | 0.0083799 | -0.021518 | -0.02128 | -0.0080591 | 0.021299 | 0.058422 | -0.0014529 | -0.026423 | 0.028878 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | -0.118 | 0.078886 | 0.082776 | -0.038036 | 0.011252 | 0.1648 | 0.14053 | -0.20078 | 121.1985 | -0.75353 | 121.2901 | 121.3081 | 0.10959 | -0.78239 | -0.56753 | 121.1157 | -0.8585 | 121.3954 | 121.2785 | 0.16274 | -0.70495 | -0.72922 | 121.4328 | 121.4039 | 121.6187 | 121.3454 | -0.98776 | 121.3278 | 121.4813 | 121.4571 | 121.3993 | -1.0705
6257.4688 | 122.3831 | -121.344 | 0.8606 | -0.0025182 | -0.071905 | 0.037088 | 0.013486 | -0.016138 | 0.0085935 | -0.029148 | -0.02128 | -0.0082729 | 0.021299 | 0.058636 | -0.0018801 | -0.021844 | 0.028878 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | -0.10885 | 0.083464 | 0.082776 | -0.033458 | 0.011252 | 0.16938 | 0.13595 | -0.20078 | 121.2351 | -0.74437 | 121.3221 | 121.3356 | 0.10044 | -0.76866 | -0.55838 | 121.1432 | -0.84934 | 121.4275 | 121.3105 | 0.16732 | -0.69122 | -0.72464 | 121.4602 | 121.4359 | 121.6462 | 121.3729 | -0.96944 | 121.3552 | 121.5134 | 121.4799 | 121.4268 | -1.0614
6259.1719 | 122.493 | -121.3303 | 0.86975 | -0.010149 | -0.071692 | 0.036874 | 0.013486 | -0.016138 | 0.0085935 | -0.021518 | -0.021067 | -0.0082729 | 0.021512 | 0.058209 | -0.0014529 | -0.017266 | 0.033457 | -0.003831 | 0.1208 | 0.08278 | 0.30222 | -0.11342 | 0.078886 | 0.082776 | -0.038036 | 0.006674 | 0.16022 | 0.12679 | -0.20078 | 121.2168 | -0.74895 | 121.313 | 121.3264 | 0.10959 | -0.78697 | -0.56753 | 121.1295 | -0.86308 | 121.4091 | 121.2922 | 0.16274 | -0.70953 | -0.74296 | 121.4511 | 121.413 | 121.6325 | 121.3637 | -0.98318 | 121.3369 | 121.4905 | 121.4571 | 121.413 | -1.0705
6260.8906 | 122.5159 | -121.3303 | 0.8606 | -0.025411 | -0.071905 | 0.037088 | 0.013058 | -0.015924 | 0.0083799 | -0.029148 | -0.02128 | -0.0080591 | 0.021085 | 0.058636 | -0.0014529 | -0.017266 | 0.028878 | -0.008409 | 0.11165 | 0.087359 | 0.3068 | -0.11342 | 0.083464 | 0.078197 | -0.038036 | 0.006674 | 0.1648 | 0.14053 | -0.20078 | 121.2168 | -0.74895 | 121.313 | 121.3219 | 0.10502 | -0.77324 | -0.5538 | 121.1295 | -0.85392 | 121.4137 | 121.2922 | 0.16274 | -0.6958 | -0.72007 | 121.4419 | 121.4176 | 121.6371 | 121.3591 | -0.97402 | 121.3369 | 121.4951 | 121.4708 | 121.4085 | -1.0614
6262.5781 | 122.5113 | -121.3165 | 0.8606 | -0.01778 | -0.072546 | 0.037088 | 0.013486 | -0.016138 | 0.0083799 | -0.0062567 | -0.02128 | -0.0082729 | 0.021726 | 0.058636 | -0.0014529 | -0.017266 | 0.0243 | -0.008409 | 0.10707 | 0.087359 | 0.31137 | -0.118 | 0.074307 | 0.078197 | -0.038036 | 0.011252 | 0.16938 | 0.13137 | -0.20078 | 121.1985 | -0.75353 | 121.2993 | 121.3081 | 0.10959 | -0.77324 | -0.54922 | 121.1157 | -0.84934 | 121.3908 | 121.2785 | 0.16274 | -0.69122 | -0.72922 | 121.4236 | 121.4039 | 121.6279 | 121.3408 | -0.9786 | 121.3278 | 121.4859 | 121.4479 | 121.3947 | -1.0614
6264.2812 | 122.4106 | -121.376 | 0.87891 | -0.010149 | -0.071905 | 0.037088 | 0.013058 | -0.016138 | 0.0081663 | -0.021518 | -0.02128 | -0.0084865 | 0.021512 | 0.058209 | -0.0012393 | -0.017266 | 0.033457 | -0.003831 | 0.10707 | 0.087359 | 0.31137 | -0.11342 | 0.083464 | 0.082776 | -0.033458 | 0.011252 | 0.1648 | 0.13595 | -0.1962 | 121.2626 | -0.77184 | 121.3588 | 121.3722 | 0.10959 | -0.79155 | -0.56753 | 121.1798 | -0.86765 | 121.4595 | 121.3426 | 0.16274 | -0.71411 | -0.74295 | 121.4831 | 121.4634 | 121.6874 | 121.4095 | -0.99233 | 121.3873 | 121.5408 | 121.512 | 121.4588 | -1.0751
6266.0156 | 122.5067 | -121.3669 | 0.84686 | -0.01778 | -0.072119 | 0.037516 | 0.013486 | -0.016352 | 0.0081663 | -0.029148 | -0.02128 | -0.0084865 | 0.021512 | 0.058209 | -0.0016665 | -0.021844 | 0.028878 | -0.012988 | 0.1208 | 0.091937 | 0.30222 | -0.10885 | 0.083464 | 0.082776 | -0.033458 | 0.011252 | 0.16938 | 0.14053 | -0.1962 | 121.258 | -0.72606 | 121.345 | 121.3539 | 0.095859 | -0.75493 | -0.54465 | 121.1707 | -0.83561 | 121.4503 | 121.3334 | 0.16274 | -0.67748 | -0.70633 | 121.4877 | 121.4588 | 121.6691 | 121.3958 | -0.95571 | 121.3781 | 121.5363 | 121.5074 | 121.4497 | -1.0431
6267.7188 | 122.4655 | -121.3669 | 0.85602 | -0.01778 | -0.071905 | 0.037302 | 0.013272 | -0.016565 | 0.0083799 | -0.013887 | -0.021494 | -0.0078455 | 0.021299 | 0.058636 | -0.0014529 | -0.021844 | 0.028878 | -0.003831 | 0.11622 | 0.091937 | 0.29764 | -0.11342 | 0.083464 | 0.078197 | -0.033458 | 0.015831 | 0.16022 | 0.13137 | -0.20078 | 121.2535 | -0.73979 | 121.345 | 121.3631 | 0.10959 | -0.76408 | -0.55838 | 121.1661 | -0.84019 | 121.4503 | 121.3334 | 0.16732 | -0.6958 | -0.72464 | 121.4831 | 121.4588 | 121.6645 | 121.3958 | -0.96944 | 121.3827 | 121.5271 | 121.4983 | 121.4451 | -1.0568
6269.4219 | 122.5021 | -121.3486 | 0.83313 | -0.01778 | -0.072119 | 0.036874 | 0.013486 | -0.016352 | 0.0081663 | -0.021518 | -0.02128 | -0.0084865 | 0.021512 | 0.058422 | -0.0014529 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | -0.118 | 0.078886 | 0.078197 | -0.033458 | 0.011252 | 0.15564 | 0.12679 | -0.1962 | 121.2306 | -0.71691 | 121.3313 | 121.3402 | 0.10959 | -0.74119 | -0.53091 | 121.1524 | -0.82188 | 121.4275 | 121.3151 | 0.16274 | -0.67749 | -0.70634 | 121.4648 | 121.4405 | 121.6508 | 121.3866 | -0.95113 | 121.3598 | 121.5042 | 121.4754 | 121.4268 | -1.0293
6271.1406 | 122.4289 | -121.3531 | 0.87433 | -0.01778 | -0.072119 | 0.037088 | 0.013272 | -0.016138 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.021512 | 0.058636 | -0.0014529 | -0.012688 | 0.033457 | -0.008409 | 0.11165 | 0.096516 | 0.29764 | -0.11342 | 0.083464 | 0.082776 | -0.028879 | 0.015831 | 0.1648 | 0.13595 | -0.1962 | 121.2397 | -0.76268 | 121.3405 | 121.3447 | 0.10502 | -0.77781 | -0.57669 | 121.1569 | -0.8585 | 121.4366 | 121.3243 | 0.16732 | -0.70953 | -0.73838 | 121.4648 | 121.4497 | 121.6508 | 121.3866 | -0.98775 | 121.369 | 121.5179 | 121.4891 | 121.4359 | -1.0705
6272.8438 | 122.4747 | -121.3531 | 0.85602 | -0.010149 | -0.072333 | 0.037088 | 0.013058 | -0.016138 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.021512 | 0.059063 | -0.0018801 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | -0.118 | 0.069728 | 0.078197 | -0.038036 | 0.020409 | 0.16022 | 0.13595 | -0.20078 | 121.2351 | -0.73979 | 121.3405 | 121.3447 | 0.10959 | -0.76866 | -0.5538 | 121.1524 | -0.83561 | 121.4229 | 121.3151 | 0.16274 | -0.6958 | -0.72007 | 121.4694 | 121.4405 | 121.6554 | 121.3866 | -0.97402 | 121.3736 | 121.5134 | 121.4891 | 121.4313 | -1.0568
6274.5469 | 122.5021 | -121.3348 | 0.86517 | -0.010149 | -0.072333 | 0.037088 | 0.013486 | -0.015711 | 0.0081663 | -0.021518 | -0.021067 | -0.0084865 | 0.021299 | 0.058636 | -0.0018801 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.118 | 0.078886 | 0.078197 | -0.028879 | 0.015831 | 0.16022 | 0.13595 | -0.20078 | 121.2168 | -0.74895 | 121.3176 | 121.3264 | 0.10959 | -0.77324 | -0.55838 | 121.1341 | -0.84934 | 121.4137 | 121.306 | 0.1719 | -0.70495 | -0.72922 | 121.4511 | 121.4268 | 121.6416 | 121.3683 | -0.98318 | 121.3507 | 121.4951 | 121.4708 | 121.413 | -1.066
6276.2812 | 122.5159 | -121.3486 | 0.85602 | -0.01778 | -0.071905 | 0.036874 | 0.013486 | -0.015924 | 0.0083799 | -0.021518 | -0.021067 | -0.0082729 | 0.021299 | 0.058422 | -0.0012393 | -0.017266 | 0.028878 | -0.012988 | 0.11622 | 0.087359 | 0.30222 | -0.118 | 0.083464 | 0.082776 | -0.033458 | 0.011252 | 0.16938 | 0.13595 | -0.19162 | 121.2306 | -0.73979 | 121.3313 | 121.3356 | 0.10502 | -0.76866 | -0.5538 | 121.157 | -0.84477 | 121.432 | 121.3151 | 0.15816 | -0.68664 | -0.72007 | 121.4648 | 121.4359 | 121.6508 | 121.3775 | -0.97402 | 121.3598 | 121.518 | 121.4845 | 121.4313 | -1.0476
6277.9844 | 122.3511 | -121.3898 | 0.89264 | -0.010149 | -0.072119 | 0.036874 | 0.013272 | -0.016138 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.021299 | 0.058422 | -0.0014529 | -0.017266 | 0.033457 | -0.003831 | 0.11622 | 0.096516 | 0.30222 | -0.11342 | 0.078886 | 0.078197 | -0.038036 | 0.015831 | 0.17396 | 0.13595 | -0.1962 | 121.2763 | -0.77641 | 121.3725 | 121.3859 | 0.10959 | -0.79612 | -0.59042 | 121.1936 | -0.87681 | 121.4687 | 121.3517 | 0.15816 | -0.71868 | -0.75669 | 121.506 | 121.4863 | 121.692 | 121.4232 | -1.0061 | 121.4056 | 121.5637 | 121.5257 | 121.468 | -1.0888
6279.7031 | 122.5342 | -121.3715 | 0.83771 | -0.0025182 | -0.072119 | 0.037302 | 0.013058 | -0.016565 | 0.0083799 | -0.013887 | -0.02128 | -0.0082729 | 0.021085 | 0.058422 | -0.0014529 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.08278 | 0.3068 | -0.11342 | 0.069728 | 0.087354 | -0.033458 | 0.015831 | 0.16938 | 0.13137 | -0.19162 | 121.258 | -0.72148 | 121.3542 | 121.3631 | 0.10502 | -0.75493 | -0.53091 | 121.1798 | -0.82188 | 121.4412 | 121.338 | 0.15816 | -0.66833 | -0.70634 | 121.4877 | 121.4542 | 121.6783 | 121.4095 | -0.95113 | 121.3873 | 121.5408 | 121.5028 | 121.4588 | -1.0293
6281.4062 | 122.4335 | -121.4035 | 0.89264 | -0.01778 | -0.071905 | 0.036874 | 0.013272 | -0.016138 | 0.0081663 | -0.021518 | -0.021067 | -0.0078455 | 0.021299 | 0.05885 | -0.0014529 | -0.017266 | 0.033457 | -0.012988 | 0.10707 | 0.087359 | 0.29764 | -0.118 | 0.083464 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.14053 | -0.20078 | 121.2855 | -0.78557 | 121.3862 | 121.3905 | 0.10502 | -0.80528 | -0.595 | 121.2027 | -0.87681 | 121.487 | 121.37 | 0.16732 | -0.72326 | -0.75211 | 121.5106 | 121.4909 | 121.7011 | 121.437 | -1.0106 | 121.4193 | 121.5729 | 121.544 | 121.4863 | -1.0934
6283.1406 | 122.5113 | -121.3531 | 0.84228 | -0.010149 | -0.072119 | 0.036874 | 0.013058 | -0.016138 | 0.0083799 | -0.021518 | -0.021067 | -0.0078455 | 0.021299 | 0.058636 | -0.0014529 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | -0.11342 | 0.078886 | 0.073618 | -0.033458 | 0.015831 | 0.16938 | 0.13595 | -0.1962 | 121.2397 | -0.72606 | 121.3359 | 121.3447 | 0.10502 | -0.75493 | -0.54007 | 121.1569 | -0.82645 | 121.432 | 121.3197 | 0.16274 | -0.67291 | -0.70633 | 121.4694 | 121.4405 | 121.6554 | 121.3866 | -0.95571 | 121.369 | 121.5225 | 121.4891 | 121.4268 | -1.0385
6284.8438 | 122.3694 | -121.3898 | 0.87891 | -0.010149 | -0.072546 | 0.036874 | 0.013058 | -0.016138 | 0.0079525 | -0.029148 | -0.021067 | -0.0084865 | 0.021299 | 0.058636 | -0.0016665 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.29764 | -0.10885 | 0.083464 | 0.082776 | -0.033458 | 0.020409 | 0.16022 | 0.13137 | -0.19162 | 121.2809 | -0.76726 | 121.3725 | 121.3814 | 0.10044 | -0.79155 | -0.58127 | 121.1981 | -0.8585 | 121.4732 | 121.3563 | 0.15816 | -0.71868 | -0.74753 | 121.5014 | 121.4771 | 121.6874 | 121.4232 | -0.98775 | 121.4102 | 121.55 | 121.5211 | 121.4725 | -1.0705
6286.5625 | 122.4747 | -121.3577 | 0.86517 | -0.01778 | -0.072333 | 0.037302 | 0.013272 | -0.015924 | 0.0083799 | -0.029148 | -0.021494 | -0.0080591 | 0.021726 | 0.058636 | -0.0018801 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | -0.118 | 0.078886 | 0.078197 | -0.038036 | 0.011252 | 0.16938 | 0.14053 | -0.20536 | 121.2397 | -0.74895 | 121.3359 | 121.3493 | 0.10959 | -0.77781 | -0.56296 | 121.1524 | -0.85392 | 121.4366 | 121.3197 | 0.16732 | -0.69579 | -0.72464 | 121.474 | 121.4451 | 121.6599 | 121.3912 | -0.98318 | 121.369 | 121.5271 | 121.4983 | 121.4359 | -1.0705
6288.2656 | 122.4518 | -121.3943 | 0.8194 | -0.01778 | -0.072333 | 0.037088 | 0.013486 | -0.016352 | 0.0083799 | -0.021518 | -0.021067 | -0.0082729 | 0.021299 | 0.05885 | -0.0016665 | -0.012688 | 0.033457 | -0.008409 | 0.11165 | 0.091937 | 0.30222 | -0.10427 | 0.078886 | 0.087354 | -0.033458 | 0.020409 | 0.16022 | 0.13137 | -0.1962 | 121.2901 | -0.70775 | 121.3817 | 121.3859 | 0.095859 | -0.72746 | -0.51718 | 121.1981 | -0.79899 | 121.4732 | 121.3609 | 0.16274 | -0.65918 | -0.68802 | 121.506 | 121.4863 | 121.6966 | 121.4278 | -0.92367 | 121.4148 | 121.5546 | 121.5257 | 121.4817 | -1.0156
6289.9688 | 122.4655 | -121.4035 | 0.85144 | -0.01778 | -0.072333 | 0.037516 | 0.013272 | -0.016138 | 0.0083799 | -0.021518 | -0.021067 | -0.0082729 | 0.021299 | 0.058636 | -0.0014529 | -0.021844 | 0.038035 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | -0.10885 | 0.078886 | 0.078197 | -0.038036 | 0.015831 | 0.1648 | 0.13137 | -0.20078 | 121.2947 | -0.73979 | 121.3817 | 121.3997 | 0.10502 | -0.76408 | -0.54922 | 121.2027 | -0.83561 | 121.4824 | 121.3655 | 0.16274 | -0.68664 | -0.72007 | 121.5152 | 121.4909 | 121.7057 | 121.4415 | -0.96029 | 121.4193 | 121.5683 | 121.5349 | 121.4817 | -1.0522
6291.6875 | 122.493 | -121.4218 | 0.82855 | -0.010149 | -0.072333 | 0.037516 | 0.013699 | -0.016352 | 0.0081663 | -0.021518 | -0.02128 | -0.0082729 | 0.021512 | 0.058422 | -0.0014529 | -0.017266 | 0.028878 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | -0.11342 | 0.074307 | 0.091933 | -0.033458 | 0.011252 | 0.1648 | 0.12222 | -0.19162 | 121.3084 | -0.71233 | 121.4045 | 121.418 | 0.10959 | -0.74119 | -0.52633 | 121.2302 | -0.8173 | 121.4961 | 121.3884 | 0.15816 | -0.66375 | -0.70634 | 121.538 | 121.5092 | 121.724 | 121.4507 | -0.94198 | 121.4331 | 121.5866 | 121.544 | 121.5137 | -1.0202
6293.3906 | 122.5204 | -121.3943 | 0.82398 | -0.0025182 | -0.072333 | 0.037088 | 0.013272 | -0.016352 | 0.0083799 | -0.021518 | -0.021067 | -0.0080591 | 0.021299 | 0.05885 | -0.0016665 | -0.017266 | 0.033457 | -0.008409 | 0.1208 | 0.087359 | 0.3068 | -0.118 | 0.074307 | 0.087354 | -0.028879 | 0.015831 | 0.1648 | 0.13137 | -0.1962 | 121.2763 | -0.70317 | 121.3771 | 121.3859 | 0.10959 | -0.73662 | -0.51718 | 121.1981 | -0.80814 | 121.4687 | 121.3655 | 0.16732 | -0.65918 | -0.6926 | 121.5152 | 121.4817 | 121.7011 | 121.4278 | -0.94198 | 121.4102 | 121.5591 | 121.5257 | 121.4817 | -1.0202
6295.1406 | 122.4426 | -121.4355 | 0.84686 | -0.010149 | -0.072333 | 0.037088 | 0.013486 | -0.016138 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.021299 | 0.058422 | -0.0016665 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.1011 | 0.30222 | -0.10427 | 0.083464 | 0.082776 | -0.028879 | 0.020409 | 0.16938 | 0.13137 | -0.1962 | 121.3313 | -0.73522 | 121.4183 | 121.4271 | 0.095859 | -0.74577 | -0.54465 | 121.2393 | -0.82645 | 121.519 | 121.4067 | 0.16732 | -0.67748 | -0.71549 | 121.5472 | 121.5366 | 121.7378 | 121.469 | -0.95113 | 121.456 | 121.6049 | 121.5669 | 121.5183 | -1.0431
6296.8438 | 122.4243 | -121.4401 | 0.83771 | -0.010149 | -0.072546 | 0.036874 | 0.013486 | -0.016565 | 0.0081663 | -0.029148 | -0.021067 | -0.0078455 | 0.021299 | 0.058636 | -0.0018801 | -0.012688 | 0.033457 | -0.008409 | 0.1208 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.078197 | -0.033458 | 0.015831 | 0.17396 | 0.14053 | -0.20536 | 121.3267 | -0.7169 | 121.4274 | 121.4317 | 0.10502 | -0.74577 | -0.53091 | 121.2348 | -0.82188 | 121.519 | 121.4067 | 0.1719 | -0.66375 | -0.69718 | 121.5609 | 121.5321 | 121.7469 | 121.4736 | -0.95113 | 121.456 | 121.6141 | 121.5807 | 121.5183 | -1.0431
6298.5625 | 122.5204 | -121.3989 | 0.82398 | -0.01778 | -0.07276 | 0.037088 | 0.013486 | -0.016352 | 0.0081663 | -0.021518 | -0.021067 | -0.0080591 | 0.021512 | 0.058422 | -0.0016665 | -0.012688 | 0.042614 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | -0.11342 | 0.074307 | 0.078197 | -0.033458 | 0.015831 | 0.16938 | 0.13137 | -0.1962 | 121.2855 | -0.70775 | 121.3862 | 121.3951 | 0.10959 | -0.73662 | -0.52176 | 121.2027 | -0.80814 | 121.4732 | 121.3655 | 0.16274 | -0.6546 | -0.6926 | 121.5152 | 121.4863 | 121.7011 | 121.4415 | -0.9374 | 121.4148 | 121.5683 | 121.5303 | 121.4771 | -1.0202
6300.2656 | 122.4518 | -121.4447 | 0.85602 | -0.01778 | -0.072546 | 0.037302 | 0.013486 | -0.016352 | 0.0081663 | -0.013887 | -0.021494 | -0.0080591 | 0.021512 | 0.058636 | -0.0016665 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.096516 | 0.30222 | -0.10885 | 0.074307 | 0.087354 | -0.028879 | 0.006674 | 0.1648 | 0.13595 | -0.1962 | 121.3359 | -0.74437 | 121.4274 | 121.4409 | 0.10502 | -0.7595 | -0.5538 | 121.2485 | -0.84934 | 121.519 | 121.4158 | 0.16732 | -0.69122 | -0.72007 | 121.5563 | 121.5412 | 121.7469 | 121.4782 | -0.96486 | 121.4514 | 121.6095 | 121.5807 | 121.5321 | -1.0522
6302 | 122.493 | -121.4401 | 0.83771 | -0.010149 | -0.072119 | 0.037302 | 0.013486 | -0.015924 | 0.0083799 | -0.036779 | -0.021494 | -0.0084865 | 0.021299 | 0.058636 | -0.0016665 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.096516 | 0.3068 | -0.11342 | 0.074307 | 0.082776 | -0.028879 | 0.020409 | 0.1648 | 0.13595 | -0.1962 | 121.3267 | -0.72148 | 121.4229 | 121.4317 | 0.10502 | -0.74119 | -0.53091 | 121.2439 | -0.8173 | 121.5144 | 121.4112 | 0.16732 | -0.67291 | -0.70176 | 121.5563 | 121.5366 | 121.7469 | 121.4782 | -0.95113 | 121.4605 | 121.6049 | 121.5761 | 121.5229 | -1.0339
6303.7344 | 122.4152 | -121.4813 | 0.88348 | -0.01778 | -0.07276 | 0.037088 | 0.013058 | -0.016138 | 0.0081663 | -0.021518 | -0.021708 | -0.0080591 | 0.021085 | 0.058636 | -0.0012393 | -0.017266 | 0.028878 | -0.008409 | 0.11622 | 0.096516 | 0.3068 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.13595 | -0.20078 | 121.3725 | -0.76726 | 121.4641 | 121.4729 | 0.10044 | -0.78697 | -0.57669 | 121.2805 | -0.86765 | 121.5602 | 121.4479 | 0.16732 | -0.7141 | -0.74753 | 121.5975 | 121.5778 | 121.7881 | 121.5102 | -0.99233 | 121.4972 | 121.6507 | 121.6173 | 121.5641 | -1.0843
6305.4375 | 122.4609 | -121.4493 | 0.8194 | -0.01778 | -0.072333 | 0.037088 | 0.013486 | -0.016138 | 0.0083799 | -0.021518 | -0.021067 | -0.0080591 | 0.021085 | 0.05885 | -0.0016665 | -0.008109 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.083464 | 0.078197 | -0.033458 | 0.020409 | 0.16938 | 0.14511 | -0.20078 | 121.3359 | -0.70317 | 121.4412 | 121.4409 | 0.10502 | -0.72746 | -0.5126 | 121.2485 | -0.79899 | 121.5327 | 121.4158 | 0.16732 | -0.65002 | -0.67429 | 121.5655 | 121.5412 | 121.7561 | 121.4827 | -0.93282 | 121.4697 | 121.6187 | 121.5944 | 121.5275 | -1.0202
6307.1406 | 122.4518 | -121.4447 | 0.82398 | -0.0025182 | -0.072546 | 0.036874 | 0.013699 | -0.016779 | 0.0079525 | -0.021518 | -0.021494 | -0.0082729 | 0.021299 | 0.058636 | -0.0016665 | -0.017266 | 0.042614 | -0.012988 | 0.11622 | 0.10567 | 0.30222 | -0.10885 | 0.074307 | 0.082776 | -0.033458 | 0.006674 | 0.16938 | 0.13137 | -0.20536 | 121.3359 | -0.70775 | 121.4274 | 121.4317 | 0.095859 | -0.7183 | -0.52176 | 121.2393 | -0.8173 | 121.519 | 121.4112 | 0.1719 | -0.6546 | -0.6926 | 121.5609 | 121.5504 | 121.7469 | 121.4873 | -0.93282 | 121.4514 | 121.6141 | 121.5761 | 121.5275 | -1.0293
6308.8594 | 122.4197 | -121.4722 | 0.82855 | -0.010149 | -0.072546 | 0.036661 | 0.013272 | -0.016352 | 0.0083799 | -0.029148 | -0.02128 | -0.0080591 | 0.021512 | 0.058636 | -0.0016665 | -0.017266 | 0.028878 | -0.008409 | 0.11165 | 0.091937 | 0.30222 | -0.11342 | 0.069728 | 0.082776 | -0.038036 | 0.011252 | 0.1648 | 0.13595 | -0.20078 | 121.3587 | -0.7169 | 121.4549 | 121.4638 | 0.10502 | -0.73661 | -0.52633 | 121.2714 | -0.8173 | 121.5419 | 121.4341 | 0.16274 | -0.66375 | -0.6926 | 121.5838 | 121.5641 | 121.7744 | 121.501 | -0.94198 | 121.4834 | 121.637 | 121.6081 | 121.5549 | -1.0293
6310.6094 | 122.4289 | -121.4676 | 0.85144 | -0.010149 | -0.072333 | 0.037302 | 0.013272 | -0.016138 | 0.0081663 | -0.021518 | -0.021494 | -0.0078455 | 0.021085 | 0.058636 | -0.0018801 | -0.021844 | 0.033457 | -0.012988 | 0.11165 | 0.091937 | 0.29764 | -0.118 | 0.078886 | 0.082776 | -0.033458 | 0.011252 | 0.17396 | 0.13595 | -0.20536 | 121.3496 | -0.73979 | 121.4457 | 121.4546 | 0.10502 | -0.7595 | -0.5538 | 121.2622 | -0.84019 | 121.5465 | 121.4341 | 0.1719 | -0.67748 | -0.71549 | 121.5792 | 121.5595 | 121.7652 | 121.501 | -0.96944 | 121.4788 | 121.6415 | 121.6035 | 121.5504 | -1.0568
6312.2969 | 122.5296 | -121.4355 | 0.82398 | -0.025411 | -0.07276 | 0.036874 | 0.013272 | -0.016138 | 0.0083799 | -0.013887 | -0.02128 | -0.0082729 | 0.021085 | 0.058636 | -0.0014529 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.118 | 0.074307 | 0.082776 | -0.028879 | 0.011252 | 0.16938 | 0.13137 | -0.1962 | 121.3175 | -0.70775 | 121.4229 | 121.4271 | 0.10959 | -0.73204 | -0.51718 | 121.2393 | -0.81272 | 121.5099 | 121.4067 | 0.16732 | -0.6546 | -0.6926 | 121.5518 | 121.5275 | 121.7423 | 121.469 | -0.94198 | 121.4468 | 121.6049 | 121.5669 | 121.5183 | -1.0202
6314 | 122.5662 | -121.4218 | 0.80109 | -0.01778 | -0.072333 | 0.037088 | 0.013272 | -0.015711 | 0.0081663 | -0.013887 | -0.021067 | -0.0082729 | 0.021085 | 0.05885 | -0.0016665 | -0.021844 | 0.028878 | -0.012988 | 0.11165 | 0.087359 | 0.30222 | -0.10885 | 0.074307 | 0.078197 | -0.038036 | 0.015831 | 0.16938 | 0.13137 | -0.1962 | 121.313 | -0.68944 | 121.4 | 121.4088 | 0.095859 | -0.71373 | -0.49887 | 121.2256 | -0.78525 | 121.4961 | 121.3838 | 0.15816 | -0.63171 | -0.66971 | 121.5335 | 121.5092 | 121.724 | 121.4507 | -0.90993 | 121.4376 | 121.5912 | 121.5532 | 121.5 | -0.99729
6315.7031 | 122.4335 | -121.4722 | 0.81482 | -0.010149 | -0.072546 | 0.036661 | 0.013272 | -0.015924 | 0.0081663 | -0.021518 | -0.021494 | -0.0080591 | 0.021085 | 0.058422 | -0.0016665 | -0.017266 | 0.033457 | 0.000747 | 0.11622 | 0.091937 | 0.30222 | -0.10427 | 0.078886 | 0.087354 | -0.038036 | 0.011252 | 0.1648 | 0.12679 | -0.20078 | 121.3679 | -0.69859 | 121.4549 | 121.4729 | 0.10501 | -0.72288 | -0.5126 | 121.2714 | -0.80357 | 121.5511 | 121.4341 | 0.16274 | -0.65002 | -0.68802 | 121.5884 | 121.5641 | 121.7744 | 121.5056 | -0.91909 | 121.4834 | 121.637 | 121.599 | 121.5595 | -1.0156
6317.4062 | 122.3969 | -121.4493 | 0.84228 | -0.025411 | -0.072546 | 0.036661 | 0.013272 | -0.016138 | 0.0081663 | -0.021518 | -0.02128 | -0.0082729 | 0.021085 | 0.05885 | -0.0016665 | -0.012688 | 0.038035 | -0.003831 | 0.10707 | 0.091937 | 0.3068 | -0.10885 | 0.074307 | 0.082776 | -0.019721 | 0.020409 | 0.16022 | 0.14053 | -0.1962 | 121.3404 | -0.73522 | 121.4366 | 121.4454 | 0.10502 | -0.75035 | -0.53549 | 121.2531 | -0.82188 | 121.5236 | 121.4296 | 0.17648 | -0.68206 | -0.70175 | 121.5563 | 121.5412 | 121.7561 | 121.4873 | -0.95113 | 121.4697 | 121.6095 | 121.5898 | 121.5321 | -1.0385
6319.125 | 122.5525 | -121.4539 | 0.82398 | -0.01778 | -0.072546 | 0.036874 | 0.013272 | -0.016138 | 0.0083799 | -0.021518 | -0.02128 | -0.0080591 | 0.020871 | 0.05885 | -0.0018801 | -0.021844 | 0.038035 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.015831 | 0.16938 | 0.13595 | -0.1962 | 121.345 | -0.70775 | 121.432 | 121.4454 | 0.10044 | -0.73662 | -0.52176 | 121.2577 | -0.80814 | 121.5327 | 121.4204 | 0.16274 | -0.6546 | -0.68802 | 121.5701 | 121.5412 | 121.7561 | 121.4919 | -0.93282 | 121.4697 | 121.6232 | 121.5898 | 121.5412 | -1.0202
6320.8281 | 122.5433 | -121.4172 | 0.78278 | -0.025411 | -0.072974 | 0.037302 | 0.013272 | -0.016138 | 0.0079525 | -0.036779 | -0.021067 | -0.0080591 | 0.021085 | 0.058422 | -0.0016665 | -0.017266 | 0.033457 | -0.017566 | 0.11165 | 0.08278 | 0.30222 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.011252 | 0.16938 | 0.13137 | -0.20536 | 121.3084 | -0.67113 | 121.4 | 121.3997 | 0.091281 | -0.7 | -0.48056 | 121.2119 | -0.77152 | 121.4961 | 121.3838 | 0.1719 | -0.6134 | -0.6514 | 121.5289 | 121.5 | 121.7195 | 121.4507 | -0.89162 | 121.4285 | 121.5866 | 121.5486 | 121.5 | -0.98813
6322.5469 | 122.4564 | -121.4905 | 0.8194 | -0.01778 | -0.072546 | 0.036874 | 0.013272 | -0.016352 | 0.0079525 | -0.021518 | -0.021494 | -0.0078455 | 0.021085 | 0.059063 | -0.0018801 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | -0.11342 | 0.074307 | 0.082776 | -0.033458 | 0.011252 | 0.16938 | 0.14053 | -0.1962 | 121.3771 | -0.70317 | 121.4778 | 121.4821 | 0.10502 | -0.72746 | -0.51718 | 121.2943 | -0.80815 | 121.5648 | 121.457 | 0.16274 | -0.65002 | -0.67887 | 121.6067 | 121.5824 | 121.7927 | 121.5239 | -0.93282 | 121.5017 | 121.6599 | 121.631 | 121.5733 | -1.0156
6324.25 | 122.5662 | -121.4584 | 0.81024 | -0.010149 | -0.072546 | 0.037088 | 0.013272 | -0.016138 | 0.0079525 | -0.021518 | -0.02128 | -0.0082729 | 0.021299 | 0.058422 | -0.0018801 | -0.021844 | 0.033457 | -0.012988 | 0.10707 | 0.091937 | 0.30222 | -0.099689 | 0.078886 | 0.087354 | -0.038036 | 0.011252 | 0.1648 | 0.13595 | -0.20536 | 121.3587 | -0.70317 | 121.4366 | 121.4454 | 0.086701 | -0.7183 | -0.50802 | 121.2531 | -0.79899 | 121.5373 | 121.4204 | 0.16732 | -0.64544 | -0.67429 | 121.5655 | 121.5504 | 121.7607 | 121.4919 | -0.90993 | 121.4697 | 121.6232 | 121.5944 | 121.5458 | -1.0156
6325.9531 | 122.5342 | -121.4676 | 0.78278 | -0.0025182 | -0.072546 | 0.036874 | 0.013699 | -0.015924 | 0.0083799 | -0.036779 | -0.02128 | -0.0080591 | 0.020871 | 0.058636 | -0.0016665 | -0.017266 | 0.038035 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | -0.11342 | 0.078886 | 0.082776 | -0.038036 | 0.015831 | 0.16022 | 0.13137 | -0.20078 | 121.3542 | -0.67113 | 121.4503 | 121.4638 | 0.10959 | -0.69542 | -0.48056 | 121.2668 | -0.76694 | 121.5465 | 121.4296 | 0.16274 | -0.62255 | -0.6514 | 121.5792 | 121.5549 | 121.7698 | 121.5056 | -0.8962 | 121.4834 | 121.6278 | 121.599 | 121.5504 | -0.98356
6327.6562 | 122.58 | -121.4355 | 0.80109 | -0.01778 | -0.072333 | 0.037302 | 0.013272 | -0.016565 | 0.0085935 | -0.021518 | -0.021494 | -0.0078455 | 0.021512 | 0.05885 | -0.0018801 | -0.012688 | 0.033457 | -0.012988 | 0.1208 | 0.091937 | 0.30222 | -0.11342 | 0.074307 | 0.082776 | -0.042615 | 0.015831 | 0.16938 | 0.13137 | -0.19162 | 121.3221 | -0.68028 | 121.4229 | 121.4226 | 0.10044 | -0.70915 | -0.49887 | 121.2439 | -0.78525 | 121.5099 | 121.3929 | 0.14901 | -0.63171 | -0.66971 | 121.5564 | 121.5275 | 121.7378 | 121.469 | -0.91451 | 121.4514 | 121.6049 | 121.5669 | 121.5183 | -0.99271
6329.3906 | 122.5662 | -121.463 | 0.80109 | -0.0025182 | -0.072333 | 0.037516 | 0.013058 | -0.016138 | 0.0081663 | -0.013887 | -0.021067 | -0.0082729 | 0.021299 | 0.05885 | -0.0014529 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.087359 | 0.3068 | -0.11342 | 0.078886 | 0.078197 | -0.033458 | 0.011252 | 0.17396 | 0.12679 | -0.1962 | 121.3496 | -0.68486 | 121.4457 | 121.4546 | 0.10502 | -0.71373 | -0.49429 | 121.2668 | -0.78983 | 121.5419 | 121.4296 | 0.16274 | -0.62713 | -0.67429 | 121.5792 | 121.5504 | 121.7698 | 121.501 | -0.91451 | 121.4743 | 121.637 | 121.5898 | 121.5412 | -0.99729
6331.0938 | 122.5067 | -121.4584 | 0.81482 | -0.010149 | -0.072546 | 0.036874 | 0.013058 | -0.016352 | 0.0081663 | -0.013887 | -0.021067 | -0.0082729 | 0.021299 | 0.05885 | -0.0014529 | -0.017266 | 0.038035 | 0.000747 | 0.11622 | 0.091937 | 0.3068 | -0.118 | 0.083464 | 0.087354 | -0.038036 | 0.020409 | 0.1648 | 0.13595 | -0.19162 | 121.3404 | -0.69859 | 121.4412 | 121.4592 | 0.11875 | -0.72288 | -0.50802 | 121.2668 | -0.79441 | 121.5419 | 121.4204 | 0.15359 | -0.65002 | -0.67887 | 121.5747 | 121.5504 | 121.7652 | 121.4965 | -0.93282 | 121.4788 | 121.6232 | 121.5944 | 121.5458 | -1.0064
6332.7969 | 122.4243 | -121.4859 | 0.83771 | -0.010149 | -0.072546 | 0.037088 | 0.013272 | -0.016138 | 0.0081663 | -0.021518 | -0.021494 | -0.0082729 | 0.021085 | 0.05885 | -0.0016665 | -0.017266 | 0.033457 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | -0.118 | 0.069728 | 0.087354 | -0.033458 | 0.011252 | 0.17396 | 0.13595 | -0.20078 | 121.3679 | -0.72148 | 121.4686 | 121.4821 | 0.11417 | -0.75035 | -0.53549 | 121.2851 | -0.82646 | 121.5556 | 121.4524 | 0.16732 | -0.66375 | -0.70176 | 121.6021 | 121.5733 | 121.7881 | 121.5194 | -0.95571 | 121.4972 | 121.6599 | 121.6219 | 121.5733 | -1.0385
6334.5156 | 122.5571 | -121.4493 | 0.80109 | -0.010149 | -0.072333 | 0.037088 | 0.013699 | -0.016138 | 0.0081663 | -0.021518 | -0.020853 | -0.0080591 | 0.021512 | 0.058636 | -0.0016665 | -0.017266 | 0.038035 | -0.017566 | 0.11622 | 0.087359 | 0.3068 | -0.12258 | 0.074307 | 0.087354 | -0.033458 | 0.015831 | 0.16022 | 0.13595 | -0.1962 | 121.3267 | -0.68486 | 121.432 | 121.4317 | 0.10502 | -0.71373 | -0.49429 | 121.2531 | -0.78525 | 121.5236 | 121.4158 | 0.16274 | -0.64086 | -0.66513 | 121.5655 | 121.5366 | 121.7561 | 121.4873 | -0.92367 | 121.4651 | 121.6095 | 121.5852 | 121.5366 | -0.99729
6336.2188 | 122.4289 | -121.4813 | 0.81024 | -0.010149 | -0.07276 | 0.036874 | 0.013058 | -0.016138 | 0.0083799 | -0.013887 | -0.02128 | -0.0087001 | 0.021085 | 0.058636 | -0.0018801 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.096516 | 0.3068 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.16022 | 0.13595 | -0.1962 | 121.3725 | -0.69402 | 121.4641 | 121.4729 | 0.10044 | -0.71373 | -0.50345 | 121.2851 | -0.79441 | 121.5602 | 121.4479 | 0.16274 | -0.65002 | -0.67429 | 121.5975 | 121.5778 | 121.7881 | 121.5194 | -0.91909 | 121.4972 | 121.6415 | 121.6173 | 121.5641 | -1.0064
6337.9375 | 122.3969 | -121.4996 | 0.82855 | -0.010149 | -0.072974 | 0.037088 | 0.013058 | -0.016138 | 0.0079525 | -0.021518 | -0.021067 | -0.0080591 | 0.021299 | 0.058422 | -0.0016665 | -0.021844 | 0.038035 | -0.008409 | 0.11165 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.091933 | -0.028879 | 0.020409 | 0.1648 | 0.14053 | -0.20078 | 121.3862 | -0.7169 | 121.4778 | 121.4912 | 0.10502 | -0.73661 | -0.52176 | 121.2989 | -0.80814 | 121.5785 | 121.4708 | 0.1719 | -0.66375 | -0.68802 | 121.6113 | 121.5916 | 121.8064 | 121.5377 | -0.94198 | 121.52 | 121.6644 | 121.6402 | 121.5916 | -1.0293
6339.6562 | 122.5388 | -121.4767 | 0.7782 | -0.01778 | -0.072333 | 0.036874 | 0.013058 | -0.016138 | 0.0079525 | -0.029148 | -0.021067 | -0.0080591 | 0.021512 | 0.05885 | -0.0016665 | -0.017266 | 0.038035 | -0.003831 | 0.11622 | 0.091937 | 0.29764 | -0.118 | 0.074307 | 0.082776 | -0.038036 | 0.015831 | 0.16022 | 0.14053 | -0.20536 | 121.3587 | -0.66197 | 121.4595 | 121.4729 | 0.11417 | -0.68626 | -0.48056 | 121.2714 | -0.76237 | 121.5511 | 121.4387 | 0.16732 | -0.61798 | -0.63767 | 121.593 | 121.5687 | 121.7744 | 121.5148 | -0.8962 | 121.4926 | 121.637 | 121.6173 | 121.5595 | -0.98356
6341.3594 | 122.4747 | -121.5179 | 0.80566 | -0.010149 | -0.07276 | 0.037088 | 0.013486 | -0.016352 | 0.0083799 | -0.029148 | -0.021067 | -0.0084865 | 0.021085 | 0.058636 | -0.0020939 | -0.012688 | 0.038035 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.074307 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.13137 | -0.20078 | 121.4045 | -0.68944 | 121.5053 | 121.5095 | 0.10502 | -0.71373 | -0.49887 | 121.3172 | -0.78983 | 121.5923 | 121.4845 | 0.16732 | -0.63628 | -0.67429 | 121.6342 | 121.6099 | 121.8247 | 121.556 | -0.91909 | 121.5338 | 121.6873 | 121.6493 | 121.6007 | -1.0064
6343.0625 | 122.5845 | -121.4722 | 0.80109 | -0.010149 | -0.072546 | 0.037088 | 0.013058 | -0.015924 | 0.0079525 | -0.013887 | -0.021067 | -0.0080591 | 0.021085 | 0.059063 | -0.0016665 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.31137 | -0.10885 | 0.078886 | 0.082776 | -0.028879 | 0.011252 | 0.16938 | 0.13595 | -0.20536 | 121.3633 | -0.68486 | 121.4503 | 121.4638 | 0.10044 | -0.71373 | -0.48971 | 121.2668 | -0.78983 | 121.5511 | 121.4433 | 0.17648 | -0.63171 | -0.66513 | 121.5884 | 121.5595 | 121.7835 | 121.5056 | -0.90993 | 121.4834 | 121.6415 | 121.6081 | 121.5549 | -1.0064
6344.7656 | 122.5296 | -121.4722 | 0.78278 | -0.01778 | -0.072546 | 0.036874 | 0.013272 | -0.016138 | 0.0083799 | -0.021518 | -0.020853 | -0.0082729 | 0.021085 | 0.05885 | -0.0018801 | -0.012688 | 0.038035 | -0.003831 | 0.1208 | 0.091937 | 0.30222 | -0.10885 | 0.078886 | 0.078197 | -0.028879 | 0.011252 | 0.16022 | 0.13595 | -0.20078 | 121.3633 | -0.66197 | 121.4595 | 121.4683 | 0.10502 | -0.69084 | -0.48056 | 121.2714 | -0.77152 | 121.5511 | 121.4433 | 0.1719 | -0.62255 | -0.64682 | 121.593 | 121.5641 | 121.7744 | 121.5102 | -0.89162 | 121.4834 | 121.6324 | 121.6081 | 121.5504 | -0.98356
6346.5 | 122.5708 | -121.4767 | 0.80566 | -0.010149 | -0.07276 | 0.036874 | 0.013486 | -0.015924 | 0.0083799 | -0.029148 | -0.021067 | -0.0082729 | 0.021299 | 0.05885 | -0.0016665 | -0.021844 | 0.038035 | -0.012988 | 0.1208 | 0.096516 | 0.3068 | -0.10427 | 0.078886 | 0.082776 | -0.033458 | 0.011252 | 0.1648 | 0.13595 | -0.20078 | 121.3725 | -0.68486 | 121.4549 | 121.4638 | 0.09128 | -0.70915 | -0.49887 | 121.276 | -0.79441 | 121.5556 | 121.4433 | 0.16732 | -0.64086 | -0.66971 | 121.5976 | 121.5733 | 121.7835 | 121.5148 | -0.90993 | 121.488 | 121.6415 | 121.6127 | 121.5595 | -1.0064
6348.2188 | 122.4655 | -121.5042 | 0.8194 | -0.01778 | -0.072333 | 0.036874 | 0.013272 | -0.016352 | 0.0083799 | -0.021518 | -0.021067 | -0.0078455 | 0.021299 | 0.059063 | -0.0018801 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.29764 | -0.11342 | 0.078886 | 0.082776 | -0.038036 | 0.015831 | 0.1648 | 0.13595 | -0.20078 | 121.3908 | -0.70317 | 121.4824 | 121.4958 | 0.10502 | -0.73204 | -0.52176 | 121.3034 | -0.80357 | 121.5831 | 121.4662 | 0.16274 | -0.6546 | -0.68345 | 121.6204 | 121.5916 | 121.8018 | 121.5377 | -0.93282 | 121.52 | 121.669 | 121.6402 | 121.587 | -1.0202
6349.9219 | 122.5662 | -121.4722 | 0.80109 | -0.010149 | -0.072546 | 0.036874 | 0.013058 | -0.016352 | 0.0085935 | -0.021518 | -0.02128 | -0.0080591 | 0.021085 | 0.05885 | -0.0018801 | -0.017266 | 0.033457 | -0.012988 | 0.11165 | 0.087359 | 0.3068 | -0.11342 | 0.078886 | 0.078197 | -0.038036 | 0.011252 | 0.1648 | 0.13595 | -0.1962 | 121.3587 | -0.68944 | 121.4549 | 121.4592 | 0.10044 | -0.71373 | -0.49429 | 121.276 | -0.78983 | 121.5511 | 121.4341 | 0.15816 | -0.63629 | -0.66513 | 121.5838 | 121.5595 | 121.779 | 121.5056 | -0.91451 | 121.4834 | 121.637 | 121.6081 | 121.5504 | -0.99729
6351.6406 | 122.4884 | -121.5088 | 0.82398 | -0.010149 | -0.072546 | 0.037088 | 0.013272 | -0.016138 | 0.0081663 | -0.013887 | -0.021067 | -0.0080591 | 0.021299 | 0.05885 | -0.0016665 | -0.012688 | 0.033457 | -0.008409 | 0.11165 | 0.096516 | 0.30222 | -0.118 | 0.074307 | 0.087354 | -0.028879 | 0.011252 | 0.1648 | 0.14511 | -0.20078 | 121.3908 | -0.71233 | 121.4961 | 121.5004 | 0.10959 | -0.72746 | -0.52176 | 121.308 | -0.81272 | 121.5831 | 121.4799 | 0.1719 | -0.65918 | -0.67887 | 121.6204 | 121.6053 | 121.811 | 121.5422 | -0.94198 | 121.52 | 121.6736 | 121.6539 | 121.5961 | -1.0248
6353.3438 | 122.5662 | -121.4767 | 0.81482 | -0.010149 | -0.073401 | 0.037516 | 0.013486 | -0.016565 | 0.0077389 | -0.021518 | -0.021067 | -0.0078455 | 0.021085 | 0.05885 | -0.0014529 | -0.012688 | 0.038035 | -0.008409 | 0.1208 | 0.087359 | 0.30222 | -0.10427 | 0.074307 | 0.087354 | -0.033458 | 0.015831 | 0.1648 | 0.13137 | -0.20078 | 121.3725 | -0.69401 | 121.4641 | 121.4683 | 0.095859 | -0.72746 | -0.5126 | 121.276 | -0.79899 | 121.5511 | 121.4433 | 0.16732 | -0.65002 | -0.68345 | 121.5976 | 121.5641 | 121.779 | 121.5148 | -0.91909 | 121.4926 | 121.6415 | 121.6081 | 121.5641 | -1.0156
6355.0469 | 122.5433 | -121.4584 | 0.79651 | -0.010149 | -0.072546 | 0.037088 | 0.013486 | -0.016565 | 0.0081663 | -0.013887 | -0.021708 | -0.0082729 | 0.021512 | 0.05885 | -0.0016665 | -0.012688 | 0.042614 | -0.012988 | 0.11622 | 0.091937 | 0.29764 | -0.118 | 0.074307 | 0.082776 | -0.042615 | 0.011252 | 0.1648 | 0.13137 | -0.1962 | 121.3404 | -0.68028 | 121.4457 | 121.4454 | 0.10502 | -0.70457 | -0.49887 | 121.2622 | -0.78526 | 121.5327 | 121.4158 | 0.15359 | -0.63171 | -0.66514 | 121.5747 | 121.5504 | 121.7561 | 121.501 | -0.91451 | 121.4697 | 121.6232 | 121.5898 | 121.5412 | -0.99271
6356.7812 | 122.4518 | -121.5408 | 0.8194 | -0.010149 | -0.072333 | 0.036874 | 0.013058 | -0.015924 | 0.0083799 | -0.029148 | -0.021494 | -0.0082729 | 0.021299 | 0.059277 | -0.0018801 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.096516 | 0.3068 | -0.11342 | 0.074307 | 0.087354 | -0.028879 | 0.015831 | 0.1648 | 0.13137 | -0.20994 | 121.4274 | -0.70317 | 121.5236 | 121.5324 | 0.10502 | -0.72288 | -0.5126 | 121.3309 | -0.80357 | 121.6151 | 121.512 | 0.18106 | -0.6546 | -0.68802 | 121.6571 | 121.6373 | 121.8476 | 121.5789 | -0.93282 | 121.5567 | 121.7056 | 121.6722 | 121.6282 | -1.0293
6358.5312 | 122.58 | -121.4722 | 0.77362 | -0.0025182 | -0.072119 | 0.036661 | 0.013699 | -0.016352 | 0.0081663 | -0.013887 | -0.021067 | -0.0084865 | 0.021299 | 0.059277 | -0.0016665 | -0.021844 | 0.033457 | -0.022144 | 0.11622 | 0.091937 | 0.30222 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.015831 | 0.16022 | 0.13137 | -0.20078 | 121.3633 | -0.6574 | 121.4503 | 121.45 | 0.086703 | -0.68168 | -0.4714 | 121.2714 | -0.75779 | 121.5511 | 121.4387 | 0.16732 | -0.6134 | -0.64225 | 121.5884 | 121.5641 | 121.7744 | 121.5056 | -0.88247 | 121.488 | 121.6324 | 121.6035 | 121.5595 | -0.9744
6360.2344 | 122.4564 | -121.5317 | 0.81482 | -0.01778 | -0.072546 | 0.037516 | 0.013486 | -0.016138 | 0.0081663 | -0.021518 | -0.021708 | -0.0082729 | 0.021299 | 0.059063 | -0.0018801 | -0.021844 | 0.033457 | -0.003831 | 0.11165 | 0.091937 | 0.31137 | -0.118 | 0.078886 | 0.091933 | -0.042615 | 0.015831 | 0.16938 | 0.12679 | -0.19162 | 121.4137 | -0.70317 | 121.5098 | 121.5278 | 0.11417 | -0.72288 | -0.50344 | 121.3401 | -0.79899 | 121.6106 | 121.4891 | 0.14901 | -0.64544 | -0.68802 | 121.6433 | 121.6236 | 121.8431 | 121.5651 | -0.93282 | 121.5475 | 121.7011 | 121.6585 | 121.6236 | -1.0064
6361.9531 | 122.5845 | -121.4859 | 0.80109 | -0.010149 | -0.07276 | 0.037088 | 0.013486 | -0.016352 | 0.0081663 | -0.021518 | -0.021494 | -0.0080591 | 0.021299 | 0.059063 | -0.0018801 | -0.021844 | 0.028878 | -0.012988 | 0.11622 | 0.087359 | 0.30222 | -0.11342 | 0.074307 | 0.082776 | -0.038036 | 0.015831 | 0.16022 | 0.12679 | -0.1962 | 121.3725 | -0.68486 | 121.4641 | 121.4729 | 0.10044 | -0.71373 | -0.49887 | 121.2897 | -0.78525 | 121.5602 | 121.4479 | 0.15816 | -0.64086 | -0.67429 | 121.6021 | 121.5733 | 121.7881 | 121.5148 | -0.91451 | 121.5017 | 121.6461 | 121.6127 | 121.5687 | -0.99729
6363.6719 | 122.5067 | -121.5271 | 0.82398 | -0.0025182 | -0.07276 | 0.036661 | 0.013058 | -0.016138 | 0.0083799 | -0.013887 | -0.021494 | -0.0078455 | 0.021299 | 0.059277 | -0.0014529 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.096516 | 0.30222 | -0.10885 | 0.069728 | 0.082776 | -0.0243 | 0.011252 | 0.16938 | 0.13137 | -0.20078 | 121.4183 | -0.70775 | 121.5053 | 121.5187 | 0.10044 | -0.72746 | -0.52176 | 121.3263 | -0.81272 | 121.5968 | 121.5028 | 0.17648 | -0.6546 | -0.6926 | 121.6433 | 121.6236 | 121.8293 | 121.5606 | -0.93282 | 121.5384 | 121.6965 | 121.6585 | 121.6099 | -1.0248
6365.375 | 122.5433 | -121.5179 | 0.78735 | -0.025411 | -0.07276 | 0.037088 | 0.013486 | -0.016138 | 0.0083799 | -0.036779 | -0.02128 | -0.0082729 | 0.021085 | 0.05885 | -0.0016665 | -0.021844 | 0.028878 | -0.012988 | 0.1208 | 0.091937 | 0.3068 | -0.11342 | 0.083464 | 0.087354 | -0.038036 | 0.015831 | 0.15564 | 0.13595 | -0.1962 | 121.4045 | -0.66655 | 121.4961 | 121.505 | 0.10044 | -0.69542 | -0.48056 | 121.3217 | -0.77152 | 121.6014 | 121.4799 | 0.15816 | -0.63171 | -0.6514 | 121.6387 | 121.6099 | 121.8247 | 121.5468 | -0.90078 | 121.5338 | 121.6736 | 121.6539 | 121.6053 | -0.98355
6367.1094 | 122.5021 | -121.5225 | 0.80566 | -0.010149 | -0.07276 | 0.037088 | 0.013272 | -0.016138 | 0.0079525 | -0.021518 | -0.021494 | -0.0078455 | 0.020871 | 0.05885 | -0.0018801 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.31137 | -0.10885 | 0.074307 | 0.082776 | -0.033458 | 0.011252 | 0.1648 | 0.14053 | -0.20078 | 121.4137 | -0.68944 | 121.5098 | 121.5141 | 0.10044 | -0.71373 | -0.49429 | 121.3217 | -0.79441 | 121.5968 | 121.4891 | 0.16732 | -0.64086 | -0.66513 | 121.6387 | 121.6145 | 121.8339 | 121.556 | -0.91451 | 121.5338 | 121.6873 | 121.6631 | 121.6053 | -1.0064
6368.8125 | 122.4884 | -121.5317 | 0.81482 | -0.01778 | -0.07276 | 0.036874 | 0.013058 | -0.016352 | 0.0081663 | -0.021518 | -0.02128 | -0.0080591 | 0.021085 | 0.058636 | -0.0012393 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.10885 | 0.088043 | 0.087354 | -0.038036 | 0.015831 | 0.16022 | 0.13137 | -0.1962 | 121.4228 | -0.69859 | 121.519 | 121.5233 | 0.10044 | -0.72288 | -0.50802 | 121.3355 | -0.79899 | 121.6197 | 121.4936 | 0.15816 | -0.6546 | -0.68345 | 121.6479 | 121.6236 | 121.8385 | 121.5651 | -0.92367 | 121.5475 | 121.6919 | 121.663 | 121.619 | -1.011
6370.5625 | 122.4884 | -121.5408 | 0.82398 | -0.01778 | -0.072974 | 0.036661 | 0.013272 | -0.016138 | 0.0079525 | -0.021518 | -0.021067 | -0.0082729 | 0.021512 | 0.059063 | -0.0016665 | -0.012688 | 0.033457 | -0.003831 | 0.11622 | 0.096516 | 0.31137 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.13137 | -0.1962 | 121.4274 | -0.70775 | 121.5281 | 121.537 | 0.10959 | -0.72746 | -0.5126 | 121.3446 | -0.80814 | 121.6197 | 121.5074 | 0.16274 | -0.6546 | -0.6926 | 121.6571 | 121.6373 | 121.8522 | 121.5743 | -0.9374 | 121.5567 | 121.7102 | 121.6722 | 121.6236 | -1.0202
6372.2656 | 122.493 | -121.5454 | 0.81024 | -0.010149 | -0.072974 | 0.036874 | 0.012845 | -0.016138 | 0.0081663 | -0.036779 | -0.021067 | -0.0080591 | 0.021299 | 0.059277 | -0.0016665 | -0.012688 | 0.038035 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.1648 | 0.13137 | -0.1962 | 121.4366 | -0.69402 | 121.5327 | 121.537 | 0.10044 | -0.7183 | -0.50345 | 121.3492 | -0.79441 | 121.6243 | 121.512 | 0.16274 | -0.64544 | -0.67887 | 121.6616 | 121.6373 | 121.8522 | 121.5834 | -0.91909 | 121.5612 | 121.7102 | 121.6768 | 121.6282 | -1.0064
6373.9688 | 122.6028 | -121.4996 | 0.76446 | -0.010149 | -0.072333 | 0.036661 | 0.012845 | -0.016352 | 0.0081663 | -0.029148 | -0.02128 | -0.0082729 | 0.021299 | 0.05885 | -0.0016665 | -0.017266 | 0.047193 | -0.003831 | 0.11622 | 0.08278 | 0.30222 | -0.10427 | 0.078886 | 0.078197 | -0.033458 | 0.015831 | 0.1648 | 0.14053 | -0.20078 | 121.3954 | -0.64824 | 121.4824 | 121.4958 | 0.10044 | -0.68168 | -0.46225 | 121.2989 | -0.74863 | 121.5785 | 121.4662 | 0.16732 | -0.59966 | -0.62393 | 121.6159 | 121.5824 | 121.8019 | 121.5468 | -0.86873 | 121.5155 | 121.6644 | 121.6402 | 121.5778 | -0.96524
6375.6719 | 122.5891 | -121.4859 | 0.78735 | -0.01778 | -0.073187 | 0.036661 | 0.013272 | -0.016352 | 0.0085935 | -0.021518 | -0.02128 | -0.0078455 | 0.020871 | 0.05885 | -0.0016665 | -0.008109 | 0.033457 | -0.012988 | 0.11622 | 0.087359 | 0.31137 | -0.11342 | 0.078886 | 0.082776 | -0.038036 | 0.006674 | 0.16938 | 0.13137 | -0.20536 | 121.3725 | -0.67113 | 121.4778 | 121.4729 | 0.10044 | -0.7 | -0.47598 | 121.2805 | -0.78068 | 121.5648 | 121.4479 | 0.16732 | -0.61797 | -0.65598 | 121.6021 | 121.5733 | 121.7973 | 121.5194 | -0.90078 | 121.4926 | 121.6553 | 121.6173 | 121.5687 | -0.99271
6377.375 | 122.58 | -121.5042 | 0.78735 | -0.010149 | -0.072974 | 0.037088 | 0.013272 | -0.016352 | 0.0081663 | -0.021518 | -0.021067 | -0.0082729 | 0.021512 | 0.059063 | -0.0016665 | -0.012688 | 0.038035 | -0.008409 | 0.1208 | 0.096516 | 0.3068 | -0.10427 | 0.078886 | 0.091933 | -0.038036 | 0.015831 | 0.16938 | 0.13595 | -0.19162 | 121.3999 | -0.66655 | 121.4915 | 121.4958 | 0.095859 | -0.69084 | -0.48056 | 121.3126 | -0.77152 | 121.5831 | 121.4662 | 0.15359 | -0.61797 | -0.6514 | 121.625 | 121.6007 | 121.811 | 121.5422 | -0.89162 | 121.52 | 121.6736 | 121.6402 | 121.5961 | -0.97898
6379.125 | 122.493 | -121.5408 | 0.80109 | -0.010149 | -0.072974 | 0.036661 | 0.013058 | -0.016352 | 0.0079525 | -0.013887 | -0.021067 | -0.0080591 | 0.021085 | 0.059063 | -0.0020939 | -0.021844 | 0.028878 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | -0.11342 | 0.083464 | 0.078197 | -0.033458 | 0.006674 | 0.1648 | 0.14053 | -0.1962 | 121.4274 | -0.68486 | 121.519 | 121.5324 | 0.10502 | -0.70915 | -0.49887 | 121.3446 | -0.79441 | 121.6243 | 121.5074 | 0.16274 | -0.63629 | -0.66056 | 121.6571 | 121.6328 | 121.8431 | 121.5697 | -0.91451 | 121.5475 | 121.7056 | 121.6814 | 121.619 | -0.99729
6380.8281 | 122.5983 | -121.5042 | 0.7782 | -0.01778 | -0.07276 | 0.037088 | 0.013058 | -0.016138 | 0.0085935 | -0.036779 | -0.02128 | -0.0078455 | 0.021512 | 0.059063 | -0.0016665 | -0.021844 | 0.033457 | -0.008409 | 0.11165 | 0.091937 | 0.3068 | -0.118 | 0.069728 | 0.078197 | -0.033458 | 0.015831 | 0.16022 | 0.13137 | -0.19162 | 121.3862 | -0.66655 | 121.4824 | 121.4958 | 0.10959 | -0.68626 | -0.4714 | 121.3126 | -0.76237 | 121.5739 | 121.4708 | 0.15816 | -0.61798 | -0.64682 | 121.6159 | 121.5961 | 121.811 | 121.5377 | -0.8962 | 121.52 | 121.6644 | 121.6356 | 121.5824 | -0.96982
6382.5938 | 122.5754 | -121.5454 | 0.79193 | -0.010149 | -0.072974 | 0.037088 | 0.013272 | -0.016352 | 0.0081663 | -0.021518 | -0.021067 | -0.0080591 | 0.021085 | 0.059063 | -0.0016665 | -0.021844 | 0.033457 | -0.017566 | 0.11165 | 0.087359 | 0.3068 | -0.11342 | 0.06515 | 0.078197 | -0.038036 | 0.011252 | 0.15564 | 0.14053 | -0.1962 | 121.432 | -0.68028 | 121.5236 | 121.5278 | 0.095859 | -0.70457 | -0.48514 | 121.3492 | -0.78068 | 121.6106 | 121.5074 | 0.15816 | -0.63629 | -0.6514 | 121.6571 | 121.6328 | 121.8522 | 121.5789 | -0.90536 | 121.5567 | 121.7011 | 121.6859 | 121.6236 | -0.98813
6384.3438 | 122.5479 | -121.5363 | 0.78278 | -0.01778 | -0.072974 | 0.036874 | 0.013699 | -0.016138 | 0.0077389 | -0.021518 | -0.021494 | -0.0076319 | 0.021085 | 0.05885 | -0.0016665 | -0.017266 | 0.042614 | -0.008409 | 0.10707 | 0.087359 | 0.3068 | -0.118 | 0.074307 | 0.082776 | -0.033458 | 0.011252 | 0.16022 | 0.13595 | -0.20078 | 121.4183 | -0.67571 | 121.519 | 121.5278 | 0.10959 | -0.69542 | -0.47598 | 121.3355 | -0.77152 | 121.6106 | 121.5028 | 0.16732 | -0.62255 | -0.64682 | 121.6433 | 121.6236 | 121.8431 | 121.5789 | -0.90078 | 121.5475 | 121.6965 | 121.6722 | 121.619 | -0.98356
6386.0469 | 122.5845 | -121.4996 | 0.76904 | -0.010149 | -0.072974 | 0.036874 | 0.013058 | -0.016352 | 0.0081663 | -0.029148 | -0.02128 | -0.0078455 | 0.021085 | 0.059063 | -0.0014529 | -0.021844 | 0.033457 | -0.003831 | 0.11622 | 0.087359 | 0.3068 | -0.11342 | 0.078886 | 0.078197 | -0.038036 | 0.011252 | 0.17396 | 0.13137 | -0.20078 | 121.3862 | -0.65282 | 121.4778 | 121.4958 | 0.10959 | -0.68168 | -0.46225 | 121.2989 | -0.75779 | 121.5785 | 121.4616 | 0.16274 | -0.59509 | -0.63767 | 121.6159 | 121.587 | 121.8064 | 121.5331 | -0.88247 | 121.5109 | 121.6736 | 121.631 | 121.5778 | -0.96982
6387.7344 | 122.5845 | -121.5363 | 0.78278 | 0.0051128 | -0.073187 | 0.037088 | 0.013058 | -0.016138 | 0.0079525 | -0.013887 | -0.021067 | -0.0080591 | 0.021085 | 0.058636 | -0.0018801 | -0.008109 | 0.033457 | -0.008409 | 0.11165 | 0.096516 | 0.30222 | -0.10885 | 0.074307 | 0.082776 | -0.033458 | 0.020409 | 0.1648 | 0.13595 | -0.1962 | 121.4274 | -0.67113 | 121.5281 | 121.5278 | 0.10044 | -0.68626 | -0.48056 | 121.3401 | -0.76237 | 121.6106 | 121.5028 | 0.16274 | -0.61798 | -0.64682 | 121.6479 | 121.6328 | 121.8385 | 121.5697 | -0.89162 | 121.5567 | 121.7011 | 121.6722 | 121.619 | -0.97898
6389.4531 | 122.58 | -121.5179 | 0.76904 | -0.0025182 | -0.072974 | 0.036661 | 0.013272 | -0.016352 | 0.0079525 | -0.013887 | -0.021494 | -0.0082729 | 0.021085 | 0.059063 | -0.0016665 | -0.021844 | 0.038035 | -0.008409 | 0.12538 | 0.096516 | 0.31595 | -0.11342 | 0.074307 | 0.082776 | -0.033458 | 0.020409 | 0.1648 | 0.13595 | -0.20078 | 121.4045 | -0.64366 | 121.4961 | 121.5095 | 0.10502 | -0.67253 | -0.45309 | 121.3172 | -0.74863 | 121.5923 | 121.4845 | 0.16732 | -0.60424 | -0.63309 | 121.6433 | 121.6145 | 121.8339 | 121.556 | -0.88247 | 121.5384 | 121.6827 | 121.6539 | 121.6007 | -0.96982
6391.1719 | 122.5204 | -121.5454 | 0.78735 | -0.0025182 | -0.072974 | 0.036874 | 0.013058 | -0.016565 | 0.0083799 | -0.021518 | -0.02128 | -0.0082729 | 0.021512 | 0.059063 | -0.0016665 | -0.012688 | 0.033457 | -0.008409 | 0.10707 | 0.091937 | 0.30222 | -0.10885 | 0.088043 | 0.087354 | -0.033458 | 0.015831 | 0.1648 | 0.13137 | -0.20078 | 121.4366 | -0.68029 | 121.5327 | 121.537 | 0.10044 | -0.69542 | -0.48514 | 121.3446 | -0.77152 | 121.6335 | 121.512 | 0.16732 | -0.62255 | -0.65598 | 121.6525 | 121.6373 | 121.8476 | 121.5789 | -0.8962 | 121.5612 | 121.7102 | 121.6768 | 121.6328 | -0.98813
6392.875 | 122.5983 | -121.4905 | 0.7782 | -0.010149 | -0.072974 | 0.037088 | 0.013058 | -0.016352 | 0.0083799 | -0.029148 | -0.021494 | -0.0080591 | 0.021085 | 0.059063 | -0.0016665 | -0.012688 | 0.028878 | -0.012988 | 0.11165 | 0.087359 | 0.3068 | -0.10885 | 0.083464 | 0.078197 | -0.028879 | 0.015831 | 0.16022 | 0.13137 | -0.20536 | 121.3816 | -0.66655 | 121.4778 | 121.4775 | 0.095859 | -0.69084 | -0.4714 | 121.2851 | -0.76237 | 121.5739 | 121.4616 | 0.17648 | -0.61798 | -0.64682 | 121.6021 | 121.5778 | 121.7973 | 121.5194 | -0.88704 | 121.5063 | 121.6507 | 121.6219 | 121.5687 | -0.98356
6394.5938 | 122.5571 | -121.5225 | 0.79651 | -0.025411 | -0.073187 | 0.037088 | 0.013058 | -0.016565 | 0.0083799 | -0.013887 | -0.021067 | -0.0080591 | 0.021726 | 0.059063 | -0.0016665 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.08278 | 0.30222 | -0.11342 | 0.078886 | 0.087354 | -0.038036 | 0.020409 | 0.1648 | 0.13137 | -0.19162 | 121.4091 | -0.68028 | 121.5053 | 121.5141 | 0.10502 | -0.71373 | -0.49429 | 121.3309 | -0.7761 | 121.6014 | 121.4845 | 0.15359 | -0.63171 | -0.66514 | 121.6387 | 121.6053 | 121.8247 | 121.556 | -0.90993 | 121.5429 | 121.6873 | 121.6539 | 121.6099 | -0.98813
6396.2969 | 122.5983 | -121.5042 | 0.7782 | -0.01778 | -0.073401 | 0.037088 | 0.013486 | -0.016352 | 0.0079525 | -0.021518 | -0.02128 | -0.0082729 | 0.021085 | 0.059063 | -0.0016665 | -0.012688 | 0.038035 | -0.008409 | 0.1208 | 0.08278 | 0.30222 | -0.10885 | 0.069728 | 0.082776 | -0.038036 | 0.011252 | 0.1648 | 0.13137 | -0.20536 | 121.3954 | -0.65739 | 121.4915 | 121.4958 | 0.10044 | -0.69542 | -0.47598 | 121.2989 | -0.76695 | 121.5739 | 121.4662 | 0.16732 | -0.6134 | -0.64682 | 121.625 | 121.587 | 121.8064 | 121.5422 | -0.88704 | 121.5155 | 121.669 | 121.6356 | 121.587 | -0.98356
6398.0156 | 122.5983 | -121.5225 | 0.78735 | -0.010149 | -0.07276 | 0.037088 | 0.012845 | -0.016565 | 0.0083799 | -0.021518 | -0.02128 | -0.0084865 | 0.021085 | 0.059063 | -0.0016665 | -0.012688 | 0.033457 | -0.012988 | 0.11622 | 0.091937 | 0.30222 | -0.10885 | 0.078886 | 0.082776 | -0.033458 | 0.011252 | 0.15564 | 0.13595 | -0.20078 | 121.4137 | -0.67113 | 121.5098 | 121.5095 | 0.095859 | -0.69542 | -0.48514 | 121.3217 | -0.7761 | 121.6014 | 121.4891 | 0.16732 | -0.63171 | -0.6514 | 121.6387 | 121.6145 | 121.8247 | 121.556 | -0.8962 | 121.5338 | 121.6782 | 121.6585 | 121.6053 | -0.98813
6399.7188 | 122.5479 | -121.5271 | 0.7782 | -0.025411 | -0.073187 | 0.036874 | 0.013058 | -0.016352 | 0.0079525 | -0.029148 | -0.021067 | -0.0082729 | 0.020871 | 0.059063 | -0.0016665 | -0.017266 | 0.033457 | -0.012988 | 0.10707 | 0.091937 | 0.30222 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.011252 | 0.16022 | 0.13595 | -0.20078 | 121.4137 | -0.67113 | 121.5098 | 121.5141 | 0.10044 | -0.68626 | -0.47598 | 121.3263 | -0.76695 | 121.606 | 121.4936 | 0.16732 | -0.61798 | -0.64225 | 121.6342 | 121.619 | 121.8293 | 121.5606 | -0.89162 | 121.5384 | 121.6873 | 121.6631 | 121.6099 | -0.97898
6401.4375 | 122.6166 | -121.5225 | 0.77362 | -0.010149 | -0.072974 | 0.036874 | 0.013058 | -0.016352 | 0.0081663 | -0.036779 | -0.021067 | -0.0080591 | 0.021085 | 0.058636 | -0.0018801 | -0.017266 | 0.033457 | -0.008409 | 0.1208 | 0.087359 | 0.3068 | -0.10427 | 0.083464 | 0.082776 | -0.033458 | 0.011252 | 0.16022 | 0.13595 | -0.20078 | 121.4183 | -0.65282 | 121.5053 | 121.5141 | 0.095859 | -0.68626 | -0.46682 | 121.3217 | -0.76237 | 121.606 | 121.4891 | 0.16732 | -0.6134 | -0.63767 | 121.6433 | 121.6099 | 121.8293 | 121.556 | -0.87789 | 121.5338 | 121.6827 | 121.6585 | 121.6053 | -0.9744
6403.1406 | 122.5708 | -121.5179 | 0.78278 | -0.01778 | -0.072974 | 0.037302 | 0.013486 | -0.016352 | 0.0083799 | -0.029148 | -0.021067 | -0.0078455 | 0.021299 | 0.059063 | -0.0016665 | -0.021844 | 0.038035 | 0.000747 | 0.11165 | 0.091937 | 0.29306 | -0.118 | 0.078886 | 0.082776 | -0.038036 | 0.015831 | 0.1648 | 0.13137 | -0.19162 | 121.3999 | -0.67113 | 121.4961 | 121.5187 | 0.11875 | -0.69084 | -0.48972 | 121.3263 | -0.76694 | 121.5968 | 121.4799 | 0.15359 | -0.61798 | -0.6514 | 121.6296 | 121.6099 | 121.811 | 121.556 | -0.90078 | 121.5338 | 121.6827 | 121.6493 | 121.6007 | -0.9744
6404.8438 | 122.5571 | -121.5363 | 0.79193 | -0.025411 | -0.072974 | 0.037088 | 0.012845 | -0.016138 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.021085 | 0.059277 | -0.0016665 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.091937 | 0.30222 | -0.118 | 0.074307 | 0.087354 | -0.033458 | 0.011252 | 0.16022 | 0.13137 | -0.20536 | 121.4183 | -0.67571 | 121.519 | 121.5233 | 0.10502 | -0.69999 | -0.48971 | 121.3309 | -0.78068 | 121.6106 | 121.5028 | 0.1719 | -0.63171 | -0.66056 | 121.6525 | 121.6282 | 121.8385 | 121.5743 | -0.90994 | 121.5475 | 121.6965 | 121.6676 | 121.6236 | -0.99729
6406.6094 | 122.5479 | -121.5363 | 0.80109 | -0.010149 | -0.072974 | 0.036874 | 0.013272 | -0.016352 | 0.0081663 | -0.021518 | -0.02128 | -0.0080591 | 0.021085 | 0.059277 | -0.0016665 | -0.021844 | 0.028878 | -0.008409 | 0.11165 | 0.096516 | 0.31137 | -0.10885 | 0.078886 | 0.091933 | -0.033458 | 0.020409 | 0.16938 | 0.13595 | -0.20078 | 121.4274 | -0.68944 | 121.5144 | 121.5278 | 0.10044 | -0.70457 | -0.48971 | 121.3355 | -0.78068 | 121.6151 | 121.5028 | 0.16732 | -0.63171 | -0.66513 | 121.6479 | 121.6328 | 121.8476 | 121.5651 | -0.90993 | 121.5567 | 121.7056 | 121.6722 | 121.6282 | -1.0019
6408.3594 | 122.525 | -121.5591 | 0.80109 | -0.01778 | -0.073401 | 0.037088 | 0.013058 | -0.015924 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.021299 | 0.059063 | -0.0018801 | -0.021844 | 0.028878 | -0.012988 | 0.1208 | 0.087359 | 0.30222 | -0.10427 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.15564 | 0.12679 | -0.20536 | 121.4549 | -0.68028 | 121.5373 | 121.5462 | 0.09128 | -0.71373 | -0.49887 | 121.3538 | -0.78525 | 121.638 | 121.5257 | 0.1719 | -0.64544 | -0.67429 | 121.6799 | 121.6465 | 121.8614 | 121.588 | -0.90535 | 121.575 | 121.7148 | 121.6859 | 121.6419 | -1.0064
6410.0625 | 122.5662 | -121.5683 | 0.78735 | -0.010149 | -0.072974 | 0.036874 | 0.013058 | -0.016565 | 0.0081663 | -0.021518 | -0.021494 | -0.0078455 | 0.021299 | 0.059063 | -0.0014529 | -0.017266 | 0.033457 | -0.003831 | 0.1208 | 0.087359 | 0.31137 | -0.118 | 0.074307 | 0.082776 | -0.028879 | 0.015831 | 0.15564 | 0.13595 | -0.19162 | 121.4503 | -0.66655 | 121.551 | 121.5645 | 0.11417 | -0.7 | -0.47598 | 121.3767 | -0.77152 | 121.6426 | 121.5394 | 0.16274 | -0.63171 | -0.6514 | 121.6891 | 121.6557 | 121.8797 | 121.6018 | -0.90536 | 121.5841 | 121.7239 | 121.7043 | 121.6511 | -0.97898
6411.7656 | 122.5342 | -121.5454 | 0.79651 | -0.010149 | -0.072974 | 0.036874 | 0.013272 | -0.016352 | 0.0081663 | -0.013887 | -0.021067 | -0.0078455 | 0.021085 | 0.059063 | -0.0016665 | -0.017266 | 0.028878 | -0.003831 | 0.1208 | 0.091937 | 0.3068 | -0.10427 | 0.078886 | 0.091933 | -0.028879 | 0.015831 | 0.16022 | 0.14053 | -0.1962 | 121.4411 | -0.67571 | 121.5281 | 121.5416 | 0.10044 | -0.70457 | -0.48971 | 121.3492 | -0.78068 | 121.6243 | 121.5165 | 0.16732 | -0.63629 | -0.65598 | 121.6662 | 121.6373 | 121.8522 | 121.5743 | -0.90078 | 121.5612 | 121.7056 | 121.6859 | 121.6373 | -0.99271
6413.4688 | 122.5754 | -121.5179 | 0.78278 | -0.0025182 | -0.072974 | 0.037088 | 0.013058 | -0.016779 | 0.0081663 | -0.021518 | -0.021067 | -0.0080591 | 0.020658 | 0.059063 | -0.0014529 | -0.017266 | 0.033457 | -0.012988 | 0.11165 | 0.087359 | 0.3068 | -0.10885 | 0.074307 | 0.087354 | -0.038036 | 0.015831 | 0.16022 | 0.14053 | -0.20536 | 121.4091 | -0.67113 | 121.5007 | 121.505 | 0.095859 | -0.69542 | -0.47598 | 121.3126 | -0.76694 | 121.5923 | 121.4799 | 0.16732 | -0.62255 | -0.64225 | 121.6296 | 121.6053 | 121.8247 | 121.5514 | -0.89162 | 121.5338 | 121.6782 | 121.6585 | 121.6053 | -0.98813
6415.1719 | 122.4976 | -121.5591 | 0.8194 | -0.0025182 | -0.07276 | 0.036874 | 0.013486 | -0.016352 | 0.0079525 | -0.029148 | -0.02128 | -0.0080591 | 0.021085 | 0.059277 | -0.0014529 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.29764 | -0.10885 | 0.069728 | 0.087354 | -0.038036 | 0.015831 | 0.16022 | 0.13595 | -0.1962 | 121.4503 | -0.70317 | 121.5419 | 121.5507 | 0.10044 | -0.72746 | -0.52176 | 121.3629 | -0.80357 | 121.6289 | 121.5211 | 0.15816 | -0.65918 | -0.68345 | 121.6754 | 121.6511 | 121.8568 | 121.5926 | -0.92824 | 121.575 | 121.7194 | 121.6951 | 121.6465 | -1.0156
6416.875 | 122.5204 | -121.5775 | 0.81024 | -0.01778 | -0.073187 | 0.037088 | 0.013058 | -0.016352 | 0.0079525 | -0.029148 | -0.021494 | -0.0082729 | 0.021299 | 0.059277 | -0.0016665 | -0.017266 | 0.028878 | -0.008409 | 0.1208 | 0.1011 | 0.3068 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.006674 | 0.16938 | 0.13595 | -0.1962 | 121.4686 | -0.68944 | 121.5602 | 121.569 | 0.10044 | -0.70915 | -0.50345 | 121.3813 | -0.80357 | 121.6563 | 121.544 | 0.16274 | -0.64086 | -0.67429 | 121.6983 | 121.6785 | 121.8843 | 121.6063 | -0.91909 | 121.5841 | 121.7468 | 121.7134 | 121.6557 | -1.0064
6418.5938 | 122.6166 | -121.5225 | 0.78735 | -0.010149 | -0.073401 | 0.036874 | 0.013486 | -0.016352 | 0.0079525 | -0.021518 | -0.021067 | -0.0082729 | 0.021299 | 0.059063 | -0.0016665 | -0.017266 | 0.033457 | -0.017566 | 0.11622 | 0.091937 | 0.30222 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.011252 | 0.16938 | 0.12679 | -0.20078 | 121.4137 | -0.67113 | 121.5053 | 121.505 | 0.091281 | -0.69542 | -0.48514 | 121.3217 | -0.7761 | 121.6014 | 121.4891 | 0.16732 | -0.61797 | -0.66056 | 121.6387 | 121.6145 | 121.8247 | 121.556 | -0.8962 | 121.5338 | 121.6919 | 121.6493 | 121.6099 | -0.98813
6420.2969 | 122.6166 | -121.5179 | 0.76904 | -0.01778 | -0.072974 | 0.036874 | 0.013272 | -0.016565 | 0.0077389 | -0.0062567 | -0.021494 | -0.0080591 | 0.021085 | 0.059277 | -0.0020939 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.118 | 0.074307 | 0.082776 | -0.042615 | 0.006674 | 0.1648 | 0.13595 | -0.1962 | 121.3999 | -0.65282 | 121.5053 | 121.5095 | 0.10959 | -0.67711 | -0.46225 | 121.3217 | -0.76237 | 121.5923 | 121.4753 | 0.15359 | -0.60424 | -0.63309 | 121.6342 | 121.6099 | 121.8247 | 121.5514 | -0.88705 | 121.5246 | 121.6827 | 121.6539 | 121.6007 | -0.96524
6422 | 122.5342 | -121.5591 | 0.80566 | -0.01778 | -0.072974 | 0.036874 | 0.013272 | -0.016138 | 0.0079525 | -0.021518 | -0.021067 | -0.0080591 | 0.021085 | 0.059277 | -0.0016665 | -0.017266 | 0.038035 | -0.017566 | 0.1208 | 0.096516 | 0.3068 | -0.10885 | 0.083464 | 0.082776 | -0.042615 | 0.011252 | 0.1648 | 0.12679 | -0.20536 | 121.4503 | -0.68486 | 121.5419 | 121.5416 | 0.091281 | -0.70915 | -0.49887 | 121.3538 | -0.79441 | 121.6426 | 121.5165 | 0.16274 | -0.64086 | -0.67887 | 121.6799 | 121.6557 | 121.8659 | 121.5972 | -0.91451 | 121.5704 | 121.7239 | 121.6859 | 121.6419 | -1.011
6423.7031 | 122.6212 | -121.5454 | 0.76446 | 0.0051128 | -0.073401 | 0.036874 | 0.012845 | -0.016565 | 0.0081663 | -0.029148 | -0.02128 | -0.0084865 | 0.021085 | 0.059063 | -0.0020939 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.011252 | 0.16022 | 0.13595 | -0.20536 | 121.4366 | -0.64824 | 121.5281 | 121.537 | 0.10044 | -0.67253 | -0.46225 | 121.3401 | -0.75321 | 121.6243 | 121.5074 | 0.16732 | -0.60424 | -0.62851 | 121.6616 | 121.6373 | 121.8476 | 121.5789 | -0.87331 | 121.5567 | 121.7056 | 121.6814 | 121.6282 | -0.96982
6425.4062 | 122.493 | -121.55 | 0.82855 | -0.010149 | -0.073187 | 0.036874 | 0.013058 | -0.015924 | 0.0081663 | -0.029148 | -0.021494 | -0.0084865 | 0.021085 | 0.059277 | -0.0016665 | -0.008109 | 0.033457 | -0.017566 | 0.11165 | 0.096516 | 0.3068 | -0.10885 | 0.078886 | 0.082776 | -0.038036 | 0.020409 | 0.16022 | 0.13595 | -0.1962 | 121.4411 | -0.7169 | 121.5419 | 121.5324 | 0.091281 | -0.73204 | -0.52176 | 121.3538 | -0.80814 | 121.6289 | 121.512 | 0.15816 | -0.66833 | -0.6926 | 121.6616 | 121.6465 | 121.8568 | 121.5834 | -0.9374 | 121.5704 | 121.7102 | 121.6859 | 121.6328 | -1.0248
6427.1094 | 122.5388 | -121.5363 | 0.82398 | -0.01778 | -0.073187 | 0.037088 | 0.013058 | -0.016138 | 0.0079525 | -0.013887 | -0.021494 | -0.0082729 | 0.021299 | 0.059277 | -0.0014529 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | -0.11342 | 0.083464 | 0.082776 | -0.038036 | 0.020409 | 0.16938 | 0.13595 | -0.19162 | 121.4228 | -0.70775 | 121.5236 | 121.5278 | 0.10502 | -0.73204 | -0.52176 | 121.3446 | -0.80357 | 121.6197 | 121.4982 | 0.15359 | -0.6546 | -0.68802 | 121.6525 | 121.6282 | 121.8385 | 121.5697 | -0.9374 | 121.5567 | 121.7056 | 121.6722 | 121.619 | -1.0156
6428.8125 | 122.5616 | -121.5271 | 0.81024 | -0.01778 | -0.073615 | 0.036874 | 0.013272 | -0.016138 | 0.0081663 | -0.036779 | -0.021494 | -0.0080591 | 0.020871 | 0.059918 | -0.0018801 | -0.017266 | 0.042614 | -0.012988 | 0.11622 | 0.1011 | 0.30222 | -0.118 | 0.078886 | 0.082776 | -0.028879 | 0.011252 | 0.16022 | 0.13137 | -0.20536 | 121.4091 | -0.69402 | 121.5098 | 121.5141 | 0.10502 | -0.70915 | -0.50802 | 121.3217 | -0.79899 | 121.606 | 121.4982 | 0.17648 | -0.65002 | -0.67887 | 121.6433 | 121.6282 | 121.8293 | 121.5697 | -0.92825 | 121.5384 | 121.6873 | 121.6585 | 121.6099 | -1.0156
6430.5625 | 122.5433 | -121.5408 | 0.82855 | -0.010149 | -0.072974 | 0.037302 | 0.013272 | -0.016352 | 0.0079525 | -0.021518 | -0.021708 | -0.0082729 | 0.021299 | 0.059491 | -0.0018801 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.118 | 0.074307 | 0.091933 | -0.028879 | 0.006674 | 0.16022 | 0.12679 | -0.20536 | 121.4228 | -0.71233 | 121.5236 | 121.5324 | 0.10959 | -0.73661 | -0.52176 | 121.3355 | -0.82188 | 121.6151 | 121.512 | 0.17648 | -0.66833 | -0.70176 | 121.6571 | 121.6328 | 121.8476 | 121.5743 | -0.94656 | 121.5475 | 121.7011 | 121.6676 | 121.6328 | -1.0339
6432.2656 | 122.5708 | -121.5363 | 0.79651 | -0.01778 | -0.072974 | 0.036874 | 0.012845 | -0.016565 | 0.0081663 | -0.036779 | -0.020853 | -0.0078455 | 0.021085 | 0.059491 | -0.0018801 | -0.021844 | 0.033457 | -0.012988 | 0.11165 | 0.096516 | 0.30222 | -0.11342 | 0.083464 | 0.087354 | -0.033458 | 0.006674 | 0.1648 | 0.13595 | -0.1962 | 121.4228 | -0.68486 | 121.5144 | 121.5233 | 0.10044 | -0.69999 | -0.49429 | 121.3401 | -0.78984 | 121.6197 | 121.5028 | 0.16274 | -0.63171 | -0.66056 | 121.6479 | 121.6328 | 121.8385 | 121.5697 | -0.90993 | 121.5429 | 121.7011 | 121.6722 | 121.6236 | -0.99271
6433.9688 | 122.5845 | -121.5134 | 0.80566 | -0.01778 | -0.072974 | 0.037088 | 0.013058 | -0.016565 | 0.0081663 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059491 | -0.0012393 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | 0.087359 | 0.3068 | -0.11342 | 0.074307 | 0.087354 | -0.028879 | 0.011252 | 0.1648 | 0.13595 | -0.1962 | 121.3999 | -0.69402 | 121.4961 | 121.505 | 0.10502 | -0.71831 | -0.49887 | 121.3172 | -0.79441 | 121.5877 | 121.4845 | 0.16732 | -0.64086 | -0.66971 | 121.625 | 121.6007 | 121.8202 | 121.5468 | -0.91909 | 121.5246 | 121.6782 | 121.6493 | 121.6007 | -1.0019
6435.6875 | 122.5388 | -121.5271 | 0.82398 | -0.010149 | -0.073615 | 0.036874 | 0.013058 | -0.016352 | 0.0079525 | -0.021518 | -0.021067 | -0.0080591 | 0.021299 | 0.059063 | -0.0016665 | -0.021844 | 0.028878 | -0.012988 | 0.1208 | 0.091937 | 0.3068 | -0.118 | 0.088043 | 0.082776 | -0.038036 | 0.020409 | 0.16938 | 0.14053 | -0.20078 | 121.4091 | -0.70317 | 121.5053 | 121.5141 | 0.10502 | -0.73204 | -0.51718 | 121.3263 | -0.80357 | 121.6151 | 121.4891 | 0.16274 | -0.6546 | -0.68345 | 121.6479 | 121.619 | 121.8339 | 121.556 | -0.94198 | 121.5475 | 121.6965 | 121.6676 | 121.6099 | -1.0248
6437.3906 | 122.6303 | -121.5042 | 0.78735 | -0.010149 | -0.073187 | 0.036874 | 0.013272 | -0.016352 | 0.0081663 | -0.021518 | -0.02128 | -0.0082729 | 0.020871 | 0.059277 | -0.0016665 | -0.017266 | 0.028878 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | -0.118 | 0.078886 | 0.078197 | -0.038036 | 0.015831 | 0.16938 | 0.13595 | -0.1962 | 121.3862 | -0.67113 | 121.4869 | 121.4958 | 0.10959 | -0.69542 | -0.48514 | 121.308 | -0.77152 | 121.5831 | 121.4662 | 0.15816 | -0.61797 | -0.6514 | 121.6204 | 121.5961 | 121.8064 | 121.5331 | -0.90536 | 121.52 | 121.6736 | 121.6402 | 121.5824 | -0.98355
6439.1406 | 122.5021 | -121.5591 | 0.81482 | -0.01778 | -0.073401 | 0.036661 | 0.013486 | -0.016565 | 0.0081663 | -0.021518 | -0.02128 | -0.0078455 | 0.020871 | 0.059063 | -0.0018801 | -0.017266 | 0.033457 | -0.008409 | 0.1208 | 0.096516 | 0.31137 | -0.10427 | 0.083464 | 0.082776 | -0.028879 | 0.015831 | 0.1648 | 0.13137 | -0.1962 | 121.4549 | -0.69401 | 121.5419 | 121.5507 | 0.095859 | -0.7183 | -0.50344 | 121.3629 | -0.79899 | 121.6426 | 121.5303 | 0.16732 | -0.65002 | -0.68345 | 121.6799 | 121.6557 | 121.8705 | 121.5926 | -0.91909 | 121.575 | 121.7239 | 121.6905 | 121.6419 | -1.011
6440.8438 | 122.5067 | -121.5775 | 0.81482 | -0.010149 | -0.073187 | 0.036661 | 0.012631 | -0.016138 | 0.0081663 | -0.036779 | -0.02128 | -0.0082729 | 0.021085 | 0.059277 | -0.0018801 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.096516 | 0.3068 | -0.118 | 0.088043 | 0.082776 | -0.038036 | 0.006674 | 0.1648 | 0.14053 | -0.20078 | 121.4595 | -0.69859 | 121.5556 | 121.569 | 0.10959 | -0.7183 | -0.50802 | 121.3767 | -0.80815 | 121.6655 | 121.5394 | 0.16274 | -0.65002 | -0.67429 | 121.6937 | 121.674 | 121.8843 | 121.6109 | -0.93282 | 121.5841 | 121.7423 | 121.718 | 121.6602 | -1.0156
6442.5625 | 122.493 | -121.5729 | 0.82398 | -0.0025182 | -0.073187 | 0.036661 | 0.013058 | -0.016352 | 0.0081663 | -0.021518 | -0.021494 | -0.0078455 | 0.021085 | 0.059063 | -0.0014529 | -0.012688 | 0.033457 | -0.012988 | 0.11622 | 0.096516 | 0.30222 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.13137 | -0.20078 | 121.4595 | -0.70775 | 121.5602 | 121.5599 | 0.10044 | -0.72746 | -0.52176 | 121.3721 | -0.80814 | 121.6518 | 121.5394 | 0.16732 | -0.6546 | -0.6926 | 121.6891 | 121.6694 | 121.8751 | 121.6063 | -0.9374 | 121.5887 | 121.7423 | 121.7042 | 121.6557 | -1.0248
6444.2656 | 122.5067 | -121.5866 | 0.83771 | -0.010149 | -0.073187 | 0.036874 | 0.013058 | -0.016138 | 0.0083799 | -0.021518 | -0.02064 | -0.0080591 | 0.021299 | 0.059063 | -0.0018801 | -0.026423 | 0.033457 | -0.003831 | 0.11622 | 0.091937 | 0.31137 | -0.11342 | 0.074307 | 0.082776 | -0.028879 | 0.015831 | 0.1648 | 0.13595 | -0.20078 | 121.4732 | -0.72148 | 121.5602 | 121.5828 | 0.10959 | -0.74577 | -0.52633 | 121.3858 | -0.82188 | 121.6609 | 121.5577 | 0.1719 | -0.67291 | -0.70176 | 121.7028 | 121.6785 | 121.898 | 121.6201 | -0.95113 | 121.6024 | 121.7514 | 121.7226 | 121.6694 | -1.0385
6445.9844 | 122.6257 | -121.5225 | 0.79193 | -0.01778 | -0.073187 | 0.037088 | 0.013058 | -0.016138 | 0.0079525 | -0.029148 | -0.021494 | -0.0080591 | 0.020871 | 0.059277 | -0.0016665 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.096516 | 0.3068 | -0.11342 | 0.078886 | 0.087354 | -0.038036 | 0.011252 | 0.1648 | 0.13137 | -0.20078 | 121.4091 | -0.68028 | 121.5053 | 121.5187 | 0.10959 | -0.69542 | -0.48514 | 121.3217 | -0.78068 | 121.6014 | 121.4845 | 0.16274 | -0.62713 | -0.66056 | 121.6342 | 121.619 | 121.8293 | 121.556 | -0.90536 | 121.5338 | 121.6873 | 121.6539 | 121.6099 | -0.99271
6447.7031 | 122.6212 | -121.4996 | 0.79651 | -0.010149 | -0.073401 | 0.036874 | 0.013058 | -0.016352 | 0.0079525 | -0.029148 | -0.02128 | -0.0078455 | 0.020871 | 0.059491 | -0.0016665 | -0.021844 | 0.0243 | -0.008409 | 0.10707 | 0.091937 | 0.31137 | -0.118 | 0.078886 | 0.078197 | -0.033458 | 0.015831 | 0.1648 | 0.13137 | -0.1962 | 121.3816 | -0.68944 | 121.4778 | 121.4912 | 0.10959 | -0.70457 | -0.48514 | 121.3034 | -0.78068 | 121.5785 | 121.4662 | 0.16274 | -0.63171 | -0.66514 | 121.6067 | 121.5916 | 121.811 | 121.5239 | -0.91451 | 121.5155 | 121.6644 | 121.631 | 121.5778 | -0.99271
6449.4062 | 122.58 | -121.5363 | 0.80566 | -0.01778 | -0.073187 | 0.036874 | 0.013058 | -0.016565 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.021085 | 0.059277 | -0.0016665 | -0.026423 | 0.028878 | -0.003831 | 0.11622 | 0.096516 | 0.3068 | -0.10885 | 0.078886 | 0.087354 | -0.038036 | 0.020409 | 0.16938 | 0.13595 | -0.20994 | 121.4274 | -0.68944 | 121.5098 | 121.5324 | 0.10502 | -0.70915 | -0.49887 | 121.3263 | -0.78526 | 121.6151 | 121.4982 | 0.1719 | -0.63628 | -0.66971 | 121.6525 | 121.6328 | 121.8431 | 121.5651 | -0.91451 | 121.5567 | 121.7056 | 121.6722 | 121.6236 | -1.0156
6451.1094 | 122.644 | -121.4996 | 0.79651 | -0.010149 | -0.073401 | 0.036447 | 0.013272 | -0.016565 | 0.0083799 | -0.021518 | -0.02128 | -0.0080591 | 0.021299 | 0.059491 | -0.0018801 | -0.012688 | 0.028878 | -0.003831 | 0.1208 | 0.087359 | 0.31137 | -0.10885 | 0.074307 | 0.087354 | -0.033458 | 0.015831 | 0.1648 | 0.14053 | -0.20078 | 121.3908 | -0.67571 | 121.4869 | 121.4958 | 0.10502 | -0.70915 | -0.48514 | 121.2989 | -0.78068 | 121.5739 | 121.4662 | 0.16732 | -0.63171 | -0.65598 | 121.6204 | 121.587 | 121.811 | 121.5285 | -0.90536 | 121.5155 | 121.6644 | 121.6402 | 121.587 | -0.99729
6452.8125 | 122.5388 | -121.5729 | 0.84686 | -0.01778 | -0.073187 | 0.036661 | 0.012845 | -0.016352 | 0.0083799 | -0.021518 | -0.02128 | -0.0080591 | 0.021085 | 0.059277 | -0.0016665 | -0.017266 | 0.042614 | 0.000747 | 0.11622 | 0.096516 | 0.3068 | -0.10427 | 0.074307 | 0.087354 | -0.033458 | 0.011252 | 0.1648 | 0.13137 | -0.20078 | 121.4686 | -0.73064 | 121.5556 | 121.5736 | 0.10501 | -0.75035 | -0.54007 | 121.3721 | -0.83561 | 121.6472 | 121.5394 | 0.16732 | -0.68206 | -0.71549 | 121.6891 | 121.6694 | 121.8797 | 121.6155 | -0.95113 | 121.5841 | 121.7377 | 121.7042 | 121.6602 | -1.0476
6454.5312 | 122.5571 | -121.5729 | 0.79651 | -0.025411 | -0.073187 | 0.036874 | 0.012845 | -0.016352 | 0.0079525 | -0.021518 | -0.021067 | -0.0080591 | 0.021085 | 0.059491 | -0.0018801 | -0.017266 | 0.033457 | -0.003831 | 0.11165 | 0.087359 | 0.3068 | -0.10885 | 0.083464 | 0.091933 | -0.028879 | 0.011252 | 0.16938 | 0.13137 | -0.20994 | 121.464 | -0.68486 | 121.5556 | 121.569 | 0.10502 | -0.70915 | -0.48971 | 121.3629 | -0.78526 | 121.6563 | 121.544 | 0.18106 | -0.62713 | -0.66514 | 121.6845 | 121.6602 | 121.8797 | 121.6063 | -0.90536 | 121.5841 | 121.7423 | 121.7042 | 121.6648 | -1.0064
6456.2812 | 122.5204 | -121.5454 | 0.83771 | -0.010149 | -0.073615 | 0.036874 | 0.013058 | -0.016779 | 0.0079525 | -0.013887 | -0.02128 | -0.0078455 | 0.020658 | 0.059491 | -0.0016665 | -0.021844 | 0.0243 | -0.003831 | 0.11622 | 0.1011 | 0.31137 | -0.10885 | 0.083464 | 0.087354 | -0.033458 | 0.006674 | 0.16022 | 0.12679 | -0.20078 | 121.4366 | -0.72148 | 121.5236 | 121.5416 | 0.10502 | -0.73661 | -0.52633 | 121.3446 | -0.83103 | 121.6289 | 121.512 | 0.16732 | -0.67749 | -0.71091 | 121.6616 | 121.6465 | 121.8568 | 121.5697 | -0.94656 | 121.5521 | 121.7056 | 121.6722 | 121.6328 | -1.0385
6458.0469 | 122.5113 | -121.5775 | 0.83771 | -0.010149 | -0.072974 | 0.036874 | 0.012845 | -0.016565 | 0.0079525 | -0.0062567 | -0.021067 | -0.0082729 | 0.020871 | 0.059063 | -0.0016665 | -0.017266 | 0.033457 | -0.012988 | 0.11165 | 0.087359 | 0.3068 | -0.10427 | 0.078886 | 0.091933 | -0.028879 | 0.015831 | 0.16022 | 0.13137 | -0.20078 | 121.4732 | -0.72606 | 121.5602 | 121.5645 | 0.09128 | -0.75035 | -0.53091 | 121.3767 | -0.82188 | 121.6563 | 121.5486 | 0.1719 | -0.67749 | -0.70634 | 121.6891 | 121.6648 | 121.8843 | 121.6109 | -0.94198 | 121.5933 | 121.7377 | 121.7088 | 121.6694 | -1.0385
6459.75 | 122.644 | -121.5134 | 0.80109 | -0.010149 | -0.073187 | 0.037088 | 0.012845 | -0.016565 | 0.0081663 | -0.021518 | -0.021494 | -0.0080591 | 0.021299 | 0.059277 | -0.0020939 | -0.021844 | 0.033457 | -0.008409 | 0.1208 | 0.087359 | 0.30222 | -0.10885 | 0.083464 | 0.078197 | -0.033458 | 0.015831 | 0.1648 | 0.13137 | -0.20536 | 121.4045 | -0.68028 | 121.4915 | 121.505 | 0.10044 | -0.71373 | -0.49887 | 121.308 | -0.78525 | 121.5968 | 121.4799 | 0.1719 | -0.63629 | -0.66971 | 121.6342 | 121.6007 | 121.8156 | 121.5468 | -0.90993 | 121.5292 | 121.6782 | 121.6447 | 121.5916 | -1.0064
6461.4531 | 122.5113 | -121.5591 | 0.85144 | -0.0025182 | -0.073187 | 0.036874 | 0.013058 | -0.016565 | 0.0081663 | -0.0062567 | -0.021494 | -0.0080591 | 0.020658 | 0.059063 | -0.0016665 | -0.021844 | 0.0243 | -0.003831 | 0.11622 | 0.096516 | 0.3068 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.006674 | 0.15564 | 0.12679 | -0.20536 | 121.4457 | -0.73521 | 121.5373 | 121.5553 | 0.10959 | -0.75492 | -0.54464 | 121.3538 | -0.84477 | 121.638 | 121.5257 | 0.1719 | -0.6958 | -0.72465 | 121.6754 | 121.6557 | 121.8659 | 121.5834 | -0.96486 | 121.5658 | 121.7148 | 121.6859 | 121.6419 | -1.0568
6463.1562 | 122.6669 | -121.5271 | 0.80566 | -0.01778 | -0.073187 | 0.036874 | 0.013058 | -0.016565 | 0.0077389 | -0.021518 | -0.021494 | -0.0080591 | 0.021299 | 0.059277 | -0.0014529 | -0.017266 | 0.038035 | -0.008409 | 0.1208 | 0.091937 | 0.3068 | -0.11342 | 0.083464 | 0.087354 | -0.033458 | 0.006674 | 0.16938 | 0.13595 | -0.20078 | 121.4137 | -0.68486 | 121.5098 | 121.5187 | 0.10502 | -0.71373 | -0.49887 | 121.3263 | -0.79899 | 121.6106 | 121.4936 | 0.16732 | -0.63628 | -0.66971 | 121.6479 | 121.619 | 121.8339 | 121.5651 | -0.91909 | 121.5338 | 121.6965 | 121.6631 | 121.6145 | -1.0064
6464.8594 | 122.5891 | -121.5363 | 0.80566 | -0.01778 | -0.073187 | 0.036661 | 0.013058 | -0.016565 | 0.0083799 | -0.021518 | -0.021494 | -0.0078455 | 0.020444 | 0.059491 | -0.0020939 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.3068 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.16938 | 0.12679 | -0.20078 | 121.4228 | -0.68944 | 121.519 | 121.5278 | 0.10502 | -0.71831 | -0.49887 | 121.3355 | -0.78983 | 121.6151 | 121.5028 | 0.16732 | -0.63628 | -0.67887 | 121.6525 | 121.6236 | 121.8431 | 121.5697 | -0.91909 | 121.5521 | 121.7056 | 121.663 | 121.619 | -1.0064
6466.6094 | 122.5525 | -121.6095 | 0.79193 | -0.010149 | -0.073401 | 0.036874 | 0.012631 | -0.015924 | 0.0077389 | -0.029148 | -0.021067 | -0.0080591 | 0.020871 | 0.059277 | -0.0020939 | -0.021844 | 0.028878 | -0.008409 | 0.11165 | 0.096516 | 0.31137 | -0.10427 | 0.078886 | 0.082776 | -0.038036 | 0.015831 | 0.1648 | 0.13595 | -0.20536 | 121.5052 | -0.68028 | 121.5877 | 121.6011 | 0.095859 | -0.69542 | -0.48056 | 121.4041 | -0.7761 | 121.6884 | 121.5715 | 0.16732 | -0.62713 | -0.65598 | 121.7211 | 121.706 | 121.9209 | 121.6384 | -0.8962 | 121.6253 | 121.7743 | 121.7454 | 121.6923 | -0.99729
6468.2969 | 122.644 | -121.5775 | 0.75531 | -0.0025182 | -0.073615 | 0.037088 | 0.013272 | -0.016565 | 0.0077389 | -0.021518 | -0.021067 | -0.0084865 | 0.020871 | 0.059063 | -0.0016665 | -0.012688 | 0.033457 | -0.012988 | 0.11622 | 0.091937 | 0.3068 | -0.10885 | 0.078886 | 0.082776 | -0.028879 | 0.015831 | 0.16022 | 0.12679 | -0.20078 | 121.4686 | -0.63909 | 121.5648 | 121.5645 | 0.095859 | -0.66337 | -0.44851 | 121.3767 | -0.73948 | 121.6563 | 121.5486 | 0.1719 | -0.59509 | -0.62852 | 121.6937 | 121.6694 | 121.8843 | 121.6109 | -0.86416 | 121.5933 | 121.7377 | 121.7042 | 121.6602 | -0.95609
6470 | 122.5891 | -121.5958 | 0.75989 | -0.010149 | -0.073615 | 0.037302 | 0.013058 | -0.016352 | 0.0081663 | -0.013887 | -0.021067 | -0.0080591 | 0.020871 | 0.059063 | -0.0020939 | -0.008109 | 0.028878 | 0.000747 | 0.11622 | 0.091937 | 0.31137 | -0.10885 | 0.074307 | 0.087354 | -0.038036 | 0.015831 | 0.16022 | 0.13137 | -0.20536 | 121.4869 | -0.64366 | 121.5877 | 121.5965 | 0.10959 | -0.66795 | -0.44851 | 121.3904 | -0.74406 | 121.6701 | 121.5577 | 0.16732 | -0.59967 | -0.62852 | 121.712 | 121.6877 | 121.9071 | 121.6246 | -0.86874 | 121.6116 | 121.756 | 121.7271 | 121.6831 | -0.96525
6471.7188 | 122.525 | -121.6232 | 0.78278 | -0.01778 | -0.073187 | 0.036661 | 0.013058 | -0.016138 | 0.0081663 | -0.029148 | -0.021067 | -0.0084865 | 0.020871 | 0.059491 | -0.0020939 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.096516 | 0.31137 | -0.118 | 0.078886 | 0.082776 | -0.038036 | 0.011252 | 0.1648 | 0.12679 | -0.1962 | 121.5052 | -0.66655 | 121.6014 | 121.6148 | 0.10959 | -0.68626 | -0.4714 | 121.427 | -0.77152 | 121.7021 | 121.5852 | 0.15816 | -0.61798 | -0.65598 | 121.7395 | 121.7197 | 121.9346 | 121.6567 | -0.90078 | 121.6345 | 121.788 | 121.75 | 121.706 | -0.97898
6473.4219 | 122.5021 | -121.6278 | 0.78278 | -0.025411 | -0.072974 | 0.037088 | 0.013058 | -0.016779 | 0.0083799 | -0.021518 | -0.021494 | -0.0080591 | 0.020871 | 0.059277 | -0.0018801 | -0.017266 | 0.028878 | -0.012988 | 0.1208 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.078197 | -0.038036 | 0.006674 | 0.16022 | 0.12679 | -0.20078 | 121.5144 | -0.66197 | 121.6105 | 121.6148 | 0.10044 | -0.69084 | -0.47598 | 121.427 | -0.7761 | 121.7067 | 121.5898 | 0.16274 | -0.62255 | -0.65598 | 121.7486 | 121.7197 | 121.9346 | 121.6567 | -0.8962 | 121.6345 | 121.788 | 121.7546 | 121.706 | -0.98356
6475.125 | 122.5891 | -121.5866 | 0.77362 | -0.01778 | -0.073401 | 0.036874 | 0.013058 | -0.016565 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.021085 | 0.059491 | -0.0018801 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.087359 | 0.3068 | -0.10885 | 0.088043 | 0.078197 | -0.038036 | 0.015831 | 0.1648 | 0.13595 | -0.20994 | 121.4778 | -0.6574 | 121.5739 | 121.5782 | 0.10044 | -0.68626 | -0.46682 | 121.3767 | -0.75779 | 121.6747 | 121.5486 | 0.1719 | -0.60882 | -0.63767 | 121.7028 | 121.674 | 121.8934 | 121.6201 | -0.88247 | 121.6024 | 121.7514 | 121.7226 | 121.6648 | -0.98356
6476.8281 | 122.6166 | -121.5912 | 0.75989 | -0.025411 | -0.073187 | 0.036874 | 0.012631 | -0.016352 | 0.0081663 | -0.021518 | -0.021067 | -0.0078455 | 0.020871 | 0.059491 | -0.0018801 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.096516 | 0.31595 | -0.11342 | 0.083464 | 0.091933 | -0.038036 | 0.006674 | 0.16022 | 0.13595 | -0.20536 | 121.4778 | -0.64366 | 121.5739 | 121.5828 | 0.10502 | -0.66337 | -0.44394 | 121.3858 | -0.75321 | 121.6747 | 121.5532 | 0.16732 | -0.59967 | -0.62394 | 121.7074 | 121.6877 | 121.9071 | 121.6246 | -0.87331 | 121.5979 | 121.7514 | 121.7271 | 121.6831 | -0.96525
6478.5938 | 122.644 | -121.5866 | 0.74158 | -0.01778 | -0.073401 | 0.036874 | 0.013058 | -0.016352 | 0.0077389 | -0.029148 | -0.020853 | -0.0080591 | 0.020871 | 0.059277 | -0.0016665 | -0.012688 | 0.038035 | -0.012988 | 0.11622 | 0.091937 | 0.31137 | -0.10885 | 0.083464 | 0.082776 | -0.038036 | 0.015831 | 0.16022 | 0.13137 | -0.20536 | 121.4778 | -0.62535 | 121.5739 | 121.5736 | 0.095859 | -0.64964 | -0.4302 | 121.3813 | -0.72575 | 121.6701 | 121.5486 | 0.16732 | -0.58136 | -0.6102 | 121.7028 | 121.6785 | 121.898 | 121.6246 | -0.85042 | 121.6024 | 121.7468 | 121.718 | 121.6694 | -0.94694
6480.2969 | 122.612 | -121.5546 | 0.75989 | -0.01778 | -0.073615 | 0.036874 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.021067 | -0.0080591 | 0.020871 | 0.059491 | -0.0012393 | -0.017266 | 0.038035 | 0.000747 | 0.11622 | 0.087359 | 0.31137 | -0.10885 | 0.083464 | 0.087354 | -0.0243 | 0.011252 | 0.16022 | 0.13137 | -0.1962 | 121.4457 | -0.64366 | 121.5373 | 121.5553 | 0.10959 | -0.67253 | -0.44851 | 121.3584 | -0.74864 | 121.638 | 121.5303 | 0.1719 | -0.59967 | -0.62852 | 121.6708 | 121.6419 | 121.8659 | 121.5926 | -0.86874 | 121.5658 | 121.7148 | 121.6859 | 121.6419 | -0.95609
6482 | 122.5662 | -121.6095 | 0.75531 | -0.010149 | -0.073401 | 0.036661 | 0.013272 | -0.016352 | 0.0079525 | -0.013887 | -0.020853 | -0.0080591 | 0.020444 | 0.059491 | -0.0020939 | -0.017266 | 0.033457 | -0.012988 | 0.11622 | 0.091937 | 0.31137 | -0.118 | 0.083464 | 0.082776 | -0.033458 | 0.015831 | 0.1648 | 0.13137 | -0.1962 | 121.4915 | -0.63909 | 121.5922 | 121.5965 | 0.10502 | -0.66337 | -0.44394 | 121.4133 | -0.73948 | 121.693 | 121.576 | 0.16274 | -0.59051 | -0.62394 | 121.7257 | 121.7014 | 121.9209 | 121.643 | -0.87331 | 121.6253 | 121.7743 | 121.7409 | 121.6923 | -0.95151
6483.75 | 122.5754 | -121.6232 | 0.75989 | -0.010149 | -0.073615 | 0.036661 | 0.013058 | -0.016565 | 0.0083799 | -0.029148 | -0.021067 | -0.0080591 | 0.021085 | 0.059063 | -0.0018801 | -0.012688 | 0.033457 | -0.003831 | 0.11622 | 0.096516 | 0.3068 | -0.099689 | 0.074307 | 0.082776 | -0.042615 | 0.011252 | 0.1648 | 0.13137 | -0.20078 | 121.5235 | -0.64366 | 121.6105 | 121.6194 | 0.095858 | -0.66337 | -0.45309 | 121.4225 | -0.74864 | 121.6975 | 121.5806 | 0.15816 | -0.59509 | -0.62852 | 121.7395 | 121.7197 | 121.93 | 121.6567 | -0.85958 | 121.6345 | 121.788 | 121.7546 | 121.706 | -0.96067
6485.4531 | 122.5662 | -121.6049 | 0.75989 | -0.010149 | -0.073401 | 0.036874 | 0.013058 | -0.016138 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059277 | -0.0016665 | -0.017266 | 0.033457 | -0.003831 | 0.11622 | 0.096516 | 0.3068 | -0.10885 | 0.088043 | 0.082776 | -0.038036 | 0.011252 | 0.1648 | 0.13595 | -0.1962 | 121.4961 | -0.64366 | 121.5877 | 121.6011 | 0.10502 | -0.66337 | -0.45309 | 121.4087 | -0.74864 | 121.693 | 121.5669 | 0.15816 | -0.59509 | -0.62394 | 121.7211 | 121.7014 | 121.9117 | 121.6384 | -0.86874 | 121.6162 | 121.7697 | 121.7409 | 121.6877 | -0.95609
6487.1562 | 122.5296 | -121.6507 | 0.7782 | -0.01778 | -0.073401 | 0.036874 | 0.013272 | -0.016565 | 0.0083799 | -0.013887 | -0.020853 | -0.0082729 | 0.020871 | 0.059491 | -0.0016665 | -0.017266 | 0.033457 | -0.012988 | 0.1208 | 0.1011 | 0.31137 | -0.10885 | 0.083464 | 0.078197 | -0.033458 | 0.015831 | 0.16022 | 0.12679 | -0.20536 | 121.5418 | -0.65739 | 121.6334 | 121.6377 | 0.095859 | -0.6771 | -0.46682 | 121.4453 | -0.76237 | 121.7342 | 121.6172 | 0.1719 | -0.61798 | -0.6514 | 121.7715 | 121.7518 | 121.9621 | 121.6842 | -0.88704 | 121.6665 | 121.8109 | 121.7775 | 121.7289 | -0.98356
6488.8594 | 122.6395 | -121.6278 | 0.74158 | -0.025411 | -0.073187 | 0.037088 | 0.013058 | -0.016352 | 0.0079525 | -0.013887 | -0.02128 | -0.0084865 | 0.020871 | 0.059491 | -0.0018801 | -0.012688 | 0.038035 | 0.000747 | 0.11622 | 0.087359 | 0.31595 | -0.11342 | 0.083464 | 0.082776 | -0.033458 | 0.011252 | 0.1648 | 0.13595 | -0.20078 | 121.5144 | -0.62535 | 121.6151 | 121.6286 | 0.11417 | -0.65422 | -0.42562 | 121.427 | -0.73033 | 121.7113 | 121.5944 | 0.16732 | -0.57678 | -0.60562 | 121.744 | 121.7152 | 121.9438 | 121.6658 | -0.855 | 121.6391 | 121.7926 | 121.7638 | 121.7106 | -0.94236
6490.625 | 122.6395 | -121.5912 | 0.75073 | -0.010149 | -0.073187 | 0.036447 | 0.013058 | -0.016352 | 0.0081663 | -0.036779 | -0.02128 | -0.0080591 | 0.021085 | 0.059491 | -0.0014529 | -0.021844 | 0.038035 | -0.003831 | 0.11622 | 0.087359 | 0.31595 | -0.11342 | 0.078886 | 0.087354 | -0.038036 | 0.015831 | 0.16022 | 0.12222 | -0.20078 | 121.4778 | -0.63451 | 121.5693 | 121.5874 | 0.10959 | -0.66337 | -0.43478 | 121.3904 | -0.7349 | 121.6701 | 121.5532 | 0.16274 | -0.59051 | -0.62852 | 121.7074 | 121.6785 | 121.9071 | 121.6292 | -0.86416 | 121.607 | 121.7514 | 121.7134 | 121.6785 | -0.95151
6492.3281 | 122.5296 | -121.6507 | 0.75531 | -0.025411 | -0.073401 | 0.036661 | 0.012845 | -0.016352 | 0.0077389 | -0.021518 | -0.021067 | -0.0080591 | 0.021085 | 0.059277 | -0.0016665 | -0.012688 | 0.033457 | -0.017566 | 0.1208 | 0.096516 | 0.3068 | -0.10427 | 0.078886 | 0.087354 | -0.033458 | 0.002095 | 0.16022 | 0.13137 | -0.20078 | 121.5464 | -0.63451 | 121.638 | 121.6331 | 0.086702 | -0.65879 | -0.44851 | 121.4499 | -0.75322 | 121.7296 | 121.6172 | 0.16732 | -0.59509 | -0.62394 | 121.7715 | 121.7472 | 121.9575 | 121.6842 | -0.85958 | 121.6528 | 121.8109 | 121.7821 | 121.7381 | -0.95609
6494.0312 | 122.6578 | -121.6095 | 0.71869 | -0.01778 | -0.073401 | 0.036447 | 0.013272 | -0.016352 | 0.0079525 | -0.013887 | -0.021067 | -0.0078455 | 0.021085 | 0.059277 | -0.0016665 | -0.017266 | 0.033457 | -0.003831 | 0.1208 | 0.091937 | 0.31595 | -0.10427 | 0.078886 | 0.082776 | -0.038036 | 0.011252 | 0.1648 | 0.13137 | -0.20078 | 121.5052 | -0.59788 | 121.5922 | 121.6057 | 0.10044 | -0.62675 | -0.40274 | 121.4087 | -0.70744 | 121.6884 | 121.5715 | 0.16274 | -0.55389 | -0.58732 | 121.7303 | 121.7014 | 121.9254 | 121.643 | -0.82296 | 121.6207 | 121.7743 | 121.7409 | 121.6923 | -0.91947
6495.7344 | 122.6303 | -121.6187 | 0.73242 | -0.010149 | -0.073615 | 0.036661 | 0.013272 | -0.016138 | 0.0081663 | -0.036779 | -0.021067 | -0.0078455 | 0.021085 | 0.059491 | -0.0018801 | -0.012688 | 0.033457 | -0.012988 | 0.12538 | 0.091937 | 0.31137 | -0.10885 | 0.074307 | 0.078197 | -0.033458 | 0.011252 | 0.16022 | 0.13595 | -0.20078 | 121.5098 | -0.60704 | 121.606 | 121.6057 | 0.095859 | -0.64048 | -0.42105 | 121.4179 | -0.72117 | 121.693 | 121.5852 | 0.16732 | -0.5722 | -0.59647 | 121.744 | 121.7106 | 121.93 | 121.6521 | -0.84127 | 121.6299 | 121.7789 | 121.7546 | 121.6968 | -0.9332
6497.4375 | 122.5296 | -121.6461 | 0.76446 | -0.01778 | -0.073615 | 0.036447 | 0.012845 | -0.016352 | 0.0083799 | -0.029148 | -0.021494 | -0.0082729 | 0.020658 | 0.059491 | -0.0018801 | -0.021844 | 0.038035 | -0.012988 | 0.1208 | 0.096516 | 0.31137 | -0.11342 | 0.074307 | 0.082776 | -0.038036 | 0.011252 | 0.16938 | 0.13595 | -0.20078 | 121.5327 | -0.64366 | 121.6243 | 121.6331 | 0.10044 | -0.66795 | -0.45309 | 121.4453 | -0.75321 | 121.7204 | 121.6081 | 0.16274 | -0.59509 | -0.62851 | 121.7669 | 121.7426 | 121.9575 | 121.6842 | -0.87789 | 121.6574 | 121.8155 | 121.7821 | 121.7289 | -0.96524
6499.1875 | 122.5479 | -121.6324 | 0.77362 | -0.010149 | -0.073401 | 0.036874 | 0.013272 | -0.016352 | 0.0079525 | -0.021518 | -0.021494 | -0.0084865 | 0.020871 | 0.059491 | -0.0020939 | -0.012688 | 0.038035 | -0.017566 | 0.1208 | 0.091937 | 0.31137 | -0.11342 | 0.078886 | 0.087354 | -0.038036 | 0.011252 | 0.1648 | 0.13137 | -0.1962 | 121.519 | -0.65282 | 121.6197 | 121.6148 | 0.095859 | -0.68168 | -0.46225 | 121.4362 | -0.76237 | 121.7113 | 121.5943 | 0.15816 | -0.60882 | -0.64225 | 121.7532 | 121.7243 | 121.9438 | 121.6704 | -0.88705 | 121.6436 | 121.7972 | 121.7638 | 121.7197 | -0.96982
6500.8906 | 122.58 | -121.6553 | 0.75531 | -0.010149 | -0.073615 | 0.036874 | 0.013272 | -0.016138 | 0.0081663 | -0.029148 | -0.02128 | -0.0080591 | 0.020871 | 0.059491 | -0.0020939 | -0.017266 | 0.038035 | -0.008409 | 0.1208 | 0.091937 | 0.3068 | -0.10885 | 0.088043 | 0.091933 | -0.028879 | 0.011252 | 0.1648 | 0.13595 | -0.20078 | 121.5464 | -0.63451 | 121.638 | 121.6469 | 0.10044 | -0.66337 | -0.44851 | 121.4545 | -0.74406 | 121.7433 | 121.6264 | 0.1719 | -0.59051 | -0.61936 | 121.7761 | 121.7472 | 121.9621 | 121.6933 | -0.86416 | 121.6665 | 121.8201 | 121.7912 | 121.7472 | -0.95609
6502.6406 | 122.6715 | -121.6461 | 0.72327 | -0.010149 | -0.073401 | 0.036874 | 0.012845 | -0.016565 | 0.0081663 | -0.029148 | -0.02128 | -0.0080591 | 0.020871 | 0.059277 | -0.0018801 | -0.012688 | 0.042614 | -0.003831 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.011252 | 0.1648 | 0.13137 | -0.20078 | 121.5327 | -0.60704 | 121.6334 | 121.6423 | 0.10959 | -0.63133 | -0.41647 | 121.4453 | -0.71201 | 121.725 | 121.6127 | 0.16732 | -0.55847 | -0.59189 | 121.7623 | 121.7381 | 121.9529 | 121.6887 | -0.83669 | 121.6574 | 121.8109 | 121.7775 | 121.7335 | -0.92405
6504.3281 | 122.6532 | -121.637 | 0.72784 | -0.01778 | -0.073187 | 0.036874 | 0.013058 | -0.016352 | 0.0081663 | -0.021518 | -0.020853 | -0.0084865 | 0.021299 | 0.059277 | -0.0018801 | -0.021844 | 0.038035 | -0.012988 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.015831 | 0.16022 | 0.12222 | -0.19162 | 121.5235 | -0.61162 | 121.6151 | 121.624 | 0.10044 | -0.63591 | -0.42105 | 121.4453 | -0.71201 | 121.7158 | 121.6035 | 0.15816 | -0.56762 | -0.60563 | 121.7532 | 121.7289 | 121.9438 | 121.675 | -0.84127 | 121.6528 | 121.7972 | 121.7592 | 121.7197 | -0.91947
6506.0469 | 122.6212 | -121.6324 | 0.72327 | -0.01778 | -0.073401 | 0.037088 | 0.012845 | -0.016138 | 0.0079525 | -0.029148 | -0.02128 | -0.0084865 | 0.020871 | 0.059491 | -0.0018801 | -0.017266 | 0.038035 | -0.017566 | 0.12538 | 0.1011 | 0.31137 | -0.10427 | 0.074307 | 0.078197 | -0.038036 | 0.024988 | 0.17396 | 0.12679 | -0.20536 | 121.5281 | -0.59788 | 121.6151 | 121.6148 | 0.086702 | -0.62217 | -0.41189 | 121.427 | -0.69828 | 121.7067 | 121.5943 | 0.16732 | -0.54931 | -0.59647 | 121.7578 | 121.7335 | 121.9438 | 121.6704 | -0.82754 | 121.6574 | 121.8063 | 121.7592 | 121.7106 | -0.92863
6507.75 | 122.6349 | -121.6095 | 0.72327 | -0.010149 | -0.073615 | 0.036661 | 0.012631 | -0.016565 | 0.0077389 | -0.021518 | -0.02128 | -0.0082729 | 0.020658 | 0.059491 | -0.0018801 | -0.017266 | 0.042614 | -0.008409 | 0.1208 | 0.096516 | 0.3068 | -0.118 | 0.088043 | 0.082776 | -0.042615 | 0.011252 | 0.1648 | 0.13595 | -0.20078 | 121.4915 | -0.60246 | 121.5922 | 121.6011 | 0.10959 | -0.62675 | -0.41647 | 121.4087 | -0.71201 | 121.6975 | 121.5669 | 0.15816 | -0.55847 | -0.58732 | 121.7303 | 121.706 | 121.9163 | 121.6521 | -0.84127 | 121.6207 | 121.7743 | 121.7454 | 121.6923 | -0.92405
6509.4688 | 122.6486 | -121.6278 | 0.72784 | -0.010149 | -0.073828 | 0.036874 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.021067 | -0.0078455 | 0.021085 | 0.059491 | -0.0018801 | -0.012688 | 0.038035 | -0.012988 | 0.12538 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.082776 | -0.033458 | 0.006674 | 0.16938 | 0.13595 | -0.20078 | 121.5144 | -0.60246 | 121.6151 | 121.6148 | 0.10044 | -0.63591 | -0.42105 | 121.427 | -0.72117 | 121.7067 | 121.5944 | 0.16732 | -0.55846 | -0.59189 | 121.7532 | 121.7197 | 121.9346 | 121.6658 | -0.84127 | 121.6345 | 121.7972 | 121.7638 | 121.7106 | -0.92862
6511.1875 | 122.58 | -121.6507 | 0.75531 | -0.025411 | -0.073615 | 0.036874 | 0.012845 | -0.016565 | 0.0079525 | -0.029148 | -0.021067 | -0.0080591 | 0.021085 | 0.059277 | -0.0016665 | -0.017266 | 0.042614 | -0.008409 | 0.11622 | 0.091937 | 0.31595 | -0.118 | 0.078886 | 0.082776 | -0.0243 | 0.015831 | 0.16938 | 0.13595 | -0.20078 | 121.5327 | -0.63909 | 121.6334 | 121.6423 | 0.10959 | -0.66337 | -0.43936 | 121.4499 | -0.73948 | 121.7296 | 121.6264 | 0.17648 | -0.58593 | -0.61936 | 121.7669 | 121.7426 | 121.9666 | 121.6933 | -0.87331 | 121.6665 | 121.8201 | 121.7866 | 121.7335 | -0.95609
6512.8906 | 122.5388 | -121.669 | 0.75989 | -0.010149 | -0.073401 | 0.036661 | 0.013058 | -0.016352 | 0.0079525 | -0.021518 | -0.021067 | -0.0076319 | 0.021085 | 0.059063 | -0.0016665 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.083464 | 0.082776 | -0.042615 | 0.015831 | 0.16938 | 0.14053 | -0.1962 | 121.5556 | -0.64366 | 121.6517 | 121.6606 | 0.10502 | -0.66795 | -0.45309 | 121.4728 | -0.74406 | 121.7525 | 121.6264 | 0.15359 | -0.59051 | -0.61936 | 121.7852 | 121.7609 | 121.9758 | 121.707 | -0.87331 | 121.6848 | 121.8384 | 121.8095 | 121.7518 | -0.95609
6514.6406 | 122.5296 | -121.6782 | 0.75989 | -0.010149 | -0.073615 | 0.036874 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059277 | -0.0016665 | -0.021844 | 0.033457 | 0.000747 | 0.12538 | 0.096516 | 0.3068 | -0.12258 | 0.083464 | 0.082776 | -0.033458 | 0.006674 | 0.17396 | 0.13595 | -0.20536 | 121.5556 | -0.63451 | 121.6563 | 121.6789 | 0.12333 | -0.66337 | -0.45309 | 121.4728 | -0.75321 | 121.7616 | 121.6447 | 0.1719 | -0.58593 | -0.62394 | 121.8035 | 121.7747 | 121.985 | 121.7116 | -0.88247 | 121.6848 | 121.8521 | 121.8141 | 121.7609 | -0.96525
6516.3438 | 122.6395 | -121.6278 | 0.71869 | -0.010149 | -0.073401 | 0.037088 | 0.012845 | -0.016565 | 0.0083799 | -0.013887 | -0.020853 | -0.0082729 | 0.020871 | 0.059704 | -0.0016665 | -0.021844 | 0.033457 | -0.003831 | 0.1208 | 0.091937 | 0.3068 | -0.10885 | 0.083464 | 0.082776 | -0.038036 | 0.011252 | 0.1648 | 0.12679 | -0.20078 | 121.519 | -0.59788 | 121.606 | 121.624 | 0.10502 | -0.62675 | -0.41189 | 121.427 | -0.70744 | 121.7113 | 121.5898 | 0.16274 | -0.55389 | -0.5919 | 121.7486 | 121.7197 | 121.9346 | 121.6613 | -0.82754 | 121.6391 | 121.7926 | 121.7546 | 121.7106 | -0.91947
6518.0469 | 122.5388 | -121.6644 | 0.78735 | -0.010149 | -0.073401 | 0.036874 | 0.013272 | -0.016565 | 0.0081663 | -0.029148 | -0.02128 | -0.0078455 | 0.020658 | 0.059491 | -0.0016665 | -0.008109 | 0.033457 | -0.012988 | 0.11622 | 0.096516 | 0.3068 | -0.118 | 0.074307 | 0.091933 | -0.038036 | 0.006674 | 0.1648 | 0.14053 | -0.20536 | 121.5464 | -0.67113 | 121.6563 | 121.6514 | 0.10502 | -0.69084 | -0.48056 | 121.4591 | -0.78068 | 121.7387 | 121.6264 | 0.16732 | -0.62255 | -0.64682 | 121.7807 | 121.7609 | 121.9712 | 121.6979 | -0.90536 | 121.6711 | 121.8292 | 121.805 | 121.7564 | -0.99271
6519.7656 | 122.6212 | -121.6415 | 0.72784 | -0.010149 | -0.073828 | 0.036661 | 0.012845 | -0.016352 | 0.0081663 | -0.029148 | -0.02064 | -0.0080591 | 0.020658 | 0.059491 | -0.0018801 | -0.017266 | 0.033457 | -0.008409 | 0.11622 | 0.096516 | 0.29764 | -0.11342 | 0.078886 | 0.091933 | -0.033458 | 0.015831 | 0.16938 | 0.13137 | -0.1962 | 121.5281 | -0.61162 | 121.6243 | 121.6331 | 0.10502 | -0.63133 | -0.43021 | 121.4453 | -0.71201 | 121.7204 | 121.6081 | 0.16274 | -0.55846 | -0.59647 | 121.7578 | 121.7381 | 121.9392 | 121.675 | -0.84127 | 121.6574 | 121.8109 | 121.7729 | 121.7335 | -0.92404
6521.4688 | 122.5891 | -121.6827 | 0.74158 | -0.025411 | -0.073187 | 0.036447 | 0.012845 | -0.016352 | 0.0081663 | -0.029148 | -0.021067 | -0.0082729 | 0.020871 | 0.059704 | -0.0018801 | -0.012688 | 0.038035 | -0.008409 | 0.1208 | 0.091937 | 0.3068 | -0.10885 | 0.074307 | 0.087354 | -0.033458 | 0.015831 | 0.16938 | 0.13595 | -0.1962 | 121.5739 | -0.62077 | 121.6701 | 121.6743 | 0.10044 | -0.64964 | -0.43478 | 121.4865 | -0.72575 | 121.757 | 121.6493 | 0.16274 | -0.5722 | -0.60562 | 121.8035 | 121.7747 | 121.9895 | 121.7208 | -0.85042 | 121.6986 | 121.8521 | 121.8187 | 121.7701 | -0.93778
6523.1719 | 122.5388 | -121.6827 | 0.75989 | -0.01778 | -0.073615 | 0.036661 | 0.013058 | -0.016565 | 0.0081663 | -0.036779 | -0.02128 | -0.0076319 | 0.020871 | 0.059277 | -0.0018801 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.096516 | 0.3068 | -0.11342 | 0.083464 | 0.091933 | -0.028879 | 0.006674 | 0.16022 | 0.13137 | -0.20536 | 121.5693 | -0.64366 | 121.6701 | 121.6743 | 0.10502 | -0.66337 | -0.45309 | 121.4774 | -0.75321 | 121.7662 | 121.6539 | 0.17648 | -0.59967 | -0.62852 | 121.799 | 121.7793 | 121.9895 | 121.7162 | -0.87331 | 121.6894 | 121.843 | 121.8141 | 121.7747 | -0.96525
6524.9062 | 122.5754 | -121.6965 | 0.75531 | -0.010149 | -0.073401 | 0.037088 | 0.012845 | -0.016352 | 0.0083799 | -0.021518 | -0.021067 | -0.0082729 | 0.020871 | 0.059491 | -0.0018801 | -0.017266 | 0.038035 | -0.008409 | 0.11165 | 0.1011 | 0.31137 | -0.11342 | 0.078886 | 0.082776 | -0.028879 | 0.006674 | 0.1648 | 0.14053 | -0.20078 | 121.583 | -0.64366 | 121.6792 | 121.6881 | 0.10502 | -0.65421 | -0.44394 | 121.4957 | -0.74864 | 121.7754 | 121.6676 | 0.1719 | -0.59051 | -0.61478 | 121.8081 | 121.7976 | 122.0078 | 121.7345 | -0.86874 | 121.7031 | 121.8613 | 121.837 | 121.7792 | -0.95609
6526.6094 | 122.5616 | -121.6827 | 0.75531 | -0.01778 | -0.073615 | 0.036874 | 0.013058 | -0.016565 | 0.0079525 | -0.013887 | -0.021067 | -0.0080591 | 0.021085 | 0.059277 | -0.0018801 | -0.017266 | 0.042614 | -0.003831 | 0.1208 | 0.096516 | 0.31595 | -0.11342 | 0.078886 | 0.087354 | -0.033458 | 0.011252 | 0.1648 | 0.13137 | -0.20078 | 121.5693 | -0.63451 | 121.6655 | 121.6789 | 0.10959 | -0.65879 | -0.43936 | 121.482 | -0.74406 | 121.7616 | 121.6493 | 0.16732 | -0.59051 | -0.62394 | 121.8035 | 121.7793 | 121.9987 | 121.7254 | -0.86874 | 121.694 | 121.8475 | 121.8141 | 121.7701 | -0.95609
6528.3281 | 122.6395 | -121.6278 | 0.71869 | -0.010149 | -0.073187 | 0.036661 | 0.013272 | -0.016138 | 0.0077389 | -0.021518 | -0.021494 | -0.0080591 | 0.020658 | 0.059491 | -0.0018801 | -0.021844 | 0.038035 | -0.008409 | 0.1208 | 0.1011 | 0.3068 | -0.11342 | 0.083464 | 0.082776 | -0.028879 | 0.020409 | 0.17396 | 0.13137 | -0.20078 | 121.5144 | -0.59788 | 121.606 | 121.6194 | 0.10502 | -0.61759 | -0.41189 | 121.427 | -0.69828 | 121.7113 | 121.5989 | 0.1719 | -0.54473 | -0.58732 | 121.7486 | 121.7289 | 121.9346 | 121.6658 | -0.83211 | 121.6482 | 121.8018 | 121.7592 | 121.7106 | -0.91947
6530.0781 | 122.5342 | -121.6461 | 0.74616 | -0.01778 | -0.073401 | 0.036661 | 0.013058 | -0.016138 | 0.0079525 | -0.013887 | -0.021067 | -0.0082729 | 0.021085 | 0.059277 | -0.0018801 | -0.017266 | 0.042614 | -0.003831 | 0.1208 | 0.091937 | 0.30222 | -0.118 | 0.078886 | 0.087354 | -0.038036 | 0.006674 | 0.16938 | 0.13137 | -0.1962 | 121.5281 | -0.62535 | 121.6289 | 121.6423 | 0.11417 | -0.65422 | -0.44394 | 121.4499 | -0.73948 | 121.725 | 121.6081 | 0.15816 | -0.57678 | -0.61478 | 121.7669 | 121.7381 | 121.9483 | 121.6887 | -0.86416 | 121.6528 | 121.8155 | 121.7775 | 121.7335 | -0.94236
6531.7812 | 122.5662 | -121.7056 | 0.75073 | -0.010149 | -0.073615 | 0.036874 | 0.013058 | -0.016352 | 0.0079525 | -0.0062567 | -0.02128 | -0.0082729 | 0.020658 | 0.059277 | -0.0018801 | -0.017266 | 0.042614 | -0.012988 | 0.12538 | 0.10567 | 0.31595 | -0.11342 | 0.078886 | 0.087354 | -0.038036 | 0.011252 | 0.15564 | 0.12679 | -0.1962 | 121.5922 | -0.62535 | 121.6884 | 121.6926 | 0.10044 | -0.64506 | -0.43478 | 121.5094 | -0.73948 | 121.7845 | 121.6676 | 0.15816 | -0.59509 | -0.62394 | 121.831 | 121.8113 | 122.0216 | 121.7482 | -0.86416 | 121.7169 | 121.8613 | 121.8324 | 121.793 | -0.94693
6533.5469 | 122.6532 | -121.6507 | 0.70038 | -0.010149 | -0.073615 | 0.036874 | 0.013058 | -0.016779 | 0.0081663 | -0.021518 | -0.02128 | -0.0078455 | 0.021085 | 0.059491 | -0.0016665 | -0.017266 | 0.042614 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | -0.118 | 0.078886 | 0.091933 | -0.033458 | 0.015831 | 0.1648 | 0.13595 | -0.20078 | 121.5327 | -0.58415 | 121.6334 | 121.6423 | 0.10959 | -0.60844 | -0.39358 | 121.4499 | -0.68455 | 121.7296 | 121.6172 | 0.16732 | -0.53558 | -0.56443 | 121.7669 | 121.7426 | 121.9575 | 121.6933 | -0.81838 | 121.6665 | 121.8155 | 121.7866 | 121.7426 | -0.90116
6535.2969 | 122.6761 | -121.6278 | 0.70953 | -0.0025182 | -0.073615 | 0.036661 | 0.012845 | -0.016352 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.020871 | 0.059491 | -0.0018801 | -0.021844 | 0.038035 | -0.008409 | 0.1208 | 0.11025 | 0.31137 | -0.11342 | 0.078886 | 0.078197 | -0.038036 | 0.015831 | 0.1648 | 0.12679 | -0.19162 | 121.5144 | -0.58873 | 121.606 | 121.6194 | 0.10502 | -0.59928 | -0.39816 | 121.4362 | -0.6937 | 121.7067 | 121.5898 | 0.15359 | -0.54473 | -0.58274 | 121.7486 | 121.7381 | 121.9392 | 121.6658 | -0.82296 | 121.6436 | 121.7926 | 121.7546 | 121.706 | -0.90116
6537.0312 | 122.6669 | -121.6507 | 0.69122 | -0.010149 | -0.073615 | 0.036661 | 0.012845 | -0.016352 | 0.0079525 | -0.021518 | -0.02128 | -0.0078455 | 0.021085 | 0.059491 | -0.0018801 | -0.008109 | 0.038035 | -0.008409 | 0.12538 | 0.091937 | 0.31137 | -0.10885 | 0.078886 | 0.087354 | -0.033458 | 0.015831 | 0.1648 | 0.13137 | -0.1962 | 121.5418 | -0.56584 | 121.6426 | 121.6423 | 0.10044 | -0.59929 | -0.37985 | 121.4545 | -0.67539 | 121.7296 | 121.6172 | 0.16274 | -0.52642 | -0.55985 | 121.7761 | 121.7426 | 121.9621 | 121.6887 | -0.80007 | 121.6665 | 121.8155 | 121.7821 | 121.7381 | -0.88742
6538.7344 | 122.5845 | -121.6919 | 0.75531 | -0.01778 | -0.073401 | 0.036661 | 0.013058 | -0.016779 | 0.0083799 | -0.021518 | -0.021067 | -0.0080591 | 0.020871 | 0.059277 | -0.0016665 | -0.017266 | 0.042614 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | -0.118 | 0.074307 | 0.082776 | -0.038036 | 0.015831 | 0.15564 | 0.12679 | -0.20078 | 121.5739 | -0.63909 | 121.6746 | 121.6835 | 0.10959 | -0.66337 | -0.45309 | 121.4911 | -0.73948 | 121.7662 | 121.6539 | 0.16274 | -0.59967 | -0.62852 | 121.8081 | 121.7838 | 121.9941 | 121.7345 | -0.87331 | 121.7077 | 121.8475 | 121.8187 | 121.7747 | -0.95609
6540.4688 | 122.6578 | -121.6507 | 0.72784 | -0.01778 | -0.073615 | 0.037088 | 0.013058 | -0.016565 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059277 | -0.0014529 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.091937 | 0.31137 | -0.118 | 0.083464 | 0.082776 | -0.033458 | 0.006674 | 0.16022 | 0.12679 | -0.20078 | 121.5327 | -0.61162 | 121.6334 | 121.6423 | 0.10959 | -0.63591 | -0.41647 | 121.4499 | -0.72117 | 121.7342 | 121.6172 | 0.16732 | -0.56762 | -0.60105 | 121.7669 | 121.7426 | 121.9621 | 121.6887 | -0.84585 | 121.6574 | 121.8109 | 121.7775 | 121.7335 | -0.92862
6542.1719 | 122.7081 | -121.6415 | 0.73242 | -0.01778 | -0.073401 | 0.036661 | 0.013058 | -0.016565 | 0.0079525 | -0.021518 | -0.021067 | -0.0080591 | 0.020658 | 0.059491 | -0.0014529 | -0.008109 | 0.033457 | -0.012988 | 0.1208 | 0.1011 | 0.30222 | -0.11342 | 0.074307 | 0.082776 | -0.038036 | 0.015831 | 0.16022 | 0.13595 | -0.20078 | 121.5281 | -0.61162 | 121.6334 | 121.6286 | 0.10044 | -0.63133 | -0.43021 | 121.4408 | -0.71659 | 121.7158 | 121.6035 | 0.16274 | -0.5722 | -0.59647 | 121.7623 | 121.7426 | 121.9438 | 121.675 | -0.84585 | 121.6574 | 121.8018 | 121.7775 | 121.7243 | -0.9332
6543.875 | 122.6715 | -121.6507 | 0.70038 | -0.01778 | -0.073615 | 0.036661 | 0.012845 | -0.016779 | 0.0079525 | -0.021518 | -0.021067 | -0.0078455 | 0.020444 | 0.059704 | -0.0016665 | -0.017266 | 0.033457 | -0.012988 | 0.1208 | 0.096516 | 0.31595 | -0.11342 | 0.083464 | 0.087354 | -0.033458 | 0.006674 | 0.15564 | 0.13595 | -0.20078 | 121.5373 | -0.57957 | 121.6334 | 121.6377 | 0.10044 | -0.60386 | -0.38442 | 121.4499 | -0.6937 | 121.7342 | 121.6172 | 0.16732 | -0.54473 | -0.56443 | 121.7715 | 121.7472 | 121.9666 | 121.6842 | -0.8138 | 121.6574 | 121.8063 | 121.7866 | 121.7381 | -0.90116
6545.5781 | 122.5525 | -121.7102 | 0.74158 | -0.010149 | -0.073615 | 0.036447 | 0.013058 | -0.016565 | 0.0079525 | -0.021518 | -0.02128 | -0.0082729 | 0.020871 | 0.059277 | -0.0018801 | -0.012688 | 0.028878 | -0.012988 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.073618 | -0.038036 | 0.011252 | 0.16022 | 0.13595 | -0.1962 | 121.5968 | -0.62535 | 121.6975 | 121.6972 | 0.10044 | -0.64964 | -0.43478 | 121.514 | -0.73033 | 121.7891 | 121.6722 | 0.15816 | -0.58136 | -0.60562 | 121.8264 | 121.8021 | 122.017 | 121.7391 | -0.855 | 121.7215 | 121.8704 | 121.8462 | 121.7838 | -0.93778
6547.2812 | 122.5616 | -121.6965 | 0.72784 | -0.01778 | -0.073828 | 0.036874 | 0.012845 | -0.016565 | 0.0081663 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059491 | -0.0020939 | -0.012688 | 0.042614 | -0.017566 | 0.1208 | 0.1011 | 0.3068 | -0.10885 | 0.074307 | 0.078197 | -0.038036 | 0.011252 | 0.16022 | 0.13595 | -0.20536 | 121.5876 | -0.60704 | 121.6838 | 121.6789 | 0.091281 | -0.62675 | -0.42105 | 121.4911 | -0.71659 | 121.7708 | 121.6584 | 0.16732 | -0.56762 | -0.59189 | 121.8173 | 121.7976 | 122.0033 | 121.7391 | -0.83669 | 121.7077 | 121.8567 | 121.8324 | 121.7747 | -0.9332
6548.9844 | 122.58 | -121.701 | 0.72327 | -0.010149 | -0.073828 | 0.036447 | 0.013058 | -0.016352 | 0.0081663 | -0.021518 | -0.020853 | -0.0080591 | 0.020871 | 0.059491 | -0.0016665 | -0.012688 | 0.042614 | -0.017566 | 0.11165 | 0.091937 | 0.3068 | -0.10885 | 0.074307 | 0.078197 | -0.038036 | 0.011252 | 0.1648 | 0.13595 | -0.20078 | 121.5922 | -0.61162 | 121.6884 | 121.6835 | 0.091281 | -0.63133 | -0.41647 | 121.5003 | -0.71201 | 121.7754 | 121.663 | 0.16274 | -0.55847 | -0.58732 | 121.8127 | 121.793 | 122.0078 | 121.7437 | -0.83211 | 121.7123 | 121.8658 | 121.837 | 121.7792 | -0.92405
6550.7188 | 122.6669 | -121.6507 | 0.70953 | -0.01778 | -0.073828 | 0.037088 | 0.012845 | -0.016352 | 0.0079525 | -0.029148 | -0.02128 | -0.0082729 | 0.021085 | 0.059491 | -0.0016665 | -0.021844 | 0.038035 | -0.012988 | 0.1208 | 0.087359 | 0.3068 | -0.11342 | 0.078886 | 0.073618 | -0.028879 | 0.006674 | 0.16022 | 0.13137 | -0.20078 | 121.5373 | -0.58873 | 121.6289 | 121.6377 | 0.10044 | -0.62218 | -0.40274 | 121.4499 | -0.70286 | 121.7296 | 121.6218 | 0.1719 | -0.54931 | -0.57816 | 121.7715 | 121.7381 | 121.9575 | 121.6887 | -0.82296 | 121.6574 | 121.8109 | 121.7821 | 121.7243 | -0.91031
6552.4062 | 122.5937 | -121.6873 | 0.70496 | -0.01778 | -0.073615 | 0.036661 | 0.012631 | -0.016565 | 0.0079525 | -0.029148 | -0.021067 | -0.0078455 | 0.020871 | 0.059491 | -0.0018801 | -0.017266 | 0.042614 | -0.012988 | 0.12538 | 0.087359 | 0.30222 | -0.11342 | 0.088043 | 0.073618 | -0.033458 | 0.011252 | 0.1648 | 0.12679 | -0.20078 | 121.5739 | -0.57957 | 121.6701 | 121.6743 | 0.10044 | -0.6176 | -0.40274 | 121.4865 | -0.6937 | 121.7754 | 121.6539 | 0.16732 | -0.54016 | -0.57816 | 121.8127 | 121.7747 | 121.9895 | 121.7299 | -0.81838 | 121.6986 | 121.8521 | 121.8141 | 121.7609 | -0.90574
6554.1094 | 122.5662 | -121.7239 | 0.72327 | -0.0025182 | -0.073615 | 0.036661 | 0.013058 | -0.016138 | 0.0079525 | -0.029148 | -0.021067 | -0.0080591 | 0.020871 | 0.059704 | -0.0014529 | -0.021844 | 0.033457 | -0.017566 | 0.11622 | 0.091937 | 0.31137 | -0.11342 | 0.078886 | 0.064461 | -0.033458 | 0.015831 | 0.16022 | 0.13595 | -0.19162 | 121.6105 | -0.60704 | 121.7021 | 121.7064 | 0.095859 | -0.63133 | -0.41189 | 121.5323 | -0.70744 | 121.8028 | 121.6905 | 0.15816 | -0.56305 | -0.58732 | 121.8402 | 121.8159 | 122.0353 | 121.7574 | -0.83669 | 121.7398 | 121.8842 | 121.8599 | 121.7884 | -0.91489
6555.8125 | 122.6212 | -121.6782 | 0.71869 | -0.01778 | -0.073615 | 0.036874 | 0.013058 | -0.016565 | 0.0081663 | -0.021518 | -0.021067 | -0.0080591 | 0.020871 | 0.059704 | -0.0016665 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.096516 | 0.31137 | -0.118 | 0.078886 | 0.073618 | -0.038036 | 0.015831 | 0.1648 | 0.12222 | -0.20078 | 121.5602 | -0.60246 | 121.6609 | 121.6652 | 0.10502 | -0.62217 | -0.40732 | 121.4774 | -0.70286 | 121.757 | 121.6401 | 0.16274 | -0.55389 | -0.59647 | 121.7944 | 121.7747 | 121.9895 | 121.7162 | -0.83669 | 121.694 | 121.843 | 121.8004 | 121.7518 | -0.91947
6557.5156 | 122.6852 | -121.6644 | 0.71869 | -0.010149 | -0.073828 | 0.036661 | 0.012845 | -0.016565 | 0.0077389 | -0.013887 | -0.02128 | -0.0080591 | 0.020871 | 0.059277 | -0.0014529 | -0.026423 | 0.033457 | -0.012988 | 0.11622 | 0.091937 | 0.3068 | -0.10885 | 0.069728 | 0.073618 | -0.028879 | 0.015831 | 0.1648 | 0.13137 | -0.20994 | 121.5556 | -0.60246 | 121.638 | 121.6514 | 0.095859 | -0.62675 | -0.41189 | 121.4545 | -0.70286 | 121.7342 | 121.6355 | 0.18106 | -0.55389 | -0.58732 | 121.7807 | 121.7564 | 121.9712 | 121.6979 | -0.82754 | 121.6803 | 121.8292 | 121.7958 | 121.738 | -0.92863
6559.2344 | 122.6807 | -121.669 | 0.68665 | -0.01778 | -0.073615 | 0.036874 | 0.013058 | -0.016352 | 0.0081663 | -0.029148 | -0.02128 | -0.0080591 | 0.020871 | 0.059704 | -0.0016665 | -0.012688 | 0.033457 | -0.008409 | 0.11165 | 0.091937 | 0.3068 | -0.118 | 0.088043 | 0.06904 | -0.033458 | 0.015831 | 0.15564 | 0.13137 | -0.1962 | 121.551 | -0.575 | 121.6563 | 121.6606 | 0.10959 | -0.59471 | -0.37985 | 121.4728 | -0.67081 | 121.757 | 121.6355 | 0.16274 | -0.531 | -0.55527 | 121.7807 | 121.7609 | 121.9758 | 121.7025 | -0.80465 | 121.6848 | 121.8246 | 121.8004 | 121.738 | -0.88285
6560.9375 | 122.6578 | -121.6873 | 0.71869 | -0.01778 | -0.073615 | 0.036661 | 0.012631 | -0.016565 | 0.0079525 | -0.013887 | -0.02128 | -0.0080591 | 0.020871 | 0.059491 | -0.0018801 | -0.021844 | 0.033457 | -0.003831 | 0.11622 | 0.091937 | 0.31137 | -0.11342 | 0.083464 | 0.06904 | -0.028879 | 0.011252 | 0.1648 | 0.12679 | -0.20536 | 121.5739 | -0.60246 | 121.6655 | 121.6835 | 0.10959 | -0.62675 | -0.40732 | 121.482 | -0.70744 | 121.7708 | 121.6584 | 0.17648 | -0.55389 | -0.5919 | 121.8035 | 121.7793 | 121.9987 | 121.7208 | -0.83211 | 121.6986 | 121.8521 | 121.8141 | 121.7564 | -0.92405
6562.6406 | 122.6852 | -121.637 | 0.70496 | -0.010149 | -0.073615 | 0.036874 | 0.013272 | -0.016565 | 0.0077389 | -0.021518 | -0.02128 | -0.0082729 | 0.020871 | 0.059277 | -0.0018801 | -0.012688 | 0.033457 | -0.022144 | 0.12538 | 0.091937 | 0.31137 | -0.11342 | 0.078886 | 0.078197 | -0.028879 | 0.011252 | 0.15564 | 0.13137 | -0.20078 | 121.5235 | -0.57957 | 121.6243 | 121.6148 | 0.091281 | -0.61302 | -0.39358 | 121.4362 | -0.6937 | 121.7158 | 121.6081 | 0.1719 | -0.54931 | -0.57358 | 121.7623 | 121.7289 | 121.9483 | 121.6704 | -0.81838 | 121.6482 | 121.7926 | 121.7683 | 121.7152 | -0.90574
6564.3281 | 122.6761 | -121.6736 | 0.70038 | -0.010149 | -0.073401 | 0.036661 | 0.012631 | -0.016565 | 0.0079525 | -0.029148 | -0.021067 | -0.0082729 | 0.020444 | 0.059277 | -0.0020939 | -0.012688 | 0.042614 | -0.012988 | 0.1208 | 0.096516 | 0.3068 | -0.10427 | 0.069728 | 0.073618 | -0.033458 | 0.011252 | 0.15564 | 0.14053 | -0.1962 | 121.5693 | -0.57957 | 121.6609 | 121.6606 | 0.09128 | -0.60386 | -0.39358 | 121.4774 | -0.68913 | 121.7433 | 121.6401 | 0.16274 | -0.54473 | -0.55985 | 121.7944 | 121.7701 | 121.9804 | 121.7162 | -0.80465 | 121.6848 | 121.8292 | 121.8141 | 121.7472 | -0.89658
6566.0938 | 122.6669 | -121.6782 | 0.70038 | -0.01778 | -0.073615 | 0.036874 | 0.012845 | -0.016352 | 0.0079525 | -0.036779 | -0.02128 | -0.0080591 | 0.021085 | 0.059491 | -0.0018801 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.31595 | -0.11342 | 0.078886 | 0.073618 | -0.038036 | 0.011252 | 0.15107 | 0.13137 | -0.20536 | 121.5647 | -0.58415 | 121.6563 | 121.6698 | 0.10502 | -0.60844 | -0.38442 | 121.4728 | -0.68913 | 121.757 | 121.6401 | 0.16732 | -0.54931 | -0.569 | 121.7944 | 121.7701 | 121.9941 | 121.7116 | -0.8138 | 121.6894 | 121.8292 | 121.8095 | 121.7518 | -0.90574
6567.7969 | 122.6807 | -121.6736 | 0.70496 | -0.010149 | -0.073615 | 0.036661 | 0.013058 | -0.016352 | 0.0077389 | -0.029148 | -0.021067 | -0.0082729 | 0.020871 | 0.059704 | -0.0018801 | -0.012688 | 0.038035 | -0.017566 | 0.1208 | 0.096516 | 0.31595 | -0.10885 | 0.074307 | 0.06904 | -0.028879 | 0.011252 | 0.1648 | 0.13137 | -0.20078 | 121.5647 | -0.58415 | 121.6609 | 121.656 | 0.091281 | -0.60844 | -0.389 | 121.4728 | -0.6937 | 121.7479 | 121.6447 | 0.1719 | -0.54016 | -0.57358 | 121.7944 | 121.7701 | 121.9895 | 121.7116 | -0.8138 | 121.6848 | 121.8384 | 121.805 | 121.7426 | -0.90574
6569.5156 | 122.6761 | -121.6782 | 0.68207 | -0.010149 | -0.073828 | 0.036661 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.020871 | 0.059277 | -0.0018801 | -0.026423 | 0.033457 | -0.012988 | 0.11622 | 0.096516 | 0.31595 | -0.118 | 0.069728 | 0.073618 | -0.033458 | 0.011252 | 0.15564 | 0.13595 | -0.20536 | 121.5602 | -0.56584 | 121.6517 | 121.6652 | 0.10502 | -0.58555 | -0.36612 | 121.4728 | -0.67082 | 121.7479 | 121.6447 | 0.1719 | -0.52643 | -0.54612 | 121.7944 | 121.7747 | 121.9941 | 121.7116 | -0.80007 | 121.6894 | 121.8338 | 121.8141 | 121.7518 | -0.88743
6571.2188 | 122.6486 | -121.6873 | 0.70953 | -0.010149 | -0.073828 | 0.036661 | 0.012631 | -0.016779 | 0.0077389 | -0.029148 | -0.021067 | -0.0078455 | 0.021085 | 0.059704 | -0.0020939 | -0.017266 | 0.042614 | -0.012988 | 0.1208 | 0.1011 | 0.3068 | -0.10885 | 0.078886 | 0.073618 | -0.028879 | 0.015831 | 0.1648 | 0.12679 | -0.20536 | 121.5785 | -0.58873 | 121.6701 | 121.6743 | 0.095859 | -0.60844 | -0.40274 | 121.482 | -0.6937 | 121.7662 | 121.6584 | 0.17648 | -0.54473 | -0.58274 | 121.8081 | 121.7884 | 121.9941 | 121.7299 | -0.81838 | 121.7031 | 121.8521 | 121.8141 | 121.7609 | -0.91489
6572.9375 | 122.6944 | -121.6553 | 0.70496 | -0.01778 | -0.074042 | 0.036661 | 0.013058 | -0.016565 | 0.0081663 | -0.021518 | -0.02128 | -0.0078455 | 0.021085 | 0.059491 | -0.0016665 | -0.021844 | 0.042614 | -0.008409 | 0.11622 | 0.1011 | 0.31595 | -0.11342 | 0.083464 | 0.06904 | -0.033458 | 0.015831 | 0.16938 | 0.13595 | -0.20078 | 121.5418 | -0.58873 | 121.6334 | 121.6469 | 0.10502 | -0.60386 | -0.389 | 121.4545 | -0.68912 | 121.7387 | 121.6218 | 0.16732 | -0.53558 | -0.569 | 121.7715 | 121.7564 | 121.9712 | 121.6979 | -0.81838 | 121.6711 | 121.8247 | 121.7912 | 121.7243 | -0.90574
6574.6719 | 122.5525 | -121.7102 | 0.73242 | -0.01778 | -0.073828 | 0.036447 | 0.012417 | -0.016352 | 0.0081663 | -0.013887 | -0.02128 | -0.0080591 | 0.020658 | 0.059491 | -0.0018801 | -0.017266 | 0.038035 | -0.012988 | 0.11165 | 0.091937 | 0.31137 | -0.11342 | 0.083464 | 0.078197 | -0.028879 | 0.015831 | 0.16022 | 0.13137 | -0.20536 | 121.5968 | -0.62078 | 121.6929 | 121.6972 | 0.10044 | -0.64048 | -0.42105 | 121.5048 | -0.71659 | 121.7937 | 121.6813 | 0.17648 | -0.5722 | -0.60105 | 121.8219 | 121.8021 | 122.0216 | 121.7482 | -0.84585 | 121.726 | 121.8704 | 121.8416 | 121.7884 | -0.93778
6576.375 | 122.5891 | -121.7194 | 0.72784 | -0.0025182 | -0.073615 | 0.036447 | 0.012845 | -0.016779 | 0.0081663 | -0.021518 | -0.021067 | -0.0078455 | 0.020658 | 0.059491 | -0.0020939 | -0.012688 | 0.033457 | -0.008409 | 0.1208 | 0.096516 | 0.31137 | -0.11342 | 0.078886 | 0.06904 | -0.033458 | 0.011252 | 0.15564 | 0.13137 | -0.1962 | 121.6059 | -0.60704 | 121.7067 | 121.711 | 0.10502 | -0.63133 | -0.41647 | 121.5232 | -0.71659 | 121.7982 | 121.6859 | 0.16274 | -0.5722 | -0.59647 | 121.8402 | 121.8159 | 122.0307 | 121.7528 | -0.84127 | 121.7306 | 121.875 | 121.8507 | 121.7884 | -0.92404
6578.0781 | 122.5571 | -121.7606 | 0.73242 | -0.010149 | -0.074042 | 0.036661 | 0.013058 | -0.016352 | 0.0079525 | -0.036779 | -0.021067 | -0.0080591 | 0.020871 | 0.059491 | -0.0016665 | -0.012688 | 0.033457 | -0.012988 | 0.11622 | 0.096516 | 0.30222 | -0.118 | 0.074307 | 0.06904 | -0.028879 | 0.011252 | 0.16938 | 0.13595 | -0.1962 | 121.6426 | -0.6162 | 121.7479 | 121.7476 | 0.10502 | -0.63591 | -0.43021 | 121.5644 | -0.72117 | 121.8349 | 121.7317 | 0.16732 | -0.56304 | -0.59647 | 121.8768 | 121.8571 | 122.0628 | 121.794 | -0.85043 | 121.7718 | 121.9299 | 121.8965 | 121.8296 | -0.92862
6579.7812 | 122.6303 | -121.7102 | 0.68665 | -0.010149 | -0.073401 | 0.036661 | 0.012845 | -0.016779 | 0.0077389 | -0.021518 | -0.02128 | -0.0082729 | 0.020444 | 0.059491 | -0.0018801 | -0.017266 | 0.033457 | -0.017566 | 0.11165 | 0.096516 | 0.31595 | -0.10885 | 0.088043 | 0.06904 | -0.038036 | 0.006674 | 0.16022 | 0.12222 | -0.19162 | 121.6014 | -0.575 | 121.6929 | 121.6926 | 0.091281 | -0.59013 | -0.37069 | 121.5186 | -0.67997 | 121.7982 | 121.6722 | 0.15359 | -0.52642 | -0.56443 | 121.8219 | 121.8067 | 122.0262 | 121.7437 | -0.79549 | 121.7169 | 121.8704 | 121.8324 | 121.7792 | -0.87827
6581.4844 | 122.5845 | -121.7194 | 0.72784 | -0.01778 | -0.073401 | 0.036661 | 0.012417 | -0.016779 | 0.0081663 | -0.029148 | -0.02128 | -0.0082729 | 0.020871 | 0.059277 | -0.0016665 | -0.012688 | 0.033457 | -0.017566 | 0.1208 | 0.096516 | 0.31137 | -0.11342 | 0.083464 | 0.073618 | -0.033458 | 0.015831 | 0.16022 | 0.13595 | -0.1962 | 121.6059 | -0.60704 | 121.7067 | 121.7018 | 0.095859 | -0.63133 | -0.41647 | 121.5232 | -0.71201 | 121.8028 | 121.6859 | 0.16274 | -0.56762 | -0.59189 | 121.8402 | 121.8159 | 122.0307 | 121.7528 | -0.84127 | 121.7352 | 121.8796 | 121.8553 | 121.793 | -0.92404
6583.1875 | 122.6715 | -121.6644 | 0.69122 | -0.01778 | -0.073401 | 0.036874 | 0.012845 | -0.016352 | 0.0077389 | -0.029148 | -0.021494 | -0.0078455 | 0.020871 | 0.059491 | -0.0023075 | -0.012688 | 0.038035 | -0.017566 | 0.11622 | 0.10567 | 0.31595 | -0.11342 | 0.078886 | 0.064461 | -0.033458 | 0.011252 | 0.15564 | 0.13595 | -0.20078 | 121.551 | -0.575 | 121.6517 | 121.6469 | 0.095859 | -0.58555 | -0.37527 | 121.4637 | -0.67997 | 121.7433 | 121.631 | 0.16732 | -0.53558 | -0.55527 | 121.7807 | 121.7701 | 121.9804 | 121.7025 | -0.80465 | 121.6757 | 121.8201 | 121.8004 | 121.7289 | -0.892
6584.8906 | 122.5525 | -121.7422 | 0.72327 | -0.010149 | -0.073401 | 0.037088 | 0.013058 | -0.016779 | 0.0079525 | -0.029148 | -0.021494 | -0.0080591 | 0.020871 | 0.059704 | -0.0016665 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.096516 | 0.3068 | -0.10885 | 0.078886 | 0.06904 | -0.028879 | 0.011252 | 0.16022 | 0.13595 | -0.20536 | 121.6334 | -0.60704 | 121.725 | 121.7293 | 0.095859 | -0.62675 | -0.41647 | 121.5369 | -0.71201 | 121.8211 | 121.7134 | 0.17648 | -0.56305 | -0.58732 | 121.8585 | 121.8388 | 122.049 | 121.7803 | -0.83211 | 121.7535 | 121.9025 | 121.8782 | 121.8113 | -0.92863
6586.625 | 122.6028 | -121.7056 | 0.73242 | -0.0025182 | -0.073615 | 0.036661 | 0.013272 | -0.016565 | 0.0079525 | -0.021518 | -0.020853 | -0.0084865 | 0.020444 | 0.059491 | -0.0020939 | -0.017266 | 0.028878 | -0.017566 | 0.1208 | 0.096516 | 0.3068 | -0.10885 | 0.069728 | 0.073618 | -0.033458 | 0.011252 | 0.1648 | 0.12679 | -0.20078 | 121.5968 | -0.61162 | 121.6884 | 121.6881 | 0.091281 | -0.63591 | -0.42563 | 121.5048 | -0.72117 | 121.7754 | 121.6722 | 0.16732 | -0.56762 | -0.60563 | 121.8264 | 121.8021 | 122.0124 | 121.7345 | -0.84127 | 121.7169 | 121.8704 | 121.8324 | 121.7792 | -0.9332
6588.3281 | 122.7036 | -121.701 | 0.66834 | -0.010149 | -0.073615 | 0.036874 | 0.013058 | -0.016779 | 0.0083799 | -0.013887 | -0.02128 | -0.0080591 | 0.020871 | 0.059704 | -0.0020939 | -0.017266 | 0.038035 | -0.008409 | 0.1208 | 0.1011 | 0.31137 | -0.10885 | 0.083464 | 0.064461 | -0.028879 | 0.002095 | 0.15564 | 0.12679 | -0.20536 | 121.5922 | -0.54753 | 121.6838 | 121.6926 | 0.10044 | -0.56724 | -0.35696 | 121.4957 | -0.66624 | 121.7845 | 121.6722 | 0.17648 | -0.51269 | -0.54154 | 121.8219 | 121.8021 | 122.0124 | 121.7391 | -0.77718 | 121.7031 | 121.8567 | 121.8278 | 121.7655 | -0.87369
6590.0312 | 122.6532 | -121.6782 | 0.69122 | -0.01778 | -0.073828 | 0.036661 | 0.013058 | -0.016565 | 0.0079525 | -0.029148 | -0.02128 | -0.0082729 | 0.020658 | 0.059491 | -0.0016665 | -0.021844 | 0.0243 | -0.017566 | 0.11622 | 0.091937 | 0.3068 | -0.10885 | 0.078886 | 0.06904 | -0.033458 | 0.006674 | 0.16938 | 0.13595 | -0.20536 | 121.5693 | -0.575 | 121.6563 | 121.6606 | 0.091281 | -0.59929 | -0.38443 | 121.4728 | -0.68455 | 121.757 | 121.6447 | 0.1719 | -0.52184 | -0.55527 | 121.7944 | 121.7701 | 121.985 | 121.7025 | -0.80007 | 121.6848 | 121.8475 | 121.8141 | 121.7472 | -0.89658
6591.7344 | 122.6898 | -121.6782 | 0.6958 | -0.010149 | -0.074042 | 0.036874 | 0.013058 | -0.016779 | 0.0079525 | -0.036779 | -0.02128 | -0.0080591 | 0.020871 | 0.059491 | -0.0018801 | -0.017266 | 0.042614 | -0.012988 | 0.1208 | 0.091937 | 0.31137 | -0.10427 | 0.074307 | 0.073618 | -0.033458 | 0.011252 | 0.16022 | 0.13595 | -0.1962 | 121.5739 | -0.575 | 121.6609 | 121.6652 | 0.09128 | -0.60386 | -0.38443 | 121.482 | -0.68455 | 121.7525 | 121.6447 | 0.16274 | -0.53558 | -0.55985 | 121.799 | 121.7701 | 121.9895 | 121.7208 | -0.80007 | 121.6894 | 121.8384 | 121.8141 | 121.7518 | -0.892
6593.4531 | 122.6715 | -121.6965 | 0.70038 | -0.01778 | -0.073615 | 0.036874 | 0.012845 | -0.016565 | 0.0083799 | -0.013887 | -0.021067 | -0.0080591 | 0.020871 | 0.059704 | -0.0018801 | -0.017266 | 0.028878 | -0.022144 | 0.1208 | 0.096516 | 0.31595 | -0.12258 | 0.074307 | 0.073618 | -0.033458 | 0.006674 | 0.16938 | 0.13595 | -0.20078 | 121.5739 | -0.57957 | 121.6792 | 121.6743 | 0.10044 | -0.60386 | -0.38442 | 121.4957 | -0.6937 | 121.7708 | 121.663 | 0.16732 | -0.531 | -0.56443 | 121.8173 | 121.793 | 122.0124 | 121.7254 | -0.82296 | 121.7031 | 121.8659 | 121.8324 | 121.7701 | -0.90116
6595.1562 | 122.6852 | -121.701 | 0.68665 | -0.01778 | -0.073401 | 0.036661 | 0.013058 | -0.016352 | 0.0081663 | -0.021518 | -0.02128 | -0.0078455 | 0.020871 | 0.059491 | -0.0018801 | -0.017266 | 0.042614 | -0.017566 | 0.1208 | 0.091937 | 0.31137 | -0.11342 | 0.083464 | 0.078197 | -0.038036 | 0.015831 | 0.17396 | 0.12679 | -0.1962 | 121.5876 | -0.56584 | 121.6838 | 121.6835 | 0.095859 | -0.59471 | -0.37527 | 121.5048 | -0.67081 | 121.7845 | 121.663 | 0.15816 | -0.51269 | -0.55985 | 121.8219 | 121.793 | 122.0124 | 121.7437 | -0.80007 | 121.7169 | 121.875 | 121.8278 | 121.7792 | -0.88285
6596.8594 | 122.6898 | -121.6827 | 0.6958 | -0.010149 | -0.073615 | 0.036874 | 0.013058 | -0.016565 | 0.0081663 | -0.029148 | -0.020853 | -0.0080591 | 0.020658 | 0.059918 | -0.0016665 | -0.026423 | 0.038035 | -0.012988 | 0.1208 | 0.091937 | 0.31137 | -0.118 | 0.078886 | 0.082776 | -0.042615 | 0.011252 | 0.16022 | 0.13595 | -0.1962 | 121.5647 | -0.575 | 121.6563 | 121.6698 | 0.10502 | -0.60386 | -0.38443 | 121.4865 | -0.68455 | 121.7616 | 121.6401 | 0.15359 | -0.53558 | -0.55985 | 121.8035 | 121.7747 | 121.9941 | 121.7208 | -0.81381 | 121.694 | 121.843 | 121.8187 | 121.7655 | -0.892
6598.6094 | 122.5845 | -121.7377 | 0.73242 | 0.0051128 | -0.073615 | 0.036661 | 0.012845 | -0.016138 | 0.0079525 | -0.021518 | -0.02128 | -0.0078455 | 0.021085 | 0.059491 | -0.0018801 | -0.012688 | 0.033457 | -0.017566 | 0.1208 | 0.096516 | 0.31137 | -0.118 | 0.083464 | 0.073618 | -0.033458 | 0.020409 | 0.1648 | 0.12679 | -0.20078 | 121.6197 | -0.61162 | 121.725 | 121.7201 | 0.10044 | -0.63591 | -0.42105 | 121.5369 | -0.71201 | 121.8211 | 121.7042 | 0.16732 | -0.56762 | -0.60563 | 121.8585 | 121.8342 | 122.049 | 121.7711 | -0.85043 | 121.7581 | 121.9025 | 121.8645 | 121.8113 | -0.9332
6600.3125 | 122.7036 | -121.6919 | 0.67291 | -0.01778 | -0.073401 | 0.036661 | 0.012631 | -0.016352 | 0.0081663 | -0.0062567 | -0.02128 | -0.0080591 | 0.020658 | 0.059491 | -0.0018801 | -0.017266 | 0.038035 | -0.012988 | 0.1208 | 0.091937 | 0.31137 | -0.11342 | 0.074307 | 0.064461 | -0.028879 | 0.020409 | 0.16938 | 0.13137 | -0.1962 | 121.5785 | -0.55211 | 121.6746 | 121.6789 | 0.10044 | -0.58098 | -0.36154 | 121.4957 | -0.6525 | 121.7662 | 121.663 | 0.16732 | -0.50353 | -0.54154 | 121.8127 | 121.7838 | 122.0033 | 121.7299 | -0.78634 | 121.7123 | 121.8613 | 121.8233 | 121.7564 | -0.86911
6602.0156 | 122.6898 | -121.6553 | 0.67291 | -0.010149 | -0.073401 | 0.036661 | 0.013058 | -0.016565 | 0.0077389 | -0.029148 | -0.02128 | -0.0082729 | 0.020871 | 0.059704 | -0.0014529 | -0.021844 | 0.0243 | -0.017566 | 0.12538 | 0.087359 | 0.31595 | -0.10885 | 0.078886 | 0.078197 | -0.033458 | 0.015831 | 0.1648 | 0.13595 | -0.1962 | 121.5464 | -0.54753 | 121.6334 | 121.6377 | 0.091281 | -0.58555 | -0.35696 | 121.4591 | -0.65708 | 121.7342 | 121.6218 | 0.16274 | -0.50811 | -0.53696 | 121.7807 | 121.7426 | 121.9712 | 121.6796 | -0.78176 | 121.6711 | 121.8201 | 121.7912 | 121.7335 | -0.86911
6603.7188 | 122.5937 | -121.7422 | 0.72327 | -0.010149 | -0.073615 | 0.036447 | 0.012845 | -0.016352 | 0.0077389 | -0.021518 | -0.02128 | -0.0080591 | 0.021085 | 0.059704 | -0.0018801 | -0.017266 | 0.038035 | -0.012988 | 0.12538 | 0.1011 | 0.31595 | -0.11342 | 0.083464 | 0.06904 | -0.042615 | 0.011252 | 0.1648 | 0.13595 | -0.1962 | 121.6288 | -0.59788 | 121.725 | 121.7293 | 0.10044 | -0.62217 | -0.40731 | 121.546 | -0.71201 | 121.8257 | 121.6996 | 0.15359 | -0.55847 | -0.58732 | 121.8676 | 121.8433 | 122.0582 | 121.7803 | -0.83669 | 121.7535 | 121.907 | 121.8782 | 121.8113 | -0.91947
6605.4062 | 122.6532 | -121.6873 | 0.69122 | -0.01778 | -0.073828 | 0.036233 | 0.012417 | -0.016779 | 0.0079525 | -0.036779 | -0.021494 | -0.0082729 | 0.020871 | 0.059491 | -0.0016665 | -0.017266 | 0.042614 | -0.012988 | 0.11622 | 0.096516 | 0.3068 | -0.118 | 0.074307 | 0.06904 | -0.033458 | 0.015831 | 0.16938 | 0.13595 | -0.20078 | 121.5693 | -0.575 | 121.6701 | 121.6743 | 0.10502 | -0.59471 | -0.38443 | 121.4865 | -0.67539 | 121.7616 | 121.6539 | 0.16732 | -0.52184 | -0.55527 | 121.8035 | 121.7838 | 121.9941 | 121.7299 | -0.80923 | 121.7031 | 121.8567 | 121.8233 | 121.7564 | -0.892
6607.1406 | 122.6166 | -121.7377 | 0.71869 | -0.025411 | -0.073615 | 0.036447 | 0.013058 | -0.016565 | 0.0079525 | -0.021518 | -0.021067 | -0.0078455 | 0.020658 | 0.059491 | -0.0020939 | -0.008109 | 0.033457 | -0.008409 | 0.11165 | 0.096516 | 0.3068 | -0.11342 | 0.078886 | 0.073618 | -0.038036 | 0.006674 | 0.16022 | 0.12679 | -0.20078 | 121.6242 | -0.60704 | 121.7296 | 121.7293 | 0.10502 | -0.62217 | -0.41189 | 121.5369 | -0.71202 | 121.8166 | 121.6996 | 0.16274 | -0.55847 | -0.5919 | 121.8493 | 121.8342 | 122.0445 | 121.7711 | -0.83211 | 121.7443 | 121.8979 | 121.8645 | 121.8113 | -0.91947
6608.8438 | 122.5662 | -121.7377 | 0.73242 | -0.0025182 | -0.073401 | 0.036874 | 0.012631 | -0.016565 | 0.0081663 | -0.029148 | -0.021494 | -0.0078455 | 0.02023 | 0.059491 | -0.0016665 | -0.017266 | 0.042614 | -0.012988 | 0.12538 | 0.1011 | 0.3068 | -0.11342 | 0.074307 | 0.078197 | -0.038036 | 0.006674 | 0.1648 | 0.13595 | -0.20078 | 121.6242 | -0.60704 | 121.7204 | 121.7247 | 0.10044 | -0.63133 | -0.42563 | 121.5369 | -0.72575 | 121.812 | 121.6996 | 0.16274 | -0.56762 | -0.59647 | 121.8631 | 121.8388 | 122.0445 | 121.7803 | -0.84585 | 121.7443 | 121.9025 | 121.8736 | 121.8159 | -0.9332
6610.6094 | 122.5983 | -121.7239 | 0.70496 | -0.01778 | -0.073828 | 0.036661 | 0.012845 | -0.016565 | 0.0077389 | -0.013887 | -0.02128 | -0.0080591 | 0.020871 | 0.059704 | -0.0016665 | -0.012688 | 0.042614 | -0.012988 | 0.11622 | 0.091937 | 0.3068 | -0.11342 | 0.078886 | 0.06904 | -0.033458 | 0.015831 | 0.1648 | 0.14053 | -0.19162 | 121.6105 | -0.58873 | 121.7113 | 121.7109 | 0.10044 | -0.61302 | -0.39816 | 121.5323 | -0.68912 | 121.8028 | 121.6905 | 0.15816 | -0.54016 | -0.56443 | 121.8402 | 121.8159 | 122.0307 | 121.7666 | -0.81838 | 121.7398 | 121.8887 | 121.8645 | 121.793 | -0.89658
6612.3281 | 122.6898 | -121.6873 | 0.69122 | -0.0025182 | -0.074042 | 0.036661 | 0.012631 | -0.016779 | 0.0079525 | -0.021518 | -0.021494 | -0.0082729 | 0.020658 | 0.059918 | -0.0014529 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.096516 | 0.31137 | -0.11342 | 0.074307 | 0.078197 | -0.033458 | 0.006674 | 0.16938 | 0.13137 | -0.1962 | 121.5739 | -0.575 | 121.6701 | 121.6743 | 0.10044 | -0.59471 | -0.37985 | 121.4911 | -0.68455 | 121.7616 | 121.6539 | 0.16274 | -0.52184 | -0.55985 | 121.8035 | 121.7838 | 121.9987 | 121.7254 | -0.80465 | 121.694 | 121.8567 | 121.8187 | 121.7655 | -0.88742
6614.0781 | 122.5937 | -121.7422 | 0.72327 | -0.010149 | -0.073615 | 0.036661 | 0.012845 | -0.016565 | 0.0081663 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059704 | -0.0018801 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.1011 | 0.31137 | -0.10427 | 0.078886 | 0.06904 | -0.038036 | 0.006674 | 0.16022 | 0.12679 | -0.20078 | 121.638 | -0.60704 | 121.725 | 121.7293 | 0.09128 | -0.62217 | -0.41189 | 121.5415 | -0.71659 | 121.8211 | 121.7042 | 0.16274 | -0.56305 | -0.59647 | 121.8585 | 121.8433 | 122.0536 | 121.7803 | -0.82754 | 121.7489 | 121.9025 | 121.869 | 121.8113 | -0.92405
6615.7812 | 122.6944 | -121.6919 | 0.70038 | -0.025411 | -0.073615 | 0.036874 | 0.012845 | -0.016352 | 0.0079525 | -0.021518 | -0.020853 | -0.0080591 | 0.020871 | 0.059704 | -0.0016665 | -0.008109 | 0.038035 | -0.008409 | 0.13454 | 0.096516 | 0.31137 | -0.12258 | 0.083464 | 0.064461 | -0.033458 | 0.020409 | 0.15564 | 0.14053 | -0.20078 | 121.5693 | -0.56584 | 121.6838 | 121.6835 | 0.11417 | -0.60386 | -0.389 | 121.4911 | -0.67997 | 121.7754 | 121.6584 | 0.16732 | -0.54473 | -0.55985 | 121.8264 | 121.7884 | 122.0033 | 121.7299 | -0.82296 | 121.7123 | 121.8475 | 121.8324 | 121.7564 | -0.90116
6617.5156 | 122.6624 | -121.7148 | 0.70496 | -0.025411 | -0.073615 | 0.036661 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.021494 | -0.0082729 | 0.020444 | 0.059491 | -0.0018801 | -0.017266 | 0.038035 | -0.012988 | 0.12538 | 0.10567 | 0.31137 | -0.11342 | 0.078886 | 0.073618 | -0.038036 | 0.015831 | 0.16022 | 0.13595 | -0.20078 | 121.6014 | -0.57957 | 121.6975 | 121.7018 | 0.10044 | -0.59928 | -0.39358 | 121.514 | -0.68912 | 121.7937 | 121.6767 | 0.16274 | -0.54473 | -0.569 | 121.8402 | 121.8205 | 122.0262 | 121.7528 | -0.81838 | 121.7306 | 121.875 | 121.8507 | 121.7884 | -0.90574
6619.2188 | 122.6349 | -121.7239 | 0.72784 | -0.025411 | -0.073828 | 0.036661 | 0.012631 | -0.016565 | 0.0077389 | -0.021518 | -0.021067 | -0.0082729 | 0.020871 | 0.059491 | -0.0016665 | -0.021844 | 0.033457 | -0.012988 | 0.1208 | 0.096516 | 0.31137 | -0.11342 | 0.078886 | 0.073618 | -0.028879 | 0.011252 | 0.1648 | 0.13137 | -0.20078 | 121.6105 | -0.60704 | 121.7021 | 121.7109 | 0.10044 | -0.63133 | -0.41647 | 121.5232 | -0.71659 | 121.8028 | 121.6951 | 0.1719 | -0.56304 | -0.59647 | 121.8447 | 121.8205 | 122.0353 | 121.7574 | -0.84127 | 121.7352 | 121.8887 | 121.8553 | 121.7976 | -0.92862
6620.9219 | 122.5983 | -121.7422 | 0.73242 | -0.010149 | -0.073828 | 0.036233 | 0.012631 | -0.016352 | 0.0079525 | -0.029148 | -0.020853 | -0.0080591 | 0.020658 | 0.059277 | -0.0018801 | -0.017266 | 0.038035 | -0.012988 | 0.11622 | 0.096516 | 0.31137 | -0.10885 | 0.078886 | 0.06904 | -0.033458 | 0.002095 | 0.15107 | 0.13137 | -0.20078 | 121.6334 | -0.6162 | 121.725 | 121.7293 | 0.095859 | -0.63591 | -0.42105 | 121.5415 | -0.73033 | 121.8211 | 121.7088 | 0.16732 | -0.58136 | -0.60105 | 121.8585 | 121.8388 | 122.0536 | 121.7803 | -0.84127 | 121.7443 | 121.8933 | 121.8736 | 121.8113 | -0.9332
6622.6562 | 122.6166 | -121.7102 | 0.73242 | -0.010149 | -0.073828 | 0.036233 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.021067 | -0.0078455 | 0.020658 | 0.059918 | -0.0018801 | -0.012688 | 0.028878 | -0.017566 | 0.1208 | 0.091937 | 0.31595 | -0.11342 | 0.083464 | 0.078197 | -0.028879 | 0.006674 | 0.1648 | 0.13137 | -0.1962 | 121.5968 | -0.61162 | 121.6975 | 121.6926 | 0.095859 | -0.64048 | -0.41647 | 121.514 | -0.72575 | 121.7937 | 121.6813 | 0.16732 | -0.56762 | -0.60105 | 121.831 | 121.8021 | 122.0262 | 121.7391 | -0.84585 | 121.7169 | 121.875 | 121.8416 | 121.7884 | -0.92862
6624.3594 | 122.5845 | -121.7468 | 0.73242 | -0.010149 | -0.073828 | 0.036447 | 0.012845 | -0.016138 | 0.0077389 | -0.021518 | -0.021067 | -0.0080591 | 0.020871 | 0.059918 | -0.0018801 | -0.017266 | 0.038035 | -0.012988 | 0.12538 | 0.091937 | 0.31595 | -0.10885 | 0.074307 | 0.073618 | -0.042615 | 0.011252 | 0.15564 | 0.12679 | -0.20536 | 121.638 | -0.60704 | 121.7296 | 121.7338 | 0.095859 | -0.64048 | -0.41647 | 121.5415 | -0.72117 | 121.8211 | 121.7042 | 0.16274 | -0.57678 | -0.60563 | 121.8722 | 121.8388 | 122.0628 | 121.7849 | -0.84127 | 121.7581 | 121.9025 | 121.8736 | 121.8204 | -0.93778
6626.0625 | 122.6852 | -121.7056 | 0.70496 | -0.0025182 | -0.073401 | 0.036447 | 0.013058 | -0.016565 | 0.0079525 | -0.021518 | -0.021067 | -0.0078455 | 0.020658 | 0.059704 | -0.0020939 | -0.021844 | 0.042614 | -0.017566 | 0.1208 | 0.096516 | 0.31595 | -0.11342 | 0.074307 | 0.06904 | -0.038036 | 0.011252 | 0.16022 | 0.13137 | -0.1962 | 121.5922 | -0.58415 | 121.6838 | 121.6881 | 0.095859 | -0.60844 | -0.389 | 121.5094 | -0.6937 | 121.7799 | 121.6676 | 0.15816 | -0.54473 | -0.57358 | 121.8264 | 121.8021 | 122.0216 | 121.7482 | -0.81838 | 121.7169 | 121.8658 | 121.837 | 121.7747 | -0.90116
6627.7812 | 122.699 | -121.6919 | 0.69122 | -0.040673 | -0.073828 | 0.036447 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059491 | -0.0018801 | -0.017266 | 0.033457 | -0.022144 | 0.1208 | 0.1011 | 0.3068 | -0.11342 | 0.078886 | 0.073618 | -0.028879 | 0.006674 | 0.1648 | 0.12679 | -0.20078 | 121.5785 | -0.57042 | 121.6746 | 121.6698 | 0.091281 | -0.59013 | -0.38443 | 121.4911 | -0.68455 | 121.7708 | 121.663 | 0.1719 | -0.52642 | -0.56443 | 121.8127 | 121.793 | 121.9987 | 121.7254 | -0.80465 | 121.6986 | 121.8567 | 121.8187 | 121.7655 | -0.892
6629.5469 | 122.5937 | -121.7239 | 0.72784 | -0.025411 | -0.073828 | 0.036447 | 0.013058 | -0.016779 | 0.0081663 | -0.013887 | -0.021494 | -0.0080591 | 0.021085 | 0.059704 | -0.0020939 | -0.017266 | 0.042614 | -0.008409 | 0.1208 | 0.1011 | 0.31595 | -0.10427 | 0.088043 | 0.073618 | -0.028879 | 0.002095 | 0.1648 | 0.13595 | -0.1962 | 121.6197 | -0.60704 | 121.7067 | 121.7155 | 0.095859 | -0.62675 | -0.41189 | 121.5277 | -0.72575 | 121.812 | 121.6951 | 0.16732 | -0.56304 | -0.59189 | 121.8447 | 121.825 | 122.0399 | 121.7666 | -0.83211 | 121.726 | 121.8887 | 121.8599 | 121.7976 | -0.92404
6631.2656 | 122.699 | -121.6782 | 0.70953 | -0.010149 | -0.073828 | 0.036874 | 0.012631 | -0.016779 | 0.0079525 | -0.013887 | -0.02128 | -0.0078455 | 0.020871 | 0.059918 | -0.0018801 | -0.017266 | 0.038035 | -0.012988 | 0.1208 | 0.096516 | 0.31595 | -0.118 | 0.088043 | 0.078197 | -0.033458 | 0.011252 | 0.16022 | 0.13595 | -0.20078 | 121.5602 | -0.58873 | 121.6609 | 121.6652 | 0.10502 | -0.61302 | -0.39358 | 121.4774 | -0.69828 | 121.7662 | 121.6447 | 0.16732 | -0.54931 | -0.57358 | 121.799 | 121.7747 | 121.9941 | 121.7162 | -0.82754 | 121.6894 | 121.8384 | 121.8141 | 121.7564 | -0.91031
6633.0312 | 122.5891 | -121.7285 | 0.72327 | -0.025411 | -0.073828 | 0.036661 | 0.013058 | -0.016352 | 0.0079525 | -0.021518 | -0.02128 | -0.0080591 | 0.020444 | 0.059918 | -0.0020939 | -0.021844 | 0.033457 | -0.008409 | 0.12538 | 0.096516 | 0.31137 | -0.10885 | 0.074307 | 0.06904 | -0.038036 | 0.006674 | 0.1648 | 0.12679 | -0.1962 | 121.6197 | -0.59788 | 121.7067 | 121.7201 | 0.10044 | -0.62675 | -0.41189 | 121.5323 | -0.71659 | 121.8028 | 121.6905 | 0.15816 | -0.55847 | -0.59647 | 121.8539 | 121.825 | 122.0399 | 121.762 | -0.83211 | 121.7352 | 121.8933 | 121.8553 | 121.7976 | -0.91947
6634.7344 | 122.5845 | -121.7468 | 0.72784 | -0.01778 | -0.073828 | 0.036447 | 0.013058 | -0.016565 | 0.0081663 | -0.036779 | -0.02128 | -0.0078455 | 0.020871 | 0.059918 | -0.0023075 | -0.012688 | 0.038035 | -0.003831 | 0.11622 | 0.096516 | 0.31595 | -0.11342 | 0.078886 | 0.06904 | -0.038036 | 0.006674 | 0.16022 | 0.13595 | -0.20078 | 121.6334 | -0.61162 | 121.7341 | 121.743 | 0.10959 | -0.63133 | -0.41189 | 121.546 | -0.72117 | 121.8257 | 121.7088 | 0.16274 | -0.56762 | -0.59189 | 121.8631 | 121.8433 | 122.0628 | 121.7849 | -0.84127 | 121.7535 | 121.907 | 121.8828 | 121.8159 | -0.92862
6636.4531 | 122.5891 | -121.7285 | 0.73242 | -0.01778 | -0.073615 | 0.036447 | 0.013058 | -0.016779 | 0.0077389 | -0.036779 | -0.021494 | -0.0076319 | 0.020871 | 0.059704 | -0.0016665 | -0.017266 | 0.033457 | -0.012988 | 0.11622 | 0.1011 | 0.31595 | -0.10885 | 0.074307 | 0.073618 | -0.028879 | 0.011252 | 0.15564 | 0.13137 | -0.20536 | 121.6197 | -0.6162 | 121.7113 | 121.7155 | 0.095859 | -0.63133 | -0.41647 | 121.5232 | -0.72117 | 121.8028 | 121.6996 | 0.17648 | -0.57678 | -0.60105 | 121.8447 | 121.8296 | 122.0445 | 121.762 | -0.84127 | 121.7398 | 121.8842 | 121.8599 | 121.8021 | -0.93778
6638.1562 | 122.7173 | -121.6919 | 0.70038 | -0.0025182 | -0.073615 | 0.036447 | 0.012845 | -0.016993 | 0.0077389 | -0.013887 | -0.02128 | -0.0080591 | 0.020658 | 0.059491 | -0.0016665 | -0.021844 | 0.038035 | -0.017566 | 0.1208 | 0.1011 | 0.31137 | -0.11342 | 0.074307 | 0.064461 | -0.028879 | 0.006674 | 0.1648 | 0.13595 | -0.20078 | 121.5785 | -0.57957 | 121.6701 | 121.6743 | 0.095859 | -0.59928 | -0.389 | 121.4911 | -0.6937 | 121.7662 | 121.663 | 0.1719 | -0.53558 | -0.56443 | 121.8127 | 121.793 | 122.0033 | 121.7299 | -0.8138 | 121.6986 | 121.8567 | 121.8278 | 121.7564 | -0.90116
6639.8594 | 122.731 | -121.7102 | 0.68665 | -0.010149 | -0.073828 | 0.036447 | 0.012631 | -0.016779 | 0.0077389 | -0.013887 | -0.021067 | -0.0080591 | 0.020871 | 0.059277 | -0.0018801 | -0.021844 | 0.038035 | -0.017566 | 0.11622 | 0.091937 | 0.31137 | -0.11342 | 0.078886 | 0.06904 | -0.038036 | 0.006674 | 0.16022 | 0.12679 | -0.20078 | 121.5968 | -0.57042 | 121.6884 | 121.6926 | 0.095859 | -0.59471 | -0.37527 | 121.5094 | -0.67997 | 121.7891 | 121.6722 | 0.16274 | -0.52642 | -0.55985 | 121.8264 | 121.8021 | 122.0216 | 121.7482 | -0.80007 | 121.7169 | 121.8704 | 121.837 | 121.7792 | -0.88743
6641.6094 | 122.5845 | -121.7239 | 0.74158 | -0.010149 | -0.073615 | 0.036233 | 0.013058 | -0.016779 | 0.0081663 | -0.036779 | -0.021067 | -0.0080591 | 0.020444 | 0.059491 | -0.0020939 | -0.026423 | 0.038035 | -0.017566 | 0.12538 | 0.1011 | 0.31137 | -0.10885 | 0.083464 | 0.078197 | -0.038036 | 0.015831 | 0.1648 | 0.13137 | -0.1962 | 121.6151 | -0.6162 | 121.6975 | 121.7064 | 0.091281 | -0.64048 | -0.4302 | 121.5277 | -0.72575 | 121.8074 | 121.6859 | 0.15816 | -0.57678 | -0.6102 | 121.8493 | 121.825 | 122.0353 | 121.762 | -0.85042 | 121.7398 | 121.8887 | 121.8553 | 121.8021 | -0.93778
6643.3125 | 122.6944 | -121.7102 | 0.69122 | -0.01778 | -0.073828 | 0.036447 | 0.012845 | -0.016779 | 0.0079525 | -0.021518 | -0.020853 | -0.0080591 | 0.020444 | 0.059704 | -0.0016665 | -0.017266 | 0.033457 | -0.017566 | 0.11622 | 0.096516 | 0.31595 | -0.11342 | 0.078886 | 0.073618 | -0.042615 | 0.011252 | 0.16022 | 0.13137 | -0.20078 | 121.5968 | -0.575 | 121.6929 | 121.6926 | 0.095859 | -0.59471 | -0.37527 | 121.5094 | -0.67997 | 121.7891 | 121.6676 | 0.15816 | -0.531 | -0.55985 | 121.8264 | 121.8067 | 122.0262 | 121.7437 | -0.80465 | 121.7215 | 121.8704 | 121.8416 | 121.7838 | -0.892
6645.0938 | 122.58 | -121.7468 | 0.74616 | -0.0025182 | -0.073401 | 0.036661 | 0.012845 | -0.016565 | 0.0079525 | -0.013887 | -0.021067 | -0.0080591 | 0.020444 | 0.059918 | -0.0016665 | -0.021844 | 0.033457 | -0.012988 | 0.1208 | 0.10567 | 0.31595 | -0.10885 | 0.088043 | 0.06904 | -0.038036 | 0.011252 | 0.16022 | 0.13137 | -0.20078 | 121.638 | -0.62535 | 121.725 | 121.7338 | 0.095859 | -0.64048 | -0.4302 | 121.546 | -0.7349 | 121.8349 | 121.7088 | 0.16274 | -0.58593 | -0.61478 | 121.8676 | 121.8525 | 122.0628 | 121.7803 | -0.855 | 121.7581 | 121.907 | 121.8782 | 121.8159 | -0.94693
6646.7969 | 122.6715 | -121.7194 | 0.68207 | -0.0025182 | -0.074042 | 0.036874 | 0.012631 | -0.016779 | 0.0077389 | -0.029148 | -0.02128 | -0.0078455 | 0.020444 | 0.059704 | -0.0018801 | -0.012688 | 0.038035 | -0.003831 | 0.1208 | 0.096516 | 0.31137 | -0.11342 | 0.078886 | 0.073618 | -0.033458 | 0.020409 | 0.15107 | 0.12222 | -0.19162 | 121.6059 | -0.56126 | 121.7067 | 121.7155 | 0.10959 | -0.58555 | -0.37069 | 121.5277 | -0.66166 | 121.7982 | 121.6859 | 0.15816 | -0.531 | -0.55985 | 121.8402 | 121.8159 | 122.0307 | 121.7574 | -0.79549 | 121.7398 | 121.8704 | 121.8416 | 121.793 | -0.87369
6648.5156 | 122.6303 | -121.7285 | 0.72784 | -0.010149 | -0.073615 | 0.036661 | 0.012631 | -0.016779 | 0.0077389 | -0.029148 | -0.021494 | -0.0078455 | 0.020444 | 0.059491 | -0.0018801 | -0.008109 | 0.042614 | -0.012988 | 0.11622 | 0.091937 | 0.31595 | -0.118 | 0.083464 | 0.073618 | -0.033458 | 0.011252 | 0.16022 | 0.12222 | -0.1962 | 121.6105 | -0.61162 | 121.7204 | 121.7155 | 0.10502 | -0.63591 | -0.41189 | 121.5323 | -0.71659 | 121.812 | 121.6951 | 0.16274 | -0.56762 | -0.60563 | 121.8447 | 121.8205 | 122.0445 | 121.7711 | -0.84585 | 121.7398 | 121.8887 | 121.8507 | 121.8021 | -0.92404
6650.2188 | 122.7036 | -121.7239 | 0.70496 | -0.010149 | -0.073615 | 0.036661 | 0.012417 | -0.016779 | 0.0079525 | -0.021518 | -0.021067 | -0.0080591 | 0.020871 | 0.059704 | -0.0016665 | -0.012688 | 0.038035 | -0.012988 | 0.1208 | 0.091937 | 0.31595 | -0.12258 | 0.078886 | 0.06904 | -0.038036 | 0.015831 | 0.1648 | 0.13137 | -0.1962 | 121.6014 | -0.58415 | 121.7113 | 121.7109 | 0.10959 | -0.61302 | -0.389 | 121.5277 | -0.68912 | 121.8028 | 121.6859 | 0.15816 | -0.54016 | -0.57358 | 121.8447 | 121.8159 | 122.0399 | 121.762 | -0.82754 | 121.7398 | 121.8887 | 121.8553 | 121.793 | -0.90116
6651.9375 | 122.7219 | -121.701 | 0.66834 | -0.01778 | -0.073615 | 0.036233 | 0.012845 | -0.016565 | 0.0079525 | -0.029148 | -0.02064 | -0.0082729 | 0.020444 | 0.059491 | -0.0018801 | -0.012688 | 0.042614 | -0.022144 | 0.1208 | 0.096516 | 0.31137 | -0.11342 | 0.088043 | 0.078197 | -0.038036 | 0.011252 | 0.17396 | 0.12679 | -0.1962 | 121.5876 | -0.54753 | 121.6884 | 121.6789 | 0.091281 | -0.57182 | -0.35696 | 121.5048 | -0.65708 | 121.7891 | 121.663 | 0.15816 | -0.49438 | -0.54154 | 121.8219 | 121.7976 | 122.0124 | 121.7437 | -0.78176 | 121.7123 | 121.875 | 121.8278 | 121.7792 | -0.86454
6653.7031 | 122.7173 | -121.7331 | 0.68207 | -0.025411 | -0.074256 | 0.036661 | 0.012631 | -0.016779 | 0.0079525 | -0.029148 | -0.02128 | -0.0078455 | 0.020658 | 0.059491 | -0.0018801 | -0.017266 | 0.033457 | -0.012988 | 0.1208 | 0.091937 | 0.3068 | -0.11342 | 0.088043 | 0.06904 | -0.033458 | 0.011252 | 0.15564 | 0.13137 | -0.1962 | 121.6197 | -0.56126 | 121.7158 | 121.7201 | 0.10044 | -0.59013 | -0.37527 | 121.5369 | -0.67082 | 121.8211 | 121.6996 | 0.16274 | -0.52643 | -0.5507 | 121.8539 | 121.825 | 122.0399 | 121.7665 | -0.79549 | 121.7443 | 121.8887 | 121.8645 | 121.8021 | -0.87827
6655.4062 | 122.6852 | -121.7102 | 0.70038 | -0.01778 | -0.074042 | 0.036447 | 0.013058 | -0.016993 | 0.0075253 | -0.021518 | -0.021067 | -0.0082729 | 0.020658 | 0.059491 | -0.0020939 | -0.012688 | 0.033457 | -0.017566 | 0.1208 | 0.091937 | 0.31137 | -0.10885 | 0.078886 | 0.06904 | -0.042615 | 0.011252 | 0.1648 | 0.13137 | -0.20536 | 121.6014 | -0.57957 | 121.6975 | 121.6926 | 0.091281 | -0.60844 | -0.389 | 121.5048 | -0.68913 | 121.7891 | 121.6676 | 0.16274 | -0.53558 | -0.569 | 121.831 | 121.8021 | 122.0216 | 121.7437 | -0.80922 | 121.7215 | 121.875 | 121.8416 | 121.7792 | -0.90574
6657.1094 | 122.6898 | -121.7285 | 0.70953 | -0.01778 | -0.074042 | 0.036447 | 0.013058 | -0.016565 | 0.0079525 | -0.021518 | -0.020853 | -0.0080591 | 0.020658 | 0.059704 | -0.0016665 | -0.017266 | 0.038035 | -0.008409 | 0.1208 | 0.096516 | 0.32053 | -0.11342 | 0.078886 | 0.073618 | -0.038036 | 0.011252 | 0.16022 | 0.13137 | -0.20078 | 121.6151 | -0.58873 | 121.7113 | 121.7201 | 0.10502 | -0.61302 | -0.389 | 121.5277 | -0.69828 | 121.8074 | 121.6905 | 0.16274 | -0.54931 | -0.57816 | 121.8493 | 121.825 | 122.049 | 121.7666 | -0.82296 | 121.7398 | 121.8887 | 121.8599 | 121.8021 | -0.91031
6658.8125 | 122.6212 | -121.7422 | 0.71411 | -0.025411 | -0.074042 | 0.036661 | 0.012417 | -0.016993 | 0.0077389 | -0.029148 | -0.02128 | -0.0078455 | 0.020871 | 0.059704 | -0.0016665 | -0.021844 | 0.038035 | -0.017566 | 0.11622 | 0.10567 | 0.31137 | -0.118 | 0.069728 | 0.073618 | -0.038036 | 0.011252 | 0.15564 | 0.13137 | -0.1962 | 121.6242 | -0.59789 | 121.7204 | 121.7247 | 0.10044 | -0.60844 | -0.40274 | 121.546 | -0.70286 | 121.812 | 121.7042 | 0.15816 | -0.55847 | -0.58274 | 121.8585 | 121.8479 | 122.0536 | 121.7803 | -0.83212 | 121.7535 | 121.8979 | 121.8736 | 121.8159 | -0.91031
6660.5625 | 122.5891 | -121.7468 | 0.70496 | -0.025411 | -0.073828 | 0.036661 | 0.012845 | -0.016565 | 0.0079525 | -0.029148 | -0.020853 | -0.0082729 | 0.020658 | 0.059704 | -0.0018801 | -0.012688 | 0.042614 | -0.012988 | 0.12538 | 0.096516 | 0.31595 | -0.11342 | 0.078886 | 0.078197 | -0.028879 | 0.006674 | 0.1648 | 0.13595 | -0.20078 | 121.6334 | -0.57957 | 121.7341 | 121.7338 | 0.10044 | -0.60844 | -0.389 | 121.546 | -0.69828 | 121.8257 | 121.7179 | 0.1719 | -0.54016 | -0.569 | 121.8722 | 121.8433 | 122.0628 | 121.7894 | -0.81838 | 121.7535 | 121.9116 | 121.8828 | 121.825 | -0.90574
6662.2656 | 122.699 | -121.7102 | 0.66834 | -0.01778 | -0.073615 | 0.036233 | 0.012845 | -0.016779 | 0.0075253 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059918 | -0.0018801 | -0.017266 | 0.038035 | -0.017566 | 0.12996 | 0.1011 | 0.31137 | -0.11342 | 0.078886 | 0.06904 | -0.033458 | 0.011252 | 0.1648 | 0.12679 | -0.20536 | 121.5968 | -0.53838 | 121.6929 | 121.6926 | 0.095859 | -0.56724 | -0.35696 | 121.5048 | -0.65708 | 121.7891 | 121.6767 | 0.1719 | -0.50354 | -0.54154 | 121.8402 | 121.8113 | 122.0216 | 121.7482 | -0.78176 | 121.7215 | 121.875 | 121.837 | 121.7792 | -0.87369
6664.0781 | 122.6028 | -121.7468 | 0.73242 | -0.010149 | -0.073828 | 0.036661 | 0.012631 | -0.016779 | 0.0077389 | -0.021518 | -0.02128 | -0.0078455 | 0.020658 | 0.059918 | -0.0014529 | -0.017266 | 0.038035 | -0.017566 | 0.11622 | 0.096516 | 0.31595 | -0.11342 | 0.074307 | 0.078197 | -0.033458 | 0.015831 | 0.16022 | 0.13137 | -0.19162 | 121.6334 | -0.6162 | 121.7296 | 121.7293 | 0.095859 | -0.63591 | -0.41647 | 121.5552 | -0.71659 | 121.8211 | 121.7134 | 0.15816 | -0.5722 | -0.60105 | 121.8631 | 121.8433 | 122.0628 | 121.7849 | -0.84585 | 121.7627 | 121.907 | 121.8782 | 121.825 | -0.92404
6665.8438 | 122.699 | -121.7422 | 0.66376 | -0.010149 | -0.074042 | 0.036447 | 0.013058 | -0.016779 | 0.0077389 | -0.021518 | -0.02128 | -0.0082729 | 0.020871 | 0.059918 | -0.0016665 | -0.012688 | 0.028878 | -0.012988 | 0.11622 | 0.10567 | 0.31137 | -0.11342 | 0.078886 | 0.073618 | -0.033458 | 0.006674 | 0.1648 | 0.13595 | -0.20078 | 121.6288 | -0.54753 | 121.7296 | 121.7293 | 0.10044 | -0.55808 | -0.35238 | 121.5415 | -0.65708 | 121.8211 | 121.7088 | 0.16732 | -0.49896 | -0.52781 | 121.8585 | 121.8479 | 122.0536 | 121.7711 | -0.77718 | 121.7489 | 121.907 | 121.8782 | 121.8159 | -0.86454
6667.625 | 122.6349 | -121.7606 | 0.72784 | -0.010149 | -0.073828 | 0.036661 | 0.012845 | -0.016993 | 0.0081663 | -0.013887 | -0.020853 | -0.0078455 | 0.020444 | 0.059918 | -0.0016665 | -0.012688 | 0.042614 | -0.012988 | 0.1208 | 0.096516 | 0.31137 | -0.10885 | 0.078886 | 0.073618 | -0.038036 | 0.015831 | 0.16022 | 0.12679 | -0.20078 | 121.6517 | -0.60704 | 121.7479 | 121.7476 | 0.095859 | -0.63133 | -0.41647 | 121.5598 | -0.71201 | 121.8394 | 121.7225 | 0.16274 | -0.56762 | -0.60105 | 121.8814 | 121.8571 | 122.0719 | 121.8032 | -0.83669 | 121.7764 | 121.9208 | 121.8874 | 121.8342 | -0.92862
6669.4062 | 122.5891 | -121.7651 | 0.71869 | 0.0051128 | -0.073828 | 0.036661 | 0.013058 | -0.016565 | 0.0077389 | -0.0062567 | -0.02128 | -0.0080591 | 0.020444 | 0.059704 | -0.0020939 | -0.017266 | 0.038035 | -0.012988 | 0.1208 | 0.1011 | 0.3068 | -0.118 | 0.078886 | 0.073618 | -0.038036 | 0.011252 | 0.15564 | 0.13137 | -0.1962 | 121.6471 | -0.59788 | 121.7479 | 121.7521 | 0.10502 | -0.61759 | -0.41189 | 121.5689 | -0.70744 | 121.844 | 121.7271 | 0.15816 | -0.56305 | -0.58732 | 121.8859 | 121.8662 | 122.0719 | 121.8032 | -0.83669 | 121.7764 | 121.9208 | 121.8965 | 121.8388 | -0.91489
6671.1094 | 122.6166 | -121.7377 | 0.74616 | -0.010149 | -0.073828 | 0.036447 | 0.012845 | -0.016779 | 0.0075253 | -0.013887 | -0.02128 | -0.0080591 | 0.020444 | 0.059918 | -0.0018801 | -0.017266 | 0.033457 | -0.012988 | 0.11622 | 0.096516 | 0.31137 | -0.10885 | 0.078886 | 0.064461 | -0.033458 | -0.002483 | 0.1648 | 0.12222 | -0.1962 | 121.6288 | -0.62993 | 121.7204 | 121.7247 | 0.095859 | -0.64964 | -0.43478 | 121.5415 | -0.74864 | 121.8166 | 121.7042 | 0.16274 | -0.58136 | -0.62394 | 121.8539 | 121.8342 | 122.049 | 121.7711 | -0.855 | 121.7352 | 121.9025 | 121.8599 | 121.8021 | -0.94236
6672.875 | 122.7173 | -121.6965 | 0.6958 | -0.01778 | -0.073615 | 0.036661 | 0.012845 | -0.016779 | 0.0077389 | -0.021518 | -0.021067 | -0.0082729 | 0.02023 | 0.059491 | -0.0020939 | -0.017266 | 0.038035 | -0.008409 | 0.12996 | 0.091937 | 0.3068 | -0.10885 | 0.074307 | 0.073618 | -0.028879 | 0.011252 | 0.1648 | 0.12679 | -0.20078 | 121.5876 | -0.56584 | 121.6792 | 121.6881 | 0.10044 | -0.60386 | -0.389 | 121.4957 | -0.68455 | 121.7708 | 121.6676 | 0.1719 | -0.531 | -0.56901 | 121.8264 | 121.7884 | 122.0033 | 121.7345 | -0.80465 | 121.7077 | 121.8613 | 121.8233 | 121.7701 | -0.89658
6674.6719 | 122.6303 | -121.7514 | 0.72327 | -0.01778 | -0.074042 | 0.036447 | 0.012631 | -0.016565 | 0.0081663 | -0.021518 | -0.02064 | -0.0078455 | 0.020658 | 0.059918 | -0.0023075 | -0.012688 | 0.042614 | -0.008409 | 0.12538 | 0.096516 | 0.31137 | -0.118 | 0.078886 | 0.06904 | -0.038036 | 0.011252 | 0.16022 | 0.13137 | -0.1962 | 121.6334 | -0.59788 | 121.7387 | 121.743 | 0.10959 | -0.62675 | -0.41189 | 121.5552 | -0.71201 | 121.8303 | 121.7134 | 0.15816 | -0.56305 | -0.59189 | 121.8768 | 121.8479 | 122.0628 | 121.794 | -0.84127 | 121.7627 | 121.9116 | 121.8828 | 121.8204 | -0.91947
6676.3906 | 122.6486 | -121.7331 | 0.70953 | -0.01778 | -0.074042 | 0.036661 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.020853 | -0.0078455 | 0.020658 | 0.059918 | -0.0016665 | -0.017266 | 0.038035 | -0.008409 | 0.12538 | 0.096516 | 0.3068 | -0.11342 | 0.078886 | 0.06904 | -0.038036 | 0.011252 | 0.1648 | 0.13137 | -0.19162 | 121.6197 | -0.58415 | 121.7158 | 121.7247 | 0.10502 | -0.61302 | -0.40274 | 121.5415 | -0.69828 | 121.812 | 121.6951 | 0.15359 | -0.54473 | -0.57816 | 121.8585 | 121.8296 | 122.0399 | 121.7711 | -0.82296 | 121.7443 | 121.8979 | 121.8645 | 121.8021 | -0.90116
6678.1562 | 122.6212 | -121.7239 | 0.74158 | -0.010149 | -0.073828 | 0.036661 | 0.013058 | -0.016993 | 0.0077389 | -0.021518 | -0.021067 | -0.0080591 | 0.020658 | 0.059918 | -0.0018801 | -0.021844 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.31137 | -0.11342 | 0.074307 | 0.073618 | -0.033458 | 0.011252 | 0.16938 | 0.13137 | -0.1962 | 121.6105 | -0.62535 | 121.7021 | 121.7155 | 0.10502 | -0.64964 | -0.4302 | 121.5277 | -0.73033 | 121.7982 | 121.6905 | 0.16274 | -0.5722 | -0.6102 | 121.8402 | 121.8159 | 122.0353 | 121.7574 | -0.855 | 121.7352 | 121.8933 | 121.8553 | 121.7976 | -0.93778
6679.9219 | 122.5891 | -121.7789 | 0.737 | 0.0051128 | -0.073401 | 0.036661 | 0.012845 | -0.016565 | 0.0079525 | -0.021518 | -0.021708 | -0.0080591 | 0.020658 | 0.059918 | -0.0020939 | -0.017266 | 0.042614 | -0.008409 | 0.1208 | 0.096516 | 0.32511 | -0.11342 | 0.083464 | 0.064461 | -0.038036 | 0.006674 | 0.1648 | 0.12679 | -0.1962 | 121.6654 | -0.6162 | 121.7616 | 121.7705 | 0.10502 | -0.64048 | -0.41189 | 121.5827 | -0.73033 | 121.8623 | 121.7408 | 0.15816 | -0.5722 | -0.61021 | 121.8997 | 121.8754 | 122.104 | 121.8215 | -0.85042 | 121.7855 | 121.9437 | 121.9057 | 121.8433 | -0.9332
6681.7031 | 122.6257 | -121.7468 | 0.73242 | -0.01778 | -0.074042 | 0.036874 | 0.012631 | -0.016565 | 0.0077389 | -0.029148 | -0.021067 | -0.0078455 | 0.020658 | 0.059704 | -0.0016665 | -0.017266 | 0.0243 | -0.012988 | 0.11622 | 0.096516 | 0.31595 | -0.11342 | 0.078886 | 0.073618 | -0.033458 | 0.011252 | 0.16022 | 0.12679 | -0.1962 | 121.6334 | -0.6162 | 121.7296 | 121.7338 | 0.10044 | -0.63591 | -0.41647 | 121.5506 | -0.72117 | 121.8257 | 121.7134 | 0.16274 | -0.5722 | -0.60563 | 121.8631 | 121.8433 | 122.0628 | 121.7711 | -0.84585 | 121.7581 | 121.907 | 121.8736 | 121.8204 | -0.92862
6683.4688 | 122.6898 | -121.7194 | 0.70953 | -0.025411 | -0.074042 | 0.036661 | 0.012631 | -0.016565 | 0.0077389 | -0.021518 | -0.021067 | -0.0080591 | 0.020444 | 0.059491 | -0.0020939 | -0.017266 | 0.033457 | -0.012988 | 0.12538 | 0.096516 | 0.31137 | -0.11342 | 0.078886 | 0.06904 | -0.038036 | 0.011252 | 0.16938 | 0.13137 | -0.20536 | 121.6059 | -0.58415 | 121.7021 | 121.7064 | 0.10044 | -0.61302 | -0.39816 | 121.514 | -0.69828 | 121.7982 | 121.6813 | 0.16732 | -0.54015 | -0.57816 | 121.8447 | 121.8159 | 122.0307 | 121.7528 | -0.82296 | 121.7306 | 121.8887 | 121.8507 | 121.7884 | -0.91489
6685.1719 | 122.6532 | -121.7422 | 0.70496 | -0.010149 | -0.074042 | 0.036447 | 0.012845 | -0.016565 | 0.0081663 | -0.021518 | -0.020853 | -0.0080591 | 0.020444 | 0.059918 | -0.0016665 | -0.021844 | 0.038035 | -0.017566 | 0.1208 | 0.091937 | 0.31137 | -0.11342 | 0.074307 | 0.064461 | -0.042615 | 0.006674 | 0.1648 | 0.13137 | -0.1962 | 121.6288 | -0.58415 | 121.7204 | 121.7247 | 0.095859 | -0.61302 | -0.39358 | 121.546 | -0.69828 | 121.8166 | 121.6996 | 0.15359 | -0.54016 | -0.57358 | 121.8631 | 121.8342 | 122.0536 | 121.7803 | -0.81838 | 121.7489 | 121.907 | 121.8736 | 121.8067 | -0.90116
6686.9375 | 122.6486 | -121.7285 | 0.71869 | -0.010149 | -0.073828 | 0.036661 | 0.012631 | -0.016352 | 0.0079525 | -0.021518 | -0.020853 | -0.0078455 | 0.020658 | 0.059704 | -0.0018801 | -0.012688 | 0.042614 | -0.012988 | 0.1208 | 0.096516 | 0.31595 | -0.11342 | 0.078886 | 0.078197 | -0.038036 | 0.006674 | 0.1648 | 0.13595 | -0.1962 | 121.6151 | -0.59788 | 121.7158 | 121.7155 | 0.10044 | -0.62217 | -0.40274 | 121.5323 | -0.71202 | 121.8074 | 121.6905 | 0.15816 | -0.55389 | -0.58274 | 121.8493 | 121.825 | 122.0445 | 121.7711 | -0.83211 | 121.7352 | 121.8933 | 121.8645 | 121.8067 | -0.91489
6688.7031 | 122.6852 | -121.6965 | 0.70038 | -0.0025182 | -0.073828 | 0.03602 | 0.012417 | -0.016565 | 0.0077389 | -0.029148 | -0.021067 | -0.0082729 | 0.02023 | 0.059704 | -0.0016665 | -0.021844 | 0.038035 | -0.012988 | 0.1208 | 0.091937 | 0.31137 | -0.10885 | 0.083464 | 0.073618 | -0.033458 | 0.015831 | 0.16022 | 0.13595 | -0.20536 | 121.5876 | -0.57957 | 121.6746 | 121.6835 | 0.095859 | -0.60844 | -0.389 | 121.4911 | -0.68455 | 121.7799 | 121.663 | 0.1719 | -0.54016 | -0.56443 | 121.8173 | 121.7884 | 122.0078 | 121.7345 | -0.80922 | 121.7123 | 121.8567 | 121.8324 | 121.7701 | -0.90574
6690.4062 | 122.6578 | -121.7285 | 0.71869 | -0.025411 | -0.073828 | 0.036233 | 0.012631 | -0.016352 | 0.0079525 | -0.021518 | -0.02128 | -0.0078455 | 0.020658 | 0.059704 | -0.0018801 | -0.021844 | 0.033457 | -0.012988 | 0.11622 | 0.096516 | 0.3068 | -0.10885 | 0.074307 | 0.078197 | -0.042615 | 0.015831 | 0.1648 | 0.13595 | -0.1962 | 121.6197 | -0.60246 | 121.7067 | 121.7155 | 0.095859 | -0.62217 | -0.41189 | 121.5323 | -0.70286 | 121.8028 | 121.6859 | 0.15359 | -0.55389 | -0.58274 | 121.8447 | 121.825 | 122.0353 | 121.762 | -0.82754 | 121.7443 | 121.8933 | 121.8645 | 121.8067 | -0.91489
6692.1719 | 122.7219 | -121.7285 | 0.70496 | -0.01778 | -0.073615 | 0.036233 | 0.012417 | -0.016565 | 0.0075253 | -0.013887 | -0.021067 | -0.0082729 | 0.020658 | 0.059491 | -0.0014529 | -0.017266 | 0.042614 | -0.008409 | 0.11622 | 0.096516 | 0.32053 | -0.118 | 0.088043 | 0.064461 | -0.033458 | 0.011252 | 0.16022 | 0.13137 | -0.20078 | 121.6105 | -0.58873 | 121.7113 | 121.7201 | 0.10959 | -0.60844 | -0.38443 | 121.5277 | -0.6937 | 121.8166 | 121.6951 | 0.16732 | -0.54473 | -0.57358 | 121.8447 | 121.825 | 122.049 | 121.7711 | -0.82296 | 121.7398 | 121.8887 | 121.8599 | 121.793 | -0.90574
6693.9375 | 122.5891 | -121.7651 | 0.73242 | -0.025411 | -0.074042 | 0.036447 | 0.012631 | -0.016779 | 0.0075253 | -0.021518 | -0.02128 | -0.0078455 | 0.020658 | 0.059491 | -0.0018801 | -0.017266 | 0.038035 | -0.008409 | 0.11622 | 0.091937 | 0.31137 | -0.118 | 0.074307 | 0.073618 | -0.038036 | 0.011252 | 0.16938 | 0.13595 | -0.1962 | 121.6471 | -0.6162 | 121.7479 | 121.7567 | 0.10959 | -0.64048 | -0.42105 | 121.5689 | -0.72117 | 121.8394 | 121.7271 | 0.15816 | -0.56304 | -0.59647 | 121.8814 | 121.8571 | 122.0765 | 121.8032 | -0.85043 | 121.7764 | 121.9345 | 121.9011 | 121.8388 | -0.92862
6695.7188 | 122.7127 | -121.7056 | 0.67749 | -0.01778 | -0.073828 | 0.036447 | 0.012631 | -0.016565 | 0.0081663 | -0.029148 | -0.021494 | -0.0080591 | 0.020658 | 0.059918 | -0.0020939 | -0.012688 | 0.047193 | -0.008409 | 0.12538 | 0.096516 | 0.31595 | -0.118 | 0.078886 | 0.073618 | -0.038036 | 0.011252 | 0.16022 | 0.13137 | -0.1962 | 121.5876 | -0.55211 | 121.6929 | 121.6972 | 0.10959 | -0.58097 | -0.36154 | 121.5094 | -0.66624 | 121.7845 | 121.6676 | 0.15816 | -0.51727 | -0.54612 | 121.831 | 121.8021 | 122.0216 | 121.7528 | -0.79549 | 121.7169 | 121.8658 | 121.837 | 121.7792 | -0.87369
6697.4062 | 122.6578 | -121.7422 | 0.71411 | -0.01778 | -0.074042 | 0.036447 | 0.012631 | -0.016565 | 0.0077389 | -0.036779 | -0.02128 | -0.0080591 | 0.020658 | 0.059277 | -0.0020939 | -0.012688 | 0.042614 | -0.008409 | 0.1208 | 0.096516 | 0.3068 | -0.11342 | 0.078886 | 0.06904 | -0.033458 | 0.011252 | 0.16022 | 0.13137 | -0.20078 | 121.6288 | -0.59331 | 121.7296 | 121.7338 | 0.10502 | -0.6176 | -0.40732 | 121.5415 | -0.70286 | 121.8211 | 121.7088 | 0.16732 | -0.55389 | -0.58274 | 121.8631 | 121.8388 | 122.049 | 121.7849 | -0.82754 | 121.7535 | 121.9025 | 121.8736 | 121.8113 | -0.91489
6699.1719 | 122.6898 | -121.7239 | 0.68207 | -0.01778 | -0.073828 | 0.036233 | 0.012631 | -0.016352 | 0.0075253 | -0.021518 | -0.021067 | -0.0082729 | 0.020444 | 0.059704 | -0.0020939 | -0.012688 | 0.033457 | -0.008409 | 0.11622 | 0.091937 | 0.32053 | -0.10885 | 0.078886 | 0.073618 | -0.033458 | 0.006674 | 0.15564 | 0.12679 | -0.1962 | 121.6151 | -0.56584 | 121.7113 | 121.7155 | 0.10044 | -0.59013 | -0.36154 | 121.5277 | -0.67539 | 121.8028 | 121.6905 | 0.16274 | -0.52643 | -0.55527 | 121.8402 | 121.8159 | 122.0445 | 121.7574 | -0.79092 | 121.7306 | 121.8796 | 121.8507 | 121.7976 | -0.87827
6700.9531 | 122.6578 | -121.7377 | 0.72327 | -0.010149 | -0.074042 | 0.036447 | 0.012417 | -0.016565 | 0.0075253 | -0.021518 | -0.021494 | -0.0080591 | 0.020871 | 0.059704 | -0.0020939 | -0.012688 | 0.028878 | -0.008409 | 0.1208 | 0.096516 | 0.31595 | -0.118 | 0.083464 | 0.073618 | -0.033458 | 0.015831 | 0.16022 | 0.12679 | -0.19162 | 121.6197 | -0.60246 | 121.725 | 121.7293 | 0.10959 | -0.62675 | -0.40731 | 121.546 | -0.70744 | 121.8211 | 121.7042 | 0.15816 | -0.56305 | -0.59647 | 121.8585 | 121.8342 | 122.0536 | 121.7665 | -0.84127 | 121.7535 | 121.8979 | 121.8645 | 121.8113 | -0.91489
6702.7188 | 122.7219 | -121.7148 | 0.70496 | -0.01778 | -0.073828 | 0.036233 | 0.012631 | -0.016993 | 0.0077389 | -0.021518 | -0.02128 | -0.0082729 | 0.020658 | 0.059918 | -0.0018801 | -0.012688 | 0.038035 | -0.003831 | 0.11622 | 0.096516 | 0.31137 | -0.10885 | 0.083464 | 0.064461 | -0.038036 | 0.011252 | 0.15564 | 0.13137 | -0.20078 | 121.6059 | -0.58873 | 121.7021 | 121.711 | 0.10502 | -0.60844 | -0.39358 | 121.514 | -0.6937 | 121.7982 | 121.6767 | 0.16274 | -0.54931 | -0.57358 | 121.831 | 121.8113 | 122.0262 | 121.7528 | -0.8138 | 121.726 | 121.8704 | 121.8462 | 121.7792 | -0.90574
6704.4219 | 122.7219 | -121.7102 | 0.69122 | -0.01778 | -0.074042 | 0.036661 | 0.012631 | -0.016779 | 0.0075253 | -0.029148 | -0.021067 | -0.0078455 | 0.021085 | 0.060132 | -0.0014529 | -0.017266 | 0.038035 | -0.008409 | 0.12538 | 0.1011 | 0.32053 | -0.11342 | 0.074307 | 0.06904 | -0.033458 | 0.006674 | 0.16022 | 0.12679 | -0.20078 | 121.5968 | -0.56584 | 121.6929 | 121.7018 | 0.10502 | -0.59013 | -0.37069 | 121.5094 | -0.68455 | 121.7845 | 121.6767 | 0.16732 | -0.531 | -0.56443 | 121.8356 | 121.8113 | 122.0307 | 121.7482 | -0.80465 | 121.7169 | 121.8704 | 121.837 | 121.7792 | -0.892
6706.1875 | 122.7219 | -121.7422 | 0.6958 | -0.0025182 | -0.073615 | 0.036447 | 0.012845 | -0.016779 | 0.0075253 | -0.029148 | -0.02128 | -0.0082729 | 0.020444 | 0.059918 | -0.0020939 | -0.017266 | 0.038035 | -0.017566 | 0.12538 | 0.087359 | 0.32053 | -0.118 | 0.078886 | 0.06904 | -0.033458 | 0.011252 | 0.16938 | 0.13137 | -0.19162 | 121.6242 | -0.57042 | 121.725 | 121.7247 | 0.10044 | -0.60844 | -0.37527 | 121.5506 | -0.68455 | 121.8211 | 121.7088 | 0.15816 | -0.52642 | -0.56443 | 121.8676 | 121.8296 | 122.0628 | 121.7803 | -0.81381 | 121.7535 | 121.9116 | 121.8736 | 121.8113 | -0.88742
6707.8906 | 122.6898 | -121.7514 | 0.71411 | -0.01778 | -0.074042 | 0.036874 | 0.012631 | -0.016565 | 0.0077389 | -0.013887 | -0.021067 | -0.0078455 | 0.020658 | 0.059918 | -0.0020939 | -0.012688 | 0.028878 | -0.017566 | 0.1208 | 0.10567 | 0.31137 | -0.11342 | 0.088043 | 0.06904 | -0.038036 | 0.006674 | 0.15564 | 0.13595 | -0.19162 | 121.638 | -0.59331 | 121.7387 | 121.7338 | 0.095859 | -0.60844 | -0.40274 | 121.5598 | -0.70744 | 121.8394 | 121.7134 | 0.15359 | -0.55847 | -0.57816 | 121.8722 | 121.8571 | 122.0628 | 121.7803 | -0.82754 | 121.7581 | 121.907 | 121.8874 | 121.8204 | -0.90573
6709.6719 | 122.6028 | -121.8018 | 0.73242 | -0.01778 | -0.073615 | 0.036447 | 0.012845 | -0.016779 | 0.0077389 | -0.021518 | -0.021067 | -0.0082729 | 0.020658 | 0.059491 | -0.0020939 | -0.021844 | 0.038035 | -0.008409 | 0.11622 | 0.1011 | 0.3068 | -0.11342 | 0.078886 | 0.073618 | -0.038036 | 0.006674 | 0.1648 | 0.12222 | -0.19162 | 121.6883 | -0.6162 | 121.7799 | 121.7933 | 0.10502 | -0.63133 | -0.42563 | 121.6101 | -0.72575 | 121.8806 | 121.7637 | 0.15359 | -0.56762 | -0.61021 | 121.918 | 121.9029 | 122.1086 | 121.8398 | -0.84585 | 121.8084 | 121.9666 | 121.924 | 121.8754 | -0.92404
6711.4375 | 122.5983 | -121.7972 | 0.71411 | -0.0025182 | -0.073828 | 0.036661 | 0.012631 | -0.016779 | 0.0075253 | -0.029148 | -0.02128 | -0.0078455 | 0.02023 | 0.059704 | -0.0020939 | -0.012688 | 0.028878 | -0.012988 | 0.11622 | 0.091937 | 0.3068 | -0.118 | 0.083464 | 0.073618 | -0.033458 | 0.006674 | 0.16938 | 0.13137 | -0.20078 | 121.6792 | -0.59789 | 121.7845 | 121.7842 | 0.10502 | -0.62217 | -0.40732 | 121.5964 | -0.70744 | 121.8806 | 121.7637 | 0.16732 | -0.54473 | -0.58274 | 121.9134 | 121.8891 | 122.104 | 121.8261 | -0.83212 | 121.8039 | 121.9666 | 121.9286 | 121.8708 | -0.91489
6713.1562 | 122.5891 | -121.7743 | 0.70038 | -0.01778 | -0.073615 | 0.036447 | 0.012204 | -0.016779 | 0.0073115 | -0.013887 | -0.02128 | -0.0082729 | 0.020444 | 0.059704 | -0.0016665 | -0.017266 | 0.042614 | -0.008409 | 0.1208 | 0.11025 | 0.31595 | -0.118 | 0.074307 | 0.073618 | -0.042615 | 0.015831 | 0.16022 | 0.14053 | -0.1962 | 121.6563 | -0.57957 | 121.757 | 121.7659 | 0.10959 | -0.59012 | -0.38442 | 121.5781 | -0.68455 | 121.8486 | 121.7317 | 0.15359 | -0.54016 | -0.55985 | 121.8951 | 121.8845 | 122.0902 | 121.8169 | -0.81838 | 121.7901 | 121.9345 | 121.9148 | 121.8479 | -0.89658
6714.9375 | 122.6532 | -121.756 | 0.72784 | -0.010149 | -0.074042 | 0.036447 | 0.012417 | -0.016779 | 0.0077389 | -0.021518 | -0.02128 | -0.0080591 | 0.020658 | 0.059918 | -0.0016665 | -0.017266 | 0.038035 | -0.012988 | 0.1208 | 0.1011 | 0.31137 | -0.11342 | 0.074307 | 0.073618 | -0.038036 | 0.011252 | 0.16938 | 0.13137 | -0.18704 | 121.6426 | -0.60704 | 121.7387 | 121.743 | 0.10044 | -0.62675 | -0.41647 | 121.5689 | -0.71659 | 121.8303 | 121.7179 | 0.14901 | -0.55846 | -0.59647 | 121.8768 | 121.8571 | 122.0674 | 121.794 | -0.84127 | 121.7672 | 121.9254 | 121.8874 | 121.8296 | -0.91489
6716.7031 | 122.7402 | -121.7422 | 0.68665 | -0.01778 | -0.074042 | 0.036447 | 0.012631 | -0.016779 | 0.0081663 | -0.021518 | -0.021708 | -0.0078455 | 0.020444 | 0.059918 | -0.0018801 | -0.021844 | 0.038035 | -0.008409 | 0.1208 | 0.091937 | 0.31595 | -0.12258 | 0.074307 | 0.073618 | -0.033458 | 0.011252 | 0.16022 | 0.12679 | -0.19162 | 121.6197 | -0.56584 | 121.7204 | 121.7338 | 0.11417 | -0.59471 | -0.37069 | 121.5506 | -0.67539 | 121.8166 | 121.7088 | 0.15816 | -0.52642 | -0.55985 | 121.8631 | 121.8342 | 122.0582 | 121.7803 | -0.80923 | 121.7535 | 121.9025 | 121.869 | 121.8159 | -0.87827
6718.4688 | 122.731 | -121.7102 | 0.68207 | -0.010149 | -0.074042 | 0.036874 | 0.012417 | -0.016138 | 0.0077389 | -0.036779 | -0.021067 | -0.0078455 | 0.020444 | 0.060132 | -0.0018801 | -0.021844 | 0.038035 | -0.008409 | 0.11165 | 0.1011 | 0.3068 | -0.118 | 0.078886 | 0.073618 | -0.038036 | 0.015831 | 0.16938 | 0.14053 | -0.20078 | 121.5922 | -0.57042 | 121.6884 | 121.7018 | 0.10959 | -0.58097 | -0.37527 | 121.5094 | -0.66624 | 121.7891 | 121.6722 | 0.16274 | -0.51269 | -0.54154 | 121.8219 | 121.8113 | 122.017 | 121.7482 | -0.80007 | 121.726 | 121.8796 | 121.8507 | 121.7838 | -0.88285
6720.1719 | 122.7448 | -121.7285 | 0.68665 | -0.01778 | -0.074042 | 0.036661 | 0.012417 | -0.016565 | 0.0077389 | -0.021518 | -0.020853 | -0.0082729 | 0.02023 | 0.059918 | -0.0018801 | -0.012688 | 0.042614 | -0.008409 | 0.1208 | 0.091937 | 0.32053 | -0.11342 | 0.078886 | 0.06904 | -0.038036 | 0.006674 | 0.16022 | 0.12679 | -0.1962 | 121.6151 | -0.56584 | 121.7158 | 121.7201 | 0.10502 | -0.59471 | -0.36611 | 121.5323 | -0.67997 | 121.8074 | 121.6905 | 0.15816 | -0.52642 | -0.55985 | 121.8493 | 121.8205 | 122.049 | 121.7711 | -0.80007 | 121.7352 | 121.8887 | 121.8553 | 121.7976 | -0.88285

## Thermal Data
Fire Time | A Position - Middle | C Position - 3' | C Position - Middle | C Position - 7'
-0.824 | 14.5974 | 14.8155 | 15.217 | 14.7636
0.176 | 14.6021 | 14.8133 | 15.2177 | 14.7621
1.176 | 14.6035 | 14.8153 | 15.2295 | 14.7704
2.176 | 14.5998 | 14.8219 | 15.2306 | 14.7688
3.176 | 15.8467 | 14.8449 | 15.2605 | 14.772
4.176 | 24.1941 | 15.0865 | 15.6375 | 14.8511
5.176 | 75.6817 | 17.0404 | 16.5021 | 15.0298
6.176 | 125.1002 | 17.1355 | 17.1838 | 15.4326
7.176 | 171.0603 | 19.4733 | 17.8887 | 19.9381
8.176 | 235.8329 | 27.3443 | 21.3964 | 27.038
9.176 | 272.7015 | 36.5192 | 29.2955 | 34.5256
10.176 | 292.705 | 43.646 | 38.575 | 44.6374
11.176 | 331.7906 | 54.2249 | 51.3933 | 57.4371
12.176 | 363.0439 | 65.0258 | 59.1359 | 69.3152
13.176 | 401.9252 | 73.2157 | 67.3005 | 76.2894
14.176 | 445.7763 | 82.0107 | 75.619 | 82.6338
15.176 | 470.2591 | 92.0344 | 86.3722 | 92.8463
16.176 | 499.3719 | 102.1046 | 96.6951 | 103.0482
17.176 | 534.0854 | 113.1665 | 104.3465 | 108.9498
18.176 | 547.0071 | 118.6469 | 112.204 | 115.6768
19.176 | 572.4352 | 125.1636 | 119.6569 | 120.9223
20.1917 | 592.3685 | 134.0076 | 126.1685 | 125.6585
21.176 | 601.55 | 139.8919 | 131.2133 | 133.7241
22.176 | 575.231 | 145.3035 | 138.2293 | 138.1772
23.176 | 544.5007 | 149.1843 | 141.461 | 141.0954
24.176 | 517.2794 | 150.9171 | 144.2963 | 144.4401
25.176 | 491.4691 | 151.807 | 145.8702 | 145.8694
26.176 | 467.2013 | 152.7257 | 147.4288 | 146.7956
27.176 | 445.4239 | 153.3878 | 148.0748 | 147.721
28.176 | 424.6221 | 153.2801 | 148.2715 | 148.7052
29.176 | 406.1741 | 152.703 | 149.2095 | 148.5611
30.176 | 390.3865 | 152.3785 | 148.5297 | 147.9382
31.176 | 375.0042 | 151.6781 | 148.1499 | 147.2675
32.176 | 360.4217 | 150.7961 | 146.292 | 146.6413
33.176 | 347.2752 | 148.6524 | 144.2532 | 144.7196
34.176 | 333.4999 | 146.4223 | 141.8555 | 142.6447
35.176 | 321.9357 | 144.3374 | 140.1622 | 140.5785
36.176 | 312.365 | 142.1792 | 138.3048 | 138.8582
37.176 | 301.4327 | 140.2902 | 136.7304 | 137.0759
38.176 | 290.4635 | 138.0443 | 135.2438 | 135.4835
39.176 | 281.7924 | 135.7828 | 133.784 | 133.5436
40.176 | 274.6901 | 134.1038 | 132.6276 | 131.9602
41.176 | 266.4722 | 132.311 | 131.2477 | 130.4699
42.176 | 257.3537 | 130.7781 | 129.6788 | 129.0076
43.176 | 250.505 | 129.2509 | 128.4101 | 127.4901
44.176 | 243.4414 | 127.8137 | 126.8604 | 126.0263
45.176 | 237.0907 | 126.4274 | 125.4756 | 124.1803
46.176 | 231.8668 | 124.9631 | 124.4018 | 122.6545
47.176 | 228.3067 | 123.4459 | 123.2894 | 121.3199
48.176 | 223.9734 | 122.0972 | 122.1394 | 120.2212
49.176 | 219.7054 | 120.8513 | 120.8443 | 119.0656
50.1917 | 215.0432 | 119.5549 | 119.6484 | 117.7605
51.176 | 210.4843 | 118.4544 | 118.4221 | 116.5569
52.176 | 206.8332 | 117.363 | 117.36 | 115.5967
53.176 | 202.5424 | 116.4616 | 116.168 | 114.6527
54.176 | 199.1132 | 115.3869 | 115.3233 | 113.5497
55.176 | 196.5114 | 114.3322 | 114.2107 | 112.3155
56.176 | 192.8739 | 113.2627 | 113.2474 | 111.5217
57.176 | 189.543 | 112.0633 | 112.2799 | 110.6162
58.176 | 185.9531 | 111.1648 | 111.4688 | 109.835
59.176 | 183.3884 | 110.4569 | 110.601 | 108.9996
60.176 | 181.613 | 109.5897 | 109.8781 | 107.897
61.176 | 179.3229 | 108.8386 | 109.2119 | 106.676
62.176 | 176.8805 | 108.14 | 108.477 | 105.8627
63.176 | 174.467 | 107.4701 | 107.8894 | 105.0678
64.176 | 172.7977 | 106.68 | 107.1313 | 104.3515
65.176 | 170.9575 | 105.9426 | 106.4504 | 103.6831
66.176 | 169.9712 | 105.2966 | 105.8253 | 102.9659
67.176 | 169.0198 | 104.7378 | 105.3187 | 102.3051
68.176 | 167.9003 | 104.1551 | 104.827 | 101.6494
69.176 | 167.7536 | 103.4865 | 104.2659 | 100.9606
70.176 | 167.716 | 102.9911 | 103.7387 | 100.3378
71.176 | 167.1633 | 102.8075 | 103.2863 | 99.7587
72.176 | 167.6075 | 102.2784 | 102.9495 | 99.226
73.176 | 168.3032 | 102.4921 | 103.461 | 99.0804
74.176 | 168.0317 | 102.1755 | 102.8802 | 98.3759
75.176 | 167.8261 | 102.0219 | 102.8294 | 98.3868
76.176 | 169.1113 | 102.5577 | 103.2778 | 98.4692
77.176 | 168.5801 | 102.8549 | 102.9452 | 98.4295
78.176 | 168.8154 | 103.0423 | 102.886 | 98.2959
79.176 | 168.408 | 103.2239 | 102.9364 | 98.1595
80.176 | 168.0698 | 102.7727 | 102.8393 | 98.2887
81.176 | 167.8955 | 102.7581 | 102.8396 | 98.4608
82.176 | 167.2181 | 102.8772 | 102.835 | 98.5076
83.176 | 169.0081 | 103.0808 | 102.7806 | 98.318
84.176 | 168.11 | 103.2395 | 102.9721 | 98.0826
85.176 | 168.0089 | 103.2357 | 102.9727 | 98.1662
86.176 | 168.1319 | 103.2965 | 103.2332 | 98.2492
87.176 | 167.9652 | 103.7014 | 103.4062 | 98.5452
88.176 | 168.5189 | 103.6907 | 103.62 | 98.6627
89.176 | 168.0579 | 103.9863 | 103.8232 | 99.9172
90.176 | 170.0289 | 103.9334 | 104.0561 | 100.398
91.176 | 172.7381 | 103.9869 | 104.1832 | 100.5865
92.176 | 175.029 | 104.1902 | 104.5961 | 100.5207
93.176 | 176.8192 | 104.6738 | 104.9811 | 100.6892
94.176 | 177.2703 | 105.3986 | 105.3875 | 101.1293
95.176 | 178.0541 | 105.5994 | 105.8231 | 101.7823
96.176 | 182.9193 | 105.9798 | 106.1945 | 102.0094
97.176 | 184.3078 | 106.91 | 106.528 | 102.4996
98.176 | 185.1999 | 107.1072 | 106.869 | 103.3059
99.176 | 185.6368 | 107.5063 | 107.4466 | 104.0495
100.176 | 187.648 | 107.7947 | 108.0942 | 104.405
101.176 | 191.4394 | 108.6375 | 108.8132 | 105.0246
102.176 | 195.5721 | 109.6365 | 109.5085 | 105.3947
103.176 | 197.2138 | 110.1191 | 110.3241 | 106.0488
104.176 | 197.9922 | 111.1618 | 110.6981 | 106.1346
105.176 | 199.9803 | 111.3521 | 111.1452 | 106.3835
106.176 | 201.7736 | 111.8079 | 111.982 | 106.9105
107.176 | 203.3357 | 112.9482 | 112.5558 | 107.2175
108.176 | 202.6431 | 113.4956 | 113.458 | 107.6425
109.176 | 203.5792 | 113.8256 | 113.9367 | 108.0969
110.176 | 203.3548 | 114.7881 | 114.4041 | 108.6997
111.176 | 204.3948 | 114.5777 | 114.955 | 109.1292
112.176 | 203.6665 | 115.3614 | 115.7301 | 109.2483
113.176 | 204.1564 | 116.4522 | 116.4097 | 109.7951
114.176 | 203.379 | 116.2417 | 116.907 | 110.0101
115.176 | 206.3786 | 116.6154 | 117.2732 | 110.4469
116.176 | 203.9346 | 117.6394 | 117.8143 | 110.9511
117.176 | 202.4652 | 118.9587 | 118.1259 | 111.0487
118.176 | 201.6092 | 119.4345 | 118.4425 | 111.711
119.176 | 200.8861 | 119.466 | 118.9097 | 111.7784
120.176 | 201.2786 | 119.5956 | 119.2682 | 112.5309
121.176 | 201.3081 | 119.6735 | 119.6511 | 113.2617
122.176 | 200.512 | 119.7413 | 119.8241 | 113.7381
123.176 | 199.5924 | 119.763 | 119.8397 | 114.1107
124.176 | 197.415 | 119.597 | 119.887 | 114.2818
125.176 | 196.66 | 119.7898 | 120.2368 | 114.8901
126.176 | 196.1483 | 119.9772 | 120.1987 | 114.6244
127.176 | 196.0408 | 119.95 | 120.1095 | 115.2169
128.176 | 194.841 | 120.0138 | 120.1686 | 114.7567
129.176 | 194.1698 | 119.943 | 120.5253 | 114.8656
130.176 | 193.8522 | 120.1014 | 120.6021 | 115.4795
131.176 | 194.0384 | 120.2143 | 120.7794 | 115.3684
132.176 | 193.6364 | 120.3879 | 121.2664 | 115.4517
133.176 | 193.2731 | 120.5982 | 121.3823 | 115.3372
134.176 | 192.8322 | 120.8619 | 121.2546 | 115.2288
135.176 | 193.6136 | 121.0698 | 121.194 | 115.1104
136.176 | 195.2143 | 121.1859 | 121.2515 | 115.0147
137.176 | 195.1866 | 121.4062 | 121.7358 | 115.3371
138.176 | 194.3946 | 121.9442 | 121.5511 | 115.3313
139.176 | 193.9043 | 121.9363 | 121.7118 | 115.3249
140.176 | 193.3676 | 122.2202 | 121.6666 | 115.2232
141.176 | 192.5621 | 122.5427 | 121.7314 | 115.2551
142.176 | 190.5677 | 122.7991 | 121.4575 | 115.458
143.176 | 189.8709 | 123.2665 | 121.233 | 115.448
144.176 | 189.3413 | 123.2706 | 121.2286 | 115.3966
145.176 | 188.3774 | 123.8849 | 121.3356 | 115.2839
146.176 | 186.5467 | 123.8509 | 121.3968 | 115.4373
147.176 | 184.7447 | 123.8377 | 121.326 | 115.3562
148.176 | 183.2552 | 124.37 | 121.4092 | 115.7358
149.176 | 181.877 | 124.4584 | 121.364 | 115.9125
150.176 | 179.7803 | 124.7408 | 121.487 | 116.1752
151.176 | 178.8665 | 124.4435 | 121.5393 | 116.4315
152.176 | 178.8875 | 124.4445 | 121.6135 | 116.9064
153.176 | 179.5321 | 124.2044 | 121.5871 | 116.7816
154.176 | 179.2533 | 123.915 | 121.5191 | 117.0069
155.176 | 178.4886 | 123.8004 | 121.9411 | 117.2803
156.176 | 178.0174 | 124.123 | 122.06 | 117.366
157.176 | 178.2354 | 124.1737 | 121.9276 | 117.454
158.176 | 178.9041 | 123.6704 | 121.745 | 117.3438
159.176 | 181.1594 | 123.3329 | 121.9266 | 117.4568
160.176 | 182.095 | 123.2183 | 122.0295 | 117.3624
161.176 | 182.8672 | 123.1253 | 122.332 | 117.4204
162.176 | 183.8417 | 122.9381 | 122.4008 | 117.3448
163.176 | 184.4135 | 122.893 | 122.4358 | 117.4344
164.176 | 185.2967 | 123.0403 | 122.5352 | 117.6488
165.176 | 184.1036 | 123.6688 | 122.6321 | 117.556
166.176 | 182.7196 | 124.2153 | 122.6897 | 117.7303
167.176 | 182.2494 | 124.2177 | 122.6806 | 117.5377
168.176 | 182.0087 | 124.9099 | 123.1286 | 118.3335
169.176 | 181.7288 | 125.032 | 123.3814 | 118.6363
170.176 | 182.1133 | 125.1716 | 123.6755 | 118.3629
171.176 | 181.6552 | 125.448 | 123.799 | 118.199
172.176 | 181.3283 | 125.5315 | 124.1867 | 118.3612
173.176 | 181.641 | 125.4659 | 124.1762 | 118.3446
174.176 | 181.525 | 125.4173 | 124.1482 | 118.7576
175.176 | 181.5872 | 125.4644 | 124.1462 | 119.2468
176.176 | 180.2342 | 125.6608 | 124.4142 | 119.3169
177.176 | 179.8338 | 126.0685 | 124.6016 | 119.8788
178.176 | 178.768 | 126.2607 | 124.7665 | 119.6085
179.176 | 177.2469 | 126.1364 | 124.9118 | 119.7034
180.176 | 176.3778 | 126.262 | 124.9775 | 119.9095
181.176 | 176.0532 | 126.2082 | 125.0461 | 120.1459
182.176 | 176.718 | 126.2755 | 125.132 | 120.5675
183.176 | 176.5472 | 125.8976 | 125.0104 | 120.8604
184.176 | 177.4263 | 125.529 | 125.0103 | 121.2309
185.176 | 176.7752 | 125.5764 | 125.0111 | 121.5321
186.176 | 177.214 | 125.5258 | 125.1596 | 122.0071
187.176 | 177.3372 | 125.6985 | 125.045 | 122.161
188.176 | 176.5929 | 126.1722 | 125.121 | 122.2842
189.176 | 177.1552 | 126.3217 | 124.9431 | 122.525
190.176 | 176.7722 | 126.8145 | 125.0107 | 122.7097
191.176 | 176.2661 | 127.039 | 125.1507 | 122.6583
192.176 | 176.2988 | 127.3777 | 125.2023 | 122.5222
193.176 | 176.4797 | 127.647 | 125.3522 | 122.1945
194.176 | 180.5747 | 127.7147 | 125.3938 | 122.731
195.176 | 180.9709 | 127.9578 | 125.4521 | 122.7348
196.176 | 181.0967 | 128.241 | 125.7744 | 122.7336
197.176 | 181.0319 | 128.3211 | 125.9713 | 122.7681
198.176 | 180.4158 | 128.3184 | 126.268 | 122.8944
199.176 | 180.5533 | 128.8579 | 126.5189 | 122.8003
200.1917 | 182.9309 | 128.3263 | 126.6676 | 123.0289
201.176 | 183.6228 | 128.6423 | 127.0767 | 123.1543
202.176 | 183.4819 | 128.6202 | 127.2347 | 123.4209
203.176 | 184.1455 | 128.8334 | 127.207 | 123.6735
204.176 | 186.3758 | 129.6249 | 127.1821 | 124.4856
205.176 | 186.5494 | 129.8594 | 127.3952 | 124.5956
206.176 | 188.2468 | 130.2755 | 127.7718 | 125.1093
207.176 | 188.2043 | 130.4236 | 128.1209 | 125.5551
208.176 | 188.7156 | 130.5743 | 128.4479 | 126.0532
209.176 | 188.5034 | 130.7996 | 128.8824 | 126.2371
210.176 | 188.4163 | 130.9432 | 129.0894 | 126.2472
211.176 | 189.5974 | 130.6789 | 129.3312 | 126.4426
212.176 | 192.4238 | 130.5131 | 129.5701 | 127.0772
213.176 | 192.5362 | 130.6929 | 129.7388 | 127.2119
214.176 | 191.7959 | 131.0885 | 129.8467 | 127.0974
215.176 | 191.0976 | 131.4598 | 129.8057 | 126.8785
216.176 | 192.0032 | 132.2916 | 129.9075 | 126.5484
217.176 | 190.436 | 132.3071 | 130.215 | 126.9786
218.176 | 190.18 | 132.6786 | 130.4455 | 126.6046
219.176 | 190.0977 | 132.6638 | 130.6581 | 127.2603
220.176 | 190.5381 | 132.7902 | 130.919 | 127.5848
221.176 | 193.3239 | 132.9892 | 131.0826 | 127.717
222.176 | 195.4017 | 133.0442 | 131.3704 | 127.4312
223.176 | 196.2621 | 133.0415 | 131.6525 | 127.615
224.176 | 196.6068 | 134.0483 | 131.806 | 128.006
225.176 | 197.5989 | 134.4948 | 132.19 | 128.8623
226.176 | 197.2192 | 134.5567 | 132.8852 | 129.7853
227.176 | 196.3667 | 135.1574 | 133.2164 | 130.9058
228.176 | 195.5817 | 135.6657 | 133.9124 | 131.1443
229.176 | 194.923 | 135.6983 | 133.9912 | 131.0526
230.176 | 193.9742 | 135.8632 | 134.2068 | 131.3163
231.176 | 193.5343 | 136.1446 | 134.64 | 131.7922
232.176 | 192.9048 | 136.7506 | 134.9003 | 131.4013
233.176 | 192.8061 | 136.9849 | 135.0361 | 131.5857
234.176 | 193.4086 | 137.7036 | 136.0176 | 131.7095
235.176 | 191.5031 | 137.8509 | 135.6662 | 131.4917
236.176 | 192.4609 | 137.5614 | 135.8115 | 131.908
237.176 | 192.6156 | 137.1459 | 136.1162 | 131.7801
238.176 | 193.2115 | 137.0149 | 136.4477 | 131.9195
239.176 | 193.2144 | 137.0037 | 136.7813 | 132.5474
240.176 | 192.1352 | 137.2491 | 136.9263 | 133.1112
241.176 | 190.8415 | 137.5853 | 137.7789 | 133.0914
242.176 | 189.535 | 138.1081 | 138.3024 | 132.6731
243.176 | 187.724 | 138.116 | 138.7752 | 132.6782
244.176 | 187.7378 | 138.4476 | 138.4978 | 133.1831
245.176 | 187.3969 | 138.4146 | 138.351 | 133.0527
246.176 | 186.9679 | 138.5293 | 138.514 | 132.953
247.176 | 186.817 | 139.0734 | 138.6804 | 132.9001
248.176 | 186.2548 | 139.5804 | 138.6559 | 133.1786
249.176 | 186.5773 | 139.6798 | 138.5524 | 133.2545
250.176 | 187.033 | 139.2748 | 138.7274 | 133.14
251.176 | 187.466 | 139.1421 | 138.9562 | 133.1895
252.176 | 187.5512 | 139.4349 | 139.0024 | 133.955
253.176 | 188.5882 | 139.8943 | 139.2609 | 134.0727
254.176 | 189.4786 | 140.0142 | 139.2974 | 133.976
255.176 | 190.0354 | 140.0472 | 139.3659 | 133.7839
256.176 | 190.9036 | 140.1088 | 139.3436 | 133.6864
257.176 | 190.7433 | 140.2944 | 139.5278 | 133.8031
258.176 | 190.2056 | 140.1672 | 139.9267 | 133.96
259.176 | 190.8595 | 141.1637 | 140.2343 | 134.107
260.176 | 190.9334 | 141.0346 | 140.4313 | 133.7982
261.176 | 191.1686 | 141.0415 | 140.5922 | 133.6619
262.176 | 190.5994 | 141.4832 | 140.7024 | 133.7732
263.176 | 191.9353 | 141.9721 | 140.8295 | 133.8788
264.176 | 193.3936 | 141.7797 | 141.0299 | 133.53
265.176 | 196.2832 | 141.4918 | 141.0228 | 133.7418
266.176 | 197.0326 | 141.6606 | 141.1515 | 134.1604
267.176 | 196.8013 | 141.9941 | 141.2436 | 134.7148
268.176 | 197.8077 | 142.2723 | 141.1762 | 134.6208
269.176 | 197.7064 | 142.1438 | 141.0629 | 134.3028
270.176 | 197.3804 | 141.9843 | 141.0083 | 134.4487
271.176 | 197.9867 | 142.1192 | 140.9036 | 134.2757
272.176 | 197.4424 | 142.0174 | 141.1293 | 134.3694
273.176 | 199.6293 | 142.0161 | 141.0707 | 134.3719
274.176 | 199.321 | 142.2586 | 141.1085 | 134.4896
275.176 | 198.1087 | 142.1882 | 141.2951 | 134.6382
276.176 | 197.5141 | 142.3781 | 141.4066 | 135.1688
277.176 | 197.3728 | 143.7882 | 141.5813 | 134.837
278.176 | 197.969 | 143.8936 | 141.8363 | 134.9149
279.176 | 197.8692 | 143.9346 | 141.9839 | 135.1879
280.176 | 198.4718 | 144.6423 | 142.0237 | 134.7322
281.176 | 198.9301 | 143.9759 | 142.1812 | 134.9887
282.176 | 200.0151 | 144.2966 | 142.4742 | 136.135
283.176 | 199.55 | 143.9441 | 142.2837 | 135.8113
284.176 | 200.153 | 143.7722 | 142.2281 | 135.5448
285.176 | 201.1756 | 143.5713 | 142.6887 | 135.6037
286.176 | 201.5907 | 143.5577 | 142.6593 | 135.6772
287.176 | 202.5111 | 143.5716 | 142.642 | 135.5725
288.176 | 203.8544 | 143.3947 | 142.8979 | 135.7527
289.176 | 204.5104 | 143.1854 | 143.1352 | 136.4237
290.176 | 206.6885 | 143.4265 | 143.3835 | 136.8475
291.176 | 208.2661 | 144.3675 | 143.7713 | 137.4669
292.176 | 208.9959 | 144.4782 | 143.8153 | 137.4898
293.176 | 208.3704 | 145.8137 | 144.0054 | 137.6591
294.176 | 207.5615 | 145.8361 | 144.634 | 138.2466
295.176 | 206.4902 | 145.7867 | 144.9823 | 138.9443
296.176 | 205.919 | 146.8351 | 145.3525 | 139.1435
297.176 | 205.628 | 146.7536 | 145.9254 | 139.6895
298.176 | 204.727 | 146.6895 | 146.3246 | 139.7383
299.176 | 205.5194 | 147.2506 | 146.4629 | 139.6553
300.176 | 205.0129 | 147.6024 | 146.3944 | 140.0794
301.176 | 203.6735 | 147.6801 | 146.5186 | 140.7461
302.176 | 203.4294 | 148.3504 | 146.826 | 140.6278
303.176 | 203.449 | 148.0542 | 146.8374 | 140.7603
304.176 | 202.6173 | 148.5753 | 147.8987 | 141.0809
305.176 | 201.99 | 149.024 | 147.9996 | 140.8966
306.176 | 201.8814 | 148.6669 | 148.0064 | 140.7663
307.176 | 204.9336 | 149.323 | 148.0142 | 140.616
308.176 | 206.421 | 150.1139 | 147.9812 | 140.9996
309.176 | 206.2464 | 149.5909 | 148.1809 | 141.8892
310.176 | 207.0483 | 149.2137 | 148.2739 | 142.0976
311.176 | 205.4129 | 149.1643 | 148.2849 | 142.0928
312.176 | 206.1935 | 149.0338 | 148.3014 | 142.2623
313.176 | 207.2889 | 148.4469 | 148.2327 | 142.347
314.176 | 207.3605 | 148.311 | 148.2206 | 142.1255
315.176 | 205.5355 | 148.1536 | 148.147 | 141.8306
316.176 | 205.8308 | 148.7368 | 148.1268 | 142.6026
317.176 | 203.6703 | 148.8989 | 148.1386 | 142.4944
318.176 | 202.8263 | 149.2424 | 148.7315 | 142.62
319.176 | 202.7207 | 150.8941 | 149.9311 | 143.0149
320.176 | 201.1533 | 150.6053 | 149.674 | 142.9049
321.176 | 200.0682 | 150.697 | 149.8724 | 142.5285
322.176 | 197.8847 | 150.3656 | 150.4232 | 142.935
323.176 | 196.1902 | 150.0426 | 150.5161 | 142.7628
324.176 | 195.39 | 149.8643 | 150.4037 | 142.7041
325.176 | 194.514 | 150.233 | 150.2733 | 142.4006
326.176 | 193.8863 | 150.1517 | 150.219 | 143.2539
327.176 | 193.5485 | 150.2556 | 150.4122 | 142.9864
328.176 | 192.2553 | 150.2415 | 150.401 | 142.8353
329.176 | 191.9887 | 150.6234 | 150.2091 | 142.5842
330.176 | 191.6605 | 149.6252 | 150.3685 | 142.5873
331.176 | 191.9088 | 149.1244 | 150.2889 | 142.6367
332.176 | 191.5413 | 148.9789 | 150.3487 | 142.5421
333.176 | 192.4124 | 148.8837 | 150.3527 | 142.5057
334.176 | 193.7372 | 149.0934 | 150.4557 | 142.0764
335.176 | 193.173 | 148.6812 | 150.0091 | 141.755
336.176 | 193.1751 | 148.742 | 149.7453 | 141.4356
337.176 | 193.9417 | 148.8457 | 149.5398 | 141.1763
338.176 | 194.5263 | 149.3696 | 149.2513 | 141.0356
339.176 | 194.1948 | 148.9771 | 148.9388 | 140.8935
340.176 | 193.2552 | 149.0235 | 148.6397 | 140.4856
341.176 | 192.2033 | 148.4088 | 148.6358 | 140.4073
342.176 | 192.4267 | 148.0152 | 148.5475 | 140.6447
343.176 | 192.2341 | 147.3174 | 148.6612 | 140.7402
344.176 | 192.125 | 147.689 | 149.1235 | 141.0696
345.176 | 193.8586 | 148.4097 | 149.2643 | 141.1239
346.176 | 194.7611 | 148.338 | 149.2897 | 141.6637
347.176 | 196.1836 | 148.5102 | 149.1466 | 142.0323
348.176 | 196.733 | 149.2791 | 149.227 | 141.9107
349.176 | 197.1922 | 149.0861 | 149.3295 | 141.6932
350.176 | 198.1945 | 148.9328 | 149.5558 | 141.8447
351.176 | 200.0714 | 149.1671 | 149.5491 | 142.0325
352.176 | 200.8463 | 150.0738 | 149.8886 | 142.3424
353.176 | 200.924 | 150.6067 | 150.0981 | 142.7089
354.176 | 201.1545 | 150.6506 | 150.2872 | 142.9557
355.176 | 200.8101 | 150.8139 | 150.5912 | 142.9846
356.176 | 199.7026 | 151.5776 | 151.0321 | 143.1873
357.176 | 198.2972 | 151.2831 | 151.3708 | 143.3539
358.176 | 197.4508 | 150.9137 | 151.3118 | 143.6111
359.176 | 197.7134 | 151.4897 | 151.5056 | 143.8117
360.176 | 197.4927 | 152.4805 | 151.7395 | 143.6127
361.176 | 195.7968 | 152.9677 | 151.7852 | 142.9101
362.176 | 194.5712 | 152.4704 | 151.7273 | 142.8072
363.176 | 194.327 | 152.2 | 151.7309 | 143.3015
364.176 | 193.351 | 151.8821 | 151.4394 | 143.2921
365.176 | 194.1039 | 151.5384 | 151.1541 | 144.5325
366.176 | 194.1109 | 150.9288 | 150.9127 | 144.1901
367.176 | 193.5112 | 150.7892 | 150.8914 | 144.0253
368.176 | 193.4633 | 150.1831 | 150.7704 | 143.8515
369.176 | 193.4273 | 150.6006 | 150.7195 | 144.0881
370.176 | 194.3835 | 150.4084 | 150.8694 | 144.5558
371.176 | 195.9764 | 150.0667 | 150.8476 | 144.3808
372.176 | 197.1772 | 149.8895 | 150.8781 | 144.1236
373.176 | 199.4737 | 150.1643 | 150.9843 | 144.1293
374.176 | 199.6877 | 150.3456 | 151.1291 | 144.2828
375.176 | 199.7299 | 151.0057 | 151.5858 | 144.2984
376.176 | 200.027 | 151.8007 | 152.267 | 145.1603
377.176 | 200.1556 | 151.7322 | 152.7533 | 145.5862
378.176 | 200.1882 | 152.0984 | 153.574 | 146.0319
379.176 | 200.731 | 152.6791 | 153.7897 | 146.2815
380.176 | 201.8937 | 152.9605 | 153.9194 | 146.3695
381.176 | 203.2421 | 153.3128 | 154.1974 | 146.1565
382.176 | 203.3942 | 153.5116 | 154.4465 | 146.2119
383.176 | 203.7056 | 153.3263 | 154.651 | 146.1472
384.176 | 202.8631 | 154.3664 | 154.5501 | 145.87
385.176 | 202.3739 | 154.0587 | 154.2222 | 145.7184
386.176 | 201.2026 | 154.0722 | 154.1099 | 145.9274
387.176 | 200.6527 | 154.0921 | 153.8881 | 146.0485
388.176 | 200.5346 | 153.7933 | 154.0192 | 145.9621
389.176 | 201.2899 | 153.6593 | 153.9062 | 145.9327
390.176 | 202.6472 | 153.4945 | 153.9566 | 145.9538
391.176 | 202.4221 | 153.161 | 153.7995 | 146.0181
392.176 | 202.1748 | 153.4161 | 153.6943 | 146.1365
393.176 | 202.7681 | 153.7472 | 154.1887 | 147.7437
394.176 | 204.34 | 153.1447 | 154.2844 | 147.6101
395.176 | 204.5987 | 152.6582 | 154.332 | 147.9343
396.176 | 205.3363 | 153.3542 | 154.8277 | 148.0261
397.176 | 206.1207 | 153.5054 | 154.7497 | 148.3035
398.176 | 206.766 | 153.4812 | 155.0877 | 148.1892
399.176 | 206.8225 | 153.8852 | 155.5536 | 148.2229
400.176 | 206.3617 | 154.3546 | 155.8951 | 148.4673
401.176 | 206.0014 | 154.8828 | 156.0962 | 148.3956
402.176 | 204.9856 | 154.6166 | 156.3344 | 148.2882
403.176 | 203.3994 | 154.2828 | 156.7053 | 148.2252
404.176 | 203.9902 | 154.684 | 156.947 | 148.8811
405.176 | 203.9516 | 155.1608 | 156.9285 | 149.1601
406.176 | 203.0786 | 155.1767 | 156.8561 | 149.2276
407.176 | 202.7179 | 155.1827 | 156.8091 | 149.1965
408.176 | 202.8919 | 154.5332 | 156.7301 | 148.9769
409.176 | 201.8255 | 154.2098 | 156.4524 | 148.7123
410.176 | 201.9599 | 153.7511 | 156.1655 | 148.505
411.176 | 200.8472 | 154.2491 | 155.9866 | 148.6175
412.176 | 200.9629 | 155.0691 | 155.9025 | 148.6301
413.176 | 199.5043 | 154.9641 | 155.9778 | 148.4623
414.176 | 199.489 | 154.6311 | 155.8076 | 148.3346
415.176 | 199.7342 | 154.7627 | 156.1092 | 148.289
416.176 | 199.3393 | 154.7833 | 156.0047 | 148.0872
417.1917 | 199.3649 | 154.5897 | 155.8111 | 148.0828
418.176 | 200.8913 | 154.1594 | 156.1532 | 147.986
419.176 | 199.785 | 153.6485 | 155.7177 | 147.8647
420.1917 | 199.978 | 153.29 | 155.5792 | 147.8404
421.176 | 200.1941 | 153.7013 | 155.4674 | 147.6882
422.176 | 200.4056 | 153.8398 | 155.4109 | 147.9581
423.1917 | 200.9264 | 153.8859 | 155.3523 | 147.8762
424.1917 | 201.7606 | 154.2588 | 155.6319 | 147.8532
425.176 | 202.3414 | 153.6093 | 155.8202 | 147.9823
426.176 | 203.0875 | 153.238 | 155.8996 | 147.9703
427.176 | 203.6091 | 152.7623 | 155.9293 | 148.5372
428.176 | 203.1853 | 153.2155 | 156.1372 | 148.2064
429.176 | 203.8614 | 153.4007 | 155.9646 | 147.9949
430.176 | 204.0243 | 153.213 | 156.19 | 148.0827
431.176 | 203.9333 | 153.7365 | 156.1108 | 148.0048
432.176 | 205.2377 | 153.8357 | 156.0388 | 148.2098
433.176 | 205.9782 | 153.9384 | 156.0384 | 148.1576
434.176 | 207.7349 | 153.8592 | 156.4855 | 148.2063
435.176 | 208.798 | 154.0119 | 156.3605 | 148.0159
436.176 | 209.236 | 154.2311 | 156.2273 | 148.1466
437.1917 | 209.2603 | 153.8656 | 156.1329 | 148.7007
438.176 | 208.0715 | 153.9691 | 156.1715 | 148.8737
439.176 | 209.171 | 153.3437 | 156.3062 | 148.7708
440.176 | 210.465 | 153.087 | 156.354 | 148.7946
441.176 | 212.2561 | 152.7368 | 156.3408 | 149.0116
442.176 | 211.4059 | 153.1838 | 156.3669 | 149.3344
443.176 | 210.3582 | 153.4162 | 156.4113 | 149.8597
444.176 | 210.3486 | 153.7957 | 156.3735 | 150.2203
445.176 | 210.8734 | 153.9895 | 156.2318 | 150.0945
446.176 | 211.3944 | 153.2768 | 156.0423 | 149.9366
447.176 | 212.0186 | 152.8911 | 155.8651 | 149.7385
448.176 | 211.3277 | 152.9658 | 155.8844 | 150.2193
449.176 | 211.1933 | 153.1462 | 155.8214 | 149.7553
450.176 | 210.6357 | 152.9384 | 155.8066 | 150.6329
451.176 | 210.4012 | 153.2891 | 155.6675 | 150.4594
452.176 | 210.6398 | 153.1349 | 155.6425 | 150.5366
453.176 | 211.4551 | 153.3086 | 155.4506 | 150.1936
454.176 | 211.6709 | 153.1001 | 155.0673 | 149.777
455.176 | 212.419 | 153.0731 | 155.0051 | 149.6024
456.176 | 210.7527 | 153.0066 | 154.7632 | 149.4353
457.176 | 211.0848 | 153.2209 | 154.7537 | 149.2344
458.176 | 210.4951 | 153.4528 | 154.7142 | 149.1199
459.176 | 209.4204 | 153.7606 | 154.7189 | 148.9244
460.176 | 208.398 | 153.5505 | 154.7213 | 148.7985
461.176 | 208.4824 | 153.1925 | 154.744 | 148.8029
462.176 | 207.6763 | 153.3848 | 155.0165 | 148.7945
463.176 | 208.0331 | 153.4686 | 155.2659 | 148.8991
464.176 | 208.0549 | 153.5814 | 155.1502 | 149.1896
465.176 | 208.7116 | 154.169 | 154.8865 | 149.0813
466.176 | 207.8613 | 154.9968 | 154.9671 | 148.8349
467.176 | 210.512 | 155.4355 | 154.924 | 148.8987
468.176 | 212.7835 | 155.4734 | 154.9726 | 149.3085
469.176 | 213.56 | 155.9283 | 154.9141 | 149.3389
470.176 | 214.2305 | 156.5493 | 154.8329 | 149.0148
471.176 | 213.9423 | 156.0493 | 154.9345 | 149.0591
472.176 | 213.3243 | 156.1566 | 155.0074 | 149.2375
473.176 | 211.4722 | 156.0916 | 155.1794 | 149.3604
474.176 | 210.2412 | 156.2015 | 155.3608 | 149.3618
475.1917 | 208.9941 | 156.6257 | 155.1076 | 149.4851
476.176 | 208.7877 | 156.4521 | 155.1539 | 149.619
477.176 | 208.9649 | 156.7174 | 155.3997 | 149.7738
478.176 | 208.4553 | 157.1367 | 155.7 | 149.8684
479.176 | 208.2795 | 157.2401 | 155.4562 | 149.8193
480.1917 | 207.6481 | 156.7937 | 155.4918 | 149.8072
481.1917 | 207.1827 | 156.1255 | 155.2928 | 149.6773
482.176 | 206.4887 | 155.8034 | 155.1405 | 149.5845
483.176 | 205.8888 | 155.6073 | 155.0839 | 149.6915
484.176 | 207.3727 | 155.3064 | 154.9169 | 149.63
485.176 | 206.817 | 155.3774 | 154.7225 | 149.9085
486.176 | 206.6904 | 155.4652 | 154.459 | 150.0413
487.176 | 207.5693 | 155.146 | 154.6719 | 150.0452
488.176 | 207.6317 | 155.0542 | 154.5884 | 150.0722
489.176 | 208.5675 | 154.639 | 154.5508 | 150.0121
490.176 | 209.0575 | 154.3185 | 154.5435 | 150.0607
491.176 | 209.1361 | 154.5928 | 154.6223 | 150.161
492.176 | 208.4935 | 154.6233 | 155.2586 | 150.2768
493.176 | 208.1133 | 154.5918 | 155.1678 | 150.2043
494.176 | 207.3976 | 154.5131 | 155.0841 | 150.2309
495.176 | 207.5931 | 154.2951 | 154.8828 | 150.0508
496.176 | 206.0171 | 154.2866 | 154.671 | 150.1371
497.176 | 205.7172 | 154.7628 | 154.1611 | 150.1745
498.176 | 205.1101 | 154.4542 | 153.9693 | 150.1501
499.176 | 205.7086 | 153.9226 | 153.7092 | 149.827
500.176 | 205.3856 | 153.6086 | 153.5052 | 149.8784
501.176 | 204.9014 | 153.4663 | 153.3503 | 149.777
502.176 | 204.2346 | 153.7681 | 153.4121 | 149.4002
503.176 | 204.4906 | 154.0293 | 153.346 | 149.0956
504.176 | 203.0529 | 154.0496 | 153.2062 | 148.9131
505.176 | 203.4184 | 153.8476 | 153.0175 | 149.0058
506.176 | 204.9845 | 153.8749 | 152.7878 | 149.0369
507.176 | 205.5333 | 154.0347 | 152.6596 | 149.1594
508.176 | 205.7951 | 154.1228 | 152.683 | 149.4081
509.176 | 205.315 | 154.0026 | 152.7691 | 149.5315
510.176 | 205.2711 | 154.1261 | 152.9338 | 149.7101
511.176 | 205.1537 | 153.7242 | 153.1211 | 149.9314
512.176 | 205.9806 | 153.7008 | 153.2971 | 149.7463
513.176 | 205.5094 | 154.2708 | 153.4065 | 149.6722
514.176 | 205.5406 | 154.4768 | 153.5319 | 149.7857
515.176 | 204.9609 | 154.4475 | 153.7045 | 149.6063
516.176 | 205.1312 | 154.1395 | 153.7833 | 149.7505
517.176 | 203.6555 | 154.141 | 153.8075 | 149.6811
518.176 | 204.0153 | 154.3464 | 153.8979 | 149.5802
519.176 | 204.1567 | 154.3956 | 154.1572 | 149.8922
520.176 | 204.6754 | 154.4328 | 154.2041 | 149.8429
521.176 | 203.5468 | 154.3377 | 154.3052 | 149.9661
522.176 | 202.6379 | 154.224 | 154.243 | 149.6704
523.176 | 202.1863 | 154.8887 | 154.3166 | 150.0996
524.176 | 201.153 | 155.3028 | 154.3764 | 150.1894
525.176 | 201.2196 | 155.0978 | 154.4265 | 150.0361
526.176 | 201.0544 | 155.2538 | 154.8034 | 150.0485
527.176 | 201.6568 | 155.0056 | 155.0937 | 150.1327
528.176 | 201.2802 | 155.6418 | 155.3321 | 149.8613
529.176 | 200.6023 | 155.7874 | 155.9293 | 150.6334
530.176 | 198.7806 | 155.8301 | 156.8131 | 150.9809
531.176 | 199.6468 | 156.3419 | 157.5113 | 151.4106
532.176 | 199.7492 | 156.5813 | 157.8349 | 151.9036
533.176 | 199.5208 | 158.3001 | 158.4736 | 153.0384
534.176 | 198.4262 | 158.2099 | 158.7381 | 153.4881
535.176 | 198.2394 | 158.3009 | 158.6414 | 153.3977
536.176 | 197.8252 | 158.0283 | 158.7952 | 153.4312
537.176 | 197.3051 | 158.1515 | 159.1153 | 153.2592
538.176 | 196.7986 | 158.2351 | 159.514 | 153.0822
539.176 | 196.5188 | 157.9133 | 159.4364 | 152.7867
540.176 | 195.9334 | 157.8956 | 159.2585 | 152.4979
541.176 | 196.4188 | 157.977 | 159.0528 | 152.4473
542.176 | 196.3452 | 157.9928 | 158.8263 | 152.2783
543.176 | 199.0416 | 157.862 | 158.2882 | 152.2141
544.176 | 200.1515 | 158.0781 | 157.8463 | 152.5556
545.176 | 201.4024 | 158.0076 | 157.6114 | 152.6849
546.176 | 201.8702 | 157.9162 | 157.6326 | 152.7388
547.176 | 201.652 | 157.9169 | 157.6323 | 152.9764
548.176 | 200.1149 | 157.6585 | 157.716 | 152.611
549.176 | 200.0354 | 157.7425 | 157.7575 | 152.5691
550.176 | 200.3872 | 157.6758 | 157.8904 | 153.4831
551.176 | 200.6955 | 157.2499 | 158.4736 | 153.1841
552.176 | 200.8988 | 157.3852 | 158.7533 | 153.0058
553.176 | 201.2242 | 157.2372 | 158.6003 | 152.8395
554.176 | 201.2687 | 157.1046 | 158.551 | 152.7345
555.176 | 201.4417 | 157.6142 | 158.3406 | 152.5518
556.176 | 201.557 | 157.3794 | 158.1609 | 152.4902
557.176 | 202.5337 | 157.84 | 158.2123 | 152.6084
558.176 | 202.1329 | 157.7311 | 158.2917 | 152.7273
559.176 | 201.3969 | 157.8446 | 158.1558 | 152.9647
560.176 | 202.4273 | 158.4939 | 158.1461 | 153.7261
561.176 | 203.2429 | 159.076 | 158.1441 | 153.6886
562.176 | 203.5096 | 158.7861 | 158.4236 | 153.2563
563.176 | 204.2562 | 158.6556 | 158.5628 | 152.9398
564.176 | 204.2914 | 159.3668 | 158.753 | 153.172
565.176 | 204.1636 | 159.1778 | 158.833 | 153.0023
566.176 | 204.4564 | 158.981 | 159.0889 | 153.1209
567.176 | 204.6064 | 158.9262 | 159.8441 | 152.949
568.176 | 205.5885 | 159.3468 | 159.9695 | 152.8813
569.176 | 204.9615 | 158.9306 | 160.3772 | 153.1885
570.176 | 204.9731 | 160.0851 | 160.3497 | 153.6691
571.176 | 205.1719 | 159.6701 | 160.1317 | 153.424
572.176 | 205.0046 | 159.8261 | 159.91 | 153.3248
573.176 | 205.6014 | 159.388 | 159.6839 | 153.1763
574.176 | 203.9764 | 159.7573 | 159.6067 | 153.2783
575.176 | 203.4301 | 159.897 | 159.484 | 153.492
576.176 | 203.8007 | 160.0856 | 159.3224 | 153.3668
577.176 | 204.6774 | 160.2317 | 159.4752 | 153.2882
578.176 | 204.2243 | 159.9901 | 159.625 | 153.1389
579.176 | 203.7835 | 159.3832 | 159.5381 | 153.0296
580.176 | 203.8657 | 158.9136 | 159.507 | 152.804
581.176 | 203.9115 | 159.0897 | 159.392 | 152.8133
582.176 | 203.9192 | 158.8269 | 159.1791 | 152.6312
583.176 | 204.6366 | 158.3397 | 158.8703 | 152.6967
584.176 | 205.8455 | 158.6032 | 158.8169 | 152.3749
585.176 | 205.4888 | 157.8327 | 158.6552 | 152.401
586.176 | 205.5218 | 157.2635 | 158.5366 | 152.6269
587.176 | 204.4211 | 158.4026 | 158.6407 | 152.4434
588.176 | 203.8992 | 158.1217 | 158.6005 | 152.4464
589.176 | 203.6011 | 157.9339 | 158.4504 | 152.6971
590.176 | 203.0925 | 157.9752 | 158.4861 | 152.8751
591.176 | 204.0897 | 157.5094 | 158.5516 | 152.9223
592.176 | 205.6761 | 157.1644 | 158.4017 | 152.7994
593.176 | 205.0071 | 156.978 | 158.7705 | 152.6771
594.176 | 204.4272 | 157.373 | 159.1848 | 152.7924
595.176 | 205.4098 | 158.6004 | 159.1465 | 152.6066
596.176 | 205.3365 | 159.0629 | 159.1363 | 152.573
597.176 | 204.0232 | 159.6987 | 159.098 | 152.6771
598.176 | 203.354 | 160.0709 | 159.0877 | 152.4877
599.176 | 203.6946 | 160.1437 | 158.891 | 152.1527
600.176 | 203.5834 | 160.4144 | 159.2126 | 152.2275
601.176 | 203.5589 | 159.9885 | 159.3394 | 152.3047
602.176 | 202.6261 | 159.6864 | 159.7527 | 152.5903
603.176 | 202.4323 | 159.7259 | 159.7715 | 153.0576
604.176 | 201.2356 | 159.3086 | 160.0433 | 153.023
605.176 | 201.0236 | 159.4848 | 160.1889 | 153.1909
606.176 | 201.0951 | 159.4402 | 160.2165 | 153.6726
607.176 | 201.0864 | 159.7006 | 160.2067 | 154.2451
608.176 | 200.386 | 159.3604 | 160.0903 | 154.1154
609.176 | 200.3766 | 159.2695 | 159.9783 | 153.976
610.176 | 200.5255 | 159.3792 | 159.7027 | 153.8167
611.176 | 200.7784 | 159.0292 | 159.4844 | 153.8042
612.176 | 200.3604 | 158.7874 | 159.3741 | 153.5022
613.176 | 200.3914 | 158.5369 | 159.3901 | 153.3805
614.176 | 200.3075 | 158.1451 | 159.3656 | 153.3565
615.176 | 200.501 | 158.2293 | 159.4327 | 153.3578
616.176 | 200.0202 | 157.9566 | 159.2889 | 153.5193
617.176 | 200.0928 | 158.4853 | 159.428 | 154.0989
618.176 | 200.1277 | 158.34 | 159.4027 | 154.2908
619.176 | 200.2673 | 158.5394 | 159.7265 | 154.4985
620.176 | 200.6903 | 158.0901 | 159.8303 | 154.0489
621.176 | 200.8191 | 158.2609 | 160.0894 | 153.904
622.176 | 200.6793 | 159.4968 | 159.9565 | 153.8788
623.176 | 200.514 | 160.1036 | 160.0028 | 153.9374
624.176 | 199.7258 | 160.3712 | 160.1204 | 153.9687
625.176 | 199.6712 | 160.9256 | 160.8115 | 154.4411
626.176 | 200.0508 | 161.2587 | 161.1089 | 154.5788
627.176 | 200.4927 | 161.0921 | 161.2434 | 154.5603
628.176 | 201.3527 | 161.1558 | 161.6191 | 154.4252
629.176 | 201.9175 | 161.5496 | 161.6129 | 154.8026
630.176 | 201.7325 | 161.0868 | 161.781 | 155.3047
631.176 | 201.6259 | 161.2956 | 161.9627 | 155.1269
632.176 | 201.5436 | 160.9364 | 162.0159 | 155.165
633.176 | 200.5757 | 161.1004 | 161.9564 | 155.161
634.176 | 201.3224 | 161.3983 | 161.8985 | 155.3574
635.176 | 202.0429 | 161.3836 | 161.7168 | 155.134
636.176 | 202.3967 | 161.473 | 161.952 | 155.1523
637.176 | 202.2661 | 161.8348 | 162.0115 | 155.1218
638.176 | 202.0135 | 161.7709 | 162.1952 | 155.3011
639.176 | 201.4112 | 162.5329 | 162.194 | 154.9974
640.176 | 201.8468 | 163.4446 | 162.3032 | 155.0548
641.176 | 202.0967 | 163.8007 | 162.3782 | 155.1432
642.176 | 202.1897 | 163.5873 | 162.1943 | 155.063
643.176 | 200.9758 | 163.6756 | 162.1653 | 155.0578
644.176 | 199.7403 | 163.1628 | 162.2208 | 155.5964
645.1917 | 200.2462 | 163.5117 | 162.18 | 155.3609
646.176 | 199.6618 | 163.2479 | 162.4029 | 155.217
647.176 | 199.6344 | 162.6477 | 162.7022 | 154.9412
648.176 | 199.4052 | 163.6341 | 163.5756 | 154.5536
649.176 | 199.825 | 164.0076 | 163.6205 | 154.5039
650.176 | 201.3278 | 163.6698 | 164.0377 | 154.9777
651.176 | 202.9416 | 163.4389 | 163.8477 | 155.041
652.176 | 203.7388 | 163.0916 | 163.835 | 155.3095
653.176 | 203.645 | 163.7006 | 163.7713 | 156.3055
654.176 | 203.7069 | 163.4501 | 164.1744 | 156.3219
655.176 | 204.7728 | 163.5525 | 164.4121 | 156.3318
656.176 | 205.2312 | 163.3991 | 164.3453 | 156.9105
657.176 | 205.5538 | 163.44 | 165.2084 | 157.234
658.176 | 206.363 | 163.206 | 165.0962 | 157.1617
659.176 | 207.6497 | 162.6988 | 165.3356 | 157.0154
660.176 | 208.1207 | 162.3529 | 165.2958 | 156.9942
661.176 | 210.0719 | 162.4047 | 165.499 | 156.9799
662.176 | 210.1512 | 163.3213 | 165.8114 | 156.7404
663.176 | 209.2668 | 163.2219 | 166.7315 | 156.7295
664.176 | 209.0077 | 163.0665 | 166.7036 | 156.7378
665.176 | 209.0274 | 163.3893 | 166.9376 | 156.9522
666.176 | 209.93 | 163.7872 | 166.9357 | 157.0021
667.176 | 209.7606 | 164.0055 | 166.8384 | 157.3638
668.176 | 209.2705 | 163.3948 | 166.4447 | 157.2569
669.176 | 210.027 | 163.0794 | 166.3967 | 157.5874
670.176 | 209.7899 | 163.0836 | 166.314 | 157.4759
671.176 | 210.4643 | 163.1309 | 166.0658 | 157.3323
672.176 | 211.2587 | 163.2138 | 165.8493 | 157.0816
673.176 | 211.0551 | 163.1718 | 165.6539 | 156.9225
674.176 | 211.6346 | 162.9925 | 165.4419 | 156.9017
675.176 | 212.3083 | 162.9935 | 165.4044 | 157.2111
676.176 | 211.4809 | 162.9216 | 165.36 | 157.2201
677.176 | 211.6892 | 162.8868 | 165.2431 | 157.3248
678.176 | 212.6686 | 162.7054 | 164.8633 | 157.5185
679.176 | 211.4925 | 162.6982 | 165.0972 | 158.0479
680.176 | 211.5063 | 163.1971 | 165.2122 | 158.465
681.176 | 212.2312 | 163.0763 | 165.1851 | 158.8221
682.176 | 211.517 | 162.6587 | 165.4766 | 158.8883
683.176 | 211.1978 | 162.7706 | 165.331 | 159.0294
684.176 | 211.7626 | 162.8433 | 165.4921 | 159.0324
685.176 | 212.383 | 162.5025 | 165.6441 | 158.9251
686.176 | 212.0082 | 163.1449 | 165.5047 | 158.9601
687.176 | 212.2459 | 163.7101 | 166.079 | 159.4064
688.176 | 212.7383 | 163.7829 | 166.7176 | 159.3976
689.176 | 213.4308 | 164.1015 | 166.8714 | 159.4506
690.176 | 215.2139 | 164.1271 | 167.2193 | 159.6257
691.176 | 215.1833 | 163.8014 | 167.7562 | 159.6417
692.176 | 215.9937 | 164.1348 | 167.8348 | 159.8121
693.176 | 216.1485 | 164.3658 | 168.1944 | 160.1376
694.176 | 216.5831 | 164.5098 | 167.6427 | 160.2758
695.176 | 216.0987 | 164.2888 | 167.4539 | 160.1689
696.176 | 215.3522 | 164.5312 | 167.2409 | 159.9707
697.176 | 216.0127 | 164.3935 | 167.0333 | 159.9829
698.176 | 217.5665 | 164.3093 | 167.2139 | 160.2384
699.176 | 218.305 | 163.9887 | 167.0536 | 160.3025
700.176 | 218.1974 | 164.4992 | 166.8705 | 160.562
701.176 | 219.4156 | 164.0225 | 166.7264 | 160.5492
702.176 | 218.9788 | 163.5149 | 166.5213 | 160.5584
703.176 | 218.6483 | 163.2339 | 166.3925 | 160.2668
704.176 | 220.4092 | 163.3955 | 166.2481 | 160.0883
705.176 | 219.838 | 163.3706 | 166.0959 | 159.973
706.176 | 219.4835 | 163.2051 | 166.2646 | 159.8497
707.176 | 218.5678 | 163.5456 | 166.2706 | 159.4826
708.176 | 220.9624 | 163.4644 | 166.4863 | 159.5001
709.176 | 221.6485 | 163.1456 | 166.5999 | 159.5175
710.176 | 222.0268 | 163.2826 | 166.618 | 159.7073
711.176 | 221.355 | 162.9486 | 166.616 | 159.7931
712.176 | 221.1324 | 162.8533 | 166.5662 | 160.0003
713.176 | 220.7606 | 162.6934 | 166.4447 | 160.0479
714.176 | 220.9456 | 162.7307 | 166.3159 | 160.2811
715.176 | 221.0052 | 162.5612 | 166.2945 | 160.1216
716.176 | 221.6978 | 162.4309 | 166.3169 | 160.0108
717.176 | 220.7541 | 162.5461 | 166.3429 | 160.1006
718.176 | 220.5095 | 162.5155 | 166.4423 | 160.2424
719.176 | 220.792 | 162.8096 | 166.9789 | 160.1381
720.176 | 222.3077 | 162.4386 | 167.1375 | 160.1425
721.176 | 222.7505 | 162.9259 | 167.1949 | 160.4446
722.176 | 223.2908 | 163.1897 | 167.1894 | 160.4376
723.176 | 223.7599 | 163.2487 | 167.2546 | 160.6277
724.176 | 223.2692 | 163.1549 | 167.1284 | 161.0325
725.176 | 222.8913 | 163.0638 | 167.0429 | 160.7371
726.176 | 222.467 | 162.9671 | 167.0564 | 161.0081
727.176 | 223.2738 | 162.7356 | 166.9396 | 161.3839
728.176 | 224.0057 | 162.4555 | 166.7494 | 161.4851
729.176 | 226.5447 | 162.3775 | 166.6787 | 161.8266
730.176 | 228.7428 | 162.0403 | 166.6784 | 162.0482
731.176 | 227.4905 | 162.313 | 166.9627 | 162.1562
732.176 | 226.7867 | 162.5977 | 167.0359 | 162.1658
733.176 | 227.244 | 162.5448 | 167.123 | 162.0465
734.176 | 227.0619 | 162.5861 | 167.2939 | 162.2622
735.176 | 225.2495 | 162.3634 | 167.5577 | 162.3774
736.176 | 225.3478 | 162.3836 | 167.622 | 162.0835
737.176 | 225.3933 | 162.3405 | 167.5674 | 161.9126
738.176 | 225.8039 | 162.13 | 167.4777 | 161.7768
739.176 | 228.0223 | 162.9308 | 167.6121 | 161.9939
740.176 | 228.2245 | 163.373 | 167.8025 | 162.0439
741.176 | 228.8153 | 163.8552 | 168.002 | 162.1019
742.176 | 231.8751 | 163.9101 | 168.35 | 162.418
743.176 | 233.8231 | 163.9525 | 168.4237 | 162.2404
744.176 | 234.5533 | 163.8722 | 168.4402 | 161.6887
745.176 | 238.0389 | 164.2733 | 168.5256 | 161.5891
746.176 | 241.1744 | 164.9411 | 168.5319 | 161.732
747.176 | 242.6079 | 165.2086 | 168.6605 | 161.8897
748.176 | 243.5787 | 164.8475 | 168.7016 | 161.7256
749.176 | 244.8934 | 164.955 | 168.836 | 161.7492
750.176 | 244.579 | 164.8007 | 168.9723 | 161.7625
751.176 | 245.1372 | 164.7793 | 169.1377 | 161.6862
752.176 | 245.4679 | 164.8145 | 169.3575 | 161.5289
753.176 | 248.3411 | 165.19 | 169.7096 | 161.9268
754.176 | 250.4539 | 165.3979 | 170.3543 | 162.1806
755.176 | 251.1277 | 166.1535 | 170.3408 | 162.6868
756.176 | 251.0289 | 165.8461 | 170.7941 | 163.2914
757.176 | 250.5443 | 165.5892 | 170.9053 | 163.0045
758.176 | 249.418 | 165.2883 | 171.0941 | 162.9738
759.176 | 249.1836 | 165.5871 | 171.4321 | 163.3313
760.176 | 248.8143 | 165.4629 | 171.4163 | 163.5314
761.176 | 247.6712 | 165.2851 | 171.5676 | 163.7573
762.176 | 248.5879 | 164.7871 | 171.5307 | 163.8202
763.176 | 247.058 | 164.5027 | 171.3946 | 163.698
764.176 | 247.5385 | 164.688 | 171.1559 | 163.4552
765.176 | 249.0363 | 164.5069 | 170.9393 | 163.4847
766.176 | 250.431 | 164.1649 | 170.765 | 163.289
767.176 | 253.2409 | 164.0895 | 170.5056 | 163.1206
768.176 | 252.728 | 164.5464 | 170.19 | 163.4364
769.176 | 251.961 | 165.0342 | 170.1274 | 163.7316
770.176 | 251.2532 | 165.518 | 170.0424 | 163.6315
771.176 | 250.1438 | 165.3775 | 169.9854 | 163.6233
772.176 | 252.7585 | 165.7162 | 170.0282 | 163.4621
773.176 | 257.4405 | 165.591 | 170.1505 | 163.4671
774.176 | 257.2446 | 165.5992 | 170.2383 | 163.1469
775.176 | 259.2421 | 165.4371 | 170.2813 | 163.021
776.176 | 261.2196 | 165.6409 | 170.4669 | 163.0898
777.176 | 264.0516 | 166.1735 | 170.6756 | 163.1528
778.176 | 263.788 | 166.2846 | 170.9191 | 163.2746
779.176 | 264.0956 | 165.8887 | 170.9897 | 163.2021
780.176 | 264.0712 | 165.4915 | 170.8054 | 163.4483
781.176 | 264.5986 | 165.3672 | 171.2022 | 163.6466
782.176 | 265.3907 | 165.3292 | 171.6807 | 163.7607
783.176 | 265.7121 | 165.7799 | 171.5744 | 164.0145
784.176 | 269.9923 | 166.2387 | 171.4721 | 164.4714
785.176 | 268.1533 | 166.2169 | 171.5588 | 164.3289
786.176 | 273.144 | 166.1163 | 171.5482 | 164.0666
787.176 | 273.9289 | 166.3681 | 171.5628 | 164.4222
788.176 | 273.6785 | 166.2611 | 171.5815 | 164.5397
789.176 | 272.0569 | 166.1668 | 172.0843 | 164.7598
790.176 | 271.0115 | 166.0379 | 171.8828 | 164.3696
791.176 | 269.7414 | 166.0756 | 171.7882 | 164.2385
792.176 | 270.6111 | 166.2533 | 171.5397 | 164.271
793.176 | 269.2597 | 166.0727 | 171.473 | 164.3537
794.176 | 269.6048 | 165.9501 | 171.2233 | 164.2538
795.176 | 279.4741 | 166.0787 | 171.077 | 164.5328
796.176 | 278.8211 | 166.1639 | 171.0364 | 164.1916
797.176 | 279.735 | 166.5744 | 171.0951 | 164.3035
798.176 | 278.9942 | 166.9788 | 171.2433 | 164.308
799.176 | 281.6911 | 167.1088 | 171.4965 | 164.1598
800.176 | 281.7653 | 167.6591 | 171.6599 | 164.1956
801.176 | 279.9611 | 167.904 | 172.0651 | 163.8309
802.176 | 280.8793 | 168.0887 | 172.2471 | 163.9502
803.176 | 280.1945 | 168.0791 | 172.1352 | 163.8428
804.176 | 291.0026 | 167.8634 | 172.1268 | 163.721
805.176 | 288.2245 | 168.0249 | 172.0781 | 163.4967
806.176 | 288.6007 | 168.0467 | 172.1772 | 163.7109
807.176 | 290.1155 | 167.9351 | 172.0209 | 163.7184
808.176 | 296.9772 | 167.6095 | 171.9062 | 164.014
809.176 | 297.9569 | 167.4006 | 171.8681 | 164.0738
810.176 | 297.6464 | 167.5611 | 171.9291 | 164.7159
811.176 | 296.8037 | 167.8959 | 171.6758 | 165.2087
812.176 | 297.0759 | 168.1005 | 171.8165 | 165.4698
813.176 | 301.6123 | 168.4494 | 172.1831 | 165.4761
814.176 | 299.093 | 168.4444 | 172.2404 | 165.4675
815.176 | 298.0629 | 168.9126 | 172.5631 | 165.8282
816.176 | 296.9343 | 168.5383 | 172.6365 | 165.7338
817.176 | 295.1933 | 168.9081 | 172.9329 | 165.751
818.176 | 292.6753 | 168.8304 | 173.1656 | 166.059
819.176 | 291.7421 | 168.9231 | 173.284 | 165.9996
820.176 | 293.0156 | 169.0468 | 173.5974 | 166.201
821.176 | 292.2771 | 169.1116 | 173.8793 | 166.2665
822.176 | 293.3278 | 168.9648 | 174.1857 | 166.322
823.176 | 293.9974 | 168.9084 | 174.3953 | 166.5209
824.176 | 295.3899 | 169.3755 | 174.3924 | 166.7495
825.176 | 295.9602 | 169.2499 | 174.424 | 166.8014
826.176 | 295.0873 | 170.6664 | 174.468 | 167.384
827.176 | 294.7248 | 170.5335 | 174.5256 | 167.2509
828.176 | 295.0225 | 170.7302 | 174.5766 | 167.5339
829.176 | 293.5584 | 170.7173 | 174.9491 | 168.0529
830.176 | 296.2844 | 170.9115 | 175.6001 | 167.8841
831.176 | 296.8405 | 171.7863 | 175.89 | 167.8559
832.176 | 300.495 | 172.6441 | 176.3065 | 168.5298
833.176 | 315.8577 | 173.1444 | 176.3417 | 169.0431
834.176 | 314.0716 | 173.9915 | 176.5012 | 168.9817
835.176 | 315.7991 | 174.3385 | 176.5093 | 169.5834
836.176 | 315.002 | 175.025 | 176.6825 | 169.4694
837.176 | 313.8625 | 174.7484 | 176.915 | 169.9254
838.176 | 313.8015 | 174.5952 | 177.0847 | 170.7266
839.176 | 331.4882 | 174.335 | 177.1117 | 170.794
840.176 | 338.795 | 174.2018 | 177.4036 | 170.6332
841.176 | 337.5711 | 174.1056 | 177.9264 | 170.7948
842.176 | 338.73 | 174.2557 | 178.3509 | 170.8545
843.176 | 337.1154 | 175.0028 | 178.7982 | 171.1422
844.176 | 333.5741 | 174.4492 | 179.0386 | 171.2459
845.176 | 331.0322 | 174.6076 | 178.9914 | 171.5604
846.176 | 326.3064 | 175.1696 | 179.0693 | 171.6042
847.176 | 326.8376 | 175.4758 | 179.0762 | 172.2321
848.176 | 326.7711 | 175.759 | 179.2786 | 171.9679
849.176 | 324.6374 | 176.0246 | 179.3656 | 172.3613
850.176 | 324.5352 | 175.2233 | 179.3084 | 172.1443
851.176 | 327.5093 | 174.8317 | 179.2221 | 172.3049
852.176 | 327.7788 | 174.6689 | 179.121 | 172.9723
853.176 | 328.3375 | 174.332 | 179.9277 | 172.8027
854.176 | 324.6051 | 174.592 | 179.7297 | 172.513
855.176 | 325.3001 | 174.8707 | 179.5836 | 172.2348
856.176 | 324.2615 | 175.2919 | 179.4126 | 172.6105
857.176 | 320.4439 | 175.05 | 179.5165 | 172.91
858.176 | 319.241 | 175.2754 | 179.5607 | 172.7273
859.176 | 319.1553 | 175.2333 | 179.4649 | 172.3862
860.176 | 318.2383 | 175.1364 | 179.4242 | 172.2875
861.176 | 316.5945 | 175.3663 | 179.0981 | 171.9217
862.176 | 317.309 | 175.1759 | 178.995 | 171.9097
863.176 | 315.8979 | 175.1079 | 178.8208 | 171.9813
864.176 | 318.0176 | 174.9432 | 178.9264 | 171.7224
865.176 | 314.1307 | 175.0064 | 179.0485 | 171.7887
866.176 | 312.2237 | 175.1743 | 179.3911 | 172.3121
867.176 | 313.4308 | 174.7248 | 179.385 | 172.2452
868.176 | 310.9181 | 174.7567 | 179.3359 | 172.0691
869.176 | 310.2669 | 174.5459 | 179.3588 | 172.1931
870.176 | 321.3947 | 174.5945 | 179.6125 | 172.0813
871.176 | 328.8581 | 174.3162 | 179.7468 | 172.2298
872.176 | 335.222 | 174.4856 | 179.9581 | 172.084
873.176 | 335.6205 | 174.5312 | 180.1287 | 171.9677
874.176 | 333.9058 | 174.3337 | 180.2038 | 172.1097
875.176 | 332.1583 | 174.4377 | 180.3238 | 171.9921
876.176 | 331.4405 | 174.4037 | 180.2552 | 171.7082
877.176 | 340.9681 | 174.8145 | 180.4232 | 171.9457
878.176 | 358.7184 | 174.8455 | 180.5777 | 172.001
879.176 | 357.0236 | 174.7366 | 180.6566 | 171.7347
880.176 | 378.2223 | 175.2191 | 180.5817 | 171.7973
881.176 | 404.0492 | 175.3204 | 180.5299 | 173.258
882.176 | 397.0972 | 175.1985 | 180.6427 | 173.6348
883.176 | 397.9135 | 175.2883 | 180.4863 | 173.6456
884.176 | 390.8807 | 175.7517 | 180.9366 | 174.1943
885.176 | 385.5566 | 175.5583 | 180.9203 | 174.0697
886.176 | 382.5598 | 175.4564 | 180.9096 | 174.5313
887.176 | 377.5299 | 175.2791 | 181.0269 | 174.3545
888.176 | 373.597 | 175.2515 | 180.8248 | 173.989
889.176 | 369.2846 | 174.822 | 180.6571 | 173.9705
890.176 | 366.0399 | 174.7949 | 180.6063 | 173.742
891.176 | 360.9454 | 175.068 | 181.0328 | 174.4995
892.176 | 357.7613 | 174.87 | 181.3396 | 174.3491
893.176 | 356.9121 | 175.3614 | 181.6344 | 174.1328
894.176 | 373.4078 | 175.2907 | 181.9674 | 173.9626
895.176 | 398.0729 | 175.4586 | 182.1166 | 174.0285
896.176 | 391.5936 | 175.3282 | 182.2966 | 173.8206
897.176 | 387.2933 | 175.9971 | 182.2867 | 173.5457
898.176 | 378.6103 | 176.4258 | 182.1877 | 173.3909
899.176 | 371.5306 | 175.9546 | 182.0005 | 173.8094
900.176 | 365.7232 | 175.8895 | 181.9532 | 174.1123
901.176 | 363.1544 | 176.1736 | 182.0139 | 173.9798
902.176 | 359.0868 | 176.2605 | 182.2438 | 174.0546
903.176 | 359.3156 | 175.9112 | 182.804 | 174.5654
904.176 | 353.9544 | 175.5526 | 182.953 | 175.2516
905.176 | 350.9853 | 175.762 | 183.0919 | 175.626
906.176 | 346.362 | 175.5535 | 182.9128 | 175.8883
907.176 | 343.9774 | 175.4598 | 182.7029 | 175.7937
908.176 | 341.6469 | 175.5382 | 182.7253 | 175.7989
909.176 | 339.2048 | 175.9253 | 182.4931 | 175.8659
910.176 | 337.8255 | 175.7512 | 182.6489 | 175.8032
911.176 | 335.581 | 175.8811 | 182.7464 | 175.7251
912.176 | 335.5164 | 176.3326 | 182.7221 | 176.2524
913.176 | 334.5879 | 176.7505 | 182.6849 | 176.2381
914.176 | 334.9116 | 176.7237 | 182.5719 | 176.2907
915.176 | 350.134 | 176.6981 | 182.6124 | 176.5233
916.176 | 346.2533 | 176.8768 | 183.1961 | 176.5531
917.176 | 357.2419 | 176.9167 | 183.5434 | 176.7792
918.176 | 375.8783 | 176.8837 | 183.6469 | 176.9665
919.176 | 382.5152 | 177.4394 | 184.0031 | 177.1212
920.176 | 399.4424 | 177.9657 | 184.4003 | 177.2122
921.176 | 419.2622 | 177.9977 | 184.6628 | 177.6153
922.176 | 428.2665 | 179.1824 | 184.7303 | 177.8615
923.176 | 437.9577 | 179.9148 | 184.9982 | 178.2222
924.176 | 435.3609 | 179.7352 | 185.1744 | 177.9147
925.176 | 435.1673 | 180.3308 | 185.0097 | 178.1264
926.176 | 443.7116 | 180.7595 | 184.8968 | 178.4446
927.176 | 442.0158 | 180.2872 | 184.8608 | 178.303
928.176 | 455.246 | 179.9663 | 184.8149 | 178.1625
929.176 | 478.2569 | 181.2732 | 184.8457 | 178.0279
930.176 | 462.7465 | 180.3379 | 184.8262 | 178.1531
931.176 | 456.8328 | 180.4594 | 184.8906 | 178.023
932.176 | 448.0476 | 180.0129 | 185.165 | 178.1597
933.176 | 445.7201 | 180.2237 | 185.3162 | 178.2058
934.176 | 451.7837 | 180.8973 | 185.8735 | 177.7959
935.176 | 468.7457 | 181.2687 | 185.969 | 178.3095
936.176 | 495.1582 | 180.727 | 185.9604 | 178.3411
937.176 | 518.5931 | 181.2829 | 186.1775 | 178.4037
938.176 | 537.3453 | 181.3038 | 186.4475 | 178.8781
939.176 | 542.7801 | 181.123 | 186.5013 | 178.9958
940.176 | 549.2046 | 180.9544 | 186.7255 | 179.2184
941.176 | 548.7039 | 180.954 | 186.8659 | 179.2815
942.176 | 532.7144 | 181.1308 | 187.0024 | 179.3776
943.176 | 523.4486 | 181.1356 | 187.248 | 179.8407
944.176 | 512.2714 | 181.3931 | 187.4292 | 180.3468
945.176 | 502 | 182.5329 | 187.4942 | 180.2053
946.176 | 489.0372 | 182.7122 | 187.3797 | 179.8805
947.176 | 484.4985 | 182.6327 | 187.5298 | 179.7782
948.176 | 489.7995 | 182.4054 | 187.5598 | 179.7167
949.176 | 494.2476 | 182.6479 | 187.6162 | 179.6048
950.176 | 518.7165 | 182.9369 | 187.8221 | 180.0803
951.176 | 534.9965 | 182.7282 | 187.9883 | 179.9894
952.176 | 525.1842 | 182.8608 | 188.1219 | 180.2168
953.176 | 522.3724 | 182.7811 | 188.3025 | 180.3608
954.176 | 512.3835 | 182.4858 | 188.1372 | 180.0804
955.176 | 505.366 | 183.3037 | 188.1032 | 180.039
956.176 | 501.3473 | 183.0812 | 188.0568 | 179.9362
957.176 | 487.9709 | 183.0528 | 187.9883 | 180.568
958.176 | 480.5015 | 182.6593 | 187.5672 | 180.7266
959.176 | 482.7203 | 182.844 | 187.1665 | 180.2657
960.176 | 473.5844 | 182.5349 | 186.8361 | 180.315
961.176 | 478.4207 | 182.3617 | 186.4655 | 179.9391
962.176 | 485.3836 | 182.4358 | 186.322 | 179.7645
963.176 | 501.7514 | 182.6712 | 186.382 | 179.8221
964.176 | 513.2772 | 182.8604 | 186.2564 | 179.8865
965.176 | 530.7187 | 183.1127 | 186.161 | 180.0212
966.176 | 539.8841 | 183.0319 | 186.1928 | 180.0731
967.176 | 539.1615 | 183.1404 | 186.2104 | 180.3764
968.176 | 537.5175 | 184.0419 | 186.3456 | 180.6649
969.176 | 526.9025 | 183.8164 | 186.06 | 180.6303
970.176 | 546.5093 | 183.8258 | 185.9214 | 180.5604
971.176 | 535.5806 | 183.6434 | 185.8195 | 180.4241
972.176 | 524.7639 | 183.888 | 185.5565 | 180.5499
973.176 | 513.1374 | 183.8213 | 185.3367 | 180.0449
974.176 | 535.9858 | 184.2592 | 185.5878 | 179.9165
975.176 | 556.5954 | 183.8224 | 185.4527 | 179.9854
976.176 | 561.9221 | 183.7509 | 185.4088 | 180.2309
977.176 | 584.882 | 183.8852 | 185.3436 | 179.9141
978.176 | 576.4172 | 183.7062 | 185.3183 | 179.8305
979.176 | 570.0001 | 183.5934 | 185.2442 | 179.9206
980.176 | 555.9503 | 183.2319 | 185.152 | 180.4192
981.176 | 543.4826 | 183.39 | 185.1026 | 180.6278
982.176 | 543.5168 | 183.9512 | 185.2829 | 181.3338
983.176 | 534.7777 | 183.9249 | 185.5084 | 181.7023
984.176 | 528.2109 | 183.9583 | 185.778 | 182.5087
985.176 | 535.8865 | 183.9621 | 185.9119 | 182.5345
986.176 | 523.53 | 183.7862 | 186.13 | 182.4444
987.176 | 530.2208 | 184.194 | 186.2755 | 182.5303
988.176 | 532.3907 | 184.035 | 186.4402 | 182.382
989.176 | 535.1802 | 183.838 | 186.7097 | 182.3427
990.176 | 555.843 | 183.5183 | 187.0384 | 182.5371
991.176 | 541.112 | 183.3768 | 187.2353 | 182.418
992.176 | 537.456 | 183.4753 | 188.0411 | 182.496
993.176 | 535.0589 | 184.0437 | 188.4578 | 182.5194
994.176 | 548.8992 | 184.3061 | 188.6593 | 182.4892
995.176 | 568.3097 | 184.3596 | 188.7326 | 182.6673
996.176 | 564.6162 | 184.6395 | 188.7663 | 183.5029
997.176 | 562.0483 | 184.7095 | 188.8267 | 185.3942
998.176 | 551.2777 | 185.3293 | 188.7079 | 185.2348
999.176 | 551.6039 | 185.9682 | 188.8955 | 185.881
1000.176 | 565.6723 | 185.5721 | 189.1652 | 186.2996
1001.176 | 572.5467 | 185.5689 | 189.0682 | 186.1935
1002.176 | 589.9196 | 186.0267 | 188.969 | 186.4018
1003.176 | 574.4508 | 185.7296 | 188.8041 | 186.9215
1004.176 | 574.1518 | 185.8803 | 188.8897 | 186.9754
1005.176 | 569.0689 | 186.4417 | 189.0678 | 186.8126
1006.176 | 571.6308 | 186.452 | 189.1833 | 186.8969
1007.176 | 566.6745 | 186.7338 | 189.3248 | 186.8835
1008.176 | 563.137 | 186.9511 | 189.4006 | 186.6879
1009.176 | 578.4577 | 186.9719 | 189.341 | 187.0024
1010.176 | 568.0853 | 187.2555 | 189.6925 | 186.93
1011.176 | 565.5672 | 187.5217 | 189.6404 | 186.6258
1012.176 | 563.6667 | 187.1694 | 189.5688 | 186.3235
1013.176 | 551.4355 | 187.2431 | 189.5914 | 186.1626
1014.176 | 544.6465 | 186.983 | 189.4846 | 186.1103
1015.176 | 537.7632 | 186.6954 | 189.402 | 186.1953
1016.176 | 550.704 | 186.7965 | 189.2491 | 186.1646
1017.176 | 560.3245 | 186.9763 | 189.1124 | 186.0126
1018.176 | 583.1111 | 186.7029 | 188.9002 | 186.0087
1019.176 | 594.0034 | 186.8613 | 188.8605 | 185.8437
1020.176 | 602.2729 | 186.707 | 189.1844 | 185.7394
1021.176 | 613.0569 | 187.1591 | 189.4609 | 185.6416
1022.176 | 613.3662 | 187.3585 | 189.6493 | 186.3308
1023.176 | 636.3173 | 187.7762 | 189.8663 | 186.5345
1024.176 | 628.1849 | 187.9137 | 190.044 | 186.5942
1025.176 | 622.7385 | 187.994 | 190.0378 | 186.4365
1026.176 | 615.6026 | 188.3696 | 190.2255 | 186.483
1027.176 | 607.0089 | 188.3144 | 190.3822 | 186.305
1028.176 | 596.9384 | 188.6957 | 190.6511 | 185.9498
1029.176 | 612.053 | 188.7822 | 190.97 | 185.8843
1030.176 | 608.0907 | 188.6054 | 191.1318 | 186.0814
1031.176 | 612.9777 | 188.8878 | 191.351 | 186.8816
1032.176 | 611.677 | 189.001 | 191.3704 | 187.1942
1033.176 | 631.3281 | 188.8369 | 191.5606 | 187.6982
1034.176 | 638.8735 | 188.4931 | 191.4782 | 188.0307
1035.176 | 624.8328 | 188.6875 | 191.7804 | 187.8596
1036.176 | 623.3714 | 188.7846 | 191.7584 | 187.9823
1037.176 | 616.043 | 188.7469 | 191.8775 | 187.9654
1038.176 | 610.8168 | 189.0292 | 191.9944 | 188.0594
1039.176 | 594.9634 | 189.7025 | 192.0639 | 187.7534
1040.176 | 613.8119 | 189.2797 | 192.5304 | 187.7275
1041.176 | 608.9136 | 189.3846 | 193.0321 | 187.5851
1042.176 | 602.7266 | 189.1458 | 193.3177 | 187.6167
1043.176 | 599.669 | 189.1751 | 193.5911 | 187.5376
1044.176 | 594.8407 | 189.5476 | 193.5908 | 187.8236
1045.176 | 595.8228 | 189.6631 | 193.6155 | 187.9898
1046.176 | 597.8087 | 189.5011 | 193.6523 | 187.9688
1047.176 | 589.3007 | 189.5482 | 193.753 | 187.5931
1048.176 | 606.0739 | 189.473 | 193.9252 | 187.4606
1049.176 | 604.7413 | 189.9285 | 194.0883 | 187.3125
1050.176 | 594.4195 | 190.1602 | 193.8287 | 187.7272
1051.176 | 592.6513 | 190.3335 | 193.4326 | 187.9999
1052.176 | 581.9035 | 190.2751 | 193.2716 | 187.9773
1053.176 | 586.8519 | 190.6358 | 193.1104 | 187.6585
1054.176 | 571.1653 | 190.7723 | 193.2848 | 187.4765
1055.176 | 574.2184 | 191.0165 | 193.9238 | 187.4332
1056.176 | 569.3973 | 191.3355 | 194.206 | 187.3176
1057.176 | 575.249 | 191.9195 | 194.6949 | 187.607
1058.176 | 569.0622 | 192.5786 | 194.7639 | 187.7637
1059.176 | 570.6842 | 192.6513 | 194.7854 | 187.6202
1060.176 | 582.9943 | 192.4652 | 194.7501 | 187.5069
1061.176 | 584.2474 | 192.4593 | 194.809 | 187.4009
1062.176 | 595.6895 | 192.5065 | 194.8055 | 187.546
1063.176 | 601.4226 | 192.0041 | 194.7182 | 187.4771
1064.176 | 602.6316 | 191.6372 | 194.6083 | 187.4032
1065.176 | 616.5371 | 191.1965 | 194.3075 | 188.1895
1066.176 | 614.8186 | 191.1523 | 194.2092 | 188.0802
1067.176 | 633.778 | 191.3335 | 194.0864 | 188.2777
1068.176 | 620.2299 | 191.3533 | 194.0045 | 187.9451
1069.176 | 602.5866 | 190.9744 | 193.9156 | 187.9454
1070.176 | 609.6107 | 190.5783 | 193.8724 | 188.0149
1071.1917 | 606.7282 | 190.2857 | 193.7954 | 187.981
1072.176 | 593.6877 | 190.561 | 193.769 | 188.0117
1073.176 | 599.3681 | 190.868 | 193.6451 | 187.6258
1074.176 | 608.291 | 190.8824 | 193.5095 | 187.8372
1075.176 | 613.8956 | 190.6507 | 193.399 | 187.6519
1076.176 | 602.8776 | 190.0487 | 193.2733 | 187.6961
1077.176 | 609.2392 | 189.9078 | 193.1498 | 187.9564
1078.176 | 626.7133 | 189.8124 | 193.1134 | 188.051
1079.176 | 631.2364 | 189.4413 | 193.0157 | 187.9942
1080.176 | 632.5094 | 189.5397 | 192.7536 | 188.4018
1081.176 | 640.4515 | 189.4505 | 192.5488 | 188.1061
1082.176 | 642.2065 | 189.0777 | 192.2512 | 188.1213
1083.176 | 652.3172 | 188.7667 | 191.9412 | 187.9756
1084.176 | 649.7289 | 188.6826 | 191.8342 | 187.9526
1085.176 | 634.8742 | 188.6435 | 191.8464 | 187.8605
1086.176 | 627.3594 | 188.9294 | 191.9265 | 187.8227
1087.176 | 611.3159 | 188.8082 | 192.0557 | 187.8629
1088.176 | 607.9886 | 188.7041 | 192.1637 | 188.4884
1089.176 | 612.5158 | 189.498 | 192.2169 | 189.0591
1090.176 | 607.5924 | 190.0892 | 192.372 | 189.1045
1091.176 | 618.9925 | 190.1532 | 192.6217 | 188.8592
1092.176 | 627.8637 | 190.4435 | 192.8294 | 188.7686
1093.176 | 645.4225 | 190.5898 | 193.177 | 188.7856
1094.176 | 651.9357 | 190.7343 | 193.4356 | 188.5232
1095.176 | 640.9611 | 190.7953 | 193.6664 | 188.5827
1096.176 | 637.1065 | 190.8821 | 194.0339 | 188.7466
1097.176 | 641.7691 | 190.8249 | 194.2538 | 188.7568
1098.176 | 641.6014 | 190.7417 | 194.7047 | 188.9497
1099.176 | 652.367 | 190.644 | 194.8506 | 188.7904
1100.176 | 662.22 | 190.9716 | 194.7395 | 188.4882
1101.1917 | 665.2093 | 191.6846 | 194.7382 | 188.4812
1102.176 | 669.4627 | 191.5228 | 194.8303 | 188.4224
1103.176 | 675.7148 | 191.4039 | 195.075 | 188.6089
1104.176 | 672.2127 | 193.1173 | 195.4566 | 189.4609
1105.176 | 681.6229 | 192.8591 | 195.6815 | 190.0084
1106.176 | 662.7682 | 192.8168 | 196.0557 | 190.2343
1107.176 | 651.6127 | 193.6676 | 196.1881 | 190.6825
1108.176 | 656.9892 | 194.5217 | 196.5723 | 191.1621
1109.176 | 656.5274 | 194.115 | 196.9883 | 191.7494
1110.176 | 648.5611 | 194.808 | 197.3192 | 192.0915
1111.176 | 653.1215 | 194.7155 | 197.5038 | 192.3283
1112.176 | 652.0842 | 194.6878 | 197.4971 | 192.5629
1113.176 | 652.5089 | 194.6502 | 197.449 | 192.4331
1114.176 | 632.4449 | 194.7044 | 197.3074 | 192.1517
1115.176 | 619.5229 | 194.9513 | 197.4681 | 191.6293
1116.176 | 620.2662 | 195.3541 | 197.2589 | 191.4714
1117.176 | 611.995 | 194.9689 | 197.1125 | 192.1524
1118.176 | 601.1235 | 195.1147 | 196.9162 | 192.8537
1119.176 | 612.7104 | 195.5871 | 196.8746 | 193.5474
1120.176 | 604.7182 | 195.5532 | 196.8615 | 193.8915
1121.176 | 610.3895 | 195.7998 | 196.9143 | 193.8127
1122.176 | 612.339 | 195.8705 | 196.9877 | 193.7088
1123.176 | 603.1526 | 196.0379 | 197.2035 | 193.8846
1124.176 | 611.2578 | 196.0182 | 196.9293 | 193.3084
1125.176 | 606.6089 | 196.025 | 196.8674 | 193.1125
1126.176 | 600.7793 | 195.6781 | 196.8044 | 192.985
1127.176 | 613.7342 | 195.6899 | 196.7793 | 193.3236
1128.176 | 630.0666 | 195.7553 | 196.9309 | 193.2515
1129.176 | 633.2371 | 195.7521 | 196.9289 | 192.9012
1130.176 | 635.2841 | 196.2006 | 197.0237 | 192.6684
1131.176 | 647.0766 | 196.4178 | 197.1433 | 193.3958
1132.176 | 642.3743 | 196.6726 | 197.0928 | 193.4338
1133.176 | 644.4833 | 196.6321 | 196.8421 | 193.2291
1134.176 | 637.1836 | 196.5709 | 196.7626 | 193.1661
1135.176 | 644.9541 | 196.5786 | 196.7311 | 193.2061
1136.176 | 639.1762 | 196.4788 | 196.6952 | 193.2846
1137.176 | 637.8471 | 196.6705 | 196.6474 | 193.3645
1138.176 | 647.2961 | 197.1244 | 196.6295 | 193.3169
1139.176 | 651.4503 | 197.3379 | 196.8791 | 192.8442
1140.176 | 662.7268 | 197.4044 | 197.1672 | 193.4748
1141.176 | 668.9093 | 197.4692 | 197.349 | 193.5406
1142.176 | 680.9947 | 198.0323 | 197.7431 | 194.3716
1143.176 | 672.696 | 198.5212 | 199.1812 | 194.8249
1144.176 | 665.657 | 199.0658 | 199.6409 | 195.0538
1145.176 | 651.8 | 199.055 | 199.7972 | 194.8443
1146.176 | 651.8232 | 199.2794 | 200.0624 | 195.1516
1147.176 | 640.3603 | 199.7878 | 200.1847 | 195.3938
1148.176 | 624.4537 | 199.9873 | 200.4731 | 195.6909
1149.176 | 614.6127 | 199.581 | 200.6209 | 196.2325
1150.176 | 617.3315 | 199.5603 | 200.8469 | 196.1435
1151.176 | 612.5322 | 199.3883 | 200.9466 | 196.9637
1152.176 | 628.8949 | 199.7275 | 201.2498 | 196.8331
1153.176 | 633.6359 | 199.9422 | 201.4966 | 196.9256
1154.176 | 627.9031 | 199.5252 | 201.4899 | 196.9516
1155.176 | 631.9097 | 199.3816 | 201.3814 | 196.8904
1156.176 | 618.1239 | 199.2332 | 201.2881 | 197.0576
1157.176 | 626.9358 | 199.0466 | 201.3218 | 196.947
1158.176 | 632.6465 | 199.1044 | 201.1968 | 196.5553
1159.176 | 631.9244 | 198.7891 | 201.1368 | 196.4466
1160.176 | 613.6494 | 198.4868 | 201.0241 | 196.4634
1161.176 | 623.8884 | 198.3266 | 200.8382 | 195.9464
1162.176 | 621.1942 | 198.4598 | 200.6735 | 196.0446
1163.176 | 607.4915 | 198.2823 | 200.5769 | 195.7778
1164.176 | 605.114 | 198.4992 | 200.6204 | 195.6686
1165.176 | 602.319 | 198.7355 | 200.6966 | 195.8869
1166.176 | 608.5943 | 198.7286 | 200.5911 | 195.6827
1167.176 | 612.6607 | 198.7872 | 200.8564 | 195.445
1168.176 | 626.229 | 198.9656 | 201.0261 | 195.2517
1169.176 | 630.5502 | 199.0114 | 201.2204 | 195.7653
1170.176 | 628.9679 | 199.1885 | 201.6193 | 196.0329
1171.176 | 611.3616 | 199.4802 | 202.3115 | 195.8464
1172.176 | 599.0612 | 199.3686 | 203.0593 | 195.5974
1173.176 | 616.83 | 200.0472 | 203.5473 | 195.9393
1174.176 | 597.9484 | 199.9215 | 203.954 | 196.104
1175.176 | 609.7799 | 199.9705 | 203.961 | 196.3269
1176.176 | 617.5239 | 200.1306 | 204.3916 | 196.8501
1177.176 | 618.153 | 200.0704 | 204.3774 | 196.7428
1178.176 | 628.7123 | 199.8589 | 204.5065 | 196.6994
1179.176 | 635.3515 | 199.8002 | 204.6856 | 196.8317
1180.176 | 618.5491 | 199.633 | 204.7843 | 197.4061
1181.176 | 617.3102 | 199.6843 | 204.696 | 197.1478
1182.176 | 614.3182 | 199.6332 | 204.4399 | 196.8395
1183.176 | 607.5303 | 199.6888 | 204.3033 | 196.7421
1184.176 | 619.7466 | 199.7305 | 204.407 | 196.8352
1185.176 | 625.5436 | 200.3805 | 204.6342 | 197.1806
1186.176 | 635.482 | 200.3885 | 204.9908 | 197.2978
1187.176 | 646.9571 | 200.6528 | 205.1569 | 196.9934
1188.176 | 630.6666 | 200.9291 | 205.2028 | 197.3699
1189.176 | 625.0693 | 200.9809 | 205.3762 | 197.3203
1190.176 | 636.5315 | 200.9837 | 205.4774 | 197.7005
1191.1917 | 632.5043 | 200.6073 | 205.4487 | 198.2569
1192.176 | 628.4869 | 200.3184 | 205.35 | 198.0719
1193.176 | 643.2455 | 200.6877 | 205.0714 | 198.1388
1194.176 | 624.1449 | 200.7292 | 205.0874 | 198.0811
1195.176 | 621.7528 | 200.7373 | 205.0114 | 198.1811
1196.176 | 619.7253 | 200.4313 | 205.026 | 197.8836
1197.176 | 606.6833 | 200.2553 | 204.8845 | 198.3032
1198.176 | 605.1368 | 200.079 | 204.6049 | 198.1971
1199.176 | 608.279 | 200.052 | 204.3824 | 198.3311
1200.176 | 620.8356 | 199.9183 | 204.1937 | 198.0545
1201.176 | 630.6764 | 199.9059 | 204.0994 | 197.7493
1202.176 | 636.1923 | 199.6745 | 204.0304 | 197.4374
1203.176 | 643.5692 | 199.8038 | 203.6647 | 197.2859
1204.176 | 624.6197 | 199.7978 | 203.3641 | 196.9136
1205.176 | 616.4788 | 199.9104 | 203.1566 | 196.773
1206.176 | 611.837 | 200.311 | 202.9382 | 196.7367
1207.176 | 610.4146 | 200.0768 | 202.6669 | 196.9987
1208.176 | 600.8525 | 200.1397 | 202.7632 | 196.77
1209.176 | 581.9261 | 200.0849 | 202.777 | 196.5713
1210.176 | 570.5391 | 200.7627 | 202.687 | 196.2545
1211.176 | 574.7804 | 200.7341 | 202.3965 | 196.2017
1212.176 | 587.911 | 200.9999 | 202.2078 | 196.3704
1213.176 | 572.7245 | 201.1675 | 202.2047 | 196.4172
1214.176 | 552.4719 | 201.4596 | 202.1415 | 196.5164
1215.176 | 534.6785 | 201.4563 | 202.2109 | 196.7166
1216.176 | 520.4252 | 202.2917 | 202.2327 | 196.612
1217.176 | 505.5691 | 202.6011 | 202.1481 | 196.9425
1218.176 | 489.7671 | 202.5514 | 202.0615 | 197.5295
1219.176 | 480.7038 | 202.7634 | 202.2034 | 197.3888
1220.176 | 481.4543 | 203.0234 | 202.1663 | 197.2
1221.176 | 503.881 | 203.2445 | 202.5747 | 197.2484
1222.176 | 505.2652 | 204.018 | 202.3716 | 197.2642
1223.176 | 499.7295 | 204.6031 | 202.2148 | 197.3186
1224.176 | 497.4765 | 205.1171 | 202.4305 | 197.7392
1225.176 | 503.4625 | 205.2226 | 202.3861 | 197.3945
1226.176 | 491.0365 | 205.5301 | 202.2753 | 197.6476
1227.176 | 479.6416 | 205.7157 | 202.1555 | 197.7901
1228.176 | 491.8458 | 205.7532 | 202.0713 | 197.5865
1229.176 | 503.0373 | 205.8865 | 202.1835 | 197.4447
1230.176 | 532.2708 | 205.5712 | 202.3522 | 197.7291
1231.176 | 550.2257 | 205.5408 | 202.4809 | 198.0348
1232.176 | 534.2854 | 205.4693 | 202.5863 | 198.9457
1233.176 | 516.5736 | 205.1309 | 202.8329 | 199.2489
1234.176 | 502.1486 | 205.5448 | 203.3606 | 199.21
1235.176 | 488.0059 | 205.4311 | 203.4692 | 198.9271
1236.176 | 478.1522 | 204.8244 | 203.6302 | 198.8857
1237.176 | 470.4278 | 204.5102 | 203.7696 | 198.6832
1238.176 | 459.1492 | 204.7938 | 203.7097 | 198.556
1239.176 | 449.4575 | 204.6875 | 203.8748 | 198.69
1240.176 | 445.5889 | 204.4467 | 203.8426 | 198.7241
1241.176 | 440.1441 | 204.3065 | 203.7002 | 198.6698
1242.176 | 434.1594 | 203.9947 | 203.6354 | 198.4938
1243.176 | 430.607 | 204.1425 | 203.5178 | 198.1964
1244.176 | 423.932 | 204.2879 | 203.3107 | 198.1006
1245.176 | 416.7095 | 204.4581 | 203.276 | 198.2066
1246.176 | 411.5066 | 204.6404 | 203.1943 | 198.597
1247.176 | 410.8823 | 204.7585 | 203.2588 | 198.808
1248.176 | 433.5904 | 204.8662 | 203.3859 | 199.1981
1249.176 | 432.8993 | 204.5994 | 203.4521 | 199.1997
1250.176 | 429.3841 | 205.0134 | 203.6994 | 199.083
1251.176 | 445.9059 | 205.2349 | 203.9191 | 199.5732
1252.176 | 457.3036 | 205.6787 | 204.1131 | 199.9394
1253.176 | 472.796 | 205.7886 | 203.9202 | 199.6542
1254.176 | 490.7862 | 205.982 | 204.0086 | 200.1761
1255.176 | 495.2904 | 206.0397 | 203.9384 | 199.792
1256.176 | 491.6399 | 206.1648 | 204.0305 | 199.8922
1257.176 | 476.9189 | 206.3415 | 203.7635 | 199.7172
1258.176 | 463.6925 | 206.1088 | 203.7986 | 199.6155
1259.176 | 453.566 | 206.2097 | 203.7502 | 199.3627
1260.176 | 444.4761 | 206.2608 | 203.7753 | 199.6685
1261.176 | 440.3858 | 206.0001 | 203.7959 | 200.1024
1262.176 | 432.1665 | 205.6708 | 203.9999 | 199.9066
1263.176 | 427.3239 | 205.326 | 204.3077 | 199.9492
1264.176 | 422.9458 | 205.1089 | 204.4882 | 200.0411
1265.176 | 418.3101 | 204.8397 | 204.486 | 199.9252
1266.176 | 417.0741 | 204.9528 | 204.6215 | 200.0815
1267.176 | 415.9502 | 204.8386 | 204.8605 | 200.0252
1268.176 | 424.6876 | 205.6344 | 204.8756 | 200.1656
1269.176 | 432.5007 | 205.4918 | 205.0546 | 200.2767
1270.176 | 427.9583 | 205.4991 | 205.0817 | 200.3865
1271.176 | 427.2339 | 205.3989 | 205.376 | 200.5954
1272.176 | 426.6522 | 205.1951 | 205.3016 | 201.1082
1273.176 | 424.9004 | 205.1091 | 205.2184 | 200.9491
1274.176 | 447.5522 | 204.9744 | 205.2459 | 201.4908
1275.176 | 439.2237 | 204.9526 | 205.3993 | 201.5732
1276.176 | 433.6279 | 204.9737 | 205.2881 | 201.2871
1277.176 | 428.4237 | 205.1572 | 205.9939 | 200.9451
1278.176 | 421.0844 | 204.9949 | 205.93 | 200.64
1279.176 | 420.1791 | 204.8222 | 205.8176 | 200.61
1280.176 | 418.5816 | 205.097 | 205.6591 | 200.4274
1281.176 | 414.14 | 205.333 | 205.6312 | 200.3341
1282.176 | 413.8051 | 205.4783 | 205.4052 | 200.2676
1283.176 | 410.2385 | 205.5715 | 205.376 | 200.1971
1284.176 | 409.9945 | 205.5033 | 205.2668 | 200.6182
1285.176 | 407.571 | 205.6218 | 205.3699 | 200.0639
1286.176 | 403.1723 | 205.6556 | 205.3776 | 199.8454
1287.176 | 396.4853 | 205.6027 | 205.2898 | 200.8248
1288.176 | 393.9341 | 205.6072 | 205.3748 | 200.5926
1289.176 | 402.0469 | 205.3172 | 205.3934 | 200.1774
1290.176 | 422.5457 | 205.2349 | 205.3152 | 199.8872
1291.176 | 440.5146 | 205.0829 | 205.3368 | 200.1174
1292.176 | 457.6262 | 204.9471 | 205.2894 | 200.1927
1293.176 | 446.4807 | 204.9746 | 205.1833 | 200.3404
1294.176 | 470.7911 | 204.983 | 205.0295 | 200.603
1295.176 | 478.3494 | 204.8521 | 204.8147 | 200.6193
1296.176 | 488.861 | 204.8833 | 204.6146 | 201.2095
1297.176 | 506.0498 | 204.8216 | 204.4705 | 201.3188
1298.176 | 543.2959 | 204.9927 | 204.6624 | 201.1612
1299.176 | 553.263 | 204.9925 | 204.6 | 201.192
1300.176 | 546.0087 | 204.6333 | 204.5395 | 201.7108
1301.176 | 531.2749 | 204.4755 | 204.3617 | 201.8622
1302.176 | 512.0015 | 204.548 | 204.3425 | 201.4777
1303.176 | 495.6509 | 204.3676 | 204.2928 | 201.4062
1304.176 | 483.3709 | 204.5423 | 204.2422 | 201.6405
1305.176 | 483.8799 | 204.513 | 203.9878 | 201.7168
1306.176 | 476.1427 | 204.8275 | 203.7305 | 201.905
1307.176 | 468.5677 | 204.9048 | 203.4916 | 201.8927
1308.176 | 460.8424 | 204.895 | 203.5748 | 201.5842
1309.176 | 453.4671 | 205.0841 | 203.6708 | 201.7215
1310.176 | 445.086 | 204.9266 | 203.6002 | 201.723
1311.176 | 439.7065 | 204.5446 | 203.5605 | 201.6974
1312.176 | 442.4226 | 204.4969 | 203.7072 | 201.9601
1313.176 | 438.1804 | 204.7897 | 203.7756 | 202.318
1314.176 | 430.671 | 204.807 | 203.705 | 202.4459
1315.176 | 425.1747 | 204.9295 | 203.9376 | 202.6906
1316.176 | 422.1593 | 204.9647 | 204.0683 | 203.0874
1317.176 | 421.1879 | 204.8144 | 204.4319 | 203.1146
1318.176 | 421.6915 | 204.9664 | 204.3802 | 202.7246
1319.176 | 418.59 | 205.0465 | 204.5837 | 202.3235
1320.176 | 416.5723 | 205.5938 | 204.5113 | 202.1949
1321.176 | 414.7172 | 206.4028 | 204.3698 | 202.9094
1322.176 | 410.6534 | 206.8492 | 204.1945 | 203.6066
1323.176 | 405.1825 | 206.4449 | 204.3374 | 203.4507
1324.176 | 401.1465 | 206.3962 | 204.4237 | 203.4863
1325.176 | 397.9295 | 206.8527 | 204.4511 | 203.745
1326.176 | 393.9615 | 206.9667 | 204.5195 | 204.0795
1327.176 | 388.3571 | 206.9594 | 204.5608 | 204.0989
1328.176 | 383.4559 | 206.925 | 204.6273 | 204.0773
1329.176 | 382.3431 | 206.9048 | 204.5815 | 204.4375
1330.176 | 379.3051 | 207.0872 | 204.4809 | 204.8657
1331.176 | 379.0598 | 207.1121 | 204.5275 | 205.1337
1332.176 | 377.5827 | 207.0831 | 204.2357 | 204.8342
1333.176 | 375.9298 | 207.0987 | 204.1806 | 204.9442
1334.176 | 369.3824 | 206.7143 | 203.9713 | 205.0177
1335.176 | 364.4768 | 206.8086 | 203.9075 | 204.9429
1336.176 | 358.9002 | 206.9743 | 203.7939 | 204.927
1337.176 | 356.33 | 207.3597 | 203.7265 | 205.0355
1338.176 | 353.3114 | 207.5257 | 203.5289 | 205.3201
1339.176 | 349.7535 | 207.6714 | 203.4855 | 205.1621
1340.176 | 347.9488 | 207.8276 | 203.4301 | 205.0872
1341.176 | 347.227 | 208.1053 | 203.7247 | 204.8175
1342.176 | 351.0509 | 208.6804 | 203.9103 | 204.619
1343.176 | 348.7167 | 208.8844 | 204.272 | 204.4597
1344.176 | 346.5127 | 208.9248 | 204.5597 | 204.6684
1345.176 | 346.6786 | 208.9099 | 204.47 | 205.0885
1346.176 | 346.953 | 209.0229 | 204.7396 | 205.3844
1347.176 | 347.6106 | 209.5057 | 204.7601 | 205.6015
1348.176 | 347.9499 | 209.4976 | 204.7467 | 205.788
1349.176 | 347.9902 | 209.4419 | 204.9775 | 205.5435
1350.176 | 344.1883 | 209.718 | 205.071 | 205.3232
1351.176 | 343.7558 | 210.0137 | 205.1421 | 205.2913
1352.176 | 345.3114 | 210.4355 | 205.063 | 205.514
1353.176 | 358.2184 | 210.5849 | 205.2962 | 205.468
1354.176 | 358.8108 | 210.9061 | 205.5904 | 205.2208
1355.176 | 356.3947 | 210.7498 | 205.6454 | 205.4483
1356.176 | 356.5407 | 211.0902 | 205.7757 | 205.9539
1357.176 | 353.7519 | 210.8784 | 206.0037 | 205.5273
1358.176 | 353.0519 | 210.9077 | 206.1816 | 205.772
1359.176 | 356.0807 | 210.7276 | 206.0728 | 205.3784
1360.176 | 372.384 | 210.8318 | 206.1473 | 205.1795
1361.176 | 374.3394 | 210.7277 | 206.065 | 204.7592
1362.176 | 374.5317 | 210.5936 | 206.1968 | 204.2305
1363.176 | 373.8712 | 210.1476 | 206.1406 | 203.8242
1364.176 | 398.2802 | 209.711 | 206.1097 | 203.9151
1365.176 | 415.8781 | 209.4415 | 206.3469 | 203.6422
1366.176 | 413.4698 | 209.3109 | 206.6427 | 203.3045
1367.176 | 442.651 | 209.2447 | 206.707 | 203.6563
1368.176 | 446.3614 | 209.0082 | 206.7995 | 203.2831
1369.176 | 464.2499 | 208.7836 | 207.0859 | 203.1242
1370.176 | 456.7611 | 208.7126 | 207.5558 | 203.4585
1371.176 | 446.2689 | 208.4616 | 207.4826 | 203.8088
1372.176 | 441.3869 | 208.3526 | 207.4992 | 203.3747
1373.176 | 433.5528 | 208.3902 | 207.5248 | 203.2425
1374.176 | 426.3765 | 208.3619 | 207.4833 | 202.806
1375.176 | 422.8749 | 208.1875 | 207.5458 | 202.8786
1376.176 | 416.6961 | 208.4286 | 207.8566 | 203.3545
1377.176 | 411.6622 | 208.6137 | 208.177 | 203.0937
1378.176 | 411.8291 | 208.6586 | 208.8003 | 203.009
1379.176 | 409.2875 | 208.6152 | 209.2309 | 203.0694
1380.176 | 405.9953 | 208.6789 | 209.5927 | 203.2479
1381.176 | 402.8371 | 208.4053 | 209.9148 | 203.0869
1382.176 | 420.744 | 208.5004 | 210.1403 | 203.0451
1383.176 | 432.2797 | 208.5531 | 210.2567 | 203.1231
1384.176 | 436.9804 | 208.3014 | 210.3487 | 203.3297
1385.176 | 432.0905 | 208.6168 | 210.2412 | 203.4696
1386.176 | 430.1328 | 208.6534 | 210.2068 | 203.7248
1387.176 | 425.5276 | 208.7836 | 210.2565 | 204.0363
1388.176 | 425.5483 | 208.7019 | 210.2551 | 203.9603
1389.176 | 423.6261 | 208.1373 | 210.2752 | 203.7642
1390.176 | 439.2473 | 207.9568 | 210.2219 | 203.9475
1391.176 | 459.6969 | 208.0806 | 210.2414 | 203.8703
1392.176 | 461.4206 | 208.0931 | 210.5518 | 204.6667
1393.176 | 465.8394 | 208.363 | 210.7607 | 204.2525
1394.176 | 459.5791 | 208.049 | 211.3118 | 204.9228
1395.176 | 450.3595 | 208.5028 | 211.8472 | 205.5123
1396.176 | 441.1436 | 208.3474 | 212.2265 | 205.3903
1397.176 | 435.8517 | 208.7756 | 212.5604 | 205.3639
1398.176 | 433.2701 | 208.305 | 212.829 | 205.2128
1399.176 | 439.4408 | 208.4851 | 213.0551 | 205.0672
1400.176 | 438.0932 | 208.6918 | 213.2665 | 205.5064
1401.176 | 432.3306 | 208.8044 | 213.6676 | 205.4302
1402.176 | 427.671 | 208.9999 | 213.8771 | 205.2444
1403.176 | 422.9695 | 209.2628 | 214.1142 | 205.0757
1404.176 | 420.843 | 209.2911 | 214.2601 | 205.1343
1405.176 | 434.7223 | 209.4878 | 214.1531 | 205.3012
1406.176 | 439.9227 | 209.2541 | 214.2771 | 205.4237
1407.176 | 439.9261 | 209.2844 | 214.0552 | 206.1132
1408.176 | 434.6951 | 209.1666 | 214.2054 | 206.2752
1409.176 | 444.7459 | 208.9975 | 214.1323 | 206.2353
1410.176 | 442.3053 | 209.0737 | 214.0603 | 206.0268
1411.176 | 464.3118 | 209.1629 | 214.1114 | 205.7178
1412.176 | 457.1762 | 208.8332 | 214.1285 | 206.1821
1413.176 | 469.5432 | 208.7611 | 213.9643 | 206.3834
1414.176 | 465.5561 | 208.5545 | 213.7949 | 206.4036
1415.176 | 494.9122 | 208.8295 | 213.6658 | 206.8482
1416.176 | 503.4507 | 208.948 | 213.7135 | 207.2581
1417.176 | 528.2432 | 209.1826 | 213.6814 | 206.8155
1418.176 | 541.3959 | 209.5619 | 214.0969 | 206.4865
1419.176 | 525.6961 | 209.7664 | 214.0723 | 206.7666
1420.176 | 512.3457 | 209.8422 | 214.1353 | 207.0974
1421.176 | 500.2102 | 209.9683 | 214.2442 | 206.7185
1422.176 | 500.871 | 209.8906 | 214.1857 | 206.9147
1423.176 | 508.2826 | 209.6631 | 214.1416 | 206.7193
1424.176 | 508.0322 | 209.6502 | 214.5242 | 206.7662
1425.176 | 520.8635 | 209.5117 | 214.725 | 206.851
1426.176 | 510.6172 | 209.717 | 214.8001 | 206.7269
1427.176 | 498.4191 | 209.7406 | 214.918 | 206.3768
1428.176 | 488.7159 | 209.6028 | 214.9065 | 206.7261
1429.176 | 477.3508 | 209.3177 | 214.9932 | 207.2361
1430.176 | 469.5222 | 209.4116 | 215.2124 | 207.3346
1431.176 | 458.6015 | 209.1365 | 215.1352 | 206.9109
1432.176 | 452.0662 | 208.9977 | 215.2019 | 206.5325
1433.176 | 444.8507 | 208.7784 | 214.9844 | 206.2578
1434.176 | 437.1043 | 208.7177 | 214.7429 | 206.2341
1435.176 | 431.0208 | 208.4528 | 214.3773 | 206.1392
1436.176 | 424.0823 | 208.4884 | 214.0349 | 206.084
1437.176 | 422.4693 | 208.3024 | 213.9419 | 206.2962
1438.176 | 417.5417 | 208.4157 | 213.8127 | 206.0031
1439.176 | 412.096 | 208.3215 | 213.7203 | 205.9222
1440.176 | 407.3409 | 208.4186 | 213.6094 | 205.5665
1441.176 | 402.3491 | 208.5531 | 213.5237 | 205.5438
1442.1917 | 396.6549 | 208.5718 | 213.4557 | 205.4078
1443.176 | 393.6948 | 208.5661 | 213.282 | 205.3832
1444.176 | 390.4581 | 208.6308 | 213.1792 | 205.2835
1445.176 | 393.2275 | 208.6786 | 212.9757 | 205.1025
1446.176 | 394.7926 | 208.6802 | 212.8382 | 205.2475
1447.176 | 394.8521 | 208.8694 | 212.4694 | 205.3506
1448.176 | 395.3324 | 208.9233 | 212.2519 | 205.071
1449.176 | 396.327 | 208.916 | 212.2588 | 205.2995
1450.176 | 397.5896 | 208.7432 | 212.3393 | 205.0516
1451.176 | 400.2781 | 208.7246 | 212.7009 | 205.4647
1452.176 | 412.894 | 208.6247 | 212.9173 | 205.9705
1453.176 | 422.6006 | 208.5443 | 213.1137 | 206.0225
1454.176 | 417.8229 | 208.5737 | 213.2235 | 206.1282
1455.176 | 413.3806 | 208.6653 | 213.2462 | 205.8982
1456.176 | 409.6513 | 208.4487 | 213.294 | 205.8515
1457.176 | 411.4059 | 208.3694 | 213.2034 | 206.1167
1458.176 | 407.2953 | 208.4512 | 213.1736 | 205.9434
1459.176 | 405.8308 | 208.3943 | 212.9817 | 205.3534
1460.176 | 412.026 | 208.1519 | 212.8723 | 205.0389
1461.176 | 412.2646 | 208.5387 | 212.7529 | 204.8892
1462.176 | 420.3912 | 208.7134 | 212.8138 | 204.9076
1463.176 | 427.008 | 208.5968 | 212.7327 | 205.0808
1464.176 | 421.4861 | 208.6555 | 212.7262 | 205.2001
1465.176 | 416.1799 | 209.1913 | 212.7724 | 205.1225
1466.176 | 412.1791 | 209.5841 | 212.8359 | 205.3471
1467.176 | 407.5239 | 209.7784 | 212.9435 | 205.3616
1468.176 | 406.9496 | 209.8002 | 213.0249 | 205.2511
1469.176 | 412.7431 | 209.6808 | 213.1867 | 204.8333
1470.176 | 410.3643 | 209.8251 | 213.2115 | 204.8041
1471.176 | 406.3087 | 209.7374 | 213.0674 | 204.9468
1472.176 | 406.2101 | 209.7808 | 212.9216 | 205.1073
1473.176 | 411.9023 | 209.5864 | 212.8424 | 205.1826
1474.176 | 455.1593 | 209.6844 | 212.9965 | 205.5886
1475.176 | 446.5442 | 209.6087 | 212.9517 | 205.7796
1476.176 | 442.513 | 209.6264 | 212.8495 | 205.7661
1477.176 | 438.6185 | 209.8563 | 212.7852 | 206.2864
1478.176 | 432.1446 | 210.1525 | 212.7096 | 206.7041
1479.176 | 428.7845 | 210.0608 | 212.7556 | 206.9826
1480.176 | 445.88 | 210.1887 | 212.7341 | 207.6494
1481.176 | 439.8202 | 210.2007 | 212.8864 | 207.9217
1482.176 | 447.4137 | 210.3859 | 213.9337 | 208.2771
1483.176 | 449.8715 | 210.7153 | 214.201 | 208.5358
1484.176 | 448.4758 | 210.7121 | 214.4288 | 208.6886
1485.176 | 454.0509 | 210.6397 | 214.6865 | 208.659
1486.176 | 466.6364 | 210.9749 | 214.5962 | 208.663
1487.176 | 493.2439 | 210.7529 | 214.6729 | 208.2589
1488.176 | 499.0593 | 210.8393 | 214.8764 | 208.4175
1489.176 | 497.7383 | 210.9471 | 215.2129 | 208.4305
1490.176 | 500.6403 | 211.5937 | 215.2767 | 208.6846
1491.176 | 522.3805 | 211.9021 | 215.4415 | 208.7962
1492.176 | 525.7906 | 212.3107 | 215.7597 | 209.315
1493.176 | 511.8632 | 212.7352 | 215.8731 | 209.251
1494.176 | 500.6266 | 212.9344 | 216.1184 | 209.2367
1495.176 | 494.435 | 213.2114 | 216.2507 | 209.356
1496.176 | 488.767 | 213.14 | 216.2962 | 209.0824
1497.176 | 483.304 | 212.826 | 216.2092 | 209.1446
1498.176 | 481.5986 | 212.7376 | 216.0729 | 209.2863
1499.176 | 472.6187 | 213.749 | 216.0024 | 208.9724
1500.176 | 468.4615 | 213.522 | 215.805 | 208.7265
1501.176 | 461.291 | 213.5491 | 215.6776 | 208.6331
1502.176 | 460.0076 | 213.1228 | 215.6088 | 208.3207
1503.176 | 458.9798 | 213.0341 | 215.6857 | 208.0878
1504.176 | 468.7103 | 213.0145 | 215.8771 | 208.0901
1505.176 | 463.6277 | 212.969 | 215.8237 | 208.3259
1506.176 | 459.7854 | 212.8738 | 215.8787 | 208.5882
1507.176 | 454.7014 | 213.1201 | 215.9813 | 208.5439
1508.176 | 447.8814 | 213.251 | 216.1414 | 208.7636
1509.176 | 444.1526 | 213.3495 | 216.3857 | 208.4297
1510.176 | 459.8213 | 213.5634 | 216.697 | 208.342
1511.176 | 483.5105 | 213.4681 | 216.6436 | 208.5966
1512.176 | 484.3156 | 213.6989 | 216.4312 | 208.4505
1513.176 | 518.184 | 214.0135 | 216.7693 | 208.4066
1514.176 | 531.3597 | 214.2134 | 216.785 | 208.7554
1515.176 | 540.7074 | 214.372 | 217.1078 | 208.9922
1516.176 | 530.9698 | 215.2011 | 217.395 | 210.1177
1517.176 | 522.911 | 215.4909 | 217.6494 | 209.7877
1518.176 | 522.7925 | 215.7451 | 217.8636 | 210.5236
1519.176 | 513.9029 | 215.5643 | 218.2472 | 210.6292
1520.176 | 521.7473 | 215.6782 | 218.4071 | 210.6803
1521.176 | 516.4468 | 215.571 | 218.7336 | 211.4127
1522.176 | 506.5031 | 215.3213 | 218.6569 | 211.5504
1523.176 | 499.4322 | 215.1306 | 218.6784 | 211.5062
1524.176 | 519.4976 | 214.9867 | 218.612 | 211.8475
1525.176 | 552.7637 | 215.0916 | 218.4481 | 211.8736
1526.176 | 547.8194 | 214.8514 | 218.2948 | 211.7649
1527.176 | 538.7766 | 214.9448 | 218.0975 | 211.7406
1528.176 | 527.1252 | 214.733 | 218.0486 | 211.7256
1529.176 | 519.4339 | 214.8342 | 218.1846 | 211.7044
1530.176 | 513.4757 | 215.0728 | 218.1533 | 211.6952
1531.176 | 508.89 | 215.3791 | 218.139 | 211.8165
1532.176 | 505.4053 | 215.6994 | 218.4983 | 211.8144
1533.176 | 500.2151 | 215.7947 | 218.2887 | 211.9084
1534.176 | 497.0864 | 215.9001 | 218.225 | 211.9259
1535.176 | 500.8423 | 215.7888 | 218.0872 | 212.1915
1536.176 | 492.4713 | 215.4419 | 218.0577 | 212.2424
1537.176 | 500.7264 | 215.5762 | 217.9778 | 212.4442
1538.176 | 497.1595 | 215.7876 | 217.8284 | 212.8807
1539.176 | 490.7419 | 215.7548 | 217.8583 | 213.1104
1540.176 | 483.4585 | 215.775 | 217.9283 | 212.7277
1541.176 | 475.6772 | 215.4304 | 217.8788 | 212.3206
1542.176 | 468.7284 | 215.7424 | 217.5423 | 211.98
1543.176 | 462.2465 | 215.7034 | 217.2857 | 211.9776
1544.176 | 457.6137 | 216.1104 | 217.216 | 212.2074
1545.176 | 449.1902 | 216.1012 | 217.2629 | 212.6519
1546.176 | 444.995 | 216.3224 | 217.1584 | 213.0387
1547.176 | 446.8781 | 216.6019 | 217.0957 | 213.0674
1548.176 | 440.4833 | 216.5419 | 216.9872 | 213.5723
1549.176 | 446.1746 | 217.1152 | 217.005 | 213.8168
1550.176 | 445.5766 | 217.48 | 216.954 | 214.2303
1551.176 | 441.5246 | 217.4788 | 217.4916 | 214.8018
1552.176 | 445.9611 | 217.372 | 217.4516 | 215.0427
1553.176 | 444.8238 | 217.1043 | 217.4748 | 215.1049
1554.176 | 446.0545 | 217.1137 | 217.5876 | 215.8351
1555.176 | 451.9471 | 217.3759 | 217.6855 | 216.0255
1556.176 | 457.6679 | 217.7252 | 217.6649 | 215.8509
1557.176 | 455.6525 | 218.1598 | 217.9404 | 216.2424
1558.176 | 451.9254 | 218.1758 | 218.1614 | 216.1903
1559.1917 | 450.5219 | 218.1496 | 218.2719 | 215.9423
1560.176 | 450.3528 | 218.0431 | 218.3099 | 215.5885
1561.176 | 447.3662 | 217.5082 | 218.3878 | 215.0661
1562.176 | 443.4145 | 217.8957 | 218.3786 | 214.5391
1563.176 | 440.7003 | 217.7712 | 218.2304 | 214.4307
1564.176 | 435.8771 | 217.883 | 217.9949 | 214.0813
1565.176 | 434.349 | 218.0451 | 217.5962 | 213.6592
1566.176 | 429.9399 | 217.8395 | 217.3262 | 213.8554
1567.176 | 432.3606 | 217.396 | 217.7204 | 214.0295
1568.176 | 446.1211 | 217.1702 | 217.6748 | 213.8628
1569.176 | 453.7724 | 217.156 | 217.6857 | 213.7748
1570.176 | 474.85 | 217.4128 | 218.2531 | 214.0026
1571.176 | 467.801 | 217.3527 | 218.2122 | 213.8964
1572.176 | 477.4375 | 217.453 | 218.4853 | 213.8875
1573.176 | 490.4662 | 217.6547 | 218.6898 | 214.2742
1574.176 | 483.4352 | 217.3673 | 218.9975 | 214.7803
1575.176 | 475.6184 | 217.3296 | 219.2752 | 214.4144
1576.176 | 471.8087 | 217.5432 | 219.393 | 214.3794
1577.176 | 462.8672 | 218.061 | 219.478 | 214.4971
1578.176 | 463.6279 | 218.4461 | 219.5867 | 214.4294
1579.176 | 469.6927 | 218.7166 | 219.4936 | 214.6747
1580.176 | 466.0129 | 218.4985 | 219.3906 | 214.489
1581.176 | 470.8549 | 218.0842 | 219.2395 | 214.2124
1582.176 | 470.9398 | 218.1327 | 219.0848 | 213.678
1583.176 | 463.3421 | 218.2388 | 218.977 | 213.58
1584.176 | 458.7569 | 218.1026 | 218.8432 | 213.6245
1585.176 | 466.0042 | 217.5238 | 218.8834 | 213.8131
1586.176 | 462.0106 | 217.406 | 218.757 | 214.0354
1587.176 | 463.8873 | 217.3611 | 218.7461 | 213.9923
1588.176 | 466.9269 | 217.3796 | 218.7603 | 214.4286
1589.176 | 484.2535 | 217.4493 | 218.8695 | 214.875
1590.176 | 486.6824 | 217.5142 | 219.0995 | 214.7127
1591.176 | 485.8549 | 217.6174 | 219.2886 | 215.0186
1592.176 | 482.4075 | 217.5401 | 219.2884 | 215.5206
1593.176 | 476.4254 | 217.7941 | 219.5921 | 215.3754
1594.176 | 478.2971 | 218.1324 | 219.7997 | 215.4091
1595.176 | 475.6478 | 218.1457 | 219.9252 | 215.4039
1596.176 | 501.5052 | 218.3166 | 219.8825 | 215.2066
1597.176 | 492.2402 | 218.8836 | 219.8754 | 215.4923
1598.176 | 485.4954 | 218.9993 | 220.2672 | 215.2048
1599.176 | 481.8082 | 219.1256 | 220.3529 | 215.5946
1600.176 | 484.9898 | 219.0116 | 220.2699 | 215.8046
1601.176 | 483.6691 | 218.9819 | 220.2146 | 216.0971
1602.176 | 480.9664 | 219.215 | 220.2196 | 216.1548
1603.176 | 480.8781 | 219.1758 | 220.2234 | 216.5623
1604.176 | 474.0335 | 219.1435 | 220.2144 | 216.8415
1605.176 | 473.2391 | 219.2356 | 220.3705 | 216.9242
1606.176 | 465.8612 | 219.1565 | 220.3716 | 216.6376
1607.176 | 455.0782 | 218.9757 | 220.2061 | 216.5374
1608.176 | 451.4292 | 219.4418 | 220.0571 | 216.4476
1609.176 | 452.9186 | 219.8329 | 219.8692 | 216.6695
1610.176 | 454.6258 | 219.9714 | 219.9539 | 216.9518
1611.176 | 452.7218 | 219.7006 | 220.1572 | 216.6925
1612.176 | 450.9359 | 219.6174 | 220.1411 | 216.4497
1613.176 | 448.9239 | 219.9325 | 220.3645 | 216.5746
1614.176 | 457.1678 | 220.1156 | 220.5426 | 216.6972
1615.176 | 469.2907 | 220.4437 | 220.888 | 217.1572
1616.176 | 475.7895 | 220.6077 | 220.912 | 217.3449
1617.176 | 475.5856 | 220.8733 | 220.9443 | 217.9472
1618.176 | 477.8678 | 220.9969 | 220.9516 | 218.2806
1619.176 | 474.5851 | 220.9734 | 220.676 | 217.8828
1620.176 | 467.9108 | 221.2047 | 220.7994 | 218.1659
1621.176 | 470.7259 | 221.4437 | 221.1331 | 218.1909
1622.176 | 479.927 | 221.6389 | 221.9548 | 218.2061
1623.176 | 484.2318 | 221.4189 | 221.9141 | 218.8026
1624.176 | 482.1028 | 220.9595 | 222.5198 | 218.2646
1625.176 | 478.3838 | 221.0134 | 222.5711 | 217.9552
1626.176 | 475.9873 | 220.9816 | 222.6113 | 217.5661
1627.176 | 471.327 | 220.7239 | 222.5382 | 217.384
1628.176 | 470.508 | 221.0364 | 222.5666 | 217.0965
1629.176 | 464.5219 | 220.6701 | 222.6376 | 217.0601
1630.176 | 468.2499 | 220.5288 | 222.6474 | 217.1155
1631.176 | 458.6676 | 220.4305 | 222.4823 | 217.1076
1632.176 | 456.7739 | 220.7397 | 222.3416 | 216.8865
1633.176 | 457.1703 | 220.9564 | 222.1201 | 216.6992
1634.176 | 452.7602 | 220.7914 | 222.0993 | 217.2407
1635.176 | 449.4323 | 221.0514 | 222.0085 | 217.6474
1636.176 | 443.6065 | 221.0911 | 221.9109 | 217.4328
1637.176 | 445.6603 | 221.4721 | 221.7105 | 217.2926
1638.176 | 439.4722 | 221.6642 | 221.5217 | 217.0207
1639.176 | 438.0991 | 222.0081 | 221.3786 | 216.7691
1640.176 | 434.3067 | 222.1334 | 221.4937 | 216.844
1641.176 | 431.5983 | 222.7751 | 221.5963 | 216.8694
1642.176 | 432.0868 | 223.0819 | 221.7994 | 216.9309
1643.176 | 433.9301 | 223.7739 | 221.7918 | 216.95
1644.176 | 433.8501 | 224.2979 | 222.3127 | 217.1897
1645.176 | 431.1775 | 224.7643 | 222.2819 | 217.6949
1646.176 | 428.7862 | 225.0058 | 222.1175 | 217.858
1647.176 | 427.0435 | 225.1973 | 221.9364 | 217.7355
1648.176 | 423.9441 | 225.2333 | 222.0496 | 217.784
1649.176 | 425.7864 | 225.1733 | 222.0687 | 217.7962
1650.176 | 428.5026 | 224.9257 | 221.946 | 217.6622
1651.176 | 427.6996 | 224.9145 | 221.8406 | 217.535
1652.176 | 426.2416 | 224.8912 | 221.8873 | 217.3485
1653.176 | 424.3642 | 224.77 | 221.9478 | 217.8049
1654.176 | 425.8266 | 224.3 | 221.8705 | 218.3704
1655.176 | 427.67 | 224.1615 | 221.772 | 218.0432
1656.176 | 431.7473 | 224.2181 | 221.8725 | 218.0273
1657.176 | 432.4738 | 224.3434 | 222.0136 | 218.0669
1658.176 | 435.8827 | 224.4635 | 222.0366 | 218.0028
1659.176 | 440.9879 | 224.428 | 221.9695 | 218.3564
1660.176 | 445.8864 | 224.4801 | 221.8206 | 218.3085
1661.176 | 449.3773 | 224.2725 | 221.6078 | 218.362
1662.176 | 448.4696 | 224.4482 | 221.6046 | 218.1446
1663.176 | 446.9182 | 224.3585 | 221.5895 | 218.3456
1664.176 | 447.336 | 224.2598 | 221.7464 | 218.8817
1665.176 | 445.3305 | 224.0682 | 222.0806 | 218.645
1666.176 | 445.3783 | 224.0294 | 222.4068 | 219.1852
1667.176 | 454.1077 | 223.8802 | 222.7018 | 219.0104
1668.176 | 465.3426 | 224.1241 | 222.966 | 218.9323
1669.176 | 462.7458 | 224.359 | 223.1513 | 218.771
1670.176 | 458.8869 | 224.1926 | 223.3792 | 218.7014
1671.176 | 468.3332 | 223.9604 | 223.6429 | 218.4394
1672.176 | 463.6915 | 224.1503 | 223.8062 | 218.4715
1673.176 | 459.4387 | 224.9515 | 224.0859 | 219.1186
1674.176 | 458.6221 | 224.4632 | 224.5355 | 219.4245
1675.176 | 458.2317 | 224.4168 | 224.9998 | 219.5867
1676.176 | 464.0434 | 223.9513 | 225.3554 | 220.0226
1677.176 | 462.2117 | 223.847 | 226.0509 | 219.72
1678.176 | 481.3838 | 223.8654 | 225.8085 | 219.6662
1679.176 | 504.6574 | 223.6429 | 225.5261 | 220.0151
1680.176 | 499.8218 | 223.2849 | 225.3329 | 219.6924
1681.176 | 503.5684 | 223.0336 | 225.0996 | 219.9608
1682.176 | 505.152 | 223.2609 | 224.8949 | 219.8685
1683.176 | 498.6384 | 223.1324 | 224.7027 | 219.3875
1684.176 | 493.7144 | 222.6913 | 224.5971 | 219.8621
1685.176 | 489.3676 | 222.7722 | 224.8397 | 220.0883
1686.176 | 516.6055 | 222.7353 | 224.737 | 220.0694
1687.176 | 515.0618 | 222.68 | 224.7447 | 219.8994
1688.176 | 518.5951 | 222.5882 | 224.7781 | 219.8682
1689.176 | 512.8412 | 222.7862 | 224.9731 | 219.7766
1690.176 | 506.4347 | 222.6614 | 224.9894 | 219.4936
1691.176 | 499.4578 | 222.834 | 224.9922 | 219.2228
1692.176 | 493.3696 | 223.2342 | 224.9348 | 219.2728
1693.176 | 486.0954 | 222.7532 | 224.9041 | 218.926
1694.176 | 482.1855 | 222.3826 | 224.8166 | 218.6999
1695.176 | 477.3425 | 222.3441 | 224.5548 | 218.8867
1696.176 | 474.0971 | 222.3079 | 224.5221 | 218.8499
1697.176 | 471.6467 | 222.4243 | 224.3151 | 218.7398
1698.176 | 477.3394 | 222.8832 | 224.2343 | 218.7633
1699.176 | 479.4178 | 223.1663 | 224.3298 | 218.5833
1700.176 | 478.0699 | 223.1425 | 224.299 | 218.7538
1701.176 | 473.0679 | 222.988 | 224.5977 | 218.683
1702.176 | 472.9391 | 223.2827 | 224.6172 | 218.7814
1703.176 | 484.4725 | 223.2517 | 224.7239 | 219.0177
1704.176 | 495.9514 | 223.3041 | 224.8152 | 219.0014
1705.176 | 491.7232 | 223.3714 | 225.0717 | 219.1849
1706.176 | 489.0888 | 223.3035 | 225.044 | 219.2918
1707.176 | 487.5722 | 223.1681 | 225.0729 | 219.3131
1708.176 | 480.0703 | 223.3084 | 225.2815 | 219.4716
1709.176 | 479.1845 | 223.2655 | 225.6971 | 219.6592
1710.176 | 473.7889 | 222.8117 | 225.7299 | 219.5489
1711.176 | 468.532 | 222.8158 | 225.7063 | 219.3413
1712.176 | 463.4093 | 222.8587 | 225.745 | 219.1974
1713.176 | 467.3122 | 222.6783 | 225.5761 | 218.9643
1714.176 | 474.3523 | 222.3649 | 225.4307 | 219.1236
1715.176 | 488.2574 | 222.4115 | 225.4189 | 218.9064
1716.176 | 516.9414 | 222.2352 | 225.4901 | 219.3752
1717.176 | 515.5188 | 222.2748 | 225.535 | 219.4561
1718.176 | 508.5318 | 222.4992 | 225.4808 | 219.449
1719.176 | 501.0254 | 222.6649 | 225.3746 | 219.4567
1720.176 | 500.7481 | 222.8844 | 225.2084 | 219.4589
1721.176 | 496.8514 | 222.8434 | 225.1909 | 219.3459
1722.176 | 492.248 | 222.4285 | 225.1749 | 219.2606
1723.176 | 499.2783 | 222.4656 | 225.055 | 219.1824
1724.176 | 501.0801 | 222.4073 | 224.9394 | 219.1266
1725.176 | 505.0024 | 222.5143 | 224.8056 | 218.9078
1726.176 | 499.1872 | 222.267 | 224.7412 | 218.6789
1727.176 | 492.3341 | 222.1495 | 224.6053 | 218.7637
1728.176 | 485.7011 | 222.2231 | 224.3865 | 218.5957
1729.176 | 487.4974 | 222.284 | 224.1176 | 218.1987
1730.176 | 487.5872 | 222.2374 | 223.9177 | 218.0845
1731.176 | 485.8096 | 222.4259 | 223.821 | 218.6853
1732.176 | 479.5445 | 222.724 | 223.6628 | 218.5171
1733.176 | 477.9866 | 223.0818 | 223.5572 | 218.222
1734.176 | 478.7542 | 223.4218 | 223.3351 | 218.2841
1735.176 | 475.5857 | 223.5426 | 223.0976 | 218.5524
1736.176 | 471.9821 | 223.9497 | 222.9174 | 218.7847
1737.176 | 473.3156 | 224.2308 | 222.811 | 218.7116
1738.176 | 471.3128 | 224.5113 | 222.907 | 218.9257
1739.176 | 471.2363 | 224.5305 | 223.0007 | 218.8947
1740.176 | 474.3823 | 224.5728 | 223.1288 | 218.9509
1741.176 | 469.7824 | 224.3173 | 223.0545 | 219.1665
1742.176 | 464.6271 | 224.203 | 222.8477 | 219.1994
1743.176 | 462.9202 | 224.1836 | 222.6631 | 218.9613
1744.176 | 459.4028 | 224.0132 | 222.7517 | 218.5897
1745.176 | 451.4362 | 223.6767 | 222.6464 | 218.2178
1746.176 | 451.3264 | 223.437 | 222.6378 | 218.5179
1747.176 | 449.38 | 223.5233 | 222.8307 | 218.0484
1748.176 | 450.5619 | 223.4615 | 222.8277 | 217.872
1749.176 | 451.6659 | 223.5759 | 222.8227 | 217.4337
1750.176 | 456.9716 | 224.0121 | 222.7786 | 217.2078
1751.176 | 455.1592 | 223.6607 | 222.7022 | 216.8668
1752.176 | 448.6069 | 223.9573 | 222.7896 | 216.8566
1753.176 | 445.5651 | 224.1771 | 222.6845 | 216.961
1754.176 | 451.3529 | 224.2579 | 222.5691 | 217.0468
1755.176 | 445.8436 | 224.1723 | 222.7141 | 217.2577
1756.176 | 444.4649 | 224.4369 | 222.8525 | 217.2548
1757.176 | 439.5234 | 224.4593 | 223.0044 | 217.1915
1758.176 | 437.0599 | 224.9534 | 223.0491 | 217.52
1759.176 | 438.6778 | 224.9375 | 222.9921 | 217.7595
1760.176 | 440.8439 | 224.7971 | 222.9931 | 217.5437
1761.176 | 439.0116 | 224.6429 | 223.1268 | 217.7126
1762.176 | 436.7328 | 224.5773 | 223.2596 | 217.9765
1763.176 | 432.0013 | 224.3482 | 223.1471 | 217.9566
1764.176 | 428.8619 | 224.0795 | 222.9787 | 218.127
1765.176 | 424.0667 | 223.7554 | 222.8029 | 217.958
1766.176 | 425.1334 | 223.6891 | 222.6398 | 217.6678
1767.176 | 430.2265 | 223.22 | 222.5142 | 217.3948
1768.176 | 433.8984 | 223.0239 | 222.3588 | 216.9047
1769.176 | 434.3241 | 223.0801 | 222.2151 | 216.333
1770.176 | 435.4694 | 222.5194 | 222.1171 | 216.4161
1771.176 | 433.0772 | 222.3716 | 222.2083 | 217.0601
1772.176 | 432.0481 | 223.5106 | 222.1846 | 216.6876
1773.176 | 430.6808 | 223.356 | 222.2732 | 216.2731
1774.176 | 428.916 | 223.193 | 222.2053 | 215.9149
1775.176 | 430.327 | 222.8499 | 222.3421 | 216.0585
1776.176 | 432.6982 | 222.8176 | 222.6031 | 216.1528
1777.176 | 434.751 | 222.7111 | 222.7655 | 216.4165
1778.176 | 433.165 | 222.4717 | 222.9703 | 216.2386
1779.176 | 434.8469 | 222.3484 | 223.0603 | 216.6443
1780.176 | 432.1797 | 222.8617 | 223.157 | 216.729
1781.176 | 429.3872 | 223.0229 | 223.7944 | 217.3009
1782.176 | 425.4282 | 222.6017 | 223.9804 | 218.0365
1783.176 | 421.2875 | 222.4173 | 224.1491 | 217.9878
1784.176 | 418.6641 | 222.606 | 224.2657 | 217.8878
1785.176 | 421.1048 | 223.0791 | 224.3865 | 217.5921
1786.176 | 418.1175 | 223.0562 | 224.6031 | 218.1553
1787.176 | 422.498 | 223.2381 | 224.8148 | 218.2174
1788.176 | 426.218 | 223.5656 | 224.9992 | 218.3109
1789.176 | 425.818 | 223.3511 | 225.2707 | 218.3062
1790.176 | 428.2136 | 223.6657 | 225.3112 | 218.9262
1791.176 | 446.3073 | 223.2581 | 225.568 | 218.4982
1792.176 | 449.5472 | 223.1872 | 225.5372 | 218.316
1793.176 | 446.4953 | 222.8651 | 225.5235 | 218.1039
1794.176 | 446.3116 | 222.9256 | 225.4741 | 218.1475
1795.176 | 440.1918 | 222.9851 | 225.3594 | 218.4301
1796.176 | 433.3809 | 222.883 | 225.1825 | 218.1499
1797.176 | 431.0441 | 222.9784 | 225.2087 | 218.2153
1798.176 | 431.1193 | 223.0547 | 224.9738 | 218.06
1799.176 | 429.6359 | 223.1994 | 224.6751 | 218.5374
1800.176 | 428.6048 | 222.7227 | 224.4278 | 218.568
1801.176 | 430.1438 | 222.3477 | 224.1085 | 218.5781
1802.1917 | 430.0562 | 222.3115 | 223.8758 | 218.5648
1803.176 | 428.9159 | 222.2749 | 223.8037 | 218.4738
1804.176 | 429.0758 | 222.2797 | 223.823 | 218.4503
1805.176 | 428.5474 | 222.1189 | 223.7812 | 218.2411
1806.176 | 430.3191 | 221.9507 | 223.732 | 218.1037
1807.176 | 444.2719 | 222.0388 | 223.7147 | 218.1081
1808.176 | 442.9004 | 221.9211 | 223.7006 | 218.1019
1809.176 | 437.2495 | 221.7878 | 223.7915 | 218.2312
1810.176 | 439.2963 | 221.3555 | 223.8377 | 218.77
1811.176 | 440.9326 | 221.2749 | 223.8368 | 218.5953
1812.176 | 444.5448 | 221.6447 | 223.7127 | 218.644
1813.176 | 442.3831 | 222.225 | 223.9044 | 218.9861
1814.176 | 442.7276 | 222.8187 | 223.8753 | 219.2412
1815.176 | 439.4314 | 222.9096 | 224.019 | 219.4381
1816.176 | 466.9838 | 222.9461 | 224.0467 | 219.2657
1817.176 | 489.3973 | 223.1709 | 223.7717 | 219.3774
1818.176 | 513.566 | 223.2912 | 223.537 | 219.5696
1819.176 | 510.6466 | 223.4539 | 223.3587 | 219.5263
1820.176 | 522.1484 | 223.2547 | 223.3024 | 219.3834
1821.176 | 533.9109 | 223.3691 | 223.1347 | 219.2637
1822.176 | 551.7871 | 223.4062 | 223.0829 | 219.2676
1823.176 | 556.5862 | 223.4827 | 223.0357 | 219.3839
1824.176 | 566.2385 | 223.4471 | 222.8958 | 219.6082
1825.176 | 584.0543 | 223.4357 | 222.7385 | 219.5978
1826.176 | 593.7438 | 223.5754 | 222.6027 | 219.6966
1827.176 | 585.6536 | 223.7982 | 222.6655 | 219.7878
1828.176 | 575.8909 | 223.9876 | 222.5872 | 219.7124
1829.176 | 559.4682 | 223.5312 | 222.4816 | 219.4887
1830.176 | 551.155 | 223.2669 | 222.4935 | 219.1075
1831.176 | 577.5185 | 223.4328 | 222.5817 | 218.9645
1832.176 | 591.1785 | 223.8566 | 222.7647 | 219.0843
1833.176 | 603.3995 | 224.22 | 222.8261 | 219.0125
1834.176 | 613.7075 | 223.9264 | 223.0641 | 218.6956
1835.176 | 623.5158 | 223.7225 | 223.1848 | 218.7313
1836.176 | 606.1786 | 223.6895 | 223.427 | 218.8426
1837.176 | 601.8467 | 223.2051 | 223.7248 | 218.726
1838.176 | 594.2728 | 222.6719 | 223.6159 | 218.7439
1839.176 | 598.1195 | 222.3922 | 223.5163 | 218.4051
1840.176 | 592.7986 | 222.2588 | 223.6912 | 218.5408
1841.176 | 591.0893 | 222.2389 | 223.6161 | 218.4463
1842.176 | 591.8318 | 222.1473 | 223.4895 | 218.3892
1843.176 | 599.2523 | 222.0015 | 223.3509 | 218.139
1844.176 | 580.0008 | 221.5069 | 223.1314 | 217.8343
1845.176 | 561.6945 | 221.1787 | 222.8304 | 217.5136
1846.176 | 544.5005 | 220.7947 | 222.6486 | 217.3946
1847.176 | 529.7969 | 220.7573 | 222.3988 | 217.1724
1848.176 | 521.9383 | 220.6645 | 222.2784 | 216.9246
1849.176 | 516.5469 | 221.0618 | 222.0564 | 216.9132
1850.176 | 515.143 | 220.9488 | 221.9947 | 216.7964
1851.176 | 514.1976 | 221.0423 | 221.823 | 216.712
1852.176 | 532.4486 | 221.0556 | 221.6794 | 216.5767
1853.176 | 524.5765 | 221.1897 | 221.919 | 216.7856
1854.176 | 520.2734 | 221.2324 | 222.1705 | 217.027
1855.176 | 516.7531 | 221.1695 | 222.4495 | 216.9989
1856.176 | 506.855 | 220.9853 | 222.5499 | 217.0087
1857.176 | 499.7182 | 221.2368 | 222.6299 | 216.9763
1858.176 | 493.318 | 221.2891 | 222.72 | 217.1467
1859.176 | 483.5838 | 221.2051 | 222.7108 | 217.3268
1860.176 | 478.7424 | 220.7534 | 222.8574 | 217.2934
1861.176 | 472.8085 | 220.5375 | 222.8963 | 217.3765
1862.176 | 463.7782 | 220.7011 | 222.8573 | 217.5
1863.176 | 455.4037 | 220.9147 | 223.1502 | 217.845
1864.176 | 453.0154 | 220.5982 | 223.3788 | 217.6556
1865.176 | 451.8895 | 220.3634 | 223.4405 | 217.6419
1866.176 | 451.8806 | 220.457 | 223.4545 | 217.7992
1867.176 | 450.8642 | 220.346 | 223.4454 | 217.4924
1868.176 | 444.7807 | 220.5335 | 223.4935 | 217.4872
1869.176 | 438.9631 | 220.7036 | 223.4633 | 217.7274
1870.176 | 439.5339 | 220.7836 | 223.5074 | 217.6555
1871.176 | 441.204 | 220.8537 | 223.6665 | 217.6195
1872.176 | 433.2488 | 220.9936 | 223.7451 | 217.4864
1873.176 | 426.0514 | 221.3528 | 223.6491 | 217.3419
1874.176 | 424.7058 | 221.6951 | 223.6539 | 217.2949
1875.176 | 427.5772 | 221.5995 | 223.5055 | 217.2662
1876.176 | 448.5985 | 221.8892 | 223.3905 | 217.5027
1877.176 | 458.854 | 222.1357 | 223.0906 | 217.2218
1878.176 | 462.4164 | 222.4246 | 222.9568 | 216.9443
1879.176 | 466.2121 | 222.4796 | 222.8982 | 216.6017
1880.176 | 471.1216 | 222.4503 | 222.7855 | 216.3589
1881.176 | 475.1649 | 222.758 | 222.6592 | 216.5289
1882.176 | 482.7267 | 223.2019 | 222.4621 | 217.0113
1883.176 | 485.3348 | 223.342 | 222.4261 | 216.9988
1884.176 | 490.1569 | 223.2326 | 222.522 | 217.3851
1885.176 | 507.7999 | 223.1157 | 222.3529 | 217.2021
1886.176 | 511.3302 | 223.5822 | 222.3345 | 217.2403
1887.176 | 522.41 | 223.9883 | 222.3406 | 216.8163
1888.176 | 527.2266 | 224.2255 | 222.2323 | 216.6568
1889.176 | 535.2865 | 224.4289 | 222.1511 | 217.0197
1890.176 | 531.2561 | 224.1217 | 222.1808 | 217.1865
1891.176 | 529.8692 | 223.8935 | 221.965 | 217.1983
1892.176 | 530.6803 | 224.1241 | 221.7784 | 217.3965
1893.176 | 531.4143 | 224.0364 | 221.6236 | 217.4751
1894.176 | 534.5632 | 224.1351 | 221.5801 | 217.4016
1895.176 | 541.0905 | 224.1029 | 221.5182 | 217.5144
1896.176 | 547.031 | 224.3392 | 221.3767 | 217.6808
1897.176 | 548.7746 | 224.3492 | 221.3021 | 217.6186
1898.176 | 552.3864 | 224.6691 | 221.3487 | 217.7893
1899.176 | 550.7086 | 224.7469 | 221.2852 | 217.9929
1900.176 | 553.8749 | 224.5674 | 221.234 | 217.7716
1901.176 | 556.1824 | 224.4731 | 221.173 | 218.5716
1902.176 | 567.9744 | 224.453 | 221.0542 | 218.3883
1903.176 | 572.1969 | 224.5102 | 221.1976 | 218.2907
1904.176 | 568.7124 | 224.8713 | 221.2198 | 218.5971
1905.176 | 573.2797 | 225.0962 | 221.4748 | 218.264
1906.176 | 574.8195 | 224.8308 | 221.8643 | 218.3138
1907.176 | 567.9365 | 224.423 | 221.9138 | 218.065
1908.176 | 574.6837 | 224.1486 | 221.9751 | 217.8581
1909.176 | 582.2827 | 223.8933 | 221.8864 | 217.6609
1910.176 | 579.389 | 223.9593 | 221.716 | 217.6712
1911.176 | 587.8485 | 223.6494 | 221.6549 | 217.5074
1912.176 | 584.5604 | 223.4691 | 221.5539 | 217.502
1913.176 | 583.495 | 223.3059 | 221.3885 | 217.4807
1914.176 | 577.0908 | 223.5084 | 221.2695 | 217.5503
1915.176 | 585.158 | 223.5876 | 221.178 | 217.614
1916.176 | 588.6963 | 223.8806 | 221.2144 | 217.7451
1917.176 | 592.4273 | 224.1953 | 221.3989 | 217.9121
1918.176 | 600.3871 | 224.3954 | 221.558 | 217.8897
1919.176 | 602.126 | 224.3655 | 221.7611 | 217.9867
1920.176 | 605.1041 | 224.3396 | 221.988 | 218.09
1921.176 | 622.602 | 224.4173 | 222.1034 | 218.2909
1922.1917 | 633.7462 | 224.1317 | 222.1432 | 218.3703
1923.176 | 631.0565 | 224.2809 | 222.2474 | 218.4351
1924.176 | 637.1443 | 224.0111 | 222.2418 | 218.4197
1925.176 | 643.7632 | 224.1495 | 222.1766 | 218.6907
1926.176 | 645.0746 | 223.6247 | 222.0442 | 218.6701
1927.176 | 652.8183 | 223.4031 | 221.936 | 218.7292
1928.176 | 658.8727 | 223.5697 | 221.8336 | 218.6599
1929.176 | 667.8165 | 223.589 | 221.8877 | 218.7388
1930.176 | 658.7386 | 223.5782 | 222.0235 | 218.8362
1931.176 | 661.5066 | 223.4887 | 222.0257 | 218.6288
1932.176 | 663.1898 | 223.1509 | 221.9077 | 218.6113
1933.176 | 657.9561 | 223.0028 | 221.8099 | 218.3956
1934.176 | 650.8949 | 222.8773 | 221.7811 | 218.4185
1935.176 | 650.2717 | 222.6883 | 221.6536 | 218.2975
1936.176 | 646.7157 | 222.7667 | 221.5426 | 218.3044
1937.176 | 653.7755 | 222.7589 | 221.7295 | 218.3998
1938.176 | 657.7328 | 222.9429 | 221.8087 | 218.5302
1939.176 | 659.8416 | 223.1287 | 221.7013 | 218.4364
1940.176 | 659.3758 | 223.4822 | 221.5304 | 218.3624
1941.176 | 643.2755 | 223.707 | 221.3103 | 218.1672
1942.176 | 638.4249 | 223.733 | 221.2815 | 218.0776
1943.176 | 642.6288 | 223.8088 | 221.1784 | 218.3262
1944.176 | 634.074 | 223.7537 | 221.0615 | 218.5287
1945.176 | 640.0621 | 223.7701 | 220.9524 | 218.7725
1946.176 | 640.1764 | 223.9073 | 221.0405 | 218.6989
1947.176 | 641.6021 | 224.0001 | 221.1851 | 218.673
1948.176 | 640.5696 | 223.9354 | 221.2298 | 218.7076
1949.176 | 648.3788 | 223.9571 | 221.2181 | 218.7519
1950.176 | 652.6963 | 223.8855 | 221.1771 | 219.2244
1951.176 | 663.5142 | 223.8363 | 221.171 | 218.8208
1952.176 | 667.957 | 223.8524 | 221.2002 | 218.5912
1953.176 | 651.67 | 223.6023 | 221.2575 | 219.0558
1954.176 | 647.5011 | 223.6934 | 221.3156 | 219.6446
1955.176 | 641.3882 | 223.677 | 221.3661 | 219.4928
1956.176 | 640.8453 | 223.9441 | 221.3987 | 219.4047
1957.176 | 645.5181 | 224.013 | 221.3943 | 219.5325
1958.176 | 643.1618 | 224.5883 | 221.4012 | 219.5292
1959.176 | 651.7273 | 224.9193 | 221.3914 | 219.3356
1960.176 | 652.1724 | 225.4153 | 221.4744 | 219.1631
1961.176 | 652.8172 | 225.4586 | 221.5922 | 219.1615
1962.176 | 662.7534 | 225.4159 | 221.59 | 219.4055
1963.176 | 661.9264 | 225.1093 | 221.6496 | 219.6993
1964.176 | 663.0024 | 225.2841 | 221.8081 | 220.1007
1965.176 | 659.0671 | 225.8174 | 221.9026 | 219.8813
1966.176 | 660.7134 | 225.9901 | 221.8622 | 219.9975
1967.176 | 655.3218 | 225.8215 | 221.9485 | 220.0478
1968.176 | 665.933 | 225.6984 | 222.0891 | 220.2567
1969.176 | 666.762 | 225.6474 | 221.9961 | 220.3741
1970.176 | 669.4154 | 225.6908 | 221.9272 | 220.158
1971.176 | 663.0493 | 225.6172 | 221.958 | 220.2963
1972.176 | 662.5473 | 225.5427 | 221.8882 | 220.203
1973.176 | 657.9086 | 225.4261 | 221.7776 | 219.9351
1974.176 | 654.7797 | 225.4147 | 221.844 | 220.0389
1975.176 | 650.4172 | 225.4734 | 221.9321 | 220.0212
1976.176 | 651.7546 | 225.7059 | 221.8882 | 219.9839
1977.176 | 651.5915 | 225.8014 | 221.8001 | 219.8179
1978.176 | 645.3307 | 225.7011 | 221.7397 | 219.5518
1979.176 | 649.3292 | 225.9212 | 221.7131 | 219.5
1980.176 | 653.6937 | 226.1517 | 221.8597 | 219.5096
1981.176 | 654.0374 | 226.1239 | 221.9815 | 219.4571
1982.176 | 655.6377 | 226.1097 | 221.8565 | 219.3058
1983.176 | 647.9637 | 226.0258 | 221.8842 | 219.1937
1984.176 | 640.3921 | 225.9039 | 221.842 | 219.0344
1985.176 | 638.0044 | 225.7344 | 221.838 | 218.7493
1986.176 | 642.2115 | 225.4361 | 222.1314 | 218.44
1987.176 | 640.5999 | 225.5106 | 222.0806 | 218.1722
1988.176 | 645.08 | 225.1894 | 222.0293 | 217.8687
1989.176 | 644.4538 | 225.0813 | 222.0387 | 217.7615
1990.176 | 644.8657 | 224.4528 | 221.9308 | 217.4973
1991.176 | 639.7878 | 224.1139 | 221.7384 | 217.4466
1992.176 | 626.6783 | 223.7814 | 221.7582 | 217.3536
1993.176 | 622.3661 | 223.6875 | 221.6337 | 217.2013
1994.176 | 616.4523 | 223.3719 | 221.4274 | 217.3634
1995.176 | 614.9892 | 223.0402 | 221.253 | 217.1985
1996.176 | 622.4894 | 223.0382 | 221.167 | 217.3905
1997.176 | 633.8452 | 223.3707 | 221.1993 | 217.8665
1998.176 | 641.9582 | 222.9956 | 221.2587 | 218.0079
1999.176 | 640.2833 | 223.094 | 221.839 | 218.3739
2000.176 | 632.8622 | 222.9376 | 221.972 | 218.2713
2001.176 | 633.4379 | 222.946 | 222.0386 | 219.1372
2002.176 | 624.1352 | 223.0844 | 222.2704 | 219.4866
2003.176 | 631.8113 | 223.192 | 222.9192 | 219.3691
2004.176 | 626.3034 | 223.2122 | 222.8616 | 219.4771
2005.176 | 616.4551 | 223.2172 | 222.9338 | 219.505
2006.176 | 624.2892 | 223.2748 | 222.9137 | 219.5264
2007.176 | 632.401 | 223.1961 | 223.0496 | 219.5901
2008.176 | 635.8473 | 223.1737 | 223.1095 | 219.3315
2009.176 | 631.2989 | 223.2956 | 223.2662 | 219.3684
2010.176 | 627.5752 | 223.4802 | 223.2658 | 219.2625
2011.176 | 618.4868 | 223.447 | 223.1688 | 219.1022
2012.176 | 634.362 | 223.3425 | 223.2648 | 219.0322
2013.176 | 634.1846 | 223.3102 | 223.2047 | 218.8754
2014.176 | 645.346 | 223.2191 | 223.2018 | 218.7549
2015.176 | 642.868 | 223.0914 | 223.2422 | 218.5655
2016.176 | 640.0118 | 222.9078 | 222.9901 | 218.4203
2017.176 | 644.9495 | 222.892 | 222.8766 | 218.541
2018.176 | 650.8534 | 222.6633 | 222.7695 | 218.6987
2019.176 | 634.0726 | 222.3917 | 222.7478 | 218.8864
2020.176 | 632.6273 | 222.1318 | 222.6622 | 218.8799
2021.176 | 629.38 | 221.8674 | 222.5991 | 219.0231
2022.176 | 639.4547 | 221.8742 | 222.5414 | 219.154
2023.176 | 632.0323 | 221.5647 | 222.4043 | 219.2997
2024.176 | 640.8314 | 221.8102 | 222.3639 | 219.4653
2025.176 | 655.1677 | 222.0847 | 222.1775 | 219.3492
2026.176 | 644.2861 | 222.4527 | 221.9954 | 219.5009
2027.176 | 653.5681 | 222.7318 | 222.0147 | 219.585
2028.176 | 641.2179 | 222.7451 | 222.2034 | 219.821
2029.176 | 649.1215 | 222.6611 | 222.2377 | 220.0034
2030.176 | 655.315 | 222.8137 | 222.4178 | 220.0175
2031.176 | 657.3821 | 223.2423 | 222.4812 | 220.1451
2032.176 | 657.2493 | 223.3872 | 222.4514 | 220.1321
2033.176 | 664.6809 | 223.741 | 222.422 | 219.9374
2034.176 | 657.7642 | 223.9072 | 222.3555 | 220.0164
2035.176 | 653.6844 | 224.1725 | 222.6989 | 220.2404
2036.176 | 651.5213 | 224.3626 | 222.929 | 219.958
2037.176 | 654.3578 | 224.7184 | 222.913 | 220.0339
2038.176 | 629.9818 | 225.2575 | 222.7791 | 220.0486
2039.176 | 622.8606 | 225.1062 | 222.405 | 219.8946
2040.176 | 630.9205 | 225.3357 | 222.3621 | 219.5817
2041.176 | 620.089 | 225.3711 | 222.1531 | 219.4287
2042.176 | 617.6658 | 225.4097 | 222.1889 | 219.518
2043.176 | 622.5584 | 225.42 | 222.0904 | 219.6254
2044.176 | 618.8103 | 225.3237 | 222.2029 | 219.6355
2045.176 | 601.125 | 225.3174 | 222.1964 | 219.7166
2046.176 | 594.6102 | 225.2836 | 222.0782 | 219.7247
2047.176 | 586.9943 | 225.3013 | 222.0281 | 219.4552
2048.176 | 588.6394 | 225.369 | 222.0005 | 219.3823
2049.176 | 586.8538 | 225.3676 | 221.868 | 219.7403
2050.176 | 585.3655 | 225.3978 | 221.8384 | 219.92
2051.176 | 602.7795 | 225.4898 | 221.7203 | 219.9872
2052.176 | 598.1165 | 225.3846 | 221.8342 | 219.8349
2053.176 | 604.7554 | 225.5218 | 221.8348 | 219.6245
2054.176 | 599.5925 | 225.77 | 221.8749 | 219.6402
2055.176 | 602.0196 | 225.6329 | 222.0131 | 220.0152
2056.176 | 589.4075 | 225.6899 | 222.1152 | 220.0747
2057.176 | 587.3743 | 225.5505 | 222.0408 | 220.3735
2058.176 | 573.1935 | 225.3737 | 222.0711 | 220.668
2059.176 | 560.1897 | 225.2955 | 222.0357 | 220.6895
2060.176 | 573.6349 | 225.0655 | 221.8569 | 220.6753
2061.176 | 560.4375 | 224.6679 | 221.8921 | 220.9178
2062.1917 | 581.1977 | 224.6797 | 221.9596 | 221.2426
2063.176 | 572.2598 | 224.6204 | 221.7562 | 221.2568
2064.176 | 567.185 | 224.5756 | 221.7075 | 221.3433
2065.176 | 570.388 | 224.8328 | 221.5182 | 221.4254
2066.176 | 582.584 | 224.9348 | 221.5226 | 221.2443
2067.176 | 589.1351 | 224.8359 | 221.255 | 221.2693
2068.176 | 593.3921 | 224.6294 | 221.0638 | 221.0432
2069.176 | 608.6974 | 224.6781 | 220.9846 | 220.7421
2070.176 | 607.9897 | 224.5022 | 220.89 | 220.6449
2071.176 | 620.1699 | 224.7506 | 220.8496 | 220.7423
2072.176 | 619.374 | 224.8877 | 220.9224 | 220.6502
2073.176 | 607.0148 | 225.1079 | 221.1678 | 220.782
2074.176 | 593.6767 | 225.0194 | 221.2674 | 221.296
2075.176 | 588.6208 | 224.9964 | 221.3808 | 221.1898
2076.176 | 576.8834 | 224.6964 | 221.3707 | 221.1988
2077.176 | 568.6179 | 224.8701 | 221.4157 | 221.4609
2078.176 | 559.3368 | 224.6289 | 221.4703 | 221.3044
2079.176 | 571.0538 | 225.2263 | 221.5695 | 221.2065
2080.176 | 569.7355 | 225.138 | 221.5145 | 221.0226
2081.176 | 589.6492 | 225.0103 | 221.8671 | 221.0159
2082.176 | 593.4646 | 225.0508 | 221.8439 | 220.7955
2083.176 | 583.7749 | 225.1785 | 221.7201 | 220.5661
2084.176 | 565.9208 | 225.0843 | 221.6735 | 220.7648
2085.176 | 568.3688 | 225.2567 | 221.6901 | 221.2291
2086.176 | 584.2755 | 225.2409 | 221.7539 | 221.2299
2087.176 | 573.361 | 225.2781 | 221.9249 | 220.9571
2088.176 | 559.5812 | 225.2066 | 221.8668 | 220.6315
2089.176 | 548.5026 | 225.1867 | 221.7981 | 220.4664
2090.176 | 550.3305 | 225.2415 | 222.0635 | 220.1349
2091.176 | 549.6712 | 225.2631 | 222.2759 | 220.0143
2092.176 | 546.6028 | 225.198 | 222.4654 | 219.7993
2093.176 | 536.6645 | 224.7973 | 222.4491 | 219.4377
2094.176 | 526.3849 | 224.6268 | 222.554 | 219.3566
2095.176 | 516.9676 | 224.5305 | 222.6728 | 219.2054
2096.176 | 511.3096 | 224.6298 | 222.7914 | 219.4348
2097.176 | 518.0121 | 224.6682 | 223.0738 | 219.4486
2098.176 | 513.556 | 224.6839 | 223.4372 | 219.6958
2099.176 | 526.6623 | 224.7051 | 223.524 | 219.8063
2100.176 | 534.784 | 224.7578 | 223.612 | 219.7174
2101.176 | 534.0867 | 224.8926 | 223.9867 | 220.034
2102.176 | 539.8831 | 225.0357 | 224.3253 | 220.1259
2103.176 | 539.6498 | 225.3235 | 225.022 | 220.6293
2104.176 | 529.3771 | 225.2588 | 225.1527 | 220.796
2105.176 | 529.8293 | 225.166 | 225.2594 | 220.8742
2106.176 | 533.4209 | 225.1353 | 225.3116 | 221.0079
2107.176 | 541.9018 | 225.0348 | 225.2167 | 221.1577
2108.176 | 532.7396 | 225.1799 | 225.1297 | 221.9236
2109.176 | 523.2906 | 225.1866 | 225.0634 | 221.8386
2110.176 | 533.1807 | 225.3372 | 224.9774 | 221.9258
2111.176 | 538.78 | 225.4167 | 224.8223 | 221.476
2112.176 | 535.9502 | 225.4541 | 224.7255 | 221.1376
2113.176 | 533.8514 | 225.7287 | 224.4944 | 221.3354
2114.176 | 523.9929 | 225.4728 | 224.4076 | 221.5637
2115.176 | 523.4239 | 225.6247 | 224.417 | 221.5036
2116.176 | 535.9051 | 225.5773 | 224.4174 | 221.43
2117.176 | 541.717 | 225.6352 | 224.3858 | 221.1798
2118.176 | 554.7914 | 225.2919 | 224.5159 | 220.8938
2119.176 | 564.0506 | 225.3058 | 224.4775 | 220.7874
2120.176 | 564.7117 | 225.3081 | 224.3857 | 220.9015
2121.176 | 552.9265 | 224.949 | 224.168 | 220.8825
2122.176 | 544.8639 | 224.8116 | 223.9848 | 220.7865
2123.176 | 539.0742 | 224.7175 | 223.8421 | 220.5905
2124.176 | 540.7185 | 224.6951 | 223.8664 | 220.2007
2125.176 | 549.723 | 224.7421 | 223.5963 | 219.8763
2126.176 | 543.4776 | 224.9024 | 223.4171 | 219.5867
2127.176 | 535.376 | 225.1993 | 223.3487 | 219.6425
2128.176 | 527.4392 | 225.0792 | 223.3802 | 219.7785
2129.176 | 523.5499 | 224.9079 | 223.4319 | 219.8464
2130.176 | 532.8154 | 224.7792 | 223.5486 | 219.8682
2131.176 | 536.6539 | 224.5352 | 223.7491 | 219.7378
2132.176 | 531.1091 | 224.4776 | 224.0758 | 219.5726
2133.176 | 535.6659 | 224.4583 | 224.1764 | 219.4161
2134.176 | 535.2021 | 224.3155 | 224.3674 | 219.2298
2135.176 | 528.3004 | 224.272 | 224.4814 | 218.9578
2136.176 | 542.9453 | 224.3524 | 224.4733 | 218.9904
2137.176 | 526.4844 | 224.3699 | 224.4486 | 218.9592
2138.176 | 533.6016 | 224.7697 | 224.4153 | 219.1184
2139.176 | 540.4848 | 225.1155 | 224.4272 | 219.0791
2140.176 | 548.9484 | 224.938 | 224.5304 | 219.5583
2141.176 | 539.9666 | 225.4053 | 224.8599 | 219.7484
2142.176 | 541.4442 | 225.4299 | 224.9548 | 219.5575
2143.176 | 534.4417 | 225.775 | 225.0186 | 219.6893
2144.176 | 544.2872 | 225.7332 | 225.3479 | 219.5496
2145.176 | 566.0351 | 225.8175 | 225.0414 | 219.6066
2146.176 | 548.6005 | 225.9267 | 224.806 | 219.8316
2147.176 | 540.6795 | 226.0026 | 224.5174 | 219.9298
2148.176 | 538.0061 | 225.8431 | 224.3836 | 220.018
2149.176 | 521.3047 | 225.7207 | 224.4368 | 220.0349
2150.176 | 517.4641 | 225.6476 | 224.2892 | 219.9265
2151.176 | 532.2794 | 225.6011 | 224.1211 | 220.0657
2152.176 | 527.5404 | 225.4934 | 223.8821 | 220.1694
2153.176 | 519.1631 | 225.5288 | 223.6962 | 220.0127
2154.176 | 526.5262 | 225.4196 | 223.563 | 219.7969
2155.176 | 526.5153 | 225.3559 | 223.3995 | 219.692
2156.176 | 518.9956 | 225.2408 | 223.3966 | 219.7909
2157.176 | 525.7831 | 225.1638 | 223.1963 | 219.7561
2158.176 | 530.0681 | 224.9428 | 223.0705 | 219.555
2159.176 | 520.6666 | 224.7195 | 223.0784 | 219.4535
2160.176 | 538.8595 | 224.4838 | 222.9338 | 219.4259
2161.176 | 549.2605 | 224.3791 | 222.7001 | 219.4365
2162.176 | 534.8997 | 224.1117 | 222.5854 | 219.7814
2163.176 | 538.9707 | 223.9149 | 222.5113 | 219.8112
2164.176 | 558.7117 | 223.9313 | 222.6662 | 219.9121
2165.176 | 554.4616 | 223.9146 | 222.709 | 220.0167
2166.176 | 550.4152 | 224.219 | 222.8998 | 220.4778
2167.176 | 577.4243 | 224.0852 | 223.2435 | 221.0438
2168.176 | 570.0197 | 224.5359 | 223.4714 | 221.3822
2169.176 | 573.4067 | 223.8532 | 223.5259 | 221.29
2170.176 | 574.1751 | 223.8108 | 223.5589 | 221.3106
2171.176 | 557.2593 | 223.8107 | 223.6221 | 221.3957
2172.176 | 571.2026 | 223.4738 | 223.6608 | 221.1244
2173.176 | 553.0591 | 223.2228 | 223.9158 | 220.7467
2174.176 | 561.7529 | 223.2252 | 223.8322 | 220.5359
2175.176 | 563.2883 | 223.3561 | 223.7467 | 220.5315
2176.176 | 559.5061 | 223.612 | 223.9211 | 220.5225
2177.176 | 581.8436 | 223.6452 | 223.9473 | 220.4239
2178.176 | 565.6711 | 223.8691 | 224.4704 | 220.6083
2179.176 | 559.7564 | 223.6714 | 224.3427 | 220.8878
2180.176 | 545.2756 | 223.6831 | 224.3792 | 221.2333
2181.176 | 544.9534 | 223.5359 | 224.4432 | 221.6959
2182.176 | 531.4271 | 223.8543 | 224.4126 | 221.994
2183.176 | 522.547 | 223.6548 | 224.388 | 222.0483
2184.176 | 520.0506 | 223.4428 | 224.4598 | 221.9194
2185.176 | 504.6205 | 223.1162 | 224.0341 | 221.6917
2186.176 | 498.37 | 223.1687 | 223.8891 | 221.5871
2187.176 | 490.5714 | 223.1039 | 223.7517 | 221.283
2188.176 | 486.8571 | 223.1074 | 223.7262 | 221.0378
2189.176 | 481.7914 | 222.7311 | 223.5688 | 220.8972
2190.176 | 474.9101 | 222.4873 | 223.6348 | 220.9757
2191.176 | 469.0452 | 222.4843 | 223.9507 | 221.1081
2192.176 | 459.813 | 222.4866 | 224.0463 | 221.2987
2193.176 | 456.2689 | 222.5218 | 223.9697 | 221.6239
2194.176 | 449.9058 | 222.2743 | 223.7849 | 221.2389
2195.176 | 454.3959 | 222.0438 | 223.6742 | 220.9389
2196.176 | 465.0764 | 222.0855 | 223.3476 | 220.8991
2197.176 | 460.3845 | 222.2816 | 223.0983 | 220.7907
2198.176 | 475.1671 | 222.2554 | 222.9851 | 220.5663
2199.176 | 469.5245 | 222.2199 | 222.9314 | 220.4864
2200.176 | 465.6917 | 222.2893 | 223.0619 | 220.4574
2201.176 | 468.2661 | 222.5066 | 222.9892 | 220.593
2202.176 | 464.3777 | 222.565 | 222.9279 | 220.5403
2203.176 | 456.3791 | 222.5532 | 222.8865 | 220.6081
2204.176 | 467.0726 | 222.7049 | 222.8242 | 220.7761
2205.176 | 470.5542 | 222.7879 | 222.6876 | 220.9362
2206.176 | 470.2003 | 222.5915 | 222.6176 | 220.9677
2207.176 | 484.1544 | 222.4241 | 222.4768 | 220.9508
2208.176 | 487.6102 | 222.419 | 222.271 | 220.8339
2209.176 | 504.854 | 222.441 | 222.1048 | 220.957
2210.176 | 525.7865 | 222.4816 | 221.8946 | 220.894
2211.176 | 532.7659 | 222.6144 | 221.6426 | 220.7187
2212.1917 | 534.275 | 222.526 | 221.4031 | 220.4952
2213.176 | 547.8501 | 222.4667 | 221.3734 | 220.3846
2214.176 | 558.6954 | 222.5678 | 221.2165 | 220.0766
2215.176 | 579.6491 | 222.6503 | 221.0972 | 219.7358
2216.176 | 564.4766 | 222.9441 | 221.1199 | 219.6025
2217.176 | 545.4692 | 223.1937 | 221.399 | 219.5132
2218.176 | 530.7046 | 223.3913 | 221.5002 | 219.4089
2219.176 | 534.0303 | 223.3227 | 221.4754 | 219.5342
2220.176 | 534.2236 | 223.4702 | 221.3567 | 219.8946
2221.176 | 539.8962 | 223.5817 | 221.2999 | 219.8014
2222.176 | 568.6158 | 223.7463 | 221.2559 | 219.4123
2223.176 | 570.6576 | 223.9656 | 221.3729 | 219.4738
2224.176 | 559.4271 | 224.1552 | 221.1759 | 218.944
2225.176 | 569.2966 | 224.4381 | 221.082 | 218.6432
2226.176 | 569.6429 | 224.5051 | 220.9567 | 218.6944
2227.176 | 550.9778 | 224.5591 | 220.79 | 218.7756
2228.176 | 550.6557 | 224.5957 | 220.8318 | 218.6641
2229.176 | 574.9305 | 224.7234 | 220.7707 | 219.1378
2230.176 | 568.5718 | 224.4729 | 220.9373 | 219.127
2231.176 | 551.2399 | 224.3691 | 220.9046 | 219.2652
2232.176 | 555.4503 | 224.4125 | 220.8866 | 219.4335
2233.176 | 560.7459 | 224.2935 | 220.7789 | 219.2885
2234.176 | 545.4855 | 224.097 | 220.6926 | 219.2891
2235.176 | 529.241 | 224.3358 | 220.7351 | 219.2991
2236.176 | 518.9956 | 224.3993 | 220.6928 | 219.3358
2237.176 | 505.3236 | 224.2376 | 220.5668 | 219.1368
2238.176 | 500.9327 | 224.039 | 220.5658 | 218.9249
2239.176 | 495.5075 | 223.979 | 220.5107 | 218.9182
2240.176 | 524.5946 | 223.9326 | 220.3691 | 218.8005
2241.176 | 514.2308 | 223.6354 | 220.2789 | 218.4716
2242.176 | 503.8893 | 223.4559 | 220.1771 | 218.3677
2243.176 | 520.0868 | 223.418 | 220.3847 | 218.5067
2244.176 | 517.6971 | 223.5922 | 220.781 | 218.9376
2245.176 | 525.7212 | 223.6058 | 220.7097 | 219.0341
2246.176 | 509.7909 | 223.5508 | 220.7033 | 218.9232
2247.176 | 498.6189 | 223.4388 | 220.8208 | 218.9095
2248.176 | 490.3652 | 223.5723 | 220.9278 | 218.8372
2249.176 | 482.9729 | 223.8863 | 220.909 | 219.1715
2250.176 | 475.9612 | 223.8338 | 220.9125 | 219.4061
2251.176 | 497.2456 | 223.9315 | 221.0106 | 219.7789
2252.176 | 495.2184 | 223.8597 | 221.2027 | 219.974
2253.176 | 514.0196 | 223.9781 | 221.4391 | 220.0691
2254.176 | 504.0012 | 223.9126 | 221.4084 | 220.0164
2255.176 | 517.6467 | 223.7423 | 221.1926 | 219.8946
2256.176 | 530.9802 | 223.844 | 220.9126 | 219.6764
2257.176 | 538.5554 | 224.1238 | 220.8292 | 219.4842
2258.176 | 533.6545 | 224.0392 | 220.6475 | 219.2957
2259.176 | 526.1703 | 224.0188 | 220.6141 | 219.1506
2260.176 | 513.6889 | 223.8441 | 220.6311 | 219.0148
2261.176 | 512.219 | 223.7283 | 220.5235 | 218.9655
2262.176 | 505.5056 | 223.6506 | 220.3995 | 218.9503
2263.176 | 524.9477 | 223.7319 | 220.3751 | 218.8473
2264.176 | 532.9072 | 223.6019 | 220.3548 | 218.6971
2265.176 | 524.5323 | 223.4918 | 220.2125 | 218.4269
2266.176 | 534.6624 | 223.425 | 220.3788 | 218.3182
2267.176 | 537.4921 | 223.7009 | 220.2712 | 218.7688
2268.176 | 535.2937 | 223.8717 | 220.2346 | 219.0075
2269.176 | 533.4887 | 223.8537 | 220.297 | 219.0246
2270.176 | 537.5927 | 224.047 | 220.7813 | 219.2976
2271.176 | 529.0245 | 224.125 | 220.8542 | 219.0586
2272.1917 | 511.5845 | 224.0379 | 220.9195 | 219.1149
2273.176 | 501.2755 | 223.8596 | 221.0129 | 218.9648
2274.176 | 489.7253 | 223.6976 | 221.0969 | 218.8936
2275.176 | 479.3201 | 223.4523 | 220.9228 | 218.7492
2276.176 | 466.715 | 223.0565 | 220.7338 | 218.7334
2277.176 | 457.0854 | 222.7551 | 220.5569 | 218.6214
2278.176 | 451.0521 | 222.5584 | 220.3123 | 218.359
2279.176 | 445.0056 | 222.4446 | 220.1295 | 218.3577
2280.176 | 444.4942 | 222.3123 | 220.0331 | 218.1327
2281.176 | 456.1846 | 222.2113 | 219.8687 | 217.8371
2282.176 | 465.6165 | 222.1782 | 219.9392 | 217.7625
2283.176 | 484.957 | 222.3574 | 219.9041 | 217.8438
2284.176 | 488.1872 | 222.521 | 220.0695 | 217.7093
2285.176 | 482.9372 | 222.7935 | 220.3766 | 217.6372
2286.176 | 482.2606 | 222.6822 | 220.8148 | 217.5038
2287.176 | 491.777 | 222.8106 | 220.7339 | 217.3586
2288.176 | 487.3949 | 222.6565 | 220.615 | 217.0215
2289.176 | 476.7733 | 222.5408 | 220.5209 | 216.7707
2290.176 | 483.0715 | 222.4733 | 220.3907 | 216.6078
2291.176 | 470.5921 | 222.3339 | 220.4333 | 216.3722
2292.176 | 479.4225 | 222.5143 | 220.4799 | 216.2083
2293.176 | 480.5577 | 222.3306 | 220.4109 | 215.8773
2294.176 | 482.8913 | 222.2028 | 220.2915 | 215.9856
2295.176 | 490.1743 | 222.2276 | 220.3016 | 215.8841
2296.176 | 498.0022 | 222.1754 | 220.2772 | 215.9287
2297.176 | 494.7511 | 222.3265 | 220.2808 | 215.9438
2298.176 | 504.4123 | 222.2276 | 220.3004 | 215.885
2299.176 | 504.5778 | 222.2824 | 220.226 | 215.8948
2300.176 | 519.2671 | 222.3187 | 220.4288 | 216.1412
2301.176 | 549.5577 | 222.3417 | 220.5019 | 216.1622
2302.176 | 545.0543 | 222.6426 | 220.4915 | 216.3454
2303.176 | 542.4412 | 222.935 | 220.4328 | 216.6262
2304.176 | 538.3912 | 223.1541 | 220.2768 | 216.813
2305.176 | 541.3068 | 223.2823 | 220.1181 | 217.0475
2306.176 | 529.8122 | 223.2141 | 219.9917 | 217.4901
2307.176 | 513.6181 | 223.3757 | 220.0118 | 217.4855
2308.176 | 498.8276 | 223.3927 | 220.2267 | 217.6289
2309.176 | 488.606 | 223.2979 | 220.3436 | 217.8724
2310.176 | 491.1409 | 223.6895 | 220.5795 | 217.905
2311.176 | 479.3564 | 223.5998 | 220.5128 | 218.1954
2312.176 | 469.9489 | 223.6051 | 220.5383 | 218.0762
2313.176 | 464.0571 | 223.6937 | 220.5619 | 218.1436
2314.176 | 460.7889 | 223.7183 | 220.4866 | 218.0284
2315.176 | 465.5437 | 223.7834 | 220.4053 | 217.9355
2316.176 | 466.216 | 223.6468 | 220.3563 | 217.7658
2317.176 | 484.1946 | 223.4789 | 220.2892 | 217.6132
2318.176 | 506.1645 | 223.6642 | 220.3218 | 217.6971
2319.176 | 503.0602 | 223.7337 | 220.2871 | 217.9291
2320.176 | 508.3248 | 224.0337 | 220.4815 | 217.8726
2321.176 | 508.7675 | 224.1592 | 220.4825 | 217.8886
2322.176 | 510.2259 | 223.8637 | 220.3203 | 218.1236
2323.176 | 529.7007 | 223.5943 | 220.3732 | 218.3917
2324.176 | 527.3819 | 223.512 | 220.3248 | 218.2408
2325.176 | 532.8699 | 223.2283 | 220.2571 | 218.2607
2326.176 | 538.9841 | 223.0965 | 220.2153 | 218.4118
2327.176 | 532.7495 | 223.23 | 220.1421 | 218.4629
2328.176 | 530.4579 | 223.4003 | 220.1515 | 218.4787
2329.176 | 530.6333 | 223.3921 | 220.1768 | 218.3995
2330.176 | 538.4529 | 223.287 | 220.2611 | 218.4174
2331.176 | 550.2543 | 223.4806 | 220.1399 | 218.4599
2332.176 | 553.0898 | 223.5693 | 220.0611 | 218.4201
2333.176 | 545.9876 | 223.4145 | 219.9842 | 218.0994
2334.176 | 534.6844 | 223.1619 | 220.0261 | 218.1646
2335.176 | 523.6384 | 222.9924 | 220.1168 | 218.0538
2336.176 | 519.4612 | 222.9372 | 220.0632 | 217.8463
2337.176 | 531.7035 | 222.982 | 220.0991 | 217.8509
2338.176 | 548.4359 | 222.8694 | 219.9349 | 218.0765
2339.176 | 542.416 | 222.7317 | 219.8918 | 218.3085
2340.176 | 553.6503 | 222.4358 | 219.7442 | 218.3959
2341.176 | 540.0257 | 222.1072 | 219.6069 | 218.3267
2342.176 | 547.1829 | 221.7958 | 219.4693 | 218.3293
2343.176 | 537.9452 | 221.695 | 219.4081 | 218.2511
2344.176 | 541.6511 | 221.5053 | 219.4244 | 218.0901
2345.176 | 539.0582 | 221.4602 | 219.3128 | 217.8248
2346.1917 | 537.169 | 221.5161 | 219.187 | 217.6128
2347.1917 | 543.4873 | 221.5315 | 219.0151 | 217.4297
2348.176 | 539.9276 | 221.3929 | 218.9443 | 217.7113
2349.176 | 525.2452 | 221.5103 | 219.0423 | 217.6669
2350.176 | 514.4628 | 221.7262 | 219.297 | 217.5601
2351.176 | 519.2544 | 221.9514 | 219.4252 | 217.565
2352.176 | 535.8307 | 222.195 | 219.5385 | 217.6461
2353.176 | 523.6486 | 222.292 | 219.5731 | 217.7528
2354.176 | 521.8864 | 222.2695 | 219.706 | 217.539
2355.176 | 514.2277 | 222.254 | 219.673 | 217.6304
2356.176 | 513.5936 | 222.0721 | 219.5733 | 217.8047
2357.176 | 523.0062 | 222.0638 | 219.4796 | 218.0558
2358.176 | 517.5636 | 221.8874 | 219.5327 | 218.0482
2359.176 | 522.9658 | 221.8849 | 219.5181 | 218.2275
2360.176 | 512.0763 | 221.6896 | 219.4678 | 218.2086
2361.176 | 503.6534 | 221.7664 | 219.3859 | 218.3551
2362.176 | 512.5149 | 221.7762 | 219.2588 | 218.4169
2363.176 | 526.7446 | 221.7652 | 219.3824 | 218.4615
2364.176 | 519.4922 | 221.7362 | 219.3947 | 218.4774
2365.176 | 533.0007 | 221.5832 | 219.4369 | 218.2954
2366.176 | 521.6562 | 221.4318 | 219.5713 | 218.5819
2367.176 | 512.6991 | 221.3013 | 219.6251 | 218.5097
2368.176 | 502.9602 | 221.4351 | 219.7248 | 218.7151
2369.176 | 498.4876 | 221.3143 | 219.6658 | 218.6568
2370.176 | 494.1241 | 221.2894 | 219.662 | 218.7758
2371.176 | 487.8838 | 221.5006 | 219.6183 | 218.7132
2372.176 | 495.2124 | 221.68 | 219.6778 | 218.5612
2373.176 | 491.8752 | 221.7865 | 219.6906 | 218.4066
2374.176 | 495.8199 | 221.7216 | 219.7457 | 218.277
2375.176 | 492.8794 | 221.5358 | 219.7793 | 218.1218
2376.176 | 490.7061 | 221.186 | 219.8313 | 218.0656
2377.176 | 490.4511 | 221.3101 | 220.0399 | 218.3228
2378.176 | 491.3729 | 221.4407 | 220.1905 | 218.1479
2379.176 | 508.1009 | 221.7085 | 220.2198 | 218.0196
2380.176 | 506.3738 | 221.6122 | 220.3208 | 218.1421
2381.176 | 513.4888 | 221.178 | 220.4047 | 218.1511
2382.176 | 513.6025 | 221.203 | 220.4407 | 218.263
2383.176 | 529.4827 | 221.3569 | 220.5203 | 218.5076
2384.176 | 528.3019 | 221.1469 | 220.627 | 218.4026
2385.176 | 537.9595 | 221.0568 | 220.7326 | 218.5681
2386.176 | 550.1919 | 220.8947 | 220.7081 | 218.5607
2387.176 | 553.6846 | 220.2692 | 220.6355 | 218.4291
2388.176 | 544.9673 | 220.4248 | 220.5885 | 218.6181
2389.176 | 550.0794 | 220.353 | 220.5665 | 218.3893
2390.176 | 551.9181 | 220.329 | 220.6806 | 218.2619
2391.176 | 550.9243 | 220.5102 | 220.78 | 218.1076
2392.176 | 533.5602 | 220.2781 | 220.7321 | 218.2079
2393.176 | 534.8623 | 220.357 | 220.7297 | 218.749
2394.176 | 548.385 | 220.4847 | 220.6838 | 218.9131
2395.176 | 543.5945 | 220.5493 | 220.7213 | 218.8987
2396.176 | 548.7556 | 220.8055 | 220.7818 | 219.1188
2397.176 | 545.1718 | 221.1018 | 220.7365 | 219.2691
2398.176 | 548.0188 | 221.0143 | 220.8167 | 219.6298
2399.176 | 546.6967 | 221.15 | 220.8858 | 219.5545
2400.176 | 534.5494 | 221.3111 | 220.8441 | 219.5332
2401.176 | 536.1467 | 221.578 | 220.9887 | 219.7693
2402.176 | 558.0973 | 221.6419 | 220.8483 | 219.9182
2403.176 | 554.179 | 221.7135 | 220.9077 | 220.0429
2404.176 | 544.9684 | 221.4447 | 220.7088 | 220.1882
2405.176 | 551.343 | 221.3755 | 220.6445 | 220.3796
2406.176 | 565.9748 | 221.482 | 220.4927 | 220.0629
2407.176 | 558.2195 | 221.504 | 220.3098 | 219.7014
2408.176 | 563.9913 | 221.3222 | 220.1265 | 219.4684
2409.176 | 569.7852 | 220.8719 | 219.9318 | 219.2459
2410.176 | 568.968 | 220.7822 | 219.7284 | 219.1088
2411.176 | 576.3206 | 220.6569 | 219.5207 | 218.928
2412.176 | 569.916 | 220.6292 | 219.2775 | 218.9191
2413.176 | 571.3693 | 220.6757 | 219.1252 | 219.016
2414.176 | 563.2398 | 220.83 | 219.0731 | 218.956
2415.176 | 542.4394 | 220.86 | 219.0309 | 219.289
2416.176 | 568.531 | 220.9081 | 219.15 | 219.3134
2417.176 | 561.2475 | 220.881 | 219.1606 | 219.7308
2418.176 | 553.7402 | 220.8801 | 219.362 | 219.7419
2419.176 | 568.3167 | 220.8328 | 219.2961 | 219.5568
2420.176 | 562.8723 | 220.8304 | 219.2301 | 219.4994
2421.176 | 542.615 | 220.9611 | 219.1011 | 219.3375
2422.176 | 529.4222 | 221.155 | 219.0361 | 219.3281
2423.176 | 529.2328 | 221.3782 | 218.8855 | 219.1064
2424.176 | 528.6639 | 221.389 | 218.8917 | 219.091
2425.176 | 536.2725 | 221.5025 | 218.9863 | 218.9628
2426.176 | 530.878 | 221.5712 | 219.0309 | 219.268
2427.176 | 528.3336 | 221.6827 | 219.1074 | 219.4374
2428.176 | 523.6444 | 221.8701 | 219.1551 | 219.8001
2429.176 | 529.2522 | 221.8102 | 219.2039 | 219.9379
2430.176 | 527.2812 | 221.7801 | 219.3962 | 219.7613
2431.176 | 520.1812 | 221.8723 | 219.4601 | 219.6349
2432.176 | 523.7012 | 222.1865 | 219.571 | 219.5733
2433.176 | 524.1968 | 222.138 | 219.5365 | 219.5046
2434.176 | 527.3453 | 222.1904 | 219.4999 | 219.4561
2435.176 | 526.5086 | 222.2451 | 219.4265 | 219.218
2436.176 | 519.895 | 222.2715 | 219.6608 | 219.0357
2437.176 | 516.0833 | 222.3351 | 219.5757 | 219.0289
2438.176 | 507.8968 | 222.4234 | 219.6534 | 218.7144
2439.176 | 499.4551 | 222.1847 | 219.9958 | 218.4694
2440.176 | 488.4708 | 222.0332 | 219.9698 | 218.5589
2441.176 | 506.4167 | 221.991 | 219.7856 | 218.6206
2442.176 | 498.1533 | 221.7291 | 219.6339 | 218.4978
2443.176 | 509.8946 | 221.5244 | 220.0932 | 218.393
2444.176 | 509.9439 | 221.5855 | 220.1325 | 218.3447
2445.176 | 510.9072 | 221.5527 | 220.1651 | 218.4719
2446.176 | 522.051 | 221.379 | 220.0044 | 218.625
2447.176 | 525.5681 | 221.3836 | 219.8532 | 218.5743
2448.176 | 541.3415 | 221.0802 | 219.6781 | 218.5366
2449.176 | 535.3758 | 220.7436 | 219.5904 | 218.3678
2450.176 | 537.2792 | 220.5324 | 219.4493 | 218.5315
2451.176 | 546.9857 | 220.5227 | 219.3153 | 218.5575
2452.176 | 547.3897 | 220.6537 | 219.1808 | 218.5473
2453.176 | 544.1345 | 220.7207 | 218.9971 | 218.5752
2454.176 | 533.8252 | 220.7895 | 218.9557 | 218.4064
2455.176 | 527.8583 | 220.9665 | 219.19 | 218.1452
2456.176 | 522.1998 | 221.1449 | 219.2368 | 218.051
2457.176 | 518.4373 | 221.5385 | 219.2436 | 218.344
2458.176 | 523.1035 | 221.6309 | 219.3861 | 218.3249
2459.176 | 537.6351 | 221.7675 | 219.6778 | 218.3643
2460.176 | 549.7336 | 221.9973 | 219.7352 | 218.4792
2461.176 | 542.8289 | 222.3512 | 219.7456 | 218.7171
2462.176 | 543.0468 | 222.5211 | 220.1033 | 218.8251
2463.176 | 552.0592 | 222.8994 | 220.3903 | 218.7925
2464.176 | 536.7481 | 222.8079 | 220.5984 | 218.8402
2465.176 | 540.8906 | 222.8413 | 220.7715 | 219.1828
2466.176 | 534.5671 | 223.1546 | 220.6156 | 219.438
2467.176 | 532.9994 | 223.3507 | 220.5452 | 219.7975
2468.176 | 536.4611 | 223.2815 | 220.5839 | 219.965
2469.176 | 535.3433 | 223.1062 | 220.5323 | 219.8498
2470.176 | 530.8792 | 223.0364 | 220.4271 | 219.622
2471.176 | 527.8645 | 223.1627 | 220.3841 | 219.4969
2472.176 | 525.8337 | 223.0878 | 220.3376 | 219.5671
2473.176 | 541.9388 | 223.028 | 220.2846 | 219.4353
2474.176 | 545.6482 | 222.9773 | 220.129 | 219.4778
2475.176 | 544.5853 | 222.7813 | 220.0875 | 219.8845
2476.176 | 546.5048 | 222.7615 | 220.0393 | 219.8381
2477.176 | 537.1865 | 222.7796 | 219.9283 | 219.4945
2478.176 | 534.6277 | 222.7338 | 219.887 | 219.2883
2479.176 | 527.3446 | 222.5249 | 219.6774 | 219.2463
2480.176 | 532.7974 | 222.2893 | 219.4701 | 219.3655
2481.176 | 538.9662 | 222.2452 | 219.345 | 219.243
2482.176 | 544.1484 | 222.1349 | 219.2323 | 219.0996
2483.176 | 546.8873 | 222.1193 | 219.1421 | 218.817
2484.176 | 540.9746 | 222.3472 | 219.0574 | 219.1048
2485.176 | 534.7441 | 222.4318 | 219.028 | 219.1248
2486.176 | 535.2266 | 222.672 | 219.0459 | 219.1443
2487.176 | 539.087 | 222.7241 | 219.1625 | 219.3339
2488.176 | 543.0732 | 222.6562 | 219.2635 | 219.3181
2489.176 | 535.5047 | 222.6243 | 219.3084 | 219.1518
2490.176 | 546.8856 | 222.6059 | 219.3911 | 219.1756
2491.176 | 550.9648 | 222.4793 | 219.482 | 219.3323
2492.176 | 551.0567 | 222.2613 | 219.4631 | 219.4576
2493.176 | 542.8589 | 222.1302 | 219.4653 | 219.3619
2494.176 | 541.2869 | 222.1606 | 219.4049 | 219.1201
2495.176 | 546.0693 | 222.2005 | 219.3895 | 219.2004
2496.176 | 540.109 | 222.3048 | 219.323 | 219.3176
2497.176 | 544.7159 | 222.4652 | 219.2582 | 219.1568
2498.176 | 547.9287 | 222.4035 | 219.1489 | 218.985
2499.176 | 537.4046 | 222.3172 | 219.2543 | 219.0112
2500.176 | 537.2266 | 222.2149 | 219.3892 | 219.1407
2501.176 | 534.3399 | 221.9269 | 219.3712 | 218.9273
2502.176 | 544.5124 | 221.6858 | 219.557 | 218.7251
2503.176 | 530.9253 | 221.2861 | 219.7691 | 218.6495
2504.176 | 523.8664 | 221.4362 | 219.6348 | 218.5616
2505.176 | 516.952 | 221.015 | 219.4915 | 218.5483
2506.176 | 531.4955 | 220.905 | 219.4749 | 218.2786
2507.176 | 520.1927 | 220.9058 | 219.4536 | 218.4167
2508.176 | 510.6588 | 220.8716 | 219.4356 | 218.272
2509.176 | 506.9133 | 220.9699 | 219.3847 | 218.4839
2510.176 | 495.6454 | 220.9989 | 219.4485 | 218.4605
2511.176 | 487.5669 | 221.0082 | 219.4565 | 218.5577
2512.176 | 487.0423 | 221.0462 | 219.476 | 218.3414
2513.176 | 501.6656 | 221.1167 | 219.433 | 218.0609
2514.176 | 496.2668 | 221.1961 | 219.2752 | 218.0592
2515.176 | 493.2056 | 221.1927 | 219.1688 | 218.0046
2516.176 | 502.1813 | 221.0213 | 219.1943 | 218.0643
2517.176 | 500.8029 | 221.0758 | 219.2858 | 218.012
2518.176 | 502.3593 | 221.0245 | 219.3636 | 218.0634
2519.176 | 506.712 | 221.1829 | 219.4095 | 218.1103
2520.176 | 498.1644 | 221.2631 | 219.5657 | 217.8662
2521.176 | 495.6502 | 221.1434 | 219.572 | 217.988
2522.176 | 489.2768 | 221.1499 | 219.6568 | 218.2338
2523.176 | 485.366 | 221.0576 | 219.8589 | 218.2516
2524.176 | 496.8401 | 220.9538 | 219.7738 | 218.0828
2525.176 | 489.4512 | 220.7606 | 219.7384 | 218.0561
2526.176 | 493.7113 | 220.5859 | 219.6656 | 217.9835
2527.176 | 489.8198 | 220.4528 | 219.6374 | 217.9391
2528.176 | 489.6616 | 220.6016 | 219.5757 | 217.9487
2529.176 | 483.8484 | 220.5012 | 219.518 | 217.762
2530.176 | 478.0041 | 220.3955 | 219.4977 | 217.6599
2531.176 | 473.0172 | 220.4755 | 219.6122 | 217.6063
2532.176 | 472.447 | 220.1003 | 219.5959 | 217.7183
2533.176 | 478.1494 | 219.9123 | 219.6449 | 218.0464
2534.176 | 496.4042 | 220.0316 | 219.7735 | 218.0776
2535.176 | 496.7777 | 219.9949 | 219.7956 | 217.9978
2536.176 | 490.3231 | 219.8271 | 219.9299 | 217.983
2537.176 | 498.9113 | 219.864 | 220.0088 | 218.0903
2538.176 | 500.6245 | 219.8653 | 220.2865 | 218.0761
2539.176 | 498.7411 | 220.3169 | 220.6265 | 218.0641
2540.176 | 492.2413 | 220.1257 | 221.0053 | 218.2256
2541.176 | 492.9942 | 220.0456 | 221.146 | 218.1143
2542.176 | 493.4349 | 220.1944 | 221.4233 | 218.0462
2543.176 | 493.7873 | 220.1096 | 221.4476 | 217.9701
2544.176 | 501.4675 | 220.003 | 221.6506 | 217.8727
2545.176 | 501.3018 | 219.6619 | 221.7425 | 217.8288
2546.176 | 508.8185 | 219.7395 | 221.7211 | 217.7671
2547.176 | 515.0288 | 219.8117 | 221.7146 | 218.0365
2548.176 | 515.1925 | 219.7838 | 221.8832 | 218.2303
2549.176 | 507.1578 | 219.9081 | 222.0107 | 218.055
2550.176 | 508.7238 | 220.0809 | 222.0562 | 218.0423
2551.176 | 507.8531 | 220.1885 | 222.0224 | 217.9975
2552.176 | 507.9691 | 219.8146 | 222.0004 | 217.9078
2553.176 | 502.5241 | 219.5772 | 221.9012 | 218.102
2554.176 | 497.5257 | 219.2752 | 221.9323 | 218.056
2555.176 | 502.8674 | 219.4314 | 221.9036 | 218.2082
2556.176 | 505.7747 | 219.4487 | 221.8343 | 218.1666
2557.176 | 505.9549 | 219.4043 | 221.7558 | 218.1787
2558.176 | 501.256 | 219.7347 | 221.7426 | 218.0791
2559.176 | 507.6 | 220.0411 | 221.78 | 218.1476
2560.176 | 502.3309 | 220.8393 | 221.9475 | 218.3916
2561.176 | 509.1768 | 221.1106 | 222.0907 | 218.1809
2562.176 | 505.6295 | 221.1677 | 221.9939 | 218.0958
2563.176 | 508.8555 | 221.1941 | 221.9615 | 218.3769
2564.176 | 505.9602 | 221.1692 | 222.0537 | 218.3064
2565.176 | 509.0768 | 221.1158 | 222.0933 | 218.2066
2566.176 | 510.613 | 221.0694 | 222.1041 | 218.1727
2567.176 | 520.2291 | 221.2197 | 222.058 | 218.0826
2568.176 | 511.7008 | 221.2605 | 222.0708 | 218.1955
2569.176 | 520.539 | 221.1218 | 222.1268 | 218.2446
2570.176 | 517.7093 | 221.2408 | 222.1057 | 218.172
2571.176 | 504.2473 | 221.3766 | 222.158 | 218.1609
2572.176 | 491.6875 | 221.4376 | 222.2293 | 218.3034
2573.176 | 483.0413 | 221.5419 | 222.2277 | 218.5371
2574.176 | 478.3244 | 221.232 | 222.3112 | 218.9854
2575.176 | 485.3542 | 221.2722 | 222.4578 | 218.9763
2576.176 | 496.7906 | 221.2792 | 222.6347 | 219.0578
2577.176 | 493.2287 | 221.2382 | 222.7602 | 219.0576
2578.176 | 503.3451 | 220.8792 | 222.7641 | 219.1083
2579.176 | 510.3165 | 220.9393 | 222.7583 | 218.9968
2580.176 | 506.6842 | 220.8036 | 222.8192 | 218.9256
2581.176 | 512.6229 | 220.8903 | 222.866 | 218.8865
2582.176 | 527.7518 | 220.7021 | 222.7052 | 218.7271
2583.176 | 525.264 | 220.3772 | 222.652 | 218.5952
2584.176 | 528.425 | 220.5757 | 222.6111 | 218.6563
2585.176 | 528.4713 | 220.6703 | 222.5388 | 218.5143
2586.176 | 526.1879 | 220.6067 | 222.5115 | 218.4331
2587.176 | 515.8009 | 220.3553 | 222.5642 | 218.5243
2588.176 | 507.1628 | 220.3714 | 222.5392 | 218.5711
2589.176 | 506.9072 | 220.3814 | 222.4709 | 218.6216
2590.176 | 511.3376 | 220.3082 | 222.4785 | 218.7807
2591.176 | 505.4792 | 220.3944 | 222.5335 | 219.1647
2592.176 | 501.2197 | 220.5694 | 222.551 | 219.222
2593.176 | 504.7299 | 220.5669 | 222.5511 | 219.6164
2594.176 | 498.2803 | 220.7146 | 222.5602 | 219.5848
2595.176 | 501.3446 | 220.8837 | 222.6224 | 219.7122
2596.176 | 501.9498 | 221.0677 | 222.6635 | 219.3843
2597.176 | 506.5714 | 221.302 | 222.6917 | 219.188
2598.176 | 508.8495 | 221.5666 | 222.7497 | 219.1737
2599.176 | 509.7914 | 221.6262 | 222.8022 | 219.4038
2600.176 | 508.7068 | 221.3626 | 222.724 | 219.6982
2601.176 | 507.9567 | 221.3171 | 222.5717 | 219.5015
2602.176 | 511.9294 | 221.0566 | 222.4189 | 219.405
2603.176 | 504.1165 | 220.9381 | 222.368 | 219.1212
2604.176 | 508.3265 | 220.6379 | 222.297 | 218.9779
2605.176 | 502.3452 | 220.6586 | 222.3049 | 218.6688
2606.176 | 494.1047 | 220.6692 | 222.3456 | 218.4536
2607.176 | 507.7304 | 220.5788 | 222.3115 | 218.3403
2608.176 | 507.361 | 220.4252 | 222.2269 | 218.3193
2609.176 | 512.7729 | 220.3388 | 222.1048 | 218.1858
2610.176 | 512.0302 | 220.0232 | 221.965 | 218.0664
2611.176 | 516.5654 | 220.0279 | 221.8207 | 217.8513
2612.176 | 518.0181 | 219.8791 | 221.6498 | 217.574
2613.176 | 512.6705 | 219.9789 | 221.6275 | 217.4374
2614.176 | 510.8739 | 219.956 | 221.5885 | 217.3746
2615.176 | 513.5468 | 219.837 | 221.4327 | 217.2473
2616.176 | 517.4167 | 219.7131 | 221.3542 | 217.5088
2617.176 | 507.0607 | 219.8571 | 221.1753 | 217.7741
2618.176 | 504.4905 | 219.8088 | 221.0896 | 217.8516
2619.176 | 497.6085 | 219.8583 | 220.9173 | 217.8879
2620.176 | 495.0463 | 219.824 | 220.8007 | 217.7963
2621.176 | 496.2717 | 219.7706 | 220.744 | 217.9179
2622.176 | 502.072 | 219.9299 | 220.5939 | 218.2155
2623.176 | 504.0867 | 219.8991 | 220.3978 | 218.6376
2624.176 | 500.0153 | 220.0038 | 220.3988 | 218.7449
2625.176 | 494.5487 | 220.0004 | 220.4586 | 218.8166
2626.176 | 494.9262 | 219.9862 | 220.5936 | 218.7046
2627.176 | 488.3048 | 219.8294 | 220.6626 | 218.6448
2628.176 | 492.7602 | 219.8562 | 220.7753 | 218.8537
2629.176 | 487.8252 | 219.7463 | 220.9199 | 218.7993
2630.176 | 485.0694 | 219.6051 | 220.9954 | 218.7656
2631.176 | 480.1597 | 220.1646 | 221.0706 | 219.0087
2632.176 | 476.4282 | 219.904 | 221.293 | 218.9538
2633.176 | 473.087 | 219.8672 | 221.4864 | 218.7972
2634.176 | 476.0924 | 219.8623 | 221.7315 | 219.0265
2635.176 | 476.1172 | 220.1011 | 221.8359 | 219.0679
2636.176 | 487.3243 | 220.1883 | 221.9764 | 219.091
2637.176 | 492.5832 | 220.1268 | 222.0703 | 219.1983
2638.176 | 492.1484 | 220.2945 | 222.2248 | 219.1017
2639.176 | 490.4646 | 220.2592 | 222.3095 | 219.1056
2640.176 | 483.7074 | 220.3571 | 222.3893 | 218.9397
2641.176 | 477.2812 | 220.3198 | 222.6157 | 218.9269
2642.176 | 481.7486 | 220.2246 | 222.6852 | 218.8398
2643.176 | 485.6906 | 220.2262 | 222.7634 | 218.9233
2644.176 | 486.8106 | 220.4377 | 222.9435 | 219.0479
2645.176 | 483.5797 | 220.4399 | 222.8512 | 218.9426
2646.176 | 487.2774 | 220.5648 | 222.8325 | 219.0184
2647.176 | 479.2915 | 220.5645 | 222.7817 | 219.2283
2648.176 | 472.3848 | 220.4955 | 222.7021 | 219.3914
2649.176 | 471.6909 | 220.6968 | 222.6282 | 219.3229
2650.176 | 464.0765 | 220.8711 | 222.4118 | 219.4055
2651.176 | 482.9742 | 220.9285 | 222.2122 | 219.7169
2652.176 | 478.9097 | 221.1864 | 222.2386 | 219.8709
2653.176 | 478.3742 | 221.3666 | 222.1902 | 219.9344
2654.176 | 476.7392 | 221.5235 | 222.072 | 219.8877
2655.176 | 474.9913 | 221.2097 | 222.039 | 220.0593
2656.176 | 481.8047 | 221.1428 | 221.8825 | 220.15
2657.176 | 481.703 | 221.1093 | 221.9052 | 220.2126
2658.176 | 484.3462 | 221.1156 | 221.6756 | 220.2977
2659.176 | 479.2218 | 221.1649 | 221.488 | 220.2946
2660.176 | 473.7759 | 221.1913 | 221.4167 | 220.1563
2661.176 | 471.7806 | 221.0494 | 221.3383 | 220.2267
2662.176 | 466.8816 | 221.0996 | 221.2689 | 220.462
2663.176 | 462.7586 | 221.014 | 221.2467 | 220.2859
2664.176 | 473.0794 | 220.8956 | 221.3306 | 220.1882
2665.176 | 479.3898 | 221.0735 | 221.4672 | 220.271
2666.176 | 482.3125 | 220.9029 | 221.3754 | 220.3112
2667.176 | 478.7729 | 220.8311 | 221.3946 | 220.0699
2668.176 | 478.2031 | 220.7264 | 221.3804 | 220.0618
2669.176 | 473.5395 | 220.7524 | 221.2956 | 220.2585
2670.176 | 468.6181 | 220.5179 | 221.1785 | 220.3563
2671.176 | 471.4809 | 220.4911 | 221.1055 | 220.2037
2672.176 | 478.6309 | 220.4991 | 220.8996 | 219.9732
2673.176 | 481.3054 | 220.4204 | 220.8114 | 219.998
2674.176 | 475.3669 | 220.4656 | 220.6758 | 219.963
2675.176 | 467.8883 | 220.2476 | 220.7138 | 220.0112
2676.176 | 466.646 | 220.3715 | 220.5281 | 220.3437
2677.176 | 463.3985 | 220.3218 | 220.4111 | 220.4298
2678.176 | 462.0593 | 220.1642 | 220.4235 | 220.6038
2679.176 | 457.0251 | 220.1148 | 220.4097 | 220.6791
2680.176 | 452.6544 | 219.8814 | 220.3267 | 220.6361
2681.176 | 449.0808 | 219.8462 | 220.3457 | 220.7061
2682.176 | 446.3011 | 219.6071 | 220.1087 | 220.4657
2683.176 | 449.394 | 219.4364 | 219.9112 | 220.4064
2684.176 | 454.2802 | 219.417 | 219.6404 | 220.4976
2685.176 | 453.4473 | 219.4082 | 219.4374 | 220.4949
2686.176 | 453.0285 | 219.5103 | 219.293 | 220.5472
2687.176 | 451.2661 | 219.6463 | 219.2049 | 220.5785
2688.176 | 450.755 | 219.8214 | 219.1592 | 220.3519
2689.176 | 456.7299 | 219.8549 | 219.1214 | 220.3198
2690.176 | 453.0672 | 220.1498 | 219.1694 | 220.0341
2691.176 | 447.1757 | 220.0739 | 219.1345 | 219.9266
2692.176 | 442.2913 | 220.2512 | 219.0288 | 219.7178
2693.176 | 441.7404 | 220.3656 | 218.936 | 219.457
2694.176 | 448.5256 | 220.3398 | 218.9059 | 219.3858
2695.176 | 448.7361 | 220.4143 | 218.8625 | 219.4001
2696.176 | 445.8995 | 220.3678 | 218.8513 | 219.2882
2697.176 | 459.7404 | 220.342 | 218.8469 | 219.4049
2698.176 | 458.7695 | 220.3263 | 218.8233 | 219.2615
2699.176 | 461.4021 | 220.2506 | 218.8532 | 219.1705
2700.176 | 463.3637 | 220.0454 | 218.7887 | 219.1342
2701.176 | 478.9698 | 220.0444 | 219.0448 | 219.2534
2702.176 | 486.9371 | 220.2649 | 219.4523 | 219.1504
2703.176 | 487.0622 | 220.219 | 219.4292 | 219.5021
2704.176 | 484.5424 | 220.3426 | 219.3606 | 219.3355
2705.176 | 488.7049 | 220.5016 | 219.2313 | 219.2602
2706.176 | 480.9933 | 220.6805 | 219.2375 | 219.194
2707.176 | 479.9565 | 220.6583 | 219.0283 | 219.1669
2708.176 | 479.9595 | 220.9532 | 219.0053 | 219.0112
2709.176 | 483.7856 | 221.1063 | 218.9568 | 218.8971
2710.176 | 496.5425 | 221.0821 | 219.1236 | 218.7688
2711.176 | 501.4954 | 220.9022 | 219.0285 | 218.7359
2712.176 | 500.7814 | 221.0391 | 218.9536 | 218.9841
2713.176 | 503.5171 | 221.0789 | 218.9168 | 219.0817
2714.176 | 506.7824 | 221.0301 | 218.823 | 218.83
2715.176 | 508.1891 | 220.6515 | 218.7597 | 218.6403
2716.176 | 509.5909 | 220.5423 | 218.7926 | 218.3733
2717.176 | 503.6625 | 220.5262 | 218.8163 | 218.2441
2718.176 | 500.4958 | 220.545 | 218.8677 | 218.2716
2719.176 | 509.3022 | 220.5095 | 218.8322 | 218.3438
2720.176 | 518.9768 | 220.2666 | 218.8716 | 218.2322
2721.176 | 515.0558 | 220.3227 | 218.9928 | 218.1965
2722.176 | 510.3677 | 220.322 | 219.0015 | 218.0651
2723.176 | 505.2816 | 220.2208 | 219.0878 | 218.1154
2724.176 | 502.9262 | 220.336 | 218.9546 | 218.1414
2725.176 | 497.5943 | 220.5692 | 218.9769 | 218.2283
2726.176 | 490.6309 | 220.7516 | 219.0094 | 218.3979
2727.176 | 485.7281 | 220.8729 | 219.0813 | 218.8051
2728.176 | 499.1178 | 221.2501 | 219.1164 | 219.1424
2729.176 | 494.4289 | 221.2648 | 219.1339 | 218.8547
2730.176 | 493.3077 | 221.0496 | 219.1222 | 218.6663
2731.176 | 492.03 | 220.7693 | 219.1998 | 218.6991
2732.176 | 491.7182 | 220.6916 | 219.1705 | 218.7113
2733.176 | 486.2157 | 220.5674 | 219.0847 | 218.6934
2734.176 | 491.2316 | 220.419 | 219.0934 | 218.6835
2735.176 | 493.2415 | 220.3073 | 219.0471 | 218.5545
2736.176 | 493.2655 | 220.1782 | 219.0915 | 218.4579
2737.176 | 489.4832 | 220.1232 | 219.1752 | 218.7129
2738.176 | 489.8123 | 219.9838 | 219.103 | 218.7276
2739.176 | 484.0238 | 219.9431 | 219.0773 | 218.7811
2740.176 | 483.9492 | 219.8738 | 219.1289 | 218.7955
2741.176 | 481.9269 | 219.6937 | 219.2198 | 218.7929
2742.176 | 484.6386 | 219.7881 | 219.2096 | 218.8813
2743.176 | 479.2649 | 219.5815 | 219.2042 | 218.9843
2744.176 | 480.6289 | 219.5093 | 219.1793 | 218.8908
2745.176 | 480.2312 | 219.2268 | 219.1893 | 218.7403
2746.176 | 486.2279 | 219.3331 | 219.2185 | 218.4893
2747.176 | 497.4891 | 219.4856 | 219.2391 | 218.4322
2748.176 | 506.7288 | 219.6753 | 219.2588 | 218.3564
2749.176 | 499.3299 | 219.9168 | 219.2522 | 218.5273
2750.176 | 499.7088 | 219.9839 | 219.273 | 218.6199
2751.176 | 493.5589 | 220.1393 | 219.3064 | 218.5531
2752.176 | 487.9905 | 220.0906 | 219.3715 | 218.4705
2753.176 | 484.5908 | 220.3354 | 219.328 | 218.4415
2754.176 | 485.0158 | 220.4667 | 219.3364 | 218.3036
2755.176 | 492.027 | 220.5439 | 219.3735 | 218.2393
2756.176 | 498.5881 | 220.53 | 219.2929 | 217.9623
2757.176 | 492.6061 | 220.4687 | 219.1669 | 217.6741
2758.176 | 489.8361 | 220.2816 | 219.1477 | 217.6095
2759.176 | 493.3915 | 220.1209 | 219.1495 | 217.7256
2760.176 | 491.2122 | 220.0871 | 219.2877 | 217.6787
2761.176 | 485.4285 | 220.1305 | 219.5068 | 217.9751
2762.176 | 490.6299 | 220.2045 | 219.4505 | 218.0606
2763.176 | 490.8625 | 220.1705 | 219.298 | 218.0752
2764.176 | 488.0124 | 220.3202 | 219.3096 | 218.2918
2765.176 | 489.9749 | 220.4015 | 219.3333 | 218.4603
2766.176 | 492.2001 | 220.5404 | 219.5058 | 218.7808
2767.176 | 489.4803 | 220.568 | 219.6078 | 218.9219
2768.176 | 491.197 | 220.758 | 219.6126 | 218.9297
2769.176 | 488.2331 | 220.8767 | 219.5743 | 218.8961
2770.176 | 482.0766 | 221.0065 | 219.567 | 218.7988
2771.176 | 482.4583 | 221.1048 | 219.6098 | 218.6665
2772.176 | 483.0395 | 221.359 | 219.7002 | 218.8222
2773.176 | 479.8667 | 221.5892 | 219.7705 | 219.0208
2774.176 | 478.1026 | 221.6067 | 219.8296 | 218.9484
2775.176 | 476.2121 | 221.7649 | 219.9056 | 219.045
2776.176 | 474.9009 | 221.9283 | 219.8866 | 219.0287
2777.176 | 474.4982 | 221.8803 | 219.8253 | 219.1713
2778.176 | 481.4455 | 221.9459 | 219.7735 | 219.5735
2779.176 | 478.6151 | 222.1438 | 219.9051 | 220.0297
2780.176 | 474.0849 | 222.1236 | 220.104 | 219.8359
2781.176 | 471.1187 | 222.0134 | 220.2309 | 220.2023
2782.176 | 465.7644 | 222.0985 | 220.3126 | 220.1965
2783.176 | 460.7687 | 222.1674 | 220.4618 | 220.0557
2784.176 | 465.2952 | 222.3368 | 220.6213 | 220.1721
2785.176 | 468.752 | 222.6999 | 220.8442 | 220.135
2786.176 | 468.4832 | 223.2035 | 221.2231 | 219.9797
2787.176 | 467.5146 | 223.8026 | 221.5433 | 220.2678
2788.176 | 465.1541 | 223.4922 | 222.096 | 220.236
2789.176 | 463.6268 | 223.4967 | 222.3589 | 220.4762
2790.176 | 468.6923 | 223.546 | 222.7348 | 221.7148
2791.176 | 468.8393 | 223.341 | 223.0237 | 221.8179
2792.176 | 469.1718 | 223.3876 | 223.2196 | 222.0605
2793.176 | 470.1694 | 223.1515 | 223.4289 | 222.01
2794.176 | 476.9562 | 223.4515 | 223.5522 | 221.77
2795.176 | 485.0486 | 223.396 | 223.5951 | 221.4452
2796.176 | 483.8474 | 223.1965 | 223.7852 | 221.2979
2797.176 | 483.6169 | 223.3385 | 223.7677 | 221.3306
2798.176 | 480.9154 | 222.9079 | 223.7691 | 221.1609
2799.176 | 484.2 | 222.7508 | 223.7292 | 221.1164
2800.176 | 490.5824 | 222.7892 | 223.8059 | 220.9565
2801.176 | 490.7278 | 222.9553 | 223.9094 | 220.8859
2802.176 | 485.8956 | 222.9077 | 223.8425 | 220.7344
2803.176 | 490.7821 | 222.979 | 223.7782 | 220.5372
2804.176 | 489.2676 | 223.0764 | 223.736 | 220.2708
2805.176 | 494.6017 | 222.968 | 223.757 | 220.2411
2806.176 | 498.5177 | 222.9048 | 223.5173 | 220.3388
2807.176 | 498.2327 | 222.9018 | 223.3823 | 220.3196
2808.176 | 497.5507 | 222.8459 | 223.2375 | 220.3165
2809.176 | 495.1285 | 222.7205 | 223.028 | 220.3452
2810.176 | 497.4318 | 222.6785 | 222.7897 | 220.4341
2811.176 | 496.0807 | 222.5918 | 222.7303 | 220.5333
2812.176 | 498.0183 | 222.7164 | 222.7314 | 220.5676
2813.176 | 503.0572 | 222.7382 | 222.6586 | 220.663
2814.176 | 498.4802 | 222.7295 | 222.8556 | 220.6708
2815.176 | 495.8468 | 222.8659 | 222.8206 | 220.7948
2816.176 | 495.2631 | 222.8835 | 222.8306 | 220.7713
2817.176 | 497.426 | 222.8991 | 223.0096 | 220.7464
2818.176 | 494.5135 | 222.9024 | 222.8576 | 220.6177
2819.176 | 487.7226 | 222.8381 | 222.8128 | 220.5432
2820.176 | 483.222 | 222.8929 | 222.7604 | 220.5693
2821.176 | 489.4482 | 223.0039 | 222.7889 | 220.6638
2822.176 | 483.4109 | 223.2217 | 222.8762 | 220.8065
2823.176 | 481.2321 | 223.3107 | 222.85 | 220.8033
2824.176 | 483.3503 | 223.1267 | 222.9347 | 220.8261
2825.176 | 484.4158 | 223.1698 | 223.0319 | 220.959
2826.176 | 480.4879 | 223.1068 | 222.9663 | 220.9771
2827.176 | 480.4411 | 223.2553 | 222.9356 | 220.8672
2828.176 | 483.0098 | 223.4136 | 223.1534 | 221.0406
2829.176 | 486.4889 | 223.5582 | 223.2284 | 221.0895
2830.176 | 490.4401 | 223.4754 | 223.3581 | 220.8564
2831.176 | 490.6949 | 223.4821 | 223.4229 | 220.678
2832.176 | 489.7666 | 223.4849 | 223.5605 | 220.55
2833.176 | 486.9082 | 223.2328 | 223.7397 | 220.4054
2834.176 | 485.817 | 223.3964 | 223.778 | 220.2834
2835.176 | 482.1196 | 223.5707 | 223.8916 | 220.2359
2836.176 | 491.9087 | 223.4084 | 224.1437 | 220.281
2837.176 | 493.038 | 223.3855 | 224.114 | 220.5473
2838.176 | 492.3296 | 223.3321 | 224.0803 | 220.5411
2839.176 | 504.3495 | 223.3181 | 224.0667 | 220.5467
2840.176 | 522.1846 | 223.4327 | 224.1173 | 220.9038
2841.176 | 519.5045 | 223.6824 | 224.0448 | 220.7706
2842.176 | 519.7851 | 223.7751 | 223.9 | 220.4866
2843.176 | 520.228 | 223.7507 | 223.9614 | 220.3098
2844.176 | 521.0541 | 223.6954 | 223.945 | 220.1467
2845.176 | 512.3709 | 223.6438 | 223.8804 | 220.0449
2846.176 | 505.6484 | 223.498 | 223.761 | 219.9681
2847.176 | 503.3613 | 223.421 | 223.7727 | 219.9315
2848.176 | 497.9455 | 223.4845 | 223.6376 | 220.117
2849.176 | 498.1667 | 223.4168 | 223.4969 | 220.1691
2850.176 | 502.1218 | 223.1981 | 223.2889 | 220.2596
2851.176 | 494.1639 | 223.0735 | 223.0595 | 220.0966
2852.176 | 494.3179 | 223.0814 | 222.9115 | 220.0245
2853.176 | 500.633 | 223.0016 | 222.8096 | 219.8195
2854.176 | 493.6112 | 223.1188 | 222.7787 | 219.7451
2855.176 | 485.2782 | 223.205 | 222.6943 | 219.7346
2856.176 | 479.3878 | 223.1705 | 222.7028 | 219.6879
2857.176 | 473.8053 | 223.1569 | 222.7602 | 219.7258
2858.176 | 473.6149 | 223.132 | 222.6424 | 220.1315
2859.176 | 471.9715 | 222.9015 | 222.6448 | 220.311
2860.176 | 472.2805 | 222.7259 | 222.6396 | 220.4572
2861.176 | 471.1773 | 222.9143 | 222.5979 | 220.6126
2862.176 | 467.4163 | 222.8725 | 222.6032 | 220.8453
2863.176 | 469.1858 | 222.8943 | 222.6215 | 221.2318
2864.176 | 472.9446 | 222.6685 | 222.5481 | 221.1073
2865.176 | 471.7894 | 222.6929 | 222.6742 | 221.0257
2866.176 | 467.6095 | 222.7524 | 222.7029 | 220.889
2867.176 | 466.9798 | 222.6017 | 222.7184 | 220.7508
2868.176 | 466.5623 | 222.7623 | 222.7676 | 220.6308
2869.176 | 464.266 | 222.761 | 222.8266 | 220.5331
2870.176 | 462.6113 | 222.6786 | 222.9853 | 220.5933
2871.176 | 460.8048 | 222.6647 | 223.0744 | 220.4674
2872.176 | 460.3047 | 222.6274 | 223.2584 | 220.4006
2873.176 | 460.5647 | 222.5805 | 223.5073 | 220.4417
2874.176 | 458.0501 | 222.4951 | 223.8376 | 220.6472
2875.176 | 454.3181 | 222.3411 | 224.0755 | 221.0482
2876.176 | 452.9718 | 222.2697 | 224.2804 | 221.4762
2877.176 | 450.4196 | 222.2143 | 224.4191 | 221.6715
2878.176 | 449.7897 | 222.1665 | 224.5732 | 221.6268
2879.176 | 457.958 | 221.8505 | 224.5951 | 221.6833
2880.176 | 456.4246 | 221.8337 | 224.7519 | 221.6065
2881.176 | 456.0213 | 221.8224 | 224.6976 | 221.6296
2882.176 | 457.7932 | 221.9683 | 224.7285 | 221.8166
2883.176 | 456.7474 | 221.9362 | 224.5682 | 221.742
2884.176 | 457.0043 | 221.9099 | 224.5381 | 221.6478
2885.176 | 459.0704 | 221.8719 | 224.2419 | 221.3477
2886.176 | 459.6514 | 221.8824 | 224.0273 | 221.0976
2887.176 | 455.8191 | 221.9855 | 223.9529 | 220.9413
2888.176 | 453.2691 | 221.9988 | 223.7617 | 220.7363
2889.176 | 451.7282 | 221.9715 | 223.4922 | 220.623
2890.176 | 454.5988 | 221.7933 | 223.3959 | 220.4917
2891.176 | 453.7742 | 221.8304 | 223.2049 | 220.5015
2892.176 | 452.3414 | 221.5803 | 222.9912 | 220.6319
2893.176 | 453.7839 | 221.3485 | 223.1207 | 220.8107
2894.176 | 455.2022 | 221.3952 | 223.3423 | 220.847
2895.176 | 461.2931 | 221.522 | 223.5359 | 221.0498
2896.176 | 464.399 | 221.4525 | 223.7676 | 221.2704
2897.176 | 468.097 | 221.8547 | 224.0086 | 221.2325
2898.176 | 481.4351 | 221.6485 | 224.2481 | 221.3595
2899.176 | 482.4038 | 221.5437 | 224.3599 | 221.4902
2900.176 | 492.45 | 221.4468 | 224.4664 | 221.5456
2901.176 | 493.6466 | 221.4191 | 224.5079 | 221.4807
2902.176 | 496.938 | 221.594 | 224.598 | 221.3864
2903.176 | 497.2029 | 221.9088 | 224.678 | 221.5478
2904.176 | 492.2876 | 222.1039 | 224.7755 | 221.957
2905.176 | 492.3379 | 222.2515 | 224.764 | 222.2481
2906.176 | 490.4293 | 222.6519 | 224.729 | 222.4218
2907.176 | 491.7603 | 222.6288 | 224.7175 | 222.2169
2908.176 | 487.5029 | 222.6375 | 224.8688 | 222.0719
2909.176 | 480.0221 | 222.7148 | 224.6772 | 222.1187
2910.176 | 475.1991 | 222.8683 | 224.5833 | 222.2358
2911.176 | 470.218 | 222.8741 | 224.4621 | 222.2435
2912.176 | 462.7756 | 222.9108 | 224.2875 | 222.3082
2913.176 | 458.3682 | 222.8165 | 224.1489 | 222.2907
2914.176 | 454.9847 | 222.7311 | 223.9953 | 222.224
2915.176 | 458.64 | 222.5779 | 223.976 | 222.3906
2916.176 | 462.2424 | 222.5261 | 223.8961 | 222.3367
2917.176 | 461.5412 | 222.4693 | 223.8834 | 222.2305
2918.176 | 465.7394 | 222.7026 | 223.769 | 222.2519
2919.176 | 470.8993 | 222.6018 | 223.6831 | 222.1553
2920.176 | 468.9551 | 222.6664 | 223.7915 | 222.2292
2921.176 | 469.974 | 222.7054 | 223.854 | 222.0474
2922.176 | 469.468 | 222.8727 | 223.8022 | 221.8205
2923.176 | 465.6886 | 222.8859 | 223.6796 | 221.7109
2924.176 | 466.9885 | 222.7352 | 223.7299 | 221.9021
2925.176 | 464.5653 | 222.6079 | 223.7638 | 221.6369
2926.176 | 464.6132 | 222.519 | 223.7548 | 221.5812
2927.176 | 466.9614 | 222.5015 | 223.5781 | 221.6161
2928.176 | 470.0901 | 222.6104 | 223.3871 | 221.5097
2929.176 | 482.475 | 222.7337 | 223.2889 | 221.301
2930.176 | 486.292 | 222.8366 | 223.1879 | 221.203
2931.176 | 491.6666 | 222.7556 | 223.1742 | 221.0111
2932.176 | 489.8106 | 222.8552 | 222.9844 | 221.0202
2933.176 | 488.0493 | 222.7171 | 222.8598 | 220.9299
2934.176 | 492.3751 | 222.8055 | 223.0101 | 220.9087
2935.176 | 490.3397 | 223.0791 | 223.115 | 220.841
2936.176 | 485.907 | 223.172 | 223.0196 | 220.8181
2937.176 | 489.2137 | 223.3631 | 223.1337 | 220.9828
2938.176 | 489.6784 | 223.4011 | 223.0888 | 221.2558
2939.176 | 490.5599 | 223.2947 | 223.0425 | 221.3661
2940.176 | 488.0799 | 223.2598 | 223.0008 | 221.5044
2941.176 | 482.8934 | 223.3014 | 223.0505 | 221.6948
2942.176 | 476.374 | 223.364 | 223.0088 | 221.8357
2943.176 | 472.9765 | 223.4303 | 223.1468 | 221.8755
2944.176 | 470.3655 | 223.3078 | 223.0019 | 222.0689
2945.176 | 469.8958 | 223.1365 | 222.942 | 222.1285
2946.176 | 470.4232 | 223.0782 | 223.1178 | 222.1756
2947.176 | 468.4329 | 222.8707 | 222.9559 | 222.3165
2948.176 | 463.4336 | 222.8533 | 222.7939 | 222.1254
2949.176 | 461.7035 | 222.9331 | 222.6637 | 222.0976
2950.176 | 460.0783 | 222.8277 | 222.6783 | 222.27
2951.176 | 461.4314 | 223.0124 | 222.7325 | 222.2637
2952.176 | 460.178 | 223.1565 | 222.7941 | 222.3057
2953.176 | 456.7679 | 223.3143 | 222.8488 | 222.2442
2954.176 | 453.9075 | 223.5612 | 222.8006 | 222.3295
2955.176 | 448.7667 | 223.585 | 222.8671 | 222.4307
2956.176 | 446.8975 | 223.7227 | 222.9103 | 222.3595
2957.176 | 445.8151 | 223.8285 | 222.8713 | 222.3424
2958.176 | 445.312 | 223.9308 | 222.8041 | 222.255
2959.176 | 441.4728 | 223.8098 | 222.8113 | 222.3744
2960.176 | 438.2868 | 223.7575 | 222.7266 | 222.4079
2961.176 | 436.9964 | 223.7615 | 222.6234 | 222.5208
2962.176 | 442.0759 | 223.6913 | 222.4992 | 222.4849
2963.176 | 445.2101 | 223.4498 | 222.4221 | 222.4904
2964.176 | 452.6601 | 223.2506 | 222.3802 | 222.3844
2965.176 | 449.7523 | 223.0933 | 222.5206 | 222.4319
2966.176 | 449.6724 | 222.8864 | 222.426 | 222.5351
2967.176 | 447.4988 | 222.7975 | 222.3239 | 222.45
2968.176 | 453.6365 | 222.9588 | 222.287 | 222.2084
2969.176 | 451.9187 | 222.9606 | 222.2817 | 222.0535
2970.176 | 449.9636 | 223.0325 | 222.1715 | 222.2587
2971.176 | 451.7642 | 222.8961 | 222.569 | 222.182
2972.176 | 452.0679 | 222.7364 | 222.4797 | 222.0585
2973.176 | 450.9896 | 222.8907 | 222.3353 | 221.924
2974.176 | 448.4098 | 222.7434 | 222.2057 | 221.9213
2975.1917 | 444.6591 | 222.5542 | 222.1474 | 221.8164
2976.1917 | 442.4914 | 222.488 | 222.1521 | 221.7793
2977.176 | 445.0304 | 222.5849 | 222.2262 | 221.7596
2978.176 | 450.6535 | 222.5281 | 222.2481 | 221.9838
2979.176 | 455.4901 | 222.5663 | 222.2852 | 222.1283
2980.176 | 458.3311 | 222.7617 | 222.1757 | 222.2778
2981.176 | 457.6121 | 222.8549 | 222.1537 | 222.4206
2982.176 | 456.7649 | 222.7558 | 222.3517 | 222.3431
2983.1917 | 455.6685 | 222.8234 | 222.2964 | 222.1676
2984.1917 | 453.9036 | 222.7825 | 222.2982 | 222.0081
2985.1917 | 455.3914 | 222.6656 | 222.3743 | 221.9494
2986.176 | 452.0721 | 222.4483 | 222.2615 | 221.9533
2987.176 | 450.2718 | 222.284 | 222.3077 | 221.8527
2988.176 | 443.2725 | 222.2205 | 222.3217 | 221.7078
2989.176 | 443.042 | 222.3292 | 222.2254 | 221.6053
2990.176 | 442.2153 | 222.373 | 222.2242 | 221.568
2991.176 | 438.0688 | 222.5462 | 222.3257 | 221.4798
2992.176 | 433.9673 | 222.7114 | 222.3426 | 221.3159
2993.176 | 430.0475 | 222.7807 | 222.2981 | 221.2552
2994.176 | 428.8001 | 223.0838 | 222.5189 | 221.2551
2995.176 | 428.7446 | 222.8727 | 222.5086 | 221.2218
2996.176 | 429.8872 | 222.8963 | 223.0433 | 221.272
2997.176 | 431.4944 | 223.0277 | 223.0701 | 221.3634
2998.176 | 438.263 | 223.1796 | 223.1293 | 221.5849
2999.176 | 437.3484 | 223.1753 | 223.1846 | 221.6414
3000.176 | 455.3192 | 223.478 | 223.2351 | 221.8492
3001.176 | 455.4385 | 223.4384 | 223.4039 | 221.8426
3002.176 | 454.8987 | 223.4674 | 223.5731 | 221.7625
3003.176 | 455.8367 | 223.5603 | 223.6705 | 221.7641
3004.176 | 454.3771 | 223.651 | 223.875 | 222.0798
3005.176 | 453.3932 | 223.6685 | 223.9484 | 221.9073
3006.176 | 455.8443 | 223.7903 | 224.2683 | 221.8888
3007.176 | 454.0992 | 223.8543 | 224.6238 | 221.8359
3008.176 | 457.3024 | 223.8637 | 224.9391 | 221.7908
3009.176 | 459.0954 | 223.8463 | 225.3063 | 221.8627
3010.176 | 458.8301 | 223.6385 | 225.3764 | 221.9207
3011.176 | 461.5709 | 223.3715 | 225.4493 | 222.1082
3012.176 | 461.9413 | 223.1337 | 225.4701 | 222.0858
3013.176 | 461.4937 | 223.0312 | 225.3714 | 222.109
3014.176 | 458.1349 | 223.137 | 225.3552 | 222.3417
3015.176 | 456.2341 | 223.1875 | 225.2504 | 222.0599
3016.176 | 454.8563 | 222.9837 | 225.2117 | 221.8484
3017.176 | 454.9635 | 222.7214 | 225.1682 | 222.0307
3018.176 | 456.4521 | 222.3483 | 225.1004 | 221.8853
3019.176 | 455.8423 | 222.2047 | 225.0013 | 222.0457
3020.176 | 456.0571 | 222.0739 | 224.9479 | 221.9583
3021.176 | 455.4364 | 222.2171 | 225.0073 | 221.8935
3022.176 | 453.3492 | 222.2032 | 224.9626 | 221.6986
3023.176 | 450.2386 | 222.2143 | 224.9576 | 221.5771
3024.176 | 449.3263 | 222.0927 | 224.916 | 221.5107
3025.176 | 448.3195 | 222.2707 | 225.0177 | 221.6824
3026.176 | 449.7659 | 222.3076 | 224.8798 | 221.8311
3027.176 | 448.6553 | 222.3608 | 224.7482 | 221.754
3028.176 | 446.5697 | 222.3859 | 224.7102 | 221.6975
3029.176 | 446.3414 | 222.3135 | 224.4863 | 221.5046
3030.176 | 453.2297 | 222.4691 | 224.2099 | 221.5088
3031.176 | 453.6746 | 222.4827 | 223.992 | 221.4379
3032.176 | 459.588 | 222.3876 | 223.8432 | 221.2725
3033.176 | 465.3308 | 222.1824 | 223.6892 | 220.9833
3034.176 | 463.9218 | 222.0744 | 223.5441 | 220.9683
3035.176 | 461.8416 | 222.0176 | 223.4252 | 220.9136
3036.176 | 461.1969 | 221.9253 | 223.3237 | 221.054
3037.176 | 459.5188 | 222.0793 | 223.2755 | 221.3955
3038.176 | 458.5198 | 222.3173 | 223.1005 | 221.4339
3039.176 | 459.9952 | 222.3517 | 223.0434 | 221.3447
3040.176 | 462.0045 | 222.3764 | 223.1279 | 221.6115
3041.176 | 459.511 | 222.4879 | 223.0238 | 221.7732
3042.176 | 461.5636 | 222.7113 | 222.9069 | 221.6923
3043.176 | 460.6567 | 222.7663 | 222.9012 | 221.6787
3044.176 | 456.3207 | 222.8467 | 223.1779 | 221.7279
3045.176 | 453.7937 | 223.1584 | 223.1958 | 221.7615
3046.176 | 450.9132 | 223.1613 | 223.1442 | 221.7149
3047.176 | 447.9602 | 223.1393 | 223.007 | 221.6392
3048.176 | 445.5956 | 223.0412 | 222.9249 | 221.6011
3049.176 | 443.1676 | 222.8527 | 222.7899 | 221.5282
3050.176 | 440.8103 | 222.6411 | 222.6345 | 221.6839
3051.176 | 441.4885 | 222.7537 | 222.5686 | 221.5528
3052.176 | 444.6845 | 222.6921 | 222.4788 | 221.5386
3053.176 | 444.4556 | 222.85 | 222.4734 | 221.61
3054.176 | 442.6744 | 222.7977 | 222.5564 | 221.6245
3055.176 | 439.1024 | 222.6799 | 222.6541 | 221.7991
3056.176 | 438.5326 | 222.5528 | 222.6481 | 222.0085
3057.176 | 444.2738 | 222.2972 | 222.8688 | 222.0702
3058.176 | 449.5605 | 222.114 | 222.6994 | 222.1369
3059.176 | 448.7334 | 222.1636 | 222.6556 | 222.193
3060.176 | 445.3749 | 222.1604 | 222.5665 | 222.2151
3061.176 | 443.2543 | 222.2219 | 222.4936 | 222.148
3062.176 | 444.6236 | 222.1844 | 222.7462 | 222.1477
3063.176 | 446.0636 | 222.1931 | 222.7974 | 222.3678
3064.176 | 449.2415 | 222.0931 | 222.8074 | 222.684
3065.176 | 452.5609 | 222.0938 | 222.7998 | 222.6031
3066.176 | 454.8624 | 222.1536 | 222.8866 | 222.6003
3067.176 | 458.0357 | 222.117 | 223.0437 | 222.5678
3068.176 | 458.4671 | 222.1531 | 223.2172 | 222.5263
3069.176 | 454.6212 | 222.1225 | 223.335 | 222.3932
3070.176 | 455.8864 | 221.939 | 223.331 | 222.3534
3071.176 | 454.3526 | 221.849 | 223.3392 | 222.3234
3072.176 | 454.34 | 221.7973 | 223.2996 | 222.2667
3073.176 | 451.301 | 221.6752 | 223.1207 | 222.1332
3074.176 | 449.8547 | 221.6158 | 223.1227 | 222.0275
3075.176 | 456.3307 | 221.6261 | 223.1275 | 222.0974
3076.176 | 460.5608 | 221.6457 | 223.2453 | 222.122
3077.176 | 461.6672 | 221.4702 | 223.3035 | 221.996
3078.176 | 465.8555 | 221.5414 | 223.4107 | 221.922
3079.176 | 468.8276 | 221.5347 | 223.4886 | 221.8646
3080.176 | 471.1906 | 221.9437 | 223.7365 | 221.8363
3081.176 | 469.9178 | 222.3898 | 223.8821 | 221.7695
3082.176 | 467.9765 | 222.5217 | 223.9556 | 221.8285
3083.176 | 466.1332 | 222.7078 | 223.9332 | 221.7981
3084.176 | 469.1885 | 223.0542 | 224.0278 | 221.8222
3085.176 | 468.8101 | 223.3248 | 224.036 | 221.8465
3086.176 | 476.3668 | 223.0416 | 224.0166 | 221.7982
3087.176 | 473.9101 | 222.9674 | 224.1296 | 221.9199
3088.176 | 470.5475 | 222.8586 | 224.34 | 221.8674
3089.176 | 467.2999 | 222.9231 | 224.5464 | 222.0461
3090.176 | 463.8371 | 222.9866 | 224.7382 | 222.251
3091.176 | 462.0429 | 223.1729 | 224.8349 | 222.213
3092.176 | 457.8478 | 223.0048 | 224.9552 | 222.3453
3093.176 | 457.3482 | 222.8666 | 224.9528 | 222.397
3094.176 | 455.0631 | 222.9557 | 224.9667 | 222.386
3095.176 | 459.3291 | 222.9206 | 224.8227 | 222.3633
3096.176 | 459.193 | 222.9763 | 224.7218 | 222.4114
3097.176 | 457.4418 | 222.8912 | 224.5536 | 222.4823
3098.176 | 454.2996 | 222.9542 | 224.5239 | 222.7951
3099.176 | 455.3627 | 223.0067 | 224.4804 | 222.7916
3100.176 | 456.0662 | 223.0572 | 224.4631 | 222.7674
3101.176 | 456.6831 | 222.9994 | 224.4125 | 222.8599
3102.176 | 458.9461 | 222.9606 | 224.3865 | 222.6966
3103.176 | 460.9318 | 223.0851 | 224.3188 | 222.8331
3104.176 | 459.6232 | 222.9885 | 224.1073 | 222.9752
3105.176 | 457.7885 | 222.919 | 223.9743 | 222.9692
3106.176 | 461.1338 | 223.0777 | 223.9005 | 223.0627
3107.176 | 461.7452 | 223.1502 | 223.8909 | 223.1652
3108.176 | 465.4401 | 223.2458 | 223.8553 | 223.3381
3109.176 | 473.9062 | 223.1757 | 223.8596 | 223.3097
3110.176 | 475.5584 | 223.1665 | 223.7874 | 223.4579
3111.176 | 477.8679 | 223.2081 | 223.7537 | 223.3815
3112.176 | 471.7896 | 223.4315 | 223.6542 | 223.3064
3113.176 | 469.1276 | 223.5652 | 223.5771 | 223.1341
3114.176 | 465.4209 | 223.3892 | 223.4928 | 223.0057
3115.176 | 467.5742 | 223.3274 | 223.5386 | 223.0885
3116.176 | 466.7118 | 223.1008 | 223.4632 | 223.245
3117.176 | 464.5407 | 223.168 | 223.4368 | 223.3132
3118.176 | 462.7758 | 223.0632 | 223.5951 | 223.2826
3119.176 | 460.1952 | 223.0587 | 223.3939 | 223.3084
3120.176 | 458.6849 | 222.9487 | 223.2713 | 223.2898
3121.176 | 456.9079 | 223.1039 | 223.2094 | 223.4366
3122.176 | 457.4581 | 223.1837 | 223.0514 | 223.2717
3123.176 | 458.9987 | 223.1199 | 222.9933 | 223.0478
3124.176 | 453.4609 | 223.0344 | 223.0536 | 223.203
3125.176 | 450.5027 | 223.0857 | 223.0848 | 223.1794
3126.176 | 449.2063 | 223.1177 | 223.1232 | 223.1701
3127.176 | 448.786 | 223.2158 | 223.1364 | 223.2012
3128.176 | 447.4191 | 223.1864 | 223.0224 | 223.0727
3129.176 | 447.1414 | 223.1779 | 222.9755 | 223.0534
3130.176 | 447.1128 | 223.0688 | 222.8647 | 223.1257
3131.176 | 448.0182 | 223.2405 | 222.6378 | 222.7723
3132.176 | 446.1362 | 223.4004 | 222.4772 | 222.8801
3133.176 | 446.5454 | 223.4612 | 222.3337 | 223.0585
3134.176 | 444.0931 | 223.2419 | 222.2592 | 223.0936
3135.176 | 441.4357 | 223.0616 | 222.2331 | 223.0334
3136.176 | 443.7482 | 223.0689 | 222.2295 | 223.0881
3137.176 | 444.9716 | 222.8192 | 222.2361 | 222.8499
3138.176 | 447.5475 | 222.8339 | 222.1915 | 222.8331
3139.176 | 445.2101 | 222.8566 | 222.1667 | 222.7602
3140.176 | 442.8901 | 222.9781 | 222.2205 | 222.9584
3141.176 | 440.8172 | 222.6763 | 222.1626 | 222.9505
3142.176 | 442.0432 | 222.6218 | 222.0943 | 222.84
3143.1917 | 440.8245 | 222.6925 | 222.1307 | 222.9203
3144.176 | 442.6107 | 222.5812 | 222.1196 | 222.9927
3145.176 | 439.5558 | 222.5332 | 222.1046 | 223.1654
3146.176 | 434.9603 | 222.5962 | 222.0368 | 223.1237
3147.176 | 430.4368 | 222.5298 | 222.0367 | 223.0678
3148.176 | 431.7391 | 222.5152 | 221.9668 | 222.9544
3149.176 | 433.621 | 222.5386 | 221.9089 | 222.9534
3150.176 | 432.1352 | 222.437 | 221.8115 | 222.9826
3151.176 | 435.3061 | 222.2579 | 221.8304 | 222.9626
3152.176 | 438.9316 | 222.2778 | 221.8795 | 222.7115
3153.176 | 439.9651 | 222.1266 | 221.8554 | 222.5723
3154.176 | 441.1585 | 222.0248 | 221.704 | 222.3764
3155.176 | 442.3631 | 222.1608 | 221.6129 | 222.2905
3156.176 | 446.6586 | 222.1209 | 221.6214 | 222.1182
3157.176 | 446.4291 | 222.1224 | 221.4818 | 222.1513
3158.176 | 444.9655 | 222.1808 | 221.3838 | 222.2807
3159.176 | 442.9762 | 222.1278 | 221.251 | 221.9591
3160.176 | 443.0519 | 221.9499 | 221.1868 | 221.6798
3161.176 | 442.0773 | 221.8429 | 221.2242 | 221.4809
3162.176 | 442.51 | 221.9678 | 221.1981 | 221.2958
3163.176 | 439.4412 | 222.123 | 221.257 | 221.6454
3164.176 | 437.3063 | 222.1624 | 221.245 | 221.5394
3165.176 | 437.2005 | 222.2829 | 221.3038 | 221.4706
3166.176 | 434.769 | 222.2689 | 221.485 | 221.6348
3167.176 | 432.5877 | 222.3063 | 221.5694 | 221.8541
3168.176 | 429.1324 | 222.3402 | 221.5075 | 221.7885
3169.176 | 430.5879 | 222.3019 | 221.4794 | 221.7262
3170.176 | 429.7731 | 222.2626 | 221.3329 | 221.731
3171.176 | 432.2315 | 222.1912 | 221.2764 | 221.707
3172.176 | 432.6958 | 222.2382 | 221.2639 | 221.4954
3173.1917 | 434.8673 | 222.1814 | 221.2369 | 221.2742
3174.176 | 440.1737 | 222.1372 | 221.2209 | 221.2019
3175.176 | 440.2638 | 222.3514 | 221.3629 | 221.2125
3176.176 | 443.5151 | 222.5146 | 221.358 | 221.2665
3177.176 | 443.4296 | 222.7205 | 221.3482 | 221.347
3178.176 | 441.7066 | 222.7337 | 221.2184 | 221.4025
3179.176 | 438.674 | 222.7045 | 221.1557 | 221.5452
3180.176 | 435.4341 | 222.6389 | 221.0664 | 221.5296
3181.176 | 430.6882 | 222.4818 | 220.9797 | 221.5115
3182.176 | 427.0243 | 222.2206 | 220.966 | 221.5282
3183.176 | 425.3508 | 222.0411 | 220.8196 | 221.7025
3184.176 | 423.9974 | 221.931 | 220.8121 | 221.7548
3185.176 | 422.816 | 221.8763 | 220.7322 | 221.6357
3186.176 | 424.9792 | 221.8243 | 220.6892 | 221.676
3187.176 | 427.8917 | 221.6951 | 220.6383 | 221.4322
3188.176 | 428.4046 | 221.4017 | 220.6746 | 221.3648
3189.176 | 431.6661 | 221.2216 | 220.6194 | 221.4076
3190.176 | 431.9021 | 221.1408 | 220.5521 | 221.2998
3191.176 | 436.6238 | 221.1837 | 220.5441 | 221.1209
3192.176 | 440.8235 | 221.5701 | 220.4269 | 221.0438
3193.176 | 442.109 | 221.6748 | 220.4135 | 220.9749
3194.176 | 444.866 | 221.9141 | 220.4626 | 221.0221
3195.176 | 445.5306 | 222.0107 | 220.2732 | 220.7887
3196.176 | 449.5884 | 222.0059 | 220.3292 | 220.6853
3197.176 | 454.0834 | 222.2441 | 220.2744 | 220.761
3198.176 | 453.0177 | 222.3049 | 220.2169 | 220.6962
3199.176 | 451.1795 | 222.41 | 220.3494 | 220.7983
3200.176 | 453.4161 | 222.3571 | 220.4153 | 221.1026
3201.176 | 451.9316 | 222.3897 | 220.4327 | 221.2522
3202.176 | 453.8822 | 222.3019 | 220.403 | 221.1604
3203.1917 | 453.7913 | 222.2555 | 220.3896 | 221.3194
3204.176 | 450.192 | 222.3416 | 220.392 | 221.5783
3205.176 | 448.5319 | 222.4929 | 220.3105 | 221.4986
3206.176 | 445.0059 | 222.5468 | 220.2474 | 221.3451
3207.176 | 442.8371 | 222.485 | 220.3737 | 221.072
3208.176 | 439.8577 | 222.3396 | 220.3212 | 220.9843
3209.176 | 441.6076 | 222.1058 | 220.251 | 220.8488
3210.176 | 440.7811 | 222.0639 | 220.2218 | 220.5289
3211.176 | 439.4703 | 221.8897 | 220.1965 | 220.4097
3212.176 | 436.6173 | 221.5952 | 220.1113 | 220.3568
3213.176 | 436.1398 | 221.3818 | 220.0423 | 220.4806
3214.176 | 433.8213 | 221.352 | 220.0543 | 220.6521
3215.176 | 432.1387 | 221.2456 | 219.9614 | 220.5979
3216.176 | 432.7156 | 221.1443 | 219.8332 | 220.7101
3217.176 | 431.4475 | 221.1923 | 219.689 | 220.9111
3218.176 | 436.2179 | 220.8836 | 219.589 | 220.9779
3219.176 | 438.1992 | 220.6758 | 219.5875 | 221.0593
3220.176 | 439.3376 | 220.3612 | 219.5887 | 220.8274
3221.176 | 439.27 | 220.3752 | 219.658 | 220.8348
3222.176 | 437.2005 | 220.477 | 219.5873 | 220.8747
3223.176 | 435.0515 | 220.8693 | 219.5615 | 221.0325
3224.176 | 432.3459 | 220.9886 | 219.5851 | 221.1102
3225.176 | 431.4915 | 221.0052 | 219.7244 | 221.0932
3226.2229 | 430.6644 | 220.9365 | 219.9995 | 220.9867
3227.176 | 430.8366 | 220.836 | 220.1455 | 220.7893
3228.176 | 430.0826 | 220.7457 | 220.2777 | 220.6011
3229.176 | 424.2246 | 220.5782 | 220.3465 | 220.4427
3230.176 | 424.4636 | 220.6583 | 220.3454 | 220.2601
3231.176 | 423.4925 | 220.728 | 220.2839 | 220.0747
3232.176 | 423.1168 | 220.722 | 220.192 | 220.0105
3233.1917 | 422.1389 | 220.4467 | 220.2946 | 220.0698
3234.176 | 418.2484 | 220.5999 | 220.3876 | 220.051
3235.176 | 415.695 | 220.7951 | 220.4779 | 220.1243
3236.176 | 415.0723 | 220.8856 | 220.6475 | 220.5084
3237.176 | 415.2326 | 221.0297 | 220.764 | 220.4349
3238.176 | 417.8067 | 221.1519 | 220.979 | 220.556
3239.176 | 413.7345 | 221.3611 | 221.1764 | 220.507
3240.176 | 409.5593 | 221.3897 | 221.3345 | 220.8403
3241.176 | 411.9878 | 221.878 | 221.3931 | 221.0299
3242.176 | 412.0991 | 221.9538 | 221.9972 | 221.2429
3243.176 | 412.7288 | 221.9726 | 222.1628 | 221.752
3244.176 | 409.759 | 222.3626 | 222.3109 | 221.6545
3245.176 | 407.9418 | 222.5844 | 222.6209 | 221.9614
3246.176 | 408.0427 | 222.4628 | 222.987 | 221.9866
3247.176 | 411.8686 | 222.6244 | 223.5004 | 222.0332
3248.176 | 411.3034 | 222.7697 | 223.9344 | 221.9364
3249.176 | 414.0128 | 222.6431 | 224.4182 | 222.3209
3250.176 | 415.2938 | 222.9716 | 224.7585 | 222.4743
3251.176 | 412.9511 | 222.9001 | 225.0827 | 222.6919
3252.176 | 413.0384 | 222.8793 | 225.5573 | 222.9401
3253.176 | 413.7866 | 223.0608 | 225.9603 | 223.1414
3254.176 | 412.5945 | 223.6325 | 226.0842 | 223.6976
3255.176 | 412.0864 | 223.4376 | 226.2816 | 223.6272
3256.176 | 413.484 | 223.4227 | 226.3612 | 223.5803
3257.176 | 412.5051 | 223.5082 | 226.6745 | 223.7523
3258.176 | 408.3503 | 223.4528 | 226.6703 | 223.6616
3259.176 | 404.82 | 223.318 | 226.5802 | 223.5893
3260.176 | 403.1024 | 223.4261 | 226.6226 | 223.6977
3261.176 | 401.4682 | 223.2902 | 226.5647 | 223.7251
3262.176 | 402.301 | 223.5409 | 226.7188 | 223.7506
3263.176 | 406.0059 | 223.5411 | 226.7867 | 223.7814
3264.176 | 407.6281 | 223.3967 | 226.8844 | 224.0622
3265.176 | 409.7531 | 223.1816 | 226.9219 | 224.2102
3266.176 | 411.0651 | 223.0062 | 227.0727 | 224.3389
3267.176 | 410.9452 | 223.063 | 227.3097 | 224.1409
3268.176 | 410.6168 | 223.1313 | 227.3254 | 224.1569
3269.176 | 408.6895 | 222.9693 | 227.3336 | 224.1771
3270.176 | 404.2331 | 222.9254 | 227.377 | 224.0652
3271.1917 | 406.8227 | 222.8165 | 227.4989 | 223.8722
3272.176 | 407.6976 | 222.7888 | 227.519 | 223.9634
3273.176 | 410.481 | 222.7296 | 227.4111 | 223.8559
3274.1917 | 412.7064 | 222.6994 | 227.3171 | 223.985
3275.1917 | 417.6005 | 222.644 | 227.2971 | 224.0337
3276.176 | 421.7512 | 222.5626 | 227.239 | 223.9494
3277.176 | 423.2678 | 222.4943 | 227.2886 | 223.9358
3278.176 | 426.2969 | 222.4018 | 227.3437 | 223.9612
3279.176 | 427.7809 | 222.5383 | 227.299 | 224.0282
3280.176 | 432.1214 | 222.8877 | 227.44 | 224.4535
3281.176 | 434.3361 | 222.9817 | 227.4186 | 224.3416
3282.176 | 433.027 | 222.9839 | 227.4277 | 224.4795
3283.176 | 435.2902 | 222.8412 | 227.3914 | 224.3341
3284.176 | 437.4359 | 222.6893 | 227.3198 | 224.3814
3285.176 | 435.9269 | 222.7698 | 227.1505 | 224.2275
3286.176 | 435.0154 | 222.7352 | 227.0224 | 223.9923
3287.176 | 430.5115 | 222.8726 | 226.9272 | 223.896
3288.176 | 429.7691 | 223.1293 | 226.8427 | 223.7355
3289.176 | 431.2433 | 223.0388 | 226.7215 | 223.6926
3290.176 | 431.0302 | 223.1594 | 226.8088 | 223.7798
3291.176 | 434.4997 | 223.2055 | 226.7881 | 223.7928
3292.176 | 438.8865 | 223.1254 | 226.6707 | 223.6145
3293.1917 | 441.9679 | 222.9704 | 226.6099 | 223.4517
3294.176 | 443.3318 | 223.1321 | 226.609 | 223.3313
3295.176 | 442.4675 | 222.9855 | 226.5057 | 223.4308
3296.176 | 445.1705 | 223.0001 | 226.556 | 223.5433
3297.176 | 444.8776 | 222.9466 | 226.5831 | 223.6415
3298.176 | 444.1202 | 222.9809 | 226.5297 | 223.557
3299.176 | 442.6468 | 223.0055 | 226.4505 | 223.4393
3300.176 | 443.0834 | 223.0417 | 226.3139 | 223.2128
3301.176 | 445.8345 | 223.057 | 226.1509 | 223.0738
3302.176 | 447.9229 | 222.9158 | 225.9064 | 223.0647
3303.176 | 451.1271 | 223.1012 | 225.7336 | 222.9473
3304.176 | 449.9544 | 223.2725 | 225.6355 | 222.8808
3305.176 | 451.0538 | 223.3925 | 225.4835 | 222.8882
3306.176 | 445.8557 | 223.5283 | 225.3672 | 223.0412
3307.176 | 439.331 | 223.5557 | 225.2843 | 222.9868
3308.176 | 436.3968 | 223.5432 | 225.243 | 223.1239
3309.176 | 435.1536 | 223.2686 | 225.0949 | 223.1777
3310.176 | 432.1915 | 223.3145 | 224.9106 | 223.1603
3311.176 | 432.8339 | 223.2544 | 224.7292 | 223.1808
3312.176 | 431.6876 | 223.2747 | 224.6836 | 223.1507
3313.176 | 439.8425 | 223.5665 | 224.804 | 223.427
3314.176 | 443.9632 | 223.7808 | 224.9638 | 223.5369
3315.176 | 450.073 | 224.0107 | 225.2532 | 223.9952
3316.176 | 454.7311 | 224.3163 | 225.4119 | 224.1814
3317.176 | 456.4248 | 224.775 | 225.5257 | 224.4346
3318.176 | 459.4165 | 225.2212 | 225.7013 | 224.8676
3319.176 | 463.3578 | 225.4065 | 226.1643 | 225.313
3320.176 | 469.2205 | 225.7302 | 226.6382 | 226.1466
3321.176 | 471.5064 | 225.8937 | 227.2228 | 227.1227
3322.176 | 471.8367 | 226.2382 | 227.7758 | 227.7027
3323.176 | 469.9471 | 226.8119 | 228.362 | 228.5168
3324.176 | 465.1764 | 227.4921 | 228.8784 | 229.0818
3325.176 | 459.9743 | 228.1909 | 229.3775 | 229.3942
3326.176 | 456.4379 | 228.9502 | 229.9094 | 230.3478
3327.176 | 460.283 | 229.3509 | 230.4296 | 230.9549
3328.176 | 456.7777 | 229.6673 | 231.1278 | 231.0365
3329.176 | 451.082 | 229.9956 | 231.7119 | 231.2834
3330.176 | 449.005 | 231.0645 | 232.1977 | 231.8906
3331.176 | 449.5015 | 231.8449 | 233.1476 | 232.392
3332.176 | 448.9192 | 232.6514 | 233.8612 | 232.7559
3333.176 | 447.4288 | 233.2205 | 234.4756 | 232.8539
3334.176 | 448.1939 | 233.6581 | 234.9382 | 232.9619
3335.176 | 446.1402 | 234.1707 | 235.4202 | 232.9199
3336.176 | 445.6126 | 234.5312 | 235.8713 | 232.9424
3337.176 | 443.6626 | 234.8851 | 236.5334 | 233.1062
3338.176 | 447.2091 | 235.3516 | 237.2531 | 233.5288
3339.176 | 447.6848 | 236.2442 | 237.6652 | 234.5008
3340.176 | 444.3162 | 236.6903 | 238.1369 | 234.6674
3341.176 | 443.9985 | 237.1287 | 238.6344 | 234.7316
3342.176 | 446.2838 | 237.4172 | 238.9322 | 235.0379
3343.176 | 445.9862 | 237.8514 | 239.1226 | 235.7147
3344.176 | 448.9305 | 237.7375 | 239.1993 | 236.1118
3345.176 | 450.3157 | 238.0306 | 239.3815 | 236.4069
3346.176 | 451.9505 | 238.1954 | 239.4894 | 236.7537
3347.176 | 447.8766 | 238.8037 | 239.7133 | 236.8222
3348.176 | 449.8574 | 239.0671 | 240.0567 | 237.0203
3349.176 | 451.8674 | 239.3938 | 240.4918 | 237.2333
3350.176 | 454.5371 | 239.2422 | 240.5303 | 237.1499
3351.176 | 451.4364 | 239.2428 | 240.6637 | 237.0866
3352.176 | 450.309 | 239.5316 | 240.8364 | 237.1587
3353.176 | 451.7313 | 239.676 | 241.4452 | 237.3222
3354.176 | 450.1041 | 239.935 | 241.7626 | 237.5549
3355.176 | 447.5675 | 240.3078 | 242.1505 | 237.8884
3356.176 | 447.5102 | 240.7514 | 242.8473 | 238.2562
3357.176 | 450.5167 | 240.8891 | 243.0268 | 238.4815
3358.176 | 452.9648 | 241.1353 | 243.7769 | 238.5946
3359.176 | 450.3172 | 241.6401 | 244.1474 | 238.881
3360.176 | 452.068 | 241.9335 | 244.33 | 239.0502
3361.176 | 450.7758 | 242.4268 | 244.7175 | 239.2107
3362.176 | 449.8043 | 242.7901 | 245.11 | 239.051
3363.176 | 450.5397 | 242.8259 | 245.551 | 239.1442
3364.176 | 449.224 | 243.2993 | 245.9606 | 239.0145
3365.176 | 448.0571 | 243.5742 | 246.1461 | 239.3227
3366.176 | 450.4243 | 243.5132 | 246.3748 | 239.3723
3367.176 | 448.4925 | 243.4556 | 246.5574 | 239.6474
3368.176 | 447.2853 | 243.7177 | 246.8351 | 239.6524
3369.176 | 451.3733 | 243.8665 | 247.057 | 239.7924
3370.176 | 455.0836 | 243.8426 | 247.3217 | 239.8775
3371.176 | 458.0913 | 244.0602 | 247.5699 | 239.8559
3372.176 | 457.5114 | 244.4818 | 247.9117 | 240.0725
3373.176 | 457.809 | 244.8711 | 247.9797 | 240.0938
3374.176 | 454.5861 | 244.965 | 248.0826 | 240.6416
3375.176 | 452.7944 | 244.9695 | 248.1545 | 241.3849
3376.176 | 455.5789 | 244.8858 | 248.2394 | 242.1516
3377.176 | 454.1358 | 244.8218 | 248.1804 | 242.6792
3378.176 | 459.111 | 244.9655 | 248.2366 | 242.8603
3379.176 | 465.882 | 244.8477 | 248.0462 | 242.876
3380.176 | 472.6181 | 245.1875 | 248.1773 | 243.2369
3381.176 | 473.4412 | 245.4518 | 248.1179 | 243.577
3382.176 | 478.0274 | 245.8227 | 248.3418 | 244.1968
3383.176 | 480.5503 | 246.365 | 248.7783 | 244.8788
3384.176 | 481.8141 | 246.9562 | 249.1881 | 245.1028
3385.176 | 484.0181 | 246.9802 | 249.5131 | 245.7612
3386.176 | 488.0171 | 247.0578 | 250.0406 | 246.3357
3387.176 | 488.8899 | 247.5732 | 250.2493 | 246.7508
3388.176 | 486.0651 | 248.0549 | 250.2693 | 247.2533
3389.176 | 482.6937 | 248.6596 | 250.3727 | 247.6337
3390.176 | 482.6056 | 249.3564 | 250.5159 | 248.6031
3391.176 | 481.919 | 249.8207 | 250.9331 | 249.0603
3392.176 | 484.2637 | 250.3729 | 251.4236 | 249.7482
3393.176 | 483.3297 | 250.6137 | 251.8379 | 249.9265
3394.176 | 483.3564 | 251.2314 | 252.4687 | 250.5196
3395.176 | 487.3451 | 251.9331 | 252.937 | 251.5648
3396.176 | 488.3002 | 252.774 | 253.2169 | 252.1724
3397.176 | 494.3332 | 253.2034 | 253.2831 | 252.7221
3398.176 | 503.6868 | 253.8312 | 253.8302 | 253.4809
3399.176 | 508.4405 | 254.8171 | 254.9847 | 253.7037
3400.176 | 511.7594 | 255.6132 | 255.2573 | 254.1398
3401.176 | 518.9405 | 256.6121 | 255.7886 | 255.1426
3402.176 | 523.2163 | 257.7306 | 256.3063 | 256.2145
3403.176 | 529.5435 | 258.3662 | 256.7816 | 257.4443
3404.176 | 535.2816 | 258.6054 | 256.9761 | 257.7003
3405.176 | 543.6322 | 259.0583 | 257.4102 | 258.3144
3406.176 | 552.6559 | 259.6066 | 257.6695 | 258.803
3407.176 | 550.6952 | 260.2038 | 258.6261 | 259.5695
3408.176 | 549.7894 | 260.7972 | 259.1113 | 260.2484
3409.176 | 545.5634 | 261.6268 | 259.5708 | 261.1998
3410.176 | 535.6743 | 261.9552 | 259.7592 | 261.7698
3411.176 | 529.7068 | 262.531 | 260.0582 | 262.5755
3412.176 | 526.9814 | 262.6624 | 260.6669 | 262.8411
3413.176 | 526.5889 | 263.0108 | 260.8156 | 262.7387
3414.176 | 521.5406 | 264.106 | 261.2134 | 262.3762
3415.176 | 519.1545 | 264.0447 | 261.6516 | 262.3395
3416.176 | 516.0524 | 264.7512 | 261.9956 | 262.2096
3417.176 | 515.6262 | 265.0656 | 262.2488 | 262.0225
3418.176 | 509.2109 | 266.095 | 262.3356 | 262.1558
3419.176 | 510.425 | 266.5703 | 262.6083 | 262.3618
3420.176 | 515.9613 | 266.6599 | 262.629 | 262.5235
3421.176 | 516.5772 | 266.6053 | 262.6738 | 262.2417
3422.176 | 512.0662 | 266.7278 | 262.7332 | 262.1601
3423.176 | 511.8571 | 266.8987 | 262.9717 | 262.6699
3424.176 | 517.5469 | 267.2528 | 262.8011 | 263.5119
3425.176 | 518.0375 | 267.1721 | 262.9163 | 263.8519
3426.176 | 516.2718 | 266.9899 | 262.8364 | 263.8306
3427.176 | 509.2691 | 266.8899 | 262.7999 | 264.2066
3428.176 | 507.1651 | 266.6943 | 262.9006 | 264.4789
3429.176 | 508.7218 | 267.1227 | 262.8823 | 264.3414
3430.176 | 518.0169 | 267.2337 | 263.0965 | 264.6762
3431.176 | 514.44 | 267.7136 | 263.3667 | 265.0097
3432.176 | 516.0379 | 267.9653 | 263.5023 | 265.7255
3433.176 | 523.666 | 268.4669 | 263.7934 | 265.727
3434.176 | 527.3687 | 268.7975 | 264.2388 | 265.9563
3435.176 | 530.9598 | 269.2721 | 264.3874 | 266.1791
3436.176 | 539.1517 | 269.0113 | 264.7215 | 266.2974
3437.176 | 545.2278 | 269.0464 | 265.0093 | 266.5754
3438.176 | 544.7512 | 268.4807 | 265.0271 | 266.7434
3439.176 | 534.8615 | 268.9709 | 264.9388 | 266.4724
3440.176 | 539.323 | 269.1078 | 264.7264 | 266.0745
3441.176 | 543.179 | 269.5315 | 264.7069 | 266.1251
3442.176 | 544.2889 | 269.9064 | 264.7129 | 266.6431
3443.176 | 549.6032 | 269.3004 | 265.0625 | 266.8104
3444.176 | 557.5768 | 269.9608 | 265.2474 | 266.88
3445.176 | 560.023 | 270.5605 | 265.6071 | 267.227
3446.176 | 564.7127 | 271.779 | 266.542 | 267.3704
3447.176 | 567.9285 | 271.882 | 266.6606 | 267.7491
3448.176 | 573.9517 | 271.697 | 266.6538 | 268.2179
3449.176 | 571.2406 | 271.5523 | 266.649 | 268.3668
3450.176 | 581.1242 | 271.7151 | 266.7424 | 268.587
3451.176 | 570.4111 | 272.1063 | 266.817 | 268.5016
3452.176 | 567.8349 | 271.8376 | 267.2282 | 268.8425
3453.176 | 558.3191 | 271.6524 | 267.3402 | 269.1254
3454.176 | 550.0676 | 271.5096 | 267.509 | 269.4598
3455.176 | 556.2397 | 271.9942 | 268.2932 | 269.9043
3456.1917 | 557.1061 | 272.6963 | 268.9285 | 270.105
3457.1917 | 561.5197 | 273.3131 | 269.0683 | 270.0329
3458.1917 | 563.8733 | 274.0418 | 269.1451 | 270.1169
3459.176 | 565.0163 | 274.1297 | 269.1635 | 269.9929
3460.176 | 569.0101 | 274.6257 | 269.1537 | 270.6825
3461.176 | 570.5545 | 275.0358 | 269.1072 | 271.2036
3462.176 | 563.3382 | 274.5571 | 269.0908 | 270.8612
3463.176 | 552.0774 | 274.8053 | 269.5497 | 270.9278
3464.176 | 542.7962 | 275.6793 | 269.6504 | 270.8394
3465.176 | 535.5691 | 276.0859 | 270.0156 | 270.5161
3466.176 | 535.6316 | 276.9513 | 270.2065 | 270.6593
3467.176 | 541.2918 | 277.4394 | 270.4191 | 270.7917
3468.176 | 545.2028 | 278.3905 | 271.0201 | 271.2101
3469.176 | 552.483 | 278.591 | 271.2678 | 271.4505
3470.176 | 554.7865 | 279.0858 | 271.4075 | 271.7817
3471.176 | 554.0156 | 279.2916 | 271.2592 | 272.1338
3472.176 | 554.8122 | 278.9415 | 271.3106 | 272.4408
3473.176 | 555.8821 | 278.9385 | 271.1439 | 272.9236
3474.176 | 560.2772 | 279.0349 | 271.5701 | 272.9011
3475.176 | 556.6518 | 278.8181 | 271.9689 | 273.4364
3476.176 | 559.0417 | 279.2135 | 272.5092 | 274.4656
3477.176 | 562.4386 | 279.7914 | 272.7981 | 274.9967
3478.176 | 558.996 | 280.2775 | 273.2758 | 274.808
3479.176 | 558.5261 | 280.5394 | 273.6102 | 275.0081
3480.176 | 555.5615 | 280.5226 | 274.0247 | 275.1296
3481.176 | 556.3254 | 280.7809 | 275.0922 | 275.4287
3482.176 | 555.7378 | 280.8561 | 274.9722 | 276.0963
3483.176 | 556.9754 | 281.0179 | 275.2671 | 276.0977
3484.176 | 558.3018 | 281.0223 | 276.0834 | 276.1192
3485.176 | 563.7892 | 281.2952 | 275.7062 | 276.1111
3486.176 | 568.5965 | 281.0535 | 275.5672 | 276.415
3487.176 | 565.5648 | 281.2457 | 275.4128 | 276.2559
3488.176 | 568.4823 | 281.5324 | 275.435 | 276.4243
3489.176 | 567.444 | 281.5878 | 275.7294 | 276.1534
3490.176 | 559.4268 | 282.3357 | 275.8566 | 275.8847
3491.176 | 553.1519 | 282.0244 | 275.9342 | 275.8716
3492.176 | 555.2176 | 282.0421 | 276.1449 | 275.8879
3493.176 | 554.1172 | 282.0347 | 276.2792 | 276.0912
3494.176 | 554.6567 | 281.8661 | 276.1278 | 276.2238
3495.176 | 551.5352 | 281.9666 | 276.0964 | 276.5062
3496.176 | 546.1607 | 282.6457 | 276.2893 | 276.9326
3497.176 | 540.7484 | 282.8114 | 276.0407 | 277.9797
3498.176 | 549.7473 | 283.3574 | 276.2097 | 278.926
3499.176 | 559.961 | 283.9865 | 276.3938 | 279.2069
3500.176 | 565.9235 | 284.4682 | 276.7634 | 278.9088
3501.176 | 562.9686 | 284.8328 | 276.9642 | 278.6012
3502.176 | 555.9279 | 284.9451 | 277.4176 | 278.9255
3503.176 | 555.2959 | 285.0875 | 277.5743 | 279.3593
3504.176 | 558.818 | 285.0056 | 277.8082 | 279.8556
3505.176 | 560.0342 | 285.3118 | 277.7729 | 280.099
3506.176 | 556.7988 | 285.1226 | 277.8432 | 280.1334
3507.176 | 559.0658 | 285.603 | 277.9905 | 280.4187
3508.176 | 560.4985 | 285.2313 | 278.2799 | 280.7285
3509.176 | 562.5195 | 285.2366 | 278.3871 | 280.9686
3510.176 | 572.7119 | 285.5486 | 278.3874 | 281.1187
3511.176 | 577.4072 | 285.4728 | 278.4555 | 281.5925
3512.176 | 577.044 | 285.2614 | 278.5562 | 282.3359
3513.176 | 574.5133 | 285.8461 | 279.0953 | 282.3018
3514.176 | 569.465 | 286.0581 | 279.4943 | 282.1497
3515.176 | 568.8791 | 286.1149 | 279.4918 | 282.079
3516.176 | 571.4347 | 286.283 | 279.5504 | 282.1622
3517.176 | 579.0682 | 286.2145 | 279.4368 | 282.4783
3518.176 | 576.1048 | 286.2843 | 279.3225 | 282.5668
3519.176 | 574.5271 | 286.5871 | 279.3125 | 283.6141
3520.176 | 578.3817 | 286.9315 | 279.4502 | 283.645
3521.176 | 576.041 | 287.3244 | 279.4794 | 283.7752
3522.176 | 577.6378 | 287.3823 | 280.0641 | 283.7948
3523.176 | 579.7021 | 287.964 | 280.0849 | 283.8839
3524.176 | 578.1573 | 288.1743 | 280.4793 | 284.2995
3525.176 | 575.4511 | 288.0818 | 280.6325 | 284.633
3526.176 | 579.5454 | 288.1105 | 280.6241 | 285.0515
3527.176 | 575.4918 | 287.9964 | 281.0392 | 284.9698
3528.176 | 572.5328 | 288.975 | 281.1482 | 284.901
3529.176 | 571.223 | 288.4145 | 281.1702 | 285.0129
3530.176 | 565.8329 | 288.9187 | 281.151 | 285.3
3531.176 | 563.6533 | 289.0836 | 281.1034 | 285.4086
3532.176 | 563.9589 | 289.3556 | 281.095 | 285.2596
3533.176 | 572.043 | 289.7189 | 281.0841 | 285.3327
3534.176 | 577.2665 | 289.8266 | 281.1498 | 284.9747
3535.176 | 586.008 | 290.2152 | 281.2152 | 285.123
3536.176 | 590.3935 | 290.2528 | 281.6772 | 285.3214
3537.176 | 595.8855 | 290.2668 | 281.6783 | 285.0468
3538.176 | 603.4255 | 290.23 | 281.8047 | 285.1716
3539.176 | 609.1777 | 290.6495 | 281.7582 | 286.3162
3540.176 | 617.588 | 290.9593 | 281.6689 | 286.3922
3541.176 | 626.5941 | 291.2137 | 282.8544 | 287.1123
3542.176 | 631.7518 | 291.3637 | 282.8717 | 287.0886
3543.176 | 627.5463 | 291.3462 | 283.0083 | 287.3795
3544.176 | 631.7291 | 291.3366 | 282.8649 | 287.6614
3545.176 | 636.0894 | 291.0933 | 282.9024 | 287.9618
3546.176 | 642.4957 | 291.428 | 283.3228 | 287.8703
3547.176 | 649.9311 | 291.5181 | 283.399 | 287.548
3548.176 | 647.5706 | 291.2745 | 283.9653 | 287.8998
3549.176 | 649.3011 | 291.1952 | 283.8985 | 287.7353
3550.176 | 652.844 | 291.4151 | 283.8411 | 288.0166
3551.176 | 647.0606 | 291.5401 | 283.7234 | 287.8355
3552.176 | 649.3729 | 291.2245 | 284.0262 | 288.1098
3553.176 | 648.7918 | 291.8788 | 284.8743 | 288.2078
3554.176 | 639.2814 | 292.1588 | 284.8702 | 288.0147
3555.176 | 634.1031 | 292.9682 | 284.845 | 287.1232
3556.176 | 630.1263 | 293.2172 | 284.9976 | 286.8355
3557.176 | 621.7983 | 293.6195 | 284.6475 | 286.3809
3558.176 | 615.8483 | 293.6888 | 285.0307 | 286.2155
3559.176 | 615.6076 | 293.994 | 285.2377 | 285.6579
3560.176 | 608.653 | 294.0728 | 285.4413 | 285.7276
3561.176 | 606.6615 | 294.6359 | 285.4514 | 286.2558
3562.176 | 620.9905 | 294.8171 | 285.779 | 287.1242
3563.176 | 626.7736 | 295.175 | 286.1884 | 287.9225
3564.176 | 629.8305 | 295.5036 | 287.3665 | 288.0611
3565.176 | 629.064 | 295.5398 | 287.2481 | 288.5058
3566.176 | 626.2553 | 295.4193 | 287.0746 | 288.0909
3567.176 | 623.2088 | 295.4562 | 287.0857 | 287.6234
3568.176 | 628.4706 | 295.9723 | 287.4391 | 287.68
3569.176 | 629.9773 | 296.4375 | 287.4225 | 288.0547
3570.176 | 636.9881 | 296.5504 | 287.1745 | 287.888
3571.176 | 636.0538 | 296.2885 | 287.2437 | 287.8496
3572.176 | 643.0372 | 296.6943 | 287.8339 | 288.3779
3573.176 | 644.4463 | 296.7013 | 288.3039 | 288.2972
3574.176 | 645.5608 | 296.6841 | 288.647 | 288.6474
3575.176 | 642.2507 | 296.8601 | 289.0443 | 288.5891
3576.176 | 642.5365 | 297.0955 | 289.0429 | 289.1261
3577.176 | 639.2716 | 296.8495 | 289.6411 | 289.6357
3578.176 | 640.7694 | 297.0082 | 289.9941 | 289.9731
3579.176 | 641.8917 | 296.6655 | 289.8331 | 290.6376
3580.176 | 636.8936 | 296.5438 | 289.8219 | 291.6092
3581.176 | 635.6275 | 296.5853 | 290.9126 | 292.0856
3582.176 | 642.6266 | 296.652 | 290.8343 | 292.1563
3583.176 | 644.6901 | 297.0025 | 290.7922 | 292.6848
3584.176 | 647.9028 | 297.1923 | 291.175 | 293.0357
3585.176 | 650.4435 | 297.297 | 291.2321 | 293.1825
3586.176 | 652.7264 | 297.6307 | 291.4166 | 293.4128
3587.176 | 654.8689 | 297.8958 | 291.863 | 293.4264
3588.176 | 652.2655 | 297.8449 | 292.3857 | 293.1698
3589.176 | 645.8408 | 297.1243 | 292.4187 | 293.0699
3590.176 | 646.363 | 297.4886 | 292.4782 | 293.368
3591.176 | 647.784 | 297.6833 | 293.334 | 293.3629
3592.176 | 651.804 | 298.1914 | 293.7622 | 294.0215
3593.176 | 649.6042 | 298.8918 | 294.3359 | 294.0005
3594.176 | 656.0771 | 299.244 | 294.132 | 294.0856
3595.176 | 653.2323 | 299.6693 | 294.4282 | 293.6982
3596.176 | 648.3688 | 299.9639 | 294.5642 | 293.8742
3597.176 | 659.6072 | 300.483 | 295.2173 | 293.7831
3598.176 | 661.4834 | 301.0382 | 295.5919 | 293.7763
3599.176 | 660.1586 | 301.8275 | 295.7037 | 293.4965
3600.176 | 667.5772 | 302.5991 | 296.8028 | 293.8463
3601.176 | 679.133 | 303.2027 | 296.4902 | 294.4455
3602.176 | 685.7969 | 304.472 | 296.3234 | 294.8381
3603.176 | 679.2024 | 305.196 | 296.976 | 295.4799
3604.176 | 675.8097 | 306.3755 | 297.1896 | 295.6124
3605.176 | 674.9487 | 306.8698 | 297.4505 | 295.7514
3606.176 | 677.7551 | 307.9367 | 297.6122 | 296.023
3607.176 | 684.183 | 308.128 | 299.0474 | 296.3221
3608.176 | 684.5391 | 308.5629 | 299.3403 | 297.2752
3609.176 | 686.9945 | 308.3838 | 299.7455 | 297.7469
3610.176 | 690.2229 | 308.6045 | 300.1728 | 298.1774
3611.176 | 686.244 | 308.7048 | 300.7165 | 298.1445
3612.176 | 683.6614 | 309.5341 | 301.1621 | 298.7324
3613.176 | 680.5941 | 309.7866 | 301.555 | 298.9085
3614.176 | 683.218 | 310.1157 | 301.7487 | 299.189
3615.176 | 685.5392 | 310.2263 | 301.4695 | 299.1357
3616.176 | 687.0467 | 310.428 | 301.313 | 299.2969
3617.176 | 684.5477 | 310.2504 | 301.1028 | 299.7702
3618.176 | 686.4781 | 310.1081 | 300.7996 | 300.3325
3619.176 | 687.4744 | 309.8543 | 300.6685 | 300.522
3620.176 | 688.7481 | 309.906 | 300.78 | 300.5496
3621.176 | 686.5886 | 309.8158 | 300.462 | 300.1486
3622.176 | 686.6961 | 310.4249 | 300.4254 | 300.6428
3623.176 | 684.1115 | 311.0613 | 301.5569 | 301.0134
3624.176 | 681.5268 | 311.0823 | 301.6545 | 302.0171
3625.176 | 675.7183 | 311.3625 | 301.706 | 303.0134
3626.176 | 672.4226 | 311.6408 | 301.5766 | 303.8162
3627.176 | 674.8701 | 311.8674 | 302.1274 | 304.0759
3628.176 | 663.0319 | 311.6929 | 301.9546 | 303.6214
3629.176 | 665.3275 | 311.5894 | 302.0317 | 303.2095
3630.176 | 668.4974 | 312.9355 | 302.3538 | 303.1184
3631.176 | 673.0116 | 313.617 | 302.7271 | 303.0279
3632.176 | 679.1265 | 314.1261 | 302.7693 | 303.2543
3633.176 | 682.5138 | 314.3836 | 303.0497 | 303.4603
3634.176 | 685.8839 | 314.4329 | 303.7498 | 304.0542
3635.176 | 684.4462 | 314.2502 | 303.9518 | 304.5853
3636.176 | 682.1312 | 314.3395 | 303.8069 | 303.8067
3637.176 | 680.7715 | 314.6093 | 304.0053 | 304.0528
3638.176 | 679.3949 | 314.8888 | 304.4461 | 303.9837
3639.176 | 669.0628 | 315.9416 | 304.599 | 304.3723
3640.176 | 656.8006 | 316.3782 | 304.8766 | 304.7647
3641.176 | 653.7539 | 317.1304 | 305.53 | 304.5261
3642.176 | 648.3697 | 317.9207 | 306.217 | 305.5317
3643.176 | 644.3329 | 318.0081 | 306.6106 | 305.5068
3644.176 | 646.5713 | 317.9551 | 307.0579 | 305.1364
3645.176 | 644.3288 | 318.1839 | 307.4326 | 304.8854
3646.176 | 645.5414 | 318.3354 | 308.1522 | 304.8891
3647.176 | 647.3367 | 319.5686 | 308.5489 | 305.0264
3648.176 | 649.5877 | 320.3926 | 308.8328 | 305.9656
3649.176 | 656.3356 | 320.8394 | 309.2517 | 306.2151
3650.176 | 660.9691 | 321.3407 | 309.9546 | 306.4613
3651.176 | 669.4203 | 321.6078 | 310.1795 | 306.1269
3652.176 | 672.613 | 322.0792 | 310.571 | 306.69
3653.176 | 678.1177 | 321.7284 | 311.0118 | 307.263
3654.176 | 675.4389 | 321.79 | 311.649 | 307.756
3655.176 | 673.4284 | 321.7543 | 312.391 | 307.7909
3656.176 | 672.7856 | 321.8486 | 312.9486 | 308.3565
3657.176 | 677.6663 | 321.7249 | 313.8249 | 308.4855
3658.176 | 676.6416 | 321.8656 | 314.3508 | 308.3205
3659.176 | 675.988 | 322.453 | 314.938 | 308.7774
3660.176 | 678.4002 | 322.697 | 315.1273 | 309.5349
3661.176 | 679.3904 | 322.7144 | 315.3448 | 310.276
3662.176 | 679.8613 | 322.6508 | 315.4554 | 310.4393
3663.176 | 677.4421 | 322.8336 | 315.9997 | 310.7627
3664.176 | 672.1321 | 323.3013 | 316.1867 | 311.4083
3665.176 | 675.7945 | 323.6426 | 316.1101 | 311.9842
3666.176 | 679.3566 | 324.0313 | 316.4109 | 311.8944
3667.176 | 681.6804 | 324.5262 | 316.7038 | 311.6387
3668.176 | 681.2254 | 325.3258 | 316.7718 | 312.1468
3669.176 | 683.3739 | 325.8613 | 317.2248 | 312.1047
3670.176 | 682.9477 | 326.6278 | 317.4676 | 311.6413
3671.176 | 685.378 | 326.5724 | 317.591 | 311.7464
3672.176 | 684.3721 | 326.5906 | 317.6777 | 311.6537
3673.176 | 682.1433 | 326.5592 | 318.1002 | 312.5621
3674.176 | 680.6471 | 326.9878 | 318.0265 | 312.8969
3675.176 | 682.1498 | 327.2097 | 318.2976 | 313.3614
3676.176 | 679.7554 | 327.4678 | 318.4079 | 313.286
3677.176 | 676.9818 | 328.0962 | 318.5662 | 314.3485
3678.176 | 677.494 | 328.2185 | 318.7526 | 314.5781
3679.176 | 680.5161 | 328.7366 | 319.6751 | 314.7287
3680.176 | 685.0867 | 328.7019 | 319.5406 | 315.053
3681.176 | 687.6066 | 328.4935 | 319.5814 | 315.0492
3682.176 | 684.6992 | 328.4108 | 320.2084 | 314.8922
3683.176 | 687.8409 | 328.7301 | 320.3811 | 314.9192
3684.176 | 689.6752 | 329.5844 | 320.422 | 314.7709
3685.176 | 690.8511 | 329.9185 | 320.4804 | 314.9383
3686.176 | 691.0044 | 330.1355 | 320.7719 | 315.4949
3687.176 | 692.0949 | 330.5048 | 321.3052 | 316.1995
3688.176 | 692.2877 | 330.5346 | 321.6082 | 316.6866
3689.176 | 691.2859 | 330.9119 | 322.1501 | 317.1547
3690.176 | 692.3371 | 331.8635 | 322.3471 | 316.9945
3691.176 | 694.4028 | 332.5968 | 323.0758 | 317.5624
3692.176 | 691.2119 | 333.2191 | 323.4403 | 318.2132
3693.176 | 697.9077 | 333.175 | 323.8258 | 318.5142
3694.176 | 699.9272 | 333.2676 | 324.1734 | 318.7308
3695.176 | 698.6779 | 333.6087 | 324.4003 | 319.2941
3696.176 | 695.7232 | 334.3329 | 324.643 | 319.6949
3697.176 | 694.8068 | 334.1904 | 324.7704 | 319.7243
3698.176 | 689.3297 | 334.5314 | 324.8848 | 319.666
3699.176 | 684.433 | 334.7259 | 325.3443 | 319.8933
3700.176 | 682.0156 | 334.9407 | 325.8333 | 319.7339
3701.176 | 685.9544 | 335.6747 | 326.1722 | 320.1269
3702.176 | 687.4207 | 336.0371 | 326.2851 | 320.8331
3703.176 | 691.0705 | 336.5292 | 326.316 | 321.5046
3704.176 | 692.6586 | 336.8279 | 326.4682 | 322.2003
3705.176 | 690.8837 | 337.0388 | 326.1617 | 323.2756
3706.176 | 692.6512 | 337.2912 | 326.2734 | 323.4286
3707.176 | 691.0038 | 337.2367 | 326.7181 | 323.2615
3708.176 | 692.6683 | 337.7685 | 327.1846 | 323.7014
3709.176 | 693.9676 | 338.6088 | 327.4826 | 324.2059
3710.176 | 694.5404 | 339.1398 | 328.1334 | 324.3126
3711.176 | 693.4275 | 339.0888 | 328.6768 | 324.6818
3712.176 | 691.579 | 339.154 | 329.1768 | 325.4151
3713.176 | 681.0506 | 339.3004 | 330.3644 | 326.1301
3714.176 | 680.709 | 339.7019 | 330.7814 | 326.4032
3715.176 | 679.0515 | 340.7294 | 331.8684 | 326.6762
3716.176 | 681.0319 | 340.8119 | 332.209 | 327.0529
3717.176 | 683.8445 | 341.0102 | 332.2188 | 327.6779
3718.176 | 683.4068 | 341.3489 | 332.5277 | 328.0556
3719.176 | 682.3178 | 342.046 | 332.3462 | 328.3414
3720.176 | 685.739 | 342.6458 | 332.2979 | 329.1502
3721.176 | 685.0002 | 343.3348 | 332.3671 | 329.0747
3722.176 | 686.7272 | 343.5349 | 333.1129 | 330.0572
3723.176 | 692.2784 | 344.1535 | 333.7071 | 330.6925
3724.176 | 699.6752 | 344.3022 | 334.4148 | 330.9163
3725.176 | 702.6076 | 344.8383 | 335.2055 | 331.1768
3726.176 | 702.8294 | 345.0422 | 335.727 | 330.9649
3727.176 | 699.6125 | 345.3351 | 336.2814 | 331.0437
3728.176 | 694.5832 | 345.5947 | 336.8007 | 331.7856
3729.176 | 694.443 | 345.8531 | 337.4 | 332.213
3730.176 | 690.6312 | 345.8703 | 338.1149 | 333.3573
3731.176 | 687.893 | 345.8619 | 338.3256 | 333.2003
3732.176 | 688.8211 | 346.1491 | 338.4939 | 332.5919
3733.176 | 692.3305 | 346.707 | 338.633 | 332.9684
3734.176 | 694.18 | 347.6632 | 339.188 | 333.1929
3735.176 | 692.1112 | 347.816 | 339.8463 | 333.3971
3736.176 | 691.5464 | 348.2213 | 340.4873 | 334.0258
3737.176 | 688.7829 | 349.3638 | 341.748 | 334.3188
3738.176 | 686.9418 | 351.3095 | 342.4895 | 335.57
3739.176 | 687.0855 | 352.729 | 343.2491 | 335.7525
3740.176 | 686.4442 | 353.212 | 343.8129 | 336.2531
3741.176 | 686.229 | 353.7981 | 344.2636 | 336.3043
3742.176 | 690.9745 | 353.9309 | 344.6217 | 336.1508
3743.176 | 695.5706 | 354.4201 | 344.9205 | 336.8546
3744.176 | 691.4949 | 354.5985 | 345.7434 | 337.0014
3745.176 | 688.1403 | 354.6451 | 345.8472 | 337.411
3746.176 | 684.6536 | 354.8584 | 345.9749 | 338.3546
3747.176 | 676.1793 | 354.6573 | 346.11 | 339.1253
3748.176 | 673.2374 | 355.0606 | 346.4217 | 338.7527
3749.176 | 675.9857 | 355.0126 | 346.9844 | 340.4005
3750.176 | 680.2348 | 355.3524 | 347.3735 | 341.0649
3751.176 | 681.765 | 355.6162 | 347.7139 | 340.6867
3752.176 | 680.8528 | 356.0873 | 348.8375 | 340.433
3753.176 | 683.3837 | 356.1843 | 349.0798 | 341.0763
3754.176 | 686.9875 | 356.6748 | 349.5875 | 341.2659
3755.176 | 689.6965 | 357.4158 | 349.991 | 341.1863
3756.176 | 685.4636 | 357.9113 | 350.3695 | 342.0433
3757.176 | 687.4189 | 359.021 | 350.9313 | 343.261
3758.176 | 688.9285 | 359.8859 | 352.2576 | 343.5362
3759.176 | 690.3345 | 359.7407 | 352.8093 | 343.4687
3760.176 | 689.3874 | 360.2486 | 352.5804 | 343.4418
3761.176 | 686.105 | 359.8197 | 352.2575 | 342.6651
3762.176 | 680.851 | 359.388 | 351.684 | 342.0891
3763.176 | 680.0373 | 359.5134 | 351.5906 | 341.8333
3764.176 | 677.6666 | 359.4263 | 351.4541 | 341.9375
3765.176 | 678.0228 | 359.9142 | 351.3478 | 341.0337
3766.176 | 682.8352 | 359.7073 | 351.5343 | 340.3783
3767.176 | 684.6739 | 359.842 | 351.5968 | 340.3612
3768.176 | 689.2044 | 360.0175 | 351.812 | 340.7417
3769.176 | 689.7135 | 360.2686 | 352.0457 | 341.3864
3770.176 | 689.3784 | 359.819 | 352.2643 | 341.3809
3771.176 | 693.7775 | 359.8747 | 352.3303 | 341.2585
3772.176 | 696.5174 | 360.2139 | 352.4102 | 341.0129
3773.176 | 697.3092 | 360.3995 | 353.1036 | 341.7165
3774.176 | 698.3422 | 360.1908 | 353.6525 | 342.4414
3775.176 | 700.1919 | 360.1188 | 353.6646 | 342.9295
3776.176 | 700.5297 | 360.0509 | 353.7484 | 343.1882
3777.176 | 696.4197 | 359.6259 | 353.7754 | 342.8688
3778.176 | 694.2175 | 359.7724 | 354.0059 | 342.9492
3779.176 | 690.8736 | 359.6632 | 353.9087 | 343.5371
3780.176 | 687.5605 | 359.6906 | 354.1036 | 344.3871
3781.176 | 684.9381 | 359.6466 | 354.341 | 344.6417
3782.176 | 684.308 | 359.2989 | 354.1732 | 344.9587
3783.176 | 681.7561 | 359.0611 | 353.7802 | 345.1101
3784.176 | 684.0159 | 359.0168 | 353.5498 | 344.7902
3785.176 | 682.1743 | 359.2001 | 353.5897 | 344.8929
3786.176 | 683.6322 | 359.0986 | 353.893 | 344.5113
3787.176 | 683.4465 | 359.1765 | 354.7069 | 344.5717
3788.176 | 685.0844 | 359.3685 | 355.1373 | 344.397
3789.176 | 689.6793 | 359.6687 | 355.6899 | 344.3528
3790.176 | 689.3512 | 359.6059 | 355.7903 | 344.7261
3791.176 | 689.3305 | 359.8043 | 356.3711 | 345.1203
3792.176 | 690.4488 | 360.6765 | 356.7494 | 344.8254
3793.176 | 691.2893 | 361.073 | 357.0047 | 344.6801
3794.176 | 695.2471 | 361.4973 | 357.3235 | 345.213
3795.176 | 695.0385 | 362.232 | 357.3653 | 345.696
3796.176 | 694.491 | 362.3839 | 357.2017 | 345.8134
3797.176 | 694.6183 | 362.2775 | 357.1702 | 345.259
3798.176 | 693.3684 | 362.5757 | 356.9645 | 344.9918
3799.176 | 692.2901 | 362.7595 | 357.0291 | 345.1575
3800.176 | 690.4434 | 362.6356 | 356.7789 | 344.8168
3801.176 | 688.8584 | 362.5515 | 356.5457 | 345.2506
3802.176 | 691.2743 | 362.7376 | 356.3519 | 346.4077
3803.176 | 694.5358 | 363.3108 | 357.0548 | 346.9519
3804.176 | 695.6911 | 363.5724 | 357.5362 | 347.3957
3805.176 | 695.8008 | 363.9327 | 357.978 | 348.4029
3806.176 | 694.7199 | 364.2808 | 358.352 | 348.3991
3807.176 | 695.5973 | 365.1776 | 359.0977 | 348.5894
3808.176 | 693.4702 | 365.417 | 359.5294 | 349.3185
3809.176 | 690.9426 | 365.5531 | 359.4426 | 349.2314
3810.176 | 687.2547 | 365.6161 | 359.197 | 349.4382
3811.176 | 686.2407 | 365.8814 | 359.1473 | 349.148
3812.176 | 682.2638 | 365.8718 | 359.1491 | 349.5624
3813.176 | 686.6981 | 366.0296 | 359.3471 | 349.5189
3814.176 | 694.5686 | 366.0532 | 359.7361 | 350.4685
3815.176 | 694.7736 | 366.7994 | 360.2225 | 351.3866
3816.176 | 698.5174 | 367.3103 | 360.4489 | 351.5596
3817.176 | 699.5951 | 367.7994 | 360.7813 | 351.2602
3818.176 | 697.1645 | 367.9319 | 361.0375 | 350.876
3819.176 | 694.2749 | 368.6061 | 361.002 | 350.2877
3820.176 | 692.6189 | 369.0621 | 361.3126 | 350.0322
3821.176 | 691.7478 | 368.8892 | 361.5965 | 349.6384
3822.176 | 693.5593 | 368.7799 | 361.5302 | 349.1717
3823.176 | 694.4248 | 368.8353 | 361.6934 | 348.9778
3824.176 | 691.7411 | 368.88 | 361.7772 | 348.6038
3825.176 | 691.2795 | 368.9749 | 361.8717 | 348.7705
3826.176 | 689.864 | 369.4448 | 361.7519 | 348.8025
3827.176 | 685.985 | 369.5957 | 362.0261 | 349.4104
3828.176 | 686.7013 | 369.8979 | 362.5124 | 349.9294
3829.176 | 688.8367 | 369.7578 | 362.3283 | 350.3192
3830.176 | 690.0952 | 369.566 | 362.1293 | 350.2836
3831.176 | 689.4437 | 369.5299 | 362.3628 | 350.606
3832.176 | 687.4076 | 370.2504 | 362.8345 | 352.09
3833.176 | 687.0846 | 370.6344 | 363.85 | 352.2423
3834.176 | 691.0629 | 370.6935 | 363.7852 | 352.0565
3835.176 | 692.1977 | 371.0357 | 363.7704 | 352.4172
3836.176 | 687.2385 | 370.8639 | 363.4587 | 352.132
3837.176 | 685.3789 | 371.2089 | 363.0444 | 352.0417
3838.176 | 694.7241 | 371.5512 | 362.9972 | 352.0773
3839.176 | 703.5081 | 372.3746 | 363.121 | 351.9371
3840.176 | 702.6586 | 372.1712 | 363.5028 | 351.4319
3841.176 | 698.7183 | 371.726 | 363.7052 | 351.9072
3842.176 | 696.8062 | 371.5105 | 363.5049 | 352.3772
3843.176 | 695.1836 | 371.5232 | 363.4463 | 352.3388
3844.176 | 695.1152 | 372.0495 | 363.1524 | 352.0022
3845.176 | 698.4077 | 372.5234 | 363.1349 | 351.9412
3846.176 | 693.7243 | 373.6761 | 363.1191 | 351.6333
3847.176 | 693.7753 | 374.2487 | 363.3274 | 351.9484
3848.176 | 693.1105 | 374.4366 | 363.6221 | 352.9294
3849.176 | 689.9662 | 374.5631 | 363.9612 | 353.1562
3850.176 | 688.5353 | 375.1419 | 364.6045 | 353.9889
3851.176 | 685.7447 | 375.8569 | 365.1723 | 354.6535
3852.176 | 683.8938 | 375.6682 | 365.7904 | 354.9718
3853.176 | 682.5279 | 376.0907 | 366.6681 | 355.258
3854.176 | 682.0843 | 376.5057 | 367.1152 | 355.3356
3855.176 | 686.1288 | 376.6501 | 367.3545 | 355.66
3856.176 | 687.1405 | 377.5479 | 369.1018 | 356.0203
3857.176 | 682.9765 | 377.3258 | 369.1656 | 356.5914
3858.176 | 680.0651 | 377.3256 | 368.8685 | 357.3379
3859.176 | 681.8031 | 377.8671 | 368.7804 | 358.0875
3860.176 | 683.8615 | 377.9913 | 369.2102 | 358.1401
3861.176 | 684.9162 | 378.1424 | 369.2448 | 358.4311
3862.176 | 685.6226 | 378.2322 | 369.1972 | 358.4769
3863.176 | 688.8855 | 378.4052 | 369.1979 | 358.6743
3864.176 | 687.547 | 378.2099 | 369.1941 | 358.7467
3865.176 | 688.2856 | 377.846 | 369.3326 | 358.4938
3866.176 | 686.1871 | 377.8633 | 369.369 | 358.5512
3867.176 | 685.7274 | 378.0272 | 369.2972 | 358.6833
3868.176 | 687.487 | 378.1065 | 369.2322 | 358.4267
3869.176 | 684.7344 | 377.8367 | 369.2152 | 358.833
3870.176 | 682.5089 | 377.9722 | 369.3239 | 359.4483
3871.176 | 679.8739 | 377.9568 | 369.382 | 360.5007
3872.176 | 680.291 | 378.018 | 369.5139 | 360.0827
3873.176 | 685.2507 | 378.3854 | 369.5896 | 360.2679
3874.176 | 688.3569 | 378.6319 | 369.7143 | 360.0649
3875.176 | 687.9659 | 378.7471 | 369.6265 | 360.7016
3876.176 | 684.335 | 379.0803 | 369.6919 | 360.2629
3877.176 | 682.0726 | 379.4141 | 369.9512 | 360.8051
3878.176 | 682.4267 | 379.4379 | 370.1548 | 361.2535
3879.176 | 682.8153 | 379.9585 | 370.6096 | 361.8011
3880.176 | 680.8071 | 380.0019 | 371.0804 | 361.7258
3881.176 | 675.9576 | 380.4085 | 371.4435 | 361.6417
3882.176 | 674.1086 | 381.5346 | 371.5382 | 361.9013
3883.176 | 671.348 | 381.7196 | 371.7276 | 361.6846
3884.176 | 671.0598 | 382.1008 | 371.9837 | 362.0205
3885.176 | 674.5443 | 382.5333 | 372.5579 | 362.5546
3886.176 | 671.1722 | 382.8242 | 373.0374 | 363.0476
3887.176 | 671.9416 | 383.2446 | 373.3789 | 363.5741
3888.176 | 674.3475 | 383.5105 | 373.4056 | 364.8951
3889.176 | 673.2197 | 384.3332 | 373.0262 | 364.9203
3890.176 | 669.0271 | 385.3827 | 373.3624 | 365.6275
3891.176 | 667.1104 | 385.8649 | 373.7676 | 365.5662
3892.176 | 667.9281 | 386.3637 | 374.1791 | 366.106
3893.176 | 669.0205 | 387.2248 | 374.3877 | 365.8304
3894.176 | 667.3593 | 386.8815 | 375.7815 | 365.9059
3895.176 | 669.3625 | 386.9537 | 376.0463 | 365.5953
3896.176 | 670.1006 | 387.3075 | 376.1085 | 366.0629
3897.176 | 671.4938 | 387.4928 | 376.348 | 365.8946
3898.176 | 672.2819 | 387.5855 | 376.3958 | 366.0388
3899.176 | 675.2564 | 387.3036 | 376.254 | 365.9329
3900.176 | 678.6795 | 387.5478 | 376.2473 | 365.8939
3901.176 | 681.7127 | 388.0771 | 376.6353 | 366.0048
3902.176 | 680.6528 | 388.3445 | 376.9338 | 366.3884
3903.176 | 679.158 | 388.7666 | 377.37 | 367.1265
3904.176 | 675.2932 | 389.2299 | 377.6922 | 367.6168
3905.176 | 674.506 | 389.4629 | 377.5477 | 367.7759
3906.176 | 674.2782 | 389.2692 | 377.6678 | 367.9519
3907.176 | 674.9772 | 390.7372 | 378.297 | 368.5522
3908.176 | 676.2704 | 391.0106 | 378.6276 | 368.878
3909.176 | 678.1588 | 391.0447 | 378.7998 | 369.3276
3910.176 | 676.3299 | 390.9053 | 378.8827 | 369.9811
3911.176 | 676.1056 | 391.0351 | 379.3886 | 370.9418
3912.176 | 675.6151 | 391.5243 | 379.6552 | 371.3778
3913.176 | 674.6462 | 391.489 | 379.6878 | 371.407
3914.176 | 673.1276 | 391.691 | 379.8113 | 371.4165
3915.176 | 672.1049 | 391.8051 | 380.3564 | 371.9346
3916.176 | 671.4765 | 392.7307 | 380.9699 | 372.5225
3917.176 | 669.569 | 393.4355 | 381.3568 | 373.3558
3918.176 | 665.3973 | 394.3576 | 382.2308 | 373.8084
3919.176 | 662.9224 | 394.7976 | 383.0208 | 374.5706
3920.176 | 659.1177 | 395.8597 | 384.1251 | 375.2393
3921.176 | 654.6324 | 396.5322 | 385.0264 | 375.5805
3922.176 | 651.0967 | 397.3493 | 385.9775 | 376.4883
3923.176 | 649.1538 | 397.9389 | 386.6959 | 376.1399
3924.176 | 643.1085 | 398.8173 | 387.0867 | 376.5316
3925.176 | 641.0913 | 399.4572 | 387.5709 | 377.0034
3926.176 | 640.297 | 399.9203 | 387.9008 | 376.8978
3927.176 | 638.5706 | 400.3363 | 388.3522 | 377.7597
3928.176 | 637.9032 | 401.1374 | 389.111 | 378.3442
3929.176 | 636.3062 | 401.9369 | 389.6586 | 379.1231
3930.176 | 635.9774 | 401.8376 | 390.2649 | 379.0814
3931.176 | 635.6762 | 401.8856 | 390.8855 | 379.0893
3932.176 | 636.2616 | 401.5524 | 390.9727 | 379.4933
3933.176 | 637.387 | 401.2009 | 391.1383 | 379.5603
3934.176 | 638.2327 | 401.582 | 391.3899 | 380.4371
3935.176 | 638.8518 | 401.8621 | 391.6893 | 380.5215
3936.176 | 637.246 | 402.6992 | 391.9572 | 380.0382
3937.176 | 639.6101 | 403.8452 | 392.4437 | 380.215
3938.176 | 640.7484 | 405.3875 | 393.4428 | 380.1769
3939.176 | 644.571 | 405.7175 | 394.487 | 380.7263
3940.176 | 646.3756 | 405.3815 | 395.1163 | 381.6127
3941.176 | 647.7865 | 404.9693 | 395.5 | 381.5109
3942.176 | 648.1817 | 404.9043 | 395.571 | 381.5001
3943.176 | 648.5306 | 404.9857 | 395.5343 | 381.4972
3944.176 | 646.4039 | 405.3055 | 395.3902 | 382.1565
3945.176 | 648.7985 | 405.4331 | 395.6695 | 383.4243
3946.176 | 651.188 | 406.2656 | 396.268 | 383.4548
3947.176 | 651.8303 | 407.2567 | 396.614 | 383.7171
3948.176 | 653.5035 | 407.4642 | 396.563 | 383.1971
3949.176 | 654.0062 | 407.9205 | 396.6895 | 383.4871
3950.176 | 650.6468 | 408.9792 | 396.9102 | 383.5175
3951.176 | 649.6417 | 409.2254 | 397.4314 | 383.9157
3952.176 | 651.3505 | 409.2303 | 398.1991 | 384.2537
3953.176 | 649.5742 | 408.8891 | 398.4957 | 384.6462
3954.176 | 650.1397 | 409.3998 | 399.1775 | 384.9602
3955.176 | 649.5194 | 409.542 | 399.2024 | 385.1752
3956.176 | 649.6478 | 409.8297 | 399.4143 | 385.4935
3957.176 | 650.3195 | 409.3083 | 399.5644 | 385.6026
3958.176 | 654.5826 | 409.0382 | 399.4968 | 385.2511
3959.176 | 659.3596 | 409.3312 | 399.494 | 384.8183
3960.176 | 665.9939 | 410.1271 | 399.8947 | 385.1007
3961.176 | 668.7658 | 410.0521 | 400.4899 | 385.6586
3962.176 | 669.3331 | 409.8586 | 400.5457 | 385.4058
3963.176 | 668.6744 | 409.7382 | 400.5189 | 385.4034
3964.176 | 669.1812 | 409.3832 | 400.6203 | 386.5396
3965.176 | 664.1272 | 409.357 | 400.5986 | 386.8831
3966.176 | 660.9994 | 409.1348 | 400.5114 | 386.5459
3967.176 | 656.3229 | 408.8654 | 400.4238 | 387.0285
3968.176 | 655.3709 | 408.6719 | 400.4475 | 386.7599
3969.176 | 655.3197 | 408.5389 | 400.1937 | 386.8198
3970.176 | 654.8853 | 408.004 | 400.0584 | 386.4774
3971.176 | 655.4057 | 407.4655 | 399.9115 | 386.0651
3972.176 | 656.3442 | 407.4324 | 399.8079 | 387.753
3973.176 | 654.8831 | 407.5758 | 399.8791 | 387.9621
3974.176 | 653.4829 | 407.5573 | 399.6737 | 387.5596
3975.176 | 654.6304 | 407.654 | 401.1653 | 386.8799
3976.176 | 654.1069 | 408.3122 | 400.878 | 386.3404
3977.176 | 659.5791 | 409.011 | 400.823 | 386.112
3978.176 | 662.7953 | 409.1761 | 400.6315 | 386.2155
3979.176 | 668.3079 | 409.0257 | 400.4652 | 386.2961
3980.176 | 668.9236 | 409.2215 | 400.2556 | 386.6966
3981.176 | 669.2199 | 408.9919 | 399.9502 | 386.6109
3982.176 | 667.256 | 409.3401 | 399.8337 | 387.0822
3983.176 | 668.7824 | 409.5464 | 399.5221 | 387.2445
3984.176 | 667.0474 | 409.8962 | 399.4173 | 387.5164
3985.176 | 665.2717 | 409.9567 | 399.1201 | 388.7187
3986.176 | 660.9115 | 409.4245 | 398.863 | 388.2698
3987.176 | 661.0382 | 409.0323 | 398.8112 | 388.6084
3988.176 | 660.5507 | 408.7297 | 399.0934 | 388.6944
3989.176 | 662.1252 | 409.1043 | 399.133 | 388.5731
3990.176 | 662.3381 | 409.2896 | 399.2524 | 388.1677
3991.176 | 667.3044 | 409.2207 | 399.525 | 387.9687
3992.176 | 668.2077 | 409.2026 | 399.67 | 388.0765
3993.176 | 672.2847 | 409.4227 | 399.7072 | 387.503
3994.176 | 671.937 | 410.0573 | 399.8369 | 386.8844
3995.176 | 670.4406 | 410.5148 | 399.5759 | 386.419
3996.176 | 668.7398 | 410.9248 | 399.5037 | 386.1207
3997.176 | 664.9834 | 410.6834 | 399.119 | 385.6371
3998.176 | 664.2907 | 410.5675 | 398.9404 | 385.1135
3999.176 | 665.3691 | 410.4098 | 398.9704 | 384.7447
4000.176 | 668.623 | 410.2814 | 398.8881 | 385.107
4001.176 | 666.6642 | 410.3435 | 398.9858 | 386.3888
4002.176 | 661.4457 | 410.6293 | 399.315 | 387.1718
4003.176 | 660.5808 | 411.6344 | 399.6115 | 387.3704
4004.176 | 661.7065 | 411.7483 | 400.018 | 387.9137
4005.176 | 662.3944 | 411.7081 | 400.0217 | 387.9258
4006.176 | 662.9876 | 411.8498 | 399.9852 | 387.6838
4007.176 | 661.3292 | 411.1103 | 400.0298 | 388.2485
4008.176 | 660.9462 | 410.9098 | 400.057 | 388.0006
4009.176 | 661.6595 | 411.5571 | 400.7743 | 387.7441
4010.176 | 662.2349 | 411.9876 | 401.3339 | 387.9142
4011.176 | 656.3863 | 411.9507 | 401.4033 | 388.5759
4012.176 | 657.977 | 411.5017 | 401.537 | 388.9348
4013.176 | 657.2654 | 411.1042 | 401.5642 | 388.9645
4014.176 | 658.384 | 410.5788 | 401.4498 | 388.7511
4015.176 | 654.6372 | 410.1094 | 401.5592 | 388.8044
4016.176 | 653.5001 | 410.2469 | 401.7588 | 388.6036
4017.176 | 653.1868 | 410.7697 | 401.8552 | 388.474
4018.176 | 651.8547 | 411.237 | 402.0438 | 388.5865
4019.176 | 649.8052 | 411.6731 | 402.5298 | 388.6959
4020.176 | 657.461 | 411.8424 | 402.8729 | 388.7627
4021.176 | 666.1744 | 412.2124 | 403.3427 | 389.205
4022.176 | 673.5593 | 413.1793 | 404.7724 | 389.3753
4023.176 | 680.7776 | 413.892 | 407.2364 | 389.8962
4024.176 | 680.8119 | 414.85 | 408.3883 | 391.3082
4025.176 | 676.45 | 415.6389 | 408.8211 | 392.6346
4026.176 | 676.7324 | 416.1325 | 409.098 | 393.4671
4027.176 | 682.959 | 416.318 | 409.1725 | 393.5073
4028.176 | 685.9134 | 416.5813 | 409.2216 | 393.2273
4029.176 | 687.378 | 417.0915 | 409.0466 | 393.3654
4030.176 | 685.7136 | 417.286 | 408.967 | 393.6421
4031.176 | 690.0167 | 417.2422 | 408.9263 | 393.4581
4032.176 | 687.7044 | 417.1723 | 408.6997 | 394.2781
4033.176 | 687.0726 | 416.9022 | 408.3904 | 394.0976
4034.176 | 686.3301 | 417.7884 | 408.209 | 393.9245
4035.176 | 685.4105 | 418.3717 | 408.3841 | 393.5374
4036.176 | 684.6696 | 418.9303 | 408.5498 | 393.0419
4037.176 | 689.6641 | 419.2962 | 408.7515 | 393.0818
4038.176 | 689.7823 | 420.2977 | 408.6836 | 393.0893
4039.176 | 686.2128 | 420.5344 | 408.7307 | 392.5431
4040.176 | 680.052 | 420.4439 | 408.4235 | 392.3874
4041.176 | 675.8506 | 420.2703 | 407.9997 | 392.0423
4042.176 | 680.3752 | 420.0398 | 407.5924 | 392.157
4043.176 | 678.672 | 420.3156 | 407.1692 | 391.7374
4044.176 | 676.9263 | 420.3891 | 407.0073 | 391.7307
4045.176 | 679.8132 | 420.1481 | 406.8998 | 391.6416
4046.176 | 678.2604 | 420.1814 | 407.1992 | 391.5968
4047.176 | 678.7173 | 419.8277 | 407.6448 | 391.8382
4048.176 | 682.0259 | 419.2819 | 407.7356 | 391.512
4049.176 | 681.2838 | 419.3223 | 407.5872 | 391.254
4050.176 | 677.6822 | 419.0709 | 407.5907 | 390.586
4051.176 | 678.1904 | 419.3562 | 407.3761 | 390.2858
4052.176 | 678.671 | 419.286 | 407.2162 | 391.7318
4053.176 | 674.3196 | 419.6839 | 407.3612 | 391.9131
4054.176 | 669.7891 | 420.5726 | 408.0371 | 392.2681
4055.176 | 662.1493 | 421.1185 | 409.1666 | 393.5914
4056.176 | 662.4892 | 421.7334 | 410.1066 | 394.3426
4057.176 | 658.8987 | 421.9588 | 410.8625 | 394.8781
4058.176 | 657.5678 | 422.3208 | 411.3063 | 394.9477
4059.176 | 663.073 | 422.5762 | 411.6659 | 395.7291
4060.176 | 665.4485 | 422.8439 | 412.1151 | 396.2431
4061.176 | 671.5872 | 422.7713 | 412.0976 | 396.6949
4062.176 | 672.7145 | 422.5497 | 412.2689 | 396.8336
4063.176 | 669.5218 | 422.6398 | 412.2069 | 397.2987
4064.176 | 670.6574 | 422.8279 | 412.1741 | 397.3177
4065.176 | 670.2109 | 422.6439 | 412.2422 | 397.6077
4066.176 | 667.7211 | 422.4372 | 412.0272 | 397.976
4067.176 | 666 | 422.15 | 412.2641 | 398.109
4068.176 | 664.0888 | 422.5677 | 412.4224 | 397.7514
4069.176 | 667.7804 | 422.2668 | 412.126 | 398.6781
4070.176 | 668.2636 | 422.299 | 411.8498 | 398.5121
4071.176 | 668.9514 | 422.4875 | 412.1442 | 397.9453
4072.176 | 669.8556 | 422.2763 | 412.014 | 397.3557
4073.176 | 670.7786 | 422.0778 | 411.9812 | 397.0674
4074.176 | 670.1771 | 422.091 | 411.7019 | 397.0232
4075.176 | 669.4944 | 422.2007 | 411.8544 | 396.8766
4076.176 | 669.8788 | 422.534 | 411.937 | 396.3947
4077.176 | 671.0697 | 422.8282 | 411.7994 | 396.0114
4078.176 | 670.7572 | 422.4275 | 411.4423 | 396.9877
4079.176 | 671.4096 | 422.1274 | 411.3674 | 397.1977
4080.176 | 669.542 | 422.0819 | 412.0883 | 397.368
4081.176 | 671.0172 | 422.4712 | 412.393 | 397.7847
4082.176 | 671.0298 | 422.854 | 412.5951 | 397.6634
4083.176 | 669.9573 | 423.1703 | 412.2238 | 397.6435
4084.176 | 667.6755 | 423.2349 | 411.9992 | 397.1906
4085.176 | 665.4668 | 423.1777 | 411.7281 | 397.066
4086.176 | 665.4093 | 422.8155 | 411.3073 | 397.2254
4087.176 | 662.1108 | 422.7834 | 411.2853 | 397.2626
4088.176 | 661.3034 | 422.5286 | 411.0986 | 397.4656
4089.176 | 661.7028 | 422.6842 | 411.3325 | 397.4738
4090.176 | 659.9209 | 423.2998 | 411.3766 | 397.2714
4091.176 | 661.7567 | 424.0843 | 411.5961 | 397.295
4092.176 | 664.2628 | 425.0525 | 411.946 | 397.4491
4093.176 | 664.9735 | 425.3493 | 412.592 | 398.0035
4094.176 | 666.6993 | 425.865 | 412.5062 | 397.8483
4095.176 | 669.3315 | 426.6579 | 412.7382 | 397.7491
4096.176 | 670.8744 | 426.4409 | 412.879 | 398.2924
4097.176 | 672.5025 | 425.9644 | 412.8137 | 398.2911
4098.176 | 673.5943 | 426.071 | 412.7339 | 398.2111
4099.176 | 673.6596 | 426.1241 | 413.2703 | 398.1026
4100.176 | 673.8576 | 425.9916 | 413.8171 | 398.4657
4101.176 | 674.9449 | 425.6783 | 413.7898 | 398.6879
4102.176 | 676.9039 | 425.5162 | 413.4545 | 398.4963
4103.176 | 680.3239 | 425.0517 | 413.4899 | 398.2723
4104.176 | 682.5993 | 424.703 | 413.9479 | 397.985
4105.176 | 685.8099 | 424.9662 | 414.544 | 398.0064
4106.176 | 685.3004 | 425.0361 | 414.9854 | 398.1903
4107.176 | 683.5933 | 424.6598 | 415.0855 | 398.7847
4108.176 | 683.5752 | 424.45 | 415.011 | 398.8689
4109.176 | 685.1682 | 424.6179 | 414.7956 | 398.5872
4110.176 | 683.9391 | 424.9632 | 415.1117 | 398.3952
4111.176 | 683.9923 | 425.5003 | 415.5003 | 399.1722
4112.176 | 683.8153 | 426.0127 | 416.0221 | 399.3339
4113.176 | 684.479 | 426.3667 | 416.146 | 399.9101
4114.176 | 682.504 | 426.7285 | 416.4944 | 400.6787
4115.176 | 679.7628 | 426.8594 | 416.7124 | 400.5372
4116.176 | 678.0478 | 427.2157 | 416.5524 | 400.5373
4117.176 | 676.2296 | 427.4279 | 416.4905 | 400.7153
4118.176 | 673.8494 | 427.6358 | 416.3195 | 400.896
4119.176 | 671.1137 | 428.0979 | 416.3839 | 401.0169
4120.176 | 667.5815 | 428.7516 | 416.2966 | 400.9002
4121.176 | 663.9861 | 429.5568 | 416.2525 | 401.4645
4122.176 | 660.1886 | 430.7845 | 416.3436 | 402.2965
4123.176 | 658.7508 | 431.5113 | 416.7323 | 403.403
4124.176 | 657.9688 | 431.6032 | 416.9302 | 403.6836
4125.176 | 657.8799 | 431.1286 | 416.5302 | 405.0827
4126.176 | 656.7352 | 431.0766 | 415.9028 | 405.4444
4127.176 | 657.1587 | 431.331 | 415.652 | 405.0992
4128.176 | 655.8959 | 431.6183 | 415.692 | 406.0637
4129.176 | 654.9213 | 431.9291 | 416.1644 | 407.2138
4130.176 | 655.9457 | 432.3997 | 416.6478 | 407.531
4131.176 | 657.8267 | 432.8286 | 417.2493 | 408.2149
4132.176 | 657.6278 | 433.1467 | 417.4403 | 407.9889
4133.176 | 660.1107 | 433.7932 | 417.661 | 408.2482
4134.176 | 661.0387 | 433.6676 | 417.8695 | 408.7037
4135.176 | 658.3285 | 433.6252 | 417.9678 | 408.3704
4136.176 | 658.9858 | 433.8281 | 417.6131 | 408.1668
4137.176 | 659.8219 | 434.1998 | 417.7074 | 408.744
4138.176 | 661.9155 | 434.7987 | 417.5568 | 408.3525
4139.176 | 664.0154 | 435.8804 | 417.6174 | 408.4038
4140.176 | 665.9052 | 435.5758 | 417.6233 | 409.0897
4141.176 | 668.8466 | 435.5139 | 417.6013 | 409.0911
4142.176 | 672.8255 | 435.0701 | 417.5449 | 410.2994
4143.176 | 675.5509 | 434.976 | 417.73 | 409.8965
4144.176 | 680.8168 | 435.7822 | 417.8613 | 410.0125
4145.176 | 685.648 | 435.414 | 418.2595 | 409.829
4146.176 | 691.3484 | 435.3366 | 418.8487 | 409.2792
4147.176 | 696.3857 | 436.2419 | 419.9453 | 410.3262
4148.176 | 699.8684 | 436.2945 | 420.5133 | 410.307
4149.176 | 703.7198 | 436.254 | 420.4821 | 410.3126
4150.176 | 707.6745 | 436.2083 | 420.6719 | 410.2121
4151.176 | 710.0716 | 436.3199 | 421.0769 | 409.83
4152.176 | 716.0848 | 436.5834 | 421.6089 | 409.4102
4153.176 | 720.8937 | 436.1536 | 422.1221 | 409.809
4154.176 | 723.5337 | 436.0978 | 422.534 | 409.8466
4155.176 | 725.0408 | 435.5904 | 422.8921 | 410.1615
4156.176 | 724.8604 | 435.4085 | 422.9875 | 410.8972
4157.176 | 722.74 | 435.1552 | 422.7529 | 411.2543
4158.176 | 721.0114 | 435.033 | 422.5846 | 411.966
4159.176 | 717.221 | 434.9926 | 422.5884 | 412.1401
4160.176 | 715.2437 | 434.6789 | 422.4276 | 412.4339
4161.176 | 713.5294 | 434.2305 | 422.1906 | 412.503
4162.176 | 710.7693 | 434.6348 | 422.3146 | 413.1304
4163.176 | 706.4603 | 434.6617 | 422.4277 | 413.9644
4164.176 | 703.6043 | 434.9059 | 422.646 | 414.4354
4165.176 | 701.639 | 435.2132 | 422.6156 | 415.9841
4166.176 | 700.1087 | 434.9741 | 422.7512 | 417.044
4167.176 | 699.0381 | 434.7358 | 423.4328 | 417.1103
4168.176 | 698.8414 | 434.7268 | 423.7454 | 417.1375
4169.176 | 695.4378 | 434.67 | 423.9969 | 416.8615
4170.176 | 693.4891 | 434.7497 | 424.1951 | 416.4989
4171.176 | 694.6874 | 434.5711 | 424.3881 | 416.2071
4172.176 | 695.4342 | 434.7961 | 424.5416 | 415.8469
4173.176 | 696.5292 | 434.8269 | 424.6818 | 415.834
4174.176 | 697.607 | 434.8221 | 424.5749 | 415.8378
4175.176 | 699.576 | 435.1332 | 424.2984 | 415.9253
4176.176 | 703.1965 | 435.4601 | 424.4737 | 415.8181
4177.176 | 704.7337 | 435.5543 | 424.9895 | 415.6136
4178.176 | 704.1045 | 435.8186 | 425.5475 | 415.921
4179.176 | 703.2429 | 436.0968 | 426.4172 | 416.9477
4180.176 | 699.318 | 436.6636 | 426.9498 | 417.9102
4181.176 | 697.6289 | 436.8668 | 427.223 | 418.1836
4182.176 | 697.1758 | 436.9326 | 427.2868 | 418.4395
4183.176 | 694.8478 | 436.7461 | 428.4421 | 418.1976
4184.176 | 691.5932 | 436.8672 | 429.9038 | 418.4673
4185.176 | 690.0111 | 437.0792 | 429.8373 | 418.5068
4186.176 | 688.08 | 436.9792 | 429.6617 | 418.3847
4187.176 | 687.5821 | 437.1769 | 429.8455 | 418.2994
4188.176 | 684.9924 | 437.4709 | 429.5606 | 418.7305
4189.176 | 679.3843 | 437.7014 | 429.6541 | 418.7379
4190.176 | 675.1399 | 437.7582 | 429.7263 | 418.6416
4191.176 | 672.8183 | 438.3005 | 430.127 | 418.4664
4192.176 | 672.0711 | 438.5379 | 430.3706 | 418.624
4193.176 | 671.2654 | 439.0065 | 430.6555 | 418.4597
4194.176 | 668.5651 | 439.4078 | 430.687 | 418.7389
4195.176 | 666.3093 | 439.6539 | 430.4689 | 419.3155
4196.176 | 665.5184 | 439.4783 | 430.6024 | 419.7812
4197.176 | 665.1227 | 439.584 | 430.4093 | 419.7533
4198.176 | 667.3534 | 439.7587 | 430.3548 | 420.8508
4199.176 | 668.7325 | 440.2216 | 430.3324 | 420.7
4200.176 | 667.9567 | 440.5728 | 430.6311 | 420.5766
4201.176 | 667.8698 | 440.9442 | 431.241 | 420.2831
4202.176 | 670.1067 | 441.1679 | 431.5832 | 420.4303
4203.1917 | 672.7377 | 441.1935 | 431.5818 | 419.8193
4204.176 | 674.4138 | 441.4158 | 432.402 | 419.4268
4205.176 | 675.0353 | 441.5838 | 432.4107 | 419.0852
4206.176 | 676.7593 | 441.7366 | 432.8694 | 419.5475
4207.176 | 677.5538 | 441.8291 | 433.0845 | 420.0373
4208.176 | 678.6748 | 442.1577 | 432.9458 | 420.218
4209.176 | 679.4436 | 441.9549 | 432.9078 | 421.056
4210.176 | 679.1508 | 442.0016 | 433.3556 | 422.1157
4211.176 | 676.3026 | 442.166 | 433.6515 | 422.18
4212.176 | 674.7726 | 442.9087 | 434.259 | 422.3737
4213.176 | 674.4865 | 443.8136 | 434.6948 | 423.0125
4214.176 | 673.7555 | 445.0016 | 434.9573 | 423.7464
4215.176 | 671.1397 | 445.1928 | 434.7532 | 424.6493
4216.176 | 668.0285 | 445.3215 | 434.7939 | 425.0172
4217.176 | 665.774 | 445.5792 | 434.7639 | 424.8082
4218.176 | 664.2165 | 446.3708 | 434.9941 | 424.9633
4219.176 | 662.5715 | 446.7394 | 434.826 | 425.0178
4220.176 | 662.093 | 447.3528 | 435.345 | 424.7474
4221.176 | 668.7113 | 447.129 | 435.2284 | 425.5482
4222.176 | 673.9534 | 447.1876 | 435.2842 | 425.4377
4223.176 | 677.1538 | 447.5729 | 435.359 | 425.5451
4224.176 | 678.6305 | 448.1073 | 435.3081 | 425.5363
4225.176 | 678.5408 | 448.418 | 435.3083 | 425.6258
4226.176 | 679.1516 | 448.8979 | 435.4873 | 425.9649
4227.176 | 676.151 | 449.7784 | 435.7737 | 426.2011
4228.176 | 673.9825 | 450.5254 | 436.6615 | 427.0758
4229.176 | 670.6393 | 450.5507 | 437.0645 | 427.0131
4230.176 | 669.9459 | 450.173 | 437.4631 | 427.3561
4231.176 | 668.9561 | 449.913 | 437.4342 | 428.6332
4232.176 | 668.1623 | 449.7941 | 437.7138 | 428.4405
4233.176 | 670.4159 | 449.5915 | 437.7093 | 428.5813
4234.176 | 670.2467 | 449.8036 | 437.4247 | 428.4237
4235.176 | 672.9367 | 449.7702 | 437.3521 | 428.2493
4236.176 | 674.7048 | 449.8976 | 437.2381 | 428.4107
4237.176 | 675.3514 | 450.5663 | 437.0088 | 428.2561
4238.176 | 675.0056 | 450.762 | 437.2554 | 428.6095
4239.176 | 675.7668 | 450.5199 | 437.7634 | 430.0539
4240.176 | 678.0973 | 450.8305 | 438.25 | 430.084
4241.176 | 679.6857 | 450.6382 | 438.5882 | 430.4717
4242.176 | 680.791 | 450.45 | 438.5867 | 430.1832
4243.176 | 680.3318 | 450.0967 | 438.382 | 430.1988
4244.176 | 680.1428 | 449.4521 | 438.7623 | 429.7433
4245.176 | 680.4888 | 448.9036 | 438.5106 | 429.8618
4246.176 | 681.1859 | 448.8301 | 438.2175 | 429.2993
4247.176 | 681.2481 | 449.4049 | 438.2684 | 429.617
4248.176 | 683.4175 | 449.5896 | 438.2941 | 429.4221
4249.176 | 684.4754 | 449.8302 | 438.1445 | 429.0601
4250.176 | 682.7474 | 450.4172 | 438.0512 | 428.8152
4251.176 | 681.848 | 451.1971 | 438.9328 | 428.4846
4252.176 | 679.272 | 451.6153 | 439.1537 | 429.0701
4253.176 | 680.8529 | 451.9814 | 439.2587 | 429.2911
4254.176 | 682.2244 | 451.7242 | 439.2143 | 429.5823
4255.176 | 682.007 | 451.4916 | 439.3151 | 429.5108
4256.176 | 682.5755 | 451.7939 | 439.105 | 430.158
4257.176 | 681.9852 | 451.7132 | 438.9107 | 430.0424
4258.176 | 682.3741 | 451.6861 | 439.031 | 429.5169
4259.176 | 682.711 | 452.082 | 438.8325 | 430.5733
4260.176 | 679.0632 | 453.8748 | 439.1255 | 431.1288
4261.176 | 676.7825 | 454.5115 | 440.2965 | 431.288
4262.1917 | 675.8293 | 455.7792 | 441.3486 | 431.3587
4263.1917 | 673.2295 | 456.4266 | 442.5678 | 432.9085
4264.176 | 672.3944 | 457.3286 | 443.3456 | 433.277
4265.176 | 671.3004 | 458.6499 | 444.233 | 434.2922
4266.176 | 668.3835 | 458.8844 | 444.8164 | 435.0004
4267.176 | 666.635 | 458.7886 | 444.9589 | 435.5334
4268.176 | 665.2264 | 458.6699 | 445.0104 | 435.1674
4269.176 | 664.9083 | 458.7008 | 445.048 | 435.7487
4270.176 | 667.314 | 458.3739 | 445.5641 | 435.518
4271.176 | 668.2089 | 458.6843 | 445.703 | 435.7017
4272.176 | 666.9142 | 459.2655 | 445.8319 | 435.4767
4273.176 | 666.4171 | 459.4717 | 445.8642 | 435.2418
4274.176 | 665.8785 | 459.7893 | 445.9708 | 435.5395
4275.176 | 670.1119 | 460.1113 | 445.7499 | 435.3727
4276.176 | 678.3413 | 460.7006 | 445.5299 | 434.8206
4277.176 | 679.2173 | 461.2125 | 445.3938 | 434.5084
4278.176 | 678.6742 | 461.494 | 445.3619 | 434.3851
4279.176 | 680.588 | 461.547 | 445.3669 | 434.5334
4280.176 | 684.259 | 461.7723 | 445.8957 | 434.3123
4281.176 | 686.6697 | 461.5111 | 445.8692 | 434.7533
4282.176 | 687.2686 | 461.9919 | 446.1114 | 434.9359
4283.176 | 688.3454 | 462.861 | 446.1349 | 434.995
4284.176 | 686.9749 | 463.5617 | 446.2522 | 435.3671
4285.176 | 687.1892 | 463.803 | 446.6872 | 435.8314
4286.176 | 687.7401 | 463.6413 | 446.7381 | 435.4165
4287.176 | 687.3457 | 463.8108 | 446.4159 | 435.6063
4288.176 | 684.2424 | 464.4939 | 446.1932 | 435.6913
4289.176 | 683.4264 | 464.2569 | 446.7066 | 436.0578
4290.176 | 682.2855 | 464.6049 | 446.9022 | 436.2888
4291.176 | 678.8655 | 465.1735 | 446.9359 | 436.3511
4292.176 | 676.743 | 466.1744 | 446.7319 | 437.1994
4293.176 | 675.4926 | 466.879 | 447.1689 | 437.7886
4294.176 | 681.11 | 467.222 | 447.2848 | 438.7415
4295.176 | 682.6866 | 467.5346 | 448.053 | 439.1226
4296.176 | 679.4852 | 467.6426 | 448.7883 | 439.7163
4297.176 | 677.6422 | 467.8584 | 449.8353 | 439.5136
4298.176 | 675.6363 | 467.9221 | 450.6074 | 439.7707
4299.176 | 674.524 | 467.5135 | 450.9006 | 440.633
4300.176 | 675.2553 | 466.6889 | 450.7496 | 440.5798
4301.176 | 676.2078 | 466.458 | 450.5765 | 440.6736
4302.176 | 677.6799 | 466.4255 | 451.5583 | 440.4358
4303.176 | 681.2793 | 467.209 | 452.1491 | 440.0244
4304.176 | 682.9552 | 467.1757 | 452.1219 | 439.4069
4305.176 | 684.0696 | 467.5127 | 452.3485 | 439.3906
4306.176 | 684.1801 | 468.1551 | 452.5824 | 438.9626
4307.176 | 685.4537 | 468.0485 | 452.4747 | 439.7629
4308.176 | 685.6114 | 468.368 | 452.4339 | 439.9281
4309.176 | 683.0987 | 468.9808 | 452.739 | 440.0005
4310.176 | 680.9711 | 469.3265 | 453.1438 | 439.4457
4311.176 | 677.7249 | 469.524 | 453.4168 | 439.8706
4312.176 | 674.994 | 468.9774 | 453.4181 | 439.8436
4313.176 | 674.0101 | 468.8641 | 453.3403 | 439.9736
4314.176 | 675.7105 | 469.2788 | 453.1648 | 439.7233
4315.176 | 680.5647 | 469.5329 | 453.2678 | 439.6516
4316.176 | 681.5022 | 470.0374 | 453.3549 | 439.2827
4317.176 | 682.2807 | 470.3275 | 453.3022 | 439.1958
4318.176 | 682.5749 | 470.5111 | 453.2966 | 439.0937
4319.176 | 684.942 | 470.8917 | 453.4927 | 439.8228
4320.176 | 684.5552 | 471.473 | 454.0866 | 440.0254
4321.176 | 683.1666 | 471.9455 | 454.5116 | 440.3738
4322.176 | 681.6419 | 472.886 | 454.3819 | 440.9209
4323.176 | 683.2269 | 474.056 | 454.1001 | 441.9586
4324.176 | 685.0837 | 474.3441 | 454.3767 | 441.738
4325.176 | 685.123 | 474.5838 | 454.328 | 441.8949
4326.176 | 683.4807 | 474.8261 | 454.7086 | 441.883
4327.176 | 681.166 | 475.0514 | 455.3901 | 442.0526
4328.176 | 679.0682 | 475.0211 | 455.8902 | 442.0115
4329.176 | 677.7976 | 474.983 | 455.8095 | 442.8551
4330.176 | 679.0778 | 474.8878 | 455.5909 | 442.8599
4331.176 | 680.035 | 475.0892 | 455.0154 | 442.793
4332.176 | 682.5416 | 474.8749 | 454.5889 | 442.2667
4333.176 | 682.0417 | 475.6179 | 454.428 | 441.5925
4334.176 | 682.5947 | 475.5731 | 454.4216 | 441.402
4335.176 | 688.2048 | 475.7425 | 454.7342 | 441.7012
4336.176 | 688.8333 | 475.7271 | 455.298 | 443.2282
4337.176 | 684.8567 | 476.2271 | 455.9642 | 443.587
4338.176 | 679.409 | 477.7899 | 456.7387 | 444.0833
4339.176 | 672.9866 | 478.2568 | 457.5856 | 444.8857
4340.176 | 673.3033 | 479.0989 | 458.0607 | 445.3369
4341.176 | 680.0613 | 479.4365 | 458.736 | 445.6706
4342.176 | 680.87 | 479.8946 | 458.7536 | 445.6594
4343.176 | 682.5142 | 480.2274 | 459.3303 | 446.0403
4344.176 | 684.9196 | 479.9531 | 459.3555 | 446.5088
4345.176 | 684.7091 | 479.878 | 459.6427 | 446.487
4346.176 | 682.3806 | 481.1799 | 459.3639 | 447.723
4347.176 | 681.7986 | 480.8309 | 459.597 | 447.7851
4348.176 | 679.3628 | 480.6425 | 459.758 | 448.3382
4349.176 | 678.0267 | 480.9468 | 459.7278 | 447.9523
4350.176 | 678.6308 | 480.7869 | 459.9929 | 448.1126
4351.176 | 681.6496 | 481.429 | 460.7044 | 447.7825
4352.176 | 684.5574 | 481.379 | 461.0384 | 447.6126
4353.176 | 685.031 | 480.9074 | 461.2895 | 447.4371
4354.176 | 686.7891 | 480.346 | 461.1732 | 446.8526
4355.176 | 689.318 | 480.3835 | 461.1243 | 446.3938
4356.176 | 691.8833 | 481.0201 | 461.4381 | 446.4301
4357.176 | 694.4914 | 480.8325 | 461.457 | 445.8669
4358.176 | 694.6419 | 480.6721 | 461.9921 | 445.4788
4359.176 | 696.9711 | 480.474 | 462.0699 | 445.7102
4360.176 | 696.5353 | 480.6169 | 461.7466 | 445.8416
4361.176 | 696.8952 | 480.7765 | 462.3116 | 446.6102
4362.176 | 696.1997 | 481.1766 | 463.3742 | 447.9908
4363.176 | 696.563 | 480.5845 | 463.5238 | 448.8062
4364.176 | 697.4161 | 480.137 | 463.4463 | 449.4913
4365.176 | 698.7438 | 479.5984 | 463.1697 | 449.7632
4366.176 | 699.8691 | 479.4847 | 462.6244 | 449.7474
4367.176 | 699.6087 | 479.6101 | 462.3821 | 449.7276
4368.176 | 698.8122 | 480.1795 | 462.1564 | 449.5626
4369.176 | 697.078 | 480.4558 | 461.8959 | 449.6421
4370.176 | 696.1604 | 481.2838 | 462.1144 | 450.1458
4371.176 | 694.3327 | 481.2399 | 462.7376 | 450.5878
4372.176 | 692.6438 | 481.2942 | 463.2999 | 451.1623
4373.176 | 690.1364 | 481.0764 | 463.3608 | 451.5641
4374.176 | 689.0463 | 480.8098 | 463.4959 | 452.116
4375.176 | 685.7553 | 480.5919 | 463.4567 | 452.3197
4376.176 | 686.006 | 480.1217 | 463.379 | 452.1541
4377.176 | 683.8113 | 479.3582 | 463.3234 | 451.8288
4378.176 | 681.812 | 478.8294 | 463.3873 | 452.679
4379.176 | 679.9937 | 478.9282 | 463.5782 | 452.5677
4380.176 | 681.9408 | 479.6233 | 464.112 | 453.0014
4381.176 | 679.9129 | 480.3916 | 464.4085 | 453.387
4382.176 | 677.3988 | 480.9449 | 464.9783 | 453.1983
4383.176 | 674.0471 | 481.7208 | 465.5188 | 453.5475
4384.176 | 673.1062 | 482.2792 | 466.0504 | 453.4626
4385.176 | 669.1139 | 482.6772 | 466.2547 | 453.835
4386.176 | 665.6387 | 482.199 | 466.234 | 454.0901
4387.176 | 667.093 | 481.7353 | 466.2033 | 453.4007
4388.176 | 671.2123 | 481.6767 | 466.0463 | 453.0754
4389.176 | 673.3959 | 481.5841 | 465.7847 | 452.8774
4390.176 | 672.9908 | 481.9798 | 465.4892 | 453.0696
4391.176 | 675.1207 | 482.1473 | 465.1093 | 453.206
4392.176 | 676.3053 | 482.0378 | 464.9703 | 453.1301
4393.176 | 677.6525 | 481.8807 | 465.0832 | 453.0292
4394.176 | 678.4923 | 482.5562 | 465.4652 | 453.0208
4395.176 | 676.6462 | 482.6455 | 466.1381 | 453.2952
4396.176 | 673.1132 | 483.2912 | 466.5439 | 453.9944
4397.176 | 670.1692 | 484.6627 | 467.1485 | 454.7259
4398.176 | 668.8646 | 484.8827 | 467.3509 | 455.2806
4399.176 | 666.0104 | 484.2399 | 467.2109 | 454.8986
4400.176 | 666.9954 | 483.6491 | 466.9363 | 455.7265
4401.176 | 668.0428 | 483.5902 | 466.5372 | 456.3523
4402.176 | 669.5971 | 484.44 | 466.7455 | 456.276
4403.176 | 669.3446 | 485.164 | 467.0456 | 457.4574
4404.176 | 669.5359 | 485.5881 | 467.6341 | 457.8443
4405.176 | 670.3434 | 485.7393 | 468.183 | 458.4825
4406.176 | 671.8391 | 486.9506 | 468.3138 | 458.2721
4407.176 | 670.6567 | 487.4429 | 469.2556 | 458.9355
4408.176 | 668.0564 | 488.5168 | 469.9434 | 459.8565
4409.176 | 666.8104 | 488.5726 | 470.0092 | 460.0909
4410.176 | 668.328 | 489.0586 | 469.678 | 460.0895
4411.176 | 672.1294 | 489.1462 | 469.9592 | 459.5407
4412.176 | 671.6328 | 489.54 | 470.4445 | 460.1438
4413.176 | 670.4926 | 489.8732 | 470.9874 | 459.9497
4414.176 | 668.7833 | 490.1286 | 471.6472 | 460.597
4415.176 | 669.6046 | 490.4461 | 472.1264 | 460.2821
4416.176 | 668.9721 | 490.7468 | 472.5198 | 461.3925
4417.176 | 666.0742 | 491.4796 | 472.7856 | 461.6483
4418.176 | 665.4561 | 491.4236 | 472.7203 | 462.2674
4419.176 | 661.8317 | 492.1838 | 473.5679 | 462.9027
4420.176 | 659.8477 | 493.3897 | 473.6988 | 464.1236
4421.176 | 657.2696 | 494.8323 | 474.0539 | 464.2789
4422.176 | 657.5508 | 494.9229 | 474.1989 | 464.9697
4423.176 | 655.9282 | 494.7163 | 474.0655 | 465.1878
4424.176 | 655.8387 | 493.9305 | 474.1231 | 465.499
4425.176 | 655.0702 | 493.7018 | 474.4739 | 466.8141
4426.176 | 654.2193 | 493.6662 | 474.6014 | 466.5818
4427.176 | 654.8837 | 494.2663 | 474.53 | 466.1899
4428.176 | 655.942 | 494.776 | 474.3377 | 465.8958
4429.176 | 661.2859 | 494.7926 | 474.0643 | 465.1937
4430.176 | 664.3418 | 494.4757 | 473.475 | 464.5911
4431.176 | 666.8136 | 494.9015 | 472.9857 | 464.0812
4432.176 | 667.832 | 495.3282 | 472.6602 | 463.4163
4433.176 | 668.3499 | 495.9645 | 472.7172 | 462.8124
4434.1917 | 668.1083 | 495.4547 | 473.014 | 463.7652
4435.176 | 667.4986 | 495.0479 | 473.2484 | 463.7381
4436.176 | 667.4732 | 494.9453 | 473.5251 | 464.9764
4437.176 | 668.0101 | 494.8385 | 473.6421 | 465.0001
4438.176 | 668.4349 | 494.8813 | 473.9574 | 464.7963
4439.176 | 670.3276 | 495.0318 | 474.3647 | 465.0695
4440.176 | 672.1997 | 495.1717 | 474.5557 | 466.2587
4441.176 | 671.9999 | 495.1112 | 474.9286 | 466.3185
4442.176 | 669.7527 | 495.0159 | 475.2384 | 466.2454
4443.176 | 672.8446 | 494.6515 | 475.3874 | 465.9615
4444.176 | 677.2682 | 493.9439 | 475.4478 | 466.6278
4445.176 | 679.8271 | 493.7303 | 475.4292 | 466.4161
4446.176 | 679.8207 | 494.1847 | 475.9292 | 466.6848
4447.176 | 679.7114 | 494.0314 | 476.055 | 466.805
4448.176 | 679.8271 | 493.6868 | 476.1357 | 467.0681
4449.176 | 679.819 | 493.4888 | 476.1533 | 468.0194
4450.176 | 680.9752 | 493.6559 | 476.1974 | 468.354
4451.176 | 680.5717 | 493.6886 | 476.3593 | 468.0184
4452.176 | 682.1434 | 493.8139 | 476.2725 | 468.8212
4453.176 | 684.4826 | 494.3763 | 477.0949 | 468.5139
4454.176 | 685.4653 | 494.9145 | 477.9938 | 469.2053
4455.176 | 686.3572 | 494.9982 | 478.2896 | 469.3809
4456.176 | 687.3499 | 495.6173 | 478.4318 | 470.0693
4457.176 | 689.3952 | 496.0014 | 478.6591 | 470.6025
4458.176 | 691.4245 | 495.8699 | 479.3385 | 470.9846
4459.176 | 691.0191 | 495.5363 | 480.2367 | 471.1662
4460.176 | 688.1101 | 495.7121 | 480.4711 | 470.9353
4461.176 | 682.8239 | 495.8924 | 480.3568 | 471.0997
4462.176 | 679.8646 | 496.8351 | 480.2404 | 471.223
4463.176 | 678.1792 | 496.5903 | 480.1129 | 471.365
4464.176 | 677.16 | 496.0386 | 479.8502 | 471.3986
4465.176 | 673.9588 | 495.6661 | 479.3766 | 471.3928
4466.176 | 671.6939 | 494.9642 | 478.9805 | 471.1264
4467.176 | 668.3086 | 494.2129 | 478.979 | 470.9718
4468.176 | 665.3027 | 493.5796 | 479.038 | 471.5427
4469.176 | 663.8211 | 493.7205 | 479.2889 | 471.3701
4470.176 | 661.6259 | 493.9262 | 479.1335 | 472.4554
4471.176 | 663.34 | 493.4826 | 478.8444 | 471.8803
4472.176 | 663.5409 | 494.0739 | 478.5648 | 471.4667
4473.176 | 663.8497 | 495.3466 | 478.4753 | 471.0374
4474.176 | 665.2386 | 496.7881 | 478.2399 | 470.6546
4475.176 | 664.8503 | 496.7026 | 478.5987 | 470.2199
4476.176 | 663.3775 | 497.0655 | 479.5084 | 471.058
4477.176 | 662.9174 | 497.7041 | 479.3789 | 470.833
4478.1917 | 661.3469 | 497.5374 | 479.5323 | 471.0958
4479.176 | 660.7246 | 497.8967 | 479.7265 | 470.6811
4480.176 | 658.9341 | 498.9383 | 479.6137 | 470.4316
4481.176 | 656.1785 | 499.7086 | 479.7981 | 470.8397
4482.176 | 652.7947 | 500.1871 | 481.0002 | 471.1637
4483.176 | 654.7027 | 500.46 | 481.5423 | 471.3473
4484.176 | 659.1989 | 500.5349 | 482.948 | 471.6204
4485.176 | 659.6474 | 500.3735 | 482.8679 | 472.3052
4486.176 | 663.0655 | 500.249 | 482.8895 | 473.1572
4487.176 | 665.0019 | 499.8991 | 482.893 | 473.5126
4488.176 | 664.9189 | 500.0597 | 483.3223 | 473.1083
4489.176 | 662.5377 | 500.6582 | 483.4198 | 473.0462
4490.176 | 663.7837 | 501.2908 | 483.8497 | 473.1354
4491.176 | 665.3974 | 501.2157 | 484.7353 | 473.853
4492.176 | 668.0572 | 502.2552 | 485.0304 | 474.4681
4493.176 | 673.1374 | 503.1063 | 485.0893 | 474.88
4494.176 | 674.3074 | 503.2404 | 485.0934 | 475.2279
4495.176 | 674.887 | 503.1587 | 485.0943 | 476.5219
4496.176 | 675.9109 | 503.2286 | 485.1913 | 476.8567
4497.176 | 679.6402 | 503.3871 | 485.5413 | 476.95
4498.176 | 679.5254 | 503.8285 | 485.4592 | 477.0129
4499.176 | 677.6247 | 504.4334 | 485.6718 | 477.2059
4500.176 | 675.7016 | 505.1806 | 485.5719 | 476.8821
4501.176 | 674.7392 | 505.3149 | 485.5117 | 476.8164
4502.176 | 673.4319 | 504.8779 | 485.475 | 476.5315
4503.176 | 671.8413 | 504.3978 | 485.5973 | 476.8275
4504.176 | 667.5659 | 503.7179 | 485.0028 | 477.0527
4505.176 | 665.7685 | 503.7442 | 485.1727 | 476.7314
4506.176 | 662.8736 | 503.5405 | 485.4556 | 476.7564
4507.176 | 662.1981 | 502.4432 | 485.4199 | 476.6929
4508.176 | 661.2636 | 502.2243 | 485.4044 | 476.3751
4509.176 | 658.0169 | 502.1703 | 484.9305 | 476.1394
4510.176 | 656.1794 | 502.2312 | 484.8949 | 476.4392
4511.176 | 655.3236 | 501.3545 | 485.9987 | 476.368
4512.176 | 660.207 | 500.6077 | 485.7696 | 476.5856
4513.176 | 662.2232 | 500.1077 | 485.1171 | 476.6928
4514.176 | 661.1873 | 500.2959 | 484.49 | 475.9226
4515.176 | 659.393 | 500.039 | 484.0759 | 475.4931
4516.176 | 659.8423 | 500.2777 | 483.8676 | 475.1782
4517.176 | 662.1658 | 500.3796 | 483.8425 | 475.2372
4518.176 | 664.4281 | 500.418 | 483.6519 | 475.2703
4519.176 | 665.8988 | 500.6262 | 483.5644 | 475.2827
4520.176 | 668.695 | 500.6798 | 483.5906 | 475.5458
4521.176 | 671.6291 | 500.8335 | 483.4566 | 475.8967
4522.176 | 671.5966 | 501.5849 | 483.7177 | 475.3452
4523.176 | 674.8229 | 501.8397 | 484.3212 | 474.9563
4524.176 | 673.9737 | 502.0489 | 484.6174 | 474.8695
4525.176 | 672.696 | 501.4355 | 484.6948 | 475.3058
4526.176 | 674.4682 | 501.2191 | 484.5097 | 475.9706
4527.176 | 674.8178 | 501.5756 | 484.3966 | 476.0676
4528.176 | 676.4117 | 501.9763 | 484.9069 | 475.6973
4529.176 | 676.9248 | 502.2674 | 485.1915 | 475.2637
4530.176 | 679.3896 | 502.5138 | 484.7711 | 475.421
4531.176 | 681.0387 | 502.1056 | 484.4632 | 476.1256
4532.176 | 681.0405 | 501.4102 | 484.3292 | 476.0585
4533.176 | 680.3609 | 500.8637 | 483.9689 | 475.7509
4534.176 | 683.1507 | 500.3389 | 483.8994 | 475.6593
4535.176 | 685.6898 | 500.4435 | 484.0806 | 475.8577
4536.176 | 687.3962 | 500.8392 | 484.2906 | 476.6793
4537.176 | 690.2367 | 501.0607 | 484.7213 | 477.259
4538.176 | 690.9055 | 501.6357 | 484.9135 | 478.045
4539.176 | 690.9172 | 501.7961 | 485.3101 | 478.1169
4540.176 | 690.0375 | 502.1613 | 485.5282 | 477.5646
4541.176 | 688.7499 | 502.7744 | 486.0348 | 478.0601
4542.176 | 686.4187 | 502.977 | 486.5666 | 479.6451
4543.176 | 686.8255 | 502.8995 | 486.6892 | 479.5662
4544.176 | 687.094 | 503.1903 | 486.4701 | 479.4585
4545.176 | 687.1976 | 503.9985 | 486.802 | 479.3691
4546.176 | 686.1145 | 504.7711 | 487.2786 | 479.3324
4547.176 | 686.6114 | 505.9792 | 487.469 | 479.7134
4548.176 | 685.7992 | 507.0881 | 487.8113 | 479.9416
4549.176 | 685.0348 | 507.4795 | 488.186 | 480.2762
4550.176 | 678.6251 | 508.6017 | 488.7263 | 480.3637
4551.176 | 672.9928 | 509.4219 | 489.229 | 480.0924
4552.176 | 671.4428 | 510.0474 | 489.5182 | 480.4112
4553.176 | 667.7043 | 511.0224 | 489.7624 | 481.1975
4554.176 | 664.4037 | 511.7673 | 489.9962 | 481.8258
4555.176 | 661.1215 | 511.1979 | 491.1156 | 482.4307
4556.176 | 659.6587 | 511.4987 | 490.9048 | 483.2824
4557.176 | 657.8711 | 511.5285 | 490.8786 | 483.7541
4558.176 | 659.4696 | 511.7234 | 491.0183 | 484.3124
4559.176 | 662.0951 | 512.072 | 490.9179 | 484.4017
4560.176 | 658.872 | 512.7927 | 491.7033 | 484.5847
4561.176 | 655.4693 | 513.9635 | 491.7978 | 484.5864
4562.176 | 655.3363 | 514.5587 | 491.9718 | 485.1381
4563.1917 | 656.4245 | 514.661 | 492.3228 | 485.4347
4564.176 | 656.4257 | 514.6303 | 492.0988 | 486.3723
4565.176 | 654.977 | 514.8041 | 491.7451 | 486.2295
4566.176 | 658.6678 | 515.3833 | 491.8572 | 486.642
4567.176 | 660.5529 | 515.6002 | 491.7354 | 486.5669
4568.176 | 662.2456 | 515.9623 | 491.8512 | 487.0969
4569.176 | 660.5235 | 516.1783 | 491.9767 | 487.2504
4570.176 | 660.573 | 516.5635 | 491.9462 | 487.7257
4571.176 | 660.0205 | 516.8147 | 492.1428 | 487.7283
4572.176 | 657.6867 | 516.6496 | 492.3938 | 487.514
4573.176 | 656.2005 | 516.8114 | 492.5052 | 487.2619
4574.176 | 651.9951 | 516.1296 | 492.524 | 486.6237
4575.176 | 650.6965 | 515.3279 | 492.3696 | 486.7872
4576.176 | 656.0466 | 515.0885 | 491.9311 | 486.6464
4577.176 | 654.366 | 515.3038 | 491.7608 | 486.0899
4578.176 | 657.0241 | 515.4683 | 491.5195 | 485.9306
4579.176 | 656.4805 | 515.558 | 491.5218 | 485.6974
4580.176 | 658.5414 | 515.2684 | 491.4651 | 485.2398
4581.176 | 659.2327 | 514.4013 | 491.2534 | 484.9565
4582.176 | 661.0573 | 514.0996 | 491.1929 | 484.5224
4583.176 | 660.4259 | 514.108 | 490.9477 | 484.6247
4584.176 | 663.9343 | 514.1468 | 490.8191 | 484.9044
4585.176 | 658.9472 | 515.1556 | 491.0695 | 484.7182
4586.176 | 659.7708 | 516.336 | 491.4775 | 484.3694
4587.176 | 661.948 | 516.6498 | 491.5712 | 483.9622
4588.176 | 660.5552 | 516.8879 | 491.5871 | 483.8993
4589.176 | 663.3294 | 517.4503 | 492.4915 | 483.6736
4590.176 | 671.2399 | 517.5926 | 492.4483 | 483.8805
4591.176 | 672.3677 | 517.2372 | 492.5089 | 483.7164
4592.176 | 669.163 | 516.9384 | 492.0296 | 483.6354
4593.176 | 669.8739 | 516.8336 | 491.6896 | 483.6943
4594.176 | 668.233 | 516.8451 | 491.9816 | 484.1701
4595.176 | 674.1646 | 516.3989 | 492.1119 | 484.0498
4596.176 | 673.4298 | 516.6738 | 492.1055 | 484.3197
4597.176 | 674.65 | 517.0165 | 491.9742 | 484.1212
4598.176 | 671.4868 | 517.5549 | 492.34 | 483.7597
4599.176 | 668.4241 | 517.7901 | 491.9744 | 483.1804
4600.176 | 671.4773 | 517.3933 | 491.8395 | 483.0767
4601.176 | 670.9669 | 517.2663 | 492.168 | 483.7927
4602.176 | 672.9004 | 517.2045 | 491.829 | 483.6226
4603.176 | 674.5492 | 516.2924 | 491.7689 | 483.2149
4604.176 | 673.3828 | 516.0994 | 492.066 | 483.1081
4605.176 | 676.68 | 515.8536 | 492.0262 | 482.8793
4606.176 | 674.5171 | 515.5983 | 491.6109 | 483.9818
4607.176 | 676.7318 | 516.7355 | 492.2073 | 483.4966
4608.176 | 678.9902 | 516.5429 | 492.4104 | 483.0022
4609.176 | 677.7218 | 516.2397 | 492.5665 | 483.0245
4610.176 | 677.4278 | 516.2314 | 492.8957 | 483.737
4611.176 | 673.4783 | 516.9745 | 493.0172 | 483.3964
4612.176 | 678.2384 | 517.4841 | 493.2072 | 483.2006
4613.176 | 675.3 | 517.609 | 493.6735 | 482.772
4614.176 | 675.279 | 517.6102 | 493.6761 | 482.5075
4615.176 | 675.8475 | 517.1793 | 493.6393 | 483.6528
4616.176 | 673.5454 | 516.8038 | 493.4449 | 483.482
4617.176 | 669.5141 | 517.3693 | 493.3025 | 483.0062
4618.176 | 666.85 | 516.8173 | 493.2919 | 482.6213
4619.176 | 662.4061 | 516.8273 | 493.2998 | 482.9972
4620.176 | 663.021 | 517.1789 | 493.1378 | 482.7623
4621.176 | 666.9497 | 517.2582 | 492.7561 | 482.5323
4622.176 | 666.824 | 517.6562 | 492.306 | 482.2438
4623.1917 | 669.177 | 517.7537 | 492.2303 | 482.5843
4624.176 | 670.49 | 518.3297 | 492.3627 | 483.6954
4625.176 | 666.7885 | 518.9735 | 492.6207 | 484.4604
4626.176 | 667.6619 | 520.3794 | 493.0037 | 484.4622
4627.176 | 665.5918 | 521.0288 | 493.5509 | 484.531
4628.176 | 665.4459 | 520.9764 | 493.6811 | 484.6278
4629.176 | 665.5343 | 520.997 | 493.8362 | 484.8524
4630.176 | 663.5752 | 521.0798 | 494.8869 | 485.0502
4631.176 | 666.1266 | 521.9385 | 494.9429 | 485.4616
4632.176 | 665.2338 | 521.5505 | 495.0086 | 485.5893
4633.176 | 666.9593 | 521.5123 | 495.015 | 486.1677
4634.176 | 669.0771 | 521.3656 | 495.3066 | 486.3774
4635.176 | 670.6624 | 521.7412 | 495.501 | 486.0512
4636.176 | 671.5596 | 522.102 | 495.5741 | 485.98
4637.176 | 668.9316 | 522.7223 | 495.5998 | 486.4514
4638.176 | 669.2602 | 522.864 | 496.0446 | 487.006
4639.176 | 669.3593 | 524.0604 | 496.8936 | 487.7048
4640.176 | 667.6623 | 524.6088 | 497.9978 | 487.7401
4641.176 | 668.0457 | 525.6005 | 498.0768 | 487.5148
4642.176 | 668.2784 | 526.269 | 497.7144 | 487.1631
4643.176 | 665.3343 | 525.4604 | 497.4125 | 487.7433
4644.176 | 666.2804 | 525.3617 | 497.4157 | 488.618
4645.176 | 660.8396 | 526.1412 | 497.466 | 489.3151
4646.176 | 660.8745 | 526.3987 | 497.4619 | 489.0672
4647.176 | 662.8858 | 526.1043 | 497.8026 | 488.3069
4648.176 | 668.425 | 526.224 | 497.9043 | 489.75
4649.176 | 668.1786 | 526.9382 | 498.1201 | 489.849
4650.176 | 662.8375 | 527.4842 | 498.549 | 489.4113
4651.176 | 662.0572 | 527.2364 | 498.7656 | 489.1239
4652.176 | 659.2982 | 526.8428 | 498.5602 | 488.6006
4653.176 | 661.7284 | 527.3134 | 498.1061 | 489.2068
4654.176 | 660.5121 | 529.1571 | 497.948 | 488.8206
4655.176 | 664.0748 | 529.0777 | 498.5245 | 488.4957
4656.176 | 663.0224 | 528.2109 | 498.8286 | 489.0994
4657.176 | 660.8518 | 527.6813 | 498.5234 | 489.5394
4658.176 | 664.7608 | 526.6865 | 498.4471 | 489.6732
4659.176 | 662.8275 | 526.8223 | 497.8659 | 489.8794
4660.176 | 663.0498 | 526.1325 | 497.5462 | 489.9191
4661.176 | 662.2412 | 525.9903 | 497.2609 | 490.0011
4662.176 | 660.8381 | 527.3572 | 497.3009 | 489.9256
4663.176 | 654.5864 | 529.5 | 497.2359 | 489.4442
4664.176 | 650.7269 | 529.7824 | 497.1888 | 489.495
4665.176 | 651.3701 | 529.8056 | 497.1197 | 490.0649
4666.176 | 650.0807 | 529.1414 | 498.2235 | 490.2303
4667.176 | 658.0725 | 529.9817 | 498.633 | 489.794
4668.176 | 658.4041 | 530.7 | 498.8857 | 489.9083
4669.176 | 664.4661 | 530.6312 | 498.9384 | 490.1433
4670.176 | 667.828 | 530.8446 | 498.7471 | 490.337
4671.176 | 668.3863 | 531.535 | 499.4993 | 490.3869
4672.176 | 670.1478 | 531.475 | 499.7803 | 490.1703
4673.176 | 668.6482 | 531.6623 | 500.1369 | 490.9222
4674.176 | 664.1345 | 531.6929 | 500.6969 | 491.6881
4675.176 | 659.4641 | 532.1535 | 501.3604 | 492.2463
4676.176 | 655.8308 | 532.2844 | 501.5725 | 493.1542
4677.176 | 649.4273 | 532.6051 | 502.1554 | 493.5047
4678.176 | 647.1838 | 533.1509 | 502.8422 | 493.4067
4679.176 | 646.7647 | 533.4113 | 502.5883 | 493.2953
4680.176 | 649.8506 | 533.7601 | 502.8824 | 493.3539
4681.176 | 645.715 | 533.1195 | 502.7948 | 492.9951
4682.176 | 645.0763 | 532.2857 | 502.6551 | 493.2973
4683.176 | 645.4611 | 531.4604 | 502.2686 | 493.3447
4684.176 | 646.2321 | 531.623 | 502.046 | 493.2656
4685.176 | 644.7784 | 531.3867 | 501.5419 | 493.0869
4686.176 | 644.3539 | 532.0352 | 501.3004 | 492.8928
4687.176 | 641.1411 | 533.3192 | 501.2646 | 492.7429
4688.176 | 641.8216 | 534.529 | 501.6759 | 492.9213
4689.176 | 640.6619 | 535.6052 | 502.2302 | 492.5175
4690.176 | 637.9946 | 536.2061 | 502.7299 | 492.4537
4691.176 | 640.689 | 537.5001 | 502.6445 | 491.8889
4692.176 | 637.863 | 537.2599 | 502.7036 | 491.6582
4693.176 | 637.0289 | 538.2395 | 502.9116 | 493.7471
4694.176 | 634.4387 | 540.5769 | 503.0446 | 493.7297
4695.176 | 628.8662 | 539.5609 | 503.017 | 493.3901
4696.176 | 630.3931 | 539.397 | 503.9908 | 493.1291
4697.176 | 631.3877 | 540.3796 | 504.4488 | 493.4457
4698.176 | 630.709 | 540.1623 | 505.0009 | 493.6681
4699.176 | 631.3802 | 540.0931 | 504.954 | 493.8331
4700.176 | 631.5396 | 539.3485 | 504.7958 | 493.1163
4701.176 | 639.0409 | 539.1612 | 504.3792 | 492.8217
4702.176 | 642.5868 | 539.75 | 504.0407 | 492.3833
4703.176 | 642.2304 | 540.0635 | 503.9091 | 492.5346
4704.176 | 642.5982 | 539.6486 | 503.9978 | 492.1208
4705.176 | 644.6086 | 539.2294 | 503.7453 | 492.2716
4706.176 | 644.5022 | 540.5539 | 503.5481 | 492.5701
4707.176 | 644.3066 | 541.1567 | 503.3988 | 492.0988
4708.176 | 643.2721 | 541.3608 | 504.2136 | 492.4878
4709.176 | 645.4803 | 541.9024 | 505.3032 | 492.5635
4710.176 | 639.6933 | 541.102 | 505.3248 | 492.8085
4711.176 | 641.0138 | 541.4511 | 505.4716 | 492.971
4712.176 | 643.3249 | 541.7821 | 505.6653 | 492.9081
4713.176 | 645.0728 | 541.8685 | 506.4135 | 493.277
4714.176 | 643.07 | 541.2548 | 506.2836 | 493.3017
4715.176 | 643.8888 | 541.407 | 506.2989 | 494.4178
4716.176 | 641.5982 | 541.0287 | 506.3732 | 495.4918
4717.176 | 642.6171 | 541.1017 | 506.029 | 495.3099
4718.176 | 643.7618 | 541.3725 | 505.671 | 495.0353
4719.176 | 640.7129 | 541.4502 | 505.4322 | 494.5844
4720.176 | 644.4653 | 541.4872 | 504.9799 | 494.5771
4721.176 | 642.6991 | 540.4573 | 504.6414 | 494.6944
4722.176 | 642.7983 | 541.0052 | 504.8534 | 494.1724
4723.176 | 642.5384 | 540.6312 | 505.3908 | 493.6815
4724.176 | 642.0466 | 539.7352 | 505.3442 | 494.0575
4725.176 | 639.1498 | 539.0028 | 504.9208 | 494.1644
4726.176 | 639.3802 | 539.6495 | 504.9162 | 493.8606
4727.176 | 640.001 | 541.1452 | 504.5204 | 493.7756
4728.176 | 640.5151 | 540.1739 | 504.6828 | 493.7794
4729.176 | 639.1109 | 540.0053 | 504.8054 | 494.2245
4730.176 | 636.7235 | 541.0512 | 504.6188 | 493.7747
4731.176 | 640.197 | 541.9588 | 504.367 | 494.5267
4732.176 | 640.4251 | 541.9767 | 504.617 | 494.4835
4733.176 | 641.0571 | 543.178 | 505.0135 | 494.896
4734.176 | 642.0927 | 543.5918 | 505.4567 | 494.58
4735.176 | 644.6187 | 543.2643 | 505.3771 | 495.2181
4736.176 | 641.8817 | 543.7651 | 505.3601 | 495.673
4737.176 | 643.1907 | 544.9983 | 505.79 | 495.762
4738.176 | 644.6065 | 546.5113 | 506.4147 | 495.7994
4739.176 | 649.5581 | 547.5576 | 506.3892 | 495.8733
4740.176 | 652.0941 | 547.3892 | 506.5101 | 495.8746
4741.176 | 663.7227 | 546.7479 | 506.2664 | 495.4282
4742.176 | 668.7025 | 547.2095 | 506.1625 | 495.4877
4743.176 | 666.8068 | 546.6554 | 505.8134 | 495.4652
4744.176 | 671.1248 | 546.7916 | 506.1036 | 496.0984
4745.176 | 664.4023 | 545.9494 | 506.2322 | 496.3943
4746.176 | 662.0484 | 545.6702 | 506.508 | 497.0769
4747.176 | 659.2642 | 546.4198 | 506.8068 | 496.9268
4748.176 | 662.0616 | 546.2993 | 506.557 | 497.1863
4749.176 | 662.465 | 546.8469 | 506.9032 | 497.1919
4750.176 | 662.3186 | 546.647 | 507.1752 | 497.0229
4751.176 | 659.187 | 546.3105 | 507.447 | 496.8857
4752.176 | 658.0469 | 546.024 | 507.4955 | 497.5157
4753.176 | 655.7968 | 547.089 | 507.6674 | 497.6542
4754.176 | 659.2808 | 547.3374 | 507.4416 | 497.1701
4755.176 | 659.6161 | 546.6281 | 507.5184 | 496.6898
4756.176 | 659.3972 | 546.9413 | 507.4831 | 495.9467
4757.176 | 662.4526 | 546.7075 | 507.0885 | 495.7382
4758.176 | 662.0191 | 546.5821 | 506.7964 | 495.5434
4759.176 | 660.1551 | 545.8585 | 506.6201 | 495.8038
4760.176 | 658.2904 | 545.0666 | 507.4416 | 495.4234
4761.176 | 658.8876 | 544.1379 | 508.3361 | 495.4567
4762.176 | 659.2429 | 544.4108 | 508.7261 | 495.6438
4763.176 | 658.7772 | 544.2036 | 509.9039 | 495.2724
4764.176 | 659.183 | 545.1605 | 510.484 | 495.1678
4765.176 | 661.4877 | 545.1949 | 511.5285 | 494.7913
4766.176 | 659.1228 | 545.5861 | 512.7413 | 494.2049
4767.176 | 660.5451 | 546.8213 | 513.0018 | 493.6784
4768.176 | 666.2428 | 546.5865 | 515.2877 | 494.3005
4769.176 | 670.3095 | 546.101 | 516.5343 | 493.9226
4770.176 | 673.0824 | 545.125 | 517.112 | 493.793
4771.176 | 675.1513 | 544.1266 | 517.1684 | 494.0511
4772.176 | 674.497 | 544.0206 | 517.4035 | 494.4097
4773.176 | 672.9361 | 542.5614 | 518.2534 | 494.6371
4774.176 | 671.2247 | 541.5044 | 518.3558 | 494.0635
4775.176 | 669.6798 | 541.9902 | 518.1871 | 494.1127
4776.176 | 669.32 | 541.5038 | 517.7248 | 493.7509
4777.176 | 665.5786 | 541.4973 | 518.101 | 493.4465
4778.176 | 664.6114 | 541.5036 | 518.6145 | 494.4126
4779.176 | 662.4592 | 541.7885 | 520.2033 | 494.175
4780.176 | 665.3476 | 541.4631 | 520.2944 | 493.6975
4781.176 | 669.0389 | 542.5428 | 519.5289 | 494.0893
4782.176 | 670.5565 | 543.3538 | 519.4337 | 493.9836
4783.176 | 668.4751 | 544.6621 | 519.9058 | 494.1919
4784.176 | 671.6278 | 544.487 | 519.4743 | 494.5765
4785.176 | 673.0723 | 545.058 | 519.0198 | 494.6186
4786.176 | 676.6254 | 545.911 | 518.4503 | 494.4963
4787.176 | 681.2327 | 546.3831 | 517.9956 | 494.5633
4788.176 | 682.8138 | 545.6169 | 517.3401 | 494.386
4789.176 | 678.1985 | 544.7053 | 516.3697 | 494.1851
4790.176 | 676.0314 | 545.5383 | 515.3122 | 494.7021
4791.176 | 672.519 | 544.9301 | 514.609 | 494.8013
4792.176 | 666.8471 | 544.8187 | 514.043 | 495.4674
4793.176 | 665.3141 | 544.2685 | 513.6662 | 495.6724
4794.176 | 667.6815 | 544.35 | 513.2079 | 495.3687
4795.176 | 665.8152 | 544.8885 | 512.9723 | 494.7736
4796.176 | 667.0172 | 545.4368 | 513.0778 | 494.5559
4797.176 | 666.615 | 545.5032 | 513.2358 | 495.1448
4798.176 | 668.9325 | 544.9254 | 513.5932 | 495.2767
4799.176 | 670.3013 | 544.0161 | 514.1634 | 496.0329
4800.176 | 671.745 | 543.0398 | 515.0677 | 496.0949
4801.176 | 670.1582 | 542.6769 | 514.8765 | 496.3022
4802.176 | 667.6018 | 541.959 | 515.1084 | 496.125
4803.176 | 666.5367 | 542.0603 | 515.7887 | 495.6762
4804.176 | 667.6702 | 544.0657 | 516.6274 | 495.3813
4805.176 | 672.8548 | 545.0345 | 519.7866 | 495.4745
4806.176 | 671.722 | 545.821 | 522.4576 | 495.4315
4807.176 | 676.6415 | 546.6432 | 524.8929 | 495.2101
4808.176 | 676.4364 | 547.3498 | 526.8745 | 495.2816
4809.176 | 678.7824 | 548.088 | 527.4662 | 495.6991
4810.176 | 678.1108 | 549.1581 | 527.3883 | 496.2766
4811.176 | 677.6583 | 548.8871 | 528.0474 | 496.5641
4812.176 | 674.9562 | 548.8952 | 528.6692 | 497.8847
4813.176 | 674.9166 | 548.4449 | 527.9193 | 498.059
4814.176 | 671.9602 | 548.0309 | 527.1034 | 498.6918
4815.176 | 668.2892 | 547.6212 | 526.6361 | 498.6323
4816.176 | 665.864 | 547.0826 | 525.8159 | 498.5349
4817.176 | 664.9494 | 546.0577 | 526.3923 | 498.2683
4818.176 | 661.9014 | 546.4164 | 526.2064 | 498.437
4819.176 | 659.6064 | 547.7479 | 525.4097 | 497.9815
4820.176 | 658.5355 | 549.2192 | 524.0064 | 498.2084
4821.176 | 659.6784 | 548.9876 | 523.2911 | 498.9595
4822.176 | 658.2801 | 547.8206 | 522.6745 | 499.384
4823.176 | 656.8426 | 548.1981 | 522.692 | 499.963
4824.176 | 656.3766 | 549.1938 | 522.8465 | 500.0666
4825.176 | 657.8325 | 549.593 | 522.7487 | 499.9543
4826.176 | 661.1247 | 549.6105 | 522.1436 | 499.9901
4827.176 | 668.1386 | 548.842 | 521.5425 | 499.8828
4828.176 | 676.6792 | 549.2801 | 520.7423 | 500.0408
4829.176 | 674.851 | 548.7313 | 520.4751 | 499.9211
4830.176 | 674.7269 | 549.1187 | 520.3507 | 500.6226
4831.176 | 672.306 | 548.5717 | 520.8403 | 500.5855
4832.176 | 669.4701 | 548.089 | 521.2249 | 500.7832
4833.176 | 666.8837 | 547.7873 | 521.4055 | 501.5542
4834.176 | 667.6493 | 547.5591 | 521.5242 | 501.2578
4835.176 | 665.4826 | 547.3758 | 521.2847 | 501.57
4836.176 | 663.8714 | 547.5017 | 520.6537 | 502.1647
4837.176 | 663.1651 | 547.0965 | 520.4337 | 502.6166
4838.176 | 668.237 | 546.9822 | 520.2917 | 503.0656
4839.176 | 672.6586 | 547.1082 | 519.7488 | 503.1177
4840.176 | 672.1365 | 547.0875 | 519.3728 | 503.3857
4841.176 | 673.5247 | 547.9821 | 518.666 | 503.0475
4842.176 | 674.432 | 548.4555 | 518.2731 | 503.0954
4843.176 | 673.04 | 547.8561 | 517.8366 | 504.4228
4844.176 | 671.2468 | 547.4663 | 517.3183 | 504.1888
4845.176 | 667.3143 | 547.8331 | 516.9176 | 503.6285
4846.176 | 667.1482 | 546.8678 | 516.3678 | 502.8462
4847.176 | 666.3521 | 546.0637 | 517.2496 | 502.1903
4848.176 | 671.7911 | 545.4847 | 518.0891 | 501.4589
4849.176 | 676.637 | 545.258 | 518.7366 | 501.5932
4850.176 | 672.9942 | 544.2148 | 518.758 | 501.5306
4851.176 | 675.2827 | 543.4846 | 519.7479 | 502.3187
4852.176 | 672.2708 | 544.0387 | 519.4823 | 502.5559
4853.176 | 670.3291 | 545.0575 | 519.6102 | 502.2104
4854.176 | 668.3325 | 546.6367 | 519.6288 | 502.4575
4855.176 | 667.682 | 546.9232 | 520.1805 | 502.555
4856.176 | 668.8042 | 546.4829 | 521.4636 | 502.0603
4857.176 | 670.8693 | 547.2567 | 522.5543 | 502.12
4858.176 | 670.4309 | 547.1488 | 522.8444 | 502.3979
4859.176 | 670.0838 | 547.9284 | 522.4824 | 502.1504
4860.176 | 666.9547 | 547.7727 | 521.8328 | 502.0773
4861.176 | 663.0101 | 547.9128 | 520.9632 | 502.3312
4862.176 | 660.1562 | 548.1376 | 520.8052 | 502.429
4863.176 | 658.0322 | 547.8815 | 520.4973 | 502.4767
4864.176 | 656.6972 | 546.7876 | 520.0267 | 502.4478
4865.176 | 655.8172 | 546.753 | 520.5821 | 502.3751
4866.176 | 655.5713 | 547.0395 | 520.8177 | 502.2886
4867.176 | 651.8376 | 547.8268 | 520.7552 | 502.2081
4868.176 | 655.7565 | 547.109 | 521.445 | 502.2978
4869.176 | 656.7333 | 546.928 | 522.2099 | 502.859
4870.176 | 658.3646 | 546.4076 | 521.3889 | 502.9045
4871.176 | 665.291 | 546.0864 | 521.188 | 502.5887
4872.176 | 665.9205 | 547.3049 | 520.5709 | 502.2983
4873.176 | 667.5181 | 548.8226 | 520.4836 | 501.9582
4874.176 | 666.16 | 548.064 | 519.9915 | 501.6232
4875.176 | 664.977 | 548.0805 | 519.7329 | 501.5669
4876.176 | 663.2871 | 548.0481 | 519.4435 | 502.5033
4877.176 | 661.3567 | 547.1145 | 519.5307 | 502.3217
4878.176 | 658.6704 | 546.8203 | 519.2921 | 502.2689
4879.176 | 656.3945 | 547.1912 | 518.9713 | 502.3843
4880.176 | 653.752 | 547.9888 | 518.8931 | 503.2024
4881.176 | 653.0554 | 547.9902 | 519.5346 | 503.3536
4882.176 | 654.4547 | 546.8568 | 520.1762 | 503.0233
4883.176 | 653.9023 | 546.3652 | 520.3286 | 503.9188
4884.176 | 652.8218 | 546.2965 | 520.3037 | 504.0189
4885.176 | 651.1985 | 546.7062 | 520.4708 | 504.2
4886.176 | 649.9416 | 547.073 | 521.0246 | 504.469
4887.176 | 650.3077 | 547.394 | 521.6646 | 504.3289
4888.176 | 652.4141 | 547.4217 | 522.1859 | 503.9569
4889.176 | 651.764 | 546.5201 | 521.8988 | 504.0388
4890.176 | 650.6936 | 546.0187 | 522.8141 | 504.2682
4891.176 | 651.0547 | 546.3521 | 522.897 | 504.422
4892.176 | 652.6396 | 546.2404 | 522.5401 | 504.9499
4893.176 | 653.1928 | 546.4107 | 522.0059 | 504.8237
4894.176 | 651.2518 | 545.46 | 521.1421 | 504.6097
4895.176 | 648.9515 | 544.9803 | 520.62 | 505.0333
4896.176 | 648.2945 | 546.1377 | 520.4107 | 505.0057
4897.176 | 648.2391 | 546.4659 | 520.4422 | 504.9284
4898.176 | 648.1614 | 547.007 | 520.1868 | 505.2892
4899.176 | 646.8358 | 547.0668 | 520.0321 | 505.4255
4900.176 | 646.0671 | 547.2951 | 519.9171 | 505.3657
4901.176 | 646.538 | 546.7316 | 519.6033 | 505.4481
4902.176 | 647.5305 | 545.801 | 519.7167 | 505.5011
4903.176 | 647.6681 | 546.7195 | 519.9453 | 506.0264
4904.176 | 647.5026 | 547.9607 | 520.7155 | 506.2791
4905.176 | 646.8597 | 548.0011 | 521.5605 | 506.6825
4906.176 | 646.6741 | 548.654 | 521.7247 | 507.5343
4907.176 | 646.6442 | 548.5581 | 521.9062 | 507.8483
4908.176 | 649.6703 | 548.3131 | 522.0759 | 508.2096
4909.176 | 650.6336 | 548.0431 | 521.8834 | 508.2671
4910.176 | 648.9857 | 549.4153 | 521.6989 | 508.2172
4911.176 | 647.458 | 549.516 | 522.3116 | 508.2084
4912.176 | 648.7238 | 549.551 | 522.7264 | 508.208
4913.176 | 652.7845 | 549.0704 | 522.6748 | 508.4466
4914.176 | 653.8314 | 548.3839 | 522.9311 | 508.8088
4915.176 | 654.9788 | 548.17 | 522.4845 | 508.4029
4916.176 | 656.5283 | 549.1561 | 521.8153 | 508.3365
4917.176 | 659.2157 | 550.1297 | 521.0111 | 508.1687
4918.176 | 662.5676 | 549.26 | 520.2314 | 508.2511
4919.176 | 664.1762 | 548.2789 | 519.547 | 508.2323
4920.176 | 663.693 | 548.1371 | 519.6236 | 508.3026
4921.176 | 661.5882 | 548.7212 | 519.9728 | 508.8057
4922.176 | 660.5283 | 547.9619 | 520.4741 | 508.5973
4923.176 | 660.0686 | 547.3543 | 520.4896 | 508.7622
4924.176 | 661.679 | 546.5101 | 520.7026 | 508.5647
4925.176 | 661.6909 | 545.4722 | 520.2533 | 508.9624
4926.176 | 660.5446 | 545.0704 | 519.6295 | 508.8567
4927.176 | 661.2414 | 545.8815 | 519.8213 | 508.6132
4928.176 | 665.3776 | 545.7378 | 520.1799 | 508.5494
4929.176 | 666.3017 | 544.2998 | 520.2991 | 508.7258
4930.176 | 669.1455 | 544.3153 | 519.915 | 508.1538
4931.176 | 669.0752 | 544.5407 | 519.9469 | 507.9461
4932.176 | 666.6972 | 545.6661 | 521.0311 | 507.8596
4933.176 | 665.9431 | 545.9924 | 522.0126 | 507.5986
4934.176 | 665.6697 | 546.1743 | 522.1452 | 507.3431
4935.176 | 663.8364 | 546.1762 | 521.8253 | 506.9582
4936.176 | 664.8415 | 545.6438 | 521.3927 | 506.8478
4937.176 | 665.7431 | 544.7682 | 520.9963 | 506.9006
4938.176 | 666.5116 | 544.5323 | 520.9341 | 507.4179
4939.176 | 667.8192 | 545.0161 | 520.8764 | 507.3417
4940.176 | 668.5838 | 544.9486 | 520.5924 | 507.3238
4941.176 | 667.5415 | 545.3302 | 520.7481 | 507.3934
4942.176 | 671.7753 | 544.7168 | 522.3477 | 507.0619
4943.176 | 676.7937 | 544.0141 | 524.1305 | 507.313
4944.176 | 678.3288 | 543.5979 | 525.5894 | 507.3964
4945.176 | 678.8097 | 543.4568 | 526.9543 | 507.57
4946.176 | 677.5649 | 544.4105 | 527.297 | 508.2844
4947.176 | 675.4254 | 543.7944 | 527.7966 | 508.4333
4948.176 | 679.8225 | 543.1208 | 527.5513 | 508.528
4949.176 | 682.5667 | 542.3882 | 527.9124 | 508.675
4950.176 | 683.4683 | 542.8226 | 527.3679 | 508.3469
4951.176 | 684.637 | 542.6532 | 526.4771 | 508.0315
4952.176 | 684.6462 | 542.4207 | 525.8863 | 507.7119
4953.176 | 686.4413 | 542.2224 | 526.6222 | 507.5272
4954.176 | 688.9338 | 541.5453 | 527.7977 | 506.9133
4955.176 | 688.6436 | 541.1301 | 528.4458 | 506.2311
4956.176 | 688.5383 | 540.9855 | 529.6787 | 505.9982
4957.176 | 688.3568 | 542.0333 | 531.7253 | 506.134
4958.176 | 687.1448 | 543.4613 | 533.7812 | 506.9438
4959.176 | 687.1304 | 544.0067 | 534.7928 | 507.0521
4960.176 | 686.0032 | 543.9367 | 534.8244 | 506.8587
4961.176 | 686.4269 | 544.4658 | 535.9785 | 507.2646
4962.176 | 683.0014 | 545.7964 | 536.6311 | 508.2483
4963.176 | 680.8717 | 545.4127 | 537.0847 | 508.2104
4964.176 | 677.9345 | 544.5805 | 537.7916 | 508.2689
4965.176 | 677.0418 | 544 | 537.2804 | 508.2966
4966.176 | 675.4404 | 544.1504 | 538.195 | 508.2173
4967.176 | 675.9382 | 544.3427 | 540.284 | 508.0749
4968.176 | 676.7887 | 543.4391 | 540.7371 | 508.0431
4969.176 | 673.1796 | 543.6838 | 540.7241 | 508.2516
4970.176 | 669.9309 | 544.1173 | 540.9001 | 508.2848
4971.176 | 667.0522 | 542.4864 | 540.5847 | 508.299
4972.176 | 665.5225 | 542.8707 | 540.0827 | 509.416
4973.176 | 662.4525 | 542.1415 | 539.4043 | 509.5205
4974.176 | 662.2503 | 541.7021 | 538.4753 | 509.3233
4975.176 | 663.7903 | 542.1499 | 537.8003 | 508.8993
4976.176 | 663.3262 | 542.8544 | 537.5924 | 508.5825
4977.176 | 660.8914 | 543.8657 | 536.8435 | 508.257
4978.176 | 657.9375 | 544.5104 | 536.3431 | 508.0668
4979.176 | 656.7351 | 542.9008 | 536.8548 | 508.5436
4980.176 | 655.4229 | 542.5899 | 536.2666 | 508.3355
4981.176 | 656.4741 | 542.9071 | 536.3354 | 508.1894
4982.176 | 655.0146 | 543.2998 | 536.6109 | 508.5282
4983.176 | 651.378 | 544.272 | 536.6545 | 508.3103
4984.176 | 650.9474 | 544.9228 | 535.5166 | 508.2948
4985.176 | 649.26 | 545.259 | 534.3504 | 508.1803
4986.176 | 650.5864 | 544.8461 | 533.1471 | 508.1743
4987.176 | 650.059 | 543.9138 | 532.2658 | 508.4145
4988.176 | 651.2792 | 543.6609 | 531.961 | 508.4618
4989.176 | 651.8075 | 543.7963 | 532.4411 | 508.5529
4990.176 | 654.2498 | 543.9547 | 532.7649 | 509.2371
4991.176 | 651.801 | 544.9733 | 532.6358 | 509.1283
4992.176 | 653.2676 | 545.5264 | 532.4255 | 509.7322
4993.176 | 652.2372 | 546.0184 | 534.3106 | 509.6672
4994.176 | 652.7299 | 545.4969 | 535.8655 | 509.8471
4995.176 | 653.4338 | 545.2024 | 535.5481 | 509.8526
4996.176 | 654.8108 | 544.7396 | 534.6378 | 510.177
4997.176 | 657.8972 | 544.3436 | 533.8066 | 510.2538
4998.176 | 658.9874 | 544.9891 | 533.3299 | 511.0513
4999.176 | 660.829 | 544.7592 | 533.1911 | 510.794
5000.176 | 664.586 | 545.4845 | 532.342 | 510.7693
5001.176 | 668.1509 | 545.2347 | 531.4859 | 510.8207
5002.176 | 670.3559 | 545.2855 | 530.9891 | 510.7963
5003.176 | 669.2393 | 545.3631 | 531.0181 | 510.6374
5004.176 | 664.412 | 545.2418 | 531.829 | 510.7752
5005.176 | 661.6868 | 543.9648 | 532.5828 | 510.5318
5006.176 | 662.5151 | 542.6838 | 533.049 | 510.3183
5007.176 | 662.1539 | 541.3408 | 532.4284 | 510.4052
5008.176 | 658.7384 | 540.5229 | 532.448 | 510.1096
5009.176 | 657.8137 | 540.9431 | 532.6728 | 510.6482
5010.176 | 657.6699 | 540.7934 | 533.45 | 510.4896
5011.176 | 656.2736 | 541.191 | 534.6829 | 511.1523
5012.176 | 655.2147 | 541.6291 | 535.5855 | 511.2379
5013.176 | 654.0178 | 540.9126 | 536.6304 | 511.2092
5014.176 | 653.5914 | 542.3584 | 537.3575 | 510.9444
5015.176 | 653.0421 | 542.9656 | 537.2534 | 510.8056
5016.176 | 651.1079 | 543.6527 | 536.4723 | 510.3468
5017.176 | 649.9611 | 543.4153 | 535.177 | 509.8638
5018.176 | 649.1786 | 543.3952 | 533.9169 | 509.8242
5019.176 | 649.9188 | 544.1744 | 532.6926 | 509.7371
5020.176 | 650.7476 | 543.9272 | 532.083 | 509.9601
5021.176 | 654.3224 | 543.5452 | 531.4531 | 509.9808
5022.176 | 654.1506 | 544.1122 | 530.4869 | 510.1341
5023.176 | 653.0452 | 544.9152 | 529.785 | 510.1943
5024.176 | 654.732 | 545.42 | 529.7582 | 509.8624
5025.176 | 654.9598 | 545.38 | 529.5526 | 509.805
5026.176 | 656.2346 | 544.7924 | 528.9384 | 510.537
5027.176 | 654.2223 | 544.4161 | 528.4368 | 510.6971
5028.176 | 653.5507 | 544.706 | 527.6328 | 510.9534
5029.176 | 653.0242 | 544.2361 | 526.8434 | 511.0902
5030.176 | 653.9382 | 543.6798 | 526.6292 | 511.4034
5031.176 | 654.3807 | 543.2901 | 526.3005 | 512.0398
5032.176 | 652.747 | 542.5713 | 525.9815 | 512.9892
5033.176 | 654.1796 | 542.6473 | 526.0523 | 512.9581
5034.176 | 654.4103 | 542.7434 | 525.9843 | 512.7639
5035.176 | 654.8849 | 542.5113 | 525.9929 | 513.4054
5036.176 | 656.218 | 542.4537 | 526.2121 | 513.795
5037.176 | 656.4968 | 541.912 | 526.4247 | 515.0726
5038.176 | 656.8577 | 541.4961 | 526.4041 | 515.1587
5039.176 | 661.3801 | 540.8583 | 525.9499 | 515.0256
5040.176 | 667.0944 | 539.8701 | 525.158 | 514.6477
5041.176 | 669.4843 | 539.478 | 524.7021 | 513.9903
5042.176 | 671.4042 | 540.7008 | 524.8315 | 513.3948
5043.176 | 671.4843 | 541.0528 | 524.6632 | 512.5065
5044.176 | 672.9418 | 540.7908 | 524.2861 | 512.0425
5045.176 | 671.2546 | 540.3802 | 524.102 | 511.7462
5046.176 | 670.6397 | 539.9791 | 524.3831 | 512.4051
5047.176 | 667.1947 | 540.5994 | 524.9275 | 512.7422
5048.176 | 664.0184 | 539.9243 | 525.9317 | 512.4843
5049.176 | 664.3273 | 539.401 | 526.2322 | 512.0857
5050.176 | 664.4329 | 539.7303 | 527.0226 | 511.6059
5051.176 | 667.0694 | 539.6291 | 527.8735 | 511.0858
5052.176 | 668.922 | 539.6888 | 529.0138 | 511.4401
5053.176 | 669.8 | 540.4451 | 529.423 | 511.7139
5054.176 | 669.6891 | 541.0078 | 529.4994 | 512.5892
5055.176 | 667.9022 | 541.3388 | 529.5436 | 512.6382
5056.176 | 665.3201 | 541.1266 | 529.751 | 512.4872
5057.176 | 670.4463 | 542.2276 | 530.4418 | 513.0733
5058.176 | 673.4849 | 541.4484 | 531.6296 | 513.6525
5059.176 | 671.9954 | 541.2685 | 531.9932 | 513.7942
5060.176 | 672.6766 | 541.6723 | 532.4701 | 513.5482
5061.176 | 673.0035 | 541.5716 | 533.2934 | 513.332
5062.176 | 673.8167 | 540.4346 | 534.2396 | 513.3876
5063.176 | 673.0676 | 539.6138 | 534.8344 | 512.8151
5064.176 | 671.1174 | 539.6845 | 536.1827 | 512.0673
5065.176 | 671.8044 | 539.1654 | 536.8976 | 511.7693
5066.176 | 672.7856 | 538.7992 | 536.5226 | 511.7144
5067.176 | 674.3683 | 538.5159 | 536.5864 | 511.6538
5068.176 | 673.8625 | 538.2909 | 536.6955 | 512.2067
5069.176 | 672.7019 | 538.2789 | 537.3107 | 513.0678
5070.176 | 671.937 | 537.3734 | 536.6261 | 513.4168
5071.176 | 670.3573 | 535.9308 | 535.7176 | 513.0285
5072.176 | 670.6191 | 534.8333 | 535.4779 | 513.4968
5073.176 | 672.3783 | 535.1539 | 535.3656 | 513.1765
5074.176 | 673.0643 | 535.3404 | 536.5929 | 513.2338
5075.176 | 670.9336 | 536.079 | 537.6248 | 512.9138
5076.176 | 673.6808 | 535.7534 | 538.0216 | 512.5272
5077.176 | 672.3654 | 535.2242 | 537.5495 | 511.9503
5078.176 | 677.229 | 534.5968 | 536.2282 | 511.8783
5079.176 | 677.0526 | 535.6282 | 536.3694 | 511.3677
5080.176 | 676.4939 | 536.6216 | 536.0429 | 511.1354
5081.176 | 676.4409 | 536.5912 | 535.0056 | 511.0256
5082.176 | 675.0165 | 536.3086 | 534.6293 | 510.8363
5083.176 | 671.1715 | 536.1207 | 534.2917 | 510.948
5084.176 | 670.5682 | 536.4339 | 534.088 | 510.9868
5085.176 | 668.6057 | 536.7813 | 534.0178 | 511.4166
5086.176 | 665.1164 | 536.7486 | 534.0651 | 511.4756
5087.176 | 662.288 | 537.0272 | 534.0818 | 511.2512
5088.176 | 660.0401 | 537.1442 | 534.0043 | 511.0151
5089.176 | 654.3469 | 536.5935 | 534.9026 | 511.17
5090.176 | 656.9232 | 536.7187 | 535.1628 | 510.9625
5091.176 | 655.0723 | 537.8072 | 535.4657 | 511.1259
5092.176 | 652.4681 | 537.5654 | 535.0408 | 510.9308
5093.176 | 648.6637 | 536.9397 | 534.2492 | 510.6899
5094.176 | 650.9895 | 538.8207 | 533.3758 | 510.6949
5095.176 | 654.1395 | 538.4577 | 532.2578 | 510.2256
5096.176 | 653.5348 | 538.7892 | 530.9855 | 510.0481
5097.176 | 651.5751 | 539.7656 | 530.3368 | 510.1371
5098.176 | 646.8079 | 538.8461 | 531.0986 | 510.0905
5099.176 | 653.8128 | 537.8261 | 531.693 | 509.992
5100.176 | 654.2901 | 536.9418 | 531.595 | 509.9851
5101.176 | 655.798 | 536.0928 | 530.4749 | 510.07
5102.176 | 650.118 | 535.5593 | 529.7701 | 510.4374
5103.176 | 651.23 | 536.0831 | 530.0115 | 510.4311
5104.176 | 649.1258 | 535.1386 | 529.7717 | 510.7492
5105.176 | 653.5295 | 535.1732 | 530.1476 | 511.0173
5106.176 | 652.379 | 537.4183 | 530.8031 | 511.3972
5107.176 | 652.9945 | 537.4555 | 530.5843 | 512.0269
5108.176 | 651.8113 | 537.5977 | 530.2977 | 511.873
5109.176 | 651.3629 | 538.4415 | 529.9272 | 511.7956
5110.176 | 651.882 | 539.752 | 530.4443 | 511.7577
5111.176 | 648.4303 | 540.1924 | 530.2982 | 512.0285
5112.176 | 654.8657 | 540.423 | 530.7106 | 512.7027
5113.176 | 649.8461 | 540.7759 | 531.3255 | 513.2151
5114.176 | 650.5147 | 541.7039 | 531.0059 | 513.7103
5115.176 | 648.3936 | 544.2584 | 531.1945 | 513.4473
5116.176 | 656.8081 | 544.4139 | 532.1117 | 513.9881
5117.176 | 653.7192 | 543.7748 | 532.1853 | 514.3799
5118.176 | 654.2033 | 543.1163 | 532.1352 | 514.599
5119.176 | 650.0285 | 543.0032 | 532.0441 | 514.7431
5120.176 | 649.9105 | 542.6739 | 531.5114 | 514.4626
5121.176 | 642.0324 | 542.0065 | 530.8706 | 513.8566
5122.176 | 646.818 | 541.9136 | 530.415 | 513.4413
5123.176 | 642.2625 | 541.3527 | 530.0537 | 513.0895
5124.176 | 644.8727 | 541.1192 | 529.6809 | 512.8831
5125.176 | 643.5291 | 542.5058 | 529.1288 | 513.0025
5126.176 | 641.9028 | 543.2321 | 528.5865 | 513.0892
5127.176 | 635.3584 | 542.4601 | 527.9831 | 512.8798
5128.176 | 640.467 | 542.6593 | 527.3758 | 512.6003
5129.1917 | 641.8741 | 542.029 | 527.345 | 512.1186
5130.176 | 642.0982 | 542.5221 | 527.4964 | 511.8953
5131.176 | 640.7695 | 543.7083 | 527.3337 | 511.9957
5132.176 | 639.4828 | 544.3568 | 526.6333 | 511.7259
5133.176 | 637.1485 | 543.3419 | 526.0071 | 511.6616
5134.1917 | 638.9726 | 541.7811 | 525.3806 | 511.9315
5135.1917 | 641.777 | 540.6768 | 524.9546 | 511.6885
5136.176 | 642.235 | 540.5331 | 524.579 | 511.2316
5137.176 | 641.4176 | 540.7782 | 524.3792 | 511.0828
5138.176 | 635.4993 | 540.328 | 524.2307 | 510.5887
5139.176 | 637.6497 | 542.5941 | 523.856 | 510.546
5140.176 | 636.8898 | 547.0972 | 524.03 | 510.3211
5141.176 | 634.2575 | 546.1765 | 525.085 | 510.1967
5142.176 | 631.7561 | 545.1687 | 525.3337 | 510.4275
5143.176 | 635.8713 | 545.2777 | 525.8226 | 510.3383
5144.176 | 635.5948 | 545.5852 | 525.6064 | 510.8262
5145.176 | 631.9938 | 545.4252 | 524.9971 | 510.5869
5146.176 | 639.5353 | 544.5716 | 524.3333 | 510.3643
5147.176 | 644.5835 | 542.9062 | 523.5482 | 510.2981
5148.176 | 644.3662 | 542.6675 | 523.0066 | 511.266
5149.176 | 647.749 | 542.4794 | 522.5169 | 511.484
5150.176 | 646.6749 | 542.8849 | 522.1251 | 511.4056
5151.176 | 648.1842 | 542.9183 | 521.4781 | 511.1944
5152.176 | 648.8233 | 542.2674 | 521.8621 | 510.7987
5153.176 | 646.8086 | 541.529 | 522.4768 | 510.7969
5154.176 | 649.4415 | 540.7046 | 522.1828 | 510.5062
5155.176 | 649.4386 | 540.0734 | 522.237 | 510.3972
5156.176 | 656.9837 | 539.4171 | 522.3278 | 510.095
5157.176 | 658.0693 | 538.6508 | 522.4905 | 510.085
5158.176 | 655.8099 | 538.0668 | 521.9384 | 509.9374
5159.176 | 657.7397 | 537.7653 | 521.492 | 509.8355
5160.176 | 656.9985 | 537.5716 | 521.2728 | 509.7443
5161.176 | 657.8279 | 537.306 | 521.5048 | 510.0414
5162.176 | 654.0199 | 537.6393 | 521.9244 | 509.8094
5163.176 | 662.573 | 539.1079 | 523.3829 | 510.3459
5164.176 | 664.6971 | 542.7589 | 524.6607 | 510.7449
5165.176 | 663.9509 | 542.4106 | 525.8261 | 511.5762
5166.176 | 664.6462 | 542.5012 | 526.8797 | 511.835
5167.176 | 668.8419 | 542.6744 | 528.1043 | 511.6975
5168.176 | 670.6781 | 542.3557 | 529.2222 | 511.6018
5169.176 | 667.9836 | 542.3155 | 529.7828 | 511.1788
5170.176 | 667.2814 | 541.9903 | 529.7187 | 510.8915
5171.176 | 672.5283 | 541.8961 | 529.2215 | 510.7322
5172.176 | 671.4746 | 541.1243 | 528.7233 | 510.6186
5173.176 | 666.9653 | 541.1783 | 528.4847 | 510.9082
5174.176 | 671.6066 | 540.0951 | 529.5443 | 511.1045
5175.176 | 676.8772 | 540.0925 | 530.051 | 511.843
5176.176 | 678.8772 | 540.6448 | 530.3333 | 512.2341
5177.176 | 681.1141 | 540.5037 | 530.3338 | 512.2357
5178.176 | 681.5573 | 540.3394 | 530.5008 | 512.4279
5179.176 | 681.2431 | 539.773 | 531.1556 | 513.2182
5180.176 | 679.4916 | 539.3091 | 532.2241 | 513.4383
5181.176 | 678.3311 | 539.0136 | 532.2089 | 513.2291
5182.176 | 678.269 | 537.4928 | 530.9833 | 512.4366
5183.176 | 677.7349 | 537.5268 | 531.4408 | 512.7335
5184.176 | 675.6982 | 536.1099 | 530.9867 | 512.9673
5185.176 | 676.5986 | 535.6036 | 530.6687 | 512.9685
5186.176 | 675.1117 | 534.7182 | 532.3323 | 512.6489
5187.176 | 676.5062 | 534.6354 | 533.766 | 512.4216
5188.176 | 673.5567 | 535.0446 | 535.7536 | 512.6603
5189.176 | 674.1495 | 535.7762 | 536.0385 | 512.095
5190.176 | 673.2721 | 535.7545 | 537.6122 | 511.4817
5191.176 | 673.7048 | 536.8586 | 538.9879 | 511.6048
5192.176 | 674.2874 | 537.1292 | 539.9416 | 512.0655
5193.176 | 675.4781 | 537.1024 | 540.0005 | 511.8504
5194.176 | 681.0122 | 536.6614 | 539.0608 | 511.8958
5195.176 | 678.233 | 536.9234 | 539.0675 | 512.2777
5196.176 | 680.3225 | 536.8367 | 539.2379 | 513.6124
5197.176 | 674.3512 | 537.8168 | 539.7156 | 513.4362
5198.176 | 677.1329 | 536.8565 | 540.5657 | 514.2246
5199.176 | 677.2096 | 536.0542 | 541.3485 | 514.7735
5200.176 | 678.8156 | 536.2256 | 542.0125 | 514.3034
5201.176 | 675.6086 | 535.5522 | 541.2941 | 513.8978
5202.176 | 673.7243 | 535.1561 | 540.4087 | 513.3792
5203.176 | 675.5304 | 535.0124 | 540.5962 | 512.5908
5204.176 | 674.9637 | 535.2835 | 541.4896 | 512.0349
5205.176 | 673.2929 | 535.5993 | 542.3028 | 512.0805
5206.176 | 672.7118 | 535.6008 | 543.7775 | 511.8834
5207.176 | 672.8568 | 535.5728 | 544.1686 | 511.9127
5208.176 | 671.5001 | 535.6914 | 543.5141 | 512.6888
5209.176 | 671.9882 | 535.3108 | 541.4693 | 513.1983
5210.176 | 670.0682 | 534.6458 | 539.7985 | 513.1073
5211.176 | 667.2044 | 533.8944 | 538.6756 | 512.6637
5212.176 | 667.308 | 533.9554 | 538.0393 | 512.3979
5213.176 | 665.1018 | 533.7379 | 538.0558 | 512.3623
5214.176 | 664.9964 | 533.7391 | 537.9529 | 512.0969
5215.176 | 664.2619 | 534.0016 | 537.7486 | 511.5719
5216.176 | 661.5701 | 534.0131 | 538.8068 | 511.2885
5217.176 | 660.3972 | 533.0312 | 538.139 | 511.2345
5218.176 | 660.6188 | 532.2146 | 537.3356 | 511.1652
5219.176 | 658.8028 | 531.337 | 536.9391 | 511.0783
5220.176 | 655.6827 | 531.1937 | 536.4743 | 510.9702
5221.176 | 655.8547 | 531.1911 | 536.6766 | 510.3992
5222.176 | 653.8506 | 530.9426 | 536.1135 | 509.9221
5223.176 | 649.4701 | 530.4424 | 535.3435 | 509.7813
5224.176 | 645.5935 | 529.6974 | 534.4365 | 509.8062
5225.176 | 644.5701 | 529.6418 | 534.0575 | 509.6004
5226.176 | 642.8505 | 529.7371 | 533.4409 | 510.1433
5227.176 | 641.4504 | 528.942 | 532.3693 | 510.0799
5228.176 | 641.9489 | 529.0936 | 531.1576 | 509.9525
5229.176 | 646.2071 | 528.9486 | 531.6154 | 509.3887
5230.176 | 646.9088 | 528.7763 | 532.0096 | 509.0058
5231.176 | 647.2406 | 528.7836 | 532.1407 | 509.1224
5232.176 | 646.5077 | 529.8405 | 533.1723 | 509.5238
5233.176 | 645.3782 | 531.3232 | 533.4994 | 509.9803
5234.176 | 642.7908 | 530.7792 | 533.2586 | 510.3388
5235.176 | 640.5272 | 531.2105 | 534.0964 | 510.2193
5236.176 | 641.3926 | 531.8035 | 534.9773 | 510.1812
5237.176 | 640.2841 | 531.6929 | 535.9845 | 509.9343
5238.176 | 638.7696 | 531.0757 | 537.2937 | 509.3333
5239.176 | 636.9989 | 530.3731 | 537.5546 | 509.301
5240.176 | 633.8726 | 530.1998 | 536.8297 | 509.4698
5241.176 | 630.9396 | 529.8745 | 536.6536 | 509.7304
5242.176 | 628.2541 | 529.4672 | 536.3473 | 510.2063
5243.176 | 629.0088 | 528.6022 | 535.1713 | 510.4901
5244.176 | 629.2729 | 528.2958 | 534.428 | 510.3723
5245.176 | 628.9532 | 528.5771 | 533.7151 | 510.0777
5246.176 | 628.4434 | 528.1326 | 533.2461 | 509.3829
5247.176 | 632.2396 | 528.2955 | 532.3063 | 508.9745
5248.176 | 634.8226 | 527.9427 | 531.868 | 508.5896
5249.176 | 634.7284 | 528.0855 | 531.5421 | 508.402
5250.176 | 636.2188 | 528.9428 | 532.0239 | 508.3806
5251.176 | 637.0064 | 529.2654 | 532.455 | 508.205
5252.176 | 636.8218 | 530.4999 | 533.0971 | 508.4957
5253.176 | 634.5334 | 531.6379 | 532.693 | 508.9336
5254.176 | 632.1941 | 531.7989 | 532.9827 | 509.329
5255.176 | 631.2751 | 531.9228 | 533.1147 | 509.403
5256.176 | 630.4751 | 531.3141 | 532.5189 | 509.3303
5257.176 | 630.1458 | 530.9022 | 531.7964 | 509.4862
5258.176 | 630.016 | 531.0003 | 531.8361 | 510.0198
5259.176 | 632.5078 | 530.2825 | 531.0978 | 510.2891
5260.176 | 632.4558 | 529.6511 | 531.1148 | 510.316
5261.176 | 631.8358 | 529.2356 | 531.3594 | 509.8775
5262.176 | 631.5447 | 529.1636 | 530.5071 | 509.8553
5263.176 | 633.1445 | 528.9237 | 530.9054 | 509.6637
5264.176 | 632.3748 | 528.3074 | 531.7482 | 509.2706
5265.176 | 632.1782 | 527.9345 | 532.3565 | 509.6451
5266.176 | 634.3018 | 526.9376 | 532.3021 | 509.6139
5267.176 | 635.2251 | 526.3129 | 531.5652 | 509.4698
5268.176 | 635.2696 | 526.5289 | 532.0117 | 509.0402
5269.176 | 637.3751 | 526.0704 | 532.6798 | 508.3718
5270.176 | 638.5727 | 526.0848 | 533.9601 | 507.9826
5271.176 | 642.0988 | 526.4956 | 535.0013 | 507.8896
5272.176 | 645.3111 | 527.5577 | 535.3739 | 507.6429
5273.176 | 645.5535 | 529.9637 | 535.7398 | 507.4053
5274.176 | 648.2441 | 530.4535 | 536.001 | 507.172
5275.176 | 651.0132 | 531.8457 | 535.0067 | 506.9198
5276.176 | 654.2203 | 530.9127 | 534.9956 | 507.1865
5277.176 | 655.6836 | 530.3219 | 535.2784 | 507.3867
5278.176 | 657.3918 | 529.9591 | 535.1845 | 507.0648
5279.176 | 659.9581 | 529.5867 | 535.8391 | 507.0644
5280.176 | 659.4906 | 529.051 | 534.6038 | 506.5755
5281.176 | 659.8472 | 528.8789 | 533.4341 | 505.9147
5282.176 | 665.0326 | 528.8947 | 533.1868 | 505.6836
5283.176 | 664.4799 | 528.9617 | 531.988 | 506.0901
5284.176 | 664.0852 | 528.5714 | 531.0849 | 506.2838
5285.176 | 663.2453 | 528.0746 | 530.5316 | 506.448
5286.176 | 660.6091 | 528.3679 | 530.6809 | 506.4479
5287.176 | 658.1577 | 528.2591 | 529.5226 | 506.5668
5288.176 | 657.5555 | 527.7676 | 528.4538 | 506.6343
5289.176 | 656.13 | 526.9199 | 527.7337 | 506.9042
5290.176 | 660.0656 | 526.7656 | 527.7979 | 507.4275
5291.176 | 661.6949 | 526.1341 | 526.9614 | 507.4933
5292.176 | 660.844 | 525.2139 | 527.3393 | 507.3159
5293.176 | 661.5282 | 524.9037 | 527.2275 | 507.0568
5294.176 | 662.3711 | 526.2783 | 527.1414 | 506.6954
5295.176 | 660.3385 | 525.5123 | 527.0124 | 506.1916
5296.176 | 657.8642 | 525.1526 | 527.6315 | 505.9685
5297.176 | 654.8318 | 527.06 | 528.3298 | 505.5437
5298.176 | 654.1337 | 526.7666 | 529.3303 | 505.5041
5299.176 | 655.3998 | 526.9801 | 529.149 | 505.3582
5300.176 | 655.9664 | 527.3226 | 529.3829 | 505.1111
5301.176 | 659.5196 | 527.7514 | 529.4603 | 505.6178
5302.176 | 656.8061 | 527.7301 | 529.1747 | 506.1878
5303.176 | 656.2125 | 527.4489 | 528.9296 | 506.2558
5304.176 | 656.1987 | 527.4354 | 529.4361 | 505.8451
5305.1917 | 661.2054 | 528.7398 | 530.7562 | 505.1395
5306.176 | 660.7048 | 529.5474 | 530.8951 | 504.8922
5307.176 | 661.3678 | 529.2386 | 530.8248 | 505.0055
5308.176 | 661.6301 | 528.7621 | 531.2427 | 504.3232
5309.176 | 663.222 | 528.023 | 530.9888 | 503.6237
5310.176 | 666.5722 | 527.7256 | 530.0159 | 503.3942
5311.176 | 671.6184 | 526.6806 | 529.5732 | 504.1363
5312.176 | 675.7963 | 526.8462 | 530.5159 | 504.8954
5313.176 | 680.9082 | 527.3816 | 531.942 | 505.016
5314.176 | 684.649 | 526.6897 | 531.0525 | 506.2477
5315.176 | 686.31 | 526.3576 | 530.0431 | 507.111
5316.176 | 685.904 | 526.1661 | 530.0714 | 508.0833
5317.176 | 685.5268 | 525.406 | 529.4414 | 507.7592
5318.176 | 687.4219 | 524.8098 | 529.4576 | 508.1079
5319.176 | 689.9153 | 524.6902 | 529.9122 | 508.876
5320.176 | 687.7374 | 524.4508 | 529.368 | 509.6083
5321.176 | 691.2276 | 523.8995 | 528.2829 | 509.2371
5322.176 | 695.0467 | 524.9109 | 527.6534 | 508.6298
5323.176 | 697.7807 | 526.6861 | 528.5875 | 508.6452
5324.176 | 698.7105 | 527.0045 | 528.2284 | 508.5227
5325.176 | 700.237 | 525.4061 | 526.7627 | 508.1156
5326.176 | 700.049 | 523.8281 | 526.5045 | 507.6744
5327.176 | 699.2153 | 522.9533 | 527.4545 | 507.8802
5328.176 | 700.1601 | 522.5685 | 527.3458 | 507.5999
5329.176 | 698.703 | 521.4911 | 527.0419 | 506.9374
5330.176 | 699.3639 | 520.568 | 528.1132 | 506.6598
5331.176 | 700.6871 | 521.9532 | 527.9909 | 506.5015
5332.176 | 700.3514 | 521.2876 | 527.7577 | 506.2989
5333.176 | 703.1493 | 520.3332 | 529.0207 | 505.7103
5334.176 | 704.7368 | 521.1544 | 529.1288 | 505.7457
5335.1917 | 709.6684 | 520.7725 | 529.1902 | 506.1161
5336.176 | 712.4251 | 520.84 | 529.1355 | 507.0788
5337.176 | 715.96 | 520.9444 | 528.0787 | 508.1818
5338.176 | 718.8792 | 521.9206 | 527.6649 | 507.7247
5339.176 | 720.5001 | 521.0553 | 527.0187 | 507.6497
5340.176 | 723.9776 | 520.7172 | 526.4873 | 508.6203
5341.176 | 723.4844 | 520.292 | 526.1785 | 509.3656
5342.176 | 722.5947 | 520.5341 | 525.8388 | 509.2685
5343.176 | 724.2014 | 521.0043 | 525.7699 | 508.6992
5344.176 | 724.3049 | 520.854 | 526.1409 | 508.1103
5345.176 | 722.5927 | 520.7535 | 525.6701 | 507.6435
5346.176 | 718.1902 | 521.4852 | 524.9204 | 507.1041
5347.176 | 716.1762 | 521.6671 | 523.9527 | 506.5454
5348.176 | 714.4476 | 521.2388 | 523.4367 | 506.4816
5349.176 | 713.8325 | 522.5933 | 524.9788 | 506.3638
5350.176 | 712.9235 | 522.2408 | 524.8226 | 505.8495
5351.176 | 714.0822 | 521.8245 | 524.6251 | 505.473
5352.176 | 716.5945 | 521.4554 | 524.9038 | 505.9327
5353.176 | 715.4571 | 520.514 | 524.6934 | 507.8034
5354.176 | 713.8985 | 520.2881 | 524.1917 | 508.5223
5355.176 | 710.8484 | 520.2334 | 524.1106 | 508.9943
5356.176 | 709.3062 | 520.7365 | 524.0336 | 509.0259
5357.176 | 706.4333 | 520.6346 | 524.0978 | 508.1411
5358.176 | 703.6212 | 521.0619 | 524.5147 | 507.4175
5359.176 | 704.8436 | 521.5252 | 524.911 | 506.9389
5360.176 | 704.0262 | 521.0491 | 524.9787 | 506.5256
5361.176 | 703.7796 | 520.5252 | 524.6714 | 506.6726
5362.176 | 698.3795 | 520.47 | 524.0656 | 508.0091
5363.176 | 692.5253 | 520.0854 | 522.8523 | 509.0578
5364.176 | 686.4629 | 520.1251 | 521.6453 | 510.0973
5365.176 | 680.1889 | 520.3263 | 521.3351 | 510.0147
5366.176 | 676.9008 | 519.4977 | 521.2081 | 509.1613
5367.176 | 673.0248 | 518.4179 | 522.1915 | 508.2583
5368.176 | 667.6463 | 517.8795 | 522.8915 | 507.4046
5369.176 | 663.6774 | 517.4739 | 522.2352 | 506.8743
5370.176 | 659.7985 | 516.9777 | 522.216 | 507.1761
5371.176 | 657.0321 | 517.0941 | 522.5986 | 506.8592
5372.176 | 654.7789 | 516.9463 | 522.3929 | 507.153
5373.176 | 652.9249 | 517.1846 | 522.9118 | 506.8083
5374.176 | 652.442 | 517.3248 | 522.8301 | 506.5349
5375.176 | 652.5617 | 516.9825 | 523.8605 | 506.4992
5376.176 | 651.7446 | 517.0626 | 525.28 | 506.3396
5377.176 | 651.8157 | 517.4629 | 526.7071 | 505.9704
5378.176 | 650.8923 | 517.7665 | 528.1961 | 506.2193
5379.176 | 650.4761 | 518.4114 | 527.8 | 505.6386
5380.176 | 651.7073 | 518.3442 | 527.8607 | 505.3304
5381.176 | 652.814 | 518.8486 | 527.6501 | 506.0149
5382.176 | 652.7336 | 518.9863 | 527.4273 | 506.1176
5383.176 | 654.0404 | 518.541 | 526.8256 | 505.5625
5384.176 | 655.5149 | 518.3799 | 526.697 | 505.6172
5385.176 | 658.0727 | 518.4664 | 526.7794 | 506.1727
5386.176 | 658.9063 | 518.1697 | 526.6824 | 505.8604
5387.176 | 658.8952 | 517.9645 | 526.2033 | 505.2179
5388.176 | 657.1128 | 517.8491 | 526.6211 | 504.9347
5389.176 | 655.5322 | 517.4581 | 526.5185 | 505.1328
5390.176 | 654.4296 | 516.8824 | 526.3515 | 505.3768
5391.176 | 653.3557 | 516.1669 | 526.5924 | 505.1371
5392.176 | 651.1719 | 516.2477 | 526.209 | 504.5497
5393.176 | 650.3747 | 516.1458 | 525.568 | 504.3941
5394.176 | 650.3992 | 516.0898 | 525.348 | 504.2189
5395.1917 | 649.1511 | 516.0421 | 525.7174 | 504.7722
5396.176 | 648.1002 | 515.1911 | 526.0247 | 504.7969
5397.176 | 648.6888 | 514.8205 | 526.1169 | 505.1383
5398.176 | 648.5759 | 515.0268 | 526.2505 | 504.7612
5399.176 | 647.6076 | 515.0015 | 525.6543 | 505.0272
5400.176 | 645.7463 | 515.8313 | 524.9314 | 504.3128
5401.176 | 643.0176 | 516.4816 | 526.2536 | 503.8161
5402.176 | 640.397 | 517.0884 | 527.6065 | 503.3405
5403.176 | 639.5257 | 517.1742 | 527.9163 | 502.8803
5404.176 | 641.0205 | 517.0263 | 528.7358 | 502.2184
5405.176 | 644.3846 | 516.783 | 528.1737 | 502.0727
5406.176 | 645.0889 | 516.9308 | 527.7161 | 503.0209
5407.176 | 644.5343 | 517.1302 | 527.411 | 504.1488
5408.176 | 645.1828 | 517.299 | 527.2138 | 504.5241
5409.176 | 644.7316 | 517.7398 | 526.8702 | 504.3794
5410.176 | 645.0624 | 517.7982 | 525.9802 | 504.3921
5411.176 | 644.6402 | 517.5173 | 525.4456 | 504.4094
5412.176 | 644.4623 | 517.7185 | 525.4347 | 504.2335
5413.176 | 642.927 | 517.44 | 525.2033 | 503.9423
5414.176 | 642.3652 | 516.9505 | 525.5001 | 503.8195
5415.176 | 642.8637 | 516.2427 | 524.9733 | 503.7575
5416.176 | 645.4358 | 515.1744 | 525.6941 | 503.1933
5417.176 | 644.0723 | 514.1592 | 525.2037 | 503.4348
5418.176 | 642.8287 | 514.3901 | 524.5536 | 503.399
5419.176 | 641.0973 | 514.7003 | 524.0355 | 503.3274
5420.176 | 640.2762 | 514.5151 | 523.6314 | 503.1149
5421.176 | 641.8106 | 514.1291 | 523.2372 | 502.7261
5422.176 | 644.1508 | 513.8466 | 522.9835 | 502.5609
5423.176 | 645.5326 | 513.4681 | 521.843 | 502.6144
5424.176 | 647.5607 | 512.8637 | 521.4686 | 503.0093
5425.1917 | 655.6838 | 512.6228 | 522.3422 | 503.2535
5426.176 | 657.3394 | 512.5905 | 523.1723 | 503.3365
5427.176 | 657.5232 | 512.4096 | 523.4986 | 503.3107
5428.176 | 657.3854 | 512.566 | 522.4794 | 503.0893
5429.176 | 654.6957 | 512.4875 | 521.3752 | 502.7547
5430.176 | 655.5813 | 512.408 | 520.6581 | 502.1504
5431.176 | 654.6326 | 511.8616 | 520.66 | 501.4848
5432.176 | 655.8973 | 511.5348 | 521.3216 | 501.6561
5433.176 | 655.8172 | 511.6488 | 520.1674 | 501.2806
5434.176 | 657.9412 | 511.624 | 519.2587 | 500.5972
5435.176 | 660.9237 | 511.9568 | 519.7884 | 500.3236
5436.176 | 665.5278 | 513.3235 | 519.797 | 500.2415
5437.176 | 671.9391 | 513.5644 | 519.6694 | 499.9656
5438.176 | 673.9651 | 513.9906 | 519.0811 | 499.459
5439.176 | 675.2165 | 514.125 | 518.1041 | 499.8229
5440.176 | 678.8196 | 513.9592 | 517.4688 | 500.4753
5441.176 | 684.3345 | 514.2046 | 517.4356 | 500.3212
5442.176 | 686.4935 | 514.1367 | 518.1072 | 500.4032
5443.176 | 691.668 | 514.042 | 518.5924 | 500.3593
5444.176 | 696.9574 | 514.5553 | 518.8142 | 500.5298
5445.176 | 699.287 | 514.4057 | 518.63 | 501.3963
5446.176 | 703.2137 | 515.179 | 518.6488 | 501.4
5447.176 | 707.9156 | 515.1862 | 518.8663 | 501.9189
5448.176 | 713.0852 | 515.6275 | 520.6369 | 502.128
5449.176 | 715.7581 | 516.0857 | 521.3314 | 502.932
5450.176 | 715.8279 | 515.8157 | 521.8216 | 504.0649
5451.176 | 713.9731 | 515.487 | 521.1052 | 504.0182
5452.176 | 712.441 | 515.469 | 520.0867 | 504.4569
5453.176 | 710.0495 | 515.0392 | 519.1739 | 503.8249
5454.176 | 707.9893 | 515.2297 | 518.2108 | 503.6826
5455.176 | 708.8117 | 514.9796 | 517.1632 | 503.4839
5456.176 | 710.4765 | 514.8485 | 517.6821 | 503.0475
5457.176 | 709.8042 | 513.9581 | 517.2618 | 502.8576
5458.176 | 709.8439 | 513.205 | 516.9898 | 502.4508
5459.176 | 708.7403 | 512.6428 | 516.8496 | 501.9682
5460.176 | 707.9903 | 512.2264 | 517.512 | 502.0457
5461.176 | 705.6626 | 511.7412 | 517.1743 | 502.3357
5462.176 | 705.4192 | 511.0692 | 516.9232 | 503.0917
5463.176 | 705.9105 | 511.0588 | 516.8458 | 503.73
5464.176 | 703.725 | 511.5155 | 516.6939 | 503.2494
5465.176 | 701.4221 | 511.2147 | 516.26 | 503.6208
5466.176 | 699.0818 | 510.8155 | 515.4094 | 503.2433
5467.176 | 697.623 | 510.451 | 514.6718 | 502.6862
5468.176 | 695.7193 | 510.1688 | 514.4384 | 502.1128
5469.176 | 694.8658 | 510.4038 | 514.3041 | 502.0816
5470.176 | 693.9033 | 510.3498 | 514.0998 | 501.4503
5471.176 | 693.4755 | 509.3624 | 512.8402 | 501.0922
5472.176 | 692.4809 | 508.1325 | 511.6096 | 501.3846
5473.176 | 690.8797 | 508.028 | 510.9416 | 501.1646
5474.176 | 691.7715 | 507.601 | 510.7318 | 500.4809
5475.176 | 693.8131 | 507.0943 | 510.9671 | 500.0408
5476.176 | 695.118 | 506.5562 | 511.6831 | 499.9765
5477.176 | 695.9543 | 506.2091 | 511.2782 | 499.9974
5478.176 | 697.0137 | 506.0451 | 511.271 | 500.235
5479.176 | 696.9262 | 505.9713 | 512.5628 | 500.0257
5480.176 | 697.1451 | 505.9628 | 512.35 | 499.2939
5481.176 | 696.0604 | 506.1403 | 512.2904 | 498.8878
5482.176 | 694.8254 | 506.5829 | 513.2143 | 498.4195
5483.176 | 693.2938 | 507.336 | 514.2681 | 498.574
5484.176 | 690.1969 | 507.4701 | 515.6012 | 498.7317
5485.176 | 691.0863 | 507.9972 | 515.8921 | 499.2838
5486.176 | 689.1258 | 508.7918 | 515.9088 | 499.3867
5487.176 | 687.5032 | 508.9569 | 515.4506 | 498.9492
5488.176 | 688.548 | 508.9819 | 515.4711 | 498.5635
5489.176 | 686.8344 | 509.3532 | 515.4687 | 498.2585
5490.176 | 688.5548 | 509.4671 | 516.0454 | 498.3655
5491.176 | 688.5444 | 509.4084 | 516.1956 | 499.0659
5492.176 | 687.7772 | 508.7931 | 515.77 | 498.8833
5493.176 | 686.7446 | 508.5406 | 515.269 | 498.7541
5494.176 | 684.3257 | 508.8824 | 516.0794 | 498.5054
5495.176 | 684.8082 | 508.7943 | 516.9303 | 499.365
5496.176 | 685.9982 | 508.7986 | 518.1649 | 500.1209
5497.176 | 684.9853 | 508.3738 | 518.5826 | 499.832
5498.176 | 681.6974 | 508.5444 | 517.869 | 499.3402
5499.176 | 678.3415 | 509.0999 | 516.4259 | 498.9743
5500.176 | 677.1817 | 508.7579 | 514.9701 | 498.0618
5501.176 | 675.276 | 508.6967 | 513.9139 | 497.9339
5502.176 | 672.4983 | 508.5552 | 513.478 | 497.9871
5503.176 | 669.8879 | 508.7323 | 513.7282 | 497.7039
5504.176 | 669.4048 | 509.0825 | 513.0111 | 497.6607
5505.176 | 668.5641 | 509.0509 | 512.4116 | 497.4444
5506.176 | 667.3782 | 508.752 | 513.1684 | 496.9995
5507.176 | 667.7855 | 508.8772 | 513.5924 | 496.721
5508.176 | 671.8008 | 508.1135 | 512.9363 | 496.566
5509.176 | 672.1857 | 507.6055 | 513.1611 | 496.8064
5510.176 | 670.2344 | 507.2121 | 512.913 | 497.1384
5511.176 | 667.8492 | 507.3081 | 511.837 | 496.9012
5512.176 | 666.4721 | 506.8074 | 510.9162 | 496.4746
5513.176 | 665.3395 | 506.3181 | 510.1769 | 496.5455
5514.176 | 665.1669 | 505.473 | 510.0082 | 497.1372
5515.176 | 664.035 | 505.0951 | 510.1534 | 498.5699
5516.176 | 661.5316 | 505.0836 | 510.2215 | 498.7661
5517.176 | 661.1944 | 504.7021 | 511.1196 | 498.3692
5518.176 | 664.1873 | 504.3576 | 511.1726 | 497.7425
5519.176 | 667.3536 | 504.2743 | 511.4599 | 497.5821
5520.176 | 669.6231 | 504.3964 | 511.9664 | 497.596
5521.176 | 670.5806 | 504.5773 | 512.5208 | 497.6836
5522.176 | 672.6933 | 505.089 | 512.3737 | 497.2275
5523.176 | 675.6691 | 506.0768 | 512.6701 | 497.0213
5524.176 | 679.0552 | 506.7182 | 513.0133 | 496.775
5525.176 | 680.6662 | 506.6999 | 514.0653 | 496.254
5526.176 | 683.133 | 506.2487 | 514.0945 | 495.8268
5527.176 | 690.5079 | 506.0546 | 514.7197 | 495.8793
5528.176 | 693.2032 | 506.4453 | 514.7927 | 496.2128
5529.176 | 694.7502 | 506.8326 | 514.3462 | 498.0895
5530.176 | 696.5383 | 506.7203 | 514.7903 | 498.6681
5531.176 | 698.4323 | 507.0535 | 514.2516 | 498.8275
5532.176 | 700.5865 | 507.369 | 513.6959 | 498.7988
5533.176 | 699.8197 | 507.3995 | 515.0962 | 499.8914
5534.176 | 697.7099 | 507.4296 | 515.0243 | 500.2308
5535.176 | 695.3794 | 508.0403 | 515.4156 | 500.0277
5536.176 | 694.5743 | 508.7544 | 514.5273 | 499.5422
5537.176 | 695.4905 | 509.4169 | 513.4635 | 498.6629
5538.176 | 695.2103 | 509.2887 | 512.5176 | 497.9541
5539.176 | 694.5317 | 509.6461 | 512.2187 | 497.4534
5540.176 | 694.3251 | 509.7091 | 512.2162 | 496.9615
5541.176 | 691.3603 | 509.4189 | 512.4715 | 496.5539
5542.176 | 689.7634 | 509.2105 | 512.4113 | 496.4231
5543.176 | 689.7212 | 509.4913 | 514.367 | 496.0781
5544.176 | 688.2982 | 509.9226 | 516.2046 | 496.4708
5545.176 | 685.9153 | 510.1951 | 515.9318 | 496.8248
5546.176 | 683.9744 | 511.21 | 515.2462 | 496.7084
5547.176 | 681.7225 | 511.5727 | 515.2897 | 496.3261
5548.176 | 680.8314 | 511.7268 | 515.033 | 496.5794
5549.176 | 680.6036 | 512.0529 | 514.7233 | 497.1554
5550.176 | 678.5969 | 511.9181 | 515.8917 | 497.0217
5551.176 | 677.8539 | 512.0552 | 516.5272 | 497.0126
5552.176 | 676.8255 | 512.6159 | 516.7564 | 497.5978
5553.176 | 675.2766 | 513.2815 | 517.2091 | 496.9648
5554.176 | 672.868 | 513.9567 | 516.4778 | 496.2396
5555.176 | 672.0109 | 513.9062 | 516.9542 | 495.4901
5556.176 | 671.9956 | 514.2059 | 517.8762 | 494.9115
5557.176 | 672.1117 | 514.7811 | 517.4373 | 494.5189
5558.176 | 671.3728 | 513.8917 | 517.6283 | 494.2601
5559.176 | 669.7739 | 513.7828 | 517.3695 | 493.6554
5560.176 | 666.3281 | 513.3411 | 516.8269 | 493.3094
5561.176 | 666.1386 | 513.1956 | 516.1598 | 494.1177
5562.176 | 666.361 | 513.9391 | 516.1364 | 494.6779
5563.176 | 665.208 | 514.3003 | 515.8831 | 496.3687
5564.176 | 662.267 | 513.8829 | 515.12 | 495.7979
5565.176 | 658.6643 | 513.0083 | 513.8004 | 495.0983
5566.176 | 656.8265 | 512.5476 | 512.7359 | 495.1094
5567.176 | 655.2363 | 511.694 | 511.7321 | 495.0897
5568.176 | 655.0399 | 510.2438 | 510.8228 | 495.0028
5569.176 | 655.7542 | 509.2364 | 509.7454 | 494.7517
5570.176 | 654.7783 | 508.8788 | 509.3663 | 494.6239
5571.176 | 653.8993 | 508.9402 | 509.5234 | 494.1597
5572.176 | 652.5065 | 508.95 | 508.9209 | 493.7497
5573.176 | 650.8056 | 508.9711 | 508.0649 | 493.7213
5574.176 | 648.5265 | 508.3521 | 507.4215 | 493.6178
5575.176 | 648.1703 | 507.6562 | 506.9197 | 494.0718
5576.176 | 647.3737 | 507.8692 | 506.5268 | 494.2938
5577.176 | 646.6783 | 507.9566 | 506.8453 | 494.2997
5578.176 | 646.1422 | 507.735 | 507.3042 | 494.0114
5579.176 | 646.5864 | 507.6484 | 507.6814 | 493.881
5580.176 | 648.9682 | 507.8996 | 507.596 | 494.1518
5581.176 | 652.5947 | 507.9754 | 508.0821 | 494.382
5582.176 | 657.6707 | 507.8857 | 509.164 | 494.2502
5583.176 | 657.3851 | 508.3852 | 510.4235 | 494.8123
5584.176 | 656.7162 | 508.4962 | 511.1799 | 494.8091
5585.176 | 654.4201 | 508.204 | 511.6846 | 495.059
5586.176 | 653.8155 | 508.0485 | 511.5515 | 495.4979
5587.176 | 653.0114 | 509.4531 | 511.3192 | 496.2597
5588.176 | 654.0703 | 510.538 | 512.3337 | 495.9787
5589.176 | 655.815 | 510.7922 | 513.3291 | 496.1159
5590.176 | 656.3612 | 511.0149 | 512.8961 | 495.9631
5591.176 | 655.158 | 511.2911 | 512.6213 | 495.5365
5592.176 | 653.3871 | 511.9584 | 512.2564 | 495.3695
5593.176 | 652.8023 | 513.0975 | 513.9248 | 494.9718
5594.176 | 652.9151 | 514.3164 | 515.7103 | 495.641
5595.176 | 652.534 | 514.6401 | 515.8374 | 496.4041
5596.176 | 654.1899 | 515.086 | 515.8717 | 495.976
5597.176 | 655.105 | 515.8346 | 515.3766 | 495.7467
5598.176 | 655.5925 | 516.1019 | 514.5428 | 495.0863
5599.176 | 653.8861 | 516.2888 | 514.3393 | 494.8309
5600.176 | 652.2428 | 515.3093 | 513.843 | 494.4721
5601.176 | 650.5959 | 514.2972 | 513.234 | 494.5636
5602.176 | 649.1539 | 513.082 | 512.8913 | 494.85
5603.176 | 646.3864 | 511.852 | 512.9416 | 495.5003
5604.176 | 644.1023 | 510.367 | 512.2044 | 495.072
5605.176 | 641.9865 | 509.5098 | 512.3193 | 494.5809
5606.176 | 641.0441 | 508.6311 | 512.8709 | 494.4554
5607.176 | 641.8126 | 507.828 | 513.4196 | 493.9394
5608.176 | 639.8742 | 506.9744 | 513.5352 | 493.521
5609.176 | 640.4342 | 506.46 | 514.3724 | 493.3583
5610.176 | 641.5502 | 506.1376 | 514.8376 | 494.1238
5611.176 | 642.1753 | 506.7514 | 515.3547 | 494.6108
5612.176 | 643.6438 | 507.4029 | 514.6819 | 494.2952
5613.176 | 645.6883 | 507.6509 | 514.1368 | 493.8662
5614.176 | 648.7183 | 507.9444 | 514.4563 | 493.704
5615.176 | 650.2826 | 508.4237 | 513.5142 | 493.4725
5616.176 | 652.6337 | 508.6224 | 513.3952 | 492.9906
5617.176 | 658.4196 | 509.336 | 513.1449 | 492.8253
5618.176 | 664.6485 | 509.4569 | 513.8989 | 492.8076
5619.176 | 666.3466 | 509.2423 | 514.4381 | 492.5574
5620.176 | 668.2907 | 510.0683 | 513.7678 | 492.2094
5621.176 | 668.7969 | 510.9332 | 513.1294 | 491.8326
5622.176 | 670.3478 | 511.7096 | 512.9337 | 491.6381
5623.176 | 674.9293 | 511.9238 | 512.6958 | 491.6624
5624.176 | 677.9477 | 512.781 | 512.4555 | 491.8444
5625.176 | 681.3678 | 512.4701 | 512.3101 | 492.3504
5626.176 | 681.7209 | 512.2441 | 512.0368 | 492.8888
5627.2073 | 680.8862 | 511.9229 | 511.8518 | 493.4404
5628.176 | 680.2103 | 511.7821 | 511.7155 | 493.6704
5629.176 | 678.6854 | 511.6887 | 511.3395 | 493.4828
5630.176 | 681.4593 | 512.4553 | 511.4108 | 493.5657
5631.176 | 681.6943 | 513.0893 | 511.4259 | 493.7642
5632.176 | 681.98 | 512.7943 | 511.1626 | 494.2414
5633.176 | 681.5128 | 512.5803 | 510.8924 | 494.7407
5634.176 | 679.7398 | 512.7972 | 510.7703 | 494.9573
5635.176 | 679.2631 | 513.4724 | 510.8494 | 495.6385
5636.176 | 678.8354 | 514.0436 | 511.0205 | 495.8917
5637.176 | 676.4076 | 513.9424 | 510.8921 | 496.3759
5638.176 | 674.1696 | 513.4277 | 510.0604 | 496.8156
5639.176 | 671.1581 | 513.2474 | 509.4496 | 496.2834
5640.176 | 670.4568 | 513.0938 | 509.1533 | 496.6676
5641.176 | 670.2219 | 513.3769 | 509.3419 | 496.3689
5642.176 | 669.3942 | 513.4068 | 509.6512 | 496.6975
5643.176 | 668.7626 | 514.7287 | 510.211 | 498.2452
5644.176 | 669.128 | 515.0139 | 510.7178 | 498.1284
5645.176 | 673.161 | 514.3998 | 510.1137 | 497.4679
5646.176 | 673.7622 | 513.6109 | 509.4965 | 497.0603
5647.176 | 673.6608 | 513.5788 | 509.2024 | 497.1262
5648.176 | 674.4416 | 513.1545 | 509.3421 | 497.5483
5649.176 | 675.1444 | 513.0824 | 509.009 | 497.7298
5650.176 | 675.4995 | 512.8866 | 508.702 | 496.985
5651.176 | 674.6371 | 512.4925 | 509.0982 | 496.479
5652.176 | 677.5246 | 512.5294 | 509.0334 | 496.244
5653.176 | 682.163 | 513.0758 | 508.9981 | 496.491
5654.176 | 688.2137 | 512.725 | 508.5213 | 497.1574
5655.176 | 692.8093 | 512.1348 | 508.3338 | 498.0042
5656.176 | 696.6612 | 513.0796 | 508.173 | 498.1809
5657.176 | 696.1027 | 512.9792 | 508.0179 | 498.6323
5658.176 | 694.4352 | 513.0024 | 507.9194 | 499.3052
5659.176 | 692.3385 | 513.0193 | 508.8307 | 499.0069
5660.176 | 693.6622 | 512.6894 | 508.9586 | 499.1073
5661.176 | 697.352 | 512.608 | 510.4633 | 498.3718
5662.176 | 701.668 | 512.0737 | 510.8436 | 497.7011
5663.176 | 701.3977 | 511.7245 | 510.1476 | 496.8171
5664.176 | 699.0155 | 511.4714 | 510.7966 | 496.1514
5665.176 | 696.7986 | 511.6781 | 510.9424 | 496.4012
5666.176 | 693.4221 | 513.0124 | 511.0118 | 496.7602
5667.176 | 691.1518 | 513.1323 | 510.9624 | 497.2993
5668.176 | 694.2964 | 513.058 | 511.1841 | 497.0268
5669.176 | 698.4006 | 513.3418 | 511.1318 | 496.6769
5670.176 | 700.5425 | 512.8767 | 511.3457 | 496.3063
5671.176 | 702.3469 | 512.832 | 510.8109 | 495.8984
5672.176 | 703.7523 | 512.4285 | 510.7995 | 496.3644
5673.176 | 704.2461 | 512.3439 | 511.2762 | 496.5701
5674.176 | 702.0109 | 512.2246 | 512.1585 | 496.3067
5675.176 | 700.5596 | 512.4378 | 512.529 | 497.084
5676.176 | 699.5058 | 512.7464 | 513.6968 | 498.1535
5677.176 | 703.4409 | 512.3943 | 514.232 | 499.2822
5678.176 | 704.9581 | 512.3009 | 513.9929 | 499.8911
5679.176 | 703.0322 | 512.674 | 513.8333 | 500.6645
5680.176 | 699.8999 | 512.8965 | 513.9637 | 500.5167
5681.176 | 696.927 | 514.1787 | 515.7635 | 500.9126
5682.176 | 693.7279 | 514.3035 | 515.4654 | 500.7223
5683.176 | 690.2699 | 514.8458 | 515.1676 | 499.9727
5684.176 | 688.6875 | 514.3855 | 515.3523 | 499.61
5685.176 | 686.2715 | 514.5461 | 516.0992 | 499.1558
5686.176 | 686.1046 | 514.5463 | 516.7695 | 498.7839
5687.176 | 686.3164 | 515.2385 | 518.5548 | 498.6524
5688.176 | 685.6764 | 515.4987 | 518.5714 | 498.8007
5689.176 | 690.8252 | 515.5667 | 518.5813 | 499.9565
5690.176 | 692.2849 | 514.7424 | 518.4569 | 500.32
5691.176 | 692.4253 | 515.0631 | 518.5835 | 500.8792
5692.176 | 690.6268 | 514.9783 | 518.6719 | 501.3509
5693.176 | 687.2358 | 515.0337 | 518.068 | 502.1518
5694.176 | 684.4055 | 515.0696 | 517.5198 | 501.9944
5695.176 | 683.1808 | 514.8786 | 517.1479 | 501.4457
5696.176 | 682.754 | 515.0258 | 516.6815 | 501.7936
5697.176 | 685.9797 | 514.9995 | 516.2091 | 501.9251
5698.176 | 686.8993 | 515.2586 | 515.7886 | 501.4261
5699.176 | 684.1466 | 515.3037 | 516.6407 | 500.847
5700.176 | 680.8721 | 515.0769 | 516.1434 | 500.8369
5701.176 | 682.4155 | 515.503 | 516.001 | 500.2278
5702.176 | 686.7644 | 515.3403 | 516.3482 | 500.3121
5703.176 | 684.9715 | 515.3271 | 517.624 | 500.0124
5704.176 | 681.4182 | 515.4253 | 517.8821 | 499.6236
5705.176 | 680.6131 | 515.1383 | 517.0418 | 499.0286
5706.176 | 678.2941 | 515.1812 | 516.3746 | 499.0034
5707.176 | 676.6327 | 515.8966 | 516.1384 | 499.4376
5708.176 | 675.1015 | 516.5333 | 515.9869 | 500.0522
5709.176 | 673.9009 | 516.9672 | 515.7725 | 500.1919
5710.176 | 673.1953 | 516.5792 | 515.2047 | 501.1654
5711.176 | 670.2594 | 516.4162 | 515.2454 | 500.8474
5712.176 | 667.881 | 517.1811 | 514.9519 | 500.5696
5713.176 | 663.8789 | 517.9337 | 514.4758 | 500.9406
5714.176 | 661.0121 | 518.1892 | 513.8439 | 501.4392
5715.176 | 658.4878 | 517.6389 | 513.0541 | 500.1772
5716.176 | 657.2951 | 517.1093 | 512.32 | 500.2268
5717.176 | 668.0082 | 517.0588 | 512.0922 | 500.5561
5718.176 | 672.8208 | 516.4784 | 512.3407 | 500.918
5719.176 | 672.1578 | 516.3993 | 511.7065 | 500.3404
5720.176 | 668.9385 | 515.1254 | 510.9565 | 500.1384
5721.176 | 665.279 | 514.1191 | 510.3378 | 499.7542
5722.176 | 661.4328 | 513.5789 | 509.7528 | 499.6053
5723.176 | 660.9114 | 512.9794 | 509.4198 | 499.3917
5724.176 | 661.4528 | 512.3173 | 509.4246 | 499.2535
5725.176 | 661.5957 | 511.7131 | 509.1247 | 499.7372
5726.176 | 660.7692 | 511.4836 | 508.631 | 499.2492
5727.176 | 659.5867 | 511.4657 | 508.4859 | 498.2543
5728.176 | 658.5279 | 511.8967 | 509.0993 | 497.6604
5729.176 | 658.5324 | 511.2447 | 509.4238 | 497.3658
5730.176 | 663.1257 | 510.5362 | 510.3098 | 497.9473
5731.176 | 665.0366 | 509.9963 | 510.1838 | 497.4255
5732.176 | 666.0656 | 509.9564 | 509.6909 | 496.5082
5733.176 | 666.1439 | 509.6746 | 508.838 | 496.7042
5734.176 | 668.4064 | 509.2183 | 508.102 | 496.3212
5735.176 | 672.3344 | 508.5952 | 508.332 | 496.0995
5736.176 | 673.954 | 508.5069 | 507.9521 | 496.3151
5737.176 | 678.5473 | 508.0246 | 507.6654 | 495.568
5738.176 | 680.0414 | 507.7766 | 507.5268 | 495.8306
5739.176 | 683.5017 | 507.9388 | 508.4685 | 495.9692
5740.176 | 690.5801 | 507.5012 | 508.2503 | 495.0501
5741.176 | 695.2252 | 507.2443 | 508.4556 | 494.5469
5742.176 | 695.7866 | 507.7577 | 508.0259 | 494.2441
5743.176 | 692.9419 | 508.6659 | 508.0226 | 494.5191
5744.176 | 690.5594 | 508.6752 | 507.9488 | 494.6586
5745.176 | 690.6314 | 509.7546 | 507.5624 | 494.6239
5746.176 | 692.004 | 509.4487 | 507.5964 | 494.7909
5747.176 | 691.4277 | 509.3923 | 507.7199 | 494.6793
5748.176 | 693.4645 | 509.2633 | 507.7415 | 494.7792
5749.176 | 693.5244 | 508.909 | 507.9172 | 496.004
5750.176 | 695.5699 | 508.9166 | 508.548 | 495.9229
5751.176 | 696.6091 | 508.96 | 508.7162 | 497.4264
5752.176 | 693.5728 | 509.307 | 509.2382 | 497.9736
5753.176 | 687.8515 | 509.7348 | 519.2326 | 497.9356
5754.176 | 684.773 | 510.4887 | 532.3321 | 498.2427
5755.176 | 682.7341 | 510.9185 | 533.006 | 503.0366
5756.176 | 678.2367 | 510.9155 | 531.9195 | 515.9333
5757.176 | 675.8709 | 511.4787 | 531.6159 | 521.1523
5758.176 | 672.6641 | 512.4222 | 531.9556 | 525.2329
5759.176 | 669.9965 | 513.146 | 531.4872 | 527.1513
5760.176 | 668.5683 | 513.2055 | 530.4066 | 528.1549
5761.176 | 665.0015 | 513.0982 | 528.7166 | 528.4425
5762.176 | 664.8702 | 512.9105 | 527.4372 | 527.7294
5763.176 | 668.2639 | 512.1913 | 525.6861 | 527.5463
5764.176 | 673.6919 | 511.3124 | 524.1514 | 528.0292
5765.176 | 675.4134 | 510.8499 | 522.8753 | 530.426
5766.176 | 676.2637 | 509.7568 | 521.2541 | 530.0555
5767.176 | 681.0586 | 508.9875 | 519.5989 | 529.6834
5768.176 | 689.929 | 508.1581 | 518.2546 | 528.5091
5769.176 | 695.259 | 507.8399 | 517.4047 | 526.4891
5770.176 | 694.6524 | 507.6353 | 516.6445 | 524.3092
5771.176 | 691.6789 | 506.7916 | 515.9283 | 522.0378
5772.176 | 689.6038 | 506.5633 | 516.5105 | 519.9868
5773.176 | 688.7296 | 509.8026 | 517.6891 | 518.2511
5774.176 | 690.6257 | 511.6179 | 521.9135 | 517.4142
5775.176 | 695.5342 | 513.7007 | 525.9542 | 515.9431
5776.176 | 702.5712 | 514.5793 | 528.4578 | 514.4395
5777.176 | 702.8053 | 515.2337 | 529.3013 | 513.7232
5778.176 | 701.8969 | 516.7037 | 530.2274 | 512.6555
5779.176 | 698.5631 | 517.2775 | 531.2649 | 512.4681
5780.176 | 694.389 | 517.1403 | 535.4828 | 512.0242
5781.176 | 696.1001 | 518.5706 | 546.8104 | 511.4147
5782.176 | 695.2696 | 518.7223 | 547.2666 | 510.975
5783.176 | 693.0655 | 518.8035 | 545.5955 | 510.7804
5784.176 | 690.851 | 518.505 | 544.1238 | 510.3179
5785.176 | 690.1448 | 517.7706 | 541.4528 | 509.86
5786.176 | 690.414 | 517.5084 | 539.2767 | 509.3398
5787.176 | 691.726 | 517.1212 | 536.6014 | 508.8902
5788.176 | 688.2556 | 516.6991 | 534.1241 | 508.6112
5789.176 | 686.1987 | 516.4917 | 531.9341 | 507.107
5790.176 | 684.8264 | 516.2981 | 530.0534 | 505.8656
5791.176 | 682.0029 | 515.6503 | 528.5313 | 505.2398
5792.176 | 680.2457 | 516.0297 | 527.0233 | 505.0443
5793.176 | 680.1941 | 516.2039 | 525.7188 | 504.748
5794.176 | 683.7064 | 515.3902 | 524.53 | 504.3627
5795.176 | 681.5995 | 514.6804 | 523.3946 | 503.8197
5796.176 | 676.5451 | 514.284 | 521.9809 | 503.1442
5797.176 | 673.142 | 513.7137 | 520.5441 | 503.6523
5798.176 | 673.2732 | 513.2011 | 519.443 | 503.0875
5799.176 | 672.6291 | 513.2909 | 518.8257 | 502.9215
5800.176 | 671.3123 | 513.4768 | 518.0873 | 502.6121
5801.176 | 669.9155 | 514.1721 | 517.7934 | 502.6023
5802.176 | 666.3088 | 514.3709 | 517.8283 | 502.7257
5803.176 | 664.7704 | 514.297 | 518.1266 | 502.118
5804.176 | 663.4052 | 514.4196 | 517.1305 | 501.9494
5805.176 | 661.7199 | 514.7269 | 515.9603 | 501.9005
5806.176 | 661.0633 | 515.1857 | 515.2281 | 501.0557
5807.176 | 660.8133 | 515.3344 | 515.3517 | 500.0823
5808.176 | 663.5796 | 515.2059 | 515.0056 | 499.9026
5809.176 | 664.7636 | 514.8624 | 514.4949 | 499.8755
5810.176 | 668.3643 | 514.2557 | 514.5534 | 499.3738
5811.176 | 670.4115 | 513.5961 | 514.2552 | 500.0481
5812.176 | 673.3221 | 513.0228 | 513.441 | 500.0422
5813.176 | 675.4205 | 512.185 | 513.0578 | 499.9458
5814.176 | 674.5436 | 511.1962 | 512.6356 | 499.7605
5815.176 | 672.5883 | 510.38 | 511.6003 | 498.7214
5816.176 | 669.8413 | 509.7499 | 510.2959 | 497.8891
5817.176 | 667.0167 | 509.7828 | 509.2985 | 497.051
5818.176 | 664.4821 | 509.2903 | 509.6511 | 497.2348
5819.176 | 664.3647 | 508.5737 | 509.3165 | 496.7899
5820.176 | 665.5723 | 508.4739 | 508.9648 | 496.1986
5821.176 | 666.447 | 508.2554 | 508.4895 | 495.9049
5822.176 | 665.2176 | 507.903 | 508.3366 | 495.7598
5823.176 | 662.1198 | 507.4346 | 507.4175 | 495.4337
5824.176 | 659.5962 | 507.1554 | 506.9399 | 495.074
5825.176 | 655.7873 | 506.2068 | 506.1189 | 494.9352
5826.176 | 651.8502 | 505.0957 | 505.6334 | 494.5879
5827.176 | 649.3954 | 504.1283 | 504.9367 | 495.1876
5828.176 | 647.15 | 502.8713 | 504.1436 | 496.2067
5829.176 | 643.0677 | 501.9587 | 503.7058 | 496.2942
5830.176 | 639.4739 | 501.179 | 502.9704 | 496.047
5831.176 | 636.0655 | 500.7675 | 502.4967 | 495.9463
5832.176 | 635.3501 | 500.398 | 502.0821 | 495.2436
5833.176 | 634.1749 | 500.134 | 501.7383 | 494.6389
5834.176 | 634.7433 | 499.699 | 501.5466 | 494.2773
5835.176 | 635.3681 | 499.2138 | 502.8496 | 493.8235
5836.176 | 634.4011 | 498.7939 | 502.8798 | 493.4034
5837.176 | 632.3109 | 498.6454 | 503.703 | 493.2852
5838.176 | 629.1172 | 498.1471 | 503.4287 | 492.6697
5839.176 | 631.5687 | 497.8752 | 503.1078 | 491.9622
5840.176 | 632.9041 | 497.6234 | 503.2111 | 491.5041
5841.176 | 633.6545 | 497.4172 | 503.1246 | 490.7525
5842.176 | 631.8257 | 497.2646 | 502.5368 | 490.1048
5843.176 | 632.1811 | 497.366 | 501.6158 | 489.5124
5844.176 | 633.0254 | 497.2613 | 500.2892 | 489.0902
5845.176 | 635.563 | 497.0431 | 500.7865 | 490.0923
5846.176 | 636.6833 | 496.7875 | 501.4399 | 491.3071
5847.176 | 638.5086 | 496.759 | 500.8562 | 490.7309
5848.176 | 638.5486 | 496.6714 | 500.7656 | 489.9188
5849.176 | 639.8035 | 497.7252 | 502.1209 | 489.428
5850.176 | 641.958 | 498.5067 | 501.8571 | 489.2126
5851.176 | 650.5859 | 499.1099 | 501.924 | 488.7765
5852.176 | 657.3074 | 499.3075 | 501.6852 | 489.2272
5853.176 | 660.1081 | 499.3325 | 501.2356 | 489.3864
5854.176 | 661.8498 | 499.3875 | 501.0994 | 489.7764
5855.176 | 661.4701 | 499.4279 | 501.0396 | 490.0033
5856.176 | 663.7214 | 499.8987 | 500.999 | 489.9335
5857.176 | 664.9451 | 500.3288 | 501.0193 | 489.7121
5858.176 | 666.6862 | 501.1241 | 500.7982 | 489.5197
5859.176 | 669.0692 | 501.6468 | 500.7533 | 490.0939
5860.176 | 675.9345 | 501.9719 | 502.39 | 490.3475
5861.176 | 681.2804 | 501.9538 | 503.0326 | 491.3629
5862.176 | 683.1993 | 502.1958 | 503.1587 | 491.3457
5863.176 | 686.5561 | 502.2107 | 503.1349 | 491.548
5864.176 | 692.9847 | 502.7819 | 503.3798 | 491.635
5865.176 | 696.6978 | 502.5172 | 503.4559 | 491.8791
5866.176 | 695.6906 | 503.0483 | 503.7287 | 492.0908
5867.176 | 695.3086 | 503.422 | 503.9762 | 492.1677
5868.176 | 693.5301 | 503.5881 | 503.8267 | 491.8739
5869.176 | 695.9214 | 503.8535 | 503.0789 | 492.1588
5870.176 | 693.2245 | 503.5473 | 502.3039 | 491.9333
5871.176 | 695.7402 | 503.4093 | 501.985 | 491.9697
5872.176 | 699.752 | 503.1911 | 501.7353 | 491.7158
5873.176 | 701.0481 | 502.792 | 501.4282 | 491.867
5874.176 | 705.2484 | 502.4363 | 501.5799 | 492.0101
5875.176 | 709.3296 | 502.4468 | 501.3085 | 491.2859
5876.176 | 715.4943 | 502.1036 | 501.2076 | 490.7815
5877.176 | 718.4908 | 501.7839 | 501.3021 | 490.4557
5878.176 | 716.7711 | 501.1496 | 501.4091 | 490.8862
5879.176 | 724.6708 | 500.7896 | 500.9517 | 491.2668
5880.176 | 727.9863 | 501.3905 | 500.6714 | 491.1223
5881.176 | 732.3225 | 501.0992 | 500.4375 | 490.7266
5882.176 | 727.8643 | 500.7581 | 499.8924 | 490.7948
5883.176 | 719.0878 | 500.5606 | 499.6381 | 490.5938
5884.176 | 725.3265 | 500.2862 | 500.0157 | 490.574
5885.176 | 727.742 | 500.0633 | 499.9494 | 490.2844
5886.176 | 726.9144 | 499.7582 | 500.2486 | 489.825
5887.176 | 723.6731 | 499.6369 | 500.1991 | 489.4877
5888.176 | 719.8682 | 499.2802 | 499.8766 | 488.9009
5889.176 | 717.019 | 499.1076 | 499.3194 | 488.4441
5890.176 | 716.8458 | 499.0021 | 499.2548 | 488.0653
5891.176 | 721.5884 | 498.827 | 500.0705 | 487.6306
5892.176 | 724.8391 | 498.3962 | 499.7046 | 487.4402
5893.176 | 727.6225 | 498.19 | 499.4978 | 487.4596
5894.176 | 729.7167 | 498.0471 | 499.4694 | 487.2727
5895.176 | 727.3655 | 497.911 | 499.0986 | 487.8799
5896.176 | 722.847 | 497.7436 | 498.7606 | 487.9304
5897.176 | 721.9546 | 497.4503 | 497.9165 | 487.8154
5898.176 | 719.9596 | 497.1352 | 497.5723 | 487.8153
5899.176 | 715.9276 | 497.0306 | 497.1321 | 487.8479
5900.176 | 711.7308 | 496.5154 | 496.8449 | 487.8882
5901.176 | 706.419 | 496.2164 | 496.3041 | 488.006
5902.176 | 700.847 | 496.1705 | 496.4987 | 488.0444
5903.176 | 697.7841 | 496.3437 | 496.6133 | 487.9529
5904.176 | 700.0747 | 496.5532 | 496.6053 | 488.4817
5905.176 | 702.3536 | 496.7311 | 496.6247 | 488.3622
5906.176 | 698.8569 | 496.6812 | 496.5316 | 488.1812
5907.176 | 691.9083 | 496.9478 | 496.228 | 487.9033
5908.176 | 685.6503 | 497.1202 | 496.417 | 487.7386
5909.176 | 680.4187 | 496.8836 | 496.8349 | 487.17
5910.176 | 675.3114 | 496.4361 | 496.6475 | 486.9589
5911.176 | 672.2633 | 496.8168 | 496.816 | 486.2913
5912.176 | 671.6712 | 496.9751 | 496.0988 | 485.5832
5913.176 | 669.68 | 497.1263 | 495.3994 | 485.191
5914.176 | 667.9948 | 497.6776 | 495.3398 | 485.3202
5915.176 | 667.2135 | 497.9698 | 495.8417 | 484.8108
5916.176 | 665.1658 | 498.1792 | 496.0325 | 484.8978
5917.176 | 662.8838 | 498.5305 | 496.2468 | 485.0048
5918.176 | 660.0172 | 498.4086 | 496.2916 | 484.9268
5919.176 | 658.9825 | 498.3168 | 496.0492 | 484.4902
5920.176 | 656.7233 | 498.1863 | 496.5803 | 483.9931
5921.176 | 656.5429 | 497.5324 | 496.9038 | 484.538
5922.176 | 656.6433 | 497.5849 | 497.0631 | 484.5806
5923.176 | 654.2095 | 497.9282 | 497.5323 | 485.4543
5924.176 | 651.0966 | 498.347 | 497.744 | 485.8245
5925.176 | 650.2492 | 499.3183 | 497.9684 | 485.8175
5926.176 | 651.7751 | 500.0435 | 499.2567 | 486.3057
5927.176 | 653.9872 | 500.4086 | 499.8259 | 485.9235
5928.176 | 655.84 | 500.5452 | 499.9607 | 486.3818
5929.176 | 656.3316 | 500.5229 | 500.151 | 486.6346
5930.176 | 660.1162 | 500.4265 | 500.4319 | 487.5377
5931.176 | 661.914 | 500.3879 | 501.3125 | 488.172
5932.176 | 665.4721 | 500.1732 | 501.5638 | 488.5816
5933.176 | 669.3526 | 500.0558 | 501.3506 | 488.5557
5934.176 | 673.4307 | 499.9699 | 501.3397 | 488.6263
5935.176 | 678.8817 | 500.0245 | 500.9149 | 488.8559
5936.176 | 684.8912 | 499.8566 | 500.5059 | 488.6951
5937.176 | 686.7581 | 499.9827 | 500.0229 | 487.947
5938.176 | 692.0325 | 499.4911 | 500.055 | 487.4259
5939.176 | 702.3795 | 498.6342 | 499.3914 | 486.8444
5940.176 | 712.9266 | 498.1091 | 499.7172 | 486.3503
5941.176 | 715.4722 | 497.7488 | 499.7059 | 485.8848
5942.176 | 714.8679 | 497.1554 | 499.8834 | 485.7699
5943.176 | 720.2564 | 496.814 | 499.7287 | 485.6777
5944.176 | 720.0965 | 496.6974 | 498.8846 | 485.5955
5945.176 | 719.5379 | 496.3836 | 498.3671 | 485.1282
5946.176 | 720.4177 | 496.0714 | 498.553 | 485.19
5947.176 | 716.8915 | 496.3299 | 498.5792 | 485.306
5948.176 | 722.7368 | 496.3561 | 499.0223 | 484.864
5949.176 | 727.9084 | 496.2086 | 498.344 | 485.179
5950.176 | 726.2565 | 496.3049 | 498.6696 | 486.1768
5951.176 | 720.2626 | 496.7037 | 499.0056 | 486.4736
5952.176 | 714.7364 | 497.1097 | 499.4511 | 487.036
5953.176 | 712.3755 | 497.1134 | 499.7166 | 487.9357
5954.176 | 710.7292 | 497.4851 | 499.9647 | 488.1268
5955.176 | 705.3066 | 497.7792 | 500.0403 | 488.3385
5956.176 | 701.1588 | 497.9255 | 499.9634 | 488.7719
5957.176 | 699.0183 | 497.5686 | 500.0029 | 488.6164
5958.176 | 705.9171 | 497.157 | 499.5875 | 488.49
5959.176 | 710.6627 | 496.8569 | 498.9079 | 488.3246
5960.176 | 718.0255 | 496.1949 | 498.5035 | 488.0466
5961.176 | 718.1288 | 496.1164 | 498.1037 | 488.8255
5962.176 | 712.8396 | 495.8999 | 497.5042 | 488.5858
5963.176 | 720.1154 | 496.3533 | 496.7844 | 488.1893
5964.176 | 728.7826 | 496.3051 | 496.2228 | 488.0714
5965.176 | 726.7826 | 496.1635 | 496.2049 | 487.7078
5966.176 | 723.1626 | 496.0836 | 496.2952 | 487.2948
5967.176 | 720.5022 | 496.0818 | 496.1727 | 486.9758
5968.176 | 717.095 | 496.2844 | 495.7989 | 486.8301
5969.176 | 713.6455 | 496.1771 | 495.6876 | 486.9614
5970.176 | 717.5142 | 495.9394 | 495.769 | 487.2687
5971.176 | 716.6633 | 495.9221 | 495.6662 | 487.6208
5972.176 | 716.7864 | 495.7453 | 495.646 | 487.7347
5973.176 | 712.3349 | 495.5409 | 495.366 | 487.8941
5974.176 | 708.2797 | 495.3431 | 495.0225 | 487.6671
5975.176 | 712.592 | 495.3639 | 495.2107 | 487.1428
5976.176 | 711.7216 | 495.863 | 495.4815 | 486.7656
5977.176 | 714.226 | 496.178 | 495.3656 | 486.5206
5978.176 | 718.0368 | 496.1988 | 495.1161 | 486.1405
5979.176 | 719.0731 | 496.1485 | 495.1103 | 486.6194
5980.176 | 715.5967 | 495.8802 | 495.2468 | 486.4493
5981.176 | 715.8702 | 495.6015 | 495.1363 | 487.0716
5982.176 | 714.1438 | 495.3288 | 494.7382 | 487.0024
5983.176 | 716.0139 | 494.9528 | 494.6882 | 487.0454
5984.176 | 718.5647 | 495.0217 | 494.5611 | 487.5975
5985.176 | 720.4641 | 495.0333 | 494.5175 | 488.3985
5986.176 | 722.8267 | 494.8945 | 494.6765 | 488.9828
5987.176 | 726.3841 | 494.5988 | 495.177 | 489.1678
5988.176 | 725.1723 | 494.4434 | 495.4112 | 488.6668
5989.176 | 723.4991 | 494.1826 | 495.3818 | 488.3731
5990.176 | 725.0451 | 494.0839 | 495.2571 | 487.73
5991.176 | 722.7833 | 493.7911 | 495.2314 | 488.1319
5992.176 | 729.3093 | 493.2141 | 494.739 | 488.0066
5993.176 | 729.0687 | 493.228 | 494.5301 | 488.038
5994.176 | 726.6884 | 492.8957 | 494.3532 | 488.0473
5995.176 | 730.5872 | 492.4711 | 493.9693 | 487.8627
5996.176 | 735.1898 | 492.0951 | 493.9313 | 487.051
5997.176 | 740.6547 | 491.5018 | 493.3883 | 486.6992
5998.176 | 749.126 | 490.9499 | 492.9382 | 486.9067
5999.176 | 748.8951 | 490.8981 | 493.2088 | 486.6591
6000.1917 | 742.2006 | 491.5186 | 493.5354 | 486.2717
6001.176 | 736.6583 | 491.5604 | 493.4639 | 486.3031
6002.176 | 737.2868 | 491.6828 | 493.6645 | 485.976
6003.176 | 732.7838 | 491.7193 | 494.046 | 485.6637
6004.176 | 727.6522 | 491.9289 | 494.0372 | 485.2496
6005.176 | 721.2995 | 492.0749 | 494.273 | 484.8988
6006.176 | 718.1177 | 491.8448 | 494.2599 | 484.3829
6007.176 | 712.2218 | 492.0975 | 494.553 | 484.1107
6008.176 | 710.9297 | 492.401 | 494.8777 | 484.1965
6009.176 | 712.212 | 492.6025 | 495.2941 | 484.4245
6010.176 | 713.8792 | 492.3779 | 495.8813 | 484.9586
6011.176 | 713.3477 | 492.4221 | 495.8604 | 485.2013
6012.176 | 716.6688 | 492.1077 | 495.7326 | 485.2278
6013.176 | 720.28 | 491.8046 | 495.6358 | 485.5801
6014.176 | 726.5534 | 491.6056 | 495.4133 | 486.3043
6015.176 | 733.7685 | 491.4459 | 495.5427 | 486.6959
6016.176 | 738.9846 | 491.0218 | 495.4448 | 486.5634
6017.176 | 741.6801 | 490.5209 | 495.3133 | 486.7602
6018.176 | 739.8411 | 490.1183 | 495.1298 | 487.3042
6019.176 | 739.2428 | 489.7851 | 494.6229 | 487.3368
6020.176 | 734.5123 | 489.6484 | 494.5728 | 486.7944
6021.176 | 729.8309 | 489.9686 | 494.7411 | 486.2551
6022.176 | 725.0738 | 490.3795 | 496.0271 | 486.7814
6023.176 | 720.9731 | 490.8185 | 496.58 | 487.1903
6024.176 | 715.3296 | 491.1597 | 497.6212 | 487.2104
6025.176 | 711.5832 | 491.3555 | 497.9762 | 487.2793
6026.176 | 711.3028 | 491.2961 | 497.7318 | 486.3368
6027.176 | 711.406 | 491.0368 | 497.5533 | 485.4884
6028.176 | 711.8511 | 490.957 | 497.6894 | 485.2687
6029.176 | 711.5388 | 490.9809 | 497.7364 | 485.4145
6030.176 | 717.3466 | 490.9211 | 498.3281 | 485.0791
6031.176 | 721.6367 | 490.7316 | 498.2508 | 485.2939
6032.176 | 719.338 | 490.4108 | 497.9069 | 485.3909
6033.176 | 715.7092 | 490.4177 | 498.064 | 486.7967
6034.176 | 711.2956 | 490.5546 | 497.5172 | 486.8822
6035.176 | 711.527 | 490.474 | 497.169 | 487.1187
6036.176 | 712.724 | 490.4643 | 496.7586 | 487.3447
6037.176 | 710.8614 | 490.9407 | 496.7103 | 487.4293
6038.176 | 707.5486 | 491.1751 | 496.6658 | 487.7539
6039.176 | 703.4679 | 490.9871 | 496.3746 | 487.4906
6040.176 | 701.1176 | 490.6216 | 496.1166 | 487.3059
6041.176 | 703.7794 | 490.278 | 495.6242 | 487.0149
6042.176 | 708.2703 | 489.5114 | 494.9474 | 486.3854
6043.176 | 709.0692 | 489.2577 | 494.4145 | 485.8025
6044.176 | 712.6325 | 488.9992 | 494.0262 | 485.224
6045.176 | 719.0052 | 489.0234 | 493.5471 | 484.5742
6046.176 | 719.6264 | 488.6935 | 492.867 | 483.8872
6047.176 | 723.6175 | 488.4592 | 492.7352 | 483.3985
6048.176 | 726.3444 | 488.5482 | 493.2234 | 483.0892
6049.176 | 727.2464 | 488.4069 | 493.2327 | 482.9946
6050.176 | 724.1194 | 488.4033 | 492.851 | 482.4779
6051.176 | 721.0562 | 488.4601 | 492.3589 | 481.9909
6052.176 | 725.679 | 488.145 | 492.0944 | 482.0402
6053.176 | 731.1296 | 488.113 | 492.3725 | 482.1132
6054.176 | 734.7954 | 487.943 | 492.3966 | 481.9699
6055.176 | 736.5558 | 487.677 | 492.1786 | 481.8525
6056.176 | 730.8454 | 487.5363 | 492.0481 | 482.8892
6057.176 | 730.4657 | 487.2864 | 491.5058 | 482.5746
6058.176 | 737.9477 | 487.0846 | 491.0811 | 482.2554
6059.176 | 740.9015 | 486.5938 | 490.7051 | 482.0423
6060.176 | 737.0318 | 486.2675 | 490.0588 | 481.6921
6061.176 | 732.8339 | 485.7372 | 489.6779 | 481.5795
6062.176 | 737.6205 | 485.2265 | 488.7628 | 481.2495
6063.176 | 739.392 | 484.9283 | 488.803 | 481.3863
6064.176 | 734.1828 | 484.7963 | 489.4901 | 482.2133
6065.176 | 727.4637 | 485.1171 | 489.9129 | 483.0423
6066.176 | 721.8469 | 485.6603 | 491.0231 | 482.754
6067.176 | 716.1723 | 486.2395 | 490.9611 | 482.785
6068.176 | 709.2818 | 486.2487 | 490.8002 | 483.1395
6069.176 | 702.7235 | 486.2344 | 490.6056 | 482.9782
6070.176 | 697.6846 | 486.6916 | 490.4242 | 482.4462
6071.176 | 694.8673 | 487.6735 | 490.202 | 481.9698
6072.176 | 693.5572 | 488.105 | 490.296 | 481.1537
6073.176 | 694.527 | 488.2111 | 490.2788 | 480.273
6074.176 | 693.9512 | 488.0848 | 490.4692 | 479.5811
6075.176 | 702.7544 | 487.9304 | 490.404 | 478.9532
6076.176 | 710.4071 | 487.754 | 490.0494 | 478.3636
6077.176 | 713.3398 | 487.4263 | 490.0358 | 478.2561
6078.176 | 710.3695 | 487.0157 | 489.8706 | 478.4527
6079.176 | 707.4133 | 486.9232 | 489.7912 | 479.2268
6080.176 | 712.6658 | 487.2696 | 489.473 | 479.2197
6081.176 | 711.9412 | 487.6379 | 489.4341 | 480.4462
6082.176 | 714.1889 | 487.6169 | 489.4952 | 479.7897
6083.176 | 710.7877 | 487.4669 | 489.3307 | 479.7289
6084.176 | 706.5104 | 487.1273 | 489.2297 | 479.3705
6085.176 | 700.7062 | 487.0594 | 488.9328 | 479.3616
6086.176 | 702.6646 | 486.9852 | 488.8545 | 479.2163
6087.176 | 707.165 | 486.7751 | 488.9579 | 479.0693
6088.176 | 704.856 | 486.5597 | 488.5731 | 479.1916
6089.176 | 703.778 | 486.5112 | 488.4414 | 478.8756
6090.176 | 711.5789 | 486.7217 | 488.4374 | 478.6046
6091.176 | 720.2311 | 486.6853 | 488.529 | 478.6943
6092.176 | 727.0737 | 486.599 | 488.5399 | 479.4031
6093.176 | 730.1053 | 486.607 | 488.5962 | 480.288
6094.176 | 728.3136 | 486.6841 | 488.8988 | 480.1638
6095.176 | 724.4832 | 486.6167 | 489.06 | 480.0166
6096.176 | 721.9139 | 486.7476 | 488.9593 | 480.0956
6097.176 | 717.8919 | 487.2724 | 489.1371 | 480.2343
6098.176 | 714.5865 | 487.1138 | 488.9613 | 479.9065
6099.176 | 710.9356 | 487.3075 | 488.9223 | 479.4644
6100.176 | 709.1675 | 487.3678 | 488.6259 | 478.8219
6101.176 | 706.1449 | 487.6106 | 488.4577 | 478.3883
6102.176 | 704.6069 | 487.8281 | 488.8913 | 478.0378
6103.176 | 702.8958 | 487.7051 | 488.9338 | 478.0142
6104.176 | 700.0325 | 487.8421 | 489.1021 | 477.7546
6105.176 | 696.7165 | 488.1319 | 489.3367 | 477.3218
6106.176 | 694.1517 | 488.151 | 490.1349 | 477.158
6107.176 | 691.4585 | 488.5766 | 490.3152 | 476.8992
6108.176 | 690.841 | 488.5213 | 490.0698 | 476.5892
6109.176 | 689.8721 | 488.3547 | 489.9344 | 476.5665
6110.176 | 692.7078 | 488.167 | 489.5115 | 476.3658
6111.176 | 691.8335 | 487.6514 | 489.2762 | 476.0695
6112.176 | 689.4767 | 487.6218 | 488.9319 | 476.1301
6113.176 | 689.9391 | 487.7022 | 488.8786 | 476.3801
6114.176 | 695.0936 | 487.5743 | 489.0615 | 476.4445
6115.176 | 694.9048 | 487.2825 | 489.2358 | 476.9558
6116.176 | 696.4514 | 486.6751 | 488.8445 | 476.9712
6117.176 | 696.1848 | 486.4489 | 488.5549 | 477.1475
6118.176 | 692.9338 | 486.1696 | 488.4028 | 477.3608
6119.176 | 693.9832 | 485.7754 | 488.2841 | 478.5784
6120.176 | 695.0382 | 485.5474 | 487.7548 | 478.1122
6121.176 | 690.6908 | 485.5514 | 487.3586 | 477.5204
6122.176 | 688.6651 | 485.3508 | 486.7354 | 477.2538
6123.176 | 693.8867 | 485.2801 | 486.5124 | 476.8817
6124.176 | 696.9097 | 484.8382 | 486.0122 | 476.5447
6125.176 | 700.7414 | 484.4966 | 485.7032 | 476.1855
6126.176 | 701.0938 | 483.9234 | 485.2636 | 476.2645
6127.176 | 700.6432 | 483.2777 | 484.7915 | 475.8223
6128.176 | 703.755 | 482.6108 | 484.0489 | 475.2544
6129.176 | 703.3329 | 482.0848 | 483.6466 | 474.7453
6130.176 | 706.5262 | 481.4281 | 483.405 | 474.4207
6131.176 | 708.2514 | 481.1812 | 483.1463 | 474.2089
6132.176 | 714.2929 | 481.4442 | 482.7405 | 474.1256
6133.176 | 718.269 | 481.1645 | 482.4951 | 473.8743
6134.176 | 714.14 | 480.771 | 482.4178 | 473.9293
6135.176 | 711.3221 | 480.7016 | 481.953 | 473.7698
6136.176 | 708.1015 | 480.9131 | 481.698 | 473.2519
6137.1917 | 703.2463 | 481.1051 | 481.4817 | 472.8524
6138.176 | 705.9057 | 481.1879 | 481.2214 | 472.6593
6139.176 | 715.7439 | 481.7429 | 480.9313 | 472.3046
6140.176 | 718.9008 | 482.4688 | 480.6154 | 472.7376
6141.176 | 715.4747 | 482.208 | 480.4582 | 472.8192
6142.176 | 712.7531 | 481.861 | 480.6437 | 472.7248
6143.176 | 708.0553 | 481.7066 | 480.3777 | 472.5768
6144.176 | 701.4508 | 481.6017 | 480.3218 | 472.8242
6145.176 | 695.9332 | 481.3381 | 480.4062 | 472.9203
6146.176 | 692.6526 | 481.5364 | 480.2372 | 472.8262
6147.176 | 692.0954 | 481.5176 | 480.0945 | 472.9775
6148.176 | 693.1578 | 481.8598 | 479.9953 | 473.2113
6149.176 | 694.5955 | 481.9312 | 480.0025 | 473.1869
6150.176 | 694.64 | 481.8878 | 480.0962 | 473.1926
6151.176 | 695.0141 | 481.9108 | 481.3813 | 473.0423
6152.176 | 692.6671 | 481.9724 | 481.4536 | 473.0918
6153.176 | 689.8553 | 482.4017 | 482.2135 | 473.3959
6154.176 | 687.8422 | 482.9109 | 482.5405 | 473.7421
6155.176 | 687.5383 | 483.5262 | 483.6349 | 474.1538
6156.176 | 684.8471 | 484.8153 | 484.7113 | 474.851
6157.176 | 687.0065 | 484.6639 | 485.1587 | 475.4628
6158.176 | 689.0132 | 484.6484 | 485.1745 | 475.7013
6159.176 | 688.8052 | 484.696 | 485.1512 | 475.557
6160.176 | 690.6397 | 484.5203 | 485.423 | 475.4626
6161.176 | 692.0059 | 485.1208 | 486.1649 | 475.3402
6162.176 | 689.3501 | 485.4807 | 486.0366 | 475.3249
6163.176 | 686.325 | 485.8415 | 486.0246 | 475.3814
6164.176 | 683.0934 | 486.7398 | 486.0484 | 475.359
6165.176 | 683.6073 | 486.8144 | 485.9765 | 475.0313
6166.176 | 682.1162 | 486.8456 | 485.9616 | 475.03
6167.176 | 683.7593 | 487.1618 | 486.0585 | 475.8011
6168.176 | 685.216 | 487.8516 | 485.8806 | 476.1044
6169.176 | 685.4799 | 487.6222 | 485.7847 | 476.9606
6170.176 | 688.5798 | 487.2771 | 485.3194 | 477.7154
6171.176 | 691.8351 | 486.9919 | 485.0568 | 477.5996
6172.176 | 694.056 | 486.834 | 485.1613 | 477.4035
6173.176 | 695.0656 | 486.8509 | 485.2309 | 477.0841
6174.176 | 692.88 | 486.8021 | 484.6052 | 476.1277
6175.176 | 693.667 | 486.3974 | 484.1617 | 475.5793
6176.176 | 695.2645 | 487.0912 | 483.8819 | 475.0875
6177.176 | 693.6892 | 487.409 | 483.6763 | 474.7838
6178.176 | 690.4995 | 487.7859 | 483.7723 | 474.6086
6179.176 | 689.6884 | 488.7057 | 484.5841 | 474.4334
6180.176 | 687.0617 | 489.2339 | 484.9721 | 474.3624
6181.176 | 682.486 | 489.5005 | 485.6095 | 474.4537
6182.176 | 685.6315 | 489.2962 | 485.7402 | 474.4296
6183.176 | 687.218 | 489.0024 | 486.0233 | 474.4835
6184.176 | 689.4391 | 488.7168 | 486.1121 | 474.3328
6185.176 | 687.5163 | 488.1179 | 485.8774 | 474.8773
6186.176 | 685.574 | 487.5618 | 485.3135 | 475.1642
6187.176 | 682.519 | 487.5856 | 485.3385 | 474.8962
6188.176 | 678.5197 | 487.5277 | 484.7868 | 474.6071
6189.176 | 676.8506 | 487.7604 | 484.4805 | 474.4692
6190.176 | 678.8563 | 487.5972 | 484.0896 | 474.463
6191.176 | 685.5503 | 487.5603 | 484.0428 | 474.3236
6192.176 | 691.3355 | 486.9296 | 483.7081 | 473.992
6193.176 | 698.8651 | 486.3147 | 483.3584 | 473.8991
6194.176 | 700.6739 | 486.0626 | 483.006 | 473.8198
6195.176 | 696.1642 | 485.4162 | 482.395 | 473.4965
6196.176 | 692.7913 | 484.9865 | 481.7393 | 473.6206
6197.176 | 691.3774 | 484.4819 | 480.805 | 473.9016
6198.176 | 692.1324 | 484.2417 | 480.4638 | 473.5173
6199.176 | 693.0333 | 484.1893 | 480.3101 | 472.9277
6200.176 | 692.9568 | 484.5391 | 480.0652 | 472.1284
6201.176 | 690.4891 | 484.6225 | 480.1252 | 471.714
6202.176 | 692.2743 | 484.5883 | 480.165 | 471.6394
6203.176 | 694.107 | 485.3208 | 480.6492 | 471.1985
6204.176 | 695.2652 | 485.0551 | 480.4839 | 471.4052
6205.176 | 694.9599 | 484.3205 | 480.0704 | 471.1962
6206.176 | 691.4584 | 483.8213 | 479.995 | 471.4202
6207.176 | 692.7725 | 483.4035 | 481.2096 | 471.4718
6208.176 | 691.5891 | 483.1986 | 481.9294 | 471.168
6209.176 | 693.2598 | 483.2827 | 482.068 | 471.3944
6210.176 | 697.4433 | 483.4288 | 482.0063 | 471.6024
6211.176 | 699.8461 | 483.4657 | 481.7559 | 471.7223
6212.176 | 695.5059 | 482.8111 | 481.3147 | 471.4876
6213.176 | 693.5529 | 482.4448 | 480.996 | 470.9417
6214.176 | 689.5891 | 481.9053 | 480.5684 | 470.845
6215.176 | 687.1239 | 481.7109 | 480.0634 | 470.5364
6216.176 | 685.9373 | 481.5838 | 479.904 | 470.3481
6217.176 | 687.7305 | 482.0866 | 479.8696 | 470.5134
6218.176 | 684.6841 | 482.976 | 479.8972 | 470.4464
6219.176 | 682.7715 | 483.7603 | 480.2556 | 470.4139
6220.176 | 684.199 | 484.1571 | 480.573 | 470.1585
6221.176 | 685.5987 | 484.0929 | 480.932 | 470.1663
6222.176 | 691.3285 | 483.6794 | 481.26 | 470.3764
6223.176 | 690.0992 | 483.221 | 481.7554 | 471.1084
6224.176 | 685.7636 | 482.6518 | 481.609 | 471.2185
6225.176 | 684.8735 | 482.119 | 481.2663 | 471.0847
6226.176 | 687.9941 | 482.3591 | 480.5878 | 470.8225
6227.2073 | 688.1762 | 482.3143 | 480.0426 | 470.6503
6228.176 | 687.1615 | 482.9327 | 479.8604 | 470.164
6229.176 | 685.5504 | 483.4636 | 480.1702 | 470.1852
6230.176 | 684.4529 | 483.5555 | 480.7154 | 469.9641
6231.176 | 687.942 | 484.3502 | 481.0514 | 469.7192
6232.176 | 692.7311 | 484.0253 | 480.8402 | 469.7776
6233.176 | 690.3031 | 483.5414 | 480.7665 | 469.8004
6234.176 | 688.278 | 483.6807 | 480.5004 | 470.0634
6235.176 | 692.6562 | 483.3727 | 480.1764 | 470.4314
6236.176 | 703.2933 | 483.1512 | 479.6443 | 470.3023
6237.176 | 708.685 | 482.6801 | 479.4268 | 470.4006
6238.176 | 703.8371 | 482.1566 | 479.2054 | 470.1802
6239.176 | 699.5968 | 481.6671 | 479.007 | 469.794
6240.176 | 698.0152 | 482.1466 | 479.031 | 469.3649
6241.176 | 698.5931 | 482.277 | 479.4097 | 469.3674
6242.176 | 699.6284 | 482.158 | 479.6034 | 469.9652
6243.176 | 696.1882 | 481.7094 | 479.4881 | 470.2821
6244.176 | 691.4749 | 481.4368 | 479.321 | 469.8867
6245.176 | 687.0854 | 481.1887 | 479.2675 | 469.5348
6246.176 | 684.6674 | 481.3294 | 479.3044 | 469.3288
6247.176 | 688.2116 | 482.0305 | 479.4463 | 469.2076
6248.176 | 693.4029 | 481.8905 | 479.3628 | 468.9734
6249.176 | 698.5692 | 481.5726 | 478.9552 | 468.8907
6250.176 | 697.0638 | 481.3416 | 479.2233 | 469.0019
6251.176 | 691.5535 | 481.1121 | 479.292 | 469.2254
6252.176 | 686.9505 | 480.8029 | 479.1369 | 469.5824
6253.176 | 683.4024 | 480.4895 | 478.8198 | 469.7073
6254.176 | 678.3523 | 480.6904 | 478.286 | 469.0809
6255.176 | 677.9648 | 480.6164 | 477.8229 | 468.4999
6256.176 | 682.9288 | 481.0091 | 477.4665 | 468.2104
6257.176 | 682.1413 | 481.0836 | 477.6521 | 468.5367
6258.176 | 685.3079 | 481.1818 | 478.0405 | 468.5734
6259.176 | 685.7863 | 481.3184 | 478.193 | 468.8549
6260.176 | 686.5286 | 481.3035 | 478.879 | 469.1127
6261.176 | 686.4493 | 481.0322 | 478.9668 | 469.3174
6262.176 | 683.0546 | 480.7167 | 479.0294 | 469.6713
6263.176 | 684.8127 | 480.4255 | 478.9462 | 469.8169
6264.176 | 686.7618 | 480.343 | 478.7759 | 470.0446
6265.176 | 692.0204 | 480.0092 | 478.8642 | 470.1157
6266.176 | 694.4943 | 480.0817 | 478.6056 | 469.7846
6267.176 | 695.1596 | 479.7827 | 478.637 | 469.4707
6268.176 | 690.9633 | 479.5922 | 478.5985 | 469.5577
6269.176 | 686.5468 | 479.7581 | 478.6667 | 469.6554
6270.176 | 681.5472 | 479.8378 | 478.764 | 469.9146
6271.176 | 679.8328 | 480.4329 | 478.6315 | 469.6576
6272.176 | 682.1352 | 481.413 | 478.2414 | 469.6318
6273.176 | 681.5462 | 481.3613 | 478.2965 | 469.1705
6274.176 | 680.8095 | 481.7075 | 478.5102 | 468.8283
6275.176 | 678.7387 | 481.6798 | 478.9103 | 468.2235
6276.176 | 678.8207 | 481.7935 | 479.219 | 468.2582
6277.176 | 677.6231 | 481.8907 | 479.5246 | 468.3071
6278.176 | 675.3812 | 481.8695 | 479.6475 | 468.3791
6279.176 | 680.5356 | 482.0704 | 479.5757 | 468.502
6280.176 | 691.5334 | 481.6241 | 479.4007 | 469.2787
6281.176 | 700.6395 | 481.3361 | 479.1504 | 468.8998
6282.176 | 705.1269 | 480.9783 | 479.1525 | 469.3099
6283.176 | 705.1083 | 480.3713 | 478.9905 | 469.4216
6284.176 | 705.1822 | 480.1473 | 478.8006 | 469.4238
6285.176 | 704.6726 | 479.8882 | 478.8702 | 469.2716
6286.176 | 703.3533 | 480.0427 | 478.9101 | 469.1444
6287.176 | 705.6513 | 480.5606 | 478.9601 | 468.8327
6288.176 | 702.8115 | 480.9032 | 479.3824 | 468.8082
6289.176 | 698.5366 | 481.2363 | 479.6002 | 468.7234
6290.176 | 695.352 | 481.4333 | 479.6965 | 469.0229
6291.176 | 695.4359 | 481.5259 | 479.7973 | 469.4257
6292.176 | 692.4124 | 481.5435 | 480.0073 | 469.5195
6293.176 | 690.0874 | 481.5156 | 480.1851 | 469.5395
6294.176 | 685.6471 | 481.2329 | 480.0966 | 469.6981
6295.176 | 683.6211 | 481.2866 | 479.9837 | 471.1272
6296.1917 | 682.5885 | 481.8719 | 480.2304 | 471.8204
6297.176 | 677.9486 | 482.4563 | 480.3675 | 471.7315
6298.176 | 675.7517 | 482.9672 | 480.2319 | 471.3423
6299.176 | 676.0641 | 482.3423 | 479.8637 | 470.5723
6300.176 | 679.5624 | 482.3443 | 479.453 | 470.1829
6301.176 | 681.7779 | 482.2178 | 479.4923 | 470.0528
6302.176 | 683.9142 | 482.2251 | 479.5508 | 469.5598
6303.176 | 689.6246 | 482.1191 | 479.3204 | 469.111
6304.176 | 699.0525 | 481.647 | 479.0985 | 469.7236
6305.176 | 706.6419 | 481.0863 | 478.879 | 469.777
6306.176 | 706.2096 | 480.5625 | 478.5282 | 469.4364
6307.176 | 702.6009 | 480.0563 | 478.2338 | 469.0428
6308.176 | 703.2027 | 479.8608 | 478.0955 | 468.8236
6309.176 | 700.377 | 479.89 | 478.0621 | 468.6444
6310.176 | 696.219 | 480.3708 | 478.0222 | 468.8693
6311.176 | 691.1266 | 480.9167 | 477.8882 | 468.6986
6312.176 | 685.4511 | 480.8934 | 477.9302 | 468.508
6313.176 | 681.2012 | 481.2224 | 477.8295 | 468.2462
6314.176 | 678.4438 | 481.9295 | 478.0682 | 467.8655
6315.176 | 688.0749 | 482.3247 | 478.3638 | 467.7609
6316.176 | 693.6094 | 482.2896 | 478.6269 | 467.5261
6317.176 | 692.5549 | 482.2151 | 478.8967 | 467.3492
6318.176 | 694.8726 | 481.9081 | 478.7741 | 467.2647
6319.176 | 695.3801 | 481.4745 | 478.7513 | 467.3784
6320.176 | 691.3727 | 481.4563 | 478.8662 | 467.4949
6321.176 | 687.3945 | 481.3691 | 478.8782 | 467.553
6322.176 | 683.2855 | 482.8167 | 479.0379 | 467.6899
6323.176 | 681.3871 | 483.3369 | 479.0349 | 467.6243
6324.176 | 682.5762 | 483.0246 | 479.076 | 467.5994
6325.176 | 682.6132 | 482.3666 | 478.7955 | 467.4603
6326.1917 | 682.2675 | 481.9268 | 478.5176 | 467.4435
6327.176 | 680.3178 | 481.8548 | 478.2829 | 467.7806
6328.176 | 678.6695 | 481.8201 | 478.3007 | 467.7528
6329.176 | 685.804 | 481.8098 | 478.6436 | 467.4248
6330.176 | 690.2843 | 481.3604 | 478.6215 | 467.2456
6331.176 | 697.0515 | 480.8168 | 478.2897 | 467.0755
6332.176 | 701.4956 | 480.3784 | 478.1583 | 467.1383
6333.176 | 708.9781 | 479.8554 | 477.9929 | 467.0914
6334.176 | 714.3959 | 479.323 | 477.6598 | 466.4812
6335.176 | 714.3349 | 478.7429 | 477.0951 | 466.248
6336.176 | 719.2517 | 478.2472 | 476.3245 | 465.8242
6337.176 | 719.0703 | 477.4511 | 476.2095 | 465.6339
6338.176 | 714.1721 | 477.2571 | 475.95 | 465.4416
6339.176 | 707.7638 | 477.4935 | 475.988 | 465.1678
6340.176 | 702.0464 | 477.6113 | 475.5785 | 464.9972
6341.176 | 694.6245 | 477.4312 | 475.3403 | 464.6545
6342.176 | 686.9273 | 477.376 | 474.9419 | 464.3628
6343.176 | 682.6837 | 477.9966 | 474.7198 | 463.8503
6344.176 | 681.0745 | 477.6251 | 474.3272 | 463.4869
6345.176 | 679.1571 | 477.4479 | 473.806 | 463.4438
6346.176 | 676.139 | 477.3218 | 473.6144 | 463.3033
6347.176 | 675.4545 | 476.9939 | 473.273 | 462.787
6348.176 | 674.3936 | 476.774 | 473.113 | 462.4509
6349.176 | 673.7159 | 476.7211 | 472.9777 | 462.3484
6350.176 | 672.2401 | 476.8824 | 472.963 | 462.3505
6351.176 | 671.4288 | 476.855 | 473.045 | 462.4552
6352.176 | 668.692 | 476.8361 | 472.9608 | 462.1377
6353.176 | 666.7843 | 476.384 | 472.5141 | 462.0024
6354.176 | 664.0537 | 475.8943 | 472.0584 | 461.5347
6355.176 | 660.8946 | 475.3633 | 471.4437 | 461.1652
6356.176 | 660.7776 | 475.0537 | 471.0164 | 461.4583
6357.176 | 667.0363 | 474.7414 | 470.5593 | 461.9801
6358.176 | 668.0648 | 474.5445 | 470.3409 | 461.989
6359.176 | 668.7483 | 474.7395 | 470.0549 | 461.682
6360.176 | 672.5218 | 474.8271 | 469.8794 | 461.6354
6361.176 | 677.6452 | 475.6168 | 469.8346 | 461.4282
6362.176 | 675.8823 | 475.6795 | 469.9269 | 461.6014
6363.176 | 673.8767 | 475.3035 | 469.5151 | 461.4538
6364.176 | 670.8619 | 475.2143 | 469.2961 | 461.5856
6365.176 | 666.665 | 476.2334 | 469.1314 | 461.6717
6366.176 | 666.1622 | 476.4277 | 469.5292 | 461.5141
6367.176 | 668.5535 | 476.6138 | 470.1084 | 461.6103
6368.176 | 668.6412 | 477.001 | 470.7343 | 462.1672
6369.176 | 667.6705 | 477.1206 | 471.2862 | 463.5217
6370.176 | 667.0973 | 477.5239 | 471.7331 | 464.2467
6371.176 | 669.8062 | 477.7504 | 471.993 | 464.4585
6372.176 | 672.5901 | 477.5643 | 471.9639 | 464.8553
6373.176 | 670.1182 | 477.2208 | 471.9404 | 464.9306
6374.176 | 669.111 | 477.0317 | 471.9477 | 465.5231
6375.176 | 675.5599 | 477.0626 | 471.8668 | 465.3065
6376.176 | 680.7343 | 477.5625 | 471.7713 | 465.0807
6377.176 | 682.0715 | 477.4992 | 471.8307 | 464.7151
6378.176 | 683.1254 | 477.8684 | 471.9517 | 464.4705
6379.176 | 682.1248 | 477.8183 | 472.2659 | 464.1064
6380.176 | 682.6616 | 478.0616 | 472.2821 | 463.668
6381.176 | 693.7112 | 478.1548 | 472.2999 | 463.5111
6382.176 | 702.2912 | 477.9644 | 472.1052 | 463.7284
6383.176 | 700.9166 | 477.2664 | 471.7025 | 463.5277
6384.176 | 701.0762 | 476.6382 | 471.3945 | 463.469
6385.176 | 704.6999 | 476.6341 | 470.9377 | 463.2455
6386.176 | 701.7746 | 476.2947 | 471.1848 | 463.1973
6387.176 | 708.8965 | 477.8816 | 471.4789 | 463.5009
6388.176 | 711.7938 | 477.5221 | 471.3503 | 463.4345
6389.176 | 712.5864 | 476.7866 | 471.125 | 463.0485
6390.176 | 708.342 | 476.1757 | 470.7906 | 462.6917
6391.176 | 702.525 | 476.3884 | 470.6814 | 462.5973
6392.176 | 698.4852 | 476.3619 | 470.7079 | 462.0358
6393.176 | 695.0354 | 476.6178 | 470.8469 | 461.6581
6394.176 | 690.3048 | 476.6265 | 471.1323 | 461.4164
6395.176 | 686.1426 | 476.8752 | 471.2911 | 461.0109
6396.176 | 684.1529 | 477.1221 | 471.3375 | 460.9307
6397.176 | 681.73 | 477.5016 | 471.3523 | 460.8919
6398.176 | 679.5617 | 477.8309 | 471.3627 | 461.1212
6399.176 | 678.8974 | 478.0896 | 471.4771 | 461.495
6400.176 | 678.9584 | 477.8913 | 471.4805 | 461.9031
6401.176 | 677.6913 | 477.7271 | 471.4685 | 462.1412
6402.176 | 675.5253 | 477.3196 | 471.6868 | 462.4188
6403.176 | 673.3631 | 477.3148 | 471.9197 | 462.4253
6404.176 | 673.4924 | 477.2382 | 471.9502 | 462.2238
6405.176 | 673.6048 | 476.9644 | 471.9845 | 462.4849
6406.176 | 671.7549 | 476.5409 | 472.0687 | 462.5907
6407.176 | 672.1974 | 476.2341 | 471.9289 | 462.4156
6408.176 | 683.2895 | 476.0616 | 471.5519 | 462.1456
6409.176 | 693.7372 | 475.905 | 471.2578 | 462.007
6410.176 | 701.3821 | 476.5558 | 470.9754 | 461.8774
6411.176 | 713.3321 | 475.9132 | 470.6522 | 461.77
6412.176 | 720.3386 | 475.2688 | 470.2228 | 461.4642
6413.176 | 724.7287 | 474.7252 | 469.7943 | 461.2374
6414.176 | 723.0299 | 474.7072 | 469.4473 | 460.7639
6415.176 | 717.1594 | 474.7816 | 469.0855 | 460.5681
6416.176 | 714.4763 | 475.2784 | 468.9281 | 460.3024
6417.176 | 711.2389 | 475.3964 | 469.2353 | 460.572
6418.176 | 708.4831 | 475.7865 | 469.5816 | 460.9701
6419.176 | 705.3609 | 475.5613 | 469.74 | 460.9139
6420.176 | 703.1019 | 475.3294 | 469.7902 | 460.9448
6421.176 | 702.4753 | 475.0828 | 469.7117 | 460.7994
6422.176 | 698.9917 | 474.7628 | 469.9199 | 460.5552
6423.176 | 696.0265 | 474.4244 | 469.8652 | 460.4836
6424.176 | 693.3743 | 474.7314 | 469.7989 | 460.2141
6425.176 | 691.9283 | 474.9893 | 469.6647 | 460.0268
6426.176 | 690.0019 | 475.3023 | 469.4651 | 459.8666
6427.176 | 690.1621 | 475.5709 | 469.4044 | 459.9532
6428.176 | 687.7213 | 476.0098 | 469.3636 | 460.1897
6429.176 | 686.2226 | 476.735 | 469.3969 | 460.6326
6430.176 | 691.4316 | 476.688 | 469.4175 | 460.94
6431.176 | 690.3671 | 476.502 | 469.3802 | 461.3594
6432.176 | 687.1355 | 476.7722 | 469.5849 | 461.4371
6433.176 | 687.4815 | 476.7719 | 469.6769 | 461.525
6434.176 | 688.4912 | 476.9587 | 469.8031 | 461.6671
6435.176 | 693.8778 | 476.7933 | 470.0855 | 462.9919
6436.176 | 695.9294 | 476.5578 | 470.4221 | 463.2202
6437.176 | 695.4717 | 477.0226 | 470.4701 | 463.0937
6438.176 | 696.7212 | 477.0305 | 470.2652 | 462.8567
6439.176 | 698.2884 | 476.7856 | 470.2833 | 462.56
6440.176 | 694.4405 | 476.9393 | 470.4303 | 462.3033
6441.176 | 690.6793 | 476.6624 | 470.5007 | 462.0885
6442.176 | 689.3589 | 476.674 | 470.6018 | 462.5537
6443.176 | 687.7925 | 476.784 | 470.6016 | 462.1724
6444.176 | 696.1125 | 476.5045 | 470.5405 | 461.8724
6445.176 | 694.6739 | 476.4794 | 470.3718 | 461.4345
6446.176 | 691.9997 | 476.0989 | 470.2456 | 460.8623
6447.176 | 691.4735 | 475.8028 | 470.2947 | 460.4956
6448.176 | 689.3212 | 475.7837 | 470.3191 | 460.4263
6449.176 | 689.2611 | 475.4823 | 470.2915 | 460.1909
6450.176 | 693.3429 | 475.4052 | 470.2326 | 460.7505
6451.176 | 693.3315 | 475.103 | 470.3015 | 460.7175
6452.176 | 691.4416 | 474.7666 | 470.3277 | 460.8086
6453.176 | 691.2634 | 475.7484 | 470.0286 | 460.8729
6454.176 | 698.1332 | 475.621 | 469.7202 | 460.8638
6455.176 | 696.4032 | 475.1743 | 469.4594 | 460.6927
6456.176 | 693.1589 | 474.9074 | 469.2043 | 460.3957
6457.176 | 690.8696 | 474.4426 | 468.9941 | 460.0359
6458.176 | 691.7168 | 474.4514 | 468.7432 | 459.8837
6459.176 | 700.9675 | 474.3447 | 468.3689 | 459.6278
6460.176 | 701.6565 | 474.6042 | 468.1744 | 459.1211
6461.176 | 698.6555 | 475.1394 | 468.0611 | 458.8202
6462.176 | 692.7602 | 475.7282 | 468.1076 | 458.5602
6463.176 | 689.1545 | 475.5449 | 468.864 | 458.0769
6464.176 | 689.6783 | 475.1686 | 468.7053 | 457.8291
6465.176 | 691.0693 | 475.335 | 468.7451 | 457.8211
6466.176 | 687.1412 | 475.1664 | 468.7521 | 458.0113
6467.176 | 688.0568 | 474.8809 | 468.6724 | 457.974
6468.176 | 687.932 | 475.0854 | 468.7599 | 457.8176
6469.176 | 685.0128 | 475.5004 | 468.8403 | 457.8965
6470.176 | 681.3772 | 475.2849 | 468.9621 | 457.9629
6471.176 | 678.7541 | 475.0602 | 469.308 | 458.1376
6472.176 | 676.2322 | 474.9562 | 469.6345 | 458.2579
6473.176 | 672.7808 | 474.7515 | 469.5224 | 458.961
6474.176 | 669.1991 | 474.7328 | 469.625 | 458.7828
6475.176 | 666.4371 | 474.766 | 469.5297 | 458.7182
6476.1917 | 666.597 | 475.2691 | 469.8444 | 458.6457
6477.176 | 662.6368 | 476.0215 | 469.8831 | 458.8293
6478.176 | 659.9629 | 476.0642 | 470.0012 | 459.0026
6479.176 | 662.4631 | 476.0579 | 470.1433 | 458.9618
6480.176 | 662.0486 | 475.8349 | 469.7368 | 458.9324
6481.176 | 664.6486 | 475.6728 | 469.6931 | 458.7676
6482.176 | 666.531 | 475.3509 | 469.6825 | 458.7215
6483.176 | 667.0185 | 475.1242 | 469.5724 | 458.6213
6484.176 | 670.0158 | 474.7689 | 469.4854 | 458.4301
6485.176 | 670.4789 | 475.1594 | 469.3071 | 458.3361
6486.176 | 669.9752 | 475.3626 | 469.331 | 458.1934
6487.176 | 667.9256 | 475.6202 | 469.4986 | 458.3936
6488.176 | 666.2406 | 475.7179 | 469.5509 | 458.4879
6489.176 | 665.1439 | 476.1002 | 469.9234 | 458.9517
6490.176 | 665.8813 | 476.1579 | 470.3342 | 459.1034
6491.176 | 668.5756 | 476.0113 | 470.4374 | 459.2473
6492.176 | 666.8965 | 475.8401 | 470.4002 | 459.2684
6493.176 | 666.0543 | 475.4275 | 470.2032 | 458.9937
6494.176 | 667.219 | 475.1665 | 469.7883 | 458.7688
6495.176 | 669.561 | 474.9139 | 469.3951 | 458.3303
6496.176 | 667.812 | 474.4916 | 469.0059 | 458.2606
6497.176 | 666.3833 | 474.892 | 468.921 | 458.085
6498.176 | 665.2345 | 475.2523 | 468.7818 | 458.1778
6499.176 | 664.1912 | 475.8083 | 469.1134 | 458.0372
6500.176 | 664.5079 | 475.6125 | 469.285 | 458.2226
6501.176 | 666.7232 | 475.2821 | 469.3418 | 458.1418
6502.176 | 669.3816 | 474.7929 | 469.1752 | 457.8221
6503.176 | 670.8664 | 474.4784 | 469.0016 | 457.4785
6504.176 | 671.5979 | 474.59 | 469.0905 | 457.2722
6505.176 | 671.4859 | 474.4271 | 468.9308 | 457.6922
6506.176 | 670.6335 | 474.6972 | 468.8545 | 457.2681
6507.176 | 669.876 | 474.3373 | 468.6688 | 456.9215
6508.176 | 673.8874 | 474.4218 | 468.6059 | 456.874
6509.176 | 674.5208 | 474.8004 | 468.7643 | 456.8969
6510.176 | 674.8414 | 474.6436 | 468.9159 | 457.0241
6511.176 | 674.2083 | 474.6824 | 469.1125 | 456.8908
6512.176 | 672.0249 | 474.9708 | 469.2024 | 456.7439
6513.176 | 671.6168 | 474.5683 | 469.0437 | 456.8986
6514.176 | 668.9267 | 474.7199 | 469.2335 | 457.2205
6515.176 | 666.0094 | 474.7744 | 469.2148 | 457.6038
6516.176 | 664.8151 | 475.0764 | 469.0468 | 457.3504
6517.176 | 662.9126 | 475.5251 | 468.9943 | 457.2008
6518.176 | 660.6528 | 475.8779 | 469.0558 | 457.5242
6519.176 | 662.9107 | 475.6902 | 468.8018 | 457.2185
6520.176 | 661.1748 | 475.6404 | 468.5751 | 457.1556
6521.176 | 661.3687 | 475.2779 | 468.2847 | 457.4981
6522.176 | 660.8436 | 474.7397 | 467.9056 | 457.3829
6523.176 | 659.5543 | 474.524 | 467.5808 | 457.1148
6524.176 | 659.4682 | 474.4235 | 467.3184 | 456.9226
6525.176 | 659.7735 | 474.8414 | 467.454 | 456.4665
6526.176 | 660.2631 | 475.4072 | 467.4093 | 456.2749
6527.176 | 658.7203 | 475.6933 | 467.7244 | 456.1652
6528.176 | 658.1257 | 475.6202 | 467.9301 | 456.0126
6529.176 | 656.1623 | 475.8029 | 468.2775 | 456.1179
6530.176 | 654.1042 | 475.7278 | 468.8297 | 456.2094
6531.176 | 653.1599 | 475.4225 | 469.1357 | 457.045
6532.176 | 650.0102 | 475.5938 | 469.338 | 457.3873
6533.176 | 649.9423 | 475.4515 | 469.566 | 457.7272
6534.176 | 650.0986 | 475.3933 | 469.6034 | 457.7107
6535.176 | 650.9124 | 475.1031 | 469.5509 | 457.7215
6536.176 | 651.1095 | 475.1572 | 469.6254 | 457.8452
6537.176 | 649.2631 | 475.4751 | 469.5748 | 458.171
6538.176 | 649.8351 | 475.8733 | 469.7272 | 458.31
6539.176 | 648.749 | 476.3877 | 470.0203 | 458.2992
6540.176 | 647.517 | 476.7133 | 470.5489 | 458.2683
6541.176 | 648.0603 | 476.8214 | 470.759 | 457.9488
6542.176 | 649.138 | 476.511 | 470.616 | 457.6265
6543.176 | 650.3577 | 476.0416 | 470.5007 | 457.7459
6544.176 | 649.1824 | 475.9512 | 470.564 | 457.8315
6545.176 | 650.9646 | 475.9975 | 470.5103 | 457.5257
6546.176 | 652.5212 | 476.2469 | 470.8059 | 457.5212
6547.176 | 652.4531 | 476.461 | 470.9918 | 457.3984
6548.176 | 651.0947 | 476.2191 | 471.0232 | 457.4167
6549.176 | 649.6315 | 475.8205 | 470.8571 | 457.5384
6550.176 | 649.0056 | 475.3295 | 470.8846 | 457.6846
6551.176 | 649.3884 | 475.9159 | 470.94 | 458.0227
6552.176 | 649.285 | 475.8978 | 470.9176 | 458.1501
6553.176 | 648.5144 | 476.0662 | 471.057 | 458.0219
6554.176 | 648.0253 | 476.3204 | 471.3378 | 458.0024
6555.176 | 645.4429 | 476.0482 | 471.5077 | 457.7637
6556.176 | 644.3165 | 475.811 | 471.3933 | 457.2982
6557.176 | 645.9642 | 475.6619 | 471.3521 | 457.1219
6558.176 | 654.879 | 475.6103 | 471.2112 | 457.1972
6559.176 | 658.545 | 475.3837 | 470.9559 | 457.0097
6560.176 | 661.0838 | 475.1051 | 470.6908 | 457.1489
6561.176 | 660.9183 | 475.2147 | 470.8057 | 457.4079
6562.176 | 659.5287 | 475.2246 | 471.05 | 457.6911
6563.176 | 658.8253 | 475.2844 | 471.0669 | 457.9568
6564.176 | 657.0979 | 475.0529 | 471.0109 | 457.9412
6565.176 | 654.0881 | 475.1996 | 470.9726 | 458.0325
6566.176 | 651.9647 | 475.1131 | 470.9862 | 457.7639
6567.176 | 651.3427 | 475.1544 | 470.9198 | 457.5937
6568.176 | 652.2648 | 475.423 | 470.9104 | 457.4223
6569.176 | 653.9685 | 475.4638 | 470.8829 | 457.5361
6570.176 | 651.9543 | 475.3104 | 471.0123 | 457.8104
6571.176 | 649.8313 | 475.0016 | 470.8752 | 457.7121
6572.176 | 653.4988 | 474.74 | 470.5162 | 457.3446
6573.176 | 658.207 | 474.5729 | 470.3302 | 457.1049
6574.176 | 658.4624 | 474.6077 | 470.2691 | 456.603
6575.176 | 657.686 | 475.0967 | 469.9918 | 456.4951
6576.176 | 657.4161 | 475.3133 | 470.0385 | 456.368
6577.176 | 655.9255 | 475.7587 | 470.6476 | 456.0842
6578.176 | 654.8531 | 476.3484 | 471.1493 | 456.0618
6579.176 | 654.9256 | 476.547 | 471.4923 | 456.1806
6580.176 | 655.4337 | 476.3286 | 471.6063 | 456.1687
6581.176 | 655.8257 | 476.1013 | 471.6454 | 456.1501
6582.176 | 654.6012 | 476.1076 | 471.8057 | 456.2119
6583.176 | 652.9244 | 475.9255 | 471.6596 | 456.3275
6584.176 | 652.8861 | 475.7425 | 471.5957 | 456.4271
6585.176 | 654.5435 | 476.0024 | 471.5466 | 456.3915
6586.176 | 652.8767 | 475.6429 | 471.4418 | 456.2916
6587.176 | 654.8079 | 475.2046 | 471.0059 | 456.2972
6588.176 | 663.5694 | 474.806 | 470.7499 | 456.2672
6589.176 | 669.7435 | 475.3518 | 470.5675 | 456.1285
6590.176 | 671.1278 | 474.7302 | 470.1836 | 456.0144
6591.176 | 669.2462 | 474.1119 | 469.625 | 455.8056
6592.176 | 664.9037 | 473.6663 | 469.1089 | 455.4974
6593.176 | 662.031 | 473.2928 | 468.5183 | 455.1044
6594.176 | 661.4028 | 474.0039 | 468.1194 | 454.6148
6595.176 | 658.0396 | 473.456 | 467.5036 | 454.5882
6596.176 | 656.299 | 472.514 | 466.9366 | 454.2891
6597.176 | 659.8578 | 472.0312 | 466.4107 | 453.8621
6598.176 | 659.1343 | 471.9562 | 466.1711 | 453.7108
6599.176 | 655.9542 | 471.9353 | 466.0199 | 453.2502
6600.176 | 653.5548 | 471.9886 | 466.2175 | 453.4014
6601.176 | 651.1602 | 472.1156 | 466.1385 | 453.7793
6602.176 | 648.1758 | 472.2066 | 466.2085 | 453.9649
6603.176 | 647.5756 | 472.1016 | 466.2582 | 453.9086
6604.176 | 647.1636 | 471.9548 | 466.1074 | 453.7781
6605.176 | 643.5351 | 471.3713 | 465.8612 | 453.4696
6606.176 | 639.1223 | 470.7904 | 465.1448 | 453.1314
6607.176 | 637.0419 | 470.4602 | 464.8828 | 452.978
6608.176 | 636.4614 | 470.2174 | 464.5495 | 452.8507
6609.176 | 638.2901 | 470.4882 | 464.652 | 452.3038
6610.176 | 650.0032 | 470.6311 | 464.6173 | 452.3106
6611.176 | 650.9141 | 470.6609 | 464.6009 | 452.3627
6612.176 | 649.6612 | 470.853 | 464.6563 | 452.5472
6613.176 | 647.3562 | 470.8738 | 464.6946 | 452.4447
6614.176 | 646.409 | 470.8616 | 464.735 | 452.4732
6615.176 | 645.2987 | 471.1291 | 465.1073 | 452.7968
6616.176 | 643.9555 | 471.6925 | 465.1575 | 452.817
6617.176 | 642.6386 | 471.7884 | 465.2063 | 452.6803
6618.176 | 642.9713 | 472.2116 | 465.4111 | 453.0175
6619.176 | 649.3381 | 472.3615 | 465.5561 | 453.0111
6620.176 | 651.9056 | 472.1824 | 465.6436 | 452.8039
6621.176 | 651.5759 | 471.6865 | 465.5215 | 452.5635
6622.176 | 654.2554 | 471.0268 | 465.3378 | 452.4557
6623.176 | 658.3377 | 471.0226 | 465.161 | 452.1786
6624.176 | 659.9972 | 471.1826 | 465.2167 | 451.9944
6625.176 | 662.759 | 470.699 | 465.0327 | 451.9779
6626.176 | 670.7515 | 470.4181 | 465.0317 | 452.2219
6627.176 | 682.1402 | 470.666 | 465.6742 | 452.1459
6628.176 | 691.5038 | 470.3648 | 465.4644 | 452.1835
6629.176 | 695.2776 | 469.9076 | 465.039 | 452.2932
6630.176 | 693.2155 | 469.34 | 464.6849 | 452.3161
6631.176 | 691.3893 | 468.9737 | 464.3763 | 452.4856
6632.176 | 692.2065 | 469.1036 | 464.2033 | 452.9742
6633.176 | 695.1867 | 468.4891 | 463.7499 | 452.9505
6634.176 | 689.7914 | 467.8395 | 463.1644 | 452.6707
6635.176 | 684.6234 | 467.3867 | 462.6854 | 452.1729
6636.176 | 682.8704 | 466.9998 | 462.2932 | 452.5112
6637.176 | 685.921 | 466.8097 | 462.116 | 452.7983
6638.176 | 685.0773 | 467.008 | 462.0723 | 452.7501
6639.176 | 681.79 | 466.9031 | 461.9946 | 452.6687
6640.176 | 676.9277 | 467.0275 | 462.0024 | 452.4794
6641.176 | 671.9903 | 467.4126 | 461.964 | 452.3197
6642.176 | 667.8117 | 467.7455 | 461.9258 | 452.336
6643.176 | 663.0035 | 467.7834 | 461.7928 | 452.0107
6644.176 | 659.5362 | 467.837 | 461.8762 | 451.8038
6645.176 | 657.661 | 468.254 | 461.8514 | 451.6244
6646.176 | 659.0938 | 468.3293 | 462.0446 | 451.6547
6647.176 | 665.5757 | 468.6776 | 462.581 | 452.2347
6648.176 | 677.0674 | 468.5054 | 462.8285 | 452.251
6649.176 | 675.6384 | 468.0824 | 463.0197 | 452.257
6650.176 | 672.491 | 467.4499 | 462.7413 | 452.1746
6651.176 | 670.3721 | 466.8687 | 462.5887 | 451.9405
6652.176 | 667.4613 | 466.9873 | 462.4226 | 451.7311
6653.176 | 665.6626 | 467.1182 | 462.4703 | 451.8985
6654.176 | 663.9218 | 467.2683 | 462.1245 | 451.7234
6655.176 | 668.1293 | 467.6542 | 462.2896 | 451.4535
6656.176 | 666.3826 | 468.3403 | 462.4089 | 451.3795
6657.176 | 664.3366 | 469.041 | 462.4966 | 451.2503
6658.176 | 663.205 | 469.2299 | 462.9084 | 451.1451
6659.176 | 661.5491 | 469.5547 | 463.3847 | 451.1999
6660.176 | 661.9895 | 469.4784 | 463.7108 | 451.3809
6661.176 | 664.0776 | 469.2869 | 463.9764 | 451.4225
6662.176 | 669.4755 | 469.1723 | 463.9929 | 451.5035
6663.176 | 668.2944 | 468.9252 | 463.8928 | 451.4722
6664.176 | 665.2894 | 468.784 | 463.7329 | 451.2112
6665.176 | 664.6579 | 468.7304 | 463.4261 | 451.0412
6666.176 | 664.7811 | 469.0077 | 463.336 | 450.9753
6667.176 | 663.9742 | 469.2981 | 464.3727 | 450.6447
6668.176 | 664.4305 | 469.3153 | 464.7199 | 450.524
6669.176 | 670.2589 | 469.1335 | 464.6596 | 450.3578
6670.176 | 681.331 | 469.1328 | 464.6202 | 450.1974
6671.176 | 687.9841 | 468.6161 | 464.3971 | 450.1734
6672.176 | 688.0089 | 468.3133 | 464.1758 | 450.2919
6673.176 | 687.421 | 468.2086 | 463.8826 | 450.5677
6674.176 | 686.0022 | 467.9061 | 463.4791 | 450.444
6675.176 | 687.2973 | 467.7217 | 463.0291 | 450.2995
6676.176 | 684.9458 | 467.2589 | 462.7212 | 450.1843
6677.176 | 681.9164 | 467.3559 | 462.7315 | 450.0241
6678.176 | 680.0204 | 467.0269 | 462.2394 | 449.6505
6679.176 | 684.8863 | 466.6354 | 461.8155 | 449.2897
6680.176 | 685.6541 | 466.1258 | 461.3672 | 449.6982
6681.176 | 683.6915 | 465.8284 | 461.145 | 450.1347
6682.176 | 680.8696 | 465.7211 | 460.9291 | 450.4826
6683.176 | 678.8815 | 465.5625 | 460.5839 | 450.3126
6684.176 | 676.5118 | 465.2874 | 460.4325 | 450.0434
6685.176 | 675.7023 | 466.0344 | 460.3355 | 450.2433
6686.176 | 675.0941 | 466.7472 | 460.5759 | 450.2466
6687.176 | 680.2764 | 466.6944 | 460.53 | 450.1786
6688.176 | 679.566 | 466.7045 | 460.4577 | 450.2827
6689.176 | 678.9788 | 466.7511 | 460.6439 | 450.3618
6690.176 | 676.2853 | 466.8821 | 460.6339 | 450.3683
6691.176 | 678.0173 | 466.8188 | 460.8046 | 450.1902
6692.176 | 683.0496 | 466.6526 | 460.883 | 449.9246
6693.176 | 680.9173 | 466.3546 | 460.6957 | 449.8263
6694.176 | 677.3633 | 465.9787 | 460.5059 | 449.7087
6695.176 | 676.0931 | 466.1636 | 460.464 | 449.6823
6696.176 | 679.9891 | 466.1401 | 460.3661 | 449.8399
6697.176 | 684.2286 | 466.1656 | 460.3733 | 450.1928
6698.176 | 680.8756 | 466.4905 | 460.2132 | 449.9908
6699.176 | 677.1564 | 467.2017 | 460.1915 | 449.7598
6700.176 | 676.7398 | 466.7773 | 460.0604 | 449.8261
6701.176 | 676.2318 | 466.511 | 459.8422 | 449.923
6702.176 | 674.0709 | 466.1033 | 459.5828 | 449.7019
6703.176 | 672.5105 | 465.9796 | 459.1939 | 449.3677
6704.176 | 670.4134 | 465.6802 | 458.8902 | 449.0974
6705.176 | 671.6717 | 465.6373 | 458.6661 | 448.7853
6706.176 | 671.4857 | 465.8826 | 458.513 | 449.2267
6707.176 | 673.8053 | 466.4752 | 458.6406 | 449.6294
6708.176 | 672.2456 | 466.7882 | 459.0758 | 450.0807
6709.176 | 669.3607 | 467.0629 | 459.7872 | 450.3329
6710.176 | 666.5498 | 467.2172 | 460.2988 | 450.3404
6711.176 | 664.3721 | 467.3924 | 460.6796 | 450.2947
6712.176 | 668.9616 | 467.3698 | 460.6229 | 450.1277
6713.176 | 675.2214 | 467.1937 | 460.6127 | 450.0853
6714.176 | 682.3945 | 467.0993 | 460.3603 | 449.9529
6715.176 | 681.5696 | 466.5406 | 460.1946 | 449.9172
6716.1917 | 679.4858 | 467.2907 | 460.463 | 449.9072
6717.176 | 677.38 | 467.784 | 460.8796 | 449.9948
6718.176 | 674.834 | 468.2801 | 461.1833 | 450.3216
6719.176 | 671.2735 | 468.632 | 461.8106 | 450.4594
6720.176 | 667.5494 | 468.6176 | 462.0559 | 450.3829