## Test Conditions
DESIREE-FIRE Intermediate Scale Test 5 - Circuit Simulator Data Only
Test Date: | 2010-03-01
DCSim DAQ Start Time | 13:30
DCSim Time for Synchronization | 13:42
Heat Source Synchronization | 0:01 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:41
Fire Time | 14:02
Offset | 0:32 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1920 | seconds
Heat Source Offset | 0:21 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1288 | seconds
Heat Source Stop Time | 14:46
Test Duration | 0:44 | hours:minutes:seconds
| 2640 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the conduit temperature 3', 5', and 7' down the conduit located in C Position. These are labeled as "C Position - 3'", "C Position - Middle", "C Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-1.6094 | 124.0173 | -62.0407 | 61.8759 | 0.080646 | -0.067994 | 0.024629 | -0.047909 | 0.054577 | 0.053534 | -0.085608 | 61.7065 | 61.7009 | 61.7247 | 61.5411 | 62.0047 | 62.1384 | 61.5046 | 61.9075 | 62.1214 | 61.9727 | 62.0653 | 61.9928 | 62.0953 | 62.0942 | 61.9551 | 61.7294 | 61.7238 | 61.7476 | 61.564 | 62.0275 | 62.1613 | 61.5275 | 61.9304 | -0.29815 | 0.20188 | -0.27992 | 0.22011
0.0625 | 123.9944 | -62.0316 | 61.908 | 0.085224 | -0.058836 | 0.020051 | -0.047909 | 0.059155 | 0.053534 | -0.090186 | 61.7065 | 61.7101 | 61.7247 | 61.532 | 62.0092 | 62.1293 | 61.5046 | 61.9075 | 62.1168 | 61.9727 | 62.0516 | 61.9836 | 62.0907 | 62.0851 | 61.9414 | 61.7294 | 61.733 | 61.7476 | 61.5549 | 62.0321 | 62.1521 | 61.5275 | 61.9304 | -0.30273 | 0.20188 | -0.28449 | 0.22011
1.8125 | 124.1272 | -62.0544 | 61.8256 | 0.085224 | -0.063415 | 0.020051 | -0.061645 | 0.059155 | 0.044377 | -0.090186 | 61.7019 | 61.6918 | 61.7202 | 61.5366 | 62.0001 | 62.1338 | 61.5092 | 61.9075 | 62.1397 | 61.991 | 62.0745 | 61.9928 | 62.1136 | 62.0988 | 61.9643 | 61.7248 | 61.7147 | 61.743 | 61.5595 | 62.023 | 62.1567 | 61.5321 | 61.9304 | -0.29815 | 0.19272 | -0.27992 | 0.21095
3.4844 | 123.9853 | -62.0773 | 61.8988 | 0.089802 | -0.063415 | 0.029208 | -0.052488 | 0.049999 | 0.048956 | -0.08103 | 61.6928 | 61.7009 | 61.7156 | 61.5274 | 62.0047 | 62.1293 | 61.5046 | 61.9029 | 62.1671 | 62.0139 | 62.1065 | 62.0248 | 62.1273 | 62.1263 | 61.9963 | 61.7157 | 61.7238 | 61.7385 | 61.5503 | 62.0275 | 62.1521 | 61.5275 | 61.9258 | -0.31189 | 0.18814 | -0.28907 | 0.21095
5.2344 | 124.0723 | -62.0499 | 61.8073 | 0.085224 | -0.058836 | 0.024629 | -0.057066 | 0.045421 | 0.053534 | -0.090186 | 61.7111 | 61.6918 | 61.7247 | 61.5228 | 61.9955 | 62.1293 | 61.5046 | 61.9029 | 62.1351 | 61.991 | 62.0745 | 61.9928 | 62.0953 | 62.1034 | 61.9597 | 61.734 | 61.7147 | 61.7476 | 61.5457 | 62.0184 | 62.1521 | 61.5275 | 61.9258 | -0.28441 | 0.20646 | -0.27076 | 0.22011
6.9688 | 124.0082 | -62.027 | 61.9034 | 0.080646 | -0.058836 | 0.029208 | -0.047909 | 0.054577 | 0.039799 | -0.08103 | 61.7111 | 61.6918 | 61.7247 | 61.5274 | 62.0001 | 62.1293 | 61.4955 | 61.8983 | 62.1076 | 61.9681 | 62.0562 | 61.9791 | 62.0816 | 62.0668 | 61.9459 | 61.734 | 61.7147 | 61.7476 | 61.5503 | 62.023 | 62.1521 | 61.5184 | 61.9212 | -0.28899 | 0.21561 | -0.27534 | 0.22927
8.6406 | 124.1135 | -62.059 | 61.7706 | 0.089802 | -0.058836 | 0.029208 | -0.052488 | 0.054577 | 0.044377 | -0.08103 | 61.6928 | 61.6918 | 61.7156 | 61.5182 | 61.9955 | 62.1293 | 61.4955 | 61.9075 | 62.1488 | 62.0002 | 62.0882 | 62.0065 | 62.1136 | 62.1034 | 61.978 | 61.7157 | 61.7147 | 61.7385 | 61.5411 | 62.0184 | 62.1521 | 61.5184 | 61.9304 | -0.30273 | 0.1973 | -0.27992 | 0.22011
10.3906 | 123.9807 | -62.059 | 61.8668 | 0.089802 | -0.054257 | 0.029208 | -0.057066 | 0.054577 | 0.058113 | -0.085608 | 61.7019 | 61.6918 | 61.7202 | 61.5137 | 61.9955 | 62.1293 | 61.4863 | 61.8983 | 62.1488 | 62.0048 | 62.0882 | 62.002 | 62.1136 | 62.1171 | 61.9734 | 61.7248 | 61.7147 | 61.743 | 61.5366 | 62.0184 | 62.1521 | 61.5092 | 61.9212 | -0.29357 | 0.21561 | -0.27534 | 0.23385
12.1406 | 123.9578 | -62.0224 | 61.8805 | 0.085224 | -0.058836 | 0.029208 | -0.047909 | 0.054577 | 0.053534 | -0.08103 | 61.6973 | 61.6918 | 61.7156 | 61.5182 | 61.9863 | 62.1201 | 61.4817 | 61.8937 | 62.1076 | 61.9636 | 62.0516 | 61.9745 | 62.077 | 62.0759 | 61.9414 | 61.7202 | 61.7147 | 61.7385 | 61.5411 | 62.0092 | 62.143 | 61.5046 | 61.9166 | -0.28899 | 0.21561 | -0.27076 | 0.23385
13.875 | 123.967 | -62.0361 | 61.8851 | 0.089802 | -0.058836 | 0.033786 | -0.047909 | 0.054577 | 0.053534 | -0.085608 | 61.7065 | 61.6964 | 61.7156 | 61.5182 | 61.9818 | 62.1201 | 61.4863 | 61.8937 | 62.1259 | 61.9773 | 62.0699 | 61.9882 | 62.0907 | 62.0897 | 61.9505 | 61.7294 | 61.7192 | 61.7385 | 61.5411 | 62.0047 | 62.143 | 61.5092 | 61.9166 | -0.27526 | 0.22019 | -0.26618 | 0.22927
15.5469 | 123.9899 | -62.0132 | 61.8988 | 0.085224 | -0.058836 | 0.024629 | -0.052488 | 0.059155 | 0.053534 | -0.085608 | 61.6973 | 61.6964 | 61.7202 | 61.5182 | 61.9955 | 62.1201 | 61.4863 | 61.8937 | 62.0985 | 61.9544 | 62.0379 | 61.9608 | 62.0724 | 62.0668 | 61.9276 | 61.7202 | 61.7192 | 61.743 | 61.5411 | 62.0184 | 62.143 | 61.5092 | 61.9166 | -0.29815 | 0.21103 | -0.27534 | 0.23385
17.2969 | 123.9853 | -62.0316 | 61.9034 | 0.089802 | -0.054257 | 0.033786 | -0.057066 | 0.049999 | 0.048956 | -0.08103 | 61.7019 | 61.6964 | 61.7156 | 61.5137 | 61.9863 | 62.1247 | 61.4817 | 61.8937 | 62.1214 | 61.9773 | 62.0653 | 61.9745 | 62.0816 | 62.0805 | 61.9505 | 61.7248 | 61.7192 | 61.7385 | 61.5366 | 62.0092 | 62.1476 | 61.5046 | 61.9166 | -0.28442 | 0.22019 | -0.27076 | 0.23385
18.9688 | 124.0997 | -62.0132 | 61.7981 | 0.089802 | -0.063415 | 0.033786 | -0.057066 | 0.06831 | 0.048956 | -0.08103 | 61.6928 | 61.6872 | 61.7202 | 61.5137 | 61.9909 | 62.1247 | 61.4863 | 61.8892 | 62.103 | 61.9498 | 62.047 | 61.9562 | 62.0816 | 62.0622 | 61.9322 | 61.7157 | 61.7101 | 61.743 | 61.5366 | 62.0138 | 62.1476 | 61.5092 | 61.912 | -0.29815 | 0.20646 | -0.27076 | 0.23385
20.7188 | 123.9853 | -62.0132 | 61.8805 | 0.089802 | -0.063415 | 0.038365 | -0.052488 | 0.049999 | 0.048956 | -0.085608 | 61.6973 | 61.6872 | 61.7202 | 61.5137 | 61.9863 | 62.1155 | 61.4817 | 61.8892 | 62.103 | 61.9498 | 62.0516 | 61.9608 | 62.0632 | 62.0622 | 61.9276 | 61.7202 | 61.7101 | 61.743 | 61.5366 | 62.0092 | 62.1384 | 61.5046 | 61.912 | -0.28899 | 0.21561 | -0.26618 | 0.23842
22.4531 | 123.9761 | -62.0178 | 61.853 | 0.094381 | -0.058836 | 0.029208 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 61.6928 | 61.6872 | 61.7202 | 61.5137 | 61.9909 | 62.1201 | 61.4817 | 61.88 | 62.1122 | 61.959 | 62.047 | 61.9699 | 62.0724 | 62.0668 | 61.9414 | 61.7157 | 61.7101 | 61.743 | 61.5366 | 62.0138 | 62.143 | 61.5046 | 61.9029 | -0.29815 | 0.21103 | -0.27076 | 0.23842
24.1875 | 123.9578 | -62.0361 | 61.8668 | 0.080646 | -0.058836 | 0.033786 | -0.061645 | 0.054577 | 0.053534 | -0.085608 | 61.6973 | 61.6826 | 61.711 | 61.5137 | 61.9818 | 62.1155 | 61.4817 | 61.8846 | 62.1168 | 61.9773 | 62.0699 | 61.9745 | 62.0907 | 62.0897 | 61.9505 | 61.7202 | 61.7055 | 61.7339 | 61.5366 | 62.0047 | 62.1384 | 61.5046 | 61.9075 | -0.28442 | 0.21561 | -0.27076 | 0.22927
25.9219 | 124.0265 | -62.0407 | 61.8164 | 0.089802 | -0.054257 | 0.033786 | -0.047909 | 0.049999 | 0.053534 | -0.085608 | 61.6973 | 61.678 | 61.7156 | 61.5091 | 61.9772 | 62.111 | 61.4726 | 61.8892 | 62.1305 | 61.9865 | 62.0745 | 61.9928 | 62.0907 | 62.0942 | 61.9551 | 61.7202 | 61.7009 | 61.7385 | 61.532 | 62.0001 | 62.1338 | 61.4955 | 61.912 | -0.27984 | 0.22477 | -0.2616 | 0.243
27.5938 | 123.9899 | -62.0087 | 61.8988 | 0.094381 | -0.058836 | 0.029208 | -0.043331 | 0.054577 | 0.044377 | -0.085608 | 61.6928 | 61.678 | 61.711 | 61.5228 | 61.9772 | 62.111 | 61.4817 | 61.8892 | 62.103 | 61.9498 | 62.0379 | 61.9653 | 62.0632 | 62.053 | 61.9231 | 61.7157 | 61.7009 | 61.7339 | 61.5457 | 62.0001 | 62.1338 | 61.5046 | 61.912 | -0.28442 | 0.21103 | -0.26618 | 0.22927
29.3438 | 124.0402 | -62.0361 | 61.7889 | 0.085224 | -0.058836 | 0.024629 | -0.061645 | 0.054577 | 0.048956 | -0.08103 | 61.6882 | 61.6735 | 61.7018 | 61.5091 | 61.9772 | 62.1201 | 61.4817 | 61.8892 | 62.1214 | 61.9773 | 62.0608 | 61.9745 | 62.0907 | 62.0851 | 61.9551 | 61.7111 | 61.6964 | 61.7247 | 61.532 | 62.0001 | 62.143 | 61.5046 | 61.912 | -0.28899 | 0.20645 | -0.27534 | 0.22011
31.0781 | 124.0219 | -62.0544 | 61.7844 | 0.085224 | -0.063415 | 0.029208 | -0.038752 | 0.054577 | 0.053534 | -0.085608 | 61.6836 | 61.6735 | 61.711 | 61.5091 | 61.9726 | 62.111 | 61.4772 | 61.88 | 62.1397 | 61.991 | 62.0837 | 62.0157 | 62.109 | 62.108 | 61.9688 | 61.7065 | 61.6964 | 61.7339 | 61.532 | 61.9955 | 62.1338 | 61.5 | 61.9029 | -0.289 | 0.20646 | -0.26161 | 0.23385
32.8281 | 124.0723 | -62.0041 | 61.7615 | 0.085224 | -0.058836 | 0.033786 | -0.047909 | 0.049999 | 0.048956 | -0.08103 | 61.6836 | 61.6689 | 61.7064 | 61.5091 | 61.968 | 62.111 | 61.4817 | 61.88 | 62.0893 | 61.9453 | 62.0379 | 61.9562 | 62.0541 | 62.053 | 61.9231 | 61.7065 | 61.6918 | 61.7293 | 61.532 | 61.9909 | 62.1338 | 61.5046 | 61.9029 | -0.28442 | 0.20188 | -0.2616 | 0.22469
34.5156 | 123.9258 | -62.0087 | 61.8439 | 0.085224 | -0.058836 | 0.029208 | -0.047909 | 0.045421 | 0.048956 | -0.076452 | 61.6882 | 61.6689 | 61.7064 | 61.4999 | 61.9772 | 62.111 | 61.4726 | 61.88 | 62.0939 | 61.9498 | 62.0379 | 61.9608 | 62.0541 | 62.0576 | 61.9322 | 61.7111 | 61.6918 | 61.7293 | 61.5228 | 62.0001 | 62.1338 | 61.4955 | 61.9029 | -0.28899 | 0.21561 | -0.27076 | 0.23385
36.2656 | 124.0036 | -62.0041 | 61.7844 | 0.089802 | -0.063415 | 0.029208 | -0.043331 | 0.054577 | 0.048956 | -0.076452 | 61.6882 | 61.6735 | 61.7018 | 61.5045 | 61.9726 | 62.111 | 61.4726 | 61.8754 | 62.0939 | 61.9407 | 62.0333 | 61.9608 | 62.0587 | 62.053 | 61.9276 | 61.7111 | 61.6964 | 61.7247 | 61.5274 | 61.9955 | 62.1338 | 61.4955 | 61.8983 | -0.28442 | 0.21561 | -0.27076 | 0.22927
38 | 123.9807 | -61.9858 | 61.8851 | 0.080646 | -0.058836 | 0.029208 | -0.057066 | 0.054577 | 0.048956 | -0.08103 | 61.6882 | 61.6735 | 61.7064 | 61.5182 | 61.9772 | 62.111 | 61.4772 | 61.8754 | 62.0664 | 61.9269 | 62.015 | 61.9287 | 62.0404 | 62.0347 | 61.9047 | 61.7111 | 61.6964 | 61.7293 | 61.5411 | 62.0001 | 62.1338 | 61.5 | 61.8983 | -0.28899 | 0.21103 | -0.27076 | 0.22927
39.6719 | 123.9532 | -62.0087 | 61.8851 | 0.089802 | -0.067994 | 0.029208 | -0.047909 | 0.059155 | 0.039799 | -0.071874 | 61.6882 | 61.678 | 61.7064 | 61.4999 | 61.9772 | 62.1064 | 61.468 | 61.8754 | 62.0985 | 61.9407 | 62.0379 | 61.9608 | 62.0678 | 62.0485 | 61.9368 | 61.7111 | 61.7009 | 61.7293 | 61.5228 | 62.0001 | 62.1293 | 61.4909 | 61.8983 | -0.28899 | 0.22019 | -0.27076 | 0.23842
41.4062 | 123.967 | -62.0453 | 61.8393 | 0.094381 | -0.067994 | 0.024629 | -0.057066 | 0.059155 | 0.048956 | -0.08103 | 61.6836 | 61.6643 | 61.7018 | 61.5274 | 61.968 | 62.1018 | 61.4634 | 61.88 | 62.1397 | 61.9773 | 62.0699 | 61.9882 | 62.1044 | 62.0942 | 61.9643 | 61.7065 | 61.6872 | 61.7247 | 61.5503 | 61.9909 | 62.1247 | 61.4863 | 61.9029 | -0.28442 | 0.22019 | -0.26618 | 0.23843
43.1406 | 123.912 | -62.0087 | 61.853 | 0.085224 | -0.058836 | 0.024629 | -0.043331 | 0.054577 | 0.044377 | -0.071874 | 61.6882 | 61.678 | 61.7064 | 61.5091 | 61.9635 | 62.1018 | 61.4634 | 61.8708 | 62.0939 | 61.9498 | 62.0333 | 61.9653 | 62.0632 | 62.053 | 61.9368 | 61.7111 | 61.7009 | 61.7293 | 61.532 | 61.9863 | 62.1247 | 61.4863 | 61.8937 | -0.27526 | 0.22477 | -0.25703 | 0.243
44.9062 | 123.9487 | -62.0224 | 61.8713 | 0.094381 | -0.063415 | 0.033786 | -0.052488 | 0.049999 | 0.053534 | -0.08103 | 61.679 | 61.6735 | 61.6973 | 61.5137 | 61.9726 | 62.1064 | 61.4634 | 61.8708 | 62.1168 | 61.959 | 62.0562 | 61.9699 | 62.0724 | 62.0759 | 61.9414 | 61.7019 | 61.6964 | 61.7202 | 61.5366 | 61.9955 | 62.1293 | 61.4863 | 61.8937 | -0.29357 | 0.21561 | -0.27534 | 0.23385
46.5625 | 123.9944 | -62.0361 | 61.7615 | 0.089802 | -0.067994 | 0.029208 | -0.052488 | 0.049999 | 0.058113 | -0.085608 | 61.6836 | 61.6689 | 61.7018 | 61.4954 | 61.968 | 62.1018 | 61.4726 | 61.8663 | 62.1259 | 61.9681 | 62.0653 | 61.9836 | 62.0861 | 62.0942 | 61.9505 | 61.7065 | 61.6918 | 61.7247 | 61.5182 | 61.9909 | 62.1247 | 61.4955 | 61.8891 | -0.28442 | 0.21103 | -0.26618 | 0.22927
48.2969 | 124.0494 | -62.0178 | 61.7661 | 0.089802 | -0.067994 | 0.024629 | -0.057066 | 0.045421 | 0.048956 | -0.090186 | 61.679 | 61.6689 | 61.6973 | 61.4999 | 61.968 | 62.0926 | 61.468 | 61.8708 | 62.1076 | 61.9498 | 62.0425 | 61.9608 | 62.0632 | 62.0668 | 61.9276 | 61.7019 | 61.6918 | 61.7202 | 61.5228 | 61.9909 | 62.1155 | 61.4909 | 61.8937 | -0.28899 | 0.21103 | -0.27076 | 0.22927
49.9688 | 124.0128 | -62.0132 | 61.7386 | 0.089802 | -0.067994 | 0.024629 | -0.052488 | 0.054577 | 0.048956 | -0.090186 | 61.6745 | 61.6643 | 61.6973 | 61.5137 | 61.9589 | 62.0972 | 61.468 | 61.8708 | 62.103 | 61.9453 | 62.0379 | 61.9608 | 62.0678 | 62.0622 | 61.9231 | 61.6973 | 61.6872 | 61.7202 | 61.5366 | 61.9818 | 62.1201 | 61.4909 | 61.8937 | -0.28442 | 0.20645 | -0.26161 | 0.22927
51.7344 | 123.9899 | -61.9949 | 61.8027 | 0.089802 | -0.058836 | 0.024629 | -0.052488 | 0.054577 | 0.053534 | -0.085608 | 61.6745 | 61.6689 | 61.6881 | 61.5045 | 61.9726 | 62.0926 | 61.4634 | 61.8342 | 62.0847 | 61.9361 | 62.0196 | 61.9424 | 62.0495 | 62.0485 | 61.9093 | 61.6973 | 61.6918 | 61.711 | 61.5274 | 61.9955 | 62.1155 | 61.4863 | 61.8571 | -0.29815 | 0.21103 | -0.2845 | 0.22469
53.6719 | 123.9212 | -61.9949 | 61.8576 | 0.085224 | -0.058836 | 0.029208 | -0.052488 | 0.054577 | 0.048956 | -0.08103 | 61.6745 | 61.6552 | 61.6927 | 61.5045 | 61.9589 | 62.0972 | 61.4588 | 61.8708 | 62.0802 | 61.9361 | 62.0241 | 61.9424 | 62.0495 | 62.0439 | 61.9139 | 61.6973 | 61.678 | 61.7156 | 61.5274 | 61.9818 | 62.1201 | 61.4817 | 61.8937 | -0.28442 | 0.21561 | -0.26618 | 0.23385
55.3594 | 124.0082 | -62.0132 | 61.7752 | 0.089802 | -0.063415 | 0.033786 | -0.052488 | 0.059155 | 0.048956 | -0.08103 | 61.6699 | 61.6597 | 61.6881 | 61.4908 | 61.9543 | 62.0972 | 61.4634 | 61.8708 | 62.103 | 61.9498 | 62.047 | 61.9608 | 62.0724 | 62.0622 | 61.9322 | 61.6928 | 61.6826 | 61.711 | 61.5137 | 61.9772 | 62.1201 | 61.4863 | 61.8937 | -0.28442 | 0.20646 | -0.26618 | 0.22469
57.0312 | 123.9578 | -61.9812 | 61.853 | 0.085224 | -0.058836 | 0.024629 | -0.047909 | 0.054577 | 0.053534 | -0.085608 | 61.679 | 61.6689 | 61.6835 | 61.5091 | 61.968 | 62.0972 | 61.4588 | 61.8571 | 62.0664 | 61.9224 | 62.0058 | 61.9333 | 62.0358 | 62.0347 | 61.8956 | 61.7019 | 61.6918 | 61.7064 | 61.532 | 61.9909 | 62.1201 | 61.4817 | 61.88 | -0.28899 | 0.22019 | -0.28449 | 0.22469
58.6875 | 123.9578 | -61.9904 | 61.853 | 0.085224 | -0.063415 | 0.024629 | -0.047909 | 0.054577 | 0.058113 | -0.08103 | 61.6699 | 61.6643 | 61.6973 | 61.4954 | 61.9635 | 62.0926 | 61.4588 | 61.8571 | 62.0756 | 61.9269 | 62.015 | 61.9424 | 62.0449 | 62.0485 | 61.9093 | 61.6928 | 61.6872 | 61.7202 | 61.5182 | 61.9863 | 62.1155 | 61.4817 | 61.88 | -0.29357 | 0.21103 | -0.26618 | 0.23842
60.3438 | 123.9716 | -62.0178 | 61.7798 | 0.089802 | -0.063415 | 0.029208 | -0.043331 | 0.054577 | 0.058113 | -0.08103 | 61.6653 | 61.6552 | 61.6835 | 61.4862 | 61.9543 | 62.0926 | 61.4588 | 61.8617 | 62.1076 | 61.9544 | 62.047 | 61.9745 | 62.0724 | 62.0759 | 61.9368 | 61.6882 | 61.678 | 61.7064 | 61.5091 | 61.9772 | 62.1155 | 61.4817 | 61.8846 | -0.289 | 0.20645 | -0.27076 | 0.22469
62.0156 | 123.9487 | -61.9858 | 61.8439 | 0.085224 | -0.054257 | 0.029208 | -0.043331 | 0.054577 | 0.053534 | -0.08103 | 61.6653 | 61.6597 | 61.6881 | 61.5045 | 61.9589 | 62.0881 | 61.4543 | 61.8571 | 62.071 | 61.9315 | 62.015 | 61.9424 | 62.0404 | 62.0393 | 61.9047 | 61.6882 | 61.6826 | 61.711 | 61.5274 | 61.9818 | 62.1109 | 61.4772 | 61.88 | -0.29357 | 0.21103 | -0.27076 | 0.23385
64.0469 | 124.0448 | -62.0087 | 61.7569 | 0.085224 | -0.072572 | 0.024629 | -0.047909 | 0.054577 | 0.048956 | -0.08103 | 61.6699 | 61.646 | 61.6835 | 61.4908 | 61.9589 | 62.0881 | 61.4543 | 61.8617 | 62.0939 | 61.9361 | 62.0333 | 61.9608 | 62.0632 | 62.0576 | 61.9276 | 61.6928 | 61.6689 | 61.7064 | 61.5137 | 61.9818 | 62.1109 | 61.4772 | 61.8846 | -0.289 | 0.21561 | -0.27534 | 0.22927
65.8438 | 124.0356 | -61.9904 | 61.7523 | 0.098959 | -0.067994 | 0.024629 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 61.6653 | 61.6506 | 61.679 | 61.4862 | 61.9543 | 62.0835 | 61.4451 | 61.8571 | 62.0893 | 61.9224 | 62.015 | 61.947 | 62.0449 | 62.0393 | 61.9093 | 61.6882 | 61.6735 | 61.7018 | 61.5091 | 61.9772 | 62.1064 | 61.468 | 61.88 | -0.289 | 0.22019 | -0.27534 | 0.23385
67.5156 | 124.0356 | -61.9995 | 61.7615 | 0.089802 | -0.063415 | 0.029208 | -0.052488 | 0.054577 | 0.048956 | -0.085608 | 61.6699 | 61.6552 | 61.679 | 61.4954 | 61.9497 | 62.0835 | 61.4634 | 61.8571 | 62.0893 | 61.9361 | 62.0287 | 61.947 | 62.0541 | 62.0485 | 61.9139 | 61.6928 | 61.678 | 61.7018 | 61.5182 | 61.9726 | 62.1064 | 61.4863 | 61.88 | -0.27984 | 0.20646 | -0.27076 | 0.21553
69.2031 | 124.0494 | -61.9904 | 61.7386 | 0.080646 | -0.058836 | 0.024629 | -0.047909 | 0.049999 | 0.053534 | -0.085608 | 61.6745 | 61.6552 | 61.6835 | 61.4999 | 61.9497 | 62.0881 | 61.4543 | 61.8525 | 62.071 | 61.9315 | 62.015 | 61.9424 | 62.0404 | 62.0439 | 61.9047 | 61.6973 | 61.678 | 61.7064 | 61.5228 | 61.9726 | 62.1109 | 61.4772 | 61.8754 | -0.27526 | 0.22019 | -0.26618 | 0.22927
70.8906 | 124.0219 | -61.9949 | 61.7523 | 0.089802 | -0.072572 | 0.029208 | -0.047909 | 0.054577 | 0.058113 | -0.085608 | 61.6653 | 61.646 | 61.6835 | 61.4862 | 61.9543 | 62.0881 | 61.4543 | 61.8525 | 62.0847 | 61.9224 | 62.0241 | 61.947 | 62.0495 | 62.053 | 61.9093 | 61.6882 | 61.6689 | 61.7064 | 61.5091 | 61.9772 | 62.1109 | 61.4772 | 61.8754 | -0.289 | 0.21103 | -0.27076 | 0.22927
72.5938 | 123.8892 | -61.9949 | 61.8347 | 0.089802 | -0.058836 | 0.024629 | -0.047909 | 0.049999 | 0.053534 | -0.08103 | 61.6607 | 61.6552 | 61.679 | 61.4816 | 61.9497 | 62.0789 | 61.4405 | 61.8479 | 62.0847 | 61.9361 | 62.0196 | 61.947 | 62.0449 | 62.0485 | 61.9139 | 61.6836 | 61.678 | 61.7018 | 61.5045 | 61.9726 | 62.1018 | 61.4634 | 61.8708 | -0.289 | 0.22019 | -0.27076 | 0.23842
74.3125 | 124.0128 | -61.9812 | 61.7432 | 0.085224 | -0.058836 | 0.020051 | -0.047909 | 0.054577 | 0.044377 | -0.08103 | 61.6607 | 61.6414 | 61.6881 | 61.4999 | 61.9451 | 62.0881 | 61.4451 | 61.8479 | 62.0664 | 61.9224 | 62.0013 | 61.9333 | 62.0358 | 62.0256 | 61.9002 | 61.6836 | 61.6643 | 61.711 | 61.5228 | 61.968 | 62.1109 | 61.468 | 61.8708 | -0.28442 | 0.21561 | -0.25703 | 0.243
75.9688 | 124.0173 | -61.9858 | 61.7477 | 0.094381 | -0.058836 | 0.024629 | -0.052488 | 0.054577 | 0.044377 | -0.085608 | 61.6607 | 61.6552 | 61.679 | 61.4862 | 61.9451 | 62.0789 | 61.4451 | 61.8113 | 62.0802 | 61.9269 | 62.0104 | 61.9333 | 62.0404 | 62.0302 | 61.9002 | 61.6836 | 61.678 | 61.7018 | 61.5091 | 61.968 | 62.1018 | 61.468 | 61.8342 | -0.28442 | 0.21561 | -0.26618 | 0.23385
77.625 | 123.999 | -61.9858 | 61.7386 | 0.085224 | -0.058836 | 0.029208 | -0.047909 | 0.049999 | 0.048956 | -0.085608 | 61.6607 | 61.6414 | 61.6744 | 61.4725 | 61.936 | 62.0835 | 61.4451 | 61.8434 | 62.071 | 61.9269 | 62.015 | 61.9379 | 62.0358 | 62.0347 | 61.9002 | 61.6836 | 61.6643 | 61.6973 | 61.4953 | 61.9589 | 62.1064 | 61.468 | 61.8663 | -0.27526 | 0.21561 | -0.2616 | 0.22927
79.2812 | 124.0128 | -61.9766 | 61.7615 | 0.085224 | -0.063415 | 0.024629 | -0.052488 | 0.054577 | 0.044377 | -0.076452 | 61.6607 | 61.6506 | 61.6744 | 61.5091 | 61.9406 | 62.0835 | 61.4405 | 61.761 | 62.0618 | 61.9132 | 62.0013 | 61.9241 | 62.0312 | 62.021 | 61.9002 | 61.6836 | 61.6735 | 61.6973 | 61.532 | 61.9634 | 62.1064 | 61.4634 | 61.7839 | -0.27984 | 0.22019 | -0.26618 | 0.23385
80.9375 | 123.999 | -61.9766 | 61.7523 | 0.094381 | -0.058836 | 0.033786 | -0.043331 | 0.054577 | 0.044377 | -0.090186 | 61.6653 | 61.646 | 61.679 | 61.4862 | 61.9406 | 62.0743 | 61.4451 | 61.7243 | 62.071 | 61.9178 | 62.0104 | 61.9333 | 62.0312 | 62.021 | 61.8864 | 61.6882 | 61.6689 | 61.7018 | 61.5091 | 61.9634 | 62.0972 | 61.468 | 61.7472 | -0.27526 | 0.22019 | -0.26161 | 0.23385
82.625 | 123.9944 | -61.9858 | 61.7706 | 0.089802 | -0.067994 | 0.029208 | -0.047909 | 0.054577 | 0.048956 | -0.085608 | 61.6653 | 61.6414 | 61.6744 | 61.4816 | 61.9406 | 62.0789 | 61.4451 | 61.7152 | 62.0756 | 61.9178 | 62.015 | 61.9379 | 62.0404 | 62.0347 | 61.9002 | 61.6882 | 61.6643 | 61.6973 | 61.5045 | 61.9634 | 62.1018 | 61.468 | 61.7381 | -0.27526 | 0.22019 | -0.26618 | 0.22927
84.2812 | 123.999 | -61.9675 | 61.7477 | 0.089802 | -0.063415 | 0.029208 | -0.052488 | 0.049999 | 0.048956 | -0.08103 | 61.6516 | 61.646 | 61.6744 | 61.477 | 61.9406 | 62.0743 | 61.4405 | 61.7243 | 62.0573 | 61.9041 | 61.9967 | 61.915 | 62.0175 | 62.0164 | 61.8864 | 61.6745 | 61.6689 | 61.6973 | 61.4999 | 61.9634 | 62.0972 | 61.4634 | 61.7472 | -0.289 | 0.21103 | -0.26618 | 0.23385
85.9375 | 124.0219 | -61.9675 | 61.7386 | 0.089802 | -0.063415 | 0.033786 | -0.038752 | 0.054577 | 0.053534 | -0.085608 | 61.6516 | 61.646 | 61.6744 | 61.4725 | 61.9406 | 62.0697 | 61.4405 | 61.7243 | 62.0573 | 61.9041 | 62.0013 | 61.9287 | 62.022 | 62.021 | 61.8819 | 61.6745 | 61.6689 | 61.6973 | 61.4953 | 61.9634 | 62.0926 | 61.4634 | 61.7472 | -0.289 | 0.21103 | -0.26618 | 0.23385
87.6094 | 123.8617 | -61.9766 | 61.821 | 0.089802 | -0.067994 | 0.024629 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 61.6607 | 61.6414 | 61.679 | 61.4862 | 61.9406 | 62.0697 | 61.4405 | 61.7243 | 62.0664 | 61.9086 | 62.0013 | 61.9333 | 62.0312 | 62.0256 | 61.8956 | 61.6836 | 61.6643 | 61.7018 | 61.5091 | 61.9634 | 62.0926 | 61.4634 | 61.7472 | -0.27984 | 0.22019 | -0.26161 | 0.23842
89.2656 | 123.88 | -61.9858 | 61.7889 | 0.089802 | -0.063415 | 0.029208 | -0.043331 | 0.054577 | 0.048956 | -0.085608 | 61.6561 | 61.6506 | 61.6698 | 61.4679 | 61.9314 | 62.0697 | 61.4314 | 61.8159 | 62.0756 | 61.9224 | 62.015 | 61.9424 | 62.0404 | 62.0347 | 61.9002 | 61.679 | 61.6735 | 61.6927 | 61.4908 | 61.9543 | 62.0926 | 61.4543 | 61.8388 | -0.27526 | 0.22477 | -0.26161 | 0.23842
90.9375 | 123.9944 | -61.972 | 61.7615 | 0.089802 | -0.058836 | 0.029208 | -0.043331 | 0.054577 | 0.053534 | -0.085608 | 61.6516 | 61.6414 | 61.6698 | 61.4908 | 61.936 | 62.0743 | 61.4268 | 61.7335 | 62.0618 | 61.9132 | 62.0013 | 61.9287 | 62.0266 | 62.0256 | 61.8864 | 61.6745 | 61.6643 | 61.6927 | 61.5137 | 61.9589 | 62.0972 | 61.4497 | 61.7564 | -0.28442 | 0.22477 | -0.26618 | 0.243
92.6719 | 123.8663 | -61.9629 | 61.8393 | 0.089802 | -0.067994 | 0.033786 | -0.047909 | 0.059155 | 0.053534 | -0.076452 | 61.6607 | 61.6368 | 61.6744 | 61.4862 | 61.9451 | 62.0652 | 61.4314 | 61.7106 | 62.0527 | 61.8949 | 61.9967 | 61.915 | 62.022 | 62.0164 | 61.8864 | 61.6836 | 61.6597 | 61.6973 | 61.5091 | 61.968 | 62.0881 | 61.4543 | 61.7335 | -0.28442 | 0.22935 | -0.27076 | 0.243
94.3594 | 123.8846 | -61.9583 | 61.8484 | 0.085224 | -0.058836 | 0.033786 | -0.047909 | 0.049999 | 0.053534 | -0.076452 | 61.6607 | 61.6368 | 61.6652 | 61.4816 | 61.936 | 62.0652 | 61.4268 | 61.7152 | 62.0435 | 61.8995 | 61.9921 | 61.9104 | 62.0083 | 62.0118 | 61.8819 | 61.6836 | 61.6597 | 61.6881 | 61.5045 | 61.9589 | 62.0881 | 61.4497 | 61.7381 | -0.27526 | 0.23392 | -0.27076 | 0.23843
96.0312 | 123.9853 | -61.9675 | 61.7386 | 0.085224 | -0.058836 | 0.029208 | -0.047909 | 0.054577 | 0.048956 | -0.08103 | 61.6561 | 61.6368 | 61.6652 | 61.4679 | 61.9406 | 62.0697 | 61.436 | 61.7014 | 62.0527 | 61.9086 | 61.9967 | 61.9196 | 62.022 | 62.0164 | 61.8864 | 61.679 | 61.6597 | 61.6881 | 61.4908 | 61.9634 | 62.0926 | 61.4588 | 61.7243 | -0.28442 | 0.22019 | -0.27534 | 0.22927
97.7031 | 123.8663 | -61.9904 | 61.7844 | 0.089802 | -0.072572 | 0.033786 | -0.043331 | 0.054577 | 0.044377 | -0.08103 | 61.6516 | 61.6323 | 61.6652 | 61.4725 | 61.9314 | 62.0697 | 61.436 | 61.7243 | 62.0802 | 61.9178 | 62.0241 | 61.947 | 62.0449 | 62.0347 | 61.9093 | 61.6745 | 61.6551 | 61.6881 | 61.4953 | 61.9543 | 62.0926 | 61.4588 | 61.7472 | -0.27984 | 0.21561 | -0.26618 | 0.22927
99.3594 | 123.912 | -61.9858 | 61.7844 | 0.085224 | -0.063415 | 0.024629 | -0.057066 | 0.059155 | 0.053534 | -0.076452 | 61.6561 | 61.6323 | 61.6606 | 61.4679 | 61.9268 | 62.0697 | 61.4314 | 61.7198 | 62.071 | 61.9224 | 62.0104 | 61.9287 | 62.0449 | 62.0393 | 61.9093 | 61.679 | 61.6551 | 61.6835 | 61.4908 | 61.9497 | 62.0926 | 61.4543 | 61.7426 | -0.27068 | 0.22477 | -0.26618 | 0.22927
101.0312 | 123.88 | -61.9949 | 61.7706 | 0.085224 | -0.054257 | 0.024629 | -0.038752 | 0.06831 | 0.053534 | -0.076452 | 61.6516 | 61.6323 | 61.6606 | 61.477 | 61.936 | 62.0697 | 61.4222 | 61.7106 | 62.0802 | 61.9407 | 62.0196 | 61.9562 | 62.0632 | 62.0485 | 61.9185 | 61.6745 | 61.6551 | 61.6835 | 61.4999 | 61.9589 | 62.0926 | 61.4451 | 61.7335 | -0.28442 | 0.22935 | -0.27534 | 0.23842
102.7188 | 123.848 | -62.0041 | 61.821 | 0.089802 | -0.067994 | 0.020051 | -0.047909 | 0.059155 | 0.048956 | -0.08103 | 61.6516 | 61.6368 | 61.6652 | 61.4862 | 61.9314 | 62.0606 | 61.4268 | 61.7198 | 62.0939 | 61.9361 | 62.0241 | 61.9562 | 62.0632 | 62.053 | 61.9231 | 61.6745 | 61.6597 | 61.6881 | 61.5091 | 61.9543 | 62.0835 | 61.4497 | 61.7426 | -0.27984 | 0.22477 | -0.26618 | 0.23843
104.375 | 123.9029 | -61.972 | 61.7935 | 0.089802 | -0.058836 | 0.024629 | -0.043331 | 0.059155 | 0.044377 | -0.085608 | 61.647 | 61.6323 | 61.6652 | 61.4862 | 61.9268 | 62.0652 | 61.4222 | 61.7198 | 62.0618 | 61.9132 | 61.9967 | 61.9287 | 62.0312 | 62.0164 | 61.8864 | 61.6699 | 61.6551 | 61.6881 | 61.5091 | 61.9497 | 62.0881 | 61.4451 | 61.7426 | -0.27984 | 0.22477 | -0.26161 | 0.243
106.0469 | 123.967 | -61.9629 | 61.7386 | 0.089802 | -0.063415 | 0.029208 | -0.052488 | 0.059155 | 0.048956 | -0.085608 | 61.647 | 61.6368 | 61.6606 | 61.4587 | 61.9222 | 62.0606 | 61.4222 | 61.7243 | 62.0527 | 61.8995 | 61.9921 | 61.9104 | 62.022 | 62.0118 | 61.8773 | 61.6699 | 61.6597 | 61.6835 | 61.4816 | 61.9451 | 62.0835 | 61.4451 | 61.7472 | -0.27526 | 0.22477 | -0.26161 | 0.23842
107.7344 | 123.9578 | -61.9537 | 61.7386 | 0.10354 | -0.063415 | 0.020051 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 61.6424 | 61.6277 | 61.6606 | 61.4862 | 61.9268 | 62.0606 | 61.4268 | 61.7381 | 62.0573 | 61.8903 | 61.9738 | 61.9104 | 62.0083 | 62.0027 | 61.8727 | 61.6653 | 61.6506 | 61.6835 | 61.5091 | 61.9497 | 62.0835 | 61.4497 | 61.761 | -0.28442 | 0.21561 | -0.26618 | 0.23385
109.4219 | 123.9487 | -61.9675 | 61.7386 | 0.085224 | -0.058836 | 0.038365 | -0.047909 | 0.049999 | 0.053534 | -0.076452 | 61.6424 | 61.6277 | 61.6606 | 61.5274 | 61.9222 | 62.056 | 61.4176 | 61.7427 | 62.0527 | 61.9086 | 62.0058 | 61.9196 | 62.0175 | 62.021 | 61.891 | 61.6653 | 61.6506 | 61.6835 | 61.5503 | 61.9451 | 62.0789 | 61.4405 | 61.7655 | -0.27984 | 0.22477 | -0.26161 | 0.243
111.0781 | 123.9441 | -61.9812 | 61.7111 | 0.089802 | -0.067994 | 0.029208 | -0.057066 | 0.054577 | 0.048956 | -0.085608 | 61.647 | 61.6368 | 61.6606 | 61.5045 | 61.9131 | 62.0606 | 61.4222 | 61.7427 | 62.071 | 61.9132 | 62.0104 | 61.9241 | 62.0358 | 62.0302 | 61.8956 | 61.6699 | 61.6597 | 61.6835 | 61.5274 | 61.936 | 62.0835 | 61.4451 | 61.7655 | -0.26611 | 0.22477 | -0.25245 | 0.23842
112.8125 | 123.9075 | -61.9766 | 61.7111 | 0.089802 | -0.058836 | 0.024629 | -0.047909 | 0.059155 | 0.044377 | -0.08103 | 61.6424 | 61.6277 | 61.6606 | 61.477 | 61.9222 | 62.0606 | 61.4131 | 61.7381 | 62.0664 | 61.9178 | 62.0013 | 61.9287 | 62.0358 | 62.021 | 61.8956 | 61.6653 | 61.6506 | 61.6835 | 61.4999 | 61.9451 | 62.0835 | 61.4359 | 61.761 | -0.27984 | 0.22935 | -0.26161 | 0.24758
114.5312 | 123.912 | -61.9949 | 61.7249 | 0.089802 | -0.063415 | 0.024629 | -0.052488 | 0.059155 | 0.058113 | -0.085608 | 61.6424 | 61.6323 | 61.6515 | 61.477 | 61.9177 | 62.0514 | 61.4222 | 61.7518 | 62.0847 | 61.9315 | 62.0196 | 61.9424 | 62.0541 | 62.053 | 61.9093 | 61.6653 | 61.6551 | 61.6744 | 61.4999 | 61.9406 | 62.0743 | 61.4451 | 61.7747 | -0.27526 | 0.22019 | -0.26618 | 0.22927
116.1875 | 123.9304 | -61.94 | 61.7523 | 0.085224 | -0.058836 | 0.029208 | -0.047909 | 0.059155 | 0.058113 | -0.08103 | 61.6424 | 61.6277 | 61.6561 | 61.4999 | 61.9131 | 62.0606 | 61.4085 | 61.7472 | 62.0252 | 61.8812 | 61.9692 | 61.8921 | 61.9992 | 61.9981 | 61.859 | 61.6653 | 61.6506 | 61.679 | 61.5228 | 61.936 | 62.0835 | 61.4314 | 61.7701 | -0.27069 | 0.23392 | -0.25703 | 0.24758
117.8906 | 123.9624 | -61.9537 | 61.7203 | 0.085224 | -0.063415 | 0.024629 | -0.043331 | 0.054577 | 0.044377 | -0.085608 | 61.6424 | 61.6231 | 61.6561 | 61.477 | 61.9177 | 62.056 | 61.4222 | 61.7427 | 62.039 | 61.8903 | 61.9784 | 61.9104 | 62.0083 | 61.9981 | 61.8681 | 61.6653 | 61.646 | 61.679 | 61.4999 | 61.9406 | 62.0789 | 61.4451 | 61.7655 | -0.27526 | 0.22019 | -0.26161 | 0.23385
119.6094 | 123.8525 | -61.9354 | 61.8073 | 0.094381 | -0.063415 | 0.038365 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 61.6424 | 61.6277 | 61.6561 | 61.5091 | 61.9177 | 62.0514 | 61.4176 | 61.7381 | 62.0298 | 61.872 | 61.9738 | 61.8921 | 61.9946 | 61.989 | 61.859 | 61.6653 | 61.6506 | 61.679 | 61.532 | 61.9406 | 62.0743 | 61.4405 | 61.761 | -0.27526 | 0.22477 | -0.26161 | 0.23843
121.3125 | 123.9395 | -61.9354 | 61.7157 | 0.094381 | -0.063415 | 0.024629 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 61.6332 | 61.6323 | 61.6515 | 61.4816 | 61.9131 | 62.056 | 61.4176 | 61.7243 | 62.0298 | 61.872 | 61.9601 | 61.8921 | 61.99 | 61.9844 | 61.8544 | 61.6561 | 61.6551 | 61.6744 | 61.5045 | 61.936 | 62.0789 | 61.4405 | 61.7472 | -0.27984 | 0.21561 | -0.2616 | 0.23385
122.9844 | 123.8663 | -61.9354 | 61.7752 | 0.085224 | -0.058836 | 0.029208 | -0.052488 | 0.054577 | 0.048956 | -0.08103 | 61.6332 | 61.6231 | 61.6561 | 61.5045 | 61.9177 | 62.0514 | 61.4039 | 61.7381 | 62.0206 | 61.8766 | 61.9646 | 61.8829 | 61.99 | 61.9844 | 61.8544 | 61.6561 | 61.646 | 61.679 | 61.5274 | 61.9406 | 62.0743 | 61.4268 | 61.761 | -0.28442 | 0.22935 | -0.26161 | 0.25216
124.6562 | 123.8205 | -61.9858 | 61.7661 | 0.094381 | -0.063415 | 0.038365 | -0.043331 | 0.054577 | 0.053534 | -0.076452 | 61.6378 | 61.6277 | 61.6469 | 61.4999 | 61.9131 | 62.0469 | 61.3947 | 61.7381 | 62.0802 | 61.9224 | 62.0241 | 61.9424 | 62.0404 | 62.0393 | 61.9093 | 61.6607 | 61.6506 | 61.6698 | 61.5228 | 61.936 | 62.0697 | 61.4176 | 61.761 | -0.27526 | 0.24308 | -0.26618 | 0.25216
126.3281 | 123.8342 | -61.9492 | 61.7935 | 0.080646 | -0.058836 | 0.024629 | -0.047909 | 0.054577 | 0.053534 | -0.08103 | 61.6378 | 61.6231 | 61.6377 | 61.4633 | 61.9177 | 62.0469 | 61.4085 | 61.7427 | 62.0298 | 61.8903 | 61.9738 | 61.9012 | 62.0037 | 62.0027 | 61.8681 | 61.6607 | 61.646 | 61.6606 | 61.4862 | 61.9406 | 62.0697 | 61.4314 | 61.7655 | -0.27984 | 0.22935 | -0.27992 | 0.22927
128 | 123.9349 | -61.9537 | 61.7065 | 0.085224 | -0.063415 | 0.029208 | -0.052488 | 0.059155 | 0.053534 | -0.08103 | 61.6378 | 61.6231 | 61.6469 | 61.5091 | 61.9131 | 62.0423 | 61.4039 | 61.7335 | 62.039 | 61.8903 | 61.9829 | 61.9012 | 62.0129 | 62.0073 | 61.8727 | 61.6607 | 61.646 | 61.6698 | 61.532 | 61.936 | 62.0652 | 61.4268 | 61.7564 | -0.27526 | 0.23392 | -0.26618 | 0.243
129.6719 | 123.8709 | -61.9217 | 61.7981 | 0.089802 | -0.067994 | 0.029208 | -0.043331 | 0.059155 | 0.053534 | -0.08103 | 61.6424 | 61.6139 | 61.6423 | 61.5137 | 61.9177 | 62.0469 | 61.4039 | 61.7472 | 62.0115 | 61.8537 | 61.9509 | 61.8784 | 61.9808 | 61.9752 | 61.8407 | 61.6653 | 61.6368 | 61.6652 | 61.5366 | 61.9406 | 62.0697 | 61.4268 | 61.7701 | -0.27526 | 0.2385 | -0.27534 | 0.23843
131.3438 | 123.9578 | -61.972 | 61.7294 | 0.089802 | -0.054257 | 0.029208 | -0.043331 | 0.059155 | 0.044377 | -0.085608 | 61.6378 | 61.6139 | 61.6423 | 61.4862 | 61.9177 | 62.0423 | 61.4039 | 61.7381 | 62.0618 | 61.9178 | 62.0013 | 61.9287 | 62.0312 | 62.0164 | 61.8864 | 61.6607 | 61.6368 | 61.6652 | 61.5091 | 61.9406 | 62.0652 | 61.4268 | 61.761 | -0.27984 | 0.23392 | -0.27534 | 0.23843
133.0156 | 123.8068 | -61.9446 | 61.7935 | 0.089802 | -0.058836 | 0.029208 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 61.6287 | 61.6277 | 61.6423 | 61.5045 | 61.9085 | 62.0423 | 61.4039 | 61.7518 | 62.0344 | 61.8857 | 61.9738 | 61.8967 | 61.9992 | 61.9935 | 61.8681 | 61.6516 | 61.6506 | 61.6652 | 61.5274 | 61.9314 | 62.0652 | 61.4268 | 61.7747 | -0.27984 | 0.22477 | -0.26618 | 0.23843
134.7188 | 123.9532 | -61.94 | 61.702 | 0.089802 | -0.054257 | 0.029208 | -0.052488 | 0.059155 | 0.039799 | -0.08103 | 61.6241 | 61.6185 | 61.6423 | 61.4954 | 61.9039 | 62.0423 | 61.4085 | 61.7472 | 62.0298 | 61.8857 | 61.9692 | 61.8875 | 61.9992 | 61.9798 | 61.859 | 61.647 | 61.6414 | 61.6652 | 61.5182 | 61.9268 | 62.0652 | 61.4314 | 61.7701 | -0.27984 | 0.21561 | -0.26161 | 0.23385
136.4219 | 123.8251 | -61.9629 | 61.7569 | 0.098959 | -0.058836 | 0.033786 | -0.047909 | 0.059155 | 0.044377 | -0.085608 | 61.6332 | 61.6185 | 61.6423 | 61.4954 | 61.8994 | 62.0469 | 61.3947 | 61.7427 | 62.0618 | 61.9041 | 61.9967 | 61.915 | 62.022 | 62.0073 | 61.8773 | 61.6561 | 61.6414 | 61.6652 | 61.5182 | 61.9222 | 62.0697 | 61.4176 | 61.7655 | -0.26611 | 0.2385 | -0.25703 | 0.24758
138.1094 | 123.8937 | -61.9675 | 61.7111 | 0.085224 | -0.054257 | 0.029208 | -0.047909 | 0.059155 | 0.048956 | -0.085608 | 61.6378 | 61.6231 | 61.6377 | 61.4725 | 61.9039 | 62.0377 | 61.4039 | 61.7381 | 62.0527 | 61.9132 | 61.9967 | 61.9196 | 62.0266 | 62.0164 | 61.8819 | 61.6607 | 61.646 | 61.6606 | 61.4953 | 61.9268 | 62.0606 | 61.4268 | 61.761 | -0.26611 | 0.23392 | -0.26618 | 0.23385
139.8281 | 123.9304 | -61.9308 | 61.7111 | 0.089802 | -0.054257 | 0.029208 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 61.6332 | 61.6048 | 61.6469 | 61.5137 | 61.8948 | 62.0423 | 61.3947 | 61.7243 | 62.0206 | 61.8766 | 61.9601 | 61.8829 | 61.9854 | 61.9798 | 61.8544 | 61.6561 | 61.6277 | 61.6698 | 61.5366 | 61.9177 | 62.0652 | 61.4176 | 61.7472 | -0.26153 | 0.2385 | -0.24787 | 0.25216
141.5 | 123.8663 | -61.9629 | 61.702 | 0.089802 | -0.058836 | 0.033786 | -0.052488 | 0.054577 | 0.048956 | -0.08103 | 61.6195 | 61.6139 | 61.6377 | 61.5045 | 61.9039 | 62.0377 | 61.3902 | 61.7427 | 62.0527 | 61.9041 | 61.9967 | 61.9104 | 62.0175 | 62.0118 | 61.8819 | 61.6424 | 61.6368 | 61.6606 | 61.5274 | 61.9268 | 62.0606 | 61.4131 | 61.7655 | -0.28442 | 0.22935 | -0.26618 | 0.24758
143.1719 | 123.7976 | -61.9446 | 61.8164 | 0.089802 | -0.067994 | 0.033786 | -0.052488 | 0.059155 | 0.044377 | -0.076452 | 61.6241 | 61.6139 | 61.6332 | 61.5182 | 61.8994 | 62.0469 | 61.3993 | 61.7381 | 62.0344 | 61.8766 | 61.9784 | 61.8921 | 62.0037 | 61.989 | 61.8681 | 61.647 | 61.6368 | 61.6561 | 61.5411 | 61.9222 | 62.0697 | 61.4222 | 61.761 | -0.27526 | 0.22477 | -0.26618 | 0.23385
144.875 | 123.7976 | -61.9354 | 61.7935 | 0.098959 | -0.058836 | 0.033786 | -0.047909 | 0.063733 | 0.053534 | -0.08103 | 61.6195 | 61.6048 | 61.6332 | 61.5228 | 61.8948 | 62.0331 | 61.3947 | 61.7289 | 62.0344 | 61.8766 | 61.9692 | 61.8875 | 61.9992 | 61.989 | 61.8544 | 61.6424 | 61.6277 | 61.6561 | 61.5457 | 61.9177 | 62.056 | 61.4176 | 61.7518 | -0.27527 | 0.22477 | -0.26161 | 0.23843
146.5625 | 123.8297 | -61.9034 | 61.7844 | 0.089802 | -0.054257 | 0.033786 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 61.6195 | 61.6094 | 61.6332 | 61.5137 | 61.8994 | 62.0331 | 61.3947 | 61.7289 | 61.9932 | 61.8491 | 61.9372 | 61.8555 | 61.9625 | 61.9523 | 61.8269 | 61.6424 | 61.6323 | 61.6561 | 61.5366 | 61.9222 | 62.056 | 61.4176 | 61.7518 | -0.27984 | 0.22477 | -0.26618 | 0.23843
148.25 | 123.9258 | -61.9537 | 61.6974 | 0.085224 | -0.058836 | 0.033786 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 61.6287 | 61.6094 | 61.6377 | 61.5411 | 61.8994 | 62.0331 | 61.3993 | 61.7381 | 62.039 | 61.8949 | 61.9875 | 61.9104 | 62.0129 | 62.0073 | 61.8773 | 61.6516 | 61.6323 | 61.6606 | 61.564 | 61.9222 | 62.056 | 61.4222 | 61.761 | -0.27069 | 0.22935 | -0.26161 | 0.23843
149.9375 | 123.8754 | -61.9675 | 61.6745 | 0.089802 | -0.067994 | 0.038365 | -0.043331 | 0.054577 | 0.044377 | -0.085608 | 61.6241 | 61.6139 | 61.6377 | 61.5137 | 61.8948 | 62.0285 | 61.3947 | 61.7335 | 62.0573 | 61.8995 | 62.0058 | 61.9241 | 62.022 | 62.0118 | 61.8819 | 61.647 | 61.6368 | 61.6606 | 61.5366 | 61.9177 | 62.0514 | 61.4176 | 61.7564 | -0.27069 | 0.22935 | -0.25703 | 0.243
151.6562 | 123.7885 | -61.9171 | 61.7981 | 0.085224 | -0.063415 | 0.024629 | -0.043331 | 0.059155 | 0.048956 | -0.076452 | 61.6195 | 61.6048 | 61.624 | 61.532 | 61.8994 | 62.0331 | 61.3902 | 61.7335 | 62.0023 | 61.8537 | 61.9417 | 61.8738 | 61.9763 | 61.9661 | 61.8407 | 61.6424 | 61.6277 | 61.6469 | 61.5549 | 61.9222 | 62.056 | 61.4131 | 61.7564 | -0.27984 | 0.22935 | -0.27534 | 0.23385
153.3281 | 123.8159 | -61.9217 | 61.7798 | 0.089802 | -0.058836 | 0.033786 | -0.052488 | 0.059155 | 0.053534 | -0.076452 | 61.6195 | 61.6139 | 61.6332 | 61.4999 | 61.8948 | 62.0331 | 61.3856 | 61.7289 | 62.0115 | 61.8629 | 61.9555 | 61.8692 | 61.9808 | 61.9752 | 61.8452 | 61.6424 | 61.6368 | 61.6561 | 61.5228 | 61.9177 | 62.056 | 61.4085 | 61.7518 | -0.27527 | 0.23392 | -0.26161 | 0.24758
155.0156 | 123.8434 | -61.9034 | 61.7661 | 0.089802 | -0.054257 | 0.033786 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 61.6195 | 61.6185 | 61.6332 | 61.5182 | 61.8994 | 62.0331 | 61.3902 | 61.7243 | 61.9932 | 61.8491 | 61.9372 | 61.8601 | 61.9625 | 61.9569 | 61.8269 | 61.6424 | 61.6414 | 61.6561 | 61.5411 | 61.9222 | 62.056 | 61.4131 | 61.7472 | -0.27984 | 0.22935 | -0.26618 | 0.24301
156.6719 | 123.9029 | -61.9492 | 61.6882 | 0.085224 | -0.049678 | 0.033786 | -0.052488 | 0.059155 | 0.053534 | -0.076452 | 61.6149 | 61.6048 | 61.6286 | 61.4862 | 61.8902 | 62.0285 | 61.3856 | 61.7198 | 62.0344 | 61.8995 | 61.9829 | 61.8967 | 62.0083 | 62.0027 | 61.8727 | 61.6378 | 61.6277 | 61.6515 | 61.5091 | 61.9131 | 62.0514 | 61.4085 | 61.7426 | -0.27527 | 0.22934 | -0.26161 | 0.243
158.3281 | 123.7885 | -61.9217 | 61.7844 | 0.080646 | -0.054257 | 0.024629 | -0.043331 | 0.049999 | 0.048956 | -0.08103 | 61.6058 | 61.6094 | 61.6286 | 61.5091 | 61.8902 | 62.0285 | 61.3856 | 61.7243 | 62.0023 | 61.8674 | 61.9463 | 61.8784 | 61.9717 | 61.9706 | 61.8407 | 61.6287 | 61.6323 | 61.6515 | 61.532 | 61.9131 | 62.0514 | 61.4085 | 61.7472 | -0.28442 | 0.22019 | -0.26161 | 0.243
160 | 123.8617 | -61.9217 | 61.7294 | 0.089802 | -0.058836 | 0.029208 | -0.043331 | 0.049999 | 0.044377 | -0.076452 | 61.6104 | 61.6048 | 61.6286 | 61.5182 | 61.8994 | 62.024 | 61.3856 | 61.7243 | 62.0115 | 61.8629 | 61.9509 | 61.8784 | 61.9717 | 61.9661 | 61.8452 | 61.6332 | 61.6277 | 61.6515 | 61.5411 | 61.9222 | 62.0469 | 61.4085 | 61.7472 | -0.289 | 0.22477 | -0.27076 | 0.243
161.6875 | 123.7701 | -61.9354 | 61.7752 | 0.089802 | -0.054257 | 0.033786 | -0.052488 | 0.059155 | 0.053534 | -0.085608 | 61.6149 | 61.591 | 61.6332 | 61.5274 | 61.8902 | 62.024 | 61.381 | 61.7335 | 62.0252 | 61.8812 | 61.9692 | 61.8829 | 61.9946 | 61.989 | 61.8498 | 61.6378 | 61.6139 | 61.6561 | 61.5503 | 61.9131 | 62.0469 | 61.4039 | 61.7564 | -0.27527 | 0.23392 | -0.25703 | 0.25216
163.3594 | 123.8983 | -61.9308 | 61.6837 | 0.085224 | -0.054257 | 0.038365 | -0.047909 | 0.059155 | 0.048956 | -0.090186 | 61.6104 | 61.6002 | 61.6286 | 61.5045 | 61.881 | 62.024 | 61.381 | 61.7243 | 62.0161 | 61.8766 | 61.9692 | 61.8829 | 61.99 | 61.9798 | 61.8407 | 61.6332 | 61.6231 | 61.6515 | 61.5274 | 61.9039 | 62.0469 | 61.4039 | 61.7472 | -0.27069 | 0.22935 | -0.25245 | 0.24758
165.0625 | 123.848 | -61.9217 | 61.7203 | 0.085224 | -0.054257 | 0.033786 | -0.052488 | 0.063733 | 0.044377 | -0.08103 | 61.6104 | 61.6048 | 61.6286 | 61.5228 | 61.8948 | 62.0285 | 61.381 | 61.7289 | 62.0069 | 61.8674 | 61.9555 | 61.8692 | 61.9854 | 61.9661 | 61.8407 | 61.6332 | 61.6277 | 61.6515 | 61.5457 | 61.9177 | 62.0514 | 61.4039 | 61.7518 | -0.28442 | 0.22935 | -0.26619 | 0.24758
166.7344 | 123.7747 | -61.9263 | 61.7615 | 0.094381 | -0.054257 | 0.029208 | -0.047909 | 0.059155 | 0.048956 | -0.08103 | 61.6149 | 61.6048 | 61.6194 | 61.5228 | 61.8902 | 62.0194 | 61.381 | 61.7243 | 62.0207 | 61.872 | 61.9555 | 61.8784 | 61.9854 | 61.9752 | 61.8452 | 61.6378 | 61.6277 | 61.6423 | 61.5457 | 61.9131 | 62.0423 | 61.4039 | 61.7472 | -0.27527 | 0.23392 | -0.27076 | 0.23843
168.4062 | 123.8205 | -61.9034 | 61.7798 | 0.085224 | -0.058836 | 0.029208 | -0.047909 | 0.059155 | 0.053534 | -0.08103 | 61.6149 | 61.6002 | 61.6194 | 61.4954 | 61.8765 | 62.024 | 61.3719 | 61.7198 | 61.9886 | 61.8445 | 61.9326 | 61.8555 | 61.9625 | 61.9569 | 61.8224 | 61.6378 | 61.6231 | 61.6423 | 61.5182 | 61.8994 | 62.0469 | 61.3947 | 61.7426 | -0.26153 | 0.24308 | -0.25703 | 0.24758
170.0938 | 123.8754 | -61.908 | 61.7249 | 0.085224 | -0.058836 | 0.029208 | -0.043331 | 0.059155 | 0.048956 | -0.085608 | 61.6104 | 61.5956 | 61.6194 | 61.5366 | 61.8856 | 62.024 | 61.3902 | 61.7243 | 61.9932 | 61.8491 | 61.9372 | 61.8646 | 61.9671 | 61.9569 | 61.8224 | 61.6332 | 61.6185 | 61.6423 | 61.5595 | 61.9085 | 62.0469 | 61.4131 | 61.7472 | -0.27526 | 0.22019 | -0.26618 | 0.22927
171.8281 | 123.7656 | -61.94 | 61.7477 | 0.080646 | -0.058836 | 0.029208 | -0.052488 | 0.063733 | 0.048956 | -0.08103 | 61.6104 | 61.591 | 61.6149 | 61.5137 | 61.8719 | 62.0148 | 61.3673 | 61.7152 | 62.0206 | 61.8812 | 61.9692 | 61.8875 | 62.0037 | 61.989 | 61.859 | 61.6332 | 61.6139 | 61.6377 | 61.5366 | 61.8948 | 62.0377 | 61.3902 | 61.7381 | -0.26153 | 0.24308 | -0.25703 | 0.24758
173.5 | 123.8892 | -61.9125 | 61.7157 | 0.089802 | -0.054257 | 0.024629 | -0.043331 | 0.059155 | 0.048956 | -0.08103 | 61.6104 | 61.6048 | 61.6149 | 61.5411 | 61.8765 | 62.0194 | 61.381 | 61.7243 | 62.0023 | 61.8583 | 61.9372 | 61.8692 | 61.9717 | 61.9615 | 61.8315 | 61.6332 | 61.6277 | 61.6377 | 61.564 | 61.8994 | 62.0423 | 61.4039 | 61.7472 | -0.26611 | 0.22935 | -0.26161 | 0.23385
175.1719 | 123.8846 | -61.8942 | 61.6699 | 0.085224 | -0.058836 | 0.029208 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 61.6104 | 61.5956 | 61.6194 | 61.532 | 61.881 | 62.0148 | 61.3673 | 61.7106 | 61.9794 | 61.8354 | 61.9234 | 61.8509 | 61.9488 | 61.9432 | 61.8132 | 61.6332 | 61.6185 | 61.6423 | 61.5549 | 61.9039 | 62.0377 | 61.3902 | 61.7335 | -0.27069 | 0.24308 | -0.26161 | 0.25216
176.875 | 123.7518 | -61.94 | 61.7432 | 0.085224 | -0.054257 | 0.038365 | -0.043331 | 0.063733 | 0.053534 | -0.071874 | 61.6104 | 61.6002 | 61.6194 | 61.5411 | 61.8765 | 62.0148 | 61.3764 | 61.7106 | 62.0252 | 61.8857 | 61.9784 | 61.8967 | 62.0037 | 61.9935 | 61.8681 | 61.6332 | 61.6231 | 61.6423 | 61.564 | 61.8994 | 62.0377 | 61.3993 | 61.7335 | -0.26611 | 0.23392 | -0.25703 | 0.243
178.5469 | 123.8251 | -61.9263 | 61.6928 | 0.076067 | -0.058836 | 0.033786 | -0.043331 | 0.059155 | 0.048956 | -0.08103 | 61.6012 | 61.591 | 61.6194 | 61.5228 | 61.8765 | 62.0102 | 61.3764 | 61.7198 | 62.0023 | 61.8674 | 61.9601 | 61.8829 | 61.9854 | 61.9752 | 61.8452 | 61.6241 | 61.6139 | 61.6423 | 61.5457 | 61.8994 | 62.0331 | 61.3993 | 61.7426 | -0.27527 | 0.22477 | -0.25703 | 0.243
180.2188 | 123.7289 | -61.8896 | 61.7798 | 0.085224 | -0.054257 | 0.033786 | -0.043331 | 0.063733 | 0.048956 | -0.076452 | 61.6104 | 61.591 | 61.624 | 61.5366 | 61.8719 | 62.0148 | 61.3673 | 61.7106 | 61.9749 | 61.8354 | 61.9234 | 61.8463 | 61.9534 | 61.9386 | 61.8132 | 61.6332 | 61.6139 | 61.6469 | 61.5595 | 61.8948 | 62.0377 | 61.3902 | 61.7335 | -0.26153 | 0.24308 | -0.24787 | 0.25674
181.9062 | 123.7381 | -61.9354 | 61.7706 | 0.085224 | -0.054257 | 0.029208 | -0.043331 | 0.063733 | 0.053534 | -0.08103 | 61.6058 | 61.591 | 61.6103 | 61.5091 | 61.8765 | 62.0102 | 61.3673 | 61.7198 | 62.0206 | 61.8812 | 61.9646 | 61.8921 | 61.9992 | 61.989 | 61.8544 | 61.6287 | 61.6139 | 61.6332 | 61.532 | 61.8994 | 62.0331 | 61.3902 | 61.7426 | -0.27069 | 0.2385 | -0.26619 | 0.24301
183.5781 | 123.7518 | -61.9171 | 61.7752 | 0.089802 | -0.058836 | 0.024629 | -0.043331 | 0.063733 | 0.053534 | -0.076452 | 61.6058 | 61.5819 | 61.6149 | 61.5228 | 61.8765 | 62.0057 | 61.3673 | 61.7106 | 62.0069 | 61.8583 | 61.9417 | 61.8738 | 61.9808 | 61.9706 | 61.8407 | 61.6287 | 61.6048 | 61.6377 | 61.5457 | 61.8994 | 62.0285 | 61.3902 | 61.7335 | -0.27069 | 0.2385 | -0.26161 | 0.24758
185.25 | 123.8434 | -61.908 | 61.7157 | 0.089802 | -0.058836 | 0.029208 | -0.047909 | 0.059155 | 0.044377 | -0.085608 | 61.6012 | 61.5865 | 61.6149 | 61.532 | 61.8673 | 62.0102 | 61.3673 | 61.7152 | 61.9978 | 61.8491 | 61.9372 | 61.8601 | 61.9671 | 61.9523 | 61.8224 | 61.6241 | 61.6094 | 61.6377 | 61.5549 | 61.8902 | 62.0331 | 61.3902 | 61.7381 | -0.26611 | 0.23392 | -0.25245 | 0.24758
186.9375 | 123.8159 | -61.9308 | 61.6837 | 0.085224 | -0.054257 | 0.024629 | -0.043331 | 0.059155 | 0.058113 | -0.076452 | 61.6058 | 61.591 | 61.6057 | 61.5228 | 61.8673 | 62.0102 | 61.3673 | 61.7106 | 62.0161 | 61.8766 | 61.9555 | 61.8875 | 61.99 | 61.989 | 61.8544 | 61.6287 | 61.6139 | 61.6286 | 61.5457 | 61.8902 | 62.0331 | 61.3902 | 61.7335 | -0.26153 | 0.2385 | -0.26161 | 0.23843
188.6094 | 123.7701 | -61.8851 | 61.7523 | 0.089802 | -0.058836 | 0.029208 | -0.043331 | 0.063733 | 0.048956 | -0.08103 | 61.5966 | 61.591 | 61.6149 | 61.532 | 61.8765 | 62.0057 | 61.3535 | 61.7106 | 61.9749 | 61.8262 | 61.9143 | 61.8417 | 61.9488 | 61.934 | 61.804 | 61.6195 | 61.6139 | 61.6377 | 61.5549 | 61.8994 | 62.0285 | 61.3764 | 61.7335 | -0.27985 | 0.24308 | -0.26161 | 0.26132
190.2969 | 123.8709 | -61.9263 | 61.6699 | 0.089802 | -0.058836 | 0.029208 | -0.043331 | 0.063733 | 0.044377 | -0.085608 | 61.6058 | 61.591 | 61.6149 | 61.5182 | 61.8627 | 62.0011 | 61.3627 | 61.7014 | 62.0161 | 61.8674 | 61.9555 | 61.8829 | 61.99 | 61.9706 | 61.8407 | 61.6287 | 61.6139 | 61.6377 | 61.5411 | 61.8856 | 62.024 | 61.3856 | 61.7243 | -0.25695 | 0.24308 | -0.24787 | 0.25216
191.9844 | 123.8571 | -61.9217 | 61.6699 | 0.094381 | -0.054257 | 0.029208 | -0.043331 | 0.063733 | 0.044377 | -0.08103 | 61.5966 | 61.5865 | 61.6057 | 61.5091 | 61.8719 | 62.0057 | 61.3627 | 61.706 | 62.0161 | 61.8674 | 61.9509 | 61.8784 | 61.9854 | 61.9661 | 61.8407 | 61.6195 | 61.6094 | 61.6286 | 61.532 | 61.8948 | 62.0285 | 61.3856 | 61.7289 | -0.27527 | 0.23392 | -0.26619 | 0.24301
193.7031 | 123.8754 | -61.8896 | 61.6882 | 0.085224 | -0.063415 | 0.024629 | -0.043331 | 0.054577 | 0.048956 | -0.076452 | 61.6012 | 61.591 | 61.6149 | 61.5274 | 61.8719 | 62.0011 | 61.3627 | 61.7014 | 61.9749 | 61.8262 | 61.9143 | 61.8463 | 61.9442 | 61.9386 | 61.8132 | 61.6241 | 61.6139 | 61.6377 | 61.5503 | 61.8948 | 62.024 | 61.3856 | 61.7243 | -0.27069 | 0.2385 | -0.25703 | 0.25216
195.375 | 123.7335 | -61.9308 | 61.7477 | 0.089802 | -0.058836 | 0.029208 | -0.043331 | 0.059155 | 0.044377 | -0.08103 | 61.6012 | 61.5819 | 61.6057 | 61.5274 | 61.8719 | 62.0011 | 61.349 | 61.6969 | 62.0206 | 61.872 | 61.9601 | 61.8875 | 61.99 | 61.9752 | 61.8498 | 61.6241 | 61.6048 | 61.6286 | 61.5503 | 61.8948 | 62.024 | 61.3719 | 61.7198 | -0.27069 | 0.25224 | -0.26619 | 0.25674
197.1875 | 123.8709 | -61.9171 | 61.6608 | 0.085224 | -0.058836 | 0.024629 | -0.052488 | 0.059155 | 0.039799 | -0.085608 | 61.6012 | 61.5865 | 61.6149 | 61.532 | 61.8673 | 62.0011 | 61.3627 | 61.7014 | 62.0023 | 61.8583 | 61.9417 | 61.8646 | 61.9763 | 61.9569 | 61.8315 | 61.6241 | 61.6094 | 61.6377 | 61.5549 | 61.8902 | 62.024 | 61.3856 | 61.7243 | -0.26611 | 0.2385 | -0.25245 | 0.25216
198.9375 | 123.7656 | -61.8851 | 61.7844 | 0.085224 | -0.054257 | 0.029208 | -0.047909 | 0.063733 | 0.053534 | -0.076452 | 61.592 | 61.5773 | 61.6103 | 61.5137 | 61.8627 | 62.0011 | 61.3535 | 61.7014 | 61.9703 | 61.8308 | 61.9143 | 61.8372 | 61.9488 | 61.9386 | 61.8086 | 61.6149 | 61.6002 | 61.6332 | 61.5366 | 61.8856 | 62.024 | 61.3764 | 61.7243 | -0.27069 | 0.2385 | -0.25245 | 0.25674
200.7031 | 123.7198 | -61.908 | 61.7477 | 0.089802 | -0.049678 | 0.029208 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 61.6012 | 61.5819 | 61.6057 | 61.5137 | 61.8673 | 62.0011 | 61.349 | 61.706 | 61.9978 | 61.8583 | 61.9372 | 61.8646 | 61.9625 | 61.9569 | 61.8269 | 61.6241 | 61.6048 | 61.6286 | 61.5366 | 61.8902 | 62.024 | 61.3719 | 61.7289 | -0.26611 | 0.25224 | -0.26161 | 0.25674
202.4062 | 123.7564 | -61.8896 | 61.7294 | 0.094381 | -0.049678 | 0.033786 | -0.043331 | 0.063733 | 0.048956 | -0.071874 | 61.592 | 61.5773 | 61.6103 | 61.5228 | 61.8582 | 61.9965 | 61.3535 | 61.7014 | 61.984 | 61.84 | 61.9234 | 61.8463 | 61.9534 | 61.9386 | 61.8178 | 61.6149 | 61.6002 | 61.6332 | 61.5457 | 61.881 | 62.0194 | 61.3764 | 61.7243 | -0.26611 | 0.2385 | -0.24787 | 0.25674
204.1562 | 123.7244 | -61.9263 | 61.7523 | 0.089802 | -0.054257 | 0.029208 | -0.043331 | 0.059155 | 0.044377 | -0.076452 | 61.592 | 61.5865 | 61.6057 | 61.532 | 61.8536 | 61.9965 | 61.3535 | 61.6923 | 62.0161 | 61.872 | 61.9555 | 61.8829 | 61.9854 | 61.9706 | 61.8498 | 61.6149 | 61.6094 | 61.6286 | 61.5549 | 61.8765 | 62.0194 | 61.3764 | 61.7152 | -0.26153 | 0.2385 | -0.24787 | 0.25216
205.9062 | 123.8205 | -61.8942 | 61.702 | 0.080646 | -0.058836 | 0.024629 | -0.043331 | 0.06831 | 0.048956 | -0.08103 | 61.6012 | 61.5773 | 61.6057 | 61.5137 | 61.8673 | 61.9965 | 61.3535 | 61.7014 | 61.9749 | 61.8354 | 61.9189 | 61.8509 | 61.9625 | 61.9432 | 61.8132 | 61.6241 | 61.6002 | 61.6286 | 61.5366 | 61.8902 | 62.0194 | 61.3764 | 61.7243 | -0.26611 | 0.24766 | -0.26161 | 0.25216
207.5938 | 123.7473 | -61.9034 | 61.7477 | 0.085224 | -0.049678 | 0.033786 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 61.592 | 61.5727 | 61.6011 | 61.5182 | 61.8627 | 61.9919 | 61.3444 | 61.7014 | 61.9886 | 61.8537 | 61.9372 | 61.8555 | 61.9625 | 61.9523 | 61.8269 | 61.6149 | 61.5956 | 61.624 | 61.5411 | 61.8856 | 62.0148 | 61.3673 | 61.7243 | -0.27069 | 0.24766 | -0.26161 | 0.25674
209.3281 | 123.7381 | -61.8851 | 61.7661 | 0.094381 | -0.058836 | 0.033786 | -0.038752 | 0.063733 | 0.048956 | -0.085608 | 61.5875 | 61.5773 | 61.6057 | 61.5137 | 61.8673 | 61.9965 | 61.349 | 61.6923 | 61.9795 | 61.8262 | 61.9189 | 61.8463 | 61.9488 | 61.934 | 61.7995 | 61.6104 | 61.6002 | 61.6286 | 61.5366 | 61.8902 | 62.0194 | 61.3719 | 61.7152 | -0.27985 | 0.2385 | -0.26161 | 0.25674
211.0156 | 123.8434 | -61.8668 | 61.6837 | 0.089802 | -0.063415 | 0.029208 | -0.038752 | 0.059155 | 0.039799 | -0.08103 | 61.5829 | 61.5727 | 61.5965 | 61.5182 | 61.8582 | 61.9873 | 61.3535 | 61.6877 | 61.9566 | 61.8033 | 61.896 | 61.828 | 61.9259 | 61.9066 | 61.7857 | 61.6058 | 61.5956 | 61.6194 | 61.5411 | 61.881 | 62.0102 | 61.3764 | 61.7106 | -0.27527 | 0.22934 | -0.26161 | 0.243
212.7656 | 123.7152 | -61.9217 | 61.7157 | 0.094381 | -0.049678 | 0.033786 | -0.047909 | 0.06831 | 0.044377 | -0.071874 | 61.592 | 61.5727 | 61.6103 | 61.5228 | 61.8582 | 61.9919 | 61.349 | 61.6923 | 62.0161 | 61.872 | 61.9555 | 61.8738 | 61.99 | 61.9661 | 61.8498 | 61.6149 | 61.5956 | 61.6332 | 61.5457 | 61.881 | 62.0148 | 61.3719 | 61.7152 | -0.26611 | 0.24308 | -0.24787 | 0.26132
214.5156 | 123.8342 | -61.908 | 61.6745 | 0.085224 | -0.054257 | 0.033786 | -0.047909 | 0.054577 | 0.044377 | -0.08103 | 61.5829 | 61.5773 | 61.6011 | 61.5137 | 61.8627 | 61.9965 | 61.3535 | 61.6923 | 61.9932 | 61.8537 | 61.9417 | 61.8601 | 61.9625 | 61.9523 | 61.8269 | 61.6058 | 61.6002 | 61.624 | 61.5366 | 61.8856 | 62.0194 | 61.3764 | 61.7152 | -0.27985 | 0.22934 | -0.26161 | 0.24758
216.25 | 123.7976 | -61.9308 | 61.6425 | 0.085224 | -0.049678 | 0.029208 | -0.043331 | 0.063733 | 0.048956 | -0.076452 | 61.5875 | 61.5727 | 61.592 | 61.5182 | 61.8582 | 61.9873 | 61.3444 | 61.6831 | 62.0161 | 61.8812 | 61.9601 | 61.8875 | 61.9946 | 61.9798 | 61.8544 | 61.6104 | 61.5956 | 61.6149 | 61.5411 | 61.881 | 62.0102 | 61.3673 | 61.706 | -0.27069 | 0.24308 | -0.26619 | 0.24758
218 | 123.8251 | -61.8942 | 61.6379 | 0.098959 | -0.067994 | 0.024629 | -0.047909 | 0.054577 | 0.044377 | -0.071874 | 61.5875 | 61.5682 | 61.5965 | 61.5182 | 61.8536 | 61.9873 | 61.3444 | 61.6831 | 61.9932 | 61.8262 | 61.9189 | 61.8463 | 61.9488 | 61.9386 | 61.8224 | 61.6104 | 61.591 | 61.6194 | 61.5411 | 61.8765 | 62.0102 | 61.3673 | 61.706 | -0.26611 | 0.24308 | -0.25703 | 0.25216
219.6875 | 123.7152 | -61.8896 | 61.734 | 0.089802 | -0.054257 | 0.024629 | -0.038752 | 0.059155 | 0.048956 | -0.076452 | 61.5783 | 61.5727 | 61.592 | 61.5137 | 61.8444 | 61.9873 | 61.3444 | 61.6923 | 61.9794 | 61.8354 | 61.9143 | 61.8509 | 61.9488 | 61.9386 | 61.8132 | 61.6012 | 61.5956 | 61.6149 | 61.5366 | 61.8673 | 62.0102 | 61.3673 | 61.7152 | -0.26611 | 0.23392 | -0.25245 | 0.24758
221.4375 | 123.7015 | -61.8851 | 61.734 | 0.094381 | -0.058836 | 0.029208 | -0.043331 | 0.06831 | 0.048956 | -0.076452 | 61.5829 | 61.5727 | 61.5965 | 61.5091 | 61.849 | 61.9873 | 61.3444 | 61.6923 | 61.9795 | 61.8262 | 61.9143 | 61.8417 | 61.9534 | 61.934 | 61.8086 | 61.6058 | 61.5956 | 61.6194 | 61.532 | 61.8719 | 62.0102 | 61.3673 | 61.7152 | -0.26611 | 0.2385 | -0.25245 | 0.25216
223.125 | 123.7381 | -61.9125 | 61.6653 | 0.085224 | -0.054257 | 0.024629 | -0.047909 | 0.06831 | 0.035221 | -0.071874 | 61.5829 | 61.5727 | 61.592 | 61.5182 | 61.8444 | 61.9873 | 61.3398 | 61.674 | 61.9978 | 61.8583 | 61.9372 | 61.8646 | 61.9808 | 61.9478 | 61.8407 | 61.6058 | 61.5956 | 61.6149 | 61.5411 | 61.8673 | 62.0102 | 61.3627 | 61.6969 | -0.26153 | 0.24308 | -0.25245 | 0.25216
224.8906 | 123.7747 | -61.9125 | 61.6516 | 0.094381 | -0.058836 | 0.024629 | -0.043331 | 0.06831 | 0.044377 | -0.076452 | 61.5783 | 61.5682 | 61.5874 | 61.5137 | 61.8444 | 61.9782 | 61.3398 | 61.6831 | 62.0069 | 61.8537 | 61.9372 | 61.8692 | 61.9808 | 61.9569 | 61.8361 | 61.6012 | 61.591 | 61.6103 | 61.5366 | 61.8673 | 62.0011 | 61.3627 | 61.706 | -0.26611 | 0.2385 | -0.25703 | 0.24758
226.5625 | 123.7381 | -61.8576 | 61.734 | 0.094381 | -0.054257 | 0.033786 | -0.047909 | 0.063733 | 0.039799 | -0.076452 | 61.5875 | 61.5682 | 61.592 | 61.5182 | 61.8444 | 61.9828 | 61.3444 | 61.674 | 61.952 | 61.8033 | 61.8914 | 61.8097 | 61.9213 | 61.8974 | 61.7812 | 61.6104 | 61.591 | 61.6149 | 61.5411 | 61.8673 | 62.0057 | 61.3673 | 61.6969 | -0.25695 | 0.24308 | -0.25245 | 0.24758
228.2969 | 123.7473 | -61.9034 | 61.7065 | 0.094381 | -0.054257 | 0.029208 | -0.043331 | 0.063733 | 0.048956 | -0.08103 | 61.5783 | 61.5682 | 61.5828 | 61.5137 | 61.8444 | 61.9828 | 61.3306 | 61.6786 | 61.9978 | 61.8491 | 61.9326 | 61.8601 | 61.9671 | 61.9523 | 61.8224 | 61.6012 | 61.591 | 61.6057 | 61.5366 | 61.8673 | 62.0057 | 61.3535 | 61.7014 | -0.26611 | 0.24766 | -0.26161 | 0.25216
230 | 123.7564 | -61.8759 | 61.7157 | 0.094381 | -0.058836 | 0.020051 | -0.038752 | 0.063733 | 0.053534 | -0.071874 | 61.5691 | 61.5636 | 61.592 | 61.4954 | 61.8444 | 61.9736 | 61.3444 | 61.6786 | 61.9703 | 61.8171 | 61.896 | 61.8372 | 61.9396 | 61.9294 | 61.804 | 61.592 | 61.5865 | 61.6149 | 61.5182 | 61.8673 | 61.9965 | 61.3673 | 61.7014 | -0.27527 | 0.22477 | -0.25245 | 0.24758
231.75 | 123.8205 | -61.8668 | 61.6425 | 0.089802 | -0.054257 | 0.024629 | -0.047909 | 0.063733 | 0.039799 | -0.085608 | 61.5783 | 61.5544 | 61.5874 | 61.5091 | 61.8444 | 61.9736 | 61.3444 | 61.6786 | 61.9566 | 61.8125 | 61.8914 | 61.8189 | 61.9305 | 61.9066 | 61.7812 | 61.6012 | 61.5773 | 61.6103 | 61.532 | 61.8673 | 61.9965 | 61.3673 | 61.7014 | -0.26611 | 0.23392 | -0.25703 | 0.24301
233.4375 | 123.761 | -61.8942 | 61.6562 | 0.085224 | -0.058836 | 0.029208 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 61.5783 | 61.559 | 61.5782 | 61.5137 | 61.8444 | 61.9782 | 61.3352 | 61.674 | 61.9794 | 61.8354 | 61.9234 | 61.8463 | 61.9534 | 61.9432 | 61.8178 | 61.6012 | 61.5819 | 61.6011 | 61.5366 | 61.8673 | 62.0011 | 61.3581 | 61.6969 | -0.26611 | 0.24308 | -0.26619 | 0.24301
235.1094 | 123.7335 | -61.8622 | 61.7477 | 0.085224 | -0.063415 | 0.029208 | -0.038752 | 0.059155 | 0.044377 | -0.071874 | 61.5783 | 61.5636 | 61.5782 | 61.5091 | 61.8444 | 61.9782 | 61.3352 | 61.6786 | 61.9474 | 61.7988 | 61.8914 | 61.8234 | 61.9213 | 61.9066 | 61.7903 | 61.6012 | 61.5865 | 61.6011 | 61.532 | 61.8673 | 62.0011 | 61.3581 | 61.7014 | -0.26611 | 0.24308 | -0.26619 | 0.24301
236.8594 | 123.6923 | -61.8668 | 61.7203 | 0.089802 | -0.058836 | 0.033786 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 61.5783 | 61.5636 | 61.5782 | 61.5091 | 61.8353 | 61.9782 | 61.3352 | 61.6694 | 61.9566 | 61.8079 | 61.9005 | 61.8189 | 61.9305 | 61.9157 | 61.7949 | 61.6012 | 61.5865 | 61.6011 | 61.532 | 61.8581 | 62.0011 | 61.3581 | 61.6923 | -0.25696 | 0.24308 | -0.25703 | 0.24301
238.5625 | 123.793 | -61.8484 | 61.6241 | 0.080646 | -0.063415 | 0.024629 | -0.052488 | 0.063733 | 0.053534 | -0.076452 | 61.5737 | 61.5636 | 61.5782 | 61.5045 | 61.8307 | 61.9782 | 61.3306 | 61.674 | 61.9291 | 61.785 | 61.8731 | 61.796 | 61.9122 | 61.902 | 61.772 | 61.5966 | 61.5865 | 61.6011 | 61.5274 | 61.8536 | 62.0011 | 61.3535 | 61.6969 | -0.25695 | 0.24308 | -0.25245 | 0.24758
240.25 | 123.8297 | -61.8851 | 61.6333 | 0.094381 | -0.063415 | 0.033786 | -0.057066 | 0.063733 | 0.058113 | -0.08103 | 61.5646 | 61.5544 | 61.5874 | 61.5045 | 61.8353 | 61.9782 | 61.3306 | 61.674 | 61.9795 | 61.8217 | 61.9189 | 61.828 | 61.9488 | 61.9432 | 61.804 | 61.5875 | 61.5773 | 61.6103 | 61.5274 | 61.8581 | 62.0011 | 61.3535 | 61.6969 | -0.27069 | 0.23392 | -0.24787 | 0.25674
242.0156 | 123.7427 | -61.8988 | 61.6196 | 0.089802 | -0.063415 | 0.033786 | -0.043331 | 0.059155 | 0.044377 | -0.076452 | 61.5691 | 61.5636 | 61.5737 | 61.5045 | 61.8353 | 61.969 | 61.3306 | 61.6786 | 61.9886 | 61.8354 | 61.9326 | 61.8555 | 61.958 | 61.9432 | 61.8224 | 61.592 | 61.5865 | 61.5965 | 61.5274 | 61.8581 | 61.9919 | 61.3535 | 61.7014 | -0.26611 | 0.2385 | -0.26161 | 0.24301
243.7656 | 123.761 | -61.8988 | 61.647 | 0.085224 | -0.058836 | 0.038365 | -0.052488 | 0.06831 | 0.039799 | -0.085608 | 61.5783 | 61.559 | 61.5737 | 61.5091 | 61.8307 | 61.9736 | 61.3352 | 61.6694 | 61.984 | 61.84 | 61.9372 | 61.8463 | 61.9671 | 61.9386 | 61.8132 | 61.6012 | 61.5819 | 61.5965 | 61.532 | 61.8536 | 61.9965 | 61.3581 | 61.6923 | -0.25238 | 0.24308 | -0.25703 | 0.23843
245.4531 | 123.6649 | -61.8851 | 61.7065 | 0.089802 | -0.058836 | 0.029208 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 61.5691 | 61.559 | 61.5782 | 61.4954 | 61.8261 | 61.9736 | 61.3261 | 61.6602 | 61.9749 | 61.8262 | 61.9143 | 61.8372 | 61.9488 | 61.934 | 61.8132 | 61.592 | 61.5819 | 61.6011 | 61.5182 | 61.849 | 61.9965 | 61.349 | 61.6831 | -0.25696 | 0.24308 | -0.24787 | 0.25216
247.1406 | 123.7473 | -61.8851 | 61.6104 | 0.085224 | -0.058836 | 0.038365 | -0.047909 | 0.059155 | 0.053534 | -0.076452 | 61.5783 | 61.5544 | 61.5737 | 61.5091 | 61.8307 | 61.9736 | 61.3261 | 61.674 | 61.9703 | 61.8262 | 61.9234 | 61.8372 | 61.9442 | 61.9386 | 61.8086 | 61.6012 | 61.5773 | 61.5965 | 61.532 | 61.8536 | 61.9965 | 61.349 | 61.6969 | -0.25238 | 0.25224 | -0.25703 | 0.24758
248.8906 | 123.793 | -61.8851 | 61.6333 | 0.089802 | -0.063415 | 0.029208 | -0.047909 | 0.054577 | 0.044377 | -0.076452 | 61.5737 | 61.5498 | 61.5645 | 61.4954 | 61.8261 | 61.969 | 61.3306 | 61.6694 | 61.9749 | 61.8217 | 61.9143 | 61.8372 | 61.9396 | 61.9294 | 61.8086 | 61.5966 | 61.5727 | 61.5874 | 61.5182 | 61.849 | 61.9919 | 61.3535 | 61.6923 | -0.25238 | 0.24308 | -0.26161 | 0.23385
250.6406 | 123.642 | -61.8713 | 61.702 | 0.089802 | -0.058836 | 0.033786 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 61.5691 | 61.5544 | 61.5691 | 61.4816 | 61.8215 | 61.9645 | 61.3169 | 61.6648 | 61.9611 | 61.8125 | 61.9051 | 61.8234 | 61.9351 | 61.9203 | 61.7995 | 61.592 | 61.5773 | 61.592 | 61.5045 | 61.8444 | 61.9873 | 61.3398 | 61.6877 | -0.25238 | 0.25224 | -0.25245 | 0.25216
252.3125 | 123.6969 | -61.8851 | 61.6837 | 0.089802 | -0.058836 | 0.029208 | -0.047909 | 0.059155 | 0.048956 | -0.085608 | 61.56 | 61.5498 | 61.5691 | 61.4954 | 61.8307 | 61.9645 | 61.3215 | 61.6648 | 61.9749 | 61.8262 | 61.9143 | 61.8372 | 61.9442 | 61.934 | 61.7995 | 61.5829 | 61.5727 | 61.592 | 61.5182 | 61.8536 | 61.9873 | 61.3444 | 61.6877 | -0.27069 | 0.2385 | -0.26161 | 0.24759
254 | 123.7793 | -61.8622 | 61.6562 | 0.094381 | -0.058836 | 0.024629 | -0.052488 | 0.063733 | 0.044377 | -0.076452 | 61.5737 | 61.5544 | 61.5737 | 61.4999 | 61.8215 | 61.9645 | 61.3215 | 61.6602 | 61.9566 | 61.8033 | 61.8868 | 61.8097 | 61.9259 | 61.9066 | 61.7857 | 61.5966 | 61.5773 | 61.5965 | 61.5228 | 61.8444 | 61.9873 | 61.3444 | 61.6831 | -0.2478 | 0.25224 | -0.24787 | 0.25216
255.75 | 123.7061 | -61.8622 | 61.6928 | 0.089802 | -0.058836 | 0.029208 | -0.038752 | 0.063733 | 0.048956 | -0.076452 | 61.5646 | 61.5544 | 61.5645 | 61.4999 | 61.8215 | 61.969 | 61.3078 | 61.6557 | 61.952 | 61.8033 | 61.8914 | 61.8234 | 61.9259 | 61.9111 | 61.7857 | 61.5875 | 61.5773 | 61.5874 | 61.5228 | 61.8444 | 61.9919 | 61.3306 | 61.6786 | -0.25696 | 0.25682 | -0.25703 | 0.25674
257.4375 | 123.6511 | -61.8851 | 61.7065 | 0.089802 | -0.058836 | 0.024629 | -0.038752 | 0.059155 | 0.044377 | -0.08103 | 61.5646 | 61.5498 | 61.5691 | 61.4954 | 61.8169 | 61.9599 | 61.3169 | 61.6465 | 61.9749 | 61.8262 | 61.9097 | 61.8463 | 61.9442 | 61.9294 | 61.804 | 61.5875 | 61.5727 | 61.592 | 61.5182 | 61.8398 | 61.9828 | 61.3398 | 61.6694 | -0.25238 | 0.24766 | -0.24787 | 0.25216
259.1094 | 123.761 | -61.8622 | 61.6379 | 0.094381 | -0.063415 | 0.033786 | -0.047909 | 0.063733 | 0.039799 | -0.071874 | 61.5646 | 61.5453 | 61.5645 | 61.4999 | 61.8215 | 61.9599 | 61.3535 | 61.6648 | 61.9566 | 61.7988 | 61.896 | 61.8143 | 61.9259 | 61.902 | 61.7903 | 61.5875 | 61.5681 | 61.5874 | 61.5228 | 61.8444 | 61.9828 | 61.3764 | 61.6877 | -0.25696 | 0.21103 | -0.25703 | 0.21096
260.8438 | 123.7473 | -61.8484 | 61.6333 | 0.094381 | -0.054257 | 0.029208 | -0.052488 | 0.059155 | 0.048956 | -0.076452 | 61.56 | 61.5498 | 61.5599 | 61.4954 | 61.8169 | 61.9599 | 61.3398 | 61.6557 | 61.9428 | 61.7942 | 61.8777 | 61.796 | 61.9076 | 61.8974 | 61.772 | 61.5829 | 61.5727 | 61.5828 | 61.5182 | 61.8398 | 61.9828 | 61.3627 | 61.6786 | -0.25696 | 0.22019 | -0.25703 | 0.22011
262.5938 | 123.6603 | -61.8805 | 61.702 | 0.10354 | -0.049678 | 0.033786 | -0.038752 | 0.063733 | 0.053534 | -0.071874 | 61.5646 | 61.5407 | 61.5645 | 61.4954 | 61.8261 | 61.9599 | 61.381 | 61.6511 | 61.984 | 61.8308 | 61.9143 | 61.8417 | 61.9442 | 61.934 | 61.8086 | 61.5875 | 61.5636 | 61.5874 | 61.5182 | 61.849 | 61.9828 | 61.4039 | 61.674 | -0.26153 | 0.18356 | -0.26161 | 0.18349
264.2812 | 123.761 | -61.8393 | 61.6425 | 0.094381 | -0.067994 | 0.024629 | -0.038752 | 0.054577 | 0.053534 | -0.076452 | 61.56 | 61.5407 | 61.5645 | 61.4908 | 61.8169 | 61.9645 | 61.3673 | 61.6557 | 61.9337 | 61.7713 | 61.8639 | 61.8005 | 61.8939 | 61.8928 | 61.7628 | 61.5829 | 61.5636 | 61.5874 | 61.5137 | 61.8398 | 61.9873 | 61.3902 | 61.6786 | -0.25696 | 0.19272 | -0.25245 | 0.19722
265.9688 | 123.6145 | -61.8484 | 61.6928 | 0.085224 | -0.063415 | 0.033786 | -0.043331 | 0.06831 | 0.048956 | -0.071874 | 61.5646 | 61.5453 | 61.5691 | 61.4999 | 61.8215 | 61.9553 | 61.3352 | 61.6511 | 61.9337 | 61.785 | 61.8822 | 61.8051 | 61.9168 | 61.8974 | 61.7766 | 61.5875 | 61.5681 | 61.592 | 61.5228 | 61.8444 | 61.9782 | 61.3581 | 61.674 | -0.25696 | 0.22935 | -0.25245 | 0.23385
267.7188 | 123.642 | -61.8576 | 61.7111 | 0.089802 | -0.063415 | 0.029208 | -0.038752 | 0.06831 | 0.053534 | -0.08103 | 61.5691 | 61.5453 | 61.5553 | 61.4954 | 61.8124 | 61.9553 | 61.3902 | 61.6557 | 61.9474 | 61.7942 | 61.8868 | 61.8189 | 61.9259 | 61.9111 | 61.7766 | 61.592 | 61.5681 | 61.5782 | 61.5182 | 61.8353 | 61.9782 | 61.4131 | 61.6786 | -0.24322 | 0.17898 | -0.25703 | 0.16517
269.4062 | 123.7427 | -61.8439 | 61.6287 | 0.089802 | -0.063415 | 0.029208 | -0.043331 | 0.063733 | 0.048956 | -0.085608 | 61.5646 | 61.5453 | 61.5691 | 61.4862 | 61.8124 | 61.9507 | 61.3627 | 61.6511 | 61.9337 | 61.7805 | 61.8731 | 61.8005 | 61.9076 | 61.8928 | 61.7583 | 61.5875 | 61.5681 | 61.592 | 61.5091 | 61.8353 | 61.9736 | 61.3856 | 61.674 | -0.2478 | 0.20187 | -0.24329 | 0.20638
271.0938 | 123.7518 | -61.8668 | 61.6653 | 0.085224 | -0.058836 | 0.029208 | -0.047909 | 0.063733 | 0.053534 | -0.076452 | 61.5646 | 61.5453 | 61.5553 | 61.4862 | 61.8169 | 61.9461 | 61.4176 | 61.6557 | 61.952 | 61.8079 | 61.896 | 61.8189 | 61.9305 | 61.9203 | 61.7903 | 61.5875 | 61.5681 | 61.5782 | 61.5091 | 61.8398 | 61.969 | 61.4405 | 61.6786 | -0.25238 | 0.14693 | -0.26161 | 0.1377
272.8594 | 123.7381 | -61.8439 | 61.6653 | 0.094381 | -0.063415 | 0.029208 | -0.043331 | 0.049999 | 0.044377 | -0.076452 | 61.5554 | 61.5315 | 61.5599 | 61.4908 | 61.8169 | 61.9553 | 61.4131 | 61.6557 | 61.9383 | 61.7805 | 61.8731 | 61.8005 | 61.8939 | 61.8882 | 61.7674 | 61.5783 | 61.5544 | 61.5828 | 61.5137 | 61.8398 | 61.9782 | 61.4359 | 61.6786 | -0.26154 | 0.14236 | -0.25703 | 0.14686
274.625 | 123.6877 | -61.8759 | 61.6516 | 0.089802 | -0.063415 | 0.033786 | -0.047909 | 0.059155 | 0.048956 | -0.08103 | 61.5554 | 61.5361 | 61.5599 | 61.4862 | 61.8078 | 61.9416 | 61.4176 | 61.6465 | 61.9657 | 61.8125 | 61.9097 | 61.828 | 61.9351 | 61.9249 | 61.7949 | 61.5783 | 61.559 | 61.5828 | 61.5091 | 61.8307 | 61.9644 | 61.4405 | 61.6694 | -0.25238 | 0.13778 | -0.24787 | 0.14228
276.3125 | 123.6969 | -61.8759 | 61.6379 | 0.089802 | -0.063415 | 0.024629 | -0.047909 | 0.059155 | 0.039799 | -0.076452 | 61.5554 | 61.5315 | 61.5553 | 61.4816 | 61.8169 | 61.9507 | 61.4405 | 61.6511 | 61.9657 | 61.8125 | 61.9005 | 61.828 | 61.9351 | 61.9157 | 61.7995 | 61.5783 | 61.5544 | 61.5782 | 61.5045 | 61.8398 | 61.9736 | 61.4634 | 61.674 | -0.26154 | 0.11489 | -0.26161 | 0.11481
278.0781 | 123.6145 | -61.8484 | 61.702 | 0.080646 | -0.058836 | 0.024629 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 61.5508 | 61.5407 | 61.5553 | 61.4862 | 61.8078 | 61.9507 | 61.468 | 61.6511 | 61.9291 | 61.7896 | 61.8731 | 61.8051 | 61.903 | 61.8974 | 61.7674 | 61.5737 | 61.5636 | 61.5782 | 61.5091 | 61.8307 | 61.9736 | 61.4909 | 61.674 | -0.25696 | 0.082835 | -0.25245 | 0.087341
279.8281 | 123.6923 | -61.8759 | 61.6379 | 0.094381 | -0.058836 | 0.029208 | -0.047909 | 0.059155 | 0.048956 | -0.071874 | 61.5554 | 61.5407 | 61.5599 | 61.4862 | 61.8032 | 61.9416 | 61.4314 | 61.6419 | 61.9703 | 61.8171 | 61.9051 | 61.828 | 61.9351 | 61.9249 | 61.804 | 61.5783 | 61.5636 | 61.5828 | 61.5091 | 61.8261 | 61.9644 | 61.4543 | 61.6648 | -0.2478 | 0.12404 | -0.24329 | 0.12855
281.5156 | 123.6145 | -61.8439 | 61.7249 | 0.080646 | -0.067994 | 0.029208 | -0.043331 | 0.059155 | 0.044377 | -0.076452 | 61.5554 | 61.5315 | 61.5508 | 61.4816 | 61.8124 | 61.9553 | 61.4634 | 61.6465 | 61.9245 | 61.7759 | 61.8731 | 61.8005 | 61.903 | 61.8882 | 61.7674 | 61.5783 | 61.5544 | 61.5737 | 61.5045 | 61.8353 | 61.9782 | 61.4863 | 61.6694 | -0.25696 | 0.091993 | -0.26161 | 0.087342
283.2656 | 123.7473 | -61.8347 | 61.6241 | 0.085224 | -0.063415 | 0.029208 | -0.047909 | 0.063733 | 0.053534 | -0.076452 | 61.5463 | 61.5315 | 61.5508 | 61.477 | 61.8078 | 61.9416 | 61.468 | 61.6374 | 61.9199 | 61.7713 | 61.8639 | 61.7868 | 61.8984 | 61.8883 | 61.7583 | 61.5691 | 61.5544 | 61.5737 | 61.4999 | 61.8307 | 61.9644 | 61.4909 | 61.6602 | -0.26154 | 0.078257 | -0.25703 | 0.082763
285 | 123.6374 | -61.8118 | 61.7065 | 0.089802 | -0.063415 | 0.029208 | -0.052488 | 0.059155 | 0.048956 | -0.076452 | 61.5554 | 61.5407 | 61.5553 | 61.4816 | 61.8169 | 61.9461 | 61.468 | 61.6511 | 61.9016 | 61.7484 | 61.841 | 61.7593 | 61.871 | 61.8608 | 61.7354 | 61.5783 | 61.5636 | 61.5782 | 61.5045 | 61.8398 | 61.969 | 61.4909 | 61.674 | -0.26154 | 0.087414 | -0.26161 | 0.087341
286.6719 | 123.5916 | -61.853 | 61.702 | 0.094381 | -0.067994 | 0.029208 | -0.047909 | 0.063733 | 0.048956 | -0.076452 | 61.5554 | 61.5361 | 61.5553 | 61.4816 | 61.8032 | 61.9461 | 61.468 | 61.6282 | 61.9474 | 61.785 | 61.8822 | 61.8051 | 61.9168 | 61.902 | 61.7766 | 61.5783 | 61.559 | 61.5782 | 61.5045 | 61.8261 | 61.969 | 61.4909 | 61.6511 | -0.2478 | 0.087414 | -0.24787 | 0.087341
288.4219 | 123.7106 | -61.8301 | 61.647 | 0.085224 | -0.063415 | 0.033786 | -0.038752 | 0.063733 | 0.039799 | -0.076452 | 61.5508 | 61.5269 | 61.5508 | 61.4816 | 61.8078 | 61.9416 | 61.468 | 61.6419 | 61.9154 | 61.7667 | 61.8639 | 61.7914 | 61.8939 | 61.8699 | 61.7537 | 61.5737 | 61.5498 | 61.5737 | 61.5045 | 61.8307 | 61.9644 | 61.4909 | 61.6648 | -0.25696 | 0.082835 | -0.25703 | 0.082763
290.1094 | 123.6603 | -61.8713 | 61.6241 | 0.089802 | -0.058836 | 0.033786 | -0.047909 | 0.063733 | 0.048956 | -0.076452 | 61.5554 | 61.5224 | 61.5508 | 61.477 | 61.8032 | 61.937 | 61.4634 | 61.6374 | 61.9611 | 61.8125 | 61.9051 | 61.8234 | 61.9351 | 61.9203 | 61.7949 | 61.5783 | 61.5453 | 61.5737 | 61.4999 | 61.8261 | 61.9599 | 61.4863 | 61.6602 | -0.2478 | 0.091993 | -0.25245 | 0.087342
291.8438 | 123.6053 | -61.8439 | 61.6791 | 0.080646 | -0.063415 | 0.029208 | -0.043331 | 0.059155 | 0.048956 | -0.071874 | 61.5508 | 61.5315 | 61.5462 | 61.4816 | 61.7986 | 61.9416 | 61.4634 | 61.6419 | 61.9245 | 61.7805 | 61.8731 | 61.8005 | 61.903 | 61.8928 | 61.772 | 61.5737 | 61.5544 | 61.5691 | 61.5045 | 61.8215 | 61.9644 | 61.4863 | 61.6648 | -0.2478 | 0.087414 | -0.25245 | 0.082763
293.5938 | 123.6649 | -61.821 | 61.6791 | 0.094381 | -0.063415 | 0.029208 | -0.043331 | 0.06831 | 0.053534 | -0.076452 | 61.5554 | 61.5315 | 61.5508 | 61.4816 | 61.8032 | 61.9416 | 61.4634 | 61.6465 | 61.9154 | 61.7576 | 61.8502 | 61.7777 | 61.8893 | 61.8745 | 61.7445 | 61.5783 | 61.5544 | 61.5737 | 61.5045 | 61.8261 | 61.9644 | 61.4863 | 61.6694 | -0.2478 | 0.091993 | -0.25245 | 0.087342
295.3281 | 123.642 | -61.8347 | 61.6699 | 0.085224 | -0.063415 | 0.029208 | -0.047909 | 0.06831 | 0.053534 | -0.071874 | 61.5417 | 61.5224 | 61.5462 | 61.4725 | 61.7986 | 61.9324 | 61.4726 | 61.6419 | 61.9199 | 61.7713 | 61.8639 | 61.7868 | 61.903 | 61.8883 | 61.7628 | 61.5646 | 61.5453 | 61.5691 | 61.4953 | 61.8215 | 61.9553 | 61.4955 | 61.6648 | -0.25696 | 0.0691 | -0.25245 | 0.073606
297.0938 | 123.7656 | -61.8393 | 61.6013 | 0.094381 | -0.058836 | 0.029208 | -0.052488 | 0.059155 | 0.048956 | -0.076452 | 61.5417 | 61.5224 | 61.537 | 61.4816 | 61.8032 | 61.9324 | 61.4588 | 61.6465 | 61.9337 | 61.7805 | 61.8685 | 61.7868 | 61.8984 | 61.8882 | 61.7628 | 61.5646 | 61.5453 | 61.5599 | 61.5045 | 61.8261 | 61.9553 | 61.4817 | 61.6694 | -0.26154 | 0.082835 | -0.26619 | 0.078185
298.8438 | 123.6786 | -61.8301 | 61.6196 | 0.089802 | -0.072572 | 0.024629 | -0.047909 | 0.063733 | 0.058113 | -0.08103 | 61.5417 | 61.5224 | 61.5462 | 61.477 | 61.7941 | 61.937 | 61.4634 | 61.6328 | 61.9199 | 61.7576 | 61.8548 | 61.7822 | 61.8939 | 61.8883 | 61.7491 | 61.5646 | 61.5453 | 61.5691 | 61.4999 | 61.8169 | 61.9599 | 61.4863 | 61.6557 | -0.25238 | 0.078257 | -0.24787 | 0.082763
300.5312 | 123.7152 | -61.8393 | 61.5921 | 0.089802 | -0.067994 | 0.029208 | -0.047909 | 0.063733 | 0.048956 | -0.076452 | 61.5508 | 61.5224 | 61.5462 | 61.477 | 61.7941 | 61.9324 | 61.4543 | 61.6282 | 61.9291 | 61.7713 | 61.8685 | 61.7914 | 61.903 | 61.8882 | 61.7628 | 61.5737 | 61.5453 | 61.5691 | 61.4999 | 61.8169 | 61.9553 | 61.4772 | 61.6511 | -0.24322 | 0.096571 | -0.24787 | 0.09192
302.2656 | 123.6603 | -61.8484 | 61.6013 | 0.089802 | -0.072572 | 0.024629 | -0.043331 | 0.063733 | 0.058113 | -0.076452 | 61.5417 | 61.5178 | 61.5416 | 61.4679 | 61.8078 | 61.9278 | 61.4634 | 61.6328 | 61.9383 | 61.7759 | 61.8731 | 61.8051 | 61.9122 | 61.9066 | 61.772 | 61.5646 | 61.5407 | 61.5645 | 61.4908 | 61.8307 | 61.9507 | 61.4863 | 61.6557 | -0.26611 | 0.078257 | -0.26619 | 0.078185
304.0156 | 123.7198 | -61.8027 | 61.6013 | 0.089802 | -0.063415 | 0.024629 | -0.047909 | 0.054577 | 0.044377 | -0.085608 | 61.5463 | 61.5224 | 61.5416 | 61.4725 | 61.7986 | 61.9324 | 61.4588 | 61.6328 | 61.8925 | 61.7393 | 61.8273 | 61.7548 | 61.8573 | 61.847 | 61.7171 | 61.5691 | 61.5453 | 61.5645 | 61.4953 | 61.8215 | 61.9553 | 61.4817 | 61.6557 | -0.25238 | 0.087414 | -0.25703 | 0.082763
305.6875 | 123.6191 | -61.8256 | 61.6928 | 0.089802 | -0.063415 | 0.033786 | -0.043331 | 0.059155 | 0.048956 | -0.076452 | 61.5371 | 61.5269 | 61.5462 | 61.4725 | 61.7849 | 61.9324 | 61.4588 | 61.6236 | 61.9154 | 61.7621 | 61.8593 | 61.7822 | 61.8847 | 61.8745 | 61.7491 | 61.56 | 61.5498 | 61.5691 | 61.4953 | 61.8078 | 61.9553 | 61.4817 | 61.6465 | -0.2478 | 0.078257 | -0.23872 | 0.087341
307.4375 | 123.6053 | -61.8622 | 61.6791 | 0.089802 | -0.063415 | 0.033786 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 61.5417 | 61.5178 | 61.5416 | 61.4679 | 61.7895 | 61.9324 | 61.4588 | 61.6236 | 61.952 | 61.7988 | 61.896 | 61.8143 | 61.9213 | 61.9111 | 61.7857 | 61.5646 | 61.5407 | 61.5645 | 61.4908 | 61.8124 | 61.9553 | 61.4817 | 61.6465 | -0.2478 | 0.082835 | -0.24787 | 0.082763
309.1875 | 123.6465 | -61.821 | 61.6745 | 0.094381 | -0.063415 | 0.042944 | -0.043331 | 0.06831 | 0.048956 | -0.076452 | 61.5463 | 61.5269 | 61.5416 | 61.477 | 61.7895 | 61.9232 | 61.4543 | 61.6282 | 61.9154 | 61.7576 | 61.8639 | 61.7777 | 61.8893 | 61.8699 | 61.7445 | 61.5691 | 61.5498 | 61.5645 | 61.4999 | 61.8124 | 61.9461 | 61.4772 | 61.6511 | -0.24322 | 0.091993 | -0.24787 | 0.087342
310.8594 | 123.6923 | -61.8301 | 61.6196 | 0.085224 | -0.058836 | 0.033786 | -0.043331 | 0.06831 | 0.048956 | -0.067295 | 61.5371 | 61.5178 | 61.537 | 61.4679 | 61.7849 | 61.9232 | 61.4634 | 61.6145 | 61.9154 | 61.7713 | 61.8639 | 61.7868 | 61.8984 | 61.8791 | 61.7628 | 61.56 | 61.5407 | 61.5599 | 61.4908 | 61.8078 | 61.9461 | 61.4863 | 61.6374 | -0.2478 | 0.073679 | -0.24787 | 0.073607
312.6094 | 123.7061 | -61.8256 | 61.6196 | 0.089802 | -0.058836 | 0.024629 | -0.047909 | 0.059155 | 0.044377 | -0.071874 | 61.5371 | 61.5178 | 61.5416 | 61.4679 | 61.7849 | 61.9324 | 61.4543 | 61.6145 | 61.9154 | 61.7667 | 61.8502 | 61.7777 | 61.8847 | 61.8699 | 61.7537 | 61.56 | 61.5407 | 61.5645 | 61.4908 | 61.8078 | 61.9553 | 61.4772 | 61.6374 | -0.2478 | 0.082836 | -0.2433 | 0.087342
314.3594 | 123.7381 | -61.8347 | 61.6333 | 0.085224 | -0.063415 | 0.029208 | -0.047909 | 0.063733 | 0.044377 | -0.076452 | 61.5417 | 61.5178 | 61.5324 | 61.4679 | 61.7895 | 61.9324 | 61.4588 | 61.6236 | 61.9199 | 61.7713 | 61.8639 | 61.7868 | 61.8984 | 61.8791 | 61.7583 | 61.5646 | 61.5407 | 61.5553 | 61.4908 | 61.8124 | 61.9553 | 61.4817 | 61.6465 | -0.2478 | 0.082835 | -0.25703 | 0.073606
316.0625 | 123.6694 | -61.8347 | 61.6241 | 0.089802 | -0.058836 | 0.029208 | -0.043331 | 0.054577 | 0.058113 | -0.076452 | 61.5325 | 61.5269 | 61.5324 | 61.4725 | 61.7941 | 61.9278 | 61.4451 | 61.619 | 61.9245 | 61.7759 | 61.8639 | 61.7914 | 61.8893 | 61.8928 | 61.7583 | 61.5554 | 61.5498 | 61.5553 | 61.4953 | 61.8169 | 61.9507 | 61.468 | 61.6419 | -0.26154 | 0.087413 | -0.26161 | 0.087341
317.8125 | 123.6603 | -61.8118 | 61.615 | 0.094381 | -0.058836 | 0.024629 | -0.047909 | 0.059155 | 0.058113 | -0.08103 | 61.5371 | 61.5086 | 61.5324 | 61.4587 | 61.7803 | 61.9278 | 61.4451 | 61.619 | 61.9062 | 61.753 | 61.8365 | 61.7639 | 61.871 | 61.8699 | 61.7308 | 61.56 | 61.5315 | 61.5553 | 61.4816 | 61.8032 | 61.9507 | 61.468 | 61.6419 | -0.24322 | 0.091992 | -0.24787 | 0.087341
319.5625 | 123.6923 | -61.8164 | 61.6241 | 0.094381 | -0.063415 | 0.033786 | -0.038752 | 0.054577 | 0.048956 | -0.08103 | 61.5371 | 61.5178 | 61.5324 | 61.4679 | 61.7895 | 61.9232 | 61.4543 | 61.6236 | 61.9108 | 61.753 | 61.8502 | 61.7777 | 61.871 | 61.8654 | 61.7354 | 61.56 | 61.5407 | 61.5553 | 61.4908 | 61.8124 | 61.9461 | 61.4772 | 61.6465 | -0.25238 | 0.082836 | -0.25703 | 0.078185
321.25 | 123.555 | -61.8256 | 61.6974 | 0.085224 | -0.054257 | 0.024629 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 61.5417 | 61.5086 | 61.5279 | 61.4587 | 61.7895 | 61.9232 | 61.4543 | 61.619 | 61.9108 | 61.7713 | 61.8502 | 61.7777 | 61.8801 | 61.8745 | 61.7491 | 61.5646 | 61.5315 | 61.5508 | 61.4816 | 61.8124 | 61.9461 | 61.4772 | 61.6419 | -0.2478 | 0.087414 | -0.26161 | 0.073607
323 | 123.6969 | -61.8073 | 61.5875 | 0.080646 | -0.058836 | 0.033786 | -0.043331 | 0.06831 | 0.048956 | -0.076452 | 61.5371 | 61.5178 | 61.5324 | 61.4633 | 61.7803 | 61.9278 | 61.4451 | 61.619 | 61.8879 | 61.7484 | 61.841 | 61.7639 | 61.8756 | 61.8562 | 61.7308 | 61.56 | 61.5407 | 61.5553 | 61.4862 | 61.8032 | 61.9507 | 61.468 | 61.6419 | -0.24322 | 0.091992 | -0.24787 | 0.087341
324.6875 | 123.5458 | -61.8347 | 61.6745 | 0.085224 | -0.054257 | 0.033786 | -0.047909 | 0.063733 | 0.053534 | -0.071874 | 61.5371 | 61.5178 | 61.5324 | 61.4725 | 61.7803 | 61.9278 | 61.4497 | 61.6099 | 61.9199 | 61.7805 | 61.8685 | 61.7868 | 61.8984 | 61.8883 | 61.7628 | 61.56 | 61.5407 | 61.5553 | 61.4953 | 61.8032 | 61.9507 | 61.4726 | 61.6328 | -0.24322 | 0.087414 | -0.24787 | 0.082763
326.4375 | 123.6099 | -61.8027 | 61.6928 | 0.085224 | -0.063415 | 0.029208 | -0.038752 | 0.054577 | 0.053534 | -0.071874 | 61.5463 | 61.5132 | 61.5279 | 61.4587 | 61.7803 | 61.9187 | 61.4451 | 61.6145 | 61.8879 | 61.7393 | 61.8319 | 61.7639 | 61.8573 | 61.8562 | 61.7308 | 61.5691 | 61.5361 | 61.5508 | 61.4816 | 61.8032 | 61.9416 | 61.468 | 61.6374 | -0.23407 | 0.10115 | -0.25245 | 0.082763
328.1875 | 123.6969 | -61.8073 | 61.6241 | 0.085224 | -0.063415 | 0.038365 | -0.047909 | 0.06831 | 0.058113 | -0.08103 | 61.5417 | 61.5086 | 61.5324 | 61.4541 | 61.7895 | 61.9187 | 61.4497 | 61.619 | 61.8925 | 61.7438 | 61.8456 | 61.7593 | 61.8756 | 61.8654 | 61.7262 | 61.5646 | 61.5315 | 61.5553 | 61.477 | 61.8124 | 61.9416 | 61.4726 | 61.6419 | -0.2478 | 0.091992 | -0.25703 | 0.082763
329.875 | 123.6969 | -61.8118 | 61.615 | 0.094381 | -0.054257 | 0.033786 | -0.043331 | 0.063733 | 0.053534 | -0.08103 | 61.5371 | 61.5132 | 61.5279 | 61.4587 | 61.7712 | 61.9095 | 61.436 | 61.6053 | 61.9062 | 61.7576 | 61.8456 | 61.7685 | 61.8756 | 61.8654 | 61.7308 | 61.56 | 61.5361 | 61.5508 | 61.4816 | 61.7941 | 61.9324 | 61.4588 | 61.6282 | -0.23407 | 0.10115 | -0.2433 | 0.09192
331.625 | 123.6832 | -61.8027 | 61.6287 | 0.089802 | -0.054257 | 0.033786 | -0.047909 | 0.059155 | 0.058113 | -0.08103 | 61.5325 | 61.5132 | 61.5279 | 61.4541 | 61.7757 | 61.9187 | 61.4497 | 61.6053 | 61.8925 | 61.7484 | 61.8365 | 61.7548 | 61.8618 | 61.8608 | 61.7216 | 61.5554 | 61.5361 | 61.5508 | 61.477 | 61.7986 | 61.9416 | 61.4726 | 61.6282 | -0.24322 | 0.082835 | -0.24787 | 0.078185
333.375 | 123.6694 | -61.8027 | 61.5875 | 0.089802 | -0.054257 | 0.033786 | -0.047909 | 0.06831 | 0.048956 | -0.076452 | 61.5188 | 61.4995 | 61.5187 | 61.4587 | 61.7712 | 61.9141 | 61.436 | 61.6007 | 61.8925 | 61.7484 | 61.8365 | 61.7548 | 61.871 | 61.8516 | 61.7262 | 61.5417 | 61.5224 | 61.5416 | 61.4816 | 61.7941 | 61.937 | 61.4588 | 61.6236 | -0.25238 | 0.082835 | -0.25245 | 0.082764
335.0781 | 123.5367 | -61.8393 | 61.6653 | 0.089802 | -0.054257 | 0.033786 | -0.043331 | 0.063733 | 0.044377 | -0.071874 | 61.5279 | 61.5086 | 61.5279 | 61.4496 | 61.7757 | 61.9095 | 61.436 | 61.6007 | 61.9291 | 61.785 | 61.8731 | 61.796 | 61.903 | 61.8837 | 61.7674 | 61.5508 | 61.5315 | 61.5508 | 61.4724 | 61.7986 | 61.9324 | 61.4588 | 61.6236 | -0.2478 | 0.091992 | -0.24787 | 0.09192
336.8125 | 123.6008 | -61.7935 | 61.6974 | 0.062332 | -0.0451 | 0.024629 | -0.043331 | 0.06831 | 0.044377 | -0.08103 | 61.5371 | 61.5086 | 61.5233 | 61.4541 | 61.7803 | 61.9141 | 61.4405 | 61.5961 | 61.8558 | 61.7484 | 61.8181 | 61.7502 | 61.8618 | 61.8379 | 61.7125 | 61.56 | 61.5315 | 61.5462 | 61.477 | 61.8032 | 61.937 | 61.4634 | 61.619 | -0.24322 | 0.096571 | -0.25703 | 0.082764
338.5781 | 123.6374 | -61.8027 | 61.5967 | 0.062332 | -0.054257 | 0.029208 | -0.043331 | 0.059155 | 0.053534 | -0.067295 | 61.5234 | 61.504 | 61.5233 | 61.4496 | 61.7757 | 61.9095 | 61.436 | 61.6053 | 61.865 | 61.7484 | 61.8319 | 61.7593 | 61.8618 | 61.8562 | 61.7354 | 61.5463 | 61.5269 | 61.5462 | 61.4724 | 61.7986 | 61.9324 | 61.4588 | 61.6282 | -0.25238 | 0.087413 | -0.25245 | 0.087342
340.2656 | 123.6649 | -61.8118 | 61.5784 | 0.062332 | -0.063415 | 0.029208 | -0.052488 | 0.059155 | 0.053534 | -0.08103 | 61.5325 | 61.504 | 61.5279 | 61.4541 | 61.7712 | 61.9095 | 61.4405 | 61.6053 | 61.8742 | 61.7484 | 61.841 | 61.7593 | 61.871 | 61.8654 | 61.7308 | 61.5554 | 61.5269 | 61.5508 | 61.477 | 61.7941 | 61.9324 | 61.4634 | 61.6282 | -0.23865 | 0.091992 | -0.2433 | 0.087342
342.0156 | 123.5779 | -61.8027 | 61.6699 | 0.06691 | -0.054257 | 0.033786 | -0.047909 | 0.06831 | 0.053534 | -0.067295 | 61.5279 | 61.504 | 61.5233 | 61.4587 | 61.7666 | 61.9004 | 61.436 | 61.6007 | 61.8696 | 61.7484 | 61.8365 | 61.7548 | 61.871 | 61.8562 | 61.7354 | 61.5508 | 61.5269 | 61.5462 | 61.4816 | 61.7895 | 61.9232 | 61.4588 | 61.6236 | -0.23865 | 0.091992 | -0.2433 | 0.087342
343.7656 | 123.6649 | -61.8073 | 61.5875 | 0.06691 | -0.058836 | 0.024629 | -0.043331 | 0.059155 | 0.053534 | -0.071874 | 61.5234 | 61.4995 | 61.5187 | 61.4496 | 61.7712 | 61.9095 | 61.436 | 61.6053 | 61.8742 | 61.7484 | 61.8319 | 61.7639 | 61.8664 | 61.8608 | 61.7354 | 61.5463 | 61.5224 | 61.5416 | 61.4724 | 61.7941 | 61.9324 | 61.4588 | 61.6282 | -0.2478 | 0.087413 | -0.25245 | 0.082764
345.4531 | 123.5458 | -61.8118 | 61.6791 | 0.06691 | -0.054257 | 0.024629 | -0.043331 | 0.059155 | 0.048956 | -0.067295 | 61.5325 | 61.4995 | 61.5187 | 61.4541 | 61.7757 | 61.9095 | 61.436 | 61.6053 | 61.8787 | 61.7576 | 61.8365 | 61.7685 | 61.871 | 61.8608 | 61.7445 | 61.5554 | 61.5224 | 61.5416 | 61.477 | 61.7986 | 61.9324 | 61.4588 | 61.6282 | -0.24322 | 0.09657 | -0.25703 | 0.082764
347.2031 | 123.5779 | -61.7661 | 61.6562 | 0.071489 | -0.049678 | 0.029208 | -0.043331 | 0.063733 | 0.053534 | -0.076452 | 61.5325 | 61.4995 | 61.5187 | 61.4496 | 61.7666 | 61.9095 | 61.4314 | 61.5916 | 61.8375 | 61.7164 | 61.7953 | 61.7227 | 61.8298 | 61.8196 | 61.6896 | 61.5554 | 61.5224 | 61.5416 | 61.4724 | 61.7895 | 61.9324 | 61.4543 | 61.6145 | -0.23407 | 0.10115 | -0.24787 | 0.087342
348.9062 | 123.5092 | -61.8073 | 61.6562 | 0.071489 | -0.054257 | 0.038365 | -0.043331 | 0.06831 | 0.058113 | -0.076452 | 61.5325 | 61.4995 | 61.5141 | 61.445 | 61.762 | 61.8958 | 61.4314 | 61.5961 | 61.8787 | 61.753 | 61.8456 | 61.7639 | 61.8756 | 61.8654 | 61.7308 | 61.5554 | 61.5224 | 61.537 | 61.4679 | 61.7849 | 61.9187 | 61.4543 | 61.619 | -0.22949 | 0.10115 | -0.24788 | 0.082763
350.6562 | 123.5275 | -61.7889 | 61.6608 | 0.071489 | -0.049678 | 0.033786 | -0.043331 | 0.063733 | 0.058113 | -0.076452 | 61.5279 | 61.4903 | 61.5187 | 61.445 | 61.7666 | 61.8958 | 61.436 | 61.5916 | 61.8604 | 61.7393 | 61.8227 | 61.7456 | 61.8527 | 61.8471 | 61.7125 | 61.5508 | 61.5132 | 61.5416 | 61.4679 | 61.7895 | 61.9187 | 61.4588 | 61.6145 | -0.23865 | 0.091992 | -0.24787 | 0.082764
352.4062 | 123.5184 | -61.8027 | 61.6562 | 0.062332 | -0.040521 | 0.024629 | -0.043331 | 0.063733 | 0.053534 | -0.071874 | 61.5234 | 61.4995 | 61.5233 | 61.4496 | 61.7712 | 61.8958 | 61.4222 | 61.5916 | 61.865 | 61.7622 | 61.8273 | 61.7593 | 61.8664 | 61.8562 | 61.7308 | 61.5463 | 61.5224 | 61.5462 | 61.4724 | 61.7941 | 61.9187 | 61.4451 | 61.6145 | -0.2478 | 0.10115 | -0.24787 | 0.10108
354.1094 | 123.555 | -61.7844 | 61.6241 | 0.06691 | -0.035942 | 0.029208 | -0.043331 | 0.059155 | 0.048956 | -0.067295 | 61.5234 | 61.4903 | 61.5187 | 61.4404 | 61.762 | 61.9004 | 61.4222 | 61.587 | 61.8513 | 61.7484 | 61.8136 | 61.741 | 61.8435 | 61.8333 | 61.7171 | 61.5463 | 61.5132 | 61.5416 | 61.4633 | 61.7849 | 61.9232 | 61.4451 | 61.6099 | -0.23865 | 0.10115 | -0.2433 | 0.096499
355.875 | 123.6465 | -61.7752 | 61.5784 | 0.06691 | -0.017627 | 0.033786 | -0.047909 | 0.063733 | 0.058113 | -0.076452 | 61.5234 | 61.4995 | 61.5141 | 61.4404 | 61.7574 | 61.8958 | 61.4268 | 61.5916 | 61.8421 | 61.7576 | 61.809 | 61.7273 | 61.8389 | 61.8333 | 61.6988 | 61.5463 | 61.5224 | 61.537 | 61.4633 | 61.7803 | 61.9187 | 61.4497 | 61.6145 | -0.23407 | 0.09657 | -0.2433 | 0.087342
357.6406 | 123.5458 | -61.7889 | 61.647 | 0.062332 | -0.013048 | 0.029208 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 61.5188 | 61.4949 | 61.5141 | 61.4541 | 61.762 | 61.8912 | 61.4268 | 61.5961 | 61.8513 | 61.7759 | 61.8181 | 61.7456 | 61.8481 | 61.8425 | 61.7125 | 61.5417 | 61.5178 | 61.537 | 61.477 | 61.7849 | 61.9141 | 61.4497 | 61.619 | -0.24323 | 0.091992 | -0.24788 | 0.087342
359.3906 | 123.5962 | -61.8301 | 61.5646 | 0.06691 | -0.022205 | 0.029208 | -0.047909 | 0.063733 | 0.048956 | -0.076452 | 61.5234 | 61.4903 | 61.5141 | 61.4312 | 61.7574 | 61.8912 | 61.4222 | 61.5961 | 61.897 | 61.8079 | 61.8593 | 61.7822 | 61.8939 | 61.8791 | 61.7537 | 61.5463 | 61.5132 | 61.537 | 61.4541 | 61.7803 | 61.9141 | 61.4451 | 61.619 | -0.23407 | 0.10115 | -0.2433 | 0.09192
361.0781 | 123.5184 | -61.7889 | 61.6196 | 0.06691 | -0.017627 | 0.029208 | -0.038752 | 0.072888 | 0.053534 | -0.08103 | 61.5234 | 61.4949 | 61.5096 | 61.445 | 61.7574 | 61.9004 | 61.4268 | 61.5916 | 61.8558 | 61.7713 | 61.8181 | 61.7502 | 61.8618 | 61.8425 | 61.7079 | 61.5463 | 61.5178 | 61.5324 | 61.4679 | 61.7803 | 61.9232 | 61.4497 | 61.6145 | -0.23407 | 0.09657 | -0.24788 | 0.082764
362.8438 | 123.5321 | -61.7844 | 61.6333 | 0.06691 | -0.013048 | 0.029208 | -0.043331 | 0.06831 | 0.058113 | -0.071874 | 61.5142 | 61.4903 | 61.5141 | 61.445 | 61.762 | 61.9004 | 61.4222 | 61.587 | 61.8513 | 61.7713 | 61.8136 | 61.741 | 61.8527 | 61.8425 | 61.7125 | 61.5371 | 61.5132 | 61.537 | 61.4679 | 61.7849 | 61.9232 | 61.4451 | 61.6099 | -0.2478 | 0.091991 | -0.24788 | 0.09192
364.5938 | 123.5825 | -61.7935 | 61.6425 | 0.062332 | -0.013048 | 0.033786 | -0.043331 | 0.063733 | 0.053534 | -0.076452 | 61.5234 | 61.4903 | 61.505 | 61.4358 | 61.7574 | 61.8866 | 61.4314 | 61.587 | 61.8558 | 61.7805 | 61.8273 | 61.7502 | 61.8573 | 61.8471 | 61.7171 | 61.5463 | 61.5132 | 61.5279 | 61.4587 | 61.7803 | 61.9095 | 61.4543 | 61.6099 | -0.23407 | 0.091991 | -0.25245 | 0.073607
366.2656 | 123.5184 | -61.8027 | 61.6425 | 0.071489 | -0.026784 | 0.038365 | -0.052488 | 0.059155 | 0.062691 | -0.08103 | 61.5234 | 61.4857 | 61.505 | 61.445 | 61.7529 | 61.8912 | 61.4176 | 61.5824 | 61.8742 | 61.7759 | 61.841 | 61.7502 | 61.8618 | 61.8654 | 61.7216 | 61.5463 | 61.5086 | 61.5279 | 61.4679 | 61.7757 | 61.9141 | 61.4405 | 61.6053 | -0.22949 | 0.10573 | -0.24787 | 0.087343
368.0156 | 123.5504 | -61.7706 | 61.6837 | 0.06691 | -0.022205 | 0.033786 | -0.047909 | 0.063733 | 0.053534 | -0.071874 | 61.5188 | 61.4903 | 61.505 | 61.4404 | 61.7574 | 61.8866 | 61.4268 | 61.587 | 61.8375 | 61.7484 | 61.8044 | 61.7227 | 61.8344 | 61.8242 | 61.6988 | 61.5417 | 61.5132 | 61.5279 | 61.4633 | 61.7803 | 61.9095 | 61.4497 | 61.6099 | -0.23865 | 0.091992 | -0.25245 | 0.078186
369.7031 | 123.6237 | -61.7844 | 61.6058 | 0.06691 | -0.017627 | 0.029208 | -0.047909 | 0.063733 | 0.058113 | -0.08103 | 61.5188 | 61.4857 | 61.505 | 61.4267 | 61.7574 | 61.8866 | 61.4176 | 61.587 | 61.8513 | 61.7667 | 61.8136 | 61.7365 | 61.8481 | 61.8425 | 61.7033 | 61.5417 | 61.5086 | 61.5279 | 61.4496 | 61.7803 | 61.9095 | 61.4405 | 61.6099 | -0.23865 | 0.10115 | -0.25245 | 0.087343
371.4531 | 123.5687 | -61.7889 | 61.6333 | 0.06691 | -0.017627 | 0.029208 | -0.052488 | 0.063733 | 0.048956 | -0.076452 | 61.5188 | 61.4812 | 61.5004 | 61.4312 | 61.7574 | 61.8958 | 61.4176 | 61.5824 | 61.8558 | 61.7713 | 61.8181 | 61.7365 | 61.8527 | 61.8379 | 61.7125 | 61.5417 | 61.504 | 61.5233 | 61.4541 | 61.7803 | 61.9187 | 61.4405 | 61.6053 | -0.23865 | 0.10115 | -0.25703 | 0.082764
373.1562 | 123.5413 | -61.7569 | 61.647 | 0.062332 | -0.017627 | 0.029208 | -0.052488 | 0.059155 | 0.053534 | -0.067295 | 61.5096 | 61.4857 | 61.5004 | 61.4358 | 61.7529 | 61.8912 | 61.4176 | 61.5778 | 61.8192 | 61.7393 | 61.7861 | 61.7044 | 61.8161 | 61.8104 | 61.6896 | 61.5325 | 61.5086 | 61.5233 | 61.4587 | 61.7757 | 61.9141 | 61.4405 | 61.6007 | -0.24323 | 0.091992 | -0.25245 | 0.082764
374.9062 | 123.5413 | -61.7889 | 61.6333 | 0.06691 | -0.017627 | 0.029208 | -0.052488 | 0.063733 | 0.058113 | -0.076452 | 61.5188 | 61.4857 | 61.505 | 61.4312 | 61.7574 | 61.8866 | 61.4176 | 61.5824 | 61.8558 | 61.7713 | 61.8181 | 61.7365 | 61.8527 | 61.8471 | 61.7125 | 61.5417 | 61.5086 | 61.5279 | 61.4541 | 61.7803 | 61.9095 | 61.4405 | 61.6053 | -0.23865 | 0.10115 | -0.25245 | 0.087343
376.5938 | 123.5321 | -61.7798 | 61.6241 | 0.06691 | -0.017627 | 0.029208 | -0.052488 | 0.06831 | 0.058113 | -0.071874 | 61.5188 | 61.4857 | 61.505 | 61.4312 | 61.7529 | 61.8958 | 61.4085 | 61.5778 | 61.8467 | 61.7622 | 61.809 | 61.7273 | 61.8481 | 61.8379 | 61.7079 | 61.5417 | 61.5086 | 61.5279 | 61.4541 | 61.7757 | 61.9187 | 61.4314 | 61.6007 | -0.23407 | 0.1103 | -0.24787 | 0.096499
378.3438 | 123.5458 | -61.7523 | 61.6425 | 0.06691 | -0.022205 | 0.033786 | -0.052488 | 0.063733 | 0.062691 | -0.076452 | 61.5234 | 61.4857 | 61.4958 | 61.4312 | 61.7483 | 61.882 | 61.4176 | 61.5733 | 61.8192 | 61.7301 | 61.7861 | 61.6998 | 61.8161 | 61.815 | 61.6759 | 61.5463 | 61.5086 | 61.5187 | 61.4541 | 61.7712 | 61.9049 | 61.4405 | 61.5961 | -0.22491 | 0.10573 | -0.25245 | 0.078186
380.0938 | 123.5229 | -61.7752 | 61.6516 | 0.062332 | -0.022205 | 0.038365 | -0.052488 | 0.063733 | 0.053534 | -0.076452 | 61.505 | 61.4903 | 61.5004 | 61.4267 | 61.7483 | 61.882 | 61.4131 | 61.5778 | 61.8375 | 61.753 | 61.8136 | 61.7227 | 61.8389 | 61.8287 | 61.6988 | 61.5279 | 61.5132 | 61.5233 | 61.4496 | 61.7712 | 61.9049 | 61.4359 | 61.6007 | -0.24323 | 0.091991 | -0.24788 | 0.087342
381.8438 | 123.6053 | -61.8027 | 61.5921 | 0.062332 | -0.013048 | 0.029208 | -0.052488 | 0.059155 | 0.048956 | -0.071874 | 61.5096 | 61.4766 | 61.5004 | 61.4267 | 61.7437 | 61.8729 | 61.4131 | 61.5733 | 61.865 | 61.7896 | 61.8319 | 61.7502 | 61.8618 | 61.8516 | 61.7308 | 61.5325 | 61.4995 | 61.5233 | 61.4496 | 61.7666 | 61.8958 | 61.4359 | 61.5961 | -0.23407 | 0.09657 | -0.2433 | 0.087342
383.5156 | 123.4909 | -61.7615 | 61.6425 | 0.06691 | -0.017627 | 0.029208 | -0.043331 | 0.063733 | 0.044377 | -0.076452 | 61.5142 | 61.4812 | 61.5004 | 61.4221 | 61.7529 | 61.8775 | 61.4131 | 61.5778 | 61.8284 | 61.7438 | 61.7907 | 61.7181 | 61.8252 | 61.8059 | 61.685 | 61.5371 | 61.504 | 61.5233 | 61.445 | 61.7757 | 61.9004 | 61.4359 | 61.6007 | -0.23865 | 0.10115 | -0.25245 | 0.087342
385.2656 | 123.4909 | -61.7752 | 61.6653 | 0.057754 | -0.026784 | 0.033786 | -0.038752 | 0.06831 | 0.053534 | -0.08103 | 61.5142 | 61.4766 | 61.4958 | 61.4221 | 61.7437 | 61.8775 | 61.4176 | 61.5778 | 61.833 | 61.7484 | 61.809 | 61.7365 | 61.8435 | 61.8287 | 61.6942 | 61.5371 | 61.4995 | 61.5187 | 61.445 | 61.7666 | 61.9004 | 61.4405 | 61.6007 | -0.22949 | 0.09657 | -0.24788 | 0.078186
387 | 123.5046 | -61.7889 | 61.615 | 0.071489 | -0.022205 | 0.033786 | -0.043331 | 0.063733 | 0.053534 | -0.076452 | 61.5142 | 61.4766 | 61.4958 | 61.4312 | 61.7437 | 61.8775 | 61.4176 | 61.5687 | 61.8604 | 61.7667 | 61.8227 | 61.7456 | 61.8527 | 61.8425 | 61.7125 | 61.5371 | 61.4995 | 61.5187 | 61.4541 | 61.7666 | 61.9004 | 61.4405 | 61.5916 | -0.22949 | 0.09657 | -0.24788 | 0.078186
388.6719 | 123.5458 | -61.7523 | 61.647 | 0.06691 | -0.013048 | 0.024629 | -0.047909 | 0.06831 | 0.058113 | -0.071874 | 61.505 | 61.4812 | 61.5004 | 61.4267 | 61.7437 | 61.8683 | 61.4085 | 61.5687 | 61.8192 | 61.7393 | 61.7769 | 61.7044 | 61.8206 | 61.8104 | 61.6804 | 61.5279 | 61.504 | 61.5233 | 61.4496 | 61.7666 | 61.8912 | 61.4314 | 61.5916 | -0.23865 | 0.096569 | -0.2433 | 0.09192
390.4219 | 123.6191 | -61.7798 | 61.5646 | 0.06691 | -0.013048 | 0.024629 | -0.047909 | 0.063733 | 0.053534 | -0.071874 | 61.5096 | 61.4766 | 61.4912 | 61.4129 | 61.7391 | 61.8683 | 61.4039 | 61.5733 | 61.8467 | 61.7667 | 61.8044 | 61.7319 | 61.8435 | 61.8333 | 61.7079 | 61.5325 | 61.4995 | 61.5141 | 61.4358 | 61.762 | 61.8912 | 61.4268 | 61.5961 | -0.22949 | 0.10573 | -0.24788 | 0.087343
392.1094 | 123.5046 | -61.8118 | 61.5967 | 0.062332 | -0.017627 | 0.024629 | -0.043331 | 0.059155 | 0.053534 | -0.071874 | 61.505 | 61.4812 | 61.4867 | 61.4175 | 61.7437 | 61.8729 | 61.4039 | 61.5687 | 61.8742 | 61.7942 | 61.8365 | 61.7685 | 61.871 | 61.8654 | 61.74 | 61.5279 | 61.504 | 61.5096 | 61.4404 | 61.7666 | 61.8958 | 61.4268 | 61.5916 | -0.23865 | 0.10115 | -0.25703 | 0.082765
393.8594 | 123.5916 | -61.7935 | 61.5738 | 0.057754 | -0.022205 | 0.015472 | -0.034174 | 0.059155 | 0.048956 | -0.076452 | 61.505 | 61.472 | 61.4958 | 61.4267 | 61.7391 | 61.8683 | 61.4039 | 61.5687 | 61.8513 | 61.7713 | 61.809 | 61.7593 | 61.8527 | 61.8425 | 61.7171 | 61.5279 | 61.4949 | 61.5187 | 61.4496 | 61.762 | 61.8912 | 61.4268 | 61.5916 | -0.23407 | 0.10115 | -0.2433 | 0.091921
395.5469 | 123.4726 | -61.7661 | 61.647 | 0.06691 | -0.013048 | 0.020051 | -0.043331 | 0.059155 | 0.058113 | -0.076452 | 61.505 | 61.472 | 61.4912 | 61.4221 | 61.7345 | 61.8683 | 61.3993 | 61.5595 | 61.833 | 61.753 | 61.7861 | 61.7227 | 61.8252 | 61.8242 | 61.6896 | 61.5279 | 61.4949 | 61.5141 | 61.445 | 61.7574 | 61.8912 | 61.4222 | 61.5824 | -0.22949 | 0.10573 | -0.2433 | 0.091921
397.2969 | 123.555 | -61.7798 | 61.5967 | 0.062332 | -0.017627 | 0.020051 | -0.043331 | 0.063733 | 0.053534 | -0.076452 | 61.5005 | 61.472 | 61.4867 | 61.4083 | 61.7391 | 61.8683 | 61.4085 | 61.5641 | 61.8421 | 61.7622 | 61.7998 | 61.7365 | 61.8435 | 61.8333 | 61.7033 | 61.5234 | 61.4949 | 61.5096 | 61.4312 | 61.762 | 61.8912 | 61.4314 | 61.587 | -0.23865 | 0.091991 | -0.25245 | 0.078186
399.0469 | 123.4726 | -61.7477 | 61.647 | 0.062332 | -0.013048 | 0.015472 | -0.043331 | 0.063733 | 0.062691 | -0.076452 | 61.505 | 61.472 | 61.4912 | 61.4221 | 61.7391 | 61.8729 | 61.3993 | 61.5641 | 61.8101 | 61.7347 | 61.7632 | 61.7044 | 61.8115 | 61.8104 | 61.6713 | 61.5279 | 61.4949 | 61.5141 | 61.445 | 61.762 | 61.8958 | 61.4222 | 61.587 | -0.23407 | 0.10573 | -0.24788 | 0.091921
400.7969 | 123.468 | -61.7798 | 61.6013 | 0.071489 | -0.017627 | 0.020051 | -0.047909 | 0.063733 | 0.053534 | -0.076452 | 61.505 | 61.472 | 61.4867 | 61.4175 | 61.7345 | 61.8637 | 61.3902 | 61.5595 | 61.8513 | 61.7622 | 61.7998 | 61.7319 | 61.8435 | 61.8333 | 61.7033 | 61.5279 | 61.4949 | 61.5096 | 61.4404 | 61.7574 | 61.8866 | 61.4131 | 61.5824 | -0.22949 | 0.11488 | -0.24788 | 0.0965
402.4844 | 123.5962 | -61.7569 | 61.5875 | 0.06691 | -0.022205 | 0.020051 | -0.038752 | 0.059155 | 0.053534 | -0.067295 | 61.505 | 61.472 | 61.4821 | 61.4129 | 61.73 | 61.8683 | 61.4039 | 61.5687 | 61.8238 | 61.7347 | 61.7769 | 61.7181 | 61.8161 | 61.8104 | 61.6896 | 61.5279 | 61.4949 | 61.505 | 61.4358 | 61.7529 | 61.8912 | 61.4268 | 61.5916 | -0.22491 | 0.10115 | -0.24788 | 0.078186
404.2344 | 123.4772 | -61.7752 | 61.6241 | 0.062332 | -0.017627 | 0.015472 | -0.043331 | 0.063733 | 0.062691 | -0.076452 | 61.5005 | 61.4674 | 61.4912 | 61.4221 | 61.73 | 61.8729 | 61.3947 | 61.5458 | 61.8375 | 61.7576 | 61.7907 | 61.7319 | 61.8389 | 61.8379 | 61.6988 | 61.5234 | 61.4903 | 61.5141 | 61.445 | 61.7529 | 61.8958 | 61.4176 | 61.5687 | -0.22949 | 0.10573 | -0.23872 | 0.0965
405.9844 | 123.5596 | -61.7386 | 61.5601 | 0.06691 | -0.017627 | 0.020051 | -0.043331 | 0.06831 | 0.053534 | -0.08103 | 61.5005 | 61.4674 | 61.4821 | 61.4175 | 61.7208 | 61.8592 | 61.3947 | 61.5504 | 61.8055 | 61.721 | 61.7586 | 61.6953 | 61.8069 | 61.7921 | 61.6576 | 61.5234 | 61.4903 | 61.505 | 61.4404 | 61.7437 | 61.882 | 61.4176 | 61.5733 | -0.22033 | 0.10573 | -0.23872 | 0.087343
407.6719 | 123.5916 | -61.7615 | 61.5097 | 0.062332 | -0.026784 | 0.024629 | -0.043331 | 0.072888 | 0.053534 | -0.076452 | 61.4959 | 61.472 | 61.4867 | 61.4129 | 61.73 | 61.8637 | 61.3902 | 61.5549 | 61.8238 | 61.7347 | 61.7861 | 61.7181 | 61.8344 | 61.815 | 61.685 | 61.5188 | 61.4949 | 61.5096 | 61.4358 | 61.7529 | 61.8866 | 61.4131 | 61.5778 | -0.23407 | 0.10573 | -0.2433 | 0.0965
409.4219 | 123.5916 | -61.7569 | 61.5646 | 0.071489 | -0.017627 | 0.020051 | -0.043331 | 0.059155 | 0.058113 | -0.076452 | 61.505 | 61.4628 | 61.4867 | 61.4175 | 61.7208 | 61.8592 | 61.3947 | 61.5504 | 61.8284 | 61.7393 | 61.7769 | 61.7136 | 61.8161 | 61.815 | 61.6804 | 61.5279 | 61.4857 | 61.5096 | 61.4404 | 61.7437 | 61.882 | 61.4176 | 61.5733 | -0.21576 | 0.1103 | -0.23414 | 0.091922
411.1719 | 123.5184 | -61.734 | 61.6379 | 0.062332 | -0.013048 | 0.024629 | -0.047909 | 0.06831 | 0.053534 | -0.067295 | 61.505 | 61.4812 | 61.4912 | 61.4221 | 61.7254 | 61.8546 | 61.3856 | 61.5458 | 61.7963 | 61.721 | 61.7586 | 61.6861 | 61.8023 | 61.7875 | 61.6667 | 61.5279 | 61.504 | 61.5141 | 61.445 | 61.7483 | 61.8775 | 61.4085 | 61.5687 | -0.22034 | 0.11946 | -0.23414 | 0.10566
412.9062 | 123.468 | -61.7798 | 61.6058 | 0.06691 | -0.013048 | 0.024629 | -0.038752 | 0.063733 | 0.053534 | -0.071874 | 61.5096 | 61.472 | 61.4958 | 61.4221 | 61.7071 | 61.8454 | 61.3719 | 61.5458 | 61.8467 | 61.7667 | 61.8044 | 61.741 | 61.8435 | 61.8333 | 61.7079 | 61.5325 | 61.4949 | 61.5187 | 61.445 | 61.73 | 61.8683 | 61.3947 | 61.5687 | -0.19744 | 0.13778 | -0.21125 | 0.12397
414.5781 | 123.5458 | -61.7706 | 61.5738 | 0.06691 | -0.022205 | 0.020051 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 61.5096 | 61.4903 | 61.5004 | 61.4358 | 61.7071 | 61.85 | 61.3719 | 61.5366 | 61.8375 | 61.7484 | 61.7907 | 61.7227 | 61.8344 | 61.8196 | 61.6988 | 61.5325 | 61.5132 | 61.5233 | 61.4587 | 61.73 | 61.8729 | 61.3947 | 61.5595 | -0.19744 | 0.13778 | -0.20667 | 0.12855
416.3281 | 123.5916 | -61.7432 | 61.5555 | 0.062332 | -0.022205 | 0.020051 | -0.038752 | 0.063733 | 0.048956 | -0.076452 | 61.5142 | 61.472 | 61.4912 | 61.4221 | 61.7162 | 61.85 | 61.3764 | 61.5458 | 61.8055 | 61.721 | 61.7632 | 61.7044 | 61.8069 | 61.7921 | 61.6667 | 61.5371 | 61.4949 | 61.5141 | 61.445 | 61.7391 | 61.8729 | 61.3993 | 61.5687 | -0.20202 | 0.13777 | -0.22498 | 0.11481
418.0781 | 123.587 | -61.7615 | 61.5417 | 0.06691 | -0.031363 | 0.010893 | -0.047909 | 0.059155 | 0.053534 | -0.076452 | 61.5005 | 61.4674 | 61.4867 | 61.4083 | 61.7208 | 61.85 | 61.3856 | 61.5458 | 61.8284 | 61.7301 | 61.7724 | 61.7136 | 61.8206 | 61.815 | 61.685 | 61.5234 | 61.4903 | 61.5096 | 61.4312 | 61.7437 | 61.8729 | 61.4085 | 61.5687 | -0.22033 | 0.11488 | -0.23414 | 0.10108
419.8281 | 123.5779 | -61.7523 | 61.5326 | 0.062332 | -0.022205 | 0.024629 | -0.043331 | 0.059155 | 0.053534 | -0.067295 | 61.5005 | 61.472 | 61.4867 | 61.4129 | 61.7071 | 61.8454 | 61.3673 | 61.5366 | 61.8147 | 61.7301 | 61.7769 | 61.709 | 61.8115 | 61.8059 | 61.685 | 61.5234 | 61.4949 | 61.5096 | 61.4358 | 61.73 | 61.8683 | 61.3902 | 61.5595 | -0.2066 | 0.1332 | -0.22041 | 0.11939
421.5 | 123.5825 | -61.7523 | 61.5555 | 0.057754 | -0.031363 | 0.024629 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 61.5096 | 61.4812 | 61.4958 | 61.4267 | 61.7025 | 61.8271 | 61.3673 | 61.5275 | 61.8101 | 61.721 | 61.7769 | 61.7044 | 61.8069 | 61.8013 | 61.6759 | 61.5325 | 61.504 | 61.5187 | 61.4496 | 61.7254 | 61.85 | 61.3902 | 61.5504 | -0.19287 | 0.14235 | -0.20667 | 0.12855
423.25 | 123.4497 | -61.7477 | 61.6013 | 0.057754 | -0.022205 | 0.024629 | -0.047909 | 0.063733 | 0.053534 | -0.076452 | 61.4913 | 61.4628 | 61.4775 | 61.3992 | 61.7208 | 61.8454 | 61.3764 | 61.5412 | 61.8055 | 61.7255 | 61.7724 | 61.6998 | 61.8115 | 61.8013 | 61.6713 | 61.5142 | 61.4857 | 61.5004 | 61.4221 | 61.7437 | 61.8683 | 61.3993 | 61.5641 | -0.22949 | 0.11488 | -0.2433 | 0.10108
425.0156 | 123.436 | -61.734 | 61.6241 | 0.062332 | -0.022205 | 0.020051 | -0.047909 | 0.054577 | 0.044377 | -0.067295 | 61.4913 | 61.4628 | 61.4821 | 61.4038 | 61.7254 | 61.8454 | 61.3856 | 61.5458 | 61.7963 | 61.7118 | 61.7541 | 61.6861 | 61.7886 | 61.7784 | 61.6667 | 61.5142 | 61.4857 | 61.505 | 61.4267 | 61.7483 | 61.8683 | 61.4085 | 61.5687 | -0.23407 | 0.10573 | -0.2433 | 0.096499
426.7656 | 123.4497 | -61.7477 | 61.647 | 0.057754 | -0.026784 | 0.024629 | -0.038752 | 0.059155 | 0.053534 | -0.08103 | 61.4959 | 61.4628 | 61.4775 | 61.4038 | 61.7162 | 61.8592 | 61.3764 | 61.5458 | 61.8055 | 61.721 | 61.7724 | 61.709 | 61.8069 | 61.8013 | 61.6667 | 61.5188 | 61.4857 | 61.5004 | 61.4267 | 61.7391 | 61.882 | 61.3993 | 61.5687 | -0.22034 | 0.11946 | -0.23872 | 0.10108
428.4531 | 123.4909 | -61.734 | 61.6241 | 0.076067 | -0.026784 | 0.029208 | -0.047909 | 0.059155 | 0.062691 | -0.071874 | 61.4959 | 61.4583 | 61.4821 | 61.4083 | 61.7162 | 61.85 | 61.3764 | 61.5366 | 61.8101 | 61.7072 | 61.7632 | 61.6861 | 61.7932 | 61.7967 | 61.6621 | 61.5188 | 61.4811 | 61.505 | 61.4312 | 61.7391 | 61.8729 | 61.3993 | 61.5595 | -0.22034 | 0.11946 | -0.23414 | 0.10566
430.2188 | 123.4406 | -61.7752 | 61.6196 | 0.062332 | -0.026784 | 0.029208 | -0.043331 | 0.06831 | 0.048956 | -0.071874 | 61.4959 | 61.4628 | 61.4729 | 61.4083 | 61.7162 | 61.8546 | 61.3764 | 61.5458 | 61.8375 | 61.7484 | 61.8044 | 61.7319 | 61.8435 | 61.8242 | 61.7033 | 61.5188 | 61.4857 | 61.4958 | 61.4312 | 61.7391 | 61.8775 | 61.3993 | 61.5687 | -0.22034 | 0.11946 | -0.2433 | 0.0965
431.9531 | 123.5184 | -61.7661 | 61.5417 | 0.062332 | -0.026784 | 0.024629 | -0.047909 | 0.06831 | 0.048956 | -0.071874 | 61.4867 | 61.4628 | 61.4821 | 61.3946 | 61.7071 | 61.8408 | 61.3764 | 61.5412 | 61.8284 | 61.7393 | 61.7907 | 61.7181 | 61.8344 | 61.815 | 61.6942 | 61.5096 | 61.4857 | 61.505 | 61.4175 | 61.73 | 61.8637 | 61.3993 | 61.5641 | -0.22034 | 0.1103 | -0.22499 | 0.10566
433.625 | 123.436 | -61.734 | 61.6241 | 0.06691 | -0.026784 | 0.020051 | -0.043331 | 0.059155 | 0.058113 | -0.071874 | 61.4867 | 61.4628 | 61.4775 | 61.3992 | 61.7117 | 61.8454 | 61.3764 | 61.5458 | 61.8009 | 61.7072 | 61.7541 | 61.6907 | 61.7932 | 61.7921 | 61.6621 | 61.5096 | 61.4857 | 61.5004 | 61.4221 | 61.7345 | 61.8683 | 61.3993 | 61.5687 | -0.22492 | 0.1103 | -0.23414 | 0.10108
435.3594 | 123.468 | -61.7432 | 61.6379 | 0.06691 | -0.035942 | 0.024629 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 61.4867 | 61.4628 | 61.4867 | 61.4038 | 61.7071 | 61.8408 | 61.3764 | 61.5275 | 61.8101 | 61.7072 | 61.7678 | 61.6953 | 61.7977 | 61.7921 | 61.6667 | 61.5096 | 61.4857 | 61.5096 | 61.4267 | 61.73 | 61.8637 | 61.3993 | 61.5504 | -0.22034 | 0.1103 | -0.22041 | 0.11023
437.0938 | 123.4955 | -61.7157 | 61.6013 | 0.06691 | -0.026784 | 0.029208 | -0.043331 | 0.054577 | 0.053534 | -0.071874 | 61.4959 | 61.4674 | 61.4729 | 61.4038 | 61.7071 | 61.8363 | 61.3764 | 61.5366 | 61.7826 | 61.6889 | 61.7449 | 61.6724 | 61.7703 | 61.7692 | 61.6438 | 61.5188 | 61.4903 | 61.4958 | 61.4267 | 61.73 | 61.8592 | 61.3993 | 61.5595 | -0.21118 | 0.11946 | -0.23414 | 0.0965
438.8438 | 123.4085 | -61.734 | 61.6562 | 0.071489 | -0.022205 | 0.024629 | -0.043331 | 0.063733 | 0.058113 | -0.076452 | 61.5096 | 61.472 | 61.4912 | 61.4175 | 61.6888 | 61.8134 | 61.3444 | 61.5092 | 61.8055 | 61.7118 | 61.7586 | 61.6907 | 61.7977 | 61.7921 | 61.6576 | 61.5325 | 61.4949 | 61.5141 | 61.4404 | 61.7116 | 61.8363 | 61.3673 | 61.5321 | -0.17913 | 0.16525 | -0.19752 | 0.14686
440.5312 | 123.4131 | -61.734 | 61.6241 | 0.06691 | -0.022205 | 0.029208 | -0.043331 | 0.063733 | 0.053534 | -0.071874 | 61.5096 | 61.472 | 61.4912 | 61.4175 | 61.6842 | 61.8225 | 61.3444 | 61.5137 | 61.8009 | 61.7118 | 61.7632 | 61.6907 | 61.7977 | 61.7875 | 61.6621 | 61.5325 | 61.4949 | 61.5141 | 61.4404 | 61.7071 | 61.8454 | 61.3673 | 61.5366 | -0.17455 | 0.16525 | -0.19294 | 0.14686
442.2812 | 123.4131 | -61.702 | 61.6333 | 0.071489 | -0.026784 | 0.020051 | -0.043331 | 0.063733 | 0.048956 | -0.067295 | 61.505 | 61.4812 | 61.4958 | 61.4221 | 61.675 | 61.8134 | 61.3444 | 61.5092 | 61.7735 | 61.6752 | 61.722 | 61.6586 | 61.7657 | 61.7509 | 61.6347 | 61.5279 | 61.504 | 61.5187 | 61.445 | 61.6979 | 61.8363 | 61.3673 | 61.5321 | -0.16998 | 0.16067 | -0.1792 | 0.15144
444.0312 | 123.4085 | -61.7157 | 61.6425 | 0.06691 | -0.026784 | 0.029208 | -0.047909 | 0.063733 | 0.048956 | -0.067295 | 61.5142 | 61.4812 | 61.5004 | 61.4221 | 61.6659 | 61.8088 | 61.3398 | 61.5046 | 61.7826 | 61.6889 | 61.7449 | 61.6678 | 61.7794 | 61.7647 | 61.6484 | 61.5371 | 61.504 | 61.5233 | 61.445 | 61.6888 | 61.8317 | 61.3627 | 61.5275 | -0.15166 | 0.1744 | -0.16547 | 0.1606
445.7812 | 123.5504 | -61.6974 | 61.5784 | 0.062332 | -0.026784 | 0.024629 | -0.043331 | 0.059155 | 0.048956 | -0.071874 | 61.5142 | 61.4766 | 61.5004 | 61.4312 | 61.6704 | 61.8088 | 61.3306 | 61.5046 | 61.7597 | 61.6706 | 61.722 | 61.6541 | 61.7565 | 61.7463 | 61.6255 | 61.5371 | 61.4995 | 61.5233 | 61.4541 | 61.6933 | 61.8317 | 61.3535 | 61.5275 | -0.15624 | 0.18356 | -0.17005 | 0.16975
447.4531 | 123.4406 | -61.6745 | 61.6653 | 0.06691 | -0.026784 | 0.020051 | -0.047909 | 0.063733 | 0.058113 | -0.071874 | 61.5279 | 61.4903 | 61.5141 | 61.4358 | 61.6659 | 61.7905 | 61.3261 | 61.4909 | 61.7414 | 61.6477 | 61.6946 | 61.6266 | 61.7382 | 61.7326 | 61.6026 | 61.5508 | 61.5132 | 61.537 | 61.4587 | 61.6888 | 61.8134 | 61.349 | 61.5137 | -0.13793 | 0.20187 | -0.15173 | 0.18807
449.125 | 123.4863 | -61.702 | 61.5784 | 0.06691 | -0.026784 | 0.020051 | -0.057066 | 0.063733 | 0.044377 | -0.08103 | 61.5371 | 61.4903 | 61.5233 | 61.445 | 61.6476 | 61.7813 | 61.3032 | 61.4771 | 61.7689 | 61.6752 | 61.722 | 61.6449 | 61.7657 | 61.7463 | 61.6209 | 61.56 | 61.5132 | 61.5462 | 61.4679 | 61.6704 | 61.8042 | 61.3261 | 61.5 | -0.11046 | 0.23392 | -0.12426 | 0.22011
450.875 | 123.4222 | -61.7203 | 61.6104 | 0.062332 | -0.026784 | 0.024629 | -0.047909 | 0.063733 | 0.053534 | -0.067295 | 61.4959 | 61.472 | 61.4775 | 61.4038 | 61.6796 | 61.8225 | 61.3398 | 61.5092 | 61.7826 | 61.6935 | 61.7449 | 61.6724 | 61.784 | 61.7738 | 61.653 | 61.5188 | 61.4949 | 61.5004 | 61.4267 | 61.7025 | 61.8454 | 61.3627 | 61.5321 | -0.18371 | 0.15609 | -0.20209 | 0.13771
452.6094 | 123.5138 | -61.7065 | 61.5601 | 0.06691 | -0.022205 | 0.015472 | -0.038752 | 0.063733 | 0.044377 | -0.071874 | 61.5188 | 61.4857 | 61.4958 | 61.4175 | 61.6521 | 61.7996 | 61.3215 | 61.4909 | 61.7735 | 61.6843 | 61.722 | 61.6678 | 61.7703 | 61.7509 | 61.6347 | 61.5417 | 61.5086 | 61.5187 | 61.4404 | 61.675 | 61.8225 | 61.3444 | 61.5137 | -0.13335 | 0.19729 | -0.15631 | 0.17433
454.3438 | 123.4772 | -61.734 | 61.5738 | 0.057754 | -0.026784 | 0.020051 | -0.043331 | 0.063733 | 0.053534 | -0.071874 | 61.5142 | 61.4766 | 61.4958 | 61.4267 | 61.6567 | 61.7951 | 61.3123 | 61.4863 | 61.7918 | 61.7072 | 61.7541 | 61.6907 | 61.7977 | 61.7875 | 61.6621 | 61.5371 | 61.4995 | 61.5187 | 61.4496 | 61.6796 | 61.818 | 61.3352 | 61.5092 | -0.14251 | 0.20187 | -0.16089 | 0.18349
456.0938 | 123.5458 | -61.7065 | 61.5646 | 0.057754 | -0.026784 | 0.020051 | -0.047909 | 0.059155 | 0.044377 | -0.071874 | 61.5142 | 61.4903 | 61.505 | 61.4312 | 61.6567 | 61.7905 | 61.3169 | 61.4863 | 61.7643 | 61.6798 | 61.7266 | 61.6586 | 61.7657 | 61.7509 | 61.6347 | 61.5371 | 61.5132 | 61.5279 | 61.4541 | 61.6796 | 61.8134 | 61.3398 | 61.5092 | -0.14251 | 0.19729 | -0.15173 | 0.18807
457.8438 | 123.5229 | -61.6974 | 61.5967 | 0.06691 | -0.022205 | 0.033786 | -0.052488 | 0.063733 | 0.044377 | -0.071874 | 61.5142 | 61.4812 | 61.505 | 61.4221 | 61.6613 | 61.7951 | 61.3215 | 61.4863 | 61.7643 | 61.6752 | 61.7312 | 61.6449 | 61.7611 | 61.7418 | 61.6255 | 61.5371 | 61.504 | 61.5279 | 61.445 | 61.6842 | 61.818 | 61.3444 | 61.5092 | -0.14708 | 0.19272 | -0.15631 | 0.18349
459.5312 | 123.4451 | -61.6379 | 61.6425 | 0.06691 | -0.031363 | 0.024629 | -0.034174 | 0.063733 | 0.062691 | -0.067295 | 61.5371 | 61.4903 | 61.5141 | 61.4404 | 61.643 | 61.7859 | 61.3169 | 61.4725 | 61.7048 | 61.6065 | 61.6625 | 61.6037 | 61.7016 | 61.7006 | 61.5706 | 61.56 | 61.5132 | 61.537 | 61.4633 | 61.6659 | 61.8088 | 61.3398 | 61.4954 | -0.10588 | 0.22019 | -0.12884 | 0.19722
461.2812 | 123.4177 | -61.6379 | 61.6333 | 0.057754 | -0.022205 | 0.024629 | -0.043331 | 0.063733 | 0.062691 | -0.076452 | 61.5417 | 61.5086 | 61.5233 | 61.4541 | 61.6247 | 61.7676 | 61.294 | 61.4588 | 61.6956 | 61.6157 | 61.6625 | 61.5945 | 61.7016 | 61.7006 | 61.5614 | 61.5646 | 61.5315 | 61.5462 | 61.477 | 61.6476 | 61.7905 | 61.3169 | 61.4817 | -0.082987 | 0.24766 | -0.10137 | 0.22927
463.0312 | 123.5184 | -61.6974 | 61.5601 | 0.062332 | -0.035942 | 0.024629 | -0.043331 | 0.063733 | 0.053534 | -0.071874 | 61.5096 | 61.472 | 61.4958 | 61.4221 | 61.6567 | 61.7905 | 61.3169 | 61.4863 | 61.7597 | 61.6614 | 61.722 | 61.6541 | 61.7611 | 61.7509 | 61.6255 | 61.5325 | 61.4949 | 61.5187 | 61.445 | 61.6796 | 61.8134 | 61.3398 | 61.5092 | -0.14708 | 0.19272 | -0.16089 | 0.17891
464.7812 | 123.4863 | -61.702 | 61.5784 | 0.06691 | -0.026784 | 0.020051 | -0.043331 | 0.059155 | 0.048956 | -0.071874 | 61.5142 | 61.4812 | 61.4958 | 61.4175 | 61.6521 | 61.7951 | 61.3306 | 61.5 | 61.7689 | 61.6752 | 61.722 | 61.6586 | 61.7611 | 61.7509 | 61.6301 | 61.5371 | 61.504 | 61.5187 | 61.4404 | 61.675 | 61.818 | 61.3535 | 61.5229 | -0.13793 | 0.18356 | -0.15631 | 0.16518
466.4531 | 123.5504 | -61.6516 | 61.5692 | 0.057754 | -0.031363 | 0.010893 | -0.043331 | 0.059155 | 0.048956 | -0.071874 | 61.5188 | 61.4903 | 61.4958 | 61.4312 | 61.6338 | 61.7722 | 61.3032 | 61.4771 | 61.7094 | 61.6202 | 61.6625 | 61.6083 | 61.7108 | 61.7006 | 61.5797 | 61.5417 | 61.5132 | 61.5187 | 61.4541 | 61.6567 | 61.7951 | 61.3261 | 61.5 | -0.11504 | 0.21561 | -0.138 | 0.19264
468.1875 | 123.3856 | -61.6928 | 61.6287 | 0.071489 | -0.026784 | 0.029208 | -0.043331 | 0.06831 | 0.053534 | -0.076452 | 61.5142 | 61.4674 | 61.5004 | 61.4175 | 61.6613 | 61.7859 | 61.3215 | 61.4817 | 61.7643 | 61.666 | 61.722 | 61.6495 | 61.7611 | 61.7463 | 61.6164 | 61.5371 | 61.4903 | 61.5233 | 61.4404 | 61.6842 | 61.8088 | 61.3444 | 61.5046 | -0.14708 | 0.19272 | -0.16089 | 0.17891
469.9375 | 123.3994 | -61.6882 | 61.6379 | 0.062332 | -0.017627 | 0.020051 | -0.043331 | 0.06831 | 0.053534 | -0.08103 | 61.5325 | 61.4995 | 61.5096 | 61.4404 | 61.6338 | 61.7584 | 61.2986 | 61.468 | 61.7506 | 61.6706 | 61.7083 | 61.6449 | 61.7565 | 61.7418 | 61.6072 | 61.5554 | 61.5224 | 61.5324 | 61.4633 | 61.6567 | 61.7813 | 61.3215 | 61.4908 | -0.1013 | 0.23392 | -0.12426 | 0.21096
471.6094 | 123.5184 | -61.6653 | 61.5738 | 0.06691 | -0.026784 | 0.024629 | -0.043331 | 0.054577 | 0.044377 | -0.076452 | 61.5417 | 61.504 | 61.5279 | 61.4496 | 61.6109 | 61.7539 | 61.2757 | 61.4496 | 61.7323 | 61.6386 | 61.69 | 61.622 | 61.7199 | 61.7097 | 61.5889 | 61.5646 | 61.5269 | 61.5508 | 61.4724 | 61.6338 | 61.7767 | 61.2986 | 61.4725 | -0.069253 | 0.26597 | -0.08306 | 0.25216
473.375 | 123.3948 | -61.6425 | 61.6699 | 0.071489 | -0.026784 | 0.029208 | -0.038752 | 0.063733 | 0.058113 | -0.076452 | 61.5508 | 61.5178 | 61.537 | 61.4587 | 61.6155 | 61.7447 | 61.2711 | 61.4313 | 61.7139 | 61.6157 | 61.6717 | 61.6037 | 61.7062 | 61.7006 | 61.566 | 61.5737 | 61.5407 | 61.5599 | 61.4816 | 61.6384 | 61.7676 | 61.294 | 61.4542 | -0.064674 | 0.27971 | -0.078481 | 0.2659
475.0625 | 123.5001 | -61.6013 | 61.6104 | 0.071489 | -0.026784 | 0.024629 | -0.043331 | 0.063733 | 0.053534 | -0.067295 | 61.5737 | 61.5315 | 61.5645 | 61.4816 | 61.5835 | 61.7127 | 61.2437 | 61.413 | 61.6727 | 61.5745 | 61.6259 | 61.5579 | 61.665 | 61.6548 | 61.534 | 61.5966 | 61.5544 | 61.5874 | 61.5045 | 61.6063 | 61.7355 | 61.2665 | 61.4359 | -0.009734 | 0.33007 | -0.018965 | 0.32084
476.8125 | 123.4497 | -61.5921 | 61.7065 | 0.06691 | -0.035942 | 0.024629 | -0.043331 | 0.063733 | 0.058113 | -0.076452 | 61.6149 | 61.5682 | 61.5965 | 61.5228 | 61.5468 | 61.676 | 61.207 | 61.3672 | 61.659 | 61.5562 | 61.6167 | 61.5488 | 61.6558 | 61.6502 | 61.5156 | 61.6378 | 61.591 | 61.6194 | 61.5457 | 61.5697 | 61.6989 | 61.2299 | 61.3901 | 0.068097 | 0.4079 | 0.049708 | 0.38951
478.5625 | 123.436 | -61.647 | 61.6562 | 0.06691 | -0.026784 | 0.033786 | -0.043331 | 0.063733 | 0.044377 | -0.071874 | 61.5371 | 61.4995 | 61.5233 | 61.4496 | 61.6109 | 61.7493 | 61.2757 | 61.4451 | 61.7139 | 61.6202 | 61.6808 | 61.6037 | 61.7108 | 61.6914 | 61.5752 | 61.56 | 61.5224 | 61.5462 | 61.4724 | 61.6338 | 61.7722 | 61.2986 | 61.468 | -0.073831 | 0.26139 | -0.087638 | 0.24759
480.2656 | 123.3765 | -61.5921 | 61.7249 | 0.057754 | -0.022205 | 0.024629 | -0.047909 | 0.054577 | 0.048956 | -0.067295 | 61.592 | 61.5636 | 61.5828 | 61.5045 | 61.5514 | 61.6943 | 61.2162 | 61.3856 | 61.6499 | 61.5699 | 61.6167 | 61.5442 | 61.6467 | 61.6411 | 61.5248 | 61.6149 | 61.5865 | 61.6057 | 61.5274 | 61.5743 | 61.7172 | 61.2391 | 61.4084 | 0.040627 | 0.37585 | 0.031395 | 0.36662
482.0312 | 123.381 | -61.5738 | 61.7203 | 0.06691 | -0.026784 | 0.020051 | -0.038752 | 0.063733 | 0.053534 | -0.076452 | 61.592 | 61.559 | 61.5737 | 61.4954 | 61.5514 | 61.6943 | 61.2208 | 61.381 | 61.6407 | 61.547 | 61.5938 | 61.535 | 61.6375 | 61.6273 | 61.4973 | 61.6149 | 61.5819 | 61.5965 | 61.5182 | 61.5743 | 61.7172 | 61.2437 | 61.4039 | 0.040627 | 0.37127 | 0.022239 | 0.35289
483.7812 | 123.4451 | -61.615 | 61.6104 | 0.076067 | -0.026784 | 0.029208 | -0.043331 | 0.059155 | 0.044377 | -0.071874 | 61.5829 | 61.5453 | 61.5645 | 61.4862 | 61.5606 | 61.6989 | 61.2253 | 61.3901 | 61.6911 | 61.5882 | 61.6442 | 61.5717 | 61.6741 | 61.6594 | 61.5431 | 61.6058 | 61.5681 | 61.5874 | 61.5091 | 61.5835 | 61.7218 | 61.2482 | 61.413 | 0.022314 | 0.35754 | 0.003926 | 0.33915
485.4688 | 123.4222 | -61.5784 | 61.6928 | 0.071489 | -0.026784 | 0.024629 | -0.047909 | 0.063733 | 0.048956 | -0.067295 | 61.5646 | 61.5315 | 61.5553 | 61.4816 | 61.5697 | 61.7081 | 61.2391 | 61.4084 | 61.6499 | 61.5516 | 61.603 | 61.5305 | 61.6421 | 61.6273 | 61.5111 | 61.5875 | 61.5544 | 61.5782 | 61.5045 | 61.5926 | 61.731 | 61.262 | 61.4313 | -0.005156 | 0.32549 | -0.014386 | 0.31626
487.2344 | 123.4222 | -61.6379 | 61.6287 | 0.071489 | -0.026784 | 0.020051 | -0.047909 | 0.059155 | 0.048956 | -0.071874 | 61.5463 | 61.5132 | 61.5324 | 61.445 | 61.588 | 61.731 | 61.2528 | 61.4222 | 61.7094 | 61.6111 | 61.6579 | 61.59 | 61.697 | 61.6868 | 61.566 | 61.5691 | 61.5361 | 61.5553 | 61.4679 | 61.6109 | 61.7539 | 61.2757 | 61.4451 | -0.041783 | 0.29344 | -0.055591 | 0.27963
488.9219 | 123.349 | -61.6379 | 61.6333 | 0.062332 | -0.022205 | 0.024629 | -0.038752 | 0.059155 | 0.048956 | -0.067295 | 61.5371 | 61.5086 | 61.5279 | 61.445 | 61.5972 | 61.7355 | 61.262 | 61.4268 | 61.7002 | 61.6157 | 61.6625 | 61.5991 | 61.697 | 61.6868 | 61.5706 | 61.56 | 61.5315 | 61.5508 | 61.4679 | 61.6201 | 61.7584 | 61.2849 | 61.4496 | -0.060096 | 0.27513 | -0.069325 | 0.2659
490.6094 | 123.4222 | -61.6013 | 61.6837 | 0.062332 | -0.026784 | 0.020051 | -0.038752 | 0.063733 | 0.053534 | -0.071874 | 61.5737 | 61.5544 | 61.5691 | 61.4816 | 61.5651 | 61.6989 | 61.2162 | 61.3947 | 61.6636 | 61.5745 | 61.6213 | 61.5625 | 61.665 | 61.6548 | 61.5294 | 61.5966 | 61.5773 | 61.592 | 61.5045 | 61.588 | 61.7218 | 61.2391 | 61.4176 | 0.008579 | 0.35754 | 0.003927 | 0.35289
492.3594 | 123.4451 | -61.5875 | 61.6379 | 0.071489 | -0.035942 | 0.015472 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 61.5691 | 61.5361 | 61.5553 | 61.4725 | 61.5651 | 61.7035 | 61.2253 | 61.3901 | 61.659 | 61.5516 | 61.603 | 61.5396 | 61.6513 | 61.6365 | 61.5157 | 61.592 | 61.559 | 61.5782 | 61.4953 | 61.588 | 61.7264 | 61.2482 | 61.413 | 0.004 | 0.3438 | -0.009808 | 0.33
494.0938 | 123.3902 | -61.5509 | 61.7661 | 0.06691 | -0.022205 | 0.024629 | -0.038752 | 0.059155 | 0.062691 | -0.067295 | 61.6104 | 61.5773 | 61.5965 | 61.5228 | 61.5331 | 61.6577 | 61.1887 | 61.3535 | 61.6178 | 61.5287 | 61.5755 | 61.5122 | 61.6101 | 61.6136 | 61.4836 | 61.6332 | 61.6002 | 61.6194 | 61.5457 | 61.556 | 61.6806 | 61.2116 | 61.3764 | 0.077254 | 0.42164 | 0.063443 | 0.40783
495.8438 | 123.4589 | -61.441 | 61.8027 | 0.06691 | -0.026784 | 0.020051 | -0.038752 | 0.063733 | 0.053534 | -0.067295 | 61.6973 | 61.6552 | 61.6835 | 61.5961 | 61.4461 | 61.5753 | 61.1063 | 61.2711 | 61.508 | 61.4143 | 61.4611 | 61.4023 | 61.5048 | 61.4946 | 61.3737 | 61.7202 | 61.678 | 61.7064 | 61.619 | 61.469 | 61.5982 | 61.1292 | 61.294 | 0.25123 | 0.59104 | 0.23742 | 0.57723
497.5312 | 123.4085 | -61.4639 | 61.8118 | 0.06691 | -0.035942 | 0.029208 | -0.043331 | 0.063733 | 0.044377 | -0.067295 | 61.6745 | 61.6414 | 61.6652 | 61.5869 | 61.4599 | 61.5936 | 61.12 | 61.2894 | 61.5308 | 61.428 | 61.4931 | 61.4206 | 61.5277 | 61.5083 | 61.3966 | 61.6973 | 61.6643 | 61.6881 | 61.6098 | 61.4827 | 61.6165 | 61.1429 | 61.3123 | 0.2146 | 0.55441 | 0.20537 | 0.54518
499.2188 | 123.4543 | -61.4914 | 61.7157 | 0.062332 | -0.035942 | 0.020051 | -0.043331 | 0.063733 | 0.048956 | -0.076452 | 61.6607 | 61.6368 | 61.6423 | 61.5732 | 61.4644 | 61.6074 | 61.1292 | 61.294 | 61.5537 | 61.4555 | 61.5114 | 61.4481 | 61.5551 | 61.5403 | 61.4149 | 61.6836 | 61.6597 | 61.6652 | 61.5961 | 61.4873 | 61.6303 | 61.1521 | 61.3169 | 0.19629 | 0.53152 | 0.1779 | 0.51313
500.9844 | 123.4634 | -61.5555 | 61.6333 | 0.06691 | -0.022205 | 0.024629 | -0.043331 | 0.059155 | 0.058113 | -0.071874 | 61.592 | 61.5544 | 61.5737 | 61.4999 | 61.5331 | 61.6715 | 61.2025 | 61.3672 | 61.6224 | 61.5333 | 61.5801 | 61.5121 | 61.6146 | 61.6136 | 61.4836 | 61.6149 | 61.5773 | 61.5965 | 61.5228 | 61.556 | 61.6943 | 61.2253 | 61.3901 | 0.05894 | 0.38959 | 0.040552 | 0.3712
502.6562 | 123.4543 | -61.5921 | 61.6333 | 0.06691 | -0.026784 | 0.020051 | -0.052488 | 0.063733 | 0.058113 | -0.071874 | 61.5783 | 61.5453 | 61.5691 | 61.4908 | 61.5514 | 61.6715 | 61.2116 | 61.3764 | 61.659 | 61.5653 | 61.6122 | 61.5396 | 61.6558 | 61.6502 | 61.5202 | 61.6012 | 61.5681 | 61.592 | 61.5137 | 61.5743 | 61.6943 | 61.2345 | 61.3993 | 0.026891 | 0.3667 | 0.017661 | 0.35747
504.4062 | 123.4268 | -61.6013 | 61.615 | 0.057754 | -0.013048 | 0.020051 | -0.038752 | 0.054577 | 0.048956 | -0.076452 | 61.6012 | 61.5727 | 61.592 | 61.5045 | 61.5148 | 61.6531 | 61.1841 | 61.3535 | 61.659 | 61.5882 | 61.6213 | 61.5625 | 61.6558 | 61.6502 | 61.5248 | 61.6241 | 61.5956 | 61.6149 | 61.5274 | 61.5377 | 61.676 | 61.207 | 61.3764 | 0.08641 | 0.41706 | 0.077178 | 0.40783
506.0938 | 123.4634 | -61.5097 | 61.6974 | 0.062332 | -0.022205 | 0.024629 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 61.6332 | 61.6002 | 61.6194 | 61.5411 | 61.4919 | 61.6257 | 61.1521 | 61.3215 | 61.572 | 61.4875 | 61.5343 | 61.4664 | 61.5689 | 61.5632 | 61.4333 | 61.6561 | 61.6231 | 61.6423 | 61.564 | 61.5148 | 61.6486 | 61.175 | 61.3443 | 0.14135 | 0.48116 | 0.12754 | 0.46735
507.8281 | 123.4589 | -61.5005 | 61.6791 | 0.057754 | -0.017627 | 0.024629 | -0.043331 | 0.059155 | 0.053534 | -0.071874 | 61.6195 | 61.5956 | 61.6057 | 61.532 | 61.5011 | 61.6257 | 61.1521 | 61.3169 | 61.5583 | 61.4829 | 61.5252 | 61.4572 | 61.5597 | 61.5541 | 61.4287 | 61.6424 | 61.6185 | 61.6286 | 61.5549 | 61.5239 | 61.6486 | 61.175 | 61.3398 | 0.11846 | 0.46742 | 0.10465 | 0.45361
509.5625 | 123.3398 | -61.4502 | 61.8164 | 0.06691 | -0.013048 | 0.024629 | -0.038752 | 0.063733 | 0.048956 | -0.067295 | 61.7248 | 61.6964 | 61.711 | 61.6327 | 61.3958 | 61.5204 | 61.0559 | 61.2299 | 61.5171 | 61.4371 | 61.4748 | 61.4114 | 61.5139 | 61.4992 | 61.3829 | 61.7477 | 61.7192 | 61.7339 | 61.6556 | 61.4186 | 61.5433 | 61.0788 | 61.2528 | 0.32906 | 0.66887 | 0.31524 | 0.65506
511.3281 | 123.4131 | -61.3449 | 61.8851 | 0.062332 | -0.013048 | 0.024629 | -0.043331 | 0.063733 | 0.053534 | -0.071874 | 61.7889 | 61.7605 | 61.7797 | 61.6968 | 61.3225 | 61.4609 | 60.9873 | 61.1566 | 61.4072 | 61.3319 | 61.3695 | 61.3016 | 61.4086 | 61.3984 | 61.273 | 61.8118 | 61.7834 | 61.8026 | 61.7197 | 61.3454 | 61.4838 | 61.0102 | 61.1795 | 0.46641 | 0.80165 | 0.45717 | 0.79241
513.0781 | 123.4909 | -61.2671 | 61.9171 | 0.062332 | -0.022205 | 0.020051 | -0.038752 | 0.059155 | 0.044377 | -0.071874 | 61.8668 | 61.8291 | 61.8484 | 61.7793 | 61.2447 | 61.383 | 60.914 | 61.0697 | 61.3294 | 61.2449 | 61.2871 | 61.2283 | 61.3262 | 61.3115 | 61.1952 | 61.8896 | 61.852 | 61.8712 | 61.8021 | 61.2676 | 61.4059 | 60.9369 | 61.0925 | 0.62207 | 0.95274 | 0.60367 | 0.93434
514.8281 | 123.3856 | -61.2671 | 61.972 | 0.071489 | -0.013048 | 0.024629 | -0.043331 | 0.063733 | 0.048956 | -0.071874 | 61.853 | 61.8108 | 61.8255 | 61.7518 | 61.2767 | 61.4014 | 60.9323 | 61.1017 | 61.3386 | 61.254 | 61.2917 | 61.2238 | 61.3308 | 61.316 | 61.1952 | 61.8759 | 61.8337 | 61.8483 | 61.7747 | 61.2996 | 61.4242 | 60.9552 | 61.1246 | 0.57629 | 0.92069 | 0.54874 | 0.89313
516.5312 | 123.3627 | -61.3266 | 61.9263 | 0.06691 | -0.017627 | 0.024629 | -0.034174 | 0.063733 | 0.053534 | -0.071874 | 61.8072 | 61.7788 | 61.8026 | 61.7106 | 61.3088 | 61.4288 | 60.9644 | 61.1292 | 61.3935 | 61.309 | 61.3512 | 61.2924 | 61.3903 | 61.3801 | 61.2547 | 61.8301 | 61.8017 | 61.8255 | 61.7335 | 61.3317 | 61.4517 | 60.9873 | 61.1521 | 0.49846 | 0.84285 | 0.4938 | 0.83819
518.2812 | 123.3261 | -61.3541 | 61.8805 | 0.062332 | -0.013048 | 0.024629 | -0.034174 | 0.059155 | 0.053534 | -0.071874 | 61.7843 | 61.7467 | 61.7659 | 61.6922 | 61.3225 | 61.4517 | 60.9781 | 61.1429 | 61.4164 | 61.341 | 61.3787 | 61.3199 | 61.4132 | 61.4076 | 61.2822 | 61.8072 | 61.7696 | 61.7888 | 61.7151 | 61.3454 | 61.4746 | 61.001 | 61.1658 | 0.46183 | 0.80623 | 0.44344 | 0.78783
520.0312 | 123.4543 | -61.3403 | 61.8393 | 0.062332 | -0.017627 | 0.015472 | -0.038752 | 0.054577 | 0.053534 | -0.071874 | 61.8164 | 61.7925 | 61.8071 | 61.7335 | 61.2905 | 61.4197 | 60.9461 | 61.1154 | 61.4027 | 61.3227 | 61.3558 | 61.3016 | 61.3949 | 61.3939 | 61.2685 | 61.8393 | 61.8154 | 61.83 | 61.7563 | 61.3133 | 61.4426 | 60.969 | 61.1383 | 0.52593 | 0.87033 | 0.51669 | 0.86108
521.7188 | 123.4451 | -61.4868 | 61.6882 | 0.057754 | -0.013048 | 0.020051 | -0.038752 | 0.059155 | 0.053534 | -0.067295 | 61.7935 | 61.7605 | 61.7843 | 61.706 | 61.3088 | 61.438 | 60.9735 | 61.1383 | 61.5446 | 61.4738 | 61.5069 | 61.4481 | 61.546 | 61.5403 | 61.4195 | 61.8164 | 61.7834 | 61.8071 | 61.7289 | 61.3317 | 61.4609 | 60.9964 | 61.1612 | 0.48472 | 0.81996 | 0.47548 | 0.81072
523.4531 | 123.3215 | -61.2671 | 61.9812 | 0.06691 | -0.00389 | 0.024629 | -0.043331 | 0.06831 | 0.053534 | -0.071874 | 61.8805 | 61.8475 | 61.8712 | 61.793 | 61.2218 | 61.3556 | 60.882 | 61.0559 | 61.334 | 61.2632 | 61.2917 | 61.2238 | 61.3354 | 61.3206 | 61.1952 | 61.9034 | 61.8703 | 61.8941 | 61.8159 | 61.2447 | 61.3785 | 60.9049 | 61.0788 | 0.6587 | 0.99852 | 0.64946 | 0.98928
525.2031 | 123.4131 | -61.1938 | 61.9675 | 0.06691 | -0.008469 | 0.024629 | -0.038752 | 0.063733 | 0.048956 | -0.071874 | 61.9629 | 61.9299 | 61.9491 | 61.8708 | 61.1394 | 61.2732 | 60.8041 | 60.9644 | 61.2608 | 61.1854 | 61.2185 | 61.1551 | 61.2576 | 61.2428 | 61.122 | 61.9858 | 61.9528 | 61.972 | 61.8937 | 61.1623 | 61.2961 | 60.827 | 60.9872 | 0.82352 | 1.1588 | 0.80969 | 1.1449
526.9688 | 123.3215 | -61.2991 | 61.9583 | 0.06691 | -0.008469 | 0.020051 | -0.038752 | 0.063733 | 0.048956 | -0.067295 | 61.8347 | 61.8017 | 61.8163 | 61.7335 | 61.2676 | 61.4014 | 60.9232 | 61.0926 | 61.366 | 61.2907 | 61.3192 | 61.2604 | 61.3629 | 61.3481 | 61.2318 | 61.8576 | 61.8246 | 61.8392 | 61.7563 | 61.2905 | 61.4242 | 60.9461 | 61.1154 | 0.56713 | 0.91153 | 0.54874 | 0.89313
528.6406 | 123.3307 | -61.2396 | 61.9766 | 0.062332 | -0.008469 | 0.024629 | -0.043331 | 0.059155 | 0.048956 | -0.071874 | 61.8713 | 61.8475 | 61.8621 | 61.7838 | 61.2081 | 61.3464 | 60.8728 | 61.0468 | 61.302 | 61.2312 | 61.2643 | 61.1963 | 61.2988 | 61.2886 | 61.1677 | 61.8942 | 61.8703 | 61.885 | 61.8067 | 61.2309 | 61.3693 | 60.8957 | 61.0697 | 0.66328 | 0.99852 | 0.65403 | 0.98928
530.4062 | 123.3902 | -61.3083 | 61.8759 | 0.053175 | -0.022205 | 0.024629 | -0.043331 | 0.054577 | 0.044377 | -0.062717 | 61.8347 | 61.7971 | 61.8163 | 61.738 | 61.263 | 61.3968 | 60.9278 | 61.0834 | 61.3615 | 61.2861 | 61.3329 | 61.265 | 61.3629 | 61.3527 | 61.2456 | 61.8576 | 61.82 | 61.8392 | 61.7609 | 61.2859 | 61.4197 | 60.9506 | 61.1063 | 0.57171 | 0.90695 | 0.55331 | 0.88855
532.1719 | 123.3261 | -61.2808 | 61.9812 | 0.06691 | -0.013048 | 0.024629 | -0.038752 | 0.06831 | 0.053534 | -0.071874 | 61.8439 | 61.8108 | 61.8392 | 61.7564 | 61.2355 | 61.3785 | 60.9094 | 61.0697 | 61.3477 | 61.2678 | 61.3055 | 61.2421 | 61.3491 | 61.3344 | 61.2089 | 61.8667 | 61.8337 | 61.8621 | 61.7792 | 61.2584 | 61.4013 | 60.9323 | 61.0925 | 0.60834 | 0.93442 | 0.60367 | 0.92976
533.9062 | 123.3353 | -62.4252 | 60.7773 | 0.06691 | -0.017627 | 0.020051 | -0.043331 | 0.06831 | 0.053534 | -0.067295 | 60.6947 | 60.6707 | 60.6809 | 60.607 | 62.3846 | 62.5276 | 62.054 | 62.2279 | 62.4921 | 62.4076 | 62.4453 | 62.3819 | 62.4935 | 62.4788 | 62.3579 | 60.7175 | 60.6936 | 60.7038 | 60.6299 | 62.4075 | 62.5504 | 62.0769 | 62.2508 | -1.69 | -1.3594 | -1.7038 | -1.3731
535.5938 | 123.3032 | -62.2971 | 60.9283 | 0.06691 | -0.017627 | 0.020051 | -0.047909 | 0.059155 | 0.044377 | -0.067295 | 60.8183 | 60.7898 | 60.8045 | 60.7307 | 62.261 | 62.3902 | 61.9213 | 62.086 | 62.364 | 62.2794 | 62.3171 | 62.2491 | 62.3562 | 62.3414 | 62.2298 | 60.8412 | 60.8126 | 60.8274 | 60.7535 | 62.2839 | 62.4131 | 61.9441 | 62.1089 | -1.4428 | -1.103 | -1.4565 | -1.1168
537.3594 | 123.436 | -62.3291 | 60.7956 | 0.062332 | -0.013048 | 0.015472 | -0.043331 | 0.063733 | 0.053534 | -0.071874 | 60.7816 | 60.7577 | 60.777 | 60.694 | 62.2839 | 62.4177 | 61.9487 | 62.1181 | 62.3914 | 62.3161 | 62.3446 | 62.2858 | 62.3928 | 62.3826 | 62.2572 | 60.8045 | 60.7806 | 60.7999 | 60.7169 | 62.3068 | 62.4406 | 61.9716 | 62.1409 | -1.5023 | -1.1671 | -1.5069 | -1.1717
539.1094 | 123.317 | -62.3749 | 60.8414 | 0.062332 | -0.013048 | 0.015472 | -0.043331 | 0.063733 | 0.048956 | -0.071874 | 60.7404 | 60.7257 | 60.7404 | 60.6574 | 62.3205 | 62.4543 | 61.9854 | 62.1593 | 62.4372 | 62.3618 | 62.3904 | 62.3315 | 62.4386 | 62.4238 | 62.303 | 60.7633 | 60.7485 | 60.7633 | 60.6803 | 62.3434 | 62.4772 | 62.0082 | 62.1822 | -1.5801 | -1.2449 | -1.5801 | -1.245
540.875 | 123.2895 | -62.3428 | 60.91 | 0.062332 | -0.013048 | 0.010893 | -0.043331 | 0.063733 | 0.048956 | -0.067295 | 60.7588 | 60.7394 | 60.7541 | 60.6711 | 62.3022 | 62.4406 | 61.9716 | 62.1318 | 62.4052 | 62.3298 | 62.3537 | 62.2995 | 62.4066 | 62.3918 | 62.2755 | 60.7816 | 60.7623 | 60.777 | 60.694 | 62.3251 | 62.4635 | 61.9945 | 62.1547 | -1.5435 | -1.2129 | -1.5481 | -1.2175
542.625 | 123.3627 | -62.4344 | 60.7773 | 0.06691 | -0.013048 | 0.024629 | -0.047909 | 0.063733 | 0.044377 | -0.067295 | 60.7175 | 60.689 | 60.7038 | 60.6162 | 62.348 | 62.4818 | 62.0082 | 62.1684 | 62.5013 | 62.4213 | 62.459 | 62.3865 | 62.4981 | 62.4788 | 62.3671 | 60.7404 | 60.7119 | 60.7267 | 60.6391 | 62.3709 | 62.5047 | 62.0311 | 62.1913 | -1.6305 | -1.2907 | -1.6442 | -1.3045
544.3125 | 123.3536 | -62.4893 | 60.6583 | 0.062332 | -0.013048 | 0.024629 | -0.043331 | 0.059155 | 0.048956 | -0.071874 | 60.626 | 60.6112 | 60.6214 | 60.5429 | 62.4258 | 62.555 | 62.0815 | 62.26 | 62.5517 | 62.4763 | 62.5139 | 62.446 | 62.5485 | 62.5383 | 62.4174 | 60.6489 | 60.6341 | 60.6443 | 60.5658 | 62.4487 | 62.5779 | 62.1044 | 62.2829 | -1.7999 | -1.4555 | -1.8045 | -1.4601
546.0625 | 110.6277 | -118.5562 | 4.6051 | 0.030283 | -0.090888 | -0.057786 | -0.13032 | -0.023249 | -0.038034 | -0.15886 | 30.0691 | 29.3882 | 29.956 | 29.6207 | 92.3579 | 92.5597 | 92.2119 | 91.9494 | 118.5865 | 118.4653 | 118.4984 | 118.4259 | 118.533 | 118.5182 | 118.3974 | 30.092 | 29.4111 | 29.9789 | 29.6436 | 92.3808 | 92.5826 | 92.2348 | 91.9723 | -62.2888 | -62.1428 | -62.4019 | -62.2558
547.8281 | 123.3353 | -120.3918 | 2.8244 | 0.06691 | -0.022205 | 0.015472 | -0.052488 | 0.054577 | 0.048956 | -0.076452 | 2.7401 | 2.7945 | 2.729 | 2.7097 | 120.5641 | 120.5271 | 120.2682 | 120.3845 | 120.4588 | 120.3696 | 120.4073 | 120.3394 | 120.4464 | 120.4408 | 120.3154 | 2.763 | 2.8173 | 2.7519 | 2.7326 | 120.587 | 120.55 | 120.2911 | 120.4074 | -117.824 | -117.5282 | -117.8351 | -117.5392
549.5156 | 123.3765 | -120.7581 | 2.4857 | 0.062332 | -0.026784 | 0.015472 | -0.052488 | 0.054577 | 0.044377 | -0.08103 | 2.6439 | 2.6891 | 2.555 | 2.435 | 120.6694 | 120.6278 | 120.1858 | 120.4898 | 120.8204 | 120.7313 | 120.7735 | 120.7056 | 120.8126 | 120.8024 | 120.677 | 2.6668 | 2.712 | 2.5779 | 2.4579 | 120.6923 | 120.6507 | 120.2087 | 120.5127 | -118.0254 | -117.5419 | -118.1143 | -117.6308
551.2656 | 123.317 | -121.0831 | 2.2064 | 0.062332 | -0.022205 | 0.015472 | -0.047909 | 0.049999 | 0.044377 | -0.076452 | 1.7648 | 1.8192 | 1.676 | 1.565 | 121.4339 | 121.5022 | 121.0832 | 121.355 | 121.1454 | 121.0609 | 121.0985 | 121.0352 | 121.1331 | 121.1274 | 121.0066 | 1.7877 | 1.8421 | 1.6989 | 1.5879 | 121.4568 | 121.5251 | 121.1061 | 121.3779 | -119.6691 | -119.3183 | -119.7579 | -119.4072
553.0156 | 123.3627 | -122.4518 | 0.7782 | 0.057754 | -0.026784 | 0.020051 | -0.061645 | 0.059155 | 0.039799 | -0.08103 | 0.8171 | 0.87593 | 0.71457 | 0.60796 | 122.3358 | 122.4453 | 121.9897 | 122.3027 | 122.5095 | 122.425 | 122.4718 | 122.3901 | 122.5109 | 122.4916 | 122.3708 | 0.83998 | 0.89882 | 0.73746 | 0.63085 | 122.3587 | 122.4682 | 122.0126 | 122.3256 | -121.5187 | -121.1726 | -121.6212 | -121.2751
554.6875 | 123.3582 | -122.4197 | 0.81482 | 0.062332 | -0.031363 | 0.010893 | -0.047909 | 0.045421 | 0.039799 | -0.076452 | 0.73468 | 0.79809 | 0.63216 | 0.5118 | 122.3496 | 122.5368 | 122.0401 | 122.3897 | 122.4821 | 122.3884 | 122.4306 | 122.3718 | 122.4652 | 122.4595 | 122.3433 | 0.75757 | 0.82098 | 0.65505 | 0.53469 | 122.3724 | 122.5597 | 122.063 | 122.4126 | -121.6149 | -121.3054 | -121.7174 | -121.4079
556.4531 | 123.3078 | -122.58 | 0.68207 | 0.062332 | -0.026784 | 0.006315 | -0.052488 | 0.054577 | 0.044377 | -0.076452 | 0.63396 | 0.69278 | 0.54517 | 0.4248 | 122.4457 | 122.6421 | 122.1408 | 122.4813 | 122.6423 | 122.5532 | 122.5863 | 122.5275 | 122.6345 | 122.6243 | 122.5035 | 0.65685 | 0.71567 | 0.56806 | 0.44769 | 122.4686 | 122.665 | 122.1637 | 122.5042 | -121.8117 | -121.5068 | -121.9005 | -121.5956
558.2031 | 123.3261 | -122.2046 | 1.062 | 0.057754 | -0.031363 | 0.020051 | -0.047909 | 0.054577 | 0.039799 | -0.08103 | 0.93614 | 0.99956 | 0.86108 | 0.7316 | 122.1298 | 122.3217 | 121.8295 | 121.9548 | 122.2623 | 122.1732 | 122.2246 | 122.1567 | 122.2592 | 122.2444 | 122.1236 | 0.95903 | 1.0224 | 0.88396 | 0.75449 | 122.1527 | 122.3446 | 121.8524 | 121.9777 | -121.1937 | -120.8933 | -121.2687 | -120.9684
559.8906 | 123.4085 | -122.3053 | 0.93384 | 0.062332 | -0.026784 | 0.010893 | -0.052488 | 0.049999 | 0.039799 | -0.076452 | 0.85372 | 0.91256 | 0.76951 | 0.64002 | 122.2259 | 122.4041 | 121.9119 | 122.0463 | 122.3676 | 122.2785 | 122.3162 | 122.2528 | 122.3553 | 122.3451 | 122.2288 | 0.87661 | 0.93545 | 0.7924 | 0.6629 | 122.2488 | 122.427 | 121.9348 | 122.0692 | -121.3722 | -121.0582 | -121.4564 | -121.1424
561.6406 | 123.2758 | -122.4014 | 0.88806 | 0.057754 | -0.031363 | 0.010893 | -0.047909 | 0.045421 | 0.044377 | -0.08103 | 0.81252 | 0.86677 | 0.72373 | 0.59881 | 122.2626 | 122.4544 | 121.9577 | 122.0876 | 122.4592 | 122.3701 | 122.4123 | 122.3535 | 122.4468 | 122.4458 | 122.3204 | 0.83541 | 0.88966 | 0.74662 | 0.62169 | 122.2855 | 122.4773 | 121.9805 | 122.1104 | -121.4501 | -121.1451 | -121.5388 | -121.2339
563.3906 | 123.3673 | -122.3602 | 0.85144 | 0.06691 | -0.026784 | 0.015472 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 0.82625 | 0.88967 | 0.73288 | 0.61712 | 122.2305 | 122.427 | 121.9302 | 122.0463 | 122.4271 | 122.3334 | 122.3757 | 122.3123 | 122.4194 | 122.4092 | 122.2838 | 0.84914 | 0.91256 | 0.75577 | 0.64001 | 122.2534 | 122.4499 | 121.9531 | 122.0692 | -121.4043 | -121.1039 | -121.4976 | -121.1973
565.1406 | 123.3536 | -122.319 | 0.84686 | 0.06691 | -0.022205 | 0.010893 | -0.043331 | 0.054577 | 0.044377 | -0.085608 | 0.84457 | 0.90798 | 0.76493 | 0.63544 | 122.2076 | 122.4041 | 121.9119 | 122.0235 | 122.3859 | 122.2968 | 122.3299 | 122.2757 | 122.3736 | 122.3634 | 122.2334 | 0.86746 | 0.93087 | 0.78782 | 0.65833 | 122.2305 | 122.427 | 121.9348 | 122.0463 | -121.3631 | -121.0673 | -121.4427 | -121.1469
566.8906 | 123.3261 | -122.438 | 0.77362 | 0.06691 | -0.022205 | 0.020051 | -0.043331 | 0.054577 | 0.039799 | -0.071874 | 0.73011 | 0.78893 | 0.6459 | 0.51638 | 122.3312 | 122.5185 | 122.0263 | 122.1654 | 122.505 | 122.4158 | 122.4581 | 122.3947 | 122.4926 | 122.4778 | 122.3662 | 0.75299 | 0.81182 | 0.66878 | 0.53927 | 122.3541 | 122.5414 | 122.0492 | 122.1883 | -121.6011 | -121.2962 | -121.6853 | -121.3804
568.5625 | 123.3627 | -122.2275 | 0.9613 | 0.057754 | -0.022205 | 0.020051 | -0.047909 | 0.059155 | 0.044377 | -0.067295 | 0.93156 | 1.0041 | 0.84276 | 0.72244 | 122.139 | 122.3079 | 121.8203 | 121.9456 | 122.2852 | 122.2053 | 122.2475 | 122.1796 | 122.2866 | 122.2719 | 122.1602 | 0.95445 | 1.027 | 0.86565 | 0.74533 | 122.1618 | 122.3308 | 121.8432 | 121.9685 | -121.2074 | -120.8887 | -121.2962 | -120.9775
570.3125 | 123.2346 | -122.168 | 1.0712 | 0.06691 | -0.022205 | 0.020051 | -0.038752 | 0.054577 | 0.048956 | -0.076452 | 0.8171 | 0.88967 | 0.73288 | 0.61254 | 122.2305 | 122.4132 | 121.9165 | 122.0418 | 122.2349 | 122.1458 | 122.188 | 122.1292 | 122.2225 | 122.2169 | 122.0915 | 0.83998 | 0.91256 | 0.75577 | 0.63543 | 122.2534 | 122.4361 | 121.9393 | 122.0647 | -121.4134 | -121.0994 | -121.4976 | -121.1836
572.0625 | 123.2758 | -122.2366 | 0.99792 | 0.06691 | -0.017627 | 0.015472 | -0.052488 | 0.049999 | 0.044377 | -0.08103 | 0.96819 | 1.0316 | 0.88397 | 0.75907 | 122.0978 | 122.2713 | 121.7837 | 121.909 | 122.3035 | 122.219 | 122.2521 | 122.1841 | 122.2866 | 122.281 | 122.1556 | 0.99108 | 1.0545 | 0.90685 | 0.78196 | 122.1206 | 122.2942 | 121.8066 | 121.9319 | -121.1296 | -120.8155 | -121.2138 | -120.8997
573.7969 | 123.262 | -122.1909 | 1.0345 | 0.06691 | -0.017627 | 0.015472 | -0.038752 | 0.059155 | 0.048956 | -0.08103 | 0.94987 | 1.0179 | 0.87939 | 0.74076 | 122.0794 | 122.2805 | 121.7837 | 121.8998 | 122.2578 | 122.1732 | 122.2063 | 122.1521 | 122.25 | 122.2398 | 122.1098 | 0.97276 | 1.0408 | 0.90228 | 0.76364 | 122.1023 | 122.3034 | 121.8066 | 121.9227 | -121.1296 | -120.8338 | -121.2001 | -120.9043
575.4844 | 123.381 | -121.9666 | 1.1993 | 0.062332 | -0.017627 | 0.015472 | -0.052488 | 0.059155 | 0.048956 | -0.08103 | 1.3162 | 1.3842 | 1.2365 | 1.1117 | 121.759 | 121.9096 | 121.4174 | 121.5427 | 122.0289 | 121.9489 | 121.982 | 121.9141 | 122.0257 | 122.0155 | 121.8855 | 1.339 | 1.4071 | 1.2594 | 1.1345 | 121.7819 | 121.9325 | 121.4403 | 121.5656 | -120.4428 | -120.1013 | -120.5225 | -120.1809
577.1875 | 123.3582 | -121.6095 | 1.5427 | 0.057754 | -0.017627 | 0.010893 | -0.052488 | 0.054577 | 0.048956 | -0.076452 | 1.4856 | 1.549 | 1.3967 | 1.2811 | 121.553 | 121.7403 | 121.2526 | 121.3779 | 121.6673 | 121.5919 | 121.6204 | 121.557 | 121.6641 | 121.6585 | 121.533 | 1.5084 | 1.5719 | 1.4196 | 1.304 | 121.5758 | 121.7631 | 121.2755 | 121.4008 | -120.0674 | -119.767 | -120.1562 | -119.8559
578.9375 | 123.2803 | -121.3989 | 1.767 | 0.076067 | -0.017627 | 0.020051 | -0.057066 | 0.059155 | 0.048956 | -0.08103 | 1.4169 | 1.4895 | 1.3418 | 1.2216 | 121.6308 | 121.7998 | 121.3167 | 121.442 | 121.475 | 121.3813 | 121.419 | 121.3419 | 121.4581 | 121.4479 | 121.3179 | 1.4398 | 1.5124 | 1.3647 | 1.2444 | 121.6537 | 121.8227 | 121.3396 | 121.4649 | -120.2139 | -119.8998 | -120.289 | -119.9749
580.625 | 123.2254 | -122.0306 | 1.181 | 0.062332 | -0.017627 | 0.020051 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 1.0964 | 1.1598 | 1.0167 | 0.88728 | 121.9375 | 122.1294 | 121.6326 | 121.7533 | 122.093 | 122.013 | 122.0507 | 121.9827 | 122.0852 | 122.0796 | 121.9542 | 1.1193 | 1.1827 | 1.0396 | 0.91017 | 121.9604 | 122.1523 | 121.6555 | 121.7762 | -120.8411 | -120.5362 | -120.9208 | -120.6159
582.3906 | 123.3353 | -121.7697 | 1.4465 | 0.071489 | -0.026784 | 0.020051 | -0.052488 | 0.054577 | 0.044377 | -0.076452 | 1.2063 | 1.2606 | 1.1175 | 0.98802 | 121.8322 | 122.0195 | 121.5456 | 121.6755 | 121.8412 | 121.7429 | 121.7898 | 121.7172 | 121.8243 | 121.8141 | 121.6933 | 1.2292 | 1.2834 | 1.1403 | 1.0109 | 121.8551 | 122.0424 | 121.5685 | 121.6984 | -120.626 | -120.3393 | -120.7148 | -120.4281
584.1406 | 123.2895 | -122.1634 | 1.0162 | 0.062332 | -0.013048 | 0.020051 | -0.043331 | 0.059155 | 0.039799 | -0.076452 | 1.0094 | 1.0682 | 0.91602 | 0.80486 | 122.0245 | 122.2072 | 121.7287 | 121.8403 | 122.2257 | 122.1503 | 122.1834 | 122.1201 | 122.2225 | 122.2032 | 122.0869 | 1.0323 | 1.0911 | 0.9389 | 0.82775 | 122.0474 | 122.2301 | 121.7516 | 121.8632 | -121.0151 | -120.7193 | -121.1085 | -120.8127
585.8906 | 123.2803 | -122.1634 | 1.0208 | 0.06691 | -0.017627 | 0.010893 | -0.047909 | 0.063733 | 0.048956 | -0.08103 | 1.0094 | 1.0728 | 0.91602 | 0.80028 | 122.0062 | 122.2072 | 121.7058 | 121.8312 | 122.2303 | 122.1458 | 122.1743 | 122.1155 | 122.2271 | 122.2123 | 122.0824 | 1.0323 | 1.0957 | 0.9389 | 0.82317 | 122.0291 | 122.2301 | 121.7287 | 121.8541 | -120.9968 | -120.6965 | -121.0902 | -120.7898
587.5781 | 123.3032 | -122.287 | 0.87433 | 0.062332 | -0.022205 | 0.015472 | -0.043331 | 0.059155 | 0.044377 | -0.071874 | 0.83999 | 0.9034 | 0.74204 | 0.63544 | 122.1802 | 122.372 | 121.8844 | 122.0097 | 122.3493 | 122.2648 | 122.3025 | 122.2437 | 122.3461 | 122.3314 | 122.2151 | 0.86288 | 0.92629 | 0.76493 | 0.65833 | 122.2031 | 122.3949 | 121.9073 | 122.0326 | -121.3402 | -121.0444 | -121.4381 | -121.1424
589.3281 | 123.2391 | -122.2504 | 0.95215 | 0.06691 | -0.022205 | 0.020051 | -0.047909 | 0.059155 | 0.053534 | -0.071874 | 0.86746 | 0.93088 | 0.77867 | 0.67207 | 122.1435 | 122.3354 | 121.8432 | 121.9731 | 122.3173 | 122.2282 | 122.2704 | 122.2025 | 122.3095 | 122.3039 | 122.1785 | 0.89035 | 0.95376 | 0.80156 | 0.69496 | 122.1664 | 122.3583 | 121.8661 | 121.996 | -121.2761 | -120.9757 | -121.3649 | -121.0645
591.0312 | 123.262 | -122.2641 | 0.9201 | 0.06691 | -0.026784 | 0.024629 | -0.047909 | 0.045421 | 0.044377 | -0.085608 | 0.8583 | 0.92172 | 0.77409 | 0.64917 | 122.1573 | 122.3446 | 121.8569 | 121.9777 | 122.331 | 122.2373 | 122.2887 | 122.2162 | 122.3095 | 122.3085 | 122.1785 | 0.88119 | 0.94461 | 0.79698 | 0.67206 | 122.1802 | 122.3675 | 121.8798 | 122.0006 | -121.299 | -120.9986 | -121.3832 | -121.0828
592.7812 | 123.175 | -122.3145 | 0.90179 | 0.062332 | -0.022205 | 0.015472 | -0.038752 | 0.063733 | 0.039799 | -0.076452 | 0.84457 | 0.90798 | 0.76493 | 0.64002 | 122.171 | 122.372 | 121.8661 | 121.9914 | 122.3768 | 122.2922 | 122.3299 | 122.2757 | 122.3782 | 122.3543 | 122.238 | 0.86746 | 0.93087 | 0.78782 | 0.6629 | 122.1939 | 122.3949 | 121.889 | 122.0143 | -121.3264 | -121.0215 | -121.4061 | -121.1012
594.5312 | 123.3032 | -122.2458 | 0.86975 | 0.06691 | -0.017627 | 0.020051 | -0.038752 | 0.054577 | 0.039799 | -0.071874 | 0.82625 | 0.89882 | 0.74662 | 0.63086 | 122.1756 | 122.3766 | 121.8752 | 121.996 | 122.3127 | 122.2282 | 122.2658 | 122.207 | 122.3004 | 122.2856 | 122.1739 | 0.84914 | 0.92171 | 0.76951 | 0.65375 | 122.1985 | 122.3995 | 121.8981 | 122.0189 | -121.3493 | -121.049 | -121.429 | -121.1286
596.2188 | 123.2117 | -122.1863 | 1.0025 | 0.071489 | -0.022205 | 0.010893 | -0.047909 | 0.054577 | 0.039799 | -0.071874 | 0.95445 | 1.0179 | 0.87023 | 0.74991 | 122.0474 | 122.2484 | 121.7516 | 121.8815 | 122.2578 | 122.1641 | 122.1972 | 122.1384 | 122.2409 | 122.2261 | 122.1144 | 0.97734 | 1.0408 | 0.89312 | 0.7728 | 122.0703 | 122.2713 | 121.7745 | 121.9044 | -121.0929 | -120.7972 | -121.1772 | -120.8814
597.9688 | 123.3353 | -122.2321 | 0.86975 | 0.06691 | -0.026784 | 0.015472 | -0.047909 | 0.054577 | 0.044377 | -0.076452 | 0.84915 | 0.9034 | 0.77409 | 0.64002 | 122.1481 | 122.3537 | 121.8615 | 121.9731 | 122.299 | 122.2053 | 122.2475 | 122.1841 | 122.2866 | 122.2764 | 122.1556 | 0.87203 | 0.92629 | 0.79698 | 0.6629 | 122.171 | 122.3766 | 121.8844 | 121.996 | -121.299 | -121.0124 | -121.374 | -121.0874
599.6562 | 123.2666 | -122.2778 | 0.86975 | 0.062332 | -0.017627 | 0.010893 | -0.052488 | 0.045421 | 0.035221 | -0.08103 | 0.8583 | 0.92172 | 0.7512 | 0.6446 | 122.1435 | 122.3354 | 121.8432 | 121.9594 | 122.3402 | 122.2602 | 122.2887 | 122.2253 | 122.3233 | 122.3131 | 122.1968 | 0.88119 | 0.94461 | 0.77409 | 0.66748 | 122.1664 | 122.3583 | 121.8661 | 121.9823 | -121.2852 | -120.9849 | -121.3923 | -121.092
601.4219 | 123.3124 | -122.0215 | 1.0849 | 0.06691 | -0.022205 | 0.020051 | -0.052488 | 0.059155 | 0.048956 | -0.085608 | 1.1239 | 1.0453 | 1.0351 | 0.92392 | 121.8643 | 122.0561 | 121.5548 | 121.6847 | 122.0884 | 121.9993 | 122.0415 | 121.969 | 122.0806 | 122.0704 | 121.9359 | 1.1467 | 1.0682 | 1.0579 | 0.94681 | 121.8872 | 122.079 | 121.5776 | 121.7076 | -120.7404 | -120.4309 | -120.8292 | -120.5197
603.125 | 123.3307 | -122.1085 | 1.0025 | 0.06691 | -0.026784 | 0.010893 | -0.047909 | 0.059155 | 0.039799 | -0.08103 | 1.0048 | 0.92172 | 0.92517 | 0.80486 | 121.997 | 122.1843 | 121.6921 | 121.8174 | 122.1754 | 122.0817 | 122.1194 | 122.0605 | 122.1676 | 122.1483 | 122.0274 | 1.0277 | 0.94461 | 0.94806 | 0.82775 | 122.0199 | 122.2072 | 121.715 | 121.8403 | -120.9922 | -120.6873 | -121.0719 | -120.7669
604.875 | 123.3124 | -122.3053 | 0.84686 | 0.071489 | -0.022205 | 0.015472 | -0.047909 | 0.063733 | 0.048956 | -0.08103 | 0.82625 | 0.74315 | 0.74662 | 0.62628 | 122.1573 | 122.3629 | 121.8661 | 121.9777 | 122.3768 | 122.2831 | 122.3208 | 122.2574 | 122.369 | 122.3543 | 122.2243 | 0.84914 | 0.76603 | 0.76951 | 0.64917 | 122.1802 | 122.3858 | 121.889 | 122.0006 | -121.331 | -121.0398 | -121.4107 | -121.1195
606.5625 | 123.2254 | -122.2321 | 0.91553 | 0.062332 | -0.022205 | 0.029208 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 0.85372 | 0.80267 | 0.78324 | 0.64917 | 122.1435 | 122.3354 | 121.8478 | 121.9639 | 122.2944 | 122.2099 | 122.2613 | 122.1841 | 122.2912 | 122.281 | 122.1556 | 0.87661 | 0.82556 | 0.80613 | 0.67206 | 122.1664 | 122.3583 | 121.8707 | 121.9868 | -121.2898 | -120.9941 | -121.3603 | -121.0645
608.3125 | 123.1888 | -122.2412 | 0.9613 | 0.06691 | -0.026784 | 0.015472 | -0.038752 | 0.059155 | 0.048956 | -0.076452 | 0.89035 | 0.80725 | 0.80156 | 0.68123 | 122.1023 | 122.2942 | 121.8066 | 121.9273 | 122.3081 | 122.2144 | 122.2567 | 122.2025 | 122.3004 | 122.2902 | 122.1648 | 0.91324 | 0.83014 | 0.82445 | 0.70412 | 122.1252 | 122.3171 | 121.8295 | 121.9502 | -121.212 | -120.9162 | -121.3008 | -121.005
610.0625 | 123.2483 | -122.1909 | 0.95215 | 0.053175 | -0.022205 | 0.020051 | -0.057066 | 0.054577 | 0.044377 | -0.08103 | 0.88577 | 0.8393 | 0.80614 | 0.68123 | 122.1069 | 122.2988 | 121.802 | 121.9273 | 122.244 | 122.1687 | 122.2109 | 122.1338 | 122.2454 | 122.2352 | 122.1098 | 0.90866 | 0.86219 | 0.82902 | 0.70412 | 122.1298 | 122.3217 | 121.8249 | 121.9502 | -121.2211 | -120.9162 | -121.3008 | -120.9959
611.8125 | 123.1888 | -122.1359 | 1.0437 | 0.06691 | -0.026784 | 0.020051 | -0.052488 | 0.059155 | 0.039799 | -0.076452 | 1.0186 | 0.96293 | 0.93891 | 0.95139 | 122.171 | 122.166 | 121.8569 | 121.9502 | 122.2028 | 122.1091 | 122.156 | 122.0834 | 122.1951 | 122.1757 | 122.0595 | 1.0414 | 0.98582 | 0.96179 | 0.97428 | 122.1939 | 122.1889 | 121.8798 | 121.9731 | -121.1525 | -120.8384 | -121.2321 | -120.918
613.5 | 123.2849 | -122.1817 | 0.92926 | 0.06691 | -0.026784 | 0.015472 | -0.043331 | 0.059155 | 0.048956 | -0.08103 | 1.2292 | 1.1507 | 1.1404 | 1.0292 | 121.8322 | 121.9554 | 121.5044 | 121.6252 | 122.2486 | 122.1549 | 122.1972 | 122.1384 | 122.2409 | 122.2307 | 122.1007 | 1.252 | 1.1735 | 1.1632 | 1.0521 | 121.8551 | 121.9783 | 121.5273 | 121.648 | -120.6031 | -120.2752 | -120.6919 | -120.364
615.25 | 123.2162 | -121.8567 | 1.2863 | 0.062332 | -0.022205 | 0.015472 | -0.052488 | 0.049999 | 0.044377 | -0.08103 | 1.1696 | 1.2377 | 1.0991 | 0.96971 | 121.8322 | 122.0012 | 121.5044 | 121.6435 | 121.919 | 121.8345 | 121.8722 | 121.8042 | 121.9067 | 121.9011 | 121.7757 | 1.1925 | 1.2605 | 1.122 | 0.9926 | 121.8551 | 122.0241 | 121.5273 | 121.6664 | -120.6626 | -120.3348 | -120.7331 | -120.4053
617.0156 | 123.3307 | -121.8521 | 1.2726 | 0.053175 | -0.026784 | 0.020051 | -0.043331 | 0.054577 | 0.039799 | -0.08103 | 1.2337 | 1.2926 | 1.1449 | 1.0338 | 121.8231 | 121.9371 | 121.4586 | 121.5931 | 121.9053 | 121.8253 | 121.8722 | 121.8088 | 121.9067 | 121.8919 | 121.7711 | 1.2566 | 1.3155 | 1.1678 | 1.0567 | 121.846 | 121.96 | 121.4815 | 121.616 | -120.5893 | -120.2249 | -120.6781 | -120.3137
618.6875 | 123.2895 | -121.8842 | 1.2177 | 0.062332 | -0.022205 | 0.015472 | -0.047909 | 0.049999 | 0.048956 | -0.085608 | 1.6641 | 1.6223 | 1.5982 | 1.4688 | 121.3652 | 121.5068 | 121.0282 | 121.1582 | 121.9465 | 121.862 | 121.8996 | 121.8362 | 121.9342 | 121.9331 | 121.7985 | 1.687 | 1.6452 | 1.6211 | 1.4917 | 121.3881 | 121.5297 | 121.0511 | 121.1811 | -119.7011 | -119.3641 | -119.7671 | -119.4301
620.4375 | 123.1613 | -121.0281 | 2.1423 | 0.06691 | -0.017627 | 0.020051 | -0.047909 | 0.059155 | 0.044377 | -0.08103 | 1.9938 | 1.9565 | 1.9141 | 1.7939 | 121.1638 | 121.168 | 120.7352 | 120.8606 | 121.095 | 121.0105 | 121.0482 | 120.9802 | 121.0873 | 121.0725 | 120.9471 | 2.0167 | 1.9794 | 1.937 | 1.8168 | 121.1867 | 121.1909 | 120.7581 | 120.8835 | -119.17 | -118.7415 | -119.2497 | -118.8212
622.1875 | 123.1796 | -120.5154 | 2.417 | 0.057754 | -0.022205 | 0.020051 | -0.043331 | 0.054577 | 0.044377 | -0.076452 | 0.94529 | 0.89882 | 0.87481 | 0.74991 | 122.0382 | 122.221 | 121.7242 | 121.8586 | 120.5732 | 120.4932 | 120.5355 | 120.4721 | 120.57 | 120.5598 | 120.439 | 0.96818 | 0.92171 | 0.8977 | 0.7728 | 122.0611 | 122.2438 | 121.7471 | 121.8815 | -121.0929 | -120.7789 | -121.1634 | -120.8494
623.875 | 123.2391 | -122.287 | 0.85144 | 0.062332 | -0.026784 | 0.020051 | -0.047909 | 0.054577 | 0.048956 | -0.085608 | 0.7942 | 0.73857 | 0.70541 | 0.58507 | 122.1802 | 122.3812 | 121.8752 | 122.0143 | 122.3493 | 122.2602 | 122.307 | 122.2391 | 122.3416 | 122.3359 | 122.2014 | 0.81709 | 0.76145 | 0.7283 | 0.60796 | 122.2031 | 122.4041 | 121.8981 | 122.0372 | -121.386 | -121.081 | -121.4747 | -121.1698
625.6094 | 123.1567 | -121.5225 | 1.8036 | 0.062332 | -0.026784 | 0.015472 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 1.3757 | 1.3338 | 1.2914 | 1.1758 | 121.6491 | 121.7769 | 121.3121 | 121.4558 | 121.5849 | 121.4957 | 121.538 | 121.4746 | 121.5771 | 121.5715 | 121.4461 | 1.3986 | 1.3567 | 1.3143 | 1.1987 | 121.672 | 121.7998 | 121.335 | 121.4787 | -120.2734 | -119.9364 | -120.3577 | -120.0207
627.3594 | 123.1659 | -121.5179 | 1.6296 | 0.057754 | -0.022205 | 0.024629 | -0.047909 | 0.054577 | 0.053534 | -0.076452 | 1.655 | 1.6131 | 1.5707 | 1.4505 | 121.3744 | 121.5068 | 121.0328 | 121.1444 | 121.5757 | 121.4957 | 121.5426 | 121.47 | 121.5725 | 121.5715 | 121.4415 | 1.6778 | 1.636 | 1.5936 | 1.4734 | 121.3973 | 121.5297 | 121.0557 | 121.1673 | -119.7194 | -119.3779 | -119.8037 | -119.4621
629.1094 | 123.2574 | -122.2366 | 0.85602 | 0.062332 | -0.026784 | 0.020051 | -0.043331 | 0.059155 | 0.044377 | -0.076452 | 0.8171 | 0.81183 | 0.7512 | 0.61712 | 122.1344 | 122.34 | 121.8432 | 121.9639 | 122.299 | 122.2098 | 122.2567 | 122.1933 | 122.2958 | 122.281 | 122.1602 | 0.83998 | 0.83472 | 0.77409 | 0.64001 | 122.1573 | 122.3629 | 121.8661 | 121.9868 | -121.3173 | -121.0261 | -121.3832 | -121.092
630.8594 | 123.2025 | -122.3236 | 0.81024 | 0.06691 | -0.031363 | 0.015472 | -0.052488 | 0.059155 | 0.053534 | -0.076452 | 0.74384 | 0.71567 | 0.66879 | 0.54844 | 122.2259 | 122.4132 | 121.9165 | 122.0463 | 122.3905 | 122.2922 | 122.3391 | 122.2711 | 122.3828 | 122.3771 | 122.2472 | 0.76673 | 0.73856 | 0.69168 | 0.57132 | 122.2488 | 122.4361 | 121.9393 | 122.0692 | -121.4821 | -121.1726 | -121.5572 | -121.2477
632.5625 | 123.2758 | -121.9894 | 1.0529 | 0.06691 | -0.031363 | 0.020051 | -0.047909 | 0.054577 | 0.044377 | -0.08103 | 1.0781 | 1.0408 | 0.99385 | 0.87355 | 121.8826 | 122.0745 | 121.5777 | 121.7076 | 122.0564 | 121.9581 | 122.0095 | 121.9415 | 122.044 | 122.0338 | 121.9084 | 1.101 | 1.0637 | 1.0167 | 0.89643 | 121.9055 | 122.0973 | 121.6005 | 121.7305 | -120.8045 | -120.4996 | -120.8887 | -120.5838
634.3125 | 123.1934 | -121.0693 | 2.0737 | 0.06691 | -0.031363 | 0.015472 | -0.047909 | 0.054577 | 0.048956 | -0.071874 | 1.7236 | 1.691 | 1.6394 | 1.5329 | 121.2416 | 121.4152 | 120.9184 | 121.0529 | 121.1362 | 121.038 | 121.0848 | 121.0214 | 121.1239 | 121.1183 | 120.9975 | 1.7465 | 1.7138 | 1.6623 | 1.5558 | 121.2645 | 121.4381 | 120.9413 | 121.0758 | -119.518 | -119.1947 | -119.6023 | -119.279
636.0625 | 123.1522 | -121.9711 | 1.2131 | 0.062332 | -0.026784 | 0.020051 | -0.043331 | 0.054577 | 0.053534 | -0.076452 | 1.0872 | 1.082 | 1.0213 | 0.89186 | 121.8688 | 122.0516 | 121.5593 | 121.6847 | 122.0335 | 121.9443 | 121.9912 | 121.9278 | 122.0257 | 122.0247 | 121.8947 | 1.1101 | 1.1049 | 1.0442 | 0.91475 | 121.8917 | 122.0745 | 121.5822 | 121.7076 | -120.7816 | -120.4721 | -120.8475 | -120.538
637.8125 | 123.1934 | -121.9162 | 1.2177 | 0.071489 | -0.026784 | 0.020051 | -0.043331 | 0.059155 | 0.048956 | -0.076452 | 1.1513 | 1.1095 | 1.0717 | 0.96055 | 121.8093 | 121.9966 | 121.509 | 121.6252 | 121.9877 | 121.8894 | 121.9363 | 121.8729 | 121.9754 | 121.9652 | 121.8397 | 1.1742 | 1.1323 | 1.0946 | 0.98344 | 121.8322 | 122.0195 | 121.5319 | 121.648 | -120.658 | -120.3577 | -120.7377 | -120.4373
639.5 | 123.1384 | -122.1085 | 1.0391 | 0.062332 | -0.026784 | 0.020051 | -0.047909 | 0.063733 | 0.048956 | -0.076452 | 0.9865 | 0.98124 | 0.91144 | 0.78655 | 121.965 | 122.1614 | 121.6692 | 121.7945 | 122.1708 | 122.0817 | 122.1285 | 122.0605 | 122.1722 | 122.1574 | 122.032 | 1.0094 | 1.0041 | 0.93433 | 0.80943 | 121.9879 | 122.1843 | 121.6921 | 121.8174 | -120.9785 | -120.6827 | -121.0536 | -120.7578
641.25 | 123.2483 | -120.9595 | 2.1286 | 0.062332 | -0.031363 | 0.020051 | -0.043331 | 0.054577 | 0.048956 | -0.076452 | 2.0945 | 2.0893 | 2.0285 | 1.8947 | 120.8388 | 121.0307 | 120.5429 | 120.6637 | 121.0218 | 120.9281 | 120.9795 | 120.9161 | 121.014 | 121.0084 | 120.883 | 2.1174 | 2.1122 | 2.0514 | 1.9176 | 120.8616 | 121.0535 | 120.5658 | 120.6866 | -118.7443 | -118.4484 | -118.8102 | -118.5144
643 | 123.1247 | -120.845 | 2.3117 | 0.062332 | -0.026784 | 0.024629 | -0.047909 | 0.059155 | 0.044377 | -0.076452 | 2.1174 | 2.1122 | 2.0514 | 1.9176 | 120.825 | 121.0078 | 120.5155 | 120.65 | 120.9074 | 120.8182 | 120.8697 | 120.7971 | 120.9042 | 120.8894 | 120.7686 | 2.1403 | 2.1351 | 2.0743 | 1.9405 | 120.8479 | 121.0307 | 120.5384 | 120.6729 | -118.7076 | -118.3981 | -118.7736 | -118.464
644.6719 | 123.2117 | -122.1497 | 0.96588 | 0.053175 | -0.035942 | 0.020051 | -0.047909 | 0.063733 | 0.048956 | -0.085608 | 0.90867 | 0.90798 | 0.84276 | 0.70412 | 122.0291 | 122.2347 | 121.7379 | 121.8541 | 122.2028 | 122.1137 | 122.1697 | 122.1017 | 122.2134 | 122.1986 | 122.0641 | 0.93155 | 0.93087 | 0.86565 | 0.72701 | 122.052 | 122.2576 | 121.7608 | 121.877 | -121.1204 | -120.8292 | -121.1863 | -120.8951
646.4219 | 123.1293 | -122.1359 | 1.0208 | 0.06691 | -0.031363 | 0.015472 | -0.043331 | 0.054577 | 0.039799 | -0.067295 | 0.92698 | 0.9034 | 0.85192 | 0.72702 | 122.0337 | 122.2118 | 121.7287 | 121.8495 | 122.2028 | 122.1046 | 122.1514 | 122.0926 | 122.1905 | 122.1757 | 122.0686 | 0.94987 | 0.92629 | 0.87481 | 0.74991 | 122.0565 | 122.2347 | 121.7516 | 121.8724 | -121.1067 | -120.8018 | -121.1817 | -120.8768
648.1875 | 123.2483 | -121.6324 | 1.4282 | 0.062332 | -0.031363 | 0.024629 | -0.043331 | 0.054577 | 0.044377 | -0.076452 | 1.3207 | 1.3063 | 1.2548 | 1.1346 | 121.6079 | 121.7952 | 121.3121 | 121.4375 | 121.6947 | 121.601 | 121.657 | 121.5891 | 121.687 | 121.6768 | 121.5559 | 1.3436 | 1.3292 | 1.2777 | 1.1574 | 121.6308 | 121.8181 | 121.335 | 121.4603 | -120.2872 | -119.9914 | -120.3531 | -120.0573
649.9375 | 123.1796 | -121.6278 | 1.4694 | 0.062332 | -0.035942 | 0.015472 | -0.052488 | 0.063733 | 0.048956 | -0.076452 | 1.3711 | 1.3521 | 1.3006 | 1.1666 | 121.5758 | 121.7631 | 121.2709 | 121.4008 | 121.6901 | 121.5919 | 121.6433 | 121.5753 | 121.6915 | 121.6768 | 121.5514 | 1.394 | 1.375 | 1.3235 | 1.1895 | 121.5987 | 121.786 | 121.2938 | 121.4237 | -120.2048 | -119.8998 | -120.2753 | -119.9703
651.6094 | 123.175 | -121.6461 | 1.4694 | 0.062332 | -0.035942 | 0.024629 | -0.043331 | 0.063733 | 0.044377 | -0.076452 | 1.7191 | 1.691 | 1.644 | 1.5192 | 121.2187 | 121.4061 | 120.9184 | 121.0529 | 121.7084 | 121.6102 | 121.6707 | 121.6028 | 121.7099 | 121.6905 | 121.5697 | 1.7419 | 1.7138 | 1.6668 | 1.5421 | 121.2416 | 121.4289 | 120.9413 | 121.0758 | -119.4997 | -119.1993 | -119.5748 | -119.2744
653.375 | 123.2025 | -121.6965 | 1.3641 | 0.062332 | -0.035942 | 0.020051 | -0.043331 | 0.063733 | 0.048956 | -0.071874 | 1.2429 | 1.2193 | 1.1541 | 1.043 | 121.6949 | 121.8776 | 121.3808 | 121.5153 | 121.7588 | 121.6605 | 121.7165 | 121.6531 | 121.7602 | 121.7454 | 121.6246 | 1.2658 | 1.2422 | 1.177 | 1.0659 | 121.7178 | 121.9005 | 121.4037 | 121.5382 | -120.452 | -120.1379 | -120.5408 | -120.2267
655.0625 | 123.0972 | -122.5479 | 0.52643 | 0.062332 | -0.0451 | 0.020051 | -0.043331 | 0.049999 | 0.053534 | -0.076452 | 0.51492 | 0.57831 | 0.49481 | 0.47975 | 122.6014 | 122.5735 | 122.3148 | 122.4263 | 122.6102 | 122.5028 | 122.568 | 122.5046 | 122.5979 | 122.6014 | 122.4715 | 0.5378 | 0.6012 | 0.5177 | 0.50264 | 122.6242 | 122.5964 | 122.3377 | 122.4492 | -122.0864 | -121.7999 | -122.1065 | -121.82
656.8125 | 123.1979 | -122.5204 | 0.56305 | 0.062332 | -0.031363 | 0.015472 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 0.51034 | 0.58289 | 0.49939 | 0.48433 | 122.6334 | 122.6009 | 122.3377 | 122.4446 | 122.5828 | 122.4891 | 122.5359 | 122.4725 | 122.575 | 122.5694 | 122.444 | 0.53323 | 0.60578 | 0.52228 | 0.50722 | 122.6563 | 122.6238 | 122.3606 | 122.4675 | -122.1231 | -121.8273 | -122.134 | -121.8383
658.5 | 123.1338 | -122.5616 | 0.54016 | 0.062332 | -0.040521 | 0.015472 | -0.043331 | 0.06831 | 0.044377 | -0.076452 | 0.50118 | 0.56457 | 0.48108 | 0.47975 | 122.6517 | 122.6192 | 122.1362 | 122.4721 | 122.624 | 122.5211 | 122.5771 | 122.5183 | 122.63 | 122.606 | 122.4852 | 0.52407 | 0.58746 | 0.50397 | 0.50264 | 122.6746 | 122.6421 | 122.1591 | 122.495 | -122.1505 | -121.635 | -122.1706 | -121.6551
660.25 | 123.0835 | -122.5662 | 0.54016 | 0.062332 | -0.040521 | 0.020051 | -0.043331 | 0.063733 | 0.048956 | -0.076452 | 0.46913 | 0.5371 | 0.39867 | 0.46143 | 122.5739 | 122.6559 | 122.1591 | 122.5042 | 122.6286 | 122.5257 | 122.5863 | 122.5229 | 122.63 | 122.6152 | 122.4898 | 0.49202 | 0.55999 | 0.42156 | 0.48432 | 122.5968 | 122.6788 | 122.182 | 122.5271 | -122.1048 | -121.69 | -122.1752 | -121.7604
662 | 123.0927 | -122.5891 | 0.53101 | 0.062332 | -0.035942 | 0.015472 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 0.47371 | 0.5371 | 0.39409 | 0.27827 | 122.4686 | 122.6513 | 122.1637 | 122.5087 | 122.6514 | 122.5532 | 122.6046 | 122.5458 | 122.6483 | 122.6426 | 122.5127 | 0.4966 | 0.55999 | 0.41698 | 0.30116 | 122.4915 | 122.6742 | 122.1866 | 122.5316 | -121.9949 | -121.69 | -122.0745 | -121.7696
663.6875 | 123.2712 | -122.5525 | 0.48065 | 0.06691 | -0.040521 | 0.020051 | -0.043331 | 0.054577 | 0.044377 | -0.071874 | 0.46913 | 0.53252 | 0.40325 | 0.28285 | 122.4594 | 122.665 | 122.1637 | 122.5225 | 122.6194 | 122.512 | 122.5725 | 122.5092 | 122.6071 | 122.5969 | 122.4806 | 0.49202 | 0.55541 | 0.42614 | 0.30574 | 122.4823 | 122.6879 | 122.1866 | 122.5454 | -121.9903 | -121.6946 | -122.0562 | -121.7604
665.4219 | 123.1888 | -122.5525 | 0.52643 | 0.057754 | -0.031363 | 0.010893 | -0.043331 | 0.059155 | 0.048956 | -0.076452 | 0.47829 | 0.55541 | 0.40783 | 0.29201 | 122.4503 | 122.6513 | 122.1591 | 122.5042 | 122.6102 | 122.5211 | 122.5634 | 122.5092 | 122.6116 | 122.6014 | 122.476 | 0.50118 | 0.5783 | 0.43071 | 0.3149 | 122.4732 | 122.6742 | 122.182 | 122.5271 | -121.972 | -121.6808 | -122.0424 | -121.7513
667.1875 | 123.2574 | -122.5296 | 0.52185 | 0.057754 | -0.040521 | 0.020051 | -0.052488 | 0.059155 | 0.044377 | -0.071874 | 0.47829 | 0.54626 | 0.40325 | 0.28285 | 122.464 | 122.6559 | 122.1591 | 122.5179 | 122.5874 | 122.4891 | 122.5497 | 122.4771 | 122.5888 | 122.574 | 122.4577 | 0.50118 | 0.56915 | 0.42614 | 0.30574 | 122.4869 | 122.6788 | 122.182 | 122.5408 | -121.9857 | -121.6808 | -122.0608 | -121.7559
668.9219 | 123.1338 | -122.5708 | 0.5722 | 0.062332 | -0.026784 | 0.015472 | -0.047909 | 0.063733 | 0.048956 | -0.08103 | 0.48745 | 0.55999 | 0.41698 | 0.30117 | 122.4411 | 122.6467 | 122.1545 | 122.2798 | 122.6331 | 122.544 | 122.5863 | 122.5229 | 122.6345 | 122.6198 | 122.4898 | 0.51033 | 0.58288 | 0.43987 | 0.32406 | 122.464 | 122.6696 | 122.1774 | 122.3027 | -121.9537 | -121.6671 | -122.0241 | -121.7375
670.5938 | 123.1247 | -122.5983 | 0.54474 | 0.057754 | -0.035942 | 0.015472 | -0.038752 | 0.054577 | 0.039799 | -0.071874 | 0.51034 | 0.57373 | 0.42614 | 0.31033 | 122.432 | 122.633 | 122.1408 | 122.2569 | 122.656 | 122.5623 | 122.6137 | 122.5595 | 122.6528 | 122.6381 | 122.5264 | 0.53323 | 0.59662 | 0.44903 | 0.33321 | 122.4548 | 122.6559 | 122.1637 | 122.2798 | -121.9216 | -121.6305 | -122.0058 | -121.7147
672.3594 | 123.1567 | -122.4747 | 0.63171 | 0.062332 | -0.031363 | 0.015472 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 0.48745 | 0.55541 | 0.41698 | 0.29659 | 122.464 | 122.6467 | 122.1545 | 122.2844 | 122.537 | 122.4433 | 122.4901 | 122.4268 | 122.5338 | 122.5236 | 122.3982 | 0.51033 | 0.5783 | 0.43987 | 0.31948 | 122.4869 | 122.6696 | 122.1774 | 122.3073 | -121.9766 | -121.6671 | -122.047 | -121.7375
674.0469 | 123.2162 | -122.5937 | 0.50812 | 0.062332 | -0.031363 | 0.010893 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 0.4966 | 0.56457 | 0.42156 | 0.30117 | 122.4457 | 122.6421 | 122.15 | 122.2753 | 122.656 | 122.5623 | 122.6046 | 122.5504 | 122.6483 | 122.6426 | 122.5127 | 0.51949 | 0.58746 | 0.44445 | 0.32406 | 122.4686 | 122.665 | 122.1728 | 122.2981 | -121.9491 | -121.6534 | -122.0241 | -121.7284
675.7812 | 123.1293 | -122.525 | 0.61798 | 0.062332 | -0.031363 | 0.024629 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 0.51492 | 0.59205 | 0.45361 | 0.32864 | 122.4274 | 122.6147 | 122.1225 | 122.2569 | 122.5874 | 122.4937 | 122.5497 | 122.4817 | 122.5842 | 122.5786 | 122.4486 | 0.5378 | 0.61493 | 0.4765 | 0.35153 | 122.4503 | 122.6376 | 122.1454 | 122.2798 | -121.9125 | -121.6076 | -121.9738 | -121.6689
677.5469 | 123.2712 | -122.5067 | 0.54016 | 0.062332 | -0.035942 | 0.015472 | -0.043331 | 0.059155 | 0.044377 | -0.076452 | 0.51034 | 0.58747 | 0.44445 | 0.31033 | 122.432 | 122.6284 | 122.1271 | 122.2524 | 122.569 | 122.4708 | 122.5222 | 122.4634 | 122.5659 | 122.5511 | 122.4303 | 0.53323 | 0.61035 | 0.46734 | 0.33321 | 122.4548 | 122.6513 | 122.1499 | 122.2753 | -121.9216 | -121.6167 | -121.9875 | -121.6826
679.2969 | 123.2208 | -122.2412 | 0.87891 | 0.053175 | -0.026784 | 0.015472 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 0.77131 | 0.83472 | 0.69168 | 0.57133 | 122.171 | 122.372 | 121.8798 | 122.0051 | 122.2944 | 122.2144 | 122.2567 | 122.1979 | 122.2958 | 122.2902 | 122.1602 | 0.7942 | 0.85761 | 0.71457 | 0.59422 | 122.1939 | 122.3949 | 121.9027 | 122.028 | -121.3997 | -121.1085 | -121.4793 | -121.1881
681.0625 | 123.2529 | -122.2549 | 0.82855 | 0.062332 | -0.026784 | 0.015472 | -0.052488 | 0.054577 | 0.048956 | -0.076452 | 0.77589 | 0.77062 | 0.70084 | 0.57591 | 122.1664 | 122.3629 | 121.8707 | 122.0006 | 122.3173 | 122.2282 | 122.2704 | 122.2025 | 122.3095 | 122.3039 | 122.1785 | 0.79878 | 0.79351 | 0.72372 | 0.5988 | 122.1893 | 122.3858 | 121.8936 | 122.0235 | -121.3905 | -121.0948 | -121.4656 | -121.1698
682.8125 | 123.1064 | -122.0764 | 1.03 | 0.06691 | -0.022205 | 0.029208 | -0.038752 | 0.054577 | 0.053534 | -0.071874 | 1.0781 | 1.114 | 1.0442 | 0.96513 | 121.965 | 122.0516 | 121.6692 | 121.7854 | 122.1433 | 122.0542 | 122.1056 | 122.0377 | 122.131 | 122.1299 | 122.0045 | 1.101 | 1.1369 | 1.0671 | 0.98802 | 121.9879 | 122.0745 | 121.6921 | 121.8083 | -120.8869 | -120.5912 | -120.9208 | -120.625
684.5 | 123.1293 | -120.8679 | 2.243 | 0.06691 | -0.031363 | 0.020051 | -0.043331 | 0.054577 | 0.048956 | -0.076452 | 2.1403 | 2.1305 | 2.0697 | 1.9313 | 120.8708 | 120.9895 | 120.52 | 120.65 | 120.9348 | 120.8366 | 120.888 | 120.8246 | 120.9225 | 120.9169 | 120.7915 | 2.1632 | 2.1534 | 2.0926 | 1.9542 | 120.8937 | 121.0123 | 120.5429 | 120.6729 | -118.7305 | -118.3798 | -118.8011 | -118.4503
686.2344 | 123.2162 | -122.2321 | 0.86975 | 0.06691 | -0.026784 | 0.015472 | -0.052488 | 0.054577 | 0.044377 | -0.071874 | 0.80336 | 0.79809 | 0.72831 | 0.59423 | 122.1435 | 122.3354 | 121.8524 | 121.9731 | 122.299 | 122.2053 | 122.2475 | 122.1796 | 122.2866 | 122.2764 | 122.1602 | 0.82625 | 0.82098 | 0.75119 | 0.61711 | 122.1664 | 122.3583 | 121.8752 | 121.996 | -121.3402 | -121.049 | -121.4152 | -121.1241
687.9844 | 123.2254 | -122.2641 | 0.81024 | 0.062332 | -0.026784 | 0.010893 | -0.047909 | 0.059155 | 0.048956 | -0.08103 | 0.71179 | 0.71109 | 0.64132 | 0.50265 | 122.2397 | 122.4361 | 121.9348 | 122.0647 | 122.3264 | 122.2373 | 122.275 | 122.2162 | 122.3233 | 122.3131 | 122.1831 | 0.73468 | 0.73398 | 0.66421 | 0.52553 | 122.2626 | 122.459 | 121.9577 | 122.0875 | -121.5279 | -121.223 | -121.5984 | -121.2935
689.6562 | 123.2346 | -122.3511 | 0.74616 | 0.057754 | -0.026784 | 0.020051 | -0.047909 | 0.059155 | 0.044377 | -0.08103 | 0.69806 | 0.69736 | 0.62758 | 0.49807 | 122.2397 | 122.4453 | 121.9485 | 122.0784 | 122.4088 | 122.3243 | 122.3711 | 122.3032 | 122.4102 | 122.3955 | 122.27 | 0.72094 | 0.72025 | 0.65047 | 0.52095 | 122.2626 | 122.4682 | 121.9714 | 122.1013 | -121.5416 | -121.2504 | -121.6121 | -121.3209
691.4062 | 123.1247 | -121.8018 | 1.3367 | 0.06691 | -0.022205 | 0.024629 | -0.047909 | 0.063733 | 0.053534 | -0.076452 | 1.2658 | 1.2606 | 1.1999 | 1.0704 | 121.6674 | 121.8593 | 121.3716 | 121.497 | 121.8687 | 121.7796 | 121.8264 | 121.7538 | 121.8655 | 121.8553 | 121.7253 | 1.2887 | 1.2834 | 1.2228 | 1.0933 | 121.6903 | 121.8822 | 121.3945 | 121.5199 | -120.4016 | -120.1058 | -120.4675 | -120.1718
693.1094 | 123.2391 | -120.4468 | 2.5864 | 0.062332 | -0.022205 | 0.010893 | -0.047909 | 0.054577 | 0.053534 | -0.08103 | 1.9159 | 1.865 | 1.8179 | 1.7161 | 121.0265 | 121.2046 | 120.7215 | 120.8606 | 120.5091 | 120.4246 | 120.4577 | 120.3989 | 120.5014 | 120.5003 | 120.3657 | 1.9388 | 1.8878 | 1.8408 | 1.739 | 121.0494 | 121.2275 | 120.7444 | 120.8835 | -119.1105 | -118.8056 | -119.2085 | -118.9036
694.8438 | 123.1796 | -121.7056 | 1.3962 | 0.062332 | -0.022205 | 0.015472 | -0.047909 | 0.063733 | 0.053534 | -0.067295 | 1.3116 | 1.2926 | 1.2457 | 1.1117 | 121.6308 | 121.8181 | 121.335 | 121.4695 | 121.768 | 121.6834 | 121.7211 | 121.6577 | 121.7694 | 121.7592 | 121.6383 | 1.3345 | 1.3155 | 1.2685 | 1.1345 | 121.6537 | 121.841 | 121.3579 | 121.4924 | -120.3192 | -120.0234 | -120.3851 | -120.0893
696.5938 | 123.1155 | -120.9366 | 2.1835 | 0.06691 | -0.031363 | 0.020051 | -0.043331 | 0.054577 | 0.053534 | -0.067295 | 2.0441 | 2.039 | 1.9782 | 1.8443 | 120.9029 | 121.081 | 120.5887 | 120.7278 | 121.0035 | 120.9052 | 120.9566 | 120.8933 | 120.9912 | 120.9901 | 120.8693 | 2.067 | 2.0618 | 2.0011 | 1.8672 | 120.9257 | 121.1039 | 120.6116 | 120.7507 | -118.8587 | -118.5446 | -118.9247 | -118.6105
698.3594 | 123.1384 | -121.994 | 1.1398 | 0.057754 | -0.026784 | 0.010893 | -0.052488 | 0.059155 | 0.048956 | -0.067295 | 1.0781 | 1.0728 | 1.003 | 0.87813 | 121.8551 | 122.0561 | 121.5639 | 121.6893 | 122.0518 | 121.9672 | 122.0049 | 121.9415 | 122.0532 | 122.043 | 121.9267 | 1.101 | 1.0957 | 1.0259 | 0.90101 | 121.878 | 122.079 | 121.5868 | 121.7121 | -120.777 | -120.4858 | -120.8521 | -120.5609
700.0625 | 123.2071 | -122.1313 | 0.90637 | 0.057754 | -0.026784 | 0.020051 | -0.043331 | 0.059155 | 0.044377 | -0.076452 | 0.89493 | 0.89425 | 0.82445 | 0.69039 | 122.0291 | 122.2393 | 121.7379 | 121.8678 | 122.1891 | 122.1046 | 122.1514 | 122.088 | 122.1905 | 122.1757 | 122.0549 | 0.91782 | 0.91714 | 0.84734 | 0.71327 | 122.052 | 122.2622 | 121.7608 | 121.8907 | -121.1342 | -120.843 | -121.2046 | -120.9134
701.7969 | 123.1796 | -122.1817 | 0.90637 | 0.06691 | -0.026784 | 0.010893 | -0.047909 | 0.059155 | 0.053534 | -0.076452 | 0.88119 | 0.88967 | 0.81071 | 0.68123 | 122.0566 | 122.2438 | 121.7516 | 121.877 | 122.2486 | 122.1549 | 122.1926 | 122.1338 | 122.2409 | 122.2352 | 122.1052 | 0.90408 | 0.91256 | 0.8336 | 0.70412 | 122.0794 | 122.2667 | 121.7745 | 121.8998 | -121.1754 | -120.8704 | -121.2458 | -120.9409
703.5469 | 123.1293 | -122.3465 | 0.80566 | 0.06691 | -0.026784 | 0.010893 | -0.043331 | 0.059155 | 0.053534 | -0.071874 | 0.72095 | 0.72941 | 0.65963 | 0.53012 | 122.2214 | 122.4041 | 121.9256 | 122.0509 | 122.4134 | 122.3197 | 122.3574 | 122.3032 | 122.4057 | 122.4 | 122.2746 | 0.74384 | 0.7523 | 0.68252 | 0.55301 | 122.2443 | 122.427 | 121.9485 | 122.0738 | -121.5004 | -121.2047 | -121.5617 | -121.266
705.2969 | 123.2712 | -122.0764 | 0.97504 | 0.062332 | -0.035942 | 0.020051 | -0.043331 | 0.054577 | 0.048956 | -0.08103 | 0.94987 | 0.95835 | 0.88397 | 0.74991 | 121.9787 | 122.1798 | 121.6921 | 121.8083 | 122.1387 | 122.0405 | 122.0965 | 122.0331 | 122.131 | 122.1254 | 121.9954 | 0.97276 | 0.98124 | 0.90685 | 0.7728 | 122.0016 | 122.2026 | 121.715 | 121.8312 | -121.0289 | -120.7422 | -121.0948 | -120.8081
707.0469 | 123.2666 | -121.9025 | 1.149 | 0.062332 | -0.031363 | 0.015472 | -0.043331 | 0.054577 | 0.058113 | -0.071874 | 1.1651 | 1.169 | 1.0946 | 0.96513 | 121.7681 | 121.96 | 121.4678 | 121.5885 | 121.9648 | 121.8711 | 121.9179 | 121.8591 | 121.957 | 121.9606 | 121.8306 | 1.188 | 1.1919 | 1.1175 | 0.98802 | 121.791 | 121.9829 | 121.4907 | 121.6114 | -120.6031 | -120.3027 | -120.6736 | -120.3732
708.7812 | 123.1659 | -121.7789 | 1.3092 | 0.057754 | -0.035942 | 0.024629 | -0.052488 | 0.063733 | 0.048956 | -0.076452 | 1.2383 | 1.2331 | 1.1632 | 1.043 | 121.704 | 121.8868 | 121.3991 | 121.5199 | 121.8366 | 121.7429 | 121.8035 | 121.7264 | 121.8426 | 121.8278 | 121.7024 | 1.2612 | 1.256 | 1.1861 | 1.0659 | 121.7269 | 121.9096 | 121.422 | 121.5427 | -120.4657 | -120.1608 | -120.5408 | -120.2359
710.4688 | 123.1567 | -121.2479 | 1.8723 | 0.06691 | -0.031363 | 0.015472 | -0.047909 | 0.06831 | 0.053534 | -0.067295 | 1.7694 | 1.7688 | 1.7035 | 1.5696 | 121.1592 | 121.3511 | 120.8634 | 120.9979 | 121.3148 | 121.2165 | 121.2633 | 121.2 | 121.3162 | 121.3014 | 121.1806 | 1.7923 | 1.7917 | 1.7264 | 1.5924 | 121.1821 | 121.374 | 120.8863 | 121.0208 | -119.3898 | -119.094 | -119.4558 | -119.1599
712.2188 | 123.1842 | -121.6736 | 1.4008 | 0.057754 | -0.035942 | 0.020051 | -0.043331 | 0.059155 | 0.048956 | -0.076452 | 1.5176 | 1.5124 | 1.4563 | 1.3223 | 121.4065 | 121.5983 | 121.1015 | 121.2314 | 121.7313 | 121.6376 | 121.6936 | 121.6303 | 121.7327 | 121.7225 | 121.5971 | 1.5405 | 1.5353 | 1.4791 | 1.3452 | 121.4293 | 121.6212 | 121.1244 | 121.2543 | -119.8888 | -119.5839 | -119.9502 | -119.6452
713.9688 | 123.1476 | -121.582 | 1.5244 | 0.06691 | -0.022205 | 0.020051 | -0.043331 | 0.059155 | 0.058113 | -0.076452 | 1.4901 | 1.4895 | 1.415 | 1.2857 | 121.4339 | 121.635 | 121.1381 | 121.2726 | 121.6489 | 121.5598 | 121.6021 | 121.5387 | 121.6412 | 121.6401 | 121.5056 | 1.513 | 1.5124 | 1.4379 | 1.3085 | 121.4568 | 121.6579 | 121.161 | 121.2955 | -119.9438 | -119.648 | -120.0189 | -119.7231
715.6406 | 123.2208 | -121.8109 | 1.2177 | 0.062332 | -0.031363 | 0.020051 | -0.047909 | 0.059155 | 0.053534 | -0.08103 | 1.0872 | 1.0774 | 1.0213 | 0.87813 | 121.8322 | 122.0424 | 121.541 | 121.6755 | 121.8732 | 121.7796 | 121.831 | 121.763 | 121.8701 | 121.8644 | 121.7299 | 1.1101 | 1.1003 | 1.0442 | 0.90101 | 121.8551 | 122.0653 | 121.5639 | 121.6984 | -120.745 | -120.4538 | -120.8109 | -120.5197
717.3906 | 123.1338 | -121.7697 | 1.3321 | 0.062332 | -0.040521 | 0.010893 | -0.043331 | 0.054577 | 0.048956 | -0.067295 | 1.2887 | 1.2606 | 1.2044 | 1.0888 | 121.6399 | 121.8318 | 121.3396 | 121.4649 | 121.832 | 121.7292 | 121.7806 | 121.7264 | 121.8243 | 121.8187 | 121.7024 | 1.3116 | 1.2834 | 1.2273 | 1.1117 | 121.6628 | 121.8547 | 121.3625 | 121.4878 | -120.3513 | -120.0509 | -120.4355 | -120.1351
719.0781 | 123.1979 | -121.9116 | 1.1215 | 0.062332 | -0.031363 | 0.020051 | -0.038752 | 0.063733 | 0.048956 | -0.08103 | 1.0689 | 1.0774 | 1.003 | 0.86439 | 121.8551 | 122.0516 | 121.5548 | 121.6938 | 121.974 | 121.8803 | 121.9317 | 121.8729 | 121.9754 | 121.9606 | 121.8306 | 1.0918 | 1.1003 | 1.0259 | 0.88728 | 121.878 | 122.0745 | 121.5776 | 121.7167 | -120.7862 | -120.4858 | -120.8521 | -120.5518
720.8125 | 123.1842 | -121.9986 | 1.0483 | 0.057754 | -0.0451 | 0.015472 | -0.034174 | 0.063733 | 0.053534 | -0.071874 | 0.9865 | 0.97667 | 0.91144 | 0.78197 | 121.9467 | 122.1385 | 121.6463 | 121.7671 | 122.0564 | 121.9535 | 122.0141 | 121.9644 | 122.0623 | 122.0521 | 121.9267 | 1.0094 | 0.99955 | 0.93433 | 0.80485 | 121.9696 | 122.1614 | 121.6692 | 121.79 | -120.9602 | -120.6598 | -121.0352 | -120.7349
722.5 | 123.1201 | -121.9482 | 1.149 | 0.057754 | -0.040521 | 0.024629 | -0.043331 | 0.06831 | 0.058113 | -0.076452 | 1.0598 | 1.0453 | 0.98469 | 0.85523 | 121.8688 | 122.0653 | 121.5777 | 121.6984 | 122.006 | 121.9077 | 121.9729 | 121.9049 | 122.0166 | 122.0064 | 121.8718 | 1.0826 | 1.0682 | 1.0076 | 0.87812 | 121.8917 | 122.0882 | 121.6005 | 121.7213 | -120.8091 | -120.5179 | -120.8842 | -120.593
724.2656 | 123.1201 | -121.9025 | 1.2131 | 0.053175 | -0.035942 | 0.015472 | -0.047909 | 0.054577 | 0.044377 | -0.071874 | 1.1605 | 1.1644 | 1.0991 | 0.95597 | 121.7727 | 121.9554 | 121.4678 | 121.6068 | 121.9556 | 121.8665 | 121.9179 | 121.8546 | 121.957 | 121.9468 | 121.8306 | 1.1834 | 1.1873 | 1.122 | 0.97886 | 121.7956 | 121.9783 | 121.4907 | 121.6297 | -120.6122 | -120.3073 | -120.6736 | -120.3686
725.9531 | 123.2346 | -122.3053 | 0.74616 | 0.062332 | -0.035942 | 0.010893 | -0.043331 | 0.054577 | 0.048956 | -0.071874 | 0.70263 | 0.70652 | 0.64132 | 0.50723 | 122.2168 | 122.4087 | 121.9256 | 122.0555 | 122.3676 | 122.2694 | 122.3162 | 122.262 | 122.3599 | 122.3543 | 122.2334 | 0.72552 | 0.7294 | 0.66421 | 0.53011 | 122.2397 | 122.4315 | 121.9485 | 122.0784 | -121.5142 | -121.223 | -121.5755 | -121.2843
727.6875 | 123.2162 | -122.3373 | 0.70496 | 0.057754 | -0.040521 | 0.015472 | -0.047909 | 0.063733 | 0.044377 | -0.076452 | 0.67974 | 0.67904 | 0.60011 | 0.48433 | 122.2351 | 122.4361 | 121.9439 | 122.0738 | 122.3951 | 122.2968 | 122.3528 | 122.2894 | 122.4011 | 122.3817 | 122.2609 | 0.70263 | 0.70193 | 0.623 | 0.50722 | 122.258 | 122.459 | 121.9668 | 122.0967 | -121.5554 | -121.2642 | -121.635 | -121.3438
729.4531 | 123.1796 | -122.2916 | 0.75989 | 0.057754 | -0.040521 | 0.015472 | -0.047909 | 0.054577 | 0.053534 | -0.08103 | 0.83541 | 0.8393 | 0.76493 | 0.63086 | 122.084 | 122.2805 | 121.7883 | 121.9182 | 122.3493 | 122.251 | 122.307 | 122.2437 | 122.3461 | 122.3451 | 122.2105 | 0.8583 | 0.86219 | 0.78782 | 0.65375 | 122.1069 | 122.3034 | 121.8111 | 121.941 | -121.2486 | -120.9528 | -121.3191 | -121.0233
731.1875 | 123.2254 | -122.113 | 0.89264 | 0.057754 | -0.040521 | 0.015472 | -0.038752 | 0.063733 | 0.053534 | -0.076452 | 0.87204 | 0.87593 | 0.80614 | 0.66291 | 122.052 | 122.2484 | 121.7516 | 121.877 | 122.1708 | 122.0725 | 122.1285 | 122.0743 | 122.1768 | 122.1666 | 122.0366 | 0.89493 | 0.89882 | 0.82902 | 0.6858 | 122.0749 | 122.2713 | 121.7745 | 121.8998 | -121.1799 | -120.8796 | -121.2458 | -120.9455
732.875 | 123.23 | -122.0993 | 0.90637 | 0.062332 | -0.040521 | 0.006315 | -0.047909 | 0.059155 | 0.048956 | -0.08103 | 0.90409 | 0.9034 | 0.83818 | 0.70412 | 122.0153 | 122.2164 | 121.715 | 121.8449 | 122.1616 | 122.0588 | 122.1056 | 122.0514 | 122.1585 | 122.1483 | 122.0183 | 0.92698 | 0.92629 | 0.86107 | 0.72701 | 122.0382 | 122.2393 | 121.7379 | 121.8678 | -121.1113 | -120.8109 | -121.1772 | -120.8768
734.625 | 123.0927 | -122.2549 | 0.84686 | 0.06691 | -0.0451 | 0.020051 | -0.043331 | 0.063733 | 0.058113 | -0.071874 | 0.77131 | 0.77062 | 0.70541 | 0.57591 | 122.1527 | 122.3446 | 121.8478 | 121.9777 | 122.3219 | 122.2098 | 122.275 | 122.2116 | 122.3187 | 122.3131 | 122.1831 | 0.7942 | 0.79351 | 0.7283 | 0.5988 | 122.1756 | 122.3675 | 121.8707 | 122.0006 | -121.3814 | -121.0765 | -121.4473 | -121.1424
736.375 | 123.1018 | -122.2321 | 0.87433 | 0.057754 | -0.049678 | 0.015472 | -0.047909 | 0.06831 | 0.048956 | -0.076452 | 0.80794 | 0.80725 | 0.74204 | 0.60796 | 122.1206 | 122.3079 | 121.8157 | 121.9502 | 122.2898 | 122.1824 | 122.2475 | 122.1841 | 122.3004 | 122.281 | 122.1556 | 0.83083 | 0.83014 | 0.76493 | 0.63085 | 122.1435 | 122.3308 | 121.8386 | 121.9731 | -121.3127 | -121.0078 | -121.3786 | -121.0737
738.0625 | 123.0972 | -122.2229 | 0.86975 | 0.062332 | -0.040521 | 0.015472 | -0.043331 | 0.059155 | 0.053534 | -0.071874 | 0.80794 | 0.81641 | 0.74662 | 0.60796 | 122.1115 | 122.3034 | 121.8066 | 121.9273 | 122.2852 | 122.1824 | 122.2384 | 122.1796 | 122.2821 | 122.2764 | 122.151 | 0.83083 | 0.8393 | 0.76951 | 0.63085 | 122.1344 | 122.3262 | 121.8295 | 121.9502 | -121.3036 | -120.9986 | -121.3649 | -121.06
739.8125 | 123.1155 | -122.2733 | 0.83313 | 0.06691 | -0.049678 | 0.015472 | -0.043331 | 0.059155 | 0.053534 | -0.067295 | 0.75758 | 0.76604 | 0.69168 | 0.56675 | 122.1619 | 122.3537 | 121.8615 | 121.9868 | 122.3402 | 122.2236 | 122.2887 | 122.2299 | 122.3324 | 122.3268 | 122.206 | 0.78046 | 0.78893 | 0.71457 | 0.58964 | 122.1847 | 122.3766 | 121.8844 | 122.0097 | -121.4043 | -121.1039 | -121.4702 | -121.1698
741.5156 | 123.1018 | -122.3282 | 0.79193 | 0.057754 | -0.040521 | 0.015472 | -0.047909 | 0.054577 | 0.053534 | -0.076452 | 0.72095 | 0.71567 | 0.65048 | 0.51638 | 122.2122 | 122.3949 | 121.9073 | 122.0326 | 122.3859 | 122.2877 | 122.3437 | 122.2803 | 122.3828 | 122.3817 | 122.2517 | 0.74384 | 0.73856 | 0.67336 | 0.53927 | 122.2351 | 122.4178 | 121.9302 | 122.0555 | -121.4913 | -121.1863 | -121.5617 | -121.2568
743.2812 | 123.1796 | -122.3465 | 0.6958 | 0.053175 | -0.049678 | 0.020051 | -0.034174 | 0.059155 | 0.044377 | -0.076452 | 0.67058 | 0.67446 | 0.59554 | 0.46143 | 122.2534 | 122.4453 | 121.9531 | 122.0738 | 122.3997 | 122.2968 | 122.3665 | 122.3123 | 122.4057 | 122.3909 | 122.27 | 0.69347 | 0.69735 | 0.61842 | 0.48432 | 122.2763 | 122.4682 | 121.976 | 122.0967 | -121.5828 | -121.2825 | -121.6579 | -121.3575
745.0781 | 123.1842 | -122.3145 | 0.71869 | 0.06691 | -0.058836 | 0.020051 | -0.043331 | 0.059155 | 0.048956 | -0.08103 | 0.6889 | 0.6882 | 0.62301 | 0.48433 | 122.2259 | 122.4178 | 121.9256 | 122.0601 | 122.3814 | 122.2556 | 122.3345 | 122.2711 | 122.3736 | 122.3634 | 122.2334 | 0.71179 | 0.71109 | 0.64589 | 0.50722 | 122.2488 | 122.4407 | 121.9485 | 122.083 | -121.537 | -121.2367 | -121.6029 | -121.3026
746.8281 | 123.1247 | -122.3145 | 0.76446 | 0.06691 | -0.049678 | 0.010893 | -0.047909 | 0.059155 | 0.053534 | -0.076452 | 0.70721 | 0.71567 | 0.62758 | 0.50723 | 122.2122 | 122.3995 | 121.9073 | 122.0418 | 122.3814 | 122.2648 | 122.3253 | 122.2665 | 122.3736 | 122.368 | 122.238 | 0.7301 | 0.73856 | 0.65047 | 0.53011 | 122.2351 | 122.4224 | 121.9302 | 122.0647 | -121.505 | -121.2001 | -121.5846 | -121.2797
748.5938 | 123.1384 | -122.2687 | 0.80109 | 0.057754 | -0.063415 | 0.010893 | -0.043331 | 0.054577 | 0.058113 | -0.076452 | 0.77131 | 0.77062 | 0.70084 | 0.56675 | 122.1481 | 122.3354 | 121.8432 | 121.9685 | 122.3264 | 122.2053 | 122.2796 | 122.2253 | 122.3233 | 122.3268 | 122.1922 | 0.7942 | 0.79351 | 0.72372 | 0.58964 | 122.171 | 122.3583 | 121.8661 | 121.9914 | -121.3768 | -121.0719 | -121.4473 | -121.1424
750.2812 | 123.0835 | -122.3419 | 0.75073 | 0.06691 | -0.049678 | 0.020051 | -0.047909 | 0.063733 | 0.058113 | -0.076452 | 0.70263 | 0.71109 | 0.6459 | 0.5118 | 122.2168 | 122.3903 | 121.9119 | 122.0418 | 122.4088 | 122.2922 | 122.362 | 122.294 | 122.4057 | 122.4 | 122.2655 | 0.72552 | 0.73398 | 0.66878 | 0.53469 | 122.2397 | 122.4132 | 121.9348 | 122.0647 | -121.5142 | -121.2092 | -121.5709 | -121.266
752.0312 | 123.0698 | -122.2549 | 0.85602 | 0.06691 | -0.054257 | 0.020051 | -0.043331 | 0.054577 | 0.048956 | -0.071874 | 0.77589 | 0.77978 | 0.70999 | 0.58049 | 122.1344 | 122.3263 | 121.8295 | 121.9639 | 122.3219 | 122.2007 | 122.275 | 122.2116 | 122.3095 | 122.3039 | 122.1831 | 0.79878 | 0.80266 | 0.73288 | 0.60338 | 122.1573 | 122.3491 | 121.8524 | 121.9868 | -121.3585 | -121.0536 | -121.4244 | -121.1195
753.7812 | 123.1064 | -121.9574 | 1.1078 | 0.062332 | -0.054257 | 0.015472 | -0.038752 | 0.059155 | 0.058113 | -0.08103 | 1.014 | 1.0133 | 0.94349 | 0.80944 | 121.9055 | 122.0928 | 121.6005 | 121.7305 | 122.0197 | 121.9031 | 121.9729 | 121.9186 | 122.0166 | 122.0155 | 121.8764 | 1.0369 | 1.0362 | 0.96637 | 0.83233 | 121.9284 | 122.1157 | 121.6234 | 121.7533 | -120.8915 | -120.5866 | -120.962 | -120.6571
755.4688 | 123.1201 | -122.1863 | 0.88806 | 0.062332 | -0.058836 | 0.020051 | -0.047909 | 0.054577 | 0.058113 | -0.076452 | 0.82168 | 0.83014 | 0.74662 | 0.63086 | 122.1023 | 122.285 | 121.7928 | 121.9273 | 122.2486 | 122.1274 | 122.2063 | 122.1384 | 122.2409 | 122.2444 | 122.1098 | 0.84456 | 0.85303 | 0.76951 | 0.65375 | 122.1252 | 122.3079 | 121.8157 | 121.9502 | -121.2807 | -120.9712 | -121.3557 | -121.0462
757.1719 | 123.1201 | -122.1725 | 0.94299 | 0.062332 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.044377 | -0.071874 | 0.8583 | 0.8622 | 0.78782 | 0.66291 | 122.0566 | 122.2484 | 121.7516 | 121.8907 | 122.2349 | 122.1091 | 122.188 | 122.1292 | 122.2317 | 122.2169 | 122.1007 | 0.88119 | 0.88508 | 0.81071 | 0.6858 | 122.0794 | 122.2713 | 121.7745 | 121.9136 | -121.1982 | -120.8933 | -121.2687 | -120.9638
758.9219 | 123.0743 | -122.168 | 0.93384 | 0.062332 | -0.054257 | 0.020051 | -0.047909 | 0.059155 | 0.058113 | -0.08103 | 0.86288 | 0.85304 | 0.7924 | 0.65833 | 122.0657 | 122.2438 | 121.7562 | 121.8907 | 122.2303 | 122.1137 | 122.188 | 122.1201 | 122.2271 | 122.2261 | 122.0869 | 0.88577 | 0.87593 | 0.81529 | 0.68122 | 122.0886 | 122.2667 | 121.7791 | 121.9136 | -121.2028 | -120.8933 | -121.2733 | -120.9638
760.6719 | 123.1522 | -122.1634 | 0.86517 | 0.062332 | -0.063415 | 0.010893 | -0.043331 | 0.054577 | 0.048956 | -0.067295 | 0.8171 | 0.82556 | 0.74204 | 0.60796 | 122.0886 | 122.2805 | 121.7883 | 121.9182 | 122.2257 | 122.1 | 122.1743 | 122.1201 | 122.218 | 122.2123 | 122.0961 | 0.83998 | 0.84845 | 0.76493 | 0.63085 | 122.1115 | 122.3034 | 121.8111 | 121.941 | -121.2715 | -120.9712 | -121.3466 | -121.0462
762.3594 | 123.0881 | -122.2412 | 0.83771 | 0.062332 | -0.058836 | 0.015472 | -0.038752 | 0.054577 | 0.048956 | -0.08103 | 0.77589 | 0.77978 | 0.70541 | 0.56675 | 122.1252 | 122.3171 | 121.834 | 121.9456 | 122.3035 | 122.1824 | 122.2567 | 122.2025 | 122.2958 | 122.2902 | 122.1602 | 0.79878 | 0.80266 | 0.7283 | 0.58964 | 122.1481 | 122.34 | 121.8569 | 121.9685 | -121.3493 | -121.0582 | -121.4198 | -121.1286
764.1094 | 123.1155 | -122.2778 | 0.81482 | 0.062332 | -0.058836 | 0.015472 | -0.043331 | 0.054577 | 0.048956 | -0.071874 | 0.73926 | 0.7523 | 0.67337 | 0.54386 | 122.1619 | 122.3491 | 121.8615 | 121.9868 | 122.3402 | 122.219 | 122.2933 | 122.2345 | 122.3324 | 122.3268 | 122.206 | 0.76215 | 0.77519 | 0.69625 | 0.56675 | 122.1847 | 122.372 | 121.8844 | 122.0097 | -121.4226 | -121.1223 | -121.4885 | -121.1881
765.7812 | 123.1293 | -122.2687 | 0.80109 | 0.062332 | -0.0451 | 0.020051 | -0.038752 | 0.059155 | 0.048956 | -0.08103 | 0.73468 | 0.73857 | 0.66421 | 0.5347 | 122.171 | 122.3675 | 121.8752 | 122.0006 | 122.331 | 122.2236 | 122.2887 | 122.2299 | 122.3278 | 122.3176 | 122.1876 | 0.75757 | 0.76145 | 0.6871 | 0.55759 | 122.1939 | 122.3903 | 121.8981 | 122.0235 | -121.4363 | -121.1406 | -121.5068 | -121.211
767.5312 | 123.2117 | -122.1451 | 0.85144 | 0.062332 | -0.054257 | 0.010893 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 0.83541 | 0.83472 | 0.76035 | 0.62628 | 122.0657 | 122.2622 | 121.7699 | 121.8953 | 122.2074 | 122.0908 | 122.156 | 122.0972 | 122.1997 | 122.194 | 122.0686 | 0.8583 | 0.85761 | 0.78324 | 0.64917 | 122.0886 | 122.285 | 121.7928 | 121.9182 | -121.2303 | -120.9345 | -121.3054 | -121.0096
769.2344 | 123.2254 | -122.1817 | 0.8194 | 0.053175 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.048956 | -0.076452 | 0.78047 | 0.77978 | 0.70541 | 0.58049 | 122.1252 | 122.3171 | 121.8203 | 121.9594 | 122.2349 | 122.1183 | 122.1972 | 122.1384 | 122.2409 | 122.2307 | 122.1052 | 0.80336 | 0.80266 | 0.7283 | 0.60338 | 122.1481 | 122.34 | 121.8432 | 121.9823 | -121.3448 | -121.0398 | -121.4198 | -121.1149
770.9844 | 123.2208 | -122.0764 | 0.89264 | 0.057754 | -0.058836 | 0.020051 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 0.86746 | 0.87593 | 0.80156 | 0.66291 | 122.0337 | 122.2255 | 121.7287 | 121.8586 | 122.1342 | 122.0176 | 122.0965 | 122.0285 | 122.1356 | 122.1254 | 122 | 0.89035 | 0.89882 | 0.82445 | 0.6858 | 122.0565 | 122.2484 | 121.7516 | 121.8815 | -121.1662 | -120.8613 | -121.2321 | -120.9272
772.6719 | 123.111 | -122.1725 | 0.89722 | 0.062332 | -0.049678 | 0.015472 | -0.038752 | 0.059155 | 0.048956 | -0.067295 | 0.82625 | 0.81641 | 0.7512 | 0.63086 | 122.0794 | 122.2713 | 121.7883 | 121.9136 | 122.2349 | 122.1229 | 122.188 | 122.1338 | 122.2317 | 122.2215 | 122.1053 | 0.84914 | 0.8393 | 0.77409 | 0.65375 | 122.1023 | 122.2942 | 121.8111 | 121.9365 | -121.2532 | -120.962 | -121.3282 | -121.0371
774.4375 | 123.1888 | -122.0215 | 0.99792 | 0.06691 | -0.058836 | 0.015472 | -0.043331 | 0.054577 | 0.053534 | -0.067295 | 0.93156 | 0.93546 | 0.8565 | 0.72244 | 121.9696 | 122.1614 | 121.6692 | 121.7991 | 122.0884 | 121.9626 | 122.037 | 121.9782 | 122.0761 | 122.075 | 121.9542 | 0.95445 | 0.95834 | 0.87938 | 0.74533 | 121.9925 | 122.1843 | 121.6921 | 121.822 | -121.038 | -120.7377 | -121.1131 | -120.8127
776.1875 | 123.1888 | -122.081 | 0.91553 | 0.06691 | -0.054257 | 0.015472 | -0.038752 | 0.059155 | 0.053534 | -0.076452 | 0.89035 | 0.89425 | 0.81529 | 0.68123 | 122.0016 | 122.1981 | 121.7104 | 121.8358 | 122.1479 | 122.0267 | 122.0965 | 122.0422 | 122.1401 | 122.1345 | 122.0045 | 0.91324 | 0.91714 | 0.83818 | 0.70412 | 122.0245 | 122.221 | 121.7333 | 121.8586 | -121.1113 | -120.8201 | -121.1863 | -120.8951
777.875 | 123.2071 | -122.1909 | 0.81024 | 0.057754 | -0.054257 | 0.015472 | -0.043331 | 0.063733 | 0.048956 | -0.071874 | 0.78505 | 0.78436 | 0.71457 | 0.58507 | 122.1069 | 122.2988 | 121.8157 | 121.9411 | 122.2486 | 122.1366 | 122.2063 | 122.1475 | 122.2546 | 122.2398 | 122.119 | 0.80794 | 0.80724 | 0.73746 | 0.60796 | 122.1298 | 122.3217 | 121.8386 | 121.9639 | -121.3219 | -121.0307 | -121.3923 | -121.1012
779.625 | 123.0698 | -122.1542 | 0.91553 | 0.062332 | -0.063415 | 0.010893 | -0.047909 | 0.063733 | 0.053534 | -0.085608 | 0.84915 | 0.84846 | 0.78782 | 0.65833 | 122.0428 | 122.2301 | 121.7516 | 121.8678 | 122.2166 | 122.0908 | 122.1651 | 122.1063 | 122.218 | 122.2078 | 122.0686 | 0.87203 | 0.87135 | 0.81071 | 0.68122 | 122.0657 | 122.253 | 121.7745 | 121.8907 | -121.1937 | -120.9025 | -121.255 | -120.9638
781.3906 | 123.0606 | -122.2641 | 0.79193 | 0.062332 | -0.058836 | 0.015472 | -0.038752 | 0.059155 | 0.053534 | -0.071874 | 0.74842 | 0.74315 | 0.68252 | 0.54844 | 122.139 | 122.3446 | 121.8432 | 121.9685 | 122.3264 | 122.2053 | 122.2796 | 122.2253 | 122.3233 | 122.3176 | 122.1922 | 0.77131 | 0.76603 | 0.70541 | 0.57132 | 122.1618 | 122.3675 | 121.8661 | 121.9914 | -121.3905 | -121.0948 | -121.4564 | -121.1607
783.0781 | 123.1384 | -122.2092 | 0.78278 | 0.057754 | -0.063415 | 0.020051 | -0.047909 | 0.063733 | 0.048956 | -0.076452 | 0.76216 | 0.76146 | 0.69168 | 0.56217 | 122.1298 | 122.3263 | 121.8249 | 121.9548 | 122.2669 | 122.1458 | 122.2292 | 122.1613 | 122.2729 | 122.2581 | 122.1327 | 0.78504 | 0.78435 | 0.71457 | 0.58506 | 122.1527 | 122.3491 | 121.8478 | 121.9777 | -121.3676 | -121.0627 | -121.4381 | -121.1332
784.8281 | 123.0652 | -122.3511 | 0.73242 | 0.06691 | -0.054257 | 0.015472 | -0.043331 | 0.059155 | 0.048956 | -0.076452 | 0.68432 | 0.68362 | 0.61385 | 0.47517 | 122.2122 | 122.4041 | 121.9119 | 122.0372 | 122.418 | 122.2968 | 122.3665 | 122.3077 | 122.4102 | 122.4 | 122.2746 | 0.70721 | 0.70651 | 0.63674 | 0.49806 | 122.2351 | 122.427 | 121.9348 | 122.0601 | -121.5279 | -121.2276 | -121.5984 | -121.298
786.5156 | 123.056 | -122.3831 | 0.68665 | 0.062332 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.048956 | -0.071874 | 0.61564 | 0.61952 | 0.54517 | 0.41564 | 122.2763 | 122.4727 | 121.9851 | 122.0967 | 122.4454 | 122.3197 | 122.3986 | 122.3398 | 122.4423 | 122.4321 | 122.3112 | 0.63853 | 0.64241 | 0.56806 | 0.43853 | 122.2992 | 122.4956 | 122.008 | 122.1196 | -121.6607 | -121.3695 | -121.7311 | -121.44
788.2656 | 123.0789 | -122.3282 | 0.70953 | 0.06691 | -0.058836 | 0.010893 | -0.043331 | 0.059155 | 0.044377 | -0.076452 | 0.64769 | 0.64241 | 0.56807 | 0.43854 | 122.2397 | 122.427 | 121.9393 | 122.0692 | 122.3951 | 122.2694 | 122.3391 | 122.2849 | 122.3873 | 122.3726 | 122.2517 | 0.67058 | 0.6653 | 0.59095 | 0.46143 | 122.2626 | 122.4499 | 121.9622 | 122.0921 | -121.592 | -121.2917 | -121.6716 | -121.3713
790.0312 | 123.0469 | -122.2961 | 0.7782 | 0.062332 | -0.058836 | 0.015472 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 0.6889 | 0.69736 | 0.62301 | 0.49807 | 122.1893 | 122.3812 | 121.8981 | 122.028 | 122.3585 | 122.2373 | 122.3116 | 122.2482 | 122.3599 | 122.3451 | 122.2243 | 0.71179 | 0.72025 | 0.64589 | 0.52095 | 122.2122 | 122.4041 | 121.921 | 122.0509 | -121.5004 | -121.2092 | -121.5663 | -121.2751
791.7031 | 123.0515 | -122.3053 | 0.74616 | 0.057754 | -0.058836 | 0.010893 | -0.047909 | 0.063733 | 0.053534 | -0.071874 | 0.67974 | 0.74772 | 0.61385 | 0.47975 | 122.2031 | 122.3949 | 121.9027 | 122.0372 | 122.3631 | 122.2465 | 122.3162 | 122.2574 | 122.369 | 122.3588 | 122.2334 | 0.70263 | 0.77061 | 0.63674 | 0.50264 | 122.2259 | 122.4178 | 121.9256 | 122.0601 | -121.5233 | -121.223 | -121.5892 | -121.2889
793.4531 | 123.0423 | -122.3923 | 0.67291 | 0.053175 | -0.058836 | 0.015472 | -0.047909 | 0.059155 | 0.048956 | -0.071874 | 0.60191 | 0.66531 | 0.53144 | 0.40649 | 122.2946 | 122.4773 | 121.9897 | 122.115 | 122.4454 | 122.3334 | 122.4077 | 122.3444 | 122.4514 | 122.4412 | 122.3204 | 0.62479 | 0.68819 | 0.55433 | 0.42937 | 122.3175 | 122.5002 | 122.0126 | 122.1379 | -121.6927 | -121.3878 | -121.7632 | -121.4583
795.2188 | 123.0515 | -122.3831 | 0.67291 | 0.057754 | -0.054257 | 0.010893 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 0.58359 | 0.65615 | 0.5177 | 0.38359 | 122.3129 | 122.5002 | 121.9943 | 122.1288 | 122.4409 | 122.3289 | 122.394 | 122.3398 | 122.4423 | 122.4367 | 122.3067 | 0.60648 | 0.67904 | 0.54059 | 0.40648 | 122.3358 | 122.5231 | 122.0172 | 122.1516 | -121.7293 | -121.4107 | -121.7952 | -121.4766
796.9531 | 123.0377 | -122.3969 | 0.65918 | 0.057754 | -0.049678 | 0.020051 | -0.043331 | 0.063733 | 0.048956 | -0.076452 | 0.59733 | 0.65615 | 0.52228 | 0.39275 | 122.2946 | 122.4819 | 121.9989 | 122.1104 | 122.4546 | 122.3472 | 122.4169 | 122.3535 | 122.4606 | 122.4458 | 122.3204 | 0.62022 | 0.67904 | 0.54517 | 0.41564 | 122.3175 | 122.5048 | 122.0218 | 122.1333 | -121.6973 | -121.4015 | -121.7723 | -121.4766
798.6406 | 123.0515 | -122.4335 | 0.64545 | 0.062332 | -0.063415 | 0.010893 | -0.043331 | 0.054577 | 0.048956 | -0.071874 | 0.56986 | 0.63325 | 0.49939 | 0.36528 | 122.3221 | 122.5048 | 122.0172 | 122.1516 | 122.4958 | 122.3701 | 122.4444 | 122.3901 | 122.488 | 122.4824 | 122.3616 | 0.59275 | 0.65614 | 0.52228 | 0.38816 | 122.345 | 122.5277 | 122.0401 | 122.1745 | -121.7522 | -121.4473 | -121.8227 | -121.5178
800.3906 | 123.0469 | -122.4106 | 0.67291 | 0.057754 | -0.067994 | 0.010893 | -0.043331 | 0.059155 | 0.044377 | -0.071874 | 0.58359 | 0.64699 | 0.5177 | 0.38817 | 122.3038 | 122.4911 | 122.0034 | 122.1333 | 122.4683 | 122.3426 | 122.4215 | 122.3673 | 122.4697 | 122.455 | 122.3387 | 0.60648 | 0.66988 | 0.54059 | 0.41106 | 122.3267 | 122.5139 | 122.0263 | 122.1562 | -121.7202 | -121.4199 | -121.7861 | -121.4857
802.1406 | 123.1338 | -122.3923 | 0.6134 | 0.06691 | -0.067994 | 0.015472 | -0.047909 | 0.054577 | 0.048956 | -0.08103 | 0.58359 | 0.64699 | 0.50397 | 0.38359 | 122.2992 | 122.4911 | 121.9989 | 122.1242 | 122.4592 | 122.3243 | 122.4077 | 122.3444 | 122.4468 | 122.4412 | 122.3112 | 0.60648 | 0.66988 | 0.52686 | 0.40648 | 122.3221 | 122.5139 | 122.0218 | 122.1471 | -121.7156 | -121.4153 | -121.7952 | -121.4949
803.8906 | 123.0469 | -122.3923 | 0.6546 | 0.062332 | -0.058836 | 0.020051 | -0.038752 | 0.059155 | 0.044377 | -0.067295 | 0.58817 | 0.66073 | 0.52228 | 0.39275 | 122.2763 | 122.4727 | 121.9851 | 122.115 | 122.4546 | 122.3334 | 122.4123 | 122.3535 | 122.4514 | 122.4367 | 122.325 | 0.61106 | 0.68361 | 0.54517 | 0.41564 | 122.2992 | 122.4956 | 122.008 | 122.1379 | -121.6881 | -121.397 | -121.754 | -121.4628
805.5938 | 123.175 | -122.3282 | 0.64087 | 0.062332 | -0.072572 | 0.010893 | -0.047909 | 0.059155 | 0.048956 | -0.08103 | 0.61106 | 0.68362 | 0.53602 | 0.40649 | 122.2671 | 122.459 | 121.9714 | 122.0967 | 122.3905 | 122.2556 | 122.3391 | 122.2803 | 122.3873 | 122.3771 | 122.2472 | 0.63395 | 0.70651 | 0.55891 | 0.42937 | 122.29 | 122.4819 | 121.9943 | 122.1196 | -121.6561 | -121.3603 | -121.7311 | -121.4354
807.3438 | 123.1384 | -122.3877 | 0.62714 | 0.062332 | -0.058836 | 0.010893 | -0.043331 | 0.063733 | 0.048956 | -0.076452 | 0.58359 | 0.64241 | 0.50855 | 0.37901 | 122.29 | 122.5002 | 121.9897 | 122.1288 | 122.45 | 122.3289 | 122.3986 | 122.3444 | 122.4514 | 122.4367 | 122.3112 | 0.60648 | 0.6653 | 0.53144 | 0.4019 | 122.3129 | 122.5231 | 122.0126 | 122.1516 | -121.7064 | -121.4061 | -121.7815 | -121.4812
809.0469 | 123.1888 | -122.3785 | 0.59509 | 0.057754 | -0.058836 | 0.006315 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 0.57901 | 0.64241 | 0.50397 | 0.37443 | 122.2946 | 122.4911 | 122.008 | 122.1288 | 122.4363 | 122.3197 | 122.3849 | 122.3352 | 122.4377 | 122.4321 | 122.3021 | 0.6019 | 0.6653 | 0.52686 | 0.39732 | 122.3175 | 122.5139 | 122.0309 | 122.1516 | -121.7156 | -121.429 | -121.7906 | -121.5041
810.7812 | 123.1613 | -122.4014 | 0.5722 | 0.062332 | -0.049678 | 0.006315 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 0.54697 | 0.61952 | 0.4765 | 0.34696 | 122.3221 | 122.514 | 122.0172 | 122.1516 | 122.4638 | 122.3517 | 122.4077 | 122.3535 | 122.4606 | 122.4504 | 122.325 | 0.56985 | 0.64241 | 0.49939 | 0.36985 | 122.345 | 122.5368 | 122.0401 | 122.1745 | -121.7751 | -121.4702 | -121.8456 | -121.5407
812.5312 | 123.0698 | -122.406 | 0.63171 | 0.062332 | -0.063415 | 0.010893 | -0.047909 | 0.059155 | 0.044377 | -0.067295 | 0.54697 | 0.62867 | 0.49023 | 0.35154 | 122.3221 | 122.514 | 122.0126 | 122.1425 | 122.4683 | 122.3426 | 122.4169 | 122.3581 | 122.4652 | 122.4504 | 122.3387 | 0.56985 | 0.65156 | 0.51312 | 0.37443 | 122.345 | 122.5368 | 122.0355 | 122.1654 | -121.7751 | -121.4656 | -121.8319 | -121.5224
814.2812 | 123.1522 | -122.3785 | 0.59967 | 0.057754 | -0.063415 | 0.015472 | -0.052488 | 0.059155 | 0.053534 | -0.067295 | 0.56528 | 0.63325 | 0.49481 | 0.36985 | 122.3038 | 122.4956 | 122.0172 | 122.1379 | 122.4363 | 122.3151 | 122.394 | 122.3261 | 122.4377 | 122.4321 | 122.3112 | 0.58817 | 0.65614 | 0.5177 | 0.39274 | 122.3267 | 122.5185 | 122.0401 | 122.1608 | -121.7385 | -121.4519 | -121.809 | -121.5224
816.0312 | 123.0789 | -122.4335 | 0.60425 | 0.06691 | -0.067994 | 0.015472 | -0.047909 | 0.063733 | 0.058113 | -0.08103 | 0.54697 | 0.61036 | 0.47192 | 0.35154 | 122.3267 | 122.5185 | 122.0355 | 122.1516 | 122.5004 | 122.3655 | 122.4489 | 122.3856 | 122.4972 | 122.4916 | 122.3524 | 0.56985 | 0.63325 | 0.49481 | 0.37443 | 122.3496 | 122.5414 | 122.0584 | 122.1745 | -121.7797 | -121.4885 | -121.8547 | -121.5636
817.7188 | 123.1155 | -122.406 | 0.59052 | 0.053175 | -0.067994 | 0.015472 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 0.50118 | 0.63325 | 0.48566 | 0.34238 | 122.3084 | 122.5002 | 122.0034 | 122.1425 | 122.4592 | 122.338 | 122.4215 | 122.3581 | 122.4606 | 122.455 | 122.3296 | 0.52407 | 0.65614 | 0.50855 | 0.36527 | 122.3312 | 122.5231 | 122.0263 | 122.1654 | -121.8072 | -121.5023 | -121.8227 | -121.5178
819.4688 | 122.8867 | -121.6644 | 1.2314 | 0.057754 | -0.067994 | 0.020051 | -0.043331 | 0.063733 | 0.058113 | -0.071874 | 0.99108 | 1.114 | 0.97553 | 0.84149 | 121.704 | 121.8959 | 121.4128 | 121.5427 | 121.7222 | 121.5964 | 121.6845 | 121.6211 | 121.7282 | 121.7225 | 121.5926 | 1.014 | 1.1369 | 0.99842 | 0.86438 | 121.7269 | 121.9188 | 121.4357 | 121.5656 | -120.713 | -120.4218 | -120.7285 | -120.4373
821.2188 | 122.7036 | -121.4172 | 1.2589 | 0.062332 | -0.063415 | 0.015472 | -0.047909 | 0.063733 | 0.058113 | -0.071874 | 1.1376 | 1.2651 | 1.1312 | 0.98802 | 121.3195 | 121.5068 | 121.0145 | 121.1536 | 121.4796 | 121.3538 | 121.4327 | 121.3693 | 121.481 | 121.4753 | 121.3454 | 1.1605 | 1.288 | 1.1541 | 1.0109 | 121.3424 | 121.5297 | 121.0374 | 121.1765 | -120.1819 | -119.8769 | -120.1883 | -119.8833
822.9688 | 122.5983 | -121.3623 | 1.2543 | 0.062332 | -0.072572 | 0.010893 | -0.052488 | 0.059155 | 0.053534 | -0.071874 | 1.1239 | 1.2606 | 1.1083 | 0.97886 | 121.2416 | 121.4427 | 120.9642 | 121.0758 | 121.4246 | 121.2897 | 121.3732 | 121.3098 | 121.4215 | 121.4158 | 121.2904 | 1.1467 | 1.2834 | 1.1312 | 1.0018 | 121.2645 | 121.4656 | 120.987 | 121.0987 | -120.1178 | -119.8403 | -120.1333 | -119.8558
824.7344 | 122.5616 | -121.3074 | 1.268 | 0.062332 | -0.067994 | 0.015472 | -0.047909 | 0.054577 | 0.053534 | -0.08103 | 1.1422 | 1.2606 | 1.122 | 0.9926 | 121.1867 | 121.3832 | 120.8955 | 121.0208 | 121.3697 | 121.2394 | 121.3228 | 121.2595 | 121.3619 | 121.3609 | 121.2263 | 1.1651 | 1.2834 | 1.1449 | 1.0155 | 121.2096 | 121.4061 | 120.9184 | 121.0437 | -120.0445 | -119.7533 | -120.0647 | -119.7734
826.4219 | 122.5296 | -121.1975 | 1.3138 | 0.053175 | -0.067994 | 0.010893 | -0.047909 | 0.059155 | 0.048956 | -0.071874 | 1.1925 | 1.3109 | 1.1724 | 1.043 | 121.0951 | 121.287 | 120.8039 | 120.9293 | 121.2507 | 121.1295 | 121.2084 | 121.1496 | 121.2567 | 121.2465 | 121.1256 | 1.2154 | 1.3338 | 1.1953 | 1.0659 | 121.118 | 121.3099 | 120.8268 | 120.9522 | -119.9026 | -119.6114 | -119.9227 | -119.6315
828.1719 | 122.5983 | -121.1929 | 1.2131 | 0.062332 | -0.072572 | 0.020051 | -0.047909 | 0.063733 | 0.058113 | -0.071874 | 1.1376 | 1.2468 | 1.1266 | 0.97886 | 121.1318 | 121.3282 | 120.836 | 120.9567 | 121.2553 | 121.1204 | 121.213 | 121.145 | 121.2567 | 121.251 | 121.1211 | 1.1605 | 1.2697 | 1.1495 | 1.0018 | 121.1546 | 121.3511 | 120.8588 | 120.9796 | -119.9942 | -119.6984 | -120.0051 | -119.7093
829.9219 | 122.5113 | -121.225 | 1.2314 | 0.062332 | -0.063415 | 0.006315 | -0.043331 | 0.063733 | 0.053534 | -0.071874 | 1.1055 | 1.2331 | 1.0946 | 0.96055 | 121.1318 | 121.3145 | 120.836 | 120.9567 | 121.2873 | 121.1616 | 121.2313 | 121.1816 | 121.2887 | 121.2785 | 121.1531 | 1.1284 | 1.256 | 1.1175 | 0.98344 | 121.1546 | 121.3374 | 120.8588 | 120.9796 | -120.0262 | -119.7304 | -120.0372 | -119.7414
831.6094 | 122.4426 | -121.1929 | 1.2405 | 0.053175 | -0.063415 | 0.010893 | -0.047909 | 0.059155 | 0.053534 | -0.071874 | 1.1239 | 1.2468 | 1.1129 | 0.97429 | 121.0906 | 121.2779 | 120.7902 | 120.9155 | 121.2461 | 121.1295 | 121.2038 | 121.145 | 121.2521 | 121.2465 | 121.1211 | 1.1467 | 1.2697 | 1.1358 | 0.99717 | 121.1134 | 121.3008 | 120.8131 | 120.9384 | -119.9667 | -119.6663 | -119.9777 | -119.6773
833.3594 | 122.4014 | -121.17 | 1.2405 | 0.06691 | -0.063415 | 0.020051 | -0.047909 | 0.059155 | 0.058113 | -0.071874 | 1.1239 | 1.2514 | 1.1129 | 0.96971 | 121.0585 | 121.255 | 120.7673 | 120.8835 | 121.237 | 121.1066 | 121.1901 | 121.1221 | 121.2292 | 121.2282 | 121.0982 | 1.1467 | 1.2743 | 1.1358 | 0.9926 | 121.0814 | 121.2779 | 120.7902 | 120.9064 | -119.9347 | -119.6434 | -119.9456 | -119.6544
835.125 | 122.438 | -121.2479 | 1.0941 | 0.06691 | -0.067994 | 0.010893 | -0.047909 | 0.059155 | 0.058113 | -0.071874 | 1.0094 | 1.1323 | 1.0076 | 0.86897 | 121.1409 | 121.3328 | 120.8451 | 120.9659 | 121.3148 | 121.1799 | 121.2588 | 121.2 | 121.307 | 121.306 | 121.176 | 1.0323 | 1.1552 | 1.0305 | 0.89186 | 121.1638 | 121.3557 | 120.868 | 120.9888 | -120.1315 | -119.8357 | -120.1333 | -119.8375
836.875 | 122.3557 | -121.1884 | 1.1902 | 0.062332 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.053534 | -0.085608 | 1.0689 | 1.1919 | 1.0579 | 0.92392 | 121.0677 | 121.255 | 120.7719 | 120.9018 | 121.2507 | 121.1249 | 121.2038 | 121.145 | 121.2475 | 121.2419 | 121.1027 | 1.0918 | 1.2148 | 1.0808 | 0.94681 | 121.0906 | 121.2779 | 120.7947 | 120.9247 | -119.9988 | -119.7029 | -120.0097 | -119.7139
838.5625 | 122.4335 | -121.1334 | 1.149 | 0.053175 | -0.072572 | 0.015472 | -0.043331 | 0.054577 | 0.044377 | -0.071874 | 1.0598 | 1.1919 | 1.0396 | 0.91018 | 121.0539 | 121.2458 | 120.7535 | 120.8789 | 121.1866 | 121.0609 | 121.1489 | 121.0901 | 121.188 | 121.1778 | 121.0615 | 1.0826 | 1.2148 | 1.0625 | 0.93307 | 121.0768 | 121.2687 | 120.7764 | 120.9018 | -119.9942 | -119.6938 | -120.0143 | -119.7139
840.3125 | 122.3328 | -121.0831 | 1.1856 | 0.053175 | -0.067994 | 0.020051 | -0.043331 | 0.063733 | 0.053534 | -0.067295 | 1.0781 | 1.201 | 1.0717 | 0.93765 | 121.0036 | 121.1955 | 120.7032 | 120.824 | 121.1362 | 121.0151 | 121.1031 | 121.0397 | 121.1468 | 121.1366 | 121.0158 | 1.101 | 1.2239 | 1.0946 | 0.96054 | 121.0265 | 121.2184 | 120.7261 | 120.8469 | -119.9255 | -119.6251 | -119.9319 | -119.6315
841.9844 | 122.3602 | -121.0373 | 1.1948 | 0.062332 | -0.067994 | 0.015472 | -0.047909 | 0.059155 | 0.058113 | -0.071874 | 1.0872 | 1.2056 | 1.0717 | 0.93765 | 120.9715 | 121.1588 | 120.6849 | 120.8011 | 121.0996 | 120.9693 | 121.0528 | 120.9894 | 121.0964 | 121.0954 | 120.9654 | 1.1101 | 1.2285 | 1.0946 | 0.96054 | 120.9944 | 121.1817 | 120.7078 | 120.824 | -119.8843 | -119.5976 | -119.8998 | -119.6132
843.7344 | 122.287 | -121.0876 | 1.1581 | 0.053175 | -0.067994 | 0.015472 | -0.047909 | 0.054577 | 0.044377 | -0.076452 | 1.0414 | 1.1644 | 1.0259 | 0.89644 | 120.9944 | 121.1817 | 120.6986 | 120.8148 | 121.1408 | 121.0197 | 121.1031 | 121.0397 | 121.1422 | 121.132 | 121.0112 | 1.0643 | 1.1873 | 1.0488 | 0.91933 | 121.0173 | 121.2046 | 120.7215 | 120.8377 | -119.953 | -119.6572 | -119.9685 | -119.6727
845.5 | 122.2275 | -121.0556 | 1.1673 | 0.057754 | -0.058836 | 0.020051 | -0.043331 | 0.054577 | 0.053534 | -0.067295 | 1.0414 | 1.1644 | 1.0259 | 0.90102 | 120.9715 | 121.1634 | 120.6803 | 120.8011 | 121.1134 | 120.9968 | 121.0757 | 121.0123 | 121.1102 | 121.1091 | 120.9883 | 1.0643 | 1.1873 | 1.0488 | 0.92391 | 120.9944 | 121.1863 | 120.7032 | 120.824 | -119.9301 | -119.6388 | -119.9456 | -119.6544
847.25 | 122.3373 | -120.9778 | 1.1261 | 0.057754 | -0.063415 | 0.015472 | -0.034174 | 0.054577 | 0.053534 | -0.076452 | 1.0689 | 1.1827 | 1.0534 | 0.91476 | 120.9166 | 121.1131 | 120.6299 | 120.7461 | 121.0355 | 120.9144 | 120.9933 | 120.9436 | 121.0324 | 121.0313 | 120.9013 | 1.0918 | 1.2056 | 1.0763 | 0.93765 | 120.9395 | 121.136 | 120.6528 | 120.769 | -119.8477 | -119.561 | -119.8632 | -119.5766
848.9844 | 122.2504 | -120.9915 | 1.1673 | 0.053175 | -0.063415 | 0.015472 | -0.038752 | 0.059155 | 0.058113 | -0.076452 | 1.0598 | 1.1781 | 1.0442 | 0.91018 | 120.9029 | 121.0948 | 120.6116 | 120.7233 | 121.0447 | 120.9281 | 121.007 | 120.9528 | 121.0507 | 121.0496 | 120.9151 | 1.0826 | 1.201 | 1.0671 | 0.93307 | 120.9257 | 121.1176 | 120.6345 | 120.7461 | -119.8431 | -119.5519 | -119.8586 | -119.5674
850.6719 | 122.2321 | -120.9732 | 1.1307 | 0.057754 | -0.067994 | 0.015472 | -0.043331 | 0.059155 | 0.044377 | -0.067295 | 1.046 | 1.1736 | 1.0305 | 0.90102 | 120.8983 | 121.0856 | 120.5933 | 120.7278 | 121.031 | 120.9052 | 120.9887 | 120.9299 | 121.0324 | 121.0176 | 120.9059 | 1.0689 | 1.1964 | 1.0534 | 0.92391 | 120.9212 | 121.1085 | 120.6162 | 120.7507 | -119.8523 | -119.5473 | -119.8678 | -119.5628
852.4219 | 122.1176 | -120.9549 | 1.1673 | 0.053175 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.058113 | -0.076452 | 1.0506 | 1.1736 | 1.0351 | 0.90102 | 120.8708 | 121.0581 | 120.5704 | 120.7004 | 121.0081 | 120.8915 | 120.9704 | 120.9116 | 121.014 | 121.013 | 120.8784 | 1.0735 | 1.1964 | 1.0579 | 0.92391 | 120.8937 | 121.081 | 120.5933 | 120.7233 | -119.8202 | -119.5198 | -119.8358 | -119.5354
854.1875 | 122.1313 | -121.0281 | 1.1124 | 0.062332 | -0.063415 | 0.015472 | -0.052488 | 0.063733 | 0.048956 | -0.062717 | 1.014 | 1.1278 | 0.99842 | 0.85981 | 120.8937 | 121.0764 | 120.5933 | 120.7324 | 121.0905 | 120.9647 | 121.0436 | 120.9756 | 121.0919 | 121.0771 | 120.9654 | 1.0369 | 1.1507 | 1.0213 | 0.8827 | 120.9166 | 121.0993 | 120.6162 | 120.7553 | -119.8797 | -119.5793 | -119.8953 | -119.5949
855.9375 | 122.2458 | -120.9137 | 1.1078 | 0.06691 | -0.058836 | 0.015472 | -0.047909 | 0.054577 | 0.048956 | -0.076452 | 1.0186 | 1.1369 | 1.0076 | 0.86897 | 120.8525 | 121.049 | 120.5613 | 120.6866 | 120.9806 | 120.8549 | 120.9292 | 120.8658 | 120.9683 | 120.9627 | 120.8372 | 1.0414 | 1.1598 | 1.0305 | 0.89186 | 120.8754 | 121.0719 | 120.5841 | 120.7095 | -119.8339 | -119.5427 | -119.8449 | -119.5537
857.6875 | 122.1313 | -120.9091 | 1.0895 | 0.057754 | -0.063415 | 0.020051 | -0.047909 | 0.06831 | 0.053534 | -0.08103 | 1.0048 | 1.1323 | 0.99842 | 0.85981 | 120.8479 | 121.0307 | 120.5429 | 120.6775 | 120.9669 | 120.8457 | 120.9292 | 120.8612 | 120.9774 | 120.9627 | 120.8281 | 1.0277 | 1.1552 | 1.0213 | 0.8827 | 120.8708 | 121.0535 | 120.5658 | 120.7004 | -119.8431 | -119.5381 | -119.8495 | -119.5445
859.375 | 122.0993 | -120.9229 | 1.1307 | 0.062332 | -0.063415 | 0.015472 | -0.047909 | 0.059155 | 0.044377 | -0.076452 | 1.014 | 1.1278 | 0.99842 | 0.86439 | 120.8296 | 121.0123 | 120.5338 | 120.65 | 120.9852 | 120.8594 | 120.9383 | 120.8749 | 120.982 | 120.9672 | 120.8464 | 1.0369 | 1.1507 | 1.0213 | 0.88728 | 120.8525 | 121.0352 | 120.5567 | 120.6729 | -119.8156 | -119.5198 | -119.8312 | -119.5354
861.0781 | 122.0764 | -120.8679 | 1.1261 | 0.053175 | -0.049678 | 0.010893 | -0.038752 | 0.059155 | 0.053534 | -0.067295 | 1.0231 | 1.1461 | 1.0122 | 0.8827 | 120.7838 | 120.9711 | 120.4926 | 120.6225 | 120.9211 | 120.8182 | 120.8788 | 120.8292 | 120.9271 | 120.9215 | 120.8006 | 1.046 | 1.169 | 1.035 | 0.90559 | 120.8067 | 120.994 | 120.5155 | 120.6454 | -119.7607 | -119.4694 | -119.7717 | -119.4804
862.8125 | 122.0169 | -120.8908 | 1.1444 | 0.062332 | -0.054257 | 0.015472 | -0.043331 | 0.059155 | 0.058113 | -0.067295 | 1.0231 | 1.1461 | 1.003 | 0.87813 | 120.7747 | 120.9528 | 120.4743 | 120.6042 | 120.9531 | 120.8366 | 120.9063 | 120.8475 | 120.95 | 120.9489 | 120.8235 | 1.046 | 1.169 | 1.0259 | 0.90101 | 120.7976 | 120.9757 | 120.4971 | 120.6271 | -119.7515 | -119.4511 | -119.7717 | -119.4713
864.5469 | 122.0078 | -120.8725 | 1.1307 | 0.062332 | -0.058836 | 0.015472 | -0.047909 | 0.06831 | 0.048956 | -0.067295 | 1.014 | 1.1415 | 0.99842 | 0.85981 | 120.7426 | 120.9437 | 120.4514 | 120.5768 | 120.9348 | 120.8137 | 120.888 | 120.8246 | 120.9408 | 120.9215 | 120.8052 | 1.0369 | 1.1644 | 1.0213 | 0.8827 | 120.7655 | 120.9666 | 120.4743 | 120.5996 | -119.7286 | -119.4374 | -119.7442 | -119.4529
866.2969 | 121.9757 | -120.8633 | 1.1307 | 0.062332 | -0.063415 | 0.015472 | -0.038752 | 0.06831 | 0.048956 | -0.071874 | 1.0094 | 1.1369 | 0.99842 | 0.86897 | 120.7426 | 120.9254 | 120.4422 | 120.5676 | 120.9257 | 120.7999 | 120.8788 | 120.8246 | 120.9317 | 120.9123 | 120.7915 | 1.0323 | 1.1598 | 1.0213 | 0.89186 | 120.7655 | 120.9483 | 120.4651 | 120.5905 | -119.7332 | -119.4328 | -119.7442 | -119.4438
868.0312 | 121.9757 | -120.7947 | 1.1261 | 0.062332 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.053534 | -0.062717 | 1.014 | 1.1323 | 1.0076 | 0.86897 | 120.7151 | 120.8933 | 120.4147 | 120.5447 | 120.857 | 120.7313 | 120.8102 | 120.7513 | 120.8538 | 120.8482 | 120.732 | 1.0369 | 1.1552 | 1.0305 | 0.89186 | 120.738 | 120.9162 | 120.4376 | 120.5676 | -119.7012 | -119.4008 | -119.7076 | -119.4072
869.7812 | 121.9162 | -120.8084 | 1.1398 | 0.062332 | -0.058836 | 0.015472 | -0.047909 | 0.063733 | 0.053534 | -0.062717 | 1.0231 | 1.1461 | 1.0122 | 0.87355 | 120.6877 | 120.8658 | 120.3873 | 120.5172 | 120.8707 | 120.7496 | 120.8239 | 120.7605 | 120.8721 | 120.8619 | 120.7457 | 1.046 | 1.169 | 1.035 | 0.89643 | 120.7106 | 120.8887 | 120.4102 | 120.5401 | -119.6645 | -119.3641 | -119.6755 | -119.3751
871.4688 | 121.9666 | -120.7214 | 1.1765 | 0.062332 | -0.058836 | 0.015472 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 1.0689 | 1.1919 | 1.0442 | 0.92392 | 120.6098 | 120.8018 | 120.3186 | 120.4486 | 120.7838 | 120.6626 | 120.7369 | 120.6781 | 120.7806 | 120.775 | 120.645 | 1.0918 | 1.2148 | 1.0671 | 0.94681 | 120.6327 | 120.8246 | 120.3415 | 120.4715 | -119.5409 | -119.2497 | -119.5656 | -119.2744
873.2188 | 122.0215 | -120.6802 | 1.1124 | 0.057754 | -0.058836 | 0.015472 | -0.043331 | 0.06831 | 0.048956 | -0.076452 | 1.0414 | 1.169 | 1.0259 | 0.89186 | 120.6236 | 120.8063 | 120.3232 | 120.4486 | 120.738 | 120.6214 | 120.6957 | 120.6369 | 120.7485 | 120.7292 | 120.6038 | 1.0643 | 1.1919 | 1.0488 | 0.91475 | 120.6465 | 120.8292 | 120.3461 | 120.4715 | -119.5821 | -119.2817 | -119.5977 | -119.2973
874.9688 | 121.8704 | -120.607 | 1.2863 | 0.062332 | -0.067994 | 0.015472 | -0.047909 | 0.054577 | 0.048956 | -0.071874 | 1.1422 | 1.2606 | 1.1266 | 0.99718 | 120.5 | 120.6827 | 120.2041 | 120.3295 | 120.6693 | 120.539 | 120.6225 | 120.5591 | 120.6616 | 120.656 | 120.5351 | 1.1651 | 1.2834 | 1.1495 | 1.0201 | 120.5229 | 120.7056 | 120.227 | 120.3524 | -119.3578 | -119.062 | -119.3734 | -119.0775
876.6406 | 121.9391 | -120.5978 | 1.2039 | 0.053175 | -0.063415 | 0.015472 | -0.047909 | 0.059155 | 0.044377 | -0.062717 | 1.101 | 1.2331 | 1.0808 | 0.95139 | 120.5091 | 120.7056 | 120.2225 | 120.3387 | 120.651 | 120.5344 | 120.6133 | 120.5499 | 120.657 | 120.6422 | 120.5351 | 1.1239 | 1.256 | 1.1037 | 0.97428 | 120.532 | 120.7285 | 120.2453 | 120.3616 | -119.4082 | -119.1215 | -119.4283 | -119.1416
878.3906 | 121.9666 | -120.5429 | 1.181 | 0.062332 | -0.063415 | 0.015472 | -0.047909 | 0.049999 | 0.048956 | -0.08103 | 1.101 | 1.2193 | 1.0808 | 0.95139 | 120.5046 | 120.6873 | 120.2087 | 120.3387 | 120.6052 | 120.4795 | 120.5584 | 120.495 | 120.5929 | 120.5919 | 120.4619 | 1.1239 | 1.2422 | 1.1037 | 0.97428 | 120.5274 | 120.7102 | 120.2316 | 120.3616 | -119.4036 | -119.1078 | -119.4237 | -119.1279
880.1562 | 121.875 | -120.5338 | 1.2222 | 0.062332 | -0.058836 | 0.015472 | -0.038752 | 0.059155 | 0.053534 | -0.08103 | 1.1147 | 1.2331 | 1.0946 | 0.96513 | 120.4725 | 120.6598 | 120.1721 | 120.3021 | 120.5961 | 120.4749 | 120.5492 | 120.495 | 120.5929 | 120.5873 | 120.4527 | 1.1376 | 1.256 | 1.1175 | 0.98802 | 120.4954 | 120.6827 | 120.195 | 120.325 | -119.3578 | -119.0574 | -119.3779 | -119.0775
881.9062 | 121.8018 | -120.5704 | 1.1993 | 0.06691 | -0.058836 | 0.015472 | -0.047909 | 0.063733 | 0.048956 | -0.067295 | 1.0781 | 1.1964 | 1.0717 | 0.93307 | 120.4862 | 120.6781 | 120.195 | 120.3158 | 120.6373 | 120.5115 | 120.5858 | 120.5225 | 120.6341 | 120.6193 | 120.5031 | 1.101 | 1.2193 | 1.0946 | 0.95596 | 120.5091 | 120.701 | 120.2179 | 120.3387 | -119.4082 | -119.1169 | -119.4146 | -119.1233
883.5781 | 121.8475 | -120.575 | 1.1581 | 0.062332 | -0.058836 | 0.010893 | -0.047909 | 0.059155 | 0.053534 | -0.071874 | 1.0552 | 1.1781 | 1.0442 | 0.9056 | 120.4817 | 120.6736 | 120.195 | 120.3158 | 120.6373 | 120.5161 | 120.5858 | 120.527 | 120.6341 | 120.6285 | 120.5031 | 1.0781 | 1.201 | 1.0671 | 0.92849 | 120.5045 | 120.6965 | 120.2179 | 120.3387 | -119.4265 | -119.1398 | -119.4375 | -119.1508
885.3281 | 121.8704 | -120.575 | 1.1169 | 0.057754 | -0.058836 | 0.006315 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 1.0231 | 1.1507 | 1.0213 | 0.8827 | 120.4954 | 120.6873 | 120.1996 | 120.3341 | 120.6327 | 120.5161 | 120.5813 | 120.527 | 120.6341 | 120.6239 | 120.4985 | 1.046 | 1.1735 | 1.0442 | 0.90559 | 120.5183 | 120.7102 | 120.2224 | 120.357 | -119.4723 | -119.1764 | -119.4741 | -119.1782
887.0781 | 121.7697 | -120.5933 | 1.1032 | 0.062332 | -0.058836 | 0.006315 | -0.043331 | 0.059155 | 0.053534 | -0.067295 | 1.014 | 1.1323 | 1.003 | 0.85981 | 120.4908 | 120.6919 | 120.2041 | 120.3295 | 120.6556 | 120.5344 | 120.5996 | 120.5499 | 120.6524 | 120.6468 | 120.526 | 1.0369 | 1.1552 | 1.0259 | 0.8827 | 120.5137 | 120.7148 | 120.227 | 120.3524 | -119.4768 | -119.1902 | -119.4878 | -119.2011
888.8281 | 121.6965 | -120.6024 | 1.0986 | 0.057754 | -0.054257 | 0.010893 | -0.052488 | 0.06831 | 0.048956 | -0.076452 | 1.0002 | 1.1186 | 0.98469 | 0.85065 | 120.4771 | 120.6827 | 120.1858 | 120.3112 | 120.6602 | 120.5482 | 120.6133 | 120.5499 | 120.6707 | 120.6514 | 120.526 | 1.0231 | 1.1415 | 1.0076 | 0.87354 | 120.5 | 120.7056 | 120.2087 | 120.3341 | -119.4768 | -119.1856 | -119.4924 | -119.2011
890.5469 | 121.6827 | -120.5704 | 1.1169 | 0.053175 | -0.058836 | 0.015472 | -0.047909 | 0.059155 | 0.048956 | -0.076452 | 1.0094 | 1.1278 | 0.98469 | 0.85065 | 120.4542 | 120.6507 | 120.1721 | 120.2929 | 120.6235 | 120.5115 | 120.5858 | 120.5225 | 120.6295 | 120.6193 | 120.4939 | 1.0323 | 1.1507 | 1.0076 | 0.87354 | 120.4771 | 120.6736 | 120.195 | 120.3158 | -119.4448 | -119.1627 | -119.4695 | -119.1874
892.2969 | 121.7194 | -120.5566 | 1.1078 | 0.057754 | -0.054257 | 0.006315 | -0.047909 | 0.063733 | 0.053534 | -0.071874 | 0.9865 | 1.1049 | 0.95722 | 0.85065 | 120.4633 | 120.6461 | 120.1675 | 120.2975 | 120.6144 | 120.5024 | 120.563 | 120.5087 | 120.6204 | 120.6102 | 120.4848 | 1.0094 | 1.1278 | 0.98011 | 0.87354 | 120.4862 | 120.669 | 120.1904 | 120.3204 | -119.4768 | -119.181 | -119.5061 | -119.2103
893.9688 | 121.6507 | -120.4926 | 1.1581 | 0.057754 | -0.058836 | 0.010893 | -0.043331 | 0.063733 | 0.044377 | -0.071874 | 1.0414 | 1.1781 | 1.0351 | 0.89186 | 120.3855 | 120.582 | 120.0897 | 120.2151 | 120.5503 | 120.4337 | 120.5034 | 120.4492 | 120.5563 | 120.5369 | 120.4207 | 1.0643 | 1.201 | 1.0579 | 0.91475 | 120.4084 | 120.6049 | 120.1126 | 120.238 | -119.3441 | -119.0482 | -119.3505 | -119.0546
895.7188 | 121.7239 | -120.4971 | 1.1032 | 0.053175 | -0.058836 | 0.006315 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 1.0002 | 1.1186 | 0.98011 | 0.85523 | 120.413 | 120.6141 | 120.1217 | 120.2425 | 120.5503 | 120.4383 | 120.5034 | 120.4492 | 120.5609 | 120.5461 | 120.4253 | 1.0231 | 1.1415 | 1.003 | 0.87812 | 120.4359 | 120.6369 | 120.1446 | 120.2654 | -119.4128 | -119.1215 | -119.4329 | -119.1416
897.4688 | 121.6965 | -120.4742 | 1.1032 | 0.053175 | -0.058836 | 0.010893 | -0.047909 | 0.072888 | 0.039799 | -0.071874 | 0.99108 | 1.1186 | 0.98011 | 0.84607 | 120.3901 | 120.5912 | 120.0988 | 120.2334 | 120.5274 | 120.4154 | 120.4851 | 120.4263 | 120.5471 | 120.514 | 120.4024 | 1.014 | 1.1415 | 1.003 | 0.86896 | 120.413 | 120.6141 | 120.1217 | 120.2563 | -119.399 | -119.1078 | -119.41 | -119.1187
899.2188 | 121.6049 | -120.4834 | 1.1307 | 0.06691 | -0.067994 | 0.006315 | -0.047909 | 0.059155 | 0.053534 | -0.062717 | 1.014 | 1.1323 | 0.99385 | 0.87813 | 120.3718 | 120.5591 | 120.0714 | 120.2059 | 120.5503 | 120.4154 | 120.4897 | 120.4355 | 120.5426 | 120.5369 | 120.4207 | 1.0369 | 1.1552 | 1.0167 | 0.90101 | 120.3947 | 120.582 | 120.0943 | 120.2288 | -119.3578 | -119.0574 | -119.3779 | -119.0775
900.9688 | 121.5958 | -120.433 | 1.1307 | 0.062332 | -0.049678 | 0.010893 | -0.043331 | 0.063733 | 0.048956 | -0.071874 | 1.0186 | 1.1415 | 1.0076 | 0.86897 | 120.3397 | 120.5271 | 120.0439 | 120.1693 | 120.4954 | 120.3834 | 120.4439 | 120.3897 | 120.4968 | 120.482 | 120.3612 | 1.0414 | 1.1644 | 1.0305 | 0.89186 | 120.3626 | 120.55 | 120.0668 | 120.1922 | -119.3212 | -119.0253 | -119.3322 | -119.0363
902.6562 | 121.637 | -120.3735 | 1.1765 | 0.071489 | -0.054257 | 0.010893 | -0.047909 | 0.06831 | 0.058113 | -0.071874 | 1.0414 | 1.169 | 1.0396 | 0.9056 | 120.294 | 120.4813 | 119.9981 | 120.1281 | 120.445 | 120.3193 | 120.3844 | 120.3256 | 120.4418 | 120.4316 | 120.3017 | 1.0643 | 1.1919 | 1.0625 | 0.92849 | 120.3168 | 120.5042 | 120.021 | 120.151 | -119.2525 | -118.9567 | -119.2543 | -118.9585
904.3906 | 121.5363 | -120.4102 | 1.1169 | 0.057754 | -0.058836 | 0.010893 | -0.047909 | 0.072888 | 0.053534 | -0.071874 | 1.0186 | 1.1323 | 0.98927 | 0.85981 | 120.3031 | 120.4996 | 120.021 | 120.1418 | 120.4679 | 120.3513 | 120.421 | 120.3622 | 120.483 | 120.4637 | 120.3383 | 1.0414 | 1.1552 | 1.0122 | 0.8827 | 120.326 | 120.5225 | 120.0439 | 120.1647 | -119.2846 | -119.0025 | -119.3138 | -119.0317
906.1406 | 121.6141 | -120.3873 | 1.0941 | 0.057754 | -0.054257 | 0.010893 | -0.043331 | 0.059155 | 0.053534 | -0.076452 | 0.99566 | 1.1278 | 0.98927 | 0.85065 | 120.3168 | 120.495 | 120.0073 | 120.1418 | 120.445 | 120.333 | 120.3982 | 120.3439 | 120.4464 | 120.4408 | 120.3108 | 1.0185 | 1.1507 | 1.0122 | 0.87354 | 120.3397 | 120.5179 | 120.0302 | 120.1647 | -119.3212 | -119.0116 | -119.3276 | -119.018
907.8906 | 121.6415 | -120.3873 | 1.0712 | 0.057754 | -0.063415 | 0.015472 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 0.99108 | 1.1232 | 0.98011 | 0.84149 | 120.3031 | 120.495 | 120.0073 | 120.1327 | 120.445 | 120.3239 | 120.4027 | 120.3394 | 120.451 | 120.4362 | 120.3154 | 1.014 | 1.1461 | 1.003 | 0.86438 | 120.326 | 120.5179 | 120.0302 | 120.1556 | -119.312 | -119.0162 | -119.323 | -119.0272
909.5781 | 121.7239 | -0.25177 | 121.5591 | 0.089802 | -0.035942 | 0.052101 | -0.025017 | 0.082044 | 0.067269 | -0.058139 | 121.3597 | 121.3263 | 121.3523 | 121.2929 | 0.19474 | 0.2567 | 0.06724 | 0.13875 | 0.34157 | 0.21583 | 0.30387 | 0.22675 | 0.33381 | 0.31904 | 0.19363 | 121.3826 | 121.3492 | 121.3752 | 121.3158 | 0.21762 | 0.27959 | 0.090128 | 0.16164 | 121.165 | 121.2925 | 121.1575 | 121.285
911.3281 | 121.9574 | -0.23804 | 121.6003 | 0.085224 | -0.040521 | 0.038365 | -0.029595 | 0.077466 | 0.067269 | -0.058139 | 121.4742 | 121.4225 | 121.4621 | 121.3845 | 0.181 | 0.25212 | 0.062662 | 0.11586 | 0.32326 | 0.19752 | 0.2764 | 0.20844 | 0.3155 | 0.30531 | 0.1799 | 121.4971 | 121.4453 | 121.485 | 121.4074 | 0.20389 | 0.27501 | 0.08555 | 0.13875 | 121.2932 | 121.4115 | 121.2811 | 121.3995
913.0781 | 121.8933 | -0.25177 | 121.6827 | 0.085224 | -0.0451 | 0.047522 | -0.029595 | 0.082044 | 0.062691 | -0.058139 | 121.52 | 121.4728 | 121.5217 | 121.444 | 0.181 | 0.24754 | 0.053505 | 0.12044 | 0.33699 | 0.20667 | 0.29929 | 0.22217 | 0.33381 | 0.31446 | 0.19363 | 121.5429 | 121.4957 | 121.5445 | 121.4669 | 0.20389 | 0.27043 | 0.076393 | 0.14333 | 121.339 | 121.4665 | 121.3407 | 121.4682
914.8281 | 121.9208 | -0.28381 | 121.7102 | 0.085224 | -0.040521 | 0.038365 | -0.025017 | 0.082044 | 0.067269 | -0.053561 | 121.552 | 121.514 | 121.5583 | 121.4715 | 0.18558 | 0.25212 | 0.058083 | 0.12044 | 0.36904 | 0.24329 | 0.32218 | 0.2588 | 0.36586 | 0.35108 | 0.23025 | 121.5749 | 121.5369 | 121.5812 | 121.4944 | 0.20847 | 0.27501 | 0.080971 | 0.14333 | 121.3664 | 121.4939 | 121.3727 | 121.5002
916.5312 | 121.8979 | -0.2655 | 121.7148 | 0.080646 | -0.040521 | 0.038365 | -0.034174 | 0.082044 | 0.067269 | -0.053561 | 121.5795 | 121.5323 | 121.5858 | 121.499 | 0.18558 | 0.24297 | 0.048926 | 0.11586 | 0.34615 | 0.22498 | 0.30387 | 0.23133 | 0.34755 | 0.33277 | 0.21194 | 121.6024 | 121.5552 | 121.6086 | 121.5219 | 0.20847 | 0.26586 | 0.071814 | 0.13875 | 121.3939 | 121.5306 | 121.4002 | 121.5368
918.2812 | 121.9894 | -0.25177 | 121.6965 | 0.089802 | -0.0451 | 0.033786 | -0.029595 | 0.06831 | 0.067269 | -0.058139 | 121.5978 | 121.5461 | 121.5995 | 121.5173 | 0.17642 | 0.25212 | 0.048926 | 0.11128 | 0.34157 | 0.20667 | 0.28556 | 0.22217 | 0.32008 | 0.31904 | 0.19363 | 121.6207 | 121.569 | 121.6224 | 121.5402 | 0.19931 | 0.27501 | 0.071814 | 0.13417 | 121.4214 | 121.5489 | 121.4231 | 121.5506
920.0156 | 122.049 | -0.27008 | 121.7102 | 0.053175 | -0.040521 | 0.033786 | -0.034174 | 0.082044 | 0.067269 | -0.058139 | 121.6115 | 121.5644 | 121.6178 | 121.5448 | 0.17642 | 0.24297 | 0.048926 | 0.12044 | 0.32326 | 0.22956 | 0.30387 | 0.23591 | 0.35213 | 0.33735 | 0.21194 | 121.6344 | 121.5873 | 121.6407 | 121.5677 | 0.19931 | 0.26586 | 0.071814 | 0.14333 | 121.4351 | 121.5626 | 121.4414 | 121.5689
921.7188 | 122.0306 | -0.26093 | 121.7239 | 0.062332 | -0.049678 | 0.038365 | -0.029595 | 0.082044 | 0.067269 | -0.062717 | 121.6344 | 121.5919 | 121.6407 | 121.5494 | 0.181 | 0.24754 | 0.062662 | 0.11128 | 0.32326 | 0.21125 | 0.29929 | 0.23133 | 0.34297 | 0.32819 | 0.19821 | 121.6573 | 121.6148 | 121.6636 | 121.5722 | 0.20389 | 0.27043 | 0.08555 | 0.13417 | 121.4534 | 121.5718 | 121.4597 | 121.578
923.4531 | 122.049 | -0.25177 | 121.7651 | 0.06691 | -0.040521 | 0.042944 | -0.029595 | 0.077466 | 0.067269 | -0.062717 | 121.6573 | 121.601 | 121.6636 | 121.5722 | 0.17185 | 0.24297 | 0.044348 | 0.11586 | 0.31868 | 0.21125 | 0.29471 | 0.22217 | 0.32924 | 0.31904 | 0.18905 | 121.6802 | 121.6239 | 121.6865 | 121.5951 | 0.19473 | 0.26586 | 0.067236 | 0.13875 | 121.4855 | 121.613 | 121.4917 | 121.6192
925.2031 | 121.9803 | -0.27924 | 121.7697 | 0.071489 | -0.0451 | 0.038365 | -0.038752 | 0.077466 | 0.071848 | -0.053561 | 121.6665 | 121.6193 | 121.6682 | 121.586 | 0.17642 | 0.24297 | 0.048926 | 0.11128 | 0.35072 | 0.23414 | 0.3176 | 0.24048 | 0.3567 | 0.35108 | 0.22567 | 121.6894 | 121.6422 | 121.6911 | 121.6089 | 0.19931 | 0.26586 | 0.071814 | 0.13417 | 121.4901 | 121.6176 | 121.4917 | 121.6192
926.9531 | 122.1085 | -0.22888 | 121.7743 | 0.071489 | -0.0451 | 0.038365 | -0.029595 | 0.082044 | 0.071848 | -0.058139 | 121.6802 | 121.6331 | 121.6911 | 121.5997 | 0.17642 | 0.24297 | 0.053505 | 0.11128 | 0.30037 | 0.18378 | 0.26725 | 0.19929 | 0.31093 | 0.30073 | 0.17074 | 121.7031 | 121.656 | 121.7139 | 121.6226 | 0.19931 | 0.26586 | 0.076393 | 0.13417 | 121.5038 | 121.6267 | 121.5146 | 121.6376
928.6406 | 121.9803 | -0.28381 | 121.8155 | 0.071489 | -0.040521 | 0.038365 | -0.020438 | 0.082044 | 0.076426 | -0.048983 | 121.6894 | 121.6422 | 121.6865 | 121.5997 | 0.181 | 0.23839 | 0.048926 | 0.1067 | 0.3553 | 0.24329 | 0.32218 | 0.26337 | 0.36586 | 0.36024 | 0.23483 | 121.7123 | 121.6651 | 121.7094 | 121.6226 | 0.20389 | 0.26128 | 0.071814 | 0.12959 | 121.5084 | 121.6404 | 121.5055 | 121.6376
930.3906 | 122.0169 | -0.28381 | 121.8201 | 0.071489 | -0.0451 | 0.038365 | -0.025017 | 0.086622 | 0.067269 | -0.058139 | 121.7031 | 121.656 | 121.7048 | 121.6226 | 0.17642 | 0.23381 | 0.048926 | 0.11128 | 0.3553 | 0.23871 | 0.32218 | 0.2588 | 0.37043 | 0.35108 | 0.22567 | 121.726 | 121.6789 | 121.7277 | 121.6455 | 0.19931 | 0.2567 | 0.071814 | 0.13417 | 121.5267 | 121.6542 | 121.5284 | 121.6559
932.1562 | 122.0123 | -0.27466 | 121.8384 | 0.06691 | -0.040521 | 0.029208 | -0.029595 | 0.077466 | 0.067269 | -0.062717 | 121.7077 | 121.6606 | 121.7094 | 121.6226 | 0.17185 | 0.23839 | 0.053505 | 0.1067 | 0.34157 | 0.23414 | 0.30387 | 0.24506 | 0.35212 | 0.34193 | 0.21194 | 121.7306 | 121.6834 | 121.7323 | 121.6455 | 0.19473 | 0.26128 | 0.076393 | 0.12959 | 121.5358 | 121.6542 | 121.5375 | 121.6559
933.8906 | 122.1268 | -0.24719 | 121.788 | 0.062332 | -0.0451 | 0.033786 | -0.01586 | 0.072888 | 0.071848 | -0.053561 | 121.7168 | 121.6651 | 121.7139 | 121.6318 | 0.17642 | 0.24754 | 0.053505 | 0.11586 | 0.30952 | 0.20209 | 0.28098 | 0.23133 | 0.32008 | 0.31904 | 0.19363 | 121.7397 | 121.688 | 121.7368 | 121.6547 | 0.19931 | 0.27043 | 0.076393 | 0.13875 | 121.5404 | 121.6633 | 121.5375 | 121.6604
935.5938 | 122.0032 | -0.29297 | 121.843 | 0.071489 | -0.0451 | 0.042944 | -0.025017 | 0.086622 | 0.067269 | -0.058139 | 121.7306 | 121.6697 | 121.7277 | 121.6409 | 0.18558 | 0.24754 | 0.058083 | 0.11128 | 0.36446 | 0.24787 | 0.33591 | 0.26795 | 0.37959 | 0.36024 | 0.23483 | 121.7535 | 121.6926 | 121.7506 | 121.6638 | 0.20847 | 0.27043 | 0.080971 | 0.13417 | 121.545 | 121.6725 | 121.5421 | 121.6696
937.3438 | 122.0764 | -0.28381 | 121.8658 | 0.071489 | -0.0451 | 0.033786 | -0.025017 | 0.072888 | 0.058113 | -0.058139 | 121.7352 | 121.6834 | 121.7368 | 121.6501 | 0.181 | 0.25212 | 0.044348 | 0.11586 | 0.3553 | 0.23871 | 0.3176 | 0.2588 | 0.3567 | 0.34193 | 0.22567 | 121.758 | 121.7063 | 121.7597 | 121.673 | 0.20389 | 0.27501 | 0.067236 | 0.13875 | 121.5542 | 121.6908 | 121.5558 | 121.6925
939.0781 | 122.049 | -0.31128 | 121.8384 | 0.062332 | -0.040521 | 0.038365 | -0.025017 | 0.077466 | 0.067269 | -0.058139 | 121.7397 | 121.6834 | 121.7323 | 121.6501 | 0.17642 | 0.24297 | 0.048926 | 0.11586 | 0.37361 | 0.27076 | 0.34964 | 0.28626 | 0.38874 | 0.37855 | 0.25314 | 121.7626 | 121.7063 | 121.7551 | 121.673 | 0.19931 | 0.26586 | 0.071814 | 0.13875 | 121.5633 | 121.6908 | 121.5558 | 121.6833
940.8281 | 122.0306 | -0.3067 | 121.8246 | 0.06691 | -0.049678 | 0.038365 | -0.029595 | 0.082044 | 0.067269 | -0.048983 | 121.7306 | 121.6743 | 121.7185 | 121.6409 | 0.19474 | 0.26586 | 0.062662 | 0.12502 | 0.37361 | 0.25702 | 0.34507 | 0.27711 | 0.38875 | 0.37397 | 0.25772 | 121.7535 | 121.6972 | 121.7414 | 121.6638 | 0.21762 | 0.28875 | 0.08555 | 0.1479 | 121.5358 | 121.6679 | 121.5238 | 121.6559
942.5156 | 122.049 | -0.32044 | 121.8384 | 0.06691 | -0.0451 | 0.042944 | -0.034174 | 0.077466 | 0.062691 | -0.058139 | 121.7352 | 121.6834 | 121.7323 | 121.6364 | 0.19931 | 0.27044 | 0.071818 | 0.14333 | 0.38735 | 0.27533 | 0.36338 | 0.28626 | 0.3979 | 0.38313 | 0.2623 | 121.758 | 121.7063 | 121.7551 | 121.6592 | 0.2222 | 0.29332 | 0.094706 | 0.16622 | 121.5358 | 121.6633 | 121.5329 | 121.6604
944.2656 | 122.0764 | -0.31128 | 121.8384 | 0.06691 | -0.035942 | 0.033786 | -0.025017 | 0.072888 | 0.067269 | -0.058139 | 121.7352 | 121.6743 | 121.7277 | 121.6455 | 0.20389 | 0.27959 | 0.071818 | 0.13417 | 0.37819 | 0.27534 | 0.34506 | 0.28626 | 0.38417 | 0.37855 | 0.25314 | 121.758 | 121.6972 | 121.7506 | 121.6684 | 0.22678 | 0.30248 | 0.094706 | 0.15706 | 121.5313 | 121.6633 | 121.5238 | 121.6559
946.0156 | 122.1405 | -0.28839 | 121.8063 | 0.06691 | -0.040521 | 0.033786 | -0.025017 | 0.077466 | 0.062691 | -0.053561 | 121.726 | 121.6651 | 121.7185 | 121.6364 | 0.21305 | 0.29333 | 0.076397 | 0.15249 | 0.3553 | 0.24787 | 0.32218 | 0.26337 | 0.36586 | 0.35108 | 0.23483 | 121.7489 | 121.688 | 121.7414 | 121.6592 | 0.23594 | 0.31621 | 0.099285 | 0.17537 | 121.5129 | 121.6496 | 121.5055 | 121.6421
947.7031 | 122.2183 | -0.30212 | 121.7651 | 0.06691 | -0.0451 | 0.033786 | -0.034174 | 0.086622 | 0.067269 | -0.062717 | 121.7214 | 121.6697 | 121.7231 | 121.6318 | 0.22221 | 0.2979 | 0.09471 | 0.15706 | 0.36903 | 0.25702 | 0.33591 | 0.26795 | 0.38875 | 0.36939 | 0.23941 | 121.7443 | 121.6926 | 121.746 | 121.6547 | 0.24509 | 0.32079 | 0.1176 | 0.17995 | 121.4992 | 121.6267 | 121.5009 | 121.6284
949.4531 | 122.0535 | -0.35248 | 121.8475 | 0.06691 | -0.049678 | 0.038365 | -0.029595 | 0.082044 | 0.067269 | -0.053561 | 121.7214 | 121.6606 | 121.7231 | 121.6364 | 0.21305 | 0.30248 | 0.090132 | 0.15706 | 0.41939 | 0.3028 | 0.39084 | 0.32288 | 0.43452 | 0.41975 | 0.29892 | 121.7443 | 121.6834 | 121.746 | 121.6592 | 0.23594 | 0.32537 | 0.11302 | 0.17995 | 121.5084 | 121.6313 | 121.5101 | 121.633
951.2031 | 122.168 | -0.3067 | 121.8475 | 0.057754 | -0.0451 | 0.042944 | -0.029595 | 0.072888 | 0.067269 | -0.058139 | 121.7352 | 121.6789 | 121.7277 | 121.6501 | 0.21763 | 0.2979 | 0.085554 | 0.16164 | 0.36446 | 0.2616 | 0.34965 | 0.27711 | 0.37959 | 0.37397 | 0.24856 | 121.758 | 121.7018 | 121.7506 | 121.673 | 0.24052 | 0.32079 | 0.10844 | 0.18453 | 121.5175 | 121.6496 | 121.5101 | 121.6421
952.9531 | 122.2137 | -0.31128 | 121.7972 | 0.06691 | -0.049678 | 0.033786 | -0.025017 | 0.077466 | 0.067269 | -0.062717 | 121.7443 | 121.6834 | 121.7323 | 121.6455 | 0.21305 | 0.30248 | 0.090132 | 0.14791 | 0.37819 | 0.2616 | 0.34506 | 0.28626 | 0.38874 | 0.37855 | 0.24856 | 121.7672 | 121.7063 | 121.7551 | 121.6684 | 0.23594 | 0.32537 | 0.11302 | 0.1708 | 121.5313 | 121.6542 | 121.5192 | 121.6421
954.6406 | 122.1497 | -0.32501 | 121.8292 | 0.06691 | -0.040521 | 0.038365 | -0.029595 | 0.082044 | 0.076426 | -0.058139 | 121.7489 | 121.6972 | 121.7368 | 121.6593 | 0.22221 | 0.2979 | 0.099289 | 0.15706 | 0.39192 | 0.28449 | 0.36338 | 0.29542 | 0.40706 | 0.40144 | 0.26687 | 121.7718 | 121.7201 | 121.7597 | 121.6821 | 0.24509 | 0.32079 | 0.12218 | 0.17995 | 121.5267 | 121.6496 | 121.5146 | 121.6375
956.4062 | 122.1451 | -0.34332 | 121.8567 | 0.062332 | -0.049678 | 0.042944 | -0.025017 | 0.077466 | 0.067269 | -0.058139 | 121.758 | 121.6972 | 121.7506 | 121.6638 | 0.21763 | 0.30248 | 0.080975 | 0.15706 | 0.40565 | 0.29364 | 0.38627 | 0.31831 | 0.42079 | 0.41059 | 0.28518 | 121.7809 | 121.7201 | 121.7735 | 121.6867 | 0.24052 | 0.32537 | 0.10386 | 0.17995 | 121.5404 | 121.6771 | 121.5329 | 121.6696
958.1562 | 122.2275 | -0.31128 | 121.8338 | 0.062332 | -0.0451 | 0.033786 | -0.029595 | 0.072888 | 0.067269 | -0.058139 | 121.758 | 121.7063 | 121.7552 | 121.6638 | 0.22221 | 0.30248 | 0.090132 | 0.16164 | 0.37361 | 0.26618 | 0.34506 | 0.28168 | 0.38417 | 0.37855 | 0.25314 | 121.7809 | 121.7292 | 121.778 | 121.6867 | 0.24509 | 0.32537 | 0.11302 | 0.18453 | 121.5358 | 121.6679 | 121.5329 | 121.665
959.8906 | 122.2229 | -0.29755 | 121.8292 | 0.071489 | -0.049678 | 0.038365 | -0.029595 | 0.082044 | 0.062691 | -0.058139 | 121.7672 | 121.7063 | 121.7597 | 121.6684 | 0.21305 | 0.2979 | 0.080975 | 0.15249 | 0.36904 | 0.24787 | 0.33591 | 0.26795 | 0.37959 | 0.36024 | 0.23941 | 121.7901 | 121.7292 | 121.7826 | 121.6913 | 0.23594 | 0.32079 | 0.10386 | 0.17537 | 121.5542 | 121.6862 | 121.5467 | 121.6788
961.6406 | 122.2275 | -0.3067 | 121.8613 | 0.053175 | -0.0451 | 0.042944 | -0.029595 | 0.082044 | 0.067269 | -0.058139 | 121.7672 | 121.7201 | 121.7689 | 121.673 | 0.21305 | 0.29333 | 0.080975 | 0.15249 | 0.35988 | 0.2616 | 0.34965 | 0.27711 | 0.38875 | 0.37397 | 0.24856 | 121.7901 | 121.743 | 121.7918 | 121.6959 | 0.23594 | 0.31621 | 0.10386 | 0.17537 | 121.5542 | 121.6862 | 121.5558 | 121.6879
963.3906 | 122.2321 | -0.30212 | 121.8384 | 0.062332 | -0.0451 | 0.038365 | -0.034174 | 0.082044 | 0.071848 | -0.058139 | 121.7764 | 121.7292 | 121.7735 | 121.6913 | 0.21305 | 0.29333 | 0.085554 | 0.14791 | 0.36446 | 0.25702 | 0.34049 | 0.26795 | 0.38417 | 0.37397 | 0.24399 | 121.7992 | 121.7521 | 121.7964 | 121.7142 | 0.23594 | 0.31621 | 0.10844 | 0.1708 | 121.5633 | 121.6908 | 121.5604 | 121.6879
965.0781 | 122.1588 | -0.32044 | 121.8796 | 0.062332 | -0.0451 | 0.029208 | -0.020438 | 0.077466 | 0.067269 | -0.058139 | 121.7901 | 121.7338 | 121.7826 | 121.7005 | 0.20389 | 0.2979 | 0.085554 | 0.14333 | 0.38277 | 0.27533 | 0.34964 | 0.3 | 0.3979 | 0.3877 | 0.2623 | 121.813 | 121.7567 | 121.8055 | 121.7233 | 0.22678 | 0.32079 | 0.10844 | 0.16622 | 121.5862 | 121.7045 | 121.5787 | 121.6971
966.8594 | 122.1359 | -0.34332 | 121.8704 | 0.062332 | -0.049678 | 0.033786 | -0.020438 | 0.082044 | 0.067269 | -0.053561 | 121.7901 | 121.7338 | 121.7918 | 121.6959 | 0.21305 | 0.2979 | 0.080975 | 0.14791 | 0.40565 | 0.29364 | 0.37711 | 0.32288 | 0.42537 | 0.41059 | 0.28976 | 121.813 | 121.7567 | 121.8147 | 121.7188 | 0.23594 | 0.32079 | 0.10386 | 0.1708 | 121.577 | 121.7091 | 121.5787 | 121.7108
968.5469 | 122.2595 | -0.30212 | 121.8521 | 0.057754 | -0.049678 | 0.029208 | -0.029595 | 0.077466 | 0.062691 | -0.048983 | 121.7993 | 121.7521 | 121.7918 | 121.7096 | 0.21305 | 0.28875 | 0.080975 | 0.15249 | 0.35988 | 0.25245 | 0.33133 | 0.27253 | 0.37959 | 0.36482 | 0.25314 | 121.8221 | 121.775 | 121.8147 | 121.7325 | 0.23594 | 0.31164 | 0.10386 | 0.17537 | 121.5862 | 121.7183 | 121.5787 | 121.7108
970.2969 | 122.1771 | -0.32044 | 121.9162 | 0.06691 | -0.040521 | 0.042944 | -0.025017 | 0.082044 | 0.067269 | -0.062717 | 121.7947 | 121.743 | 121.8009 | 121.705 | 0.21763 | 0.29333 | 0.090132 | 0.15706 | 0.38735 | 0.27991 | 0.36338 | 0.29542 | 0.40248 | 0.3877 | 0.25772 | 121.8176 | 121.7659 | 121.8238 | 121.7279 | 0.24052 | 0.31621 | 0.11302 | 0.17995 | 121.577 | 121.7045 | 121.5833 | 121.7108
972.0469 | 122.1405 | -0.3479 | 121.9025 | 0.06691 | -0.040521 | 0.033786 | -0.025017 | 0.077466 | 0.067269 | -0.058139 | 121.7993 | 121.7384 | 121.7918 | 121.7005 | 0.21763 | 0.30248 | 0.090132 | 0.15249 | 0.41481 | 0.30738 | 0.38169 | 0.32288 | 0.42537 | 0.41517 | 0.28976 | 121.8221 | 121.7613 | 121.8147 | 121.7233 | 0.24052 | 0.32537 | 0.11302 | 0.17537 | 121.5816 | 121.7091 | 121.5741 | 121.7016
973.8125 | 122.1954 | -0.33417 | 121.9208 | 0.06691 | -0.040521 | 0.038365 | -0.029595 | 0.086622 | 0.058113 | -0.062717 | 121.813 | 121.7475 | 121.8009 | 121.7096 | 0.21305 | 0.29333 | 0.085554 | 0.15249 | 0.40108 | 0.29365 | 0.37253 | 0.30457 | 0.42079 | 0.39228 | 0.27145 | 121.8359 | 121.7704 | 121.8238 | 121.7325 | 0.23594 | 0.31621 | 0.10844 | 0.17537 | 121.5999 | 121.7274 | 121.5879 | 121.7154
975.5156 | 122.287 | -0.29297 | 121.8658 | 0.06691 | -0.049678 | 0.029208 | -0.025017 | 0.072888 | 0.062691 | -0.044405 | 121.8084 | 121.7521 | 121.8055 | 121.7096 | 0.21763 | 0.30248 | 0.090132 | 0.15249 | 0.35988 | 0.24329 | 0.32218 | 0.26795 | 0.36586 | 0.35566 | 0.24856 | 121.8313 | 121.775 | 121.8284 | 121.7325 | 0.24052 | 0.32537 | 0.11302 | 0.17537 | 121.5908 | 121.7183 | 121.5879 | 121.7154
977.2656 | 122.2641 | -0.29755 | 121.8704 | 0.057754 | -0.054257 | 0.038365 | -0.029595 | 0.072888 | 0.062691 | -0.058139 | 121.8038 | 121.7521 | 121.8009 | 121.7096 | 0.21305 | 0.2979 | 0.09471 | 0.16164 | 0.3553 | 0.24329 | 0.33591 | 0.26795 | 0.37043 | 0.36024 | 0.23941 | 121.8267 | 121.775 | 121.8238 | 121.7325 | 0.23594 | 0.32079 | 0.1176 | 0.18453 | 121.5908 | 121.7091 | 121.5879 | 121.7062
979 | 122.168 | -0.34332 | 121.9162 | 0.062332 | -0.0451 | 0.038365 | -0.029595 | 0.086622 | 0.067269 | -0.058139 | 121.813 | 121.7567 | 121.8101 | 121.7142 | 0.21763 | 0.30248 | 0.090132 | 0.15706 | 0.40565 | 0.29822 | 0.38169 | 0.31373 | 0.42995 | 0.41059 | 0.28518 | 121.8359 | 121.7796 | 121.833 | 121.7371 | 0.24052 | 0.32537 | 0.11302 | 0.17995 | 121.5954 | 121.7229 | 121.5925 | 121.72
980.6875 | 122.2687 | -0.29297 | 121.875 | 0.062332 | -0.049678 | 0.042944 | -0.020438 | 0.06831 | 0.067269 | -0.058139 | 121.8221 | 121.7659 | 121.8147 | 121.7234 | 0.21305 | 0.2979 | 0.09471 | 0.15249 | 0.3553 | 0.24329 | 0.33591 | 0.27253 | 0.36128 | 0.36024 | 0.23483 | 121.845 | 121.7888 | 121.8376 | 121.7462 | 0.23594 | 0.32079 | 0.1176 | 0.17537 | 121.6091 | 121.7274 | 121.6016 | 121.72
982.4531 | 122.3007 | -0.31128 | 121.8796 | 0.062332 | -0.054257 | 0.038365 | -0.029595 | 0.072888 | 0.062691 | -0.062717 | 121.8221 | 121.7704 | 121.8192 | 121.7371 | 0.20847 | 0.28417 | 0.085554 | 0.15249 | 0.37361 | 0.25702 | 0.34964 | 0.28168 | 0.38417 | 0.37397 | 0.24856 | 121.845 | 121.7933 | 121.8421 | 121.76 | 0.23136 | 0.30706 | 0.10844 | 0.17537 | 121.6137 | 121.7366 | 121.6108 | 121.7337
984.1875 | 122.1451 | -0.35248 | 121.9208 | 0.071489 | -0.049678 | 0.042944 | -0.020438 | 0.082044 | 0.071848 | -0.044405 | 121.8313 | 121.775 | 121.8238 | 121.7371 | 0.21305 | 0.29333 | 0.085554 | 0.15706 | 0.42397 | 0.3028 | 0.39542 | 0.33204 | 0.43452 | 0.42433 | 0.30807 | 121.8542 | 121.7979 | 121.8467 | 121.76 | 0.23594 | 0.31621 | 0.10844 | 0.17995 | 121.6183 | 121.7457 | 121.6108 | 121.7383
985.9375 | 122.2046 | -0.34332 | 121.9162 | 0.062332 | -0.049678 | 0.038365 | -0.025017 | 0.072888 | 0.067269 | -0.053561 | 121.8313 | 121.7796 | 121.8238 | 121.7325 | 0.21305 | 0.29333 | 0.090132 | 0.15249 | 0.40565 | 0.29364 | 0.38169 | 0.31831 | 0.41621 | 0.41059 | 0.28976 | 121.8542 | 121.8025 | 121.8467 | 121.7554 | 0.23594 | 0.31621 | 0.11302 | 0.17537 | 121.6183 | 121.7412 | 121.6108 | 121.7337
987.6406 | 122.287 | -0.28839 | 121.8796 | 0.062332 | -0.035942 | 0.033786 | -0.025017 | 0.077466 | 0.062691 | -0.048983 | 121.8313 | 121.7704 | 121.8192 | 121.7325 | 0.21763 | 0.2979 | 0.090132 | 0.15249 | 0.35072 | 0.25245 | 0.32218 | 0.26337 | 0.36586 | 0.35108 | 0.23941 | 121.8542 | 121.7933 | 121.8421 | 121.7554 | 0.24052 | 0.32079 | 0.11302 | 0.17537 | 121.6137 | 121.7412 | 121.6016 | 121.7291
989.4062 | 122.2137 | -0.33875 | 121.9116 | 0.071489 | -0.0451 | 0.042944 | -0.034174 | 0.077466 | 0.067269 | -0.048983 | 121.8359 | 121.775 | 121.8238 | 121.7371 | 0.20847 | 0.2979 | 0.085554 | 0.15249 | 0.41023 | 0.29365 | 0.38169 | 0.30457 | 0.41621 | 0.40601 | 0.28976 | 121.8588 | 121.7979 | 121.8467 | 121.76 | 0.23136 | 0.32079 | 0.10844 | 0.17537 | 121.6274 | 121.7503 | 121.6154 | 121.7383
991.0938 | 122.2733 | -0.33875 | 121.8796 | 0.062332 | -0.040521 | 0.038365 | -0.029595 | 0.082044 | 0.067269 | -0.062717 | 121.8313 | 121.775 | 121.8284 | 121.7279 | 0.21763 | 0.30248 | 0.09471 | 0.16622 | 0.40108 | 0.29822 | 0.37711 | 0.30915 | 0.42079 | 0.40601 | 0.27603 | 121.8542 | 121.7979 | 121.8513 | 121.7508 | 0.24052 | 0.32537 | 0.1176 | 0.18911 | 121.6137 | 121.7366 | 121.6108 | 121.7337
992.875 | 122.1542 | -0.35706 | 121.9345 | 0.06691 | -0.0451 | 0.038365 | -0.025017 | 0.082044 | 0.067269 | -0.053561 | 121.8405 | 121.7842 | 121.833 | 121.7371 | 0.21763 | 0.30248 | 0.090132 | 0.16164 | 0.42397 | 0.31196 | 0.39542 | 0.33204 | 0.4391 | 0.42432 | 0.30349 | 121.8633 | 121.8071 | 121.8559 | 121.76 | 0.24052 | 0.32537 | 0.11302 | 0.18453 | 121.6228 | 121.7503 | 121.6154 | 121.7429
994.5625 | 122.1909 | -0.36621 | 121.9208 | 0.071489 | -0.0451 | 0.038365 | -0.025017 | 0.077466 | 0.067269 | -0.058139 | 121.8405 | 121.7842 | 121.8376 | 121.7508 | 0.22221 | 0.30248 | 0.090132 | 0.16622 | 0.4377 | 0.32111 | 0.40458 | 0.34119 | 0.44368 | 0.43348 | 0.30807 | 121.8633 | 121.8071 | 121.8604 | 121.7737 | 0.24509 | 0.32537 | 0.11302 | 0.18911 | 121.6183 | 121.7503 | 121.6154 | 121.7474
996.3281 | 122.3145 | -0.29755 | 121.8842 | 0.062332 | -0.049678 | 0.033786 | -0.034174 | 0.077466 | 0.062691 | -0.048983 | 121.845 | 121.7842 | 121.8376 | 121.7417 | 0.22678 | 0.2979 | 0.085554 | 0.15706 | 0.35988 | 0.24787 | 0.33133 | 0.26337 | 0.37501 | 0.36024 | 0.24856 | 121.8679 | 121.8071 | 121.8604 | 121.7646 | 0.24967 | 0.32079 | 0.10844 | 0.17995 | 121.6183 | 121.7595 | 121.6108 | 121.752
998.0781 | 122.168 | -0.34332 | 121.9574 | 0.071489 | -0.049678 | 0.038365 | -0.020438 | 0.086622 | 0.062691 | -0.053561 | 121.8496 | 121.7888 | 121.8467 | 121.7508 | 0.21763 | 0.2979 | 0.090132 | 0.16164 | 0.41481 | 0.29364 | 0.38169 | 0.32288 | 0.42995 | 0.40601 | 0.28976 | 121.8725 | 121.8116 | 121.8696 | 121.7737 | 0.24052 | 0.32079 | 0.11302 | 0.18453 | 121.632 | 121.7595 | 121.6291 | 121.7566
999.8438 | 122.287 | -0.3067 | 121.8933 | 0.062332 | -0.049678 | 0.038365 | -0.029595 | 0.077466 | 0.071848 | -0.058139 | 121.8588 | 121.7979 | 121.8513 | 121.7508 | 0.21305 | 0.2979 | 0.090132 | 0.15706 | 0.36903 | 0.25702 | 0.34507 | 0.27711 | 0.38417 | 0.37855 | 0.24856 | 121.8817 | 121.8208 | 121.8742 | 121.7737 | 0.23594 | 0.32079 | 0.11302 | 0.17995 | 121.6457 | 121.7686 | 121.6382 | 121.7612
1001.5469 | 122.2961 | -0.33875 | 121.8979 | 0.062332 | -0.049678 | 0.038365 | -0.029595 | 0.077466 | 0.062691 | -0.058139 | 121.8542 | 121.7888 | 121.8513 | 121.7554 | 0.21763 | 0.30706 | 0.090132 | 0.16622 | 0.40108 | 0.28907 | 0.37711 | 0.30915 | 0.41621 | 0.40144 | 0.28061 | 121.8771 | 121.8116 | 121.8742 | 121.7783 | 0.24052 | 0.32995 | 0.11302 | 0.18911 | 121.6366 | 121.7641 | 121.6337 | 121.7612
1003.2344 | 122.3236 | -0.30212 | 121.8933 | 0.06691 | -0.049678 | 0.038365 | -0.025017 | 0.082044 | 0.071848 | -0.062717 | 121.8634 | 121.7979 | 121.8559 | 121.7554 | 0.22221 | 0.29333 | 0.09471 | 0.15706 | 0.36903 | 0.25245 | 0.34049 | 0.27711 | 0.38417 | 0.37397 | 0.23941 | 121.8862 | 121.8208 | 121.8788 | 121.7783 | 0.24509 | 0.31621 | 0.1176 | 0.17995 | 121.6411 | 121.7686 | 121.6337 | 121.7612
1004.9844 | 122.1909 | -0.35706 | 121.9345 | 0.062332 | -0.054257 | 0.033786 | -0.029595 | 0.077466 | 0.062691 | -0.058139 | 121.8679 | 121.8117 | 121.8605 | 121.7646 | 0.21305 | 0.2979 | 0.090132 | 0.15706 | 0.41939 | 0.3028 | 0.39084 | 0.32746 | 0.43452 | 0.41975 | 0.29892 | 121.8908 | 121.8345 | 121.8833 | 121.7875 | 0.23594 | 0.32079 | 0.11302 | 0.17995 | 121.6549 | 121.7778 | 121.6474 | 121.7703
1006.6719 | 122.3373 | -0.30212 | 121.9116 | 0.062332 | -0.049678 | 0.029208 | -0.020438 | 0.082044 | 0.067269 | -0.058139 | 121.8725 | 121.8071 | 121.8605 | 121.7691 | 0.22221 | 0.29333 | 0.09471 | 0.15249 | 0.36446 | 0.25245 | 0.33133 | 0.28169 | 0.38417 | 0.36939 | 0.24399 | 121.8954 | 121.83 | 121.8833 | 121.792 | 0.24509 | 0.31621 | 0.1176 | 0.17537 | 121.6503 | 121.7778 | 121.6382 | 121.7657
1008.4219 | 122.3099 | -0.31586 | 121.9345 | 0.057754 | -0.049678 | 0.038365 | -0.034174 | 0.082044 | 0.062691 | -0.058139 | 121.8725 | 121.8162 | 121.8605 | 121.7691 | 0.21763 | 0.2979 | 0.099289 | 0.16164 | 0.37361 | 0.26618 | 0.35422 | 0.28168 | 0.3979 | 0.37855 | 0.25772 | 121.8954 | 121.8391 | 121.8833 | 121.792 | 0.24052 | 0.32079 | 0.12218 | 0.18453 | 121.6549 | 121.7732 | 121.6428 | 121.7612
1010.1094 | 122.3007 | -0.30212 | 121.9162 | 0.057754 | -0.0451 | 0.038365 | -0.025017 | 0.082044 | 0.062691 | -0.053561 | 121.8817 | 121.8162 | 121.8696 | 121.7737 | 0.21305 | 0.2979 | 0.09471 | 0.16164 | 0.35988 | 0.25702 | 0.34049 | 0.27711 | 0.38417 | 0.36482 | 0.24856 | 121.9046 | 121.8391 | 121.8925 | 121.7966 | 0.23594 | 0.32079 | 0.1176 | 0.18453 | 121.6686 | 121.787 | 121.6566 | 121.7749
1011.8594 | 122.2412 | -0.35248 | 121.9391 | 0.062332 | -0.0451 | 0.042944 | -0.034174 | 0.082044 | 0.067269 | -0.058139 | 121.8862 | 121.8162 | 121.8696 | 121.7737 | 0.21763 | 0.28875 | 0.090132 | 0.15249 | 0.41481 | 0.30738 | 0.39542 | 0.3183 | 0.43452 | 0.41975 | 0.29434 | 121.9091 | 121.8391 | 121.8925 | 121.7966 | 0.24052 | 0.31164 | 0.11302 | 0.17537 | 121.6686 | 121.7961 | 121.652 | 121.7795
1013.5469 | 122.3099 | -0.33417 | 121.907 | 0.06691 | -0.049678 | 0.038365 | -0.034174 | 0.077466 | 0.062691 | -0.058139 | 121.8771 | 121.8162 | 121.8696 | 121.7737 | 0.20847 | 0.2979 | 0.085554 | 0.15706 | 0.40108 | 0.28449 | 0.37253 | 0.29999 | 0.41163 | 0.39686 | 0.27603 | 121.9 | 121.8391 | 121.8925 | 121.7966 | 0.23136 | 0.32079 | 0.10844 | 0.17995 | 121.6686 | 121.7915 | 121.6611 | 121.7841
1015.2344 | 122.3145 | -0.3067 | 121.9299 | 0.06691 | -0.049678 | 0.029208 | -0.025017 | 0.072888 | 0.062691 | -0.062717 | 121.8817 | 121.8391 | 121.8788 | 121.7875 | 0.21305 | 0.30248 | 0.090132 | 0.15706 | 0.37361 | 0.25702 | 0.33591 | 0.28168 | 0.37959 | 0.36939 | 0.24398 | 121.9046 | 121.862 | 121.9017 | 121.8104 | 0.23594 | 0.32537 | 0.11302 | 0.17995 | 121.6686 | 121.7915 | 121.6657 | 121.7886
1017 | 122.287 | -0.32501 | 121.962 | 0.057754 | -0.049678 | 0.029208 | -0.029595 | 0.082044 | 0.062691 | -0.053561 | 121.8862 | 121.8254 | 121.8788 | 121.7875 | 0.21305 | 0.30248 | 0.090132 | 0.15249 | 0.38277 | 0.27533 | 0.35422 | 0.29542 | 0.40706 | 0.3877 | 0.27145 | 121.9091 | 121.8483 | 121.9017 | 121.8104 | 0.23594 | 0.32537 | 0.11302 | 0.17537 | 121.6732 | 121.7961 | 121.6657 | 121.7886
1018.6875 | 122.319 | -0.32044 | 121.9116 | 0.071489 | -0.0451 | 0.042944 | -0.034174 | 0.077466 | 0.067269 | -0.062717 | 121.8862 | 121.8208 | 121.8833 | 121.7783 | 0.21305 | 0.2979 | 0.085554 | 0.16622 | 0.39192 | 0.27533 | 0.36338 | 0.28626 | 0.3979 | 0.3877 | 0.25772 | 121.9091 | 121.8437 | 121.9062 | 121.8012 | 0.23594 | 0.32079 | 0.10844 | 0.18911 | 121.6732 | 121.8007 | 121.6703 | 121.7978
1020.4375 | 122.2412 | -0.35248 | 121.9666 | 0.057754 | -0.0451 | 0.038365 | -0.029595 | 0.082044 | 0.076426 | -0.048983 | 121.8862 | 121.83 | 121.8833 | 121.7829 | 0.21305 | 0.30706 | 0.09471 | 0.15706 | 0.41023 | 0.30738 | 0.39084 | 0.32288 | 0.43452 | 0.4289 | 0.3035 | 121.9091 | 121.8529 | 121.9062 | 121.8058 | 0.23594 | 0.32995 | 0.1176 | 0.17995 | 121.6732 | 121.7915 | 121.6703 | 121.7886
1022.1875 | 122.2321 | -0.35248 | 121.9574 | 0.062332 | -0.049678 | 0.038365 | -0.029595 | 0.082044 | 0.067269 | -0.053561 | 121.8862 | 121.83 | 121.8788 | 121.7783 | 0.22221 | 0.30248 | 0.099289 | 0.1708 | 0.41481 | 0.3028 | 0.39084 | 0.32288 | 0.43452 | 0.41975 | 0.29892 | 121.9091 | 121.8529 | 121.9017 | 121.8012 | 0.24509 | 0.32537 | 0.12218 | 0.19369 | 121.664 | 121.787 | 121.6566 | 121.7795
1023.9375 | 122.2183 | -0.36163 | 121.9299 | 0.062332 | -0.049678 | 0.033786 | -0.020438 | 0.077466 | 0.071848 | -0.062717 | 121.8908 | 121.83 | 121.8788 | 121.7875 | 0.21763 | 0.31164 | 0.09471 | 0.1708 | 0.42396 | 0.31195 | 0.39542 | 0.34119 | 0.4391 | 0.43348 | 0.29892 | 121.9137 | 121.8529 | 121.9017 | 121.8104 | 0.24052 | 0.33453 | 0.1176 | 0.19369 | 121.6732 | 121.7961 | 121.6611 | 121.7841
1025.625 | 122.3099 | -0.32501 | 121.9482 | 0.06691 | -0.058836 | 0.038365 | -0.029595 | 0.077466 | 0.067269 | -0.048983 | 121.8862 | 121.8345 | 121.8879 | 121.792 | 0.22221 | 0.30706 | 0.099289 | 0.16622 | 0.39192 | 0.26618 | 0.36338 | 0.29542 | 0.40248 | 0.39228 | 0.27603 | 121.9091 | 121.8574 | 121.9108 | 121.8149 | 0.24509 | 0.32995 | 0.12218 | 0.18911 | 121.664 | 121.787 | 121.6657 | 121.7886
1027.3906 | 122.2092 | -0.36621 | 121.962 | 0.06691 | -0.0451 | 0.038365 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 121.8862 | 121.8254 | 121.8788 | 121.7829 | 0.23594 | 0.31622 | 0.10387 | 0.17538 | 0.43312 | 0.32111 | 0.40458 | 0.34577 | 0.45283 | 0.43806 | 0.31723 | 121.9091 | 121.8483 | 121.9017 | 121.8058 | 0.25883 | 0.3391 | 0.12676 | 0.19826 | 121.6503 | 121.7824 | 121.6428 | 121.7749
1029.1406 | 122.3236 | -0.32959 | 121.9482 | 0.062332 | -0.058836 | 0.038365 | -0.025017 | 0.077466 | 0.058113 | -0.058139 | 121.9 | 121.8345 | 121.8879 | 121.792 | 0.22678 | 0.31164 | 0.099289 | 0.1708 | 0.39192 | 0.27075 | 0.36795 | 0.30457 | 0.40706 | 0.3877 | 0.27145 | 121.9229 | 121.8574 | 121.9108 | 121.8149 | 0.24967 | 0.33453 | 0.12218 | 0.19369 | 121.6732 | 121.8007 | 121.6611 | 121.7886
1030.9062 | 122.3007 | -0.35248 | 121.9482 | 0.06691 | -0.054257 | 0.033786 | -0.029595 | 0.077466 | 0.071848 | -0.053561 | 121.9046 | 121.8437 | 121.9017 | 121.7966 | 0.22678 | 0.30706 | 0.10387 | 0.16622 | 0.41939 | 0.29822 | 0.38626 | 0.32288 | 0.42994 | 0.42433 | 0.29892 | 121.9274 | 121.8666 | 121.9245 | 121.8195 | 0.24967 | 0.32995 | 0.12676 | 0.18911 | 121.6778 | 121.8007 | 121.6749 | 121.7978
1032.5938 | 122.2412 | -0.37537 | 121.994 | 0.062332 | -0.063415 | 0.033786 | -0.025017 | 0.077466 | 0.067269 | -0.058139 | 121.9 | 121.8437 | 121.9017 | 121.792 | 0.23594 | 0.31622 | 0.099289 | 0.1708 | 0.4377 | 0.31195 | 0.40915 | 0.35035 | 0.45283 | 0.44264 | 0.31723 | 121.9229 | 121.8666 | 121.9245 | 121.8149 | 0.25883 | 0.3391 | 0.12218 | 0.19369 | 121.664 | 121.8007 | 121.6657 | 121.8024
1034.3438 | 122.3007 | -0.33417 | 121.9162 | 0.06691 | -0.0451 | 0.029208 | -0.029595 | 0.082044 | 0.058113 | -0.048983 | 121.8954 | 121.83 | 121.8925 | 121.792 | 0.21763 | 0.31164 | 0.099289 | 0.16622 | 0.40108 | 0.28907 | 0.36338 | 0.30457 | 0.41621 | 0.39228 | 0.28518 | 121.9183 | 121.8529 | 121.9154 | 121.8149 | 0.24052 | 0.33453 | 0.12218 | 0.18911 | 121.6778 | 121.7961 | 121.6749 | 121.7932
1036.0938 | 122.2549 | -0.37537 | 121.9986 | 0.057754 | -0.049678 | 0.033786 | -0.029595 | 0.082044 | 0.071848 | -0.062717 | 121.8954 | 121.8345 | 121.8971 | 121.7966 | 0.22221 | 0.31622 | 0.099289 | 0.17996 | 0.43312 | 0.32569 | 0.40915 | 0.34577 | 0.45741 | 0.44721 | 0.31265 | 121.9183 | 121.8574 | 121.92 | 121.8195 | 0.24509 | 0.3391 | 0.12218 | 0.20284 | 121.6732 | 121.7961 | 121.6749 | 121.7978
1037.875 | 122.2412 | -0.37537 | 121.9437 | 0.071489 | -0.049678 | 0.042944 | -0.029595 | 0.086622 | 0.062691 | -0.053561 | 121.8954 | 121.83 | 121.8925 | 121.7829 | 0.23136 | 0.32995 | 0.099289 | 0.17538 | 0.44686 | 0.32569 | 0.41831 | 0.34577 | 0.46199 | 0.43806 | 0.32181 | 121.9183 | 121.8529 | 121.9154 | 121.8058 | 0.25425 | 0.35284 | 0.12218 | 0.19826 | 121.664 | 121.7961 | 121.6611 | 121.7932
1039.5625 | 122.2504 | -0.39368 | 121.9803 | 0.06691 | -0.049678 | 0.033786 | -0.020438 | 0.082044 | 0.062691 | -0.058139 | 121.9 | 121.83 | 121.8971 | 121.7966 | 0.23594 | 0.32537 | 0.10845 | 0.17996 | 0.46059 | 0.344 | 0.42746 | 0.37324 | 0.47572 | 0.45637 | 0.33554 | 121.9229 | 121.8529 | 121.92 | 121.8195 | 0.25883 | 0.34826 | 0.13133 | 0.20284 | 121.664 | 121.7915 | 121.6611 | 121.7886
1041.3125 | 122.3831 | -0.33417 | 121.9528 | 0.062332 | -0.049678 | 0.033786 | -0.034174 | 0.077466 | 0.067269 | -0.058139 | 121.9137 | 121.8437 | 121.9017 | 121.8104 | 0.22678 | 0.31164 | 0.10387 | 0.16622 | 0.3965 | 0.28449 | 0.36795 | 0.29999 | 0.41163 | 0.40144 | 0.27603 | 121.9366 | 121.8666 | 121.9245 | 121.8332 | 0.24967 | 0.33453 | 0.12676 | 0.18911 | 121.6869 | 121.8098 | 121.6749 | 121.7978
1043.0781 | 122.3877 | -0.32501 | 121.9528 | 0.062332 | -0.054257 | 0.033786 | -0.029595 | 0.072888 | 0.067269 | -0.058139 | 121.9046 | 121.8483 | 121.9062 | 121.8058 | 0.22221 | 0.31164 | 0.10845 | 0.16622 | 0.38734 | 0.27076 | 0.3588 | 0.29542 | 0.3979 | 0.39228 | 0.26687 | 121.9274 | 121.8712 | 121.9291 | 121.8287 | 0.24509 | 0.33453 | 0.13133 | 0.18911 | 121.6824 | 121.7961 | 121.684 | 121.7978
1044.8281 | 122.3373 | -0.32501 | 121.9528 | 0.06691 | -0.058836 | 0.042944 | -0.025017 | 0.072888 | 0.067269 | -0.053561 | 121.9137 | 121.8483 | 121.9108 | 121.8104 | 0.22678 | 0.32079 | 0.10387 | 0.1708 | 0.39192 | 0.26618 | 0.36796 | 0.3 | 0.3979 | 0.39228 | 0.27145 | 121.9366 | 121.8712 | 121.9337 | 121.8332 | 0.24967 | 0.34368 | 0.12676 | 0.19369 | 121.6869 | 121.8098 | 121.684 | 121.8069
1046.5156 | 122.319 | -0.33417 | 121.9391 | 0.071489 | -0.058836 | 0.038365 | -0.020438 | 0.072888 | 0.062691 | -0.058139 | 121.9137 | 121.8529 | 121.9108 | 121.8149 | 0.22678 | 0.30706 | 0.10387 | 0.1708 | 0.40566 | 0.27533 | 0.37253 | 0.31373 | 0.40706 | 0.39686 | 0.27603 | 121.9366 | 121.8757 | 121.9337 | 121.8378 | 0.24967 | 0.32995 | 0.12676 | 0.19369 | 121.6869 | 121.8098 | 121.684 | 121.8069
1048.2656 | 122.3831 | -0.32044 | 121.9711 | 0.062332 | -0.054257 | 0.033786 | -0.025017 | 0.082044 | 0.067269 | -0.053561 | 121.9091 | 121.862 | 121.92 | 121.8104 | 0.23136 | 0.31164 | 0.099289 | 0.1708 | 0.38277 | 0.26618 | 0.35422 | 0.29542 | 0.40248 | 0.3877 | 0.26687 | 121.932 | 121.8849 | 121.9429 | 121.8332 | 0.25425 | 0.33453 | 0.12218 | 0.19369 | 121.6778 | 121.8098 | 121.6886 | 121.8207
1050.0156 | 122.2321 | -0.37994 | 121.994 | 0.062332 | -0.058836 | 0.033786 | -0.020438 | 0.077466 | 0.076426 | -0.058139 | 121.9137 | 121.8574 | 121.9108 | 121.8058 | 0.22221 | 0.31622 | 0.10845 | 0.17538 | 0.44228 | 0.32111 | 0.41373 | 0.35951 | 0.45741 | 0.45637 | 0.32181 | 121.9366 | 121.8803 | 121.9337 | 121.8287 | 0.24509 | 0.3391 | 0.13133 | 0.19826 | 121.6915 | 121.8053 | 121.6886 | 121.8024
1051.7031 | 122.3145 | -0.37079 | 121.962 | 0.06691 | -0.0451 | 0.038365 | -0.020438 | 0.077466 | 0.067269 | -0.053561 | 121.9046 | 121.8574 | 121.9017 | 121.8104 | 0.23594 | 0.32995 | 0.10387 | 0.17996 | 0.4377 | 0.32569 | 0.40915 | 0.35035 | 0.44825 | 0.43806 | 0.31723 | 121.9274 | 121.8803 | 121.9245 | 121.8332 | 0.25883 | 0.35284 | 0.12676 | 0.20284 | 121.6686 | 121.8007 | 121.6657 | 121.7978
1053.4688 | 122.3831 | -0.32959 | 121.907 | 0.06691 | -0.049678 | 0.038365 | -0.025017 | 0.082044 | 0.067269 | -0.048983 | 121.9091 | 121.8529 | 121.9017 | 121.8058 | 0.23594 | 0.32079 | 0.10387 | 0.17538 | 0.3965 | 0.27991 | 0.36795 | 0.30457 | 0.41163 | 0.39686 | 0.28061 | 121.932 | 121.8757 | 121.9245 | 121.8287 | 0.25883 | 0.34368 | 0.12676 | 0.19826 | 121.6732 | 121.8053 | 121.6657 | 121.7978
1055.2344 | 122.2916 | -0.37079 | 121.9757 | 0.06691 | -0.0451 | 0.042944 | -0.01586 | 0.077466 | 0.071848 | -0.058139 | 121.9229 | 121.8574 | 121.9245 | 121.8149 | 0.23136 | 0.32079 | 0.10387 | 0.17996 | 0.4377 | 0.32569 | 0.41373 | 0.35493 | 0.44825 | 0.44264 | 0.31265 | 121.9458 | 121.8803 | 121.9474 | 121.8378 | 0.25425 | 0.34368 | 0.12676 | 0.20284 | 121.6915 | 121.819 | 121.6932 | 121.8207
1057 | 122.3007 | -0.36163 | 121.9849 | 0.06691 | -0.0451 | 0.038365 | -0.011281 | 0.0912 | 0.067269 | -0.053561 | 121.932 | 121.8574 | 121.9154 | 121.8149 | 0.23136 | 0.32537 | 0.10845 | 0.17996 | 0.42854 | 0.31653 | 0.4 | 0.35035 | 0.45283 | 0.4289 | 0.30807 | 121.9549 | 121.8803 | 121.9383 | 121.8378 | 0.25425 | 0.34826 | 0.13133 | 0.20284 | 121.7007 | 121.8236 | 121.684 | 121.8069
1058.6875 | 122.3969 | -0.20599 | 122.0856 | 0.057754 | -0.049678 | 0.033786 | -0.020438 | 0.072888 | 0.076426 | -0.048983 | 121.9458 | 121.8803 | 121.9383 | 121.8333 | 0.21305 | 0.2979 | 0.090132 | 0.16164 | 0.26375 | 0.15632 | 0.23978 | 0.18556 | 0.27888 | 0.28242 | 0.15701 | 121.9687 | 121.9032 | 121.9612 | 121.8561 | 0.23594 | 0.32079 | 0.11302 | 0.18453 | 121.7327 | 121.8556 | 121.7252 | 121.8482
1060.4531 | 122.2824 | -0.22888 | 122.1451 | 0.057754 | -0.049678 | 0.042944 | -0.025017 | 0.082044 | 0.067269 | -0.058139 | 122.0556 | 121.9948 | 122.0436 | 121.9523 | 0.1398 | 0.19261 | 0.021456 | 0.079235 | 0.28664 | 0.1792 | 0.27183 | 0.20386 | 0.31093 | 0.29615 | 0.17074 | 122.0785 | 122.0177 | 122.0665 | 121.9752 | 0.16269 | 0.2155 | 0.044344 | 0.10212 | 121.9159 | 122.0342 | 121.9038 | 122.0221
1062.2031 | 122.3831 | -0.21057 | 122.0856 | 0.06691 | -0.0451 | 0.029208 | -0.020438 | 0.082044 | 0.071848 | -0.058139 | 122.0602 | 121.9902 | 122.0436 | 121.9569 | 0.12607 | 0.19261 | 0.026035 | 0.074657 | 0.27748 | 0.16547 | 0.23978 | 0.19013 | 0.29262 | 0.28242 | 0.15243 | 122.0831 | 122.0131 | 122.0665 | 121.9798 | 0.14895 | 0.2155 | 0.048923 | 0.097545 | 121.9342 | 122.0342 | 121.9175 | 122.0175
1063.9375 | 122.2916 | -0.2243 | 122.113 | 0.062332 | -0.0451 | 0.038365 | -0.025017 | 0.086622 | 0.076426 | -0.058139 | 122.0648 | 121.9994 | 122.0527 | 121.9569 | 0.13064 | 0.19261 | 0.021456 | 0.083814 | 0.28664 | 0.1792 | 0.26267 | 0.19929 | 0.31093 | 0.30073 | 0.16617 | 122.0877 | 122.0223 | 122.0756 | 121.9798 | 0.15353 | 0.2155 | 0.044344 | 0.1067 | 121.9342 | 122.0434 | 121.9221 | 122.0313
1065.625 | 122.3007 | -0.25177 | 122.1268 | 0.057754 | -0.049678 | 0.042944 | -0.029595 | 0.082044 | 0.067269 | -0.058139 | 122.0648 | 122.004 | 122.0482 | 121.9569 | 0.13064 | 0.18803 | 0.026035 | 0.079235 | 0.30952 | 0.20209 | 0.29471 | 0.22217 | 0.33381 | 0.31904 | 0.19363 | 122.0877 | 122.0268 | 122.071 | 121.9798 | 0.15353 | 0.21092 | 0.048923 | 0.10212 | 121.9342 | 122.0388 | 121.9175 | 122.0221
1067.375 | 122.2778 | -0.25177 | 122.1451 | 0.062332 | -0.0451 | 0.038365 | -0.025017 | 0.082044 | 0.071848 | -0.053561 | 122.0648 | 121.9948 | 122.0527 | 121.9523 | 0.13064 | 0.19719 | 0.030613 | 0.079235 | 0.3141 | 0.20667 | 0.29013 | 0.22675 | 0.33381 | 0.32362 | 0.19821 | 122.0877 | 122.0177 | 122.0756 | 121.9752 | 0.15353 | 0.22007 | 0.053501 | 0.10212 | 121.9342 | 122.0342 | 121.9221 | 122.0221
1069.125 | 122.3602 | -0.21515 | 122.0947 | 0.071489 | -0.040521 | 0.033786 | -0.020438 | 0.077466 | 0.062691 | -0.048983 | 122.0602 | 122.004 | 122.0527 | 121.9569 | 0.13522 | 0.18803 | 0.021456 | 0.088392 | 0.28664 | 0.17463 | 0.24894 | 0.19471 | 0.29262 | 0.27784 | 0.16617 | 122.0831 | 122.0268 | 122.0756 | 121.9798 | 0.15811 | 0.21092 | 0.044344 | 0.11128 | 121.925 | 122.0388 | 121.9175 | 122.0313
1070.875 | 122.3282 | -0.2243 | 122.1085 | 0.062332 | -0.0451 | 0.033786 | -0.025017 | 0.086622 | 0.067269 | -0.044405 | 122.0648 | 122.004 | 122.0573 | 121.9569 | 0.14438 | 0.18803 | 0.026035 | 0.079235 | 0.28664 | 0.1792 | 0.25809 | 0.19929 | 0.31093 | 0.29157 | 0.1799 | 122.0877 | 122.0268 | 122.0802 | 121.9798 | 0.16726 | 0.21092 | 0.048923 | 0.10212 | 121.9204 | 122.0388 | 121.9129 | 122.0313
1072.6406 | 122.3969 | -0.20599 | 122.0947 | 0.057754 | -0.0451 | 0.033786 | -0.029595 | 0.086622 | 0.067269 | -0.053561 | 122.0648 | 122.004 | 122.0619 | 121.9569 | 0.13064 | 0.19261 | 0.021456 | 0.083814 | 0.26375 | 0.16089 | 0.23978 | 0.1764 | 0.29262 | 0.27326 | 0.15243 | 122.0877 | 122.0268 | 122.0848 | 121.9798 | 0.15353 | 0.2155 | 0.044344 | 0.1067 | 121.9342 | 122.0434 | 121.9313 | 122.0404
1074.3281 | 122.2824 | -0.23804 | 122.1497 | 0.071489 | -0.049678 | 0.047522 | -0.025017 | 0.0912 | 0.071848 | -0.048983 | 122.074 | 122.0177 | 122.0527 | 121.9569 | 0.13522 | 0.19261 | 0.016878 | 0.083814 | 0.30953 | 0.18836 | 0.28556 | 0.21302 | 0.32924 | 0.30988 | 0.18905 | 122.0969 | 122.0406 | 122.0756 | 121.9798 | 0.15811 | 0.2155 | 0.039766 | 0.1067 | 121.9387 | 122.0571 | 121.9175 | 122.0359
1076.0625 | 122.2733 | -0.25635 | 122.1542 | 0.062332 | -0.049678 | 0.042944 | -0.020438 | 0.086622 | 0.071848 | -0.053561 | 122.0694 | 122.0085 | 122.0665 | 121.966 | 0.12607 | 0.18345 | 0.012299 | 0.083814 | 0.31868 | 0.20667 | 0.29929 | 0.23591 | 0.34297 | 0.3282 | 0.20279 | 122.0923 | 122.0314 | 122.0894 | 121.9889 | 0.14895 | 0.20634 | 0.035187 | 0.1067 | 121.9433 | 122.0571 | 121.9404 | 122.0542
1077.8125 | 122.2916 | -0.23804 | 122.1588 | 0.053175 | -0.0451 | 0.033786 | -0.025017 | 0.0912 | 0.067269 | -0.058139 | 122.0785 | 122.0177 | 122.0711 | 121.9706 | 0.13064 | 0.18803 | 0.021456 | 0.088392 | 0.29121 | 0.19294 | 0.27182 | 0.21302 | 0.32924 | 0.30531 | 0.1799 | 122.1014 | 122.0406 | 122.0939 | 121.9935 | 0.15353 | 0.21092 | 0.044344 | 0.11128 | 121.9479 | 122.0571 | 121.9404 | 122.0496
1079.5625 | 122.3694 | -0.21973 | 122.0993 | 0.062332 | -0.0451 | 0.033786 | -0.020438 | 0.082044 | 0.067269 | -0.058139 | 122.0785 | 122.0131 | 122.0665 | 121.9706 | 0.12607 | 0.18803 | 0.021456 | 0.083814 | 0.28206 | 0.17463 | 0.25351 | 0.19929 | 0.30177 | 0.287 | 0.16159 | 122.1014 | 122.036 | 122.0894 | 121.9935 | 0.14895 | 0.21092 | 0.044344 | 0.1067 | 121.9525 | 122.0571 | 121.9404 | 122.045
1081.25 | 122.2687 | -0.25177 | 122.1451 | 0.06691 | -0.049678 | 0.033786 | -0.020438 | 0.082044 | 0.062691 | -0.053561 | 122.0877 | 122.0314 | 122.0711 | 121.9752 | 0.13522 | 0.17887 | 0.021456 | 0.074657 | 0.31868 | 0.20209 | 0.28556 | 0.23133 | 0.33381 | 0.31446 | 0.19821 | 122.1106 | 122.0543 | 122.0939 | 121.9981 | 0.15811 | 0.20176 | 0.044344 | 0.097545 | 121.9525 | 122.0662 | 121.9358 | 122.0496
1083.0156 | 122.3419 | -0.22888 | 122.1359 | 0.06691 | -0.054257 | 0.047522 | -0.01586 | 0.077466 | 0.071848 | -0.048983 | 122.0923 | 122.036 | 122.0756 | 121.9798 | 0.12149 | 0.17887 | 0.016878 | 0.074657 | 0.29579 | 0.17463 | 0.2764 | 0.21302 | 0.30635 | 0.30073 | 0.1799 | 122.1152 | 122.0589 | 122.0985 | 122.0027 | 0.14437 | 0.20176 | 0.039766 | 0.097545 | 121.9708 | 122.0754 | 121.9541 | 122.0588
1084.7656 | 122.4289 | -0.19226 | 122.1222 | 0.057754 | -0.0451 | 0.038365 | -0.025017 | 0.077466 | 0.076426 | -0.058139 | 122.0969 | 122.0314 | 122.0848 | 121.9752 | 0.11691 | 0.17887 | 0.016878 | 0.070079 | 0.25001 | 0.14716 | 0.23063 | 0.16724 | 0.26973 | 0.26869 | 0.13412 | 122.1197 | 122.0543 | 122.1077 | 121.9981 | 0.1398 | 0.20176 | 0.039766 | 0.092967 | 121.9799 | 122.08 | 121.9679 | 122.0679
1086.4688 | 122.4243 | -0.19684 | 122.1451 | 0.071489 | -0.054257 | 0.047522 | -0.029595 | 0.082044 | 0.071848 | -0.048983 | 122.1014 | 122.036 | 122.0848 | 121.9935 | 0.12149 | 0.16972 | 0.012299 | 0.070079 | 0.26833 | 0.14258 | 0.24436 | 0.16724 | 0.27888 | 0.26869 | 0.14786 | 122.1243 | 122.0589 | 122.1077 | 122.0164 | 0.14437 | 0.19261 | 0.035187 | 0.092967 | 121.9799 | 122.0891 | 121.9633 | 122.0725
1088.2188 | 122.4197 | -0.19226 | 122.1313 | 0.057754 | -0.054257 | 0.047522 | -0.029595 | 0.077466 | 0.067269 | -0.062717 | 122.1106 | 122.0406 | 122.0985 | 121.9889 | 0.11691 | 0.1743 | 0.007721 | 0.065501 | 0.25001 | 0.138 | 0.23978 | 0.16267 | 0.26973 | 0.25953 | 0.12954 | 122.1335 | 122.0635 | 122.1214 | 122.0118 | 0.1398 | 0.19718 | 0.030609 | 0.088389 | 121.9937 | 122.1029 | 121.9816 | 122.0908
1089.9688 | 122.3465 | -0.2243 | 122.1451 | 0.06691 | -0.049678 | 0.042944 | -0.029595 | 0.082044 | 0.071848 | -0.058139 | 122.106 | 122.0498 | 122.0985 | 121.9981 | 0.11691 | 0.1743 | 0.012299 | 0.070079 | 0.29121 | 0.17463 | 0.26725 | 0.19471 | 0.30635 | 0.29615 | 0.16617 | 122.1289 | 122.0726 | 122.1214 | 122.021 | 0.1398 | 0.19718 | 0.035187 | 0.092967 | 121.9891 | 122.0937 | 121.9816 | 122.0862
1091.6562 | 122.4472 | -0.17395 | 122.1222 | 0.06691 | -0.054257 | 0.033786 | -0.029595 | 0.082044 | 0.067269 | -0.053561 | 122.106 | 122.0589 | 122.1031 | 121.9935 | 0.10775 | 0.16514 | 0.012299 | 0.070079 | 0.24086 | 0.11969 | 0.20774 | 0.14435 | 0.25599 | 0.24122 | 0.12039 | 122.1289 | 122.0818 | 122.126 | 122.0164 | 0.13064 | 0.18803 | 0.035187 | 0.092967 | 121.9983 | 122.0937 | 121.9953 | 122.0908
1093.4062 | 122.3785 | -0.19684 | 122.1497 | 0.06691 | -0.058836 | 0.038365 | -0.029595 | 0.082044 | 0.062691 | -0.053561 | 122.1152 | 122.0543 | 122.1077 | 121.9935 | 0.10775 | 0.16514 | 0.003143 | 0.060923 | 0.26375 | 0.138 | 0.2352 | 0.16724 | 0.27888 | 0.25953 | 0.14328 | 122.1381 | 122.0772 | 122.1306 | 122.0164 | 0.13064 | 0.18803 | 0.026031 | 0.083811 | 122.0074 | 122.112 | 121.9999 | 122.1045
1095.1562 | 122.2824 | -0.23346 | 122.2137 | 0.06691 | -0.040521 | 0.033786 | -0.025017 | 0.086622 | 0.071848 | -0.058139 | 122.1152 | 122.0543 | 122.1214 | 122.0027 | 0.11691 | 0.16514 | 0.007721 | 0.065501 | 0.30037 | 0.19294 | 0.26725 | 0.20844 | 0.32008 | 0.30531 | 0.17532 | 122.1381 | 122.0772 | 122.1443 | 122.0256 | 0.1398 | 0.18803 | 0.030609 | 0.088389 | 121.9983 | 122.1074 | 122.0045 | 122.1137
1096.9219 | 122.3282 | -0.23804 | 122.2 | 0.062332 | -0.054257 | 0.038365 | -0.020438 | 0.077466 | 0.071848 | -0.058139 | 122.1289 | 122.0543 | 122.1168 | 122.0073 | 0.10775 | 0.16514 | 0.007721 | 0.065501 | 0.30037 | 0.18378 | 0.2764 | 0.2176 | 0.3155 | 0.30988 | 0.1799 | 122.1518 | 122.0772 | 122.1397 | 122.0301 | 0.13064 | 0.18803 | 0.030609 | 0.088389 | 122.0212 | 122.1212 | 122.0091 | 122.1091
1098.625 | 122.3007 | -0.21515 | 122.1588 | 0.06691 | -0.049678 | 0.038365 | -0.025017 | 0.082044 | 0.071848 | -0.044405 | 122.1243 | 122.0543 | 122.1214 | 122.0073 | 0.11233 | 0.16514 | 0.007721 | 0.065501 | 0.28206 | 0.16547 | 0.25351 | 0.19013 | 0.29719 | 0.287 | 0.17074 | 122.1472 | 122.0772 | 122.1443 | 122.0301 | 0.13522 | 0.18803 | 0.030609 | 0.088389 | 122.012 | 122.1166 | 122.0091 | 122.1137
1100.375 | 122.3923 | -0.16937 | 122.1542 | 0.062332 | -0.049678 | 0.038365 | -0.029595 | 0.077466 | 0.076426 | -0.053561 | 122.1289 | 122.0635 | 122.126 | 122.0164 | 0.11233 | 0.16972 | 0.012299 | 0.060923 | 0.2317 | 0.11969 | 0.20774 | 0.13978 | 0.24684 | 0.2458 | 0.11581 | 122.1518 | 122.0864 | 122.1489 | 122.0393 | 0.13522 | 0.19261 | 0.035187 | 0.083811 | 122.0166 | 122.1166 | 122.0137 | 122.1137
1102.1094 | 122.3877 | -0.21515 | 122.1634 | 0.062332 | -0.054257 | 0.033786 | -0.020438 | 0.082044 | 0.062691 | -0.058139 | 122.1289 | 122.0681 | 122.1214 | 122.0027 | 0.10775 | 0.16514 | 0.007721 | 0.070079 | 0.27748 | 0.16089 | 0.24894 | 0.19471 | 0.29719 | 0.27784 | 0.15701 | 122.1518 | 122.091 | 122.1443 | 122.0256 | 0.13064 | 0.18803 | 0.030609 | 0.092967 | 122.0212 | 122.1212 | 122.0137 | 122.1137
1103.875 | 122.4197 | -0.18768 | 122.1497 | 0.06691 | -0.0451 | 0.033786 | -0.025017 | 0.086622 | 0.071848 | -0.053561 | 122.1197 | 122.0589 | 122.1168 | 122.0027 | 0.11233 | 0.1743 | 0.016878 | 0.079235 | 0.25459 | 0.14258 | 0.22147 | 0.16267 | 0.27431 | 0.25953 | 0.13412 | 122.1426 | 122.0818 | 122.1397 | 122.0256 | 0.13522 | 0.19718 | 0.039766 | 0.10212 | 122.0074 | 122.1029 | 122.0045 | 122.1
1105.5781 | 122.3511 | -0.21515 | 122.1909 | 0.06691 | -0.049678 | 0.038365 | -0.01586 | 0.077466 | 0.067269 | -0.053561 | 122.1243 | 122.0681 | 122.1168 | 122.0073 | 0.11691 | 0.16972 | 0.007721 | 0.065501 | 0.28206 | 0.16547 | 0.25351 | 0.19929 | 0.29262 | 0.28242 | 0.16159 | 122.1472 | 122.091 | 122.1397 | 122.0301 | 0.1398 | 0.19261 | 0.030609 | 0.088389 | 122.0074 | 122.1166 | 121.9999 | 122.1091
1107.3281 | 122.4426 | -0.18768 | 122.1313 | 0.062332 | -0.040521 | 0.038365 | -0.029595 | 0.0912 | 0.071848 | -0.048983 | 122.1243 | 122.0543 | 122.1168 | 122.0073 | 0.11691 | 0.1743 | 0.012299 | 0.074657 | 0.25001 | 0.14716 | 0.22605 | 0.15809 | 0.27888 | 0.25953 | 0.1387 | 122.1472 | 122.0772 | 122.1397 | 122.0301 | 0.1398 | 0.19718 | 0.035187 | 0.097545 | 122.0074 | 122.112 | 121.9999 | 122.1045
1109.0625 | 122.3831 | -0.2243 | 122.1634 | 0.062332 | -0.049678 | 0.024629 | -0.020438 | 0.077466 | 0.062691 | -0.044405 | 122.106 | 122.0452 | 122.0985 | 121.9844 | 0.1398 | 0.18345 | 0.026035 | 0.079235 | 0.28664 | 0.17463 | 0.24893 | 0.20387 | 0.30177 | 0.287 | 0.1799 | 122.1289 | 122.0681 | 122.1214 | 122.0072 | 0.16269 | 0.20634 | 0.048923 | 0.10212 | 121.9662 | 122.08 | 121.9587 | 122.0725
1110.8125 | 122.4335 | -0.19226 | 122.1222 | 0.06691 | -0.049678 | 0.038365 | -0.025017 | 0.072888 | 0.062691 | -0.048983 | 122.1106 | 122.0498 | 122.1077 | 121.9889 | 0.12607 | 0.18803 | 0.021456 | 0.083814 | 0.25917 | 0.14258 | 0.23063 | 0.16724 | 0.26515 | 0.25495 | 0.14328 | 122.1335 | 122.0726 | 122.1306 | 122.0118 | 0.14895 | 0.21092 | 0.044344 | 0.1067 | 121.9845 | 122.0891 | 121.9816 | 122.0862
1112.5156 | 122.3145 | -0.23346 | 122.2046 | 0.062332 | -0.054257 | 0.038365 | -0.020438 | 0.086622 | 0.062691 | -0.053561 | 122.1243 | 122.0589 | 122.1214 | 121.9981 | 0.12607 | 0.17887 | 0.021456 | 0.074657 | 0.29579 | 0.1792 | 0.27182 | 0.21302 | 0.32008 | 0.29615 | 0.1799 | 122.1472 | 122.0818 | 122.1443 | 122.021 | 0.14895 | 0.20176 | 0.044344 | 0.097545 | 121.9983 | 122.1029 | 121.9953 | 122.1
1114.2656 | 122.3465 | -0.23346 | 122.2 | 0.071489 | -0.049678 | 0.038365 | -0.01586 | 0.086622 | 0.071848 | -0.053561 | 122.1289 | 122.0726 | 122.1214 | 122.0164 | 0.12607 | 0.16972 | 0.012299 | 0.070079 | 0.30495 | 0.18378 | 0.27182 | 0.2176 | 0.32008 | 0.30531 | 0.1799 | 122.1518 | 122.0955 | 122.1443 | 122.0393 | 0.14895 | 0.19261 | 0.035187 | 0.092967 | 122.0028 | 122.1166 | 121.9953 | 122.1091
1116.0156 | 122.287 | -0.23804 | 122.2 | 0.062332 | -0.0451 | 0.029208 | -0.01586 | 0.086622 | 0.071848 | -0.048983 | 122.1335 | 122.0635 | 122.1214 | 122.0073 | 0.11691 | 0.18345 | 0.016878 | 0.079235 | 0.30037 | 0.19294 | 0.26725 | 0.22218 | 0.32466 | 0.30988 | 0.18905 | 122.1564 | 122.0864 | 122.1443 | 122.0301 | 0.1398 | 0.20634 | 0.039766 | 0.10212 | 122.0166 | 122.1166 | 122.0045 | 122.1045
1117.7031 | 122.3465 | -0.21057 | 122.1771 | 0.076067 | -0.054257 | 0.038365 | -0.020438 | 0.082044 | 0.067269 | -0.053561 | 122.1381 | 122.0681 | 122.126 | 122.0073 | 0.12149 | 0.16972 | 0.021456 | 0.074657 | 0.28664 | 0.15631 | 0.24894 | 0.19013 | 0.29262 | 0.27784 | 0.15701 | 122.1609 | 122.091 | 122.1489 | 122.0301 | 0.14437 | 0.19261 | 0.044344 | 0.097545 | 122.0166 | 122.1166 | 122.0045 | 122.1045
1119.4531 | 122.3465 | -0.2243 | 122.168 | 0.076067 | -0.0451 | 0.038365 | -0.020438 | 0.082044 | 0.071848 | -0.044405 | 122.1381 | 122.0681 | 122.1306 | 122.021 | 0.11691 | 0.16514 | 0.007721 | 0.070079 | 0.30037 | 0.1792 | 0.26267 | 0.20387 | 0.30635 | 0.29615 | 0.1799 | 122.1609 | 122.091 | 122.1535 | 122.0439 | 0.1398 | 0.18803 | 0.030609 | 0.092967 | 122.0212 | 122.1303 | 122.0137 | 122.1228
1121.1875 | 122.3419 | -0.24261 | 122.1863 | 0.071489 | -0.0451 | 0.033786 | -0.025017 | 0.082044 | 0.071848 | -0.044405 | 122.1426 | 122.0772 | 122.1306 | 122.0164 | 0.11691 | 0.16972 | 0.016878 | 0.070079 | 0.3141 | 0.19751 | 0.2764 | 0.2176 | 0.32466 | 0.31446 | 0.19821 | 122.1655 | 122.1001 | 122.1535 | 122.0393 | 0.1398 | 0.19261 | 0.039766 | 0.092967 | 122.0257 | 122.1258 | 122.0137 | 122.1137
1122.9531 | 122.2916 | -0.21515 | 122.1909 | 0.057754 | -0.040521 | 0.038365 | -0.020438 | 0.086622 | 0.067269 | -0.048983 | 122.1335 | 122.0681 | 122.1214 | 122.0073 | 0.12607 | 0.17887 | 0.012299 | 0.079235 | 0.2729 | 0.17463 | 0.25351 | 0.19471 | 0.30177 | 0.28242 | 0.16617 | 122.1564 | 122.091 | 122.1443 | 122.0301 | 0.14895 | 0.20176 | 0.035187 | 0.10212 | 122.0074 | 122.1212 | 121.9953 | 122.1091
1124.6406 | 122.2961 | -0.23804 | 122.2092 | 0.071489 | -0.049678 | 0.038365 | -0.020438 | 0.072888 | 0.062691 | -0.048983 | 122.1289 | 122.0635 | 122.1214 | 122.0118 | 0.12149 | 0.18803 | 0.021456 | 0.070079 | 0.30953 | 0.18836 | 0.2764 | 0.2176 | 0.31093 | 0.30073 | 0.18905 | 122.1518 | 122.0864 | 122.1443 | 122.0347 | 0.14437 | 0.21092 | 0.044344 | 0.092967 | 122.0074 | 122.1074 | 121.9999 | 122.1
1126.3906 | 122.4014 | -0.20599 | 122.1863 | 0.062332 | -0.049678 | 0.029208 | -0.025017 | 0.082044 | 0.067269 | -0.058139 | 122.1335 | 122.0635 | 122.1214 | 122.0118 | 0.12149 | 0.17887 | 0.016878 | 0.079235 | 0.26833 | 0.15632 | 0.2352 | 0.18098 | 0.28804 | 0.27326 | 0.14786 | 122.1564 | 122.0864 | 122.1443 | 122.0347 | 0.14437 | 0.20176 | 0.039766 | 0.10212 | 122.012 | 122.1166 | 121.9999 | 122.1045
1128.1406 | 122.3648 | -0.23346 | 122.168 | 0.062332 | -0.049678 | 0.038365 | -0.025017 | 0.086622 | 0.071848 | -0.048983 | 122.1335 | 122.0726 | 122.126 | 122.0118 | 0.12607 | 0.18345 | 0.016878 | 0.074657 | 0.29579 | 0.18378 | 0.27182 | 0.20844 | 0.32008 | 0.30531 | 0.18448 | 122.1564 | 122.0955 | 122.1489 | 122.0347 | 0.14895 | 0.20634 | 0.039766 | 0.097545 | 122.0074 | 122.1166 | 121.9999 | 122.1091
1129.8906 | 122.4609 | -0.1831 | 122.1634 | 0.06691 | -0.049678 | 0.033786 | -0.025017 | 0.082044 | 0.067269 | -0.053561 | 122.1381 | 122.0635 | 122.1351 | 122.0118 | 0.12607 | 0.17887 | 0.016878 | 0.079235 | 0.25001 | 0.13343 | 0.21689 | 0.15809 | 0.26515 | 0.25037 | 0.12954 | 122.1609 | 122.0864 | 122.158 | 122.0347 | 0.14895 | 0.20176 | 0.039766 | 0.10212 | 122.012 | 122.1212 | 122.0091 | 122.1183
1131.5938 | 122.4014 | -0.21515 | 122.1725 | 0.06691 | -0.0451 | 0.038365 | -0.029595 | 0.086622 | 0.062691 | -0.048983 | 122.1426 | 122.0726 | 122.1214 | 122.0164 | 0.12149 | 0.18803 | 0.016878 | 0.079235 | 0.28206 | 0.17005 | 0.25351 | 0.18555 | 0.30177 | 0.27784 | 0.16617 | 122.1655 | 122.0955 | 122.1443 | 122.0393 | 0.14437 | 0.21092 | 0.039766 | 0.10212 | 122.0212 | 122.1258 | 121.9999 | 122.1045
1133.3438 | 122.3694 | -0.24719 | 122.168 | 0.062332 | -0.049678 | 0.038365 | -0.025017 | 0.086622 | 0.067269 | -0.048983 | 122.1335 | 122.0681 | 122.1306 | 122.0073 | 0.12149 | 0.19261 | 0.021456 | 0.079235 | 0.30952 | 0.19751 | 0.28556 | 0.22217 | 0.33381 | 0.31446 | 0.19821 | 122.1564 | 122.091 | 122.1535 | 122.0301 | 0.14437 | 0.2155 | 0.044344 | 0.10212 | 122.012 | 122.112 | 122.0091 | 122.1091
1135.0938 | 122.4609 | -0.20142 | 122.1497 | 0.06691 | -0.0451 | 0.042944 | -0.029595 | 0.082044 | 0.071848 | -0.048983 | 122.1335 | 122.0726 | 122.1306 | 122.0164 | 0.12149 | 0.17887 | 0.021456 | 0.079235 | 0.26833 | 0.15632 | 0.24436 | 0.17182 | 0.28346 | 0.27326 | 0.15243 | 122.1564 | 122.0955 | 122.1535 | 122.0393 | 0.14437 | 0.20176 | 0.044344 | 0.10212 | 122.012 | 122.112 | 122.0091 | 122.1091
1136.8438 | 122.3694 | -0.21515 | 122.1909 | 0.06691 | -0.049678 | 0.033786 | -0.01586 | 0.082044 | 0.071848 | -0.048983 | 122.1472 | 122.0818 | 122.1351 | 122.0256 | 0.11691 | 0.17887 | 0.016878 | 0.070079 | 0.28206 | 0.16547 | 0.24894 | 0.19929 | 0.29719 | 0.287 | 0.16617 | 122.1701 | 122.1047 | 122.158 | 122.0485 | 0.1398 | 0.20176 | 0.039766 | 0.092967 | 122.0303 | 122.1303 | 122.0182 | 122.1183
1138.5469 | 122.4152 | -0.21973 | 122.168 | 0.062332 | -0.040521 | 0.038365 | -0.025017 | 0.082044 | 0.067269 | -0.048983 | 122.1518 | 122.0818 | 122.1397 | 122.0302 | 0.11691 | 0.17887 | 0.012299 | 0.070079 | 0.28206 | 0.17921 | 0.25809 | 0.19471 | 0.30177 | 0.287 | 0.17074 | 122.1747 | 122.1047 | 122.1626 | 122.053 | 0.1398 | 0.20176 | 0.035187 | 0.092967 | 122.0349 | 122.1395 | 122.0228 | 122.1274
1140.2969 | 122.4426 | -0.18768 | 122.168 | 0.06691 | -0.040521 | 0.033786 | -0.020438 | 0.077466 | 0.071848 | -0.053561 | 122.1426 | 122.091 | 122.1489 | 122.0256 | 0.11233 | 0.1743 | 0.021456 | 0.065501 | 0.25459 | 0.14716 | 0.22147 | 0.16724 | 0.26515 | 0.25953 | 0.13412 | 122.1655 | 122.1138 | 122.1718 | 122.0485 | 0.13522 | 0.19718 | 0.044344 | 0.088389 | 122.0303 | 122.1212 | 122.0366 | 122.1274
1142.0312 | 122.4197 | -0.20142 | 122.1634 | 0.062332 | -0.0451 | 0.033786 | -0.029595 | 0.072888 | 0.067269 | -0.048983 | 122.1518 | 122.0818 | 122.1443 | 122.0164 | 0.11691 | 0.1743 | 0.007721 | 0.070079 | 0.26375 | 0.15632 | 0.2352 | 0.17182 | 0.2743 | 0.26869 | 0.15243 | 122.1747 | 122.1047 | 122.1672 | 122.0393 | 0.1398 | 0.19718 | 0.030609 | 0.092967 | 122.0349 | 122.1441 | 122.0274 | 122.1366
1143.7812 | 122.4106 | -0.18768 | 122.1909 | 0.06691 | -0.0451 | 0.042944 | -0.025017 | 0.086622 | 0.067269 | -0.048983 | 122.1518 | 122.0864 | 122.1351 | 122.0256 | 0.11691 | 0.1743 | 0.012299 | 0.074657 | 0.25459 | 0.14258 | 0.23063 | 0.16267 | 0.27431 | 0.25495 | 0.1387 | 122.1747 | 122.1093 | 122.158 | 122.0485 | 0.1398 | 0.19718 | 0.035187 | 0.097545 | 122.0349 | 122.1395 | 122.0182 | 122.1228
1145.4688 | 122.4289 | -0.22888 | 122.1588 | 0.062332 | -0.049678 | 0.038365 | -0.029595 | 0.082044 | 0.067269 | -0.053561 | 122.161 | 122.0864 | 122.1351 | 122.0302 | 0.11691 | 0.1743 | 0.012299 | 0.074657 | 0.29121 | 0.1792 | 0.26725 | 0.19929 | 0.31093 | 0.29615 | 0.17532 | 122.1838 | 122.1093 | 122.158 | 122.053 | 0.1398 | 0.19718 | 0.035187 | 0.097545 | 122.044 | 122.1487 | 122.0182 | 122.1228
1147.2031 | 122.4701 | -0.1831 | 122.1771 | 0.06691 | -0.049678 | 0.038365 | -0.01586 | 0.077466 | 0.067269 | -0.048983 | 122.1426 | 122.0818 | 122.1397 | 122.0164 | 0.12607 | 0.19261 | 0.026035 | 0.074657 | 0.25001 | 0.13343 | 0.22147 | 0.16724 | 0.26057 | 0.25037 | 0.13412 | 122.1655 | 122.1047 | 122.1626 | 122.0393 | 0.14895 | 0.2155 | 0.048923 | 0.097545 | 122.0166 | 122.1166 | 122.0137 | 122.1137
1148.9688 | 122.3282 | -0.23804 | 122.2321 | 0.062332 | -0.040521 | 0.047522 | -0.029595 | 0.082044 | 0.076426 | -0.053561 | 122.1518 | 122.0864 | 122.1489 | 122.0347 | 0.11691 | 0.16972 | 0.012299 | 0.074657 | 0.30037 | 0.19752 | 0.28556 | 0.20844 | 0.32008 | 0.31446 | 0.18448 | 122.1747 | 122.1093 | 122.1718 | 122.0576 | 0.1398 | 0.19261 | 0.035187 | 0.097545 | 122.0349 | 122.1395 | 122.032 | 122.1366
1150.6562 | 122.4609 | -0.16937 | 122.1863 | 0.057754 | -0.040521 | 0.042944 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.161 | 122.0955 | 122.158 | 122.0393 | 0.11233 | 0.1743 | 0.012299 | 0.070079 | 0.22713 | 0.12885 | 0.21232 | 0.14893 | 0.25599 | 0.24122 | 0.12039 | 122.1838 | 122.1184 | 122.1809 | 122.0622 | 0.13522 | 0.19718 | 0.035187 | 0.092967 | 122.0486 | 122.1487 | 122.0457 | 122.1457
1152.4062 | 122.3694 | -0.21057 | 122.2137 | 0.071489 | -0.0451 | 0.033786 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.161 | 122.0955 | 122.1489 | 122.0393 | 0.12149 | 0.1743 | 0.016878 | 0.070079 | 0.28206 | 0.16547 | 0.24436 | 0.19013 | 0.29719 | 0.28242 | 0.16159 | 122.1838 | 122.1184 | 122.1718 | 122.0622 | 0.14437 | 0.19718 | 0.039766 | 0.092967 | 122.0395 | 122.1441 | 122.0274 | 122.132
1154.1562 | 122.4518 | -0.18768 | 122.1863 | 0.06691 | -0.0451 | 0.038365 | -0.029595 | 0.082044 | 0.058113 | -0.048983 | 122.1701 | 122.1001 | 122.1535 | 122.0393 | 0.10775 | 0.16972 | 0.012299 | 0.074657 | 0.25459 | 0.14258 | 0.22605 | 0.15809 | 0.26973 | 0.2458 | 0.1387 | 122.193 | 122.123 | 122.1763 | 122.0622 | 0.13064 | 0.19261 | 0.035187 | 0.097545 | 122.0624 | 122.1578 | 122.0457 | 122.1412
1155.9219 | 122.3969 | -0.20599 | 122.2275 | 0.062332 | -0.0451 | 0.038365 | -0.020438 | 0.086622 | 0.067269 | -0.053561 | 122.1701 | 122.091 | 122.1626 | 122.0439 | 0.11691 | 0.16514 | 0.003143 | 0.065501 | 0.26833 | 0.16089 | 0.24436 | 0.18556 | 0.29262 | 0.27326 | 0.15243 | 122.193 | 122.1138 | 122.1855 | 122.0668 | 0.1398 | 0.18803 | 0.026031 | 0.088389 | 122.0532 | 122.167 | 122.0457 | 122.1595
1157.6094 | 122.3282 | -0.2243 | 122.2458 | 0.057754 | -0.040521 | 0.038365 | -0.020438 | 0.086622 | 0.071848 | -0.044405 | 122.1793 | 122.1093 | 122.1672 | 122.0576 | 0.10775 | 0.16514 | 0.007721 | 0.060923 | 0.28206 | 0.18378 | 0.26267 | 0.20387 | 0.31093 | 0.29615 | 0.1799 | 122.2022 | 122.1322 | 122.1901 | 122.0805 | 0.13064 | 0.18803 | 0.030609 | 0.083811 | 122.0715 | 122.1715 | 122.0594 | 122.1595
1159.3594 | 122.3831 | -0.21515 | 122.2366 | 0.06691 | -0.035942 | 0.047522 | -0.025017 | 0.086622 | 0.067269 | -0.048983 | 122.1747 | 122.1184 | 122.158 | 122.053 | 0.10317 | 0.16514 | 0.007721 | 0.065501 | 0.28206 | 0.17921 | 0.26267 | 0.19013 | 0.30177 | 0.28242 | 0.16617 | 122.1976 | 122.1413 | 122.1809 | 122.0759 | 0.12606 | 0.18803 | 0.030609 | 0.088389 | 122.0715 | 122.167 | 122.0549 | 122.1503
1161.0938 | 122.3282 | -0.22888 | 122.2458 | 0.06691 | -0.0451 | 0.038365 | -0.020438 | 0.082044 | 0.067269 | -0.048983 | 122.1838 | 122.1184 | 122.1764 | 122.0576 | 0.10317 | 0.16056 | 0.012299 | 0.060923 | 0.29579 | 0.18378 | 0.26725 | 0.20844 | 0.31093 | 0.29615 | 0.1799 | 122.2067 | 122.1413 | 122.1992 | 122.0805 | 0.12606 | 0.18345 | 0.035187 | 0.083811 | 122.0807 | 122.1715 | 122.0732 | 122.1641
1162.8438 | 122.3969 | -0.20142 | 122.2229 | 0.06691 | -0.049678 | 0.038365 | -0.025017 | 0.086622 | 0.067269 | -0.048983 | 122.1884 | 122.1276 | 122.1764 | 122.0622 | 0.098596 | 0.16056 | 0.007721 | 0.060923 | 0.26833 | 0.15174 | 0.23978 | 0.1764 | 0.28804 | 0.26869 | 0.15243 | 122.2113 | 122.1505 | 122.1992 | 122.0851 | 0.12148 | 0.18345 | 0.030609 | 0.083811 | 122.0898 | 122.1807 | 122.0778 | 122.1686
1164.5312 | 122.4701 | -0.18768 | 122.1863 | 0.06691 | -0.040521 | 0.033786 | -0.020438 | 0.082044 | 0.071848 | -0.048983 | 122.1701 | 122.1093 | 122.158 | 122.0485 | 0.11233 | 0.16514 | 0.003143 | 0.070079 | 0.25459 | 0.14716 | 0.22147 | 0.16724 | 0.26973 | 0.25953 | 0.1387 | 122.193 | 122.1322 | 122.1809 | 122.0714 | 0.13522 | 0.18803 | 0.026031 | 0.092967 | 122.0578 | 122.167 | 122.0457 | 122.1549
1166.2656 | 122.4106 | -0.19684 | 122.1954 | 0.062332 | -0.040521 | 0.038365 | -0.020438 | 0.086622 | 0.067269 | -0.058139 | 122.1838 | 122.1093 | 122.1626 | 122.053 | 0.10775 | 0.15598 | 0.003143 | 0.056344 | 0.25917 | 0.15632 | 0.2352 | 0.1764 | 0.28346 | 0.26411 | 0.1387 | 122.2067 | 122.1322 | 122.1855 | 122.0759 | 0.13064 | 0.17887 | 0.026031 | 0.079232 | 122.0761 | 122.1807 | 122.0549 | 122.1595
1168.0156 | 122.4197 | -0.19226 | 122.2092 | 0.062332 | -0.0451 | 0.033786 | -0.025017 | 0.082044 | 0.058113 | -0.048983 | 122.1884 | 122.1139 | 122.1718 | 122.053 | 0.10317 | 0.16056 | 0.007721 | 0.060923 | 0.25459 | 0.14716 | 0.22605 | 0.16724 | 0.27431 | 0.25037 | 0.14328 | 122.2113 | 122.1367 | 122.1947 | 122.0759 | 0.12606 | 0.18345 | 0.030609 | 0.083811 | 122.0853 | 122.1807 | 122.0686 | 122.1641
1169.7031 | 122.4655 | -0.15564 | 122.1817 | 0.057754 | -0.049678 | 0.042944 | -0.025017 | 0.072888 | 0.067269 | -0.048983 | 122.193 | 122.1276 | 122.1718 | 122.0622 | 0.10775 | 0.15598 | 0.012299 | 0.060923 | 0.21339 | 0.10596 | 0.19858 | 0.13062 | 0.22853 | 0.22291 | 0.10666 | 122.2159 | 122.1505 | 122.1947 | 122.0851 | 0.13064 | 0.17887 | 0.035187 | 0.083811 | 122.0853 | 122.1807 | 122.064 | 122.1595
1171.4531 | 122.3373 | -0.22888 | 122.2458 | 0.062332 | -0.049678 | 0.038365 | -0.020438 | 0.082044 | 0.071848 | -0.053561 | 122.1976 | 122.1276 | 122.1718 | 122.0714 | 0.10317 | 0.15598 | 0.003143 | 0.056344 | 0.29121 | 0.1792 | 0.26725 | 0.20844 | 0.31093 | 0.30073 | 0.17532 | 122.2205 | 122.1505 | 122.1947 | 122.0943 | 0.12606 | 0.17887 | 0.026031 | 0.079232 | 122.0944 | 122.1944 | 122.0686 | 122.1686
1173.2031 | 122.4197 | -0.17853 | 122.2183 | 0.06691 | -0.054257 | 0.038365 | -0.020438 | 0.082044 | 0.067269 | -0.048983 | 122.1884 | 122.123 | 122.1855 | 122.0668 | 0.098596 | 0.16056 | 0.003143 | 0.060923 | 0.24544 | 0.12427 | 0.21689 | 0.15809 | 0.26057 | 0.2458 | 0.12954 | 122.2113 | 122.1459 | 122.2084 | 122.0897 | 0.12148 | 0.18345 | 0.026031 | 0.083811 | 122.0898 | 122.1853 | 122.0869 | 122.1824
1174.8906 | 122.4792 | -0.16022 | 122.2092 | 0.057754 | -0.049678 | 0.038365 | -0.020438 | 0.086622 | 0.067269 | -0.039826 | 122.193 | 122.1276 | 122.1809 | 122.0714 | 0.10775 | 0.15141 | -0.001436 | 0.060923 | 0.21797 | 0.11054 | 0.19858 | 0.13978 | 0.24684 | 0.22749 | 0.12039 | 122.2159 | 122.1505 | 122.2038 | 122.0943 | 0.13064 | 0.17429 | 0.021452 | 0.083811 | 122.0853 | 122.1944 | 122.0732 | 122.1824
1176.6406 | 122.3373 | -0.2243 | 122.2549 | 0.071489 | -0.049678 | 0.042944 | -0.020438 | 0.086622 | 0.071848 | -0.058139 | 122.2022 | 122.1276 | 122.1947 | 122.0805 | 0.098596 | 0.15141 | -0.001436 | 0.056344 | 0.29579 | 0.17463 | 0.26725 | 0.20387 | 0.31093 | 0.29615 | 0.16617 | 122.225 | 122.1505 | 122.2176 | 122.1034 | 0.12148 | 0.17429 | 0.021452 | 0.079232 | 122.1036 | 122.2036 | 122.0961 | 122.1961
1178.3906 | 122.4747 | -0.16937 | 122.2366 | 0.06691 | -0.054257 | 0.042944 | -0.025017 | 0.082044 | 0.076426 | -0.048983 | 122.2022 | 122.1276 | 122.1855 | 122.0714 | 0.098596 | 0.15141 | -0.006014 | 0.060923 | 0.23628 | 0.11512 | 0.21232 | 0.14436 | 0.25142 | 0.2458 | 0.12039 | 122.225 | 122.1505 | 122.2084 | 122.0943 | 0.12148 | 0.17429 | 0.016874 | 0.083811 | 122.1036 | 122.2082 | 122.0869 | 122.1915
1180.0781 | 122.374 | -0.20599 | 122.2687 | 0.062332 | -0.0451 | 0.029208 | -0.01586 | 0.086622 | 0.076426 | -0.048983 | 122.2067 | 122.1367 | 122.1809 | 122.0805 | 0.10317 | 0.15598 | 0.003143 | 0.047188 | 0.26833 | 0.16089 | 0.2352 | 0.19013 | 0.29262 | 0.28242 | 0.15701 | 122.2296 | 122.1596 | 122.2038 | 122.1034 | 0.12606 | 0.17887 | 0.026031 | 0.070076 | 122.1036 | 122.2036 | 122.0778 | 122.1778
1181.8281 | 122.4655 | -0.14648 | 122.2366 | 0.071489 | -0.0451 | 0.038365 | -0.020438 | 0.072888 | 0.071848 | -0.053561 | 122.1976 | 122.1276 | 122.1901 | 122.0759 | 0.094017 | 0.15141 | -0.001436 | 0.056344 | 0.21797 | 0.10138 | 0.18485 | 0.12605 | 0.21937 | 0.21833 | 0.092923 | 122.2205 | 122.1505 | 122.213 | 122.0988 | 0.11691 | 0.17429 | 0.021452 | 0.079232 | 122.1036 | 122.199 | 122.0961 | 122.1915
1183.5312 | 122.3877 | -0.22888 | 122.2595 | 0.053175 | -0.040521 | 0.038365 | -0.020438 | 0.082044 | 0.071848 | -0.044405 | 122.2113 | 122.1367 | 122.1947 | 122.0943 | 0.10317 | 0.15598 | 0.003143 | 0.060923 | 0.28206 | 0.18836 | 0.26725 | 0.20844 | 0.31093 | 0.30073 | 0.18448 | 122.2342 | 122.1596 | 122.2176 | 122.1171 | 0.12606 | 0.17887 | 0.026031 | 0.083811 | 122.1081 | 122.2082 | 122.0915 | 122.1915
1185.2812 | 122.4564 | -0.16937 | 122.2137 | 0.071489 | -0.0451 | 0.042944 | -0.025017 | 0.086622 | 0.067269 | -0.053561 | 122.2022 | 122.1276 | 122.1855 | 122.0759 | 0.094017 | 0.15141 | 0.003143 | 0.060923 | 0.24086 | 0.12427 | 0.21232 | 0.14436 | 0.25599 | 0.23664 | 0.11581 | 122.225 | 122.1505 | 122.2084 | 122.0988 | 0.11691 | 0.17429 | 0.026031 | 0.083811 | 122.1081 | 122.199 | 122.0915 | 122.1824
1187.0312 | 122.3282 | -0.21515 | 122.2549 | 0.06691 | -0.0451 | 0.033786 | -0.025017 | 0.082044 | 0.067269 | -0.048983 | 122.2067 | 122.1322 | 122.1901 | 122.0759 | 0.089439 | 0.14683 | -0.001436 | 0.051766 | 0.28206 | 0.17005 | 0.24894 | 0.19013 | 0.29719 | 0.28242 | 0.16617 | 122.2296 | 122.1551 | 122.213 | 122.0988 | 0.11233 | 0.16972 | 0.021452 | 0.074654 | 122.1173 | 122.2082 | 122.1006 | 122.1915
1188.7188 | 122.4426 | -0.16479 | 122.2092 | 0.071489 | -0.049678 | 0.038365 | -0.025017 | 0.086622 | 0.076426 | -0.048983 | 122.2113 | 122.1413 | 122.1855 | 122.0805 | 0.098596 | 0.15598 | -0.001436 | 0.047188 | 0.23628 | 0.11512 | 0.20316 | 0.13978 | 0.25142 | 0.24122 | 0.11581 | 122.2342 | 122.1642 | 122.2084 | 122.1034 | 0.12148 | 0.17887 | 0.021452 | 0.070076 | 122.1127 | 122.2128 | 122.0869 | 122.1869
1190.4688 | 122.4014 | -0.19684 | 122.2504 | 0.06691 | -0.049678 | 0.038365 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.2113 | 122.1505 | 122.2038 | 122.0897 | 0.094017 | 0.15141 | 0.003143 | 0.051766 | 0.26375 | 0.14716 | 0.2352 | 0.1764 | 0.28346 | 0.26869 | 0.14786 | 122.2342 | 122.1734 | 122.2267 | 122.1126 | 0.11691 | 0.17429 | 0.026031 | 0.074654 | 122.1173 | 122.2082 | 122.1098 | 122.2007
1192.2031 | 122.3877 | -0.1831 | 122.2412 | 0.06691 | -0.040521 | 0.033786 | -0.025017 | 0.082044 | 0.067269 | -0.048983 | 122.2067 | 122.1367 | 122.1992 | 122.0851 | 0.094017 | 0.15598 | -0.001436 | 0.051766 | 0.25001 | 0.14258 | 0.21689 | 0.15809 | 0.26515 | 0.25037 | 0.13412 | 122.2296 | 122.1596 | 122.2221 | 122.108 | 0.11691 | 0.17887 | 0.021452 | 0.074654 | 122.1127 | 122.2082 | 122.1052 | 122.2007
1193.9688 | 122.4472 | -0.16937 | 122.2183 | 0.062332 | -0.0451 | 0.033786 | -0.01586 | 0.082044 | 0.067269 | -0.048983 | 122.2159 | 122.1459 | 122.1992 | 122.0759 | 0.098596 | 0.14683 | 0.003143 | 0.056344 | 0.2317 | 0.12427 | 0.20316 | 0.15351 | 0.25142 | 0.23664 | 0.12039 | 122.2388 | 122.1688 | 122.2221 | 122.0988 | 0.12148 | 0.16972 | 0.026031 | 0.079232 | 122.1173 | 122.2128 | 122.1006 | 122.1961
1195.7188 | 122.4014 | -0.19226 | 122.2504 | 0.06691 | -0.049678 | 0.042944 | -0.01586 | 0.086622 | 0.071848 | -0.048983 | 122.2159 | 122.1505 | 122.2038 | 122.0897 | 0.098596 | 0.14683 | 0.007721 | 0.051766 | 0.25917 | 0.14258 | 0.2352 | 0.1764 | 0.27888 | 0.26411 | 0.14328 | 122.2388 | 122.1734 | 122.2267 | 122.1126 | 0.12148 | 0.16972 | 0.030609 | 0.074654 | 122.1173 | 122.2082 | 122.1052 | 122.1961
1197.4062 | 122.4655 | -0.1831 | 122.2366 | 0.057754 | -0.0451 | 0.033786 | -0.01586 | 0.086622 | 0.062691 | -0.048983 | 122.2205 | 122.1413 | 122.2038 | 122.0897 | 0.089439 | 0.14683 | -0.001436 | 0.056344 | 0.24086 | 0.138 | 0.21689 | 0.16724 | 0.26973 | 0.2458 | 0.13412 | 122.2434 | 122.1642 | 122.2267 | 122.1126 | 0.11233 | 0.16972 | 0.021452 | 0.079232 | 122.131 | 122.2219 | 122.1144 | 122.2053
1199.1562 | 122.3557 | -0.20599 | 122.2824 | 0.06691 | -0.049678 | 0.038365 | -0.020438 | 0.082044 | 0.071848 | -0.048983 | 122.2251 | 122.1596 | 122.2038 | 122.0897 | 0.089439 | 0.14683 | -0.001436 | 0.051766 | 0.2729 | 0.15632 | 0.24436 | 0.18556 | 0.28804 | 0.27784 | 0.15701 | 122.2479 | 122.1825 | 122.2267 | 122.1126 | 0.11233 | 0.16972 | 0.021452 | 0.074654 | 122.1356 | 122.2265 | 122.1144 | 122.2053
1200.9062 | 122.406 | -0.19684 | 122.2641 | 0.06691 | -0.0451 | 0.047522 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.2251 | 122.1505 | 122.2038 | 122.0943 | 0.094017 | 0.14683 | -0.006014 | 0.051766 | 0.26375 | 0.15174 | 0.24436 | 0.1764 | 0.28346 | 0.26869 | 0.14786 | 122.2479 | 122.1734 | 122.2267 | 122.1171 | 0.11691 | 0.16972 | 0.016874 | 0.074654 | 122.131 | 122.2311 | 122.1098 | 122.2098
1202.5938 | 122.4243 | -0.18768 | 122.2366 | 0.062332 | -0.0451 | 0.033786 | -0.025017 | 0.077466 | 0.067269 | -0.053561 | 122.2159 | 122.1596 | 122.2038 | 122.0897 | 0.094017 | 0.14683 | -0.006014 | 0.056344 | 0.25001 | 0.14258 | 0.22147 | 0.16267 | 0.26515 | 0.25495 | 0.13412 | 122.2388 | 122.1825 | 122.2267 | 122.1126 | 0.11691 | 0.16972 | 0.016874 | 0.079232 | 122.1219 | 122.2219 | 122.1098 | 122.2098
1204.3438 | 122.3648 | -0.20142 | 122.2504 | 0.076067 | -0.049678 | 0.038365 | -0.025017 | 0.072888 | 0.071848 | -0.048983 | 122.2205 | 122.1642 | 122.213 | 122.0988 | 0.089439 | 0.13309 | -0.006014 | 0.060923 | 0.27748 | 0.15174 | 0.23978 | 0.1764 | 0.2743 | 0.27326 | 0.15243 | 122.2434 | 122.1871 | 122.2359 | 122.1217 | 0.11233 | 0.15598 | 0.016874 | 0.083811 | 122.131 | 122.2265 | 122.1235 | 122.219
1206.0938 | 122.4792 | -0.16479 | 122.2458 | 0.062332 | -0.0451 | 0.047522 | -0.020438 | 0.082044 | 0.071848 | -0.058139 | 122.2205 | 122.1551 | 122.2084 | 122.0988 | 0.089439 | 0.14683 | -0.006014 | 0.047188 | 0.22713 | 0.11969 | 0.21232 | 0.14436 | 0.24684 | 0.23664 | 0.10666 | 122.2434 | 122.1779 | 122.2313 | 122.1217 | 0.11233 | 0.16972 | 0.016874 | 0.070076 | 122.131 | 122.2265 | 122.119 | 122.2144
1207.8438 | 122.4335 | -0.17853 | 122.2366 | 0.06691 | -0.054257 | 0.033786 | -0.01586 | 0.082044 | 0.081005 | -0.048983 | 122.2296 | 122.1551 | 122.1992 | 122.0943 | 0.10317 | 0.15598 | -0.001436 | 0.056344 | 0.24544 | 0.12427 | 0.21231 | 0.16267 | 0.26057 | 0.25953 | 0.12954 | 122.2525 | 122.1779 | 122.2221 | 122.1171 | 0.12606 | 0.17887 | 0.021452 | 0.079232 | 122.1265 | 122.2311 | 122.0961 | 122.2007
1209.6094 | 122.3511 | -0.2243 | 122.2733 | 0.06691 | -0.040521 | 0.038365 | -0.01586 | 0.086622 | 0.081005 | -0.048983 | 122.2205 | 122.1551 | 122.2038 | 122.0988 | 0.094017 | 0.15141 | -0.006014 | 0.051766 | 0.29121 | 0.18378 | 0.26267 | 0.20844 | 0.31093 | 0.30531 | 0.17532 | 122.2434 | 122.1779 | 122.2267 | 122.1217 | 0.11691 | 0.17429 | 0.016874 | 0.074654 | 122.1265 | 122.2265 | 122.1098 | 122.2098
1211.2969 | 122.3602 | -0.21057 | 122.2778 | 0.06691 | -0.0451 | 0.042944 | -0.025017 | 0.082044 | 0.067269 | -0.048983 | 122.2251 | 122.1551 | 122.2084 | 122.0988 | 0.094017 | 0.14225 | 0.003143 | 0.056344 | 0.27748 | 0.16547 | 0.25351 | 0.18555 | 0.29262 | 0.27784 | 0.16159 | 122.2479 | 122.1779 | 122.2313 | 122.1217 | 0.11691 | 0.16514 | 0.026031 | 0.079232 | 122.131 | 122.2219 | 122.1144 | 122.2053
1213 | 122.438 | -0.1831 | 122.2366 | 0.057754 | -0.040521 | 0.038365 | -0.020438 | 0.082044 | 0.076426 | -0.048983 | 122.2159 | 122.1642 | 122.2038 | 122.0988 | 0.094017 | 0.13767 | -0.001436 | 0.047188 | 0.24086 | 0.14258 | 0.22147 | 0.16267 | 0.26515 | 0.25953 | 0.13412 | 122.2388 | 122.1871 | 122.2267 | 122.1217 | 0.11691 | 0.16056 | 0.021452 | 0.070076 | 122.1219 | 122.2173 | 122.1098 | 122.2053
1214.7656 | 122.3831 | -0.19226 | 122.2504 | 0.06691 | -0.0451 | 0.042944 | -0.020438 | 0.086622 | 0.076426 | -0.044405 | 122.2159 | 122.1596 | 122.2038 | 122.0897 | 0.098596 | 0.15141 | -0.001436 | 0.051766 | 0.25917 | 0.14716 | 0.2352 | 0.17182 | 0.27888 | 0.26869 | 0.14786 | 122.2388 | 122.1825 | 122.2267 | 122.1126 | 0.12148 | 0.17429 | 0.021452 | 0.074654 | 122.1173 | 122.2173 | 122.1052 | 122.2053
1216.5156 | 122.3785 | -0.21515 | 122.287 | 0.06691 | -0.049678 | 0.038365 | -0.01586 | 0.086622 | 0.076426 | -0.039826 | 122.2205 | 122.1505 | 122.2084 | 122.0897 | 0.094017 | 0.14225 | -0.006014 | 0.056344 | 0.28206 | 0.16547 | 0.25351 | 0.19929 | 0.30177 | 0.29158 | 0.17532 | 122.2434 | 122.1734 | 122.2313 | 122.1126 | 0.11691 | 0.16514 | 0.016874 | 0.079232 | 122.1265 | 122.2265 | 122.1144 | 122.2144
1218.2031 | 122.4792 | -0.16022 | 122.2595 | 0.062332 | -0.049678 | 0.052101 | -0.020438 | 0.077466 | 0.067269 | -0.048983 | 122.2251 | 122.1688 | 122.213 | 122.0943 | 0.094017 | 0.14225 | -0.006014 | 0.056344 | 0.22255 | 0.11054 | 0.21232 | 0.13978 | 0.23768 | 0.22749 | 0.11123 | 122.2479 | 122.1917 | 122.2359 | 122.1171 | 0.11691 | 0.16514 | 0.016874 | 0.079232 | 122.131 | 122.2311 | 122.119 | 122.219
1219.9688 | 122.4152 | -0.19226 | 122.2916 | 0.071489 | -0.040521 | 0.029208 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.2296 | 122.1734 | 122.2176 | 122.1126 | 0.089439 | 0.13767 | 0.007721 | 0.047188 | 0.26375 | 0.15174 | 0.22147 | 0.17182 | 0.27888 | 0.26411 | 0.14328 | 122.2525 | 122.1963 | 122.2404 | 122.1355 | 0.11233 | 0.16056 | 0.030609 | 0.070076 | 122.1402 | 122.2219 | 122.1281 | 122.2098
1221.7031 | 122.3831 | -0.21057 | 122.2595 | 0.06691 | -0.054257 | 0.038365 | -0.020438 | 0.0912 | 0.067269 | -0.048983 | 122.2342 | 122.1642 | 122.2176 | 122.1034 | 0.094017 | 0.14225 | -0.006014 | 0.056344 | 0.27748 | 0.15631 | 0.24894 | 0.19013 | 0.30177 | 0.27784 | 0.16159 | 122.2571 | 122.1871 | 122.2404 | 122.1263 | 0.11691 | 0.16514 | 0.016874 | 0.079232 | 122.1402 | 122.2402 | 122.1235 | 122.2236
1223.3906 | 122.3877 | -0.19226 | 122.2961 | 0.062332 | -0.049678 | 0.042944 | -0.011281 | 0.086622 | 0.076426 | -0.053561 | 122.2342 | 122.1688 | 122.2221 | 122.108 | 0.094017 | 0.13767 | -0.006014 | 0.047188 | 0.25459 | 0.14258 | 0.2352 | 0.18098 | 0.27888 | 0.26869 | 0.1387 | 122.2571 | 122.1917 | 122.245 | 122.1309 | 0.11691 | 0.16056 | 0.016874 | 0.070076 | 122.1402 | 122.2402 | 122.1281 | 122.2281
1225.0938 | 122.3602 | -0.21973 | 122.2687 | 0.062332 | -0.058836 | 0.042944 | -0.025017 | 0.086622 | 0.067269 | -0.048983 | 122.2388 | 122.1734 | 122.2176 | 122.1126 | 0.084861 | 0.13767 | -0.015171 | 0.047188 | 0.28206 | 0.16089 | 0.26267 | 0.19471 | 0.30635 | 0.287 | 0.17074 | 122.2617 | 122.1963 | 122.2404 | 122.1355 | 0.10775 | 0.16056 | 0.007717 | 0.070076 | 122.1539 | 122.254 | 122.1327 | 122.2327
1226.8594 | 122.438 | -0.1831 | 122.2595 | 0.062332 | -0.054257 | 0.042944 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.2388 | 122.1688 | 122.2176 | 122.1126 | 0.094017 | 0.14683 | -0.006014 | 0.051766 | 0.24544 | 0.12885 | 0.22605 | 0.16267 | 0.26973 | 0.25495 | 0.13412 | 122.2617 | 122.1917 | 122.2404 | 122.1355 | 0.11691 | 0.16972 | 0.016874 | 0.074654 | 122.1448 | 122.2448 | 122.1235 | 122.2236
1228.6094 | 122.4838 | -0.16937 | 122.2458 | 0.057754 | -0.049678 | 0.042944 | -0.025017 | 0.0912 | 0.071848 | -0.048983 | 122.2342 | 122.1688 | 122.2176 | 122.1126 | 0.084861 | 0.13767 | -0.010593 | 0.047188 | 0.22713 | 0.11969 | 0.21232 | 0.14436 | 0.26057 | 0.24122 | 0.12039 | 122.2571 | 122.1917 | 122.2404 | 122.1355 | 0.10775 | 0.16056 | 0.012295 | 0.070076 | 122.1493 | 122.2448 | 122.1327 | 122.2282
1230.2969 | 122.4838 | -0.15564 | 122.2687 | 0.071489 | -0.0451 | 0.038365 | -0.025017 | 0.082044 | 0.071848 | -0.053561 | 122.2388 | 122.1734 | 122.2267 | 122.1126 | 0.084861 | 0.14225 | -0.001436 | 0.051766 | 0.22713 | 0.11054 | 0.19401 | 0.13062 | 0.23768 | 0.22749 | 0.10208 | 122.2617 | 122.1963 | 122.2496 | 122.1355 | 0.10775 | 0.16514 | 0.021452 | 0.074654 | 122.1539 | 122.2402 | 122.1419 | 122.2281
1232.0469 | 122.4335 | -0.19684 | 122.287 | 0.062332 | -0.040521 | 0.042944 | -0.020438 | 0.0912 | 0.071848 | -0.048983 | 122.2434 | 122.1825 | 122.2313 | 122.1126 | 0.084861 | 0.13309 | -0.006014 | 0.047188 | 0.25917 | 0.15632 | 0.23978 | 0.1764 | 0.28804 | 0.26869 | 0.14786 | 122.2663 | 122.2054 | 122.2542 | 122.1355 | 0.10775 | 0.15598 | 0.016874 | 0.070076 | 122.1585 | 122.2494 | 122.1464 | 122.2373
1233.7969 | 122.438 | -0.16479 | 122.2595 | 0.071489 | -0.049678 | 0.042944 | -0.025017 | 0.0912 | 0.071848 | -0.048983 | 122.2388 | 122.178 | 122.2359 | 122.1126 | 0.080283 | 0.13767 | -0.006014 | 0.051766 | 0.23628 | 0.11512 | 0.20774 | 0.13978 | 0.25599 | 0.23664 | 0.11581 | 122.2617 | 122.2008 | 122.2588 | 122.1355 | 0.10317 | 0.16056 | 0.016874 | 0.074654 | 122.1585 | 122.2448 | 122.1556 | 122.2419
1235.5 | 122.4106 | -0.1831 | 122.2961 | 0.071489 | -0.049678 | 0.042944 | -0.020438 | 0.086622 | 0.071848 | -0.044405 | 122.2479 | 122.178 | 122.2313 | 122.1172 | 0.084861 | 0.14225 | -0.006014 | 0.047188 | 0.25459 | 0.13343 | 0.22605 | 0.16267 | 0.26973 | 0.25495 | 0.1387 | 122.2708 | 122.2008 | 122.2542 | 122.14 | 0.10775 | 0.16514 | 0.016874 | 0.070076 | 122.1631 | 122.254 | 122.1464 | 122.2373
1237.2344 | 122.3877 | -0.18768 | 122.3053 | 0.071489 | -0.054257 | 0.038365 | -0.025017 | 0.086622 | 0.071848 | -0.048983 | 122.2434 | 122.1688 | 122.2313 | 122.1126 | 0.084861 | 0.13767 | -0.001436 | 0.056344 | 0.25917 | 0.13343 | 0.22605 | 0.16267 | 0.27431 | 0.25953 | 0.1387 | 122.2663 | 122.1917 | 122.2542 | 122.1355 | 0.10775 | 0.16056 | 0.021452 | 0.079232 | 122.1585 | 122.2448 | 122.1464 | 122.2327
1238.9844 | 122.3969 | -0.20142 | 122.2961 | 0.062332 | -0.054257 | 0.042944 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.2479 | 122.1825 | 122.2313 | 122.1172 | 0.084861 | 0.13309 | -0.006014 | 0.047188 | 0.26375 | 0.14716 | 0.24436 | 0.18098 | 0.28804 | 0.27326 | 0.15243 | 122.2708 | 122.2054 | 122.2542 | 122.14 | 0.10775 | 0.15598 | 0.016874 | 0.070076 | 122.1631 | 122.254 | 122.1464 | 122.2373
1240.6719 | 122.4289 | -0.19226 | 122.2733 | 0.062332 | -0.0451 | 0.038365 | -0.038752 | 0.086622 | 0.062691 | -0.048983 | 122.2479 | 122.1825 | 122.2313 | 122.1172 | 0.094017 | 0.14683 | -0.006014 | 0.047188 | 0.25459 | 0.14716 | 0.23063 | 0.15351 | 0.27888 | 0.25495 | 0.14328 | 122.2708 | 122.2054 | 122.2542 | 122.14 | 0.11691 | 0.16972 | 0.016874 | 0.070076 | 122.1539 | 122.254 | 122.1373 | 122.2373
1242.4219 | 122.4518 | -0.16022 | 122.2504 | 0.062332 | -0.049678 | 0.038365 | -0.020438 | 0.082044 | 0.071848 | -0.048983 | 122.2479 | 122.1871 | 122.2313 | 122.1172 | 0.075705 | 0.13309 | -0.006014 | 0.047188 | 0.22255 | 0.11054 | 0.19858 | 0.13978 | 0.24226 | 0.23206 | 0.11123 | 122.2708 | 122.21 | 122.2542 | 122.14 | 0.098593 | 0.15598 | 0.016874 | 0.070076 | 122.1722 | 122.254 | 122.1556 | 122.2373
1244.1094 | 122.3785 | -0.2243 | 122.287 | 0.062332 | -0.054257 | 0.047522 | -0.01586 | 0.086622 | 0.067269 | -0.048983 | 122.2525 | 122.178 | 122.2313 | 122.1217 | 0.089439 | 0.13767 | -0.006014 | 0.047188 | 0.28664 | 0.17005 | 0.27183 | 0.20844 | 0.31093 | 0.29157 | 0.17532 | 122.2754 | 122.2008 | 122.2542 | 122.1446 | 0.11233 | 0.16056 | 0.016874 | 0.070076 | 122.1631 | 122.2585 | 122.1419 | 122.2373
1245.8594 | 122.4518 | -0.16022 | 122.2504 | 0.06691 | -0.049678 | 0.038365 | -0.020438 | 0.095778 | 0.067269 | -0.048983 | 122.2525 | 122.1825 | 122.2313 | 122.1172 | 0.084861 | 0.14225 | -0.006014 | 0.051766 | 0.22713 | 0.11054 | 0.19858 | 0.13978 | 0.25599 | 0.22749 | 0.11123 | 122.2754 | 122.2054 | 122.2542 | 122.14 | 0.10775 | 0.16514 | 0.016874 | 0.074654 | 122.1677 | 122.2585 | 122.1464 | 122.2373
1247.6094 | 122.5159 | -0.15564 | 122.2824 | 0.062332 | -0.054257 | 0.038365 | -0.020438 | 0.086622 | 0.071848 | -0.053561 | 122.2571 | 122.1963 | 122.2404 | 122.1309 | 0.080283 | 0.13309 | -0.019749 | 0.047188 | 0.21797 | 0.10138 | 0.19401 | 0.1352 | 0.24226 | 0.22749 | 0.10208 | 122.28 | 122.2192 | 122.2633 | 122.1538 | 0.10317 | 0.15598 | 0.003139 | 0.070076 | 122.1768 | 122.2769 | 122.1602 | 122.2602
1249.3594 | 122.4609 | -0.16022 | 122.2916 | 0.062332 | -0.0451 | 0.038365 | -0.01586 | 0.082044 | 0.062691 | -0.058139 | 122.2571 | 122.1917 | 122.2496 | 122.1309 | 0.075705 | 0.12851 | -0.006014 | 0.038032 | 0.22255 | 0.11512 | 0.19858 | 0.14436 | 0.24226 | 0.22291 | 0.10208 | 122.28 | 122.2146 | 122.2725 | 122.1538 | 0.098593 | 0.1514 | 0.016874 | 0.06092 | 122.1814 | 122.2631 | 122.1739 | 122.2556
1251.1094 | 122.4106 | -0.17853 | 122.2641 | 0.06691 | -0.049678 | 0.047522 | -0.025017 | 0.086622 | 0.067269 | -0.053561 | 122.2617 | 122.2054 | 122.2542 | 122.1355 | 0.080283 | 0.13309 | -0.015171 | 0.04261 | 0.24544 | 0.12885 | 0.22605 | 0.15351 | 0.26515 | 0.2458 | 0.12497 | 122.2846 | 122.2283 | 122.2771 | 122.1584 | 0.10317 | 0.15598 | 0.007717 | 0.065498 | 122.1814 | 122.2769 | 122.1739 | 122.2694
1252.8906 | 122.3602 | -0.18768 | 122.3007 | 0.06691 | -0.049678 | 0.038365 | -0.01586 | 0.0912 | 0.067269 | -0.048983 | 122.2663 | 122.1963 | 122.2542 | 122.1309 | 0.071126 | 0.12851 | -0.015171 | 0.038032 | 0.25459 | 0.138 | 0.22605 | 0.17182 | 0.27888 | 0.25495 | 0.1387 | 122.2891 | 122.2192 | 122.2771 | 122.1538 | 0.094014 | 0.1514 | 0.007717 | 0.06092 | 122.1951 | 122.2814 | 122.1831 | 122.2694
1254.6562 | 122.493 | -0.15106 | 122.2961 | 0.062332 | -0.054257 | 0.033786 | -0.025017 | 0.086622 | 0.076426 | -0.048983 | 122.2617 | 122.2009 | 122.2496 | 122.1355 | 0.075705 | 0.12394 | -0.010593 | 0.04261 | 0.21339 | 0.096805 | 0.18485 | 0.12604 | 0.23768 | 0.22749 | 0.10208 | 122.2846 | 122.2237 | 122.2725 | 122.1584 | 0.098593 | 0.14683 | 0.012295 | 0.065498 | 122.186 | 122.2723 | 122.1739 | 122.2602
1256.4062 | 122.4426 | -0.16022 | 122.287 | 0.062332 | -0.049678 | 0.038365 | -0.020438 | 0.086622 | 0.067269 | -0.048983 | 122.2617 | 122.1963 | 122.2496 | 122.1355 | 0.075705 | 0.12851 | -0.010593 | 0.038032 | 0.22255 | 0.11054 | 0.19858 | 0.13978 | 0.24684 | 0.22749 | 0.11123 | 122.2846 | 122.2192 | 122.2725 | 122.1584 | 0.098593 | 0.1514 | 0.012295 | 0.06092 | 122.186 | 122.2723 | 122.1739 | 122.2602
1258.1094 | 122.374 | -0.1831 | 122.3099 | 0.071489 | -0.058836 | 0.038365 | -0.025017 | 0.095778 | 0.067269 | -0.053561 | 122.2708 | 122.1963 | 122.2542 | 122.1309 | 0.075705 | 0.13309 | -0.010593 | 0.04261 | 0.25459 | 0.12427 | 0.22147 | 0.15809 | 0.27888 | 0.25037 | 0.12954 | 122.2937 | 122.2192 | 122.2771 | 122.1538 | 0.098593 | 0.15598 | 0.012295 | 0.065498 | 122.1951 | 122.2814 | 122.1785 | 122.2648
1259.8594 | 122.3877 | -0.20142 | 122.3007 | 0.057754 | -0.058836 | 0.042944 | -0.025017 | 0.077466 | 0.071848 | -0.044405 | 122.2617 | 122.2009 | 122.2542 | 122.1309 | 0.080283 | 0.12851 | -0.015171 | 0.033454 | 0.25917 | 0.14258 | 0.24436 | 0.1764 | 0.27888 | 0.27326 | 0.15701 | 122.2846 | 122.2237 | 122.2771 | 122.1538 | 0.10317 | 0.1514 | 0.007717 | 0.056342 | 122.1814 | 122.2769 | 122.1739 | 122.2694
1261.5469 | 122.4014 | -0.18768 | 122.3099 | 0.057754 | -0.049678 | 0.038365 | -0.020438 | 0.086622 | 0.062691 | -0.048983 | 122.2708 | 122.2054 | 122.2496 | 122.1355 | 0.080283 | 0.13309 | -0.010593 | 0.038032 | 0.24544 | 0.138 | 0.22605 | 0.16724 | 0.27431 | 0.25037 | 0.1387 | 122.2937 | 122.2283 | 122.2725 | 122.1584 | 0.10317 | 0.15598 | 0.012295 | 0.06092 | 122.1906 | 122.2814 | 122.1693 | 122.2602
1263.2344 | 122.374 | -0.1831 | 122.3282 | 0.071489 | -0.0451 | 0.042944 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.2708 | 122.2009 | 122.2542 | 122.1309 | 0.084861 | 0.12851 | -0.015171 | 0.038032 | 0.25459 | 0.138 | 0.22605 | 0.16267 | 0.26973 | 0.25495 | 0.13412 | 122.2937 | 122.2237 | 122.2771 | 122.1538 | 0.10775 | 0.1514 | 0.007717 | 0.06092 | 122.186 | 122.286 | 122.1693 | 122.2694
1264.9844 | 122.3785 | -0.19684 | 122.287 | 0.062332 | -0.049678 | 0.042944 | -0.01586 | 0.086622 | 0.067269 | -0.048983 | 122.2708 | 122.2009 | 122.2542 | 122.1309 | 0.080283 | 0.12851 | -0.006014 | 0.04261 | 0.25917 | 0.14716 | 0.23978 | 0.18098 | 0.28346 | 0.26411 | 0.14786 | 122.2937 | 122.2237 | 122.2771 | 122.1538 | 0.10317 | 0.1514 | 0.016874 | 0.065498 | 122.1906 | 122.2769 | 122.1739 | 122.2602
1266.6562 | 122.4747 | -0.13733 | 122.2961 | 0.06691 | -0.058836 | 0.047522 | -0.025017 | 0.086622 | 0.067269 | -0.048983 | 122.2663 | 122.2054 | 122.2633 | 122.14 | 0.075705 | 0.12851 | -0.006014 | 0.04261 | 0.20424 | 0.078493 | 0.18485 | 0.11231 | 0.22395 | 0.2046 | 0.088346 | 122.2891 | 122.2283 | 122.2862 | 122.1629 | 0.098593 | 0.1514 | 0.016874 | 0.065498 | 122.1906 | 122.2723 | 122.1876 | 122.2694
1268.4062 | 122.5204 | -0.14648 | 122.2549 | 0.062332 | -0.054257 | 0.033786 | -0.020438 | 0.086622 | 0.071848 | -0.039826 | 122.2708 | 122.2054 | 122.2496 | 122.14 | 0.080283 | 0.12851 | -0.010593 | 0.047188 | 0.20882 | 0.092227 | 0.18027 | 0.12605 | 0.23311 | 0.21833 | 0.10666 | 122.2937 | 122.2283 | 122.2725 | 122.1629 | 0.10317 | 0.1514 | 0.012295 | 0.070076 | 122.1906 | 122.2814 | 122.1693 | 122.2602
1270.1094 | 122.3785 | -0.19226 | 122.2916 | 0.062332 | -0.049678 | 0.042944 | -0.020438 | 0.0912 | 0.076426 | -0.048983 | 122.2708 | 122.2054 | 122.2588 | 122.14 | 0.071126 | 0.13767 | -0.019749 | 0.047188 | 0.25459 | 0.14258 | 0.2352 | 0.17182 | 0.28346 | 0.26869 | 0.14328 | 122.2937 | 122.2283 | 122.2816 | 122.1629 | 0.094014 | 0.16056 | 0.003139 | 0.070076 | 122.1997 | 122.2906 | 122.1876 | 122.2785
1271.8438 | 122.4609 | -0.17395 | 122.2916 | 0.071489 | -0.054257 | 0.029208 | -0.029595 | 0.082044 | 0.071848 | -0.044405 | 122.2754 | 122.2054 | 122.2588 | 122.1355 | 0.075705 | 0.12851 | -0.015171 | 0.04261 | 0.24544 | 0.11969 | 0.20316 | 0.14435 | 0.25599 | 0.2458 | 0.12954 | 122.2983 | 122.2283 | 122.2816 | 122.1584 | 0.098593 | 0.1514 | 0.007717 | 0.065498 | 122.1997 | 122.2906 | 122.1831 | 122.2739
1273.5312 | 122.5021 | -0.14648 | 122.2733 | 0.06691 | -0.0451 | 0.033786 | -0.025017 | 0.082044 | 0.062691 | -0.044405 | 122.2663 | 122.2054 | 122.2588 | 122.1492 | 0.075705 | 0.12394 | -0.010593 | 0.047188 | 0.21339 | 0.10138 | 0.18027 | 0.12147 | 0.22853 | 0.20917 | 0.10208 | 122.2891 | 122.2283 | 122.2816 | 122.1721 | 0.098593 | 0.14683 | 0.012295 | 0.070076 | 122.1906 | 122.2769 | 122.1831 | 122.2694
1275.2188 | 122.5113 | -0.15106 | 122.2733 | 0.06691 | -0.054257 | 0.033786 | -0.020438 | 0.086622 | 0.071848 | -0.053561 | 122.28 | 122.2054 | 122.2679 | 122.1446 | 0.071126 | 0.12394 | -0.015171 | 0.038032 | 0.21797 | 0.096805 | 0.18485 | 0.13062 | 0.23768 | 0.22291 | 0.097501 | 122.3029 | 122.2283 | 122.2908 | 122.1675 | 0.094014 | 0.14683 | 0.007717 | 0.06092 | 122.2089 | 122.2952 | 122.1968 | 122.2831
1276.9688 | 122.3785 | -0.19226 | 122.3145 | 0.062332 | -0.049678 | 0.042944 | -0.020438 | 0.086622 | 0.067269 | -0.048983 | 122.2708 | 122.21 | 122.2633 | 122.14 | 0.084861 | 0.13767 | -0.010593 | 0.047188 | 0.25459 | 0.14258 | 0.2352 | 0.17182 | 0.27888 | 0.25953 | 0.14328 | 122.2937 | 122.2329 | 122.2862 | 122.1629 | 0.10775 | 0.16056 | 0.012295 | 0.070076 | 122.186 | 122.2814 | 122.1785 | 122.2739
1278.7188 | 122.3785 | -0.19684 | 122.2961 | 0.071489 | -0.0451 | 0.038365 | -0.01586 | 0.0912 | 0.071848 | -0.053561 | 122.2708 | 122.21 | 122.2633 | 122.1446 | 0.075705 | 0.12851 | -0.015171 | 0.047188 | 0.26833 | 0.15174 | 0.2352 | 0.18098 | 0.28804 | 0.26869 | 0.14328 | 122.2937 | 122.2329 | 122.2862 | 122.1675 | 0.098593 | 0.1514 | 0.007717 | 0.070076 | 122.1951 | 122.286 | 122.1876 | 122.2785
1280.4219 | 122.3923 | -0.17853 | 122.3007 | 0.071489 | -0.058836 | 0.047522 | -0.01586 | 0.0912 | 0.076426 | -0.044405 | 122.28 | 122.21 | 122.2725 | 122.1492 | 0.080283 | 0.12394 | -0.019749 | 0.04261 | 0.25002 | 0.11969 | 0.22605 | 0.16267 | 0.26973 | 0.25495 | 0.13412 | 122.3029 | 122.2329 | 122.2954 | 122.1721 | 0.10317 | 0.14683 | 0.003139 | 0.065498 | 122.1997 | 122.2997 | 122.1922 | 122.2922
1282.1094 | 122.374 | -0.19226 | 122.319 | 0.06691 | -0.049678 | 0.038365 | -0.029595 | 0.082044 | 0.071848 | -0.048983 | 122.28 | 122.2146 | 122.2633 | 122.1538 | 0.071126 | 0.12851 | -0.015171 | 0.033454 | 0.25917 | 0.14258 | 0.23063 | 0.16267 | 0.27431 | 0.26411 | 0.14328 | 122.3029 | 122.2375 | 122.2862 | 122.1767 | 0.094014 | 0.1514 | 0.007717 | 0.056342 | 122.2089 | 122.2952 | 122.1922 | 122.2785
1283.8594 | 122.4472 | -0.16022 | 122.3053 | 0.06691 | -0.054257 | 0.038365 | -0.020438 | 0.0912 | 0.076426 | -0.039826 | 122.28 | 122.21 | 122.2679 | 122.1446 | 0.080283 | 0.12851 | -0.010593 | 0.047188 | 0.22713 | 0.10596 | 0.19858 | 0.13978 | 0.25142 | 0.23664 | 0.12039 | 122.3029 | 122.2329 | 122.2908 | 122.1675 | 0.10317 | 0.1514 | 0.012295 | 0.070076 | 122.1997 | 122.2906 | 122.1876 | 122.2785
1285.625 | 122.4152 | -0.16479 | 122.3373 | 0.06691 | -0.054257 | 0.042944 | -0.025017 | 0.086622 | 0.067269 | -0.044405 | 122.28 | 122.2146 | 122.2679 | 122.1492 | 0.080283 | 0.12851 | -0.010593 | 0.04261 | 0.2317 | 0.11054 | 0.20774 | 0.13978 | 0.25142 | 0.23206 | 0.12039 | 122.3029 | 122.2375 | 122.2908 | 122.1721 | 0.10317 | 0.1514 | 0.012295 | 0.065498 | 122.1997 | 122.2906 | 122.1876 | 122.2785
1287.3594 | 122.3877 | -0.19226 | 122.3099 | 0.062332 | -0.049678 | 0.033786 | -0.01586 | 0.0912 | 0.067269 | -0.048983 | 122.28 | 122.2054 | 122.2725 | 122.1492 | 0.075705 | 0.12851 | -0.001436 | 0.047188 | 0.25459 | 0.14258 | 0.22605 | 0.1764 | 0.28346 | 0.25953 | 0.14328 | 122.3029 | 122.2283 | 122.2954 | 122.1721 | 0.098593 | 0.1514 | 0.021452 | 0.070076 | 122.2043 | 122.2814 | 122.1968 | 122.2739
1289.1094 | 122.5204 | -0.13733 | 122.2916 | 0.071489 | -0.049678 | 0.042944 | -0.020438 | 0.0912 | 0.067269 | -0.053561 | 122.2754 | 122.2146 | 122.2679 | 122.1492 | 0.080283 | 0.13309 | -0.015171 | 0.04261 | 0.20882 | 0.087651 | 0.18027 | 0.11689 | 0.22853 | 0.2046 | 0.083768 | 122.2983 | 122.2375 | 122.2908 | 122.1721 | 0.10317 | 0.15598 | 0.007717 | 0.065498 | 122.1951 | 122.2906 | 122.1876 | 122.2831
1290.875 | 122.4655 | -0.16937 | 122.2961 | 0.071489 | -0.058836 | 0.033786 | -0.01586 | 0.0912 | 0.076426 | -0.048983 | 122.2754 | 122.2054 | 122.2725 | 122.1538 | 0.080283 | 0.13309 | -0.010593 | 0.04261 | 0.24086 | 0.11054 | 0.20316 | 0.15351 | 0.26057 | 0.2458 | 0.12039 | 122.2983 | 122.2283 | 122.2954 | 122.1767 | 0.10317 | 0.15598 | 0.012295 | 0.065498 | 122.1951 | 122.286 | 122.1922 | 122.2831
1292.6406 | 122.493 | -0.15564 | 122.2778 | 0.071489 | -0.0451 | 0.038365 | -0.025017 | 0.095778 | 0.076426 | -0.053561 | 122.2846 | 122.2146 | 122.2725 | 122.1446 | 0.075705 | 0.13309 | -0.015171 | 0.038032 | 0.22713 | 0.11054 | 0.19401 | 0.13062 | 0.25142 | 0.23207 | 0.10208 | 122.3075 | 122.2375 | 122.2954 | 122.1675 | 0.098593 | 0.15598 | 0.007717 | 0.06092 | 122.2089 | 122.2997 | 122.1968 | 122.2877
1294.3281 | 122.5113 | -0.14648 | 122.2824 | 0.062332 | -0.049678 | 0.038365 | -0.025017 | 0.086622 | 0.067269 | -0.048983 | 122.2846 | 122.2146 | 122.2725 | 122.1492 | 0.075705 | 0.12851 | -0.019749 | 0.038032 | 0.20882 | 0.096806 | 0.18485 | 0.12147 | 0.23311 | 0.21375 | 0.097501 | 122.3075 | 122.2375 | 122.2954 | 122.1721 | 0.098593 | 0.1514 | 0.003139 | 0.06092 | 122.2089 | 122.3043 | 122.1968 | 122.2922
1296.0938 | 122.4014 | -0.17853 | 122.3007 | 0.06691 | -0.049678 | 0.038365 | -0.01586 | 0.086622 | 0.067269 | -0.053561 | 122.2846 | 122.2192 | 122.2725 | 122.1584 | 0.075705 | 0.12851 | -0.006014 | 0.038032 | 0.24544 | 0.12885 | 0.21689 | 0.16267 | 0.26515 | 0.2458 | 0.12497 | 122.3075 | 122.2421 | 122.2954 | 122.1813 | 0.098593 | 0.1514 | 0.016874 | 0.06092 | 122.2089 | 122.2906 | 122.1968 | 122.2785
1297.8438 | 122.4747 | -0.16937 | 122.3099 | 0.071489 | -0.054257 | 0.038365 | -0.020438 | 0.0912 | 0.071848 | -0.053561 | 122.2892 | 122.2146 | 122.2679 | 122.1492 | 0.071126 | 0.13767 | -0.015171 | 0.04261 | 0.24086 | 0.11512 | 0.20774 | 0.14893 | 0.26057 | 0.24122 | 0.11581 | 122.312 | 122.2375 | 122.2908 | 122.1721 | 0.094014 | 0.16056 | 0.007717 | 0.065498 | 122.218 | 122.3043 | 122.1968 | 122.2831
1299.6094 | 122.3557 | -0.1831 | 122.3419 | 0.071489 | -0.049678 | 0.038365 | -0.025017 | 0.082044 | 0.067269 | -0.039826 | 122.2846 | 122.2192 | 122.2725 | 122.1492 | 0.075705 | 0.12851 | -0.019749 | 0.047188 | 0.25459 | 0.13343 | 0.22147 | 0.15809 | 0.26515 | 0.25037 | 0.14328 | 122.3075 | 122.2421 | 122.2954 | 122.1721 | 0.098593 | 0.1514 | 0.003139 | 0.070076 | 122.2089 | 122.3043 | 122.1968 | 122.2922
1301.3594 | 122.3877 | -0.19684 | 122.3282 | 0.06691 | -0.049678 | 0.038365 | -0.020438 | 0.0912 | 0.081005 | -0.048983 | 122.2846 | 122.2192 | 122.2725 | 122.1538 | 0.075705 | 0.12851 | -0.010593 | 0.04261 | 0.26375 | 0.14716 | 0.2352 | 0.1764 | 0.28804 | 0.27784 | 0.14786 | 122.3075 | 122.2421 | 122.2954 | 122.1767 | 0.098593 | 0.1514 | 0.012295 | 0.065498 | 122.2089 | 122.2952 | 122.1968 | 122.2831
1303.0469 | 122.5021 | -0.14191 | 122.2916 | 0.06691 | -0.054257 | 0.038365 | -0.025017 | 0.086622 | 0.071848 | -0.058139 | 122.2892 | 122.2146 | 122.2725 | 122.1492 | 0.084861 | 0.12851 | -0.019749 | 0.04261 | 0.20882 | 0.08765 | 0.18027 | 0.11689 | 0.22853 | 0.21376 | 0.083768 | 122.312 | 122.2375 | 122.2954 | 122.1721 | 0.10775 | 0.1514 | 0.003139 | 0.065498 | 122.2043 | 122.3089 | 122.1876 | 122.2922
1304.7969 | 122.406 | -0.19226 | 122.3099 | 0.062332 | -0.054257 | 0.029208 | -0.025017 | 0.082044 | 0.067269 | -0.053561 | 122.2846 | 122.2146 | 122.2725 | 122.1629 | 0.080283 | 0.12394 | -0.015171 | 0.033454 | 0.25459 | 0.138 | 0.22147 | 0.16724 | 0.27431 | 0.25953 | 0.1387 | 122.3075 | 122.2375 | 122.2954 | 122.1858 | 0.10317 | 0.14683 | 0.007717 | 0.056342 | 122.2043 | 122.2997 | 122.1922 | 122.2877
1306.4844 | 122.4655 | -0.16479 | 122.2824 | 0.071489 | -0.054257 | 0.033786 | -0.025017 | 0.0912 | 0.067269 | -0.048983 | 122.2937 | 122.2192 | 122.2725 | 122.1538 | 0.075705 | 0.13309 | -0.019749 | 0.038032 | 0.23628 | 0.11054 | 0.19858 | 0.13978 | 0.25599 | 0.23206 | 0.11581 | 122.3166 | 122.2421 | 122.2954 | 122.1767 | 0.098593 | 0.15598 | 0.003139 | 0.06092 | 122.218 | 122.3135 | 122.1968 | 122.2922
1308.2344 | 122.4655 | -0.15564 | 122.2961 | 0.076067 | -0.054257 | 0.033786 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.2846 | 122.2146 | 122.2771 | 122.1538 | 0.075705 | 0.12394 | -0.015171 | 0.04261 | 0.23171 | 0.10138 | 0.18943 | 0.1352 | 0.24226 | 0.22749 | 0.10666 | 122.3075 | 122.2375 | 122.3 | 122.1767 | 0.098593 | 0.14683 | 0.007717 | 0.065498 | 122.2089 | 122.2997 | 122.2014 | 122.2922
1310 | 122.5204 | -0.15106 | 122.2549 | 0.071489 | -0.049678 | 0.033786 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 122.2846 | 122.2237 | 122.2725 | 122.1584 | 0.075705 | 0.12394 | -0.015171 | 0.038032 | 0.22255 | 0.10138 | 0.18485 | 0.13062 | 0.23768 | 0.22291 | 0.10208 | 122.3075 | 122.2466 | 122.2954 | 122.1813 | 0.098593 | 0.14683 | 0.007717 | 0.06092 | 122.2089 | 122.2997 | 122.1968 | 122.2877
1311.6875 | 122.4564 | -0.15564 | 122.287 | 0.06691 | -0.054257 | 0.038365 | -0.020438 | 0.086622 | 0.081005 | -0.048983 | 122.2892 | 122.2146 | 122.2725 | 122.1538 | 0.080283 | 0.12851 | -0.015171 | 0.04261 | 0.22255 | 0.10138 | 0.19401 | 0.1352 | 0.24226 | 0.23664 | 0.10666 | 122.312 | 122.2375 | 122.2954 | 122.1767 | 0.10317 | 0.1514 | 0.007717 | 0.065498 | 122.2089 | 122.3043 | 122.1922 | 122.2877
1313.4219 | 122.4976 | -0.13733 | 122.2733 | 0.06691 | -0.054257 | 0.042944 | -0.025017 | 0.0912 | 0.071848 | -0.053561 | 122.2892 | 122.2237 | 122.2771 | 122.1629 | 0.075705 | 0.12851 | -0.015171 | 0.04261 | 0.20424 | 0.083072 | 0.18027 | 0.11231 | 0.22853 | 0.20918 | 0.083768 | 122.312 | 122.2466 | 122.3 | 122.1858 | 0.098593 | 0.1514 | 0.007717 | 0.065498 | 122.2134 | 122.3043 | 122.2014 | 122.2922
1315.1094 | 122.3831 | -0.21057 | 122.3328 | 0.06691 | -0.054257 | 0.038365 | -0.011281 | 0.086622 | 0.067269 | -0.053561 | 122.2983 | 122.2192 | 122.2725 | 122.1584 | 0.075705 | 0.12851 | -0.015171 | 0.04261 | 0.27748 | 0.15631 | 0.24894 | 0.19929 | 0.29719 | 0.27784 | 0.15701 | 122.3212 | 122.2421 | 122.2954 | 122.1813 | 0.098593 | 0.1514 | 0.007717 | 0.065498 | 122.2226 | 122.3135 | 122.1968 | 122.2877
1316.8594 | 122.5067 | -0.17395 | 122.3007 | 0.06691 | -0.058836 | 0.038365 | -0.025017 | 0.082044 | 0.067269 | -0.058139 | 122.2892 | 122.2192 | 122.2817 | 122.1584 | 0.080283 | 0.12851 | -0.019749 | 0.04261 | 0.24086 | 0.11511 | 0.21232 | 0.14893 | 0.25599 | 0.24122 | 0.11581 | 122.312 | 122.2421 | 122.3045 | 122.1813 | 0.10317 | 0.1514 | 0.003139 | 0.065498 | 122.2089 | 122.3089 | 122.2014 | 122.3014
1318.6094 | 122.4243 | -0.17853 | 122.2916 | 0.057754 | -0.049678 | 0.033786 | -0.01586 | 0.0912 | 0.071848 | -0.048983 | 122.2892 | 122.2192 | 122.2817 | 122.1629 | 0.075705 | 0.12851 | -0.010593 | 0.04261 | 0.23628 | 0.12885 | 0.21231 | 0.16267 | 0.26973 | 0.25038 | 0.12954 | 122.312 | 122.2421 | 122.3045 | 122.1858 | 0.098593 | 0.1514 | 0.012295 | 0.065498 | 122.2134 | 122.2997 | 122.2059 | 122.2922
1320.375 | 122.5525 | -0.16022 | 122.2778 | 0.06691 | -0.049678 | 0.047522 | -0.025017 | 0.0912 | 0.067269 | -0.048983 | 122.2983 | 122.2283 | 122.2679 | 122.1492 | 0.080283 | 0.11936 | -0.019749 | 0.038032 | 0.22713 | 0.11054 | 0.20774 | 0.1352 | 0.25142 | 0.22749 | 0.11123 | 122.3212 | 122.2512 | 122.2908 | 122.1721 | 0.10317 | 0.14225 | 0.003139 | 0.06092 | 122.218 | 122.3181 | 122.1876 | 122.2877
1322.125 | 122.438 | -0.14191 | 122.2961 | 0.062332 | -0.054257 | 0.042944 | -0.020438 | 0.095778 | 0.081005 | -0.048983 | 122.2937 | 122.2237 | 122.2817 | 122.1492 | 0.080283 | 0.12394 | -0.010593 | 0.04261 | 0.20424 | 0.08765 | 0.18485 | 0.12147 | 0.23769 | 0.22291 | 0.092924 | 122.3166 | 122.2466 | 122.3045 | 122.1721 | 0.10317 | 0.14683 | 0.012295 | 0.065498 | 122.2134 | 122.3043 | 122.2014 | 122.2922
1323.875 | 122.3923 | -0.18768 | 122.3373 | 0.062332 | -0.058836 | 0.042944 | -0.01586 | 0.0912 | 0.071848 | -0.048983 | 122.2983 | 122.2283 | 122.2771 | 122.1629 | 0.071126 | 0.11936 | -0.006014 | 0.04261 | 0.25001 | 0.12885 | 0.23063 | 0.17182 | 0.27888 | 0.25953 | 0.1387 | 122.3212 | 122.2512 | 122.3 | 122.1858 | 0.094014 | 0.14225 | 0.016874 | 0.065498 | 122.2272 | 122.3043 | 122.2059 | 122.2831
1325.6406 | 122.4838 | -0.14191 | 122.3053 | 0.062332 | -0.058836 | 0.038365 | -0.01586 | 0.095778 | 0.067269 | -0.053561 | 122.2983 | 122.2237 | 122.2725 | 122.1584 | 0.071126 | 0.12851 | -0.010593 | 0.033454 | 0.20424 | 0.083071 | 0.18027 | 0.12605 | 0.23769 | 0.20918 | 0.088346 | 122.3212 | 122.2466 | 122.2954 | 122.1813 | 0.094014 | 0.1514 | 0.012295 | 0.056342 | 122.2272 | 122.3089 | 122.2014 | 122.2831
1327.375 | 122.5159 | -0.14648 | 122.2778 | 0.062332 | -0.054257 | 0.038365 | -0.020438 | 0.0912 | 0.067269 | -0.048983 | 122.2983 | 122.2237 | 122.2771 | 122.1584 | 0.075705 | 0.12394 | -0.015171 | 0.047188 | 0.20882 | 0.092227 | 0.18485 | 0.12605 | 0.23768 | 0.21375 | 0.097501 | 122.3212 | 122.2466 | 122.3 | 122.1813 | 0.098593 | 0.14683 | 0.007717 | 0.070076 | 122.2226 | 122.3135 | 122.2014 | 122.2922
1329.0625 | 122.5296 | -0.13733 | 122.2778 | 0.057754 | -0.049678 | 0.042944 | -0.020438 | 0.082044 | 0.062691 | -0.053561 | 122.2983 | 122.2329 | 122.2771 | 122.1584 | 0.075705 | 0.12394 | -0.001436 | 0.051766 | 0.19508 | 0.087651 | 0.18027 | 0.11689 | 0.21937 | 0.20002 | 0.083768 | 122.3212 | 122.2558 | 122.3 | 122.1813 | 0.098593 | 0.14683 | 0.021452 | 0.074654 | 122.2226 | 122.2997 | 122.2014 | 122.2785
1330.8281 | 122.4426 | -0.15564 | 122.3282 | 0.062332 | -0.058836 | 0.042944 | -0.01586 | 0.0912 | 0.076426 | -0.044405 | 122.3029 | 122.2329 | 122.2817 | 122.1629 | 0.075705 | 0.12394 | -0.015171 | 0.033454 | 0.21797 | 0.096804 | 0.19858 | 0.13978 | 0.24684 | 0.23207 | 0.11124 | 122.3258 | 122.2558 | 122.3045 | 122.1858 | 0.098593 | 0.14683 | 0.007717 | 0.056342 | 122.2272 | 122.3181 | 122.2059 | 122.2968
1332.5156 | 122.3785 | -0.19226 | 122.3419 | 0.071489 | -0.049678 | 0.038365 | -0.011281 | 0.086622 | 0.076426 | -0.039826 | 122.3029 | 122.2421 | 122.2862 | 122.1675 | 0.066548 | 0.12394 | -0.019749 | 0.033454 | 0.26375 | 0.14258 | 0.23063 | 0.18098 | 0.27888 | 0.26869 | 0.15243 | 122.3258 | 122.2649 | 122.3091 | 122.1904 | 0.089436 | 0.14683 | 0.003139 | 0.056342 | 122.2363 | 122.3226 | 122.2197 | 122.306
1334.2656 | 122.3923 | -0.16937 | 122.3465 | 0.06691 | -0.054257 | 0.038365 | -0.01586 | 0.0912 | 0.071848 | -0.048983 | 122.312 | 122.2375 | 122.2862 | 122.1721 | 0.06197 | 0.11936 | -0.010593 | 0.033454 | 0.23628 | 0.11512 | 0.20774 | 0.15351 | 0.26057 | 0.24122 | 0.12039 | 122.3349 | 122.2604 | 122.3091 | 122.195 | 0.084858 | 0.14225 | 0.012295 | 0.056342 | 122.2501 | 122.3226 | 122.2243 | 122.2968
1336.0156 | 122.4243 | -0.19226 | 122.319 | 0.062332 | -0.058836 | 0.047522 | -0.020438 | 0.0912 | 0.071848 | -0.053561 | 122.3029 | 122.2421 | 122.2817 | 122.1721 | 0.075705 | 0.11478 | -0.019749 | 0.04261 | 0.25459 | 0.13342 | 0.23978 | 0.17182 | 0.28346 | 0.26411 | 0.1387 | 122.3258 | 122.2649 | 122.3045 | 122.195 | 0.098593 | 0.13767 | 0.003139 | 0.065498 | 122.2272 | 122.3226 | 122.2059 | 122.3014
1337.7031 | 122.406 | -0.1831 | 122.3511 | 0.057754 | -0.049678 | 0.038365 | -0.01586 | 0.0912 | 0.071848 | -0.044405 | 122.3075 | 122.2375 | 122.2862 | 122.1767 | 0.066548 | 0.11478 | -0.015171 | 0.033454 | 0.24086 | 0.13343 | 0.22147 | 0.16724 | 0.27431 | 0.25495 | 0.1387 | 122.3304 | 122.2604 | 122.3091 | 122.1996 | 0.089436 | 0.13767 | 0.007717 | 0.056342 | 122.2409 | 122.3226 | 122.2197 | 122.3014
1339.4375 | 117.7597 | -92.363 | 25.2365 | 0.076067 | -0.077151 | 0.010893 | -0.034174 | 0.063733 | 0.048956 | -0.08103 | 25.3441 | 25.3543 | 25.3274 | 25.2386 | 92.4724 | 92.4498 | 92.1752 | 92.3065 | 92.439 | 92.2858 | 92.3739 | 92.3288 | 92.4267 | 92.4119 | 92.2819 | 25.367 | 25.3772 | 25.3503 | 25.2615 | 92.4953 | 92.4727 | 92.1981 | 92.3294 | -67.1283 | -66.8312 | -67.145 | -66.8478
1341.1875 | 117.2836 | -92.0242 | 25.0305 | 0.085224 | -0.072572 | 0.010893 | -0.038752 | 0.072888 | 0.053534 | -0.067295 | 25.1152 | 25.1345 | 25.0893 | 25.0142 | 92.1611 | 92.1293 | 91.8548 | 91.9861 | 92.1095 | 91.9517 | 92.0351 | 91.9855 | 92.0971 | 92.0778 | 91.9569 | 25.1381 | 25.1574 | 25.1122 | 25.0371 | 92.184 | 92.1522 | 91.8776 | 92.009 | -67.0459 | -66.7396 | -67.0717 | -66.7654
1342.875 | 116.7892 | -91.7358 | 24.9481 | 0.080646 | -0.077151 | 0.015472 | -0.034174 | 0.06831 | 0.048956 | -0.062717 | 24.9961 | 25.0109 | 24.9154 | 24.8951 | 91.8589 | 91.8363 | 91.5663 | 91.6976 | 91.8165 | 91.6587 | 91.7513 | 91.7017 | 91.8041 | 91.7848 | 91.6731 | 25.019 | 25.0338 | 24.9382 | 24.918 | 91.8818 | 91.8592 | 91.5892 | 91.7205 | -66.8628 | -66.5702 | -66.9436 | -66.651
1344.625 | 116.5009 | -91.4886 | 24.852 | 0.085224 | -0.077151 | 0.020051 | -0.038752 | 0.06831 | 0.053534 | -0.071874 | 24.8908 | 24.9193 | 24.8192 | 24.7303 | 91.6163 | 91.58 | 91.0902 | 91.4458 | 91.5739 | 91.4115 | 91.5087 | 91.4499 | 91.557 | 91.5422 | 91.4168 | 24.9137 | 24.9422 | 24.8421 | 24.7532 | 91.6392 | 91.6028 | 91.1131 | 91.4687 | -66.7255 | -66.1993 | -66.7971 | -66.271
1346.375 | 116.2949 | -91.2872 | 24.7513 | 0.076067 | -0.077151 | 0.020051 | -0.034174 | 0.072888 | 0.053534 | -0.071874 | 24.8313 | 24.7774 | 24.7414 | 24.6662 | 91.4194 | 91.3877 | 90.8887 | 91.2536 | 91.3633 | 91.2101 | 91.3073 | 91.2531 | 91.3601 | 91.3408 | 91.2154 | 24.8542 | 24.8002 | 24.7643 | 24.6891 | 91.4423 | 91.4106 | 90.9116 | 91.2764 | -66.5881 | -66.0574 | -66.678 | -66.1473
1348.0625 | 116.0706 | -91.1179 | 24.7055 | 0.080646 | -0.067994 | 0.020051 | -0.034174 | 0.063733 | 0.053534 | -0.071874 | 24.7626 | 24.7087 | 24.6819 | 24.6021 | 91.0761 | 91.2412 | 90.7422 | 91.1025 | 91.1985 | 91.0499 | 91.1379 | 91.0837 | 91.1816 | 91.1714 | 91.046 | 24.7855 | 24.7316 | 24.7048 | 24.625 | 91.0989 | 91.2641 | 90.7651 | 91.1254 | -66.3134 | -65.9796 | -66.3942 | -66.0603
1349.7969 | 115.8875 | -91.0309 | 24.6506 | 0.080646 | -0.072572 | 0.015472 | -0.043331 | 0.063733 | 0.053534 | -0.062717 | 24.7031 | 24.6675 | 24.6315 | 24.5471 | 90.9616 | 91.1222 | 90.6278 | 90.988 | 91.1115 | 90.9583 | 91.0464 | 90.9876 | 91.0946 | 91.0844 | 90.9682 | 24.726 | 24.6904 | 24.6544 | 24.57 | 90.9845 | 91.145 | 90.6506 | 91.0109 | -66.2585 | -65.9246 | -66.3301 | -65.9962
1351.5469 | 115.7959 | -90.8844 | 24.5865 | 0.080646 | -0.077151 | 0.020051 | -0.038752 | 0.072888 | 0.048956 | -0.071874 | 24.6619 | 24.6125 | 24.5903 | 24.5059 | 90.8746 | 91.026 | 90.5316 | 90.8919 | 90.965 | 90.8072 | 90.9044 | 90.8456 | 90.9573 | 90.9334 | 90.8125 | 24.6848 | 24.6354 | 24.6132 | 24.5288 | 90.8975 | 91.0489 | 90.5545 | 90.9148 | -66.2127 | -65.8697 | -66.2843 | -65.9413
1353.2969 | 114.8621 | -29.4479 | 85.4691 | 0.089802 | -0.0451 | 0.047522 | -0.002124 | 0.10493 | 0.09474 | -0.035248 | 79.9793 | 80.0208 | 79.9371 | 79.8664 | 34.531 | 34.4915 | 34.2678 | 34.4155 | 29.5377 | 29.4028 | 29.4955 | 29.4458 | 29.5529 | 29.5427 | 29.4127 | 80.0022 | 80.0437 | 79.96 | 79.8893 | 34.5539 | 34.5144 | 34.2907 | 34.4384 | 45.4482 | 45.7115 | 45.4061 | 45.6693
1355 | 119.0094 | -0.16937 | 118.9087 | 0.080646 | -0.054257 | 0.047522 | -0.01586 | 0.0912 | 0.071848 | -0.048983 | 118.8415 | 118.7759 | 118.8159 | 118.6966 | 0.084861 | 0.12394 | -0.001436 | 0.056344 | 0.25002 | 0.11512 | 0.2169 | 0.15351 | 0.26057 | 0.24122 | 0.12039 | 118.8644 | 118.7988 | 118.8388 | 118.7195 | 0.10775 | 0.14683 | 0.021452 | 0.079232 | 118.7567 | 118.843 | 118.731 | 118.8173
1356.75 | 115.7547 | -24.6185 | 91.301 | 0.071489 | -0.077151 | 0.020051 | -0.029595 | 0.086622 | 0.071848 | -0.058139 | 102.1529 | 101.9991 | 102.1281 | 101.9832 | 14.7854 | 14.6959 | 14.5624 | 14.6378 | 24.69 | 24.5414 | 24.6386 | 24.5889 | 24.7052 | 24.6904 | 24.5604 | 102.1758 | 102.022 | 102.151 | 102.006 | 14.8083 | 14.7188 | 14.5853 | 14.6607 | 87.3676 | 87.5905 | 87.3427 | 87.5656
1358.5 | 119.101 | -0.15564 | 118.9362 | 0.085224 | -0.058836 | 0.042944 | -0.025017 | 0.086622 | 0.071848 | -0.044405 | 118.9102 | 118.8583 | 118.8891 | 118.7882 | 0.094017 | 0.14225 | -0.006014 | 0.11586 | 0.24086 | 0.096804 | 0.19858 | 0.13062 | 0.24226 | 0.22749 | 0.11124 | 118.9331 | 118.8812 | 118.912 | 118.8111 | 0.11691 | 0.16514 | 0.016874 | 0.13875 | 118.8162 | 118.9162 | 118.7951 | 118.8952
1360.1875 | 119.2932 | -0.14191 | 119.0735 | 0.085224 | -0.058836 | 0.038365 | -0.011281 | 0.086622 | 0.067269 | -0.053561 | 119.0338 | 118.959 | 119.0082 | 118.8889 | 0.20389 | 0.14683 | 0.062662 | 0.11128 | 0.22713 | 0.083071 | 0.18027 | 0.13063 | 0.22853 | 0.20918 | 0.088346 | 119.0567 | 118.9819 | 119.0311 | 118.9118 | 0.22678 | 0.16972 | 0.08555 | 0.13417 | 118.8299 | 118.9712 | 118.8043 | 118.9455
1361.9375 | 119.3024 | -0.20142 | 119.1925 | 0.089802 | -0.058836 | 0.033786 | -0.01586 | 0.077466 | 0.076426 | -0.048983 | 119.1391 | 119.0781 | 119.1135 | 119.008 | 0.094017 | 0.15141 | 0.003143 | 0.1067 | 0.29122 | 0.14258 | 0.2352 | 0.18556 | 0.27888 | 0.27784 | 0.15243 | 119.162 | 119.101 | 119.1364 | 119.0309 | 0.11691 | 0.17429 | 0.026031 | 0.12959 | 119.0451 | 119.136 | 119.0195 | 119.1103
1363.6875 | 116.2582 | -26.7105 | 89.209 | 0.053175 | -0.11378 | -0.025735 | -0.079959 | 0.022531 | 0.00775 | -0.10392 | 111.3923 | 111.1064 | 111.4769 | 111.2145 | 7.3001 | 7.1787 | 7.0768 | 7.1205 | 26.7637 | 26.5967 | 26.6848 | 26.6306 | 26.733 | 26.7183 | 26.6066 | 111.4152 | 111.1293 | 111.4998 | 111.2374 | 7.3229 | 7.2016 | 7.0996 | 7.1434 | 104.0923 | 104.3156 | 104.1769 | 104.4002
1365.4219 | 119.3344 | -0.1831 | 119.2383 | 0.085224 | -0.054257 | 0.038365 | -0.020438 | 0.0912 | 0.067269 | -0.048983 | 119.1712 | 119.1056 | 119.141 | 119.0446 | 0.094017 | 0.14683 | 0.003143 | 0.051766 | 0.26833 | 0.12885 | 0.22147 | 0.16267 | 0.27431 | 0.25037 | 0.13412 | 119.1941 | 119.1285 | 119.1638 | 119.0675 | 0.11691 | 0.16972 | 0.026031 | 0.074654 | 119.0772 | 119.1681 | 119.0469 | 119.1378
1367.1094 | 119.4168 | -0.19226 | 119.3024 | 0.080646 | -0.054257 | 0.047522 | -0.011281 | 0.095778 | 0.076426 | -0.048983 | 119.2765 | 119.2109 | 119.2508 | 119.1408 | 0.094017 | 0.13309 | -0.006014 | 0.051766 | 0.27291 | 0.138 | 0.23978 | 0.18098 | 0.28804 | 0.26869 | 0.14328 | 119.2994 | 119.2338 | 119.2737 | 119.1637 | 0.11691 | 0.15598 | 0.016874 | 0.074654 | 119.1825 | 119.2825 | 119.1568 | 119.2568
1368.8594 | 119.4946 | -0.17853 | 119.3665 | 0.085224 | -0.072572 | 0.042944 | -0.011281 | 0.086622 | 0.071848 | -0.044405 | 119.3498 | 119.2704 | 119.3103 | 119.2049 | 0.089439 | 0.14225 | -0.001436 | 0.047188 | 0.26375 | 0.10596 | 0.22147 | 0.16725 | 0.26515 | 0.25038 | 0.13412 | 119.3726 | 119.2933 | 119.3332 | 119.2278 | 0.11233 | 0.16514 | 0.021452 | 0.070076 | 119.2603 | 119.3512 | 119.2209 | 119.3118
1370.625 | 119.6091 | -0.16937 | 119.4214 | 0.085224 | -0.058836 | 0.042944 | -0.01586 | 0.086622 | 0.071848 | -0.044405 | 119.391 | 119.3345 | 119.3653 | 119.2553 | 0.098596 | 0.14683 | -0.001436 | 0.051766 | 0.2546 | 0.11054 | 0.21232 | 0.15351 | 0.25599 | 0.24122 | 0.12497 | 119.4139 | 119.3574 | 119.3882 | 119.2781 | 0.12148 | 0.16972 | 0.021452 | 0.074654 | 119.2924 | 119.3924 | 119.2667 | 119.3667
1372.3281 | 119.6869 | -0.17853 | 119.4305 | 0.089802 | -0.058836 | 0.042944 | -0.01586 | 0.0912 | 0.067269 | -0.048983 | 119.4322 | 119.3666 | 119.4111 | 119.301 | 0.098596 | 0.15598 | -0.001436 | 0.051766 | 0.26833 | 0.11969 | 0.22147 | 0.16267 | 0.26973 | 0.2458 | 0.12954 | 119.4551 | 119.3895 | 119.434 | 119.3239 | 0.12148 | 0.17887 | 0.021452 | 0.074654 | 119.3336 | 119.4336 | 119.3125 | 119.4125
1374.0156 | 119.7327 | -0.13733 | 119.4717 | 0.080646 | -0.054257 | 0.033786 | -0.025017 | 0.086622 | 0.071848 | -0.044405 | 119.478 | 119.4169 | 119.4477 | 119.3377 | 0.10317 | 0.15141 | 0.003143 | 0.060923 | 0.21798 | 0.083072 | 0.17112 | 0.11231 | 0.22395 | 0.20918 | 0.092924 | 119.5008 | 119.4398 | 119.4706 | 119.3606 | 0.12606 | 0.17429 | 0.026031 | 0.083811 | 119.3748 | 119.4748 | 119.3445 | 119.4446
1375.7656 | 119.7784 | -0.17853 | 119.5358 | 0.085224 | -0.054257 | 0.038365 | -0.025017 | 0.086622 | 0.067269 | -0.044405 | 119.5283 | 119.4627 | 119.4935 | 119.3926 | 0.10775 | 0.16056 | 0.003143 | 0.060923 | 0.26375 | 0.12427 | 0.21689 | 0.15351 | 0.26515 | 0.2458 | 0.13412 | 119.5512 | 119.4856 | 119.5164 | 119.4155 | 0.13064 | 0.18345 | 0.026031 | 0.083811 | 119.4206 | 119.5252 | 119.3857 | 119.4903
1377.5312 | 119.6869 | -0.21515 | 119.5953 | 0.080646 | -0.063415 | 0.038365 | -0.020438 | 0.0912 | 0.071848 | -0.044405 | 119.5741 | 119.5085 | 119.5438 | 119.4338 | 0.10317 | 0.15141 | 0.007721 | 0.051766 | 0.2958 | 0.15173 | 0.25351 | 0.19471 | 0.30635 | 0.287 | 0.17074 | 119.597 | 119.5314 | 119.5667 | 119.4567 | 0.12606 | 0.17429 | 0.030609 | 0.074654 | 119.4709 | 119.5664 | 119.4407 | 119.5361
1379.2188 | 119.8746 | -0.17853 | 119.632 | 0.071489 | -0.063415 | 0.038365 | -0.01586 | 0.082044 | 0.071848 | -0.048983 | 119.6199 | 119.5451 | 119.5942 | 119.4751 | 0.098596 | 0.15141 | 0.007721 | 0.065501 | 0.25002 | 0.11511 | 0.21689 | 0.16267 | 0.26057 | 0.25038 | 0.12954 | 119.6428 | 119.568 | 119.6171 | 119.4979 | 0.12148 | 0.17429 | 0.030609 | 0.088389 | 119.5213 | 119.6122 | 119.4956 | 119.5865
1380.9688 | 119.8791 | -0.1831 | 119.6777 | 0.094381 | -0.063415 | 0.042944 | -0.020438 | 0.086622 | 0.067269 | -0.044405 | 119.6519 | 119.5955 | 119.6354 | 119.5117 | 0.10317 | 0.16514 | 0.007721 | 0.056344 | 0.27749 | 0.11969 | 0.22605 | 0.16267 | 0.26973 | 0.25037 | 0.1387 | 119.6748 | 119.6184 | 119.6583 | 119.5346 | 0.12606 | 0.18803 | 0.030609 | 0.079232 | 119.5488 | 119.6442 | 119.5322 | 119.6277
1382.7344 | 119.8746 | -0.17395 | 119.7189 | 0.080646 | -0.049678 | 0.038365 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 119.7023 | 119.623 | 119.672 | 119.5575 | 0.10317 | 0.15598 | 0.007721 | 0.060923 | 0.2546 | 0.12427 | 0.21232 | 0.15351 | 0.26057 | 0.2458 | 0.12497 | 119.7252 | 119.6459 | 119.6949 | 119.5804 | 0.12606 | 0.17887 | 0.030609 | 0.083811 | 119.5991 | 119.6946 | 119.5689 | 119.6643
1384.4219 | 119.8608 | -0.2243 | 119.7601 | 0.089802 | -0.063415 | 0.042944 | -0.01586 | 0.0912 | 0.076426 | -0.039826 | 119.7435 | 119.6642 | 119.7132 | 119.5895 | 0.10317 | 0.15598 | -0.001436 | 0.056344 | 0.31411 | 0.16089 | 0.26725 | 0.20844 | 0.3155 | 0.30073 | 0.18448 | 119.7664 | 119.6871 | 119.7361 | 119.6124 | 0.12606 | 0.17887 | 0.021452 | 0.079232 | 119.6403 | 119.7449 | 119.6101 | 119.7147
1386.125 | 119.9936 | -0.18768 | 119.783 | 0.085224 | -0.049678 | 0.033786 | -0.01586 | 0.0912 | 0.071848 | -0.053561 | 119.7756 | 119.71 | 119.7453 | 119.6307 | 0.098596 | 0.15141 | 0.007721 | 0.056344 | 0.27291 | 0.138 | 0.22147 | 0.17182 | 0.27888 | 0.25953 | 0.13412 | 119.7984 | 119.7329 | 119.7682 | 119.6536 | 0.12148 | 0.17429 | 0.030609 | 0.079232 | 119.677 | 119.7678 | 119.6467 | 119.7376
1387.875 | 119.9249 | -0.2243 | 119.8608 | 0.089802 | -0.049678 | 0.042944 | -0.01586 | 0.0912 | 0.071848 | -0.048983 | 119.8122 | 119.742 | 119.7865 | 119.6674 | 0.10317 | 0.15598 | 0.003143 | 0.060923 | 0.31411 | 0.17463 | 0.26725 | 0.20844 | 0.3155 | 0.29615 | 0.17532 | 119.8351 | 119.7649 | 119.8094 | 119.6903 | 0.12606 | 0.17887 | 0.026031 | 0.083811 | 119.709 | 119.809 | 119.6833 | 119.7833
1389.625 | 120.0806 | -0.19226 | 119.8563 | 0.080646 | -0.058836 | 0.038365 | -0.020438 | 0.086622 | 0.071848 | -0.048983 | 119.8351 | 119.7787 | 119.814 | 119.704 | 0.10317 | 0.15598 | 0.007721 | 0.065501 | 0.27291 | 0.13342 | 0.23063 | 0.17182 | 0.27888 | 0.26411 | 0.14328 | 119.858 | 119.8015 | 119.8368 | 119.7269 | 0.12606 | 0.17887 | 0.030609 | 0.088389 | 119.7319 | 119.8274 | 119.7108 | 119.8062
1391.3125 | 120.0577 | -0.20142 | 119.9203 | 0.080646 | -0.054257 | 0.042944 | -0.01586 | 0.095778 | 0.067269 | -0.044405 | 119.8809 | 119.8107 | 119.8552 | 119.7315 | 0.10775 | 0.15598 | -0.001436 | 0.056344 | 0.28206 | 0.14716 | 0.24436 | 0.18556 | 0.29719 | 0.26869 | 0.15701 | 119.9038 | 119.8336 | 119.8781 | 119.7544 | 0.13064 | 0.17887 | 0.021452 | 0.079232 | 119.7731 | 119.8823 | 119.7474 | 119.8566
1393 | 120.0439 | -0.23804 | 119.9478 | 0.089802 | -0.054257 | 0.033786 | -0.020438 | 0.0912 | 0.067269 | -0.039826 | 119.9175 | 119.8473 | 119.8918 | 119.7727 | 0.10775 | 0.15141 | 0.012299 | 0.056344 | 0.32784 | 0.18378 | 0.27182 | 0.2176 | 0.32924 | 0.30531 | 0.19821 | 119.9404 | 119.8702 | 119.9147 | 119.7956 | 0.13064 | 0.17429 | 0.035187 | 0.079232 | 119.8097 | 119.9052 | 119.784 | 119.8795
1394.75 | 120.1355 | -0.19684 | 119.9615 | 0.085224 | -0.040521 | 0.038365 | -0.020438 | 0.0912 | 0.071848 | -0.053561 | 119.9495 | 119.8748 | 119.9193 | 119.8093 | 0.098596 | 0.15141 | -0.001436 | 0.056344 | 0.28206 | 0.15632 | 0.2352 | 0.1764 | 0.28804 | 0.26869 | 0.14328 | 119.9724 | 119.8977 | 119.9421 | 119.8322 | 0.12148 | 0.17429 | 0.021452 | 0.079232 | 119.8509 | 119.951 | 119.8207 | 119.9207
1396.5 | 120.2316 | -0.18768 | 119.9707 | 0.071489 | -0.058836 | 0.038365 | -0.020438 | 0.095778 | 0.076426 | -0.048983 | 119.9816 | 119.9114 | 119.9513 | 119.8368 | 0.098596 | 0.15141 | 0.007721 | 0.056344 | 0.25917 | 0.12885 | 0.22605 | 0.16724 | 0.28346 | 0.26411 | 0.1387 | 120.0045 | 119.9343 | 119.9742 | 119.8597 | 0.12148 | 0.17429 | 0.030609 | 0.079232 | 119.883 | 119.9739 | 119.8527 | 119.9436
1398.2031 | 120.2179 | -0.19226 | 120.0302 | 0.076067 | -0.063415 | 0.047522 | -0.020438 | 0.095778 | 0.067269 | -0.053561 | 120.0136 | 119.9389 | 119.9788 | 119.8643 | 0.10317 | 0.15598 | -0.001436 | 0.060923 | 0.26833 | 0.12885 | 0.23978 | 0.17182 | 0.28804 | 0.25953 | 0.1387 | 120.0365 | 119.9618 | 120.0017 | 119.8872 | 0.12606 | 0.17887 | 0.021452 | 0.083811 | 119.9105 | 120.0151 | 119.8756 | 119.9802
1399.9531 | 120.1447 | -0.21515 | 120.0577 | 0.085224 | -0.063415 | 0.038365 | -0.020438 | 0.086622 | 0.076426 | -0.044405 | 120.0457 | 119.971 | 120.02 | 119.8963 | 0.098596 | 0.15598 | 0.003143 | 0.056344 | 0.30037 | 0.15173 | 0.25351 | 0.19471 | 0.30177 | 0.29158 | 0.17074 | 120.0686 | 119.9939 | 120.0429 | 119.9192 | 0.12148 | 0.17887 | 0.026031 | 0.079232 | 119.9471 | 120.0425 | 119.9214 | 120.0168
1401.6562 | 120.1904 | -0.21515 | 120.1035 | 0.089802 | -0.054257 | 0.047522 | -0.01586 | 0.095778 | 0.071848 | -0.039826 | 120.0777 | 120.003 | 120.0475 | 119.933 | 0.10317 | 0.16056 | 0.007721 | 0.056344 | 0.30495 | 0.16089 | 0.26267 | 0.19929 | 0.31093 | 0.287 | 0.17532 | 120.1006 | 120.0259 | 120.0703 | 119.9558 | 0.12606 | 0.18345 | 0.030609 | 0.079232 | 119.9746 | 120.07 | 119.9443 | 120.0397
1403.4062 | 120.3598 | -0.15564 | 120.1035 | 0.085224 | -0.0451 | 0.033786 | -0.020438 | 0.086622 | 0.076426 | -0.039826 | 120.1006 | 120.0305 | 120.0749 | 119.9559 | 0.10317 | 0.16056 | 0.003143 | 0.056344 | 0.24086 | 0.11054 | 0.18943 | 0.1352 | 0.24226 | 0.23207 | 0.11581 | 120.1235 | 120.0534 | 120.0978 | 119.9787 | 0.12606 | 0.18345 | 0.026031 | 0.079232 | 119.9975 | 120.0975 | 119.9717 | 120.0718
1405.1094 | 120.3873 | -0.16022 | 120.1263 | 0.089802 | -0.054257 | 0.038365 | -0.025017 | 0.10036 | 0.071848 | -0.053561 | 120.1327 | 120.0625 | 120.1024 | 119.9833 | 0.094017 | 0.16056 | -0.001436 | 0.056344 | 0.25002 | 0.10596 | 0.19858 | 0.1352 | 0.26057 | 0.23206 | 0.10666 | 120.1556 | 120.0854 | 120.1253 | 120.0062 | 0.11691 | 0.18345 | 0.021452 | 0.079232 | 120.0387 | 120.1341 | 120.0084 | 120.1038
1406.875 | 120.3049 | -0.2243 | 120.1996 | 0.085224 | -0.054257 | 0.042944 | -0.01586 | 0.082044 | 0.076426 | -0.048983 | 120.1556 | 120.0809 | 120.1299 | 120.0154 | 0.094017 | 0.15598 | 0.007721 | 0.051766 | 0.30953 | 0.17005 | 0.26725 | 0.20844 | 0.30635 | 0.30073 | 0.17532 | 120.1785 | 120.1037 | 120.1527 | 120.0383 | 0.11691 | 0.17887 | 0.030609 | 0.074654 | 120.0616 | 120.1479 | 120.0358 | 120.1221
1408.625 | 120.314 | -0.23346 | 120.2225 | 0.089802 | -0.058836 | 0.038365 | -0.025017 | 0.0912 | 0.071848 | -0.048983 | 120.1785 | 120.1175 | 120.1528 | 120.0383 | 0.10775 | 0.15598 | 0.003143 | 0.056344 | 0.32326 | 0.17462 | 0.27182 | 0.20844 | 0.32466 | 0.30531 | 0.18448 | 120.2014 | 120.1404 | 120.1756 | 120.0612 | 0.13064 | 0.17887 | 0.026031 | 0.079232 | 120.0707 | 120.1753 | 120.045 | 120.1496
1410.3125 | 120.3781 | -0.21057 | 120.2545 | 0.089802 | -0.058836 | 0.038365 | -0.01586 | 0.086622 | 0.071848 | -0.044405 | 120.2197 | 120.1404 | 120.1894 | 120.0703 | 0.10317 | 0.16972 | 0.003143 | 0.060923 | 0.30037 | 0.15174 | 0.24894 | 0.19471 | 0.29719 | 0.28242 | 0.16617 | 120.2426 | 120.1633 | 120.2123 | 120.0932 | 0.12606 | 0.19261 | 0.026031 | 0.083811 | 120.1165 | 120.2165 | 120.0862 | 120.1862
1412 | 120.3644 | -0.21515 | 120.2957 | 0.089802 | -0.058836 | 0.042944 | -0.01586 | 0.086622 | 0.071848 | -0.044405 | 120.238 | 120.1633 | 120.2077 | 120.0932 | 0.098596 | 0.15598 | 0.003143 | 0.051766 | 0.30495 | 0.15631 | 0.25809 | 0.19929 | 0.30177 | 0.287 | 0.17074 | 120.2609 | 120.1862 | 120.2306 | 120.1161 | 0.12148 | 0.17887 | 0.026031 | 0.074654 | 120.1394 | 120.2348 | 120.1091 | 120.2046
1413.75 | 120.5109 | -0.16479 | 120.2545 | 0.089802 | -0.054257 | 0.033786 | -0.011281 | 0.0912 | 0.076426 | -0.048983 | 120.2609 | 120.1953 | 120.2352 | 120.1161 | 0.10317 | 0.15598 | 0.003143 | 0.056344 | 0.2546 | 0.11054 | 0.19858 | 0.15351 | 0.25599 | 0.24122 | 0.11581 | 120.2838 | 120.2182 | 120.258 | 120.139 | 0.12606 | 0.17887 | 0.026031 | 0.079232 | 120.1577 | 120.2577 | 120.132 | 120.232
1415.5156 | 120.5429 | -0.19226 | 120.2728 | 0.085224 | -0.067994 | 0.038365 | -0.01586 | 0.0912 | 0.062691 | -0.048983 | 120.2883 | 120.2182 | 120.2581 | 120.1482 | 0.10317 | 0.15141 | -0.001436 | 0.056344 | 0.27748 | 0.12427 | 0.23063 | 0.1764 | 0.28346 | 0.25495 | 0.14328 | 120.3112 | 120.2411 | 120.2809 | 120.1711 | 0.12606 | 0.17429 | 0.021452 | 0.079232 | 120.1852 | 120.2898 | 120.1549 | 120.2595
1417.2812 | 120.433 | -0.21057 | 120.3506 | 0.085224 | -0.054257 | 0.052101 | -0.01586 | 0.086622 | 0.067269 | -0.053561 | 120.3158 | 120.2365 | 120.2809 | 120.1665 | 0.098596 | 0.16056 | -0.001436 | 0.056344 | 0.2958 | 0.15631 | 0.26267 | 0.19471 | 0.29719 | 0.27784 | 0.15701 | 120.3387 | 120.2594 | 120.3038 | 120.1894 | 0.12148 | 0.18345 | 0.021452 | 0.079232 | 120.2172 | 120.3173 | 120.1823 | 120.2824
1418.9688 | 120.4605 | -0.21057 | 120.3644 | 0.080646 | -0.049678 | 0.042944 | -0.020438 | 0.095778 | 0.071848 | -0.048983 | 120.3387 | 120.264 | 120.3084 | 120.1894 | 0.098596 | 0.15598 | -0.001436 | 0.056344 | 0.29122 | 0.16089 | 0.25351 | 0.19013 | 0.30635 | 0.28242 | 0.16159 | 120.3616 | 120.2869 | 120.3313 | 120.2123 | 0.12148 | 0.17887 | 0.021452 | 0.079232 | 120.2401 | 120.3401 | 120.2098 | 120.3099
1420.7031 | 120.5704 | -0.19684 | 120.3506 | 0.085224 | -0.054257 | 0.038365 | -0.020438 | 0.082044 | 0.071848 | -0.058139 | 120.3616 | 120.2869 | 120.3313 | 120.2123 | 0.098596 | 0.15598 | 0.007721 | 0.056344 | 0.28206 | 0.14258 | 0.2352 | 0.1764 | 0.27888 | 0.26869 | 0.1387 | 120.3845 | 120.3098 | 120.3542 | 120.2352 | 0.12148 | 0.17887 | 0.030609 | 0.079232 | 120.263 | 120.3539 | 120.2327 | 120.3236
1422.4531 | 120.5063 | -0.21515 | 120.4147 | 0.089802 | -0.058836 | 0.042944 | -0.020438 | 0.0912 | 0.067269 | -0.048983 | 120.3891 | 120.3144 | 120.3634 | 120.2443 | 0.094017 | 0.16056 | 0.007721 | 0.056344 | 0.30495 | 0.15631 | 0.25809 | 0.19471 | 0.30635 | 0.28242 | 0.16617 | 120.412 | 120.3373 | 120.3862 | 120.2672 | 0.11691 | 0.18345 | 0.030609 | 0.079232 | 120.2951 | 120.3814 | 120.2693 | 120.3556
1424.1406 | 120.5017 | -0.21515 | 120.3278 | 0.089802 | -0.0451 | 0.038365 | -0.01586 | 0.086622 | 0.067269 | -0.053561 | 120.3158 | 120.2503 | 120.2947 | 120.1802 | 0.098596 | 0.15598 | 0.003143 | 0.056344 | 0.30495 | 0.17005 | 0.25351 | 0.19929 | 0.30177 | 0.28242 | 0.16159 | 120.3387 | 120.2732 | 120.3176 | 120.2031 | 0.12148 | 0.17887 | 0.026031 | 0.079232 | 120.2172 | 120.3127 | 120.1961 | 120.2915
1425.8906 | 120.6573 | -0.16022 | 120.3964 | 0.089802 | -0.054257 | 0.038365 | -0.025017 | 0.086622 | 0.067269 | -0.039826 | 120.3845 | 120.3144 | 120.3542 | 120.2352 | 0.10317 | 0.16514 | 0.007721 | 0.060923 | 0.25002 | 0.10596 | 0.19858 | 0.1352 | 0.24684 | 0.22749 | 0.12039 | 120.4074 | 120.3373 | 120.3771 | 120.2581 | 0.12606 | 0.18803 | 0.030609 | 0.083811 | 120.2813 | 120.3768 | 120.251 | 120.3465
1427.5781 | 120.5383 | -0.21973 | 120.4285 | 0.085224 | -0.049678 | 0.042944 | -0.020438 | 0.095778 | 0.076426 | -0.044405 | 120.4165 | 120.3464 | 120.3771 | 120.2764 | 0.10775 | 0.15598 | 0.007721 | 0.070079 | 0.30495 | 0.17005 | 0.26267 | 0.19929 | 0.31551 | 0.29615 | 0.17532 | 120.4394 | 120.3693 | 120.4 | 120.2993 | 0.13064 | 0.17887 | 0.030609 | 0.092967 | 120.3088 | 120.4088 | 120.2693 | 120.3694
1429.2812 | 120.4376 | -0.23346 | 120.4193 | 0.089802 | -0.058836 | 0.033786 | -0.029595 | 0.086622 | 0.067269 | -0.039826 | 120.0274 | 119.9618 | 119.9925 | 119.8826 | 0.37329 | 0.42609 | 0.27785 | 0.34019 | 0.32326 | 0.17462 | 0.26725 | 0.20386 | 0.32008 | 0.30073 | 0.19363 | 120.0503 | 119.9847 | 120.0154 | 119.9055 | 0.39617 | 0.44898 | 0.30073 | 0.36308 | 119.6541 | 119.7495 | 119.6192 | 119.7147
1431.0312 | 120.7077 | -0.17395 | 120.4605 | 0.085224 | -0.058836 | 0.038365 | -0.020438 | 0.086622 | 0.062691 | -0.053561 | 120.4623 | 120.3968 | 120.432 | 120.3176 | 0.10317 | 0.15141 | 0.003143 | 0.060923 | 0.25917 | 0.11511 | 0.21232 | 0.15351 | 0.26057 | 0.23664 | 0.12039 | 120.4852 | 120.4197 | 120.4549 | 120.3405 | 0.12606 | 0.17429 | 0.026031 | 0.083811 | 120.3592 | 120.4592 | 120.3289 | 120.4289
1432.7188 | 120.5063 | -0.16022 | 120.282 | 0.06691 | -0.058836 | 0.042944 | -0.020438 | 0.086622 | 0.062691 | -0.048983 | 119.9587 | 119.916 | 119.9193 | 119.8185 | 0.34124 | 0.38489 | 0.29616 | 0.34935 | 0.22713 | 0.10138 | 0.20316 | 0.13978 | 0.24684 | 0.22291 | 0.11123 | 119.9816 | 119.9389 | 119.9421 | 119.8414 | 0.36413 | 0.40777 | 0.31905 | 0.37224 | 119.6175 | 119.6625 | 119.578 | 119.6231
1434.4688 | 120.6116 | -0.19226 | 120.5292 | 0.071489 | -0.054257 | 0.038365 | -0.025017 | 0.0912 | 0.071848 | -0.048983 | 120.4806 | 120.406 | 120.4458 | 120.3313 | 0.084861 | 0.13767 | 0.003143 | 0.04261 | 0.26375 | 0.138 | 0.23063 | 0.16724 | 0.28346 | 0.26411 | 0.14328 | 120.5035 | 120.4288 | 120.4687 | 120.3542 | 0.10775 | 0.16056 | 0.026031 | 0.065498 | 120.3958 | 120.4775 | 120.3609 | 120.4426
1436.2188 | 120.7352 | -0.15106 | 120.5292 | 0.06691 | -0.067994 | 0.038365 | -0.01586 | 0.095778 | 0.071848 | -0.044405 | 120.5173 | 120.438 | 120.487 | 120.3725 | 0.089439 | 0.14225 | -0.006014 | 0.051766 | 0.21797 | 0.083068 | 0.18943 | 0.1352 | 0.24684 | 0.22291 | 0.10666 | 120.5402 | 120.4609 | 120.5099 | 120.3954 | 0.11233 | 0.16514 | 0.016874 | 0.074654 | 120.4278 | 120.5233 | 120.3975 | 120.493
1437.9062 | 120.6711 | -0.19226 | 120.5795 | 0.071489 | -0.058836 | 0.033786 | -0.01586 | 0.0912 | 0.067269 | -0.048983 | 120.5447 | 120.4655 | 120.5099 | 120.3863 | 0.084861 | 0.13767 | -0.010593 | 0.047188 | 0.26375 | 0.13342 | 0.22605 | 0.1764 | 0.28346 | 0.25953 | 0.14328 | 120.5676 | 120.4884 | 120.5327 | 120.4092 | 0.10775 | 0.16056 | 0.012295 | 0.070076 | 120.4599 | 120.5553 | 120.425 | 120.5205
1439.6562 | 120.7855 | -0.14191 | 120.5521 | 0.057754 | -0.058836 | 0.042944 | -0.025017 | 0.0912 | 0.067269 | -0.048983 | 120.5585 | 120.493 | 120.5328 | 120.4183 | 0.075705 | 0.13309 | -0.006014 | 0.04261 | 0.19966 | 0.083071 | 0.18485 | 0.11689 | 0.23311 | 0.20918 | 0.092924 | 120.5814 | 120.5158 | 120.5556 | 120.4412 | 0.098593 | 0.15598 | 0.016874 | 0.065498 | 120.4828 | 120.5645 | 120.457 | 120.5388
1441.3438 | 120.7901 | -0.16022 | 120.5978 | 0.076067 | -0.054257 | 0.033786 | -0.011281 | 0.086622 | 0.067269 | -0.048983 | 120.586 | 120.5158 | 120.5602 | 120.4412 | 0.089439 | 0.14225 | -0.006014 | 0.04261 | 0.23628 | 0.10596 | 0.194 | 0.14894 | 0.24684 | 0.22749 | 0.11123 | 120.6088 | 120.5387 | 120.5831 | 120.4641 | 0.11233 | 0.16514 | 0.016874 | 0.065498 | 120.4965 | 120.592 | 120.4708 | 120.5662
1443.1094 | 120.7993 | -0.17853 | 120.6116 | 0.06691 | -0.058836 | 0.038365 | -0.011281 | 0.086622 | 0.067269 | -0.044405 | 120.6043 | 120.5296 | 120.5831 | 120.4641 | 0.084861 | 0.13309 | -0.006014 | 0.04261 | 0.24544 | 0.11969 | 0.21689 | 0.16725 | 0.26515 | 0.2458 | 0.13412 | 120.6272 | 120.5525 | 120.606 | 120.487 | 0.10775 | 0.15598 | 0.016874 | 0.065498 | 120.5194 | 120.6103 | 120.4983 | 120.5891
1444.8594 | 120.7214 | -0.19226 | 120.6253 | 0.062332 | -0.058836 | 0.042944 | -0.020438 | 0.0912 | 0.067269 | -0.039826 | 120.6272 | 120.5662 | 120.6014 | 120.487 | 0.084861 | 0.13767 | -0.006014 | 0.051766 | 0.25459 | 0.13342 | 0.2352 | 0.17182 | 0.28346 | 0.25953 | 0.15243 | 120.65 | 120.5891 | 120.6243 | 120.5099 | 0.10775 | 0.16056 | 0.016874 | 0.074654 | 120.5423 | 120.6332 | 120.5166 | 120.6074
1446.5469 | 120.8862 | -0.16479 | 120.6345 | 0.062332 | -0.063415 | 0.038365 | -0.025017 | 0.0912 | 0.071848 | -0.048983 | 120.6546 | 120.5708 | 120.6197 | 120.5008 | 0.080283 | 0.14225 | -0.006014 | 0.04261 | 0.22713 | 0.10138 | 0.20316 | 0.13978 | 0.25599 | 0.23664 | 0.11581 | 120.6775 | 120.5937 | 120.6426 | 120.5236 | 0.10317 | 0.16514 | 0.016874 | 0.065498 | 120.5743 | 120.6606 | 120.5395 | 120.6258
1448.25 | 120.8817 | -0.15564 | 120.6757 | 0.062332 | -0.058836 | 0.042944 | -0.020438 | 0.0912 | 0.067269 | -0.053561 | 120.6684 | 120.5983 | 120.6335 | 120.5282 | 0.089439 | 0.14225 | -0.010593 | 0.056344 | 0.21797 | 0.096804 | 0.19858 | 0.1352 | 0.24684 | 0.22291 | 0.10208 | 120.6913 | 120.6212 | 120.6564 | 120.5511 | 0.11233 | 0.16514 | 0.012295 | 0.079232 | 120.5789 | 120.679 | 120.544 | 120.6441
1450 | 120.9274 | -0.14191 | 120.6802 | 0.06691 | -0.063415 | 0.047522 | -0.020438 | 0.095778 | 0.071848 | -0.048983 | 120.6913 | 120.612 | 120.6564 | 120.542 | 0.080283 | 0.13767 | -0.010593 | 0.047188 | 0.20882 | 0.078492 | 0.18943 | 0.12147 | 0.23769 | 0.21376 | 0.092924 | 120.7141 | 120.6349 | 120.6793 | 120.5649 | 0.10317 | 0.16056 | 0.012295 | 0.070076 | 120.611 | 120.7019 | 120.5761 | 120.667
1451.6875 | 120.8771 | -0.17853 | 120.6802 | 0.06691 | -0.058836 | 0.038365 | -0.020438 | 0.0912 | 0.067269 | -0.044405 | 120.705 | 120.6303 | 120.6793 | 120.5557 | 0.084861 | 0.14683 | -0.006014 | 0.051766 | 0.24544 | 0.11969 | 0.21689 | 0.15809 | 0.26973 | 0.2458 | 0.13412 | 120.7279 | 120.6532 | 120.7021 | 120.5786 | 0.10775 | 0.16972 | 0.016874 | 0.074654 | 120.6201 | 120.711 | 120.5944 | 120.6853
1453.4531 | 120.9549 | -0.13733 | 120.694 | 0.062332 | -0.058836 | 0.038365 | -0.01586 | 0.086622 | 0.076426 | -0.048983 | 120.7279 | 120.6532 | 120.6884 | 120.5786 | 0.084861 | 0.13767 | -0.010593 | 0.04261 | 0.19966 | 0.078493 | 0.17569 | 0.12147 | 0.22395 | 0.21376 | 0.088346 | 120.7508 | 120.6761 | 120.7113 | 120.6015 | 0.10775 | 0.16056 | 0.012295 | 0.065498 | 120.643 | 120.7385 | 120.6036 | 120.699
1455.2188 | 120.9045 | -0.17853 | 120.726 | 0.06691 | -0.054257 | 0.038365 | -0.025017 | 0.0912 | 0.062691 | -0.048983 | 120.7416 | 120.6669 | 120.7113 | 120.5969 | 0.084861 | 0.14683 | -0.006014 | 0.056344 | 0.24544 | 0.12427 | 0.21689 | 0.15351 | 0.26973 | 0.24122 | 0.12954 | 120.7645 | 120.6898 | 120.7342 | 120.6198 | 0.10775 | 0.16972 | 0.016874 | 0.079232 | 120.6568 | 120.7476 | 120.6264 | 120.7173
1456.9062 | 120.8267 | -0.19226 | 120.7764 | 0.071489 | -0.049678 | 0.038365 | -0.01586 | 0.086622 | 0.062691 | -0.044405 | 120.7599 | 120.6898 | 120.7388 | 120.6152 | 0.084861 | 0.14225 | -0.006014 | 0.047188 | 0.26375 | 0.14258 | 0.23063 | 0.1764 | 0.27888 | 0.25495 | 0.14786 | 120.7828 | 120.7127 | 120.7617 | 120.6381 | 0.10775 | 0.16514 | 0.016874 | 0.070076 | 120.6751 | 120.7659 | 120.6539 | 120.7448
1458.6562 | 120.9045 | -0.20142 | 120.8313 | 0.071489 | -0.054257 | 0.042944 | -0.01586 | 0.086622 | 0.062691 | -0.048983 | 120.7782 | 120.7127 | 120.7525 | 120.6427 | 0.084861 | 0.14225 | -0.010593 | 0.051766 | 0.27291 | 0.14716 | 0.24436 | 0.18556 | 0.28804 | 0.26411 | 0.15243 | 120.8011 | 120.7356 | 120.7754 | 120.6656 | 0.10775 | 0.16514 | 0.012295 | 0.074654 | 120.6934 | 120.7888 | 120.6676 | 120.7631
1460.4062 | 121.0236 | -0.13275 | 120.7809 | 0.06691 | -0.063415 | 0.042944 | -0.025017 | 0.0912 | 0.071848 | -0.053561 | 120.8011 | 120.731 | 120.7662 | 120.6427 | 0.080283 | 0.13309 | -0.010593 | 0.04261 | 0.19966 | 0.069336 | 0.1757 | 0.10773 | 0.22395 | 0.2046 | 0.07919 | 120.824 | 120.7539 | 120.7891 | 120.6656 | 0.10317 | 0.15598 | 0.012295 | 0.065498 | 120.7209 | 120.8117 | 120.686 | 120.7768
1462.1562 | 116.954 | -22.7234 | 94.1071 | 0.098959 | -0.058836 | 0.047522 | -0.006703 | 0.11409 | 0.09474 | -0.035248 | 84.2464 | 84.247 | 84.1995 | 84.1295 | 32.0588 | 32.0376 | 31.8138 | 31.9525 | 22.8223 | 22.6646 | 22.7709 | 22.7167 | 22.8375 | 22.8181 | 22.6881 | 84.2693 | 84.2699 | 84.2224 | 84.1524 | 32.0817 | 32.0605 | 31.8367 | 31.9754 | 52.1876 | 52.4327 | 52.1407 | 52.3857
1463.9062 | 120.6848 | -0.1831 | 120.575 | 0.089802 | -0.058836 | 0.042944 | -0.020438 | 0.082044 | 0.071848 | -0.048983 | 120.5356 | 120.4655 | 120.5053 | 120.3954 | 0.094017 | 0.14683 | -0.006014 | 0.051766 | 0.27291 | 0.12427 | 0.22605 | 0.16267 | 0.26515 | 0.25495 | 0.13412 | 120.5585 | 120.4884 | 120.5282 | 120.4183 | 0.11691 | 0.16972 | 0.016874 | 0.074654 | 120.4416 | 120.5416 | 120.4113 | 120.5113
1465.5938 | 120.8221 | -0.16937 | 120.6528 | 0.085224 | -0.058836 | 0.038365 | -0.01586 | 0.077466 | 0.067269 | -0.044405 | 120.6272 | 120.5479 | 120.5923 | 120.4641 | 0.10317 | 0.14683 | 0.007721 | 0.051766 | 0.2546 | 0.11054 | 0.20774 | 0.15351 | 0.24684 | 0.23664 | 0.12497 | 120.65 | 120.5708 | 120.6152 | 120.487 | 0.12606 | 0.16972 | 0.030609 | 0.074654 | 120.524 | 120.6194 | 120.4891 | 120.5845
1467.3594 | 120.575 | -0.1831 | 120.4971 | 0.062332 | -0.058836 | 0.033786 | -0.01586 | 0.0912 | 0.071848 | -0.053561 | 120.1693 | 120.1175 | 120.139 | 120.02 | 0.40991 | 0.36657 | 0.287 | 0.32646 | 0.24544 | 0.12427 | 0.21689 | 0.16724 | 0.27431 | 0.25495 | 0.12954 | 120.1922 | 120.1404 | 120.1619 | 120.0428 | 0.4328 | 0.38946 | 0.30989 | 0.34935 | 119.7594 | 119.8823 | 119.7291 | 119.852
1469.1094 | 120.7031 | -0.19684 | 120.639 | 0.071489 | -0.054257 | 0.038365 | -0.020438 | 0.086622 | 0.067269 | -0.044405 | 120.5997 | 120.5296 | 120.5648 | 120.4595 | 0.084861 | 0.13767 | -0.001436 | 0.047188 | 0.26833 | 0.14258 | 0.2352 | 0.1764 | 0.28346 | 0.26411 | 0.15243 | 120.6226 | 120.5525 | 120.5877 | 120.4824 | 0.10775 | 0.16056 | 0.021452 | 0.070076 | 120.5148 | 120.6011 | 120.4799 | 120.5662
1470.8594 | 120.7718 | -0.21515 | 120.6757 | 0.06691 | -0.058836 | 0.042944 | -0.025017 | 0.086622 | 0.076426 | -0.044405 | 120.6592 | 120.5799 | 120.6243 | 120.5099 | 0.084861 | 0.14225 | -0.001436 | 0.051766 | 0.28206 | 0.15631 | 0.25809 | 0.19013 | 0.30177 | 0.29158 | 0.17074 | 120.6821 | 120.6028 | 120.6472 | 120.5328 | 0.10775 | 0.16514 | 0.021452 | 0.074654 | 120.5743 | 120.6606 | 120.5395 | 120.6258
1472.5625 | 120.8359 | -0.21515 | 120.726 | 0.071489 | -0.063415 | 0.047522 | -0.01586 | 0.0912 | 0.076426 | -0.044405 | 120.6958 | 120.6166 | 120.6564 | 120.5374 | 0.094017 | 0.14225 | -0.006014 | 0.051766 | 0.28664 | 0.15173 | 0.26267 | 0.19929 | 0.30635 | 0.29158 | 0.17074 | 120.7187 | 120.6395 | 120.6793 | 120.5603 | 0.11691 | 0.16514 | 0.016874 | 0.074654 | 120.6018 | 120.7018 | 120.5623 | 120.6624
1474.3281 | 120.8908 | -0.15564 | 120.5978 | 0.06691 | -0.049678 | 0.047522 | -0.020438 | 0.082044 | 0.071848 | -0.044405 | 120.6134 | 120.5433 | 120.5831 | 120.4687 | 0.10775 | 0.14683 | 0.003143 | 0.056344 | 0.22255 | 0.10596 | 0.20316 | 0.1352 | 0.23768 | 0.22749 | 0.11124 | 120.6363 | 120.5662 | 120.606 | 120.4916 | 0.13064 | 0.16972 | 0.026031 | 0.079232 | 120.5057 | 120.6103 | 120.4754 | 120.58
1476.0781 | 120.8084 | -0.21057 | 120.7535 | 0.06691 | -0.058836 | 0.033786 | -0.01586 | 0.0912 | 0.071848 | -0.044405 | 120.7187 | 120.6441 | 120.6793 | 120.5557 | 0.084861 | 0.13767 | -0.010593 | 0.047188 | 0.27748 | 0.15174 | 0.24436 | 0.19471 | 0.30177 | 0.28242 | 0.16617 | 120.7416 | 120.6669 | 120.7021 | 120.5786 | 0.10775 | 0.16056 | 0.012295 | 0.070076 | 120.6339 | 120.7293 | 120.5944 | 120.6898
1477.8281 | 120.9732 | -0.16479 | 120.7169 | 0.062332 | -0.063415 | 0.033786 | -0.025017 | 0.086622 | 0.067269 | -0.044405 | 120.7462 | 120.6715 | 120.7067 | 120.5923 | 0.084861 | 0.14225 | -0.006014 | 0.051766 | 0.22713 | 0.10138 | 0.19858 | 0.13978 | 0.25142 | 0.23206 | 0.12039 | 120.7691 | 120.6944 | 120.7296 | 120.6152 | 0.10775 | 0.16514 | 0.016874 | 0.074654 | 120.6613 | 120.7522 | 120.6219 | 120.7127
1479.5156 | 120.9595 | -0.17395 | 120.7809 | 0.071489 | -0.067994 | 0.042944 | -0.025017 | 0.095778 | 0.067269 | -0.048983 | 120.7645 | 120.6944 | 120.7388 | 120.6244 | 0.089439 | 0.13767 | -0.010593 | 0.051766 | 0.24544 | 0.10596 | 0.21689 | 0.14893 | 0.26973 | 0.24122 | 0.12497 | 120.7874 | 120.7173 | 120.7617 | 120.6473 | 0.11233 | 0.16056 | 0.012295 | 0.074654 | 120.6751 | 120.7751 | 120.6493 | 120.7494
1481.2656 | 120.9091 | -0.20599 | 120.8084 | 0.062332 | -0.054257 | 0.042944 | -0.020438 | 0.0912 | 0.071848 | -0.039826 | 120.792 | 120.7219 | 120.7525 | 120.6473 | 0.089439 | 0.12851 | -0.001436 | 0.051766 | 0.26833 | 0.15174 | 0.24894 | 0.18556 | 0.29719 | 0.27784 | 0.16617 | 120.8149 | 120.7448 | 120.7754 | 120.6702 | 0.11233 | 0.1514 | 0.021452 | 0.074654 | 120.7025 | 120.7934 | 120.6631 | 120.7539
1483.0312 | 120.8633 | -0.19226 | 120.7397 | 0.094381 | -0.054257 | 0.038365 | -0.01586 | 0.11867 | 0.062691 | -0.044405 | 120.7966 | 120.7356 | 120.7617 | 120.6519 | 0.181 | 0.12851 | -0.015171 | 0.097548 | 0.28664 | 0.138 | 0.23063 | 0.1764 | 0.31093 | 0.25495 | 0.14786 | 120.8195 | 120.7585 | 120.7846 | 120.6748 | 0.20389 | 0.1514 | 0.007717 | 0.12044 | 120.6156 | 120.8117 | 120.5807 | 120.7768
1484.7188 | 121.0144 | -0.15106 | 120.7535 | 0.094381 | -0.054257 | 0.033786 | -0.025017 | 0.10036 | 0.071848 | -0.048983 | 120.8515 | 120.7265 | 120.7617 | 120.6519 | 0.075705 | 0.13309 | -0.010593 | 0.038032 | 0.24544 | 0.096805 | 0.18485 | 0.12604 | 0.25142 | 0.22291 | 0.10208 | 120.8744 | 120.7494 | 120.7846 | 120.6748 | 0.098593 | 0.15598 | 0.012295 | 0.06092 | 120.7758 | 120.8621 | 120.686 | 120.7723
1486.4688 | 121.0419 | -0.14191 | 120.7809 | 0.089802 | -0.058836 | 0.033786 | -0.020438 | 0.0912 | 0.071848 | -0.039826 | 120.8836 | 120.7494 | 120.7891 | 120.6748 | 0.080283 | 0.12394 | -0.010593 | 0.047188 | 0.23171 | 0.083071 | 0.17569 | 0.12147 | 0.23311 | 0.21376 | 0.10208 | 120.9064 | 120.7723 | 120.812 | 120.6976 | 0.10317 | 0.14683 | 0.012295 | 0.070076 | 120.8033 | 120.8941 | 120.7089 | 120.7997
1488.2188 | 120.932 | -0.18768 | 120.8588 | 0.085224 | -0.063415 | 0.042944 | -0.01586 | 0.0912 | 0.071848 | -0.039826 | 120.9064 | 120.7723 | 120.812 | 120.6885 | 0.080283 | 0.12851 | -0.006014 | 0.047188 | 0.27291 | 0.12427 | 0.23063 | 0.17182 | 0.27888 | 0.25953 | 0.14786 | 120.9293 | 120.7951 | 120.8349 | 120.7114 | 0.10317 | 0.1514 | 0.016874 | 0.070076 | 120.8262 | 120.9125 | 120.7317 | 120.818
1489.9688 | 120.9961 | -0.1831 | 120.845 | 0.080646 | -0.058836 | 0.038365 | -0.01586 | 0.0912 | 0.076426 | -0.044405 | 120.9293 | 120.7906 | 120.8303 | 120.716 | 0.080283 | 0.13309 | -0.015171 | 0.04261 | 0.26375 | 0.12427 | 0.22147 | 0.16724 | 0.27431 | 0.25953 | 0.1387 | 120.9522 | 120.8135 | 120.8532 | 120.7389 | 0.10317 | 0.15598 | 0.007717 | 0.065498 | 120.8491 | 120.9445 | 120.7501 | 120.8455
1491.6562 | 120.9686 | -0.20599 | 120.8908 | 0.080646 | -0.054257 | 0.038365 | -0.01586 | 0.086622 | 0.071848 | -0.039826 | 120.9477 | 120.8135 | 120.8532 | 120.7343 | 0.080283 | 0.12851 | -0.006014 | 0.04261 | 0.28664 | 0.15174 | 0.24436 | 0.19013 | 0.29262 | 0.27784 | 0.16617 | 120.9705 | 120.8364 | 120.8761 | 120.7572 | 0.10317 | 0.1514 | 0.016874 | 0.065498 | 120.8674 | 120.9537 | 120.7729 | 120.8592
1493.4062 | 121.0968 | -0.14648 | 120.8771 | 0.089802 | -0.063415 | 0.038365 | -0.020438 | 0.095778 | 0.062691 | -0.044405 | 120.9614 | 120.8272 | 120.8715 | 120.7526 | 0.075705 | 0.14225 | -0.010593 | 0.04261 | 0.23629 | 0.083069 | 0.18485 | 0.12605 | 0.24226 | 0.20917 | 0.10208 | 120.9843 | 120.8501 | 120.8944 | 120.7755 | 0.098593 | 0.16514 | 0.012295 | 0.065498 | 120.8857 | 120.972 | 120.7958 | 120.8821
1495.1719 | 121.0648 | -0.16937 | 120.9457 | 0.085224 | -0.058836 | 0.038365 | -0.020438 | 0.0912 | 0.071848 | -0.048983 | 120.9751 | 120.8455 | 120.8944 | 120.7663 | 0.075705 | 0.13309 | -0.010593 | 0.047188 | 0.2546 | 0.11054 | 0.20774 | 0.14893 | 0.26057 | 0.24122 | 0.12039 | 120.998 | 120.8684 | 120.9173 | 120.7892 | 0.098593 | 0.15598 | 0.012295 | 0.070076 | 120.8994 | 120.9857 | 120.8187 | 120.905
1496.9375 | 121.0602 | -0.17395 | 120.9549 | 0.085224 | -0.058836 | 0.042944 | -0.01586 | 0.0912 | 0.067269 | -0.039826 | 120.998 | 120.8638 | 120.899 | 120.7892 | 0.084861 | 0.13309 | -0.015171 | 0.047188 | 0.25917 | 0.11511 | 0.21689 | 0.15809 | 0.26515 | 0.24122 | 0.13412 | 121.0209 | 120.8867 | 120.9219 | 120.8121 | 0.10775 | 0.15598 | 0.007717 | 0.070076 | 120.9132 | 121.0132 | 120.8142 | 120.9142
1498.625 | 121.0556 | -0.21057 | 120.9824 | 0.085224 | -0.058836 | 0.047522 | -0.025017 | 0.086622 | 0.067269 | -0.039826 | 121.0072 | 120.8776 | 120.9173 | 120.803 | 0.080283 | 0.13309 | -0.010593 | 0.047188 | 0.2958 | 0.15174 | 0.25809 | 0.18555 | 0.29719 | 0.27784 | 0.17075 | 121.0301 | 120.9005 | 120.9402 | 120.8259 | 0.10317 | 0.15598 | 0.012295 | 0.070076 | 120.9269 | 121.0178 | 120.837 | 120.9279
1500.375 | 121.1655 | -0.14648 | 120.9229 | 0.094381 | -0.040521 | 0.052101 | -0.025017 | 0.095778 | 0.071848 | -0.039826 | 121.0255 | 120.8822 | 120.9265 | 120.8076 | 0.066548 | 0.12394 | -0.019749 | 0.038032 | 0.24086 | 0.10596 | 0.19859 | 0.12147 | 0.24226 | 0.21833 | 0.10666 | 121.0484 | 120.905 | 120.9494 | 120.8304 | 0.089436 | 0.14683 | 0.003139 | 0.06092 | 120.9589 | 121.0452 | 120.8599 | 120.9462
1502.1406 | 121.0876 | -0.18768 | 120.9595 | 0.085224 | -0.058836 | 0.038365 | -0.020438 | 0.10036 | 0.076426 | -0.039826 | 120.9889 | 120.8501 | 120.8853 | 120.7709 | 0.080283 | 0.13309 | -0.001436 | 0.04261 | 0.27291 | 0.12885 | 0.22605 | 0.16724 | 0.28804 | 0.26411 | 0.14786 | 121.0117 | 120.873 | 120.9082 | 120.7938 | 0.10317 | 0.15598 | 0.021452 | 0.065498 | 120.9086 | 120.9903 | 120.805 | 120.8867
1503.9062 | 121.0464 | -0.18768 | 120.9137 | 0.085224 | -0.054257 | 0.038365 | -0.01586 | 0.086622 | 0.067269 | -0.044405 | 120.9477 | 120.8593 | 120.9036 | 120.7801 | 0.075705 | 0.12851 | -0.019749 | 0.04261 | 0.27291 | 0.13343 | 0.22605 | 0.17182 | 0.27431 | 0.25495 | 0.14328 | 120.9705 | 120.8821 | 120.9265 | 120.803 | 0.098593 | 0.1514 | 0.003139 | 0.065498 | 120.8719 | 120.9674 | 120.8279 | 120.9233
1505.6094 | 120.9961 | -0.14191 | 120.813 | 0.06691 | -0.054257 | 0.052101 | -0.01586 | 0.0912 | 0.071848 | -0.039826 | 120.8103 | 120.7265 | 120.7754 | 120.6473 | 0.075705 | 0.087313 | -0.038063 | 0.015141 | 0.20882 | 0.08765 | 0.19401 | 0.12605 | 0.23311 | 0.21376 | 0.10208 | 120.8332 | 120.7494 | 120.7983 | 120.6702 | 0.098593 | 0.1102 | -0.015175 | 0.038029 | 120.7346 | 120.8484 | 120.6997 | 120.8135
1507.375 | 121.0098 | -0.19684 | 120.8771 | 0.071489 | -0.063415 | 0.042944 | -0.025017 | 0.0912 | 0.071848 | -0.044405 | 120.879 | 120.7997 | 120.8349 | 120.716 | 0.080283 | 0.11936 | -0.010593 | 0.038032 | 0.26833 | 0.13342 | 0.23978 | 0.17182 | 0.28804 | 0.26869 | 0.15243 | 120.9019 | 120.8226 | 120.8578 | 120.7389 | 0.10317 | 0.14225 | 0.012295 | 0.06092 | 120.7987 | 120.8896 | 120.7546 | 120.8455
1509.0781 | 121.1014 | -0.12817 | 120.8633 | 0.06691 | -0.054257 | 0.038365 | -0.01586 | 0.10036 | 0.067269 | -0.039826 | 120.8973 | 120.818 | 120.867 | 120.748 | 0.075705 | 0.12851 | -0.019749 | 0.04261 | 0.19508 | 0.073917 | 0.16654 | 0.11231 | 0.22853 | 0.19544 | 0.088348 | 120.9202 | 120.8409 | 120.8899 | 120.7709 | 0.098593 | 0.1514 | 0.003139 | 0.065498 | 120.8216 | 120.917 | 120.7913 | 120.8867
1510.8438 | 121.106 | -0.14191 | 120.9229 | 0.062332 | -0.058836 | 0.038365 | -0.025017 | 0.086622 | 0.062691 | -0.058139 | 120.8973 | 120.8272 | 120.8761 | 120.7618 | 0.071126 | 0.12851 | -0.010593 | 0.04261 | 0.20424 | 0.083071 | 0.18027 | 0.11689 | 0.22853 | 0.2046 | 0.083768 | 120.9202 | 120.8501 | 120.899 | 120.7846 | 0.094014 | 0.1514 | 0.012295 | 0.065498 | 120.8262 | 120.9079 | 120.805 | 120.8867
1512.5938 | 121.0556 | -0.18768 | 120.9366 | 0.071489 | -0.054257 | 0.038365 | -0.020438 | 0.0912 | 0.062691 | -0.039826 | 120.9339 | 120.8501 | 120.8944 | 120.7801 | 0.075705 | 0.12851 | -0.006014 | 0.04261 | 0.25917 | 0.13343 | 0.22605 | 0.16724 | 0.27888 | 0.25037 | 0.14786 | 120.9568 | 120.873 | 120.9173 | 120.803 | 0.098593 | 0.1514 | 0.016874 | 0.065498 | 120.8582 | 120.9399 | 120.8187 | 120.9004
1514.3438 | 121.1288 | -0.14191 | 120.9229 | 0.06691 | -0.054257 | 0.038365 | -0.020438 | 0.0912 | 0.071848 | -0.044405 | 120.9339 | 120.8593 | 120.9036 | 120.7847 | 0.075705 | 0.11936 | -0.010593 | 0.038032 | 0.20882 | 0.08765 | 0.18027 | 0.12147 | 0.23311 | 0.21376 | 0.097502 | 120.9568 | 120.8821 | 120.9265 | 120.8075 | 0.098593 | 0.14225 | 0.012295 | 0.06092 | 120.8582 | 120.9445 | 120.8279 | 120.9142
1516.0938 | 121.1609 | -0.13733 | 120.9412 | 0.062332 | -0.058836 | 0.042944 | -0.025017 | 0.086622 | 0.071848 | -0.044405 | 120.9522 | 120.873 | 120.9127 | 120.7892 | 0.071126 | 0.12394 | -0.010593 | 0.033454 | 0.19966 | 0.078493 | 0.18027 | 0.11231 | 0.22395 | 0.20918 | 0.092924 | 120.9751 | 120.8959 | 120.9356 | 120.8121 | 0.094014 | 0.14683 | 0.012295 | 0.056342 | 120.8811 | 120.9628 | 120.8416 | 120.9233
1517.8594 | 121.1426 | -0.14648 | 120.9412 | 0.06691 | -0.058836 | 0.038365 | -0.01586 | 0.095778 | 0.071848 | -0.053561 | 120.966 | 120.8959 | 120.9311 | 120.803 | 0.071126 | 0.12394 | -0.010593 | 0.04261 | 0.21339 | 0.087648 | 0.18485 | 0.13062 | 0.24226 | 0.21833 | 0.092923 | 120.9889 | 120.9188 | 120.9539 | 120.8259 | 0.094014 | 0.14683 | 0.012295 | 0.065498 | 120.8948 | 120.9766 | 120.8599 | 120.9417
1519.5938 | 121.1151 | -0.17853 | 121.0236 | 0.06691 | -0.049678 | 0.042944 | -0.011281 | 0.0912 | 0.071848 | -0.044405 | 120.9797 | 120.9005 | 120.9402 | 120.8213 | 0.071126 | 0.12851 | -0.019749 | 0.047188 | 0.24544 | 0.12885 | 0.22147 | 0.16725 | 0.26973 | 0.25038 | 0.13412 | 121.0026 | 120.9234 | 120.9631 | 120.8442 | 0.094014 | 0.1514 | 0.003139 | 0.070076 | 120.9086 | 120.9995 | 120.8691 | 120.96
1521.3594 | 121.0693 | -0.19684 | 121.0098 | 0.071489 | -0.054257 | 0.042944 | -0.01586 | 0.0912 | 0.071848 | -0.044405 | 120.9843 | 120.9096 | 120.9448 | 120.8304 | 0.071126 | 0.11936 | -0.015171 | 0.038032 | 0.26833 | 0.14258 | 0.23978 | 0.18098 | 0.28804 | 0.26869 | 0.15243 | 121.0072 | 120.9325 | 120.9677 | 120.8533 | 0.094014 | 0.14225 | 0.007717 | 0.06092 | 120.9132 | 120.9995 | 120.8737 | 120.96
1523.0625 | 121.1288 | -0.19684 | 121.019 | 0.071489 | -0.049678 | 0.038365 | -0.011281 | 0.086622 | 0.071848 | -0.044405 | 120.9889 | 120.9279 | 120.9631 | 120.8488 | 0.075705 | 0.12394 | -0.010593 | 0.04261 | 0.26833 | 0.14716 | 0.2352 | 0.18556 | 0.28346 | 0.26869 | 0.15243 | 121.0117 | 120.9508 | 120.986 | 120.8716 | 0.098593 | 0.14683 | 0.012295 | 0.065498 | 120.9132 | 120.9995 | 120.8874 | 120.9737
1524.7969 | 121.138 | -0.16022 | 121.019 | 0.06691 | -0.054257 | 0.042944 | -0.01586 | 0.0912 | 0.081005 | -0.044405 | 121.0026 | 120.9325 | 120.9723 | 120.8533 | 0.071126 | 0.12851 | -0.024328 | 0.047188 | 0.22713 | 0.10596 | 0.20316 | 0.14436 | 0.25142 | 0.24122 | 0.11581 | 121.0255 | 120.9554 | 120.9952 | 120.8762 | 0.094014 | 0.1514 | -0.00144 | 0.070076 | 120.9315 | 121.0269 | 120.9011 | 120.9966
1526.5469 | 121.1517 | -0.18768 | 121.019 | 0.062332 | -0.054257 | 0.047522 | -0.01586 | 0.10036 | 0.076426 | -0.039826 | 121.0163 | 120.9417 | 120.9906 | 120.8671 | 0.080283 | 0.11936 | -0.019749 | 0.033454 | 0.25001 | 0.13343 | 0.2352 | 0.17182 | 0.28804 | 0.26411 | 0.14786 | 121.0392 | 120.9646 | 121.0135 | 120.89 | 0.10317 | 0.14225 | 0.003139 | 0.056342 | 120.936 | 121.0361 | 120.9103 | 121.0103
1528.2344 | 121.1975 | -0.13733 | 121.0098 | 0.06691 | -0.058836 | 0.042944 | -0.01586 | 0.095778 | 0.071848 | -0.039826 | 121.0163 | 120.9508 | 120.986 | 120.8671 | 0.071126 | 0.11936 | -0.010593 | 0.038032 | 0.20424 | 0.078493 | 0.18027 | 0.12147 | 0.23311 | 0.20918 | 0.097503 | 121.0392 | 120.9737 | 121.0089 | 120.89 | 0.094014 | 0.14225 | 0.012295 | 0.06092 | 120.9452 | 121.0269 | 120.9149 | 120.9966
1529.9844 | 121.2296 | -0.13733 | 121.0098 | 0.062332 | -0.054257 | 0.042944 | -0.01586 | 0.095778 | 0.076426 | -0.039826 | 121.0301 | 120.96 | 120.9906 | 120.8762 | 0.071126 | 0.12851 | -0.015171 | 0.04261 | 0.19966 | 0.083072 | 0.18027 | 0.12147 | 0.23311 | 0.21376 | 0.097503 | 121.053 | 120.9829 | 121.0135 | 120.8991 | 0.094014 | 0.1514 | 0.007717 | 0.065498 | 120.9589 | 121.0452 | 120.9195 | 121.0057
1531.7344 | 121.2524 | -0.14648 | 121.0327 | 0.06691 | -0.049678 | 0.038365 | -0.020438 | 0.0912 | 0.067269 | -0.048983 | 121.0438 | 120.9737 | 121.0089 | 120.8946 | 0.080283 | 0.11936 | -0.015171 | 0.038032 | 0.21339 | 0.096806 | 0.18485 | 0.12605 | 0.23768 | 0.21375 | 0.097501 | 121.0667 | 120.9966 | 121.0318 | 120.9174 | 0.10317 | 0.14225 | 0.007717 | 0.06092 | 120.9635 | 121.059 | 120.9286 | 121.0241
1533.4375 | 121.2982 | -0.1236 | 121.051 | 0.06691 | -0.058836 | 0.042944 | -0.020438 | 0.0912 | 0.067269 | -0.044405 | 121.053 | 120.9691 | 121.0272 | 120.8946 | 0.06197 | 0.10562 | -0.033484 | 0.028875 | 0.19051 | 0.06476 | 0.16654 | 0.10316 | 0.2148 | 0.19087 | 0.079191 | 121.0758 | 120.992 | 121.0501 | 120.9174 | 0.084858 | 0.12851 | -0.010596 | 0.051763 | 120.991 | 121.0864 | 120.9652 | 121.0607
1535.1406 | 121.1014 | -0.14191 | 121.0831 | 0.071489 | -0.054257 | 0.038365 | -0.01586 | 0.0912 | 0.071848 | -0.044405 | 121.0759 | 120.992 | 121.0364 | 120.9083 | -0.029593 | -0.063763 | -0.23036 | -0.15425 | 0.2134 | 0.08765 | 0.18027 | 0.12605 | 0.23311 | 0.21376 | 0.097502 | 121.0987 | 121.0149 | 121.0592 | 120.9312 | -0.006705 | -0.040875 | -0.20747 | -0.13136 | 121.1054 | 121.3062 | 121.066 | 121.2667
1536.8906 | 121.3028 | -0.15106 | 121.0602 | 0.071489 | -0.049678 | 0.038365 | -0.025017 | 0.095778 | 0.067269 | -0.044405 | 121.085 | 121.0058 | 121.0409 | 120.922 | 0.06197 | 0.082735 | -0.042641 | 0.005985 | 0.22255 | 0.10138 | 0.18943 | 0.12604 | 0.24684 | 0.21833 | 0.10666 | 121.1079 | 121.0287 | 121.0638 | 120.9449 | 0.084858 | 0.10562 | -0.019753 | 0.028873 | 121.023 | 121.1276 | 120.979 | 121.0836
1538.6406 | 121.2982 | -0.14648 | 121.0831 | 0.071489 | -0.054257 | 0.047522 | -0.01586 | 0.095778 | 0.071848 | -0.035248 | 121.0804 | 121.0104 | 121.0455 | 120.9266 | 0.075705 | 0.12851 | -0.010593 | 0.04261 | 0.21797 | 0.092227 | 0.19401 | 0.13062 | 0.24226 | 0.21833 | 0.11124 | 121.1033 | 121.0332 | 121.0684 | 120.9495 | 0.098593 | 0.1514 | 0.012295 | 0.065498 | 121.0047 | 121.091 | 120.9698 | 121.0561
1540.3281 | 121.1655 | -0.12817 | 121.1014 | 0.06691 | -0.063415 | 0.038365 | -0.020438 | 0.095778 | 0.067269 | -0.048983 | 121.0942 | 121.0149 | 121.0547 | 120.9449 | 0.075705 | 0.11478 | -0.019749 | 0.028875 | 0.19508 | 0.064759 | 0.16654 | 0.10774 | 0.22395 | 0.19544 | 0.079191 | 121.1171 | 121.0378 | 121.0776 | 120.9678 | 0.098593 | 0.13767 | 0.003139 | 0.051763 | 121.0185 | 121.1139 | 120.979 | 121.0744
1542.0156 | 121.3028 | -0.16022 | 121.1014 | 0.06691 | -0.058836 | 0.038365 | -0.01586 | 0.0912 | 0.076426 | -0.044405 | 121.0942 | 121.0149 | 121.0547 | 120.9403 | 0.071126 | 0.12851 | -0.010593 | 0.04261 | 0.22713 | 0.10138 | 0.19858 | 0.14436 | 0.25142 | 0.23664 | 0.11581 | 121.1171 | 121.0378 | 121.0776 | 120.9632 | 0.094014 | 0.1514 | 0.012295 | 0.065498 | 121.023 | 121.1048 | 120.9835 | 121.0653
1543.7812 | 121.2936 | -0.14191 | 121.0693 | 0.062332 | -0.054257 | 0.042944 | -0.020438 | 0.086622 | 0.067269 | -0.03067 | 121.1033 | 121.0287 | 121.0593 | 120.9403 | 0.071126 | 0.12851 | -0.006014 | 0.047188 | 0.20424 | 0.08765 | 0.18485 | 0.12147 | 0.22853 | 0.20918 | 0.11124 | 121.1262 | 121.0516 | 121.0821 | 120.9632 | 0.094014 | 0.1514 | 0.016874 | 0.070076 | 121.0322 | 121.1093 | 120.9881 | 121.0653
1545.4688 | 121.1838 | -0.20599 | 121.1288 | 0.071489 | -0.049678 | 0.042944 | -0.020438 | 0.095778 | 0.062691 | -0.048983 | 121.1079 | 121.0287 | 121.0684 | 120.9541 | 0.071126 | 0.12394 | -0.010593 | 0.047188 | 0.27748 | 0.15632 | 0.24894 | 0.18556 | 0.30177 | 0.26869 | 0.15701 | 121.1308 | 121.0516 | 121.0913 | 120.977 | 0.094014 | 0.14683 | 0.012295 | 0.070076 | 121.0368 | 121.1185 | 120.9973 | 121.079
1547.2188 | 121.2936 | -0.16479 | 121.1197 | 0.06691 | -0.054257 | 0.042944 | -0.01586 | 0.095778 | 0.076426 | -0.044405 | 121.1171 | 121.0378 | 121.0821 | 120.9541 | 0.071126 | 0.12851 | -0.010593 | 0.04261 | 0.2317 | 0.11054 | 0.20774 | 0.14893 | 0.26057 | 0.24122 | 0.12039 | 121.1399 | 121.0607 | 121.105 | 120.977 | 0.094014 | 0.1514 | 0.012295 | 0.065498 | 121.0459 | 121.1277 | 121.011 | 121.0927
1548.9688 | 121.2296 | -0.1831 | 121.106 | 0.071489 | -0.049678 | 0.047522 | -0.01586 | 0.0912 | 0.076426 | -0.044405 | 121.1216 | 121.0516 | 121.0821 | 120.9632 | 0.071126 | 0.12394 | -0.015171 | 0.038032 | 0.25459 | 0.13343 | 0.23063 | 0.16724 | 0.27431 | 0.25953 | 0.1387 | 121.1445 | 121.0745 | 121.105 | 120.9861 | 0.094014 | 0.14683 | 0.007717 | 0.06092 | 121.0505 | 121.1368 | 121.011 | 121.0973
1550.6406 | 121.2982 | -0.16479 | 121.106 | 0.06691 | -0.058836 | 0.047522 | -0.01586 | 0.0912 | 0.071848 | -0.03067 | 121.1262 | 121.0607 | 121.0913 | 120.9724 | 0.075705 | 0.11936 | -0.015171 | 0.04261 | 0.2317 | 0.10596 | 0.21232 | 0.14893 | 0.25599 | 0.23664 | 0.13412 | 121.1491 | 121.0836 | 121.1142 | 120.9953 | 0.098593 | 0.14225 | 0.007717 | 0.065498 | 121.0505 | 121.1414 | 121.0156 | 121.1065
1552.3906 | 121.3257 | -0.16022 | 121.1243 | 0.071489 | -0.063415 | 0.047522 | -0.020438 | 0.095778 | 0.076426 | -0.044405 | 121.1354 | 121.0653 | 121.0959 | 120.9907 | 0.075705 | 0.12394 | -0.019749 | 0.04261 | 0.23171 | 0.096802 | 0.20774 | 0.13978 | 0.25599 | 0.23664 | 0.11581 | 121.1583 | 121.0882 | 121.1188 | 121.0136 | 0.098593 | 0.14683 | 0.003139 | 0.065498 | 121.0597 | 121.1551 | 121.0202 | 121.1156
1554.1562 | 121.2204 | -0.19684 | 121.1472 | 0.06691 | -0.054257 | 0.042944 | -0.01586 | 0.095778 | 0.071848 | -0.044405 | 121.1399 | 121.0653 | 121.1142 | 120.9907 | 0.075705 | 0.12394 | -0.015171 | 0.04261 | 0.26375 | 0.14258 | 0.23978 | 0.18098 | 0.29262 | 0.26869 | 0.15243 | 121.1628 | 121.0882 | 121.1371 | 121.0136 | 0.098593 | 0.14683 | 0.007717 | 0.065498 | 121.0642 | 121.1551 | 121.0385 | 121.1294
1555.9062 | 121.2479 | -0.1831 | 121.1884 | 0.062332 | -0.054257 | 0.038365 | -0.025017 | 0.095778 | 0.071848 | -0.053561 | 121.1674 | 121.0974 | 121.1325 | 121.0136 | 0.16727 | 0.11478 | 0.035191 | 0.083814 | 0.24544 | 0.12885 | 0.22147 | 0.15809 | 0.27888 | 0.25495 | 0.12954 | 121.1903 | 121.1202 | 121.1554 | 121.0365 | 0.19016 | 0.13767 | 0.058079 | 0.1067 | 121.0002 | 121.1322 | 120.9652 | 121.0973
1557.5938 | 121.3394 | -0.14648 | 121.138 | 0.06691 | -0.054257 | 0.038365 | -0.020438 | 0.095778 | 0.067269 | -0.039826 | 121.1812 | 121.1065 | 121.1371 | 121.0182 | 0.075705 | 0.1102 | -0.019749 | 0.083814 | 0.21339 | 0.092227 | 0.18485 | 0.12605 | 0.24226 | 0.21375 | 0.10666 | 121.204 | 121.1294 | 121.16 | 121.0411 | 0.098593 | 0.13309 | 0.003139 | 0.1067 | 121.1055 | 121.2009 | 121.0614 | 121.1568
1559.3594 | 121.2936 | -0.15564 | 121.1929 | 0.06691 | -0.054257 | 0.042944 | -0.011281 | 0.095778 | 0.076426 | -0.044405 | 121.1949 | 121.1157 | 121.1508 | 121.0273 | 0.06197 | 0.1102 | -0.019749 | 0.038032 | 0.22255 | 0.10138 | 0.19858 | 0.14436 | 0.25142 | 0.23207 | 0.11124 | 121.2178 | 121.1386 | 121.1737 | 121.0502 | 0.084858 | 0.13309 | 0.003139 | 0.06092 | 121.1329 | 121.2146 | 121.0888 | 121.1706
1561.0625 | 121.2845 | -0.17853 | 121.2158 | 0.06691 | -0.054257 | 0.042944 | -0.01586 | 0.095778 | 0.071848 | -0.048983 | 121.1903 | 121.1111 | 121.16 | 121.0411 | 0.066548 | 0.1102 | -0.019749 | 0.033454 | 0.24544 | 0.12427 | 0.22147 | 0.16267 | 0.27431 | 0.25038 | 0.12954 | 121.2132 | 121.134 | 121.1829 | 121.064 | 0.089436 | 0.13309 | 0.003139 | 0.056342 | 121.1238 | 121.2101 | 121.0934 | 121.1797
1562.8125 | 121.3943 | -0.10986 | 121.1517 | 0.062332 | -0.058836 | 0.038365 | -0.01586 | 0.0912 | 0.076426 | -0.053561 | 121.1995 | 121.1294 | 121.1691 | 121.0457 | 0.066548 | 0.10562 | -0.019749 | 0.033454 | 0.17219 | 0.051027 | 0.14823 | 0.094003 | 0.20106 | 0.18629 | 0.056302 | 121.2224 | 121.1523 | 121.192 | 121.0685 | 0.089436 | 0.12851 | 0.003139 | 0.056342 | 121.1329 | 121.2192 | 121.1026 | 121.1889
1564.5625 | 121.3806 | -0.15106 | 121.1838 | 0.062332 | -0.058836 | 0.042944 | -0.025017 | 0.095778 | 0.067269 | -0.053561 | 121.2086 | 121.1431 | 121.1691 | 121.0594 | 0.06197 | 0.11478 | -0.024328 | 0.038032 | 0.21339 | 0.092226 | 0.19401 | 0.12604 | 0.24684 | 0.21833 | 0.097501 | 121.2315 | 121.166 | 121.192 | 121.0823 | 0.084858 | 0.13767 | -0.00144 | 0.06092 | 121.1467 | 121.233 | 121.1072 | 121.1935
1566.3125 | 121.3669 | -0.15564 | 121.1838 | 0.071489 | -0.049678 | 0.042944 | -0.020438 | 0.0912 | 0.071848 | -0.044405 | 121.2224 | 121.1386 | 121.1783 | 121.0548 | 0.071126 | 0.1102 | -0.024328 | 0.033454 | 0.22713 | 0.10596 | 0.19858 | 0.1352 | 0.24684 | 0.22749 | 0.11124 | 121.2453 | 121.1615 | 121.2012 | 121.0777 | 0.094014 | 0.13309 | -0.00144 | 0.056342 | 121.1512 | 121.2467 | 121.1072 | 121.2026
1568 | 121.4172 | -0.13275 | 121.1929 | 0.062332 | -0.054257 | 0.033786 | -0.025017 | 0.095778 | 0.076426 | -0.048983 | 121.2224 | 121.1431 | 121.1829 | 121.064 | 0.066548 | 0.1102 | -0.024328 | 0.038032 | 0.19508 | 0.078494 | 0.16654 | 0.10773 | 0.22853 | 0.20918 | 0.083768 | 121.2453 | 121.166 | 121.2058 | 121.0869 | 0.089436 | 0.13309 | -0.00144 | 0.06092 | 121.1558 | 121.2467 | 121.1163 | 121.2072
1569.75 | 121.312 | -0.19226 | 121.2387 | 0.062332 | -0.054257 | 0.038365 | -0.029595 | 0.095778 | 0.071848 | -0.044405 | 121.2269 | 121.1569 | 121.1966 | 121.0731 | 0.071126 | 0.10562 | -0.015171 | 0.038032 | 0.25459 | 0.138 | 0.23063 | 0.16267 | 0.28804 | 0.26411 | 0.14786 | 121.2498 | 121.1798 | 121.2195 | 121.096 | 0.094014 | 0.12851 | 0.007717 | 0.06092 | 121.1558 | 121.2421 | 121.1255 | 121.2118
1571.5 | 121.4355 | -0.15106 | 121.2296 | 0.06691 | -0.054257 | 0.033786 | -0.020438 | 0.095778 | 0.067269 | -0.048983 | 121.2453 | 121.1615 | 121.2012 | 121.0823 | 0.071126 | 0.11478 | -0.019749 | 0.033454 | 0.21797 | 0.096805 | 0.18485 | 0.13062 | 0.24684 | 0.21833 | 0.10208 | 121.2681 | 121.1843 | 121.2241 | 121.1052 | 0.094014 | 0.13767 | 0.003139 | 0.056342 | 121.1741 | 121.265 | 121.1301 | 121.2209
1573.1875 | 121.3348 | -0.1831 | 121.257 | 0.071489 | -0.063415 | 0.038365 | -0.011281 | 0.10036 | 0.071848 | -0.044405 | 121.2453 | 121.1706 | 121.2103 | 121.0915 | 0.066548 | 0.11936 | -0.024328 | 0.04261 | 0.25459 | 0.11969 | 0.22147 | 0.17182 | 0.28346 | 0.25495 | 0.1387 | 121.2681 | 121.1935 | 121.2332 | 121.1143 | 0.089436 | 0.14225 | -0.00144 | 0.065498 | 121.1787 | 121.2696 | 121.1438 | 121.2347
1574.9375 | 120.9 | -0.16479 | 120.8725 | 0.080646 | -0.063415 | 0.024629 | -0.020438 | 0.10036 | 0.081005 | -0.053561 | 120.7508 | 120.7036 | 120.7342 | 120.6198 | 0.094017 | 0.12851 | -0.001436 | 0.056344 | 0.24544 | 0.10138 | 0.18942 | 0.14436 | 0.26515 | 0.2458 | 0.11123 | 120.7737 | 120.7265 | 120.7571 | 120.6427 | 0.11691 | 0.1514 | 0.021452 | 0.079232 | 120.6568 | 120.7522 | 120.6402 | 120.7356
1576.625 | 121.2067 | -0.15106 | 121.0648 | 0.085224 | -0.063415 | 0.038365 | -0.020438 | 0.086622 | 0.062691 | -0.048983 | 121.1171 | 120.9875 | 121.0272 | 120.9129 | 0.066548 | 0.11936 | -0.019749 | 0.033454 | 0.23629 | 0.087647 | 0.18943 | 0.13062 | 0.23768 | 0.21375 | 0.10208 | 121.1399 | 121.0104 | 121.0501 | 120.9358 | 0.089436 | 0.14225 | 0.003139 | 0.056342 | 121.0505 | 121.1368 | 120.9607 | 121.047
1578.3906 | 121.312 | -0.15564 | 121.106 | 0.085224 | -0.058836 | 0.033786 | -0.025017 | 0.082044 | 0.067269 | -0.048983 | 121.1262 | 121.0516 | 121.0913 | 120.9632 | 0.06197 | 0.11936 | -0.019749 | 0.033454 | 0.24086 | 0.096804 | 0.18943 | 0.13062 | 0.23768 | 0.22291 | 0.10666 | 121.1491 | 121.0745 | 121.1142 | 120.9861 | 0.084858 | 0.14225 | 0.003139 | 0.056342 | 121.0642 | 121.146 | 121.0293 | 121.1111
1580.0781 | 121.3074 | -0.13733 | 121.1334 | 0.085224 | -0.058836 | 0.038365 | -0.025017 | 0.0912 | 0.076426 | -0.039826 | 121.1674 | 121.0974 | 121.1279 | 121.009 | 0.066548 | 0.1102 | -0.024328 | 0.033454 | 0.22255 | 0.078493 | 0.17569 | 0.11231 | 0.22853 | 0.21376 | 0.097503 | 121.1903 | 121.1202 | 121.1508 | 121.0319 | 0.089436 | 0.13309 | -0.00144 | 0.056342 | 121.1009 | 121.1917 | 121.0614 | 121.1523
1581.8281 | 121.3257 | -0.14191 | 121.1929 | 0.085224 | -0.063415 | 0.038365 | -0.020438 | 0.10036 | 0.071848 | -0.044405 | 121.1995 | 121.134 | 121.16 | 121.0457 | 0.06197 | 0.1102 | -0.024328 | 0.033454 | 0.22713 | 0.078492 | 0.18027 | 0.12147 | 0.24226 | 0.21376 | 0.097502 | 121.2224 | 121.1569 | 121.1829 | 121.0685 | 0.084858 | 0.13309 | -0.00144 | 0.056342 | 121.1375 | 121.2238 | 121.098 | 121.1843
1583.5156 | 121.3531 | -0.15106 | 121.2021 | 0.085224 | -0.063415 | 0.038365 | -0.020438 | 0.086622 | 0.062691 | -0.039826 | 121.2178 | 121.1523 | 121.1783 | 121.0686 | 0.06197 | 0.11478 | -0.015171 | 0.028875 | 0.23629 | 0.087647 | 0.18943 | 0.13062 | 0.23768 | 0.21375 | 0.11124 | 121.2407 | 121.1752 | 121.2012 | 121.0914 | 0.084858 | 0.13767 | 0.007717 | 0.051763 | 121.1558 | 121.233 | 121.1163 | 121.1935
1585.2656 | 121.3028 | -0.16479 | 121.2753 | 0.080646 | -0.058836 | 0.038365 | -0.020438 | 0.095778 | 0.071848 | -0.044405 | 121.2407 | 121.1798 | 121.2149 | 121.0915 | 0.06197 | 0.1102 | -0.024328 | 0.038032 | 0.24544 | 0.10596 | 0.20316 | 0.14436 | 0.26057 | 0.23664 | 0.12039 | 121.2636 | 121.2027 | 121.2378 | 121.1143 | 0.084858 | 0.13309 | -0.00144 | 0.06092 | 121.1787 | 121.265 | 121.1529 | 121.2392
1587.0156 | 121.4401 | -0.12817 | 121.2341 | 0.089802 | -0.054257 | 0.042944 | -0.020438 | 0.0912 | 0.071848 | -0.048983 | 121.2636 | 121.1889 | 121.2241 | 121.1098 | 0.06197 | 0.1102 | -0.019749 | 0.038032 | 0.21798 | 0.073917 | 0.17112 | 0.10774 | 0.21937 | 0.20002 | 0.079191 | 121.2865 | 121.2118 | 121.247 | 121.1327 | 0.084858 | 0.13309 | 0.003139 | 0.06092 | 121.2016 | 121.2833 | 121.1621 | 121.2438
1588.7031 | 120.5063 | -46.0876 | 74.7528 | 0.085224 | -0.072572 | 0.020051 | -0.038752 | 0.077466 | 0.058113 | -0.058139 | 74.5812 | 74.5583 | 74.5622 | 74.4449 | 46.1504 | 46.1106 | 45.874 | 46.0075 | 46.1729 | 46.0151 | 46.1077 | 46.0489 | 46.1651 | 46.1458 | 46.0295 | 74.6041 | 74.5811 | 74.5851 | 74.4677 | 46.1733 | 46.1335 | 45.8969 | 46.0304 | 28.4308 | 28.7072 | 28.4118 | 28.6882
1590.4688 | 121.1975 | -45.7718 | 75.4074 | 0.080646 | -0.063415 | 0.024629 | -0.038752 | 0.0912 | 0.058113 | -0.058139 | 75.387 | 75.355 | 75.3085 | 75.2508 | 45.8849 | 45.8451 | 45.6176 | 45.7419 | 45.8524 | 45.7084 | 45.7964 | 45.733 | 45.863 | 45.8299 | 45.7137 | 75.4099 | 75.3779 | 75.3314 | 75.2736 | 45.9078 | 45.868 | 45.6405 | 45.7648 | 29.5021 | 29.7694 | 29.4236 | 29.6909
1592.1562 | 121.2433 | -45.6665 | 75.5493 | 0.085224 | -0.063415 | 0.029208 | -0.038752 | 0.082044 | 0.058113 | -0.048983 | 75.5656 | 75.4694 | 75.4825 | 75.3652 | 45.7659 | 45.7123 | 45.2697 | 45.6229 | 45.7517 | 45.6031 | 45.6957 | 45.6278 | 45.7485 | 45.7246 | 45.6175 | 75.5885 | 75.4923 | 75.5054 | 75.3881 | 45.7888 | 45.7352 | 45.2926 | 45.6458 | 29.7997 | 30.2959 | 29.7166 | 30.2128
1593.9219 | 121.3669 | -45.4559 | 75.7233 | 0.085224 | -0.067994 | 0.024629 | -0.038752 | 0.077466 | 0.058113 | -0.053561 | 75.7854 | 75.6892 | 75.7068 | 75.5805 | 45.3905 | 45.5292 | 45.0819 | 45.4352 | 45.5412 | 45.3879 | 45.4806 | 45.4172 | 45.5334 | 45.514 | 45.4024 | 75.8083 | 75.7121 | 75.7297 | 75.6033 | 45.4134 | 45.5521 | 45.1048 | 45.4581 | 30.3949 | 30.7034 | 30.3163 | 30.6249
1595.6094 | 121.3577 | -121.1014 | 0.20599 | 0.06691 | -0.086309 | 0.006315 | -0.052488 | 0.059155 | 0.039799 | -0.071874 | 0.28141 | 0.33105 | 0.25674 | 0.20501 | 121.0997 | 121.0902 | 120.8314 | 120.9247 | 121.1683 | 121.0151 | 121.1077 | 121.0489 | 121.1605 | 121.1412 | 121.0295 | 0.3043 | 0.35394 | 0.27963 | 0.2279 | 121.1226 | 121.1131 | 120.8543 | 120.9476 | -120.8183 | -120.55 | -120.843 | -120.5746
1597.3594 | 121.4539 | -121.0648 | 0.16022 | 0.085224 | -0.08173 | 0.010893 | -0.043331 | 0.063733 | 0.048956 | -0.071874 | 0.24021 | 0.28526 | 0.21096 | 0.1638 | 121.1501 | 121.1451 | 120.8772 | 120.9842 | 121.15 | 120.983 | 121.0757 | 121.0214 | 121.1285 | 121.1137 | 120.9929 | 0.26309 | 0.30815 | 0.23385 | 0.18668 | 121.173 | 121.168 | 120.9 | 121.0071 | -120.9099 | -120.637 | -120.9391 | -120.6662
1599.0625 | 121.4859 | -121.0831 | 0.17853 | 0.085224 | -0.090888 | 0.010893 | -0.043331 | 0.063733 | 0.044377 | -0.071874 | 0.22647 | 0.28526 | 0.12397 | 0.15006 | 121.1913 | 121.1726 | 120.6849 | 121.0117 | 121.1683 | 120.9922 | 121.094 | 121.0397 | 121.1468 | 121.1274 | 121.0112 | 0.24936 | 0.30815 | 0.14686 | 0.17295 | 121.2142 | 121.1955 | 120.7078 | 121.0346 | -120.9648 | -120.4584 | -121.0673 | -120.5609
1600.75 | 121.376 | -121.1334 | 0.23346 | 0.080646 | -0.086309 | 0.006315 | -0.047909 | 0.059155 | 0.044377 | -0.071874 | 0.22189 | 0.27153 | 0.11482 | 0.053901 | 121.2142 | 121.2 | 120.694 | 121.0346 | 121.2141 | 121.0471 | 121.1397 | 121.0855 | 121.1926 | 121.1778 | 121.0615 | 0.24478 | 0.29442 | 0.1377 | 0.076789 | 121.2371 | 121.2229 | 120.7169 | 121.0575 | -120.9923 | -120.4721 | -121.0994 | -120.5792
1602.5 | 121.5225 | -121.17 | 0.18768 | 0.080646 | -0.08173 | 0.006315 | -0.047909 | 0.063733 | 0.035221 | -0.071874 | 0.22189 | 0.27611 | 0.11024 | 0.053901 | 121.2325 | 121.2229 | 120.7261 | 121.0529 | 121.2507 | 121.0883 | 121.1764 | 121.1221 | 121.2338 | 121.2053 | 121.0982 | 0.24478 | 0.29899 | 0.13313 | 0.076789 | 121.2554 | 121.2458 | 120.749 | 121.0758 | -121.0106 | -120.5042 | -121.1222 | -120.6158
1604.25 | 121.4355 | -121.1746 | 0.19226 | 0.080646 | -0.086309 | 0.010893 | -0.043331 | 0.063733 | 0.053534 | -0.062717 | 0.21731 | 0.28069 | 0.11482 | 0.053901 | 121.0265 | 121.2275 | 120.7398 | 121.0758 | 121.2553 | 121.0883 | 121.1855 | 121.1313 | 121.2384 | 121.2282 | 121.1119 | 0.2402 | 0.30357 | 0.1377 | 0.076789 | 121.0494 | 121.2504 | 120.7627 | 121.0987 | -120.8091 | -120.5225 | -120.9116 | -120.625
1606 | 121.4493 | -121.1838 | 0.20599 | 0.076067 | -0.077151 | 0.020051 | -0.047909 | 0.06831 | 0.044377 | -0.071874 | 0.20816 | 0.27153 | 0.11024 | 0.049322 | 121.0448 | 121.2504 | 120.7581 | 121.0941 | 121.2598 | 121.1066 | 121.2038 | 121.1359 | 121.2521 | 121.2282 | 121.1119 | 0.23105 | 0.29442 | 0.13313 | 0.07221 | 121.0677 | 121.2733 | 120.781 | 121.117 | -120.8366 | -120.55 | -120.9345 | -120.6479
1607.6719 | 121.5317 | -121.1792 | 0.16937 | 0.080646 | -0.086309 | 0.006315 | -0.052488 | 0.063733 | 0.039799 | -0.076452 | 0.21274 | 0.27153 | 0.11024 | 0.053901 | 121.0722 | 121.2596 | 120.7581 | 121.1032 | 121.2598 | 121.0929 | 121.1855 | 121.1267 | 121.2429 | 121.219 | 121.1027 | 0.23562 | 0.29442 | 0.13313 | 0.076789 | 121.0951 | 121.2824 | 120.781 | 121.1261 | -120.8595 | -120.5454 | -120.962 | -120.6479
1609.4375 | 121.4813 | -121.2204 | 0.21057 | 0.080646 | -0.077151 | 0.010893 | -0.043331 | 0.059155 | 0.053534 | -0.071874 | 0.21274 | 0.27153 | 0.10566 | 0.05848 | 121.0768 | 121.2733 | 120.7856 | 121.117 | 121.301 | 121.1432 | 121.2313 | 121.1771 | 121.2796 | 121.2739 | 121.1485 | 0.23562 | 0.29442 | 0.12855 | 0.081368 | 121.0997 | 121.2962 | 120.8085 | 121.1399 | -120.8641 | -120.5729 | -120.9712 | -120.6799
1611.1875 | 121.5591 | -121.2341 | 0.16022 | 0.071489 | -0.086309 | 0.015472 | -0.047909 | 0.063733 | 0.044377 | -0.076452 | 0.20816 | 0.26695 | 0.096503 | 0.049322 | 121.0951 | 121.287 | 120.7902 | 121.1307 | 121.3056 | 121.1478 | 121.2496 | 121.1862 | 121.2979 | 121.2785 | 121.1577 | 0.23105 | 0.28984 | 0.11939 | 0.07221 | 121.118 | 121.3099 | 120.8131 | 121.1536 | -120.887 | -120.582 | -120.9986 | -120.6937
1612.9375 | 121.4584 | -121.2662 | 0.20599 | 0.080646 | -0.077151 | 0.010893 | -0.047909 | 0.06831 | 0.044377 | -0.062717 | 0.20358 | 0.26237 | 0.10108 | 0.053901 | 121.1226 | 121.3053 | 120.7993 | 121.149 | 121.3468 | 121.189 | 121.2771 | 121.2183 | 121.3345 | 121.3106 | 121.2035 | 0.22647 | 0.28526 | 0.12397 | 0.076789 | 121.1455 | 121.3282 | 120.8222 | 121.1719 | -120.919 | -120.5958 | -121.0215 | -120.6982
1614.625 | 121.4584 | -121.2433 | 0.21057 | 0.085224 | -0.086309 | 0.015472 | -0.047909 | 0.06831 | 0.048956 | -0.071874 | 0.20358 | 0.27153 | 0.10108 | 0.053901 | 121.1226 | 121.3191 | 120.8176 | 121.1444 | 121.3285 | 121.157 | 121.2588 | 121.1954 | 121.3116 | 121.2922 | 121.1714 | 0.22647 | 0.29442 | 0.12397 | 0.076789 | 121.1455 | 121.342 | 120.8405 | 121.1673 | -120.919 | -120.6141 | -121.0215 | -120.7166
1616.3594 | 121.5958 | -121.2341 | 0.16022 | 0.080646 | -0.08173 | 0.006315 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 0.199 | 0.26695 | 0.10108 | 0.053901 | 121.1226 | 121.3328 | 120.8222 | 121.1628 | 121.3148 | 121.1524 | 121.2404 | 121.1862 | 121.2979 | 121.2831 | 121.1623 | 0.22189 | 0.28984 | 0.12397 | 0.076789 | 121.1455 | 121.3557 | 120.8451 | 121.1856 | -120.9236 | -120.6232 | -121.0215 | -120.7211
1618.1094 | 121.5637 | -121.2524 | 0.17853 | 0.080646 | -0.086309 | 0.010893 | -0.043331 | 0.063733 | 0.044377 | -0.076452 | 0.20358 | 0.26237 | 0.10566 | 0.044743 | 121.1547 | 121.3374 | 120.8314 | 121.1765 | 121.3331 | 121.1661 | 121.2633 | 121.2091 | 121.3162 | 121.2968 | 121.176 | 0.22647 | 0.28526 | 0.12855 | 0.067631 | 121.1775 | 121.3603 | 120.8543 | 121.1994 | -120.9511 | -120.6278 | -121.049 | -120.7257
1619.8594 | 121.5591 | -121.2753 | 0.19226 | 0.080646 | -0.090888 | 0.006315 | -0.052488 | 0.059155 | 0.039799 | -0.076452 | 0.20816 | 0.26237 | 0.10108 | 0.044743 | 121.1638 | 121.3511 | 120.8451 | 120.9705 | 121.356 | 121.1844 | 121.2816 | 121.2228 | 121.3345 | 121.3151 | 121.1989 | 0.23105 | 0.28526 | 0.12397 | 0.067631 | 121.1867 | 121.374 | 120.868 | 120.9934 | -120.9557 | -120.637 | -121.0627 | -120.744
1621.5469 | 121.5179 | -121.2936 | 0.20142 | 0.080646 | -0.086309 | 0.001736 | -0.052488 | 0.063733 | 0.048956 | -0.071874 | 0.199 | 0.26237 | 0.096503 | 0.049322 | 121.1684 | 121.3603 | 120.8588 | 120.9751 | 121.3743 | 121.2073 | 121.2954 | 121.2412 | 121.3574 | 121.3426 | 121.2218 | 0.22189 | 0.28526 | 0.11939 | 0.07221 | 121.1913 | 121.3832 | 120.8817 | 120.9979 | -120.9694 | -120.6598 | -121.0719 | -120.7623
1623.3125 | 121.5683 | -121.3211 | 0.18768 | 0.085224 | -0.086309 | 0.006315 | -0.052488 | 0.063733 | 0.044377 | -0.067295 | 0.19442 | 0.25779 | 0.096503 | 0.049322 | 121.1959 | 121.374 | 120.8817 | 120.9934 | 121.4063 | 121.2348 | 121.3274 | 121.2686 | 121.3848 | 121.3655 | 121.2538 | 0.21731 | 0.28068 | 0.11939 | 0.07221 | 121.2187 | 121.3969 | 120.9046 | 121.0163 | -121.0014 | -120.6873 | -121.0994 | -120.7852
1625.0781 | 121.6553 | -121.2845 | 0.16479 | 0.085224 | -0.090888 | 0.010893 | -0.052488 | 0.06831 | 0.039799 | -0.062717 | 0.18984 | 0.26237 | 0.096503 | 0.040164 | 121.1867 | 121.3877 | 120.8817 | 120.9979 | 121.3697 | 121.1936 | 121.2954 | 121.232 | 121.3528 | 121.3243 | 121.2218 | 0.21273 | 0.28526 | 0.11939 | 0.063052 | 121.2096 | 121.4106 | 120.9046 | 121.0208 | -120.9969 | -120.6919 | -121.0902 | -120.7852
1626.8125 | 121.582 | -121.3394 | 0.20599 | 0.080646 | -0.086309 | 0.010893 | -0.043331 | 0.06831 | 0.039799 | -0.067295 | 0.20816 | 0.25779 | 0.096503 | 0.044743 | 121.2325 | 121.3969 | 120.8909 | 121.0163 | 121.4201 | 121.2531 | 121.3503 | 121.2961 | 121.4077 | 121.3792 | 121.2721 | 0.23105 | 0.28068 | 0.11939 | 0.067631 | 121.2554 | 121.4198 | 120.9138 | 121.0391 | -121.0243 | -120.6827 | -121.136 | -120.7944
1628.5 | 121.5454 | -121.3165 | 0.20142 | 0.085224 | -0.086309 | 0.006315 | -0.052488 | 0.06831 | 0.039799 | -0.071874 | 0.20358 | 0.26695 | 0.10108 | 0.044743 | 121.205 | 121.4061 | 120.9092 | 121.03 | 121.4018 | 121.2302 | 121.3228 | 121.264 | 121.3848 | 121.3563 | 121.2447 | 0.22647 | 0.28984 | 0.12397 | 0.067631 | 121.2279 | 121.4289 | 120.9321 | 121.0529 | -121.0014 | -120.7056 | -121.1039 | -120.8081
1630.25 | 121.6187 | -121.3303 | 0.19684 | 0.080646 | -0.077151 | 0.001736 | -0.052488 | 0.059155 | 0.048956 | -0.071874 | 0.199 | 0.25321 | 0.10108 | 0.044743 | 121.2325 | 121.4152 | 120.9184 | 121.0392 | 121.4109 | 121.2531 | 121.332 | 121.2778 | 121.3894 | 121.3792 | 121.2584 | 0.22189 | 0.2761 | 0.12397 | 0.067631 | 121.2554 | 121.4381 | 120.9413 | 121.062 | -121.0335 | -120.7194 | -121.1314 | -120.8173
1631.9375 | 121.6187 | -121.344 | 0.18768 | 0.076067 | -0.08173 | 0.010893 | -0.057066 | 0.059155 | 0.048956 | -0.071874 | 0.199 | 0.25321 | 0.10108 | 0.049322 | 121.2416 | 121.4152 | 120.9321 | 121.0437 | 121.4201 | 121.2623 | 121.3549 | 121.2869 | 121.4031 | 121.3929 | 121.2721 | 0.22189 | 0.2761 | 0.12397 | 0.07221 | 121.2645 | 121.4381 | 120.955 | 121.0666 | -121.0426 | -120.7331 | -121.1406 | -120.831
1633.6719 | 121.582 | -121.3623 | 0.19684 | 0.085224 | -0.08173 | 0.010893 | -0.043331 | 0.06831 | 0.044377 | -0.067295 | 0.18984 | 0.25321 | 0.096503 | 0.044743 | 121.2416 | 121.4335 | 120.9367 | 121.0529 | 121.4475 | 121.2806 | 121.3732 | 121.319 | 121.4306 | 121.4067 | 121.295 | 0.21273 | 0.2761 | 0.11939 | 0.067631 | 121.2645 | 121.4564 | 120.9596 | 121.0758 | -121.0518 | -120.7468 | -121.1451 | -120.8402
1635.4375 | 121.6278 | -121.3623 | 0.21515 | 0.080646 | -0.08173 | 0.006315 | -0.052488 | 0.054577 | 0.039799 | -0.067295 | 0.19442 | 0.25321 | 0.10108 | 0.049322 | 121.2737 | 121.4427 | 120.9413 | 121.0666 | 121.443 | 121.2806 | 121.3686 | 121.3098 | 121.4169 | 121.4021 | 121.295 | 0.21731 | 0.2761 | 0.12397 | 0.07221 | 121.2966 | 121.4656 | 120.9641 | 121.0895 | -121.0793 | -120.7468 | -121.1726 | -120.8402
1637.1875 | 121.669 | -121.3394 | 0.20599 | 0.080646 | -0.08173 | 0.015472 | -0.052488 | 0.059155 | 0.039799 | -0.071874 | 0.20358 | 0.27153 | 0.10566 | 0.049322 | 121.2645 | 121.4335 | 120.9321 | 121.0575 | 121.4201 | 121.2577 | 121.3549 | 121.2869 | 121.3986 | 121.3792 | 121.2675 | 0.22647 | 0.29442 | 0.12855 | 0.07221 | 121.2874 | 121.4564 | 120.955 | 121.0804 | -121.061 | -120.7285 | -121.1589 | -120.8264
1638.9375 | 121.6049 | -121.3577 | 0.22888 | 0.080646 | -0.077151 | 0.010893 | -0.052488 | 0.063733 | 0.048956 | -0.071874 | 0.20816 | 0.28526 | 0.11482 | 0.05848 | 121.2554 | 121.4335 | 120.9413 | 121.0529 | 121.4384 | 121.2806 | 121.3686 | 121.3052 | 121.4215 | 121.4067 | 121.2859 | 0.23105 | 0.30815 | 0.1377 | 0.081368 | 121.2783 | 121.4564 | 120.9641 | 121.0758 | -121.0472 | -120.7331 | -121.1406 | -120.8264
1640.625 | 121.6965 | -121.3577 | 0.20599 | 0.085224 | -0.08173 | 0.010893 | -0.052488 | 0.063733 | 0.048956 | -0.076452 | 0.20816 | 0.27153 | 0.11024 | 0.063059 | 121.2508 | 121.4427 | 120.9458 | 121.0712 | 121.443 | 121.276 | 121.3686 | 121.3052 | 121.4215 | 121.4067 | 121.2813 | 0.23105 | 0.29442 | 0.13313 | 0.085947 | 121.2737 | 121.4656 | 120.9687 | 121.0941 | -121.0426 | -120.7377 | -121.1406 | -120.8356
1642.375 | 121.6232 | -121.3669 | 0.21973 | 0.085224 | -0.077151 | 0.010893 | -0.052488 | 0.059155 | 0.044377 | -0.067295 | 0.20816 | 0.27611 | 0.11482 | 0.053901 | 121.2554 | 121.4518 | 120.9458 | 121.0666 | 121.4521 | 121.2897 | 121.3778 | 121.3144 | 121.426 | 121.4113 | 121.2996 | 0.23105 | 0.29899 | 0.1377 | 0.076789 | 121.2783 | 121.4747 | 120.9687 | 121.0895 | -121.0472 | -120.7377 | -121.1406 | -120.831
1644.125 | 121.7056 | -121.3623 | 0.21057 | 0.080646 | -0.072572 | 0.010893 | -0.047909 | 0.063733 | 0.039799 | -0.076452 | 0.20816 | 0.28526 | 0.11024 | 0.063059 | 121.3057 | 121.4564 | 120.955 | 121.0804 | 121.443 | 121.2897 | 121.3732 | 121.3144 | 121.426 | 121.4021 | 121.2859 | 0.23105 | 0.30815 | 0.13313 | 0.085947 | 121.3286 | 121.4793 | 120.9779 | 121.1032 | -121.0976 | -120.7468 | -121.1955 | -120.8448
1645.8906 | 121.6644 | -121.3943 | 0.2243 | 0.080646 | -0.077151 | 0.001736 | -0.052488 | 0.063733 | 0.048956 | -0.071874 | 0.20816 | 0.27611 | 0.11024 | 0.063059 | 121.2645 | 121.461 | 120.955 | 121.0712 | 121.475 | 121.3172 | 121.3961 | 121.3419 | 121.4581 | 121.4433 | 121.3225 | 0.23105 | 0.29899 | 0.13313 | 0.085947 | 121.2874 | 121.4839 | 120.9779 | 121.0941 | -121.0564 | -120.7468 | -121.1543 | -120.8448
1647.5625 | 121.7468 | -121.3531 | 0.16937 | 0.085224 | -0.072572 | 0.015472 | -0.052488 | 0.059155 | 0.039799 | -0.071874 | 0.21274 | 0.27153 | 0.10566 | 0.05848 | 121.292 | 121.4564 | 120.955 | 121.0895 | 121.4384 | 121.2806 | 121.3686 | 121.3007 | 121.4123 | 121.3929 | 121.2813 | 0.23562 | 0.29442 | 0.12855 | 0.081368 | 121.3149 | 121.4793 | 120.9779 | 121.1124 | -121.0793 | -120.7423 | -121.1863 | -120.8493
1649.3125 | 121.701 | -121.3943 | 0.20142 | 0.080646 | -0.08173 | 0.010893 | -0.057066 | 0.06831 | 0.039799 | -0.076452 | 0.20358 | 0.28069 | 0.11939 | 0.053901 | 121.2874 | 121.4702 | 120.9733 | 121.0941 | 121.475 | 121.3126 | 121.4052 | 121.3373 | 121.4627 | 121.4341 | 121.3179 | 0.22647 | 0.30357 | 0.14228 | 0.076789 | 121.3103 | 121.493 | 120.9962 | 121.117 | -121.0838 | -120.7697 | -121.168 | -120.8539
1651 | 121.7194 | -121.463 | 0.16937 | 0.085224 | -0.077151 | 0.010893 | -0.057066 | 0.063733 | 0.044377 | -0.071874 | 0.17153 | 0.23948 | 0.073611 | 0.026427 | 121.3378 | 121.5159 | 121.0145 | 121.355 | 121.5482 | 121.3859 | 121.4739 | 121.4059 | 121.5267 | 121.5074 | 121.3911 | 0.19442 | 0.26236 | 0.096499 | 0.049315 | 121.3607 | 121.5388 | 121.0374 | 121.3779 | -121.1662 | -120.843 | -121.2642 | -120.9409
1652.7344 | 121.7514 | -121.4447 | 0.16479 | 0.085224 | -0.077151 | 0.001736 | -0.047909 | 0.063733 | 0.048956 | -0.067295 | 0.17153 | 0.23032 | 0.07819 | 0.031006 | 121.3652 | 121.5342 | 121.0374 | 121.2131 | 121.5299 | 121.3676 | 121.4464 | 121.3968 | 121.5084 | 121.4937 | 121.3774 | 0.19442 | 0.25321 | 0.10108 | 0.053894 | 121.3881 | 121.5571 | 121.0603 | 121.236 | -121.1937 | -120.8659 | -121.2871 | -120.9592
1654.5 | 121.6965 | -121.4722 | 0.16479 | 0.089802 | -0.072572 | 0.010893 | -0.047909 | 0.059155 | 0.048956 | -0.062717 | 0.17153 | 0.2349 | 0.082768 | 0.026427 | 121.3652 | 121.5388 | 121.0466 | 121.1673 | 121.562 | 121.3996 | 121.4831 | 121.4243 | 121.5313 | 121.5211 | 121.4095 | 0.19442 | 0.25778 | 0.10566 | 0.049315 | 121.3881 | 121.5617 | 121.0694 | 121.1902 | -121.1937 | -120.875 | -121.2825 | -120.9638
1656.2656 | 121.701 | -121.4767 | 0.19226 | 0.080646 | -0.072572 | 0.010893 | -0.038752 | 0.059155 | 0.039799 | -0.067295 | 0.16237 | 0.23032 | 0.073611 | 0.026427 | 121.3561 | 121.548 | 121.0557 | 121.1719 | 121.5574 | 121.4042 | 121.4876 | 121.438 | 121.5359 | 121.5165 | 121.4095 | 0.18526 | 0.25321 | 0.096499 | 0.049315 | 121.379 | 121.5709 | 121.0786 | 121.1948 | -121.1937 | -120.8933 | -121.2825 | -120.9821
1658.0312 | 121.7972 | -121.4447 | 0.13733 | 0.076067 | -0.072572 | 0.010893 | -0.043331 | 0.059155 | 0.039799 | -0.071874 | 0.17153 | 0.24405 | 0.073611 | 0.026427 | 121.4385 | 121.5617 | 121.0695 | 121.1948 | 121.5208 | 121.3721 | 121.4556 | 121.4014 | 121.5039 | 121.4845 | 121.3728 | 0.19442 | 0.26694 | 0.096499 | 0.049315 | 121.4614 | 121.5846 | 121.0923 | 121.2177 | -121.267 | -120.8979 | -121.3649 | -120.9958
1659.7188 | 121.7377 | -121.5134 | 0.15564 | 0.085224 | -0.067994 | 0.010893 | -0.052488 | 0.063733 | 0.039799 | -0.067295 | 0.17153 | 0.2349 | 0.073611 | 0.031006 | 121.379 | 121.5709 | 121.0695 | 121.1994 | 121.5986 | 121.4454 | 121.5243 | 121.4609 | 121.5771 | 121.5532 | 121.4461 | 0.19442 | 0.25778 | 0.096499 | 0.053894 | 121.4019 | 121.5938 | 121.0923 | 121.2223 | -121.2075 | -120.8979 | -121.3054 | -120.9958
1661.4688 | 121.8109 | -121.4676 | 0.15564 | 0.080646 | -0.08173 | 0.006315 | -0.047909 | 0.06831 | 0.044377 | -0.076452 | 0.17153 | 0.24863 | 0.07819 | 0.00811 | 121.3927 | 121.5754 | 121.074 | 121.1994 | 121.5482 | 121.3859 | 121.4739 | 121.4197 | 121.5359 | 121.512 | 121.3911 | 0.19442 | 0.27152 | 0.10108 | 0.030998 | 121.4156 | 121.5983 | 121.0969 | 121.2223 | -121.2212 | -120.9025 | -121.3145 | -120.9958
1663.2031 | 121.7697 | -121.4905 | 0.16937 | 0.080646 | -0.067994 | 0.015472 | -0.052488 | 0.059155 | 0.039799 | -0.076452 | 0.16237 | 0.24405 | 0.073611 | 0.035585 | 121.3973 | 121.5892 | 121.0969 | 121.2177 | 121.5711 | 121.4225 | 121.506 | 121.438 | 121.5496 | 121.5303 | 121.414 | 0.18526 | 0.26694 | 0.096499 | 0.058473 | 121.4202 | 121.6121 | 121.1198 | 121.2406 | -121.2349 | -120.9346 | -121.3237 | -121.0233
1664.9531 | 121.8292 | -121.4813 | 0.14191 | 0.085224 | -0.077151 | 0.006315 | -0.043331 | 0.06831 | 0.044377 | -0.071874 | 0.23105 | 0.29442 | 0.14229 | 0.10885 | 121.5575 | 121.5342 | 121.2709 | 121.3734 | 121.5665 | 121.4042 | 121.4876 | 121.438 | 121.5496 | 121.5257 | 121.4094 | 0.25394 | 0.31731 | 0.16517 | 0.13174 | 121.5804 | 121.5571 | 121.2938 | 121.3962 | -121.3265 | -121.0399 | -121.4152 | -121.1286
1666.625 | 121.6919 | -97.8378 | 23.8266 | 0.089802 | -0.063415 | 0.020051 | -0.038752 | 0.072888 | 0.044377 | -0.067295 | 23.8469 | 23.7975 | 23.7616 | 23.6909 | 97.7144 | 97.8748 | 97.3763 | 97.5211 | 97.9276 | 97.7744 | 97.8579 | 97.7991 | 97.9107 | 97.8822 | 97.7705 | 23.8698 | 23.8204 | 23.7845 | 23.7138 | 97.7373 | 97.8977 | 97.3992 | 97.544 | -73.8675 | -73.5294 | -73.9528 | -73.6147
1668.375 | 121.7834 | -97.7737 | 23.8083 | 0.080646 | -0.063415 | 0.015472 | -0.043331 | 0.063733 | 0.044377 | -0.076452 | 23.8286 | 23.7929 | 23.7525 | 23.6725 | 97.7281 | 97.8885 | 97.39 | 97.5485 | 97.8544 | 97.7103 | 97.7892 | 97.7304 | 97.8375 | 97.8181 | 97.6973 | 23.8515 | 23.8158 | 23.7754 | 23.6954 | 97.751 | 97.9114 | 97.4129 | 97.5714 | -73.8995 | -73.5614 | -73.9757 | -73.6376
1670.125 | 121.7468 | -97.7783 | 23.8495 | 0.085224 | -0.063415 | 0.015472 | -0.038752 | 0.072888 | 0.044377 | -0.062717 | 23.8423 | 23.8158 | 23.7708 | 23.6909 | 97.7098 | 97.8794 | 97.3763 | 97.5257 | 97.8635 | 97.7149 | 97.7938 | 97.7396 | 97.8512 | 97.8227 | 97.7156 | 23.8652 | 23.8387 | 23.7937 | 23.7138 | 97.7327 | 97.9023 | 97.3992 | 97.5485 | -73.8675 | -73.5339 | -73.939 | -73.6055
1671.875 | 121.843 | -97.7371 | 23.8495 | 0.080646 | -0.072572 | 0.015472 | -0.043331 | 0.06831 | 0.044377 | -0.062717 | 23.8561 | 23.8295 | 23.7845 | 23.7138 | 97.6961 | 97.8656 | 97.3626 | 97.5073 | 97.8178 | 97.6646 | 97.7526 | 97.6938 | 97.8054 | 97.7815 | 97.6744 | 23.879 | 23.8524 | 23.8074 | 23.7366 | 97.719 | 97.8885 | 97.3854 | 97.5302 | -73.84 | -73.5065 | -73.9116 | -73.578
1673.5625 | 121.7468 | -97.7509 | 23.8953 | 0.080646 | -0.067994 | 0.010893 | -0.052488 | 0.06831 | 0.039799 | -0.071874 | 23.8836 | 23.8341 | 23.8074 | 23.7275 | 97.6915 | 97.8611 | 97.358 | 97.5119 | 97.8315 | 97.6829 | 97.7617 | 97.6984 | 97.8192 | 97.7907 | 97.679 | 23.9064 | 23.857 | 23.8303 | 23.7504 | 97.7144 | 97.884 | 97.3809 | 97.5348 | -73.808 | -73.4744 | -73.8841 | -73.5506
1675.3281 | 121.8292 | -97.7142 | 23.8724 | 0.085224 | -0.067994 | 0.015472 | -0.047909 | 0.072888 | 0.044377 | -0.067295 | 23.8927 | 23.8616 | 23.8303 | 23.7458 | 97.6824 | 97.8519 | 97.3488 | 97.4936 | 97.7995 | 97.6462 | 97.7297 | 97.6663 | 97.7871 | 97.7586 | 97.6469 | 23.9156 | 23.8845 | 23.8532 | 23.7687 | 97.7052 | 97.8748 | 97.3717 | 97.5165 | -73.7896 | -73.4561 | -73.852 | -73.5185
1677.0938 | 121.8201 | -97.7188 | 23.9227 | 0.080646 | -0.072572 | 0.020051 | -0.047909 | 0.059155 | 0.044377 | -0.071874 | 23.9248 | 23.8936 | 23.8486 | 23.7687 | 97.664 | 97.829 | 97.3214 | 97.4753 | 97.7995 | 97.6462 | 97.7389 | 97.6709 | 97.778 | 97.7632 | 97.6469 | 23.9476 | 23.9165 | 23.8715 | 23.7916 | 97.6869 | 97.8519 | 97.3442 | 97.4982 | -73.7393 | -73.3966 | -73.8154 | -73.4727
1678.8438 | 121.8063 | -121.5042 | 0.17395 | 0.080646 | -0.072572 | 0.010893 | -0.047909 | 0.063733 | 0.039799 | -0.071874 | 0.18526 | 0.24863 | 0.16975 | 0.12259 | 121.6537 | 121.6304 | 121.3762 | 121.4741 | 121.5849 | 121.4316 | 121.5151 | 121.4563 | 121.5679 | 121.544 | 121.4323 | 0.20815 | 0.27152 | 0.19264 | 0.14547 | 121.6766 | 121.6533 | 121.3991 | 121.497 | -121.4684 | -121.1909 | -121.4839 | -121.2065
1680.5469 | 121.8475 | -121.5179 | 0.16479 | 0.085224 | -0.08173 | 0.001736 | -0.052488 | 0.063733 | 0.039799 | -0.076452 | 0.16695 | 0.2349 | 0.07819 | 0.031006 | 121.4751 | 121.6487 | 121.161 | 121.4924 | 121.6032 | 121.4362 | 121.5197 | 121.4655 | 121.5817 | 121.5577 | 121.4415 | 0.18984 | 0.25778 | 0.10108 | 0.053894 | 121.498 | 121.6716 | 121.1839 | 121.5153 | -121.3082 | -120.9941 | -121.3969 | -121.0828
1682.2969 | 121.7834 | -121.6003 | 0.17395 | 0.085224 | -0.067994 | 0.001736 | -0.052488 | 0.063733 | 0.035221 | -0.071874 | 0.16695 | 0.2349 | 0.073611 | 0.026427 | 121.5117 | 121.6624 | 121.161 | 121.442 | 121.6856 | 121.5323 | 121.6021 | 121.5479 | 121.6641 | 121.6356 | 121.5285 | 0.18984 | 0.25778 | 0.096499 | 0.049315 | 121.5346 | 121.6853 | 121.1839 | 121.4649 | -121.3448 | -120.9941 | -121.4381 | -121.0874
1684.0625 | 121.9208 | -121.5408 | 0.13275 | 0.085224 | -0.072572 | 0.001736 | -0.052488 | 0.059155 | 0.039799 | -0.076452 | 0.16237 | 0.2349 | 0.073611 | 0.031006 | 121.553 | 121.6624 | 121.1656 | 121.2909 | 121.6261 | 121.4683 | 121.5426 | 121.4883 | 121.6 | 121.5806 | 121.4644 | 0.18526 | 0.25778 | 0.096499 | 0.053894 | 121.5758 | 121.6853 | 121.1885 | 121.3138 | -121.3906 | -121.0032 | -121.4793 | -121.092
1685.8125 | 121.8384 | -121.5912 | 0.16937 | 0.085224 | -0.077151 | 0.015472 | -0.052488 | 0.063733 | 0.048956 | -0.076452 | 0.16695 | 0.22574 | 0.073611 | 0.035585 | 121.5209 | 121.6807 | 121.1702 | 121.3047 | 121.6764 | 121.514 | 121.6067 | 121.5387 | 121.6549 | 121.6401 | 121.5147 | 0.18984 | 0.24863 | 0.096499 | 0.058473 | 121.5438 | 121.7036 | 121.1931 | 121.3276 | -121.354 | -121.0032 | -121.4473 | -121.0966
1687.5781 | 121.8018 | -119.3665 | 2.4033 | 0.089802 | -0.072572 | 0.006315 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 2.4562 | 2.4556 | 2.3261 | 2.2152 | 119.273 | 119.378 | 118.881 | 119.0019 | 119.4563 | 119.2939 | 119.3728 | 119.3185 | 119.4302 | 119.4154 | 119.2946 | 2.4791 | 2.4785 | 2.349 | 2.2381 | 119.2959 | 119.4009 | 118.9039 | 119.0248 | -116.8168 | -116.4248 | -116.9469 | -116.5549
1689.2656 | 121.8338 | -119.0918 | 2.6779 | 0.085224 | -0.072572 | 0.010893 | -0.047909 | 0.059155 | 0.044377 | -0.076452 | 2.6119 | 2.6296 | 2.4955 | 2.435 | 119.1357 | 119.2223 | 118.7299 | 118.8599 | 119.177 | 119.0192 | 119.1027 | 119.0439 | 119.151 | 119.1362 | 119.0153 | 2.6348 | 2.6525 | 2.5184 | 2.4579 | 119.1586 | 119.2452 | 118.7528 | 118.8828 | -116.5238 | -116.118 | -116.6402 | -116.2344
1691.0156 | 121.7606 | -97.7463 | 24.0509 | 0.089802 | -0.063415 | 0.015472 | -0.043331 | 0.06831 | 0.044377 | -0.067295 | 24.0438 | 24.0081 | 23.9814 | 23.8923 | 97.5862 | 97.7649 | 97.2573 | 97.402 | 97.8361 | 97.6829 | 97.7617 | 97.7029 | 97.8146 | 97.7907 | 97.679 | 24.0667 | 24.031 | 24.0043 | 23.9152 | 97.6091 | 97.7878 | 97.2801 | 97.4249 | -73.5424 | -73.2135 | -73.6048 | -73.2759
1692.6875 | 121.9025 | -97.673 | 24.0005 | 0.089802 | -0.067994 | 0.015472 | -0.043331 | 0.063733 | 0.048956 | -0.067295 | 24.0438 | 24.0081 | 23.9631 | 23.8969 | 97.6045 | 97.7787 | 97.271 | 97.4204 | 97.7628 | 97.605 | 97.6885 | 97.6297 | 97.7368 | 97.722 | 97.6057 | 24.0667 | 24.031 | 23.986 | 23.9198 | 97.6274 | 97.8015 | 97.2939 | 97.4432 | -73.5607 | -73.2272 | -73.6414 | -73.3079
1694.4531 | 121.9437 | -121.5591 | 0.14191 | 0.076067 | -0.08173 | -0.002842 | -0.052488 | 0.054577 | 0.039799 | -0.076452 | 0.16695 | 0.24405 | 0.07819 | 0.099691 | 121.7269 | 121.7082 | 121.2022 | 121.5382 | 121.6352 | 121.4774 | 121.5563 | 121.5067 | 121.6137 | 121.5989 | 121.4827 | 0.18984 | 0.26694 | 0.10108 | 0.12258 | 121.7498 | 121.7311 | 121.2251 | 121.5611 | -121.56 | -121.0353 | -121.6487 | -121.124
1696.1562 | 121.9162 | -121.582 | 0.15564 | 0.089802 | -0.077151 | 0.006315 | -0.052488 | 0.059155 | 0.044377 | -0.076452 | 0.16695 | 0.22574 | 0.07819 | 0.031006 | 121.5713 | 121.7128 | 121.216 | 121.5565 | 121.6718 | 121.5049 | 121.5883 | 121.5295 | 121.6412 | 121.6264 | 121.5056 | 0.18984 | 0.24863 | 0.10108 | 0.053894 | 121.5942 | 121.7357 | 121.2388 | 121.5794 | -121.4043 | -121.049 | -121.4931 | -121.1378
1697.9062 | 121.9803 | -121.6232 | 0.13275 | 0.080646 | -0.077151 | -0.002842 | -0.052488 | 0.059155 | 0.039799 | -0.076452 | 0.15779 | 0.23032 | 0.073611 | 0.026427 | 121.5804 | 121.7219 | 121.216 | 121.355 | 121.7039 | 121.5461 | 121.6204 | 121.5707 | 121.6824 | 121.663 | 121.5468 | 0.18068 | 0.25321 | 0.096499 | 0.049315 | 121.6033 | 121.7448 | 121.2388 | 121.3779 | -121.4226 | -121.0582 | -121.5068 | -121.1423
1699.5938 | 121.8567 | -121.6461 | 0.17395 | 0.085224 | -0.077151 | -0.002842 | -0.052488 | 0.059155 | 0.039799 | -0.076452 | 0.16237 | 0.23032 | 0.073611 | 0.031006 | 121.5621 | 121.7311 | 121.2343 | 121.3642 | 121.7313 | 121.569 | 121.6433 | 121.5936 | 121.7053 | 121.6859 | 121.5697 | 0.18526 | 0.25321 | 0.096499 | 0.053894 | 121.585 | 121.754 | 121.2572 | 121.3871 | -121.3997 | -121.0719 | -121.4885 | -121.1607
1701.3594 | 121.8521 | -121.6553 | 0.17853 | 0.076067 | -0.086309 | 0.001736 | -0.052488 | 0.059155 | 0.039799 | -0.076452 | 0.15779 | 0.23032 | 0.064455 | 0.026427 | 121.5667 | 121.7403 | 121.2343 | 121.3596 | 121.7313 | 121.569 | 121.657 | 121.6028 | 121.7144 | 121.6951 | 121.5788 | 0.18068 | 0.25321 | 0.087343 | 0.049315 | 121.5896 | 121.7631 | 121.2572 | 121.3825 | -121.4089 | -121.0765 | -121.5022 | -121.1698
1703.125 | 121.907 | -121.669 | 0.16937 | 0.085224 | -0.077151 | 0.001736 | -0.057066 | 0.059155 | 0.039799 | -0.08103 | 0.16237 | 0.22574 | 0.073611 | 0.031006 | 121.5804 | 121.7403 | 121.2434 | 121.3688 | 121.7542 | 121.5919 | 121.6707 | 121.6119 | 121.7282 | 121.7088 | 121.588 | 0.18526 | 0.24863 | 0.096499 | 0.053894 | 121.6033 | 121.7631 | 121.2663 | 121.3917 | -121.418 | -121.0811 | -121.5068 | -121.1698
1704.875 | 121.8567 | -121.6782 | 0.20599 | 0.080646 | -0.077151 | 0.001736 | -0.057066 | 0.059155 | 0.035221 | -0.08103 | 0.16695 | 0.22574 | 0.07819 | 0.00811 | 121.5804 | 121.7494 | 121.2526 | 121.3596 | 121.7588 | 121.601 | 121.6799 | 121.6211 | 121.7373 | 121.7134 | 121.5971 | 0.18984 | 0.24863 | 0.10108 | 0.030998 | 121.6033 | 121.7723 | 121.2755 | 121.3825 | -121.4135 | -121.0856 | -121.5022 | -121.1744
1706.5781 | 121.9391 | -121.6599 | 0.15564 | 0.085224 | -0.077151 | 0.001736 | -0.057066 | 0.054577 | 0.030642 | -0.076452 | 0.16237 | 0.2349 | 0.069033 | 0.026427 | 121.585 | 121.754 | 121.248 | 121.3779 | 121.7451 | 121.5827 | 121.6616 | 121.6028 | 121.7144 | 121.6905 | 121.5834 | 0.18526 | 0.25778 | 0.091921 | 0.049315 | 121.6079 | 121.7769 | 121.2709 | 121.4008 | -121.4226 | -121.0856 | -121.516 | -121.179
1708.3281 | 121.9528 | -121.5317 | 0.25177 | 0.076067 | -0.08173 | 0.001736 | -0.057066 | 0.049999 | 0.035221 | -0.08103 | 0.199 | 0.27153 | 0.10108 | 0.05848 | 121.5301 | 121.7265 | 121.2114 | 121.3459 | 121.6077 | 121.4499 | 121.5334 | 121.4746 | 121.5817 | 121.5669 | 121.4506 | 0.22189 | 0.29442 | 0.12397 | 0.081368 | 121.5529 | 121.7494 | 121.2343 | 121.3688 | -121.3311 | -121.0124 | -121.429 | -121.1103
1710.0156 | 121.962 | -121.582 | 0.21973 | 0.080646 | -0.08173 | -0.002842 | -0.052488 | 0.054577 | 0.026064 | -0.085608 | 0.20816 | 0.27611 | 0.12397 | 0.067638 | 121.5713 | 121.7128 | 121.216 | 121.3459 | 121.6627 | 121.5003 | 121.5792 | 121.5295 | 121.6366 | 121.6081 | 121.4964 | 0.23105 | 0.29899 | 0.14686 | 0.090526 | 121.5942 | 121.7357 | 121.2388 | 121.3688 | -121.3631 | -121.0078 | -121.4473 | -121.092
1711.7812 | 121.9437 | -121.6644 | 0.1831 | 0.080646 | -0.086309 | 0.006315 | -0.052488 | 0.059155 | 0.039799 | -0.08103 | 0.18069 | 0.24863 | 0.091925 | 0.040164 | 121.5896 | 121.7494 | 121.2572 | 121.3734 | 121.7451 | 121.5781 | 121.6707 | 121.6119 | 121.7236 | 121.7042 | 121.5834 | 0.20357 | 0.27152 | 0.11481 | 0.063052 | 121.6125 | 121.7723 | 121.2801 | 121.3962 | -121.4089 | -121.0765 | -121.4977 | -121.1652
1713.5469 | 121.8979 | -121.5637 | 0.34332 | 0.080646 | -0.086309 | -0.002842 | -0.057066 | 0.049999 | 0.035221 | -0.085608 | 0.30888 | 0.32647 | 0.21096 | 0.1409 | 121.4705 | 121.6304 | 121.129 | 121.2543 | 121.6444 | 121.4774 | 121.5609 | 121.5067 | 121.6137 | 121.5989 | 121.4781 | 0.33177 | 0.34936 | 0.23385 | 0.16379 | 121.4934 | 121.6533 | 121.1519 | 121.2772 | -121.1617 | -120.8201 | -121.2596 | -120.918
1715.3125 | 122.0215 | -119.3024 | 2.4582 | 0.085224 | -0.090888 | -0.007421 | -0.052488 | 0.049999 | 0.026064 | -0.08103 | 2.5752 | 2.6342 | 2.5505 | 2.5174 | 119.3692 | 119.3551 | 119.0138 | 119.1987 | 119.3876 | 119.2115 | 119.2949 | 119.2499 | 119.3524 | 119.3284 | 119.2213 | 2.5981 | 2.6571 | 2.5733 | 2.5403 | 119.3921 | 119.378 | 119.0366 | 119.2216 | -116.7939 | -116.4385 | -116.8187 | -116.4633
1717.0625 | 121.9437 | -118.8629 | 2.9709 | 0.080646 | -0.08173 | 0.001736 | -0.047909 | 0.054577 | 0.030642 | -0.08103 | 2.9278 | 2.9959 | 2.8114 | 2.7006 | 118.8381 | 118.9888 | 118.4918 | 118.6356 | 118.9436 | 118.7812 | 118.8647 | 118.815 | 118.9175 | 118.8936 | 118.7819 | 2.9507 | 3.0188 | 2.8343 | 2.7235 | 118.861 | 119.0117 | 118.5147 | 118.6585 | -115.9103 | -115.564 | -116.0267 | -115.6804
1718.8125 | 122.0306 | -118.6707 | 3.1265 | 0.080646 | -0.090888 | -0.002842 | -0.066223 | 0.049999 | 0.030642 | -0.08103 | 3.1521 | 3.2249 | 3.0266 | 2.9478 | 118.6229 | 118.7737 | 118.2721 | 118.4021 | 118.7513 | 118.5798 | 118.6678 | 118.6044 | 118.7207 | 118.7013 | 118.5896 | 3.175 | 3.2478 | 3.0495 | 2.9707 | 118.6458 | 118.7966 | 118.2949 | 118.425 | -115.4708 | -115.1199 | -115.5963 | -115.2455
1720.5156 | 121.9666 | -121.6965 | 0.17395 | 0.080646 | -0.090888 | 0.001736 | -0.061645 | 0.040843 | 0.021485 | -0.076452 | 0.15779 | 0.2349 | 0.073611 | 0.035585 | 121.8093 | 121.786 | 121.3121 | 121.616 | 121.7771 | 121.6056 | 121.6982 | 121.6348 | 121.7373 | 121.718 | 121.62 | 0.18068 | 0.25778 | 0.096499 | 0.058473 | 121.8322 | 121.8089 | 121.335 | 121.6389 | -121.6515 | -121.1543 | -121.7357 | -121.2385
1722.2656 | 121.9482 | -121.6919 | 0.16479 | 0.080646 | -0.086309 | -0.007421 | -0.057066 | 0.054577 | 0.030642 | -0.076452 | 0.15321 | 0.22574 | 0.069033 | 0.021847 | 121.6216 | 121.7998 | 121.2984 | 121.4558 | 121.7725 | 121.6056 | 121.6845 | 121.6348 | 121.7465 | 121.7225 | 121.6154 | 0.1761 | 0.24863 | 0.091921 | 0.044735 | 121.6445 | 121.8227 | 121.3213 | 121.4787 | -121.4684 | -121.1452 | -121.5526 | -121.2293
1724.0156 | 122.0078 | -121.7102 | 0.14648 | 0.085224 | -0.095467 | -0.007421 | -0.061645 | 0.045421 | 0.030642 | -0.08103 | 0.15779 | 0.23032 | 0.073611 | 0.031006 | 121.6079 | 121.8044 | 121.2984 | 121.4237 | 121.7954 | 121.6147 | 121.7028 | 121.6486 | 121.7556 | 121.7408 | 121.6292 | 0.18068 | 0.25321 | 0.096499 | 0.053894 | 121.6308 | 121.8272 | 121.3213 | 121.4466 | -121.4501 | -121.1406 | -121.5343 | -121.2248
1725.7031 | 122.0535 | -121.6736 | 0.13275 | 0.076067 | -0.090888 | -0.007421 | -0.057066 | 0.045421 | 0.035221 | -0.085608 | 0.15779 | 0.23032 | 0.069033 | 0.021847 | 121.6308 | 121.8044 | 121.3121 | 121.4329 | 121.7497 | 121.5827 | 121.6662 | 121.6165 | 121.719 | 121.7088 | 121.588 | 0.18068 | 0.25321 | 0.091921 | 0.044735 | 121.6537 | 121.8272 | 121.335 | 121.4558 | -121.473 | -121.1543 | -121.5617 | -121.2431
1727.4688 | 122.0398 | -121.6965 | 0.14191 | 0.080646 | -0.095467 | -0.012 | -0.061645 | 0.045421 | 0.026064 | -0.085608 | 0.14864 | 0.22116 | 0.059877 | 0.017268 | 121.6308 | 121.8044 | 121.3075 | 121.4283 | 121.7771 | 121.601 | 121.6845 | 121.6348 | 121.7419 | 121.7225 | 121.6109 | 0.17152 | 0.24405 | 0.082765 | 0.040156 | 121.6537 | 121.8272 | 121.3304 | 121.4512 | -121.4821 | -121.1589 | -121.5709 | -121.2477
1729.2344 | 122.0215 | -121.6782 | 0.1236 | 0.080646 | -0.095467 | -0.016578 | -0.061645 | 0.045421 | 0.030642 | -0.094765 | 0.14864 | 0.22574 | 0.064455 | 0.021847 | 121.6262 | 121.8181 | 121.3121 | 121.4329 | 121.7588 | 121.5827 | 121.6616 | 121.6165 | 121.7236 | 121.7088 | 121.5834 | 0.17152 | 0.24863 | 0.087343 | 0.044735 | 121.6491 | 121.841 | 121.335 | 121.4558 | -121.4776 | -121.1635 | -121.5617 | -121.2477
1731 | 122.0123 | -121.6873 | 0.16022 | 0.089802 | -0.10004 | -0.012 | -0.061645 | 0.040843 | 0.021485 | -0.094765 | 0.16237 | 0.21658 | 0.069033 | 0.021847 | 121.6583 | 121.8181 | 121.3121 | 121.4466 | 121.7771 | 121.5873 | 121.6753 | 121.6257 | 121.7282 | 121.7088 | 121.5926 | 0.18526 | 0.23947 | 0.091921 | 0.044735 | 121.6811 | 121.841 | 121.335 | 121.4695 | -121.4959 | -121.1497 | -121.5892 | -121.2431
1732.7031 | 121.9437 | -121.7285 | 0.16937 | 0.076067 | -0.10462 | -0.021157 | -0.07538 | 0.045421 | 0.021485 | -0.094765 | 0.14864 | 0.22574 | 0.059877 | 0.026427 | 121.6399 | 121.8135 | 121.3213 | 121.4512 | 121.8046 | 121.6239 | 121.7074 | 121.6531 | 121.7739 | 121.75 | 121.6338 | 0.17152 | 0.24863 | 0.082765 | 0.049315 | 121.6628 | 121.8364 | 121.3442 | 121.4741 | -121.4913 | -121.1726 | -121.5801 | -121.2614
1734.4531 | 121.8475 | -121.8063 | 0.1831 | 0.080646 | -0.10004 | -0.007421 | -0.066223 | 0.036265 | 0.026064 | -0.085608 | 0.14406 | 0.212 | 0.064455 | 0.017268 | 121.8185 | 121.7998 | 121.5319 | 121.6389 | 121.887 | 121.7063 | 121.7989 | 121.7401 | 121.8426 | 121.8324 | 121.7207 | 0.16695 | 0.23489 | 0.087343 | 0.040156 | 121.8414 | 121.8227 | 121.5548 | 121.6618 | -121.6744 | -121.3878 | -121.754 | -121.4674
1736.2188 | 121.9025 | -121.8292 | 0.16479 | 0.080646 | -0.095467 | -0.021157 | -0.066223 | 0.036265 | 0.026064 | -0.094765 | 0.13948 | 0.22116 | 0.064455 | 0.021847 | 121.7269 | 121.8456 | 121.3442 | 121.4787 | 121.9099 | 121.7338 | 121.8081 | 121.763 | 121.8655 | 121.8553 | 121.7345 | 0.16237 | 0.24405 | 0.087343 | 0.044735 | 121.7498 | 121.8684 | 121.367 | 121.5015 | -121.5874 | -121.2047 | -121.6625 | -121.2797
1737.9688 | 122.0627 | -121.7377 | 0.14191 | 0.076067 | -0.10462 | -0.025735 | -0.07538 | 0.036265 | 0.012329 | -0.094765 | 0.14864 | 0.21658 | 0.059877 | 0.017268 | 121.7407 | 121.8501 | 121.3533 | 121.4832 | 121.8137 | 121.633 | 121.7119 | 121.6623 | 121.7739 | 121.75 | 121.6429 | 0.17152 | 0.23947 | 0.082765 | 0.040156 | 121.7635 | 121.873 | 121.3762 | 121.5061 | -121.592 | -121.2047 | -121.6808 | -121.2934
1739.6406 | 121.9482 | -121.7789 | 0.17395 | 0.085224 | -0.10462 | -0.021157 | -0.061645 | 0.027109 | 0.016907 | -0.094765 | 0.14864 | 0.212 | 0.059877 | 0.017268 | 121.7132 | 121.8639 | 121.3625 | 121.4924 | 121.8641 | 121.6742 | 121.7577 | 121.7172 | 121.806 | 121.7958 | 121.6841 | 0.17152 | 0.23489 | 0.082765 | 0.040156 | 121.7361 | 121.8868 | 121.3854 | 121.5153 | -121.5646 | -121.2138 | -121.6533 | -121.3026
1741.4219 | 122.0627 | -121.7331 | 0.12817 | 0.085224 | -0.11378 | -0.016578 | -0.07538 | 0.036265 | 0.016907 | -0.099343 | 0.14406 | 0.21658 | 0.059877 | -0.001048 | 121.6995 | 121.8639 | 121.3625 | 121.4924 | 121.8183 | 121.6193 | 121.7165 | 121.6577 | 121.7694 | 121.75 | 121.6338 | 0.16695 | 0.23947 | 0.082765 | 0.02184 | 121.7223 | 121.8868 | 121.3854 | 121.5153 | -121.5554 | -121.2184 | -121.6396 | -121.3026
1743.1094 | 122.081 | -121.7331 | 0.1236 | 0.080646 | -0.10004 | -0.007421 | -0.070802 | 0.031687 | 0.016907 | -0.094765 | 0.14864 | 0.212 | 0.064455 | 0.021847 | 121.7452 | 121.8684 | 121.3716 | 121.5015 | 121.8137 | 121.633 | 121.7257 | 121.6623 | 121.7648 | 121.75 | 121.6383 | 0.17152 | 0.23489 | 0.087343 | 0.044735 | 121.7681 | 121.8913 | 121.3945 | 121.5244 | -121.5966 | -121.223 | -121.6808 | -121.3072
1744.8594 | 121.9666 | -121.8201 | 0.15564 | 0.089802 | -0.10004 | -0.012 | -0.066223 | 0.031687 | 0.026064 | -0.094765 | 0.13948 | 0.21658 | 0.055298 | 0.021847 | 121.6995 | 121.8776 | 121.3808 | 121.5061 | 121.9099 | 121.72 | 121.8081 | 121.7538 | 121.8518 | 121.8461 | 121.7253 | 0.16237 | 0.23947 | 0.078186 | 0.044735 | 121.7223 | 121.9005 | 121.4037 | 121.529 | -121.56 | -121.2413 | -121.6442 | -121.3255
1746.5781 | 122.0993 | -121.7743 | 0.14648 | 0.071489 | -0.10462 | -0.030314 | -0.070802 | 0.031687 | 0.016907 | -0.10392 | 0.14864 | 0.21658 | 0.064455 | 0.017268 | 121.7269 | 121.8868 | 121.3854 | 121.5153 | 121.8458 | 121.6697 | 121.744 | 121.7035 | 121.806 | 121.7912 | 121.6704 | 0.17152 | 0.23947 | 0.087343 | 0.040156 | 121.7498 | 121.9096 | 121.4082 | 121.5382 | -121.5783 | -121.2367 | -121.6625 | -121.3209
1748.2812 | 121.9986 | -121.8063 | 0.17395 | 0.085224 | -0.1092 | -0.016578 | -0.070802 | 0.031687 | 0.016907 | -0.090186 | 0.14406 | 0.21658 | 0.064455 | 0.021847 | 121.7635 | 121.8959 | 121.3854 | 121.5199 | 121.8916 | 121.6971 | 121.7898 | 121.7355 | 121.838 | 121.8232 | 121.7161 | 0.16695 | 0.23947 | 0.087343 | 0.044735 | 121.7864 | 121.9188 | 121.4082 | 121.5427 | -121.6195 | -121.2413 | -121.6991 | -121.3209
1750.0156 | 122.0673 | -121.7697 | 0.13733 | 0.080646 | -0.10462 | -0.016578 | -0.079959 | 0.031687 | 0.016907 | -0.090186 | 0.14864 | 0.21658 | 0.059877 | 0.012689 | 121.7361 | 121.8959 | 121.3899 | 121.5244 | 121.8504 | 121.6651 | 121.7531 | 121.6898 | 121.8014 | 121.7866 | 121.6795 | 0.17152 | 0.23947 | 0.082765 | 0.035577 | 121.759 | 121.9188 | 121.4128 | 121.5473 | -121.5874 | -121.2413 | -121.6762 | -121.3301
1751.7031 | 122.081 | -121.788 | 0.13275 | 0.080646 | -0.10004 | -0.021157 | -0.066223 | 0.036265 | 0.012329 | -0.094765 | 0.14406 | 0.22116 | 0.059877 | 0.017268 | 121.7269 | 121.9005 | 121.3991 | 121.5199 | 121.8687 | 121.688 | 121.7669 | 121.7218 | 121.8243 | 121.8004 | 121.6933 | 0.16695 | 0.24405 | 0.082765 | 0.040156 | 121.7498 | 121.9234 | 121.422 | 121.5427 | -121.5829 | -121.255 | -121.667 | -121.3392
1753.4531 | 121.994 | -121.8292 | 0.16479 | 0.076067 | -0.1092 | -0.016578 | -0.079959 | 0.036265 | 0.021485 | -0.099343 | 0.13948 | 0.21658 | 0.064455 | 0.021847 | 121.7178 | 121.9188 | 121.4128 | 121.5427 | 121.9053 | 121.72 | 121.8126 | 121.7493 | 121.8655 | 121.8507 | 121.7299 | 0.16237 | 0.23947 | 0.087343 | 0.044735 | 121.7407 | 121.9417 | 121.4357 | 121.5656 | -121.5783 | -121.2734 | -121.6533 | -121.3484
1755.1406 | 122.0718 | -121.8246 | 0.16479 | 0.080646 | -0.10462 | -0.021157 | -0.07538 | 0.031687 | 0.016907 | -0.10392 | 0.14406 | 0.21658 | 0.069033 | 0.021847 | 121.7727 | 121.9096 | 121.422 | 121.5427 | 121.9053 | 121.72 | 121.8035 | 121.7493 | 121.8563 | 121.8416 | 121.7207 | 0.16695 | 0.23947 | 0.091921 | 0.044735 | 121.7956 | 121.9325 | 121.4449 | 121.5656 | -121.6286 | -121.2779 | -121.7037 | -121.353
1756.8906 | 122.1542 | -121.8018 | 0.15106 | 0.080646 | -0.11378 | -0.025735 | -0.07538 | 0.027109 | 0.016907 | -0.094765 | 0.14406 | 0.22574 | 0.059877 | 0.026427 | 121.7407 | 121.9142 | 121.4174 | 121.5473 | 121.8824 | 121.688 | 121.776 | 121.7264 | 121.8289 | 121.8187 | 121.707 | 0.16695 | 0.24863 | 0.082765 | 0.049315 | 121.7635 | 121.9371 | 121.4403 | 121.5702 | -121.5966 | -121.2734 | -121.6808 | -121.3575
1758.6562 | 122.0627 | -121.8475 | 0.16937 | 0.071489 | -0.11378 | -0.025735 | -0.070802 | 0.027109 | 0.021485 | -0.094765 | 0.13948 | 0.21658 | 0.055298 | 0.021847 | 121.7681 | 121.9188 | 121.4403 | 121.5565 | 121.919 | 121.7338 | 121.8218 | 121.7767 | 121.8746 | 121.869 | 121.7528 | 0.16237 | 0.23947 | 0.078186 | 0.044735 | 121.791 | 121.9417 | 121.4632 | 121.5794 | -121.6286 | -121.3008 | -121.7128 | -121.385
1760.4219 | 121.9986 | -121.8704 | 0.15564 | 0.085224 | -0.090888 | 0.001736 | -0.061645 | 0.049999 | 0.035221 | -0.085608 | 0.1349 | 0.20742 | 0.11482 | 0.081375 | 0.54268 | 0.65499 | 121.6784 | 121.7762 | 121.9556 | 121.7795 | 121.8722 | 121.8088 | 121.9204 | 121.9056 | 121.7848 | 0.15779 | 0.23031 | 0.1377 | 0.10426 | 0.56557 | 0.67788 | 121.7013 | 121.7991 | -0.40778 | -121.5435 | -0.42786 | -121.5636
1762.125 | 122.0215 | -121.8384 | 0.15564 | 0.080646 | -0.090888 | -0.007421 | -0.066223 | 0.049999 | 0.035221 | -0.08103 | 0.12574 | 0.20284 | 0.055298 | -0.005627 | 0.50605 | 0.62752 | 121.4403 | 121.79 | 121.919 | 121.7475 | 121.831 | 121.7722 | 121.8884 | 121.8736 | 121.7573 | 0.14863 | 0.22573 | 0.078186 | 0.017261 | 0.52894 | 0.65041 | 121.4632 | 121.8129 | -0.38031 | -121.3146 | -0.45075 | -121.385
1763.875 | 122.0352 | -121.843 | 0.15564 | 0.085224 | -0.095467 | -0.007421 | -0.052488 | 0.054577 | 0.035221 | -0.085608 | 0.13948 | 0.20284 | 0.055298 | -0.005627 | 0.38702 | 0.52223 | 121.4403 | 121.7854 | 121.9282 | 121.7475 | 121.8355 | 121.7905 | 121.8975 | 121.8782 | 121.7573 | 0.16237 | 0.22573 | 0.078186 | 0.017261 | 0.40991 | 0.54512 | 121.4632 | 121.8083 | -0.24754 | -121.3008 | -0.33172 | -121.385
1765.625 | 121.3715 | -121.1288 | 0.16022 | 0.076067 | -0.10004 | -0.012 | -0.066223 | 0.036265 | 0.021485 | -0.090186 | 5.3086 | 5.1251 | 5.2196 | 5.0908 | 0.22678 | 0.1743 | 115.0901 | 115.0738 | 121.2049 | 121.0288 | 121.1168 | 121.0626 | 121.1651 | 121.1503 | 121.0387 | 5.3315 | 5.148 | 5.2425 | 5.1137 | 0.24967 | 0.19718 | 115.113 | 115.0967 | 5.0818 | -109.7815 | 4.9928 | -109.8705
1767.4062 | 121.9391 | -121.6965 | 0.15106 | 0.080646 | -0.090888 | -0.012 | -0.070802 | 0.045421 | 0.026064 | -0.099343 | 0.13032 | 0.20284 | 0.05072 | 0.085954 | 0.14896 | 0.20176 | 121.5364 | 121.6435 | 121.7771 | 121.6056 | 121.6845 | 121.6257 | 121.7419 | 121.7225 | 121.5971 | 0.15321 | 0.22573 | 0.073608 | 0.10884 | 0.17184 | 0.22465 | 121.5593 | 121.6664 | -0.018633 | -121.4061 | -0.098235 | -121.4857
1769.1094 | 121.8933 | -121.7377 | 0.14191 | 0.076067 | -0.090888 | -0.007421 | -0.057066 | 0.054577 | 0.035221 | -0.085608 | 0.13032 | 0.20284 | 0.046142 | -0.023943 | 0.19474 | 0.27501 | 121.3442 | 121.6755 | 121.8137 | 121.6468 | 121.7303 | 121.6806 | 121.7922 | 121.7729 | 121.6521 | 0.15321 | 0.22573 | 0.06903 | -0.001055 | 0.21762 | 0.2979 | 121.367 | 121.6984 | -0.064415 | -121.2138 | -0.14859 | -121.298
1770.8594 | 122.081 | -121.7606 | 0.13275 | 0.076067 | -0.090888 | -0.016578 | -0.07538 | 0.045421 | 0.021485 | -0.085608 | 0.1349 | 0.20284 | 0.05072 | -0.001048 | 0.2451 | 0.33453 | 121.367 | 121.703 | 121.8366 | 121.6697 | 121.744 | 121.6852 | 121.806 | 121.782 | 121.675 | 0.15779 | 0.22573 | 0.073608 | 0.02184 | 0.26799 | 0.35742 | 121.3899 | 121.7259 | -0.1102 | -121.2321 | -0.19438 | -121.3163
1772.625 | 121.994 | -121.7743 | 0.15106 | 0.080646 | -0.095467 | -0.007421 | -0.066223 | 0.036265 | 0.026064 | -0.08103 | 0.13032 | 0.20742 | 0.055298 | -0.023943 | 0.32293 | 0.43067 | 121.3854 | 121.7213 | 121.8549 | 121.6788 | 121.7669 | 121.7081 | 121.8106 | 121.8004 | 121.6933 | 0.15321 | 0.23031 | 0.078186 | -0.001055 | 0.34581 | 0.45356 | 121.4082 | 121.7442 | -0.1926 | -121.255 | -0.26763 | -121.3301
1774.3906 | 122.0901 | -121.7651 | 0.1236 | 0.080646 | -0.10004 | -0.007421 | -0.061645 | 0.045421 | 0.026064 | -0.090186 | 0.1349 | 0.20284 | 0.05072 | -0.019364 | 0.3275 | 0.43067 | 121.3945 | 121.7305 | 121.8458 | 121.6651 | 121.7577 | 121.7035 | 121.8106 | 121.7912 | 121.675 | 0.15779 | 0.22573 | 0.073608 | 0.003524 | 0.35039 | 0.45356 | 121.4174 | 121.7533 | -0.1926 | -121.2596 | -0.27678 | -121.3438
1776.0781 | 122.0169 | -121.8018 | 0.15564 | 0.080646 | -0.095467 | -0.007421 | -0.066223 | 0.040843 | 0.035221 | -0.085608 | 0.12574 | 0.19827 | 0.055298 | 0.003531 | 0.40533 | 0.52223 | 121.4037 | 121.7442 | 121.8824 | 121.7063 | 121.7943 | 121.7355 | 121.8426 | 121.837 | 121.7162 | 0.14863 | 0.22115 | 0.078186 | 0.026419 | 0.42822 | 0.54512 | 121.4266 | 121.7671 | -0.27959 | -121.2779 | -0.35003 | -121.3484
1777.8281 | 122.0627 | -121.8018 | 0.15106 | 0.080646 | -0.10004 | -0.012 | -0.061645 | 0.045421 | 0.035221 | -0.090186 | 0.13032 | 0.19827 | 0.05072 | -0.005627 | 0.25883 | 0.34826 | 121.4128 | 121.5473 | 121.8824 | 121.7017 | 121.7898 | 121.7401 | 121.8472 | 121.837 | 121.7116 | 0.15321 | 0.22115 | 0.073608 | 0.017261 | 0.28172 | 0.37115 | 121.4357 | 121.5702 | -0.12851 | -121.2825 | -0.20811 | -121.3621
1779.5938 | 122.0352 | -121.8155 | 0.14648 | 0.085224 | -0.095467 | -0.007421 | -0.066223 | 0.049999 | 0.030642 | -0.08103 | 0.13032 | 0.20742 | 0.05072 | -0.010206 | 0.25425 | 0.35284 | 121.4311 | 121.5473 | 121.9007 | 121.72 | 121.8081 | 121.7493 | 121.8655 | 121.8461 | 121.7345 | 0.15321 | 0.23031 | 0.073608 | 0.012682 | 0.27714 | 0.37573 | 121.454 | 121.5702 | -0.12393 | -121.3008 | -0.20353 | -121.3804
1781.3594 | 122.1451 | -121.8063 | 0.11902 | 0.080646 | -0.090888 | -0.012 | -0.061645 | 0.040843 | 0.030642 | -0.090186 | 0.12574 | 0.20284 | 0.055298 | -0.010206 | 0.24968 | 0.34826 | 121.4311 | 121.5611 | 121.887 | 121.7154 | 121.7943 | 121.7447 | 121.8472 | 121.837 | 121.7161 | 0.14863 | 0.22573 | 0.078186 | 0.012682 | 0.27256 | 0.37115 | 121.454 | 121.584 | -0.12393 | -121.3054 | -0.19438 | -121.3758
1783.0469 | 122.0078 | -121.8658 | 0.16479 | 0.076067 | -0.086309 | -0.007421 | -0.057066 | 0.036265 | 0.035221 | -0.08103 | 0.13032 | 0.20742 | 0.05072 | -0.010206 | 0.27257 | 0.36657 | 121.4403 | 121.5611 | 121.9419 | 121.7795 | 121.8584 | 121.8088 | 121.9021 | 121.9011 | 121.7848 | 0.15321 | 0.23031 | 0.073608 | 0.012682 | 0.29545 | 0.38946 | 121.4632 | 121.584 | -0.14224 | -121.31 | -0.22185 | -121.3896
1784.7812 | 122.0169 | -121.8613 | 0.14191 | 0.080646 | -0.08173 | -0.002842 | -0.061645 | 0.054577 | 0.026064 | -0.090186 | 0.13032 | 0.20284 | 0.046142 | -0.023943 | 0.2863 | 0.39862 | 121.4266 | 121.5611 | 121.9419 | 121.7795 | 121.8584 | 121.7996 | 121.9158 | 121.8873 | 121.7711 | 0.15321 | 0.22573 | 0.06903 | -0.001055 | 0.30919 | 0.42151 | 121.4495 | 121.584 | -0.15598 | -121.2962 | -0.24016 | -121.3804
1786.5469 | 122.1497 | -121.8292 | 0.12817 | 0.076067 | -0.090888 | 0.001736 | -0.066223 | 0.045421 | 0.030642 | -0.08103 | 0.13032 | 0.20284 | 0.05072 | -0.010206 | 0.31377 | 0.43982 | 121.4449 | 121.5702 | 121.9053 | 121.7383 | 121.831 | 121.763 | 121.8746 | 121.8599 | 121.7482 | 0.15321 | 0.22573 | 0.073608 | 0.012682 | 0.33666 | 0.46271 | 121.4678 | 121.5931 | -0.18345 | -121.3146 | -0.26305 | -121.3942
1788.25 | 122.0993 | -121.8338 | 0.1236 | 0.080646 | -0.095467 | -0.002842 | -0.061645 | 0.045421 | 0.026064 | -0.08103 | 0.1349 | 0.20742 | 0.046142 | -0.028522 | 0.34582 | 0.47187 | 121.4586 | 121.584 | 121.9144 | 121.7383 | 121.831 | 121.7722 | 121.8792 | 121.8599 | 121.7528 | 0.15779 | 0.23031 | 0.06903 | -0.005634 | 0.36871 | 0.49476 | 121.4815 | 121.6068 | -0.21092 | -121.3237 | -0.29967 | -121.4125
1789.9375 | 122.0032 | -121.8796 | 0.16479 | 0.089802 | -0.10004 | -0.007421 | -0.057066 | 0.054577 | 0.030642 | -0.085608 | 0.12574 | 0.19827 | 0.05072 | 0.00811 | 0.2863 | 0.39862 | 121.4586 | 121.5794 | 121.9694 | 121.7795 | 121.8722 | 121.8225 | 121.9342 | 121.9102 | 121.794 | 0.14863 | 0.22115 | 0.073608 | 0.030998 | 0.30919 | 0.42151 | 121.4815 | 121.6023 | -0.16056 | -121.3329 | -0.23558 | -121.4079
1791.6875 | 122.0581 | -121.8842 | 0.13733 | 0.080646 | -0.095467 | -0.002842 | -0.061645 | 0.049999 | 0.030642 | -0.094765 | 0.12574 | 0.20284 | 0.055298 | 0.003531 | 0.33666 | 0.46271 | 121.4586 | 121.5931 | 121.9648 | 121.7887 | 121.8813 | 121.8225 | 121.9342 | 121.9148 | 121.7894 | 0.14863 | 0.22573 | 0.078186 | 0.026419 | 0.35955 | 0.4856 | 121.4815 | 121.616 | -0.21092 | -121.3329 | -0.28136 | -121.4033
1793.4375 | 122.1176 | -121.875 | 0.13275 | 0.080646 | -0.086309 | -0.002842 | -0.066223 | 0.040843 | 0.021485 | -0.090186 | 0.13032 | 0.20284 | 0.05072 | -0.023943 | 0.2863 | 0.39862 | 121.4678 | 121.5931 | 121.9556 | 121.7887 | 121.8722 | 121.8088 | 121.9158 | 121.8965 | 121.7848 | 0.15321 | 0.22573 | 0.073608 | -0.001055 | 0.30919 | 0.42151 | 121.4907 | 121.616 | -0.15598 | -121.3375 | -0.23558 | -121.4171
1795.125 | 122.1817 | -121.843 | 0.10529 | 0.080646 | -0.090888 | 0.001736 | -0.057066 | 0.040843 | 0.030642 | -0.094765 | 0.12574 | 0.20284 | 0.05072 | -0.001048 | 0.25883 | 0.35284 | 121.4769 | 121.6023 | 121.9236 | 121.7521 | 121.8447 | 121.7859 | 121.8838 | 121.8736 | 121.7482 | 0.14863 | 0.22573 | 0.073608 | 0.02184 | 0.28172 | 0.37573 | 121.4998 | 121.6252 | -0.13309 | -121.3512 | -0.20811 | -121.4262
1796.875 | 122.168 | -121.8613 | 0.1236 | 0.080646 | -0.090888 | -0.002842 | -0.057066 | 0.040843 | 0.030642 | -0.090186 | 0.12574 | 0.20742 | 0.05072 | -0.046838 | 0.3504 | 0.47645 | 121.4907 | 121.6114 | 121.9419 | 121.7704 | 121.8584 | 121.8042 | 121.9021 | 121.8919 | 121.7711 | 0.14863 | 0.23031 | 0.073608 | -0.02395 | 0.37328 | 0.49934 | 121.5136 | 121.6343 | -0.22465 | -121.3649 | -0.29968 | -121.4399
1798.5625 | 122.1085 | -121.8475 | 0.15564 | 0.085224 | -0.090888 | -0.016578 | -0.061645 | 0.045421 | 0.026064 | -0.090186 | 0.13032 | 0.20284 | 0.05072 | -0.023943 | 0.31835 | 0.43067 | 121.4952 | 121.6114 | 121.9328 | 121.7566 | 121.831 | 121.7859 | 121.893 | 121.8736 | 121.7573 | 0.15321 | 0.22573 | 0.073608 | -0.001055 | 0.34124 | 0.45356 | 121.5181 | 121.6343 | -0.18803 | -121.3649 | -0.26763 | -121.4445
1800.3125 | 122.0901 | -121.9025 | 0.15564 | 0.076067 | -0.10004 | -0.012 | -0.061645 | 0.040843 | 0.030642 | -0.094765 | 0.12574 | 0.19827 | 0.05072 | -0.023943 | 0.41449 | 0.55885 | 121.4952 | 121.6206 | 121.9785 | 121.8024 | 121.8905 | 121.8408 | 121.9433 | 121.9331 | 121.8077 | 0.14863 | 0.22115 | 0.073608 | -0.001055 | 0.43738 | 0.58174 | 121.5181 | 121.6435 | -0.28875 | -121.3695 | -0.36377 | -121.4445
1802 | 122.081 | -121.9162 | 0.14648 | 0.089802 | -0.095467 | -0.016578 | -0.066223 | 0.045421 | 0.030642 | -0.085608 | 0.12574 | 0.20284 | 0.046142 | 0.003531 | 0.27714 | 0.38489 | 121.4907 | 121.6206 | 122.006 | 121.8207 | 121.8996 | 121.85 | 121.9616 | 121.9468 | 121.8306 | 0.14863 | 0.22573 | 0.06903 | 0.026419 | 0.30003 | 0.40777 | 121.5136 | 121.6435 | -0.1514 | -121.3649 | -0.231 | -121.4445
1803.75 | 122.1771 | -121.8933 | 0.1236 | 0.080646 | -0.095467 | -0.012 | -0.061645 | 0.045421 | 0.021485 | -0.090186 | 0.12574 | 0.19827 | 0.046142 | 0.017268 | 0.5381 | 0.65957 | 121.4998 | 121.6252 | 121.974 | 121.7978 | 121.8813 | 121.8317 | 121.9387 | 121.9148 | 121.8031 | 0.14863 | 0.22115 | 0.06903 | 0.040156 | 0.56099 | 0.68246 | 121.5227 | 121.648 | -0.41236 | -121.3741 | -0.49196 | -121.4537
1805.4531 | 122.1817 | -121.8933 | 0.12817 | 0.071489 | -0.095467 | -0.012 | -0.061645 | 0.040843 | 0.026064 | -0.090186 | 0.12574 | 0.20284 | 0.055298 | -0.023943 | 0.95929 | 1.0808 | 121.509 | 121.6297 | 121.9648 | 121.7978 | 121.8813 | 121.8317 | 121.9342 | 121.9194 | 121.8031 | 0.14863 | 0.22573 | 0.078186 | -0.001055 | 0.98218 | 1.1036 | 121.5319 | 121.6526 | -0.83355 | -121.3832 | -0.90399 | -121.4537
1807.2188 | 122.1634 | -121.907 | 0.13275 | 0.080646 | -0.095467 | -0.012 | -0.061645 | 0.045421 | 0.016907 | -0.090186 | 0.13032 | 0.19369 | 0.046142 | 0.012689 | 0.90893 | 1.0441 | 121.509 | 121.648 | 121.9877 | 121.8116 | 121.895 | 121.8454 | 121.9525 | 121.924 | 121.8169 | 0.15321 | 0.21658 | 0.06903 | 0.035577 | 0.93182 | 1.067 | 121.5319 | 121.6709 | -0.77861 | -121.3787 | -0.86279 | -121.4628
1808.9688 | 122.2046 | -121.8933 | 0.11902 | 0.085224 | -0.090888 | -0.007421 | -0.066223 | 0.045421 | 0.030642 | -0.099343 | 0.11659 | 0.20284 | 0.046142 | -0.005627 | 0.90893 | 1.0396 | 121.509 | 121.648 | 121.9785 | 121.8024 | 121.8859 | 121.8271 | 121.9387 | 121.924 | 121.794 | 0.13947 | 0.22573 | 0.06903 | 0.017261 | 0.93182 | 1.0624 | 121.5319 | 121.6709 | -0.79234 | -121.3924 | -0.86279 | -121.4628
1810.6562 | 122.0947 | -121.9391 | 0.14191 | 0.076067 | -0.095467 | -0.021157 | -0.070802 | 0.045421 | 0.026064 | -0.085608 | 0.12116 | 0.19827 | 0.046142 | -0.014785 | 1.0051 | 1.1311 | 121.5227 | 121.648 | 122.0152 | 121.8436 | 121.9179 | 121.8683 | 121.9845 | 121.9652 | 121.8535 | 0.14405 | 0.22115 | 0.06903 | 0.008103 | 1.028 | 1.154 | 121.5456 | 121.6709 | -0.88391 | -121.4015 | -0.95893 | -121.4766
1812.4219 | 122.1725 | -121.9025 | 0.1236 | 0.085224 | -0.10004 | -0.012 | -0.061645 | 0.036265 | 0.026064 | -0.094765 | 0.12116 | 0.20284 | 0.046142 | -0.088049 | 1.0051 | 1.1311 | 121.5181 | 121.6435 | 121.9877 | 121.8024 | 121.8905 | 121.8408 | 121.9387 | 121.9285 | 121.8077 | 0.14405 | 0.22573 | 0.06903 | -0.065161 | 1.028 | 1.154 | 121.541 | 121.6664 | -0.88391 | -121.397 | -0.95893 | -121.472
1814.1719 | 122.2046 | -121.8933 | 0.09613 | 0.080646 | -0.095467 | -0.016578 | -0.070802 | 0.045421 | 0.016907 | -0.094765 | 0.12574 | 0.20284 | 0.036985 | -0.019364 | 1.0783 | 1.2135 | 121.5273 | 121.6526 | 121.974 | 121.7978 | 121.8767 | 121.8225 | 121.9387 | 121.9102 | 121.7985 | 0.14863 | 0.22573 | 0.059873 | 0.003524 | 1.1012 | 1.2364 | 121.5502 | 121.6755 | -0.95258 | -121.4015 | -1.0413 | -121.4903
1815.9219 | 122.0718 | -121.9254 | 0.15564 | 0.085224 | -0.10004 | -0.021157 | -0.066223 | 0.040843 | 0.021485 | -0.090186 | 0.13032 | 0.19827 | 0.05072 | -0.065154 | 1.115 | 1.2456 | 121.5319 | 121.6618 | 122.0106 | 121.8253 | 121.9042 | 121.8591 | 121.9662 | 121.9468 | 121.8352 | 0.15321 | 0.22115 | 0.073608 | -0.042266 | 1.1378 | 1.2685 | 121.5548 | 121.6847 | -0.98463 | -121.4015 | -1.0642 | -121.4811
1817.625 | 122.0856 | -121.9482 | 0.15564 | 0.080646 | -0.10462 | -0.016578 | -0.07538 | 0.036265 | 0.016907 | -0.090186 | 0.12116 | 0.19827 | 0.046142 | -0.023943 | 1.2248 | 1.3554 | 121.5319 | 121.6664 | 122.0289 | 121.8436 | 121.9317 | 121.8729 | 121.9845 | 121.9651 | 121.8581 | 0.14405 | 0.22115 | 0.06903 | -0.001055 | 1.2477 | 1.3783 | 121.5548 | 121.6892 | -1.1037 | -121.4107 | -1.1787 | -121.4857
1819.375 | 122.2 | -121.9254 | 0.11444 | 0.085224 | -0.095467 | -0.016578 | -0.070802 | 0.045421 | 0.026064 | -0.094765 | 0.12574 | 0.19369 | 0.046142 | -0.028522 | 1.2615 | 1.3966 | 121.5364 | 121.6664 | 122.0106 | 121.8299 | 121.9088 | 121.8546 | 121.9708 | 121.9514 | 121.8306 | 0.14863 | 0.21658 | 0.06903 | -0.005634 | 1.2843 | 1.4195 | 121.5593 | 121.6892 | -1.1357 | -121.4107 | -1.2153 | -121.4903
1821.0781 | 122.2412 | -121.907 | 0.11444 | 0.080646 | -0.11378 | -0.016578 | -0.066223 | 0.040843 | 0.016907 | -0.094765 | 0.12574 | 0.19827 | 0.046142 | 0.003531 | 1.1653 | 1.2868 | 121.5502 | 121.6847 | 121.9877 | 121.7933 | 121.8905 | 121.8408 | 121.9479 | 121.924 | 121.8123 | 0.14863 | 0.22115 | 0.06903 | 0.026419 | 1.1882 | 1.3097 | 121.5731 | 121.7076 | -1.0396 | -121.4244 | -1.1192 | -121.504
1822.8281 | 122.2549 | -121.9208 | 0.12817 | 0.085224 | -0.10462 | -0.021157 | -0.07538 | 0.031687 | 0.016907 | -0.094765 | 0.12116 | 0.19827 | 0.05072 | -0.03768 | 1.2706 | 1.4012 | 121.5502 | 121.6755 | 122.006 | 121.8162 | 121.8996 | 121.8454 | 121.9525 | 121.9377 | 121.826 | 0.14405 | 0.22115 | 0.073608 | -0.014792 | 1.2935 | 1.4241 | 121.5731 | 121.6984 | -1.1494 | -121.429 | -1.2199 | -121.4995
1824.5938 | 122.2046 | -121.9437 | 0.11902 | 0.080646 | -0.1092 | -0.021157 | -0.070802 | 0.036265 | 0.012329 | -0.099343 | 0.12574 | 0.19827 | 0.041563 | -0.051417 | 1.5178 | 1.653 | 121.5593 | 121.6801 | 122.0243 | 121.8345 | 121.9225 | 121.8729 | 121.9799 | 121.956 | 121.8443 | 0.14863 | 0.22115 | 0.064451 | -0.028529 | 1.5407 | 1.6759 | 121.5822 | 121.703 | -1.3921 | -121.4336 | -1.4763 | -121.5178
1826.2969 | 122.1497 | -121.9711 | 0.14648 | 0.085224 | -0.095467 | -0.025735 | -0.079959 | 0.036265 | 0.016907 | -0.090186 | 0.12574 | 0.19827 | 0.041563 | -0.033101 | 1.7284 | 1.859 | 121.5593 | 121.6938 | 122.0564 | 121.8757 | 121.9454 | 121.8912 | 122.0074 | 121.988 | 121.8809 | 0.14863 | 0.22115 | 0.064451 | -0.010213 | 1.7513 | 1.8819 | 121.5822 | 121.7167 | -1.6027 | -121.4336 | -1.6869 | -121.5178
1829.4688 | 122.2687 | -121.9254 | 0.12817 | 0.085224 | -0.10462 | -0.012 | -0.07538 | 0.027109 | 0.021485 | -0.099343 | 0.13032 | 0.19827 | 0.046142 | -0.060575 | 1.6781 | 1.8132 | 121.5685 | 121.6984 | 122.0106 | 121.8207 | 121.9134 | 121.85 | 121.9525 | 121.9468 | 121.826 | 0.15321 | 0.22115 | 0.06903 | -0.037687 | 1.701 | 1.8361 | 121.5914 | 121.7213 | -1.5477 | -121.4382 | -1.6319 | -121.5224
1833.4531 | 122.2458 | -121.962 | 0.1236 | 0.085224 | -0.11378 | -0.030314 | -0.070802 | 0.031687 | 0.016907 | -0.099343 | 0.12574 | 0.19827 | 0.036985 | -0.028522 | 1.7422 | 1.8773 | 121.5639 | 121.6984 | 122.0472 | 121.8482 | 121.9317 | 121.8912 | 121.9937 | 121.9789 | 121.8626 | 0.14863 | 0.22115 | 0.059873 | -0.005634 | 1.765 | 1.9002 | 121.5868 | 121.7213 | -1.6164 | -121.4382 | -1.7052 | -121.5269
1839.6406 | 122.1634 | -122.0032 | 0.16937 | 0.080646 | -0.1092 | -0.025735 | -0.07538 | 0.031687 | 0.016907 | -0.094765 | 0.12574 | 0.19827 | 0.05072 | -0.010206 | 1.6643 | 1.7904 | 121.596 | 121.7259 | 122.0838 | 121.894 | 121.9774 | 121.9278 | 122.0349 | 122.0201 | 121.9084 | 0.14863 | 0.22115 | 0.073608 | 0.012682 | 1.6872 | 1.8132 | 121.6189 | 121.7488 | -1.5386 | -121.4702 | -1.6136 | -121.5452
1841.4844 | 122.1588 | -121.994 | 0.1236 | 0.080646 | -0.11378 | -0.021157 | -0.07538 | 0.031687 | 0.016907 | -0.094765 | 0.12116 | 0.19827 | 0.041563 | -0.010206 | 1.6231 | 1.7492 | 121.5914 | 121.7213 | 122.0747 | 121.8802 | 121.9729 | 121.9186 | 122.0257 | 122.0109 | 121.8993 | 0.14405 | 0.22115 | 0.064451 | 0.012682 | 1.646 | 1.772 | 121.6143 | 121.7442 | -1.502 | -121.4702 | -1.5816 | -121.5498
1843.1875 | 122.1771 | -122.0169 | 0.14648 | 0.085224 | -0.1092 | -0.025735 | -0.084537 | 0.027109 | 0.012329 | -0.10392 | 0.12116 | 0.19827 | 0.046142 | -0.028522 | 1.6048 | 1.7263 | 121.6051 | 121.735 | 122.1021 | 121.9077 | 121.9912 | 121.9324 | 122.044 | 122.0292 | 121.913 | 0.14405 | 0.22115 | 0.06903 | -0.005634 | 1.6277 | 1.7491 | 121.628 | 121.7579 | -1.4837 | -121.484 | -1.5587 | -121.559
1844.9375 | 122.2092 | -122.0261 | 0.16022 | 0.080646 | -0.11836 | -0.021157 | -0.07538 | 0.022531 | 0.012329 | -0.1085 | 0.12116 | 0.19369 | 0.05072 | -0.019364 | 1.5316 | 1.6667 | 121.6097 | 121.7396 | 122.1067 | 121.9077 | 122.0049 | 121.9507 | 122.0486 | 122.0384 | 121.9176 | 0.14405 | 0.21658 | 0.073608 | 0.003524 | 1.5545 | 1.6896 | 121.6326 | 121.7625 | -1.4104 | -121.4885 | -1.4808 | -121.559
1846.7031 | 122.2595 | -121.9894 | 0.1236 | 0.080646 | -0.11378 | -0.025735 | -0.07538 | 0.022531 | 0.00775 | -0.099343 | 0.12574 | 0.19369 | 0.05072 | -0.028522 | 1.5407 | 1.6759 | 121.6005 | 121.7396 | 122.0701 | 121.8757 | 121.9637 | 121.9141 | 122.012 | 121.9972 | 121.8901 | 0.14863 | 0.21658 | 0.073608 | -0.005634 | 1.5636 | 1.6988 | 121.6234 | 121.7625 | -1.415 | -121.4748 | -1.49 | -121.5498
1848.4688 | 122.2046 | -122.0078 | 0.13733 | 0.085224 | -0.11378 | -0.030314 | -0.079959 | 0.031687 | 0.016907 | -0.099343 | 0.12116 | 0.19827 | 0.041563 | -0.046838 | 1.6506 | 1.772 | 121.6097 | 121.7533 | 122.093 | 121.894 | 121.9774 | 121.9278 | 122.0394 | 122.0247 | 121.9084 | 0.14405 | 0.22115 | 0.064451 | -0.02395 | 1.6735 | 1.7949 | 121.6326 | 121.7762 | -1.5294 | -121.4885 | -1.609 | -121.5681
1850.1562 | 122.168 | -122.0352 | 0.14191 | 0.085224 | -0.11836 | -0.030314 | -0.079959 | 0.022531 | 0.012329 | -0.10392 | 0.11201 | 0.19827 | 0.041563 | -0.03768 | 1.6185 | 1.7583 | 121.6189 | 121.7488 | 122.1204 | 121.9169 | 122.0049 | 121.9553 | 122.0577 | 122.0475 | 121.9313 | 0.1349 | 0.22115 | 0.064451 | -0.014792 | 1.6414 | 1.7812 | 121.6417 | 121.7717 | -1.5065 | -121.5069 | -1.577 | -121.5773
1851.8438 | 122.2321 | -122.0398 | 0.16022 | 0.06691 | -0.11378 | -0.025735 | -0.079959 | 0.022531 | 0.016907 | -0.10392 | 0.12116 | 0.19369 | 0.041563 | -0.060575 | 1.646 | 1.7766 | 121.6189 | 121.7579 | 122.1067 | 121.926 | 122.0141 | 121.9598 | 122.0623 | 122.0567 | 121.9359 | 0.14405 | 0.21658 | 0.064451 | -0.037687 | 1.6689 | 1.7995 | 121.6417 | 121.7808 | -1.5249 | -121.4977 | -1.6045 | -121.5773
1853.5938 | 122.2641 | -122.0078 | 0.13275 | 0.085224 | -0.11836 | -0.034893 | -0.079959 | 0.022531 | 0.012329 | -0.1085 | 0.11659 | 0.19827 | 0.046142 | -0.028522 | 1.6552 | 1.7904 | 121.6234 | 121.7488 | 122.093 | 121.8894 | 121.9729 | 121.9278 | 122.0303 | 122.0201 | 121.8993 | 0.13947 | 0.22115 | 0.06903 | -0.005634 | 1.6781 | 1.8132 | 121.6463 | 121.7717 | -1.5386 | -121.5069 | -1.609 | -121.5773
1855.2812 | 122.287 | -121.994 | 0.12817 | 0.085224 | -0.11378 | -0.034893 | -0.084537 | 0.022531 | 0.00775 | -0.10392 | 0.11659 | 0.18911 | 0.041563 | -0.019364 | 1.5545 | 1.6896 | 121.628 | 121.7579 | 122.0792 | 121.8802 | 121.9591 | 121.9095 | 122.0165 | 122.0018 | 121.8901 | 0.13947 | 0.212 | 0.064451 | 0.003524 | 1.5773 | 1.7125 | 121.6509 | 121.7808 | -1.4379 | -121.5114 | -1.5129 | -121.5865
1857.0312 | 122.3373 | -122.0306 | 0.11444 | 0.080646 | -0.11378 | -0.034893 | -0.079959 | 0.022531 | 0.00775 | -0.10392 | 0.12574 | 0.20284 | 0.05072 | -0.051417 | 1.5682 | 1.6988 | 121.6326 | 121.7625 | 122.1113 | 121.9169 | 121.9957 | 121.9507 | 122.0532 | 122.0384 | 121.9267 | 0.14863 | 0.22573 | 0.073608 | -0.028529 | 1.5911 | 1.7217 | 121.6555 | 121.7854 | -1.4424 | -121.5069 | -1.5175 | -121.5819
1858.7969 | 122.3282 | -122.0718 | 0.11902 | 0.085224 | -0.11836 | -0.034893 | -0.084537 | 0.013375 | 0.00775 | -0.099343 | 0.11659 | 0.18911 | 0.041563 | -0.042259 | 1.5041 | 1.6347 | 121.8844 | 121.9777 | 122.1571 | 121.9535 | 122.0369 | 121.9873 | 122.0852 | 122.0796 | 121.9725 | 0.13947 | 0.212 | 0.064451 | -0.019371 | 1.527 | 1.6576 | 121.9073 | 122.0006 | -1.3875 | -121.7678 | -1.4625 | -121.8428
1860.5625 | 122.3053 | -122.0764 | 0.1236 | 0.080646 | -0.11836 | -0.030314 | -0.084537 | 0.022531 | 0.00775 | -0.11308 | 0.11659 | 0.19369 | 0.041563 | -0.028522 | 1.472 | 1.6027 | 121.6509 | 121.7808 | 122.1571 | 121.9581 | 122.0461 | 121.9919 | 122.0989 | 122.0842 | 121.9633 | 0.13947 | 0.21658 | 0.064451 | -0.005634 | 1.4949 | 1.6255 | 121.6738 | 121.8037 | -1.3555 | -121.5343 | -1.4305 | -121.6093
1862.2656 | 122.3099 | -122.0306 | 0.11902 | 0.080646 | -0.11378 | -0.030314 | -0.089116 | 0.017953 | 0.00775 | -0.1085 | 0.11659 | 0.19369 | 0.036985 | -0.014785 | 1.4904 | 1.6118 | 121.6555 | 121.7945 | 122.1113 | 121.9169 | 122.0003 | 121.9415 | 122.0486 | 122.0384 | 121.9221 | 0.13947 | 0.21658 | 0.059873 | 0.008103 | 1.5132 | 1.6347 | 121.6784 | 121.8174 | -1.3738 | -121.5389 | -1.4534 | -121.6185
1864.0156 | 122.3511 | -122.0306 | 0.10986 | 0.085224 | -0.11836 | -0.039471 | -0.089116 | 0.017953 | 0.003172 | -0.11308 | 0.11201 | 0.19369 | 0.036985 | -0.055996 | 1.5728 | 1.6988 | 121.6646 | 121.7945 | 122.1159 | 121.9123 | 121.9912 | 121.9415 | 122.0486 | 122.0338 | 121.9176 | 0.1349 | 0.21658 | 0.059873 | -0.033108 | 1.5957 | 1.7217 | 121.6875 | 121.8174 | -1.4608 | -121.5526 | -1.5358 | -121.6277
1865.7031 | 122.3007 | -122.0764 | 0.11902 | 0.080646 | -0.12294 | -0.030314 | -0.089116 | 0.017953 | -0.001406 | -0.11308 | 0.11659 | 0.19369 | 0.041563 | -0.023943 | 1.5133 | 1.6439 | 121.6692 | 121.8037 | 122.1571 | 121.9535 | 122.0461 | 121.9873 | 122.0944 | 122.075 | 121.9633 | 0.13947 | 0.21658 | 0.064451 | -0.001055 | 1.5361 | 1.6667 | 121.6921 | 121.8266 | -1.3967 | -121.5526 | -1.4717 | -121.6277
1867.4688 | 122.2412 | -122.0993 | 0.15106 | 0.080646 | -0.12294 | -0.034893 | -0.084537 | 0.022531 | -0.001406 | -0.11308 | 0.10743 | 0.18911 | 0.041563 | -0.046838 | 1.4812 | 1.6027 | 121.683 | 121.8083 | 122.18 | 121.9764 | 122.0644 | 122.0148 | 122.1218 | 122.0979 | 121.9862 | 0.13032 | 0.212 | 0.064451 | -0.02395 | 1.5041 | 1.6255 | 121.7058 | 121.8312 | -1.3738 | -121.5755 | -1.4396 | -121.6414
1869.1719 | 122.3145 | -122.0352 | 0.1236 | 0.076067 | -0.12752 | -0.04405 | -0.093694 | 0.013375 | -0.001406 | -0.11308 | 0.11201 | 0.19369 | 0.036985 | -0.060575 | 1.4583 | 1.5889 | 121.683 | 121.8083 | 122.1113 | 121.9077 | 121.9912 | 121.9415 | 122.0486 | 122.0338 | 121.9221 | 0.1349 | 0.21658 | 0.059873 | -0.037687 | 1.4812 | 1.6118 | 121.7058 | 121.8312 | -1.3463 | -121.5709 | -1.4213 | -121.646
1870.9219 | 122.2412 | -122.0764 | 0.14648 | 0.085224 | -0.11836 | -0.034893 | -0.089116 | 0.013375 | -0.001406 | -0.11308 | 0.11659 | 0.19369 | 0.036985 | -0.08347 | 1.4217 | 1.566 | 121.6921 | 121.822 | 122.1616 | 121.9581 | 122.0415 | 121.9873 | 122.0898 | 122.075 | 121.9633 | 0.13947 | 0.21658 | 0.059873 | -0.060582 | 1.4446 | 1.5889 | 121.715 | 121.8449 | -1.3051 | -121.5755 | -1.3847 | -121.6551
1872.625 | 122.3694 | -122.0581 | 0.13275 | 0.080646 | -0.1321 | -0.039471 | -0.093694 | 0.013375 | -0.005985 | -0.1085 | 0.11659 | 0.19369 | 0.046142 | -0.023943 | 1.44 | 1.5752 | 121.6967 | 121.822 | 122.1388 | 121.926 | 122.0186 | 121.9644 | 122.0715 | 122.0521 | 121.9496 | 0.13947 | 0.21658 | 0.06903 | -0.001055 | 1.4629 | 1.5981 | 121.7196 | 121.8449 | -1.3234 | -121.5801 | -1.3939 | -121.6505
1874.3906 | 122.3557 | -122.0856 | 0.11902 | 0.080646 | -0.12294 | -0.039471 | -0.093694 | 0.008797 | 0.003172 | -0.11308 | 0.10743 | 0.19827 | 0.046142 | -0.065154 | 1.472 | 1.6027 | 121.6921 | 121.8266 | 122.1662 | 121.9626 | 122.0461 | 121.9919 | 122.0944 | 122.0887 | 121.9725 | 0.13032 | 0.22115 | 0.06903 | -0.042266 | 1.4949 | 1.6255 | 121.715 | 121.8495 | -1.3646 | -121.5847 | -1.4259 | -121.646
1876.1562 | 122.2641 | -122.0764 | 0.16937 | 0.080646 | -0.1321 | -0.039471 | -0.084537 | 0.008797 | -0.015142 | -0.11308 | 0.11201 | 0.19369 | 0.041563 | -0.028522 | 1.4583 | 1.5798 | 121.7013 | 121.8266 | 122.1571 | 121.9443 | 122.0369 | 121.9919 | 122.0852 | 122.0613 | 121.9633 | 0.1349 | 0.21658 | 0.064451 | -0.005634 | 1.4812 | 1.6027 | 121.7242 | 121.8495 | -1.3463 | -121.5893 | -1.4167 | -121.6597
1877.9219 | 122.4014 | -122.0627 | 0.11902 | 0.085224 | -0.13668 | -0.048628 | -0.098273 | 0.008797 | -0.001406 | -0.12681 | 0.12116 | 0.19369 | 0.046142 | -0.014785 | 1.4675 | 1.5889 | 121.7058 | 121.8403 | 122.1479 | 121.926 | 122.0141 | 121.9644 | 122.0715 | 122.0613 | 121.9359 | 0.14405 | 0.21658 | 0.06903 | 0.008103 | 1.4904 | 1.6118 | 121.7287 | 121.8632 | -1.3463 | -121.5847 | -1.4213 | -121.6597
1879.6875 | 122.4014 | -122.0627 | 0.10529 | 0.076067 | -0.13668 | -0.048628 | -0.098273 | 0.008797 | -0.005985 | -0.11765 | 0.11659 | 0.19369 | 0.041563 | -0.014785 | 1.3896 | 1.5248 | 121.7058 | 121.8403 | 122.1388 | 121.926 | 122.0141 | 121.9644 | 122.0715 | 122.0567 | 121.945 | 0.13947 | 0.21658 | 0.064451 | 0.008103 | 1.4125 | 1.5477 | 121.7287 | 121.8632 | -1.2731 | -121.5893 | -1.3481 | -121.6643
1881.4375 | 122.3785 | -122.0673 | 0.15106 | 0.085224 | -0.14125 | -0.053207 | -0.089116 | 0.004219 | -0.005985 | -0.11765 | 0.11201 | 0.18911 | 0.041563 | -0.046838 | 1.408 | 1.5431 | 121.7196 | 121.8541 | 122.1525 | 121.926 | 122.0141 | 121.9781 | 122.0715 | 122.0613 | 121.9496 | 0.1349 | 0.212 | 0.064451 | -0.02395 | 1.4308 | 1.566 | 121.7425 | 121.877 | -1.2959 | -121.6076 | -1.3664 | -121.678
1883.1406 | 122.4014 | -122.081 | 0.1236 | 0.080646 | -0.13668 | -0.048628 | -0.098273 | -0.000359 | -0.005985 | -0.12681 | 0.11201 | 0.18911 | 0.041563 | -0.001048 | 1.5178 | 1.6576 | 121.715 | 121.8495 | 122.1616 | 121.9443 | 122.0324 | 121.9827 | 122.0806 | 122.075 | 121.9542 | 0.1349 | 0.212 | 0.064451 | 0.02184 | 1.5407 | 1.6805 | 121.7379 | 121.8724 | -1.4058 | -121.603 | -1.4763 | -121.6734
1884.8906 | 122.3785 | -122.0947 | 0.11902 | 0.071489 | -0.14125 | -0.053207 | -0.10285 | -0.000359 | -0.010563 | -0.12223 | 0.10743 | 0.18911 | 0.041563 | -0.033101 | 1.5499 | 1.6805 | 121.7242 | 121.8586 | 122.1662 | 121.9535 | 122.0415 | 121.9919 | 122.0944 | 122.0842 | 121.9725 | 0.13032 | 0.212 | 0.064451 | -0.010213 | 1.5728 | 1.7034 | 121.7471 | 121.8815 | -1.4424 | -121.6167 | -1.5083 | -121.6826
1886.5781 | 122.4152 | -122.1222 | 0.1236 | 0.076067 | -0.13668 | -0.053207 | -0.10285 | 0.004219 | -0.015142 | -0.13597 | 0.11201 | 0.19827 | 0.046142 | -0.042259 | 1.4492 | 1.5843 | 121.7287 | 121.8541 | 122.1983 | 121.9855 | 122.069 | 122.0193 | 122.1264 | 122.1071 | 121.9862 | 0.1349 | 0.22115 | 0.06903 | -0.019371 | 1.472 | 1.6072 | 121.7516 | 121.877 | -1.3371 | -121.6167 | -1.403 | -121.6826
1888.2656 | 122.3236 | -122.1222 | 0.14191 | 0.080646 | -0.14583 | -0.053207 | -0.098273 | 0.004219 | -0.005985 | -0.12681 | 0.11201 | 0.19369 | 0.041563 | -0.028522 | 1.4492 | 1.5843 | 121.7333 | 121.8632 | 122.2028 | 121.9764 | 122.069 | 122.0239 | 122.1264 | 122.1162 | 121.9954 | 0.1349 | 0.21658 | 0.064451 | -0.005634 | 1.472 | 1.6072 | 121.7562 | 121.8861 | -1.3371 | -121.6213 | -1.4076 | -121.6918
1890.0312 | 122.3465 | -122.1313 | 0.13733 | 0.080646 | -0.14125 | -0.053207 | -0.098273 | -0.004937 | -0.010563 | -0.12681 | 0.11659 | 0.17995 | 0.036985 | -0.033101 | 1.5224 | 1.6484 | 121.7379 | 121.8724 | 122.212 | 121.9901 | 122.0781 | 122.0331 | 122.1264 | 122.1208 | 122.0045 | 0.13947 | 0.20284 | 0.059873 | -0.010213 | 1.5453 | 1.6713 | 121.7608 | 121.8953 | -1.4058 | -121.6213 | -1.4854 | -121.7009
1891.7969 | 122.4655 | -122.1039 | 0.10529 | 0.085224 | -0.14583 | -0.057786 | -0.10743 | -0.004937 | -0.024298 | -0.13139 | 0.11659 | 0.18911 | 0.036985 | -0.055996 | 1.5133 | 1.6439 | 121.7379 | 121.8678 | 122.1891 | 121.958 | 122.0461 | 121.9965 | 122.0989 | 122.0796 | 121.9725 | 0.13947 | 0.212 | 0.059873 | -0.033108 | 1.5361 | 1.6667 | 121.7608 | 121.8907 | -1.3967 | -121.6213 | -1.4763 | -121.7009
1893.5469 | 122.3785 | -122.1268 | 0.1236 | 0.080646 | -0.14125 | -0.062364 | -0.10743 | -0.004937 | -0.024298 | -0.12681 | 0.10743 | 0.19369 | 0.036985 | -0.051417 | 1.5178 | 1.6484 | 121.7471 | 121.8724 | 122.2074 | 121.9855 | 122.0644 | 122.0193 | 122.1218 | 122.1025 | 122 | 0.13032 | 0.21658 | 0.059873 | -0.028529 | 1.5407 | 1.6713 | 121.7699 | 121.8953 | -1.4104 | -121.6396 | -1.4808 | -121.7101
1895.25 | 122.438 | -122.1222 | 0.10986 | 0.080646 | -0.15041 | -0.057786 | -0.10285 | -0.009515 | -0.028877 | -0.13139 | 0.10285 | 0.19369 | 0.036985 | -0.065154 | 1.5178 | 1.6576 | 121.7471 | 121.877 | 122.2028 | 121.9718 | 122.0644 | 122.0193 | 122.1127 | 122.0933 | 121.9908 | 0.12574 | 0.21658 | 0.059873 | -0.042266 | 1.5407 | 1.6805 | 121.7699 | 121.8998 | -1.415 | -121.6442 | -1.4808 | -121.7101
1897 | 122.3373 | -122.1817 | 0.15106 | 0.089802 | -0.15499 | -0.071521 | -0.10743 | -0.009515 | -0.024298 | -0.13139 | 0.11659 | 0.18453 | 0.036985 | -0.010206 | 1.5041 | 1.6347 | 121.7562 | 121.8861 | 122.2715 | 122.0267 | 122.1102 | 122.0743 | 122.1722 | 122.1574 | 122.0503 | 0.13947 | 0.20742 | 0.059873 | 0.012682 | 1.527 | 1.6576 | 121.7791 | 121.909 | -1.3875 | -121.6396 | -1.4671 | -121.7192
1898.6875 | 122.3785 | -122.1359 | 0.14191 | 0.076067 | -0.15499 | -0.057786 | -0.11659 | -0.004937 | -0.024298 | -0.13597 | 0.10743 | 0.18453 | 0.041563 | -0.042259 | 1.4171 | 1.5477 | 121.7608 | 121.8907 | 122.212 | 121.9809 | 122.0781 | 122.0193 | 122.131 | 122.1116 | 122 | 0.13032 | 0.20742 | 0.064451 | -0.019371 | 1.44 | 1.5706 | 121.7837 | 121.9136 | -1.3097 | -121.6534 | -1.3755 | -121.7192
1900.4375 | 122.3648 | -122.1588 | 0.15106 | 0.076067 | -0.15041 | -0.062364 | -0.10743 | -0.004937 | -0.01972 | -0.13597 | 0.11201 | 0.18911 | 0.046142 | -0.028522 | 1.3805 | 1.5111 | 121.7654 | 121.9044 | 122.2349 | 122.0084 | 122.0964 | 122.0514 | 122.1539 | 122.1391 | 122.0228 | 0.1349 | 0.212 | 0.06903 | -0.005634 | 1.4034 | 1.534 | 121.7883 | 121.9273 | -1.2685 | -121.6534 | -1.3343 | -121.7192
1902.1562 | 122.4335 | -122.1313 | 0.11902 | 0.085224 | -0.14583 | -0.066943 | -0.11201 | -0.009515 | -0.01972 | -0.14512 | 0.11201 | 0.19369 | 0.036985 | -0.046838 | 1.3896 | 1.5111 | 121.7654 | 121.8998 | 122.2166 | 121.9855 | 122.0644 | 122.0193 | 122.1218 | 122.1116 | 121.9862 | 0.1349 | 0.21658 | 0.059873 | -0.02395 | 1.4125 | 1.534 | 121.7883 | 121.9227 | -1.2776 | -121.6534 | -1.3527 | -121.7284
1903.875 | 122.3511 | -122.168 | 0.14191 | -0.001765 | -0.14583 | -0.057786 | -0.098273 | -0.000359 | -0.015142 | -0.13139 | 0.11201 | 0.19369 | 0.041563 | -0.078891 | 1.3667 | 1.4882 | 121.7699 | 121.8998 | 122.1662 | 122.0221 | 122.1102 | 122.0697 | 122.1676 | 122.1528 | 122.0366 | 0.1349 | 0.21658 | 0.064451 | -0.056003 | 1.3896 | 1.5111 | 121.7928 | 121.9227 | -1.2547 | -121.6579 | -1.3252 | -121.7284
1905.6406 | 122.3236 | -122.168 | 0.15106 | 0.002813 | -0.14583 | -0.048628 | -0.11659 | -0.004937 | -0.01972 | -0.13139 | 0.10743 | 0.19369 | 0.046142 | -0.042259 | 1.3942 | 1.5202 | 121.7745 | 121.9136 | 122.1708 | 122.0221 | 122.1193 | 122.0514 | 122.163 | 122.1482 | 122.0366 | 0.13032 | 0.21658 | 0.06903 | -0.019371 | 1.4171 | 1.5431 | 121.7974 | 121.9365 | -1.2868 | -121.6671 | -1.3481 | -121.7284
1907.3906 | 122.3373 | -122.1771 | 0.11902 | -0.001765 | -0.15041 | -0.062364 | -0.10743 | -0.004937 | -0.024298 | -0.13139 | 0.10743 | 0.18453 | 0.041563 | -0.060575 | 1.3805 | 1.5111 | 121.7699 | 121.9136 | 122.1754 | 122.0267 | 122.1148 | 122.0697 | 122.1722 | 122.1528 | 122.0457 | 0.13032 | 0.20742 | 0.064451 | -0.037687 | 1.4034 | 1.534 | 121.7928 | 121.9365 | -1.2731 | -121.6625 | -1.3389 | -121.7284
1909.0938 | 122.3328 | -122.2183 | 0.14191 | -0.001765 | -0.15499 | -0.062364 | -0.10743 | -0.004937 | -0.024298 | -0.13597 | 0.10743 | 0.18911 | 0.036985 | -0.055996 | 1.2752 | 1.4012 | 121.7883 | 121.9182 | 122.2166 | 122.0633 | 122.156 | 122.1109 | 122.2134 | 122.194 | 122.0824 | 0.13032 | 0.212 | 0.059873 | -0.033108 | 1.2981 | 1.4241 | 121.8111 | 121.941 | -1.1678 | -121.6808 | -1.2382 | -121.7513
1910.8438 | 122.3236 | -122.1588 | 0.14191 | -0.001765 | -0.15041 | -0.062364 | -0.10743 | -0.014093 | -0.01972 | -0.13597 | 0.10743 | 0.18453 | 0.036985 | -0.03768 | 1.3622 | 1.4974 | 121.7837 | 121.9273 | 122.157 | 122.0084 | 122.0964 | 122.0514 | 122.1447 | 122.1391 | 122.0228 | 0.13032 | 0.20742 | 0.059873 | -0.014792 | 1.3851 | 1.5202 | 121.8066 | 121.9502 | -1.2547 | -121.6763 | -1.3252 | -121.7467
1912.6094 | 122.406 | -122.1725 | 0.13275 | -0.010922 | -0.15499 | -0.071521 | -0.11201 | -0.009515 | -0.028877 | -0.14055 | 0.11201 | 0.19369 | 0.041563 | -0.03768 | 1.614 | 1.7354 | 121.7974 | 121.9273 | 122.1616 | 122.0176 | 122.101 | 122.0605 | 122.163 | 122.1437 | 122.032 | 0.1349 | 0.21658 | 0.064451 | -0.014792 | 1.6369 | 1.7583 | 121.8203 | 121.9502 | -1.502 | -121.6854 | -1.5724 | -121.7559
1914.375 | 122.4426 | -122.1771 | 0.11902 | -0.010922 | -0.15499 | -0.066943 | -0.11659 | -0.014093 | -0.024298 | -0.14512 | 0.11201 | 0.18453 | 0.041563 | -0.033101 | 1.5087 | 1.6347 | 121.7928 | 121.9227 | 122.1662 | 122.0221 | 122.1102 | 122.0605 | 122.163 | 122.1528 | 122.032 | 0.1349 | 0.20742 | 0.064451 | -0.010213 | 1.5316 | 1.6576 | 121.8157 | 121.9456 | -1.3967 | -121.6808 | -1.4671 | -121.7513
1916.0625 | 122.4792 | -122.1405 | 0.10071 | -0.015501 | -0.15499 | -0.071521 | -0.11659 | -0.018671 | -0.028877 | -0.14512 | 0.10743 | 0.19827 | 0.032407 | -0.069733 | 1.5407 | 1.6667 | 121.7928 | 121.9227 | 122.125 | 121.9855 | 122.069 | 122.0239 | 122.1218 | 122.1116 | 121.9954 | 0.13032 | 0.22115 | 0.055295 | -0.046845 | 1.5636 | 1.6896 | 121.8157 | 121.9456 | -1.4333 | -121.6854 | -1.5083 | -121.7604
1917.8125 | 122.3694 | -122.2275 | 0.16022 | -0.020079 | -0.15957 | -0.0761 | -0.11659 | -0.014093 | -0.024298 | -0.14512 | 0.11201 | 0.18911 | 0.036985 | -0.023943 | 1.7513 | 1.8911 | 121.8066 | 121.9319 | 122.2074 | 122.0679 | 122.1514 | 122.1109 | 122.2134 | 122.2032 | 122.0824 | 0.1349 | 0.212 | 0.059873 | -0.001055 | 1.7742 | 1.914 | 121.8295 | 121.9548 | -1.6393 | -121.6946 | -1.7143 | -121.7696
1919.5781 | 122.3602 | -122.2183 | 0.15564 | -0.020079 | -0.16873 | -0.0761 | -0.11659 | -0.018671 | -0.038034 | -0.14512 | 0.10743 | 0.18453 | 0.041563 | -0.033101 | 1.5957 | 1.7263 | 121.8112 | 121.9411 | 122.1982 | 122.0496 | 122.1422 | 122.1017 | 122.1997 | 122.1803 | 122.0732 | 0.13032 | 0.20742 | 0.064451 | -0.010213 | 1.6185 | 1.7491 | 121.834 | 121.9639 | -1.4882 | -121.7037 | -1.5541 | -121.7696
1921.3438 | 122.4518 | -122.1909 | 0.11444 | -0.029236 | -0.15957 | -0.0761 | -0.12116 | -0.023249 | -0.028877 | -0.15886 | 0.11201 | 0.18453 | 0.041563 | -0.019364 | 1.44 | 1.5752 | 121.802 | 121.9411 | 122.1616 | 122.0313 | 122.1148 | 122.0697 | 122.1676 | 122.162 | 122.032 | 0.1349 | 0.20742 | 0.064451 | 0.003524 | 1.4629 | 1.5981 | 121.8249 | 121.9639 | -1.328 | -121.69 | -1.3984 | -121.7604
1923.0312 | 122.4976 | -122.1909 | 0.12817 | -0.029236 | -0.16415 | -0.089836 | -0.12574 | -0.027827 | -0.038034 | -0.1497 | 0.10743 | 0.18911 | 0.036985 | -0.046838 | 1.3072 | 1.4287 | 121.8112 | 121.9456 | 122.1616 | 122.0267 | 122.101 | 122.0651 | 122.163 | 122.1528 | 122.0412 | 0.13032 | 0.212 | 0.059873 | -0.02395 | 1.3301 | 1.4516 | 121.834 | 121.9685 | -1.1998 | -121.7037 | -1.2702 | -121.7742
1924.7969 | 122.3785 | -122.2412 | 0.14648 | -0.024657 | -0.16873 | -0.080679 | -0.12574 | -0.023249 | -0.033455 | -0.1497 | 0.10743 | 0.19369 | 0.036985 | -0.03768 | 1.3301 | 1.4607 | 121.8249 | 121.9548 | 122.2166 | 122.0725 | 122.1605 | 122.1155 | 122.218 | 122.2078 | 122.0915 | 0.13032 | 0.21658 | 0.059873 | -0.014792 | 1.353 | 1.4836 | 121.8478 | 121.9777 | -1.2227 | -121.7175 | -1.2931 | -121.7879
1926.5625 | 122.4426 | -122.1954 | 0.12817 | -0.024657 | -0.16873 | -0.080679 | -0.12574 | -0.027827 | -0.042612 | -0.15428 | 0.10743 | 0.18911 | 0.036985 | -0.023943 | 1.1974 | 1.3325 | 121.8249 | 121.9502 | 122.1708 | 122.0267 | 122.1148 | 122.0697 | 122.1676 | 122.1528 | 122.0412 | 0.13032 | 0.212 | 0.059873 | -0.001055 | 1.2202 | 1.3554 | 121.8478 | 121.9731 | -1.0899 | -121.7175 | -1.1604 | -121.7879
1928.25 | 122.4106 | -122.2183 | 0.14191 | -0.029236 | -0.16873 | -0.089836 | -0.13948 | -0.032405 | -0.04719 | -0.15886 | 0.10743 | 0.18911 | 0.036985 | -0.033101 | 1.2752 | 1.4104 | 121.8249 | 121.9548 | 122.1891 | 122.0496 | 122.1285 | 122.0788 | 122.1859 | 122.1711 | 122.0595 | 0.13032 | 0.212 | 0.059873 | -0.010213 | 1.2981 | 1.4333 | 121.8478 | 121.9777 | -1.1678 | -121.7175 | -1.2382 | -121.7879
1930 | 122.4014 | -122.2229 | 0.14191 | -0.047549 | -0.17331 | -0.085257 | -0.13032 | -0.032405 | -0.04719 | -0.15428 | 0.10743 | 0.17995 | 0.036985 | -0.060575 | 1.5407 | 1.6667 | 121.8295 | 121.9639 | 122.1754 | 122.0496 | 122.1376 | 122.0926 | 122.1905 | 122.1757 | 122.0686 | 0.13032 | 0.20284 | 0.059873 | -0.037687 | 1.5636 | 1.6896 | 121.8524 | 121.9868 | -1.4333 | -121.722 | -1.5037 | -121.7925
1931.7031 | 122.4518 | -122.2183 | 0.13275 | -0.038393 | -0.18246 | -0.089836 | -0.1349 | -0.036983 | -0.051769 | -0.15886 | 0.10743 | 0.17995 | 0.036985 | -0.060575 | 1.44 | 1.5752 | 121.834 | 121.9685 | 122.1799 | 122.0359 | 122.1285 | 122.0834 | 122.1813 | 122.1666 | 122.0595 | 0.13032 | 0.20284 | 0.059873 | -0.037687 | 1.4629 | 1.5981 | 121.8569 | 121.9914 | -1.3326 | -121.7266 | -1.403 | -121.7971
1933.3906 | 122.406 | -122.2229 | 0.16022 | -0.029236 | -0.17788 | -0.094414 | -0.13948 | -0.032405 | -0.038034 | -0.16344 | 0.10743 | 0.18911 | 0.041563 | -0.046838 | 1.1699 | 1.3005 | 121.8432 | 121.9731 | 122.1937 | 122.045 | 122.1285 | 122.0834 | 122.1905 | 122.1849 | 122.0595 | 0.13032 | 0.212 | 0.064451 | -0.02395 | 1.1928 | 1.3234 | 121.8661 | 121.996 | -1.0625 | -121.7358 | -1.1283 | -121.8016
1935.0938 | 122.5342 | -122.2046 | 0.11902 | -0.042971 | -0.17331 | -0.098993 | -0.13948 | -0.041561 | -0.051769 | -0.17259 | 0.10743 | 0.18453 | 0.036985 | -0.074312 | 1.2157 | 1.3371 | 121.8386 | 121.9731 | 122.1616 | 122.0313 | 122.1056 | 122.0651 | 122.163 | 122.1528 | 122.032 | 0.13032 | 0.20742 | 0.059873 | -0.051424 | 1.2386 | 1.36 | 121.8615 | 121.996 | -1.1082 | -121.7312 | -1.1787 | -121.8016
1936.8125 | 122.5159 | -122.2092 | 0.1236 | -0.047549 | -0.18704 | -0.098993 | -0.14406 | -0.036983 | -0.056347 | -0.16801 | 0.11201 | 0.18911 | 0.041563 | -0.069733 | 1.2798 | 1.4058 | 121.8386 | 121.9777 | 122.1616 | 122.0221 | 122.1102 | 122.0651 | 122.1722 | 122.1528 | 122.0412 | 0.1349 | 0.212 | 0.064451 | -0.046845 | 1.3027 | 1.4287 | 121.8615 | 122.0006 | -1.1678 | -121.7266 | -1.2382 | -121.7971
1938.5781 | 122.3923 | -122.2321 | 0.15106 | -0.042971 | -0.19162 | -0.098993 | -0.13948 | -0.041561 | -0.051769 | -0.16801 | 0.10743 | 0.18911 | 0.032407 | -0.010206 | 1.1699 | 1.2913 | 121.8524 | 121.9685 | 122.1891 | 122.0404 | 122.1331 | 122.0926 | 122.1905 | 122.1803 | 122.064 | 0.13032 | 0.212 | 0.055295 | 0.012682 | 1.1928 | 1.3142 | 121.8752 | 121.9914 | -1.0625 | -121.7449 | -1.1375 | -121.8199
1940.3438 | 122.4014 | -122.2824 | 0.14191 | -0.042971 | -0.18246 | -0.098993 | -0.13948 | -0.041561 | -0.060926 | -0.16344 | 0.11201 | 0.18911 | 0.032407 | -0.11094 | 1.1562 | 1.3005 | 121.8524 | 121.9777 | 122.2394 | 122.0999 | 122.1834 | 122.1429 | 122.2408 | 122.2215 | 122.119 | 0.1349 | 0.212 | 0.055295 | -0.088056 | 1.179 | 1.3234 | 121.8752 | 122.0006 | -1.0441 | -121.7403 | -1.1237 | -121.8199
1942.0312 | 122.4884 | -122.2366 | 0.11444 | -0.052128 | -0.18246 | -0.10357 | -0.14864 | -0.050716 | -0.051769 | -0.18175 | 0.11201 | 0.18453 | 0.032407 | -0.03768 | 1.1287 | 1.2593 | 121.8386 | 121.9868 | 122.1845 | 122.0542 | 122.1331 | 122.088 | 122.1859 | 122.1849 | 122.0549 | 0.1349 | 0.20742 | 0.055295 | -0.014792 | 1.1516 | 1.2822 | 121.8615 | 122.0097 | -1.0167 | -121.7266 | -1.0963 | -121.8062
1943.7969 | 122.5388 | -122.2183 | 0.10986 | -0.056706 | -0.19162 | -0.10815 | -0.14864 | -0.046138 | -0.060926 | -0.17717 | 0.11659 | 0.18453 | 0.036985 | -0.033101 | 1.1378 | 1.273 | 121.8569 | 121.996 | 122.1616 | 122.0267 | 122.1102 | 122.0697 | 122.1722 | 122.1574 | 122.0412 | 0.13947 | 0.20742 | 0.059873 | -0.010213 | 1.1607 | 1.2959 | 121.8798 | 122.0189 | -1.0213 | -121.7403 | -1.1009 | -121.82
1945.5781 | 122.4884 | -122.2321 | 0.13275 | -0.061284 | -0.1962 | -0.10815 | -0.14864 | -0.046138 | -0.060926 | -0.18175 | 0.098273 | 0.18911 | 0.036985 | -0.03768 | 1.115 | 1.2364 | 121.8615 | 121.996 | 122.1708 | 122.0359 | 122.1239 | 122.0834 | 122.1859 | 122.1711 | 122.0503 | 0.12116 | 0.212 | 0.059873 | -0.014792 | 1.1378 | 1.2593 | 121.8844 | 122.0189 | -1.0167 | -121.7632 | -1.078 | -121.8245
1947.3438 | 122.4609 | -122.2687 | 0.14648 | -0.056706 | -0.1962 | -0.11273 | -0.16237 | -0.059872 | -0.060926 | -0.18175 | 0.10743 | 0.18911 | 0.036985 | -0.065154 | 1.1378 | 1.273 | 121.8615 | 121.996 | 122.212 | 122.0725 | 122.1559 | 122.1063 | 122.2088 | 122.2078 | 122.0869 | 0.13032 | 0.212 | 0.059873 | -0.042266 | 1.1607 | 1.2959 | 121.8844 | 122.0189 | -1.0304 | -121.7541 | -1.1009 | -121.8245
1949.0312 | 122.3969 | -122.287 | 0.14191 | -0.061284 | -0.1962 | -0.11731 | -0.15779 | -0.050716 | -0.065504 | -0.18633 | 0.10285 | 0.17995 | 0.036985 | -0.055996 | 1.1607 | 1.2913 | 121.8615 | 122.0051 | 122.2257 | 122.0908 | 122.1697 | 122.1292 | 122.2363 | 122.2215 | 122.1007 | 0.12574 | 0.20284 | 0.059873 | -0.033108 | 1.1836 | 1.3142 | 121.8844 | 122.028 | -1.0579 | -121.7587 | -1.1237 | -121.8245
1950.7969 | 122.4335 | -122.2778 | 0.14191 | -0.061284 | -0.20078 | -0.11273 | -0.15779 | -0.059872 | -0.070082 | -0.18175 | 0.10285 | 0.18453 | 0.032407 | -0.051417 | 1.1241 | 1.2501 | 121.8798 | 122.0051 | 122.2165 | 122.0771 | 122.1651 | 122.12 | 122.218 | 122.2078 | 122.0961 | 0.12574 | 0.20742 | 0.055295 | -0.028529 | 1.147 | 1.273 | 121.9027 | 122.028 | -1.0213 | -121.777 | -1.0917 | -121.8474
1952.5469 | 122.4243 | -122.2641 | 0.15106 | -0.065863 | -0.20078 | -0.12189 | -0.16237 | -0.059872 | -0.065504 | -0.19091 | 0.10285 | 0.18453 | 0.046142 | -0.019364 | 1.1562 | 1.2913 | 121.8707 | 122.0051 | 122.1982 | 122.0633 | 122.1422 | 122.1017 | 122.2042 | 122.1986 | 122.0732 | 0.12574 | 0.20742 | 0.06903 | 0.003524 | 1.179 | 1.3142 | 121.8936 | 122.028 | -1.0533 | -121.7678 | -1.11 | -121.8245
1954.25 | 122.5159 | -122.2687 | 0.10529 | -0.065863 | -0.20536 | -0.12189 | -0.16695 | -0.06445 | -0.079239 | -0.19091 | 0.10743 | 0.18911 | 0.041563 | -0.078891 | 1.1058 | 1.241 | 121.8752 | 122.0143 | 122.2028 | 122.0633 | 122.1468 | 122.1017 | 122.2042 | 122.1894 | 122.0778 | 0.13032 | 0.212 | 0.064451 | -0.056003 | 1.1287 | 1.2639 | 121.8981 | 122.0372 | -0.99836 | -121.7678 | -1.0642 | -121.8337
1956.0156 | 122.5204 | -122.2733 | 0.10529 | -0.07502 | -0.21452 | -0.13104 | -0.16695 | -0.069028 | -0.079239 | -0.19091 | 0.11201 | 0.18453 | 0.041563 | -0.028522 | 1.1562 | 1.3005 | 121.8798 | 122.0143 | 122.1982 | 122.0587 | 122.1422 | 122.1063 | 122.2042 | 122.194 | 122.0823 | 0.1349 | 0.20742 | 0.064451 | -0.005634 | 1.179 | 1.3234 | 121.9027 | 122.0372 | -1.0441 | -121.7678 | -1.1146 | -121.8383
1957.7812 | 122.58 | -122.2549 | 0.10986 | -0.070441 | -0.21452 | -0.12189 | -0.17153 | -0.06445 | -0.079239 | -0.20006 | 0.10743 | 0.18453 | 0.041563 | -0.055996 | 1.1012 | 1.2456 | 121.8936 | 122.0235 | 122.1845 | 122.0404 | 122.1331 | 122.0834 | 122.1905 | 122.1757 | 122.0549 | 0.13032 | 0.20742 | 0.064451 | -0.033108 | 1.1241 | 1.2685 | 121.9165 | 122.0463 | -0.99379 | -121.7861 | -1.0597 | -121.852
1959.5625 | 122.438 | -122.2824 | 0.13733 | -0.079598 | -0.21452 | -0.13104 | -0.16695 | -0.059872 | -0.079239 | -0.19548 | 0.11201 | 0.18453 | 0.036985 | -0.08347 | 1.4583 | 1.5843 | 121.8936 | 122.0235 | 122.2028 | 122.0679 | 122.1514 | 122.1155 | 122.2225 | 122.2032 | 122.0869 | 0.1349 | 0.20742 | 0.059873 | -0.060582 | 1.4812 | 1.6072 | 121.9165 | 122.0463 | -1.3463 | -121.7816 | -1.4213 | -121.8566
1961.25 | 122.5204 | -122.2687 | 0.1236 | -0.07502 | -0.20994 | -0.1402 | -0.17153 | -0.073606 | -0.088396 | -0.20464 | 0.11201 | 0.18911 | 0.041563 | -0.055996 | 1.2202 | 1.3509 | 121.8936 | 122.0235 | 122.1937 | 122.0587 | 122.1285 | 122.0971 | 122.1951 | 122.1803 | 122.064 | 0.1349 | 0.212 | 0.064451 | -0.033108 | 1.2431 | 1.3737 | 121.9165 | 122.0463 | -1.1082 | -121.7816 | -1.1787 | -121.852
1963 | 122.4472 | -122.2916 | 0.13275 | -0.070441 | -0.20994 | -0.1402 | -0.18069 | -0.06445 | -0.088396 | -0.20464 | 0.10743 | 0.17995 | 0.036985 | -0.03768 | 1.2019 | 1.328 | 121.8936 | 122.0326 | 122.2211 | 122.0816 | 122.1514 | 122.1109 | 122.2271 | 122.2032 | 122.0869 | 0.13032 | 0.20284 | 0.059873 | -0.014792 | 1.2248 | 1.3509 | 121.9165 | 122.0555 | -1.0945 | -121.7861 | -1.1649 | -121.8566
1964.7656 | 122.5113 | -122.2549 | 0.11902 | -0.07502 | -0.2191 | -0.13562 | -0.17611 | -0.078184 | -0.079239 | -0.20006 | 0.10285 | 0.17995 | 0.032407 | -0.069733 | 1.1012 | 1.2273 | 121.8981 | 122.0372 | 122.1799 | 122.0358 | 122.1193 | 122.0788 | 122.1768 | 122.1757 | 122.0549 | 0.12574 | 0.20284 | 0.055295 | -0.046845 | 1.1241 | 1.2501 | 121.921 | 122.0601 | -0.99836 | -121.7953 | -1.0688 | -121.8657
1966.5312 | 122.5342 | -122.2961 | 0.1236 | -0.084176 | -0.2191 | -0.13562 | -0.18069 | -0.078184 | -0.079239 | -0.2138 | 0.098273 | 0.18911 | 0.036985 | -0.051417 | 1.147 | 1.2822 | 121.8981 | 122.0372 | 122.212 | 122.077 | 122.1605 | 122.1155 | 122.218 | 122.2169 | 122.0823 | 0.12116 | 0.212 | 0.059873 | -0.028529 | 1.1699 | 1.3051 | 121.921 | 122.0601 | -1.0487 | -121.7999 | -1.11 | -121.8612
1968.2969 | 122.5983 | -122.2687 | 0.10529 | -0.084176 | -0.2191 | -0.13104 | -0.17611 | -0.069028 | -0.079239 | -0.20006 | 0.10743 | 0.18911 | 0.036985 | -0.074312 | 1.2706 | 1.4058 | 121.9027 | 122.0418 | 122.1845 | 122.0496 | 122.1376 | 122.0926 | 122.1996 | 122.1894 | 122.0686 | 0.13032 | 0.212 | 0.059873 | -0.051424 | 1.2935 | 1.4287 | 121.9256 | 122.0647 | -1.1632 | -121.7953 | -1.2336 | -121.8657
1969.9844 | 122.4564 | -122.3236 | 0.15564 | -0.079598 | -0.22367 | -0.14478 | -0.16695 | -0.073606 | -0.092974 | -0.20464 | 0.10743 | 0.18911 | 0.041563 | -0.046838 | 1.2431 | 1.3646 | 121.921 | 122.0463 | 122.244 | 122.0999 | 122.1788 | 122.1567 | 122.25 | 122.2306 | 122.119 | 0.13032 | 0.212 | 0.064451 | -0.02395 | 1.266 | 1.3875 | 121.9439 | 122.0692 | -1.1357 | -121.8136 | -1.2016 | -121.8795
1971.7344 | 122.5616 | -122.2824 | 0.11444 | -0.088755 | -0.2191 | -0.1402 | -0.18069 | -0.078184 | -0.088396 | -0.20922 | 0.10285 | 0.18911 | 0.032407 | -0.078891 | 1.234 | 1.3737 | 121.9119 | 122.0463 | 122.1937 | 122.0633 | 122.1422 | 122.1017 | 122.2042 | 122.194 | 122.0732 | 0.12574 | 0.212 | 0.055295 | -0.056003 | 1.2569 | 1.3966 | 121.9348 | 122.0692 | -1.1311 | -121.809 | -1.2016 | -121.8795
1973.5 | 122.493 | -122.319 | 0.15106 | -0.084176 | -0.2191 | -0.14478 | -0.17611 | -0.073606 | -0.088396 | -0.20464 | 0.10743 | 0.18453 | 0.027829 | -0.074312 | 1.2065 | 1.3371 | 121.921 | 122.0463 | 122.2349 | 122.0999 | 122.1743 | 122.1429 | 122.2454 | 122.2306 | 122.1144 | 0.13032 | 0.20742 | 0.050717 | -0.051424 | 1.2294 | 1.36 | 121.9439 | 122.0692 | -1.0991 | -121.8136 | -1.1787 | -121.8932
1975.1875 | 122.5708 | -122.2824 | 0.1236 | -0.088755 | -0.22367 | -0.14478 | -0.17611 | -0.078184 | -0.092974 | -0.20464 | 0.10285 | 0.18453 | 0.036985 | -0.033101 | 1.1928 | 1.3188 | 121.921 | 122.0463 | 122.1937 | 122.0587 | 122.1376 | 122.1063 | 122.2042 | 122.1894 | 122.0778 | 0.12574 | 0.20742 | 0.059873 | -0.010213 | 1.2157 | 1.3417 | 121.9439 | 122.0692 | -1.0899 | -121.8182 | -1.1558 | -121.884
1976.9531 | 122.5113 | -122.3282 | 0.13733 | -0.079598 | -0.22367 | -0.14478 | -0.18069 | -0.069028 | -0.088396 | -0.20922 | 0.10743 | 0.19369 | 0.032407 | -0.046838 | 1.0966 | 1.2318 | 121.9256 | 122.0647 | 122.2486 | 122.1045 | 122.1834 | 122.1475 | 122.2592 | 122.2398 | 122.119 | 0.13032 | 0.21658 | 0.055295 | -0.02395 | 1.1195 | 1.2547 | 121.9485 | 122.0875 | -0.98921 | -121.8182 | -1.0642 | -121.8932
1978.7031 | 122.4564 | -122.3145 | 0.15564 | -0.093333 | -0.22367 | -0.14478 | -0.18069 | -0.078184 | -0.092974 | -0.2138 | 0.10743 | 0.18911 | 0.041563 | -0.069733 | 1.1195 | 1.2501 | 121.9256 | 122.0601 | 122.2211 | 122.0908 | 122.1697 | 122.1338 | 122.2363 | 122.2215 | 122.1007 | 0.13032 | 0.212 | 0.064451 | -0.046845 | 1.1424 | 1.273 | 121.9485 | 122.083 | -1.0121 | -121.8182 | -1.078 | -121.884
1980.4062 | 122.6074 | -122.2778 | 0.10986 | -0.093333 | -0.22367 | -0.14478 | -0.18984 | -0.078184 | -0.092974 | -0.20922 | 0.10285 | 0.18911 | 0.036985 | -0.028522 | 1.0646 | 1.1998 | 121.9302 | 122.0647 | 122.1845 | 122.0542 | 122.1331 | 122.088 | 122.1996 | 122.1849 | 122.0686 | 0.12574 | 0.212 | 0.059873 | -0.005634 | 1.0875 | 1.2227 | 121.9531 | 122.0875 | -0.96174 | -121.8273 | -1.0276 | -121.8932
1982.1094 | 122.4655 | -122.319 | 0.13275 | -0.093333 | -0.22367 | -0.15394 | -0.18984 | -0.082762 | -0.097553 | -0.20922 | 0.10743 | 0.17995 | 0.046142 | -0.055996 | 1.1104 | 1.2456 | 121.9256 | 122.0555 | 122.2257 | 122.0954 | 122.1651 | 122.1292 | 122.2363 | 122.2215 | 122.1098 | 0.13032 | 0.20284 | 0.06903 | -0.033108 | 1.1333 | 1.2685 | 121.9485 | 122.0784 | -1.0029 | -121.8182 | -1.0642 | -121.8795
1983.8594 | 122.5571 | -122.2961 | 0.1236 | -0.10249 | -0.22825 | -0.15394 | -0.18526 | -0.08734 | -0.10213 | -0.21838 | 0.11201 | 0.18453 | 0.032407 | -0.065154 | 1.0692 | 1.1998 | 121.9302 | 122.0647 | 122.1937 | 122.0679 | 122.1422 | 122.1109 | 122.2088 | 122.194 | 122.0778 | 0.1349 | 0.20742 | 0.055295 | -0.042266 | 1.0921 | 1.2227 | 121.9531 | 122.0875 | -0.95716 | -121.8182 | -1.0368 | -121.8978
1985.5625 | 122.4701 | -122.3236 | 0.13275 | -0.10249 | -0.23741 | -0.14936 | -0.19442 | -0.091918 | -0.097553 | -0.21838 | 0.098273 | 0.18911 | 0.036985 | -0.046838 | 1.1287 | 1.2593 | 121.9393 | 122.0692 | 122.2211 | 122.0862 | 122.1742 | 122.1292 | 122.2317 | 122.2261 | 122.1052 | 0.12116 | 0.212 | 0.059873 | -0.02395 | 1.1516 | 1.2822 | 121.9622 | 122.0921 | -1.0304 | -121.8411 | -1.0917 | -121.9024
1987.2656 | 122.5708 | -122.3099 | 0.10071 | -0.097912 | -0.22825 | -0.15851 | -0.18984 | -0.082762 | -0.10213 | -0.2138 | 0.10743 | 0.18453 | 0.032407 | -0.019364 | 1.115 | 1.2456 | 121.9348 | 122.0738 | 122.212 | 122.0816 | 122.1514 | 122.12 | 122.2271 | 122.2077 | 122.0961 | 0.13032 | 0.20742 | 0.055295 | 0.003524 | 1.1378 | 1.2685 | 121.9577 | 122.0967 | -1.0075 | -121.8273 | -1.0825 | -121.9024
1988.9531 | 122.6028 | -122.3145 | 0.12817 | -0.097912 | -0.23283 | -0.15394 | -0.19442 | -0.08734 | -0.10213 | -0.2138 | 0.10285 | 0.18453 | 0.036985 | -0.023943 | 1.0829 | 1.2181 | 121.9393 | 122.083 | 122.2165 | 122.0816 | 122.1605 | 122.12 | 122.2271 | 122.2123 | 122.1007 | 0.12574 | 0.20742 | 0.059873 | -0.001055 | 1.1058 | 1.241 | 121.9622 | 122.1059 | -0.98005 | -121.8365 | -1.0459 | -121.9024
1990.7344 | 122.5433 | -122.3373 | 0.10986 | -0.10249 | -0.22825 | -0.14936 | -0.18984 | -0.08734 | -0.097553 | -0.22295 | 0.10285 | 0.18911 | 0.036985 | -0.074312 | 1.0783 | 1.2044 | 121.9485 | 122.083 | 122.2349 | 122.1091 | 122.188 | 122.1475 | 122.25 | 122.2398 | 122.1144 | 0.12574 | 0.212 | 0.059873 | -0.051424 | 1.1012 | 1.2272 | 121.9714 | 122.1059 | -0.97547 | -121.8457 | -1.0413 | -121.9115
1992.5 | 122.5983 | -122.3236 | 0.13275 | -0.097912 | -0.23741 | -0.15394 | -0.199 | -0.08734 | -0.10213 | -0.20922 | 0.10285 | 0.17995 | 0.036985 | -0.065154 | 1.1012 | 1.2318 | 121.9577 | 122.0876 | 122.2257 | 122.0862 | 122.1697 | 122.1246 | 122.2363 | 122.2215 | 122.1144 | 0.12574 | 0.20284 | 0.059873 | -0.042266 | 1.1241 | 1.2547 | 121.9805 | 122.1104 | -0.99836 | -121.8548 | -1.0642 | -121.9207
1994.25 | 122.5159 | -122.3694 | 0.14648 | -0.097912 | -0.23283 | -0.15851 | -0.18984 | -0.08734 | -0.10213 | -0.21838 | 0.11201 | 0.18453 | 0.036985 | -0.060575 | 1.0371 | 1.1723 | 121.9577 | 122.0876 | 122.2715 | 122.1366 | 122.2109 | 122.1795 | 122.282 | 122.2673 | 122.151 | 0.1349 | 0.20742 | 0.059873 | -0.037687 | 1.06 | 1.1952 | 121.9805 | 122.1104 | -0.92511 | -121.8457 | -1.0001 | -121.9207
1995.9531 | 122.5067 | -122.3419 | 0.14191 | -0.088755 | -0.23283 | -0.16309 | -0.18984 | -0.082762 | -0.10671 | -0.22295 | 0.11201 | 0.17995 | 0.036985 | -0.065154 | 1.2157 | 1.3554 | 121.9531 | 122.083 | 122.2532 | 122.1091 | 122.1788 | 122.1521 | 122.2592 | 122.2352 | 122.119 | 0.1349 | 0.20284 | 0.059873 | -0.042266 | 1.2386 | 1.3783 | 121.976 | 122.1059 | -1.1037 | -121.8411 | -1.1787 | -121.9161
1997.7031 | 122.493 | -122.3648 | 0.15106 | -0.10707 | -0.23741 | -0.15394 | -0.19442 | -0.082762 | -0.10213 | -0.22753 | 0.10285 | 0.17995 | 0.032407 | -0.074312 | 1.234 | 1.3646 | 121.9668 | 122.1013 | 122.2577 | 122.1274 | 122.2109 | 122.1704 | 122.282 | 122.2627 | 122.1373 | 0.12574 | 0.20284 | 0.055295 | -0.051424 | 1.2569 | 1.3875 | 121.9897 | 122.1242 | -1.1311 | -121.864 | -1.2016 | -121.9344
1999.4688 | 122.5021 | -122.374 | 0.14191 | -0.10249 | -0.22825 | -0.15394 | -0.199 | -0.091918 | -0.097553 | -0.21838 | 0.098273 | 0.18453 | 0.041563 | 0.003531 | 1.3942 | 1.534 | 121.9577 | 122.1013 | 122.2715 | 122.1457 | 122.22 | 122.175 | 122.282 | 122.2764 | 122.1556 | 0.12116 | 0.20742 | 0.064451 | 0.026419 | 1.4171 | 1.5569 | 121.9805 | 122.1242 | -1.2959 | -121.8594 | -1.3527 | -121.9161
2001.2344 | 122.6532 | -122.3145 | 0.10071 | -0.093333 | -0.23741 | -0.16309 | -0.199 | -0.08734 | -0.10671 | -0.21838 | 0.098273 | 0.18453 | 0.036985 | -0.033101 | 1.3255 | 1.4607 | 121.9668 | 122.0921 | 122.2211 | 122.077 | 122.1514 | 122.1155 | 122.2271 | 122.2077 | 122.0961 | 0.12116 | 0.20742 | 0.059873 | -0.010213 | 1.3484 | 1.4836 | 121.9897 | 122.115 | -1.2273 | -121.8685 | -1.2886 | -121.9298
2003 | 122.5204 | -122.3923 | 0.14648 | -0.10249 | -0.23741 | -0.15851 | -0.199 | -0.08734 | -0.088396 | -0.22753 | 0.10743 | 0.18453 | 0.036985 | -0.019364 | 1.3255 | 1.4516 | 121.976 | 122.0967 | 122.2898 | 122.1549 | 122.2338 | 122.1933 | 122.3049 | 122.3039 | 122.1647 | 0.13032 | 0.20742 | 0.059873 | 0.003524 | 1.3484 | 1.4745 | 121.9989 | 122.1196 | -1.2181 | -121.8685 | -1.2886 | -121.939
2004.7031 | 122.5708 | -122.3694 | 0.14648 | -0.10249 | -0.23283 | -0.15394 | -0.18984 | -0.091918 | -0.10213 | -0.22295 | 0.10743 | 0.18453 | 0.036985 | -0.03768 | 1.115 | 1.2501 | 121.9668 | 122.1059 | 122.2669 | 122.1366 | 122.2154 | 122.1795 | 122.2775 | 122.2673 | 122.1464 | 0.13032 | 0.20742 | 0.059873 | -0.014792 | 1.1378 | 1.273 | 121.9897 | 122.1288 | -1.0075 | -121.8594 | -1.078 | -121.9298
2006.4688 | 122.6212 | -122.3694 | 0.11902 | -0.10707 | -0.23283 | -0.16309 | -0.199 | -0.08734 | -0.10671 | -0.22295 | 0.11201 | 0.18911 | 0.032407 | -0.028522 | 1.1745 | 1.3051 | 121.976 | 122.0967 | 122.2623 | 122.1366 | 122.2063 | 122.1704 | 122.282 | 122.2627 | 122.1464 | 0.1349 | 0.212 | 0.055295 | -0.005634 | 1.1974 | 1.328 | 121.9989 | 122.1196 | -1.0625 | -121.864 | -1.1421 | -121.9436
2008.2188 | 122.6486 | -122.3099 | 0.11444 | -0.10249 | -0.24199 | -0.15394 | -0.18984 | -0.091918 | -0.097553 | -0.2138 | 0.10285 | 0.18453 | 0.036985 | -0.060575 | 1.1882 | 1.3142 | 121.9806 | 122.1059 | 122.2074 | 122.0679 | 122.1559 | 122.12 | 122.218 | 122.2123 | 122.0961 | 0.12574 | 0.20742 | 0.059873 | -0.037687 | 1.2111 | 1.3371 | 122.0034 | 122.1288 | -1.0854 | -121.8777 | -1.1512 | -121.9436
2009.9688 | 122.5113 | -122.3923 | 0.12817 | -0.10249 | -0.22825 | -0.16309 | -0.19442 | -0.08734 | -0.10213 | -0.2138 | 0.10285 | 0.17995 | 0.032407 | -0.092628 | 1.1607 | 1.2959 | 121.9806 | 122.1196 | 122.2898 | 122.164 | 122.2292 | 122.1979 | 122.3049 | 122.2901 | 122.1785 | 0.12574 | 0.20284 | 0.055295 | -0.06974 | 1.1836 | 1.3188 | 122.0034 | 122.1425 | -1.0579 | -121.8777 | -1.1283 | -121.9481
2011.6719 | 122.6578 | -122.319 | 0.09613 | -0.093333 | -0.23283 | -0.16309 | -0.18526 | -0.08734 | -0.10213 | -0.22295 | 0.10743 | 0.18453 | 0.041563 | -0.055996 | 1.1195 | 1.2501 | 121.976 | 122.115 | 122.2257 | 122.0862 | 122.1559 | 122.1338 | 122.2317 | 122.2169 | 122.0961 | 0.13032 | 0.20742 | 0.064451 | -0.033108 | 1.1424 | 1.273 | 121.9989 | 122.1379 | -1.0121 | -121.8685 | -1.078 | -121.9344
2013.4219 | 122.5433 | -122.3648 | 0.14648 | -0.10249 | -0.23283 | -0.14936 | -0.19442 | -0.091918 | -0.10213 | -0.21838 | 0.10285 | 0.17995 | 0.032407 | -0.051417 | 1.1424 | 1.273 | 121.9943 | 122.1288 | 122.2623 | 122.132 | 122.2154 | 122.1704 | 122.2729 | 122.2627 | 122.1464 | 0.12574 | 0.20284 | 0.055295 | -0.028529 | 1.1653 | 1.2959 | 122.0172 | 122.1516 | -1.0396 | -121.8914 | -1.11 | -121.9619
2015.1719 | 122.6669 | -122.3328 | 0.10986 | -0.10249 | -0.23741 | -0.15851 | -0.18984 | -0.091918 | -0.10213 | -0.22295 | 0.10743 | 0.17995 | 0.036985 | -0.078891 | 1.266 | 1.3966 | 121.9806 | 122.1242 | 122.2303 | 122.0954 | 122.1742 | 122.1429 | 122.2408 | 122.2306 | 122.1098 | 0.13032 | 0.20284 | 0.059873 | -0.056003 | 1.2889 | 1.4195 | 122.0034 | 122.1471 | -1.1586 | -121.8731 | -1.229 | -121.9436
2016.9375 | 122.6807 | -122.3328 | 0.10986 | -0.097912 | -0.23741 | -0.15851 | -0.199 | -0.091918 | -0.10671 | -0.22295 | 0.10285 | 0.17995 | 0.041563 | -0.03768 | 1.1607 | 1.2868 | 121.9851 | 122.1242 | 122.2349 | 122.0954 | 122.1742 | 122.1338 | 122.2408 | 122.2261 | 122.1098 | 0.12574 | 0.20284 | 0.064451 | -0.014792 | 1.1836 | 1.3097 | 122.008 | 122.1471 | -1.0579 | -121.8823 | -1.1192 | -121.9436
2018.625 | 122.5388 | -122.4014 | 0.11902 | -0.10249 | -0.23741 | -0.14936 | -0.19442 | -0.091918 | -0.10213 | -0.22295 | 0.10743 | 0.17995 | 0.036985 | -0.055996 | 1.1836 | 1.3097 | 121.9989 | 122.1196 | 122.2989 | 122.164 | 122.2521 | 122.207 | 122.3095 | 122.2993 | 122.1785 | 0.13032 | 0.20284 | 0.059873 | -0.033108 | 1.2065 | 1.3325 | 122.0218 | 122.1425 | -1.0762 | -121.8914 | -1.1466 | -121.9619
2020.3906 | 122.525 | -122.4152 | 0.1236 | -0.10707 | -0.24199 | -0.16309 | -0.18984 | -0.091918 | -0.11129 | -0.22295 | 0.098273 | 0.18911 | 0.032407 | -0.033101 | 1.1882 | 1.328 | 121.9943 | 122.1288 | 122.3081 | 122.1732 | 122.2521 | 122.2253 | 122.3232 | 122.3039 | 122.1922 | 0.12116 | 0.212 | 0.055295 | -0.010213 | 1.2111 | 1.3509 | 122.0172 | 122.1516 | -1.0899 | -121.896 | -1.1558 | -121.9619
2022.1562 | 122.5891 | -122.3969 | 0.14191 | -0.10707 | -0.23283 | -0.16309 | -0.19442 | -0.096496 | -0.10213 | -0.21838 | 0.10285 | 0.18453 | 0.036985 | -0.074312 | 1.1333 | 1.2685 | 122.0034 | 122.1379 | 122.2898 | 122.164 | 122.2338 | 122.2024 | 122.3004 | 122.2947 | 122.1785 | 0.12574 | 0.20742 | 0.059873 | -0.051424 | 1.1562 | 1.2913 | 122.0263 | 122.1608 | -1.0304 | -121.9006 | -1.0963 | -121.9665
2023.9375 | 122.493 | -122.2549 | 0.10529 | -0.056706 | -0.1962 | -0.11731 | -0.15321 | -0.059872 | -0.070082 | -0.18633 | 1.2292 | 1.2651 | 1.1907 | 1.1437 | 0.42822 | 0.40778 | 32.6058 | 33.2527 | 122.1982 | 122.0587 | 122.1376 | 122.1017 | 122.1951 | 122.1849 | 122.0686 | 1.252 | 1.288 | 1.2136 | 1.1666 | 0.45111 | 0.43067 | 32.6287 | 33.2756 | 0.80094 | -31.3767 | 0.76249 | -31.4151
2025.7031 | 122.5525 | -122.4335 | 0.13275 | -0.056706 | -0.19162 | -0.11273 | -0.14864 | -0.046138 | -0.051769 | -0.17717 | 0.093694 | 0.17537 | 0.02325 | -0.074312 | 0.084861 | 0.11936 | -0.024328 | 0.019719 | 122.3768 | 122.2418 | 122.3207 | 122.2848 | 122.3873 | 122.3817 | 122.2563 | 0.11658 | 0.19826 | 0.046138 | -0.051424 | 0.10775 | 0.14225 | -0.00144 | 0.042607 | 0.008833 | 0.11802 | -0.061611 | 0.047578
2027.4062 | 122.612 | -122.3831 | 0.10071 | -0.056706 | -0.1962 | -0.11273 | -0.15779 | -0.050716 | -0.060926 | -0.18633 | 0.093694 | 0.17079 | 0.027829 | -0.10179 | 0.10775 | 0.15598 | -0.038063 | 0.001406 | 122.3264 | 122.1869 | 122.2704 | 122.2253 | 122.3324 | 122.3222 | 122.1968 | 0.11658 | 0.19368 | 0.050717 | -0.078898 | 0.13064 | 0.17887 | -0.015175 | 0.024294 | -0.014058 | 0.13176 | -0.079923 | 0.065892
2029.0938 | 122.6898 | -122.3831 | 0.10529 | -0.056706 | -0.20078 | -0.11273 | -0.14406 | -0.059872 | -0.070082 | -0.17717 | 0.093694 | 0.17079 | 0.027829 | -0.092628 | 0.10317 | 0.16056 | -0.038063 | 0.001406 | 122.3264 | 122.1823 | 122.2704 | 122.2391 | 122.3232 | 122.313 | 122.2059 | 0.11658 | 0.19368 | 0.050717 | -0.06974 | 0.12606 | 0.18345 | -0.015175 | 0.024294 | -0.00948 | 0.13176 | -0.075345 | 0.065892
2030.8594 | 122.58 | -122.3923 | 0.11902 | -0.061284 | -0.19162 | -0.10815 | -0.15321 | -0.050716 | -0.065504 | -0.17717 | 0.093694 | 0.17079 | 0.027829 | -0.074312 | 0.11233 | 0.16514 | -0.04722 | -0.003172 | 122.331 | 122.2007 | 122.2841 | 122.2391 | 122.3416 | 122.3268 | 122.2151 | 0.11658 | 0.19368 | 0.050717 | -0.051424 | 0.13522 | 0.18803 | -0.024332 | 0.019716 | -0.018636 | 0.14091 | -0.084501 | 0.075049
2032.625 | 122.6807 | -122.3602 | 0.11444 | -0.056706 | -0.1962 | -0.11273 | -0.15779 | -0.050716 | -0.070082 | -0.17717 | 0.098273 | 0.17537 | 0.02325 | -0.10637 | 0.11233 | 0.16056 | -0.051798 | -0.003172 | 122.3035 | 122.164 | 122.2475 | 122.2024 | 122.3095 | 122.2901 | 122.1831 | 0.12116 | 0.19826 | 0.046138 | -0.083477 | 0.13522 | 0.18345 | -0.02891 | 0.019716 | -0.014057 | 0.15007 | -0.08908 | 0.075048
2034.375 | 122.6349 | -122.3923 | 0.09613 | -0.056706 | -0.1962 | -0.10815 | -0.13948 | -0.050716 | -0.070082 | -0.18175 | 0.093694 | 0.16622 | 0.02325 | -0.11094 | 0.10775 | 0.16056 | -0.056376 | -0.00775 | 122.3356 | 122.1961 | 122.2841 | 122.2528 | 122.3416 | 122.3222 | 122.2105 | 0.11658 | 0.1891 | 0.046138 | -0.088056 | 0.13064 | 0.18345 | -0.033488 | 0.015138 | -0.014058 | 0.15007 | -0.084502 | 0.079626
2036.0781 | 122.5891 | -122.4197 | 0.12817 | -0.052128 | -0.1962 | -0.11273 | -0.14864 | -0.050716 | -0.056347 | -0.18633 | 0.10285 | 0.17079 | 0.018672 | -0.097207 | 0.11691 | 0.16514 | -0.04722 | -0.00775 | 122.3676 | 122.2235 | 122.307 | 122.2711 | 122.369 | 122.3634 | 122.2334 | 0.12574 | 0.19368 | 0.04156 | -0.074319 | 0.1398 | 0.18803 | -0.024332 | 0.015138 | -0.014057 | 0.15007 | -0.098236 | 0.065892
2037.8281 | 122.1176 | -121.9025 | 0.11902 | -0.052128 | -0.19162 | -0.11273 | -0.14864 | -0.046138 | -0.060926 | -0.18175 | 0.53781 | 0.55541 | 0.49939 | 0.45686 | 0.19474 | 0.14683 | -0.051798 | -0.00775 | 121.8503 | 121.7108 | 121.7897 | 121.7538 | 121.8563 | 121.8415 | 121.7207 | 0.5607 | 0.5783 | 0.52228 | 0.47974 | 0.21762 | 0.16972 | -0.02891 | 0.015138 | 0.34307 | 0.58961 | 0.30466 | 0.55119
2039.5938 | 122.4609 | -122.1863 | 0.10071 | -0.052128 | -0.1962 | -0.10815 | -0.14864 | -0.055294 | -0.060926 | -0.17717 | 0.098273 | 0.17995 | 0.064455 | 0.067638 | 0.10775 | 0.15598 | -0.056376 | -0.003172 | 122.1342 | 121.9901 | 122.0781 | 122.0376 | 122.131 | 122.1254 | 122.0091 | 0.12116 | 0.20284 | 0.087343 | 0.090526 | 0.13064 | 0.17887 | -0.033488 | 0.019716 | -0.009479 | 0.15465 | -0.043297 | 0.12083
2041.3594 | 122.5021 | -122.1954 | 0.11902 | -0.056706 | -0.19162 | -0.11273 | -0.15321 | -0.050716 | -0.065504 | -0.18175 | 0.10285 | 0.17079 | 0.032407 | -0.065154 | 0.10317 | 0.15141 | -0.051798 | -0.016906 | 122.1387 | 122.0038 | 122.0827 | 122.0422 | 122.1447 | 122.1299 | 122.0137 | 0.12574 | 0.19368 | 0.055295 | -0.042266 | 0.12606 | 0.17429 | -0.02891 | 0.005982 | -0.000323 | 0.15465 | -0.070767 | 0.084205
2043.0312 | 122.4609 | -122.2366 | 0.1236 | -0.047549 | -0.18704 | -0.11273 | -0.15321 | -0.046138 | -0.060926 | -0.18175 | 0.098273 | 0.17537 | 0.027829 | -0.078891 | 0.11233 | 0.1743 | -0.04722 | -0.012328 | 122.1891 | 122.0496 | 122.1239 | 122.0834 | 122.1905 | 122.1757 | 122.0549 | 0.12116 | 0.19826 | 0.050717 | -0.056003 | 0.13522 | 0.19718 | -0.024332 | 0.01056 | -0.014057 | 0.14549 | -0.084501 | 0.075049
2044.7812 | 122.4243 | -122.2824 | 0.14648 | -0.052128 | -0.18704 | -0.10357 | -0.14406 | -0.055294 | -0.060926 | -0.17717 | 0.10743 | 0.17995 | 0.027829 | -0.074312 | 0.10775 | 0.16056 | -0.051798 | -0.016906 | 122.2303 | 122.0954 | 122.1788 | 122.1384 | 122.2271 | 122.2215 | 122.1052 | 0.13032 | 0.20284 | 0.050717 | -0.051424 | 0.13064 | 0.18345 | -0.02891 | 0.005982 | -0.000322 | 0.15923 | -0.079923 | 0.079627
2046.5469 | 122.5571 | -122.2458 | 0.10529 | -0.052128 | -0.18704 | -0.10357 | -0.14864 | -0.046138 | -0.056347 | -0.17717 | 0.093694 | 0.17537 | 0.027829 | -0.10179 | 0.084861 | 0.14225 | -0.051798 | -0.012328 | 122.1937 | 122.0587 | 122.1422 | 122.0972 | 122.1997 | 122.1894 | 122.0686 | 0.11658 | 0.19826 | 0.050717 | -0.078898 | 0.10775 | 0.16514 | -0.02891 | 0.01056 | 0.008833 | 0.14549 | -0.057032 | 0.079627
2048.2344 | 122.5754 | -122.2458 | 0.10529 | -0.052128 | -0.18704 | -0.10815 | -0.14406 | -0.046138 | -0.051769 | -0.17259 | 0.098273 | 0.17995 | 0.032407 | -0.097207 | 0.098596 | 0.14225 | -0.051798 | -0.00775 | 122.1937 | 122.0587 | 122.1376 | 122.1017 | 122.1997 | 122.194 | 122.0732 | 0.12116 | 0.20284 | 0.055295 | -0.074319 | 0.12148 | 0.16514 | -0.02891 | 0.015138 | -0.000323 | 0.15007 | -0.066189 | 0.084205
2050 | 122.5113 | -122.2916 | 0.13733 | -0.052128 | -0.19162 | -0.10815 | -0.13948 | -0.041561 | -0.056347 | -0.17717 | 0.098273 | 0.17995 | 0.032407 | -0.065154 | 0.094017 | 0.14683 | -0.056376 | -0.016906 | 122.2394 | 122.0999 | 122.1834 | 122.1521 | 122.25 | 122.2352 | 122.1144 | 0.12116 | 0.20284 | 0.055295 | -0.042266 | 0.11691 | 0.16972 | -0.033488 | 0.005982 | 0.004256 | 0.15465 | -0.06161 | 0.088783
2051.75 | 122.4747 | -122.3236 | 0.15106 | -0.047549 | -0.18704 | -0.10815 | -0.14406 | -0.046138 | -0.056347 | -0.17717 | 0.098273 | 0.17995 | 0.027829 | -0.092628 | 0.10317 | 0.15598 | -0.04722 | -0.016906 | 122.2761 | 122.1366 | 122.2155 | 122.1795 | 122.2775 | 122.2673 | 122.1464 | 0.12116 | 0.20284 | 0.050717 | -0.06974 | 0.12606 | 0.17887 | -0.024332 | 0.005982 | -0.004901 | 0.14549 | -0.075345 | 0.075049
2053.5 | 117.1783 | -78.3966 | 38.5025 | -0.024657 | -0.17331 | -0.085257 | -0.12574 | -0.027827 | -0.042612 | -0.15428 | 27.5143 | 28.0192 | 27.5708 | 27.6609 | 0.002454 | 0.014064 | -0.04722 | -0.003172 | 78.3719 | 78.2233 | 78.3113 | 78.2709 | 78.3688 | 78.354 | 78.2423 | 27.5372 | 28.042 | 27.5937 | 27.6838 | 0.025342 | 0.036952 | -0.024332 | 0.019716 | 27.5118 | 27.5615 | 27.5683 | 27.618
2055.25 | 122.3511 | -122.081 | 0.09613 | -0.056706 | -0.19162 | -0.11273 | -0.14864 | -0.055294 | -0.060926 | -0.17259 | 0.089116 | 0.17537 | 0.096503 | 0.063059 | 0.089439 | 0.13767 | -0.051798 | 0.001406 | 122.0243 | 121.8894 | 121.9683 | 121.9324 | 122.0257 | 122.0201 | 121.9084 | 0.112 | 0.19826 | 0.11939 | 0.085947 | 0.11233 | 0.16056 | -0.02891 | 0.024294 | -0.000323 | 0.14091 | 0.007064 | 0.1483
2056.9688 | 122.1588 | -121.7194 | 0.10071 | -0.042971 | -0.19162 | -0.10815 | -0.14864 | -0.046138 | -0.065504 | -0.17259 | 0.33178 | 0.386 | 0.32084 | 0.28285 | 0.17642 | 0.12394 | -0.060955 | 0.005985 | 121.6764 | 121.5277 | 121.6112 | 121.5707 | 121.6732 | 121.6539 | 121.5468 | 0.35466 | 0.40889 | 0.34373 | 0.30574 | 0.19931 | 0.14683 | -0.038067 | 0.028873 | 0.15535 | 0.39273 | 0.14441 | 0.38179
2058.7344 | 122.0673 | -121.6644 | 0.091553 | -0.052128 | -0.1962 | -0.11731 | -0.14406 | -0.050716 | -0.060926 | -0.17717 | 0.098273 | 0.17995 | 0.087346 | 0.05848 | 0.094017 | 0.13309 | -0.060955 | -0.003172 | 121.6123 | 121.4682 | 121.5471 | 121.5204 | 121.6137 | 121.6035 | 121.4873 | 0.12116 | 0.20284 | 0.11023 | 0.081368 | 0.11691 | 0.15598 | -0.038067 | 0.019716 | 0.004256 | 0.15923 | -0.006671 | 0.1483
2060.4375 | 121.8201 | -121.431 | 0.10529 | -0.052128 | -0.19162 | -0.10815 | -0.15321 | -0.050716 | -0.070082 | -0.17259 | 0.73926 | 0.76604 | 0.71457 | 0.66291 | 0.066548 | 0.11936 | -0.051798 | -0.00775 | 121.3788 | 121.2393 | 121.3228 | 121.2778 | 121.3803 | 121.3609 | 121.2584 | 0.76215 | 0.78893 | 0.73746 | 0.6858 | 0.089436 | 0.14225 | -0.02891 | 0.015138 | 0.67271 | 0.79106 | 0.64802 | 0.76637
2062.1875 | 121.9849 | -121.7697 | 0.14191 | -0.052128 | -0.18704 | -0.10357 | -0.14864 | -0.046138 | -0.060926 | -0.17259 | 0.089116 | 0.17537 | 0.059877 | 0.063059 | 0.071126 | 0.11936 | -0.056376 | -0.003172 | 121.7176 | 121.5827 | 121.6661 | 121.6211 | 121.7236 | 121.7088 | 121.5971 | 0.112 | 0.19826 | 0.082765 | 0.085947 | 0.094014 | 0.14225 | -0.033488 | 0.019716 | 0.01799 | 0.14549 | -0.011249 | 0.11625
2063.9531 | 122.0352 | -121.8613 | 0.13275 | -0.056706 | -0.18704 | -0.10357 | -0.13948 | -0.041561 | -0.056347 | -0.16801 | 0.089116 | 0.17537 | 0.018672 | -0.10179 | 0.075705 | 0.12851 | -0.051798 | -0.003172 | 121.8046 | 121.6742 | 121.7577 | 121.7218 | 121.8197 | 121.8049 | 121.6933 | 0.112 | 0.19826 | 0.04156 | -0.078898 | 0.098593 | 0.1514 | -0.02891 | 0.019716 | 0.013411 | 0.14091 | -0.057033 | 0.07047
2065.7031 | 122.1725 | -121.8613 | 0.10986 | -0.052128 | -0.1962 | -0.10815 | -0.14864 | -0.055294 | -0.060926 | -0.17717 | 0.093694 | 0.17537 | 0.032407 | -0.10637 | 0.071126 | 0.12394 | -0.056376 | -0.003172 | 121.8091 | 121.6651 | 121.7531 | 121.7126 | 121.806 | 121.8003 | 121.6841 | 0.11658 | 0.19826 | 0.055295 | -0.083477 | 0.094014 | 0.14683 | -0.033488 | 0.019716 | 0.022568 | 0.15007 | -0.038719 | 0.088783
2067.4062 | 122.0673 | -121.9299 | 0.13733 | -0.061284 | -0.1962 | -0.11273 | -0.14406 | -0.055294 | -0.060926 | -0.17717 | 0.089116 | 0.17079 | 0.027829 | -0.10179 | 0.084861 | 0.13767 | -0.051798 | -0.016906 | 121.8686 | 121.7337 | 121.8172 | 121.7859 | 121.8746 | 121.869 | 121.7528 | 0.112 | 0.19368 | 0.050717 | -0.078898 | 0.10775 | 0.16056 | -0.02891 | 0.005982 | 0.004255 | 0.14091 | -0.057032 | 0.079627
2069.0938 | 121.9574 | -121.9345 | 0.15106 | -0.056706 | -0.18704 | -0.11273 | -0.13948 | -0.050716 | -0.060926 | -0.17717 | 0.093694 | 0.16622 | 0.027829 | -0.11094 | 0.10317 | 0.16056 | -0.056376 | -0.012328 | 121.8778 | 121.7475 | 121.8218 | 121.795 | 121.8838 | 121.8736 | 121.7573 | 0.11658 | 0.1891 | 0.050717 | -0.088056 | 0.12606 | 0.18345 | -0.033488 | 0.01056 | -0.00948 | 0.15007 | -0.075345 | 0.084205
2070.8438 | 122.2366 | -121.9162 | 0.10529 | -0.056706 | -0.1962 | -0.11273 | -0.14406 | -0.050716 | -0.060926 | -0.18633 | 0.093694 | 0.17537 | 0.02325 | -0.092628 | 0.10317 | 0.16972 | -0.04722 | -0.00775 | 121.8595 | 121.72 | 121.8035 | 121.7721 | 121.8655 | 121.8553 | 121.7299 | 0.11658 | 0.19826 | 0.046138 | -0.06974 | 0.12606 | 0.19261 | -0.024332 | 0.015138 | -0.00948 | 0.14091 | -0.079924 | 0.07047
2072.625 | 122.1863 | -121.9437 | 0.10986 | -0.061284 | -0.19162 | -0.11273 | -0.14864 | -0.055294 | -0.056347 | -0.17717 | 0.089116 | 0.17537 | 0.02325 | -0.11094 | 0.10775 | 0.15598 | -0.051798 | -0.012328 | 121.8824 | 121.752 | 121.8309 | 121.795 | 121.8884 | 121.8873 | 121.7665 | 0.112 | 0.19826 | 0.046138 | -0.088056 | 0.13064 | 0.17887 | -0.02891 | 0.01056 | -0.018636 | 0.14091 | -0.084502 | 0.075048
2074.3906 | 122.2229 | -121.9345 | 0.12817 | -0.052128 | -0.20078 | -0.11273 | -0.15321 | -0.050716 | -0.065504 | -0.17717 | 0.089116 | 0.17537 | 0.018672 | -0.092628 | 0.098596 | 0.14683 | -0.056376 | -0.012328 | 121.8824 | 121.7337 | 121.8218 | 121.7813 | 121.8838 | 121.869 | 121.7573 | 0.112 | 0.19826 | 0.04156 | -0.06974 | 0.12148 | 0.16972 | -0.033488 | 0.01056 | -0.00948 | 0.14549 | -0.079924 | 0.075048
2076.0938 | 121.4493 | -121.4951 | 0.14648 | -0.056706 | -0.18246 | -0.11273 | -0.14406 | -0.046138 | -0.060926 | -0.18175 | 0.098273 | 0.17995 | 0.032407 | -0.10637 | 0.10317 | 0.15598 | -0.056376 | -0.003172 | 121.4383 | 121.3126 | 121.3823 | 121.351 | 121.4489 | 121.4341 | 121.3133 | 0.12116 | 0.20284 | 0.055295 | -0.083477 | 0.12606 | 0.17887 | -0.033488 | 0.019716 | -0.004901 | 0.15465 | -0.070767 | 0.088783
2077.8438 | 121.5546 | -121.5317 | 0.12817 | -0.056706 | -0.1962 | -0.11273 | -0.15321 | -0.041561 | -0.060926 | -0.17717 | 0.093694 | 0.17537 | 0.02325 | -0.10637 | 0.098596 | 0.15598 | -0.051798 | -0.012328 | 121.475 | 121.3355 | 121.4189 | 121.3785 | 121.4901 | 121.4708 | 121.3545 | 0.11658 | 0.19826 | 0.046138 | -0.083477 | 0.12148 | 0.17887 | -0.02891 | 0.01056 | -0.004902 | 0.14549 | -0.075346 | 0.075048
2079.6094 | 122.2412 | -121.9849 | 0.11444 | -0.047549 | -0.20078 | -0.10815 | -0.14864 | -0.046138 | -0.070082 | -0.18633 | 0.089116 | 0.17537 | 0.027829 | -0.08347 | 0.10317 | 0.15141 | -0.065533 | -0.003172 | 121.9373 | 121.7841 | 121.8767 | 121.8362 | 121.9387 | 121.9148 | 121.7985 | 0.112 | 0.19826 | 0.050717 | -0.060582 | 0.12606 | 0.17429 | -0.042645 | 0.019716 | -0.014058 | 0.15465 | -0.075345 | 0.093362
2081.3125 | 122.2321 | -122.0169 | 0.12817 | -0.056706 | -0.19162 | -0.11273 | -0.14406 | -0.055294 | -0.060926 | -0.17717 | 0.089116 | 0.17079 | 0.027829 | -0.092628 | 0.094017 | 0.15141 | -0.056376 | -0.00775 | 121.9602 | 121.8253 | 121.9042 | 121.8728 | 121.9616 | 121.956 | 121.8397 | 0.112 | 0.19368 | 0.050717 | -0.06974 | 0.11691 | 0.17429 | -0.033488 | 0.015138 | -0.004901 | 0.14549 | -0.066188 | 0.084205
2083 | 122.2641 | -122.0169 | 0.10529 | -0.056706 | -0.19162 | -0.10815 | -0.14864 | -0.050716 | -0.060926 | -0.17717 | 0.093694 | 0.17079 | 0.027829 | -0.092628 | 0.10317 | 0.14683 | -0.051798 | -0.016906 | 121.9602 | 121.8253 | 121.9088 | 121.8683 | 121.9662 | 121.956 | 121.8397 | 0.11658 | 0.19368 | 0.050717 | -0.06974 | 0.12606 | 0.16972 | -0.02891 | 0.005982 | -0.00948 | 0.14549 | -0.075345 | 0.079627
2084.75 | 121.8384 | -121.5637 | 0.13275 | -0.056706 | -0.19162 | -0.10815 | -0.14864 | -0.050716 | -0.060926 | -0.17259 | 0.084537 | 0.17537 | 0.027829 | -0.08347 | 0.089439 | 0.15141 | -0.056376 | -0.00775 | 121.507 | 121.3721 | 121.4556 | 121.4151 | 121.513 | 121.5028 | 121.3911 | 0.10742 | 0.19826 | 0.050717 | -0.060582 | 0.11233 | 0.17429 | -0.033488 | 0.015138 | -0.004902 | 0.14091 | -0.06161 | 0.084205
2086.5312 | 122.3099 | -121.9894 | 0.10071 | -0.061284 | -0.1962 | -0.11273 | -0.15321 | -0.050716 | -0.065504 | -0.18175 | 0.089116 | 0.17079 | 0.032407 | -0.11094 | 0.10317 | 0.15598 | -0.056376 | -0.016906 | 121.9282 | 121.7932 | 121.8767 | 121.8362 | 121.9387 | 121.9239 | 121.8077 | 0.112 | 0.19368 | 0.055295 | -0.088056 | 0.12606 | 0.17887 | -0.033488 | 0.005982 | -0.014058 | 0.14549 | -0.070767 | 0.088783
2088.2188 | 122.3099 | -122.0215 | 0.10986 | -0.056706 | -0.1962 | -0.10815 | -0.13948 | -0.050716 | -0.060926 | -0.17717 | 0.089116 | 0.17079 | 0.032407 | -0.088049 | 0.10317 | 0.15141 | -0.056376 | -0.012328 | 121.9648 | 121.8253 | 121.9133 | 121.882 | 121.9708 | 121.9606 | 121.8443 | 0.112 | 0.19368 | 0.055295 | -0.065161 | 0.12606 | 0.17429 | -0.033488 | 0.01056 | -0.014058 | 0.14549 | -0.070767 | 0.088783
2089.9688 | 122.2595 | -122.0123 | 0.10071 | -0.056706 | -0.18704 | -0.11731 | -0.14864 | -0.050716 | -0.060926 | -0.18175 | 0.079959 | 0.17079 | 0.032407 | -0.11552 | 0.10775 | 0.16056 | -0.051798 | -0.012328 | 121.9556 | 121.8253 | 121.895 | 121.8637 | 121.9616 | 121.9514 | 121.8306 | 0.10285 | 0.19368 | 0.055295 | -0.092635 | 0.13064 | 0.18345 | -0.02891 | 0.01056 | -0.027793 | 0.13176 | -0.075345 | 0.084205
2091.6719 | 122.3236 | -122.0261 | 0.10986 | -0.047549 | -0.20078 | -0.11273 | -0.14864 | -0.046138 | -0.060926 | -0.18175 | 0.084537 | 0.17537 | 0.02325 | -0.10637 | 0.10317 | 0.15598 | -0.051798 | -0.012328 | 121.9785 | 121.8253 | 121.9133 | 121.8774 | 121.9799 | 121.9651 | 121.8443 | 0.10742 | 0.19826 | 0.046138 | -0.083477 | 0.12606 | 0.17887 | -0.02891 | 0.01056 | -0.018637 | 0.13633 | -0.079924 | 0.075048
2093.4375 | 122.2229 | -122.0856 | 0.13275 | -0.052128 | -0.20078 | -0.10815 | -0.14406 | -0.046138 | -0.060926 | -0.17717 | 0.093694 | 0.17537 | 0.027829 | -0.10637 | 0.10775 | 0.15598 | -0.056376 | -0.00775 | 122.0334 | 121.8848 | 121.9774 | 121.9415 | 122.0394 | 122.0246 | 121.9084 | 0.11658 | 0.19826 | 0.050717 | -0.083477 | 0.13064 | 0.17887 | -0.033488 | 0.015138 | -0.014058 | 0.15007 | -0.079923 | 0.084205
2095.125 | 122.2137 | -122.0947 | 0.13733 | -0.056706 | -0.19162 | -0.11273 | -0.14864 | -0.046138 | -0.060926 | -0.17259 | 0.093694 | 0.17537 | 0.02325 | -0.12468 | 0.10775 | 0.16056 | -0.056376 | -0.00775 | 122.038 | 121.9031 | 121.982 | 121.9461 | 122.0486 | 122.0338 | 121.9221 | 0.11658 | 0.19826 | 0.046138 | -0.10179 | 0.13064 | 0.18345 | -0.033488 | 0.015138 | -0.014058 | 0.15007 | -0.084502 | 0.079626
2096.8281 | 122.3602 | -122.0718 | 0.10529 | -0.047549 | -0.18704 | -0.10815 | -0.14864 | -0.050716 | -0.060926 | -0.17259 | 0.093694 | 0.17537 | 0.032407 | -0.11552 | 0.10775 | 0.16514 | -0.060955 | -0.016906 | 122.0243 | 121.8848 | 121.9637 | 121.9232 | 122.0211 | 122.0109 | 121.8992 | 0.11658 | 0.19826 | 0.055295 | -0.092635 | 0.13064 | 0.18803 | -0.038067 | 0.005982 | -0.014058 | 0.15465 | -0.075345 | 0.093362
2098.5938 | 122.2366 | -122.0535 | 0.13733 | -0.047549 | -0.18246 | -0.10815 | -0.13948 | -0.036983 | -0.051769 | -0.17259 | 0.089116 | 0.17079 | 0.027829 | -0.092628 | 0.10775 | 0.16514 | -0.051798 | -0.021484 | 122.006 | 121.8711 | 121.9454 | 121.914 | 122.0165 | 122.0018 | 121.8809 | 0.112 | 0.19368 | 0.050717 | -0.06974 | 0.13064 | 0.18803 | -0.02891 | 0.001404 | -0.018636 | 0.14091 | -0.079923 | 0.079627
2100.3438 | 122.3694 | -122.0444 | 0.10071 | -0.042971 | -0.17331 | -0.098993 | -0.13032 | -0.036983 | -0.051769 | -0.15886 | 0.089116 | 0.17079 | 0.027829 | -0.10637 | 0.10775 | 0.16514 | -0.056376 | -0.00775 | 122.0014 | 121.8711 | 121.9454 | 121.9141 | 122.0074 | 121.9926 | 121.8855 | 0.112 | 0.19368 | 0.050717 | -0.083477 | 0.13064 | 0.18803 | -0.033488 | 0.015138 | -0.018636 | 0.14549 | -0.079923 | 0.084205
2102.1094 | 122.2412 | -122.0993 | 0.13275 | -0.038393 | -0.17788 | -0.094414 | -0.1349 | -0.027827 | -0.042612 | -0.15428 | 0.089116 | 0.17079 | 0.027829 | -0.088049 | 0.10317 | 0.16056 | -0.060955 | -0.012328 | 122.0609 | 121.9214 | 122.0049 | 121.9644 | 122.0715 | 122.0567 | 121.945 | 0.112 | 0.19368 | 0.050717 | -0.065161 | 0.12606 | 0.18345 | -0.038067 | 0.01056 | -0.014058 | 0.15007 | -0.075345 | 0.088784
2103.8594 | 122.2961 | -122.0901 | 0.1236 | -0.042971 | -0.17331 | -0.085257 | -0.12574 | -0.036983 | -0.038034 | -0.16801 | 0.089116 | 0.17079 | 0.027829 | -0.10179 | 0.11233 | 0.16056 | -0.051798 | -0.012328 | 122.0472 | 121.9168 | 122.0049 | 121.9644 | 122.0532 | 122.0521 | 121.9221 | 0.112 | 0.19368 | 0.050717 | -0.078898 | 0.13522 | 0.18345 | -0.02891 | 0.01056 | -0.023214 | 0.14091 | -0.084501 | 0.079627
2105.625 | 122.3419 | -122.081 | 0.11902 | -0.047549 | -0.17788 | -0.098993 | -0.1349 | -0.041561 | -0.051769 | -0.16801 | 0.084537 | 0.17079 | 0.02325 | -0.10179 | 0.10775 | 0.15598 | -0.051798 | -0.00775 | 122.0334 | 121.9031 | 121.982 | 121.9461 | 122.0394 | 122.0292 | 121.913 | 0.10742 | 0.19368 | 0.046138 | -0.078898 | 0.13064 | 0.17887 | -0.02891 | 0.015138 | -0.023215 | 0.13633 | -0.084502 | 0.075048
2107.3281 | 122.3145 | -122.1085 | 0.1236 | -0.042971 | -0.17788 | -0.098993 | -0.13032 | -0.041561 | -0.051769 | -0.16801 | 0.089116 | 0.17079 | 0.027829 | -0.11552 | 0.10317 | 0.15598 | -0.060955 | -0.00775 | 122.0655 | 121.9306 | 122.0095 | 121.9781 | 122.0669 | 122.0567 | 121.9404 | 0.112 | 0.19368 | 0.050717 | -0.092635 | 0.12606 | 0.17887 | -0.038067 | 0.015138 | -0.014058 | 0.15007 | -0.075345 | 0.088784
2109.0156 | 122.3282 | -122.1222 | 0.12817 | -0.042971 | -0.17788 | -0.094414 | -0.1349 | -0.027827 | -0.051769 | -0.16344 | 0.093694 | 0.17537 | 0.02325 | -0.088049 | 0.094017 | 0.16056 | -0.051798 | -0.00775 | 122.0792 | 121.9443 | 122.0278 | 121.9873 | 122.0944 | 122.0704 | 121.9588 | 0.11658 | 0.19826 | 0.046138 | -0.065161 | 0.11691 | 0.18345 | -0.02891 | 0.015138 | -0.000323 | 0.14549 | -0.070767 | 0.075048
2110.7656 | 122.319 | -122.1176 | 0.1236 | -0.042971 | -0.16873 | -0.094414 | -0.12574 | -0.027827 | -0.04719 | -0.16344 | 0.079959 | 0.16622 | 0.02325 | -0.10637 | 0.098596 | 0.14683 | -0.060955 | -0.012328 | 122.0746 | 121.9489 | 122.0232 | 121.9919 | 122.0898 | 122.0704 | 121.9542 | 0.10285 | 0.1891 | 0.046138 | -0.083477 | 0.12148 | 0.16972 | -0.038067 | 0.01056 | -0.018637 | 0.14091 | -0.075346 | 0.084205
2112.4844 | 122.3282 | -122.1451 | 0.14191 | -0.033814 | -0.17788 | -0.094414 | -0.13032 | -0.032405 | -0.042612 | -0.16801 | 0.089116 | 0.17079 | 0.02325 | -0.10637 | 0.075705 | 0.12394 | -0.056376 | 0.001406 | 122.1113 | 121.9672 | 122.0507 | 122.0148 | 122.1127 | 122.1025 | 121.9771 | 0.112 | 0.19368 | 0.046138 | -0.083477 | 0.098593 | 0.14683 | -0.033488 | 0.024294 | 0.013411 | 0.14549 | -0.052455 | 0.079626
2114.25 | 122.2916 | -122.1588 | 0.12817 | -0.038393 | -0.18246 | -0.098993 | -0.1349 | -0.036983 | -0.051769 | -0.16801 | 0.084537 | 0.16622 | 0.032407 | -0.10637 | 0.075705 | 0.13309 | -0.051798 | -0.012328 | 122.1204 | 121.9763 | 122.0598 | 122.0239 | 122.1218 | 122.107 | 121.9908 | 0.10742 | 0.1891 | 0.055295 | -0.083477 | 0.098593 | 0.15598 | -0.02891 | 0.01056 | 0.008832 | 0.13633 | -0.043298 | 0.084205
2116.0156 | 122.4014 | -122.1039 | 0.10071 | -0.038393 | -0.17331 | -0.094414 | -0.13032 | -0.036983 | -0.051769 | -0.16801 | 0.089116 | 0.17537 | 0.02325 | -0.10179 | 0.071126 | 0.11936 | -0.056376 | -0.016906 | 122.0655 | 121.9306 | 122.0095 | 121.9736 | 122.0669 | 122.0521 | 121.9359 | 0.112 | 0.19826 | 0.046138 | -0.078898 | 0.094014 | 0.14225 | -0.033488 | 0.005982 | 0.01799 | 0.14549 | -0.047876 | 0.079626
2117.7188 | 122.2916 | -122.1497 | 0.13733 | -0.047549 | -0.17788 | -0.098993 | -0.13948 | -0.036983 | -0.04719 | -0.16801 | 0.084537 | 0.17079 | 0.027829 | -0.11094 | 0.06197 | 0.10105 | -0.056376 | -0.016906 | 122.1021 | 121.9718 | 122.0507 | 122.0102 | 122.1127 | 122.1025 | 121.9816 | 0.10742 | 0.19368 | 0.050717 | -0.088056 | 0.084858 | 0.12393 | -0.033488 | 0.005982 | 0.022567 | 0.14091 | -0.034141 | 0.084205
2119.4688 | 122.3373 | -122.168 | 0.11902 | -0.042971 | -0.19162 | -0.094414 | -0.1349 | -0.041561 | -0.04719 | -0.17259 | 0.084537 | 0.17079 | 0.027829 | -0.10179 | 0.080283 | 0.13309 | -0.051798 | -0.00775 | 122.125 | 121.9763 | 122.0736 | 122.0331 | 122.1264 | 122.1208 | 121.9954 | 0.10742 | 0.19368 | 0.050717 | -0.078898 | 0.10317 | 0.15598 | -0.02891 | 0.015138 | 0.004254 | 0.13633 | -0.052454 | 0.079627
2121.2188 | 122.4289 | -122.1268 | 0.1236 | -0.052128 | -0.17331 | -0.094414 | -0.13948 | -0.036983 | -0.051769 | -0.16344 | 0.084537 | 0.16622 | 0.02325 | -0.10637 | 0.080283 | 0.12851 | -0.056376 | -0.012328 | 122.0746 | 121.9535 | 122.0324 | 121.9873 | 122.0898 | 122.075 | 121.9633 | 0.10742 | 0.1891 | 0.046138 | -0.083477 | 0.10317 | 0.1514 | -0.033488 | 0.01056 | 0.004254 | 0.14091 | -0.057033 | 0.079626
2122.9219 | 122.4335 | -122.1405 | 0.09613 | -0.033814 | -0.18246 | -0.094414 | -0.13032 | -0.036983 | -0.042612 | -0.16801 | 0.089116 | 0.16622 | 0.018672 | -0.092628 | 0.048236 | 0.082735 | -0.060955 | -0.012328 | 122.1067 | 121.958 | 122.0461 | 122.0102 | 122.1035 | 122.0979 | 121.9725 | 0.112 | 0.1891 | 0.04156 | -0.06974 | 0.071124 | 0.10562 | -0.038067 | 0.01056 | 0.04088 | 0.15007 | -0.029564 | 0.079627
2124.6875 | 122.4014 | -122.1634 | 0.1236 | -0.038393 | -0.17788 | -0.098993 | -0.1349 | -0.036983 | -0.051769 | -0.17259 | 0.084537 | 0.17537 | 0.027829 | -0.11552 | 0.025345 | 0.064423 | -0.051798 | -0.012328 | 122.125 | 121.9855 | 122.0644 | 122.0285 | 122.1264 | 122.1116 | 121.9908 | 0.10742 | 0.19826 | 0.050717 | -0.092635 | 0.048233 | 0.087311 | -0.02891 | 0.01056 | 0.059192 | 0.13633 | 0.002484 | 0.079627
2126.4375 | 122.4564 | -122.113 | 0.082397 | 0.098959 | -0.049678 | 0.056679 | 0.002454 | 0.10036 | 0.081005 | -0.035248 | 0.084537 | 0.16622 | 0.027829 | -0.10179 | 0.025345 | 0.059844 | -0.051798 | -0.012328 | 122.212 | 122.0634 | 122.1697 | 122.1155 | 122.2134 | 122.194 | 122.0778 | 0.10742 | 0.1891 | 0.050717 | -0.078898 | 0.048233 | 0.082732 | -0.02891 | 0.01056 | 0.059192 | 0.13633 | 0.002484 | 0.079627
2128.1406 | 122.319 | -122.1909 | 0.13275 | 0.11269 | -0.040521 | 0.061258 | 0.007033 | 0.11409 | 0.09474 | -0.026092 | 0.089116 | 0.17537 | 0.027829 | -0.10179 | 0.029923 | 0.059844 | -0.051798 | -0.003172 | 122.3036 | 122.1503 | 122.2521 | 122.1979 | 122.3049 | 122.2856 | 122.1648 | 0.112 | 0.19826 | 0.050717 | -0.078898 | 0.052811 | 0.082732 | -0.02891 | 0.019716 | 0.059193 | 0.14091 | -0.002094 | 0.079627
2129.8906 | 122.4106 | -122.1588 | 0.11444 | 0.11727 | -0.0451 | 0.056679 | -0.002124 | 0.10493 | 0.09474 | -0.03067 | 0.084537 | 0.17079 | 0.02325 | -0.10179 | 0.048236 | 0.087313 | -0.042641 | -0.00775 | 122.2761 | 122.1137 | 122.2155 | 122.1567 | 122.2637 | 122.2536 | 122.1281 | 0.10742 | 0.19368 | 0.046138 | -0.078898 | 0.071124 | 0.1102 | -0.019753 | 0.015138 | 0.036301 | 0.12718 | -0.024986 | 0.065891
2131.5938 | 122.4106 | -122.168 | 0.086975 | 0.11727 | -0.049678 | 0.052101 | 0.007033 | 0.10951 | 0.090161 | -0.026092 | 0.084537 | 0.16622 | 0.02325 | -0.10637 | 0.029923 | 0.050688 | -0.051798 | -0.016906 | 122.2852 | 122.1183 | 122.2201 | 122.175 | 122.2775 | 122.2581 | 122.1419 | 0.10742 | 0.1891 | 0.046138 | -0.083477 | 0.052811 | 0.073576 | -0.02891 | 0.005982 | 0.054614 | 0.13633 | -0.006673 | 0.075048
2133.3594 | 122.3831 | -122.1863 | 0.11902 | 0.11269 | -0.040521 | 0.061258 | 0.007033 | 0.11409 | 0.09474 | -0.03067 | 0.07538 | 0.17537 | 0.027829 | -0.10637 | 0.016188 | 0.04611 | -0.051798 | -0.012328 | 122.299 | 122.1458 | 122.2475 | 122.1933 | 122.3004 | 122.281 | 122.1556 | 0.098268 | 0.19826 | 0.050717 | -0.083477 | 0.039076 | 0.068998 | -0.02891 | 0.01056 | 0.059192 | 0.12718 | 0.011641 | 0.079627
2135.0625 | 122.4884 | -122.1634 | 0.10071 | 0.11727 | -0.0451 | 0.056679 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.084537 | 0.17537 | 0.032407 | -0.11094 | 0.020767 | 0.041532 | -0.056376 | -0.00775 | 122.2807 | 122.1183 | 122.2201 | 122.1658 | 122.2729 | 122.2444 | 122.1373 | 0.10742 | 0.19826 | 0.055295 | -0.088056 | 0.043655 | 0.06442 | -0.033488 | 0.015138 | 0.06377 | 0.14091 | 0.01164 | 0.088783
2136.8281 | 122.374 | -122.1817 | 0.13733 | 0.11269 | -0.040521 | 0.061258 | 0.011611 | 0.10951 | 0.090161 | -0.021514 | 0.089116 | 0.17079 | 0.027829 | -0.11094 | 0.016188 | 0.041532 | -0.051798 | -0.016906 | 122.2944 | 122.1412 | 122.243 | 122.1933 | 122.2912 | 122.2719 | 122.1602 | 0.112 | 0.19368 | 0.050717 | -0.088056 | 0.039076 | 0.06442 | -0.02891 | 0.005982 | 0.072928 | 0.14091 | 0.011641 | 0.079627
2138.5938 | 122.4747 | -122.1863 | 0.10529 | 0.11727 | -0.040521 | 0.052101 | 0.007033 | 0.10951 | 0.081005 | -0.03067 | 0.089116 | 0.17079 | 0.018672 | -0.10179 | 0.016188 | 0.04611 | -0.051798 | -0.016906 | 122.3036 | 122.1458 | 122.2384 | 122.1933 | 122.2958 | 122.2673 | 122.1556 | 0.112 | 0.19368 | 0.04156 | -0.078898 | 0.039076 | 0.068998 | -0.02891 | 0.005982 | 0.072928 | 0.14091 | 0.002484 | 0.07047
2140.3594 | 122.3831 | -122.2046 | 0.13275 | 0.12185 | -0.035942 | 0.052101 | 0.011611 | 0.10951 | 0.090161 | -0.016936 | 0.084537 | 0.16622 | 0.018672 | -0.10637 | 0.020767 | 0.036954 | -0.060955 | -0.00775 | 122.3264 | 122.1686 | 122.2567 | 122.2162 | 122.3141 | 122.2948 | 122.1877 | 0.10742 | 0.1891 | 0.04156 | -0.083477 | 0.043655 | 0.059842 | -0.038067 | 0.015138 | 0.06377 | 0.14549 | -0.002095 | 0.079627
2142.0625 | 122.4106 | -122.2183 | 0.14648 | 0.11269 | -0.035942 | 0.052101 | 0.011611 | 0.10951 | 0.090161 | -0.026092 | 0.089116 | 0.16622 | 0.018672 | -0.097207 | 0.016188 | 0.04611 | -0.04722 | -0.00775 | 122.331 | 122.1824 | 122.2704 | 122.2299 | 122.3278 | 122.3085 | 122.1922 | 0.112 | 0.1891 | 0.04156 | -0.074319 | 0.039076 | 0.068998 | -0.024332 | 0.015138 | 0.072928 | 0.13634 | 0.002484 | 0.065892
2143.8125 | 122.4564 | -122.2046 | 0.11902 | 0.10812 | -0.040521 | 0.061258 | 0.007033 | 0.10493 | 0.09474 | -0.026092 | 0.093694 | 0.16622 | 0.02325 | -0.11094 | 0.020767 | 0.055266 | -0.04722 | -0.016906 | 122.3127 | 122.1641 | 122.2658 | 122.2116 | 122.3095 | 122.2993 | 122.1785 | 0.11658 | 0.1891 | 0.046138 | -0.088056 | 0.043655 | 0.078154 | -0.024332 | 0.005982 | 0.072927 | 0.14091 | 0.002483 | 0.07047
2145.5 | 122.5067 | -122.1863 | 0.082397 | 0.10812 | -0.040521 | 0.052101 | 0.007033 | 0.10036 | 0.090161 | -0.026092 | 0.089116 | 0.16622 | 0.018672 | -0.11094 | 0.029923 | 0.055266 | -0.051798 | -0.00775 | 122.2944 | 122.1458 | 122.2384 | 122.1933 | 122.2866 | 122.2764 | 122.1602 | 0.112 | 0.1891 | 0.04156 | -0.088056 | 0.052811 | 0.078154 | -0.02891 | 0.015138 | 0.059193 | 0.14091 | -0.011251 | 0.07047
2147.2031 | 122.3694 | -122.2549 | 0.13275 | 0.11269 | -0.040521 | 0.061258 | 0.007033 | 0.10951 | 0.09474 | -0.026092 | 0.079959 | 0.16164 | 0.018672 | -0.11552 | 0.034501 | 0.064423 | -0.056376 | -0.012328 | 122.3676 | 122.2144 | 122.3162 | 122.262 | 122.3645 | 122.3497 | 122.2289 | 0.10285 | 0.18452 | 0.04156 | -0.092635 | 0.057389 | 0.087311 | -0.033488 | 0.01056 | 0.045458 | 0.13634 | -0.015829 | 0.075048
2148.9688 | 122.4564 | -122.1954 | 0.10071 | 0.10812 | -0.0451 | 0.052101 | 0.01619 | 0.10493 | 0.09474 | -0.03067 | 0.089116 | 0.17537 | 0.02325 | -0.10179 | 0.025345 | 0.055266 | -0.056376 | -0.012328 | 122.3036 | 122.1503 | 122.2475 | 122.2116 | 122.3004 | 122.2902 | 122.1648 | 0.112 | 0.19826 | 0.046138 | -0.078898 | 0.048233 | 0.078154 | -0.033488 | 0.01056 | 0.063771 | 0.14549 | -0.002095 | 0.079626
2150.7188 | 122.4609 | -122.2366 | 0.10529 | 0.11727 | -0.040521 | 0.061258 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.089116 | 0.17079 | 0.018672 | -0.11094 | 0.029923 | 0.069001 | -0.060955 | -0.00775 | 122.3539 | 122.1961 | 122.2979 | 122.2391 | 122.3461 | 122.3222 | 122.2105 | 0.112 | 0.19368 | 0.04156 | -0.088056 | 0.052811 | 0.091889 | -0.038067 | 0.015138 | 0.059193 | 0.15007 | -0.011251 | 0.079627
2152.4219 | 122.4106 | -122.2504 | 0.11902 | 0.11269 | -0.040521 | 0.056679 | 0.007033 | 0.10493 | 0.09474 | -0.021514 | 0.089116 | 0.17079 | 0.018672 | -0.11094 | 0.080283 | 0.13309 | -0.056376 | -0.012328 | 122.3631 | 122.2098 | 122.307 | 122.2574 | 122.3553 | 122.3451 | 122.2289 | 0.112 | 0.19368 | 0.04156 | -0.088056 | 0.10317 | 0.15598 | -0.033488 | 0.01056 | 0.008833 | 0.14549 | -0.061611 | 0.075048
2154.1719 | 122.4747 | -122.2549 | 0.10986 | 0.11269 | -0.049678 | 0.052101 | 0.002454 | 0.10493 | 0.090161 | -0.03067 | 0.084537 | 0.16622 | 0.027829 | -0.10179 | 0.084861 | 0.13767 | -0.056376 | -0.012328 | 122.3676 | 122.2053 | 122.307 | 122.2574 | 122.3599 | 122.3451 | 122.2243 | 0.10742 | 0.1891 | 0.050717 | -0.078898 | 0.10775 | 0.16056 | -0.033488 | 0.01056 | -0.000324 | 0.14091 | -0.057032 | 0.084205
2155.875 | 122.5159 | -122.2046 | 0.091553 | 0.12185 | -0.040521 | 0.052101 | 0.007033 | 0.10493 | 0.09474 | -0.021514 | 0.089116 | 0.17079 | 0.027829 | -0.10637 | 0.048236 | 0.096469 | -0.051798 | -0.012328 | 122.3264 | 122.1641 | 122.2567 | 122.2116 | 122.3095 | 122.2993 | 122.1831 | 0.112 | 0.19368 | 0.050717 | -0.083477 | 0.071124 | 0.11936 | -0.02891 | 0.01056 | 0.04088 | 0.14091 | -0.020407 | 0.079627
2157.6406 | 122.4609 | -122.2549 | 0.13733 | 0.11269 | -0.040521 | 0.061258 | 0.011611 | 0.10493 | 0.090161 | -0.021514 | 0.084537 | 0.17079 | 0.02325 | -0.11094 | 0.057392 | 0.096469 | -0.060955 | -0.012328 | 122.3676 | 122.2144 | 122.3162 | 122.2666 | 122.3599 | 122.3451 | 122.2334 | 0.10742 | 0.19368 | 0.046138 | -0.088056 | 0.08028 | 0.11936 | -0.038067 | 0.01056 | 0.027145 | 0.14549 | -0.034142 | 0.084205
2159.4062 | 122.525 | -122.2 | 0.10986 | 0.11727 | -0.049678 | 0.052101 | 0.002454 | 0.10493 | 0.085583 | -0.026092 | 0.089116 | 0.17079 | 0.014094 | -0.10179 | 0.071126 | 0.11478 | -0.056376 | -0.016906 | 122.3173 | 122.1503 | 122.2521 | 122.2025 | 122.3049 | 122.2856 | 122.1739 | 0.112 | 0.19368 | 0.036982 | -0.078898 | 0.094014 | 0.13767 | -0.033488 | 0.005982 | 0.01799 | 0.14549 | -0.057032 | 0.07047
2161.0938 | 122.4106 | -122.2641 | 0.13275 | 0.11727 | -0.0451 | 0.056679 | 0.011611 | 0.10493 | 0.09474 | -0.035248 | 0.093694 | 0.17079 | 0.027829 | -0.11552 | 0.066548 | 0.11478 | -0.056376 | -0.012328 | 122.3814 | 122.219 | 122.3208 | 122.2757 | 122.369 | 122.3588 | 122.2289 | 0.11658 | 0.19368 | 0.050717 | -0.092635 | 0.089436 | 0.13767 | -0.033488 | 0.01056 | 0.027146 | 0.15007 | -0.038719 | 0.084205
2162.8438 | 122.5342 | -122.2366 | 0.10529 | 0.11269 | -0.0451 | 0.061258 | 0.002454 | 0.10493 | 0.09474 | -0.026092 | 0.089116 | 0.17079 | 0.027829 | -0.10179 | 0.06197 | 0.1102 | -0.051798 | -0.012328 | 122.3493 | 122.1915 | 122.2979 | 122.2391 | 122.3416 | 122.3314 | 122.2105 | 0.112 | 0.19368 | 0.050717 | -0.078898 | 0.084858 | 0.13309 | -0.02891 | 0.01056 | 0.027146 | 0.14091 | -0.034141 | 0.079627
2164.6094 | 122.3923 | -122.2961 | 0.14191 | 0.11269 | -0.040521 | 0.056679 | 0.007033 | 0.10951 | 0.085583 | -0.021514 | 0.084537 | 0.17079 | 0.027829 | -0.11094 | 0.029923 | 0.059844 | -0.056376 | -0.021484 | 122.4088 | 122.2556 | 122.3528 | 122.3032 | 122.4057 | 122.3817 | 122.2746 | 0.10742 | 0.19368 | 0.050717 | -0.088056 | 0.052811 | 0.082732 | -0.033488 | 0.001404 | 0.054614 | 0.14091 | -0.002094 | 0.084205
2166.3594 | 122.5342 | -122.2275 | 0.091553 | 0.11269 | -0.040521 | 0.056679 | 0.002454 | 0.10036 | 0.085583 | -0.03067 | 0.098273 | 0.17995 | 0.027829 | -0.10637 | 0.029923 | 0.055266 | -0.056376 | -0.00775 | 122.3402 | 122.187 | 122.2842 | 122.2299 | 122.3278 | 122.3131 | 122.1968 | 0.12116 | 0.20284 | 0.050717 | -0.083477 | 0.052811 | 0.078154 | -0.033488 | 0.015138 | 0.06835 | 0.15465 | -0.002094 | 0.084205
2168.125 | 122.5433 | -122.2458 | 0.10071 | 0.11727 | -0.0451 | 0.056679 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.079959 | 0.16622 | 0.027829 | -0.11094 | 0.020767 | 0.050688 | -0.060955 | -0.00775 | 122.3631 | 122.2007 | 122.3025 | 122.2528 | 122.3553 | 122.3314 | 122.2197 | 0.10285 | 0.1891 | 0.050717 | -0.088056 | 0.043655 | 0.073576 | -0.038067 | 0.015138 | 0.059192 | 0.14091 | 0.007062 | 0.088784
2169.875 | 122.5204 | -122.2549 | 0.10986 | 0.11269 | -0.040521 | 0.056679 | 0.007033 | 0.11867 | 0.090161 | -0.03067 | 0.089116 | 0.17079 | 0.032407 | -0.1201 | 0.025345 | 0.04611 | -0.051798 | -0.012328 | 122.3676 | 122.2144 | 122.3116 | 122.262 | 122.3736 | 122.3451 | 122.2243 | 0.112 | 0.19368 | 0.055295 | -0.097215 | 0.048233 | 0.068998 | -0.02891 | 0.01056 | 0.063771 | 0.14091 | 0.007062 | 0.084205
2171.5625 | 122.4243 | -122.2961 | 0.13275 | 0.10812 | -0.049678 | 0.052101 | 0.002454 | 0.11409 | 0.09474 | -0.03067 | 0.084537 | 0.17537 | 0.02325 | -0.088049 | 0.016188 | 0.041532 | -0.060955 | -0.016906 | 122.4043 | 122.2465 | 122.3482 | 122.2986 | 122.4102 | 122.3909 | 122.2655 | 0.10742 | 0.19826 | 0.046138 | -0.065161 | 0.039076 | 0.06442 | -0.038067 | 0.005982 | 0.068349 | 0.14549 | 0.007062 | 0.084205
2173.3281 | 122.4518 | -122.2824 | 0.12817 | 0.10812 | -0.040521 | 0.061258 | 0.007033 | 0.10493 | 0.090161 | -0.021514 | 0.07538 | 0.17537 | 0.027829 | -0.10179 | 0.020767 | 0.041532 | -0.060955 | -0.00775 | 122.3905 | 122.2419 | 122.3437 | 122.2894 | 122.3873 | 122.3726 | 122.2609 | 0.098268 | 0.19826 | 0.050717 | -0.078898 | 0.043655 | 0.06442 | -0.038067 | 0.015138 | 0.054613 | 0.13634 | 0.007062 | 0.088784
2175.0781 | 122.438 | -122.319 | 0.13275 | 0.11269 | -0.035942 | 0.052101 | 0.007033 | 0.10493 | 0.090161 | -0.026092 | 0.089116 | 0.17079 | 0.032407 | -0.10637 | 0.016188 | 0.041532 | -0.056376 | 0.001406 | 122.4317 | 122.2831 | 122.3711 | 122.3261 | 122.424 | 122.4092 | 122.2929 | 0.112 | 0.19368 | 0.055295 | -0.083477 | 0.039076 | 0.06442 | -0.033488 | 0.024294 | 0.072928 | 0.14549 | 0.016219 | 0.088783
2176.8281 | 122.5708 | -122.2641 | 0.10071 | 0.11269 | -0.040521 | 0.047522 | 0.002454 | 0.10951 | 0.081005 | -0.021514 | 0.079959 | 0.17537 | 0.032407 | -0.11094 | 0.016188 | 0.041532 | -0.051798 | -0.012328 | 122.3768 | 122.2236 | 122.3116 | 122.2666 | 122.3736 | 122.3451 | 122.2426 | 0.10285 | 0.19826 | 0.055295 | -0.088056 | 0.039076 | 0.06442 | -0.02891 | 0.01056 | 0.063771 | 0.13176 | 0.016219 | 0.084205
2178.5312 | 122.5342 | -122.2366 | 0.10529 | 0.11269 | -0.040521 | 0.052101 | 0.002454 | 0.10951 | 0.085583 | -0.03067 | 0.084537 | 0.16622 | 0.02325 | -0.11094 | 0.016188 | 0.036954 | -0.051798 | -0.012328 | 122.3493 | 122.1961 | 122.2887 | 122.2391 | 122.3461 | 122.3222 | 122.206 | 0.10742 | 0.1891 | 0.046138 | -0.088056 | 0.039076 | 0.059842 | -0.02891 | 0.01056 | 0.068349 | 0.13633 | 0.007062 | 0.075048
2180.2969 | 122.5479 | -122.2687 | 0.09613 | 0.10812 | -0.0451 | 0.056679 | -0.002124 | 0.10036 | 0.090161 | -0.03067 | 0.079959 | 0.17537 | 0.018672 | -0.11552 | 0.020767 | 0.041532 | -0.056376 | -0.00775 | 122.3768 | 122.2236 | 122.3254 | 122.2666 | 122.369 | 122.3588 | 122.238 | 0.10285 | 0.19826 | 0.04156 | -0.092635 | 0.043655 | 0.06442 | -0.033488 | 0.015138 | 0.059192 | 0.13634 | -0.002095 | 0.075048
2182 | 122.4518 | -122.2961 | 0.11902 | 0.11269 | -0.0451 | 0.047522 | 0.002454 | 0.10493 | 0.09474 | -0.03067 | 0.084537 | 0.17079 | 0.02325 | -0.11094 | 0.016188 | 0.04611 | -0.051798 | -0.016906 | 122.4088 | 122.251 | 122.3437 | 122.2986 | 122.4011 | 122.3909 | 122.2655 | 0.10742 | 0.19368 | 0.046138 | -0.088056 | 0.039076 | 0.068998 | -0.02891 | 0.005982 | 0.068349 | 0.13633 | 0.007062 | 0.075048
2183.7656 | 122.4792 | -122.2961 | 0.1236 | 0.10812 | -0.040521 | 0.056679 | 0.002454 | 0.11409 | 0.090161 | -0.026092 | 0.084537 | 0.16622 | 0.02325 | -0.11094 | 0.020767 | 0.036954 | -0.060955 | -0.012328 | 122.4043 | 122.2556 | 122.3528 | 122.2986 | 122.4102 | 122.3863 | 122.2701 | 0.10742 | 0.1891 | 0.046138 | -0.088056 | 0.043655 | 0.059842 | -0.038067 | 0.01056 | 0.06377 | 0.14549 | 0.002483 | 0.084205
2185.5312 | 122.4472 | -122.3282 | 0.13733 | 0.10354 | -0.0451 | 0.052101 | 0.002454 | 0.10951 | 0.090161 | -0.021514 | 0.089116 | 0.16164 | 0.02325 | -0.11094 | 0.020767 | 0.04611 | -0.051798 | -0.00775 | 122.4317 | 122.2831 | 122.3803 | 122.3306 | 122.4377 | 122.4183 | 122.3067 | 0.112 | 0.18452 | 0.046138 | -0.088056 | 0.043655 | 0.068998 | -0.02891 | 0.015138 | 0.068349 | 0.14091 | 0.002483 | 0.075048
2187.2812 | 122.5159 | -122.3236 | 0.11902 | 0.11727 | -0.0451 | 0.061258 | 0.002454 | 0.10493 | 0.09474 | -0.026092 | 0.089116 | 0.16164 | 0.02325 | -0.11094 | 0.025345 | 0.050688 | -0.056376 | -0.00775 | 122.4409 | 122.2785 | 122.3849 | 122.3261 | 122.4285 | 122.4183 | 122.2975 | 0.112 | 0.18452 | 0.046138 | -0.088056 | 0.048233 | 0.073576 | -0.033488 | 0.015138 | 0.063771 | 0.14549 | -0.002095 | 0.079626
2189.0469 | 122.5204 | -122.3099 | 0.10986 | 0.11269 | -0.0451 | 0.056679 | 0.007033 | 0.10951 | 0.09474 | -0.026092 | 0.089116 | 0.16622 | 0.027829 | -0.10637 | 0.01161 | 0.027798 | -0.051798 | -0.012328 | 122.4226 | 122.2648 | 122.3666 | 122.3169 | 122.4194 | 122.4046 | 122.2838 | 0.112 | 0.1891 | 0.050717 | -0.083477 | 0.034498 | 0.050686 | -0.02891 | 0.01056 | 0.077506 | 0.14091 | 0.016219 | 0.079627
2190.8125 | 122.4564 | -122.3145 | 0.13733 | 0.11727 | -0.040521 | 0.056679 | 0.007033 | 0.10493 | 0.090161 | -0.026092 | 0.079959 | 0.17079 | 0.032407 | -0.11094 | 0.01161 | 0.02322 | -0.051798 | -0.012328 | 122.4317 | 122.2739 | 122.3711 | 122.3215 | 122.4194 | 122.4046 | 122.2884 | 0.10285 | 0.19368 | 0.055295 | -0.088056 | 0.034498 | 0.046108 | -0.02891 | 0.01056 | 0.068349 | 0.13176 | 0.020797 | 0.084205
2192.5312 | 122.5433 | -122.3099 | 0.10529 | 0.11269 | -0.049678 | 0.056679 | 0.002454 | 0.10493 | 0.085583 | -0.026092 | 0.089116 | 0.17079 | 0.02325 | -0.10179 | 0.01161 | 0.027798 | -0.060955 | -0.012328 | 122.4226 | 122.2602 | 122.3666 | 122.3123 | 122.4148 | 122.3955 | 122.2838 | 0.112 | 0.19368 | 0.046138 | -0.078898 | 0.034498 | 0.050686 | -0.038067 | 0.01056 | 0.077506 | 0.15007 | 0.01164 | 0.084205
2194.2969 | 122.4884 | -122.319 | 0.11444 | 0.10812 | -0.040521 | 0.061258 | 0.002454 | 0.10493 | 0.090161 | -0.026092 | 0.079959 | 0.17079 | 0.027829 | -0.092628 | 0.01161 | 0.027798 | -0.060955 | -0.016906 | 122.4271 | 122.2785 | 122.3803 | 122.3215 | 122.424 | 122.4092 | 122.2929 | 0.10285 | 0.19368 | 0.050717 | -0.06974 | 0.034498 | 0.050686 | -0.038067 | 0.005982 | 0.068349 | 0.14091 | 0.016219 | 0.088784
2196.0625 | 122.5433 | -122.3328 | 0.091553 | 0.11727 | -0.0451 | 0.047522 | 0.002454 | 0.10951 | 0.085583 | -0.021514 | 0.084537 | 0.17079 | 0.02325 | -0.10637 | 0.002454 | 0.027798 | -0.056376 | -0.016906 | 122.45 | 122.2877 | 122.3803 | 122.3352 | 122.4423 | 122.4183 | 122.3113 | 0.10742 | 0.19368 | 0.046138 | -0.083477 | 0.025342 | 0.050686 | -0.033488 | 0.005982 | 0.082083 | 0.14091 | 0.020796 | 0.079626
2197.75 | 122.5571 | -122.3328 | 0.10071 | 0.11727 | -0.0451 | 0.065837 | 0.002454 | 0.095778 | 0.090161 | -0.026092 | 0.084537 | 0.16622 | 0.02325 | -0.092628 | 0.01161 | 0.036954 | -0.056376 | -0.021484 | 122.45 | 122.2877 | 122.3986 | 122.3352 | 122.4285 | 122.4229 | 122.3067 | 0.10742 | 0.1891 | 0.046138 | -0.06974 | 0.034498 | 0.059842 | -0.033488 | 0.001404 | 0.072927 | 0.14091 | 0.01164 | 0.079626
2199.5 | 122.5479 | -122.3465 | 0.1236 | 0.10812 | -0.0451 | 0.052101 | 0.007033 | 0.10951 | 0.090161 | -0.03067 | 0.089116 | 0.16622 | 0.027829 | -0.10179 | 0.016188 | 0.032376 | -0.065533 | -0.016906 | 122.4546 | 122.3014 | 122.3986 | 122.3535 | 122.456 | 122.4367 | 122.3158 | 0.112 | 0.1891 | 0.050717 | -0.078898 | 0.039076 | 0.055264 | -0.042645 | 0.005982 | 0.072928 | 0.15465 | 0.011641 | 0.093362
2201.25 | 122.612 | -122.3053 | 0.09613 | 0.10812 | -0.054257 | 0.061258 | -0.006703 | 0.10493 | 0.085583 | -0.03067 | 0.084537 | 0.16622 | 0.02325 | -0.10179 | 0.016188 | 0.032376 | -0.060955 | -0.012328 | 122.4134 | 122.251 | 122.3666 | 122.2986 | 122.4102 | 122.3909 | 122.2746 | 0.10742 | 0.1891 | 0.046138 | -0.078898 | 0.039076 | 0.055264 | -0.038067 | 0.01056 | 0.068349 | 0.14549 | 0.007062 | 0.084205
2202.9531 | 122.493 | -122.3465 | 0.1236 | 0.10812 | -0.049678 | 0.056679 | 0.002454 | 0.10951 | 0.081005 | -0.035248 | 0.089116 | 0.17079 | 0.018672 | -0.10637 | 0.01161 | 0.027798 | -0.056376 | -0.00775 | 122.4546 | 122.2968 | 122.4032 | 122.349 | 122.456 | 122.4275 | 122.3112 | 0.112 | 0.19368 | 0.04156 | -0.083477 | 0.034498 | 0.050686 | -0.033488 | 0.015138 | 0.077506 | 0.14549 | 0.007062 | 0.075048
2204.7031 | 122.5021 | -122.3557 | 0.12817 | 0.11727 | -0.0451 | 0.056679 | 0.007033 | 0.11409 | 0.09474 | -0.021514 | 0.084537 | 0.16622 | 0.02325 | -0.10637 | 0.01161 | 0.036954 | -0.056376 | -0.00775 | 122.4729 | 122.3106 | 122.4123 | 122.3627 | 122.4697 | 122.4504 | 122.3341 | 0.10742 | 0.1891 | 0.046138 | -0.083477 | 0.034498 | 0.059842 | -0.033488 | 0.015138 | 0.072927 | 0.14091 | 0.01164 | 0.079626
2206.4531 | 122.5388 | -122.3419 | 0.10986 | 0.11727 | -0.040521 | 0.056679 | 0.007033 | 0.11409 | 0.090161 | -0.016936 | 0.079959 | 0.16164 | 0.018672 | -0.1201 | 0.020767 | 0.036954 | -0.060955 | -0.012328 | 122.4592 | 122.3014 | 122.3986 | 122.349 | 122.456 | 122.4321 | 122.325 | 0.10285 | 0.18452 | 0.04156 | -0.097215 | 0.043655 | 0.059842 | -0.038067 | 0.01056 | 0.059192 | 0.14091 | -0.002095 | 0.079627
2208.2031 | 122.5525 | -122.3602 | 0.10529 | 0.10812 | -0.0451 | 0.056679 | 0.007033 | 0.10951 | 0.090161 | -0.026092 | 0.089116 | 0.17079 | 0.02325 | -0.11094 | 0.01161 | 0.041532 | -0.060955 | -0.00775 | 122.4683 | 122.3151 | 122.4169 | 122.3673 | 122.4697 | 122.4504 | 122.3341 | 0.112 | 0.19368 | 0.046138 | -0.088056 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.077506 | 0.15007 | 0.01164 | 0.084205
2209.9531 | 122.5479 | -122.3511 | 0.1236 | 0.002813 | -0.15499 | -0.048628 | -0.093694 | 0.004219 | -0.015142 | -0.12681 | 0.084537 | 0.17079 | 0.02325 | -0.10637 | 0.01161 | 0.036954 | -0.060955 | -0.016906 | 122.3539 | 122.1961 | 122.3024 | 122.2574 | 122.3553 | 122.3359 | 122.2243 | 0.10742 | 0.19368 | 0.046138 | -0.083477 | 0.034498 | 0.059842 | -0.038067 | 0.005982 | 0.072927 | 0.14549 | 0.01164 | 0.084205
2211.6562 | 122.6257 | -122.3145 | 0.10071 | 0.11727 | -0.0451 | 0.047522 | 0.007033 | 0.10493 | 0.085583 | -0.026092 | 0.084537 | 0.17079 | 0.014094 | -0.10637 | 0.016188 | 0.027798 | -0.056376 | -0.003172 | 122.4317 | 122.2694 | 122.362 | 122.3215 | 122.4194 | 122.4 | 122.2884 | 0.10742 | 0.19368 | 0.036982 | -0.083477 | 0.039076 | 0.050686 | -0.033488 | 0.019716 | 0.068349 | 0.14091 | -0.002094 | 0.07047
2213.4219 | 122.5891 | -122.3511 | 0.10529 | 0.11269 | -0.0451 | 0.056679 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.084537 | 0.17079 | 0.02325 | -0.10637 | 0.007032 | 0.02322 | -0.051798 | -0.016906 | 122.4638 | 122.306 | 122.4078 | 122.3535 | 122.4514 | 122.4321 | 122.3204 | 0.10742 | 0.19368 | 0.046138 | -0.083477 | 0.02992 | 0.046108 | -0.02891 | 0.005982 | 0.077505 | 0.13633 | 0.016218 | 0.075048
2215.1875 | 122.5204 | -122.374 | 0.11902 | 0.11727 | -0.0451 | 0.056679 | 0.002454 | 0.11409 | 0.085583 | -0.026092 | 0.070802 | 0.17079 | 0.032407 | -0.074312 | 0.016188 | 0.032376 | -0.060955 | -0.016906 | 122.4912 | 122.3289 | 122.4306 | 122.3764 | 122.4881 | 122.4595 | 122.3479 | 0.09369 | 0.19368 | 0.055295 | -0.051424 | 0.039076 | 0.055264 | -0.038067 | 0.005982 | 0.054614 | 0.13176 | 0.016219 | 0.093362
2216.9531 | 122.58 | -122.374 | 0.1236 | 0.11269 | -0.0451 | 0.056679 | 0.007033 | 0.11409 | 0.09474 | -0.026092 | 0.084537 | 0.16164 | 0.018672 | -0.11094 | 0.01161 | 0.032376 | -0.051798 | -0.021484 | 122.4867 | 122.3289 | 122.4306 | 122.381 | 122.4881 | 122.4687 | 122.3479 | 0.10742 | 0.18452 | 0.04156 | -0.088056 | 0.034498 | 0.055264 | -0.02891 | 0.001404 | 0.072927 | 0.13633 | 0.007062 | 0.07047
2218.6562 | 122.6212 | -122.3465 | 0.10986 | -0.015501 | -0.15499 | -0.062364 | -0.10743 | -0.004937 | -0.01972 | -0.13597 | 0.089116 | 0.16622 | 0.018672 | -0.10179 | 0.016188 | 0.036954 | -0.056376 | -0.012328 | 122.331 | 122.1915 | 122.2841 | 122.2391 | 122.3416 | 122.3268 | 122.2105 | 0.112 | 0.1891 | 0.04156 | -0.078898 | 0.039076 | 0.059842 | -0.033488 | 0.01056 | 0.072928 | 0.14549 | 0.002484 | 0.075048
2220.4219 | 122.644 | -122.3831 | 0.09613 | -0.006344 | -0.15041 | -0.062364 | -0.10743 | -0.009515 | -0.01972 | -0.13139 | 0.084537 | 0.17079 | 0.027829 | -0.11552 | 0.016188 | 0.032376 | -0.060955 | -0.00775 | 122.3768 | 122.2327 | 122.3208 | 122.2757 | 122.3736 | 122.3634 | 122.2517 | 0.10742 | 0.19368 | 0.050717 | -0.092635 | 0.039076 | 0.055264 | -0.038067 | 0.015138 | 0.068349 | 0.14549 | 0.011641 | 0.088784
2222.1719 | 122.6761 | -122.3648 | 0.09613 | 0.11269 | -0.0451 | 0.061258 | 0.007033 | 0.11409 | 0.085583 | -0.026092 | 0.084537 | 0.17079 | 0.018672 | -0.10637 | 0.002454 | 0.027798 | -0.060955 | -0.012328 | 122.4775 | 122.3197 | 122.4261 | 122.3718 | 122.4789 | 122.4504 | 122.3387 | 0.10742 | 0.19368 | 0.04156 | -0.083477 | 0.025342 | 0.050686 | -0.038067 | 0.01056 | 0.082083 | 0.14549 | 0.016218 | 0.079627
2223.9219 | 122.5067 | -122.4152 | 0.11902 | 0.10354 | -0.049678 | 0.056679 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.079959 | 0.17079 | 0.02325 | -0.10179 | 0.01161 | 0.032376 | -0.056376 | -0.016906 | 122.5187 | 122.3655 | 122.4718 | 122.4222 | 122.5247 | 122.5007 | 122.3891 | 0.10285 | 0.19368 | 0.046138 | -0.078898 | 0.034498 | 0.055264 | -0.033488 | 0.005982 | 0.068349 | 0.13634 | 0.01164 | 0.079626
2225.6875 | 122.6212 | -122.3511 | 0.1236 | 0.11727 | -0.049678 | 0.061258 | 0.002454 | 0.10036 | 0.081005 | -0.026092 | 0.079959 | 0.15706 | 0.014094 | -0.11094 | 0.016188 | 0.032376 | -0.051798 | -0.016906 | 122.4683 | 122.3014 | 122.4123 | 122.3535 | 122.4514 | 122.4321 | 122.325 | 0.10285 | 0.17994 | 0.036982 | -0.088056 | 0.039076 | 0.055264 | -0.02891 | 0.005982 | 0.063771 | 0.13176 | -0.002094 | 0.065892
2227.375 | 122.5342 | -122.4243 | 0.11902 | 0.085224 | -0.072572 | 0.033786 | -0.020438 | 0.086622 | 0.062691 | -0.058139 | 0.084537 | 0.16622 | 0.02325 | -0.11094 | 0.007032 | 0.032376 | -0.056376 | -0.021484 | 122.5095 | 122.3517 | 122.4581 | 122.4039 | 122.5109 | 122.487 | 122.3662 | 0.10742 | 0.1891 | 0.046138 | -0.088056 | 0.02992 | 0.055264 | -0.033488 | 0.001404 | 0.077505 | 0.14091 | 0.016218 | 0.079626
2229.1562 | 122.5388 | -122.4197 | 0.13275 | 0.11727 | -0.049678 | 0.056679 | 0.002454 | 0.10951 | 0.09474 | -0.026092 | 0.079959 | 0.16622 | 0.02325 | -0.11094 | 0.01161 | 0.032376 | -0.056376 | -0.016906 | 122.537 | 122.3701 | 122.4764 | 122.4222 | 122.5293 | 122.5145 | 122.3936 | 0.10285 | 0.1891 | 0.046138 | -0.088056 | 0.034498 | 0.055264 | -0.033488 | 0.005982 | 0.068349 | 0.13634 | 0.01164 | 0.079626
2230.9219 | 122.58 | -122.406 | 0.11902 | -0.006344 | -0.15499 | -0.053207 | -0.10743 | -0.000359 | -0.005985 | -0.12681 | 0.07538 | 0.16164 | 0.018672 | -0.11552 | 0.016188 | 0.027798 | -0.060955 | -0.012328 | 122.3997 | 122.251 | 122.3528 | 122.2986 | 122.4056 | 122.4 | 122.2792 | 0.098268 | 0.18452 | 0.04156 | -0.092635 | 0.039076 | 0.050686 | -0.038067 | 0.01056 | 0.059192 | 0.13634 | 0.002484 | 0.079627
2232.625 | 122.6028 | -122.406 | 0.1236 | -0.006344 | -0.15499 | -0.057786 | -0.11201 | -0.004937 | -0.024298 | -0.13139 | 0.084537 | 0.16622 | 0.032407 | -0.11094 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 122.3997 | 122.251 | 122.3482 | 122.294 | 122.4011 | 122.3817 | 122.2746 | 0.10742 | 0.1891 | 0.055295 | -0.088056 | 0.034498 | 0.059842 | -0.042645 | 0.01056 | 0.072927 | 0.15007 | 0.020797 | 0.09794
2234.3906 | 122.6761 | -122.3923 | 0.09613 | -0.006344 | -0.15041 | -0.062364 | -0.11201 | 0.004219 | -0.01972 | -0.14055 | 0.084537 | 0.16622 | 0.02325 | -0.11094 | 0.016188 | 0.027798 | -0.056376 | -0.016906 | 122.3859 | 122.2419 | 122.3299 | 122.2803 | 122.3965 | 122.3726 | 122.2517 | 0.10742 | 0.1891 | 0.046138 | -0.088056 | 0.039076 | 0.050686 | -0.033488 | 0.005982 | 0.068349 | 0.14091 | 0.007062 | 0.079626
2236.0938 | 122.58 | -122.4197 | 0.10986 | -0.006344 | -0.15957 | -0.062364 | -0.11201 | -0.000359 | -0.015142 | -0.13139 | 0.084537 | 0.16164 | 0.032407 | -0.11552 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.4134 | 122.2602 | 122.3574 | 122.3077 | 122.4194 | 122.4046 | 122.2883 | 0.10742 | 0.18452 | 0.055295 | -0.092635 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.077505 | 0.14549 | 0.025375 | 0.093362
2237.8438 | 122.6807 | -122.3694 | 0.10529 | -0.006344 | -0.15499 | -0.062364 | -0.10285 | -0.000359 | -0.015142 | -0.13139 | 0.084537 | 0.16622 | 0.027829 | -0.10637 | 0.01161 | 0.027798 | -0.060955 | -0.00775 | 122.363 | 122.2144 | 122.307 | 122.2665 | 122.369 | 122.3542 | 122.238 | 0.10742 | 0.1891 | 0.050717 | -0.083477 | 0.034498 | 0.050686 | -0.038067 | 0.015138 | 0.072927 | 0.14549 | 0.016219 | 0.088784
2239.5625 | 122.5571 | -122.4243 | 0.13275 | 0.10812 | -0.0451 | 0.056679 | 0.007033 | 0.10493 | 0.090161 | -0.03067 | 0.084537 | 0.17079 | 0.027829 | -0.11094 | 0.007032 | 0.036954 | -0.056376 | -0.00775 | 122.5324 | 122.3792 | 122.481 | 122.4313 | 122.5293 | 122.5145 | 122.3936 | 0.10742 | 0.19368 | 0.050717 | -0.088056 | 0.02992 | 0.059842 | -0.033488 | 0.015138 | 0.077505 | 0.14091 | 0.020797 | 0.084205
2241.3125 | 122.6303 | -122.3831 | 0.10529 | 0.007391 | -0.13668 | -0.053207 | -0.093694 | 0.008797 | -0.001406 | -0.1085 | 0.084537 | 0.17079 | 0.018672 | -0.1201 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.3905 | 122.2464 | 122.3299 | 122.2894 | 122.3919 | 122.3817 | 122.2746 | 0.10742 | 0.19368 | 0.04156 | -0.097215 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.077505 | 0.14549 | 0.01164 | 0.079627
2243.0625 | 122.6761 | -122.3557 | 0.091553 | 0.11727 | -0.054257 | 0.056679 | 0.002454 | 0.10951 | 0.09474 | -0.021514 | 0.084537 | 0.16622 | 0.018672 | -0.10637 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.4729 | 122.3014 | 122.4123 | 122.3581 | 122.4652 | 122.4504 | 122.3341 | 0.10742 | 0.1891 | 0.04156 | -0.083477 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.077505 | 0.14549 | 0.01164 | 0.079627
2244.8281 | 122.6807 | -122.3969 | 0.10529 | 0.002813 | -0.14583 | -0.053207 | -0.10285 | -0.000359 | -0.010563 | -0.13139 | 0.07538 | 0.16622 | 0.02325 | -0.11094 | 0.016188 | 0.027798 | -0.051798 | -0.016906 | 122.3997 | 122.251 | 122.3436 | 122.294 | 122.3965 | 122.3863 | 122.2655 | 0.098268 | 0.1891 | 0.046138 | -0.088056 | 0.039076 | 0.050686 | -0.02891 | 0.005982 | 0.059192 | 0.12718 | 0.007062 | 0.075048
2246.5312 | 122.5479 | -122.4289 | 0.12817 | 0.002813 | -0.15041 | -0.053207 | -0.098273 | 0.008797 | -0.01972 | -0.13139 | 0.07538 | 0.16164 | 0.02325 | -0.11094 | 0.020767 | 0.036954 | -0.060955 | -0.016906 | 122.4317 | 122.2785 | 122.3757 | 122.3306 | 122.4377 | 122.4092 | 122.2975 | 0.098268 | 0.18452 | 0.046138 | -0.088056 | 0.043655 | 0.059842 | -0.038067 | 0.005982 | 0.054613 | 0.13634 | 0.002483 | 0.084205
2248.2969 | 122.612 | -122.3831 | 0.11902 | 0.007391 | -0.15041 | -0.053207 | -0.098273 | 0.004219 | -0.005985 | -0.12223 | 0.079959 | 0.16164 | 0.027829 | -0.10637 | 0.016188 | 0.032376 | -0.056376 | -0.016906 | 122.3905 | 122.2327 | 122.3299 | 122.2848 | 122.3873 | 122.3771 | 122.2609 | 0.10285 | 0.18452 | 0.050717 | -0.083477 | 0.039076 | 0.055264 | -0.033488 | 0.005982 | 0.063771 | 0.13634 | 0.011641 | 0.084205
2250 | 122.5616 | -122.438 | 0.13733 | 0.007391 | -0.14583 | -0.053207 | -0.098273 | 0.008797 | -0.015142 | -0.13139 | 0.084537 | 0.16622 | 0.018672 | -0.11552 | 0.01161 | 0.032376 | -0.060955 | -0.012328 | 122.4454 | 122.2922 | 122.3848 | 122.3398 | 122.4468 | 122.4229 | 122.3067 | 0.10742 | 0.1891 | 0.04156 | -0.092635 | 0.034498 | 0.055264 | -0.038067 | 0.01056 | 0.072927 | 0.14549 | 0.007062 | 0.079627
2251.7656 | 122.699 | -122.4014 | 0.10071 | 0.002813 | -0.15041 | -0.057786 | -0.10285 | 0.004219 | -0.010563 | -0.13139 | 0.084537 | 0.17079 | 0.018672 | -0.11094 | 0.01161 | 0.032376 | -0.065533 | -0.012328 | 122.4042 | 122.251 | 122.3436 | 122.2986 | 122.4056 | 122.3909 | 122.27 | 0.10742 | 0.19368 | 0.04156 | -0.088056 | 0.034498 | 0.055264 | -0.042645 | 0.01056 | 0.072927 | 0.15007 | 0.007062 | 0.084205
2253.5312 | 122.6852 | -122.406 | 0.091553 | 0.002813 | -0.15041 | -0.057786 | -0.098273 | 0.004219 | -0.015142 | -0.12681 | 0.079959 | 0.15706 | 0.027829 | -0.11094 | 0.002454 | 0.027798 | -0.060955 | -0.016906 | 122.4088 | 122.2556 | 122.3482 | 122.3077 | 122.4102 | 122.3909 | 122.2792 | 0.10285 | 0.17994 | 0.050717 | -0.088056 | 0.025342 | 0.050686 | -0.038067 | 0.005982 | 0.077505 | 0.14091 | 0.025375 | 0.088784
2255.2812 | 122.5845 | -122.287 | 0.07782 | 0.002813 | -0.14125 | -0.048628 | -0.093694 | 0.008797 | -0.010563 | -0.1085 | 0.10285 | 0.17537 | 0.091925 | 0.063059 | 0.007032 | 0.036954 | -0.056376 | -0.016906 | 122.2898 | 122.1457 | 122.2384 | 122.1933 | 122.2958 | 122.2764 | 122.1785 | 0.12574 | 0.19826 | 0.11481 | 0.085947 | 0.02992 | 0.059842 | -0.033488 | 0.005982 | 0.095819 | 0.15923 | 0.084893 | 0.1483
2257.0312 | 122.4335 | -122.0901 | 0.091553 | 0.007391 | -0.14583 | -0.048628 | -0.098273 | 0.013375 | -0.005985 | -0.12681 | 0.089116 | 0.17079 | 0.091925 | 0.049322 | 0.016188 | 0.027798 | -0.070112 | -0.016906 | 122.0975 | 121.9443 | 122.0415 | 121.9919 | 122.1035 | 122.0842 | 121.9633 | 0.112 | 0.19368 | 0.11481 | 0.07221 | 0.039076 | 0.050686 | -0.047224 | 0.005982 | 0.072928 | 0.15923 | 0.075737 | 0.16204
2258.7188 | 122.3694 | -122.2229 | 0.12817 | 0.01197 | -0.1321 | -0.039471 | -0.093694 | 0.017953 | 0.003172 | -0.11308 | 0.084537 | 0.17079 | 0.014094 | -0.088049 | 0.007032 | 0.027798 | -0.056376 | -0.021484 | 122.2349 | 122.0908 | 122.1834 | 122.1292 | 122.2409 | 122.2261 | 122.1098 | 0.10742 | 0.19368 | 0.036982 | -0.065161 | 0.02992 | 0.050686 | -0.033488 | 0.001404 | 0.077505 | 0.14091 | 0.007062 | 0.07047
2260.4688 | 122.4976 | -122.2 | 0.082397 | 0.12643 | -0.040521 | 0.047522 | 0.007033 | 0.10493 | 0.085583 | -0.021514 | 0.084537 | 0.17079 | 0.02325 | -0.08347 | 0.007032 | 0.032376 | -0.056376 | -0.021484 | 122.3264 | 122.1595 | 122.2475 | 122.207 | 122.3049 | 122.2856 | 122.1785 | 0.10742 | 0.19368 | 0.046138 | -0.060582 | 0.02992 | 0.055264 | -0.033488 | 0.001404 | 0.077505 | 0.14091 | 0.016218 | 0.079626
2262.2188 | 122.5388 | -122.2137 | 0.091553 | 0.11727 | -0.049678 | 0.038365 | 0.007033 | 0.10951 | 0.085583 | -0.021514 | 0.079959 | 0.17079 | 0.02325 | -0.11094 | 0.01161 | 0.032376 | -0.056376 | -0.00775 | 122.331 | 122.1641 | 122.2521 | 122.2208 | 122.3233 | 122.2993 | 122.1922 | 0.10285 | 0.19368 | 0.046138 | -0.088056 | 0.034498 | 0.055264 | -0.033488 | 0.015138 | 0.068349 | 0.13634 | 0.01164 | 0.079626
2263.9844 | 122.5113 | -122.2641 | 0.09613 | 0.12185 | -0.0451 | 0.042944 | 0.007033 | 0.10951 | 0.09474 | -0.035248 | 0.079959 | 0.16622 | 0.027829 | -0.11094 | 0.007032 | 0.02322 | -0.065533 | -0.012328 | 122.386 | 122.219 | 122.307 | 122.2711 | 122.3736 | 122.3588 | 122.2289 | 0.10285 | 0.1891 | 0.050717 | -0.088056 | 0.02992 | 0.046108 | -0.042645 | 0.01056 | 0.072927 | 0.14549 | 0.020797 | 0.093362
2265.6719 | 122.5113 | -122.2549 | 0.10986 | 0.12185 | -0.0451 | 0.052101 | 0.007033 | 0.11867 | 0.09474 | -0.035248 | 0.079959 | 0.17079 | 0.018672 | -0.11552 | 0.01161 | 0.027798 | -0.056376 | -0.021484 | 122.3768 | 122.2098 | 122.307 | 122.262 | 122.3736 | 122.3497 | 122.2197 | 0.10285 | 0.19368 | 0.04156 | -0.092635 | 0.034498 | 0.050686 | -0.033488 | 0.001404 | 0.068349 | 0.13634 | 0.007062 | 0.075048
2267.4219 | 122.5479 | -122.3007 | 0.10986 | 0.021127 | -0.12752 | -0.04405 | -0.084537 | 0.013375 | -0.005985 | -0.11308 | 0.089116 | 0.17537 | 0.02325 | -0.097207 | 0.007032 | 0.032376 | -0.060955 | -0.00775 | 122.3218 | 122.1732 | 122.2567 | 122.2162 | 122.3141 | 122.2947 | 122.1876 | 0.112 | 0.19826 | 0.046138 | -0.074319 | 0.02992 | 0.055264 | -0.038067 | 0.015138 | 0.082084 | 0.15007 | 0.016218 | 0.084205
2269.1875 | 122.5983 | -122.2641 | 0.10071 | 0.021127 | -0.1321 | -0.053207 | -0.089116 | 0.013375 | -0.005985 | -0.11765 | 0.07538 | 0.17079 | 0.027829 | -0.097207 | 0.01161 | 0.032376 | -0.060955 | -0.012328 | 122.2852 | 122.132 | 122.2109 | 122.175 | 122.2775 | 122.2581 | 122.1464 | 0.098268 | 0.19368 | 0.050717 | -0.074319 | 0.034498 | 0.055264 | -0.038067 | 0.01056 | 0.06377 | 0.13634 | 0.016219 | 0.088784
2270.9375 | 122.5388 | -122.3328 | 0.11444 | 0.007391 | -0.14125 | -0.04405 | -0.084537 | 0.008797 | -0.005985 | -0.11765 | 0.079959 | 0.16622 | 0.032407 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.016906 | 122.3402 | 122.1915 | 122.2887 | 122.2482 | 122.3416 | 122.3268 | 122.2151 | 0.10285 | 0.1891 | 0.055295 | -0.083477 | 0.034498 | 0.059842 | -0.042645 | 0.005982 | 0.068349 | 0.14549 | 0.020797 | 0.09794
2272.625 | 122.5021 | -122.3145 | 0.11444 | 0.021127 | -0.12752 | -0.04405 | -0.093694 | 0.017953 | -0.001406 | -0.11765 | 0.079959 | 0.17079 | 0.036985 | -0.097207 | 0.007032 | 0.032376 | -0.060955 | -0.012328 | 122.3356 | 122.1869 | 122.2704 | 122.2208 | 122.3324 | 122.313 | 122.1968 | 0.10285 | 0.19368 | 0.059873 | -0.074319 | 0.02992 | 0.055264 | -0.038067 | 0.01056 | 0.072927 | 0.14091 | 0.029953 | 0.09794
2274.375 | 122.5296 | -122.3145 | 0.12817 | 0.021127 | -0.13668 | -0.039471 | -0.084537 | 0.013375 | -0.001406 | -0.11765 | 0.084537 | 0.16622 | 0.027829 | -0.10179 | 0.01161 | 0.027798 | -0.060955 | -0.012328 | 122.3356 | 122.1778 | 122.275 | 122.2299 | 122.3278 | 122.313 | 122.1968 | 0.10742 | 0.1891 | 0.050717 | -0.078898 | 0.034498 | 0.050686 | -0.038067 | 0.01056 | 0.072927 | 0.14549 | 0.016219 | 0.088784
2276.1406 | 122.6166 | -122.3007 | 0.09613 | 0.01197 | -0.13668 | -0.04405 | -0.089116 | 0.008797 | -0.001406 | -0.11765 | 0.084537 | 0.17079 | 0.032407 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.021484 | 122.3127 | 122.164 | 122.2567 | 122.2116 | 122.3095 | 122.2993 | 122.1831 | 0.10742 | 0.19368 | 0.055295 | -0.083477 | 0.02992 | 0.055264 | -0.042645 | 0.001404 | 0.077505 | 0.15007 | 0.025375 | 0.09794
2277.9062 | 122.493 | -122.3557 | 0.11444 | 0.007391 | -0.13668 | -0.039471 | -0.089116 | 0.027109 | -0.005985 | -0.11765 | 0.084537 | 0.16164 | 0.018672 | -0.10179 | 0.007032 | 0.018642 | -0.060955 | -0.00775 | 122.363 | 122.219 | 122.3162 | 122.2665 | 122.3828 | 122.3497 | 122.238 | 0.10742 | 0.18452 | 0.04156 | -0.078898 | 0.02992 | 0.04153 | -0.038067 | 0.015138 | 0.077505 | 0.14549 | 0.01164 | 0.079627
2279.625 | 122.5021 | -122.3511 | 0.14191 | 0.016548 | -0.14125 | -0.04405 | -0.089116 | 0.013375 | 0.003172 | -0.11765 | 0.089116 | 0.17079 | 0.032407 | -0.1201 | 0.007032 | 0.027798 | -0.060955 | -0.016906 | 122.3676 | 122.2098 | 122.307 | 122.262 | 122.3644 | 122.3542 | 122.2334 | 0.112 | 0.19368 | 0.055295 | -0.097215 | 0.02992 | 0.050686 | -0.038067 | 0.005982 | 0.082084 | 0.15007 | 0.025375 | 0.093362
2281.3906 | 122.5479 | -122.3511 | 0.10529 | 0.01197 | -0.13668 | -0.039471 | -0.089116 | 0.013375 | -0.005985 | -0.11765 | 0.084537 | 0.16164 | 0.027829 | -0.11094 | 0.002454 | 0.027798 | -0.060955 | -0.012328 | 122.363 | 122.2144 | 122.3116 | 122.262 | 122.3644 | 122.3451 | 122.2334 | 0.10742 | 0.18452 | 0.050717 | -0.088056 | 0.025342 | 0.050686 | -0.038067 | 0.01056 | 0.082083 | 0.14549 | 0.025375 | 0.088784
2283.0938 | 122.4747 | -122.3602 | 0.14648 | 0.016548 | -0.1321 | -0.034893 | -0.079959 | 0.017953 | -0.001406 | -0.11308 | 0.084537 | 0.17079 | 0.027829 | -0.10637 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.3768 | 122.2281 | 122.3253 | 122.2803 | 122.3782 | 122.3588 | 122.2472 | 0.10742 | 0.19368 | 0.050717 | -0.083477 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.077505 | 0.14549 | 0.020797 | 0.088784
2284.8594 | 122.644 | -122.3236 | 0.07782 | 0.021127 | -0.13668 | -0.039471 | -0.098273 | 0.017953 | 0.003172 | -0.10392 | 0.084537 | 0.16622 | 0.02325 | -0.10637 | 0.002454 | 0.027798 | -0.060955 | -0.016906 | 122.3447 | 122.1869 | 122.2841 | 122.2253 | 122.3416 | 122.3268 | 122.2197 | 0.10742 | 0.1891 | 0.046138 | -0.083477 | 0.025342 | 0.050686 | -0.038067 | 0.005982 | 0.082083 | 0.14549 | 0.020796 | 0.084205
2286.5625 | 122.6624 | -122.3373 | 0.09613 | 0.01197 | -0.13668 | -0.034893 | -0.093694 | 0.022531 | -0.001406 | -0.11308 | 0.093694 | 0.16622 | 0.027829 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 122.3493 | 122.2007 | 122.3024 | 122.2436 | 122.3599 | 122.3359 | 122.2243 | 0.11658 | 0.1891 | 0.050717 | -0.083477 | 0.034498 | 0.059842 | -0.042645 | 0.01056 | 0.082084 | 0.15923 | 0.016219 | 0.093362
2288.2656 | 122.6486 | -122.3465 | 0.10986 | 0.016548 | -0.13668 | -0.04405 | -0.079959 | 0.013375 | -0.001406 | -0.1085 | 0.07538 | 0.16622 | 0.032407 | -0.10637 | 0.01161 | 0.032376 | -0.060955 | -0.012328 | 122.363 | 122.2098 | 122.3024 | 122.2665 | 122.3599 | 122.3451 | 122.238 | 0.098268 | 0.1891 | 0.055295 | -0.083477 | 0.034498 | 0.055264 | -0.038067 | 0.01056 | 0.06377 | 0.13634 | 0.020797 | 0.093362
2290.0312 | 122.6349 | -122.3602 | 0.086975 | 0.01197 | -0.12752 | -0.039471 | -0.089116 | 0.017953 | -0.001406 | -0.11765 | 0.079959 | 0.17079 | 0.02325 | -0.078891 | 0.007032 | 0.027798 | -0.060955 | -0.016906 | 122.3722 | 122.2327 | 122.3208 | 122.2711 | 122.3782 | 122.3588 | 122.2426 | 0.10285 | 0.19368 | 0.046138 | -0.056003 | 0.02992 | 0.050686 | -0.038067 | 0.005982 | 0.072927 | 0.14091 | 0.016218 | 0.084205
2291.7969 | 122.6578 | -122.3282 | 0.10529 | 0.021127 | -0.12752 | -0.034893 | -0.089116 | 0.022531 | -0.001406 | -0.11308 | 0.089116 | 0.17079 | 0.02325 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 122.3493 | 122.2007 | 122.2933 | 122.2391 | 122.3507 | 122.3268 | 122.2151 | 0.112 | 0.19368 | 0.046138 | -0.083477 | 0.02992 | 0.055264 | -0.042645 | 0.005982 | 0.082084 | 0.15465 | 0.016218 | 0.088783
2293.5469 | 122.5433 | -122.3877 | 0.13275 | 0.021127 | -0.1321 | -0.039471 | -0.084537 | 0.017953 | -0.001406 | -0.11308 | 0.079959 | 0.17537 | 0.027829 | -0.097207 | 0.01161 | 0.02322 | -0.060955 | -0.016906 | 122.4088 | 122.2556 | 122.3482 | 122.3032 | 122.4056 | 122.3863 | 122.2746 | 0.10285 | 0.19826 | 0.050717 | -0.074319 | 0.034498 | 0.046108 | -0.038067 | 0.005982 | 0.068349 | 0.14091 | 0.016219 | 0.088784
2295.25 | 122.6349 | -122.3648 | 0.10071 | 0.016548 | -0.13668 | -0.04405 | -0.084537 | 0.022531 | -0.005985 | -0.10392 | 0.084537 | 0.16622 | 0.032407 | -0.097207 | 0.016188 | 0.032376 | -0.060955 | -0.012328 | 122.3814 | 122.2281 | 122.3208 | 122.2803 | 122.3873 | 122.3588 | 122.2609 | 0.10742 | 0.1891 | 0.055295 | -0.074319 | 0.039076 | 0.055264 | -0.038067 | 0.01056 | 0.068349 | 0.14549 | 0.016219 | 0.093362
2297.0156 | 122.5525 | -122.3923 | 0.14191 | 0.01197 | -0.13668 | -0.034893 | -0.084537 | 0.017953 | -0.001406 | -0.1085 | 0.07538 | 0.17079 | 0.032407 | -0.10637 | 0.01161 | 0.02322 | -0.060955 | -0.016906 | 122.4042 | 122.2556 | 122.3574 | 122.3077 | 122.4102 | 122.3909 | 122.2838 | 0.098268 | 0.19368 | 0.055295 | -0.083477 | 0.034498 | 0.046108 | -0.038067 | 0.005982 | 0.06377 | 0.13634 | 0.020797 | 0.093362
2298.7188 | 122.5616 | -122.3923 | 0.13733 | 0.007391 | -0.12752 | -0.04405 | -0.07538 | 0.017953 | 0.003172 | -0.10392 | 0.07538 | 0.16622 | 0.027829 | -0.11094 | 0.01161 | 0.036954 | -0.060955 | -0.012328 | 122.3997 | 122.2648 | 122.3482 | 122.3169 | 122.4102 | 122.3954 | 122.2884 | 0.098268 | 0.1891 | 0.050717 | -0.088056 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.06377 | 0.13634 | 0.016219 | 0.088784
2300.4844 | 122.5937 | -122.3831 | 0.12817 | 0.016548 | -0.1321 | -0.034893 | -0.079959 | 0.017953 | 0.003172 | -0.1085 | 0.084537 | 0.16622 | 0.027829 | -0.1201 | 0.007032 | 0.02322 | -0.065533 | -0.021484 | 122.3997 | 122.251 | 122.3482 | 122.3032 | 122.4011 | 122.3863 | 122.2746 | 0.10742 | 0.1891 | 0.050717 | -0.097215 | 0.02992 | 0.046108 | -0.042645 | 0.001404 | 0.077505 | 0.15007 | 0.020797 | 0.093362
2302.2031 | 122.6349 | -122.3831 | 0.11902 | 0.021127 | -0.12752 | -0.039471 | -0.084537 | 0.017953 | 0.003172 | -0.1085 | 0.084537 | 0.16622 | 0.02325 | -0.1201 | 0.002454 | 0.032376 | -0.060955 | -0.016906 | 122.4042 | 122.2556 | 122.3436 | 122.2986 | 122.4011 | 122.3863 | 122.2746 | 0.10742 | 0.1891 | 0.046138 | -0.097215 | 0.025342 | 0.055264 | -0.038067 | 0.005982 | 0.082083 | 0.14549 | 0.020796 | 0.084205
2303.9688 | 122.5525 | -122.4243 | 0.11902 | 0.021127 | -0.12294 | -0.034893 | -0.07538 | 0.022531 | 0.00775 | -0.1085 | 0.084537 | 0.16164 | 0.02325 | -0.097207 | 0.01161 | 0.032376 | -0.056376 | -0.021484 | 122.4454 | 122.3014 | 122.3894 | 122.3489 | 122.4468 | 122.4321 | 122.3158 | 0.10742 | 0.18452 | 0.046138 | -0.074319 | 0.034498 | 0.055264 | -0.033488 | 0.001404 | 0.072927 | 0.14091 | 0.01164 | 0.079626
2305.7344 | 122.6028 | -122.4106 | 0.10986 | 0.016548 | -0.11836 | -0.039471 | -0.084537 | 0.027109 | -0.001406 | -0.11308 | 0.079959 | 0.16622 | 0.02325 | -0.11094 | 0.01161 | 0.032376 | -0.070112 | -0.021484 | 122.4271 | 122.2922 | 122.3711 | 122.326 | 122.4377 | 122.4092 | 122.2975 | 0.10285 | 0.1891 | 0.046138 | -0.088056 | 0.034498 | 0.055264 | -0.047224 | 0.001404 | 0.068349 | 0.15007 | 0.01164 | 0.093362
2307.4844 | 122.6624 | -122.4152 | 0.10529 | 0.025705 | -0.12752 | -0.04405 | -0.079959 | 0.013375 | 0.003172 | -0.1085 | 0.089116 | 0.16622 | 0.027829 | -0.10179 | 0.007032 | 0.032376 | -0.056376 | -0.00775 | 122.4409 | 122.2876 | 122.3711 | 122.3352 | 122.4285 | 122.4183 | 122.3067 | 0.112 | 0.1891 | 0.050717 | -0.078898 | 0.02992 | 0.055264 | -0.033488 | 0.015138 | 0.082084 | 0.14549 | 0.020797 | 0.084205
2309.2656 | 122.6395 | -122.3831 | 0.10986 | 0.021127 | -0.11836 | -0.034893 | -0.079959 | 0.022531 | -0.001406 | -0.11308 | 0.084537 | 0.16622 | 0.02325 | -0.088049 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 122.4042 | 122.2648 | 122.3482 | 122.3032 | 122.4056 | 122.3817 | 122.27 | 0.10742 | 0.1891 | 0.046138 | -0.065161 | 0.02992 | 0.059842 | -0.042645 | 0.005982 | 0.077505 | 0.15007 | 0.016218 | 0.088783
2310.9688 | 122.6624 | -122.4014 | 0.10071 | 0.016548 | -0.12294 | -0.034893 | -0.079959 | 0.027109 | 0.003172 | -0.099343 | 0.089116 | 0.17537 | 0.018672 | -0.097207 | 0.01161 | 0.027798 | -0.060955 | -0.012328 | 122.418 | 122.2785 | 122.3665 | 122.3215 | 122.4285 | 122.4046 | 122.3021 | 0.112 | 0.19826 | 0.04156 | -0.074319 | 0.034498 | 0.050686 | -0.038067 | 0.01056 | 0.077506 | 0.15007 | 0.007062 | 0.079627
2312.7344 | 122.6486 | -122.4152 | 0.10986 | 0.025705 | -0.12752 | -0.034893 | -0.079959 | 0.027109 | -0.001406 | -0.10392 | 0.079959 | 0.16622 | 0.027829 | -0.088049 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.4409 | 122.2876 | 122.3803 | 122.3352 | 122.4423 | 122.4138 | 122.3112 | 0.10285 | 0.1891 | 0.050717 | -0.065161 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.072927 | 0.14091 | 0.020797 | 0.088784
2314.4375 | 122.6212 | -122.4197 | 0.10986 | 0.025705 | -0.12294 | -0.034893 | -0.070802 | 0.027109 | 0.00775 | -0.10392 | 0.089116 | 0.17079 | 0.032407 | -0.092628 | 0.016188 | 0.032376 | -0.070112 | -0.021484 | 122.4454 | 122.2968 | 122.3848 | 122.3489 | 122.4468 | 122.4275 | 122.3158 | 0.112 | 0.19368 | 0.055295 | -0.06974 | 0.039076 | 0.055264 | -0.047224 | 0.001404 | 0.072928 | 0.15923 | 0.016219 | 0.10252
2316.2031 | 122.6898 | -122.3877 | 0.073242 | 0.025705 | -0.12294 | -0.034893 | -0.079959 | 0.022531 | 0.00775 | -0.10392 | 0.084537 | 0.16164 | 0.018672 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 122.4134 | 122.2648 | 122.3528 | 122.3077 | 122.4102 | 122.3954 | 122.2838 | 0.10742 | 0.18452 | 0.04156 | -0.083477 | 0.02992 | 0.059842 | -0.042645 | 0.005982 | 0.077505 | 0.15007 | 0.01164 | 0.084205
2317.8906 | 122.7127 | -122.3785 | 0.091553 | 0.016548 | -0.12294 | -0.030314 | -0.070802 | 0.027109 | 0.00775 | -0.1085 | 0.07538 | 0.17079 | 0.027829 | -0.074312 | 0.002454 | 0.036954 | -0.060955 | -0.016906 | 122.3951 | 122.2556 | 122.3482 | 122.3077 | 122.4056 | 122.3863 | 122.27 | 0.098268 | 0.19368 | 0.050717 | -0.051424 | 0.025342 | 0.059842 | -0.038067 | 0.005982 | 0.072926 | 0.13634 | 0.025375 | 0.088784
2319.6406 | 122.7219 | -122.4197 | 0.10529 | 0.021127 | -0.12752 | -0.030314 | -0.079959 | 0.017953 | 0.00775 | -0.1085 | 0.084537 | 0.17079 | 0.027829 | -0.078891 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 122.4409 | 122.2922 | 122.3894 | 122.3398 | 122.4377 | 122.4275 | 122.3112 | 0.10742 | 0.19368 | 0.050717 | -0.056003 | 0.025342 | 0.055264 | -0.042645 | 0.01056 | 0.082083 | 0.15007 | 0.025375 | 0.093362
2321.3906 | 122.7081 | -122.4197 | 0.082397 | 0.030283 | -0.12294 | -0.034893 | -0.070802 | 0.017953 | 0.012329 | -0.099343 | 0.079959 | 0.16622 | 0.027829 | -0.055996 | 0.01161 | 0.036954 | -0.060955 | -0.016906 | 122.45 | 122.2968 | 122.3848 | 122.3489 | 122.4377 | 122.4321 | 122.3204 | 0.10285 | 0.1891 | 0.050717 | -0.033108 | 0.034498 | 0.059842 | -0.038067 | 0.005982 | 0.068349 | 0.14091 | 0.016219 | 0.088784
2323.0938 | 122.6349 | -122.4289 | 0.10529 | 0.021127 | -0.12752 | -0.030314 | -0.070802 | 0.027109 | 0.003172 | -0.099343 | 0.079959 | 0.16622 | 0.02325 | -0.10179 | 0.01161 | 0.027798 | -0.060955 | -0.016906 | 122.45 | 122.3014 | 122.3986 | 122.3581 | 122.456 | 122.4321 | 122.3296 | 0.10285 | 0.1891 | 0.046138 | -0.078898 | 0.034498 | 0.050686 | -0.038067 | 0.005982 | 0.068349 | 0.14091 | 0.01164 | 0.084205
2324.8594 | 122.6807 | -122.4289 | 0.10071 | 0.025705 | -0.12752 | -0.034893 | -0.07538 | 0.022531 | 0.00775 | -0.10392 | 0.07538 | 0.16622 | 0.018672 | -0.10179 | 0.01161 | 0.032376 | -0.065533 | -0.021484 | 122.4546 | 122.3014 | 122.394 | 122.3535 | 122.4514 | 122.4366 | 122.325 | 0.098268 | 0.1891 | 0.04156 | -0.078898 | 0.034498 | 0.055264 | -0.042645 | 0.001404 | 0.06377 | 0.14091 | 0.007062 | 0.084205
2326.625 | 122.7356 | -122.4014 | 0.07782 | 0.021127 | -0.11836 | -0.030314 | -0.079959 | 0.022531 | 0.003172 | -0.1085 | 0.084537 | 0.17079 | 0.027829 | -0.11552 | 0.002454 | 0.027798 | -0.070112 | -0.021484 | 122.4226 | 122.2831 | 122.3711 | 122.3215 | 122.424 | 122.4046 | 122.2929 | 0.10742 | 0.19368 | 0.050717 | -0.092635 | 0.025342 | 0.050686 | -0.047224 | 0.001404 | 0.082083 | 0.15465 | 0.025375 | 0.097941
2328.375 | 122.6669 | -122.4609 | 0.10529 | 0.025705 | -0.12294 | -0.030314 | -0.079959 | 0.027109 | 0.00775 | -0.10392 | 0.084537 | 0.16164 | 0.018672 | -0.097207 | 0.01161 | 0.032376 | -0.056376 | -0.012328 | 122.4866 | 122.338 | 122.4306 | 122.381 | 122.488 | 122.4687 | 122.357 | 0.10742 | 0.18452 | 0.04156 | -0.074319 | 0.034498 | 0.055264 | -0.033488 | 0.01056 | 0.072927 | 0.14091 | 0.007062 | 0.075048
2330.0781 | 122.6303 | -122.4335 | 0.11902 | 0.025705 | -0.12752 | -0.030314 | -0.07538 | 0.027109 | 0.00775 | -0.099343 | 0.07538 | 0.17079 | 0.02325 | -0.10637 | 0.01161 | 0.036954 | -0.060955 | -0.016906 | 122.4592 | 122.306 | 122.4032 | 122.3581 | 122.4606 | 122.4412 | 122.3341 | 0.098268 | 0.19368 | 0.046138 | -0.083477 | 0.034498 | 0.059842 | -0.038067 | 0.005982 | 0.06377 | 0.13634 | 0.01164 | 0.084205
2331.8281 | 122.731 | -122.4197 | 0.11444 | 0.025705 | -0.11836 | -0.030314 | -0.066223 | 0.027109 | 0.00775 | -0.10392 | 0.07538 | 0.16622 | 0.018672 | -0.10637 | 0.01161 | 0.032376 | -0.065533 | -0.012328 | 122.4454 | 122.3014 | 122.3894 | 122.3535 | 122.4468 | 122.4275 | 122.3158 | 0.098268 | 0.1891 | 0.04156 | -0.083477 | 0.034498 | 0.055264 | -0.042645 | 0.01056 | 0.06377 | 0.14091 | 0.007062 | 0.084205
2333.5156 | 122.6349 | -122.4747 | 0.13275 | 0.034862 | -0.11378 | -0.021157 | -0.070802 | 0.031687 | 0.012329 | -0.094765 | 0.084537 | 0.16622 | 0.02325 | -0.10637 | 0.01161 | 0.027798 | -0.060955 | -0.016906 | 122.5095 | 122.3609 | 122.4535 | 122.4039 | 122.5064 | 122.487 | 122.3799 | 0.10742 | 0.1891 | 0.046138 | -0.083477 | 0.034498 | 0.050686 | -0.038067 | 0.005982 | 0.072927 | 0.14549 | 0.01164 | 0.084205
2335.2812 | 122.7356 | -122.438 | 0.10071 | 0.030283 | -0.12294 | -0.021157 | -0.070802 | 0.027109 | 0.003172 | -0.099343 | 0.079959 | 0.16622 | 0.027829 | -0.092628 | 0.016188 | 0.027798 | -0.060955 | -0.012328 | 122.4683 | 122.3151 | 122.4169 | 122.3672 | 122.4652 | 122.4412 | 122.3387 | 0.10285 | 0.1891 | 0.050717 | -0.06974 | 0.039076 | 0.050686 | -0.038067 | 0.01056 | 0.063771 | 0.14091 | 0.011641 | 0.088784
2336.9688 | 122.6028 | -122.4792 | 0.11902 | 0.034862 | -0.11836 | -0.034893 | -0.070802 | 0.027109 | 0.00775 | -0.085608 | 0.07538 | 0.16622 | 0.02325 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 122.5141 | 122.3609 | 122.4444 | 122.4084 | 122.5064 | 122.487 | 122.3936 | 0.098268 | 0.1891 | 0.046138 | -0.083477 | 0.02992 | 0.059842 | -0.042645 | 0.005982 | 0.068348 | 0.14091 | 0.016218 | 0.088783
2338.7188 | 122.6578 | -122.4426 | 0.10986 | 0.044018 | -0.11378 | -0.025735 | -0.070802 | 0.031687 | 0.012329 | -0.10392 | 0.070802 | 0.16622 | 0.032407 | -0.074312 | 0.016188 | 0.032376 | -0.060955 | -0.021484 | 122.4866 | 122.3288 | 122.4169 | 122.3718 | 122.4743 | 122.455 | 122.3387 | 0.09369 | 0.1891 | 0.055295 | -0.051424 | 0.039076 | 0.055264 | -0.038067 | 0.001404 | 0.054614 | 0.13176 | 0.016219 | 0.093362
2340.4844 | 122.6486 | -122.438 | 0.10529 | 0.030283 | -0.11836 | -0.021157 | -0.07538 | 0.031687 | 0.012329 | -0.099343 | 0.084537 | 0.16164 | 0.032407 | -0.11094 | 0.007032 | 0.02322 | -0.056376 | -0.016906 | 122.4683 | 122.3197 | 122.4169 | 122.3627 | 122.4697 | 122.4504 | 122.3387 | 0.10742 | 0.18452 | 0.055295 | -0.088056 | 0.02992 | 0.046108 | -0.033488 | 0.005982 | 0.077505 | 0.14091 | 0.025375 | 0.088783
2342.25 | 122.699 | -122.4472 | 0.10071 | 0.025705 | -0.11378 | -0.030314 | -0.070802 | 0.017953 | 0.012329 | -0.094765 | 0.07538 | 0.16622 | 0.02325 | -0.11094 | 0.01161 | 0.027798 | -0.056376 | -0.021484 | 122.4729 | 122.3334 | 122.4169 | 122.3764 | 122.4652 | 122.4595 | 122.3524 | 0.098268 | 0.1891 | 0.046138 | -0.088056 | 0.034498 | 0.050686 | -0.033488 | 0.001404 | 0.06377 | 0.13176 | 0.01164 | 0.079626
2343.9375 | 122.7081 | -122.4655 | 0.082397 | 0.030283 | -0.11836 | -0.034893 | -0.066223 | 0.031687 | 0.003172 | -0.10392 | 0.084537 | 0.16164 | 0.02325 | -0.10637 | 0.01161 | 0.027798 | -0.056376 | -0.012328 | 122.4958 | 122.3472 | 122.4306 | 122.3993 | 122.4972 | 122.4687 | 122.3616 | 0.10742 | 0.18452 | 0.046138 | -0.083477 | 0.034498 | 0.050686 | -0.033488 | 0.01056 | 0.072927 | 0.14091 | 0.01164 | 0.079626
2345.7031 | 122.6028 | -122.4747 | 0.14648 | 0.030283 | -0.12294 | -0.021157 | -0.066223 | 0.027109 | 0.012329 | -0.094765 | 0.084537 | 0.16622 | 0.02325 | -0.069733 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 122.505 | 122.3517 | 122.4535 | 122.4084 | 122.5018 | 122.487 | 122.3799 | 0.10742 | 0.1891 | 0.046138 | -0.046845 | 0.025342 | 0.055264 | -0.042645 | 0.005982 | 0.082083 | 0.15007 | 0.020796 | 0.088783
2347.3906 | 122.6578 | -122.4609 | 0.14191 | 0.034862 | -0.1092 | -0.021157 | -0.070802 | 0.022531 | 0.012329 | -0.094765 | 0.084537 | 0.17079 | 0.027829 | -0.097207 | 0.016188 | 0.032376 | -0.060955 | -0.016906 | 122.4958 | 122.3517 | 122.4398 | 122.3901 | 122.4835 | 122.4733 | 122.3662 | 0.10742 | 0.19368 | 0.050717 | -0.074319 | 0.039076 | 0.055264 | -0.038067 | 0.005982 | 0.068349 | 0.14549 | 0.011641 | 0.088784
2349.0938 | 122.7356 | -122.4152 | 0.09613 | 0.030283 | -0.12294 | -0.021157 | -0.070802 | 0.031687 | 0.012329 | -0.10392 | 0.079959 | 0.16622 | 0.027829 | -0.11552 | 0.016188 | 0.027798 | -0.060955 | -0.012328 | 122.4454 | 122.2922 | 122.394 | 122.3444 | 122.4468 | 122.4275 | 122.3112 | 0.10285 | 0.1891 | 0.050717 | -0.092635 | 0.039076 | 0.050686 | -0.038067 | 0.01056 | 0.063771 | 0.14091 | 0.011641 | 0.088784
2350.8594 | 122.6349 | -122.4564 | 0.14648 | 0.034862 | -0.12294 | -0.021157 | -0.066223 | 0.036265 | 0.012329 | -0.099343 | 0.07538 | 0.16164 | 0.027829 | -0.10179 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.4912 | 122.3334 | 122.4352 | 122.3901 | 122.4926 | 122.4687 | 122.357 | 0.098268 | 0.18452 | 0.050717 | -0.078898 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.068348 | 0.13634 | 0.020797 | 0.088784
2352.625 | 122.7356 | -122.4701 | 0.10529 | 0.034862 | -0.12294 | -0.025735 | -0.066223 | 0.036265 | 0.00775 | -0.094765 | 0.084537 | 0.16164 | 0.018672 | -0.08347 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 122.505 | 122.3472 | 122.4444 | 122.4039 | 122.5064 | 122.4778 | 122.3753 | 0.10742 | 0.18452 | 0.04156 | -0.060582 | 0.025342 | 0.055264 | -0.042645 | 0.005982 | 0.082083 | 0.15007 | 0.016218 | 0.084205
2354.3281 | 122.6395 | -122.4701 | 0.10529 | 0.025705 | -0.1092 | -0.025735 | -0.066223 | 0.036265 | 0.021485 | -0.094765 | 0.07538 | 0.17079 | 0.02325 | -0.088049 | 0.01161 | 0.02322 | -0.056376 | -0.016906 | 122.4958 | 122.3609 | 122.4444 | 122.4039 | 122.5064 | 122.4916 | 122.3753 | 0.098268 | 0.19368 | 0.046138 | -0.065161 | 0.034498 | 0.046108 | -0.033488 | 0.005982 | 0.06377 | 0.13176 | 0.01164 | 0.079626
2356.0938 | 122.7219 | -122.4792 | 0.091553 | 0.034862 | -0.11836 | -0.021157 | -0.066223 | 0.036265 | 0.012329 | -0.099343 | 0.079959 | 0.17079 | 0.027829 | -0.078891 | 0.01161 | 0.032376 | -0.065533 | -0.016906 | 122.5141 | 122.3609 | 122.4581 | 122.413 | 122.5155 | 122.4916 | 122.3799 | 0.10285 | 0.19368 | 0.050717 | -0.056003 | 0.034498 | 0.055264 | -0.042645 | 0.005982 | 0.068349 | 0.14549 | 0.016219 | 0.093362
2357.8438 | 122.7402 | -122.4655 | 0.10071 | 0.034862 | -0.12294 | -0.025735 | -0.061645 | 0.036265 | 0.012329 | -0.094765 | 0.079959 | 0.16622 | 0.02325 | -0.097207 | 0.007032 | 0.027798 | -0.060955 | -0.016906 | 122.5004 | 122.3426 | 122.4398 | 122.4039 | 122.5018 | 122.4778 | 122.3708 | 0.10285 | 0.1891 | 0.046138 | -0.074319 | 0.02992 | 0.050686 | -0.038067 | 0.005982 | 0.072927 | 0.14091 | 0.016218 | 0.084205
2359.5469 | 122.6532 | -122.4976 | 0.11902 | 0.034862 | -0.11378 | -0.025735 | -0.061645 | 0.036265 | 0.016907 | -0.090186 | 0.079959 | 0.16622 | 0.027829 | -0.10637 | 0.007032 | 0.027798 | -0.060955 | -0.012328 | 122.5324 | 122.3838 | 122.4718 | 122.4359 | 122.5338 | 122.5145 | 122.4074 | 0.10285 | 0.1891 | 0.050717 | -0.083477 | 0.02992 | 0.050686 | -0.038067 | 0.01056 | 0.072927 | 0.14091 | 0.020797 | 0.088784
2361.3125 | 122.7676 | -122.4609 | 0.073242 | 0.03944 | -0.11378 | -0.025735 | -0.061645 | 0.036265 | 0.016907 | -0.085608 | 0.079959 | 0.17079 | 0.02325 | -0.078891 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 122.5004 | 122.3472 | 122.4352 | 122.3993 | 122.4972 | 122.4778 | 122.3753 | 0.10285 | 0.19368 | 0.046138 | -0.056003 | 0.02992 | 0.055264 | -0.047224 | 0.005982 | 0.072927 | 0.15007 | 0.016218 | 0.093362
2363.0625 | 122.7676 | -122.4792 | 0.091553 | 0.034862 | -0.11378 | -0.021157 | -0.070802 | 0.036265 | 0.016907 | -0.094765 | 0.084537 | 0.16622 | 0.027829 | -0.023943 | 0.016188 | 0.036954 | -0.065533 | -0.012328 | 122.5141 | 122.3655 | 122.4581 | 122.4084 | 122.5155 | 122.4962 | 122.3845 | 0.10742 | 0.1891 | 0.050717 | -0.001055 | 0.039076 | 0.059842 | -0.042645 | 0.01056 | 0.068349 | 0.15007 | 0.011641 | 0.093362
2364.8281 | 122.6532 | -122.5067 | 0.12817 | 0.034862 | -0.11378 | -0.016578 | -0.066223 | 0.040843 | 0.012329 | -0.094765 | 0.07538 | 0.16622 | 0.018672 | -0.10637 | 0.01161 | 0.041532 | -0.060955 | -0.016906 | 122.5416 | 122.3929 | 122.4901 | 122.4405 | 122.5476 | 122.519 | 122.4119 | 0.098268 | 0.1891 | 0.04156 | -0.083477 | 0.034498 | 0.06442 | -0.038067 | 0.005982 | 0.06377 | 0.13634 | 0.007062 | 0.079627
2366.5312 | 122.644 | -122.5204 | 0.13275 | 0.034862 | -0.11378 | -0.016578 | -0.057066 | 0.040843 | 0.016907 | -0.099343 | 0.07538 | 0.16164 | 0.018672 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.016906 | 122.5553 | 122.4067 | 122.5039 | 122.4634 | 122.5613 | 122.5374 | 122.4211 | 0.098268 | 0.18452 | 0.04156 | -0.078898 | 0.034498 | 0.059842 | -0.047224 | 0.005982 | 0.06377 | 0.14549 | 0.007062 | 0.088784
2368.3125 | 122.644 | -122.5296 | 0.13733 | 0.034862 | -0.1092 | -0.025735 | -0.061645 | 0.040843 | 0.021485 | -0.090186 | 0.07538 | 0.16164 | 0.02325 | -0.11094 | 0.007032 | 0.02322 | -0.065533 | -0.016906 | 122.5645 | 122.4204 | 122.5039 | 122.468 | 122.5704 | 122.5511 | 122.4394 | 0.098268 | 0.18452 | 0.046138 | -0.088056 | 0.02992 | 0.046108 | -0.042645 | 0.005982 | 0.068348 | 0.14091 | 0.016218 | 0.088783
2370.0156 | 122.7768 | -122.5113 | 0.09613 | 0.034862 | -0.1092 | -0.025735 | -0.070802 | 0.040843 | 0.00775 | -0.094765 | 0.079959 | 0.17079 | 0.027829 | -0.10637 | 0.01161 | 0.027798 | -0.060955 | -0.016906 | 122.5462 | 122.4021 | 122.4856 | 122.4405 | 122.5521 | 122.519 | 122.4165 | 0.10285 | 0.19368 | 0.050717 | -0.083477 | 0.034498 | 0.050686 | -0.038067 | 0.005982 | 0.068349 | 0.14091 | 0.016219 | 0.088784
2371.7656 | 122.6624 | -122.5067 | 0.13275 | 0.044018 | -0.11836 | -0.021157 | -0.061645 | 0.031687 | 0.00775 | -0.094765 | 0.084537 | 0.16622 | 0.018672 | -0.097207 | 0.007032 | 0.027798 | -0.060955 | -0.016906 | 122.5507 | 122.3884 | 122.4856 | 122.4451 | 122.5384 | 122.5145 | 122.4119 | 0.10742 | 0.1891 | 0.04156 | -0.074319 | 0.02992 | 0.050686 | -0.038067 | 0.005982 | 0.077505 | 0.14549 | 0.01164 | 0.079627
2373.5156 | 122.6532 | -122.5067 | 0.12817 | 0.034862 | -0.1092 | -0.012 | -0.066223 | 0.045421 | 0.016907 | -0.090186 | 0.084537 | 0.16164 | 0.02325 | -0.10637 | 0.007032 | 0.027798 | -0.060955 | -0.012328 | 122.5416 | 122.3975 | 122.4947 | 122.4405 | 122.5521 | 122.5236 | 122.4165 | 0.10742 | 0.18452 | 0.046138 | -0.083477 | 0.02992 | 0.050686 | -0.038067 | 0.01056 | 0.077505 | 0.14549 | 0.016218 | 0.084205
2375.2188 | 122.7539 | -122.5021 | 0.11444 | 0.034862 | -0.1092 | -0.016578 | -0.057066 | 0.045421 | 0.021485 | -0.090186 | 0.089116 | 0.17537 | 0.02325 | -0.097207 | 0.01161 | 0.032376 | -0.065533 | -0.021484 | 122.537 | 122.3929 | 122.4856 | 122.4451 | 122.5476 | 122.5236 | 122.4119 | 0.112 | 0.19826 | 0.046138 | -0.074319 | 0.034498 | 0.055264 | -0.042645 | 0.001404 | 0.077506 | 0.15465 | 0.01164 | 0.088783
2376.9688 | 122.7859 | -122.4747 | 0.09613 | 0.03944 | -0.1092 | -0.016578 | -0.07538 | 0.036265 | 0.016907 | -0.085608 | 0.07538 | 0.16622 | 0.02325 | -0.097207 | 0.01161 | 0.036954 | -0.060955 | -0.021484 | 122.5141 | 122.3655 | 122.4581 | 122.3993 | 122.5109 | 122.4916 | 122.3891 | 0.098268 | 0.1891 | 0.046138 | -0.074319 | 0.034498 | 0.059842 | -0.038067 | 0.001404 | 0.06377 | 0.13634 | 0.01164 | 0.084205
2378.6562 | 122.6669 | -122.5525 | 0.12817 | 0.03944 | -0.1092 | -0.025735 | -0.061645 | 0.031687 | 0.026064 | -0.090186 | 0.079959 | 0.17079 | 0.027829 | -0.11552 | 0.01161 | 0.032376 | -0.070112 | -0.012328 | 122.5919 | 122.4433 | 122.5268 | 122.4908 | 122.5842 | 122.5786 | 122.4623 | 0.10285 | 0.19368 | 0.050717 | -0.092635 | 0.034498 | 0.055264 | -0.047224 | 0.01056 | 0.068349 | 0.15007 | 0.016219 | 0.097941
2380.4062 | 122.731 | -122.5159 | 0.10071 | 0.044018 | -0.1092 | -0.016578 | -0.066223 | 0.040843 | 0.016907 | -0.094765 | 0.079959 | 0.16164 | 0.018672 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 122.5599 | 122.4067 | 122.4993 | 122.4496 | 122.5567 | 122.5328 | 122.4211 | 0.10285 | 0.18452 | 0.04156 | -0.088056 | 0.02992 | 0.055264 | -0.042645 | 0.01056 | 0.072927 | 0.14549 | 0.01164 | 0.084205
2382.1562 | 122.6852 | -122.5067 | 0.13733 | 0.03944 | -0.11378 | -0.016578 | -0.066223 | 0.036265 | 0.021485 | -0.090186 | 0.079959 | 0.17079 | 0.027829 | -0.10179 | 0.007032 | 0.036954 | -0.060955 | -0.016906 | 122.5462 | 122.3929 | 122.4901 | 122.4405 | 122.543 | 122.5282 | 122.4165 | 0.10285 | 0.19368 | 0.050717 | -0.078898 | 0.02992 | 0.059842 | -0.038067 | 0.005982 | 0.072927 | 0.14091 | 0.020797 | 0.088784
2383.9219 | 122.7768 | -122.5113 | 0.10071 | 0.03944 | -0.10462 | -0.016578 | -0.066223 | 0.036265 | 0.016907 | -0.090186 | 0.079959 | 0.16622 | 0.02325 | -0.10179 | 0.01161 | 0.032376 | -0.065533 | -0.021484 | 122.5507 | 122.4067 | 122.4947 | 122.4451 | 122.5476 | 122.5282 | 122.4211 | 0.10285 | 0.1891 | 0.046138 | -0.078898 | 0.034498 | 0.055264 | -0.042645 | 0.001404 | 0.068349 | 0.14549 | 0.01164 | 0.088783
2385.6094 | 122.7036 | -122.5479 | 0.13275 | 0.03944 | -0.11378 | -0.025735 | -0.057066 | 0.036265 | 0.021485 | -0.094765 | 0.07538 | 0.16164 | 0.02325 | -0.10637 | 0.007032 | 0.027798 | -0.060955 | -0.021484 | 122.5874 | 122.4341 | 122.5222 | 122.4908 | 122.5842 | 122.5694 | 122.4531 | 0.098268 | 0.18452 | 0.046138 | -0.083477 | 0.02992 | 0.050686 | -0.038067 | 0.001404 | 0.068348 | 0.13634 | 0.016218 | 0.084205
2387.4062 | 122.7722 | -122.5067 | 0.10529 | 0.044018 | -0.11378 | -0.021157 | -0.061645 | 0.040843 | 0.016907 | -0.085608 | 0.07538 | 0.16164 | 0.02325 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 122.5507 | 122.3929 | 122.4856 | 122.4451 | 122.5476 | 122.5236 | 122.4211 | 0.098268 | 0.18452 | 0.046138 | -0.083477 | 0.025342 | 0.055264 | -0.042645 | 0.01056 | 0.072926 | 0.14091 | 0.020796 | 0.088783
2389.1094 | 122.7814 | -122.5113 | 0.10071 | 0.034862 | -0.11378 | -0.021157 | -0.066223 | 0.036265 | 0.016907 | -0.090186 | 0.07538 | 0.16164 | 0.02325 | -0.11094 | 0.01161 | 0.032376 | -0.065533 | -0.021484 | 122.5462 | 122.3975 | 122.4901 | 122.4451 | 122.5476 | 122.5282 | 122.4211 | 0.098268 | 0.18452 | 0.046138 | -0.088056 | 0.034498 | 0.055264 | -0.042645 | 0.001404 | 0.06377 | 0.14091 | 0.01164 | 0.088783
2390.875 | 122.7676 | -122.5296 | 0.09613 | 0.034862 | -0.1092 | -0.021157 | -0.070802 | 0.040843 | 0.012329 | -0.085608 | 0.079959 | 0.16164 | 0.02325 | -0.10179 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.5645 | 122.4204 | 122.5084 | 122.4588 | 122.5704 | 122.5419 | 122.444 | 0.10285 | 0.18452 | 0.046138 | -0.078898 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.072927 | 0.14091 | 0.016218 | 0.084205
2392.6406 | 122.8134 | -122.5204 | 0.10071 | 0.044018 | -0.11378 | -0.016578 | -0.057066 | 0.040843 | 0.021485 | -0.090186 | 0.079959 | 0.17079 | 0.02325 | -0.092628 | 0.01161 | 0.041532 | -0.070112 | -0.021484 | 122.5645 | 122.4067 | 122.5039 | 122.4634 | 122.5613 | 122.5419 | 122.4303 | 0.10285 | 0.19368 | 0.046138 | -0.06974 | 0.034498 | 0.06442 | -0.047224 | 0.001404 | 0.068349 | 0.15007 | 0.01164 | 0.093362
2394.4062 | 122.6578 | -122.5296 | 0.11444 | 0.044018 | -0.11378 | -0.021157 | -0.061645 | 0.040843 | 0.026064 | -0.090186 | 0.07538 | 0.16164 | 0.02325 | -0.11094 | 0.020767 | 0.032376 | -0.060955 | -0.012328 | 122.5736 | 122.4158 | 122.5084 | 122.468 | 122.5704 | 122.5557 | 122.4394 | 0.098268 | 0.18452 | 0.046138 | -0.088056 | 0.043655 | 0.055264 | -0.038067 | 0.01056 | 0.054613 | 0.13634 | 0.002483 | 0.084205
2396.1094 | 122.6898 | -122.5616 | 0.11902 | 0.044018 | -0.1092 | -0.016578 | -0.057066 | 0.040843 | 0.012329 | -0.085608 | 0.07538 | 0.15706 | 0.02325 | -0.092628 | 0.007032 | 0.02322 | -0.065533 | -0.016906 | 122.6057 | 122.4524 | 122.5451 | 122.5046 | 122.6025 | 122.574 | 122.476 | 0.098268 | 0.17994 | 0.046138 | -0.06974 | 0.02992 | 0.046108 | -0.042645 | 0.005982 | 0.068348 | 0.14091 | 0.016218 | 0.088783
2397.875 | 122.7859 | -122.5159 | 0.10529 | 0.044018 | -0.10004 | -0.012 | -0.066223 | 0.049999 | 0.026064 | -0.094765 | 0.07538 | 0.16622 | 0.014094 | -0.11094 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.5599 | 122.4158 | 122.5039 | 122.4496 | 122.5659 | 122.5419 | 122.4211 | 0.098268 | 0.1891 | 0.036982 | -0.088056 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.068348 | 0.13634 | 0.007062 | 0.075049
2399.5781 | 122.7356 | -122.5388 | 0.11444 | 0.044018 | -0.1092 | -0.016578 | -0.066223 | 0.049999 | 0.012329 | -0.085608 | 0.084537 | 0.16164 | 0.032407 | -0.092628 | 0.007032 | 0.027798 | -0.070112 | -0.016906 | 122.5828 | 122.4296 | 122.5222 | 122.4725 | 122.5888 | 122.5511 | 122.4531 | 0.10742 | 0.18452 | 0.055295 | -0.06974 | 0.02992 | 0.050686 | -0.047224 | 0.005982 | 0.077505 | 0.15465 | 0.025375 | 0.10252
2401.3438 | 122.8226 | -122.5067 | 0.091553 | 0.044018 | -0.1092 | -0.021157 | -0.047909 | 0.045421 | 0.016907 | -0.085608 | 0.079959 | 0.15706 | 0.027829 | -0.10637 | 0.002454 | 0.036954 | -0.060955 | -0.021484 | 122.5507 | 122.3975 | 122.4856 | 122.4588 | 122.5521 | 122.5236 | 122.4211 | 0.10285 | 0.17994 | 0.050717 | -0.083477 | 0.025342 | 0.059842 | -0.038067 | 0.001404 | 0.077505 | 0.14091 | 0.025375 | 0.088784
2403.0938 | 122.7997 | -122.5296 | 0.10071 | 0.044018 | -0.1092 | -0.012 | -0.061645 | 0.040843 | 0.021485 | -0.08103 | 0.07538 | 0.17079 | 0.018672 | -0.092628 | 0.007032 | 0.02322 | -0.070112 | -0.016906 | 122.5736 | 122.4204 | 122.5176 | 122.468 | 122.5704 | 122.5511 | 122.4486 | 0.098268 | 0.19368 | 0.04156 | -0.06974 | 0.02992 | 0.046108 | -0.047224 | 0.005982 | 0.068348 | 0.14549 | 0.01164 | 0.088784
2404.9531 | 122.7539 | -122.5616 | 0.11902 | 0.034862 | -0.1092 | -0.012 | -0.061645 | 0.045421 | 0.021485 | -0.085608 | 0.07538 | 0.17079 | 0.02325 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.026063 | 122.5965 | 122.4524 | 122.5496 | 122.5 | 122.6071 | 122.5831 | 122.476 | 0.098268 | 0.19368 | 0.046138 | -0.088056 | 0.02992 | 0.055264 | -0.047224 | -0.003175 | 0.068348 | 0.14549 | 0.016218 | 0.093362
2407.1719 | 122.8134 | -122.525 | 0.091553 | 0.044018 | -0.10462 | -0.016578 | -0.061645 | 0.045421 | 0.021485 | -0.085608 | 0.07538 | 0.16164 | 0.027829 | -0.092628 | -0.002124 | 0.032376 | -0.060955 | -0.026063 | 122.569 | 122.4204 | 122.5084 | 122.4634 | 122.5704 | 122.5465 | 122.4394 | 0.098268 | 0.18452 | 0.050717 | -0.06974 | 0.020764 | 0.055264 | -0.038067 | -0.003175 | 0.077504 | 0.13634 | 0.029953 | 0.088784
2409.8125 | 122.8592 | -122.5067 | 0.11444 | 0.03944 | -0.1092 | -0.012 | -0.061645 | 0.045421 | 0.021485 | -0.085608 | 0.070802 | 0.16622 | 0.014094 | -0.097207 | 0.01161 | 0.032376 | -0.060955 | -0.016906 | 122.5462 | 122.3975 | 122.4947 | 122.4451 | 122.5521 | 122.5282 | 122.4211 | 0.09369 | 0.1891 | 0.036982 | -0.074319 | 0.034498 | 0.055264 | -0.038067 | 0.005982 | 0.059192 | 0.13176 | 0.002484 | 0.075049
2412.8906 | 122.7585 | -122.5662 | 0.11444 | 0.048597 | -0.10462 | -0.012 | -0.057066 | 0.049999 | 0.026064 | -0.08103 | 0.084537 | 0.15706 | 0.027829 | -0.08347 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 122.6148 | 122.4616 | 122.5542 | 122.5092 | 122.6162 | 122.5923 | 122.4852 | 0.10742 | 0.17994 | 0.050717 | -0.060582 | 0.02992 | 0.055264 | -0.047224 | 0.005982 | 0.077505 | 0.15465 | 0.020797 | 0.097941
2414.6875 | 122.7173 | -122.5708 | 0.13275 | 0.048597 | -0.10004 | -0.016578 | -0.061645 | 0.040843 | 0.021485 | -0.085608 | 0.079959 | 0.15706 | 0.014094 | -0.11094 | 0.007032 | 0.027798 | -0.060955 | -0.021484 | 122.6194 | 122.4708 | 122.5542 | 122.5092 | 122.6116 | 122.5923 | 122.4852 | 0.10285 | 0.17994 | 0.036982 | -0.088056 | 0.02992 | 0.050686 | -0.038067 | 0.001404 | 0.072927 | 0.14091 | 0.007062 | 0.075049
2416.4844 | 122.731 | -122.5708 | 0.11902 | 0.048597 | -0.090888 | -0.012 | -0.061645 | 0.049999 | 0.030642 | -0.085608 | 0.07538 | 0.16622 | 0.02325 | -0.10637 | 0.01161 | 0.027798 | -0.060955 | -0.012328 | 122.6194 | 122.4799 | 122.5588 | 122.5092 | 122.6208 | 122.6014 | 122.4852 | 0.098268 | 0.1891 | 0.046138 | -0.083477 | 0.034498 | 0.050686 | -0.038067 | 0.01056 | 0.06377 | 0.13634 | 0.01164 | 0.084205
2418.25 | 122.7676 | -122.5571 | 0.11902 | 0.053175 | -0.1092 | -0.007421 | -0.061645 | 0.040843 | 0.021485 | -0.085608 | 0.07538 | 0.16622 | 0.02325 | -0.11094 | 0.01161 | 0.032376 | -0.065533 | -0.016906 | 122.6102 | 122.4479 | 122.5496 | 122.4954 | 122.5979 | 122.5786 | 122.4715 | 0.098268 | 0.1891 | 0.046138 | -0.088056 | 0.034498 | 0.055264 | -0.042645 | 0.005982 | 0.06377 | 0.14091 | 0.01164 | 0.088783
2420.0312 | 122.7036 | -122.5708 | 0.13275 | 0.03944 | -0.1092 | -0.016578 | -0.052488 | 0.040843 | 0.021485 | -0.085608 | 0.079959 | 0.16622 | 0.018672 | -0.10179 | 0.016188 | 0.027798 | -0.070112 | -0.012328 | 122.6102 | 122.4616 | 122.5542 | 122.5183 | 122.6116 | 122.5923 | 122.4852 | 0.10285 | 0.1891 | 0.04156 | -0.078898 | 0.039076 | 0.050686 | -0.047224 | 0.01056 | 0.063771 | 0.15007 | 0.002484 | 0.088784
2421.7188 | 122.699 | -122.5845 | 0.12817 | 0.048597 | -0.10462 | -0.016578 | -0.061645 | 0.045421 | 0.026064 | -0.085608 | 0.079959 | 0.16622 | 0.02325 | -0.10637 | 0.007032 | 0.027798 | -0.056376 | -0.016906 | 122.6331 | 122.4799 | 122.568 | 122.5229 | 122.63 | 122.6106 | 122.4989 | 0.10285 | 0.1891 | 0.046138 | -0.083477 | 0.02992 | 0.050686 | -0.033488 | 0.005982 | 0.072927 | 0.13634 | 0.016218 | 0.079626
2423.4688 | 122.731 | -122.5845 | 0.12817 | 0.048597 | -0.1092 | -0.007421 | -0.052488 | 0.045421 | 0.016907 | -0.08103 | 0.079959 | 0.16164 | 0.027829 | -0.097207 | 0.01161 | 0.032376 | -0.060955 | -0.012328 | 122.6331 | 122.4753 | 122.5771 | 122.532 | 122.63 | 122.6014 | 122.5035 | 0.10285 | 0.18452 | 0.050717 | -0.074319 | 0.034498 | 0.055264 | -0.038067 | 0.01056 | 0.068349 | 0.14091 | 0.016219 | 0.088784
2425.25 | 122.8592 | -122.5433 | 0.086975 | 0.044018 | -0.10004 | -0.012 | -0.061645 | 0.045421 | 0.035221 | -0.085608 | 0.07538 | 0.16164 | 0.02325 | -0.097207 | 0.01161 | 0.027798 | -0.065533 | -0.016906 | 122.5874 | 122.4433 | 122.5313 | 122.4817 | 122.5888 | 122.5786 | 122.4577 | 0.098268 | 0.18452 | 0.046138 | -0.074319 | 0.034498 | 0.050686 | -0.042645 | 0.005982 | 0.06377 | 0.14091 | 0.01164 | 0.088783
2427.0156 | 122.7951 | -122.5708 | 0.10986 | 0.053175 | -0.10462 | -0.016578 | -0.066223 | 0.045421 | 0.021485 | -0.085608 | 0.079959 | 0.16164 | 0.018672 | -0.088049 | 0.007032 | 0.036954 | -0.056376 | -0.016906 | 122.624 | 122.4662 | 122.5542 | 122.5046 | 122.6162 | 122.5923 | 122.4852 | 0.10285 | 0.18452 | 0.04156 | -0.065161 | 0.02992 | 0.059842 | -0.033488 | 0.005982 | 0.072927 | 0.13634 | 0.01164 | 0.075048
2428.7031 | 122.8455 | -122.58 | 0.082397 | 0.053175 | -0.10004 | -0.021157 | -0.061645 | 0.049999 | 0.026064 | -0.085608 | 0.070802 | 0.17079 | 0.027829 | -0.097207 | 0.01161 | 0.027798 | -0.056376 | -0.012328 | 122.6331 | 122.4799 | 122.5588 | 122.5183 | 122.63 | 122.606 | 122.4943 | 0.09369 | 0.19368 | 0.050717 | -0.074319 | 0.034498 | 0.050686 | -0.033488 | 0.01056 | 0.059192 | 0.12718 | 0.016219 | 0.084205
2430.4531 | 122.7081 | -122.5891 | 0.14191 | 0.053175 | -0.10004 | -0.007421 | -0.061645 | 0.049999 | 0.026064 | -0.08103 | 0.079959 | 0.16164 | 0.02325 | -0.078891 | 0.007032 | 0.032376 | -0.070112 | -0.021484 | 122.6423 | 122.4891 | 122.5817 | 122.5275 | 122.6391 | 122.6152 | 122.5081 | 0.10285 | 0.18452 | 0.046138 | -0.056003 | 0.02992 | 0.055264 | -0.047224 | 0.001404 | 0.072927 | 0.15007 | 0.016218 | 0.093362
2432.2344 | 122.6944 | -122.6028 | 0.11444 | 0.048597 | -0.095467 | -0.012 | -0.061645 | 0.049999 | 0.026064 | -0.076452 | 0.070802 | 0.17079 | 0.018672 | -0.11094 | 0.01161 | 0.032376 | -0.051798 | -0.016906 | 122.6514 | 122.5074 | 122.5908 | 122.5412 | 122.6528 | 122.6289 | 122.5264 | 0.09369 | 0.19368 | 0.04156 | -0.088056 | 0.034498 | 0.055264 | -0.02891 | 0.005982 | 0.059192 | 0.1226 | 0.007062 | 0.07047
2434 | 122.7081 | -122.6028 | 0.11902 | 0.057754 | -0.10004 | -0.012 | -0.052488 | 0.054577 | 0.030642 | -0.076452 | 0.079959 | 0.16164 | 0.027829 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.016906 | 122.6606 | 122.5028 | 122.5908 | 122.5504 | 122.6574 | 122.6335 | 122.5264 | 0.10285 | 0.18452 | 0.050717 | -0.083477 | 0.034498 | 0.059842 | -0.042645 | 0.005982 | 0.068349 | 0.14549 | 0.016219 | 0.093362
2435.7031 | 122.7997 | -122.5983 | 0.10071 | 0.057754 | -0.095467 | -0.012 | -0.057066 | 0.049999 | 0.026064 | -0.08103 | 0.084537 | 0.16622 | 0.032407 | -0.10179 | 0.01161 | 0.036954 | -0.060955 | -0.021484 | 122.656 | 122.5028 | 122.5863 | 122.5412 | 122.6483 | 122.6243 | 122.5172 | 0.10742 | 0.1891 | 0.055295 | -0.078898 | 0.034498 | 0.059842 | -0.038067 | 0.001404 | 0.072927 | 0.14549 | 0.020797 | 0.093362
2437.4688 | 122.8271 | -122.5754 | 0.073242 | 0.053175 | -0.10462 | -0.012 | -0.057066 | 0.049999 | 0.026064 | -0.076452 | 0.07538 | 0.17079 | 0.027829 | -0.10179 | 0.01161 | 0.036954 | -0.065533 | -0.021484 | 122.6286 | 122.4708 | 122.5634 | 122.5183 | 122.6254 | 122.6014 | 122.4989 | 0.098268 | 0.19368 | 0.050717 | -0.078898 | 0.034498 | 0.059842 | -0.042645 | 0.001404 | 0.06377 | 0.14091 | 0.016219 | 0.093362
2439.2344 | 122.7585 | -122.6074 | 0.11902 | 0.057754 | -0.095467 | -0.016578 | -0.052488 | 0.049999 | 0.030642 | -0.076452 | 0.084537 | 0.16164 | 0.02325 | -0.10637 | 0.01161 | 0.036954 | -0.060955 | -0.016906 | 122.6652 | 122.512 | 122.5908 | 122.5549 | 122.6574 | 122.6381 | 122.531 | 0.10742 | 0.18452 | 0.046138 | -0.083477 | 0.034498 | 0.059842 | -0.038067 | 0.005982 | 0.072927 | 0.14549 | 0.01164 | 0.084205
2440.9219 | 122.8729 | -122.5708 | 0.091553 | 0.053175 | -0.095467 | -0.002842 | -0.057066 | 0.054577 | 0.030642 | -0.076452 | 0.07538 | 0.16622 | 0.018672 | -0.074312 | 0.01161 | 0.032376 | -0.065533 | -0.030641 | 122.624 | 122.4753 | 122.568 | 122.5137 | 122.6254 | 122.6014 | 122.4943 | 0.098268 | 0.1891 | 0.04156 | -0.051424 | 0.034498 | 0.055264 | -0.042645 | -0.007753 | 0.06377 | 0.14091 | 0.007062 | 0.084205
2442.6719 | 122.7585 | -122.5891 | 0.1236 | 0.053175 | -0.095467 | -0.002842 | -0.047909 | 0.054577 | 0.030642 | -0.08103 | 0.079959 | 0.16622 | 0.02325 | -0.097207 | 0.016188 | 0.027798 | -0.065533 | -0.016906 | 122.6423 | 122.4936 | 122.5863 | 122.5412 | 122.6437 | 122.6198 | 122.5081 | 0.10285 | 0.1891 | 0.046138 | -0.074319 | 0.039076 | 0.050686 | -0.042645 | 0.005982 | 0.063771 | 0.14549 | 0.007062 | 0.088783
2444.4531 | 122.8409 | -122.5845 | 0.10071 | 0.057754 | -0.090888 | -0.007421 | -0.052488 | 0.054577 | 0.030642 | -0.076452 | 0.079959 | 0.17079 | 0.018672 | -0.10637 | 0.007032 | 0.027798 | -0.065533 | -0.016906 | 122.6423 | 122.4936 | 122.5771 | 122.532 | 122.6391 | 122.6152 | 122.5081 | 0.10285 | 0.19368 | 0.04156 | -0.083477 | 0.02992 | 0.050686 | -0.042645 | 0.005982 | 0.072927 | 0.14549 | 0.01164 | 0.084205
2446.2344 | 122.8134 | -122.5937 | 0.091553 | 0.053175 | -0.10004 | -0.016578 | -0.047909 | 0.049999 | 0.030642 | -0.076452 | 0.07538 | 0.16622 | 0.02325 | -0.11094 | 0.01161 | 0.027798 | -0.065533 | -0.016906 | 122.6469 | 122.4936 | 122.5771 | 122.5458 | 122.6437 | 122.6243 | 122.5172 | 0.098268 | 0.1891 | 0.046138 | -0.088056 | 0.034498 | 0.050686 | -0.042645 | 0.005982 | 0.06377 | 0.14091 | 0.01164 | 0.088783
2447.9375 | 122.7997 | -122.5937 | 0.11444 | 0.053175 | -0.090888 | -0.002842 | -0.043331 | 0.054577 | 0.044377 | -0.071874 | 0.079959 | 0.15706 | 0.018672 | -0.10637 | 0.007032 | 0.032376 | -0.060955 | -0.021484 | 122.6469 | 122.5028 | 122.5908 | 122.5504 | 122.6483 | 122.6381 | 122.5218 | 0.10285 | 0.17994 | 0.04156 | -0.083477 | 0.02992 | 0.055264 | -0.038067 | 0.001404 | 0.072927 | 0.14091 | 0.01164 | 0.079627
2449.625 | 122.818 | -122.5754 | 0.10529 | 0.057754 | -0.10004 | -0.002842 | -0.057066 | 0.049999 | 0.035221 | -0.076452 | 0.084537 | 0.16164 | 0.027829 | -0.10637 | 0.016188 | 0.032376 | -0.060955 | -0.021484 | 122.6331 | 122.4753 | 122.5725 | 122.5183 | 122.6254 | 122.6106 | 122.4989 | 0.10742 | 0.18452 | 0.050717 | -0.083477 | 0.039076 | 0.055264 | -0.038067 | 0.001404 | 0.068349 | 0.14549 | 0.011641 | 0.088784
2451.3906 | 122.8592 | -122.5845 | 0.10986 | 0.048597 | -0.095467 | -0.016578 | -0.043331 | 0.059155 | 0.030642 | -0.076452 | 0.07538 | 0.16164 | 0.02325 | -0.08347 | 0.01161 | 0.027798 | -0.051798 | -0.012328 | 122.6331 | 122.4891 | 122.568 | 122.5412 | 122.6437 | 122.6152 | 122.5081 | 0.098268 | 0.18452 | 0.046138 | -0.060582 | 0.034498 | 0.050686 | -0.02891 | 0.01056 | 0.06377 | 0.12718 | 0.01164 | 0.075048
2453.1562 | 122.8363 | -122.6074 | 0.10529 | 0.057754 | -0.10462 | -0.007421 | -0.057066 | 0.059155 | 0.026064 | -0.076452 | 0.070802 | 0.15248 | 0.018672 | -0.10179 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 122.6652 | 122.5028 | 122.6 | 122.5504 | 122.6666 | 122.6335 | 122.531 | 0.09369 | 0.17537 | 0.04156 | -0.078898 | 0.02992 | 0.055264 | -0.042645 | 0.01056 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2454.8438 | 122.8409 | -122.5754 | 0.10071 | 0.048597 | -0.090888 | -0.012 | -0.047909 | 0.063733 | 0.030642 | -0.076452 | 0.079959 | 0.16164 | 0.018672 | -0.10179 | 0.007032 | 0.032376 | -0.060955 | -0.021484 | 122.624 | 122.4845 | 122.5634 | 122.5275 | 122.6391 | 122.606 | 122.4989 | 0.10285 | 0.18452 | 0.04156 | -0.078898 | 0.02992 | 0.055264 | -0.038067 | 0.001404 | 0.072927 | 0.14091 | 0.01164 | 0.079627
2456.5469 | 122.8455 | -122.5845 | 0.10071 | 0.057754 | -0.095467 | -0.002842 | -0.043331 | 0.049999 | 0.030642 | -0.08103 | 0.07538 | 0.17079 | 0.02325 | -0.088049 | 0.016188 | 0.02322 | -0.065533 | -0.012328 | 122.6423 | 122.4891 | 122.5817 | 122.5412 | 122.6345 | 122.6152 | 122.5035 | 0.098268 | 0.19368 | 0.046138 | -0.065161 | 0.039076 | 0.046108 | -0.042645 | 0.01056 | 0.059192 | 0.14091 | 0.007062 | 0.088783
2458.3125 | 122.7676 | -122.6303 | 0.10986 | 0.057754 | -0.095467 | -0.002842 | -0.043331 | 0.054577 | 0.030642 | -0.076452 | 0.07538 | 0.17079 | 0.018672 | -0.10179 | 0.016188 | 0.032376 | -0.065533 | -0.016906 | 122.6881 | 122.5348 | 122.6275 | 122.587 | 122.6849 | 122.661 | 122.5539 | 0.098268 | 0.19368 | 0.04156 | -0.078898 | 0.039076 | 0.055264 | -0.042645 | 0.005982 | 0.059192 | 0.14091 | 0.002484 | 0.084205
2460 | 122.7585 | -122.612 | 0.1236 | 0.053175 | -0.095467 | -0.007421 | -0.043331 | 0.054577 | 0.039799 | -0.071874 | 0.07538 | 0.16622 | 0.02325 | -0.088049 | 0.01161 | 0.027798 | -0.065533 | -0.021484 | 122.6652 | 122.5165 | 122.6046 | 122.5687 | 122.6666 | 122.6518 | 122.5401 | 0.098268 | 0.1891 | 0.046138 | -0.065161 | 0.034498 | 0.050686 | -0.042645 | 0.001404 | 0.06377 | 0.14091 | 0.01164 | 0.088783
2461.6875 | 122.7493 | -122.612 | 0.11444 | 0.062332 | -0.095467 | 0.001736 | -0.047909 | 0.059155 | 0.035221 | -0.076452 | 0.079959 | 0.16164 | 0.027829 | -0.097207 | 0.007032 | 0.027798 | -0.060955 | -0.016906 | 122.6743 | 122.5165 | 122.6137 | 122.5641 | 122.6712 | 122.6472 | 122.5355 | 0.10285 | 0.18452 | 0.050717 | -0.074319 | 0.02992 | 0.050686 | -0.038067 | 0.005982 | 0.072927 | 0.14091 | 0.020797 | 0.088784
2463.4531 | 122.8088 | -122.6028 | 0.12817 | 0.053175 | -0.10004 | -0.007421 | -0.047909 | 0.054577 | 0.035221 | -0.071874 | 0.070802 | 0.15706 | 0.018672 | -0.10637 | 0.01161 | 0.036954 | -0.070112 | -0.016906 | 122.656 | 122.5028 | 122.5954 | 122.5549 | 122.6574 | 122.6381 | 122.531 | 0.09369 | 0.17994 | 0.04156 | -0.083477 | 0.034498 | 0.059842 | -0.047224 | 0.005982 | 0.059192 | 0.14091 | 0.007062 | 0.088784
2465.1719 | 122.7814 | -122.6303 | 0.13275 | 0.053175 | -0.10004 | -0.002842 | -0.043331 | 0.059155 | 0.035221 | -0.071874 | 0.079959 | 0.16622 | 0.02325 | -0.11094 | 0.01161 | 0.032376 | -0.060955 | -0.021484 | 122.6835 | 122.5303 | 122.6275 | 122.587 | 122.6895 | 122.6655 | 122.5584 | 0.10285 | 0.1891 | 0.046138 | -0.088056 | 0.034498 | 0.055264 | -0.038067 | 0.001404 | 0.068349 | 0.14091 | 0.01164 | 0.084205
2466.9531 | 122.7585 | -122.6532 | 0.13733 | 0.062332 | -0.095467 | 0.001736 | -0.047909 | 0.059155 | 0.030642 | -0.076452 | 0.07538 | 0.15706 | 0.027829 | -0.11552 | 0.01161 | 0.027798 | -0.065533 | -0.026063 | 122.7155 | 122.5577 | 122.6549 | 122.6053 | 122.7124 | 122.6838 | 122.5767 | 0.098268 | 0.17994 | 0.050717 | -0.092635 | 0.034498 | 0.050686 | -0.042645 | -0.003175 | 0.06377 | 0.14091 | 0.016219 | 0.093362
2468.7031 | 122.8088 | -122.6212 | 0.11444 | 0.057754 | -0.090888 | 0.006315 | -0.047909 | 0.059155 | 0.035221 | -0.071874 | 0.070802 | 0.16622 | 0.018672 | -0.10637 | 0.007032 | 0.027798 | -0.065533 | -0.021484 | 122.6789 | 122.5303 | 122.6275 | 122.5732 | 122.6803 | 122.6564 | 122.5493 | 0.09369 | 0.1891 | 0.04156 | -0.083477 | 0.02992 | 0.050686 | -0.042645 | 0.001404 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2470.4844 | 122.8134 | -122.6212 | 0.11444 | 0.057754 | -0.095467 | -0.002842 | -0.047909 | 0.054577 | 0.030642 | -0.071874 | 0.079959 | 0.16622 | 0.02325 | -0.097207 | 0.01161 | 0.032376 | -0.065533 | -0.016906 | 122.6789 | 122.5257 | 122.6183 | 122.5732 | 122.6757 | 122.6518 | 122.5493 | 0.10285 | 0.1891 | 0.046138 | -0.074319 | 0.034498 | 0.055264 | -0.042645 | 0.005982 | 0.068349 | 0.14549 | 0.01164 | 0.088783
2472.2656 | 122.818 | -122.6486 | 0.1236 | 0.048597 | -0.10462 | 0.001736 | -0.057066 | 0.059155 | 0.039799 | -0.067295 | 0.07538 | 0.16164 | 0.027829 | -0.11094 | 0.01161 | 0.032376 | -0.070112 | -0.021484 | 122.6972 | 122.544 | 122.6504 | 122.5916 | 122.7078 | 122.6884 | 122.5813 | 0.098268 | 0.18452 | 0.050717 | -0.088056 | 0.034498 | 0.055264 | -0.047224 | 0.001404 | 0.06377 | 0.14549 | 0.016219 | 0.097941
2473.9688 | 122.8729 | -122.5983 | 0.09613 | 0.062332 | -0.090888 | -0.002842 | -0.047909 | 0.054577 | 0.026064 | -0.071874 | 0.079959 | 0.17537 | 0.018672 | -0.11094 | 0.01161 | 0.032376 | -0.060955 | -0.026063 | 122.6606 | 122.5074 | 122.5954 | 122.5504 | 122.6528 | 122.6243 | 122.5264 | 0.10285 | 0.19826 | 0.04156 | -0.088056 | 0.034498 | 0.055264 | -0.038067 | -0.003175 | 0.068349 | 0.14091 | 0.007062 | 0.079627
2475.7188 | 122.7859 | -122.6624 | 0.1236 | 0.057754 | -0.086309 | 0.001736 | -0.043331 | 0.059155 | 0.035221 | -0.071874 | 0.07538 | 0.16622 | 0.02325 | -0.097207 | 0.01161 | 0.032376 | -0.065533 | -0.012328 | 122.7201 | 122.576 | 122.6641 | 122.619 | 122.7215 | 122.6976 | 122.5905 | 0.098268 | 0.1891 | 0.046138 | -0.074319 | 0.034498 | 0.055264 | -0.042645 | 0.01056 | 0.06377 | 0.14091 | 0.01164 | 0.088783
2477.5 | 122.8134 | -122.6486 | 0.12817 | 0.062332 | -0.090888 | -0.002842 | -0.047909 | 0.054577 | 0.044377 | -0.08103 | 0.070802 | 0.16622 | 0.02325 | -0.10637 | 0.016188 | 0.032376 | -0.060955 | -0.021484 | 122.711 | 122.5577 | 122.6458 | 122.6007 | 122.7032 | 122.693 | 122.5676 | 0.09369 | 0.1891 | 0.046138 | -0.083477 | 0.039076 | 0.055264 | -0.038067 | 0.001404 | 0.054614 | 0.13176 | 0.007062 | 0.084205
2479.2031 | 122.8363 | -122.612 | 0.10529 | 0.06691 | -0.095467 | -0.007421 | -0.052488 | 0.054577 | 0.030642 | -0.076452 | 0.079959 | 0.15706 | 0.018672 | -0.11552 | 0.01161 | 0.032376 | -0.070112 | -0.016906 | 122.6789 | 122.5165 | 122.6046 | 122.5595 | 122.6666 | 122.6426 | 122.5355 | 0.10285 | 0.17994 | 0.04156 | -0.092635 | 0.034498 | 0.055264 | -0.047224 | 0.005982 | 0.068349 | 0.15007 | 0.007062 | 0.088784
2480.9844 | 122.7768 | -122.6807 | 0.1236 | 0.062332 | -0.090888 | -0.002842 | -0.057066 | 0.059155 | 0.035221 | -0.071874 | 0.079959 | 0.16622 | 0.018672 | -0.10637 | 0.01161 | 0.032376 | -0.056376 | -0.016906 | 122.743 | 122.5898 | 122.6778 | 122.6236 | 122.7398 | 122.7159 | 122.6088 | 0.10285 | 0.1891 | 0.04156 | -0.083477 | 0.034498 | 0.055264 | -0.033488 | 0.005982 | 0.068349 | 0.13634 | 0.007062 | 0.075048
2482.75 | 122.8683 | -122.6166 | 0.10986 | 0.057754 | -0.090888 | 0.001736 | -0.047909 | 0.059155 | 0.030642 | -0.071874 | 0.079959 | 0.16164 | 0.02325 | -0.10637 | 0.01161 | 0.032376 | -0.070112 | -0.012328 | 122.6743 | 122.5257 | 122.6183 | 122.5687 | 122.6757 | 122.6472 | 122.5447 | 0.10285 | 0.18452 | 0.046138 | -0.083477 | 0.034498 | 0.055264 | -0.047224 | 0.01056 | 0.068349 | 0.15007 | 0.01164 | 0.093362
2484.5 | 122.9416 | -122.612 | 0.073242 | 0.057754 | -0.095467 | 0.001736 | -0.052488 | 0.059155 | 0.030642 | -0.067295 | 0.070802 | 0.16164 | 0.018672 | -0.097207 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 122.6698 | 122.5165 | 122.6137 | 122.5595 | 122.6712 | 122.6426 | 122.5447 | 0.09369 | 0.18452 | 0.04156 | -0.074319 | 0.02992 | 0.055264 | -0.042645 | 0.01056 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2486.2031 | 122.7814 | -122.644 | 0.11902 | 0.062332 | -0.090888 | -0.002842 | -0.043331 | 0.059155 | 0.039799 | -0.076452 | 0.066223 | 0.16622 | 0.027829 | -0.11552 | 0.01161 | 0.032376 | -0.065533 | -0.012328 | 122.7064 | 122.5532 | 122.6412 | 122.6007 | 122.7032 | 122.6838 | 122.5676 | 0.089111 | 0.1891 | 0.050717 | -0.092635 | 0.034498 | 0.055264 | -0.042645 | 0.01056 | 0.054613 | 0.13176 | 0.016219 | 0.093362
2487.9688 | 122.905 | -122.6257 | 0.10071 | 0.06691 | -0.10004 | 0.001736 | -0.047909 | 0.054577 | 0.035221 | -0.067295 | 0.070802 | 0.17079 | 0.02325 | -0.10637 | 0.007032 | 0.027798 | -0.070112 | -0.012328 | 122.6926 | 122.5257 | 122.6275 | 122.5778 | 122.6803 | 122.661 | 122.5584 | 0.09369 | 0.19368 | 0.046138 | -0.083477 | 0.02992 | 0.050686 | -0.047224 | 0.01056 | 0.06377 | 0.14091 | 0.016218 | 0.093362
2489.7188 | 122.8867 | -122.644 | 0.10071 | 0.062332 | -0.086309 | 0.001736 | -0.034174 | 0.054577 | 0.039799 | -0.067295 | 0.07538 | 0.16622 | 0.018672 | -0.097207 | 0.007032 | 0.027798 | -0.065533 | -0.021484 | 122.7064 | 122.5577 | 122.6458 | 122.6099 | 122.6986 | 122.6838 | 122.5767 | 0.098268 | 0.1891 | 0.04156 | -0.074319 | 0.02992 | 0.050686 | -0.042645 | 0.001404 | 0.068348 | 0.14091 | 0.01164 | 0.084205
2491.4844 | 122.7905 | -122.6486 | 0.13275 | 0.062332 | -0.090888 | 0.001736 | -0.043331 | 0.063733 | 0.035221 | -0.071874 | 0.070802 | 0.16164 | 0.027829 | -0.10179 | 0.007032 | 0.027798 | -0.070112 | -0.021484 | 122.711 | 122.5577 | 122.6504 | 122.6053 | 122.7124 | 122.6838 | 122.5767 | 0.09369 | 0.18452 | 0.050717 | -0.078898 | 0.02992 | 0.050686 | -0.047224 | 0.001404 | 0.06377 | 0.14091 | 0.020797 | 0.097941
2493.2656 | 122.8592 | -122.6578 | 0.09613 | 0.057754 | -0.090888 | 0.001736 | -0.043331 | 0.059155 | 0.039799 | -0.071874 | 0.070802 | 0.16622 | 0.02325 | -0.11094 | 0.01161 | 0.041532 | -0.065533 | -0.012328 | 122.7155 | 122.5669 | 122.6595 | 122.6144 | 122.7169 | 122.6976 | 122.5859 | 0.09369 | 0.1891 | 0.046138 | -0.088056 | 0.034498 | 0.06442 | -0.042645 | 0.01056 | 0.059192 | 0.13633 | 0.01164 | 0.088783
2494.9688 | 122.9324 | -122.5983 | 0.082397 | 0.057754 | -0.095467 | 0.006315 | -0.043331 | 0.049999 | 0.035221 | -0.071874 | 0.07538 | 0.16622 | 0.018672 | -0.11094 | 0.01161 | 0.032376 | -0.056376 | -0.012328 | 122.656 | 122.5028 | 122.6046 | 122.5549 | 122.6483 | 122.6335 | 122.5264 | 0.098268 | 0.1891 | 0.04156 | -0.088056 | 0.034498 | 0.055264 | -0.033488 | 0.01056 | 0.06377 | 0.13176 | 0.007062 | 0.075048
2496.7188 | 122.8088 | -122.6761 | 0.10529 | 0.062332 | -0.095467 | -0.012 | -0.047909 | 0.063733 | 0.030642 | -0.071874 | 0.066223 | 0.16164 | 0.018672 | -0.11094 | 0.01161 | 0.032376 | -0.070112 | -0.021484 | 122.7384 | 122.5806 | 122.6641 | 122.6282 | 122.7398 | 122.7067 | 122.6042 | 0.089111 | 0.18452 | 0.04156 | -0.088056 | 0.034498 | 0.055264 | -0.047224 | 0.001404 | 0.054613 | 0.13633 | 0.007062 | 0.088784
2498.4219 | 122.9187 | -122.6166 | 0.091553 | 0.062332 | -0.095467 | 0.001736 | -0.043331 | 0.063733 | 0.039799 | -0.076452 | 0.070802 | 0.16622 | 0.018672 | -0.097207 | 0.002454 | 0.027798 | -0.065533 | -0.021484 | 122.6789 | 122.5211 | 122.6183 | 122.5732 | 122.6803 | 122.6564 | 122.5401 | 0.09369 | 0.1891 | 0.04156 | -0.074319 | 0.025342 | 0.050686 | -0.042645 | 0.001404 | 0.068348 | 0.13633 | 0.016218 | 0.084205
2500.1875 | 122.7997 | -122.6578 | 0.12817 | 0.076067 | -0.090888 | -0.002842 | -0.043331 | 0.059155 | 0.039799 | -0.067295 | 0.070802 | 0.16164 | 0.018672 | -0.092628 | 0.01161 | 0.032376 | -0.060955 | -0.016906 | 122.7338 | 122.5669 | 122.6549 | 122.6144 | 122.7169 | 122.6976 | 122.5905 | 0.09369 | 0.18452 | 0.04156 | -0.06974 | 0.034498 | 0.055264 | -0.038067 | 0.005982 | 0.059192 | 0.13176 | 0.007062 | 0.079627
2501.8906 | 122.9233 | -122.6212 | 0.068665 | 0.057754 | -0.08173 | 0.001736 | -0.043331 | 0.059155 | 0.035221 | -0.071874 | 0.070802 | 0.16622 | 0.014094 | -0.097207 | 0.007032 | 0.02322 | -0.07469 | -0.026063 | 122.6789 | 122.5394 | 122.6229 | 122.5778 | 122.6803 | 122.6564 | 122.5493 | 0.09369 | 0.1891 | 0.036982 | -0.074319 | 0.02992 | 0.046108 | -0.051802 | -0.003175 | 0.06377 | 0.14549 | 0.007062 | 0.088784
2503.6562 | 122.8592 | -122.644 | 0.10986 | 0.057754 | -0.095467 | 0.001736 | -0.047909 | 0.059155 | 0.039799 | -0.067295 | 0.079959 | 0.16164 | 0.02325 | -0.10637 | 0.01161 | 0.027798 | -0.060955 | -0.016906 | 122.7018 | 122.5486 | 122.6458 | 122.5961 | 122.7032 | 122.6838 | 122.5767 | 0.10285 | 0.18452 | 0.046138 | -0.083477 | 0.034498 | 0.050686 | -0.038067 | 0.005982 | 0.068349 | 0.14091 | 0.01164 | 0.084205
2505.4375 | 122.905 | -122.6807 | 0.086975 | 0.062332 | -0.090888 | -0.002842 | -0.047909 | 0.054577 | 0.035221 | -0.067295 | 0.07538 | 0.16622 | 0.018672 | -0.10637 | 0.007032 | 0.036954 | -0.060955 | -0.012328 | 122.743 | 122.5898 | 122.6778 | 122.6328 | 122.7352 | 122.7159 | 122.6134 | 0.098268 | 0.1891 | 0.04156 | -0.083477 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.068348 | 0.13634 | 0.01164 | 0.079627
2507.1406 | 122.8134 | -122.6761 | 0.11444 | 0.06691 | -0.090888 | 0.006315 | -0.043331 | 0.063733 | 0.044377 | -0.058139 | 0.07538 | 0.16622 | 0.02325 | -0.10179 | 0.01161 | 0.02322 | -0.056376 | -0.016906 | 122.743 | 122.5852 | 122.6824 | 122.6328 | 122.7398 | 122.7205 | 122.6179 | 0.098268 | 0.1891 | 0.046138 | -0.078898 | 0.034498 | 0.046108 | -0.033488 | 0.005982 | 0.06377 | 0.13176 | 0.01164 | 0.079626
2508.8906 | 122.9416 | -122.6257 | 0.09613 | 0.062332 | -0.090888 | 0.001736 | -0.047909 | 0.059155 | 0.035221 | -0.071874 | 0.07538 | 0.16622 | 0.02325 | -0.11094 | 0.01161 | 0.032376 | -0.065533 | -0.016906 | 122.6881 | 122.5348 | 122.6275 | 122.5778 | 122.6849 | 122.661 | 122.5539 | 0.098268 | 0.1891 | 0.046138 | -0.088056 | 0.034498 | 0.055264 | -0.042645 | 0.005982 | 0.06377 | 0.14091 | 0.01164 | 0.088783
2510.5781 | 122.9233 | -122.644 | 0.09613 | 0.06691 | -0.090888 | 0.001736 | -0.038752 | 0.063733 | 0.044377 | -0.067295 | 0.070802 | 0.16164 | 0.014094 | -0.10637 | 0.01161 | 0.036954 | -0.060955 | -0.021484 | 122.711 | 122.5532 | 122.6458 | 122.6053 | 122.7078 | 122.6884 | 122.5767 | 0.09369 | 0.18452 | 0.036982 | -0.083477 | 0.034498 | 0.059842 | -0.038067 | 0.001404 | 0.059192 | 0.13176 | 0.002484 | 0.075049
2512.3438 | 122.7905 | -122.6532 | 0.1236 | 0.071489 | -0.086309 | 0.001736 | -0.043331 | 0.06831 | 0.044377 | -0.067295 | 0.070802 | 0.15706 | 0.018672 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 122.7247 | 122.5669 | 122.6549 | 122.6099 | 122.7215 | 122.6976 | 122.5859 | 0.09369 | 0.17994 | 0.04156 | -0.088056 | 0.02992 | 0.055264 | -0.042645 | 0.01056 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2514.0938 | 122.7905 | -122.6807 | 0.13733 | 0.06691 | -0.086309 | 0.001736 | -0.038752 | 0.063733 | 0.039799 | -0.067295 | 0.070802 | 0.16164 | 0.027829 | -0.092628 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 122.7476 | 122.5944 | 122.6824 | 122.6419 | 122.7444 | 122.7205 | 122.6134 | 0.09369 | 0.18452 | 0.050717 | -0.06974 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.06377 | 0.13176 | 0.020797 | 0.088784
2515.8438 | 122.818 | -122.7081 | 0.1236 | 0.062332 | -0.077151 | 0.006315 | -0.038752 | 0.063733 | 0.039799 | -0.071874 | 0.070802 | 0.15706 | 0.018672 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.021484 | 122.7705 | 122.631 | 122.7144 | 122.6694 | 122.7719 | 122.7479 | 122.6363 | 0.09369 | 0.17994 | 0.04156 | -0.083477 | 0.025342 | 0.055264 | -0.042645 | 0.001404 | 0.068348 | 0.13633 | 0.016218 | 0.084205
2517.6094 | 122.8867 | -122.644 | 0.10529 | 0.057754 | -0.086309 | 0.006315 | -0.038752 | 0.063733 | 0.044377 | -0.067295 | 0.07538 | 0.16622 | 0.014094 | -0.074312 | 0.002454 | 0.032376 | -0.070112 | -0.016906 | 122.7018 | 122.5577 | 122.6504 | 122.6053 | 122.7078 | 122.6884 | 122.5767 | 0.098268 | 0.1891 | 0.036982 | -0.051424 | 0.025342 | 0.055264 | -0.047224 | 0.005982 | 0.072926 | 0.14549 | 0.01164 | 0.084206
2519.375 | 122.9416 | -122.6395 | 0.09613 | 0.062332 | -0.08173 | 0.001736 | -0.043331 | 0.059155 | 0.044377 | -0.062717 | 0.07538 | 0.16164 | 0.018672 | -0.10179 | 0.016188 | 0.032376 | -0.065533 | -0.026063 | 122.7018 | 122.5577 | 122.6412 | 122.5961 | 122.6986 | 122.6838 | 122.5767 | 0.098268 | 0.18452 | 0.04156 | -0.078898 | 0.039076 | 0.055264 | -0.042645 | -0.003175 | 0.059192 | 0.14091 | 0.002484 | 0.084205
2521.1406 | 122.9141 | -122.6395 | 0.07782 | 0.071489 | -0.086309 | 0.006315 | -0.043331 | 0.063733 | 0.044377 | -0.062717 | 0.070802 | 0.16622 | 0.018672 | -0.11094 | 0.01161 | 0.036954 | -0.065533 | -0.021484 | 122.711 | 122.5532 | 122.6458 | 122.5961 | 122.7032 | 122.6838 | 122.5767 | 0.09369 | 0.1891 | 0.04156 | -0.088056 | 0.034498 | 0.059842 | -0.042645 | 0.001404 | 0.059192 | 0.13633 | 0.007062 | 0.084205
2522.8438 | 122.8592 | -122.6807 | 0.1236 | 0.06691 | -0.090888 | 0.001736 | -0.043331 | 0.059155 | 0.039799 | -0.062717 | 0.07538 | 0.16622 | 0.02325 | -0.097207 | 0.002454 | 0.027798 | -0.065533 | -0.021484 | 122.7476 | 122.5898 | 122.6824 | 122.6373 | 122.7398 | 122.7205 | 122.6179 | 0.098268 | 0.1891 | 0.046138 | -0.074319 | 0.025342 | 0.050686 | -0.042645 | 0.001404 | 0.072926 | 0.14091 | 0.020796 | 0.088783
2524.5938 | 122.8226 | -122.6852 | 0.12817 | 0.062332 | -0.08173 | 0.006315 | -0.043331 | 0.059155 | 0.035221 | -0.067295 | 0.070802 | 0.16164 | 0.018672 | -0.097207 | 0.01161 | 0.032376 | -0.065533 | -0.016906 | 122.7476 | 122.6035 | 122.6916 | 122.6419 | 122.7444 | 122.7205 | 122.6179 | 0.09369 | 0.18452 | 0.04156 | -0.074319 | 0.034498 | 0.055264 | -0.042645 | 0.005982 | 0.059192 | 0.13633 | 0.007062 | 0.084205
2526.3594 | 122.9462 | -122.6349 | 0.07782 | 0.06691 | -0.090888 | 0.006315 | -0.038752 | 0.059155 | 0.048956 | -0.067295 | 0.079959 | 0.15248 | 0.02325 | -0.10637 | 0.007032 | 0.027798 | -0.065533 | -0.021484 | 122.7018 | 122.544 | 122.6412 | 122.5961 | 122.694 | 122.6838 | 122.5676 | 0.10285 | 0.17537 | 0.046138 | -0.083477 | 0.02992 | 0.050686 | -0.042645 | 0.001404 | 0.072927 | 0.14549 | 0.016218 | 0.088783
2528.0625 | 122.8455 | -122.6944 | 0.12817 | 0.071489 | -0.077151 | 0.001736 | -0.034174 | 0.06831 | 0.039799 | -0.067295 | 0.07538 | 0.15248 | 0.02325 | -0.092628 | 0.007032 | 0.02322 | -0.065533 | -0.021484 | 122.7659 | 122.6172 | 122.6961 | 122.6602 | 122.7627 | 122.7342 | 122.6271 | 0.098268 | 0.17537 | 0.046138 | -0.06974 | 0.02992 | 0.046108 | -0.042645 | 0.001404 | 0.068348 | 0.14091 | 0.016218 | 0.088783
2529.8125 | 122.8867 | -122.6944 | 0.11444 | 0.06691 | -0.086309 | 0.001736 | -0.034174 | 0.059155 | 0.044377 | -0.067295 | 0.070802 | 0.15706 | 0.02325 | -0.10179 | 0.002454 | 0.02322 | -0.060955 | -0.016906 | 122.7613 | 122.6081 | 122.6961 | 122.6602 | 122.7536 | 122.7388 | 122.6271 | 0.09369 | 0.17994 | 0.046138 | -0.078898 | 0.025342 | 0.046108 | -0.038067 | 0.005982 | 0.068348 | 0.13176 | 0.020796 | 0.084205
2531.5 | 122.9507 | -122.6715 | 0.068665 | 0.062332 | -0.08173 | 0.001736 | -0.043331 | 0.06831 | 0.039799 | -0.071874 | 0.066223 | 0.16164 | 0.018672 | -0.10179 | 0.01161 | 0.027798 | -0.060955 | -0.016906 | 122.7338 | 122.5898 | 122.6732 | 122.6282 | 122.7398 | 122.7113 | 122.5996 | 0.089111 | 0.18452 | 0.04156 | -0.078898 | 0.034498 | 0.050686 | -0.038067 | 0.005982 | 0.054613 | 0.12718 | 0.007062 | 0.079627
2533.25 | 122.937 | -122.6669 | 0.10529 | 0.06691 | -0.090888 | 0.001736 | -0.047909 | 0.072888 | 0.039799 | -0.071874 | 0.070802 | 0.16164 | 0.018672 | -0.097207 | 0.002454 | 0.032376 | -0.065533 | -0.021484 | 122.7338 | 122.576 | 122.6687 | 122.619 | 122.7398 | 122.7067 | 122.5951 | 0.09369 | 0.18452 | 0.04156 | -0.074319 | 0.025342 | 0.055264 | -0.042645 | 0.001404 | 0.068348 | 0.13633 | 0.016218 | 0.084205
2535.0156 | 122.8363 | -122.7173 | 0.11902 | 0.071489 | -0.090888 | 0.001736 | -0.038752 | 0.063733 | 0.039799 | -0.062717 | 0.070802 | 0.16622 | 0.018672 | -0.097207 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 122.7888 | 122.6264 | 122.719 | 122.6785 | 122.781 | 122.7571 | 122.6546 | 0.09369 | 0.1891 | 0.04156 | -0.074319 | 0.02992 | 0.055264 | -0.042645 | 0.005982 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2536.7812 | 122.9599 | -122.6349 | 0.086975 | 0.062332 | -0.090888 | 0.006315 | -0.038752 | 0.059155 | 0.044377 | -0.067295 | 0.070802 | 0.16164 | 0.02325 | -0.10637 | 0.007032 | 0.036954 | -0.060955 | -0.016906 | 122.6972 | 122.544 | 122.6412 | 122.5961 | 122.694 | 122.6793 | 122.5676 | 0.09369 | 0.18452 | 0.046138 | -0.083477 | 0.02992 | 0.059842 | -0.038067 | 0.005982 | 0.06377 | 0.13176 | 0.016218 | 0.084205
2538.5469 | 122.8271 | -122.6807 | 0.13275 | 0.071489 | -0.08173 | 0.001736 | -0.043331 | 0.063733 | 0.048956 | -0.062717 | 0.07538 | 0.15248 | 0.014094 | -0.10179 | 0.01161 | 0.02322 | -0.065533 | -0.016906 | 122.7522 | 122.5989 | 122.6824 | 122.6373 | 122.7444 | 122.7296 | 122.6179 | 0.098268 | 0.17537 | 0.036982 | -0.078898 | 0.034498 | 0.046108 | -0.042645 | 0.005982 | 0.06377 | 0.14091 | 0.002484 | 0.079627
2540.2344 | 122.9599 | -122.6669 | 0.082397 | 0.057754 | -0.086309 | 0.006315 | -0.038752 | 0.054577 | 0.044377 | -0.062717 | 0.07538 | 0.16622 | 0.018672 | -0.10179 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 122.7247 | 122.5806 | 122.6732 | 122.6282 | 122.7215 | 122.7113 | 122.6042 | 0.098268 | 0.1891 | 0.04156 | -0.078898 | 0.02992 | 0.055264 | -0.042645 | 0.005982 | 0.068348 | 0.14091 | 0.01164 | 0.084205
2541.9844 | 122.9233 | -122.6669 | 0.10529 | 0.062332 | -0.090888 | 0.001736 | -0.038752 | 0.063733 | 0.039799 | -0.067295 | 0.07538 | 0.16164 | 0.018672 | -0.11094 | 0.007032 | 0.032376 | -0.060955 | -0.021484 | 122.7293 | 122.576 | 122.6687 | 122.6282 | 122.7307 | 122.7067 | 122.5996 | 0.098268 | 0.18452 | 0.04156 | -0.088056 | 0.02992 | 0.055264 | -0.038067 | 0.001404 | 0.068348 | 0.13634 | 0.01164 | 0.079627
2543.6719 | 122.9828 | -122.6807 | 0.086975 | 0.06691 | -0.08173 | 0.001736 | -0.034174 | 0.059155 | 0.044377 | -0.062717 | 0.070802 | 0.16622 | 0.032407 | -0.097207 | 0.01161 | 0.032376 | -0.056376 | -0.026063 | 122.7476 | 122.5989 | 122.6824 | 122.6465 | 122.7398 | 122.725 | 122.6179 | 0.09369 | 0.1891 | 0.055295 | -0.074319 | 0.034498 | 0.055264 | -0.033488 | -0.003175 | 0.059192 | 0.12718 | 0.020797 | 0.088783
2545.4531 | 122.8363 | -122.6898 | 0.14191 | 0.06691 | -0.08173 | 0.010893 | -0.038752 | 0.063733 | 0.039799 | -0.062717 | 0.070802 | 0.16164 | 0.018672 | -0.097207 | 0.002454 | 0.032376 | -0.070112 | -0.021484 | 122.7567 | 122.6081 | 122.7007 | 122.6511 | 122.7536 | 122.7296 | 122.6271 | 0.09369 | 0.18452 | 0.04156 | -0.074319 | 0.025342 | 0.055264 | -0.047224 | 0.001404 | 0.068348 | 0.14091 | 0.016218 | 0.088784
2547.2188 | 122.9004 | -122.6807 | 0.10986 | 0.071489 | -0.090888 | 0.006315 | -0.047909 | 0.072888 | 0.048956 | -0.067295 | 0.070802 | 0.15248 | 0.018672 | -0.11552 | 0.002454 | 0.027798 | -0.070112 | -0.012328 | 122.7522 | 122.5898 | 122.687 | 122.6328 | 122.7536 | 122.7296 | 122.6134 | 0.09369 | 0.17537 | 0.04156 | -0.092635 | 0.025342 | 0.050686 | -0.047224 | 0.01056 | 0.068348 | 0.14091 | 0.016218 | 0.088784
2548.9844 | 122.9874 | -122.6807 | 0.10071 | 0.06691 | -0.090888 | 0.001736 | -0.038752 | 0.063733 | 0.035221 | -0.062717 | 0.07538 | 0.15706 | 0.02325 | -0.10179 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 122.7476 | 122.5898 | 122.6824 | 122.6419 | 122.7444 | 122.7159 | 122.6179 | 0.098268 | 0.17994 | 0.046138 | -0.078898 | 0.02992 | 0.055264 | -0.047224 | 0.005982 | 0.068348 | 0.14549 | 0.016218 | 0.093362
2550.6719 | 122.9599 | -122.6761 | 0.10071 | 0.06691 | -0.08173 | 0.001736 | -0.034174 | 0.059155 | 0.048956 | -0.062717 | 0.07538 | 0.15706 | 0.02325 | -0.11552 | 0.01161 | 0.032376 | -0.060955 | -0.016906 | 122.743 | 122.5944 | 122.6778 | 122.6419 | 122.7352 | 122.725 | 122.6134 | 0.098268 | 0.17994 | 0.046138 | -0.092635 | 0.034498 | 0.055264 | -0.038067 | 0.005982 | 0.06377 | 0.13634 | 0.01164 | 0.084205
2552.4375 | 122.9187 | -122.6898 | 0.082397 | 0.06691 | -0.086309 | 0.006315 | -0.038752 | 0.059155 | 0.044377 | -0.067295 | 0.070802 | 0.16164 | 0.02325 | -0.088049 | 0.002454 | 0.02322 | -0.060955 | -0.021484 | 122.7567 | 122.6035 | 122.6961 | 122.6511 | 122.749 | 122.7342 | 122.6225 | 0.09369 | 0.18452 | 0.046138 | -0.065161 | 0.025342 | 0.046108 | -0.038067 | 0.001404 | 0.068348 | 0.13176 | 0.020796 | 0.084205
2554.2188 | 122.8775 | -122.6898 | 0.10529 | 0.06691 | -0.077151 | 0.001736 | -0.043331 | 0.063733 | 0.048956 | -0.067295 | 0.07538 | 0.16164 | 0.014094 | -0.10179 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 122.7567 | 122.6127 | 122.6916 | 122.6465 | 122.7536 | 122.7388 | 122.6225 | 0.098268 | 0.18452 | 0.036982 | -0.078898 | 0.025342 | 0.059842 | -0.042645 | 0.005982 | 0.072926 | 0.14091 | 0.01164 | 0.079627
2555.9844 | 122.9233 | -122.6852 | 0.09613 | 0.06691 | -0.08173 | 0.006315 | -0.052488 | 0.063733 | 0.044377 | -0.067295 | 0.070802 | 0.17079 | 0.018672 | -0.11552 | 0.01161 | 0.027798 | -0.056376 | -0.021484 | 122.7522 | 122.6035 | 122.6916 | 122.6328 | 122.749 | 122.7296 | 122.6179 | 0.09369 | 0.19368 | 0.04156 | -0.092635 | 0.034498 | 0.050686 | -0.033488 | 0.001404 | 0.059192 | 0.12718 | 0.007062 | 0.075048
2557.6719 | 122.8592 | -122.699 | 0.1236 | 0.06691 | -0.08173 | 0.001736 | -0.043331 | 0.063733 | 0.044377 | -0.067295 | 0.066223 | 0.16622 | 0.018672 | -0.11094 | 0.01161 | 0.027798 | -0.07469 | -0.021484 | 122.7659 | 122.6172 | 122.7007 | 122.6556 | 122.7627 | 122.7434 | 122.6317 | 0.089111 | 0.1891 | 0.04156 | -0.088056 | 0.034498 | 0.050686 | -0.051802 | 0.001404 | 0.054613 | 0.14091 | 0.007062 | 0.093362
2559.4375 | 122.8958 | -122.7127 | 0.082397 | 0.06691 | -0.086309 | 0.006315 | -0.038752 | 0.063733 | 0.048956 | -0.058139 | 0.07538 | 0.16164 | 0.027829 | -0.092628 | 0.007032 | 0.018642 | -0.065533 | -0.021484 | 122.7796 | 122.6264 | 122.719 | 122.674 | 122.7764 | 122.7617 | 122.6546 | 0.098268 | 0.18452 | 0.050717 | -0.06974 | 0.02992 | 0.04153 | -0.042645 | 0.001404 | 0.068348 | 0.14091 | 0.020797 | 0.093362
2561.1875 | 122.9416 | -122.7036 | 0.091553 | 0.062332 | -0.090888 | -0.002842 | -0.047909 | 0.063733 | 0.048956 | -0.071874 | 0.079959 | 0.15248 | 0.014094 | -0.10637 | 0.01161 | 0.032376 | -0.070112 | -0.021484 | 122.7659 | 122.6127 | 122.7007 | 122.6556 | 122.7673 | 122.7525 | 122.6317 | 0.10285 | 0.17537 | 0.036982 | -0.083477 | 0.034498 | 0.055264 | -0.047224 | 0.001404 | 0.068349 | 0.15007 | 0.002484 | 0.084206
2562.8906 | 122.9095 | -122.7173 | 0.11444 | 0.071489 | -0.086309 | -0.002842 | -0.038752 | 0.063733 | 0.048956 | -0.067295 | 0.07538 | 0.15706 | 0.018672 | -0.097207 | 0.007032 | 0.032376 | -0.060955 | -0.026063 | 122.7888 | 122.631 | 122.7144 | 122.6785 | 122.781 | 122.7662 | 122.65 | 0.098268 | 0.17994 | 0.04156 | -0.074319 | 0.02992 | 0.055264 | -0.038067 | -0.003175 | 0.068348 | 0.13634 | 0.01164 | 0.079627
2564.5781 | 122.905 | -122.6807 | 0.10529 | 0.06691 | -0.086309 | 0.001736 | -0.038752 | 0.059155 | 0.048956 | -0.062717 | 0.066223 | 0.15706 | 0.02325 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.021484 | 122.7476 | 122.5944 | 122.6824 | 122.6419 | 122.7398 | 122.7296 | 122.6179 | 0.089111 | 0.17994 | 0.046138 | -0.078898 | 0.034498 | 0.059842 | -0.047224 | 0.001404 | 0.054613 | 0.13633 | 0.01164 | 0.093362
2566.3438 | 122.9462 | -122.6715 | 0.059509 | 0.071489 | -0.086309 | 0.001736 | -0.043331 | 0.063733 | 0.048956 | -0.067295 | 0.07538 | 0.16164 | 0.009515 | -0.074312 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 122.743 | 122.5852 | 122.6732 | 122.6282 | 122.7352 | 122.7205 | 122.6042 | 0.098268 | 0.18452 | 0.032403 | -0.051424 | 0.02992 | 0.059842 | -0.042645 | 0.005982 | 0.068348 | 0.14091 | 0.002483 | 0.075048
2568.125 | 122.8775 | -122.7127 | 0.1236 | 0.071489 | -0.077151 | 0.006315 | -0.038752 | 0.063733 | 0.053534 | -0.071874 | 0.070802 | 0.15706 | 0.018672 | -0.10179 | 0.007032 | 0.027798 | -0.065533 | -0.021484 | 122.7842 | 122.6356 | 122.719 | 122.674 | 122.7764 | 122.7662 | 122.6408 | 0.09369 | 0.17994 | 0.04156 | -0.078898 | 0.02992 | 0.050686 | -0.042645 | 0.001404 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2569.8125 | 122.9507 | -122.6898 | 0.073242 | 0.071489 | -0.086309 | -0.007421 | -0.038752 | 0.063733 | 0.044377 | -0.062717 | 0.070802 | 0.16164 | 0.027829 | -0.10179 | 0.002454 | 0.032376 | -0.060955 | -0.016906 | 122.7613 | 122.6035 | 122.6824 | 122.6511 | 122.7536 | 122.7342 | 122.6271 | 0.09369 | 0.18452 | 0.050717 | -0.078898 | 0.025342 | 0.055264 | -0.038067 | 0.005982 | 0.068348 | 0.13176 | 0.025375 | 0.088784
2571.5156 | 122.9965 | -122.6944 | 0.07782 | 0.06691 | -0.08173 | 0.001736 | -0.043331 | 0.059155 | 0.039799 | -0.062717 | 0.079959 | 0.15706 | 0.014094 | -0.11552 | 0.007032 | 0.032376 | -0.056376 | -0.016906 | 122.7613 | 122.6127 | 122.6961 | 122.6511 | 122.7536 | 122.7342 | 122.6317 | 0.10285 | 0.17994 | 0.036982 | -0.092635 | 0.02992 | 0.055264 | -0.033488 | 0.005982 | 0.072927 | 0.13634 | 0.007062 | 0.07047
2573.2188 | 123.0057 | -122.6807 | 0.091553 | 0.06691 | -0.086309 | 0.006315 | -0.043331 | 0.072888 | 0.048956 | -0.062717 | 0.079959 | 0.16164 | 0.018672 | -0.11094 | 0.016188 | 0.036954 | -0.065533 | -0.026063 | 122.7476 | 122.5944 | 122.687 | 122.6373 | 122.7536 | 122.7296 | 122.6179 | 0.10285 | 0.18452 | 0.04156 | -0.088056 | 0.039076 | 0.059842 | -0.042645 | -0.003175 | 0.063771 | 0.14549 | 0.002484 | 0.084205
2574.9844 | 122.9874 | -122.6944 | 0.10071 | 0.071489 | -0.086309 | -0.002842 | -0.034174 | 0.059155 | 0.044377 | -0.062717 | 0.07538 | 0.16164 | 0.018672 | -0.097207 | 0.007032 | 0.032376 | -0.065533 | -0.021484 | 122.7659 | 122.6081 | 122.6916 | 122.6602 | 122.7536 | 122.7388 | 122.6317 | 0.098268 | 0.18452 | 0.04156 | -0.074319 | 0.02992 | 0.055264 | -0.042645 | 0.001404 | 0.068348 | 0.14091 | 0.01164 | 0.084205
2576.6719 | 122.9919 | -122.6944 | 0.09613 | 0.076067 | -0.08173 | 0.010893 | -0.043331 | 0.06831 | 0.035221 | -0.062717 | 0.061645 | 0.15706 | 0.018672 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 122.7705 | 122.6127 | 122.7053 | 122.6511 | 122.7627 | 122.7296 | 122.6317 | 0.084533 | 0.17994 | 0.04156 | -0.088056 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.054613 | 0.13176 | 0.01164 | 0.088784
2578.4531 | 123.0103 | -122.6807 | 0.09613 | 0.071489 | -0.086309 | -0.002842 | -0.038752 | 0.063733 | 0.044377 | -0.067295 | 0.061645 | 0.15706 | 0.02325 | -0.10179 | 0.016188 | 0.032376 | -0.065533 | -0.021484 | 122.7522 | 122.5944 | 122.6778 | 122.6419 | 122.7444 | 122.725 | 122.6134 | 0.084533 | 0.17994 | 0.046138 | -0.078898 | 0.039076 | 0.055264 | -0.042645 | 0.001404 | 0.045457 | 0.12718 | 0.007062 | 0.088783
2580.2188 | 122.9187 | -122.7539 | 0.10071 | 0.076067 | -0.08173 | 0.010893 | -0.038752 | 0.063733 | 0.048956 | -0.067295 | 0.061645 | 0.16164 | 0.02325 | -0.092628 | 0.016188 | 0.032376 | -0.060955 | -0.021484 | 122.83 | 122.6722 | 122.7648 | 122.7152 | 122.8176 | 122.8029 | 122.6866 | 0.084533 | 0.18452 | 0.046138 | -0.06974 | 0.039076 | 0.055264 | -0.038067 | 0.001404 | 0.045457 | 0.1226 | 0.007062 | 0.084205
2581.9062 | 122.9645 | -122.6669 | 0.091553 | 0.071489 | -0.090888 | 0.006315 | -0.043331 | 0.06831 | 0.039799 | -0.062717 | 0.066223 | 0.16164 | 0.018672 | -0.08347 | 0.002454 | 0.027798 | -0.060955 | -0.016906 | 122.7384 | 122.576 | 122.6732 | 122.6236 | 122.7352 | 122.7067 | 122.6042 | 0.089111 | 0.18452 | 0.04156 | -0.060582 | 0.025342 | 0.050686 | -0.038067 | 0.005982 | 0.063769 | 0.12718 | 0.016218 | 0.079627
2583.6719 | 122.8729 | -122.7127 | 0.14191 | 0.06691 | -0.086309 | 0.006315 | -0.043331 | 0.059155 | 0.048956 | -0.062717 | 0.070802 | 0.16622 | 0.009515 | -0.092628 | 0.01161 | 0.027798 | -0.065533 | -0.021484 | 122.7796 | 122.6264 | 122.719 | 122.6694 | 122.7719 | 122.7617 | 122.65 | 0.09369 | 0.1891 | 0.032403 | -0.06974 | 0.034498 | 0.050686 | -0.042645 | 0.001404 | 0.059192 | 0.13633 | -0.002095 | 0.075048
2585.4531 | 122.9874 | -122.7264 | 0.07782 | 0.071489 | -0.086309 | 0.010893 | -0.034174 | 0.06831 | 0.044377 | -0.067295 | 0.07538 | 0.15706 | 0.014094 | -0.11094 | 0.002454 | 0.02322 | -0.070112 | -0.012328 | 122.7979 | 122.6401 | 122.7373 | 122.6923 | 122.7947 | 122.7708 | 122.6591 | 0.098268 | 0.17994 | 0.036982 | -0.088056 | 0.025342 | 0.046108 | -0.047224 | 0.01056 | 0.072926 | 0.14549 | 0.01164 | 0.084206
2587.2031 | 123.0194 | -122.7081 | 0.07782 | 0.076067 | -0.086309 | 0.001736 | -0.043331 | 0.054577 | 0.044377 | -0.067295 | 0.070802 | 0.15706 | 0.014094 | -0.10179 | 0.016188 | 0.036954 | -0.060955 | -0.021484 | 122.7842 | 122.6218 | 122.7099 | 122.6648 | 122.7627 | 122.7525 | 122.6408 | 0.09369 | 0.17994 | 0.036982 | -0.078898 | 0.039076 | 0.059842 | -0.038067 | 0.001404 | 0.054614 | 0.13176 | -0.002094 | 0.075049
2588.9688 | 123.0103 | -122.699 | 0.082397 | 0.076067 | -0.090888 | 0.006315 | -0.052488 | 0.072888 | 0.039799 | -0.067295 | 0.070802 | 0.16622 | 0.014094 | -0.097207 | 0.002454 | 0.027798 | -0.065533 | -0.012328 | 122.775 | 122.6081 | 122.7053 | 122.6465 | 122.7719 | 122.7388 | 122.6317 | 0.09369 | 0.1891 | 0.036982 | -0.074319 | 0.025342 | 0.050686 | -0.042645 | 0.01056 | 0.068348 | 0.13633 | 0.01164 | 0.079627
2590.6562 | 122.8546 | -122.7127 | 0.10986 | 0.071489 | -0.08173 | 0.006315 | -0.038752 | 0.06831 | 0.044377 | -0.062717 | 0.066223 | 0.16164 | 0.027829 | -0.10637 | 0.007032 | 0.027798 | -0.065533 | -0.016906 | 122.7842 | 122.631 | 122.719 | 122.674 | 122.781 | 122.7571 | 122.65 | 0.089111 | 0.18452 | 0.050717 | -0.083477 | 0.02992 | 0.050686 | -0.042645 | 0.005982 | 0.059191 | 0.13176 | 0.020797 | 0.093362
2592.4375 | 122.9004 | -122.7219 | 0.10529 | 0.071489 | -0.077151 | 0.001736 | -0.038752 | 0.072888 | 0.048956 | -0.062717 | 0.07538 | 0.15706 | 0.018672 | -0.08347 | 0.002454 | 0.036954 | -0.065533 | -0.021484 | 122.7934 | 122.6447 | 122.7236 | 122.6831 | 122.7948 | 122.7708 | 122.6591 | 0.098268 | 0.17994 | 0.04156 | -0.060582 | 0.025342 | 0.059842 | -0.042645 | 0.001404 | 0.072926 | 0.14091 | 0.016218 | 0.084205
2594.1562 | 122.2641 | -122.1588 | 0.11902 | 0.11727 | -0.026784 | 0.052101 | 0.011611 | 0.13698 | 0.09474 | -0.012357 | 0.46455 | 0.50505 | 0.48108 | 0.42938 | 0.071126 | 0.032376 | -0.060955 | -0.012328 | 122.2761 | 122.132 | 122.2109 | 122.1704 | 122.2958 | 122.2536 | 122.1465 | 0.48744 | 0.52794 | 0.50397 | 0.45227 | 0.094014 | 0.055264 | -0.038067 | 0.01056 | 0.39343 | 0.52551 | 0.40995 | 0.54203
2595.9219 | 122.3465 | -122.2275 | 0.10986 | 0.076067 | -0.08173 | 0.010893 | -0.034174 | 0.072888 | 0.053534 | -0.062717 | 0.070802 | 0.16164 | 0.07819 | 0.049322 | 0.002454 | 0.027798 | -0.060955 | -0.021484 | 122.3035 | 122.1457 | 122.2384 | 122.1933 | 122.3004 | 122.281 | 122.1648 | 0.09369 | 0.18452 | 0.10108 | 0.07221 | 0.025342 | 0.050686 | -0.038067 | 0.001404 | 0.068348 | 0.13176 | 0.075736 | 0.13914
2597.625 | 122.5479 | -122.3236 | 0.091553 | 0.06691 | -0.08173 | 0.010893 | -0.034174 | 0.06831 | 0.044377 | -0.067295 | 0.070802 | 0.15706 | 0.018672 | -0.10179 | 0.007032 | 0.027798 | -0.065533 | -0.021484 | 122.3905 | 122.2419 | 122.3345 | 122.2894 | 122.3919 | 122.368 | 122.2563 | 0.09369 | 0.17994 | 0.04156 | -0.078898 | 0.02992 | 0.050686 | -0.042645 | 0.001404 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2599.4062 | 122.5571 | -122.3648 | 0.10529 | 0.076067 | -0.077151 | 0.010893 | -0.034174 | 0.072888 | 0.048956 | -0.062717 | 0.07538 | 0.16622 | 0.014094 | -0.10179 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 122.4409 | 122.2877 | 122.3757 | 122.3306 | 122.4377 | 122.4138 | 122.3021 | 0.098268 | 0.1891 | 0.036982 | -0.078898 | 0.02992 | 0.055264 | -0.042645 | 0.005982 | 0.068348 | 0.14091 | 0.007062 | 0.079627
2601.0938 | 122.5708 | -122.3831 | 0.13275 | 0.076067 | -0.077151 | 0.015472 | -0.038752 | 0.06831 | 0.053534 | -0.058139 | 0.070802 | 0.15706 | 0.02325 | -0.10179 | 0.01161 | 0.027798 | -0.070112 | -0.021484 | 122.4592 | 122.306 | 122.3986 | 122.3444 | 122.4514 | 122.4367 | 122.325 | 0.09369 | 0.17994 | 0.046138 | -0.078898 | 0.034498 | 0.050686 | -0.047224 | 0.001404 | 0.059192 | 0.14091 | 0.01164 | 0.093362
2602.8438 | 122.6074 | -122.4014 | 0.10986 | 0.071489 | -0.08173 | 0.015472 | -0.043331 | 0.06831 | 0.048956 | -0.062717 | 0.07538 | 0.16164 | 0.027829 | -0.10637 | 0.01161 | 0.02322 | -0.065533 | -0.021484 | 122.4729 | 122.3197 | 122.4169 | 122.3581 | 122.4697 | 122.4504 | 122.3387 | 0.098268 | 0.18452 | 0.050717 | -0.083477 | 0.034498 | 0.046108 | -0.042645 | 0.001404 | 0.06377 | 0.14091 | 0.016219 | 0.093362
2604.5469 | 122.6624 | -122.3969 | 0.10071 | 0.076067 | -0.08173 | 0.001736 | -0.043331 | 0.063733 | 0.044377 | -0.058139 | 0.070802 | 0.16622 | 0.014094 | -0.10637 | 0.007032 | 0.02322 | -0.070112 | -0.016906 | 122.4729 | 122.3151 | 122.3986 | 122.3535 | 122.4606 | 122.4412 | 122.3387 | 0.09369 | 0.1891 | 0.036982 | -0.083477 | 0.02992 | 0.046108 | -0.047224 | 0.005982 | 0.06377 | 0.14091 | 0.007062 | 0.084206
2606.3125 | 122.5845 | -122.4243 | 0.1236 | 0.076067 | -0.077151 | 0.010893 | -0.047909 | 0.077466 | 0.044377 | -0.058139 | 0.07538 | 0.15248 | 0.02325 | -0.11094 | 0.002454 | 0.027798 | -0.065533 | -0.021484 | 122.5004 | 122.3472 | 122.4352 | 122.3764 | 122.5018 | 122.4687 | 122.3662 | 0.098268 | 0.17537 | 0.046138 | -0.088056 | 0.025342 | 0.050686 | -0.042645 | 0.001404 | 0.072926 | 0.14091 | 0.020796 | 0.088783
2608.0156 | 122.7127 | -122.4152 | 0.082397 | 0.076067 | -0.086309 | 0.015472 | -0.047909 | 0.072888 | 0.048956 | -0.058139 | 0.070802 | 0.16164 | 0.02325 | -0.11094 | 0.01161 | 0.032376 | -0.060955 | -0.012328 | 122.4912 | 122.3289 | 122.4306 | 122.3673 | 122.488 | 122.4641 | 122.357 | 0.09369 | 0.18452 | 0.046138 | -0.088056 | 0.034498 | 0.055264 | -0.038067 | 0.01056 | 0.059192 | 0.13176 | 0.01164 | 0.084205
2609.7656 | 122.6898 | -122.4335 | 0.09613 | 0.062332 | -0.08173 | 0.015472 | -0.043331 | 0.063733 | 0.053534 | -0.067295 | 0.070802 | 0.15706 | 0.018672 | -0.11094 | 0.007032 | 0.032376 | -0.07469 | -0.026063 | 122.4958 | 122.3517 | 122.4489 | 122.3901 | 122.4972 | 122.487 | 122.3662 | 0.09369 | 0.17994 | 0.04156 | -0.088056 | 0.02992 | 0.055264 | -0.051802 | -0.003175 | 0.06377 | 0.14549 | 0.01164 | 0.093362
2611.5312 | 122.6257 | -122.4609 | 0.11902 | 0.071489 | -0.08173 | 0.015472 | -0.043331 | 0.072888 | 0.048956 | -0.058139 | 0.070802 | 0.16164 | 0.009515 | -0.10179 | -0.002124 | 0.032376 | -0.070112 | -0.021484 | 122.5324 | 122.3792 | 122.4764 | 122.4176 | 122.5338 | 122.5099 | 122.4028 | 0.09369 | 0.18452 | 0.032403 | -0.078898 | 0.020764 | 0.055264 | -0.047224 | 0.001404 | 0.072926 | 0.14091 | 0.011639 | 0.079627
2613.2969 | 122.6028 | -122.5204 | 0.12817 | 0.080646 | -0.08173 | 0.015472 | -0.038752 | 0.072888 | 0.048956 | -0.058139 | 0.070802 | 0.16622 | 0.018672 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.021484 | 122.6011 | 122.4387 | 122.5359 | 122.4817 | 122.5933 | 122.5694 | 122.4623 | 0.09369 | 0.1891 | 0.04156 | -0.083477 | 0.02992 | 0.055264 | -0.042645 | 0.001404 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2615.0156 | 122.6395 | -122.4976 | 0.10071 | 0.071489 | -0.077151 | 0.010893 | -0.047909 | 0.06831 | 0.048956 | -0.067295 | 0.07538 | 0.16622 | 0.027829 | -0.097207 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 122.569 | 122.4204 | 122.5085 | 122.4496 | 122.5659 | 122.5465 | 122.4303 | 0.098268 | 0.1891 | 0.050717 | -0.074319 | 0.025342 | 0.055264 | -0.042645 | 0.01056 | 0.072926 | 0.14091 | 0.025375 | 0.093362
2616.7656 | 122.6303 | -122.5113 | 0.13275 | 0.076067 | -0.077151 | 0.010893 | -0.043331 | 0.06831 | 0.048956 | -0.058139 | 0.07538 | 0.16164 | 0.018672 | -0.078891 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 122.5874 | 122.4341 | 122.5222 | 122.468 | 122.5796 | 122.5602 | 122.4532 | 0.098268 | 0.18452 | 0.04156 | -0.056003 | 0.02992 | 0.055264 | -0.042645 | 0.01056 | 0.068348 | 0.14091 | 0.01164 | 0.084205
2618.5469 | 122.7631 | -122.4518 | 0.09613 | 0.076067 | -0.077151 | 0.020051 | -0.043331 | 0.072888 | 0.048956 | -0.062717 | 0.070802 | 0.15248 | 0.02325 | -0.08347 | 0.007032 | 0.027798 | -0.065533 | -0.021484 | 122.5278 | 122.3746 | 122.4718 | 122.4085 | 122.5247 | 122.5007 | 122.3891 | 0.09369 | 0.17537 | 0.046138 | -0.060582 | 0.02992 | 0.050686 | -0.042645 | 0.001404 | 0.06377 | 0.13633 | 0.016218 | 0.088783
2620.2656 | 122.7814 | -122.5021 | 0.082397 | 0.071489 | -0.086309 | 0.015472 | -0.043331 | 0.077466 | 0.048956 | -0.062717 | 0.066223 | 0.15706 | 0.018672 | -0.074312 | 0.007032 | 0.027798 | -0.065533 | -0.021484 | 122.5736 | 122.4158 | 122.5176 | 122.4588 | 122.5796 | 122.5511 | 122.4394 | 0.089111 | 0.17994 | 0.04156 | -0.051424 | 0.02992 | 0.050686 | -0.042645 | 0.001404 | 0.059191 | 0.13176 | 0.01164 | 0.084205
2622.0312 | 122.6532 | -122.5204 | 0.10986 | 0.080646 | -0.077151 | 0.020051 | -0.043331 | 0.077466 | 0.053534 | -0.062717 | 0.079959 | 0.16164 | 0.009515 | -0.078891 | 0.007032 | 0.032376 | -0.065533 | -0.026063 | 122.6011 | 122.4433 | 122.5405 | 122.4771 | 122.5979 | 122.574 | 122.4577 | 0.10285 | 0.18452 | 0.032403 | -0.056003 | 0.02992 | 0.055264 | -0.042645 | -0.003175 | 0.072927 | 0.14549 | 0.002483 | 0.075048
2623.7812 | 122.7859 | -122.4838 | 0.09613 | 0.076067 | -0.072572 | 0.020051 | -0.038752 | 0.077466 | 0.044377 | -0.053561 | 0.066223 | 0.15706 | 0.018672 | -0.088049 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 122.5599 | 122.4113 | 122.5039 | 122.4451 | 122.5613 | 122.5282 | 122.4303 | 0.089111 | 0.17994 | 0.04156 | -0.065161 | 0.02992 | 0.055264 | -0.042645 | 0.005982 | 0.059191 | 0.13176 | 0.01164 | 0.084205
2625.5 | 122.7905 | -122.4838 | 0.091553 | 0.080646 | -0.08173 | 0.015472 | -0.043331 | 0.072888 | 0.048956 | -0.062717 | 0.066223 | 0.15248 | 0.014094 | -0.08347 | 0.007032 | 0.032376 | -0.056376 | -0.016906 | 122.5645 | 122.4021 | 122.4993 | 122.4405 | 122.5567 | 122.5328 | 122.4211 | 0.089111 | 0.17537 | 0.036982 | -0.060582 | 0.02992 | 0.055264 | -0.033488 | 0.005982 | 0.059191 | 0.1226 | 0.007062 | 0.07047
2627.25 | 122.7356 | -122.5021 | 0.10529 | 0.080646 | -0.08173 | 0.015472 | -0.038752 | 0.072888 | 0.048956 | -0.058139 | 0.070802 | 0.16622 | 0.014094 | -0.10179 | 0.002454 | 0.027798 | -0.070112 | -0.021484 | 122.5828 | 122.4204 | 122.5176 | 122.4634 | 122.575 | 122.5511 | 122.444 | 0.09369 | 0.1891 | 0.036982 | -0.078898 | 0.025342 | 0.050686 | -0.047224 | 0.001404 | 0.068348 | 0.14091 | 0.01164 | 0.084206
2628.9531 | 122.7264 | -122.525 | 0.11902 | 0.080646 | -0.077151 | 0.020051 | -0.043331 | 0.072888 | 0.053534 | -0.058139 | 0.07538 | 0.15706 | 0.018672 | -0.10637 | 0.007032 | 0.027798 | -0.065533 | -0.016906 | 122.6057 | 122.4479 | 122.5451 | 122.4817 | 122.5979 | 122.5786 | 122.4669 | 0.098268 | 0.17994 | 0.04156 | -0.083477 | 0.02992 | 0.050686 | -0.042645 | 0.005982 | 0.068348 | 0.14091 | 0.01164 | 0.084205
2630.7188 | 122.8134 | -122.493 | 0.082397 | 0.085224 | -0.067994 | 0.020051 | -0.043331 | 0.072888 | 0.044377 | -0.062717 | 0.066223 | 0.15706 | 0.018672 | -0.10637 | 0.002454 | 0.02322 | -0.060955 | -0.026063 | 122.5782 | 122.425 | 122.513 | 122.4497 | 122.5659 | 122.5374 | 122.4303 | 0.089111 | 0.17994 | 0.04156 | -0.083477 | 0.025342 | 0.046108 | -0.038067 | -0.003175 | 0.063769 | 0.12718 | 0.016218 | 0.079627
2632.4844 | 122.6898 | -122.5113 | 0.11902 | 0.076067 | -0.072572 | 0.015472 | -0.043331 | 0.082044 | 0.053534 | -0.053561 | 0.061645 | 0.15706 | 0.02325 | -0.097207 | 0.002454 | 0.02322 | -0.065533 | -0.021484 | 122.5874 | 122.4387 | 122.5268 | 122.468 | 122.5933 | 122.5648 | 122.4577 | 0.084533 | 0.17994 | 0.046138 | -0.074319 | 0.025342 | 0.046108 | -0.042645 | 0.001404 | 0.059191 | 0.12718 | 0.020796 | 0.088783
2634.2344 | 122.8271 | -122.5021 | 0.086975 | 0.076067 | -0.077151 | 0.015472 | -0.043331 | 0.06831 | 0.053534 | -0.053561 | 0.070802 | 0.16164 | 0.014094 | -0.10637 | 0.01161 | 0.027798 | -0.060955 | -0.016906 | 122.5782 | 122.425 | 122.5176 | 122.4588 | 122.5704 | 122.5557 | 122.4486 | 0.09369 | 0.18452 | 0.036982 | -0.083477 | 0.034498 | 0.050686 | -0.038067 | 0.005982 | 0.059192 | 0.13176 | 0.002484 | 0.075049
2635.9844 | 122.8043 | -122.4976 | 0.073242 | 0.080646 | -0.072572 | 0.020051 | -0.043331 | 0.077466 | 0.053534 | -0.053561 | 0.070802 | 0.15706 | 0.018672 | -0.10637 | 0.007032 | 0.02322 | -0.065533 | -0.021484 | 122.5782 | 122.425 | 122.5176 | 122.4542 | 122.575 | 122.5511 | 122.444 | 0.09369 | 0.17994 | 0.04156 | -0.083477 | 0.02992 | 0.046108 | -0.042645 | 0.001404 | 0.06377 | 0.13633 | 0.01164 | 0.084205
2637.7344 | 122.8134 | -122.5113 | 0.07782 | 0.076067 | -0.077151 | 0.020051 | -0.047909 | 0.077466 | 0.048956 | -0.058139 | 0.066223 | 0.16164 | 0.009515 | -0.11552 | 0.002454 | 0.027798 | -0.070112 | -0.012328 | 122.5874 | 122.4341 | 122.5313 | 122.4634 | 122.5888 | 122.5602 | 122.4532 | 0.089111 | 0.18452 | 0.032403 | -0.092635 | 0.025342 | 0.050686 | -0.047224 | 0.01056 | 0.063769 | 0.13633 | 0.007061 | 0.079627
2639.4375 | 122.7264 | -122.5571 | 0.10986 | 0.080646 | -0.072572 | 0.020051 | -0.043331 | 0.082044 | 0.048956 | -0.048983 | 0.061645 | 0.16164 | 0.018672 | -0.11094 | 0.002454 | 0.027798 | -0.065533 | -0.021484 | 122.6377 | 122.4845 | 122.5771 | 122.5137 | 122.6391 | 122.606 | 122.5081 | 0.084533 | 0.18452 | 0.04156 | -0.088056 | 0.025342 | 0.050686 | -0.042645 | 0.001404 | 0.059191 | 0.12718 | 0.016218 | 0.084205
2641.1875 | 122.7356 | -122.5616 | 0.10071 | 0.080646 | -0.067994 | 0.020051 | -0.043331 | 0.06831 | 0.053534 | -0.053561 | 0.070802 | 0.16164 | 0.009515 | -0.10637 | 0.007032 | 0.02322 | -0.065533 | -0.016906 | 122.6423 | 122.4937 | 122.5817 | 122.5183 | 122.63 | 122.6152 | 122.5081 | 0.09369 | 0.18452 | 0.032403 | -0.083477 | 0.02992 | 0.046108 | -0.042645 | 0.005982 | 0.06377 | 0.13633 | 0.002483 | 0.075048

## Thermal Data
Fire Time | C Position - 3' | C Position - Middle | C Position - 7'
-0.8083 | 9.1041 | 9.1797 | 9.1345
0.1917 | 9.1057 | 9.1782 | 9.1394
1.1917 | 9.0992 | 9.1836 | 9.1348
2.1917 | 9.1049 | 9.1859 | 9.1431
3.1917 | 9.1051 | 9.1787 | 9.1479
4.1917 | 9.0809 | 9.1655 | 9.1882
5.1917 | 9.0971 | 9.1872 | 9.277
6.1917 | 9.1047 | 9.2016 | 9.7826
7.1917 | 10.0085 | 9.5987 | 10.1161
8.1917 | 10.6903 | 9.9322 | 10.9364
9.1917 | 11.1362 | 10.4184 | 11.8121
10.1917 | 11.4676 | 11.342 | 12.8942
11.2073 | 12.4519 | 12.9113 | 14.5834
12.1917 | 13.4728 | 14.2872 | 16.533
13.1917 | 15.0632 | 15.3776 | 18.8573
14.1917 | 15.8203 | 16.6776 | 20.0203
15.1917 | 17.8925 | 18.6454 | 20.9293
16.1917 | 19.5701 | 20.3276 | 22.246
17.1917 | 20.7985 | 22.1625 | 24.7091
18.1917 | 22.1233 | 24.1711 | 26.5523
19.1917 | 23.7228 | 26.4815 | 28.5129
20.1917 | 25.2968 | 28.3033 | 30.9255
21.1917 | 27.5634 | 30.8978 | 33.4243
22.1917 | 29.903 | 33.2668 | 35.9528
23.1917 | 31.8795 | 34.6008 | 37.8216
24.1917 | 34.6633 | 36.8837 | 40.1222
25.1917 | 36.8535 | 38.5872 | 41.7425
26.1917 | 40.1326 | 40.4198 | 44.0379
27.1917 | 42.1069 | 42.1477 | 45.5421
28.1917 | 44.0046 | 45.1385 | 47.5677
29.1917 | 45.4518 | 47.1249 | 49.7929
30.1917 | 47.4955 | 48.8315 | 51.2283
31.1917 | 49.086 | 50.3981 | 52.5002
32.1917 | 50.7206 | 52.0429 | 53.6675
33.1917 | 52.3967 | 54.1691 | 55.2052
34.1917 | 54.9392 | 55.5955 | 57.1914
35.1917 | 57.279 | 57.017 | 58.7531
36.1917 | 60.6464 | 59.3424 | 60.375
37.1917 | 63.0319 | 61.888 | 62.6927
38.1917 | 64.9725 | 64.9185 | 64.721
39.1917 | 66.2995 | 67.5163 | 66.5075
40.1917 | 68.0951 | 69.307 | 67.7919
41.2073 | 70.0017 | 71.857 | 70.4474
42.1917 | 72.1248 | 74.1919 | 72.5339
43.1917 | 73.8439 | 75.6278 | 75.0262
44.1917 | 75.1347 | 77.3573 | 77.3099
45.1917 | 76.5325 | 78.8756 | 78.5696
46.1917 | 77.8404 | 80.7603 | 80.3353
47.1917 | 79.164 | 82.4352 | 82.171
48.1917 | 81.0114 | 83.2457 | 83.0795
49.1917 | 83.0081 | 85.0968 | 83.9865
50.1917 | 84.1443 | 85.7923 | 85.2869
51.1917 | 85.2462 | 86.511 | 86.1254
52.1917 | 87.4825 | 87.5548 | 88.0551
53.1917 | 88.054 | 88.919 | 89.5723
54.1917 | 89.6326 | 90.456 | 91.049
55.1917 | 91.5272 | 92.4045 | 92.6336
56.1917 | 92.2613 | 93.4255 | 93.4388
57.1917 | 93.1468 | 94.3916 | 94.6128
58.1917 | 93.8631 | 95.1219 | 95.7947
59.1917 | 95.2549 | 96.4819 | 97.0921
60.1917 | 96.443 | 97.5451 | 97.5841
61.1917 | 98.539 | 98.491 | 97.8425
62.1917 | 99.71 | 99.2606 | 98.3022
63.1917 | 101.3699 | 99.8115 | 99.1872
64.1917 | 102.5575 | 100.5105 | 99.9779
65.1917 | 103.2518 | 101.6196 | 100.3416
66.1917 | 104.5726 | 102.4789 | 101.0604
67.1917 | 105.2028 | 103.2805 | 101.7686
68.1917 | 105.4112 | 103.8054 | 102.0299
69.2073 | 105.8021 | 104.1865 | 102.8652
70.1917 | 106.7905 | 104.9276 | 103.5109
71.1917 | 106.7186 | 105.3134 | 103.7591
72.1917 | 106.9998 | 105.8259 | 103.9871
73.1917 | 107.3726 | 106.4613 | 104.9135
74.1917 | 107.9043 | 107.5312 | 105.4042
75.1917 | 108.6675 | 108.1296 | 106.1407
76.1917 | 109.5886 | 108.8537 | 106.2826
77.1917 | 110.2577 | 109.6759 | 106.5024
78.1917 | 110.6179 | 110.4754 | 107.778
79.1917 | 111.2968 | 111.2083 | 108.5232
80.1917 | 112.4539 | 111.776 | 109.296
81.1917 | 113.7098 | 112.3639 | 109.9656
82.1917 | 114.8222 | 113.2509 | 110.724
83.1917 | 115.4034 | 113.8544 | 110.9971
84.1917 | 115.796 | 114.8517 | 112.8024
85.1917 | 116.5992 | 115.3041 | 112.8388
86.1917 | 116.8414 | 115.8792 | 113.1494
87.1917 | 117.3396 | 116.4812 | 113.5569
88.1917 | 117.7398 | 117.0324 | 113.9862
89.1917 | 118.1676 | 117.7431 | 114.4327
90.1917 | 118.5215 | 118.3646 | 114.8856
91.1917 | 120.0112 | 119.7889 | 115.3062
92.1917 | 120.153 | 120.288 | 115.852
93.2073 | 120.3067 | 120.5547 | 116.5127
94.1917 | 121.1174 | 120.879 | 117.0557
95.1917 | 121.2428 | 120.9927 | 117.4678
96.1917 | 121.3934 | 121.2008 | 117.4545
97.2073 | 121.3196 | 121.3374 | 117.673
98.1917 | 121.5671 | 121.7379 | 117.6546
99.2073 | 121.9231 | 122.4767 | 118.5064
100.1917 | 121.9028 | 122.7692 | 118.8017
101.1917 | 121.9016 | 123.046 | 118.8884
102.1917 | 122.7291 | 123.1765 | 119.0667
103.1917 | 122.5894 | 123.254 | 119.2791
104.1917 | 122.6342 | 123.643 | 119.5298
105.1917 | 123.1383 | 123.6913 | 119.8116
106.1917 | 123.1501 | 123.7485 | 120.1361
107.1917 | 123.4648 | 124.0026 | 120.5746
108.1917 | 124.1954 | 124.2188 | 120.9147
109.1917 | 124.3362 | 124.5061 | 120.9891
110.1917 | 124.4112 | 124.8482 | 121.2427
111.1917 | 124.3099 | 124.9345 | 121.6497
112.1917 | 124.1215 | 125.3448 | 121.6759
113.1917 | 124.4892 | 125.4977 | 122.4712
114.1917 | 124.3829 | 125.897 | 122.9365
115.1917 | 125.094 | 126.0263 | 123.1943
116.1917 | 125.9418 | 126.6032 | 123.5586
117.1917 | 126.5307 | 127.0963 | 124.0187
118.1917 | 126.8842 | 127.7387 | 124.5472
119.1917 | 127.3261 | 127.9668 | 124.5798
120.1917 | 127.7908 | 128.8341 | 125.3292
121.1917 | 128.7284 | 128.8735 | 125.5731
122.1917 | 129.2187 | 129.4983 | 126.2632
123.1917 | 129.1856 | 129.7525 | 126.1557
124.1917 | 129.2359 | 129.9875 | 126.2115
125.1917 | 129.4749 | 130.0774 | 126.2127
126.1917 | 129.6194 | 130.129 | 125.8774
127.1917 | 129.6852 | 130.2136 | 125.87
128.1917 | 129.6731 | 130.2545 | 125.8326
129.1917 | 129.6499 | 131.279 | 126.3662
130.1917 | 129.7962 | 131.3034 | 125.923
131.1917 | 129.8523 | 131.8732 | 126.2237
132.1917 | 130.0923 | 132.1032 | 126.2026
133.1917 | 130.2762 | 132.505 | 126.0916
134.1917 | 130.4695 | 132.6442 | 126.3763
135.1917 | 130.5003 | 132.9983 | 126.3266
136.1917 | 131.1155 | 132.762 | 126.2198
137.1917 | 132.6345 | 132.6387 | 126.0111
138.1917 | 132.4566 | 132.6641 | 126.2503
139.1917 | 132.5529 | 132.6665 | 126.1142
140.1917 | 132.531 | 132.8441 | 126.3749
141.1917 | 132.785 | 133.4266 | 126.1346
142.1917 | 133.3077 | 133.8482 | 125.7878
143.1917 | 133.8126 | 134.1467 | 125.5014
144.1917 | 133.8734 | 134.2439 | 125.7074
145.1917 | 133.8124 | 134.3303 | 125.5419
146.1917 | 133.8023 | 134.2653 | 125.4636
147.1917 | 133.5575 | 134.4157 | 125.5716
148.1917 | 133.5455 | 134.4537 | 125.5032
149.1917 | 134.2202 | 134.4223 | 125.5822
150.1917 | 134.1469 | 134.2752 | 125.5944
151.1917 | 134.4012 | 134.1298 | 125.6981
152.1917 | 134.1395 | 134.0983 | 125.6528
153.1917 | 133.8383 | 134.1554 | 125.8961
154.1917 | 134.0646 | 134.0288 | 126.1667
155.1917 | 134.1014 | 133.8541 | 126.0775
156.1917 | 134.9228 | 134.166 | 126.1259
157.1917 | 135.0791 | 134.2663 | 126.2269
158.1917 | 135.4777 | 134.1683 | 126.3271
159.1917 | 135.7102 | 134.1772 | 126.4008
160.1917 | 135.9198 | 134.2008 | 126.6815
161.1917 | 135.9064 | 134.5683 | 127.8282
162.2073 | 135.5973 | 134.5605 | 127.252
163.1917 | 135.3261 | 135.3935 | 127.0843
164.1917 | 135.1758 | 135.2347 | 127.6729
165.1917 | 135.1058 | 135.1612 | 127.5111
166.1917 | 135.143 | 135.1123 | 128.0416
167.1917 | 135.8703 | 135.4949 | 127.9272
168.1917 | 136.1347 | 135.7797 | 128.9935
169.1917 | 136.5748 | 136.4773 | 129.3309
170.1917 | 136.9203 | 137.1386 | 129.5229
171.1917 | 136.9822 | 137.1593 | 130.8624
172.1917 | 137.1067 | 137.1905 | 130.8602
173.1917 | 137.0438 | 137.3708 | 131.2793
174.1917 | 137.1755 | 137.6829 | 130.7075
175.1917 | 137.4816 | 137.6668 | 130.3226
176.1917 | 137.5281 | 137.8367 | 130.3548
177.1917 | 137.5365 | 137.6901 | 130.297
178.1917 | 137.414 | 137.8074 | 130.4364
179.1917 | 137.5208 | 138.0647 | 130.6347
180.1917 | 137.4878 | 138.1373 | 130.7661
181.1917 | 137.7036 | 137.9321 | 130.8722
182.1917 | 137.5565 | 137.8736 | 130.9347
183.1917 | 137.4559 | 137.5907 | 130.8054
184.1917 | 137.8732 | 137.5962 | 131.0335
185.1917 | 137.8365 | 137.8118 | 131.1556
186.1917 | 137.6953 | 138.9068 | 131.1452
187.1917 | 137.6848 | 138.8701 | 131.136
188.1917 | 137.8388 | 139.1803 | 131.3645
189.1917 | 138.0352 | 139.586 | 131.0719
190.1917 | 138.4713 | 139.6917 | 131.6529
191.1917 | 139.0709 | 139.8076 | 131.5605
192.1917 | 139.4265 | 140.001 | 131.5289
193.1917 | 139.1511 | 139.9643 | 131.7538
194.1917 | 139.1884 | 140.0532 | 132.1128
195.1917 | 139.5038 | 140.0927 | 132.3717
196.1917 | 139.5316 | 140.0946 | 132.5488
197.1917 | 140.3354 | 140.3126 | 132.5393
198.1917 | 140.9523 | 140.8718 | 133.0414
199.1917 | 141.5689 | 141.4855 | 133.1016
200.1917 | 141.9817 | 142.0318 | 133.4067
201.1917 | 142.3147 | 141.9238 | 133.7231
202.1917 | 142.9231 | 142.3491 | 134.1914
203.1917 | 143.1323 | 142.2879 | 133.9505
204.1917 | 143.341 | 142.6379 | 133.9404
205.1917 | 143.8884 | 142.91 | 134.0327
206.1917 | 144.234 | 143.2622 | 134.1253
207.1917 | 144.6713 | 143.7138 | 134.0001
208.1917 | 145.2086 | 143.9256 | 134.0202
209.1917 | 145.8675 | 144.2188 | 134.1386
210.1917 | 145.9092 | 144.4181 | 134.0891
211.1917 | 146.5685 | 144.6888 | 134.4014
212.1917 | 147.2868 | 145.2104 | 134.9256
213.1917 | 147.6663 | 145.4088 | 135.1597
214.1917 | 148.78 | 145.7011 | 135.2658
215.1917 | 149.2503 | 146.1949 | 135.8641
216.1917 | 149.5674 | 146.4195 | 135.9165
217.1917 | 149.7944 | 146.5687 | 136.3194
218.1917 | 150.2934 | 147.3066 | 136.8701
219.1917 | 150.8416 | 147.5602 | 137.8788
220.1917 | 151.9177 | 148.3171 | 138.2697
221.1917 | 152.5126 | 149.2015 | 138.3023
222.1917 | 152.1622 | 149.5988 | 139.0553
223.1917 | 151.9358 | 150.5814 | 139.7138
224.1917 | 152.3029 | 150.5574 | 141.0303
225.1917 | 152.7446 | 150.8085 | 141.1797
226.1917 | 153.0391 | 151.0165 | 141.7445
227.1917 | 152.9696 | 151.1054 | 141.9382
228.1917 | 152.7787 | 150.949 | 142.6972
229.1917 | 153.1777 | 151.2793 | 142.7578
230.1917 | 152.91 | 151.2553 | 143.4199
231.1917 | 153.6112 | 151.3021 | 143.5959
232.1917 | 153.257 | 151.1237 | 143.3669
233.1917 | 154.0081 | 151.3373 | 143.2139
234.1917 | 153.7208 | 151.3222 | 143.299
235.1917 | 153.6358 | 151.3387 | 143.0647
236.1917 | 153.8116 | 151.2993 | 143.0143
237.1917 | 153.9543 | 151.4729 | 142.7963
238.1917 | 154.0437 | 151.5062 | 142.5154
239.1917 | 153.9535 | 151.1841 | 142.133
240.1917 | 153.7686 | 151.5314 | 142.1736
241.1917 | 154.077 | 151.335 | 142.3795
242.1917 | 154.0384 | 151.3744 | 142.4247
243.1917 | 154.0061 | 151.9995 | 142.9358
244.1917 | 153.9042 | 151.8083 | 142.6408
245.1917 | 154.0066 | 151.579 | 142.7685
246.1917 | 155.5502 | 151.8471 | 143.3291
247.1917 | 156.0381 | 151.8642 | 143.143
248.1917 | 156.9576 | 152.4606 | 143.3472
249.1917 | 156.9747 | 153.2818 | 143.5251
250.1917 | 157.0372 | 153.5092 | 143.458
251.1917 | 157.0033 | 153.7375 | 143.3032
252.1917 | 157.0839 | 153.5979 | 143.0971
253.1917 | 158.1704 | 153.493 | 143.6783
254.1917 | 158.4953 | 153.3734 | 143.8509
255.1917 | 158.18 | 153.4193 | 143.7337
256.1917 | 158.0748 | 153.748 | 143.7298
257.1917 | 158.0188 | 154.2036 | 143.7721
258.1917 | 158.7387 | 154.7446 | 143.8889
259.1917 | 159.1433 | 155.2862 | 143.9021
260.1917 | 158.8595 | 155.8318 | 143.9729
261.1917 | 158.7464 | 156.3549 | 144.1765
262.1917 | 159.1615 | 156.585 | 144.98
263.1917 | 159.4915 | 156.9926 | 144.975
264.1917 | 160.2041 | 157.4371 | 145.0952
265.1917 | 160.2281 | 157.4497 | 145.5814
266.1917 | 160.5014 | 158.1322 | 145.7372
267.1917 | 161.4103 | 157.9794 | 146.2822
268.1917 | 161.3067 | 158.1197 | 146.1653
269.1917 | 161.4131 | 158.2812 | 146.5802
270.1917 | 161.3868 | 158.7106 | 147.0851
271.1917 | 162.1404 | 159.3481 | 148.5576
272.1917 | 162.7278 | 159.6512 | 148.4437
273.1917 | 162.8401 | 159.8138 | 148.4084
274.1917 | 163.1795 | 159.8675 | 148.5216
275.1917 | 163.0093 | 159.8142 | 148.6193
276.1917 | 163.049 | 159.8078 | 148.9633
277.1917 | 163.4621 | 159.7665 | 148.8829
278.1917 | 163.3296 | 160.2397 | 149.0141
279.1917 | 163.1943 | 160.1091 | 148.9354
280.1917 | 163.1743 | 160.451 | 149.3533
281.1917 | 163.2871 | 160.5111 | 149.3912
282.1917 | 163.5578 | 161.0774 | 150.1795
283.1917 | 164.0699 | 161.2467 | 150.0136
284.1917 | 163.8859 | 161.3121 | 150.6744
285.1917 | 164.0087 | 161.6303 | 150.9362
286.1917 | 164.1982 | 161.5786 | 151.6599
287.1917 | 164.5165 | 161.5636 | 151.8488
288.1917 | 164.5664 | 161.3383 | 151.9424
289.1917 | 164.9712 | 161.5585 | 151.7194
290.1917 | 165.1193 | 162.3461 | 151.7517
291.1917 | 164.891 | 162.7809 | 151.8025
292.1917 | 165.6761 | 162.7665 | 152.1376
293.1917 | 165.4467 | 162.5249 | 151.8291
294.1917 | 165.3517 | 162.3818 | 151.5407
295.1917 | 165.8731 | 162.6623 | 151.2961
296.1917 | 166.0388 | 162.4331 | 151.0602
297.1917 | 166.1769 | 162.9013 | 151.4901
298.1917 | 166.3685 | 163.0156 | 151.9623
299.1917 | 166.3499 | 163.0519 | 152.3293
300.1917 | 166.8206 | 163.3163 | 152.2572
301.1917 | 167.1112 | 163.1629 | 152.0185
302.1917 | 167.3635 | 163.4385 | 152.9215
303.1917 | 167.2384 | 163.6296 | 153.0443
304.1917 | 167.2361 | 163.4124 | 152.7479
305.2073 | 167.2555 | 163.1041 | 152.8645
306.1917 | 167.4501 | 163.039 | 152.7379
307.1917 | 167.0109 | 162.9019 | 152.779
308.1917 | 166.7749 | 162.8394 | 152.8288
309.1917 | 166.2767 | 162.7173 | 153.2837
310.1917 | 165.7867 | 162.2693 | 153.0069
311.2073 | 165.3594 | 161.9596 | 153.1798
312.1917 | 165.0916 | 161.5634 | 153.1104
313.1917 | 165.064 | 161.307 | 153.6021
314.1917 | 164.7367 | 161.4644 | 153.2671
315.1917 | 165.1901 | 162.2415 | 153.4481
316.1917 | 165.2362 | 161.9499 | 153.6116
317.1917 | 165.2249 | 161.9765 | 154.3797
318.1917 | 165.4222 | 161.8208 | 154.7849
319.1917 | 165.5463 | 161.8775 | 154.9437
320.1917 | 165.4276 | 162.0044 | 154.9457
321.1917 | 165.0109 | 161.9452 | 154.9797
322.1917 | 164.6268 | 162.3746 | 155.4789
323.1917 | 164.5631 | 162.1404 | 155.505
324.1917 | 164.8502 | 162.1889 | 155.3595
325.1917 | 164.6426 | 161.9641 | 155.2596
326.1917 | 164.43 | 161.7531 | 155.2798
327.1917 | 164.4034 | 161.8331 | 155.0005
328.1917 | 164.2073 | 161.4376 | 154.6568
329.1917 | 164.2396 | 161.0402 | 154.3245
330.1917 | 163.908 | 160.6597 | 154.1348
331.1917 | 163.6687 | 160.3433 | 154.192
332.1917 | 163.4339 | 160.1422 | 154.7013
333.1917 | 163.0453 | 159.8747 | 154.6321
334.1917 | 163.2251 | 159.7882 | 154.8842
335.1917 | 163.2393 | 160.6892 | 156.1175
336.1917 | 162.8903 | 160.3328 | 156.2455
337.1917 | 163.1003 | 159.7524 | 157.2008
338.1917 | 163.0104 | 159.5918 | 157.4548
339.1917 | 163.1086 | 159.5759 | 157.1666
340.1917 | 163.0905 | 159.2376 | 157.2749
341.1917 | 162.9817 | 158.8632 | 157.1421
342.1917 | 162.8048 | 159.3271 | 158.1823
343.1917 | 163.0957 | 159.2587 | 158.3679
344.1917 | 163.6041 | 159.2895 | 158.4878
345.1917 | 164.1422 | 159.866 | 158.6943
346.1917 | 163.9798 | 160.2452 | 158.9362
347.1917 | 164.0534 | 160.6342 | 158.538
348.1917 | 164.0943 | 161.3376 | 158.8979
349.1917 | 164.1317 | 161.771 | 158.7159
350.1917 | 164.2564 | 161.7779 | 158.3074
351.1917 | 164.8167 | 161.7536 | 158.1482
352.1917 | 165.1988 | 161.6364 | 157.9311
353.1917 | 165.297 | 161.5026 | 157.7049
354.1917 | 165.0933 | 161.6074 | 157.5304
355.1917 | 164.9873 | 161.7822 | 157.4926
356.1917 | 165.235 | 161.7589 | 157.3905
357.1917 | 165.2348 | 161.6303 | 157.2609
358.1917 | 165.1282 | 161.6511 | 157.1786
359.1917 | 165.6211 | 161.8201 | 156.8595
360.1917 | 165.4378 | 162.02 | 156.9334
361.1917 | 165.6917 | 161.8863 | 157.8672
362.1917 | 165.4203 | 162.1881 | 157.6701
363.1917 | 165.6078 | 161.9374 | 157.4424
364.1917 | 165.3347 | 161.9494 | 157.437
365.1917 | 165.3366 | 161.8523 | 157.1859
366.1917 | 165.658 | 162.6936 | 157.4112
367.1917 | 166.1168 | 163.1027 | 157.729
368.1917 | 166.2466 | 163.0386 | 157.7577
369.1917 | 166.299 | 163.161 | 157.8758
370.1917 | 166.3298 | 163.3709 | 157.7315
371.1917 | 167.0792 | 163.0821 | 157.8221
372.1917 | 166.9476 | 162.8762 | 157.8581
373.1917 | 167.0196 | 162.923 | 157.4985
374.1917 | 167.0307 | 163.4435 | 157.4179
375.1917 | 167.5189 | 163.408 | 157.2359
376.1917 | 167.5581 | 163.4995 | 157.1976
377.1917 | 167.7156 | 163.7901 | 157.2389
378.1917 | 167.6589 | 163.6978 | 157.2498
379.1917 | 167.7506 | 164.1347 | 157.8674
380.1917 | 167.6715 | 164.4151 | 158.1928
381.1917 | 167.5844 | 164.3904 | 157.7665
382.1917 | 167.3678 | 164.2534 | 157.3504
383.1917 | 167.0087 | 164.5221 | 157.472
384.1917 | 166.8105 | 164.5718 | 157.5328
385.1917 | 166.6533 | 164.4395 | 158.0034
386.1917 | 166.7607 | 164.3167 | 157.7461
387.1917 | 166.7651 | 164.5317 | 157.3911
388.1917 | 166.4306 | 164.2104 | 157.1968
389.1917 | 166.2839 | 164.1837 | 157.0693
390.1917 | 166.2646 | 164.0871 | 157.1091
391.1917 | 166.1518 | 163.8866 | 157.0575
392.1917 | 166.0624 | 164.0938 | 157.1778
393.1917 | 165.7562 | 164.207 | 156.9529
394.1917 | 165.5138 | 164.303 | 156.7506
395.1917 | 165.6995 | 164.2094 | 156.7296
396.1917 | 165.5195 | 164.3513 | 156.9683
397.1917 | 165.7634 | 164.6343 | 157.2198
398.1917 | 165.8368 | 164.462 | 157.5697
399.1917 | 165.7662 | 164.8335 | 158.5508
400.1917 | 165.8766 | 164.9825 | 158.4643
401.1917 | 165.8063 | 165.3262 | 158.9135
402.1917 | 166.2958 | 165.3419 | 158.8786
403.1917 | 166.422 | 165.4158 | 158.9983
404.1917 | 166.2639 | 165.7838 | 159.0806
405.1917 | 166.5964 | 165.575 | 159.2041
406.1917 | 166.8559 | 165.4786 | 159.1469
407.1917 | 166.6689 | 165.505 | 158.9905
408.1917 | 166.3327 | 165.3559 | 159.2296
409.1917 | 166.9207 | 165.2824 | 159.1579
410.1917 | 166.7977 | 165.255 | 158.9667
411.1917 | 166.6888 | 165.7571 | 159.3496
412.1917 | 166.2755 | 165.5342 | 159.509
413.1917 | 166.079 | 165.7714 | 159.7824
414.1917 | 166 | 165.7389 | 159.9076
415.1917 | 166.3479 | 165.7514 | 160.2995
416.1917 | 166.7412 | 165.6875 | 160.7029
417.1917 | 166.7033 | 166.0573 | 161.0132
418.1917 | 167.0628 | 166.3059 | 161.0805
419.1917 | 167.475 | 166.43 | 161.0179
420.1917 | 168.0642 | 166.6671 | 160.7795
421.1917 | 168.5261 | 167.0138 | 160.5477
422.1917 | 169.0469 | 167.2042 | 160.5441
423.1917 | 170.1116 | 168.1307 | 160.8557
424.1917 | 169.9126 | 167.9209 | 160.5353
425.2073 | 170.5624 | 167.9296 | 160.7782
426.1917 | 170.5584 | 167.8179 | 161.894
427.1917 | 170.6644 | 167.5678 | 161.8256
428.1917 | 170.4799 | 167.8984 | 162.0263
429.1917 | 170.0642 | 167.7988 | 162.0156
430.1917 | 170.2622 | 168.1873 | 161.8923
431.1917 | 170.6735 | 168.2731 | 162.2089
432.1917 | 171.2043 | 168.4377 | 162.0776
433.1917 | 171.2832 | 168.7608 | 161.9805
434.1917 | 171.7051 | 168.8778 | 161.9297
435.1917 | 172.0738 | 168.7497 | 161.9128
436.1917 | 172.1464 | 169.0685 | 162.1462
437.1917 | 172.6037 | 169.1854 | 162.421
438.1917 | 172.5062 | 169.5405 | 162.6507
439.1917 | 172.3562 | 169.4988 | 162.6307
440.1917 | 172.6139 | 169.5828 | 162.7757
441.1917 | 172.6366 | 170.4097 | 163.0919
442.1917 | 172.2945 | 170.1312 | 163.4276
443.1917 | 172.4598 | 169.9877 | 163.4892
444.1917 | 173.1575 | 170.3383 | 163.8995
445.1917 | 172.8798 | 170.1938 | 163.6289
446.1917 | 173.0063 | 170.1649 | 163.6033
447.1917 | 173.3685 | 170.2445 | 163.4292
448.1917 | 174.0319 | 170.1611 | 163.155
449.1917 | 174.4488 | 170.6582 | 163.1942
450.1917 | 174.5763 | 170.737 | 163.3428
451.1917 | 174.7759 | 170.622 | 163.3289
452.1917 | 174.7402 | 170.8037 | 163.3568
453.1917 | 175.0529 | 170.7242 | 163.0388
454.1917 | 175.124 | 170.6601 | 162.9122
455.1917 | 175.2757 | 171.0071 | 163.0395
456.1917 | 175.07 | 171.1182 | 163.1099
457.1917 | 175.3315 | 171.3747 | 163.2474
458.1917 | 175.5665 | 171.7208 | 163.1988
459.1917 | 176.6485 | 171.9781 | 162.8135
460.1917 | 176.9639 | 172.0745 | 162.6729
461.1917 | 176.7611 | 172.0677 | 162.6735
462.1917 | 176.964 | 172.2222 | 163.1175
463.1917 | 177.4494 | 172.3584 | 163.2384
464.1917 | 177.396 | 172.0461 | 163.2341
465.1917 | 177.9788 | 171.9796 | 163.4331
466.1917 | 177.7758 | 172.0586 | 163.4032
467.1917 | 177.4357 | 172.5318 | 163.4258
468.1917 | 177.3776 | 173.198 | 164.0104
469.1917 | 177.7196 | 173.962 | 164.0817
470.1917 | 177.8504 | 174.2058 | 164.2203
471.1917 | 178.6753 | 174.529 | 164.2612
472.1917 | 178.7226 | 174.4116 | 164.0268
473.1917 | 179.0718 | 174.4033 | 163.7794
474.1917 | 179.0764 | 174.5698 | 164.1692
475.1917 | 178.9972 | 174.5003 | 164.1195
476.1917 | 179.0897 | 174.3467 | 164.4438
477.1917 | 178.9849 | 174.8772 | 164.659
478.1917 | 179.076 | 174.8828 | 165.0281
479.1917 | 179.1609 | 174.6703 | 164.7907
480.1917 | 179.3061 | 174.4182 | 164.7891
481.1917 | 179.152 | 174.2905 | 164.7889
482.1917 | 179.5069 | 174.7341 | 165.3527
483.1917 | 179.1477 | 174.4264 | 164.8772
484.1917 | 178.8038 | 174.1904 | 165.1723
485.1917 | 178.1656 | 174.2517 | 165.3252
486.1917 | 177.8287 | 174.2434 | 165.2733
487.1917 | 177.6189 | 174.2842 | 165.4259
488.1917 | 177.4351 | 174.0748 | 165.3742
489.1917 | 178.3685 | 174.0767 | 165.3178
490.1917 | 178.3119 | 173.9059 | 165.4537
491.1917 | 178.2219 | 173.9648 | 165.3951
492.1917 | 178.6923 | 174.2328 | 165.8596
493.1917 | 178.7944 | 174.9408 | 166.1619
494.1917 | 179.6358 | 175.4277 | 166.5267
495.1917 | 179.9126 | 175.8076 | 167.1499
496.1917 | 180.5744 | 176.0228 | 167.7954
497.1917 | 181.0345 | 176.5155 | 167.7809
498.1917 | 181.5021 | 176.6323 | 168.3116
499.1917 | 181.5218 | 177.4401 | 170.1186
500.1917 | 182.0981 | 177.4295 | 170.0699
501.1917 | 182.0582 | 177.6314 | 170.0864
502.1917 | 182.0703 | 177.7307 | 170.6044
503.1917 | 181.8836 | 177.8615 | 170.3727
504.1917 | 182.3636 | 177.968 | 170.6407
505.1917 | 182.9788 | 178.0298 | 170.1612
506.1917 | 183.1678 | 178.091 | 170.3048
507.1917 | 183.1039 | 178.0999 | 170.4052
508.1917 | 182.781 | 178.1203 | 171.363
509.1917 | 182.9493 | 178.645 | 171.8443
510.1917 | 182.9774 | 178.8547 | 171.8824
511.1917 | 183.5788 | 178.8984 | 172.4264
512.1917 | 184.0945 | 179.3854 | 172.7461
513.1917 | 184.7789 | 179.6429 | 172.9183
514.1917 | 185.1389 | 179.8806 | 172.6994
515.1917 | 185.6016 | 180.3216 | 173.2499
516.1917 | 185.123 | 179.9738 | 173.0634
517.1917 | 184.8845 | 179.8764 | 173.3645
518.1917 | 184.9141 | 180.1664 | 172.9763
519.1917 | 184.8735 | 180.6747 | 172.865
520.1917 | 185.0645 | 180.9681 | 173.1763
521.1917 | 185.5078 | 181.0361 | 173.3434
522.1917 | 186.0221 | 181.1333 | 173.2895
523.1917 | 186.4122 | 181.1387 | 173.6295
524.1917 | 186.3701 | 181.378 | 173.323
525.1917 | 185.9295 | 181.2633 | 173.1477
526.1917 | 185.8771 | 181.4647 | 173.1424
527.1917 | 185.8055 | 181.302 | 172.8799
528.1917 | 185.9955 | 181.0673 | 172.8672
529.1917 | 185.848 | 180.849 | 173.1049
530.1917 | 186.0537 | 181.0674 | 173.2944
531.1917 | 186.759 | 181.3262 | 173.5653
532.1917 | 186.4527 | 181.578 | 174.304
533.1917 | 186.735 | 181.8088 | 174.0747
534.1917 | 186.5843 | 181.9129 | 175.0603
535.1917 | 186.4763 | 182.1161 | 175.5022
536.1917 | 186.123 | 181.9322 | 175.4546
537.1917 | 186.1192 | 181.7589 | 175.2478
538.1917 | 186.5282 | 181.8835 | 175.0897
539.1917 | 186.3741 | 181.6438 | 174.8625
540.1917 | 186.0405 | 181.6061 | 174.7955
541.1917 | 185.7125 | 181.55 | 174.6632
542.1917 | 186.59 | 181.2505 | 174.8184
543.1917 | 186.8847 | 181.5678 | 175.536
544.1917 | 187.2239 | 181.9806 | 175.4727
545.1917 | 186.8948 | 182.3392 | 175.5363
546.1917 | 187.5151 | 182.4278 | 175.4356
547.1917 | 187.8396 | 182.6421 | 175.1664
548.1917 | 187.6823 | 182.6324 | 174.88
549.1917 | 187.6879 | 182.8115 | 175.156
550.1917 | 187.5598 | 183.2281 | 175.1213
551.1917 | 187.7761 | 183.7477 | 175.5492
552.1917 | 187.4195 | 183.5609 | 175.4753
553.1917 | 187.0115 | 183.3672 | 175.5372
554.1917 | 186.6302 | 183.8782 | 175.9858
555.1917 | 186.4864 | 183.8762 | 175.9796
556.1917 | 187.2835 | 183.7756 | 176.1369
557.1917 | 186.9898 | 183.8309 | 176.3777
558.1917 | 186.6393 | 183.8192 | 176.7353
559.1917 | 186.6947 | 183.8448 | 176.8532
560.1917 | 186.3955 | 183.7677 | 176.4777
561.1917 | 187.3417 | 184.4143 | 176.3677
562.1917 | 186.849 | 184.3943 | 176.4625
563.1917 | 186.6756 | 184.5014 | 176.429
564.1917 | 186.8273 | 184.7175 | 176.1276
565.1917 | 187.0625 | 184.6636 | 176.1611
566.1917 | 187.1881 | 185.6991 | 176.646
567.1917 | 186.911 | 185.6075 | 177.4405
568.1917 | 186.9165 | 185.7621 | 177.737
569.1917 | 186.9574 | 185.4278 | 177.3981
570.1917 | 187.0641 | 185.3134 | 177.2602
571.1917 | 186.9059 | 185.0231 | 177.3705
572.1917 | 187.0315 | 184.8679 | 177.0971
573.1917 | 187.2791 | 184.7524 | 177.0382
574.1917 | 187.7455 | 184.4227 | 176.8451
575.1917 | 187.5454 | 184.2587 | 177.1127
576.1917 | 187.4903 | 184.2485 | 177.145
577.1917 | 187.0894 | 184.0386 | 176.7136
578.1917 | 187.2431 | 184.0333 | 176.3794
579.1917 | 188.6198 | 184.2023 | 175.9825
580.1917 | 189.4971 | 184.1749 | 176.035
581.1917 | 189.5723 | 184.137 | 176.0742
582.1917 | 190.0704 | 183.9697 | 176.0759
583.1917 | 190.3067 | 183.8974 | 175.862
584.1917 | 190.6464 | 184.4757 | 177.098
585.1917 | 190.8489 | 184.3894 | 178.3136
586.1917 | 191.1852 | 184.7808 | 178.8008
587.1917 | 191.2377 | 184.9593 | 178.7012
588.1917 | 191.1335 | 184.919 | 178.6899
589.1917 | 191.3062 | 185.5982 | 178.4702
590.1917 | 191.4615 | 185.9955 | 178.4978
591.1917 | 191.1187 | 186.6025 | 178.5458
592.1917 | 191.722 | 186.6028 | 178.338
593.1917 | 191.9656 | 186.2215 | 178.8356
594.1917 | 191.7091 | 186.0705 | 178.6262
595.1917 | 191.7726 | 185.8321 | 178.2313
596.1917 | 191.5834 | 185.6558 | 178.299
597.1917 | 191.448 | 185.8923 | 178.5595
598.1917 | 191.2633 | 186.1566 | 178.9528
599.1917 | 191.4897 | 186.2498 | 179.3797
600.1917 | 191.9931 | 186.5738 | 180.0792
601.1917 | 191.749 | 186.551 | 180.3242
602.1917 | 191.3258 | 186.6967 | 179.7456
603.1917 | 191.1173 | 186.646 | 179.6956
604.1917 | 191.1611 | 186.5485 | 179.1382
605.1917 | 190.8087 | 186.1298 | 178.889
606.1917 | 190.4924 | 185.9207 | 179.0171
607.1917 | 190.5345 | 185.9569 | 179.0034
608.1917 | 191.0772 | 186.2458 | 178.9522
609.1917 | 190.9633 | 186.8522 | 179.2022
610.1917 | 191.7529 | 186.9814 | 179.999
611.1917 | 191.3716 | 187.0435 | 180.7254
612.1917 | 191.07 | 187.2871 | 180.7167
613.1917 | 191.3982 | 188.0974 | 181.3552
614.1917 | 191.1161 | 187.9101 | 182.2963
615.1917 | 191.4376 | 187.9871 | 182.3611
616.1917 | 191.4846 | 188.0604 | 182.6336
617.1917 | 190.9902 | 188.01 | 183.1798
618.1917 | 191.4025 | 187.9129 | 183.4572
619.1917 | 191.1652 | 187.954 | 183.9501
620.1917 | 191.0114 | 187.9479 | 183.5624
621.1917 | 191.3524 | 187.8086 | 183.1666
622.1917 | 192.1407 | 187.6547 | 183.4349
623.1917 | 192.5269 | 187.4394 | 183.8683
624.1917 | 193.1559 | 187.3926 | 184.242
625.1917 | 193.1102 | 187.6586 | 184.6562
626.1917 | 194.2206 | 187.9726 | 184.9198
627.1917 | 194.199 | 188.091 | 184.6709
628.1917 | 194.6127 | 188.204 | 185.0906
629.1917 | 194.2898 | 188.0592 | 185.2112
630.1917 | 193.7131 | 187.8846 | 185.3424
631.1917 | 194.5159 | 187.8742 | 185.3322
632.1917 | 193.9106 | 187.9907 | 185.1243
633.1917 | 193.3196 | 188.2248 | 184.8916
634.1917 | 193.1731 | 188.4099 | 185.1262
635.1917 | 193.0511 | 188.334 | 185.0117
636.1917 | 192.8726 | 188.2911 | 184.6161
637.1917 | 192.7744 | 188.1917 | 184.6818
638.1917 | 193.097 | 188.6462 | 185.2079
639.1917 | 192.9524 | 189.3074 | 186.1311
640.1917 | 193.4791 | 189.4617 | 186.1246
641.1917 | 193.6358 | 189.3544 | 186.8121
642.1917 | 193.8483 | 189.2826 | 186.8494
643.1917 | 193.5289 | 189.6251 | 187.0054
644.1917 | 193.5381 | 189.5494 | 187.3454
645.1917 | 193.6384 | 190.0955 | 187.6001
646.1917 | 193.2277 | 190.0119 | 188.3611
647.1917 | 193.4951 | 190.3226 | 188.2459
648.1917 | 193.0776 | 190.0677 | 188.2976
649.1917 | 192.705 | 189.7583 | 187.7647
650.1917 | 192.3575 | 189.4916 | 187.7509
651.1917 | 192.3403 | 189.5808 | 187.8399
652.1917 | 192.5982 | 189.3571 | 188.3023
653.1917 | 193.2684 | 189.252 | 187.9925
654.1917 | 193.4995 | 189.4091 | 188.4407
655.1917 | 193.6095 | 189.3802 | 188.2517
656.1917 | 193.3559 | 189.8906 | 188.3396
657.1917 | 193.0124 | 189.7901 | 189.019
658.1917 | 192.5096 | 189.6509 | 188.6846
659.1917 | 192.2845 | 189.918 | 188.3804
660.1917 | 192.2741 | 190.0942 | 188.1229
661.1917 | 192.0971 | 189.9441 | 187.834
662.1917 | 191.8609 | 189.7875 | 187.9444
663.1917 | 191.4406 | 189.9048 | 187.5433
664.1917 | 191.0921 | 189.6076 | 187.3135
665.2073 | 191.3188 | 189.4859 | 187.197
666.1917 | 191.4625 | 190.0823 | 186.859
667.1917 | 191.7448 | 189.843 | 187.2052
668.1917 | 191.9371 | 189.9954 | 187.2919
669.1917 | 191.7745 | 190.4823 | 187.2535
670.1917 | 192.05 | 190.7631 | 186.9064
671.1917 | 192.5042 | 190.8617 | 187.8522
672.1917 | 192.5961 | 191.0648 | 188.6498
673.1917 | 192.7063 | 191.1009 | 189.6432
674.1917 | 192.683 | 191.4001 | 189.8956
675.1917 | 193.6676 | 191.5146 | 190.0643
676.1917 | 193.5861 | 191.7536 | 190.6269
677.1917 | 194.2482 | 192.6623 | 191.4829
678.1917 | 194.3921 | 192.4528 | 191.103
679.1917 | 194.1011 | 192.2471 | 191.1519
680.1917 | 194.418 | 192.3496 | 191.2714
681.1917 | 194.0526 | 192.0626 | 191.0232
682.1917 | 193.8848 | 191.9967 | 190.9869
683.1917 | 193.6763 | 191.856 | 190.9872
684.1917 | 194.053 | 191.7475 | 190.9656
685.1917 | 193.6743 | 191.722 | 190.9475
686.1917 | 193.5058 | 192.3129 | 190.4636
687.2073 | 194.3014 | 192.2398 | 190.1986
688.1917 | 195.0019 | 193.4615 | 190.0728
689.1917 | 195.1667 | 193.7102 | 189.8292
690.1917 | 195.2008 | 193.7078 | 190.1383
691.2073 | 195.1171 | 193.9549 | 190.7655
692.1917 | 195.8911 | 193.9602 | 191.3071
693.1917 | 196.2924 | 194.0875 | 191.0132
694.1917 | 196.5816 | 194.2653 | 191.0874
695.1917 | 196.8704 | 194.8614 | 191.701
696.1917 | 198.0673 | 195.7536 | 192.2815
697.2073 | 198.4384 | 197.2563 | 192.9034
698.1917 | 199.2823 | 198.2357 | 193.6026
699.1917 | 200.6728 | 198.8406 | 194.6748
700.1917 | 201.6409 | 198.7586 | 195.1771
701.1917 | 202.0142 | 199.4394 | 194.8584
702.1917 | 202.3279 | 200.6102 | 195.3437
703.2073 | 202.6637 | 200.0317 | 195.3035
704.1917 | 202.2773 | 199.8482 | 195.2564
705.1917 | 201.7335 | 199.5798 | 195.0775
706.1917 | 202.0429 | 199.5385 | 194.9753
707.2073 | 202.3151 | 200.2083 | 194.7357
708.1917 | 202.4571 | 199.645 | 194.4934
709.2073 | 202.073 | 199.1777 | 193.9691
710.1917 | 201.6027 | 198.7753 | 193.3892
711.2073 | 200.9716 | 198.2639 | 193.768
712.1917 | 200.2727 | 198.6031 | 193.7251
713.1917 | 200.3308 | 198.0106 | 193.0338
714.1917 | 199.6859 | 197.4892 | 192.685
715.1917 | 199.6465 | 197.1154 | 192.3927
716.1917 | 199.0707 | 196.5558 | 192.1872
717.1917 | 198.4892 | 196.0912 | 191.8229
718.1917 | 198.0507 | 195.6286 | 191.6707
719.1917 | 197.1772 | 195.196 | 191.0881
720.1917 | 196.5626 | 194.6756 | 190.4477
721.1917 | 196.4943 | 194.2928 | 190.3553
722.1917 | 196.1614 | 193.9893 | 189.9789
723.1917 | 196.0072 | 193.694 | 189.6696
724.1917 | 195.6053 | 193.2624 | 189.3591
725.2073 | 195.5492 | 193.0671 | 189.2767
726.1917 | 196.2036 | 193.6148 | 189.1782
727.1917 | 195.8533 | 193.3812 | 189.529
728.1917 | 196.003 | 193.6271 | 189.8799
729.1917 | 195.7684 | 194.0561 | 189.8353
730.1917 | 195.4545 | 194.7524 | 190.1717
731.1917 | 195.4793 | 195.0509 | 190.7852
732.1917 | 195.1718 | 194.7626 | 190.6186
733.1917 | 194.8409 | 194.5988 | 190.3709
734.1917 | 194.6052 | 195.0431 | 190.855
735.1917 | 194.7282 | 195.2713 | 190.9197
736.1917 | 194.6032 | 195.6075 | 190.7635
737.1917 | 194.5944 | 195.7156 | 190.8781
738.1917 | 194.5342 | 195.8067 | 190.8563
739.1917 | 194.1319 | 195.5021 | 190.8607
740.1917 | 193.9781 | 195.7255 | 191.355
741.1917 | 193.6861 | 195.7589 | 191.2817
742.1917 | 193.482 | 195.5926 | 191.0223
743.1917 | 193.609 | 195.1665 | 190.5717
744.1917 | 193.4985 | 194.6736 | 190.267
745.1917 | 193.4479 | 194.2396 | 190.1057
746.1917 | 192.9219 | 194.077 | 189.5629
747.1917 | 192.6455 | 194.2352 | 189.912
748.1917 | 192.3873 | 193.7848 | 189.8696
749.1917 | 192.3184 | 193.3119 | 189.7526
750.1917 | 192.2461 | 193.2819 | 189.7977
751.1917 | 191.9429 | 193.0959 | 189.4427
752.1917 | 191.5571 | 192.8024 | 189.2294
753.1917 | 191.8256 | 193.0035 | 189.0119
754.1917 | 192.5479 | 193.6923 | 189.6853
755.1917 | 192.3213 | 193.4513 | 189.6335
756.1917 | 193.0676 | 193.668 | 189.9185
757.1917 | 193.0908 | 193.9389 | 189.7678
758.1917 | 192.8793 | 193.9296 | 190.0619
759.1917 | 192.5288 | 193.8383 | 190.6265
760.1917 | 192.7789 | 193.8354 | 190.4906
761.1917 | 192.6098 | 193.6352 | 190.1083
762.1917 | 192.6474 | 193.8314 | 190.1833
763.1917 | 192.5885 | 193.8902 | 190.8032
764.1917 | 192.1727 | 193.899 | 190.7287
765.1917 | 192.2615 | 193.4304 | 190.6598
766.1917 | 192.0993 | 193.4126 | 190.9376
767.1917 | 192.0883 | 193.3599 | 190.8596
768.1917 | 192.1962 | 193.1833 | 190.2917
769.1917 | 191.8889 | 192.9857 | 189.8966
770.1917 | 192.1209 | 192.5759 | 189.5493
771.1917 | 192.1848 | 192.236 | 189.3559
772.1917 | 191.9504 | 192.0305 | 189.0669
773.1917 | 191.9128 | 191.7464 | 188.7728
774.1917 | 191.5897 | 191.4237 | 188.6136
775.1917 | 191.2961 | 191.1643 | 188.3363
776.1917 | 191.3076 | 190.7684 | 188.0475
777.1917 | 191.0744 | 190.3723 | 187.9642
778.1917 | 190.9663 | 190.1274 | 187.8556
779.1917 | 190.976 | 189.7428 | 187.7799
780.1917 | 191.0992 | 189.4636 | 187.5738
781.1917 | 191.3151 | 189.32 | 187.5008
782.1917 | 191.2635 | 189.1933 | 187.4691
783.1917 | 191.3347 | 189.5301 | 187.9963
784.1917 | 191.4831 | 189.7281 | 188.1542
785.1917 | 192.0029 | 190.2194 | 188.3522
786.1917 | 192.4344 | 190.5382 | 188.4074
787.1917 | 192.3502 | 190.7215 | 188.139
788.1917 | 192.9401 | 190.7657 | 188.0319
789.1917 | 193.4835 | 191.1059 | 188.4778
790.1917 | 193.2368 | 191.264 | 188.3794
791.1917 | 193.3709 | 191.4594 | 188.3383
792.1917 | 193.2392 | 191.8613 | 188.4011
793.1917 | 194.13 | 191.9909 | 188.4202
794.1917 | 194.0403 | 192.2426 | 189.406
795.1917 | 194.603 | 192.3515 | 190.0478
796.1917 | 194.3577 | 192.5854 | 190.6924
797.1917 | 194.2915 | 193.1142 | 191.2076
798.1917 | 194.3341 | 193.3558 | 191.4988
799.1917 | 194.7335 | 193.7569 | 192.7225
800.1917 | 194.7218 | 194.0568 | 193.6843
801.1917 | 195.5353 | 194.1083 | 194.17
802.1917 | 196.4482 | 194.4177 | 195.1309
803.1917 | 196.7561 | 195.7118 | 195.4477
804.1917 | 197.9449 | 196.7685 | 197.191
805.1917 | 198.4039 | 197.0499 | 197.7848
806.1917 | 199.7308 | 197.3275 | 197.9743
807.1917 | 200.0034 | 198.3389 | 198.8969
808.1917 | 201.1811 | 198.7118 | 199.5376
809.1917 | 202.573 | 199.0794 | 200.1503
810.1917 | 204.1904 | 199.6486 | 200.6092
811.1917 | 205.0689 | 200.2235 | 201.0546
812.1917 | 206.9153 | 201.4272 | 201.7148
813.1917 | 207.7871 | 201.7808 | 201.7496
814.1917 | 208.6128 | 202.0268 | 202.106
815.1917 | 208.6207 | 202.2268 | 202.8131
816.1917 | 208.2934 | 202.9393 | 202.9167
817.1917 | 208.9428 | 202.9475 | 202.6498
818.1917 | 208.8177 | 203.1125 | 202.4319
819.1917 | 208.4156 | 203.1248 | 202.6448
820.1917 | 208.5647 | 202.8975 | 202.9565
821.1917 | 208.1466 | 202.6054 | 202.7996
822.1917 | 208.5979 | 202.3661 | 202.5446
823.1917 | 207.6745 | 202.1774 | 202.1403
824.1917 | 207.6909 | 202.9446 | 202.2402
825.1917 | 206.9543 | 202.2335 | 201.7311
826.1917 | 207.2358 | 201.8617 | 201.258
827.1917 | 207.4415 | 202.0698 | 200.7082
828.1917 | 207.5055 | 201.7676 | 200.1751
829.1917 | 207.3797 | 201.4147 | 200.1264
830.1917 | 207.0128 | 201.1905 | 199.7455
831.1917 | 206.7845 | 201.0618 | 199.353
832.1917 | 207.0132 | 200.8419 | 199.0487
833.1917 | 207.0526 | 200.5951 | 198.4993
834.1917 | 206.9009 | 200.133 | 198.3216
835.1917 | 206.6503 | 199.973 | 198.1907
836.1917 | 206.2133 | 199.9148 | 198.1007
837.1917 | 205.7932 | 199.6782 | 198.2707
838.1917 | 205.5026 | 199.6241 | 199.0488
839.1917 | 205.1003 | 199.7838 | 199.1396
840.1917 | 205.4317 | 199.7899 | 200.4055
841.1917 | 205.4295 | 199.8135 | 200.2491
842.1917 | 205.0475 | 200.0755 | 199.9682
843.1917 | 205.756 | 200.2101 | 200.0139
844.1917 | 206.2204 | 200.4986 | 199.9181
845.2073 | 206.23 | 200.7545 | 200.1769
846.1917 | 206.3196 | 200.9243 | 200.3552
847.1917 | 206.6864 | 200.8677 | 200.2371
848.1917 | 206.3318 | 200.9467 | 200.2093
849.1917 | 206.1874 | 201.347 | 200.8725
850.1917 | 206.3476 | 201.3332 | 202.5312
851.1917 | 206.5936 | 201.5298 | 202.8474
852.1917 | 206.0713 | 201.893 | 203.078
853.1917 | 206.2634 | 202.372 | 203.8556
854.1917 | 206.2184 | 202.7006 | 203.7495
855.1917 | 206.7791 | 202.6417 | 203.7383
856.1917 | 207.0271 | 202.4902 | 203.516
857.1917 | 206.6447 | 203.1726 | 204.1035
858.1917 | 207.0308 | 203.1039 | 203.9385
859.1917 | 207.2938 | 204.4405 | 203.906
860.1917 | 207.1044 | 204.1316 | 203.9454
861.1917 | 206.9074 | 203.7347 | 203.2388
862.1917 | 206.6404 | 203.6596 | 202.77
863.1917 | 206.1739 | 203.4337 | 202.3622
864.1917 | 205.9954 | 203.7799 | 201.8072
865.1917 | 205.9833 | 203.9663 | 201.3453
866.1917 | 206.5541 | 204.5624 | 201.4532
867.1917 | 206.7507 | 205.063 | 202.174
868.1917 | 206.2682 | 204.8316 | 201.7702
869.1917 | 205.9857 | 205.1444 | 202.9642
870.1917 | 205.9897 | 205.066 | 202.653
871.1917 | 206.4823 | 205.8303 | 203.4495
872.1917 | 206.8101 | 205.7696 | 203.0866
873.1917 | 207.2009 | 206.1552 | 204.3722
874.1917 | 207.5826 | 206.3205 | 204.2841
875.1917 | 207.8162 | 206.3893 | 204.5304
876.1917 | 207.797 | 206.1563 | 205.1675
877.1917 | 207.4935 | 206.5066 | 204.4767
878.1917 | 207.6432 | 207.8529 | 204.8252
879.1917 | 208.3744 | 208.0069 | 205.3461
880.1917 | 208.4497 | 208.089 | 205.6367
881.1917 | 208.2504 | 208.1571 | 205.2506
882.2073 | 208.7335 | 208.0447 | 204.7877
883.1917 | 208.8632 | 207.9521 | 204.5145
884.1917 | 208.8971 | 207.5707 | 204.9586
885.1917 | 208.7211 | 207.465 | 205.1684
886.1917 | 209.0023 | 207.6532 | 204.8648
887.1917 | 208.9498 | 207.8722 | 204.8865
888.1917 | 208.3696 | 207.4487 | 204.4301
889.1917 | 208.5468 | 207.0018 | 204.1633
890.1917 | 208.2176 | 206.6685 | 203.7932
891.1917 | 207.4623 | 206.3536 | 203.4114
892.1917 | 206.9145 | 206.1555 | 203.1305
893.1917 | 206.5679 | 205.5402 | 202.4804
894.1917 | 206.3951 | 205.2808 | 202.0692
895.1917 | 206.0695 | 205.0364 | 201.8383
896.1917 | 205.6019 | 205.5587 | 202.1206
897.1917 | 205.1147 | 205.1205 | 202.017
898.1917 | 205.2744 | 205.2475 | 202.0679
899.1917 | 205.3797 | 205.2839 | 202.0593
900.1917 | 205.7449 | 204.8441 | 201.6168
901.1917 | 205.3707 | 204.4359 | 201.3412
902.1917 | 205.8111 | 204.6768 | 202.1578
903.1917 | 206.048 | 204.7388 | 202.2044
904.1917 | 206.5252 | 204.7109 | 203.4907
905.1917 | 206.791 | 204.8172 | 204.0808
906.1917 | 207.1866 | 205.7235 | 204.2802
907.1917 | 208.8947 | 205.8027 | 204.575
908.1917 | 209.4184 | 206.2537 | 204.892
909.1917 | 209.9993 | 206.9396 | 204.6664
910.1917 | 211.2921 | 207.5553 | 204.9924
911.1917 | 212.3502 | 207.4556 | 204.9225
912.2073 | 213.2497 | 208.1095 | 204.954
913.1917 | 214.2091 | 208.4389 | 204.6159
914.1917 | 214.3568 | 208.7311 | 204.876
915.1917 | 215.5903 | 208.9839 | 205.2118
916.1917 | 216.3397 | 209.296 | 205.074
917.1917 | 216.2669 | 209.8083 | 206.1883
918.1917 | 216.1865 | 211.0134 | 206.3646
919.1917 | 216.5865 | 211.7787 | 206.1306
920.1917 | 216.7757 | 211.4093 | 206.2474
921.1917 | 217.4382 | 211.4038 | 206.3685
922.1917 | 217.3936 | 211.6379 | 206.4021
923.1917 | 218.1482 | 212.3235 | 206.9152
924.1917 | 218.7448 | 212.9994 | 207.8828
925.1917 | 219.4971 | 213.2711 | 208.4952
926.1917 | 219.3458 | 213.7891 | 208.8065
927.1917 | 219.5504 | 214.035 | 208.9275
928.1917 | 219.6398 | 214.0107 | 208.8656
929.1917 | 219.4206 | 213.9712 | 209.728
930.1917 | 219.0848 | 213.9186 | 209.9603
931.1917 | 218.4495 | 213.7694 | 210.1712
932.1917 | 218.0347 | 213.746 | 210.287
933.1917 | 217.5676 | 213.38 | 210.0059
934.1917 | 217.2771 | 213.03 | 210.3883
935.1917 | 217.1401 | 212.6656 | 209.9209
936.1917 | 217.4555 | 212.5573 | 209.5954
937.1917 | 217.6713 | 212.6877 | 209.3866
938.1917 | 217.2569 | 212.9194 | 209.3867
939.1917 | 217.0268 | 212.7345 | 209.5951
940.1917 | 217.2588 | 212.2831 | 209.7966
941.1917 | 217.0073 | 212.1145 | 209.8192
942.1917 | 216.696 | 212.6465 | 209.6215
943.1917 | 216.769 | 212.4675 | 209.3492
944.1917 | 217.0063 | 212.5388 | 209.2995
945.1917 | 216.8204 | 212.5259 | 208.8758
946.1917 | 216.9407 | 212.5713 | 209.1105
947.1917 | 216.9227 | 212.4898 | 209.7595
948.1917 | 216.8722 | 212.3581 | 209.6496
949.1917 | 216.9107 | 212.4771 | 209.4619
950.1917 | 216.8099 | 212.8542 | 209.4228
951.1917 | 217.2735 | 212.6921 | 209.2934
952.1917 | 217.2312 | 213.4275 | 210.2604
953.1917 | 217.55 | 213.5663 | 210.5836
954.1917 | 217.7748 | 213.9137 | 210.984
955.1917 | 218.4587 | 213.7805 | 210.9998
956.1917 | 219.1833 | 214.0685 | 211.1515
957.1917 | 219.7884 | 214.0518 | 211.1209
958.1917 | 219.7339 | 214.7849 | 211.2355
959.1917 | 220.238 | 215.1931 | 211.512
960.1917 | 220.1895 | 216.0269 | 212.0302
961.1917 | 221.0938 | 217.0663 | 213.2884
962.1917 | 220.7932 | 217.5135 | 212.9917
963.1917 | 222.6998 | 219.7172 | 213.1265
964.1917 | 222.318 | 219.3918 | 213.1417
965.1917 | 222.3596 | 221.1004 | 213.696
966.1917 | 223.6265 | 222.5827 | 214.8565
967.1917 | 224.6313 | 223.0279 | 217.175
968.1917 | 225.055 | 223.3552 | 217.742
969.1917 | 225.2181 | 223.3963 | 218.1692
970.1917 | 224.9769 | 223.2897 | 218.1116
971.1917 | 224.9651 | 223.148 | 217.8122
972.2073 | 225.3357 | 222.701 | 217.3698
973.1917 | 224.9704 | 222.3246 | 217.0885
974.1917 | 224.4403 | 221.8551 | 216.7187
975.1917 | 224.1088 | 221.5609 | 216.5792
976.1917 | 223.7382 | 221.3522 | 216.525
977.1917 | 222.8481 | 220.8934 | 216.3754
978.1917 | 222.3829 | 220.498 | 217.0557
979.1917 | 221.8358 | 220.0457 | 216.5459
980.1917 | 221.4207 | 219.9224 | 216.6306
981.1917 | 220.6247 | 219.7374 | 216.3392
982.1917 | 220.3299 | 219.576 | 216.0663
983.1917 | 219.7509 | 219.3752 | 215.7831
984.1917 | 219.4576 | 219.2538 | 216.0534
985.1917 | 219.1584 | 218.9039 | 216.2982
986.1917 | 218.5618 | 218.6361 | 215.9139
987.1917 | 217.8076 | 218.4591 | 216.5105
988.1917 | 218.1341 | 218.485 | 216.3772
989.1917 | 218.4429 | 218.4877 | 215.7169
990.1917 | 218.4174 | 218.4778 | 215.7429
991.1917 | 218.2532 | 218.2282 | 215.7482
992.1917 | 217.9388 | 218.1003 | 215.2506
993.1917 | 217.9345 | 218.3244 | 214.7976
994.1917 | 218.4876 | 218.4625 | 214.716
995.1917 | 218.5593 | 218.8746 | 214.7899
996.1917 | 218.5462 | 219.2217 | 214.8384
997.1917 | 218.0378 | 218.9264 | 214.3774
998.1917 | 217.6332 | 219.6445 | 215.1603
999.1917 | 217.1553 | 219.1377 | 214.5733
1000.1917 | 216.5804 | 219.3684 | 214.2603
1001.1917 | 216.5534 | 219.4979 | 213.8492
1002.1917 | 217.4543 | 219.3151 | 214.0964
1003.1917 | 217.8005 | 219.3522 | 214.2607
1004.1917 | 217.8337 | 218.9356 | 215.02
1005.1917 | 217.97 | 218.838 | 214.8376
1006.1917 | 218.3689 | 219.0786 | 214.939
1007.1917 | 218.95 | 219.0304 | 214.9699
1008.1917 | 219.2728 | 219.5596 | 215.1402
1009.1917 | 220.2418 | 220.257 | 215.3272
1010.1917 | 220.4421 | 220.6122 | 215.8066
1011.1917 | 220.8109 | 221.1481 | 215.9061
1012.1917 | 221.0241 | 221.0931 | 215.6902
1013.1917 | 222.1368 | 221.2156 | 215.7853
1014.1917 | 222.3304 | 221.3204 | 215.3975
1015.1917 | 222.3992 | 221.1456 | 215.442
1016.1917 | 222.1843 | 221.0559 | 215.4529
1017.1917 | 221.8418 | 220.8912 | 215.2368
1018.1917 | 221.6921 | 221.0973 | 215.1816
1019.1917 | 221.409 | 221.4307 | 215.0687
1020.1917 | 220.9319 | 220.853 | 214.8611
1021.1917 | 220.6326 | 220.7058 | 214.9152
1022.1917 | 220.3812 | 220.2734 | 214.6019
1023.1917 | 220.3038 | 220.0776 | 214.7185
1024.1917 | 220.22 | 220.0454 | 214.5843
1025.1917 | 219.8983 | 220.0052 | 214.7863
1026.1917 | 220.0322 | 220.5821 | 214.8666
1027.1917 | 220.507 | 220.207 | 214.909
1028.1917 | 220.9403 | 219.8451 | 215.4391
1029.1917 | 220.9452 | 219.9715 | 215.9303
1030.1917 | 221.2792 | 219.9814 | 216.0578
1031.1917 | 221.7335 | 220.0629 | 216.185
1032.2073 | 221.5451 | 220.1545 | 215.8149
1033.1917 | 221.3799 | 220.2527 | 215.6167
1034.1917 | 221.2185 | 220.166 | 215.5449
1035.1917 | 221.3063 | 219.9617 | 215.5986
1036.1917 | 221.0977 | 220.1067 | 215.562
1037.1917 | 221.1662 | 220.0487 | 215.7272
1038.1917 | 221.287 | 219.9125 | 215.8287
1039.1917 | 221.2008 | 219.8631 | 215.9614
1040.1917 | 221.1328 | 219.727 | 216.115
1041.1917 | 221.0068 | 219.4398 | 216.2348
1042.1917 | 220.7282 | 219.0947 | 216.1381
1043.2073 | 220.4949 | 218.8865 | 215.9207
1044.1917 | 220.633 | 219.9047 | 216.4696
1045.1917 | 220.3774 | 220.8929 | 217.2722
1046.1917 | 220.2249 | 221.0522 | 217.6634
1047.1917 | 220.7431 | 221.5364 | 218.2553
1048.1917 | 221.7369 | 222.4971 | 219.1845
1049.1917 | 222.3183 | 222.5431 | 219.244
1050.1917 | 223.0308 | 222.8126 | 219.6946
1051.1917 | 223.3322 | 223.0294 | 219.3946
1052.1917 | 223.8719 | 223.4389 | 219.958
1053.2073 | 224.0717 | 224.0771 | 220.3903
1054.1917 | 224.4616 | 224.6799 | 221.0334
1055.1917 | 225.8943 | 225.4806 | 222.3282
1056.1917 | 226.4594 | 226.2843 | 222.8141
1057.1917 | 227.1369 | 226.8687 | 223.2853
1058.1917 | 227.9095 | 228.1361 | 223.8271
1059.1917 | 228.0971 | 228.7141 | 224.4303
1060.1917 | 228.746 | 229.4911 | 225.1788
1061.1917 | 228.6949 | 229.6027 | 224.9493
1062.1917 | 229.075 | 229.8618 | 225.0064
1063.2073 | 229.8732 | 230.5403 | 225.6667
1064.1917 | 229.843 | 230.4692 | 225.5026
1065.1917 | 230.1827 | 230.4176 | 225.6629
1066.1917 | 230.3136 | 230.6979 | 225.5136
1067.1917 | 230.6916 | 230.8519 | 225.5473
1068.1917 | 230.7353 | 231.0927 | 225.425
1069.1917 | 230.8572 | 231.5294 | 225.9067
1070.1917 | 231.1884 | 232.1454 | 226.7464
1071.1917 | 231.7719 | 232.9429 | 227.5542
1072.1917 | 232.1874 | 233.7927 | 228.2452
1073.1917 | 232.3919 | 234.6205 | 228.8613
1074.1917 | 232.973 | 235.4456 | 229.1693
1075.1917 | 233.1961 | 235.7423 | 230.1534
1076.1917 | 233.4662 | 236.0955 | 231.0583
1077.1917 | 234.2497 | 236.4041 | 230.7818
1078.1917 | 234.5118 | 236.5046 | 230.5227
1079.1917 | 234.4318 | 236.387 | 230.3947
1080.1917 | 234.4004 | 236.1715 | 230.7147
1081.1917 | 234.2109 | 236.1826 | 231.1264
1082.1917 | 234.2875 | 235.9932 | 230.4944
1083.1917 | 234.0414 | 235.7596 | 230.5074
1084.1917 | 233.9546 | 235.6535 | 230.7141
1085.1917 | 234.0026 | 235.5865 | 230.55
1086.1917 | 233.9919 | 235.8834 | 230.8711
1087.1917 | 234.0215 | 235.8561 | 230.8529
1088.1917 | 233.9948 | 235.9508 | 230.7439
1089.1917 | 234.2828 | 236.0525 | 230.5129
1090.1917 | 234.5946 | 236.1278 | 230.7068
1091.1917 | 234.8305 | 236.2627 | 230.8112
1092.2073 | 235.27 | 236.4199 | 230.739
1093.1917 | 235.4897 | 236.9023 | 230.6832
1094.1917 | 235.7516 | 236.9878 | 230.4585
1095.1917 | 235.3751 | 236.8011 | 230.6741
1096.1917 | 235.7057 | 236.5936 | 230.0742
1097.1917 | 235.4551 | 236.3582 | 229.9525
1098.1917 | 236.1367 | 235.9809 | 230.1341
1099.1917 | 236.1919 | 235.9599 | 230.2525
1100.1917 | 236.336 | 236.069 | 230.0701
1101.1917 | 236.1032 | 236.1126 | 230.4228
1102.1917 | 235.759 | 236.0717 | 230.5676
1103.1917 | 235.7325 | 235.8623 | 230.3067
1104.1917 | 236.5667 | 235.7276 | 230.2266
1105.1917 | 236.1835 | 235.4395 | 230.262
1106.1917 | 236.5218 | 235.1194 | 229.9972
1107.1917 | 236.4342 | 235.6447 | 229.9574
1108.1917 | 237.4514 | 235.462 | 229.8985
1109.1917 | 237.2761 | 235.4371 | 229.9118
1110.1917 | 237.251 | 235.5441 | 229.9472
1111.1917 | 237.1596 | 235.3673 | 229.9507
1112.1917 | 237.2497 | 235.2297 | 229.7586
1113.1917 | 237.1245 | 234.9789 | 229.8103
1114.1917 | 237.2402 | 235.03 | 229.5115
1115.1917 | 237.2211 | 235.3 | 229.5189
1116.1917 | 237.3385 | 235.4172 | 229.8912
1117.1917 | 237.5759 | 235.5478 | 230.2472
1118.1917 | 237.9725 | 235.8655 | 230.5043
1119.1917 | 238.7036 | 236.4067 | 231.5216
1120.1917 | 239.6985 | 237.0954 | 232.3698
1121.1917 | 239.8603 | 238.0807 | 232.7298
1122.1917 | 240.6551 | 238.5933 | 233.4871
1123.1917 | 240.6379 | 239.18 | 234.0849
1124.1917 | 240.5291 | 239.4399 | 234.4577
1125.1917 | 240.8208 | 239.6608 | 234.3608
1126.1917 | 241.0082 | 239.4878 | 234.4959
1127.1917 | 241.3917 | 239.5159 | 234.5388
1128.1917 | 241.4438 | 239.4585 | 234.3597
1129.1917 | 241.0606 | 239.2174 | 234.4194
1130.1917 | 240.7767 | 238.9939 | 234.2462
1131.1917 | 240.4479 | 238.7626 | 234.386
1132.1917 | 240.7176 | 238.5631 | 234.1003
1133.1917 | 240.1187 | 238.9364 | 234.2603
1134.1917 | 240.9552 | 239.2964 | 235.7726
1135.1917 | 240.9352 | 239.2529 | 235.4466
1136.1917 | 240.5631 | 239.387 | 235.2876
1137.1917 | 241.202 | 239.3334 | 235.2745
1138.1917 | 241.5305 | 239.663 | 235.1428
1139.1917 | 241.7391 | 239.6198 | 234.7295
1140.1917 | 241.5097 | 239.7149 | 234.6178
1141.1917 | 241.3162 | 240.1977 | 234.5096
1142.1917 | 240.8991 | 240.0097 | 234.1512
1143.1917 | 240.9785 | 239.9501 | 234.1538
1144.1917 | 240.5112 | 239.7881 | 233.6703
1145.1917 | 240.2292 | 239.7042 | 233.5731
1146.1917 | 240.6639 | 239.88 | 233.3115
1147.1917 | 240.7141 | 240.059 | 233.464
1148.1917 | 240.6924 | 240.1666 | 233.7358
1149.1917 | 240.7242 | 240.2293 | 234.1579
1150.1917 | 241.3705 | 240.4408 | 233.9991
1151.1917 | 241.5198 | 240.4653 | 233.9268
1152.1917 | 241.4826 | 240.4599 | 233.9653
1153.1917 | 241.7219 | 240.0935 | 233.9345
1154.1917 | 241.5912 | 240.146 | 233.7385
1155.1917 | 243.212 | 241.0983 | 234.0652
1156.1917 | 242.5104 | 240.9118 | 233.9816
1157.1917 | 242.2744 | 240.9019 | 233.9316
1158.1917 | 241.9425 | 241.1351 | 234.1042
1159.1917 | 241.8611 | 240.9294 | 234.2103
1160.1917 | 241.6334 | 240.5026 | 233.7536
1161.1917 | 241.2608 | 240.2723 | 233.4709
1162.1917 | 241.005 | 239.91 | 233.3132
1163.1917 | 240.8395 | 239.3995 | 233.273
1164.1917 | 240.9615 | 239.2624 | 233.3836
1165.1917 | 240.8339 | 238.9547 | 233.5086
1166.1917 | 240.7252 | 238.7196 | 233.9141
1167.1917 | 240.6679 | 238.4123 | 233.7025
1168.1917 | 241.0975 | 238.2433 | 234.1197
1169.1917 | 242.0531 | 238.5493 | 234.1422
1170.1917 | 242.0339 | 239.0987 | 234.0561
1171.1917 | 242.1983 | 239.301 | 234.3461
1172.1917 | 242.2689 | 238.8019 | 234.7882
1173.1917 | 241.9344 | 238.4264 | 234.8979
1174.1917 | 242.2795 | 238.2489 | 234.6159
1175.1917 | 241.8349 | 237.9935 | 234.4665
1176.1917 | 241.5037 | 237.8495 | 234.6016
1177.1917 | 241.2779 | 238.4297 | 234.9441
1178.1917 | 241.2074 | 238.9992 | 235.4037
1179.1917 | 241.2184 | 239.1893 | 235.5108
1180.1917 | 240.8 | 239.0952 | 235.5937
1181.1917 | 240.6723 | 238.8689 | 235.3072
1182.1917 | 240.7457 | 238.7976 | 235.087
1183.1917 | 240.82 | 238.6976 | 234.747
1184.1917 | 240.6872 | 238.7625 | 234.76
1185.1917 | 240.1134 | 238.8523 | 234.6641
1186.1917 | 239.777 | 238.6471 | 234.7415
1187.1917 | 239.9833 | 238.557 | 234.369
1188.1917 | 239.6051 | 238.2194 | 234.8282
1189.1917 | 239.3326 | 237.8639 | 234.9221
1190.1917 | 239.0486 | 237.8307 | 234.9009
1191.1917 | 238.7106 | 237.7185 | 234.7565
1192.1917 | 238.5158 | 237.5921 | 234.9143
1193.1917 | 238.4631 | 237.5122 | 234.7249
1194.1917 | 238.4782 | 237.741 | 234.9912
1195.1917 | 238.4656 | 237.7995 | 235.4
1196.1917 | 238.6117 | 238.027 | 235.2319
1197.1917 | 239.1323 | 238.3658 | 235.1851
1198.1917 | 239.3626 | 238.5379 | 235.6688
1199.1917 | 239.5463 | 238.6669 | 236.0917
1200.1917 | 239.7609 | 238.5596 | 236.4317
1201.1917 | 239.6321 | 238.5996 | 236.4642
1202.1917 | 239.4094 | 238.4972 | 236.2851
1203.1917 | 239.3948 | 238.8062 | 236.5542
1204.1917 | 239.4243 | 238.8845 | 236.7189
1205.1917 | 239.618 | 239.0171 | 236.975
1206.1917 | 239.7133 | 239.7106 | 237.3139
1207.1917 | 240.2988 | 240.2121 | 237.8788
1208.1917 | 240.644 | 240.8714 | 238.1743
1209.1917 | 241.5398 | 241.372 | 238.5088
1210.1917 | 241.7337 | 241.5564 | 239.5089
1211.1917 | 241.8459 | 241.8482 | 239.6668
1212.1917 | 241.9647 | 241.9515 | 239.6065
1213.1917 | 242.2965 | 242.2568 | 239.8524
1214.1917 | 242.7834 | 242.4259 | 240.1001
1215.1917 | 242.9419 | 242.5015 | 240.7198
1216.1917 | 243.1352 | 242.7492 | 240.5846
1217.1917 | 243.4643 | 242.967 | 240.8748
1218.1917 | 243.6519 | 243.0602 | 241.5079
1219.1917 | 243.7605 | 243.2702 | 241.6561
1220.1917 | 243.5023 | 243.2536 | 241.4067
1221.1917 | 244.1324 | 243.3165 | 241.5855
1222.1917 | 243.7953 | 243.5049 | 241.7441
1223.1917 | 243.942 | 243.6088 | 241.7064
1224.1917 | 244.2578 | 243.8876 | 242.3412
1225.1917 | 244.3063 | 244.1839 | 242.2407
1226.1917 | 244.496 | 244.6141 | 242.4555
1227.1917 | 244.587 | 244.4761 | 242.0279
1228.1917 | 244.7211 | 244.4774 | 241.9468
1229.1917 | 244.9896 | 244.5943 | 241.8872
1230.1917 | 244.9524 | 244.6757 | 241.8956
1231.1917 | 244.9554 | 245.1345 | 242.8537
1232.1917 | 245.3246 | 245.2708 | 242.4479
1233.1917 | 245.5239 | 245.2324 | 242.3029
1234.1917 | 245.5481 | 245.1662 | 242.2474
1235.1917 | 245.508 | 245.0305 | 241.9595
1236.1917 | 245.5146 | 244.9538 | 242.0044
1237.1917 | 245.7055 | 244.8093 | 241.8357
1238.1917 | 246.3868 | 244.9106 | 241.782
1239.1917 | 246.0485 | 244.9159 | 241.5517
1240.1917 | 245.7181 | 244.5912 | 241.8433
1241.1917 | 245.3555 | 244.2721 | 241.7352
1242.1917 | 245.2102 | 244.4364 | 241.9081
1243.1917 | 245.0236 | 244.4877 | 242.2527
1244.1917 | 245.0926 | 244.6075 | 242.3533
1245.1917 | 245.0323 | 244.5412 | 242.1841
1246.1917 | 245.0163 | 244.503 | 242.9068
1247.1917 | 245.0835 | 244.3236 | 242.8197
1248.1917 | 244.9145 | 244.2818 | 242.4435
1249.1917 | 245.0398 | 244.2649 | 242.4694
1250.1917 | 245.0619 | 244.416 | 242.3506
1251.1917 | 245.6099 | 244.326 | 242.3742
1252.1917 | 245.7881 | 244.2249 | 242.3373
1253.1917 | 246.0801 | 243.9957 | 242.0095
1254.1917 | 246.3418 | 244.0295 | 241.8991
1255.1917 | 246.8153 | 244.5004 | 241.7261
1256.1917 | 246.8086 | 245.1962 | 241.7903
1257.1917 | 247.0826 | 245.2256 | 241.8377
1258.1917 | 246.9793 | 245.4713 | 241.8944
1259.1917 | 246.7011 | 245.51 | 241.6948
1260.1917 | 246.6987 | 245.5861 | 241.8155
1261.1917 | 246.4517 | 245.8297 | 241.6436
1262.1917 | 246.4129 | 245.8323 | 241.415
1263.1917 | 246.2912 | 245.6889 | 241.4678
1264.1917 | 246.45 | 245.5376 | 241.4058
1265.1917 | 246.8453 | 245.619 | 241.6206
1266.1917 | 246.9191 | 245.5753 | 241.9049
1267.1917 | 247.4801 | 245.863 | 242.1914
1268.1917 | 247.8706 | 245.8645 | 242.5638
1269.1917 | 248.1926 | 245.996 | 242.6234
1270.1917 | 248.4879 | 246.4089 | 242.9086
1271.1917 | 248.5866 | 247.1397 | 243.3347
1272.1917 | 248.603 | 247.7736 | 243.8501
1273.1917 | 248.6828 | 248.1126 | 244.0638
1274.1917 | 248.9041 | 248.6637 | 244.6915
1275.1917 | 248.8685 | 248.8113 | 245.1865
1276.1917 | 249.1655 | 248.8025 | 245.4512
1277.1917 | 249.1988 | 248.7173 | 245.5067
1278.1917 | 249.604 | 248.9929 | 246.1339
1279.1917 | 249.7049 | 249.1029 | 246.5761
1280.1917 | 250.3587 | 249.0426 | 246.6243
1281.1917 | 250.6045 | 249.8049 | 246.9917
1282.1917 | 250.6841 | 249.8602 | 246.974
1283.1917 | 250.4688 | 249.9332 | 247.3079
1284.1917 | 250.5559 | 249.7988 | 247.1143
1285.1917 | 250.4957 | 249.9687 | 247.2341
1286.1917 | 250.4998 | 249.978 | 247.1299
1287.1917 | 250.6152 | 249.7713 | 247.2931
1288.1917 | 250.3888 | 249.6177 | 247.2978
1289.1917 | 250.1682 | 249.5979 | 248.0825
1290.1917 | 250.3684 | 249.792 | 248.204
1291.1917 | 250.5274 | 249.7875 | 248.4574
1292.1917 | 250.9744 | 250.3681 | 248.7936
1293.1917 | 251.4778 | 251.267 | 249.3409
1294.1917 | 252.0506 | 250.9161 | 249.6522
1295.1917 | 252.1016 | 251.1833 | 249.823
1296.1917 | 251.9143 | 251.8586 | 250.3157
1297.1917 | 251.9284 | 252.0519 | 250.4067
1298.1917 | 251.897 | 252.1846 | 250.5058
1299.1917 | 252.348 | 252.5508 | 250.8029
1300.1917 | 252.7498 | 252.7294 | 251.0344
1301.1917 | 253.4165 | 253.4109 | 251.8169
1302.1917 | 253.8723 | 253.9295 | 252.5609
1303.1917 | 254.4793 | 254.3619 | 252.8589
1304.1917 | 254.8737 | 254.9957 | 253.0855
1305.1917 | 254.9372 | 255.1525 | 253.4876
1306.1917 | 255.0057 | 255.489 | 253.8154
1307.1917 | 255.4914 | 256.1312 | 254.0172
1308.1917 | 255.8186 | 255.8846 | 254.2447
1309.1917 | 255.4709 | 255.7634 | 253.9617
1310.1917 | 256.2625 | 255.6443 | 253.7711
1311.1917 | 256.8021 | 255.7044 | 253.8352
1312.1917 | 257.0815 | 255.7354 | 254.0065
1313.1917 | 257.2875 | 255.7162 | 254.1015
1314.1917 | 257.4082 | 255.7501 | 254.2331
1315.1917 | 257.8554 | 255.8845 | 254.4672
1316.1917 | 258.4792 | 256.4027 | 254.6587
1317.1917 | 259.0365 | 256.5515 | 254.8032
1318.1917 | 259.4715 | 256.8942 | 255.4056
1319.1917 | 259.5902 | 257.2812 | 255.6284
1320.1917 | 259.4206 | 257.6238 | 256.0125
1321.1917 | 259.8056 | 257.8384 | 256.2516
1322.1917 | 260.0047 | 258.3975 | 256.8683
1323.1917 | 259.9759 | 258.5231 | 257.0991
1324.1917 | 259.9263 | 258.7515 | 257.2418
1325.1917 | 259.7608 | 259.155 | 257.2422
1326.1917 | 259.7572 | 259.3217 | 257.5956
1327.1917 | 259.5766 | 259.2764 | 257.9948
1328.1917 | 259.6591 | 259.392 | 258.0551
1329.1917 | 259.707 | 259.3185 | 258.051
1330.1917 | 259.837 | 259.4996 | 258.2394
1331.1917 | 260.2885 | 259.7308 | 258.5983
1332.1917 | 260.5192 | 260.1605 | 259.9963
1333.1917 | 260.7178 | 259.9543 | 261.8595
1334.1917 | 260.741 | 260.2655 | 262.5213
1335.1917 | 260.6885 | 260.0934 | 263.4073
1336.1917 | 260.8155 | 259.9733 | 264.6374
1337.1917 | 260.887 | 259.919 | 266.1472
1338.1917 | 261.1201 | 260.0255 | 266.699
1339.1917 | 261.692 | 260.1865 | 267.7455
1340.1917 | 262.5794 | 260.3824 | 268.3797
1341.1917 | 263.0483 | 260.7687 | 269.78
1342.1917 | 263.7294 | 260.8938 | 270.2938
1343.1917 | 264.9874 | 261.0371 | 270.4608
1344.1917 | 265.0229 | 261.3353 | 271.0968
1345.1917 | 265.4229 | 261.398 | 272.6183
1346.1917 | 265.655 | 261.3784 | 273.1304
1347.1917 | 265.5309 | 261.7067 | 273.6774
1348.1917 | 265.5486 | 262.0826 | 275.0466
1349.1917 | 265.4456 | 261.9377 | 275.2789
1350.1917 | 265.7862 | 262.0456 | 276.0852
1351.1917 | 265.5185 | 262.1087 | 276.647
1352.1917 | 265.758 | 262.3249 | 277.4608
1353.1917 | 265.8594 | 262.5266 | 277.8348
1354.1917 | 265.9837 | 262.7884 | 277.98
1355.1917 | 266.2815 | 263.1418 | 278.0009
1356.1917 | 266.3721 | 263.4006 | 277.7378
1357.1917 | 266.5244 | 263.4709 | 277.5974
1358.1917 | 266.834 | 263.8547 | 277.9646
1359.1917 | 266.9377 | 264.2171 | 278.3172
1360.1917 | 267.3031 | 264.3191 | 279.0132
1361.1917 | 267.9427 | 264.7266 | 279.7598
1362.1917 | 268.4818 | 265.3978 | 281.4195
1363.1917 | 269.6304 | 265.8553 | 282.2551
1364.1917 | 270.8079 | 266.7121 | 283.3322
1365.1917 | 270.9352 | 267.3508 | 283.981
1366.1917 | 271.3412 | 267.6079 | 284.2643
1367.1917 | 271.5584 | 267.9661 | 285.2176
1368.1917 | 272.0504 | 267.9993 | 286.0726
1369.1917 | 272.4154 | 268.4725 | 286.8612
1370.1917 | 272.6666 | 269.6093 | 286.718
1371.1917 | 272.9086 | 269.6256 | 286.5619
1372.1917 | 272.8509 | 269.7977 | 287.3207
1373.1917 | 272.9768 | 269.5851 | 287.162
1374.1917 | 273.0821 | 269.557 | 287.7626
1375.1917 | 272.7551 | 269.5588 | 288.7941
1376.1917 | 273.1483 | 269.5914 | 289.3925
1377.1917 | 273.1669 | 270.1977 | 290.4554
1378.1917 | 273.1027 | 270.5448 | 290.899
1379.1917 | 272.9305 | 270.924 | 291.8132
1380.1917 | 272.7604 | 271.1023 | 291.3873
1381.1917 | 272.6242 | 271.0585 | 291.5547
1382.1917 | 272.3449 | 271.0897 | 291.0842
1383.1917 | 272.5544 | 271.1505 | 290.651
1384.1917 | 272.3217 | 271.0598 | 290.5386
1385.1917 | 272.3356 | 271.0306 | 290.4458
1386.1917 | 272.4896 | 271.0472 | 290.8079
1387.1917 | 272.4045 | 271.0163 | 290.5363
1388.1917 | 272.4428 | 270.8529 | 291.4832
1389.1917 | 272.4541 | 270.6059 | 292.3159
1390.1917 | 272.7365 | 270.3722 | 292.2488
1391.1917 | 272.8819 | 270.6596 | 292.9891
1392.1917 | 273.0984 | 270.5983 | 292.7239
1393.1917 | 273.3343 | 270.4936 | 292.428
1394.1917 | 273.2552 | 270.5132 | 292.2851
1395.1917 | 273.5938 | 270.5955 | 292.3994
1396.1917 | 273.7254 | 270.6593 | 292.9234
1397.1917 | 273.8364 | 270.6165 | 293.3768
1398.1917 | 274.1348 | 270.9998 | 294.0013
1399.1917 | 274.2107 | 271.2425 | 293.8003
1400.1917 | 274.399 | 271.2483 | 294.0044
1401.1917 | 274.3867 | 271.1883 | 294.2406
1402.1917 | 274.6623 | 271.4641 | 295.5434
1403.1917 | 275.0946 | 271.7707 | 295.4172
1404.1917 | 275.5561 | 271.8434 | 295.7299
1405.1917 | 275.8897 | 271.6328 | 295.5184
1406.1917 | 276.1333 | 272.3115 | 296.3442
1407.1917 | 278.2009 | 272.6794 | 296.7499
1408.1917 | 278.5517 | 273.7798 | 297.4619
1409.1917 | 278.7886 | 274.2669 | 297.5201
1410.1917 | 278.9473 | 274.4122 | 297.2457
1411.1917 | 279.9806 | 274.6615 | 297.5678
1412.1917 | 280.5103 | 275.0416 | 298.0619
1413.1917 | 281.1401 | 275.4254 | 298.651
1414.1917 | 281.59 | 276.1208 | 299.1148
1415.1917 | 282.1025 | 276.8874 | 299.4775
1416.1917 | 282.4123 | 276.9791 | 300.1825
1417.1917 | 282.9077 | 277.0163 | 300.1493
1418.1917 | 283.257 | 277.6337 | 300.8709
1419.1917 | 283.8285 | 277.9903 | 301.5437
1420.1917 | 284.1043 | 278.4106 | 302.212
1421.1917 | 284.855 | 278.758 | 302.0268
1422.1917 | 284.8547 | 278.6936 | 302.913
1423.1917 | 284.5537 | 279.1996 | 302.6606
1424.1917 | 284.3421 | 279.5012 | 304.0585
1425.1917 | 284.2425 | 279.616 | 304.5259
1426.1917 | 284.1283 | 279.9059 | 305.0936
1427.1917 | 284.3605 | 280.1108 | 305.2508
1428.1917 | 284.9037 | 280.5508 | 305.7959
1429.1917 | 285.6613 | 281.4011 | 307.2735
1430.1917 | 285.8964 | 281.8348 | 306.9911
1431.1917 | 285.8227 | 281.6481 | 307.3976
1432.1917 | 285.9267 | 281.9158 | 307.381
1433.1917 | 286.2033 | 282.2562 | 308.1468
1434.1917 | 286.1286 | 282.8256 | 308.2014
1435.1917 | 286.0386 | 282.7598 | 308.254
1436.1917 | 286.1228 | 283.0209 | 308.2115
1437.1917 | 286.117 | 283.7204 | 309.025
1438.1917 | 285.9196 | 284.194 | 309.3351
1439.1917 | 286.1797 | 284.7292 | 310.3507
1440.1917 | 286.4152 | 285.3194 | 310.2359
1441.1917 | 286.6104 | 285.9747 | 310.3422
1442.1917 | 286.8523 | 286.5007 | 309.8188
1443.1917 | 287.7413 | 286.7216 | 310.2945
1444.1917 | 288.1612 | 286.9156 | 310.7613
1445.1917 | 289.1847 | 287.7977 | 311.2467
1446.1917 | 289.5983 | 288.9079 | 312.4154
1447.1917 | 289.9209 | 289.2711 | 313.6863
1448.1917 | 290.5203 | 290.2639 | 315.2622
1449.1917 | 290.6297 | 290.8731 | 315.4494
1450.1917 | 290.5111 | 291.6311 | 315.1038
1451.1917 | 290.4448 | 291.914 | 314.8379
1452.1917 | 290.3846 | 292.2067 | 314.8652
1453.1917 | 290.238 | 292.088 | 314.3532
1454.1917 | 290.1898 | 292.5737 | 315.1075
1455.1917 | 290.1073 | 292.4525 | 316.6113
1456.1917 | 290.0962 | 293.0575 | 316.3489
1457.1917 | 290.3276 | 293.1599 | 316.9751
1458.1917 | 290.7303 | 293.2133 | 317.4837
1459.1917 | 290.6531 | 292.8835 | 316.7761
1460.1917 | 290.4965 | 292.3995 | 316.07
1461.1917 | 290.6775 | 292.0382 | 315.9285
1462.1917 | 290.9688 | 292.007 | 315.7346
1463.1917 | 291.1589 | 292.4791 | 316.7562
1464.1917 | 291.7839 | 292.6783 | 316.7772
1465.1917 | 292.0742 | 292.7359 | 316.9908
1466.1917 | 292.3867 | 292.868 | 316.8493
1467.1917 | 292.1655 | 292.7813 | 316.6865
1468.1917 | 292.0911 | 292.8588 | 317.9845
1469.1917 | 292.1581 | 292.761 | 318.2909
1470.1917 | 291.8409 | 293.2436 | 318.4717
1471.1917 | 291.8517 | 292.9631 | 319.3381
1472.1917 | 291.5746 | 292.6724 | 319.0766
1473.1917 | 291.355 | 293.2906 | 319.1778
1474.1917 | 291.2909 | 293.2749 | 318.6931
1475.1917 | 291.145 | 292.9577 | 319.1597
1476.1917 | 291.2387 | 293.1145 | 320.0377
1477.1917 | 291.6613 | 293.1146 | 319.9713
1478.1917 | 291.9194 | 293.111 | 321.1142
1479.1917 | 291.9079 | 293.0253 | 320.774
1480.1917 | 292.3603 | 293.0807 | 321.2833
1481.1917 | 292.9315 | 293.393 | 321.4244
1482.1917 | 293.125 | 293.5312 | 321.796
1483.1917 | 294.0151 | 293.7858 | 322.2983
1484.1917 | 294.7489 | 293.6156 | 322.038
1485.1917 | 296.0495 | 294.069 | 322.0335
1486.1917 | 296.7806 | 294.68 | 321.4709
1487.1917 | 297.9879 | 294.9274 | 321.9032
1488.1917 | 298.407 | 295.6867 | 321.9139
1489.1917 | 299.0406 | 295.9147 | 322.1629
1490.1917 | 299.7354 | 295.7557 | 322.8899
1491.1917 | 300.5628 | 295.6335 | 324.1804
1492.1917 | 301.5276 | 296.409 | 324.3915
1493.1917 | 302.0059 | 296.9044 | 325.2087
1494.1917 | 301.5151 | 297.8648 | 324.6992
1495.1917 | 301.1969 | 297.7042 | 324.7262
1496.1917 | 300.7977 | 297.2245 | 324.3267
1497.1917 | 300.32 | 296.9073 | 323.6581
1498.1917 | 299.9004 | 296.9445 | 322.7125
1499.1917 | 299.729 | 296.6641 | 322.917
1500.1917 | 300.1171 | 296.5777 | 322.6006
1501.1917 | 300.4571 | 297.1426 | 322.8573
1502.1917 | 300.4511 | 297.4007 | 323.9148
1503.1917 | 300.7043 | 297.7762 | 324.0445
1504.1917 | 300.5664 | 297.7969 | 323.7168
1505.1917 | 300.4819 | 298.0005 | 323.3251
1506.1917 | 300.4543 | 298.1065 | 323.1958
1507.1917 | 300.4126 | 297.8492 | 323.0477
1508.1917 | 300.374 | 298.0629 | 323.7072
1509.1917 | 300.4521 | 297.9555 | 323.3394
1510.1917 | 300.4105 | 298.4196 | 323.1149
1511.1917 | 300.2151 | 298.8248 | 322.993
1512.1917 | 300.5123 | 298.5665 | 323.0539
1513.1917 | 300.658 | 298.7917 | 323.1867
1514.1917 | 300.7619 | 298.8097 | 323.4598
1515.1917 | 300.7697 | 299.0792 | 323.2183
1516.1917 | 301.1253 | 299.1477 | 323.0557
1517.1917 | 301.4859 | 299.8079 | 323.2704
1518.1917 | 301.7704 | 300.5707 | 323.6051
1519.1917 | 302.0759 | 301.3066 | 324.2952
1520.1917 | 301.968 | 301.7856 | 325.0111
1521.1917 | 302.0956 | 302.2931 | 325.1715
1522.1917 | 302.303 | 302.6186 | 326.9885
1523.1917 | 302.5186 | 302.8456 | 327.8351
1524.1917 | 303.1315 | 303.6625 | 328.6295
1525.1917 | 303.7121 | 304.3099 | 328.9828
1526.1917 | 303.9395 | 305.436 | 329.119
1527.1917 | 303.9558 | 306.231 | 329.3111
1528.1917 | 304.0549 | 306.4048 | 329.5862
1529.1917 | 304.1709 | 306.4507 | 329.9199
1530.1917 | 304.5929 | 306.4973 | 329.5657
1531.1917 | 304.7361 | 306.3493 | 329.6806
1532.1917 | 305.2928 | 306.4423 | 329.3682
1533.1917 | 305.466 | 306.0602 | 329.1403
1534.1917 | 305.6205 | 305.8277 | 330.1633
1535.1917 | 305.6524 | 305.6775 | 330.7418
1536.1917 | 306.2617 | 305.3352 | 331.2027
1537.1917 | 306.6496 | 305.0883 | 331.7866
1538.1917 | 306.5916 | 305.0971 | 332.1716
1539.1917 | 306.6792 | 305.4341 | 332.05
1540.1917 | 306.1963 | 305.9117 | 331.5668
1541.1917 | 306.6394 | 305.8878 | 331.5776
1542.1917 | 306.8072 | 306.1349 | 331.8844
1543.1917 | 307.0698 | 306.0376 | 331.8712
1544.1917 | 307.1792 | 306.4795 | 332.9875
1545.1917 | 307.1933 | 307.0051 | 333.0295
1546.1917 | 308.3469 | 306.9458 | 332.9128
1547.1917 | 308.6388 | 307.2194 | 332.7736
1548.1917 | 309.6903 | 307.9887 | 334.1425
1549.1917 | 309.9365 | 308.0249 | 335.1471
1550.1917 | 310.8765 | 308.3189 | 335.8525
1551.1917 | 311.2902 | 308.1712 | 336.208
1552.1917 | 311.767 | 308.324 | 335.798
1553.1917 | 312.6095 | 308.4781 | 337.2747
1554.1917 | 313.5047 | 308.8771 | 337.9449
1555.1917 | 314.0272 | 309.6173 | 338.3623
1556.1917 | 314.4787 | 309.9285 | 337.7812
1557.1917 | 315.0958 | 310.1948 | 337.3306
1558.1917 | 315.8586 | 310.7913 | 336.7727
1559.1917 | 315.9632 | 311.2327 | 337.5653
1560.1917 | 315.9882 | 311.4732 | 338.0946
1561.1917 | 316.1333 | 311.5467 | 338.5672
1562.1917 | 316.5963 | 312.1051 | 338.7408
1563.1917 | 317.0913 | 311.9144 | 339.4821
1564.1917 | 317.8542 | 312.2755 | 339.7789
1565.2073 | 318.051 | 312.6696 | 339.5478
1566.1917 | 318.8598 | 313.8933 | 340.4719
1567.1917 | 318.9959 | 314.2873 | 341.4512
1568.1917 | 319.0164 | 314.2707 | 341.9595
1569.1917 | 318.8332 | 314.1199 | 342.9252
1570.1917 | 319.3328 | 314.568 | 343.5422
1571.1917 | 319.3241 | 314.7885 | 343.7128
1572.1917 | 319.7198 | 314.9708 | 343.9499
1573.1917 | 319.9866 | 315.5664 | 343.6071
1574.1917 | 320.4399 | 316.3911 | 346.6685
1575.1917 | 320.7673 | 317.1296 | 348.0012
1576.1917 | 320.9805 | 317.9773 | 348.8746
1577.1917 | 321.1172 | 318.7367 | 348.922
1578.1917 | 322.8815 | 319.5439 | 349.0843
1579.1917 | 322.8808 | 319.3729 | 349.0906
1580.1917 | 322.6238 | 319.0881 | 349.0328
1581.1917 | 322.8024 | 319.1386 | 348.9047
1582.1917 | 323.5109 | 319.219 | 351.0824
1583.1917 | 324.0239 | 318.9418 | 351.2573
1584.1917 | 324.3933 | 319.1875 | 351.5833
1585.1917 | 324.9083 | 318.8771 | 352.753
1586.1917 | 325.9707 | 318.5208 | 352.821
1587.1917 | 326.1551 | 318.4933 | 355.0307
1588.1917 | 326.4413 | 320.4683 | 355.2602
1589.1917 | 327.2432 | 320.8736 | 357.9089
1590.1917 | 327.6839 | 321.3524 | 359.0909
1591.1917 | 328.5917 | 321.8496 | 359.8266
1592.1917 | 328.8328 | 322.3517 | 361.2445
1593.1917 | 328.8708 | 322.8796 | 361.698
1594.1917 | 328.6126 | 323.0792 | 362.2397
1595.1917 | 328.3467 | 323.1118 | 361.8796
1596.1917 | 327.8951 | 323.4538 | 361.9659
1597.1917 | 328.0677 | 323.8005 | 362.7092
1598.1917 | 328.2505 | 324.3321 | 363.5882
1599.1917 | 328.6431 | 326.2046 | 365.2839
1600.1917 | 330.0165 | 327.18 | 367.0121
1601.1917 | 329.9832 | 327.4689 | 368.8297
1602.1917 | 330.2587 | 327.9829 | 369.3034
1603.1917 | 330.0734 | 328.7642 | 369.4649
1604.1917 | 330.2984 | 329.4451 | 369.4378
1605.1917 | 330.9473 | 329.6269 | 369.2993
1606.1917 | 331.6327 | 330.6168 | 368.7484
1607.1917 | 331.9913 | 330.3189 | 368.8027
1608.1917 | 332.5704 | 329.9044 | 369.4858
1609.1917 | 333.0212 | 330.4334 | 369.3669
1610.1917 | 333.951 | 330.8439 | 371.0108
1611.1917 | 334.6483 | 331.0125 | 371.0259
1612.1917 | 335.059 | 331.4218 | 370.9995
1613.1917 | 335.4386 | 331.0839 | 370.5395
1614.1917 | 335.8359 | 331.0598 | 370.9961
1615.1917 | 335.8394 | 331.3518 | 370.6641
1616.1917 | 335.5372 | 331.252 | 370.1328
1617.1917 | 335.5869 | 331.0438 | 372.3029
1618.1917 | 335.7415 | 330.6572 | 372.3513
1619.1917 | 335.7857 | 330.3406 | 372.9323
1620.1917 | 335.3452 | 330.3151 | 373.7121
1621.1917 | 335.4855 | 330.4186 | 374.1119
1622.1917 | 335.9122 | 331.0066 | 373.3916
1623.1917 | 336.1109 | 331.6972 | 374.9694
1624.1917 | 336.2408 | 332.4793 | 374.9377
1625.1917 | 336.553 | 333.3024 | 375.1625
1626.1917 | 336.6304 | 333.2943 | 376.2149
1627.1917 | 336.3525 | 333.3117 | 375.2295
1628.1917 | 336.1705 | 333.5672 | 374.6213
1629.1917 | 336.4875 | 333.4415 | 375.5239
1630.1917 | 336.9 | 333.2746 | 376.2069
1631.1917 | 336.8152 | 334.7461 | 375.5967
1632.1917 | 336.2647 | 333.9507 | 376.6633
1633.1917 | 336.7563 | 333.5816 | 375.8983
1634.1917 | 337.2728 | 334.0756 | 375.8832
1635.1917 | 337.6321 | 334.2145 | 375.7171
1636.1917 | 337.9297 | 334.7952 | 376.3997
1637.1917 | 338.5379 | 334.9495 | 377.5573
1638.1917 | 339.1754 | 335.3072 | 378.3655
1639.1917 | 339.82 | 335.6011 | 379.6039
1640.1917 | 340.6374 | 335.9998 | 380.4542
1641.1917 | 341.6622 | 335.8053 | 380.0754
1642.1917 | 342.7529 | 336.2191 | 380.7706
1643.1917 | 343.6681 | 335.8577 | 380.8866
1644.1917 | 344.602 | 335.9674 | 380.5202
1645.1917 | 344.8487 | 336.3764 | 381.3534
1646.1917 | 344.4457 | 336.3269 | 382.422
1647.1917 | 344.4098 | 336.607 | 383.7472
1648.1917 | 345.0705 | 336.3482 | 383.2759
1649.1917 | 344.7714 | 336.0482 | 384.9596
1650.1917 | 344.6656 | 336.6593 | 386.5465
1651.1917 | 344.7172 | 339.3978 | 386.7594
1652.1917 | 345.3388 | 339.6195 | 387.7617
1653.1917 | 345.5314 | 340.3039 | 388.7899
1654.1917 | 346.4786 | 340.51 | 387.7624
1655.1917 | 347.0064 | 341.302 | 387.0594
1656.1917 | 347.2121 | 341.9344 | 386.5775
1657.1917 | 347.1662 | 342.145 | 386.0886
1658.1917 | 346.7936 | 342.3074 | 385.5414
1659.1917 | 346.6708 | 343.1605 | 384.6706
1660.1917 | 347.158 | 343.2959 | 384.6167
1661.1917 | 347.6199 | 343.6254 | 385.1834
1662.1917 | 347.9256 | 344.7357 | 387.1605
1663.1917 | 348.4701 | 345.5541 | 388.7111
1664.1917 | 348.9817 | 345.8587 | 389.9188
1665.1917 | 349.5216 | 346.7367 | 391.4365
1666.1917 | 349.7964 | 347.3206 | 391.317
1667.1917 | 350.0721 | 348.1923 | 391.4101
1668.1917 | 350.8239 | 348.4508 | 391.963
1669.1917 | 351.2187 | 348.4528 | 391.5488
1670.1917 | 352.0092 | 348.5358 | 393.0148
1671.1917 | 352.6485 | 348.8487 | 394.1331
1672.1917 | 353.8731 | 349.7904 | 396.7884
1673.1917 | 355.1648 | 351.7054 | 398.4385
1674.1917 | 356.2799 | 353.1756 | 398.0491
1675.1917 | 356.9908 | 355.4867 | 398.4068
1676.1917 | 357.4375 | 355.9338 | 398.6502
1677.1917 | 358.0899 | 356.2587 | 401.0597
1678.1917 | 359.1305 | 357.0075 | 402.552
1679.1917 | 359.4415 | 358.3205 | 404.8887
1680.1917 | 360.0348 | 358.7402 | 403.8976
1681.1917 | 361.3017 | 358.781 | 404.256
1682.1917 | 361.9514 | 359.4662 | 403.4885
1683.1917 | 362.4778 | 359.3982 | 403.8059
1684.1917 | 363.9732 | 359.9678 | 403.7668
1685.1917 | 363.5955 | 360.1884 | 404.6893
1686.1917 | 363.6857 | 360.0343 | 406.2964
1687.1917 | 363.2228 | 359.8846 | 407.3269
1688.1917 | 362.8057 | 360.3962 | 408.5217
1689.1917 | 362.3617 | 360.0086 | 407.3963
1690.1917 | 362.265 | 359.8832 | 407.7087
1691.1917 | 362.3215 | 359.676 | 407.5973
1692.1917 | 362.4026 | 359.0022 | 407.3478
1693.1917 | 362.1965 | 358.7199 | 408.0708
1694.1917 | 361.8351 | 359.4202 | 408.5878
1695.1917 | 361.6969 | 359.4115 | 409.2506
1696.1917 | 361.4557 | 359.8261 | 409.9202
1697.1917 | 361.8359 | 361.515 | 410.5785
1698.1917 | 362.1413 | 361.5738 | 411.009
1699.1917 | 362.7303 | 362.0026 | 411.7942
1700.1917 | 362.5968 | 362.2766 | 410.2134
1701.1917 | 362.763 | 362.0249 | 409.335
1702.1917 | 362.7444 | 361.7013 | 408.8193
1703.1917 | 363.9684 | 361.6753 | 407.8548
1704.1917 | 364.8636 | 361.2543 | 408.5842
1705.1917 | 366.1538 | 361.4844 | 408.3535
1706.1917 | 366.7609 | 361.6803 | 408.5833
1707.1917 | 367.5452 | 360.9627 | 408.5653
1708.1917 | 368.0686 | 360.1341 | 408.162
1709.1917 | 368.4587 | 360.9977 | 408.811
1710.1917 | 369.0067 | 361.1859 | 408.3027
1711.1917 | 368.8673 | 361.5073 | 407.9422
1712.1917 | 369.0152 | 361.9203 | 407.4774
1713.1917 | 368.9841 | 361.9022 | 406.8342
1714.1917 | 368.6509 | 362.3948 | 406.3444
1715.1917 | 368.2772 | 362.6153 | 405.4319
1716.1917 | 368.2434 | 362.5774 | 404.3176
1717.1917 | 368.5774 | 362.4675 | 404.3509
1718.1917 | 368.6505 | 362.7382 | 404.2376
1719.1917 | 368.9502 | 363.6008 | 402.9554
1720.1917 | 369.3743 | 364.3463 | 402.4317
1721.1917 | 370.0955 | 364.8079 | 402.4649
1722.1917 | 370.2562 | 364.9796 | 401.7852
1723.1917 | 370.4302 | 365.1675 | 401.8623
1724.1917 | 372.1635 | 365.3197 | 403.0591
1725.1917 | 372.0656 | 365.3206 | 402.2406
1726.1917 | 371.89 | 366.3086 | 401.7067
1727.1917 | 371.572 | 367.3444 | 401.9087
1728.1917 | 371.5815 | 367.1709 | 402.3362
1729.1917 | 371.3144 | 367.0163 | 403.5303
1730.1917 | 371.3471 | 366.8865 | 403.6225
1731.1917 | 371.2147 | 366.6825 | 404.3743
1732.1917 | 371.6735 | 367.4249 | 406.515
1733.1917 | 372.4553 | 368.263 | 407.4741
1734.1917 | 373.1391 | 369.8067 | 408.7706
1735.1917 | 373.2329 | 372.0403 | 409.2316
1736.1917 | 373.2148 | 371.8825 | 408.435
1737.1917 | 372.7424 | 371.932 | 408.8372
1738.1917 | 372.3296 | 371.9801 | 408.2392
1739.1917 | 372.2387 | 371.7759 | 408.8974
1740.1917 | 371.9421 | 371.6178 | 408.2096
1741.1917 | 371.676 | 371.2794 | 407.8108
1742.1917 | 371.6358 | 371.0338 | 408.7627
1743.1917 | 372.4647 | 371.4905 | 410.0185
1744.1917 | 373.3131 | 371.7227 | 409.5408
1745.1917 | 373.9913 | 372.4991 | 409.5178
1746.1917 | 373.881 | 372.6411 | 409.2094
1747.1917 | 374.1149 | 372.6817 | 409.0584
1748.1917 | 374.1042 | 373.2472 | 408.8124
1749.1917 | 374.7954 | 373.7741 | 409.279
1750.1917 | 375.0927 | 373.5732 | 411.7656
1751.1917 | 374.9662 | 373.444 | 412.4769
1752.1917 | 374.8914 | 372.9467 | 412.1607
1753.1917 | 374.9078 | 373.0182 | 412.1293
1754.1917 | 375.2081 | 373.3861 | 412.2927
1755.1917 | 374.8102 | 372.9546 | 411.8111
1756.1917 | 374.5649 | 372.9312 | 412.914
1757.1917 | 374.4644 | 372.6354 | 413.8954
1758.1917 | 375.0681 | 372.3968 | 415.03
1759.1917 | 375.2262 | 372.4079 | 415.1043
1760.1917 | 375.4706 | 372.7168 | 416.6772
1761.1917 | 375.7766 | 373.2662 | 418.1144
1762.1917 | 376.2431 | 374.1772 | 417.9228
1763.1917 | 377.0386 | 374.4856 | 419.8675
1764.1917 | 376.8081 | 374.6208 | 420.9695
1765.1917 | 376.9799 | 374.8287 | 422.0909
1766.1917 | 377.4624 | 375.2946 | 422.4393
1767.1917 | 378.3751 | 375.9905 | 422.9271
1768.1917 | 378.7009 | 376.6662 | 423.2812
1769.1917 | 379.1557 | 376.7307 | 422.5768
1770.1917 | 380.3075 | 376.8901 | 422.444
1771.1917 | 381.3546 | 378.7034 | 424.0809
1772.1917 | 382.4375 | 379.1873 | 425.3143
1773.1917 | 383.2153 | 380.1384 | 426.0468
1774.1917 | 383.4797 | 381.5907 | 426.3886
1775.1917 | 384.5512 | 381.7943 | 425.624
1776.1917 | 384.8183 | 382.2649 | 424.709
1777.1917 | 385.4529 | 382.8864 | 425.6242
1778.1917 | 386.1583 | 383.1209 | 425.8076
1779.1917 | 386.4299 | 383.9306 | 425.6101
1780.1917 | 386.8064 | 384.1247 | 425.8317
1781.1917 | 387.3313 | 383.8181 | 426.9189
1782.1917 | 387.4663 | 383.9301 | 426.8933
1783.1917 | 387.3531 | 383.6857 | 426.5171
1784.1917 | 387.4001 | 383.3553 | 425.1609
1785.1917 | 387.3557 | 383.2791 | 425.8036
1786.1917 | 387.9749 | 383.8858 | 426.2177
1787.1917 | 388.9598 | 383.9283 | 428.0718
1788.1917 | 388.9165 | 383.706 | 428.3928
1789.1917 | 389.7755 | 383.9997 | 429.754
1790.1917 | 391.2612 | 385.4478 | 430.1962
1791.1917 | 391.9737 | 386.1354 | 429.6542
1792.1917 | 392.2935 | 386.0425 | 429.1787
1793.1917 | 393.3636 | 386.2058 | 428.8748
1794.1917 | 393.6797 | 385.9383 | 430.303
1795.1917 | 394.115 | 386.5286 | 430.5446
1796.1917 | 394.4411 | 387.5893 | 432.7437
1797.1917 | 395.2429 | 387.7794 | 433.6523
1798.1917 | 395.3401 | 387.8861 | 434.6677
1799.1917 | 395.934 | 387.9712 | 434.3475
1800.1917 | 396.888 | 387.8752 | 433.6529
1801.1917 | 397.6893 | 388.0223 | 434.7013
1802.1917 | 398.1753 | 387.4675 | 434.3891
1803.1917 | 398.9036 | 387.9165 | 435.0552
1804.1917 | 400.0017 | 388.9202 | 435.9188
1805.1917 | 400.2469 | 389.3186 | 436.0784
1806.1917 | 400.1881 | 389.0781 | 435.907
1807.1917 | 401.0147 | 389.9677 | 436.5274
1808.1917 | 401.8336 | 390.6673 | 437.8242
1809.1917 | 402.0223 | 391.6921 | 437.546
1810.1917 | 402.1744 | 391.7312 | 439.0165
1811.1917 | 402.4461 | 392.3703 | 438.2358
1812.1917 | 403.2042 | 393.2353 | 438.2636
1813.1917 | 403.644 | 394.1267 | 439.1109
1814.1917 | 403.871 | 394.5956 | 439.3658
1815.1917 | 404.6875 | 395.3794 | 439.6516
1816.1917 | 405.1978 | 395.8987 | 441.2292
1817.1917 | 406.1754 | 395.7814 | 440.9403
1818.1917 | 407.1016 | 395.5969 | 441.3002
1819.1917 | 407.5997 | 396.0861 | 440.7901
1820.1917 | 407.824 | 395.8506 | 440.9882
1821.1917 | 408.0642 | 396.1174 | 440.2707
1822.1917 | 407.9005 | 396.2928 | 439.252
1823.1917 | 408.2213 | 396.8364 | 439.6194
1824.1917 | 408.2 | 396.7049 | 439.4075
1825.1917 | 408.3944 | 397.1245 | 438.3093
1826.1917 | 408.341 | 397.2723 | 437.7807
1827.1917 | 408.3964 | 397.5568 | 437.9878
1828.1917 | 407.978 | 397.7689 | 438.0323
1829.1917 | 407.7118 | 397.9051 | 438.3844
1830.1917 | 407.5361 | 397.486 | 436.5744
1831.1917 | 407.9021 | 397.206 | 435.8366
1832.1917 | 407.8034 | 396.7961 | 435.3706
1833.1917 | 408.0306 | 396.7952 | 434.8961
1834.1917 | 407.6613 | 396.5608 | 434.9914
1835.1917 | 407.6904 | 396.3464 | 433.7937
1836.1917 | 407.0824 | 396.1294 | 433.1653
1837.1917 | 406.3993 | 395.5474 | 432.3127
1838.1917 | 406.2107 | 394.7826 | 430.5496
1839.1917 | 405.3911 | 394.2687 | 429.624
1840.1917 | 405.7528 | 394.4782 | 428.9811
1841.1917 | 405.3902 | 394.4444 | 427.7376
1842.1917 | 405.1463 | 394.0988 | 427.3958
1843.1917 | 405.236 | 393.5775 | 428.7074
1844.1917 | 405.5705 | 393.4955 | 429.5139
1845.1917 | 405.8461 | 393.5996 | 429.5853
1846.1917 | 406.5601 | 393.7769 | 430.2081
1847.1917 | 407.1322 | 394.0958 | 430.7832
1848.1917 | 408.1836 | 394.39 | 432.5791
1849.1917 | 408.4169 | 394.9021 | 433.7
1850.1917 | 409.1036 | 395.0186 | 433.7066
1851.1917 | 409.1926 | 396.1855 | 435.1787
1852.1917 | 409.8761 | 396.5867 | 435.3775
1853.1917 | 410.0649 | 396.8688 | 435.8569
1854.1917 | 409.9594 | 397.1481 | 436.4079
1855.1917 | 410.18 | 397.7869 | 437.341
1856.1917 | 410.555 | 399.9535 | 438.8991
1857.1917 | 411.1367 | 400.1173 | 439.5653
1858.1917 | 411.0473 | 400.134 | 439.7965
1859.1917 | 411.9372 | 400.0317 | 440.8027
1860.1917 | 412.2384 | 400.1804 | 441.2435
1861.2073 | 411.6654 | 399.9552 | 440.4336
1862.1917 | 411.7343 | 399.8757 | 441.9978
1863.2073 | 411.7502 | 399.6661 | 441.5138
1864.1917 | 412.3984 | 401.67 | 442.2059
1865.1917 | 412.747 | 402.2271 | 441.967
1866.1917 | 413.4047 | 403.3653 | 444.3984
1867.1917 | 414.9584 | 404.5882 | 444.9061
1868.1917 | 415.8486 | 405.6717 | 444.4731
1869.1917 | 416.0099 | 405.9557 | 444.5066
1870.1917 | 416.2413 | 406.4111 | 444.9788
1871.1917 | 416.2972 | 406.3416 | 444.2435
1872.1917 | 416.0065 | 405.8418 | 444.1104
1873.1917 | 415.5602 | 406.1362 | 443.3252
1874.1917 | 415.8047 | 405.899 | 444.2624
1875.1917 | 415.9927 | 405.8789 | 443.2431
1876.1917 | 417.1338 | 406.0469 | 443.877
1877.1917 | 418.4185 | 406.6978 | 444.1143
1878.1917 | 419.4314 | 408.0452 | 445.2059
1879.1917 | 419.3832 | 408.9592 | 446.309
1880.1917 | 419.7842 | 409.6198 | 446.379
1881.1917 | 418.9832 | 409.4213 | 445.0866
1882.1917 | 418.6728 | 408.7434 | 443.1782
1883.1917 | 417.7231 | 408.2674 | 442.4603
1884.1917 | 417.1724 | 408.3958 | 441.6999
1885.1917 | 416.9168 | 408.4469 | 442.6005
1886.1917 | 416.7389 | 408.3957 | 443.2339
1887.1917 | 416.8209 | 408.4818 | 445.3346
1888.1917 | 417.0585 | 408.9909 | 446.1676
1889.1917 | 417.5778 | 409.184 | 446.4027
1890.1917 | 417.3654 | 409.1551 | 446.8197
1891.1917 | 417.9643 | 409.9334 | 447.3535
1892.1917 | 418.7338 | 410.1767 | 447.5289
1893.1917 | 418.7744 | 409.9274 | 447.1027
1894.1917 | 418.9817 | 409.4918 | 446.6323
1895.1917 | 419.5074 | 409.2729 | 447.733
1896.1917 | 419.7007 | 409.1833 | 448.3535
1897.1917 | 419.9064 | 409.1273 | 448.9925
1898.1917 | 421.1015 | 409.0153 | 448.7324
1899.1917 | 421.4876 | 409.7174 | 450.0482
1900.1917 | 421.6536 | 410.5228 | 450.6841
1901.1917 | 421.3711 | 411.4915 | 452.7559
1902.1917 | 422.01 | 412.0994 | 452.4269
1903.1917 | 422.4331 | 412.8112 | 453.4314
1904.1917 | 422.2926 | 413.1907 | 453.6346
1905.1917 | 422.5696 | 413.769 | 453.7386
1906.1917 | 422.4248 | 413.9821 | 454.5998
1907.1917 | 423.9119 | 414.6005 | 454.3798
1908.1917 | 423.7437 | 414.9292 | 455.3021
1909.1917 | 423.5132 | 415.5266 | 454.9851
1910.1917 | 423.7849 | 415.8804 | 456.1563
1911.1917 | 424.2293 | 415.9159 | 454.8473
1912.1917 | 423.8041 | 416.2048 | 455.2285
1913.1917 | 424.0775 | 415.6472 | 454.8194
1914.1917 | 424.0747 | 415.3838 | 453.4384
1915.1917 | 424.1873 | 415.3649 | 452.7997
1916.1917 | 423.6607 | 415.1687 | 451.9391
1917.1917 | 423.652 | 414.9424 | 450.9554
1918.1917 | 423.191 | 414.4147 | 450.931
1919.1917 | 423.0165 | 413.6599 | 450.1992
1920.1917 | 422.9255 | 413.087 | 449.4645
1921.1917 | 423.5758 | 413.3825 | 449.8152
1922.1917 | 423.4739 | 412.8177 | 448.5904
1923.1917 | 423.2077 | 412.9337 | 448.6998
1924.1917 | 422.7294 | 412.2114 | 448.8128
1925.1917 | 423.0441 | 412.1829 | 447.4611
1926.1917 | 423.2763 | 412.3414 | 446.7868
1927.1917 | 423.2436 | 412.0072 | 447.4439
1928.1917 | 422.9811 | 412.6696 | 448.1458
1929.1917 | 422.6799 | 413.5753 | 448.78
1930.1917 | 422.7117 | 414.3371 | 449.1594
1931.1917 | 423.3703 | 415.6009 | 451.5121
1932.1917 | 423.866 | 416.6983 | 452.3404
1933.1917 | 424.9993 | 417.5645 | 452.3017
1934.1917 | 424.324 | 418.0854 | 452.3395
1935.1917 | 424.222 | 417.8238 | 452.3415
1936.1917 | 423.7629 | 417.2317 | 451.2169
1937.1917 | 423.8529 | 416.6115 | 450.3919
1938.1917 | 424.8611 | 416.4642 | 450.1504
1939.1917 | 425.072 | 416.3271 | 450.7011
1940.1917 | 425.5077 | 418.1448 | 451.6213
1941.1917 | 426.5175 | 418.7551 | 452.0823
1942.1917 | 426.5398 | 418.5824 | 453.0706
1943.1917 | 426.5031 | 419.4885 | 452.6704
1944.1917 | 426.3248 | 419.8677 | 452.9112
1945.1917 | 425.8734 | 419.9991 | 452.0599
1946.1917 | 425.1602 | 419.8408 | 452.4362
1947.1917 | 424.8247 | 419.8042 | 452.7444
1948.1917 | 424.824 | 419.4785 | 454.1224
1949.1917 | 425.34 | 420.4634 | 455.1167
1950.1917 | 425.4867 | 421.0658 | 456.0094
1951.1917 | 425.9402 | 421.1438 | 455.9233
1952.1917 | 425.943 | 421.4742 | 455.178
1953.1917 | 426.3568 | 421.7877 | 455.4822
1954.1917 | 426.6738 | 422.3239 | 454.4487
1955.1917 | 427.5519 | 423.1019 | 456.6053
1956.1917 | 428.5791 | 422.7523 | 455.5086
1957.1917 | 428.7019 | 422.0562 | 455.4531
1958.1917 | 428.8282 | 421.5104 | 455.0677
1959.1917 | 429.2728 | 420.9043 | 455.6341
1960.1917 | 429.9348 | 421.4409 | 457.3803
1961.1917 | 430.2716 | 422.6427 | 459.6494
1962.1917 | 431.2517 | 423.6203 | 459.6512
1963.2073 | 431.5721 | 423.8032 | 458.959
1964.1917 | 432.007 | 424.5065 | 459.3728
1965.1917 | 432.8289 | 424.4851 | 458.9988
1966.1917 | 433.6603 | 424.1132 | 458.1417
1967.1917 | 434.5579 | 425.0683 | 459.7118
1968.1917 | 435.3785 | 425.4253 | 459.5916
1969.1917 | 436.3505 | 426.6553 | 460.7115
1970.1917 | 437.5346 | 427.9914 | 462.1353
1971.1917 | 437.94 | 428.3096 | 462.1345
1972.1917 | 437.7418 | 427.8977 | 461.1927
1973.1917 | 438.5861 | 427.6153 | 461.9093
1974.1917 | 438.5268 | 427.2168 | 461.1928
1975.1917 | 438.5654 | 426.751 | 461.0496
1976.1917 | 438.4206 | 426.7737 | 461.7124
1977.1917 | 439.0656 | 427.1252 | 461.8657
1978.1917 | 439.3671 | 426.1707 | 461.3428
1979.1917 | 439.3642 | 425.4985 | 461.6978
1980.1917 | 439.6439 | 425.3336 | 461.888
1981.1917 | 439.9352 | 425.3203 | 461.7726
1982.1917 | 440.8529 | 425.7982 | 462.3725
1983.1917 | 441.9372 | 425.8236 | 462.8387
1984.1917 | 442.8355 | 426.3657 | 463.2845
1985.1917 | 443.583 | 426.8135 | 465.3509
1986.1917 | 444.1346 | 428.1335 | 465.4368
1987.1917 | 444.5705 | 429.7513 | 466.8109
1988.1917 | 444.3422 | 430.0786 | 465.422
1989.1917 | 443.9845 | 430.4117 | 464.4591
1990.1917 | 443.6386 | 430.6314 | 463.4131
1991.1917 | 442.9119 | 430.3986 | 462.1999
1992.1917 | 441.9979 | 429.9454 | 461.6196
1993.2073 | 441.3069 | 429.6038 | 461.511
1994.1917 | 440.8236 | 429.6233 | 461.0764
1995.1917 | 440.7937 | 430.1215 | 461.9064
1996.1917 | 441.0741 | 430.6907 | 463.7296
1997.1917 | 441.6186 | 430.79 | 464.2579
1998.1917 | 441.8726 | 431.2783 | 465.6196
1999.1917 | 442.1081 | 431.391 | 466.1817
2000.1917 | 441.3546 | 431.3931 | 465.7164
2001.1917 | 441.6875 | 431.2348 | 465.725
2002.1917 | 441.5651 | 430.7185 | 465.5653
2003.1917 | 441.507 | 430.5485 | 465.9447
2004.1917 | 441.6976 | 430.2966 | 465.546
2005.1917 | 441.3681 | 429.8157 | 464.4479
2006.1917 | 440.8759 | 429.0277 | 463.3657
2007.1917 | 440.1766 | 428.5494 | 461.2143
2008.1917 | 440.2814 | 428.3309 | 461.2068
2009.1917 | 439.988 | 428.3756 | 461.7206
2010.1917 | 440.0907 | 428.0055 | 462.4665
2011.1917 | 439.9759 | 427.4543 | 461.8625
2012.1917 | 440.1299 | 426.8274 | 461.1835
2013.1917 | 439.8671 | 426.6215 | 461.3032
2014.1917 | 439.951 | 426.9792 | 462.3807
2015.1917 | 440.4401 | 427.6078 | 462.1493
2016.1917 | 441.8107 | 428.4768 | 462.9496
2017.1917 | 442.5624 | 429.2516 | 463.9891
2018.1917 | 442.8341 | 429.6558 | 464.1099
2019.1917 | 444.1697 | 430.1466 | 464.3628
2020.1917 | 444.3719 | 429.9 | 464.5758
2021.1917 | 444.5955 | 429.851 | 465.2773
2022.1917 | 444.5816 | 429.5057 | 464.5444
2023.2073 | 444.9598 | 429.4178 | 464.5604
2024.1917 | 444.9351 | 429.6949 | 465.5153
2025.1917 | 444.7733 | 430.8914 | 465.1124
2026.1917 | 445.0744 | 431.5323 | 465.7349
2027.1917 | 446.0535 | 432.3203 | 465.9328
2028.1917 | 446.534 | 432.8174 | 466.9694
2029.1917 | 447.4357 | 433.3637 | 468.9585
2030.1917 | 448.0492 | 434.0609 | 468.462
2031.1917 | 448.0843 | 433.8335 | 468.3216
2032.1917 | 448.2767 | 433.4938 | 467.6523
2033.1917 | 448.9525 | 433.9964 | 468.1469
2034.1917 | 449.0959 | 434.6835 | 467.5054
2035.1917 | 449.3284 | 434.3622 | 466.2047
2036.1917 | 449.1493 | 434.8325 | 465.406
2037.1917 | 449.6591 | 435.4279 | 464.6855
2038.1917 | 450.5636 | 435.9398 | 464.8615
2039.1917 | 450.553 | 436.4167 | 464.1072
2040.1917 | 450.5095 | 437.2938 | 463.7582
2041.1917 | 450.6226 | 436.7468 | 462.8523
2042.1917 | 450.4926 | 436.0328 | 461.3965
2043.1917 | 450.365 | 435.6354 | 460.6079
2044.1917 | 450.6786 | 435.1073 | 460.7506
2045.1917 | 450.2679 | 435.131 | 460.1583
2046.1917 | 450.3617 | 435.059 | 459.2667
2047.1917 | 450.5611 | 434.7685 | 457.9275
2048.1917 | 450.45 | 434.9633 | 458.2194
2049.1917 | 450.7406 | 434.6947 | 457.8931
2050.1917 | 450.1297 | 434.3612 | 457.269
2051.1917 | 449.83 | 433.8524 | 457.2014
2052.1917 | 449.2513 | 433.4339 | 457.1606
2053.1917 | 448.8951 | 433.2253 | 456.2848
2054.1917 | 449.3285 | 432.9506 | 455.3649
2055.1917 | 449.7424 | 433.4339 | 456.3887
2056.1917 | 450.9938 | 434.149 | 457.4824
2057.1917 | 451.6596 | 434.1938 | 457.1431
2058.1917 | 452.6704 | 435.6387 | 457.4253
2059.1917 | 452.8935 | 436.0141 | 456.4852
2060.1917 | 452.6618 | 435.5804 | 455.6529
2061.1917 | 452.3023 | 435.17 | 455.153
2062.1917 | 452.2937 | 434.8658 | 454.7744
2063.1917 | 452.3599 | 435.6325 | 455.0673
2064.1917 | 453.8759 | 437.5502 | 457.5082
2065.1917 | 455.9995 | 438.1753 | 458.2882
2066.1917 | 457.0881 | 438.2 | 457.5819
2067.1917 | 457.6338 | 438.6774 | 457.9833
2068.1917 | 458.4491 | 439.6256 | 458.2791
2069.1917 | 458.7422 | 440.2334 | 458.697
2070.1917 | 458.6548 | 441.0753 | 459.4441
2071.1917 | 458.7724 | 441.6113 | 461.7775
2072.1917 | 459.5058 | 443.127 | 464.6797
2073.1917 | 459.5589 | 443.3261 | 464.0544
2074.1917 | 458.9099 | 443.1689 | 463.4198
2075.1917 | 458.2663 | 442.7235 | 463.5411
2076.1917 | 457.4542 | 442.2402 | 463.3525
2077.1917 | 457.002 | 441.6775 | 463.3506
2078.1917 | 456.2984 | 441.3198 | 463.0136
2079.1917 | 455.9658 | 440.6617 | 463.3241
2080.1917 | 456.1578 | 441.4056 | 463.8655
2081.1917 | 456.278 | 441.9735 | 466.6334
2082.2073 | 456.1985 | 442.7065 | 469.7697
2083.2073 | 455.9629 | 442.21 | 468.8096
2084.1917 | 455.7607 | 441.5395 | 468.1148
2085.1917 | 455.5449 | 441.4497 | 468.4322
2086.2073 | 455.1525 | 441.3299 | 468.1622
2087.1917 | 454.9401 | 440.884 | 468.1479
2088.2073 | 454.5548 | 440.4382 | 467.6911
2089.1917 | 455 | 440.2465 | 467.4679
2090.1917 | 455.9065 | 440.4888 | 468.1178
2091.1917 | 455.3453 | 441.1428 | 467.8258
2092.1917 | 456.4181 | 441.6858 | 467.3997
2093.1917 | 456.1374 | 441.8343 | 466.8663
2094.1917 | 455.6225 | 441.5781 | 465.4751
2095.1917 | 455.4992 | 442.498 | 465.3494
2096.1917 | 455.572 | 442.8805 | 465.1169
2097.1917 | 455.2566 | 442.5412 | 464.7449
2098.1917 | 455.1391 | 442.5187 | 464.7145
2099.1917 | 455.4326 | 442.536 | 465.3857
2100.1917 | 455.6336 | 443.8885 | 465.7184
2101.1917 | 455.6292 | 444.5881 | 466.4309
2102.1917 | 455.7897 | 445.5489 | 466.9071
2103.1917 | 456.6001 | 445.4322 | 466.7719
2104.1917 | 456.6591 | 445.3064 | 467.9358
2105.1917 | 456.5388 | 444.978 | 466.7981
2106.1917 | 456.6735 | 444.9594 | 466.1965
2107.1917 | 457.6446 | 445.4214 | 465.5327
2108.1917 | 458.1084 | 445.4115 | 465.2201
2109.1917 | 458.2699 | 445.3837 | 465.1894
2110.1917 | 458.0744 | 444.6583 | 464.7214
2111.1917 | 458.0186 | 444.0897 | 464.2605
2112.1917 | 458.1686 | 444.3217 | 463.8133
2113.2073 | 458.1324 | 445.4591 | 463.9717
2114.1917 | 459.3462 | 445.4802 | 463.8642
2115.1917 | 459.0946 | 445.8429 | 462.8973
2116.1917 | 458.9241 | 445.5199 | 462.933
2117.1917 | 458.6205 | 445.2666 | 463.3072
2118.1917 | 458.1232 | 445.5336 | 462.9983
2119.1917 | 457.527 | 445.3685 | 461.7656
2120.1917 | 457.8265 | 446.305 | 461.5941
2121.1917 | 458.0822 | 446.2158 | 461.134
2122.1917 | 458.471 | 445.9101 | 461.4407
2123.1917 | 458.2292 | 446.6649 | 461.8184
2124.1917 | 458.3721 | 446.969 | 462.203
2125.1917 | 458.5025 | 447.1147 | 461.6083
2126.1917 | 459.0258 | 446.8629 | 461.1894
2127.1917 | 458.9635 | 446.5177 | 461.537
2128.1917 | 459.2027 | 446.2158 | 462.0767
2129.1917 | 459.2532 | 445.7302 | 463.1616
2130.1917 | 459.0128 | 446.5308 | 462.4411
2131.1917 | 459.1753 | 446.3466 | 462.6444
2132.1917 | 458.7485 | 447.2562 | 462.5266
2133.2073 | 458.8126 | 447.4623 | 461.687
2134.1917 | 459.6067 | 447.4662 | 461.8543
2135.1917 | 459.913 | 448.2454 | 463.0413
2136.1917 | 460.5375 | 449.7035 | 464.1762
2137.1917 | 460.9768 | 450.1763 | 467.2568
2138.1917 | 460.949 | 450.2162 | 468.2756
2139.1917 | 460.5483 | 450.0127 | 468.8545
2140.1917 | 461.4305 | 451.4924 | 469.5971
2141.1917 | 461.1568 | 451.6471 | 469.0284
2142.1917 | 460.9474 | 451.7373 | 467.9531
2143.2073 | 461.5298 | 451.5921 | 467.6582
2144.1917 | 462.2556 | 451.7607 | 467.9558
2145.1917 | 463.1646 | 452.0919 | 469.449
2146.1917 | 464.0413 | 452.391 | 468.9882
2147.1917 | 464.7526 | 452.8579 | 468.6818
2148.1917 | 465.3656 | 453.4156 | 469.2784
2149.1917 | 465.6444 | 453.5034 | 468.8628
2150.1917 | 465.7974 | 453.8857 | 467.8411
2151.1917 | 466.1537 | 453.6305 | 467.0059
2152.1917 | 466.4293 | 453.151 | 466.2576
2153.1917 | 465.9341 | 452.8698 | 466.9875
2154.1917 | 465.8934 | 454.4435 | 467.1655
2155.1917 | 465.7386 | 454.7939 | 468.5192
2156.1917 | 466.3279 | 455.4794 | 470.2095
2157.1917 | 466.3412 | 454.9412 | 470.5548
2158.1917 | 467.2945 | 456.0212 | 471.9322
2159.1917 | 466.9903 | 456.0846 | 472.3768
2160.1917 | 466.6286 | 455.8005 | 472.6348
2161.1917 | 466.1767 | 455.5747 | 472.482
2162.1917 | 466.0755 | 455.2682 | 471.1665
2163.1917 | 466.2581 | 455.3647 | 470.5034
2164.1917 | 465.9776 | 455.1615 | 470.0381
2165.1917 | 465.9984 | 455.8592 | 470.1331
2166.1917 | 466.0071 | 455.6403 | 469.3295
2167.1917 | 465.5845 | 455.5963 | 468.9832
2168.1917 | 465.044 | 455.6544 | 468.6498
2169.1917 | 464.8189 | 456.7574 | 469.5167
2170.1917 | 466.0188 | 457.7078 | 470.1829
2171.1917 | 465.263 | 458.5197 | 470.4517
2172.1917 | 465.4106 | 458.3244 | 470.3355
2173.1917 | 465.0174 | 458.2144 | 470.8269
2174.1917 | 464.5236 | 457.825 | 470.9046
2175.1917 | 464.2058 | 457.6163 | 470.325
2176.1917 | 464.7199 | 457.273 | 470.2075
2177.1917 | 465.2739 | 456.6948 | 470.0323
2178.1917 | 465.6863 | 456.4044 | 469.531
2179.1917 | 466.3724 | 456.3552 | 469.2955
2180.1917 | 466.5532 | 456.027 | 469.5445
2181.1917 | 466.6583 | 455.919 | 470.569
2182.1917 | 467.2426 | 456.2585 | 472.5603
2183.1917 | 467.3479 | 456.8339 | 473.6813
2184.1917 | 468.4321 | 456.923 | 473.4393
2185.1917 | 468.763 | 456.3475 | 472.8277
2186.1917 | 468.867 | 455.9492 | 473.3153
2187.1917 | 469.3821 | 456.2012 | 474.7547
2188.1917 | 470.0157 | 456.4526 | 475.5894
2189.1917 | 470.0719 | 456.2157 | 476.5914
2190.1917 | 470.2102 | 456.5042 | 477.3644
2191.1917 | 471.3171 | 456.6533 | 477.223
2192.1917 | 473.0467 | 457.0764 | 477.1595
2193.1917 | 473.6028 | 457.1031 | 476.6036
2194.1917 | 475.8564 | 457.5206 | 478.1718
2195.1917 | 476.6256 | 458.5856 | 478.0202
2196.1917 | 477.1258 | 459.1894 | 478.0402
2197.1917 | 476.91 | 459.21 | 476.9119
2198.1917 | 476.227 | 459.4939 | 475.7078
2199.1917 | 475.8878 | 459.4747 | 474.664
2200.1917 | 477.0184 | 459.4374 | 474.3988
2201.1917 | 476.9915 | 459.8618 | 475.3596
2202.1917 | 476.9459 | 459.6939 | 474.4467
2203.1917 | 476.6396 | 459.5205 | 474.9259
2204.1917 | 476.2378 | 459.1177 | 475.4243
2205.1917 | 476.2009 | 459.5021 | 474.4519
2206.1917 | 476.4074 | 459.7223 | 473.9737
2207.1917 | 476.934 | 459.7035 | 473.8837
2208.1917 | 476.6482 | 459.3183 | 473.9834
2209.1917 | 477.3443 | 459.4452 | 473.8634
2210.1917 | 477.0886 | 459.201 | 474.3059
2211.1917 | 476.8102 | 460.2167 | 474.7079
2212.1917 | 476.848 | 460.0715 | 474.3098
2213.1917 | 477.1182 | 461.1293 | 475.5939
2214.1917 | 478.0381 | 461.0323 | 475.8458
2215.1917 | 478.1147 | 460.7695 | 475.1273
2216.1917 | 478.3355 | 460.5634 | 474.7792
2217.1917 | 478.1329 | 460.6965 | 474.4333
2218.1917 | 478.3735 | 460.7779 | 473.6806
2219.1917 | 478.0174 | 460.399 | 473.1863
2220.1917 | 478.1074 | 460.5563 | 473.5344
2221.1917 | 478.5306 | 461.0854 | 473.4567
2222.1917 | 479.6083 | 460.9016 | 473.8495
2223.1917 | 480.1842 | 460.8768 | 474.785
2224.1917 | 480.3838 | 460.6448 | 476.2104
2225.1917 | 480.1845 | 460.4383 | 477.3323
2226.1917 | 480.1225 | 461.2901 | 476.9349
2227.1917 | 479.7674 | 461.4481 | 477.026
2228.1917 | 480.1864 | 461.846 | 476.9996
2229.1917 | 481.2347 | 461.851 | 476.7823
2230.1917 | 482.1231 | 462.3068 | 476.5681
2231.1917 | 481.8177 | 462.3774 | 476.3756
2232.1917 | 482.3974 | 462.5273 | 476.6612
2233.2073 | 482.3036 | 462.7653 | 476.6748
2234.1917 | 482.168 | 462.8925 | 477.3346
2235.1917 | 482.1555 | 462.922 | 477.5443
2236.1917 | 482.4159 | 463.3611 | 478.2125
2237.1917 | 482.8191 | 464.0439 | 478.5339
2238.1917 | 483.1818 | 464.0173 | 478.6672
2239.1917 | 483.9583 | 464.7148 | 477.6515
2240.1917 | 484.0693 | 464.5842 | 476.9435
2241.1917 | 484.6882 | 464.0692 | 476.8812
2242.1917 | 484.7664 | 464.2816 | 477.8765
2243.1917 | 484.761 | 465.8113 | 478.1952
2244.1917 | 485.517 | 467.3845 | 478.5354
2245.1917 | 486.247 | 468.2007 | 480.6074
2246.1917 | 486.0338 | 468.6439 | 480.244
2247.1917 | 486.5868 | 468.4439 | 480.2051
2248.1917 | 487.0175 | 467.8493 | 480.0764
2249.1917 | 486.2529 | 467.3478 | 479.1302
2250.1917 | 486.7359 | 466.9484 | 478.6973
2251.1917 | 487.0542 | 466.2663 | 478.7111
2252.1917 | 487.1157 | 466.2595 | 478.453
2253.1917 | 487.4502 | 466.151 | 479.4002
2254.1917 | 487.9634 | 466.0532 | 479.3759
2255.1917 | 488.0302 | 467.1797 | 480.6039
2256.1917 | 488.3376 | 467.233 | 480.3623
2257.1917 | 488.502 | 467.4669 | 482.0332
2258.1917 | 488.3068 | 467.6781 | 482.0796
2259.1917 | 488.3729 | 468.0906 | 482.6847
2260.1917 | 488.0832 | 468.0824 | 483.9758
2261.1917 | 487.9864 | 468.6132 | 483.7439
2262.1917 | 488.3023 | 468.6995 | 483.1835
2263.2073 | 488.1778 | 469.7315 | 483.9111
2264.1917 | 488.1536 | 470.0259 | 483.6408
2265.1917 | 490.1121 | 470.5967 | 483.8227
2266.1917 | 489.6564 | 471.1141 | 483.1204
2267.1917 | 489.0552 | 470.942 | 482.9447
2268.1917 | 488.8628 | 470.8291 | 483.4871
2269.1917 | 488.3411 | 470.0061 | 482.704
2270.1917 | 488.7002 | 469.9217 | 483.0385
2271.1917 | 489.45 | 470.0639 | 483.222
2272.1917 | 490.19 | 470.4213 | 483.2567
2273.1917 | 490.7235 | 470.6385 | 483.588
2274.1917 | 490.8821 | 470.6341 | 483.4663
2275.1917 | 491.1876 | 470.8578 | 483.7161
2276.1917 | 490.7689 | 470.7351 | 483.5272
2277.1917 | 490.5351 | 470.6658 | 483.4033
2278.1917 | 491.9977 | 470.9858 | 485.5546
2279.1917 | 492.8494 | 471.3696 | 485.8078
2280.1917 | 492.9106 | 471.6392 | 486.2438
2281.1917 | 492.6405 | 471.6661 | 486.0158
2282.1917 | 493.3987 | 472.2424 | 485.3788
2283.1917 | 493.6656 | 472.1302 | 484.775
2284.1917 | 493.4584 | 471.7802 | 485.2638
2285.1917 | 493.0463 | 471.4347 | 484.7599
2286.1917 | 493.4716 | 471.3379 | 484.7579
2287.1917 | 493.5988 | 471.2633 | 484.9873
2288.1917 | 494.0973 | 471.3331 | 486.3838
2289.1917 | 494.1672 | 471.4204 | 487.5397
2290.1917 | 493.487 | 470.7911 | 487.1546
2291.1917 | 493.007 | 470.3557 | 487.7332
2292.1917 | 494.1076 | 470.843 | 487.9747
2293.1917 | 494.1919 | 471.3282 | 489.1137
2294.1917 | 494.3242 | 471.4146 | 488.5626
2295.1917 | 494.6156 | 472.0215 | 488.343
2296.1917 | 495.754 | 472.1343 | 488.2888
2297.1917 | 495.8861 | 473.666 | 488.5645
2298.1917 | 497.0453 | 474.7971 | 490.6387
2299.1917 | 497.6391 | 475.8508 | 491.0099
2300.1917 | 497.6538 | 476.2646 | 491.691
2301.1917 | 497.3818 | 476.8166 | 491.8037
2302.1917 | 497.2465 | 477.014 | 492.1763
2303.1917 | 497.0934 | 476.9143 | 491.4345
2304.1917 | 497.9755 | 477.153 | 492.0175
2305.1917 | 498.4767 | 478.3349 | 492.7987
2306.1917 | 499.2836 | 478.97 | 493.603
2307.1917 | 500.0555 | 479.8173 | 494.8464
2308.1917 | 500.7201 | 480.7113 | 494.956
2309.1917 | 501.0964 | 480.7573 | 495.5638
2310.1917 | 500.8596 | 480.4948 | 495.7861
2311.1917 | 500.4157 | 482.1137 | 495.7744
2312.1917 | 500.6829 | 482.0294 | 494.957
2313.2073 | 500.6584 | 481.8446 | 494.373
2314.1917 | 500.5138 | 481.5293 | 494.1572
2315.1917 | 499.8116 | 480.9788 | 493.3385
2316.1917 | 499.9785 | 480.7229 | 492.7789
2317.1917 | 499.7405 | 479.9907 | 492.8169
2318.1917 | 499.1872 | 479.233 | 492.8449
2319.1917 | 498.4631 | 478.5911 | 492.0589
2320.1917 | 498.2283 | 478.0431 | 491.5048
2321.1917 | 499.013 | 477.9546 | 491.3122
2322.1917 | 499.452 | 477.8072 | 492.7042
2323.2073 | 498.8172 | 477.9908 | 492.1388
2324.1917 | 498.8462 | 477.9353 | 491.7975
2325.1917 | 498.5671 | 477.653 | 492.4058
2326.1917 | 498.6434 | 477.6304 | 491.5192
2327.1917 | 497.9602 | 476.8783 | 490.2713
2328.1917 | 497.1875 | 476.4383 | 489.665
2329.1917 | 496.2268 | 475.6323 | 489.0159
2330.1917 | 496.1178 | 475.9102 | 487.5179
2331.1917 | 495.9659 | 475.5767 | 486.7968
2332.1917 | 496.2901 | 475.129 | 486.2745
2333.1917 | 495.6324 | 474.4877 | 486.1986
2334.1917 | 496.1288 | 474.4446 | 486.3399
2335.1917 | 495.7512 | 473.9852 | 486.0686
2336.1917 | 495.195 | 474.3385 | 485.8214
2337.1917 | 494.2427 | 473.7951 | 485.5568
2338.1917 | 494.7823 | 473.7385 | 485.9849
2339.1917 | 495.0606 | 474.0105 | 486.2594
2340.1917 | 494.8351 | 476.0776 | 486.7179
2341.1917 | 495.452 | 475.977 | 486.5118
2342.1917 | 495.5819 | 475.8944 | 486.4548
2343.1917 | 495.561 | 475.7029 | 485.9007
2344.1917 | 495.6612 | 475.031 | 485.6598
2345.1917 | 495.6102 | 474.6949 | 484.9844
2346.1917 | 495.0584 | 473.6994 | 484.2765
2347.1917 | 494.5099 | 473.3371 | 483.9741
2348.1917 | 494.0258 | 472.4202 | 484.1053
2349.1917 | 493.561 | 472.4374 | 485.3376
2350.1917 | 493.1646 | 471.8039 | 486.6743
2351.1917 | 492.7553 | 471.4295 | 487.0561
2352.1917 | 492.5706 | 470.9118 | 486.7015
2353.1917 | 492.1137 | 470.5133 | 486.5306
2354.1917 | 492.3304 | 470.1759 | 486.9592
2355.1917 | 493.1684 | 470.2277 | 487.0556
2356.1917 | 493.9651 | 470.8845 | 487.8818
2357.1917 | 494.4615 | 471.7558 | 488.7379
2358.1917 | 494.1411 | 472.4929 | 489.1039
2359.1917 | 493.7986 | 472.6383 | 489.9323
2360.1917 | 494.2691 | 472.865 | 489.8202
2361.1917 | 494.0151 | 473.0138 | 490.2687
2362.1917 | 494.8784 | 472.8652 | 489.9038
2363.1917 | 494.6664 | 473.613 | 491.0842
2364.1917 | 494.3721 | 474.0315 | 492.3358
2365.1917 | 495.051 | 474.4447 | 492.1645
2366.1917 | 495.5091 | 474.9554 | 492.1863
2367.1917 | 495.4464 | 475.4113 | 492.2138
2368.1917 | 495.6463 | 475.7188 | 491.8883
2369.1917 | 495.3482 | 475.9347 | 491.9265
2370.1917 | 494.9647 | 476.1484 | 492.3591
2371.1917 | 494.8359 | 476.1311 | 492.4283
2372.1917 | 494.7402 | 475.9568 | 491.927
2373.1917 | 494.475 | 475.5565 | 491.4897
2374.1917 | 494.7629 | 475.4698 | 491.665
2375.1917 | 494.3849 | 476.6133 | 491.9655
2376.1917 | 494.6901 | 476.6978 | 493.0818
2377.1917 | 494.8746 | 476.6902 | 492.6682
2378.1917 | 494.9876 | 476.6089 | 492.2288
2379.1917 | 495.7597 | 476.3109 | 492.4281
2380.1917 | 496.9673 | 476.8142 | 493.8724
2381.1917 | 497.1305 | 476.699 | 494.1755
2382.1917 | 498.1198 | 478.2161 | 495.1153
2383.1917 | 498.8573 | 479.4981 | 496.4938
2384.1917 | 498.8813 | 480.0014 | 496.3773
2385.1917 | 498.7228 | 481.1144 | 495.5137
2386.1917 | 498.6893 | 481.6326 | 496.0948
2387.1917 | 498.4786 | 481.6213 | 495.6355
2388.1917 | 497.9325 | 481.3031 | 494.5731
2389.1917 | 497.5104 | 480.9617 | 494.3933
2390.1917 | 497.5452 | 480.7962 | 493.4999
2391.1917 | 498.0694 | 481.2772 | 493.0492
2392.1917 | 500.0486 | 482.0645 | 491.4893
2393.1917 | 500.3691 | 482.1885 | 491.1106
2394.1917 | 500.0569 | 482.0552 | 490.9098
2395.1917 | 500.049 | 482.0958 | 490.343
2396.1917 | 499.686 | 482.9164 | 490.861
2397.1917 | 499.1027 | 482.8988 | 490.1125
2398.1917 | 499.28 | 482.4085 | 490.1145
2399.1917 | 499.2329 | 481.6398 | 489.3886
2400.1917 | 498.5211 | 480.6161 | 489.4138
2401.1917 | 498.1873 | 480.0876 | 489.7269
2402.1917 | 498.5903 | 480.3251 | 488.9069
2403.1917 | 499.1062 | 480.3679 | 489.4332
2404.1917 | 499.717 | 480.1505 | 489.4082
2405.1917 | 500.4308 | 479.794 | 490.3748
2406.1917 | 500.1818 | 479.6432 | 489.4661
2407.1917 | 500.0842 | 479.7001 | 489.649
2408.1917 | 500.0555 | 480.1221 | 489.9651
2409.1917 | 500.2498 | 480.2375 | 490.1107
2410.1917 | 500.7972 | 480.0781 | 490.688
2411.1917 | 500.3976 | 479.599 | 491.09
2412.1917 | 499.953 | 479.4716 | 491.6376
2413.1917 | 500.0058 | 480.6916 | 492.6179
2414.1917 | 500.079 | 481.5317 | 494.0597
2415.1917 | 500.7332 | 482.114 | 495.0057
2416.1917 | 500.5266 | 482.3035 | 494.2494
2417.1917 | 500.4412 | 482.2786 | 494.7056
2418.1917 | 500.6773 | 483.3622 | 495.409
2419.1917 | 501.0709 | 483.6141 | 494.9274
2420.1917 | 501.6443 | 484.0206 | 494.5984
2421.1917 | 501.4201 | 483.9437 | 494.6641
2422.1917 | 501.8243 | 484.5051 | 495.3403
2423.1917 | 502.1109 | 484.1996 | 494.7443
2424.1917 | 502.3895 | 484.3961 | 494.8592
2425.1917 | 502.6611 | 484.5504 | 494.967
2426.1917 | 502.8398 | 484.7424 | 495.1739
2427.1917 | 503.1795 | 484.4725 | 495.122
2428.1917 | 503.8412 | 484.8505 | 495.062
2429.1917 | 502.9405 | 484.2693 | 495.0995
2430.1917 | 502.1907 | 483.6787 | 494.0655
2431.1917 | 502.5222 | 483.3363 | 492.9105
2432.1917 | 503.0597 | 483.2634 | 493.2088
2433.1917 | 503.9921 | 483.2289 | 493.6388
2434.1917 | 504.0231 | 483.9746 | 493.8079
2435.1917 | 504.4617 | 484.0208 | 494.2
2436.1917 | 504.3429 | 484.6662 | 495.4826
2437.1917 | 504.3582 | 485.0537 | 495.9539
2438.1917 | 504.7232 | 486.5096 | 495.3662
2439.1917 | 505.2014 | 486.6428 | 495.1572
2440.1917 | 505.2421 | 486.609 | 494.8849
2441.1917 | 505.1624 | 486.6816 | 494.9924
2442.1917 | 505.4815 | 487.0704 | 494.3462
2443.1917 | 506.6304 | 486.8586 | 494.6237
2444.1917 | 506.8772 | 487.7261 | 495.5409
2445.1917 | 506.8791 | 487.8584 | 495.5443
2446.1917 | 506.9764 | 487.4601 | 494.5748
2447.1917 | 505.9644 | 487.0455 | 494.8998
2448.1917 | 506.1463 | 486.8328 | 495.0973
2449.1917 | 506.1221 | 487.1587 | 495.8752
2450.1917 | 507.5453 | 487.666 | 496.0003
2451.1917 | 508.3316 | 489.0066 | 496.5552
2452.1917 | 508.6049 | 488.8132 | 497.5782
2453.1917 | 508.3562 | 488.829 | 497.3602
2454.1917 | 509.2802 | 488.6008 | 496.8659
2455.1917 | 509.1816 | 488.7156 | 496.7437
2456.1917 | 509.6252 | 488.9219 | 497.1866
2457.1917 | 509.7727 | 488.9543 | 498.5629
2458.1917 | 509.0367 | 488.5918 | 498.2246
2459.1917 | 508.5484 | 488.4358 | 498.7796
2460.1917 | 507.9251 | 487.9178 | 498.629
2461.1917 | 507.6351 | 487.0128 | 497.6396
2462.1917 | 507.4683 | 486.6821 | 498.2867
2463.1917 | 507.4757 | 487.0266 | 498.2739
2464.1917 | 507.495 | 486.6845 | 497.9229
2465.1917 | 507.3938 | 486.2989 | 499.1172
2466.1917 | 508.2569 | 485.8121 | 498.9941
2467.1917 | 507.9286 | 485.8647 | 500.2486
2468.1917 | 507.0103 | 485.5157 | 500.216
2469.1917 | 506.465 | 485.2083 | 499.7229
2470.1917 | 504.9548 | 485.1957 | 499.2455
2471.1917 | 505.6889 | 485.5243 | 498.9907
2472.1917 | 505.8087 | 485.8623 | 498.1756
2473.1917 | 506.2368 | 486.1886 | 498.2681
2474.1917 | 506.6978 | 486.2407 | 498.489
2475.1917 | 506.6832 | 485.6378 | 500.0077
2476.1917 | 505.3837 | 485.8128 | 500.9783
2477.1917 | 505.3292 | 487.4933 | 500.603
2478.1917 | 504.944 | 487.9629 | 501.0921
2479.1917 | 505.6641 | 488.5184 | 500.1423
2480.1917 | 506.2402 | 488.8043 | 500.055
2481.1917 | 506.4054 | 489.1585 | 499.5105
2482.1917 | 506.5796 | 489.4669 | 500.1481
2483.1917 | 506.048 | 489.5342 | 500.9323
2484.1917 | 505.6025 | 490.8298 | 501.5817
2485.1917 | 505.9157 | 490.3923 | 501.7066
2486.1917 | 506.3172 | 491.0627 | 501.1824
2487.1917 | 505.5791 | 491.1006 | 501.0934
2488.1917 | 505.409 | 491.0343 | 501.6678
2489.1917 | 505.3917 | 490.1369 | 501.141
2490.1917 | 505.199 | 489.7797 | 499.8962
2491.1917 | 505.0995 | 489.034 | 499.0343
2492.1917 | 505.3662 | 488.6174 | 498.7818
2493.1917 | 505.7595 | 488.2195 | 498.3334
2494.1917 | 505.3466 | 488.1916 | 497.2691
2495.1917 | 504.6055 | 488.0037 | 497.5267
2496.1917 | 504.6334 | 488.7899 | 497.0775
2497.1917 | 503.385 | 489.1594 | 496.3982
2498.1917 | 503.0517 | 488.967 | 496.0763
2499.1917 | 504.3639 | 489.3211 | 495.962
2500.1917 | 504.0407 | 489.0322 | 495.65
2501.1917 | 503.5995 | 488.8625 | 495.305
2502.1917 | 503.3571 | 489.5998 | 495.2436
2503.1917 | 503.905 | 489.6845 | 495.8623
2504.1917 | 504.8335 | 489.7141 | 495.6361
2505.1917 | 505.2387 | 490.7226 | 495.2396
2506.1917 | 504.5886 | 490.4913 | 494.2497
2507.1917 | 504.0515 | 490.0034 | 494.4748
2508.1917 | 504.4925 | 489.1572 | 494.2568
2509.1917 | 503.9598 | 488.1715 | 493.5443
2510.1917 | 502.8033 | 487.1616 | 492.1401
2511.1917 | 503.3958 | 486.2873 | 491.1543
2512.1917 | 502.9232 | 485.6443 | 491.3806
2513.1917 | 502.985 | 484.7264 | 491.4136
2514.1917 | 503.7054 | 484.3062 | 491.7167
2515.1917 | 503.5607 | 484.1263 | 492.8201
2516.1917 | 503.3409 | 484.6246 | 493.1626
2517.1917 | 503.7814 | 485.0128 | 493.9099
2518.1917 | 504.0563 | 485.5542 | 494.3683
2519.1917 | 504.4222 | 486.161 | 494.4039
2520.1917 | 504.1723 | 485.9182 | 494.4647
2521.1917 | 504.7006 | 485.3506 | 494.1343
2522.1917 | 504.5281 | 485.1012 | 493.2907
2523.1917 | 503.9888 | 484.7242 | 492.8597
2524.1917 | 502.4093 | 484.454 | 491.9007
2525.1917 | 502.0611 | 484.0399 | 490.751
2526.1917 | 501.5156 | 483.6058 | 490.5817
2527.1917 | 501.2517 | 482.9257 | 490.5268
2528.1917 | 501.0665 | 482.4226 | 490.0577
2529.1917 | 500.6714 | 481.8705 | 489.3133
2530.1917 | 500.3389 | 482.0113 | 489.0876
2531.1917 | 500.1359 | 482.2551 | 488.0844
2532.1917 | 499.9942 | 481.9959 | 487.6745
2533.1917 | 499.8281 | 481.4816 | 486.9682
2534.1917 | 500.8593 | 481.7856 | 486.8544
2535.1917 | 500.5318 | 481.4394 | 486.6934
2536.1917 | 499.9599 | 481.3595 | 486.5712
2537.1917 | 498.3453 | 480.7613 | 486.0237
2538.1917 | 498.949 | 480.2763 | 485.6196
2539.1917 | 499.2433 | 479.8242 | 485.3467
2540.2073 | 499.3906 | 479.7293 | 484.8178
2541.1917 | 499.2403 | 479.8192 | 484.7785
2542.1917 | 499.4085 | 480.3141 | 484.2814
2543.1917 | 498.9385 | 480.7694 | 484.6276
2544.2073 | 498.276 | 480.3552 | 485.0719
2545.1917 | 498.5693 | 480.0259 | 485.4187
2546.1917 | 499.0788 | 480.0596 | 486.1719
2547.1917 | 499.2219 | 479.9735 | 486.1945
2548.1917 | 497.715 | 479.8939 | 485.2285
2549.1917 | 497.2579 | 479.4266 | 485.0547
2550.1917 | 496.9414 | 479.3612 | 485.0666
2551.1917 | 496.6166 | 478.6484 | 484.3821
2552.1917 | 495.0152 | 478.2628 | 483.5484
2553.1917 | 495.2572 | 478.3375 | 483.1196
2554.1917 | 495.7391 | 478.3758 | 483.2808
2555.1917 | 495.5629 | 478.5096 | 484.4539
2556.1917 | 495.7372 | 478.9415 | 484.8639
2557.1917 | 495.954 | 479.2647 | 484.4326
2558.1917 | 496.2098 | 479.8873 | 484.1928
2559.1917 | 496.9461 | 480.2121 | 484.3412
2560.1917 | 496.8567 | 479.9101 | 483.6881
2561.1917 | 495.7636 | 479.2563 | 484.1227
2562.1917 | 495.7231 | 479.0484 | 485.1203
2563.1917 | 496.1569 | 479.1941 | 484.7202
2564.1917 | 495.1437 | 479.2129 | 485.352
2565.1917 | 495.0506 | 478.9297 | 485.427
2566.1917 | 495.0266 | 478.5483 | 484.9382
2567.1917 | 494.5111 | 479.0625 | 486.1916
2568.1917 | 494.8465 | 479.4476 | 487.0566
2569.1917 | 495.663 | 481.0557 | 488.3859
2570.1917 | 496.1779 | 482.3168 | 490.2811
2571.1917 | 496.6536 | 483.4982 | 490.6652
2572.1917 | 496.8365 | 483.5097 | 491.1638
2573.1917 | 497.2559 | 484.0244 | 491.6229
2574.1917 | 497.4517 | 484.4431 | 491.9088
2575.1917 | 498.6944 | 484.8029 | 491.14
2576.1917 | 498.3168 | 484.4893 | 490.6157
2577.1917 | 497.4397 | 484.39 | 491.0072
2578.1917 | 497.3079 | 484.5993 | 491.3021
2579.1917 | 496.6626 | 485.1382 | 491.1251
2580.1917 | 496.4316 | 485.5981 | 490.6588
2581.1917 | 496.1508 | 484.8719 | 489.8434
2582.1917 | 495.5741 | 483.9354 | 489.1196
2583.1917 | 494.3369 | 483.5257 | 489.2893
2584.1917 | 494.2639 | 483.1187 | 489.7695
2585.1917 | 493.4353 | 482.6344 | 489.8658
2586.1917 | 493.4633 | 481.8873 | 489.6896
2587.1917 | 493.6818 | 481.3611 | 488.9636
2588.1917 | 494.4479 | 481.3911 | 488.3189
2589.1917 | 493.4192 | 482.1939 | 487.618
2590.1917 | 493.1095 | 481.6592 | 486.9999
2591.1917 | 493.9303 | 481.7264 | 486.3621
2592.1917 | 493.918 | 481.1639 | 486.3986
2593.1917 | 493.2774 | 480.7976 | 485.8928
2594.1917 | 493.3828 | 480.2774 | 485.7382
2595.1917 | 492.8006 | 480.1089 | 484.9622
2596.1917 | 492.1691 | 479.0559 | 484.6673
2597.1917 | 492.0328 | 478.9595 | 484.8547
2598.1917 | 492.2374 | 478.7007 | 484.9027
2599.1917 | 493.0754 | 478.7345 | 484.4989
2600.1917 | 492.8967 | 479.0969 | 483.1398
2601.1917 | 493.2655 | 478.5171 | 482.2387
2602.1917 | 493.4068 | 478.0221 | 482.5943
2603.1917 | 493.7516 | 478.213 | 482.6884
2604.1917 | 494.0799 | 478.3073 | 482.1315
2605.1917 | 494.2769 | 477.9066 | 481.5797
2606.1917 | 494.4732 | 478.2977 | 481.3684
2607.1917 | 494.7285 | 478.2367 | 480.8246
2608.1917 | 494.733 | 478.8784 | 481.4465
2609.1917 | 494.5981 | 479.5381 | 482.2743
2610.1917 | 494.5261 | 480.1704 | 482.5094
2611.1917 | 494.587 | 480.0813 | 483.0004
2612.1917 | 495.7002 | 480.3787 | 483.2524
2613.1917 | 495.5786 | 480.8493 | 483.2748
2614.1917 | 495.7359 | 480.5525 | 483.4158
2615.1917 | 495.6612 | 480.5541 | 483.183
2616.1917 | 496.205 | 480.6729 | 484.2039
2617.1917 | 496.8735 | 481.5842 | 484.4781
2618.1917 | 496.5325 | 481.5752 | 484.2374
2619.1917 | 496.7419 | 481.6555 | 484.4388
2620.1917 | 497.3448 | 482.2344 | 485.9964
2621.1917 | 497.77 | 482.3931 | 485.8843
2622.1917 | 499.0418 | 482.7801 | 485.6999
2623.1917 | 499.6991 | 483.2608 | 486.1761
2624.1917 | 499.1494 | 484.1594 | 486.104
2625.1917 | 498.5559 | 484.7878 | 486.3619
2626.1917 | 499.4148 | 484.4639 | 486.0854
2627.1917 | 499.8346 | 484.4414 | 485.4775
2628.1917 | 499.603 | 483.9773 | 485.1642
2629.1917 | 498.9546 | 483.8949 | 485.6411
2630.1917 | 498.5683 | 484.1112 | 485.4659
2631.1917 | 497.3652 | 484.4967 | 485.3413
2632.1917 | 496.8792 | 484.8318 | 485.0834
2633.1917 | 497.1178 | 484.7901 | 484.9732
2634.1917 | 497.3677 | 484.2931 | 485.5838
2635.1917 | 497.6335 | 483.6604 | 485.8609
2636.1917 | 498.0078 | 483.0437 | 486.1557
2637.1917 | 498.2219 | 482.2886 | 485.8301
2638.1917 | 498.2753 | 481.887 | 486.5779
2639.1917 | 499.0268 | 482.0019 | 487.2088
2640.1917 | 499.1207 | 482.1074 | 487.2546