## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 5 - Circuit Simulator Data Only
Test Date: | 2010-03-01
DCSim DAQ Start Time | 13:30
DCSim Time for Synchronization | 13:42
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:41
Heat Source Start Time | 14:02
DCSim Offset | 0:32 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1920 | seconds
Heat Source Offset | 0:21 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1288 | seconds
Heat Source Stop Time | 14:46
Test Duration | 0:44 | hour:minutes:seconds
| 2640 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", " D Position - 7'", respectively.
SWGR Trip | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", " D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-1.6094 | 124.0173 | -62.0407 | 61.8759 | -0.0049592 | 0.02123 | 0.01561 | 0.00067508 | 0.065896 | -0.00016869 | 0.070397 | -62.114 | 61.8439 | -62.2467 | -61.9904 | 61.5463 | 0.20142 | -0.22888 | 0.18768 | 61.8622 | -62.2147 | -0.20599 | -0.032044 | -0.073243 | 0.050354 | -0.32959 | -0.17395 | -0.013733 | 0.13275 | 61.8118 | 62.2284 | 123.587 | 123.8846 | -0.073243 | 123.9029 | 62.2421 | -0.17395 | 123.8846 | -0.073243 | 62.2421 | 123.587 | 123.9029 | -124.1226 | -124.0906
0.0625 | 123.9944 | -62.0316 | 61.908 | 0.0026703 | 0.019307 | 0.019241 | -0.0029565 | 0.065469 | -0.0031595 | 0.069757 | -62.1048 | 61.8576 | -62.2421 | -61.972 | 61.5784 | 0.21973 | -0.24261 | 0.18768 | 61.8805 | -62.2284 | -0.21057 | -0.050354 | -0.073242 | 0.059509 | -0.32959 | -0.19684 | -0.027466 | 0.13733 | 61.7889 | 62.2192 | 123.6099 | 123.8892 | -0.073242 | 123.912 | 62.2513 | -0.19684 | 123.8892 | -0.073242 | 62.2513 | 123.6099 | 123.912 | -124.1501 | -124.1364
1.8125 | 124.1272 | -62.0544 | 61.8256 | -0.012589 | 0.016957 | 0.01561 | 0.0015295 | 0.066964 | -0.0033731 | 0.070184 | -62.2467 | 61.8668 | -62.3199 | -62.1277 | 61.409 | 0.068665 | -0.027466 | 0.059509 | 61.8942 | -62.2604 | -0.2655 | 0.041198 | -0.19226 | -0.073243 | -0.41656 | -0.20599 | 0.068664 | 0.073242 | 62.027 | 62.114 | 123.4634 | 123.9212 | -0.19226 | 123.9487 | 62.1231 | -0.20599 | 123.9212 | -0.19226 | 62.1231 | 123.4634 | 123.9487 | -124.1455 | -124.086
3.4844 | 123.9853 | -62.0773 | 61.8988 | 0.0026703 | 0.015676 | 0.014755 | -0.0035973 | 0.066751 | -0.0040139 | 0.069757 | -62.114 | 61.8301 | -62.2375 | -61.9858 | 61.5646 | 0.2243 | -0.2655 | 0.17395 | 61.8393 | -62.2192 | -0.16022 | -0.068665 | -0.036621 | 0.091553 | -0.33417 | -0.14191 | -0.05951 | 0.1236 | 61.8118 | 62.2513 | 123.642 | 123.9075 | -0.036621 | 123.9166 | 62.3016 | -0.14191 | 123.9075 | -0.036621 | 62.3016 | 123.642 | 123.9166 | -124.1364 | -124.118
5.2344 | 124.0723 | -62.0499 | 61.8073 | 0.0026703 | 0.018453 | 0.0186 | 0.0028113 | 0.064615 | -0.0057229 | 0.070397 | -62.1826 | 61.8851 | -62.2925 | -62.0499 | 61.4868 | 0.17395 | -0.018311 | 0.17395 | 61.853 | -62.2559 | -0.24261 | 0.07782 | -0.13275 | 0 | -0.32044 | -0.20599 | 0.045776 | 0.10986 | 62.0316 | 62.2238 | 123.5367 | 123.9349 | -0.13275 | 123.9029 | 62.2238 | -0.20599 | 123.9349 | -0.13275 | 62.2238 | 123.5367 | 123.9029 | -124.0997 | -124.0631
6.9688 | 124.0082 | -62.027 | 61.9034 | -0.0049592 | 0.018453 | 0.011551 | -0.0038111 | 0.063119 | -0.0014505 | 0.067834 | -62.1048 | 61.8851 | -62.2284 | -61.9904 | 61.5555 | 0.2243 | -0.18768 | 0.17853 | 61.8942 | -62.2238 | -0.20142 | -0.01831 | -0.077819 | 0.036622 | -0.3479 | -0.19684 | -0.009155 | 0.1236 | 61.8393 | 62.2055 | 123.5825 | 123.912 | -0.077819 | 123.9212 | 62.2513 | -0.19684 | 123.912 | -0.077819 | 62.2513 | 123.5825 | 123.9212 | -124.1318 | -124.1272
8.6406 | 124.1135 | -62.059 | 61.7706 | 0.0026703 | 0.019734 | 0.014541 | 0.0038795 | 0.064401 | -0.0042277 | 0.066766 | -62.2147 | 61.8759 | -62.2879 | -62.1002 | 61.4136 | 0.07782 | -0.009155 | 0.07782 | 61.8988 | -62.2467 | -0.22888 | 0.10529 | -0.15564 | -0.041199 | -0.35706 | -0.18768 | 0.12817 | 0.073242 | 62.0499 | 62.1368 | 123.4726 | 123.9349 | -0.15564 | 123.9578 | 62.1368 | -0.18768 | 123.9349 | -0.15564 | 62.1368 | 123.4726 | 123.9578 | -124.0585 | -124.0173
10.3906 | 123.9807 | -62.059 | 61.8668 | -0.0049592 | 0.017598 | 0.014969 | -0.0035973 | 0.064187 | -0.0031595 | 0.070825 | -62.0682 | 61.9034 | -62.2055 | -61.8988 | 61.6333 | 0.29297 | -0.09613 | 0.31586 | 61.8988 | -62.2055 | -0.14648 | 0.036621 | -0.009155 | 0.16022 | -0.23346 | -0.14648 | 0.032044 | 0.13733 | 61.9629 | 62.3749 | 123.6923 | 123.9624 | -0.009155 | 123.9578 | 62.352 | -0.14648 | 123.9624 | -0.009155 | 62.352 | 123.6923 | 123.9578 | -124.0723 | -124.0723
12.1406 | 123.9578 | -62.0224 | 61.8805 | 0.0103 | 0.019094 | 0.013473 | -0.0050927 | 0.062692 | -0.0025187 | 0.069757 | -62.0682 | 61.8805 | -62.1872 | -61.9034 | 61.6333 | 0.29755 | -0.15106 | 0.3067 | 61.8988 | -62.1735 | -0.1648 | 0 | -0.045776 | 0.11902 | -0.24719 | -0.15106 | 0.018311 | 0.11902 | 61.8713 | 62.3291 | 123.6557 | 123.9029 | -0.045776 | 123.9212 | 62.3199 | -0.15106 | 123.9029 | -0.045776 | 62.3199 | 123.6557 | 123.9212 | -124.0677 | -124.054
13.875 | 123.967 | -62.0361 | 61.8851 | -0.0049592 | 0.018239 | 0.014114 | -0.0027429 | 0.065683 | -0.0050821 | 0.069757 | -62.0544 | 61.8896 | -62.2009 | -61.8896 | 61.6287 | 0.29755 | -0.10986 | 0.29297 | 61.8851 | -62.1918 | -0.16479 | 0.004577 | -0.01831 | 0.14648 | -0.25635 | -0.15564 | 0 | 0.14648 | 61.9263 | 62.3291 | 123.6649 | 123.9258 | -0.01831 | 123.9212 | 62.3337 | -0.15564 | 123.9258 | -0.01831 | 62.3337 | 123.6649 | 123.9212 | -124.086 | -124.0768
15.5469 | 123.9899 | -62.0132 | 61.8988 | -0.012589 | 0.019094 | 0.014969 | 0.00024788 | 0.064401 | -0.0029459 | 0.071038 | -62.0956 | 61.8439 | -62.2375 | -61.972 | 61.5646 | 0.21515 | -0.20599 | 0.17853 | 61.8851 | -62.1964 | -0.2243 | -0.054932 | -0.082397 | 0.041199 | -0.33417 | -0.18311 | -0.013733 | 0.14191 | 61.8073 | 62.1918 | 123.5779 | 123.8571 | -0.082397 | 123.8983 | 62.2284 | -0.18311 | 123.8571 | -0.082397 | 62.2284 | 123.5779 | 123.8983 | -124.1364 | -124.0952
17.2969 | 123.9853 | -62.0316 | 61.9034 | -0.0049592 | 0.020589 | 0.016678 | -0.00017952 | 0.06376 | -0.0027323 | 0.06997 | -62.0728 | 61.8439 | -62.2238 | -61.9492 | 61.5738 | 0.21973 | -0.23346 | 0.19226 | 61.853 | -62.2055 | -0.19226 | -0.059509 | -0.041199 | 0.082397 | -0.32959 | -0.17395 | -0.050354 | 0.15106 | 61.7981 | 62.2238 | 123.6053 | 123.8754 | -0.041199 | 123.8846 | 62.2513 | -0.17395 | 123.8754 | -0.041199 | 62.2513 | 123.6053 | 123.8846 | -124.1272 | -124.1089
18.9688 | 124.0997 | -62.0132 | 61.7981 | 0.0026703 | 0.019948 | 0.013046 | 3.4284e-05 | 0.064187 | -0.0048685 | 0.06762 | -62.1826 | 61.8805 | -62.2971 | -62.0316 | 61.4914 | 0.15106 | 0.10529 | 0.18768 | 61.9171 | -62.2284 | -0.28381 | 0.082397 | -0.16937 | -0.01831 | -0.3067 | -0.21515 | 0.11902 | 0.11444 | 62.1185 | 62.2009 | 123.5046 | 123.8937 | -0.16937 | 123.9304 | 62.1643 | -0.21515 | 123.8937 | -0.16937 | 62.1643 | 123.5046 | 123.9304 | -124.0952 | -124.0265
20.7188 | 123.9853 | -62.0132 | 61.8805 | -0.020218 | 0.021443 | 0.016037 | -0.0038111 | 0.062692 | -0.0035867 | 0.070611 | -62.0911 | 61.8988 | -62.178 | -61.9308 | 61.5967 | 0.27466 | -0.11444 | 0.26093 | 61.8942 | -62.2009 | -0.1648 | 0.018311 | -0.077819 | 0.082398 | -0.28381 | -0.18768 | 0.013733 | 0.086976 | 61.8988 | 62.2742 | 123.6099 | 123.912 | -0.077819 | 123.9075 | 62.2879 | -0.18768 | 123.912 | -0.077819 | 62.2879 | 123.6099 | 123.9075 | -124.0585 | -124.0814
22.4531 | 123.9761 | -62.0178 | 61.853 | -0.0049592 | 0.022939 | 0.014969 | -0.0016747 | 0.065256 | -0.0031595 | 0.069329 | -62.0819 | 61.908 | -62.1872 | -61.9171 | 61.6013 | 0.27466 | -0.10529 | 0.27008 | 61.908 | -62.1643 | -0.16937 | 0.054932 | -0.064087 | 0.10071 | -0.25177 | -0.14648 | 0.054932 | 0.10529 | 61.9125 | 62.2879 | 123.6191 | 123.9258 | -0.064087 | 123.9258 | 62.2925 | -0.14648 | 123.9258 | -0.064087 | 62.2925 | 123.6191 | 123.9258 | -124.0402 | -124.0173
24.1875 | 123.9578 | -62.0361 | 61.8668 | 0.0026703 | 0.014608 | 0.014541 | -0.0021021 | 0.064401 | -0.0042277 | 0.070825 | -62.0407 | 61.8393 | -62.2147 | -61.8896 | 61.6196 | 0.28381 | -0.11444 | 0.3067 | 61.8805 | -62.146 | -0.17853 | -0.027466 | -0.004577 | 0.14648 | -0.24719 | -0.10986 | 0.013733 | 0.17395 | 61.9217 | 62.3428 | 123.6557 | 123.8754 | -0.004577 | 123.9166 | 62.3199 | -0.10986 | 123.8754 | -0.004577 | 62.3199 | 123.6557 | 123.9166 | -124.0814 | -124.0128
25.9219 | 124.0265 | -62.0407 | 61.8164 | -0.0049592 | 0.021016 | 0.011764 | 0.00024788 | 0.063974 | -0.0023049 | 0.070397 | -62.114 | 61.9034 | -62.233 | -62.0041 | 61.5143 | 0.20142 | 0.059509 | 0.21973 | 61.8896 | -62.2192 | -0.19226 | 0.086975 | -0.073243 | 0.036621 | -0.30212 | -0.17853 | 0.073242 | 0.11902 | 62.1002 | 62.2604 | 123.555 | 123.9441 | -0.073243 | 123.9304 | 62.2421 | -0.17853 | 123.9441 | -0.073243 | 62.2421 | 123.555 | 123.9304 | -124.0494 | -124.0356
27.5938 | 123.9899 | -62.0087 | 61.8988 | -0.0049592 | 0.021871 | 0.015823 | 3.4284e-05 | 0.063547 | -0.0031595 | 0.070611 | -62.0911 | 61.8576 | -62.2238 | -61.9537 | 61.5463 | 0.19684 | -0.16479 | 0.16937 | 61.8942 | -62.1872 | -0.21515 | -0.041199 | -0.082397 | 0.054932 | -0.35248 | -0.17853 | -0.004578 | 0.13275 | 61.8439 | 62.178 | 123.555 | 123.8663 | -0.082397 | 123.9029 | 62.2055 | -0.17853 | 123.8663 | -0.082397 | 62.2055 | 123.555 | 123.9029 | -124.1226 | -124.086
29.3438 | 124.0402 | -62.0361 | 61.7889 | -0.020218 | 0.022298 | 0.015823 | 0.0066565 | 0.068033 | -0.0055093 | 0.067834 | -62.1231 | 61.8713 | -62.2559 | -62.0087 | 61.4731 | 0.14191 | -0.032043 | 0.16479 | 61.8851 | -62.2513 | -0.21973 | 0.082398 | -0.086975 | 0.027466 | -0.31586 | -0.21515 | 0.096131 | 0.13275 | 62.0041 | 62.2009 | 123.5092 | 123.9075 | -0.086975 | 123.9212 | 62.178 | -0.21515 | 123.9075 | -0.086975 | 62.178 | 123.5092 | 123.9212 | -124.0448 | -124.0402
31.0781 | 124.0219 | -62.0544 | 61.7844 | 0.0103 | 0.019948 | 0.015396 | 0.0025977 | 0.066537 | -0.0046549 | 0.070397 | -62.1552 | 61.8622 | -62.3016 | -61.9995 | 61.4868 | 0.17853 | -0.027466 | 0.18768 | 61.8622 | -62.2421 | -0.24719 | 0.07782 | -0.10071 | 0.054931 | -0.29755 | -0.18768 | 0.07782 | 0.14649 | 62.027 | 62.2421 | 123.5413 | 123.9166 | -0.10071 | 123.9166 | 62.233 | -0.18768 | 123.9166 | -0.10071 | 62.233 | 123.5413 | 123.9166 | -124.086 | -124.0265
32.8281 | 124.0723 | -62.0041 | 61.7615 | -0.012589 | 0.020803 | 0.015182 | -0.0016747 | 0.064401 | -0.0018777 | 0.069543 | -62.1735 | 61.9217 | -62.2925 | -62.0361 | 61.4548 | 0.14191 | 0.10071 | 0.17853 | 61.8851 | -62.233 | -0.28839 | 0.16022 | -0.16937 | -0.032044 | -0.3067 | -0.22888 | 0.1236 | 0.11902 | 62.1048 | 62.1826 | 123.4589 | 123.9258 | -0.16937 | 123.8892 | 62.146 | -0.22888 | 123.9258 | -0.16937 | 62.146 | 123.4589 | 123.8892 | -124.054 | -123.9944
34.5156 | 123.9258 | -62.0087 | 61.8439 | 0.0026703 | 0.019521 | 0.014114 | -0.0050927 | 0.065042 | -0.0020913 | 0.069116 | -62.0132 | 61.9034 | -62.1735 | -61.9034 | 61.6104 | 0.30212 | -0.10529 | 0.32044 | 61.853 | -62.2009 | -0.16479 | 0.059509 | -0.004578 | 0.10529 | -0.23346 | -0.19226 | 0.009155 | 0.16022 | 61.9034 | 62.3291 | 123.6191 | 123.912 | -0.004578 | 123.8617 | 62.3108 | -0.19226 | 123.912 | -0.004578 | 62.3108 | 123.6191 | 123.8617 | -124.0173 | -124.0448
36.2656 | 124.0036 | -62.0041 | 61.7844 | -0.0049592 | 0.020803 | 0.014755 | -0.0012475 | 0.062051 | -0.0033731 | 0.06997 | -62.1094 | 61.8759 | -62.233 | -61.9675 | 61.5143 | 0.18768 | 0.050354 | 0.22888 | 61.8851 | -62.2101 | -0.22888 | 0.091553 | -0.10529 | 0.036621 | -0.27008 | -0.20599 | 0.10071 | 0.1236 | 62.0544 | 62.233 | 123.5184 | 123.88 | -0.10529 | 123.8892 | 62.1918 | -0.20599 | 123.88 | -0.10529 | 62.1918 | 123.5184 | 123.8892 | -124.0173 | -123.9944
38 | 123.9807 | -61.9858 | 61.8851 | -0.012589 | 0.020375 | 0.014969 | -0.0016747 | 0.064187 | -0.0029459 | 0.069757 | -62.0773 | 61.8713 | -62.2192 | -61.9675 | 61.5463 | 0.20142 | -0.16022 | 0.19684 | 61.8347 | -62.178 | -0.23346 | -0.013733 | -0.091553 | 0.018311 | -0.33875 | -0.19226 | -0.050354 | 0.14191 | 61.8256 | 62.1826 | 123.5321 | 123.8571 | -0.091553 | 123.8205 | 62.1872 | -0.19226 | 123.8571 | -0.091553 | 62.1872 | 123.5321 | 123.8205 | -124.1043 | -124.0631
39.6719 | 123.9532 | -62.0087 | 61.8851 | 0.0026703 | 0.018239 | 0.017532 | -0.00017952 | 0.063547 | -0.0035867 | 0.070397 | -62.0728 | 61.821 | -62.233 | -61.94 | 61.5555 | 0.21973 | -0.22888 | 0.19684 | 61.8576 | -62.146 | -0.2243 | -0.064087 | -0.064087 | 0.068665 | -0.32959 | -0.13733 | -0.027466 | 0.16022 | 61.7798 | 62.2055 | 123.5641 | 123.8297 | -0.064087 | 123.8663 | 62.2284 | -0.13733 | 123.8297 | -0.064087 | 62.2284 | 123.5641 | 123.8663 | -124.118 | -124.0311
41.4062 | 123.967 | -62.0453 | 61.8393 | 0.0026703 | 0.019948 | 0.01326 | -0.0016747 | 0.064401 | -0.0029459 | 0.067834 | -62.059 | 61.8576 | -62.1918 | -61.94 | 61.5555 | 0.23804 | -0.004578 | 0.2655 | 61.8942 | -62.1735 | -0.14648 | 0.018311 | -0.013733 | 0.10529 | -0.28381 | -0.12817 | 0.054932 | 0.13275 | 62.0407 | 62.3108 | 123.6008 | 123.9029 | -0.013733 | 123.9395 | 62.2833 | -0.12817 | 123.9029 | -0.013733 | 62.2833 | 123.6008 | 123.9395 | -124.0311 | -124.0128
43.1406 | 123.912 | -62.0087 | 61.853 | -0.0049592 | 0.018666 | 0.013473 | -0.0035973 | 0.063547 | -0.0018777 | 0.068688 | -62.0316 | 61.8668 | -62.1643 | -61.8759 | 61.6196 | 0.29297 | -0.11444 | 0.30212 | 61.8301 | -62.1597 | -0.15564 | 0.013733 | -0.022888 | 0.13275 | -0.23346 | -0.15106 | -0.022888 | 0.13275 | 61.8942 | 62.3108 | 123.6282 | 123.8754 | -0.022888 | 123.8388 | 62.3016 | -0.15106 | 123.8754 | -0.022888 | 62.3016 | 123.6282 | 123.8388 | -124.0173 | -124.0128
44.9062 | 123.9487 | -62.0224 | 61.8713 | -0.0049592 | 0.018453 | 0.015182 | -0.00039312 | 0.065683 | -0.0025187 | 0.069543 | -62.0865 | 61.8027 | -62.233 | -61.9263 | 61.5463 | 0.21973 | -0.24261 | 0.19226 | 61.8393 | -62.1597 | -0.21057 | -0.068665 | -0.064087 | 0.09613 | -0.32501 | -0.13733 | -0.032044 | 0.14648 | 61.7798 | 62.2147 | 123.5687 | 123.8251 | -0.064087 | 123.8617 | 62.2421 | -0.13733 | 123.8251 | -0.064087 | 62.2421 | 123.5687 | 123.8617 | -124.1043 | -124.0311
46.5625 | 123.9944 | -62.0361 | 61.7615 | 0.0026703 | 0.021443 | 0.01625 | 0.0023841 | 0.062906 | -0.0050821 | 0.068048 | -62.146 | 61.8484 | -62.2787 | -61.9858 | 61.4731 | 0.17395 | -0.022888 | 0.19226 | 61.8439 | -62.2147 | -0.24262 | 0.086975 | -0.10986 | 0.050354 | -0.28839 | -0.17853 | 0.082397 | 0.13275 | 62.0132 | 62.2284 | 123.5092 | 123.8846 | -0.10986 | 123.88 | 62.2101 | -0.17853 | 123.8846 | -0.10986 | 62.2101 | 123.5092 | 123.88 | -124.0402 | -123.9761
48.2969 | 124.0494 | -62.0178 | 61.7661 | 0.0026703 | 0.018453 | 0.012192 | 0.0038795 | 0.064187 | -0.0044413 | 0.070397 | -62.1826 | 61.8393 | -62.3062 | -62.0773 | 61.409 | 0.082397 | -0.018311 | 0.10071 | 61.8118 | -62.2604 | -0.28839 | 0.073242 | -0.16479 | -0.05951 | -0.35706 | -0.24262 | 0.045777 | 0.1236 | 61.9995 | 62.1185 | 123.4268 | 123.8571 | -0.16479 | 123.8297 | 62.1002 | -0.24262 | 123.8571 | -0.16479 | 62.1002 | 123.4268 | 123.8297 | -124.0723 | -124.0265
49.9688 | 124.0128 | -62.0132 | 61.7386 | 0.0103 | 0.019521 | 0.012619 | 0.0013159 | 0.063333 | -0.0048685 | 0.069757 | -62.1689 | 61.8805 | -62.2742 | -62.0132 | 61.4639 | 0.15564 | 0.022888 | 0.20142 | 61.8622 | -62.2101 | -0.26093 | 0.14191 | -0.15564 | 0 | -0.27466 | -0.19684 | 0.1236 | 0.10529 | 62.0361 | 62.2147 | 123.4772 | 123.8937 | -0.15564 | 123.8754 | 62.1689 | -0.19684 | 123.8937 | -0.15564 | 62.1689 | 123.4772 | 123.8754 | -124.0128 | -123.9487
51.7344 | 123.9899 | -61.9949 | 61.8027 | -0.0049592 | 0.020162 | 0.014755 | -0.0012475 | 0.064187 | -0.0035867 | 0.069116 | -62.1368 | 61.8393 | -62.2284 | -62.0132 | 61.4914 | 0.17395 | -0.17853 | 0.15106 | 61.8027 | -62.2192 | -0.23346 | 0.036621 | -0.14191 | -0.018311 | -0.31128 | -0.2243 | 0 | 0.091553 | 61.8164 | 62.146 | 123.4863 | 123.8342 | -0.14191 | 123.7976 | 62.1689 | -0.2243 | 123.8342 | -0.14191 | 62.1689 | 123.4863 | 123.7976 | -124.0311 | -124.0219
53.6719 | 123.9212 | -61.9949 | 61.8576 | -0.012589 | 0.019094 | 0.0087735 | -0.0044519 | 0.063974 | -0.0023049 | 0.071679 | -62.0682 | 61.8256 | -62.178 | -61.9537 | 61.5372 | 0.21515 | -0.20599 | 0.17853 | 61.8164 | -62.1964 | -0.18311 | -0.032043 | -0.073242 | 0.041199 | -0.32043 | -0.20142 | -0.041199 | 0.10986 | 61.7889 | 62.1735 | 123.5321 | 123.8205 | -0.073242 | 123.8113 | 62.2101 | -0.20142 | 123.8205 | -0.073242 | 62.2101 | 123.5321 | 123.8113 | -124.0356 | -124.054
55.3594 | 124.0082 | -62.0132 | 61.7752 | -0.0049592 | 0.01888 | 0.014755 | 0.0025977 | 0.064401 | -0.0027323 | 0.069757 | -62.1231 | 61.8622 | -62.2604 | -61.9858 | 61.4594 | 0.16479 | 0.004578 | 0.20142 | 61.853 | -62.2055 | -0.24719 | 0.086975 | -0.10986 | 0.027466 | -0.31586 | -0.19226 | 0.077819 | 0.13733 | 62.0178 | 62.2147 | 123.4726 | 123.8754 | -0.10986 | 123.8663 | 62.178 | -0.19226 | 123.8754 | -0.10986 | 62.178 | 123.4726 | 123.8663 | -124.0356 | -123.9807
57.0312 | 123.9578 | -61.9812 | 61.853 | -0.0049592 | 0.018453 | 0.014969 | -0.0055199 | 0.063119 | -0.0014505 | 0.06997 | -62.1094 | 61.8851 | -62.1826 | -61.94 | 61.5326 | 0.22888 | -0.1236 | 0.20599 | 61.853 | -62.1689 | -0.20142 | 0.032044 | -0.12817 | 0.041199 | -0.32043 | -0.18768 | 0 | 0.073242 | 61.8576 | 62.1872 | 123.5138 | 123.8663 | -0.12817 | 123.8342 | 62.2101 | -0.18768 | 123.8663 | -0.12817 | 62.2101 | 123.5138 | 123.8342 | -124.0356 | -124.0219
58.6875 | 123.9578 | -61.9904 | 61.853 | -0.012589 | 0.01888 | 0.012405 | -0.0027429 | 0.06376 | -0.00080969 | 0.06997 | -62.0865 | 61.8851 | -62.1643 | -61.9675 | 61.5097 | 0.20142 | -0.11444 | 0.17853 | 61.853 | -62.1735 | -0.17395 | 0.032044 | -0.096131 | 0.022888 | -0.34332 | -0.18311 | 0 | 0.07782 | 61.8759 | 62.1689 | 123.5001 | 123.8754 | -0.096131 | 123.8434 | 62.1918 | -0.18311 | 123.8754 | -0.096131 | 62.1918 | 123.5001 | 123.8434 | -124.0173 | -124.0265
60.3438 | 123.9716 | -62.0178 | 61.7798 | -0.012589 | 0.019521 | 0.014541 | -0.00017952 | 0.061197 | -0.0031595 | 0.068902 | -62.0865 | 61.8805 | -62.2009 | -61.9904 | 61.4868 | 0.1831 | 0.054932 | 0.2243 | 61.8805 | -62.2238 | -0.18311 | 0.10071 | -0.068665 | 0.027466 | -0.29297 | -0.20599 | 0.10071 | 0.11444 | 62.0728 | 62.2421 | 123.5046 | 123.8983 | -0.068665 | 123.8983 | 62.2009 | -0.20599 | 123.8983 | -0.068665 | 62.2009 | 123.5046 | 123.8983 | -123.9807 | -124.0036
62.0156 | 123.9487 | -61.9858 | 61.8439 | -0.012589 | 0.01888 | 0.017105 | -0.0033837 | 0.062692 | -0.0014505 | 0.071466 | -62.0956 | 61.8668 | -62.1597 | -61.9492 | 61.5097 | 0.21057 | -0.13275 | 0.16937 | 61.8393 | -62.1735 | -0.17395 | 0.022888 | -0.10986 | 0.036621 | -0.33417 | -0.18768 | -0.004578 | 0.064087 | 61.853 | 62.1552 | 123.4955 | 123.8525 | -0.10986 | 123.8251 | 62.1964 | -0.18768 | 123.8525 | -0.10986 | 62.1964 | 123.4955 | 123.8251 | -124.0036 | -124.0173
64.0469 | 124.0448 | -62.0087 | 61.7569 | 0.0026703 | 0.023793 | 0.01561 | 0.0051611 | 0.064828 | -0.0065775 | 0.069543 | -62.1597 | 61.8942 | -62.2696 | -62.0499 | 61.3907 | 0.086975 | 0.013733 | 0.091553 | 61.8484 | -62.233 | -0.26093 | 0.13733 | -0.15106 | -0.041199 | -0.36621 | -0.2243 | 0.091553 | 0.10986 | 62.0224 | 62.1002 | 123.3994 | 123.9029 | -0.15106 | 123.8571 | 62.0956 | -0.2243 | 123.9029 | -0.15106 | 62.0956 | 123.3994 | 123.8571 | -124.0265 | -123.9899
65.8438 | 124.0356 | -61.9904 | 61.7523 | -0.0049592 | 0.017171 | 0.012405 | -0.0018885 | 0.063547 | -0.0023049 | 0.071679 | -62.1689 | 61.8576 | -62.265 | -62.0041 | 61.4456 | 0.15106 | 0.11444 | 0.19226 | 61.8713 | -62.1964 | -0.27466 | 0.10529 | -0.17853 | -0.013733 | -0.3067 | -0.20599 | 0.11902 | 0.096131 | 62.1048 | 62.1826 | 123.436 | 123.848 | -0.17853 | 123.8617 | 62.1414 | -0.20599 | 123.848 | -0.17853 | 62.1414 | 123.436 | 123.8617 | -124.0173 | -123.9487
67.5156 | 124.0356 | -61.9995 | 61.7615 | 0.0026703 | 0.019521 | 0.016464 | 0.0017431 | 0.066324 | -0.0061503 | 0.070825 | -62.1918 | 61.8118 | -62.2925 | -62.0499 | 61.409 | 0.091553 | 0.018311 | 0.10071 | 61.8576 | -62.1918 | -0.29297 | 0.050354 | -0.19226 | -0.050354 | -0.35248 | -0.19226 | 0.09613 | 0.10071 | 62.0178 | 62.1002 | 123.4085 | 123.8113 | -0.19226 | 123.8571 | 62.0911 | -0.19226 | 123.8113 | -0.19226 | 62.0911 | 123.4085 | 123.8571 | -124.054 | -123.9532
69.2031 | 124.0494 | -61.9904 | 61.7386 | -0.0049592 | 0.021657 | 0.015182 | 0.0023841 | 0.06611 | -0.0044413 | 0.069543 | -62.1689 | 61.8301 | -62.265 | -62.059 | 61.4136 | 0.10071 | 0.013733 | 0.10071 | 61.8439 | -62.2284 | -0.27466 | 0.091553 | -0.17853 | -0.068665 | -0.32501 | -0.23804 | 0.10529 | 0.096131 | 62.0041 | 62.0911 | 123.4039 | 123.8205 | -0.17853 | 123.8342 | 62.0911 | -0.23804 | 123.8205 | -0.17853 | 62.0911 | 123.4039 | 123.8342 | -124.0036 | -123.967
70.8906 | 124.0219 | -61.9949 | 61.7523 | -0.0049592 | 0.017598 | 0.016037 | -0.00039312 | 0.066964 | -0.0050821 | 0.069329 | -62.1826 | 61.8622 | -62.2696 | -62.0773 | 61.377 | 0.059509 | -0.027466 | 0.059509 | 61.8439 | -62.2238 | -0.27466 | 0.10986 | -0.18768 | -0.082398 | -0.37537 | -0.22888 | 0.091553 | 0.086975 | 61.9675 | 62.0544 | 123.3719 | 123.8571 | -0.18768 | 123.8388 | 62.0544 | -0.22888 | 123.8571 | -0.18768 | 62.0544 | 123.3719 | 123.8388 | -124.0219 | -123.9761
72.5938 | 123.8892 | -61.9949 | 61.8347 | -0.0049592 | 0.018666 | 0.012832 | -0.0068017 | 0.06376 | -0.0055093 | 0.069116 | -62.027 | 61.8851 | -62.1277 | -61.8988 | 61.5601 | 0.27466 | -0.14648 | 0.29297 | 61.8347 | -62.1414 | -0.13275 | 0.050354 | -0.032044 | 0.09613 | -0.27466 | -0.14648 | 0 | 0.10071 | 61.8484 | 62.2879 | 123.555 | 123.88 | -0.032044 | 123.8297 | 62.2696 | -0.14648 | 123.88 | -0.032044 | 62.2696 | 123.555 | 123.8297 | -123.9624 | -123.9761
74.3125 | 124.0128 | -61.9812 | 61.7432 | 0.0103 | 0.019521 | 0.014755 | -0.00082032 | 0.064828 | -0.0040139 | 0.069329 | -62.1597 | 61.8805 | -62.2375 | -62.0178 | 61.4182 | 0.14648 | 0.07782 | 0.1831 | 61.8484 | -62.1735 | -0.25635 | 0.13733 | -0.17853 | -0.036621 | -0.32501 | -0.19226 | 0.10529 | 0.07782 | 62.059 | 62.1643 | 123.3994 | 123.8617 | -0.17853 | 123.8297 | 62.1277 | -0.19226 | 123.8617 | -0.17853 | 62.1277 | 123.3994 | 123.8297 | -123.9807 | -123.9166
75.9688 | 124.0173 | -61.9858 | 61.7477 | 0.0026703 | 0.019734 | 0.011551 | -0.0014611 | 0.064615 | -0.0048685 | 0.071038 | -62.146 | 61.9171 | -62.1964 | -62.0132 | 61.4365 | 0.15106 | 0.10986 | 0.17853 | 61.9125 | -62.2147 | -0.21057 | 0.16937 | -0.16022 | -0.027466 | -0.31128 | -0.22888 | 0.16479 | 0.050354 | 62.0956 | 62.1643 | 123.4222 | 123.9029 | -0.16022 | 123.8983 | 62.1368 | -0.22888 | 123.9029 | -0.16022 | 62.1368 | 123.4222 | 123.8983 | -123.9441 | -123.9624
77.625 | 123.999 | -61.9858 | 61.7386 | 0.0026703 | 0.016317 | 0.014114 | 3.4284e-05 | 0.064401 | -0.0040139 | 0.072106 | -62.1414 | 61.8668 | -62.2055 | -62.0132 | 61.4365 | 0.16479 | 0.10529 | 0.19684 | 61.9034 | -62.1872 | -0.21973 | 0.12817 | -0.15564 | -0.027466 | -0.30212 | -0.20142 | 0.1648 | 0.064087 | 62.0911 | 62.1826 | 123.4222 | 123.8525 | -0.15564 | 123.8892 | 62.1506 | -0.20142 | 123.8525 | -0.15564 | 62.1506 | 123.4222 | 123.8892 | -123.9441 | -123.9258
79.2812 | 124.0128 | -61.9766 | 61.7615 | -0.0049592 | 0.020162 | 0.014114 | -0.00060672 | 0.064401 | -0.0061503 | 0.071252 | -62.1277 | 61.8805 | -62.2284 | -62.0178 | 61.4273 | 0.1831 | 0.11902 | 0.1831 | 61.9125 | -62.1872 | -0.25177 | 0.11902 | -0.15106 | -0.041198 | -0.33417 | -0.21057 | 0.15106 | 0.10071 | 62.0956 | 62.1597 | 123.4039 | 123.8571 | -0.15106 | 123.8892 | 62.1597 | -0.21057 | 123.8571 | -0.15106 | 62.1597 | 123.4039 | 123.8892 | -123.9899 | -123.9487
80.9375 | 123.999 | -61.9766 | 61.7523 | 0.0103 | 0.020803 | 0.017746 | -0.0025293 | 0.065896 | -0.0038003 | 0.070611 | -62.146 | 61.8301 | -62.2421 | -62.027 | 61.3907 | 0.10986 | -0.086975 | 0.064087 | 61.8256 | -62.1964 | -0.2655 | 0.07782 | -0.16937 | -0.050354 | -0.36163 | -0.21973 | 0.073243 | 0.09613 | 61.8896 | 62.0407 | 123.3673 | 123.8068 | -0.16937 | 123.8022 | 62.0865 | -0.21973 | 123.8068 | -0.16937 | 62.0865 | 123.3673 | 123.8022 | -123.9944 | -123.9487
82.625 | 123.9944 | -61.9858 | 61.7706 | 0.0103 | 0.019948 | 0.014969 | 0.0021705 | 0.068033 | -0.0052957 | 0.069543 | -62.1689 | 61.8118 | -62.2559 | -62.0453 | 61.3815 | 0.09613 | 0.004578 | 0.10071 | 61.8439 | -62.1872 | -0.27008 | 0.041199 | -0.1831 | -0.059509 | -0.3891 | -0.20142 | 0.073242 | 0.086975 | 61.9904 | 62.0865 | 123.3673 | 123.7976 | -0.1831 | 123.8297 | 62.0819 | -0.20142 | 123.7976 | -0.1831 | 62.0819 | 123.3673 | 123.8297 | -124.0265 | -123.9578
84.2812 | 123.999 | -61.9675 | 61.7477 | -0.0049592 | 0.020162 | 0.017105 | 3.4284e-05 | 0.066964 | -0.0033731 | 0.06997 | -62.1597 | 61.853 | -62.2375 | -62.0544 | 61.3861 | 0.082397 | -0.041199 | 0.064087 | 61.8393 | -62.2284 | -0.27008 | 0.10528 | -0.19226 | -0.086975 | -0.36163 | -0.26093 | 0.091552 | 0.07782 | 61.9263 | 62.0316 | 123.3536 | 123.8205 | -0.19226 | 123.8068 | 62.0499 | -0.26093 | 123.8205 | -0.19226 | 62.0499 | 123.3536 | 123.8068 | -123.9853 | -123.9761
85.9375 | 124.0219 | -61.9675 | 61.7386 | 0.0026703 | 0.020589 | 0.014541 | -0.0023157 | 0.066751 | -0.0042277 | 0.070825 | -62.1918 | 61.8164 | -62.2696 | -62.0728 | 61.3678 | 0.073242 | -0.027466 | 0.064087 | 61.8484 | -62.2055 | -0.30212 | 0.07782 | -0.2243 | -0.10529 | -0.37079 | -0.23804 | 0.10986 | 0.07782 | 61.94 | 62.0316 | 123.3353 | 123.7839 | -0.2243 | 123.8159 | 62.0407 | -0.23804 | 123.7839 | -0.2243 | 62.0407 | 123.3353 | 123.8159 | -124.0082 | -123.9441
87.6094 | 123.8617 | -61.9766 | 61.821 | -0.0049592 | 0.016957 | 0.016678 | -0.0048791 | 0.067605 | -0.0029459 | 0.071679 | -62.0453 | 61.8073 | -62.178 | -61.9171 | 61.5143 | 0.2243 | -0.23804 | 0.18768 | 61.8164 | -62.1689 | -0.20142 | -0.013733 | -0.068664 | 0.05951 | -0.3067 | -0.19226 | -0.004578 | 0.13275 | 61.7386 | 62.1643 | 123.4909 | 123.7839 | -0.068664 | 123.793 | 62.2009 | -0.19226 | 123.7839 | -0.068664 | 62.2009 | 123.4909 | 123.793 | -123.999 | -123.9899
89.2656 | 123.88 | -61.9858 | 61.7889 | -0.012589 | 0.01888 | 0.017319 | -0.0040247 | 0.064187 | -0.0040139 | 0.071893 | -62.0132 | 61.8301 | -62.1643 | -61.9125 | 61.5189 | 0.24719 | -0.009155 | 0.27008 | 61.8484 | -62.1735 | -0.17853 | 0.041199 | -0.027466 | 0.073242 | -0.27008 | -0.18768 | 0.05951 | 0.15106 | 61.9766 | 62.2559 | 123.5046 | 123.8159 | -0.027466 | 123.8342 | 62.233 | -0.18768 | 123.8159 | -0.027466 | 62.233 | 123.5046 | 123.8342 | -123.9532 | -123.9624
90.9375 | 123.9944 | -61.972 | 61.7615 | -0.0049592 | 0.019521 | 0.014328 | 0.00088868 | 0.065683 | -0.0059365 | 0.072106 | -62.1735 | 61.8027 | -62.2604 | -62.0407 | 61.3815 | 0.09613 | -0.036621 | 0.054932 | 61.8484 | -62.1872 | -0.28839 | 0.041198 | -0.20142 | -0.068664 | -0.37994 | -0.21515 | 0.086975 | 0.086975 | 61.9354 | 62.027 | 123.3536 | 123.7747 | -0.20142 | 123.8205 | 62.0682 | -0.21515 | 123.7747 | -0.20142 | 62.0682 | 123.3536 | 123.8205 | -124.0219 | -123.9487
92.6719 | 123.8663 | -61.9629 | 61.8393 | 0.0026703 | 0.016317 | 0.011551 | -0.0021021 | 0.062692 | -0.0046549 | 0.071038 | -62.0453 | 61.7569 | -62.178 | -61.9263 | 61.5143 | 0.21973 | -0.21515 | 0.19226 | 61.7844 | -62.1826 | -0.21515 | -0.082397 | -0.082397 | 0.036621 | -0.32501 | -0.21973 | -0.054931 | 0.13275 | 61.7477 | 62.1552 | 123.4772 | 123.7198 | -0.082397 | 123.7473 | 62.1826 | -0.21973 | 123.7198 | -0.082397 | 62.1826 | 123.4772 | 123.7473 | -124.0173 | -124.0219
94.3594 | 123.8846 | -61.9583 | 61.8484 | 0.0026703 | 0.023793 | 0.012192 | -0.0046655 | 0.064828 | -0.0052957 | 0.06997 | -62.0407 | 61.8484 | -62.146 | -61.94 | 61.4777 | 0.19226 | -0.14191 | 0.16479 | 61.8347 | -62.1506 | -0.18768 | 0 | -0.082397 | 0.018311 | -0.37079 | -0.19226 | -0.013733 | 0.10529 | 61.8164 | 62.1231 | 123.436 | 123.8068 | -0.082397 | 123.793 | 62.1506 | -0.19226 | 123.8068 | -0.082397 | 62.1506 | 123.436 | 123.793 | -123.9944 | -123.999
96.0312 | 123.9853 | -61.9675 | 61.7386 | 0.0026703 | 0.01888 | 0.015182 | -0.00017952 | 0.062478 | -0.0055093 | 0.068688 | -62.1506 | 61.8576 | -62.2055 | -61.9995 | 61.409 | 0.15106 | 0.10986 | 0.19226 | 61.8622 | -62.1826 | -0.23804 | 0.11902 | -0.18311 | -0.032044 | -0.32959 | -0.21515 | 0.1236 | 0.054931 | 62.0773 | 62.1597 | 123.3765 | 123.8251 | -0.18311 | 123.8297 | 62.1185 | -0.21515 | 123.8251 | -0.18311 | 62.1185 | 123.3765 | 123.8297 | -123.9441 | -123.9212
97.7031 | 123.8663 | -61.9904 | 61.7844 | 0.0026703 | 0.021016 | 0.01561 | 3.4284e-05 | 0.063547 | -0.0042277 | 0.06997 | -62.0544 | 61.8118 | -62.1689 | -61.9354 | 61.4777 | 0.21515 | -0.24261 | 0.18768 | 61.7844 | -62.1918 | -0.17853 | 0.027466 | -0.064087 | 0.054931 | -0.3067 | -0.20142 | 0 | 0.11444 | 61.7477 | 62.178 | 123.468 | 123.8022 | -0.064087 | 123.7747 | 62.2055 | -0.20142 | 123.8022 | -0.064087 | 62.2055 | 123.468 | 123.7747 | -123.9532 | -123.9761
99.3594 | 123.912 | -61.9858 | 61.7844 | -0.0049592 | 0.020162 | 0.018173 | -0.0014611 | 0.063547 | -0.0048685 | 0.070825 | -62.1002 | 61.8256 | -62.2101 | -61.9492 | 61.4456 | 0.16937 | -0.21057 | 0.15106 | 61.8027 | -62.1689 | -0.2243 | 0.041199 | -0.11444 | 0.036621 | -0.33874 | -0.1831 | 0.01831 | 0.10986 | 61.7752 | 62.1368 | 123.4314 | 123.8113 | -0.11444 | 123.7885 | 62.1552 | -0.1831 | 123.8113 | -0.11444 | 62.1552 | 123.4314 | 123.7885 | -123.9944 | -123.9532
101.0312 | 123.88 | -61.9949 | 61.7706 | 0.0026703 | 0.014608 | 0.014755 | -0.0033837 | 0.062692 | -0.0035867 | 0.068261 | -62.027 | 61.8622 | -62.1735 | -61.8713 | 61.5234 | 0.26093 | -0.013733 | 0.29297 | 61.821 | -62.146 | -0.17853 | 0.091553 | -0.032044 | 0.1236 | -0.24719 | -0.15106 | 0.050354 | 0.14648 | 61.9812 | 62.2879 | 123.5184 | 123.8571 | -0.032044 | 123.8159 | 62.2559 | -0.15106 | 123.8571 | -0.032044 | 62.2559 | 123.5184 | 123.8159 | -123.9441 | -123.9166
102.7188 | 123.848 | -62.0041 | 61.821 | -0.0049592 | 0.019521 | 0.014541 | -0.0029565 | 0.063119 | -0.0044413 | 0.068048 | -61.9858 | 61.8484 | -62.114 | -61.8484 | 61.5509 | 0.27008 | -0.10529 | 0.32501 | 61.8256 | -62.1231 | -0.10986 | 0.027466 | 0.01831 | 0.15564 | -0.27008 | -0.11902 | 0.004578 | 0.12817 | 61.8988 | 62.3291 | 123.555 | 123.8525 | 0.01831 | 123.8297 | 62.2742 | -0.11902 | 123.8525 | 0.01831 | 62.2742 | 123.555 | 123.8297 | -123.9349 | -123.9441
104.375 | 123.9029 | -61.972 | 61.7935 | -0.012589 | 0.01888 | 0.015182 | -0.0042383 | 0.063547 | -0.0035867 | 0.068688 | -62.059 | 61.8484 | -62.1277 | -61.9034 | 61.5051 | 0.22888 | -0.10529 | 0.22888 | 61.8439 | -62.1368 | -0.15564 | 0.054932 | -0.086975 | 0.068665 | -0.28839 | -0.16479 | 0.050354 | 0.068665 | 61.8668 | 62.2009 | 123.4772 | 123.8205 | -0.086975 | 123.8159 | 62.2009 | -0.16479 | 123.8205 | -0.086975 | 62.2009 | 123.4772 | 123.8159 | -123.9212 | -123.9304
106.0469 | 123.967 | -61.9629 | 61.7386 | 0.0026703 | 0.021443 | 0.016037 | 0.0030249 | 0.064615 | -0.0052957 | 0.071252 | -62.1597 | 61.8118 | -62.2604 | -62.0224 | 61.3403 | 0.082397 | -0.009155 | 0.082397 | 61.8256 | -62.1597 | -0.29755 | 0.073243 | -0.19684 | -0.059509 | -0.39825 | -0.19684 | 0.086976 | 0.10071 | 61.9537 | 62.0453 | 123.3032 | 123.7747 | -0.19684 | 123.7885 | 62.0453 | -0.19684 | 123.7747 | -0.19684 | 62.0453 | 123.3032 | 123.7885 | -123.999 | -123.8983
107.7344 | 123.9578 | -61.9537 | 61.7386 | -0.012589 | 0.020375 | 0.013687 | 0.0015295 | 0.064615 | -0.0046549 | 0.069116 | -62.1414 | 61.7798 | -62.2787 | -62.027 | 61.3586 | 0.10071 | -0.027466 | 0.10071 | 61.8164 | -62.2101 | -0.32501 | 0.041199 | -0.18768 | -0.073243 | -0.37994 | -0.25635 | 0.07782 | 0.13733 | 61.9263 | 62.0544 | 123.3124 | 123.7335 | -0.18768 | 123.7701 | 62.0544 | -0.25635 | 123.7335 | -0.18768 | 62.0544 | 123.3124 | 123.7701 | -124.0173 | -123.9487
109.4219 | 123.9487 | -61.9675 | 61.7386 | -0.0049592 | 0.020375 | 0.014328 | -0.0031701 | 0.064828 | -0.0067911 | 0.069329 | -62.0865 | 61.8576 | -62.1643 | -61.9675 | 61.4273 | 0.15564 | 0.082397 | 0.21515 | 61.8668 | -62.1597 | -0.19684 | 0.11902 | -0.11902 | 0 | -0.31128 | -0.19226 | 0.12817 | 0.07782 | 62.0499 | 62.1826 | 123.3948 | 123.8251 | -0.11902 | 123.8342 | 62.1231 | -0.19226 | 123.8251 | -0.11902 | 62.1231 | 123.3948 | 123.8342 | -123.9029 | -123.8983
111.0781 | 123.9441 | -61.9812 | 61.7111 | 0.0026703 | 0.020375 | 0.011764 | 0.00067508 | 0.067178 | -0.0035867 | 0.071038 | -62.114 | 61.7889 | -62.2375 | -61.9949 | 61.3815 | 0.1236 | -0.032043 | 0.11902 | 61.8118 | -62.2009 | -0.25635 | 0.077819 | -0.13275 | -0.013733 | -0.32959 | -0.21973 | 0.10071 | 0.1236 | 61.9492 | 62.1002 | 123.3627 | 123.7701 | -0.13275 | 123.793 | 62.1048 | -0.21973 | 123.7701 | -0.13275 | 62.1048 | 123.3627 | 123.793 | -123.9487 | -123.912
112.8125 | 123.9075 | -61.9766 | 61.7111 | -0.0049592 | 0.022725 | 0.01326 | -0.0012475 | 0.066751 | -0.0033731 | 0.069757 | -62.0682 | 61.8484 | -62.2009 | -61.9354 | 61.4365 | 0.16937 | -0.018311 | 0.20599 | 61.8393 | -62.1918 | -0.2243 | 0.13733 | -0.091552 | 0.041199 | -0.27466 | -0.21515 | 0.12817 | 0.13275 | 61.9583 | 62.1826 | 123.4131 | 123.8251 | -0.091552 | 123.8159 | 62.146 | -0.21515 | 123.8251 | -0.091552 | 62.146 | 123.4131 | 123.8159 | -123.912 | -123.9029
114.5312 | 123.912 | -61.9949 | 61.7249 | -0.0049592 | 0.019734 | 0.017105 | -0.00082032 | 0.067819 | -0.0061503 | 0.070397 | -62.0819 | 61.7889 | -62.2284 | -61.9583 | 61.4365 | 0.16937 | -0.009155 | 0.21973 | 61.8118 | -62.1643 | -0.23346 | 0.064086 | -0.086975 | 0.036621 | -0.28839 | -0.16937 | 0.086975 | 0.14648 | 61.9858 | 62.2147 | 123.4314 | 123.7839 | -0.086975 | 123.8068 | 62.1643 | -0.16937 | 123.7839 | -0.086975 | 62.1643 | 123.4314 | 123.8068 | -123.9532 | -123.8892
116.1875 | 123.9304 | -61.94 | 61.7523 | -0.0049592 | 0.018025 | 0.013046 | -0.0044519 | 0.065256 | -0.0033731 | 0.071466 | -62.0728 | 61.8759 | -62.1689 | -61.9537 | 61.4502 | 0.16937 | 0.082397 | 0.19684 | 61.8851 | -62.1597 | -0.22888 | 0.1236 | -0.13275 | -0.013733 | -0.30212 | -0.21973 | 0.13275 | 0.09613 | 62.0224 | 62.1368 | 123.3902 | 123.8159 | -0.13275 | 123.8251 | 62.1094 | -0.21973 | 123.8159 | -0.13275 | 62.1094 | 123.3902 | 123.8251 | -123.9212 | -123.912
117.8906 | 123.9624 | -61.9537 | 61.7203 | 0.0026703 | 0.019948 | 0.017959 | 0.0015295 | 0.065896 | -0.0059365 | 0.068261 | -62.1414 | 61.8118 | -62.2559 | -62.0224 | 61.3632 | 0.091553 | 0.018311 | 0.10071 | 61.8301 | -62.1735 | -0.30212 | 0.091553 | -0.18768 | -0.068665 | -0.35706 | -0.21973 | 0.10986 | 0.11444 | 61.972 | 62.0544 | 123.317 | 123.7656 | -0.18768 | 123.7839 | 62.0453 | -0.21973 | 123.7656 | -0.18768 | 62.0453 | 123.317 | 123.7839 | -123.9761 | -123.8937
119.6094 | 123.8525 | -61.9354 | 61.8073 | -0.020218 | 0.019094 | 0.0092007 | -0.0076563 | 0.065042 | -0.0012369 | 0.071252 | -62.0361 | 61.8439 | -62.1277 | -61.9217 | 61.4777 | 0.18768 | -0.15106 | 0.17853 | 61.8347 | -62.1735 | -0.19226 | 0.036621 | -0.10071 | 0.013733 | -0.32959 | -0.23804 | 0.027466 | 0.091553 | 61.7844 | 62.114 | 123.4131 | 123.7793 | -0.10071 | 123.7701 | 62.1231 | -0.23804 | 123.7793 | -0.10071 | 62.1231 | 123.4131 | 123.7701 | -123.9349 | -123.9807
121.3125 | 123.9395 | -61.9354 | 61.7157 | 0.0026703 | 0.02123 | 0.014969 | 3.4284e-05 | 0.065256 | -0.0048685 | 0.07232 | -62.1231 | 61.821 | -62.2375 | -62.0224 | 61.3541 | 0.086975 | -0.059509 | 0.068665 | 61.8027 | -62.1872 | -0.30212 | 0.10529 | -0.18768 | -0.086975 | -0.36163 | -0.25177 | 0.086975 | 0.11444 | 61.8759 | 62.0041 | 123.2895 | 123.7564 | -0.18768 | 123.7381 | 62.0224 | -0.25177 | 123.7564 | -0.18768 | 62.0224 | 123.2895 | 123.7381 | -123.9532 | -123.9029
122.9844 | 123.8663 | -61.9354 | 61.7752 | -0.012589 | 0.020589 | 0.013901 | -0.0061609 | 0.06376 | -0.0020913 | 0.070825 | -62.059 | 61.8484 | -62.1506 | -61.9125 | 61.4777 | 0.23804 | -0.10529 | 0.21515 | 61.8118 | -62.1277 | -0.21515 | 0.073242 | -0.1236 | 0.022888 | -0.29755 | -0.19226 | 0.036621 | 0.091553 | 61.8301 | 62.1506 | 123.4131 | 123.7839 | -0.1236 | 123.7473 | 62.1735 | -0.19226 | 123.7839 | -0.1236 | 62.1735 | 123.4131 | 123.7473 | -123.9258 | -123.9029
124.6562 | 123.8205 | -61.9858 | 61.7661 | -0.0049592 | 0.019734 | 0.011337 | -0.0027429 | 0.063333 | -0.0010233 | 0.071038 | -61.9995 | 61.8073 | -62.1506 | -61.8347 | 61.5463 | 0.29755 | -0.10071 | 0.3067 | 61.8118 | -62.1323 | -0.16479 | 0.041199 | -0.013733 | 0.15106 | -0.21973 | -0.14648 | 0.045777 | 0.15106 | 61.8851 | 62.2925 | 123.5321 | 123.793 | -0.013733 | 123.7976 | 62.2833 | -0.14648 | 123.793 | -0.013733 | 62.2833 | 123.5321 | 123.7976 | -123.9166 | -123.8983
126.3281 | 123.8342 | -61.9492 | 61.7935 | -0.0049592 | 0.017812 | 0.01561 | -0.0018885 | 0.06376 | -0.0048685 | 0.070397 | -62.0224 | 61.7889 | -62.1643 | -61.8896 | 61.4822 | 0.21973 | -0.2243 | 0.19226 | 61.7661 | -62.146 | -0.21515 | -0.004578 | -0.073242 | 0.05951 | -0.31128 | -0.19684 | -0.027466 | 0.14191 | 61.7249 | 62.1414 | 123.4314 | 123.7381 | -0.073242 | 123.7152 | 62.1689 | -0.19684 | 123.7381 | -0.073242 | 62.1689 | 123.4314 | 123.7152 | -123.9578 | -123.9395
128 | 123.9349 | -61.9537 | 61.7065 | 0.0026703 | 0.018453 | 0.015396 | -0.00060672 | 0.065256 | -0.0048685 | 0.069329 | -62.1002 | 61.8576 | -62.2055 | -61.9583 | 61.3907 | 0.15564 | 0.082397 | 0.17853 | 61.8713 | -62.1643 | -0.25177 | 0.15106 | -0.14648 | -0.004578 | -0.31586 | -0.21057 | 0.16479 | 0.10529 | 62.0361 | 62.1323 | 123.3444 | 123.8113 | -0.14648 | 123.8251 | 62.1094 | -0.21057 | 123.8113 | -0.14648 | 62.1094 | 123.3444 | 123.8251 | -123.912 | -123.8709
129.6719 | 123.8709 | -61.9217 | 61.7981 | -0.012589 | 0.017812 | 0.016464 | -0.0055199 | 0.064828 | -0.0046549 | 0.069116 | -62.027 | 61.821 | -62.1277 | -61.9125 | 61.4548 | 0.20142 | -0.13733 | 0.16022 | 61.8256 | -62.1414 | -0.20599 | 0.022888 | -0.10529 | 0.009155 | -0.34332 | -0.21973 | 0.027466 | 0.10071 | 61.7844 | 62.0819 | 123.3765 | 123.7427 | -0.10529 | 123.7473 | 62.1231 | -0.21973 | 123.7427 | -0.10529 | 62.1231 | 123.3765 | 123.7473 | -123.9258 | -123.9395
131.3438 | 123.9578 | -61.972 | 61.7294 | -0.0049592 | 0.019094 | 0.016037 | 0.00088868 | 0.067178 | -0.0044413 | 0.071252 | -62.1414 | 61.821 | -62.2559 | -62.0087 | 61.3358 | 0.07782 | 0.009155 | 0.10071 | 61.8439 | -62.1552 | -0.28381 | 0.091553 | -0.16937 | -0.036621 | -0.39368 | -0.1831 | 0.11444 | 0.11444 | 61.9812 | 62.0728 | 123.3078 | 123.793 | -0.16937 | 123.8159 | 62.0499 | -0.1831 | 123.793 | -0.16937 | 62.0499 | 123.3078 | 123.8159 | -123.9853 | -123.8846
133.0156 | 123.8068 | -61.9446 | 61.7935 | 0.0026703 | 0.017598 | 0.010269 | -0.00060672 | 0.063333 | -0.0033731 | 0.070611 | -61.9995 | 61.8118 | -62.1689 | -61.8759 | 61.4777 | 0.21515 | -0.21515 | 0.1831 | 61.7889 | -62.1277 | -0.2243 | 0.018311 | -0.054932 | 0.068664 | -0.31586 | -0.18311 | -0.004578 | 0.16937 | 61.7294 | 62.1277 | 123.4222 | 123.7564 | -0.054932 | 123.7335 | 62.1597 | -0.18311 | 123.7564 | -0.054932 | 62.1597 | 123.4222 | 123.7335 | -123.9624 | -123.9212
134.7188 | 123.9532 | -61.94 | 61.702 | -0.0049592 | 0.02358 | 0.014969 | 0.0015295 | 0.065469 | -0.0040139 | 0.071252 | -62.1323 | 61.7935 | -62.233 | -62.0224 | 61.3403 | 0.068665 | -0.022888 | 0.059509 | 61.853 | -62.1552 | -0.29297 | 0.091553 | -0.19226 | -0.082398 | -0.36163 | -0.21515 | 0.15106 | 0.10071 | 61.9171 | 61.9995 | 123.2803 | 123.7335 | -0.19226 | 123.793 | 62.0087 | -0.21515 | 123.7335 | -0.19226 | 62.0087 | 123.2803 | 123.793 | -123.9349 | -123.8571
136.4219 | 123.8251 | -61.9629 | 61.7569 | -0.0049592 | 0.018666 | 0.01625 | -0.0055199 | 0.062692 | -0.0042277 | 0.069757 | -61.9904 | 61.7935 | -62.1643 | -61.8576 | 61.5143 | 0.25177 | -0.013733 | 0.27008 | 61.8256 | -62.1094 | -0.20142 | 0.036621 | -0.027465 | 0.10529 | -0.24262 | -0.14648 | 0.068665 | 0.17395 | 61.9492 | 62.233 | 123.4772 | 123.7564 | -0.027465 | 123.7885 | 62.2147 | -0.14648 | 123.7564 | -0.027465 | 62.2147 | 123.4772 | 123.7885 | -123.9212 | -123.8663
138.1094 | 123.8937 | -61.9675 | 61.7111 | 0.0026703 | 0.019948 | 0.01326 | 3.4284e-05 | 0.065896 | -0.0065775 | 0.06997 | -62.059 | 61.8073 | -62.2147 | -61.9354 | 61.4136 | 0.17395 | -0.018311 | 0.20599 | 61.8118 | -62.1506 | -0.24719 | 0.09613 | -0.091553 | 0.032043 | -0.29755 | -0.18311 | 0.10071 | 0.15564 | 61.9492 | 62.1735 | 123.381 | 123.7747 | -0.091553 | 123.7793 | 62.1414 | -0.18311 | 123.7747 | -0.091553 | 62.1414 | 123.381 | 123.7793 | -123.9258 | -123.8617
139.8281 | 123.9304 | -61.9308 | 61.7111 | -0.012589 | 0.019948 | 0.011764 | -0.0023157 | 0.064187 | -0.0025187 | 0.068688 | -62.0956 | 61.8622 | -62.1918 | -61.972 | 61.3998 | 0.14648 | 0.11444 | 0.16022 | 61.8622 | -62.1414 | -0.26093 | 0.15106 | -0.16479 | -0.041199 | -0.31128 | -0.21057 | 0.15106 | 0.09613 | 62.0453 | 62.0911 | 123.3307 | 123.793 | -0.16479 | 123.793 | 62.0773 | -0.21057 | 123.793 | -0.16479 | 62.0773 | 123.3307 | 123.793 | -123.9029 | -123.8525
141.5 | 123.8663 | -61.9629 | 61.702 | 0.0026703 | 0.018666 | 0.018173 | -0.0010339 | 0.065469 | -0.0055093 | 0.070397 | -62.0682 | 61.7752 | -62.2147 | -61.9308 | 61.4044 | 0.16937 | -0.027466 | 0.19684 | 61.8073 | -62.1506 | -0.25177 | 0.073243 | -0.10529 | 0.032044 | -0.29755 | -0.18768 | 0.10529 | 0.14648 | 61.9354 | 62.1597 | 123.3673 | 123.7381 | -0.10529 | 123.7701 | 62.1323 | -0.18768 | 123.7381 | -0.10529 | 62.1323 | 123.3673 | 123.7701 | -123.9166 | -123.8525
143.1719 | 123.7976 | -61.9446 | 61.8164 | -0.012589 | 0.017171 | 0.013046 | -0.0063745 | 0.065896 | -0.0059365 | 0.069543 | -61.972 | 61.8164 | -62.0911 | -61.8347 | 61.5189 | 0.28839 | -0.12817 | 0.27008 | 61.8347 | -62.0544 | -0.14648 | 0 | -0.027466 | 0.10986 | -0.29755 | -0.10986 | 0.018311 | 0.11902 | 61.8164 | 62.2147 | 123.4634 | 123.761 | -0.027466 | 123.7793 | 62.233 | -0.10986 | 123.761 | -0.027466 | 62.233 | 123.4634 | 123.7793 | -123.9075 | -123.8708
144.875 | 123.7976 | -61.9354 | 61.7935 | -0.012589 | 0.015676 | 0.010055 | -0.0050927 | 0.062478 | -0.0038003 | 0.06997 | -61.9583 | 61.7935 | -62.1185 | -61.8073 | 61.5417 | 0.28839 | -0.10986 | 0.31128 | 61.821 | -62.0865 | -0.1831 | 0 | -0.022888 | 0.12817 | -0.25177 | -0.15106 | 0.027466 | 0.16022 | 61.8256 | 62.2467 | 123.4772 | 123.7289 | -0.022888 | 123.7564 | 62.2238 | -0.15106 | 123.7289 | -0.022888 | 62.2238 | 123.4772 | 123.7564 | -123.912 | -123.88
146.5625 | 123.8297 | -61.9034 | 61.7844 | 0.0026703 | 0.019094 | 0.014328 | -0.0014611 | 0.061197 | -0.0029459 | 0.068902 | -62.0041 | 61.821 | -62.1002 | -61.8576 | 61.496 | 0.25177 | -0.10986 | 0.25177 | 61.8256 | -62.1048 | -0.19684 | 0.036621 | -0.10071 | 0.045776 | -0.28839 | -0.20142 | 0.041199 | 0.096131 | 61.7935 | 62.1552 | 123.3994 | 123.7244 | -0.10071 | 123.7289 | 62.1552 | -0.20142 | 123.7244 | -0.10071 | 62.1552 | 123.3994 | 123.7289 | -123.8846 | -123.8892
148.25 | 123.9258 | -61.9537 | 61.6974 | -0.0049592 | 0.021871 | 0.0186 | 0.0036657 | 0.064187 | -0.0048685 | 0.070611 | -62.114 | 61.8164 | -62.2101 | -61.9995 | 61.3266 | 0.07782 | -0.032043 | 0.050354 | 61.8073 | -62.178 | -0.25635 | 0.11902 | -0.16022 | -0.045777 | -0.37079 | -0.22431 | 0.10986 | 0.09613 | 61.9217 | 62.0041 | 123.2803 | 123.7701 | -0.16022 | 123.761 | 62.0316 | -0.22431 | 123.7701 | -0.16022 | 62.0316 | 123.2803 | 123.761 | -123.9075 | -123.8754
149.9375 | 123.8754 | -61.9675 | 61.6745 | -0.0049592 | 0.019307 | 0.014328 | -0.00060672 | 0.064828 | -0.0067911 | 0.06997 | -62.0728 | 61.8164 | -62.2147 | -61.9354 | 61.409 | 0.16479 | 0.027466 | 0.21057 | 61.8118 | -62.1323 | -0.24719 | 0.14191 | -0.10529 | 0.032043 | -0.2655 | -0.1648 | 0.13733 | 0.14191 | 61.9949 | 62.178 | 123.3765 | 123.7839 | -0.10529 | 123.7793 | 62.1323 | -0.1648 | 123.7839 | -0.10529 | 62.1323 | 123.3765 | 123.7793 | -123.8892 | -123.8068
151.6562 | 123.7885 | -61.9171 | 61.7981 | 0.0026703 | 0.020375 | 0.014541 | -0.0063745 | 0.065042 | -0.0033731 | 0.069329 | -61.9446 | 61.8164 | -62.1323 | -61.7935 | 61.5417 | 0.29297 | -0.11444 | 0.28839 | 61.8073 | -62.1002 | -0.21515 | 0.01831 | -0.027466 | 0.1236 | -0.25635 | -0.18311 | 0.009155 | 0.18768 | 61.8027 | 62.2055 | 123.4589 | 123.7335 | -0.027466 | 123.7244 | 62.2101 | -0.18311 | 123.7335 | -0.027466 | 62.2101 | 123.4589 | 123.7244 | -123.9304 | -123.8983
153.3281 | 123.8159 | -61.9217 | 61.7798 | -0.020218 | 0.016317 | 0.01326 | -0.0050927 | 0.062692 | -0.0020913 | 0.069329 | -62.0041 | 61.8256 | -62.1094 | -61.8301 | 61.5097 | 0.27008 | -0.10986 | 0.25177 | 61.8439 | -62.0865 | -0.18768 | 0.045777 | -0.082397 | 0.091553 | -0.27008 | -0.16479 | 0.064087 | 0.10529 | 61.8118 | 62.1735 | 123.4314 | 123.7473 | -0.082397 | 123.7656 | 62.1918 | -0.16479 | 123.7473 | -0.082397 | 62.1918 | 123.4314 | 123.7656 | -123.8892 | -123.8663
155.0156 | 123.8434 | -61.9034 | 61.7661 | 0.0103 | 0.019094 | 0.013046 | -0.0021021 | 0.06376 | -0.0048685 | 0.070397 | -62.027 | 61.8073 | -62.1277 | -61.8988 | 61.441 | 0.17853 | -0.10986 | 0.16937 | 61.8073 | -62.1185 | -0.2243 | 0.041199 | -0.1236 | 0.004577 | -0.32501 | -0.21515 | 0.041199 | 0.10071 | 61.7935 | 62.0728 | 123.3444 | 123.7106 | -0.1236 | 123.7106 | 62.0819 | -0.21515 | 123.7106 | -0.1236 | 62.0819 | 123.3444 | 123.7106 | -123.8937 | -123.8846
156.6719 | 123.9029 | -61.9492 | 61.6882 | 0.0026703 | 0.022084 | 0.016678 | 0.0023841 | 0.066964 | -0.0048685 | 0.069757 | -62.1048 | 61.7615 | -62.2467 | -61.9812 | 61.3358 | 0.086975 | -0.027466 | 0.10529 | 61.7798 | -62.2055 | -0.29755 | 0.073243 | -0.15564 | -0.032043 | -0.35248 | -0.25635 | 0.091553 | 0.14191 | 61.9217 | 62.0544 | 123.2849 | 123.7106 | -0.15564 | 123.7289 | 62.0361 | -0.25635 | 123.7106 | -0.15564 | 62.0361 | 123.2849 | 123.7289 | -123.9349 | -123.8937
158.3281 | 123.7885 | -61.9217 | 61.7844 | 0.0026703 | 0.016744 | 0.011337 | -0.0035973 | 0.064615 | -0.0044413 | 0.071038 | -61.9583 | 61.7935 | -62.0819 | -61.8164 | 61.5143 | 0.28839 | -0.14191 | 0.27924 | 61.7981 | -62.0819 | -0.16022 | 0.009155 | -0.036621 | 0.10529 | -0.27008 | -0.16022 | 0.013733 | 0.1236 | 61.7798 | 62.2009 | 123.436 | 123.7152 | -0.036621 | 123.7198 | 62.2101 | -0.16022 | 123.7152 | -0.036621 | 62.2101 | 123.436 | 123.7198 | -123.8663 | -123.8663
160 | 123.8617 | -61.9217 | 61.7294 | -0.0049592 | 0.01888 | 0.019455 | 0.00088868 | 0.064828 | -0.0038003 | 0.071038 | -62.059 | 61.8027 | -62.1826 | -61.9171 | 61.3953 | 0.14191 | -0.16479 | 0.13275 | 61.7752 | -62.1414 | -0.26093 | 0.073242 | -0.13733 | 0.004578 | -0.33417 | -0.21973 | 0.045777 | 0.1236 | 61.7569 | 62.0544 | 123.317 | 123.7244 | -0.13733 | 123.6969 | 62.0636 | -0.21973 | 123.7244 | -0.13733 | 62.0636 | 123.317 | 123.6969 | -123.912 | -123.8708
161.6875 | 123.7701 | -61.9354 | 61.7752 | 0.0026703 | 0.016317 | 0.01561 | -0.0014611 | 0.063119 | -0.0033731 | 0.070825 | -61.9812 | 61.7523 | -62.1552 | -61.8713 | 61.4594 | 0.21057 | -0.21973 | 0.1831 | 61.7523 | -62.1048 | -0.21973 | -0.022889 | -0.045776 | 0.064087 | -0.31586 | -0.16937 | -0.022889 | 0.17395 | 61.7157 | 62.1185 | 123.3948 | 123.6877 | -0.045776 | 123.6877 | 62.146 | -0.16937 | 123.6877 | -0.045776 | 62.146 | 123.3948 | 123.6877 | -123.9304 | -123.88
163.3594 | 123.8983 | -61.9308 | 61.6837 | 0.0026703 | 0.019521 | 0.012832 | -0.00082032 | 0.062692 | -0.0014505 | 0.073388 | -62.0773 | 61.8164 | -62.1918 | -61.9354 | 61.3907 | 0.15564 | 0.10071 | 0.19684 | 61.8439 | -62.1323 | -0.26093 | 0.13275 | -0.14648 | -0.004578 | -0.29297 | -0.20142 | 0.16022 | 0.11444 | 62.0316 | 62.1277 | 123.3215 | 123.7473 | -0.14648 | 123.7747 | 62.0865 | -0.20142 | 123.7473 | -0.14648 | 62.0865 | 123.3215 | 123.7747 | -123.8754 | -123.8159
165.0625 | 123.848 | -61.9217 | 61.7203 | 0.0026703 | 0.018666 | 0.017105 | 0.0017431 | 0.063974 | -0.0057229 | 0.070397 | -62.0773 | 61.7661 | -62.178 | -61.9125 | 61.3815 | 0.14648 | -0.16022 | 0.1236 | 61.7523 | -62.0956 | -0.25635 | 0.045776 | -0.15564 | 0.009155 | -0.33874 | -0.17395 | 0.032043 | 0.10071 | 61.7615 | 62.0453 | 123.3032 | 123.6877 | -0.15564 | 123.674 | 62.0682 | -0.17395 | 123.6877 | -0.15564 | 62.0682 | 123.3032 | 123.674 | -123.8983 | -123.8159
166.7344 | 123.7747 | -61.9263 | 61.7615 | 0.0026703 | 0.018666 | 0.019027 | -0.0010339 | 0.064828 | -0.0020913 | 0.068688 | -61.9949 | 61.7615 | -62.1414 | -61.8484 | 61.4548 | 0.21973 | -0.26093 | 0.19684 | 61.7477 | -62.1506 | -0.21515 | 0 | -0.068664 | 0.07782 | -0.3067 | -0.2243 | -0.013733 | 0.14648 | 61.6653 | 62.1231 | 123.381 | 123.6877 | -0.068664 | 123.674 | 62.146 | -0.2243 | 123.6877 | -0.068664 | 62.146 | 123.381 | 123.674 | -123.9029 | -123.912
168.4062 | 123.8205 | -61.9034 | 61.7798 | -0.0049592 | 0.019307 | 0.014328 | -0.0061609 | 0.062051 | -0.0020913 | 0.069757 | -62.0224 | 61.8027 | -62.114 | -61.8851 | 61.4319 | 0.19684 | -0.10986 | 0.16937 | 61.7935 | -62.1094 | -0.21057 | 0.022888 | -0.11902 | 0.01831 | -0.3479 | -0.20599 | 0.013733 | 0.091553 | 61.7935 | 62.0728 | 123.3353 | 123.7061 | -0.11902 | 123.6969 | 62.1002 | -0.20599 | 123.7061 | -0.11902 | 62.1002 | 123.3353 | 123.6969 | -123.8937 | -123.8892
170.0938 | 123.8754 | -61.908 | 61.7249 | -0.0049592 | 0.017812 | 0.014969 | 3.4284e-05 | 0.064615 | -0.0046549 | 0.069329 | -62.0865 | 61.7615 | -62.2238 | -61.9629 | 61.3403 | 0.09613 | -0.13733 | 0.086975 | 61.7661 | -62.1414 | -0.31586 | 0.036621 | -0.17853 | -0.054932 | -0.38452 | -0.23346 | 0.041198 | 0.13733 | 61.7706 | 61.9949 | 123.2483 | 123.6694 | -0.17853 | 123.674 | 62.0041 | -0.23346 | 123.6694 | -0.17853 | 62.0041 | 123.2483 | 123.674 | -123.9487 | -123.8663
171.8281 | 123.7656 | -61.94 | 61.7477 | -0.0049592 | 0.018025 | 0.017319 | -0.0057337 | 0.060983 | -0.0025187 | 0.070611 | -61.9537 | 61.7889 | -62.0911 | -61.7798 | 61.5189 | 0.29297 | -0.10071 | 0.32501 | 61.7935 | -62.0911 | -0.15106 | 0.041198 | -0.013733 | 0.16022 | -0.22888 | -0.15106 | 0.045776 | 0.13733 | 61.8393 | 62.265 | 123.4589 | 123.7289 | -0.013733 | 123.7335 | 62.233 | -0.15106 | 123.7289 | -0.013733 | 62.233 | 123.4589 | 123.7335 | -123.8388 | -123.8388
173.5 | 123.8892 | -61.9125 | 61.7157 | -0.0049592 | 0.019948 | 0.016678 | 3.4284e-05 | 0.063547 | -0.0048685 | 0.070184 | -62.1048 | 61.7889 | -62.2238 | -61.9629 | 61.3312 | 0.082397 | -0.054932 | 0.082397 | 61.7798 | -62.1597 | -0.31128 | 0.073242 | -0.19226 | -0.050354 | -0.38452 | -0.24719 | 0.064087 | 0.11902 | 61.8576 | 61.9949 | 123.2437 | 123.7015 | -0.19226 | 123.6923 | 61.9949 | -0.24719 | 123.7015 | -0.19226 | 61.9949 | 123.2437 | 123.6923 | -123.9395 | -123.8754
175.1719 | 123.8846 | -61.8942 | 61.6699 | -0.0049592 | 0.018453 | 0.015823 | 0.0019569 | 0.062265 | -0.0025187 | 0.067407 | -62.0682 | 61.853 | -62.1552 | -61.94 | 61.3632 | 0.15564 | 0.10986 | 0.17853 | 61.8118 | -62.114 | -0.26092 | 0.1831 | -0.17395 | -0.045776 | -0.3067 | -0.21973 | 0.14191 | 0.086975 | 62.0041 | 62.0728 | 123.2574 | 123.7473 | -0.17395 | 123.7061 | 62.0499 | -0.21973 | 123.7473 | -0.17395 | 62.0499 | 123.2574 | 123.7061 | -123.8251 | -123.7839
176.875 | 123.7518 | -61.94 | 61.7432 | -0.0049592 | 0.021443 | 0.016037 | -0.0027429 | 0.062692 | -0.0023049 | 0.06762 | -61.9858 | 61.7661 | -62.1185 | -61.8393 | 61.4594 | 0.21515 | -0.23346 | 0.20142 | 61.7386 | -62.1094 | -0.17853 | 0.022888 | -0.045777 | 0.10071 | -0.28381 | -0.16937 | -0.004578 | 0.13275 | 61.7065 | 62.1414 | 123.3994 | 123.7061 | -0.045777 | 123.6786 | 62.1552 | -0.16937 | 123.7061 | -0.045777 | 62.1552 | 123.3994 | 123.6786 | -123.8617 | -123.8525
178.5469 | 123.8251 | -61.9263 | 61.6928 | -0.0049592 | 0.019521 | 0.019455 | 0.0017431 | 0.065042 | -0.0038003 | 0.070184 | -62.0499 | 61.7844 | -62.2009 | -61.9125 | 61.3678 | 0.16937 | -0.022888 | 0.16937 | 61.7889 | -62.1323 | -0.27466 | 0.091553 | -0.1236 | 0.013733 | -0.32501 | -0.20599 | 0.09613 | 0.15106 | 61.9034 | 62.0956 | 123.2941 | 123.7106 | -0.1236 | 123.7152 | 62.0956 | -0.20599 | 123.7106 | -0.1236 | 62.0956 | 123.2941 | 123.7152 | -123.8937 | -123.8251
180.2188 | 123.7289 | -61.8896 | 61.7798 | -0.012589 | 0.018453 | 0.0098417 | -0.0050927 | 0.063333 | -0.0029459 | 0.070397 | -61.9354 | 61.8118 | -62.0911 | -61.7981 | 61.5051 | 0.27466 | -0.13275 | 0.29755 | 61.7844 | -62.059 | -0.20142 | 0.032044 | -0.045777 | 0.091552 | -0.27466 | -0.16937 | 0.004578 | 0.15564 | 61.7569 | 62.1872 | 123.3948 | 123.7015 | -0.045777 | 123.674 | 62.1643 | -0.16937 | 123.7015 | -0.045777 | 62.1643 | 123.3948 | 123.674 | -123.8708 | -123.8388
181.9062 | 123.7381 | -61.9354 | 61.7706 | -0.0049592 | 0.020375 | 0.017105 | -0.0029565 | 0.063333 | -0.0042277 | 0.069543 | -61.9675 | 61.7294 | -62.1231 | -61.8347 | 61.4502 | 0.21515 | -0.22888 | 0.19684 | 61.7569 | -62.0911 | -0.18768 | -0.041199 | -0.032043 | 0.10071 | -0.32043 | -0.15564 | -0.013733 | 0.15564 | 61.7065 | 62.1323 | 123.3856 | 123.6649 | -0.032043 | 123.6923 | 62.1506 | -0.15564 | 123.6649 | -0.032043 | 62.1506 | 123.3856 | 123.6923 | -123.8937 | -123.8617
183.5781 | 123.7518 | -61.9171 | 61.7752 | 0.0026703 | 0.015889 | 0.010055 | -0.0035973 | 0.060983 | -0.0042277 | 0.071466 | -61.9537 | 61.8118 | -62.0682 | -61.8073 | 61.496 | 0.28839 | -0.14648 | 0.28839 | 61.7889 | -62.0865 | -0.15106 | 0.036621 | -0.036621 | 0.10986 | -0.27924 | -0.16937 | 0.013732 | 0.11444 | 61.7706 | 62.2055 | 123.4131 | 123.7289 | -0.036621 | 123.7061 | 62.2055 | -0.16937 | 123.7289 | -0.036621 | 62.2055 | 123.4131 | 123.7061 | -123.8434 | -123.8617
185.25 | 123.8434 | -61.908 | 61.7157 | -0.0049592 | 0.02123 | 0.016464 | -0.00060672 | 0.063333 | -0.0035867 | 0.068048 | -62.0636 | 61.7661 | -62.1964 | -61.9537 | 61.3358 | 0.086975 | -0.10986 | 0.068665 | 61.7615 | -62.1323 | -0.28839 | 0.050354 | -0.15564 | -0.045776 | -0.37994 | -0.2243 | 0.045777 | 0.13275 | 61.7981 | 61.9766 | 123.2437 | 123.674 | -0.15564 | 123.6694 | 61.9949 | -0.2243 | 123.674 | -0.15564 | 61.9949 | 123.2437 | 123.6694 | -123.912 | -123.848
186.9375 | 123.8159 | -61.9308 | 61.6837 | 0.0103 | 0.021443 | 0.019668 | 0.00088868 | 0.064615 | -0.0044413 | 0.06997 | -62.0453 | 61.7844 | -62.178 | -61.8805 | 61.377 | 0.16479 | -0.009155 | 0.19684 | 61.7752 | -62.1231 | -0.24719 | 0.10071 | -0.11444 | 0.050354 | -0.3067 | -0.19226 | 0.091553 | 0.13275 | 61.9217 | 62.1277 | 123.3078 | 123.7152 | -0.11444 | 123.7061 | 62.0956 | -0.19226 | 123.7152 | -0.11444 | 62.0956 | 123.3078 | 123.7061 | -123.8617 | -123.8068
188.6094 | 123.7701 | -61.8851 | 61.7523 | 0.0026703 | 0.017385 | 0.01326 | -0.0068017 | 0.063547 | -0.0020913 | 0.068261 | -62.0087 | 61.8164 | -62.1048 | -61.8484 | 61.441 | 0.20142 | -0.11444 | 0.19226 | 61.7844 | -62.0544 | -0.21973 | 0.064087 | -0.1236 | 0.036621 | -0.31128 | -0.16937 | 0.032044 | 0.09613 | 61.7706 | 62.0773 | 123.3261 | 123.7015 | -0.1236 | 123.6694 | 62.0865 | -0.16937 | 123.7015 | -0.1236 | 62.0865 | 123.3261 | 123.6694 | -123.8571 | -123.8068
190.2969 | 123.8709 | -61.9263 | 61.6699 | 0.0103 | 0.020375 | 0.015182 | 0.0034521 | 0.065256 | -0.0059365 | 0.069543 | -62.0911 | 61.7798 | -62.2055 | -61.9766 | 61.29 | 0.068665 | 0.004578 | 0.086975 | 61.7661 | -62.1323 | -0.27923 | 0.10986 | -0.16479 | -0.050354 | -0.37994 | -0.20599 | 0.09613 | 0.11444 | 61.9308 | 62.0132 | 123.2162 | 123.7061 | -0.16479 | 123.6923 | 61.9949 | -0.20599 | 123.7061 | -0.16479 | 61.9949 | 123.2162 | 123.6923 | -123.8754 | -123.8022
191.9844 | 123.8571 | -61.9217 | 61.6699 | 0.0026703 | 0.020162 | 0.016037 | 0.00046148 | 0.064828 | -0.0061503 | 0.070825 | -62.0865 | 61.7569 | -62.1964 | -61.9583 | 61.3174 | 0.073242 | 0.009155 | 0.07782 | 61.7706 | -62.1277 | -0.27466 | 0.086975 | -0.16479 | -0.036621 | -0.35248 | -0.20599 | 0.10071 | 0.10986 | 61.9308 | 61.9995 | 123.2391 | 123.6786 | -0.16479 | 123.6923 | 61.9949 | -0.20599 | 123.6786 | -0.16479 | 61.9949 | 123.2391 | 123.6923 | -123.8663 | -123.7976
193.7031 | 123.8754 | -61.8896 | 61.6882 | -0.0049592 | 0.020162 | 0.01561 | -0.0014611 | 0.063119 | -0.0040139 | 0.071466 | -62.1002 | 61.7889 | -62.1872 | -61.9812 | 61.2991 | 0.086975 | -0.041199 | 0.073242 | 61.7615 | -62.114 | -0.29755 | 0.10071 | -0.21057 | -0.091553 | -0.3891 | -0.22431 | 0.073243 | 0.086975 | 61.8484 | 61.9629 | 123.1888 | 123.6786 | -0.21057 | 123.6511 | 61.9766 | -0.22431 | 123.6786 | -0.21057 | 61.9766 | 123.1888 | 123.6511 | -123.8754 | -123.8022
195.375 | 123.7335 | -61.9308 | 61.7477 | -0.0049592 | 0.019521 | 0.014328 | -0.0059473 | 0.06376 | -0.0046549 | 0.071252 | -61.9354 | 61.7935 | -62.0819 | -61.7981 | 61.4822 | 0.28839 | -0.07782 | 0.32501 | 61.7477 | -62.0636 | -0.15106 | 0.045776 | -0.004578 | 0.13275 | -0.2655 | -0.13275 | 0 | 0.14648 | 61.853 | 62.2559 | 123.4131 | 123.7244 | -0.004578 | 123.6786 | 62.2192 | -0.13275 | 123.7244 | -0.004578 | 62.2192 | 123.4131 | 123.6786 | -123.8297 | -123.8113
197.1875 | 123.8709 | -61.9171 | 61.6608 | 0.0026703 | 0.019948 | 0.015182 | 0.0019569 | 0.065469 | -0.0042277 | 0.06997 | -62.0865 | 61.7569 | -62.1964 | -61.972 | 61.2854 | 0.082397 | 0.004578 | 0.07782 | 61.7661 | -62.1048 | -0.27924 | 0.09613 | -0.16937 | -0.054932 | -0.37537 | -0.18768 | 0.10529 | 0.10986 | 61.9217 | 61.9949 | 123.2025 | 123.674 | -0.16937 | 123.6832 | 61.9995 | -0.18768 | 123.674 | -0.16937 | 61.9995 | 123.2025 | 123.6832 | -123.8571 | -123.7656
198.9375 | 123.7656 | -61.8851 | 61.7844 | -0.0049592 | 0.015889 | 0.011551 | -0.0038111 | 0.06611 | -0.0055093 | 0.068902 | -61.9949 | 61.734 | -62.1048 | -61.8576 | 61.4273 | 0.20142 | -0.16022 | 0.17853 | 61.7615 | -62.0544 | -0.21973 | -0.050354 | -0.10986 | 0.027466 | -0.35706 | -0.16937 | -0.022888 | 0.10986 | 61.7249 | 62.0636 | 123.3124 | 123.6191 | -0.10986 | 123.6465 | 62.0865 | -0.16937 | 123.6191 | -0.10986 | 62.0865 | 123.3124 | 123.6465 | -123.8892 | -123.8388
200.7031 | 123.7198 | -61.908 | 61.7477 | -0.020218 | 0.016957 | 0.014114 | -0.0046655 | 0.063333 | -0.0029459 | 0.069543 | -61.9446 | 61.7752 | -62.0865 | -61.7798 | 61.4868 | 0.28381 | -0.13275 | 0.32044 | 61.7752 | -62.0773 | -0.17853 | 0.027466 | -0.036621 | 0.12817 | -0.26093 | -0.16937 | 0.027466 | 0.14191 | 61.7752 | 62.2284 | 123.3948 | 123.6832 | -0.036621 | 123.6832 | 62.1918 | -0.16937 | 123.6832 | -0.036621 | 62.1918 | 123.3948 | 123.6832 | -123.8342 | -123.8251
202.4062 | 123.7564 | -61.8896 | 61.7294 | 0.0026703 | 0.019734 | 0.017105 | -0.0042383 | 0.06141 | -0.0031595 | 0.071466 | -61.9766 | 61.7889 | -62.0865 | -61.8164 | 61.4685 | 0.24261 | -0.10071 | 0.25177 | 61.7844 | -62.0773 | -0.19684 | 0.059509 | -0.086976 | 0.073242 | -0.26093 | -0.18768 | 0.054932 | 0.10986 | 61.7889 | 62.1414 | 123.3582 | 123.6786 | -0.086976 | 123.674 | 62.1323 | -0.18768 | 123.6786 | -0.086976 | 62.1323 | 123.3582 | 123.674 | -123.8159 | -123.8068
204.1562 | 123.7244 | -61.9263 | 61.7523 | -0.0049592 | 0.018666 | 0.016037 | -0.0018885 | 0.063547 | -0.0059365 | 0.068261 | -61.9263 | 61.7615 | -62.0819 | -61.7706 | 61.4914 | 0.29755 | -0.10529 | 0.32959 | 61.7935 | -62.0636 | -0.15564 | 0.009156 | 0 | 0.15564 | -0.26093 | -0.13733 | 0.041199 | 0.15564 | 61.821 | 62.2559 | 123.4177 | 123.6877 | 0 | 123.7198 | 62.2238 | -0.13733 | 123.6877 | 0 | 62.2238 | 123.4177 | 123.7198 | -123.8342 | -123.8159
205.9062 | 123.8205 | -61.8942 | 61.702 | -0.012589 | 0.018025 | 0.011978 | 0.00046148 | 0.065469 | -0.0050821 | 0.070397 | -62.0499 | 61.7661 | -62.178 | -61.9308 | 61.3083 | 0.10986 | -0.13275 | 0.086975 | 61.7706 | -62.0682 | -0.28381 | 0.064087 | -0.15564 | -0.036621 | -0.39368 | -0.17395 | 0.068665 | 0.12817 | 61.7615 | 61.9812 | 123.2025 | 123.6603 | -0.15564 | 123.6649 | 62.0041 | -0.17395 | 123.6603 | -0.15564 | 62.0041 | 123.2025 | 123.6649 | -123.88 | -123.7701
207.5938 | 123.7473 | -61.9034 | 61.7477 | -0.012589 | 0.017385 | 0.017746 | -0.0025293 | 0.065469 | -0.0027323 | 0.069329 | -61.9766 | 61.7706 | -62.0773 | -61.8027 | 61.4639 | 0.23804 | -0.091553 | 0.25635 | 61.7981 | -62.0499 | -0.17395 | 0.022888 | -0.073243 | 0.10071 | -0.28381 | -0.14648 | 0.050354 | 0.10071 | 61.8118 | 62.1597 | 123.3673 | 123.674 | -0.073243 | 123.7015 | 62.1414 | -0.14648 | 123.674 | -0.073243 | 62.1414 | 123.3673 | 123.7015 | -123.8251 | -123.7976
209.3281 | 123.7381 | -61.8851 | 61.7661 | -0.0049592 | 0.018239 | 0.01625 | -0.0018885 | 0.064187 | -0.0033731 | 0.068261 | -61.9583 | 61.7432 | -62.0865 | -61.8484 | 61.4136 | 0.21057 | -0.21057 | 0.19684 | 61.734 | -62.0773 | -0.20142 | -0.022888 | -0.073242 | 0.036621 | -0.35248 | -0.19226 | -0.032043 | 0.12817 | 61.6745 | 62.0819 | 123.2986 | 123.6282 | -0.073242 | 123.6191 | 62.0956 | -0.19226 | 123.6282 | -0.073242 | 62.0956 | 123.2986 | 123.6191 | -123.8525 | -123.8434
211.0156 | 123.8434 | -61.8668 | 61.6837 | -0.0049592 | 0.022298 | 0.014114 | 0.0011023 | 0.065896 | -0.0042277 | 0.069329 | -62.059 | 61.7386 | -62.1826 | -61.9217 | 61.3037 | 0.09613 | -0.064087 | 0.073242 | 61.7706 | -62.114 | -0.31586 | 0.054931 | -0.19226 | -0.054932 | -0.37994 | -0.24719 | 0.086975 | 0.1236 | 61.8027 | 61.94 | 123.1705 | 123.6053 | -0.19226 | 123.6374 | 61.9629 | -0.24719 | 123.6053 | -0.19226 | 61.9629 | 123.1705 | 123.6374 | -123.8663 | -123.7976
212.7656 | 123.7152 | -61.9217 | 61.7157 | -0.012589 | 0.020375 | 0.017746 | -0.0029565 | 0.063547 | -0.0057229 | 0.069329 | -61.9308 | 61.7706 | -62.0773 | -61.7889 | 61.4594 | 0.27008 | -0.064087 | 0.29297 | 61.7798 | -62.0865 | -0.15564 | 0.054932 | -0.009155 | 0.13275 | -0.25635 | -0.16479 | 0.064087 | 0.14648 | 61.8576 | 62.2147 | 123.381 | 123.6923 | -0.009155 | 123.7015 | 62.1918 | -0.16479 | 123.6923 | -0.009155 | 62.1918 | 123.381 | 123.7015 | -123.793 | -123.8022
214.5156 | 123.8342 | -61.908 | 61.6745 | 0.0026703 | 0.022298 | 0.01625 | 3.4284e-05 | 0.065896 | -0.0046549 | 0.070397 | -62.059 | 61.7523 | -62.178 | -61.9629 | 61.2854 | 0.07782 | -0.032043 | 0.073242 | 61.7615 | -62.1414 | -0.27008 | 0.077819 | -0.15106 | -0.054932 | -0.3891 | -0.23346 | 0.086975 | 0.11902 | 61.8759 | 61.9812 | 123.1934 | 123.6603 | -0.15106 | 123.6694 | 61.9858 | -0.23346 | 123.6603 | -0.15106 | 61.9858 | 123.1934 | 123.6694 | -123.8525 | -123.8159
216.25 | 123.7976 | -61.9308 | 61.6425 | 0.0026703 | 0.018025 | 0.015396 | -0.0010339 | 0.064828 | -0.0050821 | 0.069116 | -62.0316 | 61.7523 | -62.1735 | -61.8851 | 61.3586 | 0.16022 | 0.041199 | 0.20142 | 61.7889 | -62.1048 | -0.24262 | 0.10986 | -0.10071 | 0.045776 | -0.28381 | -0.17395 | 0.14648 | 0.14191 | 61.972 | 62.1323 | 123.2895 | 123.6832 | -0.10071 | 123.7198 | 62.0911 | -0.17395 | 123.6832 | -0.10071 | 62.0911 | 123.2895 | 123.7198 | -123.8159 | -123.7473
218 | 123.8251 | -61.8942 | 61.6379 | -0.0049592 | 0.017171 | 0.013046 | -0.00017952 | 0.064401 | -0.0052957 | 0.069543 | -62.0316 | 61.7752 | -62.1506 | -61.908 | 61.3541 | 0.15564 | 0.059509 | 0.18768 | 61.7752 | -62.114 | -0.25635 | 0.13733 | -0.13733 | -0.013733 | -0.28381 | -0.21973 | 0.13733 | 0.11902 | 61.9537 | 62.0819 | 123.2483 | 123.6694 | -0.13733 | 123.6694 | 62.0499 | -0.21973 | 123.6694 | -0.13733 | 62.0499 | 123.2483 | 123.6694 | -123.7885 | -123.7518
219.6875 | 123.7152 | -61.8896 | 61.734 | -0.020218 | 0.017812 | 0.01561 | -0.0059473 | 0.066537 | -0.0027323 | 0.068688 | -61.9629 | 61.7477 | -62.1002 | -61.8622 | 61.4136 | 0.21057 | -0.21057 | 0.1831 | 61.734 | -62.0636 | -0.21057 | 0.013733 | -0.073243 | 0.027465 | -0.32044 | -0.17395 | 0 | 0.13733 | 61.6791 | 62.0728 | 123.3032 | 123.6374 | -0.073243 | 123.6237 | 62.1002 | -0.17395 | 123.6374 | -0.073243 | 62.1002 | 123.3032 | 123.6237 | -123.8342 | -123.7976
221.4375 | 123.7015 | -61.8851 | 61.734 | -0.012589 | 0.02123 | 0.018387 | -0.0021021 | 0.066324 | -0.0016641 | 0.071038 | -61.9308 | 61.7294 | -62.1048 | -61.8301 | 61.4044 | 0.21515 | -0.26093 | 0.19684 | 61.7294 | -62.0911 | -0.21973 | -0.004578 | -0.045776 | 0.054932 | -0.32959 | -0.20599 | -0.004578 | 0.17395 | 61.6241 | 62.0819 | 123.2895 | 123.6145 | -0.045776 | 123.6145 | 62.1002 | -0.20599 | 123.6145 | -0.045776 | 62.1002 | 123.2895 | 123.6145 | -123.8388 | -123.8251
223.125 | 123.7381 | -61.9125 | 61.6653 | -0.0049592 | 0.017171 | 0.016891 | -0.0040247 | 0.061624 | -0.0046549 | 0.069116 | -61.9629 | 61.7661 | -62.1048 | -61.8393 | 61.409 | 0.21057 | 0.027466 | 0.23804 | 61.8164 | -62.0544 | -0.19226 | 0.10071 | -0.050354 | 0.073243 | -0.25635 | -0.14191 | 0.15106 | 0.14191 | 61.94 | 62.1506 | 123.3215 | 123.6786 | -0.050354 | 123.7289 | 62.1231 | -0.14191 | 123.6786 | -0.050354 | 62.1231 | 123.3215 | 123.7289 | -123.7701 | -123.7198
224.8906 | 123.7747 | -61.9125 | 61.6516 | -0.012589 | 0.018239 | 0.014541 | 0.0011023 | 0.065042 | -0.0046549 | 0.069543 | -61.9995 | 61.7386 | -62.178 | -61.8851 | 61.3358 | 0.16479 | -0.013733 | 0.19684 | 61.7569 | -62.0911 | -0.2655 | 0.086975 | -0.086975 | 0.027466 | -0.31586 | -0.17853 | 0.10529 | 0.17853 | 61.8988 | 62.1094 | 123.2483 | 123.6511 | -0.086975 | 123.6694 | 62.0773 | -0.17853 | 123.6511 | -0.086975 | 62.0773 | 123.2483 | 123.6694 | -123.8297 | -123.7427
226.5625 | 123.7381 | -61.8576 | 61.734 | -0.0049592 | 0.017598 | 0.014541 | -0.0059473 | 0.064187 | -0.0023049 | 0.070184 | -61.9949 | 61.7477 | -62.0728 | -61.8439 | 61.4044 | 0.19226 | -0.13733 | 0.16937 | 61.7294 | -62.0728 | -0.21515 | 0.013733 | -0.13733 | 0.013733 | -0.32959 | -0.21515 | -0.004578 | 0.07782 | 61.7203 | 62.027 | 123.262 | 123.6053 | -0.13733 | 123.587 | 62.0499 | -0.21515 | 123.6053 | -0.13733 | 62.0499 | 123.262 | 123.587 | -123.8068 | -123.8068
228.2969 | 123.7473 | -61.9034 | 61.7065 | -0.012589 | 0.016957 | 0.014969 | -0.0025293 | 0.063974 | -0.0031595 | 0.069543 | -61.9629 | 61.7752 | -62.1002 | -61.8393 | 61.3815 | 0.21057 | 0.050354 | 0.26093 | 61.8027 | -62.0819 | -0.19684 | 0.068665 | -0.05951 | 0.064087 | -0.32501 | -0.17853 | 0.09613 | 0.13733 | 61.9537 | 62.1643 | 123.2849 | 123.6786 | -0.05951 | 123.7061 | 62.114 | -0.17853 | 123.6786 | -0.05951 | 62.114 | 123.2849 | 123.7061 | -123.8068 | -123.7885
230 | 123.7564 | -61.8759 | 61.7157 | 0.0026703 | 0.017812 | 0.01561 | 0.00067508 | 0.067392 | -0.0031595 | 0.069543 | -62.0087 | 61.7386 | -62.146 | -61.8576 | 61.3724 | 0.16479 | -0.19226 | 0.15564 | 61.7386 | -62.0544 | -0.27008 | 0.022888 | -0.13275 | 0.018311 | -0.34332 | -0.17853 | 0.022888 | 0.13733 | 61.6837 | 62.0316 | 123.2483 | 123.6145 | -0.13275 | 123.6145 | 62.0407 | -0.17853 | 123.6145 | -0.13275 | 62.0407 | 123.2483 | 123.6145 | -123.8617 | -123.7701
231.75 | 123.8205 | -61.8668 | 61.6425 | -0.0049592 | 0.020803 | 0.017746 | 0.00088868 | 0.066537 | -0.0050821 | 0.071038 | -62.0682 | 61.7111 | -62.1826 | -61.9446 | 61.29 | 0.10071 | 0.009155 | 0.10529 | 61.7661 | -62.1231 | -0.31586 | 0.068665 | -0.20142 | -0.07782 | -0.35248 | -0.25635 | 0.1236 | 0.11444 | 61.8759 | 61.972 | 123.1567 | 123.5779 | -0.20142 | 123.6328 | 61.9675 | -0.25635 | 123.5779 | -0.20142 | 61.9675 | 123.1567 | 123.6328 | -123.8251 | -123.7656
233.4375 | 123.761 | -61.8942 | 61.6562 | 0.0103 | 0.019094 | 0.014328 | 0.0021705 | 0.064615 | -0.0074319 | 0.069543 | -61.9949 | 61.7432 | -62.1643 | -61.8622 | 61.3266 | 0.16937 | -0.013733 | 0.2243 | 61.7477 | -62.1048 | -0.27008 | 0.086975 | -0.10071 | 0.032043 | -0.32959 | -0.21057 | 0.091553 | 0.16937 | 61.8805 | 62.1185 | 123.2208 | 123.6374 | -0.10071 | 123.642 | 62.0636 | -0.21057 | 123.6374 | -0.10071 | 62.0636 | 123.2208 | 123.642 | -123.8205 | -123.761
235.1094 | 123.7335 | -61.8622 | 61.7477 | -0.012589 | 0.017385 | 0.014755 | -0.0046655 | 0.062906 | -0.0020913 | 0.070397 | -61.9537 | 61.7386 | -62.059 | -61.8301 | 61.3998 | 0.19684 | -0.16479 | 0.1831 | 61.7569 | -62.0819 | -0.19684 | -0.009156 | -0.091552 | 0.032044 | -0.3479 | -0.21973 | 0.009155 | 0.10529 | 61.6974 | 62.0453 | 123.262 | 123.6008 | -0.091552 | 123.6191 | 62.059 | -0.21973 | 123.6008 | -0.091552 | 62.059 | 123.262 | 123.6191 | -123.8068 | -123.8297
236.8594 | 123.6923 | -61.8668 | 61.7203 | 0.0026703 | 0.018453 | 0.013687 | -0.0042383 | 0.065469 | -0.0048685 | 0.069543 | -61.9492 | 61.7661 | -62.0773 | -61.7981 | 61.4365 | 0.24719 | -0.10071 | 0.25635 | 61.7844 | -62.0316 | -0.21057 | 0.045776 | -0.082398 | 0.068664 | -0.28381 | -0.16479 | 0.064087 | 0.12817 | 61.7661 | 62.1231 | 123.3032 | 123.6328 | -0.082398 | 123.6511 | 62.114 | -0.16479 | 123.6328 | -0.082398 | 62.114 | 123.3032 | 123.6511 | -123.7976 | -123.7518
238.5625 | 123.793 | -61.8484 | 61.6241 | -0.0049592 | 0.020162 | 0.013473 | -0.0035973 | 0.062478 | -0.0023049 | 0.068688 | -62.0224 | 61.7752 | -62.1277 | -61.8896 | 61.3266 | 0.15106 | 0.086975 | 0.20599 | 61.7798 | -62.059 | -0.27924 | 0.15106 | -0.17395 | -0.041198 | -0.29755 | -0.21057 | 0.15564 | 0.10529 | 61.9354 | 62.0544 | 123.175 | 123.6237 | -0.17395 | 123.6282 | 61.9995 | -0.21057 | 123.6237 | -0.17395 | 61.9995 | 123.175 | 123.6282 | -123.7518 | -123.6832
240.25 | 123.8297 | -61.8851 | 61.6333 | -0.0049592 | 0.022084 | 0.018814 | 0.00088868 | 0.065042 | -0.0033731 | 0.069757 | -62.0773 | 61.734 | -62.1597 | -61.9354 | 61.2717 | 0.086975 | -0.022888 | 0.064087 | 61.7432 | -62.1552 | -0.27466 | 0.10071 | -0.19226 | -0.050354 | -0.36163 | -0.27008 | 0.10986 | 0.082397 | 61.8622 | 61.9492 | 123.1567 | 123.6191 | -0.19226 | 123.6282 | 61.972 | -0.27008 | 123.6191 | -0.19226 | 61.972 | 123.1567 | 123.6282 | -123.793 | -123.7885
242.0156 | 123.7427 | -61.8988 | 61.6196 | -0.0049592 | 0.020162 | 0.014969 | 0.0021705 | 0.06376 | -0.0038003 | 0.069757 | -61.9904 | 61.7432 | -62.1414 | -61.8576 | 61.3449 | 0.17853 | -0.022888 | 0.23346 | 61.7157 | -62.1368 | -0.24261 | 0.1236 | -0.091552 | 0.041199 | -0.27466 | -0.23804 | 0.09613 | 0.15106 | 61.8759 | 62.1323 | 123.2437 | 123.642 | -0.091552 | 123.6145 | 62.0773 | -0.23804 | 123.642 | -0.091552 | 62.0773 | 123.2437 | 123.6145 | -123.761 | -123.7564
243.7656 | 123.761 | -61.8988 | 61.647 | 0.0026703 | 0.017385 | 0.017319 | -0.00039312 | 0.062265 | -0.0042277 | 0.068902 | -62.0041 | 61.7249 | -62.1597 | -61.8576 | 61.3403 | 0.17395 | 0.009155 | 0.21515 | 61.7432 | -62.1002 | -0.26093 | 0.07782 | -0.10529 | 0.041199 | -0.3067 | -0.20142 | 0.09613 | 0.15564 | 61.908 | 62.114 | 123.2391 | 123.6237 | -0.10529 | 123.642 | 62.0728 | -0.20142 | 123.6237 | -0.10529 | 62.0728 | 123.2391 | 123.642 | -123.8068 | -123.7473
245.4531 | 123.6649 | -61.8851 | 61.7065 | -0.0049592 | 0.019734 | 0.011123 | -0.0061609 | 0.062692 | -0.0044413 | 0.070184 | -61.9034 | 61.7661 | -62.0453 | -61.7798 | 61.4594 | 0.28381 | -0.09613 | 0.32044 | 61.7386 | -62.0499 | -0.16022 | 0.059509 | -0.01831 | 0.10529 | -0.24719 | -0.16479 | 0.032043 | 0.14191 | 61.7889 | 62.2055 | 123.3444 | 123.6511 | -0.01831 | 123.6237 | 62.1689 | -0.16479 | 123.6511 | -0.01831 | 62.1689 | 123.3444 | 123.6237 | -123.7518 | -123.7564
247.1406 | 123.7473 | -61.8851 | 61.6104 | -0.012589 | 0.019094 | 0.01561 | 0.00024788 | 0.063333 | -0.0029459 | 0.06762 | -62.0041 | 61.7432 | -62.1643 | -61.8668 | 61.3358 | 0.16937 | 0.041199 | 0.21057 | 61.7432 | -62.0956 | -0.27924 | 0.13275 | -0.11902 | 0.018311 | -0.27466 | -0.21057 | 0.13275 | 0.16022 | 61.9263 | 62.0956 | 123.2208 | 123.6282 | -0.11902 | 123.6282 | 62.0544 | -0.21057 | 123.6282 | -0.11902 | 62.0544 | 123.2208 | 123.6282 | -123.7747 | -123.7061
248.8906 | 123.793 | -61.8851 | 61.6333 | 0.0103 | 0.017812 | 0.014328 | -0.0010339 | 0.064828 | -0.0020913 | 0.069543 | -62.0682 | 61.7706 | -62.146 | -61.9446 | 61.2671 | 0.07782 | 0 | 0.10071 | 61.734 | -62.114 | -0.26092 | 0.13733 | -0.1831 | -0.059509 | -0.36621 | -0.22888 | 0.10071 | 0.07782 | 61.8851 | 61.9858 | 123.1522 | 123.6557 | -0.1831 | 123.6191 | 61.9629 | -0.22888 | 123.6557 | -0.1831 | 61.9629 | 123.1522 | 123.6191 | -123.7793 | -123.7473
250.6406 | 123.642 | -61.8713 | 61.702 | -0.0049592 | 0.021443 | 0.012192 | -0.0046655 | 0.062478 | -0.0025187 | 0.068475 | -61.8713 | 61.7569 | -62.0407 | -61.7477 | 61.4685 | 0.28839 | -0.11444 | 0.32501 | 61.7432 | -62.059 | -0.16937 | 0.054932 | 0 | 0.1236 | -0.23346 | -0.18768 | 0.041199 | 0.16937 | 61.7569 | 62.1964 | 123.3398 | 123.6282 | 0 | 123.6145 | 62.1597 | -0.18768 | 123.6282 | 0 | 62.1597 | 123.3398 | 123.6145 | -123.7427 | -123.761
252.3125 | 123.6969 | -61.8851 | 61.6837 | -0.0049592 | 0.015676 | 0.014328 | -0.0010339 | 0.06376 | -0.0031595 | 0.071252 | -61.9766 | 61.7111 | -62.114 | -61.821 | 61.3724 | 0.19226 | -0.21515 | 0.17853 | 61.6974 | -62.0407 | -0.22888 | 0.027466 | -0.091553 | 0.064087 | -0.31128 | -0.15564 | 0.013733 | 0.13733 | 61.6699 | 62.0636 | 123.2574 | 123.5962 | -0.091553 | 123.5825 | 62.0773 | -0.15564 | 123.5962 | -0.091553 | 62.0773 | 123.2574 | 123.5825 | -123.7976 | -123.7244
254 | 123.7793 | -61.8622 | 61.6562 | -0.0049592 | 0.018239 | 0.016037 | -0.00039312 | 0.064401 | -0.0038003 | 0.069543 | -62.027 | 61.7706 | -62.1231 | -61.8805 | 61.3129 | 0.14191 | 0.09613 | 0.19226 | 61.7889 | -62.0728 | -0.26093 | 0.11444 | -0.16479 | -0.01831 | -0.34332 | -0.21057 | 0.13275 | 0.09613 | 61.9583 | 62.0544 | 123.175 | 123.6328 | -0.16479 | 123.6511 | 62.0041 | -0.21057 | 123.6328 | -0.16479 | 62.0041 | 123.175 | 123.6511 | -123.7793 | -123.7289
255.75 | 123.7061 | -61.8622 | 61.6928 | -0.0049592 | 0.017812 | 0.011123 | -0.0050927 | 0.065256 | -0.0029459 | 0.068475 | -61.972 | 61.7889 | -62.0544 | -61.8439 | 61.377 | 0.17853 | -0.11444 | 0.1831 | 61.7294 | -62.0316 | -0.19226 | 0.09613 | -0.10986 | 0.018311 | -0.31586 | -0.16937 | 0.036621 | 0.082397 | 61.7477 | 62.0453 | 123.2391 | 123.6511 | -0.10986 | 123.5916 | 62.0407 | -0.16937 | 123.6511 | -0.10986 | 62.0407 | 123.2391 | 123.5916 | -123.7473 | -123.7244
257.4375 | 123.6511 | -61.8851 | 61.7065 | 0.0026703 | 0.016317 | 0.013046 | -0.0010339 | 0.064401 | -0.0038003 | 0.068261 | -61.8942 | 61.7477 | -62.0499 | -61.7477 | 61.4456 | 0.28381 | -0.10071 | 0.32044 | 61.7386 | -62.0178 | -0.16479 | 0.041199 | -0.009155 | 0.13733 | -0.26093 | -0.13275 | 0.032043 | 0.15564 | 61.7844 | 62.2055 | 123.3307 | 123.6328 | -0.009155 | 123.6237 | 62.1689 | -0.13275 | 123.6328 | -0.009155 | 62.1689 | 123.3307 | 123.6237 | -123.7564 | -123.7244
259.1094 | 123.761 | -61.8622 | 61.6379 | 0.0026703 | 0.021657 | 0.017319 | -0.0023157 | 0.063974 | -0.0029459 | 0.069329 | -61.9949 | 61.7569 | -62.0956 | -61.8576 | 61.322 | 0.14648 | 0.082397 | 0.20142 | 61.7844 | -62.0682 | -0.23346 | 0.11902 | -0.13275 | 0.004578 | -0.31586 | -0.20599 | 0.14648 | 0.10071 | 61.9446 | 62.0636 | 123.1842 | 123.6191 | -0.13275 | 123.6465 | 62.0087 | -0.20599 | 123.6191 | -0.13275 | 62.0087 | 123.1842 | 123.6465 | -123.7335 | -123.7061
260.8438 | 123.7473 | -61.8484 | 61.6333 | -0.012589 | 0.019948 | 0.014755 | -0.0033837 | 0.062906 | -0.0029459 | 0.069543 | -62.0087 | 61.7798 | -62.0911 | -61.8713 | 61.3174 | 0.15106 | 0.10071 | 0.20142 | 61.7569 | -62.0773 | -0.24261 | 0.14648 | -0.16022 | -0.022888 | -0.31586 | -0.22888 | 0.1236 | 0.082397 | 61.9492 | 62.0499 | 123.1659 | 123.6282 | -0.16022 | 123.6053 | 61.9995 | -0.22888 | 123.6282 | -0.16022 | 61.9995 | 123.1659 | 123.6053 | -123.7244 | -123.7106
262.5938 | 123.6603 | -61.8805 | 61.702 | -0.0049592 | 0.018239 | 0.016678 | -0.0016747 | 0.063974 | -0.0016641 | 0.070184 | -61.9171 | 61.7203 | -62.0956 | -61.7935 | 61.3861 | 0.19684 | -0.2243 | 0.19226 | 61.6699 | -62.0636 | -0.21515 | 0.018311 | -0.036621 | 0.086975 | -0.31586 | -0.18311 | -0.032043 | 0.17853 | 61.6562 | 62.0728 | 123.2666 | 123.6008 | -0.036621 | 123.5504 | 62.0773 | -0.18311 | 123.6008 | -0.036621 | 62.0773 | 123.2666 | 123.5504 | -123.7976 | -123.7656
264.2812 | 123.761 | -61.8393 | 61.6425 | -0.0049592 | 0.020589 | 0.014114 | -0.00060672 | 0.062051 | -0.0014505 | 0.06997 | -62.0087 | 61.8073 | -62.1277 | -61.8713 | 61.3083 | 0.15106 | 0.12817 | 0.18768 | 61.7889 | -62.0728 | -0.28839 | 0.16479 | -0.16937 | -0.032044 | -0.33417 | -0.23346 | 0.14648 | 0.11902 | 61.9675 | 62.027 | 123.1476 | 123.6465 | -0.16937 | 123.6282 | 61.9904 | -0.23346 | 123.6465 | -0.16937 | 61.9904 | 123.1476 | 123.6282 | -123.7701 | -123.7152
265.9688 | 123.6145 | -61.8484 | 61.6928 | -0.0049592 | 0.01888 | 0.01561 | -0.0031701 | 0.063119 | 4.4906e-05 | 0.067193 | -61.8805 | 61.734 | -62.0499 | -61.734 | 61.4594 | 0.27924 | -0.14191 | 0.33417 | 61.7157 | -62.0499 | -0.20142 | 0.041199 | -0.032043 | 0.11444 | -0.23346 | -0.20142 | 0.022888 | 0.16937 | 61.7065 | 62.1826 | 123.3078 | 123.5825 | -0.032043 | 123.5641 | 62.1277 | -0.20142 | 123.5825 | -0.032043 | 62.1277 | 123.3078 | 123.5641 | -123.7427 | -123.7427
267.7188 | 123.642 | -61.8576 | 61.7111 | -0.012589 | 0.019948 | 0.013473 | -0.0010339 | 0.061838 | -0.0031595 | 0.068475 | -61.8759 | 61.7477 | -62.0361 | -61.7432 | 61.4319 | 0.25635 | -0.15106 | 0.27008 | 61.7203 | -62.0361 | -0.17853 | 0.036621 | -0.018311 | 0.11444 | -0.27924 | -0.17853 | 0.009155 | 0.16022 | 61.7065 | 62.1277 | 123.2895 | 123.6053 | -0.018311 | 123.5779 | 62.114 | -0.17853 | 123.6053 | -0.018311 | 62.114 | 123.2895 | 123.5779 | -123.7473 | -123.7473
269.4062 | 123.7427 | -61.8439 | 61.6287 | 0.0103 | 0.01888 | 0.01326 | -0.00017952 | 0.062906 | -0.0052957 | 0.068475 | -62.0132 | 61.7294 | -62.0911 | -61.8576 | 61.322 | 0.16022 | 0.091553 | 0.19226 | 61.7706 | -62.0316 | -0.24719 | 0.10071 | -0.16937 | -0.013733 | -0.3067 | -0.18768 | 0.14191 | 0.077819 | 61.9354 | 62.0361 | 123.1659 | 123.5733 | -0.16937 | 123.6145 | 62.0041 | -0.18768 | 123.5733 | -0.16937 | 62.0041 | 123.1659 | 123.6145 | -123.7198 | -123.6603
271.0938 | 123.7518 | -61.8668 | 61.6653 | -0.012589 | 0.020375 | 0.014328 | -0.00060672 | 0.064187 | -0.0044413 | 0.070611 | -62.0132 | 61.7294 | -62.1368 | -61.8805 | 61.29 | 0.11902 | -0.13275 | 0.1236 | 61.6882 | -62.0728 | -0.27008 | 0.064087 | -0.14648 | -0.013733 | -0.37537 | -0.20599 | 0.022888 | 0.1236 | 61.734 | 61.9904 | 123.1567 | 123.5962 | -0.14648 | 123.555 | 61.9858 | -0.20599 | 123.5962 | -0.14648 | 61.9858 | 123.1567 | 123.555 | -123.8022 | -123.7381
272.8594 | 123.7381 | -61.8439 | 61.6653 | -0.0049592 | 0.020162 | 0.015396 | -0.00060672 | 0.066324 | -0.0057229 | 0.070825 | -62.0178 | 61.7249 | -62.1506 | -61.8668 | 61.2946 | 0.11902 | -0.14648 | 0.10529 | 61.7249 | -62.0682 | -0.3067 | 0.05951 | -0.17395 | -0.022888 | -0.37079 | -0.2243 | 0.05951 | 0.13275 | 61.6974 | 61.9492 | 123.1384 | 123.5687 | -0.17395 | 123.5687 | 61.9629 | -0.2243 | 123.5687 | -0.17395 | 61.9629 | 123.1384 | 123.5687 | -123.8159 | -123.7335
274.625 | 123.6877 | -61.8759 | 61.6516 | -0.012589 | 0.017598 | 0.016037 | 0.0011023 | 0.064615 | -0.0063639 | 0.068475 | -61.9812 | 61.7249 | -62.114 | -61.8393 | 61.3312 | 0.15564 | -0.032043 | 0.22888 | 61.7294 | -62.0728 | -0.23804 | 0.073243 | -0.10529 | 0.036622 | -0.32043 | -0.19684 | 0.07782 | 0.13275 | 61.8439 | 62.1048 | 123.2071 | 123.6008 | -0.10529 | 123.6053 | 62.0316 | -0.19684 | 123.6008 | -0.10529 | 62.0316 | 123.2071 | 123.6053 | -123.7656 | -123.7244
276.3125 | 123.6969 | -61.8759 | 61.6379 | -0.0049592 | 0.02123 | 0.014755 | -0.0014611 | 0.064828 | -0.0055093 | 0.071252 | -61.9766 | 61.702 | -62.1414 | -61.8393 | 61.3083 | 0.16479 | -0.027466 | 0.19684 | 61.6928 | -62.0911 | -0.2655 | 0.064087 | -0.10071 | 0.036622 | -0.32959 | -0.21515 | 0.054932 | 0.16479 | 61.8484 | 62.0728 | 123.1842 | 123.5779 | -0.10071 | 123.5687 | 62.0407 | -0.21515 | 123.5779 | -0.10071 | 62.0407 | 123.1842 | 123.5687 | -123.7793 | -123.7289
278.0781 | 123.6145 | -61.8484 | 61.702 | -0.0049592 | 0.020162 | 0.014114 | -0.0070153 | 0.063333 | -0.0025187 | 0.069543 | -61.8851 | 61.7523 | -62.0453 | -61.7249 | 61.4639 | 0.28381 | -0.10986 | 0.32959 | 61.7203 | -62.0316 | -0.19684 | 0.050354 | -0.036621 | 0.1236 | -0.23804 | -0.1831 | 0.018311 | 0.16022 | 61.7386 | 62.178 | 123.3124 | 123.6008 | -0.036621 | 123.5687 | 62.1323 | -0.1831 | 123.6008 | -0.036621 | 62.1323 | 123.3124 | 123.5687 | -123.7473 | -123.7335
279.8281 | 123.6923 | -61.8759 | 61.6379 | 0.0026703 | 0.020803 | 0.01326 | 0.0038795 | 0.065683 | -0.0046549 | 0.070397 | -61.9675 | 61.702 | -62.1231 | -61.8439 | 61.3129 | 0.17395 | -0.036621 | 0.20599 | 61.6882 | -62.0453 | -0.24719 | 0.064087 | -0.091552 | 0.032044 | -0.32501 | -0.16937 | 0.050354 | 0.15564 | 61.8393 | 62.0819 | 123.1888 | 123.5779 | -0.091552 | 123.5641 | 62.0499 | -0.16937 | 123.5779 | -0.091552 | 62.0499 | 123.1888 | 123.5641 | -123.761 | -123.6832
281.5156 | 123.6145 | -61.8439 | 61.7249 | 0.0103 | 0.019307 | 0.015823 | -0.0050927 | 0.063547 | -0.0029459 | 0.070397 | -61.9034 | 61.7065 | -62.0499 | -61.7889 | 61.3998 | 0.2243 | -0.24719 | 0.20142 | 61.6699 | -62.059 | -0.20599 | -0.018311 | -0.059509 | 0.054932 | -0.32501 | -0.21515 | -0.054932 | 0.14648 | 61.5967 | 62.0453 | 123.2437 | 123.5504 | -0.059509 | 123.5138 | 62.0682 | -0.21515 | 123.5504 | -0.059509 | 62.0682 | 123.2437 | 123.5138 | -123.7747 | -123.7839
283.2656 | 123.7473 | -61.8347 | 61.6241 | 0.0026703 | 0.021016 | 0.014755 | -0.00039312 | 0.063974 | -0.0031595 | 0.068475 | -62.0087 | 61.7706 | -62.114 | -61.8668 | 61.29 | 0.15564 | 0.09613 | 0.19226 | 61.7752 | -62.0453 | -0.27924 | 0.14648 | -0.17395 | -0.032043 | -0.33417 | -0.21057 | 0.15106 | 0.10529 | 61.9308 | 62.027 | 123.1247 | 123.6053 | -0.17395 | 123.6099 | 61.9904 | -0.21057 | 123.6053 | -0.17395 | 61.9904 | 123.1247 | 123.6099 | -123.7381 | -123.6694
285 | 123.6374 | -61.8118 | 61.7065 | -0.0049592 | 0.019948 | 0.012619 | -0.0068017 | 0.064615 | -0.0031595 | 0.070825 | -61.9217 | 61.7294 | -62.027 | -61.8118 | 61.3632 | 0.19684 | -0.14191 | 0.17853 | 61.6928 | -61.9995 | -0.21515 | 0.022888 | -0.10986 | 0 | -0.34332 | -0.18768 | -0.013733 | 0.10529 | 61.6699 | 61.9904 | 123.175 | 123.5413 | -0.10986 | 123.5046 | 62.0087 | -0.18768 | 123.5413 | -0.10986 | 62.0087 | 123.175 | 123.5046 | -123.7335 | -123.7061
286.6719 | 123.5916 | -61.853 | 61.702 | 0.0026703 | 0.019734 | 0.013687 | -0.0021021 | 0.063974 | -0.0042277 | 0.072106 | -61.8622 | 61.7294 | -62.0178 | -61.7294 | 61.4319 | 0.28839 | -0.10529 | 0.31128 | 61.734 | -62.0224 | -0.1648 | 0.027466 | -0.009156 | 0.1236 | -0.27008 | -0.16937 | 0.032044 | 0.15564 | 61.7477 | 62.1643 | 123.2849 | 123.5825 | -0.009156 | 123.587 | 62.1414 | -0.16937 | 123.5825 | -0.009156 | 62.1414 | 123.2849 | 123.587 | -123.7198 | -123.7244
288.4219 | 123.7106 | -61.8301 | 61.647 | 0.0026703 | 0.019094 | 0.015396 | -0.00039312 | 0.065683 | -0.0048685 | 0.070825 | -61.9904 | 61.7065 | -62.114 | -61.853 | 61.3037 | 0.14648 | -0.15564 | 0.1236 | 61.6974 | -62.0544 | -0.28381 | 0.059509 | -0.16022 | -0.022888 | -0.34332 | -0.2243 | 0.050354 | 0.1236 | 61.6745 | 61.9537 | 123.1338 | 123.5367 | -0.16022 | 123.5275 | 61.9766 | -0.2243 | 123.5367 | -0.16022 | 61.9766 | 123.1338 | 123.5275 | -123.761 | -123.7015
290.1094 | 123.6603 | -61.8713 | 61.6241 | -0.012589 | 0.020375 | 0.012405 | -0.0018885 | 0.06141 | -0.0050821 | 0.06997 | -61.9217 | 61.7569 | -62.0682 | -61.7889 | 61.3541 | 0.20599 | 0.041199 | 0.25177 | 61.7432 | -62.0453 | -0.19684 | 0.13275 | -0.050354 | 0.082398 | -0.27008 | -0.17395 | 0.11902 | 0.14648 | 61.9125 | 62.1231 | 123.2254 | 123.6282 | -0.050354 | 123.6145 | 62.0773 | -0.17395 | 123.6282 | -0.050354 | 62.0773 | 123.2254 | 123.6145 | -123.6923 | -123.6694
291.8438 | 123.6053 | -61.8439 | 61.6791 | 0.0026703 | 0.020162 | 0.013046 | -0.0035973 | 0.063333 | -0.0027323 | 0.068475 | -61.8622 | 61.7294 | -62.0407 | -61.7203 | 61.4502 | 0.29755 | -0.11444 | 0.33417 | 61.7294 | -62.0132 | -0.19684 | 0.050354 | -0.018311 | 0.1236 | -0.22888 | -0.16937 | 0.050354 | 0.17853 | 61.7294 | 62.178 | 123.2941 | 123.5733 | -0.018311 | 123.5733 | 62.1414 | -0.16937 | 123.5733 | -0.018311 | 62.1414 | 123.2941 | 123.5733 | -123.7198 | -123.6923
293.5938 | 123.6649 | -61.821 | 61.6791 | -0.0049592 | 0.017598 | 0.015182 | -0.0021021 | 0.062692 | -0.0042277 | 0.070611 | -61.9308 | 61.7523 | -62.0224 | -61.7844 | 61.3632 | 0.20599 | -0.11902 | 0.21515 | 61.734 | -62.0041 | -0.20142 | 0.073242 | -0.10986 | 0.036621 | -0.31586 | -0.1831 | 0.054932 | 0.091553 | 61.702 | 62.0361 | 123.1842 | 123.5733 | -0.10986 | 123.555 | 62.027 | -0.1831 | 123.5733 | -0.10986 | 62.027 | 123.1842 | 123.555 | -123.7015 | -123.6832
295.3281 | 123.642 | -61.8347 | 61.6699 | -0.012589 | 0.019521 | 0.013473 | 0.0021705 | 0.063547 | -0.0046549 | 0.069543 | -61.9492 | 61.702 | -62.0911 | -61.7935 | 61.3358 | 0.17395 | -0.20599 | 0.16479 | 61.6928 | -62.0316 | -0.25635 | 0.032043 | -0.11444 | 0.041199 | -0.33417 | -0.19684 | 0.022888 | 0.14191 | 61.6287 | 61.9995 | 123.1705 | 123.5367 | -0.11444 | 123.5275 | 62.0087 | -0.19684 | 123.5367 | -0.11444 | 62.0087 | 123.1705 | 123.5275 | -123.761 | -123.7015
297.0938 | 123.7656 | -61.8393 | 61.6013 | -0.0049592 | 0.021657 | 0.012619 | 0.0017431 | 0.062906 | -0.0044413 | 0.06997 | -62.0407 | 61.7249 | -62.146 | -61.8942 | 61.2396 | 0.073242 | -0.036621 | 0.07782 | 61.7111 | -62.0911 | -0.3067 | 0.1236 | -0.20142 | -0.054932 | -0.36163 | -0.25177 | 0.10986 | 0.10529 | 61.8027 | 61.9171 | 123.0789 | 123.5641 | -0.20142 | 123.5504 | 61.9125 | -0.25177 | 123.5641 | -0.20142 | 61.9125 | 123.0789 | 123.5504 | -123.7473 | -123.6923
298.8438 | 123.6786 | -61.8301 | 61.6196 | 0.0026703 | 0.017812 | 0.014541 | 0.00067508 | 0.065256 | -0.0033731 | 0.072106 | -61.972 | 61.7065 | -62.1094 | -61.8256 | 61.3083 | 0.16479 | -0.009155 | 0.23346 | 61.6745 | -62.0636 | -0.27924 | 0.086975 | -0.14191 | 0.004577 | -0.31128 | -0.23346 | 0.054932 | 0.13733 | 61.821 | 62.0636 | 123.1384 | 123.5367 | -0.14191 | 123.5046 | 61.9949 | -0.23346 | 123.5367 | -0.14191 | 61.9949 | 123.1384 | 123.5046 | -123.7289 | -123.6832
300.5312 | 123.7152 | -61.8393 | 61.5921 | 0.0026703 | 0.020375 | 0.014541 | -0.00082032 | 0.064187 | -0.0027323 | 0.069757 | -61.9858 | 61.7386 | -62.0956 | -61.8713 | 61.2762 | 0.15564 | 0.10529 | 0.20142 | 61.7249 | -62.0819 | -0.25635 | 0.14648 | -0.14648 | -0.032044 | -0.31586 | -0.24262 | 0.13275 | 0.10986 | 61.9446 | 62.0407 | 123.1155 | 123.5779 | -0.14648 | 123.5641 | 61.9949 | -0.24262 | 123.5779 | -0.14648 | 61.9949 | 123.1155 | 123.5641 | -123.6877 | -123.674
302.2656 | 123.6603 | -61.8484 | 61.6013 | 0.0026703 | 0.019734 | 0.015182 | -0.00017952 | 0.064401 | -0.0063639 | 0.06997 | -61.9583 | 61.7065 | -62.1231 | -61.821 | 61.322 | 0.17853 | -0.013733 | 0.23346 | 61.7111 | -62.0499 | -0.27466 | 0.10529 | -0.10986 | 0.027466 | -0.27924 | -0.20142 | 0.10986 | 0.1648 | 61.8347 | 62.0819 | 123.1705 | 123.555 | -0.10986 | 123.5596 | 62.027 | -0.20142 | 123.555 | -0.10986 | 62.027 | 123.1705 | 123.5596 | -123.7244 | -123.6511
304.0156 | 123.7198 | -61.8027 | 61.6013 | 0.0026703 | 0.020375 | 0.016464 | 0.0017431 | 0.064401 | -0.0029459 | 0.070611 | -62.0132 | 61.6928 | -62.1094 | -61.9034 | 61.2534 | 0.09613 | -0.059509 | 0.091553 | 61.7157 | -62.0636 | -0.3067 | 0.091553 | -0.21057 | -0.10071 | -0.3479 | -0.26093 | 0.11444 | 0.09613 | 61.7432 | 61.8942 | 123.056 | 123.4955 | -0.21057 | 123.5184 | 61.8988 | -0.26093 | 123.4955 | -0.21057 | 61.8988 | 123.056 | 123.5184 | -123.7106 | -123.6649
305.6875 | 123.6191 | -61.8256 | 61.6928 | -0.012589 | 0.018453 | 0.013046 | -0.0076563 | 0.062478 | -0.0044413 | 0.069757 | -61.9125 | 61.7386 | -62.0407 | -61.7661 | 61.3678 | 0.25177 | -0.10529 | 0.24261 | 61.7065 | -61.9995 | -0.21515 | 0.045776 | -0.086975 | 0.05951 | -0.32501 | -0.17395 | 0.013733 | 0.12817 | 61.7203 | 62.0682 | 123.1934 | 123.5641 | -0.086975 | 123.5321 | 62.0773 | -0.17395 | 123.5641 | -0.086975 | 62.0773 | 123.1934 | 123.5321 | -123.7335 | -123.6923
307.4375 | 123.6053 | -61.8622 | 61.6791 | -0.0049592 | 0.018239 | 0.016891 | -0.0029565 | 0.061197 | -0.0035867 | 0.069329 | -61.8668 | 61.6928 | -62.0361 | -61.734 | 61.409 | 0.28381 | -0.07782 | 0.32044 | 61.6745 | -61.972 | -0.17395 | 0.013733 | -0.004577 | 0.12817 | -0.27008 | -0.10986 | -0.004577 | 0.16937 | 61.7844 | 62.1826 | 123.2712 | 123.555 | -0.004577 | 123.5367 | 62.146 | -0.10986 | 123.555 | -0.004577 | 62.146 | 123.2712 | 123.5367 | -123.7152 | -123.6511
309.1875 | 123.6465 | -61.821 | 61.6745 | 0.0026703 | 0.018453 | 0.010696 | -0.0046655 | 0.061197 | -0.0025187 | 0.069757 | -61.9263 | 61.7111 | -62.0499 | -61.7935 | 61.3403 | 0.19684 | -0.10986 | 0.16937 | 61.7065 | -62.0041 | -0.22888 | 0.036621 | -0.10529 | 0.027466 | -0.33417 | -0.1831 | 0.032043 | 0.1236 | 61.7111 | 61.9904 | 123.1613 | 123.5321 | -0.10529 | 123.5275 | 62.0178 | -0.1831 | 123.5321 | -0.10529 | 62.0178 | 123.1613 | 123.5275 | -123.7244 | -123.6786
310.8594 | 123.6923 | -61.8301 | 61.6196 | -0.0049592 | 0.020589 | 0.015182 | -0.0025293 | 0.062478 | -0.0052957 | 0.066339 | -61.94 | 61.734 | -62.0361 | -61.8256 | 61.3129 | 0.16937 | 0.064087 | 0.20142 | 61.7706 | -62.0132 | -0.20599 | 0.11444 | -0.10986 | 0.004577 | -0.3067 | -0.18311 | 0.15106 | 0.096131 | 61.8942 | 62.0316 | 123.143 | 123.5641 | -0.10986 | 123.6008 | 61.9995 | -0.18311 | 123.5641 | -0.10986 | 61.9995 | 123.143 | 123.6008 | -123.6557 | -123.6328
312.6094 | 123.7061 | -61.8256 | 61.6196 | 0.0026703 | 0.018666 | 0.013473 | -0.0012475 | 0.06376 | -0.0055093 | 0.068048 | -61.9904 | 61.7249 | -62.1002 | -61.8256 | 61.29 | 0.15106 | 0.10986 | 0.21515 | 61.7615 | -62.0178 | -0.27466 | 0.10529 | -0.16479 | 0 | -0.32959 | -0.19226 | 0.14191 | 0.10986 | 61.9354 | 62.0407 | 123.1155 | 123.5504 | -0.16479 | 123.587 | 61.9766 | -0.19226 | 123.5504 | -0.16479 | 61.9766 | 123.1155 | 123.587 | -123.7198 | -123.6374
314.3594 | 123.7381 | -61.8347 | 61.6333 | 0.0026703 | 0.020375 | 0.016464 | 0.00088868 | 0.064615 | -0.0050821 | 0.069543 | -62.0087 | 61.7065 | -62.1185 | -61.908 | 61.1847 | 0.068665 | -0.027466 | 0.059509 | 61.702 | -62.0773 | -0.28381 | 0.073242 | -0.17395 | -0.073242 | -0.44861 | -0.24262 | 0.068664 | 0.10986 | 61.8073 | 61.8942 | 123.0194 | 123.5413 | -0.17395 | 123.5367 | 61.9034 | -0.24262 | 123.5413 | -0.17395 | 61.9034 | 123.0194 | 123.5367 | -123.7518 | -123.7106
316.0625 | 123.6694 | -61.8347 | 61.6241 | -0.0049592 | 0.020803 | 0.011337 | 0.00046148 | 0.066964 | -0.0065775 | 0.070611 | -61.9583 | 61.6653 | -62.1002 | -61.8439 | 61.2762 | 0.14191 | -0.018311 | 0.16937 | 61.7065 | -62.0544 | -0.2655 | 0.041198 | -0.1236 | -0.009155 | -0.3479 | -0.21973 | 0.082397 | 0.14191 | 61.8164 | 62.0041 | 123.111 | 123.5001 | -0.1236 | 123.5413 | 61.9766 | -0.21973 | 123.5001 | -0.1236 | 61.9766 | 123.111 | 123.5413 | -123.7244 | -123.6786
317.8125 | 123.6603 | -61.8118 | 61.615 | -0.012589 | 0.020162 | 0.014755 | -0.0023157 | 0.064187 | -0.0031595 | 0.06997 | -61.9125 | 61.7569 | -62.0499 | -61.821 | 61.3266 | 0.17853 | 0.07782 | 0.23346 | 61.7432 | -62.0316 | -0.23804 | 0.14191 | -0.10071 | -0.009155 | -0.28839 | -0.21973 | 0.12817 | 0.13733 | 61.8896 | 62.0453 | 123.1384 | 123.5687 | -0.10071 | 123.555 | 61.9904 | -0.21973 | 123.5687 | -0.10071 | 61.9904 | 123.1384 | 123.555 | -123.6649 | -123.6465
319.5625 | 123.6923 | -61.8164 | 61.6241 | -0.012589 | 0.02123 | 0.017532 | -0.0014611 | 0.065042 | -0.0048685 | 0.068902 | -61.9949 | 61.6928 | -62.0956 | -61.8805 | 61.2534 | 0.10529 | -0.07782 | 0.09613 | 61.7111 | -62.0682 | -0.27924 | 0.068664 | -0.17853 | -0.064087 | -0.37079 | -0.25177 | 0.086975 | 0.10071 | 61.7386 | 61.9125 | 123.0698 | 123.5092 | -0.17853 | 123.5275 | 61.9217 | -0.25177 | 123.5092 | -0.17853 | 61.9217 | 123.0698 | 123.5275 | -123.7198 | -123.6923
321.25 | 123.555 | -61.8256 | 61.6974 | -0.012589 | 0.018666 | 0.0186 | -0.0046655 | 0.063333 | -0.0033731 | 0.06997 | -61.8713 | 61.6837 | -62.0544 | -61.7661 | 61.3724 | 0.21973 | -0.25177 | 0.19684 | 61.6608 | -62.0178 | -0.22888 | -0.013733 | -0.045776 | 0.05951 | -0.32501 | -0.19226 | -0.036621 | 0.1831 | 61.5738 | 62.0224 | 123.1979 | 123.5092 | -0.045776 | 123.4863 | 62.0453 | -0.19226 | 123.5092 | -0.045776 | 62.0453 | 123.1979 | 123.4863 | -123.7518 | -123.7152
323 | 123.6969 | -61.8073 | 61.5875 | 0.0103 | 0.017598 | 0.017319 | 0.0015295 | 0.063547 | -0.0057229 | 0.069757 | -62.0178 | 61.7111 | -62.114 | -61.9034 | 61.203 | 0.082397 | -0.032043 | 0.073242 | 61.6974 | -62.059 | -0.3067 | 0.1236 | -0.21057 | -0.09613 | -0.38452 | -0.25177 | 0.10986 | 0.096131 | 61.7752 | 61.8805 | 123.0103 | 123.5184 | -0.21057 | 123.5046 | 61.8896 | -0.25177 | 123.5184 | -0.21057 | 61.8896 | 123.0103 | 123.5046 | -123.7015 | -123.6465
324.6875 | 123.5458 | -61.8347 | 61.6745 | -0.012589 | 0.019094 | 0.011551 | -0.0042383 | 0.062906 | -0.0027323 | 0.070184 | -61.8301 | 61.7065 | -61.9858 | -61.7157 | 61.4182 | 0.28381 | -0.10986 | 0.32501 | 61.6791 | -61.9949 | -0.15106 | 0.032043 | 0.004578 | 0.11902 | -0.25635 | -0.16022 | 0.004577 | 0.15564 | 61.7249 | 62.1597 | 123.2529 | 123.5413 | 0.004578 | 123.5138 | 62.1185 | -0.16022 | 123.5413 | 0.004578 | 62.1185 | 123.2529 | 123.5138 | -123.6603 | -123.6694
326.4375 | 123.6099 | -61.8027 | 61.6928 | -0.0049592 | 0.017598 | 0.0092007 | -0.0025293 | 0.064401 | -0.0031595 | 0.069757 | -61.908 | 61.7203 | -62.0041 | -61.7798 | 61.3312 | 0.20599 | -0.1236 | 0.17853 | 61.7249 | -62.0178 | -0.20142 | 0.027466 | -0.10529 | 0.022888 | -0.36163 | -0.21515 | 0.032044 | 0.09613 | 61.6791 | 61.9812 | 123.1338 | 123.5229 | -0.10529 | 123.5275 | 62.0087 | -0.21515 | 123.5229 | -0.10529 | 62.0087 | 123.1338 | 123.5275 | -123.6969 | -123.7106
328.1875 | 123.6969 | -61.8073 | 61.6241 | 0.0026703 | 0.024221 | 0.014541 | 0.0015295 | 0.064401 | -0.0057229 | 0.070397 | -61.9812 | 61.7249 | -62.1002 | -61.8668 | 61.2259 | 0.091553 | -0.073242 | 0.082397 | 61.7065 | -62.059 | -0.29297 | 0.10071 | -0.17395 | -0.059509 | -0.39826 | -0.25177 | 0.082397 | 0.11902 | 61.734 | 61.8896 | 123.0331 | 123.5321 | -0.17395 | 123.5138 | 61.8988 | -0.25177 | 123.5321 | -0.17395 | 61.8988 | 123.0331 | 123.5138 | -123.7244 | -123.6832
329.875 | 123.6969 | -61.8118 | 61.615 | -0.0049592 | 0.020375 | 0.017319 | -0.0012475 | 0.064828 | -0.0038003 | 0.068688 | -61.9629 | 61.734 | -62.0865 | -61.8256 | 61.2671 | 0.15106 | 0.091553 | 0.21057 | 61.7203 | -62.0407 | -0.27466 | 0.11902 | -0.15106 | -0.013733 | -0.3479 | -0.22888 | 0.10529 | 0.1236 | 61.9034 | 62.0224 | 123.0789 | 123.5458 | -0.15106 | 123.5321 | 61.9629 | -0.22888 | 123.5458 | -0.15106 | 61.9629 | 123.0789 | 123.5321 | -123.7015 | -123.6557
331.625 | 123.6832 | -61.8027 | 61.6287 | 0.0026703 | 0.01888 | 0.013687 | 0.00067508 | 0.065256 | -0.0059365 | 0.06997 | -61.9949 | 61.6837 | -62.1231 | -61.853 | 61.235 | 0.10529 | -0.1236 | 0.09613 | 61.702 | -62.0453 | -0.32044 | 0.054932 | -0.19226 | -0.050354 | -0.39368 | -0.24262 | 0.073242 | 0.12817 | 61.6791 | 61.8988 | 123.0377 | 123.4863 | -0.19226 | 123.5046 | 61.908 | -0.24262 | 123.4863 | -0.19226 | 61.908 | 123.0377 | 123.5046 | -123.7518 | -123.674
333.375 | 123.6694 | -61.8027 | 61.5875 | 0.0026703 | 0.019734 | 0.012405 | -0.0031701 | 0.063547 | -0.0057229 | 0.069329 | -61.9583 | 61.7111 | -62.0911 | -61.8164 | 61.2808 | 0.16022 | 0.10071 | 0.20142 | 61.7432 | -62.0178 | -0.28839 | 0.1236 | -0.15564 | -0.013733 | -0.3067 | -0.21515 | 0.15564 | 0.13275 | 61.9034 | 62.0041 | 123.0835 | 123.5138 | -0.15564 | 123.5458 | 61.9629 | -0.21515 | 123.5138 | -0.15564 | 61.9629 | 123.0835 | 123.5458 | -123.6786 | -123.6053
335.0781 | 123.5367 | -61.8393 | 61.6653 | 0.0026703 | 0.017812 | 0.018173 | -0.0059473 | 0.062051 | -0.0029459 | 0.070184 | -61.8484 | 61.702 | -62.0316 | -61.7111 | 61.3861 | 0.27008 | -0.082397 | 0.30212 | 61.702 | -61.9995 | -0.19226 | 0.036621 | -0.009156 | 0.12817 | -0.27924 | -0.16022 | 0.036621 | 0.1831 | 61.7569 | 62.1414 | 123.2254 | 123.5413 | -0.009156 | 123.5413 | 62.1094 | -0.16022 | 123.5413 | -0.009156 | 62.1094 | 123.2254 | 123.5413 | -123.6969 | -123.6649
336.8125 | 123.6008 | -61.7935 | 61.6974 | 0.0026703 | 0.020375 | 0.013473 | -0.0050927 | 0.061838 | -0.0014505 | 0.070397 | -61.8896 | 61.6837 | -62.0132 | -61.7706 | 61.3266 | 0.17853 | -0.16022 | 0.17395 | 61.6608 | -61.9904 | -0.21973 | -0.013733 | -0.09613 | 0.022888 | -0.37079 | -0.19684 | -0.036621 | 0.1236 | 61.6333 | 61.9675 | 123.1201 | 123.4772 | -0.09613 | 123.4543 | 61.972 | -0.19684 | 123.4772 | -0.09613 | 61.972 | 123.1201 | 123.4543 | -123.7106 | -123.6877
338.5781 | 123.6374 | -61.8027 | 61.5967 | -0.0049592 | 0.018239 | 0.01091 | 0.00088868 | 0.062906 | -0.0040139 | 0.070184 | -61.9125 | 61.7157 | -62.0453 | -61.7981 | 61.2854 | 0.16937 | 0.091553 | 0.21973 | 61.7432 | -61.9904 | -0.24262 | 0.11902 | -0.10986 | 0.004577 | -0.31128 | -0.18768 | 0.14648 | 0.13275 | 61.8942 | 62.0224 | 123.0881 | 123.5184 | -0.10986 | 123.5458 | 61.972 | -0.18768 | 123.5184 | -0.10986 | 61.972 | 123.0881 | 123.5458 | -123.642 | -123.587
340.2656 | 123.6649 | -61.8118 | 61.5784 | -0.0049592 | 0.019094 | 0.016891 | -0.00017952 | 0.063119 | -0.0061503 | 0.070397 | -62.0041 | 61.6837 | -62.1002 | -61.8713 | 61.1984 | 0.073242 | -0.036621 | 0.059509 | 61.6837 | -62.0453 | -0.28839 | 0.10529 | -0.19226 | -0.059509 | -0.37994 | -0.23346 | 0.10529 | 0.096131 | 61.7752 | 61.8713 | 123.0103 | 123.4955 | -0.19226 | 123.4955 | 61.8851 | -0.23346 | 123.4955 | -0.19226 | 61.8851 | 123.0103 | 123.4955 | -123.6786 | -123.6237
342.0156 | 123.5779 | -61.8027 | 61.6699 | -0.012589 | 0.016957 | 0.01561 | -0.0046655 | 0.063119 | -0.0042277 | 0.068688 | -61.8896 | 61.6837 | -62.0087 | -61.7569 | 61.3358 | 0.20599 | -0.17395 | 0.19684 | 61.6608 | -61.9904 | -0.20599 | 0.013733 | -0.086975 | 0.045776 | -0.33417 | -0.18768 | -0.009155 | 0.11902 | 61.6287 | 61.9995 | 123.1384 | 123.4863 | -0.086975 | 123.4634 | 62.0087 | -0.18768 | 123.4863 | -0.086975 | 62.0087 | 123.1384 | 123.4634 | -123.6786 | -123.6603
343.7656 | 123.6649 | -61.8073 | 61.5875 | 0.0026703 | 0.019094 | 0.014114 | 0.0011023 | 0.064828 | -0.0040139 | 0.069757 | -61.9858 | 61.6745 | -62.0956 | -61.8668 | 61.203 | 0.068665 | 0 | 0.09613 | 61.702 | -62.0041 | -0.28839 | 0.086976 | -0.17853 | -0.059509 | -0.38452 | -0.19684 | 0.11444 | 0.10986 | 61.8073 | 61.9034 | 123.0103 | 123.4818 | -0.17853 | 123.5092 | 61.8759 | -0.19684 | 123.4818 | -0.17853 | 61.8759 | 123.0103 | 123.5092 | -123.6832 | -123.5916
345.4531 | 123.5458 | -61.8118 | 61.6791 | -0.0049592 | 0.018453 | 0.013687 | -0.00039312 | 0.06376 | -0.0033731 | 0.069116 | -61.8393 | 61.6745 | -62.0361 | -61.7477 | 61.3403 | 0.21057 | -0.26093 | 0.18768 | 61.647 | -61.9904 | -0.2243 | -0.004577 | -0.027465 | 0.064087 | -0.33875 | -0.17853 | -0.032043 | 0.19684 | 61.5509 | 61.9995 | 123.1522 | 123.4863 | -0.027465 | 123.4589 | 62.0224 | -0.17853 | 123.4863 | -0.027465 | 62.0224 | 123.1522 | 123.4589 | -123.7152 | -123.6694
347.2031 | 123.5779 | -61.7661 | 61.6562 | 0.017929 | 0.019094 | 0.016037 | -0.0048791 | 0.062906 | -0.0042277 | 0.069329 | -61.8805 | 61.7065 | -62.0224 | -61.7477 | 61.3495 | 0.22888 | -0.11444 | 0.23804 | 61.6974 | -61.9858 | -0.25635 | 0.050354 | -0.11444 | 0.01831 | -0.3067 | -0.21973 | 0.041199 | 0.14191 | 61.6516 | 62.0041 | 123.1155 | 123.4726 | -0.11444 | 123.4634 | 61.9949 | -0.21973 | 123.4726 | -0.11444 | 61.9949 | 123.1155 | 123.4634 | -123.6786 | -123.642
348.9062 | 123.5092 | -61.8073 | 61.6562 | -0.0049592 | 0.018666 | 0.0096279 | -0.0035973 | 0.062478 | -0.0042277 | 0.068261 | -61.8118 | 61.6837 | -61.9904 | -61.6791 | 61.3953 | 0.28839 | -0.10071 | 0.33417 | 61.7065 | -61.94 | -0.1831 | 0.027466 | -0.004578 | 0.12817 | -0.26093 | -0.13275 | 0.050354 | 0.17853 | 61.7065 | 62.1414 | 123.2025 | 123.4909 | -0.004578 | 123.5138 | 62.0956 | -0.13275 | 123.4909 | -0.004578 | 62.0956 | 123.2025 | 123.5138 | -123.6465 | -123.5962
350.6562 | 123.5275 | -61.7889 | 61.6608 | -0.012589 | 0.017171 | 0.014755 | -0.0023157 | 0.062692 | -0.0033731 | 0.069329 | -61.8393 | 61.7065 | -62.0132 | -61.6882 | 61.3815 | 0.2655 | -0.12817 | 0.28839 | 61.7111 | -61.9812 | -0.22431 | 0.045776 | -0.050354 | 0.10071 | -0.27924 | -0.19226 | 0.050354 | 0.17395 | 61.6608 | 62.0773 | 123.1705 | 123.4955 | -0.050354 | 123.5001 | 62.0544 | -0.19226 | 123.4955 | -0.050354 | 62.0544 | 123.1705 | 123.5001 | -123.674 | -123.642
352.4062 | 123.5184 | -61.8027 | 61.6562 | -0.012589 | 0.017171 | 0.015182 | -0.0021021 | 0.062265 | -0.0074319 | 0.068048 | -61.8347 | 61.6699 | -62.0316 | -61.6837 | 61.3907 | 0.27008 | -0.09613 | 0.32959 | 61.6974 | -61.9354 | -0.22888 | 0.013733 | -0.032044 | 0.11902 | -0.2655 | -0.13275 | 0.041199 | 0.19684 | 61.7065 | 62.1323 | 123.1934 | 123.4726 | -0.032044 | 123.5001 | 62.0728 | -0.13275 | 123.4726 | -0.032044 | 62.0728 | 123.1934 | 123.5001 | -123.6877 | -123.5916
354.1094 | 123.555 | -61.7844 | 61.6241 | 0.0103 | 0.017812 | 0.014114 | -0.0018885 | 0.063119 | -0.0031595 | 0.068688 | -61.8713 | 61.6974 | -62.059 | -61.7294 | 61.3174 | 0.21057 | 0.009155 | 0.27008 | 61.7203 | -61.9812 | -0.27466 | 0.073242 | -0.086975 | 0.054932 | -0.3067 | -0.19684 | 0.09613 | 0.18768 | 61.7935 | 62.0544 | 123.1018 | 123.4818 | -0.086975 | 123.5046 | 61.9949 | -0.19684 | 123.4818 | -0.086975 | 61.9949 | 123.1018 | 123.5046 | -123.6832 | -123.6053
355.875 | 123.6465 | -61.7752 | 61.5784 | 0.0026703 | 0.019521 | 0.011337 | -0.00017952 | 0.062906 | -0.0050821 | 0.069116 | -61.94 | 61.7157 | -62.0682 | -61.8027 | 61.2625 | 0.15106 | 0.11444 | 0.21057 | 61.7249 | -62.0178 | -0.29297 | 0.13733 | -0.16479 | -0.027465 | -0.31586 | -0.24261 | 0.14648 | 0.12817 | 61.8896 | 61.9858 | 123.0377 | 123.4909 | -0.16479 | 123.5001 | 61.9263 | -0.24261 | 123.4909 | -0.16479 | 61.9263 | 123.0377 | 123.5001 | -123.6465 | -123.5962
357.6406 | 123.5458 | -61.7889 | 61.647 | -0.012589 | 0.019094 | 0.011978 | -0.0025293 | 0.063119 | -0.0042277 | 0.068261 | -61.8301 | 61.702 | -61.9675 | -61.6882 | 61.3724 | 0.26093 | -0.11902 | 0.28839 | 61.6974 | -61.9629 | -0.17853 | 0.054931 | -0.041199 | 0.10071 | -0.27466 | -0.17395 | 0.050354 | 0.13733 | 61.6699 | 62.0773 | 123.1613 | 123.4909 | -0.041199 | 123.4863 | 62.0499 | -0.17395 | 123.4909 | -0.041199 | 62.0499 | 123.1613 | 123.4863 | -123.6145 | -123.6099
359.3906 | 123.5962 | -61.8301 | 61.5646 | 0.0026703 | 0.018453 | 0.0098417 | 0.0017431 | 0.062692 | -0.0057229 | 0.069329 | -61.8988 | 61.6562 | -62.0911 | -61.7844 | 61.2671 | 0.17395 | -0.032043 | 0.21515 | 61.6745 | -62.0316 | -0.26093 | 0.091553 | -0.068665 | 0.045776 | -0.29755 | -0.20142 | 0.10986 | 0.19226 | 61.7981 | 62.0453 | 123.0972 | 123.4863 | -0.068665 | 123.5046 | 62.0041 | -0.20142 | 123.4863 | -0.068665 | 62.0041 | 123.0972 | 123.5046 | -123.6557 | -123.5962
361.0781 | 123.5184 | -61.7889 | 61.6196 | -0.0049592 | 0.019094 | 0.01091 | -0.0035973 | 0.062265 | -0.0044413 | 0.068475 | -61.8301 | 61.6837 | -62.0178 | -61.6837 | 61.3861 | 0.27924 | -0.086975 | 0.31586 | 61.6699 | -61.9583 | -0.22888 | 0.064087 | -0.041199 | 0.10528 | -0.23346 | -0.16937 | 0.050354 | 0.18768 | 61.702 | 62.1048 | 123.175 | 123.4726 | -0.041199 | 123.4589 | 62.0682 | -0.16937 | 123.4726 | -0.041199 | 62.0682 | 123.175 | 123.4589 | -123.6374 | -123.5779
362.8438 | 123.5321 | -61.7844 | 61.6333 | -0.0049592 | 0.019521 | 0.014541 | -0.0061609 | 0.062906 | -0.0029459 | 0.069329 | -61.8256 | 61.702 | -61.9629 | -61.6837 | 61.3907 | 0.28839 | -0.11902 | 0.28839 | 61.6928 | -61.9583 | -0.17853 | 0.068664 | -0.041199 | 0.10071 | -0.24262 | -0.17395 | 0.059509 | 0.13733 | 61.6653 | 62.0728 | 123.175 | 123.4863 | -0.041199 | 123.4772 | 62.0728 | -0.17395 | 123.4863 | -0.041199 | 62.0728 | 123.175 | 123.4772 | -123.5962 | -123.5916
364.5938 | 123.5825 | -61.7935 | 61.6425 | -0.0049592 | 0.018025 | 0.016037 | 0.0021705 | 0.06376 | -0.0031595 | 0.07232 | -61.9217 | 61.6791 | -62.1002 | -61.7798 | 61.2762 | 0.15564 | -0.17853 | 0.16937 | 61.6653 | -61.9675 | -0.3067 | 0.036621 | -0.12817 | 0.013733 | -0.36621 | -0.17395 | 0.022888 | 0.17853 | 61.615 | 61.9629 | 123.0698 | 123.4726 | -0.12817 | 123.4589 | 61.9492 | -0.17395 | 123.4726 | -0.12817 | 61.9492 | 123.0698 | 123.4589 | -123.7427 | -123.6099
366.2656 | 123.5184 | -61.8027 | 61.6425 | -0.012589 | 0.019094 | 0.014755 | -0.0021021 | 0.062906 | -0.0035867 | 0.068688 | -61.8118 | 61.6928 | -61.972 | -61.6562 | 61.3861 | 0.27924 | -0.091553 | 0.32959 | 61.6928 | -61.9537 | -0.16937 | 0.050354 | -0.009156 | 0.14648 | -0.25635 | -0.15106 | 0.050354 | 0.16022 | 61.7111 | 62.1323 | 123.1888 | 123.4955 | -0.009156 | 123.4955 | 62.0819 | -0.15106 | 123.4955 | -0.009156 | 62.0819 | 123.1888 | 123.4955 | -123.6145 | -123.5962
368.0156 | 123.5504 | -61.7706 | 61.6837 | -0.0049592 | 0.019307 | 0.011551 | -0.0027429 | 0.063547 | -0.0016641 | 0.068902 | -61.8713 | 61.6837 | -62.0224 | -61.7569 | 61.3358 | 0.19226 | -0.16479 | 0.1831 | 61.6837 | -61.9583 | -0.25177 | 0 | -0.10071 | 0.013733 | -0.3479 | -0.18768 | 0 | 0.15106 | 61.6058 | 61.9537 | 123.1064 | 123.4543 | -0.10071 | 123.4543 | 61.9629 | -0.18768 | 123.4543 | -0.10071 | 61.9629 | 123.1064 | 123.4543 | -123.7061 | -123.642
369.7031 | 123.6237 | -61.7844 | 61.6058 | -0.012589 | 0.022084 | 0.020736 | 0.0023841 | 0.062051 | -0.0042277 | 0.068048 | -61.9492 | 61.6699 | -62.0956 | -61.821 | 61.2076 | 0.10071 | -0.11444 | 0.09613 | 61.6653 | -62.0132 | -0.31128 | 0.064087 | -0.16479 | -0.036621 | -0.39825 | -0.22888 | 0.059509 | 0.14648 | 61.6699 | 61.8805 | 122.9919 | 123.4543 | -0.16479 | 123.4497 | 61.8851 | -0.22888 | 123.4543 | -0.16479 | 61.8851 | 122.9919 | 123.4497 | -123.7015 | -123.6191
371.4531 | 123.5687 | -61.7889 | 61.6333 | 0.0026703 | 0.019521 | 0.013046 | -0.00039312 | 0.065683 | -0.0055093 | 0.069116 | -61.9125 | 61.6653 | -62.0682 | -61.7432 | 61.2946 | 0.16022 | -0.18768 | 0.16479 | 61.6516 | -62.0041 | -0.27924 | 0.032043 | -0.1236 | 0.045776 | -0.33875 | -0.21515 | 0.01831 | 0.15564 | 61.6013 | 61.9537 | 123.0835 | 123.4543 | -0.1236 | 123.4406 | 61.9492 | -0.21515 | 123.4543 | -0.1236 | 61.9492 | 123.0835 | 123.4406 | -123.7015 | -123.6374
373.1562 | 123.5413 | -61.7569 | 61.647 | 0.0026703 | 0.017385 | 0.016464 | -0.0033837 | 0.062265 | -0.0055093 | 0.06997 | -61.8713 | 61.6974 | -62.0087 | -61.734 | 61.3495 | 0.21973 | -0.11444 | 0.23346 | 61.6882 | -61.9583 | -0.25177 | 0.050354 | -0.11444 | 0.022888 | -0.29755 | -0.20142 | 0.041198 | 0.13733 | 61.6425 | 61.9904 | 123.1064 | 123.4543 | -0.11444 | 123.4451 | 61.9766 | -0.20142 | 123.4543 | -0.11444 | 61.9766 | 123.1064 | 123.4451 | -123.6557 | -123.6053
374.9062 | 123.5413 | -61.7889 | 61.6333 | 0.0026703 | 0.01653 | 0.014969 | -0.00060672 | 0.063119 | -0.0070047 | 0.069543 | -61.8942 | 61.6287 | -62.0544 | -61.734 | 61.2946 | 0.19684 | -0.19684 | 0.19226 | 61.6608 | -61.9446 | -0.2655 | -0.004578 | -0.10529 | 0.054931 | -0.33875 | -0.15564 | 0.027466 | 0.16022 | 61.5921 | 61.9812 | 123.0835 | 123.4177 | -0.10529 | 123.4497 | 61.9858 | -0.15564 | 123.4177 | -0.10529 | 61.9858 | 123.0835 | 123.4497 | -123.6877 | -123.5779
376.5938 | 123.5321 | -61.7798 | 61.6241 | -0.012589 | 0.018239 | 0.01561 | -0.0059473 | 0.062265 | -0.0038003 | 0.068475 | -61.8759 | 61.6928 | -61.9812 | -61.7157 | 61.3266 | 0.23346 | -0.1236 | 0.21057 | 61.702 | -61.9492 | -0.20142 | 0.068664 | -0.096131 | 0.064087 | -0.29755 | -0.16937 | 0.077819 | 0.10529 | 61.6562 | 61.9904 | 123.1064 | 123.4726 | -0.096131 | 123.4818 | 62.0132 | -0.16937 | 123.4726 | -0.096131 | 62.0132 | 123.1064 | 123.4818 | -123.6053 | -123.5733
378.3438 | 123.5458 | -61.7523 | 61.6425 | -0.0049592 | 0.018666 | 0.015396 | -0.0031701 | 0.062906 | -0.0052957 | 0.069329 | -61.8759 | 61.6699 | -62.0132 | -61.7432 | 61.3174 | 0.20599 | -0.13733 | 0.1831 | 61.6699 | -61.972 | -0.26093 | 0.027466 | -0.1236 | 0.009155 | -0.32501 | -0.21973 | 0.027466 | 0.13733 | 61.615 | 61.9354 | 123.0698 | 123.4222 | -0.1236 | 123.4222 | 61.9583 | -0.21973 | 123.4222 | -0.1236 | 61.9583 | 123.0698 | 123.4222 | -123.6557 | -123.6145
380.0938 | 123.5229 | -61.7752 | 61.6516 | -0.0049592 | 0.016744 | 0.014755 | -0.0012475 | 0.064187 | -0.0082865 | 0.070184 | -61.8439 | 61.6745 | -62.0087 | -61.6882 | 61.3449 | 0.24719 | 0 | 0.30212 | 61.6882 | -61.9354 | -0.23346 | 0.022889 | -0.068664 | 0.086976 | -0.3067 | -0.16022 | 0.036621 | 0.1648 | 61.7752 | 62.0773 | 123.1201 | 123.4497 | -0.068664 | 123.4634 | 62.0224 | -0.16022 | 123.4497 | -0.068664 | 62.0224 | 123.1201 | 123.4634 | -123.6603 | -123.587
381.8438 | 123.6053 | -61.8027 | 61.5921 | 0.0103 | 0.019094 | 0.017105 | 0.0013159 | 0.064615 | -0.0063639 | 0.068475 | -61.9171 | 61.6333 | -62.0956 | -61.8027 | 61.2213 | 0.13275 | -0.022888 | 0.15106 | 61.6608 | -62.0132 | -0.29297 | 0.041199 | -0.11444 | 0 | -0.37079 | -0.21057 | 0.068665 | 0.17853 | 61.7798 | 61.9537 | 123.024 | 123.436 | -0.11444 | 123.4634 | 61.9354 | -0.21057 | 123.436 | -0.11444 | 61.9354 | 123.024 | 123.4634 | -123.6877 | -123.6053
383.5156 | 123.4909 | -61.7615 | 61.6425 | -0.0049592 | 0.01653 | 0.014755 | -0.0038111 | 0.064187 | -0.0018777 | 0.069757 | -61.8256 | 61.7065 | -61.9583 | -61.6653 | 61.3724 | 0.28839 | -0.1236 | 0.27924 | 61.6608 | -61.9537 | -0.19684 | 0.064087 | -0.064087 | 0.096131 | -0.27008 | -0.19226 | 0.018311 | 0.13275 | 61.6379 | 62.0407 | 123.1338 | 123.468 | -0.064087 | 123.4222 | 62.0499 | -0.19226 | 123.468 | -0.064087 | 62.0499 | 123.1338 | 123.4222 | -123.6008 | -123.5962
385.2656 | 123.4909 | -61.7752 | 61.6653 | 0.0026703 | 0.01888 | 0.012619 | -0.00039312 | 0.063974 | -0.0042277 | 0.070397 | -61.8301 | 61.6241 | -62.0636 | -61.7111 | 61.322 | 0.20599 | -0.23346 | 0.18768 | 61.647 | -61.9812 | -0.28839 | -0.041198 | -0.054931 | 0.064087 | -0.34332 | -0.20599 | -0.01831 | 0.23346 | 61.5417 | 61.9629 | 123.0972 | 123.3994 | -0.054931 | 123.4222 | 61.9812 | -0.20599 | 123.3994 | -0.054931 | 61.9812 | 123.0972 | 123.4222 | -123.7289 | -123.6465
387 | 123.5046 | -61.7889 | 61.615 | -0.0049592 | 0.018239 | 0.015396 | -0.0010339 | 0.063333 | -0.0065775 | 0.070184 | -61.8439 | 61.6241 | -62.0178 | -61.7111 | 61.3312 | 0.21515 | -0.23346 | 0.20599 | 61.615 | -61.972 | -0.22888 | 0.009156 | -0.054932 | 0.077819 | -0.28381 | -0.18311 | 0 | 0.17395 | 61.5555 | 61.9949 | 123.1201 | 123.4131 | -0.054932 | 123.4039 | 62.0041 | -0.18311 | 123.4131 | -0.054932 | 62.0041 | 123.1201 | 123.4039 | -123.6328 | -123.587
388.6719 | 123.5458 | -61.7523 | 61.647 | 0.0026703 | 0.019094 | 0.014755 | -0.0023157 | 0.062906 | -0.0048685 | 0.070611 | -61.8622 | 61.6745 | -61.9904 | -61.734 | 61.3037 | 0.19226 | -0.16022 | 0.19226 | 61.6837 | -61.9766 | -0.23804 | 0.027466 | -0.10986 | 0.01831 | -0.34332 | -0.22431 | 0.036621 | 0.12817 | 61.5921 | 61.9446 | 123.056 | 123.4268 | -0.10986 | 123.436 | 61.9446 | -0.22431 | 123.4268 | -0.10986 | 61.9446 | 123.056 | 123.436 | -123.6374 | -123.6237
390.4219 | 123.6191 | -61.7798 | 61.5646 | -0.0049592 | 0.022725 | 0.014541 | 0.0034521 | 0.062692 | -0.0070047 | 0.069757 | -61.9766 | 61.6287 | -62.1002 | -61.8347 | 61.1664 | 0.082397 | 0.009155 | 0.11444 | 61.6653 | -61.9949 | -0.32044 | 0.064087 | -0.19684 | -0.054932 | -0.39825 | -0.21515 | 0.10071 | 0.1236 | 61.7889 | 61.8942 | 122.9462 | 123.4085 | -0.19684 | 123.4451 | 61.8622 | -0.21515 | 123.4085 | -0.19684 | 61.8622 | 122.9462 | 123.4451 | -123.6649 | -123.5596
392.1094 | 123.5046 | -61.8118 | 61.5967 | 0.0026703 | 0.018239 | 0.016464 | -0.00060672 | 0.063333 | -0.0046549 | 0.071038 | -61.8942 | 61.6241 | -62.0544 | -61.7432 | 61.2991 | 0.17853 | -0.21057 | 0.18768 | 61.6058 | -61.9629 | -0.24261 | 0.027466 | -0.082397 | 0.068665 | -0.29755 | -0.15106 | 0.009155 | 0.16022 | 61.6013 | 61.9995 | 123.111 | 123.436 | -0.082397 | 123.4177 | 61.9904 | -0.15106 | 123.436 | -0.082397 | 61.9904 | 123.111 | 123.4177 | -123.6511 | -123.5596
393.8594 | 123.5916 | -61.7935 | 61.5738 | -0.012589 | 0.023366 | 0.016891 | 0.0028113 | 0.064615 | -0.0044413 | 0.06997 | -61.908 | 61.7111 | -62.0361 | -61.8073 | 61.1984 | 0.10986 | -0.027466 | 0.15106 | 61.6425 | -62.027 | -0.24262 | 0.13733 | -0.11444 | -0.013733 | -0.37537 | -0.23346 | 0.068664 | 0.12817 | 61.7661 | 61.9446 | 122.9919 | 123.5046 | -0.11444 | 123.436 | 61.9034 | -0.23346 | 123.5046 | -0.11444 | 61.9034 | 122.9919 | 123.436 | -123.6099 | -123.6008
395.5469 | 123.4726 | -61.7661 | 61.647 | -0.012589 | 0.016103 | 0.010269 | -0.0048791 | 0.063547 | -0.0035867 | 0.06997 | -61.7889 | 61.6837 | -61.9858 | -61.6562 | 61.3953 | 0.29297 | -0.10986 | 0.32501 | 61.6745 | -61.9308 | -0.21973 | 0.036621 | -0.022888 | 0.10986 | -0.25177 | -0.16479 | 0.027466 | 0.19684 | 61.6562 | 62.0911 | 123.1613 | 123.4497 | -0.022888 | 123.4406 | 62.059 | -0.16479 | 123.4497 | -0.022888 | 62.059 | 123.1613 | 123.4406 | -123.6328 | -123.5779
397.2969 | 123.555 | -61.7798 | 61.5967 | 0.0026703 | 0.019521 | 0.016891 | -0.0018885 | 0.064615 | -0.0078591 | 0.06997 | -61.9125 | 61.6241 | -62.0773 | -61.7752 | 61.2671 | 0.16479 | -0.17395 | 0.16022 | 61.647 | -61.9492 | -0.29755 | 0.027466 | -0.13275 | 0.004577 | -0.32959 | -0.16937 | 0.050354 | 0.16479 | 61.6058 | 61.94 | 123.0469 | 123.4039 | -0.13275 | 123.4268 | 61.9446 | -0.16937 | 123.4039 | -0.13275 | 61.9446 | 123.0469 | 123.4268 | -123.674 | -123.5458
399.0469 | 123.4726 | -61.7477 | 61.647 | -0.0049592 | 0.019734 | 0.016037 | -0.0038111 | 0.063547 | -0.0025187 | 0.070184 | -61.8256 | 61.6608 | -61.9858 | -61.7065 | 61.3129 | 0.21515 | -0.2243 | 0.19684 | 61.6333 | -61.9629 | -0.23804 | 0.013733 | -0.07782 | 0.041199 | -0.33417 | -0.21515 | -0.013733 | 0.16022 | 61.5234 | 61.9446 | 123.0606 | 123.4085 | -0.07782 | 123.381 | 61.9629 | -0.21515 | 123.4085 | -0.07782 | 61.9629 | 123.0606 | 123.381 | -123.6328 | -123.6099
400.7969 | 123.468 | -61.7798 | 61.6013 | 0.0026703 | 0.017385 | 0.015182 | -0.0035973 | 0.062265 | -0.0057229 | 0.068048 | -61.7935 | 61.6608 | -61.9675 | -61.6425 | 61.3724 | 0.29297 | -0.09613 | 0.32044 | 61.6791 | -61.9125 | -0.18768 | 0.05951 | -0.013733 | 0.13733 | -0.22888 | -0.13275 | 0.07782 | 0.17395 | 61.6837 | 62.1002 | 123.1522 | 123.4406 | -0.013733 | 123.4589 | 62.0728 | -0.13275 | 123.4406 | -0.013733 | 62.0728 | 123.1522 | 123.4589 | -123.5687 | -123.5138
402.4844 | 123.5962 | -61.7569 | 61.5875 | 0.0026703 | 0.018239 | 0.012619 | 0.00067508 | 0.064401 | -0.0048685 | 0.070397 | -61.94 | 61.6287 | -62.0773 | -61.8118 | 61.1984 | 0.10529 | -0.11444 | 0.091553 | 61.6699 | -61.9492 | -0.32043 | 0.041199 | -0.1831 | -0.054932 | -0.3891 | -0.19226 | 0.082398 | 0.13733 | 61.6425 | 61.8484 | 122.9553 | 123.3856 | -0.1831 | 123.4268 | 61.8622 | -0.19226 | 123.3856 | -0.1831 | 61.8622 | 122.9553 | 123.4268 | -123.6649 | -123.5367
404.2344 | 123.4772 | -61.7752 | 61.6241 | 0.0026703 | 0.018666 | 0.01561 | -0.0055199 | 0.06376 | -0.0059365 | 0.067193 | -61.7889 | 61.6516 | -61.9629 | -61.647 | 61.3861 | 0.30212 | -0.10529 | 0.34332 | 61.6837 | -61.9263 | -0.18768 | 0.027465 | -0.013732 | 0.12817 | -0.23804 | -0.15106 | 0.059509 | 0.17395 | 61.6699 | 62.1185 | 123.1613 | 123.4268 | -0.013732 | 123.4589 | 62.0773 | -0.15106 | 123.4268 | -0.013732 | 62.0773 | 123.1613 | 123.4589 | -123.587 | -123.5504
405.9844 | 123.5596 | -61.7386 | 61.5601 | 0.0026703 | 0.018025 | 0.016037 | -0.0023157 | 0.061838 | -0.0061503 | 0.069329 | -61.9034 | 61.6699 | -62.0132 | -61.7706 | 61.2488 | 0.16937 | 0.09613 | 0.21515 | 61.702 | -61.9858 | -0.27466 | 0.10986 | -0.1648 | -0.032044 | -0.31128 | -0.24719 | 0.14191 | 0.10986 | 61.8347 | 61.9537 | 122.9874 | 123.4085 | -0.1648 | 123.4406 | 61.908 | -0.24719 | 123.4085 | -0.1648 | 61.908 | 122.9874 | 123.4406 | -123.5733 | -123.5458
407.6719 | 123.5916 | -61.7615 | 61.5097 | 0.0026703 | 0.018666 | 0.012192 | -0.00082032 | 0.06376 | -0.0057229 | 0.068475 | -61.9263 | 61.7065 | -62.0544 | -61.7706 | 61.2167 | 0.15564 | 0.11902 | 0.20142 | 61.6928 | -61.9766 | -0.29297 | 0.19684 | -0.1648 | -0.009155 | -0.29297 | -0.21515 | 0.18311 | 0.12817 | 61.8805 | 61.9629 | 122.9782 | 123.468 | -0.1648 | 123.4543 | 61.9171 | -0.21515 | 123.468 | -0.1648 | 61.9171 | 122.9782 | 123.4543 | -123.5641 | -123.4863
409.4219 | 123.5916 | -61.7569 | 61.5646 | -0.0049592 | 0.019948 | 0.015823 | -0.0010339 | 0.064187 | -0.0052957 | 0.069329 | -61.908 | 61.7157 | -62.0361 | -61.7798 | 61.2259 | 0.15106 | 0.10071 | 0.20599 | 61.7249 | -61.9675 | -0.27924 | 0.15106 | -0.15106 | -0.022888 | -0.33875 | -0.21057 | 0.16022 | 0.12817 | 61.8576 | 61.9629 | 122.9828 | 123.4726 | -0.15106 | 123.4818 | 61.908 | -0.21057 | 123.4726 | -0.15106 | 61.908 | 122.9828 | 123.4818 | -123.6008 | -123.5321
411.1719 | 123.5184 | -61.734 | 61.6379 | -0.0049592 | 0.019307 | 0.01326 | -0.0072289 | 0.062265 | -0.0035867 | 0.071038 | -61.8576 | 61.6882 | -61.9446 | -61.7157 | 61.2991 | 0.21057 | -0.11444 | 0.21057 | 61.6653 | -61.9537 | -0.21057 | 0.050354 | -0.1236 | 0.018311 | -0.33875 | -0.21973 | 0.027466 | 0.086975 | 61.6196 | 61.9446 | 123.0331 | 123.4222 | -0.1236 | 123.3994 | 61.9446 | -0.21973 | 123.4222 | -0.1236 | 61.9446 | 123.0331 | 123.3994 | -123.5825 | -123.5916
412.9062 | 123.468 | -61.7798 | 61.6058 | 0.0026703 | 0.019521 | 0.011551 | -0.0031701 | 0.063119 | -0.0040139 | 0.068261 | -61.7889 | 61.6653 | -61.9675 | -61.6562 | 61.3495 | 0.27924 | -0.064087 | 0.32044 | 61.6516 | -61.9537 | -0.18768 | 0.059509 | -0.009155 | 0.1236 | -0.25635 | -0.17395 | 0.045776 | 0.17853 | 61.7157 | 62.1002 | 123.1293 | 123.4451 | -0.009155 | 123.4314 | 62.059 | -0.17395 | 123.4451 | -0.009155 | 62.059 | 123.1293 | 123.4314 | -123.5733 | -123.5596
414.5781 | 123.5458 | -61.7706 | 61.5738 | -0.0049592 | 0.020162 | 0.016037 | 0.0030249 | 0.065683 | -0.0057229 | 0.069329 | -61.8668 | 61.6745 | -62.027 | -61.7477 | 61.2305 | 0.13733 | -0.027466 | 0.19226 | 61.6745 | -61.9995 | -0.25635 | 0.10071 | -0.09613 | 0.022888 | -0.34332 | -0.22888 | 0.10071 | 0.16022 | 61.7432 | 61.9629 | 123.0011 | 123.4451 | -0.09613 | 123.4451 | 61.908 | -0.22888 | 123.4451 | -0.09613 | 61.908 | 123.0011 | 123.4451 | -123.6008 | -123.5733
416.3281 | 123.5916 | -61.7432 | 61.5555 | 0.0103 | 0.020589 | 0.020523 | -0.00039312 | 0.065256 | -0.0067911 | 0.069116 | -61.9492 | 61.6425 | -62.059 | -61.821 | 61.1755 | 0.068665 | -0.041199 | 0.068665 | 61.6653 | -61.9949 | -0.31586 | 0.086975 | -0.20599 | -0.07782 | -0.37994 | -0.25177 | 0.10986 | 0.10986 | 61.702 | 61.8118 | 122.9187 | 123.3856 | -0.20599 | 123.4085 | 61.8118 | -0.25177 | 123.3856 | -0.20599 | 61.8118 | 122.9187 | 123.4085 | -123.6145 | -123.5504
418.0781 | 123.587 | -61.7615 | 61.5417 | -0.0049592 | 0.019734 | 0.020736 | -0.00039312 | 0.065896 | -0.0048685 | 0.068902 | -61.94 | 61.6699 | -62.0407 | -61.8256 | 61.1572 | 0.073242 | 0.013733 | 0.086975 | 61.6379 | -61.9904 | -0.27923 | 0.12817 | -0.17853 | -0.064087 | -0.38452 | -0.22888 | 0.09613 | 0.10071 | 61.7752 | 61.8484 | 122.9187 | 123.4314 | -0.17853 | 123.3994 | 61.8347 | -0.22888 | 123.4314 | -0.17853 | 61.8347 | 122.9187 | 123.3994 | -123.5825 | -123.5321
419.8281 | 123.5779 | -61.7523 | 61.5326 | -0.0049592 | 0.01888 | 0.015182 | -0.0042383 | 0.064187 | -0.0042277 | 0.068048 | -61.9034 | 61.7157 | -61.9949 | -61.7935 | 61.2442 | 0.14648 | 0.1236 | 0.19226 | 61.6745 | -61.9812 | -0.24262 | 0.18311 | -0.15106 | -0.041199 | -0.28839 | -0.22888 | 0.14191 | 0.091553 | 61.8759 | 61.9446 | 122.9965 | 123.468 | -0.15106 | 123.4268 | 61.8988 | -0.22888 | 123.468 | -0.15106 | 61.8988 | 122.9965 | 123.4268 | -123.5275 | -123.5138
421.5 | 123.5825 | -61.7523 | 61.5555 | 0.0026703 | 0.020589 | 0.010269 | 0.00024788 | 0.065256 | -0.0057229 | 0.070184 | -61.9446 | 61.6333 | -62.0636 | -61.8118 | 61.171 | 0.086975 | 0 | 0.10529 | 61.6745 | -61.9629 | -0.31128 | 0.07782 | -0.19226 | -0.05951 | -0.38452 | -0.21057 | 0.11902 | 0.11902 | 61.7523 | 61.8576 | 122.9233 | 123.3856 | -0.19226 | 123.4268 | 61.8393 | -0.21057 | 123.3856 | -0.19226 | 61.8393 | 122.9233 | 123.4268 | -123.6191 | -123.5184
423.25 | 123.4497 | -61.7477 | 61.6013 | -0.012589 | 0.01888 | 0.017319 | -0.0029565 | 0.065683 | -0.0061503 | 0.070825 | -61.8256 | 61.6241 | -61.9675 | -61.7111 | 61.3037 | 0.20599 | -0.2243 | 0.21057 | 61.6287 | -61.9675 | -0.21973 | 0.022889 | -0.07782 | 0.036621 | -0.29755 | -0.21973 | 0.027466 | 0.14191 | 61.5234 | 61.9583 | 123.0515 | 123.3719 | -0.07782 | 123.3765 | 61.9537 | -0.21973 | 123.3719 | -0.07782 | 61.9537 | 123.0515 | 123.3765 | -123.5687 | -123.5687
425.0156 | 123.436 | -61.734 | 61.6241 | -0.012589 | 0.018453 | 0.012192 | -0.0053063 | 0.065896 | -0.0038003 | 0.070184 | -61.8118 | 61.6425 | -61.9904 | -61.702 | 61.2991 | 0.21973 | -0.21057 | 0.19684 | 61.6562 | -61.9308 | -0.25635 | 0.01831 | -0.07782 | 0.032044 | -0.32501 | -0.19684 | 0.032043 | 0.17853 | 61.5234 | 61.9308 | 123.0331 | 123.3765 | -0.07782 | 123.3902 | 61.9537 | -0.19684 | 123.3765 | -0.07782 | 61.9537 | 123.0331 | 123.3902 | -123.6145 | -123.555
426.7656 | 123.4497 | -61.7477 | 61.647 | -0.012589 | 0.021016 | 0.011764 | -0.0035973 | 0.065896 | -0.0055093 | 0.070611 | -61.7981 | 61.647 | -61.9583 | -61.6882 | 61.29 | 0.20142 | -0.21515 | 0.20142 | 61.6425 | -61.9492 | -0.21057 | 0 | -0.050354 | 0.05951 | -0.35706 | -0.20142 | -0.004578 | 0.16022 | 61.5326 | 61.9492 | 123.0377 | 123.3948 | -0.050354 | 123.3902 | 61.9492 | -0.20142 | 123.3948 | -0.050354 | 61.9492 | 123.0377 | 123.3902 | -123.6053 | -123.5962
428.4531 | 123.4909 | -61.734 | 61.6241 | -0.012589 | 0.018025 | 0.014114 | -0.0023157 | 0.064401 | -0.0035867 | 0.070611 | -61.8301 | 61.6653 | -61.9675 | -61.7065 | 61.2946 | 0.18768 | -0.13733 | 0.19226 | 61.6928 | -61.9171 | -0.23346 | 0.041198 | -0.09613 | 0.027466 | -0.32959 | -0.1831 | 0.068664 | 0.13733 | 61.5967 | 61.9263 | 123.0286 | 123.3994 | -0.09613 | 123.4268 | 61.9217 | -0.1831 | 123.3994 | -0.09613 | 61.9217 | 123.0286 | 123.4268 | -123.5916 | -123.5413
430.2188 | 123.4406 | -61.7752 | 61.6196 | -0.020218 | 0.019307 | 0.017959 | -0.00039312 | 0.065469 | -0.0072183 | 0.06762 | -61.821 | 61.6104 | -61.9995 | -61.6882 | 61.2717 | 0.20142 | -0.21057 | 0.19684 | 61.6196 | -61.9446 | -0.2243 | -0.009155 | -0.045776 | 0.086976 | -0.3479 | -0.16937 | 0 | 0.17853 | 61.5646 | 61.972 | 123.0469 | 123.3856 | -0.045776 | 123.3948 | 61.9766 | -0.16937 | 123.3856 | -0.045776 | 61.9766 | 123.0469 | 123.3948 | -123.6191 | -123.5641
431.9531 | 123.5184 | -61.7661 | 61.5417 | -0.0049592 | 0.019307 | 0.014328 | 0.0025977 | 0.064615 | -0.0057229 | 0.070611 | -61.8668 | 61.6425 | -62.0316 | -61.7386 | 61.2122 | 0.16937 | -0.018311 | 0.20599 | 61.6333 | -61.9812 | -0.2655 | 0.10071 | -0.10071 | 0.027466 | -0.32959 | -0.21515 | 0.091553 | 0.16479 | 61.7477 | 61.972 | 122.9782 | 123.4085 | -0.10071 | 123.3994 | 61.9354 | -0.21515 | 123.4085 | -0.10071 | 61.9354 | 122.9782 | 123.3994 | -123.5733 | -123.5229
433.625 | 123.436 | -61.734 | 61.6241 | 0.0026703 | 0.016744 | 0.012832 | -0.0057337 | 0.061197 | -0.0044413 | 0.068902 | -61.8301 | 61.6013 | -61.9904 | -61.702 | 61.2991 | 0.21515 | -0.17395 | 0.19226 | 61.6379 | -61.9171 | -0.25635 | -0.022889 | -0.09613 | 0.032044 | -0.32501 | -0.1831 | 0.013732 | 0.16022 | 61.5601 | 61.9263 | 123.0331 | 123.3353 | -0.09613 | 123.3719 | 61.9492 | -0.1831 | 123.3353 | -0.09613 | 61.9492 | 123.0331 | 123.3719 | -123.6145 | -123.5413
435.3594 | 123.468 | -61.7432 | 61.6379 | 0.0026703 | 0.017385 | 0.01326 | -0.0035973 | 0.064401 | -0.0014505 | 0.069543 | -61.8256 | 61.647 | -61.94 | -61.7203 | 61.2854 | 0.20142 | -0.13275 | 0.19226 | 61.6562 | -61.9354 | -0.19684 | 0.009156 | -0.082398 | 0.022888 | -0.35248 | -0.19226 | 0.018311 | 0.11444 | 61.6104 | 61.9354 | 123.0286 | 123.3902 | -0.082398 | 123.3994 | 61.9446 | -0.19226 | 123.3902 | -0.082398 | 61.9446 | 123.0286 | 123.3994 | -123.5779 | -123.5733
437.0938 | 123.4955 | -61.7157 | 61.6013 | -0.0049592 | 0.019734 | 0.011551 | -0.0029565 | 0.061197 | -0.0031595 | 0.069329 | -61.8301 | 61.6379 | -61.9583 | -61.6974 | 61.2808 | 0.18768 | -0.11902 | 0.17853 | 61.6608 | -61.9766 | -0.24261 | 0.036621 | -0.11444 | 0.01831 | -0.32043 | -0.26093 | 0.05951 | 0.12817 | 61.5967 | 61.8942 | 122.9965 | 123.3536 | -0.11444 | 123.3765 | 61.9034 | -0.26093 | 123.3536 | -0.11444 | 61.9034 | 122.9965 | 123.3765 | -123.5596 | -123.5779
438.8438 | 123.4085 | -61.734 | 61.6562 | -0.020218 | 0.01888 | 0.014969 | -0.0038111 | 0.060342 | -0.0046549 | 0.071466 | -61.7249 | 61.6699 | -61.9263 | -61.5738 | 61.3861 | 0.28381 | -0.11902 | 0.33417 | 61.6699 | -61.8942 | -0.19226 | 0.013733 | 0.009155 | 0.16022 | -0.27008 | -0.16022 | 0.013733 | 0.20142 | 61.615 | 62.0682 | 123.1201 | 123.4039 | 0.009155 | 123.4039 | 62.0178 | -0.16022 | 123.4039 | 0.009155 | 62.0178 | 123.1201 | 123.4039 | -123.5825 | -123.5504
440.5312 | 123.4131 | -61.734 | 61.6241 | 0.0103 | 0.019521 | 0.013046 | -0.0023157 | 0.064615 | -0.0050821 | 0.069116 | -61.7477 | 61.6837 | -61.9446 | -61.5875 | 61.3541 | 0.27924 | -0.10529 | 0.33417 | 61.647 | -61.8942 | -0.21057 | 0.059509 | -0.013733 | 0.14648 | -0.27008 | -0.16022 | 0.022888 | 0.19684 | 61.6287 | 62.0682 | 123.0881 | 123.4177 | -0.013733 | 123.381 | 62.0132 | -0.16022 | 123.4177 | -0.013733 | 62.0132 | 123.0881 | 123.381 | -123.5687 | -123.5184
442.2812 | 123.4131 | -61.702 | 61.6333 | 0.0026703 | 0.020803 | 0.011978 | -0.0038111 | 0.062265 | -0.0055093 | 0.070184 | -61.7294 | 61.6928 | -61.9125 | -61.5601 | 61.4044 | 0.27924 | -0.11902 | 0.33875 | 61.6745 | -61.8988 | -0.21057 | 0.059509 | -0.027466 | 0.14191 | -0.22888 | -0.19684 | 0.041199 | 0.18311 | 61.5829 | 62.0407 | 123.1064 | 123.3948 | -0.027466 | 123.3765 | 61.9812 | -0.19684 | 123.3948 | -0.027466 | 61.9812 | 123.1064 | 123.3765 | -123.5458 | -123.5321
444.0312 | 123.4085 | -61.7157 | 61.6425 | -0.0049592 | 0.019094 | 0.015823 | -0.0038111 | 0.062692 | -0.0061503 | 0.067407 | -61.7203 | 61.6699 | -61.9446 | -61.5738 | 61.377 | 0.29297 | -0.11902 | 0.32501 | 61.6882 | -61.8759 | -0.22888 | 0.027466 | -0.004578 | 0.14191 | -0.2655 | -0.16022 | 0.045776 | 0.2243 | 61.5967 | 62.0407 | 123.0927 | 123.3856 | -0.004578 | 123.4039 | 62.0087 | -0.16022 | 123.3856 | -0.004578 | 62.0087 | 123.0927 | 123.4039 | -123.587 | -123.5184
445.7812 | 123.5504 | -61.6974 | 61.5784 | -0.0049592 | 0.020375 | 0.011764 | 0.0036657 | 0.06376 | -0.0061503 | 0.068688 | -61.8942 | 61.647 | -62.0132 | -61.7569 | 61.1938 | 0.07782 | -0.036621 | 0.07782 | 61.6791 | -61.9629 | -0.31586 | 0.068665 | -0.19684 | -0.059509 | -0.38452 | -0.2655 | 0.10071 | 0.11902 | 61.6608 | 61.7752 | 122.8912 | 123.3444 | -0.19684 | 123.3765 | 61.7752 | -0.2655 | 123.3444 | -0.19684 | 61.7752 | 122.8912 | 123.3765 | -123.5916 | -123.5413
447.4531 | 123.4406 | -61.6745 | 61.6653 | -0.0049592 | 0.018025 | 0.013687 | -0.0053063 | 0.061838 | -0.0038003 | 0.06997 | -61.7798 | 61.6745 | -61.9263 | -61.6425 | 61.2991 | 0.17853 | -0.14191 | 0.18768 | 61.6699 | -61.8896 | -0.25177 | 0.009156 | -0.10528 | 0.032044 | -0.36621 | -0.21515 | 0.004578 | 0.14649 | 61.5326 | 61.8622 | 122.9736 | 123.349 | -0.10528 | 123.3444 | 61.853 | -0.21515 | 123.349 | -0.10528 | 61.853 | 122.9736 | 123.3444 | -123.5916 | -123.555
449.125 | 123.4863 | -61.702 | 61.5784 | 0.0026703 | 0.019521 | 0.012619 | 0.0011023 | 0.063333 | -0.0074319 | 0.070611 | -61.7981 | 61.6745 | -61.9904 | -61.6562 | 61.2854 | 0.17853 | -0.009155 | 0.21973 | 61.6974 | -61.8942 | -0.28839 | 0.096131 | -0.096131 | 0.045776 | -0.29297 | -0.19226 | 0.11902 | 0.19226 | 61.6928 | 61.9217 | 122.9874 | 123.3765 | -0.096131 | 123.3994 | 61.8805 | -0.19226 | 123.3765 | -0.096131 | 61.8805 | 122.9874 | 123.3994 | -123.5687 | -123.4726
450.875 | 123.4222 | -61.7203 | 61.6104 | -0.020218 | 0.01888 | 0.013046 | -0.0035973 | 0.062265 | -0.0025187 | 0.069116 | -61.7294 | 61.6653 | -61.8896 | -61.5738 | 61.3724 | 0.30212 | -0.10529 | 0.32501 | 61.6745 | -61.9217 | -0.16937 | 0.054931 | -0.009155 | 0.14648 | -0.23804 | -0.20142 | 0.064087 | 0.16022 | 61.615 | 62.0453 | 123.0927 | 123.3856 | -0.009155 | 123.3948 | 62.0224 | -0.20142 | 123.3856 | -0.009155 | 62.0224 | 123.0927 | 123.3948 | -123.5001 | -123.5321
452.6094 | 123.5138 | -61.7065 | 61.5601 | -0.0049592 | 0.022725 | 0.011337 | -0.00060672 | 0.063547 | -0.0046549 | 0.069329 | -61.8301 | 61.7294 | -61.972 | -61.7065 | 61.2442 | 0.14648 | 0.064087 | 0.20599 | 61.7065 | -61.9308 | -0.2655 | 0.16937 | -0.1236 | 0 | -0.31586 | -0.2243 | 0.14648 | 0.14191 | 61.7706 | 61.9125 | 122.9507 | 123.436 | -0.1236 | 123.4131 | 61.853 | -0.2243 | 123.436 | -0.1236 | 61.853 | 122.9507 | 123.4131 | -123.5321 | -123.4909
454.3438 | 123.4772 | -61.734 | 61.5738 | -0.0049592 | 0.018239 | 0.014969 | 0.00024788 | 0.065469 | -0.0052957 | 0.068688 | -61.8256 | 61.6333 | -62.0132 | -61.6837 | 61.2579 | 0.16937 | -0.022888 | 0.22888 | 61.6837 | -61.9354 | -0.27924 | 0.059509 | -0.091553 | 0.050354 | -0.31586 | -0.20142 | 0.10986 | 0.18768 | 61.7111 | 61.9629 | 122.9919 | 123.3673 | -0.091553 | 123.4177 | 61.9034 | -0.20142 | 123.3673 | -0.091553 | 61.9034 | 122.9919 | 123.4177 | -123.587 | -123.5092
456.0938 | 123.5458 | -61.7065 | 61.5646 | 0.0026703 | 0.019521 | 0.014541 | -0.00039312 | 0.065256 | -0.0057229 | 0.069543 | -61.8759 | 61.6241 | -62.0178 | -61.734 | 61.1984 | 0.073242 | -0.009155 | 0.11902 | 61.647 | -61.9492 | -0.31128 | 0.05951 | -0.16937 | -0.027466 | -0.36621 | -0.24261 | 0.082398 | 0.14191 | 61.6974 | 61.8256 | 122.905 | 123.3307 | -0.16937 | 123.3536 | 61.7798 | -0.24261 | 123.3307 | -0.16937 | 61.7798 | 122.905 | 123.3536 | -123.5825 | -123.5138
457.8438 | 123.5229 | -61.6974 | 61.5967 | -0.0049592 | 0.019094 | 0.015182 | -0.0031701 | 0.065256 | -0.0057229 | 0.072747 | -61.8713 | 61.6745 | -61.9858 | -61.7523 | 61.2167 | 0.09613 | -0.091553 | 0.082397 | 61.6653 | -61.94 | -0.28839 | 0.07782 | -0.17395 | -0.054931 | -0.37994 | -0.24261 | 0.068664 | 0.11444 | 61.6058 | 61.7798 | 122.9141 | 123.3719 | -0.17395 | 123.3627 | 61.7935 | -0.24261 | 123.3719 | -0.17395 | 61.7935 | 122.9141 | 123.3627 | -123.5825 | -123.5367
459.5312 | 123.4451 | -61.6379 | 61.6425 | 0.0026703 | 0.017171 | 0.012619 | -0.0076563 | 0.062906 | -0.0020913 | 0.06997 | -61.7844 | 61.6837 | -61.8988 | -61.6516 | 61.3266 | 0.20599 | -0.11902 | 0.18768 | 61.7111 | -61.8851 | -0.26093 | 0.041199 | -0.14648 | -0.013733 | -0.31586 | -0.24719 | 0.068665 | 0.11444 | 61.5189 | 61.8256 | 122.9645 | 123.3215 | -0.14648 | 123.349 | 61.8439 | -0.24719 | 123.3215 | -0.14648 | 61.8439 | 122.9645 | 123.349 | -123.5413 | -123.5275
461.2812 | 123.4177 | -61.6379 | 61.6333 | -0.012589 | 0.019094 | 0.01326 | -0.0016747 | 0.064187 | -0.0078591 | 0.070611 | -61.7661 | 61.6791 | -61.9125 | -61.6058 | 61.3403 | 0.20142 | -0.20599 | 0.20599 | 61.6837 | -61.8576 | -0.27466 | 0.045776 | -0.12817 | 0.032043 | -0.29297 | -0.21973 | 0.050354 | 0.14648 | 61.4319 | 61.8439 | 122.9782 | 123.317 | -0.12817 | 123.3215 | 61.8393 | -0.21973 | 123.317 | -0.12817 | 61.8393 | 122.9782 | 123.3215 | -123.5458 | -123.4909
463.0312 | 123.5184 | -61.6974 | 61.5601 | 0.0026703 | 0.020375 | 0.013473 | -0.00082032 | 0.064401 | -0.0046549 | 0.069543 | -61.8439 | 61.702 | -61.9629 | -61.7249 | 61.2122 | 0.15106 | 0.09613 | 0.19684 | 61.6837 | -61.9583 | -0.2655 | 0.14191 | -0.14648 | -0.027466 | -0.3479 | -0.26093 | 0.1236 | 0.11902 | 61.7935 | 61.8942 | 122.9095 | 123.3994 | -0.14648 | 123.381 | 61.8484 | -0.26093 | 123.3994 | -0.14648 | 61.8484 | 122.9095 | 123.381 | -123.523 | -123.5184
464.7812 | 123.4863 | -61.702 | 61.5784 | 0.0026703 | 0.022084 | 0.013046 | 0.0013159 | 0.063974 | -0.0048685 | 0.071038 | -61.8622 | 61.6425 | -61.9766 | -61.7249 | 61.2305 | 0.14191 | -0.14191 | 0.13275 | 61.6379 | -61.9354 | -0.27466 | 0.064087 | -0.16022 | -0.022889 | -0.3479 | -0.23346 | 0.059509 | 0.11444 | 61.5601 | 61.8347 | 122.9324 | 123.3444 | -0.16022 | 123.3398 | 61.8439 | -0.23346 | 123.3444 | -0.16022 | 61.8439 | 122.9324 | 123.3398 | -123.555 | -123.5138
466.4531 | 123.5504 | -61.6516 | 61.5692 | -0.0049592 | 0.01888 | 0.014969 | 3.4284e-05 | 0.064401 | -0.0050821 | 0.069757 | -61.8851 | 61.6745 | -61.9812 | -61.7477 | 61.1893 | 0.073242 | -0.027466 | 0.07782 | 61.6837 | -61.9171 | -0.32959 | 0.10529 | -0.23346 | -0.096131 | -0.37994 | -0.2655 | 0.11444 | 0.09613 | 61.6241 | 61.7294 | 122.8409 | 123.3261 | -0.23346 | 123.3353 | 61.7249 | -0.2655 | 123.3261 | -0.23346 | 61.7249 | 122.8409 | 123.3353 | -123.5504 | -123.4863
468.1875 | 123.3856 | -61.6928 | 61.6287 | 0.0026703 | 0.019307 | 0.013901 | -0.0042383 | 0.064187 | -0.0046549 | 0.070184 | -61.7569 | 61.5967 | -61.9308 | -61.6333 | 61.3174 | 0.21057 | -0.23804 | 0.21057 | 61.615 | -61.9034 | -0.23804 | -0.032043 | -0.064087 | 0.059509 | -0.31128 | -0.21057 | -0.013733 | 0.17395 | 61.4548 | 61.9034 | 123.0103 | 123.2895 | -0.064087 | 123.3078 | 61.9034 | -0.21057 | 123.2895 | -0.064087 | 61.9034 | 123.0103 | 123.3078 | -123.5596 | -123.5321
469.9375 | 123.3994 | -61.6882 | 61.6379 | -0.0049592 | 0.018666 | 0.017532 | -0.0010339 | 0.063547 | -0.0046549 | 0.069329 | -61.7706 | 61.6013 | -61.908 | -61.6379 | 61.2991 | 0.21057 | -0.20599 | 0.19684 | 61.6379 | -61.8896 | -0.21973 | -0.036621 | -0.082398 | 0.050354 | -0.33875 | -0.20142 | 0 | 0.13733 | 61.4822 | 61.8851 | 122.9874 | 123.2895 | -0.082398 | 123.3261 | 61.8988 | -0.20142 | 123.2895 | -0.082398 | 61.8988 | 122.9874 | 123.3261 | -123.5458 | -123.5275
471.6094 | 123.5184 | -61.6653 | 61.5738 | -0.0049592 | 0.021657 | 0.012619 | 0.0011023 | 0.064401 | -0.0074319 | 0.069329 | -61.8301 | 61.6653 | -61.9812 | -61.6928 | 61.2305 | 0.10071 | 0 | 0.10986 | 61.7111 | -61.9171 | -0.31586 | 0.091552 | -0.1648 | -0.027466 | -0.34332 | -0.25177 | 0.13733 | 0.15106 | 61.6653 | 61.7752 | 122.8958 | 123.3307 | -0.1648 | 123.3765 | 61.7661 | -0.25177 | 123.3307 | -0.1648 | 61.7661 | 122.8958 | 123.3765 | -123.555 | -123.4909
473.375 | 123.3948 | -61.6425 | 61.6699 | 0.0026703 | 0.018453 | 0.012832 | -0.00082032 | 0.064615 | -0.0055093 | 0.068688 | -61.7157 | 61.6608 | -61.8942 | -61.5967 | 61.3403 | 0.20142 | -0.21515 | 0.18768 | 61.6837 | -61.8393 | -0.25177 | -0.009155 | -0.073242 | 0.045776 | -0.32959 | -0.19684 | 0.013733 | 0.17853 | 61.4273 | 61.8301 | 122.9828 | 123.3032 | -0.073242 | 123.3261 | 61.8439 | -0.19684 | 123.3032 | -0.073242 | 61.8439 | 122.9828 | 123.3261 | -123.5641 | -123.5092
475.0625 | 123.5001 | -61.6013 | 61.6104 | 0.0026703 | 0.018453 | 0.016678 | -0.0010339 | 0.063974 | -0.0061503 | 0.069757 | -61.7569 | 61.7523 | -61.8713 | -61.6425 | 61.2946 | 0.15564 | 0.082397 | 0.20599 | 61.7752 | -61.8256 | -0.27008 | 0.14191 | -0.15564 | -0.041199 | -0.31586 | -0.22431 | 0.16479 | 0.11444 | 61.6837 | 61.8073 | 122.8958 | 123.3536 | -0.15564 | 123.3765 | 61.7569 | -0.22431 | 123.3536 | -0.15564 | 61.7569 | 122.8958 | 123.3765 | -123.4818 | -123.436
476.8125 | 123.4497 | -61.5921 | 61.7065 | -0.0049592 | 0.020375 | 0.014541 | -0.0018885 | 0.063333 | -0.0031595 | 0.071252 | -61.7157 | 61.7294 | -61.8668 | -61.5875 | 61.3586 | 0.16479 | -0.16937 | 0.17853 | 61.7157 | -61.8118 | -0.27466 | 0.022888 | -0.1236 | 0.004578 | -0.3479 | -0.21973 | 0.009155 | 0.15106 | 61.4227 | 61.7706 | 122.9507 | 123.3215 | -0.1236 | 123.3078 | 61.7569 | -0.21973 | 123.3215 | -0.1236 | 61.7569 | 122.9507 | 123.3078 | -123.5733 | -123.5184
478.5625 | 123.436 | -61.647 | 61.6562 | -0.0049592 | 0.017171 | 0.013901 | -0.0072289 | 0.065042 | -0.0031595 | 0.068902 | -61.7477 | 61.6928 | -61.8713 | -61.6425 | 61.3083 | 0.18768 | -0.11902 | 0.17853 | 61.7111 | -61.8484 | -0.2243 | 0.036621 | -0.10071 | 0.004578 | -0.3479 | -0.20142 | 0.054932 | 0.1236 | 61.528 | 61.8256 | 122.9553 | 123.3398 | -0.10071 | 123.3582 | 61.8347 | -0.20142 | 123.3398 | -0.10071 | 61.8347 | 122.9553 | 123.3582 | -123.5275 | -123.5046
480.2656 | 123.3765 | -61.5921 | 61.7249 | -0.0049592 | 0.021871 | 0.014755 | -0.0025293 | 0.064615 | -0.0052957 | 0.069757 | -61.6562 | 61.7065 | -61.8073 | -61.5417 | 61.3861 | 0.21973 | -0.21057 | 0.20599 | 61.7386 | -61.7844 | -0.21515 | -0.018311 | -0.064087 | 0.050354 | -0.33875 | -0.19226 | 0.013732 | 0.15106 | 61.3815 | 61.7981 | 122.9782 | 123.2986 | -0.064087 | 123.3307 | 61.8118 | -0.19226 | 123.2986 | -0.064087 | 61.8118 | 122.9782 | 123.3307 | -123.5321 | -123.5092
482.0312 | 123.381 | -61.5738 | 61.7203 | 0.0026703 | 0.018453 | 0.014114 | -0.0038111 | 0.063547 | -0.0046549 | 0.068902 | -61.615 | 61.7935 | -61.7569 | -61.4548 | 61.4639 | 0.28839 | -0.091553 | 0.34332 | 61.7615 | -61.7615 | -0.18311 | 0.073242 | -0.041198 | 0.11902 | -0.25635 | -0.18768 | 0.041199 | 0.14191 | 61.4822 | 61.9171 | 123.0377 | 123.3673 | -0.041198 | 123.3353 | 61.8622 | -0.18768 | 123.3673 | -0.041198 | 61.8622 | 123.0377 | 123.3353 | -123.4772 | -123.4818
483.7812 | 123.4451 | -61.615 | 61.6104 | -0.0049592 | 0.020162 | 0.018173 | 0.0013159 | 0.06376 | -0.0052957 | 0.070825 | -61.7294 | 61.6974 | -61.8988 | -61.5738 | 61.3129 | 0.17853 | -0.018311 | 0.2243 | 61.734 | -61.8256 | -0.28381 | 0.086975 | -0.11444 | 0.041198 | -0.29755 | -0.21057 | 0.1236 | 0.16937 | 61.5967 | 61.8393 | 122.9279 | 123.3124 | -0.11444 | 123.349 | 61.7935 | -0.21057 | 123.3124 | -0.11444 | 61.7935 | 122.9279 | 123.349 | -123.5092 | -123.436
485.4688 | 123.4222 | -61.5784 | 61.6928 | -0.012589 | 0.020162 | 0.0096279 | -0.0061609 | 0.061838 | -0.0046549 | 0.069116 | -61.7065 | 61.7477 | -61.8164 | -61.5738 | 61.3495 | 0.17853 | -0.10986 | 0.18768 | 61.7203 | -61.8301 | -0.23804 | 0.054932 | -0.12817 | 0.004577 | -0.34332 | -0.25177 | 0.027466 | 0.10986 | 61.4685 | 61.7661 | 122.9279 | 123.3261 | -0.12817 | 123.2986 | 61.7569 | -0.25177 | 123.3261 | -0.12817 | 61.7569 | 122.9279 | 123.2986 | -123.5092 | -123.5229
487.2344 | 123.4222 | -61.6379 | 61.6287 | -0.0049592 | 0.020375 | 0.014541 | 0.00024788 | 0.064187 | -0.0059365 | 0.06997 | -61.7432 | 61.7294 | -61.8896 | -61.5829 | 61.3129 | 0.18768 | -0.018311 | 0.2243 | 61.7065 | -61.8896 | -0.25177 | 0.10071 | -0.10529 | 0.054931 | -0.31586 | -0.25177 | 0.07782 | 0.14648 | 61.6196 | 61.8622 | 122.9507 | 123.3673 | -0.10529 | 123.3444 | 61.8256 | -0.25177 | 123.3673 | -0.10529 | 61.8256 | 122.9507 | 123.3444 | -123.5184 | -123.5184
488.9219 | 123.349 | -61.6379 | 61.6333 | -0.0049592 | 0.019307 | 0.0186 | -0.0046655 | 0.061624 | -0.0044413 | 0.068902 | -61.6653 | 61.6882 | -61.8301 | -61.5189 | 61.3907 | 0.27466 | -0.10071 | 0.33417 | 61.6882 | -61.821 | -0.19226 | 0.054931 | -0.027466 | 0.11902 | -0.24262 | -0.18311 | 0.054931 | 0.1648 | 61.5372 | 61.972 | 123.0286 | 123.3261 | -0.027466 | 123.3261 | 61.9125 | -0.18311 | 123.3261 | -0.027466 | 61.9125 | 123.0286 | 123.3261 | -123.4634 | -123.4543
490.6094 | 123.4222 | -61.6013 | 61.6837 | -0.0049592 | 0.018666 | 0.014541 | -0.0057337 | 0.060983 | -0.0052957 | 0.068688 | -61.6882 | 61.7294 | -61.8256 | -61.5463 | 61.3724 | 0.19226 | -0.13733 | 0.19226 | 61.734 | -61.8073 | -0.22431 | 0.045776 | -0.086975 | 0.054931 | -0.31128 | -0.20599 | 0.050354 | 0.13733 | 61.4639 | 61.7935 | 122.9736 | 123.3307 | -0.086975 | 123.3353 | 61.7935 | -0.20599 | 123.3307 | -0.086975 | 61.7935 | 122.9736 | 123.3353 | -123.5092 | -123.4909
492.3594 | 123.4451 | -61.5875 | 61.6379 | 0.0026703 | 0.019948 | 0.011337 | 0.0025977 | 0.059701 | -0.0057229 | 0.070397 | -61.7294 | 61.7294 | -61.8942 | -61.615 | 61.2808 | 0.13275 | -0.032043 | 0.16479 | 61.7157 | -61.8484 | -0.3067 | 0.091553 | -0.14191 | -0.027466 | -0.35706 | -0.26093 | 0.07782 | 0.1648 | 61.5555 | 61.7523 | 122.8683 | 123.317 | -0.14191 | 123.3032 | 61.7203 | -0.26093 | 123.317 | -0.14191 | 61.7203 | 122.8683 | 123.3032 | -123.5321 | -123.4863
494.0938 | 123.3902 | -61.5509 | 61.7661 | -0.0049592 | 0.01888 | 0.0094143 | -0.0038111 | 0.062692 | -0.0067911 | 0.070825 | -61.6287 | 61.7432 | -61.8027 | -61.5143 | 61.4044 | 0.21515 | -0.20142 | 0.19684 | 61.7615 | -61.7477 | -0.25177 | -0.022888 | -0.07782 | 0.036621 | -0.36163 | -0.19684 | -0.004577 | 0.17395 | 61.3495 | 61.7477 | 122.9553 | 123.2941 | -0.07782 | 123.3124 | 61.7661 | -0.19684 | 123.2941 | -0.07782 | 61.7661 | 122.9553 | 123.3124 | -123.5687 | -123.5138
495.8438 | 123.4589 | -61.441 | 61.8027 | -0.0049592 | 0.019734 | 0.013687 | -0.00017952 | 0.063119 | -0.0063639 | 0.069757 | -61.647 | 61.8164 | -61.7386 | -61.5051 | 61.4044 | 0.13733 | -0.13275 | 0.13275 | 61.853 | -61.6837 | -0.29755 | 0.013733 | -0.20599 | -0.064087 | -0.39825 | -0.24262 | 0.050354 | 0.091552 | 61.3083 | 61.5738 | 122.8455 | 123.2574 | -0.20599 | 123.2941 | 61.5784 | -0.24262 | 123.2574 | -0.20599 | 61.5784 | 122.8455 | 123.2941 | -123.5413 | -123.4863
497.5312 | 123.4085 | -61.4639 | 61.8118 | -0.0049592 | 0.018239 | 0.011337 | -0.0055199 | 0.061624 | -0.0052957 | 0.069329 | -61.5738 | 61.8393 | -61.702 | -61.4502 | 61.4731 | 0.21057 | -0.12817 | 0.18768 | 61.8576 | -61.6653 | -0.23804 | 0.027465 | -0.10986 | 0.013733 | -0.33875 | -0.20142 | 0.045776 | 0.12817 | 61.3358 | 61.6516 | 122.937 | 123.3032 | -0.10986 | 123.3215 | 61.6745 | -0.20142 | 123.3032 | -0.10986 | 61.6745 | 122.937 | 123.3215 | -123.5138 | -123.4772
499.2188 | 123.4543 | -61.4914 | 61.7157 | -0.0049592 | 0.019521 | 0.012405 | -0.00039312 | 0.065683 | -0.0076455 | 0.069116 | -61.6104 | 61.8347 | -61.7798 | -61.4822 | 61.409 | 0.17853 | 0.009155 | 0.21515 | 61.8484 | -61.7157 | -0.28839 | 0.11902 | -0.11902 | 0.009155 | -0.3067 | -0.2243 | 0.13275 | 0.16937 | 61.5005 | 61.7065 | 122.9004 | 123.3261 | -0.11902 | 123.3398 | 61.6699 | -0.2243 | 123.3261 | -0.11902 | 61.6699 | 122.9004 | 123.3398 | -123.4955 | -123.4314
500.9844 | 123.4634 | -61.5555 | 61.6333 | 0.0026703 | 0.019307 | 0.015182 | -0.0044519 | 0.063119 | -0.0067911 | 0.069116 | -61.7249 | 61.7523 | -61.8576 | -61.5921 | 61.3083 | 0.14648 | 0.10529 | 0.21515 | 61.7981 | -61.8073 | -0.30212 | 0.11902 | -0.16937 | -0.036621 | -0.32501 | -0.25177 | 0.16479 | 0.13275 | 61.6608 | 61.7706 | 122.8638 | 123.3078 | -0.16937 | 123.3536 | 61.702 | -0.25177 | 123.3078 | -0.16937 | 61.702 | 122.8638 | 123.3536 | -123.4909 | -123.4406
502.6562 | 123.4543 | -61.5921 | 61.6333 | 0.0026703 | 0.019948 | 0.014755 | -0.0012475 | 0.062051 | -0.0055093 | 0.069543 | -61.7477 | 61.6791 | -61.8851 | -61.6425 | 61.2717 | 0.10986 | -0.11902 | 0.09613 | 61.7065 | -61.8256 | -0.29297 | 0.045776 | -0.15564 | -0.050354 | -0.36163 | -0.23346 | 0.073242 | 0.13733 | 61.4731 | 61.6882 | 122.8638 | 123.2712 | -0.15564 | 123.2986 | 61.702 | -0.23346 | 123.2712 | -0.15564 | 61.702 | 122.8638 | 123.2986 | -123.5184 | -123.4589
504.4062 | 123.4268 | -61.6013 | 61.615 | -0.0049592 | 0.017171 | 0.012832 | -0.00017952 | 0.062692 | -0.0050821 | 0.06997 | -61.7157 | 61.7111 | -61.8439 | -61.6013 | 61.2762 | 0.13733 | -0.022888 | 0.17395 | 61.7111 | -61.8484 | -0.24262 | 0.096131 | -0.11444 | 0 | -0.33874 | -0.24719 | 0.096131 | 0.12817 | 61.5784 | 61.7752 | 122.8775 | 123.3124 | -0.11444 | 123.3124 | 61.7386 | -0.24719 | 123.3124 | -0.11444 | 61.7386 | 122.8775 | 123.3124 | -123.4589 | -123.4634
506.0938 | 123.4634 | -61.5097 | 61.6974 | -0.0049592 | 0.018666 | 0.012619 | -0.0012475 | 0.065683 | -0.0055093 | 0.069543 | -61.702 | 61.7752 | -61.8439 | -61.6013 | 61.2991 | 0.091553 | -0.064087 | 0.09613 | 61.8118 | -61.7615 | -0.33417 | 0.07782 | -0.19226 | -0.091552 | -0.39825 | -0.25177 | 0.11444 | 0.14191 | 61.4456 | 61.6058 | 122.8088 | 123.2849 | -0.19226 | 123.3215 | 61.6013 | -0.25177 | 123.2849 | -0.19226 | 61.6013 | 122.8088 | 123.3215 | -123.5413 | -123.4589
507.8281 | 123.4589 | -61.5005 | 61.6791 | -0.012589 | 0.019948 | 0.014755 | -0.0031701 | 0.063547 | -0.0040139 | 0.071466 | -61.6928 | 61.7981 | -61.8118 | -61.5692 | 61.3312 | 0.086975 | -0.036621 | 0.082397 | 61.8118 | -61.7615 | -0.31128 | 0.11902 | -0.19226 | -0.068665 | -0.3479 | -0.26093 | 0.13275 | 0.11902 | 61.4639 | 61.5829 | 122.8317 | 123.2986 | -0.19226 | 123.3124 | 61.5875 | -0.26093 | 123.2986 | -0.19226 | 61.5875 | 122.8317 | 123.3124 | -123.4909 | -123.4406
509.5625 | 123.3398 | -61.4502 | 61.8164 | -0.0049592 | 0.018666 | 0.014755 | -0.0038111 | 0.063547 | -0.0050821 | 0.068902 | -61.5143 | 61.8301 | -61.6974 | -61.3998 | 61.496 | 0.20142 | -0.25177 | 0.16937 | 61.8393 | -61.647 | -0.24719 | 0.013733 | -0.064087 | 0.050354 | -0.32043 | -0.19684 | 0.022888 | 0.18311 | 61.1984 | 61.6196 | 122.9462 | 123.2803 | -0.064087 | 123.2895 | 61.6516 | -0.19684 | 123.2803 | -0.064087 | 61.6516 | 122.9462 | 123.2895 | -123.5138 | -123.4634
511.3281 | 123.4131 | -61.3449 | 61.8851 | -0.012589 | 0.021016 | 0.01326 | -0.0010339 | 0.063333 | -0.0052957 | 0.069543 | -61.4594 | 61.9354 | -61.5967 | -61.3449 | 61.5417 | 0.17395 | -0.17395 | 0.16022 | 61.9629 | -61.5829 | -0.25177 | 0.050354 | -0.11444 | 0 | -0.34332 | -0.23804 | 0.07782 | 0.13733 | 61.171 | 61.5051 | 122.8867 | 123.2803 | -0.11444 | 123.3078 | 61.5189 | -0.23804 | 123.2803 | -0.11444 | 61.5189 | 122.8867 | 123.3078 | -123.4818 | -123.468
513.0781 | 123.4909 | -61.2671 | 61.9171 | -0.0049592 | 0.020803 | 0.019455 | 0.0013159 | 0.063547 | -0.0055093 | 0.069543 | -61.4822 | 62.0224 | -61.5738 | -61.3586 | 61.5326 | 0.10529 | -0.022888 | 0.091553 | 62.0316 | -61.528 | -0.3067 | 0.10529 | -0.21515 | -0.091553 | -0.38452 | -0.26093 | 0.11444 | 0.091553 | 61.2442 | 61.3586 | 122.7997 | 123.2895 | -0.21515 | 123.2986 | 61.3724 | -0.26093 | 123.2895 | -0.21515 | 61.3724 | 122.7997 | 123.2986 | -123.4909 | -123.4451
514.8281 | 123.3856 | -61.2671 | 61.972 | -0.0049592 | 0.020375 | 0.015396 | -0.0072289 | 0.060769 | -0.0038003 | 0.069329 | -61.3953 | 62.0178 | -61.496 | -61.2717 | 61.6516 | 0.21515 | -0.10986 | 0.20599 | 62.0178 | -61.5005 | -0.22888 | 0.045776 | -0.12817 | -0.004577 | -0.32043 | -0.23346 | 0.045776 | 0.10071 | 61.1572 | 61.4731 | 122.9187 | 123.2849 | -0.12817 | 123.2849 | 61.4822 | -0.23346 | 123.2849 | -0.12817 | 61.4822 | 122.9187 | 123.2849 | -123.468 | -123.4726
516.5312 | 123.3627 | -61.3266 | 61.9263 | -0.0049592 | 0.018666 | 0.014755 | -0.0050927 | 0.064615 | -0.0025187 | 0.069116 | -61.4319 | 61.9629 | -61.5875 | -61.2946 | 61.5738 | 0.20599 | -0.18768 | 0.19684 | 61.94 | -61.5555 | -0.26093 | 0.036621 | -0.10529 | 0.032043 | -0.35248 | -0.22888 | 0.013732 | 0.15564 | 61.1389 | 61.5234 | 122.9004 | 123.2895 | -0.10529 | 123.2666 | 61.5326 | -0.22888 | 123.2895 | -0.10529 | 61.5326 | 122.9004 | 123.2666 | -123.5138 | -123.4818
518.2812 | 123.3261 | -61.3541 | 61.8805 | 0.0026703 | 0.016317 | 0.01625 | -0.0023157 | 0.060983 | -0.0057229 | 0.069757 | -61.3815 | 61.9034 | -61.5601 | -61.2396 | 61.6287 | 0.28839 | -0.086975 | 0.32044 | 61.9354 | -61.5509 | -0.20599 | 0.022888 | -0.027466 | 0.11444 | -0.25177 | -0.19684 | 0.054932 | 0.17853 | 61.2671 | 61.6745 | 122.9828 | 123.2574 | -0.027466 | 123.2895 | 61.6425 | -0.19684 | 123.2574 | -0.027466 | 61.6425 | 122.9828 | 123.2895 | -123.4406 | -123.4314
520.0312 | 123.4543 | -61.3403 | 61.8393 | 0.0026703 | 0.021016 | 0.014114 | 0.0019569 | 0.06376 | -0.0044413 | 0.06997 | -61.5189 | 61.94 | -61.6379 | -61.3953 | 61.4731 | 0.086975 | -0.050354 | 0.086975 | 61.9766 | -61.5784 | -0.29755 | 0.10071 | -0.17853 | -0.054932 | -0.36621 | -0.23804 | 0.13733 | 0.11902 | 61.29 | 61.4273 | 122.8134 | 123.2803 | -0.17853 | 123.317 | 61.4273 | -0.23804 | 123.2803 | -0.17853 | 61.4273 | 122.8134 | 123.317 | -123.4772 | -123.4177
521.7188 | 123.4451 | -61.4868 | 61.6882 | 0.0103 | 0.020803 | 0.016037 | 0.0015295 | 0.062692 | -0.0074319 | 0.071252 | -61.6745 | 61.7569 | -61.7981 | -61.5601 | 61.3129 | -0.10986 | -0.19684 | -0.059509 | 61.7935 | -61.7249 | -0.31128 | 0.068665 | -0.18768 | -0.073243 | -0.37537 | -0.23804 | 0.10529 | 0.1236 | 61.29 | 61.4273 | 122.7997 | 123.2437 | -0.18768 | 123.2803 | 61.377 | -0.23804 | 123.2437 | -0.18768 | 61.377 | 122.7997 | 123.2803 | -123.4863 | -123.4131
523.4531 | 123.3215 | -61.2671 | 61.9812 | -0.0049592 | 0.019734 | 0.014969 | -0.0031701 | 0.063333 | -0.0061503 | 0.070397 | -61.3312 | 61.9766 | -61.5372 | -61.2213 | 61.6699 | 0.21057 | -0.24719 | 0.21057 | 61.9675 | -61.5051 | -0.27008 | -0.004577 | -0.064087 | 0.045777 | -0.31128 | -0.23804 | -0.013733 | 0.20599 | 61.0199 | 61.4777 | 122.937 | 123.2437 | -0.064087 | 123.2346 | 61.4777 | -0.23804 | 123.2437 | -0.064087 | 61.4777 | 122.937 | 123.2346 | -123.5184 | -123.4863
525.2031 | 123.4131 | -61.1938 | 61.9675 | 0.0103 | 0.019094 | 0.017532 | -0.00082032 | 0.063333 | -0.0061503 | 0.068688 | -61.322 | 62.1277 | -61.4594 | -61.1664 | 61.7065 | 0.16937 | 0.064087 | 0.2243 | 62.1185 | -61.4319 | -0.2655 | 0.16022 | -0.12817 | 0.027466 | -0.26092 | -0.23804 | 0.15106 | 0.13733 | 61.2579 | 61.4182 | 122.9004 | 123.3215 | -0.12817 | 123.3124 | 61.3632 | -0.23804 | 123.3215 | -0.12817 | 61.3632 | 122.9004 | 123.3124 | -123.4268 | -123.3994
526.9688 | 123.3215 | -61.2991 | 61.9583 | -0.0049592 | 0.019521 | 0.012405 | -0.0053063 | 0.061838 | -0.0044413 | 0.06997 | -61.3495 | 61.9904 | -61.5051 | -61.2213 | 61.6745 | 0.28839 | -0.11902 | 0.33417 | 61.9537 | -61.5234 | -0.20599 | 0.032043 | -0.050354 | 0.07782 | -0.28381 | -0.2243 | -0.004578 | 0.15564 | 61.1801 | 61.6333 | 122.9736 | 123.2895 | -0.050354 | 123.2529 | 61.5875 | -0.2243 | 123.2895 | -0.050354 | 61.5875 | 122.9736 | 123.2529 | -123.4634 | -123.4818
528.6406 | 123.3307 | -61.2396 | 61.9766 | -0.0049592 | 0.01653 | 0.01625 | -0.0044519 | 0.062265 | -0.0042277 | 0.068902 | -61.2946 | 62.0407 | -61.441 | -61.1481 | 61.7111 | 0.27466 | -0.027466 | 0.33875 | 62.0499 | -61.4456 | -0.20142 | 0.064086 | -0.054932 | 0.091553 | -0.2655 | -0.20599 | 0.073242 | 0.14648 | 61.2122 | 61.5784 | 122.9507 | 123.2803 | -0.054932 | 123.2895 | 61.5143 | -0.20599 | 123.2803 | -0.054932 | 61.5143 | 122.9507 | 123.2895 | -123.4177 | -123.4222
530.4062 | 123.3902 | -61.3083 | 61.8759 | 0.0026703 | 0.019948 | 0.012832 | 0.0013159 | 0.062478 | -0.0040139 | 0.069543 | -61.4044 | 61.9675 | -61.5784 | -61.2717 | 61.5646 | 0.17853 | -0.009155 | 0.23346 | 61.9904 | -61.5189 | -0.27008 | 0.091552 | -0.09613 | 0.036622 | -0.31128 | -0.21057 | 0.11444 | 0.17395 | 61.2991 | 61.5417 | 122.8729 | 123.2758 | -0.09613 | 123.2986 | 61.4868 | -0.21057 | 123.2758 | -0.09613 | 61.4868 | 122.8729 | 123.2986 | -123.4543 | -123.3948
532.1719 | 123.3261 | -61.2808 | 61.9812 | -0.012589 | 0.018239 | 0.012192 | -0.0048791 | 0.062265 | -0.0038003 | 0.068261 | -61.3129 | 62.0499 | -61.4731 | -61.1664 | 61.6791 | 0.27466 | -0.13275 | 0.31128 | 62.0132 | -61.441 | -0.19226 | 0.068665 | -0.032043 | 0.11444 | -0.30212 | -0.16022 | 0.032044 | 0.16022 | 61.1481 | 61.5921 | 122.9599 | 123.3307 | -0.032043 | 123.2941 | 61.5555 | -0.16022 | 123.3307 | -0.032043 | 61.5555 | 122.9599 | 123.2941 | -123.4543 | -123.4222
533.9062 | 123.3353 | -62.4252 | 60.7773 | -0.0049592 | 0.022939 | 0.011978 | -0.0018885 | 0.062692 | -0.0046549 | 0.067193 | -62.4527 | 60.9009 | -62.6358 | -62.3291 | 60.5209 | 0.21973 | -0.004578 | 0.29297 | 60.91 | -62.5992 | -0.21057 | 0.1236 | -0.027466 | 0.09613 | -0.25635 | -0.17395 | 0.13275 | 0.18311 | 62.4207 | 62.7182 | 122.9462 | 123.3261 | -0.027466 | 123.3353 | 62.645 | -0.17395 | 123.3261 | -0.027466 | 62.645 | 122.9462 | 123.3353 | -123.4131 | -123.3765
535.5938 | 123.3032 | -62.2971 | 60.9283 | -0.012589 | 0.018666 | 0.018173 | 0.00088868 | 0.064828 | -0.0055093 | 0.070397 | -62.3474 | 60.9329 | -62.5214 | -62.233 | 60.6308 | 0.19684 | -0.24719 | 0.2243 | 60.9512 | -62.5031 | -0.2243 | 0.004577 | -0.050354 | 0.064087 | -0.29755 | -0.20599 | 0.022888 | 0.17395 | 62.0499 | 62.5214 | 122.9279 | 123.23 | -0.050354 | 123.2483 | 62.4939 | -0.20599 | 123.23 | -0.050354 | 62.4939 | 122.9279 | 123.2483 | -123.4497 | -123.4314
537.3594 | 123.436 | -62.3291 | 60.7956 | 0.017929 | 0.021657 | 0.017105 | 0.0011023 | 0.063333 | -0.0050821 | 0.070611 | -62.5168 | 60.9192 | -62.6541 | -62.4023 | 60.434 | 0.073242 | -0.032043 | 0.07782 | 60.9558 | -62.6038 | -0.32501 | 0.1236 | -0.18768 | -0.073242 | -0.36163 | -0.27466 | 0.16022 | 0.13733 | 62.2971 | 62.4069 | 122.7631 | 123.2483 | -0.18768 | 123.2849 | 62.4023 | -0.27466 | 123.2483 | -0.18768 | 62.4023 | 122.7631 | 123.2849 | -123.4497 | -123.3994
539.1094 | 123.317 | -62.3749 | 60.8414 | 0.0026703 | 0.018025 | 0.013687 | -0.00060672 | 0.065042 | -0.0063639 | 0.069543 | -62.4619 | 60.8826 | -62.6221 | -62.3245 | 60.5026 | 0.16937 | -0.21973 | 0.19226 | 60.8643 | -62.5671 | -0.24719 | 0.041198 | -0.086975 | 0.050354 | -0.33874 | -0.19226 | 0.022888 | 0.16022 | 62.1552 | 62.5671 | 122.8775 | 123.2574 | -0.086975 | 123.2391 | 62.5443 | -0.19226 | 123.2574 | -0.086975 | 62.5443 | 122.8775 | 123.2391 | -123.4634 | -123.4085
540.875 | 123.2895 | -62.3428 | 60.91 | 0.0026703 | 0.018666 | 0.0083463 | -0.0029565 | 0.063333 | -0.0040139 | 0.072534 | -62.3932 | 60.8963 | -62.5763 | -62.2513 | 60.5896 | 0.20142 | -0.21973 | 0.21057 | 60.9283 | -62.5122 | -0.23346 | -0.013733 | -0.050354 | 0.091552 | -0.32043 | -0.16937 | 0.018311 | 0.18311 | 62.1231 | 62.5534 | 122.9324 | 123.2391 | -0.050354 | 123.2712 | 62.5443 | -0.16937 | 123.2391 | -0.050354 | 62.5443 | 122.9324 | 123.2712 | -123.4863 | -123.4222
542.625 | 123.3627 | -62.4344 | 60.7773 | 0.0026703 | 0.020162 | 0.012832 | 0.00046148 | 0.064187 | -0.0076455 | 0.069543 | -62.5076 | 60.8276 | -62.6999 | -62.3749 | 60.4568 | 0.17853 | -0.013733 | 0.23804 | 60.878 | -62.6083 | -0.2655 | 0.050354 | -0.073242 | 0.059509 | -0.32043 | -0.17395 | 0.10071 | 0.19226 | 62.4207 | 62.6724 | 122.8912 | 123.262 | -0.073242 | 123.3124 | 62.6129 | -0.17395 | 123.262 | -0.073242 | 62.6129 | 122.8912 | 123.3124 | -123.4772 | -123.3856
544.3125 | 123.3536 | -62.4893 | 60.6583 | -0.0049592 | 0.019734 | 0.015396 | 0.0015295 | 0.064187 | -0.0048685 | 0.069116 | -62.5992 | 60.7361 | -62.7777 | -62.4664 | 60.3607 | 0.16937 | -0.036621 | 0.20599 | 60.759 | -62.7594 | -0.28839 | 0.07782 | -0.10986 | 0.022888 | -0.29755 | -0.27008 | 0.10071 | 0.17853 | 62.4527 | 62.6953 | 122.85 | 123.2254 | -0.10986 | 123.2483 | 62.6587 | -0.27008 | 123.2254 | -0.10986 | 62.6587 | 122.85 | 123.2483 | -123.436 | -123.4177
546.0625 | 110.6277 | -118.5562 | 4.6051 | 0.0103 | 0.020803 | 0.016678 | 0.00024788 | 0.065469 | -0.0038003 | 0.071679 | -117.9108 | 5.0949 | -118.3914 | -118.3777 | 4.7562 | -2.8564 | -0.036621 | 0.032043 | 4.9713 | -118.6111 | 0.16479 | 0.48981 | 0.64545 | 0.17853 | 0.15106 | -0.054932 | 0.36621 | 0.48065 | 118.5196 | 118.5883 | 123.3124 | 123.6511 | 0.64545 | 123.5275 | 115.6998 | -0.054932 | 123.6511 | 0.64545 | 115.6998 | 123.3124 | 123.5275 | -122.9965 | -123.2162
547.8281 | 123.3353 | -120.3918 | 2.8244 | -0.0049592 | 0.019734 | 0.016464 | -0.0050927 | 0.062051 | -0.0038003 | 0.070825 | -120.3506 | 2.8427 | -120.6985 | -120.2362 | 2.7466 | -1.7303 | -0.21973 | 0.13275 | 2.8748 | -120.7077 | -0.3067 | 0.01831 | 0.041199 | 0.15564 | -0.07782 | -0.31586 | 0.050354 | 0.3479 | 120.1721 | 120.5246 | 123.1384 | 123.2346 | 0.041199 | 123.2666 | 118.6615 | -0.31586 | 123.2346 | 0.041199 | 118.6615 | 123.1384 | 123.2666 | -123.5229 | -123.5321
549.5156 | 123.3765 | -120.7581 | 2.4857 | 0.0103 | 0.019307 | 0.0186 | -0.00082032 | 0.064615 | -0.0087137 | 0.069116 | -120.488 | 2.71 | -120.813 | -119.7098 | 3.1403 | -1.3596 | 0.16479 | 0.40741 | 3.2043 | -120.3735 | -0.054931 | 0.2243 | 0.27008 | 1.0483 | 0.6546 | 0.38452 | 0.71869 | 0.32501 | 120.9229 | 121.1655 | 123.8983 | 123.468 | 0.27008 | 123.9624 | 119.3985 | 0.38452 | 123.468 | 0.27008 | 119.3985 | 123.8983 | 123.9624 | -123.2986 | -122.8592
551.2656 | 123.317 | -121.0831 | 2.2064 | -0.012589 | 0.019948 | 0.014969 | -0.0040247 | 0.065683 | -0.0038003 | 0.070825 | -121.5912 | 1.6342 | -121.8567 | -121.3806 | 1.6571 | -1.8631 | -0.35248 | 0.050354 | 1.68 | -121.8567 | -0.77362 | -0.57221 | -0.50812 | -0.29755 | -0.54932 | -0.77362 | -0.52643 | 0.2655 | 120.7306 | 121.1334 | 122.7402 | 122.7173 | -0.50812 | 122.7631 | 119.22 | -0.77362 | 122.7173 | -0.50812 | 119.22 | 122.7402 | 122.7631 | -124.0631 | -124.0631
553.0156 | 123.3627 | -122.4518 | 0.7782 | 0.0103 | 0.018666 | 0.012619 | -0.00017952 | 0.065683 | -0.0052957 | 0.069116 | -122.3465 | 0.87891 | -122.7036 | -122.1771 | 0.77362 | -1.8906 | -0.10529 | 0.13275 | 0.92926 | -122.612 | -0.25177 | 0.10071 | 0.10528 | 0.27466 | -0.004577 | -0.16022 | 0.15106 | 0.35706 | 122.3465 | 122.5845 | 123.2254 | 123.3307 | 0.10528 | 123.381 | 120.5612 | -0.16022 | 123.3307 | 0.10528 | 120.5612 | 123.2254 | 123.381 | -123.4818 | -123.3902
554.6875 | 123.3582 | -122.4197 | 0.81482 | -0.0049592 | 0.018453 | 0.019455 | -0.00060672 | 0.063333 | -0.0080729 | 0.070825 | -122.3465 | 0.83771 | -122.6852 | -122.1497 | 0.80566 | -1.9043 | -0.13733 | 0.15106 | 0.99792 | -122.7173 | -0.2655 | 0.022889 | 0.073242 | 0.27008 | -0.009155 | -0.29755 | 0.18311 | 0.33875 | 122.2824 | 122.5708 | 123.2254 | 123.2574 | 0.073242 | 123.4177 | 120.5154 | -0.29755 | 123.2574 | 0.073242 | 120.5154 | 123.2254 | 123.4177 | -123.5001 | -123.5321
556.4531 | 123.3078 | -122.58 | 0.68207 | -0.020218 | 0.019094 | 0.012619 | -0.0085107 | 0.061624 | -0.0029459 | 0.070184 | -122.5296 | 0.71411 | -122.7905 | -122.3969 | 0.61798 | -1.9455 | -0.24261 | 0.13275 | 0.72784 | -122.8363 | -0.21057 | 0.032043 | 0.050354 | 0.1831 | -0.064087 | -0.25635 | 0.045776 | 0.26093 | 122.3373 | 122.7127 | 123.1979 | 123.2941 | 0.050354 | 123.3078 | 120.6345 | -0.25635 | 123.2941 | 0.050354 | 120.6345 | 123.1979 | 123.3078 | -123.4726 | -123.5184
558.2031 | 123.3261 | -122.2046 | 1.062 | -0.0049592 | 0.015035 | 0.014114 | -0.0057337 | 0.063974 | -0.0046549 | 0.069329 | -122.1634 | 1.0529 | -122.4472 | -122.0169 | 0.99335 | -1.9592 | -0.25177 | 0.086975 | 1.1398 | -122.374 | -0.24262 | -0.009156 | 0.041199 | 0.18768 | -0.068665 | -0.16937 | 0.07782 | 0.28381 | 121.9528 | 122.2916 | 123.1979 | 123.2574 | 0.041199 | 123.3444 | 120.2454 | -0.16937 | 123.2574 | 0.041199 | 120.2454 | 123.1979 | 123.3444 | -123.5092 | -123.436
559.8906 | 123.4085 | -122.3053 | 0.93384 | -0.0049592 | 0.017598 | 0.010696 | 0.0025977 | 0.065469 | -0.0072183 | 0.069757 | -122.3648 | 0.92926 | -122.6303 | -122.2458 | 0.71411 | -2.0966 | -0.10529 | 0.018311 | 0.98877 | -122.5983 | -0.32501 | -0.004578 | -0.059509 | 0.059509 | -0.21973 | -0.29297 | 0.054932 | 0.2655 | 122.2 | 122.3236 | 123.0194 | 123.2346 | -0.059509 | 123.2941 | 120.2087 | -0.29297 | 123.2346 | -0.059509 | 120.2087 | 123.0194 | 123.2941 | -123.5641 | -123.5321
561.6406 | 123.2758 | -122.4014 | 0.88806 | 0.0026703 | 0.017598 | 0.012405 | -0.0033837 | 0.065683 | -0.0055093 | 0.06997 | -122.3145 | 0.89264 | -122.6074 | -122.168 | 0.80566 | -2.0096 | -0.33875 | 0.11902 | 0.91095 | -122.58 | -0.20599 | 0.004577 | 0.086975 | 0.23346 | -0.082398 | -0.17853 | 0.022888 | 0.29297 | 122.0627 | 122.5204 | 123.2071 | 123.2941 | 0.086975 | 123.3124 | 120.3918 | -0.17853 | 123.2941 | 0.086975 | 120.3918 | 123.2071 | 123.3124 | -123.4955 | -123.468
563.3906 | 123.3673 | -122.3602 | 0.85144 | -0.012589 | 0.017385 | 0.01091 | -0.0042383 | 0.060342 | -0.0067911 | 0.06997 | -122.3831 | 0.90179 | -122.644 | -122.2504 | 0.72784 | -2.0645 | -0.036621 | 0.14191 | 0.9201 | -122.6761 | -0.28381 | 0.050354 | -0.022889 | 0.10986 | -0.1236 | -0.31586 | 0.068665 | 0.26093 | 122.3236 | 122.5021 | 123.0881 | 123.262 | -0.022889 | 123.2803 | 120.2957 | -0.31586 | 123.262 | -0.022889 | 120.2957 | 123.0881 | 123.2803 | -123.4955 | -123.5275
565.1406 | 123.3536 | -122.319 | 0.84686 | 0.0026703 | 0.016957 | 0.014541 | -0.0033837 | 0.062265 | -0.0061503 | 0.070611 | -122.3557 | 0.92926 | -122.6257 | -122.2229 | 0.75073 | -2.092 | -0.022888 | 0.13275 | 0.97046 | -122.6303 | -0.3067 | 0.082397 | -0.036621 | 0.096131 | -0.096131 | -0.31128 | 0.1236 | 0.27008 | 122.2961 | 122.4518 | 123.0698 | 123.2483 | -0.036621 | 123.2895 | 120.2271 | -0.31128 | 123.2483 | -0.036621 | 120.2271 | 123.0698 | 123.2895 | -123.4726 | -123.4772
566.8906 | 123.3261 | -122.438 | 0.77362 | 0.0026703 | 0.018453 | 0.014541 | -0.0029565 | 0.06376 | -0.0031595 | 0.073815 | -122.4243 | 0.80109 | -122.7173 | -122.2687 | 0.6958 | -2.1515 | -0.35706 | 0.022888 | 0.83313 | -122.6852 | -0.27924 | 0.027465 | 0.013733 | 0.16937 | -0.07782 | -0.24719 | 0.059509 | 0.29297 | 122.081 | 122.4609 | 123.1339 | 123.2391 | 0.013733 | 123.2712 | 120.2866 | -0.24719 | 123.2391 | 0.013733 | 120.2866 | 123.1339 | 123.2712 | -123.4909 | -123.4589
568.5625 | 123.3627 | -122.2275 | 0.9613 | 0.0026703 | 0.020162 | 0.015396 | -0.0012475 | 0.062478 | -0.0055093 | 0.067834 | -122.2778 | 1.0162 | -122.5708 | -122.1268 | 0.83771 | -2.0828 | 0 | 0.13733 | 1.0437 | -122.5571 | -0.34332 | 0.054931 | -0.050354 | 0.10071 | -0.1236 | -0.32959 | 0.082397 | 0.29297 | 122.2275 | 122.3648 | 123.0652 | 123.2437 | -0.050354 | 123.2712 | 120.1447 | -0.32959 | 123.2437 | -0.050354 | 120.1447 | 123.0652 | 123.2712 | -123.5321 | -123.5184
570.3125 | 123.2346 | -122.168 | 1.0712 | -0.0049592 | 0.018666 | 0.015182 | -0.0061609 | 0.064187 | -0.0029459 | 0.069329 | -122.081 | 1.0483 | -122.3785 | -121.9528 | 1.0345 | -1.9958 | -0.17853 | 0.24261 | 1.0803 | -122.4243 | -0.21057 | -0.022888 | 0.086975 | 0.21515 | -0.036621 | -0.25635 | 0.009155 | 0.29755 | 121.9894 | 122.4106 | 123.2025 | 123.2162 | 0.086975 | 123.2483 | 120.1721 | -0.25635 | 123.2162 | 0.086975 | 120.1721 | 123.2025 | 123.2483 | -123.4497 | -123.4955
572.0625 | 123.2758 | -122.2366 | 0.99792 | -0.0049592 | 0.017598 | 0.01561 | -0.0059473 | 0.06376 | -0.0059365 | 0.068261 | -122.2 | 1.0071 | -122.4655 | -122.0627 | 0.90179 | -2.1286 | -0.26093 | 0.091553 | 1.0208 | -122.4609 | -0.22888 | 0.009155 | 0.036621 | 0.17395 | -0.096131 | -0.2243 | 0.022888 | 0.2655 | 121.9757 | 122.3282 | 123.1384 | 123.2437 | 0.036621 | 123.2574 | 120.108 | -0.2243 | 123.2437 | 0.036621 | 120.108 | 123.1384 | 123.2574 | -123.4634 | -123.4589
573.7969 | 123.262 | -122.1909 | 1.0345 | -0.0049592 | 0.016103 | 0.016891 | -0.0027429 | 0.063119 | -0.0035867 | 0.070611 | -122.1359 | 1.03 | -122.4472 | -122.0032 | 0.95673 | -2.0874 | -0.10529 | 0.21057 | 1.0849 | -122.4564 | -0.25635 | -0.004578 | 0.054932 | 0.18768 | -0.07782 | -0.2655 | 0.050354 | 0.31128 | 122.0856 | 122.4014 | 123.1476 | 123.2208 | 0.054932 | 123.2758 | 120.1035 | -0.2655 | 123.2208 | 0.054932 | 120.1035 | 123.1476 | 123.2758 | -123.4818 | -123.4909
575.4844 | 123.381 | -121.9666 | 1.1993 | -0.0049592 | 0.020803 | 0.017746 | 0.0015295 | 0.064828 | -0.0055093 | 0.071466 | -122.0169 | 1.268 | -122.3236 | -121.9025 | 1.0574 | -2.2385 | -0.13275 | 0.009155 | 1.2955 | -122.2778 | -0.35705 | 0.068664 | -0.050354 | 0.064087 | -0.14191 | -0.31128 | 0.09613 | 0.3067 | 121.8338 | 121.9757 | 123.024 | 123.2346 | -0.050354 | 123.262 | 119.7281 | -0.31128 | 123.2346 | -0.050354 | 119.7281 | 123.024 | 123.262 | -123.5229 | -123.4772
577.1875 | 123.3582 | -121.6095 | 1.5427 | 0.0103 | 0.021443 | 0.013687 | 0.00024788 | 0.064187 | -0.0065775 | 0.069543 | -121.6644 | 1.6251 | -121.9299 | -121.5408 | 1.3916 | -2.1652 | -0.21515 | -0.050354 | 1.6388 | -121.9162 | -0.32043 | 0.082397 | -0.054932 | 0.068664 | -0.15106 | -0.3067 | 0.09613 | 0.2655 | 121.3943 | 121.5591 | 123.0011 | 123.2346 | -0.054932 | 123.2483 | 119.4443 | -0.3067 | 123.2346 | -0.054932 | 119.4443 | 123.0011 | 123.2483 | -123.4726 | -123.4589
578.9375 | 123.2803 | -121.3989 | 1.767 | -0.0049592 | 0.015035 | 0.015396 | -0.0059473 | 0.063333 | -0.0038003 | 0.071679 | -121.6187 | 1.5427 | -121.8979 | -121.2891 | 1.6937 | -1.9501 | -0.2243 | 0.12817 | 1.8082 | -121.7834 | -0.49896 | -0.2243 | -0.21973 | 0.10986 | -0.073242 | -0.38452 | 0.041199 | 0.27924 | 121.1746 | 121.5271 | 123.0927 | 122.9416 | -0.21973 | 123.2071 | 119.4489 | -0.38452 | 122.9416 | -0.21973 | 119.4489 | 123.0927 | 123.2071 | -123.6649 | -123.5504
580.625 | 123.2254 | -122.0306 | 1.181 | -0.0049592 | 0.018453 | 0.01091 | -0.0061609 | 0.062265 | -0.0057229 | 0.070611 | -121.9849 | 1.1581 | -122.2824 | -121.8384 | 1.1215 | -2.0828 | -0.25635 | 0.21515 | 1.181 | -122.2778 | -0.25177 | -0.022888 | 0.045777 | 0.19226 | -0.059509 | -0.24719 | 0 | 0.29755 | 121.7743 | 122.2458 | 123.1522 | 123.1888 | 0.045777 | 123.2117 | 119.9478 | -0.24719 | 123.1888 | 0.045777 | 119.9478 | 123.1522 | 123.2117 | -123.4634 | -123.4589
582.3906 | 123.3353 | -121.7697 | 1.4465 | -0.0049592 | 0.022298 | 0.013046 | 0.0011023 | 0.064828 | -0.0087137 | 0.071893 | -121.8109 | 1.4053 | -122.1222 | -121.7331 | 1.1902 | -2.2522 | -0.17853 | 0.004578 | 1.3962 | -122.1359 | -0.35248 | -0.041199 | -0.041199 | 0.036621 | -0.25635 | -0.36621 | -0.050354 | 0.31128 | 121.5912 | 121.7743 | 122.9599 | 123.175 | -0.041199 | 123.1659 | 119.5175 | -0.36621 | 123.175 | -0.041199 | 119.5175 | 122.9599 | 123.1659 | -123.5687 | -123.5825
584.1406 | 123.2895 | -122.1634 | 1.0162 | 0.0026703 | 0.020162 | 0.016037 | -0.00017952 | 0.065469 | -0.0052957 | 0.071893 | -122.1359 | 1.062 | -122.4289 | -121.9986 | 0.93842 | -2.1835 | -0.27924 | 0.07782 | 1.0803 | -122.4106 | -0.2655 | 0.045777 | 0.027466 | 0.16479 | -0.077819 | -0.24719 | 0.064087 | 0.29297 | 121.8842 | 122.2412 | 123.1018 | 123.2254 | 0.027466 | 123.2437 | 119.9799 | -0.24719 | 123.2254 | 0.027466 | 119.9799 | 123.1018 | 123.2437 | -123.4451 | -123.4268
585.8906 | 123.2803 | -122.1634 | 1.0208 | -0.0049592 | 0.020375 | 0.018814 | -0.00039312 | 0.062906 | -0.0059365 | 0.068902 | -122.0993 | 1.0712 | -122.4335 | -121.9849 | 0.94757 | -2.179 | -0.082397 | 0.16022 | 1.0941 | -122.4564 | -0.27008 | 0.050354 | 0.064087 | 0.17853 | -0.073242 | -0.29297 | 0.073242 | 0.33417 | 122.081 | 122.3236 | 123.111 | 123.2346 | 0.064087 | 123.2574 | 119.9844 | -0.29297 | 123.2346 | 0.064087 | 119.9844 | 123.111 | 123.2574 | -123.4543 | -123.4772
587.5781 | 123.3032 | -122.287 | 0.87433 | -0.0049592 | 0.019094 | 0.013687 | -0.0033837 | 0.063974 | -0.0040139 | 0.073388 | -122.287 | 0.92468 | -122.5754 | -122.1634 | 0.78735 | -2.2247 | -0.28381 | 0.068665 | 0.93842 | -122.5616 | -0.28839 | 0.050354 | 0 | 0.1236 | -0.086975 | -0.27466 | 0.064087 | 0.28839 | 122.0032 | 122.3557 | 123.0743 | 123.2117 | 0 | 123.2254 | 120.0623 | -0.27466 | 123.2117 | 0 | 120.0623 | 123.0743 | 123.2254 | -123.4497 | -123.436
589.3281 | 123.2391 | -122.2504 | 0.95215 | -0.0049592 | 0.01653 | 0.015396 | -0.0082971 | 0.063547 | -0.0052957 | 0.071038 | -122.2137 | 0.94757 | -122.4747 | -122.0627 | 0.91553 | -2.1423 | -0.22888 | 0.17853 | 0.98419 | -122.493 | -0.2243 | -0.004577 | 0.036621 | 0.18768 | -0.036621 | -0.24262 | 0.032044 | 0.26093 | 122.0215 | 122.4289 | 123.1659 | 123.1979 | 0.036621 | 123.2346 | 120.108 | -0.24262 | 123.1979 | 0.036621 | 120.108 | 123.1659 | 123.2346 | -123.4268 | -123.4451
591.0312 | 123.262 | -122.2641 | 0.9201 | -0.012589 | 0.018239 | 0.013046 | -0.0040247 | 0.06376 | -0.0025187 | 0.071893 | -122.2366 | 0.92926 | -122.525 | -122.1313 | 0.83771 | -2.2293 | -0.27008 | 0.07782 | 0.95673 | -122.5571 | -0.26093 | 0.009155 | 0.027466 | 0.13275 | -0.082397 | -0.29297 | 0.036621 | 0.28839 | 121.994 | 122.3419 | 123.1018 | 123.1934 | 0.027466 | 123.2208 | 120.0348 | -0.29297 | 123.1934 | 0.027466 | 120.0348 | 123.1018 | 123.2208 | -123.4451 | -123.4772
592.7812 | 123.175 | -122.3145 | 0.90179 | 0.0103 | 0.018025 | 0.017319 | -0.0053063 | 0.061624 | -0.0023049 | 0.067834 | -122.2046 | 0.87891 | -122.5388 | -122.0673 | 0.87433 | -2.1378 | -0.23804 | 0.23804 | 0.9201 | -122.5708 | -0.2243 | -0.022888 | 0.10986 | 0.24719 | -0.027465 | -0.25635 | 0.018311 | 0.33417 | 122.0764 | 122.5525 | 123.1888 | 123.1934 | 0.10986 | 123.2346 | 120.1767 | -0.25635 | 123.1934 | 0.10986 | 120.1767 | 123.1888 | 123.2346 | -123.4406 | -123.4726
594.5312 | 123.3032 | -122.2458 | 0.86975 | 0.0103 | 0.018239 | 0.013046 | 0.00046148 | 0.063119 | -0.0059365 | 0.069757 | -122.2916 | 0.92926 | -122.5983 | -122.1542 | 0.75531 | -2.2476 | -0.032043 | 0.13733 | 0.97046 | -122.5616 | -0.35248 | 0.059509 | -0.045776 | 0.091553 | -0.11444 | -0.31586 | 0.10071 | 0.3067 | 122.2137 | 122.3831 | 123.0011 | 123.175 | -0.045776 | 123.2162 | 119.9982 | -0.31586 | 123.175 | -0.045776 | 119.9982 | 123.0011 | 123.2162 | -123.468 | -123.4314
596.2188 | 123.2117 | -122.1863 | 1.0025 | -0.012589 | 0.018239 | 0.014755 | -0.0046655 | 0.062478 | -0.0048685 | 0.068261 | -122.1039 | 1.0071 | -122.4243 | -121.9528 | 0.98419 | -2.1332 | -0.26093 | 0.23346 | 1.0208 | -122.4701 | -0.23804 | 0.004578 | 0.082397 | 0.23346 | -0.01831 | -0.28381 | 0.018311 | 0.32043 | 121.9254 | 122.4197 | 123.1705 | 123.1934 | 0.082397 | 123.2071 | 120.0531 | -0.28381 | 123.1934 | 0.082397 | 120.0531 | 123.1705 | 123.2071 | -123.4268 | -123.4726
597.9688 | 123.3353 | -122.2321 | 0.86975 | 0.0103 | 0.019094 | 0.0094143 | 0.00046148 | 0.062051 | -0.0061503 | 0.06762 | -122.3053 | 0.95673 | -122.5937 | -122.1451 | 0.76446 | -2.2705 | -0.018311 | 0.1236 | 1.0071 | -122.5296 | -0.36163 | 0.086975 | -0.073242 | 0.086975 | -0.10529 | -0.29755 | 0.13733 | 0.28839 | 122.2137 | 122.3557 | 122.9965 | 123.1888 | -0.073242 | 123.2391 | 119.9615 | -0.29755 | 123.1888 | -0.073242 | 119.9615 | 122.9965 | 123.2391 | -123.4634 | -123.3994
599.6562 | 123.2666 | -122.2778 | 0.86975 | 0.0026703 | 0.019094 | 0.014969 | 0.00067508 | 0.063547 | -0.0061503 | 0.070184 | -122.2458 | 0.9201 | -122.5937 | -122.0993 | 0.80566 | -2.2385 | -0.11902 | 0.16937 | 0.95673 | -122.5708 | -0.31586 | 0.050354 | 0.032043 | 0.17853 | -0.064087 | -0.29297 | 0.086975 | 0.3479 | 122.1588 | 122.4472 | 123.0835 | 123.1979 | 0.032043 | 123.2346 | 120.0394 | -0.29297 | 123.1979 | 0.032043 | 120.0394 | 123.0835 | 123.2346 | -123.4634 | -123.4406
601.4219 | 123.3124 | -122.0215 | 1.0849 | -0.0049592 | 0.018239 | 0.0077053 | -0.0057337 | 0.060983 | -0.0052957 | 0.070825 | -122.0673 | 1.181 | -122.3328 | -121.9254 | 1.0117 | -2.2842 | -0.018311 | 0.13275 | 1.2222 | -122.3282 | -0.31128 | 0.09613 | -0.045777 | 0.09613 | -0.073242 | -0.3067 | 0.13733 | 0.2655 | 122.0032 | 122.1542 | 123.0331 | 123.2025 | -0.045777 | 123.2437 | 119.7372 | -0.3067 | 123.2025 | -0.045777 | 119.7372 | 123.0331 | 123.2437 | -123.4177 | -123.4131
603.125 | 123.3307 | -122.1085 | 1.0025 | 0.0026703 | 0.018453 | 0.013473 | -0.00017952 | 0.064401 | -0.0074319 | 0.070611 | -122.1771 | 1.0849 | -122.4426 | -122.0535 | 0.85602 | -2.3621 | -0.10986 | 0.004578 | 1.1078 | -122.3831 | -0.33417 | 0.082398 | -0.068665 | 0.054931 | -0.14648 | -0.27466 | 0.10529 | 0.2655 | 121.9986 | 122.113 | 122.9645 | 123.1934 | -0.068665 | 123.2162 | 119.7464 | -0.27466 | 123.1934 | -0.068665 | 119.7464 | 122.9645 | 123.2162 | -123.4451 | -123.3856
604.875 | 123.3124 | -122.3053 | 0.84686 | -0.012589 | 0.018025 | 0.017105 | -0.00082032 | 0.065042 | -0.0067911 | 0.06997 | -122.2824 | 0.94757 | -122.5662 | -122.1863 | 0.73242 | -2.33 | -0.10529 | 0.022888 | 0.9613 | -122.5708 | -0.26093 | 0.10071 | 0.022888 | 0.11902 | -0.11444 | -0.2655 | 0.11444 | 0.28381 | 122.2 | 122.3282 | 123.0377 | 123.2529 | 0.022888 | 123.2666 | 119.9753 | -0.2655 | 123.2529 | 0.022888 | 119.9753 | 123.0377 | 123.2666 | -123.4131 | -123.4177
606.5625 | 123.2254 | -122.2321 | 0.91553 | -0.012589 | 0.019307 | 0.010483 | -0.0085107 | 0.062478 | -0.0027323 | 0.069329 | -122.2366 | 0.92468 | -122.4838 | -122.113 | 0.82398 | -2.2705 | -0.23804 | 0.10986 | 0.93384 | -122.5571 | -0.25177 | 0.009156 | -0.004577 | 0.11902 | -0.091552 | -0.32501 | 0.018311 | 0.24719 | 121.994 | 122.3419 | 123.056 | 123.1567 | -0.004577 | 123.1659 | 119.9615 | -0.32501 | 123.1567 | -0.004577 | 119.9615 | 123.056 | 123.1659 | -123.3994 | -123.4726
608.3125 | 123.1888 | -122.2412 | 0.9613 | -0.012589 | 0.01888 | 0.019241 | -0.0031701 | 0.062906 | -0.0052957 | 0.070825 | -122.1359 | 0.93384 | -122.4655 | -122.0169 | 0.89264 | -2.2568 | -0.35706 | 0.10529 | 0.97504 | -122.5067 | -0.2243 | -0.027466 | 0.10529 | 0.2243 | -0.068665 | -0.2655 | 0.013733 | 0.32959 | 121.8842 | 122.3465 | 123.1339 | 123.175 | 0.10529 | 123.2162 | 119.9844 | -0.2655 | 123.175 | 0.10529 | 119.9844 | 123.1339 | 123.2162 | -123.4268 | -123.468
610.0625 | 123.2483 | -122.1909 | 0.95215 | 0.0026703 | 0.018666 | 0.014328 | 0.0017431 | 0.062692 | -0.0067911 | 0.070825 | -122.2 | 0.92926 | -122.5571 | -122.0581 | 0.83313 | -2.2705 | -0.11902 | 0.16022 | 0.97961 | -122.5342 | -0.36621 | -0.022888 | -0.009155 | 0.13275 | -0.11902 | -0.34332 | 0.027466 | 0.35706 | 122.0718 | 122.3511 | 123.024 | 123.1201 | -0.009155 | 123.1705 | 119.9203 | -0.34332 | 123.1201 | -0.009155 | 119.9203 | 123.024 | 123.1705 | -123.5092 | -123.4863
611.8125 | 123.1888 | -122.1359 | 1.0437 | -0.0049592 | 0.017385 | 0.0186 | -0.0053063 | 0.062906 | -0.0048685 | 0.070825 | -122.0306 | 1.0529 | -122.3785 | -121.8979 | 1.0025 | -2.2522 | -0.39368 | 0.082397 | 1.0803 | -122.3373 | -0.24262 | 0.009155 | 0.10528 | 0.23804 | -0.041199 | -0.20142 | 0.036621 | 0.3479 | 121.7422 | 122.2183 | 123.1384 | 123.1888 | 0.10528 | 123.2162 | 119.8837 | -0.20142 | 123.1888 | 0.10528 | 119.8837 | 123.1384 | 123.2162 | -123.4222 | -123.381
613.5 | 123.2849 | -122.1817 | 0.92926 | -0.012589 | 0.018453 | 0.01625 | 0.00024788 | 0.064187 | -0.0046549 | 0.068261 | -122.1909 | 0.98877 | -122.5067 | -122.0581 | 0.83771 | -2.3346 | -0.045776 | 0.13733 | 1.0391 | -122.4792 | -0.32501 | 0.05951 | -0.009155 | 0.1236 | -0.091552 | -0.29755 | 0.10986 | 0.31586 | 122.1359 | 122.319 | 123.0194 | 123.1705 | -0.009155 | 123.2208 | 119.8471 | -0.29755 | 123.1705 | -0.009155 | 119.8471 | 123.0194 | 123.2208 | -123.436 | -123.4085
615.25 | 123.2162 | -121.8567 | 1.2863 | -0.0049592 | 0.017812 | 0.01326 | -0.0070153 | 0.061838 | -0.0063639 | 0.070611 | -121.8292 | 1.3321 | -122.0856 | -121.7056 | 1.2131 | -2.2339 | -0.21515 | 0.13275 | 1.355 | -122.1451 | -0.22888 | 0.045776 | 0.027465 | 0.15106 | -0.073242 | -0.28839 | 0.068664 | 0.25635 | 121.6415 | 121.9894 | 123.0698 | 123.1888 | 0.027465 | 123.2117 | 119.6228 | -0.28839 | 123.1888 | 0.027465 | 119.6228 | 123.0698 | 123.2117 | -123.3719 | -123.4314
617.0156 | 123.3307 | -121.8521 | 1.2726 | 0.0103 | 0.017598 | 0.013687 | 0.00088868 | 0.062906 | -0.0052957 | 0.072747 | -121.9208 | 1.3138 | -122.1817 | -121.7926 | 1.1032 | -2.3666 | -0.14191 | 0.009155 | 1.3275 | -122.1634 | -0.32959 | 0.041199 | -0.068664 | 0.059509 | -0.16937 | -0.31128 | 0.054932 | 0.26093 | 121.7102 | 121.8613 | 122.9553 | 123.1659 | -0.068664 | 123.1796 | 119.4855 | -0.31128 | 123.1659 | -0.068664 | 119.4855 | 122.9553 | 123.1796 | -123.4543 | -123.436
618.6875 | 123.2895 | -121.8842 | 1.2177 | 0.0026703 | 0.019094 | 0.018387 | -0.0025293 | 0.063333 | -0.0065775 | 0.06997 | -121.9528 | 1.2634 | -122.2458 | -121.8018 | 1.0666 | -2.3849 | -0.14191 | 0.022888 | 1.3046 | -122.2046 | -0.36163 | 0.045777 | -0.068665 | 0.082397 | -0.15106 | -0.32043 | 0.086975 | 0.29297 | 121.7422 | 121.907 | 122.9507 | 123.1476 | -0.068665 | 123.1888 | 119.4992 | -0.32043 | 123.1476 | -0.068665 | 119.4992 | 122.9507 | 123.1888 | -123.4634 | -123.4222
620.4375 | 123.1613 | -121.0281 | 2.1423 | -0.020218 | 0.018025 | 0.017319 | -0.0029565 | 0.063547 | -0.0057229 | 0.070184 | -121.0098 | 2.0279 | -121.3348 | -120.7672 | 2.1149 | -2.0508 | -0.17853 | 0.32501 | 2.1332 | -121.2204 | -0.3067 | -0.11444 | 0.01831 | 0.26093 | -0.027466 | -0.19226 | -0.009155 | 0.32501 | 120.8496 | 121.3531 | 123.143 | 123.056 | 0.01831 | 123.1613 | 118.9774 | -0.19226 | 123.056 | 0.01831 | 118.9774 | 123.143 | 123.1613 | -123.4772 | -123.3627
622.1875 | 123.1796 | -120.5154 | 2.417 | -0.0049592 | 0.016957 | 0.01561 | -0.0055199 | 0.062906 | -0.0050821 | 0.070184 | -122.2229 | 0.93842 | -122.4747 | -122.0901 | 0.83771 | -2.3666 | -0.25177 | 0.064087 | 0.95673 | -122.5159 | -1.9592 | -1.4786 | -1.7075 | -1.5747 | -1.5793 | -2.0004 | -1.4603 | 0.25177 | 120.2637 | 120.5795 | 121.3531 | 121.4539 | -1.7075 | 121.4722 | 118.1488 | -2.0004 | 121.4539 | -1.7075 | 118.1488 | 121.3531 | 121.4722 | -124.8917 | -124.9329
623.875 | 123.2391 | -122.287 | 0.85144 | -0.012589 | 0.019734 | 0.011551 | 0.0030249 | 0.065042 | -0.0072183 | 0.069329 | -122.2641 | 0.8606 | -122.58 | -122.1085 | 0.77362 | -2.3254 | -0.1236 | 0.15564 | 0.92926 | -122.5616 | -0.29297 | 0.009156 | 0.022888 | 0.17853 | -0.077819 | -0.27466 | 0.07782 | 0.31586 | 122.1634 | 122.4426 | 123.0606 | 123.1476 | 0.022888 | 123.2162 | 119.9615 | -0.27466 | 123.1476 | 0.022888 | 119.9615 | 123.0606 | 123.2162 | -123.4314 | -123.4131
625.6094 | 123.1567 | -121.5225 | 1.8036 | -0.0049592 | 0.016103 | 0.013901 | -0.0068017 | 0.063333 | -0.0040139 | 0.068475 | -121.6873 | 1.4099 | -121.9482 | -121.4813 | 1.4099 | -2.1973 | -0.23346 | 0.19684 | 1.4877 | -121.9711 | -0.42572 | -0.39368 | -0.16479 | 0.041199 | -0.39368 | -0.44861 | -0.31586 | 0.26093 | 121.2891 | 121.7194 | 122.9324 | 122.9324 | -0.16479 | 123.0103 | 119.3253 | -0.44861 | 122.9324 | -0.16479 | 119.3253 | 122.9324 | 123.0103 | -123.7518 | -123.7747
627.3594 | 123.1659 | -121.5179 | 1.6296 | -0.012589 | 0.015462 | 0.019882 | -0.0021021 | 0.065469 | -0.0057229 | 0.071038 | -121.4355 | 1.6159 | -121.788 | -121.3211 | 1.561 | -2.2385 | -0.32044 | 0.13275 | 1.6434 | -121.7606 | -0.27008 | -0.013733 | 0.082397 | 0.19684 | -0.068665 | -0.24262 | 0.013733 | 0.35248 | 121.1975 | 121.6507 | 123.0789 | 123.1338 | 0.082397 | 123.1613 | 119.2795 | -0.24262 | 123.1338 | 0.082397 | 119.2795 | 123.0789 | 123.1613 | -123.4177 | -123.3902
629.1094 | 123.2574 | -122.2366 | 0.85602 | -0.012589 | 0.01888 | 0.013046 | 0.0030249 | 0.062906 | -0.0065775 | 0.071038 | -122.2687 | 0.91095 | -122.5891 | -122.113 | 0.75073 | -2.3666 | -0.068665 | 0.16479 | 0.92926 | -122.5754 | -0.35248 | 0.054932 | -0.032044 | 0.1236 | -0.10529 | -0.33875 | 0.073242 | 0.32043 | 122.168 | 122.4014 | 122.9874 | 123.1476 | -0.032044 | 123.1659 | 119.87 | -0.33875 | 123.1476 | -0.032044 | 119.87 | 122.9874 | 123.1659 | -123.4451 | -123.4314
630.8594 | 123.2025 | -122.3236 | 0.81024 | -0.020218 | 0.019521 | 0.0072781 | -0.0078699 | 0.062051 | -0.0038003 | 0.069757 | -122.3053 | 0.83771 | -122.5525 | -122.1771 | 0.73242 | -2.3804 | -0.24261 | 0.07782 | 0.85602 | -122.644 | -0.22888 | 0.027466 | 0.01831 | 0.14648 | -0.07782 | -0.32044 | 0.045776 | 0.24719 | 122.081 | 122.4014 | 123.056 | 123.1613 | 0.01831 | 123.1796 | 119.9432 | -0.32044 | 123.1613 | 0.01831 | 119.9432 | 123.056 | 123.1796 | -123.3627 | -123.4543
632.5625 | 123.2758 | -121.9894 | 1.0529 | -0.0049592 | 0.017598 | 0.016037 | -0.0012475 | 0.060769 | -0.0055093 | 0.069757 | -121.9803 | 1.2085 | -122.2595 | -121.8338 | 1.03 | -2.3575 | -0.013733 | 0.14648 | 1.2268 | -122.2641 | -0.27008 | 0.15564 | 0.009155 | 0.15564 | -0.022888 | -0.27466 | 0.17395 | 0.27923 | 121.9757 | 122.1359 | 123.0194 | 123.1979 | 0.009155 | 123.2162 | 119.632 | -0.27466 | 123.1979 | 0.009155 | 119.632 | 123.0194 | 123.2162 | -123.3124 | -123.317
634.3125 | 123.1934 | -121.0693 | 2.0737 | -0.020218 | 0.01653 | 0.011123 | -0.0059473 | 0.060983 | -0.0059365 | 0.070184 | -120.9961 | 2.1332 | -121.2616 | -120.8862 | 1.9821 | -2.2568 | -0.25177 | 0.059509 | 2.1103 | -121.3165 | -0.19226 | 0.05951 | 0.073242 | 0.18311 | -0.091552 | -0.24719 | 0.036622 | 0.2655 | 120.8176 | 121.1288 | 123.0515 | 123.2025 | 0.073242 | 123.1796 | 118.8126 | -0.24719 | 123.2025 | 0.073242 | 118.8126 | 123.0515 | 123.1796 | -123.3353 | -123.3902
636.0625 | 123.1522 | -121.9711 | 1.2131 | -0.0049592 | 0.017812 | 0.013473 | -0.0040247 | 0.062051 | -0.0072183 | 0.071893 | -121.8567 | 1.1856 | -122.2 | -121.7377 | 1.1353 | -2.3392 | -0.34332 | 0.10986 | 1.2039 | -122.2 | -0.22888 | -0.027466 | 0.11444 | 0.23346 | -0.07782 | -0.22888 | -0.009156 | 0.34332 | 121.6278 | 122.081 | 123.1064 | 123.1567 | 0.11444 | 123.175 | 119.632 | -0.22888 | 123.1567 | 0.11444 | 119.632 | 123.1064 | 123.175 | -123.4131 | -123.4131
637.8125 | 123.1934 | -121.9162 | 1.2177 | 0.0026703 | 0.017171 | 0.015823 | -0.0033837 | 0.061197 | -0.0035867 | 0.071038 | -121.8155 | 1.3 | -122.1039 | -121.7331 | 1.1581 | -2.3529 | -0.26093 | 0.082397 | 1.3092 | -122.1268 | -0.18768 | 0.082398 | 0.10071 | 0.18311 | -0.059509 | -0.21057 | 0.091553 | 0.28839 | 121.6553 | 121.9986 | 123.0743 | 123.2162 | 0.10071 | 123.2254 | 119.5633 | -0.21057 | 123.2162 | 0.10071 | 119.5633 | 123.0743 | 123.2254 | -123.3215 | -123.3444
639.5 | 123.1384 | -122.1085 | 1.0391 | -0.0049592 | 0.019094 | 0.014755 | -0.00039312 | 0.06376 | -0.0059365 | 0.069543 | -121.994 | 1.0254 | -122.3557 | -121.875 | 0.97961 | -2.3346 | -0.36621 | 0.11902 | 1.0666 | -122.3465 | -0.24719 | -0.013733 | 0.11444 | 0.23346 | -0.05951 | -0.23804 | 0.027465 | 0.36163 | 121.7422 | 122.2275 | 123.0881 | 123.1338 | 0.11444 | 123.175 | 119.7739 | -0.23804 | 123.1338 | 0.11444 | 119.7739 | 123.0881 | 123.175 | -123.3948 | -123.3856
641.25 | 123.2483 | -120.9595 | 2.1286 | -0.0049592 | 0.020803 | 0.012192 | -0.0016747 | 0.060556 | -0.0052957 | 0.070397 | -120.9549 | 2.1744 | -121.2616 | -120.8359 | 2.0142 | -2.33 | -0.032043 | 0.15106 | 2.2156 | -121.2616 | -0.30212 | 0.045776 | 0.004578 | 0.1236 | -0.11444 | -0.30212 | 0.086975 | 0.3067 | 120.9274 | 121.1105 | 122.9736 | 123.1338 | 0.004578 | 123.175 | 118.6295 | -0.30212 | 123.1338 | 0.004578 | 118.6295 | 122.9736 | 123.175 | -123.3902 | -123.3902
643 | 123.1247 | -120.845 | 2.3117 | -0.012589 | 0.018453 | 0.013046 | -0.0055199 | 0.061197 | -0.0052957 | 0.068048 | -120.7214 | 2.2751 | -121.0785 | -120.5887 | 2.2385 | -2.2156 | -0.24719 | 0.24261 | 2.2888 | -121.1197 | -0.23346 | -0.036622 | 0.1236 | 0.25635 | -0.073243 | -0.27466 | -0.022889 | 0.35706 | 120.5978 | 121.0876 | 123.0835 | 123.1201 | 0.1236 | 123.1339 | 118.6295 | -0.27466 | 123.1201 | 0.1236 | 118.6295 | 123.0835 | 123.1339 | -123.3902 | -123.4314
644.6719 | 123.2117 | -122.1497 | 0.96588 | -0.0049592 | 0.018453 | 0.014328 | 0.0047339 | 0.062692 | -0.0078591 | 0.071038 | -122.0993 | 0.99335 | -122.4884 | -121.9803 | 0.86975 | -2.3895 | -0.12817 | 0.15564 | 1.0208 | -122.4564 | -0.33875 | 0.027466 | 0.050354 | 0.16937 | -0.09613 | -0.3067 | 0.054932 | 0.3891 | 122.0215 | 122.3053 | 123.0194 | 123.143 | 0.050354 | 123.1705 | 119.7601 | -0.3067 | 123.143 | 0.050354 | 119.7601 | 123.0194 | 123.1705 | -123.4543 | -123.4222
646.4219 | 123.1293 | -122.1359 | 1.0208 | 0.0026703 | 0.017812 | 0.016037 | -0.0029565 | 0.063974 | -0.0031595 | 0.070184 | -122.0215 | 1.0025 | -122.3099 | -121.9025 | 0.97046 | -2.3529 | -0.36621 | 0.1236 | 1.03 | -122.3465 | -0.17395 | -0.018311 | 0.11444 | 0.23346 | -0.050354 | -0.21057 | 0.009155 | 0.28839 | 121.7697 | 122.2595 | 123.1064 | 123.1384 | 0.11444 | 123.1659 | 119.783 | -0.21057 | 123.1384 | 0.11444 | 119.783 | 123.1064 | 123.1659 | -123.3307 | -123.3673
648.1875 | 123.2483 | -121.6324 | 1.4282 | -0.0049592 | 0.019948 | 0.011123 | -0.00060672 | 0.065256 | -0.0072183 | 0.070611 | -121.6553 | 1.5152 | -121.962 | -121.5271 | 1.3184 | -2.4307 | -0.1831 | 0.018311 | 1.5381 | -121.8979 | -0.32959 | 0.086975 | -0.022888 | 0.10528 | -0.10986 | -0.2655 | 0.10986 | 0.3067 | 121.4493 | 121.6507 | 122.9507 | 123.1476 | -0.022888 | 123.1705 | 119.2017 | -0.2655 | 123.1476 | -0.022888 | 119.2017 | 122.9507 | 123.1705 | -123.3902 | -123.3261
649.9375 | 123.1796 | -121.6278 | 1.4694 | -0.0049592 | 0.015676 | 0.015182 | -0.0074427 | 0.060983 | -0.0035867 | 0.070397 | -121.6324 | 1.4694 | -121.9116 | -121.4813 | 1.3962 | -2.3804 | -0.24261 | 0.10529 | 1.5244 | -121.8887 | -0.28381 | 0 | -0.004577 | 0.14648 | -0.073242 | -0.26093 | 0.054932 | 0.27924 | 121.3852 | 121.7331 | 123.024 | 123.0972 | -0.004577 | 123.1522 | 119.2474 | -0.26093 | 123.0972 | -0.004577 | 119.2474 | 123.024 | 123.1522 | -123.381 | -123.3582
651.6094 | 123.175 | -121.6461 | 1.4694 | 0.0026703 | 0.018666 | 0.0186 | -0.0044519 | 0.062478 | -0.0063639 | 0.068261 | -121.6415 | 1.4511 | -121.8887 | -121.4859 | 1.3733 | -2.3758 | -0.23804 | 0.09613 | 1.4923 | -121.9162 | -0.24262 | -0.01831 | 0.004577 | 0.16022 | -0.09613 | -0.27008 | 0.022889 | 0.24719 | 121.4081 | 121.7422 | 123.0194 | 123.0972 | 0.004577 | 123.1384 | 119.2703 | -0.27008 | 123.0972 | 0.004577 | 119.2703 | 123.0194 | 123.1384 | -123.3582 | -123.3856
653.375 | 123.2025 | -121.6965 | 1.3641 | -0.0049592 | 0.018453 | 0.014755 | -0.0029565 | 0.062692 | -0.0029459 | 0.069329 | -121.6324 | 1.5656 | -121.8979 | -121.5363 | 1.3046 | -2.4811 | -0.21973 | -0.018311 | 1.4786 | -122.0078 | -0.20142 | 0.20142 | 0.064087 | 0.16022 | -0.05951 | -0.31128 | 0.11444 | 0.2655 | 121.4767 | 121.6782 | 123.0011 | 123.262 | 0.064087 | 123.175 | 119.2154 | -0.31128 | 123.262 | 0.064087 | 119.2154 | 123.0011 | 123.175 | -123.262 | -123.3719
655.0625 | 123.0972 | -122.5479 | 0.52643 | -0.0049592 | 0.019307 | 0.014114 | -0.0046655 | 0.062478 | -0.0031595 | 0.070184 | -122.4976 | 0.54932 | -122.7859 | -122.3557 | 0.48523 | -2.4673 | -0.24719 | 0.1236 | 0.60883 | -122.818 | -0.23804 | 0.022888 | 0.050354 | 0.19226 | -0.041199 | -0.27008 | 0.082398 | 0.28839 | 122.3007 | 122.6715 | 123.0331 | 123.0972 | 0.050354 | 123.1567 | 120.0806 | -0.27008 | 123.0972 | 0.050354 | 120.0806 | 123.0331 | 123.1567 | -123.3124 | -123.3444
656.8125 | 123.1979 | -122.5204 | 0.56305 | -0.0049592 | 0.016957 | 0.01326 | 3.4284e-05 | 0.062692 | -0.0076455 | 0.069329 | -122.5021 | 0.59509 | -122.85 | -122.3877 | 0.43945 | -2.5131 | -0.24719 | 0.032043 | 0.63629 | -122.7905 | -0.32959 | 0.032044 | 0.018311 | 0.13275 | -0.1236 | -0.27008 | 0.073243 | 0.3479 | 122.2733 | 122.5525 | 122.9599 | 123.1155 | 0.018311 | 123.1567 | 120.0073 | -0.27008 | 123.1155 | 0.018311 | 120.0073 | 122.9599 | 123.1567 | -123.4131 | -123.3536
658.5 | 123.1338 | -122.5616 | 0.54016 | 0.0026703 | 0.015462 | 0.016037 | -0.0012475 | 0.062051 | -0.0065775 | 0.068261 | -122.4838 | 0.55389 | -122.8317 | -122.3511 | 0.48981 | -2.4445 | -0.32501 | 0.10529 | 0.59052 | -122.7951 | -0.27008 | 0.013733 | 0.07782 | 0.21057 | -0.050354 | -0.23346 | 0.050354 | 0.3479 | 122.2366 | 122.6669 | 123.0515 | 123.1155 | 0.07782 | 123.1522 | 120.1172 | -0.23346 | 123.1155 | 0.07782 | 120.1172 | 123.0515 | 123.1522 | -123.3719 | -123.3353
660.25 | 123.0835 | -122.5662 | 0.54016 | -0.0049592 | 0.019734 | 0.016037 | -0.0059473 | 0.061624 | -0.0025187 | 0.069543 | -122.4701 | 0.52643 | -122.8226 | -122.319 | 0.52185 | -2.3941 | -0.24719 | 0.21973 | 0.5722 | -122.8729 | -0.25635 | -0.013733 | 0.09613 | 0.24719 | -0.01831 | -0.3067 | 0.032044 | 0.35248 | 122.319 | 122.7859 | 123.0881 | 123.0927 | 0.09613 | 123.1384 | 120.1721 | -0.3067 | 123.0927 | 0.09613 | 120.1721 | 123.0881 | 123.1384 | -123.3627 | -123.4131
662 | 123.0927 | -122.5891 | 0.53101 | -0.0049592 | 0.018239 | 0.01326 | -0.0044519 | 0.061197 | -0.0061503 | 0.06762 | -122.4747 | 0.53101 | -122.7997 | -122.3282 | 0.51727 | -2.4033 | -0.23346 | 0.22888 | 0.56305 | -122.8729 | -0.21057 | 0 | 0.11444 | 0.26093 | -0.013733 | -0.28381 | 0.032043 | 0.32501 | 122.3557 | 122.818 | 123.1064 | 123.1201 | 0.11444 | 123.1522 | 120.1859 | -0.28381 | 123.1201 | 0.11444 | 120.1859 | 123.1064 | 123.1522 | -123.3307 | -123.4039
663.6875 | 123.2712 | -122.5525 | 0.48065 | 0.0026703 | 0.019094 | 0.017105 | 0.0017431 | 0.063974 | -0.0080729 | 0.070184 | -122.6166 | 0.56305 | -122.9141 | -122.5113 | 0.35248 | -2.5772 | -0.13733 | 0.022888 | 0.58136 | -122.8821 | -0.36163 | 0.082397 | -0.064087 | 0.041198 | -0.12817 | -0.32959 | 0.10071 | 0.29755 | 122.4152 | 122.5754 | 122.905 | 123.1155 | -0.064087 | 123.1339 | 119.9753 | -0.32959 | 123.1155 | -0.064087 | 119.9753 | 122.905 | 123.1339 | -123.3948 | -123.3627
665.4219 | 123.1888 | -122.5525 | 0.52643 | 0.0026703 | 0.01888 | 0.014541 | 0.0021705 | 0.06376 | -0.0082865 | 0.071893 | -122.5204 | 0.56305 | -122.8775 | -122.4152 | 0.44861 | -2.4902 | -0.1236 | 0.12817 | 0.6134 | -122.8226 | -0.32501 | 0.036621 | 0.032043 | 0.13733 | -0.07782 | -0.27008 | 0.086975 | 0.35706 | 122.4289 | 122.6807 | 123.0011 | 123.1155 | 0.032043 | 123.1659 | 120.0623 | -0.27008 | 123.1155 | 0.032043 | 120.0623 | 123.0011 | 123.1659 | -123.4039 | -123.349
667.1875 | 123.2574 | -122.5296 | 0.52185 | 0.0103 | 0.018453 | 0.0186 | -0.00017952 | 0.06376 | -0.0089273 | 0.068688 | -122.5616 | 0.57678 | -122.8821 | -122.4564 | 0.40283 | -2.5864 | -0.09613 | 0.027466 | 0.62714 | -122.8317 | -0.35248 | 0.054931 | -0.032044 | 0.073242 | -0.11902 | -0.30212 | 0.10529 | 0.32043 | 122.4335 | 122.5571 | 122.9324 | 123.1064 | -0.032044 | 123.1567 | 119.9432 | -0.30212 | 123.1064 | -0.032044 | 119.9432 | 122.9324 | 123.1567 | -123.4039 | -123.3536
668.9219 | 123.1338 | -122.5708 | 0.5722 | -0.0049592 | 0.016317 | 0.011337 | -0.0046655 | 0.065469 | -0.0070047 | 0.070184 | -122.4838 | 0.51727 | -122.8363 | -122.3602 | 0.50812 | -2.504 | -0.3891 | 0.09613 | 0.56305 | -122.7722 | -0.2655 | -0.054932 | 0.086975 | 0.21057 | -0.064087 | -0.20142 | -0.009156 | 0.35248 | 122.1817 | 122.6669 | 123.0789 | 123.0881 | 0.086975 | 123.1339 | 120.0668 | -0.20142 | 123.0881 | 0.086975 | 120.0668 | 123.0789 | 123.1339 | -123.4085 | -123.3444
670.5938 | 123.1247 | -122.5983 | 0.54474 | -0.012589 | 0.019521 | 0.01326 | -0.0068017 | 0.063119 | -0.0076455 | 0.070397 | -122.3969 | 0.59052 | -122.7631 | -122.2778 | 0.59967 | -2.3758 | -0.21515 | 0.24719 | 0.61798 | -122.7722 | -0.16479 | 0.045776 | 0.20142 | 0.32044 | 0.054931 | -0.17395 | 0.073242 | 0.36621 | 122.3831 | 122.8455 | 123.1979 | 123.1888 | 0.20142 | 123.2162 | 120.2225 | -0.17395 | 123.1888 | 0.20142 | 120.2225 | 123.1979 | 123.2162 | -123.3078 | -123.317
672.3594 | 123.1567 | -122.4747 | 0.63171 | -0.0049592 | 0.01888 | 0.012192 | -0.0042383 | 0.062692 | -0.0046549 | 0.071252 | -122.4243 | 0.61798 | -122.7219 | -122.3282 | 0.56305 | -2.4994 | -0.28381 | 0.082397 | 0.68207 | -122.7722 | -0.24719 | -0.013733 | 0.050354 | 0.14648 | -0.068665 | -0.29755 | 0.050354 | 0.29755 | 122.1909 | 122.5571 | 123.0377 | 123.0927 | 0.050354 | 123.1567 | 119.9753 | -0.29755 | 123.0927 | 0.050354 | 119.9753 | 123.0377 | 123.1567 | -123.3536 | -123.4039
674.0469 | 123.2162 | -122.5937 | 0.50812 | -0.0049592 | 0.018239 | 0.016464 | 0.0023841 | 0.065469 | -0.0080729 | 0.070825 | -122.5571 | 0.52643 | -122.9141 | -122.4106 | 0.43945 | -2.5223 | -0.10986 | 0.16022 | 0.58136 | -122.8775 | -0.32044 | 0.01831 | 0.036621 | 0.18311 | -0.068665 | -0.28381 | 0.073242 | 0.35706 | 122.4838 | 122.7539 | 123.0331 | 123.1201 | 0.036621 | 123.175 | 120.0714 | -0.28381 | 123.1201 | 0.036621 | 120.0714 | 123.0331 | 123.175 | -123.4222 | -123.3856
675.7812 | 123.1293 | -122.525 | 0.61798 | -0.012589 | 0.018025 | 0.0098417 | -0.0029565 | 0.063119 | -0.0025187 | 0.070184 | -122.438 | 0.59967 | -122.7631 | -122.2961 | 0.58136 | -2.4445 | -0.27008 | 0.20599 | 0.60883 | -122.7951 | -0.23804 | -0.018311 | 0.086975 | 0.22888 | -0.036621 | -0.27008 | -0.009155 | 0.32501 | 122.2549 | 122.731 | 123.1064 | 123.1247 | 0.086975 | 123.1338 | 120.0806 | -0.27008 | 123.1247 | 0.086975 | 120.0806 | 123.1064 | 123.1338 | -123.381 | -123.4131
677.5469 | 123.2712 | -122.5067 | 0.54016 | -0.012589 | 0.015889 | 0.014114 | -0.0031701 | 0.063333 | -0.0091409 | 0.071679 | -122.5662 | 0.62256 | -122.8592 | -122.4197 | 0.4303 | -2.5726 | 0.004578 | 0.12817 | 0.66376 | -122.8271 | -0.35248 | 0.082398 | -0.059509 | 0.086975 | -0.10986 | -0.32043 | 0.1236 | 0.29297 | 122.5113 | 122.6349 | 122.937 | 123.1293 | -0.059509 | 123.1705 | 119.9341 | -0.32043 | 123.1293 | -0.059509 | 119.9341 | 122.937 | 123.1705 | -123.3994 | -123.3673
679.2969 | 123.2208 | -122.2412 | 0.87891 | -0.0049592 | 0.019948 | 0.012832 | 0.00024788 | 0.064615 | -0.0091409 | 0.071038 | -122.2092 | 0.87433 | -122.5662 | -122.0901 | 0.75531 | -2.5085 | -0.11444 | 0.14648 | 0.91095 | -122.5296 | -0.32501 | -0.004577 | 0.032044 | 0.15106 | -0.1236 | -0.28839 | 0.032044 | 0.35706 | 122.1268 | 122.3877 | 122.9965 | 123.1155 | 0.032044 | 123.1522 | 119.7327 | -0.28839 | 123.1155 | 0.032044 | 119.7327 | 122.9965 | 123.1522 | -123.4451 | -123.4085
681.0625 | 123.2529 | -122.2549 | 0.82855 | -0.0049592 | 0.01888 | 0.01091 | -0.0042383 | 0.062906 | -0.0046549 | 0.070397 | -122.3099 | 0.8606 | -122.5754 | -122.1771 | 0.68665 | -2.5543 | 0.004578 | 0.1236 | 0.91553 | -122.5937 | -0.32043 | 0.032044 | -0.054931 | 0.07782 | -0.14191 | -0.33875 | 0.086975 | 0.2655 | 122.2595 | 122.3785 | 122.9416 | 123.1155 | -0.054931 | 123.1705 | 119.7006 | -0.33875 | 123.1155 | -0.054931 | 119.7006 | 122.9416 | 123.1705 | -123.4039 | -123.4222
682.8125 | 123.1064 | -122.0764 | 1.03 | -0.0049592 | 0.016744 | 0.013473 | -0.0065881 | 0.06141 | -0.0038003 | 0.068048 | -122.0123 | 1.0162 | -122.3785 | -121.8796 | 0.98877 | -2.4765 | -0.22888 | 0.24719 | 1.0208 | -122.3831 | -0.30212 | -0.013733 | 0.064087 | 0.19684 | -0.041198 | -0.3067 | -0.009155 | 0.36621 | 121.8475 | 122.3236 | 123.0652 | 123.0927 | 0.064087 | 123.0972 | 119.5999 | -0.3067 | 123.0927 | 0.064087 | 119.5999 | 123.0652 | 123.0972 | -123.4085 | -123.4131
684.5 | 123.1293 | -120.8679 | 2.243 | 0.0026703 | 0.018666 | 0.010483 | -0.0053063 | 0.062265 | -0.0044413 | 0.070611 | -120.8633 | 2.2385 | -121.2067 | -120.7077 | 2.1606 | -2.3575 | -0.27466 | 0.21515 | 2.1881 | -121.1838 | -0.33875 | -0.004578 | 0.004578 | 0.16022 | -0.082397 | -0.31586 | -0.054932 | 0.34332 | 120.5933 | 121.0831 | 123.0286 | 123.1064 | 0.004578 | 123.056 | 118.5104 | -0.31586 | 123.1064 | 0.004578 | 118.5104 | 123.0286 | 123.056 | -123.4497 | -123.4268
686.2344 | 123.2162 | -122.2321 | 0.86975 | -0.020218 | 0.01888 | 0.019882 | 0.0011023 | 0.06376 | -0.0070047 | 0.071466 | -122.2046 | 0.87433 | -122.5525 | -122.0993 | 0.75073 | -2.5497 | -0.1236 | 0.1236 | 0.92926 | -122.4838 | -0.32043 | 0.004578 | 0.027466 | 0.13275 | -0.11902 | -0.25177 | 0.059509 | 0.3479 | 122.1085 | 122.3557 | 122.9828 | 123.1064 | 0.027466 | 123.1613 | 119.6823 | -0.25177 | 123.1064 | 0.027466 | 119.6823 | 122.9828 | 123.1613 | -123.4222 | -123.3536
687.9844 | 123.2254 | -122.2641 | 0.81024 | -0.0049592 | 0.01653 | 0.013473 | 0.00046148 | 0.065469 | -0.0095681 | 0.06997 | -122.2595 | 0.83313 | -122.5983 | -122.1359 | 0.70038 | -2.5269 | -0.073242 | 0.16937 | 0.89264 | -122.5708 | -0.33417 | 0.022888 | 0.004578 | 0.12817 | -0.10986 | -0.3067 | 0.082397 | 0.33875 | 122.1909 | 122.4335 | 122.9645 | 123.0972 | 0.004578 | 123.1567 | 119.7372 | -0.3067 | 123.0972 | 0.004578 | 119.7372 | 122.9645 | 123.1567 | -123.4085 | -123.381
689.6562 | 123.2346 | -122.3511 | 0.74616 | 0.0026703 | 0.018666 | 0.013473 | -0.0012475 | 0.064401 | -0.0080729 | 0.071466 | -122.3785 | 0.79651 | -122.6715 | -122.2549 | 0.60425 | -2.6276 | -0.22888 | 0.013733 | 0.80566 | -122.6532 | -0.32044 | 0.050354 | -0.027466 | 0.09613 | -0.14191 | -0.30212 | 0.059509 | 0.29297 | 122.1222 | 122.3648 | 122.9553 | 123.1476 | -0.027466 | 123.1567 | 119.7235 | -0.30212 | 123.1476 | -0.027466 | 119.7235 | 122.9553 | 123.1567 | -123.4177 | -123.3994
691.4062 | 123.1247 | -121.8018 | 1.3367 | -0.0049592 | 0.017598 | 0.015823 | -0.0063745 | 0.059701 | -0.0035867 | 0.06997 | -121.701 | 1.3184 | -122.0078 | -121.5729 | 1.3138 | -2.4307 | -0.25177 | 0.2243 | 1.3458 | -122.0856 | -0.20599 | -0.018311 | 0.10071 | 0.22888 | -0.022888 | -0.28381 | 0.009155 | 0.3067 | 121.55 | 122.0261 | 123.1155 | 123.1201 | 0.10071 | 123.1476 | 119.371 | -0.28381 | 123.1201 | 0.10071 | 119.371 | 123.1155 | 123.1476 | -123.3444 | -123.4222
693.1094 | 123.2391 | -120.4468 | 2.5864 | -0.0049592 | 0.018453 | 0.012832 | -0.0035973 | 0.063547 | -0.0044413 | 0.06997 | -120.2957 | 2.9984 | -120.575 | -120.1584 | 2.655 | -2.4307 | -0.082397 | 0.036621 | 2.861 | -120.5887 | -0.12817 | 0.41199 | 0.15106 | 0.28839 | 0.068664 | -0.14191 | 0.27466 | 0.27924 | 120.3644 | 120.4834 | 123.1018 | 123.4451 | 0.15106 | 123.3078 | 118.0161 | -0.14191 | 123.4451 | 0.15106 | 118.0161 | 123.1018 | 123.3078 | -123.1613 | -123.175
694.8438 | 123.1796 | -121.7056 | 1.3962 | 0.0026703 | 0.018239 | 0.015396 | -0.0063745 | 0.062051 | -0.0065775 | 0.071252 | -121.6736 | 1.387 | -121.9711 | -121.5683 | 1.3046 | -2.5085 | -0.23346 | 0.09613 | 1.4374 | -122.0032 | -0.2655 | -0.009155 | 0.032043 | 0.13733 | -0.091553 | -0.29755 | 0.041199 | 0.29755 | 121.4722 | 121.8018 | 123.0103 | 123.0927 | 0.032043 | 123.143 | 119.1971 | -0.29755 | 123.0927 | 0.032043 | 119.1971 | 123.0103 | 123.143 | -123.3673 | -123.3994
696.5938 | 123.1155 | -120.9366 | 2.1835 | -0.0049592 | 0.019521 | 0.0098417 | -0.0050927 | 0.060983 | -0.0052957 | 0.070397 | -120.845 | 2.1835 | -121.1655 | -120.7077 | 2.1744 | -2.3941 | -0.25635 | 0.24261 | 2.211 | -121.17 | -0.22888 | 0 | 0.091552 | 0.22888 | -0.009156 | -0.23346 | 0.027466 | 0.32043 | 120.6802 | 121.1792 | 123.111 | 123.1201 | 0.091552 | 123.1476 | 118.5425 | -0.23346 | 123.1201 | 0.091552 | 118.5425 | 123.111 | 123.1476 | -123.349 | -123.3536
698.3594 | 123.1384 | -121.994 | 1.1398 | -0.012589 | 0.015676 | 0.010696 | -0.0027429 | 0.061838 | -0.0042277 | 0.068688 | -121.8796 | 1.1444 | -122.2412 | -121.756 | 1.0849 | -2.4994 | -0.16022 | 0.25177 | 1.1902 | -122.2504 | -0.24719 | 0.004577 | 0.11444 | 0.23804 | -0.054932 | -0.25635 | 0.050354 | 0.36163 | 121.8338 | 122.2458 | 123.0789 | 123.1384 | 0.11444 | 123.1842 | 119.4946 | -0.25635 | 123.1384 | 0.11444 | 119.4946 | 123.0789 | 123.1842 | -123.381 | -123.3902
700.0625 | 123.2071 | -122.1313 | 0.90637 | -0.0049592 | 0.019948 | 0.015182 | 0.0013159 | 0.062692 | -0.0080729 | 0.070825 | -122.1268 | 0.96588 | -122.4792 | -122.0032 | 0.83771 | -2.5726 | -0.068665 | 0.16022 | 1.0117 | -122.4518 | -0.3479 | 0.059509 | 0.004578 | 0.12817 | -0.068664 | -0.32043 | 0.10529 | 0.35248 | 122.0627 | 122.2916 | 122.9691 | 123.0972 | 0.004578 | 123.143 | 119.5587 | -0.32043 | 123.0972 | 0.004578 | 119.5587 | 122.9691 | 123.143 | -123.3856 | -123.3582
701.7969 | 123.1796 | -122.1817 | 0.90637 | 0.0026703 | 0.015676 | 0.012192 | -0.0046655 | 0.065896 | -0.0046549 | 0.069757 | -122.1542 | 0.94299 | -122.4243 | -122.0352 | 0.83771 | -2.5955 | -0.23804 | 0.10071 | 0.9613 | -122.4564 | -0.24261 | 0.036621 | 0.027466 | 0.14648 | -0.068664 | -0.27466 | 0.054932 | 0.27008 | 121.9437 | 122.2824 | 123.0194 | 123.1247 | 0.027466 | 123.143 | 119.5862 | -0.27466 | 123.1247 | 0.027466 | 119.5862 | 123.0194 | 123.143 | -123.3307 | -123.3627
703.5469 | 123.1293 | -122.3465 | 0.80566 | -0.012589 | 0.014821 | 0.019882 | -0.0038111 | 0.064187 | -0.0038003 | 0.067407 | -122.2229 | 0.7782 | -122.5754 | -122.1085 | 0.75073 | -2.5726 | -0.36163 | 0.11444 | 0.80109 | -122.5616 | -0.22888 | -0.027466 | 0.1236 | 0.23804 | -0.054932 | -0.21515 | -0.004578 | 0.35248 | 121.9849 | 122.4609 | 123.0972 | 123.1247 | 0.1236 | 123.1476 | 119.7739 | -0.21515 | 123.1247 | 0.1236 | 119.7739 | 123.0972 | 123.1476 | -123.381 | -123.3673
705.2969 | 123.2712 | -122.0764 | 0.97504 | 0.0103 | 0.01888 | 0.014755 | 3.4284e-05 | 0.063974 | -0.0059365 | 0.071038 | -122.1313 | 1.0345 | -122.4152 | -122.0261 | 0.83313 | -2.6825 | -0.12817 | 0.022888 | 1.0574 | -122.3831 | -0.33875 | 0.059509 | -0.054932 | 0.050354 | -0.14191 | -0.3067 | 0.082397 | 0.28381 | 121.9482 | 122.0993 | 122.9095 | 123.111 | -0.054932 | 123.1338 | 119.3939 | -0.3067 | 123.111 | -0.054932 | 119.3939 | 122.9095 | 123.1338 | -123.3902 | -123.3582
707.0469 | 123.2666 | -121.9025 | 1.149 | -0.0049592 | 0.019948 | 0.013473 | 0.00024788 | 0.062265 | -0.0042277 | 0.072534 | -121.9391 | 1.2177 | -122.2137 | -121.8292 | 1.0208 | -2.6825 | -0.14191 | 0 | 1.2543 | -122.2137 | -0.31128 | 0.068664 | -0.036621 | 0.073242 | -0.12817 | -0.31128 | 0.10529 | 0.27466 | 121.7606 | 121.9025 | 122.9233 | 123.1201 | -0.036621 | 123.1567 | 119.22 | -0.31128 | 123.1201 | -0.036621 | 119.22 | 122.9233 | 123.1567 | -123.3627 | -123.3627
708.7812 | 123.1659 | -121.7789 | 1.3092 | 0.0026703 | 0.015035 | 0.013046 | -0.0046655 | 0.063333 | -0.0055093 | 0.070611 | -121.7651 | 1.3092 | -122.0306 | -121.6461 | 1.2131 | -2.5955 | -0.24261 | 0.082397 | 1.355 | -122.0718 | -0.25177 | 0 | 0.013733 | 0.13275 | -0.09613 | -0.29297 | 0.045776 | 0.2655 | 121.5363 | 121.8613 | 122.9919 | 123.0881 | 0.013733 | 123.1338 | 119.1834 | -0.29297 | 123.0881 | 0.013733 | 119.1834 | 122.9919 | 123.1338 | -123.3398 | -123.381
710.4688 | 123.1567 | -121.2479 | 1.8723 | -0.0049592 | 0.015248 | 0.011764 | -0.0038111 | 0.060769 | -0.0055093 | 0.069116 | -121.2021 | 1.8036 | -121.5546 | -121.1197 | 1.7212 | -2.5909 | -0.31586 | 0.07782 | 1.8494 | -121.5546 | -0.3067 | -0.068664 | 0.045777 | 0.12817 | -0.15106 | -0.3067 | -0.022888 | 0.35248 | 120.932 | 121.3257 | 122.9691 | 123.0515 | 0.045777 | 123.0972 | 118.6569 | -0.3067 | 123.0515 | 0.045777 | 118.6569 | 122.9691 | 123.0972 | -123.4268 | -123.4268
712.2188 | 123.1842 | -121.6736 | 1.4008 | -0.0049592 | 0.019094 | 0.013901 | 0.00067508 | 0.062478 | -0.0080729 | 0.070611 | -121.5042 | 1.5747 | -121.8521 | -121.3806 | 1.4603 | -2.5864 | -0.1236 | 0.16022 | 1.6159 | -121.8018 | -0.17853 | 0.17395 | 0.16937 | 0.29297 | 0.059509 | -0.12817 | 0.21515 | 0.3479 | 121.55 | 121.8338 | 123.1339 | 123.2483 | 0.16937 | 123.2895 | 119.0872 | -0.12817 | 123.2483 | 0.16937 | 119.0872 | 123.1339 | 123.2895 | -123.2529 | -123.2025
713.9688 | 123.1476 | -121.582 | 1.5244 | 0.0103 | 0.017171 | 0.012192 | -0.0072289 | 0.062692 | -0.0055093 | 0.069543 | -121.4767 | 1.5656 | -121.7972 | -121.3486 | 1.5152 | -2.5223 | -0.25635 | 0.17853 | 1.593 | -121.8155 | -0.21515 | 0.041199 | 0.10528 | 0.23346 | -0.009155 | -0.23346 | 0.068665 | 0.32043 | 121.3257 | 121.7606 | 123.0972 | 123.1476 | 0.10528 | 123.175 | 119.0598 | -0.23346 | 123.1476 | 0.10528 | 119.0598 | 123.0972 | 123.175 | -123.3215 | -123.3398
715.6406 | 123.2208 | -121.8109 | 1.2177 | 0.0026703 | 0.018025 | 0.0096279 | -0.00017952 | 0.06141 | -0.0065775 | 0.070397 | -121.8338 | 1.3 | -122.1542 | -121.6965 | 1.1261 | -2.5406 | 0.018311 | 0.20599 | 1.3367 | -122.1359 | -0.34332 | 0.082398 | -0.022888 | 0.11444 | -0.091552 | -0.32501 | 0.11902 | 0.32044 | 121.8292 | 122.0169 | 122.937 | 123.111 | -0.022888 | 123.1476 | 119.2703 | -0.32501 | 123.111 | -0.022888 | 119.2703 | 122.937 | 123.1476 | -123.3719 | -123.3536
717.3906 | 123.1338 | -121.7697 | 1.3321 | -0.0049592 | 0.018025 | 0.0079189 | -0.0040247 | 0.062906 | -0.0057229 | 0.07232 | -121.6782 | 1.3275 | -122.0215 | -121.5637 | 1.2772 | -2.5269 | -0.14191 | 0.21973 | 1.3596 | -122.0352 | -0.25177 | -0.004577 | 0.091552 | 0.20599 | -0.054931 | -0.2655 | 0.027466 | 0.34332 | 121.6278 | 121.9894 | 123.0469 | 123.0972 | 0.091552 | 123.1293 | 119.2429 | -0.2655 | 123.0972 | 0.091552 | 119.2429 | 123.0469 | 123.1293 | -123.3536 | -123.3673
719.0781 | 123.1979 | -121.9116 | 1.1215 | 0.0026703 | 0.018025 | 0.013687 | -0.0021021 | 0.062692 | -0.0029459 | 0.071038 | -121.9254 | 1.1856 | -122.2412 | -121.8155 | 1.0208 | -2.623 | -0.050354 | 0.14191 | 1.2222 | -122.2549 | -0.32959 | 0.064087 | -0.013733 | 0.09613 | -0.10071 | -0.34332 | 0.10071 | 0.31586 | 121.8613 | 122.0535 | 122.9324 | 123.0972 | -0.013733 | 123.1338 | 119.2886 | -0.34332 | 123.0972 | -0.013733 | 119.2886 | 122.9324 | 123.1338 | -123.3627 | -123.3765
720.8125 | 123.1842 | -121.9986 | 1.0483 | 0.0026703 | 0.017598 | 0.014328 | -0.0027429 | 0.061197 | -0.0038003 | 0.069543 | -121.9803 | 1.0849 | -122.3328 | -121.8842 | 0.94757 | -2.6184 | -0.036621 | 0.16022 | 1.1444 | -122.3419 | -0.33417 | 0.036621 | 0.01831 | 0.11444 | -0.10071 | -0.34332 | 0.09613 | 0.35248 | 121.962 | 122.1588 | 122.9462 | 123.0835 | 0.01831 | 123.143 | 119.3802 | -0.34332 | 123.0835 | 0.01831 | 119.3802 | 122.9462 | 123.143 | -123.381 | -123.3902
722.5 | 123.1201 | -121.9482 | 1.149 | -0.012589 | 0.013753 | 0.015823 | -0.0035973 | 0.062692 | -0.0065775 | 0.068688 | -121.875 | 1.1398 | -122.2137 | -121.7377 | 1.0986 | -2.6138 | -0.36163 | 0.12817 | 1.1856 | -122.2046 | -0.2655 | -0.009155 | 0.073242 | 0.21057 | -0.050354 | -0.25635 | 0.036621 | 0.33875 | 121.5866 | 122.0764 | 123.0469 | 123.0881 | 0.073242 | 123.1338 | 119.3344 | -0.25635 | 123.0881 | 0.073242 | 119.3344 | 123.0469 | 123.1338 | -123.3627 | -123.3536
724.2656 | 123.1201 | -121.9025 | 1.2131 | -0.0049592 | 0.020589 | 0.013046 | -0.0044519 | 0.063974 | -0.0033731 | 0.070825 | -121.8063 | 1.2131 | -122.1313 | -121.7148 | 1.1444 | -2.6276 | -0.33875 | 0.10529 | 1.2314 | -122.1817 | -0.22888 | 0 | 0.096131 | 0.18768 | -0.068665 | -0.27924 | 0.01831 | 0.32501 | 121.5637 | 122.0078 | 123.0469 | 123.1155 | 0.096131 | 123.1339 | 119.2749 | -0.27924 | 123.1155 | 0.096131 | 119.2749 | 123.0469 | 123.1339 | -123.3444 | -123.3948
725.9531 | 123.2346 | -122.3053 | 0.74616 | -0.0049592 | 0.020589 | 0.01326 | 0.00088868 | 0.064615 | -0.0059365 | 0.069757 | -122.3373 | 0.81482 | -122.6303 | -122.2321 | 0.58594 | -2.7695 | -0.14648 | 0.013733 | 0.85144 | -122.6028 | -0.32501 | 0.068664 | -0.032043 | 0.073242 | -0.16022 | -0.29755 | 0.10528 | 0.29297 | 122.1588 | 122.319 | 122.8912 | 123.1201 | -0.032043 | 123.1567 | 119.5358 | -0.29755 | 123.1201 | -0.032043 | 119.5358 | 122.8912 | 123.1567 | -123.3765 | -123.349
727.6875 | 123.2162 | -122.3373 | 0.70496 | -0.0049592 | 0.018025 | 0.013687 | -0.00017952 | 0.063974 | -0.0072183 | 0.068902 | -122.3694 | 0.77362 | -122.7127 | -122.2504 | 0.59509 | -2.6962 | -0.027466 | 0.12817 | 0.8194 | -122.6761 | -0.37537 | 0.068665 | -0.032044 | 0.086975 | -0.10986 | -0.33875 | 0.11444 | 0.34332 | 122.3099 | 122.4655 | 122.9324 | 123.111 | -0.032044 | 123.1567 | 119.6411 | -0.33875 | 123.111 | -0.032044 | 119.6411 | 122.9324 | 123.1567 | -123.4177 | -123.381
729.4531 | 123.1796 | -122.2916 | 0.75989 | -0.0049592 | 0.019948 | 0.013687 | 0.00046148 | 0.062692 | -0.0061503 | 0.070825 | -122.1405 | 0.92926 | -122.4976 | -122.0398 | 0.75531 | -2.7283 | -0.16479 | 0.068665 | 0.95215 | -122.5388 | -0.20599 | 0.16937 | 0.15106 | 0.25177 | -0.004578 | -0.24719 | 0.19226 | 0.35706 | 122.1268 | 122.3602 | 123.0469 | 123.2208 | 0.15106 | 123.2437 | 119.5633 | -0.24719 | 123.2208 | 0.15106 | 119.5633 | 123.0469 | 123.2437 | -123.2574 | -123.2986
731.1875 | 123.2254 | -122.113 | 0.89264 | 0.0026703 | 0.019521 | 0.015182 | -0.0061609 | 0.06376 | -0.0040139 | 0.068261 | -122.1634 | 0.97504 | -122.4655 | -122.0535 | 0.79193 | -2.6917 | 0 | 0.13275 | 1.0025 | -122.4792 | -0.35248 | 0.082398 | -0.050354 | 0.059509 | -0.10071 | -0.36621 | 0.10986 | 0.30212 | 122.113 | 122.2458 | 122.905 | 123.0881 | -0.050354 | 123.1155 | 119.4214 | -0.36621 | 123.0881 | -0.050354 | 119.4214 | 122.905 | 123.1155 | -123.3582 | -123.3719
732.875 | 123.23 | -122.0993 | 0.90637 | 0.0103 | 0.018025 | 0.013901 | -0.0016747 | 0.06376 | -0.0033731 | 0.071466 | -122.1588 | 0.97504 | -122.438 | -122.0673 | 0.78735 | -2.7649 | -0.10986 | 0.018311 | 1.0208 | -122.4518 | -0.33875 | 0.068665 | -0.059509 | 0.032043 | -0.11902 | -0.35248 | 0.11444 | 0.27924 | 121.9894 | 122.1176 | 122.8867 | 123.0743 | -0.059509 | 123.1201 | 119.3344 | -0.35248 | 123.0743 | -0.059509 | 119.3344 | 122.8867 | 123.1201 | -123.3444 | -123.3582
734.625 | 123.0927 | -122.2549 | 0.84686 | -0.0049592 | 0.016957 | 0.014969 | -0.0072289 | 0.063547 | -0.0031595 | 0.070397 | -122.1634 | 0.83771 | -122.4609 | -122.049 | 0.81024 | -2.6047 | -0.26093 | 0.21515 | 0.87433 | -122.5204 | -0.20599 | -0.009155 | 0.091553 | 0.20599 | -0.036621 | -0.2655 | 0.027466 | 0.29755 | 121.994 | 122.4701 | 123.0652 | 123.0927 | 0.091553 | 123.1293 | 119.6503 | -0.2655 | 123.0927 | 0.091553 | 119.6503 | 123.0652 | 123.1293 | -123.3078 | -123.3673
736.375 | 123.1018 | -122.2321 | 0.87433 | -0.0049592 | 0.018239 | 0.017105 | -0.0042383 | 0.062478 | -0.0067911 | 0.06997 | -122.1542 | 0.84686 | -122.4792 | -122.0352 | 0.81482 | -2.6733 | -0.34332 | 0.10071 | 0.91095 | -122.4655 | -0.24719 | -0.027466 | 0.07782 | 0.19684 | -0.05951 | -0.23346 | 0.036621 | 0.32501 | 121.8887 | 122.3328 | 123.0469 | 123.0789 | 0.07782 | 123.143 | 119.5587 | -0.23346 | 123.0789 | 0.07782 | 119.5587 | 123.0469 | 123.143 | -123.3536 | -123.3398
738.0625 | 123.0972 | -122.2229 | 0.86975 | -0.0049592 | 0.016103 | 0.013901 | -0.0065881 | 0.060556 | -0.0065775 | 0.070397 | -122.1405 | 0.84228 | -122.5021 | -122.0215 | 0.83313 | -2.6138 | -0.23804 | 0.2655 | 0.87891 | -122.4426 | -0.27924 | -0.027466 | 0.082397 | 0.20142 | -0.036621 | -0.21973 | 0.009155 | 0.36163 | 121.9849 | 122.4884 | 123.056 | 123.0652 | 0.082397 | 123.1018 | 119.6091 | -0.21973 | 123.0652 | 0.082397 | 119.6091 | 123.056 | 123.1018 | -123.3719 | -123.3124
739.8125 | 123.1155 | -122.2733 | 0.83313 | -0.0049592 | 0.017385 | 0.016891 | -0.0010339 | 0.062906 | -0.0055093 | 0.069757 | -122.1725 | 0.82855 | -122.5113 | -122.049 | 0.77362 | -2.6779 | -0.35706 | 0.10529 | 0.83313 | -122.5433 | -0.23804 | -0.004578 | 0.10071 | 0.2243 | -0.059509 | -0.27008 | 0 | 0.33875 | 121.9162 | 122.3785 | 123.0469 | 123.1018 | 0.10071 | 123.1064 | 119.5953 | -0.27008 | 123.1018 | 0.10071 | 119.5953 | 123.0469 | 123.1064 | -123.3444 | -123.3765
741.5156 | 123.1018 | -122.3282 | 0.79193 | -0.020218 | 0.01888 | 0.014328 | -0.0018885 | 0.063974 | -0.0057229 | 0.070397 | -122.2275 | 0.77362 | -122.5479 | -122.1222 | 0.71411 | -2.7008 | -0.32959 | 0.09613 | 0.80566 | -122.5754 | -0.21973 | -0.01831 | 0.10071 | 0.20599 | -0.07782 | -0.24719 | 0.013733 | 0.32043 | 121.9986 | 122.4243 | 123.0423 | 123.1018 | 0.10071 | 123.1338 | 119.6274 | -0.24719 | 123.1018 | 0.10071 | 119.6274 | 123.0423 | 123.1338 | -123.3398 | -123.3673
743.2812 | 123.1796 | -122.3465 | 0.6958 | 0.0026703 | 0.020162 | 0.018814 | 0.00067508 | 0.063119 | -0.0080729 | 0.069543 | -122.3373 | 0.74158 | -122.6715 | -122.2046 | 0.59052 | -2.7237 | -0.082397 | 0.15106 | 0.75989 | -122.6578 | -0.32501 | 0.045776 | 0.009156 | 0.14191 | -0.10529 | -0.31128 | 0.064087 | 0.33417 | 122.2641 | 122.4976 | 122.937 | 123.0881 | 0.009156 | 123.1064 | 119.6228 | -0.31128 | 123.0881 | 0.009156 | 119.6228 | 122.937 | 123.1064 | -123.3673 | -123.3536
745.0781 | 123.1842 | -122.3145 | 0.71869 | -0.0049592 | 0.018025 | 0.011978 | -0.0023157 | 0.059915 | -0.0044413 | 0.068261 | -122.3236 | 0.76904 | -122.612 | -122.2046 | 0.61798 | -2.7283 | -0.064087 | 0.12817 | 0.81482 | -122.6349 | -0.29755 | 0.050354 | -0.009155 | 0.10986 | -0.10071 | -0.32044 | 0.09613 | 0.28839 | 122.2504 | 122.4426 | 122.9324 | 123.0835 | -0.009155 | 123.1293 | 119.5862 | -0.32044 | 123.0835 | -0.009155 | 119.5862 | 122.9324 | 123.1293 | -123.3307 | -123.3536
746.8281 | 123.1247 | -122.3145 | 0.76446 | -0.0049592 | 0.020589 | 0.014755 | -0.0023157 | 0.060342 | -0.0042277 | 0.069757 | -122.2595 | 0.77362 | -122.5983 | -122.1588 | 0.68207 | -2.6871 | -0.086975 | 0.18768 | 0.82855 | -122.612 | -0.28381 | 0.009156 | 0.054932 | 0.15564 | -0.082397 | -0.29755 | 0.064087 | 0.33875 | 122.2275 | 122.5021 | 122.9965 | 123.0881 | 0.054932 | 123.143 | 119.6274 | -0.29755 | 123.0881 | 0.054932 | 119.6274 | 122.9965 | 123.143 | -123.3627 | -123.3765
748.5938 | 123.1384 | -122.2687 | 0.80109 | -0.0049592 | 0.019307 | 0.013687 | -0.0046655 | 0.060983 | -0.0035867 | 0.070184 | -122.2366 | 0.82855 | -122.5433 | -122.1268 | 0.70953 | -2.7283 | -0.24719 | 0.086975 | 0.85144 | -122.5662 | -0.27466 | 0.027466 | 0.032044 | 0.14191 | -0.091552 | -0.29755 | 0.050354 | 0.3067 | 122.0215 | 122.3557 | 122.9782 | 123.0972 | 0.032044 | 123.1201 | 119.5404 | -0.29755 | 123.0972 | 0.032044 | 119.5404 | 122.9782 | 123.1201 | -123.3444 | -123.3673
750.2812 | 123.0835 | -122.3419 | 0.75073 | 0.0026703 | 0.018025 | 0.010269 | -0.0018885 | 0.061838 | -0.0050821 | 0.068475 | -122.2137 | 0.75073 | -122.5845 | -122.0901 | 0.72327 | -2.71 | -0.36163 | 0.1236 | 0.77362 | -122.6028 | -0.24262 | 0 | 0.12817 | 0.25177 | -0.027465 | -0.26093 | 0.022889 | 0.37079 | 121.9803 | 122.4655 | 123.0652 | 123.0927 | 0.12817 | 123.1155 | 119.632 | -0.26093 | 123.0927 | 0.12817 | 119.632 | 123.0652 | 123.1155 | -123.3353 | -123.3536
752.0312 | 123.0698 | -122.2549 | 0.85602 | -0.012589 | 0.018239 | 0.017532 | -0.0055199 | 0.062906 | -0.0035867 | 0.069543 | -122.1176 | 0.81482 | -122.4976 | -122.0078 | 0.82398 | -2.623 | -0.25635 | 0.24719 | 0.87433 | -122.5479 | -0.24262 | -0.041199 | 0.13733 | 0.24719 | -0.032043 | -0.29297 | 0.018311 | 0.37994 | 121.9986 | 122.5021 | 123.0789 | 123.0698 | 0.13733 | 123.1293 | 119.632 | -0.29297 | 123.0698 | 0.13733 | 119.632 | 123.0789 | 123.1293 | -123.3536 | -123.4039
753.7812 | 123.1064 | -121.9574 | 1.1078 | -0.0049592 | 0.017385 | 0.012192 | -0.0029565 | 0.062265 | -0.0029459 | 0.069543 | -121.907 | 1.0986 | -122.2412 | -121.788 | 1.0529 | -2.6505 | -0.24261 | 0.16479 | 1.1444 | -122.2641 | -0.28381 | -0.009155 | 0.050354 | 0.16937 | -0.054932 | -0.3067 | 0.036621 | 0.33417 | 121.7148 | 122.1222 | 123.0103 | 123.056 | 0.050354 | 123.1018 | 119.3069 | -0.3067 | 123.056 | 0.050354 | 119.3069 | 123.0103 | 123.1018 | -123.349 | -123.3719
755.4688 | 123.1201 | -122.1863 | 0.88806 | 0.0026703 | 0.018666 | 0.017532 | -0.0021021 | 0.062051 | -0.0044413 | 0.070825 | -122.1405 | 0.87891 | -122.4701 | -122.0261 | 0.79193 | -2.7557 | -0.27008 | 0.064087 | 0.91095 | -122.4976 | -0.28381 | -0.009156 | 0.045776 | 0.16022 | -0.096131 | -0.31128 | 0.022888 | 0.32959 | 121.9162 | 122.2504 | 122.9782 | 123.0652 | 0.045776 | 123.0972 | 119.4305 | -0.31128 | 123.0652 | 0.045776 | 119.4305 | 122.9782 | 123.0972 | -123.3582 | -123.3856
757.1719 | 123.1201 | -122.1725 | 0.94299 | 0.0026703 | 0.016317 | 0.013046 | -0.00082032 | 0.062265 | -0.0031595 | 0.070397 | -122.0673 | 0.9201 | -122.4426 | -121.9757 | 0.84228 | -2.7374 | -0.33417 | 0.10071 | 0.94757 | -122.4243 | -0.27008 | -0.022888 | 0.10528 | 0.19684 | -0.10071 | -0.25177 | 0.004578 | 0.37537 | 121.8384 | 122.2733 | 123.0148 | 123.0927 | 0.10528 | 123.1201 | 119.4351 | -0.25177 | 123.0927 | 0.10528 | 119.4351 | 123.0148 | 123.1201 | -123.3856 | -123.3673
758.9219 | 123.0743 | -122.168 | 0.93384 | -0.012589 | 0.020162 | 0.01326 | 0.0015295 | 0.063547 | -0.0067911 | 0.069329 | -122.0718 | 0.91095 | -122.4197 | -121.9437 | 0.88348 | -2.7191 | -0.36621 | 0.11444 | 0.94757 | -122.406 | -0.25177 | -0.022888 | 0.096131 | 0.2243 | -0.050354 | -0.23804 | 0.013733 | 0.3479 | 121.8018 | 122.2824 | 123.0515 | 123.0789 | 0.096131 | 123.1155 | 119.4489 | -0.23804 | 123.0789 | 0.096131 | 119.4489 | 123.0515 | 123.1155 | -123.3536 | -123.3398
760.6719 | 123.1522 | -122.1634 | 0.86517 | -0.012589 | 0.017171 | 0.012832 | 0.00024788 | 0.062051 | -0.0091409 | 0.071038 | -122.1268 | 0.89264 | -122.5113 | -122.0398 | 0.7782 | -2.742 | -0.14191 | 0.15106 | 0.93842 | -122.4884 | -0.3479 | 0.027466 | 0.036621 | 0.1236 | -0.086975 | -0.32501 | 0.073243 | 0.38452 | 122.0215 | 122.3145 | 122.9416 | 123.056 | 0.036621 | 123.1018 | 119.4214 | -0.32501 | 123.056 | 0.036621 | 119.4214 | 122.9416 | 123.1018 | -123.3765 | -123.3536
762.3594 | 123.0881 | -122.2412 | 0.83771 | -0.0049592 | 0.016744 | 0.010696 | -0.0048791 | 0.060769 | -0.0065775 | 0.069116 | -122.1542 | 0.81482 | -122.5204 | -122.0261 | 0.79651 | -2.6825 | -0.15564 | 0.21515 | 0.86975 | -122.5479 | -0.27924 | -0.022889 | 0.086975 | 0.21515 | -0.041199 | -0.3067 | 0.032043 | 0.36621 | 122.0856 | 122.4564 | 123.0377 | 123.056 | 0.086975 | 123.111 | 119.5587 | -0.3067 | 123.056 | 0.086975 | 119.5587 | 123.0377 | 123.111 | -123.3582 | -123.3856
764.1094 | 123.1155 | -122.2778 | 0.81482 | 0.0103 | 0.017598 | 0.014541 | -0.0042383 | 0.063333 | -0.0063639 | 0.072534 | -122.2137 | 0.79651 | -122.5342 | -122.0993 | 0.72784 | -2.7603 | -0.29755 | 0.082397 | 0.84228 | -122.5342 | -0.25635 | -0.01831 | 0.064087 | 0.17853 | -0.086975 | -0.25635 | 0.027466 | 0.32044 | 121.9803 | 122.3602 | 123.0057 | 123.0743 | 0.064087 | 123.1201 | 119.5175 | -0.25635 | 123.0743 | 0.064087 | 119.5175 | 123.0057 | 123.1201 | -123.349 | -123.349
765.7812 | 123.1293 | -122.2687 | 0.80109 | -0.012589 | 0.017385 | 0.011123 | -0.0050927 | 0.061838 | -0.0035867 | 0.069329 | -122.2366 | 0.79651 | -122.5159 | -122.1268 | 0.71411 | -2.774 | -0.27466 | 0.082397 | 0.85144 | -122.5571 | -0.24719 | -0.004577 | 0.032044 | 0.14191 | -0.086975 | -0.28839 | 0.050354 | 0.27924 | 121.994 | 122.3511 | 122.9828 | 123.0652 | 0.032044 | 123.1201 | 119.4946 | -0.28839 | 123.0652 | 0.032044 | 119.4946 | 122.9828 | 123.1201 | -123.317 | -123.3582
767.5312 | 123.2117 | -122.1451 | 0.85144 | 0.0026703 | 0.016317 | 0.014755 | -0.00060672 | 0.064401 | -0.0091409 | 0.068688 | -122.1771 | 0.93384 | -122.5159 | -122.1039 | 0.70038 | -2.8564 | -0.13733 | 0.022888 | 0.95673 | -122.4243 | -0.37079 | 0.082398 | -0.032043 | 0.041199 | -0.15106 | -0.27923 | 0.10529 | 0.33874 | 122.0078 | 122.168 | 122.8455 | 123.0789 | -0.032043 | 123.1018 | 119.2886 | -0.27923 | 123.0789 | -0.032043 | 119.2886 | 122.8455 | 123.1018 | -123.3673 | -123.2758
769.2344 | 123.2254 | -122.1817 | 0.8194 | -0.012589 | 0.018453 | 0.012619 | 0.00067508 | 0.06611 | -0.0074319 | 0.068475 | -122.2275 | 0.89264 | -122.5433 | -122.1405 | 0.70038 | -2.8473 | -0.15106 | 0.004578 | 0.95215 | -122.4564 | -0.36163 | 0.073242 | -0.045776 | 0.041199 | -0.11902 | -0.27466 | 0.13275 | 0.31586 | 122.0306 | 122.1863 | 122.8821 | 123.0743 | -0.045776 | 123.1338 | 119.3344 | -0.27466 | 123.0743 | -0.045776 | 119.3344 | 122.8821 | 123.1338 | -123.3627 | -123.2758
770.9844 | 123.2208 | -122.0764 | 0.89264 | 0.0026703 | 0.019734 | 0.013473 | 0.00046148 | 0.065683 | -0.0052957 | 0.071679 | -122.1725 | 0.9613 | -122.4564 | -122.0444 | 0.76904 | -2.8564 | -0.14191 | 0.009155 | 0.99792 | -122.4426 | -0.37994 | 0.068665 | -0.09613 | 0.032043 | -0.1236 | -0.36621 | 0.10529 | 0.28381 | 121.9345 | 122.0856 | 122.8455 | 123.0377 | -0.09613 | 123.0743 | 119.22 | -0.36621 | 123.0377 | -0.09613 | 119.22 | 122.8455 | 123.0743 | -123.349 | -123.3353
772.6719 | 123.111 | -122.1725 | 0.89722 | -0.0049592 | 0.017598 | 0.011551 | -0.0061609 | 0.062906 | -0.0061503 | 0.06997 | -122.1405 | 0.89264 | -122.4564 | -122.049 | 0.79193 | -2.774 | -0.28381 | 0.068665 | 0.90637 | -122.4747 | -0.28381 | -0.004578 | 0.032043 | 0.1236 | -0.10529 | -0.30212 | 0.009155 | 0.31586 | 121.8887 | 122.2412 | 122.9645 | 123.0652 | 0.032043 | 123.0789 | 119.3985 | -0.30212 | 123.0652 | 0.032043 | 119.3985 | 122.9645 | 123.0789 | -123.3536 | -123.3719
774.4375 | 123.1888 | -122.0215 | 0.99792 | -0.012589 | 0.01888 | 0.014755 | -0.00017952 | 0.06376 | -0.0074319 | 0.06997 | -122.049 | 1.0345 | -122.3694 | -121.9437 | 0.87433 | -2.8198 | -0.24261 | 0.027466 | 1.062 | -122.3465 | -0.3479 | 0.036621 | -0.027466 | 0.077819 | -0.1236 | -0.32501 | 0.064087 | 0.32043 | 121.7789 | 122.049 | 122.8958 | 123.056 | -0.027466 | 123.0835 | 119.2017 | -0.32501 | 123.056 | -0.027466 | 119.2017 | 122.8958 | 123.0835 | -123.3673 | -123.3444
776.1875 | 123.1888 | -122.081 | 0.91553 | -0.020218 | 0.020589 | 0.0085599 | -0.0055199 | 0.062906 | -0.0040139 | 0.069116 | -122.113 | 0.98877 | -122.4152 | -122.0123 | 0.80109 | -2.8061 | -0.009155 | 0.13275 | 1.0162 | -122.4289 | -0.33417 | 0.073243 | -0.032043 | 0.068665 | -0.11444 | -0.3479 | 0.10071 | 0.30212 | 122.0718 | 122.2137 | 122.8821 | 123.0698 | -0.032043 | 123.0972 | 119.2749 | -0.3479 | 123.0698 | -0.032043 | 119.2749 | 122.8821 | 123.0972 | -123.3307 | -123.3444
777.875 | 123.2071 | -122.1909 | 0.81024 | -0.0049592 | 0.017812 | 0.014755 | -0.0010339 | 0.064401 | -0.0063639 | 0.069543 | -122.2137 | 0.88348 | -122.525 | -122.1359 | 0.68207 | -2.8793 | -0.10529 | 0.041199 | 0.91095 | -122.5388 | -0.33417 | 0.073242 | -0.022888 | 0.054932 | -0.12817 | -0.3479 | 0.10071 | 0.31128 | 122.0856 | 122.2321 | 122.8729 | 123.0743 | -0.022888 | 123.1018 | 119.3115 | -0.3479 | 123.0743 | -0.022888 | 119.3115 | 122.8729 | 123.1018 | -123.3353 | -123.349
779.625 | 123.0698 | -122.1542 | 0.91553 | -0.0049592 | 0.018239 | 0.019882 | -0.0040247 | 0.065469 | -0.0042277 | 0.069757 | -122.049 | 0.88348 | -122.3923 | -121.9391 | 0.87891 | -2.742 | -0.37537 | 0.10986 | 0.9201 | -122.4426 | -0.23804 | -0.032043 | 0.10529 | 0.21515 | -0.036621 | -0.28839 | 0.004578 | 0.34332 | 121.7789 | 122.2641 | 123.0331 | 123.0377 | 0.10529 | 123.0743 | 119.4122 | -0.28839 | 123.0377 | 0.10529 | 119.4122 | 123.0331 | 123.0743 | -123.3078 | -123.3582
781.3906 | 123.0606 | -122.2641 | 0.79193 | -0.020218 | 0.017812 | 0.015182 | -0.0035973 | 0.060983 | -0.0072183 | 0.070184 | -122.1359 | 0.81024 | -122.5159 | -122.0398 | 0.78735 | -2.7145 | -0.22888 | 0.24719 | 0.8194 | -122.5113 | -0.25177 | 0.018311 | 0.12817 | 0.2243 | -0.004577 | -0.24719 | 0.027466 | 0.37994 | 122.0352 | 122.5113 | 123.0515 | 123.0743 | 0.12817 | 123.0835 | 119.5496 | -0.24719 | 123.0743 | 0.12817 | 119.5496 | 123.0515 | 123.0835 | -123.3078 | -123.3032
783.0781 | 123.1384 | -122.2092 | 0.78278 | -0.0049592 | 0.015676 | 0.019455 | 0.0021705 | 0.066537 | -0.0074319 | 0.070184 | -122.1863 | 0.82855 | -122.5708 | -122.0901 | 0.70038 | -2.8015 | -0.14191 | 0.14191 | 0.88348 | -122.5067 | -0.36163 | 0.045776 | 0.022888 | 0.11902 | -0.082398 | -0.29755 | 0.10071 | 0.38452 | 122.0673 | 122.3511 | 122.9095 | 123.0377 | 0.022888 | 123.0927 | 119.4077 | -0.29755 | 123.0377 | 0.022888 | 119.4077 | 122.9095 | 123.0927 | -123.3536 | -123.2895
784.8281 | 123.0652 | -122.3511 | 0.73242 | 0.0026703 | 0.016957 | 0.011337 | -0.0046655 | 0.063333 | -0.0059365 | 0.070611 | -122.2183 | 0.72784 | -122.5616 | -122.1268 | 0.70038 | -2.7878 | -0.35248 | 0.10529 | 0.75989 | -122.5616 | -0.21057 | -0.004578 | 0.13275 | 0.2243 | -0.032044 | -0.21057 | 0.027466 | 0.34332 | 121.9986 | 122.4564 | 123.0515 | 123.0789 | 0.13275 | 123.111 | 119.5633 | -0.21057 | 123.0789 | 0.13275 | 119.5633 | 123.0515 | 123.111 | -123.2941 | -123.2941
786.5156 | 123.056 | -122.3831 | 0.68665 | -0.0049592 | 0.01888 | 0.019455 | -0.0018885 | 0.064187 | -0.0052957 | 0.069757 | -122.2687 | 0.65918 | -122.6669 | -122.1817 | 0.63629 | -2.7786 | -0.37994 | 0.10986 | 0.70953 | -122.644 | -0.28381 | -0.027466 | 0.11444 | 0.20142 | -0.050354 | -0.26093 | 0.022888 | 0.39825 | 122.0032 | 122.493 | 123.0194 | 123.0423 | 0.11444 | 123.0927 | 119.6045 | -0.26093 | 123.0423 | 0.11444 | 119.6045 | 123.0194 | 123.0927 | -123.3536 | -123.3307
788.2656 | 123.0789 | -122.3282 | 0.70953 | -0.012589 | 0.017598 | 0.010696 | -0.0059473 | 0.061624 | -0.0052957 | 0.070397 | -122.2458 | 0.70953 | -122.5983 | -122.1222 | 0.68207 | -2.7328 | -0.21057 | 0.23804 | 0.73242 | -122.644 | -0.27008 | 0 | 0.082397 | 0.20599 | -0.027466 | -0.31586 | 0.022888 | 0.35248 | 122.1176 | 122.5662 | 123.0103 | 123.0377 | 0.082397 | 123.0606 | 119.5953 | -0.31586 | 123.0377 | 0.082397 | 119.5953 | 123.0103 | 123.0606 | -123.3078 | -123.3536
790.0312 | 123.0469 | -122.2961 | 0.7782 | -0.012589 | 0.019094 | 0.01561 | -0.0023157 | 0.060983 | -0.0035867 | 0.070611 | -122.1817 | 0.76446 | -122.5525 | -122.0901 | 0.70496 | -2.7786 | -0.35248 | 0.10986 | 0.78278 | -122.5891 | -0.25635 | -0.013733 | 0.11444 | 0.20599 | -0.073242 | -0.29297 | 0.004578 | 0.37079 | 121.9437 | 122.406 | 123.0011 | 123.0606 | 0.11444 | 123.0789 | 119.5175 | -0.29297 | 123.0606 | 0.11444 | 119.5175 | 123.0011 | 123.0789 | -123.3307 | -123.3673
791.7031 | 123.0515 | -122.3053 | 0.74616 | -0.012589 | 0.018025 | 0.012832 | -0.0046655 | 0.060342 | -0.0057229 | 0.06997 | -122.2229 | 0.72327 | -122.5754 | -122.113 | 0.68665 | -2.742 | -0.27008 | 0.20142 | 0.76446 | -122.5891 | -0.27008 | -0.022888 | 0.082398 | 0.19226 | -0.059509 | -0.28381 | 0.01831 | 0.35248 | 122.0352 | 122.5067 | 122.9919 | 123.0286 | 0.082398 | 123.0698 | 119.5633 | -0.28381 | 123.0286 | 0.082398 | 119.5633 | 122.9919 | 123.0698 | -123.3215 | -123.3353
793.4531 | 123.0423 | -122.3923 | 0.67291 | 0.0026703 | 0.017385 | 0.013687 | -0.00082032 | 0.063333 | -0.0050821 | 0.070825 | -122.287 | 0.64087 | -122.6669 | -122.1634 | 0.61798 | -2.7969 | -0.36621 | 0.10986 | 0.68665 | -122.6532 | -0.27466 | -0.032044 | 0.10529 | 0.22888 | -0.054932 | -0.26093 | 0.013733 | 0.37994 | 122.0261 | 122.5021 | 123.0103 | 123.0331 | 0.10529 | 123.0789 | 119.5953 | -0.26093 | 123.0331 | 0.10529 | 119.5953 | 123.0103 | 123.0789 | -123.3398 | -123.3261
795.2188 | 123.0515 | -122.3831 | 0.67291 | 0.0026703 | 0.015676 | 0.015396 | -0.0065881 | 0.061838 | -0.0061503 | 0.068261 | -122.287 | 0.63629 | -122.6395 | -122.1634 | 0.63171 | -2.7512 | -0.23804 | 0.25635 | 0.68207 | -122.6807 | -0.25635 | -0.036621 | 0.096131 | 0.21973 | -0.041199 | -0.29755 | 0.009155 | 0.35248 | 122.1451 | 122.6395 | 123.0148 | 123.0194 | 0.096131 | 123.0652 | 119.632 | -0.29755 | 123.0194 | 0.096131 | 119.632 | 123.0148 | 123.0652 | -123.3124 | -123.3536
796.9531 | 123.0377 | -122.3969 | 0.65918 | -0.012589 | 0.018239 | 0.014969 | -0.0035973 | 0.061624 | -0.0052957 | 0.069329 | -122.2961 | 0.64087 | -122.6532 | -122.1725 | 0.62714 | -2.7512 | -0.27924 | 0.23804 | 0.66834 | -122.6898 | -0.25635 | -0.018311 | 0.10071 | 0.22431 | -0.032044 | -0.29297 | 0.009155 | 0.35706 | 122.1176 | 122.6349 | 123.024 | 123.0377 | 0.10071 | 123.0652 | 119.6457 | -0.29297 | 123.0377 | 0.10071 | 119.6457 | 123.024 | 123.0652 | -123.3124 | -123.349
798.6406 | 123.0515 | -122.4335 | 0.64545 | 0.0026703 | 0.01888 | 0.016037 | -0.0014611 | 0.063547 | -0.0063639 | 0.070825 | -122.3419 | 0.62256 | -122.7036 | -122.2504 | 0.56763 | -2.8244 | -0.36621 | 0.10529 | 0.6546 | -122.699 | -0.27008 | -0.022888 | 0.091553 | 0.18311 | -0.07782 | -0.2655 | 0.009155 | 0.36163 | 122.0673 | 122.5388 | 123.0011 | 123.056 | 0.091553 | 123.0881 | 119.6091 | -0.2655 | 123.056 | 0.091553 | 119.6091 | 123.0011 | 123.0881 | -123.349 | -123.3444
800.3906 | 123.0469 | -122.4106 | 0.67291 | -0.012589 | 0.016744 | 0.011978 | -0.0033837 | 0.063547 | -0.0063639 | 0.069757 | -122.3007 | 0.62256 | -122.6395 | -122.1771 | 0.59967 | -2.8244 | -0.36163 | 0.11444 | 0.67749 | -122.6303 | -0.22888 | -0.050354 | 0.10986 | 0.23346 | -0.073243 | -0.21973 | 0.004577 | 0.33875 | 122.049 | 122.525 | 123.0103 | 123.0331 | 0.10986 | 123.0881 | 119.5862 | -0.21973 | 123.0331 | 0.10986 | 119.5862 | 123.0103 | 123.0881 | -123.3124 | -123.3032
802.1406 | 123.1338 | -122.3923 | 0.6134 | -0.012589 | 0.017598 | 0.012192 | 0.0028113 | 0.061838 | -0.0074319 | 0.070397 | -122.3648 | 0.65918 | -122.7081 | -122.2183 | 0.54932 | -2.8427 | -0.1236 | 0.16022 | 0.70953 | -122.7036 | -0.31586 | 0.045777 | 0.027466 | 0.17395 | -0.064087 | -0.31128 | 0.096131 | 0.34332 | 122.2687 | 122.5525 | 122.9416 | 123.0515 | 0.027466 | 123.1018 | 119.5496 | -0.31128 | 123.0515 | 0.027466 | 119.5496 | 122.9416 | 123.1018 | -123.3215 | -123.317
803.8906 | 123.0469 | -122.3923 | 0.6546 | -0.0049592 | 0.018239 | 0.011337 | -0.0042383 | 0.062265 | -0.0029459 | 0.069329 | -122.3007 | 0.65002 | -122.6532 | -122.168 | 0.62714 | -2.7786 | -0.20142 | 0.21515 | 0.67749 | -122.7081 | -0.26093 | -0.004578 | 0.091553 | 0.2243 | -0.027466 | -0.31586 | 0.022888 | 0.35248 | 122.1909 | 122.6074 | 123.0194 | 123.0423 | 0.091553 | 123.0698 | 119.6136 | -0.31586 | 123.0423 | 0.091553 | 119.6136 | 123.0194 | 123.0698 | -123.3078 | -123.3627
805.5938 | 123.175 | -122.3282 | 0.64087 | 0.0026703 | 0.01888 | 0.017959 | 0.0019569 | 0.064401 | -0.0076455 | 0.068048 | -122.3602 | 0.69122 | -122.7036 | -122.2641 | 0.49439 | -2.948 | -0.10986 | 0.018311 | 0.74158 | -122.6761 | -0.37537 | 0.050354 | -0.032043 | 0.064087 | -0.14648 | -0.3479 | 0.10071 | 0.34332 | 122.2183 | 122.3465 | 122.8226 | 123.0194 | -0.032043 | 123.0698 | 119.3802 | -0.3479 | 123.0194 | -0.032043 | 119.3802 | 122.8226 | 123.0698 | -123.3444 | -123.317
807.3438 | 123.1384 | -122.3877 | 0.62714 | 0.0026703 | 0.020162 | 0.016037 | 0.00024788 | 0.065896 | -0.0078591 | 0.069116 | -122.3419 | 0.67291 | -122.7127 | -122.2321 | 0.54932 | -2.8519 | -0.1236 | 0.16022 | 0.6958 | -122.7127 | -0.32501 | 0.045777 | 0.045776 | 0.15564 | -0.07782 | -0.32501 | 0.068665 | 0.37079 | 122.2641 | 122.5479 | 122.937 | 123.0606 | 0.045776 | 123.0835 | 119.5358 | -0.32501 | 123.0606 | 0.045776 | 119.5358 | 122.937 | 123.0835 | -123.3398 | -123.3398
809.0469 | 123.1888 | -122.3785 | 0.59509 | 0.0026703 | 0.02123 | 0.01326 | -0.0016747 | 0.064615 | -0.0050821 | 0.069116 | -122.4152 | 0.67749 | -122.7173 | -122.3145 | 0.47607 | -2.9617 | -0.11444 | 0.009155 | 0.70496 | -122.7127 | -0.33875 | 0.082397 | -0.036621 | 0.064087 | -0.11902 | -0.33417 | 0.10986 | 0.30212 | 122.2641 | 122.3877 | 122.8546 | 123.056 | -0.036621 | 123.0835 | 119.4168 | -0.33417 | 123.056 | -0.036621 | 119.4168 | 122.8546 | 123.0835 | -123.3124 | -123.3078
810.7812 | 123.1613 | -122.4014 | 0.5722 | -0.0049592 | 0.019734 | 0.012192 | -0.0040247 | 0.062478 | -0.0091409 | 0.070825 | -122.438 | 0.64087 | -122.7493 | -122.3053 | 0.47607 | -2.8976 | -0.036621 | 0.13275 | 0.67291 | -122.7448 | -0.3479 | 0.068664 | -0.036621 | 0.09613 | -0.096131 | -0.34332 | 0.10071 | 0.31128 | 122.3648 | 122.5342 | 122.8775 | 123.0423 | -0.036621 | 123.0743 | 119.5038 | -0.34332 | 123.0423 | -0.036621 | 119.5038 | 122.8775 | 123.0743 | -123.3215 | -123.317
812.5312 | 123.0698 | -122.406 | 0.63171 | -0.012589 | 0.019094 | 0.010055 | -0.0057337 | 0.063119 | -0.0067911 | 0.069329 | -122.3145 | 0.61798 | -122.6715 | -122.2137 | 0.59052 | -2.8198 | -0.14648 | 0.22888 | 0.65918 | -122.7219 | -0.2655 | -0.013733 | 0.091553 | 0.19226 | -0.041199 | -0.31586 | 0.027466 | 0.35706 | 122.2595 | 122.6349 | 122.9965 | 123.024 | 0.091553 | 123.0652 | 119.5862 | -0.31586 | 123.024 | 0.091553 | 119.5862 | 122.9965 | 123.0652 | -123.3032 | -123.3536
814.2812 | 123.1522 | -122.3785 | 0.59967 | -0.012589 | 0.020803 | 0.012832 | -0.00039312 | 0.065256 | -0.0065775 | 0.070825 | -122.4106 | 0.67749 | -122.7036 | -122.2961 | 0.48981 | -2.9434 | -0.25177 | 0.009155 | 0.66834 | -122.7036 | -0.32501 | 0.07782 | -0.032043 | 0.082397 | -0.10986 | -0.32501 | 0.068665 | 0.29297 | 122.1268 | 122.3877 | 122.8683 | 123.056 | -0.032043 | 123.0469 | 119.4351 | -0.32501 | 123.056 | -0.032043 | 119.4351 | 122.8683 | 123.0469 | -123.3032 | -123.3032
816.0312 | 123.0789 | -122.4335 | 0.60425 | -0.0049592 | 0.018453 | 0.01091 | -0.0057337 | 0.062051 | -0.0048685 | 0.070397 | -122.3785 | 0.59967 | -122.6852 | -122.2824 | 0.51727 | -2.8931 | -0.3067 | 0.068665 | 0.63171 | -122.7402 | -0.25177 | -0.004578 | 0.054932 | 0.15106 | -0.086975 | -0.3067 | 0.027466 | 0.3067 | 122.1268 | 122.5021 | 122.9507 | 123.0331 | 0.054932 | 123.0652 | 119.5404 | -0.3067 | 123.0331 | 0.054932 | 119.5404 | 122.9507 | 123.0652 | -123.2895 | -123.3444
817.7188 | 123.1155 | -122.406 | 0.59052 | -0.012589 | 0.019521 | 0.010055 | -0.0012475 | 0.063974 | -0.0070047 | 0.069543 | -122.3694 | 0.63629 | -122.7448 | -122.2504 | 0.52185 | -2.8793 | -0.10071 | 0.16479 | 0.68207 | -122.7219 | -0.33874 | 0.045777 | 0.036621 | 0.15564 | -0.068664 | -0.31586 | 0.091553 | 0.37537 | 122.3053 | 122.5708 | 122.9279 | 123.0423 | 0.036621 | 123.0881 | 119.5267 | -0.31586 | 123.0423 | 0.036621 | 119.5267 | 122.9279 | 123.0881 | -123.3353 | -123.3124
819.4688 | 122.8867 | -121.6644 | 1.2314 | -0.0049592 | 0.01653 | 0.01561 | -0.0044519 | 0.064187 | -0.0063639 | 0.072106 | -121.5591 | 1.2039 | -121.8979 | -121.463 | 1.1765 | -2.7969 | -0.36163 | 0.10986 | 1.2543 | -121.9528 | -0.23346 | -0.027466 | 0.10529 | 0.20142 | -0.054931 | -0.28839 | 0.022888 | 0.33874 | 121.3028 | 121.7743 | 122.8409 | 122.8683 | 0.10529 | 122.9187 | 118.8675 | -0.28839 | 122.8683 | 0.10529 | 118.8675 | 122.8409 | 122.9187 | -123.1293 | -123.1842
821.2188 | 122.7036 | -121.4172 | 1.2589 | 0.017929 | 0.019734 | 0.011978 | -0.0070153 | 0.062265 | -0.0050821 | 0.067834 | -121.3486 | 1.2497 | -121.6782 | -121.2387 | 1.1993 | -2.774 | -0.24261 | 0.18768 | 1.2772 | -121.7148 | -0.26093 | -0.009155 | 0.068664 | 0.17853 | -0.059509 | -0.29755 | 0.018311 | 0.32959 | 121.1746 | 121.6049 | 122.6166 | 122.6669 | 0.068664 | 122.6944 | 118.6432 | -0.29755 | 122.6669 | 0.068664 | 118.6432 | 122.6166 | 122.6944 | -122.937 | -122.9736
822.9688 | 122.5983 | -121.3623 | 1.2543 | -0.012589 | 0.015676 | 0.013473 | -0.0057337 | 0.061624 | -0.0042277 | 0.069757 | -121.2662 | 1.2268 | -121.6003 | -121.138 | 1.2268 | -2.7603 | -0.25635 | 0.21973 | 1.2726 | -121.6278 | -0.23804 | -0.027465 | 0.096131 | 0.22431 | -0.027465 | -0.2655 | 0.018311 | 0.33417 | 121.106 | 121.582 | 122.5891 | 122.5891 | 0.096131 | 122.6349 | 118.602 | -0.2655 | 122.5891 | 0.096131 | 118.602 | 122.5891 | 122.6349 | -122.8546 | -122.8821
824.7344 | 122.5616 | -121.3074 | 1.268 | -0.0049592 | 0.019094 | 0.016678 | -0.0021021 | 0.064828 | -0.0072183 | 0.070184 | -121.1884 | 1.2314 | -121.5637 | -121.0876 | 1.2131 | -2.7969 | -0.35706 | 0.11902 | 1.3 | -121.5317 | -0.25635 | -0.036621 | 0.11902 | 0.21973 | -0.054931 | -0.2243 | 0.032044 | 0.37537 | 120.9503 | 121.4264 | 122.5204 | 122.5388 | 0.11902 | 122.6074 | 118.5104 | -0.2243 | 122.5388 | 0.11902 | 118.5104 | 122.5204 | 122.6074 | -122.8317 | -122.7997
826.4219 | 122.5296 | -121.1975 | 1.3138 | 0.0026703 | 0.015248 | 0.011978 | -0.0033837 | 0.063119 | -0.0080729 | 0.069116 | -121.1197 | 1.2817 | -121.4722 | -120.9869 | 1.2497 | -2.8107 | -0.36163 | 0.11902 | 1.3367 | -121.4493 | -0.27466 | -0.032044 | 0.07782 | 0.21057 | -0.064087 | -0.25177 | 0.022888 | 0.35248 | 120.8359 | 121.3165 | 122.4472 | 122.4792 | 0.07782 | 122.5342 | 118.3868 | -0.25177 | 122.4792 | 0.07782 | 118.3868 | 122.4472 | 122.5342 | -122.7859 | -122.7631
828.1719 | 122.5983 | -121.1929 | 1.2131 | 0.0026703 | 0.017812 | 0.014328 | -0.0029565 | 0.062478 | -0.0055093 | 0.069757 | -121.2387 | 1.268 | -121.5454 | -121.1197 | 1.1124 | -2.8748 | -0.022888 | 0.13733 | 1.3046 | -121.5546 | -0.35248 | 0.054931 | -0.045776 | 0.073242 | -0.10071 | -0.36163 | 0.091552 | 0.3067 | 121.17 | 121.3303 | 122.3053 | 122.4609 | -0.045776 | 122.4976 | 118.3182 | -0.36163 | 122.4609 | -0.045776 | 118.3182 | 122.3053 | 122.4976 | -122.7585 | -122.7676
829.9219 | 122.5113 | -121.225 | 1.2314 | -0.0049592 | 0.013539 | 0.012192 | -0.0068017 | 0.061624 | -0.0065775 | 0.067834 | -121.2204 | 1.2085 | -121.5454 | -121.0831 | 1.1398 | -2.861 | -0.27466 | 0.082397 | 1.268 | -121.5408 | -0.32043 | -0.022888 | 0.004578 | 0.14191 | -0.091552 | -0.31586 | 0.036621 | 0.32501 | 120.9503 | 121.3074 | 122.3648 | 122.4335 | 0.004578 | 122.493 | 118.364 | -0.31586 | 122.4335 | 0.004578 | 118.364 | 122.3648 | 122.493 | -122.7768 | -122.7722
831.6094 | 122.4426 | -121.1929 | 1.2405 | -0.012589 | 0.017598 | 0.011764 | -0.0044519 | 0.061838 | -0.0072183 | 0.067407 | -121.0739 | 1.236 | -121.4355 | -120.9503 | 1.2177 | -2.7695 | -0.2243 | 0.24261 | 1.2543 | -121.463 | -0.24262 | -0.004578 | 0.11902 | 0.24262 | -0.022889 | -0.27008 | 0.013732 | 0.36163 | 120.9686 | 121.4355 | 122.4106 | 122.4289 | 0.11902 | 122.4472 | 118.4235 | -0.27008 | 122.4289 | 0.11902 | 118.4235 | 122.4106 | 122.4472 | -122.6761 | -122.7036
833.3594 | 122.4014 | -121.17 | 1.2405 | -0.0049592 | 0.019521 | 0.01091 | -0.0055199 | 0.05842 | -0.0052957 | 0.070397 | -121.0739 | 1.2314 | -121.4493 | -120.9503 | 1.2131 | -2.7878 | -0.27008 | 0.20599 | 1.268 | -121.4584 | -0.27924 | -0.009156 | 0.09613 | 0.21973 | -0.027466 | -0.28839 | 0.027465 | 0.37537 | 120.9 | 121.376 | 122.3831 | 122.4014 | 0.09613 | 122.438 | 118.3823 | -0.28839 | 122.4014 | 0.09613 | 118.3823 | 122.3831 | 122.438 | -122.6898 | -122.699
835.125 | 122.438 | -121.2479 | 1.0941 | -0.012589 | 0.019094 | 0.017105 | -0.0038111 | 0.060983 | -0.0046549 | 0.068902 | -121.2112 | 1.1261 | -121.5408 | -121.0785 | 1.0574 | -2.861 | -0.2655 | 0.1236 | 1.1627 | -121.5454 | -0.29297 | 0.032044 | 0.036621 | 0.16937 | -0.036621 | -0.29755 | 0.068665 | 0.32959 | 120.9824 | 121.3715 | 122.3053 | 122.374 | 0.036621 | 122.4106 | 118.3868 | -0.29755 | 122.374 | 0.036621 | 118.3868 | 122.3053 | 122.4106 | -122.6349 | -122.6395
836.875 | 122.3557 | -121.1884 | 1.1902 | -0.012589 | 0.018666 | 0.013687 | -0.00082032 | 0.062906 | -0.0057229 | 0.067193 | -121.051 | 1.1627 | -121.4447 | -120.9412 | 1.1398 | -2.8381 | -0.3891 | 0.11902 | 1.2131 | -121.4355 | -0.25635 | -0.027466 | 0.13733 | 0.24719 | -0.050354 | -0.24719 | 0.022888 | 0.39368 | 120.7993 | 121.3074 | 122.3282 | 122.3511 | 0.13733 | 122.4014 | 118.3502 | -0.24719 | 122.3511 | 0.13733 | 118.3502 | 122.3282 | 122.4014 | -122.6349 | -122.6257
838.5625 | 122.4335 | -121.1334 | 1.149 | -0.0049592 | 0.016103 | 0.016891 | 0.0017431 | 0.062692 | -0.0061503 | 0.069543 | -121.1105 | 1.1993 | -121.4813 | -121.0419 | 1.0345 | -2.9022 | -0.13733 | 0.068665 | 1.2405 | -121.4447 | -0.3479 | 0.050354 | 0.022888 | 0.091553 | -0.11444 | -0.31128 | 0.091553 | 0.37079 | 120.9961 | 121.2021 | 122.168 | 122.3328 | 0.022888 | 122.374 | 118.2312 | -0.31128 | 122.3328 | 0.022888 | 118.2312 | 122.168 | 122.374 | -122.6303 | -122.5937
840.3125 | 122.3328 | -121.0831 | 1.1856 | -0.0049592 | 0.019948 | 0.018387 | -0.0057337 | 0.05842 | -0.0040139 | 0.069757 | -121.0236 | 1.2085 | -121.3898 | -120.9137 | 1.149 | -2.8061 | -0.14191 | 0.21973 | 1.2314 | -121.4081 | -0.3067 | 0.022888 | 0.059509 | 0.16937 | -0.036621 | -0.32501 | 0.045776 | 0.36621 | 120.9412 | 121.3028 | 122.2321 | 122.2916 | 0.059509 | 122.3145 | 118.277 | -0.32501 | 122.2916 | 0.059509 | 118.277 | 122.2321 | 122.3145 | -122.5754 | -122.5937
841.9844 | 122.3602 | -121.0373 | 1.1948 | 0.0026703 | 0.017385 | 0.014969 | -0.0010339 | 0.062478 | -0.0070047 | 0.068902 | -121.0373 | 1.2085 | -121.3943 | -120.9045 | 1.1261 | -2.8839 | -0.3067 | 0.068665 | 1.2451 | -121.3394 | -0.35706 | 0.013733 | 0 | 0.13275 | -0.068664 | -0.30213 | 0.050354 | 0.35706 | 120.7306 | 121.106 | 122.1634 | 122.2458 | 0 | 122.2824 | 118.1534 | -0.30213 | 122.2458 | 0 | 118.1534 | 122.1634 | 122.2824 | -122.5891 | -122.5342
843.7344 | 122.287 | -121.0876 | 1.1581 | 0.0026703 | 0.018239 | 0.013046 | -0.0014611 | 0.063119 | -0.0033731 | 0.069543 | -121.0098 | 1.1627 | -121.3669 | -120.8771 | 1.1215 | -2.8519 | -0.33875 | 0.11444 | 1.1993 | -121.3669 | -0.27924 | 0.004578 | 0.077819 | 0.21057 | -0.036621 | -0.27924 | 0.041199 | 0.35706 | 120.7489 | 121.2021 | 122.2092 | 122.2504 | 0.077819 | 122.287 | 118.2358 | -0.27924 | 122.2504 | 0.077819 | 118.2358 | 122.2092 | 122.287 | -122.525 | -122.525
845.5 | 122.2275 | -121.0556 | 1.1673 | 0.0026703 | 0.017812 | 0.012619 | -0.0035973 | 0.061838 | -0.0044413 | 0.068475 | -120.9778 | 1.1398 | -121.3257 | -120.8862 | 1.0986 | -2.8656 | -0.35248 | 0.10986 | 1.1948 | -121.3669 | -0.27008 | -0.027465 | 0.07782 | 0.16937 | -0.068664 | -0.31128 | 0.027466 | 0.3479 | 120.7031 | 121.1655 | 122.1542 | 122.1954 | 0.07782 | 122.2504 | 118.19 | -0.31128 | 122.1954 | 0.07782 | 118.19 | 122.1542 | 122.2504 | -122.493 | -122.5342
847.25 | 122.3373 | -120.9778 | 1.1261 | -0.012589 | 0.017171 | 0.015396 | -0.0025293 | 0.061624 | -0.0040139 | 0.072106 | -121.0556 | 1.1902 | -121.3531 | -120.9183 | 1.0391 | -2.9022 | -0.004578 | 0.11902 | 1.2589 | -121.3806 | -0.37537 | 0.064087 | -0.07782 | 0.059509 | -0.086975 | -0.40283 | 0.13275 | 0.29755 | 120.9732 | 121.0968 | 122.0169 | 122.168 | -0.07782 | 122.2366 | 118.0756 | -0.40283 | 122.168 | -0.07782 | 118.0756 | 122.0169 | 122.2366 | -122.4792 | -122.5067
848.9844 | 122.2504 | -120.9915 | 1.1673 | -0.012589 | 0.018666 | 0.013901 | -0.0023157 | 0.060983 | -0.0070047 | 0.069116 | -120.9686 | 1.1765 | -121.2845 | -120.8679 | 1.0666 | -2.8839 | -0.068665 | 0.16022 | 1.2222 | -121.3257 | -0.29297 | 0.009156 | 0.022888 | 0.1236 | -0.10071 | -0.33417 | 0.054932 | 0.31586 | 120.9229 | 121.1517 | 122.0581 | 122.168 | 0.022888 | 122.2137 | 118.1076 | -0.33417 | 122.168 | 0.022888 | 118.1076 | 122.0581 | 122.2137 | -122.4518 | -122.493
850.6719 | 122.2321 | -120.9732 | 1.1307 | -0.0049592 | 0.014821 | 0.014328 | 0.0025977 | 0.062906 | -0.0076455 | 0.06997 | -120.932 | 1.1765 | -121.3303 | -120.8221 | 1.0666 | -2.8702 | -0.14191 | 0.14648 | 1.2222 | -121.2708 | -0.35705 | 0.045777 | 0.041199 | 0.15106 | -0.064087 | -0.29755 | 0.091553 | 0.39825 | 120.8313 | 121.1197 | 122.0398 | 122.1497 | 0.041199 | 122.1954 | 118.103 | -0.29755 | 122.1497 | 0.041199 | 118.103 | 122.0398 | 122.1954 | -122.4609 | -122.4014
852.4219 | 122.1176 | -120.9549 | 1.1673 | -0.012589 | 0.016317 | 0.013901 | -0.0063745 | 0.064187 | -0.0044413 | 0.068261 | -120.8771 | 1.149 | -121.2296 | -120.7306 | 1.1398 | -2.7878 | -0.25635 | 0.2243 | 1.2039 | -121.2341 | -0.27466 | -0.01831 | 0.07782 | 0.2243 | -0.027465 | -0.27924 | 0.036621 | 0.35248 | 120.6985 | 121.1792 | 122.0947 | 122.1039 | 0.07782 | 122.1588 | 118.1671 | -0.27924 | 122.1039 | 0.07782 | 118.1671 | 122.0947 | 122.1588 | -122.3969 | -122.4014
854.1875 | 122.1313 | -121.0281 | 1.1124 | 0.0026703 | 0.019094 | 0.014328 | -0.0031701 | 0.063547 | -0.0059365 | 0.068688 | -120.8954 | 1.1078 | -121.2524 | -120.7809 | 1.062 | -2.8473 | -0.39368 | 0.11444 | 1.1444 | -121.257 | -0.2243 | -0.004578 | 0.13275 | 0.24719 | -0.050354 | -0.22888 | 0.032043 | 0.35706 | 120.6345 | 121.1426 | 122.0901 | 122.1359 | 0.13275 | 122.1725 | 118.1808 | -0.22888 | 122.1359 | 0.13275 | 118.1808 | 122.0901 | 122.1725 | -122.3648 | -122.3694
855.9375 | 122.2458 | -120.9137 | 1.1078 | -0.0049592 | 0.017171 | 0.012619 | -0.0016747 | 0.062051 | -0.0076455 | 0.06997 | -120.9595 | 1.1765 | -121.3028 | -120.8359 | 0.98877 | -2.9068 | -0.022888 | 0.12817 | 1.2268 | -121.2708 | -0.3891 | 0.068665 | -0.045777 | 0.07782 | -0.11902 | -0.35706 | 0.11902 | 0.34332 | 120.8908 | 121.0419 | 121.9025 | 122.0901 | -0.045777 | 122.1405 | 118.0069 | -0.35706 | 122.0901 | -0.045777 | 118.0069 | 121.9025 | 122.1405 | -122.4106 | -122.3785
857.6875 | 122.1313 | -120.9091 | 1.0895 | 0.0026703 | 0.017385 | 0.012619 | -0.0038111 | 0.062478 | -0.0067911 | 0.066125 | -120.8908 | 1.1353 | -121.2433 | -120.8084 | 1.0162 | -2.8885 | -0.073242 | 0.16937 | 1.1993 | -121.2433 | -0.33417 | 0.045776 | 0.018311 | 0.10071 | -0.073243 | -0.33417 | 0.10986 | 0.35248 | 120.8359 | 121.0785 | 121.9254 | 122.0444 | 0.018311 | 122.1085 | 118.0206 | -0.33417 | 122.0444 | 0.018311 | 118.0206 | 121.9254 | 122.1085 | -122.3328 | -122.3328
859.375 | 122.0993 | -120.9229 | 1.1307 | -0.012589 | 0.018025 | 0.012832 | -0.0053063 | 0.063119 | -0.0044413 | 0.070184 | -120.8771 | 1.1261 | -121.225 | -120.7764 | 1.0391 | -2.9068 | -0.27008 | 0.086975 | 1.1673 | -121.2524 | -0.30212 | -0.004577 | 0.045777 | 0.14649 | -0.091552 | -0.32959 | 0.036621 | 0.3479 | 120.6528 | 121.0098 | 121.962 | 122.049 | 0.045777 | 122.0901 | 118.0161 | -0.32959 | 122.049 | 0.045777 | 118.0161 | 121.962 | 122.0901 | -122.3557 | -122.3831
861.0781 | 122.0764 | -120.8679 | 1.1261 | -0.0049592 | 0.019094 | 0.01561 | -0.0063745 | 0.061197 | -0.0052957 | 0.068902 | -120.8405 | 1.1627 | -121.1655 | -120.726 | 1.062 | -2.9205 | -0.26093 | 0.10986 | 1.1673 | -121.1838 | -0.29755 | 0.036621 | 0.027466 | 0.14191 | -0.064087 | -0.31586 | 0.041198 | 0.32501 | 120.607 | 120.9778 | 121.9299 | 122.0306 | 0.027466 | 122.0352 | 117.9474 | -0.31586 | 122.0306 | 0.027466 | 117.9474 | 121.9299 | 122.0352 | -122.2916 | -122.3099
862.8125 | 122.0169 | -120.8908 | 1.1444 | -0.0049592 | 0.01653 | 0.014969 | -0.00060672 | 0.060556 | -0.0048685 | 0.068902 | -120.7626 | 1.1124 | -121.1563 | -120.639 | 1.0986 | -2.8564 | -0.37537 | 0.12817 | 1.1536 | -121.1243 | -0.2655 | -0.032043 | 0.12817 | 0.25177 | -0.045776 | -0.23346 | 0.009155 | 0.39368 | 120.5154 | 121.019 | 121.9894 | 122.0032 | 0.12817 | 122.0444 | 118.0344 | -0.23346 | 122.0032 | 0.12817 | 118.0344 | 121.9894 | 122.0444 | -122.3007 | -122.2687
864.5469 | 122.0078 | -120.8725 | 1.1307 | -0.020218 | 0.018025 | 0.010483 | -0.0050927 | 0.060556 | -0.0038003 | 0.069329 | -120.7809 | 1.1353 | -121.1105 | -120.6573 | 1.0941 | -2.8336 | -0.26093 | 0.18768 | 1.1627 | -121.1151 | -0.23804 | 0.004578 | 0.091553 | 0.21515 | -0.036621 | -0.24261 | 0.032044 | 0.32959 | 120.6116 | 121.0602 | 121.9666 | 122.0078 | 0.091553 | 122.0352 | 118.0389 | -0.24261 | 122.0078 | 0.091553 | 118.0389 | 121.9666 | 122.0352 | -122.2412 | -122.2458
866.2969 | 121.9757 | -120.8633 | 1.1307 | -0.0049592 | 0.015676 | 0.012405 | 0.00024788 | 0.064401 | -0.0085001 | 0.067193 | -120.7443 | 1.1215 | -121.1197 | -120.6299 | 1.0757 | -2.8702 | -0.37537 | 0.10986 | 1.1444 | -121.0831 | -0.25635 | -0.009155 | 0.11902 | 0.23346 | -0.054931 | -0.21973 | 0.013733 | 0.37537 | 120.488 | 120.9732 | 121.9391 | 121.9849 | 0.11902 | 122.0078 | 117.9932 | -0.21973 | 121.9849 | 0.11902 | 117.9932 | 121.9391 | 122.0078 | -122.2504 | -122.2137
868.0312 | 121.9757 | -120.7947 | 1.1261 | -0.0049592 | 0.01418 | 0.012192 | -0.0057337 | 0.062265 | -0.0057229 | 0.070184 | -120.7489 | 1.1215 | -121.106 | -120.6482 | 1.0574 | -2.9068 | -0.32044 | 0.09613 | 1.1856 | -121.0556 | -0.31128 | -0.004578 | 0.045777 | 0.14648 | -0.068665 | -0.26093 | 0.059509 | 0.35706 | 120.4742 | 120.8908 | 121.8521 | 121.9162 | 0.045777 | 121.9803 | 117.8879 | -0.26093 | 121.9162 | 0.045777 | 117.8879 | 121.8521 | 121.9803 | -122.2321 | -122.1817
869.7812 | 121.9162 | -120.8084 | 1.1398 | -0.0049592 | 0.017171 | 0.011764 | -0.0033837 | 0.059915 | -0.0042277 | 0.068475 | -120.6802 | 1.1124 | -121.0327 | -120.5566 | 1.1169 | -2.8107 | -0.27008 | 0.24261 | 1.1719 | -121.0602 | -0.2243 | -0.027466 | 0.12817 | 0.25177 | -0.022889 | -0.25177 | 0.032043 | 0.35248 | 120.5383 | 121.051 | 121.9254 | 121.9208 | 0.12817 | 121.9803 | 117.9977 | -0.25177 | 121.9208 | 0.12817 | 117.9977 | 121.9254 | 121.9803 | -122.1725 | -122.2
871.4688 | 121.9666 | -120.7214 | 1.1765 | -0.0049592 | 0.017171 | 0.010483 | -0.0059473 | 0.059701 | -0.0048685 | 0.069543 | -120.6573 | 1.1902 | -120.9732 | -120.5566 | 1.0986 | -2.9205 | -0.26093 | 0.10071 | 1.2589 | -121.0007 | -0.25177 | 0.013733 | 0.064087 | 0.16479 | -0.07782 | -0.27923 | 0.082397 | 0.31586 | 120.4605 | 120.8221 | 121.8201 | 121.9116 | 0.064087 | 121.9803 | 117.8009 | -0.27923 | 121.9116 | 0.064087 | 117.8009 | 121.8201 | 121.9803 | -122.1497 | -122.1771
873.2188 | 122.0215 | -120.6802 | 1.1124 | -0.0049592 | 0.018025 | 0.0098417 | -0.0014611 | 0.05906 | -0.0065775 | 0.069543 | -120.7306 | 1.1765 | -121.0785 | -120.6116 | 1.0071 | -2.948 | -0.013733 | 0.11444 | 1.2314 | -121.051 | -0.39825 | 0.064087 | -0.050354 | 0.068665 | -0.10529 | -0.37079 | 0.11902 | 0.3479 | 120.6665 | 120.7947 | 121.6873 | 121.8567 | -0.050354 | 121.9116 | 117.7322 | -0.37079 | 121.8567 | -0.050354 | 117.7322 | 121.6873 | 121.9116 | -122.1909 | -122.1634
874.9688 | 121.8704 | -120.607 | 1.2863 | 0.0103 | 0.016744 | 0.015396 | -0.0016747 | 0.064187 | -0.0063639 | 0.068902 | -120.4971 | 1.2497 | -120.8633 | -120.3781 | 1.2085 | -2.861 | -0.3891 | 0.1236 | 1.268 | -120.8542 | -0.25635 | -0.036621 | 0.10986 | 0.22888 | -0.07782 | -0.24719 | -0.018311 | 0.36621 | 120.2179 | 120.7306 | 121.8155 | 121.8567 | 0.10986 | 121.875 | 117.746 | -0.24719 | 121.8567 | 0.10986 | 117.746 | 121.8155 | 121.875 | -122.1497 | -122.1405
876.6406 | 121.9391 | -120.5978 | 1.2039 | -0.0049592 | 0.020589 | 0.014114 | 0.00067508 | 0.064187 | -0.0072183 | 0.068261 | -120.5658 | 1.2451 | -120.9274 | -120.4468 | 1.1078 | -2.9068 | -0.082397 | 0.15106 | 1.2726 | -120.9091 | -0.32959 | 0.041199 | 0.032043 | 0.15106 | -0.09613 | -0.31128 | 0.068665 | 0.36163 | 120.5154 | 120.7489 | 121.7056 | 121.843 | 0.032043 | 121.8704 | 117.691 | -0.31128 | 121.843 | 0.032043 | 117.691 | 121.7056 | 121.8704 | -122.1313 | -122.113
878.3906 | 121.9666 | -120.5429 | 1.181 | -0.0049592 | 0.018666 | 0.012619 | -0.00060672 | 0.063974 | -0.0042277 | 0.068048 | -120.639 | 1.236 | -120.9183 | -120.5246 | 1.0345 | -2.9892 | -0.15106 | 0 | 1.268 | -120.8817 | -0.37537 | 0.054932 | -0.09613 | 0.018311 | -0.14648 | -0.33875 | 0.086975 | 0.27924 | 120.3918 | 120.5429 | 121.5775 | 121.7789 | -0.09613 | 121.8109 | 117.5537 | -0.33875 | 121.7789 | -0.09613 | 117.5537 | 121.5775 | 121.8109 | -122.0993 | -122.0627
880.1562 | 121.875 | -120.5338 | 1.2222 | 0.0026703 | 0.018025 | 0.017319 | -0.00017952 | 0.062692 | -0.0080729 | 0.070825 | -120.5063 | 1.2543 | -120.8908 | -120.3918 | 1.1353 | -2.9114 | -0.1236 | 0.14648 | 1.2909 | -120.8542 | -0.35706 | 0.032043 | 0.027465 | 0.14191 | -0.086975 | -0.32043 | 0.068665 | 0.38452 | 120.4102 | 120.6802 | 121.669 | 121.788 | 0.027465 | 121.8246 | 117.6224 | -0.32043 | 121.788 | 0.027465 | 117.6224 | 121.669 | 121.8246 | -122.113 | -122.0764
881.9062 | 121.8018 | -120.5704 | 1.1993 | -0.012589 | 0.015889 | 0.012619 | -0.0070153 | 0.060556 | -0.0059365 | 0.071893 | -120.52 | 1.1765 | -120.8588 | -120.4056 | 1.1627 | -2.8656 | -0.25635 | 0.18768 | 1.2177 | -120.9 | -0.28839 | -0.022888 | 0.050354 | 0.16479 | -0.036621 | -0.32959 | 0.01831 | 0.33875 | 120.314 | 120.7581 | 121.7331 | 121.7468 | 0.050354 | 121.788 | 117.7048 | -0.32959 | 121.7468 | 0.050354 | 117.7048 | 121.7331 | 121.788 | -122.0581 | -122.0993
883.5781 | 121.8475 | -120.575 | 1.1581 | -0.0049592 | 0.01653 | 0.015182 | 0.00088868 | 0.062051 | -0.0070047 | 0.06762 | -120.5383 | 1.1902 | -120.8954 | -120.4193 | 1.0803 | -2.9022 | -0.13275 | 0.16937 | 1.2314 | -120.8679 | -0.32044 | 0.032044 | 0.036621 | 0.15564 | -0.07782 | -0.29297 | 0.073242 | 0.35706 | 120.4422 | 120.7443 | 121.6553 | 121.7651 | 0.036621 | 121.8063 | 117.6727 | -0.29297 | 121.7651 | 0.036621 | 117.6727 | 121.6553 | 121.8063 | -122.0535 | -122.0261
885.3281 | 121.8704 | -120.575 | 1.1169 | 0.0026703 | 0.019734 | 0.011978 | -0.0014611 | 0.062692 | -0.0059365 | 0.071466 | -120.5978 | 1.1902 | -120.9137 | -120.4834 | 0.98877 | -2.9892 | -0.19684 | 0.004578 | 1.2131 | -120.8725 | -0.33875 | 0.073243 | -0.022888 | 0.091553 | -0.12817 | -0.29755 | 0.096131 | 0.31586 | 120.3781 | 120.5795 | 121.5637 | 121.7651 | -0.022888 | 121.788 | 117.5858 | -0.29755 | 121.7651 | -0.022888 | 117.5858 | 121.5637 | 121.788 | -122.0306 | -121.9894
887.0781 | 121.7697 | -120.5933 | 1.1032 | 0.0026703 | 0.015889 | 0.013687 | -0.0063745 | 0.05906 | -0.0042277 | 0.06997 | -120.5795 | 1.1215 | -120.8954 | -120.4742 | 1.0254 | -2.9297 | -0.2655 | 0.07782 | 1.1581 | -120.8679 | -0.30212 | 0.018311 | 0.013733 | 0.11902 | -0.077819 | -0.27466 | 0.054932 | 0.31586 | 120.3278 | 120.6711 | 121.6187 | 121.7148 | 0.013733 | 121.7514 | 117.6636 | -0.27466 | 121.7148 | 0.013733 | 117.6636 | 121.6187 | 121.7514 | -121.9986 | -121.9711
888.8281 | 121.6965 | -120.6024 | 1.0986 | -0.0049592 | 0.016744 | 0.01091 | -0.0042383 | 0.060983 | -0.0048685 | 0.067407 | -120.488 | 1.1032 | -120.8359 | -120.3827 | 1.0941 | -2.8564 | -0.24261 | 0.25177 | 1.1398 | -120.8633 | -0.23346 | 0.004577 | 0.11444 | 0.21973 | -0.004578 | -0.26093 | 0.041199 | 0.3479 | 120.3598 | 120.8542 | 121.6965 | 121.7056 | 0.11444 | 121.7422 | 117.746 | -0.26093 | 121.7056 | 0.11444 | 117.746 | 121.6965 | 121.7422 | -121.9345 | -121.962
890.5469 | 121.6827 | -120.5704 | 1.1169 | -0.012589 | 0.01418 | 0.011337 | -0.0061609 | 0.061624 | -0.0059365 | 0.069543 | -120.4651 | 1.1078 | -120.8359 | -120.3415 | 1.1032 | -2.8519 | -0.25177 | 0.23804 | 1.1536 | -120.845 | -0.2655 | -0.009155 | 0.10529 | 0.22888 | -0.013733 | -0.27466 | 0.036621 | 0.37079 | 120.3186 | 120.8084 | 121.6736 | 121.6782 | 0.10529 | 121.7239 | 117.7185 | -0.27466 | 121.6782 | 0.10529 | 117.7185 | 121.6736 | 121.7239 | -121.9528 | -121.962
892.2969 | 121.7194 | -120.5566 | 1.1078 | 0.0026703 | 0.018239 | 0.018387 | 0.00046148 | 0.061624 | -0.0082865 | 0.068902 | -120.5017 | 1.1078 | -120.8588 | -120.3735 | 1.03 | -2.9343 | -0.33875 | 0.091553 | 1.1353 | -120.7993 | -0.30212 | 0 | 0.054932 | 0.18311 | -0.07782 | -0.24261 | 0.027466 | 0.35706 | 120.2179 | 120.6482 | 121.5866 | 121.6644 | 0.054932 | 121.6919 | 117.6224 | -0.24261 | 121.6644 | 0.054932 | 117.6224 | 121.5866 | 121.6919 | -121.9666 | -121.907
893.9688 | 121.6507 | -120.4926 | 1.1581 | -0.012589 | 0.019307 | 0.016464 | -0.0046655 | 0.060129 | -0.0063639 | 0.068688 | -120.3873 | 1.149 | -120.7489 | -120.2591 | 1.1353 | -2.8564 | -0.2243 | 0.24719 | 1.1993 | -120.7947 | -0.25635 | -0.009155 | 0.10529 | 0.23346 | -0.022888 | -0.30212 | 0.041199 | 0.36163 | 120.2682 | 120.7397 | 121.6278 | 121.6415 | 0.10529 | 121.6919 | 117.6361 | -0.30212 | 121.6415 | 0.10529 | 117.6361 | 121.6278 | 121.6919 | -121.907 | -121.9528
895.7188 | 121.7239 | -120.4971 | 1.1032 | -0.0049592 | 0.017385 | 0.012832 | 0.00024788 | 0.063547 | -0.0078591 | 0.06762 | -120.488 | 1.1398 | -120.8267 | -120.3781 | 1.0025 | -2.9709 | -0.29297 | 0.050354 | 1.1719 | -120.7993 | -0.32959 | 0.036622 | 0.009155 | 0.11902 | -0.10071 | -0.30212 | 0.068665 | 0.33875 | 120.2042 | 120.5475 | 121.4996 | 121.637 | 0.009155 | 121.669 | 117.5262 | -0.30212 | 121.637 | 0.009155 | 117.5262 | 121.4996 | 121.669 | -121.9299 | -121.9025
897.4688 | 121.6965 | -120.4742 | 1.1032 | -0.0049592 | 0.019307 | 0.01625 | -0.00017952 | 0.062051 | -0.0078591 | 0.068902 | -120.4422 | 1.1169 | -120.7901 | -120.3186 | 1.0162 | -2.9297 | -0.12817 | 0.16022 | 1.1719 | -120.7764 | -0.31586 | 0.013733 | 0.032043 | 0.15564 | -0.086975 | -0.30212 | 0.068665 | 0.3479 | 120.3461 | 120.6345 | 121.4905 | 121.5912 | 0.032043 | 121.6461 | 117.5446 | -0.30212 | 121.5912 | 0.032043 | 117.5446 | 121.4905 | 121.6461 | -121.8933 | -121.8796
899.2188 | 121.6049 | -120.4834 | 1.1307 | -0.012589 | 0.015462 | 0.014541 | -0.0029565 | 0.062692 | -0.0061503 | 0.070184 | -120.3644 | 1.1032 | -120.7352 | -120.2637 | 1.1078 | -2.9114 | -0.37994 | 0.1236 | 1.1627 | -120.7123 | -0.25177 | -0.027466 | 0.11902 | 0.21973 | -0.022888 | -0.22888 | 0.032044 | 0.37079 | 120.1035 | 120.607 | 121.5912 | 121.5866 | 0.11902 | 121.6461 | 117.572 | -0.22888 | 121.5866 | 0.11902 | 117.572 | 121.5912 | 121.6461 | -121.8658 | -121.843
900.9688 | 121.5958 | -120.433 | 1.1307 | -0.012589 | 0.016103 | 0.014969 | -0.0040247 | 0.062265 | -0.0070047 | 0.067407 | -120.3506 | 1.1398 | -120.7123 | -120.2316 | 1.0986 | -2.8976 | -0.14191 | 0.21973 | 1.1719 | -120.7123 | -0.27924 | 0.009156 | 0.082397 | 0.20142 | -0.032043 | -0.27924 | 0.041199 | 0.36163 | 120.2911 | 120.6528 | 121.5317 | 121.5729 | 0.082397 | 121.6049 | 117.5354 | -0.27924 | 121.5729 | 0.082397 | 117.5354 | 121.5317 | 121.6049 | -121.843 | -121.843
902.6562 | 121.637 | -120.3735 | 1.1765 | 0.0026703 | 0.016957 | 0.016037 | -0.0057337 | 0.062265 | -0.0044413 | 0.068261 | -120.3323 | 1.1581 | -120.6573 | -120.2225 | 1.0986 | -2.9663 | -0.27924 | 0.064087 | 1.2222 | -120.694 | -0.28381 | -0.018311 | 0.041199 | 0.15106 | -0.07782 | -0.32043 | 0.045776 | 0.32501 | 120.0943 | 120.4376 | 121.4722 | 121.5317 | 0.041199 | 121.5958 | 117.4072 | -0.32043 | 121.5317 | 0.041199 | 117.4072 | 121.4722 | 121.5958 | -121.8338 | -121.8704
904.3906 | 121.5363 | -120.4102 | 1.1169 | 0.0026703 | 0.017598 | 0.012192 | -0.0046655 | 0.060556 | -0.0046549 | 0.067834 | -120.2911 | 1.1215 | -120.6848 | -120.1721 | 1.1078 | -2.8839 | -0.23804 | 0.23346 | 1.1581 | -120.6985 | -0.27466 | 0.004578 | 0.11902 | 0.23804 | -0.009155 | -0.28839 | 0.041199 | 0.39368 | 120.1721 | 120.6436 | 121.5179 | 121.5317 | 0.11902 | 121.5683 | 117.5262 | -0.28839 | 121.5317 | 0.11902 | 117.5262 | 121.5179 | 121.5683 | -121.8018 | -121.8155
906.1406 | 121.6141 | -120.3873 | 1.0941 | -0.0049592 | 0.01888 | 0.013046 | 0.00046148 | 0.065256 | -0.0072183 | 0.068902 | -120.3506 | 1.1215 | -120.7581 | -120.2499 | 0.97046 | -2.9846 | -0.1236 | 0.1236 | 1.1856 | -120.6802 | -0.37079 | 0.027466 | 0.036621 | 0.13733 | -0.1236 | -0.29297 | 0.091553 | 0.40741 | 120.2637 | 120.5109 | 121.3577 | 121.5088 | 0.036621 | 121.5729 | 117.4026 | -0.29297 | 121.5088 | 0.036621 | 117.4026 | 121.3577 | 121.5729 | -121.8521 | -121.7743
907.8906 | 121.6415 | -120.3873 | 1.0712 | -0.0049592 | 0.018666 | 0.014755 | 0.00024788 | 0.060342 | -0.0065775 | 0.068048 | -120.4285 | 1.1398 | -120.7352 | -120.2957 | 0.9201 | -3.0396 | -0.11902 | 0.013733 | 1.1673 | -120.6985 | -0.3479 | 0.068665 | -0.041199 | 0.091553 | -0.15106 | -0.31128 | 0.09613 | 0.3067 | 120.2682 | 120.401 | 121.3074 | 121.5271 | -0.041199 | 121.5546 | 117.3477 | -0.31128 | 121.5271 | -0.041199 | 117.3477 | 121.3074 | 121.5546 | -121.8063 | -121.7697
909.5781 | 121.7239 | -0.25177 | 121.5591 | 0.0103 | 0.019521 | 0.0098417 | -0.0093653 | 0.060556 | -0.0042277 | 0.06762 | -0.091553 | 121.6003 | -0.50812 | 0.12817 | 120.8954 | 4.4174 | 0.19226 | 0.57678 | 121.6415 | -0.4303 | -0.25635 | 0.041199 | 0.16022 | 0.37994 | -0.66376 | -0.17853 | 0.082398 | 0.41656 | 0.44403 | 0.82855 | 121.1472 | 121.8521 | 0.16022 | 121.8933 | 4.6692 | -0.17853 | 121.8521 | 0.16022 | 4.6692 | 121.1472 | 121.8933 | -122.0673 | -121.9894
911.3281 | 121.9574 | -0.23804 | 121.6003 | -0.0049592 | 0.020589 | 0.011551 | 0.00067508 | 0.060983 | -0.0070047 | 0.069116 | -0.17853 | 121.7102 | -0.53101 | 0.004578 | 120.8496 | 4.1473 | 0.20142 | 0.27466 | 121.8109 | -0.46234 | -0.29297 | 0.10986 | 0.059509 | 0.24261 | -0.75073 | -0.2243 | 0.21057 | 0.35248 | 0.43945 | 0.5127 | 121.0876 | 121.9482 | 0.059509 | 122.049 | 4.3854 | -0.2243 | 121.9482 | 0.059509 | 4.3854 | 121.0876 | 122.049 | -122.1313 | -122.0627
913.0781 | 121.8933 | -0.25177 | 121.6827 | 0.0026703 | 0.01653 | 0.01326 | -0.0072289 | 0.060769 | -0.0050821 | 0.068688 | -0.16937 | 121.6919 | -0.52185 | 0.054932 | 120.9869 | 4.1977 | 0.064087 | 0.3891 | 121.788 | -0.43488 | -0.27008 | 0.009156 | 0.082397 | 0.3067 | -0.6958 | -0.18311 | 0.10529 | 0.35248 | 0.31586 | 0.64087 | 121.2387 | 121.9437 | 0.082397 | 122.0398 | 4.4495 | -0.18311 | 121.9437 | 0.082397 | 4.4495 | 121.2387 | 122.0398 | -122.2046 | -122.1176
914.8281 | 121.9208 | -0.28381 | 121.7102 | 0.0026703 | 0.018666 | 0.01091 | -0.0040247 | 0.06141 | -0.0048685 | 0.066979 | -0.13275 | 121.7743 | -0.50812 | 0.050354 | 121.0007 | 4.1702 | 0.018311 | 0.33417 | 121.8109 | -0.43488 | -0.2243 | 0.064087 | 0.15106 | 0.33417 | -0.70953 | -0.15106 | 0.10071 | 0.37537 | 0.30212 | 0.61798 | 121.2845 | 122.0581 | 0.15106 | 122.0947 | 4.454 | -0.15106 | 122.0581 | 0.15106 | 4.454 | 121.2845 | 122.0947 | -122.2183 | -122.1451
916.5312 | 121.8979 | -0.2655 | 121.7148 | 0.0026703 | 0.016744 | 0.011337 | -0.0033837 | 0.060556 | -0.0055093 | 0.067407 | -0.11444 | 121.7834 | -0.52185 | 0.10986 | 121.0693 | 4.248 | 0.032043 | 0.44861 | 121.8292 | -0.43488 | -0.25635 | 0.068664 | 0.15106 | 0.37537 | -0.64545 | -0.16937 | 0.11444 | 0.40741 | 0.29755 | 0.71411 | 121.3348 | 122.0489 | 0.15106 | 122.0947 | 4.5135 | -0.16937 | 122.0489 | 0.15106 | 4.5135 | 121.3348 | 122.0947 | -122.2366 | -122.1497
918.2812 | 121.9894 | -0.25177 | 121.6965 | -0.0049592 | 0.019948 | 0.010483 | 0.0015295 | 0.059701 | -0.0080729 | 0.068475 | -0.14191 | 121.8246 | -0.53558 | 0.07782 | 121.0281 | 4.1885 | 0.18768 | 0.41657 | 121.8979 | -0.45319 | -0.28381 | 0.12817 | 0.10986 | 0.32959 | -0.66833 | -0.20142 | 0.20142 | 0.39368 | 0.43945 | 0.66834 | 121.2799 | 122.0764 | 0.10986 | 122.1497 | 4.4403 | -0.20142 | 122.0764 | 0.10986 | 4.4403 | 121.2799 | 122.1497 | -122.2321 | -122.1497
920.0156 | 122.049 | -0.27008 | 121.7102 | -0.0049592 | 0.018239 | 0.013473 | 0.0025977 | 0.062051 | -0.0072183 | 0.065911 | -0.17853 | 121.8155 | -0.56305 | 0.018311 | 120.9915 | 4.129 | 0.16479 | 0.31128 | 121.9254 | -0.44861 | -0.29297 | 0.10529 | 0.091553 | 0.28839 | -0.71869 | -0.17853 | 0.21515 | 0.38452 | 0.43488 | 0.58136 | 121.2616 | 122.0856 | 0.091553 | 122.1954 | 4.3991 | -0.17853 | 122.0856 | 0.091553 | 4.3991 | 121.2616 | 122.1954 | -122.2733 | -122.1588
921.7188 | 122.0306 | -0.26093 | 121.7239 | -0.0049592 | 0.020162 | 0.014755 | 0.0028113 | 0.06376 | -0.0080729 | 0.068048 | -0.13733 | 121.8292 | -0.53101 | 0.045776 | 121.051 | 4.1702 | 0.15564 | 0.36163 | 121.9116 | -0.46692 | -0.27008 | 0.10529 | 0.1236 | 0.3067 | -0.67291 | -0.20599 | 0.18768 | 0.39368 | 0.41657 | 0.62256 | 121.3119 | 122.0901 | 0.1236 | 122.1725 | 4.4312 | -0.20599 | 122.0901 | 0.1236 | 4.4312 | 121.3119 | 122.1725 | -122.2549 | -122.1909
923.4531 | 122.049 | -0.25177 | 121.7651 | -0.0049592 | 0.018666 | 0.0186 | -0.00017952 | 0.063547 | -0.0065775 | 0.069116 | -0.14648 | 121.8475 | -0.55389 | 0.045776 | 121.0648 | 4.1885 | 0.14191 | 0.3479 | 121.9666 | -0.45776 | -0.30212 | 0.082397 | 0.10529 | 0.29755 | -0.70038 | -0.20599 | 0.20142 | 0.40741 | 0.39368 | 0.59967 | 121.3165 | 122.0993 | 0.10529 | 122.2183 | 4.4403 | -0.20599 | 122.0993 | 0.10529 | 4.4403 | 121.3165 | 122.2183 | -122.319 | -122.2229
925.2031 | 121.9803 | -0.27924 | 121.7697 | -0.0049592 | 0.017812 | 0.015182 | -0.0065881 | 0.060983 | -0.0052957 | 0.068475 | -0.10986 | 121.8338 | -0.51727 | 0.10529 | 121.1472 | 4.2709 | 0.11444 | 0.46692 | 121.9254 | -0.4303 | -0.23804 | 0.064087 | 0.16937 | 0.38452 | -0.62256 | -0.15106 | 0.15564 | 0.40741 | 0.39368 | 0.74615 | 121.4264 | 122.113 | 0.16937 | 122.2046 | 4.5502 | -0.15106 | 122.113 | 0.16937 | 4.5502 | 121.4264 | 122.2046 | -122.287 | -122.2
926.9531 | 122.1085 | -0.22888 | 121.7743 | -0.0049592 | 0.017385 | 0.014755 | -0.00082032 | 0.062692 | -0.0076455 | 0.068475 | -0.20142 | 121.9116 | -0.53101 | -0.022888 | 121.0419 | 4.1199 | 0.11444 | 0.22888 | 121.9574 | -0.45776 | -0.30212 | 0.13733 | 0.027466 | 0.20599 | -0.73242 | -0.22888 | 0.1831 | 0.32959 | 0.34332 | 0.45776 | 121.2708 | 122.1405 | 0.027466 | 122.1863 | 4.3488 | -0.22888 | 122.1405 | 0.027466 | 4.3488 | 121.2708 | 122.1863 | -122.3053 | -122.2321
928.6406 | 121.9803 | -0.28381 | 121.8155 | -0.0049592 | 0.019734 | 0.012405 | -0.0061609 | 0.061197 | -0.0046549 | 0.067407 | -0.09613 | 121.875 | -0.48981 | 0.10529 | 121.1884 | 4.2984 | 0.018311 | 0.44403 | 121.9482 | -0.42572 | -0.20599 | 0.059509 | 0.18768 | 0.3891 | -0.62714 | -0.14191 | 0.13275 | 0.39368 | 0.30212 | 0.72784 | 121.4722 | 122.1588 | 0.18768 | 122.2321 | 4.5822 | -0.14191 | 122.1588 | 0.18768 | 4.5822 | 121.4722 | 122.2321 | -122.3053 | -122.2412
930.3906 | 122.0169 | -0.28381 | 121.8201 | 0.0026703 | 0.017171 | 0.01326 | -0.0050927 | 0.062051 | -0.0055093 | 0.068902 | -0.10529 | 121.875 | -0.49439 | 0.07782 | 121.138 | 4.248 | -0.064087 | 0.35248 | 121.9254 | -0.41657 | -0.21057 | 0.054932 | 0.17853 | 0.36163 | -0.68207 | -0.13275 | 0.10529 | 0.3891 | 0.21973 | 0.63629 | 121.4218 | 122.1588 | 0.17853 | 122.2092 | 4.5319 | -0.13275 | 122.1588 | 0.17853 | 4.5319 | 121.4218 | 122.2092 | -122.3145 | -122.2366
932.1562 | 122.0123 | -0.27466 | 121.8384 | -0.012589 | 0.018239 | 0.012832 | -0.0050927 | 0.06141 | -0.0061503 | 0.067193 | -0.09613 | 121.8796 | -0.48523 | 0.12817 | 121.1929 | 4.2984 | -0.004578 | 0.46234 | 121.962 | -0.4303 | -0.21057 | 0.041199 | 0.17853 | 0.40283 | -0.64545 | -0.15564 | 0.1236 | 0.3891 | 0.27008 | 0.737 | 121.4676 | 122.1542 | 0.17853 | 122.2366 | 4.5731 | -0.15564 | 122.1542 | 0.17853 | 4.5731 | 121.4676 | 122.2366 | -122.3236 | -122.2687
933.8906 | 122.1268 | -0.24719 | 121.788 | -0.0049592 | 0.022512 | 0.012192 | 0.0019569 | 0.061624 | -0.0082865 | 0.06762 | -0.1831 | 121.9757 | -0.54016 | 0.022888 | 121.1197 | 4.2252 | 0.23346 | 0.37994 | 122.0352 | -0.44861 | -0.29297 | 0.18768 | 0.064087 | 0.27008 | -0.66833 | -0.20142 | 0.24719 | 0.35706 | 0.48065 | 0.62714 | 121.3669 | 122.2229 | 0.064087 | 122.2824 | 4.4724 | -0.20142 | 122.2229 | 0.064087 | 4.4724 | 121.3669 | 122.2824 | -122.3282 | -122.2366
935.5938 | 122.0032 | -0.29297 | 121.843 | 0.0103 | 0.01888 | 0.014114 | -0.0050927 | 0.063119 | -0.0038003 | 0.069116 | -0.091553 | 121.9208 | -0.48981 | 0.12817 | 121.2296 | 4.3304 | 0 | 0.46234 | 121.9803 | -0.4303 | -0.19684 | 0.077819 | 0.20142 | 0.42114 | -0.6134 | -0.13733 | 0.13733 | 0.39825 | 0.29297 | 0.75531 | 121.5225 | 122.2137 | 0.20142 | 122.2733 | 4.6234 | -0.13733 | 122.2137 | 0.20142 | 4.6234 | 121.5225 | 122.2733 | -122.3328 | -122.2733
937.3438 | 122.0764 | -0.28381 | 121.8658 | 0.0026703 | 0.017812 | 0.013046 | -0.0033837 | 0.062265 | -0.0042277 | 0.068688 | -0.15106 | 121.9116 | -0.52185 | 0.036621 | 121.1563 | 4.2389 | -0.013733 | 0.31128 | 121.9894 | -0.44403 | -0.23804 | 0.045776 | 0.13275 | 0.32043 | -0.70953 | -0.16022 | 0.1236 | 0.37079 | 0.27008 | 0.59509 | 121.4401 | 122.1954 | 0.13275 | 122.2733 | 4.5227 | -0.16022 | 122.1954 | 0.13275 | 4.5227 | 121.4401 | 122.2733 | -122.3877 | -122.3099
939.0781 | 122.049 | -0.31128 | 121.8384 | -0.012589 | 0.020589 | 0.012832 | -0.00060672 | 0.060983 | -0.0055093 | 0.066552 | -0.10529 | 121.9254 | -0.5127 | 0.1236 | 121.225 | 4.3259 | 0.059509 | 0.48065 | 121.994 | -0.45776 | -0.20142 | 0.086975 | 0.20599 | 0.43487 | -0.6134 | -0.14649 | 0.15564 | 0.40741 | 0.37079 | 0.79193 | 121.5363 | 122.2366 | 0.20599 | 122.3053 | 4.6371 | -0.14649 | 122.2366 | 0.20599 | 4.6371 | 121.5363 | 122.3053 | -122.3511 | -122.2961
940.8281 | 122.0306 | -0.3067 | 121.8246 | -0.012589 | 0.018453 | 0.011978 | -0.0021021 | 0.059701 | -0.0044413 | 0.067193 | -0.1236 | 121.9299 | -0.5127 | 0.09613 | 121.2112 | 4.3396 | 0.018311 | 0.48523 | 121.9986 | -0.43945 | -0.20599 | 0.10529 | 0.18311 | 0.40283 | -0.6134 | -0.13275 | 0.17395 | 0.3891 | 0.32501 | 0.79193 | 121.5179 | 122.2366 | 0.18311 | 122.3053 | 4.6463 | -0.13275 | 122.2366 | 0.18311 | 4.6463 | 121.5179 | 122.3053 | -122.3373 | -122.2641
942.5156 | 122.049 | -0.32044 | 121.8384 | -0.0049592 | 0.01888 | 0.01326 | 0.0019569 | 0.063119 | -0.0072183 | 0.06997 | -0.11444 | 121.9345 | -0.52643 | 0.073242 | 121.1838 | 4.2984 | -0.086975 | 0.3479 | 122.0032 | -0.44861 | -0.20599 | 0.09613 | 0.20599 | 0.39368 | -0.6546 | -0.12817 | 0.16479 | 0.41199 | 0.23346 | 0.66834 | 121.5042 | 122.2549 | 0.20599 | 122.3236 | 4.6188 | -0.12817 | 122.2549 | 0.20599 | 4.6188 | 121.5042 | 122.3236 | -122.3648 | -122.287
944.2656 | 122.0764 | -0.31128 | 121.8384 | -0.0049592 | 0.017812 | 0.012832 | -0.00060672 | 0.058633 | -0.0035867 | 0.067407 | -0.14191 | 121.9162 | -0.51727 | 0.068665 | 121.1792 | 4.3304 | 0.11444 | 0.4715 | 121.9894 | -0.48065 | -0.20599 | 0.07782 | 0.16937 | 0.37994 | -0.65918 | -0.16937 | 0.15106 | 0.37537 | 0.42572 | 0.78278 | 121.4905 | 122.2275 | 0.16937 | 122.3007 | 4.6417 | -0.16937 | 122.2275 | 0.16937 | 4.6417 | 121.4905 | 122.3007 | -122.3557 | -122.319
946.0156 | 122.1405 | -0.28839 | 121.8063 | -0.012589 | 0.020803 | 0.010696 | 0.0019569 | 0.063119 | -0.0065775 | 0.068048 | -0.20142 | 121.907 | -0.58136 | 0.013733 | 121.138 | 4.2755 | 0.15564 | 0.39825 | 122.0032 | -0.50354 | -0.29297 | 0.10071 | 0.086975 | 0.30212 | -0.66833 | -0.21515 | 0.19684 | 0.37994 | 0.44403 | 0.68664 | 121.4264 | 122.1954 | 0.086975 | 122.2916 | 4.5639 | -0.21515 | 122.1954 | 0.086975 | 4.5639 | 121.4264 | 122.2916 | -122.3877 | -122.3099
947.7031 | 122.2183 | -0.30212 | 121.7651 | -0.012589 | 0.018025 | 0.011764 | -0.00017952 | 0.063333 | -0.0055093 | 0.069116 | -0.27008 | 121.9666 | -0.59509 | -0.073242 | 121.0648 | 4.1748 | 0.1236 | 0.23346 | 122.0169 | -0.52185 | -0.29297 | 0.20142 | 0.032043 | 0.22888 | -0.70038 | -0.21973 | 0.25177 | 0.32501 | 0.42572 | 0.53558 | 121.3669 | 122.2687 | 0.032043 | 122.319 | 4.4769 | -0.21973 | 122.2687 | 0.032043 | 4.4769 | 121.3669 | 122.319 | -122.3602 | -122.287
949.4531 | 122.0535 | -0.35248 | 121.8475 | -0.012589 | 0.018666 | 0.012405 | -0.0076563 | 0.061624 | -0.0040139 | 0.070611 | -0.15106 | 121.907 | -0.55847 | 0.07782 | 121.2296 | 4.3625 | 0.022888 | 0.46234 | 121.9711 | -0.47607 | -0.20599 | 0.059509 | 0.20142 | 0.4303 | -0.61798 | -0.1236 | 0.1236 | 0.40741 | 0.37537 | 0.81482 | 121.582 | 122.2595 | 0.20142 | 122.3236 | 4.715 | -0.1236 | 122.2595 | 0.20142 | 4.715 | 121.582 | 122.3236 | -122.406 | -122.3236
951.2031 | 122.168 | -0.3067 | 121.8475 | 0.0026703 | 0.019521 | 0.014541 | 0.00067508 | 0.063547 | -0.0033731 | 0.068475 | -0.22888 | 121.9437 | -0.57678 | -0.022888 | 121.1105 | 4.248 | 0 | 0.28839 | 122.049 | -0.48523 | -0.27008 | 0.096131 | 0.07782 | 0.28381 | -0.737 | -0.17853 | 0.20142 | 0.3479 | 0.3067 | 0.59509 | 121.4172 | 122.2504 | 0.07782 | 122.3557 | 4.5547 | -0.17853 | 122.2504 | 0.07782 | 4.5547 | 121.4172 | 122.3557 | -122.4243 | -122.3328
952.9531 | 122.2137 | -0.31128 | 121.7972 | -0.012589 | 0.021016 | 0.012405 | 0.0019569 | 0.062478 | -0.0063639 | 0.069543 | -0.23804 | 121.9391 | -0.59052 | -0.068665 | 121.1014 | 4.2206 | 0.14648 | 0.28839 | 122.0352 | -0.50354 | -0.27924 | 0.14191 | 0.073242 | 0.24261 | -0.6958 | -0.19226 | 0.23804 | 0.35248 | 0.45776 | 0.59967 | 121.4127 | 122.2504 | 0.073242 | 122.3465 | 4.5319 | -0.19226 | 122.2504 | 0.073242 | 4.5319 | 121.4127 | 122.3465 | -122.3877 | -122.3007
954.6406 | 122.1497 | -0.32501 | 121.8292 | -0.012589 | 0.017385 | 0.011551 | -0.0070153 | 0.061838 | -0.0055093 | 0.067834 | -0.20599 | 121.9711 | -0.54474 | -0.027466 | 121.1517 | 4.2801 | 0.027466 | 0.31586 | 121.9894 | -0.48981 | -0.21973 | 0.14191 | 0.11902 | 0.29755 | -0.67749 | -0.16479 | 0.16022 | 0.33874 | 0.35248 | 0.64087 | 121.4767 | 122.2961 | 0.11902 | 122.3145 | 4.6051 | -0.16479 | 122.2961 | 0.11902 | 4.6051 | 121.4767 | 122.3145 | -122.374 | -122.319
956.4062 | 122.1451 | -0.34332 | 121.8567 | -0.012589 | 0.019307 | 0.014114 | -0.0042383 | 0.059915 | -0.0042277 | 0.069116 | -0.21057 | 121.9299 | -0.54016 | 0 | 121.1746 | 4.2984 | 0.009155 | 0.31128 | 122.0078 | -0.49896 | -0.19684 | 0.073243 | 0.13275 | 0.34332 | -0.68207 | -0.15564 | 0.15106 | 0.32959 | 0.35248 | 0.6546 | 121.5179 | 122.2733 | 0.13275 | 122.3511 | 4.6417 | -0.15564 | 122.2733 | 0.13275 | 4.6417 | 121.5179 | 122.3511 | -122.3969 | -122.3557
958.1562 | 122.2275 | -0.31128 | 121.8338 | -0.0049592 | 0.018239 | 0.015396 | 0.00046148 | 0.063333 | -0.0070047 | 0.068261 | -0.27924 | 121.9528 | -0.60425 | -0.086975 | 121.0785 | 4.2114 | 0.14191 | 0.25177 | 122.0901 | -0.50812 | -0.29297 | 0.11902 | 0.032043 | 0.2243 | -0.75531 | -0.19684 | 0.25635 | 0.32501 | 0.45319 | 0.56305 | 121.3898 | 122.2641 | 0.032043 | 122.4014 | 4.5227 | -0.19684 | 122.2641 | 0.032043 | 4.5227 | 121.3898 | 122.4014 | -122.438 | -122.3419
959.8906 | 122.2229 | -0.29755 | 121.8292 | -0.0049592 | 0.019307 | 0.013046 | -0.0010339 | 0.062051 | -0.0057229 | 0.06762 | -0.25635 | 122.0261 | -0.60883 | -0.050354 | 121.1243 | 4.2847 | 0.24261 | 0.36621 | 122.0627 | -0.52185 | -0.31128 | 0.19684 | 0.041198 | 0.24719 | -0.70496 | -0.2243 | 0.23346 | 0.35248 | 0.54016 | 0.66376 | 121.4218 | 122.3236 | 0.041198 | 122.3602 | 4.5822 | -0.2243 | 122.3236 | 0.041198 | 4.5822 | 121.4218 | 122.3602 | -122.438 | -122.3511
961.6406 | 122.2275 | -0.3067 | 121.8613 | 0.0026703 | 0.018025 | 0.01091 | -0.0033837 | 0.062051 | -0.0055093 | 0.066339 | -0.27008 | 122.0352 | -0.5722 | -0.059509 | 121.138 | 4.2938 | 0.24261 | 0.37079 | 122.0673 | -0.52185 | -0.2655 | 0.17395 | 0.036621 | 0.24719 | -0.72327 | -0.21515 | 0.20599 | 0.30212 | 0.54932 | 0.67749 | 121.4447 | 122.3419 | 0.036621 | 122.374 | 4.6005 | -0.21515 | 122.3419 | 0.036621 | 4.6005 | 121.4447 | 122.374 | -122.4335 | -122.3831
963.3906 | 122.2321 | -0.30212 | 121.8384 | -0.0049592 | 0.019521 | 0.010269 | -0.0021021 | 0.061624 | -0.0063639 | 0.068475 | -0.27466 | 122.0306 | -0.57678 | -0.050354 | 121.1288 | 4.2938 | 0.2655 | 0.35706 | 122.081 | -0.52185 | -0.27466 | 0.19226 | 0.027466 | 0.25177 | -0.70953 | -0.21973 | 0.24262 | 0.30212 | 0.56763 | 0.65918 | 121.431 | 122.3328 | 0.027466 | 122.3831 | 4.5959 | -0.21973 | 122.3328 | 0.027466 | 4.5959 | 121.431 | 122.3831 | -122.4152 | -122.3602
965.0781 | 122.1588 | -0.32044 | 121.8796 | 0.017929 | 0.019094 | 0.010483 | -0.0014611 | 0.060769 | -0.0029459 | 0.069116 | -0.1831 | 121.962 | -0.52643 | 0.013733 | 121.2021 | 4.3259 | -0.036621 | 0.32044 | 122.0306 | -0.45319 | -0.20599 | 0.082397 | 0.13733 | 0.33417 | -0.67749 | -0.13275 | 0.15106 | 0.34332 | 0.28381 | 0.64087 | 121.5225 | 122.2824 | 0.13733 | 122.3511 | 4.6463 | -0.13275 | 122.2824 | 0.13733 | 4.6463 | 121.5225 | 122.3511 | -122.406 | -122.3328
966.8594 | 122.1359 | -0.34332 | 121.8704 | -0.0049592 | 0.019307 | 0.016678 | -0.0016747 | 0.06141 | -0.0063639 | 0.068688 | -0.16022 | 121.994 | -0.54932 | 0.041199 | 121.2341 | 4.3488 | -0.073242 | 0.31586 | 122.0673 | -0.46234 | -0.20599 | 0.1236 | 0.18311 | 0.38452 | -0.63629 | -0.11902 | 0.19684 | 0.3891 | 0.27008 | 0.65918 | 121.5775 | 122.3373 | 0.18311 | 122.4106 | 4.6921 | -0.11902 | 122.3373 | 0.18311 | 4.6921 | 121.5775 | 122.4106 | -122.4197 | -122.3328
968.5469 | 122.2595 | -0.30212 | 121.8521 | 0.0103 | 0.019307 | 0.0087735 | 0.0021705 | 0.063547 | -0.0061503 | 0.068688 | -0.2655 | 121.9849 | -0.58136 | -0.068665 | 121.138 | 4.2709 | 0.15564 | 0.24719 | 122.0993 | -0.49896 | -0.27924 | 0.13275 | 0.036621 | 0.23346 | -0.71411 | -0.19684 | 0.24719 | 0.31586 | 0.45776 | 0.54932 | 121.4401 | 122.287 | 0.036621 | 122.4014 | 4.5731 | -0.19684 | 122.287 | 0.036621 | 4.5731 | 121.4401 | 122.4014 | -122.4335 | -122.3511
970.2969 | 122.1771 | -0.32044 | 121.9162 | 0.0026703 | 0.017171 | 0.0092007 | -0.0053063 | 0.062906 | -0.0025187 | 0.068048 | -0.21515 | 121.994 | -0.54474 | 0.009155 | 121.225 | 4.3442 | 0.018311 | 0.35706 | 122.0856 | -0.46692 | -0.2243 | 0.07782 | 0.10529 | 0.32959 | -0.69122 | -0.14648 | 0.16937 | 0.32959 | 0.33875 | 0.67749 | 121.5454 | 122.3145 | 0.10529 | 122.406 | 4.6646 | -0.14648 | 122.3145 | 0.10529 | 4.6646 | 121.5454 | 122.406 | -122.4609 | -122.3831
972.0469 | 122.1405 | -0.3479 | 121.9025 | 0.0026703 | 0.018666 | 0.014328 | -0.00082032 | 0.063333 | -0.0059365 | 0.068902 | -0.14648 | 121.962 | -0.53101 | 0.050354 | 121.2479 | 4.3716 | -0.086975 | 0.35706 | 122.0535 | -0.46692 | -0.18311 | 0.059509 | 0.20142 | 0.39825 | -0.6546 | -0.11902 | 0.15106 | 0.38452 | 0.26092 | 0.70496 | 121.5958 | 122.3099 | 0.20142 | 122.4014 | 4.7195 | -0.11902 | 122.3099 | 0.20142 | 4.7195 | 121.5958 | 122.4014 | -122.4335 | -122.3694
973.8125 | 122.1954 | -0.33417 | 121.9208 | -0.0049592 | 0.018025 | 0.0083463 | -0.0055199 | 0.063333 | -0.0038003 | 0.069757 | -0.20599 | 122.0123 | -0.53558 | -0.013733 | 121.2067 | 4.3442 | 0.013733 | 0.32959 | 122.0901 | -0.48981 | -0.20142 | 0.091553 | 0.12817 | 0.32043 | -0.71411 | -0.15564 | 0.16937 | 0.32959 | 0.3479 | 0.66376 | 121.5408 | 122.3465 | 0.12817 | 122.4243 | 4.6783 | -0.15564 | 122.3465 | 0.12817 | 4.6783 | 121.5408 | 122.4243 | -122.4564 | -122.4106
975.5156 | 122.287 | -0.29297 | 121.8658 | -0.0049592 | 0.017598 | 0.015823 | 0.0019569 | 0.063547 | -0.0080729 | 0.069543 | -0.27008 | 122.0215 | -0.58594 | -0.086975 | 121.1243 | 4.2709 | 0.13733 | 0.24261 | 122.1268 | -0.51727 | -0.29297 | 0.15564 | 0.022888 | 0.20599 | -0.74158 | -0.2243 | 0.26093 | 0.31586 | 0.4303 | 0.53558 | 121.4172 | 122.3145 | 0.022888 | 122.4197 | 4.5639 | -0.2243 | 122.3145 | 0.022888 | 4.5639 | 121.4172 | 122.4197 | -122.4518 | -122.3831
977.2656 | 122.2641 | -0.29755 | 121.8704 | 0.0103 | 0.019521 | 0.014969 | -0.0021021 | 0.064401 | -0.0080729 | 0.068902 | -0.27008 | 122.0169 | -0.5722 | -0.050354 | 121.1517 | 4.2847 | 0.07782 | 0.25177 | 122.1313 | -0.50354 | -0.27466 | 0.14648 | 0.027465 | 0.24719 | -0.71869 | -0.20599 | 0.26093 | 0.30212 | 0.37537 | 0.54932 | 121.4493 | 122.3145 | 0.027465 | 122.4289 | 4.5822 | -0.20599 | 122.3145 | 0.027465 | 4.5822 | 121.4493 | 122.4289 | -122.4426 | -122.374
979 | 122.168 | -0.34332 | 121.9162 | -0.0049592 | 0.018666 | 0.013473 | -0.0055199 | 0.062692 | -0.0029459 | 0.068475 | -0.15564 | 121.9986 | -0.52185 | 0.027466 | 121.257 | 4.39 | -0.073242 | 0.3479 | 122.0581 | -0.4715 | -0.17853 | 0.082397 | 0.18768 | 0.37079 | -0.65918 | -0.12817 | 0.14191 | 0.36621 | 0.27008 | 0.69122 | 121.6003 | 122.3419 | 0.18768 | 122.4014 | 4.7333 | -0.12817 | 122.3419 | 0.18768 | 4.7333 | 121.6003 | 122.4014 | -122.4381 | -122.3877
980.6875 | 122.2687 | -0.29297 | 121.875 | 0.0026703 | 0.017385 | 0.012619 | 0.00024788 | 0.063974 | -0.0085001 | 0.068688 | -0.27924 | 122.0352 | -0.59509 | -0.068665 | 121.1746 | 4.335 | 0.25177 | 0.35706 | 122.1451 | -0.50354 | -0.30212 | 0.16022 | 0.013733 | 0.2243 | -0.70038 | -0.21057 | 0.27008 | 0.31586 | 0.54474 | 0.65002 | 121.4676 | 122.3282 | 0.013733 | 122.4381 | 4.628 | -0.21057 | 122.3282 | 0.013733 | 4.628 | 121.4676 | 122.4381 | -122.4701 | -122.3785
982.4531 | 122.3007 | -0.31128 | 121.8796 | 0.0026703 | 0.018239 | 0.017746 | -0.00082032 | 0.061624 | -0.0065775 | 0.069329 | -0.2655 | 122.0352 | -0.56305 | -0.082397 | 121.1472 | 4.2801 | 0.14648 | 0.25635 | 122.1176 | -0.48981 | -0.25177 | 0.15564 | 0.045776 | 0.22888 | -0.73242 | -0.17853 | 0.23804 | 0.29755 | 0.45776 | 0.56763 | 121.4584 | 122.3465 | 0.045776 | 122.4289 | 4.5914 | -0.17853 | 122.3465 | 0.045776 | 4.5914 | 121.4584 | 122.4289 | -122.4426 | -122.3694
984.1875 | 122.1451 | -0.35248 | 121.9208 | -0.012589 | 0.020375 | 0.010269 | -0.0057337 | 0.061197 | -0.0044413 | 0.070184 | -0.16937 | 122.0398 | -0.52185 | 0.045776 | 121.2936 | 4.4815 | 0.004578 | 0.45319 | 122.081 | -0.47607 | -0.16937 | 0.11902 | 0.18311 | 0.39825 | -0.62714 | -0.1236 | 0.16022 | 0.35248 | 0.35706 | 0.80566 | 121.6461 | 122.3923 | 0.18311 | 122.4335 | 4.834 | -0.1236 | 122.3923 | 0.18311 | 4.834 | 121.6461 | 122.4335 | -122.4426 | -122.3969
985.9375 | 122.2046 | -0.34332 | 121.9162 | 0.0026703 | 0.017812 | 0.014755 | -0.0031701 | 0.061838 | -0.0063639 | 0.068475 | -0.1831 | 122.0398 | -0.56305 | 0.009155 | 121.2616 | 4.4174 | 0.17853 | 0.4303 | 122.1313 | -0.5127 | -0.21973 | 0.1236 | 0.16022 | 0.35248 | -0.6546 | -0.16937 | 0.21515 | 0.37994 | 0.52185 | 0.77362 | 121.6049 | 122.3831 | 0.16022 | 122.4747 | 4.7607 | -0.16937 | 122.3831 | 0.16022 | 4.7607 | 121.6049 | 122.4747 | -122.4792 | -122.4289
987.6406 | 122.287 | -0.28839 | 121.8796 | 0.0103 | 0.01888 | 0.010269 | -0.00082032 | 0.060983 | -0.0059365 | 0.069116 | -0.28381 | 122.0398 | -0.58594 | -0.064087 | 121.1792 | 4.3716 | 0.28381 | 0.37079 | 122.1268 | -0.51727 | -0.29755 | 0.16022 | 0.004578 | 0.2243 | -0.70038 | -0.22888 | 0.24719 | 0.30212 | 0.5722 | 0.65918 | 121.4676 | 122.3282 | 0.004578 | 122.4152 | 4.66 | -0.22888 | 122.3282 | 0.004578 | 4.66 | 121.4676 | 122.4152 | -122.4655 | -122.3969
989.4062 | 122.2137 | -0.33875 | 121.9116 | 0.0026703 | 0.017598 | 0.01091 | -0.0035973 | 0.059488 | -0.0061503 | 0.067834 | -0.20142 | 122.0306 | -0.56305 | 0.009155 | 121.2662 | 4.4312 | 0.17853 | 0.43488 | 122.1451 | -0.52643 | -0.2243 | 0.11902 | 0.13733 | 0.3479 | -0.64545 | -0.18768 | 0.23346 | 0.36163 | 0.51727 | 0.77362 | 121.6049 | 122.3694 | 0.13733 | 122.4838 | 4.7699 | -0.18768 | 122.3694 | 0.13733 | 4.7699 | 121.6049 | 122.4838 | -122.4747 | -122.438
991.0938 | 122.2733 | -0.33875 | 121.8796 | -0.0049592 | 0.020162 | 0.015182 | -0.00017952 | 0.063119 | -0.0044413 | 0.068048 | -0.25635 | 122.0901 | -0.59967 | -0.059509 | 121.1929 | 4.3716 | 0.041199 | 0.2655 | 122.1176 | -0.51727 | -0.26093 | 0.21057 | 0.082397 | 0.27924 | -0.68665 | -0.17853 | 0.23804 | 0.34332 | 0.37994 | 0.60425 | 121.5317 | 122.4289 | 0.082397 | 122.4564 | 4.7104 | -0.17853 | 122.4289 | 0.082397 | 4.7104 | 121.5317 | 122.4564 | -122.4792 | -122.3969
992.875 | 122.1542 | -0.35706 | 121.9345 | -0.0049592 | 0.019094 | 0.012192 | -0.0059473 | 0.062051 | -0.0055093 | 0.068688 | -0.16937 | 122.0123 | -0.53558 | 0.054932 | 121.3165 | 4.5227 | -0.004578 | 0.46234 | 122.113 | -0.48065 | -0.17853 | 0.07782 | 0.18768 | 0.41199 | -0.61798 | -0.1236 | 0.17853 | 0.36621 | 0.35248 | 0.8194 | 121.6736 | 122.3694 | 0.18768 | 122.4701 | 4.8798 | -0.1236 | 122.3694 | 0.18768 | 4.8798 | 121.6736 | 122.4701 | -122.4701 | -122.4152
994.5625 | 122.1909 | -0.36621 | 121.9208 | -0.0049592 | 0.020375 | 0.010055 | -0.00060672 | 0.065256 | -0.0061503 | 0.067193 | -0.15106 | 122.0352 | -0.55389 | 0.027466 | 121.2753 | 4.4312 | -0.068665 | 0.32501 | 122.0993 | -0.48065 | -0.18768 | 0.11444 | 0.21515 | 0.39368 | -0.64545 | -0.11444 | 0.17853 | 0.40283 | 0.29755 | 0.69122 | 121.6415 | 122.4014 | 0.21515 | 122.4655 | 4.7974 | -0.11444 | 122.4014 | 0.21515 | 4.7974 | 121.6415 | 122.4655 | -122.4747 | -122.4014
996.3281 | 122.3145 | -0.29755 | 121.8842 | 0.0026703 | 0.020803 | 0.010696 | -0.0027429 | 0.061197 | -0.0052957 | 0.066979 | -0.27008 | 122.0993 | -0.59052 | -0.068665 | 121.1884 | 4.3716 | 0.28381 | 0.35248 | 122.1771 | -0.52185 | -0.29297 | 0.21515 | 0.027465 | 0.22888 | -0.6958 | -0.2243 | 0.29297 | 0.32043 | 0.58136 | 0.65002 | 121.4859 | 122.3969 | 0.027465 | 122.4747 | 4.6692 | -0.2243 | 122.3969 | 0.027465 | 4.6692 | 121.4859 | 122.4747 | -122.4747 | -122.406
998.0781 | 122.168 | -0.34332 | 121.9574 | -0.0049592 | 0.018453 | 0.014755 | -0.0055199 | 0.062906 | -0.0046549 | 0.067407 | -0.13733 | 122.049 | -0.53101 | 0.045776 | 121.3394 | 4.509 | 0.036621 | 0.45776 | 122.1176 | -0.48065 | -0.18768 | 0.091553 | 0.20599 | 0.3891 | -0.61798 | -0.13733 | 0.16022 | 0.39368 | 0.37994 | 0.80109 | 121.6827 | 122.3923 | 0.20599 | 122.4609 | 4.8523 | -0.13733 | 122.3923 | 0.20599 | 4.8523 | 121.6827 | 122.4609 | -122.4884 | -122.438
999.8438 | 122.287 | -0.3067 | 121.8933 | 0.0026703 | 0.017171 | 0.013046 | 3.4284e-05 | 0.06141 | -0.0072183 | 0.067834 | -0.24261 | 122.0627 | -0.5722 | -0.013733 | 121.2341 | 4.4128 | 0.20142 | 0.38452 | 122.1634 | -0.50812 | -0.2655 | 0.16937 | 0.064087 | 0.29297 | -0.65918 | -0.20142 | 0.27008 | 0.32959 | 0.50812 | 0.69122 | 121.5408 | 122.3694 | 0.064087 | 122.4701 | 4.7195 | -0.20142 | 122.3694 | 0.064087 | 4.7195 | 121.5408 | 122.4701 | -122.4655 | -122.4014
1001.5469 | 122.2961 | -0.33875 | 121.8979 | -0.0049592 | 0.019307 | 0.014328 | 0.00067508 | 0.064187 | -0.0061503 | 0.067834 | -0.24261 | 122.0718 | -0.57678 | -0.050354 | 121.2021 | 4.3671 | 0.17395 | 0.31586 | 122.168 | -0.52643 | -0.23804 | 0.17395 | 0.09613 | 0.28839 | -0.6958 | -0.18768 | 0.27008 | 0.33417 | 0.5127 | 0.6546 | 121.5408 | 122.4106 | 0.09613 | 122.5067 | 4.7058 | -0.18768 | 122.4106 | 0.09613 | 4.7058 | 121.5408 | 122.5067 | -122.4747 | -122.4243
1003.2344 | 122.3236 | -0.30212 | 121.8933 | -0.012589 | 0.020162 | 0.016037 | -0.0021021 | 0.060769 | -0.0048685 | 0.069116 | -0.26093 | 122.0993 | -0.58136 | -0.068665 | 121.2204 | 4.4037 | 0.25635 | 0.37994 | 122.1634 | -0.52643 | -0.27924 | 0.20599 | 0.041199 | 0.23346 | -0.67291 | -0.2243 | 0.27008 | 0.32043 | 0.55847 | 0.68207 | 121.5225 | 122.4014 | 0.041199 | 122.4655 | 4.7058 | -0.2243 | 122.4014 | 0.041199 | 4.7058 | 121.5225 | 122.4655 | -122.4747 | -122.4197
1004.9844 | 122.1909 | -0.35706 | 121.9345 | -0.0049592 | 0.019094 | 0.010483 | -0.0023157 | 0.062906 | -0.0048685 | 0.069757 | -0.16022 | 122.0581 | -0.53101 | 0.045776 | 121.2982 | 4.4678 | -0.086975 | 0.36163 | 122.0993 | -0.4715 | -0.17395 | 0.1236 | 0.19684 | 0.40283 | -0.63629 | -0.11444 | 0.16479 | 0.37079 | 0.27008 | 0.71869 | 121.6553 | 122.4152 | 0.19684 | 122.4564 | 4.8248 | -0.11444 | 122.4152 | 0.19684 | 4.8248 | 121.6553 | 122.4564 | -122.4655 | -122.406
1006.6719 | 122.3373 | -0.30212 | 121.9116 | -0.0049592 | 0.019521 | 0.014969 | 0.00088868 | 0.063547 | -0.0050821 | 0.068261 | -0.28381 | 122.081 | -0.58136 | -0.082397 | 121.2067 | 4.3488 | 0.1236 | 0.23346 | 122.1588 | -0.49896 | -0.27924 | 0.16937 | 0.018311 | 0.21973 | -0.70496 | -0.19684 | 0.24719 | 0.29755 | 0.42572 | 0.53558 | 121.5088 | 122.3831 | 0.018311 | 122.4609 | 4.6509 | -0.19684 | 122.3831 | 0.018311 | 4.6509 | 121.5088 | 122.4609 | -122.493 | -122.4106
1008.4219 | 122.3099 | -0.31586 | 121.9345 | -0.012589 | 0.019734 | 0.013901 | -0.0010339 | 0.063333 | -0.0042277 | 0.067407 | -0.28839 | 122.1039 | -0.55389 | -0.09613 | 121.2067 | 4.3442 | 0.11902 | 0.23346 | 122.1863 | -0.50354 | -0.23804 | 0.16937 | 0.027466 | 0.21973 | -0.72784 | -0.18768 | 0.25177 | 0.2655 | 0.43488 | 0.54932 | 121.5225 | 122.4197 | 0.027466 | 122.5021 | 4.66 | -0.18768 | 122.4197 | 0.027466 | 4.66 | 121.5225 | 122.5021 | -122.4884 | -122.438
1010.1094 | 122.3007 | -0.30212 | 121.9162 | 0.017929 | 0.016957 | 0.016891 | 3.4284e-05 | 0.062906 | -0.0072183 | 0.068688 | -0.23804 | 122.0856 | -0.54932 | -0.054932 | 121.2158 | 4.4174 | 0.15106 | 0.32044 | 122.1725 | -0.50354 | -0.24719 | 0.16937 | 0.064087 | 0.24719 | -0.70038 | -0.20142 | 0.25635 | 0.31128 | 0.45319 | 0.62256 | 121.5179 | 122.3877 | 0.064087 | 122.4747 | 4.7195 | -0.20142 | 122.3877 | 0.064087 | 4.7195 | 121.5179 | 122.4747 | -122.4655 | -122.4197
1011.8594 | 122.2412 | -0.35248 | 121.9391 | -0.0049592 | 0.015889 | 0.010483 | -0.0082971 | 0.060129 | -0.0033731 | 0.068902 | -0.21973 | 122.049 | -0.53101 | -0.022888 | 121.2799 | 4.4449 | -0.009155 | 0.31586 | 122.1222 | -0.49896 | -0.17853 | 0.10986 | 0.13275 | 0.32959 | -0.65918 | -0.14648 | 0.1831 | 0.31128 | 0.34332 | 0.66834 | 121.6324 | 122.4014 | 0.13275 | 122.4747 | 4.7974 | -0.14648 | 122.4014 | 0.13275 | 4.7974 | 121.6324 | 122.4747 | -122.4701 | -122.438
1013.5469 | 122.3099 | -0.33417 | 121.907 | 0.0026703 | 0.019307 | 0.013473 | -0.00017952 | 0.06141 | -0.0044413 | 0.06762 | -0.2655 | 122.0901 | -0.5722 | -0.068665 | 121.2524 | 4.4403 | 0.24261 | 0.37537 | 122.1771 | -0.49896 | -0.23804 | 0.18311 | 0.068664 | 0.2655 | -0.6546 | -0.1648 | 0.27008 | 0.3067 | 0.57678 | 0.70953 | 121.5866 | 122.4243 | 0.068664 | 122.5113 | 4.7745 | -0.1648 | 122.4243 | 0.068664 | 4.7745 | 121.5866 | 122.5113 | -122.4792 | -122.406
1015.2344 | 122.3145 | -0.3067 | 121.9299 | -0.0049592 | 0.02123 | 0.012192 | -0.0031701 | 0.060129 | -0.0063639 | 0.068902 | -0.27008 | 122.1039 | -0.56305 | -0.064087 | 121.2341 | 4.4312 | 0.25635 | 0.37537 | 122.1954 | -0.50354 | -0.25635 | 0.17395 | 0.036621 | 0.24261 | -0.6958 | -0.19684 | 0.2655 | 0.29297 | 0.56305 | 0.68207 | 121.5408 | 122.4106 | 0.036621 | 122.5021 | 4.7379 | -0.19684 | 122.4106 | 0.036621 | 4.7379 | 121.5408 | 122.5021 | -122.493 | -122.4335
1017 | 122.287 | -0.32501 | 121.962 | 0.0103 | 0.019948 | 0.014114 | 0.00067508 | 0.062265 | -0.0072183 | 0.068902 | -0.2243 | 122.0901 | -0.56305 | -0.009155 | 121.2662 | 4.4724 | 0.16937 | 0.41657 | 122.168 | -0.50812 | -0.23804 | 0.12817 | 0.10071 | 0.31586 | -0.6958 | -0.18311 | 0.20599 | 0.33875 | 0.49439 | 0.74158 | 121.5912 | 122.4152 | 0.10071 | 122.493 | 4.7974 | -0.18311 | 122.4152 | 0.10071 | 4.7974 | 121.5912 | 122.493 | -122.525 | -122.4701
1018.6875 | 122.319 | -0.32044 | 121.9116 | -0.0049592 | 0.020162 | 0.012619 | -0.0042383 | 0.060983 | -0.0048685 | 0.068688 | -0.28839 | 122.1039 | -0.55389 | -0.086975 | 121.2341 | 4.4357 | 0.27466 | 0.37079 | 122.1909 | -0.53101 | -0.23346 | 0.19226 | 0.032044 | 0.23346 | -0.67749 | -0.21057 | 0.27924 | 0.2655 | 0.59509 | 0.69122 | 121.5546 | 122.4243 | 0.032044 | 122.5113 | 4.7562 | -0.21057 | 122.4243 | 0.032044 | 4.7562 | 121.5546 | 122.5113 | -122.4655 | -122.4426
1020.4375 | 122.2412 | -0.35248 | 121.9666 | -0.012589 | 0.01653 | 0.012832 | -0.0050927 | 0.060556 | -0.0044413 | 0.068902 | -0.21057 | 122.0901 | -0.54016 | -0.009155 | 121.2982 | 4.509 | 0.1831 | 0.45319 | 122.1817 | -0.50812 | -0.18768 | 0.1236 | 0.14191 | 0.34332 | -0.66833 | -0.15564 | 0.21515 | 0.32959 | 0.53558 | 0.80566 | 121.6507 | 122.4426 | 0.14191 | 122.5342 | 4.8614 | -0.15564 | 122.4426 | 0.14191 | 4.8614 | 121.6507 | 122.5342 | -122.5067 | -122.4747
1022.1875 | 122.2321 | -0.35248 | 121.9574 | 0.0026703 | 0.016957 | 0.013687 | -0.0018885 | 0.062478 | -0.0067911 | 0.066979 | -0.19226 | 122.0627 | -0.53558 | 0.018311 | 121.3028 | 4.4952 | -0.068665 | 0.34332 | 122.1359 | -0.48065 | -0.18311 | 0.10529 | 0.16022 | 0.37079 | -0.6546 | -0.12817 | 0.17853 | 0.34332 | 0.28381 | 0.6958 | 121.6553 | 122.4152 | 0.16022 | 122.4884 | 4.8477 | -0.12817 | 122.4152 | 0.16022 | 4.8477 | 121.6553 | 122.4884 | -122.493 | -122.438
1023.9375 | 122.2183 | -0.36163 | 121.9299 | -0.0049592 | 0.019521 | 0.01091 | -0.0050927 | 0.062265 | -0.0035867 | 0.068688 | -0.19684 | 122.0947 | -0.54932 | 0.018311 | 121.3486 | 4.5593 | 0.022888 | 0.43945 | 122.1542 | -0.49896 | -0.18768 | 0.1648 | 0.16479 | 0.37994 | -0.58136 | -0.13733 | 0.2243 | 0.35248 | 0.38452 | 0.80109 | 121.7102 | 122.4564 | 0.16479 | 122.5159 | 4.921 | -0.13733 | 122.4564 | 0.16479 | 4.921 | 121.7102 | 122.5159 | -122.4792 | -122.4289
1025.625 | 122.3099 | -0.32501 | 121.9482 | -0.0049592 | 0.016957 | 0.011978 | 0.0021705 | 0.064187 | -0.0065775 | 0.068475 | -0.24261 | 122.1085 | -0.56305 | -0.050354 | 121.2616 | 4.4266 | 0.009155 | 0.28839 | 122.1863 | -0.49896 | -0.23804 | 0.16022 | 0.082397 | 0.27466 | -0.68664 | -0.17395 | 0.23804 | 0.32043 | 0.33417 | 0.6134 | 121.5866 | 122.4335 | 0.082397 | 122.5113 | 4.7516 | -0.17395 | 122.4335 | 0.082397 | 4.7516 | 121.5866 | 122.5113 | -122.5113 | -122.4472
1027.3906 | 122.2092 | -0.36621 | 121.962 | -0.012589 | 0.019094 | 0.0096279 | -0.0078699 | 0.060983 | -0.0046549 | 0.068902 | -0.17853 | 122.0764 | -0.55389 | 0.041199 | 121.3486 | 4.5639 | 0.018311 | 0.4715 | 122.1451 | -0.50812 | -0.18768 | 0.11444 | 0.18768 | 0.40741 | -0.6134 | -0.14191 | 0.18311 | 0.37537 | 0.38452 | 0.83771 | 121.7148 | 122.4426 | 0.18768 | 122.5113 | 4.9301 | -0.14191 | 122.4426 | 0.18768 | 4.9301 | 121.7148 | 122.5113 | -122.5159 | -122.4701
1029.1406 | 122.3236 | -0.32959 | 121.9482 | 0.0103 | 0.020803 | 0.013473 | 0.0013159 | 0.062478 | -0.0070047 | 0.068048 | -0.25177 | 122.0856 | -0.58136 | -0.054932 | 121.2112 | 4.4083 | 0.15564 | 0.32501 | 122.2137 | -0.50354 | -0.25177 | 0.13733 | 0.07782 | 0.27466 | -0.737 | -0.17395 | 0.2655 | 0.32959 | 0.48523 | 0.6546 | 121.5408 | 122.4152 | 0.07782 | 122.5433 | 4.7379 | -0.17395 | 122.4152 | 0.07782 | 4.7379 | 121.5408 | 122.5433 | -122.5296 | -122.4518
1030.9062 | 122.3007 | -0.35248 | 121.9482 | -0.0049592 | 0.015676 | 0.010055 | -0.0074427 | 0.060983 | -0.0063639 | 0.068688 | -0.2655 | 122.0444 | -0.54474 | -0.032043 | 121.2936 | 4.4632 | 0.032043 | 0.32501 | 122.1497 | -0.51727 | -0.19226 | 0.096131 | 0.086975 | 0.32044 | -0.6546 | -0.16479 | 0.20142 | 0.27924 | 0.38452 | 0.67749 | 121.6461 | 122.3969 | 0.086975 | 122.5021 | 4.8157 | -0.16479 | 122.3969 | 0.086975 | 4.8157 | 121.6461 | 122.5021 | -122.493 | -122.4655
1032.5938 | 122.2412 | -0.37537 | 121.994 | -0.0049592 | 0.019734 | 0.0096279 | -0.0021021 | 0.06376 | -0.0040139 | 0.067834 | -0.16937 | 122.0901 | -0.54474 | 0.032043 | 121.3303 | 4.5181 | -0.073242 | 0.35706 | 122.1451 | -0.4715 | -0.16937 | 0.09613 | 0.20599 | 0.40741 | -0.66376 | -0.096131 | 0.15106 | 0.37537 | 0.30212 | 0.73242 | 121.7056 | 122.4655 | 0.20599 | 122.5204 | 4.8935 | -0.096131 | 122.4655 | 0.20599 | 4.8935 | 121.7056 | 122.5204 | -122.5388 | -122.4655
1034.3438 | 122.3007 | -0.33417 | 121.9162 | -0.0049592 | 0.018666 | 0.01326 | -0.00017952 | 0.062478 | -0.0095681 | 0.067834 | -0.22888 | 122.0901 | -0.59052 | -0.013733 | 121.2753 | 4.4907 | 0.16937 | 0.42114 | 122.2321 | -0.50812 | -0.25635 | 0.17395 | 0.10528 | 0.32043 | -0.64087 | -0.17395 | 0.31586 | 0.36163 | 0.50354 | 0.75531 | 121.6095 | 122.4243 | 0.10528 | 122.5662 | 4.8248 | -0.17395 | 122.4243 | 0.10528 | 4.8248 | 121.6095 | 122.5662 | -122.5067 | -122.4243
1036.0938 | 122.2549 | -0.37537 | 121.9986 | -0.0049592 | 0.018666 | 0.015823 | -0.0050927 | 0.06141 | -0.0040139 | 0.069543 | -0.20142 | 122.0947 | -0.55847 | -0.004578 | 121.2845 | 4.4815 | -0.018311 | 0.34332 | 122.1497 | -0.49439 | -0.18311 | 0.096131 | 0.17395 | 0.37079 | -0.71411 | -0.11902 | 0.15106 | 0.35706 | 0.35705 | 0.71869 | 121.6599 | 122.4701 | 0.17395 | 122.525 | 4.8569 | -0.11902 | 122.4701 | 0.17395 | 4.8569 | 121.6599 | 122.525 | -122.5571 | -122.493
1037.875 | 122.2412 | -0.37537 | 121.9437 | -0.012589 | 0.019094 | 0.0098417 | -0.0035973 | 0.060342 | -0.0057229 | 0.068261 | -0.18768 | 122.0764 | -0.56305 | 0.022888 | 121.3211 | 4.5731 | 0.09613 | 0.46692 | 122.1497 | -0.51727 | -0.18768 | 0.13275 | 0.18768 | 0.39825 | -0.62256 | -0.14191 | 0.20599 | 0.37537 | 0.4715 | 0.84228 | 121.6965 | 122.4518 | 0.18768 | 122.525 | 4.9484 | -0.14191 | 122.4518 | 0.18768 | 4.9484 | 121.6965 | 122.525 | -122.5067 | -122.4609
1039.5625 | 122.2504 | -0.39368 | 121.9803 | 0.0026703 | 0.022512 | 0.011978 | -0.0012475 | 0.062906 | -0.0055093 | 0.067193 | -0.17853 | 122.0947 | -0.54016 | 0.036621 | 121.3394 | 4.5227 | -0.09613 | 0.36163 | 122.1634 | -0.48523 | -0.14648 | 0.11444 | 0.21515 | 0.4303 | -0.64087 | -0.091552 | 0.1831 | 0.36163 | 0.29755 | 0.75531 | 121.7331 | 122.4884 | 0.21515 | 122.5571 | 4.9164 | -0.091552 | 122.4884 | 0.21515 | 4.9164 | 121.7331 | 122.5571 | -122.5204 | -122.4655
1041.3125 | 122.3831 | -0.33417 | 121.9528 | 0.0103 | 0.016103 | 0.01091 | 0.00046148 | 0.063119 | -0.0087137 | 0.067834 | -0.29297 | 122.1313 | -0.59967 | -0.09613 | 121.2112 | 4.4174 | 0.11902 | 0.23346 | 122.2595 | -0.52185 | -0.2655 | 0.17853 | 0.041198 | 0.23804 | -0.74158 | -0.18768 | 0.3067 | 0.3067 | 0.45319 | 0.56763 | 121.5454 | 122.4655 | 0.041198 | 122.5937 | 4.7516 | -0.18768 | 122.4655 | 0.041198 | 4.7516 | 121.5454 | 122.5937 | -122.5525 | -122.4747
1043.0781 | 122.3877 | -0.32501 | 121.9528 | 0.0026703 | 0.019948 | 0.011978 | -0.0029565 | 0.06376 | -0.0076455 | 0.068048 | -0.27924 | 122.1405 | -0.60883 | -0.086975 | 121.2296 | 4.422 | 0.17853 | 0.25635 | 122.2275 | -0.53558 | -0.28381 | 0.18768 | 0.045776 | 0.23804 | -0.72327 | -0.21057 | 0.27466 | 0.32959 | 0.50354 | 0.58136 | 121.5546 | 122.4655 | 0.045776 | 122.5525 | 4.747 | -0.21057 | 122.4655 | 0.045776 | 4.747 | 121.5546 | 122.5525 | -122.5616 | -122.4884
1044.8281 | 122.3373 | -0.32501 | 121.9528 | 0.0026703 | 0.019094 | 0.012405 | 0.0011023 | 0.064401 | -0.0067911 | 0.067193 | -0.23804 | 122.1085 | -0.58594 | -0.009155 | 121.2662 | 4.4998 | 0.17395 | 0.3479 | 122.2137 | -0.50354 | -0.26093 | 0.15564 | 0.086975 | 0.31586 | -0.68665 | -0.17853 | 0.26093 | 0.3479 | 0.49896 | 0.67291 | 121.5912 | 122.4335 | 0.086975 | 122.5388 | 4.8248 | -0.17853 | 122.4335 | 0.086975 | 4.8248 | 121.5912 | 122.5388 | -122.5388 | -122.4564
1046.5156 | 122.319 | -0.33417 | 121.9391 | -0.0049592 | 0.01888 | 0.011337 | -0.0025293 | 0.062478 | -0.0087137 | 0.069116 | -0.21973 | 122.1313 | -0.5722 | -0.013733 | 121.3074 | 4.5181 | 0.15564 | 0.39368 | 122.2046 | -0.50354 | -0.23804 | 0.19226 | 0.11444 | 0.32043 | -0.63171 | -0.16937 | 0.2655 | 0.35248 | 0.48981 | 0.72784 | 121.6415 | 122.4655 | 0.11444 | 122.5388 | 4.8523 | -0.16937 | 122.4655 | 0.11444 | 4.8523 | 121.6415 | 122.5388 | -122.5113 | -122.4426
1048.2656 | 122.3831 | -0.32044 | 121.9711 | 0.0026703 | 0.018666 | 0.010696 | -0.0033837 | 0.064828 | -0.0063639 | 0.067407 | -0.27924 | 122.1313 | -0.58136 | -0.11444 | 121.2479 | 4.4357 | 0.082397 | 0.25177 | 122.2183 | -0.52185 | -0.26092 | 0.16022 | 0.041199 | 0.20599 | -0.72327 | -0.20142 | 0.24719 | 0.30212 | 0.40283 | 0.57221 | 121.5683 | 122.4518 | 0.041199 | 122.5388 | 4.7562 | -0.20142 | 122.4518 | 0.041199 | 4.7562 | 121.5683 | 122.5388 | -122.5525 | -122.493
1050.0156 | 122.2321 | -0.37994 | 121.994 | -0.012589 | 0.017385 | 0.0087735 | -0.0068017 | 0.061838 | -0.0035867 | 0.068261 | -0.20142 | 122.0947 | -0.54474 | 0.027466 | 121.3852 | 4.6143 | 0.064087 | 0.48981 | 122.1954 | -0.48065 | -0.16479 | 0.10071 | 0.17853 | 0.40741 | -0.60883 | -0.10071 | 0.20142 | 0.34332 | 0.44403 | 0.86975 | 121.7651 | 122.4747 | 0.17853 | 122.5754 | 4.9942 | -0.10071 | 122.4747 | 0.17853 | 4.9942 | 121.7651 | 122.5754 | -122.5388 | -122.4747
1051.7031 | 122.3145 | -0.37079 | 121.962 | -0.0049592 | 0.020803 | 0.010696 | -0.0055199 | 0.059274 | -0.0042277 | 0.066979 | -0.25177 | 122.1268 | -0.55847 | -0.064087 | 121.2845 | 4.5044 | 0.022888 | 0.32959 | 122.1725 | -0.53101 | -0.18768 | 0.16479 | 0.11902 | 0.3067 | -0.67749 | -0.16022 | 0.21057 | 0.3067 | 0.39368 | 0.70038 | 121.6553 | 122.4976 | 0.11902 | 122.5433 | 4.8752 | -0.16022 | 122.4976 | 0.11902 | 4.8752 | 121.6553 | 122.5433 | -122.5204 | -122.493
1053.4688 | 122.3831 | -0.32959 | 121.907 | 0.0103 | 0.019307 | 0.013046 | -0.0023157 | 0.060556 | -0.0059365 | 0.069757 | -0.32501 | 122.1313 | -0.59509 | -0.09613 | 121.2479 | 4.4861 | 0.2655 | 0.37994 | 122.2137 | -0.55847 | -0.2655 | 0.22431 | 0.004578 | 0.23346 | -0.65918 | -0.22888 | 0.3067 | 0.27008 | 0.59509 | 0.70953 | 121.5775 | 122.4609 | 0.004578 | 122.5433 | 4.8157 | -0.22888 | 122.4609 | 0.004578 | 4.8157 | 121.5775 | 122.5433 | -122.5021 | -122.4655
1055.2344 | 122.2916 | -0.37079 | 121.9757 | 0.0026703 | 0.014608 | 0.01326 | -0.0061609 | 0.06141 | -0.0031595 | 0.068048 | -0.26093 | 122.0764 | -0.57678 | -0.032043 | 121.3211 | 4.541 | 0.041199 | 0.36621 | 122.1909 | -0.50354 | -0.20599 | 0.10071 | 0.10986 | 0.33875 | -0.6546 | -0.13275 | 0.21515 | 0.31586 | 0.41199 | 0.737 | 121.6919 | 122.4472 | 0.10986 | 122.5616 | 4.9118 | -0.13275 | 122.4472 | 0.10986 | 4.9118 | 121.6919 | 122.5616 | -122.5525 | -122.4792
1057 | 122.3007 | -0.36163 | 121.9849 | 0.0026703 | 0.018239 | 0.012405 | -0.0046655 | 0.060556 | -0.0033731 | 0.068048 | -0.24719 | 122.1359 | -0.55847 | -0.045776 | 121.3074 | 4.541 | 0.032043 | 0.3479 | 122.2 | -0.5127 | -0.19684 | 0.15106 | 0.11444 | 0.31586 | -0.67749 | -0.15106 | 0.21515 | 0.31128 | 0.39368 | 0.70953 | 121.669 | 122.4976 | 0.11444 | 122.5616 | 4.9026 | -0.15106 | 122.4976 | 0.11444 | 4.9026 | 121.669 | 122.5616 | -122.5433 | -122.4976
1058.6875 | 122.3969 | -0.20599 | 122.0856 | 0.0026703 | 0.016103 | 0.014755 | 3.4284e-05 | 0.061624 | -0.0082865 | 0.065911 | -0.20142 | 122.2092 | -0.49896 | 0.018311 | 121.3623 | 4.541 | 0.29755 | 0.37537 | 122.3648 | -0.4303 | -0.29297 | 0.1236 | 0.004578 | 0.22431 | -0.72327 | -0.2243 | 0.27924 | 0.29755 | 0.50354 | 0.58136 | 121.5683 | 122.4152 | 0.004578 | 122.5708 | 4.747 | -0.2243 | 122.4152 | 0.004578 | 4.747 | 121.5683 | 122.5708 | -122.5845 | -122.5159
1060.4531 | 122.2824 | -0.22888 | 122.1451 | -0.0049592 | 0.018025 | 0.013046 | -0.0046655 | 0.060556 | -0.0046549 | 0.067407 | -0.086975 | 122.2366 | -0.42114 | 0.13275 | 121.4859 | 4.6234 | 0.027466 | 0.42572 | 122.2824 | -0.37079 | -0.19226 | 0.091552 | 0.14191 | 0.36163 | -0.65918 | -0.14191 | 0.13733 | 0.33417 | 0.25635 | 0.6546 | 121.7148 | 122.4655 | 0.14191 | 122.5113 | 4.8523 | -0.14191 | 122.4655 | 0.14191 | 4.8523 | 121.7148 | 122.5113 | -122.5662 | -122.5159
1062.2031 | 122.3831 | -0.21057 | 122.0856 | 0.0026703 | 0.017385 | 0.013046 | 0.0015295 | 0.062265 | -0.0080729 | 0.069116 | -0.16937 | 122.2549 | -0.48065 | 0.027466 | 121.3623 | 4.4815 | 0.12817 | 0.24719 | 122.4014 | -0.3891 | -0.27008 | 0.16937 | 0.041198 | 0.23804 | -0.72327 | -0.17853 | 0.31586 | 0.31128 | 0.33875 | 0.45776 | 121.5729 | 122.4655 | 0.041198 | 122.612 | 4.6921 | -0.17853 | 122.4655 | 0.041198 | 4.6921 | 121.5729 | 122.612 | -122.5662 | -122.4747
1063.9375 | 122.2916 | -0.2243 | 122.113 | -0.020218 | 0.017171 | 0.012619 | -0.0053063 | 0.061624 | -0.0048685 | 0.068261 | -0.11902 | 122.2412 | -0.41657 | 0.11444 | 121.463 | 4.5776 | 0.032043 | 0.37079 | 122.319 | -0.37079 | -0.19226 | 0.12817 | 0.10529 | 0.33875 | -0.65002 | -0.14648 | 0.20599 | 0.29755 | 0.25635 | 0.59509 | 121.6873 | 122.4655 | 0.10529 | 122.5433 | 4.8019 | -0.14648 | 122.4655 | 0.10529 | 4.8019 | 121.6873 | 122.5433 | -122.5296 | -122.4838
1065.625 | 122.3007 | -0.25177 | 122.1268 | -0.012589 | 0.017598 | 0.014969 | -0.0046655 | 0.06141 | -0.0033731 | 0.069543 | -0.082397 | 122.2366 | -0.4303 | 0.11444 | 121.4447 | 4.5685 | -0.009155 | 0.33875 | 122.3648 | -0.37994 | -0.17853 | 0.10986 | 0.16937 | 0.36621 | -0.68207 | -0.12817 | 0.23804 | 0.3479 | 0.24261 | 0.59052 | 121.6965 | 122.4884 | 0.16937 | 122.6166 | 4.8203 | -0.12817 | 122.4884 | 0.16937 | 4.8203 | 121.6965 | 122.6166 | -122.5571 | -122.5067
1067.375 | 122.2778 | -0.25177 | 122.1451 | 0.0026703 | 0.019521 | 0.013473 | 0.00024788 | 0.06376 | -0.0074319 | 0.067193 | -0.07782 | 122.2275 | -0.42572 | 0.14648 | 121.4813 | 4.5959 | -0.064087 | 0.35706 | 122.3099 | -0.36621 | -0.17395 | 0.082397 | 0.17395 | 0.39825 | -0.66376 | -0.11444 | 0.16479 | 0.3479 | 0.18768 | 0.60883 | 121.7331 | 122.4792 | 0.17395 | 122.5616 | 4.8477 | -0.11444 | 122.4792 | 0.17395 | 4.8477 | 121.7331 | 122.5616 | -122.5708 | -122.5113
1069.125 | 122.3602 | -0.21515 | 122.0947 | 0.0026703 | 0.017598 | 0.0096279 | -0.0016747 | 0.060983 | -0.0059365 | 0.066552 | -0.15564 | 122.2733 | -0.46234 | 0.054932 | 121.4035 | 4.5502 | 0.23804 | 0.3891 | 122.3877 | -0.39825 | -0.24719 | 0.17853 | 0.059509 | 0.27008 | -0.69122 | -0.1831 | 0.29297 | 0.3067 | 0.45319 | 0.60425 | 121.6187 | 122.4884 | 0.059509 | 122.6028 | 4.7653 | -0.1831 | 122.4884 | 0.059509 | 4.7653 | 121.6187 | 122.6028 | -122.5571 | -122.493
1070.875 | 122.3282 | -0.2243 | 122.1085 | 0.0026703 | 0.018453 | 0.012405 | -0.0042383 | 0.060983 | -0.0010233 | 0.067407 | -0.1236 | 122.2458 | -0.42114 | 0.10071 | 121.4401 | 4.5502 | 0.045776 | 0.32959 | 122.3328 | -0.37994 | -0.19684 | 0.13733 | 0.10071 | 0.32501 | -0.66833 | -0.15564 | 0.22431 | 0.29755 | 0.27008 | 0.55389 | 121.6644 | 122.4701 | 0.10071 | 122.5571 | 4.7745 | -0.15564 | 122.4701 | 0.10071 | 4.7745 | 121.6644 | 122.5571 | -122.5296 | -122.4884
1072.6406 | 122.3969 | -0.20599 | 122.0947 | -0.0049592 | 0.019948 | 0.011337 | 0.00067508 | 0.062478 | -0.0065775 | 0.068048 | -0.18768 | 122.2824 | -0.48523 | 0.032043 | 121.3989 | 4.5547 | 0.28381 | 0.37994 | 122.406 | -0.41657 | -0.27924 | 0.18768 | 0.018311 | 0.23804 | -0.6958 | -0.21057 | 0.31128 | 0.29755 | 0.48981 | 0.58594 | 121.6049 | 122.4884 | 0.018311 | 122.612 | 4.7607 | -0.21057 | 122.4884 | 0.018311 | 4.7607 | 121.6049 | 122.612 | -122.58 | -122.5113
1074.3281 | 122.2824 | -0.23804 | 122.1497 | 0.0026703 | 0.019307 | 0.011337 | -0.0027429 | 0.061624 | -0.0046549 | 0.068261 | -0.050354 | 122.3007 | -0.42114 | 0.17395 | 121.5317 | 4.6509 | 0.013733 | 0.45776 | 122.319 | -0.37079 | -0.18311 | 0.15106 | 0.18768 | 0.41199 | -0.61798 | -0.13275 | 0.16937 | 0.37079 | 0.25177 | 0.6958 | 121.7697 | 122.5388 | 0.18768 | 122.5571 | 4.8889 | -0.13275 | 122.5388 | 0.18768 | 4.8889 | 121.7697 | 122.5571 | -122.5708 | -122.5204
1076.0625 | 122.2733 | -0.25635 | 122.1542 | -0.0049592 | 0.017812 | 0.011978 | -0.0023157 | 0.061624 | -0.0061503 | 0.065911 | -0.068665 | 122.2916 | -0.41199 | 0.17395 | 121.5179 | 4.6738 | 0.064087 | 0.48981 | 122.3282 | -0.37079 | -0.15564 | 0.13733 | 0.18768 | 0.4303 | -0.63629 | -0.11444 | 0.17395 | 0.34332 | 0.32044 | 0.74616 | 121.7743 | 122.5479 | 0.18768 | 122.5845 | 4.9301 | -0.11444 | 122.5479 | 0.18768 | 4.9301 | 121.7743 | 122.5845 | -122.5662 | -122.525
1077.8125 | 122.2916 | -0.23804 | 122.1588 | -0.0049592 | 0.017171 | 0.014755 | -0.0035973 | 0.063119 | -0.0048685 | 0.066979 | -0.086975 | 122.3099 | -0.41199 | 0.15564 | 121.4951 | 4.6463 | 0.027466 | 0.42572 | 122.3602 | -0.37079 | -0.17395 | 0.15106 | 0.15106 | 0.39368 | -0.66376 | -0.13275 | 0.20142 | 0.32501 | 0.2655 | 0.66376 | 121.7331 | 122.5479 | 0.15106 | 122.5983 | 4.8843 | -0.13275 | 122.5479 | 0.15106 | 4.8843 | 121.7331 | 122.5983 | -122.5708 | -122.5296
1079.5625 | 122.3694 | -0.21973 | 122.0993 | -0.0049592 | 0.019521 | 0.012619 | -0.0010339 | 0.061624 | -0.0074319 | 0.066979 | -0.10986 | 122.3099 | -0.45319 | 0.07782 | 121.4172 | 4.5685 | 0.22888 | 0.38452 | 122.4014 | -0.39368 | -0.23346 | 0.21057 | 0.10986 | 0.29755 | -0.68207 | -0.17395 | 0.30212 | 0.34332 | 0.44861 | 0.60425 | 121.637 | 122.5296 | 0.10986 | 122.6212 | 4.7882 | -0.17395 | 122.5296 | 0.10986 | 4.7882 | 121.637 | 122.6212 | -122.5525 | -122.493
1081.25 | 122.2687 | -0.25177 | 122.1451 | -0.0049592 | 0.017171 | 0.015396 | -0.0014611 | 0.060342 | -0.0046549 | 0.06762 | -0.059509 | 122.2321 | -0.39368 | 0.16022 | 121.5042 | 4.6371 | -0.082397 | 0.35706 | 122.3419 | -0.35706 | -0.14191 | 0.086975 | 0.19226 | 0.41199 | -0.64087 | -0.10529 | 0.19684 | 0.33417 | 0.16937 | 0.60883 | 121.756 | 122.4838 | 0.19226 | 122.5937 | 4.8889 | -0.10529 | 122.4838 | 0.19226 | 4.8889 | 121.756 | 122.5937 | -122.5388 | -122.5021
1083.0156 | 122.3419 | -0.22888 | 122.1359 | 0.0026703 | 0.017812 | 0.010483 | -0.0038111 | 0.062478 | -0.0065775 | 0.06762 | -0.091553 | 122.2916 | -0.4303 | 0.11444 | 121.4722 | 4.6005 | 0.19226 | 0.42114 | 122.3969 | -0.37994 | -0.20142 | 0.15564 | 0.13733 | 0.34332 | -0.66376 | -0.15106 | 0.26093 | 0.33875 | 0.42114 | 0.65002 | 121.701 | 122.5204 | 0.13733 | 122.6257 | 4.8294 | -0.15106 | 122.5204 | 0.13733 | 4.8294 | 121.701 | 122.6257 | -122.5662 | -122.5159
1084.7656 | 122.4289 | -0.19226 | 122.1222 | 0.0026703 | 0.019521 | 0.0087735 | 0.0040931 | 0.063974 | -0.0070047 | 0.066979 | -0.16937 | 122.3099 | -0.46692 | 0.032043 | 121.3898 | 4.5273 | 0.15106 | 0.25635 | 122.4106 | -0.39825 | -0.27466 | 0.18768 | 0.022888 | 0.2243 | -0.73242 | -0.20599 | 0.28839 | 0.29755 | 0.34332 | 0.44861 | 121.582 | 122.5021 | 0.022888 | 122.6028 | 4.7195 | -0.20599 | 122.5021 | 0.022888 | 4.7195 | 121.582 | 122.6028 | -122.5891 | -122.5204
1086.4688 | 122.4243 | -0.19684 | 122.1451 | 0.0103 | 0.018666 | 0.012192 | -0.00060672 | 0.065042 | -0.0059365 | 0.067407 | -0.15106 | 122.3053 | -0.46234 | 0.036621 | 121.3943 | 4.5181 | 0.14648 | 0.23346 | 122.3602 | -0.39368 | -0.2655 | 0.16022 | 0.045776 | 0.23346 | -0.75073 | -0.19684 | 0.21515 | 0.31128 | 0.34332 | 0.4303 | 121.5912 | 122.5021 | 0.045776 | 122.5571 | 4.715 | -0.19684 | 122.5021 | 0.045776 | 4.715 | 121.5912 | 122.5571 | -122.6074 | -122.5388
1088.2188 | 122.4197 | -0.19226 | 122.1313 | -0.0049592 | 0.018453 | 0.014755 | -0.00039312 | 0.06376 | -0.0048685 | 0.068048 | -0.16479 | 122.3282 | -0.43945 | 0.036621 | 121.4172 | 4.5273 | 0.18768 | 0.2655 | 122.374 | -0.39368 | -0.24719 | 0.19684 | 0.027466 | 0.22888 | -0.71411 | -0.20142 | 0.24261 | 0.27466 | 0.37994 | 0.45776 | 121.6095 | 122.5204 | 0.027466 | 122.5662 | 4.7195 | -0.20142 | 122.5204 | 0.027466 | 4.7195 | 121.6095 | 122.5662 | -122.5708 | -122.525
1089.9688 | 122.3465 | -0.2243 | 122.1451 | -0.0049592 | 0.018666 | 0.013687 | -0.0057337 | 0.062265 | -0.0029459 | 0.066979 | -0.11444 | 122.3282 | -0.40741 | 0.10529 | 121.4859 | 4.6051 | 0.045776 | 0.33875 | 122.3465 | -0.36621 | -0.18311 | 0.1831 | 0.10986 | 0.32959 | -0.65918 | -0.14191 | 0.20142 | 0.29297 | 0.27008 | 0.56305 | 121.7102 | 122.5525 | 0.10986 | 122.5708 | 4.8294 | -0.14191 | 122.5525 | 0.10986 | 4.8294 | 121.7102 | 122.5708 | -122.5525 | -122.5113
1091.6562 | 122.4472 | -0.17395 | 122.1222 | 0.0103 | 0.014608 | 0.014969 | 0.00024788 | 0.063547 | -0.0078591 | 0.06997 | -0.15564 | 122.319 | -0.43488 | 0.050354 | 121.4218 | 4.5547 | 0.16022 | 0.26093 | 122.4106 | -0.35706 | -0.26093 | 0.19684 | 0.01831 | 0.2243 | -0.70038 | -0.18311 | 0.28839 | 0.27924 | 0.33417 | 0.43488 | 121.5958 | 122.493 | 0.01831 | 122.5845 | 4.7287 | -0.18311 | 122.493 | 0.01831 | 4.7287 | 121.5958 | 122.5845 | -122.5571 | -122.4792
1093.4062 | 122.3785 | -0.19684 | 122.1497 | 0.0026703 | 0.019734 | 0.011978 | 0.00067508 | 0.060342 | -0.0048685 | 0.06997 | -0.082397 | 122.3007 | -0.41657 | 0.10071 | 121.4722 | 4.628 | 0.16479 | 0.35248 | 122.4152 | -0.37079 | -0.21973 | 0.15106 | 0.11444 | 0.29755 | -0.67749 | -0.17395 | 0.2655 | 0.33417 | 0.36163 | 0.54932 | 121.669 | 122.4976 | 0.11444 | 122.612 | 4.8248 | -0.17395 | 122.4976 | 0.11444 | 4.8248 | 121.669 | 122.612 | -122.5662 | -122.5204
1095.1562 | 122.2824 | -0.23346 | 122.2137 | -0.0049592 | 0.018453 | 0.01326 | -0.0055199 | 0.065256 | -0.0067911 | 0.06762 | -0.027466 | 122.3007 | -0.35706 | 0.16022 | 121.5454 | 4.6646 | -0.068665 | 0.36163 | 122.3602 | -0.33417 | -0.1236 | 0.086975 | 0.20599 | 0.39368 | -0.66833 | -0.10071 | 0.14648 | 0.32959 | 0.16479 | 0.59509 | 121.7789 | 122.5342 | 0.20599 | 122.5937 | 4.8981 | -0.10071 | 122.5342 | 0.20599 | 4.8981 | 121.7789 | 122.5937 | -122.5708 | -122.5479
1096.9219 | 122.3282 | -0.23804 | 122.2 | 0.0026703 | 0.015248 | 0.011337 | -0.0053063 | 0.062906 | -0.0063639 | 0.06997 | -0.09613 | 122.2595 | -0.40741 | 0.1236 | 121.5134 | 4.6371 | 0.004578 | 0.33875 | 122.4243 | -0.33875 | -0.16937 | 0.059509 | 0.14191 | 0.36163 | -0.68664 | -0.10071 | 0.2243 | 0.31128 | 0.24261 | 0.57678 | 121.7514 | 122.4976 | 0.14191 | 122.6624 | 4.8752 | -0.10071 | 122.4976 | 0.14191 | 4.8752 | 121.7514 | 122.6624 | -122.6074 | -122.5388
1098.625 | 122.3007 | -0.21515 | 122.1588 | -0.020218 | 0.019521 | 0.012192 | -0.0057337 | 0.062265 | -0.0048685 | 0.069543 | -0.073242 | 122.3236 | -0.40283 | 0.14648 | 121.5317 | 4.7012 | 0.045776 | 0.40741 | 122.3602 | -0.35248 | -0.18768 | 0.16479 | 0.14191 | 0.36163 | -0.62714 | -0.13733 | 0.20142 | 0.32959 | 0.26093 | 0.62256 | 121.7468 | 122.5388 | 0.14191 | 122.5754 | 4.9164 | -0.13733 | 122.5388 | 0.14191 | 4.9164 | 121.7468 | 122.5754 | -122.5616 | -122.5113
1100.375 | 122.3923 | -0.16937 | 122.1542 | 0.0026703 | 0.019521 | 0.012832 | 0.0011023 | 0.062051 | -0.0076455 | 0.068048 | -0.1236 | 122.3511 | -0.43945 | 0.082397 | 121.4722 | 4.6371 | 0.25177 | 0.40283 | 122.4197 | -0.37537 | -0.27008 | 0.19684 | 0.045777 | 0.25177 | -0.68207 | -0.20599 | 0.2655 | 0.31586 | 0.42114 | 0.57221 | 121.6415 | 122.5204 | 0.045777 | 122.5891 | 4.8065 | -0.20599 | 122.5204 | 0.045777 | 4.8065 | 121.6415 | 122.5891 | -122.5937 | -122.5296
1102.1094 | 122.3877 | -0.21515 | 122.1634 | -0.0049592 | 0.01653 | 0.014114 | 0.00046148 | 0.064187 | -0.0055093 | 0.066766 | -0.10071 | 122.3511 | -0.45319 | 0.12817 | 121.4951 | 4.66 | 0.20599 | 0.4303 | 122.4243 | -0.3479 | -0.23804 | 0.18768 | 0.11444 | 0.34332 | -0.66833 | -0.13275 | 0.26093 | 0.35248 | 0.42114 | 0.64545 | 121.7102 | 122.5662 | 0.11444 | 122.6395 | 4.8752 | -0.13275 | 122.5662 | 0.11444 | 4.8752 | 121.7102 | 122.6395 | -122.6166 | -122.5113
1103.875 | 122.4197 | -0.18768 | 122.1497 | 0.0026703 | 0.019948 | 0.011337 | -0.00017952 | 0.062692 | -0.0076455 | 0.068261 | -0.14648 | 122.3282 | -0.44403 | 0.050354 | 121.431 | 4.5731 | 0.10986 | 0.25635 | 122.4426 | -0.3891 | -0.25635 | 0.17853 | 0.041199 | 0.23804 | -0.71869 | -0.20142 | 0.29297 | 0.29755 | 0.29755 | 0.44403 | 121.6187 | 122.5159 | 0.041199 | 122.6303 | 4.7607 | -0.20142 | 122.5159 | 0.041199 | 4.7607 | 121.6187 | 122.6303 | -122.5937 | -122.5388
1105.5781 | 122.3511 | -0.21515 | 122.1909 | -0.0049592 | 0.018239 | 0.011978 | -0.0050927 | 0.062051 | -0.0040139 | 0.068902 | -0.086975 | 122.319 | -0.39368 | 0.091553 | 121.4996 | 4.6509 | 0.018311 | 0.32044 | 122.3877 | -0.37537 | -0.17853 | 0.12817 | 0.12817 | 0.3067 | -0.69122 | -0.16022 | 0.19684 | 0.3067 | 0.23346 | 0.53558 | 121.7148 | 122.5342 | 0.12817 | 122.6028 | 4.866 | -0.16022 | 122.5342 | 0.12817 | 4.866 | 121.7148 | 122.6028 | -122.5845 | -122.5662
1107.3281 | 122.4426 | -0.18768 | 122.1313 | -0.0049592 | 0.022725 | 0.014969 | 0.0011023 | 0.062692 | -0.0057229 | 0.069329 | -0.14191 | 122.3923 | -0.4303 | 0.054932 | 121.4401 | 4.6188 | 0.27924 | 0.37537 | 122.438 | -0.39825 | -0.24262 | 0.26093 | 0.045776 | 0.24261 | -0.69122 | -0.21057 | 0.3067 | 0.28839 | 0.46692 | 0.56305 | 121.6278 | 122.58 | 0.045776 | 122.6257 | 4.8065 | -0.21057 | 122.58 | 0.045776 | 4.8065 | 121.6278 | 122.6257 | -122.5616 | -122.5296
1109.0625 | 122.3831 | -0.2243 | 122.1634 | 0.0026703 | 0.020803 | 0.015182 | 0.00024788 | 0.065683 | -0.0057229 | 0.067834 | -0.11902 | 122.3053 | -0.43945 | 0.10071 | 121.4813 | 4.6326 | 0 | 0.33417 | 122.3785 | -0.37537 | -0.21515 | 0.14191 | 0.10529 | 0.32501 | -0.68207 | -0.15106 | 0.21515 | 0.32043 | 0.2243 | 0.55847 | 121.7056 | 122.5296 | 0.10529 | 122.6028 | 4.8569 | -0.15106 | 122.5296 | 0.10529 | 4.8569 | 121.7056 | 122.6028 | -122.6028 | -122.5388
1110.8125 | 122.4335 | -0.19226 | 122.1222 | -0.0049592 | 0.017171 | 0.01561 | -0.0023157 | 0.062692 | -0.0063639 | 0.06997 | -0.17853 | 122.3145 | -0.46234 | 0.022888 | 121.4218 | 4.5914 | 0.10986 | 0.2655 | 122.4106 | -0.37994 | -0.27008 | 0.19226 | 0.013733 | 0.21515 | -0.70038 | -0.18768 | 0.28839 | 0.28381 | 0.30212 | 0.45776 | 121.6141 | 122.5067 | 0.013733 | 122.6028 | 4.7836 | -0.18768 | 122.5067 | 0.013733 | 4.7836 | 121.6141 | 122.6028 | -122.5845 | -122.5021
1112.5156 | 122.3145 | -0.23346 | 122.2046 | -0.0049592 | 0.015889 | 0.012619 | -0.0072289 | 0.062265 | -0.0046549 | 0.067407 | -0.045776 | 122.3053 | -0.40283 | 0.17853 | 121.5729 | 4.7607 | 0.027466 | 0.49439 | 122.3602 | -0.35706 | -0.16937 | 0.10071 | 0.18768 | 0.41199 | -0.63171 | -0.1236 | 0.15564 | 0.35706 | 0.26093 | 0.72784 | 121.8063 | 122.5388 | 0.18768 | 122.5937 | 4.9942 | -0.1236 | 122.5388 | 0.18768 | 4.9942 | 121.8063 | 122.5937 | -122.6074 | -122.5616
1114.2656 | 122.3465 | -0.23346 | 122.2 | -0.0049592 | 0.012471 | 0.010269 | -0.0057337 | 0.062265 | -0.0050821 | 0.068261 | -0.10986 | 122.2687 | -0.40741 | 0.10071 | 121.4996 | 4.66 | 0.032043 | 0.33875 | 122.3877 | -0.36621 | -0.17395 | 0.068665 | 0.1236 | 0.33417 | -0.70038 | -0.13275 | 0.18768 | 0.29755 | 0.2655 | 0.5722 | 121.7331 | 122.5021 | 0.1236 | 122.6212 | 4.8935 | -0.13275 | 122.5021 | 0.1236 | 4.8935 | 121.7331 | 122.6212 | -122.6074 | -122.5662
1116.0156 | 122.287 | -0.23804 | 122.2 | 0.0026703 | 0.020375 | 0.014755 | -0.00082032 | 0.062051 | -0.0055093 | 0.071252 | -0.036621 | 122.3053 | -0.37537 | 0.15564 | 121.5408 | 4.7012 | -0.073242 | 0.3891 | 122.374 | -0.33875 | -0.13733 | 0.10529 | 0.20142 | 0.39368 | -0.65918 | -0.10071 | 0.17395 | 0.33874 | 0.16479 | 0.62714 | 121.7789 | 122.5433 | 0.20142 | 122.612 | 4.9393 | -0.10071 | 122.5433 | 0.20142 | 4.9393 | 121.7789 | 122.612 | -122.5754 | -122.5388
1117.7031 | 122.3465 | -0.21057 | 122.1771 | -0.0049592 | 0.019734 | 0.01625 | 0.00067508 | 0.062265 | -0.0038003 | 0.068261 | -0.073242 | 122.3236 | -0.40741 | 0.14648 | 121.5042 | 4.6738 | -0.022888 | 0.35248 | 122.3877 | -0.35706 | -0.19684 | 0.14648 | 0.13733 | 0.35706 | -0.67291 | -0.14648 | 0.21057 | 0.33417 | 0.18768 | 0.56305 | 121.7148 | 122.5342 | 0.13733 | 122.5983 | 4.8843 | -0.14648 | 122.5342 | 0.13733 | 4.8843 | 121.7148 | 122.5983 | -122.5845 | -122.5342
1119.4531 | 122.3465 | -0.2243 | 122.168 | -0.012589 | 0.018239 | 0.015396 | -0.0042383 | 0.061624 | -0.0025187 | 0.069329 | -0.10529 | 122.3648 | -0.40741 | 0.10986 | 121.5088 | 4.6921 | 0.045776 | 0.37537 | 122.406 | -0.37079 | -0.18311 | 0.19684 | 0.11902 | 0.33417 | -0.65918 | -0.14648 | 0.23804 | 0.30212 | 0.27008 | 0.59967 | 121.7331 | 122.5891 | 0.11902 | 122.6303 | 4.9164 | -0.14648 | 122.5891 | 0.11902 | 4.9164 | 121.7331 | 122.6303 | -122.5754 | -122.5388
1121.1875 | 122.3419 | -0.24261 | 122.1863 | -0.0049592 | 0.017171 | 0.014541 | -0.0044519 | 0.060983 | -0.0044413 | 0.068261 | -0.086975 | 122.3602 | -0.41199 | 0.1236 | 121.5179 | 4.6921 | 0.041199 | 0.39368 | 122.3648 | -0.36163 | -0.16937 | 0.17395 | 0.15564 | 0.36621 | -0.66833 | -0.11902 | 0.17853 | 0.32501 | 0.28381 | 0.63629 | 121.7606 | 122.6028 | 0.15564 | 122.6074 | 4.9347 | -0.11902 | 122.6028 | 0.15564 | 4.9347 | 121.7606 | 122.6074 | -122.5983 | -122.5479
1122.9531 | 122.2916 | -0.21515 | 122.1909 | -0.012589 | 0.018666 | 0.012192 | -0.0021021 | 0.059915 | -0.0035867 | 0.068688 | -0.045776 | 122.3328 | -0.40283 | 0.1831 | 121.5637 | 4.7653 | 0.059509 | 0.49439 | 122.3694 | -0.36163 | -0.18768 | 0.14191 | 0.16937 | 0.39825 | -0.62714 | -0.14648 | 0.17853 | 0.35706 | 0.27466 | 0.70953 | 121.7789 | 122.5479 | 0.16937 | 122.5845 | 4.9805 | -0.14648 | 122.5479 | 0.16937 | 4.9805 | 121.7789 | 122.5845 | -122.5937 | -122.5525
1124.6406 | 122.2961 | -0.23804 | 122.2092 | -0.012589 | 0.016317 | 0.010055 | -0.0035973 | 0.061197 | -0.0046549 | 0.06762 | -0.050354 | 122.3328 | -0.41657 | 0.17395 | 121.55 | 4.7699 | 0.027466 | 0.47607 | 122.3785 | -0.36163 | -0.17853 | 0.1236 | 0.18768 | 0.41199 | -0.65918 | -0.1236 | 0.16937 | 0.36621 | 0.2655 | 0.71411 | 121.788 | 122.5708 | 0.18768 | 122.6166 | 5.0079 | -0.1236 | 122.5708 | 0.18768 | 5.0079 | 121.788 | 122.6166 | -122.6257 | -122.5708
1126.3906 | 122.4014 | -0.20599 | 122.1863 | 0.0026703 | 0.016957 | 0.012619 | 0.0025977 | 0.06376 | -0.0085001 | 0.069116 | -0.1236 | 122.3328 | -0.45319 | 0.12817 | 121.4905 | 4.6783 | 0.18768 | 0.41657 | 122.4014 | -0.3891 | -0.24719 | 0.14648 | 0.082398 | 0.33417 | -0.6958 | -0.1831 | 0.21515 | 0.32959 | 0.39368 | 0.62256 | 121.6965 | 122.5388 | 0.082398 | 122.6074 | 4.8843 | -0.1831 | 122.5388 | 0.082398 | 4.8843 | 121.6965 | 122.6074 | -122.6395 | -122.5754
1128.1406 | 122.3648 | -0.23346 | 122.168 | -0.012589 | 0.017812 | 0.014541 | -0.0063745 | 0.06376 | -0.0063639 | 0.068475 | -0.1236 | 122.3282 | -0.42572 | 0.091553 | 121.4905 | 4.6967 | 0.073242 | 0.36163 | 122.4289 | -0.37079 | -0.19226 | 0.16022 | 0.10986 | 0.32501 | -0.67749 | -0.13733 | 0.26093 | 0.30212 | 0.3067 | 0.59509 | 121.7239 | 122.5616 | 0.10986 | 122.6624 | 4.9301 | -0.13733 | 122.5616 | 0.10986 | 4.9301 | 121.7239 | 122.6624 | -122.5937 | -122.5388
1129.8906 | 122.4609 | -0.1831 | 122.1634 | 0.0103 | 0.019094 | 0.012192 | 0.0036657 | 0.062692 | -0.0057229 | 0.068048 | -0.1831 | 122.3465 | -0.45319 | 0.032043 | 121.4264 | 4.6051 | 0.15564 | 0.25177 | 122.4518 | -0.40283 | -0.27008 | 0.18311 | 0 | 0.21515 | -0.737 | -0.21973 | 0.28839 | 0.27008 | 0.33874 | 0.43488 | 121.6095 | 122.5296 | 0 | 122.6349 | 4.7882 | -0.21973 | 122.5296 | 0 | 4.7882 | 121.6095 | 122.6349 | -122.6166 | -122.5662
1131.5938 | 122.4014 | -0.21515 | 122.1725 | 0.0026703 | 0.021016 | 0.013473 | 3.4284e-05 | 0.06376 | -0.0072183 | 0.068688 | -0.11902 | 122.3282 | -0.44403 | 0.09613 | 121.4996 | 4.7104 | 0.20142 | 0.42114 | 122.4335 | -0.37994 | -0.22888 | 0.15564 | 0.09613 | 0.31128 | -0.67291 | -0.16479 | 0.26093 | 0.32501 | 0.41657 | 0.63629 | 121.7148 | 122.5433 | 0.09613 | 122.6486 | 4.9255 | -0.16479 | 122.5433 | 0.09613 | 4.9255 | 121.7148 | 122.6486 | -122.6166 | -122.5525
1133.3438 | 122.3694 | -0.24719 | 122.168 | -0.012589 | 0.017812 | 0.011764 | -0.0042383 | 0.062906 | -0.0059365 | 0.065911 | -0.10986 | 122.3602 | -0.42114 | 0.086975 | 121.5042 | 4.7058 | 0.21973 | 0.42572 | 122.4197 | -0.39825 | -0.17395 | 0.19226 | 0.13733 | 0.33417 | -0.66376 | -0.15106 | 0.25177 | 0.31128 | 0.46692 | 0.67291 | 121.7514 | 122.6074 | 0.13733 | 122.6669 | 4.953 | -0.15106 | 122.6074 | 0.13733 | 4.953 | 121.7514 | 122.6669 | -122.5891 | -122.5662
1135.0938 | 122.4609 | -0.20142 | 122.1497 | -0.0049592 | 0.017598 | 0.012192 | -0.0010339 | 0.062051 | -0.0061503 | 0.067193 | -0.16937 | 122.3511 | -0.44403 | 0.045776 | 121.4584 | 4.6738 | 0.29297 | 0.39368 | 122.4564 | -0.39825 | -0.24261 | 0.20142 | 0.032043 | 0.24719 | -0.69122 | -0.19684 | 0.3067 | 0.27466 | 0.49438 | 0.59509 | 121.6599 | 122.5525 | 0.032043 | 122.6578 | 4.8752 | -0.19684 | 122.5525 | 0.032043 | 4.8752 | 121.6599 | 122.6578 | -122.5937 | -122.5479
1136.8438 | 122.3694 | -0.21515 | 122.1909 | -0.012589 | 0.016103 | 0.014755 | -0.0072289 | 0.061197 | -0.0061503 | 0.070611 | -0.1236 | 122.3328 | -0.39825 | 0.10071 | 121.5042 | 4.6875 | 0.036621 | 0.33875 | 122.3785 | -0.34332 | -0.1831 | 0.14191 | 0.091553 | 0.31586 | -0.68665 | -0.12817 | 0.18768 | 0.27466 | 0.25177 | 0.55389 | 121.7194 | 122.5479 | 0.091553 | 122.5937 | 4.9026 | -0.12817 | 122.5479 | 0.091553 | 4.9026 | 121.7194 | 122.5937 | -122.5891 | -122.5342
1138.5469 | 122.4152 | -0.21973 | 122.168 | 0.0026703 | 0.018453 | 0.011123 | 3.4284e-05 | 0.064828 | -0.0085001 | 0.068475 | -0.13733 | 122.3557 | -0.43488 | 0.068665 | 121.4813 | 4.6646 | 0.050354 | 0.28839 | 122.4289 | -0.36163 | -0.21515 | 0.18768 | 0.082398 | 0.28839 | -0.68665 | -0.14191 | 0.26093 | 0.29755 | 0.27008 | 0.50812 | 121.7011 | 122.5754 | 0.082398 | 122.6486 | 4.8843 | -0.14191 | 122.5754 | 0.082398 | 4.8843 | 121.7011 | 122.6486 | -122.6028 | -122.5296
1140.2969 | 122.4426 | -0.18768 | 122.168 | -0.0049592 | 0.019734 | 0.016037 | -0.0025293 | 0.062692 | -0.0046549 | 0.066766 | -0.14648 | 122.3877 | -0.42572 | 0.054932 | 121.4767 | 4.6829 | 0.28381 | 0.38452 | 122.4289 | -0.39825 | -0.23804 | 0.21973 | 0.041199 | 0.24261 | -0.69122 | -0.21057 | 0.26093 | 0.27924 | 0.4715 | 0.5722 | 121.6644 | 122.5754 | 0.041199 | 122.6166 | 4.8706 | -0.21057 | 122.5754 | 0.041199 | 4.8706 | 121.6644 | 122.6166 | -122.5937 | -122.5662
1142.0312 | 122.4197 | -0.20142 | 122.1634 | 0.0026703 | 0.020162 | 0.012619 | -0.00017952 | 0.063547 | -0.0063639 | 0.068475 | -0.14648 | 122.3465 | -0.42572 | 0.091553 | 121.4859 | 4.6967 | 0.16937 | 0.35248 | 122.438 | -0.37994 | -0.2243 | 0.18311 | 0.054932 | 0.29297 | -0.67749 | -0.17853 | 0.27466 | 0.27924 | 0.37079 | 0.55389 | 121.6873 | 122.5479 | 0.054932 | 122.6395 | 4.8981 | -0.17853 | 122.5479 | 0.054932 | 4.8981 | 121.6873 | 122.6395 | -122.5891 | -122.5433
1143.7812 | 122.4106 | -0.18768 | 122.1909 | 0.0026703 | 0.018453 | 0.013687 | 3.4284e-05 | 0.064615 | -0.0093545 | 0.069757 | -0.09613 | 122.3648 | -0.4303 | 0.11444 | 121.5179 | 4.7287 | 0.17853 | 0.42572 | 122.4335 | -0.37537 | -0.24262 | 0.17395 | 0.091553 | 0.30212 | -0.67291 | -0.18768 | 0.24262 | 0.33417 | 0.36621 | 0.6134 | 121.7056 | 122.5525 | 0.091553 | 122.6212 | 4.9164 | -0.18768 | 122.5525 | 0.091553 | 4.9164 | 121.7056 | 122.6212 | -122.6212 | -122.5662
1145.4688 | 122.4289 | -0.22888 | 122.1588 | 0.0026703 | 0.021871 | 0.013473 | -0.0018885 | 0.062692 | -0.0072183 | 0.067193 | -0.11902 | 122.3923 | -0.45319 | 0.086975 | 121.5134 | 4.7333 | 0.23346 | 0.41657 | 122.4335 | -0.37994 | -0.2243 | 0.23346 | 0.10986 | 0.31586 | -0.64545 | -0.15106 | 0.27466 | 0.33417 | 0.46234 | 0.64545 | 121.7422 | 122.6212 | 0.10986 | 122.6624 | 4.9622 | -0.15106 | 122.6212 | 0.10986 | 4.9622 | 121.7422 | 122.6624 | -122.612 | -122.5388
1147.2031 | 122.4701 | -0.1831 | 122.1771 | -0.012589 | 0.018025 | 0.010696 | -0.0031701 | 0.062051 | -0.0072183 | 0.068688 | -0.16937 | 122.3511 | -0.43488 | 0.009155 | 121.4539 | 4.6463 | 0.15564 | 0.26093 | 122.4747 | -0.37079 | -0.25177 | 0.17395 | 0.013732 | 0.19226 | -0.72327 | -0.18768 | 0.29755 | 0.2655 | 0.33874 | 0.44403 | 121.637 | 122.5342 | 0.013732 | 122.6578 | 4.8294 | -0.18768 | 122.5342 | 0.013732 | 4.8294 | 121.637 | 122.6578 | -122.612 | -122.5479
1148.9688 | 122.3282 | -0.23804 | 122.2321 | -0.0049592 | 0.019307 | 0.010696 | -0.0057337 | 0.063547 | -0.0061503 | 0.067193 | -0.041199 | 122.374 | -0.37994 | 0.15106 | 121.5683 | 4.7745 | -0.064087 | 0.37079 | 122.4243 | -0.35248 | -0.14191 | 0.14191 | 0.19684 | 0.3891 | -0.66376 | -0.11444 | 0.19226 | 0.33875 | 0.17395 | 0.60883 | 121.8063 | 122.612 | 0.19684 | 122.6624 | 5.0125 | -0.11444 | 122.612 | 0.19684 | 5.0125 | 121.8063 | 122.6624 | -122.612 | -122.5845
1150.6562 | 122.4609 | -0.16937 | 122.1863 | -0.0049592 | 0.015676 | 0.0081327 | -0.0040247 | 0.063547 | -0.0059365 | 0.068261 | -0.16479 | 122.3648 | -0.44861 | 0.036621 | 121.4676 | 4.7104 | 0.29297 | 0.37994 | 122.4747 | -0.38452 | -0.27924 | 0.17853 | 0.004578 | 0.20599 | -0.71869 | -0.21515 | 0.28839 | 0.28381 | 0.46234 | 0.54932 | 121.637 | 122.5342 | 0.004578 | 122.644 | 4.8798 | -0.21515 | 122.5342 | 0.004578 | 4.8798 | 121.637 | 122.644 | -122.6349 | -122.5708
1152.4062 | 122.3694 | -0.21057 | 122.2137 | 0.0026703 | 0.01653 | 0.0092007 | -0.0082971 | 0.063547 | -0.0042277 | 0.068261 | -0.10071 | 122.3602 | -0.39825 | 0.086975 | 121.5317 | 4.7379 | 0.050354 | 0.34332 | 122.438 | -0.36163 | -0.18768 | 0.14648 | 0.10986 | 0.29755 | -0.68207 | -0.15106 | 0.2243 | 0.29755 | 0.26093 | 0.55389 | 121.7422 | 122.5708 | 0.10986 | 122.6486 | 4.9484 | -0.15106 | 122.5708 | 0.10986 | 4.9484 | 121.7422 | 122.6486 | -122.612 | -122.5754
1154.1562 | 122.4518 | -0.18768 | 122.1863 | 0.0026703 | 0.016957 | 0.013046 | -0.0023157 | 0.062051 | -0.0061503 | 0.067407 | -0.16937 | 122.3785 | -0.43945 | 0.050354 | 121.4813 | 4.6967 | 0.31586 | 0.39825 | 122.4792 | -0.37079 | -0.25177 | 0.19226 | 0.01831 | 0.23804 | -0.70496 | -0.18311 | 0.29297 | 0.27008 | 0.50354 | 0.58594 | 121.669 | 122.5662 | 0.01831 | 122.6669 | 4.8843 | -0.18311 | 122.5662 | 0.01831 | 4.8843 | 121.669 | 122.6669 | -122.6257 | -122.5571
1155.9219 | 122.3969 | -0.20599 | 122.2275 | 0.0026703 | 0.016103 | 0.010269 | -0.0029565 | 0.064401 | -0.0070047 | 0.069116 | -0.09613 | 122.3923 | -0.40741 | 0.10986 | 121.5134 | 4.7653 | 0.21973 | 0.42114 | 122.4792 | -0.37994 | -0.20142 | 0.16479 | 0.10986 | 0.31586 | -0.71411 | -0.17395 | 0.25177 | 0.31128 | 0.42572 | 0.62714 | 121.7194 | 122.5983 | 0.10986 | 122.6852 | 4.9713 | -0.17395 | 122.5983 | 0.10986 | 4.9713 | 121.7194 | 122.6852 | -122.6349 | -122.6074
1157.6094 | 122.3282 | -0.2243 | 122.2458 | 0.0026703 | 0.021657 | 0.011764 | -0.0076563 | 0.063119 | -0.0061503 | 0.068475 | -0.041199 | 122.3694 | -0.39825 | 0.16479 | 121.5866 | 4.8294 | 0.041199 | 0.46692 | 122.438 | -0.33417 | -0.17395 | 0.1236 | 0.18311 | 0.3891 | -0.65918 | -0.10986 | 0.19226 | 0.35706 | 0.2655 | 0.69122 | 121.8109 | 122.5937 | 0.18311 | 122.6624 | 5.0537 | -0.10986 | 122.5937 | 0.18311 | 5.0537 | 121.8109 | 122.6624 | -122.644 | -122.58
1159.3594 | 122.3831 | -0.21515 | 122.2366 | 0.0026703 | 0.018025 | 0.012405 | -0.0029565 | 0.06141 | -0.0061503 | 0.069116 | -0.082397 | 122.3831 | -0.3891 | 0.10986 | 121.5225 | 4.7607 | 0.036621 | 0.33875 | 122.4426 | -0.33875 | -0.17395 | 0.14648 | 0.13275 | 0.32501 | -0.71411 | -0.1236 | 0.20599 | 0.3067 | 0.25177 | 0.55389 | 121.7377 | 122.5983 | 0.13275 | 122.6578 | 4.9759 | -0.1236 | 122.5983 | 0.13275 | 4.9759 | 121.7377 | 122.6578 | -122.6257 | -122.5754
1161.0938 | 122.3282 | -0.22888 | 122.2458 | 0.0026703 | 0.01653 | 0.012405 | -0.0031701 | 0.060983 | -0.0057229 | 0.067193 | -0.036621 | 122.3511 | -0.3891 | 0.20142 | 121.6187 | 4.8614 | 0.059509 | 0.51727 | 122.4152 | -0.33875 | -0.16022 | 0.10528 | 0.19226 | 0.4303 | -0.62714 | -0.10986 | 0.16937 | 0.35248 | 0.28839 | 0.74616 | 121.8475 | 122.58 | 0.19226 | 122.644 | 5.0903 | -0.10986 | 122.58 | 0.19226 | 5.0903 | 121.8475 | 122.644 | -122.6349 | -122.5845
1162.8438 | 122.3969 | -0.20142 | 122.2229 | 0.0026703 | 0.019521 | 0.0094143 | -0.0025293 | 0.060983 | -0.0048685 | 0.067193 | -0.10529 | 122.3923 | -0.39368 | 0.13275 | 121.55 | 4.7791 | 0.045776 | 0.35706 | 122.4243 | -0.32501 | -0.19226 | 0.16937 | 0.09613 | 0.33417 | -0.67291 | -0.1236 | 0.20142 | 0.28839 | 0.24719 | 0.55847 | 121.7514 | 122.5937 | 0.09613 | 122.6257 | 4.9805 | -0.1236 | 122.5937 | 0.09613 | 4.9805 | 121.7514 | 122.6257 | -122.6166 | -122.5479
1164.5312 | 122.4701 | -0.18768 | 122.1863 | -0.0049592 | 0.018025 | 0.0094143 | 3.4284e-05 | 0.060556 | -0.0065775 | 0.068902 | -0.15564 | 122.3831 | -0.43945 | 0.059509 | 121.4676 | 4.7424 | 0.30212 | 0.39368 | 122.4609 | -0.3891 | -0.25177 | 0.19684 | 0.032043 | 0.24719 | -0.71869 | -0.20142 | 0.27466 | 0.28381 | 0.48981 | 0.58136 | 121.6553 | 122.5708 | 0.032043 | 122.6486 | 4.9301 | -0.20142 | 122.5708 | 0.032043 | 4.9301 | 121.6553 | 122.6486 | -122.6257 | -122.5754
1166.2656 | 122.4106 | -0.19684 | 122.1954 | 0.0026703 | 0.020589 | 0.014328 | 0.0017431 | 0.064187 | -0.0082865 | 0.068475 | -0.068665 | 122.3877 | -0.43488 | 0.1236 | 121.5271 | 4.7791 | 0.16937 | 0.41657 | 122.4747 | -0.3479 | -0.23804 | 0.19226 | 0.12817 | 0.32043 | -0.66833 | -0.15106 | 0.27923 | 0.36621 | 0.36621 | 0.6134 | 121.7239 | 122.5845 | 0.12817 | 122.6715 | 4.9759 | -0.15106 | 122.5845 | 0.12817 | 4.9759 | 121.7239 | 122.6715 | -122.6303 | -122.5433
1168.0156 | 122.4197 | -0.19226 | 122.2092 | -0.0049592 | 0.018239 | 0.013046 | -0.00017952 | 0.063547 | -0.0067911 | 0.06997 | -0.10071 | 122.406 | -0.4303 | 0.11902 | 121.5271 | 4.7836 | 0.22888 | 0.42572 | 122.4747 | -0.35248 | -0.23804 | 0.19684 | 0.091553 | 0.31128 | -0.68207 | -0.16022 | 0.2655 | 0.32959 | 0.42114 | 0.61798 | 121.7194 | 122.5983 | 0.091553 | 122.6669 | 4.9759 | -0.16022 | 122.5983 | 0.091553 | 4.9759 | 121.7194 | 122.6669 | -122.6395 | -122.5616
1169.7031 | 122.4655 | -0.15564 | 122.1817 | -0.0049592 | 0.019948 | 0.013046 | -0.0021021 | 0.06376 | -0.0059365 | 0.068475 | -0.14191 | 122.3923 | -0.4303 | 0.050354 | 121.4676 | 4.6921 | 0.15564 | 0.27008 | 122.5159 | -0.36163 | -0.27466 | 0.21057 | 0.013733 | 0.20599 | -0.71411 | -0.20599 | 0.33417 | 0.28839 | 0.31128 | 0.42572 | 121.6232 | 122.5479 | 0.013733 | 122.6715 | 4.8477 | -0.20599 | 122.5479 | 0.013733 | 4.8477 | 121.6232 | 122.6715 | -122.612 | -122.5433
1171.4531 | 122.3373 | -0.22888 | 122.2458 | 0.0026703 | 0.018453 | 0.012405 | -0.0050927 | 0.066537 | -0.0072183 | 0.069543 | -0.018311 | 122.3969 | -0.36163 | 0.17853 | 121.6003 | 4.8294 | -0.082397 | 0.37537 | 122.4289 | -0.32044 | -0.13275 | 0.15106 | 0.21057 | 0.40741 | -0.64545 | -0.091553 | 0.1831 | 0.34332 | 0.14649 | 0.60425 | 121.8292 | 122.6257 | 0.21057 | 122.6578 | 5.0583 | -0.091553 | 122.6257 | 0.21057 | 5.0583 | 121.8292 | 122.6578 | -122.6074 | -122.5662
1173.2031 | 122.4197 | -0.17853 | 122.2183 | 0.0103 | 0.018025 | 0.011551 | 0.0015295 | 0.062692 | -0.0063639 | 0.071466 | -0.07782 | 122.4014 | -0.40741 | 0.11902 | 121.5683 | 4.7928 | 0.18768 | 0.43945 | 122.5113 | -0.3479 | -0.22888 | 0.1831 | 0.10071 | 0.29755 | -0.65002 | -0.16937 | 0.29297 | 0.32959 | 0.36621 | 0.61798 | 121.7468 | 122.58 | 0.10071 | 122.6898 | 4.9713 | -0.16937 | 122.58 | 0.10071 | 4.9713 | 121.7468 | 122.6898 | -122.6257 | -122.5662
1174.8906 | 122.4792 | -0.16022 | 122.2092 | -0.0049592 | 0.020589 | 0.012619 | -0.0048791 | 0.064401 | -0.0063639 | 0.069116 | -0.14191 | 122.4518 | -0.40741 | 0.064087 | 121.4996 | 4.7699 | 0.29755 | 0.37994 | 122.5113 | -0.35706 | -0.24719 | 0.24262 | 0.01831 | 0.2243 | -0.70953 | -0.19684 | 0.30213 | 0.2655 | 0.45776 | 0.54016 | 121.6599 | 122.612 | 0.01831 | 122.6715 | 4.9301 | -0.19684 | 122.612 | 0.01831 | 4.9301 | 121.6599 | 122.6715 | -122.6166 | -122.5662
1176.6406 | 122.3373 | -0.2243 | 122.2549 | -0.0049592 | 0.015889 | 0.011337 | -0.0040247 | 0.064615 | -0.0063639 | 0.068261 | -0.022888 | 122.3831 | -0.37079 | 0.16479 | 121.582 | 4.8111 | -0.045776 | 0.36163 | 122.438 | -0.30212 | -0.14648 | 0.12817 | 0.20142 | 0.3891 | -0.67291 | -0.07782 | 0.18311 | 0.3479 | 0.17853 | 0.58594 | 121.8063 | 122.6074 | 0.20142 | 122.6624 | 5.0354 | -0.07782 | 122.6074 | 0.20142 | 5.0354 | 121.8063 | 122.6624 | -122.6257 | -122.5571
1178.3906 | 122.4747 | -0.16937 | 122.2366 | 0.0103 | 0.02123 | 0.013046 | -0.00060672 | 0.066537 | -0.0050821 | 0.068475 | -0.14191 | 122.4014 | -0.40741 | 0.050354 | 121.4767 | 4.7333 | 0.16937 | 0.2655 | 122.5113 | -0.34332 | -0.23804 | 0.16479 | 0.027466 | 0.21973 | -0.75989 | -0.17395 | 0.27466 | 0.2655 | 0.33875 | 0.43488 | 121.6461 | 122.5708 | 0.027466 | 122.6807 | 4.9026 | -0.17395 | 122.5708 | 0.027466 | 4.9026 | 121.6461 | 122.6807 | -122.644 | -122.58
1180.0781 | 122.374 | -0.20599 | 122.2687 | -0.012589 | 0.017171 | 0.014541 | -0.0065881 | 0.064615 | -0.0074319 | 0.068902 | -0.041199 | 122.3465 | -0.36621 | 0.13733 | 121.5546 | 4.8203 | -0.027466 | 0.3479 | 122.4792 | -0.31128 | -0.16022 | 0.07782 | 0.1648 | 0.34332 | -0.71411 | -0.10528 | 0.21057 | 0.32501 | 0.17853 | 0.55389 | 121.7606 | 122.5525 | 0.1648 | 122.6852 | 5.0262 | -0.10528 | 122.5525 | 0.1648 | 5.0262 | 121.7606 | 122.6852 | -122.6349 | -122.58
1181.8281 | 122.4655 | -0.14648 | 122.2366 | -0.0049592 | 0.01888 | 0.0094143 | -0.0035973 | 0.064615 | -0.0080729 | 0.067834 | -0.13733 | 122.4014 | -0.40741 | 0.068665 | 121.5042 | 4.7653 | 0.31586 | 0.3891 | 122.5388 | -0.37079 | -0.26093 | 0.16479 | 0.009155 | 0.21515 | -0.73242 | -0.2243 | 0.30212 | 0.27008 | 0.46234 | 0.53558 | 121.6507 | 122.5479 | 0.009155 | 122.6852 | 4.9118 | -0.2243 | 122.5479 | 0.009155 | 4.9118 | 121.6507 | 122.6852 | -122.644 | -122.6074
1183.5312 | 122.3877 | -0.22888 | 122.2595 | -0.012589 | 0.016957 | 0.011764 | -0.0046655 | 0.060342 | -0.0067911 | 0.067193 | -0.059509 | 122.4014 | -0.36621 | 0.11444 | 121.5591 | 4.8019 | 0.013733 | 0.32959 | 122.4609 | -0.32959 | -0.13733 | 0.14191 | 0.16937 | 0.34332 | -0.70038 | -0.10071 | 0.20142 | 0.3067 | 0.24261 | 0.55847 | 121.788 | 122.6303 | 0.16937 | 122.6898 | 5.0308 | -0.10071 | 122.6303 | 0.16937 | 5.0308 | 121.788 | 122.6898 | -122.6257 | -122.5891
1185.2812 | 122.4564 | -0.16937 | 122.2137 | 0.0026703 | 0.018025 | 0.012192 | -0.00082032 | 0.062265 | -0.0063639 | 0.071466 | -0.1236 | 122.3969 | -0.41199 | 0.073242 | 121.4996 | 4.7836 | 0.27924 | 0.3891 | 122.4701 | -0.37079 | -0.24261 | 0.18311 | 0.045777 | 0.24261 | -0.71411 | -0.20142 | 0.25635 | 0.28839 | 0.44861 | 0.55847 | 121.669 | 122.5662 | 0.045777 | 122.6395 | 4.953 | -0.20142 | 122.5662 | 0.045777 | 4.953 | 121.669 | 122.6395 | -122.6257 | -122.5845
1187.0312 | 122.3282 | -0.21515 | 122.2549 | 0.0103 | 0.014608 | 0.0092007 | -0.0048791 | 0.061838 | -0.0061503 | 0.065911 | -0.032043 | 122.3877 | -0.36163 | 0.19226 | 121.6095 | 4.9072 | 0.082397 | 0.52643 | 122.4747 | -0.3067 | -0.14648 | 0.13275 | 0.18311 | 0.40741 | -0.64545 | -0.091553 | 0.21973 | 0.32959 | 0.29755 | 0.74158 | 121.8246 | 122.6028 | 0.18311 | 122.6898 | 5.1224 | -0.091553 | 122.6028 | 0.18311 | 5.1224 | 121.8246 | 122.6898 | -122.6166 | -122.5616
1188.7188 | 122.4426 | -0.16479 | 122.2092 | 0.0026703 | 0.017598 | 0.014114 | 0.0021705 | 0.061624 | -0.0061503 | 0.069116 | -0.10529 | 122.4243 | -0.42114 | 0.11444 | 121.5454 | 4.834 | 0.24719 | 0.42114 | 122.525 | -0.35248 | -0.25635 | 0.21515 | 0.059509 | 0.27924 | -0.66376 | -0.18768 | 0.31586 | 0.31586 | 0.41199 | 0.58594 | 121.7102 | 122.5891 | 0.059509 | 122.6898 | 4.9988 | -0.18768 | 122.5891 | 0.059509 | 4.9988 | 121.7102 | 122.6898 | -122.6303 | -122.5616
1190.4688 | 122.4014 | -0.19684 | 122.2504 | 0.0026703 | 0.017171 | 0.0087735 | -0.0057337 | 0.061624 | -0.0061503 | 0.068475 | -0.09613 | 122.4014 | -0.37079 | 0.11902 | 121.5591 | 4.8248 | 0.059509 | 0.35706 | 122.4976 | -0.33417 | -0.17395 | 0.15106 | 0.10071 | 0.31586 | -0.69122 | -0.13733 | 0.24719 | 0.27466 | 0.25635 | 0.55389 | 121.756 | 122.5983 | 0.10071 | 122.6944 | 5.0217 | -0.13733 | 122.5983 | 0.10071 | 5.0217 | 121.756 | 122.6944 | -122.6212 | -122.5845
1192.2031 | 122.3877 | -0.1831 | 122.2412 | 0.0026703 | 0.017385 | 0.011337 | -0.0029565 | 0.062051 | -0.0074319 | 0.068688 | -0.054932 | 122.4106 | -0.3891 | 0.13733 | 121.5729 | 4.8614 | 0.2243 | 0.45319 | 122.4976 | -0.36163 | -0.20599 | 0.16937 | 0.12817 | 0.32043 | -0.66834 | -0.17853 | 0.25635 | 0.33417 | 0.40741 | 0.63629 | 121.756 | 122.5937 | 0.12817 | 122.6807 | 5.0446 | -0.17853 | 122.5937 | 0.12817 | 5.0446 | 121.756 | 122.6807 | -122.6303 | -122.6028
1193.9688 | 122.4472 | -0.16937 | 122.2183 | -0.0049592 | 0.017385 | 0.016037 | 3.4284e-05 | 0.064401 | -0.0074319 | 0.068048 | -0.11444 | 122.406 | -0.41657 | 0.1236 | 121.5317 | 4.8477 | 0.24261 | 0.42572 | 122.5204 | -0.35248 | -0.24719 | 0.18768 | 0.054932 | 0.29297 | -0.68665 | -0.18311 | 0.30212 | 0.30212 | 0.41199 | 0.59509 | 121.701 | 122.5754 | 0.054932 | 122.6898 | 5.0171 | -0.18311 | 122.5754 | 0.054932 | 5.0171 | 121.701 | 122.6898 | -122.6349 | -122.5708
1195.7188 | 122.4014 | -0.19226 | 122.2504 | -0.0049592 | 0.020803 | 0.0089871 | -0.0050927 | 0.062051 | -0.0029459 | 0.06997 | -0.082397 | 122.3969 | -0.36621 | 0.12817 | 121.5866 | 4.8431 | 0.059509 | 0.38452 | 122.4609 | -0.33417 | -0.17395 | 0.14648 | 0.10986 | 0.32044 | -0.66376 | -0.14191 | 0.21057 | 0.28381 | 0.25177 | 0.57678 | 121.7789 | 122.5891 | 0.10986 | 122.6532 | 5.0354 | -0.14191 | 122.5891 | 0.10986 | 5.0354 | 121.7789 | 122.6532 | -122.6166 | -122.5845
1197.4062 | 122.4655 | -0.1831 | 122.2366 | 0.0026703 | 0.019734 | 0.013046 | -0.0018885 | 0.061624 | -0.0055093 | 0.068475 | -0.1236 | 122.4335 | -0.39825 | 0.091553 | 121.5179 | 4.8157 | 0.28381 | 0.39368 | 122.5296 | -0.37994 | -0.21515 | 0.19684 | 0.059509 | 0.27466 | -0.71869 | -0.19684 | 0.29297 | 0.27466 | 0.46692 | 0.57678 | 121.701 | 122.6166 | 0.059509 | 122.7127 | 4.9988 | -0.19684 | 122.6166 | 0.059509 | 4.9988 | 121.701 | 122.7127 | -122.6349 | -122.6166
1199.1562 | 122.3557 | -0.20599 | 122.2824 | -0.0049592 | 0.016103 | 0.012832 | -0.0012475 | 0.063333 | -0.0055093 | 0.067834 | -0.013733 | 122.4197 | -0.36621 | 0.19684 | 121.6278 | 4.8752 | -0.059509 | 0.3891 | 122.4747 | -0.32501 | -0.16022 | 0.13733 | 0.19226 | 0.40283 | -0.6546 | -0.11902 | 0.19226 | 0.35248 | 0.14649 | 0.59509 | 121.8338 | 122.6257 | 0.19226 | 122.6807 | 5.0812 | -0.11902 | 122.6257 | 0.19226 | 5.0812 | 121.8338 | 122.6807 | -122.6486 | -122.6074
1200.9062 | 122.406 | -0.19684 | 122.2641 | 0.0103 | 0.018025 | 0.011764 | -0.0033837 | 0.063119 | -0.0078591 | 0.068688 | -0.032043 | 122.406 | -0.37079 | 0.16022 | 121.5912 | 4.9118 | 0.18768 | 0.45776 | 122.5159 | -0.33417 | -0.17395 | 0.14191 | 0.1648 | 0.35706 | -0.67291 | -0.13733 | 0.25177 | 0.33875 | 0.38452 | 0.6546 | 121.788 | 122.6028 | 0.1648 | 122.7127 | 5.1086 | -0.13733 | 122.6028 | 0.1648 | 5.1086 | 121.788 | 122.7127 | -122.6349 | -122.5983
1202.5938 | 122.4243 | -0.18768 | 122.2366 | -0.0049592 | 0.022512 | 0.013046 | 0.0023841 | 0.064615 | -0.0070047 | 0.069329 | -0.054932 | 122.4197 | -0.39368 | 0.15106 | 121.55 | 4.8798 | 0.19226 | 0.40741 | 122.5296 | -0.34332 | -0.20599 | 0.18311 | 0.13275 | 0.33874 | -0.68664 | -0.15564 | 0.29297 | 0.33875 | 0.37994 | 0.59509 | 121.7377 | 122.6074 | 0.13275 | 122.7173 | 5.0674 | -0.15564 | 122.6074 | 0.13275 | 5.0674 | 121.7377 | 122.7173 | -122.6303 | -122.58
1204.3438 | 122.3648 | -0.20142 | 122.2504 | -0.0049592 | 0.018666 | 0.0089871 | -0.0050927 | 0.062906 | -0.0046549 | 0.068475 | -0.045776 | 122.4335 | -0.3479 | 0.19684 | 121.6278 | 4.9301 | 0.045776 | 0.45776 | 122.4747 | -0.32501 | -0.14648 | 0.18311 | 0.15564 | 0.39825 | -0.62256 | -0.1236 | 0.2243 | 0.30212 | 0.24719 | 0.65918 | 121.8292 | 122.6349 | 0.15564 | 122.6761 | 5.1315 | -0.1236 | 122.6349 | 0.15564 | 5.1315 | 121.8292 | 122.6761 | -122.5983 | -122.5754
1206.0938 | 122.4792 | -0.16479 | 122.2458 | 0.0103 | 0.019094 | 0.015182 | 0.00067508 | 0.063119 | -0.0061503 | 0.066339 | -0.10529 | 122.4197 | -0.41199 | 0.082397 | 121.5179 | 4.8111 | 0.18768 | 0.31586 | 122.5388 | -0.3479 | -0.24719 | 0.17395 | 0.059509 | 0.24719 | -0.72785 | -0.1831 | 0.29297 | 0.3067 | 0.35248 | 0.48065 | 121.6827 | 122.5845 | 0.059509 | 122.7036 | 4.9759 | -0.1831 | 122.5845 | 0.059509 | 4.9759 | 121.6827 | 122.7036 | -122.6578 | -122.5937
1207.8438 | 122.4335 | -0.17853 | 122.2366 | 0.0026703 | 0.02123 | 0.011764 | 0.00067508 | 0.064828 | -0.0067911 | 0.070825 | -0.07782 | 122.4106 | -0.3891 | 0.13275 | 121.5775 | 4.8935 | 0.1831 | 0.40741 | 122.5067 | -0.36621 | -0.21057 | 0.17395 | 0.10071 | 0.31128 | -0.65918 | -0.18768 | 0.27008 | 0.31128 | 0.36163 | 0.58594 | 121.756 | 122.5891 | 0.10071 | 122.6852 | 5.072 | -0.18768 | 122.5891 | 0.10071 | 5.072 | 121.756 | 122.6852 | -122.6257 | -122.6028
1209.6094 | 122.3511 | -0.2243 | 122.2733 | -0.0049592 | 0.018666 | 0.014969 | -0.0074427 | 0.061838 | -0.0063639 | 0.069757 | -0.013733 | 122.4197 | -0.35706 | 0.19684 | 121.6507 | 4.9942 | 0.041199 | 0.50812 | 122.4976 | -0.32501 | -0.13275 | 0.14649 | 0.21057 | 0.42114 | -0.62256 | -0.10071 | 0.22431 | 0.34332 | 0.2655 | 0.73242 | 121.875 | 122.644 | 0.21057 | 122.7219 | 5.2185 | -0.10071 | 122.644 | 0.21057 | 5.2185 | 121.875 | 122.7219 | -122.6303 | -122.5983
1211.2969 | 122.3602 | -0.21057 | 122.2778 | 0.0026703 | 0.018025 | 0.011337 | -0.0018885 | 0.062478 | -0.0059365 | 0.068475 | -0.022888 | 122.4243 | -0.37537 | 0.17395 | 121.6187 | 4.9118 | -0.050354 | 0.38452 | 122.4976 | -0.31586 | -0.16479 | 0.14648 | 0.18768 | 0.38452 | -0.65918 | -0.10529 | 0.21973 | 0.35248 | 0.16022 | 0.59509 | 121.8292 | 122.6349 | 0.18768 | 122.7081 | 5.1224 | -0.10529 | 122.6349 | 0.18768 | 5.1224 | 121.8292 | 122.7081 | -122.6532 | -122.5937
1213 | 122.438 | -0.1831 | 122.2366 | -0.0049592 | 0.017171 | 0.0098417 | -0.0048791 | 0.061624 | -0.0072183 | 0.066125 | -0.07782 | 122.4243 | -0.40283 | 0.10071 | 121.5363 | 4.8798 | 0.26093 | 0.42114 | 122.5159 | -0.36163 | -0.21973 | 0.18768 | 0.10528 | 0.28381 | -0.70038 | -0.17853 | 0.27924 | 0.32501 | 0.44403 | 0.60425 | 121.7194 | 122.6074 | 0.10528 | 122.699 | 5.0629 | -0.17853 | 122.6074 | 0.10528 | 5.0629 | 121.7194 | 122.699 | -122.6395 | -122.5983
1214.7656 | 122.3831 | -0.19226 | 122.2504 | 0.0026703 | 0.01653 | 0.012832 | -0.0023157 | 0.062906 | -0.0076455 | 0.069329 | -0.036621 | 122.3877 | -0.37994 | 0.17853 | 121.6095 | 4.9759 | 0.15564 | 0.50354 | 122.4884 | -0.32501 | -0.18768 | 0.13733 | 0.15564 | 0.37079 | -0.64087 | -0.13275 | 0.23804 | 0.34332 | 0.3479 | 0.6958 | 121.8018 | 122.58 | 0.15564 | 122.6807 | 5.1682 | -0.13275 | 122.58 | 0.15564 | 5.1682 | 121.8018 | 122.6807 | -122.6303 | -122.5754
1216.5156 | 122.3785 | -0.21515 | 122.287 | -0.012589 | 0.015462 | 0.014328 | -0.0040247 | 0.062051 | -0.0061503 | 0.067193 | -0.022888 | 122.3877 | -0.37537 | 0.14191 | 121.5775 | 4.9026 | -0.009155 | 0.36163 | 122.5113 | -0.32959 | -0.16022 | 0.10071 | 0.19226 | 0.35706 | -0.70953 | -0.11444 | 0.22431 | 0.35248 | 0.20599 | 0.57678 | 121.7926 | 122.6028 | 0.19226 | 122.7264 | 5.1178 | -0.11444 | 122.6028 | 0.19226 | 5.1178 | 121.7926 | 122.7264 | -122.6624 | -122.6166
1218.2031 | 122.4792 | -0.16022 | 122.2595 | -0.0049592 | 0.020162 | 0.012832 | 0.00067508 | 0.062906 | -0.0063639 | 0.069329 | -0.10071 | 122.4426 | -0.40741 | 0.091553 | 121.5225 | 4.8386 | 0.073242 | 0.29755 | 122.5342 | -0.33417 | -0.24719 | 0.18311 | 0.059509 | 0.25177 | -0.737 | -0.17395 | 0.27466 | 0.3067 | 0.23346 | 0.45776 | 121.6827 | 122.6028 | 0.059509 | 122.6944 | 4.9988 | -0.17395 | 122.6028 | 0.059509 | 4.9988 | 121.6827 | 122.6944 | -122.6669 | -122.5937
1219.9688 | 122.4152 | -0.19226 | 122.2916 | 0.0026703 | 0.018666 | 0.010055 | -0.0059473 | 0.059915 | -0.0063639 | 0.06997 | -0.068665 | 122.4289 | -0.3891 | 0.14191 | 121.5729 | 4.9026 | 0.041199 | 0.3479 | 122.5296 | -0.32959 | -0.19684 | 0.13733 | 0.1236 | 0.33417 | -0.71869 | -0.13733 | 0.23804 | 0.32043 | 0.23346 | 0.54016 | 121.7651 | 122.6212 | 0.1236 | 122.7219 | 5.0949 | -0.13733 | 122.6212 | 0.1236 | 5.0949 | 121.7651 | 122.7219 | -122.6807 | -122.6212
1221.7031 | 122.3831 | -0.21057 | 122.2595 | 0.0103 | 0.017598 | 0.016037 | -0.0033837 | 0.061197 | -0.0059365 | 0.068048 | -0.022888 | 122.4243 | -0.37537 | 0.18768 | 121.6187 | 4.9805 | 0.14648 | 0.50812 | 122.5342 | -0.32501 | -0.16479 | 0.16479 | 0.18768 | 0.39825 | -0.64087 | -0.11444 | 0.27466 | 0.35248 | 0.35706 | 0.71869 | 121.8292 | 122.6349 | 0.18768 | 122.7448 | 5.191 | -0.11444 | 122.6349 | 0.18768 | 5.191 | 121.8292 | 122.7448 | -122.6349 | -122.5845
1223.3906 | 122.3877 | -0.19226 | 122.2961 | 0.0026703 | 0.013326 | 0.010269 | -0.0053063 | 0.061624 | -0.0059365 | 0.068261 | -0.022888 | 122.406 | -0.37994 | 0.18768 | 121.5958 | 4.9301 | -0.036621 | 0.37079 | 122.4792 | -0.28381 | -0.18768 | 0.10986 | 0.16937 | 0.37994 | -0.70038 | -0.091552 | 0.1831 | 0.35706 | 0.15564 | 0.56305 | 121.788 | 122.5983 | 0.16937 | 122.6715 | 5.1224 | -0.091552 | 122.5983 | 0.16937 | 5.1224 | 121.788 | 122.6715 | -122.6761 | -122.58
1225.0938 | 122.3602 | -0.21973 | 122.2687 | -0.012589 | 0.014394 | 0.0057827 | -0.0035973 | 0.060556 | -0.0063639 | 0.06762 | -0.018311 | 122.3831 | -0.37537 | 0.21973 | 121.6599 | 4.9942 | 0.091553 | 0.50354 | 122.4884 | -0.31586 | -0.15564 | 0.11444 | 0.20142 | 0.43945 | -0.60883 | -0.09613 | 0.21973 | 0.35705 | 0.31128 | 0.72327 | 121.8796 | 122.6028 | 0.20142 | 122.7081 | 5.2139 | -0.09613 | 122.6028 | 0.20142 | 5.2139 | 121.8796 | 122.7081 | -122.644 | -122.5845
1226.8594 | 122.438 | -0.1831 | 122.2595 | 0.0026703 | 0.01888 | 0.015396 | 0.00088868 | 0.063547 | -0.0055093 | 0.06997 | -0.059509 | 122.4472 | -0.37079 | 0.15106 | 121.5958 | 4.9072 | 0.004578 | 0.35706 | 122.493 | -0.32501 | -0.18768 | 0.18768 | 0.1236 | 0.33417 | -0.66376 | -0.14191 | 0.23346 | 0.31128 | 0.18768 | 0.54016 | 121.7789 | 122.6303 | 0.1236 | 122.6761 | 5.0903 | -0.14191 | 122.6303 | 0.1236 | 5.0903 | 121.7789 | 122.6761 | -122.6303 | -122.5845
1228.6094 | 122.4838 | -0.16937 | 122.2458 | -0.012589 | 0.018025 | 0.013046 | 0.0025977 | 0.064187 | -0.0087137 | 0.06762 | -0.11444 | 122.4564 | -0.41199 | 0.068665 | 121.4996 | 4.8386 | 0.19226 | 0.28839 | 122.5433 | -0.32501 | -0.24261 | 0.21057 | 0.054932 | 0.23804 | -0.74616 | -0.15564 | 0.29755 | 0.29755 | 0.36163 | 0.45776 | 121.669 | 122.6257 | 0.054932 | 122.7127 | 5.0079 | -0.15564 | 122.6257 | 0.054932 | 5.0079 | 121.669 | 122.7127 | -122.6578 | -122.5708
1230.2969 | 122.4838 | -0.15564 | 122.2687 | -0.012589 | 0.017385 | 0.012405 | -0.0029565 | 0.061624 | -0.0048685 | 0.068475 | -0.14648 | 122.4426 | -0.42572 | 0.086975 | 121.5363 | 4.9118 | 0.3067 | 0.40283 | 122.5433 | -0.36163 | -0.27008 | 0.17395 | 0.009156 | 0.24261 | -0.73242 | -0.20599 | 0.27466 | 0.27924 | 0.46234 | 0.55847 | 121.6919 | 122.5983 | 0.009156 | 122.699 | 5.0674 | -0.20599 | 122.5983 | 0.009156 | 5.0674 | 121.6919 | 122.699 | -122.6944 | -122.6303
1232.0469 | 122.4335 | -0.19684 | 122.287 | 0.0026703 | 0.018025 | 0.011764 | -0.0068017 | 0.062478 | -0.0031595 | 0.066552 | -0.073242 | 122.4289 | -0.37079 | 0.12817 | 121.6187 | 4.9347 | 0.059509 | 0.36621 | 122.5159 | -0.31586 | -0.17395 | 0.14191 | 0.1236 | 0.32501 | -0.66833 | -0.11902 | 0.22888 | 0.29755 | 0.25635 | 0.56305 | 121.8155 | 122.6257 | 0.1236 | 122.7127 | 5.1315 | -0.11902 | 122.6257 | 0.1236 | 5.1315 | 121.8155 | 122.7127 | -122.6578 | -122.6028
1233.7969 | 122.438 | -0.16479 | 122.2595 | 0.0026703 | 0.018666 | 0.011551 | 0.00046148 | 0.065042 | -0.0078591 | 0.067407 | -0.09613 | 122.4518 | -0.40741 | 0.12817 | 121.5637 | 4.9484 | 0.23804 | 0.43945 | 122.5708 | -0.33875 | -0.24261 | 0.19226 | 0.068665 | 0.29297 | -0.6958 | -0.17395 | 0.31128 | 0.31128 | 0.40283 | 0.60425 | 121.7285 | 122.6166 | 0.068665 | 122.7356 | 5.1132 | -0.17395 | 122.6166 | 0.068665 | 5.1132 | 121.7285 | 122.7356 | -122.6669 | -122.5983
1235.5 | 122.4106 | -0.1831 | 122.2961 | -0.0049592 | 0.018666 | 0.011123 | -0.0074427 | 0.062692 | -0.0063639 | 0.066766 | -0.073242 | 122.4426 | -0.36163 | 0.15564 | 121.6095 | 4.9576 | 0.059509 | 0.39368 | 122.5159 | -0.32501 | -0.17853 | 0.14648 | 0.10986 | 0.33874 | -0.68665 | -0.14191 | 0.21973 | 0.28839 | 0.24261 | 0.57678 | 121.7926 | 122.6257 | 0.10986 | 122.699 | 5.1407 | -0.14191 | 122.6257 | 0.10986 | 5.1407 | 121.7926 | 122.699 | -122.6578 | -122.6212
1237.2344 | 122.3877 | -0.18768 | 122.3053 | 0.0026703 | 0.021016 | 0.011123 | -0.0033837 | 0.059488 | -0.0050821 | 0.069543 | -0.013733 | 122.4335 | -0.3479 | 0.19226 | 121.637 | 4.9988 | 0.17853 | 0.49896 | 122.5388 | -0.32044 | -0.16022 | 0.12817 | 0.17395 | 0.37994 | -0.66833 | -0.13275 | 0.23346 | 0.33417 | 0.36621 | 0.68664 | 121.8246 | 122.6212 | 0.17395 | 122.7264 | 5.1865 | -0.13275 | 122.6212 | 0.17395 | 5.1865 | 121.8246 | 122.7264 | -122.6532 | -122.6257
1238.9844 | 122.3969 | -0.20142 | 122.2961 | -0.0049592 | 0.01653 | 0.011123 | -0.00017952 | 0.064401 | -0.0061503 | 0.071038 | -0.027466 | 122.4014 | -0.37537 | 0.18768 | 121.6278 | 4.9896 | -0.032043 | 0.37537 | 122.5571 | -0.29297 | -0.17395 | 0.10528 | 0.17395 | 0.3891 | -0.66833 | -0.091553 | 0.26093 | 0.3479 | 0.16937 | 0.57678 | 121.8292 | 122.6028 | 0.17395 | 122.7585 | 5.191 | -0.091553 | 122.6028 | 0.17395 | 5.191 | 121.8292 | 122.7585 | -122.6715 | -122.5891
1240.6719 | 122.4289 | -0.19226 | 122.2733 | -0.0049592 | 0.019521 | 0.012192 | -0.00039312 | 0.064187 | -0.0063639 | 0.066979 | -0.059509 | 122.4472 | -0.37994 | 0.16479 | 121.5866 | 4.953 | 0.009155 | 0.35248 | 122.5342 | -0.31128 | -0.18768 | 0.17395 | 0.13275 | 0.35706 | -0.68664 | -0.11902 | 0.26093 | 0.32044 | 0.20142 | 0.54474 | 121.7789 | 122.6395 | 0.13275 | 122.7264 | 5.1453 | -0.11902 | 122.6395 | 0.13275 | 5.1453 | 121.7789 | 122.7264 | -122.6532 | -122.5845
1242.4219 | 122.4518 | -0.16022 | 122.2504 | 0.0026703 | 0.02123 | 0.013687 | 3.4284e-05 | 0.063974 | -0.0082865 | 0.068902 | -0.073242 | 122.4747 | -0.40741 | 0.14648 | 121.5958 | 4.953 | 0.23346 | 0.44403 | 122.5388 | -0.35248 | -0.24719 | 0.2243 | 0.086975 | 0.3067 | -0.6546 | -0.19226 | 0.28839 | 0.33417 | 0.39368 | 0.60425 | 121.756 | 122.6349 | 0.086975 | 122.699 | 5.1132 | -0.19226 | 122.6349 | 0.086975 | 5.1132 | 121.756 | 122.699 | -122.6578 | -122.6028
1244.1094 | 122.3785 | -0.2243 | 122.287 | 0.0103 | 0.019094 | 0.014328 | -0.0033837 | 0.064187 | -0.0061503 | 0.068688 | -0.004578 | 122.4655 | -0.33417 | 0.1831 | 121.6324 | 4.9942 | -0.054932 | 0.38452 | 122.4976 | -0.32959 | -0.10986 | 0.17853 | 0.21973 | 0.40741 | -0.6546 | -0.10529 | 0.21057 | 0.32959 | 0.16937 | 0.60882 | 121.8567 | 122.6898 | 0.21973 | 122.7219 | 5.2185 | -0.10529 | 122.6898 | 0.21973 | 5.2185 | 121.8567 | 122.7219 | -122.6212 | -122.6166
1245.8594 | 122.4518 | -0.16022 | 122.2504 | -0.0049592 | 0.017385 | 0.0087735 | -0.0016747 | 0.063333 | -0.0065775 | 0.066552 | -0.064087 | 122.4472 | -0.41199 | 0.1236 | 121.582 | 4.9667 | 0.25177 | 0.43945 | 122.5616 | -0.33875 | -0.25177 | 0.19684 | 0.09613 | 0.28381 | -0.66833 | -0.17853 | 0.31128 | 0.3479 | 0.41199 | 0.59967 | 121.7422 | 122.6074 | 0.09613 | 122.7219 | 5.127 | -0.17853 | 122.6074 | 0.09613 | 5.127 | 121.7422 | 122.7219 | -122.6624 | -122.5891
1247.6094 | 122.5159 | -0.15564 | 122.2824 | 0.0026703 | 0.019521 | 0.013046 | -0.00060672 | 0.06376 | -0.0031595 | 0.069329 | -0.10529 | 122.4884 | -0.39368 | 0.086975 | 121.5454 | 4.9026 | 0.15106 | 0.29297 | 122.5845 | -0.33417 | -0.23804 | 0.20599 | 0.050354 | 0.24261 | -0.737 | -0.17853 | 0.30212 | 0.28839 | 0.3067 | 0.44861 | 121.7011 | 122.644 | 0.050354 | 122.7402 | 5.0583 | -0.17853 | 122.644 | 0.050354 | 5.0583 | 121.7011 | 122.7402 | -122.6761 | -122.6166
1249.3594 | 122.4609 | -0.16022 | 122.2916 | -0.012589 | 0.021016 | 0.017105 | -0.0027429 | 0.063119 | -0.0044413 | 0.068261 | -0.022888 | 122.5159 | -0.37079 | 0.16479 | 121.6003 | 4.9988 | 0.21057 | 0.44861 | 122.5433 | -0.34332 | -0.21057 | 0.2243 | 0.13733 | 0.32501 | -0.69122 | -0.18311 | 0.25177 | 0.3479 | 0.37079 | 0.60882 | 121.7606 | 122.6761 | 0.13733 | 122.7036 | 5.159 | -0.18311 | 122.6761 | 0.13733 | 5.159 | 121.7606 | 122.7036 | -122.6624 | -122.6349
1251.1094 | 122.4106 | -0.17853 | 122.2641 | 0.0026703 | 0.017385 | 0.0092007 | -0.0093653 | 0.060983 | -0.0046549 | 0.068261 | -0.045776 | 122.4838 | -0.37079 | 0.13275 | 121.6232 | 4.9713 | 0.068665 | 0.35706 | 122.5342 | -0.32044 | -0.19226 | 0.21973 | 0.13275 | 0.31128 | -0.64087 | -0.14191 | 0.27008 | 0.32501 | 0.24719 | 0.53558 | 121.8018 | 122.6624 | 0.13275 | 122.7127 | 5.1498 | -0.14191 | 122.6624 | 0.13275 | 5.1498 | 121.8018 | 122.7127 | -122.6349 | -122.5845
1252.8906 | 122.3602 | -0.18768 | 122.3007 | 0.0026703 | 0.019094 | 0.013687 | -0.0063745 | 0.064615 | -0.0059365 | 0.068902 | 0.018311 | 122.4564 | -0.34332 | 0.2243 | 121.7102 | 5.0949 | 0.082397 | 0.51727 | 122.5296 | -0.3067 | -0.15564 | 0.15564 | 0.20599 | 0.41199 | -0.59051 | -0.11902 | 0.22888 | 0.36163 | 0.27008 | 0.70496 | 121.8979 | 122.644 | 0.20599 | 122.7173 | 5.2826 | -0.11902 | 122.644 | 0.20599 | 5.2826 | 121.8979 | 122.7173 | -122.644 | -122.6074
1254.6562 | 122.493 | -0.15106 | 122.2961 | -0.0049592 | 0.019094 | 0.0098417 | -0.00060672 | 0.064615 | -0.0085001 | 0.068475 | -0.086975 | 122.493 | -0.39368 | 0.10529 | 121.5591 | 4.9255 | 0.068665 | 0.31128 | 122.5708 | -0.33417 | -0.24261 | 0.19684 | 0.064087 | 0.25635 | -0.737 | -0.1831 | 0.27466 | 0.3067 | 0.21973 | 0.46234 | 121.7102 | 122.644 | 0.064087 | 122.7219 | 5.0766 | -0.1831 | 122.644 | 0.064087 | 5.0766 | 121.7102 | 122.7219 | -122.6898 | -122.6303
1256.4062 | 122.4426 | -0.16022 | 122.287 | -0.0049592 | 0.021871 | 0.01326 | 0.00067508 | 0.064828 | -0.0067911 | 0.067834 | -0.032043 | 122.493 | -0.38452 | 0.16937 | 121.6141 | 5.0217 | 0.21515 | 0.43945 | 122.5845 | -0.32501 | -0.2243 | 0.20599 | 0.12817 | 0.32959 | -0.67291 | -0.1648 | 0.29755 | 0.35248 | 0.37537 | 0.59967 | 121.7743 | 122.6532 | 0.12817 | 122.7448 | 5.1819 | -0.1648 | 122.6532 | 0.12817 | 5.1819 | 121.7743 | 122.7448 | -122.6715 | -122.612
1258.1094 | 122.374 | -0.1831 | 122.3099 | 0.0026703 | 0.016957 | 0.013473 | -0.0061609 | 0.061624 | -0.0048685 | 0.06762 | 0.004578 | 122.4884 | -0.33417 | 0.21515 | 121.6782 | 5.0812 | 0.10529 | 0.51727 | 122.5433 | -0.30212 | -0.15106 | 0.17853 | 0.18768 | 0.39825 | -0.63171 | -0.11902 | 0.23346 | 0.33875 | 0.28839 | 0.70038 | 121.8613 | 122.6715 | 0.18768 | 122.7264 | 5.2643 | -0.11902 | 122.6715 | 0.18768 | 5.2643 | 121.8613 | 122.7264 | -122.644 | -122.612
1259.8594 | 122.3877 | -0.20142 | 122.3007 | 0.0103 | 0.017812 | 0.012192 | -0.0025293 | 0.062051 | -0.0046549 | 0.06997 | 0 | 122.4747 | -0.3479 | 0.1831 | 121.6415 | 5.0171 | -0.027466 | 0.38452 | 122.5204 | -0.32044 | -0.14648 | 0.17395 | 0.20142 | 0.38452 | -0.65918 | -0.11902 | 0.21973 | 0.3479 | 0.17395 | 0.58594 | 121.843 | 122.6761 | 0.20142 | 122.7219 | 5.2185 | -0.11902 | 122.6761 | 0.20142 | 5.2185 | 121.843 | 122.7219 | -122.6486 | -122.6212
1261.5469 | 122.4014 | -0.18768 | 122.3099 | -0.012589 | 0.015676 | 0.013473 | -0.0025293 | 0.061197 | -0.0061503 | 0.06762 | -0.013733 | 122.4655 | -0.3479 | 0.18768 | 121.637 | 5.0354 | -0.022888 | 0.39368 | 122.5342 | -0.28839 | -0.16022 | 0.15564 | 0.17395 | 0.37537 | -0.67291 | -0.10071 | 0.22431 | 0.33417 | 0.16479 | 0.58136 | 121.8246 | 122.6532 | 0.17395 | 122.7219 | 5.2231 | -0.10071 | 122.6532 | 0.17395 | 5.2231 | 121.8246 | 122.7219 | -122.6578 | -122.5983
1263.2344 | 122.374 | -0.1831 | 122.3282 | 0.0026703 | 0.016744 | 0.012192 | -0.0053063 | 0.062906 | -0.0059365 | 0.067834 | -0.022888 | 122.4518 | -0.36163 | 0.20142 | 121.669 | 5.0766 | 0.054932 | 0.47607 | 122.5388 | -0.31128 | -0.17853 | 0.1236 | 0.16022 | 0.38452 | -0.65918 | -0.12817 | 0.21057 | 0.33874 | 0.23804 | 0.65918 | 121.8521 | 122.6349 | 0.16022 | 122.7219 | 5.2597 | -0.12817 | 122.6349 | 0.16022 | 5.2597 | 121.8521 | 122.7219 | -122.6898 | -122.6395
1264.9844 | 122.3785 | -0.19684 | 122.287 | -0.0049592 | 0.014394 | 0.014328 | -0.0029565 | 0.063119 | -0.0067911 | 0.069329 | 0.009155 | 122.438 | -0.32959 | 0.21057 | 121.6507 | 5.0446 | -0.054932 | 0.39825 | 122.525 | -0.30212 | -0.13275 | 0.15106 | 0.20599 | 0.40741 | -0.63629 | -0.10529 | 0.23804 | 0.33875 | 0.14191 | 0.59509 | 121.8475 | 122.6349 | 0.20599 | 122.7219 | 5.2414 | -0.10529 | 122.6349 | 0.20599 | 5.2414 | 121.8475 | 122.7219 | -122.6166 | -122.5891
1266.6562 | 122.4747 | -0.13733 | 122.2961 | 0.0026703 | 0.01888 | 0.012405 | -0.0044519 | 0.06141 | -0.0042277 | 0.06762 | -0.073242 | 122.4976 | -0.37994 | 0.10529 | 121.5591 | 4.9942 | 0.28381 | 0.42114 | 122.5983 | -0.36163 | -0.24261 | 0.20142 | 0.064087 | 0.24262 | -0.737 | -0.2243 | 0.30212 | 0.3067 | 0.42114 | 0.55847 | 121.6965 | 122.6349 | 0.064087 | 122.7356 | 5.1315 | -0.2243 | 122.6349 | 0.064087 | 5.1315 | 121.6965 | 122.7356 | -122.6761 | -122.6578
1268.4062 | 122.5204 | -0.14648 | 122.2549 | 0.0026703 | 0.019948 | 0.014541 | 0.0019569 | 0.060769 | -0.0059365 | 0.069116 | -0.10071 | 122.4747 | -0.37994 | 0.068665 | 121.55 | 4.9255 | 0.17853 | 0.28381 | 122.5616 | -0.33875 | -0.23346 | 0.21973 | 0.045776 | 0.21515 | -0.70496 | -0.19226 | 0.3067 | 0.27924 | 0.32501 | 0.4303 | 121.6965 | 122.6212 | 0.045776 | 122.7081 | 5.072 | -0.19226 | 122.6212 | 0.045776 | 5.072 | 121.6965 | 122.7081 | -122.6349 | -122.5937
1270.1094 | 122.3785 | -0.19226 | 122.2916 | -0.0049592 | 0.017812 | 0.012192 | -0.0080835 | 0.061838 | -0.0055093 | 0.069543 | -0.022888 | 122.4701 | -0.34332 | 0.20142 | 121.6736 | 5.0903 | 0.059509 | 0.48981 | 122.5571 | -0.32959 | -0.15106 | 0.17853 | 0.16937 | 0.39368 | -0.61798 | -0.13733 | 0.2655 | 0.32043 | 0.25177 | 0.68207 | 121.8658 | 122.6624 | 0.16937 | 122.7493 | 5.2826 | -0.13733 | 122.6624 | 0.16937 | 5.2826 | 121.8658 | 122.7493 | -122.6349 | -122.6212
1271.8438 | 122.4609 | -0.17395 | 122.2916 | -0.0049592 | 0.016317 | 0.012405 | 0.0028113 | 0.061197 | -0.0078591 | 0.066766 | -0.041199 | 122.4747 | -0.37537 | 0.15564 | 121.582 | 5.0217 | 0.19684 | 0.41657 | 122.5891 | -0.31586 | -0.20142 | 0.1831 | 0.13275 | 0.32959 | -0.70953 | -0.14191 | 0.29755 | 0.33417 | 0.37079 | 0.59052 | 121.756 | 122.6486 | 0.13275 | 122.7631 | 5.1956 | -0.14191 | 122.6486 | 0.13275 | 5.1956 | 121.756 | 122.7631 | -122.6669 | -122.6074
1273.5312 | 122.5021 | -0.14648 | 122.2733 | 0.0103 | 0.018239 | 0.011551 | -0.00039312 | 0.062265 | -0.0048685 | 0.069543 | -0.10986 | 122.493 | -0.39368 | 0.09613 | 121.5546 | 4.953 | 0.14191 | 0.28381 | 122.5891 | -0.33875 | -0.24719 | 0.21973 | 0.036621 | 0.24261 | -0.71869 | -0.19226 | 0.31586 | 0.28381 | 0.28839 | 0.4303 | 121.701 | 122.6395 | 0.036621 | 122.7356 | 5.0995 | -0.19226 | 122.6395 | 0.036621 | 5.0995 | 121.701 | 122.7356 | -122.6669 | -122.612
1275.2188 | 122.5113 | -0.15106 | 122.2733 | 0.0103 | 0.01888 | 0.013046 | 0.0013159 | 0.063974 | -0.0061503 | 0.068475 | -0.09613 | 122.4976 | -0.38452 | 0.10529 | 121.5408 | 4.9576 | 0.20599 | 0.32501 | 122.6028 | -0.33417 | -0.23346 | 0.22431 | 0.054932 | 0.25635 | -0.73242 | -0.1831 | 0.32959 | 0.28839 | 0.35706 | 0.47607 | 121.6919 | 122.6486 | 0.054932 | 122.7539 | 5.1086 | -0.1831 | 122.6486 | 0.054932 | 5.1086 | 121.6919 | 122.7539 | -122.6578 | -122.6074
1276.9688 | 122.3785 | -0.19226 | 122.3145 | -0.0049592 | 0.017812 | 0.012619 | -0.0070153 | 0.062906 | -0.0048685 | 0.067834 | 0.022888 | 122.4655 | -0.3479 | 0.20142 | 121.6873 | 5.127 | 0.068665 | 0.50812 | 122.5342 | -0.3067 | -0.15564 | 0.15106 | 0.21515 | 0.39368 | -0.62714 | -0.11444 | 0.21973 | 0.37079 | 0.26093 | 0.70038 | 121.8796 | 122.6578 | 0.21515 | 122.7264 | 5.3192 | -0.11444 | 122.6578 | 0.21515 | 5.3192 | 121.8796 | 122.7264 | -122.6624 | -122.6212
1278.7188 | 122.3785 | -0.19684 | 122.2961 | -0.0049592 | 0.016317 | 0.010483 | -0.0046655 | 0.061838 | -0.0067911 | 0.06762 | 0.004578 | 122.4701 | -0.33875 | 0.21973 | 121.6965 | 5.1086 | 0.086975 | 0.52643 | 122.5388 | -0.29755 | -0.14191 | 0.17395 | 0.20142 | 0.41657 | -0.59967 | -0.10071 | 0.24261 | 0.34332 | 0.28381 | 0.72327 | 121.8933 | 122.6669 | 0.20142 | 122.7356 | 5.3055 | -0.10071 | 122.6669 | 0.20142 | 5.3055 | 121.8933 | 122.7356 | -122.6349 | -122.5937
1280.4219 | 122.3923 | -0.17853 | 122.3007 | -0.0049592 | 0.015248 | 0.010483 | -0.0061609 | 0.061197 | -0.0055093 | 0.066766 | -0.045776 | 122.4426 | -0.3479 | 0.20142 | 121.6553 | 5.0858 | 0.064087 | 0.4715 | 122.5571 | -0.29297 | -0.16937 | 0.14191 | 0.13275 | 0.37994 | -0.64545 | -0.11444 | 0.25635 | 0.30212 | 0.24261 | 0.65002 | 121.8338 | 122.6212 | 0.13275 | 122.7356 | 5.2643 | -0.11444 | 122.6212 | 0.13275 | 5.2643 | 121.8338 | 122.7356 | -122.6486 | -122.5937
1282.1094 | 122.374 | -0.19226 | 122.319 | 0.0026703 | 0.016957 | 0.014328 | -0.0053063 | 0.06141 | -0.0063639 | 0.066766 | 0.004578 | 122.4792 | -0.34332 | 0.20599 | 121.669 | 5.1178 | 0.10529 | 0.53101 | 122.5754 | -0.32959 | -0.15106 | 0.16022 | 0.19684 | 0.39826 | -0.65002 | -0.13733 | 0.25635 | 0.3479 | 0.29755 | 0.72327 | 121.8613 | 122.6715 | 0.19684 | 122.7676 | 5.3101 | -0.13733 | 122.6715 | 0.19684 | 5.3101 | 121.8613 | 122.7676 | -122.6624 | -122.6486
1283.8594 | 122.4472 | -0.16022 | 122.3053 | 0.0026703 | 0.018666 | 0.013901 | 0.00067508 | 0.063974 | -0.0093545 | 0.067834 | -0.036621 | 122.4838 | -0.38452 | 0.16022 | 121.5958 | 5.0491 | 0.17853 | 0.4303 | 122.612 | -0.32959 | -0.2243 | 0.17853 | 0.1236 | 0.32043 | -0.70953 | -0.16937 | 0.3067 | 0.3479 | 0.33874 | 0.59052 | 121.756 | 122.644 | 0.1236 | 122.7722 | 5.2094 | -0.16937 | 122.644 | 0.1236 | 5.2094 | 121.756 | 122.7722 | -122.6898 | -122.6349
1285.625 | 122.4152 | -0.16479 | 122.3373 | -0.012589 | 0.01418 | 0.011978 | -0.00082032 | 0.06376 | -0.0072183 | 0.071466 | -0.041199 | 122.4518 | -0.36621 | 0.19226 | 121.6415 | 5.0583 | 0 | 0.37994 | 122.5891 | -0.29297 | -0.20142 | 0.11444 | 0.1236 | 0.35706 | -0.6958 | -0.12817 | 0.25177 | 0.32501 | 0.16479 | 0.54474 | 121.8063 | 122.6166 | 0.1236 | 122.7539 | 5.2231 | -0.12817 | 122.6166 | 0.1236 | 5.2231 | 121.8063 | 122.7539 | -122.7036 | -122.6303
1287.3594 | 122.3877 | -0.19226 | 122.3099 | -0.0049592 | 0.016317 | 0.012192 | -0.0055199 | 0.060556 | -0.0059365 | 0.068048 | 0.013733 | 122.4838 | -0.33875 | 0.21515 | 121.6782 | 5.1407 | 0.11902 | 0.51727 | 122.5433 | -0.31586 | -0.14648 | 0.17395 | 0.20599 | 0.40741 | -0.63171 | -0.1236 | 0.23346 | 0.35248 | 0.31128 | 0.70953 | 121.8704 | 122.6761 | 0.20599 | 122.7356 | 5.3329 | -0.1236 | 122.6761 | 0.20599 | 5.3329 | 121.8704 | 122.7356 | -122.6486 | -122.6257
1289.1094 | 122.5204 | -0.13733 | 122.2916 | 0.0026703 | 0.015889 | 0.0089871 | -0.0016747 | 0.062692 | -0.0050821 | 0.069116 | -0.12817 | 122.4747 | -0.39825 | 0.09613 | 121.5591 | 5.04 | 0.32959 | 0.40741 | 122.6257 | -0.33417 | -0.26092 | 0.1831 | 0.009155 | 0.23346 | -0.73242 | -0.19684 | 0.33417 | 0.27008 | 0.46692 | 0.54474 | 121.6965 | 122.612 | 0.009155 | 122.7631 | 5.1773 | -0.19684 | 122.612 | 0.009155 | 5.1773 | 121.6965 | 122.7631 | -122.6898 | -122.6257
1290.875 | 122.4655 | -0.16937 | 122.2961 | -0.0049592 | 0.020375 | 0.011337 | -0.0027429 | 0.06141 | -0.0074319 | 0.070184 | -0.041199 | 122.493 | -0.37994 | 0.16937 | 121.6187 | 5.0766 | 0.20599 | 0.46692 | 122.6074 | -0.32501 | -0.21057 | 0.19684 | 0.12817 | 0.33875 | -0.67749 | -0.15564 | 0.31128 | 0.33875 | 0.37537 | 0.63629 | 121.788 | 122.6624 | 0.12817 | 122.7768 | 5.246 | -0.15564 | 122.6624 | 0.12817 | 5.246 | 121.788 | 122.7768 | -122.6761 | -122.6212
1292.6406 | 122.493 | -0.15564 | 122.2778 | 0.017929 | 0.016957 | 0.013687 | 0.00024788 | 0.063119 | -0.0067911 | 0.068475 | -0.082397 | 122.4792 | -0.36621 | 0.11902 | 121.582 | 5.0171 | 0.21057 | 0.34332 | 122.5937 | -0.33875 | -0.21057 | 0.20142 | 0.073243 | 0.27466 | -0.6958 | -0.18311 | 0.31586 | 0.28381 | 0.36621 | 0.49896 | 121.7377 | 122.6349 | 0.073243 | 122.7493 | 5.1727 | -0.18311 | 122.6349 | 0.073243 | 5.1727 | 121.7377 | 122.7493 | -122.644 | -122.6166
1294.3281 | 122.5113 | -0.14648 | 122.2824 | 0.0026703 | 0.018666 | 0.013901 | -0.0010339 | 0.065042 | -0.0057229 | 0.069329 | -0.091553 | 122.4838 | -0.36163 | 0.091553 | 121.5454 | 5.0079 | 0.2243 | 0.32501 | 122.612 | -0.32044 | -0.21515 | 0.20142 | 0.054931 | 0.23804 | -0.737 | -0.17395 | 0.32959 | 0.27008 | 0.37079 | 0.4715 | 121.6919 | 122.6303 | 0.054931 | 122.7585 | 5.1544 | -0.17395 | 122.6303 | 0.054931 | 5.1544 | 121.6919 | 122.7585 | -122.644 | -122.6028
1296.0938 | 122.4014 | -0.17853 | 122.3007 | -0.0049592 | 0.018239 | 0.015182 | -0.0016747 | 0.063547 | -0.0076455 | 0.069543 | -0.004578 | 122.4838 | -0.33875 | 0.19684 | 121.6736 | 5.1132 | -0.013733 | 0.3891 | 122.525 | -0.29755 | -0.16022 | 0.18311 | 0.17395 | 0.37537 | -0.62714 | -0.11902 | 0.2243 | 0.33417 | 0.16479 | 0.56763 | 121.8521 | 122.6624 | 0.17395 | 122.7036 | 5.2917 | -0.11902 | 122.6624 | 0.17395 | 5.2917 | 121.8521 | 122.7036 | -122.6395 | -122.5983
1297.8438 | 122.4747 | -0.16937 | 122.3099 | -0.012589 | 0.020162 | 0.010055 | -0.0035973 | 0.06611 | -0.0050821 | 0.069757 | -0.036621 | 122.4838 | -0.38452 | 0.15564 | 121.6141 | 5.0949 | 0.21515 | 0.44861 | 122.5937 | -0.32501 | -0.21515 | 0.17395 | 0.13275 | 0.32501 | -0.6958 | -0.15564 | 0.28381 | 0.3479 | 0.38452 | 0.61798 | 121.7834 | 122.6532 | 0.13275 | 122.7631 | 5.2643 | -0.15564 | 122.6532 | 0.13275 | 5.2643 | 121.7834 | 122.7631 | -122.6944 | -122.6349
1299.6094 | 122.3557 | -0.1831 | 122.3419 | 0.0026703 | 0.018453 | 0.0087735 | -0.0082971 | 0.061197 | -0.0074319 | 0.068261 | 0.018311 | 122.4792 | -0.3067 | 0.21057 | 121.7102 | 5.1727 | 0.091553 | 0.52185 | 122.5479 | -0.3067 | -0.1236 | 0.13733 | 0.20142 | 0.39368 | -0.63171 | -0.1236 | 0.20599 | 0.32501 | 0.27466 | 0.70496 | 121.8933 | 122.6624 | 0.20142 | 122.731 | 5.3558 | -0.1236 | 122.6624 | 0.20142 | 5.3558 | 121.8933 | 122.731 | -122.6486 | -122.6486
1301.3594 | 122.3877 | -0.19684 | 122.3282 | -0.0049592 | 0.016103 | 0.015823 | -0.0057337 | 0.062265 | -0.0046549 | 0.06997 | 0.004578 | 122.493 | -0.34332 | 0.21057 | 121.669 | 5.1361 | -0.027466 | 0.39825 | 122.5479 | -0.28839 | -0.14648 | 0.16479 | 0.20142 | 0.40741 | -0.65918 | -0.091553 | 0.21973 | 0.3479 | 0.16937 | 0.59509 | 121.8658 | 122.6898 | 0.20142 | 122.7448 | 5.3329 | -0.091553 | 122.6898 | 0.20142 | 5.3329 | 121.8658 | 122.7448 | -122.6715 | -122.6166
1303.0469 | 122.5021 | -0.14191 | 122.2916 | -0.0049592 | 0.017598 | 0.0094143 | -0.0016747 | 0.061624 | -0.0048685 | 0.068902 | -0.10529 | 122.4747 | -0.3891 | 0.10071 | 121.5729 | 5.0674 | 0.30212 | 0.42114 | 122.6257 | -0.33875 | -0.24719 | 0.1831 | 0.036621 | 0.24262 | -0.71869 | -0.19684 | 0.33417 | 0.28381 | 0.44403 | 0.56305 | 121.7148 | 122.6166 | 0.036621 | 122.7676 | 5.2094 | -0.19684 | 122.6166 | 0.036621 | 5.2094 | 121.7148 | 122.7676 | -122.6807 | -122.6303
1304.7969 | 122.406 | -0.19226 | 122.3099 | -0.0049592 | 0.01653 | 0.012619 | -0.0072289 | 0.061197 | -0.0048685 | 0.06762 | -0.018311 | 122.4838 | -0.34332 | 0.16479 | 121.6324 | 5.0949 | 0.009155 | 0.37537 | 122.5616 | -0.31128 | -0.15106 | 0.17395 | 0.17395 | 0.35706 | -0.67749 | -0.11902 | 0.25177 | 0.32501 | 0.20142 | 0.56763 | 121.8246 | 122.6761 | 0.17395 | 122.7539 | 5.2872 | -0.11902 | 122.6761 | 0.17395 | 5.2872 | 121.8246 | 122.7539 | -122.6532 | -122.6212
1306.4844 | 122.4655 | -0.16479 | 122.2824 | -0.0049592 | 0.019307 | 0.015396 | -0.0023157 | 0.062692 | -0.0040139 | 0.066766 | -0.045776 | 122.493 | -0.37079 | 0.11444 | 121.5729 | 5.1041 | 0.27008 | 0.44403 | 122.6074 | -0.3479 | -0.20599 | 0.21057 | 0.11902 | 0.27924 | -0.70953 | -0.1831 | 0.32501 | 0.32501 | 0.43488 | 0.60883 | 121.7377 | 122.6578 | 0.11902 | 122.7722 | 5.2689 | -0.1831 | 122.6578 | 0.11902 | 5.2689 | 121.7377 | 122.7722 | -122.6532 | -122.6303
1308.2344 | 122.4655 | -0.15564 | 122.2961 | -0.012589 | 0.016103 | 0.011337 | 0.0013159 | 0.062692 | -0.0085001 | 0.069116 | -0.050354 | 122.4747 | -0.37994 | 0.16479 | 121.6003 | 5.1178 | 0.20599 | 0.44403 | 122.612 | -0.31586 | -0.2243 | 0.17853 | 0.10529 | 0.32044 | -0.6958 | -0.16022 | 0.31586 | 0.32959 | 0.36163 | 0.59967 | 121.756 | 122.6303 | 0.10529 | 122.7676 | 5.2734 | -0.16022 | 122.6303 | 0.10529 | 5.2734 | 121.756 | 122.7676 | -122.6761 | -122.612
1310 | 122.5204 | -0.15106 | 122.2549 | -0.020218 | 0.015676 | 0.011764 | -0.0057337 | 0.062478 | -0.0057229 | 0.068475 | -0.10986 | 122.5067 | -0.37994 | 0.07782 | 121.5683 | 5.0674 | 0.32959 | 0.42114 | 122.58 | -0.32959 | -0.22888 | 0.25177 | 0.041199 | 0.22888 | -0.68665 | -0.17853 | 0.32501 | 0.27008 | 0.48065 | 0.5722 | 121.7194 | 122.6578 | 0.041199 | 122.731 | 5.2185 | -0.17853 | 122.6578 | 0.041199 | 5.2185 | 121.7194 | 122.731 | -122.6349 | -122.5845
1311.6875 | 122.4564 | -0.15564 | 122.287 | 0.0026703 | 0.019521 | 0.012192 | -0.0044519 | 0.06141 | -0.0055093 | 0.068902 | -0.050354 | 122.4976 | -0.35248 | 0.13733 | 121.6003 | 5.1132 | 0.27466 | 0.45319 | 122.5754 | -0.36163 | -0.19684 | 0.21057 | 0.10529 | 0.29297 | -0.68664 | -0.20599 | 0.28839 | 0.30212 | 0.4303 | 0.60883 | 121.756 | 122.6532 | 0.10529 | 122.731 | 5.2689 | -0.20599 | 122.6532 | 0.10529 | 5.2689 | 121.756 | 122.731 | -122.6395 | -122.6486
1313.4219 | 122.4976 | -0.13733 | 122.2733 | -0.0049592 | 0.017171 | 0.0085599 | -0.0018885 | 0.061197 | -0.0070047 | 0.069757 | -0.082397 | 122.5342 | -0.39825 | 0.10529 | 121.5637 | 5.0949 | 0.30212 | 0.4303 | 122.6257 | -0.32959 | -0.26092 | 0.26093 | 0.054932 | 0.24262 | -0.70953 | -0.19226 | 0.35248 | 0.31586 | 0.43945 | 0.56763 | 121.701 | 122.6715 | 0.054932 | 122.7631 | 5.2322 | -0.19226 | 122.6715 | 0.054932 | 5.2322 | 121.701 | 122.7631 | -122.6715 | -122.6028
1315.1094 | 122.3831 | -0.21057 | 122.3328 | 0.0026703 | 0.013753 | 0.010269 | -0.0025293 | 0.062906 | -0.0067911 | 0.069116 | 0 | 122.4655 | -0.33875 | 0.19226 | 121.6644 | 5.1727 | -0.027466 | 0.40741 | 122.5571 | -0.28839 | -0.12817 | 0.13275 | 0.21057 | 0.40283 | -0.66833 | -0.07782 | 0.2243 | 0.33875 | 0.18311 | 0.61798 | 121.875 | 122.6761 | 0.21057 | 122.7676 | 5.3833 | -0.07782 | 122.6761 | 0.21057 | 5.3833 | 121.875 | 122.7676 | -122.6715 | -122.6212
1316.8594 | 122.5067 | -0.17395 | 122.3007 | 0.0103 | 0.017385 | 0.013046 | -0.0014611 | 0.065469 | -0.0067911 | 0.069329 | -0.086975 | 122.493 | -0.3891 | 0.09613 | 121.5408 | 5.0812 | 0.21057 | 0.35248 | 122.6212 | -0.32044 | -0.21515 | 0.19226 | 0.086975 | 0.27008 | -0.75989 | -0.14649 | 0.32044 | 0.30212 | 0.38452 | 0.52643 | 121.7148 | 122.6669 | 0.086975 | 122.7951 | 5.2551 | -0.14649 | 122.6669 | 0.086975 | 5.2551 | 121.7148 | 122.7951 | -122.6898 | -122.6212
1318.6094 | 122.4243 | -0.17853 | 122.2916 | -0.0049592 | 0.018239 | 0.0092007 | -0.0070153 | 0.06141 | -0.0038003 | 0.068261 | -0.054932 | 122.5113 | -0.35248 | 0.13733 | 121.6232 | 5.1407 | 0.064087 | 0.37537 | 122.5616 | -0.32044 | -0.17395 | 0.21973 | 0.1236 | 0.31586 | -0.66833 | -0.14191 | 0.27008 | 0.29755 | 0.24261 | 0.55389 | 121.8018 | 122.6898 | 0.1236 | 122.7402 | 5.3192 | -0.14191 | 122.6898 | 0.1236 | 5.3192 | 121.8018 | 122.7402 | -122.644 | -122.612
1320.375 | 122.5525 | -0.16022 | 122.2778 | 0.0026703 | 0.018666 | 0.013473 | -0.0012475 | 0.062906 | -0.0065775 | 0.067407 | -0.12817 | 122.5204 | -0.3891 | 0.09613 | 121.5088 | 5.04 | 0.19684 | 0.31128 | 122.5983 | -0.34332 | -0.22888 | 0.24262 | 0.032043 | 0.25635 | -0.76904 | -0.18311 | 0.32044 | 0.26092 | 0.35706 | 0.4715 | 121.669 | 122.6807 | 0.032043 | 122.7585 | 5.2002 | -0.18311 | 122.6807 | 0.032043 | 5.2002 | 121.669 | 122.7585 | -122.6669 | -122.6212
1322.125 | 122.438 | -0.14191 | 122.2961 | -0.0049592 | 0.01888 | 0.010055 | -0.0048791 | 0.06376 | -0.0063639 | 0.067834 | -0.027466 | 122.5067 | -0.34332 | 0.14648 | 121.6141 | 5.159 | 0.23804 | 0.48065 | 122.6166 | -0.32044 | -0.20142 | 0.21057 | 0.11444 | 0.28839 | -0.68207 | -0.17853 | 0.32043 | 0.31586 | 0.37994 | 0.62256 | 121.756 | 122.6486 | 0.11444 | 122.7585 | 5.3009 | -0.17853 | 122.6486 | 0.11444 | 5.3009 | 121.756 | 122.7585 | -122.6395 | -122.6166
1323.875 | 122.3923 | -0.18768 | 122.3373 | -0.0049592 | 0.017598 | 0.014541 | -0.0025293 | 0.062692 | -0.0050821 | 0.068688 | 0.013733 | 122.4609 | -0.32044 | 0.20599 | 121.6415 | 5.1865 | -0.050354 | 0.41199 | 122.58 | -0.27924 | -0.13275 | 0.1236 | 0.20142 | 0.39368 | -0.6958 | -0.091553 | 0.24262 | 0.33417 | 0.13733 | 0.59967 | 121.8292 | 122.6486 | 0.20142 | 122.7676 | 5.3741 | -0.091553 | 122.6486 | 0.20142 | 5.3741 | 121.8292 | 122.7676 | -122.6578 | -122.6166
1325.6406 | 122.4838 | -0.14191 | 122.3053 | 0.0026703 | 0.019307 | 0.013473 | -0.0038111 | 0.060342 | -0.0052957 | 0.071466 | -0.082397 | 122.5113 | -0.37537 | 0.11444 | 121.5637 | 5.1224 | 0.29297 | 0.4303 | 122.5845 | -0.3479 | -0.23346 | 0.20599 | 0.05951 | 0.25635 | -0.74158 | -0.20599 | 0.27924 | 0.29297 | 0.43488 | 0.57221 | 121.7056 | 122.6532 | 0.05951 | 122.7264 | 5.2643 | -0.20599 | 122.6532 | 0.05951 | 5.2643 | 121.7056 | 122.7264 | -122.6807 | -122.6532
1327.375 | 122.5159 | -0.14648 | 122.2778 | 0.0103 | 0.020162 | 0.01561 | -0.0021021 | 0.061838 | -0.0057229 | 0.068902 | -0.10529 | 122.5342 | -0.40283 | 0.10071 | 121.5408 | 5.127 | 0.32044 | 0.42572 | 122.6028 | -0.33875 | -0.25635 | 0.25635 | 0.041198 | 0.24719 | -0.737 | -0.19226 | 0.32501 | 0.29755 | 0.46692 | 0.5722 | 121.6873 | 122.6807 | 0.041198 | 122.7493 | 5.2734 | -0.19226 | 122.6807 | 0.041198 | 5.2734 | 121.6873 | 122.7493 | -122.6807 | -122.6166
1329.0625 | 122.5296 | -0.13733 | 122.2778 | -0.0049592 | 0.017812 | 0.015182 | -0.0010339 | 0.062906 | -0.0052957 | 0.071252 | -0.11444 | 122.5159 | -0.37537 | 0.07782 | 121.5179 | 5.0766 | 0.23346 | 0.33417 | 122.5845 | -0.32501 | -0.23804 | 0.23804 | 0.022888 | 0.21515 | -0.75989 | -0.18768 | 0.3067 | 0.26092 | 0.37079 | 0.4715 | 121.6553 | 122.6532 | 0.022888 | 122.7219 | 5.2139 | -0.18768 | 122.6532 | 0.022888 | 5.2139 | 121.6553 | 122.7219 | -122.6532 | -122.6028
1330.8281 | 122.4426 | -0.15564 | 122.3282 | -0.012589 | 0.017598 | 0.0098417 | -0.0065881 | 0.061197 | -0.0040139 | 0.067407 | -0.068665 | 122.5204 | -0.35706 | 0.15106 | 121.6187 | 5.191 | 0.07782 | 0.4303 | 122.5616 | -0.31586 | -0.20142 | 0.19226 | 0.086975 | 0.3067 | -0.70953 | -0.16022 | 0.23346 | 0.28839 | 0.23346 | 0.58594 | 121.7743 | 122.6761 | 0.086975 | 122.7173 | 5.3467 | -0.16022 | 122.6761 | 0.086975 | 5.3467 | 121.7743 | 122.7173 | -122.6852 | -122.644
1332.5156 | 122.3785 | -0.19226 | 122.3419 | -0.0049592 | 0.015248 | 0.01326 | -0.0044519 | 0.063547 | -0.0072183 | 0.070184 | -0.004578 | 122.4655 | -0.34332 | 0.20599 | 121.6415 | 5.1956 | -0.018311 | 0.41657 | 122.5616 | -0.26093 | -0.15106 | 0.1236 | 0.18768 | 0.39826 | -0.70038 | -0.068664 | 0.21973 | 0.33874 | 0.17395 | 0.60883 | 121.8338 | 122.6578 | 0.18768 | 122.7539 | 5.3879 | -0.068664 | 122.6578 | 0.18768 | 5.3879 | 121.8338 | 122.7539 | -122.6852 | -122.6028
1334.2656 | 122.3923 | -0.16937 | 122.3465 | 0.0026703 | 0.016317 | 0.012619 | -0.0048791 | 0.062692 | -0.0055093 | 0.068688 | -0.022888 | 122.4976 | -0.32959 | 0.21057 | 121.6507 | 5.2505 | 0.073242 | 0.48065 | 122.5433 | -0.30212 | -0.16022 | 0.15106 | 0.14649 | 0.37994 | -0.6958 | -0.13275 | 0.19684 | 0.3067 | 0.24261 | 0.65003 | 121.8201 | 122.6669 | 0.14649 | 122.7127 | 5.4199 | -0.13275 | 122.6669 | 0.14649 | 5.4199 | 121.8201 | 122.7127 | -122.6761 | -122.6486
1336.0156 | 122.4243 | -0.19226 | 122.319 | 0.0026703 | 0.016957 | 0.0098417 | -0.0053063 | 0.059274 | -0.0029459 | 0.067834 | -0.036621 | 122.5021 | -0.33417 | 0.16479 | 121.6003 | 5.1682 | 0.036621 | 0.37994 | 122.5662 | -0.29297 | -0.14191 | 0.1831 | 0.15564 | 0.35706 | -0.71869 | -0.10071 | 0.24719 | 0.29755 | 0.22888 | 0.5722 | 121.7926 | 122.6944 | 0.15564 | 122.7585 | 5.3604 | -0.10071 | 122.6944 | 0.15564 | 5.3604 | 121.7926 | 122.7585 | -122.6532 | -122.612
1337.7031 | 122.406 | -0.1831 | 122.3511 | -0.0049592 | 0.01653 | 0.014969 | 3.4284e-05 | 0.062906 | -0.0031595 | 0.066552 | 0.018311 | 122.4976 | -0.34332 | 0.21973 | 121.6187 | 5.2094 | -0.018311 | 0.41199 | 122.5525 | -0.28839 | -0.16022 | 0.14648 | 0.20142 | 0.40283 | -0.73242 | -0.10529 | 0.20142 | 0.36163 | 0.16479 | 0.59509 | 121.8018 | 122.6807 | 0.20142 | 122.7356 | 5.3925 | -0.10529 | 122.6807 | 0.20142 | 5.3925 | 121.8018 | 122.7356 | -122.6944 | -122.6395
1339.4375 | 117.7597 | -92.363 | 25.2365 | -0.012589 | 0.01653 | 0.010696 | 6.9377 | 0.0013821 | -0.0038003 | 7.0221 | -92.3355 | 25.2914 | -92.6422 | 0.31128 | 18.3289 | -1.3962 | -0.29755 | 0.10529 | 17.4912 | -84.906 | -0.27924 | 0.054932 | 0.027466 | 92.6743 | -6.9077 | 7.457 | -7.7454 | 0.3067 | 92.0654 | 92.4683 | 110.6918 | 117.6544 | 0.027466 | 109.8541 | 90.9668 | 7.457 | 117.6544 | 0.027466 | 90.9668 | 110.6918 | 109.8541 | -117.8787 | -110.1425
1341.1875 | 117.2836 | -92.0242 | 25.0305 | -0.0049592 | 0.012899 | 0.0098417 | 6.9377 | 0.0048001 | -0.0067911 | 7.0221 | -92.0471 | 25.1129 | -92.3538 | 0.21515 | 18.1412 | -1.236 | -0.073242 | 0.09613 | 17.4225 | -84.5764 | -0.32959 | 0.082397 | -0.022888 | 92.2394 | -6.8893 | 7.4478 | -7.608 | 0.3067 | 91.951 | 92.1204 | 110.1654 | 117.1371 | -0.022888 | 109.4467 | 90.7883 | 7.4478 | 117.1371 | -0.022888 | 90.7883 | 110.1654 | 109.4467 | -117.3843 | -109.6069
1342.875 | 116.7892 | -91.7358 | 24.9481 | -0.012589 | 0.017812 | 0.013901 | 6.9377 | 0.0020229 | -0.0078591 | 7.0221 | -91.6672 | 24.9847 | -91.9647 | 0.27008 | 18.1366 | -1.0666 | -0.1831 | 0.16022 | 17.3355 | -84.3567 | -0.22888 | 0.036621 | 0.068665 | 92.0059 | -6.8115 | 7.3792 | -7.6126 | 0.29755 | 91.5527 | 91.8961 | 109.8724 | 116.7206 | 0.068665 | 109.0713 | 90.6693 | 7.3792 | 116.7206 | 0.068665 | 90.6693 | 109.8724 | 109.0713 | -116.9128 | -109.3048
1344.625 | 116.5009 | -91.4886 | 24.852 | 0.0026703 | 0.017812 | 0.017959 | 6.9377 | 0.0043729 | -0.0063639 | 7.0221 | -91.4474 | 24.9298 | -91.713 | 0.24719 | 18.0634 | -1.0849 | -0.3067 | 0.036621 | 17.276 | -84.1415 | -0.22431 | 0.07782 | 0.041198 | 91.7358 | -6.7886 | 7.3471 | -7.576 | 0.2655 | 91.1819 | 91.5253 | 109.552 | 116.4185 | 0.041198 | 108.7646 | 90.4037 | 7.3471 | 116.4185 | 0.041198 | 90.4037 | 109.552 | 108.7646 | -116.5649 | -108.9935
1346.375 | 116.2949 | -91.2872 | 24.7513 | -0.0049592 | 0.01653 | 0.017319 | 6.9377 | 0.0043729 | -0.0076455 | 7.0221 | -91.3422 | 24.8611 | -91.571 | 0.15564 | 17.9626 | -1.1307 | -0.009155 | 0.045776 | 17.2714 | -83.9859 | -0.28381 | 0.10986 | -0.054932 | 91.4429 | -6.7886 | 7.3013 | -7.4799 | 0.22888 | 91.2781 | 91.333 | 109.2499 | 116.1484 | -0.054932 | 108.5587 | 90.1566 | 7.3013 | 116.1484 | -0.054932 | 90.1566 | 109.2499 | 108.5587 | -116.3223 | -108.7372
1348.0625 | 116.0706 | -91.1179 | 24.7055 | -0.0049592 | 0.016957 | 0.012192 | 6.9377 | 0.0026639 | -0.0080729 | 7.0221 | -91.1499 | 24.8108 | -91.4108 | 0.21973 | 17.9672 | -1.0941 | -0.054932 | 0.064087 | 17.2302 | -83.8715 | -0.29297 | 0.10529 | -0.032043 | 91.3376 | -6.7383 | 7.2464 | -7.4753 | 0.26093 | 91.0629 | 91.1819 | 109.0851 | 115.9286 | -0.032043 | 108.3481 | 90.0238 | 7.2464 | 115.9286 | -0.032043 | 90.0238 | 109.0851 | 108.3481 | -116.1163 | -108.577
1349.7969 | 115.8875 | -91.0309 | 24.6506 | 0.0103 | 0.01653 | 0.01326 | 6.9377 | 0.0050137 | -0.0085001 | 7.0221 | -91.0263 | 24.7467 | -91.3055 | 0.20142 | 17.9489 | -1.0941 | -0.086975 | 0.045776 | 17.2165 | -83.7616 | -0.27466 | 0.09613 | 0.004578 | 91.2323 | -6.7017 | 7.2693 | -7.4341 | 0.27924 | 90.9439 | 91.0767 | 108.9798 | 115.7776 | 0.004578 | 108.2474 | 89.9368 | 7.2693 | 115.7776 | 0.004578 | 89.9368 | 108.9798 | 108.2474 | -115.9561 | -108.4122
1351.5469 | 115.7959 | -90.8844 | 24.5865 | -0.0049592 | 0.015462 | 0.015182 | 6.9377 | 0.0015957 | -0.0085001 | 7.0221 | -91.0217 | 24.6735 | -91.2003 | 0.11902 | 17.8619 | -1.181 | -0.1236 | -0.10529 | 17.1707 | -83.7112 | -0.31586 | 0.086975 | -0.13733 | 91.0034 | -6.7245 | 7.1732 | -7.4158 | 0.17853 | 90.7608 | 90.7791 | 108.7463 | 115.5579 | -0.13733 | 108.0551 | 89.7034 | 7.1732 | 115.5579 | -0.13733 | 89.7034 | 108.7463 | 108.0551 | -115.7867 | -108.2977
1353.2969 | 114.8621 | -29.4479 | 85.4691 | -0.012589 | 0.012471 | 0.01326 | 6.9377 | 0.0033047 | -0.0055093 | 7.0221 | -31.041 | 84.1187 | -30.8807 | 53.5309 | 75.4944 | 2.7832 | 1.3687 | 1.4328 | 74.6704 | -21.2723 | -1.4328 | -1.3504 | -1.593 | 82.9788 | -9.9747 | 8.1757 | -10.7986 | -0.16022 | 30.8166 | 30.8807 | 104.9423 | 113.5666 | -1.593 | 104.1183 | 32.2311 | 8.1757 | 113.5666 | -1.593 | 32.2311 | 104.9423 | 104.1183 | -116.3498 | -106.7413
1355 | 119.0094 | -0.16937 | 118.9087 | 0.0026703 | 0.015462 | 0.01091 | 0.0087927 | -0.0039585 | -0.0042277 | 0.042413 | -0.032043 | 119.0689 | -0.37079 | 119.0964 | 118.1625 | 5.0354 | 118.7027 | 0.9201 | 119.133 | -0.33417 | -0.20142 | 0.16022 | 0.13733 | 119.2657 | -0.74615 | -0.16479 | 0.22431 | 0.33875 | 118.8721 | 1.0895 | 118.3319 | 119.2383 | 0.13733 | 119.3024 | 5.2048 | -0.16479 | 119.2383 | 0.13733 | 5.2048 | 118.3319 | 119.3024 | -119.2795 | -119.2429
1356.75 | 115.7547 | -24.6185 | 91.301 | -0.0049592 | 0.010762 | 0.014328 | 6.9377 | 0.018899 | -0.0082865 | 7.0221 | -24.0097 | 92.0563 | -24.1928 | 37.0926 | 84.668 | 0.77362 | 36.319 | -0.79651 | 84.1782 | -16.8457 | 0.42572 | 0.75531 | 0.60882 | 61.7111 | -6.633 | 7.7728 | -7.1228 | 0.18311 | 60.9375 | 23.822 | 109.2865 | 116.6748 | 0.60882 | 108.7967 | 25.3922 | 7.7728 | 116.6748 | 0.60882 | 25.3922 | 109.2865 | 108.7967 | -115.4938 | -108.1467
1358.5 | 119.101 | -0.15564 | 118.9362 | 0.0026703 | 0.01653 | 0.011123 | 0.0017431 | 0.059701 | -0.0035867 | 0.091332 | -0.050354 | 119.1467 | -0.37994 | 7.37 | 118.1488 | 2.2339 | -0.11902 | 0.71411 | 119.22 | -0.32959 | -0.2243 | 0.21057 | 0.10529 | 7.5256 | -0.78735 | -0.17395 | 0.28381 | 0.32959 | 0.036621 | 0.86975 | 118.3044 | 119.3024 | 0.10529 | 119.3756 | 2.3895 | -0.17395 | 119.3024 | 0.10529 | 2.3895 | 118.3044 | 119.3756 | -119.3161 | -119.2657
1360.1875 | 119.2932 | -0.14191 | 119.0735 | 0.0026703 | 0.013967 | 0.012619 | 0.0030249 | 0.060769 | -0.0050821 | 0.1018 | -0.1236 | 119.2566 | -0.42114 | 2.6459 | 118.1625 | 2.7832 | -0.064087 | 0.59052 | 119.339 | -0.35248 | -0.27924 | 0.18311 | 0.018311 | 2.7878 | -0.91095 | -0.21057 | 0.2655 | 0.29755 | 0.07782 | 0.73242 | 118.3044 | 119.3985 | 0.018311 | 119.4809 | 2.9251 | -0.21057 | 119.3985 | 0.018311 | 2.9251 | 118.3044 | 119.4809 | -119.4946 | -119.426
1361.9375 | 119.3024 | -0.20142 | 119.1925 | 0.0026703 | 0.013967 | 0.0021511 | -0.0025293 | 0.059274 | -0.0040139 | 0.10052 | -0.050354 | 119.3161 | -0.35248 | 2.9572 | 118.1763 | 1.8906 | -0.19684 | 0.77362 | 119.4077 | -0.32501 | -0.15106 | 0.1236 | 0.15106 | 3.1586 | -1.0162 | -0.1236 | 0.21515 | 0.30212 | 0.004578 | 0.97504 | 118.3777 | 119.5175 | 0.15106 | 119.6091 | 2.092 | -0.1236 | 119.5175 | 0.15106 | 2.092 | 118.3777 | 119.6091 | -119.545 | -119.5175
1363.6875 | 116.2582 | -26.7105 | 89.209 | -0.088882 | 0.0094806 | 0.01091 | 6.9377 | 0.03428 | -0.0050821 | 7.0221 | -27.5711 | 88.8428 | -27.7542 | 2.2476 | 80.2094 | 0.4715 | 37.0148 | 0.09613 | 79.5914 | -19.5145 | -1.0437 | -0.36621 | -0.8606 | 28.9581 | -8.9996 | 7.196 | -9.6176 | 0.18311 | 63.7253 | 26.8066 | 106.9199 | 115.5533 | -0.8606 | 106.3019 | 27.182 | 7.196 | 115.5533 | -0.8606 | 27.182 | 106.9199 | 106.3019 | -116.9632 | -108.7234
1365.4219 | 119.3344 | -0.1831 | 119.2383 | 0.0026703 | 0.014821 | 0.0089871 | -0.0010339 | 0.060769 | -0.0023049 | 0.10223 | -0.059509 | 119.3619 | -0.35706 | 2.449 | 118.1213 | 2.4902 | -0.19226 | 0.64087 | 119.4305 | -0.32501 | -0.17395 | 0.1236 | 0.1236 | 2.6321 | -1.1169 | -0.14191 | 0.19226 | 0.29755 | -0.009156 | 0.82397 | 118.3044 | 119.545 | 0.1236 | 119.6136 | 2.6733 | -0.14191 | 119.545 | 0.1236 | 2.6733 | 118.3044 | 119.6136 | -119.5953 | -119.5633
1367.1094 | 119.4168 | -0.19226 | 119.3024 | -0.012589 | 0.014821 | 0.0079189 | 0.0036657 | 0.057779 | -0.0027323 | 0.10287 | -0.064087 | 119.4717 | -0.36621 | 3.1631 | 118.0984 | 2.2156 | -0.1831 | 0.64545 | 119.5496 | -0.32959 | -0.17395 | 0.16937 | 0.12817 | 3.3554 | -1.2039 | -0.13733 | 0.24719 | 0.30212 | 0.009156 | 0.83771 | 118.2907 | 119.664 | 0.12817 | 119.7418 | 2.4078 | -0.13733 | 119.664 | 0.12817 | 2.4078 | 118.2907 | 119.7418 | -119.6686 | -119.632
1368.8594 | 119.4946 | -0.17853 | 119.3665 | -0.0049592 | 0.013326 | 0.01091 | 0.0058021 | 0.058206 | -0.0025187 | 0.099023 | -0.064087 | 119.5358 | -0.36621 | 9.4482 | 117.7826 | 1.8997 | -0.17853 | 0.64087 | 119.6091 | -0.31128 | -0.18768 | 0.16937 | 0.11444 | 9.6268 | -1.5839 | -0.13275 | 0.24262 | 0.30212 | 0 | 0.8194 | 117.9611 | 119.7144 | 0.11444 | 119.7876 | 2.0782 | -0.13275 | 119.7144 | 0.11444 | 2.0782 | 117.9611 | 119.7876 | -119.7327 | -119.6777
1370.625 | 119.6091 | -0.16937 | 119.4214 | -0.012589 | 0.012899 | 0.0096279 | 0.0083655 | 0.057992 | 0.05516 | 0.1582 | -0.11444 | 119.5862 | -0.41657 | 8.5419 | 7.3608 | 1.5015 | -0.073242 | 0.58594 | 119.696 | -0.34332 | -0.24719 | 0.16479 | 0.054932 | 8.7112 | -112.0605 | -0.17395 | 0.27466 | 0.30212 | 0.096131 | 0.75531 | 7.5302 | 119.7556 | 0.054932 | 119.8654 | 1.6708 | -0.17395 | 119.7556 | 0.054932 | 1.6708 | 7.5302 | 119.8654 | -119.838 | -119.7647
1372.3281 | 119.6869 | -0.17853 | 119.4305 | -0.0049592 | 0.013112 | 0.0074917 | 0.0098609 | 0.057565 | 0.055587 | 0.1614 | -0.13275 | 119.6457 | -0.42572 | 8.2764 | 4.4586 | 1.6342 | -0.064087 | 0.61798 | 119.7418 | -0.37079 | -0.24719 | 0.21515 | 0.045777 | 8.4549 | -114.9719 | -0.19226 | 0.31128 | 0.29297 | 0.11444 | 0.79651 | 4.6371 | 119.8242 | 0.045777 | 119.9203 | 1.8127 | -0.19226 | 119.8242 | 0.045777 | 1.8127 | 4.6371 | 119.9203 | -119.8563 | -119.8013
1374.0156 | 119.7327 | -0.13733 | 119.4717 | 0.0026703 | 0.014608 | 0.0077053 | 0.0098609 | 0.055856 | 0.055801 | 0.16226 | -0.11902 | 119.7052 | -0.41657 | 9.0408 | 4.097 | 0.25635 | -0.054932 | 0.62256 | 119.7876 | -0.35248 | -0.27924 | 0.23346 | 0.01831 | 9.1782 | -115.3748 | -0.21515 | 0.31586 | 0.29755 | 0.082397 | 0.75989 | 4.2343 | 119.8425 | 0.01831 | 119.9249 | 0.39368 | -0.21515 | 119.8425 | 0.01831 | 0.39368 | 4.2343 | 119.9249 | -119.8883 | -119.8242
1375.7656 | 119.7784 | -0.17853 | 119.5358 | 0.0026703 | 0.015889 | 0.014328 | 0.010502 | 0.056497 | 0.058791 | 0.16396 | -0.11444 | 119.7464 | -0.41657 | 8.9676 | 3.8086 | 0.27008 | -0.086975 | 0.50812 | 119.8013 | -0.35248 | -0.23804 | 0.21057 | 0.064087 | 9.1461 | -115.7272 | -0.17395 | 0.2655 | 0.30212 | 0.091553 | 0.68665 | 3.9871 | 119.9249 | 0.064087 | 119.9799 | 0.44861 | -0.17395 | 119.9249 | 0.064087 | 0.44861 | 3.9871 | 119.9799 | -119.9524 | -119.8883
1377.5312 | 119.6869 | -0.21515 | 119.5953 | -0.0049592 | 0.012899 | 0.0085599 | 0.0058021 | 0.05842 | 0.060928 | 0.16247 | -0.027466 | 119.7281 | -0.36163 | 9.0958 | 3.9185 | 0.3891 | -0.23804 | 0.62714 | 119.8242 | -0.30212 | -0.14648 | 0.13275 | 0.18768 | 9.3109 | -115.6769 | -0.086975 | 0.22888 | 0.33417 | -0.022888 | 0.84229 | 4.1336 | 119.9432 | 0.18768 | 120.0394 | 0.60425 | -0.086975 | 119.9432 | 0.18768 | 0.60425 | 4.1336 | 120.0394 | -119.957 | -119.8975
1379.2188 | 119.8746 | -0.17853 | 119.632 | 0.0103 | 0.014394 | 0.0092007 | 0.0087927 | 0.05842 | 0.056441 | 0.1629 | -0.13275 | 119.8105 | -0.41657 | 8.2855 | 3.7857 | 0.25177 | -0.10986 | 0.5127 | 119.8975 | -0.35706 | -0.23804 | 0.17853 | 0.045777 | 8.4641 | -115.8463 | -0.17853 | 0.2655 | 0.28381 | 0.068665 | 0.69122 | 3.9642 | 119.989 | 0.045777 | 120.076 | 0.4303 | -0.17853 | 119.989 | 0.045777 | 0.4303 | 3.9642 | 120.076 | -120.0485 | -119.989
1380.9688 | 119.8791 | -0.1831 | 119.6777 | 0.0103 | 0.021657 | 0.0087735 | 0.01157 | 0.05906 | 0.059432 | 0.16268 | -0.045776 | 119.9341 | -0.39825 | 8.0933 | 3.8132 | 0.69122 | -0.11444 | 0.62714 | 119.9341 | -0.35706 | -0.21515 | 0.25635 | 0.13733 | 8.2764 | -115.8646 | -0.17395 | 0.25635 | 0.35248 | 0.068664 | 0.81024 | 3.9963 | 120.1172 | 0.13733 | 120.1172 | 0.87433 | -0.17395 | 120.1172 | 0.13733 | 0.87433 | 3.9963 | 120.1172 | -120.076 | -120.0348
1382.7344 | 119.8746 | -0.17395 | 119.7189 | -0.0049592 | 0.013967 | 0.0030057 | 0.0017431 | 0.056497 | 0.060073 | 0.16439 | -0.086975 | 119.9249 | -0.3891 | 8.3496 | 3.9597 | 0.2243 | -0.19684 | 0.17853 | 119.9387 | -0.34332 | -0.21515 | 0.20599 | 0.086975 | 8.5236 | -115.7593 | -0.16937 | 0.21973 | 0.30212 | -0.022888 | 0.35248 | 4.1336 | 120.0989 | 0.086975 | 120.1126 | 0.39825 | -0.16937 | 120.0989 | 0.086975 | 0.39825 | 4.1336 | 120.1126 | -120.108 | -120.0623
1384.4219 | 119.8608 | -0.2243 | 119.7601 | -0.0049592 | 0.015248 | 0.0083463 | 0.0062293 | 0.058206 | 0.060928 | 0.16418 | -0.036621 | 119.9249 | -0.35248 | 8.139 | 3.9825 | 0.2655 | -0.2655 | 0.20142 | 119.9799 | -0.31586 | -0.12817 | 0.16479 | 0.18768 | 8.3633 | -115.7776 | -0.091553 | 0.21973 | 0.31586 | -0.041199 | 0.42572 | 4.2068 | 120.1492 | 0.18768 | 120.2042 | 0.48981 | -0.091553 | 120.1492 | 0.18768 | 0.48981 | 4.2068 | 120.2042 | -120.1126 | -120.076
1386.125 | 119.9936 | -0.18768 | 119.783 | 0.0026703 | 0.013753 | 0.0079189 | 0.0075111 | 0.056283 | 0.057937 | 0.16482 | -0.11902 | 119.9524 | -0.39368 | 8.5831 | 3.891 | 0.15106 | -0.064087 | 0.11902 | 120.0714 | -0.36163 | -0.20599 | 0.16937 | 0.068664 | 8.7708 | -115.892 | -0.17395 | 0.28839 | 0.27466 | 0.1236 | 0.3067 | 4.0787 | 120.1401 | 0.068664 | 120.2591 | 0.33874 | -0.17395 | 120.1401 | 0.068664 | 0.33874 | 4.0787 | 120.2591 | -120.1767 | -120.1447
1387.875 | 119.9249 | -0.2243 | 119.8608 | 0.0026703 | 0.016317 | 0.010696 | 0.010288 | 0.05906 | 0.060287 | 0.16311 | -0.032043 | 119.9615 | -0.36621 | 8.67 | 3.9963 | 0.25635 | -0.27924 | 0.21057 | 120.0851 | -0.3067 | -0.14191 | 0.10071 | 0.19226 | 8.8943 | -115.8646 | -0.082398 | 0.2243 | 0.33417 | -0.054932 | 0.43488 | 4.2206 | 120.1859 | 0.19226 | 120.3094 | 0.48065 | -0.082398 | 120.1859 | 0.19226 | 0.48065 | 4.2206 | 120.3094 | -120.2271 | -120.1675
1389.625 | 120.0806 | -0.19226 | 119.8563 | -0.012589 | 0.015248 | 0.0096279 | 0.011143 | 0.05842 | 0.057082 | 0.16482 | -0.11444 | 120.0439 | -0.42114 | 8.3817 | 3.9185 | 0.15106 | -0.16022 | 0.09613 | 120.1675 | -0.34332 | -0.22888 | 0.18768 | 0.07782 | 8.5739 | -115.9378 | -0.15106 | 0.31128 | 0.3067 | 0.032044 | 0.28839 | 4.1107 | 120.2362 | 0.07782 | 120.3598 | 0.34332 | -0.15106 | 120.2362 | 0.07782 | 0.34332 | 4.1107 | 120.3598 | -120.2774 | -120.1996
1391.3125 | 120.0577 | -0.20142 | 119.9203 | -0.0049592 | 0.014608 | 0.0089871 | 0.0058021 | 0.05906 | 0.056869 | 0.16119 | -0.091553 | 120.0806 | -0.3891 | 8.1161 | 4.0421 | 0.17395 | -0.16937 | 0.14191 | 120.1401 | -0.31128 | -0.18768 | 0.16022 | 0.10986 | 8.3176 | -115.8783 | -0.10986 | 0.21973 | 0.29755 | 0.032043 | 0.34332 | 4.2435 | 120.282 | 0.10986 | 120.3415 | 0.37537 | -0.10986 | 120.282 | 0.10986 | 0.37537 | 4.2435 | 120.3415 | -120.3094 | -120.2316
1393 | 120.0439 | -0.23804 | 119.9478 | 0.0103 | 0.016103 | 0.0077053 | 0.0094337 | 0.058206 | 0.055587 | 0.16268 | -0.009155 | 120.0897 | -0.37994 | 10.0845 | 4.0558 | 0.26093 | -0.27466 | 0.20599 | 120.163 | -0.30212 | -0.14191 | 0.14191 | 0.22888 | 10.3226 | -115.892 | -0.064087 | 0.21515 | 0.37079 | -0.036621 | 0.44403 | 4.2938 | 120.3278 | 0.22888 | 120.401 | 0.49896 | -0.064087 | 120.3278 | 0.22888 | 0.49896 | 4.2938 | 120.401 | -120.3278 | -120.2499
1394.75 | 120.1355 | -0.19684 | 119.9615 | -0.0049592 | 0.014394 | 0.0053555 | 0.0077247 | 0.057138 | 0.057937 | 0.16097 | -0.059509 | 120.1447 | -0.39368 | 9.5261 | 3.9276 | 0.14191 | -0.091553 | 0.14648 | 120.2545 | -0.35248 | -0.19684 | 0.18311 | 0.13733 | 9.7229 | -116.0339 | -0.15564 | 0.29297 | 0.33417 | 0.10529 | 0.34332 | 4.1244 | 120.3415 | 0.13733 | 120.4514 | 0.33875 | -0.15564 | 120.3415 | 0.13733 | 0.33875 | 4.1244 | 120.4514 | -120.3552 | -120.314
1396.5 | 120.2316 | -0.18768 | 119.9707 | -0.0049592 | 0.017598 | 0.011978 | 0.010502 | 0.059701 | 0.056441 | 0.16439 | -0.12817 | 120.2042 | -0.41657 | 8.8257 | 3.8544 | 0.4715 | -0.09613 | 0.054932 | 120.2774 | -0.35248 | -0.22888 | 0.23346 | 0.059509 | 9.0134 | -116.1163 | -0.1648 | 0.3067 | 0.28839 | 0.091553 | 0.24261 | 4.0421 | 120.3918 | 0.059509 | 120.4651 | 0.65918 | -0.1648 | 120.3918 | 0.059509 | 0.65918 | 4.0421 | 120.4651 | -120.3873 | -120.3232
1398.2031 | 120.2179 | -0.19226 | 120.0302 | 0.0026703 | 0.014608 | 0.0072781 | 0.012638 | 0.056497 | 0.05815 | 0.16461 | -0.059509 | 120.2179 | -0.41657 | 7.7866 | 3.9322 | 0.60883 | -0.11902 | 0.1236 | 120.282 | -0.35248 | -0.2243 | 0.18768 | 0.13275 | 7.9788 | -116.098 | -0.16022 | 0.25177 | 0.35706 | 0.073242 | 0.31586 | 4.1245 | 120.4102 | 0.13275 | 120.4742 | 0.80109 | -0.16022 | 120.4102 | 0.13275 | 0.80109 | 4.1245 | 120.4742 | -120.4468 | -120.3827
1399.9531 | 120.1447 | -0.21515 | 120.0577 | -0.0049592 | 0.013112 | 0.01091 | 0.0043067 | 0.057138 | 0.05815 | 0.16332 | -0.036621 | 120.2271 | -0.37537 | 8.3038 | 3.9734 | 0.67749 | -0.23346 | 0.25177 | 120.2957 | -0.32044 | -0.16022 | 0.16937 | 0.17853 | 8.519 | -116.0843 | -0.10529 | 0.23804 | 0.33874 | -0.01831 | 0.46692 | 4.1885 | 120.4422 | 0.17853 | 120.5109 | 0.89264 | -0.10529 | 120.4422 | 0.17853 | 0.89264 | 4.1885 | 120.5109 | -120.433 | -120.3781
1401.6562 | 120.1904 | -0.21515 | 120.1035 | -0.012589 | 0.016744 | 0.0077053 | 0.0062293 | 0.057565 | 0.059005 | 0.16204 | -0.036621 | 120.2545 | -0.38452 | 8.0292 | 3.9276 | 0.63629 | 0.1236 | 0.58594 | 120.3369 | -0.32501 | -0.16937 | 0.15106 | 0.17853 | 8.2443 | -116.1758 | -0.10986 | 0.23346 | 0.3479 | 0.33875 | 0.80109 | 4.1428 | 120.4697 | 0.17853 | 120.5521 | 0.85144 | -0.10986 | 120.4697 | 0.17853 | 0.85144 | 4.1428 | 120.5521 | -120.488 | -120.4285
1403.4062 | 120.3598 | -0.15564 | 120.1035 | -0.0049592 | 0.013539 | 0.010483 | 0.012424 | 0.058633 | 0.058578 | 0.16439 | -0.13733 | 120.3186 | -0.42572 | 8.2443 | 3.8406 | 0.52185 | 1.2314 | 1.3779 | 120.4285 | -0.34332 | -0.27008 | 0.21515 | 0.018311 | 8.4 | -116.2628 | -0.18768 | 0.32501 | 0.28839 | 1.387 | 1.5335 | 3.9963 | 120.4742 | 0.018311 | 120.5841 | 0.67749 | -0.18768 | 120.4742 | 0.018311 | 0.67749 | 3.9963 | 120.5841 | -120.5292 | -120.4468
1405.1094 | 120.3873 | -0.16022 | 120.1263 | -0.0049592 | 0.014608 | 0.010055 | 0.0090063 | 0.057351 | 0.058578 | 0.16311 | -0.13733 | 120.3552 | -0.41657 | 8.0017 | 3.7445 | 0.53101 | 1.8631 | 1.9821 | 120.4193 | -0.35248 | -0.25635 | 0.22888 | 0.022888 | 8.1619 | -116.3818 | -0.19226 | 0.29297 | 0.27924 | 2.0233 | 2.1423 | 3.9047 | 120.5154 | 0.022888 | 120.5795 | 0.69122 | -0.19226 | 120.5154 | 0.022888 | 0.69122 | 3.9047 | 120.5795 | -120.5429 | -120.4788
1406.875 | 120.3049 | -0.2243 | 120.1996 | -0.0049592 | 0.013967 | 0.011551 | 0.0066565 | 0.056924 | 0.061355 | 0.16332 | -0.041199 | 120.3186 | -0.37079 | 9.2056 | 3.8452 | 0.67291 | 1.8951 | 2.33 | 120.401 | -0.31586 | -0.14648 | 0.11902 | 0.18311 | 9.4299 | -116.3544 | -0.091553 | 0.20142 | 0.32959 | 2.1194 | 2.5543 | 4.0695 | 120.5429 | 0.18311 | 120.6253 | 0.89722 | -0.091553 | 120.5429 | 0.18311 | 0.89722 | 4.0695 | 120.6253 | -120.5704 | -120.5154
1408.625 | 120.314 | -0.23346 | 120.2225 | -0.0049592 | 0.012258 | 0.0083463 | 0.0070837 | 0.062692 | 0.059432 | 0.16589 | -0.022888 | 120.3552 | -0.37994 | 0.29297 | 3.7857 | 0.71869 | 2.0737 | 2.5589 | 120.433 | -0.29755 | -0.14649 | 0.13275 | 0.21057 | 0.52643 | -116.4368 | -0.064087 | 0.21057 | 0.35706 | 2.3071 | 2.7924 | 4.0192 | 120.5887 | 0.21057 | 120.6665 | 0.95215 | -0.064087 | 120.5887 | 0.21057 | 0.95215 | 4.0192 | 120.6665 | -120.6024 | -120.52
1410.3125 | 120.3781 | -0.21057 | 120.2545 | -0.012589 | 0.013753 | 0.0085599 | 0.0075111 | 0.062906 | 0.056228 | 0.16888 | -0.050354 | 120.3873 | -0.37079 | 0.1236 | 3.7399 | 0.69122 | 2.9846 | 3.3554 | 120.4834 | -0.31586 | -0.16022 | 0.13275 | 0.16022 | 0.33417 | -116.5146 | -0.10529 | 0.22888 | 0.32043 | 3.1952 | 3.566 | 3.9505 | 120.5978 | 0.16022 | 120.694 | 0.90179 | -0.10529 | 120.5978 | 0.16022 | 0.90179 | 3.9505 | 120.694 | -120.6253 | -120.5704
1412 | 120.3644 | -0.21515 | 120.2957 | -0.012589 | 0.014394 | 0.010696 | 0.0072973 | 0.063974 | 0.058791 | 0.16695 | -0.027466 | 120.4422 | -0.36163 | 0.17853 | 3.7491 | 0.84686 | 3.1677 | 3.6118 | 120.5109 | -0.32501 | -0.14648 | 0.14648 | 0.18768 | 0.39368 | -116.5466 | -0.10986 | 0.21515 | 0.33417 | 3.3829 | 3.8269 | 3.9642 | 120.6573 | 0.18768 | 120.726 | 1.062 | -0.10986 | 120.6573 | 0.18768 | 1.062 | 3.9642 | 120.726 | -120.6573 | -120.6207
1413.75 | 120.5109 | -0.16479 | 120.2545 | -0.0049592 | 0.013753 | 0.010269 | 0.011997 | 0.06376 | 0.056869 | 0.16589 | -0.12817 | 120.433 | -0.42572 | 0.041199 | 3.6026 | 0.87891 | -0.064087 | 0.07782 | 120.5887 | -0.34332 | -0.26092 | 0.17853 | 0.036621 | 0.20599 | -116.6519 | -0.17853 | 0.33417 | 0.29755 | 0.10071 | 0.24261 | 3.7674 | 120.5978 | 0.036621 | 120.7535 | 1.0437 | -0.17853 | 120.5978 | 0.036621 | 1.0437 | 3.7674 | 120.7535 | -120.6802 | -120.5978
1415.5156 | 120.5429 | -0.19226 | 120.2728 | 0.0026703 | 0.018025 | 0.010696 | 0.013279 | 0.06611 | 0.055373 | 0.16695 | -0.10529 | 120.5063 | -0.42114 | 0.064087 | 3.653 | 0.99792 | -0.064087 | 0.10529 | 120.6024 | -0.34332 | -0.22888 | 0.23346 | 0.086975 | 0.25635 | -116.6199 | -0.15106 | 0.32959 | 0.31586 | 0.12817 | 0.29755 | 3.8452 | 120.6985 | 0.086975 | 120.7947 | 1.1902 | -0.15106 | 120.6985 | 0.086975 | 1.1902 | 3.8452 | 120.7947 | -120.694 | -120.6162
1417.2812 | 120.433 | -0.21057 | 120.3506 | -0.0049592 | 0.012899 | 0.0077053 | 0.0066565 | 0.063119 | 0.059432 | 0.16695 | -0.013733 | 120.4834 | -0.37994 | 0.16022 | 3.7994 | 0.98419 | -0.18768 | 0.25177 | 120.6116 | -0.32501 | -0.16937 | 0.13275 | 0.19684 | 0.37079 | -116.5512 | -0.11444 | 0.26093 | 0.36621 | 0.022888 | 0.46234 | 4.01 | 120.694 | 0.19684 | 120.8221 | 1.1948 | -0.11444 | 120.694 | 0.19684 | 1.1948 | 4.01 | 120.8221 | -120.7306 | -120.6757
1418.9688 | 120.4605 | -0.21057 | 120.3644 | -0.0049592 | 0.015676 | 0.0087735 | 0.0066565 | 0.060342 | 0.058578 | 0.16802 | -0.018311 | 120.5338 | -0.37537 | 0.17853 | 3.804 | 0.55389 | -0.19226 | 0.28381 | 120.5521 | -0.32501 | -0.16479 | 0.16937 | 0.19226 | 0.3891 | -116.5604 | -0.11444 | 0.18768 | 0.35705 | 0.01831 | 0.49438 | 4.0146 | 120.7443 | 0.19226 | 120.7626 | 0.76446 | -0.11444 | 120.7443 | 0.19226 | 0.76446 | 4.0146 | 120.7626 | -120.7397 | -120.6894
1420.7031 | 120.5704 | -0.19684 | 120.3506 | 0.0103 | 0.015462 | 0.0070645 | 0.012211 | 0.064615 | 0.056441 | 0.16866 | -0.073242 | 120.5795 | -0.40741 | 0.10986 | 4.9484 | 0.46692 | -0.082397 | 0.15106 | 120.6528 | -0.33875 | -0.21057 | 0.22888 | 0.1236 | 0.3067 | -115.4022 | -0.14191 | 0.30212 | 0.33417 | 0.11444 | 0.3479 | 5.1453 | 120.7764 | 0.1236 | 120.8496 | 0.66376 | -0.14191 | 120.7764 | 0.1236 | 0.66376 | 5.1453 | 120.8496 | -120.7581 | -120.6894
1422.4531 | 120.5063 | -0.21515 | 120.4147 | -0.012589 | 0.014608 | 0.0094143 | 0.0062293 | 0.064615 | 0.058364 | 0.16802 | -0.013733 | 120.575 | -0.35248 | 0.18768 | 4.4403 | 0.57678 | -0.19684 | 0.27924 | 120.6665 | -0.32501 | -0.13733 | 0.16022 | 0.20142 | 0.40283 | -115.9744 | -0.10986 | 0.25177 | 0.33875 | 0.018311 | 0.49438 | 4.6555 | 120.7901 | 0.20142 | 120.8817 | 0.79193 | -0.10986 | 120.7901 | 0.20142 | 0.79193 | 4.6555 | 120.8817 | -120.7672 | -120.7397
1424.1406 | 120.5017 | -0.21515 | 120.3278 | 0.0103 | 0.092153 | 0.081192 | 0.0070837 | 0.061197 | 0.06285 | 0.1708 | 120.2087 | 120.5658 | -0.37079 | 0.13275 | 0.091553 | 0.10529 | -0.15564 | 0.21973 | 120.5887 | -0.33417 | -0.15564 | 0.23804 | 120.4239 | 0.3479 | -120.2362 | -0.11902 | 0.26093 | 120.5795 | 0.059509 | 0.43488 | 0.3067 | 120.7809 | 120.4239 | 120.8038 | 0.32044 | -0.11902 | 120.7809 | 120.4239 | 0.32044 | 0.3067 | 120.8038 | -120.6985 | -120.6619
1425.8906 | 120.6573 | -0.16022 | 120.3964 | 0.0026703 | 0.093648 | 0.086746 | 0.0098609 | 0.060342 | 0.062637 | 0.17123 | 120.2225 | 120.6482 | -0.40741 | 0.068665 | 0.009155 | -0.009155 | 0.045776 | 0.14648 | 120.6619 | -0.37079 | -0.24719 | 0.25177 | 120.3827 | 0.22888 | -120.3873 | -0.21057 | 0.2655 | 120.6299 | 0.20599 | 0.3067 | 0.16937 | 120.8084 | 120.3827 | 120.8221 | 0.15106 | -0.21057 | 120.8084 | 120.3827 | 0.15106 | 0.16937 | 120.8221 | -120.8038 | -120.7672
1427.5781 | 120.5383 | -0.21973 | 120.4285 | -0.0049592 | 0.093862 | 0.08461 | 0.0055885 | 0.061197 | 0.062209 | 0.17016 | 120.3598 | 120.5887 | -0.37994 | 0.21515 | 0.14648 | 0.14191 | -0.16937 | 0.3067 | 120.6436 | -0.33417 | -0.16022 | 0.16022 | 120.5795 | 0.43488 | -120.282 | -0.11444 | 0.21515 | 120.7397 | 0.050354 | 0.52643 | 0.36621 | 120.8084 | 120.5795 | 120.8633 | 0.36163 | -0.11444 | 120.8084 | 120.5795 | 0.36163 | 0.36621 | 120.8633 | -120.8084 | -120.7626
1429.2812 | 120.4376 | -0.23346 | 120.4193 | -0.012589 | 0.015889 | 0.0070645 | 0.0068701 | 0.061838 | 0.060928 | 0.177 | 0.022888 | 0.76446 | -0.33875 | 0.21057 | 0.17395 | 0.15106 | -0.15106 | 0.30212 | 120.6162 | -0.32501 | -0.10529 | -119.6548 | 0.25635 | 0.44403 | -120.2454 | -0.091553 | 0.19684 | 0.36163 | 0.082397 | 0.53558 | 0.40741 | 0.99792 | 0.25635 | 120.8496 | 0.38452 | -0.091553 | 0.99792 | 0.25635 | 0.38452 | 0.40741 | 120.8496 | -120.7581 | -120.7443
1431.0312 | 120.7077 | -0.17395 | 120.4605 | -0.0049592 | 0.018453 | 0.010269 | 0.011143 | 0.062051 | 0.059646 | 0.17977 | -0.091553 | 0.19226 | -0.36163 | 0.064087 | -0.004578 | -0.018311 | -0.041199 | 0.10529 | 120.7489 | -0.35706 | -0.18768 | -120.2682 | 0.082397 | 0.23804 | -120.4651 | -0.18311 | 0.28839 | 0.27008 | 0.13275 | 0.27924 | 0.16937 | 0.36621 | 0.082397 | 120.9229 | 0.15564 | -0.18311 | 0.36621 | 0.082397 | 0.15564 | 0.16937 | 120.9229 | -120.8221 | -120.8176
1432.7188 | 120.5063 | -0.16022 | 120.282 | -0.0049592 | 0.017385 | 0.012192 | 0.0081519 | -0.0020359 | 0.061141 | 0.10287 | -0.059509 | 0.19684 | -0.34332 | 120.0394 | 0.068665 | 0.009155 | -0.068665 | 0.13275 | 120.6116 | -0.34332 | -0.18311 | -120.0851 | 0.10071 | 120.1996 | -120.2133 | -0.18311 | 0.32959 | 0.28381 | 0.091552 | 0.29297 | 0.22888 | 0.35706 | 0.10071 | 120.7718 | 0.16937 | -0.18311 | 0.35706 | 0.10071 | 0.16937 | 0.22888 | 120.7718 | -120.6253 | -120.6253
1434.4688 | 120.6116 | -0.19226 | 120.5292 | -0.0049592 | 0.016957 | 0.011123 | 0.0038795 | -0.0035313 | 0.06285 | 0.10436 | 0.009155 | 0.14191 | -0.31586 | 120.2957 | 0.13733 | 0.064087 | -0.12817 | 0.20142 | 120.7443 | -0.33875 | -0.1236 | -120.3873 | 0.20142 | 120.488 | -120.3918 | -0.14648 | 0.21515 | 0.32501 | 0.064087 | 0.39368 | 0.32959 | 0.33417 | 0.20142 | 120.9366 | 0.25635 | -0.14648 | 0.33417 | 0.20142 | 0.25635 | 0.32959 | 120.9366 | -120.845 | -120.8679
1436.2188 | 120.7352 | -0.15106 | 120.5292 | -0.0049592 | 0.018453 | 0.01326 | 0.0081519 | -0.0018223 | 0.061141 | 0.10201 | -0.064087 | 0.18768 | -0.35248 | 120.2454 | 0.018311 | -0.013733 | -0.091553 | 0.091553 | 120.845 | -0.3479 | -0.20142 | -120.3415 | 0.086975 | 120.3964 | -120.5109 | -0.19684 | 0.31586 | 0.28839 | 0.059509 | 0.24261 | 0.16937 | 0.33874 | 0.086975 | 120.9961 | 0.13733 | -0.19684 | 0.33874 | 0.086975 | 0.13733 | 0.16937 | 120.9961 | -120.8817 | -120.8771
1437.9062 | 120.6711 | -0.19226 | 120.5795 | 0.0026703 | 0.016744 | 0.0079189 | 0.0040931 | -0.0043857 | 0.06285 | 0.10116 | -0.004578 | 0.15564 | -0.33875 | 120.3598 | 0.1236 | 0.073242 | -0.12817 | 0.20599 | 120.8176 | -0.33417 | -0.14648 | -120.4239 | 0.18768 | 120.5521 | -120.4559 | -0.14191 | 0.23804 | 0.33417 | 0.064087 | 0.39826 | 0.31586 | 0.3479 | 0.18768 | 121.0098 | 0.2655 | -0.14191 | 0.3479 | 0.18768 | 0.2655 | 0.31586 | 121.0098 | -120.9183 | -120.9137
1439.6562 | 120.7855 | -0.14191 | 120.5521 | 0.0026703 | 0.014821 | 0.0096279 | 0.0094337 | -0.0024631 | 0.062209 | 0.10308 | -0.10986 | 0.20599 | -0.36163 | 120.3003 | -0.027466 | 0.032043 | 0.022888 | 0.13733 | 120.8862 | -0.34332 | -0.21973 | -120.3461 | 0.032044 | 120.4422 | -120.5795 | -0.20142 | 0.33417 | 0.25177 | 0.16479 | 0.27924 | 0.11444 | 0.3479 | 0.032044 | 121.0281 | 0.17395 | -0.20142 | 0.3479 | 0.032044 | 0.17395 | 0.11444 | 121.0281 | -120.9137 | -120.8954
1441.3438 | 120.7901 | -0.16022 | 120.5978 | -0.0049592 | 0.019307 | 0.01326 | 0.014774 | -0.0037449 | 0.060287 | 0.10629 | -0.064087 | 0.17395 | -0.33875 | 120.3323 | -0.027466 | 0.032043 | -0.064087 | 0.14191 | 120.8862 | -0.34332 | -0.17853 | -120.4239 | 0.09613 | 120.4926 | -120.6253 | -0.18311 | 0.28839 | 0.27466 | 0.09613 | 0.30212 | 0.13275 | 0.33417 | 0.09613 | 121.0464 | 0.19226 | -0.18311 | 0.33417 | 0.09613 | 0.19226 | 0.13275 | 121.0464 | -120.9366 | -120.9412
1443.1094 | 120.7993 | -0.17853 | 120.6116 | 0.0026703 | 0.018453 | 0.011337 | 0.010929 | -0.0041721 | 0.061568 | 0.1033 | -0.045776 | 0.16937 | -0.36163 | 120.3781 | -0.018311 | 0.041199 | -0.059509 | 0.13733 | 120.9045 | -0.32501 | -0.1831 | -120.4422 | 0.13275 | 120.5566 | -120.6299 | -0.14648 | 0.29297 | 0.31586 | 0.11902 | 0.31586 | 0.16022 | 0.3479 | 0.13275 | 121.0831 | 0.21973 | -0.14648 | 0.3479 | 0.13275 | 0.21973 | 0.16022 | 121.0831 | -120.9732 | -120.9366
1444.8594 | 120.7214 | -0.19226 | 120.6253 | 0.0026703 | 0.016103 | 0.012832 | 0.0032385 | -0.0069491 | 0.063918 | 0.10308 | 0.013733 | 0.14648 | -0.3067 | 120.4742 | 0.091553 | 0.16479 | -0.19226 | 0.28381 | 120.8405 | -0.32044 | -0.11444 | -120.4788 | 0.20599 | 120.6665 | -120.5338 | -0.12817 | 0.21515 | 0.32043 | 0 | 0.47607 | 0.28381 | 0.33874 | 0.20599 | 121.0327 | 0.35706 | -0.12817 | 0.33874 | 0.20599 | 0.35706 | 0.28381 | 121.0327 | -120.932 | -120.9457
1446.5469 | 120.8862 | -0.16479 | 120.6345 | -0.012589 | 0.018025 | 0.012192 | 0.01157 | -0.0056675 | 0.061782 | 0.105 | -0.086975 | 0.1831 | -0.37079 | 120.3781 | -0.045776 | 0.013733 | -0.054932 | 0.09613 | 120.9732 | -0.33417 | -0.20599 | -120.4514 | 0.07782 | 120.5429 | -120.6802 | -0.16937 | 0.33875 | 0.28381 | 0.10986 | 0.26092 | 0.11902 | 0.3479 | 0.07782 | 121.138 | 0.17853 | -0.16937 | 0.3479 | 0.07782 | 0.17853 | 0.11902 | 121.138 | -121.0052 | -120.9686
1448.25 | 120.8817 | -0.15564 | 120.6757 | -0.0049592 | 0.018666 | 0.012832 | 0.010929 | -0.0026767 | 0.061996 | 0.10607 | -0.068665 | 0.16937 | -0.35706 | 120.401 | -0.032043 | 0.050354 | -0.07782 | 0.1236 | 120.9686 | -0.32044 | -0.20142 | -120.5063 | 0.086975 | 120.5566 | -120.7077 | -0.1648 | 0.29297 | 0.28839 | 0.07782 | 0.27924 | 0.1236 | 0.32501 | 0.086975 | 121.1243 | 0.20599 | -0.1648 | 0.32501 | 0.086975 | 0.20599 | 0.1236 | 121.1243 | -121.0327 | -120.9961
1450 | 120.9274 | -0.14191 | 120.6802 | -0.0049592 | 0.020162 | 0.0062101 | 0.0092199 | -0.0043857 | 0.061355 | 0.1065 | -0.091553 | 0.18768 | -0.34332 | 120.433 | -0.036621 | 0.018311 | -0.004578 | 0.13733 | 120.9961 | -0.35706 | -0.20142 | -120.4926 | 0.050354 | 120.575 | -120.7169 | -0.21515 | 0.31586 | 0.25177 | 0.13733 | 0.27924 | 0.10529 | 0.32959 | 0.050354 | 121.138 | 0.16022 | -0.21515 | 0.32959 | 0.050354 | 0.16022 | 0.10529 | 121.138 | -121.0236 | -121.0373
1451.6875 | 120.8771 | -0.17853 | 120.6802 | -0.0049592 | 0.016317 | 0.011764 | 0.011143 | -0.0054539 | 0.060928 | 0.10372 | -0.027466 | 0.16479 | -0.33875 | 120.4971 | -0.013733 | 0.027466 | -0.11902 | 0.16022 | 120.9915 | -0.34332 | -0.16022 | -120.5154 | 0.15106 | 120.6757 | -120.694 | -0.16479 | 0.31128 | 0.31128 | 0.059509 | 0.33874 | 0.16479 | 0.34332 | 0.15106 | 121.17 | 0.20599 | -0.16479 | 0.34332 | 0.15106 | 0.20599 | 0.16479 | 121.17 | -121.019 | -121.0236
1453.4531 | 120.9549 | -0.13733 | 120.694 | 0.0026703 | 0.016744 | 0.0064237 | 0.0079383 | -0.0045993 | 0.061782 | 0.10436 | -0.10986 | 0.17853 | -0.37079 | 120.4514 | -0.064087 | -0.027466 | -0.032043 | 0.10529 | 121.019 | -0.3479 | -0.23346 | -120.5154 | 0.027466 | 120.5887 | -120.7581 | -0.21057 | 0.32501 | 0.26093 | 0.10529 | 0.24262 | 0.073242 | 0.31586 | 0.027466 | 121.1563 | 0.10986 | -0.21057 | 0.31586 | 0.027466 | 0.10986 | 0.073242 | 121.1563 | -121.0648 | -121.0419
1455.2188 | 120.9045 | -0.17853 | 120.726 | 0.0026703 | 0.017812 | 0.012405 | 0.0047339 | -0.0052401 | 0.063277 | 0.10394 | -0.068665 | 0.15564 | -0.33875 | 120.5017 | -0.036621 | 0.004578 | -0.054932 | 0.13275 | 121.0052 | -0.3479 | -0.16022 | -120.5704 | 0.10986 | 120.6802 | -120.7626 | -0.16937 | 0.27924 | 0.27008 | 0.1236 | 0.31128 | 0.14191 | 0.33417 | 0.10986 | 121.1838 | 0.18311 | -0.16937 | 0.33417 | 0.10986 | 0.18311 | 0.14191 | 121.1838 | -121.0648 | -121.0739
1456.9062 | 120.8267 | -0.19226 | 120.7764 | -0.020218 | 0.014821 | 0.01091 | 0.0051611 | -0.0048129 | 0.063277 | 0.1033 | 0.022888 | 0.11902 | -0.30212 | 120.6482 | 0.045776 | 0.1236 | -0.21057 | 0.26093 | 121.0144 | -0.31128 | -0.10986 | -120.6573 | 0.21515 | 120.8405 | -120.7306 | -0.11902 | 0.23804 | 0.32501 | -0.01831 | 0.45319 | 0.23804 | 0.31128 | 0.21515 | 121.2067 | 0.31586 | -0.11902 | 0.31128 | 0.21515 | 0.31586 | 0.23804 | 121.2067 | -121.0785 | -121.0876
1458.6562 | 120.9045 | -0.20142 | 120.8313 | 0.0026703 | 0.014821 | 0.012192 | 0.0079383 | -0.0060947 | 0.061782 | 0.10415 | -0.009155 | 0.11444 | -0.32044 | 120.5658 | 0 | 0.091553 | -0.23804 | 0.1831 | 121.0556 | -0.30212 | -0.11902 | -120.7169 | 0.19226 | 120.7672 | -120.8313 | -0.10071 | 0.2243 | 0.31128 | -0.036621 | 0.38452 | 0.20142 | 0.31586 | 0.19226 | 121.257 | 0.29297 | -0.10071 | 0.31586 | 0.19226 | 0.29297 | 0.20142 | 121.257 | -121.1517 | -121.1334
1460.4062 | 121.0236 | -0.13275 | 120.7809 | 0.0026703 | 0.016957 | 0.011764 | 0.0094337 | -0.0069491 | 0.061782 | 0.10244 | -0.09613 | 0.17853 | -0.3479 | 120.5429 | -0.068665 | 0.004578 | -0.018311 | 0.10529 | 121.106 | -0.36621 | -0.21515 | -120.6024 | 0.036621 | 120.6757 | -120.8496 | -0.23346 | 0.32501 | 0.25177 | 0.11444 | 0.23804 | 0.064086 | 0.31128 | 0.036621 | 121.2387 | 0.13733 | -0.23346 | 0.31128 | 0.036621 | 0.13733 | 0.064086 | 121.2387 | -121.1288 | -121.1472
1462.1562 | 116.954 | -22.7234 | 94.1071 | 0.0103 | 0.019307 | 0.0079189 | 6.9377 | -0.0067355 | 0.035293 | 7.0221 | -0.054932 | 0.068665 | -23.8678 | 89.035 | -0.064087 | 0.17395 | -0.37994 | 0.13733 | 88.266 | -15.7425 | -1.1444 | -94.0384 | 22.6685 | 111.7584 | -94.1711 | 6.9809 | -5.8411 | 23.8129 | 22.3434 | 22.8607 | 22.6593 | 22.7921 | 22.6685 | 110.9894 | 22.8973 | 6.9809 | 22.7921 | 22.6685 | 22.8973 | 22.6593 | 110.9894 | -117.9749 | -109.8495
1463.9062 | 120.6848 | -0.1831 | 120.575 | 0.0026703 | 0.014394 | 0.0081327 | 0.0040931 | -0.0035313 | 0.062423 | 0.10565 | -0.054932 | 0.13733 | -0.31586 | 120.3415 | 0.004578 | 0.19684 | -0.18768 | 0.19226 | 120.7809 | -0.31128 | -0.13275 | -120.4376 | 0.12817 | 120.5246 | -120.5704 | -0.12817 | 0.20599 | 0.26093 | -0.004578 | 0.37537 | 0.18768 | 0.32043 | 0.12817 | 120.9641 | 0.37994 | -0.12817 | 0.32043 | 0.12817 | 0.37994 | 0.18768 | 120.9641 | -120.8908 | -120.8862
1465.5938 | 120.8221 | -0.16937 | 120.6528 | 0.0026703 | 0.019307 | 0.0066373 | 0.040622 | -0.0024631 | 0.061782 | 0.13876 | -0.059509 | 0.13733 | -0.36621 | 120.3873 | -0.050354 | 1.5381 | -0.1831 | 0.10986 | 120.9137 | -0.33417 | -0.19684 | -120.5154 | 0.10986 | 120.5566 | -120.7031 | -0.16479 | 0.26093 | 0.3067 | -0.013732 | 0.27924 | 0.11902 | 0.3067 | 0.10986 | 121.0831 | 1.7075 | -0.16479 | 0.3067 | 0.10986 | 1.7075 | 0.11902 | 121.0831 | -121.019 | -120.9869
1467.3594 | 120.575 | -0.1831 | 120.4971 | -0.0049592 | 0.014608 | 0.0089871 | 0.0030249 | -0.0020359 | 0.061782 | 0.099023 | 0.027466 | 0.11902 | -0.32959 | 120.3369 | 0.050354 | 0.11444 | -0.21057 | 0.27008 | 120.7443 | -0.30212 | -0.14649 | -120.3781 | 0.21057 | 120.52 | -120.4468 | -0.11902 | 0.24719 | 0.35706 | -0.027466 | 0.45319 | 0.23346 | 0.30212 | 0.21057 | 120.9274 | 0.29755 | -0.11902 | 0.30212 | 0.21057 | 0.29755 | 0.23346 | 120.9274 | -120.8267 | -120.7993
1469.1094 | 120.7031 | -0.19684 | 120.639 | 0.0026703 | 0.01888 | 0.0083463 | -0.0029565 | -0.0045993 | 0.063918 | 0.098596 | 0.018311 | 0.11902 | -0.30212 | 120.4468 | 0.032043 | 0.16937 | -0.21057 | 0.24261 | 120.8633 | -0.31586 | -0.10529 | -120.52 | 0.21515 | 120.6436 | -120.607 | -0.11902 | 0.2243 | 0.32044 | -0.013733 | 0.43945 | 0.22888 | 0.31586 | 0.21515 | 121.0602 | 0.36621 | -0.11902 | 0.31586 | 0.21515 | 0.36621 | 0.22888 | 121.0602 | -120.9412 | -120.9549
1470.8594 | 120.7718 | -0.21515 | 120.6757 | 0.0026703 | 0.017385 | 0.0072781 | 0.0049475 | -0.0018223 | 0.063064 | 0.10244 | 0.004578 | 0.11444 | -0.32044 | 120.4697 | 0.009155 | 0.12817 | -0.26093 | 0.21057 | 120.9045 | -0.30212 | -0.10529 | -120.5612 | 0.21973 | 120.6848 | -120.6665 | -0.086975 | 0.22888 | 0.32501 | -0.045776 | 0.42572 | 0.2243 | 0.32959 | 0.21973 | 121.1197 | 0.34332 | -0.086975 | 0.32959 | 0.21973 | 0.34332 | 0.2243 | 121.1197 | -120.9961 | -120.9778
1472.5625 | 120.8359 | -0.21515 | 120.726 | -0.0049592 | 0.017385 | 0.0066373 | 0.0023841 | -0.0045993 | 0.062209 | 0.099664 | -0.027466 | 0.1236 | -0.31128 | 120.488 | -0.013733 | 0.13275 | -0.20599 | 0.16479 | 120.9595 | -0.32044 | -0.09613 | -120.6024 | 0.18768 | 120.7031 | -120.7397 | -0.10529 | 0.23346 | 0.28381 | 0.009155 | 0.37994 | 0.20142 | 0.33875 | 0.18768 | 121.1746 | 0.3479 | -0.10529 | 0.33875 | 0.18768 | 0.3479 | 0.20142 | 121.1746 | -121.0373 | -121.0464
1474.3281 | 120.8908 | -0.15564 | 120.5978 | 0.0026703 | 0.019307 | 0.0096279 | 0.0032385 | -0.0016087 | 0.061782 | 0.093682 | -0.082397 | 0.16937 | -0.35248 | 120.3781 | -0.073242 | 1.5976 | -0.050354 | 0.10986 | 120.9824 | -0.33875 | -0.19684 | -120.4285 | 0.073243 | 120.5338 | -120.6711 | -0.18311 | 0.38452 | 0.27008 | 0.10529 | 0.2655 | 0.082398 | 0.32501 | 0.073243 | 121.138 | 1.7532 | -0.18311 | 0.32501 | 0.073243 | 1.7532 | 0.082398 | 121.138 | -120.9503 | -120.9366
1476.0781 | 120.8084 | -0.21057 | 120.7535 | 0.0026703 | 0.014394 | 0.011337 | -0.0029565 | -0.0016087 | 0.061782 | 0.095605 | 0.018311 | 0.13733 | -0.32044 | 120.5566 | 0.054932 | 1.886 | -0.2243 | 0.26093 | 120.9915 | -0.30212 | -0.10986 | -120.6162 | 0.22888 | 120.7672 | -120.6985 | -0.091553 | 0.23804 | 0.33875 | -0.013733 | 0.4715 | 0.2655 | 0.3479 | 0.22888 | 121.2021 | 2.0966 | -0.091553 | 0.3479 | 0.22888 | 2.0966 | 0.2655 | 121.2021 | -121.0739 | -121.0556
1477.8281 | 120.9732 | -0.16479 | 120.7169 | -0.0049592 | 0.015462 | 0.012832 | 0.0055885 | -0.0039585 | 0.061782 | 0.095391 | -0.073242 | 0.13275 | -0.35248 | 120.4651 | -0.10071 | 1.9592 | -0.086975 | 0.07782 | 121.0876 | -0.32501 | -0.18768 | -120.5841 | 0.091553 | 120.6299 | -120.8176 | -0.16022 | 0.37079 | 0.27924 | 0.07782 | 0.24261 | 0.064087 | 0.29755 | 0.091553 | 121.2524 | 2.124 | -0.16022 | 0.29755 | 0.091553 | 2.124 | 0.064087 | 121.2524 | -121.0693 | -121.0419
1479.5156 | 120.9595 | -0.17395 | 120.7809 | -0.012589 | 0.018666 | 0.0062101 | 0.0040931 | -0.0018223 | 0.060714 | 0.095178 | -0.032043 | 0.16022 | -0.3479 | 120.5612 | -0.022888 | 2.2339 | -0.13275 | 0.16022 | 121.0693 | -0.32044 | -0.17395 | -120.6207 | 0.14191 | 120.7352 | -120.8038 | -0.14649 | 0.28839 | 0.31586 | 0.041199 | 0.33417 | 0.15106 | 0.33417 | 0.14191 | 121.2433 | 2.4078 | -0.14649 | 0.33417 | 0.14191 | 2.4078 | 0.15106 | 121.2433 | -121.1288 | -121.1014
1481.2656 | 120.9091 | -0.20599 | 120.8084 | -0.0049592 | 0.01888 | 0.0066373 | -0.00060672 | -0.00054047 | 0.063918 | 0.09475 | 0 | 0.1236 | -0.28839 | 120.5704 | 0.013733 | 2.243 | -0.23346 | 0.17853 | 121.0464 | -0.29755 | -0.082397 | -120.6848 | 0.20599 | 120.7764 | -120.7947 | -0.091552 | 0.23804 | 0.28839 | -0.027465 | 0.38452 | 0.21973 | 0.32959 | 0.20599 | 121.2524 | 2.449 | -0.091552 | 0.32959 | 0.20599 | 2.449 | 0.21973 | 121.2524 | -121.0968 | -121.106
1483.0312 | 120.8633 | -0.19226 | 120.7397 | -0.012589 | 0.018666 | 0.0053555 | -0.0021021 | 0.00010033 | 0.062637 | 0.087914 | 0.036621 | 0.13733 | -0.30212 | 120.7535 | 0.036621 | 0.28839 | -0.27924 | 0.21057 | 121.0052 | -0.27924 | -0.10986 | -120.6024 | 0.22888 | 120.9457 | -120.7031 | -0.086975 | 0.2655 | 0.33875 | -0.086975 | 0.40283 | 0.22888 | 0.32959 | 0.22888 | 121.1975 | 0.48065 | -0.086975 | 0.32959 | 0.22888 | 0.48065 | 0.22888 | 121.1975 | -121.0419 | -121.019
1484.7188 | 121.0144 | -0.15106 | 120.7535 | 0.0026703 | 0.016957 | 0.0027921 | -0.0042383 | -0.0054539 | 0.060714 | 0.088983 | -0.086975 | 0.14648 | -0.34332 | 120.8908 | -0.059509 | 0.52643 | -0.054932 | 0.13275 | 121.1014 | -0.34332 | -0.19226 | -120.607 | 0.064087 | 121.0419 | -120.813 | -0.19226 | 0.3479 | 0.25635 | 0.09613 | 0.28381 | 0.091553 | 0.29755 | 0.064087 | 121.2524 | 0.67749 | -0.19226 | 0.29755 | 0.064087 | 0.67749 | 0.091553 | 121.2524 | -121.0968 | -121.0968
1486.4688 | 121.0419 | -0.14191 | 120.7809 | 0.0026703 | 0.017385 | 0.0055691 | 0.0017431 | -0.0018223 | 0.060287 | 0.088128 | -0.09613 | 0.16937 | -0.33417 | 120.9824 | -0.082397 | 0.16479 | -0.10529 | 0.086975 | 121.1517 | -0.32959 | -0.19226 | -120.6116 | 0.045777 | 121.1243 | -120.8633 | -0.18768 | 0.37079 | 0.23804 | 0.036621 | 0.22888 | 0.05951 | 0.31128 | 0.045777 | 121.2936 | 0.3067 | -0.18768 | 0.31128 | 0.045777 | 0.3067 | 0.05951 | 121.2936 | -121.1151 | -121.1105
1488.2188 | 120.932 | -0.18768 | 120.8588 | -0.0049592 | 0.015676 | 0.0081327 | -0.0033837 | -0.00032687 | 0.061141 | 0.091546 | 0.018311 | 0.13275 | -0.30212 | 121.1151 | 0.041199 | 0.20142 | -0.28839 | 0.21057 | 121.1105 | -0.30212 | -0.11444 | -120.726 | 0.20599 | 121.3028 | -120.8176 | -0.11444 | 0.25177 | 0.32044 | -0.10071 | 0.39825 | 0.22888 | 0.32043 | 0.20599 | 121.2982 | 0.3891 | -0.11444 | 0.32043 | 0.20599 | 0.3891 | 0.22888 | 121.2982 | -121.1609 | -121.1609
1489.9688 | 120.9961 | -0.1831 | 120.845 | -0.0049592 | 0.01653 | 0.0047147 | -0.0029565 | -0.0041721 | 0.061355 | 0.088983 | -0.050354 | 0.15564 | -0.31128 | 121.0922 | 0.004578 | 0.12817 | -0.19684 | 0.19684 | 121.1243 | -0.3067 | -0.12817 | -120.6894 | 0.13275 | 121.2753 | -120.8405 | -0.1236 | 0.27924 | 0.26092 | -0.013733 | 0.37994 | 0.18768 | 0.33874 | 0.13275 | 121.3074 | 0.31128 | -0.1236 | 0.33874 | 0.13275 | 0.31128 | 0.18768 | 121.3074 | -121.1563 | -121.1517
1491.6562 | 120.9686 | -0.20599 | 120.8908 | 0.0026703 | 0.013753 | 0.00044212 | 0.0017431 | -0.0043857 | 0.060928 | 0.09176 | 0.041199 | 0.1236 | -0.3067 | 121.17 | 0.027466 | 0.16937 | -0.27466 | 0.23804 | 121.1426 | -0.29755 | -0.10071 | -120.7672 | 0.24719 | 121.376 | -120.8633 | -0.091552 | 0.25177 | 0.3479 | -0.068664 | 0.44403 | 0.23346 | 0.32959 | 0.24719 | 121.3486 | 0.37537 | -0.091552 | 0.32959 | 0.24719 | 0.37537 | 0.23346 | 121.3486 | -121.1975 | -121.1884
1493.4062 | 121.0968 | -0.14648 | 120.8771 | 0.0026703 | 0.019094 | 0.0064237 | 0.0023841 | -0.0043857 | 0.059219 | 0.088555 | -0.064087 | 0.16479 | -0.33417 | 121.1151 | -0.050354 | 0.036621 | -0.064087 | 0.13733 | 121.2204 | -0.34332 | -0.18768 | -120.7123 | 0.082397 | 121.2616 | -120.9274 | -0.19684 | 0.34332 | 0.27008 | 0.082397 | 0.28381 | 0.09613 | 0.31128 | 0.082397 | 121.3669 | 0.18311 | -0.19684 | 0.31128 | 0.082397 | 0.18311 | 0.09613 | 121.3669 | -121.2112 | -121.2204
1495.1719 | 121.0648 | -0.16937 | 120.9457 | -0.0049592 | 0.015462 | 0.0036465 | -0.0035973 | -0.0043857 | 0.0605 | 0.092828 | -0.045776 | 0.1236 | -0.30212 | 121.1426 | -0.013733 | 0.082397 | -0.1831 | 0.15564 | 121.2112 | -0.3067 | -0.13275 | -120.8221 | 0.1236 | 121.312 | -120.9595 | -0.13733 | 0.2655 | 0.25635 | -0.013732 | 0.32501 | 0.15564 | 0.29297 | 0.1236 | 121.3806 | 0.25177 | -0.13733 | 0.29297 | 0.1236 | 0.25177 | 0.15564 | 121.3806 | -121.2479 | -121.2524
1496.9375 | 121.0602 | -0.17395 | 120.9549 | -0.0049592 | 0.016317 | 0.0038601 | -0.0010339 | -0.0054539 | 0.060714 | 0.087487 | -0.013733 | 0.11902 | -0.29755 | 121.2021 | 0.045776 | 0.11444 | -0.20142 | 0.23804 | 121.2021 | -0.31586 | -0.1236 | -120.8359 | 0.16022 | 121.376 | -120.9091 | -0.14191 | 0.24719 | 0.28381 | -0.027466 | 0.41199 | 0.21973 | 0.29297 | 0.16022 | 121.376 | 0.28839 | -0.14191 | 0.29297 | 0.16022 | 0.28839 | 0.21973 | 121.376 | -121.2524 | -121.2708
1498.625 | 121.0556 | -0.21057 | 120.9824 | -0.0049592 | 0.015889 | 0.0049283 | 0.0017431 | -0.0048129 | 0.061141 | 0.08941 | 0.032043 | 0.10071 | -0.28381 | 121.2479 | 0.050354 | 0.12817 | -0.28839 | 0.2243 | 121.1975 | -0.28839 | -0.073242 | -120.8817 | 0.24261 | 121.4584 | -120.932 | -0.07782 | 0.21515 | 0.31586 | -0.07782 | 0.43488 | 0.26093 | 0.31128 | 0.24261 | 121.4081 | 0.33875 | -0.07782 | 0.31128 | 0.24261 | 0.33875 | 0.26093 | 121.4081 | -121.2662 | -121.2708
1500.375 | 121.1655 | -0.14648 | 120.9229 | 0.0103 | 0.017385 | 0.0030057 | 0.00046148 | -0.0058811 | 0.061568 | 0.091546 | -0.09613 | 0.16937 | -0.35706 | 121.1472 | -0.054932 | -0.018311 | -0.009155 | 0.11902 | 121.2296 | -0.34332 | -0.21057 | -120.7535 | 0.050354 | 121.2936 | -120.9778 | -0.19684 | 0.3067 | 0.26093 | 0.13733 | 0.2655 | 0.091552 | 0.31586 | 0.050354 | 121.376 | 0.12817 | -0.19684 | 0.31586 | 0.050354 | 0.12817 | 0.091552 | 121.376 | -121.2799 | -121.2662
1502.1406 | 121.0876 | -0.18768 | 120.9595 | -0.012589 | 0.014821 | 0.0068509 | -0.00060672 | -0.0048129 | 0.061355 | 0.090264 | -0.050354 | 0.1236 | -0.29755 | 121.1655 | 0.004578 | 0.054932 | -0.18768 | 0.17853 | 121.1929 | -0.32501 | -0.10986 | -120.8359 | 0.13733 | 121.3531 | -120.9549 | -0.13733 | 0.23346 | 0.24719 | 0 | 0.36621 | 0.19226 | 0.31128 | 0.13733 | 121.3806 | 0.24261 | -0.13733 | 0.31128 | 0.13733 | 0.24261 | 0.19226 | 121.3806 | -121.257 | -121.2845
1503.9062 | 121.0464 | -0.18768 | 120.9137 | -0.012589 | 0.017385 | 0.0047147 | -0.0010339 | -0.0073765 | 0.062637 | 0.091332 | 0 | 0.11444 | -0.31128 | 121.2158 | 0.009155 | 0.059509 | -0.14648 | 0.20599 | 121.225 | -0.33417 | -0.1236 | -120.7993 | 0.18768 | 121.4035 | -120.9045 | -0.14648 | 0.31128 | 0.31128 | 0.041199 | 0.39368 | 0.19684 | 0.30212 | 0.18768 | 121.4127 | 0.24719 | -0.14648 | 0.30212 | 0.18768 | 0.24719 | 0.19684 | 121.4127 | -121.225 | -121.2479
1505.6094 | 120.9961 | -0.14191 | 120.813 | 0.0026703 | 0.016317 | 0.0040737 | 0.0025977 | 0.00052773 | -0.0044413 | 0.034936 | -0.045776 | 0.14648 | -0.33417 | 121.0281 | 120.1035 | 0.65002 | -0.073242 | 0.16479 | 121.1105 | -0.32044 | -0.19226 | -120.6665 | 0.096131 | 121.17 | -0.70953 | -0.17853 | 0.29755 | 0.28839 | 0.068665 | 0.3067 | 120.2454 | 0.28839 | 0.096131 | 121.2524 | 0.79193 | -0.17853 | 0.28839 | 0.096131 | 0.79193 | 120.2454 | 121.2524 | -121.1472 | -121.1334
1507.375 | 121.0098 | -0.19684 | 120.8771 | -0.012589 | 0.018453 | 0.0053555 | 0.0011023 | -0.00011327 | -0.0035867 | 0.036218 | -0.022888 | 0.11444 | -0.31586 | 121.1105 | 120.1813 | 0.94757 | -0.19226 | 0.16937 | 121.1517 | -0.32044 | -0.11902 | -120.7626 | 0.17395 | 121.3074 | -0.6958 | -0.1236 | 0.27466 | 0.29297 | 0.004577 | 0.36621 | 120.3781 | 0.31128 | 0.17395 | 121.3486 | 1.1444 | -0.1236 | 0.31128 | 0.17395 | 1.1444 | 120.3781 | 121.3486 | -121.1929 | -121.1975
1509.0781 | 121.1014 | -0.12817 | 120.8633 | -0.012589 | 0.016744 | 0.0083463 | 0.0055885 | -0.0043857 | -0.0044413 | 0.03515 | -0.10529 | 0.15564 | -0.35248 | 121.0922 | 120.1538 | 0.54932 | -0.041199 | 0.09613 | 121.2204 | -0.35248 | -0.2243 | -120.7077 | 0.022888 | 121.2204 | -0.70953 | -0.2243 | 0.35706 | 0.24719 | 0.086975 | 0.2243 | 120.282 | 0.28381 | 0.022888 | 121.3486 | 0.67749 | -0.2243 | 0.28381 | 0.022888 | 0.67749 | 120.282 | 121.3486 | -121.2158 | -121.2158
1510.8438 | 121.106 | -0.14191 | 120.9229 | 0.0103 | 0.016317 | 0.0034329 | 0.0032385 | -0.0037449 | -0.0048685 | 0.036218 | -0.082397 | 0.14191 | -0.3479 | 121.1243 | 120.195 | 0.59052 | -0.054932 | 0.13275 | 121.2204 | -0.32501 | -0.20599 | -120.7809 | 0.05951 | 121.2662 | -0.72785 | -0.18311 | 0.29755 | 0.2655 | 0.086975 | 0.27466 | 120.3369 | 0.28381 | 0.05951 | 121.3623 | 0.73242 | -0.18311 | 0.28381 | 0.05951 | 0.73242 | 120.3369 | 121.3623 | -121.2708 | -121.2479
1512.5938 | 121.0556 | -0.18768 | 120.9366 | -0.020218 | 0.01653 | 0.0066373 | 0.0034521 | -0.0048129 | -0.0031595 | 0.036004 | -0.041199 | 0.11444 | -0.27466 | 121.1838 | 120.2408 | 0.56305 | -0.20142 | 0.16022 | 121.2067 | -0.31586 | -0.086975 | -120.8221 | 0.14648 | 121.3715 | -0.6958 | -0.12817 | 0.27008 | 0.23346 | -0.013733 | 0.3479 | 120.4285 | 0.30212 | 0.14648 | 121.3943 | 0.75073 | -0.12817 | 0.30212 | 0.14648 | 0.75073 | 120.4285 | 121.3943 | -121.2112 | -121.2524
1514.3438 | 121.1288 | -0.14191 | 120.9229 | -0.0049592 | 0.014821 | 0.0042875 | 0.0066565 | -0.0067355 | -0.0070047 | 0.037286 | -0.11444 | 0.1236 | -0.34332 | 121.1472 | 120.2087 | 0.47607 | -0.045776 | 0.10071 | 121.2524 | -0.32501 | -0.20142 | -120.7993 | 0.027466 | 121.2891 | -0.71411 | -0.18311 | 0.32959 | 0.22888 | 0.096131 | 0.24262 | 120.3506 | 0.2655 | 0.027466 | 121.3943 | 0.61798 | -0.18311 | 0.2655 | 0.027466 | 0.61798 | 120.3506 | 121.3943 | -121.2662 | -121.2479
1516.0938 | 121.1609 | -0.13733 | 120.9412 | 0.0103 | 0.019094 | 0.00065592 | 0.0068701 | -0.0058811 | -0.0067911 | 0.036645 | -0.11444 | 0.15106 | -0.32501 | 121.1563 | 120.2225 | 0.49439 | -0.036621 | 0.10529 | 121.2708 | -0.36163 | -0.18768 | -120.7901 | 0.022888 | 121.2936 | -0.71869 | -0.2243 | 0.32959 | 0.21057 | 0.10071 | 0.24262 | 120.3598 | 0.28839 | 0.022888 | 121.4081 | 0.63171 | -0.2243 | 0.28839 | 0.022888 | 0.63171 | 120.3598 | 121.4081 | -121.2662 | -121.3028
1517.8594 | 121.1426 | -0.14648 | 120.9412 | 0.0026703 | 0.018666 | 0.0059963 | 0.012424 | -0.0035313 | -0.0067911 | 0.038781 | -0.045776 | 0.14191 | -0.34332 | 121.2021 | 120.2362 | 0.52643 | -0.11902 | 0.11444 | 121.2982 | -0.33875 | -0.19684 | -120.7993 | 0.10071 | 121.3486 | -0.70496 | -0.19226 | 0.35706 | 0.29755 | 0.027465 | 0.26093 | 120.3827 | 0.28839 | 0.10071 | 121.4447 | 0.67291 | -0.19226 | 0.28839 | 0.10071 | 0.67291 | 120.3827 | 121.4447 | -121.2845 | -121.2799
1519.5938 | 121.1151 | -0.17853 | 121.0236 | -0.0049592 | 0.016317 | 0.0023647 | 0.0021705 | -0.0069491 | -0.0031595 | 0.037927 | -0.045776 | 0.14191 | -0.3067 | 121.2158 | 120.3186 | 0.56305 | -0.17395 | 0.16022 | 121.2158 | -0.31586 | -0.12817 | -120.8817 | 0.13275 | 121.3943 | -0.70496 | -0.13733 | 0.19226 | 0.26093 | 0.004578 | 0.33874 | 120.4971 | 0.32044 | 0.13275 | 121.3943 | 0.74158 | -0.13733 | 0.32044 | 0.13275 | 0.74158 | 120.4971 | 121.3943 | -121.3303 | -121.3394
1521.3594 | 121.0693 | -0.19684 | 121.0098 | 0.0026703 | 0.01653 | 0.0017239 | 0.0017431 | -0.0045993 | -0.0038003 | 0.037072 | 0.004578 | 0.10529 | -0.28839 | 121.3028 | 120.3964 | 0.67291 | -0.25177 | 0.2655 | 121.2479 | -0.31128 | -0.091553 | -120.9045 | 0.20142 | 121.4996 | -0.6134 | -0.11444 | 0.23804 | 0.29297 | -0.054932 | 0.46234 | 120.5933 | 0.30212 | 0.20142 | 121.4447 | 0.86975 | -0.11444 | 0.30212 | 0.20142 | 0.86975 | 120.5933 | 121.4447 | -121.2982 | -121.3211
1523.0625 | 121.1288 | -0.19684 | 121.019 | 0.0026703 | 0.016317 | 0.0079189 | 0.0066565 | -0.0060947 | -0.0046549 | 0.037713 | -0.027466 | 0.11444 | -0.29297 | 121.2387 | 120.3232 | 0.52643 | -0.22888 | 0.17395 | 121.2799 | -0.31128 | -0.096131 | -120.9045 | 0.16937 | 121.4355 | -0.6958 | -0.11444 | 0.26093 | 0.2655 | -0.032044 | 0.37079 | 120.52 | 0.31128 | 0.16937 | 121.4767 | 0.72327 | -0.11444 | 0.31128 | 0.16937 | 0.72327 | 120.52 | 121.4767 | -121.312 | -121.3303
1524.7969 | 121.138 | -0.16022 | 121.019 | 0.0026703 | 0.015889 | 0.0066373 | 0.0053747 | -0.0058811 | -0.0078591 | 0.037072 | -0.050354 | 0.14191 | -0.3067 | 121.2524 | 120.3232 | 0.54932 | -0.10071 | 0.15106 | 121.344 | -0.34332 | -0.14648 | -120.8771 | 0.10986 | 121.4127 | -0.6958 | -0.18311 | 0.32501 | 0.25635 | 0.059509 | 0.31128 | 120.4834 | 0.30212 | 0.10986 | 121.5042 | 0.70953 | -0.18311 | 0.30212 | 0.10986 | 0.70953 | 120.4834 | 121.5042 | -121.3257 | -121.3623
1526.5469 | 121.1517 | -0.18768 | 121.019 | -0.012589 | 0.014821 | 0.0045011 | 0.0051611 | -0.0058811 | -0.0038003 | 0.038995 | -0.036621 | 0.1236 | -0.32501 | 121.257 | 120.3461 | 0.43488 | -0.1831 | 0.16479 | 121.2845 | -0.31586 | -0.13733 | -120.8954 | 0.15106 | 121.4447 | -0.67291 | -0.12817 | 0.2655 | 0.28839 | 0.004578 | 0.35248 | 120.5338 | 0.31128 | 0.15106 | 121.4722 | 0.62256 | -0.12817 | 0.31128 | 0.15106 | 0.62256 | 120.5338 | 121.4722 | -121.344 | -121.3348
1528.2344 | 121.1975 | -0.13733 | 121.0098 | 0.0103 | 0.018239 | 0.0068509 | 0.010502 | -0.0039585 | -0.0067911 | 0.037927 | -0.050354 | 0.13733 | -0.34332 | 121.2845 | 120.3369 | 0.49896 | -0.10529 | 0.13275 | 121.3577 | -0.32501 | -0.20599 | -120.8725 | 0.086975 | 121.4218 | -0.67291 | -0.18768 | 0.3479 | 0.29297 | 0.032043 | 0.27008 | 120.4742 | 0.27466 | 0.086975 | 121.4951 | 0.63629 | -0.18768 | 0.27466 | 0.086975 | 0.63629 | 120.4742 | 121.4951 | -121.3531 | -121.3348
1529.9844 | 121.2296 | -0.13733 | 121.0098 | 0.0026703 | 0.020162 | 0.0045011 | 0.0070837 | -0.0052401 | -0.0063639 | 0.038995 | -0.091553 | 0.14191 | -0.33417 | 121.2433 | 120.2957 | 0.54932 | -0.054932 | 0.10529 | 121.376 | -0.3479 | -0.19684 | -120.8679 | 0.045776 | 121.3806 | -0.71411 | -0.21057 | 0.36621 | 0.24261 | 0.082397 | 0.24262 | 120.433 | 0.27924 | 0.045776 | 121.5134 | 0.68665 | -0.21057 | 0.27924 | 0.045776 | 0.68665 | 120.433 | 121.5134 | -121.344 | -121.3577
1531.7344 | 121.2524 | -0.14648 | 121.0327 | 0.017929 | 0.017598 | -0.00019868 | 0.0081519 | -0.0045993 | -0.0063639 | 0.037927 | -0.10986 | 0.15106 | -0.32501 | 121.2616 | 120.3049 | 0.68665 | -0.10071 | 0.068665 | 121.3577 | -0.32959 | -0.17853 | -120.8817 | 0.036621 | 121.4081 | -0.72784 | -0.18311 | 0.32501 | 0.21515 | 0.045776 | 0.21515 | 120.4514 | 0.29755 | 0.036621 | 121.5042 | 0.83313 | -0.18311 | 0.29755 | 0.036621 | 0.83313 | 120.4514 | 121.5042 | -121.3577 | -121.3623
1533.4375 | 121.2982 | -0.1236 | 121.051 | -0.0049592 | 0.017812 | 0.01091 | 0.0013159 | 0.0026639 | -0.0038003 | 0.0281 | -0.073242 | 0.14191 | -0.3067 | 121.2891 | 120.3323 | 0.65002 | -0.17853 | 0.11444 | 121.3531 | -0.29755 | -0.18311 | -120.9091 | 0.050354 | 121.4127 | -0.71869 | -0.17395 | 0.30212 | 0.23346 | -0.054932 | 0.23804 | 120.4559 | 0.2655 | 0.050354 | 121.4767 | 0.77362 | -0.17395 | 0.2655 | 0.050354 | 0.77362 | 120.4559 | 121.4767 | -121.3577 | -121.3486
1535.1406 | 121.1014 | -0.14191 | 121.0831 | 0.0026703 | 0.018239 | -0.0034031 | -0.0055199 | -0.0035313 | -0.0044413 | 0.037713 | -0.041199 | 0.11444 | -0.3067 | 121.3303 | 120.4193 | 0.74158 | -0.23804 | 0.14648 | 121.3531 | -0.27466 | -0.16479 | -120.9686 | 0.10071 | 121.4722 | -0.66376 | -0.13275 | 0.27008 | 0.2655 | -0.09613 | 0.28839 | 120.5612 | 0.25635 | 0.10071 | 121.4951 | 0.88348 | -0.13275 | 0.25635 | 0.10071 | 0.88348 | 120.5612 | 121.4951 | -121.3898 | -121.3577
1536.8906 | 121.3028 | -0.15106 | 121.0602 | -0.0049592 | 0.017812 | 0.0062101 | 0.0087927 | -0.0035313 | -0.0072183 | 0.039636 | -0.10986 | 0.1236 | -0.33875 | 121.2662 | 120.3415 | 0.64087 | -0.09613 | 0.054932 | 121.431 | -0.34332 | -0.18768 | -120.9366 | 0.041199 | 121.4172 | -0.71869 | -0.19226 | 0.37079 | 0.22888 | 0.054932 | 0.20599 | 120.4926 | 0.27466 | 0.041199 | 121.582 | 0.79193 | -0.19226 | 0.27466 | 0.041199 | 0.79193 | 120.4926 | 121.582 | -121.3989 | -121.4035
1538.6406 | 121.2982 | -0.14648 | 121.0831 | 0.0103 | 0.019734 | 0.0055691 | 0.0068701 | -0.0033175 | -0.0055093 | 0.04049 | -0.091553 | 0.14648 | -0.3479 | 121.312 | 120.3598 | 0.77362 | -0.050354 | 0.1236 | 121.4264 | -0.32501 | -0.20142 | -120.9366 | 0.054931 | 121.4584 | -0.72327 | -0.17853 | 0.34332 | 0.25635 | 0.09613 | 0.27008 | 120.5063 | 0.29297 | 0.054931 | 121.5729 | 0.9201 | -0.17853 | 0.29297 | 0.054931 | 0.9201 | 120.5063 | 121.5729 | -121.431 | -121.4081
1540.3281 | 121.1655 | -0.12817 | 121.1014 | -0.012589 | 0.017812 | 0.0062101 | 0.0025977 | -0.0035313 | -0.0048685 | 0.036859 | 0 | 0.082397 | -0.27008 | 121.3806 | 120.4376 | 0.84686 | -0.2655 | 0.21515 | 121.3165 | -0.27466 | -0.14191 | -121.019 | 0.12817 | 121.5088 | -0.66376 | -0.14648 | 0.21515 | 0.27008 | -0.13733 | 0.34332 | 120.5658 | 0.21057 | 0.12817 | 121.4447 | 0.97504 | -0.14648 | 0.21057 | 0.12817 | 0.97504 | 120.5658 | 121.4447 | -121.3715 | -121.376
1542.0156 | 121.3028 | -0.16022 | 121.1014 | 0.0103 | 0.01888 | 0.0070645 | 0.0090063 | -0.0039585 | -0.0070047 | 0.041772 | -0.073242 | 0.14648 | -0.32959 | 121.2845 | 120.3369 | 0.737 | -0.086975 | 0.082397 | 121.4218 | -0.33417 | -0.16937 | -120.9549 | 0.086975 | 121.4447 | -0.76447 | -0.17395 | 0.32044 | 0.25635 | 0.073242 | 0.24261 | 120.4971 | 0.3067 | 0.086975 | 121.582 | 0.89722 | -0.17395 | 0.3067 | 0.086975 | 0.89722 | 120.4971 | 121.582 | -121.431 | -121.4355
1543.7812 | 121.2936 | -0.14191 | 121.0693 | 0.0103 | 0.01888 | 0.0079189 | 0.0064429 | -0.0028903 | -0.0065775 | 0.040277 | -0.091553 | 0.1236 | -0.33417 | 121.3394 | 120.3918 | 0.8194 | -0.059509 | 0.12817 | 121.4447 | -0.32501 | -0.19226 | -120.9457 | 0.050354 | 121.4813 | -0.67749 | -0.18311 | 0.37537 | 0.24261 | 0.082398 | 0.27008 | 120.5338 | 0.2655 | 0.050354 | 121.5866 | 0.9613 | -0.18311 | 0.2655 | 0.050354 | 0.9613 | 120.5338 | 121.5866 | -121.4035 | -121.3943
1545.4688 | 121.1838 | -0.20599 | 121.1288 | 0.0026703 | 0.015889 | 0.0051419 | 0.0017431 | -0.0037449 | -0.0046549 | 0.039208 | 0.013733 | 0.10986 | -0.30212 | 121.4264 | 120.5017 | 0.87433 | -0.20142 | 0.25177 | 121.3806 | -0.29297 | -0.09613 | -121.019 | 0.21973 | 121.6324 | -0.62714 | -0.086975 | 0.25177 | 0.31586 | 0.004578 | 0.45776 | 120.7077 | 0.31586 | 0.21973 | 121.5866 | 1.0803 | -0.086975 | 0.31586 | 0.21973 | 1.0803 | 120.7077 | 121.5866 | -121.431 | -121.4218
1547.2188 | 121.2936 | -0.16479 | 121.1197 | -0.0049592 | 0.016957 | 0.0059963 | 0.0092199 | -0.0043857 | -0.0067911 | 0.041131 | -0.064087 | 0.13733 | -0.34332 | 121.3898 | 120.4147 | 0.80566 | -0.10071 | 0.13733 | 121.4493 | -0.32501 | -0.17853 | -120.9824 | 0.10071 | 121.5546 | -0.70496 | -0.16022 | 0.32959 | 0.27924 | 0.064087 | 0.30212 | 120.5795 | 0.30212 | 0.10071 | 121.6141 | 0.97046 | -0.16022 | 0.30212 | 0.10071 | 0.97046 | 120.5795 | 121.6141 | -121.463 | -121.4447
1548.9688 | 121.2296 | -0.1831 | 121.106 | -0.012589 | 0.018239 | 0.0023647 | 0.0028113 | -0.0080173 | -0.0063639 | 0.038781 | 0 | 0.1236 | -0.28839 | 121.4172 | 120.4605 | 0.85144 | -0.14648 | 0.19684 | 121.4218 | -0.32501 | -0.10529 | -120.9824 | 0.1831 | 121.6003 | -0.64545 | -0.14191 | 0.31586 | 0.28839 | 0.036621 | 0.37994 | 120.6436 | 0.3067 | 0.1831 | 121.6049 | 1.0345 | -0.14191 | 0.3067 | 0.1831 | 1.0345 | 120.6436 | 121.6049 | -121.3943 | -121.431
1550.6406 | 121.2982 | -0.16479 | 121.106 | -0.012589 | 0.018239 | 0.0070645 | 0.0094337 | -0.0056675 | -0.0063639 | 0.041345 | -0.027466 | 0.1236 | -0.33417 | 121.3943 | 120.4514 | 0.89264 | -0.13275 | 0.12817 | 121.4813 | -0.32501 | -0.16937 | -120.9824 | 0.13733 | 121.5591 | -0.6546 | -0.16022 | 0.37537 | 0.3067 | 0.032044 | 0.29297 | 120.6162 | 0.28839 | 0.13733 | 121.6461 | 1.0574 | -0.16022 | 0.28839 | 0.13733 | 1.0574 | 120.6162 | 121.6461 | -121.4401 | -121.431
1552.3906 | 121.3257 | -0.16022 | 121.1243 | 0.0026703 | 0.020589 | 0.0068509 | 0.0083655 | -0.0013949 | -0.0065775 | 0.042199 | -0.07782 | 0.14191 | -0.32044 | 121.3623 | 120.4147 | 0.85144 | -0.16937 | 0.10986 | 121.4676 | -0.32501 | -0.16022 | -120.9824 | 0.082397 | 121.5225 | -0.70953 | -0.1648 | 0.34332 | 0.24262 | -0.009156 | 0.27008 | 120.575 | 0.30212 | 0.082397 | 121.6278 | 1.0117 | -0.1648 | 0.30212 | 0.082397 | 1.0117 | 120.575 | 121.6278 | -121.4447 | -121.4493
1554.1562 | 121.2204 | -0.19684 | 121.1472 | -0.012589 | 0.015248 | 0.0072781 | 0.0049475 | -0.0048129 | -0.0061503 | 0.041986 | 0.004578 | 0.10986 | -0.27924 | 121.463 | 120.5338 | 1.0208 | -0.21515 | 0.24719 | 121.4859 | -0.3067 | -0.082398 | -121.0373 | 0.20142 | 121.6599 | -0.6134 | -0.10986 | 0.33875 | 0.28381 | -0.018311 | 0.44403 | 120.7306 | 0.3067 | 0.20142 | 121.6827 | 1.2177 | -0.10986 | 0.3067 | 0.20142 | 1.2177 | 120.7306 | 121.6827 | -121.4264 | -121.4539
1555.9062 | 121.2479 | -0.1831 | 121.1884 | -0.0049592 | 0.012685 | 0.0062101 | 0.0047339 | -0.0050265 | -0.0050821 | 0.027673 | 0.009155 | 0.10071 | -0.28839 | 121.4493 | 120.5246 | 1.0162 | -0.26093 | 0.2243 | 121.4493 | -0.27924 | -0.10529 | -121.0876 | 0.19226 | 121.6324 | -0.66376 | -0.096131 | 0.26093 | 0.29755 | -0.07782 | 0.40741 | 120.7077 | 0.28381 | 0.19226 | 121.6324 | 1.1993 | -0.096131 | 0.28381 | 0.19226 | 1.1993 | 120.7077 | 121.6324 | -121.4767 | -121.4676
1557.5938 | 121.3394 | -0.14648 | 121.138 | 0.0026703 | 0.018239 | 0.0045011 | 0.0079383 | -0.00075407 | -0.0078591 | 0.029595 | -0.041199 | 0.14191 | -0.30212 | 121.4355 | 120.4834 | 1.0345 | -0.10529 | 0.17395 | 121.5225 | -0.31586 | -0.15564 | -120.9961 | 0.10529 | 121.582 | -0.6546 | -0.16937 | 0.38452 | 0.26093 | 0.041198 | 0.32043 | 120.6299 | 0.28839 | 0.10529 | 121.669 | 1.181 | -0.16937 | 0.28839 | 0.10529 | 1.181 | 120.6299 | 121.669 | -121.4401 | -121.4539
1559.3594 | 121.2936 | -0.15564 | 121.1929 | -0.0049592 | 0.01653 | 0.0027921 | 0.0036657 | -0.0024631 | -0.0048685 | 0.027673 | -0.036621 | 0.12817 | -0.28381 | 121.4447 | 120.5154 | 1.0162 | -0.19684 | 0.20142 | 121.5042 | -0.3067 | -0.12817 | -121.0648 | 0.11902 | 121.6003 | -0.67749 | -0.15106 | 0.31128 | 0.24719 | -0.041198 | 0.35706 | 120.6711 | 0.28381 | 0.11902 | 121.6599 | 1.1719 | -0.15106 | 0.28381 | 0.11902 | 1.1719 | 120.6711 | 121.6599 | -121.4767 | -121.4996
1561.0625 | 121.2845 | -0.17853 | 121.2158 | -0.0049592 | 0.016957 | 0.0053555 | 0.0055885 | -0.0043857 | -0.0040139 | 0.03045 | 0.013733 | 0.09613 | -0.27008 | 121.4905 | 120.5475 | 0.97961 | -0.24719 | 0.20599 | 121.4951 | -0.28839 | -0.091553 | -121.1197 | 0.19226 | 121.669 | -0.66833 | -0.10986 | 0.27924 | 0.28381 | -0.068664 | 0.38452 | 120.726 | 0.27466 | 0.19226 | 121.6736 | 1.1581 | -0.10986 | 0.27466 | 0.19226 | 1.1581 | 120.726 | 121.6736 | -121.4859 | -121.5042
1562.8125 | 121.3943 | -0.10986 | 121.1517 | -0.0049592 | 0.017598 | 0.0045011 | 0.0085791 | -0.0058811 | -0.0070047 | 0.029168 | -0.082397 | 0.15106 | -0.35706 | 121.4172 | 120.4468 | 0.97504 | -0.032043 | 0.11444 | 121.5363 | -0.32501 | -0.24719 | -121.0007 | 0.027466 | 121.5271 | -0.70496 | -0.21515 | 0.38452 | 0.27466 | 0.07782 | 0.2243 | 120.5566 | 0.26093 | 0.027466 | 121.6461 | 1.0849 | -0.21515 | 0.26093 | 0.027466 | 1.0849 | 120.5566 | 121.6461 | -121.5088 | -121.4767
1564.5625 | 121.3806 | -0.15106 | 121.1838 | -0.0049592 | 0.020803 | 0.0096279 | 0.0092199 | -0.0026767 | -0.0046549 | 0.027246 | -0.054932 | 0.14191 | -0.30212 | 121.4539 | 120.5017 | 0.95673 | -0.18768 | 0.14648 | 121.5225 | -0.3067 | -0.15106 | -121.0419 | 0.09613 | 121.6049 | -0.68207 | -0.15564 | 0.33874 | 0.24719 | -0.036621 | 0.29755 | 120.6528 | 0.29297 | 0.09613 | 121.6736 | 1.1078 | -0.15564 | 0.29297 | 0.09613 | 1.1078 | 120.6528 | 121.6736 | -121.4859 | -121.4905
1566.3125 | 121.3669 | -0.15564 | 121.1838 | 0.0026703 | 0.016103 | 0.0032193 | 0.0062293 | -0.0037449 | -0.0074319 | 0.027459 | -0.064087 | 0.15106 | -0.32501 | 121.4676 | 120.5154 | 1.0391 | -0.082397 | 0.16022 | 121.5225 | -0.32959 | -0.16937 | -121.0327 | 0.091553 | 121.6232 | -0.66834 | -0.17395 | 0.33874 | 0.26093 | 0.073243 | 0.31586 | 120.6711 | 0.3067 | 0.091553 | 121.6782 | 1.1948 | -0.17395 | 0.3067 | 0.091553 | 1.1948 | 120.6711 | 121.6782 | -121.5088 | -121.5134
1568 | 121.4172 | -0.13275 | 121.1929 | -0.012589 | 0.017171 | 0.0062101 | 0.0043067 | -0.0033175 | -0.0063639 | 0.029809 | -0.10071 | 0.15106 | -0.3479 | 121.4172 | 120.488 | 0.99335 | -0.032043 | 0.10986 | 121.5729 | -0.32959 | -0.21515 | -121.0419 | 0.032043 | 121.55 | -0.70496 | -0.19684 | 0.37994 | 0.24719 | 0.10071 | 0.24261 | 120.6207 | 0.28381 | 0.032043 | 121.7056 | 1.1261 | -0.19684 | 0.28381 | 0.032043 | 1.1261 | 120.6207 | 121.7056 | -121.5408 | -121.5225
1569.75 | 121.312 | -0.19226 | 121.2387 | 0.0026703 | 0.013967 | 0.0053555 | 0.0051611 | -0.0039585 | -0.0076455 | 0.027673 | 0.013733 | 0.086975 | -0.28381 | 121.5363 | 120.575 | 1.03 | -0.27466 | 0.2243 | 121.5225 | -0.25635 | -0.091552 | -121.1517 | 0.20599 | 121.7285 | -0.66376 | -0.064087 | 0.28381 | 0.29755 | -0.082397 | 0.41656 | 120.7672 | 0.27924 | 0.20599 | 121.7148 | 1.2222 | -0.064087 | 0.27924 | 0.20599 | 1.2222 | 120.7672 | 121.7148 | -121.5225 | -121.4951
1571.5 | 121.4355 | -0.15106 | 121.2296 | 0.0026703 | 0.015462 | 0.0062101 | 0.0075111 | -0.0056675 | -0.0067911 | 0.029168 | -0.086975 | 0.14191 | -0.32044 | 121.4355 | 120.488 | 0.95215 | -0.13733 | 0.086975 | 121.5637 | -0.32959 | -0.16937 | -121.0876 | 0.064087 | 121.5866 | -0.74158 | -0.17853 | 0.33417 | 0.23346 | 0.013733 | 0.23804 | 120.639 | 0.29297 | 0.064087 | 121.7148 | 1.1032 | -0.17853 | 0.29297 | 0.064087 | 1.1032 | 120.639 | 121.7148 | -121.55 | -121.5591
1573.1875 | 121.3348 | -0.1831 | 121.257 | -0.0049592 | 0.015889 | 0.0092007 | 0.0038795 | -0.0065219 | -0.0027323 | 0.029595 | -0.013733 | 0.1236 | -0.2655 | 121.5591 | 120.6436 | 1.0757 | -0.21057 | 0.23346 | 121.4996 | -0.3067 | -0.082398 | -121.1334 | 0.16937 | 121.7422 | -0.6134 | -0.1236 | 0.24262 | 0.25177 | -0.027466 | 0.41656 | 120.8267 | 0.3067 | 0.16937 | 121.6827 | 1.2589 | -0.1236 | 0.3067 | 0.16937 | 1.2589 | 120.8267 | 121.6827 | -121.5225 | -121.5637
1574.9375 | 120.9 | -0.16479 | 120.8725 | -0.0049592 | 0.014394 | 0.0051419 | 0.0013159 | -0.0045993 | -0.0038003 | 0.029595 | 0.004578 | 0.10529 | -0.28839 | 121.1288 | 120.2042 | 1.0529 | -0.22888 | 0.26093 | 121.1197 | -0.28381 | -0.1236 | -120.7672 | 0.16937 | 121.2936 | -0.66833 | -0.11902 | 0.24719 | 0.29297 | -0.064087 | 0.42572 | 120.369 | 0.27008 | 0.16937 | 121.2845 | 1.2177 | -0.11902 | 0.27008 | 0.16937 | 1.2177 | 120.369 | 121.2845 | -121.1609 | -121.1563
1576.625 | 121.2067 | -0.15106 | 121.0648 | -0.0049592 | 0.01653 | 0.0055691 | 0.0087927 | -0.0024631 | -0.0067911 | 0.028314 | -0.004578 | 0.10529 | -0.31586 | 121.3165 | 120.3644 | 1.0071 | -0.11444 | 0.15564 | 121.3806 | -0.31128 | -0.16479 | -120.9595 | 0.14648 | 121.4676 | -0.70038 | -0.16022 | 0.31586 | 0.31128 | 0.036621 | 0.3067 | 120.5154 | 0.25635 | 0.14648 | 121.5317 | 1.1581 | -0.16022 | 0.25635 | 0.14648 | 1.1581 | 120.5154 | 121.5317 | -121.3806 | -121.376
1578.3906 | 121.312 | -0.15564 | 121.106 | -0.0049592 | 0.017812 | 0.0038601 | 0.010929 | -0.0041721 | -0.0044413 | 0.028741 | -0.045776 | 0.14648 | -0.32959 | 121.344 | 120.3827 | 0.98419 | -0.10071 | 0.086975 | 121.4676 | -0.30212 | -0.17395 | -120.9595 | 0.10986 | 121.4996 | -0.72327 | -0.14648 | 0.36163 | 0.28381 | 0.054932 | 0.24261 | 120.5383 | 0.30212 | 0.10986 | 121.6232 | 1.1398 | -0.14648 | 0.30212 | 0.10986 | 1.1398 | 120.5383 | 121.6232 | -121.4355 | -121.4081
1580.0781 | 121.3074 | -0.13733 | 121.1334 | -0.0049592 | 0.018239 | 0.0025785 | 0.0083655 | -0.0043857 | -0.0059365 | 0.028741 | -0.027466 | 0.14648 | -0.31586 | 121.4355 | 120.4834 | 1.0712 | -0.11902 | 0.16022 | 121.4767 | -0.29755 | -0.17853 | -120.9869 | 0.10986 | 121.5729 | -0.65002 | -0.16022 | 0.34332 | 0.28839 | 0.01831 | 0.29755 | 120.6207 | 0.28381 | 0.10986 | 121.6141 | 1.2085 | -0.16022 | 0.28381 | 0.10986 | 1.2085 | 120.6207 | 121.6141 | -121.4493 | -121.431
1581.8281 | 121.3257 | -0.14191 | 121.1929 | -0.020218 | 0.018453 | 0.0055691 | 0.0036657 | -0.0050265 | -0.0040139 | 0.03045 | -0.036621 | 0.12817 | -0.3067 | 121.431 | 120.5109 | 1.0529 | -0.07782 | 0.16937 | 121.5088 | -0.32501 | -0.16479 | -121.0648 | 0.10529 | 121.5729 | -0.68207 | -0.18311 | 0.31586 | 0.27008 | 0.064087 | 0.31128 | 120.6528 | 0.27008 | 0.10529 | 121.6507 | 1.1948 | -0.18311 | 0.27008 | 0.10529 | 1.1948 | 120.6528 | 121.6507 | -121.4996 | -121.5179
1583.5156 | 121.3531 | -0.15106 | 121.2021 | 0.0103 | 0.017598 | 0.0045011 | 0.010715 | -0.0041721 | -0.0057229 | 0.029168 | -0.032043 | 0.15106 | -0.3067 | 121.4676 | 120.5246 | 1.0757 | -0.1236 | 0.16022 | 121.5363 | -0.32044 | -0.15564 | -121.051 | 0.11902 | 121.6187 | -0.67749 | -0.16937 | 0.33417 | 0.27466 | 0.027466 | 0.31128 | 120.6757 | 0.30212 | 0.11902 | 121.6873 | 1.2268 | -0.16937 | 0.30212 | 0.11902 | 1.2268 | 120.6757 | 121.6873 | -121.5088 | -121.5225
1585.2656 | 121.3028 | -0.16479 | 121.2753 | 0.0026703 | 0.015676 | 0.0019375 | 0.0017431 | -0.0048129 | -0.0023049 | 0.027673 | 0.009155 | 0.10986 | -0.28839 | 121.5546 | 120.6299 | 1.1307 | -0.2243 | 0.24261 | 121.5729 | -0.27924 | -0.1236 | -121.1655 | 0.17395 | 121.7194 | -0.64545 | -0.11444 | 0.29755 | 0.29755 | -0.059509 | 0.40741 | 120.7947 | 0.27466 | 0.17395 | 121.7377 | 1.2955 | -0.11444 | 0.27466 | 0.17395 | 1.2955 | 120.7947 | 121.7377 | -121.5637 | -121.5546
1587.0156 | 121.4401 | -0.12817 | 121.2341 | 0.0103 | 0.019948 | 0.0083463 | 0.0083655 | -0.0039585 | -0.0059365 | 0.027673 | -0.059509 | 0.15106 | -0.31586 | 121.5225 | 120.5704 | 1.0986 | -0.10071 | 0.14191 | 121.5729 | -0.32501 | -0.18768 | -121.0831 | 0.068665 | 121.6507 | -0.66376 | -0.19684 | 0.33874 | 0.25635 | 0.027466 | 0.27008 | 120.6985 | 0.27924 | 0.068665 | 121.701 | 1.2268 | -0.19684 | 0.27924 | 0.068665 | 1.2268 | 120.6985 | 121.701 | -121.55 | -121.5591
1588.7031 | 120.5063 | -46.0876 | 74.7528 | 0.0026703 | 0.019521 | 0.0077053 | 0.0011023 | -0.0039585 | -0.0023049 | 0.0084468 | 0.054932 | 0.16479 | -46.1929 | 75.0961 | 74.4095 | 0.48065 | -0.18768 | 0.28839 | 74.968 | -46.2158 | -0.10529 | -74.588 | 46.1426 | 121.1838 | -0.34332 | -0.12817 | 0.21515 | 46.2479 | 45.9 | 46.376 | 120.4971 | 46.2524 | 46.1426 | 121.0556 | 46.5683 | -0.12817 | 46.2524 | 46.1426 | 46.5683 | 120.4971 | 121.0556 | -120.9457 | -120.9686
1590.4688 | 121.1975 | -45.7718 | 75.4074 | 0.0026703 | 0.01653 | 0.0051419 | 0.0036657 | -0.0054539 | -0.0029459 | 0.005456 | 0.013733 | 0.16022 | -45.8862 | 75.6866 | 75.0046 | 0.48065 | -0.14648 | 0.25177 | 75.6042 | -45.9366 | -0.11444 | -75.2472 | 45.7855 | 121.4584 | -0.40283 | -0.16479 | 0.19684 | 45.9 | 45.6253 | 46.0236 | 120.7764 | 45.932 | 45.7855 | 121.376 | 46.2524 | -0.16479 | 45.932 | 45.7855 | 46.2524 | 120.7764 | 121.376 | -121.2936 | -121.344
1592.1562 | 121.2433 | -45.6665 | 75.5493 | -0.0049592 | 0.015889 | 0.0051419 | 0.0055885 | -0.0058811 | -0.0031595 | 0.0067378 | 0.036621 | 0.16937 | -45.813 | 75.8606 | 75.1602 | 1.062 | -0.16937 | 0.27924 | 75.737 | -45.8176 | -0.14648 | -75.3799 | 45.7031 | 121.5271 | -0.3891 | -0.15106 | 0.18768 | 45.8496 | 45.4971 | 45.9457 | 120.8267 | 45.8359 | 45.7031 | 121.4035 | 46.7285 | -0.15106 | 45.8359 | 45.7031 | 46.7285 | 120.8267 | 121.4035 | -121.3623 | -121.3669
1593.9219 | 121.3669 | -45.4559 | 75.7233 | 0.0026703 | 0.021016 | 0.0066373 | 0.0083655 | -0.0037449 | -0.0046549 | 0.0073786 | -0.018311 | 0.1831 | -45.6802 | 75.9796 | 75.2747 | 1.4832 | -0.004578 | 0.15564 | 75.9796 | -45.726 | -0.2243 | -75.5402 | 45.4376 | 121.4355 | -0.44861 | -0.27008 | 0.25635 | 45.6619 | 45.4514 | 45.6116 | 120.7306 | 45.639 | 45.4376 | 121.4355 | 46.9391 | -0.27008 | 45.639 | 45.4376 | 46.9391 | 120.7306 | 121.4355 | -121.4035 | -121.4493
1595.6094 | 121.3577 | -121.1014 | 0.20599 | -0.0049592 | 0.017598 | 0.0077053 | 0.050022 | -0.0024631 | -0.0050821 | 0.0095148 | 0.10071 | 0.21973 | -121.3898 | 0.25177 | 0.11444 | -0.13275 | -0.13733 | 0.3067 | 0.32501 | -121.3669 | -0.28839 | 0.013733 | 121.2021 | 121.3531 | -0.091553 | -0.2655 | 0.11902 | 121.4905 | 120.9641 | 121.4081 | 121.2158 | 121.3211 | 121.2021 | 121.4264 | 120.9686 | -0.2655 | 121.3211 | 121.2021 | 120.9686 | 121.2158 | 121.4264 | -121.5958 | -121.5729
1597.3594 | 121.4539 | -121.0648 | 0.16022 | 0.0026703 | 0.016317 | 0.0087735 | 0.049595 | -0.0033175 | -0.0038003 | 0.008874 | 0.013733 | 0.25635 | -0.21515 | 0.14191 | 0.041199 | -0.13275 | 0.045776 | 0.22888 | 0.37079 | -121.4218 | 120.8496 | 0.096131 | 121.0785 | 121.2067 | -0.11902 | -0.35706 | 0.21057 | 0.22888 | 121.1105 | 121.2936 | 121.106 | 121.3211 | 121.0785 | 121.4355 | 120.932 | -0.35706 | 121.3211 | 121.0785 | 120.932 | 121.106 | 121.4355 | -0.37537 | -121.582
1599.0625 | 121.4859 | -121.0831 | 0.17853 | -0.012589 | 0.019307 | 0.014328 | 0.055149 | -0.0035313 | -0.0048685 | 0.0075922 | 0.027466 | 0.23804 | -0.20599 | 0.14191 | 0.050354 | -0.15564 | -0.041199 | 0.20599 | 0.35248 | -121.4584 | 120.8771 | 0.059509 | 121.1105 | 121.225 | -0.12817 | -0.37537 | 0.17395 | 0.23346 | 121.0419 | 121.2891 | 121.1334 | 121.3211 | 121.1105 | 121.4355 | 120.9274 | -0.37537 | 121.3211 | 121.1105 | 120.9274 | 121.1334 | 121.4355 | -0.38452 | -121.637
1600.75 | 121.376 | -121.1334 | 0.23346 | 0.0026703 | 0.017385 | 0.012192 | 0.051731 | -0.0043857 | -0.0031595 | 0.0093012 | 0.1236 | 0.21057 | -0.17853 | 0.26093 | 0.15564 | 0.009155 | -0.10986 | 0.36621 | 0.3067 | -121.4355 | 120.9549 | -0.022888 | 121.257 | 121.3943 | -0.077819 | -0.30212 | 0.073243 | 0.30212 | 121.0236 | 121.4996 | 121.2891 | 121.344 | 121.257 | 121.4401 | 121.1426 | -0.30212 | 121.344 | 121.257 | 121.1426 | 121.2891 | 121.4401 | -0.41199 | -121.669
1602.5 | 121.5225 | -121.17 | 0.18768 | 0.0026703 | 0.01653 | 0.010696 | 0.054935 | -0.0039585 | -0.0078591 | 0.010156 | 0.036621 | 0.24261 | -0.21973 | 0.13733 | 0.027466 | -0.1236 | 0.018311 | 0.19684 | 0.33875 | -121.4447 | 120.9503 | 0.054932 | 121.2067 | 121.3074 | -0.16022 | -0.27466 | 0.15106 | 0.25635 | 121.1884 | 121.3669 | 121.1975 | 121.4127 | 121.2067 | 121.5088 | 121.0464 | -0.27466 | 121.4127 | 121.2067 | 121.0464 | 121.1975 | 121.5088 | -0.40741 | -121.6324
1604.25 | 121.4355 | -121.1746 | 0.19226 | -0.0049592 | 0.018666 | 0.015823 | 0.049808 | -0.0063083 | -0.0044413 | 0.010583 | 0.068665 | 0.22888 | -0.17853 | 0.19684 | 0.086975 | -0.086975 | -0.091553 | 0.27924 | 0.32044 | -121.4767 | 120.9961 | 0.036621 | 121.2433 | 121.3715 | -0.10529 | -0.30212 | 0.12817 | 0.24719 | 121.0831 | 121.4539 | 121.2616 | 121.4035 | 121.2433 | 121.4951 | 121.0876 | -0.30212 | 121.4035 | 121.2433 | 121.0876 | 121.2616 | 121.4951 | -0.37079 | -121.669
1606 | 121.4493 | -121.1838 | 0.20599 | -0.012589 | 0.016103 | 0.013901 | 0.052799 | -0.0052401 | -0.0057229 | 0.008233 | 0.064087 | 0.21515 | -0.1831 | 0.16937 | 0.091553 | -0.073242 | -0.082397 | 0.28381 | 0.32044 | -121.4584 | 121.0007 | 0.009155 | 121.2479 | 121.3531 | -0.11444 | -0.27466 | 0.11444 | 0.24719 | 121.1014 | 121.4676 | 121.2753 | 121.3989 | 121.2479 | 121.5042 | 121.1105 | -0.27466 | 121.3989 | 121.2479 | 121.1105 | 121.2753 | 121.5042 | -0.3891 | -121.6644
1607.6719 | 121.5317 | -121.1792 | 0.16937 | 0.0026703 | 0.017171 | 0.012192 | 0.057926 | -0.0075901 | -0.0072183 | 0.0078058 | 0.018311 | 0.25177 | -0.21515 | 0.13733 | 0.045776 | -0.064087 | 0.07782 | 0.21973 | 0.35248 | -121.4859 | 120.9641 | 0.082397 | 121.1975 | 121.3165 | -0.1236 | -0.3067 | 0.18311 | 0.23346 | 121.257 | 121.3989 | 121.225 | 121.431 | 121.1975 | 121.5317 | 121.1151 | -0.3067 | 121.431 | 121.1975 | 121.1151 | 121.225 | 121.5317 | -0.38452 | -121.6553
1609.4375 | 121.4813 | -121.2204 | 0.21057 | -0.0049592 | 0.018239 | 0.01091 | 0.054508 | -0.0056675 | -0.0074319 | 0.009942 | 0.082397 | 0.21973 | -0.17395 | 0.19226 | 0.10071 | -0.091553 | -0.07782 | 0.28839 | 0.31586 | -121.5134 | 121.0464 | 0.009156 | 121.3028 | 121.4127 | -0.10986 | -0.29297 | 0.10529 | 0.25635 | 121.1426 | 121.5088 | 121.3211 | 121.4401 | 121.3028 | 121.5363 | 121.1288 | -0.29297 | 121.4401 | 121.3028 | 121.1288 | 121.3211 | 121.5363 | -0.38452 | -121.7239
1611.1875 | 121.5591 | -121.2341 | 0.16022 | -0.0049592 | 0.018453 | 0.013687 | 0.056858 | -0.0056675 | -0.0067911 | 0.0084468 | 0.009155 | 0.24261 | -0.21515 | 0.1236 | 0.041199 | -0.054932 | 0.082397 | 0.21973 | 0.33417 | -121.5637 | 121.019 | 0.082398 | 121.2433 | 121.3577 | -0.11902 | -0.32959 | 0.17395 | 0.2243 | 121.3165 | 121.4539 | 121.2753 | 121.4767 | 121.2433 | 121.5683 | 121.1792 | -0.32959 | 121.4767 | 121.2433 | 121.1792 | 121.2753 | 121.5683 | -0.37537 | -121.7239
1612.9375 | 121.4584 | -121.2662 | 0.20599 | -0.0049592 | 0.016103 | 0.01326 | 0.058353 | -0.0035313 | -0.0065775 | 0.008874 | 0.12817 | 0.20142 | -0.15106 | 0.24719 | 0.14191 | 0.041199 | -0.086975 | 0.36163 | 0.31128 | -121.5317 | 121.1151 | -0.004578 | 121.3943 | 121.5134 | -0.064087 | -0.2655 | 0.10528 | 0.27924 | 121.1792 | 121.6278 | 121.4081 | 121.4676 | 121.3943 | 121.5775 | 121.3074 | -0.2655 | 121.4676 | 121.3943 | 121.3074 | 121.4081 | 121.5775 | -0.35706 | -121.7377
1614.625 | 121.4584 | -121.2433 | 0.21057 | -0.0049592 | 0.016744 | 0.0087735 | 0.054722 | -0.0069491 | -0.0048685 | 0.008233 | 0.12817 | 0.21515 | -0.16479 | 0.28381 | 0.17853 | 0.11902 | -0.1236 | 0.37537 | 0.29297 | -121.5363 | 121.0785 | 0.004578 | 121.3715 | 121.5271 | -0.032043 | -0.29297 | 0.082398 | 0.29297 | 121.1197 | 121.6187 | 121.4218 | 121.4584 | 121.3715 | 121.5363 | 121.3623 | -0.29297 | 121.4584 | 121.3715 | 121.3623 | 121.4218 | 121.5363 | -0.37537 | -121.7468
1616.3594 | 121.5958 | -121.2341 | 0.16022 | -0.0049592 | 0.015462 | 0.013046 | 0.06348 | -0.0022495 | -0.0095681 | 0.0084468 | 0.041199 | 0.24261 | -0.2243 | 0.14648 | 0.013733 | 0.086975 | 0.018311 | 0.17395 | 0.33417 | -121.5591 | 121.0098 | 0.082398 | 121.2753 | 121.3806 | -0.14648 | -0.32501 | 0.17395 | 0.2655 | 121.2524 | 121.4081 | 121.2479 | 121.4767 | 121.2753 | 121.5683 | 121.3211 | -0.32501 | 121.4767 | 121.2753 | 121.3211 | 121.2479 | 121.5683 | -0.38452 | -121.7194
1618.1094 | 121.5637 | -121.2524 | 0.17853 | 0.0103 | 0.017812 | 0.0081327 | 0.062198 | -0.0031039 | -0.0076455 | 0.007165 | 0.091553 | 0.22888 | -0.20599 | 0.17853 | 0.07782 | 0.13733 | -0.018311 | 0.25177 | 0.32044 | -121.5729 | 121.0464 | 0.050354 | 121.344 | 121.431 | -0.10071 | -0.32043 | 0.14191 | 0.29755 | 121.2341 | 121.5042 | 121.3303 | 121.4813 | 121.344 | 121.5729 | 121.3898 | -0.32043 | 121.4813 | 121.344 | 121.3898 | 121.3303 | 121.5729 | -0.38452 | -121.7514
1619.8594 | 121.5591 | -121.2753 | 0.19226 | -0.012589 | 0.016744 | 0.010483 | 0.058353 | -0.0043857 | -0.0040139 | 0.0073786 | 0.064087 | 0.23346 | -0.19684 | 0.16479 | 0.059509 | 0.11902 | 0.041199 | 0.24719 | 0.33417 | -121.6232 | 121.0785 | 0.041198 | 121.3394 | 121.4401 | -0.13275 | -0.3479 | 0.14191 | 0.26093 | 121.3165 | 121.5225 | 121.3348 | 121.5088 | 121.3394 | 121.6095 | 121.3943 | -0.3479 | 121.5088 | 121.3394 | 121.3943 | 121.3348 | 121.6095 | -0.3891 | -121.8155
1621.5469 | 121.5179 | -121.2936 | 0.20142 | 0.0026703 | 0.015889 | 0.0070645 | 0.056431 | -0.0063083 | -0.0061503 | 0.0084468 | 0.1236 | 0.23346 | -0.16937 | 0.24719 | 0.15106 | 0.21515 | -0.091553 | 0.36621 | 0.29297 | -121.582 | 121.1243 | 0.032043 | 121.4172 | 121.5408 | -0.050354 | -0.28839 | 0.091553 | 0.29297 | 121.2021 | 121.6599 | 121.4447 | 121.5271 | 121.4172 | 121.5866 | 121.5088 | -0.28839 | 121.5271 | 121.4172 | 121.5088 | 121.4447 | 121.5866 | -0.37079 | -121.7834
1623.3125 | 121.5683 | -121.3211 | 0.18768 | -0.012589 | 0.017385 | 0.011123 | 0.056858 | -0.0048129 | -0.0038003 | 0.0090876 | 0.073242 | 0.21057 | -0.17395 | 0.17395 | 0.09613 | 0.16937 | -0.07782 | 0.28381 | 0.31128 | -121.6095 | 121.1472 | 0.022888 | 121.3943 | 121.4951 | -0.091553 | -0.28839 | 0.1236 | 0.24719 | 121.2433 | 121.6049 | 121.4172 | 121.5317 | 121.3943 | 121.6324 | 121.4905 | -0.28839 | 121.5317 | 121.3943 | 121.4905 | 121.4172 | 121.6324 | -0.36163 | -121.7972
1625.0781 | 121.6553 | -121.2845 | 0.16479 | 0.0026703 | 0.01888 | 0.0059963 | 0.061771 | -0.0050265 | -0.0070047 | 0.010583 | 0.013733 | 0.2655 | -0.21973 | 0.12817 | 0.027466 | 0.082397 | 0.07782 | 0.21057 | 0.3479 | -121.6507 | 121.0648 | 0.10071 | 121.2982 | 121.4127 | -0.13733 | -0.36621 | 0.1831 | 0.23346 | 121.3623 | 121.4951 | 121.312 | 121.55 | 121.2982 | 121.6324 | 121.3669 | -0.36621 | 121.55 | 121.2982 | 121.3669 | 121.312 | 121.6324 | -0.38452 | -121.8155
1626.8125 | 121.582 | -121.3394 | 0.20599 | 0.0026703 | 0.016957 | 0.0085599 | 0.066257 | -0.0052401 | -0.0052957 | 0.01101 | 0.07782 | 0.21973 | -0.17853 | 0.21515 | 0.10986 | 0.21057 | -0.14191 | 0.29297 | 0.29755 | -121.6049 | 121.1609 | 0.013733 | 121.4172 | 121.5546 | -0.096131 | -0.2655 | 0.091552 | 0.25635 | 121.1975 | 121.6324 | 121.4493 | 121.5591 | 121.4172 | 121.637 | 121.55 | -0.2655 | 121.5591 | 121.4172 | 121.55 | 121.4493 | 121.637 | -0.38452 | -121.8109
1628.5 | 121.5454 | -121.3165 | 0.20142 | -0.0049592 | 0.018025 | 0.0057827 | 0.059635 | -0.0058811 | -0.0033731 | 0.0075922 | 0.10071 | 0.21973 | -0.16937 | 0.2243 | 0.15106 | 0.21973 | -0.10071 | 0.3479 | 0.28381 | -121.6324 | 121.1472 | 0.018311 | 121.4172 | 121.5408 | -0.050354 | -0.31586 | 0.082397 | 0.27008 | 121.2158 | 121.6644 | 121.4676 | 121.5363 | 121.4172 | 121.6003 | 121.5363 | -0.31586 | 121.5363 | 121.4172 | 121.5363 | 121.4676 | 121.6003 | -0.37079 | -121.8338
1630.25 | 121.6187 | -121.3303 | 0.19684 | -0.0049592 | 0.017385 | 0.010269 | 0.063267 | -0.0069491 | -0.0059365 | 0.010797 | 0.064087 | 0.21973 | -0.16937 | 0.16479 | 0.086975 | 0.16937 | -0.073242 | 0.28381 | 0.29297 | -121.6415 | 121.1609 | 0.022889 | 121.3943 | 121.4951 | -0.10986 | -0.31128 | 0.096131 | 0.23346 | 121.257 | 121.6141 | 121.4172 | 121.55 | 121.3943 | 121.6232 | 121.4996 | -0.31128 | 121.55 | 121.3943 | 121.4996 | 121.4172 | 121.6232 | -0.36621 | -121.8384
1631.9375 | 121.6187 | -121.344 | 0.18768 | -0.012589 | 0.017385 | 0.01091 | 0.064335 | -0.0033175 | -0.0052957 | 0.0093012 | 0.073242 | 0.21057 | -0.1831 | 0.1831 | 0.07782 | 0.16479 | -0.086975 | 0.27924 | 0.31586 | -121.669 | 121.1609 | 0.022888 | 121.4172 | 121.5271 | -0.10986 | -0.32501 | 0.12817 | 0.25635 | 121.257 | 121.6232 | 121.4218 | 121.5546 | 121.4172 | 121.6599 | 121.5088 | -0.32501 | 121.5546 | 121.4172 | 121.5088 | 121.4218 | 121.6599 | -0.37079 | -121.8567
1633.6719 | 121.582 | -121.3623 | 0.19684 | -0.012589 | 0.018453 | 0.0068509 | 0.070316 | -0.0045993 | -0.0063639 | 0.009942 | 0.13733 | 0.19684 | -0.17395 | 0.25635 | 0.14648 | 0.22888 | -0.09613 | 0.36621 | 0.29755 | -121.6644 | 121.1884 | 0 | 121.4996 | 121.6187 | -0.050354 | -0.30212 | 0.10071 | 0.31128 | 121.2662 | 121.7285 | 121.5088 | 121.5591 | 121.4996 | 121.6599 | 121.5912 | -0.30212 | 121.5591 | 121.4996 | 121.5912 | 121.5088 | 121.6599 | -0.37079 | -121.8613
1635.4375 | 121.6278 | -121.3623 | 0.21515 | -0.0049592 | 0.016957 | 0.014541 | 0.065403 | -0.0037449 | -0.0070047 | 0.008874 | 0.10986 | 0.18768 | -0.19226 | 0.20599 | 0.11444 | 0.18768 | -0.10986 | 0.29297 | 0.29297 | -121.6782 | 121.17 | -0.027466 | 121.4722 | 121.5683 | -0.10071 | -0.31586 | 0.07782 | 0.30212 | 121.2524 | 121.6553 | 121.4767 | 121.55 | 121.4722 | 121.6553 | 121.55 | -0.31586 | 121.55 | 121.4722 | 121.55 | 121.4767 | 121.6553 | -0.40741 | -121.8933
1637.1875 | 121.669 | -121.3394 | 0.20599 | -0.0049592 | 0.019094 | 0.011337 | 0.15021 | -0.0043857 | -0.0063639 | 0.007165 | 0.032043 | 0.25177 | -0.20599 | 0.1831 | 0.07782 | 0.11444 | 0.018311 | 0.25177 | 0.31586 | -121.6599 | 121.1334 | 0.045776 | 121.3715 | 121.5225 | -0.12817 | -0.32043 | 0.10986 | 0.23804 | 121.3577 | 121.5912 | 121.4172 | 121.5912 | 121.3715 | 121.6553 | 121.4539 | -0.32043 | 121.5912 | 121.3715 | 121.4539 | 121.4172 | 121.6553 | -0.41199 | -121.8658
1638.9375 | 121.6049 | -121.3577 | 0.22888 | 0.0026703 | 0.016103 | 0.0089871 | 0.16004 | -0.0045993 | -0.0048685 | 0.008874 | 0.091553 | 0.21057 | -0.16937 | 0.2243 | 0.16479 | 0.21973 | -0.10529 | 0.33875 | 0.31586 | -121.6461 | 121.1884 | -0.018311 | 121.4493 | 121.582 | -0.064087 | -0.28839 | 0.086975 | 0.26093 | 121.2524 | 121.6965 | 121.5225 | 121.5683 | 121.4493 | 121.6736 | 121.5775 | -0.28839 | 121.5683 | 121.4493 | 121.5775 | 121.5225 | 121.6736 | -0.39826 | -121.875
1640.625 | 121.6965 | -121.3577 | 0.20599 | -0.0049592 | 0.017385 | 0.01091 | 0.16773 | -0.0052401 | -0.0074319 | 0.0090876 | 0.041199 | 0.25635 | -0.19684 | 0.15106 | 0.068665 | 0.13733 | -0.086975 | 0.23346 | 0.33417 | -121.6873 | 121.1609 | 0.050354 | 121.3989 | 121.5088 | -0.13733 | -0.32959 | 0.12817 | 0.23804 | 121.2708 | 121.5912 | 121.4264 | 121.6141 | 121.3989 | 121.6919 | 121.4951 | -0.32959 | 121.6141 | 121.3989 | 121.4951 | 121.4264 | 121.6919 | -0.40283 | -121.8933
1642.375 | 121.6232 | -121.3669 | 0.21973 | 0.0026703 | 0.018453 | 0.011551 | 0.16153 | -0.0082309 | -0.0074319 | 0.0086604 | 0.12817 | 0.20599 | -0.16022 | 0.23346 | 0.16937 | 0.21515 | -0.068665 | 0.34332 | 0.28381 | -121.6965 | 121.2067 | -0.013733 | 121.4951 | 121.6003 | -0.050354 | -0.32959 | 0.064086 | 0.28839 | 121.2982 | 121.7102 | 121.5363 | 121.5729 | 121.4951 | 121.6507 | 121.582 | -0.32959 | 121.5729 | 121.4951 | 121.582 | 121.5363 | 121.6507 | -0.37994 | -121.9162
1644.125 | 121.7056 | -121.3623 | 0.21057 | 0.017929 | 0.015248 | 0.01326 | 0.17115 | -0.0026767 | -0.0097819 | 0.009942 | 0.09613 | 0.21973 | -0.21973 | 0.18768 | 0.09613 | 0.11902 | -0.022888 | 0.26093 | 0.32044 | -121.6644 | 121.1426 | 0.009156 | 121.4584 | 121.55 | -0.11444 | -0.30212 | 0.10986 | 0.31586 | 121.3394 | 121.6232 | 121.4584 | 121.582 | 121.4584 | 121.6827 | 121.4813 | -0.30212 | 121.582 | 121.4584 | 121.4813 | 121.4584 | 121.6827 | -0.4303 | -121.875
1645.8906 | 121.6644 | -121.3943 | 0.2243 | 0.0026703 | 0.015889 | 0.011764 | 0.1673 | -0.0035313 | -0.0057229 | 0.0078058 | 0.054932 | 0.19226 | -0.18768 | 0.16479 | 0.11902 | 0.16937 | -0.082397 | 0.27466 | 0.31586 | -121.6827 | 121.2067 | -0.032043 | 121.4493 | 121.5591 | -0.10529 | -0.28839 | 0.091553 | 0.24261 | 121.312 | 121.669 | 121.5134 | 121.5866 | 121.4493 | 121.7102 | 121.5637 | -0.28839 | 121.5866 | 121.4493 | 121.5637 | 121.5134 | 121.7102 | -0.41199 | -121.907
1647.5625 | 121.7468 | -121.3531 | 0.16937 | 0.0026703 | 0.020589 | 0.013687 | 0.17478 | -0.0048129 | -0.0055093 | 0.0084468 | 0.027466 | 0.25635 | -0.21057 | 0.12817 | 0.059509 | 0.10071 | 0.07782 | 0.21515 | 0.33875 | -121.7331 | 121.1426 | 0.086975 | 121.3806 | 121.4813 | -0.10986 | -0.37994 | 0.16937 | 0.23804 | 121.431 | 121.5683 | 121.4127 | 121.6095 | 121.3806 | 121.6919 | 121.4539 | -0.37994 | 121.6095 | 121.3806 | 121.4539 | 121.4127 | 121.6919 | -0.37994 | -121.9025
1649.3125 | 121.701 | -121.3943 | 0.20142 | -0.012589 | 0.02123 | 0.015396 | 0.17841 | -0.0041721 | -0.0057229 | 0.0093012 | 0.10071 | 0.24719 | -0.19226 | 0.19226 | 0.10071 | 0.14648 | -0.022888 | 0.26093 | 0.32501 | -121.756 | 121.2021 | 0.045776 | 121.4951 | 121.5866 | -0.10071 | -0.36163 | 0.1236 | 0.29297 | 121.3715 | 121.6553 | 121.4951 | 121.6415 | 121.4951 | 121.7194 | 121.5408 | -0.36163 | 121.6415 | 121.4951 | 121.5408 | 121.4951 | 121.7194 | -0.39368 | -121.9574
1651 | 121.7194 | -121.463 | 0.16937 | 0.0026703 | 0.019734 | 0.012832 | 0.031437 | -0.0035313 | -0.0057229 | 0.011865 | 0.032043 | 0.23804 | -0.21515 | 0.11902 | 0.022888 | 0.091553 | 0.009155 | 0.21515 | 0.29297 | -121.788 | 121.2479 | 0.068664 | 121.4951 | 121.582 | -0.14649 | -0.32501 | 0.1236 | 0.24719 | 121.4722 | 121.6782 | 121.4859 | 121.7011 | 121.4951 | 121.756 | 121.5546 | -0.32501 | 121.7011 | 121.4951 | 121.5546 | 121.4859 | 121.756 | -0.38452 | -121.9574
1652.7344 | 121.7514 | -121.4447 | 0.16479 | 0.0026703 | 0.017385 | 0.013901 | 0.032718 | -0.0028903 | -0.0046549 | 0.010369 | 0.041199 | 0.2243 | -0.21515 | 0.13275 | 0.032043 | 0.09613 | 0 | 0.20142 | 0.31586 | -121.7743 | 121.2296 | 0.059509 | 121.4859 | 121.5775 | -0.13275 | -0.32959 | 0.15106 | 0.25635 | 121.4447 | 121.6461 | 121.4767 | 121.669 | 121.4859 | 121.7606 | 121.5408 | -0.32959 | 121.669 | 121.4859 | 121.5408 | 121.4767 | 121.7606 | -0.37994 | -121.9391
1654.5 | 121.6965 | -121.4722 | 0.16479 | 0.0026703 | 0.01653 | 0.015396 | 0.028019 | -0.0052401 | -0.0035867 | 0.008233 | 0.041199 | 0.21057 | -0.18768 | 0.14191 | 0.10529 | 0.16937 | -0.09613 | 0.26093 | 0.28381 | -121.7651 | 121.2845 | 0.045776 | 121.5134 | 121.6141 | -0.059509 | -0.29297 | 0.11902 | 0.22888 | 121.376 | 121.7331 | 121.5775 | 121.6827 | 121.5134 | 121.756 | 121.6415 | -0.29297 | 121.6827 | 121.5134 | 121.6415 | 121.5775 | 121.756 | -0.35248 | -121.9299
1656.2656 | 121.701 | -121.4767 | 0.19226 | -0.0049592 | 0.018025 | 0.0094143 | 0.026096 | -0.0056675 | -0.0033731 | 0.008874 | 0.059509 | 0.20599 | -0.17853 | 0.15564 | 0.07782 | 0.1831 | -0.10986 | 0.27466 | 0.29297 | -121.7834 | 121.2982 | 0.013733 | 121.5363 | 121.6324 | -0.11444 | -0.3067 | 0.10071 | 0.23804 | 121.3669 | 121.7514 | 121.5546 | 121.6827 | 121.5363 | 121.7697 | 121.6599 | -0.3067 | 121.6827 | 121.5363 | 121.6599 | 121.5546 | 121.7697 | -0.37079 | -121.9757
1658.0312 | 121.7972 | -121.4447 | 0.13733 | 0.0103 | 0.017171 | 0.012405 | 0.033359 | -0.0052401 | -0.0038003 | 0.008874 | 0.013733 | 0.25177 | -0.21057 | 0.11902 | 0.009155 | 0.09613 | -0.013733 | 0.1831 | 0.29297 | -121.8201 | 121.2341 | 0.11444 | 121.4584 | 121.5637 | -0.12817 | -0.37537 | 0.15564 | 0.2243 | 121.431 | 121.6278 | 121.4539 | 121.6965 | 121.4584 | 121.7377 | 121.5408 | -0.37537 | 121.6965 | 121.4584 | 121.5408 | 121.4539 | 121.7377 | -0.3479 | -121.9574
1659.7188 | 121.7377 | -121.5134 | 0.15564 | 0.0103 | 0.015248 | 0.010269 | 0.032932 | -0.0039585 | -0.0076455 | 0.008874 | 0.064087 | 0.21973 | -0.20599 | 0.16937 | 0.041199 | 0.13733 | 0 | 0.25177 | 0.30212 | -121.788 | 121.3074 | 0.064087 | 121.5775 | 121.6827 | -0.11444 | -0.27466 | 0.14648 | 0.27008 | 121.5134 | 121.7651 | 121.5546 | 121.7331 | 121.5775 | 121.8155 | 121.6507 | -0.27466 | 121.7331 | 121.5775 | 121.6507 | 121.5546 | 121.8155 | -0.36163 | -121.9437
1661.4688 | 121.8109 | -121.4676 | 0.15564 | 0.0103 | 0.019521 | 0.013046 | 0.031437 | -0.0043857 | -0.0055093 | 0.008874 | 0.013733 | 0.24719 | -0.22888 | 0.10986 | 0.050354 | 0.086975 | 0.082397 | 0.2243 | 0.31128 | -121.8384 | 121.2387 | 0.091552 | 121.4813 | 121.5775 | -0.10529 | -0.37079 | 0.15564 | 0.24261 | 121.55 | 121.6919 | 121.5179 | 121.7148 | 121.4813 | 121.7789 | 121.5546 | -0.37079 | 121.7148 | 121.4813 | 121.5546 | 121.5179 | 121.7789 | -0.38452 | -121.994
1663.2031 | 121.7697 | -121.4905 | 0.16937 | 0.0026703 | 0.015676 | 0.013687 | 0.030582 | -0.0024631 | -0.0085001 | 0.011437 | 0.045776 | 0.21973 | -0.18768 | 0.16022 | 0.068665 | 0.15564 | -0.10529 | 0.25635 | 0.29297 | -121.7743 | 121.3028 | 0.050354 | 121.5363 | 121.6507 | -0.10071 | -0.28381 | 0.1236 | 0.23346 | 121.3852 | 121.7468 | 121.5591 | 121.7102 | 121.5363 | 121.7834 | 121.6461 | -0.28381 | 121.7102 | 121.5363 | 121.6461 | 121.5591 | 121.7834 | -0.35706 | -121.9437
1664.9531 | 121.8292 | -121.4813 | 0.14191 | 0.0026703 | 0.016744 | 0.011551 | 0.032078 | -0.0026767 | -0.0067911 | 0.010369 | 0.009155 | 0.22888 | -0.21515 | 0.11902 | 0.022888 | 0.11444 | -0.027466 | 0.18768 | 0.28381 | -121.8201 | 121.2662 | 0.086975 | 121.4905 | 121.6003 | -0.11902 | -0.33875 | 0.14191 | 0.2243 | 121.4539 | 121.669 | 121.5042 | 121.7102 | 121.4905 | 121.7651 | 121.5958 | -0.33875 | 121.7102 | 121.4905 | 121.5958 | 121.5042 | 121.7651 | -0.35706 | -121.962
1666.625 | 121.6919 | -97.8378 | 23.8266 | -0.0049592 | 0.014394 | 0.010483 | 0.0045203 | 0.0086453 | -0.0040139 | 0.0075922 | 0.036621 | 0.18768 | -0.18768 | 0.14191 | 23.703 | 23.9731 | -0.11902 | 0.2655 | 23.9136 | -98.1033 | 97.6501 | -23.6389 | 97.8745 | 97.9797 | -0.1236 | -0.2655 | 0.086975 | 0.2243 | 97.7188 | 98.1033 | 121.5408 | 98.0255 | 97.8745 | 121.7514 | 121.8109 | -0.2655 | 98.0255 | 97.8745 | 121.8109 | 121.5408 | 121.7514 | -24.0143 | -121.9299
1668.375 | 121.7834 | -97.7737 | 23.8083 | -0.012589 | 0.016317 | 0.012832 | 0.012424 | 0.0077909 | -0.0078591 | 0.008874 | 0.004578 | 0.20599 | -0.22888 | 0.10986 | 23.6618 | 23.9182 | -0.086975 | 0.20599 | 23.9548 | -98.1125 | 97.5449 | -23.6023 | 97.7783 | 97.8836 | -0.14648 | -0.33875 | 0.14648 | 0.23346 | 97.6868 | 97.9797 | 121.4355 | 97.9797 | 97.7783 | 121.7285 | 121.6919 | -0.33875 | 97.9797 | 97.7783 | 121.6919 | 121.4355 | 121.7285 | -24.0372 | -121.9208
1670.125 | 121.7468 | -97.7783 | 23.8495 | -0.012589 | 0.017385 | 0.012192 | 0.0053747 | 0.0067227 | -0.0070047 | 0.0086604 | 0.054932 | 0.17853 | -0.20142 | 0.15564 | 23.7488 | 24.0143 | -0.12817 | 0.27008 | 23.9456 | -98.0942 | 97.5769 | -23.671 | 97.8333 | 97.934 | -0.10071 | -0.31586 | 0.096131 | 0.25635 | 97.6501 | 98.0484 | 121.5271 | 97.9568 | 97.8333 | 121.7239 | 121.7926 | -0.31586 | 97.9568 | 97.8333 | 121.7926 | 121.5271 | 121.7239 | -24.0509 | -121.9437
1671.875 | 121.843 | -97.7371 | 23.8495 | 0.0103 | 0.014821 | 0.011123 | 0.010715 | 0.0058681 | -0.0059365 | 0.0095148 | -0.022888 | 0.21057 | -0.23804 | 0.10071 | 23.6847 | 23.909 | 0.054932 | 0.19684 | 24.0234 | -98.0942 | 97.4991 | -23.6389 | 97.7142 | 97.8378 | -0.1648 | -0.35706 | 0.17395 | 0.21515 | 97.7921 | 97.934 | 121.4218 | 97.9477 | 97.7142 | 121.7606 | 121.6461 | -0.35706 | 97.9477 | 97.7142 | 121.6461 | 121.4218 | 121.7606 | -24.0875 | -121.9437
1673.5625 | 121.7468 | -97.7509 | 23.8953 | -0.012589 | 0.017385 | 0.011764 | 0.0098609 | 0.010995 | -0.0065775 | 0.01101 | 0.07782 | 0.16937 | -0.21515 | 0.21057 | 23.7946 | 24.0692 | -0.17395 | 0.27924 | 23.9777 | -98.0209 | 97.5357 | -23.7259 | 97.8287 | 97.9614 | -0.10071 | -0.27008 | 0.082397 | 0.29297 | 97.5769 | 98.0301 | 121.5454 | 97.9202 | 97.8287 | 121.7285 | 121.8201 | -0.27008 | 97.9202 | 97.8287 | 121.8201 | 121.5454 | 121.7285 | -24.1104 | -121.9162
1675.3281 | 121.8292 | -97.7142 | 23.8724 | 0.0026703 | 0.017171 | 0.016891 | 0.01157 | 0.0080045 | -0.0074319 | 0.012292 | 0.045776 | 0.19684 | -0.21973 | 0.13733 | 23.7167 | 23.9685 | -0.032043 | 0.21057 | 24.0143 | -98.0759 | 97.4945 | -23.6755 | 97.76 | 97.8516 | -0.15564 | -0.36163 | 0.14191 | 0.2655 | 97.6822 | 97.9248 | 121.431 | 97.9111 | 97.76 | 121.7285 | 121.6827 | -0.36163 | 97.9111 | 97.76 | 121.6827 | 121.431 | 121.7285 | -24.0921 | -121.9482
1677.0938 | 121.8201 | -97.7188 | 23.9227 | 0.0103 | 0.017812 | 0.012405 | 0.010288 | 0.0082181 | -0.0097819 | 0.010156 | 0.054932 | 0.21057 | -0.21973 | 0.15106 | 23.79 | 24.0326 | -0.045776 | 0.24261 | 24.028 | -98.0621 | 97.4991 | -23.7122 | 97.7737 | 97.8699 | -0.13275 | -0.34332 | 0.10529 | 0.27466 | 97.673 | 97.9614 | 121.5088 | 97.9294 | 97.7737 | 121.7468 | 121.7514 | -0.34332 | 97.9294 | 97.7737 | 121.7514 | 121.5088 | 121.7468 | -24.1425 | -121.9849
1678.8438 | 121.8063 | -121.5042 | 0.17395 | -0.0049592 | 0.015248 | 0.012832 | 0.024387 | -0.0054539 | -0.0027323 | 0.0080194 | 0.1236 | 0.19684 | -0.16937 | 0.23346 | 0.15564 | 0.19684 | -0.10529 | 0.35706 | 0.2655 | -121.907 | 121.3348 | 0.022888 | 121.6278 | 121.7377 | -0.01831 | -0.40283 | 0.091553 | 0.29297 | 121.3989 | 121.8613 | 121.6599 | 121.701 | 121.6278 | 121.7697 | 121.701 | -0.40283 | 121.701 | 121.6278 | 121.701 | 121.6599 | 121.7697 | -0.34332 | -122.081
1680.5469 | 121.8475 | -121.5179 | 0.16479 | -0.0049592 | 0.014821 | 0.010055 | 0.026737 | -0.0060947 | -0.0055093 | 0.0069514 | 0.073242 | 0.19684 | -0.16479 | 0.16022 | 0.086975 | 0.17853 | -0.086975 | 0.28381 | 0.28381 | -121.8979 | 121.3531 | 0.032043 | 121.5912 | 121.6782 | -0.07782 | -0.37994 | 0.11902 | 0.23804 | 121.431 | 121.8018 | 121.6049 | 121.7148 | 121.5912 | 121.8018 | 121.6965 | -0.37994 | 121.7148 | 121.5912 | 121.6965 | 121.6049 | 121.8018 | -0.32959 | -122.0627
1682.2969 | 121.7834 | -121.6003 | 0.17395 | -0.0049592 | 0.018453 | 0.011551 | 0.029514 | -0.0073765 | -0.0048685 | 0.0086604 | 0.13733 | 0.18768 | -0.17395 | 0.25635 | 0.13733 | 0.21973 | -0.1236 | 0.36621 | 0.27466 | -121.8933 | 121.4264 | 0.013733 | 121.7377 | 121.8567 | -0.036621 | -0.29297 | 0.10071 | 0.31128 | 121.4767 | 121.9666 | 121.7377 | 121.788 | 121.7377 | 121.875 | 121.8201 | -0.29297 | 121.788 | 121.7377 | 121.8201 | 121.7377 | 121.875 | -0.3479 | -122.0673
1684.0625 | 121.9208 | -121.5408 | 0.13275 | 0.0026703 | 0.015035 | 0.0098417 | 0.03165 | -0.0058811 | -0.0065775 | 0.0078058 | 0.004578 | 0.21515 | -0.21973 | 0.11902 | 0.022888 | 0.086975 | 0.054932 | 0.21973 | 0.32044 | -121.9208 | 121.3211 | 0.082398 | 121.5454 | 121.6599 | -0.10986 | -0.37994 | 0.18768 | 0.22431 | 121.5958 | 121.7606 | 121.5637 | 121.756 | 121.5454 | 121.8613 | 121.6278 | -0.37994 | 121.756 | 121.5454 | 121.6278 | 121.5637 | 121.8613 | -0.35248 | -122.0535
1685.8125 | 121.8384 | -121.5912 | 0.16937 | -0.012589 | 0.016317 | 0.011978 | 0.030582 | -0.0028903 | -0.0048685 | 0.010156 | 0.068665 | 0.20599 | -0.18768 | 0.16937 | 0.073242 | 0.16937 | -0.07782 | 0.26093 | 0.27008 | -121.907 | 121.4035 | 0.036621 | 121.6599 | 121.7606 | -0.096131 | -0.31586 | 0.10071 | 0.25635 | 121.5134 | 121.8521 | 121.6644 | 121.7972 | 121.6599 | 121.8613 | 121.7606 | -0.31586 | 121.7972 | 121.6599 | 121.7606 | 121.6644 | 121.8613 | -0.35706 | -122.0764
1687.5781 | 121.8018 | -119.3665 | 2.4033 | -0.012589 | 0.015889 | 0.012832 | 0.028232 | -0.0050265 | -0.0078591 | 0.010583 | 0.11444 | 0.18768 | -0.17853 | 0.25635 | 2.3117 | 2.4445 | -0.12817 | 0.36621 | 2.4765 | -119.6869 | 119.1879 | -2.2156 | 119.4809 | 119.6228 | -0.091552 | -0.32044 | 0.073242 | 0.29297 | 119.2383 | 119.7327 | 121.6782 | 119.5541 | 119.4809 | 121.843 | 121.8109 | -0.32044 | 119.5541 | 119.4809 | 121.8109 | 121.6782 | 121.843 | -2.5818 | -122.0901
1689.2656 | 121.8338 | -119.0918 | 2.6779 | -0.012589 | 0.019094 | 0.014328 | 0.028873 | -0.0035313 | -0.0061503 | 0.008874 | 0.09613 | 0.21057 | -0.19226 | 0.21973 | 2.6321 | 2.7237 | -0.10071 | 0.32501 | 2.7924 | -119.3985 | 118.8995 | -2.4673 | 119.1879 | 119.3115 | -0.045776 | -0.3067 | 0.11444 | 0.28839 | 118.9911 | 119.4168 | 121.7239 | 119.3024 | 119.1879 | 121.8842 | 121.8155 | -0.3067 | 119.3024 | 119.1879 | 121.8155 | 121.7239 | 121.8842 | -2.8702 | -122.0764
1691.0156 | 121.7606 | -97.7463 | 24.0509 | -0.0049592 | 0.016957 | 0.0062101 | 0.0081519 | 0.0077909 | -0.0038003 | 0.0075922 | 0.086975 | 0.15106 | -0.19684 | 0.22888 | 23.996 | 24.2569 | -0.14648 | 0.34332 | 24.1653 | -97.9385 | 97.5494 | -23.8998 | 97.8333 | 97.9752 | -0.054931 | -0.19226 | 0.11444 | 0.28381 | 97.5998 | 98.0896 | 121.7422 | 97.8973 | 97.8333 | 121.9116 | 122.0032 | -0.19226 | 97.8973 | 97.8333 | 122.0032 | 121.7422 | 121.9116 | -24.2477 | -121.9894
1692.6875 | 121.9025 | -97.673 | 24.0005 | -0.0049592 | 0.016744 | 0.013473 | 0.010929 | 0.0080045 | -0.0087137 | 0.0084468 | -0.018311 | 0.21973 | -0.24261 | 0.11902 | 23.8632 | 24.1013 | 0.068665 | 0.20599 | 24.202 | -97.9935 | 97.4304 | -23.7808 | 97.6547 | 97.7921 | -0.13733 | -0.32043 | 0.20142 | 0.2243 | 97.7417 | 97.879 | 121.5363 | 97.8928 | 97.6547 | 121.875 | 121.7743 | -0.32043 | 97.8928 | 97.6547 | 121.7743 | 121.5363 | 121.875 | -24.2432 | -121.994
1694.4531 | 121.9437 | -121.5591 | 0.14191 | 0.0026703 | 0.018453 | 0.013046 | 0.034641 | -0.0045993 | -0.0076455 | 0.009942 | 0.022888 | 0.21973 | -0.21515 | 0.16022 | 0.036621 | 0.10529 | -0.064087 | 0.20142 | 0.31128 | -121.9437 | 121.344 | 0.07782 | 121.582 | 121.7194 | -0.10529 | -0.38452 | 0.16937 | 0.23804 | 121.4951 | 121.7606 | 121.5958 | 121.7789 | 121.582 | 121.8704 | 121.6644 | -0.38452 | 121.7789 | 121.582 | 121.6644 | 121.5958 | 121.8704 | -0.35706 | -122.0856
1696.1562 | 121.9162 | -121.582 | 0.15564 | 0.0026703 | 0.017171 | 0.013901 | 0.034214 | -0.0037449 | -0.0074319 | 0.011651 | 0.073242 | 0.20599 | -0.21057 | 0.17395 | 0.073242 | 0.12817 | -0.018311 | 0.25177 | 0.28839 | -121.9986 | 121.3715 | 0.050354 | 121.6553 | 121.756 | -0.082398 | -0.41657 | 0.13275 | 0.28381 | 121.5637 | 121.8338 | 121.6553 | 121.788 | 121.6553 | 121.8704 | 121.7102 | -0.41657 | 121.788 | 121.6553 | 121.7102 | 121.6553 | 121.8704 | -0.36621 | -122.1542
1697.9062 | 121.9803 | -121.6232 | 0.13275 | -0.0049592 | 0.018453 | 0.011337 | 0.033359 | -0.0039585 | -0.0080729 | 0.010156 | 0.018311 | 0.24719 | -0.20599 | 0.11444 | 0.013733 | 0.082397 | 0.018311 | 0.17853 | 0.30212 | -121.9666 | 121.4172 | 0.11444 | 121.6415 | 121.7377 | -0.11902 | -0.34332 | 0.16937 | 0.22431 | 121.6415 | 121.8018 | 121.637 | 121.8704 | 121.6415 | 121.9254 | 121.7056 | -0.34332 | 121.8704 | 121.6415 | 121.7056 | 121.637 | 121.9254 | -0.33875 | -122.0993
1699.5938 | 121.8567 | -121.6461 | 0.17395 | -0.0049592 | 0.017598 | 0.01091 | 0.025455 | -0.0078037 | -0.0059365 | 0.011224 | 0.091553 | 0.21057 | -0.18768 | 0.22888 | 0.15106 | 0.21515 | -0.1236 | 0.3479 | 0.27008 | -121.9849 | 121.4584 | 0.036621 | 121.7377 | 121.875 | -0.022888 | -0.33875 | 0.096131 | 0.27924 | 121.5225 | 121.994 | 121.7972 | 121.8567 | 121.7377 | 121.9162 | 121.8613 | -0.33875 | 121.8567 | 121.7377 | 121.8613 | 121.7972 | 121.9162 | -0.36163 | -122.1588
1701.3594 | 121.8521 | -121.6553 | 0.17853 | 0.0026703 | 0.020162 | 0.0083463 | 0.027164 | -0.0045993 | -0.0061503 | 0.010156 | 0.11902 | 0.19684 | -0.18768 | 0.26093 | 0.15106 | 0.22888 | -0.16022 | 0.37994 | 0.27008 | -121.962 | 121.4676 | 0.01831 | 121.7743 | 121.9162 | -0.027466 | -0.3067 | 0.091553 | 0.3067 | 121.4951 | 122.0352 | 121.8063 | 121.8521 | 121.7743 | 121.9254 | 121.8842 | -0.3067 | 121.8521 | 121.7743 | 121.8842 | 121.8063 | 121.9254 | -0.36621 | -122.1405
1703.125 | 121.907 | -121.669 | 0.16937 | 0.0026703 | 0.016317 | 0.014969 | 0.0293 | -0.0054539 | -0.0048685 | 0.0095148 | 0.086975 | 0.20142 | -0.1831 | 0.18768 | 0.082397 | 0.16937 | -0.11902 | 0.28381 | 0.27008 | -121.9711 | 121.4859 | 0.032043 | 121.756 | 121.8567 | -0.086976 | -0.30212 | 0.10071 | 0.27008 | 121.55 | 121.9528 | 121.7514 | 121.8704 | 121.756 | 121.9391 | 121.8384 | -0.30212 | 121.8704 | 121.756 | 121.8384 | 121.7514 | 121.9391 | -0.35248 | -122.1405
1704.875 | 121.8567 | -121.6782 | 0.20599 | 0.0026703 | 0.016317 | 0.011551 | 0.030155 | -0.0069491 | -0.0070047 | 0.011437 | 0.13275 | 0.17853 | -0.17853 | 0.26093 | 0.15564 | 0.24261 | -0.15106 | 0.36163 | 0.27924 | -121.9299 | 121.4996 | -0.027466 | 121.8109 | 121.9391 | -0.050354 | -0.25177 | 0.073242 | 0.31128 | 121.5271 | 122.0398 | 121.8338 | 121.8567 | 121.8109 | 121.9574 | 121.9208 | -0.25177 | 121.8567 | 121.8109 | 121.9208 | 121.8338 | 121.9574 | -0.38452 | -122.1359
1706.5781 | 121.9391 | -121.6599 | 0.15564 | 0.0026703 | 0.015676 | 0.016464 | 0.036564 | -0.0031039 | -0.0080729 | 0.0090876 | 0.07782 | 0.2243 | -0.22888 | 0.20142 | 0.059509 | 0.13733 | -0.032043 | 0.27008 | 0.30212 | -121.9894 | 121.431 | 0.068664 | 121.7377 | 121.8613 | -0.096131 | -0.32959 | 0.14648 | 0.3067 | 121.6278 | 121.9299 | 121.7194 | 121.8842 | 121.7377 | 121.962 | 121.7972 | -0.32959 | 121.8842 | 121.7377 | 121.7972 | 121.7194 | 121.962 | -0.38452 | -122.1451
1708.3281 | 121.9528 | -121.5317 | 0.25177 | 0.0026703 | 0.018025 | 0.012405 | 0.034427 | -0.0033175 | -0.0082865 | 0.011651 | 0.082397 | 0.23804 | -0.21057 | 0.1831 | 0.17395 | 0.13275 | -0.013733 | 0.24261 | 0.41657 | -121.8567 | 121.3211 | -0.013733 | 121.6141 | 121.7148 | -0.07782 | -0.32501 | 0.1648 | 0.29297 | 121.5179 | 121.7743 | 121.7056 | 121.7697 | 121.6141 | 121.9482 | 121.6644 | -0.32501 | 121.7697 | 121.6141 | 121.6644 | 121.7056 | 121.9482 | -0.46234 | -122.1085
1710.0156 | 121.962 | -121.582 | 0.21973 | -0.0049592 | 0.016103 | 0.012832 | 0.033359 | -0.0024631 | -0.0074319 | 0.008874 | 0.032043 | 0.2243 | -0.23346 | 0.16022 | 0.11902 | 0.11902 | 0.004578 | 0.26093 | 0.36163 | -121.9345 | 121.3486 | 0.004577 | 121.6141 | 121.7422 | -0.10071 | -0.35248 | 0.14191 | 0.2655 | 121.5866 | 121.843 | 121.701 | 121.8063 | 121.6141 | 121.9437 | 121.701 | -0.35248 | 121.8063 | 121.6141 | 121.701 | 121.701 | 121.9437 | -0.45319 | -122.1542
1711.7812 | 121.9437 | -121.6644 | 0.1831 | -0.012589 | 0.016957 | 0.010055 | 0.024387 | -0.0067355 | -0.0046549 | 0.011224 | 0.068665 | 0.19684 | -0.17853 | 0.16022 | 0.1236 | 0.16022 | -0.07782 | 0.2655 | 0.29297 | -122.0078 | 121.4859 | 0.013733 | 121.7331 | 121.8246 | -0.059509 | -0.34332 | 0.10986 | 0.24719 | 121.5866 | 121.9299 | 121.788 | 121.8613 | 121.7331 | 121.9574 | 121.8246 | -0.34332 | 121.8613 | 121.7331 | 121.8246 | 121.788 | 121.9574 | -0.36163 | -122.1909
1713.5469 | 121.8979 | -121.5637 | 0.34332 | 0.0026703 | 0.015462 | 0.01561 | 0.030369 | -0.0048129 | -0.0052957 | 0.0097284 | 0.12817 | 0.18768 | -0.17395 | 0.22888 | 0.29297 | 0.21973 | -0.17395 | 0.32044 | 0.42572 | -121.8201 | 121.3898 | -0.15564 | 121.6919 | 121.7926 | -0.050354 | -0.25635 | 0.082397 | 0.30212 | 121.3898 | 121.8842 | 121.8567 | 121.7514 | 121.6919 | 121.9894 | 121.7834 | -0.25635 | 121.7514 | 121.6919 | 121.7834 | 121.8567 | 121.9894 | -0.51727 | -122.1634
1715.3125 | 122.0215 | -119.3024 | 2.4582 | 0.0026703 | 0.015248 | 0.010696 | 0.029087 | -0.0022495 | -0.0063639 | 0.0084468 | 0.013733 | 0.22888 | -0.22888 | 0.1236 | 2.3621 | 0.086975 | 0.045776 | 0.2243 | 2.6321 | -119.6915 | 119.0735 | -2.2293 | 119.3161 | 119.426 | -0.09613 | -0.3891 | 0.17395 | 0.24261 | 119.3481 | 119.5267 | 121.6644 | 119.5312 | 119.3161 | 121.9345 | 119.3893 | -0.3891 | 119.5312 | 119.3161 | 119.3893 | 121.6644 | 121.9345 | -2.6871 | -122.1497
1717.0625 | 121.9437 | -118.8629 | 2.9709 | -0.012589 | 0.015676 | 0.0087735 | 0.023105 | -0.0031039 | -0.0042277 | 0.0086604 | 0.050354 | 0.19226 | -0.17853 | 0.16479 | 2.9617 | 0.16937 | -0.073242 | 0.27008 | 3.1586 | -119.133 | 118.6844 | -2.7786 | 118.9133 | 119.0277 | -0.009155 | -0.27008 | 0.18768 | 0.22888 | 118.7897 | 119.133 | 121.8246 | 119.0552 | 118.9133 | 122.0215 | 119.0323 | -0.27008 | 119.0552 | 118.9133 | 119.0323 | 121.8246 | 122.0215 | -3.1494 | -122.1039
1718.8125 | 122.0306 | -118.6707 | 3.1265 | 0.0026703 | 0.016317 | 0.01091 | 0.034 | -0.0016087 | -0.0080729 | 0.0084468 | 0.009155 | 0.2243 | -0.22888 | 0.10071 | 2.9709 | 0.073242 | 0.004578 | 0.16937 | 3.2959 | -118.9911 | 118.4418 | -2.9022 | 118.6798 | 118.7714 | -0.15564 | -0.32044 | 0.16937 | 0.23804 | 118.6752 | 118.84 | 121.6415 | 118.895 | 118.6798 | 121.9666 | 118.7439 | -0.32044 | 118.895 | 118.6798 | 118.7439 | 121.6415 | 121.9666 | -3.3554 | -122.1176
1720.5156 | 121.9666 | -121.6965 | 0.17395 | -0.012589 | 0.017171 | 0.016678 | 0.031437 | -0.0026767 | -0.0074319 | 0.010369 | 0.059509 | 0.21515 | -0.21057 | 0.19684 | 0.10071 | 0.16022 | -0.11902 | 0.28381 | 0.28839 | -121.9711 | 121.4859 | 0.041199 | 121.756 | 121.8933 | -0.073242 | -0.27466 | 0.11444 | 0.27008 | 121.5775 | 121.9803 | 121.7972 | 121.9116 | 121.756 | 121.9849 | 121.8567 | -0.27466 | 121.9116 | 121.756 | 121.8567 | 121.7972 | 121.9849 | -0.38452 | -122.1451
1722.2656 | 121.9482 | -121.6919 | 0.16479 | -0.0049592 | 0.01653 | 0.0079189 | 0.026096 | -0.0060947 | -0.0046549 | 0.0097284 | 0.064087 | 0.20142 | -0.1831 | 0.16022 | 0.091553 | 0.17395 | -0.07782 | 0.28381 | 0.27924 | -122.0398 | 121.5088 | 0.036621 | 121.756 | 121.8521 | -0.073242 | -0.3479 | 0.11444 | 0.24719 | 121.6141 | 121.9757 | 121.7834 | 121.8933 | 121.756 | 121.9711 | 121.8658 | -0.3479 | 121.8933 | 121.756 | 121.8658 | 121.7834 | 121.9711 | -0.3479 | -122.2046
1724.0156 | 122.0078 | -121.7102 | 0.14648 | 0.0026703 | 0.017385 | 0.011123 | 0.032291 | -0.0035313 | -0.0057229 | 0.010369 | 0.041199 | 0.23346 | -0.20599 | 0.12817 | 0.018311 | 0.09613 | 0.013733 | 0.19684 | 0.28839 | -122.0306 | 121.5042 | 0.086975 | 121.7514 | 121.8384 | -0.12817 | -0.32044 | 0.14191 | 0.24719 | 121.7239 | 121.907 | 121.7285 | 121.9437 | 121.7514 | 121.9986 | 121.8063 | -0.32044 | 121.9437 | 121.7514 | 121.8063 | 121.7285 | 121.9986 | -0.35248 | -122.1771
1725.7031 | 122.0535 | -121.6736 | 0.13275 | 0.0103 | 0.016317 | 0.0081327 | 0.026951 | -0.0045993 | -0.0087137 | 0.0097284 | 0 | 0.21057 | -0.22888 | 0.12817 | 0.032043 | 0.086975 | 0.054932 | 0.21973 | 0.30212 | -122.0398 | 121.4447 | 0.07782 | 121.6736 | 121.8018 | -0.10071 | -0.36621 | 0.16937 | 0.22888 | 121.7285 | 121.8933 | 121.7056 | 121.8842 | 121.6736 | 121.9757 | 121.7606 | -0.36621 | 121.8842 | 121.6736 | 121.7606 | 121.7056 | 121.9757 | -0.36163 | -122.1725
1727.4688 | 122.0398 | -121.6965 | 0.14191 | -0.0049592 | 0.018666 | 0.010055 | 0.030582 | -0.0033175 | -0.0074319 | 0.0095148 | 0.013733 | 0.22888 | -0.21515 | 0.1236 | 0.027466 | 0.073242 | 0.045776 | 0.21515 | 0.28839 | -122.0581 | 121.4813 | 0.086975 | 121.7102 | 121.8201 | -0.11444 | -0.36163 | 0.14648 | 0.22888 | 121.7422 | 121.9116 | 121.7239 | 121.9254 | 121.7102 | 121.9849 | 121.7697 | -0.36163 | 121.9254 | 121.7102 | 121.7697 | 121.7239 | 121.9849 | -0.35706 | -122.2
1729.2344 | 122.0215 | -121.6782 | 0.1236 | 0.0026703 | 0.01653 | 0.0081327 | 0.026951 | -0.0065219 | -0.0055093 | 0.0093012 | 0.013733 | 0.21973 | -0.20142 | 0.10986 | 0.032043 | 0.086975 | 0.045776 | 0.2243 | 0.30212 | -122.0993 | 121.4767 | 0.096131 | 121.6919 | 121.788 | -0.091553 | -0.42114 | 0.17853 | 0.21515 | 121.7239 | 121.9025 | 121.7102 | 121.8979 | 121.6919 | 121.9803 | 121.7651 | -0.42114 | 121.8979 | 121.6919 | 121.7651 | 121.7102 | 121.9803 | -0.32501 | -122.2229
1731 | 122.0123 | -121.6873 | 0.16022 | 0.0026703 | 0.019734 | 0.011123 | 0.027164 | -0.0048129 | -0.0048685 | 0.011224 | 0.027466 | 0.2243 | -0.21057 | 0.1236 | 0.032043 | 0.10071 | 0.050354 | 0.22888 | 0.30212 | -122.081 | 121.4767 | 0.064087 | 121.7148 | 121.8109 | -0.12817 | -0.39368 | 0.14191 | 0.23804 | 121.7377 | 121.9162 | 121.7194 | 121.9116 | 121.7148 | 121.9894 | 121.788 | -0.39368 | 121.9116 | 121.7148 | 121.788 | 121.7194 | 121.9894 | -0.37079 | -122.2412
1732.7031 | 121.9437 | -121.7285 | 0.16937 | 0.0026703 | 0.016957 | 0.010055 | 0.024601 | -0.0048129 | -0.0061503 | 0.0084468 | 0.07782 | 0.1831 | -0.17395 | 0.21515 | 0.14191 | 0.20599 | -0.10986 | 0.33875 | 0.27466 | -122.0627 | 121.5546 | 0.013732 | 121.8063 | 121.9437 | -0.027466 | -0.33417 | 0.10529 | 0.25177 | 121.6187 | 122.0673 | 121.8704 | 121.9116 | 121.8063 | 122.0032 | 121.9345 | -0.33417 | 121.9116 | 121.8063 | 121.9345 | 121.8704 | 122.0032 | -0.34332 | -122.2321
1734.4531 | 121.8475 | -121.8063 | 0.1831 | -0.0049592 | 0.017171 | 0.0081327 | 0.026523 | -0.0069491 | -0.0080729 | 0.010797 | 0.10071 | 0.18768 | -0.16937 | 0.21973 | 0.12817 | 0.19226 | -0.086975 | 0.34332 | 0.25635 | -122.0673 | 121.637 | 0.004578 | 121.907 | 122.0261 | -0.054931 | -0.26093 | 0.073243 | 0.27008 | 121.7194 | 122.1497 | 121.9345 | 121.994 | 121.907 | 122.0627 | 121.9986 | -0.26093 | 121.994 | 121.907 | 121.9986 | 121.9345 | 122.0627 | -0.35248 | -122.2504
1736.2188 | 121.9025 | -121.8292 | 0.16479 | -0.0049592 | 0.016957 | 0.0057827 | 0.025882 | -0.0058811 | -0.0055093 | 0.008874 | 0.13275 | 0.19684 | -0.16479 | 0.24261 | 0.14648 | 0.21973 | -0.10986 | 0.36621 | 0.2655 | -122.081 | 121.6644 | 0.032043 | 121.962 | 122.0718 | -0.018311 | -0.25177 | 0.10071 | 0.29755 | 121.7194 | 122.1954 | 121.9757 | 122.0261 | 121.962 | 122.0947 | 122.049 | -0.25177 | 122.0261 | 121.962 | 122.049 | 121.9757 | 122.0947 | -0.32959 | -122.2458
1737.9688 | 122.0627 | -121.7377 | 0.14191 | -0.0049592 | 0.022725 | 0.015823 | 0.032505 | -0.0043857 | -0.0080729 | 0.0073786 | 0.036621 | 0.24261 | -0.21973 | 0.11444 | -0.009155 | 0.059509 | 0 | 0.15564 | 0.30212 | -122.1222 | 121.5179 | 0.10071 | 121.7743 | 121.8521 | -0.15106 | -0.38452 | 0.16022 | 0.25635 | 121.7377 | 121.8933 | 121.7285 | 121.9803 | 121.7743 | 122.0398 | 121.7972 | -0.38452 | 121.9803 | 121.7743 | 121.7972 | 121.7285 | 122.0398 | -0.36163 | -122.2641
1739.6406 | 121.9482 | -121.7789 | 0.17395 | -0.0049592 | 0.01888 | 0.014114 | 0.023105 | -0.0043857 | -0.0055093 | 0.0097284 | 0.073242 | 0.19684 | -0.1831 | 0.19684 | 0.11902 | 0.20142 | -0.091553 | 0.31586 | 0.25635 | -122.113 | 121.5958 | 0.022888 | 121.8521 | 121.9757 | -0.054931 | -0.33417 | 0.082398 | 0.25635 | 121.6873 | 122.0947 | 121.8979 | 121.9757 | 121.8521 | 122.0352 | 121.9803 | -0.33417 | 121.9757 | 121.8521 | 121.9803 | 121.8979 | 122.0352 | -0.35706 | -122.287
1741.4219 | 122.0627 | -121.7331 | 0.12817 | -0.0049592 | 0.015035 | 0.0077053 | 0.027591 | -0.0071629 | -0.0052957 | 0.010369 | -0.004578 | 0.21973 | -0.26093 | 0.1236 | 0.027466 | 0.068665 | 0.068665 | 0.21057 | 0.31586 | -122.1222 | 121.4722 | 0.091553 | 121.7285 | 121.8567 | -0.10071 | -0.3891 | 0.18768 | 0.25635 | 121.8018 | 121.9437 | 121.7606 | 121.9528 | 121.7285 | 122.0489 | 121.8018 | -0.3891 | 121.9528 | 121.7285 | 121.8018 | 121.7606 | 122.0489 | -0.3891 | -122.2504
1743.1094 | 122.081 | -121.7331 | 0.1236 | 0.0026703 | 0.018239 | 0.014114 | 0.028232 | -0.0043857 | -0.0046549 | 0.0097284 | 0.013733 | 0.2243 | -0.20142 | 0.11902 | 0.027466 | 0.073242 | 0.068665 | 0.20142 | 0.30212 | -122.1634 | 121.5317 | 0.10071 | 121.7468 | 121.8521 | -0.09613 | -0.4303 | 0.17853 | 0.21515 | 121.8018 | 121.9345 | 121.7606 | 121.9574 | 121.7468 | 122.0352 | 121.8063 | -0.4303 | 121.9574 | 121.7468 | 121.8063 | 121.7606 | 122.0352 | -0.32501 | -122.287
1744.8594 | 121.9666 | -121.8201 | 0.15564 | -0.012589 | 0.015676 | 0.0070645 | 0.026096 | -0.0052401 | -0.0033731 | 0.010797 | 0.09613 | 0.19226 | -0.17395 | 0.2243 | 0.14191 | 0.19684 | -0.09613 | 0.35248 | 0.2655 | -122.1405 | 121.6461 | 0.036621 | 121.9162 | 122.0444 | -0.013733 | -0.32043 | 0.10986 | 0.27008 | 121.7239 | 122.1725 | 121.962 | 122.0123 | 121.9162 | 122.0856 | 122.0169 | -0.32043 | 122.0123 | 121.9162 | 122.0169 | 121.962 | 122.0856 | -0.32959 | -122.2961
1746.5781 | 122.0993 | -121.7743 | 0.14648 | 0.0026703 | 0.019521 | 0.017959 | 0.029728 | -0.0035313 | -0.0042277 | 0.0093012 | 0.027466 | 0.2243 | -0.21973 | 0.1236 | 0.018311 | 0.091553 | -0.045776 | 0.20142 | 0.29297 | -122.1451 | 121.5546 | 0.07782 | 121.8018 | 121.8979 | -0.12817 | -0.37079 | 0.14648 | 0.24719 | 121.7285 | 121.9757 | 121.7926 | 121.9986 | 121.8018 | 122.0673 | 121.8658 | -0.37079 | 121.9986 | 121.8018 | 121.8658 | 121.7926 | 122.0673 | -0.36621 | -122.2916
1748.2812 | 121.9986 | -121.8063 | 0.17395 | -0.0049592 | 0.01653 | 0.012405 | 0.023319 | -0.0054539 | -0.0040139 | 0.01101 | 0.086975 | 0.19684 | -0.1831 | 0.21515 | 0.11902 | 0.19226 | -0.10986 | 0.32501 | 0.25635 | -122.1313 | 121.6232 | 0.022888 | 121.8933 | 122.0215 | -0.054931 | -0.32501 | 0.082398 | 0.27008 | 121.6965 | 122.1313 | 121.9254 | 122.0032 | 121.8933 | 122.0627 | 121.9986 | -0.32501 | 122.0032 | 121.8933 | 121.9986 | 121.9254 | 122.0627 | -0.35706 | -122.3053
1750.0156 | 122.0673 | -121.7697 | 0.13733 | 0.0026703 | 0.015248 | 0.010269 | 0.031437 | -0.0026767 | -0.0085001 | 0.0084468 | 0.068665 | 0.21515 | -0.21515 | 0.15564 | 0.045776 | 0.1236 | -0.013733 | 0.2243 | 0.29297 | -122.1085 | 121.5546 | 0.07782 | 121.8384 | 121.9254 | -0.091553 | -0.33875 | 0.15564 | 0.28381 | 121.756 | 121.994 | 121.8155 | 121.9849 | 121.8384 | 122.0627 | 121.8933 | -0.33875 | 121.9849 | 121.8384 | 121.8933 | 121.8155 | 122.0627 | -0.35248 | -122.2458
1751.7031 | 122.081 | -121.788 | 0.13275 | 0.0103 | 0.016317 | 0.0094143 | 0.0293 | -0.00096767 | -0.0046549 | 0.011224 | 0.045776 | 0.21973 | -0.20599 | 0.16479 | 0.050354 | 0.10986 | 0.009155 | 0.25177 | 0.27008 | -122.1313 | 121.582 | 0.086976 | 121.8338 | 121.9528 | -0.082397 | -0.34332 | 0.13733 | 0.25177 | 121.7972 | 122.0398 | 121.8384 | 122.0078 | 121.8338 | 122.0581 | 121.8979 | -0.34332 | 122.0078 | 121.8338 | 121.8979 | 121.8384 | 122.0581 | -0.33875 | -122.2641
1753.4531 | 121.994 | -121.8292 | 0.16479 | -0.0049592 | 0.017812 | 0.012192 | 0.026951 | -0.0035313 | -0.0055093 | 0.0093012 | 0.13275 | 0.1831 | -0.15564 | 0.2243 | 0.13275 | 0.21515 | -0.17395 | 0.32501 | 0.25177 | -122.1497 | 121.6736 | 0.01831 | 121.962 | 122.0535 | -0.032044 | -0.32043 | 0.086975 | 0.28839 | 121.6553 | 122.1542 | 121.962 | 122.0123 | 121.962 | 122.081 | 122.0444 | -0.32043 | 122.0123 | 121.962 | 122.0444 | 121.962 | 122.081 | -0.32044 | -122.3145
1755.1406 | 122.0718 | -121.8246 | 0.16479 | -0.012589 | 0.017385 | 0.01326 | 0.024601 | -0.0037449 | -0.0057229 | 0.0097284 | 0.064087 | 0.17395 | -0.1831 | 0.15564 | 0.082397 | 0.16022 | -0.086975 | 0.26093 | 0.25635 | -122.1771 | 121.6415 | 0.009155 | 121.8887 | 121.9803 | -0.082398 | -0.35248 | 0.091553 | 0.24719 | 121.7377 | 122.0856 | 121.907 | 121.9986 | 121.8887 | 122.081 | 121.9849 | -0.35248 | 121.9986 | 121.8887 | 121.9849 | 121.907 | 122.081 | -0.3479 | -122.3419
1756.8906 | 122.1542 | -121.8018 | 0.15106 | 0.0026703 | 0.017385 | 0.011337 | 0.032505 | -0.0037449 | -0.0072183 | 0.0097284 | 0.013733 | 0.23804 | -0.19684 | 0.11902 | 0.013733 | 0.068665 | 0.009155 | 0.17395 | 0.27924 | -122.1863 | 121.6049 | 0.086975 | 121.8155 | 121.9208 | -0.13733 | -0.38452 | 0.12817 | 0.21057 | 121.8109 | 121.9757 | 121.8155 | 122.0398 | 121.8155 | 122.081 | 121.8704 | -0.38452 | 122.0398 | 121.8155 | 121.8704 | 121.8155 | 122.081 | -0.3479 | -122.3373
1758.6562 | 122.0627 | -121.8475 | 0.16937 | -0.0049592 | 0.018025 | 0.010483 | 0.02396 | -0.0043857 | -0.0059365 | 0.011437 | 0.064087 | 0.18768 | -0.16479 | 0.17853 | 0.086975 | 0.17395 | -0.11902 | 0.27466 | 0.25635 | -122.1909 | 121.6827 | 0.01831 | 121.9116 | 122.0261 | -0.082398 | -0.34332 | 0.086975 | 0.22888 | 121.7285 | 122.1222 | 121.9345 | 122.0352 | 121.9116 | 122.1039 | 122.0215 | -0.34332 | 122.0352 | 121.9116 | 122.0215 | 121.9345 | 122.1039 | -0.33417 | -122.3602
1760.4219 | 121.9986 | -121.8704 | 0.15564 | 0.0026703 | 0.016103 | 0.0087735 | 0.018406 | -0.0033175 | -0.0031595 | 0.0084468 | 0.1236 | 0.18768 | -0.1831 | 0.21057 | 0.10529 | 0.21515 | -0.16022 | 0.3067 | 0.23804 | -122.1542 | 121.6873 | 0.032043 | 121.994 | 122.081 | -0.050354 | -0.28381 | 0.082397 | 0.3067 | 121.7102 | 122.1771 | 121.9757 | 122.0581 | 121.994 | 122.1085 | 122.0856 | -0.28381 | 122.0581 | 121.994 | 122.0856 | 121.9757 | 122.1085 | -0.33874 | -122.3099
1762.125 | 122.0215 | -121.8384 | 0.15564 | -0.012589 | 0.014394 | 0.012192 | 0.015842 | -0.0054539 | -0.0055093 | 0.0075922 | 0.10071 | 0.20142 | -0.19684 | 0.21057 | 0.13275 | 0.19684 | -0.11902 | 0.33875 | 0.2655 | -122.1497 | 121.6415 | 0.045776 | 121.9391 | 122.049 | -0.022889 | -0.31128 | 0.10986 | 0.29755 | 121.7194 | 122.1771 | 121.9711 | 122.0398 | 121.9391 | 122.1039 | 122.0352 | -0.31128 | 122.0398 | 121.9391 | 122.0352 | 121.9711 | 122.1039 | -0.35248 | -122.3053
1763.875 | 122.0352 | -121.843 | 0.15564 | 0.0026703 | 0.015676 | 0.0083463 | 0.016056 | -0.0033175 | -0.0078591 | 0.0090876 | 0.09613 | 0.17853 | -0.19684 | 0.20142 | 0.10986 | 0.17853 | -0.068665 | 0.32959 | 0.27008 | -122.2 | 121.6461 | 0.022888 | 121.9391 | 122.0444 | -0.045777 | -0.35706 | 0.11444 | 0.29297 | 121.7743 | 122.1725 | 121.9528 | 122.0215 | 121.9391 | 122.113 | 122.0215 | -0.35706 | 122.0215 | 121.9391 | 122.0215 | 121.9528 | 122.113 | -0.35248 | -122.3557
1765.625 | 121.3715 | -121.1288 | 0.16022 | -0.0049592 | 0.018025 | 0.010483 | 0.015415 | -0.00075407 | -0.0074319 | 0.0050288 | 0.091553 | 0.1831 | -0.21057 | 0.19684 | 0.11444 | 0.16479 | -0.16479 | 0.27466 | 0.27924 | -121.3943 | 120.9183 | 0.022888 | 121.2204 | 121.3257 | -0.045776 | -0.2655 | 0.11902 | 0.30212 | 120.9641 | 121.4035 | 121.2433 | 121.3119 | 121.2204 | 121.4081 | 121.2936 | -0.2655 | 121.3119 | 121.2204 | 121.2936 | 121.2433 | 121.4081 | -0.37079 | -121.5546
1767.4062 | 121.9391 | -121.6965 | 0.15106 | 0.0103 | 0.016957 | 0.011764 | 0.012424 | -0.0028903 | -0.0055093 | 0.0043878 | 0.041199 | 0.19226 | -0.17853 | 0.15106 | 0.082397 | 0.14648 | -0.10529 | 0.27466 | 0.26093 | -122.0261 | 121.5179 | 0.041199 | 121.7377 | 121.8475 | -0.068665 | -0.32959 | 0.10986 | 0.21973 | 121.5912 | 121.9711 | 121.7789 | 121.8887 | 121.7377 | 121.9574 | 121.843 | -0.32959 | 121.8887 | 121.7377 | 121.843 | 121.7789 | 121.9574 | -0.32959 | -122.1771
1769.1094 | 121.8933 | -121.7377 | 0.14191 | -0.012589 | 0.018453 | 0.0085599 | 0.015415 | -0.0050265 | -0.0067911 | 0.0041742 | 0.10071 | 0.17395 | -0.1831 | 0.24261 | 0.15106 | 0.21057 | -0.16022 | 0.35248 | 0.25177 | -122.0444 | 121.5546 | 0.032043 | 121.8384 | 121.9803 | 0.009155 | -0.3067 | 0.10986 | 0.28381 | 121.5775 | 122.0901 | 121.8887 | 121.9116 | 121.8384 | 121.9894 | 121.9482 | -0.3067 | 121.9116 | 121.8384 | 121.9482 | 121.8887 | 121.9894 | -0.32501 | -122.1863
1770.8594 | 122.081 | -121.7606 | 0.13275 | -0.012589 | 0.020375 | 0.013046 | 0.023105 | -0.0020359 | -0.0048685 | 0.005456 | 0.032043 | 0.23346 | -0.21973 | 0.10986 | -0.004578 | 0.059509 | 0 | 0.16479 | 0.28381 | -122.113 | 121.5408 | 0.10071 | 121.7926 | 121.8704 | -0.13733 | -0.35248 | 0.15106 | 0.25177 | 121.7606 | 121.9254 | 121.756 | 121.994 | 121.7926 | 122.0444 | 121.8201 | -0.35248 | 121.994 | 121.7926 | 121.8201 | 121.756 | 122.0444 | -0.35248 | -122.2458
1772.625 | 121.994 | -121.7743 | 0.15106 | -0.012589 | 0.018666 | 0.012405 | 0.016697 | -0.0035313 | -0.0033731 | 0.0063104 | 0.045776 | 0.20142 | -0.1831 | 0.17395 | 0.073242 | 0.15106 | -0.1236 | 0.26093 | 0.26093 | -122.1405 | 121.5912 | 0.050354 | 121.8201 | 121.9482 | -0.07782 | -0.36621 | 0.10986 | 0.22888 | 121.6507 | 122.0352 | 121.8475 | 121.9757 | 121.8201 | 122.0352 | 121.9254 | -0.36621 | 121.9757 | 121.8201 | 121.9254 | 121.8475 | 122.0352 | -0.33417 | -122.2916
1774.3906 | 122.0901 | -121.7651 | 0.1236 | 0.0026703 | 0.016744 | 0.014541 | 0.020328 | -0.0045993 | -0.0089273 | 0.005456 | 0.009155 | 0.20142 | -0.22888 | 0.11444 | 0.009155 | 0.050354 | 0.009155 | 0.17395 | 0.29297 | -122.1268 | 121.5363 | 0.07782 | 121.7743 | 121.8796 | -0.11444 | -0.36163 | 0.16937 | 0.23804 | 121.7743 | 121.9391 | 121.7743 | 121.9666 | 121.7743 | 122.0581 | 121.8155 | -0.36163 | 121.9666 | 121.7743 | 121.8155 | 121.7743 | 122.0581 | -0.35248 | -122.2504
1776.0781 | 122.0169 | -121.8018 | 0.15564 | -0.0049592 | 0.015676 | 0.0094143 | 0.01456 | -0.0033175 | -0.0048685 | 0.006524 | 0.050354 | 0.19684 | -0.17853 | 0.17395 | 0.086975 | 0.17395 | -0.10986 | 0.28839 | 0.25635 | -122.1588 | 121.6232 | 0.041198 | 121.8521 | 121.9757 | -0.068665 | -0.35705 | 0.10071 | 0.22888 | 121.6919 | 122.0901 | 121.8887 | 121.9986 | 121.8521 | 122.0581 | 121.9757 | -0.35705 | 121.9986 | 121.8521 | 121.9757 | 121.8887 | 122.0581 | -0.33417 | -122.3145
1777.8281 | 122.0627 | -121.8018 | 0.15106 | -0.0049592 | 0.017598 | 0.014969 | 0.022251 | -0.0033175 | -0.0067911 | 0.0058832 | 0.041199 | 0.22888 | -0.23804 | 0.16022 | 0.050354 | 0.10529 | -0.018311 | 0.24261 | 0.27924 | -122.1359 | 121.5637 | 0.07782 | 121.843 | 121.962 | -0.10071 | -0.33417 | 0.12817 | 0.27924 | 121.7834 | 122.0444 | 121.8521 | 122.0306 | 121.843 | 122.081 | 121.907 | -0.33417 | 122.0306 | 121.843 | 121.907 | 121.8521 | 122.081 | -0.3891 | -122.287
1779.5938 | 122.0352 | -121.8155 | 0.14648 | -0.0049592 | 0.017171 | 0.0083463 | 0.013706 | -0.0050265 | -0.0035867 | 0.0050288 | 0.050354 | 0.17395 | -0.18768 | 0.16479 | 0.07782 | 0.16022 | -0.09613 | 0.25177 | 0.25177 | -122.1497 | 121.6278 | 0.027466 | 121.8658 | 121.9803 | -0.068664 | -0.33417 | 0.10529 | 0.23804 | 121.7194 | 122.0673 | 121.8933 | 121.9894 | 121.8658 | 122.0673 | 121.9757 | -0.33417 | 121.9894 | 121.8658 | 121.9757 | 121.8933 | 122.0673 | -0.33417 | -122.2961
1781.3594 | 122.1451 | -121.8063 | 0.11902 | 0.0026703 | 0.016957 | 0.0094143 | 0.022678 | -0.0022495 | -0.0070047 | 0.006524 | 0.004578 | 0.21057 | -0.22888 | 0.091553 | -0.009155 | 0.064087 | -0.009155 | 0.16022 | 0.29755 | -122.1451 | 121.5775 | 0.091552 | 121.8109 | 121.8979 | -0.12817 | -0.33875 | 0.17853 | 0.23346 | 121.7972 | 121.9666 | 121.7972 | 122.0169 | 121.8109 | 122.1039 | 121.8704 | -0.33875 | 122.0169 | 121.8109 | 121.8704 | 121.7972 | 122.1039 | -0.3479 | -122.2641
1783.0469 | 122.0078 | -121.8658 | 0.16479 | 0.0103 | 0.015889 | 0.012832 | 0.015629 | -0.0045993 | -0.0052957 | 0.0063104 | 0.10529 | 0.16479 | -0.19684 | 0.20599 | 0.11444 | 0.19226 | -0.17853 | 0.29755 | 0.24719 | -122.1588 | 121.669 | 0 | 121.9711 | 122.0718 | -0.050354 | -0.29297 | 0.082397 | 0.30212 | 121.6873 | 122.1634 | 121.9803 | 122.0306 | 121.9711 | 122.113 | 122.0581 | -0.29297 | 122.0306 | 121.9711 | 122.0581 | 121.9803 | 122.113 | -0.36163 | -122.3236
1784.7812 | 122.0169 | -121.8613 | 0.14191 | 0.0026703 | 0.018025 | 0.0096279 | 0.014988 | -0.0045993 | -0.0065775 | 0.0046014 | 0.10986 | 0.18768 | -0.19226 | 0.21973 | 0.13275 | 0.1831 | -0.10529 | 0.34332 | 0.27008 | -122.1863 | 121.669 | 0.045776 | 121.9711 | 122.081 | -0.009156 | -0.32501 | 0.12817 | 0.30212 | 121.756 | 122.2046 | 121.994 | 122.049 | 121.9711 | 122.1313 | 122.0444 | -0.32501 | 122.049 | 121.9711 | 122.0444 | 121.994 | 122.1313 | -0.33417 | -122.3282
1786.5469 | 122.1497 | -121.8292 | 0.12817 | 0.0103 | 0.016103 | 0.0070645 | 0.023746 | -0.0039585 | -0.0074319 | 0.0046014 | 0.036621 | 0.20599 | -0.22888 | 0.12817 | 0.009155 | 0.073242 | -0.013733 | 0.17395 | 0.27466 | -122.1634 | 121.6003 | 0.07782 | 121.8658 | 121.9574 | -0.11902 | -0.33417 | 0.14648 | 0.2655 | 121.8155 | 122.0032 | 121.8384 | 122.0352 | 121.8658 | 122.1039 | 121.9025 | -0.33417 | 122.0352 | 121.8658 | 121.9025 | 121.8384 | 122.1039 | -0.35706 | -122.2916
1788.25 | 122.0993 | -121.8338 | 0.1236 | 0.0026703 | 0.017385 | 0.010483 | 0.022465 | -0.0048129 | -0.0087137 | 0.0058832 | 0.045776 | 0.19684 | -0.21973 | 0.16937 | 0.068665 | 0.11902 | -0.036621 | 0.26093 | 0.2655 | -122.1954 | 121.6141 | 0.073242 | 121.8796 | 122.0032 | -0.054931 | -0.36163 | 0.14191 | 0.2655 | 121.7972 | 122.0947 | 121.9025 | 122.0306 | 121.8796 | 122.0993 | 121.9528 | -0.36163 | 122.0306 | 121.8796 | 121.9528 | 121.9025 | 122.0993 | -0.34332 | -122.319
1789.9375 | 122.0032 | -121.8796 | 0.16479 | -0.0049592 | 0.015035 | 0.0096279 | 0.01392 | -0.0041721 | -0.0029459 | 0.0058832 | 0.1236 | 0.16937 | -0.18768 | 0.21973 | 0.13275 | 0.21973 | -0.13733 | 0.35248 | 0.25177 | -122.2046 | 121.6919 | 0.004578 | 122.0032 | 122.0993 | -0.032044 | -0.32501 | 0.086975 | 0.31128 | 121.7422 | 122.2321 | 122.0123 | 122.049 | 122.0032 | 122.1313 | 122.0993 | -0.32501 | 122.049 | 122.0032 | 122.0993 | 122.0123 | 122.1313 | -0.35248 | -122.3694
1791.6875 | 122.0581 | -121.8842 | 0.13733 | 0.0026703 | 0.018666 | 0.0083463 | 0.017765 | -0.0045993 | -0.0065775 | 0.0052424 | 0.09613 | 0.17395 | -0.18768 | 0.19684 | 0.10071 | 0.16937 | -0.036621 | 0.30212 | 0.26093 | -122.1954 | 121.6965 | 0.036621 | 121.9803 | 122.081 | -0.036621 | -0.31128 | 0.1236 | 0.28381 | 121.8475 | 122.1863 | 121.9849 | 122.0581 | 121.9803 | 122.1451 | 122.0535 | -0.31128 | 122.0581 | 121.9803 | 122.0535 | 121.9849 | 122.1451 | -0.32501 | -122.3328
1793.4375 | 122.1176 | -121.875 | 0.13275 | -0.0049592 | 0.019521 | 0.012192 | 0.020542 | -0.0043857 | -0.0067911 | 0.0043878 | 0.064087 | 0.21973 | -0.21973 | 0.16479 | 0.054932 | 0.10986 | -0.013733 | 0.24261 | 0.27466 | -122.2321 | 121.6553 | 0.086976 | 121.9391 | 122.0398 | -0.077819 | -0.35706 | 0.14191 | 0.28381 | 121.8613 | 122.1176 | 121.9299 | 122.0947 | 121.9391 | 122.1497 | 121.9849 | -0.35706 | 122.0947 | 121.9391 | 121.9849 | 121.9299 | 122.1497 | -0.35248 | -122.3648
1795.125 | 122.1817 | -121.843 | 0.10529 | 0.0103 | 0.017812 | 0.013901 | 0.01691 | -0.0050265 | -0.0042277 | 0.006524 | -0.009155 | 0.2243 | -0.21515 | 0.11444 | 0.022888 | 0.068665 | 0.07782 | 0.20599 | 0.27466 | -122.2733 | 121.6278 | 0.11902 | 121.8338 | 121.9574 | -0.082398 | -0.4303 | 0.16937 | 0.20599 | 121.9208 | 122.049 | 121.8658 | 122.0673 | 121.8338 | 122.1176 | 121.9116 | -0.4303 | 122.0673 | 121.8338 | 121.9116 | 121.8658 | 122.1176 | -0.32044 | -122.3785
1796.875 | 122.168 | -121.8613 | 0.1236 | 0.0026703 | 0.016317 | 0.0092007 | 0.017551 | -0.0028903 | -0.0033731 | 0.006524 | 0.009155 | 0.21515 | -0.23346 | 0.11444 | 0.004578 | 0.09613 | -0.045776 | 0.1831 | 0.27466 | -122.2137 | 121.6278 | 0.091553 | 121.8704 | 121.9757 | -0.11902 | -0.35248 | 0.15106 | 0.24261 | 121.8155 | 122.0444 | 121.8658 | 122.0764 | 121.8704 | 122.1359 | 121.9574 | -0.35248 | 122.0764 | 121.8704 | 121.9574 | 121.8658 | 122.1359 | -0.35706 | -122.3373
1798.5625 | 122.1085 | -121.8475 | 0.15564 | -0.012589 | 0.017171 | 0.0094143 | 0.01392 | -0.0035313 | -0.0061503 | 0.0050288 | 0.050354 | 0.19684 | -0.20142 | 0.14648 | 0.09613 | 0.15564 | -0.10071 | 0.28381 | 0.23346 | -122.2183 | 121.6461 | 0.041198 | 121.8979 | 121.994 | -0.05951 | -0.37079 | 0.077819 | 0.25177 | 121.7468 | 122.1313 | 121.9437 | 122.0444 | 121.8979 | 122.081 | 122.0032 | -0.37079 | 122.0444 | 121.8979 | 122.0032 | 121.9437 | 122.081 | -0.35706 | -122.374
1800.3125 | 122.0901 | -121.9025 | 0.15564 | -0.0049592 | 0.015676 | 0.012192 | 0.016483 | -0.0035313 | -0.0059365 | 0.005456 | 0.073242 | 0.17853 | -0.17395 | 0.16479 | 0.086975 | 0.16479 | -0.14191 | 0.27924 | 0.24261 | -122.1909 | 121.7285 | 0.022888 | 121.9757 | 122.0673 | -0.068665 | -0.28839 | 0.086975 | 0.24719 | 121.7606 | 122.1817 | 121.9894 | 122.081 | 121.9757 | 122.1451 | 122.0673 | -0.28839 | 122.081 | 121.9757 | 122.0673 | 121.9894 | 122.1451 | -0.32959 | -122.3465
1802 | 122.081 | -121.9162 | 0.14648 | 0.0026703 | 0.017812 | 0.0077053 | 0.015415 | -0.0043857 | -0.0061503 | 0.0052424 | 0.10529 | 0.19684 | -0.16479 | 0.23346 | 0.11444 | 0.17395 | -0.082397 | 0.31586 | 0.24719 | -122.2366 | 121.7514 | 0.050354 | 122.0215 | 122.1497 | -0.032043 | -0.32043 | 0.10071 | 0.27008 | 121.8338 | 122.2321 | 122.0306 | 122.113 | 122.0215 | 122.1634 | 122.0901 | -0.32043 | 122.113 | 122.0215 | 122.0901 | 122.0306 | 122.1634 | -0.31128 | -122.3831
1803.75 | 122.1771 | -121.8933 | 0.1236 | 0.0103 | 0.017812 | 0.014755 | 0.022465 | -0.0016087 | -0.0089273 | 0.0058832 | 0.068665 | 0.18768 | -0.21057 | 0.16479 | 0.041199 | 0.10071 | -0.032043 | 0.21973 | 0.27008 | -122.2275 | 121.6827 | 0.064087 | 121.962 | 122.0581 | -0.082397 | -0.33417 | 0.14649 | 0.27924 | 121.8613 | 122.113 | 121.9345 | 122.081 | 121.962 | 122.1634 | 121.994 | -0.33417 | 122.081 | 121.962 | 121.994 | 121.9345 | 122.1634 | -0.33417 | -122.3511
1805.4531 | 122.1817 | -121.8933 | 0.12817 | 0.0103 | 0.016317 | 0.012405 | 0.021396 | -0.0039585 | -0.0057229 | 0.0069514 | 0.032043 | 0.21057 | -0.2243 | 0.12817 | 0.018311 | 0.07782 | -0.018311 | 0.18768 | 0.26093 | -122.2412 | 121.669 | 0.082397 | 121.9254 | 122.0215 | -0.10986 | -0.3479 | 0.13275 | 0.25635 | 121.875 | 122.081 | 121.9116 | 122.1039 | 121.9254 | 122.1542 | 121.9711 | -0.3479 | 122.1039 | 121.9254 | 121.9711 | 121.9116 | 122.1542 | -0.35248 | -122.3694
1807.2188 | 122.1634 | -121.907 | 0.13275 | -0.0049592 | 0.015248 | 0.010696 | 0.022037 | -0.0035313 | -0.0063639 | 0.0086604 | 0.050354 | 0.19684 | -0.21973 | 0.14191 | 0.032043 | 0.10529 | -0.036621 | 0.19684 | 0.27924 | -122.2504 | 121.6873 | 0.064087 | 121.9574 | 122.049 | -0.10071 | -0.34332 | 0.14648 | 0.27008 | 121.8704 | 122.1039 | 121.9391 | 122.1039 | 121.9574 | 122.1863 | 122.0123 | -0.34332 | 122.1039 | 121.9574 | 122.0123 | 121.9391 | 122.1863 | -0.35248 | -122.3831
1808.9688 | 122.2046 | -121.8933 | 0.11902 | -0.012589 | 0.020162 | 0.010269 | 0.021824 | -0.0024631 | -0.0057229 | 0.0058832 | 0.041199 | 0.20599 | -0.23804 | 0.09613 | -0.004578 | 0.059509 | -0.013733 | 0.17853 | 0.27466 | -122.2916 | 121.6553 | 0.086975 | 121.9345 | 121.9894 | -0.1236 | -0.39825 | 0.15564 | 0.27924 | 121.8796 | 122.0718 | 121.8887 | 122.0993 | 121.9345 | 122.168 | 121.9528 | -0.39825 | 122.0993 | 121.9345 | 121.9528 | 121.8887 | 122.168 | -0.35706 | -122.4106
1810.6562 | 122.0947 | -121.9391 | 0.14191 | -0.012589 | 0.016103 | 0.010055 | 0.012424 | -0.0052401 | -0.0057229 | 0.006524 | 0.091553 | 0.1831 | -0.17395 | 0.17853 | 0.086975 | 0.19226 | -0.16937 | 0.28839 | 0.24261 | -122.2412 | 121.7651 | 0.041198 | 122.0306 | 122.1176 | -0.054932 | -0.30212 | 0.10071 | 0.2655 | 121.7697 | 122.2275 | 122.0261 | 122.1222 | 122.0306 | 122.1817 | 122.1313 | -0.30212 | 122.1222 | 122.0306 | 122.1313 | 122.0261 | 122.1817 | -0.31586 | -122.3831
1812.4219 | 122.1725 | -121.9025 | 0.1236 | 0.0026703 | 0.016317 | 0.0098417 | 0.019901 | -0.0033175 | -0.0059365 | 0.0069514 | 0.068665 | 0.20599 | -0.21973 | 0.14648 | 0.027466 | 0.12817 | -0.036621 | 0.24261 | 0.2655 | -122.2412 | 121.6827 | 0.082398 | 121.9711 | 122.049 | -0.09613 | -0.33875 | 0.14191 | 0.28839 | 121.8658 | 122.1451 | 121.9299 | 122.1085 | 121.9711 | 122.168 | 122.0306 | -0.33875 | 122.1085 | 121.9711 | 122.0306 | 121.9299 | 122.168 | -0.34332 | -122.3648
1814.1719 | 122.2046 | -121.8933 | 0.09613 | -0.0049592 | 0.018666 | 0.0087735 | 0.017551 | -0.0048129 | -0.0059365 | 0.0060968 | 0 | 0.21515 | -0.20599 | 0.10529 | 0.022888 | 0.073242 | 0.050354 | 0.21057 | 0.27924 | -122.3053 | 121.6873 | 0.11902 | 121.8933 | 121.9986 | -0.073242 | -0.41199 | 0.18311 | 0.20599 | 121.9437 | 122.1039 | 121.9162 | 122.1085 | 121.8933 | 122.1725 | 121.9666 | -0.41199 | 122.1085 | 121.8933 | 121.9666 | 121.9162 | 122.1725 | -0.30212 | -122.4014
1815.9219 | 122.0718 | -121.9254 | 0.15564 | -0.012589 | 0.014394 | 0.011764 | 0.013279 | -0.0050265 | -0.0061503 | 0.0056696 | 0.11444 | 0.15564 | -0.19226 | 0.22888 | 0.13733 | 0.20142 | -0.13275 | 0.36163 | 0.23346 | -122.2504 | 121.7331 | 0 | 122.0398 | 122.1542 | -0.018311 | -0.32501 | 0.077819 | 0.3067 | 121.7926 | 122.287 | 122.0627 | 122.081 | 122.0398 | 122.1588 | 122.1268 | -0.32501 | 122.081 | 122.0398 | 122.1268 | 122.0627 | 122.1588 | -0.3479 | -122.406
1817.625 | 122.0856 | -121.9482 | 0.15564 | -0.0049592 | 0.018453 | 0.012405 | 0.015201 | -0.0069491 | -0.0050821 | 0.0069514 | 0.10529 | 0.17853 | -0.16937 | 0.22888 | 0.13275 | 0.2243 | -0.12817 | 0.35706 | 0.24261 | -122.2824 | 121.7789 | 0.022888 | 122.0535 | 122.1771 | -0.022889 | -0.33417 | 0.086975 | 0.27466 | 121.8201 | 122.3053 | 122.081 | 122.1268 | 122.0535 | 122.1909 | 122.1725 | -0.33417 | 122.1268 | 122.0535 | 122.1725 | 122.081 | 122.1909 | -0.32501 | -122.4381
1819.375 | 122.2 | -121.9254 | 0.11444 | 0.0026703 | 0.017598 | 0.011123 | 0.020542 | -0.0039585 | -0.0093545 | 0.0046014 | 0.032043 | 0.20599 | -0.21515 | 0.14648 | 0.050354 | 0.10071 | 0 | 0.23804 | 0.28381 | -122.287 | 121.7102 | 0.091553 | 121.9574 | 122.0718 | -0.064087 | -0.36163 | 0.16937 | 0.24719 | 121.9254 | 122.1634 | 121.9757 | 122.1313 | 121.9574 | 122.2092 | 122.0261 | -0.36163 | 122.1313 | 121.9574 | 122.0261 | 121.9757 | 122.2092 | -0.32959 | -122.4014
1821.0781 | 122.2412 | -121.907 | 0.11444 | -0.0049592 | 0.016744 | 0.0085599 | 0.019687 | -0.0031039 | -0.0055093 | 0.0084468 | -0.022888 | 0.21057 | -0.2243 | 0.082397 | -0.009155 | 0.073242 | 0.004578 | 0.16022 | 0.27466 | -122.287 | 121.6827 | 0.09613 | 121.8842 | 121.9894 | -0.1236 | -0.37994 | 0.16022 | 0.20142 | 121.9116 | 122.0673 | 121.8979 | 122.1176 | 121.8842 | 122.1817 | 121.9803 | -0.37994 | 122.1176 | 121.8842 | 121.9803 | 121.8979 | 122.1817 | -0.33875 | -122.4014
1822.8281 | 122.2549 | -121.9208 | 0.12817 | -0.012589 | 0.019307 | 0.01091 | 0.020969 | -0.0045993 | -0.0061503 | 0.0067378 | 0.009155 | 0.21515 | -0.23346 | 0.12817 | 0.013733 | 0.09613 | 0.032043 | 0.21973 | 0.25635 | -122.3373 | 121.6873 | 0.086975 | 121.9299 | 122.049 | -0.11444 | -0.41656 | 0.12817 | 0.24261 | 121.9528 | 122.1405 | 121.9345 | 122.1359 | 121.9299 | 122.1771 | 122.0169 | -0.41656 | 122.1359 | 121.9299 | 122.0169 | 121.9345 | 122.1771 | -0.36163 | -122.4655
1824.5938 | 122.2046 | -121.9437 | 0.11902 | 0.0026703 | 0.01653 | 0.011764 | 0.022037 | -0.0045993 | -0.0061503 | 0.0067378 | 0.050354 | 0.18768 | -0.20142 | 0.16022 | 0.064087 | 0.11902 | -0.032043 | 0.25635 | 0.27008 | -122.3099 | 121.7422 | 0.068664 | 121.994 | 122.1039 | -0.054932 | -0.36621 | 0.15106 | 0.25177 | 121.9116 | 122.2 | 122.0078 | 122.1313 | 121.994 | 122.2137 | 122.0627 | -0.36621 | 122.1313 | 121.994 | 122.0627 | 122.0078 | 122.2137 | -0.32044 | -122.4289
1826.2969 | 122.1497 | -121.9711 | 0.14648 | -0.012589 | 0.014821 | 0.0064237 | 0.011143 | -0.0067355 | -0.0044413 | 0.0050288 | 0.045776 | 0.19684 | -0.18768 | 0.16479 | 0.09613 | 0.17395 | -0.09613 | 0.29755 | 0.25177 | -122.319 | 121.7834 | 0.050354 | 122.0169 | 122.1359 | -0.050354 | -0.3479 | 0.10529 | 0.23346 | 121.875 | 122.2687 | 122.0673 | 122.168 | 122.0169 | 122.2229 | 122.1451 | -0.3479 | 122.168 | 122.0169 | 122.1451 | 122.0673 | 122.2229 | -0.33417 | -122.4655
1829.4688 | 122.2687 | -121.9254 | 0.12817 | 0.0103 | 0.018239 | 0.010696 | 0.016269 | -0.0054539 | -0.0063639 | 0.0052424 | -0.009155 | 0.2243 | -0.23346 | 0.10071 | 0 | 0.068665 | 0.054932 | 0.19226 | 0.28381 | -122.3373 | 121.6919 | 0.09613 | 121.9162 | 122.0261 | -0.12817 | -0.41199 | 0.15564 | 0.2243 | 121.9803 | 122.1176 | 121.9254 | 122.1497 | 121.9162 | 122.2092 | 121.994 | -0.41199 | 122.1497 | 121.9162 | 121.994 | 121.9254 | 122.2092 | -0.36163 | -122.4655
1833.4531 | 122.2458 | -121.962 | 0.1236 | 0.0103 | 0.015248 | 0.0085599 | 0.021824 | -0.0026767 | -0.0070047 | 0.0056696 | 0.036621 | 0.21973 | -0.2243 | 0.15564 | 0.045776 | 0.10529 | 0 | 0.23346 | 0.27924 | -122.3053 | 121.7377 | 0.096131 | 121.9986 | 122.1176 | -0.07782 | -0.34332 | 0.15564 | 0.26093 | 121.962 | 122.1954 | 122.0078 | 122.1817 | 121.9986 | 122.2412 | 122.0673 | -0.34332 | 122.1817 | 121.9986 | 122.0673 | 122.0078 | 122.2412 | -0.3479 | -122.4289
1839.6406 | 122.1634 | -122.0032 | 0.16937 | -0.012589 | 0.019307 | 0.012832 | 0.018406 | -0.0043857 | -0.0033731 | 0.0056696 | 0.11902 | 0.16937 | -0.17853 | 0.20599 | 0.11444 | 0.20599 | -0.18768 | 0.31586 | 0.2243 | -122.3328 | 121.8246 | 0 | 122.1222 | 122.2092 | -0.054932 | -0.32959 | 0.054931 | 0.29755 | 121.8155 | 122.319 | 122.1176 | 122.1725 | 122.1222 | 122.2275 | 122.2092 | -0.32959 | 122.1725 | 122.1222 | 122.2092 | 122.1176 | 122.2275 | -0.3479 | -122.5021
1841.4844 | 122.1588 | -121.994 | 0.1236 | 0.0103 | 0.015676 | 0.0098417 | 0.015842 | -0.0031039 | -0.0050821 | 0.0073786 | 0.10071 | 0.16937 | -0.17853 | 0.23804 | 0.14191 | 0.21057 | -0.1236 | 0.33875 | 0.25177 | -122.3007 | 121.8155 | 0.045777 | 122.0947 | 122.2321 | 0.018311 | -0.3067 | 0.12817 | 0.27924 | 121.8704 | 122.3328 | 122.1359 | 122.1634 | 122.0947 | 122.2458 | 122.2046 | -0.3067 | 122.1634 | 122.0947 | 122.2046 | 122.1359 | 122.2458 | -0.30212 | -122.4243
1843.1875 | 122.1771 | -122.0169 | 0.14648 | -0.0049592 | 0.015676 | 0.0094143 | 0.018619 | -0.0033175 | -0.0061503 | 0.0069514 | 0.10529 | 0.16479 | -0.17395 | 0.21973 | 0.10529 | 0.20142 | -0.1831 | 0.31128 | 0.23346 | -122.3099 | 121.843 | 0.018311 | 122.1222 | 122.2366 | -0.041198 | -0.29297 | 0.086975 | 0.27924 | 121.8338 | 122.3282 | 122.1222 | 122.1817 | 122.1222 | 122.2504 | 122.2183 | -0.29297 | 122.1817 | 122.1222 | 122.2183 | 122.1222 | 122.2504 | -0.32043 | -122.4564
1844.9375 | 122.2092 | -122.0261 | 0.16022 | -0.0049592 | 0.015248 | 0.010055 | 0.016056 | -0.0056675 | -0.0061503 | 0.0067378 | 0.09613 | 0.17853 | -0.16479 | 0.18768 | 0.091553 | 0.16479 | -0.15106 | 0.28381 | 0.24261 | -122.3099 | 121.8613 | 0.018311 | 122.1222 | 122.2137 | -0.068664 | -0.28381 | 0.082398 | 0.26092 | 121.875 | 122.3099 | 122.1176 | 122.2046 | 122.1222 | 122.2687 | 122.1909 | -0.28381 | 122.2046 | 122.1222 | 122.1909 | 122.1176 | 122.2687 | -0.32501 | -122.4701
1846.7031 | 122.2595 | -121.9894 | 0.1236 | -0.012589 | 0.016957 | 0.011551 | 0.019047 | -0.0035313 | -0.0072183 | 0.0052424 | 0.036621 | 0.19684 | -0.20142 | 0.12817 | 0.032043 | 0.082397 | 0.013733 | 0.2243 | 0.2655 | -122.3465 | 121.788 | 0.073242 | 122.0261 | 122.1176 | -0.091553 | -0.35706 | 0.14191 | 0.23804 | 122.0032 | 122.2137 | 122.0215 | 122.1863 | 122.0261 | 122.2549 | 122.0718 | -0.35706 | 122.1863 | 122.0261 | 122.0718 | 122.0215 | 122.2549 | -0.32501 | -122.4701
1848.4688 | 122.2046 | -122.0078 | 0.13733 | -0.0049592 | 0.016103 | 0.013901 | 0.020756 | -0.0033175 | -0.0067911 | 0.0075922 | 0.09613 | 0.16937 | -0.1831 | 0.2243 | 0.10071 | 0.19684 | -0.17853 | 0.28839 | 0.23346 | -122.3236 | 121.8246 | 0.032044 | 122.1039 | 122.2321 | -0.036621 | -0.31586 | 0.09613 | 0.27924 | 121.8292 | 122.2961 | 122.1085 | 122.1771 | 122.1039 | 122.2412 | 122.2046 | -0.31586 | 122.1771 | 122.1039 | 122.2046 | 122.1085 | 122.2412 | -0.32043 | -122.4609
1850.1562 | 122.168 | -122.0352 | 0.14191 | -0.012589 | 0.015248 | 0.012832 | 0.015415 | -0.0054539 | -0.0059365 | 0.006524 | 0.11444 | 0.16479 | -0.1831 | 0.23804 | 0.13733 | 0.21515 | -0.14648 | 0.3479 | 0.23804 | -122.3328 | 121.8521 | 0.022888 | 122.1497 | 122.2733 | -0.004578 | -0.29755 | 0.09613 | 0.29755 | 121.8887 | 122.3831 | 122.1725 | 122.2 | 122.1497 | 122.2733 | 122.2504 | -0.29755 | 122.2 | 122.1497 | 122.2504 | 122.1725 | 122.2733 | -0.32501 | -122.4747
1851.8438 | 122.2321 | -122.0398 | 0.16022 | -0.0049592 | 0.016744 | 0.013901 | 0.01691 | -0.0028903 | -0.0052957 | 0.008874 | 0.064087 | 0.15106 | -0.18768 | 0.17853 | 0.073242 | 0.15564 | -0.14191 | 0.27008 | 0.25635 | -122.3511 | 121.8521 | -0.009155 | 122.1039 | 122.2183 | -0.086975 | -0.31128 | 0.096131 | 0.25177 | 121.8979 | 122.3099 | 122.113 | 122.1909 | 122.1039 | 122.2961 | 122.1954 | -0.31128 | 122.1909 | 122.1039 | 122.1954 | 122.113 | 122.2961 | -0.3479 | -122.5113
1853.5938 | 122.2641 | -122.0078 | 0.13275 | 0.0026703 | 0.016317 | 0.012192 | 0.019474 | -0.0037449 | -0.0044413 | 0.0048152 | 0.064087 | 0.20142 | -0.19684 | 0.15106 | 0.032043 | 0.086975 | 0.018311 | 0.24261 | 0.24719 | -122.3877 | 121.8109 | 0.068665 | 122.0718 | 122.1588 | -0.10071 | -0.37994 | 0.11444 | 0.26093 | 122.0261 | 122.2504 | 122.0398 | 122.2092 | 122.0718 | 122.2549 | 122.0947 | -0.37994 | 122.2092 | 122.0718 | 122.0947 | 122.0398 | 122.2549 | -0.32959 | -122.5204
1855.2812 | 122.287 | -121.994 | 0.12817 | -0.0049592 | 0.016957 | 0.014328 | 0.020542 | -0.0031039 | -0.0085001 | 0.0075922 | 0.018311 | 0.21515 | -0.23804 | 0.13275 | 0.004578 | 0.086975 | 0.022888 | 0.22888 | 0.27466 | -122.3831 | 121.756 | 0.086975 | 122.0123 | 122.1268 | -0.1236 | -0.3891 | 0.14648 | 0.25635 | 122.0169 | 122.2229 | 121.9986 | 122.2092 | 122.0123 | 122.2687 | 122.081 | -0.3891 | 122.2092 | 122.0123 | 122.081 | 121.9986 | 122.2687 | -0.36621 | -122.5113
1857.0312 | 122.3373 | -122.0306 | 0.11444 | -0.0049592 | 0.017598 | 0.010055 | 0.019901 | -0.0011813 | -0.0074319 | 0.0067378 | 0 | 0.21515 | -0.22888 | 0.091553 | 0 | 0.068665 | -0.013733 | 0.15564 | 0.27008 | -122.3877 | 121.8018 | 0.10071 | 122.0306 | 122.1222 | -0.11444 | -0.35705 | 0.15564 | 0.22888 | 122.0169 | 122.1863 | 122.0306 | 122.2458 | 122.0306 | 122.3007 | 122.0993 | -0.35705 | 122.2458 | 122.0306 | 122.0993 | 122.0306 | 122.3007 | -0.34332 | -122.5021
1858.7969 | 122.3282 | -122.0718 | 0.11902 | -0.0049592 | 0.018666 | 0.012192 | 0.020969 | -0.0011813 | -0.0059365 | 0.0095148 | 0.009155 | 0.21515 | -0.22888 | 0.09613 | 0.013733 | 0.064087 | -0.004578 | 0.14191 | 0.27924 | -122.4152 | 121.843 | 0.09613 | 122.081 | 122.168 | -0.10529 | -0.34332 | 0.16022 | 0.23804 | 122.0673 | 122.2137 | 122.0856 | 122.287 | 122.081 | 122.3511 | 122.1359 | -0.34332 | 122.287 | 122.081 | 122.1359 | 122.0856 | 122.3511 | -0.3479 | -122.5342
1860.5625 | 122.3053 | -122.0764 | 0.1236 | -0.0049592 | 0.017385 | 0.012619 | 0.016056 | -0.0052401 | -0.0038003 | 0.007165 | 0.018311 | 0.19226 | -0.21973 | 0.1236 | 0.036621 | 0.073242 | 0.032043 | 0.21515 | 0.27008 | -122.4335 | 121.8567 | 0.068665 | 122.0947 | 122.2 | -0.086975 | -0.35706 | 0.14649 | 0.23804 | 122.1085 | 122.2916 | 122.113 | 122.2687 | 122.0947 | 122.3465 | 122.1497 | -0.35706 | 122.2687 | 122.0947 | 122.1497 | 122.113 | 122.3465 | -0.34332 | -122.5571
1862.2656 | 122.3099 | -122.0306 | 0.11902 | 0.0026703 | 0.016744 | 0.012619 | 0.019687 | -0.0035313 | -0.0067911 | 0.0093012 | 0.004578 | 0.21515 | -0.22888 | 0.13275 | 0.032043 | 0.10529 | -0.082397 | 0.20142 | 0.23804 | -122.4014 | 121.8018 | 0.09613 | 122.0352 | 122.1634 | -0.086976 | -0.37079 | 0.11902 | 0.23346 | 121.9482 | 122.2321 | 122.0627 | 122.2458 | 122.0352 | 122.2687 | 122.1359 | -0.37079 | 122.2458 | 122.0352 | 122.1359 | 122.0627 | 122.2687 | -0.3479 | -122.5204
1864.0156 | 122.3511 | -122.0306 | 0.10986 | 0.0026703 | 0.017598 | 0.010269 | 0.016697 | -0.0048129 | -0.0055093 | 0.008233 | -0.009155 | 0.22888 | -0.23346 | 0.09613 | 0.018311 | 0.059509 | 0.059509 | 0.20142 | 0.28381 | -122.4335 | 121.7972 | 0.11902 | 122.0215 | 122.1268 | -0.091552 | -0.40283 | 0.17395 | 0.2243 | 122.0901 | 122.2321 | 122.049 | 122.2595 | 122.0215 | 122.3145 | 122.0901 | -0.40283 | 122.2595 | 122.0215 | 122.0901 | 122.049 | 122.3145 | -0.34332 | -122.5433
1865.7031 | 122.3007 | -122.0764 | 0.11902 | 0.0026703 | 0.017385 | 0.0066373 | 0.019687 | -0.0013949 | -0.0082865 | 0.0086604 | 0.059509 | 0.20142 | -0.21057 | 0.14191 | 0.045776 | 0.11444 | -0.041199 | 0.22888 | 0.25177 | -122.4197 | 121.8658 | 0.082397 | 122.1359 | 122.2183 | -0.073243 | -0.34332 | 0.13275 | 0.27008 | 122.0352 | 122.3053 | 122.1222 | 122.2778 | 122.1359 | 122.3282 | 122.1909 | -0.34332 | 122.2778 | 122.1359 | 122.1909 | 122.1222 | 122.3282 | -0.32959 | -122.5388
1867.4688 | 122.2412 | -122.0993 | 0.15106 | -0.012589 | 0.016957 | 0.01091 | 0.016483 | -0.0016087 | -0.0059365 | 0.0078058 | 0.10529 | 0.15106 | -0.1831 | 0.20599 | 0.1236 | 0.19684 | -0.19684 | 0.29755 | 0.21515 | -122.3923 | 121.9162 | 0 | 122.2046 | 122.3053 | -0.027466 | -0.29297 | 0.064087 | 0.28839 | 121.9025 | 122.3969 | 122.2229 | 122.2504 | 122.2046 | 122.3145 | 122.2961 | -0.29297 | 122.2504 | 122.2046 | 122.2961 | 122.2229 | 122.3145 | -0.33417 | -122.5433
1869.1719 | 122.3145 | -122.0352 | 0.1236 | -0.0049592 | 0.018025 | 0.010483 | 0.018619 | -0.0045993 | -0.0059365 | 0.006524 | 0.027466 | 0.20599 | -0.21973 | 0.14191 | 0.045776 | 0.10529 | -0.004578 | 0.23346 | 0.26093 | -122.4289 | 121.8155 | 0.082398 | 122.0627 | 122.1771 | -0.07782 | -0.39368 | 0.13733 | 0.24719 | 122.0306 | 122.2687 | 122.081 | 122.2412 | 122.0627 | 122.2961 | 122.1405 | -0.39368 | 122.2412 | 122.0627 | 122.1405 | 122.081 | 122.2961 | -0.34332 | -122.5525
1870.9219 | 122.2412 | -122.0764 | 0.14648 | -0.012589 | 0.015676 | 0.010696 | 0.011143 | -0.0052401 | -0.0038003 | 0.0043878 | 0.091553 | 0.15106 | -0.17853 | 0.21515 | 0.12817 | 0.21973 | -0.13733 | 0.34332 | 0.22888 | -122.4289 | 121.8979 | 0.004578 | 122.168 | 122.2916 | -0.01831 | -0.35248 | 0.082398 | 0.27008 | 121.9391 | 122.4197 | 122.2046 | 122.2275 | 122.168 | 122.3053 | 122.2961 | -0.35248 | 122.2275 | 122.168 | 122.2961 | 122.2046 | 122.3053 | -0.32501 | -122.5754
1872.625 | 122.3694 | -122.0581 | 0.13275 | -0.0049592 | 0.014821 | 0.010055 | 0.015842 | -0.0052401 | -0.0057229 | 0.0075922 | 0 | 0.19226 | -0.2243 | 0.10986 | 0.009155 | 0.059509 | 0.054932 | 0.20599 | 0.28381 | -122.4289 | 121.8338 | 0.05951 | 122.0581 | 122.168 | -0.1236 | -0.37079 | 0.15106 | 0.2243 | 122.113 | 122.2641 | 122.0673 | 122.2504 | 122.0581 | 122.3419 | 122.1176 | -0.37079 | 122.2504 | 122.0581 | 122.1176 | 122.0673 | 122.3419 | -0.35706 | -122.5616
1874.3906 | 122.3557 | -122.0856 | 0.11902 | 0.0026703 | 0.015248 | 0.01091 | 0.016483 | -0.0048129 | -0.0072183 | 0.0060968 | 0.027466 | 0.19684 | -0.21057 | 0.11902 | 0.018311 | 0.073242 | 0.032043 | 0.22888 | 0.27466 | -122.4106 | 121.875 | 0.077819 | 122.113 | 122.2046 | -0.10071 | -0.32501 | 0.15564 | 0.23804 | 122.1176 | 122.3145 | 122.1039 | 122.2824 | 122.113 | 122.3602 | 122.1588 | -0.32501 | 122.2824 | 122.113 | 122.1588 | 122.1039 | 122.3602 | -0.32959 | -122.5296
1876.1562 | 122.2641 | -122.0764 | 0.16937 | -0.012589 | 0.016744 | 0.014328 | 0.014133 | -0.0026767 | -0.0076455 | 0.007165 | 0.082397 | 0.1831 | -0.20599 | 0.20599 | 0.027466 | 0.11444 | -0.1236 | 0.32501 | 0.24261 | -122.4106 | 121.8704 | 0.013732 | 122.1588 | 122.2824 | -0.14191 | -0.33417 | 0.073242 | 0.28839 | 121.9528 | 122.4014 | 122.1039 | 122.2595 | 122.1588 | 122.319 | 122.1909 | -0.33417 | 122.2595 | 122.1588 | 122.1909 | 122.1039 | 122.319 | -0.37537 | -122.58
1877.9219 | 122.4014 | -122.0627 | 0.11902 | 0.0026703 | 0.018453 | 0.0087735 | 0.02161 | -0.0033175 | -0.0074319 | 0.007165 | 0 | 0.19684 | -0.21973 | 0.10071 | -0.07782 | -0.009155 | -0.004578 | 0.16937 | 0.27008 | -122.438 | 121.843 | 0.077819 | 122.0627 | 122.1634 | -0.19684 | -0.37537 | 0.15106 | 0.21973 | 122.0581 | 122.2321 | 121.9849 | 122.2595 | 122.0627 | 122.3328 | 122.0535 | -0.37537 | 122.2595 | 122.0627 | 122.0535 | 121.9849 | 122.3328 | -0.33875 | -122.5571
1879.6875 | 122.4014 | -122.0627 | 0.10529 | 0.0026703 | 0.018453 | 0.0064237 | 0.018619 | -0.0048129 | -0.0061503 | 0.0052424 | 0 | 0.20142 | -0.22888 | 0.10529 | -0.068665 | -0.009155 | 0.041199 | 0.19684 | 0.27466 | -122.4792 | 121.8338 | 0.09613 | 122.0627 | 122.168 | -0.17395 | -0.41656 | 0.16937 | 0.22888 | 122.1039 | 122.2595 | 121.994 | 122.2641 | 122.0627 | 122.3373 | 122.0535 | -0.41656 | 122.2641 | 122.0627 | 122.0535 | 121.994 | 122.3373 | -0.33417 | -122.5845
1881.4375 | 122.3785 | -122.0673 | 0.15106 | 0.0103 | 0.019521 | 0.012192 | 0.018192 | -0.0020359 | -0.0052957 | 0.0069514 | 0.032043 | 0.20599 | -0.21057 | 0.11902 | -0.064087 | 0.009155 | -0.082397 | 0.1831 | 0.24719 | -122.4609 | 121.8567 | 0.054932 | 122.0993 | 122.1863 | -0.21515 | -0.39368 | 0.09613 | 0.24261 | 121.9849 | 122.2504 | 122.0032 | 122.2733 | 122.0993 | 122.3145 | 122.0764 | -0.39368 | 122.2733 | 122.0993 | 122.0764 | 122.0032 | 122.3145 | -0.36163 | -122.612
1883.1406 | 122.4014 | -122.081 | 0.1236 | -0.012589 | 0.017171 | 0.011764 | 0.014988 | -0.0039585 | -0.0057229 | 0.0075922 | 0.009155 | 0.21515 | -0.20142 | 0.09613 | -0.07782 | -0.022888 | 0.068665 | 0.20599 | 0.27924 | -122.4747 | 121.8796 | 0.091553 | 122.0901 | 122.1771 | -0.20142 | -0.39368 | 0.15564 | 0.21057 | 122.1497 | 122.287 | 122.0032 | 122.2961 | 122.0901 | 122.3602 | 122.0581 | -0.39368 | 122.2961 | 122.0901 | 122.0581 | 122.0032 | 122.3602 | -0.32501 | -122.5983
1884.8906 | 122.3785 | -122.0947 | 0.11902 | -0.0049592 | 0.018025 | 0.0098417 | 0.020328 | -0.0013949 | -0.0070047 | 0.008233 | 0.041199 | 0.19684 | -0.2243 | 0.11902 | -0.082397 | -0.022888 | -0.027466 | 0.18768 | 0.27008 | -122.4884 | 121.8704 | 0.077819 | 122.1359 | 122.2137 | -0.20142 | -0.39368 | 0.15106 | 0.2655 | 122.0673 | 122.2824 | 122.0123 | 122.2916 | 122.1359 | 122.3648 | 122.0718 | -0.39368 | 122.2916 | 122.1359 | 122.0718 | 122.0123 | 122.3648 | -0.34332 | -122.6074
1886.5781 | 122.4152 | -122.1222 | 0.1236 | 0.0103 | 0.019948 | 0.010055 | 0.017978 | -0.0039585 | -0.0059365 | 0.008874 | -0.004578 | 0.21057 | -0.23346 | 0.086975 | -0.10986 | -0.032043 | -0.013733 | 0.16022 | 0.27466 | -122.4884 | 121.8887 | 0.086975 | 122.1176 | 122.2092 | -0.23346 | -0.36621 | 0.15106 | 0.22888 | 122.1085 | 122.2824 | 122.0123 | 122.3328 | 122.1176 | 122.3969 | 122.0901 | -0.36621 | 122.3328 | 122.1176 | 122.0901 | 122.0123 | 122.3969 | -0.35706 | -122.612
1888.2656 | 122.3236 | -122.1222 | 0.14191 | 0.0026703 | 0.015462 | 0.012619 | 0.01157 | -0.0033175 | -0.0065775 | 0.005456 | 0.050354 | 0.19226 | -0.17853 | 0.15564 | -0.027466 | 0.064087 | -0.10986 | 0.24719 | 0.22888 | -122.493 | 121.9437 | 0.050354 | 122.1725 | 122.2778 | -0.16937 | -0.37079 | 0.086975 | 0.22888 | 122.0123 | 122.3694 | 122.0947 | 122.3145 | 122.1725 | 122.3511 | 122.1863 | -0.37079 | 122.3145 | 122.1725 | 122.1863 | 122.0947 | 122.3511 | -0.32044 | -122.6349
1890.0312 | 122.3465 | -122.1313 | 0.13733 | 0.0026703 | 0.017171 | 0.011551 | 0.012851 | -0.0037449 | -0.0052957 | 0.0056696 | 0.036621 | 0.16479 | -0.19226 | 0.15564 | -0.027466 | 0.032043 | -0.10529 | 0.26093 | 0.23346 | -122.4838 | 121.9391 | 0.027466 | 122.168 | 122.287 | -0.16479 | -0.35248 | 0.09613 | 0.22888 | 122.0261 | 122.3923 | 122.1039 | 122.2961 | 122.168 | 122.3648 | 122.1634 | -0.35248 | 122.2961 | 122.168 | 122.1634 | 122.1039 | 122.3648 | -0.32959 | -122.6212
1891.7969 | 122.4655 | -122.1039 | 0.10529 | -0.0049592 | 0.016103 | 0.011978 | 0.021396 | -0.0020359 | -0.0091409 | 0.0078058 | 0 | 0.19684 | -0.22888 | 0.10986 | -0.12817 | -0.050354 | -0.013733 | 0.14191 | 0.27466 | -122.4792 | 121.875 | 0.091552 | 122.1039 | 122.2137 | -0.23346 | -0.37537 | 0.16937 | 0.22888 | 122.0901 | 122.2458 | 121.9757 | 122.3007 | 122.1039 | 122.3785 | 122.0535 | -0.37537 | 122.3007 | 122.1039 | 122.0535 | 121.9757 | 122.3785 | -0.33417 | -122.5845
1893.5469 | 122.3785 | -122.1268 | 0.1236 | 0.0026703 | 0.01653 | 0.011551 | 0.018192 | -0.0016087 | -0.0074319 | 0.0075922 | 0.050354 | 0.18768 | -0.2243 | 0.14648 | -0.073242 | 0 | -0.032043 | 0.21973 | 0.27008 | -122.493 | 121.9025 | 0.064087 | 122.1771 | 122.2733 | -0.19684 | -0.36621 | 0.14649 | 0.27466 | 122.0947 | 122.3465 | 122.0535 | 122.3145 | 122.1771 | 122.3969 | 122.1268 | -0.36621 | 122.3145 | 122.1771 | 122.1268 | 122.0535 | 122.3969 | -0.3479 | -122.6166
1895.25 | 122.438 | -122.1222 | 0.10986 | -0.0049592 | 0.017598 | 0.0087735 | 0.015629 | -0.0033175 | -0.0067911 | 0.007165 | 0 | 0.21057 | -0.2243 | 0.11444 | -0.09613 | -0.041199 | 0.032043 | 0.21057 | 0.27008 | -122.4838 | 121.8979 | 0.10071 | 122.1222 | 122.2366 | -0.20599 | -0.36163 | 0.16022 | 0.2243 | 122.1542 | 122.3328 | 122.0261 | 122.3328 | 122.1222 | 122.3923 | 122.081 | -0.36163 | 122.3328 | 122.1222 | 122.081 | 122.0261 | 122.3923 | -0.33417 | -122.5937
1897 | 122.3373 | -122.1817 | 0.15106 | 0.0103 | 0.017385 | 0.012405 | 0.013492 | -0.0048129 | -0.0040139 | 0.007165 | 0.091553 | 0.15564 | -0.18768 | 0.18768 | -0.013733 | 0.059509 | -0.16022 | 0.28839 | 0.22888 | -122.4747 | 121.994 | 0.004578 | 122.2733 | 122.3694 | -0.16479 | -0.29297 | 0.07782 | 0.27924 | 122.0215 | 122.4701 | 122.168 | 122.3373 | 122.2733 | 122.4106 | 122.2412 | -0.29297 | 122.3373 | 122.2733 | 122.2412 | 122.168 | 122.4106 | -0.33874 | -122.6257
1898.6875 | 122.3785 | -122.1359 | 0.14191 | 0.0026703 | 0.012899 | 0.0092007 | 0.010929 | -0.0045993 | -0.0074319 | 0.0063104 | 0.009155 | 0.16937 | -0.19226 | 0.14648 | -0.045776 | 0.032043 | -0.09613 | 0.27466 | 0.22888 | -122.4884 | 121.9437 | 0.027466 | 122.1451 | 122.2824 | -0.18768 | -0.35248 | 0.086975 | 0.20142 | 122.0398 | 122.4106 | 122.0901 | 122.3053 | 122.1451 | 122.3648 | 122.168 | -0.35248 | 122.3053 | 122.1451 | 122.168 | 122.0901 | 122.3648 | -0.33417 | -122.6303
1900.4375 | 122.3648 | -122.1588 | 0.15106 | 0.0026703 | 0.017812 | 0.011123 | 0.016056 | -0.0060947 | -0.0065775 | 0.0058832 | 0.086975 | 0.16479 | -0.17395 | 0.16479 | -0.050354 | 0.032043 | -0.13275 | 0.28381 | 0.24719 | -122.4655 | 121.9849 | 0.013733 | 122.2458 | 122.3236 | -0.20142 | -0.3067 | 0.09613 | 0.26092 | 122.0261 | 122.4426 | 122.1085 | 122.3236 | 122.2458 | 122.406 | 122.1909 | -0.3067 | 122.3236 | 122.2458 | 122.1909 | 122.1085 | 122.406 | -0.32501 | -122.6166
1902.1562 | 122.4335 | -122.1313 | 0.11902 | 0.0026703 | 0.020589 | 0.012832 | 0.018619 | -0.0016087 | -0.0074319 | 0.007165 | 0 | 0.21057 | -0.23804 | 0.10071 | -0.13733 | -0.054932 | -0.009155 | 0.16937 | 0.27924 | -122.5113 | 121.8933 | 0.091552 | 122.1313 | 122.2321 | -0.25635 | -0.37994 | 0.16022 | 0.23804 | 122.1222 | 122.3007 | 121.994 | 122.3419 | 122.1313 | 122.4106 | 122.0764 | -0.37994 | 122.3419 | 122.1313 | 122.0764 | 121.994 | 122.4106 | -0.35706 | -122.6303
1903.875 | 122.3511 | -122.168 | 0.14191 | -0.0049592 | 0.01653 | 0.010269 | 0.018619 | -0.0022495 | -0.0048685 | 0.0080194 | 0.091553 | 0.16022 | -0.16937 | 0.20599 | -0.032043 | 0.045776 | -0.17853 | 0.28381 | 0.2243 | -122.4655 | 121.9986 | 0.01831 | 122.2595 | 122.374 | -0.17395 | -0.29755 | 0.082397 | 0.26093 | 121.9894 | 122.4518 | 122.1359 | 122.3282 | 122.2595 | 122.3923 | 122.2137 | -0.29755 | 122.3282 | 122.2595 | 122.2137 | 122.1359 | 122.3923 | -0.31128 | -122.6074
1905.6406 | 122.3236 | -122.168 | 0.15106 | -0.0049592 | 0.018666 | 0.0077053 | 0.01456 | -0.0033175 | -0.0048685 | 0.0063104 | 0.10986 | 0.16937 | -0.17395 | 0.23346 | 0 | 0.068665 | -0.14191 | 0.35248 | 0.24719 | -122.5067 | 121.994 | 0.018311 | 122.2778 | 122.4014 | -0.15106 | -0.33875 | 0.09613 | 0.28381 | 122.0261 | 122.5204 | 122.168 | 122.3373 | 122.2778 | 122.4152 | 122.2366 | -0.33875 | 122.3373 | 122.2778 | 122.2366 | 122.168 | 122.4152 | -0.32501 | -122.6578
1907.3906 | 122.3373 | -122.1771 | 0.11902 | -0.0049592 | 0.016957 | 0.013473 | 0.015201 | -0.0024631 | -0.0091409 | 0.0078058 | 0.10986 | 0.18768 | -0.1831 | 0.21973 | -0.027466 | 0.045776 | -0.10529 | 0.33417 | 0.23804 | -122.5204 | 121.994 | 0.068664 | 122.287 | 122.3969 | -0.14649 | -0.34332 | 0.11902 | 0.29297 | 122.0718 | 122.5113 | 122.1497 | 122.3648 | 122.287 | 122.4152 | 122.2229 | -0.34332 | 122.3648 | 122.287 | 122.2229 | 122.1497 | 122.4152 | -0.30212 | -122.6395
1909.0938 | 122.3328 | -122.2183 | 0.14191 | -0.012589 | 0.016957 | 0.013473 | 0.017338 | -0.0033175 | -0.0038003 | 0.0060968 | 0.10986 | 0.16479 | -0.17395 | 0.22888 | -0.018311 | 0.059509 | -0.18768 | 0.31128 | 0.21973 | -122.5204 | 122.0444 | 0.022888 | 122.3282 | 122.4472 | -0.16022 | -0.30212 | 0.07782 | 0.28381 | 122.0306 | 122.5296 | 122.2 | 122.3831 | 122.3282 | 122.4381 | 122.2778 | -0.30212 | 122.3831 | 122.3282 | 122.2778 | 122.2 | 122.4381 | -0.31586 | -122.6624
1910.8438 | 122.3236 | -122.1588 | 0.14191 | 0.0026703 | 0.015462 | 0.0098417 | 0.014347 | -0.0063083 | -0.0033731 | 0.005456 | 0.10071 | 0.16937 | -0.19226 | 0.23804 | -0.004578 | 0.073242 | -0.15106 | 0.35248 | 0.23346 | -122.5479 | 121.9666 | 0.027466 | 122.2595 | 122.3969 | -0.14649 | -0.3891 | 0.091552 | 0.29297 | 122.0078 | 122.5113 | 122.1542 | 122.3282 | 122.2595 | 122.3923 | 122.2321 | -0.3891 | 122.3282 | 122.2595 | 122.2321 | 122.1542 | 122.3923 | -0.33417 | -122.6898
1912.6094 | 122.406 | -122.1725 | 0.13275 | 0.0026703 | 0.017598 | 0.011123 | 0.012851 | -0.0065219 | -0.0023049 | 0.0078058 | 0.032043 | 0.16937 | -0.19226 | 0.14648 | -0.091553 | -0.018311 | -0.10986 | 0.26093 | 0.23346 | -122.5754 | 121.9803 | 0.036622 | 122.2046 | 122.319 | -0.2243 | -0.40283 | 0.10071 | 0.2243 | 122.0627 | 122.4335 | 122.081 | 122.3419 | 122.2046 | 122.406 | 122.1542 | -0.40283 | 122.3419 | 122.2046 | 122.1542 | 122.081 | 122.406 | -0.32501 | -122.7081
1914.375 | 122.4426 | -122.1771 | 0.11902 | 0.0103 | 0.019948 | 0.012405 | 0.022678 | -0.0028903 | -0.010209 | 0.0086604 | 0.064087 | 0.1831 | -0.20142 | 0.15106 | -0.13733 | -0.073242 | -0.045776 | 0.20599 | 0.28381 | -122.5296 | 121.9757 | 0.064086 | 122.2412 | 122.3282 | -0.25635 | -0.35248 | 0.16479 | 0.2655 | 122.1313 | 122.3831 | 122.0398 | 122.3602 | 122.2412 | 122.4609 | 122.1039 | -0.35248 | 122.3602 | 122.2412 | 122.1039 | 122.0398 | 122.4609 | -0.32044 | -122.6486
1916.0625 | 122.4792 | -122.1405 | 0.10071 | 0.0026703 | 0.016317 | 0.011337 | 0.017124 | -0.0041721 | -0.0059365 | 0.008233 | -0.004578 | 0.20599 | -0.21515 | 0.11902 | 0.009155 | 0.059509 | 0.054932 | 0.20599 | 0.27008 | -122.5662 | 121.9254 | 0.10529 | 122.1359 | 122.2595 | -0.091553 | -0.42572 | 0.16937 | 0.21057 | 122.1954 | 122.3465 | 122.1497 | 122.3465 | 122.1359 | 122.4106 | 122.2 | -0.42572 | 122.3465 | 122.1359 | 122.2 | 122.1497 | 122.4106 | -0.31586 | -122.6669
1917.8125 | 122.3694 | -122.2275 | 0.16022 | 0.0026703 | 0.015676 | 0.010269 | 0.01456 | -0.0058811 | -0.0072183 | 0.008233 | 0.10071 | 0.16022 | -0.17395 | 0.21973 | 0 | 0.19684 | -0.1236 | 0.32501 | 0.24261 | -122.5525 | 122.0535 | 0 | 122.3282 | 122.4472 | -0.16022 | -0.32501 | 0.082398 | 0.27466 | 122.1039 | 122.5525 | 122.2275 | 122.3877 | 122.3282 | 122.4701 | 122.4243 | -0.32501 | 122.3877 | 122.3282 | 122.4243 | 122.2275 | 122.4701 | -0.33417 | -122.7127
1919.5781 | 122.3602 | -122.2183 | 0.15564 | -0.0049592 | 0.020375 | 0.011337 | 0.017765 | -0.0048129 | -0.0052957 | 0.0046014 | 0.11444 | 0.17395 | -0.17853 | 0.21515 | -0.009155 | 0.19684 | -0.17853 | 0.31586 | 0.2243 | -122.5342 | 122.0398 | 0.01831 | 122.3328 | 122.4335 | -0.16479 | -0.31586 | 0.068664 | 0.29297 | 122.0398 | 122.5342 | 122.2092 | 122.3923 | 122.3328 | 122.4426 | 122.4152 | -0.31586 | 122.3923 | 122.3328 | 122.4152 | 122.2092 | 122.4426 | -0.33417 | -122.6898
1921.3438 | 122.4518 | -122.1909 | 0.11444 | 0.0026703 | 0.017385 | 0.011978 | 0.01926 | -0.0035313 | -0.0082865 | 0.0073786 | 0.045776 | 0.19226 | -0.21057 | 0.17395 | -0.082397 | 0.10071 | -0.018311 | 0.25177 | 0.25635 | -122.5662 | 121.9803 | 0.07782 | 122.2366 | 122.3648 | -0.19684 | -0.37537 | 0.14191 | 0.25635 | 122.1725 | 122.4426 | 122.1085 | 122.3831 | 122.2366 | 122.4472 | 122.2916 | -0.37537 | 122.3831 | 122.2366 | 122.2916 | 122.1085 | 122.4472 | -0.32501 | -122.6807
1923.0312 | 122.4976 | -122.1909 | 0.12817 | -0.0049592 | 0.01653 | 0.010269 | 0.022251 | -0.0028903 | -0.0074319 | 0.0078058 | 0.013733 | 0.18768 | -0.20142 | 0.12817 | -0.1236 | 0.068665 | -0.004578 | 0.18768 | 0.2655 | -122.5342 | 121.9894 | 0.059509 | 122.2046 | 122.319 | -0.25177 | -0.34332 | 0.13733 | 0.21515 | 122.1863 | 122.3785 | 122.0673 | 122.3785 | 122.2046 | 122.4564 | 122.2595 | -0.34332 | 122.3785 | 122.2046 | 122.2595 | 122.0673 | 122.4564 | -0.32959 | -122.6624
1924.7969 | 122.3785 | -122.2412 | 0.14648 | 0.0026703 | 0.018666 | 0.011978 | 0.015201 | -0.0020359 | -0.0040139 | 0.0078058 | 0.10529 | 0.15564 | -0.19226 | 0.21973 | -0.022888 | 0.19684 | -0.18768 | 0.29297 | 0.24719 | -122.5388 | 122.049 | 0.009156 | 122.3465 | 122.4609 | -0.16937 | -0.29755 | 0.10071 | 0.29755 | 122.0535 | 122.5342 | 122.2183 | 122.3969 | 122.3465 | 122.4884 | 122.438 | -0.29755 | 122.3969 | 122.3465 | 122.438 | 122.2183 | 122.4884 | -0.33874 | -122.6852
1926.5625 | 122.4426 | -122.1954 | 0.12817 | 0.0103 | 0.018025 | 0.016464 | 0.01392 | -0.0058811 | -0.0046549 | 0.007165 | 0.073242 | 0.18768 | -0.19684 | 0.14648 | -0.082397 | 0.09613 | -0.013733 | 0.23804 | 0.2655 | -122.5708 | 121.9986 | 0.059509 | 122.2687 | 122.3419 | -0.21057 | -0.37537 | 0.13733 | 0.27008 | 122.1817 | 122.4335 | 122.113 | 122.3831 | 122.2687 | 122.4609 | 122.2916 | -0.37537 | 122.3831 | 122.2687 | 122.2916 | 122.113 | 122.4609 | -0.32501 | -122.699
1928.25 | 122.4106 | -122.2183 | 0.14191 | 0.0026703 | 0.016957 | 0.012619 | 0.013492 | -0.0045993 | -0.0055093 | 0.0084468 | 0.091553 | 0.16022 | -0.17395 | 0.17853 | -0.041199 | 0.16022 | -0.041199 | 0.3067 | 0.23346 | -122.58 | 122.0444 | 0.01831 | 122.3099 | 122.3969 | -0.18311 | -0.36163 | 0.091552 | 0.2655 | 122.1771 | 122.525 | 122.1771 | 122.3785 | 122.3099 | 122.4518 | 122.3785 | -0.36163 | 122.3785 | 122.3099 | 122.3785 | 122.1771 | 122.4518 | -0.31586 | -122.7219
1930 | 122.4014 | -122.2229 | 0.14191 | 0.0026703 | 0.016317 | 0.0098417 | 0.017338 | -0.0024631 | -0.0082865 | 0.0090876 | 0.10071 | 0.16022 | -0.17395 | 0.20599 | -0.041199 | 0.20142 | -0.17853 | 0.29755 | 0.24719 | -122.5204 | 122.0489 | 0.01831 | 122.3236 | 122.4289 | -0.18311 | -0.29755 | 0.10528 | 0.27466 | 122.0444 | 122.5204 | 122.1817 | 122.3831 | 122.3236 | 122.4701 | 122.4243 | -0.29755 | 122.3831 | 122.3236 | 122.4243 | 122.1817 | 122.4701 | -0.31586 | -122.6624
1931.7031 | 122.4518 | -122.2183 | 0.13275 | -0.012589 | 0.016103 | 0.010055 | 0.013065 | -0.0041721 | -0.0055093 | 0.0075922 | 0.050354 | 0.16937 | -0.18768 | 0.16479 | -0.073242 | 0.14648 | -0.10071 | 0.25635 | 0.24719 | -122.5937 | 122.0306 | 0.036622 | 122.2687 | 122.3831 | -0.20599 | -0.37537 | 0.11444 | 0.23804 | 122.1176 | 122.4747 | 122.1451 | 122.3877 | 122.2687 | 122.4655 | 122.3648 | -0.37537 | 122.3877 | 122.2687 | 122.3648 | 122.1451 | 122.4655 | -0.32043 | -122.7264
1933.3906 | 122.406 | -122.2229 | 0.16022 | -0.0049592 | 0.017385 | 0.011978 | 0.013492 | -0.0033175 | -0.0029459 | 0.008874 | 0.082397 | 0.19226 | -0.17853 | 0.20599 | -0.027466 | 0.20142 | -0.12817 | 0.32959 | 0.22888 | -122.5754 | 122.0444 | 0.032044 | 122.3053 | 122.4289 | -0.18768 | -0.35248 | 0.068665 | 0.26092 | 122.0947 | 122.5525 | 122.1954 | 122.4152 | 122.3053 | 122.4518 | 122.4243 | -0.35248 | 122.4152 | 122.3053 | 122.4243 | 122.1954 | 122.4518 | -0.33874 | -122.7356
1935.0938 | 122.5342 | -122.2046 | 0.11902 | -0.0049592 | 0.018239 | 0.01625 | 0.021183 | -0.0033175 | -0.0048685 | 0.0073786 | 0.027466 | 0.19226 | -0.21515 | 0.11902 | -0.14191 | 0.073242 | -0.013733 | 0.18768 | 0.2655 | -122.58 | 121.9894 | 0.073242 | 122.2321 | 122.3236 | -0.26093 | -0.37537 | 0.14648 | 0.24261 | 122.1909 | 122.3923 | 122.0627 | 122.3969 | 122.2321 | 122.4701 | 122.2778 | -0.37537 | 122.3969 | 122.2321 | 122.2778 | 122.0627 | 122.4701 | -0.33417 | -122.699
1936.8125 | 122.5159 | -122.2092 | 0.1236 | 0.0026703 | 0.018666 | 0.014114 | 0.018833 | -0.0018223 | -0.0080729 | 0.007165 | 0.036621 | 0.20599 | -0.21515 | 0.13275 | -0.15106 | 0.07782 | -0.022888 | 0.17853 | 0.27008 | -122.6074 | 121.994 | 0.082398 | 122.2458 | 122.3419 | -0.27466 | -0.39826 | 0.14649 | 0.25177 | 122.1863 | 122.3877 | 122.0581 | 122.4152 | 122.2458 | 122.4792 | 122.287 | -0.39826 | 122.4152 | 122.2458 | 122.287 | 122.0581 | 122.4792 | -0.33875 | -122.731
1938.5781 | 122.3923 | -122.2321 | 0.15106 | -0.0049592 | 0.018453 | 0.0096279 | 0.011783 | -0.0026767 | -0.0057229 | 0.007165 | 0.11902 | 0.16937 | -0.16479 | 0.24261 | 0 | 0.21973 | -0.15106 | 0.3479 | 0.21973 | -122.5662 | 122.0673 | 0.018311 | 122.3511 | 122.4747 | -0.15106 | -0.33417 | 0.068665 | 0.28381 | 122.081 | 122.58 | 122.2321 | 122.4014 | 122.3511 | 122.4518 | 122.4518 | -0.33417 | 122.4014 | 122.3511 | 122.4518 | 122.2321 | 122.4518 | -0.31586 | -122.7173
1940.3438 | 122.4014 | -122.2824 | 0.14191 | -0.012589 | 0.018239 | 0.010696 | 0.01392 | -0.0058811 | -0.0029459 | 0.0063104 | 0.1236 | 0.16479 | -0.15564 | 0.23804 | -0.009155 | 0.21515 | -0.14191 | 0.37537 | 0.2243 | -122.5845 | 122.1268 | 0.022888 | 122.406 | 122.5204 | -0.15106 | -0.30212 | 0.082397 | 0.27924 | 122.1405 | 122.6578 | 122.2733 | 122.4472 | 122.406 | 122.5067 | 122.4976 | -0.30212 | 122.4472 | 122.406 | 122.4976 | 122.2733 | 122.5067 | -0.29755 | -122.7264
1942.0312 | 122.4884 | -122.2366 | 0.11444 | 0.0026703 | 0.01653 | 0.012619 | 0.020542 | -0.0067355 | -0.0074319 | 0.0058832 | 0.041199 | 0.18768 | -0.20599 | 0.16937 | -0.086975 | 0.11444 | -0.032043 | 0.24719 | 0.26093 | -122.6074 | 122.0306 | 0.073242 | 122.2778 | 122.406 | -0.20142 | -0.37079 | 0.14648 | 0.24719 | 122.2046 | 122.4838 | 122.1497 | 122.4243 | 122.2778 | 122.4976 | 122.3511 | -0.37079 | 122.4243 | 122.2778 | 122.3511 | 122.1497 | 122.4976 | -0.32044 | -122.7219
1943.7969 | 122.5388 | -122.2183 | 0.10986 | 0.0026703 | 0.018666 | 0.012832 | 0.018406 | -0.0035313 | -0.0072183 | 0.0067378 | 0 | 0.20599 | -0.21973 | 0.086975 | -0.18768 | 0.050354 | 0.009155 | 0.15564 | 0.26093 | -122.6166 | 121.9986 | 0.096131 | 122.2183 | 122.3053 | -0.29755 | -0.39825 | 0.15106 | 0.21973 | 122.2275 | 122.374 | 122.0306 | 122.4243 | 122.2183 | 122.4792 | 122.2687 | -0.39825 | 122.4243 | 122.2183 | 122.2687 | 122.0306 | 122.4792 | -0.32959 | -122.7264
1945.5781 | 122.4884 | -122.2321 | 0.13275 | 0.0026703 | 0.016957 | 0.0092007 | 0.019901 | -0.0024631 | -0.0089273 | 0.0080194 | 0.041199 | 0.17853 | -0.21515 | 0.16022 | -0.11902 | 0.1236 | -0.041199 | 0.25635 | 0.24719 | -122.5845 | 122.0169 | 0.045777 | 122.2733 | 122.3923 | -0.25177 | -0.35248 | 0.11444 | 0.25635 | 122.1909 | 122.4884 | 122.113 | 122.4106 | 122.2733 | 122.4792 | 122.3557 | -0.35248 | 122.4106 | 122.2733 | 122.3557 | 122.113 | 122.4792 | -0.3479 | -122.7173
1947.3438 | 122.4609 | -122.2687 | 0.14648 | -0.0049592 | 0.018239 | 0.012192 | 0.013279 | -0.0078037 | -0.0048685 | 0.008874 | 0.032043 | 0.16937 | -0.19226 | 0.16937 | -0.10071 | 0.16937 | -0.091553 | 0.25177 | 0.24261 | -122.6212 | 122.0764 | 0.022889 | 122.3007 | 122.438 | -0.24719 | -0.35248 | 0.096131 | 0.2243 | 122.1771 | 122.5204 | 122.168 | 122.438 | 122.3007 | 122.5113 | 122.438 | -0.35248 | 122.438 | 122.3007 | 122.438 | 122.168 | 122.5113 | -0.33874 | -122.7676
1949.0312 | 122.3969 | -122.287 | 0.14191 | -0.0049592 | 0.016744 | 0.01091 | 0.015415 | -0.0041721 | -0.0050821 | 0.0080194 | 0.1236 | 0.16022 | -0.16479 | 0.2243 | -0.050354 | 0.20142 | -0.13275 | 0.36163 | 0.23804 | -122.612 | 122.1222 | 0.01831 | 122.4106 | 122.5113 | -0.19226 | -0.32501 | 0.09613 | 0.28839 | 122.1542 | 122.6486 | 122.2366 | 122.4472 | 122.4106 | 122.525 | 122.4884 | -0.32501 | 122.4472 | 122.4106 | 122.4884 | 122.2366 | 122.525 | -0.3067 | -122.7539
1950.7969 | 122.4335 | -122.2778 | 0.14191 | 0.0026703 | 0.016317 | 0.015823 | 0.017551 | -0.0024631 | -0.0044413 | 0.006524 | 0.10529 | 0.15564 | -0.1831 | 0.20599 | 0.091553 | 0.19684 | -0.17395 | 0.29297 | 0.21973 | -122.5937 | 122.0947 | 0.013733 | 122.3831 | 122.4838 | -0.050354 | -0.31586 | 0.07782 | 0.28839 | 122.1039 | 122.5708 | 122.3694 | 122.4335 | 122.3831 | 122.4976 | 122.4747 | -0.31586 | 122.4335 | 122.3831 | 122.4747 | 122.3694 | 122.4976 | -0.32501 | -122.7356
1952.5469 | 122.4243 | -122.2641 | 0.15106 | -0.0049592 | 0.016957 | 0.0072781 | 0.016697 | -0.0054539 | -0.0080729 | 0.0073786 | 0.10529 | 0.15564 | -0.17395 | 0.24261 | 0.12817 | 0.21057 | -0.12817 | 0.35706 | 0.21973 | -122.5983 | 122.0901 | 0.004578 | 122.3694 | 122.5067 | -0.022888 | -0.33417 | 0.068665 | 0.27924 | 122.1359 | 122.6212 | 122.3923 | 122.4197 | 122.3694 | 122.4838 | 122.4747 | -0.33417 | 122.4197 | 122.3694 | 122.4747 | 122.3923 | 122.4838 | -0.32501 | -122.7493
1954.25 | 122.5159 | -122.2687 | 0.10529 | -0.012589 | 0.017385 | 0.017105 | 0.022037 | -0.00096767 | -0.0085001 | 0.0093012 | 0.045776 | 0.15564 | -0.21057 | 0.12817 | 0.013733 | 0.07782 | -0.004578 | 0.18768 | 0.26093 | -122.6074 | 122.0581 | 0.050354 | 122.3145 | 122.3969 | -0.091553 | -0.33875 | 0.15564 | 0.25635 | 122.2641 | 122.4564 | 122.2824 | 122.4243 | 122.3145 | 122.5296 | 122.3465 | -0.33875 | 122.4243 | 122.3145 | 122.3465 | 122.2824 | 122.5296 | -0.31586 | -122.7127
1956.0156 | 122.5204 | -122.2733 | 0.10529 | 0.0026703 | 0.018025 | 0.0074917 | 0.01926 | -0.0050265 | -0.0097819 | 0.0058832 | 0.009155 | 0.19226 | -0.23346 | 0.15106 | 0.036621 | 0.10071 | -0.009155 | 0.23346 | 0.2655 | -122.6166 | 122.0398 | 0.086975 | 122.2824 | 122.4243 | -0.068665 | -0.34332 | 0.16022 | 0.24261 | 122.2641 | 122.5067 | 122.3099 | 122.4655 | 122.2824 | 122.5388 | 122.374 | -0.34332 | 122.4655 | 122.2824 | 122.374 | 122.3099 | 122.5388 | -0.33875 | -122.7219
1957.7812 | 122.58 | -122.2549 | 0.10986 | -0.0049592 | 0.01888 | 0.010055 | 0.020328 | -0.0035313 | -0.0061503 | 0.0080194 | -0.004578 | 0.20599 | -0.21057 | 0.07782 | -0.027466 | 0.032043 | 0.013733 | 0.14648 | 0.23346 | -122.644 | 122.0444 | 0.096131 | 122.2504 | 122.3328 | -0.13733 | -0.3891 | 0.1236 | 0.20599 | 122.2687 | 122.4014 | 122.2275 | 122.4609 | 122.2504 | 122.4884 | 122.287 | -0.3891 | 122.4609 | 122.2504 | 122.287 | 122.2275 | 122.4884 | -0.32043 | -122.7539
1959.5625 | 122.438 | -122.2824 | 0.13733 | -0.0049592 | 0.016957 | 0.011123 | 0.013492 | -0.0033175 | -0.0061503 | 0.0056696 | 0.10986 | 0.13733 | -0.1831 | 0.21057 | 0.11444 | 0.21057 | -0.18768 | 0.3067 | 0.2243 | -122.5845 | 122.0993 | 0 | 122.3923 | 122.493 | -0.022888 | -0.30212 | 0.086975 | 0.29297 | 122.0947 | 122.5891 | 122.3969 | 122.4197 | 122.3923 | 122.5067 | 122.493 | -0.30212 | 122.4197 | 122.3923 | 122.493 | 122.3969 | 122.5067 | -0.32043 | -122.7219
1961.25 | 122.5204 | -122.2687 | 0.1236 | -0.0049592 | 0.019948 | 0.0083463 | 0.019047 | -0.0037449 | -0.0087137 | 0.0095148 | 0.054932 | 0.20142 | -0.21515 | 0.16479 | 0.050354 | 0.11902 | -0.036621 | 0.24261 | 0.25635 | -122.6212 | 122.0535 | 0.07782 | 122.3236 | 122.4335 | -0.073242 | -0.35248 | 0.13275 | 0.27008 | 122.2321 | 122.5113 | 122.319 | 122.4701 | 122.3236 | 122.525 | 122.3877 | -0.35248 | 122.4701 | 122.3236 | 122.3877 | 122.319 | 122.525 | -0.33875 | -122.7448
1963 | 122.4472 | -122.2916 | 0.13275 | 0.0026703 | 0.015889 | 0.01091 | 0.013279 | -0.0056675 | -0.0044413 | 0.0080194 | 0.10071 | 0.16022 | -0.17395 | 0.19226 | 0.10986 | 0.17853 | -0.068665 | 0.32044 | 0.21515 | -122.644 | 122.1176 | 0.027466 | 122.3923 | 122.4838 | -0.022888 | -0.35248 | 0.082398 | 0.27466 | 122.2229 | 122.612 | 122.4014 | 122.4518 | 122.3923 | 122.5067 | 122.4701 | -0.35248 | 122.4518 | 122.3923 | 122.4701 | 122.4014 | 122.5067 | -0.3067 | -122.7768
1964.7656 | 122.5113 | -122.2549 | 0.11902 | -0.012589 | 0.017598 | 0.0098417 | 0.013279 | -0.0065219 | -0.0048685 | 0.006524 | 0.032043 | 0.16937 | -0.19226 | 0.16022 | 0.09613 | 0.15564 | -0.09613 | 0.2655 | 0.2243 | -122.6395 | 122.0627 | 0.050354 | 122.287 | 122.4152 | -0.022889 | -0.38452 | 0.10529 | 0.2243 | 122.1588 | 122.5204 | 122.3511 | 122.4243 | 122.287 | 122.4792 | 122.4106 | -0.38452 | 122.4243 | 122.287 | 122.4106 | 122.3511 | 122.4792 | -0.31128 | -122.7585
1966.5312 | 122.5342 | -122.2961 | 0.1236 | -0.0049592 | 0.016957 | 0.015182 | 0.022678 | -0.0033175 | -0.0087137 | 0.007165 | 0.045776 | 0.16937 | -0.21973 | 0.17853 | 0.045776 | 0.13275 | -0.036621 | 0.22888 | 0.2655 | -122.6028 | 122.0764 | 0.045777 | 122.3419 | 122.4747 | -0.07782 | -0.3067 | 0.14191 | 0.2655 | 122.2595 | 122.525 | 122.3419 | 122.4655 | 122.3419 | 122.5616 | 122.4289 | -0.3067 | 122.4655 | 122.3419 | 122.4289 | 122.3419 | 122.5616 | -0.34332 | -122.7264
1968.2969 | 122.5983 | -122.2687 | 0.10529 | 0.0026703 | 0.017812 | 0.013473 | 0.018192 | -0.00032687 | -0.0059365 | 0.0093012 | -0.018311 | 0.20142 | -0.21973 | 0.082397 | -0.027466 | 0.050354 | -0.004578 | 0.16479 | 0.27924 | -122.6578 | 122.0489 | 0.09613 | 122.2504 | 122.3511 | -0.13275 | -0.3891 | 0.17395 | 0.20142 | 122.2641 | 122.4335 | 122.2412 | 122.4701 | 122.2504 | 122.5479 | 122.319 | -0.3891 | 122.4701 | 122.2504 | 122.319 | 122.2412 | 122.5479 | -0.32501 | -122.7631
1969.9844 | 122.4564 | -122.3236 | 0.15564 | -0.0049592 | 0.015248 | 0.011978 | 0.015201 | -0.0011813 | -0.0052957 | 0.0086604 | 0.091553 | 0.16022 | -0.16479 | 0.21057 | 0.11902 | 0.21057 | -0.19684 | 0.30212 | 0.21057 | -122.5937 | 122.1588 | 0.004577 | 122.4152 | 122.5342 | -0.036621 | -0.27008 | 0.054931 | 0.25635 | 122.1268 | 122.6257 | 122.4426 | 122.4838 | 122.4152 | 122.5342 | 122.5342 | -0.27008 | 122.4838 | 122.4152 | 122.5342 | 122.4426 | 122.5342 | -0.32044 | -122.7493
1971.7344 | 122.5616 | -122.2824 | 0.11444 | 0.0026703 | 0.018453 | 0.014328 | 0.018619 | -0.0037449 | -0.0072183 | 0.0080194 | 0.027466 | 0.19226 | -0.21515 | 0.11444 | 0 | 0.07782 | -0.013733 | 0.19684 | 0.25635 | -122.6578 | 122.0673 | 0.07782 | 122.3099 | 122.3969 | -0.11444 | -0.37537 | 0.14191 | 0.24261 | 122.2687 | 122.4792 | 122.2824 | 122.4747 | 122.3099 | 122.5388 | 122.3602 | -0.37537 | 122.4747 | 122.3099 | 122.3602 | 122.2824 | 122.5388 | -0.32959 | -122.7722
1973.5 | 122.493 | -122.319 | 0.15106 | -0.012589 | 0.015676 | 0.0094143 | 0.01456 | -0.0020359 | -0.0050821 | 0.0084468 | 0.082397 | 0.16022 | -0.17395 | 0.19226 | 0.10529 | 0.19684 | -0.16022 | 0.27466 | 0.22888 | -122.6349 | 122.1451 | 0.009155 | 122.4014 | 122.5113 | -0.045776 | -0.31586 | 0.07782 | 0.25635 | 122.1588 | 122.5937 | 122.4243 | 122.4792 | 122.4014 | 122.5479 | 122.5159 | -0.31586 | 122.4792 | 122.4014 | 122.5159 | 122.4243 | 122.5479 | -0.32501 | -122.7859
1975.1875 | 122.5708 | -122.2824 | 0.1236 | 0.0026703 | 0.018453 | 0.015823 | 0.021183 | -0.00054047 | -0.0055093 | 0.0078058 | 0.054932 | 0.19684 | -0.19684 | 0.11902 | 0.022888 | 0.068665 | -0.013733 | 0.18768 | 0.25635 | -122.7081 | 122.0856 | 0.073242 | 122.3373 | 122.4014 | -0.10071 | -0.42572 | 0.13275 | 0.25177 | 122.2687 | 122.4701 | 122.3053 | 122.4792 | 122.3373 | 122.5388 | 122.3511 | -0.42572 | 122.4792 | 122.3373 | 122.3511 | 122.3053 | 122.5388 | -0.32043 | -122.8317
1976.9531 | 122.5113 | -122.3282 | 0.13733 | -0.0049592 | 0.017812 | 0.010696 | 0.013279 | -0.0045993 | -0.0040139 | 0.008233 | 0.041199 | 0.17395 | -0.1831 | 0.16479 | 0.073242 | 0.15106 | -0.10986 | 0.26093 | 0.2243 | -122.6807 | 122.1451 | 0.036621 | 122.3694 | 122.493 | -0.064087 | -0.35248 | 0.086975 | 0.2243 | 122.2183 | 122.5891 | 122.4014 | 122.5021 | 122.3694 | 122.5525 | 122.4792 | -0.35248 | 122.5021 | 122.3694 | 122.4792 | 122.4014 | 122.5525 | -0.32043 | -122.818
1978.7031 | 122.4564 | -122.3145 | 0.15564 | -0.0049592 | 0.018025 | 0.0094143 | 0.017124 | -0.0026767 | -0.0048685 | 0.0080194 | 0.10071 | 0.15564 | -0.17853 | 0.22888 | 0.12817 | 0.20599 | -0.13733 | 0.35706 | 0.23346 | -122.6898 | 122.1359 | 0 | 122.4152 | 122.5433 | -0.027466 | -0.37537 | 0.077819 | 0.27924 | 122.1771 | 122.6715 | 122.4426 | 122.4701 | 122.4152 | 122.5479 | 122.5204 | -0.37537 | 122.4701 | 122.4152 | 122.5204 | 122.4426 | 122.5479 | -0.33417 | -122.8455
1980.4062 | 122.6074 | -122.2778 | 0.10986 | -0.012589 | 0.018666 | 0.011123 | 0.021396 | -0.0045993 | -0.0061503 | 0.0075922 | 0.009155 | 0.19226 | -0.20599 | 0.11444 | 0.004578 | 0.073242 | 0.045776 | 0.21057 | 0.27008 | -122.6898 | 122.0718 | 0.082398 | 122.287 | 122.3923 | -0.10529 | -0.41199 | 0.16022 | 0.21515 | 122.3236 | 122.4884 | 122.2824 | 122.4701 | 122.287 | 122.5479 | 122.3511 | -0.41199 | 122.4701 | 122.287 | 122.3511 | 122.2824 | 122.5479 | -0.31586 | -122.7997
1982.1094 | 122.4655 | -122.319 | 0.13275 | -0.0049592 | 0.015462 | 0.013046 | 0.014988 | -0.0054539 | -0.0063639 | 0.0078058 | 0.11444 | 0.16937 | -0.18768 | 0.2243 | 0.11902 | 0.20599 | -0.12817 | 0.3479 | 0.23346 | -122.6761 | 122.1313 | 0.036622 | 122.4335 | 122.5433 | -0.013732 | -0.35706 | 0.10071 | 0.30212 | 122.1909 | 122.6669 | 122.438 | 122.4884 | 122.4335 | 122.5525 | 122.525 | -0.35706 | 122.4884 | 122.4335 | 122.525 | 122.438 | 122.5525 | -0.32043 | -122.8088
1983.8594 | 122.5571 | -122.2961 | 0.1236 | -0.0049592 | 0.016317 | 0.01091 | 0.021183 | -0.0031039 | -0.0057229 | 0.0058832 | 0.064087 | 0.16479 | -0.23804 | 0.16937 | 0.045776 | 0.11444 | -0.041199 | 0.24261 | 0.25635 | -122.6715 | 122.0581 | 0.041199 | 122.3602 | 122.4655 | -0.07782 | -0.37537 | 0.13275 | 0.30212 | 122.2549 | 122.5388 | 122.3419 | 122.4609 | 122.3602 | 122.5525 | 122.4106 | -0.37537 | 122.4609 | 122.3602 | 122.4106 | 122.3419 | 122.5525 | -0.36163 | -122.7951
1985.5625 | 122.4701 | -122.3236 | 0.13275 | -0.012589 | 0.017812 | 0.010483 | 0.015629 | -0.0039585 | -0.0063639 | 0.0069514 | 0.10071 | 0.15106 | -0.16022 | 0.22888 | 0.15106 | 0.21057 | -0.16479 | 0.35706 | 0.23346 | -122.644 | 122.1634 | 0.018311 | 122.4243 | 122.5525 | 0.018311 | -0.32044 | 0.10071 | 0.26093 | 122.1588 | 122.6807 | 122.4747 | 122.4747 | 122.4243 | 122.5571 | 122.5342 | -0.32044 | 122.4747 | 122.4243 | 122.5342 | 122.4747 | 122.5571 | -0.29297 | -122.7768
1987.2656 | 122.5708 | -122.3099 | 0.10071 | 0.0026703 | 0.016317 | 0.0092007 | 0.021396 | -0.0026767 | -0.0080729 | 0.005456 | 0.07782 | 0.17395 | -0.21515 | 0.16937 | 0.059509 | 0.1236 | -0.045776 | 0.24719 | 0.2655 | -122.644 | 122.0947 | 0.073242 | 122.3877 | 122.4792 | -0.041199 | -0.33417 | 0.16479 | 0.29297 | 122.2641 | 122.5571 | 122.3694 | 122.4838 | 122.3877 | 122.5754 | 122.4335 | -0.33417 | 122.4838 | 122.3877 | 122.4335 | 122.3694 | 122.5754 | -0.31586 | -122.7448
1988.9531 | 122.6028 | -122.3145 | 0.12817 | -0.0049592 | 0.020589 | 0.012619 | 0.022251 | -0.0024631 | -0.0061503 | 0.0078058 | 0.045776 | 0.19226 | -0.21515 | 0.14191 | 0.022888 | 0.10071 | -0.018311 | 0.20599 | 0.24261 | -122.7173 | 122.0993 | 0.064087 | 122.3602 | 122.4564 | -0.10529 | -0.40283 | 0.11444 | 0.26093 | 122.2961 | 122.5204 | 122.3373 | 122.5067 | 122.3602 | 122.5571 | 122.4152 | -0.40283 | 122.5067 | 122.3602 | 122.4152 | 122.3373 | 122.5571 | -0.34332 | -122.8455
1990.7344 | 122.5433 | -122.3373 | 0.10986 | -0.0049592 | 0.015035 | 0.012405 | 0.013279 | -0.0045993 | -0.0061503 | 0.0078058 | 0.050354 | 0.17395 | -0.20142 | 0.15106 | 0.07782 | 0.16937 | -0.09613 | 0.2655 | 0.22888 | -122.699 | 122.1359 | 0.064087 | 122.3877 | 122.4884 | -0.032043 | -0.36163 | 0.11902 | 0.25177 | 122.2412 | 122.6028 | 122.4152 | 122.5113 | 122.3877 | 122.5662 | 122.5067 | -0.36163 | 122.5113 | 122.3877 | 122.5067 | 122.4152 | 122.5662 | -0.31128 | -122.8088
1992.5 | 122.5983 | -122.3236 | 0.13275 | -0.0049592 | 0.018025 | 0.014328 | 0.020115 | -0.0028903 | -0.0070047 | 0.0093012 | 0.022888 | 0.18768 | -0.19684 | 0.13733 | 0.032043 | 0.11902 | -0.10986 | 0.21515 | 0.26093 | -122.6715 | 122.1268 | 0.054932 | 122.3465 | 122.4609 | -0.10071 | -0.3479 | 0.12817 | 0.21973 | 122.2137 | 122.5388 | 122.3557 | 122.5113 | 122.3465 | 122.5845 | 122.4426 | -0.3479 | 122.5113 | 122.3465 | 122.4426 | 122.3557 | 122.5845 | -0.32959 | -122.8043
1994.25 | 122.5159 | -122.3694 | 0.14648 | 0.0026703 | 0.01418 | 0.010055 | 0.017124 | -0.0041721 | -0.0048685 | 0.0073786 | 0.09613 | 0.15564 | -0.16479 | 0.18768 | 0.10529 | 0.1831 | -0.17395 | 0.3067 | 0.22888 | -122.6624 | 122.2046 | 0.009156 | 122.4655 | 122.5571 | -0.041198 | -0.29297 | 0.082398 | 0.26092 | 122.1954 | 122.6761 | 122.4747 | 122.525 | 122.4655 | 122.5983 | 122.5525 | -0.29297 | 122.525 | 122.4655 | 122.5525 | 122.4747 | 122.5983 | -0.31128 | -122.8088
1995.9531 | 122.5067 | -122.3419 | 0.14191 | 0.0026703 | 0.015462 | 0.010696 | 0.01456 | -0.0041721 | -0.0076455 | 0.0090876 | 0.10529 | 0.1831 | -0.16937 | 0.21515 | 0.11902 | 0.1831 | -0.09613 | 0.32501 | 0.22888 | -122.6852 | 122.1725 | 0.041198 | 122.4472 | 122.5571 | -0.022888 | -0.34332 | 0.086975 | 0.27466 | 122.2458 | 122.6669 | 122.4609 | 122.525 | 122.4472 | 122.5708 | 122.525 | -0.34332 | 122.525 | 122.4472 | 122.525 | 122.4609 | 122.5708 | -0.31128 | -122.8271
1997.7031 | 122.493 | -122.3648 | 0.15106 | -0.0049592 | 0.016744 | 0.011123 | 0.019474 | -0.0016087 | -0.0063639 | 0.0084468 | 0.11902 | 0.16022 | -0.17853 | 0.21057 | 0.11444 | 0.20142 | -0.18768 | 0.30212 | 0.21057 | -122.6761 | 122.1863 | 0.009155 | 122.4838 | 122.5754 | -0.036621 | -0.31128 | 0.059509 | 0.29755 | 122.1771 | 122.6669 | 122.4792 | 122.525 | 122.4838 | 122.5754 | 122.5662 | -0.31128 | 122.525 | 122.4838 | 122.5662 | 122.4792 | 122.5754 | -0.32959 | -122.8271
1999.4688 | 122.5021 | -122.374 | 0.14191 | -0.012589 | 0.018025 | 0.0089871 | 0.016269 | -0.0041721 | -0.0061503 | 0.0075922 | 0.10071 | 0.16479 | -0.17853 | 0.23346 | 0.13275 | 0.21973 | -0.15564 | 0.33875 | 0.21515 | -122.6852 | 122.1954 | 0.022888 | 122.4747 | 122.6074 | -0.009156 | -0.31128 | 0.073242 | 0.27924 | 122.2183 | 122.7127 | 122.5067 | 122.5388 | 122.4747 | 122.5891 | 122.5937 | -0.31128 | 122.5388 | 122.4747 | 122.5937 | 122.5067 | 122.5891 | -0.32044 | -122.8271
2001.2344 | 122.6532 | -122.3145 | 0.10071 | 0.0026703 | 0.017385 | 0.01326 | 0.02396 | -0.0041721 | -0.0076455 | 0.008233 | -0.004578 | 0.20142 | -0.2243 | 0.09613 | -0.013733 | 0.054932 | -0.022888 | 0.16022 | 0.26093 | -122.7173 | 122.0901 | 0.10071 | 122.3099 | 122.4106 | -0.11444 | -0.40283 | 0.16022 | 0.21973 | 122.2916 | 122.4747 | 122.3007 | 122.5159 | 122.3099 | 122.5754 | 122.3694 | -0.40283 | 122.5159 | 122.3099 | 122.3694 | 122.3007 | 122.5754 | -0.32501 | -122.818
2003 | 122.5204 | -122.3923 | 0.14648 | 0.0026703 | 0.017812 | 0.012192 | 0.01926 | -0.0035313 | -0.0057229 | 0.007165 | 0.12817 | 0.16479 | -0.17395 | 0.21973 | 0.1236 | 0.19226 | -0.19226 | 0.29297 | 0.21057 | -122.7127 | 122.2183 | 0.018311 | 122.5204 | 122.612 | -0.022888 | -0.32044 | 0.064087 | 0.30212 | 122.2 | 122.6852 | 122.5159 | 122.5571 | 122.5204 | 122.6028 | 122.5845 | -0.32044 | 122.5571 | 122.5204 | 122.5845 | 122.5159 | 122.6028 | -0.32043 | -122.8592
2004.7031 | 122.5708 | -122.3694 | 0.14648 | 0.0026703 | 0.018453 | 0.012619 | 0.01691 | -0.0037449 | -0.0044413 | 0.0090876 | 0.050354 | 0.16937 | -0.19684 | 0.16937 | 0.059509 | 0.13733 | -0.10529 | 0.25177 | 0.2243 | -122.7173 | 122.1725 | 0.022889 | 122.4197 | 122.5388 | -0.086975 | -0.3479 | 0.07782 | 0.24719 | 122.2641 | 122.6212 | 122.4289 | 122.5388 | 122.4197 | 122.5937 | 122.5067 | -0.3479 | 122.5388 | 122.4197 | 122.5067 | 122.4289 | 122.5937 | -0.34332 | -122.8638
2006.4688 | 122.6212 | -122.3694 | 0.11902 | 0.0026703 | 0.016317 | 0.01091 | 0.022037 | -0.0018223 | -0.0076455 | 0.0069514 | 0.064087 | 0.1831 | -0.21057 | 0.16479 | 0.022888 | 0.091553 | -0.032043 | 0.20599 | 0.24719 | -122.7036 | 122.1588 | 0.064086 | 122.4335 | 122.5342 | -0.096131 | -0.33417 | 0.12817 | 0.27466 | 122.3373 | 122.5754 | 122.3923 | 122.5525 | 122.4335 | 122.6166 | 122.4609 | -0.33417 | 122.5525 | 122.4335 | 122.4609 | 122.3923 | 122.6166 | -0.32959 | -122.8226
2008.2188 | 122.6486 | -122.3099 | 0.11444 | -0.012589 | 0.020589 | 0.011551 | 0.02161 | -0.00054047 | -0.0046549 | 0.0060968 | 0.018311 | 0.21057 | -0.21057 | 0.1236 | 0.018311 | 0.068665 | 0.036621 | 0.21057 | 0.27008 | -122.7448 | 122.0993 | 0.09613 | 122.3282 | 122.4335 | -0.09613 | -0.43488 | 0.15564 | 0.22888 | 122.3465 | 122.5204 | 122.3282 | 122.5204 | 122.3282 | 122.58 | 122.3785 | -0.43488 | 122.5204 | 122.3282 | 122.3785 | 122.3282 | 122.58 | -0.32501 | -122.8592
2009.9688 | 122.5113 | -122.3923 | 0.12817 | -0.0049592 | 0.015462 | 0.0079189 | 0.016269 | -0.0058811 | -0.0059365 | 0.008874 | 0.09613 | 0.16937 | -0.17853 | 0.21973 | 0.14191 | 0.20142 | -0.14648 | 0.3479 | 0.22888 | -122.6944 | 122.2137 | 0.041199 | 122.4884 | 122.612 | 0.013733 | -0.30212 | 0.10071 | 0.27466 | 122.2458 | 122.7402 | 122.5342 | 122.5616 | 122.4884 | 122.6212 | 122.5937 | -0.30212 | 122.5616 | 122.4884 | 122.5937 | 122.5342 | 122.6212 | -0.3067 | -122.8226
2011.6719 | 122.6578 | -122.319 | 0.09613 | 0.0103 | 0.017812 | 0.011551 | 0.020542 | -0.0043857 | -0.0076455 | 0.0075922 | -0.013733 | 0.21057 | -0.21973 | 0.10071 | 0.013733 | 0.073242 | 0.045776 | 0.20599 | 0.2655 | -122.7356 | 122.0993 | 0.11444 | 122.3053 | 122.4197 | -0.082397 | -0.41657 | 0.16937 | 0.20599 | 122.3648 | 122.525 | 122.3328 | 122.5296 | 122.3053 | 122.5845 | 122.3923 | -0.41657 | 122.5296 | 122.3053 | 122.3923 | 122.3328 | 122.5845 | -0.31586 | -122.8317
2013.4219 | 122.5433 | -122.3648 | 0.14648 | -0.012589 | 0.016744 | 0.0053555 | 0.018619 | -0.0045993 | -0.0057229 | 0.0097284 | 0.10071 | 0.15564 | -0.18768 | 0.19226 | 0.10529 | 0.1831 | -0.17395 | 0.29755 | 0.21515 | -122.6852 | 122.1771 | 0.009156 | 122.4655 | 122.5571 | -0.041198 | -0.32044 | 0.068665 | 0.28839 | 122.1909 | 122.6624 | 122.4701 | 122.5204 | 122.4655 | 122.58 | 122.5479 | -0.32044 | 122.5204 | 122.4655 | 122.5479 | 122.4701 | 122.58 | -0.33417 | -122.8317
2015.1719 | 122.6669 | -122.3328 | 0.10986 | 0.0103 | 0.015462 | 0.013901 | 0.021183 | -0.0031039 | -0.0080729 | 0.008874 | 0.004578 | 0.20599 | -0.22888 | 0.10071 | 0 | 0.064087 | 0.013733 | 0.15564 | 0.2655 | -122.7448 | 122.1039 | 0.096131 | 122.3373 | 122.4335 | -0.10986 | -0.41199 | 0.15564 | 0.23346 | 122.3465 | 122.4884 | 122.3328 | 122.5388 | 122.3373 | 122.5983 | 122.3969 | -0.41199 | 122.5388 | 122.3373 | 122.3969 | 122.3328 | 122.5983 | -0.33875 | -122.8546
2016.9375 | 122.6807 | -122.3328 | 0.10986 | 0.0026703 | 0.019521 | 0.0098417 | 0.021183 | -0.0020359 | -0.0080729 | 0.0075922 | -0.018311 | 0.21973 | -0.21515 | 0.086975 | -0.022888 | 0.068665 | 0.004578 | 0.15106 | 0.2655 | -122.7264 | 122.1176 | 0.10986 | 122.3145 | 122.4197 | -0.13275 | -0.39368 | 0.15564 | 0.19684 | 122.3373 | 122.4838 | 122.3099 | 122.5525 | 122.3145 | 122.5983 | 122.4014 | -0.39368 | 122.5525 | 122.3145 | 122.4014 | 122.3099 | 122.5983 | -0.32501 | -122.8363
2018.625 | 122.5388 | -122.4014 | 0.11902 | 0.0103 | 0.016103 | 0.0092007 | 0.017124 | -0.0031039 | -0.0076455 | 0.0090876 | 0.10071 | 0.16937 | -0.16479 | 0.19226 | 0.10071 | 0.21057 | -0.16937 | 0.29755 | 0.22888 | -122.7219 | 122.2366 | 0.050354 | 122.5021 | 122.5937 | -0.018311 | -0.32044 | 0.10986 | 0.2655 | 122.2321 | 122.699 | 122.5021 | 122.5708 | 122.5021 | 122.6303 | 122.612 | -0.32044 | 122.5708 | 122.5021 | 122.612 | 122.5021 | 122.6303 | -0.28381 | -122.8409
2020.3906 | 122.525 | -122.4152 | 0.1236 | -0.0049592 | 0.017171 | 0.0053555 | 0.015629 | -0.0067355 | -0.0044413 | 0.0067378 | 0.10986 | 0.16022 | -0.17853 | 0.21057 | 0.13733 | 0.21973 | -0.14191 | 0.35706 | 0.21973 | -122.7539 | 122.2366 | 0.036621 | 122.525 | 122.6257 | 0.013733 | -0.33875 | 0.096131 | 0.28839 | 122.2733 | 122.7722 | 122.5525 | 122.5754 | 122.525 | 122.6349 | 122.6349 | -0.33875 | 122.5754 | 122.525 | 122.6349 | 122.5525 | 122.6349 | -0.30212 | -122.8775
2022.1562 | 122.5891 | -122.3969 | 0.14191 | 0.0026703 | 0.015248 | 0.011337 | 0.018619 | -0.0048129 | -0.0042277 | 0.0073786 | 0.064087 | 0.15564 | -0.17853 | 0.14648 | 0.064087 | 0.15564 | -0.11444 | 0.25177 | 0.23804 | -122.7356 | 122.2183 | 0.013733 | 122.4609 | 122.5433 | -0.07782 | -0.33875 | 0.09613 | 0.24261 | 122.2824 | 122.6486 | 122.4609 | 122.5525 | 122.4609 | 122.6349 | 122.5525 | -0.33875 | 122.5525 | 122.4609 | 122.5525 | 122.4609 | 122.6349 | -0.32044 | -122.8775
2023.9375 | 122.493 | -122.2549 | 0.10529 | 0.0026703 | 0.020375 | 0.0081327 | 0.011143 | -0.0033175 | -0.0040139 | 0.0080194 | 0.013733 | 0.19684 | -0.24719 | 0.10986 | -0.013733 | 0.059509 | 0.045776 | 0.19226 | 0.24261 | -122.6303 | 122.0078 | 0.091552 | 122.2687 | 122.3648 | -0.11902 | -0.37537 | 0.13733 | 0.26093 | 122.3007 | 122.4472 | 122.2412 | 122.4518 | 122.2687 | 122.4976 | 122.3145 | -0.37537 | 122.4518 | 122.2687 | 122.3145 | 122.2412 | 122.4976 | -0.35248 | -122.7356
2025.7031 | 122.5525 | -122.4335 | 0.13275 | -0.0049592 | 0.018453 | 0.0092007 | 0.010288 | -0.0037449 | -0.0040139 | 0.0084468 | 0.068665 | 0.16022 | -0.1831 | 0.17395 | 0.07782 | 0.15564 | -0.14191 | 0.2655 | 0.22888 | -122.7448 | 122.2504 | 0.027466 | 122.5021 | 122.6074 | -0.054931 | -0.31128 | 0.096131 | 0.25177 | 122.2916 | 122.699 | 122.5113 | 122.5937 | 122.5021 | 122.6624 | 122.5891 | -0.31128 | 122.5937 | 122.5021 | 122.5891 | 122.5113 | 122.6624 | -0.31586 | -122.8775
2027.4062 | 122.612 | -122.3831 | 0.10071 | 0.0026703 | 0.018666 | 0.013046 | 0.019901 | -0.00054047 | -0.0078591 | 0.008233 | 0.064087 | 0.16937 | -0.2243 | 0.15564 | 0.018311 | 0.10529 | -0.045776 | 0.21973 | 0.26093 | -122.7264 | 122.1588 | 0.068665 | 122.4472 | 122.5388 | -0.082397 | -0.34332 | 0.16022 | 0.28839 | 122.3373 | 122.6028 | 122.4014 | 122.5525 | 122.4472 | 122.644 | 122.4884 | -0.34332 | 122.5525 | 122.4472 | 122.4884 | 122.4014 | 122.644 | -0.32501 | -122.8271
2029.0938 | 122.6898 | -122.3831 | 0.10529 | -0.0049592 | 0.016317 | 0.0083463 | 0.017124 | -0.0026767 | -0.0055093 | 0.0073786 | -0.036621 | 0.19226 | -0.21515 | 0.082397 | -0.013733 | 0.059509 | -0.009155 | 0.15106 | 0.24719 | -122.7585 | 122.168 | 0.086975 | 122.3465 | 122.4655 | -0.11902 | -0.37537 | 0.14191 | 0.17853 | 122.374 | 122.5342 | 122.3694 | 122.5754 | 122.3465 | 122.6303 | 122.4426 | -0.37537 | 122.5754 | 122.3465 | 122.4426 | 122.3694 | 122.6303 | -0.32044 | -122.8638
2030.8594 | 122.58 | -122.3923 | 0.11902 | -0.0049592 | 0.015676 | 0.0064237 | 0.010715 | -0.0043857 | -0.0042277 | 0.0080194 | 0.041199 | 0.17395 | -0.18768 | 0.16022 | 0.091553 | 0.17395 | -0.11444 | 0.27924 | 0.21515 | -122.7402 | 122.2046 | 0.054931 | 122.4335 | 122.5525 | -0.027466 | -0.3479 | 0.09613 | 0.22888 | 122.2778 | 122.6715 | 122.4838 | 122.5662 | 122.4335 | 122.6074 | 122.5662 | -0.3479 | 122.5662 | 122.4335 | 122.5662 | 122.4838 | 122.6074 | -0.3067 | -122.8592
2032.625 | 122.6807 | -122.3602 | 0.11444 | 0.0026703 | 0.019094 | 0.012405 | 0.015201 | -0.0045993 | -0.0067911 | 0.0069514 | -0.009155 | 0.19684 | -0.21973 | 0.09613 | -0.004578 | 0.064087 | 0.041199 | 0.18768 | 0.27008 | -122.7859 | 122.1405 | 0.082397 | 122.3511 | 122.4564 | -0.11902 | -0.42572 | 0.15564 | 0.21057 | 122.4014 | 122.5479 | 122.3557 | 122.5571 | 122.3511 | 122.6303 | 122.4243 | -0.42572 | 122.5571 | 122.3511 | 122.4243 | 122.3557 | 122.6303 | -0.33417 | -122.9004
2034.375 | 122.6349 | -122.3923 | 0.09613 | -0.0049592 | 0.017812 | 0.011337 | 0.01926 | -0.0037449 | -0.0087137 | 0.0093012 | 0.054932 | 0.19684 | -0.21973 | 0.17395 | 0.050354 | 0.11902 | -0.045776 | 0.23804 | 0.24261 | -122.731 | 122.1725 | 0.10071 | 122.4472 | 122.5662 | -0.045776 | -0.33875 | 0.14649 | 0.27466 | 122.3465 | 122.6303 | 122.4426 | 122.5891 | 122.4472 | 122.6349 | 122.5113 | -0.33875 | 122.5891 | 122.4472 | 122.5113 | 122.4426 | 122.6349 | -0.31586 | -122.8271
2036.0781 | 122.5891 | -122.4197 | 0.12817 | -0.0049592 | 0.014821 | 0.013046 | 0.011143 | -0.0041721 | -0.0050821 | 0.0093012 | 0.073242 | 0.14648 | -0.1831 | 0.15106 | 0.073242 | 0.14648 | -0.13275 | 0.26093 | 0.21057 | -122.7402 | 122.2366 | 0.01831 | 122.493 | 122.5708 | -0.054932 | -0.32043 | 0.082397 | 0.25635 | 122.287 | 122.6807 | 122.493 | 122.5662 | 122.493 | 122.6303 | 122.5662 | -0.32043 | 122.5662 | 122.493 | 122.5662 | 122.493 | 122.6303 | -0.31128 | -122.8683
2037.8281 | 122.1176 | -121.9025 | 0.11902 | 0.0026703 | 0.017385 | 0.011123 | 0.016483 | -0.0018223 | -0.0057229 | 0.008874 | 0.068665 | 0.19226 | -0.21057 | 0.14648 | 0.045776 | 0.11902 | -0.036621 | -5.0949 | 0.24719 | -122.2321 | 121.6919 | 0.073242 | 121.9711 | 122.049 | -0.073243 | -0.32959 | 0.12817 | 0.27924 | 121.8658 | 116.8076 | 121.9482 | 122.0947 | 121.9711 | 122.1497 | 122.0215 | -0.32959 | 122.0947 | 121.9711 | 122.0215 | 121.9482 | 122.1497 | -0.32959 | -122.3511
2039.5938 | 122.4609 | -122.1863 | 0.10071 | -0.012589 | 0.018453 | 0.012405 | 0.016269 | -0.0013949 | -0.0048685 | 0.010156 | -0.004578 | 0.19684 | -0.21515 | 0.073242 | -0.004578 | 0.064087 | -0.018311 | -0.59052 | 0.27008 | -122.5388 | 121.9711 | 0.09613 | 122.1817 | 122.2595 | -0.10529 | -0.35248 | 0.16937 | 0.21057 | 122.168 | 121.5958 | 122.1817 | 122.3831 | 122.1817 | 122.4564 | 122.2504 | -0.35248 | 122.3831 | 122.1817 | 122.2504 | 122.1817 | 122.4564 | -0.31586 | -122.6395
2041.3594 | 122.5021 | -122.1954 | 0.11902 | -0.0049592 | 0.016957 | 0.013687 | 0.014774 | -0.0031039 | -0.0055093 | 0.012719 | 0.004578 | 0.21057 | -0.21515 | 0.10986 | 0.018311 | 0.073242 | 0.041199 | -0.3891 | 0.2655 | -122.5845 | 121.9803 | 0.091552 | 122.2 | 122.3053 | -0.10071 | -0.3891 | 0.14648 | 0.21973 | 122.2366 | 121.8063 | 122.2137 | 122.406 | 122.2 | 122.4609 | 122.2687 | -0.3891 | 122.406 | 122.2 | 122.2687 | 122.2137 | 122.4609 | -0.33417 | -122.7036
2043.0312 | 122.4609 | -122.2366 | 0.1236 | -0.012589 | 0.018025 | 0.0074917 | 0.011783 | -0.0033175 | -0.0050821 | 0.010583 | 0.054932 | 0.1831 | -0.1831 | 0.15106 | 0.068665 | 0.13733 | -0.11444 | -0.45319 | 0.19684 | -122.5983 | 122.0535 | 0.059509 | 122.2916 | 122.3877 | -0.054931 | -0.36163 | 0.073242 | 0.23804 | 122.1222 | 121.7834 | 122.3053 | 122.4197 | 122.2916 | 122.4335 | 122.374 | -0.36163 | 122.4197 | 122.2916 | 122.374 | 122.3053 | 122.4335 | -0.3067 | -122.7219
2044.7812 | 122.4243 | -122.2824 | 0.14648 | -0.0049592 | 0.015462 | 0.0096279 | 0.01157 | -0.0037449 | -0.0067911 | 0.0086604 | 0.10986 | 0.14648 | -0.17853 | 0.20142 | 0.11444 | 0.19684 | -0.1831 | -0.27008 | 0.21515 | -122.5845 | 122.1039 | 0 | 122.3923 | 122.4838 | -0.032043 | -0.30212 | 0.068665 | 0.28839 | 122.0993 | 122.0123 | 122.3969 | 122.4289 | 122.3923 | 122.4976 | 122.4792 | -0.30212 | 122.4289 | 122.3923 | 122.4792 | 122.3969 | 122.4976 | -0.32501 | -122.731
2046.5469 | 122.5571 | -122.2458 | 0.10529 | 0.0026703 | 0.019307 | 0.0079189 | 0.017124 | -0.0041721 | -0.0061503 | 0.008233 | -0.027466 | 0.19226 | -0.22888 | 0.10986 | 0 | 0.050354 | 0.07782 | -0.20142 | 0.26093 | -122.6486 | 122.0169 | 0.086975 | 122.2183 | 122.3557 | -0.10529 | -0.40283 | 0.15564 | 0.20142 | 122.3236 | 122.0444 | 122.2458 | 122.4381 | 122.2183 | 122.5067 | 122.2961 | -0.40283 | 122.4381 | 122.2183 | 122.2961 | 122.2458 | 122.5067 | -0.33417 | -122.7539
2048.2344 | 122.5754 | -122.2458 | 0.10529 | -0.0049592 | 0.019307 | 0.015396 | 0.01691 | -0.0041721 | -0.0050821 | 0.01101 | 0.009155 | 0.20599 | -0.23804 | 0.10071 | 0.009155 | 0.059509 | 0.064087 | -0.16022 | 0.2655 | -122.6852 | 122.0078 | 0.10071 | 122.2549 | 122.3465 | -0.096131 | -0.43945 | 0.16022 | 0.24719 | 122.3099 | 122.0856 | 122.2549 | 122.4518 | 122.2549 | 122.5113 | 122.3053 | -0.43945 | 122.4518 | 122.2549 | 122.3053 | 122.2549 | 122.5113 | -0.34332 | -122.7905
2050 | 122.5113 | -122.2916 | 0.13733 | 0.0026703 | 0.016103 | 0.0070645 | 0.011997 | -0.0039585 | -0.0063639 | 0.012292 | 0.036621 | 0.18768 | -0.19226 | 0.16022 | 0.059509 | 0.15106 | -0.091553 | 0.27008 | 0.2243 | -122.6532 | 122.0993 | 0.050354 | 122.3282 | 122.4518 | -0.07782 | -0.36163 | 0.086975 | 0.22888 | 122.2 | 122.5616 | 122.3511 | 122.4792 | 122.3282 | 122.5159 | 122.4426 | -0.36163 | 122.4792 | 122.3282 | 122.4426 | 122.3511 | 122.5159 | -0.32959 | -122.7905
2051.75 | 122.4747 | -122.3236 | 0.15106 | 0.0026703 | 0.015248 | 0.0079189 | 0.017124 | -0.0020359 | -0.0061503 | 0.010797 | 0.10529 | 0.16479 | -0.16937 | 0.20142 | 0.10071 | 0.20599 | -0.1831 | 0.31128 | 0.21515 | -122.6257 | 122.1542 | 0.013733 | 122.4289 | 122.525 | -0.050354 | -0.30212 | 0.064087 | 0.27466 | 122.1405 | 122.6349 | 122.4243 | 122.4884 | 122.4289 | 122.5388 | 122.5296 | -0.30212 | 122.4884 | 122.4289 | 122.5296 | 122.4243 | 122.5388 | -0.32044 | -122.7768
2053.5 | 117.1783 | -78.3966 | 38.5025 | 0.0026703 | 0.017385 | 0.010483 | 6.9377 | 0.0086453 | -0.010636 | 7.0221 | 0.073242 | 0.14191 | -0.1831 | 0.15564 | 28.3768 | 28.4775 | -0.032043 | -19.2902 | 27.2736 | -64.3616 | 78.2135 | -38.3606 | 78.4698 | 78.5522 | -10.1257 | 14.035 | -11.2289 | 0.25635 | 78.3646 | 59.1064 | 106.7734 | 78.5385 | 78.4698 | 105.6702 | 106.8741 | 14.035 | 78.5385 | 78.4698 | 106.8741 | 106.7734 | 105.6702 | -38.6856 | -102.8641
2055.25 | 122.3511 | -122.081 | 0.09613 | 0.0103 | 0.017598 | 0.011337 | 0.011783 | -0.0031039 | -0.0044413 | 0.0075922 | -0.013733 | 0.20599 | -0.20599 | 0.082397 | 0.004578 | 0.045776 | 0.054932 | 0.19684 | 0.26093 | -122.4243 | 121.875 | 0.10986 | 122.0673 | 122.1634 | -0.091552 | -0.34332 | 0.1648 | 0.19226 | 122.1359 | 122.2778 | 122.0856 | 122.287 | 122.0673 | 122.3419 | 122.1268 | -0.34332 | 122.287 | 122.0673 | 122.1268 | 122.0856 | 122.3419 | -0.30212 | -122.5204
2056.9688 | 122.1588 | -121.7194 | 0.10071 | 0.0026703 | 0.017385 | 0.010269 | 0.0092199 | -0.0031039 | -0.0061503 | 0.005456 | -0.022888 | 0.19226 | -0.23804 | 0.09613 | 0.009155 | 0.068665 | 0.032043 | 0.19684 | 0.27008 | -122.1634 | 121.4813 | 0.091553 | 121.6965 | 121.8155 | -0.091553 | -0.44403 | 0.16937 | 0.21515 | 121.7514 | 121.9162 | 121.7285 | 121.9116 | 121.6965 | 121.9894 | 121.788 | -0.44403 | 121.9116 | 121.6965 | 121.788 | 121.7285 | 121.9894 | -0.33875 | -122.2641
2058.7344 | 122.0673 | -121.6644 | 0.091553 | 0.0026703 | 0.018025 | 0.010269 | 0.01456 | -0.0026767 | -0.0035867 | 0.010583 | -0.022888 | 0.18768 | -0.21515 | 0.10071 | -0.009155 | 0.054932 | 0.045776 | 0.19684 | 0.26093 | -122.081 | 121.4493 | 0.09613 | 121.6415 | 121.7651 | -0.10071 | -0.41657 | 0.16937 | 0.19226 | 121.7102 | 121.8613 | 121.6553 | 121.8521 | 121.6415 | 121.9254 | 121.7194 | -0.41657 | 121.8521 | 121.6415 | 121.7194 | 121.6553 | 121.9254 | -0.3067 | -122.1725
2060.4375 | 121.8201 | -121.431 | 0.10529 | 0.0026703 | 0.016317 | 0.014328 | 0.012424 | -0.00096767 | -0.0023049 | 0.0069514 | -0.018311 | 0.19226 | -0.21057 | 0.1236 | 0.009155 | 0.086975 | -0.07782 | 0.18768 | 0.2243 | -121.8063 | 121.2204 | 0.086975 | 121.4127 | 121.5546 | -0.096131 | -0.37537 | 0.11902 | 0.19226 | 121.3531 | 121.6187 | 121.4401 | 121.6232 | 121.4127 | 121.6553 | 121.5179 | -0.37537 | 121.6232 | 121.4127 | 121.5179 | 121.4401 | 121.6553 | -0.31586 | -121.9116
2062.1875 | 121.9849 | -121.7697 | 0.14191 | -0.0049592 | 0.01888 | 0.012192 | 0.0083655 | -0.0054539 | -0.0035867 | 0.0063104 | 0.10529 | 0.16937 | -0.16479 | 0.21973 | 0.1236 | 0.20142 | -0.15564 | 0.3479 | 0.21973 | -122.1039 | 121.6049 | 0.027466 | 121.875 | 121.9894 | -0.018311 | -0.33417 | 0.07782 | 0.27008 | 121.6141 | 122.1176 | 121.8933 | 121.9391 | 121.875 | 121.9894 | 121.9711 | -0.33417 | 121.9391 | 121.875 | 121.9711 | 121.8933 | 121.9894 | -0.3067 | -122.2458
2063.9531 | 122.0352 | -121.8613 | 0.13275 | -0.0049592 | 0.015462 | 0.0098417 | 0.010929 | -0.0041721 | -0.0027323 | 0.0060968 | 0.086975 | 0.16937 | -0.18768 | 0.21973 | 0.1236 | 0.19684 | -0.16479 | 0.33417 | 0.20142 | -122.1588 | 121.6736 | 0.036622 | 121.9482 | 122.081 | -0.009155 | -0.29755 | 0.068665 | 0.27466 | 121.6965 | 122.1954 | 121.9849 | 122.0306 | 121.9482 | 122.0627 | 122.0581 | -0.29755 | 122.0306 | 121.9482 | 122.0581 | 121.9849 | 122.0627 | -0.32043 | -122.2916
2065.7031 | 122.1725 | -121.8613 | 0.10986 | 0.0026703 | 0.016744 | 0.012832 | 0.015629 | -0.00054047 | -0.0065775 | 0.0078058 | 0.004578 | 0.19684 | -0.2243 | 0.11444 | -0.013733 | 0.082397 | -0.059509 | 0.16937 | 0.23346 | -122.1817 | 121.637 | 0.086975 | 121.8658 | 121.9757 | -0.1236 | -0.32044 | 0.1236 | 0.22888 | 121.8018 | 122.0306 | 121.8475 | 122.0581 | 121.8658 | 122.0947 | 121.9437 | -0.32044 | 122.0581 | 121.8658 | 121.9437 | 121.8475 | 122.0947 | -0.33417 | -122.2916
2067.4062 | 122.0673 | -121.9299 | 0.13733 | 0.0026703 | 0.015462 | 0.0098417 | 0.01456 | -0.0033175 | -0.0031595 | 0.0073786 | 0.091553 | 0.16479 | -0.17395 | 0.2243 | 0.09613 | 0.18768 | -0.19684 | 0.29297 | 0.20142 | -122.1817 | 121.756 | 0.027466 | 122.0215 | 122.1542 | -0.041199 | -0.25177 | 0.064087 | 0.2655 | 121.7331 | 122.2229 | 122.0261 | 122.0947 | 122.0215 | 122.1313 | 122.1176 | -0.25177 | 122.0947 | 122.0215 | 122.1176 | 122.0261 | 122.1313 | -0.31128 | -122.319
2069.0938 | 121.9574 | -121.9345 | 0.15106 | 0.0026703 | 0.01653 | 0.013687 | 0.011143 | -0.0033175 | -0.0080729 | 0.0069514 | 0.10529 | 0.14648 | -0.17853 | 0.23804 | 0.11902 | 0.19226 | -0.1236 | 0.35706 | 0.20599 | -122.2504 | 121.756 | -0.004578 | 122.0398 | 122.1725 | -0.032043 | -0.31586 | 0.054932 | 0.28381 | 121.8109 | 122.2916 | 122.0535 | 122.081 | 122.0398 | 122.1405 | 122.1268 | -0.31586 | 122.081 | 122.0398 | 122.1268 | 122.0535 | 122.1405 | -0.32959 | -122.4014
2070.8438 | 122.2366 | -121.9162 | 0.10529 | 0.0026703 | 0.019734 | 0.012832 | 0.017124 | -0.0041721 | -0.0046549 | 0.0084468 | -0.009155 | 0.20142 | -0.21973 | 0.086975 | -0.009155 | 0.059509 | -0.009155 | 0.15564 | 0.23804 | -122.2687 | 121.6965 | 0.09613 | 121.907 | 122.0032 | -0.11444 | -0.35248 | 0.13275 | 0.21057 | 121.907 | 122.0718 | 121.907 | 122.1176 | 121.907 | 122.1542 | 121.9757 | -0.35248 | 122.1176 | 121.907 | 121.9757 | 121.907 | 122.1542 | -0.32501 | -122.374
2072.625 | 122.1863 | -121.9437 | 0.10986 | 0.0103 | 0.016957 | 0.012192 | 0.01691 | -0.0022495 | -0.0078591 | 0.0084468 | 0.050354 | 0.16937 | -0.21973 | 0.16022 | 0.041199 | 0.09613 | -0.054932 | 0.24719 | 0.24261 | -122.2687 | 121.7239 | 0.05951 | 121.994 | 122.1039 | -0.068664 | -0.32501 | 0.13275 | 0.27008 | 121.8887 | 122.1909 | 121.9849 | 122.113 | 121.994 | 122.1863 | 122.0398 | -0.32501 | 122.113 | 121.994 | 122.0398 | 121.9849 | 122.1863 | -0.32959 | -122.3785
2074.3906 | 122.2229 | -121.9345 | 0.12817 | -0.0049592 | 0.018239 | 0.01091 | 0.014988 | -0.00096767 | -0.0074319 | 0.0095148 | 0.027466 | 0.20142 | -0.22888 | 0.1236 | 0.018311 | 0.082397 | -0.018311 | 0.1831 | 0.24719 | -122.3053 | 121.7056 | 0.073242 | 121.962 | 122.0581 | -0.10986 | -0.37079 | 0.11902 | 0.25635 | 121.9162 | 122.1176 | 121.9528 | 122.1359 | 121.962 | 122.1817 | 122.0169 | -0.37079 | 122.1359 | 121.962 | 122.0169 | 121.9528 | 122.1817 | -0.35706 | -122.4335
2076.0938 | 121.4493 | -121.4951 | 0.14648 | -0.012589 | 0.017385 | 0.0089871 | 0.0096473 | -0.0056675 | -0.0040139 | 0.0075922 | 0.054932 | 0.15564 | -0.18768 | 0.18768 | 0.11444 | 0.17395 | -0.11444 | 0.30212 | 0.21515 | -122.319 | 121.3074 | 0.009156 | 121.55 | 121.6827 | -0.032043 | -0.82397 | 0.068665 | 0.24261 | 121.3806 | 121.7972 | 121.6095 | 121.6507 | 121.55 | 121.7102 | 121.669 | -0.82397 | 121.6507 | 121.55 | 121.669 | 121.6095 | 121.7102 | -0.33417 | -122.4655
2077.8438 | 121.5546 | -121.5317 | 0.12817 | -0.0049592 | 0.017171 | 0.0083463 | 0.010502 | -0.0048129 | -0.0038003 | 0.0067378 | 0.045776 | 0.15564 | -0.17395 | 0.15106 | 0.068665 | 0.13733 | -0.10986 | 0.23346 | 0.22888 | -122.3099 | 121.3577 | 0.027466 | 121.5775 | 121.6827 | -0.059509 | -0.7782 | 0.10071 | 0.21973 | 121.4218 | 121.7651 | 121.6003 | 121.6873 | 121.5775 | 121.7606 | 121.669 | -0.7782 | 121.6873 | 121.5775 | 121.669 | 121.6003 | 121.7606 | -0.30212 | -122.438
2079.6094 | 122.2412 | -121.9849 | 0.11444 | 0.0026703 | 0.015248 | 0.0096279 | 0.017978 | -0.0013949 | -0.0076455 | 0.0080194 | 0.041199 | 0.17395 | -0.21973 | 0.1236 | 0.013733 | 0.07782 | -0.027466 | 0.18768 | 0.24261 | -122.3099 | 121.7651 | 0.059509 | 122.0261 | 122.1085 | -0.10071 | -0.32501 | 0.12817 | 0.26093 | 121.9574 | 122.1725 | 121.9986 | 122.1588 | 122.0261 | 122.2275 | 122.0627 | -0.32501 | 122.1588 | 122.0261 | 122.0627 | 121.9986 | 122.2275 | -0.33417 | -122.4243
2081.3125 | 122.2321 | -122.0169 | 0.12817 | 0.0026703 | 0.021443 | 0.01326 | 0.017124 | 0.00010033 | -0.0074319 | 0.0093012 | 0.073242 | 0.1831 | -0.19684 | 0.15106 | 0.041199 | 0.091553 | -0.041199 | 0.2243 | 0.25177 | -122.3694 | 121.8201 | 0.054931 | 122.0901 | 122.168 | -0.086975 | -0.35248 | 0.1236 | 0.27008 | 121.9757 | 122.2412 | 122.0581 | 122.2 | 122.0901 | 122.2687 | 122.1085 | -0.35248 | 122.2 | 122.0901 | 122.1085 | 122.0581 | 122.2687 | -0.32501 | -122.4976
2083 | 122.2641 | -122.0169 | 0.10529 | 0.0026703 | 0.016317 | 0.013901 | 0.018833 | -0.0033175 | -0.0082865 | 0.0093012 | 0.036621 | 0.19226 | -0.21973 | 0.1236 | 0.032043 | 0.09613 | -0.032043 | 0.19684 | 0.2243 | -122.3511 | 121.7972 | 0.086975 | 122.0535 | 122.1405 | -0.073243 | -0.33417 | 0.11902 | 0.25635 | 121.9849 | 122.2137 | 122.049 | 122.2092 | 122.0535 | 122.2412 | 122.113 | -0.33417 | 122.2092 | 122.0535 | 122.113 | 122.049 | 122.2412 | -0.32501 | -122.4564
2084.75 | 121.8384 | -121.5637 | 0.13275 | -0.012589 | 0.015676 | 0.011551 | 0.0085791 | -0.0041721 | -0.0038003 | 0.0086604 | 0.054932 | 0.15564 | -0.18768 | 0.15106 | 0.064087 | 0.15564 | -0.11444 | 0.24719 | 0.21973 | -122.3373 | 121.376 | 0.022889 | 121.6187 | 121.7148 | -0.068664 | -0.77362 | 0.086976 | 0.24261 | 121.4493 | 121.8109 | 121.6278 | 121.7194 | 121.6187 | 121.7834 | 121.7194 | -0.77362 | 121.7194 | 121.6187 | 121.7194 | 121.6278 | 121.7834 | -0.32043 | -122.4701
2086.5312 | 122.3099 | -121.9894 | 0.10071 | -0.0049592 | 0.018239 | 0.012832 | 0.019047 | -0.0028903 | -0.0072183 | 0.0095148 | -0.004578 | 0.1831 | -0.21973 | 0.082397 | -0.018311 | 0.068665 | -0.022888 | 0.16022 | 0.25635 | -122.3694 | 121.7697 | 0.082397 | 121.9849 | 122.0718 | -0.11902 | -0.37994 | 0.15564 | 0.21515 | 121.9666 | 122.1497 | 121.9711 | 122.1725 | 121.9849 | 122.2458 | 122.0581 | -0.37994 | 122.1725 | 121.9849 | 122.0581 | 121.9711 | 122.2458 | -0.32044 | -122.4701
2088.2188 | 122.3099 | -122.0215 | 0.10986 | 0.0026703 | 0.018666 | 0.015182 | 0.018406 | -0.0033175 | -0.0055093 | 0.0084468 | 0.009155 | 0.1831 | -0.21515 | 0.10071 | -0.004578 | 0.068665 | 0.004578 | 0.17853 | 0.23346 | -122.3648 | 121.8063 | 0.073242 | 122.0306 | 122.1222 | -0.11444 | -0.34332 | 0.1236 | 0.2243 | 122.0261 | 122.2 | 122.0169 | 122.2046 | 122.0306 | 122.2549 | 122.0901 | -0.34332 | 122.2046 | 122.0306 | 122.0901 | 122.0169 | 122.2549 | -0.32501 | -122.4747
2089.9688 | 122.2595 | -122.0123 | 0.10071 | 0.0026703 | 0.017812 | 0.010483 | 0.014347 | -0.0024631 | -0.0085001 | 0.008233 | 0.036621 | 0.20599 | -0.21973 | 0.14648 | 0.050354 | 0.10986 | -0.032043 | 0.23346 | 0.24261 | -122.3648 | 121.7926 | 0.10529 | 122.0489 | 122.1588 | -0.050354 | -0.35248 | 0.14191 | 0.25635 | 121.9803 | 122.2458 | 122.0627 | 122.2183 | 122.0489 | 122.2549 | 122.1222 | -0.35248 | 122.2183 | 122.0489 | 122.1222 | 122.0627 | 122.2549 | -0.32044 | -122.4655
2091.6719 | 122.3236 | -122.0261 | 0.10986 | 0.0026703 | 0.015676 | 0.0089871 | 0.013706 | -0.0024631 | -0.0065775 | 0.008233 | 0.004578 | 0.1831 | -0.22888 | 0.11444 | 0.009155 | 0.082397 | 0.036621 | 0.20599 | 0.24719 | -122.3877 | 121.7972 | 0.073242 | 122.0306 | 122.1405 | -0.10071 | -0.36163 | 0.13733 | 0.23346 | 122.0627 | 122.2321 | 122.0352 | 122.2092 | 122.0306 | 122.2733 | 122.1085 | -0.36163 | 122.2092 | 122.0306 | 122.1085 | 122.0352 | 122.2733 | -0.33875 | -122.4976
2093.4375 | 122.2229 | -122.0856 | 0.13275 | -0.0049592 | 0.015889 | 0.012619 | 0.012424 | -0.0022495 | -0.0048685 | 0.0078058 | 0.09613 | 0.15106 | -0.19684 | 0.20142 | 0.09613 | 0.20599 | -0.18768 | 0.29755 | 0.20599 | -122.3831 | 121.8887 | 0.018311 | 122.1817 | 122.287 | -0.036621 | -0.29755 | 0.073243 | 0.29297 | 121.8979 | 122.3831 | 122.1817 | 122.2366 | 122.1817 | 122.2916 | 122.2916 | -0.29755 | 122.2366 | 122.1817 | 122.2916 | 122.1817 | 122.2916 | -0.32959 | -122.5159
2095.125 | 122.2137 | -122.0947 | 0.13733 | 0.0026703 | 0.014394 | 0.0070645 | 0.012211 | -0.0048129 | -0.0070047 | 0.0093012 | 0.11444 | 0.14648 | -0.16022 | 0.19226 | 0.11902 | 0.20599 | -0.19684 | 0.28839 | 0.20142 | -122.3557 | 121.9345 | 0.009155 | 122.2092 | 122.287 | -0.01831 | -0.26093 | 0.064087 | 0.27466 | 121.8979 | 122.3831 | 122.2137 | 122.2412 | 122.2092 | 122.2961 | 122.3007 | -0.26093 | 122.2412 | 122.2092 | 122.3007 | 122.2137 | 122.2961 | -0.29755 | -122.493
2096.8281 | 122.3602 | -122.0718 | 0.10529 | 0.0026703 | 0.018025 | 0.012405 | 0.016269 | -0.0024631 | -0.0078591 | 0.0069514 | -0.018311 | 0.20142 | -0.2243 | 0.068665 | -0.027466 | 0.045776 | 0.009155 | 0.16022 | 0.25177 | -122.4243 | 121.8475 | 0.09613 | 122.0535 | 122.1405 | -0.13275 | -0.35248 | 0.14648 | 0.20599 | 122.081 | 122.2321 | 122.0444 | 122.2733 | 122.0535 | 122.3236 | 122.1176 | -0.35248 | 122.2733 | 122.0535 | 122.1176 | 122.0444 | 122.3236 | -0.32959 | -122.5296
2098.5938 | 122.2366 | -122.0535 | 0.13733 | 0.0026703 | 0.018666 | 0.012405 | 0.0087927 | -0.0054539 | -0.0063639 | 0.0084468 | 0.086975 | 0.16479 | -0.18768 | 0.19684 | 0.11444 | 0.21057 | -0.13733 | 0.32501 | 0.20599 | -122.4335 | 121.8658 | 0.027466 | 122.1405 | 122.2504 | -0.022888 | -0.37994 | 0.068665 | 0.27466 | 121.9162 | 122.3785 | 122.168 | 122.2183 | 122.1405 | 122.2595 | 122.2641 | -0.37994 | 122.2183 | 122.1405 | 122.2641 | 122.168 | 122.2595 | -0.32501 | -122.5708
2100.3438 | 122.3694 | -122.0444 | 0.10071 | 0.0026703 | 0.016317 | 0.012619 | 0.016483 | 0.00052773 | -0.0093545 | 0.008874 | 0 | 0.17853 | -0.22888 | 0.07782 | -0.022888 | 0.059509 | -0.009155 | 0.15106 | 0.25635 | -122.4518 | 121.8155 | 0.07782 | 122.0444 | 122.1222 | -0.1236 | -0.40741 | 0.15564 | 0.22888 | 122.0352 | 122.1954 | 122.0215 | 122.2229 | 122.0444 | 122.3007 | 122.1039 | -0.40741 | 122.2229 | 122.0444 | 122.1039 | 122.0215 | 122.3007 | -0.32959 | -122.5525
2102.1094 | 122.2412 | -122.0993 | 0.13275 | -0.0049592 | 0.015462 | 0.0092007 | 0.010929 | -0.0022495 | -0.0067911 | 0.0073786 | 0.11444 | 0.15564 | -0.19684 | 0.22888 | 0.12817 | 0.21057 | -0.13733 | 0.36163 | 0.19226 | -122.4197 | 121.9025 | 0.022889 | 122.2137 | 122.3282 | -0.004577 | -0.32044 | 0.05951 | 0.31128 | 121.962 | 122.4609 | 122.2275 | 122.2549 | 122.2137 | 122.2916 | 122.3099 | -0.32044 | 122.2549 | 122.2137 | 122.3099 | 122.2275 | 122.2916 | -0.32959 | -122.5525
2103.8594 | 122.2961 | -122.0901 | 0.1236 | -0.0049592 | 0.016744 | 0.010055 | 0.011356 | -0.0020359 | -0.0063639 | 0.0063104 | 0.045776 | 0.16937 | -0.1831 | 0.15564 | 0.054932 | 0.13275 | -0.11444 | 0.2655 | 0.2243 | -122.406 | 121.907 | 0.045777 | 122.1359 | 122.2458 | -0.068664 | -0.31586 | 0.10071 | 0.22888 | 121.9757 | 122.3557 | 122.1451 | 122.2595 | 122.1359 | 122.3145 | 122.2229 | -0.31586 | 122.2595 | 122.1359 | 122.2229 | 122.1451 | 122.3145 | -0.3067 | -122.5296
2105.625 | 122.3419 | -122.081 | 0.11902 | 0.0026703 | 0.015248 | 0.01091 | 0.016056 | -0.0033175 | -0.0050821 | 0.0095148 | 0.018311 | 0.16937 | -0.21057 | 0.1236 | 0.022888 | 0.07782 | 0.018311 | 0.22888 | 0.23804 | -122.438 | 121.8704 | 0.050354 | 122.0993 | 122.2046 | -0.096131 | -0.35706 | 0.11902 | 0.22888 | 122.0993 | 122.3099 | 122.1039 | 122.2504 | 122.0993 | 122.319 | 122.1588 | -0.35706 | 122.2504 | 122.0993 | 122.1588 | 122.1039 | 122.319 | -0.32959 | -122.5571
2107.3281 | 122.3145 | -122.1085 | 0.1236 | -0.0049592 | 0.015462 | 0.011123 | 0.013492 | -0.0060947 | -0.0063639 | 0.0073786 | 0.068665 | 0.16937 | -0.20142 | 0.14648 | 0.022888 | 0.086975 | 0 | 0.24719 | 0.24261 | -122.4747 | 121.907 | 0.045777 | 122.1771 | 122.2549 | -0.10071 | -0.36621 | 0.11902 | 0.27008 | 122.1085 | 122.3557 | 122.1313 | 122.2778 | 122.1771 | 122.3511 | 122.1954 | -0.36621 | 122.2778 | 122.1771 | 122.1954 | 122.1313 | 122.3511 | -0.32501 | -122.5983
2109.0156 | 122.3282 | -122.1222 | 0.12817 | 0.0026703 | 0.01653 | 0.011764 | 0.01926 | -0.0022495 | -0.0085001 | 0.0080194 | 0.059509 | 0.16937 | -0.21057 | 0.16022 | 0.032043 | 0.11444 | -0.045776 | 0.23804 | 0.24261 | -122.4472 | 121.9116 | 0.041199 | 122.1817 | 122.2824 | -0.096131 | -0.32501 | 0.11444 | 0.27008 | 122.0764 | 122.3602 | 122.1542 | 122.2916 | 122.1817 | 122.3648 | 122.2366 | -0.32501 | 122.2916 | 122.1817 | 122.2366 | 122.1542 | 122.3648 | -0.33875 | -122.5754
2110.7656 | 122.319 | -122.1176 | 0.1236 | 0.0026703 | 0.015676 | 0.0094143 | 0.01157 | -0.0058811 | -0.0038003 | 0.0075922 | 0.050354 | 0.16479 | -0.1831 | 0.18768 | 0.091553 | 0.16937 | -0.11444 | 0.29297 | 0.21515 | -122.4838 | 121.9345 | 0.041199 | 122.168 | 122.3053 | -0.032043 | -0.36621 | 0.091553 | 0.23346 | 122.0032 | 122.4106 | 122.2092 | 122.2824 | 122.168 | 122.3328 | 122.287 | -0.36621 | 122.2824 | 122.168 | 122.287 | 122.2092 | 122.3328 | -0.3067 | -122.6074
2112.4844 | 122.3282 | -122.1451 | 0.14191 | -0.0049592 | 0.017598 | 0.0079189 | 0.011356 | -0.0031039 | -0.0035867 | 0.0084468 | 0.068665 | 0.14648 | -0.17395 | 0.16937 | 0.050354 | 0.15106 | -0.13275 | 0.26093 | 0.21515 | -122.4747 | 121.9711 | 0.004577 | 122.2137 | 122.3145 | -0.091553 | -0.32959 | 0.073242 | 0.24261 | 122.0123 | 122.406 | 122.1954 | 122.2916 | 122.2137 | 122.3602 | 122.2961 | -0.32959 | 122.2916 | 122.2137 | 122.2961 | 122.1954 | 122.3602 | -0.31586 | -122.6166
2114.25 | 122.2916 | -122.1588 | 0.12817 | -0.0049592 | 0.016317 | 0.011337 | 0.017551 | -0.0028903 | -0.0055093 | 0.0095148 | 0.11902 | 0.13275 | -0.17853 | 0.21515 | 0.10071 | 0.19226 | -0.21515 | 0.31128 | 0.20142 | -122.4747 | 121.9803 | 0.004577 | 122.2778 | 122.374 | -0.027466 | -0.31586 | 0.073242 | 0.29755 | 121.9437 | 122.4701 | 122.2595 | 122.2916 | 122.2778 | 122.3602 | 122.3511 | -0.31586 | 122.2916 | 122.2778 | 122.3511 | 122.2595 | 122.3602 | -0.3067 | -122.6028
2116.0156 | 122.4014 | -122.1039 | 0.10071 | -0.0049592 | 0.016103 | 0.010483 | 0.017338 | -0.00054047 | -0.0055093 | 0.007165 | 0.004578 | 0.19226 | -0.22888 | 0.13733 | 0.013733 | 0.073242 | 0.027466 | 0.23346 | 0.25635 | -122.4792 | 121.875 | 0.091553 | 122.1085 | 122.2412 | -0.086975 | -0.37537 | 0.15564 | 0.23346 | 122.1313 | 122.3373 | 122.1176 | 122.2961 | 122.1085 | 122.3602 | 122.1771 | -0.37537 | 122.2961 | 122.1085 | 122.1771 | 122.1176 | 122.3602 | -0.32959 | -122.58
2117.7188 | 122.2916 | -122.1497 | 0.13733 | -0.0049592 | 0.020162 | 0.013901 | 0.014133 | -0.00096767 | -0.0057229 | 0.007165 | 0.1236 | 0.13733 | -0.16479 | 0.20599 | 0.10529 | 0.19226 | -0.1831 | 0.30212 | 0.19226 | -122.4747 | 121.9849 | 0 | 122.2733 | 122.3557 | -0.032043 | -0.32501 | 0.054932 | 0.28839 | 121.9666 | 122.4518 | 122.2549 | 122.287 | 122.2733 | 122.3419 | 122.3419 | -0.32501 | 122.287 | 122.2733 | 122.3419 | 122.2549 | 122.3419 | -0.30212 | -122.612
2119.4688 | 122.3373 | -122.168 | 0.11902 | -0.0049592 | 0.015676 | 0.010055 | 0.01691 | -0.0054539 | -0.0078591 | 0.011437 | 0.07782 | 0.14191 | -0.20599 | 0.19226 | 0.11444 | 0.1831 | -0.16937 | 0.29297 | 0.20599 | -122.4655 | 121.962 | 0.022888 | 122.2458 | 122.3602 | -0.004578 | -0.29755 | 0.086975 | 0.28381 | 121.9986 | 122.4609 | 122.2824 | 122.3099 | 122.2458 | 122.374 | 122.3511 | -0.29755 | 122.3099 | 122.2458 | 122.3511 | 122.2824 | 122.374 | -0.32501 | -122.5845
2121.2188 | 122.4289 | -122.1268 | 0.1236 | -0.020218 | 0.019521 | 0.011551 | 0.015415 | -0.0022495 | -0.0046549 | 0.0073786 | 0.009155 | 0.19226 | -0.21515 | 0.10529 | -0.009155 | 0.07782 | -0.032043 | 0.1831 | 0.26093 | -122.5571 | 121.9116 | 0.068665 | 122.1359 | 122.2321 | -0.13275 | -0.4303 | 0.13733 | 0.2243 | 122.0947 | 122.3099 | 122.1176 | 122.319 | 122.1359 | 122.3877 | 122.2046 | -0.4303 | 122.319 | 122.1359 | 122.2046 | 122.1176 | 122.3877 | -0.33875 | -122.6807
2122.9219 | 122.4335 | -122.1405 | 0.09613 | 0.0103 | 0.018453 | 0.016037 | 0.014347 | -0.0028903 | -0.0080729 | 0.008233 | 0.009155 | 0.19226 | -0.24719 | 0.12817 | 0.013733 | 0.073242 | 0.032043 | 0.21515 | 0.24719 | -122.5525 | 121.8933 | 0.096131 | 122.1497 | 122.2687 | -0.082397 | -0.41199 | 0.15106 | 0.25635 | 122.1725 | 122.3557 | 122.1542 | 122.3328 | 122.1497 | 122.3877 | 122.2137 | -0.41199 | 122.3328 | 122.1497 | 122.2137 | 122.1542 | 122.3877 | -0.34332 | -122.6486
2124.6875 | 122.4014 | -122.1634 | 0.1236 | 0.0103 | 0.020375 | 0.014328 | 0.015629 | -0.0013949 | -0.0052957 | 0.0093012 | 0.054932 | 0.16937 | -0.21515 | 0.16022 | 0.059509 | 0.11444 | -0.032043 | 0.23804 | 0.24719 | -122.5159 | 121.9482 | 0.045777 | 122.2183 | 122.3236 | -0.064087 | -0.35248 | 0.1236 | 0.27008 | 122.1313 | 122.4014 | 122.2229 | 122.3328 | 122.2183 | 122.4106 | 122.2778 | -0.35248 | 122.3328 | 122.2183 | 122.2778 | 122.2229 | 122.4106 | -0.33875 | -122.6395
2126.4375 | 122.4564 | -122.113 | 0.082397 | -0.0049592 | 0.017598 | 0.0092007 | 0.011356 | -0.0041721 | -0.0038003 | 0.010156 | -0.022888 | 0.20142 | -0.23346 | 0.10529 | -0.004578 | 0.054932 | 0.064087 | 0.19684 | 0.24261 | -122.5342 | 121.8796 | 0.11902 | 122.0901 | 122.2183 | -0.086975 | -0.42114 | 0.16022 | 0.21057 | 122.1771 | 122.3099 | 122.1085 | 122.3145 | 122.0901 | 122.3557 | 122.168 | -0.42114 | 122.3145 | 122.0901 | 122.168 | 122.1085 | 122.3557 | -0.31586 | -122.6166
2128.1406 | 122.319 | -122.1909 | 0.13275 | -0.0049592 | 0.016103 | 0.010483 | 0.014347 | -0.0016087 | -0.0065775 | 0.0084468 | 0.10986 | 0.13275 | -0.17395 | 0.20142 | 0.10986 | 0.20599 | -0.19684 | 0.28839 | 0.18768 | -122.5067 | 122.0169 | 0 | 122.3007 | 122.3923 | -0.022888 | -0.31586 | 0.054932 | 0.28381 | 121.994 | 122.4792 | 122.3007 | 122.3236 | 122.3007 | 122.3785 | 122.3969 | -0.31586 | 122.3236 | 122.3007 | 122.3969 | 122.3007 | 122.3785 | -0.3067 | -122.6395
2129.8906 | 122.4106 | -122.1588 | 0.11444 | 0.0026703 | 0.017385 | 0.011337 | 0.01456 | -0.0050265 | -0.0063639 | 0.0095148 | 0.032043 | 0.1831 | -0.21057 | 0.11444 | 0.022888 | 0.086975 | 0.032043 | 0.21973 | 0.23804 | -122.5708 | 121.9482 | 0.068664 | 122.1909 | 122.2733 | -0.091553 | -0.41199 | 0.1236 | 0.24261 | 122.1909 | 122.3785 | 122.1817 | 122.3419 | 122.1909 | 122.3969 | 122.2458 | -0.41199 | 122.3419 | 122.1909 | 122.2458 | 122.1817 | 122.3969 | -0.32501 | -122.6852
2131.5938 | 122.4106 | -122.168 | 0.086975 | -0.0049592 | 0.015889 | 0.011551 | 0.016697 | -0.0028903 | -0.0097819 | 0.0075922 | 0.041199 | 0.16937 | -0.21973 | 0.14648 | 0.045776 | 0.10986 | -0.013733 | 0.24719 | 0.24261 | -122.5433 | 121.9482 | 0.082398 | 122.2092 | 122.3145 | -0.041199 | -0.37537 | 0.15564 | 0.26093 | 122.1542 | 122.4152 | 122.2137 | 122.3373 | 122.2092 | 122.4106 | 122.2778 | -0.37537 | 122.3373 | 122.2092 | 122.2778 | 122.2137 | 122.4106 | -0.3067 | -122.6303
2133.3594 | 122.3831 | -122.1863 | 0.11902 | 0.0103 | 0.01418 | 0.011551 | 0.0090063 | -0.0028903 | -0.0065775 | 0.0097284 | 0.036621 | 0.14648 | -0.19226 | 0.14648 | 0.068665 | 0.14648 | -0.11902 | 0.25635 | 0.24719 | -122.5021 | 121.994 | 0.027465 | 122.2229 | 122.3328 | -0.050354 | -0.31586 | 0.12817 | 0.22888 | 122.0673 | 122.4426 | 122.2549 | 122.3328 | 122.2229 | 122.4335 | 122.3328 | -0.31586 | 122.3328 | 122.2229 | 122.3328 | 122.2549 | 122.4335 | -0.31128 | -122.6212
2135.0625 | 122.4884 | -122.1634 | 0.10071 | -0.012589 | 0.019734 | 0.01561 | 0.017124 | -0.0013949 | -0.0072183 | 0.008874 | 0.009155 | 0.18768 | -0.21057 | 0.091553 | -0.022888 | 0.064087 | -0.013733 | 0.15106 | 0.24719 | -122.5662 | 121.9528 | 0.086975 | 122.1725 | 122.2549 | -0.1236 | -0.40283 | 0.14648 | 0.21973 | 122.1497 | 122.3145 | 122.1405 | 122.3511 | 122.1725 | 122.4106 | 122.2275 | -0.40283 | 122.3511 | 122.1725 | 122.2275 | 122.1405 | 122.4106 | -0.31128 | -122.6669
2136.8281 | 122.374 | -122.1817 | 0.13733 | -0.012589 | 0.016317 | 0.010483 | 0.011356 | -0.0035313 | -0.0057229 | 0.008874 | 0.045776 | 0.15564 | -0.18768 | 0.17853 | 0.09613 | 0.1831 | -0.12817 | 0.3067 | 0.19226 | -122.5433 | 121.994 | 0.018311 | 122.2275 | 122.3602 | -0.041199 | -0.36163 | 0.054932 | 0.23346 | 122.0535 | 122.4884 | 122.2778 | 122.3373 | 122.2275 | 122.374 | 122.3648 | -0.36163 | 122.3373 | 122.2275 | 122.3648 | 122.2778 | 122.374 | -0.32501 | -122.6807
2138.5938 | 122.4747 | -122.1863 | 0.10529 | -0.0049592 | 0.017812 | 0.0066373 | 0.014347 | -0.0043857 | -0.0061503 | 0.0090876 | -0.018311 | 0.20142 | -0.22888 | 0.10529 | 0.009155 | 0.064087 | 0.036621 | 0.1831 | 0.26093 | -122.5708 | 121.9574 | 0.09613 | 122.168 | 122.2916 | -0.096131 | -0.38452 | 0.15564 | 0.21057 | 122.2229 | 122.3694 | 122.1954 | 122.3877 | 122.168 | 122.4472 | 122.2504 | -0.38452 | 122.3877 | 122.168 | 122.2504 | 122.1954 | 122.4472 | -0.33417 | -122.6761
2140.3594 | 122.3831 | -122.2046 | 0.13275 | -0.0049592 | 0.015462 | 0.0094143 | 0.013492 | -0.0035313 | -0.0057229 | 0.0075922 | 0.07782 | 0.13275 | -0.19226 | 0.17853 | 0.09613 | 0.1831 | -0.18768 | 0.28381 | 0.21973 | -122.525 | 122.0123 | 0 | 122.2824 | 122.3831 | -0.036621 | -0.32043 | 0.086976 | 0.27008 | 122.0169 | 122.4884 | 122.3007 | 122.3373 | 122.2824 | 122.4243 | 122.3877 | -0.32043 | 122.3373 | 122.2824 | 122.3877 | 122.3007 | 122.4243 | -0.32501 | -122.6578
2142.0625 | 122.4106 | -122.2183 | 0.14648 | -0.012589 | 0.015889 | 0.0085599 | 0.013279 | -0.0058811 | -0.0044413 | 0.006524 | 0.068665 | 0.15106 | -0.16022 | 0.14648 | 0.068665 | 0.14648 | -0.10071 | 0.25635 | 0.21057 | -122.58 | 122.0581 | 0.004578 | 122.287 | 122.3648 | -0.077819 | -0.36163 | 0.064087 | 0.22888 | 122.1176 | 122.4747 | 122.287 | 122.3694 | 122.287 | 122.4289 | 122.3648 | -0.36163 | 122.3694 | 122.287 | 122.3648 | 122.287 | 122.4289 | -0.3067 | -122.7264
2143.8125 | 122.4564 | -122.2046 | 0.11902 | 0.0026703 | 0.016744 | 0.0085599 | 0.019901 | -0.0048129 | -0.0091409 | 0.0084468 | 0.050354 | 0.1831 | -0.22888 | 0.16479 | 0.050354 | 0.11902 | -0.041199 | 0.24719 | 0.24261 | -122.5983 | 121.9757 | 0.064086 | 122.2549 | 122.3694 | -0.068665 | -0.39368 | 0.1236 | 0.27924 | 122.1634 | 122.4518 | 122.2549 | 122.3877 | 122.2549 | 122.4472 | 122.3236 | -0.39368 | 122.3877 | 122.2549 | 122.3236 | 122.2549 | 122.4472 | -0.3479 | -122.7173
2145.5 | 122.5067 | -122.1863 | 0.082397 | 0.0026703 | 0.01888 | 0.011551 | 0.01691 | -0.0024631 | -0.0052957 | 0.007165 | -0.027466 | 0.17853 | -0.21515 | 0.086975 | -0.022888 | 0.036621 | -0.009155 | 0.16022 | 0.23346 | -122.5754 | 121.9711 | 0.096131 | 122.1588 | 122.2733 | -0.10528 | -0.3891 | 0.15106 | 0.18768 | 122.1771 | 122.3465 | 122.1634 | 122.3648 | 122.1588 | 122.4197 | 122.2229 | -0.3891 | 122.3648 | 122.1588 | 122.2229 | 122.1634 | 122.4197 | -0.29755 | -122.6578
2147.2031 | 122.3694 | -122.2549 | 0.13275 | -0.012589 | 0.017385 | 0.013687 | 0.011783 | -0.0043857 | -0.0040139 | 0.0090876 | 0.09613 | 0.15564 | -0.16937 | 0.19684 | 0.09613 | 0.19226 | -0.16937 | 0.29297 | 0.20599 | -122.5891 | 122.0856 | 0.022889 | 122.3511 | 122.4518 | -0.036621 | -0.33417 | 0.073243 | 0.2655 | 122.0856 | 122.5479 | 122.3511 | 122.4106 | 122.3511 | 122.4609 | 122.4472 | -0.33417 | 122.4106 | 122.3511 | 122.4472 | 122.3511 | 122.4609 | -0.30212 | -122.7219
2148.9688 | 122.4564 | -122.1954 | 0.10071 | 0.0026703 | 0.018666 | 0.010483 | 0.017551 | -0.0033175 | -0.0044413 | 0.0069514 | 0.059509 | 0.19684 | -0.21515 | 0.16022 | 0.050354 | 0.11902 | -0.045776 | 0.23346 | 0.22888 | -122.6166 | 121.9803 | 0.09613 | 122.2549 | 122.3557 | -0.050354 | -0.42114 | 0.12817 | 0.27466 | 122.1497 | 122.4289 | 122.2458 | 122.3923 | 122.2549 | 122.4243 | 122.3145 | -0.42114 | 122.3923 | 122.2549 | 122.3145 | 122.2458 | 122.4243 | -0.31586 | -122.7173
2150.7188 | 122.4609 | -122.2366 | 0.10529 | -0.0049592 | 0.017812 | 0.0096279 | 0.017551 | -0.0018223 | -0.0052957 | 0.0067378 | 0.027466 | 0.18768 | -0.2243 | 0.16937 | 0.059509 | 0.1236 | -0.054932 | 0.2243 | 0.24719 | -122.5983 | 122.0123 | 0.082397 | 122.2641 | 122.406 | -0.045777 | -0.36163 | 0.14191 | 0.25177 | 122.1817 | 122.4609 | 122.2961 | 122.4243 | 122.2641 | 122.4838 | 122.3602 | -0.36163 | 122.4243 | 122.2641 | 122.3602 | 122.2961 | 122.4838 | -0.32959 | -122.7036
2152.4219 | 122.4106 | -122.2504 | 0.11902 | 0.0103 | 0.014821 | 0.010055 | 0.013492 | -0.0048129 | -0.0059365 | 0.0095148 | 0.064087 | 0.14648 | -0.1831 | 0.20142 | 0.1236 | 0.1831 | -0.091553 | 0.31586 | 0.21057 | -122.6166 | 122.0673 | 0.027465 | 122.3145 | 122.4518 | 0.004577 | -0.36621 | 0.091552 | 0.24719 | 122.1588 | 122.5662 | 122.374 | 122.3969 | 122.3145 | 122.4609 | 122.4335 | -0.36621 | 122.3969 | 122.3145 | 122.4335 | 122.374 | 122.4609 | -0.30212 | -122.7356
2154.1719 | 122.4747 | -122.2549 | 0.10986 | 0.0026703 | 0.01888 | 0.011551 | 0.017338 | -0.0024631 | -0.0072183 | 0.008874 | 0.050354 | 0.18768 | -0.21973 | 0.15564 | 0.036621 | 0.09613 | -0.027466 | 0.21973 | 0.23804 | -122.5891 | 122.0352 | 0.07782 | 122.3053 | 122.4106 | -0.073242 | -0.33417 | 0.12817 | 0.27008 | 122.2275 | 122.4747 | 122.2916 | 122.4426 | 122.3053 | 122.493 | 122.3511 | -0.33417 | 122.4426 | 122.3053 | 122.3511 | 122.2916 | 122.493 | -0.32959 | -122.699
2155.875 | 122.5159 | -122.2046 | 0.091553 | 0.0103 | 0.015676 | 0.010269 | 0.014988 | -0.0016087 | -0.0072183 | 0.0097284 | -0.013733 | 0.18768 | -0.23346 | 0.091553 | -0.004578 | 0.082397 | -0.022888 | 0.15564 | 0.23346 | -122.6303 | 121.9711 | 0.09613 | 122.1909 | 122.2961 | -0.096131 | -0.42572 | 0.14191 | 0.21973 | 122.1817 | 122.3602 | 122.2 | 122.3923 | 122.1909 | 122.438 | 122.287 | -0.42572 | 122.3923 | 122.1909 | 122.287 | 122.2 | 122.438 | -0.32501 | -122.7219
2157.6406 | 122.4609 | -122.2549 | 0.13733 | -0.0049592 | 0.015462 | 0.010055 | 0.010074 | -0.0043857 | -0.0061503 | 0.0080194 | 0.027466 | 0.17853 | -0.16479 | 0.15564 | 0.073242 | 0.15106 | -0.10071 | 0.27924 | 0.21515 | -122.6212 | 122.0901 | 0.041199 | 122.2824 | 122.4106 | -0.064087 | -0.36621 | 0.07782 | 0.19226 | 122.1542 | 122.5342 | 122.3282 | 122.4335 | 122.2824 | 122.4701 | 122.406 | -0.36621 | 122.4335 | 122.2824 | 122.406 | 122.3282 | 122.4701 | -0.30212 | -122.7585
2159.4062 | 122.525 | -122.2 | 0.10986 | 0.0026703 | 0.018025 | 0.010055 | 0.018406 | -0.0031039 | -0.0050821 | 0.0090876 | -0.004578 | 0.16937 | -0.22888 | 0.10071 | -0.009155 | 0.073242 | -0.041199 | 0.16937 | 0.24719 | -122.5983 | 121.9711 | 0.05951 | 122.1954 | 122.3007 | -0.11902 | -0.39826 | 0.13733 | 0.2243 | 122.1588 | 122.3694 | 122.1909 | 122.3694 | 122.1954 | 122.4472 | 122.2733 | -0.39826 | 122.3694 | 122.1954 | 122.2733 | 122.1909 | 122.4472 | -0.33875 | -122.7081
2161.0938 | 122.4106 | -122.2641 | 0.13275 | 0.0026703 | 0.017171 | 0.013687 | 0.012638 | -0.0026767 | -0.0074319 | 0.0084468 | 0.086975 | 0.15106 | -0.17853 | 0.18768 | 0.091553 | 0.17853 | -0.1831 | 0.27924 | 0.21973 | -122.5983 | 122.0856 | 0.018311 | 122.3511 | 122.4518 | -0.041198 | -0.33417 | 0.086976 | 0.2655 | 122.081 | 122.5433 | 122.3557 | 122.4152 | 122.3511 | 122.4838 | 122.4426 | -0.33417 | 122.4152 | 122.3511 | 122.4426 | 122.3557 | 122.4838 | -0.31128 | -122.731
2162.8438 | 122.5342 | -122.2366 | 0.10529 | 0.0026703 | 0.015889 | 0.012832 | 0.01691 | -0.00096767 | -0.0061503 | 0.0086604 | 0.032043 | 0.19226 | -0.21973 | 0.11444 | 0 | 0.07782 | -0.009155 | 0.17853 | 0.25177 | -122.5891 | 122.0169 | 0.086975 | 122.2687 | 122.3511 | -0.10529 | -0.35248 | 0.14648 | 0.25177 | 122.2275 | 122.4152 | 122.2366 | 122.4289 | 122.2687 | 122.4884 | 122.3145 | -0.35248 | 122.4289 | 122.2687 | 122.3145 | 122.2366 | 122.4884 | -0.32501 | -122.6944
2164.6094 | 122.3923 | -122.2961 | 0.14191 | 0.0026703 | 0.017812 | 0.011337 | 0.010715 | -0.0043857 | -0.0052957 | 0.0067378 | 0.10529 | 0.16022 | -0.16937 | 0.21515 | 0.12817 | 0.21057 | -0.13733 | 0.3479 | 0.19684 | -122.6349 | 122.1268 | 0.01831 | 122.4014 | 122.5113 | -0.013733 | -0.33875 | 0.054931 | 0.27466 | 122.1588 | 122.644 | 122.4243 | 122.4564 | 122.4014 | 122.493 | 122.5067 | -0.33875 | 122.4564 | 122.4014 | 122.5067 | 122.4243 | 122.493 | -0.31128 | -122.7768
2166.3594 | 122.5342 | -122.2275 | 0.091553 | 0.0026703 | 0.015889 | 0.0072781 | 0.015629 | -0.0039585 | -0.0067911 | 0.0078058 | -0.004578 | 0.1831 | -0.21515 | 0.11444 | 0.013733 | 0.07782 | 0.036621 | 0.21057 | 0.25635 | -122.612 | 122.0123 | 0.091552 | 122.2229 | 122.3419 | -0.07782 | -0.38452 | 0.1648 | 0.21057 | 122.2641 | 122.438 | 122.2412 | 122.4106 | 122.2229 | 122.4838 | 122.3053 | -0.38452 | 122.4106 | 122.2229 | 122.3053 | 122.2412 | 122.4838 | -0.3067 | -122.7036
2168.125 | 122.5433 | -122.2458 | 0.10071 | 0.0026703 | 0.016957 | 0.011764 | 0.015415 | -0.0037449 | -0.0048685 | 0.0075922 | -0.013733 | 0.18768 | -0.21515 | 0.091553 | 0 | 0.09613 | -0.054932 | 0.1831 | 0.23346 | -122.6257 | 122.0306 | 0.086975 | 122.2321 | 122.3373 | -0.10071 | -0.37994 | 0.13275 | 0.20142 | 122.1909 | 122.4289 | 122.2458 | 122.4335 | 122.2321 | 122.4792 | 122.3419 | -0.37994 | 122.4335 | 122.2321 | 122.3419 | 122.2458 | 122.4792 | -0.31586 | -122.7264
2169.875 | 122.5204 | -122.2549 | 0.10986 | 0.0026703 | 0.019307 | 0.012405 | 0.016056 | 0.00052773 | -0.0065775 | 0.0075922 | 0.013733 | 0.1831 | -0.20599 | 0.11444 | 0.009155 | 0.10986 | -0.082397 | 0.19226 | 0.22888 | -122.6257 | 122.0489 | 0.073242 | 122.2687 | 122.3694 | -0.10071 | -0.37079 | 0.11902 | 0.21973 | 122.1725 | 122.4472 | 122.2641 | 122.438 | 122.2687 | 122.4838 | 122.3648 | -0.37079 | 122.438 | 122.2687 | 122.3648 | 122.2641 | 122.4838 | -0.31586 | -122.7356
2171.5625 | 122.4243 | -122.2961 | 0.13275 | -0.0049592 | 0.019094 | 0.011123 | 0.010502 | -0.0039585 | -0.0044413 | 0.0073786 | 0.10071 | 0.16479 | -0.17395 | 0.20142 | 0.10986 | 0.18768 | -0.091553 | 0.32959 | 0.21973 | -122.6395 | 122.1222 | 0.032044 | 122.3969 | 122.4976 | -0.022888 | -0.34332 | 0.086976 | 0.27466 | 122.2046 | 122.6257 | 122.406 | 122.4609 | 122.3969 | 122.5159 | 122.4838 | -0.34332 | 122.4609 | 122.3969 | 122.4838 | 122.406 | 122.5159 | -0.3067 | -122.7722
2173.3281 | 122.4518 | -122.2824 | 0.12817 | -0.020218 | 0.015248 | 0.0079189 | 0.0098609 | -0.0045993 | -0.0042277 | 0.0095148 | 0.086975 | 0.16022 | -0.18768 | 0.20599 | 0.10986 | 0.19226 | -0.12817 | 0.32959 | 0.21515 | -122.6074 | 122.0947 | 0.032043 | 122.3694 | 122.4884 | -0.018311 | -0.32501 | 0.086975 | 0.27466 | 122.1542 | 122.612 | 122.3923 | 122.4426 | 122.3694 | 122.4976 | 122.4747 | -0.32501 | 122.4426 | 122.3694 | 122.4747 | 122.3923 | 122.4976 | -0.31586 | -122.7356
2175.0781 | 122.438 | -122.319 | 0.13275 | -0.012589 | 0.018025 | 0.012832 | 0.013492 | -0.0013949 | -0.0057229 | 0.0086604 | 0.10986 | 0.14648 | -0.15564 | 0.21515 | 0.09613 | 0.19226 | -0.18768 | 0.30212 | 0.21973 | -122.612 | 122.1634 | 0.013733 | 122.4289 | 122.5342 | -0.036621 | -0.29297 | 0.086976 | 0.2655 | 122.1313 | 122.6212 | 122.4152 | 122.4655 | 122.4289 | 122.5388 | 122.5113 | -0.29297 | 122.4655 | 122.4289 | 122.5113 | 122.4152 | 122.5388 | -0.28839 | -122.7448
2176.8281 | 122.5708 | -122.2641 | 0.10071 | 0.0103 | 0.01653 | 0.012405 | 0.016056 | -0.0013949 | -0.0055093 | 0.0067378 | -0.009155 | 0.17395 | -0.23346 | 0.11902 | -0.004578 | 0.064087 | 0.036621 | 0.20599 | 0.26093 | -122.6624 | 122.0306 | 0.073242 | 122.2549 | 122.3831 | -0.10529 | -0.39825 | 0.16022 | 0.2243 | 122.3007 | 122.4701 | 122.2595 | 122.438 | 122.2549 | 122.525 | 122.3282 | -0.39825 | 122.438 | 122.2549 | 122.3282 | 122.2595 | 122.525 | -0.33417 | -122.7631
2178.5312 | 122.5342 | -122.2366 | 0.10529 | -0.012589 | 0.018239 | 0.01326 | 0.014347 | -0.0045993 | -0.0044413 | 0.0069514 | 0.013733 | 0.1831 | -0.21515 | 0.10071 | 0.013733 | 0.064087 | 0.027466 | 0.21973 | 0.25635 | -122.6898 | 122.0215 | 0.077819 | 122.2504 | 122.3373 | -0.091553 | -0.45319 | 0.15106 | 0.22888 | 122.2641 | 122.4564 | 122.2504 | 122.4197 | 122.2504 | 122.493 | 122.3007 | -0.45319 | 122.4197 | 122.2504 | 122.3007 | 122.2504 | 122.493 | -0.32044 | -122.7951
2180.2969 | 122.5479 | -122.2687 | 0.09613 | -0.020218 | 0.012471 | 0.0098417 | 0.012638 | -0.0043857 | -0.0048685 | 0.0080194 | 0.018311 | 0.15106 | -0.21973 | 0.11902 | 0.027466 | 0.068665 | 0.018311 | 0.21515 | 0.23346 | -122.6852 | 122.0489 | 0.054932 | 122.287 | 122.3877 | -0.068664 | -0.41657 | 0.13733 | 0.23804 | 122.287 | 122.4838 | 122.2961 | 122.4197 | 122.287 | 122.5021 | 122.3373 | -0.41657 | 122.4197 | 122.287 | 122.3373 | 122.2961 | 122.5021 | -0.31586 | -122.7814
2182 | 122.4518 | -122.2961 | 0.11902 | 0.0103 | 0.017598 | 0.011123 | 0.011783 | -0.0054539 | -0.0029459 | 0.0090876 | 0.068665 | 0.14648 | -0.17853 | 0.20142 | 0.10529 | 0.17853 | -0.11444 | 0.32044 | 0.20142 | -122.644 | 122.1176 | 0.027465 | 122.3648 | 122.4976 | -0.013733 | -0.3479 | 0.082397 | 0.24719 | 122.1817 | 122.6166 | 122.4014 | 122.4426 | 122.3648 | 122.4976 | 122.4747 | -0.3479 | 122.4426 | 122.3648 | 122.4747 | 122.4014 | 122.4976 | -0.29755 | -122.7631
2183.7656 | 122.4792 | -122.2961 | 0.1236 | -0.0049592 | 0.016103 | 0.011551 | 0.015201 | -0.0050265 | -0.0070047 | 0.0084468 | 0.073242 | 0.13733 | -0.18768 | 0.19226 | 0.086975 | 0.14648 | -0.054932 | 0.28839 | 0.21057 | -122.6486 | 122.1085 | 0.013733 | 122.3694 | 122.4884 | -0.036621 | -0.35248 | 0.086975 | 0.26092 | 122.2412 | 122.5845 | 122.3831 | 122.4335 | 122.3694 | 122.5067 | 122.4426 | -0.35248 | 122.4335 | 122.3694 | 122.4426 | 122.3831 | 122.5067 | -0.31128 | -122.7722
2185.5312 | 122.4472 | -122.3282 | 0.13733 | -0.0049592 | 0.015248 | 0.010055 | 0.013492 | -0.0050265 | -0.0046549 | 0.0080194 | 0.10529 | 0.14191 | -0.18768 | 0.24261 | 0.11444 | 0.18768 | -0.13275 | 0.3479 | 0.19684 | -122.6257 | 122.1405 | 0.004578 | 122.4335 | 122.5708 | -0.022888 | -0.29755 | 0.059509 | 0.29297 | 122.1954 | 122.6761 | 122.4426 | 122.4701 | 122.4335 | 122.525 | 122.5159 | -0.29755 | 122.4701 | 122.4335 | 122.5159 | 122.4426 | 122.525 | -0.32501 | -122.7631
2187.2812 | 122.5159 | -122.3236 | 0.11902 | -0.012589 | 0.017385 | 0.010483 | 0.011783 | -0.0043857 | -0.0065775 | 0.0069514 | 0.050354 | 0.16479 | -0.19684 | 0.15564 | 0.064087 | 0.13275 | -0.091553 | 0.24261 | 0.21057 | -122.6761 | 122.1268 | 0.045776 | 122.374 | 122.4792 | -0.054932 | -0.35248 | 0.091552 | 0.24719 | 122.2321 | 122.5662 | 122.3877 | 122.4884 | 122.374 | 122.5342 | 122.4564 | -0.35248 | 122.4884 | 122.374 | 122.4564 | 122.3877 | 122.5342 | -0.31586 | -122.7951
2189.0469 | 122.5204 | -122.3099 | 0.10986 | -0.0049592 | 0.017812 | 0.0098417 | 0.012211 | -0.0022495 | -0.0061503 | 0.008233 | 0.050354 | 0.16022 | -0.20142 | 0.16479 | 0.050354 | 0.13275 | -0.10529 | 0.26093 | 0.21515 | -122.6852 | 122.1085 | 0.050354 | 122.3602 | 122.4747 | -0.059509 | -0.37537 | 0.10529 | 0.25177 | 122.2046 | 122.5708 | 122.3602 | 122.4701 | 122.3602 | 122.525 | 122.4426 | -0.37537 | 122.4701 | 122.3602 | 122.4426 | 122.3602 | 122.525 | -0.31128 | -122.7951
2190.8125 | 122.4564 | -122.3145 | 0.13733 | -0.012589 | 0.015462 | 0.0092007 | 0.013706 | -0.0045993 | -0.0074319 | 0.008233 | 0.10529 | 0.15106 | -0.17395 | 0.23346 | 0.10986 | 0.19684 | -0.14648 | 0.36163 | 0.20599 | -122.6257 | 122.1405 | 0.013733 | 122.4197 | 122.5479 | -0.027466 | -0.31128 | 0.068665 | 0.27924 | 122.168 | 122.6761 | 122.4243 | 122.4655 | 122.4197 | 122.5204 | 122.5113 | -0.31128 | 122.4655 | 122.4197 | 122.5113 | 122.4243 | 122.5204 | -0.31128 | -122.7631
2192.5312 | 122.5433 | -122.3099 | 0.10529 | 0.0026703 | 0.017598 | 0.011123 | 0.015629 | -0.0041721 | -0.0070047 | 0.0069514 | 0.045776 | 0.16937 | -0.18768 | 0.15564 | 0.027466 | 0.091553 | -0.009155 | 0.24261 | 0.21973 | -122.7036 | 122.1222 | 0.064087 | 122.3557 | 122.4655 | -0.07782 | -0.39368 | 0.11444 | 0.23346 | 122.3007 | 122.5525 | 122.3373 | 122.4792 | 122.3557 | 122.5296 | 122.4014 | -0.39368 | 122.4792 | 122.3557 | 122.4014 | 122.3373 | 122.5296 | -0.29297 | -122.8088
2194.2969 | 122.4884 | -122.319 | 0.11444 | -0.0049592 | 0.019094 | 0.0077053 | 0.011783 | -0.0048129 | -0.0040139 | 0.007165 | 0.068665 | 0.16022 | -0.17395 | 0.20142 | 0.11444 | 0.17853 | -0.1236 | 0.32959 | 0.21057 | -122.6761 | 122.1451 | 0.045776 | 122.3877 | 122.5204 | 0 | -0.35706 | 0.09613 | 0.24261 | 122.1954 | 122.6486 | 122.4335 | 122.4792 | 122.3877 | 122.5296 | 122.4976 | -0.35706 | 122.4792 | 122.3877 | 122.4976 | 122.4335 | 122.5296 | -0.28839 | -122.7905
2196.0625 | 122.5433 | -122.3328 | 0.091553 | -0.0049592 | 0.017385 | 0.0089871 | 0.018833 | -0.0024631 | -0.0061503 | 0.0090876 | 0.082397 | 0.17395 | -0.21973 | 0.1831 | 0.054932 | 0.10071 | -0.045776 | 0.23346 | 0.21515 | -122.6578 | 122.113 | 0.082397 | 122.4152 | 122.5159 | -0.036621 | -0.32501 | 0.1236 | 0.30212 | 122.287 | 122.5662 | 122.3877 | 122.5067 | 122.4152 | 122.5479 | 122.4335 | -0.32501 | 122.5067 | 122.4152 | 122.4335 | 122.3877 | 122.5479 | -0.31128 | -122.7493
2197.75 | 122.5571 | -122.3328 | 0.10071 | -0.012589 | 0.019094 | 0.0089871 | 0.017338 | -0.0020359 | -0.0059365 | 0.008233 | 0.027466 | 0.1831 | -0.19684 | 0.16022 | 0.054932 | 0.13733 | -0.13275 | 0.24261 | 0.20599 | -122.6624 | 122.1359 | 0.082397 | 122.3602 | 122.493 | -0.045776 | -0.32959 | 0.10529 | 0.2243 | 122.2 | 122.5754 | 122.3877 | 122.5159 | 122.3602 | 122.5388 | 122.4701 | -0.32959 | 122.5159 | 122.3602 | 122.4701 | 122.3877 | 122.5388 | -0.29755 | -122.7631
2199.5 | 122.5479 | -122.3465 | 0.1236 | 0.0103 | 0.015035 | 0.0068509 | 0.015842 | -0.00054047 | -0.0057229 | 0.0097284 | 0.045776 | 0.16479 | -0.19684 | 0.17853 | 0.07782 | 0.16022 | -0.15564 | 0.2655 | 0.19226 | -122.6395 | 122.1497 | 0.041199 | 122.3923 | 122.525 | -0.045776 | -0.29297 | 0.068665 | 0.24261 | 122.1909 | 122.612 | 122.4243 | 122.5113 | 122.3923 | 122.5388 | 122.5067 | -0.29297 | 122.5113 | 122.3923 | 122.5067 | 122.4243 | 122.5388 | -0.32043 | -122.7631
2201.25 | 122.612 | -122.3053 | 0.09613 | 0.0026703 | 0.021871 | 0.011551 | 0.014133 | -0.0031039 | -0.0057229 | 0.0073786 | 0.009155 | 0.20599 | -0.21057 | 0.11444 | 0.013733 | 0.068665 | 0.032043 | 0.19684 | 0.24261 | -122.7356 | 122.0947 | 0.10986 | 122.3145 | 122.4197 | -0.082397 | -0.4303 | 0.14649 | 0.21973 | 122.3373 | 122.5021 | 122.319 | 122.5113 | 122.3145 | 122.5479 | 122.374 | -0.4303 | 122.5113 | 122.3145 | 122.374 | 122.319 | 122.5479 | -0.3067 | -122.8317
2202.9531 | 122.493 | -122.3465 | 0.1236 | -0.0049592 | 0.018666 | 0.01091 | 0.013492 | -0.0026767 | -0.0063639 | 0.0086604 | 0.09613 | 0.16022 | -0.1831 | 0.21515 | 0.11902 | 0.19226 | -0.12817 | 0.32959 | 0.21057 | -122.6715 | 122.1634 | 0.036621 | 122.4426 | 122.5616 | -0.004577 | -0.32501 | 0.086975 | 0.27924 | 122.2183 | 122.6761 | 122.4655 | 122.5067 | 122.4426 | 122.5571 | 122.5388 | -0.32501 | 122.5067 | 122.4426 | 122.5388 | 122.4655 | 122.5571 | -0.3067 | -122.7951
2204.7031 | 122.5021 | -122.3557 | 0.12817 | -0.0049592 | 0.014608 | 0.011123 | 0.011356 | -0.0041721 | -0.0038003 | 0.0063104 | 0.068665 | 0.16479 | -0.19226 | 0.20142 | 0.10529 | 0.19226 | -0.13275 | 0.32044 | 0.21057 | -122.6761 | 122.1634 | 0.036621 | 122.4243 | 122.5571 | -0.022888 | -0.32043 | 0.082397 | 0.26093 | 122.2229 | 122.6761 | 122.4609 | 122.5204 | 122.4243 | 122.5662 | 122.5479 | -0.32043 | 122.5204 | 122.4243 | 122.5479 | 122.4609 | 122.5662 | -0.32044 | -122.8043
2206.4531 | 122.5388 | -122.3419 | 0.10986 | 0.0026703 | 0.01119 | 0.0085599 | 0.011997 | -0.0052401 | -0.0048685 | 0.0069514 | 0.032043 | 0.15106 | -0.19226 | 0.16022 | 0.064087 | 0.14191 | -0.10071 | 0.27924 | 0.21973 | -122.6349 | 122.1497 | 0.041199 | 122.374 | 122.5021 | -0.045776 | -0.29297 | 0.10986 | 0.2243 | 122.2412 | 122.6212 | 122.406 | 122.493 | 122.374 | 122.5616 | 122.4838 | -0.29297 | 122.493 | 122.374 | 122.4838 | 122.406 | 122.5616 | -0.30212 | -122.7448
2208.2031 | 122.5525 | -122.3602 | 0.10529 | -0.0049592 | 0.016317 | 0.013473 | 0.011997 | -0.0050265 | -0.0048685 | 0.0086604 | 0.036621 | 0.16022 | -0.19684 | 0.16937 | 0.068665 | 0.14191 | -0.091553 | 0.25177 | 0.20599 | -122.6944 | 122.1634 | 0.054931 | 122.3969 | 122.5296 | -0.036621 | -0.33417 | 0.10071 | 0.23346 | 122.2687 | 122.612 | 122.4289 | 122.5204 | 122.3969 | 122.5662 | 122.5021 | -0.33417 | 122.5204 | 122.3969 | 122.5021 | 122.4289 | 122.5662 | -0.30212 | -122.7997
2209.9531 | 122.5479 | -122.3511 | 0.1236 | 0.0026703 | 0.016744 | 0.0085599 | 0.013706 | -0.0041721 | -0.0042277 | 0.0060968 | 0.045776 | 0.14191 | -0.16937 | 0.16479 | 0.054932 | 0.13733 | -0.10071 | 0.26093 | 0.21515 | -122.7493 | 122.1817 | 0.018311 | 122.3969 | 122.5159 | -0.068664 | -0.39826 | 0.091553 | 0.21515 | 122.2504 | 122.612 | 122.406 | 122.493 | 122.3969 | 122.5662 | 122.4884 | -0.39826 | 122.493 | 122.3969 | 122.4884 | 122.406 | 122.5662 | -0.29297 | -122.8729
2211.6562 | 122.6257 | -122.3145 | 0.10071 | -0.0049592 | 0.01653 | 0.0098417 | 0.016056 | -0.0043857 | -0.0072183 | 0.0073786 | -0.018311 | 0.18768 | -0.23804 | 0.10986 | -0.009155 | 0.041199 | 0.041199 | 0.21515 | 0.25177 | -122.6944 | 122.0764 | 0.086975 | 122.2961 | 122.4243 | -0.10986 | -0.37994 | 0.15106 | 0.21973 | 122.3557 | 122.5296 | 122.3053 | 122.5021 | 122.2961 | 122.5662 | 122.3557 | -0.37994 | 122.5021 | 122.2961 | 122.3557 | 122.3053 | 122.5662 | -0.33875 | -122.7951
2213.4219 | 122.5891 | -122.3511 | 0.10529 | 0.0026703 | 0.01653 | 0.011978 | 0.020328 | -0.0033175 | -0.0085001 | 0.008233 | 0.082397 | 0.17853 | -0.21515 | 0.16479 | 0.054932 | 0.11902 | -0.041199 | 0.25635 | 0.25177 | -122.6852 | 122.1359 | 0.073242 | 122.4335 | 122.5159 | -0.050354 | -0.33417 | 0.14648 | 0.29755 | 122.3099 | 122.6074 | 122.406 | 122.5296 | 122.4335 | 122.6028 | 122.4701 | -0.33417 | 122.5296 | 122.4335 | 122.4701 | 122.406 | 122.6028 | -0.32044 | -122.7905
2215.1875 | 122.5204 | -122.374 | 0.11902 | 0.0026703 | 0.015676 | 0.010055 | 0.011143 | -0.0035313 | -0.0050821 | 0.0073786 | 0.091553 | 0.14648 | -0.1831 | 0.20599 | 0.12817 | 0.17395 | -0.13275 | 0.33417 | 0.19684 | -122.6715 | 122.1909 | 0.027465 | 122.4655 | 122.58 | 0.009155 | -0.29755 | 0.077819 | 0.27466 | 122.2412 | 122.7081 | 122.5021 | 122.5204 | 122.4655 | 122.5708 | 122.5479 | -0.29755 | 122.5204 | 122.4655 | 122.5479 | 122.5021 | 122.5708 | -0.30212 | -122.7905
2216.9531 | 122.58 | -122.374 | 0.1236 | -0.0049592 | 0.015248 | 0.0092007 | 0.011997 | -0.0050265 | -0.0031595 | 0.0084468 | 0.041199 | 0.16479 | -0.19226 | 0.16479 | 0.064087 | 0.13733 | -0.10986 | 0.26093 | 0.20142 | -122.731 | 122.1817 | 0.041199 | 122.4152 | 122.5388 | -0.059509 | -0.35706 | 0.07782 | 0.23346 | 122.2641 | 122.6349 | 122.438 | 122.5388 | 122.4152 | 122.5754 | 122.5113 | -0.35706 | 122.5388 | 122.4152 | 122.5113 | 122.438 | 122.5754 | -0.31586 | -122.8546
2218.6562 | 122.6212 | -122.3465 | 0.10986 | -0.0049592 | 0.018666 | 0.0096279 | 0.017124 | -0.0028903 | -0.0067911 | 0.0084468 | 0.009155 | 0.17395 | -0.23804 | 0.14191 | 0.022888 | 0.068665 | 0.032043 | 0.2243 | 0.23804 | -122.7081 | 122.1085 | 0.064087 | 122.3557 | 122.4884 | -0.086975 | -0.36163 | 0.12817 | 0.24719 | 122.3785 | 122.5708 | 122.3694 | 122.5204 | 122.3557 | 122.5845 | 122.4152 | -0.36163 | 122.5204 | 122.3557 | 122.4152 | 122.3694 | 122.5845 | -0.3479 | -122.818
2220.4219 | 122.644 | -122.3831 | 0.09613 | 0.0103 | 0.021016 | 0.010055 | 0.017551 | -0.00075407 | -0.0074319 | 0.0090876 | 0.041199 | 0.20599 | -0.21057 | 0.1236 | 0.013733 | 0.054932 | -0.004578 | 0.17853 | 0.24261 | -122.7219 | 122.1725 | 0.10986 | 122.4243 | 122.5067 | -0.082397 | -0.33875 | 0.14649 | 0.25177 | 122.3785 | 122.5616 | 122.3969 | 122.5891 | 122.4243 | 122.6257 | 122.438 | -0.33875 | 122.5891 | 122.4243 | 122.438 | 122.3969 | 122.6257 | -0.3067 | -122.818
2222.1719 | 122.6761 | -122.3648 | 0.09613 | 0.0103 | 0.015889 | 0.011551 | 0.017978 | -0.0024631 | -0.0078591 | 0.0093012 | -0.022888 | 0.18768 | -0.2243 | 0.073242 | -0.018311 | 0.054932 | 0.004578 | 0.15564 | 0.24719 | -122.7127 | 122.1405 | 0.091553 | 122.3419 | 122.438 | -0.11444 | -0.3479 | 0.15106 | 0.20142 | 122.3694 | 122.5204 | 122.3465 | 122.5525 | 122.3419 | 122.612 | 122.4197 | -0.3479 | 122.5525 | 122.3419 | 122.4197 | 122.3465 | 122.612 | -0.32043 | -122.8088
2223.9219 | 122.5067 | -122.4152 | 0.11902 | 0.0026703 | 0.015035 | 0.010696 | 0.0090063 | -0.0037449 | -0.0065775 | 0.0090876 | 0.082397 | 0.16022 | -0.1831 | 0.20599 | 0.12817 | 0.21515 | -0.13275 | 0.35706 | 0.20599 | -122.6807 | 122.2321 | 0.041198 | 122.4976 | 122.6212 | 0.009155 | -0.2655 | 0.086975 | 0.2655 | 122.2824 | 122.7722 | 122.5433 | 122.5754 | 122.4976 | 122.6212 | 122.6303 | -0.2655 | 122.5754 | 122.4976 | 122.6303 | 122.5433 | 122.6212 | -0.30212 | -122.7997
2225.6875 | 122.6212 | -122.3511 | 0.1236 | -0.012589 | 0.018453 | 0.0079189 | 0.015629 | 0.00010033 | -0.0082865 | 0.0078058 | 0.059509 | 0.1831 | -0.21515 | 0.15106 | 0.050354 | 0.10071 | -0.036621 | 0.25177 | 0.21973 | -122.7127 | 122.1359 | 0.059509 | 122.4106 | 122.5021 | -0.073242 | -0.36163 | 0.096131 | 0.27466 | 122.3145 | 122.6028 | 122.4014 | 122.5342 | 122.4106 | 122.5708 | 122.4518 | -0.36163 | 122.5342 | 122.4106 | 122.4518 | 122.4014 | 122.5708 | -0.33875 | -122.8363
2227.375 | 122.5342 | -122.4243 | 0.11902 | -0.0049592 | 0.015676 | 0.0092007 | 0.013492 | -0.00096767 | -0.0046549 | 0.011224 | 0.09613 | 0.13275 | -0.16937 | 0.20142 | 0.11444 | 0.18768 | -0.19226 | 0.31128 | 0.18768 | -122.7127 | 122.2549 | 0.013732 | 122.5204 | 122.6257 | -0.004578 | -0.28839 | 0.068664 | 0.2655 | 122.2321 | 122.7356 | 122.5388 | 122.5571 | 122.5204 | 122.612 | 122.612 | -0.28839 | 122.5571 | 122.5204 | 122.612 | 122.5388 | 122.612 | -0.28839 | -122.8317
2229.1562 | 122.5388 | -122.4197 | 0.13275 | -0.0049592 | 0.017812 | 0.011123 | 0.016056 | -0.0033175 | -0.0059365 | 0.0086604 | 0.10071 | 0.14191 | -0.16937 | 0.21057 | 0.1236 | 0.19684 | -0.21973 | 0.3067 | 0.20142 | -122.6852 | 122.2504 | 0.009156 | 122.5204 | 122.6303 | -0.009155 | -0.2655 | 0.068665 | 0.27008 | 122.2 | 122.7264 | 122.5433 | 122.5616 | 122.5204 | 122.6212 | 122.6166 | -0.2655 | 122.5616 | 122.5204 | 122.6166 | 122.5433 | 122.6212 | -0.30212 | -122.818
2230.9219 | 122.58 | -122.406 | 0.11902 | -0.0049592 | 0.014821 | 0.013046 | 0.016697 | -0.00096767 | -0.0063639 | 0.0093012 | 0.050354 | 0.16022 | -0.19226 | 0.16937 | 0.091553 | 0.17853 | -0.16937 | 0.27466 | 0.19226 | -122.6807 | 122.2137 | 0.041198 | 122.4564 | 122.5754 | -0.027466 | -0.27466 | 0.073242 | 0.24261 | 122.2366 | 122.6807 | 122.4976 | 122.5662 | 122.4564 | 122.5983 | 122.5845 | -0.27466 | 122.5662 | 122.4564 | 122.5845 | 122.4976 | 122.5983 | -0.31128 | -122.7997
2232.625 | 122.6028 | -122.406 | 0.1236 | 0.0103 | 0.017385 | 0.012405 | 0.015201 | -0.0013949 | -0.0072183 | 0.0080194 | 0.064087 | 0.16937 | -0.19226 | 0.16937 | 0.073242 | 0.16479 | -0.16022 | 0.2655 | 0.21515 | -122.6944 | 122.2137 | 0.045777 | 122.4701 | 122.5754 | -0.050354 | -0.28839 | 0.091553 | 0.25635 | 122.2458 | 122.6715 | 122.4792 | 122.5754 | 122.4701 | 122.6212 | 122.5708 | -0.28839 | 122.5754 | 122.4701 | 122.5708 | 122.4792 | 122.6212 | -0.31586 | -122.818
2234.3906 | 122.6761 | -122.3923 | 0.09613 | -0.0049592 | 0.018025 | 0.011337 | 0.014133 | -0.0031039 | -0.0067911 | 0.007165 | -0.004578 | 0.16937 | -0.22888 | 0.10529 | 0 | 0.064087 | 0.027466 | 0.20599 | 0.26093 | -122.7814 | 122.1634 | 0.073243 | 122.3877 | 122.4976 | -0.09613 | -0.3891 | 0.1648 | 0.2243 | 122.4197 | 122.5983 | 122.3923 | 122.5616 | 122.3877 | 122.6532 | 122.4564 | -0.3891 | 122.5616 | 122.3877 | 122.4564 | 122.3923 | 122.6532 | -0.32501 | -122.8775
2236.0938 | 122.58 | -122.4197 | 0.10986 | -0.0049592 | 0.017812 | 0.012832 | 0.015629 | -0.0018223 | -0.0046549 | 0.009942 | 0.073242 | 0.14648 | -0.19684 | 0.19226 | 0.09613 | 0.18768 | -0.16022 | 0.29297 | 0.20142 | -122.7219 | 122.2229 | 0.036621 | 122.493 | 122.612 | -0.013733 | -0.30212 | 0.091553 | 0.27008 | 122.2595 | 122.7127 | 122.5159 | 122.5662 | 122.493 | 122.6212 | 122.6074 | -0.30212 | 122.5662 | 122.493 | 122.6074 | 122.5159 | 122.6212 | -0.3067 | -122.8317
2237.8438 | 122.6807 | -122.3694 | 0.10529 | 0.0026703 | 0.017385 | 0.011764 | 0.017551 | -0.0028903 | -0.0074319 | 0.0090876 | 0.009155 | 0.17853 | -0.21515 | 0.10071 | -0.013733 | 0.027466 | 0 | 0.16937 | 0.24719 | -122.7402 | 122.1542 | 0.073242 | 122.3785 | 122.4701 | -0.11902 | -0.37079 | 0.14191 | 0.2243 | 122.3694 | 122.5388 | 122.3557 | 122.5479 | 122.3785 | 122.6166 | 122.3969 | -0.37079 | 122.5479 | 122.3785 | 122.3969 | 122.3557 | 122.6166 | -0.32044 | -122.8455
2239.5625 | 122.5571 | -122.4243 | 0.13275 | -0.0049592 | 0.017385 | 0.011978 | 0.014774 | -0.00054047 | -0.0052957 | 0.0084468 | 0.10529 | 0.14648 | -0.16479 | 0.20142 | 0.10986 | 0.15564 | -0.18768 | 0.29755 | 0.19226 | -122.7219 | 122.2595 | 0.013733 | 122.5296 | 122.6257 | -0.022888 | -0.29755 | 0.05951 | 0.27008 | 122.2366 | 122.7219 | 122.5342 | 122.5708 | 122.5296 | 122.6166 | 122.58 | -0.29755 | 122.5708 | 122.5296 | 122.58 | 122.5342 | 122.6166 | -0.29755 | -122.8546
2241.3125 | 122.6303 | -122.3831 | 0.10529 | 0.017929 | 0.015462 | 0.014541 | 0.014988 | -0.0011813 | -0.0065775 | 0.0093012 | 0.059509 | 0.17395 | -0.21057 | 0.15564 | 0.045776 | 0.10529 | -0.050354 | 0.24719 | 0.2243 | -122.7402 | 122.1725 | 0.068664 | 122.4426 | 122.5388 | -0.05951 | -0.35706 | 0.11902 | 0.27008 | 122.3328 | 122.6303 | 122.4289 | 122.5571 | 122.4426 | 122.6074 | 122.4884 | -0.35706 | 122.5571 | 122.4426 | 122.4884 | 122.4289 | 122.6074 | -0.31586 | -122.8455
2243.0625 | 122.6761 | -122.3557 | 0.091553 | -0.0049592 | 0.019948 | 0.010269 | 0.014133 | -0.0018223 | -0.0078591 | 0.0078058 | 0.013733 | 0.20142 | -0.21515 | 0.10071 | 0.018311 | 0.086975 | 0.027466 | 0.21057 | 0.24261 | -122.7722 | 122.1405 | 0.10986 | 122.3694 | 122.4564 | -0.073242 | -0.41656 | 0.15106 | 0.22888 | 122.3831 | 122.5662 | 122.374 | 122.5571 | 122.3694 | 122.5983 | 122.4426 | -0.41656 | 122.5571 | 122.3694 | 122.4426 | 122.374 | 122.5983 | -0.3067 | -122.8638
2244.8281 | 122.6807 | -122.3969 | 0.10529 | -0.0049592 | 0.019521 | 0.0096279 | 0.014774 | -0.00075407 | -0.0067911 | 0.012078 | 0.004578 | 0.19226 | -0.21515 | 0.073242 | -0.022888 | 0.050354 | 0.004578 | 0.15564 | 0.23804 | -122.7814 | 122.1817 | 0.086975 | 122.4014 | 122.4701 | -0.12817 | -0.38452 | 0.13275 | 0.21973 | 122.4014 | 122.5525 | 122.374 | 122.5891 | 122.4014 | 122.6349 | 122.4472 | -0.38452 | 122.5891 | 122.4014 | 122.4472 | 122.374 | 122.6349 | -0.32044 | -122.8867
2246.5312 | 122.5479 | -122.4289 | 0.12817 | 0.0026703 | 0.014608 | 0.010055 | 0.0090063 | -0.0028903 | -0.0048685 | 0.0086604 | 0.10529 | 0.1236 | -0.18768 | 0.21057 | 0.13275 | 0.20599 | -0.1236 | 0.35248 | 0.21515 | -122.7402 | 122.2412 | -0.004578 | 122.5342 | 122.6395 | 0.004577 | -0.31128 | 0.086975 | 0.29297 | 122.3053 | 122.7814 | 122.5616 | 122.5525 | 122.5342 | 122.644 | 122.6349 | -0.31128 | 122.5525 | 122.5342 | 122.6349 | 122.5616 | 122.644 | -0.31586 | -122.8683
2248.2969 | 122.612 | -122.3831 | 0.11902 | 0.0026703 | 0.016317 | 0.010269 | 0.012638 | -0.0022495 | -0.0033731 | 0.0090876 | 0.068665 | 0.1831 | -0.19226 | 0.14191 | 0.064087 | 0.15564 | -0.10071 | 0.26093 | 0.21515 | -122.7539 | 122.1909 | 0.064086 | 122.4518 | 122.525 | -0.054932 | -0.37079 | 0.09613 | 0.26093 | 122.2824 | 122.644 | 122.4472 | 122.5662 | 122.4518 | 122.5983 | 122.5388 | -0.37079 | 122.5662 | 122.4518 | 122.5388 | 122.4472 | 122.5983 | -0.31128 | -122.8729
2250 | 122.5616 | -122.438 | 0.13733 | -0.0049592 | 0.017812 | 0.010483 | 0.014774 | -0.00054047 | -0.0065775 | 0.0084468 | 0.10529 | 0.13733 | -0.17395 | 0.21515 | 0.10529 | 0.19226 | -0.19226 | 0.3067 | 0.19684 | -122.7448 | 122.2641 | 0 | 122.5433 | 122.6532 | -0.032043 | -0.3067 | 0.059509 | 0.27924 | 122.2458 | 122.7448 | 122.5433 | 122.5754 | 122.5433 | 122.6349 | 122.6303 | -0.3067 | 122.5754 | 122.5433 | 122.6303 | 122.5433 | 122.6349 | -0.31128 | -122.8821
2251.7656 | 122.699 | -122.4014 | 0.10071 | -0.0049592 | 0.02123 | 0.011551 | 0.019901 | -0.0020359 | -0.0059365 | 0.010156 | 0.013733 | 0.16479 | -0.21973 | 0.10986 | -0.013733 | 0.073242 | -0.045776 | 0.17853 | 0.23346 | -122.7951 | 122.1817 | 0.064087 | 122.4152 | 122.5113 | -0.11444 | -0.39368 | 0.13275 | 0.23346 | 122.3557 | 122.58 | 122.3877 | 122.5662 | 122.4152 | 122.6349 | 122.4747 | -0.39368 | 122.5662 | 122.4152 | 122.4747 | 122.3877 | 122.6349 | -0.32044 | -122.8958
2253.5312 | 122.6852 | -122.406 | 0.091553 | -0.0049592 | 0.017171 | 0.016464 | 0.018833 | -0.0022495 | -0.0082865 | 0.0093012 | 0.041199 | 0.16937 | -0.20599 | 0.10071 | 0 | 0.073242 | -0.027466 | 0.17395 | 0.24261 | -122.7951 | 122.2 | 0.07782 | 122.4472 | 122.5067 | -0.091553 | -0.3891 | 0.15106 | 0.24719 | 122.3785 | 122.58 | 122.406 | 122.5754 | 122.4472 | 122.6486 | 122.4792 | -0.3891 | 122.5754 | 122.4472 | 122.4792 | 122.406 | 122.6486 | -0.29755 | -122.8867
2255.2812 | 122.5845 | -122.287 | 0.07782 | 0.0026703 | 0.018666 | 0.0098417 | 0.012424 | -0.0024631 | -0.0065775 | 0.009942 | -0.004578 | 0.20142 | -0.22888 | 0.082397 | 0.009155 | 0.064087 | 0.064087 | 0.19684 | 0.23804 | -122.7036 | 122.0581 | 0.1236 | 122.2824 | 122.3694 | -0.068665 | -0.41657 | 0.16022 | 0.2243 | 122.3511 | 122.4838 | 122.2961 | 122.4884 | 122.2824 | 122.525 | 122.3511 | -0.41657 | 122.4884 | 122.2824 | 122.3511 | 122.2961 | 122.525 | -0.3067 | -122.7814
2257.0312 | 122.4335 | -122.0901 | 0.091553 | -0.0049592 | 0.018025 | 0.0072781 | 0.01456 | 0.00010033 | -0.0078591 | 0.0084468 | 0.013733 | 0.16937 | -0.24719 | 0.07782 | -0.032043 | 0.054932 | 0.009155 | 0.15564 | 0.24261 | -122.5021 | 121.843 | 0.07782 | 122.1039 | 122.168 | -0.1236 | -0.41199 | 0.15106 | 0.26093 | 122.0993 | 122.2458 | 122.0581 | 122.2595 | 122.1039 | 122.3328 | 122.1451 | -0.41199 | 122.2595 | 122.1039 | 122.1451 | 122.0581 | 122.3328 | -0.33874 | -122.5937
2258.7188 | 122.3694 | -122.2229 | 0.12817 | 0.0026703 | 0.015889 | 0.011123 | 0.013279 | -0.0022495 | -0.0029459 | 0.01101 | 0.09613 | 0.15106 | -0.15564 | 0.21057 | 0.11444 | 0.21057 | -0.1831 | 0.32044 | 0.18768 | -122.525 | 122.0673 | 0.022888 | 122.319 | 122.4335 | -0.013733 | -0.30212 | 0.059509 | 0.25177 | 122.0398 | 122.5433 | 122.3373 | 122.374 | 122.319 | 122.4106 | 122.4335 | -0.30212 | 122.374 | 122.319 | 122.4335 | 122.3373 | 122.4106 | -0.28381 | -122.6532
2260.4688 | 122.4976 | -122.2 | 0.082397 | -0.0049592 | 0.020162 | 0.013046 | 0.017338 | -0.0018223 | -0.0057229 | 0.0093012 | 0.036621 | 0.19226 | -0.21973 | 0.10071 | -0.009155 | 0.068665 | -0.022888 | 0.18768 | 0.23804 | -122.5937 | 121.9803 | 0.10986 | 122.2366 | 122.3007 | -0.091552 | -0.39368 | 0.15564 | 0.25635 | 122.1771 | 122.3877 | 122.1909 | 122.3923 | 122.2366 | 122.438 | 122.2687 | -0.39368 | 122.3923 | 122.2366 | 122.2687 | 122.1909 | 122.438 | -0.30212 | -122.6761
2262.2188 | 122.5388 | -122.2137 | 0.091553 | -0.0049592 | 0.017812 | 0.012192 | 0.016483 | -0.0031039 | -0.0042277 | 0.0097284 | -0.027466 | 0.1831 | -0.21057 | 0.10071 | -0.009155 | 0.082397 | -0.041199 | 0.16937 | 0.23804 | -122.612 | 122.0032 | 0.091552 | 122.1863 | 122.3145 | -0.10071 | -0.39825 | 0.14648 | 0.18311 | 122.1725 | 122.3831 | 122.2046 | 122.3969 | 122.1863 | 122.4518 | 122.2961 | -0.39825 | 122.3969 | 122.1863 | 122.2961 | 122.2046 | 122.4518 | -0.30212 | -122.7036
2263.9844 | 122.5113 | -122.2641 | 0.09613 | -0.0049592 | 0.017598 | 0.013046 | 0.011783 | -0.0024631 | -0.0048685 | 0.011437 | 0.022888 | 0.16937 | -0.18768 | 0.12817 | 0.027466 | 0.07782 | 0.022888 | 0.22888 | 0.24719 | -122.6669 | 122.0764 | 0.073243 | 122.287 | 122.3923 | -0.068664 | -0.40283 | 0.15106 | 0.21057 | 122.287 | 122.493 | 122.2916 | 122.4335 | 122.287 | 122.5113 | 122.3419 | -0.40283 | 122.4335 | 122.287 | 122.3419 | 122.2916 | 122.5113 | -0.28381 | -122.7631
2265.6719 | 122.5113 | -122.2549 | 0.10986 | -0.012589 | 0.016103 | 0.012405 | 0.018192 | -0.0026767 | -0.0046549 | 0.01101 | 0.059509 | 0.17853 | -0.20599 | 0.14648 | 0.041199 | 0.09613 | -0.045776 | 0.23804 | 0.23804 | -122.5983 | 122.0489 | 0.068665 | 122.3145 | 122.4014 | -0.068664 | -0.34332 | 0.12817 | 0.2655 | 122.2092 | 122.493 | 122.2961 | 122.4335 | 122.3145 | 122.493 | 122.3511 | -0.34332 | 122.4335 | 122.3145 | 122.3511 | 122.2961 | 122.493 | -0.31586 | -122.7081
2267.4219 | 122.5479 | -122.3007 | 0.10986 | 0.0026703 | 0.017171 | 0.0087735 | 0.013706 | -0.0043857 | -0.0061503 | 0.011651 | 0.018311 | 0.16022 | -0.19226 | 0.11902 | 0.036621 | 0.09613 | 0.027466 | 0.23346 | 0.24261 | -122.6715 | 122.1085 | 0.050354 | 122.319 | 122.4197 | -0.073242 | -0.37079 | 0.13275 | 0.21057 | 122.3282 | 122.5342 | 122.3373 | 122.4609 | 122.319 | 122.5433 | 122.3969 | -0.37079 | 122.4609 | 122.319 | 122.3969 | 122.3373 | 122.5433 | -0.30212 | -122.7814
2269.1875 | 122.5983 | -122.2641 | 0.10071 | -0.0049592 | 0.018025 | 0.0066373 | 0.018833 | -0.00075407 | -0.0070047 | 0.010369 | 0.004578 | 0.18768 | -0.2243 | 0.086975 | -0.013733 | 0.050354 | 0 | 0.14648 | 0.24261 | -122.6486 | 122.0398 | 0.086975 | 122.2687 | 122.3511 | -0.11444 | -0.38452 | 0.14191 | 0.22888 | 122.2641 | 122.4106 | 122.2504 | 122.4518 | 122.2687 | 122.5067 | 122.3145 | -0.38452 | 122.4518 | 122.2687 | 122.3145 | 122.2504 | 122.5067 | -0.32501 | -122.7493
2270.9375 | 122.5388 | -122.3328 | 0.11444 | -0.012589 | 0.019307 | 0.013901 | 0.016056 | 0.00010033 | -0.0063639 | 0.010797 | 0.050354 | 0.14191 | -0.18768 | 0.15564 | 0.073242 | 0.14648 | -0.13275 | 0.27008 | 0.21515 | -122.6257 | 122.1451 | 0.027466 | 122.3831 | 122.4884 | -0.041199 | -0.29297 | 0.10071 | 0.23804 | 122.2 | 122.6028 | 122.406 | 122.4747 | 122.3831 | 122.5479 | 122.4792 | -0.29297 | 122.4747 | 122.3831 | 122.4792 | 122.406 | 122.5479 | -0.30212 | -122.7402
2272.625 | 122.5021 | -122.3145 | 0.11444 | 0.0103 | 0.013967 | 0.0034329 | 0.016269 | -0.00032687 | -0.0065775 | 0.0093012 | 0.07782 | 0.14648 | -0.1831 | 0.17853 | 0.07782 | 0.18768 | -0.16479 | 0.27924 | 0.20142 | -122.6257 | 122.1313 | 0.032043 | 122.3923 | 122.493 | -0.036621 | -0.31128 | 0.086975 | 0.26092 | 122.1497 | 122.5937 | 122.3923 | 122.4609 | 122.3923 | 122.5159 | 122.5021 | -0.31128 | 122.4609 | 122.3923 | 122.5021 | 122.3923 | 122.5159 | -0.29755 | -122.7402
2274.375 | 122.5296 | -122.3145 | 0.12817 | -0.0049592 | 0.01653 | 0.011123 | 0.013065 | -0.0035313 | -0.0029459 | 0.011651 | 0.050354 | 0.15106 | -0.17395 | 0.16022 | 0.064087 | 0.14191 | -0.10071 | 0.2655 | 0.20599 | -122.6807 | 122.1405 | 0.022888 | 122.3648 | 122.4747 | -0.064087 | -0.36621 | 0.07782 | 0.2243 | 122.2137 | 122.58 | 122.3785 | 122.4655 | 122.3648 | 122.5204 | 122.4564 | -0.36621 | 122.4655 | 122.3648 | 122.4564 | 122.3785 | 122.5204 | -0.30212 | -122.8088
2276.1406 | 122.6166 | -122.3007 | 0.09613 | 0.0103 | 0.018239 | 0.0092007 | 0.017124 | -0.0035313 | -0.0072183 | 0.008874 | -0.022888 | 0.19226 | -0.21973 | 0.09613 | -0.004578 | 0.073242 | 0.041199 | 0.19684 | 0.23804 | -122.7081 | 122.081 | 0.096131 | 122.2778 | 122.3969 | -0.10071 | -0.40741 | 0.14191 | 0.19684 | 122.3419 | 122.4976 | 122.2961 | 122.493 | 122.2778 | 122.5388 | 122.374 | -0.40741 | 122.493 | 122.2778 | 122.374 | 122.2961 | 122.5388 | -0.31586 | -122.8043
2277.9062 | 122.493 | -122.3557 | 0.11444 | -0.0049592 | 0.016103 | 0.01561 | 0.016269 | -0.0011813 | -0.0057229 | 0.012506 | 0.10986 | 0.13275 | -0.1831 | 0.21057 | 0.10071 | 0.19684 | -0.19684 | 0.3067 | 0.20142 | -122.6395 | 122.1725 | 0.01831 | 122.4655 | 122.5662 | -0.013733 | -0.28381 | 0.086975 | 0.29297 | 122.1588 | 122.6624 | 122.4564 | 122.4884 | 122.4655 | 122.5571 | 122.5525 | -0.28381 | 122.4884 | 122.4655 | 122.5525 | 122.4564 | 122.5571 | -0.29755 | -122.7539
2279.625 | 122.5021 | -122.3511 | 0.14191 | 0.0026703 | 0.016317 | 0.012619 | 0.013706 | -0.0050265 | -0.0072183 | 0.011865 | 0.10986 | 0.15564 | -0.15564 | 0.22888 | 0.13733 | 0.20599 | -0.1236 | 0.34332 | 0.20142 | -122.6715 | 122.1954 | 0.013733 | 122.4609 | 122.58 | -0.004578 | -0.32044 | 0.059509 | 0.2655 | 122.2275 | 122.6944 | 122.4884 | 122.5067 | 122.4609 | 122.5525 | 122.5571 | -0.32044 | 122.5067 | 122.4609 | 122.5571 | 122.4884 | 122.5525 | -0.29755 | -122.8134
2281.3906 | 122.5479 | -122.3511 | 0.10529 | -0.0049592 | 0.017598 | 0.0089871 | 0.012851 | -0.0043857 | -0.0057229 | 0.009942 | 0.045776 | 0.15564 | -0.16937 | 0.15106 | 0.059509 | 0.1236 | -0.082397 | 0.25177 | 0.20599 | -122.6807 | 122.1817 | 0.050354 | 122.3969 | 122.5021 | -0.045777 | -0.32959 | 0.10071 | 0.21515 | 122.2687 | 122.6028 | 122.4106 | 122.5067 | 122.3969 | 122.5571 | 122.4747 | -0.32959 | 122.5067 | 122.3969 | 122.4747 | 122.4106 | 122.5571 | -0.27466 | -122.7859
2283.0938 | 122.4747 | -122.3602 | 0.14648 | 0.0026703 | 0.016317 | 0.012832 | 0.015201 | -0.0031039 | -0.0072183 | 0.010156 | 0.10986 | 0.16479 | -0.16937 | 0.24261 | 0.13733 | 0.20142 | -0.15106 | 0.35706 | 0.21973 | -122.699 | 122.1909 | 0.018311 | 122.4701 | 122.6028 | -0.009155 | -0.33875 | 0.073243 | 0.27924 | 122.2092 | 122.7173 | 122.4976 | 122.525 | 122.4701 | 122.58 | 122.5616 | -0.33875 | 122.525 | 122.4701 | 122.5616 | 122.4976 | 122.58 | -0.31586 | -122.8455
2284.8594 | 122.644 | -122.3236 | 0.07782 | -0.0049592 | 0.016317 | 0.011764 | 0.018833 | -0.0058811 | -0.0063639 | 0.011224 | 0 | 0.17853 | -0.23346 | 0.11444 | 0 | 0.050354 | 0.041199 | 0.2243 | 0.23346 | -122.7493 | 122.0901 | 0.10071 | 122.3236 | 122.438 | -0.07782 | -0.42572 | 0.15564 | 0.23346 | 122.3648 | 122.5479 | 122.3236 | 122.5021 | 122.3236 | 122.5571 | 122.374 | -0.42572 | 122.5021 | 122.3236 | 122.374 | 122.3236 | 122.5571 | -0.31128 | -122.8271
2286.5625 | 122.6624 | -122.3373 | 0.09613 | 0.0026703 | 0.016957 | 0.013046 | 0.020542 | -0.0016087 | -0.0067911 | 0.012506 | 0 | 0.19226 | -0.21057 | 0.091553 | -0.032043 | 0.050354 | -0.004578 | 0.14648 | 0.23804 | -122.7219 | 122.1268 | 0.096131 | 122.3373 | 122.4289 | -0.12817 | -0.38452 | 0.14191 | 0.21057 | 122.3328 | 122.4838 | 122.3053 | 122.5296 | 122.3373 | 122.5754 | 122.3877 | -0.38452 | 122.5296 | 122.3373 | 122.3877 | 122.3053 | 122.5754 | -0.3067 | -122.818
2288.2656 | 122.6486 | -122.3465 | 0.10986 | -0.012589 | 0.016957 | 0.013046 | 0.020115 | -0.0041721 | -0.0052957 | 0.012078 | 0.004578 | 0.17853 | -0.21057 | 0.11902 | 0.004578 | 0.064087 | -0.032043 | 0.16022 | 0.23346 | -122.7448 | 122.1359 | 0.068665 | 122.3511 | 122.4655 | -0.10529 | -0.39825 | 0.1236 | 0.21515 | 122.3145 | 122.5067 | 122.3511 | 122.525 | 122.3511 | 122.58 | 122.4106 | -0.39825 | 122.525 | 122.3511 | 122.4106 | 122.3511 | 122.58 | -0.32043 | -122.8546
2290.0312 | 122.6349 | -122.3602 | 0.086975 | 0.0026703 | 0.016957 | 0.0098417 | 0.017551 | -0.0037449 | -0.0057229 | 0.0095148 | 0 | 0.19684 | -0.21973 | 0.15106 | 0.032043 | 0.091553 | 0.009155 | 0.23346 | 0.22888 | -122.7448 | 122.1405 | 0.10986 | 122.3602 | 122.5113 | -0.054932 | -0.38452 | 0.14191 | 0.21973 | 122.3694 | 122.5937 | 122.3923 | 122.5571 | 122.3602 | 122.5891 | 122.4518 | -0.38452 | 122.5571 | 122.3602 | 122.4518 | 122.3923 | 122.5891 | -0.3067 | -122.8317
2291.7969 | 122.6578 | -122.3282 | 0.10529 | 0.0103 | 0.016957 | 0.012619 | 0.012424 | -0.0045993 | -0.0050821 | 0.013146 | -0.018311 | 0.1831 | -0.21973 | 0.10986 | 0.013733 | 0.059509 | 0.032043 | 0.19684 | 0.24719 | -122.7539 | 122.1085 | 0.077819 | 122.3099 | 122.438 | -0.091553 | -0.42572 | 0.14191 | 0.20142 | 122.3602 | 122.525 | 122.3419 | 122.5113 | 122.3099 | 122.5754 | 122.3877 | -0.42572 | 122.5113 | 122.3099 | 122.3877 | 122.3419 | 122.5754 | -0.32501 | -122.8592
2293.5469 | 122.5433 | -122.3877 | 0.13275 | 0.0103 | 0.017812 | 0.0087735 | 0.013065 | -0.0052401 | -0.0046549 | 0.010797 | 0.086975 | 0.16479 | -0.16937 | 0.20142 | 0.10071 | 0.16937 | -0.091553 | 0.32044 | 0.21515 | -122.7493 | 122.2183 | 0.032044 | 122.4747 | 122.5891 | -0.032043 | -0.36163 | 0.082398 | 0.25635 | 122.2961 | 122.7081 | 122.4884 | 122.5525 | 122.4747 | 122.6028 | 122.5571 | -0.36163 | 122.5525 | 122.4747 | 122.5571 | 122.4884 | 122.6028 | -0.30212 | -122.8821
2295.25 | 122.6349 | -122.3648 | 0.10071 | 0.0103 | 0.017598 | 0.012192 | 0.017978 | -0.0024631 | -0.0035867 | 0.011651 | 0.022888 | 0.17395 | -0.20142 | 0.13733 | 0.032043 | 0.1236 | -0.10986 | 0.2243 | 0.22888 | -122.7264 | 122.1634 | 0.073242 | 122.3877 | 122.5021 | -0.068665 | -0.36163 | 0.12817 | 0.2243 | 122.2549 | 122.5891 | 122.3969 | 122.5388 | 122.3877 | 122.5937 | 122.4884 | -0.36163 | 122.5388 | 122.3877 | 122.4884 | 122.3969 | 122.5937 | -0.30212 | -122.8271
2297.0156 | 122.5525 | -122.3923 | 0.14191 | -0.0049592 | 0.018666 | 0.01561 | 0.015842 | -0.0028903 | -0.0044413 | 0.011865 | 0.10986 | 0.14191 | -0.1831 | 0.20599 | 0.10529 | 0.19684 | -0.20142 | 0.28839 | 0.19684 | -122.7173 | 122.2092 | 0 | 122.5021 | 122.5983 | -0.036621 | -0.32501 | 0.054931 | 0.29297 | 122.1909 | 122.6807 | 122.4976 | 122.5342 | 122.5021 | 122.5891 | 122.5891 | -0.32501 | 122.5342 | 122.5021 | 122.5891 | 122.4976 | 122.5891 | -0.32501 | -122.8592
2298.7188 | 122.5616 | -122.3923 | 0.13733 | 0.0103 | 0.018666 | 0.011764 | 0.017765 | -0.0028903 | -0.0048685 | 0.010797 | 0.086975 | 0.16022 | -0.17853 | 0.19684 | 0.09613 | 0.19226 | -0.18768 | 0.27924 | 0.20142 | -122.731 | 122.2137 | 0.022888 | 122.4792 | 122.5891 | -0.041199 | -0.33875 | 0.064087 | 0.2655 | 122.2046 | 122.6715 | 122.4884 | 122.5525 | 122.4792 | 122.5937 | 122.5845 | -0.33875 | 122.5525 | 122.4792 | 122.5845 | 122.4884 | 122.5937 | -0.31586 | -122.8683
2300.4844 | 122.5937 | -122.3831 | 0.12817 | -0.0049592 | 0.017598 | 0.012832 | 0.01157 | -0.0041721 | -0.0029459 | 0.010369 | 0.050354 | 0.14648 | -0.17853 | 0.15564 | 0.054932 | 0.15106 | -0.11444 | 0.26093 | 0.20142 | -122.7264 | 122.2046 | 0.01831 | 122.4335 | 122.5388 | -0.073242 | -0.34332 | 0.073242 | 0.22888 | 122.2687 | 122.644 | 122.438 | 122.5296 | 122.4335 | 122.5845 | 122.5342 | -0.34332 | 122.5296 | 122.4335 | 122.5342 | 122.438 | 122.5845 | -0.3067 | -122.8546
2302.2031 | 122.6349 | -122.3831 | 0.11902 | 0.0026703 | 0.018453 | 0.0079189 | 0.017124 | -0.0043857 | -0.0080729 | 0.010369 | 0.045776 | 0.19226 | -0.21973 | 0.14648 | 0.027466 | 0.09613 | 0.032043 | 0.22888 | 0.24719 | -122.7493 | 122.1634 | 0.073242 | 122.4289 | 122.5296 | -0.091553 | -0.36621 | 0.12817 | 0.2655 | 122.4152 | 122.612 | 122.4106 | 122.5754 | 122.4289 | 122.6303 | 122.4792 | -0.36621 | 122.5754 | 122.4289 | 122.4792 | 122.4106 | 122.6303 | -0.33875 | -122.8683
2303.9688 | 122.5525 | -122.4243 | 0.11902 | -0.0049592 | 0.017598 | 0.011123 | 0.017978 | -0.00096767 | -0.0059365 | 0.012933 | 0.10986 | 0.13733 | -0.16022 | 0.2243 | 0.11444 | 0.19684 | -0.18768 | 0.30212 | 0.20599 | -122.7264 | 122.2641 | 0.01831 | 122.5342 | 122.6486 | -0.004578 | -0.30212 | 0.086975 | 0.27008 | 122.2366 | 122.7264 | 122.5388 | 122.5616 | 122.5342 | 122.6303 | 122.6212 | -0.30212 | 122.5616 | 122.5342 | 122.6212 | 122.5388 | 122.6303 | -0.27924 | -122.8455
2305.7344 | 122.6028 | -122.4106 | 0.10986 | 0.0026703 | 0.019521 | 0.015396 | 0.017765 | -0.00011327 | -0.0063639 | 0.0093012 | 0.091553 | 0.16022 | -0.1831 | 0.21515 | 0.09613 | 0.17395 | -0.17853 | 0.28381 | 0.19226 | -122.7448 | 122.2275 | 0.050354 | 122.5021 | 122.6257 | -0.013733 | -0.33417 | 0.082398 | 0.27466 | 122.2321 | 122.6944 | 122.5067 | 122.5708 | 122.5021 | 122.6028 | 122.5845 | -0.33417 | 122.5708 | 122.5021 | 122.5845 | 122.5067 | 122.6028 | -0.29297 | -122.8546
2307.4844 | 122.6624 | -122.4152 | 0.10529 | 0.0026703 | 0.017171 | 0.014114 | 0.020328 | 0.00010033 | -0.0089273 | 0.009942 | 0.041199 | 0.16022 | -0.21515 | 0.14191 | 0 | 0.086975 | -0.032043 | 0.19226 | 0.23804 | -122.7585 | 122.2 | 0.054931 | 122.4564 | 122.5571 | -0.10529 | -0.34332 | 0.13275 | 0.25635 | 122.3831 | 122.6074 | 122.4152 | 122.5754 | 122.4564 | 122.6532 | 122.5021 | -0.34332 | 122.5754 | 122.4564 | 122.5021 | 122.4152 | 122.6532 | -0.32044 | -122.8638
2309.2656 | 122.6395 | -122.3831 | 0.10986 | 0.0026703 | 0.018025 | 0.014114 | 0.019047 | -0.0026767 | -0.0063639 | 0.01101 | 0.054932 | 0.18768 | -0.21515 | 0.16022 | 0.07782 | 0.11444 | -0.054932 | 0.25177 | 0.23346 | -122.7631 | 122.168 | 0.07782 | 122.438 | 122.5433 | -0.032043 | -0.37994 | 0.1236 | 0.27008 | 122.3282 | 122.6349 | 122.4609 | 122.5708 | 122.438 | 122.6166 | 122.4976 | -0.37994 | 122.5708 | 122.438 | 122.4976 | 122.4609 | 122.6166 | -0.32501 | -122.8729
2310.9688 | 122.6624 | -122.4014 | 0.10071 | 0.0026703 | 0.01888 | 0.011337 | 0.01392 | -0.0043857 | -0.0040139 | 0.010583 | 0.027466 | 0.1831 | -0.20142 | 0.11902 | 0.036621 | 0.09613 | 0.022888 | 0.2243 | 0.23804 | -122.8043 | 122.2 | 0.082397 | 122.4289 | 122.5204 | -0.064087 | -0.40283 | 0.13733 | 0.22888 | 122.4243 | 122.6257 | 122.438 | 122.5845 | 122.4289 | 122.6395 | 122.4976 | -0.40283 | 122.5845 | 122.4289 | 122.4976 | 122.438 | 122.6395 | -0.30212 | -122.905
2312.7344 | 122.6486 | -122.4152 | 0.10986 | 0.0026703 | 0.019521 | 0.011978 | 0.01926 | -0.0011813 | -0.0067911 | 0.012292 | 0.064087 | 0.16479 | -0.20142 | 0.13275 | 0.041199 | 0.10529 | -0.027466 | 0.21515 | 0.23346 | -122.7676 | 122.2137 | 0.054932 | 122.4792 | 122.5479 | -0.068664 | -0.35248 | 0.1236 | 0.2655 | 122.3877 | 122.6303 | 122.4564 | 122.58 | 122.4792 | 122.6486 | 122.5204 | -0.35248 | 122.58 | 122.4792 | 122.5204 | 122.4564 | 122.6486 | -0.31128 | -122.8775
2314.4375 | 122.6212 | -122.4197 | 0.10986 | 0.0026703 | 0.017171 | 0.012405 | 0.010288 | -0.0031039 | -0.0020913 | 0.011224 | 0.036621 | 0.14648 | -0.17853 | 0.15106 | 0.086975 | 0.15106 | -0.10529 | 0.25177 | 0.20142 | -122.8226 | 122.2412 | 0.036621 | 122.4564 | 122.5708 | -0.022888 | -0.40283 | 0.091553 | 0.21515 | 122.3145 | 122.6715 | 122.5067 | 122.5662 | 122.4564 | 122.6212 | 122.5708 | -0.40283 | 122.5662 | 122.4564 | 122.5708 | 122.5067 | 122.6212 | -0.28839 | -122.9324
2316.2031 | 122.6898 | -122.3877 | 0.073242 | 0.0026703 | 0.015889 | 0.0068509 | 0.015201 | -0.0050265 | -0.0067911 | 0.010583 | -0.032043 | 0.19684 | -0.2243 | 0.09613 | 0.013733 | 0.064087 | 0.054932 | 0.20142 | 0.24719 | -122.7814 | 122.1634 | 0.1236 | 122.3557 | 122.4838 | -0.059509 | -0.39368 | 0.17395 | 0.19226 | 122.4426 | 122.5891 | 122.4014 | 122.5845 | 122.3557 | 122.6349 | 122.4518 | -0.39368 | 122.5845 | 122.3557 | 122.4518 | 122.4014 | 122.6349 | -0.29755 | -122.8546
2317.8906 | 122.7127 | -122.3785 | 0.091553 | -0.0049592 | 0.019521 | 0.014541 | 0.020115 | -0.00075407 | -0.0070047 | 0.0097284 | 0.013733 | 0.17853 | -0.21973 | 0.07782 | -0.032043 | 0.036621 | 0.004578 | 0.13275 | 0.23346 | -122.8134 | 122.1588 | 0.086975 | 122.3923 | 122.4564 | -0.1236 | -0.43488 | 0.14191 | 0.23346 | 122.3831 | 122.5113 | 122.3465 | 122.5571 | 122.3923 | 122.612 | 122.4152 | -0.43488 | 122.5571 | 122.3923 | 122.4152 | 122.3465 | 122.612 | -0.31128 | -122.905
2319.6406 | 122.7219 | -122.4197 | 0.10529 | 0.0026703 | 0.015248 | 0.0096279 | 0.017978 | -0.00096767 | -0.0052957 | 0.012719 | -0.018311 | 0.18768 | -0.2243 | 0.068665 | -0.022888 | 0.045776 | 0.004578 | 0.15564 | 0.25177 | -122.7676 | 122.1954 | 0.082397 | 122.4014 | 122.4884 | -0.12817 | -0.3479 | 0.14648 | 0.20599 | 122.4243 | 122.5754 | 122.3969 | 122.6074 | 122.4014 | 122.6715 | 122.4655 | -0.3479 | 122.6074 | 122.4014 | 122.4655 | 122.3969 | 122.6715 | -0.32959 | -122.8729
2321.3906 | 122.7081 | -122.4197 | 0.082397 | -0.0049592 | 0.017171 | 0.01326 | 0.013706 | -0.0039585 | -0.0055093 | 0.0095148 | -0.032043 | 0.1831 | -0.2243 | 0.073242 | 0.013733 | 0.054932 | 0.054932 | 0.19226 | 0.24719 | -122.8226 | 122.1954 | 0.10071 | 122.3877 | 122.493 | -0.068664 | -0.40283 | 0.16479 | 0.19226 | 122.4747 | 122.612 | 122.4335 | 122.6028 | 122.3877 | 122.6669 | 122.4747 | -0.40283 | 122.6028 | 122.3877 | 122.4747 | 122.4335 | 122.6669 | -0.3067 | -122.905
2323.0938 | 122.6349 | -122.4289 | 0.10529 | -0.0049592 | 0.017385 | 0.0083463 | 0.013065 | -0.0052401 | -0.0031595 | 0.009942 | 0.050354 | 0.14191 | -0.16937 | 0.15106 | 0.068665 | 0.15564 | -0.10529 | 0.2655 | 0.20142 | -122.8088 | 122.2595 | 0.036621 | 122.4792 | 122.58 | -0.036621 | -0.37994 | 0.09613 | 0.21973 | 122.3236 | 122.6944 | 122.4976 | 122.5708 | 122.4792 | 122.6303 | 122.5845 | -0.37994 | 122.5708 | 122.4792 | 122.5845 | 122.4976 | 122.6303 | -0.27466 | -122.9141
2324.8594 | 122.6807 | -122.4289 | 0.10071 | 0.0026703 | 0.017171 | 0.011337 | 0.019901 | -0.0041721 | -0.0048685 | 0.0095148 | 0.050354 | 0.17853 | -0.21973 | 0.13733 | 0.022888 | 0.10529 | -0.018311 | 0.21057 | 0.2243 | -122.7448 | 122.2092 | 0.07782 | 122.4792 | 122.5662 | -0.07782 | -0.31586 | 0.1236 | 0.27008 | 122.4106 | 122.6395 | 122.4518 | 122.6074 | 122.4792 | 122.6532 | 122.5342 | -0.31586 | 122.6074 | 122.4792 | 122.5342 | 122.4518 | 122.6532 | -0.32044 | -122.8455
2326.625 | 122.7356 | -122.4014 | 0.07782 | 0.0026703 | 0.015248 | 0.012405 | 0.019687 | -0.0020359 | -0.0059365 | 0.010156 | -0.022888 | 0.19684 | -0.2243 | 0.09613 | -0.009155 | 0.059509 | -0.009155 | 0.15564 | 0.24719 | -122.7814 | 122.1771 | 0.11902 | 122.3785 | 122.4976 | -0.086975 | -0.37994 | 0.16937 | 0.20142 | 122.3923 | 122.5571 | 122.3923 | 122.5983 | 122.3785 | 122.6486 | 122.4609 | -0.37994 | 122.5983 | 122.3785 | 122.4609 | 122.3923 | 122.6486 | -0.30212 | -122.8592
2328.375 | 122.6669 | -122.4609 | 0.10529 | -0.012589 | 0.016957 | 0.0098417 | 0.01691 | -0.0018223 | -0.0070047 | 0.011437 | 0.068665 | 0.17395 | -0.21973 | 0.13275 | 0.050354 | 0.10529 | -0.022888 | 0.24261 | 0.21973 | -122.7997 | 122.2412 | 0.068664 | 122.5296 | 122.5937 | -0.054932 | -0.33875 | 0.11444 | 0.28839 | 122.438 | 122.7036 | 122.5113 | 122.6349 | 122.5296 | 122.6807 | 122.5662 | -0.33875 | 122.6349 | 122.5296 | 122.5662 | 122.5113 | 122.6807 | -0.32501 | -122.905
2330.0781 | 122.6303 | -122.4335 | 0.11902 | -0.0049592 | 0.017812 | 0.0081327 | 0.012851 | -0.0035313 | -0.0040139 | 0.0097284 | 0.073242 | 0.15564 | -0.18768 | 0.14648 | 0.07782 | 0.13733 | -0.032043 | 0.27008 | 0.21515 | -122.818 | 122.2458 | 0.036621 | 122.5067 | 122.58 | -0.041199 | -0.38452 | 0.09613 | 0.26092 | 122.4014 | 122.7036 | 122.5113 | 122.5891 | 122.5067 | 122.6486 | 122.5708 | -0.38452 | 122.5891 | 122.5067 | 122.5708 | 122.5113 | 122.6486 | -0.3067 | -122.937
2331.8281 | 122.731 | -122.4197 | 0.11444 | 0.0026703 | 0.01653 | 0.01091 | 0.01926 | -0.00096767 | -0.0057229 | 0.011437 | -0.009155 | 0.1831 | -0.21973 | 0.091553 | -0.018311 | 0.059509 | -0.004578 | 0.16937 | 0.24719 | -122.7814 | 122.2 | 0.068664 | 122.4106 | 122.5113 | -0.13275 | -0.36163 | 0.13275 | 0.21057 | 122.4152 | 122.5891 | 122.4014 | 122.6028 | 122.4106 | 122.6669 | 122.4792 | -0.36163 | 122.6028 | 122.4106 | 122.4792 | 122.4014 | 122.6669 | -0.33417 | -122.8958
2333.5156 | 122.6349 | -122.4747 | 0.13275 | 0.0026703 | 0.018025 | 0.010696 | 0.012424 | -0.0039585 | -0.0029459 | 0.0075922 | 0.054932 | 0.13733 | -0.1831 | 0.14648 | 0.073242 | 0.17853 | -0.11902 | 0.27466 | 0.1831 | -122.818 | 122.2916 | 0.004578 | 122.5296 | 122.6212 | -0.059509 | -0.34332 | 0.050354 | 0.23804 | 122.3557 | 122.7493 | 122.5479 | 122.612 | 122.5296 | 122.6578 | 122.6532 | -0.34332 | 122.612 | 122.5296 | 122.6532 | 122.5479 | 122.6578 | -0.31586 | -122.9507
2335.2812 | 122.7356 | -122.438 | 0.10071 | -0.0049592 | 0.016744 | 0.012619 | 0.019047 | -0.0018223 | -0.0059365 | 0.011437 | -0.013733 | 0.18768 | -0.2243 | 0.082397 | -0.022888 | 0.059509 | -0.004578 | 0.16022 | 0.25177 | -122.8134 | 122.2137 | 0.086975 | 122.4243 | 122.5204 | -0.1236 | -0.37537 | 0.15106 | 0.21057 | 122.4335 | 122.5983 | 122.4152 | 122.6257 | 122.4243 | 122.6898 | 122.4976 | -0.37537 | 122.6257 | 122.4243 | 122.4976 | 122.4152 | 122.6898 | -0.32501 | -122.9141
2336.9688 | 122.6028 | -122.4792 | 0.11902 | -0.012589 | 0.015248 | 0.012619 | 0.015842 | -0.0016087 | -0.0050821 | 0.012078 | 0.10071 | 0.14648 | -0.17395 | 0.19226 | 0.11444 | 0.20599 | -0.17853 | 0.3067 | 0.21057 | -122.7997 | 122.3053 | 0.027465 | 122.58 | 122.6715 | -0.004578 | -0.32044 | 0.091552 | 0.27466 | 122.3007 | 122.7859 | 122.5937 | 122.6257 | 122.58 | 122.6898 | 122.6852 | -0.32044 | 122.6257 | 122.58 | 122.6852 | 122.5937 | 122.6898 | -0.29297 | -122.9187
2338.7188 | 122.6578 | -122.4426 | 0.10986 | -0.012589 | 0.017598 | 0.0064237 | 0.014774 | -0.0026767 | -0.0065775 | 0.010583 | 0.045776 | 0.15106 | -0.18768 | 0.14191 | 0.068665 | 0.13275 | -0.086975 | 0.25635 | 0.21057 | -122.8088 | 122.2549 | 0.041199 | 122.4884 | 122.5845 | -0.041198 | -0.36621 | 0.10071 | 0.23346 | 122.3557 | 122.699 | 122.5113 | 122.5937 | 122.4884 | 122.6532 | 122.5754 | -0.36621 | 122.5937 | 122.4884 | 122.5754 | 122.5113 | 122.6532 | -0.29755 | -122.9187
2340.4844 | 122.6486 | -122.438 | 0.10529 | 0.0026703 | 0.01653 | 0.012832 | 0.014347 | -0.0041721 | -0.0050821 | 0.011224 | 0.068665 | 0.16022 | -0.1831 | 0.16937 | 0.064087 | 0.12817 | -0.036621 | 0.27466 | 0.21515 | -122.8363 | 122.2549 | 0.054931 | 122.5067 | 122.6074 | -0.041199 | -0.39825 | 0.10986 | 0.25177 | 122.4014 | 122.7127 | 122.5021 | 122.5983 | 122.5067 | 122.6532 | 122.5662 | -0.39825 | 122.5983 | 122.5067 | 122.5662 | 122.5021 | 122.6532 | -0.28839 | -122.9416
2342.25 | 122.699 | -122.4472 | 0.10071 | 0.0103 | 0.019307 | 0.0098417 | 0.021183 | -0.0039585 | -0.0055093 | 0.010583 | 0.059509 | 0.18768 | -0.19684 | 0.16479 | 0.036621 | 0.10529 | -0.032043 | 0.25635 | 0.23346 | -122.818 | 122.2504 | 0.086975 | 122.5067 | 122.612 | -0.064087 | -0.37079 | 0.13275 | 0.25635 | 122.4152 | 122.7036 | 122.4838 | 122.6349 | 122.5067 | 122.6807 | 122.5525 | -0.37079 | 122.6349 | 122.5067 | 122.5525 | 122.4838 | 122.6807 | -0.29755 | -122.9187
2343.9375 | 122.7081 | -122.4655 | 0.082397 | 0.0026703 | 0.020803 | 0.016678 | 0.019047 | -0.0041721 | -0.0052957 | 0.010156 | 0.068665 | 0.17853 | -0.21057 | 0.14191 | 0.036621 | 0.10986 | -0.036621 | 0.22888 | 0.22888 | -122.8271 | 122.2549 | 0.096131 | 122.5342 | 122.6074 | -0.045776 | -0.36163 | 0.14649 | 0.27924 | 122.4289 | 122.6944 | 122.5021 | 122.644 | 122.5342 | 122.6944 | 122.5754 | -0.36163 | 122.644 | 122.5342 | 122.5754 | 122.5021 | 122.6944 | -0.29297 | -122.9095
2345.7031 | 122.6028 | -122.4747 | 0.14648 | -0.0049592 | 0.016103 | 0.015182 | 0.017124 | -0.0022495 | -0.0055093 | 0.012078 | 0.10986 | 0.14648 | -0.17395 | 0.19684 | 0.09613 | 0.20142 | -0.18768 | 0.31586 | 0.20599 | -122.7997 | 122.3007 | 0 | 122.5845 | 122.6715 | -0.050354 | -0.32501 | 0.05951 | 0.28381 | 122.287 | 122.7905 | 122.5708 | 122.6212 | 122.5845 | 122.6807 | 122.6761 | -0.32501 | 122.6212 | 122.5845 | 122.6761 | 122.5708 | 122.6807 | -0.32043 | -122.9462
2347.3906 | 122.6578 | -122.4609 | 0.14191 | 0.0026703 | 0.017171 | 0.010055 | 0.012211 | -0.0024631 | -0.0048685 | 0.010156 | 0.041199 | 0.15106 | -0.17853 | 0.14648 | 0.07782 | 0.14648 | -0.10986 | 0.25177 | 0.20599 | -122.8409 | 122.2824 | 0.009155 | 122.5021 | 122.6074 | -0.064087 | -0.37994 | 0.064087 | 0.21973 | 122.3511 | 122.7127 | 122.5388 | 122.612 | 122.5021 | 122.6669 | 122.6074 | -0.37994 | 122.612 | 122.5021 | 122.6074 | 122.5388 | 122.6669 | -0.32044 | -122.9828
2349.0938 | 122.7356 | -122.4152 | 0.09613 | -0.0049592 | 0.017385 | 0.013687 | 0.01926 | -0.0018223 | -0.0059365 | 0.009942 | 0.009155 | 0.17853 | -0.21515 | 0.10529 | -0.018311 | 0.073242 | -0.009155 | 0.16022 | 0.24261 | -122.8271 | 122.2 | 0.082398 | 122.4243 | 122.5204 | -0.11444 | -0.41199 | 0.14649 | 0.2243 | 122.406 | 122.5754 | 122.3969 | 122.5937 | 122.4243 | 122.6578 | 122.4884 | -0.41199 | 122.5937 | 122.4243 | 122.4884 | 122.3969 | 122.6578 | -0.31128 | -122.9233
2350.8594 | 122.6349 | -122.4564 | 0.14648 | -0.0049592 | 0.019734 | 0.010483 | 0.013706 | -0.0013949 | -0.0033731 | 0.0090876 | 0.11444 | 0.14648 | -0.17853 | 0.19226 | 0.10071 | 0.20142 | -0.17853 | 0.29755 | 0.1831 | -122.8043 | 122.2778 | 0 | 122.5708 | 122.6486 | -0.045776 | -0.3479 | 0.036621 | 0.29297 | 122.2778 | 122.7539 | 122.5571 | 122.6028 | 122.5708 | 122.6395 | 122.6578 | -0.3479 | 122.6028 | 122.5708 | 122.6578 | 122.5571 | 122.6395 | -0.32501 | -122.9507
2352.625 | 122.7356 | -122.4701 | 0.10529 | 0.0103 | 0.021657 | 0.011764 | 0.022892 | 0.00052773 | -0.0052957 | 0.009942 | 0.073242 | 0.1831 | -0.20142 | 0.13275 | 0.018311 | 0.07782 | -0.027466 | 0.20142 | 0.25635 | -122.8409 | 122.2687 | 0.077819 | 122.5433 | 122.6028 | -0.086975 | -0.37079 | 0.15106 | 0.27466 | 122.4426 | 122.6715 | 122.4884 | 122.6532 | 122.5433 | 122.7264 | 122.5479 | -0.37079 | 122.6532 | 122.5433 | 122.5479 | 122.4884 | 122.7264 | -0.3067 | -122.9462
2354.3281 | 122.6395 | -122.4701 | 0.10529 | -0.0049592 | 0.015676 | 0.01326 | 0.010502 | -0.0024631 | -0.0040139 | 0.009942 | 0.09613 | 0.16022 | -0.19226 | 0.20599 | 0.11902 | 0.1831 | -0.13733 | 0.33417 | 0.21515 | -122.8409 | 122.2778 | 0.054931 | 122.5662 | 122.6761 | 0.013733 | -0.37079 | 0.10986 | 0.28839 | 122.3328 | 122.8043 | 122.5891 | 122.6303 | 122.5662 | 122.6852 | 122.6532 | -0.37079 | 122.6303 | 122.5662 | 122.6532 | 122.5891 | 122.6852 | -0.29755 | -122.9462
2356.0938 | 122.7219 | -122.4792 | 0.091553 | -0.0049592 | 0.017385 | 0.011551 | 0.015415 | -0.0024631 | -0.0033731 | 0.011651 | 0.059509 | 0.17395 | -0.21973 | 0.14191 | 0.045776 | 0.091553 | 0.009155 | 0.23804 | 0.24719 | -122.8592 | 122.2595 | 0.082397 | 122.5388 | 122.6212 | -0.045777 | -0.37994 | 0.15564 | 0.27924 | 122.4884 | 122.7173 | 122.525 | 122.6532 | 122.5388 | 122.7264 | 122.5708 | -0.37994 | 122.6532 | 122.5388 | 122.5708 | 122.525 | 122.7264 | -0.31128 | -122.9507
2357.8438 | 122.7402 | -122.4655 | 0.10071 | 0.0026703 | 0.01653 | 0.012619 | 0.019901 | -0.00075407 | -0.0072183 | 0.011224 | 0.036621 | 0.16479 | -0.21515 | 0.1236 | 0.027466 | 0.073242 | -0.018311 | 0.19226 | 0.2243 | -122.85 | 122.2504 | 0.064087 | 122.5021 | 122.5891 | -0.073242 | -0.38452 | 0.1236 | 0.25177 | 122.4472 | 122.6578 | 122.493 | 122.6303 | 122.5021 | 122.6898 | 122.5388 | -0.38452 | 122.6303 | 122.5021 | 122.5388 | 122.493 | 122.6898 | -0.31586 | -122.9507
2359.5469 | 122.6532 | -122.4976 | 0.11902 | 0.0026703 | 0.019307 | 0.012192 | 0.01456 | -0.0065219 | -0.0029459 | 0.010156 | 0.082397 | 0.16022 | -0.16937 | 0.21057 | 0.12817 | 0.19684 | -0.13733 | 0.33875 | 0.21515 | -122.8546 | 122.3282 | 0.041198 | 122.58 | 122.7081 | 0.009155 | -0.35706 | 0.09613 | 0.25177 | 122.3602 | 122.8363 | 122.6257 | 122.6578 | 122.58 | 122.7127 | 122.6944 | -0.35706 | 122.6578 | 122.58 | 122.6944 | 122.6257 | 122.7127 | -0.28839 | -122.9736
2361.3125 | 122.7676 | -122.4609 | 0.073242 | -0.012589 | 0.016957 | 0.014328 | 0.018406 | -0.0020359 | -0.0055093 | 0.012719 | -0.013733 | 0.1831 | -0.21057 | 0.086975 | -0.018311 | 0.050354 | 0.022888 | 0.16479 | 0.24261 | -122.8409 | 122.2504 | 0.10986 | 122.4472 | 122.5479 | -0.091553 | -0.37994 | 0.16937 | 0.19684 | 122.4838 | 122.6257 | 122.4426 | 122.644 | 122.4472 | 122.7036 | 122.5113 | -0.37994 | 122.644 | 122.4472 | 122.5113 | 122.4426 | 122.7036 | -0.28381 | -122.9141
2363.0625 | 122.7676 | -122.4792 | 0.091553 | -0.0049592 | 0.017598 | 0.014541 | 0.017978 | -0.0013949 | -0.0067911 | 0.010369 | 0.013733 | 0.17853 | -0.21973 | 0.10071 | -0.013733 | 0.050354 | 0 | 0.16479 | 0.24261 | -122.8455 | 122.2595 | 0.086975 | 122.493 | 122.58 | -0.10529 | -0.36621 | 0.15106 | 0.23346 | 122.4792 | 122.644 | 122.4655 | 122.6578 | 122.493 | 122.7219 | 122.5296 | -0.36621 | 122.6578 | 122.493 | 122.5296 | 122.4655 | 122.7219 | -0.31128 | -122.937
2364.8281 | 122.6532 | -122.5067 | 0.12817 | -0.0049592 | 0.017171 | 0.010483 | 0.013279 | -0.0022495 | -0.0014505 | 0.0095148 | 0.10071 | 0.15106 | -0.16479 | 0.17853 | 0.10071 | 0.19684 | -0.17853 | 0.29297 | 0.20599 | -122.8363 | 122.3419 | 0.022888 | 122.6074 | 122.6852 | -0.027466 | -0.32959 | 0.07782 | 0.2655 | 122.3282 | 122.7997 | 122.6074 | 122.6578 | 122.6074 | 122.7127 | 122.7036 | -0.32959 | 122.6578 | 122.6074 | 122.7036 | 122.6074 | 122.7127 | -0.29297 | -122.9645
2366.5312 | 122.644 | -122.5204 | 0.13275 | -0.0049592 | 0.016744 | 0.010055 | 0.013706 | -0.0043857 | -0.0046549 | 0.011437 | 0.091553 | 0.15106 | -0.1831 | 0.21973 | 0.13275 | 0.21057 | -0.1236 | 0.35248 | 0.19684 | -122.818 | 122.3373 | 0.018311 | 122.612 | 122.7402 | 0 | -0.29755 | 0.064087 | 0.27466 | 122.3969 | 122.8729 | 122.6532 | 122.6715 | 122.612 | 122.7173 | 122.731 | -0.29755 | 122.6715 | 122.612 | 122.731 | 122.6532 | 122.7173 | -0.31586 | -122.9507
2368.3125 | 122.644 | -122.5296 | 0.13733 | -0.0049592 | 0.019094 | 0.012619 | 0.017978 | -0.0024631 | -0.0042277 | 0.0097284 | 0.11902 | 0.13275 | -0.16022 | 0.20599 | 0.10529 | 0.20142 | -0.19684 | 0.29755 | 0.20142 | -122.8363 | 122.3694 | -0.004578 | 122.6486 | 122.7356 | -0.032043 | -0.3067 | 0.064087 | 0.27924 | 122.3328 | 122.8271 | 122.6349 | 122.6624 | 122.6486 | 122.731 | 122.731 | -0.3067 | 122.6624 | 122.6486 | 122.731 | 122.6349 | 122.731 | -0.29755 | -122.9736
2370.0156 | 122.7768 | -122.5113 | 0.09613 | 0.0103 | 0.01888 | 0.012192 | 0.01926 | -0.00054047 | -0.0087137 | 0.011224 | 0.018311 | 0.17395 | -0.21515 | 0.10529 | -0.018311 | 0.041199 | 0.009155 | 0.17395 | 0.24719 | -122.8455 | 122.2961 | 0.07782 | 122.5296 | 122.6166 | -0.11444 | -0.33417 | 0.15106 | 0.23346 | 122.5204 | 122.6852 | 122.493 | 122.6852 | 122.5296 | 122.7585 | 122.5525 | -0.33417 | 122.6852 | 122.5296 | 122.5525 | 122.493 | 122.7585 | -0.31128 | -122.9416
2371.7656 | 122.6624 | -122.5067 | 0.13275 | 0.0026703 | 0.013967 | 0.016678 | 0.016269 | -0.0024631 | -0.0052957 | 0.01101 | 0.09613 | 0.15106 | -0.16479 | 0.19226 | 0.10986 | 0.20142 | -0.1831 | 0.30212 | 0.19226 | -122.8043 | 122.3419 | 0.018311 | 122.6028 | 122.699 | -0.022888 | -0.29755 | 0.05951 | 0.26092 | 122.3236 | 122.8088 | 122.6166 | 122.6578 | 122.6028 | 122.699 | 122.7081 | -0.29755 | 122.6578 | 122.6028 | 122.7081 | 122.6166 | 122.699 | -0.29755 | -122.937
2373.5156 | 122.6532 | -122.5067 | 0.12817 | 0.0026703 | 0.016744 | 0.011337 | 0.016269 | -0.0028903 | -0.0050821 | 0.012292 | 0.11444 | 0.13275 | -0.16479 | 0.21973 | 0.11444 | 0.20599 | -0.20599 | 0.31586 | 0.18768 | -122.8088 | 122.3419 | 0.004577 | 122.6212 | 122.7264 | -0.013733 | -0.30212 | 0.059509 | 0.27924 | 122.3007 | 122.8226 | 122.6212 | 122.6395 | 122.6212 | 122.6944 | 122.7127 | -0.30212 | 122.6395 | 122.6212 | 122.7127 | 122.6212 | 122.6944 | -0.29297 | -122.937
2375.2188 | 122.7539 | -122.5021 | 0.11444 | -0.0049592 | 0.015676 | 0.012192 | 0.019047 | -0.0018223 | -0.0072183 | 0.011865 | 0.036621 | 0.17853 | -0.21515 | 0.1236 | 0.004578 | 0.086975 | -0.013733 | 0.1831 | 0.22888 | -122.8546 | 122.287 | 0.064087 | 122.5388 | 122.6257 | -0.10986 | -0.35248 | 0.11444 | 0.25177 | 122.4884 | 122.6852 | 122.5067 | 122.6807 | 122.5388 | 122.731 | 122.5891 | -0.35248 | 122.6807 | 122.5388 | 122.5891 | 122.5067 | 122.731 | -0.32959 | -122.9691
2376.9688 | 122.7859 | -122.4747 | 0.09613 | 0.0026703 | 0.017598 | 0.014328 | 0.016269 | 0.0024503 | -0.0085001 | 0.0097284 | 0.009155 | 0.17395 | -0.21057 | 0.09613 | 0.022888 | 0.073242 | -0.022888 | 0.19226 | 0.24261 | -122.85 | 122.2641 | 0.07782 | 122.4838 | 122.5708 | -0.073242 | -0.37537 | 0.14649 | 0.21973 | 122.4518 | 122.6669 | 122.4976 | 122.6486 | 122.4838 | 122.7173 | 122.5479 | -0.37537 | 122.6486 | 122.4838 | 122.5479 | 122.4976 | 122.7173 | -0.3067 | -122.9462
2378.6562 | 122.6669 | -122.5525 | 0.12817 | -0.0049592 | 0.016957 | 0.0087735 | 0.015629 | -0.0011813 | -0.0048685 | 0.012719 | 0.082397 | 0.13275 | -0.16479 | 0.20142 | 0.11902 | 0.20142 | -0.19684 | 0.32044 | 0.19226 | -122.8317 | 122.3877 | 0.004577 | 122.6349 | 122.7539 | -0.009155 | -0.27924 | 0.064087 | 0.24719 | 122.3557 | 122.8729 | 122.6715 | 122.6852 | 122.6349 | 122.7448 | 122.7539 | -0.27924 | 122.6852 | 122.6349 | 122.7539 | 122.6715 | 122.7448 | -0.29297 | -122.9599
2380.4062 | 122.731 | -122.5159 | 0.10071 | -0.012589 | 0.015248 | 0.012832 | 0.013279 | -0.0035313 | -0.0044413 | 0.01101 | 0.050354 | 0.15106 | -0.17853 | 0.13733 | 0.068665 | 0.13733 | -0.086975 | 0.25635 | 0.19684 | -122.8912 | 122.3373 | 0.050354 | 122.5662 | 122.6532 | -0.032043 | -0.37537 | 0.09613 | 0.22888 | 122.4289 | 122.7722 | 122.5845 | 122.6669 | 122.5662 | 122.7127 | 122.6532 | -0.37537 | 122.6669 | 122.5662 | 122.6532 | 122.5845 | 122.7127 | -0.27924 | -122.9919
2382.1562 | 122.6852 | -122.5067 | 0.13733 | -0.012589 | 0.015676 | 0.010483 | 0.013065 | -0.0041721 | -0.0038003 | 0.01101 | 0.07782 | 0.16022 | -0.17395 | 0.21515 | 0.10986 | 0.18768 | -0.1236 | 0.32501 | 0.20599 | -122.8683 | 122.3328 | 0.022888 | 122.5845 | 122.7219 | -0.027466 | -0.36163 | 0.068665 | 0.25177 | 122.3831 | 122.8317 | 122.6166 | 122.6669 | 122.5845 | 122.7127 | 122.6944 | -0.36163 | 122.6669 | 122.5845 | 122.6944 | 122.6166 | 122.7127 | -0.31128 | -123.0057
2383.9219 | 122.7768 | -122.5113 | 0.10071 | 0.0103 | 0.018025 | 0.0098417 | 0.020115 | -0.0026767 | -0.0040139 | 0.011865 | 0.027466 | 0.18768 | -0.22888 | 0.10986 | -0.004578 | 0.10071 | -0.059509 | 0.17853 | 0.23346 | -122.9004 | 122.2824 | 0.086975 | 122.5388 | 122.6212 | -0.10529 | -0.3891 | 0.13275 | 0.25635 | 122.4518 | 122.6898 | 122.5067 | 122.699 | 122.5388 | 122.7448 | 122.612 | -0.3891 | 122.699 | 122.5388 | 122.612 | 122.5067 | 122.7448 | -0.32959 | -123.0011
2385.6094 | 122.7036 | -122.5479 | 0.13275 | 0.0103 | 0.013753 | 0.0098417 | 0.015201 | -0.0028903 | -0.0044413 | 0.012719 | 0.086975 | 0.14191 | -0.17395 | 0.19684 | 0.09613 | 0.18768 | -0.17853 | 0.3067 | 0.20142 | -122.85 | 122.374 | 0.009156 | 122.6349 | 122.7448 | -0.036621 | -0.30212 | 0.068665 | 0.26092 | 122.3694 | 122.8546 | 122.644 | 122.6898 | 122.6349 | 122.7493 | 122.7356 | -0.30212 | 122.6898 | 122.6349 | 122.7356 | 122.644 | 122.7493 | -0.3067 | -122.9828
2387.4062 | 122.7722 | -122.5067 | 0.10529 | -0.012589 | 0.016103 | 0.011551 | 0.015842 | -0.0043857 | -0.0059365 | 0.011865 | 0.041199 | 0.16479 | -0.20142 | 0.13275 | 0.022888 | 0.086975 | 0.022888 | 0.22888 | 0.23346 | -122.9004 | 122.3053 | 0.059509 | 122.5479 | 122.6395 | -0.082398 | -0.39368 | 0.12817 | 0.24262 | 122.5296 | 122.7356 | 122.5296 | 122.6715 | 122.5479 | 122.7402 | 122.5937 | -0.39368 | 122.6715 | 122.5479 | 122.5937 | 122.5296 | 122.7402 | -0.3067 | -123.0057
2389.1094 | 122.7814 | -122.5113 | 0.10071 | 0.0026703 | 0.017598 | 0.012405 | 0.019687 | -0.0016087 | -0.0055093 | 0.012506 | 0.027466 | 0.19226 | -0.21057 | 0.11902 | 0 | 0.086975 | -0.027466 | 0.19226 | 0.2243 | -122.8409 | 122.3007 | 0.091553 | 122.5388 | 122.6303 | -0.10071 | -0.32959 | 0.1236 | 0.23804 | 122.4838 | 122.7036 | 122.5113 | 122.7036 | 122.5388 | 122.7356 | 122.5983 | -0.32959 | 122.7036 | 122.5388 | 122.5983 | 122.5113 | 122.7356 | -0.31128 | -122.9416
2390.875 | 122.7676 | -122.5296 | 0.09613 | 0.017929 | 0.019734 | 0.0083463 | 0.018192 | -0.0033175 | -0.0046549 | 0.011865 | 0.050354 | 0.16022 | -0.20599 | 0.16479 | 0.045776 | 0.10529 | -0.018311 | 0.24719 | 0.23804 | -122.8775 | 122.3236 | 0.064087 | 122.58 | 122.6944 | -0.050354 | -0.3479 | 0.14191 | 0.25635 | 122.5113 | 122.7768 | 122.5754 | 122.6898 | 122.58 | 122.7676 | 122.6349 | -0.3479 | 122.6898 | 122.58 | 122.6349 | 122.5754 | 122.7676 | -0.30212 | -122.9736
2392.6406 | 122.8134 | -122.5204 | 0.10071 | -0.0049592 | 0.014821 | 0.012619 | 0.017124 | -0.0016087 | -0.0044413 | 0.010156 | -0.004578 | 0.19226 | -0.21973 | 0.10071 | 0.004578 | 0.091553 | -0.073242 | 0.1831 | 0.21973 | -122.8592 | 122.3007 | 0.091553 | 122.5159 | 122.6212 | -0.09613 | -0.33874 | 0.11902 | 0.21515 | 122.4472 | 122.7036 | 122.525 | 122.7127 | 122.5159 | 122.7402 | 122.612 | -0.33874 | 122.7127 | 122.5159 | 122.612 | 122.525 | 122.7402 | -0.32044 | -122.9599
2394.4062 | 122.6578 | -122.5296 | 0.11444 | -0.0049592 | 0.020589 | 0.0083463 | 0.010074 | -0.0037449 | -0.0035867 | 0.0084468 | 0.11902 | 0.16022 | -0.17395 | 0.21515 | 0.12817 | 0.20599 | -0.1236 | 0.3479 | 0.19684 | -122.8821 | 122.3557 | 0.045776 | 122.6486 | 122.7448 | 0.013733 | -0.35248 | 0.082397 | 0.29297 | 122.406 | 122.8775 | 122.6578 | 122.6898 | 122.6486 | 122.7264 | 122.7356 | -0.35248 | 122.6898 | 122.6486 | 122.7356 | 122.6578 | 122.7264 | -0.28839 | -122.9965
2396.1094 | 122.6898 | -122.5616 | 0.11902 | 0.0026703 | 0.015889 | 0.011978 | 0.01691 | -0.0028903 | -0.0048685 | 0.011437 | 0.10529 | 0.13733 | -0.17395 | 0.19226 | 0.10986 | 0.19684 | -0.18768 | 0.30212 | 0.19226 | -122.8638 | 122.3877 | 0.01831 | 122.6669 | 122.7539 | -0.009156 | -0.30212 | 0.073242 | 0.27924 | 122.374 | 122.8638 | 122.6715 | 122.699 | 122.6669 | 122.7539 | 122.7585 | -0.30212 | 122.699 | 122.6669 | 122.7585 | 122.6715 | 122.7539 | -0.29297 | -122.9828
2397.875 | 122.7859 | -122.5159 | 0.10529 | -0.012589 | 0.016744 | 0.0092007 | 0.014347 | -0.0037449 | -0.0059365 | 0.010583 | 0.027466 | 0.16022 | -0.20599 | 0.11902 | 0.009155 | 0.073242 | 0.022888 | 0.22888 | 0.23346 | -122.9141 | 122.3099 | 0.054931 | 122.5433 | 122.6349 | -0.096131 | -0.39826 | 0.12817 | 0.23346 | 122.5388 | 122.7448 | 122.525 | 122.6761 | 122.5433 | 122.7493 | 122.5891 | -0.39826 | 122.6761 | 122.5433 | 122.5891 | 122.525 | 122.7493 | -0.31128 | -123.0194
2399.5781 | 122.7356 | -122.5388 | 0.11444 | -0.0049592 | 0.019521 | 0.0077053 | 0.013065 | -0.0033175 | -0.0038003 | 0.0093012 | 0.036621 | 0.14648 | -0.17853 | 0.14191 | 0.059509 | 0.14648 | -0.091553 | 0.25177 | 0.20142 | -122.8912 | 122.3602 | 0.032043 | 122.5754 | 122.6807 | -0.054932 | -0.35248 | 0.086975 | 0.21515 | 122.4472 | 122.7905 | 122.5983 | 122.6852 | 122.5754 | 122.7402 | 122.6852 | -0.35248 | 122.6852 | 122.5754 | 122.6852 | 122.5983 | 122.7402 | -0.29297 | -123.0057
2401.3438 | 122.8226 | -122.5067 | 0.091553 | -0.0049592 | 0.01888 | 0.0098417 | 0.017978 | -0.0035313 | -0.0040139 | 0.010583 | 0.004578 | 0.1831 | -0.2243 | 0.09613 | -0.004578 | 0.059509 | 0.050354 | 0.20142 | 0.23346 | -122.9233 | 122.2824 | 0.091552 | 122.5113 | 122.6028 | -0.096131 | -0.41656 | 0.14191 | 0.22888 | 122.5571 | 122.7081 | 122.5021 | 122.6898 | 122.5113 | 122.7402 | 122.5662 | -0.41656 | 122.6898 | 122.5113 | 122.5662 | 122.5021 | 122.7402 | -0.31586 | -123.0148
2403.0938 | 122.7997 | -122.5296 | 0.10071 | 0.0026703 | 0.018453 | 0.011337 | 0.018406 | -0.0020359 | -0.0052957 | 0.013146 | 0.045776 | 0.17853 | -0.20142 | 0.1236 | 0.009155 | 0.054932 | -0.018311 | 0.18768 | 0.2243 | -122.85 | 122.3282 | 0.07782 | 122.5754 | 122.6532 | -0.091553 | -0.32044 | 0.1236 | 0.24719 | 122.5113 | 122.7173 | 122.5388 | 122.7081 | 122.5754 | 122.7539 | 122.5845 | -0.32044 | 122.7081 | 122.5754 | 122.5845 | 122.5388 | 122.7539 | -0.30212 | -122.9507
2404.9531 | 122.7539 | -122.5616 | 0.11902 | 0.0103 | 0.011617 | 0.0077053 | 0.011143 | -0.0028903 | -0.0046549 | 0.011224 | 0.009155 | 0.13733 | -0.19684 | 0.14191 | 0.086975 | 0.15106 | -0.09613 | 0.25177 | 0.21057 | -122.8729 | 122.3648 | 0.01831 | 122.5708 | 122.7036 | -0.032044 | -0.31128 | 0.091552 | 0.20599 | 122.4655 | 122.8134 | 122.6486 | 122.699 | 122.5708 | 122.7722 | 122.7127 | -0.31128 | 122.699 | 122.5708 | 122.7127 | 122.6486 | 122.7722 | -0.31586 | -122.9919
2407.1719 | 122.8134 | -122.525 | 0.091553 | -0.012589 | 0.017812 | 0.0094143 | 0.015415 | -0.0045993 | -0.0070047 | 0.0095148 | -0.009155 | 0.18768 | -0.23346 | 0.10071 | 0.009155 | 0.064087 | 0.054932 | 0.21515 | 0.22888 | -122.905 | 122.2916 | 0.09613 | 122.5159 | 122.6257 | -0.082398 | -0.37994 | 0.13733 | 0.2243 | 122.58 | 122.7402 | 122.5342 | 122.7127 | 122.5159 | 122.7539 | 122.5891 | -0.37994 | 122.7127 | 122.5159 | 122.5891 | 122.5342 | 122.7539 | -0.32501 | -122.9965
2409.8125 | 122.8592 | -122.5067 | 0.11444 | 0.0103 | 0.019307 | 0.011978 | 0.018406 | -0.0037449 | -0.0061503 | 0.01336 | -0.004578 | 0.17395 | -0.21973 | 0.091553 | -0.013733 | 0.059509 | -0.009155 | 0.13733 | 0.24261 | -122.9141 | 122.287 | 0.059509 | 122.5021 | 122.5983 | -0.12817 | -0.40741 | 0.12817 | 0.21515 | 122.4976 | 122.644 | 122.493 | 122.6807 | 122.5021 | 122.7493 | 122.5662 | -0.40741 | 122.6807 | 122.5021 | 122.5662 | 122.493 | 122.7493 | -0.33417 | -123.0286
2412.8906 | 122.7585 | -122.5662 | 0.11444 | -0.012589 | 0.015462 | 0.011551 | 0.012211 | -0.0031039 | -0.0040139 | 0.010369 | 0.036621 | 0.15564 | -0.17853 | 0.16937 | 0.068665 | 0.16022 | -0.09613 | 0.2655 | 0.20599 | -122.9004 | 122.3877 | 0.041199 | 122.6028 | 122.7356 | -0.045776 | -0.33417 | 0.091553 | 0.21515 | 122.4701 | 122.8317 | 122.6349 | 122.7219 | 122.6028 | 122.7722 | 122.7264 | -0.33417 | 122.7219 | 122.6028 | 122.7264 | 122.6349 | 122.7722 | -0.29297 | -123.0148
2414.6875 | 122.7173 | -122.5708 | 0.13275 | -0.0049592 | 0.016957 | 0.0057827 | 0.015629 | -0.0045993 | -0.0072183 | 0.0084468 | 0.09613 | 0.12817 | -0.16937 | 0.21515 | 0.1236 | 0.17395 | -0.10071 | 0.32959 | 0.20142 | -122.8867 | 122.4014 | -0.004577 | 122.6669 | 122.7859 | -0.009155 | -0.31586 | 0.068665 | 0.2655 | 122.4701 | 122.9004 | 122.6944 | 122.699 | 122.6669 | 122.7722 | 122.7448 | -0.31586 | 122.699 | 122.6669 | 122.7448 | 122.6944 | 122.7722 | -0.30212 | -123.0194
2416.4844 | 122.731 | -122.5708 | 0.11902 | 0.0026703 | 0.015889 | 0.012405 | 0.015201 | -0.0054539 | -0.0085001 | 0.011865 | 0.091553 | 0.13275 | -0.18768 | 0.19684 | 0.10529 | 0.16022 | -0.050354 | 0.31586 | 0.21057 | -122.9233 | 122.3831 | 0.013732 | 122.6624 | 122.7676 | -0.013733 | -0.35248 | 0.091552 | 0.27924 | 122.5204 | 122.8867 | 122.6761 | 122.7036 | 122.6624 | 122.7814 | 122.731 | -0.35248 | 122.7036 | 122.6624 | 122.731 | 122.6761 | 122.7814 | -0.3067 | -123.0423
2418.25 | 122.7676 | -122.5571 | 0.11902 | 0.0026703 | 0.017171 | 0.0089871 | 0.014347 | -0.0039585 | -0.0044413 | 0.010369 | 0.054932 | 0.14648 | -0.16937 | 0.16479 | 0.064087 | 0.15106 | -0.10071 | 0.2655 | 0.20142 | -122.8912 | 122.3877 | 0.027465 | 122.612 | 122.7219 | -0.054932 | -0.33417 | 0.082397 | 0.22431 | 122.4564 | 122.8226 | 122.6212 | 122.7036 | 122.612 | 122.7585 | 122.7081 | -0.33417 | 122.7036 | 122.612 | 122.7081 | 122.6212 | 122.7585 | -0.28839 | -123.0103
2420.0312 | 122.7036 | -122.5708 | 0.13275 | 0.0026703 | 0.016103 | 0.01091 | 0.014988 | -0.0022495 | -0.0072183 | 0.008874 | 0.11444 | 0.13733 | -0.17853 | 0.23346 | 0.12817 | 0.20142 | -0.15564 | 0.34332 | 0.21057 | -122.8867 | 122.3923 | 0.004578 | 122.6852 | 122.8043 | -0.004577 | -0.31586 | 0.07782 | 0.29297 | 122.4152 | 122.9141 | 122.699 | 122.7081 | 122.6852 | 122.7814 | 122.7722 | -0.31586 | 122.7081 | 122.6852 | 122.7722 | 122.699 | 122.7814 | -0.31128 | -123.0194
2421.7188 | 122.699 | -122.5845 | 0.12817 | 0.0103 | 0.014821 | 0.010269 | 0.015842 | -0.0069491 | -0.0061503 | 0.011224 | 0.11444 | 0.13733 | -0.1831 | 0.23346 | 0.12817 | 0.20599 | -0.13733 | 0.3479 | 0.18768 | -122.8729 | 122.4014 | 0.009155 | 122.699 | 122.818 | 0 | -0.28839 | 0.059509 | 0.29755 | 122.4472 | 122.9324 | 122.7127 | 122.7219 | 122.699 | 122.7722 | 122.7905 | -0.28839 | 122.7219 | 122.699 | 122.7905 | 122.7127 | 122.7722 | -0.31128 | -123.0011
2423.4688 | 122.731 | -122.5845 | 0.12817 | 0.0103 | 0.015462 | 0.012405 | 0.01926 | -0.00054047 | -0.0082865 | 0.011651 | 0.09613 | 0.14648 | -0.17853 | 0.21515 | 0.10529 | 0.19684 | -0.17853 | 0.29755 | 0.19684 | -122.8683 | 122.406 | 0.01831 | 122.6807 | 122.7997 | -0.022888 | -0.28381 | 0.068664 | 0.27466 | 122.406 | 122.8821 | 122.6898 | 122.731 | 122.6807 | 122.7814 | 122.7814 | -0.28381 | 122.731 | 122.6807 | 122.7814 | 122.6898 | 122.7814 | -0.3067 | -122.9965
2425.25 | 122.8592 | -122.5433 | 0.086975 | 0.0103 | 0.01653 | 0.011337 | 0.020969 | -0.0013949 | -0.0052957 | 0.008874 | 0.004578 | 0.1831 | -0.21057 | 0.091553 | -0.013733 | 0.054932 | 0 | 0.16022 | 0.25177 | -122.9324 | 122.3328 | 0.09613 | 122.5479 | 122.6349 | -0.10071 | -0.3891 | 0.16479 | 0.21515 | 122.5433 | 122.7036 | 122.5296 | 122.7264 | 122.5479 | 122.7951 | 122.5983 | -0.3891 | 122.7264 | 122.5479 | 122.5983 | 122.5296 | 122.7951 | -0.29755 | -123.0194
2427.0156 | 122.7951 | -122.5708 | 0.10986 | -0.0049592 | 0.016744 | 0.01091 | 0.020756 | 0.00095493 | -0.0072183 | 0.010797 | 0.068665 | 0.18768 | -0.21057 | 0.16022 | 0.041199 | 0.10071 | -0.036621 | 0.23346 | 0.22888 | -122.8912 | 122.3602 | 0.07782 | 122.6395 | 122.731 | -0.068664 | -0.32043 | 0.11902 | 0.27924 | 122.5342 | 122.8043 | 122.612 | 122.7585 | 122.6395 | 122.7997 | 122.6715 | -0.32043 | 122.7585 | 122.6395 | 122.6715 | 122.612 | 122.7997 | -0.32043 | -123.0011
2428.7031 | 122.8455 | -122.58 | 0.082397 | 0.0026703 | 0.018666 | 0.0186 | 0.016697 | 0.00010033 | -0.0050821 | 0.012292 | 0.027466 | 0.16937 | -0.21973 | 0.11444 | 0.009155 | 0.086975 | -0.013733 | 0.17853 | 0.2243 | -122.9279 | 122.3602 | 0.086976 | 122.6074 | 122.6944 | -0.073242 | -0.3479 | 0.14191 | 0.24719 | 122.5662 | 122.7585 | 122.5891 | 122.7493 | 122.6074 | 122.8043 | 122.6669 | -0.3479 | 122.7493 | 122.6074 | 122.6669 | 122.5891 | 122.8043 | -0.30212 | -123.0103
2430.4531 | 122.7081 | -122.5891 | 0.14191 | 0.0026703 | 0.016744 | 0.0098417 | 0.010715 | -0.0041721 | -0.0055093 | 0.011865 | 0.10529 | 0.16022 | -0.17853 | 0.2243 | 0.16022 | 0.21515 | -0.14648 | 0.35248 | 0.20599 | -122.8912 | 122.4106 | 0.01831 | 122.6944 | 122.8134 | 0.01831 | -0.30212 | 0.064087 | 0.28381 | 122.4426 | 122.9416 | 122.7493 | 122.7493 | 122.6944 | 122.7951 | 122.8043 | -0.30212 | 122.7493 | 122.6944 | 122.8043 | 122.7493 | 122.7951 | -0.32044 | -123.0331
2432.2344 | 122.6944 | -122.6028 | 0.11444 | -0.0049592 | 0.013753 | 0.012405 | 0.012851 | -0.0022495 | -0.0046549 | 0.0097284 | 0.09613 | 0.14191 | -0.17395 | 0.22888 | 0.13275 | 0.21057 | -0.13733 | 0.36163 | 0.19226 | -122.9324 | 122.4289 | 0.027466 | 122.699 | 122.8317 | 0.01831 | -0.32959 | 0.07782 | 0.27008 | 122.4655 | 122.9645 | 122.7356 | 122.7448 | 122.699 | 122.7951 | 122.8134 | -0.32959 | 122.7448 | 122.699 | 122.8134 | 122.7356 | 122.7951 | -0.28839 | -123.0469
2434 | 122.7081 | -122.6028 | 0.11902 | 0.0026703 | 0.017812 | 0.0087735 | 0.015201 | -0.0054539 | -0.0046549 | 0.01101 | 0.10071 | 0.15564 | -0.16937 | 0.21973 | 0.12817 | 0.20142 | -0.13275 | 0.36163 | 0.20142 | -122.937 | 122.4335 | 0.036621 | 122.7036 | 122.8226 | 0.009155 | -0.33417 | 0.082397 | 0.27008 | 122.4701 | 122.9645 | 122.731 | 122.7585 | 122.7036 | 122.8043 | 122.8043 | -0.33417 | 122.7585 | 122.7036 | 122.8043 | 122.731 | 122.8043 | -0.28839 | -123.056
2435.7031 | 122.7997 | -122.5983 | 0.10071 | -0.0049592 | 0.017171 | 0.0079189 | 0.019901 | -0.0035313 | -0.0038003 | 0.011437 | 0.036621 | 0.15564 | -0.21515 | 0.1831 | 0.054932 | 0.14191 | -0.15106 | 0.25177 | 0.20599 | -122.9004 | 122.3831 | 0.054932 | 122.6349 | 122.7814 | -0.045776 | -0.30212 | 0.10529 | 0.25177 | 122.4472 | 122.85 | 122.6532 | 122.7539 | 122.6349 | 122.8043 | 122.7402 | -0.30212 | 122.7539 | 122.6349 | 122.7402 | 122.6532 | 122.8043 | -0.31586 | -123.0011
2437.4688 | 122.8271 | -122.5754 | 0.073242 | -0.0049592 | 0.017385 | 0.011123 | 0.019687 | -0.0018223 | -0.0082865 | 0.011224 | 0.064087 | 0.17853 | -0.21973 | 0.16479 | 0.054932 | 0.11444 | -0.027466 | 0.25635 | 0.21973 | -122.905 | 122.3557 | 0.10529 | 122.6395 | 122.7402 | -0.01831 | -0.32959 | 0.14649 | 0.28381 | 122.5479 | 122.8317 | 122.6303 | 122.7539 | 122.6395 | 122.7951 | 122.6898 | -0.32959 | 122.7539 | 122.6395 | 122.6898 | 122.6303 | 122.7951 | -0.29297 | -122.9782
2439.2344 | 122.7585 | -122.6074 | 0.11902 | -0.012589 | 0.017171 | 0.0092007 | 0.011356 | -0.0041721 | -0.0048685 | 0.011437 | 0.091553 | 0.13733 | -0.17853 | 0.20142 | 0.10071 | 0.17853 | -0.073242 | 0.33417 | 0.20599 | -122.9279 | 122.4289 | 0.01831 | 122.699 | 122.8088 | -0.018311 | -0.32043 | 0.086975 | 0.27008 | 122.5342 | 122.9416 | 122.7081 | 122.7448 | 122.699 | 122.8134 | 122.7859 | -0.32043 | 122.7448 | 122.699 | 122.7859 | 122.7081 | 122.8134 | -0.29755 | -123.0469
2440.9219 | 122.8729 | -122.5708 | 0.091553 | -0.0049592 | 0.019521 | 0.010483 | 0.019901 | -0.0037449 | -0.0044413 | 0.011651 | 0.036621 | 0.19684 | -0.21973 | 0.091553 | -0.018311 | 0.050354 | -0.004578 | 0.16937 | 0.23804 | -122.9507 | 122.3511 | 0.10529 | 122.6074 | 122.6624 | -0.10986 | -0.37994 | 0.14648 | 0.25635 | 122.5662 | 122.7402 | 122.5525 | 122.7676 | 122.6074 | 122.8088 | 122.6212 | -0.37994 | 122.7676 | 122.6074 | 122.6212 | 122.5525 | 122.8088 | -0.31128 | -123.0423
2442.6719 | 122.7585 | -122.5891 | 0.1236 | 0.0026703 | 0.015462 | 0.010696 | 0.013065 | -0.0018223 | -0.0057229 | 0.012078 | 0.07782 | 0.1236 | -0.16479 | 0.19684 | 0.10529 | 0.20142 | -0.17853 | 0.29297 | 0.19226 | -122.8729 | 122.4243 | 0 | 122.6669 | 122.7859 | -0.01831 | -0.28381 | 0.068665 | 0.24261 | 122.4106 | 122.8821 | 122.6944 | 122.7127 | 122.6669 | 122.7814 | 122.7905 | -0.28381 | 122.7127 | 122.6669 | 122.7905 | 122.6944 | 122.7814 | -0.28839 | -122.9965
2444.4531 | 122.8409 | -122.5845 | 0.10071 | -0.0049592 | 0.016957 | 0.013687 | 0.01926 | -0.0022495 | -0.0046549 | 0.011437 | 0.022888 | 0.19684 | -0.21057 | 0.13275 | 0.013733 | 0.10071 | -0.091553 | 0.21057 | 0.20599 | -122.9233 | 122.374 | 0.09613 | 122.6074 | 122.7173 | -0.086975 | -0.33874 | 0.10529 | 0.23346 | 122.493 | 122.7951 | 122.5983 | 122.7814 | 122.6074 | 122.7905 | 122.6852 | -0.33874 | 122.7814 | 122.6074 | 122.6852 | 122.5983 | 122.7905 | -0.31128 | -123.024
2446.2344 | 122.8134 | -122.5937 | 0.091553 | 0.0103 | 0.019094 | 0.010483 | 0.01691 | -0.00096767 | -0.0089273 | 0.011651 | 0.068665 | 0.15564 | -0.21515 | 0.15564 | 0.041199 | 0.10986 | -0.032043 | 0.2243 | 0.23346 | -122.9279 | 122.3785 | 0.064087 | 122.6624 | 122.7493 | -0.050354 | -0.33417 | 0.14191 | 0.28381 | 122.5616 | 122.818 | 122.6349 | 122.7493 | 122.6624 | 122.8271 | 122.7036 | -0.33417 | 122.7493 | 122.6624 | 122.7036 | 122.6349 | 122.8271 | -0.3067 | -123.0194
2447.9375 | 122.7997 | -122.5937 | 0.11444 | 0.0026703 | 0.016317 | 0.013473 | 0.011997 | -0.0022495 | -0.0048685 | 0.011651 | 0.032043 | 0.16022 | -0.17395 | 0.15106 | 0.068665 | 0.14648 | -0.086975 | 0.24261 | 0.20599 | -122.9507 | 122.4197 | 0.045776 | 122.6257 | 122.7448 | -0.045776 | -0.35706 | 0.091553 | 0.20599 | 122.5067 | 122.8363 | 122.6624 | 122.7539 | 122.6257 | 122.7997 | 122.7402 | -0.35706 | 122.7539 | 122.6257 | 122.7402 | 122.6624 | 122.7997 | -0.28839 | -123.0652
2449.625 | 122.818 | -122.5754 | 0.10529 | -0.020218 | 0.014394 | 0.0083463 | 0.015842 | -0.0024631 | -0.0063639 | 0.0097284 | 0.050354 | 0.16479 | -0.17395 | 0.14648 | 0.045776 | 0.10071 | -0.009155 | 0.25635 | 0.23346 | -122.9279 | 122.4014 | 0.059509 | 122.6257 | 122.7219 | -0.05951 | -0.35248 | 0.12817 | 0.2243 | 122.5662 | 122.8317 | 122.6212 | 122.7402 | 122.6257 | 122.8088 | 122.6761 | -0.35248 | 122.7402 | 122.6257 | 122.6761 | 122.6212 | 122.8088 | -0.27924 | -123.0331
2451.3906 | 122.8592 | -122.5845 | 0.10986 | 0.0026703 | 0.01888 | 0.011978 | 0.019474 | -0.00096767 | -0.0055093 | 0.012078 | 0.018311 | 0.17395 | -0.21057 | 0.11444 | 0.022888 | 0.10986 | -0.10529 | 0.21057 | 0.23804 | -122.9233 | 122.374 | 0.064087 | 122.6028 | 122.699 | -0.086975 | -0.33874 | 0.12817 | 0.22888 | 122.4792 | 122.7951 | 122.6074 | 122.7585 | 122.6028 | 122.8226 | 122.6944 | -0.33874 | 122.7585 | 122.6028 | 122.6944 | 122.6074 | 122.8226 | -0.32043 | -123.0331
2453.1562 | 122.8363 | -122.6074 | 0.10529 | -0.0049592 | 0.018239 | 0.011978 | 0.019474 | -0.00075407 | -0.0061503 | 0.011865 | 0.050354 | 0.16937 | -0.19684 | 0.16022 | 0.041199 | 0.11444 | -0.022888 | 0.24719 | 0.23346 | -122.9507 | 122.4106 | 0.064087 | 122.6578 | 122.7676 | -0.064087 | -0.34332 | 0.12817 | 0.24719 | 122.5845 | 122.8546 | 122.6486 | 122.7768 | 122.6578 | 122.8409 | 122.7219 | -0.34332 | 122.7768 | 122.6578 | 122.7219 | 122.6486 | 122.8409 | -0.30212 | -123.056
2454.8438 | 122.8409 | -122.5754 | 0.10071 | 0.0026703 | 0.019307 | 0.012192 | 0.017978 | -0.0035313 | -0.0050821 | 0.012078 | 0.050354 | 0.16937 | -0.20142 | 0.16479 | 0.045776 | 0.1236 | -0.032043 | 0.23346 | 0.21973 | -122.9645 | 122.374 | 0.068665 | 122.6257 | 122.7402 | -0.054932 | -0.3891 | 0.11902 | 0.25177 | 122.5433 | 122.8088 | 122.6212 | 122.7448 | 122.6257 | 122.7951 | 122.699 | -0.3891 | 122.7448 | 122.6257 | 122.699 | 122.6212 | 122.7951 | -0.30212 | -123.0652
2456.5469 | 122.8455 | -122.5845 | 0.10071 | 0.0026703 | 0.015889 | 0.012192 | 0.012424 | -0.0050265 | -0.0048685 | 0.010369 | 0.027466 | 0.19226 | -0.19684 | 0.10529 | 0.027466 | 0.082397 | 0.022888 | 0.21973 | 0.21973 | -122.9965 | 122.3877 | 0.091553 | 122.612 | 122.6898 | -0.073242 | -0.41199 | 0.11902 | 0.2243 | 122.6074 | 122.8043 | 122.612 | 122.7768 | 122.612 | 122.8043 | 122.6669 | -0.41199 | 122.7768 | 122.612 | 122.6669 | 122.612 | 122.8043 | -0.29755 | -123.0972
2458.3125 | 122.7676 | -122.6303 | 0.10986 | 0.0026703 | 0.015035 | 0.010055 | 0.012851 | -0.00054047 | -0.0059365 | 0.012078 | 0.10071 | 0.13733 | -0.15564 | 0.18768 | 0.10071 | 0.19226 | -0.17395 | 0.30212 | 0.17853 | -122.9233 | 122.4747 | 0.027466 | 122.731 | 122.818 | -0.009155 | -0.29297 | 0.068665 | 0.25635 | 122.4564 | 122.9324 | 122.731 | 122.7676 | 122.731 | 122.8088 | 122.8226 | -0.29297 | 122.7676 | 122.731 | 122.8226 | 122.731 | 122.8088 | -0.2655 | -123.0331
2460 | 122.7585 | -122.612 | 0.1236 | 0.0026703 | 0.015676 | 0.017105 | 0.015629 | -0.0043857 | -0.0050821 | 0.011224 | 0.091553 | 0.15564 | -0.16479 | 0.2243 | 0.10071 | 0.16937 | -0.07782 | 0.33875 | 0.20142 | -122.9187 | 122.4472 | 0.032044 | 122.7036 | 122.8363 | -0.022888 | -0.3067 | 0.07782 | 0.25635 | 122.5342 | 122.9507 | 122.7127 | 122.7676 | 122.7036 | 122.8134 | 122.7814 | -0.3067 | 122.7676 | 122.7036 | 122.7814 | 122.7127 | 122.8134 | -0.28839 | -123.0423
2461.6875 | 122.7493 | -122.612 | 0.11444 | -0.0049592 | 0.014394 | 0.010483 | 0.014347 | -0.0022495 | -0.0052957 | 0.011651 | 0.10529 | 0.13275 | -0.1831 | 0.23346 | 0.12817 | 0.20142 | -0.13275 | 0.36163 | 0.20142 | -122.9462 | 122.4289 | 0.01831 | 122.7173 | 122.8455 | 0.013733 | -0.33417 | 0.086975 | 0.28839 | 122.4792 | 122.9736 | 122.7402 | 122.7448 | 122.7173 | 122.8134 | 122.8134 | -0.33417 | 122.7448 | 122.7173 | 122.8134 | 122.7402 | 122.8134 | -0.29755 | -123.0606
2463.4531 | 122.8088 | -122.6028 | 0.12817 | 0.0026703 | 0.017171 | 0.011978 | 0.01392 | -0.0018223 | -0.0063639 | 0.01101 | 0.068665 | 0.16479 | -0.17853 | 0.15564 | 0.059509 | 0.14648 | -0.13275 | 0.2655 | 0.20142 | -122.9645 | 122.4243 | 0.036621 | 122.6715 | 122.7585 | -0.068665 | -0.36163 | 0.073242 | 0.24719 | 122.4701 | 122.8683 | 122.6624 | 122.7676 | 122.6715 | 122.8043 | 122.7493 | -0.36163 | 122.7676 | 122.6715 | 122.7493 | 122.6624 | 122.8043 | -0.3067 | -123.0927
2465.1719 | 122.7814 | -122.6303 | 0.13275 | 0.0026703 | 0.017812 | 0.0089871 | 0.015415 | -0.0024631 | -0.0052957 | 0.010369 | 0.09613 | 0.13275 | -0.17395 | 0.19684 | 0.091553 | 0.17395 | -0.16479 | 0.3067 | 0.19684 | -122.9416 | 122.4564 | 0 | 122.7264 | 122.8271 | -0.041198 | -0.31128 | 0.064087 | 0.27008 | 122.4655 | 122.937 | 122.7219 | 122.7631 | 122.7264 | 122.8271 | 122.8043 | -0.31128 | 122.7631 | 122.7264 | 122.8043 | 122.7219 | 122.8271 | -0.3067 | -123.0743
2466.9531 | 122.7585 | -122.6532 | 0.13733 | 0.0026703 | 0.012471 | 0.014114 | 0.018619 | -0.0018223 | -0.0078591 | 0.011865 | 0.10529 | 0.11902 | -0.17395 | 0.21515 | 0.11444 | 0.19684 | -0.19684 | 0.31128 | 0.20599 | -122.905 | 122.4792 | -0.01831 | 122.7585 | 122.8683 | -0.022888 | -0.25177 | 0.068665 | 0.27924 | 122.4564 | 122.9645 | 122.7676 | 122.7722 | 122.7585 | 122.8592 | 122.85 | -0.25177 | 122.7722 | 122.7585 | 122.85 | 122.7676 | 122.8592 | -0.31128 | -123.0423
2468.7031 | 122.8088 | -122.6212 | 0.11444 | 0.0026703 | 0.015676 | 0.0085599 | 0.014133 | -0.0045993 | -0.0052957 | 0.010369 | 0.059509 | 0.14191 | -0.17395 | 0.18768 | 0.091553 | 0.17853 | -0.1236 | 0.31128 | 0.18768 | -122.9187 | 122.4472 | 0.027466 | 122.6807 | 122.8088 | -0.022888 | -0.29755 | 0.073242 | 0.23346 | 122.4976 | 122.9324 | 122.7127 | 122.7631 | 122.6807 | 122.8088 | 122.7997 | -0.29755 | 122.7631 | 122.6807 | 122.7997 | 122.7127 | 122.8088 | -0.28839 | -123.0331
2470.4844 | 122.8134 | -122.6212 | 0.11444 | 0.0026703 | 0.018453 | 0.0081327 | 0.017124 | -0.0026767 | -0.0067911 | 0.0095148 | 0.082397 | 0.14648 | -0.17395 | 0.19684 | 0.068665 | 0.13275 | -0.032043 | 0.27924 | 0.21057 | -122.9965 | 122.4472 | 0.032043 | 122.7036 | 122.818 | -0.045776 | -0.37537 | 0.09613 | 0.25635 | 122.5891 | 122.9004 | 122.6898 | 122.7676 | 122.7036 | 122.8317 | 122.7539 | -0.37537 | 122.7676 | 122.7036 | 122.7539 | 122.6898 | 122.8317 | -0.28839 | -123.111
2472.2656 | 122.818 | -122.6486 | 0.1236 | 0.0026703 | 0.019307 | 0.015823 | 0.012638 | -0.0028903 | -0.0038003 | 0.01101 | 0.073242 | 0.13275 | -0.17853 | 0.17853 | 0.068665 | 0.14191 | -0.13275 | 0.2655 | 0.19684 | -122.9507 | 122.4701 | 0.009155 | 122.7219 | 122.8271 | -0.054931 | -0.30212 | 0.073242 | 0.25177 | 122.5159 | 122.9141 | 122.7173 | 122.7814 | 122.7219 | 122.8455 | 122.7905 | -0.30212 | 122.7814 | 122.7219 | 122.7905 | 122.7173 | 122.8455 | -0.30212 | -123.0743
2473.9688 | 122.8729 | -122.5983 | 0.09613 | 0.0026703 | 0.018453 | 0.012619 | 0.020969 | -0.0020359 | -0.0065775 | 0.012719 | 0.059509 | 0.16937 | -0.21057 | 0.17853 | 0.041199 | 0.10986 | -0.027466 | 0.23804 | 0.23346 | -122.9782 | 122.3877 | 0.073243 | 122.6578 | 122.7768 | -0.054931 | -0.37994 | 0.13733 | 0.27008 | 122.5708 | 122.8363 | 122.6395 | 122.7676 | 122.6578 | 122.8317 | 122.7081 | -0.37994 | 122.7676 | 122.6578 | 122.7081 | 122.6395 | 122.8317 | -0.3067 | -123.0743
2475.7188 | 122.7859 | -122.6624 | 0.1236 | -0.0049592 | 0.014608 | 0.013473 | 0.015415 | -0.0020359 | -0.0055093 | 0.012078 | 0.10986 | 0.1236 | -0.17395 | 0.21057 | 0.10986 | 0.19226 | -0.18768 | 0.31586 | 0.1831 | -122.9416 | 122.4884 | 0 | 122.7722 | 122.8729 | -0.013733 | -0.27923 | 0.059509 | 0.28381 | 122.4747 | 122.9782 | 122.7722 | 122.7859 | 122.7722 | 122.8455 | 122.8546 | -0.27923 | 122.7859 | 122.7722 | 122.8546 | 122.7722 | 122.8455 | -0.29755 | -123.0652
2477.5 | 122.8134 | -122.6486 | 0.12817 | 0.0026703 | 0.018666 | 0.011337 | 0.018406 | -0.0022495 | -0.0067911 | 0.011437 | 0.07782 | 0.14648 | -0.17853 | 0.20142 | 0.086975 | 0.1831 | -0.16937 | 0.28839 | 0.19226 | -122.9782 | 122.4701 | 0.01831 | 122.7264 | 122.85 | -0.041199 | -0.32959 | 0.064087 | 0.25635 | 122.4792 | 122.937 | 122.7356 | 122.7951 | 122.7264 | 122.8409 | 122.8317 | -0.32959 | 122.7951 | 122.7264 | 122.8317 | 122.7356 | 122.8409 | -0.3067 | -123.1064
2479.2031 | 122.8363 | -122.612 | 0.10529 | 0.0026703 | 0.013326 | 0.015182 | 0.01392 | -0.0035313 | -0.0055093 | 0.01101 | 0.073242 | 0.15106 | -0.17395 | 0.17395 | 0.068665 | 0.1236 | -0.027466 | 0.27466 | 0.20599 | -122.9874 | 122.438 | 0.045776 | 122.6852 | 122.7859 | -0.036621 | -0.37537 | 0.10071 | 0.24719 | 122.5845 | 122.8867 | 122.6807 | 122.7631 | 122.6852 | 122.818 | 122.7356 | -0.37537 | 122.7631 | 122.6852 | 122.7356 | 122.6807 | 122.818 | -0.27924 | -123.0927
2480.9844 | 122.7768 | -122.6807 | 0.1236 | -0.012589 | 0.01888 | 0.01326 | 0.018406 | -0.0024631 | -0.0052957 | 0.012078 | 0.10529 | 0.16479 | -0.19226 | 0.21515 | 0.10986 | 0.19684 | -0.19226 | 0.29297 | 0.19684 | -122.9691 | 122.4884 | 0.041199 | 122.7859 | 122.8958 | -0.013733 | -0.28839 | 0.073242 | 0.29755 | 122.4884 | 122.9736 | 122.7905 | 122.8455 | 122.7859 | 122.8775 | 122.8775 | -0.28839 | 122.8455 | 122.7859 | 122.8775 | 122.7905 | 122.8775 | -0.31586 | -123.0927
2482.75 | 122.8683 | -122.6166 | 0.10986 | 0.0026703 | 0.018239 | 0.011551 | 0.017551 | -0.00096767 | -0.0085001 | 0.010797 | 0.036621 | 0.15564 | -0.20599 | 0.17853 | 0.064087 | 0.13275 | -0.1236 | 0.24719 | 0.21057 | -122.9553 | 122.4106 | 0.045777 | 122.6532 | 122.7951 | -0.045776 | -0.33874 | 0.10071 | 0.24262 | 122.493 | 122.8638 | 122.6807 | 122.7722 | 122.6532 | 122.8271 | 122.7493 | -0.33874 | 122.7722 | 122.6532 | 122.7493 | 122.6807 | 122.8271 | -0.31586 | -123.0652
2484.5 | 122.9416 | -122.612 | 0.073242 | 0.0026703 | 0.015889 | 0.010269 | 0.018406 | -0.0031039 | -0.0029459 | 0.0095148 | -0.004578 | 0.17853 | -0.23346 | 0.086975 | -0.022888 | 0.032043 | 0.009155 | 0.16479 | 0.23804 | -122.9782 | 122.3785 | 0.10529 | 122.6074 | 122.699 | -0.09613 | -0.36621 | 0.16479 | 0.22888 | 122.6212 | 122.7768 | 122.5891 | 122.7905 | 122.6074 | 122.85 | 122.644 | -0.36621 | 122.7905 | 122.6074 | 122.644 | 122.5891 | 122.85 | -0.3067 | -123.0515
2486.2031 | 122.7814 | -122.644 | 0.11902 | -0.0049592 | 0.015676 | 0.016037 | 0.012424 | -0.0043857 | -0.0059365 | 0.012292 | 0.11444 | 0.1236 | -0.19226 | 0.21973 | 0.1236 | 0.19684 | -0.13733 | 0.35248 | 0.20599 | -122.9828 | 122.4518 | 0.004577 | 122.7585 | 122.8638 | 0.004577 | -0.33875 | 0.086975 | 0.3067 | 122.5067 | 122.9965 | 122.7676 | 122.7676 | 122.7585 | 122.85 | 122.8409 | -0.33875 | 122.7676 | 122.7585 | 122.8409 | 122.7676 | 122.85 | -0.31128 | -123.1018
2487.9688 | 122.905 | -122.6257 | 0.10071 | 0.0026703 | 0.014821 | 0.0089871 | 0.02161 | -0.0022495 | -0.0061503 | 0.01101 | 0.032043 | 0.17853 | -0.2243 | 0.1236 | -0.004578 | 0.068665 | -0.013733 | 0.18768 | 0.23346 | -123.0057 | 122.4014 | 0.07782 | 122.6578 | 122.7493 | -0.10529 | -0.37994 | 0.13275 | 0.25635 | 122.612 | 122.8134 | 122.6212 | 122.8043 | 122.6578 | 122.8592 | 122.6944 | -0.37994 | 122.8043 | 122.6578 | 122.6944 | 122.6212 | 122.8592 | -0.32501 | -123.1064
2489.7188 | 122.8867 | -122.644 | 0.10071 | -0.0049592 | 0.017171 | 0.014328 | 0.017978 | -0.0024631 | -0.0057229 | 0.010156 | 0.036621 | 0.16937 | -0.2243 | 0.11902 | 0.013733 | 0.086975 | -0.009155 | 0.17853 | 0.23346 | -123.0011 | 122.4197 | 0.068665 | 122.6807 | 122.7631 | -0.086975 | -0.35706 | 0.13275 | 0.26093 | 122.6349 | 122.8226 | 122.6578 | 122.8134 | 122.6807 | 122.8775 | 122.731 | -0.35706 | 122.8134 | 122.6807 | 122.731 | 122.6578 | 122.8775 | -0.32501 | -123.1018
2491.4844 | 122.7905 | -122.6486 | 0.13275 | -0.012589 | 0.016744 | 0.011337 | 0.011143 | -0.0037449 | -0.0055093 | 0.011437 | 0.09613 | 0.13275 | -0.16937 | 0.23346 | 0.13275 | 0.19226 | -0.12817 | 0.36163 | 0.17853 | -122.9828 | 122.4792 | 0 | 122.7448 | 122.8821 | 0 | -0.33417 | 0.045777 | 0.2655 | 122.5204 | 123.0103 | 122.7814 | 122.7814 | 122.7448 | 122.8271 | 122.8409 | -0.33417 | 122.7814 | 122.7448 | 122.8409 | 122.7814 | 122.8271 | -0.30212 | -123.1155
2493.2656 | 122.8592 | -122.6578 | 0.09613 | 0.0026703 | 0.019734 | 0.013046 | 0.017124 | -0.00075407 | -0.0048685 | 0.011865 | 0.054932 | 0.14191 | -0.1831 | 0.17853 | 0.073242 | 0.15564 | -0.15564 | 0.27008 | 0.20142 | -123.0194 | 122.4747 | 0.045777 | 122.7127 | 122.8363 | -0.022888 | -0.36163 | 0.10529 | 0.23804 | 122.5021 | 122.9279 | 122.731 | 122.7997 | 122.7127 | 122.8592 | 122.8134 | -0.36163 | 122.7997 | 122.7127 | 122.8134 | 122.731 | 122.8592 | -0.27924 | -123.1155
2494.9688 | 122.9324 | -122.5983 | 0.082397 | 0.017929 | 0.017598 | 0.013901 | 0.018833 | -0.0031039 | -0.0061503 | 0.011224 | -0.004578 | 0.19226 | -0.21057 | 0.091553 | -0.018311 | 0.036621 | 0.022888 | 0.16022 | 0.22888 | -123.0011 | 122.3877 | 0.10986 | 122.5937 | 122.6898 | -0.10071 | -0.40283 | 0.14649 | 0.20599 | 122.6212 | 122.7585 | 122.58 | 122.7905 | 122.5937 | 122.8271 | 122.6349 | -0.40283 | 122.7905 | 122.5937 | 122.6349 | 122.58 | 122.8271 | -0.29297 | -123.0835
2496.7188 | 122.8088 | -122.6761 | 0.10529 | 0.0026703 | 0.017385 | 0.010696 | 0.014133 | -0.0033175 | -0.0059365 | 0.014642 | 0.09613 | 0.13275 | -0.16937 | 0.21057 | 0.11444 | 0.21057 | -0.19226 | 0.31586 | 0.18768 | -122.9416 | 122.5067 | 0.027465 | 122.7722 | 122.8867 | 0.009155 | -0.2655 | 0.082397 | 0.2655 | 122.4838 | 122.9919 | 122.7905 | 122.8088 | 122.7722 | 122.8638 | 122.8867 | -0.2655 | 122.8088 | 122.7722 | 122.8867 | 122.7905 | 122.8638 | -0.27466 | -123.0469
2498.4219 | 122.9187 | -122.6166 | 0.091553 | 0.0026703 | 0.017385 | 0.0074917 | 0.01456 | -0.00032687 | -0.0065775 | 0.012078 | -0.009155 | 0.17853 | -0.2243 | 0.11902 | 0.009155 | 0.054932 | 0.032043 | 0.21515 | 0.23804 | -122.9919 | 122.3923 | 0.086975 | 122.6074 | 122.7356 | -0.082398 | -0.37537 | 0.14648 | 0.21515 | 122.6486 | 122.8317 | 122.6257 | 122.7951 | 122.6074 | 122.8546 | 122.6715 | -0.37537 | 122.7951 | 122.6074 | 122.6715 | 122.6257 | 122.8546 | -0.31586 | -123.0835
2500.1875 | 122.7997 | -122.6578 | 0.12817 | 0.0026703 | 0.01653 | 0.0047147 | 0.01392 | -0.0013949 | -0.0050821 | 0.012078 | 0.091553 | 0.11902 | -0.15106 | 0.20142 | 0.091553 | 0.17395 | -0.17395 | 0.29755 | 0.1831 | -122.9919 | 122.5067 | -0.009155 | 122.7493 | 122.8592 | -0.036621 | -0.33417 | 0.054931 | 0.24261 | 122.4838 | 122.9553 | 122.7493 | 122.7768 | 122.7493 | 122.8409 | 122.8317 | -0.33417 | 122.7768 | 122.7493 | 122.8317 | 122.7493 | 122.8409 | -0.27924 | -123.1201
2501.8906 | 122.9233 | -122.6212 | 0.068665 | 0.0026703 | 0.018666 | 0.0098417 | 0.015842 | -0.0024631 | -0.0065775 | 0.012078 | -0.009155 | 0.18768 | -0.21515 | 0.10986 | -0.004578 | 0.054932 | 0.059509 | 0.21515 | 0.23346 | -123.0148 | 122.406 | 0.11902 | 122.612 | 122.731 | -0.073243 | -0.39368 | 0.16479 | 0.20599 | 122.6807 | 122.8363 | 122.6166 | 122.8088 | 122.612 | 122.8546 | 122.6761 | -0.39368 | 122.8088 | 122.612 | 122.6761 | 122.6166 | 122.8546 | -0.28381 | -123.0835
2503.6562 | 122.8592 | -122.644 | 0.10986 | 0.0026703 | 0.015889 | 0.0083463 | 0.012851 | -0.0028903 | -0.0044413 | 0.012292 | 0.045776 | 0.14191 | -0.19684 | 0.15564 | 0.068665 | 0.14648 | -0.10071 | 0.26093 | 0.19226 | -123.0194 | 122.4472 | 0.032044 | 122.6898 | 122.7997 | -0.041198 | -0.37537 | 0.082398 | 0.24261 | 122.5433 | 122.905 | 122.7127 | 122.7859 | 122.6898 | 122.8363 | 122.7905 | -0.37537 | 122.7859 | 122.6898 | 122.7905 | 122.7127 | 122.8363 | -0.3067 | -123.1293
2505.4375 | 122.905 | -122.6807 | 0.086975 | -0.0049592 | 0.017171 | 0.014328 | 0.020969 | -0.0045993 | -0.0097819 | 0.012292 | 0.073242 | 0.17853 | -0.18768 | 0.14191 | 0.027466 | 0.09613 | -0.036621 | 0.2243 | 0.21515 | -122.9874 | 122.493 | 0.091553 | 122.7539 | 122.8226 | -0.059509 | -0.3067 | 0.12817 | 0.26092 | 122.644 | 122.905 | 122.7081 | 122.8592 | 122.7539 | 122.8958 | 122.7768 | -0.3067 | 122.8592 | 122.7539 | 122.7768 | 122.7081 | 122.8958 | -0.27466 | -123.0743
2507.1406 | 122.8134 | -122.6761 | 0.11444 | -0.0049592 | 0.016957 | 0.01561 | 0.01456 | -0.0031039 | -0.0044413 | 0.012506 | 0.10986 | 0.11902 | -0.16479 | 0.21057 | 0.10071 | 0.19684 | -0.21515 | 0.29755 | 0.19226 | -122.9736 | 122.5113 | 0.004578 | 122.7859 | 122.8867 | -0.013733 | -0.29755 | 0.07782 | 0.27466 | 122.4609 | 122.9736 | 122.7768 | 122.7951 | 122.7859 | 122.8683 | 122.8729 | -0.29755 | 122.7951 | 122.7859 | 122.8729 | 122.7768 | 122.8683 | -0.27924 | -123.0881
2508.8906 | 122.9416 | -122.6257 | 0.09613 | -0.0049592 | 0.017171 | 0.01091 | 0.020328 | -0.0011813 | -0.0061503 | 0.011224 | 0.013733 | 0.19226 | -0.21057 | 0.091553 | -0.013733 | 0.050354 | 0.004578 | 0.16022 | 0.23804 | -123.0331 | 122.4152 | 0.096131 | 122.6395 | 122.7173 | -0.10986 | -0.40741 | 0.14191 | 0.2243 | 122.6303 | 122.7859 | 122.612 | 122.818 | 122.6395 | 122.8638 | 122.6761 | -0.40741 | 122.818 | 122.6395 | 122.6761 | 122.612 | 122.8638 | -0.3067 | -123.1293
2510.5781 | 122.9233 | -122.644 | 0.09613 | 0.0026703 | 0.015462 | 0.015182 | 0.01926 | -0.0013949 | -0.0072183 | 0.013787 | 0.018311 | 0.16937 | -0.21515 | 0.091553 | 0.004578 | 0.07782 | -0.009155 | 0.17853 | 0.23346 | -123.0194 | 122.4289 | 0.073243 | 122.6624 | 122.7356 | -0.091552 | -0.37537 | 0.13733 | 0.23346 | 122.6349 | 122.8226 | 122.6486 | 122.8134 | 122.6624 | 122.8775 | 122.7219 | -0.37537 | 122.8134 | 122.6624 | 122.7219 | 122.6486 | 122.8775 | -0.31128 | -123.1155
2512.3438 | 122.7905 | -122.6532 | 0.1236 | -0.0049592 | 0.017171 | 0.011123 | 0.010715 | -0.0037449 | -0.0059365 | 0.010369 | 0.10071 | 0.1236 | -0.16937 | 0.21973 | 0.12817 | 0.20142 | -0.13275 | 0.3479 | 0.17853 | -123.0103 | 122.4838 | 0 | 122.7539 | 122.8729 | 0.004578 | -0.35706 | 0.054932 | 0.27008 | 122.5204 | 123.0011 | 122.7814 | 122.7768 | 122.7539 | 122.8317 | 122.8546 | -0.35706 | 122.7768 | 122.7539 | 122.8546 | 122.7814 | 122.8317 | -0.29297 | -123.1339
2514.0938 | 122.7905 | -122.6807 | 0.13733 | -0.0049592 | 0.018453 | 0.010269 | 0.011143 | -0.0028903 | -0.0044413 | 0.010369 | 0.10529 | 0.13275 | -0.17853 | 0.2243 | 0.14648 | 0.21515 | -0.13733 | 0.3479 | 0.19226 | -123.0286 | 122.5021 | -0.004578 | 122.7859 | 122.905 | 0.009155 | -0.3479 | 0.054932 | 0.28381 | 122.5433 | 123.0286 | 122.8271 | 122.8134 | 122.7859 | 122.8729 | 122.8958 | -0.3479 | 122.8134 | 122.7859 | 122.8958 | 122.8271 | 122.8729 | -0.31586 | -123.1659
2515.8438 | 122.818 | -122.7081 | 0.1236 | 0.0103 | 0.016744 | 0.012619 | 0.016483 | -0.0011813 | -0.0065775 | 0.011651 | 0.10986 | 0.13733 | -0.17853 | 0.21515 | 0.10529 | 0.20142 | -0.19684 | 0.30212 | 0.18768 | -122.9736 | 122.5296 | 0.013733 | 122.818 | 122.9233 | -0.01831 | -0.2655 | 0.064087 | 0.28839 | 122.5113 | 123.0103 | 122.8134 | 122.8455 | 122.818 | 122.8958 | 122.9095 | -0.2655 | 122.8455 | 122.818 | 122.9095 | 122.8134 | 122.8958 | -0.30212 | -123.0972
2517.6094 | 122.8867 | -122.644 | 0.10529 | -0.0049592 | 0.016744 | 0.0096279 | 0.017338 | -0.0011813 | -0.0074319 | 0.014001 | 0.027466 | 0.16937 | -0.19684 | 0.14191 | 0.045776 | 0.13275 | -0.11444 | 0.25177 | 0.20142 | -123.0194 | 122.4472 | 0.064087 | 122.6715 | 122.7859 | -0.05951 | -0.37537 | 0.09613 | 0.2243 | 122.5296 | 122.8958 | 122.6898 | 122.8134 | 122.6715 | 122.8455 | 122.7768 | -0.37537 | 122.8134 | 122.6715 | 122.7768 | 122.6898 | 122.8455 | -0.30212 | -123.1247
2519.375 | 122.9416 | -122.6395 | 0.09613 | 0.0026703 | 0.015462 | 0.013901 | 0.014133 | -0.0041721 | -0.0065775 | 0.012933 | -0.009155 | 0.17395 | -0.19684 | 0.11902 | 0.004578 | 0.059509 | 0.045776 | 0.21515 | 0.24719 | -123.0057 | 122.4426 | 0.07782 | 122.6303 | 122.7585 | -0.091552 | -0.36621 | 0.15106 | 0.18768 | 122.6852 | 122.8546 | 122.644 | 122.8134 | 122.6303 | 122.8867 | 122.699 | -0.36621 | 122.8134 | 122.6303 | 122.699 | 122.644 | 122.8867 | -0.29297 | -123.1018
2521.1406 | 122.9141 | -122.6395 | 0.07782 | -0.0049592 | 0.016744 | 0.0085599 | 0.018833 | -0.0026767 | -0.0063639 | 0.0095148 | 0.004578 | 0.17853 | -0.2243 | 0.13275 | 0.022888 | 0.091553 | -0.004578 | 0.24719 | 0.21973 | -123.0194 | 122.4152 | 0.10071 | 122.644 | 122.7722 | -0.054932 | -0.37994 | 0.14191 | 0.22888 | 122.6349 | 122.8867 | 122.6624 | 122.818 | 122.644 | 122.8592 | 122.731 | -0.37994 | 122.818 | 122.644 | 122.731 | 122.6624 | 122.8592 | -0.30212 | -123.0972
2522.8438 | 122.8592 | -122.6807 | 0.1236 | -0.0049592 | 0.017812 | 0.0087735 | 0.010715 | -0.0024631 | -0.0074319 | 0.010369 | 0.054932 | 0.13733 | -0.17853 | 0.15106 | 0.068665 | 0.15106 | -0.091553 | 0.25635 | 0.21057 | -123.0331 | 122.5021 | 0.013733 | 122.7356 | 122.8317 | -0.054931 | -0.35248 | 0.086975 | 0.23346 | 122.5891 | 122.937 | 122.7493 | 122.818 | 122.7356 | 122.8912 | 122.8317 | -0.35248 | 122.818 | 122.7356 | 122.8317 | 122.7493 | 122.8912 | -0.30212 | -123.1567
2524.5938 | 122.8226 | -122.6852 | 0.12817 | 0.0026703 | 0.01653 | 0.014328 | 0.016269 | -0.0016087 | -0.0044413 | 0.01336 | 0.10529 | 0.13275 | -0.1831 | 0.20599 | 0.11444 | 0.19684 | -0.1831 | 0.32044 | 0.17853 | -122.9965 | 122.5021 | 0.004577 | 122.7905 | 122.8912 | -0.013733 | -0.31128 | 0.050354 | 0.28839 | 122.5021 | 123.0057 | 122.7997 | 122.818 | 122.7905 | 122.8638 | 122.8821 | -0.31128 | 122.818 | 122.7905 | 122.8821 | 122.7997 | 122.8638 | -0.31128 | -123.1247
2526.3594 | 122.9462 | -122.6349 | 0.07782 | 0.0026703 | 0.01653 | 0.011123 | 0.013492 | -0.0041721 | -0.0050821 | 0.010156 | -0.004578 | 0.1831 | -0.21057 | 0.10986 | 0.009155 | 0.059509 | 0.068665 | 0.20599 | 0.24261 | -123.0377 | 122.4243 | 0.10528 | 122.6303 | 122.7448 | -0.068665 | -0.40283 | 0.16479 | 0.20599 | 122.7036 | 122.8409 | 122.644 | 122.818 | 122.6303 | 122.8775 | 122.6944 | -0.40283 | 122.818 | 122.6303 | 122.6944 | 122.644 | 122.8775 | -0.28839 | -123.1155
2528.0625 | 122.8455 | -122.6944 | 0.12817 | -0.0049592 | 0.016744 | 0.0051419 | 0.011143 | -0.0033175 | -0.0063639 | 0.012933 | 0.073242 | 0.14191 | -0.16479 | 0.21057 | 0.11444 | 0.17853 | -0.13733 | 0.31586 | 0.18768 | -123.0286 | 122.5296 | 0.013733 | 122.7676 | 122.905 | -0.013733 | -0.33417 | 0.059509 | 0.23804 | 122.5571 | 123.0103 | 122.8088 | 122.8363 | 122.7676 | 122.8821 | 122.8729 | -0.33417 | 122.8363 | 122.7676 | 122.8729 | 122.8088 | 122.8821 | -0.29297 | -123.1567
2529.8125 | 122.8867 | -122.6944 | 0.11444 | 0.0026703 | 0.013326 | 0.010055 | 0.01456 | -0.0041721 | -0.0059365 | 0.010797 | 0.036621 | 0.15564 | -0.19226 | 0.16022 | 0.054932 | 0.13275 | -0.086975 | 0.26093 | 0.20599 | -123.0011 | 122.5021 | 0.041199 | 122.731 | 122.8546 | -0.059509 | -0.3067 | 0.091553 | 0.22888 | 122.6074 | 122.9553 | 122.7493 | 122.85 | 122.731 | 122.9004 | 122.8271 | -0.3067 | 122.85 | 122.731 | 122.8271 | 122.7493 | 122.9004 | -0.3067 | -123.1155
2531.5 | 122.9507 | -122.6715 | 0.068665 | 0.0026703 | 0.018025 | 0.0081327 | 0.018833 | -0.0024631 | -0.0044413 | 0.011651 | 0.013733 | 0.16479 | -0.21973 | 0.13733 | 0.004578 | 0.068665 | 0.036621 | 0.21973 | 0.24261 | -123.0331 | 122.4518 | 0.09613 | 122.6852 | 122.8088 | -0.064087 | -0.36163 | 0.17395 | 0.23346 | 122.7081 | 122.8912 | 122.6761 | 122.8363 | 122.6852 | 122.9141 | 122.7402 | -0.36163 | 122.8363 | 122.6852 | 122.7402 | 122.6761 | 122.9141 | -0.28839 | -123.1018
2533.25 | 122.937 | -122.6669 | 0.10529 | 0.0026703 | 0.014821 | 0.013901 | 0.021183 | 0.0026639 | -0.0089273 | 0.011651 | 0.032043 | 0.16937 | -0.20599 | 0.12817 | 0 | 0.082397 | -0.018311 | 0.19684 | 0.21515 | -122.9919 | 122.4609 | 0.064087 | 122.699 | 122.7951 | -0.10529 | -0.32501 | 0.10986 | 0.23804 | 122.6486 | 122.8638 | 122.6669 | 122.8363 | 122.699 | 122.8821 | 122.7493 | -0.32501 | 122.8363 | 122.699 | 122.7493 | 122.6669 | 122.8821 | -0.31128 | -123.0972
2535.0156 | 122.8363 | -122.7173 | 0.11902 | 0.0026703 | 0.018025 | 0.010055 | 0.01456 | -0.00054047 | -0.0070047 | 0.01101 | 0.10529 | 0.14648 | -0.16022 | 0.2243 | 0.11444 | 0.19226 | -0.21973 | 0.29297 | 0.18768 | -123.0377 | 122.5571 | 0.027465 | 122.8226 | 122.9416 | -0.004578 | -0.32043 | 0.068664 | 0.2655 | 122.4976 | 123.0103 | 122.8317 | 122.8638 | 122.8226 | 122.905 | 122.9095 | -0.32043 | 122.8638 | 122.8226 | 122.9095 | 122.8317 | 122.905 | -0.27924 | -123.1567
2536.7812 | 122.9599 | -122.6349 | 0.086975 | 0.0103 | 0.019948 | 0.011551 | 0.01691 | -0.00075407 | -0.0033731 | 0.011865 | 0.004578 | 0.20142 | -0.21515 | 0.11444 | 0.009155 | 0.050354 | 0.041199 | 0.21057 | 0.23804 | -123.0652 | 122.4197 | 0.11444 | 122.6395 | 122.7493 | -0.07782 | -0.4303 | 0.15106 | 0.21973 | 122.6761 | 122.8455 | 122.644 | 122.8363 | 122.6395 | 122.8729 | 122.6852 | -0.4303 | 122.8363 | 122.6395 | 122.6852 | 122.644 | 122.8729 | -0.30212 | -123.1522
2538.5469 | 122.8271 | -122.6807 | 0.13275 | -0.0049592 | 0.016103 | 0.01091 | 0.011143 | -0.0024631 | -0.0038003 | 0.012506 | 0.07782 | 0.14191 | -0.1831 | 0.20599 | 0.13275 | 0.19226 | -0.14648 | 0.3479 | 0.19226 | -123.0515 | 122.4976 | 0.009156 | 122.7585 | 122.8867 | 0 | -0.37079 | 0.05951 | 0.26092 | 122.5342 | 123.0286 | 122.8134 | 122.8226 | 122.7585 | 122.8729 | 122.8729 | -0.37079 | 122.8226 | 122.7585 | 122.8729 | 122.8134 | 122.8729 | -0.31586 | -123.1842
2540.2344 | 122.9599 | -122.6669 | 0.082397 | 0.0026703 | 0.018025 | 0.014755 | 0.017978 | -0.00032687 | -0.0059365 | 0.013574 | 0.004578 | 0.15564 | -0.21057 | 0.1236 | 0.022888 | 0.11444 | -0.091553 | 0.18768 | 0.21057 | -123.0377 | 122.4564 | 0.073243 | 122.6715 | 122.7905 | -0.059509 | -0.37079 | 0.12817 | 0.21515 | 122.5754 | 122.8546 | 122.6898 | 122.8226 | 122.6715 | 122.8775 | 122.7814 | -0.37079 | 122.8226 | 122.6715 | 122.7814 | 122.6898 | 122.8775 | -0.29297 | -123.1201
2541.9844 | 122.9233 | -122.6669 | 0.10529 | -0.0049592 | 0.017385 | 0.0096279 | 0.017338 | -0.0013949 | -0.0065775 | 0.010797 | 0.027466 | 0.16479 | -0.21515 | 0.14648 | 0.041199 | 0.10071 | -0.018311 | 0.23804 | 0.21515 | -123.0194 | 122.4518 | 0.059509 | 122.6944 | 122.8134 | -0.064087 | -0.35248 | 0.10986 | 0.24261 | 122.6486 | 122.905 | 122.7081 | 122.8317 | 122.6944 | 122.8821 | 122.7676 | -0.35248 | 122.8317 | 122.6944 | 122.7676 | 122.7081 | 122.8821 | -0.32044 | -123.1247
2543.6719 | 122.9828 | -122.6807 | 0.086975 | -0.012589 | 0.017598 | 0.013046 | 0.020115 | 0.00074133 | -0.0061503 | 0.012506 | 0.009155 | 0.16937 | -0.2243 | 0.10986 | -0.018311 | 0.068665 | 0 | 0.16937 | 0.22888 | -123.024 | 122.4564 | 0.082398 | 122.6898 | 122.7905 | -0.10529 | -0.34332 | 0.14191 | 0.23346 | 122.6807 | 122.85 | 122.6624 | 122.85 | 122.6898 | 122.9095 | 122.7493 | -0.34332 | 122.85 | 122.6898 | 122.7493 | 122.6624 | 122.9095 | -0.31128 | -123.111
2545.4531 | 122.8363 | -122.6898 | 0.14191 | -0.012589 | 0.016103 | 0.0057827 | 0.0092199 | -0.0024631 | -0.0046549 | 0.012506 | 0.091553 | 0.13275 | -0.17853 | 0.2243 | 0.13275 | 0.20599 | -0.15564 | 0.36163 | 0.17853 | -123.0515 | 122.5113 | -0.009156 | 122.7814 | 122.9141 | -0.009156 | -0.36163 | 0.036621 | 0.27008 | 122.5342 | 123.0515 | 122.8226 | 122.8226 | 122.7814 | 122.8683 | 122.8958 | -0.36163 | 122.8226 | 122.7814 | 122.8958 | 122.8226 | 122.8683 | -0.32044 | -123.1934
2547.2188 | 122.9004 | -122.6807 | 0.10986 | -0.0049592 | 0.019307 | 0.010269 | 0.014133 | -0.0033175 | -0.0044413 | 0.0093012 | 0.07782 | 0.15106 | -0.18768 | 0.16479 | 0.054932 | 0.09613 | 0.009155 | 0.24719 | 0.23346 | -123.024 | 122.493 | 0.041199 | 122.7585 | 122.8455 | -0.054931 | -0.34332 | 0.1236 | 0.2655 | 122.6898 | 122.9279 | 122.7356 | 122.8317 | 122.7585 | 122.9141 | 122.7768 | -0.34332 | 122.8317 | 122.7585 | 122.7768 | 122.7356 | 122.9141 | -0.29755 | -123.1339
2548.9844 | 122.9874 | -122.6807 | 0.10071 | -0.0049592 | 0.017812 | 0.011764 | 0.018406 | -0.0022495 | -0.0082865 | 0.011437 | -0.009155 | 0.17395 | -0.21973 | 0.086975 | -0.009155 | 0.064087 | -0.013733 | 0.16479 | 0.25635 | -123.0377 | 122.4609 | 0.073242 | 122.6715 | 122.7676 | -0.10986 | -0.35706 | 0.15564 | 0.21057 | 122.6669 | 122.8455 | 122.6715 | 122.8546 | 122.6715 | 122.937 | 122.7448 | -0.35706 | 122.8546 | 122.6715 | 122.7448 | 122.6715 | 122.937 | -0.32044 | -123.1384
2550.6719 | 122.9599 | -122.6761 | 0.10071 | -0.0049592 | 0.019734 | 0.01326 | 0.017338 | -0.00096767 | -0.0057229 | 0.011224 | -0.004578 | 0.17853 | -0.21057 | 0.11444 | 0.013733 | 0.091553 | -0.073242 | 0.1831 | 0.22888 | -123.0652 | 122.4655 | 0.07782 | 122.6715 | 122.7905 | -0.086975 | -0.3891 | 0.12817 | 0.20599 | 122.6028 | 122.8592 | 122.6898 | 122.8546 | 122.6715 | 122.905 | 122.7676 | -0.3891 | 122.8546 | 122.6715 | 122.7676 | 122.6898 | 122.905 | -0.31128 | -123.1659
2552.4375 | 122.9187 | -122.6898 | 0.082397 | -0.0049592 | 0.015676 | 0.0081327 | 0.017765 | -0.00032687 | -0.0065775 | 0.012506 | 0.045776 | 0.15564 | -0.21515 | 0.15106 | 0.041199 | 0.11444 | -0.018311 | 0.2655 | 0.22888 | -123.0331 | 122.4747 | 0.073243 | 122.7356 | 122.8409 | -0.041198 | -0.34332 | 0.14649 | 0.26093 | 122.6715 | 122.9553 | 122.731 | 122.8455 | 122.7356 | 122.9187 | 122.8043 | -0.34332 | 122.8455 | 122.7356 | 122.8043 | 122.731 | 122.9187 | -0.29755 | -123.1155
2554.2188 | 122.8775 | -122.6898 | 0.10529 | -0.012589 | 0.017598 | 0.0079189 | 0.010074 | -0.0041721 | -0.0055093 | 0.011224 | 0.068665 | 0.15106 | -0.16022 | 0.19684 | 0.10529 | 0.19226 | -0.11902 | 0.31586 | 0.19226 | -123.0469 | 122.5296 | 0.045776 | 122.7585 | 122.8867 | 0 | -0.35706 | 0.086975 | 0.22888 | 122.5708 | 123.0057 | 122.7951 | 122.8409 | 122.7585 | 122.8821 | 122.8821 | -0.35706 | 122.8409 | 122.7585 | 122.8821 | 122.7951 | 122.8821 | -0.2655 | -123.1522
2555.9844 | 122.9233 | -122.6852 | 0.09613 | 0.0026703 | 0.018239 | 0.01326 | 0.01691 | -0.00075407 | -0.0074319 | 0.012506 | 0.068665 | 0.16937 | -0.19684 | 0.15564 | 0.050354 | 0.10986 | -0.032043 | 0.25177 | 0.23346 | -123.0286 | 122.4884 | 0.073243 | 122.7539 | 122.8409 | -0.045776 | -0.34332 | 0.13733 | 0.2655 | 122.6532 | 122.937 | 122.7356 | 122.8546 | 122.7539 | 122.9187 | 122.7951 | -0.34332 | 122.8546 | 122.7539 | 122.7951 | 122.7356 | 122.9187 | -0.29297 | -123.1247
2557.6719 | 122.8592 | -122.699 | 0.1236 | -0.0049592 | 0.020589 | 0.0074917 | 0.0096473 | -0.0039585 | -0.0050821 | 0.012933 | 0.086975 | 0.15564 | -0.17395 | 0.21057 | 0.12817 | 0.21057 | -0.13275 | 0.33417 | 0.19226 | -123.056 | 122.525 | 0.032044 | 122.7859 | 122.9095 | 0.004578 | -0.35706 | 0.068665 | 0.26092 | 122.5662 | 123.0331 | 122.8271 | 122.8546 | 122.7859 | 122.8912 | 122.9095 | -0.35706 | 122.8546 | 122.7859 | 122.9095 | 122.8271 | 122.8912 | -0.29755 | -123.1796
2559.4375 | 122.8958 | -122.7127 | 0.082397 | 0.0026703 | 0.018453 | 0.012192 | 0.013706 | -0.0041721 | -0.0042277 | 0.0086604 | 0.041199 | 0.15564 | -0.17853 | 0.15564 | 0.082397 | 0.15106 | -0.10529 | 0.27924 | 0.20599 | -123.0652 | 122.5342 | 0.073243 | 122.7539 | 122.8683 | 0 | -0.35248 | 0.1236 | 0.21973 | 122.6074 | 122.9919 | 122.7951 | 122.8683 | 122.7539 | 122.9187 | 122.8638 | -0.35248 | 122.8683 | 122.7539 | 122.8638 | 122.7951 | 122.9187 | -0.26092 | -123.1476
2561.1875 | 122.9416 | -122.7036 | 0.091553 | 0.0026703 | 0.017385 | 0.0081327 | 0.019474 | -0.00075407 | -0.0074319 | 0.012719 | 0.041199 | 0.15106 | -0.19226 | 0.15106 | 0.045776 | 0.13275 | -0.12817 | 0.24719 | 0.19684 | -123.0286 | 122.5113 | 0.059509 | 122.7448 | 122.8546 | -0.045777 | -0.32501 | 0.10529 | 0.23346 | 122.5754 | 122.9507 | 122.7493 | 122.8546 | 122.7448 | 122.9004 | 122.8363 | -0.32501 | 122.8546 | 122.7448 | 122.8363 | 122.7493 | 122.9004 | -0.28381 | -123.1201
2562.8906 | 122.9095 | -122.7173 | 0.11444 | 0.0026703 | 0.015462 | 0.012192 | 0.016269 | -0.0016087 | -0.0067911 | 0.011437 | 0.07782 | 0.12817 | -0.16937 | 0.18768 | 0.086975 | 0.17853 | -0.16479 | 0.28839 | 0.19684 | -123.024 | 122.5479 | 0.013733 | 122.7951 | 122.905 | -0.027466 | -0.3067 | 0.082397 | 0.24719 | 122.5525 | 123.0057 | 122.8043 | 122.8455 | 122.7951 | 122.9141 | 122.8958 | -0.3067 | 122.8455 | 122.7951 | 122.8958 | 122.8043 | 122.9141 | -0.28381 | -123.1384
2564.5781 | 122.905 | -122.6807 | 0.10529 | 0.0026703 | 0.016103 | 0.0074917 | 0.012211 | -0.0058811 | -0.0044413 | 0.010583 | 0.07782 | 0.14648 | -0.1831 | 0.14648 | 0.064087 | 0.10986 | -0.009155 | 0.25177 | 0.22888 | -123.1018 | 122.4976 | 0.041198 | 122.7585 | 122.8271 | -0.041199 | -0.42114 | 0.1236 | 0.26092 | 122.6715 | 122.9324 | 122.7448 | 122.8271 | 122.7585 | 122.9095 | 122.7905 | -0.42114 | 122.8271 | 122.7585 | 122.7905 | 122.7448 | 122.9095 | -0.28839 | -123.2071
2566.3438 | 122.9462 | -122.6715 | 0.059509 | 0.017929 | 0.015462 | 0.015396 | 0.018619 | -0.00054047 | -0.0055093 | 0.0095148 | 0.018311 | 0.16937 | -0.22888 | 0.15106 | 0.032043 | 0.10529 | -0.009155 | 0.23346 | 0.2243 | -123.0606 | 122.4426 | 0.10986 | 122.6898 | 122.8226 | -0.027466 | -0.3891 | 0.16479 | 0.24719 | 122.6624 | 122.905 | 122.7036 | 122.8409 | 122.6898 | 122.8958 | 122.7768 | -0.3891 | 122.8409 | 122.6898 | 122.7768 | 122.7036 | 122.8958 | -0.28839 | -123.1201
2568.125 | 122.8775 | -122.7127 | 0.1236 | 0.0026703 | 0.015462 | 0.0098417 | 0.012851 | -0.0039585 | -0.0048685 | 0.01101 | 0.082397 | 0.14648 | -0.19684 | 0.1831 | 0.082397 | 0.15564 | -0.045776 | 0.29297 | 0.20142 | -123.0652 | 122.5159 | 0.022888 | 122.7951 | 122.8958 | -0.041199 | -0.35248 | 0.07782 | 0.27924 | 122.6669 | 123.0057 | 122.7951 | 122.8592 | 122.7951 | 122.9141 | 122.8683 | -0.35248 | 122.8592 | 122.7951 | 122.8683 | 122.7951 | 122.9141 | -0.32043 | -123.1888
2569.8125 | 122.9507 | -122.6898 | 0.073242 | 0.0026703 | 0.01888 | 0.0092007 | 0.019901 | -0.0052401 | -0.0059365 | 0.0097284 | 0.032043 | 0.17853 | -0.22888 | 0.14191 | 0.032043 | 0.10529 | -0.004578 | 0.24261 | 0.21515 | -123.0789 | 122.4609 | 0.10529 | 122.7219 | 122.8317 | -0.041199 | -0.3891 | 0.14191 | 0.26093 | 122.6852 | 122.9324 | 122.7219 | 122.8683 | 122.7219 | 122.905 | 122.7951 | -0.3891 | 122.8683 | 122.7219 | 122.7951 | 122.7219 | 122.905 | -0.30212 | -123.1522
2571.5156 | 122.9965 | -122.6944 | 0.07782 | 0.0026703 | 0.01888 | 0.014969 | 0.018406 | -0.0020359 | -0.0050821 | 0.011865 | -0.018311 | 0.17853 | -0.21515 | 0.054932 | -0.027466 | 0.022888 | 0.013733 | 0.16937 | 0.2243 | -123.0789 | 122.4792 | 0.10071 | 122.6761 | 122.7493 | -0.10529 | -0.38452 | 0.14648 | 0.19684 | 122.7081 | 122.8638 | 122.6669 | 122.8729 | 122.6761 | 122.9187 | 122.7173 | -0.38452 | 122.8729 | 122.6761 | 122.7173 | 122.6669 | 122.9187 | -0.29297 | -123.1567
2573.2188 | 123.0057 | -122.6807 | 0.091553 | 0.0026703 | 0.019948 | 0.011123 | 0.016697 | -0.0013949 | -0.0050821 | 0.012719 | -0.013733 | 0.18768 | -0.20599 | 0.07782 | -0.013733 | 0.068665 | -0.009155 | 0.15106 | 0.21973 | -123.0972 | 122.4747 | 0.09613 | 122.6669 | 122.7585 | -0.10529 | -0.41657 | 0.12817 | 0.19226 | 122.6715 | 122.8317 | 122.6669 | 122.8683 | 122.6669 | 122.9004 | 122.7493 | -0.41657 | 122.8683 | 122.6669 | 122.7493 | 122.6669 | 122.9004 | -0.29755 | -123.1888
2574.9844 | 122.9874 | -122.6944 | 0.10071 | 0.0026703 | 0.017171 | 0.012192 | 0.016483 | -0.00096767 | -0.0052957 | 0.011437 | 0 | 0.18768 | -0.19226 | 0.086975 | -0.013733 | 0.082397 | -0.027466 | 0.17853 | 0.23346 | -123.0927 | 122.5021 | 0.086975 | 122.6944 | 122.7814 | -0.11444 | -0.39825 | 0.13275 | 0.19226 | 122.6669 | 122.8729 | 122.6807 | 122.8821 | 122.6944 | 122.9279 | 122.7768 | -0.39825 | 122.8821 | 122.6944 | 122.7768 | 122.6807 | 122.9279 | -0.29297 | -123.1934
2576.6719 | 122.9919 | -122.6944 | 0.09613 | 0.0026703 | 0.018239 | 0.0092007 | 0.010715 | -0.0048129 | -0.0055093 | 0.012292 | -0.027466 | 0.17395 | -0.21515 | 0.09613 | -0.004578 | 0.054932 | 0.073242 | 0.21057 | 0.24261 | -123.0789 | 122.4792 | 0.07782 | 122.6669 | 122.7905 | -0.10071 | -0.38452 | 0.14649 | 0.18768 | 122.7676 | 122.905 | 122.6898 | 122.8683 | 122.6669 | 122.937 | 122.7493 | -0.38452 | 122.8683 | 122.6669 | 122.7493 | 122.6898 | 122.937 | -0.31128 | -123.175
2578.4531 | 123.0103 | -122.6807 | 0.09613 | -0.0049592 | 0.016744 | 0.01091 | 0.018619 | -0.0020359 | -0.0042277 | 0.010156 | 0 | 0.16937 | -0.21515 | 0.086975 | -0.018311 | 0.059509 | 0 | 0.14648 | 0.22888 | -123.0789 | 122.4655 | 0.073243 | 122.6807 | 122.7676 | -0.11444 | -0.39825 | 0.13275 | 0.21515 | 122.6807 | 122.8271 | 122.6624 | 122.85 | 122.6807 | 122.9095 | 122.7402 | -0.39825 | 122.85 | 122.6807 | 122.7402 | 122.6624 | 122.9095 | -0.31128 | -123.175
2580.2188 | 122.9187 | -122.7539 | 0.10071 | 0.0026703 | 0.018025 | 0.0098417 | 0.0094337 | -0.0063083 | -0.0023049 | 0.011224 | 0.041199 | 0.14191 | -0.17853 | 0.13275 | 0.064087 | 0.14191 | -0.10529 | 0.26093 | 0.18768 | -123.0881 | 122.5754 | 0.041199 | 122.7951 | 122.8867 | -0.036621 | -0.33417 | 0.086975 | 0.21973 | 122.6486 | 123.0148 | 122.818 | 122.8958 | 122.7951 | 122.9416 | 122.8958 | -0.33417 | 122.8958 | 122.7951 | 122.8958 | 122.818 | 122.9416 | -0.27924 | -123.1888
2581.9062 | 122.9645 | -122.6669 | 0.091553 | -0.012589 | 0.015889 | 0.0092007 | 0.01392 | -0.0048129 | -0.0033731 | 0.011651 | 0 | 0.16937 | -0.21515 | 0.10071 | 0.004578 | 0.068665 | 0.032043 | 0.23346 | 0.23346 | -123.0927 | 122.4518 | 0.07782 | 122.6669 | 122.7676 | -0.086975 | -0.42572 | 0.14191 | 0.21515 | 122.699 | 122.9004 | 122.6715 | 122.8363 | 122.6669 | 122.9004 | 122.7356 | -0.42572 | 122.8363 | 122.6669 | 122.7356 | 122.6715 | 122.9004 | -0.3067 | -123.1842
2583.6719 | 122.8729 | -122.7127 | 0.14191 | -0.0049592 | 0.015889 | 0.010055 | 0.011997 | -0.0026767 | -0.0059365 | 0.012719 | 0.10986 | 0.13733 | -0.20142 | 0.21057 | 0.1236 | 0.20599 | -0.14648 | 0.35706 | 0.20142 | -123.0652 | 122.5113 | -0.004578 | 122.8226 | 122.9233 | -0.018311 | -0.35248 | 0.059509 | 0.31128 | 122.5662 | 123.0698 | 122.8363 | 122.85 | 122.8226 | 122.9141 | 122.9187 | -0.35248 | 122.85 | 122.8226 | 122.9187 | 122.8363 | 122.9141 | -0.34332 | -123.2071
2585.4531 | 122.9874 | -122.7264 | 0.07782 | -0.0049592 | 0.017598 | 0.0089871 | 0.014347 | -0.0020359 | -0.0063639 | 0.010797 | 0.022888 | 0.17395 | -0.22888 | 0.10529 | 0.013733 | 0.068665 | 0.036621 | 0.22888 | 0.24261 | -123.1247 | 122.4976 | 0.09613 | 122.7493 | 122.8317 | -0.064087 | -0.39826 | 0.16479 | 0.25177 | 122.7631 | 122.9553 | 122.7402 | 122.9004 | 122.7493 | 122.9691 | 122.7951 | -0.39826 | 122.9004 | 122.7493 | 122.7951 | 122.7402 | 122.9691 | -0.3067 | -123.2025
2587.2031 | 123.0194 | -122.7081 | 0.07782 | 0.0026703 | 0.016744 | 0.0083463 | 0.01926 | 0.00010033 | -0.0076455 | 0.013146 | -0.018311 | 0.17395 | -0.21973 | 0.086975 | -0.045776 | 0.045776 | -0.018311 | 0.17395 | 0.21057 | -123.0698 | 122.4884 | 0.09613 | 122.6898 | 122.7951 | -0.1236 | -0.36163 | 0.13275 | 0.20142 | 122.6898 | 122.8821 | 122.6624 | 122.8821 | 122.6898 | 122.9187 | 122.7539 | -0.36163 | 122.8821 | 122.6898 | 122.7539 | 122.6624 | 122.9187 | -0.29755 | -123.1476
2588.9688 | 123.0103 | -122.699 | 0.082397 | 0.0026703 | 0.018025 | 0.012192 | 0.014133 | -0.0037449 | -0.0055093 | 0.011437 | 0.004578 | 0.18768 | -0.21057 | 0.082397 | 0 | 0.068665 | 0.068665 | 0.20142 | 0.23346 | -123.1018 | 122.4884 | 0.10529 | 122.7036 | 122.7814 | -0.082397 | -0.40283 | 0.15106 | 0.21515 | 122.7676 | 122.9004 | 122.699 | 122.8867 | 122.7036 | 122.9324 | 122.7676 | -0.40283 | 122.8867 | 122.7036 | 122.7676 | 122.699 | 122.9324 | -0.29297 | -123.1842
2590.6562 | 122.8546 | -122.7127 | 0.10986 | -0.012589 | 0.015248 | 0.011337 | 0.011356 | -0.0043857 | -0.0038003 | 0.0090876 | 0.10529 | 0.11444 | -0.17395 | 0.21515 | 0.11444 | 0.20599 | -0.13275 | 0.35706 | 0.19226 | -123.0835 | 122.5388 | 0.004578 | 122.818 | 122.9279 | 0.004578 | -0.37079 | 0.082398 | 0.27924 | 122.58 | 123.0698 | 122.8271 | 122.8271 | 122.818 | 122.905 | 122.9187 | -0.37079 | 122.8271 | 122.818 | 122.9187 | 122.8271 | 122.905 | -0.28381 | -123.1934
2592.4375 | 122.9004 | -122.7219 | 0.10529 | -0.0049592 | 0.014821 | 0.010483 | 0.012211 | -0.0056675 | -0.0035867 | 0.013146 | 0.054932 | 0.16022 | -0.17395 | 0.17853 | 0.091553 | 0.18768 | -0.11902 | 0.31586 | 0.18768 | -123.0789 | 122.5479 | 0.054931 | 122.7768 | 122.9004 | -0.013733 | -0.35706 | 0.082397 | 0.22888 | 122.6028 | 123.0377 | 122.8134 | 122.8821 | 122.7768 | 122.9095 | 122.9095 | -0.35706 | 122.8821 | 122.7768 | 122.9095 | 122.8134 | 122.9095 | -0.27924 | -123.1842
2594.1562 | 122.2641 | -122.1588 | 0.11902 | -0.0049592 | 0.016103 | 0.011764 | 0.011143 | -0.00075407 | -0.0014505 | 0.013146 | 0.045776 | 0.13733 | -0.18768 | 0.13733 | 0.054932 | 0.13733 | -0.10071 | 0.25635 | 0.20599 | -122.4701 | 121.9711 | 0.01831 | 122.2046 | 122.2961 | -0.064087 | -0.31128 | 0.086975 | 0.23346 | 122.0581 | 122.4152 | 122.2137 | 122.2961 | 122.2046 | 122.3648 | 122.2961 | -0.31128 | 122.2961 | 122.2046 | 122.2961 | 122.2137 | 122.3648 | -0.3067 | -122.5891
2595.9219 | 122.3465 | -122.2275 | 0.10986 | 0.0103 | 0.015248 | 0.011337 | 0.0090063 | -0.00011327 | -0.0038003 | 0.0090876 | 0.091553 | 0.16022 | -0.17853 | 0.20142 | 0.086975 | 0.18768 | -0.13275 | 0.34332 | 0.19684 | -122.5296 | 122.049 | 0.050354 | 122.319 | 122.4289 | -0.022888 | -0.30212 | 0.086975 | 0.27008 | 122.0947 | 122.5708 | 122.3145 | 122.3877 | 122.319 | 122.4243 | 122.4152 | -0.30212 | 122.3877 | 122.319 | 122.4152 | 122.3145 | 122.4243 | -0.28839 | -122.6395
2597.625 | 122.5479 | -122.3236 | 0.091553 | 0.017929 | 0.018666 | 0.01091 | 0.019047 | -0.00054047 | -0.0059365 | 0.01101 | 0.050354 | 0.16479 | -0.20599 | 0.16479 | 0.013733 | 0.10529 | -0.018311 | 0.24261 | 0.2243 | -122.6486 | 122.1176 | 0.073242 | 122.374 | 122.4884 | -0.07782 | -0.32501 | 0.13275 | 0.25635 | 122.3053 | 122.5662 | 122.3373 | 122.4884 | 122.374 | 122.5479 | 122.4289 | -0.32501 | 122.4884 | 122.374 | 122.4289 | 122.3373 | 122.5479 | -0.29755 | -122.7402
2599.4062 | 122.5571 | -122.3648 | 0.10529 | -0.0049592 | 0.017171 | 0.0092007 | 0.010715 | -0.0039585 | -0.0038003 | 0.012078 | 0.050354 | 0.14191 | -0.1831 | 0.15564 | 0.064087 | 0.14191 | -0.10986 | 0.25635 | 0.20142 | -122.7081 | 122.1817 | 0.036621 | 122.4152 | 122.5204 | -0.041199 | -0.34332 | 0.09613 | 0.23346 | 122.2549 | 122.6212 | 122.4289 | 122.5067 | 122.4152 | 122.5662 | 122.5067 | -0.34332 | 122.5067 | 122.4152 | 122.5067 | 122.4289 | 122.5662 | -0.28839 | -122.8134
2601.0938 | 122.5708 | -122.3831 | 0.13275 | -0.0049592 | 0.017598 | 0.010269 | 0.013279 | -0.0020359 | -0.0042277 | 0.010797 | 0.036621 | 0.16022 | -0.17853 | 0.16937 | 0.07782 | 0.13275 | -0.11444 | 0.27924 | 0.20599 | -122.7585 | 122.2046 | 0.027466 | 122.4197 | 122.5525 | -0.054931 | -0.37537 | 0.073243 | 0.21515 | 122.2687 | 122.6624 | 122.4609 | 122.5433 | 122.4197 | 122.5891 | 122.5159 | -0.37537 | 122.5433 | 122.4197 | 122.5159 | 122.4609 | 122.5891 | -0.31128 | -122.8912
2602.8438 | 122.6074 | -122.4014 | 0.10986 | -0.012589 | 0.015889 | 0.011764 | 0.014988 | -0.0028903 | -0.0065775 | 0.012292 | 0.064087 | 0.15564 | -0.1831 | 0.17853 | 0.050354 | 0.11444 | -0.022888 | 0.27008 | 0.21515 | -122.731 | 122.2183 | 0.045777 | 122.4655 | 122.58 | -0.059509 | -0.32959 | 0.10529 | 0.24719 | 122.3785 | 122.6715 | 122.4518 | 122.5571 | 122.4655 | 122.6166 | 122.5159 | -0.32959 | 122.5571 | 122.4655 | 122.5159 | 122.4518 | 122.6166 | -0.29297 | -122.8409
2604.5469 | 122.6624 | -122.3969 | 0.10071 | -0.0049592 | 0.017171 | 0.010269 | 0.019901 | -0.00054047 | -0.0027323 | 0.010583 | 0.013733 | 0.16479 | -0.21057 | 0.1236 | 0.013733 | 0.073242 | -0.064087 | 0.17395 | 0.2243 | -122.7814 | 122.1863 | 0.064087 | 122.4106 | 122.5204 | -0.086975 | -0.38452 | 0.1236 | 0.2243 | 122.3328 | 122.5708 | 122.4106 | 122.5616 | 122.4106 | 122.6212 | 122.4701 | -0.38452 | 122.5616 | 122.4106 | 122.4701 | 122.4106 | 122.6212 | -0.31128 | -122.8821
2606.3125 | 122.5845 | -122.4243 | 0.1236 | -0.0049592 | 0.014821 | 0.014328 | 0.012211 | -0.0054539 | -0.0033731 | 0.012719 | 0.059509 | 0.15106 | -0.17853 | 0.21057 | 0.12817 | 0.17853 | -0.1236 | 0.32044 | 0.17853 | -122.7722 | 122.2458 | 0.027466 | 122.4838 | 122.6349 | 0.004578 | -0.3479 | 0.054932 | 0.23804 | 122.3007 | 122.7448 | 122.5525 | 122.5754 | 122.4838 | 122.6028 | 122.6028 | -0.3479 | 122.5754 | 122.4838 | 122.6028 | 122.5525 | 122.6028 | -0.30212 | -122.8958
2608.0156 | 122.7127 | -122.4152 | 0.082397 | 0.0103 | 0.015676 | 0.014541 | 0.022465 | -0.0020359 | -0.0078591 | 0.012078 | -0.004578 | 0.1831 | -0.21057 | 0.10529 | -0.022888 | 0.059509 | 0.004578 | 0.16479 | 0.21515 | -122.7905 | 122.2046 | 0.10071 | 122.4106 | 122.5204 | -0.10528 | -0.37537 | 0.13275 | 0.20599 | 122.4197 | 122.58 | 122.3923 | 122.5983 | 122.4106 | 122.6303 | 122.4747 | -0.37537 | 122.5983 | 122.4106 | 122.4747 | 122.3923 | 122.6303 | -0.29297 | -122.8729
2609.7656 | 122.6898 | -122.4335 | 0.09613 | -0.0049592 | 0.016957 | 0.012619 | 0.018833 | -0.0018223 | -0.0061503 | 0.013146 | 0.064087 | 0.17853 | -0.19226 | 0.16937 | 0.036621 | 0.09613 | -0.041199 | 0.25177 | 0.21057 | -122.8134 | 122.2412 | 0.082398 | 122.4976 | 122.6028 | -0.059509 | -0.37994 | 0.11444 | 0.25635 | 122.3923 | 122.6852 | 122.4701 | 122.612 | 122.4976 | 122.644 | 122.5296 | -0.37994 | 122.612 | 122.4976 | 122.5296 | 122.4701 | 122.644 | -0.28839 | -122.9095
2611.5312 | 122.6257 | -122.4609 | 0.11902 | -0.0049592 | 0.017171 | 0.010483 | 0.013065 | -0.0039585 | -0.0050821 | 0.012292 | 0.09613 | 0.13733 | -0.16479 | 0.21515 | 0.10071 | 0.16937 | -0.064087 | 0.32501 | 0.20142 | -122.8271 | 122.2961 | 0.01831 | 122.5571 | 122.6761 | -0.018311 | -0.36621 | 0.082397 | 0.26092 | 122.3969 | 122.7859 | 122.5616 | 122.5983 | 122.5571 | 122.6624 | 122.6303 | -0.36621 | 122.5983 | 122.5571 | 122.6303 | 122.5616 | 122.6624 | -0.28381 | -122.9462
2613.2969 | 122.6028 | -122.5204 | 0.12817 | -0.0049592 | 0.015889 | 0.012192 | 0.015201 | -0.0022495 | -0.0057229 | 0.013574 | 0.091553 | 0.13733 | -0.16479 | 0.21515 | 0.091553 | 0.21057 | -0.20142 | 0.30212 | 0.1831 | -122.7722 | 122.3557 | 0.009155 | 122.612 | 122.7356 | -0.036621 | -0.25177 | 0.054931 | 0.25635 | 122.319 | 122.8226 | 122.612 | 122.6578 | 122.612 | 122.7036 | 122.731 | -0.25177 | 122.6578 | 122.612 | 122.731 | 122.612 | 122.7036 | -0.29297 | -122.9004
2615.0156 | 122.6395 | -122.4976 | 0.10071 | 0.0103 | 0.016103 | 0.011764 | 0.013706 | -0.0035313 | -0.0050821 | 0.012506 | 0.091553 | 0.13275 | -0.17395 | 0.20142 | 0.10071 | 0.15564 | -0.064087 | 0.32959 | 0.21515 | -122.8043 | 122.3236 | 0.032043 | 122.5891 | 122.699 | 0 | -0.3067 | 0.11444 | 0.2655 | 122.4335 | 122.8271 | 122.5983 | 122.6303 | 122.5891 | 122.7127 | 122.6532 | -0.3067 | 122.6303 | 122.5891 | 122.6532 | 122.5983 | 122.7127 | -0.27466 | -122.905
2616.7656 | 122.6303 | -122.5113 | 0.13275 | -0.0049592 | 0.016957 | 0.012192 | 0.017338 | -0.0011813 | -0.0052957 | 0.013787 | 0.11444 | 0.13733 | -0.16479 | 0.21057 | 0.091553 | 0.21057 | -0.18768 | 0.31586 | 0.19684 | -122.7997 | 122.3465 | 0.004578 | 122.6257 | 122.7219 | -0.041198 | -0.28839 | 0.064087 | 0.27924 | 122.3236 | 122.8271 | 122.6028 | 122.6486 | 122.6257 | 122.7081 | 122.7219 | -0.28839 | 122.6486 | 122.6257 | 122.7219 | 122.6028 | 122.7081 | -0.29755 | -122.9324
2618.5469 | 122.7631 | -122.4518 | 0.09613 | 0.0026703 | 0.019094 | 0.017319 | 0.019687 | -0.0022495 | -0.0061503 | 0.014001 | -0.009155 | 0.16022 | -0.2243 | 0.091553 | -0.013733 | 0.07782 | -0.018311 | 0.16479 | 0.22888 | -122.8683 | 122.2275 | 0.064087 | 122.4426 | 122.5433 | -0.10986 | -0.41657 | 0.13275 | 0.21515 | 122.4335 | 122.6166 | 122.438 | 122.612 | 122.4426 | 122.6807 | 122.5296 | -0.41657 | 122.612 | 122.4426 | 122.5296 | 122.438 | 122.6807 | -0.32043 | -122.9645
2620.2656 | 122.7814 | -122.5021 | 0.082397 | -0.0049592 | 0.01888 | 0.011551 | 0.018192 | -0.0028903 | -0.0052957 | 0.011651 | -0.004578 | 0.1831 | -0.20599 | 0.082397 | -0.018311 | 0.050354 | 0.004578 | 0.14648 | 0.23804 | -122.8592 | 122.2961 | 0.10071 | 122.4976 | 122.5845 | -0.10071 | -0.35706 | 0.15564 | 0.20142 | 122.5067 | 122.6486 | 122.4838 | 122.6852 | 122.4976 | 122.7402 | 122.5525 | -0.35706 | 122.6852 | 122.4976 | 122.5525 | 122.4838 | 122.7402 | -0.28839 | -122.9416
2622.0312 | 122.6532 | -122.5204 | 0.10986 | 0.0026703 | 0.018453 | 0.0094143 | 0.012638 | -0.0065219 | -0.0050821 | 0.012933 | 0.10529 | 0.13733 | -0.16022 | 0.21515 | 0.12817 | 0.20142 | -0.1236 | 0.36621 | 0.19226 | -122.8958 | 122.3602 | 0.027466 | 122.6257 | 122.7356 | 0.018311 | -0.37537 | 0.082398 | 0.2655 | 122.3969 | 122.8867 | 122.6486 | 122.6578 | 122.6257 | 122.7127 | 122.7219 | -0.37537 | 122.6578 | 122.6257 | 122.7219 | 122.6486 | 122.7127 | -0.27008 | -123.0057
2623.7812 | 122.7859 | -122.4838 | 0.09613 | 0.0026703 | 0.017385 | 0.0096279 | 0.019687 | -0.0011813 | -0.0078591 | 0.011651 | -0.018311 | 0.17395 | -0.18768 | 0.082397 | -0.013733 | 0.054932 | -0.013733 | 0.15564 | 0.22888 | -122.8271 | 122.2961 | 0.07782 | 122.4655 | 122.5662 | -0.10986 | -0.34332 | 0.13275 | 0.16937 | 122.4701 | 122.6395 | 122.4701 | 122.6578 | 122.4655 | 122.7127 | 122.5388 | -0.34332 | 122.6578 | 122.4655 | 122.5388 | 122.4701 | 122.7127 | -0.28381 | -122.9233
2625.5 | 122.7905 | -122.4838 | 0.091553 | -0.0049592 | 0.019521 | 0.013046 | 0.016697 | -0.0018223 | -0.0050821 | 0.014215 | -0.009155 | 0.18768 | -0.20599 | 0.11902 | 0.004578 | 0.064087 | 0.036621 | 0.20142 | 0.24719 | -122.8729 | 122.2778 | 0.09613 | 122.4747 | 122.6028 | -0.086975 | -0.3891 | 0.15564 | 0.19684 | 122.5204 | 122.6852 | 122.4884 | 122.6715 | 122.4747 | 122.731 | 122.5479 | -0.3891 | 122.6715 | 122.4747 | 122.5479 | 122.4884 | 122.731 | -0.29755 | -122.9645
2627.25 | 122.7356 | -122.5021 | 0.10529 | 0.0103 | 0.017812 | 0.0096279 | 0.019474 | -0.0026767 | -0.0072183 | 0.015283 | 0.073242 | 0.14648 | -0.19226 | 0.15106 | 0.045776 | 0.11444 | -0.045776 | 0.23804 | 0.21057 | -122.8729 | 122.3099 | 0.041198 | 122.5754 | 122.6532 | -0.05951 | -0.37079 | 0.10529 | 0.2655 | 122.4564 | 122.7402 | 122.5479 | 122.6486 | 122.5754 | 122.7127 | 122.6166 | -0.37079 | 122.6486 | 122.5754 | 122.6166 | 122.5479 | 122.7127 | -0.29755 | -122.9782
2628.9531 | 122.7264 | -122.525 | 0.11902 | -0.0049592 | 0.016744 | 0.011551 | 0.010288 | -0.0013949 | -0.0035867 | 0.013787 | 0.050354 | 0.13275 | -0.16479 | 0.15564 | 0.073242 | 0.16479 | -0.11444 | 0.27466 | 0.18768 | -122.8958 | 122.3602 | 0.013732 | 122.5754 | 122.6807 | -0.045777 | -0.37079 | 0.068664 | 0.21515 | 122.4106 | 122.7997 | 122.5983 | 122.6578 | 122.5754 | 122.7127 | 122.6898 | -0.37079 | 122.6578 | 122.5754 | 122.6898 | 122.5983 | 122.7127 | -0.28381 | -123.0148
2630.7188 | 122.8134 | -122.493 | 0.082397 | 0.0026703 | 0.018239 | 0.0087735 | 0.018619 | -0.0022495 | -0.0035867 | 0.010369 | 0 | 0.17853 | -0.21515 | 0.091553 | 0 | 0.082397 | -0.032043 | 0.17853 | 0.23346 | -122.8638 | 122.2778 | 0.096131 | 122.493 | 122.5845 | -0.082397 | -0.37079 | 0.15106 | 0.21515 | 122.4609 | 122.6715 | 122.493 | 122.6715 | 122.493 | 122.7264 | 122.5754 | -0.37079 | 122.6715 | 122.493 | 122.5754 | 122.493 | 122.7264 | -0.29755 | -122.9462
2632.4844 | 122.6898 | -122.5113 | 0.11902 | -0.0049592 | 0.015462 | 0.0083463 | 0.013706 | -0.0039585 | -0.0027323 | 0.012933 | 0.07782 | 0.13733 | -0.17395 | 0.20599 | 0.09613 | 0.17395 | -0.082397 | 0.32959 | 0.19226 | -122.8775 | 122.3373 | 0.01831 | 122.5891 | 122.7173 | -0.022889 | -0.36621 | 0.073242 | 0.25177 | 122.4289 | 122.8409 | 122.6074 | 122.6486 | 122.5891 | 122.7036 | 122.6852 | -0.36621 | 122.6486 | 122.5891 | 122.6852 | 122.6074 | 122.7036 | -0.29297 | -122.9965
2634.2344 | 122.8271 | -122.5021 | 0.086975 | -0.0049592 | 0.01888 | 0.0087735 | 0.016483 | -0.0022495 | -0.0065775 | 0.012933 | 0 | 0.1831 | -0.21057 | 0.11444 | 0.004578 | 0.064087 | 0.054932 | 0.20599 | 0.21515 | -122.8821 | 122.2916 | 0.09613 | 122.5021 | 122.6166 | -0.082397 | -0.37994 | 0.12817 | 0.21057 | 122.5571 | 122.7081 | 122.5067 | 122.6852 | 122.5021 | 122.7173 | 122.5662 | -0.37994 | 122.6852 | 122.5021 | 122.5662 | 122.5067 | 122.7173 | -0.29755 | -122.9691
2635.9844 | 122.8043 | -122.4976 | 0.073242 | 0.0103 | 0.018666 | 0.010055 | 0.016269 | -0.0026767 | -0.0023049 | 0.01336 | -0.018311 | 0.19226 | -0.20142 | 0.10071 | 0.004578 | 0.059509 | 0.045776 | 0.20142 | 0.23346 | -122.9233 | 122.2961 | 0.11902 | 122.4792 | 122.5983 | -0.068664 | -0.42572 | 0.16022 | 0.18311 | 122.5433 | 122.699 | 122.5021 | 122.6898 | 122.4792 | 122.731 | 122.5571 | -0.42572 | 122.6898 | 122.4792 | 122.5571 | 122.5021 | 122.731 | -0.27466 | -122.9965
2637.7344 | 122.8134 | -122.5113 | 0.07782 | 0.0026703 | 0.013753 | 0.0087735 | 0.015842 | -0.0043857 | -0.0038003 | 0.014001 | -0.036621 | 0.17853 | -0.2243 | 0.09613 | 0.009155 | 0.059509 | 0.068665 | 0.21515 | 0.24719 | -122.9187 | 122.287 | 0.10071 | 122.4747 | 122.6074 | -0.068665 | -0.40741 | 0.16937 | 0.18768 | 122.58 | 122.7264 | 122.5204 | 122.6898 | 122.4747 | 122.7585 | 122.5708 | -0.40741 | 122.6898 | 122.4747 | 122.5708 | 122.5204 | 122.7585 | -0.30212 | -122.9965
2639.4375 | 122.7264 | -122.5571 | 0.10986 | 0.017929 | 0.016317 | 0.0064237 | 0.016269 | -0.0037449 | -0.0057229 | 0.011437 | 0.091553 | 0.13275 | -0.1831 | 0.19684 | 0.10529 | 0.16937 | -0.054932 | 0.32501 | 0.20599 | -122.9187 | 122.374 | 0.022888 | 122.6486 | 122.7539 | -0.004577 | -0.36163 | 0.096131 | 0.27466 | 122.5021 | 122.8821 | 122.6624 | 122.6898 | 122.6486 | 122.7631 | 122.7264 | -0.36163 | 122.6898 | 122.6486 | 122.7264 | 122.6624 | 122.7631 | -0.29297 | -123.0286
2641.1875 | 122.7356 | -122.5616 | 0.10071 | -0.0049592 | 0.016957 | 0.011978 | 0.01456 | -0.0035313 | -0.0044413 | 0.012719 | 0.068665 | 0.14191 | -0.17853 | 0.17395 | 0.09613 | 0.16937 | -0.10986 | 0.30212 | 0.20599 | -122.9141 | 122.3831 | 0.041199 | 122.6303 | 122.7356 | -0.004578 | -0.35248 | 0.10529 | 0.24719 | 122.4518 | 122.8638 | 122.6578 | 122.7036 | 122.6303 | 122.7676 | 122.731 | -0.35248 | 122.7036 | 122.6303 | 122.731 | 122.6578 | 122.7676 | -0.27924 | -123.0148

## Thermal Data
Fire Time | D Position - 3' | D Position - Middle | D Position - 7'
-0.8083 | 8.9801 | 8.8903 | 8.7706
0.1917 | 8.9824 | 8.9101 | 8.6704
1.1917 | 8.9871 | 8.8923 | 8.7554
2.1917 | 8.9876 | 8.9006 | 8.6466
3.1917 | 8.9842 | 8.892 | 8.7771
4.1917 | 8.9927 | 9.1181 | 8.7013
5.1917 | 8.9246 | 9.7293 | 8.6732
6.1917 | 9.3969 | 11.4504 | 10.8215
7.1917 | 11.241 | 12.1623 | 12.5965
8.1917 | 12.0694 | 13.7864 | 13.8884
9.1917 | 13.169 | 15.7478 | 14.9483
10.1917 | 14.6063 | 17.4639 | 16.1391
11.2073 | 15.8514 | 20.2518 | 17.8872
12.1917 | 16.978 | 23.137 | 19.4645
13.1917 | 18.2246 | 26.4006 | 21.5435
14.1917 | 20.0581 | 30.9676 | 22.9447
15.1917 | 22.2632 | 33.6456 | 23.7639
16.1917 | 24.0299 | 36.8677 | 24.9382
17.1917 | 25.2638 | 39.414 | 26.5563
18.1917 | 26.6451 | 42.6523 | 27.2002
19.1917 | 28.4203 | 45.4962 | 28.8222
20.1917 | 30.9098 | 48.2634 | 30.3932
21.1917 | 32.653 | 51.2442 | 32.0564
22.1917 | 34.3921 | 53.3712 | 33.8226
23.1917 | 35.7824 | 54.9264 | 35.4952
24.1917 | 38.1943 | 57.9454 | 37.6733
25.1917 | 40.843 | 62.1353 | 40.0453
26.1917 | 42.0897 | 65.104 | 42.3061
27.1917 | 44.9757 | 68.7381 | 44.1135
28.1917 | 47.9028 | 72.7206 | 46.6029
29.1917 | 50.1968 | 77.6192 | 50.2151
30.1917 | 52.7918 | 81.6344 | 53.7105
31.1917 | 54.744 | 84.4922 | 56.5614
32.1917 | 56.3035 | 88.0779 | 59.1174
33.1917 | 57.7393 | 91.6721 | 61.349
34.1917 | 60.1591 | 94.1967 | 64.0523
35.1917 | 60.6883 | 96.5079 | 65.6132
36.1917 | 61.3881 | 98.576 | 67.6505
37.1917 | 61.8915 | 100.9796 | 69.3839
38.1917 | 62.7837 | 102.6784 | 70.7959
39.1917 | 64.6343 | 105.0114 | 72.5878
40.1917 | 66.7528 | 107.0789 | 74.1051
41.2073 | 67.5869 | 108.5021 | 75.7625
42.1917 | 70.6668 | 110.0312 | 77.2893
43.1917 | 73.3156 | 111.7312 | 78.7495
44.1917 | 74.9074 | 113.4802 | 79.9101
45.1917 | 76.6576 | 114.1526 | 80.0324
46.1917 | 78.9171 | 114.2108 | 81.1325
47.1917 | 79.7837 | 116.1642 | 82.9816
48.1917 | 80.5114 | 117.5167 | 84.9271
49.1917 | 82.0278 | 118.8344 | 85.747
50.1917 | 84.8124 | 119.7534 | 85.9209
51.1917 | 86.2489 | 120.017 | 86.7725
52.1917 | 86.8829 | 120.5555 | 87.2906
53.1917 | 88.1511 | 121.0581 | 88.1125
54.1917 | 88.7559 | 120.9315 | 88.7133
55.1917 | 89.0926 | 121.6042 | 89.4405
56.1917 | 89.4169 | 122.8682 | 90.1299
57.1917 | 89.546 | 124.3169 | 91.3367
58.1917 | 89.4269 | 125.0021 | 92.7591
59.1917 | 90.3593 | 125.0599 | 93.7926
60.1917 | 91.739 | 126.1198 | 94.8902
61.1917 | 92.5231 | 127.34 | 96.175
62.1917 | 93.1489 | 127.9448 | 97.5855
63.1917 | 93.3301 | 127.5882 | 98.0199
64.1917 | 94.4183 | 128.0564 | 98.1998
65.1917 | 94.7215 | 129.018 | 98.6864
66.1917 | 96.3295 | 131.3831 | 100.4415
67.1917 | 97.3556 | 133.0746 | 103.2104
68.1917 | 98.7178 | 135.3162 | 105.2096
69.2073 | 101.1404 | 138.3439 | 108.098
70.1917 | 102.5248 | 139.8528 | 110.4844
71.1917 | 103.8903 | 141.0168 | 111.7611
72.1917 | 103.9729 | 141.636 | 112.2767
73.1917 | 104.3276 | 142.8881 | 113.6169
74.1917 | 104.7191 | 143.5312 | 114.9342
75.1917 | 106.5558 | 143.7339 | 116.1959
76.1917 | 107.647 | 144.6525 | 116.4752
77.1917 | 108.1556 | 146.017 | 117.4314
78.1917 | 108.6177 | 145.6732 | 118.5716
79.1917 | 109.424 | 145.5557 | 118.5573
80.1917 | 109.9796 | 146.8177 | 119.7383
81.1917 | 110.3829 | 147.8442 | 120.3653
82.1917 | 111.5384 | 148.0574 | 121.9099
83.1917 | 111.8561 | 148.9515 | 122.727
84.1917 | 112.4691 | 148.8453 | 123.9151
85.1917 | 112.8825 | 148.5503 | 124.6102
86.1917 | 113.4761 | 148.5471 | 124.6797
87.1917 | 114.1542 | 149.3483 | 124.4343
88.1917 | 115.3159 | 151.6069 | 126.1118
89.1917 | 118.5063 | 153.8452 | 128.2452
90.1917 | 119.4841 | 153.8057 | 130.4695
91.1917 | 121.007 | 155.0319 | 130.6501
92.1917 | 121.5069 | 155.9397 | 130.4385
93.2073 | 123.6342 | 157.1357 | 130.2847
94.1917 | 123.0694 | 158.2676 | 133.2321
95.1917 | 126.015 | 159.1858 | 135.0372
96.1917 | 127.6665 | 160.9877 | 135.053
97.2073 | 129.2766 | 161.761 | 135.7472
98.1917 | 129.5567 | 163.3789 | 136.0904
99.2073 | 130.3551 | 164.2892 | 136.524
100.1917 | 129.5135 | 164.8007 | 138.1699
101.1917 | 129.9669 | 165.5657 | 139.438
102.1917 | 130.1374 | 165.9321 | 140.3422
103.1917 | 131.7988 | 167.2767 | 141.828
104.1917 | 132.153 | 167.8986 | 142.1128
105.1917 | 132.3693 | 167.9252 | 141.6638
106.1917 | 132.5214 | 168.7778 | 141.3884
107.1917 | 131.8503 | 169.0472 | 141.2631
108.1917 | 131.287 | 169.3749 | 141.0522
109.1917 | 131.4642 | 169.5097 | 140.3708
110.1917 | 131.4872 | 170.4406 | 140.6141
111.1917 | 132.9894 | 172.0741 | 141.303
112.1917 | 132.8666 | 173.4935 | 141.6897
113.1917 | 132.7944 | 174.2153 | 142.7681
114.1917 | 133.3202 | 173.4351 | 142.1912
115.1917 | 133.3464 | 173.8267 | 142.2542
116.1917 | 132.8907 | 173.5166 | 143.3984
117.1917 | 132.461 | 173.4732 | 143.5127
118.1917 | 132.9167 | 173.8016 | 144.5129
119.1917 | 133.7176 | 174.637 | 145.2885
120.1917 | 136.1426 | 175.4846 | 145.4718
121.1917 | 136.9615 | 175.6234 | 145.9342
122.1917 | 136.3593 | 175.3639 | 147.273
123.1917 | 136.0026 | 176.439 | 147.2251
124.1917 | 135.3829 | 176.2172 | 148.1452
125.1917 | 136.1735 | 176.384 | 147.5768
126.1917 | 135.544 | 177.0677 | 147.2867
127.1917 | 137.2536 | 178.562 | 147.1953
128.1917 | 136.7949 | 179.255 | 148.1504
129.1917 | 136.8775 | 180.5261 | 149.7576
130.1917 | 136.3071 | 179.8883 | 150.8573
131.1917 | 136.3547 | 179.3865 | 150.2804
132.1917 | 135.8897 | 179.9644 | 151.0373
133.1917 | 135.5336 | 180.3279 | 151.6831
134.1917 | 136.0836 | 180.2428 | 151.8632
135.1917 | 136.3569 | 179.5521 | 152.6469
136.1917 | 136.7322 | 179.226 | 152.6068
137.1917 | 136.9047 | 178.8396 | 152.6575
138.1917 | 136.6788 | 178.679 | 152.7363
139.1917 | 135.8666 | 178.042 | 153.4455
140.1917 | 135.9973 | 177.6437 | 154.7181
141.1917 | 136.4982 | 178.6595 | 155.6659
142.1917 | 137.281 | 177.9907 | 155.5491
143.1917 | 137.1731 | 177.404 | 156.0399
144.1917 | 136.6428 | 177.8808 | 157.2516
145.1917 | 136.6507 | 178.1372 | 157.5603
146.1917 | 136.2933 | 178.4485 | 159.2131
147.1917 | 135.6242 | 178.9311 | 159.5351
148.1917 | 135.7232 | 179.5555 | 160.8352
149.1917 | 136.8407 | 179.4444 | 163.5512
150.1917 | 137.6166 | 180.3528 | 163.4644
151.1917 | 137.6376 | 181.934 | 163.9199
152.1917 | 137.969 | 182.2902 | 164.9309
153.1917 | 138.025 | 181.9646 | 164.9173
154.1917 | 137.7745 | 181.539 | 164.6672
155.1917 | 137.5051 | 181.1796 | 165.0691
156.1917 | 136.7486 | 180.3966 | 164.2458
157.1917 | 136.8654 | 179.9262 | 164.4408
158.1917 | 136.2191 | 179.271 | 164.7927
159.1917 | 137.0179 | 179.8963 | 165.7133
160.1917 | 137.4307 | 179.9611 | 167.0459
161.1917 | 136.2149 | 179.2954 | 167.402
162.2073 | 136.0029 | 180.0122 | 167.6173
163.1917 | 136.0127 | 179.957 | 167.9109
164.1917 | 135.2098 | 180.3719 | 167.2595
165.1917 | 135.5676 | 179.5281 | 166.8504
166.1917 | 135.883 | 178.4347 | 166.6463
167.1917 | 135.7784 | 177.8209 | 166.5157
168.1917 | 135.8322 | 177.0771 | 166.4732
169.1917 | 135.4477 | 177.0624 | 165.6227
170.1917 | 135.9887 | 178.191 | 165.3368
171.1917 | 135.9541 | 178.7023 | 164.4515
172.1917 | 135.4017 | 178.6998 | 164.5132
173.1917 | 136.3256 | 178.9941 | 164.9131
174.1917 | 137.8097 | 179.7071 | 165.5147
175.1917 | 139.2603 | 180.3398 | 167.0367
176.1917 | 139.1395 | 180.8971 | 167.905
177.1917 | 139.0539 | 180.4988 | 167.847
178.1917 | 138.7813 | 180.7397 | 168.4273
179.1917 | 138.9876 | 180.649 | 169.7188
180.1917 | 138.4978 | 180.7927 | 169.7474
181.1917 | 139.5685 | 180.5125 | 170.0577
182.1917 | 138.7802 | 180.9882 | 170.7788
183.1917 | 140.4478 | 180.8834 | 171.0593
184.1917 | 140.4653 | 181.4144 | 171.3819
185.1917 | 139.3352 | 180.6837 | 171.5591
186.1917 | 138.8226 | 180.9245 | 171.1247
187.1917 | 138.6364 | 180.8991 | 170.6817
188.1917 | 138.5958 | 180.0759 | 170.8764
189.1917 | 138.8307 | 180.656 | 169.8316
190.1917 | 138.5733 | 180.6428 | 169.5291
191.1917 | 138.6432 | 181.143 | 169.7927
192.1917 | 138.6279 | 181.4613 | 169.4761
193.1917 | 138.8779 | 181.1741 | 169.1771
194.1917 | 139.179 | 180.1519 | 168.1703
195.1917 | 138.5482 | 179.2724 | 167.9817
196.1917 | 138.3311 | 179.1108 | 168.473
197.1917 | 138.4349 | 178.9222 | 168.7654
198.1917 | 138.8528 | 179.1094 | 168.4975
199.1917 | 139.3572 | 179.9304 | 168.1298
200.1917 | 140.1313 | 181.3672 | 167.7845
201.1917 | 139.8026 | 181.363 | 168.8299
202.1917 | 139.4862 | 181.483 | 168.8851
203.1917 | 138.6915 | 180.9757 | 168.8782
204.1917 | 138.8383 | 180.2247 | 167.887
205.1917 | 138.5366 | 180.1747 | 168.2587
206.1917 | 138.6587 | 179.2043 | 168.249
207.1917 | 138.7153 | 178.7027 | 167.6261
208.1917 | 138.1074 | 177.9282 | 166.9798
209.1917 | 138.1333 | 177.2084 | 165.9891
210.1917 | 137.944 | 176.8214 | 165.7884
211.1917 | 137.3841 | 175.7491 | 165.0551
212.1917 | 137.2997 | 176.5527 | 164.4844
213.1917 | 137.1662 | 176.7057 | 164.0796
214.1917 | 137.5566 | 176.1574 | 163.5071
215.1917 | 137.8435 | 175.9873 | 163.1112
216.1917 | 137.897 | 176.458 | 162.5964
217.1917 | 138.8757 | 177.0045 | 162.4725
218.1917 | 139.3057 | 177.1422 | 161.9999
219.1917 | 139.439 | 176.8718 | 161.5243
220.1917 | 139.0649 | 176.8898 | 163.0828
221.1917 | 139.4319 | 176.7128 | 162.9456
222.1917 | 139.8681 | 177.4318 | 162.5889
223.1917 | 139.2599 | 177.6498 | 162.7363
224.1917 | 138.9566 | 177.3335 | 162.2976
225.1917 | 139.8389 | 177.5042 | 162.8335
226.1917 | 140.805 | 177.4184 | 163.5792
227.1917 | 142.1838 | 177.7599 | 163.0968
228.1917 | 143.0298 | 179.1312 | 163.7113
229.1917 | 142.9188 | 179.6881 | 165.3338
230.1917 | 143.3198 | 181.1141 | 165.8347
231.1917 | 142.9134 | 180.1412 | 165.5224
232.1917 | 143.3041 | 179.6852 | 165.1099
233.1917 | 144.1385 | 180.6137 | 165.0854
234.1917 | 144.2372 | 181.1175 | 165.5576
235.1917 | 144.0415 | 181.826 | 166.5512
236.1917 | 144.2315 | 182.274 | 167.1703
237.1917 | 144.8953 | 183.3321 | 168.0927
238.1917 | 144.7773 | 184.7284 | 169.6756
239.1917 | 145.5306 | 185.9227 | 171.7332
240.1917 | 145.0821 | 185.928 | 171.749
241.1917 | 145.2601 | 186.1275 | 171.6797
242.1917 | 144.7807 | 188.1434 | 173.626
243.1917 | 146.7538 | 188.6973 | 174.3845
244.1917 | 146.3394 | 188.7545 | 173.6532
245.1917 | 146.4287 | 189.3905 | 173.4867
246.1917 | 145.992 | 189.3067 | 173.0161
247.1917 | 146.6174 | 189.4633 | 173.4262
248.1917 | 146.244 | 189.1951 | 173.4905
249.1917 | 146.702 | 189.2205 | 173.131
250.1917 | 146.8654 | 188.9655 | 172.8694
251.1917 | 146.6938 | 189.8552 | 173.1306
252.1917 | 146.4901 | 190.3186 | 174.8548
253.1917 | 146.4496 | 190.6726 | 176.1563
254.1917 | 146.0853 | 191.7577 | 178.5582
255.1917 | 145.4027 | 192.1046 | 179.941
256.1917 | 146.6537 | 191.9341 | 179.9951
257.1917 | 146.5151 | 191.5481 | 179.6899
258.1917 | 146.2387 | 190.5327 | 179.5627
259.1917 | 145.9587 | 190.3577 | 178.9771
260.1917 | 146.1796 | 190.7534 | 179.6632
261.1917 | 146.4101 | 191.3024 | 179.4916
262.1917 | 146.3307 | 191.5223 | 179.3165
263.1917 | 147.0259 | 192.994 | 179.1318
264.1917 | 147.3721 | 194.2068 | 180.3362
265.1917 | 147.0341 | 194.5035 | 180.8667
266.1917 | 146.7046 | 195.0226 | 181.5969
267.1917 | 146.9176 | 194.4228 | 181.8944
268.1917 | 147.5323 | 194.1563 | 181.8685
269.1917 | 147.9601 | 193.2614 | 180.9205
270.1917 | 148.3861 | 193.6858 | 181.426
271.1917 | 148.6758 | 193.804 | 181.0495
272.1917 | 149.2653 | 193.8169 | 181.0975
273.1917 | 150.0848 | 194.263 | 183.6737
274.1917 | 150.4679 | 195.0272 | 183.5916
275.1917 | 150.5577 | 195.4618 | 185.0028
276.1917 | 150.9061 | 194.9627 | 184.7116
277.1917 | 151.5071 | 194.6504 | 185.1281
278.1917 | 151.2133 | 194.0344 | 184.3898
279.1917 | 150.6958 | 193.895 | 183.2038
280.1917 | 150.7212 | 193.7501 | 182.9689
281.1917 | 151.4426 | 193.6763 | 183.2548
282.1917 | 151.2102 | 192.7722 | 182.2707
283.1917 | 151.5134 | 193.3942 | 181.6642
284.1917 | 151.5298 | 194.6645 | 182.5807
285.1917 | 152.4126 | 195.0009 | 184.2056
286.1917 | 151.7427 | 194.7286 | 183.7373
287.1917 | 151.6199 | 194.603 | 184.3984
288.1917 | 152.1543 | 194.4674 | 184.5721
289.1917 | 151.8655 | 195.0656 | 184.3629
290.1917 | 151.6416 | 195.3947 | 184.0212
291.1917 | 151.7402 | 195.6392 | 183.4177
292.1917 | 152.8065 | 196.1865 | 182.9204
293.1917 | 153.3319 | 196.7405 | 182.5631
294.1917 | 153.5714 | 196.7842 | 182.7691
295.1917 | 152.913 | 196.3105 | 183.0316
296.1917 | 152.4971 | 195.9533 | 183.5113
297.1917 | 152.0483 | 195.5339 | 183.8649
298.1917 | 151.9048 | 195.7256 | 183.8075
299.1917 | 152.6504 | 197.032 | 184.0103
300.1917 | 152.4209 | 197.6266 | 185.1351
301.1917 | 152.5521 | 198.1599 | 185.6543
302.1917 | 153.7766 | 199.9931 | 185.2777
303.1917 | 153.1576 | 198.8811 | 186.4085
304.1917 | 154.566 | 199.7239 | 186.9508
305.2073 | 154.96 | 199.8771 | 187.076
306.1917 | 156.0213 | 201.5013 | 187.9384
307.1917 | 155.9423 | 202.1007 | 188.4092
308.1917 | 155.4392 | 202.7989 | 191.0779
309.1917 | 156.7841 | 204.9078 | 191.8582
310.1917 | 156.5274 | 206.1253 | 194.3496
311.2073 | 157.0488 | 206.7565 | 195.7044
312.1917 | 157.3954 | 207.3516 | 195.5457
313.1917 | 157.4859 | 207.1137 | 195.4197
314.1917 | 158.409 | 208.4528 | 196.1663
315.1917 | 159.3249 | 208.0553 | 195.9828
316.1917 | 159.2218 | 207.5915 | 194.9319
317.1917 | 159.9382 | 208.1813 | 194.7531
318.1917 | 159.5535 | 207.3235 | 194.4564
319.1917 | 159.3675 | 206.9351 | 193.6999
320.1917 | 158.9278 | 206.4642 | 193.4359
321.1917 | 160.0776 | 206.8019 | 193.6873
322.1917 | 159.9407 | 207.0008 | 193.9838
323.1917 | 160.5323 | 207.5053 | 194.0898
324.1917 | 160.3586 | 207.4794 | 195.4365
325.1917 | 160.7429 | 208.2424 | 197.1315
326.1917 | 161.1093 | 207.8119 | 197.0483
327.1917 | 161.0416 | 208.3623 | 196.5983
328.1917 | 160.9545 | 207.985 | 196.6129
329.1917 | 161.3018 | 208.1788 | 196.5099
330.1917 | 161.7557 | 209.2629 | 197.2924
331.1917 | 161.658 | 209.4398 | 197.4079
332.1917 | 163.9401 | 211.7793 | 198.0936
333.1917 | 163.4804 | 212.8324 | 199.0558
334.1917 | 163.6394 | 212.6234 | 199.9662
335.1917 | 163.511 | 213.074 | 201.3411
336.1917 | 163.2786 | 213.3518 | 203.0184
337.1917 | 164.2586 | 214.4994 | 203.5481
338.1917 | 166.5881 | 214.3514 | 204.8547
339.1917 | 167.3391 | 214.6614 | 206.4806
340.1917 | 168.3685 | 214.4949 | 207.243
341.1917 | 169.4108 | 215.0999 | 207.347
342.1917 | 169.7892 | 215.3959 | 207.6782
343.1917 | 169.7949 | 215.2898 | 208.0707
344.1917 | 169.6233 | 216.0841 | 208.8691
345.1917 | 168.2503 | 215.8192 | 208.0436
346.1917 | 167.6714 | 216.3334 | 208.8991
347.1917 | 168.6493 | 216.74 | 210.9264
348.1917 | 168.3574 | 215.9493 | 211.1856
349.1917 | 168.0502 | 216.9257 | 211.7048
350.1917 | 167.959 | 217.7467 | 210.5335
351.1917 | 168.7909 | 217.5959 | 209.9732
352.1917 | 168.5687 | 217.9045 | 209.8069
353.1917 | 169.5896 | 218.4733 | 209.5843
354.1917 | 168.256 | 218.6453 | 210.3865
355.1917 | 167.9769 | 218.3696 | 210.303
356.1917 | 167.9059 | 218.6144 | 209.8388
357.1917 | 168.3852 | 218.4533 | 209.9024
358.1917 | 169.5103 | 218.6441 | 211.1085
359.1917 | 170.1628 | 219.2568 | 211.6586
360.1917 | 169.9575 | 219.0323 | 211.2579
361.1917 | 169.1954 | 219.1776 | 210.9289
362.1917 | 168.8623 | 220.9596 | 211.616
363.1917 | 168.5753 | 220.7604 | 211.5166
364.1917 | 168.1804 | 219.3915 | 211.0324
365.1917 | 166.721 | 218.7108 | 209.7971
366.1917 | 166.4172 | 218.2946 | 209.5795
367.1917 | 166.0431 | 217.2602 | 208.3398
368.1917 | 167.1627 | 216.9237 | 207.2139
369.1917 | 167.2692 | 216.7717 | 208.7242
370.1917 | 166.5397 | 216.7211 | 207.5673
371.1917 | 166.7929 | 216.2051 | 207.3284
372.1917 | 166.8495 | 216.0305 | 206.8454
373.1917 | 166.3725 | 215.9185 | 206.0144
374.1917 | 166.3125 | 217.1221 | 205.3793
375.1917 | 166.4239 | 217.6872 | 205.5291
376.1917 | 166.7515 | 216.1544 | 205.026
377.1917 | 166.1938 | 215.1602 | 205.5535
378.1917 | 165.575 | 214.5176 | 205.0579
379.1917 | 165.5949 | 213.7778 | 205.297
380.1917 | 164.2624 | 215.26 | 204.5392
381.1917 | 163.7697 | 215.2815 | 205.2299
382.1917 | 163.2271 | 215.2502 | 205.9495
383.1917 | 164.1828 | 216.0369 | 207.3703
384.1917 | 166.5372 | 216.8769 | 208.0629
385.1917 | 166.3408 | 217.4991 | 208.5861
386.1917 | 166.5875 | 218.4136 | 209.011
387.1917 | 166.0162 | 218.5329 | 208.7659
388.1917 | 166.6568 | 219.5933 | 209.2585
389.1917 | 167.0735 | 219.51 | 209.1538
390.1917 | 166.8771 | 219.3666 | 208.5005
391.1917 | 166.8387 | 219.1742 | 208.365
392.1917 | 165.9749 | 218.7825 | 208.2032
393.1917 | 166.2909 | 219.0327 | 206.5473
394.1917 | 165.2879 | 218.8658 | 205.7712
395.1917 | 164.6112 | 218.3818 | 205.6061
396.1917 | 164.3064 | 218.2655 | 205.3146
397.1917 | 163.6033 | 217.5275 | 205.6183
398.1917 | 163.571 | 216.4968 | 203.9403
399.1917 | 163.593 | 214.9656 | 202.8282
400.1917 | 164.3277 | 216.4738 | 202.7857
401.1917 | 164.858 | 217.2605 | 203.515
402.1917 | 164.7607 | 216.9738 | 203.5725
403.1917 | 165.6581 | 216.553 | 205.0987
404.1917 | 166.3398 | 216.4572 | 205.3708
405.1917 | 165.991 | 217.0198 | 205.3217
406.1917 | 165.8313 | 216.5786 | 205.2796
407.1917 | 165.746 | 217.7807 | 204.5702
408.1917 | 165.4613 | 218.6281 | 205.6857
409.1917 | 165.3193 | 218.8438 | 205.2446
410.1917 | 165.8867 | 218.4735 | 204.3389
411.1917 | 165.6715 | 218.0464 | 203.2157
412.1917 | 165.9285 | 217.987 | 203.0462
413.1917 | 165.6515 | 216.5049 | 202.5065
414.1917 | 165.0137 | 215.9579 | 201.5619
415.1917 | 164.4275 | 216.1182 | 200.8269
416.1917 | 163.7015 | 215.5787 | 200.222
417.1917 | 163.1739 | 215.0631 | 199.6403
418.1917 | 162.8634 | 214.991 | 200.5057
419.1917 | 163.0373 | 215.0685 | 200.5567
420.1917 | 164.5365 | 214.8016 | 200.1837
421.1917 | 165.4442 | 214.5244 | 200.079
422.1917 | 165.6905 | 213.8969 | 199.977
423.1917 | 165.4117 | 213.3429 | 199.0663
424.1917 | 165.7985 | 213.3734 | 198.4323
425.2073 | 165.3493 | 213.7134 | 198.5374
426.1917 | 165.7161 | 214.577 | 198.7141
427.1917 | 166.7122 | 215.0017 | 198.221
428.1917 | 167.1033 | 215.3891 | 198.229
429.1917 | 167.1331 | 216.0411 | 198.3385
430.1917 | 167.5417 | 215.3406 | 198.0227
431.1917 | 167.8112 | 215.434 | 197.2357
432.1917 | 167.5147 | 215.1497 | 196.1979
433.1917 | 167.6593 | 215.0263 | 195.8868
434.1917 | 167.565 | 215.1469 | 196.374
435.1917 | 167.0764 | 214.6624 | 196.2352
436.1917 | 168.1473 | 214.199 | 195.3924
437.1917 | 169.057 | 213.8988 | 195.3329
438.1917 | 169.4876 | 214.2372 | 194.9594
439.1917 | 170.6667 | 214.2981 | 194.6962
440.1917 | 170.3535 | 214.8745 | 194.6085
441.1917 | 170.1634 | 214.6166 | 194.5914
442.1917 | 169.8789 | 215.5634 | 195.4178
443.1917 | 169.8736 | 216.2692 | 196.5121
444.1917 | 169.8441 | 215.6975 | 197.9179
445.1917 | 170.2291 | 215.8058 | 198.5407
446.1917 | 170.8559 | 216.4878 | 198.6322
447.1917 | 170.431 | 217.2828 | 199.967
448.1917 | 171.007 | 218.4122 | 201.5594
449.1917 | 171.9086 | 218.4796 | 202.2819
450.1917 | 171.8247 | 217.5268 | 202.6031
451.1917 | 171.373 | 217.1243 | 203.0162
452.1917 | 170.986 | 216.8948 | 202.8237
453.1917 | 170.865 | 216.457 | 202.1832
454.1917 | 170.2622 | 216.2049 | 201.3106
455.1917 | 169.5312 | 216.0221 | 201.2105
456.1917 | 168.6818 | 216.0204 | 201.138
457.1917 | 168.1813 | 216.4034 | 202.1779
458.1917 | 167.6512 | 215.4929 | 202.7236
459.1917 | 166.4886 | 215.7222 | 202.5891
460.1917 | 167.1137 | 215.3602 | 202.1704
461.1917 | 166.9664 | 216.3101 | 202.7401
462.1917 | 166.8828 | 216.4614 | 202.8125
463.1917 | 166.7581 | 215.8008 | 203.3568
464.1917 | 167.2124 | 216.2431 | 203.3773
465.1917 | 166.9033 | 215.2672 | 203.5696
466.1917 | 167.2325 | 214.6131 | 203.1392
467.1917 | 167.407 | 214.8537 | 202.5527
468.1917 | 167.5758 | 215.3423 | 202.5888
469.1917 | 167.4674 | 214.9401 | 202.253
470.1917 | 167.3453 | 215.9596 | 201.615
471.1917 | 167.2593 | 216.8574 | 201.3907
472.1917 | 167.2988 | 215.2349 | 201.04
473.1917 | 166.9855 | 214.2502 | 201.1519
474.1917 | 167.2444 | 215.0557 | 202.4483
475.1917 | 167.1761 | 215.0705 | 202.2918
476.1917 | 166.3229 | 215.4695 | 202.5883
477.1917 | 166.5519 | 216.6048 | 203.8114
478.1917 | 165.8057 | 217.026 | 204.2402
479.1917 | 167.002 | 217.831 | 204.6523
480.1917 | 166.9239 | 218.2135 | 205.2957
481.1917 | 167.1331 | 218.2922 | 204.7399
482.1917 | 167.1031 | 218.2299 | 204.0981
483.1917 | 167.8451 | 218.5519 | 203.7728
484.1917 | 169.4284 | 218.7974 | 203.0188
485.1917 | 170.731 | 219.1211 | 204.2342
486.1917 | 171.0458 | 219.105 | 203.8917
487.1917 | 171.0919 | 219.0007 | 203.469
488.1917 | 171.0508 | 219.316 | 203.4077
489.1917 | 171.3646 | 219.8808 | 203.6977
490.1917 | 171.087 | 219.4359 | 203.5264
491.1917 | 170.8249 | 219.1913 | 203.6646
492.1917 | 170.4848 | 218.7995 | 203.2611
493.1917 | 169.5384 | 217.9513 | 202.7904
494.1917 | 169.7104 | 217.5066 | 202.1269
495.1917 | 172.1613 | 218.9498 | 201.8399
496.1917 | 174.1996 | 220.3603 | 202.3788
497.1917 | 174.4016 | 221.6991 | 203.4262
498.1917 | 174.3697 | 223.6744 | 204.493
499.1917 | 174.3289 | 223.9021 | 205.1096
500.1917 | 174.1181 | 222.9418 | 205.1922
501.1917 | 174.5594 | 222.9906 | 205.6043
502.1917 | 174.1516 | 222.9863 | 205.497
503.1917 | 175.6385 | 224.1777 | 205.3819
504.1917 | 176.1079 | 225.1374 | 206.224
505.1917 | 175.8811 | 225.4215 | 206.0899
506.1917 | 175.5726 | 225.4159 | 205.6761
507.1917 | 174.7386 | 225.2286 | 205.5049
508.1917 | 175.6017 | 224.9865 | 205.4915
509.1917 | 175.4822 | 224.494 | 205.2132
510.1917 | 176.0071 | 224.248 | 204.389
511.1917 | 175.1483 | 224.6905 | 204.9764
512.1917 | 177.2362 | 225.2597 | 205.2301
513.1917 | 177.0299 | 226.2341 | 205.5965
514.1917 | 177.4702 | 227.4743 | 205.716
515.1917 | 177.6762 | 227.6836 | 206.183
516.1917 | 178.5138 | 228.6637 | 207.1563
517.1917 | 177.7965 | 229.5113 | 207.4641
518.1917 | 176.3794 | 229.561 | 207.7251
519.1917 | 176.3522 | 228.8999 | 207.638
520.1917 | 176.3514 | 229.5179 | 207.6227
521.1917 | 176.9466 | 229.4177 | 207.5043
522.1917 | 176.5136 | 229.1509 | 207.7974
523.1917 | 175.8968 | 228.9906 | 208.4253
524.1917 | 175.0259 | 228.9439 | 208.4968
525.1917 | 174.9178 | 229.431 | 208.7219
526.1917 | 174.422 | 228.9168 | 209.2617
527.1917 | 175.8572 | 228.5526 | 210.3303
528.1917 | 176.1264 | 228.8224 | 209.9541
529.1917 | 175.7735 | 227.8759 | 209.7907
530.1917 | 175.0053 | 227.2199 | 210.3592
531.1917 | 174.6513 | 226.455 | 209.9767
532.1917 | 174.7498 | 226.4905 | 210.2997
533.1917 | 175.288 | 226.5635 | 210.5208
534.1917 | 175.8717 | 227.1297 | 210.5572
535.1917 | 178.4787 | 229.0939 | 213.0506
536.1917 | 181.1098 | 231.5105 | 214.2262
537.1917 | 181.3345 | 232.477 | 215.5667
538.1917 | 182.1448 | 232.4239 | 214.9753
539.1917 | 182.2728 | 233.4511 | 215.1636
540.1917 | 181.6832 | 233.4632 | 214.4334
541.1917 | 181.5847 | 232.9584 | 213.7104
542.1917 | 181.1238 | 233.455 | 213.0202
543.1917 | 180.2803 | 233.7105 | 213.1575
544.1917 | 180.1116 | 233.3071 | 213.5359
545.1917 | 179.8787 | 233.2184 | 213.6266
546.1917 | 180.4063 | 232.9389 | 213.0334
547.1917 | 179.1728 | 232.8739 | 212.3042
548.1917 | 179.3439 | 232.6006 | 211.3486
549.1917 | 180.8729 | 232.6607 | 210.9874
550.1917 | 181.3175 | 231.8026 | 210.2207
551.1917 | 181.3251 | 231.7577 | 209.8845
552.1917 | 182.7722 | 231.8292 | 208.6611
553.1917 | 182.6743 | 231.6553 | 207.9754
554.1917 | 182.3894 | 231.0247 | 207.3129
555.1917 | 183.147 | 230.5723 | 206.5749
556.1917 | 183.2705 | 230.1015 | 206.2614
557.1917 | 182.8317 | 229.5971 | 206.3532
558.1917 | 183.0567 | 229.3442 | 207.4528
559.1917 | 183.1677 | 228.8667 | 207.1096
560.1917 | 183.2106 | 227.8844 | 206.4576
561.1917 | 182.2624 | 227.2726 | 206.162
562.1917 | 182.2704 | 227.6657 | 206.2783
563.1917 | 182.4791 | 227.5837 | 206.5752
564.1917 | 181.4768 | 227.2959 | 205.3206
565.1917 | 180.8447 | 227.0322 | 206.1105
566.1917 | 181.9011 | 228.0863 | 206.6182
567.1917 | 182.8096 | 229.2822 | 208.0297
568.1917 | 182.3621 | 228.4605 | 207.4397
569.1917 | 182.5899 | 228.7884 | 207.7115
570.1917 | 181.4095 | 229.2876 | 208.5581
571.1917 | 181.2908 | 229.6346 | 208.8063
572.1917 | 180.3876 | 228.7866 | 208.5654
573.1917 | 180.349 | 228.2645 | 207.8375
574.1917 | 179.6057 | 227.6853 | 207.1448
575.1917 | 179.8653 | 227.5714 | 206.6819
576.1917 | 180.0581 | 227.6376 | 207.3394
577.1917 | 179.803 | 227.4249 | 206.8883
578.1917 | 179.1868 | 227.0806 | 206.2668
579.1917 | 178.9833 | 226.8475 | 206.3023
580.1917 | 179.387 | 226.7863 | 206.0014
581.1917 | 179.6327 | 227.1013 | 206.9734
582.1917 | 180.0941 | 228.0294 | 207.5918
583.1917 | 179.5364 | 228.0815 | 208.0008
584.1917 | 179.4486 | 228.0696 | 207.9472
585.1917 | 179.6428 | 228.1147 | 207.524
586.1917 | 179.4588 | 227.6918 | 207.337
587.1917 | 178.9488 | 226.8289 | 207.242
588.1917 | 178.5298 | 226.1037 | 206.592
589.1917 | 177.8835 | 225.4059 | 205.6984
590.1917 | 177.2983 | 225.3188 | 204.7974
591.1917 | 177.1514 | 224.2316 | 204.7038
592.1917 | 178.5129 | 224.8035 | 205.438
593.1917 | 179.362 | 223.4323 | 205.6244
594.1917 | 179.0777 | 224.035 | 206.6201
595.1917 | 179.275 | 225.4094 | 206.7516
596.1917 | 179.8436 | 225.6839 | 207.081
597.1917 | 180.2269 | 224.4058 | 206.4433
598.1917 | 180.6753 | 224.9122 | 206.4422
599.1917 | 182.9925 | 225.9616 | 206.6406
600.1917 | 184.3395 | 226.6246 | 207.3563
601.1917 | 184.253 | 227.2693 | 208.7621
602.1917 | 184.3779 | 228.3896 | 210.3725
603.1917 | 184.5026 | 228.5441 | 211.8001
604.1917 | 184.7182 | 229.3455 | 212.0655
605.1917 | 185.4729 | 229.8728 | 211.5558
606.1917 | 185.7122 | 229.5868 | 210.7662
607.1917 | 185.3148 | 229.3728 | 210.9959
608.1917 | 186.0507 | 229.8635 | 211.8406
609.1917 | 186.2544 | 229.3328 | 211.3304
610.1917 | 185.9629 | 228.2121 | 210.3313
611.1917 | 186.301 | 226.8344 | 209.4057
612.1917 | 186.7672 | 226.6131 | 208.6593
613.1917 | 185.9733 | 227.2311 | 208.4217
614.1917 | 188.0025 | 228.3226 | 209.3957
615.1917 | 188.6753 | 228.6971 | 210.4428
616.1917 | 187.9222 | 227.933 | 209.4519
617.1917 | 187.1426 | 227.9079 | 210.0977
618.1917 | 187.607 | 228.3603 | 210.4413
619.1917 | 188.4472 | 228.4768 | 210.1064
620.1917 | 187.9446 | 228.2784 | 209.4428
621.1917 | 188.0833 | 228.6491 | 209.134
622.1917 | 187.7994 | 227.9014 | 208.4895
623.1917 | 187.6259 | 227.8037 | 208.6159
624.1917 | 187.2879 | 227.18 | 208.4553
625.1917 | 186.973 | 226.5883 | 207.871
626.1917 | 186.6676 | 226.24 | 207.5292
627.1917 | 186.567 | 225.4426 | 207.5021
628.1917 | 186.8393 | 225.2636 | 207.1567
629.1917 | 187.3515 | 225.2511 | 206.8951
630.1917 | 188.8338 | 224.6519 | 207.1917
631.1917 | 189.2488 | 225.4165 | 206.8192
632.1917 | 189.8568 | 225.8634 | 206.9502
633.1917 | 188.0942 | 226.0111 | 207.1554
634.1917 | 187.2883 | 225.8996 | 207.1671
635.1917 | 186.6355 | 226.1986 | 206.4097
636.1917 | 187.3981 | 226.3026 | 206.0785
637.1917 | 187.4789 | 225.4971 | 205.9893
638.1917 | 186.6322 | 224.8346 | 205.2541
639.1917 | 186.1576 | 224.6341 | 205.359
640.1917 | 184.8302 | 224.7933 | 205.6645
641.1917 | 184.1249 | 224.7917 | 205.3792
642.1917 | 184.3187 | 224.6565 | 205.6337
643.1917 | 183.8408 | 224.741 | 206.0726
644.1917 | 183.803 | 224.6431 | 206.0725
645.1917 | 184.0187 | 225.5915 | 206.3385
646.1917 | 184.7796 | 226.2796 | 206.904
647.1917 | 184.0934 | 226.1552 | 206.6709
648.1917 | 183.848 | 225.8853 | 207.233
649.1917 | 183.5359 | 225.3859 | 207.378
650.1917 | 183.4652 | 224.6102 | 206.9526
651.1917 | 183.194 | 223.7596 | 206.5732
652.1917 | 183.2278 | 223.2633 | 206.4672
653.1917 | 182.9188 | 223.0934 | 206.8638
654.1917 | 182.7757 | 223.0614 | 205.5781
655.1917 | 182.6561 | 223.9334 | 205.5428
656.1917 | 182.7648 | 223.9502 | 205.8142
657.1917 | 181.8223 | 224.9425 | 205.5336
658.1917 | 181.5854 | 224.5533 | 205.5191
659.1917 | 181.2979 | 224.8245 | 205.9594
660.1917 | 181.8379 | 226.3705 | 206.0672
661.1917 | 181.121 | 226.5548 | 206.5285
662.1917 | 180.7927 | 226.5373 | 206.3635
663.1917 | 181.069 | 227.7434 | 207
664.1917 | 181.1986 | 227.7992 | 206.9862
665.2073 | 181.5629 | 228.2495 | 207.9837
666.1917 | 182.1197 | 229.3002 | 208.0575
667.1917 | 181.3675 | 230.1593 | 208.1414
668.1917 | 182.7204 | 230.2282 | 207.4342
669.1917 | 182.6648 | 229.2824 | 207.1385
670.1917 | 182.9041 | 228.7698 | 207.1199
671.1917 | 184.1121 | 229.4215 | 207.1896
672.1917 | 183.6573 | 229.3036 | 207.842
673.1917 | 183.1003 | 229.9373 | 208.361
674.1917 | 184.2591 | 230.7461 | 208.0415
675.1917 | 184.4447 | 232.0514 | 208.6035
676.1917 | 184.8843 | 233.449 | 209.5158
677.1917 | 186.0289 | 234.2901 | 210.1678
678.1917 | 186.1761 | 234.0787 | 210.0374
679.1917 | 187.3465 | 233.2942 | 209.6547
680.1917 | 187.0043 | 232.331 | 208.7356
681.1917 | 187.0159 | 232.1833 | 208.673
682.1917 | 186.6306 | 232.3447 | 209.3898
683.1917 | 187.0485 | 231.9905 | 210.2099
684.1917 | 185.6429 | 232.5574 | 209.9023
685.1917 | 185.5459 | 232.2648 | 209.4691
686.1917 | 185.3801 | 232.2927 | 209.9616
687.2073 | 184.594 | 233.3763 | 210.6522
688.1917 | 184.8598 | 233.3 | 210.7519
689.1917 | 184.9715 | 231.7956 | 210.116
690.1917 | 185.0631 | 230.9116 | 209.6365
691.2073 | 184.7702 | 230.7776 | 209.3144
692.1917 | 184.4794 | 229.8775 | 209.3438
693.1917 | 184.1677 | 229.8372 | 208.7163
694.1917 | 184.2562 | 229.858 | 208.9353
695.1917 | 184.6727 | 229.5475 | 209.2319
696.1917 | 184.7969 | 228.8529 | 209.2018
697.2073 | 183.9502 | 228.4081 | 209.0925
698.1917 | 183.3927 | 227.912 | 209.6026
699.1917 | 183.8676 | 227.4414 | 209.6245
700.1917 | 183.3432 | 226.914 | 209.7398
701.1917 | 183.7393 | 226.5288 | 209.9492
702.1917 | 184.4648 | 227.543 | 210.6859
703.2073 | 184.8767 | 229.018 | 210.6758
704.1917 | 186.3354 | 229.7854 | 212.1073
705.1917 | 187.2384 | 230.1804 | 212.2058
706.1917 | 188.0422 | 229.5452 | 211.9746
707.2073 | 188.8819 | 230.2467 | 212.0442
708.1917 | 189.17 | 230.6655 | 212.3977
709.2073 | 190.556 | 229.8597 | 211.771
710.1917 | 191.8817 | 232.5212 | 211.9232
711.2073 | 194.6765 | 233.7733 | 214.5383
712.1917 | 194.3137 | 234.3324 | 214.9031
713.1917 | 194.1519 | 234.7623 | 214.9784
714.1917 | 194.8479 | 235.4382 | 214.0065
715.1917 | 193.8521 | 236.1902 | 213.6145
716.1917 | 195.3204 | 237.6092 | 215.3464
717.1917 | 198.0484 | 238.0764 | 217.2221
718.1917 | 197.9792 | 237.9144 | 217.9183
719.1917 | 197.9482 | 239.137 | 217.8784
720.1917 | 198.9198 | 240.7123 | 217.9576
721.1917 | 198.2932 | 241.2723 | 216.8637
722.1917 | 197.3145 | 241.7531 | 216.5723
723.1917 | 200.1939 | 241.7469 | 217.3481
724.1917 | 200.693 | 242.3844 | 217.9861
725.2073 | 199.9005 | 241.8907 | 217.439
726.1917 | 199.3602 | 240.4069 | 216.3787
727.1917 | 198.6739 | 238.8817 | 215.2442
728.1917 | 197.8612 | 238.2043 | 214.4154
729.1917 | 197.2933 | 237.96 | 213.9434
730.1917 | 196.522 | 238.2871 | 214.608
731.1917 | 196.7192 | 238.2637 | 214.0399
732.1917 | 197.264 | 239.62 | 213.6643
733.1917 | 199.9937 | 240.4662 | 214.0968
734.1917 | 200.8277 | 240.2559 | 213.3376
735.1917 | 200.467 | 240.0849 | 213.5129
736.1917 | 200.4242 | 241.3301 | 214.2767
737.1917 | 200.0593 | 241.7166 | 213.9504
738.1917 | 201.3781 | 241.1686 | 215.2549
739.1917 | 201.618 | 240.3087 | 215.0993
740.1917 | 200.8214 | 240.3118 | 214.7261
741.1917 | 202.0119 | 241.6409 | 216.6144
742.1917 | 202.1146 | 242.55 | 216.9953
743.1917 | 203.1917 | 241.7016 | 218.5455
744.1917 | 202.6618 | 241.1018 | 218.1714
745.1917 | 203.944 | 242.063 | 218.2792
746.1917 | 204.0472 | 242.5605 | 217.8361
747.1917 | 203.0992 | 241.5359 | 218.1967
748.1917 | 203.8725 | 240.2526 | 218.2794
749.1917 | 203.0352 | 239.6106 | 218.3863
750.1917 | 202.4446 | 240.51 | 218.4704
751.1917 | 203.1241 | 240.6647 | 217.8108
752.1917 | 202.1436 | 240.8653 | 217.1414
753.1917 | 203.1532 | 239.9409 | 216.2931
754.1917 | 204.5907 | 240.0365 | 216.4477
755.1917 | 204.5678 | 239.0017 | 215.4121
756.1917 | 206.1581 | 238.4369 | 214.5931
757.1917 | 206.8874 | 238.0724 | 213.8309
758.1917 | 207.6719 | 238.2855 | 213.8696
759.1917 | 207.1558 | 237.3669 | 213.1323
760.1917 | 207.8614 | 238.3691 | 212.7128
761.1917 | 208.2224 | 240.0147 | 212.1452
762.1917 | 208.7391 | 241.409 | 211.7284
763.1917 | 208.7932 | 241.8831 | 211.8162
764.1917 | 207.4677 | 241.6283 | 212.0995
765.1917 | 208.0468 | 240.7598 | 212.6819
766.1917 | 206.9257 | 240.8225 | 211.8546
767.1917 | 209.3394 | 241.2768 | 212.534
768.1917 | 210.4159 | 241.5154 | 214.5897
769.1917 | 211.2273 | 243.048 | 215.3529
770.1917 | 211.6755 | 243.2136 | 215.8142
771.1917 | 211.4253 | 243.7996 | 215.1151
772.1917 | 212.8252 | 244.9788 | 216.3498
773.1917 | 212.1599 | 245.0253 | 217.3306
774.1917 | 212.9125 | 245.2182 | 218.1198
775.1917 | 214.6331 | 246.0478 | 218.8135
776.1917 | 213.4242 | 247.142 | 218.1063
777.1917 | 212.2704 | 246.973 | 217.6075
778.1917 | 212.4219 | 247.2901 | 217.659
779.1917 | 213.5209 | 248.1449 | 219.4906
780.1917 | 214.8351 | 247.5562 | 220.0948
781.1917 | 213.802 | 248.5927 | 220.0752
782.1917 | 212.9057 | 249.2265 | 221.1764
783.1917 | 211.9417 | 248.2693 | 220.1995
784.1917 | 210.2146 | 246.5996 | 218.8456
785.1917 | 208.8926 | 246.7217 | 218.3705
786.1917 | 207.5244 | 246.0895 | 218.5615
787.1917 | 206.2904 | 244.783 | 218.3023
788.1917 | 205.6492 | 244.1741 | 218.8044
789.1917 | 205.9043 | 244.0058 | 219.1296
790.1917 | 204.6452 | 243.5603 | 219.0149
791.1917 | 204.392 | 242.4145 | 219.1122
792.1917 | 204.5293 | 242.1373 | 219.6225
793.1917 | 203.1434 | 242.3032 | 221.5576
794.1917 | 202.4998 | 241.9185 | 222.0552
795.1917 | 201.8904 | 242.0732 | 222.2063
796.1917 | 201.5659 | 242.5151 | 222.5463
797.1917 | 201.7103 | 242.8935 | 222.1822
798.1917 | 201.4526 | 243.22 | 221.9454
799.1917 | 201.0856 | 243.369 | 221.2601
800.1917 | 200.2512 | 244.3413 | 221.2048
801.1917 | 200.0598 | 244.0813 | 220.6278
802.1917 | 199.0154 | 242.5514 | 220.1652
803.1917 | 198.752 | 241.2351 | 219.5188
804.1917 | 197.882 | 240.7772 | 219.5029
805.1917 | 198.0824 | 240.2532 | 219.1596
806.1917 | 198.3577 | 239.2891 | 219.3869
807.1917 | 197.7926 | 237.8451 | 218.9017
808.1917 | 197.3774 | 237.3762 | 219.4159
809.1917 | 197.3871 | 236.5293 | 219.4593
810.1917 | 196.7766 | 235.3903 | 219.2952
811.1917 | 196.2874 | 234.6379 | 218.9438
812.1917 | 196.0179 | 234.4022 | 218.9599
813.1917 | 195.8288 | 233.6928 | 218.9697
814.1917 | 194.706 | 232.8818 | 218.6021
815.1917 | 194.7125 | 232.379 | 218.0981
816.1917 | 193.4267 | 232.7671 | 217.7577
817.1917 | 193.138 | 232.5013 | 218.4138
818.1917 | 193.1653 | 232.1616 | 217.8382
819.1917 | 192.5614 | 232.8941 | 217.7607
820.1917 | 192.2577 | 234.7719 | 218.1935
821.1917 | 192.8509 | 236.1399 | 217.9505
822.1917 | 192.9089 | 236.1659 | 218.4182
823.1917 | 194.1779 | 236.5324 | 218.0755
824.1917 | 194.0158 | 237.1855 | 217.8117
825.1917 | 193.8007 | 236.1781 | 217.5442
826.1917 | 194.219 | 236.4879 | 217.2697
827.1917 | 193.9145 | 236.5718 | 218.2093
828.1917 | 193.5958 | 236.8962 | 218.522
829.1917 | 193.5781 | 238.1721 | 218.9468
830.1917 | 194.6287 | 238.2903 | 220.0143
831.1917 | 194.8781 | 239.0541 | 220.4447
832.1917 | 194.531 | 240.0483 | 220.3312
833.1917 | 195.1904 | 240.6419 | 219.6418
834.1917 | 195.7802 | 239.4381 | 220.5826
835.1917 | 196.0072 | 239.9455 | 219.9619
836.1917 | 195.986 | 239.5107 | 220.3937
837.1917 | 196.092 | 239.7243 | 220.3146
838.1917 | 196.914 | 239.9659 | 220.6314
839.1917 | 197.8534 | 240.1819 | 219.7777
840.1917 | 199.0797 | 240.5312 | 219.7472
841.1917 | 199.7668 | 240.7962 | 219.096
842.1917 | 199.9466 | 240.0131 | 218.7131
843.1917 | 199.2407 | 239.1208 | 219.5494
844.1917 | 198.807 | 238.4499 | 219.1289
845.2073 | 198.6598 | 238.5563 | 218.7041
846.1917 | 198.3015 | 238.4519 | 219.0533
847.1917 | 196.8768 | 237.8324 | 219.3924
848.1917 | 196.0521 | 237.7695 | 218.9119
849.1917 | 195.9398 | 237.1381 | 218.7353
850.1917 | 196.0478 | 237.3321 | 218.859
851.1917 | 197.0052 | 238.1268 | 218.2111
852.1917 | 196.6486 | 238.1875 | 218.3071
853.1917 | 197.2141 | 238.1971 | 218.9826
854.1917 | 198.1978 | 238.6424 | 220.2996
855.1917 | 198.7068 | 239.1072 | 220.2701
856.1917 | 198.7039 | 239.2385 | 220.305
857.1917 | 199.2829 | 240.121 | 220.0186
858.1917 | 199.73 | 241.5016 | 220.5236
859.1917 | 199.9327 | 241.4659 | 220.8612
860.1917 | 199.2482 | 241.308 | 221.044
861.1917 | 199.0011 | 240.5737 | 220.4563
862.1917 | 199.5395 | 240.2458 | 220.3374
863.1917 | 200.098 | 241.9343 | 219.9202
864.1917 | 200.8988 | 242.2154 | 220.6612
865.1917 | 201.2298 | 242.5288 | 221.3415
866.1917 | 201.3783 | 242.5801 | 220.7231
867.1917 | 201.6972 | 242.6733 | 221.0915
868.1917 | 201.4125 | 241.2576 | 222.1211
869.1917 | 200.5932 | 240.3334 | 221.7873
870.1917 | 199.8079 | 239.2492 | 221.2039
871.1917 | 199.5916 | 238.7687 | 220.3253
872.1917 | 199.4319 | 238.3062 | 220.138
873.1917 | 199.1749 | 237.9024 | 219.6783
874.1917 | 199.5625 | 238.5158 | 220.146
875.1917 | 199.3759 | 238.3743 | 220.4509
876.1917 | 200.5354 | 238.8754 | 221.1522
877.1917 | 200.3072 | 239.3211 | 220.9192
878.1917 | 200.4865 | 237.9415 | 220.5573
879.1917 | 200.2225 | 237.2593 | 220.6065
880.1917 | 199.8305 | 237.3776 | 220.6327
881.1917 | 199.4703 | 236.4905 | 220.3285
882.2073 | 199.6755 | 236.2137 | 220.8317
883.1917 | 200.667 | 236.5426 | 220.8826
884.1917 | 200.4683 | 236.7932 | 220.1821
885.1917 | 199.9167 | 236.6264 | 220.1074
886.1917 | 200.4053 | 237.3982 | 220.0828
887.1917 | 200.5551 | 238.6831 | 220.0531
888.1917 | 201.6419 | 240.5853 | 221.8903
889.1917 | 204.9072 | 242.9588 | 222.5061
890.1917 | 206.8564 | 244.2936 | 225.423
891.1917 | 207.9435 | 244.8721 | 225.9146
892.1917 | 207.4881 | 245.0077 | 228.3656
893.1917 | 208.7661 | 245.0007 | 230.0291
894.1917 | 210.995 | 245.8711 | 229.5041
895.1917 | 214.6943 | 246.8952 | 231.9505
896.1917 | 215.4222 | 247.7516 | 232.0097
897.1917 | 215.2512 | 248.0332 | 231.8415
898.1917 | 215.1422 | 248.7865 | 232.8079
899.1917 | 215.256 | 248.7654 | 231.9888
900.1917 | 214.2716 | 248.7789 | 231.6014
901.1917 | 214.5395 | 248.9105 | 231.7488
902.1917 | 214.8204 | 249.3398 | 230.5964
903.1917 | 213.9644 | 250.567 | 229.9527
904.1917 | 213.1384 | 249.2127 | 229.2392
905.1917 | 212.1388 | 248.585 | 229.1864
906.1917 | 212.1095 | 247.8387 | 229.3604
907.1917 | 211.5684 | 248.199 | 229.4502
908.1917 | 210.8846 | 249.0746 | 230.0713
909.1917 | 210.1166 | 249.7601 | 231.3103
910.1917 | 209.6077 | 250.7065 | 231.921
911.1917 | 209.7227 | 251.4717 | 231.4088
912.2073 | 208.675 | 252.4002 | 231.4415
913.1917 | 208.6875 | 252.8358 | 231.358
914.1917 | 209.4065 | 254.3362 | 232.2105
915.1917 | 208.6307 | 255.5423 | 233.3607
916.1917 | 209.9256 | 256.3124 | 233.6173
917.1917 | 210.4358 | 257.2233 | 234.4758
918.1917 | 209.7482 | 257.3553 | 235.7
919.1917 | 208.5688 | 256.9044 | 235.4713
920.1917 | 207.6855 | 257.7698 | 235.4751
921.1917 | 207.3298 | 258.5862 | 235.3447
922.1917 | 208.0419 | 258.9987 | 235.7718
923.1917 | 208.1257 | 258.3725 | 235.7036
924.1917 | 208.9676 | 258.5102 | 236.3486
925.1917 | 209.3539 | 258.4016 | 235.6837
926.1917 | 209.8142 | 260.4663 | 235.5466
927.1917 | 213.8724 | 262.901 | 238.8864
928.1917 | 215.6737 | 263.7826 | 240.8291
929.1917 | 215.7798 | 265.4983 | 240.7353
930.1917 | 215.6785 | 267.161 | 242.3108
931.1917 | 217.8976 | 268.4995 | 243.6362
932.1917 | 218.9973 | 269.2934 | 244.6255
933.1917 | 221.9602 | 270.1139 | 244.9812
934.1917 | 223.4844 | 272.462 | 245.4616
935.1917 | 223.259 | 273.9327 | 246.5889
936.1917 | 223.2148 | 273.7577 | 246.9894
937.1917 | 224.4644 | 273.7374 | 246.9449
938.1917 | 228.8008 | 276.3241 | 248.1318
939.1917 | 229.8349 | 277.5502 | 248.0204
940.1917 | 231.0608 | 277.6198 | 247.6004
941.1917 | 233.618 | 278.5805 | 246.9362
942.1917 | 235.1001 | 279.6406 | 247.6901
943.1917 | 234.3596 | 280.4029 | 246.7211
944.1917 | 233.4688 | 280.2787 | 245.3611
945.1917 | 233.0919 | 280.9687 | 246.4868
946.1917 | 232.5736 | 281.7755 | 246.938
947.1917 | 233.4551 | 282.8051 | 247.1581
948.1917 | 232.6892 | 284.0919 | 248.2299
949.1917 | 231.8191 | 284.3666 | 247.4574
950.1917 | 230.8702 | 283.597 | 248.7842
951.1917 | 230.0931 | 283.4851 | 249.4754
952.1917 | 229.2838 | 283.2761 | 250.077
953.1917 | 229.5787 | 283.4265 | 250.4114
954.1917 | 228.9257 | 284.5884 | 251.6118
955.1917 | 228.5117 | 283.7648 | 252.2195
956.1917 | 227.2648 | 282.4583 | 251.9787
957.1917 | 225.9667 | 280.8714 | 252.0016
958.1917 | 226.9889 | 281.3859 | 251.3202
959.1917 | 226.2463 | 280.8093 | 250.8508
960.1917 | 226.0789 | 280.642 | 250.4459
961.1917 | 225.8285 | 280.9143 | 250.8997
962.1917 | 227.2286 | 281.5869 | 251.0127
963.1917 | 227.2352 | 281.1702 | 252.2409
964.1917 | 226.1432 | 279.9471 | 251.485
965.1917 | 225.2566 | 278.2049 | 250.8179
966.1917 | 223.9753 | 278.1339 | 250.6926
967.1917 | 223.831 | 279.5895 | 249.9183
968.1917 | 225.1484 | 279.6293 | 251.2275
969.1917 | 226.4416 | 279.2322 | 250.3838
970.1917 | 227.8009 | 280.1698 | 250.4633
971.1917 | 229.7145 | 282.2558 | 251.0151
972.2073 | 234.247 | 283.2191 | 252.7294
973.1917 | 234.9335 | 285.1688 | 255.3762
974.1917 | 236.5455 | 285.3011 | 256.6327
975.1917 | 238.575 | 285.7304 | 256.736
976.1917 | 240.1374 | 287.9127 | 256.5933
977.1917 | 239.5318 | 288.9108 | 257.8794
978.1917 | 240.5175 | 288.7883 | 258.792
979.1917 | 240.3941 | 288.9074 | 257.8091
980.1917 | 242.0466 | 290.5199 | 258.49
981.1917 | 242.9202 | 291.5268 | 257.9165
982.1917 | 241.3979 | 291.979 | 259.5469
983.1917 | 241.5638 | 292.4941 | 260.9796
984.1917 | 240.445 | 291.0588 | 260.5507
985.1917 | 239.8702 | 290.1895 | 260.0031
986.1917 | 239.6661 | 290.9678 | 258.8194
987.1917 | 240.3971 | 291.8316 | 257.8758
988.1917 | 239.7026 | 292.02 | 258.5416
989.1917 | 239.3174 | 291.6646 | 258.1895
990.1917 | 238.4973 | 291.4682 | 258.0125
991.1917 | 238.4308 | 290.9322 | 257.4444
992.1917 | 237.8422 | 290.8718 | 256.7493
993.1917 | 237.6413 | 290.0697 | 256.6784
994.1917 | 237.8101 | 290.307 | 256.9401
995.1917 | 236.277 | 289.9219 | 257.3319
996.1917 | 236.6538 | 290.5382 | 257.4575
997.1917 | 237.0601 | 291.655 | 258.6562
998.1917 | 237.896 | 293.1094 | 258.8738
999.1917 | 240.7547 | 295.1368 | 260.7895
1000.1917 | 241.6408 | 295.574 | 262.0106
1001.1917 | 241.0357 | 294.6901 | 261.4154
1002.1917 | 240.8283 | 294.614 | 260.8867
1003.1917 | 240.2963 | 293.679 | 260.7357
1004.1917 | 240.3439 | 294.3227 | 260.9145
1005.1917 | 239.1628 | 293.5902 | 259.9899
1006.1917 | 238.5076 | 293.9995 | 259.9022
1007.1917 | 237.5278 | 292.6638 | 259.4347
1008.1917 | 236.3321 | 291.1717 | 258.8847
1009.1917 | 235.7465 | 291.1533 | 259.1549
1010.1917 | 236.2427 | 292.4759 | 261.1654
1011.1917 | 237.1238 | 292.3624 | 262.1749
1012.1917 | 237.9821 | 293.733 | 263.6662
1013.1917 | 239.0115 | 294.455 | 263.8639
1014.1917 | 239.3926 | 294.7413 | 264.3742
1015.1917 | 239.4799 | 295.2001 | 266.6266
1016.1917 | 241.4478 | 295.946 | 268.7512
1017.1917 | 241.675 | 296.578 | 269.1061
1018.1917 | 242.5353 | 297.1382 | 268.7196
1019.1917 | 243.4093 | 298.1015 | 269.3774
1020.1917 | 244.4873 | 299.619 | 270.1901
1021.1917 | 244.2364 | 299.6698 | 269.4631
1022.1917 | 243.8892 | 300.23 | 269.0634
1023.1917 | 243.606 | 299.9573 | 269.051
1024.1917 | 242.8983 | 300.0178 | 267.986
1025.1917 | 242.4982 | 299.9004 | 267.6201
1026.1917 | 242.2018 | 300.1276 | 266.7511
1027.1917 | 242.3287 | 300.0262 | 265.8813
1028.1917 | 242.1492 | 300.8008 | 266.7642
1029.1917 | 244.2839 | 301.1409 | 266.6681
1030.1917 | 243.7193 | 301.2956 | 268.7666
1031.1917 | 242.9735 | 301.6373 | 268.7725
1032.2073 | 245.0391 | 302.0128 | 269.738
1033.1917 | 244.1904 | 301.9211 | 268.5815
1034.1917 | 244.7354 | 301.3844 | 269.6154
1035.1917 | 244.0771 | 300.6654 | 268.7217
1036.1917 | 246.9337 | 301.7926 | 268.3903
1037.1917 | 247.9288 | 302.6654 | 267.1816
1038.1917 | 249.8111 | 304.2676 | 269.6948
1039.1917 | 251.9796 | 305.9108 | 272.1134
1040.1917 | 252.2491 | 307.1307 | 272.8525
1041.1917 | 252.228 | 309.2752 | 273.1033
1042.1917 | 254.1574 | 310.2319 | 273.6741
1043.2073 | 254.664 | 310.7065 | 273.3761
1044.1917 | 253.696 | 310.2525 | 272.4835
1045.1917 | 252.8292 | 310.1002 | 271.6783
1046.1917 | 252.6895 | 311.0168 | 271.1843
1047.1917 | 252.0009 | 311.3421 | 271.1174
1048.1917 | 250.3439 | 309.9746 | 270.318
1049.1917 | 248.6281 | 309.0585 | 270.3908
1050.1917 | 248.4689 | 309.3109 | 271.9988
1051.1917 | 250.471 | 309.8244 | 275.1332
1052.1917 | 250.4505 | 311.1783 | 274.4892
1053.2073 | 249.2675 | 311.073 | 274.3794
1054.1917 | 248.5966 | 310.1847 | 274.7369
1055.1917 | 248.1617 | 311.3393 | 275.359
1056.1917 | 248.7532 | 311.4546 | 274.882
1057.1917 | 248.4536 | 312.5524 | 274.6318
1058.1917 | 248.3932 | 313.6409 | 275.2563
1059.1917 | 247.0962 | 314.8529 | 274.829
1060.1917 | 247.5682 | 315.7385 | 275.2144
1061.1917 | 247.9989 | 315.4627 | 275.4149
1062.1917 | 250.6155 | 315.8385 | 277.0253
1063.2073 | 251.651 | 316.4881 | 277.7196
1064.1917 | 250.9396 | 317.5459 | 276.9624
1065.1917 | 252.8283 | 318.9989 | 280.4598
1066.1917 | 257.6975 | 320.7513 | 281.5073
1067.1917 | 259.5752 | 323.4711 | 283.6178
1068.1917 | 258.3082 | 325.5059 | 283.9582
1069.1917 | 256.8263 | 326.0907 | 283.9176
1070.1917 | 255.9538 | 326.8226 | 284.3981
1071.1917 | 254.7413 | 327.3663 | 284.6604
1072.1917 | 254.6603 | 328.9349 | 286.5164
1073.1917 | 254.4486 | 329.0807 | 286.4166
1074.1917 | 253.8096 | 328.4397 | 287.0179
1075.1917 | 255.5479 | 328.8315 | 287.1978
1076.1917 | 257.3585 | 329.8025 | 288.3965
1077.1917 | 257.8449 | 330.9742 | 289.6876
1078.1917 | 258.4765 | 330.6708 | 289.3278
1079.1917 | 262.2083 | 332.2951 | 290.6515
1080.1917 | 262.6353 | 333.5815 | 292.0674
1081.1917 | 262.7815 | 334.6148 | 291.7953
1082.1917 | 263.7006 | 337.2921 | 291.284
1083.1917 | 266.8999 | 339.622 | 289.6394
1084.1917 | 267.2917 | 340.8838 | 288.4909
1085.1917 | 267.3099 | 342.7793 | 286.9272
1086.1917 | 268.6662 | 345.5373 | 285.0071
1087.1917 | 269.7192 | 347.762 | 283.7371
1088.1917 | 268.5287 | 347.1273 | 282.5359
1089.1917 | 267.6627 | 345.283 | 280.7022
1090.1917 | 267.3376 | 344.4269 | 280.5474
1091.1917 | 267.4558 | 343.5041 | 279.8579
1092.2073 | 270.0924 | 343.2756 | 278.4814
1093.1917 | 269.2493 | 341.3367 | 278.7004
1094.1917 | 270.5779 | 339.7719 | 278.7865
1095.1917 | 269.3447 | 338.4574 | 277.8661
1096.1917 | 269.5926 | 338.1458 | 277.7117
1097.1917 | 269.5024 | 337.8429 | 276.9951
1098.1917 | 268.81 | 338.003 | 276.9095
1099.1917 | 270.0143 | 336.9246 | 276.2108
1100.1917 | 269.9219 | 337.472 | 275.7019
1101.1917 | 269.7342 | 336.0584 | 274.9923
1102.1917 | 271.7973 | 336.0576 | 274.318
1103.1917 | 273.5547 | 337.2328 | 273.2524
1104.1917 | 275.4248 | 337.1416 | 273.2102
1105.1917 | 276.2388 | 338.8854 | 273.8554
1106.1917 | 276.4436 | 340.4152 | 274.3591
1107.1917 | 278.399 | 340.4707 | 274.6072
1108.1917 | 278.1851 | 340.9658 | 273.8151
1109.1917 | 278.5958 | 341.1873 | 274.2301
1110.1917 | 278.7414 | 341.5449 | 273.7761
1111.1917 | 278.4427 | 341.0022 | 274.5414
1112.1917 | 277.2497 | 340.0561 | 274.4063
1113.1917 | 277.1279 | 339.0134 | 273.8586
1114.1917 | 277.9846 | 339.7217 | 274.6934
1115.1917 | 277.7772 | 340.6371 | 274.4288
1116.1917 | 278.0398 | 339.0675 | 275.4048
1117.1917 | 277.1296 | 339.8588 | 275.7425
1118.1917 | 276.4173 | 339.1433 | 275.3375
1119.1917 | 275.4263 | 337.3151 | 274.0127
1120.1917 | 274.6375 | 336.5088 | 274.8681
1121.1917 | 273.7834 | 338.1357 | 275.6639
1122.1917 | 274.2865 | 337.4378 | 276.8996
1123.1917 | 275.1768 | 336.4462 | 277.6225
1124.1917 | 278.5134 | 336.7462 | 279.0217
1125.1917 | 279.0481 | 336.5428 | 279.0378
1126.1917 | 280.884 | 338.5193 | 278.4628
1127.1917 | 280.4538 | 337.6512 | 277.019
1128.1917 | 281.9873 | 337.8358 | 278.9134
1129.1917 | 282.357 | 337.9442 | 279.338
1130.1917 | 279.8799 | 337.4059 | 279.2432
1131.1917 | 277.7856 | 338.2117 | 280.2735
1132.1917 | 277.7369 | 339.249 | 281.053
1133.1917 | 276.8864 | 340.2057 | 281.3463
1134.1917 | 276.2896 | 343.1431 | 282.507
1135.1917 | 275.1924 | 341.9719 | 282.1574
1136.1917 | 274.7039 | 342.4336 | 282.5187
1137.1917 | 274.823 | 343.8213 | 282.6356
1138.1917 | 273.9736 | 345.5252 | 283.0289
1139.1917 | 275.5057 | 346.9614 | 284.9832
1140.1917 | 274.7827 | 346.3552 | 284.9055
1141.1917 | 273.9059 | 345.5831 | 284.8903
1142.1917 | 273.4644 | 344.8394 | 284.9553
1143.1917 | 272.6673 | 344.3629 | 285.0292
1144.1917 | 270.7516 | 342.9892 | 285.6448
1145.1917 | 269.3182 | 345.0609 | 286.4381
1146.1917 | 267.605 | 343.9325 | 285.7713
1147.1917 | 265.5896 | 341.442 | 285.2674
1148.1917 | 265.0596 | 339.4771 | 284.6353
1149.1917 | 263.3177 | 340.5562 | 285.4112
1150.1917 | 262.7315 | 342.3294 | 285.8415
1151.1917 | 262.1702 | 341.2576 | 284.8987
1152.1917 | 262.8245 | 341.4154 | 285.5878
1153.1917 | 262.473 | 339.5632 | 285.65
1154.1917 | 262.1086 | 338.5343 | 286.3751
1155.1917 | 262.0025 | 338.5687 | 287.9163
1156.1917 | 265.0646 | 339.735 | 290.1484
1157.1917 | 266.4708 | 340.17 | 290.2387
1158.1917 | 268.2217 | 340.3705 | 291.1106
1159.1917 | 267.7096 | 341.9908 | 291.6803
1160.1917 | 268.1105 | 342.2064 | 292.897
1161.1917 | 268.3736 | 342.3919 | 292.3685
1162.1917 | 267.4282 | 341.4052 | 293.1388
1163.1917 | 268.1719 | 341.8222 | 293.2451
1164.1917 | 269.6218 | 342.4328 | 295.5002
1165.1917 | 272.2548 | 343.0325 | 296.7145
1166.1917 | 272.5301 | 343.413 | 297.3489
1167.1917 | 275.235 | 345.1778 | 298.822
1168.1917 | 274.5655 | 345.6589 | 299.082
1169.1917 | 275.072 | 346.5015 | 299.9095
1170.1917 | 273.998 | 347.9447 | 299.1979
1171.1917 | 274.0187 | 347.6343 | 298.9214
1172.1917 | 274.309 | 347.8119 | 300.4083
1173.1917 | 274.5 | 347.7392 | 300.904
1174.1917 | 277.2838 | 348.8453 | 301.9612
1175.1917 | 279.1646 | 350.6452 | 302.5904
1176.1917 | 278.428 | 350.8171 | 303.1438
1177.1917 | 278.3025 | 352.0966 | 303.5421
1178.1917 | 278.136 | 353.489 | 304.0492
1179.1917 | 277.676 | 354.3988 | 303.672
1180.1917 | 279.6531 | 355.6554 | 303.9338
1181.1917 | 280.3056 | 355.442 | 303.8586
1182.1917 | 280.0193 | 355.4059 | 302.14
1183.1917 | 282.2404 | 354.4049 | 302.8065
1184.1917 | 281.4998 | 354.4866 | 301.8101
1185.1917 | 281.1097 | 355.2107 | 302.3465
1186.1917 | 281.8336 | 356.0797 | 303.8232
1187.1917 | 282.1234 | 356.2937 | 303.7684
1188.1917 | 281.4554 | 356.7902 | 304.1049
1189.1917 | 283.1492 | 356.7106 | 303.8402
1190.1917 | 284.0917 | 356.5698 | 304.6918
1191.1917 | 285.9896 | 356.6662 | 304.9399
1192.1917 | 284.3074 | 357.3639 | 306.0451
1193.1917 | 285.6715 | 357.9342 | 305.4512
1194.1917 | 286.851 | 358.4025 | 305.8147
1195.1917 | 286.5156 | 358.3306 | 304.8257
1196.1917 | 284.2368 | 357.0449 | 303.6417
1197.1917 | 284.9618 | 356.848 | 302.6849
1198.1917 | 284.2801 | 357.1492 | 303.5724
1199.1917 | 284.0105 | 358.0992 | 303.4335
1200.1917 | 284.0724 | 359.6867 | 302.3901
1201.1917 | 284.7158 | 361.7845 | 304.0247
1202.1917 | 285.0703 | 363.129 | 305.1298
1203.1917 | 285.0001 | 362.8096 | 307.2314
1204.1917 | 286.5246 | 362.8083 | 309.4401
1205.1917 | 286.7257 | 364.5014 | 309.5251
1206.1917 | 286.3223 | 364.8658 | 309.3346
1207.1917 | 286.4849 | 365.4375 | 308.438
1208.1917 | 285.8747 | 363.4537 | 307.6033
1209.1917 | 285.3542 | 362.241 | 307.2995
1210.1917 | 285.9363 | 362.172 | 307.1295
1211.1917 | 284.9343 | 362.2501 | 308.6897
1212.1917 | 284.836 | 362.2819 | 308.6146
1213.1917 | 284.0562 | 362.5695 | 309.3429
1214.1917 | 284.1298 | 363.6769 | 309.1115
1215.1917 | 282.7608 | 364.712 | 309.3686
1216.1917 | 282.4766 | 364.4569 | 307.5407
1217.1917 | 281.772 | 364.4657 | 307.273
1218.1917 | 281.6504 | 364.6497 | 307.3387
1219.1917 | 281.333 | 366.0546 | 308.0104
1220.1917 | 281.9471 | 367.269 | 308.5353
1221.1917 | 283.2317 | 366.4556 | 308.356
1222.1917 | 283.8232 | 366.539 | 309.2562
1223.1917 | 283.4585 | 366.1477 | 308.7831
1224.1917 | 285.6164 | 366.9986 | 308.1132
1225.1917 | 286.0806 | 366.7542 | 309.0115
1226.1917 | 285.5683 | 366.278 | 308.8091
1227.1917 | 285.6189 | 365.2413 | 307.9909
1228.1917 | 284.5616 | 362.5774 | 305.8745
1229.1917 | 285.1153 | 361.9392 | 304.8812
1230.1917 | 284.4145 | 362.6534 | 303.2697
1231.1917 | 284.3796 | 363.3546 | 304.9859
1232.1917 | 284.6884 | 364.4195 | 305.3155
1233.1917 | 285.6701 | 366.1915 | 306.0344
1234.1917 | 285.4432 | 367.6545 | 306.6915
1235.1917 | 286.1819 | 368.0619 | 306.504
1236.1917 | 287.6798 | 368.2853 | 305.997
1237.1917 | 287.6845 | 367.3085 | 306.0382
1238.1917 | 287.8542 | 366.5979 | 306.9948
1239.1917 | 287.8894 | 366.3701 | 308.0101
1240.1917 | 287.7252 | 366.8365 | 307.4946
1241.1917 | 288.1163 | 368.4042 | 309.6366
1242.1917 | 290.0448 | 370.9213 | 310.4671
1243.1917 | 290.6757 | 372.8436 | 312.0634
1244.1917 | 290.4182 | 372.8892 | 311.8153
1245.1917 | 291.5696 | 373.1074 | 313.3305
1246.1917 | 292.834 | 374.0937 | 314.3536
1247.1917 | 293.2829 | 374.6932 | 315.7405
1248.1917 | 293.2477 | 374.2532 | 316.5004
1249.1917 | 293.5572 | 375.1291 | 316.7013
1250.1917 | 292.8743 | 375.4903 | 316.2684
1251.1917 | 293.5051 | 374.8782 | 315.5581
1252.1917 | 293.1023 | 374.1319 | 314.2604
1253.1917 | 293.5676 | 373.4531 | 314.1429
1254.1917 | 293.4123 | 372.7002 | 313.9753
1255.1917 | 293.4636 | 372.4755 | 313.9661
1256.1917 | 292.7568 | 371.9736 | 312.8835
1257.1917 | 294.0438 | 372.098 | 312.6498
1258.1917 | 294.4454 | 372.6626 | 312.8344
1259.1917 | 295.6752 | 373.097 | 314.2489
1260.1917 | 297.8027 | 375.0418 | 315.4201
1261.1917 | 298.1489 | 375.7705 | 317.5424
1262.1917 | 298.2004 | 376.4737 | 317.7147
1263.1917 | 298.8025 | 375.9241 | 316.5132
1264.1917 | 300.4394 | 375.4049 | 316.4802
1265.1917 | 300.6653 | 375.5384 | 316.1122
1266.1917 | 300.1857 | 374.5973 | 314.1781
1267.1917 | 301.7874 | 374.2754 | 313.9797
1268.1917 | 300.6593 | 374.8534 | 315.5445
1269.1917 | 301.8864 | 375.6724 | 315.0645
1270.1917 | 303.2801 | 376.188 | 314.6085
1271.1917 | 304.091 | 375.4766 | 313.5303
1272.1917 | 303.1171 | 374.9181 | 315.7596
1273.1917 | 304.8431 | 376.4956 | 315.7916
1274.1917 | 305.1505 | 380.5354 | 316.3069
1275.1917 | 305.9549 | 382.4407 | 318.429
1276.1917 | 306.1387 | 384.9632 | 318.9564
1277.1917 | 305.2569 | 387.1865 | 319.5483
1278.1917 | 303.7687 | 388.986 | 321.1691
1279.1917 | 305.364 | 390.4431 | 321.3878
1280.1917 | 303.5653 | 389.4001 | 321.468
1281.1917 | 304.5071 | 389.0404 | 321.9178
1282.1917 | 308.062 | 390.9929 | 321.4328
1283.1917 | 308.3226 | 391.4846 | 320.0758
1284.1917 | 307.6844 | 390.8704 | 320.6766
1285.1917 | 306.947 | 391.1086 | 321.9129
1286.1917 | 310.2716 | 393.3872 | 322.5201
1287.1917 | 310.9745 | 393.4741 | 325.1996
1288.1917 | 312.0014 | 392.4585 | 325.4407
1289.1917 | 311.6614 | 392.6186 | 326.0869
1290.1917 | 312.0823 | 392.9901 | 327.3963
1291.1917 | 312.5786 | 392.6508 | 327.4586
1292.1917 | 312.2123 | 392.9483 | 327.8441
1293.1917 | 311.9687 | 393.1874 | 326.8539
1294.1917 | 312.4057 | 394.3138 | 327.6328
1295.1917 | 310.9865 | 395.4629 | 327.4511
1296.1917 | 311.6528 | 394.825 | 327.7634
1297.1917 | 312.6612 | 396.6886 | 328.364
1298.1917 | 311.8689 | 395.3756 | 328.0446
1299.1917 | 312.3484 | 397.1736 | 328.4423
1300.1917 | 313.6131 | 402.7335 | 328.7088
1301.1917 | 313.5018 | 407.4217 | 331.1143
1302.1917 | 314.5882 | 409.0453 | 331.829
1303.1917 | 313.7241 | 408.3651 | 332.6979
1304.1917 | 312.7461 | 410.0442 | 333.9123
1305.1917 | 313.9602 | 411.2832 | 332.473
1306.1917 | 312.4255 | 408.5182 | 332.627
1307.1917 | 312.0189 | 407.3593 | 331.3754
1308.1917 | 315.9976 | 406.4293 | 330.7941
1309.1917 | 317.9187 | 405.6108 | 331.3035
1310.1917 | 320.0051 | 404.2721 | 331.4662
1311.1917 | 321.0765 | 406.8393 | 335.6446
1312.1917 | 321.8687 | 408.4221 | 337.1448
1313.1917 | 322.3831 | 410.1929 | 336.1397
1314.1917 | 324.6952 | 413.1571 | 335.354
1315.1917 | 323.5491 | 413.6962 | 336.0371
1316.1917 | 323.9788 | 415.0162 | 335.9112
1317.1917 | 322.8026 | 417.7844 | 336.7506
1318.1917 | 322.2899 | 418.7995 | 336.7231
1319.1917 | 322.4021 | 420.8274 | 337.7042
1320.1917 | 321.4063 | 423.0523 | 338.2855
1321.1917 | 322.4767 | 425.0794 | 338.1524
1322.1917 | 323.5361 | 425.1141 | 337.0379
1323.1917 | 324.0402 | 426.5891 | 337.746
1324.1917 | 325.7579 | 428.5417 | 336.4361
1325.1917 | 326.7484 | 427.7925 | 336.8972
1326.1917 | 328.3578 | 427.852 | 338.0805
1327.1917 | 327.7031 | 429.6429 | 336.5828
1328.1917 | 327.4781 | 429.3911 | 335.544
1329.1917 | 327.5038 | 427.0094 | 335.5849
1330.1917 | 326.9056 | 425.8683 | 338.0224
1331.1917 | 327.7447 | 426.5702 | 340.5576
1332.1917 | 328.6193 | 426.6041 | 341.9377
1333.1917 | 328.9525 | 424.7302 | 343.2273
1334.1917 | 329.6175 | 422.6342 | 343.4953
1335.1917 | 331.1182 | 430.6813 | 346.0921
1336.1917 | 331.5495 | 432.2929 | 344.2981
1337.1917 | 331.5863 | 432.8393 | 342.9004
1338.1917 | 332.1537 | 432.9827 | 340.6763
1339.1917 | 334.8687 | 431.5795 | 340.2177
1340.1917 | 334.861 | 430.2022 | 340.6241
1341.1917 | 334.1013 | 430.5981 | 341.0163
1342.1917 | 334.9373 | 431.8314 | 339.7915
1343.1917 | 335.6162 | 432.8207 | 339.6522
1344.1917 | 335.4594 | 433.4219 | 338.7458
1345.1917 | 337.5032 | 436.5041 | 339.1671
1346.1917 | 337.1951 | 436.3305 | 338.4605
1347.1917 | 338.8499 | 437.6866 | 340.4163
1348.1917 | 338.8998 | 439.3612 | 341.0485
1349.1917 | 340.0265 | 444.7212 | 342.9956
1350.1917 | 339.7416 | 444.8313 | 343.4131
1351.1917 | 342.8339 | 447.7685 | 344.86
1352.1917 | 343.2418 | 450.9331 | 345.394
1353.1917 | 342.4779 | 449.4037 | 345.8289
1354.1917 | 346.1638 | 450.9596 | 345.9253
1355.1917 | 349.3567 | 451.6801 | 346.44
1356.1917 | 347.9918 | 454.0998 | 345.5092
1357.1917 | 346.1591 | 452.2184 | 342.9066
1358.1917 | 344.5018 | 448.9614 | 340.4225
1359.1917 | 346.8563 | 450.4687 | 339.4429
1360.1917 | 345.7468 | 453.325 | 338.9693
1361.1917 | 346.9311 | 456.4953 | 337.8248
1362.1917 | 347.5352 | 457.7547 | 339.6985
1363.1917 | 346.6623 | 458.9408 | 340.6143
1364.1917 | 348.4914 | 460.4094 | 342.77
1365.1917 | 350.6672 | 461.7333 | 342.4788
1366.1917 | 352.1477 | 461.041 | 341.4582
1367.1917 | 356.7696 | 463.0093 | 342.1319
1368.1917 | 359.7254 | 464.1233 | 344.3282
1369.1917 | 358.6046 | 469.891 | 347.4454
1370.1917 | 359.6896 | 471.8625 | 349.3863
1371.1917 | 361.2706 | 474.2184 | 350.0663
1372.1917 | 361.1247 | 476.4403 | 349.0683
1373.1917 | 360.5641 | 477.0868 | 349.9612
1374.1917 | 361.3833 | 479.2449 | 352.2821
1375.1917 | 362.4173 | 484.3471 | 353.0622
1376.1917 | 362.2538 | 486.1129 | 351.457
1377.1917 | 364.7807 | 492.8324 | 352.0852
1378.1917 | 363.4733 | 496.773 | 352.7926
1379.1917 | 364.7957 | 495.1963 | 354.2169
1380.1917 | 366.7853 | 495.3544 | 356.2828
1381.1917 | 368.4382 | 493.4521 | 359.1796
1382.1917 | 368.5431 | 488.5182 | 359.459
1383.1917 | 367.3627 | 487.9369 | 357.5422
1384.1917 | 365.6406 | 485.4197 | 357.8777
1385.1917 | 366.4411 | 482.1868 | 356.8255
1386.1917 | 365.5289 | 480.3239 | 357.8266
1387.1917 | 367.6834 | 484.557 | 361.5745
1388.1917 | 370.0466 | 485.566 | 361.8831
1389.1917 | 370.8909 | 488.0038 | 364.366
1390.1917 | 370.1666 | 486.8191 | 368.2758
1391.1917 | 369.9481 | 485.5652 | 368.6313
1392.1917 | 371.4768 | 487.7973 | 371.4336
1393.1917 | 373.6199 | 486.3114 | 371.0228
1394.1917 | 373.9742 | 483.0993 | 370.6289
1395.1917 | 374.1133 | 481.7227 | 370.0796
1396.1917 | 376.4674 | 486.9194 | 372.1928
1397.1917 | 376.996 | 491.5318 | 371.6461
1398.1917 | 377.8453 | 499.5113 | 372.9786
1399.1917 | 380.1777 | 503.161 | 374.956
1400.1917 | 380.5057 | 506.4136 | 374.0335
1401.1917 | 379.8627 | 507.4337 | 373.5986
1402.1917 | 379.4724 | 505.2122 | 372.35
1403.1917 | 378.6557 | 509.227 | 373.4915
1404.1917 | 379.2796 | 512.1794 | 378.2056
1405.1917 | 380.2865 | 514.0736 | 378.6288
1406.1917 | 380.2942 | 516.7681 | 377.4506
1407.1917 | 381.9149 | 515.7687 | 378.9055
1408.1917 | 384.1992 | 518.7867 | 379.4452
1409.1917 | 382.1085 | 520.244 | 378.4226
1410.1917 | 381.6242 | 519.1194 | 377.8517
1411.1917 | 384.2717 | 519.2604 | 376.626
1412.1917 | 387.5459 | 518.9076 | 378.1469
1413.1917 | 387.1081 | 519.8598 | 377.8596
1414.1917 | 389.5477 | 521.6456 | 381.9482
1415.1917 | 390.5805 | 524.5956 | 384.0325
1416.1917 | 390.4281 | 524.6161 | 384.0506
1417.1917 | 390.8261 | 529.7861 | 384.3404
1418.1917 | 391.4525 | 530.8358 | 384.3577
1419.1917 | 391.1865 | 531.0861 | 383.1972
1420.1917 | 392.1085 | 536.7634 | 386.1882
1421.1917 | 393.261 | 537.5656 | 385.4274
1422.1917 | 393.9595 | 536.8094 | 383.6664
1423.1917 | 394.2013 | 539.5684 | 384.3054
1424.1917 | 392.2466 | 538.8713 | 383.8627
1425.1917 | 395.3363 | 541.2196 | 382.9273
1426.1917 | 393.3181 | 541.0288 | 383.9216
1427.1917 | 394.7029 | 538.8021 | 385.6336
1428.1917 | 396.3814 | 542.8338 | 386.025
1429.1917 | 396.0859 | 548.6287 | 389.5901
1430.1917 | 395.5363 | 549.1568 | 388.6469
1431.1917 | 396.57 | 552.3269 | 390.3529
1432.1917 | 400.1523 | 553.9003 | 390.4536
1433.1917 | 399.8527 | 554.2066 | 390.4381
1434.1917 | 400.4837 | 554.1748 | 391.2203
1435.1917 | 400.8951 | 557.4748 | 394.1656
1436.1917 | 400.0541 | 559.7583 | 393.0794
1437.1917 | 402.0284 | 561.2745 | 392.263
1438.1917 | 402.9232 | 557.5782 | 392.4394
1439.1917 | 403.969 | 562.0255 | 393.3482
1440.1917 | 403.0697 | 563.2908 | 395.4338
1441.1917 | 403.3159 | 563.7762 | 395.9094
1442.1917 | 406.2919 | 565.5468 | 395.1917
1443.1917 | 406.7818 | 565.8817 | 396.7757
1444.1917 | 406.8076 | 575.4532 | 396.0497
1445.1917 | 407.2954 | 579.9103 | 397.1766
1446.1917 | 406.6794 | 578.3126 | 399.4987
1447.1917 | 406.0307 | 577.3321 | 399.0957
1448.1917 | 407.0077 | 576.3718 | 398.0542
1449.1917 | 407.3028 | 577.0367 | 396.5803
1450.1917 | 409.4238 | 575.5531 | 396.0258
1451.1917 | 410.7839 | 573.0376 | 399.4497
1452.1917 | 410.7434 | 576.5303 | 401.9732
1453.1917 | 410.8679 | 579.6017 | 404.5496
1454.1917 | 410.4844 | 578.9587 | 407.5151
1455.1917 | 410.4256 | 579.5933 | 409.1441
1456.1917 | 409.8483 | 578.7242 | 410.1976
1457.1917 | 410.7978 | 578.4453 | 411.8698
1458.1917 | 409.4322 | 576.6467 | 411.4545
1459.1917 | 409.2214 | 575.4353 | 412.2184
1460.1917 | 410.6096 | 577.9769 | 413.3908
1461.1917 | 411.9533 | 578.3944 | 412.2613
1462.1917 | 414.0597 | 575.4908 | 410.5468
1463.1917 | 413.9876 | 577.959 | 411.3204
1464.1917 | 416.101 | 578.6331 | 412.8993
1465.1917 | 415.0132 | 583.1272 | 413.9748
1466.1917 | 414.8719 | 584.3697 | 417.1631
1467.1917 | 415.0977 | 588.5201 | 416.8623
1468.1917 | 414.4478 | 586.6986 | 418.5021
1469.1917 | 416.3049 | 587.1736 | 419.6823
1470.1917 | 416.3229 | 585.5082 | 418.4892
1471.1917 | 418.1673 | 585.0376 | 418.9034
1472.1917 | 418.252 | 586.5533 | 419.0043
1473.1917 | 419.3258 | 589.2268 | 422.3869
1474.1917 | 420.9936 | 588.0183 | 422.8122
1475.1917 | 422.0183 | 585.9207 | 422.6922
1476.1917 | 420.4127 | 584.0115 | 422.4105
1477.1917 | 422.9837 | 585.244 | 421.9556
1478.1917 | 422.0384 | 582.8886 | 422.2656
1479.1917 | 423.0241 | 582.1625 | 420.6333
1480.1917 | 425.8404 | 581.55 | 419.467
1481.1917 | 428.9745 | 580.3315 | 417.6717
1482.1917 | 428.7161 | 580.5747 | 416.7219
1483.1917 | 429.6384 | 583.3842 | 414.5904
1484.1917 | 431.2459 | 582.626 | 412.4587
1485.1917 | 431.3877 | 582.2537 | 412.4816
1486.1917 | 430.3513 | 582.6555 | 411.809
1487.1917 | 431.876 | 580.4581 | 413.7697
1488.1917 | 432.0604 | 581.8898 | 414.2889
1489.1917 | 433.1923 | 583.5074 | 412.1521
1490.1917 | 433.34 | 583.028 | 413.7443
1491.1917 | 434.9329 | 583.645 | 414.8787
1492.1917 | 434.3284 | 583.9595 | 414.536
1493.1917 | 434.9865 | 586.0254 | 412.8987
1494.1917 | 436.0279 | 591.3437 | 414.4972
1495.1917 | 434.4597 | 589.9792 | 416.0222
1496.1917 | 434.6558 | 589.3784 | 418.5666
1497.1917 | 434.7397 | 590.7018 | 420.8845
1498.1917 | 433.7006 | 588.515 | 418.9781
1499.1917 | 433.8117 | 590.5543 | 417.8047
1500.1917 | 434.7768 | 588.1167 | 419.3218
1501.1917 | 436.8846 | 586.7259 | 421.2221
1502.1917 | 436.1811 | 588.4902 | 421.1115
1503.1917 | 436.6105 | 591.2085 | 420.6508
1504.1917 | 433.7784 | 587.2173 | 421.6143
1505.1917 | 432.9312 | 588.3649 | 421.1716
1506.1917 | 432.9153 | 591.0233 | 421.9654
1507.1917 | 434.5984 | 591.2292 | 424.0382
1508.1917 | 434.3405 | 589.8072 | 424.2082
1509.1917 | 433.6477 | 586.8205 | 425.1104
1510.1917 | 433.4636 | 586.4268 | 426.5541
1511.1917 | 433.6836 | 586.07 | 427.1087
1512.1917 | 434.5333 | 585.0577 | 428.6175
1513.1917 | 434.5191 | 588.0627 | 427.7207
1514.1917 | 435.6536 | 585.933 | 427.7815
1515.1917 | 435.5869 | 586.119 | 427.138
1516.1917 | 437.8355 | 588.6338 | 426.5856
1517.1917 | 437.8362 | 592.5489 | 428.0579
1518.1917 | 437.6118 | 593.2726 | 429.2306
1519.1917 | 440.2123 | 592.2275 | 430.9036
1520.1917 | 440.7314 | 589.3211 | 432.0759
1521.1917 | 440.7918 | 587.9113 | 433.1376
1522.1917 | 441.0189 | 592.2048 | 431.7606
1523.1917 | 445.2715 | 596.6978 | 431.9977
1524.1917 | 445.0911 | 597.9656 | 431.0067
1525.1917 | 448.1277 | 600.3895 | 431.108
1526.1917 | 447.4958 | 595.5886 | 433.8212
1527.1917 | 446.9624 | 594.4988 | 436.4213
1528.1917 | 447.1114 | 593.0313 | 441.0224
1529.1917 | 447.6895 | 592.3879 | 443.2744
1530.1917 | 448.2234 | 589.8317 | 445.3036
1531.1917 | 448.0156 | 590.4502 | 446.2695
1532.1917 | 448.1784 | 588.9626 | 444.3958
1533.1917 | 450.5719 | 592.4274 | 444.2379
1534.1917 | 451.2703 | 593.7254 | 443.4808
1535.1917 | 451.0278 | 593.7662 | 444.1542
1536.1917 | 451.318 | 594.6644 | 445.07
1537.1917 | 451.6531 | 594.3401 | 444.9388
1538.1917 | 451.4795 | 596.033 | 446.1035
1539.1917 | 452.1868 | 598.4075 | 447.172
1540.1917 | 454.9521 | 596.7977 | 446.2512
1541.1917 | 454.7481 | 598.8134 | 445.0481
1542.1917 | 454.9326 | 599.6523 | 445.2978
1543.1917 | 455.3708 | 602.6501 | 443.7849
1544.1917 | 456.993 | 608.3958 | 442.5836
1545.1917 | 459.5522 | 606.9896 | 442.1808
1546.1917 | 458.2911 | 609.6519 | 443.6474
1547.1917 | 457.2252 | 615.7584 | 440.7207
1548.1917 | 457.5054 | 622.7731 | 441.2522
1549.1917 | 459.5536 | 620.6293 | 439.1213
1550.1917 | 460.5644 | 620.3422 | 439.3661
1551.1917 | 462.6341 | 620.5799 | 440.3649
1552.1917 | 462.905 | 624.3195 | 438.9639
1553.1917 | 462.6364 | 624.045 | 437.7805
1554.1917 | 462.5134 | 623.091 | 436.6659
1555.1917 | 463.1688 | 622.9582 | 434.0122
1556.1917 | 466.3712 | 621.3501 | 433.6997
1557.1917 | 467.3979 | 620.2521 | 434.2129
1558.1917 | 469.6246 | 621.6286 | 432.9298
1559.1917 | 473.6131 | 618.3869 | 432.8474
1560.1917 | 475.2385 | 620.0643 | 431.6168
1561.1917 | 475.6367 | 620.9473 | 430.9764
1562.1917 | 475.4445 | 622.1302 | 431.331
1563.1917 | 477.2773 | 621.6588 | 433.4366
1564.1917 | 476.5406 | 621.1479 | 434.9082
1565.2073 | 477.628 | 620.7277 | 438.3058
1566.1917 | 479.6892 | 620.1795 | 439.1257
1567.1917 | 479.2191 | 619.7741 | 439.64
1568.1917 | 478.967 | 619.9181 | 440.6721
1569.1917 | 478.4843 | 619.6561 | 442.75
1570.1917 | 480.1649 | 619.9938 | 443.8862
1571.1917 | 481.9821 | 620.4057 | 443.7487
1572.1917 | 481.8706 | 621.5488 | 444.7113
1573.1917 | 484.0225 | 623.5953 | 445.7176
1574.1917 | 486.7885 | 624.4603 | 446.6861
1575.1917 | 488.8643 | 624.9558 | 447.0428
1576.1917 | 489.2734 | 624.9197 | 447.6538
1577.1917 | 490.6875 | 626.6546 | 450.6306
1578.1917 | 491.8725 | 627.2973 | 452.3617
1579.1917 | 492.6153 | 627.1356 | 452.6744
1580.1917 | 492.5066 | 625.8211 | 453.2776
1581.1917 | 495.2225 | 624.2812 | 453.4841
1582.1917 | 496.4245 | 623.774 | 454.311
1583.1917 | 498.0994 | 623.4352 | 455.3077
1584.1917 | 499.6896 | 624.8932 | 457.0681
1585.1917 | 499.5107 | 623.4517 | 457.9381
1586.1917 | 499.9664 | 622.5934 | 461.1845
1587.1917 | 500.3117 | 621.0791 | 463.8787
1588.1917 | 497.8949 | 621.518 | 465.2091
1589.1917 | 499.2419 | 623.6644 | 465.7099
1590.1917 | 500.4469 | 624.7943 | 465.7405
1591.1917 | 500.421 | 623.7642 | 468.2631
1592.1917 | 501.8523 | 621.6293 | 469.4303
1593.1917 | 501.4988 | 619.6697 | 470.4556
1594.1917 | 501.5007 | 619.5096 | 472.5589
1595.1917 | 501.3981 | 618.4734 | 475.6145
1596.1917 | 501.4718 | 614.4899 | 477.6734
1597.1917 | 500.2494 | 616.565 | 477.9412
1598.1917 | 501.6301 | 618.8477 | 478.0195
1599.1917 | 503.5043 | 623.8883 | 479.8994
1600.1917 | 501.9576 | 624.5161 | 481.7778
1601.1917 | 502.9322 | 628.2643 | 484.8697
1602.1917 | 504.0389 | 632.0237 | 485.6137
1603.1917 | 506.5927 | 629.9058 | 486.7278
1604.1917 | 506.2343 | 629.6361 | 486.807
1605.1917 | 506.8492 | 627.3573 | 488.5995
1606.1917 | 505.3183 | 627.8736 | 492.7573
1607.1917 | 504.6419 | 625.9426 | 496.0799
1608.1917 | 502.9699 | 626.096 | 499.4455
1609.1917 | 501.9048 | 628.4107 | 500.4581
1610.1917 | 503.0713 | 628.4491 | 502.2419
1611.1917 | 502.8888 | 628.084 | 504.2202
1612.1917 | 503.8727 | 627.9014 | 505.1726
1613.1917 | 506.2203 | 625.989 | 507.5805
1614.1917 | 505.3723 | 624.5051 | 508.3137
1615.1917 | 505.8761 | 626.0145 | 507.5786
1616.1917 | 505.842 | 628.0334 | 510.3102
1617.1917 | 508.3186 | 628.2244 | 511.9766
1618.1917 | 507.8237 | 628.6403 | 512.401
1619.1917 | 508.2752 | 632.7544 | 511.3565
1620.1917 | 510.258 | 631.972 | 513.4399
1621.1917 | 510.1881 | 630.7801 | 515.7047
1622.1917 | 510.3018 | 629.185 | 513.8814
1623.1917 | 511.6719 | 628.6662 | 512.2118
1624.1917 | 512.4647 | 627.4687 | 509.8059
1625.1917 | 512.9768 | 627.6999 | 510.7833
1626.1917 | 515.5631 | 627.9946 | 510.8101
1627.1917 | 516.1026 | 626.9655 | 510.3065
1628.1917 | 515.8986 | 628.348 | 509.7651
1629.1917 | 517.3633 | 628.9528 | 511.3636
1630.1917 | 519.1249 | 630.5334 | 512.2872
1631.1917 | 519.3792 | 629.0329 | 512.4264
1632.1917 | 519.0314 | 628.8235 | 515.1242
1633.1917 | 519.0728 | 628.8209 | 515.4238
1634.1917 | 522.4613 | 626.7268 | 515.3741
1635.1917 | 523.5219 | 626.7259 | 515.5841
1636.1917 | 523.638 | 625.9491 | 515.6111
1637.1917 | 523.949 | 626.7855 | 514.2706
1638.1917 | 525.7942 | 624.8805 | 515.7228
1639.1917 | 526.147 | 625.0349 | 516.1891
1640.1917 | 526.9852 | 626.1392 | 515.528
1641.1917 | 528.2864 | 632.1416 | 513.1719
1642.1917 | 530.7614 | 632.5245 | 514.2116
1643.1917 | 529.4972 | 629.1739 | 515.0643
1644.1917 | 530.3436 | 626.2751 | 515.7673
1645.1917 | 531.5117 | 629.4725 | 514.7727
1646.1917 | 531.9626 | 628.5432 | 516.7418
1647.1917 | 533.0789 | 628.2319 | 518.9892
1648.1917 | 534.5475 | 628.2135 | 520.7899
1649.1917 | 534.1352 | 626.4957 | 521.8295
1650.1917 | 532.9399 | 626.3728 | 522.0339
1651.1917 | 534.3487 | 628.7029 | 521.556
1652.1917 | 535.1269 | 629.9798 | 521.2714
1653.1917 | 533.5182 | 631.5517 | 519.6864
1654.1917 | 535.1024 | 628.5893 | 520.0973
1655.1917 | 537.7025 | 632.7784 | 519.2957
1656.1917 | 538.2936 | 635.2694 | 519.0211
1657.1917 | 538.9165 | 634.1301 | 518.7003
1658.1917 | 540.776 | 632.1936 | 520.1702
1659.1917 | 544.2602 | 633.5662 | 522.8588
1660.1917 | 545.6251 | 633.7547 | 523.3271
1661.1917 | 546.3188 | 631.3723 | 526.4329
1662.1917 | 547.5396 | 632.0233 | 527.6244
1663.1917 | 549.4707 | 632.2881 | 530.2294
1664.1917 | 549.3466 | 629.4349 | 532.6701
1665.1917 | 550.653 | 630.1017 | 532.5349
1666.1917 | 552.222 | 628.1027 | 534.0929
1667.1917 | 553.2981 | 627.0137 | 535.1112
1668.1917 | 554.0246 | 629.3835 | 535.8554
1669.1917 | 554.0399 | 628.3219 | 537.1914
1670.1917 | 555.7172 | 626.4681 | 538.8374
1671.1917 | 557.6976 | 627.6874 | 538.4472
1672.1917 | 563.3272 | 634.6582 | 537.2374
1673.1917 | 569.1293 | 639.2171 | 535.176
1674.1917 | 575.5909 | 643.4893 | 533.7378
1675.1917 | 578.0349 | 646.0675 | 532.0074
1676.1917 | 578.7016 | 643.3693 | 535.1417
1677.1917 | 580.8649 | 643.7074 | 539.6663
1678.1917 | 581.6307 | 642.1404 | 541.6198
1679.1917 | 581.875 | 643.6391 | 540.9024
1680.1917 | 583.8789 | 646.2041 | 542.5163
1681.1917 | 582.4808 | 645.2609 | 546.1711
1682.1917 | 582.0448 | 643.7447 | 547.9613
1683.1917 | 582.0394 | 641.8334 | 551.9921
1684.1917 | 580.2567 | 639.7028 | 551.0325
1685.1917 | 580.4122 | 637.8102 | 552.7298
1686.1917 | 581.9927 | 638.7133 | 555.0487
1687.1917 | 583.9778 | 638.8042 | 552.6444
1688.1917 | 582.9601 | 638.5384 | 553.8983
1689.1917 | 580.9197 | 635.1655 | 556.3977
1690.1917 | 580.2162 | 634.3907 | 560.2555
1691.1917 | 578.7806 | 636.9413 | 560.0831
1692.1917 | 579.5862 | 635.7952 | 561.0145
1693.1917 | 580.4619 | 633.3569 | 560.823
1694.1917 | 581.5981 | 634.2414 | 559.9324
1695.1917 | 583.7182 | 634.2236 | 561.3164
1696.1917 | 582.9523 | 639.3613 | 563.0679
1697.1917 | 584.5517 | 650.5332 | 562.0079
1698.1917 | 586.002 | 647.7618 | 562.3314
1699.1917 | 585.1479 | 645.0491 | 567.9511
1700.1917 | 587.4948 | 646.9854 | 571.521
1701.1917 | 586.53 | 646.6501 | 570.8318
1702.1917 | 586.5963 | 645.6758 | 568.3492
1703.1917 | 587.381 | 644.3028 | 565.8623
1704.1917 | 586.303 | 641.3709 | 566.2003
1705.1917 | 587.4992 | 643.775 | 566.3893
1706.1917 | 588.0126 | 642.7338 | 566.2759
1707.1917 | 589.1695 | 644.5046 | 566.6233
1708.1917 | 588.8058 | 642.7118 | 566.4108
1709.1917 | 590.686 | 649.8855 | 566.2015
1710.1917 | 587.9574 | 646.6922 | 564.3937
1711.1917 | 586.908 | 645.7015 | 564.5341
1712.1917 | 587.8079 | 647.0341 | 563.4579
1713.1917 | 587.8941 | 643.8741 | 563.7034
1714.1917 | 587.8399 | 640.1438 | 561.7174
1715.1917 | 586.7711 | 638.9717 | 560.0425
1716.1917 | 587.5623 | 641.8048 | 559.0767
1717.1917 | 588.7725 | 647.2149 | 557.8904
1718.1917 | 588.532 | 645.325 | 559.5102
1719.1917 | 589.5396 | 648.0799 | 560.9944
1720.1917 | 588.9616 | 647.7819 | 561.3979
1721.1917 | 592.1441 | 646.2205 | 561.544
1722.1917 | 590.4316 | 647.4187 | 563.5254
1723.1917 | 593.7201 | 648.8454 | 565.137
1724.1917 | 593.848 | 650.7 | 570.0854
1725.1917 | 592.5009 | 648.1614 | 570.727
1726.1917 | 594.4421 | 648.673 | 570.5447
1727.1917 | 594.0295 | 646.0983 | 572.0003
1728.1917 | 594.2146 | 648.6061 | 575.2382
1729.1917 | 597.4274 | 646.5559 | 576.6099
1730.1917 | 594.1446 | 643.9156 | 576.3442
1731.1917 | 594.9087 | 645.1571 | 578.9031
1732.1917 | 594.0433 | 643.3931 | 582.7186
1733.1917 | 593.1029 | 646.9727 | 580.5474
1734.1917 | 593.037 | 643.1064 | 577.3177
1735.1917 | 591.6379 | 643.9813 | 576.0332
1736.1917 | 590.8691 | 640.032 | 573.7038
1737.1917 | 592.7531 | 642.091 | 577.7053
1738.1917 | 592.3777 | 642.3937 | 575.345
1739.1917 | 593.1548 | 641.1944 | 576.2779
1740.1917 | 592.8556 | 639.3571 | 580.9758
1741.1917 | 592.2477 | 643.7529 | 584.4894
1742.1917 | 590.3833 | 642.3866 | 586.9236
1743.1917 | 590.0689 | 642.059 | 587.5675
1744.1917 | 591.7491 | 644.5079 | 591.9781
1745.1917 | 599.2493 | 642.8681 | 589.6368
1746.1917 | 594.8351 | 642.7749 | 587.6843
1747.1917 | 595.1888 | 643.9929 | 591.1359
1748.1917 | 597.4628 | 643.5699 | 591.755
1749.1917 | 596.6083 | 645.3689 | 592.0797
1750.1917 | 595.5055 | 646.4825 | 592.8211
1751.1917 | 594.2398 | 646.3528 | 595.3469
1752.1917 | 592.4017 | 646.6512 | 593.4163
1753.1917 | 595.4566 | 647.6563 | 596.1076
1754.1917 | 596.0269 | 646.3055 | 598.8332
1755.1917 | 597.4988 | 648.9584 | 597.9658
1756.1917 | 596.7605 | 648.0082 | 597.6333
1757.1917 | 596.3979 | 646.4793 | 596.9059
1758.1917 | 597.2687 | 648.2437 | 595.8369
1759.1917 | 596.188 | 643.5683 | 594.4173
1760.1917 | 595.4131 | 641.1469 | 594.4965
1761.1917 | 601.8495 | 647.6523 | 594.4758
1762.1917 | 604.8625 | 654.8309 | 593.8795
1763.1917 | 603.4838 | 659.3732 | 595.0554
1764.1917 | 602.6929 | 658.2959 | 594.8799
1765.1917 | 602.7373 | 656.1198 | 593.3263
1766.1917 | 603.8605 | 653.8954 | 592.3759
1767.1917 | 604.111 | 653.6657 | 593.5659
1768.1917 | 603.8018 | 653.2434 | 592.7061
1769.1917 | 603.8786 | 650.8588 | 592.6321
1770.1917 | 609.4347 | 653.1946 | 592.1309
1771.1917 | 606.8511 | 651.2506 | 594.9464
1772.1917 | 606.8463 | 653.9646 | 598.469
1773.1917 | 611.8773 | 664.1342 | 604.7178
1774.1917 | 615.2088 | 663.0291 | 603.0667
1775.1917 | 616.5747 | 664.8822 | 601.5503
1776.1917 | 618.9655 | 660.4908 | 601.4985
1777.1917 | 619.764 | 662.4927 | 603.4093
1778.1917 | 617.9651 | 665.2065 | 603.6502
1779.1917 | 619.0676 | 662.655 | 602.2032
1780.1917 | 615.8095 | 658.7148 | 601.614
1781.1917 | 616.0165 | 658.5913 | 603.2315
1782.1917 | 622.0588 | 662.4961 | 601.4558
1783.1917 | 624.1965 | 665.8685 | 600.3962
1784.1917 | 624.0033 | 664.2617 | 596.9441
1785.1917 | 624.3497 | 664.8417 | 595.7108
1786.1917 | 624.5095 | 666.7553 | 601.9706
1787.1917 | 622.2795 | 666.2239 | 601.8481
1788.1917 | 624.6092 | 665.1303 | 599.9952
1789.1917 | 625.2565 | 662.5364 | 600.1018
1790.1917 | 623.941 | 663.9037 | 602.1438
1791.1917 | 628.2747 | 667.0277 | 603.8212
1792.1917 | 626.8548 | 665.9909 | 604.5575
1793.1917 | 626.9209 | 664.3208 | 602.2254
1794.1917 | 625.3386 | 660.1276 | 603.0271
1795.1917 | 624.4577 | 657.3754 | 603.2599
1796.1917 | 630.7536 | 661.6566 | 608.5025
1797.1917 | 635.9648 | 669.0547 | 614.7459
1798.1917 | 637.1685 | 668.1496 | 611.1334
1799.1917 | 635.4417 | 667.2563 | 614.8448
1800.1917 | 634.5327 | 666.3139 | 616.921
1801.1917 | 633.9973 | 665.268 | 616.5385
1802.1917 | 633.8223 | 664.634 | 615.2989
1803.1917 | 635.0917 | 665.349 | 613.1514
1804.1917 | 635.2519 | 666.3318 | 616.4369
1805.1917 | 637.2443 | 664.4588 | 617.1146
1806.1917 | 637.4852 | 669.213 | 617.3688
1807.1917 | 637.9728 | 673.8516 | 620.5059
1808.1917 | 643.3162 | 680.9878 | 623.2775
1809.1917 | 644.5041 | 679.7183 | 622.6087
1810.1917 | 647.4946 | 680.4554 | 623.1786
1811.1917 | 646.5767 | 676.2815 | 625.1722
1812.1917 | 649.0041 | 676.4502 | 626.6658
1813.1917 | 650.3216 | 677.7137 | 626.1811
1814.1917 | 650.8576 | 674.5538 | 625.5875
1815.1917 | 648.8167 | 671.2057 | 624.1146
1816.1917 | 649.7165 | 671.4141 | 620.0657
1817.1917 | 649.2166 | 669.1094 | 618.4644
1818.1917 | 651.806 | 669.5502 | 617.2908
1819.1917 | 654.3275 | 670.6428 | 614.9204
1820.1917 | 655.1238 | 670.4076 | 610.8939
1821.1917 | 656.7145 | 672.112 | 611.1946
1822.1917 | 658.298 | 673.3142 | 617.9025
1823.1917 | 659.2752 | 669.9012 | 615.0528
1824.1917 | 659.9471 | 669.1759 | 613.5122
1825.1917 | 658.9533 | 668.6786 | 612.7016
1826.1917 | 659.5 | 672.2272 | 612.0984
1827.1917 | 657.5307 | 670.8649 | 611.6674
1828.1917 | 663.5439 | 670.7177 | 611.6444
1829.1917 | 665.0991 | 674.6283 | 609.7939
1830.1917 | 669.6549 | 676.0204 | 607.3951
1831.1917 | 667.5231 | 674.7507 | 607.0078
1832.1917 | 669.5911 | 679.8476 | 617.2806
1833.1917 | 665.8267 | 676.9362 | 616.009
1834.1917 | 662.1769 | 676.7425 | 612.8072
1835.1917 | 660.4261 | 678.4573 | 622.0344
1836.1917 | 665.5315 | 681.085 | 618.9898
1837.1917 | 662.4218 | 679.6454 | 620.6589
1838.1917 | 662.2665 | 679.8191 | 619.2999
1839.1917 | 666.5264 | 680.8262 | 615.6516
1840.1917 | 665.2891 | 678.8499 | 611.8687
1841.1917 | 663.9133 | 678.1728 | 608.7526
1842.1917 | 659.6066 | 673.8104 | 607.0861
1843.1917 | 659.927 | 673.6118 | 608.1272
1844.1917 | 662.5384 | 670.4833 | 607.8157
1845.1917 | 659.8212 | 667.6383 | 608.861
1846.1917 | 661.2536 | 667.3593 | 608.54
1847.1917 | 665.2297 | 668.535 | 609.1301
1848.1917 | 661.9154 | 672.3083 | 613.6674
1849.1917 | 659.8246 | 671.3028 | 613.3024
1850.1917 | 663.2454 | 670.2347 | 614.4952
1851.1917 | 663.9828 | 667.825 | 612.5266
1852.1917 | 664.4052 | 668.3946 | 609.4289
1853.1917 | 662.1953 | 670.6664 | 610.7712
1854.1917 | 664.9439 | 675.1586 | 610.501
1855.1917 | 664.5039 | 673.0411 | 607.4846
1856.1917 | 662.2773 | 671.8973 | 608.8104
1857.1917 | 661.1939 | 671.1958 | 615.2616
1858.1917 | 661.7987 | 671.9378 | 615.2568
1859.1917 | 661.2583 | 671.4466 | 617.2021
1860.1917 | 664.2726 | 672.538 | 613.152
1861.2073 | 663.026 | 672.8636 | 609.4637
1862.1917 | 663.2583 | 675.0042 | 613.2127
1863.2073 | 667.974 | 679.483 | 613.5128
1864.1917 | 665.7118 | 679.6661 | 610.5225
1865.1917 | 666.9695 | 678.973 | 607.1665
1866.1917 | 669.8216 | 679.5825 | 620.2845
1867.1917 | 672.4568 | 686.4434 | 623.842
1868.1917 | 672.5696 | 682.944 | 622.6568
1869.1917 | 672.9119 | 679.8296 | 624.5061
1870.1917 | 674.5803 | 691.4449 | 633.6412
1871.1917 | 673.4098 | 692.5207 | 631.2543
1872.1917 | 671.3104 | 688.5905 | 629.0272
1873.1917 | 672.5983 | 686.4338 | 626.6016
1874.1917 | 672.14 | 685.3794 | 627.7633
1875.1917 | 672.6248 | 681.5299 | 626.068
1876.1917 | 670.9286 | 681.4867 | 625.3594
1877.1917 | 673.0055 | 688.4851 | 629.7441
1878.1917 | 675.0945 | 689.8333 | 636.4536
1879.1917 | 676.041 | 692.6901 | 639.7648
1880.1917 | 677.1653 | 688.9912 | 640.1514
1881.1917 | 674.2153 | 682.93 | 639.2601
1882.1917 | 671.0889 | 679.8888 | 636.3086
1883.1917 | 669.7578 | 677.4627 | 634.4464
1884.1917 | 672.7984 | 679.4423 | 635.1046
1885.1917 | 668.3708 | 679.9675 | 631.8616
1886.1917 | 667.0498 | 676.5149 | 632.0752
1887.1917 | 667.0042 | 680.823 | 637.3545
1888.1917 | 674.7706 | 690.6914 | 651.1113
1889.1917 | 673.7337 | 687.4586 | 646.8348
1890.1917 | 670.7589 | 684.9443 | 647.7012
1891.1917 | 671.8035 | 691.162 | 647.7307
1892.1917 | 675.4122 | 689.4925 | 642.4235
1893.1917 | 673.2003 | 682.5201 | 637.4232
1894.1917 | 675.0395 | 681.8849 | 633.268
1895.1917 | 672.8578 | 681.5112 | 630.7567
1896.1917 | 672.4481 | 677.3396 | 630.8897
1897.1917 | 672.846 | 681.4703 | 635.0042
1898.1917 | 673.2033 | 678.0132 | 630.3095
1899.1917 | 670.2464 | 680.3106 | 630.3447
1900.1917 | 672.0582 | 684.6062 | 629.6544
1901.1917 | 669.3285 | 680.8539 | 631.2712
1902.1917 | 668.4538 | 679.2095 | 634.3012
1903.1917 | 667.8619 | 677.3752 | 636.1475
1904.1917 | 669.9879 | 682.2683 | 639.3955
1905.1917 | 670.2552 | 682.8858 | 638.7257
1906.1917 | 671.8442 | 683.3379 | 644.9766
1907.1917 | 675.0266 | 689.3128 | 649.5019
1908.1917 | 672.5156 | 692.9925 | 647.3947
1909.1917 | 678.9162 | 696.3938 | 646.6573
1910.1917 | 678.9044 | 696.328 | 646.3943
1911.1917 | 677.3266 | 690.9432 | 647.1635
1912.1917 | 677.3203 | 688.1216 | 647.5504
1913.1917 | 676.0334 | 686.8154 | 642.1605
1914.1917 | 673.2537 | 681.6976 | 654.9394
1915.1917 | 670.2099 | 680.2098 | 654.0991
1916.1917 | 670.0188 | 678.202 | 650.983
1917.1917 | 669.3203 | 676.2635 | 650.1322
1918.1917 | 670.6013 | 674.3256 | 647.0296
1919.1917 | 668.3553 | 670.8023 | 640.3967
1920.1917 | 666.0316 | 668.2993 | 639.1668
1921.1917 | 669.3548 | 673.2493 | 646.9194
1922.1917 | 665.1921 | 668.0604 | 643.4287
1923.1917 | 674.395 | 666.9351 | 640.8211
1924.1917 | 675.3574 | 668.7756 | 638.0448
1925.1917 | 679.2603 | 672.8366 | 648.3398
1926.1917 | 676.3589 | 678.4796 | 648.6144
1927.1917 | 672.9524 | 678.0536 | 650.1321
1928.1917 | 678.8513 | 676.7962 | 648.8356
1929.1917 | 677.9362 | 676.7528 | 651.2105
1930.1917 | 684.6268 | 681.8476 | 656.6744
1931.1917 | 686.062 | 683.1199 | 654.1025
1932.1917 | 691.793 | 686.1483 | 652.7719
1933.1917 | 691.4478 | 688.8111 | 656.7989
1934.1917 | 686.4073 | 686.6659 | 656.1325
1935.1917 | 686.5385 | 684.0989 | 653.8785
1936.1917 | 683.4023 | 682.8164 | 651.0231
1937.1917 | 683.98 | 684.6841 | 652.277
1938.1917 | 684.6346 | 685.4294 | 659.1032
1939.1917 | 683.8686 | 683.5947 | 660.2624
1940.1917 | 683.8222 | 688.9958 | 659.7189
1941.1917 | 681.3589 | 686.5896 | 658.2171
1942.1917 | 681.8079 | 686.9757 | 661.4999
1943.1917 | 681.0306 | 682.3318 | 656.5179
1944.1917 | 684.6213 | 680.8845 | 655.4426
1945.1917 | 685.138 | 681.9216 | 651.176
1946.1917 | 680.0488 | 676.7198 | 646.9017
1947.1917 | 678.6778 | 675.1125 | 646.8308
1948.1917 | 678.7739 | 677.7919 | 647.374
1949.1917 | 679.2357 | 684.6226 | 644.6942
1950.1917 | 679.5014 | 689.754 | 643.2536
1951.1917 | 683.6769 | 693.1905 | 645.7411
1952.1917 | 687.6361 | 690.3071 | 648.2868
1953.1917 | 685.9064 | 685.4929 | 648.116
1954.1917 | 689.4516 | 684.5689 | 647.8296
1955.1917 | 691.4849 | 681.7526 | 642.6984
1956.1917 | 694.2678 | 685.9196 | 644.8738
1957.1917 | 690.3718 | 684.8158 | 644.1328
1958.1917 | 687.682 | 684.8488 | 645.4321
1959.1917 | 685.4077 | 684.2905 | 645.3672
1960.1917 | 680.581 | 685.6176 | 645.4612
1961.1917 | 680.9777 | 683.7445 | 644.4372
1962.1917 | 679.8092 | 685.1723 | 645.5883
1963.2073 | 680.191 | 684.8161 | 645.4761
1964.1917 | 678.7682 | 681.3906 | 643.1497
1965.1917 | 677.6544 | 680.2685 | 643.2629
1966.1917 | 677.9251 | 680.0427 | 651.8662
1967.1917 | 672.7612 | 681.1278 | 653.4579
1968.1917 | 673.165 | 680.9409 | 655.9876
1969.1917 | 678.7538 | 682.8836 | 661.5689
1970.1917 | 678.3409 | 684.1203 | 655.4207
1971.1917 | 679.3574 | 686.3146 | 650.1424
1972.1917 | 678.7915 | 688.6046 | 650.2874
1973.1917 | 677.6174 | 683.8683 | 649.4913
1974.1917 | 678.4856 | 686.4155 | 653.9261
1975.1917 | 680.2636 | 688.59 | 651.8641
1976.1917 | 678.5806 | 685.0043 | 658.6136
1977.1917 | 676.9924 | 682.4917 | 653.4201
1978.1917 | 676.9429 | 683.0694 | 652.716
1979.1917 | 681.2646 | 681.1562 | 651.6012
1980.1917 | 684.1754 | 684.6477 | 650.947
1981.1917 | 682.7644 | 682.5386 | 648.1734
1982.1917 | 684.3289 | 678.5416 | 646.9864
1983.1917 | 683.9674 | 681.1947 | 649.9425
1984.1917 | 686.648 | 683.1295 | 667.3511
1985.1917 | 688.8739 | 684.7867 | 665.8859
1986.1917 | 688.0362 | 687.484 | 682.0218
1987.1917 | 688.2454 | 685.5476 | 685.9268
1988.1917 | 692.2834 | 685.491 | 679.4281
1989.1917 | 693.7929 | 690.8428 | 676.3151
1990.1917 | 692.4442 | 691.1842 | 673.789
1991.1917 | 697.3729 | 691.4207 | 672.5215
1992.1917 | 695.6464 | 686.7028 | 672.8885
1993.2073 | 693.1745 | 689.9301 | 668.4575
1994.1917 | 695.5554 | 688.216 | 665.082
1995.1917 | 693.6868 | 687.9584 | 662.9544
1996.1917 | 693.1936 | 689.5728 | 664.9941
1997.1917 | 693.4076 | 692.1812 | 671.2923
1998.1917 | 692.6787 | 692.7573 | 673.6029
1999.1917 | 688.9827 | 687.4281 | 668.8394
2000.1917 | 686.6647 | 684.1796 | 663.7644
2001.1917 | 685.9044 | 685.9402 | 667.8605
2002.1917 | 681.7209 | 683.2701 | 668.015
2003.1917 | 680.3249 | 681.6796 | 662.4708
2004.1917 | 678.6708 | 680.5793 | 661.078
2005.1917 | 676.465 | 679.9295 | 658.9771
2006.1917 | 676.2536 | 679.2253 | 655.2502
2007.1917 | 675.51 | 677.2677 | 653.1276
2008.1917 | 675.8483 | 679.029 | 651.2954
2009.1917 | 675.1384 | 677.7635 | 651.4407
2010.1917 | 672.7102 | 676.463 | 649.7222
2011.1917 | 668.0477 | 675.6077 | 651.1634
2012.1917 | 667.5899 | 677.8922 | 648.1898
2013.1917 | 670.6907 | 681.9963 | 651.4182
2014.1917 | 673.0438 | 682.0415 | 649.8705
2015.1917 | 675.5355 | 683.117 | 648.5531
2016.1917 | 675.1585 | 682.4157 | 652.8972
2017.1917 | 673.8814 | 684.8622 | 654.909
2018.1917 | 680.1136 | 691.9244 | 659.6722
2019.1917 | 677.7392 | 688.0506 | 667.0038
2020.1917 | 674.568 | 683.7843 | 667.3259
2021.1917 | 679.3685 | 683.6835 | 669.0953
2022.1917 | 678.6531 | 684.9639 | 672.4178
2023.2073 | 679.7256 | 686.1363 | 669.3258
2024.1917 | 679.1295 | 684.5665 | 668.3868
2025.1917 | 679.8914 | 686.3086 | 679.0942
2026.1917 | 681.1585 | 693.4161 | 676.9214
2027.1917 | 685.0026 | 691.6296 | 673.0021
2028.1917 | 683.7242 | 695.5968 | 684.7798
2029.1917 | 684.3871 | 695.7696 | 681.5545
2030.1917 | 685.6812 | 694.7235 | 678.8317
2031.1917 | 680.1425 | 688.483 | 674.2162
2032.1917 | 678.9535 | 687.8483 | 670.012
2033.1917 | 682.0702 | 685.6654 | 667.5717
2034.1917 | 681.3854 | 686.9593 | 664.6436
2035.1917 | 682.8255 | 685.111 | 661.8764
2036.1917 | 688.8283 | 684.3135 | 660.2906
2037.1917 | 684.8934 | 682.843 | 660.8634
2038.1917 | 686.0012 | 679.5589 | 663.5626
2039.1917 | 685.4604 | 679.3785 | 667.5167
2040.1917 | 687.8911 | 681.7261 | 673.8072
2041.1917 | 686.2987 | 679.4783 | 674.9548
2042.1917 | 685.4958 | 677.2284 | 670.6176
2043.1917 | 693.271 | 675.0002 | 671.6637
2044.1917 | 695.9802 | 672.6494 | 669.8154
2045.1917 | 700.5035 | 670.2104 | 664.4912
2046.1917 | 701.5365 | 670.0088 | 671.2464
2047.1917 | 699.7536 | 671.7278 | 669.8369
2048.1917 | 705.9917 | 671.0269 | 669.8927
2049.1917 | 704.6663 | 669.3165 | 672.6748
2050.1917 | 711.1444 | 667.6055 | 668.5404
2051.1917 | 709.2984 | 664.357 | 665.3567
2052.1917 | 704.5861 | 664.0765 | 662.5093
2053.1917 | 697.7411 | 662.5835 | 658.9425
2054.1917 | 700.9979 | 661.0871 | 657.282
2055.1917 | 696.6163 | 670.1433 | 662.167
2056.1917 | 690.0302 | 673.1247 | 658.6741
2057.1917 | 683.7242 | 671.5766 | 657.1401
2058.1917 | 684.0043 | 676.7056 | 657.8764
2059.1917 | 682.111 | 678.9828 | 660.6078
2060.1917 | 679.9029 | 676.083 | 667.8745
2061.1917 | 680.6144 | 671.3149 | 671.9169
2062.1917 | 690.4617 | 673.5858 | 670.9538
2063.1917 | 693.6346 | 674.4959 | 668.573
2064.1917 | 691.5192 | 678.5459 | 677.988
2065.1917 | 687.4705 | 685.241 | 687.1844
2066.1917 | 681.0863 | 681.1789 | 685.9083
2067.1917 | 684.883 | 679.5783 | 689.4378
2068.1917 | 686.6918 | 684.4212 | 689.6136
2069.1917 | 683.545 | 679.4772 | 683.1961
2070.1917 | 680.6702 | 679.7681 | 682.4608
2071.1917 | 681.3261 | 681.6849 | 684.8625
2072.1917 | 677.6338 | 677.6497 | 689.0647
2073.1917 | 677.7816 | 679.5069 | 691.9598
2074.1917 | 676.2921 | 675.6586 | 684.4419
2075.1917 | 674.0382 | 674.5842 | 681.7964
2076.1917 | 673.6859 | 673.3937 | 680.7493
2077.1917 | 672.0999 | 668.4476 | 683.1806
2078.1917 | 671.9663 | 668.0486 | 689.6389
2079.1917 | 666.3683 | 670.5008 | 691.005
2080.1917 | 667.5122 | 670.5649 | 698.3492
2081.1917 | 666.9555 | 674.0038 | 696.8185
2082.2073 | 662.8511 | 670.3919 | 701.7303
2083.2073 | 658.6848 | 666.8176 | 693.6034
2084.1917 | 660.629 | 665.149 | 695.1616
2085.1917 | 661.091 | 666.4521 | 694.2425
2086.2073 | 662.4321 | 663.5862 | 691.5973
2087.1917 | 665.8661 | 660.0858 | 695.0659
2088.2073 | 670.187 | 660.5739 | 698.8325
2089.1917 | 662.3116 | 657.2611 | 690.0983
2090.1917 | 666.0363 | 662.5005 | 689.538
2091.1917 | 669.9511 | 659.3622 | 682.9663
2092.1917 | 671.393 | 659.9311 | 685.4995
2093.1917 | 670.0224 | 660.9262 | 687.7313
2094.1917 | 670.796 | 660.8399 | 685.1152
2095.1917 | 667.5121 | 663.9997 | 687.8147
2096.1917 | 670.8658 | 670.4797 | 696.4941
2097.1917 | 671.3833 | 668.7272 | 694.6893
2098.1917 | 677.9419 | 666.438 | 691.5547
2099.1917 | 681.6438 | 671.7129 | 688.0607
2100.1917 | 678.8169 | 670.8141 | 687.9249
2101.1917 | 676.717 | 665.7788 | 684.6225
2102.1917 | 673.9424 | 670.4312 | 684.3693
2103.1917 | 675.1185 | 667.8999 | 679.116
2104.1917 | 681.6577 | 666.9213 | 683.3356
2105.1917 | 676.4366 | 666.3642 | 686.8083
2106.1917 | 675.3593 | 669.6666 | 687.4529
2107.1917 | 675.9023 | 675.44 | 687.0547
2108.1917 | 672.6134 | 675.0239 | 692.5868
2109.1917 | 669.5356 | 674.9446 | 691.524
2110.1917 | 669.2835 | 671.7208 | 684.6778
2111.1917 | 663.4922 | 664.3016 | 679.5937
2112.1917 | 666.9288 | 667.016 | 684.974
2113.2073 | 662.7198 | 664.4971 | 688.519
2114.1917 | 672.9431 | 664.3721 | 697.16
2115.1917 | 669.7518 | 660.3336 | 696.46
2116.1917 | 680.5709 | 657.455 | 689.5366
2117.1917 | 682.8407 | 656.1968 | 681.4196
2118.1917 | 683.6662 | 653.7269 | 677.5979
2119.1917 | 682.1158 | 654.8816 | 682.0235
2120.1917 | 685.1999 | 651.1844 | 689.1309
2121.1917 | 685.03 | 653.0932 | 690.6163
2122.1917 | 689.0395 | 652.0649 | 689.5385
2123.1917 | 685.7904 | 656.571 | 686.8042
2124.1917 | 682.8264 | 654.2703 | 680.8721
2125.1917 | 690.2177 | 653.1236 | 679.8541
2126.1917 | 692.0725 | 651.9227 | 674.1762
2127.1917 | 688.5402 | 649.7477 | 677.5994
2128.1917 | 689.2164 | 648.9983 | 675.9096
2129.1917 | 691.6715 | 653.3378 | 675.42
2130.1917 | 700.2468 | 651.6991 | 674.8887
2131.1917 | 698.2789 | 649.0112 | 673.3188
2132.1917 | 706.1709 | 652.4602 | 675.7214
2133.2073 | 704.3446 | 651.3546 | 677.1414
2134.1917 | 702.7016 | 653.606 | 682.0436
2135.1917 | 702.574 | 657.0955 | 681.6186
2136.1917 | 704.2508 | 659.9239 | 684.773
2137.1917 | 702.8237 | 671.4814 | 691.4338
2138.1917 | 705.1786 | 669.9556 | 691.7952
2139.1917 | 704.6791 | 664.1965 | 695.2162
2140.1917 | 703.2202 | 671.7828 | 694.4118
2141.1917 | 702.6994 | 669.7675 | 690.0826
2142.1917 | 707.1533 | 667.6796 | 689.0865
2143.2073 | 701.6393 | 668.1706 | 690.9276
2144.1917 | 700.5498 | 670.8294 | 697.0085
2145.1917 | 695.6441 | 679.7492 | 693.819
2146.1917 | 691.9573 | 677.0342 | 691.5834
2147.1917 | 691.3778 | 678.0679 | 707.6883
2148.1917 | 686.1357 | 676.2194 | 698.9614
2149.1917 | 683.3769 | 685.7 | 704.5786
2150.1917 | 682.7433 | 687.4687 | 705.9433
2151.1917 | 682.0094 | 694.4295 | 703.8083
2152.1917 | 680.5873 | 686.5102 | 706.6259
2153.1917 | 679.1572 | 684.9831 | 706.8054
2154.1917 | 676.521 | 685.6716 | 710.9981
2155.1917 | 677.6411 | 688.8093 | 714.1074
2156.1917 | 673.9676 | 683.8518 | 709.1628
2157.1917 | 675.116 | 685.3058 | 703.0896
2158.1917 | 678.3672 | 680.3254 | 696.6251
2159.1917 | 680.1189 | 688.5374 | 696.9609
2160.1917 | 675.8915 | 684.3944 | 704.8174
2161.1917 | 674.8651 | 687.2875 | 702.2963
2162.1917 | 672.7706 | 681.8078 | 700.6206
2163.1917 | 673.555 | 674.7633 | 693.2754
2164.1917 | 673.3978 | 669.9992 | 685.2674
2165.1917 | 672.1778 | 665.848 | 678.8402
2166.1917 | 673.8561 | 661.909 | 675.28
2167.1917 | 673.549 | 660.5714 | 674.1666
2168.1917 | 676.5941 | 665.5552 | 677.2394
2169.1917 | 682.5655 | 672.0304 | 680.4064
2170.1917 | 686.5744 | 676.4721 | 685.2527
2171.1917 | 688.9893 | 675.5391 | 691.0341
2172.1917 | 686.6915 | 682.5969 | 698.8492
2173.1917 | 686.1182 | 678.8147 | 703.0404
2174.1917 | 688.5953 | 673.9373 | 709.4209
2175.1917 | 690.0657 | 671.8221 | 707.4831
2176.1917 | 687.865 | 668.9484 | 709.5104
2177.1917 | 688.74 | 673.5309 | 710.4361
2178.1917 | 688.4808 | 677.6902 | 708.5319
2179.1917 | 685.9198 | 679.3257 | 704.3497
2180.1917 | 688.779 | 673.403 | 706.6488
2181.1917 | 689.5514 | 669.1458 | 708.7611
2182.1917 | 694.0908 | 686.3613 | 720.8056
2183.1917 | 689.5536 | 686.855 | 727.9897
2184.1917 | 686.0067 | 689.9507 | 730.1491
2185.1917 | 681.9142 | 684.6254 | 724.8014
2186.1917 | 680.3142 | 687.3641 | 727.3464
2187.1917 | 679.1798 | 687.8823 | 723.636
2188.1917 | 677.7807 | 680.2788 | 715.8792
2189.1917 | 680.4394 | 676.0402 | 718.7355
2190.1917 | 677.6587 | 670.7485 | 716.6741
2191.1917 | 678.7659 | 684.7484 | 721.0846
2192.1917 | 684.8953 | 689.6 | 713.7784
2193.1917 | 693.8538 | 684.4566 | 715.5914
2194.1917 | 701.4149 | 688.5979 | 712.9193
2195.1917 | 701.8653 | 693.571 | 727.1549
2196.1917 | 701.2553 | 697.6996 | 718.0812
2197.1917 | 702.6893 | 693.5702 | 707.9275
2198.1917 | 694.7013 | 684.284 | 699.9978
2199.1917 | 701.8401 | 682.59 | 693.0761
2200.1917 | 702.2394 | 679.3653 | 687.9385
2201.1917 | 701.1383 | 675.942 | 681.4852
2202.1917 | 698.377 | 680.5896 | 680.7021
2203.1917 | 690.8418 | 673.4288 | 676.275
2204.1917 | 696.1065 | 669.2876 | 677.233
2205.1917 | 689.1177 | 666.4824 | 676.2914
2206.1917 | 681.4423 | 670.5713 | 680.0405
2207.1917 | 675.5127 | 667.661 | 676.9393
2208.1917 | 669.2417 | 663.1104 | 672.6456
2209.1917 | 665.0606 | 661.7822 | 675.4023
2210.1917 | 661.4522 | 659.7952 | 669.8507
2211.1917 | 665.3743 | 659.393 | 669.5335
2212.1917 | 676.5656 | 657.3351 | 669.5877
2213.1917 | 685.7098 | 653.4694 | 664.6774
2214.1917 | 688.1139 | 659.1446 | 669.2692
2215.1917 | 688.0286 | 656.9579 | 664.2822
2216.1917 | 685.8426 | 659.4587 | 660.3321
2217.1917 | 685.3386 | 663.1072 | 657.3868
2218.1917 | 688.3985 | 661.5338 | 657.8023
2219.1917 | 691.0643 | 657.5399 | 656.2135
2220.1917 | 696.0053 | 655.6765 | 653.4313
2221.1917 | 694.5606 | 654.5966 | 650.4907
2222.1917 | 691.3092 | 653.5145 | 652.7485
2223.1917 | 698.3049 | 664.2388 | 651.4246
2224.1917 | 707.0422 | 661.3256 | 649.9213
2225.1917 | 713.233 | 660.7815 | 652.3519
2226.1917 | 715.1206 | 660.6618 | 649.8897
2227.1917 | 716.5507 | 667.3803 | 649.6797
2228.1917 | 710.8349 | 678.6056 | 650.5308
2229.1917 | 709.4659 | 683.475 | 653.6471
2230.1917 | 707.3698 | 678.9562 | 653.4957
2231.1917 | 704.0088 | 676.6089 | 662.734
2232.1917 | 704.3404 | 675.7151 | 665.8376
2233.2073 | 706.6835 | 672.5042 | 665.4156
2234.1917 | 705.2707 | 671.687 | 663.223
2235.1917 | 695.9872 | 665.5205 | 659.715
2236.1917 | 694.1026 | 662.7654 | 658.3526
2237.1917 | 690.4561 | 661.4292 | 655.3377
2238.1917 | 686.1164 | 659.4004 | 652.4915
2239.1917 | 691.1909 | 657.4898 | 650.9395
2240.1917 | 686.7465 | 654.1219 | 646.8073
2241.1917 | 687.0269 | 653.8372 | 661.2236
2242.1917 | 692.7535 | 654.7021 | 673.3257
2243.1917 | 694.5515 | 656.9239 | 681.6112
2244.1917 | 691.1089 | 658.8453 | 694.8433
2245.1917 | 697.6079 | 658.8114 | 701.6074
2246.1917 | 702.9572 | 665.223 | 708.4308
2247.1917 | 704.5764 | 664.0941 | 699.9583
2248.1917 | 701.0332 | 662.7097 | 693.6857
2249.1917 | 691.5801 | 659.4655 | 689.8204
2250.1917 | 695.2945 | 658.3602 | 683.2406
2251.1917 | 691.3618 | 655.2468 | 677.5274
2252.1917 | 699.0303 | 661.3146 | 673.7887
2253.1917 | 711.8344 | 659.0949 | 669.0175
2254.1917 | 711.4609 | 657.0752 | 669.2646
2255.1917 | 712.0266 | 660.2308 | 669.1887
2256.1917 | 706.136 | 658.9454 | 669.4675
2257.1917 | 702.9324 | 659.3949 | 682.9094
2258.1917 | 706.7083 | 657.3708 | 681.0273
2259.1917 | 708.9005 | 662.0892 | 686.5086
2260.1917 | 705.8101 | 657.6973 | 697.6974
2261.1917 | 706.3893 | 660.1203 | 704.893
2262.1917 | 706.1954 | 657.89 | 704.0331
2263.2073 | 706.3962 | 656.0407 | 699.0717
2264.1917 | 706.1434 | 658.5216 | 706.5029
2265.1917 | 706.5773 | 657.7905 | 710.359
2266.1917 | 705.0376 | 657.5527 | 712.8949
2267.1917 | 703.4274 | 657.4472 | 706.872
2268.1917 | 708.6379 | 663.7501 | 708.8102
2269.1917 | 710.1474 | 662.9014 | 698.6878
2270.1917 | 719.5764 | 660.9393 | 701.5974
2271.1917 | 721.3503 | 660.7657 | 704.4725
2272.1917 | 724.0412 | 662.2977 | 706.9513
2273.1917 | 722.0907 | 660.4879 | 708.5639
2274.1917 | 715.4824 | 658.4401 | 700.4761
2275.1917 | 714.5562 | 656 | 702.7302
2276.1917 | 725.3317 | 655.8674 | 695.3641
2277.1917 | 724.9158 | 654.7178 | 690.2282
2278.1917 | 725.0239 | 655.3059 | 693.2462
2279.1917 | 728.3533 | 653.5269 | 690.9356
2280.1917 | 730.0311 | 651.6308 | 685.528
2281.1917 | 723.9392 | 651.9882 | 681.4559
2282.1917 | 714.2947 | 651.8681 | 681.9386
2283.1917 | 712.9088 | 651.0457 | 681.869
2284.1917 | 712.1429 | 651.2909 | 680.4038
2285.1917 | 701.3958 | 651.4358 | 677.4956
2286.1917 | 702.0072 | 651.8792 | 672.0969
2287.1917 | 705.6255 | 653.0757 | 673.7105
2288.1917 | 706.4375 | 652.5932 | 673.1359
2289.1917 | 704.392 | 655.1039 | 679.6569
2290.1917 | 695.3256 | 653.8004 | 677.2429
2291.1917 | 689.6125 | 653.9862 | 682.8111
2292.1917 | 683.4786 | 654.6134 | 679.9314
2293.1917 | 678.6364 | 656.0975 | 688.1323
2294.1917 | 688.5006 | 653.8136 | 680.5906
2295.1917 | 686.2137 | 652.4641 | 679.733
2296.1917 | 688.0031 | 651.1988 | 685.3307
2297.1917 | 690.3797 | 650.9409 | 688.8835
2298.1917 | 690.8977 | 648.4095 | 694.7641
2299.1917 | 697.7438 | 650.5364 | 693.0586
2300.1917 | 693.7215 | 651.3501 | 702.4611
2301.1917 | 695.0918 | 650.537 | 703.3508
2302.1917 | 693.2489 | 654.0682 | 695.59
2303.1917 | 694.0278 | 654.6199 | 697.6888
2304.1917 | 695.5292 | 654.9774 | 700.0885
2305.1917 | 693.9763 | 656.0906 | 694.2828
2306.1917 | 698.9599 | 655.2458 | 697.5503
2307.1917 | 697.3979 | 655.8043 | 693.3594
2308.1917 | 698.3166 | 655.8774 | 691.1969
2309.1917 | 699.4183 | 656.4225 | 697.322
2310.1917 | 699.4562 | 655.701 | 693.2179
2311.1917 | 706.2565 | 656.9961 | 693.0968
2312.1917 | 699.4 | 656.6922 | 685.1138
2313.2073 | 703.7057 | 656.7996 | 681.8658
2314.1917 | 701.5699 | 656.8324 | 678.405
2315.1917 | 698.6194 | 656.7205 | 674.4278
2316.1917 | 689.4103 | 654.6032 | 668.6854
2317.1917 | 693.0158 | 652.4969 | 666.0967
2318.1917 | 686.3003 | 652.1371 | 668.3354
2319.1917 | 680.0211 | 649.8089 | 662.4806
2320.1917 | 676.2978 | 649.0978 | 663.8785
2321.1917 | 680.2471 | 652.0562 | 662.5352
2322.1917 | 678.1541 | 653.0053 | 672.2493
2323.2073 | 672.2818 | 651.5953 | 675.4807
2324.1917 | 690.5736 | 649.0581 | 669.3214
2325.1917 | 685.7186 | 646.9385 | 664.5211
2326.1917 | 683.2609 | 644.9768 | 666.4273
2327.1917 | 678.491 | 645.025 | 662.8324
2328.1917 | 673.855 | 643.999 | 659.179
2329.1917 | 683.2661 | 642.5022 | 663.0899
2330.1917 | 676.3503 | 640.9016 | 659.9369
2331.1917 | 674.8026 | 639.9266 | 656.8009
2332.1917 | 673.1119 | 639.4993 | 657.893
2333.1917 | 670.2868 | 638.0706 | 655.6129
2334.1917 | 677.7008 | 637.1971 | 667.4924
2335.1917 | 689.1777 | 637.6635 | 674.6234
2336.1917 | 690.6498 | 641.182 | 673.8252
2337.1917 | 683.4445 | 638.75 | 669.9526
2338.1917 | 689.7619 | 637.6418 | 666.0593
2339.1917 | 711.7184 | 637.8759 | 662.3064
2340.1917 | 713.3873 | 637.5124 | 673.1063
2341.1917 | 714.581 | 638.0492 | 677.5809
2342.1917 | 701.9539 | 638.5162 | 686.8828
2343.1917 | 692.8527 | 637.9002 | 677.4525
2344.1917 | 695.935 | 637.8456 | 673.1853
2345.1917 | 700.3853 | 636.8954 | 665.6775
2346.1917 | 689.4223 | 637.016 | 662.5301
2347.1917 | 686.0131 | 639.8278 | 678.0216
2348.1917 | 687.2008 | 643.0455 | 686.0014
2349.1917 | 683.5618 | 643.7733 | 698.706
2350.1917 | 686.143 | 644.7285 | 699.4975
2351.1917 | 683.3885 | 644.6687 | 691.6311
2352.1917 | 678.4875 | 645.1704 | 695.9955
2353.1917 | 678.0114 | 645.8613 | 697.2024
2354.1917 | 676.0923 | 643.3131 | 686.4992
2355.1917 | 683.7218 | 641.9456 | 691.3865
2356.1917 | 690.8623 | 639.8284 | 686.9153
2357.1917 | 695.7091 | 638.1575 | 694.7199
2358.1917 | 705.2191 | 639.1501 | 700.6193
2359.1917 | 696.6663 | 640.5324 | 691.4221
2360.1917 | 696.1019 | 640.1421 | 693.295
2361.1917 | 694.6649 | 638.9377 | 701.1712
2362.1917 | 695.8207 | 637.4331 | 705.2014
2363.1917 | 712.3866 | 636.7245 | 715.0358
2364.1917 | 712.4042 | 634.7497 | 719.7608
2365.1917 | 720.5961 | 633.7806 | 725.4379
2366.1917 | 716.268 | 633.1228 | 728.8011
2367.1917 | 721.733 | 632.6786 | 729.3624
2368.1917 | 720.5335 | 632.3215 | 732.2071
2369.1917 | 729.0421 | 630.2939 | 733.401
2370.1917 | 731.2771 | 631.8497 | 731.3072
2371.1917 | 723.0896 | 631.9922 | 718.5329
2372.1917 | 713.4864 | 633.2513 | 708.0866
2373.1917 | 702.8635 | 633.6724 | 712.205
2374.1917 | 693.5494 | 635.8632 | 712.0429
2375.1917 | 684.8227 | 634.976 | 704.3336
2376.1917 | 676.3664 | 635.1145 | 710.434
2377.1917 | 670.9393 | 634.4086 | 700.8515
2378.1917 | 665.6422 | 634.1191 | 691.4679
2379.1917 | 671.8783 | 632.7488 | 693.3482
2380.1917 | 685.4626 | 630.6609 | 701.1643
2381.1917 | 691.7709 | 627.2111 | 704.0646
2382.1917 | 699.3965 | 626.7868 | 715.0587
2383.1917 | 703.6642 | 625.9043 | 722.6068
2384.1917 | 708.6205 | 624.2493 | 721.8034
2385.1917 | 716.2791 | 623.3044 | 717.0314
2386.1917 | 713.107 | 623.535 | 717.753
2387.1917 | 710.9572 | 621.6148 | 722.0334
2388.1917 | 705.6666 | 621.8588 | 724.1515
2389.1917 | 700.7157 | 620.942 | 727.156
2390.1917 | 696.5446 | 619.7395 | 729.7516
2391.1917 | 697.1292 | 617.8359 | 728.6786
2392.1917 | 709.0143 | 616.314 | 719.5285
2393.1917 | 702.5831 | 615.3553 | 720.7401
2394.1917 | 697.4849 | 616.4572 | 706.2554
2395.1917 | 692.4466 | 616.0701 | 706.5883
2396.1917 | 687.8807 | 616.4016 | 694.4922
2397.1917 | 683.692 | 616.6575 | 691.5873
2398.1917 | 688.5255 | 617.4012 | 685.0333
2399.1917 | 684.6789 | 615.9981 | 682.5476
2400.1917 | 679.5086 | 614.5355 | 682.5965
2401.1917 | 680.072 | 612.3498 | 685.0028
2402.1917 | 676.3 | 610.9495 | 690.2226
2403.1917 | 688.0136 | 610.7091 | 690.3386
2404.1917 | 692.6664 | 611.9939 | 696.2445
2405.1917 | 685.9419 | 612.8961 | 693.1102
2406.1917 | 690.9352 | 612.5731 | 695.3043
2407.1917 | 700.9018 | 612.9755 | 697.6807
2408.1917 | 707.372 | 613.9377 | 703.4817
2409.1917 | 709.6538 | 611.8772 | 707.9718
2410.1917 | 711.885 | 610.0773 | 716.0455
2411.1917 | 712.8388 | 610.799 | 718.102
2412.1917 | 703.7246 | 611.6736 | 720.276
2413.1917 | 705.6785 | 611.1661 | 719.1734
2414.1917 | 703.8665 | 611.1811 | 713.7328
2415.1917 | 704.9348 | 610.7476 | 712.051
2416.1917 | 696.7062 | 610.5259 | 714.9012
2417.1917 | 690.8864 | 611.3838 | 707.2589
2418.1917 | 686.2466 | 612.2912 | 707.7553
2419.1917 | 689.6283 | 612.1832 | 694.7801
2420.1917 | 683.1086 | 611.0982 | 695.3975
2421.1917 | 678.6207 | 610.6824 | 703.044
2422.1917 | 689.7616 | 610.2521 | 706.6571
2423.1917 | 683.3566 | 609.5123 | 708.2479
2424.1917 | 680.3501 | 611.0326 | 704.1529
2425.1917 | 681.7933 | 610.1978 | 706.8272
2426.1917 | 678.0011 | 608.7052 | 710.77
2427.1917 | 688.3152 | 608.4764 | 714.62
2428.1917 | 690.8625 | 608.5322 | 716.7202
2429.1917 | 692.3925 | 607.628 | 717.7711
2430.1917 | 684.9531 | 606.336 | 714.3994
2431.1917 | 677.6129 | 605.1188 | 709.2168
2432.1917 | 682.63 | 603.8793 | 703.0277
2433.1917 | 695.6933 | 603.0486 | 707.5846
2434.1917 | 695.7943 | 603.0069 | 712.4418
2435.1917 | 702.4892 | 604.357 | 712.6585
2436.1917 | 702.0548 | 604.1407 | 714.1677
2437.1917 | 705.3482 | 603.2604 | 717.9418
2438.1917 | 700.0458 | 602.4693 | 720.2144
2439.1917 | 698.7053 | 601.6778 | 723.3779
2440.1917 | 690.7916 | 601.1342 | 722.3851
2441.1917 | 686.9094 | 602.4939 | 714.4413
2442.1917 | 680.1175 | 605.2101 | 713.0574
2443.1917 | 675.3908 | 605.7384 | 711.7648
2444.1917 | 675.5286 | 605.1683 | 716.5001
2445.1917 | 677.4523 | 604.1864 | 723.04
2446.1917 | 673.7075 | 603.9049 | 717.1996
2447.1917 | 669.5324 | 602.781 | 716.2492
2448.1917 | 665.5976 | 601.752 | 712.1398
2449.1917 | 665.4839 | 601.9906 | 712.6069
2450.1917 | 676.6533 | 602.1856 | 712.3154
2451.1917 | 677.3792 | 602.56 | 718.7158
2452.1917 | 677.4055 | 603.091 | 723.5168
2453.1917 | 675.5545 | 605.6024 | 717.9682
2454.1917 | 674.3715 | 605.1642 | 718.2926
2455.1917 | 681.8593 | 603.658 | 718.5764
2456.1917 | 686.9117 | 604.6186 | 717.7179
2457.1917 | 678.9458 | 606.3456 | 712.3645
2458.1917 | 675.1818 | 605.3912 | 709.2562
2459.1917 | 678.9416 | 606.9599 | 709.5652
2460.1917 | 679.4094 | 607.3245 | 698.3668
2461.1917 | 672.1963 | 609.0384 | 695.4931
2462.1917 | 667.8789 | 608.6319 | 687.9929
2463.1917 | 663.5654 | 608.9532 | 687.7667
2464.1917 | 660.6462 | 608.8725 | 689.644
2465.1917 | 664.3769 | 607.7789 | 688.1221
2466.1917 | 657.4931 | 606.7724 | 687.8629
2467.1917 | 653.7728 | 606.8803 | 679.8125
2468.1917 | 654.8352 | 606.6064 | 676.6365
2469.1917 | 652.8258 | 608.9144 | 678.1836
2470.1917 | 651.8464 | 607.9563 | 678.2475
2471.1917 | 648.5666 | 607.9288 | 674.4483
2472.1917 | 649.3717 | 607.502 | 675.9681
2473.1917 | 650.0516 | 609.2085 | 674.4898
2474.1917 | 647.2566 | 608.5922 | 672.9055
2475.1917 | 644.5942 | 608.6729 | 671.3109
2476.1917 | 643.9852 | 607.6541 | 677.0735
2477.1917 | 646.962 | 605.1723 | 687.0891
2478.1917 | 646.9252 | 603.4915 | 698.5744
2479.1917 | 651.2031 | 602.3355 | 697.5857
2480.1917 | 652.8186 | 602.5213 | 704.2108
2481.1917 | 655.5987 | 601.9141 | 702.7954
2482.1917 | 651.2122 | 601.631 | 707.143
2483.1917 | 652.6097 | 601.7936 | 705.6263
2484.1917 | 650.644 | 603.728 | 699.0781
2485.1917 | 647.8461 | 604.7091 | 692.0826
2486.1917 | 647.543 | 607.1879 | 689.0701
2487.1917 | 645.3203 | 608.1892 | 692.0477
2488.1917 | 646.7233 | 607.249 | 683.4863
2489.1917 | 642.9161 | 605.6195 | 680.0968
2490.1917 | 640.7787 | 604.749 | 674.8758
2491.1917 | 641.745 | 604.0543 | 674.3343
2492.1917 | 641.736 | 602.0554 | 679.7797
2493.1917 | 643.1775 | 600.6851 | 677.732
2494.1917 | 646.014 | 599.7829 | 675.8679
2495.1917 | 642.7731 | 599.4397 | 675.096
2496.1917 | 640.541 | 599.2823 | 673.0769
2497.1917 | 639.2326 | 599.0054 | 674.2181
2498.1917 | 636.8361 | 598.9633 | 667.9773
2499.1917 | 638.2689 | 598.0984 | 672.1817
2500.1917 | 637.1923 | 596.5658 | 668.2801
2501.1917 | 635.0471 | 595.7258 | 661.4407
2502.1917 | 634.6038 | 597.1708 | 667.4136
2503.1917 | 639.0374 | 595.6574 | 677.9501
2504.1917 | 640.1806 | 594.8197 | 686.7183
2505.1917 | 637.1848 | 594.4345 | 683.004
2506.1917 | 635.5223 | 596.4155 | 672.1822
2507.1917 | 633.7361 | 598.7739 | 667.2306
2508.1917 | 634.1324 | 597.8105 | 663.4791
2509.1917 | 636.3394 | 597.3964 | 662.7759
2510.1917 | 635.2249 | 597.3618 | 663.0235
2511.1917 | 633.5901 | 598.1764 | 660.4579
2512.1917 | 632.1729 | 598.7228 | 656.1541
2513.1917 | 631.5769 | 597.6112 | 668.1249
2514.1917 | 630.1464 | 596.7652 | 670.2061
2515.1917 | 628.3205 | 597.3197 | 666.889
2516.1917 | 627.3413 | 597.2087 | 667.7576
2517.1917 | 630.3412 | 595.9143 | 672.6951
2518.1917 | 629.7993 | 593.6537 | 680.2332
2519.1917 | 626.8922 | 593.4048 | 678.8016
2520.1917 | 626.5851 | 594.6433 | 670.5817
2521.1917 | 628.2984 | 595.1827 | 662.8483
2522.1917 | 627.4848 | 595.1573 | 662.4054
2523.1917 | 625.7378 | 592.4872 | 671.8107
2524.1917 | 622.7384 | 590.4817 | 672.0243
2525.1917 | 620.7292 | 589.7775 | 665.8392
2526.1917 | 618.0092 | 588.7968 | 667.628
2527.1917 | 618.2356 | 588.0211 | 673.0578
2528.1917 | 616.0793 | 586.9611 | 673.631
2529.1917 | 617.7718 | 586.4298 | 674.1526
2530.1917 | 618.6838 | 587.2948 | 672.868
2531.1917 | 618.7531 | 588.3834 | 667.3579
2532.1917 | 618.2479 | 587.8494 | 664.556
2533.1917 | 617.0628 | 586.8108 | 663.7237
2534.1917 | 615.0175 | 586.8104 | 659.9015
2535.1917 | 614.6474 | 586.867 | 662.9607
2536.1917 | 613.199 | 586.2796 | 660.9893
2537.1917 | 613.5998 | 586.9148 | 659.4274
2538.1917 | 614.7694 | 587.3254 | 660.68
2539.1917 | 614.0605 | 586.8486 | 662.3302
2540.2073 | 612.6864 | 584.07 | 666.6624
2541.1917 | 611.2506 | 584.3961 | 667.3978
2542.1917 | 609.7026 | 584.596 | 667.7172
2543.1917 | 609.2256 | 585.3471 | 661.7342
2544.2073 | 608.9318 | 585.8102 | 663.6177
2545.1917 | 610.1009 | 586.0909 | 665.8658
2546.1917 | 615.9376 | 584.6475 | 673.5044
2547.1917 | 614.7779 | 584.2797 | 673.1766
2548.1917 | 614.7205 | 583.8895 | 684.3046
2549.1917 | 614.0225 | 583.6229 | 684.7944
2550.1917 | 611.8924 | 582.7976 | 684.6644
2551.1917 | 610.4489 | 581.2625 | 677.7126
2552.1917 | 610.966 | 581.7695 | 679.2798
2553.1917 | 609.1694 | 582.1434 | 679.4848
2554.1917 | 608.389 | 583.3236 | 672.8159
2555.1917 | 608.0076 | 584.1436 | 672.9194
2556.1917 | 606.9185 | 584.0544 | 665.6361
2557.1917 | 606.6386 | 584.478 | 663.5845
2558.1917 | 606.1061 | 583.5201 | 666.0335
2559.1917 | 606.5133 | 584.0173 | 666.1653
2560.1917 | 606.3644 | 584.8823 | 660.6244
2561.1917 | 604.3771 | 584.7694 | 663.7219
2562.1917 | 604.2236 | 583.1526 | 660.5935
2563.1917 | 604.3466 | 583.1378 | 664.9828
2564.1917 | 602.6356 | 583.3291 | 665.7089
2565.1917 | 600.7352 | 585.1111 | 656.3249
2566.1917 | 599.92 | 586.6321 | 650.7187
2567.1917 | 598.0494 | 586.6766 | 645.1589
2568.1917 | 596.8853 | 585.8753 | 652.9887
2569.1917 | 595.9834 | 585.8457 | 656.0092
2570.1917 | 594.1253 | 584.0658 | 658.0103
2571.1917 | 592.1643 | 583.2124 | 660.9192
2572.1917 | 590.2994 | 583.9271 | 652.0165
2573.1917 | 589.3583 | 584.4603 | 656.5794
2574.1917 | 588.1718 | 582.9355 | 663.8707
2575.1917 | 586.9232 | 582.277 | 669.1959
2576.1917 | 585.9674 | 582.9025 | 662.5634
2577.1917 | 585.3669 | 582.9615 | 653.1396
2578.1917 | 584.5547 | 582.467 | 646.7719
2579.1917 | 583.8747 | 582.1377 | 639.1041
2580.1917 | 584.6755 | 583.5432 | 632.1192
2581.1917 | 585.1783 | 584.8946 | 624.9113
2582.1917 | 585.3906 | 587.0476 | 620.9913
2583.1917 | 586.9038 | 588.8959 | 617.5286
2584.1917 | 586.5515 | 588.696 | 623.8939
2585.1917 | 587.0852 | 589.6801 | 620.5576
2586.1917 | 586.7087 | 588.8037 | 620.9562
2587.1917 | 585.6233 | 587.0616 | 621.6567
2588.1917 | 584.6254 | 587.1253 | 622.1704
2589.1917 | 584.5382 | 587.7311 | 621.3525
2590.1917 | 583.8133 | 588.7927 | 618.7647
2591.1917 | 583.4913 | 589.7766 | 623.2119
2592.1917 | 581.9447 | 588.3561 | 622.6105
2593.1917 | 581.1414 | 587.7373 | 622.7667
2594.1917 | 580.0974 | 585.1231 | 623.0219
2595.1917 | 578.8764 | 583.3836 | 629.0304
2596.1917 | 579.1039 | 583.4966 | 624.461
2597.1917 | 578.2358 | 582.3635 | 620.8845
2598.1917 | 577.153 | 580.6017 | 616.6749
2599.1917 | 576.1961 | 578.6907 | 616.941
2600.1917 | 575.8386 | 577.1085 | 624.6903
2601.1917 | 575.2688 | 574.8596 | 634.8558
2602.1917 | 574.7791 | 572.8733 | 644.1819
2603.1917 | 573.3557 | 570.8733 | 638.4391
2604.1917 | 572.5036 | 571.7009 | 638.8636
2605.1917 | 572.1442 | 571.2087 | 639.4717
2606.1917 | 572.1994 | 571.4235 | 651.1581
2607.1917 | 571.8857 | 571.9597 | 648.3894
2608.1917 | 572.8317 | 573.1409 | 642.1506
2609.1917 | 572.5111 | 573.9483 | 641.9065
2610.1917 | 571.7682 | 575.0087 | 636.9566
2611.1917 | 571.5843 | 575.5699 | 640.9936
2612.1917 | 571.8123 | 576.2124 | 643.0061
2613.1917 | 571.2683 | 575.1947 | 639.4963
2614.1917 | 572.3948 | 574.5564 | 639.638
2615.1917 | 573.072 | 573.6138 | 637.235
2616.1917 | 573.1352 | 572.8205 | 641.1517
2617.1917 | 571.422 | 570.3465 | 638.1963
2618.1917 | 571.7168 | 569.381 | 637.5732
2619.1917 | 571.6658 | 569.0595 | 642.5923
2620.1917 | 570.9891 | 567.568 | 640.2046
2621.1917 | 570.1786 | 567.1594 | 641.1724
2622.1917 | 569.7705 | 568.039 | 638.8607
2623.1917 | 569.3526 | 568.9466 | 634.9852
2624.1917 | 569.3767 | 571.2893 | 628.4252
2625.1917 | 568.6124 | 570.7815 | 629.1188
2626.1917 | 569.0899 | 570.7343 | 624.1741
2627.1917 | 568.9006 | 571.6433 | 619.3632
2628.1917 | 569.6459 | 572.5509 | 617.976
2629.1917 | 570.6311 | 573.6295 | 621.7873
2630.1917 | 570.1341 | 574.0218 | 619.0197
2631.1917 | 570.0715 | 572.7999 | 615.8069
2632.1917 | 569.7511 | 571.6274 | 614.4244
2633.1917 | 568.806 | 571.4928 | 615.4261
2634.1917 | 569.5975 | 572.8821 | 613.9289
2635.1917 | 569.3492 | 574.1621 | 614.947
2636.1917 | 569.8154 | 574.7969 | 609.5397
2637.1917 | 569.406 | 575.2778 | 610.3454
2638.1917 | 569.5322 | 574.0822 | 607.7299
2639.1917 | 568.9261 | 572.8766 | 610.6305
2640.1917 | 568.7107 | 570.6668 | 611.3815